## Test Facts
Last Row in IR Data sets: | 114
Power On | 82

## Penlight Matrix
Matrix of CAROLFIRE Penlight Small Scale Exposure Tests
Test # | Primary Application | Cable Insulation/Jacket Material | [8 empty] | Cable Item number (or numbers) | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  | Thermal Exposure kW/m2 (oC) see note 1 | Raceway Type |  |  | Group #
|  | Thermoset |  |  |  | Mixed | Spec. | Thermoplastic
|  | XLPE/ CSPE | EPR/ CPE | SR | XLPO/ XLPO | XLPE/ PVC | Vita- Link | PE/ PVC | PVC/ PVC | Tefzel |  | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 |  | 12" Tray | 2.5" Cnd | Air Drop
1 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.7 (475) | X |  |  | 1
2 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
3 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) | X
4 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
5 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
6 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) | X
7 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  | X
8 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  | X
9 | FMI | X | [8 empty] | 14 | X |  |  |  | X |  |  |  |  | X |  |  | 17.3 (470) |  |  | X
10 | FMI | [7 empty] | X |  | 5 | X |  |  |  | X |  |  |  |  | X |  |  | 6.1 (300) |  |  | X
11 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
12 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
13 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
14 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
15 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
16 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) | X
17 | FMI |  | X | [7 empty] | 2 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
18 | FMI |  |  | X | [6 empty] | 9 |  |  | X |  |  | X |  |  |  | X |  |  | 51 (700) | X
19 | FMI |  |  |  | X | [5 empty] | 8 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
20 | FMI |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
21 | FMI | [7 empty] | X |  | 1 |  |  | X |  |  | X |  |  |  | X |  |  | 6.1 (300) | X
22 | FMI | [8 empty] | X | 12 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) | X
23 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
24 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  | X
25 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
26 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  | X
27 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
28 | FMI | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  | X |  |  | 17.3 (470) |  |  | X
29 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
30 | FMI | [6 empty] | X |  |  | 15 |  |  | X |  |  | X |  |  |  | X |  |  | 7.3 (325) |  |  | X
31 | FMI | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | 51 (700) | X
32 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  | X
33 | Note 2 | [5 empty] | X |  |  |  | 11 |  |  | X |  |  |  | X | [5 empty] | NOT RUN |  |  | X
34 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 2
35 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
36 | 2-A, C | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
37 | 2-B, C | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
38 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 3
39 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
40 | Note 3 | X | [8 empty] | 10 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
41 | Note 3 | X | [5 empty] | X |  |  | 10&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
42 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 4
43 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
44 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
45 | 2-A, B, C | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
46 | 2-A, B, C | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X
47 | 2-A, C | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
48 | 2-B, C |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
49 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
50 | 2-A, B, C | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
51 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X |  |  | 5
52 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
53 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
54 | Note 3 | X | X | X | X |  |  | X |  | X | 10,2,9,8,15&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
55 | Note 3 | X | X |  |  | X |  | X | X | X | 10,2,3,15,1&12 |  |  | X |  |  | X | [5 empty] | X | NOT RUN | X
56 | Note 3 | X | X | [7 empty] | 10&2 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
57 | Note 3 |  | X |  |  |  |  | X |  |  | 2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
58 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
59 | Note 3 | X | X |  |  |  |  | X |  |  | 10,2&15 |  |  | X |  |  | X |  |  |  |  | X |  | NOT RUN |  | X
60 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X | [5 empty] | X | 23 (525) | X |  |  | 6
61 | 2-A, C |  |  |  |  | X |  |  |  |  | 3 |  |  | X |  |  | X |  |  |  |  | X |  | 23 (525) |  | X
62 | 2-A, C | X | [8 empty] | 13 |  |  |  | X |  |  |  |  | X | X |  |  | 17.3 (470) | X |  |  | 7
63 | 2-B, C | [7 empty] | X |  | 6 |  |  |  | X |  |  |  |  | X | X |  |  | 7.2 (325) | X
64 | 2-A, C | X | [8 empty] | 13 |  | X | [5 empty] | X |  | X |  |  | 17.3 (470) | X |  |  | 8
65 | 2-B, C | [7 empty] | X |  | 4 |  | X | [5 empty] | X |  | X |  |  | 7.2 (325) | X
66 | Note 2 | X |  |  |  |  | X |  |  |  | 10&11 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X |  |  | 9
67 | Note 2 | [5 empty] | X | X | X |  | 11,15&1 |  |  | X |  |  | X | X |  |  |  |  | X | NOT RUN | X
68 | 2-A, B, C | X | X |  | X | X | X | X |  |  | 10,2,8,3,11&15 |  |  | X |  |  | X | X |  |  |  |  | X | 23 (525) | X
Spec1 | Note 5 | [6 empty] | X | [5 empty] | X |  |  | X |  |  |  | X |  | X | Varies | X
Notes:
Not Run = Test was NOT RUN - these tests were dropped from testing per the additional notes below (see Notes 2 and 3). FMI = Fire Modeling Improvement 2-A, B, C = Bin 2, Items A, B, and/or C
1. Thermal Exposure conditions (Column X) are shown as both the nominal heat flux from the shroud (kW/m2) and shroud temperature (oC)
2. Based on the results of preliminary testing and Test 31, those subsequent tests involving the Vitalink cable in Penlight were not conducted. As a result, Tests 32, 33, 66 and 67 were not performed
3. Initial plans had called for the conduct of testing at two flux levels (one high flux condition and one low flux condition). Based on peer review feedback, it was decided to run all tests at the same heat flux (an intermediate flux value appopriate to each cable configuration). As a result, those tests originally planned as repeated test configurations performed under low flux conditions (Groups 3 and 5, Tests - and 51-59) were not conducted.
4. At the request of the Fire modeling teams, the tests in groups 7 and 8 were revised to provide additional thermal response data for single cables of varying plastic to copper content.
5. Special Test 1 (Spec1) was added to the matrix at the request of the fire modeling teams. This was a thermal-monitoring test only involving more extensive temperature response measurements for a cable bundle in conjunction with a single cable. This test involved no electrical functionality monitoring. The exposure conditions for this test were varied. The exposure began at 350C, was increased to 350C and then increased again to 375C. See data file for details.

## Shorting Summary
Shorting Sequence for Test 65
Test conditions: Cable: 2-conductor plus shield and drain wire, 16AWG, PVC insulated, PVC jacketed, industrial grade General Cable (Cable Item #4). Cable specimens present: One length of cable was monitored for electrical performance, a second length of cable monitored for temperature response, no other cable samples present. Raceway: 12" B-Line Series 2 tray (part number 248P09-12-144) located centrally in the Penlight chamber with chamber end walls closed and un-heated. One thermocouple was attached to the inner surface of the center tray rung. Exposure conditions: Shroud set to temperature of 325C, nominal 7.2 kW/m2 flux from shroud. Electrical repsonse monitoring: IRMS system using three channels - one for each insulated conductor and a third for the un-insulated shield drain wire (the drain was treated as a third conductor and was not grounded), however the cable tray was grounded. Thermal response monitoring: Shroud temperature and one cable temperature (see maps). Shroud power: Initiated after 82 seconds of baseline data monitoring.
DAQ Time | Penlight Time | Event | Interpretation
82 | 0 | Initiate Penlight Heating
340-352 | 258-270 | Shield (conductor 3) intermittently shorts to conductors 1 & 2 at less than 100 ohms (66 & 74) | First short circuit indications are between three conductors (intermittent)
364-367 | 282-285 | Conductor 1 and the Shield both short to ground intermittently at less than 1000 ohms (383 & 697) | Conductor 1 & Shield short to ground (intermittent)
376 | 294 | Conductor 2 shorts to the Shield (conductor 3) at less than 100 ohms (30)
379 | 297 | Conductor 1 shorts to conductor 2 at less than 100 ohms (69)
391 | 309 | Conductor 1 shorts to the Shield at less than 100 ohms (35)
450-457 | 368-375 | Conductors 1 & 2 and the Shield (conductor 3) all short to ground at less than 100 ohms (79, 36 & 98) | All conductors have shorted to ground at less than 100 ohms
633 | 551 | Power to Penlight shutoff
Additional Observations
Observation 1 | Note: For an instrument cable of this type, the Shield wire would normally be grounded. Using the IRMS system, the Shield was treated as a third conductor independent of the external ground (the tray).
Observation 2 | The initial shorting faults occurred between the insulated conductors and the Shield, and occurred 258 seconds (4.3 min.) after start of heating. The initial faults to ground occurred 282 seconds (4.7 min.) after start of heating.

## Thermocouple Map
Thermocouple map for TC's on and within the cable
Cable = PVC/PVC, 2-C with Shield (Cable Item #4)
Translation to data file names used in "PenTemps" WorkSheet:
| Map Name |  | Data File Name | Location
| TC1 | = | "Cable" | Within cable just below cable jacket, center position

## C-C
Conductor to Conductor Resistances
Penlight Test 65 |  |  | 2006-08-29 | 11:06
PVC | 2-C & Shield | Tray
325 C | 7.2 kW/m2
Penlight Time | C1-2 | Penlight Time | C1-3 | Penlight Time | C2-3 | Penlight Time | Minimums
-81 | 257537.9994 | -77.5 | 256937.9994 | -75 | 257737.9994 | -81 | 256937.9994
-72 | 257537.9994 | -69.5 | 256937.9994 | -66.5 | 257737.9994 | -72 | 256937.9994
-63.5 | 257537.9994 | -61 | 256937.9994 | -58 | 257737.9994 | -63.5 | 256937.9994
-55.5 | 257537.9994 | -52.5 | 256937.9994 | -49.5 | 257737.9994 | -55.5 | 256937.9994
-47 | 257537.9994 | -44 | 256937.9994 | -41.5 | 257737.9994 | -47 | 256937.9994
-38.5 | 257537.9994 | -35.5 | 256937.9994 | -33 | 257737.9994 | -38.5 | 256937.9994
-30 | 257537.9994 | -27.5 | 256937.9994 | -24.5 | 257737.9994 | -30 | 256937.9994
-21.5 | 257537.9994 | -19 | 256937.9994 | -16 | 257737.9994 | -21.5 | 256937.9994
-13.5 | 257537.9994 | -10.5 | 256937.9994 | -7.5 | 257737.9994 | -13.5 | 256937.9994
-5 | 85779.3315 | -2 | 256937.9994 | 0.5 | 257737.9994 | -5 | 85779.3315
3.5 | 257537.9994 | 6.5 | 256937.9994 | 9 | 257737.9994 | 3.5 | 256937.9994
12 | 257537.9994 | 14.5 | 256937.9994 | 17.5 | 257737.9994 | 12 | 256937.9994
20.5 | 257537.9994 | 23 | 256937.9994 | 26 | 257737.9994 | 20.5 | 256937.9994
28.5 | 257537.9994 | 31.5 | 256937.9994 | 34.5 | 257737.9994 | 28.5 | 256937.9994
37 | 257537.9994 | 40 | 256937.9994 | 42.5 | 257737.9994 | 37 | 256937.9994
45.5 | 257537.9994 | 48.5 | 256937.9994 | 51 | 257737.9994 | 45.5 | 256937.9994
54 | 128718.9988 | 56.5 | 256937.9994 | 59.5 | 257737.9994 | 54 | 128718.9988
62.5 | 257537.9994 | 65 | 256937.9994 | 68 | 257737.9994 | 62.5 | 256937.9994
70.5 | 257537.9994 | 73.5 | 256937.9994 | 76.5 | 257737.9994 | 70.5 | 256937.9994
79 | 257537.9994 | 82 | 256937.9994 | 84.5 | 257737.9994 | 79 | 256937.9994
87.5 | 257537.9994 | 90.5 | 256937.9994 | 93 | 257737.9994 | 87.5 | 256937.9994
96 | 257537.9994 | 98.5 | 256937.9994 | 101.5 | 257737.9994 | 96 | 256937.9994
104.5 | 257537.9994 | 107 | 256937.9994 | 110 | 257737.9994 | 104.5 | 256937.9994
112.5 | 257537.9994 | 115.5 | 256937.9994 | 118.5 | 257737.9994 | 112.5 | 256937.9994
121 | 257537.9994 | 124 | 256937.9994 | 126.5 | 257737.9994 | 121 | 256937.9994
129.5 | 257537.9994 | 132.5 | 256937.9994 | 135 | 257737.9994 | 129.5 | 256937.9994
138 | 257537.9994 | 140.5 | 256937.9994 | 143.5 | 257737.9994 | 138 | 256937.9994
146.5 | 257537.9994 | 149 | 256937.9994 | 152 | 257737.9994 | 146.5 | 256937.9994
154.5 | 257537.9994 | 157.5 | 256937.9994 | 160 | 257737.9994 | 154.5 | 256937.9994
163 | 257537.9994 | 166 | 256937.9994 | 168.5 | 257737.9994 | 163 | 256937.9994
171.5 | 257537.9994 | 174.5 | 256937.9994 | 177 | 257737.9994 | 171.5 | 256937.9994
180 | 257537.9994 | 182.5 | 256937.9994 | 185.5 | 257737.9994 | 180 | 256937.9994
188.5 | 257537.9994 | 191 | 256937.9994 | 194 | 257737.9994 | 188.5 | 256937.9994
196.5 | 257537.9994 | 199.5 | 256937.9994 | 202.5 | 257737.9994 | 196.5 | 256937.9994
205 | 257537.9994 | 208 | 256937.9994 | 210.5 | 257737.9994 | 205 | 256937.9994
213.5 | 257537.9994 | 216.5 | 256937.9994 | 219 | 257737.9994 | 213.5 | 256937.9994
222 | 257537.9994 | 224.5 | 256937.9994 | 227.5 | 257737.9994 | 222 | 256937.9994
230.5 | 257537.9994 | 233 | 256937.9994 | 235.5 | 257737.9994 | 230.5 | 256937.9994
238.5 | 257537.9994 | 241.5 | 256937.9994 | 244.5 | 257737.9994 | 238.5 | 256937.9994
247 | 257537.9994 | 250 | 256937.9994 | 252.5 | 257737.9994 | 247 | 256937.9994
255.5 | 257537.9994 | 258 | 65.839 | 261 | 85812.6408 | 255.5 | 65.839
263.5 | 257537.9994 | 266.5 | 256937.9994 | 269.5 | 73.6256 | 263.5 | 73.6256
272.5 | 257338.0776 | 275 | 256937.9994 | 278 | 257737.9994 | 272.5 | 256937.9994
280.5 | 257537.9994 | 283.5 | 48.8051 | 286.5 | 64309.4806 | 280.5 | 48.8051
289 | 257338.0388 | 292 | 256638.1167 | 294.5 | 30.2841 | 289 | 30.2841
297.5 | 68.9082 | 300 | 1403.6203 | 303 | 42.7933 | 297.5 | 42.7933
305.5 | 73.0061 | 308.5 | 34.5017 | 311.5 | 70.1233 | 305.5 | 34.5017
314 | 42.6265 | 317 | 70.137 | 319.5 | 31.3016 | 314 | 31.3016
322.5 | 75.2735 | 325.5 | 39.7336 | 328 | 38.9767 | 322.5 | 38.9767
331 | 71.7634 | 334 | 27.9703 | 336.5 | 25.4505 | 331 | 25.4505
339.5 | 72.3822 | 342.5 | 74.2952 | 345 | 50.765 | 339.5 | 50.765
348 | 24.4383 | 350.5 | 38.4786 | 353.5 | 23.5882 | 348 | 23.5882
356.5 | 25.58 | 359 | 51.9707 | 362 | 59.5896 | 356.5 | 25.58
364.5 | 73.8896 | 367.5 | 68.7205 | 370.5 | 17.8421 | 364.5 | 17.8421
373 | 32.5297 | 376 | 31.7593 | 378.5 | 495.1501 | 373 | 31.7593
381.5 | 837.6001 | 384 | 2837.2002 | 387 | 3459.2145 | 381.5 | 837.6001
389.5 | 361.7764 | 392.5 | 3453.4251 | 395.5 | 1111.2861 | 389.5 | 361.7764
398.5 | 532.8371 | 401 | 165.2685 | 404 | 43.602 | 398.5 | 43.602
406.5 | 2.5257 | 409.5 | 39.5266 | 412.5 | 11.4823 | 406.5 | 2.5257
415 | 1919.855 | 418 | 1304.0259 | 420.5 | 656.9579 | 415 | 656.9579
423.5 | 1572.1005 | 426.5 | 4701.5379 | 429 | 39.517 | 423.5 | 39.517
431.5 | 303.2539 | 434.5 | 440.4301 | 437.5 | 12197.3923 | 431.5 | 303.2539
440 | 10996.4308 | 443 | 5898.8167 | 445.5 | 2981.798 | 440 | 2981.798
448.5 | 3167.5671 | 451.5 | 327.4459 | 454.5 | 7377.2246 | 448.5 | 327.4459
457 | 1532.4985 | 460 | 5410.6562 | 462.5 | 4064.1148 | 457 | 1532.4985
465.5 | 20.5569 | 468.5 | 2846.3536 | 471 | 3057.7643 | 465.5 | 20.5569
473.5 | 9334.5595 | 476.5 | 9.9592 | 479.5 | 0.92476 | 473.5 | 0.92476
482.5 | 7613.5253 | 485 | 14.5861 | 488 | 269.2243 | 482.5 | 14.5861
490.5 | 9.3444 | 493.5 | 14.3748 | 496 | 1.3167 | 490.5 | 1.3167
499 | 12.4664 | 501.5 | 4.5146 | 504.5 | 26.0911 | 499 | 4.5146
507.5 | 22.7753 | 510.5 | 14.007 | 513 | 8.7109 | 507.5 | 8.7109
516 | 0.084728 | 518.5 | 4249.3594 | 521.5 | 0.28254 | 516 | 0.084728
524 | 15.7113 | 527 | 2.0879 | 529.5 | 23.9678 | 524 | 2.0879
532.5 | 25.7391 | 535.5 | 25.0662 | 538 | 8.3309 | 532.5 | 8.3309
541 | 13.8576 | 544 | 29.3403 | 546.5 | 1165.3893 | 541 | 13.8576
549.5 | 5.7481 | 552 | 22.1263 | 555 | 0.5243 | 549.5 | 0.5243
557.5 | 5.2977 | 560.5 | 5092.6666 | 563.5 | 1.8187 | 557.5 | 1.8187
566 | 5.4324 | 569 | 3.0714 | 571.5 | 0.72491 | 566 | 0.72491
574.5 | 0.92304 | 577.5 | 0.2148 | 580 | 3.2672 | 574.5 | 0.2148
583 | 18.2941 | 585.5 | 4.5146 | 588.5 | 14.0515 | 583 | 4.5146
591.5 | 11.909 | 594 | 7.2403 | 597 | 16.5606 | 591.5 | 7.2403
599.5 | 2.2449 | 602.5 | 6.7766 | 605.5 | 24.214 | 599.5 | 2.2449
608.5 | 1.5708 | 611 | 23.1521 | 614 | 0.60464 | 608.5 | 0.60464
616.5 | 13.1837 | 619.5 | 0.13308 | 622 | 2.1983 | 616.5 | 0.13308
625 | 14.1189 | 627.5 | 17.2364 | 630.5 | 7.4852 | 625 | 7.4852
633.5 | 29.0442 | 636 | 9.5697 | 639 | 13.6348 | 633.5 | 9.5697
642 | 8.912 | 644.5 | 23.4569 | 647.5 | 2.283 | 642 | 2.283
650 | 24.5495 | 653 | 15.0108 | 656 | 16.9983 | 650 | 15.0108
658.5 | 13.442 | 661.5 | 14.0594 | 664.5 | 23.053 | 658.5 | 13.442
667 | 28.4487 | 669.5 | 17.6804 | 672.5 | 8.3783 | 667 | 8.3783
675.5 | 2.6706 | 678 | 0.11133 | 681 | 3.224 | 675.5 | 0.11133
684 | 15.6575 | 686.5 | 19.2603 | 689.5 | 1.9449 | 684 | 1.9449
692 | 0.12545 | 695 | 1.2472 | 697.5 | 13.7387 | 692 | 0.12545
700.5 | 20.8152 | 703.5 | 5.4533 | 706.5 | 13.6348 | 700.5 | 5.4533
709 | 13.2869 | 712 | 0.59675 | 714.5 | 16.5606 | 709 | 0.59675
717.5 | 16.5782 | 720.5 | 25.0662 | 723 | 5.1119 | 717.5 | 5.1119
726 | 5.2977 | 728.5 | 10.5486 | 731.5 | 3.6137 | 726 | 3.6137
734 | 24.1784 | 737 | 6.7304 | 739.5 | 17.8834 | 734 | 6.7304
742.5 | 18.4627 | 745.5 | 11.5948 | 748 | 16.8886 | 742.5 | 11.5948
751 | 17.6241 | 753.5 | 2.9852 | 756.5 | 15.5872 | 751 | 2.9852
759.5 | 0.90515 | 762 | 17.9595 | 765 | 5.6506 | 759.5 | 0.90515
767.5 | 20.9908 | 770.5 | 5.8606 | 773.5 | 0.32291 | 767.5 | 0.32291
776 | 28.1858 | 779 | 17.0156 | 781.5 | 20.7346 | 776 | 17.0156
784.5 | 8.0569 | 787.5 | 5.2733 | 790 | 15.9099 | 784.5 | 5.2733
793 | 9.1518 | 795.5 | 16.5218 | 798.5 | 14.5766 | 793 | 9.1518
801.5 | 17.5132 | 804.5 | 7.4736 | 807 | 30.1505 | 801.5 | 7.4736
810 | 0.37042 | 812.5 | 17.0707 | 815.5 | 0.041566 | 810 | 0.041566
818 | 17.1815 | 821 | 16.4126 | 823.5 | 0.16362 | 818 | 0.16362
826.5 | 20.8737 | 829.5 | 29.8778 | 832 | 24.3993 | 826.5 | 20.8737

## C-G Min
Average Conductor to Ground Resistances
Penlight Test 65 |  |  | 2006-08-29 | 11:06
PVC | 2-C & Shield | Tray
325 C | 7.2 kW/m2
Penlight Time | C1-G |  | Penlight Time | C2-G | Penlight Time | C3-G | Penlight Time | Minimums
-79.25 | 256938 |  | -78 | 257538 | -76.25 | 256938 | -79.25 | 256938
-70.75 | 256938 |  | -69.25 | 257538 | -68 | 256938 | -70.75 | 256938
-62.25 | 256938 |  | -60.75 | 257538 | -59.5 | 256938 | -62.25 | 256938
-54 | 256938 |  | -52.5 | 257538 | -51 | 256938 | -54 | 256938
-45.5 | 256938 |  | -44.25 | 257538 | -42.75 | 256938 | -45.5 | 256938
-37 | 256938 |  | -35.75 | 257538 | -34.25 | 256938 | -37 | 256938
-28.75 | 256938 |  | -27.25 | 257538 | -26 | 256938 | -28.75 | 256938
-20.25 | 256938 |  | -18.75 | 257538 | -17.5 | 256938 | -20.25 | 256938
-12 | 256938 |  | -10.5 | 257538 | -9 | 256938 | -12 | 256938
-3.5 | 85779.3333 |  | -2.25 | 257538 | -0.75 | 256938 | -3.5 | 85779.3333
5 | 256938 |  | 6.25 | 257538 | 7.75 | 256938 | 5 | 256938
13.25 | 256938 |  | 14.75 | 257538 | 16 | 256938 | 13.25 | 256938
21.75 | 256938 |  | 23.25 | 257538 | 24.5 | 256938 | 21.75 | 256938
30 | 256938 |  | 31.5 | 257538 | 33 | 256938 | 30 | 256938
38.5 | 256938 |  | 39.75 | 257538 | 41.25 | 256938 | 38.5 | 256938
47 | 256938 |  | 48.25 | 257538 | 49.75 | 256938 | 47 | 256938
55.25 | 128719 |  | 56.75 | 257538 | 58 | 256938 | 55.25 | 128719
63.75 | 256938 |  | 65.25 | 257538 | 66.5 | 256938 | 63.75 | 256938
72 | 256938 |  | 73.5 | 257538 | 75 | 256938 | 72 | 256938
80.5 | 256938 |  | 81.75 | 257538 | 83.25 | 256938 | 80.5 | 256938
89 | 256938 |  | 90.25 | 257538 | 91.75 | 256938 | 89 | 256938
97.25 | 256938 |  | 98.75 | 257538 | 100 | 256938 | 97.25 | 256938
105.75 | 256938 |  | 107.25 | 257538 | 108.5 | 256938 | 105.75 | 256938
114 | 256938 |  | 115.5 | 257538 | 117 | 256938 | 114 | 256938
122.5 | 256938 |  | 123.75 | 257538 | 125.25 | 256938 | 122.5 | 256938
131 | 256938 |  | 132.25 | 257538 | 133.75 | 256938 | 131 | 256938
139.25 | 256938 |  | 140.75 | 257538 | 142 | 256938 | 139.25 | 256938
147.75 | 256938 |  | 149.25 | 257538 | 150.5 | 256938 | 147.75 | 256938
156 | 256938 |  | 157.25 | 257538 | 158.75 | 256938 | 156 | 256938
164.5 | 256938 |  | 165.75 | 257538 | 167.25 | 256938 | 164.5 | 256938
173 | 256938 |  | 174.25 | 257538 | 175.75 | 256938 | 173 | 256938
181.25 | 256938 |  | 182.75 | 257538 | 184 | 256938 | 181.25 | 256938
189.75 | 256938 |  | 191.25 | 257538 | 192.5 | 256938 | 189.75 | 256938
198 | 256938 |  | 199.5 | 257538 | 201 | 256938 | 198 | 256938
206.5 | 256938 |  | 207.75 | 257538 | 209.25 | 256938 | 206.5 | 256938
215 | 256938 |  | 216.25 | 257538 | 217.75 | 256938 | 215 | 256938
223.25 | 256938 |  | 224.75 | 257538 | 226 | 256938 | 223.25 | 256938
231.75 | 256938 |  | 233 | 257538 | 234.25 | 256938 | 231.75 | 256938
240 | 256938 |  | 241.5 | 257538 | 243 | 256938 | 240 | 256938
248.5 | 256938 |  | 249.75 | 257538 | 251.25 | 256938 | 248.5 | 256938
256.75 | 13931.4636 |  | 258.25 | 128868.9418 | 259.5 | 9044.5496 | 256.75 | 9044.5496
265 | 256938 |  | 266.5 | 4785.7357 | 268 | 256938 | 265 | 4785.7357
273.75 | 256938 |  | 275.25 | 257538 | 276.5 | 256938 | 273.75 | 256938
282 | 382.9406 |  | 283.5 | 128818.9224 | 285 | 697.2682 | 282 | 382.9406
290.5 | 256938 |  | 291.75 | 3442.1424 | 293.25 | 9783.3327 | 290.5 | 3442.1424
298.75 | 5726.7296 |  | 300.25 | 27262.9488 | 301.5 | 6373.4377 | 298.75 | 5726.7296
307 | 2485.8775 |  | 308.5 | 9416.8665 | 310 | 3003.7435 | 307 | 2485.8775
315.5 | 12471.7976 |  | 316.75 | 1200.6925 | 318.25 | 2906.8374 | 315.5 | 1200.6925
324 | 4310.8196 |  | 325.25 | 2703.0968 | 326.75 | 7564.0088 | 324 | 2703.0968
332.5 | 591.3109 |  | 333.75 | 4251.6012 | 335.25 | 487.7701 | 332.5 | 487.7701
341 | 3186.6771 |  | 342.25 | 3328.2372 | 343.75 | 4941.3399 | 341 | 3186.6771
349.25 | 1654.8135 |  | 350.75 | 2293.6972 | 352 | 9408.9862 | 349.25 | 1654.8135
357.75 | 4590.2824 |  | 359.25 | 9284.6339 | 360.5 | 8746.8152 | 357.75 | 4590.2824
366 | 4971.1726 |  | 367.5 | 35.5426 | 369 | 98.1494 | 366 | 35.5426
374.5 | 78.5754 |  | 375.75 | 3.4896 | 377.25 | 31.6521 | 374.5 | 3.4896
382.75 | 23.126 |  | 384.25 | 7.6866 | 385.5 | 29.3333 | 382.75 | 7.6866
391 | 2.6632 |  | 392.5 | 20.6624 | 394 | 4.2002 | 391 | 2.6632
399.75 | 2.2718 |  | 401.25 | 1.6482 | 402.5 | 2.3249 | 399.75 | 1.6482
408 | 3.4026 |  | 409.5 | 6.4303 | 411 | 18.4745 | 408 | 3.4026
416.5 | 12.6366 |  | 417.75 | 6.8347 | 419.25 | 7.7122 | 416.5 | 6.8347
425 | 12.284 |  | 426.25 | 1.8193 | 427.75 | 7.9916 | 425 | 1.8193
433 | 1.5611 |  | 434.5 | 7.109 | 436 | 28.4716 | 433 | 1.5611
441.5 | 23.3717 |  | 442.75 | 20.6264 | 444.25 | 7.3162 | 441.5 | 7.3162
450 | 10.199 |  | 451.5 | 8.3642 | 453 | 1.4418 | 450 | 1.4418
458.5 | 12.0617 |  | 459.75 | 5.9157 | 461.25 | 13.9712 | 458.5 | 5.9157
467 | 1.1311 |  | 468.25 | 0.78538 | 469.75 | 12.9429 | 467 | 0.78538
475 | 11.3683 |  | 476.5 | 0.63934 | 478 | 0.95758 | 475 | 0.63934
483.75 | 15.9396 |  | 485.25 | 1.3178 | 486.5 | 0.68077 | 483.75 | 0.68077
492 | 10.7644 |  | 493.25 | 2.8472 | 494.75 | 4.4445 | 492 | 2.8472
500.25 | 5.9951 |  | 501.75 | 27.3274 | 503 | 23.4856 | 500.25 | 5.9951
509 | 15.3671 |  | 510.25 | 10.1401 | 511.75 | 3.6743 | 509 | 3.6743
517.25 | 1.6323 |  | 518.75 | 1.2718 | 520 | 3.094 | 517.25 | 1.2718
525.5 | 3.6026 |  | 526.75 | 10.2902 | 528.25 | 2.195 | 525.5 | 2.195
534 | 26.3086 |  | 535.25 | 9.765 | 536.75 | 16.616 | 534 | 9.765
542.5 | 15.2227 |  | 543.75 | 4.6177 | 545.25 | 11.5699 | 542.5 | 4.6177
550.75 | 7.2151 |  | 552.25 | 1.0337 | 553.5 | 1.0733 | 550.75 | 1.0337
559 | 6.7708 |  | 560.5 | 3.3419 | 562 | 16.7824 | 559 | 3.3419
567.5 | 4.572 |  | 568.75 | 0.83614 | 570.25 | 11.6101 | 567.5 | 0.83614
576 | 0.63984 |  | 577.25 | 4.7696 | 578.75 | 24.3532 | 576 | 0.63984
584.25 | 5.9951 |  | 585.75 | 15.4154 | 587 | 4.8548 | 584.25 | 4.8548
592.75 | 8.6841 |  | 594.25 | 17.8957 | 595.5 | 7.1438 | 592.75 | 7.1438
601 | 3.7608 |  | 602.5 | 17.0018 | 604 | 1.511 | 601 | 1.511
609.75 | 3.0964 |  | 611.25 | 0.95458 | 612.5 | 1.6764 | 609.75 | 0.95458
618 | 1.6764 |  | 619.25 | 3.716 | 620.75 | 6.1936 | 618 | 1.6764
626.25 | 15.481 |  | 627.75 | 8.9303 | 629 | 1.9123 | 626.25 | 1.9123
634.75 | 10.9836 |  | 636.25 | 15.0036 | 637.5 | 0.99725 | 634.75 | 0.99725
643.25 | 10.3375 |  | 644.75 | 2.6855 | 646 | 0.99725 | 643.25 | 0.99725
651.5 | 16.3594 |  | 653 | 5.3734 | 654.5 | 8.472 | 651.5 | 5.3734
660 | 14.8119 |  | 661.5 | 6.3302 | 663 | 1.7112 | 660 | 1.7112
668.25 | 18.9991 |  | 669.75 | 1.0741 | 671 | 20.7318 | 668.25 | 1.0741
676.75 | 1.4357 |  | 678.25 | 4.7271 | 679.5 | 27.9593 | 676.75 | 1.4357
685.25 | 17.0018 |  | 686.75 | 3.4663 | 688 | 8.1355 | 685.25 | 3.4663
693.5 | 1.6725 |  | 694.75 | 6.2425 | 696.25 | 3.6743 | 693.5 | 1.6725
702 | 6.921 |  | 703.5 | 6.3302 | 705 | 22.9259 | 702 | 6.3302
710.5 | 0.95758 |  | 711.75 | 10.3847 | 713.25 | 1.3913 | 710.5 | 0.95758
719 | 17.9121 |  | 720.25 | 6.5887 | 721.75 | 1.7916 | 719 | 1.7916
727.25 | 6.7708 |  | 728.75 | 5.1113 | 730 | 1.4312 | 727.25 | 1.4312
735.5 | 8.181 |  | 736.75 | 8.3879 | 738.25 | 11.2237 | 735.5 | 8.181
744 | 12.9837 |  | 745.25 | 14.4549 | 746.75 | 1.9183 | 744 | 1.9183
752.25 | 4.487 |  | 753.75 | 16.9333 | 755 | 8.9144 | 752.25 | 4.487
760.75 | 2.4406 |  | 762.25 | 7.1201 | 763.5 | 3.7577 | 760.75 | 2.4406
769 | 7.3228 |  | 770.5 | 1.232 | 772 | 12.736 | 769 | 1.232
777.5 | 18.3416 |  | 778.75 | 22.0246 | 780.25 | 2.324 | 777.5 | 2.324
786 | 6.7434 |  | 787.25 | 17.2524 | 788.75 | 20.9371 | 786 | 6.7434
794.25 | 10.5742 |  | 795.75 | 9.4469 | 797 | 2.1545 | 794.25 | 2.1545
803 | 8.9144 |  | 804.25 | 8.115 | 805.75 | 25.5908 | 803 | 8.115
811.25 | 1.9138 |  | 812.75 | 1.591 | 814 | 4.9992 | 811.25 | 1.591
819.5 | 17.7453 |  | 820.75 | 1.7112 | 822.25 | 6.2373 | 819.5 | 1.7112
828 | 22.1612 |  | 829.25 | 25.652 | 830.75 | 26.3293 | 828 | 22.1612

## PenTemps
DAQ Time | Penlight Time | Shroud | Cable | Tray Rung
0 | -82 | 27.7 | 31.7 | 30.4
1 | -81 | 27.7 | 31.7 | 30.4
2 | -80 | 27.6 | 31.7 | 30.4
3 | -79 | 27.6 | 31.7 | 30.4
4 | -78 | 27.6 | 31.7 | 30.4
5 | -77 | 27.6 | 31.7 | 30.4
6 | -76 | 27.6 | 31.7 | 30.4
7 | -75 | 27.6 | 31.7 | 30.4
8 | -74 | 27.6 | 31.7 | 30.4
9 | -73 | 27.6 | 31.7 | 30.4
10 | -72 | 27.6 | 31.7 | 30.5
11 | -71 | 27.6 | 31.7 | 30.4
12 | -70 | 27.6 | 31.7 | 30.4
13 | -69 | 27.6 | 31.7 | 30.4
14 | -68 | 27.6 | 31.7 | 30.4
15 | -67 | 27.6 | 31.7 | 30.5
16 | -66 | 27.6 | 31.7 | 30.5
17 | -65 | 27.6 | 31.7 | 30.5
18 | -64 | 27.6 | 31.7 | 30.4
19 | -63 | 27.6 | 31.7 | 30.5
20 | -62 | 27.6 | 31.7 | 30.5
21 | -61 | 27.6 | 31.7 | 30.5
22 | -60 | 27.6 | 31.7 | 30.5
23 | -59 | 27.6 | 31.7 | 30.4
24 | -58 | 27.6 | 31.7 | 30.5
25 | -57 | 27.6 | 31.7 | 30.5
26 | -56 | 27.6 | 31.7 | 30.5
27 | -55 | 27.5 | 31.7 | 30.5
28 | -54 | 27.5 | 31.7 | 30.5
29 | -53 | 27.5 | 31.7 | 30.5
30 | -52 | 27.5 | 31.7 | 30.5
31 | -51 | 27.5 | 31.7 | 30.5
32 | -50 | 27.5 | 31.7 | 30.5
33 | -49 | 27.5 | 31.7 | 30.5
34 | -48 | 27.5 | 31.7 | 30.5
35 | -47 | 27.5 | 31.7 | 30.5
36 | -46 | 27.5 | 31.7 | 30.5
37 | -45 | 27.5 | 31.7 | 30.5
38 | -44 | 27.5 | 31.7 | 30.5
39 | -43 | 27.5 | 31.7 | 30.5
40 | -42 | 27.5 | 31.7 | 30.5
41 | -41 | 27.5 | 31.7 | 30.5
42 | -40 | 27.5 | 31.7 | 30.5
43 | -39 | 27.5 | 31.7 | 30.5
44 | -38 | 27.5 | 31.7 | 30.5
45 | -37 | 27.5 | 31.7 | 30.5
46 | -36 | 27.5 | 31.7 | 30.5
47 | -35 | 27.5 | 31.7 | 30.5
48 | -34 | 27.5 | 31.7 | 30.5
49 | -33 | 27.5 | 31.8 | 30.5
50 | -32 | 27.5 | 31.7 | 30.5
51 | -31 | 27.5 | 31.7 | 30.5
52 | -30 | 27.5 | 31.8 | 30.5
53 | -29 | 27.5 | 31.8 | 30.5
54 | -28 | 27.4 | 31.8 | 30.5
55 | -27 | 27.4 | 31.8 | 30.5
56 | -26 | 27.4 | 31.8 | 30.5
57 | -25 | 27.4 | 31.7 | 30.5
58 | -24 | 27.4 | 31.8 | 30.5
59 | -23 | 27.4 | 31.8 | 30.5
60 | -22 | 27.4 | 31.8 | 30.5
61 | -21 | 27.4 | 31.8 | 30.5
62 | -20 | 27.4 | 31.8 | 30.5
63 | -19 | 27.4 | 31.8 | 30.5
64 | -18 | 27.4 | 31.8 | 30.5
65 | -17 | 27.4 | 31.8 | 30.5
66 | -16 | 27.4 | 31.8 | 30.5
67 | -15 | 27.4 | 31.8 | 30.5
68 | -14 | 27.4 | 31.8 | 30.5
69 | -13 | 27.4 | 31.8 | 30.5
70 | -12 | 27.4 | 31.8 | 30.5
71 | -11 | 27.4 | 31.8 | 30.5
72 | -10 | 27.4 | 31.8 | 30.5
73 | -9 | 27.4 | 31.8 | 30.5
74 | -8 | 27.4 | 31.8 | 30.5
75 | -7 | 27.3 | 31.8 | 30.5
76 | -6 | 27.3 | 31.8 | 30.5
77 | -5 | 27.3 | 31.8 | 30.5
78 | -4 | 27.2 | 31.8 | 30
79 | -3 | 27 | 31.9 | 29.2
80 | -2 | 27.1 | 31.9 | 29
81 | -1 | 27.5 | 31.9 | 29
82 | 0 | 28.3 | 31.9 | 29
83 | 1 | 29.7 | 31.9 | 29.1
84 | 2 | 31.6 | 31.9 | 29.1
85 | 3 | 34 | 31.9 | 29.1
86 | 4 | 36.8 | 31.9 | 29.2
87 | 5 | 39.9 | 31.9 | 29.2
88 | 6 | 43.3 | 31.9 | 29.3
89 | 7 | 47 | 31.9 | 29.3
90 | 8 | 50.8 | 31.9 | 29.4
91 | 9 | 54.9 | 32 | 29.5
92 | 10 | 59.1 | 32 | 29.6
93 | 11 | 63.6 | 32.1 | 29.7
94 | 12 | 68.2 | 32.1 | 29.8
95 | 13 | 72.9 | 32.2 | 29.9
96 | 14 | 77.9 | 32.3 | 30.1
97 | 15 | 83 | 32.4 | 30.2
98 | 16 | 88.2 | 32.5 | 30.4
99 | 17 | 93.4 | 32.6 | 30.6
100 | 18 | 98.7 | 32.8 | 30.8
101 | 19 | 104.1 | 32.9 | 31
102 | 20 | 109.6 | 33.1 | 31.3
103 | 21 | 115.2 | 33.3 | 31.5
104 | 22 | 120.9 | 33.5 | 31.8
105 | 23 | 126.6 | 33.7 | 32.1
106 | 24 | 132.4 | 33.9 | 32.4
107 | 25 | 138.2 | 34.2 | 32.7
108 | 26 | 143.9 | 34.5 | 33.1
109 | 27 | 149.7 | 34.8 | 33.5
110 | 28 | 155.6 | 35.1 | 34
111 | 29 | 161.5 | 35.4 | 34.5
112 | 30 | 167.4 | 35.8 | 34.9
113 | 31 | 173.4 | 36.2 | 35.4
114 | 32 | 179.3 | 36.7 | 35.8
115 | 33 | 185.3 | 37.1 | 36.5
116 | 34 | 191.2 | 37.6 | 37.1
117 | 35 | 197.1 | 38.1 | 37.6
118 | 36 | 203 | 38.6 | 38.2
119 | 37 | 208.9 | 39.2 | 38.9
120 | 38 | 214.9 | 39.8 | 39.5
121 | 39 | 220.8 | 40.4 | 40.3
122 | 40 | 226.6 | 41 | 41
123 | 41 | 232.5 | 41.7 | 41.8
124 | 42 | 238.4 | 42.4 | 42.6
125 | 43 | 244.2 | 43.1 | 43.4
126 | 44 | 249.9 | 43.9 | 44.3
127 | 45 | 255.7 | 44.7 | 45.2
128 | 46 | 261.4 | 45.5 | 46.1
129 | 47 | 267 | 46.3 | 47
130 | 48 | 272.6 | 47.2 | 47.9
131 | 49 | 278.4 | 48.1 | 48.9
132 | 50 | 284.1 | 49.1 | 50
133 | 51 | 289.6 | 50.1 | 51.1
134 | 52 | 295 | 51.1 | 52.3
135 | 53 | 300.4 | 52.2 | 53.4
136 | 54 | 305.6 | 53.3 | 54.8
137 | 55 | 310.4 | 54.4 | 56
138 | 56 | 314.9 | 55.5 | 57.2
139 | 57 | 319.1 | 56.7 | 58.5
140 | 58 | 323 | 57.9 | 59.7
141 | 59 | 326.8 | 59.1 | 61
142 | 60 | 330.4 | 60.4 | 62.5
143 | 61 | 333.8 | 61.7 | 64
144 | 62 | 337 | 63 | 65.6
145 | 63 | 339.7 | 64.3 | 67.2
146 | 64 | 342.1 | 65.7 | 68.7
147 | 65 | 344.3 | 67.1 | 70.1
148 | 66 | 346.1 | 68.6 | 71.5
149 | 67 | 347.8 | 70 | 72.9
150 | 68 | 349.2 | 71.4 | 74.4
151 | 69 | 350.2 | 72.9 | 75.7
152 | 70 | 351.1 | 74.4 | 77.1
153 | 71 | 351.8 | 75.9 | 78.4
154 | 72 | 352.3 | 77.4 | 79.7
155 | 73 | 352.8 | 78.9 | 81
156 | 74 | 353.2 | 80.4 | 82.3
157 | 75 | 353.4 | 81.9 | 83.7
158 | 76 | 353.6 | 83.3 | 85
159 | 77 | 353.7 | 84.8 | 86.2
160 | 78 | 353.7 | 86.2 | 87.4
161 | 79 | 353.6 | 87.6 | 88.6
162 | 80 | 353.5 | 89.1 | 89.8
163 | 81 | 353.3 | 90.4 | 91
164 | 82 | 353.1 | 91.8 | 92.2
165 | 83 | 352.8 | 93.2 | 93.4
166 | 84 | 352.6 | 94.5 | 94.6
167 | 85 | 352.3 | 95.9 | 95.9
168 | 86 | 351.9 | 97.2 | 97.1
169 | 87 | 351.6 | 98.6 | 98.3
170 | 88 | 351.3 | 99.9 | 99.4
171 | 89 | 351 | 101.2 | 100.5
172 | 90 | 350.6 | 102.4 | 101.8
173 | 91 | 350.1 | 103.7 | 102.9
174 | 92 | 349.7 | 105 | 104.1
175 | 93 | 349.3 | 106.3 | 105.2
176 | 94 | 348.9 | 107.5 | 106.3
177 | 95 | 348.2 | 108.7 | 107.4
178 | 96 | 347.7 | 110 | 108.5
179 | 97 | 347.1 | 111.2 | 109.6
180 | 98 | 346.6 | 112.4 | 110.7
181 | 99 | 346 | 113.6 | 111.8
182 | 100 | 345.4 | 114.8 | 112.8
183 | 101 | 344.9 | 116 | 113.8
184 | 102 | 344.3 | 117.1 | 114.8
185 | 103 | 343.7 | 118.3 | 115.8
186 | 104 | 343.1 | 119.4 | 116.8
187 | 105 | 342.5 | 120.5 | 117.8
188 | 106 | 342 | 121.6 | 118.8
189 | 107 | 341.5 | 122.7 | 119.8
190 | 108 | 340.8 | 123.8 | 120.7
191 | 109 | 340.3 | 124.8 | 121.7
192 | 110 | 339.8 | 125.9 | 122.6
193 | 111 | 339.3 | 126.9 | 123.6
194 | 112 | 338.7 | 128 | 124.5
195 | 113 | 338.1 | 129 | 125.5
196 | 114 | 337.5 | 130 | 126.5
197 | 115 | 336.8 | 131 | 127.4
198 | 116 | 336.3 | 132 | 128.3
199 | 117 | 335.7 | 132.9 | 129.3
200 | 118 | 335 | 133.9 | 130.2
201 | 119 | 334.4 | 134.8 | 131.1
202 | 120 | 333.9 | 135.7 | 132
203 | 121 | 333.3 | 136.7 | 132.9
204 | 122 | 332.7 | 137.5 | 133.8
205 | 123 | 332.2 | 138.4 | 134.6
206 | 124 | 331.8 | 139.3 | 135.5
207 | 125 | 331.3 | 140.2 | 136.4
208 | 126 | 330.7 | 141 | 137.2
209 | 127 | 330.2 | 141.8 | 138.1
210 | 128 | 329.6 | 142.6 | 138.9
211 | 129 | 329 | 143.4 | 139.7
212 | 130 | 328.4 | 144.2 | 140.5
213 | 131 | 327.8 | 145 | 141.3
214 | 132 | 327.2 | 145.8 | 142.2
215 | 133 | 326.6 | 146.5 | 143
216 | 134 | 326.1 | 147.3 | 143.7
217 | 135 | 325.6 | 148 | 144.5
218 | 136 | 325 | 148.8 | 145.3
219 | 137 | 324.5 | 149.5 | 146
220 | 138 | 323.9 | 150.3 | 146.5
221 | 139 | 323.3 | 151 | 147.2
222 | 140 | 322.7 | 151.7 | 147.9
223 | 141 | 322 | 152.3 | 148.7
224 | 142 | 321.5 | 153 | 149.4
225 | 143 | 320.9 | 153.7 | 150.1
226 | 144 | 320.4 | 154.4 | 150.7
227 | 145 | 319.9 | 155.1 | 151.4
228 | 146 | 319.4 | 155.8 | 152.1
229 | 147 | 318.9 | 156.4 | 152.8
230 | 148 | 318.4 | 157.1 | 153.5
231 | 149 | 318 | 157.8 | 154.2
232 | 150 | 317.6 | 158.5 | 154.8
233 | 151 | 317.2 | 159.1 | 155.5
234 | 152 | 316.8 | 159.8 | 156.2
235 | 153 | 316.6 | 160.5 | 156.8
236 | 154 | 316.3 | 161.2 | 157.3
237 | 155 | 316.1 | 161.9 | 157.9
238 | 156 | 316.1 | 162.6 | 158.6
239 | 157 | 316.1 | 163.2 | 159.2
240 | 158 | 316.1 | 163.9 | 159.8
241 | 159 | 316.1 | 164.6 | 160.4
242 | 160 | 316.3 | 165.3 | 161
243 | 161 | 316.5 | 166 | 161.7
244 | 162 | 316.8 | 166.7 | 162.3
245 | 163 | 317.1 | 167.4 | 163
246 | 164 | 317.4 | 168.1 | 163.7
247 | 165 | 317.8 | 168.8 | 164.4
248 | 166 | 318.2 | 169.5 | 165.1
249 | 167 | 318.6 | 170.2 | 165.8
250 | 168 | 319.1 | 170.9 | 166.5
251 | 169 | 319.5 | 171.6 | 167.2
252 | 170 | 319.9 | 172.3 | 167.9
253 | 171 | 320.4 | 172.9 | 168.6
254 | 172 | 320.9 | 173.6 | 169.3
255 | 173 | 321.4 | 174.3 | 170
256 | 174 | 321.9 | 175 | 170.7
257 | 175 | 322.3 | 175.7 | 171.4
258 | 176 | 322.8 | 176.4 | 172.1
259 | 177 | 323.3 | 177.1 | 172.9
260 | 178 | 323.7 | 177.8 | 173.6
261 | 179 | 324 | 178.4 | 174.3
262 | 180 | 324.4 | 179.1 | 175.1
263 | 181 | 324.8 | 179.8 | 175.7
264 | 182 | 325.1 | 180.5 | 176.5
265 | 183 | 325.3 | 181.1 | 177.1
266 | 184 | 325.6 | 181.8 | 177.8
267 | 185 | 325.9 | 182.5 | 178.5
268 | 186 | 326.1 | 183.1 | 179.1
269 | 187 | 326.3 | 183.8 | 179.8
270 | 188 | 326.5 | 184.5 | 180.4
271 | 189 | 326.7 | 185.1 | 181.1
272 | 190 | 326.8 | 185.7 | 181.7
273 | 191 | 326.9 | 186.4 | 182.4
274 | 192 | 326.8 | 187 | 183
275 | 193 | 326.9 | 187.7 | 183.7
276 | 194 | 326.9 | 188.3 | 184.3
277 | 195 | 326.9 | 188.9 | 184.9
278 | 196 | 326.9 | 189.5 | 185.6
279 | 197 | 326.9 | 190.2 | 186.2
280 | 198 | 326.9 | 190.8 | 186.8
281 | 199 | 326.9 | 191.5 | 187.4
282 | 200 | 327 | 192.1 | 188.1
283 | 201 | 326.8 | 192.7 | 188.7
284 | 202 | 326.7 | 193.4 | 189.3
285 | 203 | 326.7 | 194 | 189.9
286 | 204 | 326.6 | 194.7 | 190.5
287 | 205 | 326.5 | 197.6 | 191.1
288 | 206 | 326.5 | 200.1 | 191.7
289 | 207 | 326.4 | 201.3 | 192.3
290 | 208 | 326.3 | 202.1 | 192.9
291 | 209 | 326.2 | 202.7 | 193.5
292 | 210 | 326.1 | 203.1 | 194.1
293 | 211 | 326.1 | 203.5 | 194.6
294 | 212 | 326.1 | 203.9 | 195.2
295 | 213 | 326 | 204.2 | 195.8
296 | 214 | 326 | 204.6 | 196.4
297 | 215 | 326 | 205 | 197
298 | 216 | 326 | 205.4 | 197.5
299 | 217 | 325.9 | 205.8 | 198
300 | 218 | 325.9 | 206.2 | 198.6
301 | 219 | 325.8 | 206.6 | 199.2
302 | 220 | 325.7 | 207 | 199.7
303 | 221 | 325.6 | 207.5 | 200.3
304 | 222 | 325.5 | 207.9 | 200.8
305 | 223 | 325.5 | 208.3 | 201.4
306 | 224 | 325.4 | 208.7 | 201.9
307 | 225 | 325.4 | 209.2 | 202.5
308 | 226 | 325.4 | 209.6 | 203
309 | 227 | 325.4 | 210 | 203.5
310 | 228 | 325.3 | 210.5 | 204.1
311 | 229 | 325.3 | 210.9 | 204.6
312 | 230 | 325.3 | 211.3 | 205.2
313 | 231 | 325.2 | 211.8 | 205.7
314 | 232 | 325.3 | 212.2 | 206.2
315 | 233 | 325.3 | 212.7 | 206.8
316 | 234 | 325.4 | 213.1 | 207.3
317 | 235 | 325.3 | 213.5 | 207.8
318 | 236 | 325.2 | 214 | 208.3
319 | 237 | 325.1 | 214.4 | 208.8
320 | 238 | 325.1 | 214.9 | 209.3
321 | 239 | 325 | 215.4 | 209.8
322 | 240 | 325 | 215.8 | 210.3
323 | 241 | 325 | 216.3 | 210.9
324 | 242 | 325 | 216.8 | 211.4
325 | 243 | 325 | 217.2 | 211.9
326 | 244 | 325.1 | 217.7 | 212.4
327 | 245 | 325.1 | 218.2 | 212.8
328 | 246 | 325.1 | 218.7 | 213.3
329 | 247 | 325.2 | 219.3 | 213.9
330 | 248 | 325.1 | 219.8 | 214.3
331 | 249 | 325.1 | 220.3 | 214.8
332 | 250 | 325.2 | 220.8 | 215.3
333 | 251 | 325.3 | 221.3 | 215.8
334 | 252 | 325.2 | 221.8 | 216.3
335 | 253 | 325.3 | 222.3 | 216.7
336 | 254 | 325.3 | 222.8 | 217.2
337 | 255 | 325.3 | 223.3 | 217.7
338 | 256 | 325.3 | 223.7 | 218.2
339 | 257 | 325.3 | 224.2 | 218.6
340 | 258 | 325.3 | 224.7 | 219.1 | Time of first failure
341 | 259 | 325.3 | 225.2 | 219.5 | 258 | 0
342 | 260 | 325.4 | 225.6 | 220 | 258 | 900
343 | 261 | 325.4 | 226.1 | 220.5
344 | 262 | 325.4 | 226.5 | 220.9
345 | 263 | 325.4 | 227 | 221.4
346 | 264 | 325.3 | 227.4 | 221.8
347 | 265 | 325.3 | 227.9 | 222.2
348 | 266 | 325.3 | 228.4 | 222.7
349 | 267 | 325.3 | 228.8 | 223.1
350 | 268 | 325.3 | 229.3 | 223.5
351 | 269 | 325.2 | 229.8 | 224
352 | 270 | 325.2 | 230.3 | 224.4
353 | 271 | 325 | 230.8 | 224.8
354 | 272 | 324.9 | 231.3 | 225.1
355 | 273 | 324.9 | 231.8 | 225.6
356 | 274 | 324.8 | 232.3 | 226
357 | 275 | 324.8 | 232.8 | 226.5
358 | 276 | 324.8 | 233.3 | 226.9
359 | 277 | 324.7 | 233.8 | 227.3
360 | 278 | 324.6 | 234.3 | 227.7
361 | 279 | 324.6 | 234.8 | 228.1
362 | 280 | 324.5 | 235.3 | 228.5
363 | 281 | 324.4 | 235.8 | 228.9
364 | 282 | 324.3 | 236.3 | 229.3
365 | 283 | 324.3 | 236.8 | 229.7
366 | 284 | 324.3 | 237.2 | 230.1
367 | 285 | 324.3 | 237.7 | 230.5
368 | 286 | 324.3 | 238.2 | 230.9
369 | 287 | 324.2 | 238.7 | 231.2
370 | 288 | 324.1 | 239.1 | 231.6
371 | 289 | 324.1 | 239.6 | 232
372 | 290 | 324 | 240.1 | 232.3
373 | 291 | 324 | 240.5 | 232.7
374 | 292 | 324 | 240.9 | 233.1
375 | 293 | 324 | 241.4 | 233.4
376 | 294 | 324.1 | 241.8 | 233.8
377 | 295 | 324.1 | 242.3 | 234.1
378 | 296 | 324.1 | 242.7 | 234.6
379 | 297 | 324.1 | 243.1 | 234.9
380 | 298 | 324 | 243.5 | 235.3
381 | 299 | 323.9 | 243.9 | 235.6
382 | 300 | 323.6 | 244.8 | 235.3
383 | 301 | 323.9 | 244.8 | 236.2
384 | 302 | 324 | 245.2 | 236.5
385 | 303 | 324.1 | 245.5 | 237.1
386 | 304 | 324 | 245.9 | 237.4
387 | 305 | 324 | 246.3 | 237.8
388 | 306 | 324.1 | 246.8 | 238.1
389 | 307 | 324.1 | 247.2 | 238.5
390 | 308 | 324.1 | 247.5 | 238.8
391 | 309 | 324.1 | 247.9 | 239.1
392 | 310 | 324.1 | 248.3 | 239.5
393 | 311 | 324.1 | 248.7 | 239.8
394 | 312 | 324.2 | 249.1 | 240.1
395 | 313 | 324.2 | 249.5 | 240.5
396 | 314 | 324.2 | 249.9 | 240.8
397 | 315 | 324.3 | 250.3 | 241.1
398 | 316 | 324.3 | 250.7 | 241.4
399 | 317 | 324.3 | 251.1 | 241.7
400 | 318 | 324.3 | 251.5 | 242.1
401 | 319 | 324.2 | 251.8 | 242.4
402 | 320 | 324.2 | 252.2 | 242.7
403 | 321 | 324.1 | 252.7 | 243
404 | 322 | 324.1 | 253 | 243.3
405 | 323 | 324.1 | 253.4 | 243.7
406 | 324 | 324 | 253.8 | 244
407 | 325 | 324 | 254.2 | 244.3
408 | 326 | 323.9 | 254.5 | 244.6
409 | 327 | 323.8 | 254.9 | 244.9
410 | 328 | 323.8 | 255.3 | 245.2
411 | 329 | 323.8 | 255.6 | 245.4
412 | 330 | 323.8 | 255.9 | 245.8
413 | 331 | 323.7 | 256.3 | 246.1
414 | 332 | 323.7 | 256.7 | 246.4
415 | 333 | 323.7 | 257.1 | 246.6
416 | 334 | 323.6 | 257.5 | 246.9
417 | 335 | 323.6 | 257.9 | 247.2
418 | 336 | 323.6 | 258.3 | 247.5
419 | 337 | 323.6 | 258.6 | 247.7
420 | 338 | 323.5 | 259 | 248
421 | 339 | 323.5 | 259.4 | 248.3
422 | 340 | 323.4 | 259.8 | 248.6
423 | 341 | 323.4 | 260.2 | 248.9
424 | 342 | 323.3 | 260.6 | 249.1
425 | 343 | 323.3 | 261 | 249.4
426 | 344 | 323.3 | 261.4 | 249.7
427 | 345 | 323.2 | 261.8 | 249.9
428 | 346 | 323.2 | 262.2 | 250.2
429 | 347 | 323.3 | 262.6 | 250.5
430 | 348 | 323.3 | 263 | 250.7
431 | 349 | 323.2 | 263.4 | 251
432 | 350 | 323.2 | 263.8 | 251.2
433 | 351 | 323.1 | 264.2 | 251.5
434 | 352 | 323.1 | 264.5 | 251.8
435 | 353 | 323.2 | 264.9 | 252
436 | 354 | 323.2 | 265.3 | 252.3
437 | 355 | 323.2 | 265.6 | 252.5
438 | 356 | 323.3 | 266 | 252.8
439 | 357 | 323.4 | 266.3 | 253
440 | 358 | 323.5 | 266.7 | 253.3
441 | 359 | 323.5 | 267 | 253.6
442 | 360 | 323.6 | 267.3 | 253.8
443 | 361 | 323.6 | 267.7 | 254
444 | 362 | 323.6 | 268 | 254.3
445 | 363 | 323.6 | 268.3 | 254.6
446 | 364 | 323.6 | 268.6 | 254.8
447 | 365 | 323.7 | 268.9 | 255
448 | 366 | 323.6 | 269.3 | 255.3
449 | 367 | 323.6 | 269.6 | 255.5
450 | 368 | 323.7 | 269.9 | 255.7
451 | 369 | 323.7 | 270.2 | 256
452 | 370 | 323.7 | 270.4 | 256.2
453 | 371 | 323.7 | 270.7 | 256.4
454 | 372 | 323.7 | 271 | 256.6
455 | 373 | 323.6 | 271.4 | 256.3
456 | 374 | 323.7 | 271.6 | 256.8
457 | 375 | 323.7 | 271.9 | 256.9
458 | 376 | 323.7 | 272.2 | 256.9
459 | 377 | 323.7 | 272.6 | 256.8
460 | 378 | 323.7 | 272.8 | 257.1
461 | 379 | 323.7 | 273 | 257.7
462 | 380 | 323.8 | 273.2 | 258.4
463 | 381 | 323.8 | 273.6 | 258.5
464 | 382 | 323.8 | 273.9 | 258.8
465 | 383 | 323.8 | 274.2 | 259
466 | 384 | 323.8 | 274.5 | 259.2
467 | 385 | 323.8 | 274.8 | 259.5
468 | 386 | 323.8 | 275.2 | 259.7
469 | 387 | 323.7 | 275.5 | 259.9
470 | 388 | 323.6 | 275.8 | 260.1
471 | 389 | 323.5 | 276.1 | 260.2
472 | 390 | 323.4 | 276.4 | 260.4
473 | 391 | 323.4 | 276.7 | 260.6
474 | 392 | 323.3 | 277 | 260.8
475 | 393 | 323.3 | 277.3 | 261
476 | 394 | 323.2 | 277.6 | 261.2
477 | 395 | 323.1 | 277.9 | 261.4
478 | 396 | 323.1 | 278.2 | 261.7
479 | 397 | 323.1 | 278.5 | 261.8
480 | 398 | 323.1 | 278.8 | 262
481 | 399 | 323.1 | 279.1 | 262.1
482 | 400 | 323.2 | 279.4 | 262.4
483 | 401 | 323.1 | 279.7 | 262.6
484 | 402 | 323.1 | 280 | 262.8
485 | 403 | 323.1 | 280.2 | 263
486 | 404 | 323.1 | 280.5 | 263.2
487 | 405 | 323.1 | 280.8 | 263.3
488 | 406 | 323.1 | 281.1 | 263.5
489 | 407 | 323.1 | 281.3 | 263.7
490 | 408 | 323 | 281.7 | 263.5
491 | 409 | 323 | 281.9 | 263.7
492 | 410 | 323 | 282.2 | 263.9
493 | 411 | 322.8 | 282.6 | 263.4
494 | 412 | 322.8 | 282.9 | 263.3
495 | 413 | 322.8 | 283.1 | 264
496 | 414 | 322.9 | 283.2 | 264.6
497 | 415 | 323 | 283.4 | 265.1
498 | 416 | 323 | 283.7 | 265.3
499 | 417 | 322.9 | 283.9 | 265.4
500 | 418 | 322.8 | 284.2 | 265.6
501 | 419 | 322.7 | 284.4 | 265.7
502 | 420 | 322.6 | 284.7 | 265.9
503 | 421 | 322.5 | 284.9 | 266.1
504 | 422 | 322.4 | 285.1 | 266.2
505 | 423 | 322.4 | 285.4 | 266.4
506 | 424 | 322.4 | 285.6 | 266.5
507 | 425 | 322.5 | 285.9 | 266.7
508 | 426 | 322.4 | 286.2 | 266.2
509 | 427 | 322.4 | 286.3 | 267
510 | 428 | 322.5 | 286.6 | 267.2
511 | 429 | 322.3 | 287 | 266.1
512 | 430 | 322.4 | 287.1 | 266.8
513 | 431 | 322.6 | 287.2 | 267.7
514 | 432 | 322.6 | 287.5 | 267.8
515 | 433 | 322.6 | 287.7 | 268
516 | 434 | 322.6 | 287.9 | 268.2
517 | 435 | 322.6 | 288.1 | 268.3
518 | 436 | 322.6 | 288.3 | 268.5
519 | 437 | 322.6 | 288.5 | 268.6
520 | 438 | 322.5 | 288.7 | 268.7
521 | 439 | 322.5 | 288.9 | 268.9
522 | 440 | 322.5 | 289.1 | 269.1
523 | 441 | 322.5 | 289.3 | 269.2
524 | 442 | 322.5 | 289.5 | 269.4
525 | 443 | 322.5 | 289.6 | 269.5
526 | 444 | 322.5 | 289.7 | 269.6
527 | 445 | 322.5 | 289.9 | 269.8
528 | 446 | 322.4 | 290 | 269.9
529 | 447 | 322.4 | 290.1 | 270.1
530 | 448 | 322.4 | 290.2 | 270.2
531 | 449 | 322.5 | 290.4 | 270.4
532 | 450 | 322.6 | 290.5 | 270.5
533 | 451 | 322.6 | 290.6 | 270.6
534 | 452 | 322.6 | 290.7 | 270.8
535 | 453 | 322.6 | 290.8 | 270.9
536 | 454 | 322.6 | 290.9 | 271.1
537 | 455 | 322.5 | 291 | 271.2
538 | 456 | 322.5 | 291.1 | 271.3
539 | 457 | 322.5 | 291.2 | 271.5
540 | 458 | 322.5 | 291.3 | 271.6
541 | 459 | 322.4 | 291.4 | 271.7
542 | 460 | 322.4 | 291.5 | 271.9
543 | 461 | 322.4 | 291.6 | 272
544 | 462 | 322.4 | 291.6 | 272.1
545 | 463 | 322.4 | 291.7 | 272.2
546 | 464 | 322.4 | 291.8 | 272.4
547 | 465 | 322.4 | 291.9 | 272.5
548 | 466 | 322.4 | 291.9 | 272.6
549 | 467 | 322.4 | 292 | 272.8
550 | 468 | 322.3 | 292 | 272.9
551 | 469 | 322.4 | 292.1 | 273
552 | 470 | 322.4 | 292.1 | 273.2
553 | 471 | 322.4 | 292.2 | 273.3
554 | 472 | 322.4 | 292.3 | 273.4
555 | 473 | 322.5 | 292.3 | 273.6
556 | 474 | 322.5 | 292.4 | 273.7
557 | 475 | 322.6 | 292.5 | 273.9
558 | 476 | 322.6 | 292.5 | 274
559 | 477 | 322.6 | 292.6 | 274.1
560 | 478 | 322.6 | 292.6 | 274.2
561 | 479 | 322.6 | 292.7 | 274.3
562 | 480 | 322.6 | 292.7 | 274.4
563 | 481 | 322.7 | 292.7 | 274.5
564 | 482 | 322.7 | 292.8 | 274.7
565 | 483 | 322.7 | 292.8 | 274.8
566 | 484 | 322.8 | 292.8 | 274.9
567 | 485 | 322.8 | 292.8 | 275.1
568 | 486 | 322.8 | 292.8 | 275.2
569 | 487 | 322.8 | 292.8 | 275.3
570 | 488 | 322.8 | 292.9 | 275.4
571 | 489 | 322.8 | 292.9 | 275.5
572 | 490 | 322.8 | 292.9 | 275.7
573 | 491 | 322.9 | 292.9 | 275.8
574 | 492 | 322.9 | 292.8 | 275.9
575 | 493 | 322.8 | 292.9 | 276.1
576 | 494 | 322.8 | 292.9 | 276.2
577 | 495 | 322.8 | 292.9 | 276.3
578 | 496 | 322.8 | 292.9 | 276.4
579 | 497 | 322.7 | 292.9 | 276.5
580 | 498 | 322.7 | 292.9 | 276.6
581 | 499 | 322.7 | 292.9 | 276.8
582 | 500 | 322.7 | 292.8 | 276.9
583 | 501 | 322.6 | 292.8 | 277
584 | 502 | 322.6 | 292.8 | 277.2
585 | 503 | 322.6 | 292.8 | 277.3
586 | 504 | 322.5 | 292.8 | 277.4
587 | 505 | 322.5 | 292.8 | 277.5
588 | 506 | 322.5 | 292.8 | 277.6
589 | 507 | 322.5 | 292.8 | 277.7
590 | 508 | 322.4 | 292.8 | 277.8
591 | 509 | 322.4 | 292.8 | 277.9
592 | 510 | 322.5 | 292.8 | 278
593 | 511 | 322.5 | 292.8 | 278.1
594 | 512 | 322.5 | 292.8 | 278.2
595 | 513 | 322.5 | 292.8 | 278.4
596 | 514 | 322.6 | 292.8 | 278.5
597 | 515 | 322.5 | 292.8 | 278.5
598 | 516 | 322.5 | 292.9 | 278.7
599 | 517 | 322.6 | 292.9 | 278.8
600 | 518 | 322.5 | 292.9 | 278.8
601 | 519 | 322.6 | 292.9 | 279
602 | 520 | 322.6 | 292.9 | 279.1
603 | 521 | 322.7 | 292.9 | 279.1
604 | 522 | 322.7 | 292.9 | 279.3
605 | 523 | 322.7 | 292.9 | 279.3
606 | 524 | 322.7 | 292.9 | 279.4
607 | 525 | 322.7 | 293 | 279.5
608 | 526 | 322.7 | 293 | 279.6
609 | 527 | 322.7 | 293 | 279.8
610 | 528 | 322.6 | 293 | 279.8
611 | 529 | 322.7 | 293 | 280
612 | 530 | 322.6 | 293 | 280.1
613 | 531 | 322.6 | 293.1 | 280.2
614 | 532 | 322.6 | 293.1 | 280.3
615 | 533 | 322.6 | 293.1 | 280.4
616 | 534 | 322.6 | 293.1 | 280.5
617 | 535 | 322.7 | 293.2 | 280.6
618 | 536 | 322.7 | 293.2 | 280.9
619 | 537 | 322.8 | 293.2 | 281.2
620 | 538 | 322.8 | 293.2 | 281.5
621 | 539 | 322.8 | 293.2 | 281.6
622 | 540 | 322.8 | 293.2 | 281.7
623 | 541 | 322.7 | 293.2 | 281.7
624 | 542 | 322.5 | 293.2 | 281.8
625 | 543 | 322.3 | 293.3 | 281.9
626 | 544 | 322 | 293.3 | 282
627 | 545 | 321.8 | 293.3 | 282
628 | 546 | 321.5 | 293.3 | 282.1
629 | 547 | 321.3 | 293.3 | 282.2
630 | 548 | 321 | 293.4 | 282.3
631 | 549 | 320.7 | 293.4 | 282.3
632 | 550 | 320.4 | 293.4 | 282.4
633 | 551 | 320.2 | 293.4 | 282.4
634 | 552 | 319.9 | 293.4 | 282.5
635 | 553 | 319.6 | 293.4 | 282.5
636 | 554 | 319.2 | 293.4 | 282.6
637 | 555 | 318.8 | 293.4 | 282.6
638 | 556 | 318.4 | 293.4 | 282.7
639 | 557 | 318.1 | 293.4 | 282.7
640 | 558 | 317.8 | 293.4 | 282.8
641 | 559 | 317.4 | 293.4 | 282.8
642 | 560 | 317 | 293.4 | 282.8
643 | 561 | 316.7 | 293.4 | 282.9
644 | 562 | 316.3 | 293.4 | 282.9
645 | 563 | 316 | 293.4 | 282.9
646 | 564 | 315.7 | 293.3 | 282.9
647 | 565 | 315.4 | 293.3 | 282.9
648 | 566 | 315 | 293.3 | 282.9
649 | 567 | 314.6 | 293.3 | 282.9
650 | 568 | 314.3 | 293.3 | 282.9
651 | 569 | 314 | 293.2 | 282.9
652 | 570 | 313.6 | 293.2 | 282.9
653 | 571 | 313.2 | 293.2 | 282.9
654 | 572 | 312.8 | 293.2 | 283
655 | 573 | 312.4 | 293.1 | 283
656 | 574 | 312.1 | 293.1 | 282.9
657 | 575 | 311.7 | 293.1 | 282.9
658 | 576 | 311.3 | 293 | 282.9
659 | 577 | 310.9 | 293 | 282.9
660 | 578 | 310.5 | 293 | 282.9
661 | 579 | 310.1 | 292.9 | 282.9
662 | 580 | 309.7 | 292.9 | 282.9
663 | 581 | 309.3 | 292.9 | 282.9
664 | 582 | 308.9 | 292.8 | 282.9
665 | 583 | 308.5 | 292.7 | 282.8
666 | 584 | 308.1 | 292.7 | 282.8
667 | 585 | 307.7 | 292.7 | 282.8
668 | 586 | 307.3 | 292.6 | 282.8
669 | 587 | 306.9 | 292.6 | 282.7
670 | 588 | 306.5 | 292.5 | 282.7
671 | 589 | 306.1 | 292.5 | 282.7
672 | 590 | 305.7 | 292.4 | 282.6
673 | 591 | 305.3 | 292.3 | 282.6
674 | 592 | 304.8 | 292.3 | 282.5
675 | 593 | 304.4 | 292.2 | 282.5
676 | 594 | 304.1 | 292.1 | 282.4
677 | 595 | 303.7 | 292 | 282.3
678 | 596 | 303.3 | 291.9 | 282.3
679 | 597 | 302.9 | 291.9 | 282.2
680 | 598 | 302.5 | 291.8 | 282.2
681 | 599 | 302.2 | 291.7 | 282
682 | 600 | 301.8 | 291.7 | 282
683 | 601 | 301.4 | 291.6 | 281.9
684 | 602 | 301 | 291.5 | 281.8
685 | 603 | 300.7 | 291.4 | 281.7
686 | 604 | 300.3 | 291.3 | 281.7
687 | 605 | 299.9 | 291.3 | 281.6
688 | 606 | 299.6 | 291.2 | 281.5
689 | 607 | 299.1 | 291.1 | 281.4
690 | 608 | 298.7 | 291 | 281.3
691 | 609 | 298.3 | 290.9 | 281.2
692 | 610 | 297.9 | 290.9 | 281.1
693 | 611 | 297.6 | 290.8 | 281
694 | 612 | 297.2 | 290.7 | 280.9
695 | 613 | 296.8 | 290.6 | 280.8
696 | 614 | 296.4 | 290.5 | 280.7
697 | 615 | 296.1 | 290.4 | 280.6
698 | 616 | 295.7 | 290.3 | 280.5
699 | 617 | 295.3 | 290.2 | 280.4
700 | 618 | 294.9 | 290.1 | 280.3
701 | 619 | 294.6 | 290 | 280.2
702 | 620 | 294.2 | 289.9 | 280.1
703 | 621 | 293.9 | 289.8 | 280
704 | 622 | 293.5 | 289.7 | 279.9
705 | 623 | 293.1 | 289.6 | 279.7
706 | 624 | 292.6 | 289.5 | 279.6
707 | 625 | 292.2 | 289.4 | 279.5
708 | 626 | 291.9 | 289.3 | 279.4
709 | 627 | 291.5 | 289.2 | 279.2
710 | 628 | 291.1 | 289.1 | 279.1
711 | 629 | 290.8 | 289 | 279
712 | 630 | 290.4 | 288.9 | 278.9
713 | 631 | 290 | 288.8 | 278.7
714 | 632 | 289.6 | 288.7 | 278.6
715 | 633 | 289.2 | 288.6 | 278.5
716 | 634 | 288.8 | 288.4 | 278.3
717 | 635 | 288.4 | 288.3 | 278.2
718 | 636 | 288 | 288.2 | 278
719 | 637 | 287.6 | 288.1 | 277.9
720 | 638 | 287.3 | 288 | 277.7
721 | 639 | 286.9 | 287.9 | 277.6
722 | 640 | 286.4 | 287.8 | 277.4
723 | 641 | 286.1 | 287.7 | 277.3
724 | 642 | 285.7 | 287.5 | 277.2
725 | 643 | 285.3 | 287.4 | 277
726 | 644 | 284.9 | 287.3 | 276.9
727 | 645 | 284.5 | 287.1 | 276.7
728 | 646 | 284.1 | 287 | 276.6
729 | 647 | 283.7 | 286.9 | 276.4
730 | 648 | 283.3 | 286.7 | 276.3
731 | 649 | 283 | 286.6 | 276.1
732 | 650 | 282.6 | 286.4 | 276
733 | 651 | 282.3 | 286.3 | 275.8
734 | 652 | 281.9 | 286.1 | 275.7
735 | 653 | 281.5 | 286 | 275.5
736 | 654 | 281.2 | 285.8 | 275.3
737 | 655 | 280.8 | 285.7 | 275.2
738 | 656 | 280.5 | 285.5 | 275
739 | 657 | 280.1 | 285.4 | 274.9
740 | 658 | 279.8 | 285.2 | 274.7
741 | 659 | 279.4 | 285.1 | 274.5
742 | 660 | 279.1 | 284.9 | 274.3
743 | 661 | 278.7 | 284.7 | 274.2
744 | 662 | 278.4 | 284.6 | 274
745 | 663 | 278 | 284.4 | 273.9
746 | 664 | 277.6 | 284.2 | 273.7
747 | 665 | 277.3 | 284.1 | 273.5
748 | 666 | 276.9 | 283.9 | 273.4
749 | 667 | 276.6 | 283.7 | 273.2
750 | 668 | 276.2 | 283.5 | 273
751 | 669 | 275.9 | 283.4 | 272.8
752 | 670 | 275.6 | 283.2 | 272.7
753 | 671 | 275.3 | 283 | 272.5
754 | 672 | 275 | 282.9 | 272.3
755 | 673 | 274.6 | 282.7 | 272.1
756 | 674 | 274.3 | 282.5 | 271.9
757 | 675 | 273.9 | 282.3 | 271.8
758 | 676 | 273.6 | 282.1 | 271.6
759 | 677 | 273.2 | 281.9 | 271.4
760 | 678 | 272.9 | 281.7 | 271.3
761 | 679 | 272.6 | 281.5 | 271.1
762 | 680 | 272.2 | 281.3 | 270.9
763 | 681 | 271.9 | 281.1 | 270.7
764 | 682 | 271.6 | 280.9 | 270.5
765 | 683 | 271.2 | 280.7 | 270.3
766 | 684 | 270.9 | 280.5 | 270.1
767 | 685 | 270.5 | 280.3 | 270
768 | 686 | 270.2 | 280.1 | 269.8
769 | 687 | 269.8 | 279.9 | 269.6
770 | 688 | 269.5 | 279.7 | 269.4
771 | 689 | 269.1 | 279.5 | 269.2
772 | 690 | 268.8 | 279.3 | 269
773 | 691 | 268.4 | 279.1 | 268.9
774 | 692 | 268.1 | 278.8 | 268.7
775 | 693 | 267.8 | 278.6 | 268.5
776 | 694 | 267.5 | 278.4 | 268.3
777 | 695 | 267.1 | 278.2 | 268.1
778 | 696 | 266.8 | 278 | 267.9
779 | 697 | 266.4 | 277.8 | 267.7
780 | 698 | 266.1 | 277.6 | 267.5
781 | 699 | 265.8 | 277.3 | 267.3
782 | 700 | 265.4 | 277.1 | 267.1
783 | 701 | 265.1 | 276.9 | 266.9
784 | 702 | 264.8 | 276.7 | 266.7
785 | 703 | 264.5 | 276.4 | 266.5
786 | 704 | 264.2 | 276.2 | 266.3
787 | 705 | 263.9 | 275.9 | 266.1
788 | 706 | 263.5 | 275.7 | 265.9
789 | 707 | 263.1 | 275.4 | 265.7
790 | 708 | 262.8 | 275.2 | 265.5
791 | 709 | 262.4 | 275 | 265.3
792 | 710 | 262.1 | 274.8 | 265.1
793 | 711 | 261.7 | 274.5 | 264.9
794 | 712 | 261.4 | 274.3 | 264.7
795 | 713 | 261.1 | 274.1 | 264.5
796 | 714 | 260.8 | 273.8 | 264.3
797 | 715 | 260.4 | 273.6 | 264.1
798 | 716 | 260.1 | 273.3 | 263.9
799 | 717 | 259.8 | 273.1 | 263.7
800 | 718 | 259.4 | 272.8 | 263.5
801 | 719 | 259.1 | 272.6 | 263.2
802 | 720 | 258.8 | 272.3 | 263
803 | 721 | 258.5 | 272.1 | 262.8
804 | 722 | 258.2 | 271.8 | 262.6
805 | 723 | 257.9 | 271.6 | 262.4
806 | 724 | 257.6 | 271.4 | 262.3
807 | 725 | 257.3 | 271.1 | 262
808 | 726 | 257 | 270.9 | 261.9
809 | 727 | 256.7 | 270.7 | 261.7
810 | 728 | 256.4 | 270.4 | 261.4
811 | 729 | 256.1 | 270.2 | 261.3
812 | 730 | 255.8 | 269.9 | 261
813 | 731 | 255.5 | 269.7 | 260.8
814 | 732 | 255.1 | 269.4 | 260.6
815 | 733 | 254.8 | 269.2 | 260.4
816 | 734 | 254.5 | 268.9 | 260.2
817 | 735 | 254.1 | 268.7 | 260
818 | 736 | 253.8 | 268.4 | 259.8
819 | 737 | 253.5 | 268.2 | 259.6
820 | 738 | 253.2 | 267.9 | 259.4
821 | 739 | 252.9 | 267.7 | 259.2
822 | 740 | 252.6 | 267.4 | 259
823 | 741 | 252.3 | 267.1 | 258.8
824 | 742 | 252 | 266.9 | 258.5
825 | 743 | 251.7 | 266.6 | 258.4
826 | 744 | 251.4 | 266.3 | 258.1
827 | 745 | 251.1 | 266 | 257.9
828 | 746 | 250.7 | 265.8 | 257.7
829 | 747 | 250.5 | 265.5 | 257.5
830 | 748 | 250.2 | 265.2 | 257.3
831 | 749 | 249.9 | 265 | 257.1
832 | 750 | 249.6 | 264.7 | 256.9
833 | 751 | 249.3 | 264.4 | 256.7
834 | 752 | 249 | 264.2 | 256.5
835 | 753 | 248.7 | 263.9 | 256.2
836 | 754 | 248.4 | 263.7 | 256
837 | 755 | 248.1 | 263.4 | 255.8
838 | 756 | 247.8 | 263.2 | 255.6
839 | 757 | 247.6 | 262.9 | 255.4
840 | 758 | 247.3 | 262.6 | 255.2
841 | 759 | 247 | 262.4 | 255
842 | 760 | 246.7 | 262.1 | 254.8
843 | 761 | 246.4 | 261.8 | 254.6
844 | 762 | 246.1 | 261.5 | 254.4
845 | 763 | 245.8 | 261.3 | 254.2
846 | 764 | 245.5 | 261 | 254
847 | 765 | 245.2 | 260.7 | 253.8
848 | 766 | 244.9 | 260.4 | 253.5
849 | 767 | 244.6 | 260.2 | 253.4
850 | 768 | 244.3 | 259.9 | 253.2
851 | 769 | 244 | 259.6 | 252.9
852 | 770 | 243.7 | 259.4 | 252.7
853 | 771 | 243.5 | 259.1 | 252.5
854 | 772 | 243.2 | 258.8 | 252.3
855 | 773 | 242.9 | 258.5 | 252.1
856 | 774 | 242.7 | 258.3 | 251.9
857 | 775 | 242.4 | 258 | 251.7
858 | 776 | 242.1 | 257.7 | 251.5
859 | 777 | 241.8 | 257.4 | 251.3
860 | 778 | 241.5 | 257.1 | 251.1
861 | 779 | 241.3 | 256.8 | 250.9
862 | 780 | 241 | 256.5 | 250.6
863 | 781 | 240.7 | 256.3 | 250.5
864 | 782 | 240.5 | 256 | 250.2
865 | 783 | 240.2 | 255.7 | 250
866 | 784 | 240 | 255.5 | 249.8
867 | 785 | 239.7 | 255.2 | 249.6
868 | 786 | 239.5 | 254.9 | 249.4
869 | 787 | 239.2 | 254.6 | 249.2
870 | 788 | 238.9 | 254.4 | 248.9
871 | 789 | 238.6 | 254.1 | 248.8
872 | 790 | 238.3 | 253.8 | 248.5
873 | 791 | 238 | 253.6 | 248.3
874 | 792 | 237.8 | 253.3 | 248.1
875 | 793 | 237.5 | 253 | 247.9
876 | 794 | 237.2 | 252.8 | 247.7
877 | 795 | 236.9 | 252.5 | 247.5
878 | 796 | 236.7 | 252.2 | 247.3
879 | 797 | 236.4 | 252 | 247.1
880 | 798 | 236.1 | 251.7 | 246.9
881 | 799 | 235.9 | 251.4 | 246.7
882 | 800 | 235.6 | 251.2 | 246.4
883 | 801 | 235.3 | 250.9 | 246.2
884 | 802 | 235 | 250.7 | 246
885 | 803 | 234.8 | 250.4 | 245.8
886 | 804 | 234.5 | 250.2 | 245.5
887 | 805 | 234.3 | 250 | 245.4
888 | 806 | 234 | 249.7 | 245.2
889 | 807 | 233.8 | 249.5 | 245
890 | 808 | 233.5 | 249.2 | 244.7
891 | 809 | 233.2 | 249 | 244.5
892 | 810 | 233 | 248.8 | 244.3
893 | 811 | 232.7 | 248.5 | 244.1
894 | 812 | 232.4 | 248.3 | 243.9
895 | 813 | 232.1 | 248 | 243.7
896 | 814 | 231.9 | 247.8 | 243.4
897 | 815 | 231.6 | 247.6 | 243.2
898 | 816 | 231.3 | 247.3 | 243
899 | 817 | 231 | 247.1 | 242.8
900 | 818 | 230.7 | 246.8 | 242.6
901 | 819 | 230.4 | 246.6 | 242.4
902 | 820 | 230.2 | 246.3 | 242.2
903 | 821 | 229.9 | 246.1 | 242
904 | 822 | 229.6 | 245.8 | 241.8
905 | 823 | 229.3 | 245.6 | 241.6
906 | 824 | 229.1 | 245.3 | 241.4
907 | 825 | 228.9 | 245.1 | 241.2
908 | 826 | 228.6 | 244.8 | 241
909 | 827 | 228.4 | 244.6 | 240.8
910 | 828 | 228.2 | 244.3 | 240.6

## C2-3
Penlight Test 65 |  |  | 2006-08-29 | 11:06 |  | Vs = |  | 157.4103 |  | R = | 100
PVC | 2-C & Shield | Tray
325 C | 7.2 kW/m2 |  | Conductors | 2 & 3
Time-5 | N11 | N12 | Time-6 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
38958.4619 | 1 | 0 | 38958.4619 | 1 | 0 | -75 | 7 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38958.462 | 1 | 0 | 38958.462 | 1 | 0 | -66.5 | 15.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38958.4621 | 1 | 0 | 38958.4621 | 1 | 0 | -58 | 24 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38958.4622 | 1 | 0 | 38958.4622 | 1 | 0 | -49.5 | 32.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38958.4623 | 1 | 0 | 38958.4623 | 1 | 0 | -41.5 | 40.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38958.4624 | 1 | 0 | 38958.4624 | 1 | 0 | -33 | 49 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38958.4625 | 1 | 0 | 38958.4625 | 1 | 0 | -24.5 | 57.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38958.4626 | 1 | 0 | 38958.4626 | 1 | 0 | -16 | 66 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38958.4627 | 1 | 0 | 38958.4627 | 1 | 0 | -7.5 | 74.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38958.4628 | 1 | 0 | 38958.4628 | 1 | 0 | 0.5 | 82.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38958.4629 | 1 | 0 | 38958.4629 | 1 | 0 | 9 | 91 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38958.463 | 1 | 0 | 38958.463 | 1 | 0 | 17.5 | 99.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38958.4631 | 1 | 0 | 38958.4631 | 1 | 0 | 26 | 108 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38958.4632 | 1 | 0 | 38958.4632 | 1 | 0 | 34.5 | 116.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38958.4633 | 1 | 0 | 38958.4633 | 1 | 0 | 42.5 | 124.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38958.4634 | 1 | 0 | 38958.4634 | 1 | 0 | 51 | 133 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38958.4635 | 1 | 0 | 38958.4635 | 1 | 0 | 59.5 | 141.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38958.4636 | 1 | 0 | 38958.4636 | 1 | 0 | 68 | 150 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38958.4637 | 1 | 0 | 38958.4637 | 1 | 0 | 76.5 | 158.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38958.4638 | 1 | 0 | 38958.4638 | 1 | 0 | 84.5 | 166.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38958.4639 | 1 | 0 | 38958.4639 | 1 | 0 | 93 | 175 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38958.464 | 1 | 0 | 38958.464 | 1 | 0 | 101.5 | 183.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38958.4641 | 1 | 0 | 38958.4641 | 1 | 0 | 110 | 192 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38958.4642 | 1 | 0 | 38958.4642 | 1 | 0 | 118.5 | 200.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38958.4642 | 1 | 0 | 38958.4643 | 1 | 0 | 126.5 | 208.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38958.4643 | 1 | 0 | 38958.4644 | 1 | 0 | 135 | 217 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38958.4644 | 1 | 0 | 38958.4645 | 1 | 0 | 143.5 | 225.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38958.4645 | 1 | 0 | 38958.4646 | 1 | 0 | 152 | 234 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38958.4646 | 1 | 0 | 38958.4647 | 1 | 0 | 160 | 242 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38958.4647 | 1 | 0 | 38958.4647 | 1 | 0 | 168.5 | 250.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38958.4648 | 1 | 0 | 38958.4648 | 1 | 0 | 177 | 259 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38958.4649 | 1 | 0 | 38958.4649 | 1 | 0 | 185.5 | 267.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38958.465 | 1 | 0 | 38958.465 | 1 | 0 | 194 | 276 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38958.4651 | 1 | 0 | 38958.4651 | 1 | 0 | 202.5 | 284.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38958.4652 | 1 | 0 | 38958.4652 | 1 | 0 | 210.5 | 292.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38958.4653 | 1 | 0 | 38958.4653 | 1 | 0 | 219 | 301 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38958.4654 | 1 | 0 | 38958.4654 | 1 | 0 | 227.5 | 309.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38958.4655 | 1 | 0 | 38958.4655 | 1 | 0 | 235.5 | 317.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38958.4656 | 1 | 0 | 38958.4656 | 1 | 0 | 244.5 | 326.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38958.4657 | 1 | 0 | 38958.4657 | 1 | 0 | 252.5 | 334.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38958.4658 | 1 | 3 | 38958.4658 | 1 | 1 | 261 | 343 | 0.06105 | 0.18315 | 0.06105 | 0.06105 | 0.0006105 | 0.0018315 | 0.0006105 | 0.0006105 | 0.001221 | 0 | 128868.9418 | 332144233.1417 | 85812.6408
38958.4659 | 920 | 955 | 38958.4659 | 2 | 3 | 269.5 | 351.5 | 56.1661 | 58.3028 | 0.1221 | 0.18315 | 0.56166 | 0.58303 | 0.001221 | 0.0018315 | 0.021368 | 0.0006105 | 4785.7357 | 274868.4845 | 73.6256
38958.466 | 1 | 0 | 38958.466 | 1 | 0 | 278 | 360 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
38958.4661 | 2 | 4 | 38958.4661 | 1 | 1 | 286.5 | 368.5 | 0.1221 | 0.2442 | 0.06105 | 0.06105 | 0.001221 | 0.002442 | 0.0006105 | 0.0006105 | 0.001221 | 0 | 128818.9224 | 332015314.211 | 64309.4806
38958.4662 | 1087 | 1142 | 38958.4662 | 1127 | 1176 | 294.5 | 376.5 | 66.3614 | 69.7192 | 68.8034 | 71.7949 | 0.66361 | 0.69719 | 0.68803 | 0.71795 | 0.033578 | 0.029915 | 3442.1424 | 9783.3327 | 30.2841
38958.4663 | 1072 | 1050 | 38958.4663 | 952 | 991 | 303 | 385 | 65.4457 | 64.1026 | 58.1197 | 60.5006 | 0.65446 | 0.64103 | 0.5812 | 0.60501 | 0.013431 | 0.02381 | 27262.9488 | 6373.4377 | 42.7933
38958.4664 | 966 | 944 | 38958.4664 | 1049 | 1026 | 311.5 | 393.5 | 58.9744 | 57.6313 | 64.0415 | 62.6374 | 0.58974 | 0.57631 | 0.64042 | 0.62637 | 0.013431 | 0.014042 | 12546.9462 | 10317.8154 | 70.1233
38958.4665 | 1060 | 1147 | 38958.4665 | 947 | 926 | 319.5 | 401.5 | 64.7131 | 70.0244 | 57.8144 | 56.5324 | 0.64713 | 0.70024 | 0.57814 | 0.56532 | 0.053114 | 0.012821 | 1200.6925 | 2906.8374 | 31.3016
38958.4666 | 1090 | 1067 | 38958.4666 | 1189 | 1178 | 328 | 410 | 66.5446 | 65.1404 | 72.5885 | 71.917 | 0.66545 | 0.6514 | 0.72589 | 0.71917 | 0.014042 | 0.0067155 | 4011.1273 | 7564.0088 | 38.9767
38958.4667 | 1155 | 1133 | 38958.4667 | 1090 | 1069 | 336.5 | 418.5 | 70.5128 | 69.1697 | 66.5446 | 65.2625 | 0.70513 | 0.6917 | 0.66545 | 0.65263 | 0.013431 | 0.012821 | 10136.4857 | 14237.5047 | 25.4505
38958.4668 | 1041 | 1019 | 38958.4668 | 1185 | 1167 | 345 | 427 | 63.5531 | 62.21 | 72.3443 | 71.2454 | 0.63553 | 0.6221 | 0.72344 | 0.71245 | 0.013431 | 0.010989 | 7740.0396 | 47676.7297 | 50.765
38958.4669 | 1179 | 1130 | 38958.4669 | 948 | 925 | 353.5 | 435.5 | 71.978 | 68.9866 | 57.8755 | 56.4713 | 0.71978 | 0.68987 | 0.57875 | 0.56471 | 0.029915 | 0.014042 | 2293.6972 | 9408.9862 | 23.5882
38958.467 | 1006 | 983 | 38958.467 | 1156 | 1135 | 362 | 444 | 61.4164 | 60.0122 | 70.5739 | 69.2918 | 0.61416 | 0.60012 | 0.70574 | 0.69292 | 0.014042 | 0.012821 | 9284.6339 | 16208.5337 | 59.5896
38958.4671 | 1897 | 1065 | 38958.4671 | 2197 | 678 | 370.5 | 452.5 | 115.812 | 65.0183 | 134.127 | 41.3919 | 1.1581 | 0.65018 | 1.3413 | 0.41392 | 0.50794 | 0.92735 | 35.5426 | 98.1494 | 17.8421
38958.4672 | 2492 | 4 | 38958.4672 | 1987 | 4 | 378.5 | 460.5 | 152.1368 | 0.2442 | 121.3065 | 0.2442 | 1.5214 | 0.002442 | 1.2131 | 0.002442 | 1.5189 | 1.2106 | 3.4896 | 31.6521 | 495.1501
38958.4673 | 1989 | 4 | 38958.4673 | 1972 | 3 | 387 | 469 | 121.4286 | 0.2442 | 120.3907 | 0.18315 | 1.2143 | 0.002442 | 1.2039 | 0.0018315 | 1.2118 | 1.2021 | 29.8862 | 30.9541 | 3459.2145
38958.4674 | 2025 | 2 | 38958.4674 | 2475 | 3 | 395.5 | 477.5 | 123.6264 | 0.1221 | 151.0989 | 0.18315 | 1.2363 | 0.001221 | 1.511 | 0.0018315 | 1.235 | 1.5092 | 28.0138 | 4.2002 | 1111.2861
38958.4675 | 2538 | 2 | 38958.4675 | 2524 | 3 | 404 | 486 | 154.9451 | 0.1221 | 154.0904 | 0.18315 | 1.5495 | 0.001221 | 1.5409 | 0.0018315 | 1.5482 | 1.5391 | 1.6482 | 2.3249 | 43.602
38958.4676 | 974 | 924 | 38958.4676 | 2182 | 3 | 412.5 | 494.5 | 59.4628 | 56.4103 | 133.2112 | 0.18315 | 0.59463 | 0.5641 | 1.3321 | 0.0018315 | 0.030525 | 1.3303 | 31.7606 | 18.4745 | 11.4823
38958.4677 | 2415 | 2 | 38958.4677 | 2371 | 2 | 420.5 | 502.5 | 147.4359 | 0.1221 | 144.7497 | 0.1221 | 1.4744 | 0.001221 | 1.4475 | 0.001221 | 1.4731 | 1.4463 | 6.8347 | 8.8634 | 656.9579
38958.4677 | 2534 | 7 | 38958.4678 | 2400 | 3 | 429 | 511 | 154.7009 | 0.42735 | 146.5201 | 0.18315 | 1.547 | 0.0042735 | 1.4652 | 0.0018315 | 1.5427 | 1.4634 | 1.8193 | 7.9916 | 39.517
38958.4678 | 2027 | 1 | 38958.4679 | 2008 | 1 | 437.5 | 519.5 | 123.7485 | 0.06105 | 122.5885 | 0.06105 | 1.2375 | 0.0006105 | 1.2259 | 0.0006105 | 1.2369 | 1.2253 | 27.2625 | 28.4716 | 12197.3923
38958.4679 | 2140 | 1 | 38958.468 | 2403 | 1 | 445.5 | 527.5 | 130.6471 | 0.06105 | 146.7033 | 0.06105 | 1.3065 | 0.0006105 | 1.467 | 0.0006105 | 1.3059 | 1.4664 | 20.6264 | 7.3162 | 2981.798
38958.468 | 2167 | 1 | 38958.4681 | 2116 | 1 | 454.5 | 536.5 | 132.2955 | 0.06105 | 129.1819 | 0.06105 | 1.323 | 0.0006105 | 1.2918 | 0.0006105 | 1.3223 | 1.2912 | 19.0327 | 21.9164 | 7377.2246
38958.4681 | 2316 | 1 | 38958.4681 | 2179 | 1 | 462.5 | 544.5 | 141.3919 | 0.06105 | 133.0281 | 0.06105 | 1.4139 | 0.0006105 | 1.3303 | 0.0006105 | 1.4133 | 1.3297 | 11.3606 | 18.4114 | 4064.1148
38958.4682 | 2358 | 1 | 38958.4683 | 2219 | 0 | 471 | 553 | 143.956 | 0.06105 | 135.4701 | 0 | 1.4396 | 0.0006105 | 1.3547 | 0 | 1.4389 | 1.3547 | 9.3746 | 16.1956 | 3057.7643
38958.4683 | 2562 | 0 | 38958.4683 | 2519 | 1 | 479.5 | 561.5 | 156.4103 | 0 | 153.7851 | 0.06105 | 1.5641 | 0 | 1.5379 | 0.0006105 | 1.5641 | 1.5372 | 0.63934 | 2.3979 | 0.92476
38958.4684 | 2545 | 1 | 38958.4684 | 2364 | 0 | 488 | 570 | 155.3724 | 0.06105 | 144.3223 | 0 | 1.5537 | 0.0006105 | 1.4432 | 0 | 1.5531 | 1.4432 | 1.3178 | 9.0685 | 269.2243
38958.4685 | 2507 | 0 | 38958.4685 | 2360 | 1 | 496 | 578 | 153.0525 | 0 | 144.0781 | 0.06105 | 1.5305 | 0 | 1.4408 | 0.0006105 | 1.5305 | 1.4402 | 2.8472 | 9.2997 | 1.3167
38958.4686 | 2025 | 0 | 38958.4686 | 2088 | 0 | 504.5 | 586.5 | 123.6264 | 0 | 127.4725 | 0 | 1.2363 | 0 | 1.2747 | 0 | 1.2363 | 1.2747 | 27.3274 | 23.4856 | 26.0911
38958.4687 | 2341 | 0 | 38958.4687 | 2488 | 1 | 513 | 595 | 142.9182 | 0 | 151.8926 | 0.06105 | 1.4292 | 0 | 1.5189 | 0.0006105 | 1.4292 | 1.5183 | 10.1401 | 3.6743 | 8.7109
38958.4688 | 2546 | 0 | 38958.4688 | 2501 | 0 | 521.5 | 603.5 | 155.4335 | 0 | 152.6862 | 0 | 1.5543 | 0 | 1.5269 | 0 | 1.5543 | 1.5269 | 1.2718 | 3.094 | 0.28254
38958.4689 | 2059 | 0 | 38958.4689 | 2523 | 0 | 529.5 | 611.5 | 125.7021 | 0 | 154.0293 | 0 | 1.257 | 0 | 1.5403 | 0 | 1.257 | 1.5403 | 25.2249 | 2.195 | 23.9678
38958.469 | 2349 | 0 | 38958.469 | 2211 | 0 | 538 | 620 | 143.4066 | 0 | 134.9817 | 0 | 1.4341 | 0 | 1.3498 | 0 | 1.4341 | 1.3498 | 9.765 | 16.616 | 8.3309
38958.4691 | 2465 | 1 | 38958.4691 | 2311 | 0 | 546.5 | 628.5 | 150.4884 | 0.06105 | 141.0867 | 0 | 1.5049 | 0.0006105 | 1.4109 | 0 | 1.5043 | 1.4109 | 4.6177 | 11.5699 | 1165.3893
38958.4692 | 2552 | 0 | 38958.4692 | 2551 | 0 | 555 | 637 | 155.7998 | 0 | 155.7387 | 0 | 1.558 | 0 | 1.5574 | 0 | 1.558 | 1.5574 | 1.0337 | 1.0733 | 0.5243
38958.4693 | 2495 | 0 | 38958.4693 | 2008 | 0 | 563.5 | 645.5 | 152.3199 | 0 | 122.5885 | 0 | 1.5232 | 0 | 1.2259 | 0 | 1.5232 | 1.2259 | 3.3419 | 28.4054 | 1.8187
38958.4694 | 2557 | 0 | 38958.4694 | 2209 | 0 | 571.5 | 653.5 | 156.105 | 0 | 134.8596 | 0 | 1.5611 | 0 | 1.3486 | 0 | 1.5611 | 1.3486 | 0.83614 | 16.7216 | 0.72491
38958.4695 | 2461 | 0 | 38958.4695 | 1990 | 0 | 580 | 662 | 150.2442 | 0 | 121.4896 | 0 | 1.5024 | 0 | 1.2149 | 0 | 1.5024 | 1.2149 | 4.7696 | 29.5668 | 3.2672
38958.4696 | 2234 | 0 | 38958.4696 | 2459 | 0 | 588.5 | 670.5 | 136.3858 | 0 | 150.1221 | 0 | 1.3639 | 0 | 1.5012 | 0 | 1.3639 | 1.5012 | 15.4154 | 4.8548 | 14.0515
38958.4697 | 2187 | 0 | 38958.4697 | 2193 | 0 | 597 | 679 | 133.5165 | 0 | 133.8828 | 0 | 1.3352 | 0 | 1.3388 | 0 | 1.3352 | 1.3388 | 17.8957 | 17.5732 | 16.5606
38958.4698 | 2055 | 0 | 38958.4698 | 2540 | 0 | 605.5 | 687.5 | 125.4579 | 0 | 155.0672 | 0 | 1.2546 | 0 | 1.5507 | 0 | 1.2546 | 1.5507 | 25.4686 | 1.511 | 24.214
38958.4699 | 2554 | 0 | 38958.4699 | 2028 | 0 | 614 | 696 | 155.9219 | 0 | 123.8095 | 0 | 1.5592 | 0 | 1.2381 | 0 | 1.5592 | 1.2381 | 0.95458 | 27.1391 | 0.60464
38958.47 | 2486 | 0 | 38958.47 | 2428 | 0 | 622 | 704 | 151.7705 | 0 | 148.2295 | 0 | 1.5177 | 0 | 1.4823 | 0 | 1.5177 | 1.4823 | 3.716 | 6.1936 | 2.1983
38958.4701 | 2367 | 0 | 38958.4701 | 2530 | 0 | 630.5 | 712.5 | 144.5055 | 0 | 154.4567 | 0 | 1.4451 | 0 | 1.5446 | 0 | 1.4451 | 1.5446 | 8.9303 | 1.9123 | 7.4852
38958.4702 | 2242 | 0 | 38958.4702 | 2133 | 0 | 639 | 721 | 136.8742 | 0 | 130.2198 | 0 | 1.3687 | 0 | 1.3022 | 0 | 1.3687 | 1.3022 | 15.0036 | 20.8805 | 13.6348
38958.4703 | 2484 | 0 | 38958.4703 | 2233 | 0 | 647.5 | 729.5 | 151.6484 | 0 | 136.3248 | 0 | 1.5165 | 0 | 1.3632 | 0 | 1.5165 | 1.3632 | 3.7995 | 15.4671 | 2.283
38958.4704 | 2179 | 0 | 38958.4704 | 2377 | 0 | 656 | 738 | 133.0281 | 0 | 145.116 | 0 | 1.3303 | 0 | 1.4512 | 0 | 1.3303 | 1.4512 | 18.3286 | 8.472 | 16.9983
38958.4705 | 2074 | 0 | 38958.4705 | 2535 | 0 | 664.5 | 746.5 | 126.6178 | 0 | 154.7619 | 0 | 1.2662 | 0 | 1.5476 | 0 | 1.2662 | 1.5476 | 24.3192 | 1.7112 | 23.053
38958.4706 | 2348 | 0 | 38958.4706 | 2071 | 0 | 672.5 | 754.5 | 143.3455 | 0 | 126.4347 | 0 | 1.4335 | 0 | 1.2643 | 0 | 1.4335 | 1.2643 | 9.8118 | 24.4993 | 8.3783
38958.4707 | 2462 | 0 | 38958.4707 | 2015 | 0 | 681 | 763 | 150.3053 | 0 | 123.0159 | 0 | 1.5031 | 0 | 1.2302 | 0 | 1.5031 | 1.2302 | 4.7271 | 27.9593 | 3.224
38958.4708 | 2492 | 0 | 38958.4708 | 1973 | 0 | 689.5 | 771.5 | 152.1368 | 0 | 120.4518 | 0 | 1.5214 | 0 | 1.2045 | 0 | 1.5214 | 1.2045 | 3.4663 | 30.6832 | 1.9449
38958.4709 | 2240 | 0 | 38958.4709 | 2487 | 0 | 697.5 | 779.5 | 136.7521 | 0 | 151.8315 | 0 | 1.3675 | 0 | 1.5183 | 0 | 1.3675 | 1.5183 | 15.1062 | 3.6743 | 13.7387
38958.471 | 2242 | 0 | 38958.471 | 2017 | 0 | 706.5 | 788.5 | 136.8742 | 0 | 123.138 | 0 | 1.3687 | 0 | 1.2314 | 0 | 1.3687 | 1.2314 | 15.0036 | 27.8324 | 13.6348
38958.4711 | 2187 | 0 | 38958.4711 | 2543 | 0 | 714.5 | 796.5 | 133.5165 | 0 | 155.2503 | 0 | 1.3352 | 0 | 1.5525 | 0 | 1.3352 | 1.5525 | 17.8957 | 1.3913 | 16.5606
38958.4711 | 2419 | 0 | 38958.4712 | 2533 | 0 | 723 | 805 | 147.6801 | 0 | 154.6398 | 0 | 1.4768 | 0 | 1.5464 | 0 | 1.4768 | 1.5464 | 6.5887 | 1.7916 | 5.1119
38958.4713 | 2453 | 0 | 38958.4713 | 2542 | 0 | 731.5 | 813.5 | 149.7558 | 0 | 155.1893 | 0 | 1.4976 | 0 | 1.5519 | 0 | 1.4976 | 1.5519 | 5.1113 | 1.4312 | 3.6137
38958.4713 | 2163 | 0 | 38958.4714 | 1966 | 0 | 739.5 | 821.5 | 132.0513 | 0 | 120.0244 | 0 | 1.3205 | 0 | 1.2002 | 0 | 1.3205 | 1.2002 | 19.2039 | 31.1485 | 17.8834
38958.4714 | 2181 | 0 | 38958.4715 | 2456 | 0 | 748 | 830 | 133.1502 | 0 | 149.9389 | 0 | 1.3315 | 0 | 1.4994 | 0 | 1.3315 | 1.4994 | 18.2201 | 4.9829 | 16.8886
38958.4715 | 2205 | 0 | 38958.4716 | 1978 | 0 | 756.5 | 838.5 | 134.6154 | 0 | 120.757 | 0 | 1.3462 | 0 | 1.2076 | 0 | 1.3462 | 1.2076 | 16.9333 | 30.3529 | 15.5872
38958.4716 | 2407 | 0 | 38958.4717 | 2485 | 0 | 765 | 847 | 146.9475 | 0 | 151.7094 | 0 | 1.4695 | 0 | 1.5171 | 0 | 1.4695 | 1.5171 | 7.1201 | 3.7577 | 5.6506
38958.4717 | 2547 | 0 | 38958.4717 | 1991 | 0 | 773.5 | 855.5 | 155.4945 | 0 | 121.5507 | 0 | 1.5549 | 0 | 1.2155 | 0 | 1.5549 | 1.2155 | 1.232 | 29.5018 | 0.32291
38958.4718 | 2113 | 0 | 38958.4718 | 2082 | 0 | 781.5 | 863.5 | 128.9988 | 0 | 127.1062 | 0 | 1.29 | 0 | 1.2711 | 0 | 1.29 | 1.2711 | 22.0246 | 23.8415 | 20.7346
38958.4719 | 2199 | 0 | 38958.4719 | 2132 | 0 | 790 | 872 | 134.2491 | 0 | 130.1587 | 0 | 1.3425 | 0 | 1.3016 | 0 | 1.3425 | 1.3016 | 17.2524 | 20.9371 | 15.9099
38958.472 | 2224 | 0 | 38958.472 | 2524 | 0 | 798.5 | 880.5 | 135.7753 | 0 | 154.0904 | 0 | 1.3578 | 0 | 1.5409 | 0 | 1.3578 | 1.5409 | 15.9344 | 2.1545 | 14.5766
38958.4721 | 1963 | 0 | 38958.4721 | 2053 | 0 | 807 | 889 | 119.8413 | 0 | 125.3358 | 0 | 1.1984 | 0 | 1.2534 | 0 | 1.1984 | 1.2534 | 31.349 | 25.5908 | 30.1505
38958.4722 | 2538 | 0 | 38958.4722 | 2267 | 0 | 815.5 | 897.5 | 154.9451 | 0 | 138.4005 | 0 | 1.5495 | 0 | 1.384 | 0 | 1.5495 | 1.384 | 1.591 | 13.7353 | 0.041566
38958.4723 | 2535 | 0 | 38958.4723 | 2427 | 0 | 823.5 | 905.5 | 154.7619 | 0 | 148.1685 | 0 | 1.5476 | 0 | 1.4817 | 0 | 1.5476 | 1.4817 | 1.7112 | 6.2373 | 0.16362
38958.4724 | 2052 | 0 | 38958.4724 | 2041 | 0 | 832 | 914 | 125.2747 | 0 | 124.6032 | 0 | 1.2527 | 0 | 1.246 | 0 | 1.2527 | 1.246 | 25.652 | 26.3293 | 24.3993

## C1-3
Penlight Test 65 |  |  | 2006-08-29 | 11:06 |  | Vs = |  | 156.9219 |  | R = | 100
PVC | 2-C & Shield | Tray
325 C | 7.2 kW/m2 |  | Conductors | 1 & 3
Time-3 | N11 | N12 | Time-4 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
38958.4619 | 1 | 0 | 38958.4619 | 1 | 0 | -77.5 | 4.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38958.462 | 1 | 0 | 38958.462 | 1 | 0 | -69.5 | 12.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38958.4621 | 1 | 0 | 38958.4621 | 1 | 0 | -61 | 21 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38958.4622 | 1 | 0 | 38958.4622 | 1 | 0 | -52.5 | 29.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38958.4623 | 1 | 0 | 38958.4623 | 1 | 0 | -44 | 38 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38958.4624 | 1 | 0 | 38958.4624 | 1 | 0 | -35.5 | 46.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38958.4625 | 1 | 0 | 38958.4625 | 1 | 0 | -27.5 | 54.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38958.4626 | 1 | 0 | 38958.4626 | 1 | 0 | -19 | 63 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38958.4627 | 1 | 0 | 38958.4627 | 1 | 0 | -10.5 | 71.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38958.4628 | 1 | 0 | 38958.4628 | 1 | 0 | -2 | 80 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38958.4629 | 1 | 0 | 38958.4629 | 1 | 0 | 6.5 | 88.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38958.463 | 1 | 0 | 38958.463 | 1 | 0 | 14.5 | 96.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38958.463 | 1 | 0 | 38958.4631 | 1 | 0 | 23 | 105 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38958.4631 | 1 | 0 | 38958.4632 | 1 | 0 | 31.5 | 113.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38958.4632 | 1 | 0 | 38958.4633 | 1 | 0 | 40 | 122 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38958.4633 | 1 | 0 | 38958.4634 | 1 | 0 | 48.5 | 130.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38958.4634 | 1 | 0 | 38958.4634 | 1 | 0 | 56.5 | 138.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38958.4635 | 1 | 0 | 38958.4636 | 1 | 0 | 65 | 147 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38958.4636 | 1 | 0 | 38958.4636 | 1 | 0 | 73.5 | 155.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38958.4637 | 1 | 0 | 38958.4638 | 1 | 0 | 82 | 164 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38958.4638 | 1 | 0 | 38958.4638 | 1 | 0 | 90.5 | 172.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38958.4639 | 1 | 0 | 38958.4639 | 1 | 0 | 98.5 | 180.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38958.464 | 1 | 0 | 38958.464 | 1 | 0 | 107 | 189 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38958.4641 | 1 | 0 | 38958.4641 | 1 | 0 | 115.5 | 197.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38958.4642 | 1 | 0 | 38958.4642 | 1 | 0 | 124 | 206 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38958.4643 | 1 | 0 | 38958.4643 | 1 | 0 | 132.5 | 214.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38958.4644 | 1 | 0 | 38958.4644 | 1 | 0 | 140.5 | 222.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38958.4645 | 1 | 0 | 38958.4645 | 1 | 0 | 149 | 231 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38958.4646 | 1 | 0 | 38958.4646 | 1 | 0 | 157.5 | 239.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38958.4647 | 1 | 0 | 38958.4647 | 1 | 0 | 166 | 248 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38958.4648 | 1 | 0 | 38958.4648 | 1 | 0 | 174.5 | 256.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38958.4649 | 1 | 0 | 38958.4649 | 1 | 0 | 182.5 | 264.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38958.465 | 1 | 0 | 38958.465 | 1 | 0 | 191 | 273 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38958.4651 | 1 | 0 | 38958.4651 | 1 | 0 | 199.5 | 281.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38958.4652 | 1 | 0 | 38958.4652 | 1 | 0 | 208 | 290 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38958.4653 | 1 | 0 | 38958.4653 | 1 | 0 | 216.5 | 298.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38958.4654 | 1 | 0 | 38958.4654 | 1 | 0 | 224.5 | 306.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38958.4655 | 1 | 0 | 38958.4655 | 1 | 0 | 233 | 315 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38958.4656 | 1 | 0 | 38958.4656 | 1 | 0 | 241.5 | 323.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38958.4657 | 1 | 0 | 38958.4657 | 1 | 0 | 250 | 332 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38958.4658 | 978 | 956 | 38958.4658 | 1095 | 1071 | 258 | 340 | 59.707 | 58.3639 | 66.8498 | 65.3846 | 0.59707 | 0.58364 | 0.6685 | 0.65385 | 0.013431 | 0.014652 | 13931.4636 | 9044.5496 | 65.839
38958.4659 | 1 | 0 | 38958.4659 | 1 | 0 | 266.5 | 348.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38958.466 | 1 | 0 | 38958.466 | 1 | 0 | 275 | 357 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
38958.4661 | 1151 | 911 | 38958.4661 | 924 | 931 | 283.5 | 365.5 | 70.2686 | 55.6166 | 56.4103 | 56.8376 | 0.70269 | 0.55617 | 0.5641 | 0.56838 | 0.14652 | 0.0042735 | 382.9406 | 697.2682 | 48.8051
38958.4662 | 2 | 1 | 38958.4662 | 2 | 1 | 292 | 374 | 0.1221 | 0.06105 | 0.1221 | 0.06105 | 0.001221 | 0.0006105 | 0.001221 | 0.0006105 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256638.1167
38958.4662 | 118 | 162 | 38958.4663 | 1156 | 1187 | 300 | 382 | 7.2039 | 9.8901 | 70.5739 | 72.4664 | 0.072039 | 0.098901 | 0.70574 | 0.72466 | 0.026862 | 0.018926 | 5726.7296 | 13768.4212 | 1403.6203
38958.4664 | 1104 | 1081 | 38958.4664 | 1106 | 1170 | 308.5 | 390.5 | 67.3993 | 65.9951 | 67.5214 | 71.4286 | 0.67399 | 0.65995 | 0.67521 | 0.71429 | 0.014042 | 0.039072 | 2485.8775 | 3003.7435 | 34.5017
38958.4664 | 963 | 941 | 38958.4665 | 1024 | 1001 | 317 | 399 | 58.7912 | 57.4481 | 62.5153 | 61.1111 | 0.58791 | 0.57448 | 0.62515 | 0.61111 | 0.013431 | 0.014042 | 12471.7976 | 10327.1751 | 70.137
38958.4666 | 1084 | 1061 | 38958.4666 | 988 | 965 | 325.5 | 407.5 | 66.1783 | 64.7741 | 60.3175 | 58.9133 | 0.66178 | 0.64774 | 0.60317 | 0.58913 | 0.014042 | 0.014042 | 11075.5652 | 11075.5652 | 39.7336
38958.4666 | 1113 | 1090 | 38958.4667 | 1191 | 1023 | 334 | 416 | 67.9487 | 66.5446 | 72.7106 | 62.4542 | 0.67949 | 0.66545 | 0.72711 | 0.62454 | 0.014042 | 0.10256 | 591.3109 | 487.7701 | 27.9703
38958.4667 | 946 | 924 | 38958.4668 | 962 | 1004 | 342.5 | 424.5 | 57.7534 | 56.4103 | 58.7302 | 61.2943 | 0.57753 | 0.5641 | 0.5873 | 0.61294 | 0.013431 | 0.025641 | 49214.4123 | 4941.3399 | 74.2952
38958.4668 | 1090 | 1067 | 38958.4669 | 964 | 943 | 350.5 | 432.5 | 66.5446 | 65.1404 | 58.8523 | 57.5702 | 0.66545 | 0.6514 | 0.58852 | 0.5757 | 0.014042 | 0.012821 | 9435.3257 | 14595.9649 | 38.4786
38958.4669 | 1031 | 1009 | 38958.467 | 1110 | 1165 | 359 | 441 | 62.9426 | 61.5995 | 67.7656 | 71.1233 | 0.62943 | 0.616 | 0.67766 | 0.71123 | 0.013431 | 0.033578 | 4590.2824 | 8746.8152 | 51.9707
38958.467 | 968 | 946 | 38958.467 | 1011 | 988 | 367.5 | 449.5 | 59.0965 | 57.7534 | 61.7216 | 60.3175 | 0.59096 | 0.57753 | 0.61722 | 0.60317 | 0.013431 | 0.014042 | 12464.3485 | 10345.2492 | 68.7205
38958.4671 | 2111 | 1054 | 38958.4672 | 1694 | 667 | 376 | 458 | 128.8767 | 64.3468 | 103.4188 | 40.7204 | 1.2888 | 0.64347 | 1.0342 | 0.4072 | 0.6453 | 0.62698 | 192.4278 | 128.8081 | 31.7593
38958.4672 | 2066 | 4 | 38958.4672 | 1992 | 4 | 384 | 466 | 126.1294 | 0.2442 | 121.6117 | 0.2442 | 1.2613 | 0.002442 | 1.2161 | 0.002442 | 1.2589 | 1.2137 | 24.6236 | 29.3333 | 2837.2002
38958.4673 | 2096 | 3 | 38958.4673 | 2009 | 3 | 392.5 | 474.5 | 127.9609 | 0.18315 | 122.6496 | 0.18315 | 1.2796 | 0.0018315 | 1.2265 | 0.0018315 | 1.2778 | 1.2247 | 22.781 | 28.17 | 3453.4251
38958.4674 | 2514 | 3 | 38958.4674 | 2340 | 2 | 401 | 483 | 153.4799 | 0.18315 | 142.8571 | 0.1221 | 1.5348 | 0.0018315 | 1.4286 | 0.001221 | 1.533 | 1.4274 | 2.2718 | 10.2393 | 165.2685
38958.4675 | 1134 | 1029 | 38958.4675 | 1085 | 842 | 409.5 | 491.5 | 69.2308 | 62.8205 | 66.2393 | 51.4042 | 0.69231 | 0.62821 | 0.66239 | 0.51404 | 0.064103 | 0.14835 | 1346.8578 | 62486.9865 | 39.5266
38958.4676 | 2021 | 3 | 38958.4676 | 2387 | 2 | 418 | 500 | 123.3822 | 0.18315 | 145.7265 | 0.1221 | 1.2338 | 0.0018315 | 1.4573 | 0.001221 | 1.232 | 1.456 | 27.7591 | 7.7122 | 1304.0259
38958.4677 | 2119 | 2 | 38958.4677 | 1181 | 1127 | 426.5 | 508.5 | 129.3651 | 0.1221 | 72.1001 | 68.8034 | 1.2937 | 0.001221 | 0.721 | 0.68803 | 1.2924 | 0.032967 | 21.2458 | 26.4615 | 4701.5379
38958.4678 | 2531 | 2 | 38958.4678 | 1980 | 1 | 434.5 | 516.5 | 154.5177 | 0.1221 | 120.8791 | 0.06105 | 1.5452 | 0.001221 | 1.2088 | 0.0006105 | 1.544 | 1.2082 | 1.5611 | 30.8301 | 440.4301
38958.4679 | 2085 | 1 | 38958.4679 | 2258 | 1 | 443 | 525 | 127.2894 | 0.06105 | 137.851 | 0.06105 | 1.2729 | 0.0006105 | 1.3785 | 0.0006105 | 1.2723 | 1.3779 | 23.3717 | 13.8668 | 5898.8167
38958.468 | 2339 | 1 | 38958.468 | 2534 | 1 | 451.5 | 533.5 | 142.7961 | 0.06105 | 154.7009 | 0.06105 | 1.428 | 0.0006105 | 1.547 | 0.0006105 | 1.4274 | 1.5464 | 10.199 | 1.4418 | 327.4459
38958.4681 | 2128 | 1 | 38958.4681 | 2256 | 1 | 460 | 542 | 129.9145 | 0.06105 | 137.7289 | 0.06105 | 1.2991 | 0.0006105 | 1.3773 | 0.0006105 | 1.2985 | 1.3767 | 20.8685 | 13.9712 | 5410.6562
38958.4682 | 2321 | 1 | 38958.4682 | 2277 | 1 | 468.5 | 550.5 | 141.6972 | 0.06105 | 139.011 | 0.06105 | 1.417 | 0.0006105 | 1.3901 | 0.0006105 | 1.4164 | 1.3895 | 10.7851 | 12.9429 | 2846.3536
38958.4683 | 2308 | 0 | 38958.4683 | 2547 | 1 | 476.5 | 558.5 | 140.9035 | 0 | 155.4945 | 0.06105 | 1.409 | 0 | 1.5549 | 0.0006105 | 1.409 | 1.5543 | 11.3683 | 0.95758 | 9.9592
38958.4684 | 2217 | 0 | 38958.4684 | 2554 | 1 | 485 | 567 | 135.348 | 0 | 155.9219 | 0.06105 | 1.3535 | 0 | 1.5592 | 0.0006105 | 1.3535 | 1.5586 | 15.9396 | 0.68077 | 14.5861
38958.4685 | 2221 | 0 | 38958.4685 | 2475 | 14 | 493.5 | 575.5 | 135.5922 | 0 | 151.0989 | 0.8547 | 1.3559 | 0 | 1.511 | 0.008547 | 1.3559 | 1.5024 | 15.7308 | 4.4445 | 14.3748
38958.4686 | 2425 | 0 | 38958.4686 | 2071 | 0 | 501.5 | 583.5 | 148.0464 | 0 | 126.4347 | 0 | 1.4805 | 0 | 1.2643 | 0 | 1.4805 | 1.2643 | 5.9951 | 24.113 | 4.5146
38958.4687 | 2228 | 0 | 38958.4687 | 2431 | 1 | 510.5 | 592.5 | 136.0195 | 0 | 148.4127 | 0.06105 | 1.3602 | 0 | 1.4841 | 0.0006105 | 1.3602 | 1.4835 | 15.3671 | 5.777 | 14.007
38958.4688 | 2141 | 1 | 38958.4688 | 2316 | 1 | 518.5 | 600.5 | 130.7082 | 0.06105 | 141.3919 | 0.06105 | 1.3071 | 0.0006105 | 1.4139 | 0.0006105 | 1.3065 | 1.4133 | 20.15 | 11.0119 | 4249.3594
38958.4689 | 2481 | 0 | 38958.4689 | 2086 | 0 | 527 | 609 | 151.4652 | 0 | 127.3504 | 0 | 1.5147 | 0 | 1.2735 | 0 | 1.5147 | 1.2735 | 3.6026 | 23.2205 | 2.0879
38958.469 | 2035 | 0 | 38958.469 | 2204 | 0 | 535.5 | 617.5 | 124.2369 | 0 | 134.5543 | 0 | 1.2424 | 0 | 1.3455 | 0 | 1.2424 | 1.3455 | 26.3086 | 16.6234 | 25.0662
38958.4691 | 1969 | 0 | 38958.4691 | 2067 | 0 | 544 | 626 | 120.2076 | 0 | 126.1905 | 0 | 1.2021 | 0 | 1.2619 | 0 | 1.2021 | 1.2619 | 30.5424 | 24.3532 | 29.3403
38958.4692 | 2083 | 0 | 38958.4692 | 2161 | 0 | 552 | 634 | 127.1673 | 0 | 131.9292 | 0 | 1.2717 | 0 | 1.3193 | 0 | 1.2717 | 1.3193 | 23.398 | 18.944 | 22.1263
38958.4693 | 2215 | 1 | 38958.4693 | 2201 | 0 | 560.5 | 642.5 | 135.2259 | 0.06105 | 134.3712 | 0 | 1.3523 | 0.0006105 | 1.3437 | 0 | 1.3516 | 1.3437 | 16.0948 | 16.7824 | 5092.6666
38958.4694 | 2458 | 0 | 38958.4694 | 2303 | 0 | 569 | 651 | 150.0611 | 0 | 140.5983 | 0 | 1.5006 | 0 | 1.406 | 0 | 1.5006 | 1.406 | 4.572 | 11.6101 | 3.0714
38958.4695 | 2526 | 0 | 38958.4695 | 2068 | 1 | 577.5 | 659.5 | 154.2125 | 0 | 126.2515 | 0.06105 | 1.5421 | 0 | 1.2625 | 0.0006105 | 1.5421 | 1.2619 | 1.7569 | 24.3532 | 0.2148
38958.4696 | 2425 | 0 | 38958.4696 | 2112 | 0 | 585.5 | 667.5 | 148.0464 | 0 | 128.9377 | 0 | 1.4805 | 0 | 1.2894 | 0 | 1.4805 | 1.2894 | 5.9951 | 21.7036 | 4.5146
38958.4697 | 2365 | 0 | 38958.4697 | 2399 | 0 | 594 | 676 | 144.3834 | 0 | 146.4591 | 0 | 1.4438 | 0 | 1.4646 | 0 | 1.4438 | 1.4646 | 8.6841 | 7.1438 | 7.2403
38958.4698 | 2375 | 0 | 38958.4698 | 2009 | 0 | 602.5 | 684.5 | 144.9939 | 0 | 122.6496 | 0 | 1.4499 | 0 | 1.2265 | 0 | 1.4499 | 1.2265 | 8.2265 | 27.9433 | 6.7766
38958.4698 | 2066 | 0 | 38958.4699 | 2528 | 0 | 611 | 693 | 126.1294 | 0 | 154.3346 | 0 | 1.2613 | 0 | 1.5433 | 0 | 1.2613 | 1.5433 | 24.4134 | 1.6764 | 23.1521
38958.47 | 2528 | 0 | 38958.47 | 2393 | 0 | 619.5 | 701.5 | 154.3346 | 0 | 146.0928 | 0 | 1.5433 | 0 | 1.4609 | 0 | 1.5433 | 1.4609 | 1.6764 | 7.4125 | 0.13308
38958.47 | 2168 | 0 | 38958.4701 | 2098 | 0 | 627.5 | 709.5 | 132.3565 | 0 | 128.083 | 0 | 1.3236 | 0 | 1.2808 | 0 | 1.3236 | 1.2808 | 18.56 | 22.5157 | 17.2364
38958.4701 | 2316 | 0 | 38958.4702 | 2545 | 0 | 636 | 718 | 141.3919 | 0 | 155.3724 | 0 | 1.4139 | 0 | 1.5537 | 0 | 1.4139 | 1.5537 | 10.9836 | 0.99725 | 9.5697
38958.4702 | 2061 | 0 | 38958.4703 | 2545 | 0 | 644.5 | 726.5 | 125.8242 | 0 | 155.3724 | 0 | 1.2582 | 0 | 1.5537 | 0 | 1.2582 | 1.5537 | 24.7152 | 0.99725 | 23.4569
38958.4703 | 2209 | 0 | 38958.4704 | 2000 | 0 | 653 | 735 | 134.8596 | 0 | 122.1001 | 0 | 1.3486 | 0 | 1.221 | 0 | 1.3486 | 1.221 | 16.3594 | 28.519 | 15.0108
38958.4704 | 2227 | 0 | 38958.4705 | 2482 | 0 | 661.5 | 743.5 | 135.9585 | 0 | 151.5263 | 0 | 1.3596 | 0 | 1.5153 | 0 | 1.3596 | 1.5153 | 15.4189 | 3.5608 | 14.0594
38958.4705 | 2160 | 0 | 38958.4705 | 2129 | 0 | 669.5 | 751.5 | 131.8681 | 0 | 129.9756 | 0 | 1.3187 | 0 | 1.2998 | 0 | 1.3187 | 1.2998 | 18.9991 | 20.7318 | 17.6804
38958.4706 | 2534 | 0 | 38958.4706 | 1972 | 0 | 678 | 760 | 154.7009 | 0 | 120.3907 | 0 | 1.547 | 0 | 1.2039 | 0 | 1.547 | 1.2039 | 1.4357 | 30.3438 | 0.11133
38958.4707 | 2132 | 0 | 38958.4707 | 2378 | 1 | 686.5 | 768.5 | 130.1587 | 0 | 145.177 | 0.06105 | 1.3016 | 0 | 1.4518 | 0.0006105 | 1.3016 | 1.4512 | 20.5619 | 8.1355 | 19.2603
38958.4708 | 2501 | 0 | 38958.4708 | 2346 | 0 | 695 | 777 | 152.6862 | 0 | 143.2234 | 0 | 1.5269 | 0 | 1.4322 | 0 | 1.5269 | 1.4322 | 2.7741 | 9.5644 | 1.2472
38958.4709 | 2404 | 0 | 38958.4709 | 2093 | 2 | 703.5 | 785.5 | 146.7643 | 0 | 127.7778 | 0.1221 | 1.4676 | 0 | 1.2778 | 0.001221 | 1.4676 | 1.2766 | 6.921 | 22.9259 | 5.4533
38958.471 | 2546 | 0 | 38958.471 | 2489 | 0 | 712 | 794 | 155.4335 | 0 | 151.9536 | 0 | 1.5543 | 0 | 1.5195 | 0 | 1.5543 | 1.5195 | 0.95758 | 3.2696 | 0.59675
38958.4711 | 2035 | 0 | 38958.4711 | 2202 | 0 | 720.5 | 802.5 | 124.2369 | 0 | 134.4322 | 0 | 1.2424 | 0 | 1.3443 | 0 | 1.2424 | 1.3443 | 26.3086 | 16.7293 | 25.0662
38958.4712 | 2296 | 0 | 38958.4712 | 2068 | 0 | 728.5 | 810.5 | 140.1709 | 0 | 126.2515 | 0 | 1.4017 | 0 | 1.2625 | 0 | 1.4017 | 1.2625 | 11.9503 | 24.293 | 10.5486
38958.4713 | 2376 | 0 | 38958.4713 | 2311 | 0 | 737 | 819 | 145.0549 | 0 | 141.0867 | 0 | 1.4505 | 0 | 1.4109 | 0 | 1.4505 | 1.4109 | 8.181 | 11.2237 | 6.7304
38958.4714 | 2275 | 0 | 38958.4714 | 2522 | 0 | 745.5 | 827.5 | 138.8889 | 0 | 153.9683 | 0 | 1.3889 | 0 | 1.5397 | 0 | 1.3889 | 1.5397 | 12.9837 | 1.9183 | 11.5948
38958.4715 | 2460 | 0 | 38958.4715 | 2360 | 0 | 753.5 | 835.5 | 150.1832 | 0 | 144.0781 | 0 | 1.5018 | 0 | 1.4408 | 0 | 1.5018 | 1.4408 | 4.487 | 8.9144 | 2.9852
38958.4716 | 2155 | 0 | 38958.4716 | 2002 | 0 | 762 | 844 | 131.5629 | 0 | 122.2222 | 0 | 1.3156 | 0 | 1.2222 | 0 | 1.3156 | 1.2222 | 19.2752 | 28.3906 | 17.9595
38958.4717 | 2395 | 0 | 38958.4717 | 2280 | 0 | 770.5 | 852.5 | 146.2149 | 0 | 139.1941 | 0 | 1.4621 | 0 | 1.3919 | 0 | 1.4621 | 1.3919 | 7.3228 | 12.736 | 5.8606
38958.4718 | 2172 | 0 | 38958.4718 | 2512 | 0 | 779 | 861 | 132.6007 | 0 | 153.3578 | 0 | 1.326 | 0 | 1.5336 | 0 | 1.326 | 1.5336 | 18.3416 | 2.324 | 17.0156
38958.4719 | 2408 | 0 | 38958.4719 | 2094 | 0 | 787.5 | 869.5 | 147.0085 | 0 | 127.8388 | 0 | 1.4701 | 0 | 1.2784 | 0 | 1.4701 | 1.2784 | 6.7434 | 22.7498 | 5.2733
38958.472 | 2181 | 0 | 38958.472 | 1968 | 0 | 795.5 | 877.5 | 133.1502 | 0 | 120.1465 | 0 | 1.3315 | 0 | 1.2015 | 0 | 1.3315 | 1.2015 | 17.8533 | 30.6087 | 16.5218
38958.4721 | 2360 | 0 | 38958.4721 | 2007 | 0 | 804.5 | 886.5 | 144.0781 | 0 | 122.5275 | 0 | 1.4408 | 0 | 1.2253 | 0 | 1.4408 | 1.2253 | 8.9144 | 28.0708 | 7.4736
38958.4722 | 2171 | 0 | 38958.4722 | 2448 | 0 | 812.5 | 894.5 | 132.5397 | 0 | 149.4505 | 0 | 1.3254 | 0 | 1.4945 | 0 | 1.3254 | 1.4945 | 18.3961 | 4.9992 | 17.0707
38958.4723 | 2183 | 0 | 38958.4723 | 2349 | 0 | 821 | 903 | 133.2723 | 0 | 143.4066 | 0 | 1.3327 | 0 | 1.4341 | 0 | 1.3327 | 1.4341 | 17.7453 | 9.4244 | 16.4126
38958.4724 | 1961 | 0 | 38958.4724 | 1996 | 0 | 829.5 | 911.5 | 119.7192 | 0 | 121.8559 | 0 | 1.1972 | 0 | 1.2186 | 0 | 1.1972 | 1.2186 | 31.075 | 28.7766 | 29.8778

## C1-2
Penlight Test 65 |  |  | 2006-08-29 | 11:06 |  | Vs = |  | 157.2882 |  | R = | 100
PVC | 2-C & Shield | Tray
325 C | 7.2 kW/m2 |  | Conductors | 1 & 2
Time-1 | N11 | N12 | Time-2 | N21 | N22 | Penlight Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
38958.4618 | 1 | 0 | 38958.4619 | 1 | 0 | -81 | 1 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257538 | 257538 | 257537.9994
38958.4619 | 1 | 0 | 38958.462 | 1 | 0 | -72 | 10 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257538 | 257538 | 257537.9994
38958.462 | 1 | 0 | 38958.4621 | 1 | 0 | -63.5 | 18.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257538 | 257538 | 257537.9994
38958.4621 | 1 | 0 | 38958.4622 | 1 | 0 | -55.5 | 26.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257538 | 257538 | 257537.9994
38958.4622 | 1 | 0 | 38958.4623 | 1 | 0 | -47 | 35 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257538 | 257538 | 257537.9994
38958.4623 | 1 | 0 | 38958.4623 | 1 | 0 | -38.5 | 43.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257538 | 257538 | 257537.9994
38958.4624 | 1 | 0 | 38958.4625 | 1 | 0 | -30 | 52 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257538 | 257538 | 257537.9994
38958.4625 | 1 | 0 | 38958.4625 | 1 | 0 | -21.5 | 60.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257538 | 257538 | 257537.9994
38958.4626 | 1 | 0 | 38958.4626 | 1 | 0 | -13.5 | 68.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257538 | 257538 | 257537.9994
38958.4627 | 3 | 0 | 38958.4627 | 1 | 0 | -5 | 77 | 0.18315 | 0 | 0.06105 | 0 | 0.0018315 | 0 | 0.0006105 | 0 | 0.0018315 | 0.0006105 | 85779.3333 | 257538 | 85779.3315
38958.4628 | 1 | 0 | 38958.4628 | 1 | 0 | 3.5 | 85.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257538 | 257538 | 257537.9994
38958.4629 | 1 | 0 | 38958.4629 | 1 | 0 | 12 | 94 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257538 | 257538 | 257537.9994
38958.463 | 1 | 0 | 38958.463 | 1 | 0 | 20.5 | 102.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257538 | 257538 | 257537.9994
38958.4631 | 1 | 0 | 38958.4631 | 1 | 0 | 28.5 | 110.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257538 | 257538 | 257537.9994
38958.4632 | 1 | 0 | 38958.4632 | 1 | 0 | 37 | 119 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257538 | 257538 | 257537.9994
38958.4633 | 1 | 0 | 38958.4633 | 1 | 0 | 45.5 | 127.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257538 | 257538 | 257537.9994
38958.4634 | 2 | 0 | 38958.4634 | 1 | 0 | 54 | 136 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 128719 | 257538 | 128718.9988
38958.4635 | 1 | 0 | 38958.4635 | 1 | 0 | 62.5 | 144.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257538 | 257538 | 257537.9994
38958.4636 | 1 | 0 | 38958.4636 | 1 | 0 | 70.5 | 152.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257538 | 257538 | 257537.9994
38958.4637 | 1 | 0 | 38958.4637 | 1 | 0 | 79 | 161 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257538 | 257538 | 257537.9994
38958.4638 | 1 | 0 | 38958.4638 | 1 | 0 | 87.5 | 169.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257538 | 257538 | 257537.9994
38958.4639 | 1 | 0 | 38958.4639 | 1 | 0 | 96 | 178 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257538 | 257538 | 257537.9994
38958.464 | 1 | 0 | 38958.464 | 1 | 0 | 104.5 | 186.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257538 | 257538 | 257537.9994
38958.4641 | 1 | 0 | 38958.4641 | 1 | 0 | 112.5 | 194.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257538 | 257538 | 257537.9994
38958.4642 | 1 | 0 | 38958.4642 | 1 | 0 | 121 | 203 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257538 | 257538 | 257537.9994
38958.4643 | 1 | 0 | 38958.4643 | 1 | 0 | 129.5 | 211.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257538 | 257538 | 257537.9994
38958.4644 | 1 | 0 | 38958.4644 | 1 | 0 | 138 | 220 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257538 | 257538 | 257537.9994
38958.4645 | 1 | 0 | 38958.4645 | 1 | 0 | 146.5 | 228.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257538 | 257538 | 257537.9994
38958.4646 | 1 | 0 | 38958.4646 | 1 | 0 | 154.5 | 236.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257538 | 257538 | 257537.9994
38958.4647 | 1 | 0 | 38958.4647 | 1 | 0 | 163 | 245 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257538 | 257538 | 257537.9994
38958.4648 | 1 | 0 | 38958.4648 | 1 | 0 | 171.5 | 253.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257538 | 257538 | 257537.9994
38958.4649 | 1 | 0 | 38958.4649 | 1 | 0 | 180 | 262 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257538 | 257538 | 257537.9994
38958.465 | 1 | 0 | 38958.465 | 1 | 0 | 188.5 | 270.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257538 | 257538 | 257537.9994
38958.4651 | 1 | 0 | 38958.4651 | 1 | 0 | 196.5 | 278.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257538 | 257538 | 257537.9994
38958.4652 | 1 | 0 | 38958.4652 | 1 | 0 | 205 | 287 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257538 | 257538 | 257537.9994
38958.4653 | 1 | 0 | 38958.4653 | 1 | 0 | 213.5 | 295.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257538 | 257538 | 257537.9994
38958.4653 | 1 | 0 | 38958.4654 | 1 | 0 | 222 | 304 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257538 | 257538 | 257537.9994
38958.4655 | 1 | 0 | 38958.4655 | 1 | 0 | 230.5 | 312.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257538 | 257538 | 257537.9994
38958.4655 | 1 | 0 | 38958.4656 | 1 | 0 | 238.5 | 320.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257538 | 257538 | 257537.9994
38958.4656 | 1 | 0 | 38958.4657 | 1 | 0 | 247 | 329 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257538 | 257538 | 257537.9994
38958.4657 | 1 | 0 | 38958.4658 | 1 | 0 | 255.5 | 337.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257538 | 257538 | 257537.9994
38958.4658 | 1 | 0 | 38958.4658 | 1 | 0 | 263.5 | 345.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257538 | 257538 | 257537.9994
38958.4659 | 1 | 1 | 38958.4659 | 1 | 0 | 272.5 | 354.5 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 663258214.44 | 257538 | 257338.0776
38958.466 | 1 | 0 | 38958.466 | 1 | 0 | 280.5 | 362.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257538 | 257538 | 257537.9994
38958.4661 | 1 | 1 | 38958.4661 | 2 | 1 | 289 | 371 | 0.06105 | 0.06105 | 0.1221 | 0.06105 | 0.0006105 | 0.0006105 | 0.001221 | 0.0006105 | 0 | 0.0006105 | 663000576.44 | 257437.9612 | 257338.0388
38958.4662 | 973 | 949 | 38958.4662 | 21 | 19 | 297.5 | 379.5 | 59.4017 | 57.9365 | 1.2821 | 1.16 | 0.59402 | 0.57937 | 0.012821 | 0.0116 | 0.014652 | 0.001221 | 6863.768 | 148294.0782 | 68.9082
38958.4663 | 955 | 933 | 38958.4663 | 1006 | 982 | 305.5 | 387.5 | 58.3028 | 56.9597 | 61.4164 | 59.9512 | 0.58303 | 0.5696 | 0.61416 | 0.59951 | 0.013431 | 0.014652 | 13408.4276 | 9416.8665 | 73.0061
38958.4664 | 1073 | 1051 | 38958.4664 | 1011 | 988 | 314 | 396 | 65.5067 | 64.1636 | 61.7216 | 60.3175 | 0.65507 | 0.64164 | 0.61722 | 0.60317 | 0.013431 | 0.014042 | 12809.8088 | 10239.835 | 42.6265
38958.4665 | 924 | 928 | 38958.4665 | 1009 | 1056 | 322.5 | 404.5 | 56.4103 | 56.6545 | 61.5995 | 64.4689 | 0.5641 | 0.56654 | 0.616 | 0.64469 | 0.002442 | 0.028694 | 4310.8196 | 2703.0968 | 75.2735
38958.4666 | 939 | 944 | 38958.4666 | 951 | 990 | 331 | 413 | 57.326 | 57.6313 | 58.0586 | 60.4396 | 0.57326 | 0.57631 | 0.58059 | 0.6044 | 0.0030525 | 0.02381 | 6019.0271 | 4251.6012 | 71.7634
38958.4667 | 953 | 930 | 38958.4667 | 1066 | 1150 | 339.5 | 421.5 | 58.1807 | 56.7766 | 65.0794 | 70.2076 | 0.58181 | 0.56777 | 0.65079 | 0.70208 | 0.014042 | 0.051282 | 3186.6771 | 3328.2372 | 72.3822
38958.4668 | 1112 | 1171 | 38958.4668 | 1018 | 997 | 348 | 430 | 67.8877 | 71.4896 | 62.149 | 60.8669 | 0.67888 | 0.7149 | 0.62149 | 0.60867 | 0.03602 | 0.012821 | 1654.8135 | 3970.5486 | 24.4383
38958.4669 | 1153 | 1132 | 38958.4669 | 1156 | 1136 | 356.5 | 438.5 | 70.3907 | 69.1087 | 70.5739 | 69.3529 | 0.70391 | 0.69109 | 0.70574 | 0.69353 | 0.012821 | 0.01221 | 10236.3736 | 15955.1671 | 25.58
38958.467 | 918 | 953 | 38958.467 | 979 | 957 | 364.5 | 446.5 | 56.044 | 58.1807 | 59.768 | 58.4249 | 0.56044 | 0.58181 | 0.59768 | 0.58425 | 0.021368 | 0.013431 | 4971.1726 | 58107.4894 | 73.8896
38958.4671 | 2220 | 931 | 38958.4671 | 2148 | 776 | 373 | 455 | 135.5311 | 56.8376 | 131.1355 | 47.3748 | 1.3553 | 0.56838 | 1.3114 | 0.47375 | 0.78694 | 0.83761 | 78.5754 | 111.4371 | 32.5297
38958.4672 | 2103 | 4 | 38958.4672 | 2394 | 4 | 381.5 | 463.5 | 128.3883 | 0.2442 | 146.1538 | 0.2442 | 1.2839 | 0.002442 | 1.4615 | 0.002442 | 1.2814 | 1.4591 | 23.126 | 7.6866 | 837.6001
38958.4673 | 2510 | 3 | 38958.4673 | 2155 | 3 | 389.5 | 471.5 | 153.2357 | 0.18315 | 131.5629 | 0.18315 | 1.5324 | 0.0018315 | 1.3156 | 0.0018315 | 1.5305 | 1.3138 | 2.6632 | 20.6624 | 361.7764
38958.4674 | 2404 | 4 | 38958.4674 | 2254 | 2 | 398.5 | 480.5 | 146.7643 | 0.2442 | 137.6068 | 0.1221 | 1.4676 | 0.002442 | 1.3761 | 0.001221 | 1.4652 | 1.3748 | 7.2661 | 14.4924 | 532.8371
38958.4675 | 2098 | 822 | 38958.4675 | 1027 | 982 | 406.5 | 488.5 | 128.083 | 50.1832 | 62.6984 | 59.9512 | 1.2808 | 0.50183 | 0.62698 | 0.59951 | 0.779 | 0.027473 | 3.4026 | 6.4303 | 2.5257
38958.4676 | 2289 | 3 | 38958.4676 | 2060 | 3 | 415 | 497 | 139.7436 | 0.18315 | 125.7631 | 0.18315 | 1.3974 | 0.0018315 | 1.2576 | 0.0018315 | 1.3956 | 1.2558 | 12.6366 | 25.3967 | 1919.855
38958.4677 | 2293 | 2 | 38958.4677 | 1566 | 1050 | 423.5 | 505.5 | 139.9878 | 0.1221 | 95.6044 | 64.1026 | 1.3999 | 0.001221 | 0.95604 | 0.64103 | 1.3987 | 0.31502 | 12.284 | 12.5799 | 1572.1005
38958.4678 | 2483 | 2 | 38958.4678 | 2409 | 2 | 431.5 | 513.5 | 151.5873 | 0.1221 | 147.0696 | 0.1221 | 1.5159 | 0.001221 | 1.4707 | 0.001221 | 1.5147 | 1.4695 | 3.807 | 7.109 | 303.2539
38958.4679 | 2018 | 1 | 38958.4679 | 2069 | 1 | 440 | 522 | 123.199 | 0.06105 | 126.3126 | 0.06105 | 1.232 | 0.0006105 | 1.2631 | 0.0006105 | 1.2314 | 1.2625 | 27.7396 | 24.5777 | 10996.4308
38958.468 | 2165 | 1 | 38958.468 | 2378 | 1 | 448.5 | 530.5 | 132.1734 | 0.06105 | 145.177 | 0.06105 | 1.3217 | 0.0006105 | 1.4518 | 0.0006105 | 1.3211 | 1.4512 | 19.1158 | 8.3642 | 3167.5671
38958.4681 | 2301 | 1 | 38958.4681 | 2433 | 1 | 457 | 539 | 140.4762 | 0.06105 | 148.5348 | 0.06105 | 1.4048 | 0.0006105 | 1.4853 | 0.0006105 | 1.4042 | 1.4847 | 12.0617 | 5.9157 | 1532.4985
38958.4682 | 2549 | 1 | 38958.4682 | 2557 | 1 | 465.5 | 547.5 | 155.6166 | 0.06105 | 156.105 | 0.06105 | 1.5562 | 0.0006105 | 1.5611 | 0.0006105 | 1.5556 | 1.5604 | 1.1311 | 0.78538 | 20.5569
38958.4683 | 2007 | 1 | 38958.4683 | 2154 | 1 | 473.5 | 555.5 | 122.5275 | 0.06105 | 131.5018 | 0.06105 | 1.2253 | 0.0006105 | 1.315 | 0.0006105 | 1.2247 | 1.3144 | 28.456 | 19.6503 | 9334.5595
38958.4684 | 2178 | 1 | 38958.4684 | 2084 | 1 | 482.5 | 564.5 | 132.967 | 0.06105 | 127.2283 | 0.06105 | 1.3297 | 0.0006105 | 1.2723 | 0.0006105 | 1.3291 | 1.2717 | 18.335 | 23.7001 | 7613.5253
38958.4685 | 2326 | 0 | 38958.4685 | 2072 | 0 | 490.5 | 572.5 | 142.0024 | 0 | 126.4957 | 0 | 1.42 | 0 | 1.265 | 0 | 1.42 | 1.265 | 10.7644 | 24.3427 | 9.3444
38958.4686 | 2263 | 0 | 38958.4686 | 1987 | 0 | 499 | 581 | 138.1563 | 0 | 121.3065 | 0 | 1.3816 | 0 | 1.2131 | 0 | 1.3816 | 1.2131 | 13.848 | 29.6618 | 12.4664
38958.4687 | 2077 | 0 | 38958.4687 | 2077 | 1 | 507.5 | 589.5 | 126.801 | 0 | 126.801 | 0.06105 | 1.268 | 0 | 1.268 | 0.0006105 | 1.268 | 1.2674 | 24.0433 | 24.1031 | 22.7753
38958.4688 | 2535 | 0 | 38958.4688 | 2472 | 0 | 516 | 598 | 154.7619 | 0 | 150.9158 | 0 | 1.5476 | 0 | 1.5092 | 0 | 1.5476 | 1.5092 | 1.6323 | 4.2225 | 0.084728
38958.4688 | 2201 | 0 | 38958.4689 | 2336 | 0 | 524 | 606 | 134.3712 | 0 | 142.6129 | 0 | 1.3437 | 0 | 1.4261 | 0 | 1.3437 | 1.4261 | 17.055 | 10.2902 | 15.7113
38958.4689 | 2029 | 0 | 38958.469 | 2128 | 0 | 532.5 | 614.5 | 123.8706 | 0 | 129.9145 | 0 | 1.2387 | 0 | 1.2991 | 0 | 1.2387 | 1.2991 | 26.9778 | 21.0705 | 25.7391
38958.469 | 2236 | 0 | 38958.4691 | 2072 | 0 | 541 | 623 | 136.5079 | 0 | 126.4957 | 0 | 1.3651 | 0 | 1.265 | 0 | 1.3651 | 1.265 | 15.2227 | 24.3427 | 13.8576
38958.4691 | 2403 | 0 | 38958.4692 | 1984 | 0 | 549.5 | 631.5 | 146.7033 | 0 | 121.1233 | 0 | 1.467 | 0 | 1.2112 | 0 | 1.467 | 1.2112 | 7.2151 | 29.8579 | 5.7481
38958.4692 | 2413 | 0 | 38958.4692 | 2233 | 0 | 557.5 | 639.5 | 147.3138 | 0 | 136.3248 | 0 | 1.4731 | 0 | 1.3632 | 0 | 1.4731 | 1.3632 | 6.7708 | 15.3775 | 5.2977
38958.4693 | 2410 | 0 | 38958.4694 | 2296 | 0 | 566 | 648 | 147.1306 | 0 | 140.1709 | 0 | 1.4713 | 0 | 1.4017 | 0 | 1.4713 | 1.4017 | 6.9037 | 12.2117 | 5.4324
38958.4694 | 2560 | 0 | 38958.4694 | 2253 | 0 | 574.5 | 656.5 | 156.2882 | 0 | 137.5458 | 0 | 1.5629 | 0 | 1.3755 | 0 | 1.5629 | 1.3755 | 0.63984 | 14.3533 | 0.92304
38958.4695 | 2154 | 0 | 38958.4695 | 2132 | 0 | 583 | 665 | 131.5018 | 0 | 130.1587 | 0 | 1.315 | 0 | 1.3016 | 0 | 1.315 | 1.3016 | 19.6091 | 20.8433 | 18.2941
38958.4696 | 2274 | 0 | 38958.4696 | 2139 | 0 | 591.5 | 673.5 | 138.8278 | 0 | 130.5861 | 0 | 1.3883 | 0 | 1.3059 | 0 | 1.3883 | 1.3059 | 13.2973 | 20.4479 | 11.909
38958.4697 | 2483 | 0 | 38958.4697 | 2202 | 0 | 599.5 | 681.5 | 151.5873 | 0 | 134.4322 | 0 | 1.5159 | 0 | 1.3443 | 0 | 1.5159 | 1.3443 | 3.7608 | 17.0018 | 2.2449
38958.4698 | 2499 | 0 | 38958.4698 | 2278 | 0 | 608.5 | 690.5 | 152.5641 | 0 | 139.072 | 0 | 1.5256 | 0 | 1.3907 | 0 | 1.5256 | 1.3907 | 3.0964 | 13.0983 | 1.5708
38958.4699 | 2249 | 0 | 38958.4699 | 1976 | 0 | 616.5 | 698.5 | 137.3016 | 0 | 120.6349 | 0 | 1.373 | 0 | 1.2063 | 0 | 1.373 | 1.2063 | 14.5567 | 30.3836 | 13.1837
38958.47 | 2231 | 0 | 38958.47 | 2105 | 0 | 625 | 707 | 136.2027 | 0 | 128.5104 | 0 | 1.362 | 0 | 1.2851 | 0 | 1.362 | 1.2851 | 15.481 | 22.3933 | 14.1189
38958.4701 | 1978 | 0 | 38958.4701 | 2181 | 0 | 633.5 | 715.5 | 120.757 | 0 | 133.1502 | 0 | 1.2076 | 0 | 1.3315 | 0 | 1.2076 | 1.3315 | 30.2518 | 18.1284 | 29.0442
38958.4702 | 2335 | 0 | 38958.4702 | 2509 | 0 | 642 | 724 | 142.5519 | 0 | 153.1746 | 0 | 1.4255 | 0 | 1.5317 | 0 | 1.4255 | 1.5317 | 10.3375 | 2.6855 | 8.912
38958.4703 | 2048 | 0 | 38958.4703 | 2445 | 0 | 650 | 732 | 125.0305 | 0 | 149.2674 | 0 | 1.2503 | 0 | 1.4927 | 0 | 1.2503 | 1.4927 | 25.7998 | 5.3734 | 24.5495
38958.4704 | 2244 | 0 | 38958.4704 | 2423 | 0 | 658.5 | 740.5 | 136.9963 | 0 | 147.9243 | 0 | 1.37 | 0 | 1.4792 | 0 | 1.37 | 1.4792 | 14.8119 | 6.3302 | 13.442
38958.4705 | 1987 | 0 | 38958.4705 | 2549 | 0 | 667 | 749 | 121.3065 | 0 | 155.6166 | 0 | 1.2131 | 0 | 1.5562 | 0 | 1.2131 | 1.5562 | 29.6618 | 1.0741 | 28.4487
38958.4706 | 2473 | 0 | 38958.4706 | 2210 | 0 | 675.5 | 757.5 | 150.9768 | 0 | 134.9206 | 0 | 1.5098 | 0 | 1.3492 | 0 | 1.5098 | 1.3492 | 4.1803 | 16.5783 | 2.6706
38958.4707 | 2202 | 0 | 38958.4707 | 2151 | 0 | 684 | 766 | 134.4322 | 0 | 131.3187 | 0 | 1.3443 | 0 | 1.3132 | 0 | 1.3443 | 1.3132 | 17.0018 | 19.7759 | 15.6575
38958.4708 | 2534 | 0 | 38958.4708 | 2425 | 0 | 692 | 774 | 154.7009 | 0 | 148.0464 | 0 | 1.547 | 0 | 1.4805 | 0 | 1.547 | 1.4805 | 1.6725 | 6.2425 | 0.12545
38958.4709 | 2110 | 0 | 38958.4709 | 2423 | 0 | 700.5 | 782.5 | 128.8156 | 0 | 147.9243 | 0 | 1.2882 | 0 | 1.4792 | 0 | 1.2882 | 1.4792 | 22.1033 | 6.3302 | 20.8152
38958.471 | 2247 | 0 | 38958.471 | 2334 | 0 | 709 | 791 | 137.1795 | 0 | 142.4908 | 0 | 1.3718 | 0 | 1.4249 | 0 | 1.3718 | 1.4249 | 14.6587 | 10.3847 | 13.2869
38958.4711 | 2185 | 0 | 38958.4711 | 2098 | 0 | 717.5 | 799.5 | 133.3944 | 0 | 128.083 | 0 | 1.3339 | 0 | 1.2808 | 0 | 1.3339 | 1.2808 | 17.9121 | 22.8017 | 16.5782
38958.4712 | 2413 | 0 | 38958.4712 | 2082 | 0 | 726 | 808 | 147.3138 | 0 | 127.1062 | 0 | 1.4731 | 0 | 1.2711 | 0 | 1.4731 | 1.2711 | 6.7708 | 23.7454 | 5.2977
38958.4713 | 2054 | 0 | 38958.4713 | 2377 | 0 | 734 | 816 | 125.3968 | 0 | 145.116 | 0 | 1.254 | 0 | 1.4512 | 0 | 1.254 | 1.4512 | 25.4323 | 8.3879 | 24.1784
38958.4714 | 2151 | 0 | 38958.4714 | 2251 | 0 | 742.5 | 824.5 | 131.3187 | 0 | 137.4237 | 0 | 1.3132 | 0 | 1.3742 | 0 | 1.3132 | 1.3742 | 19.7759 | 14.4549 | 18.4627
38958.4715 | 2166 | 0 | 38958.4715 | 2029 | 0 | 751 | 833 | 132.2344 | 0 | 123.8706 | 0 | 1.3223 | 0 | 1.2387 | 0 | 1.3223 | 1.2387 | 18.9464 | 26.9778 | 17.6241
38958.4716 | 2515 | 0 | 38958.4716 | 1967 | 0 | 759.5 | 841.5 | 153.5409 | 0 | 120.0855 | 0 | 1.5354 | 0 | 1.2009 | 0 | 1.5354 | 1.2009 | 2.4406 | 30.9802 | 0.90515
38958.4717 | 2107 | 0 | 38958.4717 | 2381 | 0 | 767.5 | 849.5 | 128.6325 | 0 | 145.3602 | 0 | 1.2863 | 0 | 1.4536 | 0 | 1.2863 | 1.4536 | 22.2772 | 8.2058 | 20.9908
38958.4718 | 1991 | 0 | 38958.4718 | 2027 | 0 | 776 | 858 | 121.5507 | 0 | 123.7485 | 0 | 1.2155 | 0 | 1.2375 | 0 | 1.2155 | 1.2375 | 29.4013 | 27.1031 | 28.1858
38958.4719 | 2353 | 0 | 38958.4719 | 2108 | 0 | 784.5 | 866.5 | 143.6508 | 0 | 128.6935 | 0 | 1.4365 | 0 | 1.2869 | 0 | 1.4365 | 1.2869 | 9.4934 | 22.2192 | 8.0569
38958.472 | 2330 | 0 | 38958.472 | 2354 | 0 | 793 | 875 | 142.2466 | 0 | 143.7118 | 0 | 1.4225 | 0 | 1.4371 | 0 | 1.4225 | 1.4371 | 10.5742 | 9.4469 | 9.1518
38958.4721 | 2168 | 0 | 38958.4721 | 2383 | 0 | 801.5 | 883.5 | 132.3565 | 0 | 145.4823 | 0 | 1.3236 | 0 | 1.4548 | 0 | 1.3236 | 1.4548 | 18.8367 | 8.115 | 17.5132
38958.4722 | 2528 | 0 | 38958.4722 | 2449 | 0 | 810 | 892 | 154.3346 | 0 | 149.5116 | 0 | 1.5433 | 0 | 1.4951 | 0 | 1.5433 | 1.4951 | 1.9138 | 5.2013 | 0.37042
38958.4722 | 2174 | 0 | 38958.4723 | 2484 | 0 | 818 | 900 | 132.7228 | 0 | 151.6484 | 0 | 1.3272 | 0 | 1.5165 | 0 | 1.3272 | 1.5165 | 18.5087 | 3.719 | 17.1815
38958.4723 | 2109 | 0 | 38958.4724 | 1968 | 0 | 826.5 | 908.5 | 128.7546 | 0 | 120.1465 | 0 | 1.2875 | 0 | 1.2015 | 0 | 1.2875 | 1.2015 | 22.1612 | 30.9136 | 20.8737

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | Penlight Test 65 |  |  | 2006-08-29 | 11:06
38958.4618 | 1 | 0 | 1 | PVC | 2-C & Shield | Tray
38958.4619 | 1 | 0 | 1 | 325 C | 7.2 kW/m2 |  | Conductors
38958.462 | 1 | 0 | 1
38958.4621 | 1 | 0 | 1
38958.4622 | 1 | 0 | 1
38958.4623 | 1 | 0 | 1
38958.4624 | 1 | 0 | 1
38958.4625 | 1 | 0 | 1
38958.4626 | 1 | 0 | 1
38958.4627 | 3 | 0 | 1
38958.4628 | 1 | 0 | 1
38958.4629 | 1 | 0 | 1
38958.463 | 1 | 0 | 1
38958.4631 | 1 | 0 | 1
38958.4632 | 1 | 0 | 1
38958.4633 | 1 | 0 | 1
38958.4634 | 2 | 0 | 1
38958.4635 | 1 | 0 | 1
38958.4636 | 1 | 0 | 1
38958.4637 | 1 | 0 | 1
38958.4638 | 1 | 0 | 1
38958.4639 | 1 | 0 | 1
38958.464 | 1 | 0 | 1
38958.4641 | 1 | 0 | 1
38958.4642 | 1 | 0 | 1
38958.4643 | 1 | 0 | 1
38958.4644 | 1 | 0 | 1
38958.4645 | 1 | 0 | 1
38958.4646 | 1 | 0 | 1
38958.4647 | 1 | 0 | 1
38958.4648 | 1 | 0 | 1
38958.4649 | 1 | 0 | 1
38958.465 | 1 | 0 | 1
38958.4651 | 1 | 0 | 1
38958.4652 | 1 | 0 | 1
38958.4653 | 1 | 0 | 1
38958.4653 | 1 | 0 | 1
38958.4655 | 1 | 0 | 1
38958.4655 | 1 | 0 | 1
38958.4656 | 1 | 0 | 1
38958.4657 | 1 | 0 | 1
38958.4658 | 1 | 0 | 1
38958.4659 | 1 | 1 | 1
38958.466 | 1 | 0 | 1
38958.4661 | 1 | 1 | 1
38958.4662 | 973 | 949 | 1
38958.4663 | 955 | 933 | 1
38958.4664 | 1073 | 1051 | 1
38958.4665 | 924 | 928 | 1
38958.4666 | 939 | 944 | 1
38958.4667 | 953 | 930 | 1
38958.4668 | 1112 | 1171 | 1
38958.4669 | 1153 | 1132 | 1
38958.467 | 918 | 953 | 1
38958.4671 | 2220 | 931 | 1
38958.4672 | 2103 | 4 | 1
38958.4673 | 2510 | 3 | 1
38958.4674 | 2404 | 4 | 1
38958.4675 | 2098 | 822 | 1
38958.4676 | 2289 | 3 | 1
38958.4677 | 2293 | 2 | 1
38958.4678 | 2483 | 2 | 1
38958.4679 | 2018 | 1 | 1
38958.468 | 2165 | 1 | 1
38958.4681 | 2301 | 1 | 1
38958.4682 | 2549 | 1 | 1
38958.4683 | 2007 | 1 | 1
38958.4684 | 2178 | 1 | 1
38958.4685 | 2326 | 0 | 1
38958.4686 | 2263 | 0 | 1
38958.4687 | 2077 | 0 | 1
38958.4688 | 2535 | 0 | 1
38958.4688 | 2201 | 0 | 1
38958.4689 | 2029 | 0 | 1
38958.469 | 2236 | 0 | 1
38958.4691 | 2403 | 0 | 1
38958.4692 | 2413 | 0 | 1
38958.4693 | 2410 | 0 | 1
38958.4694 | 2560 | 0 | 1
38958.4695 | 2154 | 0 | 1
38958.4696 | 2274 | 0 | 1
38958.4697 | 2483 | 0 | 1
38958.4698 | 2499 | 0 | 1
38958.4699 | 2249 | 0 | 1
38958.47 | 2231 | 0 | 1
38958.4701 | 1978 | 0 | 1
38958.4702 | 2335 | 0 | 1
38958.4703 | 2048 | 0 | 1
38958.4704 | 2244 | 0 | 1
38958.4705 | 1987 | 0 | 1
38958.4706 | 2473 | 0 | 1
38958.4707 | 2202 | 0 | 1
38958.4708 | 2534 | 0 | 1
38958.4709 | 2110 | 0 | 1
38958.471 | 2247 | 0 | 1
38958.4711 | 2185 | 0 | 1
38958.4712 | 2413 | 0 | 1
38958.4713 | 2054 | 0 | 1
38958.4714 | 2151 | 0 | 1
38958.4715 | 2166 | 0 | 1
38958.4716 | 2515 | 0 | 1
38958.4717 | 2107 | 0 | 1
38958.4718 | 1991 | 0 | 1
38958.4719 | 2353 | 0 | 1
38958.472 | 2330 | 0 | 1
38958.4721 | 2168 | 0 | 1
38958.4722 | 2528 | 0 | 1
38958.4722 | 2174 | 0 | 1
38958.4723 | 2109 | 0 | 1
1
38958.4619 | 1 | 0 | 2
38958.462 | 1 | 0 | 2
38958.4621 | 1 | 0 | 2
38958.4622 | 1 | 0 | 2
38958.4623 | 1 | 0 | 2
38958.4623 | 1 | 0 | 2
38958.4625 | 1 | 0 | 2
38958.4625 | 1 | 0 | 2
38958.4626 | 1 | 0 | 2
38958.4627 | 1 | 0 | 2
38958.4628 | 1 | 0 | 2
38958.4629 | 1 | 0 | 2
38958.463 | 1 | 0 | 2
38958.4631 | 1 | 0 | 2
38958.4632 | 1 | 0 | 2
38958.4633 | 1 | 0 | 2
38958.4634 | 1 | 0 | 2
38958.4635 | 1 | 0 | 2
38958.4636 | 1 | 0 | 2
38958.4637 | 1 | 0 | 2
38958.4638 | 1 | 0 | 2
38958.4639 | 1 | 0 | 2
38958.464 | 1 | 0 | 2
38958.4641 | 1 | 0 | 2
38958.4642 | 1 | 0 | 2
38958.4643 | 1 | 0 | 2
38958.4644 | 1 | 0 | 2
38958.4645 | 1 | 0 | 2
38958.4646 | 1 | 0 | 2
38958.4647 | 1 | 0 | 2
38958.4648 | 1 | 0 | 2
38958.4649 | 1 | 0 | 2
38958.465 | 1 | 0 | 2
38958.4651 | 1 | 0 | 2
38958.4652 | 1 | 0 | 2
38958.4653 | 1 | 0 | 2
38958.4654 | 1 | 0 | 2
38958.4655 | 1 | 0 | 2
38958.4656 | 1 | 0 | 2
38958.4657 | 1 | 0 | 2
38958.4658 | 1 | 0 | 2
38958.4658 | 1 | 0 | 2
38958.4659 | 1 | 0 | 2
38958.466 | 1 | 0 | 2
38958.4661 | 2 | 1 | 2
38958.4662 | 21 | 19 | 2
38958.4663 | 1006 | 982 | 2
38958.4664 | 1011 | 988 | 2
38958.4665 | 1009 | 1056 | 2
38958.4666 | 951 | 990 | 2
38958.4667 | 1066 | 1150 | 2
38958.4668 | 1018 | 997 | 2
38958.4669 | 1156 | 1136 | 2
38958.467 | 979 | 957 | 2
38958.4671 | 2148 | 776 | 2
38958.4672 | 2394 | 4 | 2
38958.4673 | 2155 | 3 | 2
38958.4674 | 2254 | 2 | 2
38958.4675 | 1027 | 982 | 2
38958.4676 | 2060 | 3 | 2
38958.4677 | 1566 | 1050 | 2
38958.4678 | 2409 | 2 | 2
38958.4679 | 2069 | 1 | 2
38958.468 | 2378 | 1 | 2
38958.4681 | 2433 | 1 | 2
38958.4682 | 2557 | 1 | 2
38958.4683 | 2154 | 1 | 2
38958.4684 | 2084 | 1 | 2
38958.4685 | 2072 | 0 | 2
38958.4686 | 1987 | 0 | 2
38958.4687 | 2077 | 1 | 2
38958.4688 | 2472 | 0 | 2
38958.4689 | 2336 | 0 | 2
38958.469 | 2128 | 0 | 2
38958.4691 | 2072 | 0 | 2
38958.4692 | 1984 | 0 | 2
38958.4692 | 2233 | 0 | 2
38958.4694 | 2296 | 0 | 2
38958.4694 | 2253 | 0 | 2
38958.4695 | 2132 | 0 | 2
38958.4696 | 2139 | 0 | 2
38958.4697 | 2202 | 0 | 2
38958.4698 | 2278 | 0 | 2
38958.4699 | 1976 | 0 | 2
38958.47 | 2105 | 0 | 2
38958.4701 | 2181 | 0 | 2
38958.4702 | 2509 | 0 | 2
38958.4703 | 2445 | 0 | 2
38958.4704 | 2423 | 0 | 2
38958.4705 | 2549 | 0 | 2
38958.4706 | 2210 | 0 | 2
38958.4707 | 2151 | 0 | 2
38958.4708 | 2425 | 0 | 2
38958.4709 | 2423 | 0 | 2
38958.471 | 2334 | 0 | 2
38958.4711 | 2098 | 0 | 2
38958.4712 | 2082 | 0 | 2
38958.4713 | 2377 | 0 | 2
38958.4714 | 2251 | 0 | 2
38958.4715 | 2029 | 0 | 2
38958.4716 | 1967 | 0 | 2
38958.4717 | 2381 | 0 | 2
38958.4718 | 2027 | 0 | 2
38958.4719 | 2108 | 0 | 2
38958.472 | 2354 | 0 | 2
38958.4721 | 2383 | 0 | 2
38958.4722 | 2449 | 0 | 2
38958.4723 | 2484 | 0 | 2
38958.4724 | 1968 | 0 | 2
2
38958.4619 | 1 | 0 | 3
38958.462 | 1 | 0 | 3
38958.4621 | 1 | 0 | 3
38958.4622 | 1 | 0 | 3
38958.4623 | 1 | 0 | 3
38958.4624 | 1 | 0 | 3
38958.4625 | 1 | 0 | 3
38958.4626 | 1 | 0 | 3
38958.4627 | 1 | 0 | 3
38958.4628 | 1 | 0 | 3
38958.4629 | 1 | 0 | 3
38958.463 | 1 | 0 | 3
38958.463 | 1 | 0 | 3
38958.4631 | 1 | 0 | 3
38958.4632 | 1 | 0 | 3
38958.4633 | 1 | 0 | 3
38958.4634 | 1 | 0 | 3
38958.4635 | 1 | 0 | 3
38958.4636 | 1 | 0 | 3
38958.4637 | 1 | 0 | 3
38958.4638 | 1 | 0 | 3
38958.4639 | 1 | 0 | 3
38958.464 | 1 | 0 | 3
38958.4641 | 1 | 0 | 3
38958.4642 | 1 | 0 | 3
38958.4643 | 1 | 0 | 3
38958.4644 | 1 | 0 | 3
38958.4645 | 1 | 0 | 3
38958.4646 | 1 | 0 | 3
38958.4647 | 1 | 0 | 3
38958.4648 | 1 | 0 | 3
38958.4649 | 1 | 0 | 3
38958.465 | 1 | 0 | 3
38958.4651 | 1 | 0 | 3
38958.4652 | 1 | 0 | 3
38958.4653 | 1 | 0 | 3
38958.4654 | 1 | 0 | 3
38958.4655 | 1 | 0 | 3
38958.4656 | 1 | 0 | 3
38958.4657 | 1 | 0 | 3
38958.4658 | 978 | 956 | 3
38958.4659 | 1 | 0 | 3
38958.466 | 1 | 0 | 3
38958.4661 | 1151 | 911 | 3
38958.4662 | 2 | 1 | 3
38958.4662 | 118 | 162 | 3
38958.4664 | 1104 | 1081 | 3
38958.4664 | 963 | 941 | 3
38958.4666 | 1084 | 1061 | 3
38958.4666 | 1113 | 1090 | 3
38958.4667 | 946 | 924 | 3
38958.4668 | 1090 | 1067 | 3
38958.4669 | 1031 | 1009 | 3
38958.467 | 968 | 946 | 3
38958.4671 | 2111 | 1054 | 3
38958.4672 | 2066 | 4 | 3
38958.4673 | 2096 | 3 | 3
38958.4674 | 2514 | 3 | 3
38958.4675 | 1134 | 1029 | 3
38958.4676 | 2021 | 3 | 3
38958.4677 | 2119 | 2 | 3
38958.4678 | 2531 | 2 | 3
38958.4679 | 2085 | 1 | 3
38958.468 | 2339 | 1 | 3
38958.4681 | 2128 | 1 | 3
38958.4682 | 2321 | 1 | 3
38958.4683 | 2308 | 0 | 3
38958.4684 | 2217 | 0 | 3
38958.4685 | 2221 | 0 | 3
38958.4686 | 2425 | 0 | 3
38958.4687 | 2228 | 0 | 3
38958.4688 | 2141 | 1 | 3
38958.4689 | 2481 | 0 | 3
38958.469 | 2035 | 0 | 3
38958.4691 | 1969 | 0 | 3
38958.4692 | 2083 | 0 | 3
38958.4693 | 2215 | 1 | 3
38958.4694 | 2458 | 0 | 3
38958.4695 | 2526 | 0 | 3
38958.4696 | 2425 | 0 | 3
38958.4697 | 2365 | 0 | 3
38958.4698 | 2375 | 0 | 3
38958.4698 | 2066 | 0 | 3
38958.47 | 2528 | 0 | 3
38958.47 | 2168 | 0 | 3
38958.4701 | 2316 | 0 | 3
38958.4702 | 2061 | 0 | 3
38958.4703 | 2209 | 0 | 3
38958.4704 | 2227 | 0 | 3
38958.4705 | 2160 | 0 | 3
38958.4706 | 2534 | 0 | 3
38958.4707 | 2132 | 0 | 3
38958.4708 | 2501 | 0 | 3
38958.4709 | 2404 | 0 | 3
38958.471 | 2546 | 0 | 3
38958.4711 | 2035 | 0 | 3
38958.4712 | 2296 | 0 | 3
38958.4713 | 2376 | 0 | 3
38958.4714 | 2275 | 0 | 3
38958.4715 | 2460 | 0 | 3
38958.4716 | 2155 | 0 | 3
38958.4717 | 2395 | 0 | 3
38958.4718 | 2172 | 0 | 3
38958.4719 | 2408 | 0 | 3
38958.472 | 2181 | 0 | 3
38958.4721 | 2360 | 0 | 3
38958.4722 | 2171 | 0 | 3
38958.4723 | 2183 | 0 | 3
38958.4724 | 1961 | 0 | 3
3
38958.4619 | 1 | 0 | 4
38958.462 | 1 | 0 | 4
38958.4621 | 1 | 0 | 4
38958.4622 | 1 | 0 | 4
38958.4623 | 1 | 0 | 4
38958.4624 | 1 | 0 | 4
38958.4625 | 1 | 0 | 4
38958.4626 | 1 | 0 | 4
38958.4627 | 1 | 0 | 4
38958.4628 | 1 | 0 | 4
38958.4629 | 1 | 0 | 4
38958.463 | 1 | 0 | 4
38958.4631 | 1 | 0 | 4
38958.4632 | 1 | 0 | 4
38958.4633 | 1 | 0 | 4
38958.4634 | 1 | 0 | 4
38958.4634 | 1 | 0 | 4
38958.4636 | 1 | 0 | 4
38958.4636 | 1 | 0 | 4
38958.4638 | 1 | 0 | 4
38958.4638 | 1 | 0 | 4
38958.4639 | 1 | 0 | 4
38958.464 | 1 | 0 | 4
38958.4641 | 1 | 0 | 4
38958.4642 | 1 | 0 | 4
38958.4643 | 1 | 0 | 4
38958.4644 | 1 | 0 | 4
38958.4645 | 1 | 0 | 4
38958.4646 | 1 | 0 | 4
38958.4647 | 1 | 0 | 4
38958.4648 | 1 | 0 | 4
38958.4649 | 1 | 0 | 4
38958.465 | 1 | 0 | 4
38958.4651 | 1 | 0 | 4
38958.4652 | 1 | 0 | 4
38958.4653 | 1 | 0 | 4
38958.4654 | 1 | 0 | 4
38958.4655 | 1 | 0 | 4
38958.4656 | 1 | 0 | 4
38958.4657 | 1 | 0 | 4
38958.4658 | 1095 | 1071 | 4
38958.4659 | 1 | 0 | 4
38958.466 | 1 | 0 | 4
38958.4661 | 924 | 931 | 4
38958.4662 | 2 | 1 | 4
38958.4663 | 1156 | 1187 | 4
38958.4664 | 1106 | 1170 | 4
38958.4665 | 1024 | 1001 | 4
38958.4666 | 988 | 965 | 4
38958.4667 | 1191 | 1023 | 4
38958.4668 | 962 | 1004 | 4
38958.4669 | 964 | 943 | 4
38958.467 | 1110 | 1165 | 4
38958.467 | 1011 | 988 | 4
38958.4672 | 1694 | 667 | 4
38958.4672 | 1992 | 4 | 4
38958.4673 | 2009 | 3 | 4
38958.4674 | 2340 | 2 | 4
38958.4675 | 1085 | 842 | 4
38958.4676 | 2387 | 2 | 4
38958.4677 | 1181 | 1127 | 4
38958.4678 | 1980 | 1 | 4
38958.4679 | 2258 | 1 | 4
38958.468 | 2534 | 1 | 4
38958.4681 | 2256 | 1 | 4
38958.4682 | 2277 | 1 | 4
38958.4683 | 2547 | 1 | 4
38958.4684 | 2554 | 1 | 4
38958.4685 | 2475 | 14 | 4
38958.4686 | 2071 | 0 | 4
38958.4687 | 2431 | 1 | 4
38958.4688 | 2316 | 1 | 4
38958.4689 | 2086 | 0 | 4
38958.469 | 2204 | 0 | 4
38958.4691 | 2067 | 0 | 4
38958.4692 | 2161 | 0 | 4
38958.4693 | 2201 | 0 | 4
38958.4694 | 2303 | 0 | 4
38958.4695 | 2068 | 1 | 4
38958.4696 | 2112 | 0 | 4
38958.4697 | 2399 | 0 | 4
38958.4698 | 2009 | 0 | 4
38958.4699 | 2528 | 0 | 4
38958.47 | 2393 | 0 | 4
38958.4701 | 2098 | 0 | 4
38958.4702 | 2545 | 0 | 4
38958.4703 | 2545 | 0 | 4
38958.4704 | 2000 | 0 | 4
38958.4705 | 2482 | 0 | 4
38958.4705 | 2129 | 0 | 4
38958.4706 | 1972 | 0 | 4
38958.4707 | 2378 | 1 | 4
38958.4708 | 2346 | 0 | 4
38958.4709 | 2093 | 2 | 4
38958.471 | 2489 | 0 | 4
38958.4711 | 2202 | 0 | 4
38958.4712 | 2068 | 0 | 4
38958.4713 | 2311 | 0 | 4
38958.4714 | 2522 | 0 | 4
38958.4715 | 2360 | 0 | 4
38958.4716 | 2002 | 0 | 4
38958.4717 | 2280 | 0 | 4
38958.4718 | 2512 | 0 | 4
38958.4719 | 2094 | 0 | 4
38958.472 | 1968 | 0 | 4
38958.4721 | 2007 | 0 | 4
38958.4722 | 2448 | 0 | 4
38958.4723 | 2349 | 0 | 4
38958.4724 | 1996 | 0 | 4
4
38958.4619 | 1 | 0 | 5
38958.462 | 1 | 0 | 5
38958.4621 | 1 | 0 | 5
38958.4622 | 1 | 0 | 5
38958.4623 | 1 | 0 | 5
38958.4624 | 1 | 0 | 5
38958.4625 | 1 | 0 | 5
38958.4626 | 1 | 0 | 5
38958.4627 | 1 | 0 | 5
38958.4628 | 1 | 0 | 5
38958.4629 | 1 | 0 | 5
38958.463 | 1 | 0 | 5
38958.4631 | 1 | 0 | 5
38958.4632 | 1 | 0 | 5
38958.4633 | 1 | 0 | 5
38958.4634 | 1 | 0 | 5
38958.4635 | 1 | 0 | 5
38958.4636 | 1 | 0 | 5
38958.4637 | 1 | 0 | 5
38958.4638 | 1 | 0 | 5
38958.4639 | 1 | 0 | 5
38958.464 | 1 | 0 | 5
38958.4641 | 1 | 0 | 5
38958.4642 | 1 | 0 | 5
38958.4642 | 1 | 0 | 5
38958.4643 | 1 | 0 | 5
38958.4644 | 1 | 0 | 5
38958.4645 | 1 | 0 | 5
38958.4646 | 1 | 0 | 5
38958.4647 | 1 | 0 | 5
38958.4648 | 1 | 0 | 5
38958.4649 | 1 | 0 | 5
38958.465 | 1 | 0 | 5
38958.4651 | 1 | 0 | 5
38958.4652 | 1 | 0 | 5
38958.4653 | 1 | 0 | 5
38958.4654 | 1 | 0 | 5
38958.4655 | 1 | 0 | 5
38958.4656 | 1 | 0 | 5
38958.4657 | 1 | 0 | 5
38958.4658 | 1 | 3 | 5
38958.4659 | 920 | 955 | 5
38958.466 | 1 | 0 | 5
38958.4661 | 2 | 4 | 5
38958.4662 | 1087 | 1142 | 5
38958.4663 | 1072 | 1050 | 5
38958.4664 | 966 | 944 | 5
38958.4665 | 1060 | 1147 | 5
38958.4666 | 1090 | 1067 | 5
38958.4667 | 1155 | 1133 | 5
38958.4668 | 1041 | 1019 | 5
38958.4669 | 1179 | 1130 | 5
38958.467 | 1006 | 983 | 5
38958.4671 | 1897 | 1065 | 5
38958.4672 | 2492 | 4 | 5
38958.4673 | 1989 | 4 | 5
38958.4674 | 2025 | 2 | 5
38958.4675 | 2538 | 2 | 5
38958.4676 | 974 | 924 | 5
38958.4677 | 2415 | 2 | 5
38958.4677 | 2534 | 7 | 5
38958.4678 | 2027 | 1 | 5
38958.4679 | 2140 | 1 | 5
38958.468 | 2167 | 1 | 5
38958.4681 | 2316 | 1 | 5
38958.4682 | 2358 | 1 | 5
38958.4683 | 2562 | 0 | 5
38958.4684 | 2545 | 1 | 5
38958.4685 | 2507 | 0 | 5
38958.4686 | 2025 | 0 | 5
38958.4687 | 2341 | 0 | 5
38958.4688 | 2546 | 0 | 5
38958.4689 | 2059 | 0 | 5
38958.469 | 2349 | 0 | 5
38958.4691 | 2465 | 1 | 5
38958.4692 | 2552 | 0 | 5
38958.4693 | 2495 | 0 | 5
38958.4694 | 2557 | 0 | 5
38958.4695 | 2461 | 0 | 5
38958.4696 | 2234 | 0 | 5
38958.4697 | 2187 | 0 | 5
38958.4698 | 2055 | 0 | 5
38958.4699 | 2554 | 0 | 5
38958.47 | 2486 | 0 | 5
38958.4701 | 2367 | 0 | 5
38958.4702 | 2242 | 0 | 5
38958.4703 | 2484 | 0 | 5
38958.4704 | 2179 | 0 | 5
38958.4705 | 2074 | 0 | 5
38958.4706 | 2348 | 0 | 5
38958.4707 | 2462 | 0 | 5
38958.4708 | 2492 | 0 | 5
38958.4709 | 2240 | 0 | 5
38958.471 | 2242 | 0 | 5
38958.4711 | 2187 | 0 | 5
38958.4711 | 2419 | 0 | 5
38958.4713 | 2453 | 0 | 5
38958.4713 | 2163 | 0 | 5
38958.4714 | 2181 | 0 | 5
38958.4715 | 2205 | 0 | 5
38958.4716 | 2407 | 0 | 5
38958.4717 | 2547 | 0 | 5
38958.4718 | 2113 | 0 | 5
38958.4719 | 2199 | 0 | 5
38958.472 | 2224 | 0 | 5
38958.4721 | 1963 | 0 | 5
38958.4722 | 2538 | 0 | 5
38958.4723 | 2535 | 0 | 5
38958.4724 | 2052 | 0 | 5
5
38958.4619 | 1 | 0 | 6
38958.462 | 1 | 0 | 6
38958.4621 | 1 | 0 | 6
38958.4622 | 1 | 0 | 6
38958.4623 | 1 | 0 | 6
38958.4624 | 1 | 0 | 6
38958.4625 | 1 | 0 | 6
38958.4626 | 1 | 0 | 6
38958.4627 | 1 | 0 | 6
38958.4628 | 1 | 0 | 6
38958.4629 | 1 | 0 | 6
38958.463 | 1 | 0 | 6
38958.4631 | 1 | 0 | 6
38958.4632 | 1 | 0 | 6
38958.4633 | 1 | 0 | 6
38958.4634 | 1 | 0 | 6
38958.4635 | 1 | 0 | 6
38958.4636 | 1 | 0 | 6
38958.4637 | 1 | 0 | 6
38958.4638 | 1 | 0 | 6
38958.4639 | 1 | 0 | 6
38958.464 | 1 | 0 | 6
38958.4641 | 1 | 0 | 6
38958.4642 | 1 | 0 | 6
38958.4643 | 1 | 0 | 6
38958.4644 | 1 | 0 | 6
38958.4645 | 1 | 0 | 6
38958.4646 | 1 | 0 | 6
38958.4647 | 1 | 0 | 6
38958.4647 | 1 | 0 | 6
38958.4648 | 1 | 0 | 6
38958.4649 | 1 | 0 | 6
38958.465 | 1 | 0 | 6
38958.4651 | 1 | 0 | 6
38958.4652 | 1 | 0 | 6
38958.4653 | 1 | 0 | 6
38958.4654 | 1 | 0 | 6
38958.4655 | 1 | 0 | 6
38958.4656 | 1 | 0 | 6
38958.4657 | 1 | 0 | 6
38958.4658 | 1 | 1 | 6
38958.4659 | 2 | 3 | 6
38958.466 | 1 | 0 | 6
38958.4661 | 1 | 1 | 6
38958.4662 | 1127 | 1176 | 6
38958.4663 | 952 | 991 | 6
38958.4664 | 1049 | 1026 | 6
38958.4665 | 947 | 926 | 6
38958.4666 | 1189 | 1178 | 6
38958.4667 | 1090 | 1069 | 6
38958.4668 | 1185 | 1167 | 6
38958.4669 | 948 | 925 | 6
38958.467 | 1156 | 1135 | 6
38958.4671 | 2197 | 678 | 6
38958.4672 | 1987 | 4 | 6
38958.4673 | 1972 | 3 | 6
38958.4674 | 2475 | 3 | 6
38958.4675 | 2524 | 3 | 6
38958.4676 | 2182 | 3 | 6
38958.4677 | 2371 | 2 | 6
38958.4678 | 2400 | 3 | 6
38958.4679 | 2008 | 1 | 6
38958.468 | 2403 | 1 | 6
38958.4681 | 2116 | 1 | 6
38958.4681 | 2179 | 1 | 6
38958.4683 | 2219 | 0 | 6
38958.4683 | 2519 | 1 | 6
38958.4684 | 2364 | 0 | 6
38958.4685 | 2360 | 1 | 6
38958.4686 | 2088 | 0 | 6
38958.4687 | 2488 | 1 | 6
38958.4688 | 2501 | 0 | 6
38958.4689 | 2523 | 0 | 6
38958.469 | 2211 | 0 | 6
38958.4691 | 2311 | 0 | 6
38958.4692 | 2551 | 0 | 6
38958.4693 | 2008 | 0 | 6
38958.4694 | 2209 | 0 | 6
38958.4695 | 1990 | 0 | 6
38958.4696 | 2459 | 0 | 6
38958.4697 | 2193 | 0 | 6
38958.4698 | 2540 | 0 | 6
38958.4699 | 2028 | 0 | 6
38958.47 | 2428 | 0 | 6
38958.4701 | 2530 | 0 | 6
38958.4702 | 2133 | 0 | 6
38958.4703 | 2233 | 0 | 6
38958.4704 | 2377 | 0 | 6
38958.4705 | 2535 | 0 | 6
38958.4706 | 2071 | 0 | 6
38958.4707 | 2015 | 0 | 6
38958.4708 | 1973 | 0 | 6
38958.4709 | 2487 | 0 | 6
38958.471 | 2017 | 0 | 6
38958.4711 | 2543 | 0 | 6
38958.4712 | 2533 | 0 | 6
38958.4713 | 2542 | 0 | 6
38958.4714 | 1966 | 0 | 6
38958.4715 | 2456 | 0 | 6
38958.4716 | 1978 | 0 | 6
38958.4717 | 2485 | 0 | 6
38958.4717 | 1991 | 0 | 6
38958.4718 | 2082 | 0 | 6
38958.4719 | 2132 | 0 | 6
38958.472 | 2524 | 0 | 6
38958.4721 | 2053 | 0 | 6
38958.4722 | 2267 | 0 | 6
38958.4723 | 2427 | 0 | 6
38958.4724 | 2041 | 0 | 6
6