## Test Conditions
DESIREE-FIRE Intermediate Scale Test Number 7 - Circuit Simulator Data Only
Test Date: | 2010-03-09
DCSim DAQ Start Time | 13:14
DCSim Time for Synchronization | 13:16
Heat Source Synchronization | 0:00 | hour:minutes:seconds
Heat Source DAQ Start Time | 13:15
Heat Source Start Time | 14:00
DCSim Offset | 0:46 | hour:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 2760 | seconds
Heat Source Offset | 0:45 | hour:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 2695 | seconds
Heat Source Stop Time | 14:40
Test Duration | 0:40 | hour:minutes:seconds
| 2400 | seconds
CT500 Turns | 2 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 Turns | 5 | 1 or 5
Pre-Test Baseline: | Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
SWGR Close | PE/PVC, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 8, 9, and 10 represents the air temperature 3', 5', and 7' down the tray located in D Position. These are labeled as "D Position - 3'", "D Position - Middle", " D Position - 7'", respectively.
SWGR Trip | PE/PVC, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 8, 9, and 10 represents the air temperature 3', 5', and 7' down the tray located in D Position. These are labeled as "D Position - 3'", "D Position - Middle", " D Position - 7'", respectively.
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | SWGR_CT500 | SWGR-a_CT35_1_PC | SWGR-a_CT35_2_N1 | SWGR-b_CT35_1_PT | SWGR-b_CT35_2_G | SWGR-b_CT35_3_R | SWGR-b_CT35_4_N2 | SWGR-a_VT7_1_C1 | SWGR-a_VTU_1_PC | SWGR-a_VTU_2_N1 | SWGR-b_VT7_1_G | SWGR-b_VT7_2_R | SWGR-b_VT7_3_T | SWGR-b_VT7_4_SP | SWGR-b_VT7_5_SP | SWGR-b_VTU_1_PT | SWGR-b_VTU_2_N2 | {SWGR-C} V(N1) - V(Batt -) | {SWGR-C} V(PC) - V(Batt +) | {SWGR-C} V(C1) - V(Batt +) | {SWGR-T} V(G) - V(Batt -) | {SWGR-T} V(R) - V(Batt +) | {SWGR-T} V(N2) - V(Batt -) | {SWGR-T} V(PT) - V(Batt +) | {SWGR-C} V(C1) - V(N1) | {SWGR-T} V(SP1) - V(Batt -) | {SWGR-T} V(SP2) - V(Batt -) | {SWGR-T} V(R) - V(Batt -) | {SWGR-T} V(PC) - V(Batt -) | {SWGR-T} V(C1) - V(Batt -) | {SWGR-T} V(PT) - V(Batt -) | {SWGR-T} V(T) - V(Batt -) | {SWGR-T} V(N2) - V(Batt -) | {SWGR-C} V(PC) - V(Batt -) | {SWGR-C} V(C1) - V(Batt -) | {SWGR-T} V(T) - V(Batt -) | {SWGR-T} V(R) - V(Batt -) | {SWGR-T} V(PT) - V(Batt -) | {SWGR-C} V(N1) - V(Batt +) | {SWGR-T} V(N2) - V(Batt +)
-0.8125 | 121.9803 | -60.9421 | 60.9146 | -0.005951 | 0.021522 | 0.019944 | 0.004202 | -0.0049796 | 0.062948 | 0.068802 | 0.26093 | 60.9512 | -61.1389 | 60.9283 | -60.8826 | -61.116 | 0.036621 | 0.20599 | 61.0062 | -61.0703 | -0.19684 | 0.036621 | 61.203 | 121.8704 | -121.7972 | -0.12817 | 0.091553 | 61.3998 | 60.9787 | 61.1481 | 0.05951 | 121.8933 | 61.203 | 121.9482 | -0.17395 | -0.12817 | 121.8933 | 61.203 | -0.17395 | 0.05951 | 121.9482 | -122.0535 | -121.9849
0.9375 | 122.0352 | -60.9192 | 60.9375 | 0.0016785 | 0.022804 | 0.016526 | -0.00092499 | -0.0069022 | 0.063376 | 0.070724 | 0.24261 | 61.0016 | -61.1343 | 60.9467 | -60.8597 | -61.1069 | 0.09613 | 0.21515 | 61.0336 | -61.1069 | -0.21515 | 0.064087 | 61.1618 | 121.8658 | -121.7972 | -0.18768 | 0.09613 | 61.377 | 61.0153 | 61.1343 | 0.059509 | 121.9208 | 61.1618 | 121.9528 | -0.18768 | -0.18768 | 121.9208 | 61.1618 | -0.18768 | 0.059509 | 121.9528 | -122.0718 | -122.0444
2.6094 | 122.0718 | -60.8917 | 60.9055 | 0.009308 | 0.017464 | 0.013749 | -0.0030612 | -0.0056204 | 0.066153 | 0.069015 | 0.23346 | 60.8917 | -61.1023 | 60.965 | -60.8139 | -61.0474 | -0.10529 | 0.28381 | 60.9329 | -61.0794 | -0.21057 | -0.013733 | 61.1252 | 121.8567 | -121.7194 | -0.18768 | 0.027465 | 61.3358 | 60.7864 | 61.1755 | 0.07782 | 121.7834 | 61.1252 | 121.8246 | -0.15564 | -0.18768 | 121.7834 | 61.1252 | -0.15564 | 0.07782 | 121.8246 | -122.0078 | -121.9849
4.3438 | 121.9666 | -60.9375 | 60.9375 | -0.005951 | 0.02195 | 0.01503 | 0.0063382 | -0.0049796 | 0.064016 | 0.068374 | 0.27924 | 60.9833 | -61.1481 | 60.9512 | -60.8322 | -61.0886 | 0.032043 | 0.2243 | 61.0153 | -61.0703 | -0.21057 | 0.045776 | 61.2167 | 121.8887 | -121.7697 | -0.13275 | 0.07782 | 61.4273 | 60.9695 | 61.1618 | 0.10529 | 121.9208 | 61.2167 | 121.9528 | -0.15106 | -0.13275 | 121.9208 | 61.2167 | -0.15106 | 0.10529 | 121.9528 | -122.0856 | -122.0078
6.0938 | 122.1222 | -60.9146 | 60.8826 | 0.0016785 | 0.021522 | 0.015671 | -0.0047702 | -0.0094656 | 0.067007 | 0.069015 | 0.13733 | 60.9146 | -61.1389 | 60.878 | -60.8688 | -61.1114 | -0.10071 | 0.16937 | 60.9375 | -61.1252 | -0.2243 | 0.032044 | 61.0519 | 121.7926 | -121.7514 | -0.21057 | 0.054932 | 61.2762 | 60.8139 | 61.084 | 0.045777 | 121.8292 | 61.0519 | 121.8521 | -0.19684 | -0.21057 | 121.8292 | 61.0519 | -0.19684 | 0.045777 | 121.8521 | -122.0215 | -122.0078
7.8281 | 121.9894 | -60.9695 | 60.9238 | 0.0016785 | 0.0196 | 0.013535 | -0.00071139 | -0.008184 | 0.065725 | 0.068802 | 0.21973 | 60.8917 | -61.1298 | 60.9238 | -60.8459 | -61.084 | -0.19684 | 0.17395 | 60.9146 | -61.0977 | -0.16022 | -0.032043 | 61.1893 | 121.8933 | -121.7697 | -0.12817 | -0.009155 | 61.3495 | 60.7727 | 61.1435 | 0.1236 | 121.8613 | 61.1893 | 121.8842 | -0.11444 | -0.12817 | 121.8613 | 61.1893 | -0.11444 | 0.1236 | 121.8842 | -122.0535 | -122.0215
9.5469 | 122.0993 | -60.878 | 60.9375 | -0.005951 | 0.019173 | 0.018876 | 0.0046292 | -0.008184 | 0.064016 | 0.067947 | 0.21515 | 61.0291 | -61.1481 | 60.9055 | -60.8963 | -61.1526 | 0.12817 | 0.18768 | 61.0062 | -61.1069 | -0.27008 | 0.091553 | 61.0931 | 121.7834 | -121.8338 | -0.22888 | 0.068665 | 61.3632 | 61.0062 | 61.0657 | -0.01831 | 121.907 | 61.0931 | 121.8842 | -0.27466 | -0.22888 | 121.907 | 61.0931 | -0.27466 | -0.01831 | 121.8842 | -122.0856 | -122.0444
11.2188 | 122.0261 | -60.9421 | 60.91 | 0.009308 | 0.020241 | 0.020157 | 0.001852 | -0.0062614 | 0.064444 | 0.071792 | 0.17853 | 60.9787 | -61.1435 | 60.8459 | -60.9421 | -61.1893 | 0.050354 | 0.11444 | 60.9924 | -61.084 | -0.20142 | 0.068665 | 61.1206 | 121.788 | -121.8521 | -0.14191 | 0.082398 | 61.322 | 60.9924 | 61.0565 | 0 | 121.9208 | 61.1206 | 121.9345 | -0.24719 | -0.14191 | 121.9208 | 61.1206 | -0.24719 | 0 | 121.9345 | -122.0535 | -121.994
12.9531 | 122.0718 | -60.8917 | 60.9055 | -0.005951 | 0.020027 | 0.011826 | -0.004343 | -0.0088248 | 0.06423 | 0.06752 | 0.20599 | 60.9375 | -61.1206 | 60.9467 | -60.8231 | -61.0565 | -0.12817 | 0.25177 | 60.9512 | -61.084 | -0.22888 | 0.032043 | 61.0977 | 121.8384 | -121.7285 | -0.19226 | 0.045776 | 61.3266 | 60.7636 | 61.1435 | 0.068665 | 121.8292 | 61.0977 | 121.843 | -0.16479 | -0.19226 | 121.8292 | 61.0977 | -0.16479 | 0.068665 | 121.843 | -122.0261 | -121.9894
14.625 | 122.0856 | -60.9146 | 60.878 | -0.005951 | 0.018532 | 0.014176 | -0.00028419 | -0.0083976 | 0.067007 | 0.068374 | 0.13733 | 60.9192 | -61.1526 | 60.8643 | -60.8963 | -61.1298 | -0.10529 | 0.12817 | 60.9421 | -61.1526 | -0.23804 | 0.041198 | 61.0519 | 121.7789 | -121.7743 | -0.23804 | 0.064087 | 61.29 | 60.8093 | 61.0428 | 0.018311 | 121.8338 | 61.0519 | 121.8567 | -0.21515 | -0.23804 | 121.8338 | 61.0519 | -0.21515 | 0.018311 | 121.8567 | -122.0306 | -122.0306
16.375 | 122.1085 | -60.8826 | 60.9009 | -0.013581 | 0.021095 | 0.012467 | 0.00078401 | -0.0094656 | 0.065084 | 0.065597 | 0.17853 | 60.9467 | -61.1435 | 60.8871 | -60.8917 | -61.1481 | 0.10071 | 0.20142 | 61.0291 | -61.084 | -0.26093 | 0.045776 | 61.0611 | 121.7697 | -121.7926 | -0.20142 | 0.12817 | 61.322 | 60.9833 | 61.084 | -0.009156 | 121.8292 | 61.0611 | 121.9116 | -0.2655 | -0.20142 | 121.8292 | 61.0611 | -0.2655 | -0.009156 | 121.9116 | -122.0444 | -121.9849
18.1094 | 122.0856 | -60.9055 | 60.8734 | 0.0016785 | 0.016823 | 0.018021 | -0.0011386 | -0.0096794 | 0.065298 | 0.068802 | 0.15564 | 60.9009 | -61.171 | 60.8688 | -60.9009 | -61.1252 | -0.10986 | 0.15106 | 60.9238 | -61.116 | -0.2655 | 0.027466 | 61.0611 | 121.7743 | -121.7743 | -0.21057 | 0.050354 | 61.3266 | 60.7956 | 61.0565 | 0.004578 | 121.8063 | 61.0611 | 121.8292 | -0.21973 | -0.21057 | 121.8063 | 61.0611 | -0.21973 | 0.004578 | 121.8292 | -122.0444 | -121.9894
19.8438 | 121.9986 | -60.9375 | 60.9009 | 0.0016785 | 0.020882 | 0.018448 | 0.0029202 | -0.0054068 | 0.063589 | 0.067734 | 0.19684 | 60.997 | -61.1481 | 60.8734 | -60.9192 | -61.1298 | -0.050354 | 0.12817 | 60.9924 | -61.116 | -0.21057 | 0.09613 | 61.1343 | 121.8109 | -121.8201 | -0.17853 | 0.091553 | 61.3449 | 60.8871 | 61.0657 | 0.018311 | 121.9345 | 61.1343 | 121.9299 | -0.19226 | -0.17853 | 121.9345 | 61.1343 | -0.19226 | 0.018311 | 121.9299 | -122.049 | -122.0169
21.5312 | 122.0627 | -60.9329 | 60.878 | 0.0016785 | 0.018745 | 0.016526 | 0.00099761 | -0.008184 | 0.064657 | 0.06752 | 0.18768 | 60.8963 | -61.1206 | 60.8826 | -60.8734 | -61.1023 | -0.11902 | 0.15564 | 60.9512 | -61.1206 | -0.18768 | 0.01831 | 61.1206 | 121.8155 | -121.7514 | -0.18768 | 0.073242 | 61.3083 | 60.8139 | 61.0886 | 0.059509 | 121.8292 | 61.1206 | 121.8842 | -0.16937 | -0.18768 | 121.8292 | 61.1206 | -0.16937 | 0.059509 | 121.8842 | -121.9986 | -121.9986
23.2812 | 121.9986 | -60.9604 | 60.9192 | -0.005951 | 0.023018 | 0.019944 | 0.003561 | -0.0054068 | 0.065512 | 0.067306 | 0.18768 | 61.0016 | -61.1435 | 60.8734 | -60.9329 | -61.1572 | 0.009155 | 0.10529 | 61.0107 | -61.0886 | -0.18311 | 0.082398 | 61.1481 | 121.8338 | -121.8521 | -0.12817 | 0.091553 | 61.3312 | 60.9695 | 61.0657 | 0.027466 | 121.962 | 61.1481 | 121.9711 | -0.19684 | -0.12817 | 121.962 | 61.1481 | -0.19684 | 0.027466 | 121.9711 | -122.0627 | -122.0078
25.0156 | 121.9528 | -60.965 | 60.878 | 0.0016785 | 0.0196 | 0.018876 | -0.00049779 | -0.005834 | 0.064016 | 0.070724 | 0.26093 | 60.9192 | -61.116 | 60.9467 | -60.8322 | -61.0474 | -0.21057 | 0.19684 | 60.9238 | -61.0977 | -0.15106 | 0.041198 | 61.2259 | 121.9116 | -121.7102 | -0.13275 | 0.045776 | 61.377 | 60.7544 | 61.1618 | 0.13275 | 121.8842 | 61.2259 | 121.8887 | -0.082397 | -0.13275 | 121.8842 | 61.2259 | -0.082397 | 0.13275 | 121.8887 | -121.994 | -121.9757
26.6875 | 121.9849 | -60.9375 | 60.8963 | -0.013581 | 0.019173 | 0.016953 | 0.00057041 | -0.006475 | 0.067007 | 0.068802 | 0.21515 | 60.878 | -61.1389 | 60.8917 | -60.8551 | -61.0931 | -0.17853 | 0.17853 | 60.9009 | -61.0931 | -0.20142 | -0.01831 | 61.1526 | 121.8292 | -121.7514 | -0.15564 | 0.004578 | 61.3541 | 60.759 | 61.116 | 0.082397 | 121.8155 | 61.1526 | 121.8384 | -0.15564 | -0.15564 | 121.8155 | 61.1526 | -0.15564 | 0.082397 | 121.8384 | -122.0352 | -121.9894
28.4219 | 122.0398 | -60.8871 | 60.9238 | -0.005951 | 0.017891 | 0.014817 | -0.0011386 | -0.010107 | 0.062735 | 0.068374 | 0.22888 | 60.9055 | -61.1114 | 60.9833 | -60.8139 | -61.0428 | -0.07782 | 0.28839 | 60.9512 | -61.0794 | -0.2243 | -0.01831 | 61.116 | 121.8704 | -121.7377 | -0.19226 | 0.027466 | 61.3403 | 60.8093 | 61.1755 | 0.073242 | 121.7926 | 61.116 | 121.8384 | -0.15564 | -0.19226 | 121.7926 | 61.116 | -0.15564 | 0.073242 | 121.8384 | -122.0352 | -122.0032
30.0938 | 121.962 | -60.9375 | 60.8826 | 0.0016785 | 0.018745 | 0.015458 | 0.0020658 | -0.009252 | 0.063376 | 0.068588 | 0.23804 | 60.9238 | -61.116 | 60.9238 | -60.8459 | -61.0748 | -0.19226 | 0.1831 | 60.9192 | -61.116 | -0.17853 | 0.041199 | 61.1755 | 121.8613 | -121.7285 | -0.17853 | 0.036621 | 61.3541 | 60.7452 | 61.1206 | 0.091553 | 121.8613 | 61.1755 | 121.8567 | -0.13733 | -0.17853 | 121.8613 | 61.1755 | -0.13733 | 0.091553 | 121.8567 | -121.9986 | -121.9986
31.8594 | 121.9391 | -60.9375 | 60.9421 | -0.005951 | 0.020668 | 0.018235 | 0.005911 | -0.0062614 | 0.058676 | 0.06987 | 0.24719 | 60.9467 | -61.1343 | 60.9512 | -60.8505 | -61.0886 | 0.032043 | 0.25635 | 61.0245 | -61.0565 | -0.19684 | 0.004577 | 61.1847 | 121.8887 | -121.7926 | -0.11902 | 0.082397 | 61.3815 | 60.9695 | 61.1938 | 0.086975 | 121.8842 | 61.1847 | 121.962 | -0.15106 | -0.11902 | 121.8842 | 61.1847 | -0.15106 | 0.086975 | 121.962 | -122.0764 | -121.9986
33.5938 | 122.0581 | -60.878 | 60.9192 | 0.009308 | 0.020027 | 0.017167 | -0.0028476 | -0.0062614 | 0.064871 | 0.067947 | 0.23804 | 60.9604 | -61.1252 | 60.9329 | -60.8368 | -61.0794 | 0.004578 | 0.26093 | 60.9467 | -61.1023 | -0.24719 | 0.041199 | 61.116 | 121.8109 | -121.756 | -0.2243 | 0.027466 | 61.3632 | 60.8826 | 61.1389 | 0.041199 | 121.8384 | 61.116 | 121.8246 | -0.20142 | -0.2243 | 121.8384 | 61.116 | -0.20142 | 0.041199 | 121.8246 | -122.0444 | -122.0215
35.3281 | 121.9528 | -60.9467 | 60.8963 | 0.0016785 | 0.022163 | 0.018235 | 0.0014248 | -0.0049796 | 0.064444 | 0.069656 | 0.24261 | 60.9192 | -61.1206 | 60.9558 | -60.8276 | -61.0474 | -0.20599 | 0.20142 | 60.9146 | -61.0931 | -0.17395 | 0.022888 | 61.1893 | 121.9025 | -121.7239 | -0.14648 | 0.018311 | 61.3632 | 60.7407 | 61.1481 | 0.11902 | 121.8658 | 61.1893 | 121.8613 | -0.10071 | -0.14648 | 121.8658 | 61.1893 | -0.10071 | 0.11902 | 121.8613 | -122.0169 | -121.9894
37 | 122.0718 | -60.8917 | 60.8643 | 0.0016785 | 0.021736 | 0.015244 | -0.0022068 | -0.008184 | 0.066153 | 0.06987 | 0.16022 | 60.9055 | -61.1252 | 60.8688 | -60.8917 | -61.1114 | -0.11444 | 0.15106 | 60.9283 | -61.1206 | -0.23346 | 0.041199 | 61.0519 | 121.7606 | -121.756 | -0.22888 | 0.064087 | 61.2854 | 60.7773 | 61.0428 | 0 | 121.7972 | 61.0519 | 121.8201 | -0.21973 | -0.22888 | 121.7972 | 61.0519 | -0.21973 | 0 | 121.8201 | -121.9894 | -121.9849
38.75 | 122.0581 | -60.9055 | 60.878 | -0.005951 | 0.018532 | 0.016953 | -0.002634 | -0.0090384 | 0.063589 | 0.069229 | 0.16479 | 60.9283 | -61.1298 | 60.9055 | -60.8551 | -61.0931 | -0.11444 | 0.19684 | 60.9283 | -61.0977 | -0.2243 | 0.050354 | 61.0703 | 121.8109 | -121.7331 | -0.19226 | 0.050354 | 61.2946 | 60.791 | 61.1023 | 0.050354 | 121.8338 | 61.0703 | 121.8338 | -0.18768 | -0.19226 | 121.8338 | 61.0703 | -0.18768 | 0.050354 | 121.8338 | -122.0078 | -121.9757
40.4844 | 122.0856 | -60.9055 | 60.8551 | -0.005951 | 0.017036 | 0.012253 | -0.00071139 | -0.0071158 | 0.063803 | 0.070297 | 0.16022 | 60.8688 | -61.1481 | 60.8643 | -60.8917 | -61.1069 | -0.10529 | 0.14648 | 60.9375 | -61.0794 | -0.24261 | 0.013732 | 61.0657 | 121.7697 | -121.7468 | -0.17395 | 0.082397 | 61.3083 | 60.8002 | 61.0519 | 0.013733 | 121.7743 | 61.0657 | 121.843 | -0.20142 | -0.17395 | 121.7743 | 61.0657 | -0.20142 | 0.013733 | 121.843 | -122.0032 | -121.9345
42.1562 | 121.9803 | -60.9421 | 60.8871 | -0.005951 | 0.020454 | 0.020157 | 0.0022794 | -0.006475 | 0.062948 | 0.06752 | 0.18768 | 60.9879 | -61.1481 | 60.878 | -60.91 | -61.1435 | -0.022888 | 0.11444 | 60.9787 | -61.0977 | -0.20599 | 0.10071 | 61.1298 | 121.8201 | -121.7972 | -0.15564 | 0.091553 | 61.3358 | 60.9192 | 61.0565 | 0.032044 | 121.9299 | 61.1298 | 121.9208 | -0.20142 | -0.15564 | 121.9299 | 61.1298 | -0.20142 | 0.032044 | 121.9208 | -122.0352 | -121.9849
43.9062 | 121.9482 | -60.9329 | 60.9329 | -0.013581 | 0.021736 | 0.019944 | 0.0050564 | -0.008184 | 0.064016 | 0.070297 | 0.23804 | 60.9604 | -61.1389 | 60.91 | -60.8734 | -61.1206 | 0.045776 | 0.1831 | 61.0107 | -61.0794 | -0.20599 | 0.027466 | 61.171 | 121.843 | -121.8063 | -0.14649 | 0.07782 | 61.377 | 60.9787 | 61.116 | 0.059509 | 121.8933 | 61.171 | 121.9437 | -0.18768 | -0.14649 | 121.8933 | 61.171 | -0.18768 | 0.059509 | 121.9437 | -122.0718 | -122.0123
45.6562 | 121.9391 | -60.9604 | 60.8917 | -0.005951 | 0.020454 | 0.016312 | 0.001852 | -0.0069022 | 0.064016 | 0.069015 | 0.25635 | 60.9192 | -61.1069 | 60.9421 | -60.8185 | -61.0519 | -0.19226 | 0.1831 | 60.9283 | -61.0748 | -0.14648 | 0.027465 | 61.2167 | 121.9025 | -121.7102 | -0.11444 | 0.036621 | 61.3632 | 60.7681 | 61.1435 | 0.14191 | 121.8796 | 61.2167 | 121.8887 | -0.091553 | -0.11444 | 121.8796 | 61.2167 | -0.091553 | 0.14191 | 121.8887 | -121.9986 | -121.9666
47.4062 | 121.9666 | -60.9238 | 60.9238 | -0.005951 | 0.021309 | 0.018876 | 0.0037748 | -0.005834 | 0.062735 | 0.069229 | 0.2243 | 60.9695 | -61.1206 | 60.8826 | -60.8963 | -61.1389 | 0.041199 | 0.15106 | 60.997 | -61.0886 | -0.19684 | 0.045776 | 61.1481 | 121.8063 | -121.8201 | -0.1648 | 0.073242 | 61.3449 | 60.965 | 61.0748 | 0.027466 | 121.8933 | 61.1481 | 121.9208 | -0.21515 | -0.1648 | 121.8933 | 61.1481 | -0.21515 | 0.027466 | 121.9208 | -122.0444 | -122.0123
49.0781 | 121.9482 | -60.9283 | 60.9009 | -0.013581 | 0.021736 | 0.017808 | 0.0031338 | -0.0062614 | 0.062521 | 0.068802 | 0.24719 | 60.9741 | -61.1389 | 60.9055 | -60.8643 | -61.1069 | 0.045776 | 0.1831 | 60.9924 | -61.0748 | -0.21057 | 0.073242 | 61.1755 | 121.8338 | -121.7651 | -0.14648 | 0.091553 | 61.3861 | 60.9741 | 61.1114 | 0.064087 | 121.9025 | 61.1755 | 121.9208 | -0.17853 | -0.14648 | 121.9025 | 61.1755 | -0.17853 | 0.064087 | 121.9208 | -122.0398 | -121.9757
50.8281 | 121.9849 | -60.9192 | 60.9055 | -0.005951 | 0.021522 | 0.016526 | 0.0031338 | -0.0069022 | 0.063589 | 0.068588 | 0.23346 | 60.9741 | -61.1069 | 60.91 | -60.8322 | -61.0931 | 0.068665 | 0.20599 | 60.997 | -61.0657 | -0.18768 | 0.068664 | 61.1526 | 121.8292 | -121.7377 | -0.14648 | 0.091552 | 61.3403 | 60.9879 | 61.1252 | 0.086975 | 121.8933 | 61.1526 | 121.9162 | -0.17395 | -0.14648 | 121.8933 | 61.1526 | -0.17395 | 0.086975 | 121.9162 | -122.0123 | -121.9711
52.4844 | 122.0444 | -60.8871 | 60.9146 | -0.005951 | 0.018318 | 0.018235 | -0.0045566 | -0.007543 | 0.065298 | 0.067306 | 0.23804 | 60.9375 | -61.0931 | 60.9421 | -60.7956 | -61.0611 | -0.013733 | 0.27924 | 60.9512 | -61.0657 | -0.20599 | 0.022888 | 61.1252 | 121.8292 | -121.7102 | -0.17853 | 0.036621 | 61.3312 | 60.8734 | 61.1664 | 0.091553 | 121.8246 | 61.1252 | 121.8384 | -0.17395 | -0.17853 | 121.8246 | 61.1252 | -0.17395 | 0.091553 | 121.8384 | -122.0078 | -121.9803
54.2188 | 122.0718 | -60.8963 | 60.8688 | 0.0016785 | 0.017464 | 0.015885 | -0.0041294 | -0.0060478 | 0.064657 | 0.066238 | 0.15106 | 60.9329 | -61.1069 | 60.8688 | -60.8505 | -61.0931 | -0.09613 | 0.1831 | 60.9558 | -61.0794 | -0.21057 | 0.064087 | 61.0474 | 121.7651 | -121.7194 | -0.18311 | 0.086976 | 61.2579 | 60.8002 | 61.0794 | 0.045776 | 121.8292 | 61.0474 | 121.8521 | -0.19684 | -0.18311 | 121.8292 | 61.0474 | -0.19684 | 0.045776 | 121.8521 | -121.9757 | -121.9482
55.8906 | 121.9757 | -60.9283 | 60.9329 | -0.013581 | 0.018959 | 0.019517 | 0.0046292 | -0.0054068 | 0.059957 | 0.068374 | 0.20142 | 60.9695 | -61.1389 | 60.8734 | -60.8963 | -61.1481 | 0.073242 | 0.15106 | 61.0291 | -61.0703 | -0.21057 | 0.036621 | 61.1298 | 121.8018 | -121.8292 | -0.14191 | 0.096131 | 61.3403 | 61.0016 | 61.0794 | 0.032044 | 121.8979 | 61.1298 | 121.9574 | -0.21973 | -0.14191 | 121.8979 | 61.1298 | -0.21973 | 0.032044 | 121.9574 | -122.0718 | -122.0032
57.625 | 122.0901 | -60.8688 | 60.8826 | -0.005951 | 0.021522 | 0.016526 | -0.0019932 | -0.0090384 | 0.06423 | 0.069443 | 0.20142 | 60.9421 | -61.0886 | 60.8734 | -60.8688 | -61.1343 | 0.10071 | 0.19226 | 61.0153 | -61.0931 | -0.21973 | 0.05951 | 61.0703 | 121.7422 | -121.7514 | -0.22431 | 0.13275 | 61.29 | 60.9695 | 61.0611 | 0 | 121.8109 | 61.0703 | 121.8842 | -0.2655 | -0.22431 | 121.8109 | 61.0703 | -0.2655 | 0 | 121.8842 | -121.9711 | -121.9757
59.2969 | 122.0261 | -60.8963 | 60.8597 | -0.013581 | 0.017891 | 0.015244 | -0.0045566 | -0.0071158 | 0.065298 | 0.068588 | 0.17853 | 60.8871 | -61.0931 | 60.91 | -60.8276 | -61.0382 | -0.11902 | 0.23804 | 60.9512 | -61.0794 | -0.19684 | 0.027466 | 61.0748 | 121.8063 | -121.6873 | -0.18311 | 0.091553 | 61.2717 | 60.7773 | 61.1343 | 0.068664 | 121.7834 | 61.0748 | 121.8475 | -0.14191 | -0.18311 | 121.7834 | 61.0748 | -0.14191 | 0.068664 | 121.8475 | -121.9528 | -121.9391
61.0469 | 122.0993 | -60.8643 | 60.9146 | 0.0016785 | 0.019173 | 0.010117 | -7.059e-05 | -0.0077566 | 0.062521 | 0.068161 | 0.17395 | 60.9375 | -61.1526 | 60.8643 | -60.8688 | -61.1343 | 0.13275 | 0.18768 | 61.0336 | -61.0748 | -0.28839 | 0.022888 | 61.0382 | 121.7285 | -121.7834 | -0.21057 | 0.11902 | 61.3266 | 60.997 | 61.0519 | -0.004577 | 121.8018 | 61.0382 | 121.8979 | -0.27008 | -0.21057 | 121.8018 | 61.0382 | -0.27008 | -0.004577 | 121.8979 | -122.0673 | -121.9894
62.7188 | 122.0123 | -60.8963 | 60.8597 | -0.013581 | 0.019173 | 0.015671 | -0.0017794 | -0.009252 | 0.065512 | 0.068588 | 0.21515 | 60.8917 | -61.1069 | 60.9283 | -60.8139 | -61.0474 | -0.12817 | 0.24261 | 60.9375 | -61.0977 | -0.21057 | 0.032044 | 61.1114 | 121.8246 | -121.6736 | -0.20142 | 0.07782 | 61.322 | 60.7681 | 61.1389 | 0.082397 | 121.788 | 61.1114 | 121.8338 | -0.15106 | -0.20142 | 121.788 | 61.1114 | -0.15106 | 0.082397 | 121.8338 | -121.9666 | -121.9574
64.4531 | 121.9345 | -60.9146 | 60.9467 | 0.0016785 | 0.021309 | 0.014176 | 0.0044156 | -0.0056204 | 0.062307 | 0.071365 | 0.27008 | 60.965 | -61.1069 | 60.9421 | -60.8231 | -61.084 | 0.041199 | 0.24719 | 60.9879 | -61.0565 | -0.19226 | 0.018311 | 61.1847 | 121.8567 | -121.7697 | -0.14191 | 0.041199 | 61.377 | 60.9558 | 61.1618 | 0.091553 | 121.8796 | 61.1847 | 121.9025 | -0.16937 | -0.14191 | 121.8796 | 61.1847 | -0.16937 | 0.091553 | 121.9025 | -122.0535 | -122.0032
66.2031 | 121.9482 | -60.8917 | 60.91 | -0.005951 | 0.019386 | 0.015244 | 0.003561 | -0.0060478 | 0.061453 | 0.069015 | 0.24261 | 60.9604 | -61.1252 | 60.8963 | -60.8551 | -61.1114 | 0.045776 | 0.1831 | 61.0291 | -61.0291 | -0.23346 | 0.050354 | 61.1343 | 121.788 | -121.7651 | -0.13733 | 0.11902 | 61.3678 | 60.9375 | 61.0748 | 0.036621 | 121.8521 | 61.1343 | 121.9208 | -0.21973 | -0.13733 | 121.8521 | 61.1343 | -0.21973 | 0.036621 | 121.9208 | -122.0352 | -121.9391
67.9375 | 121.9208 | -60.9421 | 60.8826 | -0.005951 | 0.020454 | 0.02208 | -0.0013522 | -0.0056204 | 0.064444 | 0.067734 | 0.23346 | 60.91 | -61.1114 | 60.9329 | -60.791 | -61.0291 | -0.20599 | 0.20599 | 60.9192 | -61.0794 | -0.16937 | 0.027466 | 61.1755 | 121.875 | -121.6736 | -0.13733 | 0.036621 | 61.3449 | 60.7361 | 61.1481 | 0.15106 | 121.8521 | 61.1755 | 121.8613 | -0.086975 | -0.13733 | 121.8521 | 61.1755 | -0.086975 | 0.15106 | 121.8613 | -121.994 | -121.962
69.6719 | 121.9711 | -60.8826 | 60.9283 | 0.0016785 | 0.019813 | 0.017808 | 0.0031338 | -0.0069022 | 0.064016 | 0.069015 | 0.25177 | 60.9924 | -61.1069 | 60.9238 | -60.8368 | -61.0886 | 0.068665 | 0.21515 | 60.9924 | -61.0748 | -0.22431 | 0.064087 | 61.1343 | 121.8063 | -121.7651 | -0.19226 | 0.064087 | 61.3586 | 60.9512 | 61.0977 | 0.045776 | 121.875 | 61.1343 | 121.875 | -0.20599 | -0.19226 | 121.875 | 61.1343 | -0.20599 | 0.045776 | 121.875 | -122.0352 | -122.0032
71.3438 | 121.9208 | -60.9604 | 60.8688 | -0.005951 | 0.017891 | 0.016953 | -0.0022068 | -0.005834 | 0.063589 | 0.067947 | 0.22888 | 60.878 | -61.0886 | 60.9146 | -60.8047 | -61.0565 | -0.18768 | 0.20142 | 60.91 | -61.0657 | -0.12817 | 0.009156 | 61.1893 | 121.875 | -121.6736 | -0.10529 | 0.041199 | 61.3174 | 60.7727 | 61.1618 | 0.15564 | 121.8384 | 61.1893 | 121.8704 | -0.096131 | -0.10529 | 121.8384 | 61.1893 | -0.096131 | 0.15564 | 121.8704 | -121.9574 | -121.9345
73.0781 | 121.9666 | -60.9283 | 60.8963 | 0.016937 | 0.020027 | 0.018235 | 0.004202 | -0.005834 | 0.062948 | 0.070083 | 0.20599 | 60.9558 | -61.1298 | 60.8551 | -60.8963 | -61.1481 | 0.059509 | 0.12817 | 60.9924 | -61.0794 | -0.20142 | 0.05951 | 61.1343 | 121.7834 | -121.7926 | -0.15106 | 0.096131 | 61.3358 | 60.9879 | 61.0565 | 0.032044 | 121.8842 | 61.1343 | 121.9208 | -0.21973 | -0.15106 | 121.8842 | 61.1343 | -0.21973 | 0.032044 | 121.9208 | -122.0261 | -121.9757
74.75 | 121.9528 | -60.9009 | 60.9192 | 0.0016785 | 0.020668 | 0.018021 | 0.001852 | -0.0073294 | 0.062735 | 0.066879 | 0.2243 | 60.965 | -61.1114 | 60.91 | -60.8185 | -61.0794 | 0.050354 | 0.21973 | 61.0016 | -61.084 | -0.21057 | 0.045777 | 61.1252 | 121.8109 | -121.7377 | -0.1831 | 0.082398 | 61.3358 | 60.9512 | 61.1206 | 0.082398 | 121.8658 | 61.1252 | 121.9025 | -0.17853 | -0.1831 | 121.8658 | 61.1252 | -0.17853 | 0.082398 | 121.9025 | -122.0306 | -122.0032
76.5 | 121.9254 | -60.91 | 60.9329 | 0.0016785 | 0.019813 | 0.018662 | 0.00078401 | -0.0056204 | 0.062735 | 0.069015 | 0.24261 | 60.9375 | -61.0931 | 60.9375 | -60.8093 | -61.0748 | 0.041199 | 0.22888 | 61.0107 | -61.0245 | -0.18311 | 0.004578 | 61.1526 | 121.8475 | -121.7422 | -0.11444 | 0.07782 | 61.3358 | 60.9512 | 61.1389 | 0.10071 | 121.8475 | 61.1526 | 121.9208 | -0.16479 | -0.11444 | 121.8475 | 61.1526 | -0.16479 | 0.10071 | 121.9208 | -122.0261 | -121.9574
78.2344 | 121.994 | -60.878 | 60.9238 | -0.005951 | 0.021309 | 0.014603 | -0.0049838 | -0.0079704 | 0.061453 | 0.068802 | 0.22888 | 60.8963 | -61.0931 | 60.9421 | -60.791 | -61.0245 | -0.10529 | 0.27008 | 60.9283 | -61.1069 | -0.21515 | -0.027466 | 61.1069 | 121.8201 | -121.7148 | -0.22888 | 0.004578 | 61.322 | 60.7727 | 61.1481 | 0.086975 | 121.7743 | 61.1069 | 121.8063 | -0.14648 | -0.22888 | 121.7743 | 61.1069 | -0.14648 | 0.086975 | 121.8063 | -122.0169 | -122.0306
79.9531 | 121.9299 | -60.9146 | 60.9283 | 0.0016785 | 0.021522 | 0.016739 | 0.0029202 | -0.0071158 | 0.06188 | 0.068374 | 0.27924 | 60.9833 | -61.1114 | 60.9238 | -60.8368 | -61.0794 | 0.036621 | 0.2243 | 60.965 | -61.0565 | -0.19684 | 0.054931 | 61.1938 | 121.8384 | -121.7651 | -0.14191 | 0.036621 | 61.3907 | 60.9512 | 61.1389 | 0.07782 | 121.8979 | 61.1938 | 121.8796 | -0.1648 | -0.14191 | 121.8979 | 61.1938 | -0.1648 | 0.07782 | 121.8796 | -122.0398 | -121.9849
81.625 | 121.9299 | -60.9375 | 60.8643 | -0.013581 | 0.0196 | 0.019303 | -7.059e-05 | -0.0066886 | 0.065512 | 0.071579 | 0.20142 | 60.9146 | -61.1343 | 60.878 | -60.8688 | -61.0794 | -0.10986 | 0.16937 | 60.9329 | -61.0748 | -0.19684 | 0.050354 | 61.1389 | 121.8155 | -121.7331 | -0.13733 | 0.068664 | 61.3358 | 60.8276 | 61.1069 | 0.068665 | 121.8521 | 61.1389 | 121.8704 | -0.14191 | -0.13733 | 121.8521 | 61.1389 | -0.14191 | 0.068665 | 121.8704 | -121.9986 | -121.9391
83.3594 | 121.907 | -60.9421 | 60.8734 | -0.013581 | 0.021309 | 0.018021 | 0.00014321 | -0.0056204 | 0.06423 | 0.06987 | 0.21973 | 60.9009 | -61.1298 | 60.9009 | -60.8231 | -61.0611 | -0.15106 | 0.17853 | 60.9375 | -61.0657 | -0.18768 | 0.027466 | 61.1618 | 121.843 | -121.6965 | -0.1236 | 0.064087 | 61.3495 | 60.791 | 61.1206 | 0.11902 | 121.843 | 61.1618 | 121.8796 | -0.11902 | -0.1236 | 121.843 | 61.1618 | -0.11902 | 0.11902 | 121.8796 | -122.0032 | -121.9391
85.0938 | 122.0581 | -60.8734 | 60.8963 | -0.013581 | 0.019813 | 0.015671 | -0.0022068 | -0.0096794 | 0.062735 | 0.068588 | 0.20142 | 60.9467 | -61.0977 | 60.8688 | -60.8505 | -61.1069 | 0.082397 | 0.19684 | 60.9741 | -61.1023 | -0.2243 | 0.050354 | 61.0748 | 121.7422 | -121.7468 | -0.22888 | 0.07782 | 61.2991 | 60.9558 | 61.0703 | 0.022888 | 121.8201 | 61.0748 | 121.8475 | -0.23346 | -0.22888 | 121.8201 | 61.0748 | -0.23346 | 0.022888 | 121.8475 | -121.994 | -121.9986
86.7812 | 121.9299 | -60.91 | 60.9146 | -0.005951 | 0.020241 | 0.019089 | 0.003561 | -0.0086112 | 0.065298 | 0.070297 | 0.25177 | 60.9558 | -61.116 | 60.9238 | -60.8093 | -61.0748 | 0.050354 | 0.21515 | 60.9787 | -61.0611 | -0.20599 | 0.041199 | 61.1618 | 121.8338 | -121.7239 | -0.15106 | 0.064087 | 61.3678 | 60.9604 | 61.1252 | 0.10071 | 121.8658 | 61.1618 | 121.8887 | -0.16479 | -0.15106 | 121.8658 | 61.1618 | -0.16479 | 0.10071 | 121.8887 | -122.0306 | -121.9757
88.5312 | 122.0169 | -60.9055 | 60.8322 | 0.009308 | 0.016823 | 0.016312 | -0.005411 | -0.008184 | 0.063803 | 0.066025 | 0.16022 | 60.8871 | -61.0931 | 60.8551 | -60.8597 | -61.0931 | -0.10986 | 0.16022 | 60.9375 | -61.0931 | -0.18768 | 0.054932 | 61.0657 | 121.7606 | -121.6919 | -0.18768 | 0.10529 | 61.2534 | 60.7956 | 61.0657 | 0.045777 | 121.7926 | 61.0657 | 121.843 | -0.18768 | -0.18768 | 121.7926 | 61.0657 | -0.18768 | 0.045777 | 121.843 | -121.9254 | -121.9254
90.2031 | 121.962 | -60.9283 | 60.8917 | -0.005951 | 0.022163 | 0.017594 | 0.002493 | -0.007543 | 0.064444 | 0.067734 | 0.16937 | 60.9695 | -61.1298 | 60.8459 | -60.8917 | -61.1114 | -0.032043 | 0.10529 | 60.9695 | -61.1114 | -0.20142 | 0.077819 | 61.0977 | 121.7743 | -121.7834 | -0.1831 | 0.077819 | 61.2991 | 60.8963 | 61.0336 | 0.036621 | 121.8979 | 61.0977 | 121.8979 | -0.1831 | -0.1831 | 121.8979 | 61.0977 | -0.1831 | 0.036621 | 121.8979 | -122.0215 | -122.0032
91.9062 | 121.8933 | -60.9558 | 60.878 | -0.013581 | 0.020882 | 0.020585 | 0.002493 | -0.0066886 | 0.065084 | 0.070083 | 0.25635 | 60.9055 | -61.1069 | 60.9146 | -60.8047 | -61.0382 | -0.18768 | 0.21057 | 60.9009 | -61.0748 | -0.15106 | 0.027466 | 61.2122 | 121.8704 | -121.6827 | -0.11902 | 0.022888 | 61.3632 | 60.7681 | 61.1664 | 0.15106 | 121.8613 | 61.2122 | 121.8567 | -0.082397 | -0.11902 | 121.8613 | 61.2122 | -0.082397 | 0.15106 | 121.8567 | -121.9849 | -121.9528
93.6406 | 122.049 | -60.8414 | 60.8917 | 0.0016785 | 0.019813 | 0.016526 | -0.00049779 | -0.006475 | 0.064444 | 0.068588 | 0.18768 | 60.9558 | -61.1206 | 60.8597 | -60.8688 | -61.1252 | 0.09613 | 0.19226 | 60.9879 | -61.0886 | -0.27923 | 0.064087 | 61.0291 | 121.701 | -121.7606 | -0.24719 | 0.09613 | 61.3083 | 60.9375 | 61.0336 | -0.027465 | 121.7972 | 61.0291 | 121.8292 | -0.28381 | -0.24719 | 121.7972 | 61.0291 | -0.28381 | -0.027465 | 121.8292 | -122.0123 | -121.9803
95.3906 | 121.907 | -60.9512 | 60.878 | -0.005951 | 0.020668 | 0.014603 | 0.00057041 | -0.0056204 | 0.064444 | 0.067093 | 0.24261 | 60.8917 | -61.0931 | 60.9375 | -60.8047 | -61.0245 | -0.18768 | 0.21515 | 60.9055 | -61.0748 | -0.14191 | 0.013733 | 61.1938 | 121.8887 | -121.6827 | -0.1236 | 0.027466 | 61.3358 | 60.7636 | 61.1664 | 0.14648 | 121.843 | 61.1938 | 121.8567 | -0.073242 | -0.1236 | 121.843 | 61.1938 | -0.073242 | 0.14648 | 121.8567 | -121.9711 | -121.9528
97.0781 | 122.0078 | -60.8734 | 60.8734 | 0.0016785 | 0.018959 | 0.011399 | -0.0022068 | -0.0083976 | 0.061239 | 0.067734 | 0.21973 | 60.8871 | -61.0931 | 60.9283 | -60.7727 | -61.0291 | -0.13733 | 0.27008 | 60.9055 | -61.0703 | -0.21973 | 0.013733 | 61.0931 | 121.8018 | -121.6461 | -0.19684 | 0.032044 | 61.3129 | 60.7361 | 61.1435 | 0.10071 | 121.7606 | 61.0931 | 121.7789 | -0.15564 | -0.19684 | 121.7606 | 61.0931 | -0.15564 | 0.10071 | 121.7789 | -121.9666 | -121.9437
98.8281 | 121.9666 | -60.878 | 60.8734 | 0.0016785 | 0.021736 | 0.018448 | 0.004202 | -0.007543 | 0.06188 | 0.068802 | 0.23346 | 60.9741 | -61.116 | 60.91 | -60.8231 | -61.0657 | 0.064087 | 0.20599 | 60.997 | -61.0977 | -0.23804 | 0.10071 | 61.1115 | 121.788 | -121.6965 | -0.21973 | 0.1236 | 61.3495 | 60.9421 | 61.084 | 0.054932 | 121.8521 | 61.1115 | 121.875 | -0.18768 | -0.21973 | 121.8521 | 61.1115 | -0.18768 | 0.054932 | 121.875 | -121.9894 | -121.9711
100.5469 | 121.9528 | -60.9146 | 60.8643 | 0.0016785 | 0.019813 | 0.01439 | -0.00092499 | -0.0062614 | 0.064016 | 0.06987 | 0.16937 | 60.8826 | -61.1343 | 60.8688 | -60.8459 | -61.0611 | -0.15564 | 0.17853 | 60.9467 | -61.084 | -0.21973 | 0.01831 | 61.084 | 121.7834 | -121.7102 | -0.16937 | 0.082397 | 61.3037 | 60.759 | 61.0931 | 0.068665 | 121.7972 | 61.084 | 121.8613 | -0.14648 | -0.16937 | 121.7972 | 61.084 | -0.14648 | 0.068665 | 121.8613 | -121.9986 | -121.9482
102.2188 | 122.0398 | -60.8414 | 60.8597 | -0.013581 | 0.020454 | 0.01439 | 0.00035681 | -0.006475 | 0.062094 | 0.068802 | 0.16937 | 60.9558 | -61.1114 | 60.8505 | -60.8643 | -61.1298 | 0.11444 | 0.18768 | 61.0153 | -61.0519 | -0.27008 | 0.096131 | 61.0107 | 121.6919 | -121.7239 | -0.21057 | 0.15564 | 61.2808 | 60.9558 | 61.0291 | -0.022888 | 121.7972 | 61.0107 | 121.8567 | -0.28839 | -0.21057 | 121.7972 | 61.0107 | -0.28839 | -0.022888 | 121.8567 | -121.9711 | -121.9116
103.9531 | 122.0352 | -60.8368 | 60.878 | 0.0016785 | 0.022591 | 0.016312 | 0.0029202 | -0.0073294 | 0.062521 | 0.068161 | 0.1831 | 60.9879 | -61.1206 | 60.8688 | -60.8551 | -61.1252 | 0.11444 | 0.1831 | 61.0107 | -61.0611 | -0.28381 | 0.10986 | 61.0199 | 121.7056 | -121.7331 | -0.2243 | 0.13275 | 61.3037 | 60.9512 | 61.0199 | -0.018311 | 121.8246 | 61.0199 | 121.8475 | -0.28839 | -0.2243 | 121.8246 | 61.0199 | -0.28839 | -0.018311 | 121.8475 | -121.9986 | -121.9391
105.6875 | 121.9711 | -60.8643 | 60.8917 | 0.0016785 | 0.019813 | 0.01439 | -0.0019932 | -0.008184 | 0.064016 | 0.06987 | 0.23346 | 60.8871 | -61.1069 | 60.9375 | -60.7681 | -61.0153 | -0.10529 | 0.27466 | 60.9329 | -61.0794 | -0.24262 | -0.004578 | 61.0977 | 121.8018 | -121.6599 | -0.21515 | 0.041198 | 61.3403 | 60.759 | 61.1389 | 0.096131 | 121.7514 | 61.0977 | 121.7972 | -0.15106 | -0.21515 | 121.7514 | 61.0977 | -0.15106 | 0.096131 | 121.7972 | -121.9986 | -121.9711
107.3594 | 121.9574 | -60.9055 | 60.8734 | 0.0016785 | 0.019813 | 0.015671 | 0.0039884 | -0.0056204 | 0.062735 | 0.070083 | 0.18768 | 60.9741 | -61.1389 | 60.8322 | -60.8917 | -61.1389 | 0.032043 | 0.086975 | 61.0291 | -61.0611 | -0.23346 | 0.10071 | 61.0931 | 121.7377 | -121.7651 | -0.15564 | 0.15564 | 61.3266 | 60.9375 | 60.9924 | 0.013733 | 121.8796 | 61.0931 | 121.9345 | -0.23346 | -0.15564 | 121.8796 | 61.0931 | -0.23346 | 0.013733 | 121.9345 | -122.0123 | -121.9345
109.0312 | 121.8933 | -60.8917 | 60.9146 | -0.005951 | 0.021095 | 0.020798 | 0.0029202 | -0.0066886 | 0.064871 | 0.071151 | 0.23804 | 60.9558 | -61.0977 | 60.9055 | -60.8047 | -61.0703 | 0.054932 | 0.23346 | 60.9924 | -61.0336 | -0.20599 | 0.041199 | 61.1298 | 121.7972 | -121.7194 | -0.14191 | 0.07782 | 61.3358 | 60.9467 | 61.1252 | 0.086975 | 121.8475 | 61.1298 | 121.8842 | -0.17853 | -0.14191 | 121.8475 | 61.1298 | -0.17853 | 0.086975 | 121.8842 | -122.0123 | -121.9482
110.7812 | 122.0444 | -60.8322 | 60.8734 | -0.005951 | 0.020241 | 0.017594 | -7.059e-05 | -0.0056204 | 0.064871 | 0.066665 | 0.16022 | 60.9375 | -61.1206 | 60.8459 | -60.8597 | -61.1343 | 0.11444 | 0.16479 | 61.0153 | -61.0519 | -0.28839 | 0.064087 | 60.9924 | 121.6782 | -121.7331 | -0.21973 | 0.14191 | 61.2808 | 60.9467 | 60.997 | -0.027466 | 121.7697 | 60.9924 | 121.8475 | -0.30212 | -0.21973 | 121.7697 | 60.9924 | -0.30212 | -0.027466 | 121.8475 | -121.994 | -121.9254
112.5312 | 122.0078 | -60.8597 | 60.8871 | -0.005951 | 0.021736 | 0.012894 | -0.0017794 | -0.0071158 | 0.06188 | 0.068161 | 0.1831 | 60.9558 | -61.1114 | 60.8871 | -60.8139 | -61.0886 | 0.1236 | 0.19684 | 61.0199 | -61.0748 | -0.25177 | 0.068665 | 61.0428 | 121.7468 | -121.7011 | -0.21515 | 0.13275 | 61.2946 | 60.9833 | 61.0565 | 0.045776 | 121.8155 | 61.0428 | 121.8796 | -0.22888 | -0.21515 | 121.8155 | 61.0428 | -0.22888 | 0.045776 | 121.8796 | -121.9986 | -121.962
114.2031 | 122.0352 | -60.8459 | 60.8734 | -0.013581 | 0.02195 | 0.015885 | -0.0022068 | -0.0051932 | 0.063376 | 0.068374 | 0.16022 | 60.9467 | -61.0977 | 60.8551 | -60.8597 | -61.1252 | 0.10986 | 0.18768 | 60.997 | -61.0886 | -0.25177 | 0.073242 | 61.0062 | 121.7011 | -121.7331 | -0.24262 | 0.1236 | 61.2579 | 60.9558 | 61.0336 | -0.013733 | 121.7926 | 61.0062 | 121.843 | -0.27924 | -0.24262 | 121.7926 | 61.0062 | -0.27924 | -0.013733 | 121.843 | -121.9711 | -121.962
115.9531 | 121.9711 | -60.8505 | 60.8643 | -0.013581 | 0.021095 | 0.01204 | -0.0022068 | -0.0079704 | 0.063589 | 0.067947 | 0.22888 | 60.8917 | -61.0794 | 60.9421 | -60.7773 | -61.0062 | -0.10986 | 0.31128 | 60.9238 | -61.0703 | -0.22888 | 0.027466 | 61.0794 | 121.7926 | -121.6415 | -0.21973 | 0.059509 | 61.3083 | 60.7407 | 61.1618 | 0.073242 | 121.7422 | 61.0794 | 121.7743 | -0.15564 | -0.21973 | 121.7422 | 61.0794 | -0.15564 | 0.073242 | 121.7743 | -121.9437 | -121.9345
117.7031 | 121.9025 | -60.9192 | 60.9009 | 0.0016785 | 0.020668 | 0.017808 | 0.003561 | -0.0045524 | 0.061026 | 0.068374 | 0.25635 | 60.9467 | -61.0794 | 60.9146 | -60.8185 | -61.0748 | 0.032043 | 0.2243 | 61.0062 | -61.0336 | -0.16022 | 0.045776 | 61.1755 | 121.8338 | -121.7194 | -0.11444 | 0.10529 | 61.3358 | 60.9512 | 61.1435 | 0.10071 | 121.8658 | 61.1755 | 121.9254 | -0.15564 | -0.11444 | 121.8658 | 61.1755 | -0.15564 | 0.10071 | 121.9254 | -121.9803 | -121.9345
119.375 | 121.907 | -60.8963 | 60.9146 | -0.005951 | 0.022591 | 0.017167 | 0.0046292 | -0.0060478 | 0.062948 | 0.070083 | 0.24261 | 60.9421 | -61.0977 | 60.9329 | -60.8093 | -61.0565 | 0.045776 | 0.22888 | 60.9787 | -61.0336 | -0.20142 | 0.027466 | 61.1389 | 121.8292 | -121.7239 | -0.13733 | 0.064087 | 61.3403 | 60.9421 | 61.1252 | 0.086975 | 121.8384 | 61.1389 | 121.875 | -0.16022 | -0.13733 | 121.8384 | 61.1389 | -0.16022 | 0.086975 | 121.875 | -122.0123 | -121.9482
121.1094 | 122.0215 | -60.8414 | 60.8963 | -0.013581 | 0.020027 | 0.015671 | -0.00092499 | -0.0062614 | 0.063376 | 0.068374 | 0.1831 | 60.9329 | -61.0931 | 60.8551 | -60.8231 | -61.0886 | 0.07782 | 0.20599 | 60.9741 | -61.0657 | -0.25177 | 0.036621 | 61.0245 | 121.6965 | -121.7194 | -0.2243 | 0.07782 | 61.2762 | 60.9192 | 61.0474 | 0.018311 | 121.7743 | 61.0245 | 121.8155 | -0.24719 | -0.2243 | 121.7743 | 61.0245 | -0.24719 | 0.018311 | 121.8155 | -121.9894 | -121.962
122.8594 | 121.9391 | -60.91 | 60.8551 | 0.0016785 | 0.021095 | 0.017167 | 0.0033474 | -0.0045524 | 0.061453 | 0.068588 | 0.16937 | 60.9421 | -61.1298 | 60.8185 | -60.8826 | -61.1298 | 0.054932 | 0.10986 | 61.0153 | -61.0748 | -0.21973 | 0.086975 | 61.0794 | 121.7285 | -121.7377 | -0.16479 | 0.16022 | 61.2991 | 60.965 | 61.0199 | 0.027466 | 121.8521 | 61.0794 | 121.9254 | -0.21973 | -0.16479 | 121.8521 | 61.0794 | -0.21973 | 0.027466 | 121.9254 | -121.9849 | -121.9299
124.5312 | 121.8796 | -60.8871 | 60.91 | 0.0016785 | 0.020882 | 0.016312 | 0.0020658 | -0.0069022 | 0.062521 | 0.070297 | 0.25635 | 60.9329 | -61.0886 | 60.9192 | -60.8047 | -61.0565 | 0.032043 | 0.21515 | 60.9695 | -61.0565 | -0.20142 | 0.022888 | 61.1435 | 121.8063 | -121.7148 | -0.16937 | 0.059509 | 61.3449 | 60.9192 | 61.1023 | 0.082397 | 121.8201 | 61.1435 | 121.8567 | -0.16937 | -0.16937 | 121.8201 | 61.1435 | -0.16937 | 0.082397 | 121.8567 | -121.9986 | -121.9666
126.2656 | 122.0123 | -60.8597 | 60.878 | -0.013581 | 0.017677 | 0.015885 | -0.0030612 | -0.0083976 | 0.064444 | 0.067947 | 0.21515 | 60.9009 | -61.1069 | 60.9009 | -60.8002 | -61.0428 | 0.009155 | 0.27008 | 60.9604 | -61.0748 | -0.24719 | 0.022888 | 61.0748 | 121.7606 | -121.6782 | -0.21515 | 0.082397 | 61.322 | 60.8688 | 61.1298 | 0.059509 | 121.7606 | 61.0748 | 121.8201 | -0.18311 | -0.21515 | 121.7606 | 61.0748 | -0.18311 | 0.059509 | 121.8201 | -121.9849 | -121.9528
127.9375 | 122.0352 | -60.8414 | 60.878 | -0.013581 | 0.022163 | 0.015671 | -0.0013522 | -0.007543 | 0.063803 | 0.067734 | 0.15106 | 60.9695 | -61.0886 | 60.8459 | -60.8551 | -61.116 | 0.15564 | 0.1831 | 61.0245 | -61.0657 | -0.24719 | 0.091552 | 60.9924 | 121.6873 | -121.7331 | -0.2243 | 0.14648 | 61.2396 | 60.997 | 61.0245 | -0.013733 | 121.8109 | 60.9924 | 121.8658 | -0.27466 | -0.2243 | 121.8109 | 60.9924 | -0.27466 | -0.013733 | 121.8658 | -121.9666 | -121.9437
129.6719 | 122.0169 | -60.8322 | 60.8551 | -0.005951 | 0.020027 | 0.01204 | -0.00049779 | -0.0056204 | 0.063803 | 0.069656 | 0.16479 | 60.9833 | -61.1206 | 60.8322 | -60.8551 | -61.1206 | 0.15106 | 0.17395 | 61.0107 | -61.0794 | -0.28839 | 0.12817 | 60.997 | 121.6644 | -121.7102 | -0.24719 | 0.15564 | 61.2854 | 60.9833 | 61.0062 | -0.022889 | 121.8155 | 60.997 | 121.843 | -0.28839 | -0.24719 | 121.8155 | 60.997 | -0.28839 | -0.022889 | 121.843 | -121.9757 | -121.9345
131.4062 | 122.0169 | -60.8551 | 60.8231 | -0.013581 | 0.020668 | 0.01503 | -0.0037022 | -0.0090384 | 0.065298 | 0.067947 | 0.13733 | 60.8871 | -61.084 | 60.8414 | -60.8551 | -61.0703 | -0.10071 | 0.17853 | 60.91 | -61.1023 | -0.22888 | 0.064087 | 60.9924 | 121.6965 | -121.6782 | -0.24719 | 0.086975 | 61.2213 | 60.7544 | 61.0336 | 0 | 121.7422 | 60.9924 | 121.7651 | -0.21515 | -0.24719 | 121.7422 | 60.9924 | -0.21515 | 0 | 121.7651 | -121.907 | -121.9254
133.1562 | 121.8887 | -60.9238 | 60.878 | -0.005951 | 0.020027 | 0.018235 | -7.059e-05 | -0.008184 | 0.063376 | 0.068588 | 0.20142 | 60.8871 | -61.084 | 60.9009 | -60.8139 | -61.0382 | -0.18768 | 0.19684 | 60.8917 | -61.0794 | -0.16022 | 0.009155 | 61.1252 | 121.8246 | -121.6919 | -0.15564 | 0.013733 | 61.2854 | 60.7361 | 61.1206 | 0.10986 | 121.8109 | 61.1252 | 121.8155 | -0.11444 | -0.15564 | 121.8109 | 61.1252 | -0.11444 | 0.10986 | 121.8155 | -121.962 | -121.9574
134.9062 | 121.9025 | -60.9329 | 60.8414 | -0.013581 | 0.02195 | 0.018662 | 0.002493 | -0.0083976 | 0.064871 | 0.069656 | 0.16937 | 60.9375 | -61.1069 | 60.8597 | -60.8643 | -61.0794 | -0.07782 | 0.14191 | 60.9467 | -61.0977 | -0.17395 | 0.09613 | 61.1023 | 121.7926 | -121.7056 | -0.1648 | 0.10529 | 61.2762 | 60.8551 | 61.0748 | 0.068664 | 121.8704 | 61.1023 | 121.8796 | -0.14649 | -0.1648 | 121.8704 | 61.1023 | -0.14649 | 0.068664 | 121.8796 | -121.9482 | -121.9391
136.6562 | 121.9025 | -60.9055 | 60.9238 | -0.005951 | 0.024513 | 0.022935 | 0.0048428 | -0.005834 | 0.064657 | 0.068161 | 0.25635 | 60.9879 | -61.1023 | 60.8871 | -60.8368 | -61.084 | 0.041199 | 0.19226 | 60.9787 | -61.0886 | -0.19684 | 0.064087 | 61.1618 | 121.7926 | -121.7606 | -0.18311 | 0.054932 | 61.3586 | 60.9467 | 61.0977 | 0.068665 | 121.8933 | 61.1618 | 121.8842 | -0.17853 | -0.18311 | 121.8933 | 61.1618 | -0.17853 | 0.068665 | 121.8842 | -122.0261 | -122.0123
138.3906 | 121.9162 | -60.8643 | 60.8871 | -0.005951 | 0.021309 | 0.014603 | 0.00099761 | -0.0062614 | 0.063376 | 0.06987 | 0.23804 | 60.9512 | -61.1343 | 60.8871 | -60.8139 | -61.0794 | 0.059509 | 0.23346 | 60.9787 | -61.0565 | -0.27008 | 0.064087 | 61.1023 | 121.7514 | -121.7011 | -0.19226 | 0.091553 | 61.3724 | 60.9238 | 61.0977 | 0.050354 | 121.8155 | 61.1023 | 121.843 | -0.21515 | -0.19226 | 121.8155 | 61.1023 | -0.21515 | 0.050354 | 121.843 | -122.0215 | -121.9437
140.0625 | 121.9986 | -60.8459 | 60.8368 | -0.005951 | 0.019813 | 0.013321 | -0.006052 | -0.0096794 | 0.064871 | 0.068588 | 0.16937 | 60.8963 | -61.0794 | 60.8688 | -60.8047 | -61.0428 | -0.11444 | 0.22888 | 60.9467 | -61.0794 | -0.23346 | 0.059509 | 61.0153 | 121.7148 | -121.6415 | -0.23346 | 0.10986 | 61.2488 | 60.7315 | 61.0748 | 0.041198 | 121.7422 | 61.0153 | 121.7926 | -0.19684 | -0.23346 | 121.7422 | 61.0153 | -0.19684 | 0.041198 | 121.7926 | -121.9162 | -121.9162
141.8125 | 121.9849 | -60.8871 | 60.8597 | 0.0016785 | 0.0196 | 0.012681 | -0.0037022 | -0.0077566 | 0.064016 | 0.069443 | 0.16937 | 60.8963 | -61.084 | 60.8597 | -60.8231 | -61.0519 | -0.11902 | 0.20599 | 60.9009 | -61.0886 | -0.19684 | 0.036621 | 61.0565 | 121.7468 | -121.6827 | -0.20142 | 0.041199 | 61.2534 | 60.7681 | 61.0931 | 0.064087 | 121.7834 | 61.0565 | 121.788 | -0.16479 | -0.20142 | 121.7834 | 61.0565 | -0.16479 | 0.064087 | 121.788 | -121.9437 | -121.9482
143.5469 | 121.8979 | -60.9192 | 60.8688 | -0.02121 | 0.017677 | 0.014176 | 0.0022794 | -0.0056204 | 0.064016 | 0.070724 | 0.16479 | 60.9375 | -61.1389 | 60.8414 | -60.8688 | -61.1114 | -0.032043 | 0.11902 | 60.965 | -61.0794 | -0.21973 | 0.068665 | 61.084 | 121.7606 | -121.7377 | -0.16022 | 0.096131 | 61.3037 | 60.8871 | 61.0382 | 0.050354 | 121.8567 | 61.084 | 121.8842 | -0.19226 | -0.16022 | 121.8567 | 61.084 | -0.19226 | 0.050354 | 121.8842 | -122.0078 | -121.9482
145.2812 | 121.9986 | -60.8414 | 60.8917 | -0.005951 | 0.020027 | 0.016099 | 0.00014321 | -0.009252 | 0.064657 | 0.070297 | 0.15106 | 60.965 | -61.1252 | 60.8276 | -60.8643 | -61.1389 | 0.11902 | 0.17395 | 61.0016 | -61.0703 | -0.28381 | 0.073242 | 60.9924 | 121.669 | -121.756 | -0.22888 | 0.10986 | 61.2762 | 60.9604 | 61.0153 | -0.022888 | 121.8063 | 60.9924 | 121.843 | -0.29755 | -0.22888 | 121.8063 | 60.9924 | -0.29755 | -0.022888 | 121.843 | -122.0169 | -121.962
146.9531 | 121.8842 | -60.9009 | 60.8826 | -0.005951 | 0.020882 | 0.018235 | 0.0048428 | -0.0039114 | 0.060598 | 0.069015 | 0.23804 | 60.9375 | -61.0931 | 60.9055 | -60.8139 | -61.0611 | 0.032043 | 0.24719 | 60.9879 | -61.0245 | -0.19226 | 0.054932 | 61.1389 | 121.8063 | -121.6965 | -0.1236 | 0.10529 | 61.3312 | 60.9329 | 61.1481 | 0.086975 | 121.8384 | 61.1389 | 121.8887 | -0.16022 | -0.1236 | 121.8384 | 61.1389 | -0.16022 | 0.086975 | 121.8887 | -121.9757 | -121.907
148.6875 | 121.9208 | -60.8963 | 60.9055 | -0.005951 | 0.019173 | 0.013749 | 0.00057041 | -0.0079704 | 0.064444 | 0.068802 | 0.21515 | 60.9604 | -61.1298 | 60.8505 | -60.8597 | -61.116 | 0.050354 | 0.15106 | 60.9741 | -61.0565 | -0.23346 | 0.054931 | 61.1114 | 121.7468 | -121.7651 | -0.16022 | 0.068664 | 61.3449 | 60.9467 | 61.0474 | 0.036621 | 121.8567 | 61.1114 | 121.8704 | -0.21973 | -0.16022 | 121.8567 | 61.1114 | -0.21973 | 0.036621 | 121.8704 | -122.0352 | -121.962
150.4219 | 121.9391 | -60.9283 | 60.8414 | 0.0016785 | 0.020027 | 0.014603 | 0.0016384 | -0.0043388 | 0.062735 | 0.068588 | 0.16479 | 60.9512 | -61.0977 | 60.8185 | -60.8734 | -61.1252 | 0.036621 | 0.10986 | 61.0107 | -61.0428 | -0.16937 | 0.10986 | 61.0931 | 121.7468 | -121.7148 | -0.11444 | 0.16937 | 61.2625 | 60.965 | 61.0382 | 0.054932 | 121.8796 | 61.0931 | 121.9391 | -0.19684 | -0.11444 | 121.8796 | 61.0931 | -0.19684 | 0.054932 | 121.9391 | -121.9391 | -121.8842
152.1094 | 122.0398 | -60.8368 | 60.8597 | -0.005951 | 0.0196 | 0.017594 | -0.002634 | -0.0071158 | 0.061453 | 0.070511 | 0.14648 | 60.9467 | -61.0977 | 60.8276 | -60.8643 | -61.1298 | 0.12817 | 0.20142 | 60.9558 | -61.084 | -0.26093 | 0.086975 | 60.9833 | 121.6644 | -121.7239 | -0.24719 | 0.096131 | 61.2442 | 60.965 | 61.0382 | -0.027466 | 121.7834 | 60.9833 | 121.7926 | -0.29297 | -0.24719 | 121.7834 | 60.9833 | -0.29297 | -0.027466 | 121.7926 | -121.9574 | -121.9437
153.8594 | 121.9116 | -69.2276 | 52.4963 | -0.005951 | 0.019173 | 0.020157 | -0.0022068 | -0.0073294 | 0.065298 | 0.070297 | -0.1831 | 52.5055 | -69.4519 | 52.5375 | -69.1406 | -69.3878 | -0.21973 | 0.17395 | 52.5009 | -69.4702 | -0.2243 | 0.009155 | 69.0445 | 121.7651 | -121.637 | -0.24262 | 0.004578 | 69.2688 | 69.0079 | 69.4016 | 0.086975 | 121.7331 | 69.0445 | 121.7285 | -0.16022 | -0.24262 | 121.7331 | 69.0445 | -0.16022 | 0.086975 | 121.7285 | -121.9482 | -121.9666
155.5938 | 121.875 | -70.4224 | 51.3428 | -0.005951 | 0.01725 | 0.015671 | 0.0016384 | -0.007543 | 0.065512 | 0.069015 | -0.11902 | 51.3794 | -70.5963 | 51.4252 | -70.2301 | -70.5002 | -0.20599 | 0.18768 | 51.3977 | -70.5505 | -0.17395 | 0.036622 | 70.3033 | 121.8475 | -121.5729 | -0.12817 | 0.054932 | 70.4773 | 70.2164 | 70.61 | 0.19226 | 121.8018 | 70.3033 | 121.8201 | -0.07782 | -0.12817 | 121.8018 | 70.3033 | -0.07782 | 0.19226 | 121.8201 | -121.9391 | -121.8933
157.3594 | 122.0215 | -70.5139 | 51.1688 | -0.013581 | 0.016823 | 0.013108 | -0.0039158 | -0.0086112 | 0.06423 | 0.068802 | -0.21057 | 51.21 | -70.7794 | 51.2283 | -70.4178 | -70.6924 | -0.15106 | 0.17395 | 51.21 | -70.7611 | -0.2655 | 0.041199 | 70.3033 | 121.7422 | -121.5866 | -0.24719 | 0.041199 | 70.5688 | 70.3629 | 70.6879 | 0.09613 | 121.7239 | 70.3033 | 121.7239 | -0.17853 | -0.24719 | 121.7239 | 70.3033 | -0.17853 | 0.09613 | 121.7239 | -121.9482 | -121.9299
159.0312 | 121.8887 | -70.784 | 50.9811 | -0.005951 | 0.0196 | 0.014817 | -0.0017794 | -0.0090384 | 0.064871 | 0.069229 | -0.12817 | 50.9811 | -70.9396 | 51.0361 | -70.6375 | -70.8939 | -0.20599 | 0.16022 | 51.004 | -70.9717 | -0.15564 | 0 | 70.6558 | 121.8201 | -121.6187 | -0.18768 | 0.022888 | 70.8115 | 70.578 | 70.9442 | 0.14648 | 121.7651 | 70.6558 | 121.788 | -0.10986 | -0.18768 | 121.7651 | 70.6558 | -0.10986 | 0.14648 | 121.788 | -121.9208 | -121.9528
160.75 | 121.9757 | -60.8963 | 60.8368 | 0.0016785 | 0.021309 | 0.015458 | -0.00049779 | -0.008184 | 0.06423 | 0.06987 | 0.22888 | 60.8597 | -61.1069 | 60.8368 | -60.8505 | -61.1069 | 0.064087 | 0.2243 | 60.9283 | -61.0931 | -0.21057 | 0.022888 | 61.1252 | 121.7331 | -121.6873 | -0.19684 | 0.091553 | 61.3358 | 60.9604 | 61.1206 | 0.045776 | 121.756 | 61.1252 | 121.8246 | -0.21057 | -0.19684 | 121.756 | 61.1252 | -0.21057 | 0.045776 | 121.8246 | -121.9437 | -121.9299
162.4219 | 121.8567 | -60.9558 | 60.8368 | 0.009308 | 0.0196 | 0.01204 | 0.003561 | -0.0079704 | 0.061666 | 0.068374 | 0.26093 | 60.9055 | -61.1389 | 60.878 | -60.8505 | -61.084 | 0.036621 | 0.22888 | 60.9604 | -61.084 | -0.18311 | 0.068665 | 61.2167 | 121.8338 | -121.6873 | -0.12817 | 0.1236 | 61.3998 | 60.9924 | 61.1847 | 0.10529 | 121.8613 | 61.2167 | 121.9162 | -0.12817 | -0.12817 | 121.8613 | 61.2167 | -0.12817 | 0.10529 | 121.9162 | -121.9757 | -121.9208
164.0938 | 121.994 | -60.8871 | 60.8231 | 0.0016785 | 0.018532 | 0.01439 | -0.0024204 | -0.0079704 | 0.06188 | 0.068588 | 0.15564 | 60.8871 | -61.1389 | 60.7864 | -60.8871 | -61.1435 | 0.11902 | 0.19684 | 60.9238 | -61.1069 | -0.25177 | 0.064087 | 61.0428 | 121.6736 | -121.7102 | -0.21973 | 0.10071 | 61.2946 | 61.0062 | 61.084 | 0 | 121.7743 | 61.0428 | 121.8109 | -0.25635 | -0.21973 | 121.7743 | 61.0428 | -0.25635 | 0 | 121.8109 | -121.962 | -121.9299
165.8281 | 121.8887 | -60.9558 | 60.8093 | -0.013581 | 0.019173 | 0.016953 | 0.0022794 | -0.0062614 | 0.065725 | 0.06987 | 0.15564 | 60.8963 | -61.1618 | 60.7773 | -60.9192 | -61.1481 | -0.018311 | 0.11902 | 60.91 | -61.1481 | -0.20599 | 0.086975 | 61.1115 | 121.7331 | -121.7285 | -0.19226 | 0.10071 | 61.3174 | 60.9375 | 61.0748 | 0.036622 | 121.8521 | 61.1115 | 121.8658 | -0.19226 | -0.19226 | 121.8521 | 61.1115 | -0.19226 | 0.036622 | 121.8658 | -121.9711 | -121.9574
167.5 | 121.8658 | -60.9604 | 60.8002 | -0.005951 | 0.020027 | 0.018235 | 0.0016384 | -0.0079704 | 0.063589 | 0.071151 | 0.24261 | 60.8322 | -61.1343 | 60.8368 | -60.8368 | -61.0748 | -0.16479 | 0.19684 | 60.8368 | -61.1298 | -0.17395 | 0.032043 | 61.203 | 121.7972 | -121.637 | -0.16937 | 0.036621 | 61.377 | 60.7956 | 61.1572 | 0.1236 | 121.7926 | 61.203 | 121.7972 | -0.11444 | -0.16937 | 121.7926 | 61.203 | -0.11444 | 0.1236 | 121.7972 | -121.9345 | -121.9299
169.2344 | 121.8842 | -61.0062 | 60.7773 | -0.013581 | 0.022377 | 0.019303 | 0.0022794 | -0.0071158 | 0.064444 | 0.069015 | 0.20142 | 60.8414 | -61.2259 | 60.7361 | -60.9604 | -61.2213 | 0.054932 | 0.16479 | 60.8414 | -61.1893 | -0.21973 | 0.064087 | 61.2076 | 121.7422 | -121.7377 | -0.1831 | 0.064087 | 61.4273 | 61.0611 | 61.171 | 0.045777 | 121.8475 | 61.2076 | 121.8475 | -0.21515 | -0.1831 | 121.8475 | 61.2076 | -0.21515 | 0.045777 | 121.8475 | -122.0032 | -121.9666
170.9062 | 121.8658 | -60.9833 | 60.791 | 0.0016785 | 0.021522 | 0.016526 | 0.0014248 | -0.0051932 | 0.064016 | 0.067947 | 0.25177 | 60.8231 | -61.1801 | 60.8002 | -60.8963 | -61.1526 | 0.036621 | 0.21973 | 60.8688 | -61.1435 | -0.19684 | 0.032043 | 61.235 | 121.7834 | -121.6873 | -0.16022 | 0.077819 | 61.4319 | 61.0199 | 61.203 | 0.086975 | 121.8063 | 61.235 | 121.8521 | -0.16937 | -0.16022 | 121.8063 | 61.235 | -0.16937 | 0.086975 | 121.8521 | -121.9711 | -121.9345
172.6406 | 121.8979 | -61.084 | 60.6766 | -0.005951 | 0.022163 | 0.018021 | 0.0027066 | -0.0034842 | 0.063162 | 0.070511 | 0.52185 | 60.5942 | -61.4365 | 60.4843 | -61.203 | -61.4502 | 0.004578 | 0.068665 | 60.6354 | -61.3724 | -0.35248 | -0.082398 | 61.6058 | 121.5683 | -121.8796 | -0.28839 | -0.041199 | 61.9583 | 61.0886 | 61.1526 | -0.11902 | 121.6782 | 61.6058 | 121.7194 | -0.36621 | -0.28839 | 121.6782 | 61.6058 | -0.36621 | -0.11902 | 121.7194 | -122.113 | -122.0489
174.375 | 121.8063 | -70.9488 | 50.8301 | -0.02121 | 0.020027 | 0.015671 | -0.0019932 | -0.005834 | 0.063376 | 0.070724 | 10.9177 | 51.1093 | -70.8527 | 50.853 | -70.8435 | -71.0724 | 2.0096 | 1.7853 | 50.7019 | -71.3699 | 0.096131 | 0.27924 | 81.8665 | 121.8018 | -121.6736 | -0.42114 | -0.12817 | 81.7703 | 72.9584 | 72.7341 | 0.10529 | 122.0581 | 81.8665 | 121.6507 | -0.1236 | -0.42114 | 122.0581 | 81.8665 | -0.1236 | 0.10529 | 121.6507 | -121.6827 | -122.2
176.0625 | 121.9528 | -70.3995 | 51.329 | -0.005951 | 0.020241 | 0.016312 | -0.00071139 | -0.0077566 | 0.064016 | 0.069015 | -0.21515 | 51.4389 | -70.6055 | 51.3702 | -70.3033 | -70.5917 | 0.036621 | 0.073242 | 51.4114 | -70.6375 | -0.20599 | 0.10986 | 70.1843 | 121.7697 | -121.6324 | -0.23804 | 0.082397 | 70.3903 | 70.4361 | 70.4727 | 0.09613 | 121.8384 | 70.1843 | 121.8109 | -0.19226 | -0.23804 | 121.8384 | 70.1843 | -0.19226 | 0.09613 | 121.8109 | -121.9345 | -121.9666
177.8125 | 121.907 | -69.7861 | 52.034 | 0.0016785 | 0.020454 | 0.018448 | -0.0013522 | -0.007543 | 0.063803 | 0.069443 | 0.41657 | 52.1027 | -69.9554 | 52.0065 | -69.6487 | -69.9326 | 0.14648 | 0.21057 | 52.1118 | -69.9188 | -0.16937 | 0.068664 | 70.2026 | 121.7926 | -121.6827 | -0.13275 | 0.077819 | 70.372 | 69.9326 | 69.9966 | 0.13733 | 121.8887 | 70.2026 | 121.8979 | -0.14648 | -0.13275 | 121.8887 | 70.2026 | -0.14648 | 0.13733 | 121.8979 | -121.9894 | -121.9528
179.5625 | 121.9482 | -71.4386 | 50.2533 | -0.013581 | 0.019386 | 0.013108 | -0.0039158 | -0.0077566 | 0.063162 | 0.068588 | -0.32959 | 50.3632 | -71.6446 | 50.2808 | -71.3654 | -71.6537 | 0.068665 | 0.13275 | 50.3723 | -71.64 | -0.20599 | 0.10986 | 71.109 | 121.7194 | -121.6187 | -0.20142 | 0.11902 | 71.315 | 71.5073 | 71.5713 | 0.073243 | 121.8018 | 71.109 | 121.8109 | -0.21515 | -0.20142 | 121.8018 | 71.109 | -0.21515 | 0.073243 | 121.8109 | -121.8979 | -121.8933
181.2344 | 121.8979 | -73.2422 | 48.4177 | 0.0016785 | 0.019813 | 0.01439 | -0.0041294 | -0.0086112 | 0.064871 | 0.069015 | -0.29755 | 48.4589 | -73.4985 | 48.5458 | -73.114 | -73.4207 | -0.15106 | 0.25635 | 48.4543 | -73.4756 | -0.25635 | 0.041198 | 72.9446 | 121.788 | -121.5317 | -0.23346 | 0.036621 | 73.201 | 73.0911 | 73.4985 | 0.12817 | 121.701 | 72.9446 | 121.6965 | -0.17853 | -0.23346 | 121.701 | 72.9446 | -0.17853 | 0.12817 | 121.6965 | -121.9162 | -121.8933
182.9844 | 121.8887 | -72.3358 | 49.4064 | 0.009308 | 0.023018 | 0.020585 | 0.0016384 | -0.0069022 | 0.063162 | 0.068374 | -0.20142 | 49.4797 | -72.5555 | 49.411 | -72.258 | -72.551 | 0.10529 | 0.14191 | 49.5392 | -72.5235 | -0.21973 | 0.073242 | 72.1344 | 121.7468 | -121.6644 | -0.18768 | 0.13275 | 72.3541 | 72.4411 | 72.4777 | 0.077819 | 121.8155 | 72.1344 | 121.875 | -0.21515 | -0.18768 | 121.8155 | 72.1344 | -0.21515 | 0.077819 | 121.875 | -121.962 | -121.9299
184.7188 | 122.0078 | -109.5612 | 12.0758 | -0.013581 | 0.018959 | 0.015671 | -0.0030612 | -0.009893 | 0.063162 | 0.068161 | -4.6463 | 12.1216 | -109.877 | 12.2177 | -109.3781 | -109.758 | -0.27466 | 0.16937 | 12.085 | -109.877 | -0.31586 | 0.045776 | 104.9149 | 121.7789 | -121.4539 | -0.31586 | 0.009155 | 105.2307 | 109.2865 | 109.7305 | 0.1831 | 121.6827 | 104.9149 | 121.6461 | -0.19684 | -0.31586 | 121.6827 | 104.9149 | -0.19684 | 0.1831 | 121.6461 | -121.9528 | -121.9528
186.4062 | 122.0032 | -110.2295 | 11.4395 | -0.005951 | 0.019386 | 0.01503 | -0.0030612 | -0.009252 | 0.065084 | 0.068802 | -4.8248 | 11.4899 | -110.5362 | 11.5311 | -110.051 | -110.4172 | -0.27924 | 0.11444 | 11.4578 | -110.5133 | -0.3067 | 0.050354 | 105.4047 | 121.7606 | -121.4905 | -0.28381 | 0.018311 | 105.7114 | 109.9503 | 110.3439 | 0.17853 | 121.7194 | 105.4047 | 121.6873 | -0.18768 | -0.28381 | 121.7194 | 105.4047 | -0.18768 | 0.17853 | 121.6873 | -121.9757 | -121.9528
188.1562 | 121.9162 | -110.4584 | 11.261 | -0.013581 | 0.020027 | 0.019089 | 0.0031338 | -0.0062614 | 0.061666 | 0.068802 | -4.8843 | 11.3754 | -110.7376 | 11.293 | -110.3119 | -110.7147 | -0.11902 | 0.022888 | 11.3251 | -110.7147 | -0.27924 | 0.11444 | 105.574 | 121.7514 | -121.5729 | -0.25635 | 0.064087 | 105.8533 | 110.3394 | 110.4813 | 0.14648 | 121.8338 | 105.574 | 121.7834 | -0.25635 | -0.25635 | 121.8338 | 105.574 | -0.25635 | 0.14648 | 121.7834 | -121.9986 | -121.9757
189.8906 | 121.9345 | -110.8337 | 10.9177 | -0.013581 | 0.020027 | 0.022507 | 0.0012112 | -0.006475 | 0.062521 | 0.070083 | -4.985 | 11.0001 | -111.0947 | 10.9177 | -110.7651 | -111.2091 | -0.14191 | -0.032043 | 10.9497 | -111.1176 | -0.26093 | 0.082397 | 105.8487 | 121.7514 | -121.6827 | -0.28381 | 0.032043 | 106.1096 | 110.6918 | 110.8017 | 0.068664 | 121.8338 | 105.8487 | 121.7834 | -0.37537 | -0.28381 | 121.8338 | 105.8487 | -0.37537 | 0.068664 | 121.7834 | -122.0123 | -122.0352
191.5625 | 121.8658 | -111.0718 | 10.7071 | 0.0016785 | 0.018745 | 0.016526 | 0.001852 | -0.0083976 | 0.064871 | 0.070083 | -5.0079 | 10.7483 | -111.3419 | 10.762 | -110.8246 | -111.2366 | -0.11902 | 0.1236 | 10.762 | -111.2869 | -0.27008 | 0.041199 | 106.0638 | 121.8338 | -121.5317 | -0.21515 | 0.054932 | 106.3339 | 110.9528 | 111.1954 | 0.24719 | 121.8201 | 106.0638 | 121.8338 | -0.16479 | -0.21515 | 121.8201 | 106.0638 | -0.16479 | 0.24719 | 121.8338 | -122.049 | -121.994
193.3125 | 121.8521 | -111.4426 | 10.3455 | 0.009308 | 0.02195 | 0.015671 | 0.00014321 | -0.005834 | 0.064444 | 0.069015 | -5.0674 | 10.4324 | -111.6302 | 10.4874 | -111.2 | -111.6257 | -0.17853 | 0.10986 | 10.4095 | -111.6394 | -0.18768 | 0.086975 | 106.3751 | 121.9299 | -121.5454 | -0.19684 | 0.064087 | 106.5628 | 111.264 | 111.5524 | 0.24262 | 121.875 | 106.3751 | 121.8521 | -0.1831 | -0.19684 | 121.875 | 106.3751 | -0.1831 | 0.24262 | 121.8521 | -121.9757 | -121.9849
195.0469 | 121.9574 | -111.0764 | 10.6064 | -0.005951 | 0.018532 | 0.016739 | -0.0084018 | -0.0066886 | 0.065939 | 0.069443 | -5.0583 | 10.6705 | -111.319 | 10.7574 | -110.8475 | -111.2228 | -0.24719 | 0.15564 | 10.643 | -111.3464 | -0.24261 | 0.064087 | 106.0181 | 121.8338 | -121.4539 | -0.27008 | 0.036621 | 106.2607 | 110.8292 | 111.232 | 0.22888 | 121.7468 | 106.0181 | 121.7194 | -0.14648 | -0.27008 | 121.7468 | 106.0181 | -0.14648 | 0.22888 | 121.7194 | -121.9254 | -121.9528
196.7188 | 121.8567 | -111.5112 | 10.2539 | -0.013581 | 0.021309 | 0.012681 | -0.0049838 | -0.0060478 | 0.065298 | 0.070511 | -5.0903 | 10.2814 | -111.7172 | 10.35 | -111.2274 | -111.6028 | -0.33417 | 0.10986 | 10.2768 | -111.731 | -0.20599 | 0.027466 | 106.4209 | 121.8613 | -121.4813 | -0.21973 | 0.022888 | 106.6269 | 111.1771 | 111.6211 | 0.28381 | 121.7926 | 106.4209 | 121.788 | -0.091553 | -0.21973 | 121.7926 | 106.4209 | -0.091553 | 0.28381 | 121.788 | -121.9711 | -121.9849
198.4531 | 121.8704 | -111.4151 | 10.3775 | -0.005951 | 0.021095 | 0.018021 | 0.002493 | -0.009252 | 0.063803 | 0.072006 | -5.0858 | 10.437 | -111.6394 | 10.4233 | -111.232 | -111.6028 | -0.24719 | 0.10071 | 10.3683 | -111.6028 | -0.2243 | 0.05951 | 106.3293 | 121.8384 | -121.6095 | -0.18768 | -0.009155 | 106.5537 | 111.1679 | 111.5158 | 0.1831 | 121.8521 | 106.3293 | 121.7834 | -0.18768 | -0.18768 | 121.8521 | 106.3293 | -0.18768 | 0.1831 | 121.7834 | -122.0169 | -121.9803
200.1875 | 121.9528 | -111.8271 | 9.8969 | 0.0016785 | 0.017464 | 0.010972 | -0.006052 | -0.0088248 | 0.065298 | 0.06752 | -5.2185 | 9.9426 | -112.0285 | 10.0021 | -111.5524 | -111.9324 | -0.28839 | 0.16937 | 9.9106 | -112.0697 | -0.20142 | 0.045776 | 106.6086 | 121.8292 | -121.4493 | -0.24262 | 0.013732 | 106.81 | 111.5387 | 111.9965 | 0.27466 | 121.7697 | 106.6086 | 121.7377 | -0.10529 | -0.24262 | 121.7697 | 106.6086 | -0.10529 | 0.27466 | 121.7377 | -121.9254 | -121.9666
201.9219 | 121.8567 | -111.969 | 9.8328 | -0.005951 | 0.018318 | 0.017808 | 0.0044156 | -0.0073294 | 0.063589 | 0.06987 | -5.278 | 9.8465 | -112.2574 | 9.9289 | -111.8134 | -112.2437 | -0.15564 | 0.064087 | 9.8282 | -112.2025 | -0.28839 | 0.013733 | 106.691 | 121.8979 | -121.6461 | -0.23346 | -0.004578 | 106.9794 | 111.8134 | 112.0331 | 0.15564 | 121.8155 | 106.691 | 121.7972 | -0.27466 | -0.23346 | 121.8155 | 106.691 | -0.27466 | 0.15564 | 121.7972 | -122.0901 | -122.0352
203.5938 | 121.7606 | -67.2272 | 54.6341 | -0.005951 | 0.019173 | 0.01439 | -0.0024204 | -0.0088248 | 0.065084 | 0.069015 | 0.46234 | 54.6433 | -67.2546 | 54.689 | -66.9571 | -67.2409 | -0.16937 | 0.21057 | 54.6249 | -67.3233 | -0.027466 | 0.009156 | 67.6895 | 121.9162 | -121.5912 | -0.09613 | -0.009155 | 67.717 | 67.0578 | 67.4377 | 0.27008 | 121.8704 | 67.6895 | 121.8521 | -0.013733 | -0.09613 | 121.8704 | 67.6895 | -0.013733 | 0.27008 | 121.8521 | -121.8887 | -121.9574
205.3281 | 121.8109 | -67.7353 | 54.0665 | -0.013581 | 0.021309 | 0.015244 | 0.00078401 | -0.0086112 | 0.064657 | 0.068374 | 0.041199 | 54.1351 | -67.8635 | 54.0436 | -67.6254 | -67.8955 | 0.068665 | 0.15106 | 54.1214 | -67.9047 | -0.12817 | 0.068665 | 67.7765 | 121.7789 | -121.6919 | -0.16937 | 0.054932 | 67.9047 | 67.804 | 67.8864 | 0.10986 | 121.8704 | 67.7765 | 121.8567 | -0.16022 | -0.16937 | 121.8704 | 67.7765 | -0.16022 | 0.10986 | 121.8567 | -121.9299 | -121.9711
207 | 121.7834 | -65.4602 | 56.3416 | -0.005951 | 0.022163 | 0.013108 | 0.0016384 | -0.0062614 | 0.063162 | 0.068374 | -0.045776 | 56.3919 | -65.593 | 56.3828 | -65.2863 | -65.5609 | -0.091553 | 0.12817 | 56.4056 | -65.5655 | -0.13275 | 0.050354 | 65.4144 | 121.843 | -121.6278 | -0.10529 | 0.064087 | 65.5472 | 65.3687 | 65.5884 | 0.17395 | 121.8521 | 65.4144 | 121.8658 | -0.10071 | -0.10529 | 121.8521 | 65.4144 | -0.10071 | 0.17395 | 121.8658 | -121.9345 | -121.907
208.7344 | 121.8887 | -61.1252 | 60.5804 | -0.02121 | 0.019173 | 0.013962 | -0.0037022 | -0.005834 | 0.066153 | 0.068802 | 0.28839 | 60.5942 | -61.2946 | 60.6216 | -61.0062 | -61.2625 | -0.050354 | 0.30212 | 60.6262 | -61.3174 | -0.16937 | 0.013733 | 61.4136 | 121.7468 | -121.5866 | -0.19226 | 0.045777 | 61.5829 | 61.0748 | 61.4273 | 0.11902 | 121.7194 | 61.4136 | 121.7514 | -0.13733 | -0.19226 | 121.7194 | 61.4136 | -0.13733 | 0.11902 | 121.7514 | -121.875 | -121.8979
210.4219 | 121.8704 | -61.0977 | 60.5896 | -0.005951 | 0.0196 | 0.011612 | -0.0041294 | -0.0088248 | 0.064657 | 0.069015 | 0.27466 | 60.5759 | -61.3358 | 60.64 | -61.0062 | -61.2579 | -0.091553 | 0.28381 | 60.6033 | -61.3495 | -0.23804 | -0.013733 | 61.3724 | 121.7377 | -121.5958 | -0.25177 | 0.013733 | 61.6104 | 61.0062 | 61.3815 | 0.091552 | 121.6736 | 61.3724 | 121.7011 | -0.16022 | -0.25177 | 121.6736 | 61.3724 | -0.16022 | 0.091552 | 121.7011 | -121.9254 | -121.9391
212.1562 | 121.875 | -61.084 | 60.6171 | -0.005951 | 0.021095 | 0.017808 | -0.0030612 | -0.0088248 | 0.063162 | 0.065811 | 0.24719 | 60.5896 | -61.3266 | 60.64 | -61.0245 | -61.2625 | -0.082397 | 0.3067 | 60.6171 | -61.3632 | -0.24262 | -0.027465 | 61.3312 | 121.7239 | -121.6415 | -0.27924 | 0 | 61.5738 | 61.0016 | 61.3907 | 0.059509 | 121.6736 | 61.3312 | 121.701 | -0.17853 | -0.27924 | 121.6736 | 61.3312 | -0.17853 | 0.059509 | 121.701 | -121.9437 | -121.9803
213.9062 | 121.8613 | -61.1526 | 60.5759 | 0.0016785 | 0.021522 | 0.016526 | 0.0031338 | -0.0077566 | 0.062948 | 0.070511 | 0.20599 | 60.6308 | -61.3495 | 60.553 | -61.1435 | -61.3861 | 0.091553 | 0.13275 | 60.6949 | -61.377 | -0.19684 | 0.054931 | 61.3586 | 121.7056 | -121.7194 | -0.2243 | 0.11902 | 61.5555 | 61.2442 | 61.2854 | 0.009155 | 121.7834 | 61.3586 | 121.8475 | -0.23346 | -0.2243 | 121.7834 | 61.3586 | -0.23346 | 0.009155 | 121.8475 | -121.9254 | -121.9528
215.5938 | 121.8155 | -61.1801 | 60.553 | 0.0016785 | 0.021309 | 0.016953 | 0.00035681 | -0.0077566 | 0.06423 | 0.066879 | 0.21515 | 60.6125 | -61.3815 | 60.5484 | -61.084 | -61.3266 | -0.11902 | 0.1831 | 60.5621 | -61.3678 | -0.20142 | 0.059509 | 61.3953 | 121.7285 | -121.637 | -0.18768 | 0.009155 | 61.5967 | 61.0611 | 61.3632 | 0.096131 | 121.7926 | 61.3953 | 121.7422 | -0.14648 | -0.18768 | 121.7926 | 61.3953 | -0.14648 | 0.096131 | 121.7422 | -121.9345 | -121.9208
217.3281 | 121.9391 | -61.1114 | 60.5392 | 0.0016785 | 0.022804 | 0.015458 | 0.0014248 | -0.007543 | 0.065298 | 0.068802 | 0.16022 | 60.6583 | -61.409 | 60.5026 | -61.1435 | -61.4227 | 0.14648 | 0.1831 | 60.64 | -61.4136 | -0.29755 | 0.11902 | 61.2717 | 121.6141 | -121.6827 | -0.30212 | 0.10071 | 61.5692 | 61.2579 | 61.2946 | -0.032044 | 121.7697 | 61.2717 | 121.7514 | -0.31128 | -0.30212 | 121.7697 | 61.2717 | -0.31128 | -0.032044 | 121.7514 | -121.9482 | -121.9528
219 | 121.8567 | -61.203 | 60.5576 | -0.013581 | 0.020241 | 0.016739 | 0.0029202 | -0.0062614 | 0.063162 | 0.070297 | 0.19684 | 60.6216 | -61.4273 | 60.5072 | -61.1572 | -61.4136 | 0.068665 | 0.15106 | 60.6445 | -61.3678 | -0.2243 | 0.064087 | 61.3998 | 121.7102 | -121.7148 | -0.16479 | 0.086975 | 61.6241 | 61.2717 | 61.3541 | 0.045776 | 121.8246 | 61.3998 | 121.8475 | -0.21057 | -0.16479 | 121.8246 | 61.3998 | -0.21057 | 0.045776 | 121.8475 | -121.9849 | -121.9254
220.7344 | 121.9711 | -61.171 | 60.4477 | -0.005951 | 0.0196 | 0.020798 | -0.0049838 | -0.0069022 | 0.063803 | 0.068802 | 0.1236 | 60.5347 | -61.4227 | 60.4797 | -61.1481 | -61.3998 | -0.091553 | 0.16479 | 60.5392 | -61.441 | -0.25177 | 0.086975 | 61.2946 | 121.6507 | -121.5958 | -0.27008 | 0.091553 | 61.5463 | 61.0794 | 61.3358 | 0.022888 | 121.7056 | 61.2946 | 121.7102 | -0.22888 | -0.27008 | 121.7056 | 61.2946 | -0.22888 | 0.022888 | 121.7102 | -121.8704 | -121.8887
222.4844 | 121.8613 | -61.2076 | 60.4523 | -0.013581 | 0.021309 | 0.015458 | -0.0032748 | -0.0086112 | 0.064871 | 0.067947 | 0.16022 | 60.5118 | -61.4502 | 60.4889 | -61.1618 | -61.3953 | -0.14191 | 0.17395 | 60.5209 | -61.4365 | -0.24261 | 0.059509 | 61.3678 | 121.6965 | -121.6141 | -0.22888 | 0.068664 | 61.6104 | 61.0657 | 61.3815 | 0.045777 | 121.7194 | 61.3678 | 121.7285 | -0.18768 | -0.22888 | 121.7194 | 61.3678 | -0.18768 | 0.045777 | 121.7285 | -121.9025 | -121.8887
224.2188 | 121.8521 | -61.2579 | 60.4752 | 0.0016785 | 0.019813 | 0.013749 | -0.0011386 | -0.0077566 | 0.064016 | 0.067734 | 0.20142 | 60.4797 | -61.4594 | 60.498 | -61.1526 | -61.377 | -0.20142 | 0.18768 | 60.498 | -61.4365 | -0.20142 | 0.004577 | 61.4594 | 121.756 | -121.6278 | -0.17853 | 0.022888 | 61.6608 | 61.0565 | 61.4456 | 0.10529 | 121.7377 | 61.4594 | 121.756 | -0.11902 | -0.17853 | 121.7377 | 61.4594 | -0.11902 | 0.10529 | 121.756 | -121.9345 | -121.9116
225.9062 | 121.8658 | -61.5234 | 60.1685 | -0.013581 | 0.02195 | 0.016739 | 0.001852 | -0.0066886 | 0.062521 | 0.070083 | 0.23346 | 60.2692 | -61.7569 | 60.1501 | -61.528 | -61.7661 | 0.11444 | 0.16022 | 60.2783 | -61.7249 | -0.23346 | 0.10071 | 61.7569 | 121.6736 | -121.6965 | -0.20142 | 0.10986 | 61.9904 | 61.6379 | 61.6837 | -0.004578 | 121.7926 | 61.7569 | 121.8018 | -0.24262 | -0.20142 | 121.7926 | 61.7569 | -0.24262 | -0.004578 | 121.8018 | -121.9254 | -121.8933
227.6562 | 121.8292 | -61.8896 | 59.8434 | -0.005951 | 0.020027 | 0.020585 | 0.0020658 | -0.0077566 | 0.063803 | 0.070297 | 0.15106 | 59.8434 | -62.1368 | 59.8297 | -61.8439 | -62.114 | 0.059509 | 0.20142 | 59.903 | -62.0911 | -0.24719 | 0 | 62.0407 | 121.7194 | -121.6873 | -0.20142 | 0.059509 | 62.2879 | 61.9492 | 62.0911 | 0.045776 | 121.7331 | 62.0407 | 121.7926 | -0.22431 | -0.20142 | 121.7331 | 62.0407 | -0.22431 | 0.045776 | 121.7926 | -121.9803 | -121.9345
229.4062 | 121.907 | -61.6608 | 60.0082 | -0.005951 | 0.020454 | 0.0096899 | 0.00057041 | -0.0073294 | 0.062521 | 0.069443 | 0.16937 | 60.0586 | -61.9629 | 59.9945 | -61.6653 | -61.9217 | 0.064087 | 0.21515 | 60.1135 | -61.8896 | -0.30212 | 0.050354 | 61.8301 | 121.6553 | -121.6736 | -0.22888 | 0.10529 | 62.1323 | 61.7249 | 61.8759 | -0.004577 | 121.7194 | 61.8301 | 121.7743 | -0.26093 | -0.22888 | 121.7194 | 61.8301 | -0.26093 | -0.004577 | 121.7743 | -121.9711 | -121.8979
231.1406 | 121.9482 | -61.4365 | 60.2234 | -0.013581 | 0.021309 | 0.016099 | -0.0028476 | -0.005834 | 0.060598 | 0.067306 | 0.10529 | 60.26 | -61.7523 | 60.1501 | -61.4685 | -61.7432 | 0.12817 | 0.16022 | 60.3287 | -61.6974 | -0.31586 | 0.036621 | 61.5417 | 121.5866 | -121.6919 | -0.26093 | 0.10529 | 61.8576 | 61.5646 | 61.5967 | -0.032044 | 121.6965 | 61.5417 | 121.7651 | -0.3067 | -0.26093 | 121.6965 | 61.5417 | -0.3067 | -0.032044 | 121.7651 | -121.9757 | -121.9208
232.875 | 121.8338 | -61.9858 | 59.761 | -0.005951 | 0.021309 | 0.015458 | 0.002493 | -0.003057 | 0.06188 | 0.068161 | 0.19684 | 59.8068 | -62.1872 | 59.7473 | -61.9125 | -62.1689 | 0.027466 | 0.1831 | 59.848 | -62.1368 | -0.20142 | 0.045777 | 62.1826 | 121.7331 | -121.6736 | -0.15106 | 0.086975 | 62.384 | 62.0132 | 62.1689 | 0.073242 | 121.7926 | 62.1826 | 121.8338 | -0.1831 | -0.15106 | 121.7926 | 62.1826 | -0.1831 | 0.073242 | 121.8338 | -121.9482 | -121.8979
234.6094 | 121.8613 | -62.1872 | 59.5505 | -0.005951 | 0.019813 | 0.017594 | 0.00057041 | -0.0041252 | 0.061026 | 0.070511 | 0.1236 | 59.5963 | -62.4069 | 59.5093 | -62.1323 | -62.4023 | 0.073242 | 0.15106 | 59.6054 | -62.3886 | -0.21973 | 0.045776 | 62.3108 | 121.6965 | -121.6827 | -0.20142 | 0.054932 | 62.5305 | 62.2604 | 62.3383 | 0.054932 | 121.7834 | 62.3108 | 121.7926 | -0.21515 | -0.20142 | 121.7834 | 62.3108 | -0.21515 | 0.054932 | 121.7926 | -121.9574 | -121.9391
236.3438 | 121.8796 | -64.6408 | 57.0786 | 0.0016785 | 0.020454 | 0.014817 | -0.00071139 | -0.005834 | 0.062307 | 0.068802 | -0.022888 | 57.1884 | -64.8285 | 57.0602 | -64.5905 | -64.8514 | 0.073242 | 0.11444 | 57.2205 | -64.8193 | -0.18768 | 0.10986 | 64.6179 | 121.7011 | -121.669 | -0.17853 | 0.14191 | 64.8056 | 64.7141 | 64.7552 | 0.050354 | 121.8292 | 64.6179 | 121.8613 | -0.21057 | -0.17853 | 121.8292 | 64.6179 | -0.21057 | 0.050354 | 121.8613 | -121.907 | -121.8979
238.0156 | 121.9299 | -65.2771 | 56.3324 | -0.005951 | 0.017677 | 0.018235 | -0.00712 | -0.008184 | 0.067221 | 0.070297 | -0.068665 | 56.5018 | -65.4099 | 56.4926 | -65.126 | -65.387 | -0.16479 | 0.11444 | 56.5109 | -65.4785 | -0.13275 | 0.16937 | 65.2084 | 121.7697 | -121.4584 | -0.20142 | 0.17853 | 65.3412 | 65.1123 | 65.3915 | 0.15106 | 121.7789 | 65.2084 | 121.788 | -0.10986 | -0.20142 | 121.7789 | 65.2084 | -0.10986 | 0.15106 | 121.788 | -121.7422 | -121.8109
239.75 | 121.8887 | -65.0299 | 56.6666 | -0.005951 | 0.020027 | 0.015458 | -0.00028419 | -0.0073294 | 0.064871 | 0.072006 | -0.27008 | 56.3232 | -65.6433 | 56.2363 | -65.3915 | -65.6479 | -0.13733 | -0.07782 | 56.3782 | -65.6296 | -0.6134 | -0.34332 | 64.7598 | 121.2662 | -122.0581 | -0.59967 | -0.28839 | 65.3732 | 64.8926 | 64.9521 | -0.36163 | 121.3531 | 64.7598 | 121.4081 | -0.61798 | -0.59967 | 121.3531 | 64.7598 | -0.61798 | -0.36163 | 121.4081 | -122.3099 | -122.2961
241.4688 | 121.8887 | -65.6616 | 56.0211 | -0.005951 | 0.02195 | 0.018876 | -0.0047702 | -0.007543 | 0.062094 | 0.070297 | -0.3067 | 56.163 | -65.7715 | 56.2042 | -65.4282 | -65.712 | -0.2655 | 0.13275 | 56.1539 | -65.7852 | -0.10986 | 0.14191 | 65.3549 | 121.8658 | -121.4493 | -0.1236 | 0.13275 | 65.4648 | 65.3961 | 65.7944 | 0.23346 | 121.8246 | 65.3549 | 121.8155 | -0.050354 | -0.1236 | 121.8246 | 65.3549 | -0.050354 | 0.23346 | 121.8155 | -121.7926 | -121.8063
243.1562 | 121.8979 | -65.0482 | 56.6071 | -0.005951 | 0.019173 | 0.016526 | -0.002634 | -0.0073294 | 0.065939 | 0.066879 | 0.013733 | 56.6071 | -65.3046 | 56.6803 | -64.9704 | -65.2222 | -0.15564 | 0.2655 | 56.6254 | -65.3137 | -0.25635 | 0 | 65.062 | 121.7285 | -121.5775 | -0.2655 | 0.01831 | 65.3183 | 64.8926 | 65.3137 | 0.07782 | 121.6553 | 65.062 | 121.6736 | -0.17395 | -0.2655 | 121.6553 | 65.062 | -0.17395 | 0.07782 | 121.6736 | -121.9116 | -121.9208
244.8906 | 121.9666 | -64.801 | 56.8176 | -0.005951 | 0.020241 | 0.016099 | 0.00099761 | -0.0096794 | 0.063803 | 0.067947 | -0.068665 | 56.8268 | -65.181 | 56.7032 | -64.9338 | -65.2176 | 0.15106 | 0.20142 | 56.8359 | -65.1855 | -0.37994 | 0.009155 | 64.7324 | 121.5042 | -121.7514 | -0.38452 | 0.01831 | 65.1123 | 64.9521 | 65.0024 | -0.13275 | 121.6278 | 64.7324 | 121.637 | -0.41657 | -0.38452 | 121.6278 | 64.7324 | -0.41657 | -0.13275 | 121.637 | -121.9986 | -122.0032
246.5625 | 121.9116 | -65.5014 | 56.1401 | 0.0016785 | 0.016396 | 0.015671 | -0.0032748 | -0.007543 | 0.063376 | 0.070297 | 0 | 56.1676 | -65.7669 | 56.2088 | -65.4282 | -65.6937 | -0.11444 | 0.25635 | 56.163 | -65.744 | -0.2655 | 0.027466 | 65.5014 | 121.7102 | -121.5683 | -0.24262 | 0.022888 | 65.7669 | 65.387 | 65.7578 | 0.073242 | 121.669 | 65.5014 | 121.6644 | -0.19226 | -0.24262 | 121.669 | 65.5014 | -0.19226 | 0.073242 | 121.6644 | -121.907 | -121.8842
248.3125 | 121.9025 | -65.1581 | 56.5063 | 0.009308 | 0.0196 | 0.014176 | -0.0030612 | -0.0079704 | 0.062094 | 0.067947 | 0.1236 | 56.4835 | -65.451 | 56.5247 | -65.094 | -65.3641 | -0.050354 | 0.29755 | 56.4926 | -65.4831 | -0.29297 | -0.022889 | 65.2817 | 121.6827 | -121.6003 | -0.32501 | -0.013733 | 65.5746 | 65.1077 | 65.4556 | 0.064087 | 121.6415 | 65.2817 | 121.6507 | -0.20599 | -0.32501 | 121.6415 | 65.2817 | -0.20599 | 0.064087 | 121.6507 | -121.9574 | -121.9894
249.9844 | 121.9025 | -65.4144 | 56.282 | -0.005951 | 0.019173 | 0.013962 | -0.0045566 | -0.0094656 | 0.06423 | 0.068802 | 0.018311 | 56.1905 | -65.7166 | 56.2958 | -65.3275 | -65.5884 | -0.091553 | 0.32501 | 56.2775 | -65.6845 | -0.30212 | -0.091552 | 65.4327 | 121.7102 | -121.6095 | -0.27008 | -0.004577 | 65.7349 | 65.3229 | 65.7394 | 0.086975 | 121.6049 | 65.4327 | 121.6919 | -0.17395 | -0.27008 | 121.6049 | 65.4327 | -0.17395 | 0.086975 | 121.6919 | -121.9986 | -121.9666
251.7188 | 121.9574 | -65.2496 | 56.3599 | -0.005951 | 0.017464 | 0.01204 | -0.004343 | -0.0096794 | 0.064657 | 0.068374 | -0.14191 | 56.4423 | -65.5151 | 56.4102 | -65.2267 | -65.4831 | -0.16479 | 0.10071 | 56.4514 | -65.4831 | -0.2655 | 0.082398 | 65.1077 | 121.6599 | -121.5866 | -0.23346 | 0.091553 | 65.3732 | 65.0848 | 65.3503 | 0.022888 | 121.6919 | 65.1077 | 121.7011 | -0.23346 | -0.23346 | 121.6919 | 65.1077 | -0.23346 | 0.022888 | 121.7011 | -121.875 | -121.843
253.3906 | 121.8887 | -65.062 | 56.5842 | -0.005951 | 0.02195 | 0.015885 | -0.00071139 | -0.0090384 | 0.06423 | 0.068161 | 0.07782 | 56.6757 | -65.2588 | 56.7444 | -64.8926 | -65.1489 | -0.11902 | 0.28381 | 56.6757 | -65.2679 | -0.19684 | 0.091553 | 65.1398 | 121.8063 | -121.4767 | -0.20599 | 0.091553 | 65.3366 | 64.9429 | 65.3458 | 0.16937 | 121.7377 | 65.1398 | 121.7377 | -0.086975 | -0.20599 | 121.7377 | 65.1398 | -0.086975 | 0.16937 | 121.7377 | -121.843 | -121.8521
255.0625 | 121.9482 | -64.9658 | 56.6757 | -0.005951 | 0.016609 | 0.011612 | -0.0017794 | -0.0077566 | 0.065939 | 0.068374 | 0.12817 | 56.7627 | -65.2039 | 56.7673 | -64.856 | -65.1077 | -0.027466 | 0.29755 | 56.7627 | -65.1627 | -0.23804 | 0.086975 | 65.094 | 121.7331 | -121.5317 | -0.19684 | 0.086975 | 65.332 | 64.9384 | 65.2634 | 0.10986 | 121.7285 | 65.094 | 121.7285 | -0.14191 | -0.19684 | 121.7285 | 65.094 | -0.14191 | 0.10986 | 121.7285 | -121.8796 | -121.8384
256.7969 | 121.8292 | -65.0665 | 56.6299 | -0.005951 | 0.020882 | 0.014817 | -0.00071139 | -0.0090384 | 0.065939 | 0.071365 | 0.036621 | 56.7169 | -65.1947 | 56.7398 | -64.8834 | -65.1489 | -0.19226 | 0.1831 | 56.7169 | -65.1901 | -0.12817 | 0.086975 | 65.1031 | 121.8063 | -121.5134 | -0.1236 | 0.086975 | 65.2313 | 64.8743 | 65.2496 | 0.18311 | 121.7834 | 65.1031 | 121.7834 | -0.082398 | -0.1236 | 121.7834 | 65.1031 | -0.082398 | 0.18311 | 121.7834 | -121.8246 | -121.8201
258.5312 | 121.7972 | -64.1693 | 57.5134 | -0.013581 | 0.018532 | 0.015458 | -0.0011386 | -0.006475 | 0.06423 | 0.068588 | 0.13733 | 57.5638 | -64.3524 | 57.5912 | -64.0549 | -64.3295 | -0.20142 | 0.21515 | 57.5729 | -64.3341 | -0.1831 | 0.050354 | 64.3066 | 121.7606 | -121.5683 | -0.16479 | 0.059509 | 64.4897 | 63.9679 | 64.3845 | 0.11444 | 121.7331 | 64.3066 | 121.7422 | -0.16022 | -0.16479 | 121.7331 | 64.3066 | -0.16022 | 0.11444 | 121.7422 | -121.8658 | -121.8475
260.2656 | 121.907 | -63.8855 | 57.7606 | -0.013581 | 0.021309 | 0.014176 | -0.0032748 | -0.0077566 | 0.063162 | 0.066879 | 0.082397 | 57.8796 | -64.0274 | 57.8979 | -63.7344 | -63.9908 | -0.17395 | 0.22888 | 57.8613 | -64.0778 | -0.14191 | 0.11902 | 63.9679 | 121.7834 | -121.4951 | -0.19226 | 0.10071 | 64.1098 | 63.7115 | 64.1144 | 0.15106 | 121.7651 | 63.9679 | 121.7468 | -0.10529 | -0.19226 | 121.7651 | 63.9679 | -0.10529 | 0.15106 | 121.7468 | -121.788 | -121.8384
262 | 121.4676 | -28.775 | 93.0588 | -0.005951 | 0.018959 | 0.016312 | 0.0016384 | -0.0056204 | 0.063376 | 0.068374 | 3.7079 | 93.0313 | -28.9581 | 92.8802 | -28.7842 | -28.8849 | 0 | 0.25635 | 93.0954 | -28.9124 | -0.18311 | -0.027466 | 32.4829 | 121.6553 | -121.843 | -0.13733 | 0.036621 | 32.666 | 28.775 | 29.0314 | -0.009156 | 121.8063 | 32.4829 | 121.8704 | -0.10986 | -0.13733 | 121.8063 | 32.4829 | -0.10986 | -0.009156 | 121.8704 | -122.0169 | -121.9711
263.7344 | 121.9528 | -63.5651 | 57.962 | -0.013581 | 0.021095 | 0.014817 | -0.0045566 | -0.0083976 | 0.062735 | 0.069443 | 0.16022 | 58.9783 | -62.9379 | 59.0012 | -62.6541 | -62.9013 | -0.17395 | 0.19684 | 58.96 | -62.9974 | 0.62714 | 1.0162 | 63.7253 | 122.5662 | -120.6162 | 0.56763 | 0.99793 | 63.0981 | 63.3911 | 63.7619 | 0.91095 | 122.5433 | 63.7253 | 122.525 | 0.66376 | 0.56763 | 122.5433 | 63.7253 | 0.66376 | 0.91095 | 122.525 | -120.9 | -120.9595
265.4062 | 122.0261 | -47.9462 | 73.732 | -0.005951 | 0.020241 | 0.020157 | 0.0020658 | -0.0083976 | 0.061666 | 0.068161 | 1.4694 | 74.2172 | -47.7539 | 74.4232 | -47.1405 | -47.8683 | -0.43945 | 0.27466 | 74.1348 | -47.8271 | 0.19226 | 0.48523 | 49.4156 | 122.3694 | -120.8725 | 0.11902 | 0.40283 | 49.2233 | 47.5067 | 48.2208 | 0.80566 | 122.1634 | 49.4156 | 122.081 | 0.07782 | 0.11902 | 122.1634 | 49.4156 | 0.07782 | 0.80566 | 122.081 | -121.4859 | -121.5591
267.1406 | 121.7148 | -27.4521 | 94.3542 | 0.0016785 | 0.021522 | 0.01738 | -0.0019932 | -0.0077566 | 0.063162 | 0.06987 | 4.0924 | 94.5511 | -27.4429 | 94.3817 | -27.2827 | -27.3651 | -0.027466 | 0.33417 | 94.5419 | -27.4475 | 0.009155 | 0.19684 | 31.5445 | 121.8338 | -121.637 | 0.004577 | 0.18768 | 31.5353 | 27.4246 | 27.7863 | 0.16937 | 122.0032 | 31.5445 | 121.994 | 0.086975 | 0.004577 | 122.0032 | 31.5445 | 0.086975 | 0.16937 | 121.994 | -121.7972 | -121.8018
268.8906 | 121.7926 | -27.0813 | 94.6838 | 0.0016785 | 0.021095 | 0.016739 | 0.00099761 | -0.0069022 | 0.06423 | 0.068374 | 4.0604 | 94.7479 | -27.3056 | 94.4824 | -27.182 | -27.2736 | 0.12817 | 0.19684 | 94.7891 | -27.2507 | -0.2243 | 0.064087 | 31.1417 | 121.5637 | -121.8658 | -0.16937 | 0.10529 | 31.366 | 27.2095 | 27.2781 | -0.10071 | 121.8292 | 31.1417 | 121.8704 | -0.19226 | -0.16937 | 121.8292 | 31.1417 | -0.19226 | -0.10071 | 121.8704 | -121.9894 | -121.9345
270.5781 | 121.8933 | -26.6647 | 95.0226 | 0.0016785 | 0.02195 | 0.013108 | -0.0066928 | -0.0079704 | 0.066153 | 0.067947 | 4.129 | 95.2194 | -26.7883 | 95.0272 | -26.6052 | -26.6922 | 0.041199 | 0.28381 | 95.2469 | -26.7563 | -0.1236 | 0.19684 | 30.7938 | 121.6919 | -121.6278 | -0.091553 | 0.2243 | 30.9174 | 26.7059 | 26.9485 | 0.059509 | 121.8842 | 30.7938 | 121.9116 | -0.027466 | -0.091553 | 121.8842 | 30.7938 | -0.027466 | 0.059509 | 121.9116 | -121.8109 | -121.7789
272.3125 | 121.7697 | -26.564 | 95.2148 | -0.005951 | 0.022163 | 0.015244 | 0.00057041 | -0.005834 | 0.063803 | 0.067734 | 4.1473 | 95.2332 | -26.7792 | 95.0134 | -26.6327 | -26.7059 | 0.027466 | 0.21057 | 95.2835 | -26.7426 | -0.21515 | 0.01831 | 30.7114 | 121.5775 | -121.8475 | -0.17853 | 0.068664 | 30.9265 | 26.5915 | 26.7746 | -0.068664 | 121.7972 | 30.7114 | 121.8475 | -0.14191 | -0.17853 | 121.7972 | 30.7114 | -0.14191 | -0.068664 | 121.8475 | -121.994 | -121.9574
274.0469 | 121.8658 | -26.619 | 95.1187 | -0.013581 | 0.020668 | 0.011826 | -0.00071139 | -0.0071158 | 0.06188 | 0.066879 | 4.129 | 95.1782 | -26.8753 | 94.931 | -26.738 | -26.8387 | 0.2243 | 0.28381 | 95.2286 | -26.8204 | -0.25635 | 0.05951 | 30.748 | 121.55 | -121.8567 | -0.20142 | 0.10986 | 31.0043 | 26.8433 | 26.9028 | -0.11902 | 121.7972 | 30.748 | 121.8475 | -0.21973 | -0.20142 | 121.7972 | 30.748 | -0.21973 | -0.11902 | 121.8475 | -121.994 | -121.9391
275.7812 | 121.8246 | -26.683 | 95.0455 | 0.009308 | 0.020241 | 0.017594 | 0.00099761 | -0.0049796 | 0.062094 | 0.06987 | 4.097 | 95.1553 | -26.8845 | 94.8853 | -26.7609 | -26.8524 | 0.15564 | 0.16937 | 95.256 | -26.825 | -0.20142 | 0.10986 | 30.78 | 121.5683 | -121.8063 | -0.14191 | 0.21057 | 30.9814 | 26.8387 | 26.8524 | -0.07782 | 121.8384 | 30.78 | 121.9391 | -0.16937 | -0.14191 | 121.8384 | 30.78 | -0.16937 | -0.07782 | 121.9391 | -121.9299 | -121.8704
277.4531 | 121.8109 | -26.5091 | 95.2286 | 0.0016785 | 0.020241 | 0.016739 | -0.0019932 | -0.0049796 | 0.064016 | 0.068588 | 4.1382 | 95.3293 | -26.7059 | 95.0226 | -26.6098 | -26.6968 | 0.1236 | 0.1831 | 95.3888 | -26.6739 | -0.19684 | 0.10071 | 30.6473 | 121.5317 | -121.8384 | -0.16479 | 0.16022 | 30.8441 | 26.6327 | 26.6922 | -0.10071 | 121.8384 | 30.6473 | 121.8979 | -0.18768 | -0.16479 | 121.8384 | 30.6473 | -0.18768 | -0.10071 | 121.8979 | -121.9345 | -121.9025
279.125 | 121.907 | -26.6876 | 94.9768 | -0.005951 | 0.0196 | 0.011826 | -0.0069064 | -0.0094656 | 0.06658 | 0.067093 | 4.0329 | 95.0546 | -26.9119 | 94.8441 | -26.7838 | -26.8662 | 0.036621 | 0.24261 | 95.0867 | -26.889 | -0.2243 | 0.077819 | 30.7205 | 121.5317 | -121.7606 | -0.20142 | 0.10986 | 30.9448 | 26.7242 | 26.9302 | -0.09613 | 121.7422 | 30.7205 | 121.7743 | -0.17853 | -0.20142 | 121.7422 | 30.7205 | -0.17853 | -0.09613 | 121.7743 | -121.8887 | -121.8658
280.8594 | 121.8704 | -27.1912 | 94.4962 | -0.02121 | 0.015755 | 0.012467 | -0.0047702 | -0.010534 | 0.063589 | 0.069443 | 4.1245 | 95.105 | -26.857 | 94.9585 | -26.683 | -26.7883 | -0.009155 | 0.32501 | 95.1187 | -26.8662 | 0.33417 | 0.60882 | 31.3156 | 122.1497 | -121.1792 | 0.32501 | 0.62256 | 30.9814 | 27.182 | 27.5162 | 0.50812 | 122.2961 | 31.3156 | 122.3099 | 0.40283 | 0.32501 | 122.2961 | 31.3156 | 0.40283 | 0.50812 | 122.3099 | -121.3531 | -121.3623
282.5938 | 121.8109 | -26.8341 | 94.9356 | -0.005951 | 0.020882 | 0.013535 | -7.059e-05 | -0.005834 | 0.061026 | 0.06987 | 4.0741 | 95.0272 | -27.0172 | 94.7891 | -26.8662 | -26.9302 | 0.082397 | 0.23346 | 95.0363 | -26.944 | -0.18311 | 0.091553 | 30.9082 | 121.6232 | -121.8018 | -0.10986 | 0.10071 | 31.0913 | 26.9165 | 27.0676 | -0.032044 | 121.8613 | 30.9082 | 121.8704 | -0.096131 | -0.10986 | 121.8613 | 30.9082 | -0.096131 | -0.032044 | 121.8704 | -121.9528 | -121.8796
284.3281 | 121.7651 | -26.9348 | 94.7983 | -0.005951 | 0.022804 | 0.016526 | 0.0022794 | -0.0045524 | 0.060812 | 0.066879 | 4.097 | 94.812 | -27.2232 | 94.5511 | -27.0721 | -27.15 | 0.16022 | 0.30212 | 94.8624 | -27.1774 | -0.28839 | 0.013733 | 31.0318 | 121.4859 | -121.8704 | -0.24262 | 0.064087 | 31.3202 | 27.095 | 27.2369 | -0.13733 | 121.7468 | 31.0318 | 121.7972 | -0.21515 | -0.24262 | 121.7468 | 31.0318 | -0.21515 | -0.13733 | 121.7972 | -122.0215 | -121.9757
286.0625 | 121.7926 | -26.8295 | 94.9722 | 0.0016785 | 0.021736 | 0.014817 | 0.001852 | -0.0056204 | 0.064016 | 0.069015 | 4.0878 | 95.0409 | -26.9806 | 94.7937 | -26.8616 | -26.9485 | 0.18768 | 0.2243 | 95.1096 | -26.9165 | -0.15106 | 0.068665 | 30.9174 | 121.6232 | -121.8338 | -0.086975 | 0.13733 | 31.0684 | 27.0172 | 27.0538 | -0.032043 | 121.8704 | 30.9174 | 121.9391 | -0.11902 | -0.086975 | 121.8704 | 30.9174 | -0.11902 | -0.032043 | 121.9391 | -121.9528 | -121.8887
287.7969 | 121.7514 | -26.6098 | 95.1462 | -0.005951 | 0.020454 | 0.017167 | 0.0020658 | -0.005834 | 0.060812 | 0.068802 | 4.1107 | 95.2011 | -26.8021 | 94.9905 | -26.6556 | -26.7471 | 0.14191 | 0.2655 | 95.2789 | -26.7288 | -0.19226 | 0.054932 | 30.7205 | 121.6003 | -121.8018 | -0.11902 | 0.13275 | 30.9128 | 26.7517 | 26.8753 | -0.045777 | 121.8109 | 30.7205 | 121.8887 | -0.13733 | -0.11902 | 121.8109 | 30.7205 | -0.13733 | -0.045777 | 121.8887 | -121.9482 | -121.875
289.5312 | 121.7606 | -26.7105 | 95.0821 | 0.0016785 | 0.022163 | 0.014817 | -0.0015658 | -0.0069022 | 0.063376 | 0.069443 | 4.129 | 95.1782 | -26.8204 | 94.9677 | -26.683 | -26.7929 | 0.15106 | 0.28381 | 95.2148 | -26.8341 | -0.10986 | 0.096131 | 30.8395 | 121.6782 | -121.7651 | -0.1236 | 0.13275 | 30.9494 | 26.8616 | 26.9943 | 0.027466 | 121.8887 | 30.8395 | 121.9254 | -0.082398 | -0.1236 | 121.8887 | 30.8395 | -0.082398 | 0.027466 | 121.9254 | -121.9025 | -121.9162
291.2031 | 121.8063 | -26.6602 | 95.0638 | 0.0016785 | 0.0196 | 0.011185 | -0.00092499 | -0.0071158 | 0.063376 | 0.068374 | 4.0787 | 95.137 | -26.8936 | 94.8807 | -26.77 | -26.8799 | 0.16937 | 0.27924 | 95.1462 | -26.8845 | -0.23346 | 0.073242 | 30.7388 | 121.5408 | -121.8338 | -0.2243 | 0.082397 | 30.9723 | 26.8295 | 26.9394 | -0.10986 | 121.7972 | 30.7388 | 121.8063 | -0.21973 | -0.2243 | 121.7972 | 30.7388 | -0.21973 | -0.10986 | 121.8063 | -121.9574 | -121.9482
292.9375 | 121.8842 | -26.4038 | 95.3064 | -0.013581 | 0.019386 | 0.013108 | -0.0096836 | -0.0083976 | 0.065298 | 0.068374 | 3.8498 | 95.2148 | -26.7471 | 94.9631 | -26.651 | -26.7746 | -0.51727 | -0.17853 | 95.137 | -26.8478 | -0.34332 | -0.091552 | 30.2536 | 121.3669 | -121.9574 | -0.44403 | -0.16937 | 30.5969 | 25.8865 | 26.2253 | -0.24719 | 121.6187 | 30.2536 | 121.5408 | -0.37079 | -0.44403 | 121.6187 | 30.2536 | -0.37079 | -0.24719 | 121.5408 | -122.0535 | -122.1542
294.6094 | 121.8979 | -21.373 | 100.2914 | 0.009308 | 0.019386 | 0.011612 | -0.004343 | -0.0073294 | 0.062094 | 0.068161 | 4.953 | 100.4059 | -21.6385 | 100.09 | -21.5012 | -21.579 | 0.28839 | 0.30212 | 100.4791 | -21.579 | -0.2655 | 0.11444 | 26.326 | 121.463 | -121.7926 | -0.20599 | 0.18768 | 26.5915 | 21.6614 | 21.6751 | -0.12817 | 121.7789 | 26.326 | 121.8521 | -0.20599 | -0.20599 | 121.7789 | 26.326 | -0.20599 | -0.12817 | 121.8521 | -121.9299 | -121.8704
296.3438 | 121.8842 | -20.9381 | 100.7492 | -0.013581 | 0.019386 | 0.011612 | -0.0041294 | -0.0079704 | 0.064016 | 0.067947 | 4.8752 | 100.5249 | -21.4233 | 100.296 | -21.286 | -21.3135 | -0.004578 | 0.32501 | 100.6531 | -21.3409 | -0.48523 | -0.22431 | 25.8133 | 121.2341 | -122.0352 | -0.40283 | -0.096131 | 26.2985 | 20.9335 | 21.2631 | -0.3479 | 121.463 | 25.8133 | 121.5912 | -0.37537 | -0.40283 | 121.463 | 25.8133 | -0.37537 | -0.3479 | 121.5912 | -122.1725 | -122.0901
298.0156 | 89.4928 | -0.15106 | 69.1818 | 0.0016785 | 0.019813 | 0.01439 | 0.0014248 | -0.0062614 | 0.06423 | 0.068588 | 5.6808 | 100.9323 | -21.1533 | 100.5249 | -21.0251 | -21.0754 | 0.32959 | 0.33875 | 100.9415 | -21.1166 | -21.0022 | 31.7505 | 5.8319 | 100.676 | -90.2069 | -20.9656 | 31.7596 | 26.8341 | 0.48065 | 0.48981 | -20.874 | 101.0834 | 5.8319 | 101.0925 | -20.9244 | -20.9656 | 101.0834 | 5.8319 | -20.9244 | -20.874 | 101.0925 | -90.3351 | -90.2985
299.7656 | 121.9162 | -20.2515 | 97.9935 | 0.0016785 | 0.022163 | 0.016099 | 0.0014248 | -0.0054068 | 0.061239 | 0.069656 | 5.2551 | 101.5503 | -20.4803 | 101.3168 | -20.2652 | -20.2972 | 0.29297 | 0.28839 | 101.7197 | -20.3201 | -0.22888 | 3.5568 | 25.5066 | 121.5683 | -118.2587 | -0.068664 | 3.7262 | 25.7355 | 20.5444 | 20.5399 | -0.013733 | 121.8018 | 25.5066 | 121.9711 | -0.045776 | -0.068664 | 121.8018 | 25.5066 | -0.045776 | -0.013733 | 121.9711 | -118.4738 | -118.3136
301.5 | 121.9711 | -118.2312 | 3.3875 | -0.005951 | 0.019386 | 0.013962 | 0.0016384 | -0.0060478 | 0.062521 | 0.068374 | -6.8069 | 3.4698 | -118.6569 | 3.3829 | -118.0801 | -118.5013 | -0.25177 | 0.018311 | 3.4424 | -118.5699 | -0.42572 | 0.082398 | 111.4243 | 121.6141 | -121.4676 | -0.33875 | 0.054932 | 111.85 | 117.9794 | 118.2495 | 0.15106 | 121.701 | 111.4243 | 121.6736 | -0.27008 | -0.33875 | 121.701 | 111.4243 | -0.27008 | 0.15106 | 121.6736 | -122.0444 | -121.9574
303.2344 | 121.9116 | -119.6594 | 1.9913 | -0.005951 | 0.017677 | 0.01503 | -0.0030612 | -0.0062614 | 0.065298 | 0.071579 | -6.9168 | 2.0599 | -119.9158 | 2.0416 | -119.426 | -119.8242 | -0.40741 | 0.009155 | 2.0462 | -119.9341 | -0.25635 | 0.068665 | 112.7426 | 121.701 | -121.4172 | -0.27466 | 0.054932 | 112.999 | 119.252 | 119.6686 | 0.23346 | 121.7194 | 112.7426 | 121.7056 | -0.16479 | -0.27466 | 121.7194 | 112.7426 | -0.16479 | 0.23346 | 121.7056 | -121.907 | -121.9254
304.9688 | 121.9116 | -119.6777 | 2.0279 | 0.009308 | 0.018745 | 0.016739 | -7.059e-05 | -0.004766 | 0.063162 | 0.072006 | -6.9626 | 2.0737 | -120.0119 | 1.9409 | -119.4992 | -119.9203 | -0.21515 | -0.054932 | 2.0645 | -119.9387 | -0.33417 | 0.045776 | 112.7151 | 121.6187 | -121.5271 | -0.26093 | 0.036621 | 113.0493 | 119.4626 | 119.6228 | 0.17853 | 121.7514 | 112.7151 | 121.7422 | -0.24262 | -0.26093 | 121.7514 | 112.7151 | -0.24262 | 0.17853 | 121.7422 | -122.0398 | -121.9666
306.6406 | 121.8109 | -119.7372 | 1.9958 | -0.005951 | 0.020882 | 0.014817 | -0.0030612 | -0.0062614 | 0.065298 | 0.071151 | -6.8939 | 2.005 | -119.9203 | 2.0325 | -119.3985 | -119.8013 | -0.4303 | 0.086975 | 2.0142 | -119.9341 | -0.1831 | 0.009155 | 112.8433 | 121.7697 | -121.3943 | -0.19684 | 0.01831 | 113.0264 | 119.3069 | 119.8242 | 0.33875 | 121.7422 | 112.8433 | 121.7514 | -0.064087 | -0.19684 | 121.7422 | 112.8433 | -0.064087 | 0.33875 | 121.7514 | -121.9162 | -121.9299
308.375 | 121.8063 | -119.7693 | 1.9409 | 0.0016785 | 0.015968 | 0.011612 | -0.0051974 | -0.0086112 | 0.062735 | 0.069656 | -6.9031 | 1.9638 | -119.9753 | 1.9775 | -119.4672 | -119.838 | -0.39368 | 0.091553 | 1.9547 | -119.9524 | -0.20599 | 0.022888 | 112.8662 | 121.7468 | -121.4081 | -0.18311 | 0.013733 | 113.0722 | 119.3756 | 119.8608 | 0.30212 | 121.7331 | 112.8662 | 121.7239 | -0.068665 | -0.18311 | 121.7331 | 112.8662 | -0.068665 | 0.30212 | 121.7239 | -121.9162 | -121.8933
310.0469 | 121.8796 | -119.8242 | 1.8539 | -0.013581 | 0.017677 | 0.013962 | -0.0058384 | -0.0086112 | 0.064016 | 0.067306 | -6.9489 | 1.9089 | -120.0348 | 1.9318 | -119.4946 | -119.9249 | -0.3479 | 0.13275 | 1.9043 | -120.0897 | -0.21057 | 0.054932 | 112.8754 | 121.756 | -121.3486 | -0.2655 | 0.050354 | 113.0859 | 119.4763 | 119.957 | 0.32959 | 121.7331 | 112.8754 | 121.7285 | -0.10071 | -0.2655 | 121.7331 | 112.8754 | -0.10071 | 0.32959 | 121.7285 | -121.8887 | -121.9437
311.7812 | 121.8704 | -119.8608 | 1.8173 | -0.005951 | 0.017677 | 0.011612 | -0.0045566 | -0.011175 | 0.06188 | 0.067306 | -6.9305 | 1.8585 | -120.0531 | 1.8997 | -119.5267 | -119.9524 | -0.3479 | 0.13733 | 1.8494 | -120.0714 | -0.19226 | 0.041199 | 112.9303 | 121.7606 | -121.344 | -0.21057 | 0.032043 | 113.1226 | 119.5129 | 119.9982 | 0.33417 | 121.7194 | 112.9303 | 121.7102 | -0.091553 | -0.21057 | 121.7194 | 112.9303 | -0.091553 | 0.33417 | 121.7102 | -121.8704 | -121.8887
313.5156 | 121.7651 | -119.7556 | 1.9913 | -0.005951 | 0.018745 | 0.016526 | -0.00028419 | -0.005834 | 0.065298 | 0.069443 | -6.8848 | 2.0187 | -119.9066 | 2.0691 | -119.3893 | -119.783 | -0.41657 | 0.10986 | 2.0233 | -119.9158 | -0.15106 | 0.027466 | 112.8708 | 121.8246 | -121.3806 | -0.16022 | 0.032043 | 113.0219 | 119.339 | 119.8654 | 0.36621 | 121.7743 | 112.8708 | 121.7789 | -0.027466 | -0.16022 | 121.7743 | 112.8708 | -0.027466 | 0.36621 | 121.7789 | -121.8979 | -121.907
315.2031 | 121.843 | -119.3893 | 2.2659 | 0.0016785 | 0.01725 | 0.014603 | -0.0024204 | -0.0088248 | 0.062307 | 0.068588 | -6.8527 | 2.298 | -119.5862 | 2.3575 | -119.0826 | -119.4992 | -0.28839 | 0.16479 | 2.3026 | -119.6228 | -0.19684 | 0.032044 | 112.5366 | 121.7468 | -121.3486 | -0.23346 | 0.036621 | 112.7335 | 119.101 | 119.5541 | 0.3067 | 121.6873 | 112.5366 | 121.6919 | -0.10986 | -0.23346 | 121.6873 | 112.5366 | -0.10986 | 0.3067 | 121.6919 | -121.8521 | -121.8887
316.9531 | 121.756 | -119.1834 | 2.5406 | -0.013581 | 0.0196 | 0.01503 | 0.00078401 | -0.0096794 | 0.065084 | 0.069229 | -6.8527 | 2.5681 | -119.3893 | 2.5269 | -118.9041 | -119.3207 | -0.32044 | 0.064087 | 2.5452 | -119.3756 | -0.20599 | 0.027466 | 112.3306 | 121.7102 | -121.4447 | -0.19226 | 0.004578 | 112.5366 | 118.8629 | 119.2474 | 0.27924 | 121.7514 | 112.3306 | 121.7285 | -0.13733 | -0.19226 | 121.7514 | 112.3306 | -0.13733 | 0.27924 | 121.7285 | -121.9299 | -121.9162
318.625 | 121.7468 | -118.8766 | 2.8381 | -0.005951 | 0.017891 | 0.018021 | -0.0034884 | -0.0090384 | 0.064444 | 0.068161 | -6.633 | 2.8748 | -119.014 | 2.916 | -118.5104 | -118.9133 | -0.31586 | 0.16022 | 2.8839 | -119.0231 | -0.13733 | 0.036621 | 112.2437 | 121.7926 | -121.3486 | -0.14648 | 0.045776 | 112.381 | 118.5608 | 119.0369 | 0.36621 | 121.7514 | 112.2437 | 121.7606 | -0.036621 | -0.14648 | 121.7514 | 112.2437 | -0.036621 | 0.36621 | 121.7606 | -121.8521 | -121.8613
320.3594 | 121.8155 | -119.4351 | 2.2247 | -0.013581 | 0.016823 | 0.014176 | -0.0062656 | -0.010534 | 0.065298 | 0.070297 | -6.9305 | 2.2476 | -119.6411 | 2.2339 | -119.1788 | -119.5999 | -0.32501 | 0.064087 | 2.2385 | -119.696 | -0.20599 | 0.022889 | 112.5046 | 121.669 | -121.4035 | -0.26093 | 0.013733 | 112.7106 | 119.1101 | 119.4992 | 0.25635 | 121.6827 | 112.5046 | 121.6736 | -0.16479 | -0.26093 | 121.6827 | 112.5046 | -0.16479 | 0.25635 | 121.6736 | -121.8658 | -121.9208
322.0312 | 121.8658 | -119.5679 | 2.0462 | -0.013581 | 0.018532 | 0.014817 | -0.0058384 | -0.010107 | 0.064016 | 0.06987 | -6.9626 | 2.1286 | -119.7876 | 2.1149 | -119.2932 | -119.6915 | -0.31586 | 0.10986 | 2.1149 | -119.8151 | -0.21973 | 0.082397 | 112.6053 | 121.6827 | -121.3394 | -0.24719 | 0.068664 | 112.825 | 119.252 | 119.6777 | 0.27466 | 121.6965 | 112.6053 | 121.6827 | -0.1236 | -0.24719 | 121.6965 | 112.6053 | -0.1236 | 0.27466 | 121.6827 | -121.8338 | -121.8613
323.75 | 121.5591 | -118.4921 | 3.0212 | 0.0016785 | 0.019813 | 0.01439 | 0.0033474 | -0.0069022 | 0.060598 | 0.067947 | -8.4457 | 3.0075 | -118.7256 | 2.9755 | -118.2083 | -118.6386 | -0.32959 | 0.018311 | 2.9984 | -118.6707 | -0.23346 | -0.013733 | 110.0464 | 121.4676 | -121.2296 | -0.17853 | -0.022888 | 110.2798 | 118.1625 | 118.5104 | 0.28381 | 121.4996 | 110.0464 | 121.4905 | -0.14648 | -0.17853 | 121.4996 | 110.0464 | -0.14648 | 0.28381 | 121.4905 | -121.7468 | -121.6919
325.4844 | 121.3486 | -118.602 | 3.1128 | -0.013581 | 0.017036 | 0.017808 | 0.0014248 | -0.0069022 | 0.061666 | 0.067734 | -6.7291 | 3.1357 | -118.8492 | 3.0853 | -118.3411 | -118.7714 | -0.16937 | 0.068665 | 3.1403 | -118.8171 | -0.24719 | 0.022888 | 111.8729 | 121.6873 | -121.4539 | -0.21515 | 0.027466 | 112.1201 | 118.4326 | 118.6707 | 0.26093 | 121.7377 | 111.8729 | 121.7422 | -0.16937 | -0.21515 | 121.7377 | 111.8729 | -0.16937 | 0.26093 | 121.7422 | -121.962 | -121.9299
327.2188 | 121.8338 | -118.6569 | 2.9846 | -0.013581 | 0.018318 | 0.016099 | -0.006052 | -0.008184 | 0.064016 | 0.069443 | -6.7749 | 3.0029 | -118.9041 | 2.9846 | -118.4235 | -118.8629 | -0.17395 | 0.09613 | 3.0304 | -118.9041 | -0.24719 | 0.018311 | 111.882 | 121.6415 | -121.4081 | -0.24719 | 0.045777 | 112.1292 | 118.483 | 118.7531 | 0.23346 | 121.6599 | 111.882 | 121.6873 | -0.20599 | -0.24719 | 121.6599 | 111.882 | -0.20599 | 0.23346 | 121.6873 | -121.8887 | -121.8887
328.9531 | 121.8384 | -118.8309 | 2.7878 | -0.005951 | 0.019813 | 0.01204 | -0.0075474 | -0.0071158 | 0.062521 | 0.068802 | -6.8665 | 2.8244 | -119.1101 | 2.7466 | -118.6523 | -119.0598 | -0.31586 | 0.032043 | 2.7924 | -119.1376 | -0.27923 | 0.036621 | 111.9644 | 121.5775 | -121.4401 | -0.3067 | 0.004577 | 112.2437 | 118.515 | 118.8629 | 0.17853 | 121.6553 | 111.9644 | 121.6232 | -0.22888 | -0.3067 | 121.6553 | 111.9644 | -0.22888 | 0.17853 | 121.6232 | -121.8979 | -121.9254
330.7188 | 121.7789 | -118.808 | 2.8748 | 0.009308 | 0.019173 | 0.012681 | 0.0014248 | -0.008184 | 0.063162 | 0.07222 | -6.8298 | 2.9388 | -119.0552 | 2.8198 | -118.602 | -119.0277 | -0.16937 | 0.004578 | 2.9434 | -119.0048 | -0.24719 | 0.064087 | 111.9781 | 121.6278 | -121.4767 | -0.19684 | 0.068664 | 112.2253 | 118.6386 | 118.8126 | 0.20599 | 121.7468 | 111.9781 | 121.7514 | -0.21973 | -0.19684 | 121.7468 | 111.9781 | -0.21973 | 0.20599 | 121.7514 | -121.9299 | -121.8796
332.3906 | 121.7056 | -119.1055 | 2.5681 | 0.009308 | 0.018532 | 0.019089 | -0.0030612 | -0.0062614 | 0.061239 | 0.069229 | -6.7886 | 2.5772 | -119.3115 | 2.6184 | -118.808 | -119.2108 | -0.37994 | 0.10986 | 2.5681 | -119.3207 | -0.20599 | 0.009155 | 112.3169 | 121.7239 | -121.376 | -0.21515 | 0 | 112.5229 | 118.7256 | 119.2154 | 0.29755 | 121.6827 | 112.3169 | 121.6736 | -0.10528 | -0.21515 | 121.6827 | 112.3169 | -0.10528 | 0.29755 | 121.6736 | -121.8796 | -121.8887
334.0625 | 121.6965 | -118.721 | 2.9709 | -0.005951 | 0.020241 | 0.018662 | -0.0015658 | -0.0066886 | 0.064444 | 0.071151 | -6.72 | 3.0029 | -118.927 | 3.0396 | -118.3868 | -118.808 | -0.37079 | 0.11444 | 2.9755 | -118.895 | -0.20599 | 0.032044 | 112.001 | 121.7606 | -121.3577 | -0.17395 | 0.004578 | 112.207 | 118.3502 | 118.8354 | 0.33417 | 121.7239 | 112.001 | 121.6965 | -0.086975 | -0.17395 | 121.7239 | 112.001 | -0.086975 | 0.33417 | 121.6965 | -121.8979 | -121.8658
335.7969 | 121.7285 | -119.1879 | 2.5269 | -0.013581 | 0.018745 | 0.011399 | -0.0028476 | -0.0088248 | 0.062735 | 0.069229 | -6.7886 | 2.5269 | -119.3802 | 2.5681 | -118.8629 | -119.2612 | -0.39825 | 0.1236 | 2.5085 | -119.3939 | -0.19226 | 0 | 112.3993 | 121.756 | -121.3898 | -0.20599 | -0.01831 | 112.5916 | 118.7897 | 119.3115 | 0.32501 | 121.7148 | 112.3993 | 121.6965 | -0.073242 | -0.20599 | 121.7148 | 112.3993 | -0.073242 | 0.32501 | 121.6965 | -121.907 | -121.9208
337.5312 | 121.7377 | -119.3298 | 2.4033 | -0.005951 | 0.020668 | 0.011826 | -0.0017794 | -0.0049796 | 0.060812 | 0.06987 | -6.8802 | 2.4399 | -119.5724 | 2.3529 | -119.0918 | -119.5267 | -0.16479 | 0.068665 | 2.4261 | -119.5404 | -0.24262 | 0.036621 | 112.4496 | 121.6827 | -121.4951 | -0.21057 | 0.022888 | 112.6923 | 119.165 | 119.3985 | 0.23804 | 121.7697 | 112.4496 | 121.756 | -0.19684 | -0.21057 | 121.7697 | 112.4496 | -0.19684 | 0.23804 | 121.756 | -121.9757 | -121.9437
339.2656 | 121.8155 | -118.8171 | 2.8107 | 0.0016785 | 0.020027 | 0.012894 | -0.0064792 | -0.009252 | 0.063376 | 0.068802 | -6.7886 | 2.8702 | -119.0277 | 2.9022 | -118.5333 | -118.9499 | -0.27008 | 0.17853 | 2.8336 | -119.0735 | -0.21057 | 0.059509 | 112.0285 | 121.7194 | -121.344 | -0.25635 | 0.022888 | 112.2391 | 118.5471 | 118.9957 | 0.28381 | 121.6873 | 112.0285 | 121.6507 | -0.13275 | -0.25635 | 121.6873 | 112.0285 | -0.13275 | 0.28381 | 121.6507 | -121.8384 | -121.8842
341 | 121.8338 | -119.2612 | 2.3621 | -0.013581 | 0.020027 | 0.01738 | -0.0011386 | -0.0066886 | 0.062521 | 0.069229 | -6.9214 | 2.4216 | -119.5633 | 2.3575 | -119.0826 | -119.4992 | -0.11902 | 0.073242 | 2.449 | -119.5358 | -0.30212 | 0.059509 | 112.3398 | 121.6187 | -121.4447 | -0.27466 | 0.086975 | 112.6419 | 119.1422 | 119.3344 | 0.17853 | 121.6827 | 112.3398 | 121.7102 | -0.23804 | -0.27466 | 121.6827 | 112.3398 | -0.23804 | 0.17853 | 121.7102 | -121.9254 | -121.8979
342.6719 | 121.7514 | -119.3436 | 2.3438 | 0.0016785 | 0.018745 | 0.01439 | 0.00014321 | -0.0060478 | 0.062948 | 0.070083 | -6.9031 | 2.3712 | -119.5724 | 2.3209 | -119.0872 | -119.5084 | -0.27924 | 0.054932 | 2.3666 | -119.5633 | -0.22888 | 0.027466 | 112.4405 | 121.6644 | -121.431 | -0.21973 | 0.022888 | 112.6694 | 119.0643 | 119.3985 | 0.25635 | 121.7148 | 112.4405 | 121.7102 | -0.1648 | -0.21973 | 121.7148 | 112.4405 | -0.1648 | 0.25635 | 121.7102 | -121.9162 | -121.907
344.4062 | 121.7422 | -119.252 | 2.449 | 0.009308 | 0.018532 | 0.016312 | -0.005411 | -0.0049796 | 0.064444 | 0.068374 | -6.8115 | 2.4399 | -119.4443 | 2.4994 | -118.9545 | -119.3527 | -0.37537 | 0.10529 | 2.4628 | -119.4489 | -0.19226 | -0.009156 | 112.4405 | 121.7514 | -121.4035 | -0.19684 | 0.013733 | 112.6328 | 118.8766 | 119.3573 | 0.29755 | 121.6919 | 112.4405 | 121.7148 | -0.10071 | -0.19684 | 121.6919 | 112.4405 | -0.10071 | 0.29755 | 121.7148 | -121.8933 | -121.8979
346.1562 | 121.7331 | -119.1055 | 2.5955 | -0.005951 | 0.019386 | 0.019517 | -0.0049838 | -0.0066886 | 0.06423 | 0.069656 | -6.7795 | 2.6184 | -119.2932 | 2.655 | -118.7759 | -119.1925 | -0.38452 | 0.1236 | 2.5772 | -119.3344 | -0.18768 | 0.022888 | 112.326 | 121.7606 | -121.3715 | -0.22888 | -0.018311 | 112.5137 | 118.721 | 119.2291 | 0.32959 | 121.7239 | 112.326 | 121.6827 | -0.086975 | -0.22888 | 121.7239 | 112.326 | -0.086975 | 0.32959 | 121.6827 | -121.8887 | -121.9299
347.8906 | 121.7834 | -119.133 | 2.5772 | -0.005951 | 0.017464 | 0.013962 | 0.00099761 | -0.0062614 | 0.061666 | 0.070938 | -6.871 | 2.6138 | -119.4077 | 2.4719 | -118.9545 | -119.3665 | -0.15106 | -0.009155 | 2.6138 | -119.3985 | -0.27466 | 0.036622 | 112.262 | 121.6049 | -121.5317 | -0.2655 | 0.036622 | 112.5366 | 118.9819 | 119.1238 | 0.17853 | 121.7468 | 112.262 | 121.7468 | -0.23346 | -0.2655 | 121.7468 | 112.262 | -0.23346 | 0.17853 | 121.7468 | -121.9849 | -121.9757
349.5625 | 121.8475 | -119.2062 | 2.4078 | -0.005951 | 0.018532 | 0.016312 | -0.0073336 | -0.0077566 | 0.064657 | 0.068161 | -6.8939 | 2.4673 | -119.4122 | 2.4261 | -118.9774 | -119.3939 | -0.32044 | 0.059509 | 2.4582 | -119.5038 | -0.20599 | 0.059509 | 112.3123 | 121.6324 | -121.3852 | -0.29755 | 0.050354 | 112.5183 | 118.8858 | 119.2657 | 0.22888 | 121.6736 | 112.3123 | 121.6644 | -0.18768 | -0.29755 | 121.6736 | 112.3123 | -0.18768 | 0.22888 | 121.6644 | -121.8201 | -121.9116
351.2969 | 121.8658 | -119.2062 | 2.4445 | -0.013581 | 0.018745 | 0.01204 | -0.005411 | -0.0083976 | 0.06423 | 0.067734 | -6.8893 | 2.4582 | -119.4443 | 2.4261 | -118.9774 | -119.3985 | -0.29297 | 0.064087 | 2.449 | -119.5129 | -0.23804 | 0.013733 | 112.3169 | 121.6324 | -121.4218 | -0.3067 | 0.004578 | 112.5549 | 118.9133 | 119.2703 | 0.22888 | 121.6644 | 112.3169 | 121.6553 | -0.19226 | -0.3067 | 121.6644 | 112.3169 | -0.19226 | 0.22888 | 121.6553 | -121.8887 | -121.9574
353.0469 | 121.7422 | -119.0964 | 2.5772 | -0.005951 | 0.019386 | 0.015885 | -0.00071139 | -0.007543 | 0.062735 | 0.069656 | -6.8665 | 2.6047 | -119.3848 | 2.5681 | -118.8583 | -119.2657 | -0.29755 | 0.086975 | 2.5909 | -119.3619 | -0.28839 | 0.027466 | 112.2299 | 121.6644 | -121.4355 | -0.2655 | 0.013733 | 112.5183 | 118.7988 | 119.1833 | 0.23804 | 121.701 | 112.2299 | 121.6873 | -0.16937 | -0.2655 | 121.701 | 112.2299 | -0.16937 | 0.23804 | 121.6873 | -121.962 | -121.9391
354.7188 | 121.7331 | -118.7485 | 2.9663 | 0.0016785 | 0.015755 | 0.017808 | -0.0019932 | -0.0071158 | 0.061666 | 0.069229 | -6.7749 | 2.9709 | -118.9774 | 2.9663 | -118.4738 | -118.8583 | -0.32501 | 0.09613 | 2.9343 | -118.959 | -0.22888 | 0.004577 | 111.9736 | 121.7148 | -121.4401 | -0.21057 | -0.032044 | 112.2025 | 118.4235 | 118.8446 | 0.27466 | 121.7194 | 111.9736 | 121.6827 | -0.10986 | -0.21057 | 121.7194 | 111.9736 | -0.10986 | 0.27466 | 121.6827 | -121.9437 | -121.9254
356.4688 | 121.756 | -118.9362 | 2.774 | -0.028839 | 0.019173 | 0.014176 | -0.0013522 | -0.0079704 | 0.064657 | 0.072006 | -6.8298 | 2.7878 | -119.1788 | 2.71 | -118.6981 | -119.1193 | -0.25635 | 0.036621 | 2.7786 | -119.1971 | -0.24262 | 0.013733 | 112.1063 | 121.6461 | -121.4722 | -0.26093 | 0.004577 | 112.3489 | 118.6798 | 118.9728 | 0.23804 | 121.7239 | 112.1063 | 121.7148 | -0.18311 | -0.26093 | 121.7239 | 112.1063 | -0.18311 | 0.23804 | 121.7148 | -121.9528 | -121.9711
358.1562 | 121.7377 | -118.6981 | 2.9846 | -0.005951 | 0.018318 | 0.017594 | -0.0051974 | -0.0088248 | 0.063162 | 0.069229 | -6.7337 | 3.0075 | -118.8766 | 3.0579 | -118.3914 | -118.7943 | -0.37537 | 0.11444 | 3.0075 | -118.9178 | -0.17853 | 0.022888 | 111.9644 | 121.756 | -121.376 | -0.21973 | 0.022888 | 112.1429 | 118.3228 | 118.8126 | 0.3067 | 121.7056 | 111.9644 | 121.7056 | -0.09613 | -0.21973 | 121.7056 | 111.9644 | -0.09613 | 0.3067 | 121.7056 | -121.8613 | -121.9025
359.9062 | 121.8475 | -118.5104 | 3.067 | -0.005951 | 0.022163 | 0.01503 | -0.0017794 | -0.01032 | 0.064444 | 0.070083 | -6.7291 | 3.154 | -118.7988 | 3.1082 | -118.3136 | -118.7439 | -0.1831 | 0.13275 | 3.1448 | -118.8675 | -0.28839 | 0.086975 | 111.7813 | 121.6187 | -121.3806 | -0.35706 | 0.077819 | 112.0697 | 118.3273 | 118.6432 | 0.19684 | 121.6644 | 111.7813 | 121.6553 | -0.23346 | -0.35706 | 121.6644 | 111.7813 | -0.23346 | 0.19684 | 121.6553 | -121.8658 | -121.9345
361.5781 | 121.8567 | -118.5883 | 3.0167 | -0.013581 | 0.016396 | 0.010544 | -0.0062656 | -0.006475 | 0.064444 | 0.067734 | -6.8115 | 3.0624 | -118.8675 | 3.0487 | -118.3594 | -118.7759 | -0.3067 | 0.073242 | 3.0533 | -118.8583 | -0.27924 | 0.045776 | 111.7767 | 121.637 | -121.376 | -0.27008 | 0.036621 | 112.056 | 118.2816 | 118.6615 | 0.22888 | 121.6507 | 111.7767 | 121.6415 | -0.18768 | -0.27008 | 121.6507 | 111.7767 | -0.18768 | 0.22888 | 121.6415 | -121.8842 | -121.875
363.25 | 121.8155 | -118.0115 | 3.5843 | -0.005951 | 0.017036 | 0.016099 | -0.0013522 | -0.0090384 | 0.065084 | 0.069015 | -6.5231 | 3.6346 | -118.2541 | 3.6346 | -117.8101 | -118.2083 | -0.43945 | 0.073242 | 3.5934 | -118.3273 | -0.24261 | 0.050354 | 111.4883 | 121.6461 | -121.3943 | -0.31586 | 0.009155 | 111.731 | 117.572 | 118.0847 | 0.20142 | 121.6461 | 111.4883 | 121.6049 | -0.19684 | -0.31586 | 121.6461 | 111.4883 | -0.19684 | 0.20142 | 121.6049 | -121.8384 | -121.9116
364.9844 | 121.8063 | -119.3619 | 2.2888 | -0.013581 | 0.017677 | 0.016526 | -0.0028476 | -0.0069022 | 0.063376 | 0.070083 | -6.9031 | 2.298 | -119.5724 | 2.3117 | -119.1055 | -119.5496 | -0.42572 | 0.054932 | 2.2797 | -119.6228 | -0.21057 | 0.009156 | 112.4588 | 121.6736 | -121.3943 | -0.26093 | -0.009155 | 112.6694 | 118.9362 | 119.4168 | 0.25635 | 121.6599 | 112.4588 | 121.6415 | -0.18768 | -0.26093 | 121.6599 | 112.4588 | -0.18768 | 0.25635 | 121.6415 | -121.8613 | -121.9116
366.7188 | 121.9025 | -119.6045 | 2.0325 | 0.0016785 | 0.018105 | 0.013962 | -0.00071139 | -0.0077566 | 0.060385 | 0.068588 | -6.9717 | 2.1286 | -119.9432 | 2.037 | -119.4031 | -119.8563 | -0.10529 | 0.10071 | 2.1057 | -119.8746 | -0.33875 | 0.09613 | 112.6328 | 121.6415 | -121.4355 | -0.27008 | 0.073242 | 112.9715 | 119.4992 | 119.7052 | 0.20142 | 121.7331 | 112.6328 | 121.7102 | -0.25177 | -0.27008 | 121.7331 | 112.6328 | -0.25177 | 0.20142 | 121.7102 | -121.9757 | -121.907
368.3906 | 121.9116 | -120.1996 | 1.4603 | 0.0016785 | 0.0196 | 0.015244 | -0.0039158 | -0.0077566 | 0.06188 | 0.068374 | -7.1457 | 1.5472 | -120.4834 | 1.4099 | -120.0256 | -120.4742 | -0.10986 | 0.045776 | 1.5564 | -120.5109 | -0.28381 | 0.086975 | 113.0539 | 121.6095 | -121.4859 | -0.31128 | 0.09613 | 113.3377 | 120.0897 | 120.2454 | 0.17395 | 121.7468 | 113.0539 | 121.756 | -0.27466 | -0.31128 | 121.7468 | 113.0539 | -0.27466 | 0.17395 | 121.756 | -121.9437 | -121.9711
370.0625 | 121.8613 | -120.3644 | 1.3229 | -0.013581 | 0.019173 | 0.01439 | -0.00071139 | -0.005834 | 0.064016 | 0.070511 | -7.1182 | 1.4008 | -120.6573 | 1.3229 | -120.1218 | -120.5795 | -0.13275 | 0.10986 | 1.4053 | -120.5887 | -0.29297 | 0.07782 | 113.2462 | 121.6873 | -121.4447 | -0.2243 | 0.082397 | 113.5391 | 120.2316 | 120.4742 | 0.24262 | 121.7651 | 113.2462 | 121.7697 | -0.21515 | -0.2243 | 121.7651 | 113.2462 | -0.21515 | 0.24262 | 121.7697 | -121.9803 | -121.9116
371.7969 | 121.8796 | -120.1263 | 1.5656 | -0.005951 | 0.019813 | 0.013962 | -0.0096836 | -0.0090384 | 0.063803 | 0.068802 | -7.0267 | 1.593 | -120.3552 | 1.5839 | -119.8471 | -120.2866 | -0.31128 | 0.14191 | 1.5701 | -120.3964 | -0.22888 | 0.027466 | 113.0997 | 121.7102 | -121.4127 | -0.27008 | 0.004577 | 113.3286 | 119.8151 | 120.2683 | 0.27924 | 121.7194 | 113.0997 | 121.6965 | -0.16022 | -0.27008 | 121.7194 | 113.0997 | -0.16022 | 0.27924 | 121.6965 | -121.9208 | -121.962
373.4688 | 121.9345 | -120.1309 | 1.5427 | -0.005951 | 0.020882 | 0.015244 | -0.0028476 | -0.0086112 | 0.062735 | 0.071579 | -7.1091 | 1.6434 | -120.4147 | 1.5244 | -119.9341 | -120.3873 | -0.086975 | 0.064087 | 1.6342 | -120.4239 | -0.28381 | 0.10071 | 113.0219 | 121.6553 | -121.4767 | -0.29297 | 0.091552 | 113.3057 | 120.0439 | 120.195 | 0.19684 | 121.7743 | 113.0219 | 121.7651 | -0.25635 | -0.29297 | 121.7743 | 113.0219 | -0.25635 | 0.19684 | 121.7651 | -121.9574 | -121.9666
375.2031 | 121.9254 | -120.0485 | 1.6525 | -0.005951 | 0.021522 | 0.013108 | -0.0028476 | -0.0094656 | 0.062948 | 0.069443 | -7.1091 | 1.7395 | -120.3278 | 1.6205 | -119.8563 | -120.3049 | -0.091553 | 0.059509 | 1.7303 | -120.3461 | -0.27924 | 0.086975 | 112.9395 | 121.669 | -121.5088 | -0.29755 | 0.07782 | 113.2187 | 119.957 | 120.108 | 0.19226 | 121.788 | 112.9395 | 121.7789 | -0.25635 | -0.29755 | 121.788 | 112.9395 | -0.25635 | 0.19226 | 121.7789 | -121.9803 | -121.9986
376.9375 | 121.9116 | -120.5566 | 1.1124 | -0.005951 | 0.017677 | 0.013749 | -0.0066928 | -0.0096794 | 0.065939 | 0.071792 | -7.1732 | 1.1856 | -120.8176 | 1.1398 | -120.2957 | -120.7352 | -0.3067 | 0.10529 | 1.1581 | -120.8542 | -0.26093 | 0.073242 | 113.3835 | 121.6965 | -121.4081 | -0.29755 | 0.045776 | 113.6444 | 120.2499 | 120.6619 | 0.26093 | 121.7422 | 113.3835 | 121.7148 | -0.17853 | -0.29755 | 121.7422 | 113.3835 | -0.17853 | 0.26093 | 121.7148 | -121.9299 | -121.9666
378.6719 | 121.8018 | -120.2911 | 1.4191 | -0.005951 | 0.018745 | 0.015671 | -0.0058384 | -0.0090384 | 0.065512 | 0.070297 | -7.0587 | 1.4694 | -120.5109 | 1.4603 | -120.0256 | -120.433 | -0.37994 | 0.091553 | 1.4603 | -120.5338 | -0.21973 | 0.050354 | 113.2324 | 121.7514 | -121.4447 | -0.24261 | 0.041199 | 113.4521 | 119.9112 | 120.3827 | 0.2655 | 121.7606 | 113.2324 | 121.7514 | -0.14191 | -0.24261 | 121.7606 | 113.2324 | -0.14191 | 0.2655 | 121.7514 | -121.9299 | -121.9528
380.3594 | 121.9345 | -120.4697 | 1.2451 | -0.005951 | 0.017677 | 0.014176 | -0.0011386 | -0.010107 | 0.064444 | 0.068161 | -7.0862 | 1.593 | -120.4742 | 1.4694 | -120.0348 | -120.6436 | -0.32044 | -0.16022 | 1.5152 | -120.7077 | -0.004577 | 0.3479 | 113.3835 | 121.9391 | -121.2799 | -0.23804 | 0.27008 | 113.3881 | 120.1492 | 120.3094 | 0.43488 | 122.0627 | 113.3835 | 121.9849 | -0.17395 | -0.23804 | 122.0627 | 113.3835 | -0.17395 | 0.43488 | 121.9849 | -121.7194 | -121.9528
382.0938 | 121.8521 | -120.2637 | 1.4648 | -0.013581 | 0.0196 | 0.015458 | -0.0039158 | -0.008184 | 0.06658 | 0.070511 | -7.1091 | 1.5244 | -120.4559 | 1.4923 | -119.9615 | -120.3873 | -0.3479 | 0.050354 | 1.4969 | -120.5109 | -0.19226 | 0.059509 | 113.1546 | 121.756 | -121.4264 | -0.24719 | 0.032043 | 113.3469 | 119.9158 | 120.314 | 0.30212 | 121.788 | 113.1546 | 121.7606 | -0.1236 | -0.24719 | 121.788 | 113.1546 | -0.1236 | 0.30212 | 121.7606 | -121.9208 | -121.9757
383.8438 | 121.7743 | -120.314 | 1.4557 | -0.005951 | 0.018745 | 0.015885 | 0.00099761 | -0.0071158 | 0.060385 | 0.068161 | -7.0908 | 1.5015 | -120.5704 | 1.4603 | -120.0302 | -120.4651 | -0.1831 | 0.12817 | 1.4877 | -120.5017 | -0.25635 | 0.045777 | 113.2233 | 121.7743 | -121.4859 | -0.18768 | 0.032044 | 113.4796 | 120.1309 | 120.4422 | 0.28381 | 121.8155 | 113.2233 | 121.8018 | -0.15106 | -0.18768 | 121.8155 | 113.2233 | -0.15106 | 0.28381 | 121.8018 | -122.0261 | -121.9574
385.5312 | 121.875 | -120.3278 | 1.3504 | -0.005951 | 0.019813 | 0.017167 | -0.007761 | -0.0066886 | 0.062948 | 0.06987 | -7.0999 | 1.4053 | -120.5566 | 1.4374 | -120.0256 | -120.4514 | -0.3479 | 0.14648 | 1.4099 | -120.5933 | -0.22888 | 0.054931 | 113.2278 | 121.7651 | -121.376 | -0.2655 | 0.059509 | 113.4567 | 119.9799 | 120.4742 | 0.30212 | 121.7331 | 113.2278 | 121.7377 | -0.1236 | -0.2655 | 121.7331 | 113.2278 | -0.1236 | 0.30212 | 121.7377 | -121.907 | -121.9437
387.2656 | 121.8567 | -120.0577 | 1.6571 | -0.013581 | 0.015755 | 0.015458 | -0.0064792 | -0.0083976 | 0.062948 | 0.069443 | -7.0129 | 1.68 | -120.2866 | 1.7532 | -119.7327 | -120.1584 | -0.32501 | 0.17853 | 1.6754 | -120.2591 | -0.22888 | 0.022889 | 113.0447 | 121.8109 | -121.3898 | -0.20142 | 0.018311 | 113.2736 | 119.7327 | 120.2362 | 0.32501 | 121.7377 | 113.0447 | 121.7331 | -0.10071 | -0.20142 | 121.7377 | 113.0447 | -0.10071 | 0.32501 | 121.7331 | -121.9437 | -121.9162
389 | 121.7468 | -120.1492 | 1.6022 | 0.009308 | 0.018105 | 0.016099 | -0.0022068 | -0.0071158 | 0.063376 | 0.070511 | -7.0084 | 1.6067 | -120.3964 | 1.6479 | -119.8334 | -120.2408 | -0.37537 | 0.13733 | 1.5793 | -120.3644 | -0.24719 | 0.004577 | 113.1409 | 121.7972 | -121.4355 | -0.21515 | -0.022888 | 113.3881 | 119.7739 | 120.2866 | 0.31586 | 121.756 | 113.1409 | 121.7285 | -0.091553 | -0.21515 | 121.756 | 113.1409 | -0.091553 | 0.31586 | 121.7285 | -121.9986 | -121.9666
390.75 | 121.7606 | -120.1813 | 1.5472 | 0.009308 | 0.017464 | 0.015458 | -0.0019932 | -0.0079704 | 0.064016 | 0.06987 | -7.0633 | 1.5839 | -120.4285 | 1.593 | -119.902 | -120.3049 | -0.33875 | 0.10529 | 1.5518 | -120.4056 | -0.24719 | 0.036621 | 113.118 | 121.7743 | -121.4493 | -0.22431 | 0.004578 | 113.3652 | 119.8425 | 120.2866 | 0.27923 | 121.7651 | 113.118 | 121.7331 | -0.1236 | -0.22431 | 121.7651 | 113.118 | -0.1236 | 0.27923 | 121.7331 | -121.9757 | -121.9528
392.4375 | 121.8246 | -120.1035 | 1.6205 | 0.0016785 | 0.017464 | 0.016312 | -0.0034884 | -0.007543 | 0.064657 | 0.071365 | -7.1182 | 1.68 | -120.401 | 1.5381 | -119.957 | -120.3781 | -0.13733 | -0.018311 | 1.6708 | -120.3964 | -0.29755 | 0.05951 | 112.9852 | 121.6415 | -121.5775 | -0.29297 | 0.050354 | 113.2828 | 119.9661 | 120.0851 | 0.14648 | 121.7834 | 112.9852 | 121.7743 | -0.27466 | -0.29297 | 121.7834 | 112.9852 | -0.27466 | 0.14648 | 121.7743 | -122.0215 | -122.0169
394.1875 | 121.9025 | -120.0943 | 1.6113 | -0.005951 | 0.019173 | 0.01204 | -0.0017794 | -0.007543 | 0.064016 | 0.068374 | -7.1503 | 1.6754 | -120.401 | 1.5472 | -119.9203 | -120.3781 | -0.10986 | 0.064087 | 1.6617 | -120.3918 | -0.3067 | 0.064087 | 112.944 | 121.6415 | -121.5317 | -0.29755 | 0.050354 | 113.2507 | 119.9844 | 120.1584 | 0.17395 | 121.7697 | 112.944 | 121.756 | -0.28381 | -0.29755 | 121.7697 | 112.944 | -0.28381 | 0.17395 | 121.756 | -122.0123 | -122.0032
395.9531 | 121.7789 | -120.1172 | 1.6388 | 0.0016785 | 0.020027 | 0.016312 | -0.00071139 | -0.0066886 | 0.062094 | 0.070938 | -7.0221 | 1.6663 | -120.3781 | 1.6251 | -119.8654 | -120.314 | -0.18768 | 0.09613 | 1.6663 | -120.3827 | -0.26093 | 0.027466 | 113.0951 | 121.7422 | -121.5042 | -0.2655 | 0.027466 | 113.356 | 119.9295 | 120.2133 | 0.25177 | 121.7834 | 113.0951 | 121.7834 | -0.19684 | -0.2655 | 121.7834 | 113.0951 | -0.19684 | 0.25177 | 121.7834 | -122.0169 | -122.0215
397.6406 | 121.8338 | -120.1218 | 1.5701 | 0.009308 | 0.020027 | 0.018235 | -0.0017794 | -0.0071158 | 0.062948 | 0.070511 | -7.1548 | 1.6571 | -120.433 | 1.5152 | -119.957 | -120.3781 | -0.16022 | 0.004578 | 1.6571 | -120.4056 | -0.31128 | 0.086975 | 112.9669 | 121.637 | -121.5271 | -0.28381 | 0.086975 | 113.2782 | 119.9615 | 120.1263 | 0.16479 | 121.7789 | 112.9669 | 121.7789 | -0.25635 | -0.28381 | 121.7789 | 112.9669 | -0.25635 | 0.16479 | 121.7789 | -122.0032 | -121.9757
399.375 | 121.9025 | -120.3918 | 1.2955 | 0.0016785 | 0.015755 | 0.014603 | -0.010965 | -0.0079704 | 0.064657 | 0.070511 | -7.164 | 1.3458 | -120.6482 | 1.3321 | -120.1263 | -120.5292 | -0.32501 | 0.11902 | 1.3367 | -120.6894 | -0.25635 | 0.050354 | 113.2278 | 121.7239 | -121.4218 | -0.29755 | 0.041199 | 113.4842 | 120.0668 | 120.5109 | 0.2655 | 121.7377 | 113.2278 | 121.7285 | -0.13733 | -0.29755 | 121.7377 | 113.2278 | -0.13733 | 0.2655 | 121.7285 | -121.9437 | -121.9849
401.0469 | 121.8475 | -120.1813 | 1.5106 | -0.013581 | 0.015755 | 0.012253 | -0.0066928 | -0.0079704 | 0.061453 | 0.068588 | -7.0679 | 1.5198 | -120.4422 | 1.5884 | -119.902 | -120.3232 | -0.29755 | 0.17853 | 1.5381 | -120.4376 | -0.26093 | 0.009155 | 113.1134 | 121.7697 | -121.4127 | -0.25635 | 0.027466 | 113.3743 | 119.8837 | 120.3598 | 0.27923 | 121.701 | 113.1134 | 121.7194 | -0.14191 | -0.25635 | 121.701 | 113.1134 | -0.14191 | 0.27923 | 121.7194 | -121.9528 | -121.9482
402.7969 | 121.8704 | -120.4742 | 1.2085 | 0.0016785 | 0.015755 | 0.01204 | -0.0062656 | -0.007543 | 0.063376 | 0.06987 | -7.1274 | 1.2817 | -120.7031 | 1.3275 | -120.1675 | -120.5887 | -0.34332 | 0.16937 | 1.268 | -120.7352 | -0.22888 | 0.073242 | 113.3469 | 121.8018 | -121.376 | -0.26093 | 0.059509 | 113.5757 | 120.1309 | 120.6436 | 0.3067 | 121.756 | 113.3469 | 121.7422 | -0.11444 | -0.26093 | 121.756 | 113.3469 | -0.11444 | 0.3067 | 121.7422 | -121.9116 | -121.9437
404.5312 | 121.7834 | -120.5017 | 1.2589 | -0.013581 | 0.018318 | 0.01503 | -0.0015658 | -0.0077566 | 0.064016 | 0.070938 | -7.1182 | 1.2634 | -120.7581 | 1.3138 | -120.1813 | -120.607 | -0.37994 | 0.14648 | 1.2405 | -120.7489 | -0.25635 | 0.004578 | 113.3835 | 121.8155 | -121.4401 | -0.24719 | -0.01831 | 113.6398 | 120.1218 | 120.6482 | 0.32044 | 121.7651 | 113.3835 | 121.7422 | -0.10529 | -0.24719 | 121.7651 | 113.3835 | -0.10529 | 0.32044 | 121.7422 | -122.0169 | -122.0078
406.2812 | 121.8567 | -120.0302 | 1.6708 | -0.005951 | 0.018532 | 0.01204 | -0.0037022 | -0.010107 | 0.063803 | 0.067734 | -7.1091 | 1.7395 | -120.2866 | 1.7212 | -119.7647 | -120.163 | -0.32959 | 0.054932 | 1.7258 | -120.2774 | -0.25635 | 0.068665 | 112.9211 | 121.7514 | -121.4355 | -0.24719 | 0.054932 | 113.1775 | 119.7006 | 120.0851 | 0.2655 | 121.7697 | 112.9211 | 121.756 | -0.13275 | -0.24719 | 121.7697 | 112.9211 | -0.13275 | 0.2655 | 121.756 | -121.9574 | -121.9482
408.0156 | 121.8155 | -120.52 | 1.2222 | -0.005951 | 0.018105 | 0.018876 | -0.0030612 | -0.005834 | 0.06423 | 0.069015 | -7.196 | 1.2726 | -120.7718 | 1.1993 | -120.314 | -120.7306 | -0.27466 | 0.041199 | 1.2634 | -120.7352 | -0.25177 | 0.050354 | 113.324 | 121.7194 | -121.5363 | -0.21515 | 0.041199 | 113.5757 | 120.2454 | 120.5612 | 0.20599 | 121.7926 | 113.324 | 121.7834 | -0.21057 | -0.21515 | 121.7926 | 113.324 | -0.21057 | 0.20599 | 121.7834 | -121.994 | -121.9574
409.75 | 121.8292 | -120.5475 | 1.236 | -0.005951 | 0.019173 | 0.01204 | 0.00078401 | -0.0049796 | 0.059744 | 0.069229 | -7.1594 | 1.268 | -120.7993 | 1.1765 | -120.3186 | -120.7672 | -0.15564 | 0.032043 | 1.2772 | -120.7901 | -0.25177 | 0.032043 | 113.3881 | 121.7239 | -121.5546 | -0.24262 | 0.041199 | 113.6398 | 120.3918 | 120.5795 | 0.22888 | 121.8155 | 113.3881 | 121.8246 | -0.21973 | -0.24262 | 121.8155 | 113.3881 | -0.21973 | 0.22888 | 121.8246 | -122.0352 | -122.0261
411.4219 | 121.8063 | -120.4697 | 1.3138 | -0.013581 | 0.020882 | 0.016312 | -0.0019932 | -0.006475 | 0.062307 | 0.070297 | -7.1732 | 1.3458 | -120.7031 | 1.2497 | -120.2316 | -120.6528 | -0.27466 | 0.027466 | 1.355 | -120.7489 | -0.23346 | 0.032043 | 113.2965 | 121.7194 | -121.5454 | -0.27923 | 0.041198 | 113.53 | 120.195 | 120.4971 | 0.23804 | 121.8155 | 113.2965 | 121.8246 | -0.1831 | -0.27923 | 121.8155 | 113.2965 | -0.1831 | 0.23804 | 121.8246 | -122.0169 | -122.0627
413.1719 | 121.7834 | -120.4742 | 1.3046 | -0.005951 | 0.020454 | 0.02208 | -0.0041294 | -0.0062614 | 0.062735 | 0.068588 | -7.1274 | 1.3641 | -120.6985 | 1.2909 | -120.2133 | -120.6619 | -0.17395 | 0.10071 | 1.3687 | -120.6894 | -0.2243 | 0.05951 | 113.3469 | 121.7651 | -121.5179 | -0.21515 | 0.064087 | 113.5712 | 120.3003 | 120.575 | 0.26093 | 121.8384 | 113.3469 | 121.843 | -0.18768 | -0.21515 | 121.8384 | 113.3469 | -0.18768 | 0.26093 | 121.843 | -122.0032 | -121.994
414.9219 | 121.9025 | -120.5383 | 1.1627 | -0.005951 | 0.019386 | 0.016099 | -0.0034884 | -0.0071158 | 0.063376 | 0.070938 | -7.2372 | 1.236 | -120.8954 | 1.1307 | -120.3369 | -120.8038 | -0.13275 | 0.036621 | 1.2314 | -120.845 | -0.35706 | 0.073242 | 113.3011 | 121.669 | -121.4996 | -0.3067 | 0.068664 | 113.6581 | 120.4056 | 120.575 | 0.20142 | 121.7743 | 113.3011 | 121.7697 | -0.2655 | -0.3067 | 121.7743 | 113.3011 | -0.2655 | 0.20142 | 121.7697 | -122.0581 | -122.0078
416.6094 | 121.7514 | -120.6482 | 1.1261 | -0.005951 | 0.020027 | 0.015244 | -0.004343 | -0.0088248 | 0.06423 | 0.070724 | -7.1869 | 1.1444 | -120.8496 | 1.1765 | -120.3232 | -120.726 | -0.40283 | 0.10986 | 1.1261 | -120.9 | -0.20142 | 0.01831 | 113.4613 | 121.8246 | -121.4493 | -0.25177 | 0 | 113.6627 | 120.2454 | 120.7581 | 0.32501 | 121.7926 | 113.4613 | 121.7743 | -0.07782 | -0.25177 | 121.7926 | 113.4613 | -0.07782 | 0.32501 | 121.7743 | -121.9757 | -122.0261
418.3438 | 121.8384 | -120.5566 | 1.181 | -0.005951 | 0.019386 | 0.011826 | 0.00014321 | -0.0071158 | 0.06188 | 0.067734 | -7.1869 | 1.2451 | -120.8267 | 1.1719 | -120.3186 | -120.7535 | -0.15564 | 0.10529 | 1.2177 | -120.8267 | -0.27008 | 0.064087 | 113.3698 | 121.7285 | -121.4996 | -0.27008 | 0.036621 | 113.6398 | 120.401 | 120.6619 | 0.23804 | 121.8018 | 113.3698 | 121.7743 | -0.19684 | -0.27008 | 121.8018 | 113.3698 | -0.19684 | 0.23804 | 121.7743 | -122.0078 | -122.0078
420.0781 | 121.8155 | -120.6299 | 1.1536 | 0.009308 | 0.021095 | 0.018448 | -0.0019932 | -0.0073294 | 0.063162 | 0.070938 | -7.1548 | 1.1993 | -120.8633 | 1.1627 | -120.3323 | -120.7718 | -0.17395 | 0.12817 | 1.1993 | -120.8542 | -0.23346 | 0.045777 | 113.475 | 121.7926 | -121.4859 | -0.2243 | 0.045777 | 113.7085 | 120.4559 | 120.7581 | 0.29755 | 121.8292 | 113.475 | 121.8292 | -0.14191 | -0.2243 | 121.8292 | 113.475 | -0.14191 | 0.29755 | 121.8292 | -122.0169 | -122.0078
421.75 | 121.8109 | -120.4605 | 1.3092 | 0.0016785 | 0.020668 | 0.016739 | -0.00049779 | -0.0077566 | 0.063162 | 0.072433 | -7.2144 | 1.3596 | -120.694 | 1.2543 | -120.2499 | -120.6528 | -0.24261 | 0.022888 | 1.3504 | -120.6985 | -0.23346 | 0.050354 | 113.2462 | 121.7148 | -121.5591 | -0.23804 | 0.041199 | 113.4796 | 120.2179 | 120.4834 | 0.21057 | 121.8201 | 113.2462 | 121.8109 | -0.19226 | -0.23804 | 121.8201 | 113.2462 | -0.19226 | 0.21057 | 121.8109 | -122.0032 | -122.0078
423.4844 | 121.9025 | -120.4788 | 1.2268 | -0.013581 | 0.017891 | 0.010544 | -0.0064792 | -0.0086112 | 0.064871 | 0.069443 | -7.1457 | 1.2772 | -120.7077 | 1.2772 | -120.195 | -120.639 | -0.21515 | 0.14191 | 1.2817 | -120.7352 | -0.22888 | 0.050354 | 113.3331 | 121.756 | -121.4218 | -0.25635 | 0.054931 | 113.562 | 120.2637 | 120.6207 | 0.28381 | 121.756 | 113.3331 | 121.7606 | -0.16022 | -0.25635 | 121.756 | 113.3331 | -0.16022 | 0.28381 | 121.7606 | -121.9345 | -121.962
425.2188 | 121.9208 | -120.4239 | 1.2589 | 0.0016785 | 0.01725 | 0.0096899 | -0.0062656 | -0.010534 | 0.063162 | 0.069443 | -7.2418 | 1.3138 | -120.694 | 1.2955 | -120.1859 | -120.6024 | -0.31128 | 0.082397 | 1.3092 | -120.6985 | -0.27008 | 0.054932 | 113.1821 | 121.7194 | -121.4447 | -0.27466 | 0.050354 | 113.4521 | 120.1126 | 120.5063 | 0.23804 | 121.7377 | 113.1821 | 121.7331 | -0.17853 | -0.27466 | 121.7377 | 113.1821 | -0.17853 | 0.23804 | 121.7331 | -121.9528 | -121.9574
426.8906 | 121.788 | -120.5566 | 1.2314 | -0.005951 | 0.018745 | 0.014176 | -0.00049779 | -0.0066886 | 0.061026 | 0.069443 | -7.1686 | 1.2497 | -120.8221 | 1.2131 | -120.2911 | -120.7397 | -0.17853 | 0.13275 | 1.2634 | -120.7718 | -0.2655 | 0.018311 | 113.3881 | 121.7697 | -121.5225 | -0.21515 | 0.032044 | 113.6536 | 120.3781 | 120.6894 | 0.2655 | 121.8063 | 113.3881 | 121.8201 | -0.1831 | -0.21515 | 121.8063 | 113.3881 | -0.1831 | 0.2655 | 121.8201 | -122.0535 | -122.0032
428.625 | 121.8704 | -120.5933 | 1.1581 | -0.02121 | 0.019386 | 0.016099 | -0.0047702 | -0.007543 | 0.062948 | 0.069443 | -7.1548 | 1.2085 | -120.7764 | 1.2497 | -120.2499 | -120.694 | -0.30212 | 0.16022 | 1.1993 | -120.8084 | -0.1831 | 0.050354 | 113.4384 | 121.843 | -121.4081 | -0.21515 | 0.041199 | 113.6215 | 120.2911 | 120.7535 | 0.34332 | 121.8018 | 113.4384 | 121.7926 | -0.10071 | -0.21515 | 121.8018 | 113.4384 | -0.10071 | 0.34332 | 121.7926 | -121.9345 | -121.9666
430.3594 | 121.7789 | -120.5658 | 1.1627 | -0.02121 | 0.018745 | 0.014817 | -0.00071139 | -0.0066886 | 0.062307 | 0.068802 | -7.2006 | 1.1948 | -120.8267 | 1.1948 | -120.3003 | -120.7169 | -0.34332 | 0.086975 | 1.1856 | -120.8405 | -0.26093 | 0.032043 | 113.3652 | 121.7606 | -121.463 | -0.27466 | 0.022888 | 113.6261 | 120.2225 | 120.6528 | 0.2655 | 121.7606 | 113.3652 | 121.7514 | -0.15106 | -0.27466 | 121.7606 | 113.3652 | -0.15106 | 0.2655 | 121.7514 | -121.9894 | -122.0032
432.1094 | 121.7468 | -120.6299 | 1.1307 | -0.013581 | 0.020241 | 0.016312 | -0.0024204 | -0.0096794 | 0.064016 | 0.070297 | -7.4844 | 1.149 | -120.8267 | 1.1765 | -120.3186 | -120.7306 | -0.68207 | -0.14191 | 1.1307 | -120.8954 | -0.19684 | 0.018311 | 113.1454 | 121.8063 | -121.4493 | -0.2655 | 0 | 113.3423 | 119.9478 | 120.488 | 0.31128 | 121.7789 | 113.1454 | 121.7606 | -0.10071 | -0.2655 | 121.7789 | 113.1454 | -0.10071 | 0.31128 | 121.7606 | -121.9574 | -122.0261
433.8438 | 121.8292 | -119.9066 | 1.8402 | -0.013581 | 0.016823 | 0.015671 | -0.00028419 | -0.008184 | 0.061666 | 0.068588 | -7.0724 | 1.9135 | -120.1767 | 1.767 | -119.7235 | -120.1401 | -0.11444 | 0.054932 | 1.8906 | -120.1767 | -0.27008 | 0.073242 | 112.8342 | 121.6736 | -121.5637 | -0.27008 | 0.050354 | 113.1042 | 119.7922 | 119.9615 | 0.1831 | 121.8201 | 112.8342 | 121.7972 | -0.23346 | -0.27008 | 121.8201 | 112.8342 | -0.23346 | 0.1831 | 121.7972 | -122.0169 | -122.0169
435.5156 | 121.8842 | -121.0007 | 0.71411 | -0.02121 | 0.021095 | 0.016953 | -0.0032748 | -0.0094656 | 0.060812 | 0.069656 | -7.3242 | 0.79651 | -121.3165 | 0.6958 | -120.8084 | -121.2433 | -0.13733 | 0.086975 | 0.79193 | -121.3257 | -0.31586 | 0.082398 | 113.6765 | 121.6965 | -121.5225 | -0.32501 | 0.07782 | 113.9923 | 120.8633 | 121.0876 | 0.19226 | 121.7972 | 113.6765 | 121.7926 | -0.24262 | -0.32501 | 121.7972 | 113.6765 | -0.24262 | 0.19226 | 121.7926 | -122.0306 | -122.0398
437.25 | 121.8704 | -120.8084 | 0.90637 | -0.005951 | 0.015968 | 0.013321 | -0.0075474 | -0.0090384 | 0.062735 | 0.06987 | -7.2418 | 0.94757 | -121.0419 | 1.0025 | -120.5017 | -120.9274 | -0.34332 | 0.14648 | 0.92926 | -121.0922 | -0.23346 | 0.041199 | 113.5666 | 121.8109 | -121.4081 | -0.28381 | 0.022888 | 113.8 | 120.4651 | 120.9549 | 0.3067 | 121.756 | 113.5666 | 121.7377 | -0.11902 | -0.28381 | 121.756 | 113.5666 | -0.11902 | 0.3067 | 121.7377 | -121.9482 | -121.9986
438.9844 | 121.7972 | -121.2479 | 0.49896 | -0.02121 | 0.020241 | 0.015458 | -0.0024204 | -0.0088248 | 0.063589 | 0.069656 | -7.3792 | 0.55847 | -121.5179 | 0.47607 | -121.0281 | -121.4493 | -0.28839 | 0.032043 | 0.55389 | -121.5042 | -0.27008 | 0.05951 | 113.8687 | 121.7239 | -121.5271 | -0.25635 | 0.054932 | 114.1388 | 120.9595 | 121.2799 | 0.21973 | 121.8063 | 113.8687 | 121.8018 | -0.20142 | -0.25635 | 121.8063 | 113.8687 | -0.20142 | 0.21973 | 121.8018 | -122.0169 | -122.0032
440.7188 | 121.9162 | -121.2067 | 0.48065 | -0.013581 | 0.018318 | 0.013108 | -0.0075474 | -0.009252 | 0.065084 | 0.070297 | -7.402 | 0.53558 | -121.4859 | 0.49896 | -120.9869 | -121.4172 | -0.3067 | 0.050354 | 0.52185 | -121.5454 | -0.27924 | 0.054931 | 113.8046 | 121.7056 | -121.4676 | -0.33875 | 0.041199 | 114.0839 | 120.9 | 121.257 | 0.21973 | 121.7422 | 113.8046 | 121.7285 | -0.21057 | -0.33875 | 121.7422 | 113.8046 | -0.21057 | 0.21973 | 121.7285 | -121.9666 | -122.0261
442.3906 | 121.7789 | -121.4172 | 0.36163 | -0.013581 | 0.017464 | 0.021012 | -0.002634 | -0.0083976 | 0.064444 | 0.068802 | -7.3471 | 0.37994 | -121.5958 | 0.43945 | -121.0556 | -121.4951 | -0.39368 | 0.11902 | 0.37537 | -121.6232 | -0.17853 | 0.018311 | 114.0701 | 121.8567 | -121.4172 | -0.20599 | 0.013733 | 114.2487 | 121.0236 | 121.5363 | 0.36163 | 121.7972 | 114.0701 | 121.7926 | -0.07782 | -0.20599 | 121.7972 | 114.0701 | -0.07782 | 0.36163 | 121.7926 | -121.9574 | -121.9849
444.0781 | 121.788 | -121.4218 | 0.37537 | -0.013581 | 0.020027 | 0.013749 | -0.0030612 | -0.0088248 | 0.066153 | 0.070083 | -7.3563 | 0.36163 | -121.6278 | 0.42114 | -121.1014 | -121.5134 | -0.38452 | 0.1236 | 0.37537 | -121.6507 | -0.20599 | -0.013733 | 114.0656 | 121.843 | -121.4767 | -0.22888 | 0 | 114.2715 | 121.0373 | 121.5454 | 0.32044 | 121.7834 | 114.0656 | 121.7972 | -0.091553 | -0.22888 | 121.7834 | 114.0656 | -0.091553 | 0.32044 | 121.7972 | -122.0032 | -122.0261
445.8281 | 121.8246 | -121.1838 | 0.55847 | -0.005951 | 0.022163 | 0.01439 | 0.00014321 | -0.0086112 | 0.06423 | 0.069229 | -7.3883 | 0.64545 | -121.4767 | 0.5127 | -120.9869 | -121.4493 | -0.14648 | 0.013733 | 0.61798 | -121.4539 | -0.29297 | 0.086975 | 113.7955 | 121.6965 | -121.5454 | -0.27008 | 0.059509 | 114.0884 | 121.0373 | 121.1975 | 0.19684 | 121.8292 | 113.7955 | 121.8018 | -0.2655 | -0.27008 | 121.8292 | 113.7955 | -0.2655 | 0.19684 | 121.8018 | -122.0352 | -122.0123
447.5625 | 121.6003 | -121.3989 | 0.17853 | 0.0016785 | 0.019813 | 0.016099 | 0.00035681 | -0.0073294 | 0.062094 | 0.071151 | -7.8323 | 0.2243 | -121.6644 | 0.17853 | -121.1243 | -121.5912 | -0.24719 | 0.09613 | 0.2243 | -121.6736 | -0.2655 | 0.045776 | 113.5666 | 121.5775 | -121.3028 | -0.27466 | 0.045776 | 113.8321 | 121.1517 | 121.4951 | 0.27466 | 121.6232 | 113.5666 | 121.6232 | -0.19226 | -0.27466 | 121.6232 | 113.5666 | -0.19226 | 0.27466 | 121.6232 | -121.843 | -121.8521
449.2344 | 121.788 | -121.5866 | 0.16479 | 0.0016785 | 0.019813 | 0.014176 | -0.0030612 | -0.0086112 | 0.063376 | 0.069656 | -7.4341 | 0.21973 | -121.8201 | 0.18768 | -121.2982 | -121.756 | -0.1831 | 0.1236 | 0.23804 | -121.8155 | -0.23346 | 0.054932 | 114.1525 | 121.7743 | -121.463 | -0.22888 | 0.073242 | 114.386 | 121.4035 | 121.7102 | 0.28839 | 121.8063 | 114.1525 | 121.8246 | -0.16937 | -0.22888 | 121.8063 | 114.1525 | -0.16937 | 0.28839 | 121.8246 | -121.9849 | -121.9803
450.9844 | 121.7697 | -121.5866 | 0.16937 | -0.005951 | 0.018532 | 0.0099037 | -0.0066928 | -0.0077566 | 0.062521 | 0.070297 | -7.4158 | 0.19226 | -121.8109 | 0.21515 | -121.2524 | -121.6736 | -0.3891 | 0.10071 | 0.20142 | -121.7743 | -0.2243 | 0.022888 | 114.1708 | 121.8018 | -121.4218 | -0.18768 | 0.032043 | 114.3951 | 121.1975 | 121.6873 | 0.33417 | 121.7789 | 114.1708 | 121.788 | -0.086975 | -0.18768 | 121.7789 | 114.1708 | -0.086975 | 0.33417 | 121.788 | -121.9803 | -121.9437
452.6719 | 121.8613 | -121.55 | 0.14648 | -0.013581 | 0.019813 | 0.013535 | -0.0090426 | -0.0073294 | 0.062307 | 0.068802 | -7.402 | 0.18768 | -121.788 | 0.25177 | -121.2112 | -121.6644 | -0.32959 | 0.16937 | 0.19226 | -121.8201 | -0.23804 | 0.041199 | 114.1479 | 121.8018 | -121.3577 | -0.27008 | 0.045777 | 114.386 | 121.2204 | 121.7194 | 0.33875 | 121.7377 | 114.1479 | 121.7422 | -0.11444 | -0.27008 | 121.7377 | 114.1479 | -0.11444 | 0.33875 | 121.7422 | -121.9345 | -121.9666
454.4062 | 121.7972 | -121.5866 | 0.1831 | 0.0016785 | 0.020454 | 0.015458 | -0.0013522 | -0.0069022 | 0.063803 | 0.071792 | -7.4707 | 0.23804 | -121.8338 | 0.13733 | -121.344 | -121.788 | -0.27924 | 0.032043 | 0.21515 | -121.8567 | -0.24719 | 0.054932 | 114.1159 | 121.7239 | -121.5271 | -0.27008 | 0.032044 | 114.3631 | 121.3074 | 121.6187 | 0.24262 | 121.8246 | 114.1159 | 121.8018 | -0.20142 | -0.27008 | 121.8246 | 114.1159 | -0.20142 | 0.24262 | 121.8018 | -122.0169 | -122.0398
456.1562 | 121.7606 | -121.5866 | 0.19226 | -0.005951 | 0.017464 | 0.01738 | -0.0028476 | -0.0077566 | 0.063162 | 0.068161 | -7.3883 | 0.20599 | -121.7834 | 0.23346 | -121.2479 | -121.669 | -0.42114 | 0.11902 | 0.18768 | -121.8475 | -0.19684 | 0.013733 | 114.1983 | 121.8201 | -121.4401 | -0.26093 | -0.004578 | 114.3951 | 121.1655 | 121.7056 | 0.33874 | 121.7926 | 114.1983 | 121.7743 | -0.082397 | -0.26093 | 121.7926 | 114.1983 | -0.082397 | 0.33874 | 121.7743 | -121.9757 | -122.0398
457.9062 | 121.8338 | -121.5729 | 0.16479 | -0.013581 | 0.0196 | 0.013108 | -0.00071139 | -0.0079704 | 0.063376 | 0.070938 | -7.5073 | 0.22888 | -121.8658 | 0.09613 | -121.376 | -121.8201 | -0.19684 | 0 | 0.21515 | -121.8704 | -0.29297 | 0.064087 | 114.0656 | 121.669 | -121.5408 | -0.29755 | 0.050354 | 114.3585 | 121.376 | 121.5729 | 0.19684 | 121.8018 | 114.0656 | 121.788 | -0.24719 | -0.29755 | 121.8018 | 114.0656 | -0.24719 | 0.19684 | 121.788 | -122.0306 | -122.0352
459.5938 | 121.7789 | -121.5866 | 0.17395 | 0.0016785 | 0.021522 | 0.016953 | -0.0011386 | -0.0056204 | 0.063589 | 0.069015 | -7.4387 | 0.19226 | -121.8155 | 0.21057 | -121.2982 | -121.7239 | -0.36621 | 0.09613 | 0.17853 | -121.8384 | -0.22888 | 0.018311 | 114.1479 | 121.7972 | -121.4722 | -0.25177 | 0.004578 | 114.3768 | 121.2204 | 121.6827 | 0.28839 | 121.7789 | 114.1479 | 121.7651 | -0.13733 | -0.25177 | 121.7789 | 114.1479 | -0.13733 | 0.28839 | 121.7651 | -121.9894 | -122.0123
461.3438 | 121.843 | -121.5729 | 0.16479 | -0.005951 | 0.019813 | 0.010972 | -0.008829 | -0.009893 | 0.066366 | 0.069229 | -7.4661 | 0.20599 | -121.8063 | 0.17853 | -121.3074 | -121.7377 | -0.35706 | 0.07782 | 0.19684 | -121.8521 | -0.23346 | 0.041199 | 114.1068 | 121.7514 | -121.4722 | -0.27924 | 0.032043 | 114.3402 | 121.2158 | 121.6507 | 0.2655 | 121.7789 | 114.1068 | 121.7697 | -0.1648 | -0.27924 | 121.7789 | 114.1068 | -0.1648 | 0.2655 | 121.7697 | -121.9711 | -122.0169
463.0156 | 121.9116 | -121.5408 | 0.13733 | -0.013581 | 0.0196 | 0.016739 | -0.0056248 | -0.0094656 | 0.064444 | 0.070511 | -7.4936 | 0.20142 | -121.8201 | 0.18768 | -121.2891 | -121.7239 | -0.33875 | 0.09613 | 0.19684 | -121.8567 | -0.27923 | 0.064087 | 114.0472 | 121.7285 | -121.4264 | -0.31586 | 0.059509 | 114.3265 | 121.2021 | 121.637 | 0.25177 | 121.7422 | 114.0472 | 121.7377 | -0.1831 | -0.31586 | 121.7422 | 114.0472 | -0.1831 | 0.25177 | 121.7377 | -121.9574 | -121.994
464.75 | 121.7743 | -121.5729 | 0.18768 | -0.005951 | 0.017677 | 0.015671 | -0.002634 | -0.005834 | 0.062521 | 0.070297 | -7.4615 | 0.21515 | -121.8658 | 0.19684 | -121.3165 | -121.7331 | -0.3479 | 0.082397 | 0.18768 | -121.8338 | -0.29297 | 0.027466 | 114.1113 | 121.7697 | -121.5042 | -0.26093 | 0 | 114.4043 | 121.225 | 121.6553 | 0.25635 | 121.788 | 114.1113 | 121.7606 | -0.16022 | -0.26093 | 121.788 | 114.1113 | -0.16022 | 0.25635 | 121.7606 | -122.0535 | -122.0215
466.4844 | 121.8521 | -121.6187 | 0.16022 | -0.005951 | 0.017464 | 0.015671 | -0.0066928 | -0.0088248 | 0.063589 | 0.068161 | -7.4844 | 0.19684 | -121.7926 | 0.17853 | -121.3257 | -121.7468 | -0.33875 | 0.064087 | 0.1831 | -121.8613 | -0.17395 | 0.036621 | 114.1342 | 121.7972 | -121.4859 | -0.24262 | 0.022888 | 114.3082 | 121.2799 | 121.6827 | 0.29297 | 121.8155 | 114.1342 | 121.8018 | -0.12817 | -0.24262 | 121.8155 | 114.1342 | -0.12817 | 0.29297 | 121.8018 | -121.9528 | -122.0215
468.1719 | 121.875 | -121.5637 | 0.13275 | -0.005951 | 0.01725 | 0.011399 | -0.0086154 | -0.010747 | 0.065298 | 0.068374 | -7.5027 | 0.20599 | -121.8246 | 0.16022 | -121.344 | -121.7651 | -0.32501 | 0.054932 | 0.17395 | -121.8658 | -0.26093 | 0.073243 | 114.061 | 121.7239 | -121.4767 | -0.30212 | 0.041199 | 114.3219 | 121.2387 | 121.6187 | 0.21973 | 121.7697 | 114.061 | 121.7377 | -0.20142 | -0.30212 | 121.7697 | 114.061 | -0.20142 | 0.21973 | 121.7377 | -121.9574 | -121.9986
469.8906 | 121.8658 | -121.5683 | 0.15106 | -0.005951 | 0.018532 | 0.016739 | -0.00049779 | -0.0066886 | 0.061239 | 0.069229 | -7.4982 | 0.21515 | -121.8796 | 0.15564 | -121.3623 | -121.8201 | -0.14191 | 0.07782 | 0.21515 | -121.8475 | -0.31128 | 0.064087 | 114.0701 | 121.7239 | -121.5134 | -0.27924 | 0.064087 | 114.3814 | 121.4264 | 121.6461 | 0.20599 | 121.7834 | 114.0701 | 121.7834 | -0.25177 | -0.27924 | 121.7834 | 114.0701 | -0.25177 | 0.20599 | 121.7834 | -122.0306 | -121.9986
471.5781 | 121.7606 | -121.6095 | 0.16937 | -0.013581 | 0.019173 | 0.015671 | -0.0034884 | -0.0036978 | 0.062094 | 0.068374 | -7.4341 | 0.19226 | -121.8613 | 0.21515 | -121.2845 | -121.7148 | -0.37994 | 0.12817 | 0.17395 | -121.8201 | -0.25177 | 0.022888 | 114.1754 | 121.8246 | -121.4539 | -0.21057 | 0.004577 | 114.4272 | 121.2296 | 121.7377 | 0.32501 | 121.8018 | 114.1754 | 121.7834 | -0.10529 | -0.21057 | 121.8018 | 114.1754 | -0.10529 | 0.32501 | 121.7834 | -122.0306 | -121.9894
473.25 | 121.8018 | -121.6049 | 0.17395 | -0.013581 | 0.018318 | 0.013108 | -0.0045566 | -0.0079704 | 0.063162 | 0.071365 | -7.5119 | 0.20599 | -121.8658 | 0.12817 | -121.3715 | -121.8063 | -0.27008 | 0.032043 | 0.21057 | -121.875 | -0.26093 | 0.032044 | 114.093 | 121.7331 | -121.5454 | -0.27008 | 0.036621 | 114.3539 | 121.3348 | 121.637 | 0.23346 | 121.8109 | 114.093 | 121.8155 | -0.20142 | -0.27008 | 121.8109 | 114.093 | -0.20142 | 0.23346 | 121.8155 | -122.0398 | -122.049
474.9844 | 121.8521 | -121.5729 | 0.15106 | -0.013581 | 0.018105 | 0.011399 | -0.010752 | -0.0094656 | 0.062307 | 0.067734 | -7.4707 | 0.17395 | -121.8292 | 0.24719 | -121.2479 | -121.7056 | -0.33875 | 0.16937 | 0.18768 | -121.8475 | -0.25635 | 0.022888 | 114.1022 | 121.8201 | -121.3989 | -0.27466 | 0.036621 | 114.3585 | 121.2341 | 121.7422 | 0.32501 | 121.7468 | 114.1022 | 121.7606 | -0.13275 | -0.27466 | 121.7468 | 114.1022 | -0.13275 | 0.32501 | 121.7606 | -121.9803 | -121.9986
476.6562 | 121.8567 | -121.5775 | 0.16937 | -0.005951 | 0.018745 | 0.016099 | -0.0092564 | -0.0069022 | 0.061666 | 0.070511 | -7.5211 | 0.21973 | -121.9208 | 0.16022 | -121.3715 | -121.8338 | -0.15106 | 0.10529 | 0.21057 | -121.8613 | -0.34332 | 0.050354 | 114.0564 | 121.7377 | -121.5408 | -0.28381 | 0.041198 | 114.3997 | 121.4264 | 121.6827 | 0.20599 | 121.7972 | 114.0564 | 121.788 | -0.25635 | -0.28381 | 121.7972 | 114.0564 | -0.25635 | 0.20599 | 121.788 | -122.0901 | -122.0306
478.3906 | 121.7972 | -121.6003 | 0.1831 | 0.0016785 | 0.020241 | 0.017808 | -0.0090426 | -0.007543 | 0.064016 | 0.06987 | -7.4707 | 0.21515 | -121.8887 | 0.14191 | -121.3715 | -121.843 | -0.18768 | 0.064087 | 0.22888 | -121.8887 | -0.28839 | 0.032044 | 114.1296 | 121.7422 | -121.5546 | -0.28839 | 0.045777 | 114.418 | 121.4127 | 121.6644 | 0.22888 | 121.8155 | 114.1296 | 121.8292 | -0.24262 | -0.28839 | 121.8155 | 114.1296 | -0.24262 | 0.22888 | 121.8292 | -122.0718 | -122.0718
480.125 | 121.8201 | -121.6095 | 0.17853 | -0.005951 | 0.018318 | 0.014603 | -0.0098972 | -0.0051932 | 0.062521 | 0.06987 | -7.4844 | 0.23804 | -121.875 | 0.17853 | -121.3486 | -121.8109 | -0.1831 | 0.11444 | 0.21515 | -121.843 | -0.2655 | 0.059509 | 114.1251 | 121.788 | -121.5271 | -0.23346 | 0.036621 | 114.3906 | 121.4264 | 121.7239 | 0.26093 | 121.8475 | 114.1251 | 121.8246 | -0.20142 | -0.23346 | 121.8475 | 114.1251 | -0.20142 | 0.26093 | 121.8246 | -122.0535 | -122.0215
481.875 | 121.7926 | -121.6095 | 0.16937 | -0.005951 | 0.018959 | 0.011612 | -0.014383 | -0.008184 | 0.063162 | 0.067734 | -7.4661 | 0.17853 | -121.8201 | 0.22888 | -121.2845 | -121.7285 | -0.40283 | 0.11902 | 0.17395 | -121.8613 | -0.21057 | 0.009155 | 114.1434 | 121.8384 | -121.4539 | -0.25177 | 0.004577 | 114.3539 | 121.2067 | 121.7285 | 0.32501 | 121.788 | 114.1434 | 121.7834 | -0.11902 | -0.25177 | 121.788 | 114.1434 | -0.11902 | 0.32501 | 121.7834 | -121.9894 | -122.0306
483.5625 | 121.9299 | -121.5546 | 0.14648 | -0.013581 | 0.01725 | 0.013962 | -0.015879 | -0.0073294 | 0.062948 | 0.068588 | -7.5485 | 0.1831 | -121.8246 | 0.16022 | -121.3486 | -121.7697 | -0.31586 | 0.041199 | 0.19684 | -121.8704 | -0.27008 | 0.036621 | 114.006 | 121.7148 | -121.4951 | -0.31586 | 0.050354 | 114.2761 | 121.2387 | 121.5958 | 0.20599 | 121.7377 | 114.006 | 121.7514 | -0.21515 | -0.31586 | 121.7377 | 114.006 | -0.21515 | 0.20599 | 121.7514 | -121.9711 | -122.0169
485.2969 | 121.843 | -121.6003 | 0.16479 | 0.0016785 | 0.018532 | 0.01439 | -0.005411 | -0.0079704 | 0.062948 | 0.070938 | -7.5302 | 0.22888 | -121.8933 | 0.10986 | -121.4127 | -121.8704 | -0.16022 | 0.018311 | 0.21057 | -121.8704 | -0.29297 | 0.064087 | 114.0701 | 121.7102 | -121.5775 | -0.27008 | 0.045776 | 114.3631 | 121.4401 | 121.6187 | 0.18768 | 121.8292 | 114.0701 | 121.8109 | -0.27008 | -0.27008 | 121.8292 | 114.0701 | -0.27008 | 0.18768 | 121.8109 | -122.0581 | -122.0352
487.0312 | 121.8018 | -121.6187 | 0.15564 | -0.005951 | 0.014687 | 0.016099 | -0.012888 | -0.0056204 | 0.063803 | 0.070297 | -7.4753 | 0.17395 | -121.8521 | 0.2243 | -121.2936 | -121.7285 | -0.40283 | 0.12817 | 0.1831 | -121.8613 | -0.23346 | 0.01831 | 114.1434 | 121.843 | -121.4493 | -0.24262 | 0.027465 | 114.3768 | 121.2158 | 121.7468 | 0.32501 | 121.7926 | 114.1434 | 121.8018 | -0.10986 | -0.24262 | 121.7926 | 114.1434 | -0.10986 | 0.32501 | 121.8018 | -122.0078 | -122.0169
488.7031 | 121.9254 | -121.5683 | 0.14191 | -0.013581 | 0.0196 | 0.014603 | -0.013102 | -0.0094656 | 0.065512 | 0.068588 | -7.5623 | 0.19684 | -121.8384 | 0.16479 | -121.3394 | -121.7834 | -0.32959 | 0.041199 | 0.1831 | -121.8658 | -0.27008 | 0.054931 | 114.006 | 121.7331 | -121.4813 | -0.29755 | 0.041198 | 114.2761 | 121.2387 | 121.6095 | 0.22888 | 121.7651 | 114.006 | 121.7514 | -0.21515 | -0.29755 | 121.7651 | 114.006 | -0.21515 | 0.22888 | 121.7514 | -121.9803 | -122.0078
490.4375 | 121.9299 | -121.582 | 0.15564 | -0.005951 | 0.018745 | 0.012681 | -0.014597 | -0.009893 | 0.062094 | 0.067734 | -7.5531 | 0.20142 | -121.8658 | 0.18768 | -121.3303 | -121.7789 | -0.32959 | 0.086975 | 0.18768 | -121.8796 | -0.28381 | 0.045776 | 114.0289 | 121.7697 | -121.4859 | -0.29755 | 0.032043 | 114.3127 | 121.2524 | 121.669 | 0.25177 | 121.7834 | 114.0289 | 121.7697 | -0.19684 | -0.29755 | 121.7834 | 114.0289 | -0.19684 | 0.25177 | 121.7697 | -122.0215 | -122.0352
492.1094 | 121.8063 | -121.6187 | 0.20142 | -0.005951 | 0.017891 | 0.012894 | -0.0047702 | -0.0071158 | 0.062521 | 0.068374 | -7.5027 | 0.23804 | -121.8887 | 0.19684 | -121.3486 | -121.8246 | -0.17395 | 0.10529 | 0.21057 | -121.8521 | -0.27008 | 0.036621 | 114.1159 | 121.8155 | -121.55 | -0.23346 | 0.009155 | 114.386 | 121.4447 | 121.7239 | 0.27008 | 121.8567 | 114.1159 | 121.8292 | -0.20599 | -0.23346 | 121.8567 | 114.1159 | -0.20599 | 0.27008 | 121.8292 | -122.0901 | -122.0535
493.8438 | 121.8292 | -121.6187 | 0.16937 | -0.005951 | 0.017464 | 0.017808 | -0.013315 | -0.0088248 | 0.062948 | 0.069656 | -7.5027 | 0.18768 | -121.843 | 0.20599 | -121.3211 | -121.7377 | -0.39368 | 0.10986 | 0.1831 | -121.8292 | -0.22431 | 0.01831 | 114.1159 | 121.8246 | -121.4905 | -0.21057 | 0.013732 | 114.3402 | 121.225 | 121.7285 | 0.29755 | 121.8063 | 114.1159 | 121.8018 | -0.11902 | -0.21057 | 121.8063 | 114.1159 | -0.11902 | 0.29755 | 121.8018 | -122.0123 | -121.9986
495.5938 | 121.8384 | -121.6324 | 0.15106 | 0.0016785 | 0.019173 | 0.014176 | -0.005411 | -0.0069022 | 0.059744 | 0.070297 | -7.5394 | 0.21057 | -121.9208 | 0.13275 | -121.4081 | -121.8521 | -0.17395 | 0.041199 | 0.2243 | -121.8658 | -0.28839 | 0.059509 | 114.093 | 121.7651 | -121.5591 | -0.23346 | 0.073242 | 114.3814 | 121.4584 | 121.6736 | 0.2243 | 121.843 | 114.093 | 121.8567 | -0.21973 | -0.23346 | 121.843 | 114.093 | -0.21973 | 0.2243 | 121.8567 | -122.0718 | -122.0169
497.2812 | 121.9391 | -121.582 | 0.14648 | -0.013581 | 0.018532 | 0.012467 | -0.016092 | -0.0071158 | 0.064444 | 0.069656 | -7.5806 | 0.19226 | -121.8704 | 0.16022 | -121.3394 | -121.7972 | -0.31586 | 0.045776 | 0.19226 | -121.8567 | -0.28839 | 0.045777 | 114.0015 | 121.7422 | -121.4859 | -0.27466 | 0.045777 | 114.2899 | 121.2662 | 121.6278 | 0.24261 | 121.7743 | 114.0015 | 121.7743 | -0.21515 | -0.27466 | 121.7743 | 114.0015 | -0.21515 | 0.24261 | 121.7743 | -122.0169 | -122.0032
499.0156 | 121.8201 | -121.6049 | 0.17395 | -0.02121 | 0.0196 | 0.015885 | -0.0096836 | -0.007543 | 0.063803 | 0.06987 | -7.489 | 0.17853 | -121.8384 | 0.23346 | -121.2936 | -121.7331 | -0.40741 | 0.13275 | 0.17395 | -121.875 | -0.23346 | 0.004578 | 114.1159 | 121.8384 | -121.4676 | -0.27008 | 0 | 114.3494 | 121.1975 | 121.7377 | 0.31128 | 121.7834 | 114.1159 | 121.7789 | -0.12817 | -0.27008 | 121.7834 | 114.1159 | -0.12817 | 0.31128 | 121.7789 | -122.0123 | -122.049
500.7656 | 121.9437 | -121.582 | 0.13733 | 0.0016785 | 0.017677 | 0.0090491 | -0.013102 | -0.009252 | 0.065084 | 0.068802 | -7.576 | 0.20142 | -121.843 | 0.20142 | -121.3211 | -121.756 | -0.32501 | 0.10986 | 0.19226 | -121.8658 | -0.26093 | 0.064087 | 114.006 | 121.7834 | -121.4584 | -0.28381 | 0.054932 | 114.267 | 121.257 | 121.6919 | 0.26093 | 121.7834 | 114.006 | 121.7743 | -0.17395 | -0.28381 | 121.7834 | 114.006 | -0.17395 | 0.26093 | 121.7743 | -121.9803 | -122.0032
502.4531 | 121.9391 | -121.5683 | 0.14191 | -0.005951 | 0.017464 | 0.01204 | -0.0081882 | -0.0094656 | 0.062094 | 0.070724 | -7.6035 | 0.21057 | -121.9116 | 0.14191 | -121.3989 | -121.8658 | -0.12817 | 0.073242 | 0.24719 | -121.8796 | -0.34332 | 0.068664 | 113.9648 | 121.7102 | -121.5408 | -0.31128 | 0.10528 | 114.3082 | 121.4401 | 121.6415 | 0.16937 | 121.7789 | 113.9648 | 121.8155 | -0.29755 | -0.31128 | 121.7789 | 113.9648 | -0.29755 | 0.16937 | 121.8155 | -122.0535 | -122.0215
504.1875 | 121.8658 | -121.5912 | 0.16022 | -0.013581 | 0.018959 | 0.016739 | -0.013315 | -0.009893 | 0.064444 | 0.070083 | -7.5531 | 0.17853 | -121.8567 | 0.18768 | -121.3303 | -121.7789 | -0.36163 | 0.082397 | 0.16937 | -121.8704 | -0.2655 | 0.018311 | 114.0381 | 121.7789 | -121.4905 | -0.27923 | 0.009156 | 114.3036 | 121.2296 | 121.6736 | 0.26093 | 121.7697 | 114.0381 | 121.7606 | -0.18768 | -0.27923 | 121.7697 | 114.0381 | -0.18768 | 0.26093 | 121.7606 | -122.0169 | -122.0306
505.9375 | 121.8658 | -121.582 | 0.15564 | -0.013581 | 0.018959 | 0.015458 | -0.0056248 | -0.0094656 | 0.06423 | 0.069015 | -7.608 | 0.21973 | -121.9025 | 0.11902 | -121.4264 | -121.8658 | -0.23346 | -0.004578 | 0.21057 | -121.9116 | -0.32044 | 0.064087 | 113.974 | 121.701 | -121.582 | -0.32959 | 0.054931 | 114.2944 | 121.3486 | 121.5775 | 0.15564 | 121.8018 | 113.974 | 121.7926 | -0.28381 | -0.32959 | 121.8018 | 113.974 | -0.28381 | 0.15564 | 121.7926 | -122.0581 | -122.0673
507.6094 | 121.9666 | -121.5729 | 0.14191 | -0.013581 | 0.0196 | 0.012467 | -0.011179 | -0.0086112 | 0.062307 | 0.06752 | -7.6126 | 0.25177 | -121.8704 | 0.10986 | -121.4035 | -121.8613 | -0.12817 | 0.068665 | 0.2243 | -121.9254 | -0.29755 | 0.10986 | 113.9603 | 121.6827 | -121.5454 | -0.35248 | 0.082397 | 114.2578 | 121.4447 | 121.6415 | 0.16937 | 121.8246 | 113.9603 | 121.7972 | -0.28839 | -0.35248 | 121.8246 | 113.9603 | -0.28839 | 0.16937 | 121.7972 | -122.0123 | -122.0673
509.3438 | 121.9299 | -121.5958 | 0.12817 | 0.0016785 | 0.018105 | 0.013321 | -0.013956 | -0.011388 | 0.065084 | 0.069229 | -7.5806 | 0.20599 | -121.8613 | 0.21057 | -121.312 | -121.7514 | -0.33875 | 0.11902 | 0.17395 | -121.8704 | -0.2655 | 0.07782 | 114.0152 | 121.8063 | -121.4401 | -0.27466 | 0.045776 | 114.2807 | 121.257 | 121.7148 | 0.28381 | 121.8018 | 114.0152 | 121.7697 | -0.15564 | -0.27466 | 121.8018 | 114.0152 | -0.15564 | 0.28381 | 121.7697 | -121.9894 | -121.9986
511.0781 | 121.9162 | -121.6095 | 0.16479 | -0.005951 | 0.018532 | 0.013321 | -0.01417 | -0.011388 | 0.064444 | 0.067093 | -7.5211 | 0.17853 | -121.8613 | 0.24261 | -121.2845 | -121.7194 | -0.36163 | 0.16937 | 0.17853 | -121.8704 | -0.25177 | 0.013733 | 114.0884 | 121.8521 | -121.4493 | -0.26093 | 0.013733 | 114.3402 | 121.2479 | 121.7789 | 0.32501 | 121.788 | 114.0884 | 121.788 | -0.10986 | -0.26093 | 121.788 | 114.0884 | -0.10986 | 0.32501 | 121.788 | -122.0261 | -122.0352
512.8281 | 121.7972 | -121.6141 | 0.16022 | 0.009308 | 0.020027 | 0.015244 | -0.008829 | -0.0073294 | 0.062094 | 0.068588 | -7.5073 | 0.19684 | -121.8796 | 0.23804 | -121.3028 | -121.7422 | -0.41199 | 0.1236 | 0.19226 | -121.8567 | -0.2655 | 0.036621 | 114.1068 | 121.8521 | -121.463 | -0.24261 | 0.032044 | 114.3723 | 121.2021 | 121.7377 | 0.31128 | 121.8109 | 114.1068 | 121.8063 | -0.12817 | -0.24261 | 121.8109 | 114.1068 | -0.12817 | 0.31128 | 121.8063 | -122.0398 | -122.0169
514.5156 | 121.875 | -121.6049 | 0.15106 | 0.0016785 | 0.020241 | 0.015671 | -0.007761 | -0.0077566 | 0.064657 | 0.069443 | -7.6309 | 0.23804 | -121.9162 | 0.1236 | -121.4264 | -121.875 | -0.21057 | 0 | 0.22888 | -121.8887 | -0.31128 | 0.086975 | 113.974 | 121.7285 | -121.5775 | -0.28381 | 0.07782 | 114.2853 | 121.3943 | 121.6049 | 0.17853 | 121.843 | 113.974 | 121.8338 | -0.27008 | -0.28381 | 121.843 | 113.974 | -0.27008 | 0.17853 | 121.8338 | -122.0673 | -122.0398
516.25 | 121.8658 | -121.6141 | 0.16022 | -0.005951 | 0.018105 | 0.011826 | -0.00947 | -0.0071158 | 0.061666 | 0.068588 | -7.6492 | 0.21973 | -121.9345 | 0.10986 | -121.4584 | -121.8842 | -0.16937 | 0.009155 | 0.2243 | -121.8933 | -0.32043 | 0.05951 | 113.9648 | 121.7239 | -121.6187 | -0.27924 | 0.064087 | 114.2853 | 121.4447 | 121.6232 | 0.15564 | 121.8338 | 113.9648 | 121.8384 | -0.27008 | -0.27924 | 121.8338 | 113.9648 | -0.27008 | 0.15564 | 121.8384 | -122.0947 | -122.0535
518 | 121.8933 | -121.6095 | 0.14191 | -0.005951 | 0.017464 | 0.013535 | -0.017374 | -0.009893 | 0.065512 | 0.069443 | -7.5577 | 0.19226 | -121.8338 | 0.24719 | -121.2662 | -121.7285 | -0.33417 | 0.16937 | 0.17853 | -121.8933 | -0.2243 | 0.050354 | 114.0518 | 121.8567 | -121.4081 | -0.28381 | 0.036621 | 114.2761 | 121.2753 | 121.7789 | 0.34332 | 121.8018 | 114.0518 | 121.788 | -0.11902 | -0.28381 | 121.8018 | 114.0518 | -0.11902 | 0.34332 | 121.788 | -121.9757 | -122.0352
519.6719 | 121.907 | -121.6003 | 0.14648 | -0.02121 | 0.0196 | 0.012894 | -0.015238 | -0.01032 | 0.064871 | 0.070297 | -7.5943 | 0.17853 | -121.8796 | 0.20599 | -121.312 | -121.756 | -0.35248 | 0.13275 | 0.19684 | -121.8796 | -0.27924 | 0.032044 | 114.006 | 121.8063 | -121.4584 | -0.27924 | 0.050354 | 114.2853 | 121.2479 | 121.7331 | 0.28839 | 121.7789 | 114.006 | 121.7972 | -0.15564 | -0.27924 | 121.7789 | 114.006 | -0.15564 | 0.28839 | 121.7972 | -122.0261 | -122.0261
521.4062 | 121.9482 | -121.5591 | 0.12817 | -0.005951 | 0.017464 | 0.01503 | -0.01182 | -0.011175 | 0.064657 | 0.069656 | -7.6492 | 0.21057 | -121.8384 | 0.17853 | -121.3669 | -121.7834 | -0.32959 | 0.050354 | 0.17853 | -121.8933 | -0.27924 | 0.082397 | 113.9099 | 121.7377 | -121.4951 | -0.33417 | 0.050354 | 114.1891 | 121.2296 | 121.6095 | 0.19226 | 121.7697 | 113.9099 | 121.7377 | -0.2243 | -0.33417 | 121.7697 | 113.9099 | -0.2243 | 0.19226 | 121.7377 | -121.9666 | -122.0215
523.1562 | 121.9574 | -121.5683 | 0.13733 | 0.0016785 | 0.019173 | 0.011612 | -0.00947 | -0.0094656 | 0.062948 | 0.066879 | -7.6675 | 0.2243 | -121.9254 | 0.14191 | -121.3989 | -121.8567 | -0.12817 | 0.059509 | 0.23804 | -121.8613 | -0.35706 | 0.086975 | 113.9008 | 121.7102 | -121.5363 | -0.29297 | 0.10071 | 114.2578 | 121.4401 | 121.6278 | 0.16937 | 121.7926 | 113.9008 | 121.8063 | -0.28839 | -0.29297 | 121.7926 | 113.9008 | -0.28839 | 0.16937 | 121.8063 | -122.0627 | -121.9986
524.8906 | 121.8933 | -121.6049 | 0.15564 | 0.0016785 | 0.019173 | 0.012467 | -0.016519 | -0.010534 | 0.065084 | 0.070083 | -7.5577 | 0.20142 | -121.8201 | 0.27008 | -121.2982 | -121.7194 | -0.37994 | 0.17853 | 0.17853 | -121.8567 | -0.21515 | 0.045776 | 114.0472 | 121.875 | -121.4539 | -0.25177 | 0.022888 | 114.2624 | 121.225 | 121.7834 | 0.3067 | 121.8063 | 114.0472 | 121.7834 | -0.11444 | -0.25177 | 121.8063 | 114.0472 | -0.11444 | 0.3067 | 121.7834 | -121.9757 | -122.0123
526.5625 | 121.9345 | -121.5454 | 0.12817 | -0.013581 | 0.01725 | 0.011399 | -0.013956 | -0.010107 | 0.062735 | 0.069443 | -7.6172 | 0.19226 | -121.8567 | 0.21973 | -121.3165 | -121.7606 | -0.32959 | 0.11902 | 0.17853 | -121.8796 | -0.31128 | 0.064087 | 113.9282 | 121.7651 | -121.4447 | -0.33417 | 0.050354 | 114.2395 | 121.2158 | 121.6644 | 0.22888 | 121.7377 | 113.9282 | 121.7239 | -0.21515 | -0.33417 | 121.7377 | 113.9282 | -0.21515 | 0.22888 | 121.7239 | -121.9849 | -122.0078
528.3125 | 121.8201 | -121.6324 | 0.1831 | 0.009308 | 0.017891 | 0.011399 | -0.0045566 | -0.006475 | 0.059103 | 0.068588 | -7.5668 | 0.2243 | -121.907 | 0.19684 | -121.376 | -121.8338 | -0.20599 | 0.10986 | 0.22888 | -121.8658 | -0.27466 | 0.041199 | 114.0656 | 121.8292 | -121.5591 | -0.23346 | 0.045777 | 114.3402 | 121.4264 | 121.7422 | 0.25635 | 121.8567 | 114.0656 | 121.8613 | -0.20142 | -0.23346 | 121.8567 | 114.0656 | -0.20142 | 0.25635 | 121.8613 | -122.0901 | -122.0489
529.9844 | 121.8475 | -121.6415 | 0.16937 | -0.005951 | 0.017891 | 0.015244 | -0.0084018 | -0.0049796 | 0.060812 | 0.069443 | -7.6126 | 0.21515 | -121.907 | 0.13733 | -121.4127 | -121.8704 | -0.17853 | 0.036621 | 0.24261 | -121.8201 | -0.2655 | 0.045776 | 114.0289 | 121.7789 | -121.582 | -0.17853 | 0.073242 | 114.2944 | 121.463 | 121.6782 | 0.22888 | 121.8567 | 114.0289 | 121.8842 | -0.22888 | -0.17853 | 121.8567 | 114.0289 | -0.22888 | 0.22888 | 121.8842 | -122.0764 | -121.9894
531.7188 | 121.8201 | -121.6415 | 0.1831 | -0.005951 | 0.018959 | 0.01439 | -0.0081882 | -0.006475 | 0.060598 | 0.070083 | -7.5806 | 0.21973 | -121.8933 | 0.17853 | -121.376 | -121.843 | -0.19226 | 0.091553 | 0.21515 | -121.8613 | -0.25177 | 0.036622 | 114.061 | 121.8201 | -121.5591 | -0.21973 | 0.032044 | 114.3127 | 121.4493 | 121.7331 | 0.2655 | 121.8613 | 114.061 | 121.8567 | -0.20142 | -0.21973 | 121.8613 | 114.061 | -0.20142 | 0.2655 | 121.8567 | -122.0764 | -122.0444
533.4531 | 121.8201 | -121.6324 | 0.17853 | 0.0016785 | 0.01725 | 0.014176 | -0.010111 | -0.008184 | 0.061666 | 0.068802 | -7.5714 | 0.21973 | -121.9025 | 0.19226 | -121.3486 | -121.8246 | -0.19684 | 0.11902 | 0.2243 | -121.875 | -0.27008 | 0.041199 | 114.061 | 121.8246 | -121.5271 | -0.24262 | 0.045776 | 114.3311 | 121.4355 | 121.7514 | 0.28381 | 121.8521 | 114.061 | 121.8567 | -0.19226 | -0.24262 | 121.8521 | 114.061 | -0.19226 | 0.28381 | 121.8567 | -122.081 | -122.0535
535.125 | 121.8155 | -121.6232 | 0.1831 | 0.0016785 | 0.020027 | 0.018021 | -0.0069064 | -0.0069022 | 0.061239 | 0.069015 | -7.608 | 0.22888 | -121.8933 | 0.1236 | -121.3898 | -121.8521 | -0.16022 | 0.041199 | 0.24261 | -121.8475 | -0.27008 | 0.045777 | 114.0152 | 121.7468 | -121.5729 | -0.2243 | 0.05951 | 114.2853 | 121.463 | 121.6644 | 0.23346 | 121.8521 | 114.0152 | 121.8658 | -0.22888 | -0.2243 | 121.8521 | 114.0152 | -0.22888 | 0.23346 | 121.8658 | -122.0764 | -122.0306
536.875 | 121.8246 | -121.6187 | 0.18768 | -0.013581 | 0.018105 | 0.012681 | -0.010752 | -0.0060478 | 0.063589 | 0.068588 | -7.6263 | 0.2243 | -121.8933 | 0.13275 | -121.3989 | -121.8338 | -0.24261 | 0.018311 | 0.21973 | -121.8521 | -0.27466 | 0.036621 | 113.9923 | 121.7514 | -121.5866 | -0.23346 | 0.032044 | 114.267 | 121.376 | 121.637 | 0.21973 | 121.843 | 113.9923 | 121.8384 | -0.21515 | -0.23346 | 121.843 | 113.9923 | -0.21515 | 0.21973 | 121.8384 | -122.081 | -122.0398
538.5469 | 121.8201 | -121.6278 | 0.19684 | -0.005951 | 0.018745 | 0.011612 | -0.0096836 | -0.0073294 | 0.063162 | 0.069443 | -7.5806 | 0.21057 | -121.8933 | 0.18768 | -121.3531 | -121.8155 | -0.20142 | 0.11902 | 0.21973 | -121.8567 | -0.2655 | 0.013733 | 114.0472 | 121.8155 | -121.55 | -0.22888 | 0.022889 | 114.3127 | 121.4264 | 121.7468 | 0.27466 | 121.8384 | 114.0472 | 121.8475 | -0.18768 | -0.22888 | 121.8384 | 114.0472 | -0.18768 | 0.27466 | 121.8475 | -122.0901 | -122.0535
540.2812 | 121.9528 | -121.6003 | 0.13275 | -0.005951 | 0.0196 | 0.015458 | -0.015024 | -0.0086112 | 0.063162 | 0.070511 | -7.6584 | 0.21973 | -121.8979 | 0.13733 | -121.3898 | -121.8475 | -0.15106 | 0.059509 | 0.23804 | -121.9025 | -0.29755 | 0.086976 | 113.942 | 121.7377 | -121.5225 | -0.30212 | 0.10529 | 114.2395 | 121.4493 | 121.6599 | 0.21057 | 121.8201 | 113.942 | 121.8384 | -0.24719 | -0.30212 | 121.8201 | 113.942 | -0.24719 | 0.21057 | 121.8384 | -122.0306 | -122.0352
542.0312 | 121.9391 | -121.5958 | 0.15106 | -0.02121 | 0.018105 | 0.013749 | -0.015024 | -0.0086112 | 0.062094 | 0.06987 | -7.6172 | 0.20599 | -121.875 | 0.16937 | -121.3486 | -121.8246 | -0.18768 | 0.09613 | 0.22888 | -121.8979 | -0.27924 | 0.054932 | 113.9786 | 121.7651 | -121.4996 | -0.30212 | 0.07782 | 114.2578 | 121.4081 | 121.6919 | 0.24719 | 121.8018 | 113.9786 | 121.8246 | -0.22888 | -0.30212 | 121.8018 | 113.9786 | -0.22888 | 0.24719 | 121.8246 | -122.0261 | -122.0489
543.7656 | 121.8475 | -121.637 | 0.19684 | -0.005951 | 0.022163 | 0.013962 | -0.006052 | -0.0049796 | 0.060171 | 0.070511 | -7.6309 | 0.2243 | -121.9162 | 0.14191 | -121.4081 | -121.8704 | -0.17395 | 0.050354 | 0.22888 | -121.8704 | -0.27924 | 0.027466 | 114.006 | 121.7789 | -121.6049 | -0.23346 | 0.032044 | 114.2853 | 121.463 | 121.6873 | 0.22888 | 121.8613 | 114.006 | 121.8658 | -0.23346 | -0.23346 | 121.8613 | 114.006 | -0.23346 | 0.22888 | 121.8658 | -122.113 | -122.0673
545.4375 | 121.8384 | -121.637 | 0.17853 | 0.0016785 | 0.018745 | 0.01439 | -0.012033 | -0.0056204 | 0.062521 | 0.070297 | -7.6584 | 0.22888 | -121.8796 | 0.16022 | -121.3852 | -121.8155 | -0.30212 | 0.059509 | 0.20142 | -121.8704 | -0.24262 | 0.050354 | 113.9786 | 121.7972 | -121.5637 | -0.23346 | 0.022888 | 114.2212 | 121.3348 | 121.6965 | 0.25177 | 121.8658 | 113.9786 | 121.8384 | -0.17853 | -0.23346 | 121.8658 | 113.9786 | -0.17853 | 0.25177 | 121.8384 | -122.0581 | -122.049
547.1719 | 121.8201 | -121.637 | 0.17395 | -0.013581 | 0.017677 | 0.013108 | -0.01417 | -0.007543 | 0.062948 | 0.070297 | -7.5623 | 0.19226 | -121.875 | 0.23346 | -121.3211 | -121.7377 | -0.41199 | 0.10986 | 0.20599 | -121.8521 | -0.23804 | 0.018311 | 114.0747 | 121.8704 | -121.4951 | -0.21515 | 0.032044 | 114.3127 | 121.225 | 121.7468 | 0.31586 | 121.8292 | 114.0747 | 121.843 | -0.10071 | -0.21515 | 121.8292 | 114.0747 | -0.10071 | 0.31586 | 121.843 | -122.049 | -122.0261
548.9219 | 121.8338 | -121.6553 | 0.17853 | 0.0016785 | 0.018318 | 0.012894 | -0.0086154 | -0.0079704 | 0.064871 | 0.069443 | -7.608 | 0.21515 | -121.9345 | 0.18768 | -121.3715 | -121.8384 | -0.19684 | 0.13275 | 0.21515 | -121.8842 | -0.27924 | 0.036621 | 114.0472 | 121.843 | -121.55 | -0.22888 | 0.036621 | 114.3265 | 121.4584 | 121.788 | 0.28381 | 121.8704 | 114.0472 | 121.8704 | -0.18311 | -0.22888 | 121.8704 | 114.0472 | -0.18311 | 0.28381 | 121.8704 | -122.113 | -122.0627
550.5938 | 121.8338 | -121.6461 | 0.19226 | -0.005951 | 0.019386 | 0.013749 | -0.013742 | -0.0069022 | 0.062307 | 0.068802 | -7.5989 | 0.19684 | -121.8979 | 0.21973 | -121.3257 | -121.756 | -0.3891 | 0.10529 | 0.19684 | -121.8796 | -0.25177 | 0.004577 | 114.0472 | 121.8658 | -121.5179 | -0.23346 | 0.004577 | 114.299 | 121.257 | 121.7514 | 0.32043 | 121.843 | 114.0472 | 121.843 | -0.10986 | -0.23346 | 121.843 | 114.0472 | -0.10986 | 0.32043 | 121.843 | -122.0901 | -122.0718
552.3281 | 121.9757 | -121.6232 | 0.13275 | -0.013581 | 0.018532 | 0.017167 | -0.016519 | -0.0086112 | 0.065084 | 0.072006 | -7.6767 | 0.21057 | -121.8567 | 0.16479 | -121.3806 | -121.8338 | -0.31128 | 0.054932 | 0.19684 | -121.9345 | -0.23346 | 0.07782 | 113.9465 | 121.788 | -121.5134 | -0.31128 | 0.064087 | 114.18 | 121.312 | 121.6782 | 0.24262 | 121.8338 | 113.9465 | 121.8201 | -0.21057 | -0.31128 | 121.8338 | 113.9465 | -0.21057 | 0.24262 | 121.8201 | -121.9894 | -122.0673
554.0625 | 121.8384 | -121.6324 | 0.16022 | 0.0016785 | 0.019173 | 0.014176 | -0.0090426 | -0.0086112 | 0.063162 | 0.070083 | -7.6675 | 0.21515 | -121.9025 | 0.13733 | -121.4264 | -121.8521 | -0.27924 | 0.036621 | 0.21973 | -121.9208 | -0.27008 | 0.054932 | 113.9648 | 121.7697 | -121.5866 | -0.28839 | 0.05951 | 114.2349 | 121.3531 | 121.669 | 0.20599 | 121.8475 | 113.9648 | 121.8521 | -0.21973 | -0.28839 | 121.8475 | 113.9648 | -0.21973 | 0.20599 | 121.8521 | -122.0627 | -122.081
555.8125 | 121.9437 | -121.6232 | 0.16479 | -0.005951 | 0.020454 | 0.014817 | -0.014597 | -0.0094656 | 0.065298 | 0.06987 | -7.6767 | 0.19226 | -121.8842 | 0.1831 | -121.3898 | -121.7972 | -0.34332 | 0.068665 | 0.19684 | -121.9162 | -0.26093 | 0.027466 | 113.9465 | 121.8063 | -121.5546 | -0.29297 | 0.032043 | 114.2075 | 121.2799 | 121.6919 | 0.23346 | 121.8155 | 113.9465 | 121.8201 | -0.17395 | -0.29297 | 121.8155 | 113.9465 | -0.17395 | 0.23346 | 121.8201 | -122.049 | -122.081
557.4844 | 121.8567 | -121.6232 | 0.19226 | 0.0016785 | 0.020454 | 0.01738 | -0.0096836 | -0.0079704 | 0.066793 | 0.068374 | -7.5989 | 0.23346 | -121.8796 | 0.21973 | -121.3577 | -121.7789 | -0.37537 | 0.11444 | 0.20599 | -121.8979 | -0.25635 | 0.041198 | 114.0244 | 121.843 | -121.55 | -0.27466 | 0.013733 | 114.2807 | 121.2479 | 121.7377 | 0.2655 | 121.8567 | 114.0244 | 121.8292 | -0.15564 | -0.27466 | 121.8567 | 114.0244 | -0.15564 | 0.2655 | 121.8292 | -122.0718 | -122.0901
559.2188 | 121.8796 | -121.6599 | 0.1831 | -0.013581 | 0.018318 | 0.01439 | -0.0073336 | -0.0079704 | 0.062735 | 0.070511 | -7.6675 | 0.22888 | -121.9437 | 0.15564 | -121.431 | -121.8887 | -0.17395 | 0.032043 | 0.2243 | -121.9208 | -0.28381 | 0.045777 | 113.9923 | 121.8155 | -121.6141 | -0.26093 | 0.041199 | 114.2761 | 121.4859 | 121.6919 | 0.22888 | 121.8887 | 113.9923 | 121.8842 | -0.22888 | -0.26093 | 121.8887 | 113.9923 | -0.22888 | 0.22888 | 121.8842 | -122.1268 | -122.1039
560.9688 | 121.8979 | -121.6415 | 0.17395 | -0.005951 | 0.023231 | 0.015885 | -0.008829 | -0.0073294 | 0.062094 | 0.070297 | -7.695 | 0.24719 | -121.9437 | 0.11444 | -121.4722 | -121.9116 | -0.19684 | 0 | 0.24719 | -121.9437 | -0.30212 | 0.073242 | 113.9465 | 121.756 | -121.6461 | -0.30212 | 0.073242 | 114.2487 | 121.4447 | 121.6415 | 0.16937 | 121.8887 | 113.9465 | 121.8887 | -0.27008 | -0.30212 | 121.8887 | 113.9465 | -0.27008 | 0.16937 | 121.8887 | -122.1176 | -122.1176
562.6406 | 121.994 | -121.6141 | 0.15106 | -0.013581 | 0.021309 | 0.013962 | -0.012033 | -0.009252 | 0.063589 | 0.070083 | -7.7225 | 0.23346 | -121.9208 | 0.1236 | -121.4401 | -121.9025 | -0.11444 | 0.073242 | 0.25177 | -121.962 | -0.3067 | 0.082397 | 113.8916 | 121.7377 | -121.5912 | -0.3479 | 0.10071 | 114.1983 | 121.4996 | 121.6873 | 0.17395 | 121.8475 | 113.8916 | 121.8658 | -0.28839 | -0.3479 | 121.8475 | 113.8916 | -0.28839 | 0.17395 | 121.8658 | -122.0718 | -122.113
564.3906 | 121.9345 | -121.6278 | 0.15106 | -0.013581 | 0.018745 | 0.014603 | -0.015238 | -0.009893 | 0.062948 | 0.070083 | -7.6401 | 0.19684 | -121.8796 | 0.24719 | -121.3165 | -121.7651 | -0.37079 | 0.1831 | 0.17853 | -121.9299 | -0.25177 | 0.045776 | 113.9877 | 121.875 | -121.4676 | -0.30212 | 0.027466 | 114.2395 | 121.257 | 121.8109 | 0.31128 | 121.8246 | 113.9877 | 121.8063 | -0.13733 | -0.30212 | 121.8246 | 113.9877 | -0.13733 | 0.31128 | 121.8063 | -122.0306 | -122.081
566.0625 | 121.9391 | -121.6187 | 0.14648 | -0.005951 | 0.016396 | 0.010117 | -0.016519 | -0.009893 | 0.063162 | 0.066452 | -7.6447 | 0.21057 | -121.8887 | 0.25177 | -121.3028 | -121.7331 | -0.37079 | 0.17853 | 0.19226 | -121.8979 | -0.27008 | 0.064087 | 113.974 | 121.8704 | -121.4493 | -0.27924 | 0.045777 | 114.2441 | 121.2479 | 121.7972 | 0.31586 | 121.8292 | 113.974 | 121.8109 | -0.11444 | -0.27924 | 121.8292 | 113.974 | -0.11444 | 0.31586 | 121.8109 | -122.0352 | -122.0444
567.8125 | 121.9528 | -121.5958 | 0.15564 | -0.005951 | 0.017464 | 0.0069129 | -0.012461 | -0.0054068 | 0.062094 | 0.069656 | -7.6996 | 0.17853 | -121.9116 | 0.1831 | -121.3806 | -121.8246 | -0.33417 | 0.059509 | 0.20599 | -121.8979 | -0.31586 | 0.022888 | 113.8962 | 121.7789 | -121.5363 | -0.30212 | 0.050354 | 114.212 | 121.2616 | 121.6553 | 0.21515 | 121.7743 | 113.8962 | 121.8018 | -0.22888 | -0.30212 | 121.7743 | 113.8962 | -0.22888 | 0.21515 | 121.8018 | -122.0673 | -122.0535
569.4844 | 121.8475 | -121.6873 | 0.16937 | -0.005951 | 0.022377 | 0.0088355 | -0.0081882 | -0.0083976 | 0.062735 | 0.068588 | -7.6218 | 0.20599 | -121.9437 | 0.23346 | -121.3486 | -121.7651 | -0.41199 | 0.1236 | 0.17853 | -121.9025 | -0.25635 | 0.036621 | 114.0656 | 121.9208 | -121.5179 | -0.21515 | 0.009155 | 114.3219 | 121.2753 | 121.8109 | 0.33874 | 121.8933 | 114.0656 | 121.8658 | -0.07782 | -0.21515 | 121.8933 | 114.0656 | -0.07782 | 0.33874 | 121.8658 | -122.113 | -122.0718
571.2188 | 121.8979 | -121.6507 | 0.16937 | -0.005951 | 0.018318 | 0.013962 | -0.012461 | -0.0090384 | 0.062307 | 0.071579 | -7.7271 | 0.23346 | -121.9666 | 0.11444 | -121.463 | -121.8887 | -0.21973 | 0.004578 | 0.23346 | -121.907 | -0.31586 | 0.064086 | 113.9236 | 121.7651 | -121.6324 | -0.25635 | 0.064086 | 114.2395 | 121.431 | 121.6553 | 0.18768 | 121.8842 | 113.9236 | 121.8842 | -0.23804 | -0.25635 | 121.8842 | 113.9236 | -0.23804 | 0.18768 | 121.8842 | -122.1359 | -122.0764
572.9844 | 121.9666 | -121.6232 | 0.14191 | -0.005951 | 0.019386 | 0.011826 | -0.015879 | -0.0094656 | 0.064444 | 0.068802 | -7.7179 | 0.19684 | -121.875 | 0.1831 | -121.3943 | -121.8292 | -0.33875 | 0.054932 | 0.20599 | -121.907 | -0.25177 | 0.054931 | 113.9053 | 121.8063 | -121.5363 | -0.28381 | 0.064087 | 114.1571 | 121.2845 | 121.6782 | 0.22888 | 121.8201 | 113.9053 | 121.8292 | -0.20599 | -0.28381 | 121.8201 | 113.9053 | -0.20599 | 0.22888 | 121.8292 | -122.0169 | -122.049
574.6562 | 121.9849 | -121.6141 | 0.15106 | -0.013581 | 0.016182 | 0.01503 | -0.013315 | -0.010747 | 0.062521 | 0.068802 | -7.7271 | 0.19684 | -121.8933 | 0.17395 | -121.3943 | -121.8246 | -0.34332 | 0.068665 | 0.20599 | -121.9254 | -0.27924 | 0.045776 | 113.887 | 121.788 | -121.5454 | -0.31128 | 0.054932 | 114.1663 | 121.2708 | 121.6827 | 0.21973 | 121.8109 | 113.887 | 121.8201 | -0.21057 | -0.31128 | 121.8109 | 113.887 | -0.21057 | 0.21973 | 121.8201 | -122.0444 | -122.0764
576.3906 | 121.9208 | -121.6507 | 0.16937 | -0.013581 | 0.018532 | 0.01204 | -0.0075474 | -0.0094656 | 0.062307 | 0.06987 | -7.7591 | 0.2243 | -122.0032 | 0.1236 | -121.4996 | -121.9482 | -0.18768 | 0.022888 | 0.22888 | -121.9437 | -0.35248 | 0.054931 | 113.8916 | 121.7743 | -121.669 | -0.29297 | 0.059509 | 114.2441 | 121.463 | 121.6736 | 0.15106 | 121.875 | 113.8916 | 121.8796 | -0.29755 | -0.29297 | 121.875 | 113.8916 | -0.29755 | 0.15106 | 121.8796 | -122.1725 | -122.113
578.125 | 122.0032 | -121.6141 | 0.16479 | 0.0016785 | 0.018959 | 0.0099037 | -0.01417 | -0.0086112 | 0.062521 | 0.069229 | -7.7362 | 0.20599 | -121.9116 | 0.1831 | -121.376 | -121.8018 | -0.32501 | 0.082397 | 0.19226 | -121.9254 | -0.29755 | 0.041199 | 113.8779 | 121.7972 | -121.5408 | -0.31128 | 0.027466 | 114.1754 | 121.2891 | 121.6965 | 0.23804 | 121.8201 | 113.8779 | 121.8063 | -0.18768 | -0.31128 | 121.8201 | 113.8779 | -0.18768 | 0.23804 | 121.8063 | -122.0764 | -122.0901
579.8594 | 121.994 | -121.6324 | 0.14191 | 0.0016785 | 0.01725 | 0.013749 | -0.0096836 | -0.009252 | 0.062307 | 0.068374 | -7.7042 | 0.20599 | -121.9391 | 0.17395 | -121.4172 | -121.8704 | -0.18768 | 0.10071 | 0.23346 | -121.9391 | -0.3067 | 0.064087 | 113.9282 | 121.8063 | -121.5591 | -0.3067 | 0.091552 | 114.2349 | 121.4447 | 121.7331 | 0.21515 | 121.8384 | 113.9282 | 121.8658 | -0.23804 | -0.3067 | 121.8384 | 113.9282 | -0.23804 | 0.21515 | 121.8658 | -122.081 | -122.081
581.5938 | 121.9574 | -121.6187 | 0.16022 | -0.005951 | 0.017464 | 0.0077673 | -0.01182 | -0.008184 | 0.062521 | 0.069656 | -7.7454 | 0.19684 | -121.907 | 0.18768 | -121.3989 | -121.8246 | -0.34332 | 0.073242 | 0.21973 | -121.907 | -0.28839 | 0.036621 | 113.8733 | 121.8063 | -121.5591 | -0.28839 | 0.05951 | 114.1617 | 121.2753 | 121.6919 | 0.21973 | 121.8155 | 113.8733 | 121.8384 | -0.20599 | -0.28839 | 121.8155 | 113.8733 | -0.20599 | 0.21973 | 121.8384 | -122.0673 | -122.0673
583.2812 | 121.9849 | -121.6049 | 0.14191 | -0.005951 | 0.018105 | 0.010117 | -0.012461 | -0.0079704 | 0.062735 | 0.068161 | -7.7591 | 0.20142 | -121.9208 | 0.17853 | -121.4035 | -121.843 | -0.32959 | 0.045776 | 0.20142 | -121.9025 | -0.31586 | 0.059509 | 113.8458 | 121.7834 | -121.5454 | -0.29755 | 0.059509 | 114.1617 | 121.2753 | 121.6507 | 0.20142 | 121.8063 | 113.8458 | 121.8063 | -0.23804 | -0.29755 | 121.8063 | 113.8458 | -0.23804 | 0.20142 | 121.8063 | -122.0627 | -122.0444
585.0312 | 121.9208 | -121.6599 | 0.17395 | -0.013581 | 0.020241 | 0.014603 | -0.0062656 | -0.0062614 | 0.061239 | 0.068161 | -7.7499 | 0.2243 | -121.9666 | 0.13275 | -121.4813 | -121.9162 | -0.21057 | -0.009155 | 0.23804 | -121.9299 | -0.3067 | 0.050354 | 113.9099 | 121.7926 | -121.6553 | -0.27008 | 0.064087 | 114.2166 | 121.4493 | 121.6507 | 0.17853 | 121.8842 | 113.9099 | 121.8979 | -0.25635 | -0.27008 | 121.8842 | 113.9099 | -0.25635 | 0.17853 | 121.8979 | -122.1405 | -122.1039
586.7031 | 121.9116 | -121.6644 | 0.17853 | -0.013581 | 0.018532 | 0.013962 | -0.0098972 | -0.0096794 | 0.064657 | 0.070724 | -7.7774 | 0.23346 | -121.9711 | 0.13275 | -121.4447 | -121.9162 | -0.23804 | 0.004578 | 0.2243 | -121.9437 | -0.3067 | 0.054931 | 113.887 | 121.7972 | -121.6232 | -0.27924 | 0.045776 | 114.1937 | 121.4264 | 121.669 | 0.21973 | 121.8979 | 113.887 | 121.8887 | -0.25177 | -0.27924 | 121.8979 | 113.887 | -0.25177 | 0.21973 | 121.8887 | -122.1497 | -122.1222
588.4375 | 121.9162 | -121.6461 | 0.17853 | -0.005951 | 0.018532 | 0.019517 | -0.010324 | -0.0086112 | 0.061239 | 0.06987 | -7.7683 | 0.2243 | -121.9574 | 0.11902 | -121.4722 | -121.9345 | -0.19684 | -0.009155 | 0.23346 | -121.9482 | -0.31128 | 0.045776 | 113.8779 | 121.7651 | -121.6507 | -0.30212 | 0.054931 | 114.1891 | 121.4493 | 121.637 | 0.17395 | 121.8704 | 113.8779 | 121.8796 | -0.28839 | -0.30212 | 121.8704 | 113.8779 | -0.28839 | 0.17395 | 121.8796 | -122.1359 | -122.1268
590.1719 | 121.9757 | -121.6232 | 0.16022 | -0.005951 | 0.017677 | 0.010972 | -0.014811 | -0.0077566 | 0.061666 | 0.068161 | -7.7225 | 0.19684 | -121.907 | 0.23346 | -121.3715 | -121.8338 | -0.24261 | 0.13733 | 0.20599 | -121.907 | -0.28381 | 0.036621 | 113.9008 | 121.8567 | -121.5317 | -0.28381 | 0.045777 | 114.1846 | 121.3806 | 121.7606 | 0.25177 | 121.8201 | 113.9008 | 121.8292 | -0.21057 | -0.28381 | 121.8201 | 113.9008 | -0.21057 | 0.25177 | 121.8292 | -122.0673 | -122.0673
591.9219 | 121.8796 | -121.6736 | 0.19684 | -0.005951 | 0.019813 | 0.016312 | -0.0084018 | -0.0071158 | 0.05953 | 0.071151 | -7.7225 | 0.22888 | -121.962 | 0.19684 | -121.4035 | -121.875 | -0.18768 | 0.11902 | 0.23346 | -121.8979 | -0.28839 | 0.032044 | 113.9511 | 121.8704 | -121.6003 | -0.2243 | 0.036621 | 114.2395 | 121.4859 | 121.7926 | 0.27008 | 121.9025 | 113.9511 | 121.907 | -0.20142 | -0.2243 | 121.9025 | 113.9511 | -0.20142 | 0.27008 | 121.907 | -122.1588 | -122.0947
593.6094 | 121.875 | -121.6782 | 0.17853 | -0.02121 | 0.018959 | 0.014603 | -0.012888 | -0.007543 | 0.062948 | 0.06987 | -7.7133 | 0.19226 | -121.9116 | 0.2243 | -121.3623 | -121.788 | -0.39825 | 0.09613 | 0.18768 | -121.8979 | -0.23346 | 0.013733 | 113.9648 | 121.9025 | -121.5408 | -0.21973 | 0.009155 | 114.1983 | 121.2799 | 121.7743 | 0.31586 | 121.8704 | 113.9648 | 121.8658 | -0.10986 | -0.21973 | 121.8704 | 113.9648 | -0.10986 | 0.31586 | 121.8658 | -122.0901 | -122.0764
595.3438 | 121.8704 | -121.6782 | 0.18768 | 0.0016785 | 0.020027 | 0.01503 | -0.0092564 | -0.008184 | 0.063376 | 0.069229 | -7.7911 | 0.23346 | -121.962 | 0.16479 | -121.4264 | -121.8613 | -0.29755 | 0.027466 | 0.20142 | -121.9437 | -0.28381 | 0.045776 | 113.887 | 121.843 | -121.6141 | -0.2655 | 0.013733 | 114.1708 | 121.3806 | 121.7056 | 0.25177 | 121.9116 | 113.887 | 121.8796 | -0.1831 | -0.2655 | 121.9116 | 113.887 | -0.1831 | 0.25177 | 121.8796 | -122.1497 | -122.1313
597.0938 | 121.9299 | -121.6461 | 0.1831 | 0.0016785 | 0.019813 | 0.013749 | -0.012461 | -0.0079704 | 0.062735 | 0.069015 | -7.8049 | 0.24261 | -121.9666 | 0.10071 | -121.4722 | -121.9345 | -0.17395 | -0.018311 | 0.21515 | -121.9666 | -0.32044 | 0.05951 | 113.8412 | 121.7468 | -121.6553 | -0.32044 | 0.032044 | 114.1617 | 121.4722 | 121.6278 | 0.17395 | 121.8887 | 113.8412 | 121.8613 | -0.28839 | -0.32044 | 121.8887 | 113.8412 | -0.28839 | 0.17395 | 121.8613 | -122.1497 | -122.1497
598.7812 | 121.8887 | -121.6461 | 0.1831 | -0.02121 | 0.017891 | 0.01439 | -0.010965 | -0.0088248 | 0.06188 | 0.068588 | -7.7408 | 0.19226 | -121.8933 | 0.22888 | -121.3486 | -121.7972 | -0.39825 | 0.11444 | 0.17395 | -121.9437 | -0.24719 | 0.009156 | 113.9053 | 121.875 | -121.5317 | -0.29755 | -0.009155 | 114.1525 | 121.2479 | 121.7606 | 0.29755 | 121.8384 | 113.9053 | 121.8201 | -0.15106 | -0.29755 | 121.8384 | 113.9053 | -0.15106 | 0.29755 | 121.8201 | -122.0764 | -122.1268
600.5156 | 121.9254 | -121.6873 | 0.17853 | -0.005951 | 0.019813 | 0.017594 | -0.0075474 | -0.0069022 | 0.062094 | 0.070083 | -7.8369 | 0.22888 | -121.9803 | 0.11902 | -121.5088 | -121.9574 | -0.18768 | 0 | 0.25177 | -121.9391 | -0.29297 | 0.050354 | 113.8504 | 121.8063 | -121.6873 | -0.25177 | 0.073242 | 114.1434 | 121.4996 | 121.6873 | 0.17853 | 121.9162 | 113.8504 | 121.9391 | -0.27008 | -0.25177 | 121.9162 | 113.8504 | -0.27008 | 0.17853 | 121.9391 | -122.1588 | -122.1176
602.25 | 121.962 | -121.6278 | 0.15106 | 0.0016785 | 0.018532 | 0.011612 | -0.017374 | -0.007543 | 0.064871 | 0.070297 | -7.7957 | 0.20142 | -121.9254 | 0.23346 | -121.3348 | -121.788 | -0.35248 | 0.13275 | 0.17853 | -121.9208 | -0.29755 | 0.050354 | 113.8321 | 121.8613 | -121.4859 | -0.29297 | 0.027466 | 114.1296 | 121.2753 | 121.7606 | 0.29297 | 121.8292 | 113.8321 | 121.8063 | -0.16022 | -0.29297 | 121.8292 | 113.8321 | -0.16022 | 0.29297 | 121.8063 | -122.0764 | -122.0718
604 | 121.875 | -121.669 | 0.20142 | -0.005951 | 0.018318 | 0.014176 | -0.012461 | -0.0077566 | 0.062948 | 0.068588 | -7.7683 | 0.19684 | -121.9391 | 0.21057 | -121.3852 | -121.8201 | -0.37537 | 0.10529 | 0.19684 | -121.9208 | -0.27008 | -0.004578 | 113.9008 | 121.8796 | -121.5866 | -0.25177 | -0.004578 | 114.1708 | 121.2936 | 121.7743 | 0.28381 | 121.8658 | 113.9008 | 121.8658 | -0.15106 | -0.25177 | 121.8658 | 113.9008 | -0.15106 | 0.28381 | 121.8658 | -122.1405 | -122.1222
605.6875 | 122.0169 | -121.6278 | 0.15106 | -0.005951 | 0.015755 | 0.011185 | -0.013956 | -0.0083976 | 0.06423 | 0.070511 | -7.8094 | 0.20599 | -121.9116 | 0.17395 | -121.4172 | -121.8475 | -0.33875 | 0.050354 | 0.20142 | -121.9482 | -0.28381 | 0.054932 | 113.8184 | 121.8018 | -121.5683 | -0.32043 | 0.050354 | 114.1022 | 121.2891 | 121.6782 | 0.21057 | 121.8338 | 113.8184 | 121.8292 | -0.21973 | -0.32043 | 121.8338 | 113.8184 | -0.21973 | 0.21057 | 121.8292 | -122.0627 | -122.0993
607.4219 | 122.0123 | -121.6187 | 0.14191 | -0.005951 | 0.017036 | 0.016312 | -0.014597 | -0.009252 | 0.065084 | 0.069015 | -7.8552 | 0.2243 | -121.9162 | 0.17395 | -121.4081 | -121.8567 | -0.33417 | 0.064087 | 0.20142 | -121.9437 | -0.29755 | 0.082397 | 113.7634 | 121.7926 | -121.55 | -0.32501 | 0.059509 | 114.061 | 121.2845 | 121.6827 | 0.21057 | 121.843 | 113.7634 | 121.8201 | -0.23804 | -0.32501 | 121.843 | 113.7634 | -0.23804 | 0.21057 | 121.8201 | -122.0581 | -122.0856
609.1094 | 122.0078 | -121.6232 | 0.15106 | 0.0016785 | 0.018745 | 0.01204 | -0.010111 | -0.011602 | 0.062094 | 0.068802 | -7.8598 | 0.24261 | -122.0032 | 0.14648 | -121.463 | -121.9299 | -0.13733 | 0.050354 | 0.23346 | -121.9711 | -0.37994 | 0.091553 | 113.7634 | 121.7697 | -121.6141 | -0.3479 | 0.082397 | 114.1434 | 121.4859 | 121.6736 | 0.16022 | 121.8658 | 113.7634 | 121.8567 | -0.3067 | -0.3479 | 121.8658 | 113.7634 | -0.3067 | 0.16022 | 121.8567 | -122.1542 | -122.1222
610.8438 | 121.9757 | -121.6461 | 0.15564 | -0.005951 | 0.018318 | 0.01503 | -0.012247 | -0.0088248 | 0.063803 | 0.068588 | -7.7728 | 0.20599 | -121.9345 | 0.23346 | -121.3669 | -121.8201 | -0.28381 | 0.15106 | 0.2243 | -121.9574 | -0.28839 | 0.050354 | 113.8733 | 121.8796 | -121.5225 | -0.31128 | 0.068664 | 114.1617 | 121.3623 | 121.7972 | 0.27924 | 121.8521 | 113.8733 | 121.8704 | -0.17395 | -0.31128 | 121.8521 | 113.8733 | -0.17395 | 0.27924 | 121.8704 | -122.0901 | -122.113
612.5781 | 121.9574 | -121.6415 | 0.16937 | 0.0016785 | 0.018532 | 0.011399 | -0.013529 | -0.009252 | 0.062735 | 0.067947 | -7.7637 | 0.17853 | -121.9345 | 0.26093 | -121.344 | -121.8201 | -0.31586 | 0.16022 | 0.21057 | -121.9208 | -0.29297 | 0.009155 | 113.8779 | 121.9025 | -121.5134 | -0.27923 | 0.041198 | 114.1708 | 121.3257 | 121.8018 | 0.29755 | 121.8201 | 113.8779 | 121.8521 | -0.17853 | -0.27923 | 121.8201 | 113.8779 | -0.17853 | 0.29755 | 121.8521 | -122.1039 | -122.0901
614.25 | 121.8842 | -121.669 | 0.18768 | -0.005951 | 0.019386 | 0.01439 | -0.0086154 | -0.008184 | 0.062521 | 0.069229 | -7.782 | 0.21057 | -121.9437 | 0.23804 | -121.376 | -121.8063 | -0.36621 | 0.10986 | 0.20142 | -121.8933 | -0.27466 | 0.022888 | 113.887 | 121.907 | -121.5637 | -0.22431 | 0.013733 | 114.1617 | 121.3028 | 121.7789 | 0.29297 | 121.8796 | 113.887 | 121.8704 | -0.13733 | -0.22431 | 121.8796 | 113.887 | -0.13733 | 0.29297 | 121.8704 | -122.1313 | -122.081
615.9844 | 121.8979 | -121.6553 | 0.1831 | 0.0016785 | 0.0196 | 0.013108 | -0.012247 | -0.0094656 | 0.063803 | 0.069656 | -7.782 | 0.18768 | -121.9254 | 0.24261 | -121.376 | -121.7972 | -0.40283 | 0.10529 | 0.19684 | -121.9482 | -0.27008 | 0.004578 | 113.8733 | 121.8979 | -121.5591 | -0.29297 | 0.013733 | 114.1434 | 121.2524 | 121.7606 | 0.27923 | 121.843 | 113.8733 | 121.8521 | -0.14191 | -0.29297 | 121.843 | 113.8733 | -0.14191 | 0.27923 | 121.8521 | -122.1085 | -122.1313
617.7344 | 121.8933 | -121.701 | 0.18768 | 0.0016785 | 0.017891 | 0.012467 | -0.011606 | -0.01032 | 0.062735 | 0.069229 | -7.7911 | 0.19226 | -121.9391 | 0.23346 | -121.3898 | -121.8109 | -0.42114 | 0.086975 | 0.20599 | -121.9299 | -0.23804 | 0.004578 | 113.9099 | 121.9345 | -121.5775 | -0.22888 | 0.018311 | 114.1479 | 121.2799 | 121.788 | 0.31128 | 121.8933 | 113.9099 | 121.907 | -0.10986 | -0.22888 | 121.8933 | 113.9099 | -0.10986 | 0.31128 | 121.907 | -122.1268 | -122.1176
619.4844 | 122.0032 | -121.6141 | 0.14648 | 0.0016785 | 0.020027 | 0.015671 | -0.012888 | -0.009893 | 0.064871 | 0.068802 | -7.8369 | 0.20599 | -121.9254 | 0.1831 | -121.4035 | -121.8384 | -0.3479 | 0.054932 | 0.20142 | -121.9345 | -0.31128 | 0.05951 | 113.7772 | 121.7972 | -121.55 | -0.32043 | 0.054932 | 114.0884 | 121.2662 | 121.669 | 0.21057 | 121.8201 | 113.7772 | 121.8155 | -0.2243 | -0.32043 | 121.8201 | 113.7772 | -0.2243 | 0.21057 | 121.8155 | -122.0718 | -122.081
621.1562 | 122.0123 | -121.6049 | 0.13733 | 0.0016785 | 0.018532 | 0.012681 | -0.012033 | -0.012029 | 0.066366 | 0.069229 | -7.8552 | 0.20599 | -121.907 | 0.2243 | -121.3806 | -121.843 | -0.35248 | 0.11444 | 0.19226 | -121.9391 | -0.30212 | 0.068665 | 113.7497 | 121.8292 | -121.5179 | -0.33417 | 0.054932 | 114.0518 | 121.2524 | 121.7194 | 0.2243 | 121.8109 | 113.7497 | 121.7972 | -0.23804 | -0.33417 | 121.8109 | 113.7497 | -0.23804 | 0.2243 | 121.7972 | -122.0444 | -122.0764
622.9062 | 121.9711 | -121.6507 | 0.16479 | -0.02121 | 0.020454 | 0.014176 | -0.006052 | -0.0062614 | 0.061453 | 0.069443 | -7.8415 | 0.24719 | -121.9666 | 0.19684 | -121.4447 | -121.8796 | -0.16937 | 0.09613 | 0.24261 | -121.9757 | -0.31586 | 0.082397 | 113.8092 | 121.8475 | -121.6095 | -0.32501 | 0.07782 | 114.1251 | 121.4813 | 121.7468 | 0.20599 | 121.8979 | 113.8092 | 121.8933 | -0.22888 | -0.32501 | 121.8979 | 113.8092 | -0.22888 | 0.20599 | 121.8933 | -122.1313 | -122.1405
624.5781 | 121.962 | -121.6644 | 0.16022 | -0.005951 | 0.017677 | 0.011826 | -0.012674 | -0.010107 | 0.060598 | 0.069015 | -7.7911 | 0.20599 | -121.9574 | 0.27924 | -121.3623 | -121.8063 | -0.33875 | 0.16937 | 0.21973 | -121.9254 | -0.29297 | 0.045777 | 113.8733 | 121.9437 | -121.5225 | -0.26093 | 0.05951 | 114.1663 | 121.3257 | 121.8338 | 0.30212 | 121.8704 | 113.8733 | 121.8842 | -0.14191 | -0.26093 | 121.8704 | 113.8733 | -0.14191 | 0.30212 | 121.8842 | -122.1176 | -122.0856
626.3125 | 121.9391 | -121.6461 | 0.17853 | -0.013581 | 0.0196 | 0.014176 | -0.0073336 | -0.0049796 | 0.060812 | 0.071151 | -7.8873 | 0.23804 | -121.9757 | 0.13733 | -121.4905 | -121.9482 | -0.19226 | -0.022888 | 0.23346 | -121.9299 | -0.32959 | 0.059509 | 113.7588 | 121.7834 | -121.669 | -0.28381 | 0.054931 | 114.0884 | 121.4539 | 121.6232 | 0.15564 | 121.8842 | 113.7588 | 121.8796 | -0.30212 | -0.28381 | 121.8842 | 113.7588 | -0.30212 | 0.15564 | 121.8796 | -122.1542 | -122.1085
628 | 122.0123 | -121.6232 | 0.15564 | -0.005951 | 0.020454 | 0.013321 | -0.019297 | -0.0090384 | 0.063162 | 0.068802 | -7.869 | 0.21515 | -121.9254 | 0.20599 | -121.3715 | -121.843 | -0.35248 | 0.086975 | 0.21057 | -121.9391 | -0.30212 | 0.059509 | 113.7543 | 121.8292 | -121.5271 | -0.31586 | 0.054931 | 114.0564 | 121.2708 | 121.7102 | 0.25177 | 121.8384 | 113.7543 | 121.8338 | -0.21973 | -0.31586 | 121.8384 | 113.7543 | -0.21973 | 0.25177 | 121.8338 | -122.081 | -122.0947
629.7344 | 122.0078 | -121.6278 | 0.15106 | -0.02121 | 0.016182 | 0.012894 | -0.015024 | -0.0088248 | 0.064016 | 0.068802 | -7.8873 | 0.19684 | -121.9345 | 0.18768 | -121.4035 | -121.8475 | -0.3479 | 0.036621 | 0.19684 | -121.9345 | -0.3067 | 0.045776 | 113.7405 | 121.8155 | -121.5546 | -0.3067 | 0.045776 | 114.0472 | 121.2799 | 121.6644 | 0.22431 | 121.8246 | 113.7405 | 121.8246 | -0.21973 | -0.3067 | 121.8246 | 113.7405 | -0.21973 | 0.22431 | 121.8246 | -122.0856 | -122.0856
631.4062 | 122.0032 | -121.6278 | 0.14648 | -0.005951 | 0.019813 | 0.0096899 | -0.014597 | -0.0088248 | 0.063376 | 0.070511 | -7.901 | 0.20142 | -121.9116 | 0.20142 | -121.4127 | -121.8475 | -0.3479 | 0.041199 | 0.19684 | -121.9574 | -0.28381 | 0.054932 | 113.7268 | 121.8292 | -121.5591 | -0.32959 | 0.050354 | 114.0106 | 121.2799 | 121.669 | 0.21515 | 121.8292 | 113.7268 | 121.8246 | -0.21973 | -0.32959 | 121.8292 | 113.7268 | -0.21973 | 0.21515 | 121.8246 | -122.0581 | -122.1039
633.0938 | 122.0215 | -121.637 | 0.16022 | -0.013581 | 0.017677 | 0.0069129 | -0.012033 | -0.009893 | 0.062307 | 0.069015 | -7.8873 | 0.21515 | -121.9528 | 0.1831 | -121.4035 | -121.8613 | -0.32501 | 0.059509 | 0.18768 | -121.9437 | -0.31586 | 0.054932 | 113.7497 | 121.8201 | -121.5637 | -0.3067 | 0.027466 | 114.0656 | 121.312 | 121.6965 | 0.23346 | 121.8521 | 113.7497 | 121.8246 | -0.2243 | -0.3067 | 121.8521 | 113.7497 | -0.2243 | 0.23346 | 121.8246 | -122.113 | -122.1039
634.8438 | 121.9528 | -121.6507 | 0.16022 | -0.005951 | 0.0196 | 0.014817 | -0.010965 | -0.0071158 | 0.063162 | 0.069656 | -7.8644 | 0.20599 | -121.9208 | 0.20142 | -121.4172 | -121.8475 | -0.36621 | 0.064087 | 0.20142 | -121.9849 | -0.27008 | 0.045777 | 113.7863 | 121.8521 | -121.5775 | -0.33417 | 0.041199 | 114.0564 | 121.2845 | 121.7148 | 0.23346 | 121.8567 | 113.7863 | 121.8521 | -0.19684 | -0.33417 | 121.8567 | 113.7863 | -0.19684 | 0.23346 | 121.8521 | -122.081 | -122.1451
636.5156 | 121.9528 | -121.6736 | 0.16937 | 0.0016785 | 0.01725 | 0.013108 | -0.013102 | -0.009252 | 0.065084 | 0.068161 | -7.8735 | 0.20599 | -121.9437 | 0.21057 | -121.4218 | -121.8613 | -0.37079 | 0.054932 | 0.1831 | -121.9254 | -0.27008 | 0.036621 | 113.8 | 121.8842 | -121.5912 | -0.25177 | 0.013732 | 114.0701 | 121.3028 | 121.7285 | 0.25177 | 121.8796 | 113.8 | 121.8567 | -0.18768 | -0.25177 | 121.8796 | 113.8 | -0.18768 | 0.25177 | 121.8567 | -122.113 | -122.0947
638.2656 | 122.0352 | -121.6415 | 0.13275 | -0.013581 | 0.020454 | 0.011612 | -0.013529 | -0.0086112 | 0.062948 | 0.071365 | -7.9056 | 0.21515 | -121.9391 | 0.20599 | -121.3943 | -121.843 | -0.3479 | 0.073242 | 0.20599 | -121.9345 | -0.29755 | 0.082398 | 113.736 | 121.8475 | -121.5271 | -0.29297 | 0.073243 | 114.0335 | 121.2936 | 121.7148 | 0.24719 | 121.8567 | 113.736 | 121.8475 | -0.20142 | -0.29297 | 121.8567 | 113.736 | -0.20142 | 0.24719 | 121.8475 | -122.0718 | -122.0673
640 | 121.8887 | -121.7285 | 0.19684 | -0.013581 | 0.020882 | 0.013321 | -0.0069064 | -0.0054068 | 0.060385 | 0.068588 | -7.8415 | 0.21515 | -122.0032 | 0.21057 | -121.431 | -121.875 | -0.21057 | 0.091553 | 0.21973 | -121.9482 | -0.27466 | 0.018311 | 113.887 | 121.9391 | -121.6278 | -0.21973 | 0.022889 | 114.1617 | 121.5179 | 121.8201 | 0.29755 | 121.9437 | 113.887 | 121.9482 | -0.14648 | -0.21973 | 121.9437 | 113.887 | -0.14648 | 0.29755 | 121.9482 | -122.2 | -122.1451
641.6562 | 122.0169 | -121.6599 | 0.12817 | 0.0016785 | 0.019386 | 0.012894 | -0.013742 | -0.009893 | 0.064871 | 0.06987 | -7.9193 | 0.2243 | -121.962 | 0.16022 | -121.4447 | -121.9254 | -0.1831 | 0.054932 | 0.22888 | -121.9528 | -0.30212 | 0.09613 | 113.7405 | 121.8201 | -121.5729 | -0.29297 | 0.10071 | 114.0427 | 121.4767 | 121.7148 | 0.21515 | 121.8842 | 113.7405 | 121.8887 | -0.2655 | -0.29297 | 121.8842 | 113.7405 | -0.2655 | 0.21515 | 121.8887 | -122.0901 | -122.081
643.4062 | 122.0215 | -121.6736 | 0.14191 | -0.005951 | 0.018105 | 0.014817 | -0.0098972 | -0.0083976 | 0.062521 | 0.069229 | -7.9422 | 0.25635 | -121.9894 | 0.15106 | -121.4676 | -121.9437 | -0.16022 | 0.041199 | 0.22888 | -121.962 | -0.31586 | 0.11444 | 113.7314 | 121.8246 | -121.6095 | -0.28839 | 0.086975 | 114.0472 | 121.5134 | 121.7148 | 0.20599 | 121.9299 | 113.7314 | 121.9025 | -0.27008 | -0.28839 | 121.9299 | 113.7314 | -0.27008 | 0.20599 | 121.9025 | -122.1313 | -122.1039
645.0781 | 122.0261 | -121.6599 | 0.15106 | -0.013581 | 0.0196 | 0.013962 | -0.0090426 | -0.0062614 | 0.061666 | 0.06752 | -7.9468 | 0.25635 | -121.9803 | 0.11902 | -121.463 | -121.9437 | -0.14648 | 0.041199 | 0.24719 | -121.9803 | -0.32044 | 0.10529 | 113.7131 | 121.7789 | -121.6141 | -0.32044 | 0.09613 | 114.0335 | 121.5134 | 121.7011 | 0.19684 | 121.9162 | 113.7131 | 121.907 | -0.28381 | -0.32044 | 121.9162 | 113.7131 | -0.28381 | 0.19684 | 121.907 | -122.1313 | -122.1313
646.8125 | 122.0215 | -121.6873 | 0.13733 | -0.013581 | 0.021095 | 0.01204 | -0.012888 | -0.0066886 | 0.06423 | 0.068588 | -7.933 | 0.20599 | -121.9711 | 0.16479 | -121.4447 | -121.9345 | -0.18768 | 0.064087 | 0.19684 | -121.9986 | -0.28381 | 0.068665 | 113.7543 | 121.8521 | -121.582 | -0.31128 | 0.059509 | 114.0381 | 121.4996 | 121.7514 | 0.24261 | 121.8933 | 113.7543 | 121.8842 | -0.24719 | -0.31128 | 121.8933 | 113.7543 | -0.24719 | 0.24261 | 121.8842 | -122.1085 | -122.1359
648.5469 | 121.9025 | -121.7239 | 0.16022 | 0.0016785 | 0.021095 | 0.015458 | -0.008829 | -0.0077566 | 0.063162 | 0.069015 | -7.8735 | 0.21515 | -122.0261 | 0.16022 | -121.463 | -121.9162 | -0.21973 | 0.10071 | 0.21515 | -121.9711 | -0.30212 | 0.054932 | 113.8504 | 121.8842 | -121.6232 | -0.24719 | 0.054932 | 114.1525 | 121.5042 | 121.8246 | 0.26093 | 121.9391 | 113.8504 | 121.9391 | -0.19226 | -0.24719 | 121.9391 | 113.8504 | -0.19226 | 0.26093 | 121.9391 | -122.1863 | -122.1313
650.2188 | 121.9803 | -121.7056 | 0.13275 | 0.009308 | 0.018532 | 0.012681 | -0.0090426 | -0.0069022 | 0.060812 | 0.069443 | -7.9468 | 0.19684 | -122.0261 | 0.13275 | -121.4539 | -121.9345 | -0.16937 | 0.07782 | 0.20142 | -121.9803 | -0.32043 | 0.064087 | 113.7589 | 121.8384 | -121.5866 | -0.27466 | 0.068665 | 114.0793 | 121.5363 | 121.7834 | 0.25177 | 121.9025 | 113.7589 | 121.907 | -0.22888 | -0.27466 | 121.9025 | 113.7589 | -0.22888 | 0.25177 | 121.907 | -122.1588 | -122.113
651.9688 | 122.0078 | -121.6873 | 0.10071 | -0.005951 | 0.017036 | 0.011612 | -0.016519 | -0.0088248 | 0.065298 | 0.069656 | -7.9742 | 0.1831 | -121.9574 | 0.13733 | -121.431 | -121.8933 | -0.33417 | 0.045776 | 0.15564 | -121.9894 | -0.27008 | 0.082397 | 113.7131 | 121.8246 | -121.5317 | -0.30212 | 0.054932 | 113.9832 | 121.3531 | 121.7331 | 0.25635 | 121.8704 | 113.7131 | 121.843 | -0.20599 | -0.30212 | 121.8704 | 113.7131 | -0.20599 | 0.25635 | 121.843 | -122.0581 | -122.0901
653.7188 | 121.9986 | -121.7102 | 0.14191 | -0.005951 | 0.015968 | 0.010972 | -0.012461 | -0.009252 | 0.062735 | 0.068588 | -7.9056 | 0.16022 | -121.9711 | 0.20599 | -121.4081 | -121.8887 | -0.28839 | 0.14191 | 0.16022 | -121.9803 | -0.26093 | 0.01831 | 113.8046 | 121.9162 | -121.55 | -0.27008 | 0.01831 | 114.0656 | 121.4218 | 121.8521 | 0.30212 | 121.8704 | 113.8046 | 121.8704 | -0.17853 | -0.27008 | 121.8704 | 113.8046 | -0.17853 | 0.30212 | 121.8704 | -122.113 | -122.1222
655.4062 | 122.0078 | -121.6873 | 0.13275 | -0.013581 | 0.020241 | 0.012467 | -0.012033 | -0.010534 | 0.061239 | 0.06752 | -7.9376 | 0.16479 | -121.9986 | 0.18768 | -121.4218 | -121.8933 | -0.27008 | 0.12817 | 0.1831 | -121.9437 | -0.31128 | 0.032044 | 113.7497 | 121.875 | -121.5546 | -0.25635 | 0.050354 | 114.061 | 121.4172 | 121.8155 | 0.2655 | 121.8521 | 113.7497 | 121.8704 | -0.20599 | -0.25635 | 121.8521 | 113.7497 | -0.20599 | 0.2655 | 121.8704 | -122.1313 | -122.0764
657.1406 | 121.9986 | -121.6919 | 0.1236 | 0.009308 | 0.018318 | 0.014603 | -0.013102 | -0.012456 | 0.065298 | 0.070724 | -7.9697 | 0.17853 | -121.9849 | 0.15564 | -121.4401 | -121.8887 | -0.36163 | 0.059509 | 0.16937 | -121.9849 | -0.29297 | 0.054932 | 113.7222 | 121.8475 | -121.5637 | -0.29297 | 0.045777 | 114.0152 | 121.3303 | 121.7514 | 0.25177 | 121.8704 | 113.7222 | 121.8613 | -0.19684 | -0.29297 | 121.8704 | 113.7222 | -0.19684 | 0.25177 | 121.8613 | -122.1085 | -122.1085
658.8906 | 121.9894 | -121.6965 | 0.13733 | 0.0016785 | 0.020027 | 0.012467 | -0.0081882 | -0.0088248 | 0.060812 | 0.069443 | -7.9697 | 0.2243 | -122.049 | 0.12817 | -121.4813 | -121.9482 | -0.18768 | 0.07782 | 0.21057 | -122.0123 | -0.35248 | 0.086975 | 113.7268 | 121.8246 | -121.6187 | -0.31586 | 0.073242 | 114.0793 | 121.5088 | 121.7743 | 0.21515 | 121.9208 | 113.7268 | 121.907 | -0.25177 | -0.31586 | 121.9208 | 113.7268 | -0.25177 | 0.21515 | 121.907 | -122.1863 | -122.1497
660.5625 | 121.9894 | -121.6919 | 0.13733 | -0.013581 | 0.016823 | 0.014176 | -0.0081882 | -0.0066886 | 0.061239 | 0.067093 | -7.9697 | 0.19684 | -122.0261 | 0.12817 | -121.4813 | -121.962 | -0.18768 | 0.086975 | 0.2243 | -121.9803 | -0.33417 | 0.059509 | 113.7222 | 121.8201 | -121.6187 | -0.28839 | 0.086975 | 114.0564 | 121.5042 | 121.7789 | 0.21057 | 121.8887 | 113.7222 | 121.9162 | -0.27008 | -0.28839 | 121.8887 | 113.7222 | -0.27008 | 0.21057 | 121.9162 | -122.1634 | -122.1176
662.2969 | 121.9894 | -121.7148 | 0.13275 | -0.005951 | 0.016823 | 0.010544 | -0.011393 | -0.0083976 | 0.061666 | 0.068161 | -7.9285 | 0.16479 | -121.962 | 0.21973 | -121.3806 | -121.8475 | -0.33875 | 0.16479 | 0.16479 | -121.994 | -0.24719 | 0.032044 | 113.7863 | 121.9345 | -121.5134 | -0.27924 | 0.032044 | 114.0335 | 121.376 | 121.8796 | 0.33417 | 121.8796 | 113.7863 | 121.8796 | -0.13275 | -0.27924 | 121.8796 | 113.7863 | -0.13275 | 0.33417 | 121.8796 | -122.0947 | -122.1268
664.0312 | 121.907 | -121.7514 | 0.15106 | -0.005951 | 0.019173 | 0.010331 | -0.007761 | -0.0088248 | 0.062307 | 0.069443 | -7.9376 | 0.21515 | -122.0123 | 0.16479 | -121.4722 | -121.9391 | -0.21973 | 0.10071 | 0.18768 | -121.9803 | -0.26093 | 0.064087 | 113.8138 | 121.9162 | -121.6232 | -0.22888 | 0.036621 | 114.0747 | 121.5317 | 121.8521 | 0.27924 | 121.9666 | 113.8138 | 121.9391 | -0.18768 | -0.22888 | 121.9666 | 113.8138 | -0.18768 | 0.27924 | 121.9391 | -122.1634 | -122.1313
665.7812 | 121.8933 | -121.7377 | 0.16022 | -0.013581 | 0.020027 | 0.01439 | -0.013529 | -0.0060478 | 0.063589 | 0.071151 | -7.9193 | 0.16479 | -121.9803 | 0.19226 | -121.4172 | -121.8475 | -0.41199 | 0.082397 | 0.18768 | -121.9894 | -0.24262 | 0.004578 | 113.8184 | 121.9299 | -121.5775 | -0.25177 | 0.027466 | 114.061 | 121.3257 | 121.8201 | 0.32044 | 121.9025 | 113.8184 | 121.9254 | -0.10986 | -0.25177 | 121.9025 | 113.8184 | -0.10986 | 0.32044 | 121.9254 | -122.1405 | -122.1497
667.5156 | 121.8842 | -121.7239 | 0.15564 | 0.0016785 | 0.0196 | 0.013962 | -0.0090426 | -0.0071158 | 0.062735 | 0.072006 | -7.9422 | 0.18768 | -121.9986 | 0.19684 | -121.4264 | -121.8658 | -0.3891 | 0.10071 | 0.15106 | -121.9711 | -0.27466 | 0.032043 | 113.7817 | 121.9208 | -121.582 | -0.24719 | -0.004578 | 114.0564 | 121.3348 | 121.8246 | 0.29755 | 121.9116 | 113.7817 | 121.875 | -0.14191 | -0.24719 | 121.9116 | 113.7817 | -0.14191 | 0.29755 | 121.875 | -122.1542 | -122.1268
669.1875 | 121.9849 | -121.6919 | 0.09613 | -0.013581 | 0.01725 | 0.0096899 | -0.013956 | -0.009893 | 0.063803 | 0.06752 | -7.9697 | 0.16479 | -121.9666 | 0.20142 | -121.3989 | -121.8613 | -0.37079 | 0.1236 | 0.18768 | -122.0078 | -0.27466 | 0.068665 | 113.7222 | 121.8933 | -121.4951 | -0.31586 | 0.091553 | 113.9969 | 121.3211 | 121.8155 | 0.29297 | 121.8567 | 113.7222 | 121.8796 | -0.16937 | -0.31586 | 121.8567 | 113.7222 | -0.16937 | 0.29297 | 121.8796 | -122.0627 | -122.1039
670.9375 | 121.8979 | -121.7422 | 0.15106 | -0.005951 | 0.016609 | 0.013749 | -0.010752 | -0.0088248 | 0.064016 | 0.069656 | -7.933 | 0.14191 | -121.9803 | 0.1831 | -121.4401 | -121.8567 | -0.42572 | 0.091553 | 0.15106 | -121.9803 | -0.23804 | -0.009155 | 113.8092 | 121.9254 | -121.5912 | -0.23804 | 0 | 114.0472 | 121.3165 | 121.8338 | 0.30212 | 121.8842 | 113.8092 | 121.8933 | -0.11444 | -0.23804 | 121.8842 | 113.8092 | -0.11444 | 0.30212 | 121.8933 | -122.1313 | -122.1313
672.6094 | 121.9345 | -121.7285 | 0.13733 | 0.016937 | 0.020454 | 0.012253 | -0.0069064 | -0.0083976 | 0.062521 | 0.068802 | -8.0246 | 0.20142 | -122.0352 | 0.10986 | -121.5225 | -121.9711 | -0.28381 | -0.004578 | 0.19226 | -122.0078 | -0.3067 | 0.064087 | 113.7039 | 121.8384 | -121.6599 | -0.27923 | 0.054932 | 114.0106 | 121.4447 | 121.7239 | 0.20599 | 121.9299 | 113.7039 | 121.9208 | -0.24261 | -0.27923 | 121.9299 | 113.7039 | -0.24261 | 0.20599 | 121.9208 | -122.1725 | -122.1451
674.3594 | 121.9528 | -121.7239 | 0.12817 | -0.005951 | 0.018959 | 0.011612 | -0.0075474 | -0.0073294 | 0.063589 | 0.067947 | -8.0338 | 0.21057 | -122.0398 | 0.091553 | -121.5591 | -122.0352 | -0.20142 | -0.022888 | 0.19684 | -121.9986 | -0.31586 | 0.082397 | 113.6902 | 121.8155 | -121.6873 | -0.27466 | 0.068664 | 114.006 | 121.5225 | 121.7011 | 0.16479 | 121.9345 | 113.6902 | 121.9208 | -0.31128 | -0.27466 | 121.9345 | 113.6902 | -0.31128 | 0.16479 | 121.9208 | -122.168 | -122.1268
676.1094 | 121.9391 | -121.7194 | 0.15564 | -0.013581 | 0.020882 | 0.013321 | -0.00947 | -0.0073294 | 0.065725 | 0.06987 | -8.0292 | 0.21515 | -122.0306 | 0.073242 | -121.5363 | -121.9986 | -0.17853 | -0.032043 | 0.20142 | -122.049 | -0.31128 | 0.059509 | 113.6902 | 121.7926 | -121.6919 | -0.32959 | 0.045776 | 114.0015 | 121.5408 | 121.6873 | 0.1831 | 121.9345 | 113.6902 | 121.9208 | -0.27924 | -0.32959 | 121.9345 | 113.6902 | -0.27924 | 0.1831 | 121.9208 | -122.1863 | -122.2046
677.8594 | 121.994 | -121.7148 | 0.1236 | -0.005951 | 0.018745 | 0.013749 | -0.015238 | -0.0096794 | 0.062094 | 0.068588 | -8.0109 | 0.17853 | -121.9849 | 0.13733 | -121.4584 | -121.9162 | -0.37537 | 0.041199 | 0.17395 | -122.0215 | -0.27008 | 0.054932 | 113.7039 | 121.8521 | -121.582 | -0.3067 | 0.050354 | 113.974 | 121.3394 | 121.756 | 0.25635 | 121.8933 | 113.7039 | 121.8887 | -0.20142 | -0.3067 | 121.8933 | 113.7039 | -0.20142 | 0.25635 | 121.8887 | -122.1085 | -122.1451
679.5938 | 121.9894 | -121.7194 | 0.12817 | -0.005951 | 0.018532 | 0.015458 | -0.012461 | -0.005834 | 0.063162 | 0.069443 | -7.9605 | 0.15564 | -121.9803 | 0.21973 | -121.4035 | -121.875 | -0.36163 | 0.14648 | 0.16022 | -121.9894 | -0.26093 | 0.027466 | 113.7588 | 121.9391 | -121.5317 | -0.27008 | 0.032043 | 114.0198 | 121.3577 | 121.8658 | 0.31586 | 121.875 | 113.7588 | 121.8796 | -0.15564 | -0.27008 | 121.875 | 113.7588 | -0.15564 | 0.31586 | 121.8796 | -122.1085 | -122.1176
681.2656 | 122.0261 | -121.6736 | 0.12817 | -0.013581 | 0.018532 | 0.010331 | -0.012888 | -0.0083976 | 0.064444 | 0.06987 | -8.0521 | 0.18768 | -121.9803 | 0.16022 | -121.4447 | -121.8979 | -0.37079 | 0.045776 | 0.17853 | -121.994 | -0.3067 | 0.059509 | 113.6215 | 121.8338 | -121.5729 | -0.32043 | 0.050354 | 113.9282 | 121.3028 | 121.7194 | 0.22888 | 121.8613 | 113.6215 | 121.8521 | -0.2243 | -0.32043 | 121.8613 | 113.6215 | -0.2243 | 0.22888 | 121.8521 | -122.1085 | -122.1222
683 | 121.9254 | -121.6965 | 0.16479 | -0.005951 | 0.020241 | 0.012253 | -0.0079746 | -0.006475 | 0.061239 | 0.069656 | -8.0246 | 0.20142 | -122.0398 | 0.15106 | -121.4905 | -121.9162 | -0.32959 | 0.032043 | 0.18768 | -121.9482 | -0.34332 | 0.036621 | 113.6719 | 121.8475 | -121.6553 | -0.25177 | 0.022888 | 114.0152 | 121.3669 | 121.7285 | 0.20599 | 121.8979 | 113.6719 | 121.8842 | -0.21973 | -0.25177 | 121.8979 | 113.6719 | -0.21973 | 0.20599 | 121.8842 | -122.2046 | -122.113
684.75 | 121.9482 | -121.7285 | 0.13733 | -0.02121 | 0.0196 | 0.014603 | -0.01417 | -0.009893 | 0.063162 | 0.068588 | -8.0109 | 0.17395 | -121.9803 | 0.17853 | -121.4539 | -121.9025 | -0.42572 | 0.054932 | 0.17395 | -121.9894 | -0.25177 | 0.036621 | 113.7177 | 121.907 | -121.5912 | -0.26093 | 0.036621 | 113.9694 | 121.3028 | 121.7834 | 0.27466 | 121.9025 | 113.7177 | 121.9025 | -0.17395 | -0.26093 | 121.9025 | 113.7177 | -0.17395 | 0.27466 | 121.9025 | -122.1176 | -122.1268
686.4219 | 122.0261 | -121.6965 | 0.11444 | -0.02121 | 0.018532 | 0.012681 | -0.0086154 | -0.0088248 | 0.063803 | 0.070511 | -8.0566 | 0.16022 | -122.0032 | 0.14191 | -121.4859 | -121.9116 | -0.37537 | 0.032043 | 0.19226 | -122.0215 | -0.3067 | 0.045776 | 113.6398 | 121.8384 | -121.6003 | -0.32501 | 0.07782 | 113.9465 | 121.3211 | 121.7285 | 0.21057 | 121.8567 | 113.6398 | 121.8887 | -0.21515 | -0.32501 | 121.8567 | 113.6398 | -0.21515 | 0.21057 | 121.8887 | -122.1176 | -122.1359
688.1562 | 122.0123 | -121.7102 | 0.11444 | 0.0016785 | 0.0196 | 0.011612 | -0.013315 | -0.011602 | 0.064871 | 0.070083 | -8.0429 | 0.16937 | -121.9986 | 0.18768 | -121.4539 | -121.8933 | -0.37537 | 0.073242 | 0.17853 | -122.0078 | -0.28839 | 0.054932 | 113.6673 | 121.8979 | -121.5683 | -0.29755 | 0.064087 | 113.9557 | 121.3348 | 121.7834 | 0.25635 | 121.8796 | 113.6673 | 121.8887 | -0.18311 | -0.29755 | 121.8796 | 113.6673 | -0.18311 | 0.25635 | 121.8887 | -122.113 | -122.1222
689.9062 | 122.0078 | -121.7285 | 0.11902 | -0.005951 | 0.016609 | 0.01204 | -0.010965 | -0.011388 | 0.062948 | 0.068374 | -8.0154 | 0.16022 | -122.0169 | 0.21973 | -121.4264 | -121.8979 | -0.31128 | 0.13275 | 0.16479 | -121.9894 | -0.28839 | 0.041198 | 113.7131 | 121.9482 | -121.5454 | -0.26093 | 0.045776 | 114.0015 | 121.4172 | 121.8613 | 0.30212 | 121.8887 | 113.7131 | 121.8933 | -0.16937 | -0.26093 | 121.8887 | 113.7131 | -0.16937 | 0.30212 | 121.8933 | -122.1359 | -122.1085
691.5781 | 122.0261 | -121.6965 | 0.1236 | -0.005951 | 0.017464 | 0.013535 | -0.0098972 | -0.010534 | 0.063803 | 0.069656 | -8.02 | 0.1831 | -122.0032 | 0.18768 | -121.4584 | -121.9208 | -0.27466 | 0.10071 | 0.20599 | -122.0032 | -0.3067 | 0.059509 | 113.6765 | 121.8842 | -121.582 | -0.3067 | 0.082398 | 113.9832 | 121.4218 | 121.7972 | 0.23804 | 121.8796 | 113.6765 | 121.9025 | -0.2243 | -0.3067 | 121.8796 | 113.6765 | -0.2243 | 0.23804 | 121.9025 | -122.1268 | -122.1268
693.3281 | 121.9711 | -121.7331 | 0.14191 | 0.0016785 | 0.020027 | 0.014176 | -0.0051974 | -0.0073294 | 0.062735 | 0.068161 | -8.0704 | 0.21973 | -122.049 | 0.082397 | -121.5317 | -121.9986 | -0.22888 | -0.036621 | 0.22888 | -121.994 | -0.31586 | 0.07782 | 113.6627 | 121.8155 | -121.6736 | -0.26093 | 0.086975 | 113.9786 | 121.5042 | 121.6965 | 0.20142 | 121.9528 | 113.6627 | 121.962 | -0.2655 | -0.26093 | 121.9528 | 113.6627 | -0.2655 | 0.20142 | 121.962 | -122.1909 | -122.1359
695.0156 | 121.9254 | -121.7514 | 0.17395 | -0.005951 | 0.0196 | 0.013962 | -0.0096836 | -0.0069022 | 0.064444 | 0.068374 | -8.0429 | 0.21973 | -122.0078 | 0.16937 | -121.4676 | -121.9162 | -0.39825 | 0.050354 | 0.17853 | -122.0123 | -0.25635 | 0.045777 | 113.7085 | 121.9208 | -121.6415 | -0.26093 | 0.004578 | 113.9648 | 121.3531 | 121.8018 | 0.28381 | 121.9711 | 113.7085 | 121.9299 | -0.1648 | -0.26093 | 121.9711 | 113.7085 | -0.1648 | 0.28381 | 121.9299 | -122.1817 | -122.1863
696.75 | 121.9254 | -121.7514 | 0.15106 | -0.013581 | 0.020882 | 0.016953 | -0.0098972 | -0.0071158 | 0.060385 | 0.06987 | -8.0429 | 0.18768 | -122.049 | 0.1236 | -121.5042 | -121.962 | -0.23346 | 0.036621 | 0.21057 | -122.0123 | -0.29755 | 0.036621 | 113.7085 | 121.875 | -121.6553 | -0.26093 | 0.059509 | 114.006 | 121.5179 | 121.788 | 0.24719 | 121.9391 | 113.7085 | 121.962 | -0.21057 | -0.26093 | 121.9391 | 113.7085 | -0.21057 | 0.24719 | 121.962 | -122.2 | -122.1634
698.5 | 121.9666 | -121.7239 | 0.13275 | -0.005951 | 0.019173 | 0.015885 | -0.014383 | -0.0086112 | 0.061666 | 0.06987 | -8.0658 | 0.17395 | -121.9711 | 0.16022 | -121.4539 | -121.907 | -0.40741 | 0.045776 | 0.16479 | -122.0169 | -0.24719 | 0.041199 | 113.6581 | 121.8842 | -121.5866 | -0.29297 | 0.032044 | 113.9053 | 121.3165 | 121.7697 | 0.27008 | 121.8979 | 113.6581 | 121.8887 | -0.1831 | -0.29297 | 121.8979 | 113.6581 | -0.1831 | 0.27008 | 121.8887 | -122.1039 | -122.1497
700.2344 | 121.994 | -121.6827 | 0.13275 | -0.005951 | 0.018532 | 0.010544 | -0.013742 | -0.0088248 | 0.063162 | 0.067093 | -8.0246 | 0.16479 | -121.9666 | 0.22888 | -121.3943 | -121.843 | -0.37994 | 0.14648 | 0.1831 | -121.9711 | -0.28381 | 0.032044 | 113.6581 | 121.9116 | -121.5271 | -0.28839 | 0.050354 | 113.942 | 121.3028 | 121.8292 | 0.28839 | 121.8475 | 113.6581 | 121.8658 | -0.16022 | -0.28839 | 121.8475 | 113.6581 | -0.16022 | 0.28839 | 121.8658 | -122.0993 | -122.1039
701.9219 | 121.9849 | -121.7148 | 0.15106 | -0.013581 | 0.018318 | 0.010758 | -0.006052 | -0.0066886 | 0.061026 | 0.068802 | -8.0795 | 0.19226 | -122.0673 | 0.13733 | -121.4905 | -121.9574 | -0.21515 | 0.068665 | 0.21057 | -121.9711 | -0.35248 | 0.041199 | 113.6353 | 121.8521 | -121.6415 | -0.25635 | 0.059509 | 113.9877 | 121.4996 | 121.7834 | 0.2243 | 121.907 | 113.6353 | 121.9254 | -0.24261 | -0.25635 | 121.907 | 113.6353 | -0.24261 | 0.2243 | 121.9254 | -122.2183 | -122.1222
703.6719 | 121.9345 | -121.7285 | 0.16937 | -0.005951 | 0.01725 | 0.01503 | -0.0084018 | -0.0045524 | 0.059957 | 0.072006 | -8.0978 | 0.20599 | -122.0398 | 0.091553 | -121.5408 | -122.0078 | -0.19684 | -0.022888 | 0.21057 | -121.9986 | -0.31128 | 0.036621 | 113.6307 | 121.8201 | -121.7102 | -0.27008 | 0.041198 | 113.942 | 121.5317 | 121.7056 | 0.18768 | 121.9345 | 113.6307 | 121.9391 | -0.27923 | -0.27008 | 121.9345 | 113.6307 | -0.27923 | 0.18768 | 121.9391 | -122.2092 | -122.168
705.4219 | 121.907 | -121.7422 | 0.17853 | 0.0016785 | 0.020241 | 0.012253 | -0.013315 | -0.006475 | 0.062948 | 0.067306 | -8.0246 | 0.15106 | -121.9986 | 0.20599 | -121.4218 | -121.8704 | -0.45776 | 0.086975 | 0.15564 | -121.9711 | -0.25635 | -0.027466 | 113.7177 | 121.9482 | -121.6003 | -0.22888 | -0.022888 | 113.974 | 121.2845 | 121.8292 | 0.32044 | 121.8933 | 113.7177 | 121.8979 | -0.12817 | -0.22888 | 121.8933 | 113.7177 | -0.12817 | 0.32044 | 121.8979 | -122.1771 | -122.1497
707.1406 | 122.0352 | -121.7102 | 0.10071 | -0.005951 | 0.019386 | 0.012681 | -0.01417 | -0.008184 | 0.062307 | 0.068588 | -8.139 | 0.20599 | -122.0398 | 0.091553 | -121.5042 | -121.9894 | -0.17395 | 0.027466 | 0.21973 | -122.0078 | -0.32959 | 0.10529 | 113.5712 | 121.8018 | -121.6049 | -0.29755 | 0.11902 | 113.9008 | 121.5363 | 121.7377 | 0.20599 | 121.9162 | 113.5712 | 121.9299 | -0.27924 | -0.29755 | 121.9162 | 113.5712 | -0.27924 | 0.20599 | 121.9299 | -122.1405 | -122.1085
708.875 | 121.994 | -121.7102 | 0.13275 | 0.009308 | 0.019386 | 0.012253 | -0.01417 | -0.010961 | 0.06423 | 0.070083 | -8.0521 | 0.18768 | -121.9666 | 0.2243 | -121.3898 | -121.8613 | -0.3891 | 0.14191 | 0.16022 | -121.9986 | -0.25635 | 0.054932 | 113.6581 | 121.9345 | -121.5225 | -0.28839 | 0.027466 | 113.9145 | 121.3211 | 121.8521 | 0.32043 | 121.8979 | 113.6581 | 121.8704 | -0.15106 | -0.28839 | 121.8979 | 113.6581 | -0.15106 | 0.32043 | 121.8704 | -122.0993 | -122.1313
710.5469 | 121.9116 | -121.7331 | 0.15564 | -0.005951 | 0.020027 | 0.018876 | -0.011179 | -0.0060478 | 0.06188 | 0.070724 | -8.0338 | 0.17853 | -121.9986 | 0.19684 | -121.431 | -121.8796 | -0.43945 | 0.07782 | 0.15564 | -121.9757 | -0.2655 | 0.022888 | 113.6993 | 121.9299 | -121.5866 | -0.24262 | 0 | 113.9648 | 121.2936 | 121.8109 | 0.30212 | 121.9116 | 113.6993 | 121.8887 | -0.14648 | -0.24262 | 121.9116 | 113.6993 | -0.14648 | 0.30212 | 121.8887 | -122.1542 | -122.1313
712.2812 | 121.9208 | -121.756 | 0.16937 | 0.0016785 | 0.019386 | 0.018448 | -0.007761 | -0.0073294 | 0.060598 | 0.069656 | -8.0566 | 0.20599 | -122.0535 | 0.16479 | -121.4676 | -121.9437 | -0.24719 | 0.082397 | 0.21057 | -121.9894 | -0.29755 | 0.036621 | 113.6993 | 121.9208 | -121.637 | -0.23346 | 0.041198 | 113.9969 | 121.5088 | 121.8384 | 0.28839 | 121.962 | 113.6993 | 121.9666 | -0.18768 | -0.23346 | 121.962 | 113.6993 | -0.18768 | 0.28839 | 121.9666 | -122.2229 | -122.1588
714 | 122.0306 | -121.6919 | 0.12817 | -0.005951 | 0.01725 | 0.012253 | -0.015451 | -0.007543 | 0.063376 | 0.069229 | -8.1253 | 0.16479 | -121.9803 | 0.17395 | -121.4218 | -121.8887 | -0.37994 | 0.07782 | 0.1831 | -121.9803 | -0.28839 | 0.036621 | 113.5666 | 121.8658 | -121.55 | -0.28839 | 0.054931 | 113.855 | 121.312 | 121.7697 | 0.27008 | 121.8567 | 113.5666 | 121.875 | -0.19684 | -0.28839 | 121.8567 | 113.5666 | -0.19684 | 0.27008 | 121.875 | -122.1085 | -122.1085
715.6875 | 121.9666 | -121.7422 | 0.16937 | -0.005951 | 0.019173 | 0.01503 | -0.0056248 | -0.0073294 | 0.060171 | 0.070297 | -8.1345 | 0.19684 | -122.0535 | 0.10529 | -121.55 | -122.0032 | -0.20142 | 0 | 0.21973 | -122.0032 | -0.31128 | 0.027465 | 113.6078 | 121.8475 | -121.7194 | -0.26093 | 0.050354 | 113.9191 | 121.5408 | 121.7422 | 0.19226 | 121.9391 | 113.6078 | 121.962 | -0.26093 | -0.26093 | 121.9391 | 113.6078 | -0.26093 | 0.19226 | 121.962 | -122.2229 | -122.1725
717.4375 | 122.0444 | -121.6965 | 0.13275 | 0.009308 | 0.018745 | 0.011185 | -0.011393 | -0.007543 | 0.061026 | 0.067947 | -8.1665 | 0.2243 | -122.0535 | 0.091553 | -121.5179 | -122.0078 | -0.14648 | 0.022888 | 0.23346 | -122.0261 | -0.35706 | 0.091553 | 113.53 | 121.788 | -121.6507 | -0.32959 | 0.10071 | 113.887 | 121.55 | 121.7194 | 0.17853 | 121.9208 | 113.53 | 121.9299 | -0.31128 | -0.32959 | 121.9208 | 113.53 | -0.31128 | 0.17853 | 121.9299 | -122.1863 | -122.1588
719.1875 | 121.907 | -121.7331 | 0.16937 | 0.009308 | 0.019173 | 0.011399 | -0.010324 | -0.0086112 | 0.062307 | 0.068374 | -8.0887 | 0.20142 | -122.0581 | 0.16479 | -121.4722 | -121.9482 | -0.2243 | 0.091553 | 0.19684 | -122.0032 | -0.32501 | 0.032043 | 113.6444 | 121.8979 | -121.6415 | -0.27008 | 0.027465 | 113.9694 | 121.5088 | 121.8246 | 0.26093 | 121.9345 | 113.6444 | 121.9299 | -0.21515 | -0.27008 | 121.9345 | 113.6444 | -0.21515 | 0.26093 | 121.9299 | -122.2275 | -122.1725
720.9375 | 122.0215 | -121.6782 | 0.12817 | -0.013581 | 0.019173 | 0.01738 | -0.013529 | -0.0073294 | 0.062094 | 0.069443 | -8.1573 | 0.21057 | -122.0581 | 0.10986 | -121.5134 | -121.9803 | -0.16479 | 0.041199 | 0.21973 | -121.994 | -0.37994 | 0.082397 | 113.5208 | 121.788 | -121.6415 | -0.31586 | 0.091553 | 113.9008 | 121.5134 | 121.7194 | 0.16479 | 121.8887 | 113.5208 | 121.8979 | -0.30212 | -0.31586 | 121.8887 | 113.5208 | -0.30212 | 0.16479 | 121.8979 | -122.1863 | -122.1222
722.6094 | 122.0398 | -121.6782 | 0.11902 | 0.0016785 | 0.0196 | 0.01738 | -0.012033 | -0.008184 | 0.062521 | 0.070938 | -8.1985 | 0.21515 | -122.0261 | 0.082397 | -121.5317 | -122.0032 | -0.14648 | 0.022888 | 0.21973 | -122.0261 | -0.3479 | 0.09613 | 113.4796 | 121.7606 | -121.6507 | -0.3479 | 0.10071 | 113.8275 | 121.5317 | 121.701 | 0.14648 | 121.8933 | 113.4796 | 121.8979 | -0.32501 | -0.3479 | 121.8933 | 113.4796 | -0.32501 | 0.14648 | 121.8979 | -122.1451 | -122.1451
724.3438 | 122.0215 | -121.7331 | 0.13733 | -0.005951 | 0.018105 | 0.0090491 | -0.015451 | -0.01032 | 0.062948 | 0.067306 | -8.1024 | 0.17395 | -121.9666 | 0.22888 | -121.3943 | -121.8475 | -0.40283 | 0.16022 | 0.18768 | -122.0078 | -0.23346 | 0.036621 | 113.6307 | 121.962 | -121.5317 | -0.27466 | 0.050354 | 113.8641 | 121.3303 | 121.8933 | 0.33875 | 121.907 | 113.6307 | 121.9208 | -0.11444 | -0.27466 | 121.907 | 113.6307 | -0.11444 | 0.33875 | 121.9208 | -122.1039 | -122.1451
726.0938 | 122.0169 | -121.6873 | 0.1236 | -0.005951 | 0.017036 | 0.0088355 | -0.018015 | -0.012243 | 0.062307 | 0.069656 | -8.139 | 0.17395 | -121.9894 | 0.18768 | -121.431 | -121.8796 | -0.35248 | 0.10071 | 0.18768 | -122.0078 | -0.30212 | 0.050354 | 113.5483 | 121.875 | -121.5546 | -0.32043 | 0.064087 | 113.8504 | 121.3348 | 121.788 | 0.25635 | 121.8613 | 113.5483 | 121.875 | -0.19226 | -0.32043 | 121.8613 | 113.5483 | -0.19226 | 0.25635 | 121.875 | -122.113 | -122.1313
727.8438 | 121.9894 | -121.701 | 0.14648 | -0.005951 | 0.023445 | 0.019089 | -0.0069064 | -0.0079704 | 0.062094 | 0.066879 | -8.1436 | 0.21057 | -122.0444 | 0.14648 | -121.4996 | -121.9757 | -0.18768 | 0.064087 | 0.20599 | -122.049 | -0.34332 | 0.064087 | 113.5574 | 121.8475 | -121.6461 | -0.3479 | 0.05951 | 113.9008 | 121.5134 | 121.7651 | 0.20142 | 121.9116 | 113.5574 | 121.907 | -0.27466 | -0.3479 | 121.9116 | 113.5574 | -0.27466 | 0.20142 | 121.907 | -122.1909 | -122.1954
729.5156 | 121.9025 | -121.7331 | 0.16022 | 0.0016785 | 0.015541 | 0.013108 | -0.00947 | -0.0049796 | 0.060812 | 0.068588 | -8.1161 | 0.16022 | -122.0123 | 0.19684 | -121.431 | -121.8842 | -0.42114 | 0.091553 | 0.17395 | -121.9528 | -0.27924 | 0 | 113.6169 | 121.9299 | -121.5912 | -0.21973 | 0.013733 | 113.8962 | 121.3119 | 121.8246 | 0.30212 | 121.8933 | 113.6169 | 121.907 | -0.15106 | -0.21973 | 121.8933 | 113.6169 | -0.15106 | 0.30212 | 121.907 | -122.1725 | -122.113
731.25 | 121.9299 | -121.7377 | 0.15106 | -0.005951 | 0.018745 | 0.018448 | -0.0056248 | -0.0077566 | 0.058462 | 0.070511 | -8.1116 | 0.19684 | -122.0627 | 0.13275 | -121.5179 | -121.9894 | -0.20142 | 0.050354 | 0.21515 | -122.0032 | -0.32501 | 0.045776 | 113.6261 | 121.8704 | -121.669 | -0.2655 | 0.064087 | 113.9511 | 121.5363 | 121.788 | 0.21973 | 121.9345 | 113.6261 | 121.9528 | -0.25177 | -0.2655 | 121.9345 | 113.6261 | -0.25177 | 0.21973 | 121.9528 | -122.2137 | -122.1542
733.0156 | 121.9391 | -121.7606 | 0.13733 | 0.0016785 | 0.020454 | 0.013749 | -0.006052 | -0.006475 | 0.061453 | 0.071579 | -8.1436 | 0.20599 | -122.0444 | 0.10529 | -121.5363 | -121.994 | -0.20599 | 0.004578 | 0.21515 | -122.0215 | -0.28381 | 0.068665 | 113.6169 | 121.8658 | -121.6736 | -0.26093 | 0.07782 | 113.9008 | 121.5546 | 121.7651 | 0.2243 | 121.9666 | 113.6169 | 121.9757 | -0.23346 | -0.26093 | 121.9666 | 113.6169 | -0.23346 | 0.2243 | 121.9757 | -122.1817 | -122.1588
734.7031 | 121.9162 | -121.7651 | 0.16022 | -0.013581 | 0.019386 | 0.017808 | -0.013102 | -0.0060478 | 0.062948 | 0.06987 | -8.107 | 0.17853 | -122.0032 | 0.21057 | -121.4218 | -121.8658 | -0.4303 | 0.10529 | 0.16937 | -122.0306 | -0.23804 | 0.018311 | 113.6581 | 121.9757 | -121.582 | -0.2655 | 0.009156 | 113.8962 | 121.3348 | 121.8704 | 0.34332 | 121.9437 | 113.6581 | 121.9345 | -0.10071 | -0.2655 | 121.9437 | 113.6581 | -0.10071 | 0.34332 | 121.9345 | -122.1634 | -122.1909
736.4531 | 121.9208 | -121.7606 | 0.16479 | 0.0016785 | 0.021095 | 0.013321 | -0.0073336 | -0.0086112 | 0.061239 | 0.067947 | -8.1299 | 0.20142 | -122.0535 | 0.15106 | -121.5088 | -121.9574 | -0.21515 | 0.073242 | 0.21057 | -122.0215 | -0.29297 | 0.036621 | 113.6307 | 121.9116 | -121.6736 | -0.26093 | 0.045776 | 113.9236 | 121.5454 | 121.8338 | 0.25177 | 121.962 | 113.6307 | 121.9711 | -0.19684 | -0.26093 | 121.962 | 113.6307 | -0.19684 | 0.25177 | 121.9711 | -122.2183 | -122.1863
738.2031 | 121.9208 | -121.7468 | 0.16022 | -0.005951 | 0.018318 | 0.011185 | -0.00947 | -0.0088248 | 0.059957 | 0.070297 | -8.1436 | 0.21057 | -122.0352 | 0.14191 | -121.4722 | -121.9391 | -0.2243 | 0.082397 | 0.20599 | -121.9757 | -0.28839 | 0.050354 | 113.6032 | 121.8887 | -121.6324 | -0.22888 | 0.045777 | 113.8916 | 121.5225 | 121.8292 | 0.27466 | 121.9574 | 113.6032 | 121.9528 | -0.19226 | -0.22888 | 121.9574 | 113.6032 | -0.19226 | 0.27466 | 121.9528 | -122.1954 | -122.1359
739.9531 | 121.962 | -121.7468 | 0.15106 | -0.013581 | 0.020027 | 0.013535 | -0.008829 | -0.0069022 | 0.062735 | 0.068802 | -8.2352 | 0.20599 | -122.0398 | 0.059509 | -121.5546 | -122.0261 | -0.18768 | -0.022888 | 0.21515 | -122.049 | -0.29297 | 0.054932 | 113.5117 | 121.8063 | -121.7056 | -0.30212 | 0.064087 | 113.8046 | 121.5591 | 121.7239 | 0.19226 | 121.9528 | 113.5117 | 121.962 | -0.27924 | -0.30212 | 121.9528 | 113.5117 | -0.27924 | 0.19226 | 121.962 | -122.1909 | -122.2
741.625 | 121.9254 | -121.7468 | 0.15106 | -0.013581 | 0.017677 | 0.013108 | -0.0092564 | -0.006475 | 0.062735 | 0.071151 | -8.194 | 0.19684 | -122.049 | 0.10986 | -121.5179 | -121.9986 | -0.20599 | 0.009155 | 0.21057 | -122.0261 | -0.30212 | 0.045776 | 113.5529 | 121.8567 | -121.669 | -0.27924 | 0.059509 | 113.855 | 121.5408 | 121.756 | 0.22888 | 121.9437 | 113.5529 | 121.9574 | -0.25177 | -0.27924 | 121.9437 | 113.5529 | -0.25177 | 0.22888 | 121.9574 | -122.2 | -122.1771
743.3594 | 121.9894 | -121.7239 | 0.14191 | -0.02121 | 0.017464 | 0.013535 | -0.012033 | -0.0060478 | 0.061666 | 0.068802 | -8.2535 | 0.21515 | -122.049 | 0.068665 | -121.5729 | -122.0169 | -0.20142 | -0.032043 | 0.23804 | -122.0352 | -0.32501 | 0.073242 | 113.4705 | 121.7926 | -121.7148 | -0.31128 | 0.09613 | 113.7955 | 121.5225 | 121.6919 | 0.15106 | 121.9391 | 113.4705 | 121.962 | -0.29297 | -0.31128 | 121.9391 | 113.4705 | -0.29297 | 0.15106 | 121.962 | -122.1909 | -122.1771
745.0938 | 121.9528 | -121.7468 | 0.16022 | -0.005951 | 0.018532 | 0.013749 | -0.011393 | -0.0069022 | 0.062948 | 0.072006 | -8.226 | 0.21057 | -122.0261 | 0.073242 | -121.5591 | -122.0169 | -0.19684 | -0.018311 | 0.23346 | -122.0032 | -0.27924 | 0.050354 | 113.5208 | 121.8201 | -121.7194 | -0.25635 | 0.073242 | 113.8 | 121.55 | 121.7285 | 0.18768 | 121.9574 | 113.5208 | 121.9803 | -0.27008 | -0.25635 | 121.9574 | 113.5208 | -0.27008 | 0.18768 | 121.9803 | -122.1863 | -122.1634
746.8281 | 122.0673 | -121.7056 | 0.12817 | -0.02121 | 0.0196 | 0.0096899 | -0.015665 | -0.0079704 | 0.063162 | 0.068161 | -8.2352 | 0.19226 | -122.0169 | 0.086975 | -121.5225 | -121.9757 | -0.17395 | 0.054932 | 0.20599 | -122.049 | -0.31128 | 0.064087 | 113.4705 | 121.7926 | -121.6507 | -0.34332 | 0.07782 | 113.7817 | 121.5317 | 121.7606 | 0.18311 | 121.8979 | 113.4705 | 121.9116 | -0.27008 | -0.34332 | 121.8979 | 113.4705 | -0.27008 | 0.18311 | 121.9116 | -122.1451 | -122.1771
748.5156 | 121.9894 | -121.7239 | 0.12817 | -0.005951 | 0.017891 | 0.010117 | -0.014597 | -0.007543 | 0.06423 | 0.069229 | -8.2443 | 0.20599 | -121.9986 | 0.14648 | -121.4676 | -121.9162 | -0.37079 | 0.032043 | 0.18768 | -122.0306 | -0.27466 | 0.07782 | 113.4796 | 121.8704 | -121.5958 | -0.3067 | 0.059509 | 113.7543 | 121.3531 | 121.756 | 0.25635 | 121.9299 | 113.4796 | 121.9116 | -0.19226 | -0.3067 | 121.9299 | 113.4796 | -0.19226 | 0.25635 | 121.9116 | -122.1268 | -122.1588
750.25 | 121.9803 | -121.7285 | 0.15106 | -0.013581 | 0.019173 | 0.016526 | -0.0081882 | -0.0045524 | 0.06188 | 0.070724 | -8.2535 | 0.21057 | -122.0856 | 0.073242 | -121.5591 | -122.0078 | -0.21057 | -0.036621 | 0.21057 | -122.0078 | -0.35706 | 0.059509 | 113.475 | 121.8018 | -121.7102 | -0.27923 | 0.059509 | 113.8321 | 121.5179 | 121.6919 | 0.16937 | 121.9391 | 113.475 | 121.9391 | -0.27923 | -0.27923 | 121.9391 | 113.475 | -0.27923 | 0.16937 | 121.9391 | -122.2366 | -122.1588
751.9375 | 121.9528 | -121.7514 | 0.15106 | -0.013581 | 0.020882 | 0.011399 | -0.0079746 | -0.0069022 | 0.062094 | 0.069656 | -8.2169 | 0.20142 | -122.0673 | 0.11444 | -121.5408 | -122.0078 | -0.19684 | 0.013733 | 0.23346 | -121.994 | -0.31586 | 0.050354 | 113.5345 | 121.8658 | -121.6919 | -0.24262 | 0.082397 | 113.8504 | 121.5546 | 121.7651 | 0.21057 | 121.9528 | 113.5345 | 121.9849 | -0.25635 | -0.24262 | 121.9528 | 113.5345 | -0.25635 | 0.21057 | 121.9849 | -122.2183 | -122.1451
753.6719 | 121.962 | -121.7422 | 0.15106 | -0.005951 | 0.019173 | 0.016739 | -0.0092564 | -0.006475 | 0.060171 | 0.070938 | -8.2352 | 0.21057 | -122.0673 | 0.091553 | -121.55 | -122.0169 | -0.20142 | -0.013733 | 0.21973 | -122.0169 | -0.32501 | 0.059509 | 113.5071 | 121.8338 | -121.701 | -0.27466 | 0.068665 | 113.8321 | 121.5408 | 121.7285 | 0.19226 | 121.9528 | 113.5071 | 121.962 | -0.27466 | -0.27466 | 121.9528 | 113.5071 | -0.27466 | 0.19226 | 121.962 | -122.2183 | -122.168
755.4219 | 121.9162 | -121.7743 | 0.16937 | 0.009308 | 0.018959 | 0.012894 | -0.008829 | -0.0071158 | 0.062948 | 0.070511 | -8.1985 | 0.20599 | -122.0627 | 0.15564 | -121.4951 | -121.962 | -0.25177 | 0.082397 | 0.21973 | -122.0306 | -0.28839 | 0.036621 | 113.5757 | 121.9299 | -121.6644 | -0.25635 | 0.050354 | 113.8641 | 121.5225 | 121.8567 | 0.27924 | 121.9803 | 113.5757 | 121.994 | -0.18768 | -0.25635 | 121.9803 | 113.5757 | -0.18768 | 0.27924 | 121.994 | -122.2321 | -122.2
757.1562 | 122.0398 | -121.7331 | 0.1236 | -0.005951 | 0.016823 | 0.010544 | -0.016947 | -0.0066886 | 0.064444 | 0.066879 | -8.2077 | 0.17853 | -121.9894 | 0.21515 | -121.4035 | -121.8842 | -0.36621 | 0.14191 | 0.1831 | -122.0306 | -0.25635 | 0.054932 | 113.5254 | 121.9482 | -121.5271 | -0.29755 | 0.059509 | 113.7817 | 121.3669 | 121.875 | 0.32959 | 121.9116 | 113.5254 | 121.9162 | -0.15106 | -0.29755 | 121.9116 | 113.5254 | -0.15106 | 0.32959 | 121.9162 | -122.113 | -122.1542
758.8906 | 122.0078 | -121.7194 | 0.15106 | 0.0016785 | 0.017891 | 0.014817 | -0.0084018 | -0.0077566 | 0.061026 | 0.070083 | -8.2443 | 0.19226 | -122.0627 | 0.14191 | -121.4996 | -121.9711 | -0.19684 | 0.073242 | 0.2243 | -122.0398 | -0.34332 | 0.041199 | 113.475 | 121.8613 | -121.6507 | -0.32044 | 0.073242 | 113.8184 | 121.5225 | 121.7926 | 0.21973 | 121.9116 | 113.475 | 121.9437 | -0.25177 | -0.32044 | 121.9116 | 113.475 | -0.25177 | 0.21973 | 121.9437 | -122.2137 | -122.1909
760.5625 | 121.9574 | -121.7606 | 0.14648 | 0.0016785 | 0.018959 | 0.01439 | -0.013956 | -0.009893 | 0.064016 | 0.070938 | -8.2306 | 0.17395 | -122.0123 | 0.17853 | -121.4905 | -121.9162 | -0.41199 | 0.045776 | 0.16022 | -122.0261 | -0.25177 | 0.027466 | 113.53 | 121.9391 | -121.637 | -0.2655 | 0.013733 | 113.7817 | 121.3486 | 121.8063 | 0.27008 | 121.9345 | 113.53 | 121.9208 | -0.15564 | -0.2655 | 121.9345 | 113.53 | -0.15564 | 0.27008 | 121.9208 | -122.1588 | -122.1725
762.2969 | 122.0078 | -121.7148 | 0.14648 | -0.005951 | 0.015755 | 0.0096899 | -0.01417 | -0.010961 | 0.061453 | 0.068588 | -8.2169 | 0.16479 | -122.0078 | 0.20142 | -121.4493 | -121.9162 | -0.31128 | 0.12817 | 0.1831 | -122.0352 | -0.29297 | 0.018311 | 113.4979 | 121.9162 | -121.5958 | -0.32043 | 0.036621 | 113.7909 | 121.4035 | 121.843 | 0.2655 | 121.8796 | 113.4979 | 121.8979 | -0.20142 | -0.32043 | 121.8796 | 113.4979 | -0.20142 | 0.2655 | 121.8979 | -122.1542 | -122.1817
763.9688 | 122.0718 | -121.7102 | 0.13733 | 0.009308 | 0.018532 | 0.015885 | -0.011179 | -0.0079704 | 0.062094 | 0.068161 | -8.3176 | 0.2243 | -122.081 | 0.09613 | -121.5408 | -122.0306 | -0.14191 | 0.009155 | 0.2243 | -122.0398 | -0.37079 | 0.086975 | 113.3926 | 121.8063 | -121.6782 | -0.32959 | 0.086975 | 113.7634 | 121.5683 | 121.7194 | 0.16937 | 121.9345 | 113.3926 | 121.9345 | -0.32044 | -0.32959 | 121.9345 | 113.3926 | -0.32044 | 0.16937 | 121.9345 | -122.2183 | -122.1771
765.7188 | 121.9391 | -121.7606 | 0.16022 | -0.005951 | 0.019386 | 0.011399 | -0.0064792 | -0.0069022 | 0.061666 | 0.068802 | -8.2397 | 0.18768 | -122.0673 | 0.15106 | -121.5225 | -122.0078 | -0.21515 | 0.041199 | 0.21057 | -122.0123 | -0.3067 | 0.027466 | 113.5208 | 121.9116 | -121.6827 | -0.25177 | 0.050354 | 113.8275 | 121.5454 | 121.8018 | 0.23804 | 121.9482 | 113.5208 | 121.9711 | -0.24719 | -0.25177 | 121.9482 | 113.5208 | -0.24719 | 0.23804 | 121.9711 | -122.2275 | -122.1725
767.4531 | 122.0215 | -121.7239 | 0.14191 | -0.005951 | 0.017464 | 0.0088355 | -0.014383 | -0.009893 | 0.063162 | 0.068588 | -8.2306 | 0.17395 | -121.9803 | 0.20142 | -121.431 | -121.8979 | -0.35706 | 0.12817 | 0.18768 | -122.0261 | -0.25635 | 0.032043 | 113.4933 | 121.9254 | -121.5729 | -0.30212 | 0.045776 | 113.7497 | 121.3669 | 121.8521 | 0.29297 | 121.8979 | 113.4933 | 121.9116 | -0.17395 | -0.30212 | 121.8979 | 113.4933 | -0.17395 | 0.29297 | 121.9116 | -122.1222 | -122.168
769.1875 | 122.0398 | -121.7056 | 0.10529 | 0.0016785 | 0.020241 | 0.012894 | -0.015238 | -0.009893 | 0.064444 | 0.068161 | -8.2901 | 0.17853 | -122.0078 | 0.12817 | -121.4905 | -121.9437 | -0.35706 | 0.018311 | 0.16937 | -122.0261 | -0.30212 | 0.073242 | 113.4155 | 121.8338 | -121.5958 | -0.32043 | 0.064087 | 113.7177 | 121.3486 | 121.7239 | 0.21515 | 121.8842 | 113.4155 | 121.875 | -0.23804 | -0.32043 | 121.8842 | 113.4155 | -0.23804 | 0.21515 | 121.875 | -122.113 | -122.1313
770.9375 | 122.0352 | -121.701 | 0.12817 | -0.013581 | 0.0196 | 0.0099037 | -0.014811 | -0.0077566 | 0.063589 | 0.06987 | -8.2718 | 0.1831 | -122.0032 | 0.19226 | -121.4355 | -121.8887 | -0.38452 | 0.09613 | 0.17395 | -122.0123 | -0.30212 | 0.054931 | 113.4293 | 121.8933 | -121.5637 | -0.31128 | 0.045776 | 113.7314 | 121.3165 | 121.7972 | 0.2655 | 121.8842 | 113.4293 | 121.875 | -0.18768 | -0.31128 | 121.8842 | 113.4293 | -0.18768 | 0.2655 | 121.875 | -122.1313 | -122.1405
772.6094 | 121.9254 | -121.7697 | 0.16937 | -0.005951 | 0.019813 | 0.012894 | -0.010965 | -0.009252 | 0.063376 | 0.069443 | -8.2214 | 0.15106 | -122.0398 | 0.21973 | -121.4401 | -121.8887 | -0.44403 | 0.091553 | 0.16022 | -122.0169 | -0.27008 | -0.018311 | 113.5483 | 121.9894 | -121.6095 | -0.24719 | -0.009156 | 113.8184 | 121.3257 | 121.8613 | 0.32959 | 121.9208 | 113.5483 | 121.9299 | -0.11902 | -0.24719 | 121.9208 | 113.5483 | -0.11902 | 0.32959 | 121.9299 | -122.2092 | -122.1863
774.3438 | 121.9757 | -121.7514 | 0.14648 | -0.005951 | 0.018959 | 0.013962 | -0.0081882 | -0.009252 | 0.063589 | 0.071579 | -8.3084 | 0.21515 | -122.1039 | 0.10071 | -121.5683 | -122.0261 | -0.23804 | -0.036621 | 0.21973 | -122.0535 | -0.35248 | 0.068665 | 113.443 | 121.8521 | -121.7148 | -0.30212 | 0.073243 | 113.7955 | 121.5134 | 121.7148 | 0.18311 | 121.9666 | 113.443 | 121.9711 | -0.27466 | -0.30212 | 121.9666 | 113.443 | -0.27466 | 0.18311 | 121.9711 | -122.2504 | -122.2
776.0938 | 122.1085 | -121.7239 | 0.12817 | -0.005951 | 0.019173 | 0.011185 | -0.010324 | -0.009252 | 0.063376 | 0.067093 | -8.3542 | 0.19226 | -122.0673 | 0.10986 | -121.5546 | -122.0215 | -0.16479 | 0.009155 | 0.21057 | -122.0673 | -0.34332 | 0.064087 | 113.3698 | 121.8338 | -121.6827 | -0.34332 | 0.082397 | 113.7131 | 121.5591 | 121.7331 | 0.16937 | 121.9162 | 113.3698 | 121.9345 | -0.29755 | -0.34332 | 121.9162 | 113.3698 | -0.29755 | 0.16937 | 121.9345 | -122.1954 | -122.1954
777.8281 | 122.0169 | -121.7239 | 0.09613 | -0.005951 | 0.018105 | 0.014176 | -0.016519 | -0.0096794 | 0.066153 | 0.067947 | -8.2718 | 0.1831 | -122.0078 | 0.21515 | -121.4172 | -121.8796 | -0.39825 | 0.1236 | 0.19226 | -122.0215 | -0.28381 | 0.086975 | 113.4521 | 121.9391 | -121.5134 | -0.29755 | 0.096131 | 113.736 | 121.3257 | 121.8475 | 0.3067 | 121.907 | 113.4521 | 121.9162 | -0.15564 | -0.29755 | 121.907 | 113.4521 | -0.15564 | 0.3067 | 121.9162 | -122.1039 | -122.1176
779.5156 | 122.0398 | -121.7285 | 0.12817 | -0.013581 | 0.019813 | 0.011826 | -0.01182 | -0.0077566 | 0.063376 | 0.068374 | -8.2855 | 0.20142 | -122.0352 | 0.18768 | -121.463 | -121.9437 | -0.25635 | 0.07782 | 0.20142 | -122.0306 | -0.3067 | 0.073242 | 113.443 | 121.9162 | -121.5912 | -0.30212 | 0.073242 | 113.7497 | 121.4722 | 121.8063 | 0.2655 | 121.9299 | 113.443 | 121.9299 | -0.21515 | -0.30212 | 121.9299 | 113.443 | -0.21515 | 0.2655 | 121.9299 | -122.1634 | -122.1588
781.2656 | 121.9299 | -121.7377 | 0.14648 | -0.005951 | 0.0196 | 0.013535 | -0.0084018 | -0.005834 | 0.061453 | 0.068161 | -8.3267 | 0.19684 | -122.0627 | 0.15564 | -121.4951 | -121.9299 | -0.38452 | 0.036621 | 0.21515 | -122.0078 | -0.32501 | 0.050354 | 113.411 | 121.8933 | -121.6415 | -0.27008 | 0.068665 | 113.736 | 121.3531 | 121.7743 | 0.24262 | 121.9345 | 113.411 | 121.9528 | -0.19226 | -0.27008 | 121.9345 | 113.411 | -0.19226 | 0.24262 | 121.9528 | -122.2092 | -122.1542
783 | 121.9574 | -121.7514 | 0.16022 | -0.013581 | 0.018105 | 0.014603 | -0.0081882 | -0.0077566 | 0.062307 | 0.068588 | -8.3405 | 0.20142 | -122.0673 | 0.082397 | -121.5546 | -121.9849 | -0.28381 | -0.036621 | 0.21515 | -121.9986 | -0.31586 | 0.041199 | 113.4109 | 121.8338 | -121.7148 | -0.24719 | 0.054932 | 113.7268 | 121.4676 | 121.7148 | 0.19684 | 121.9528 | 113.4109 | 121.9666 | -0.23346 | -0.24719 | 121.9528 | 113.4109 | -0.23346 | 0.19684 | 121.9666 | -122.2275 | -122.1588
784.6719 | 121.9528 | -121.756 | 0.16022 | -0.013581 | 0.020027 | 0.016312 | -0.010111 | -0.0071158 | 0.063589 | 0.068802 | -8.2901 | 0.20599 | -122.0535 | 0.15106 | -121.5134 | -121.9849 | -0.22888 | 0.091553 | 0.2243 | -122.0306 | -0.29755 | 0.045777 | 113.4659 | 121.907 | -121.6736 | -0.27466 | 0.064087 | 113.7634 | 121.5271 | 121.8475 | 0.24261 | 121.962 | 113.4659 | 121.9803 | -0.22888 | -0.27466 | 121.962 | 113.4659 | -0.22888 | 0.24261 | 121.9803 | -122.2137 | -122.1909
786.4219 | 121.9757 | -121.7422 | 0.14648 | -0.005951 | 0.01725 | 0.016312 | -0.0075474 | -0.0066886 | 0.062948 | 0.069443 | -8.3542 | 0.21057 | -122.0535 | 0.068665 | -121.5683 | -122.0444 | -0.19226 | -0.050354 | 0.21515 | -122.0444 | -0.31128 | 0.064087 | 113.3881 | 121.8109 | -121.7148 | -0.30212 | 0.068665 | 113.6993 | 121.55 | 121.6919 | 0.17395 | 121.9528 | 113.3881 | 121.9574 | -0.30212 | -0.30212 | 121.9528 | 113.3881 | -0.30212 | 0.17395 | 121.9574 | -122.2 | -122.1909
788.1719 | 121.9391 | -121.6827 | 0.14191 | 0.0016785 | 0.020454 | 0.010972 | -0.010538 | -0.0069022 | 0.063376 | 0.068802 | -8.3542 | 0.19226 | -122.0032 | 0.064087 | -121.5179 | -121.9757 | -0.21973 | -0.041199 | 0.18768 | -121.9849 | -0.32044 | 0.050354 | 113.3286 | 121.7468 | -121.6599 | -0.30212 | 0.045776 | 113.649 | 121.463 | 121.6415 | 0.16479 | 121.875 | 113.3286 | 121.8704 | -0.29297 | -0.30212 | 121.875 | 113.3286 | -0.29297 | 0.16479 | 121.8704 | -122.1451 | -122.1268
789.9219 | 122.0215 | -121.6461 | 0.11444 | -0.013581 | 0.017036 | 0.0092627 | -0.019724 | -0.010961 | 0.063162 | 0.070511 | -8.3771 | 0.17395 | -121.994 | 0.11444 | -121.463 | -121.907 | -0.3479 | 0.004578 | 0.16937 | -121.9986 | -0.3479 | 0.059509 | 113.269 | 121.7606 | -121.5775 | -0.35248 | 0.054932 | 113.6169 | 121.2982 | 121.6507 | 0.1831 | 121.8201 | 113.269 | 121.8155 | -0.26093 | -0.35248 | 121.8201 | 113.269 | -0.26093 | 0.1831 | 121.8155 | -122.1085 | -122.113
791.5938 | 121.9162 | -121.7194 | 0.16022 | 0.0016785 | 0.019813 | 0.015458 | -0.00712 | -0.008184 | 0.061666 | 0.068374 | -8.313 | 0.16937 | -122.0398 | 0.1236 | -121.4996 | -121.962 | -0.21057 | 0.036621 | 0.19684 | -122.0123 | -0.32044 | 0.009156 | 113.4064 | 121.843 | -121.6599 | -0.29297 | 0.036621 | 113.7268 | 121.5088 | 121.756 | 0.21973 | 121.8887 | 113.4064 | 121.9162 | -0.24262 | -0.29297 | 121.8887 | 113.4064 | -0.24262 | 0.21973 | 121.9162 | -122.2 | -122.1725
793.3281 | 121.9025 | -121.7285 | 0.13733 | -0.013581 | 0.016823 | 0.011826 | -0.012461 | -0.0062614 | 0.062521 | 0.070511 | -8.3176 | 0.14648 | -122.0032 | 0.17853 | -121.4493 | -121.8613 | -0.43488 | 0.068665 | 0.16937 | -121.9803 | -0.27466 | 0.009155 | 113.4109 | 121.907 | -121.5866 | -0.25177 | 0.032044 | 113.6856 | 121.2936 | 121.7972 | 0.27924 | 121.875 | 113.4109 | 121.8979 | -0.13275 | -0.25177 | 121.875 | 113.4109 | -0.13275 | 0.27924 | 121.8979 | -122.1405 | -122.1176
795 | 121.907 | -121.7514 | 0.13733 | 0.0016785 | 0.02195 | 0.013108 | -0.011393 | -0.0060478 | 0.060812 | 0.068374 | -8.345 | 0.17853 | -122.0169 | 0.16479 | -121.4584 | -121.907 | -0.3891 | 0.068665 | 0.16479 | -121.9803 | -0.2655 | 0.041199 | 113.4064 | 121.9162 | -121.5958 | -0.22888 | 0.027466 | 113.6719 | 121.3623 | 121.8201 | 0.29297 | 121.9299 | 113.4064 | 121.9162 | -0.15564 | -0.22888 | 121.9299 | 113.4064 | -0.15564 | 0.29297 | 121.9162 | -122.1542 | -122.1176
796.7344 | 122.0261 | -121.7148 | 0.11444 | -0.005951 | 0.019173 | 0.011399 | -0.017588 | -0.010534 | 0.06658 | 0.069443 | -8.3954 | 0.16022 | -121.9894 | 0.15106 | -121.463 | -121.9254 | -0.35706 | 0.050354 | 0.16937 | -122.0123 | -0.27466 | 0.045776 | 113.3194 | 121.8658 | -121.5775 | -0.29755 | 0.054932 | 113.5941 | 121.3577 | 121.7651 | 0.25177 | 121.875 | 113.3194 | 121.8842 | -0.21057 | -0.29755 | 121.875 | 113.3194 | -0.21057 | 0.25177 | 121.8842 | -122.1039 | -122.1268
798.4688 | 121.994 | -121.7239 | 0.11444 | -0.013581 | 0.020668 | 0.013321 | -0.014597 | -0.0096794 | 0.062735 | 0.069229 | -8.3908 | 0.17853 | -122.0078 | 0.14191 | -121.4859 | -121.9299 | -0.38452 | 0.022888 | 0.17395 | -122.0261 | -0.28381 | 0.064087 | 113.3331 | 121.8658 | -121.6003 | -0.30212 | 0.059509 | 113.6169 | 121.3394 | 121.7468 | 0.23804 | 121.9025 | 113.3331 | 121.8979 | -0.20599 | -0.30212 | 121.9025 | 113.3331 | -0.20599 | 0.23804 | 121.8979 | -122.1222 | -122.1405
800.2031 | 122.0352 | -121.6873 | 0.10529 | -0.005951 | 0.015968 | 0.010544 | -0.014383 | -0.010107 | 0.062948 | 0.069229 | -8.4229 | 0.16022 | -122.0581 | 0.13733 | -121.4951 | -121.9208 | -0.35706 | 0.041199 | 0.18768 | -121.9849 | -0.37079 | 0.054931 | 113.2645 | 121.8246 | -121.6003 | -0.29755 | 0.082397 | 113.6353 | 121.3303 | 121.7285 | 0.19226 | 121.8475 | 113.2645 | 121.875 | -0.23346 | -0.29755 | 121.8475 | 113.2645 | -0.23346 | 0.19226 | 121.875 | -122.1634 | -122.0901
801.9375 | 121.9482 | -121.7606 | 0.13275 | 0.0016785 | 0.017891 | 0.012253 | -0.0045566 | -0.0088248 | 0.061453 | 0.069656 | -8.3633 | 0.19684 | -122.0581 | 0.10529 | -121.55 | -122.0169 | -0.2243 | 0.004578 | 0.19226 | -122.0261 | -0.29755 | 0.064087 | 113.3972 | 121.8658 | -121.6827 | -0.2655 | 0.05951 | 113.6948 | 121.5363 | 121.7651 | 0.21057 | 121.9574 | 113.3972 | 121.9528 | -0.25635 | -0.2655 | 121.9574 | 113.3972 | -0.25635 | 0.21057 | 121.9528 | -122.1909 | -122.1588
803.625 | 121.9528 | -121.7422 | 0.12817 | -0.005951 | 0.020241 | 0.016739 | -0.0062656 | -0.008184 | 0.062094 | 0.06987 | -8.3908 | 0.21057 | -122.081 | 0.086975 | -121.5591 | -122.0215 | -0.22888 | -0.032043 | 0.19684 | -122.0169 | -0.33875 | 0.082397 | 113.3514 | 121.8292 | -121.6873 | -0.27466 | 0.068664 | 113.6902 | 121.5134 | 121.7102 | 0.18311 | 121.9528 | 113.3514 | 121.9391 | -0.27923 | -0.27466 | 121.9528 | 113.3514 | -0.27923 | 0.18311 | 121.9391 | -122.2092 | -122.1451
805.375 | 121.9711 | -121.7422 | 0.13733 | 0.0016785 | 0.019386 | 0.0096899 | -0.0073336 | -0.0069022 | 0.063162 | 0.070938 | -8.4274 | 0.21973 | -122.0718 | 0.07782 | -121.5683 | -122.0169 | -0.23346 | -0.022888 | 0.20142 | -122.0123 | -0.32959 | 0.082398 | 113.3148 | 121.8201 | -121.7056 | -0.27008 | 0.064087 | 113.6444 | 121.5088 | 121.7194 | 0.17395 | 121.962 | 113.3148 | 121.9437 | -0.27466 | -0.27008 | 121.962 | 113.3148 | -0.27466 | 0.17395 | 121.9437 | -122.2092 | -122.1497
807.1094 | 121.9208 | -121.756 | 0.14191 | -0.013581 | 0.019813 | 0.012467 | -0.0084018 | -0.0051932 | 0.062521 | 0.06987 | -8.3725 | 0.21057 | -122.0673 | 0.14648 | -121.4951 | -121.9803 | -0.21515 | 0.09613 | 0.19684 | -122.0078 | -0.31128 | 0.068664 | 113.3835 | 121.9025 | -121.637 | -0.25177 | 0.054931 | 113.6948 | 121.5408 | 121.8521 | 0.26093 | 121.9666 | 113.3835 | 121.9528 | -0.22431 | -0.25177 | 121.9666 | 113.3835 | -0.22431 | 0.26093 | 121.9528 | -122.2092 | -122.1497
808.8438 | 121.9162 | -121.7834 | 0.13733 | -0.005951 | 0.020027 | 0.01439 | -0.010752 | -0.0062614 | 0.062094 | 0.069229 | -8.3633 | 0.19226 | -122.049 | 0.14648 | -121.4951 | -121.9666 | -0.22888 | 0.09613 | 0.20142 | -122.0261 | -0.2655 | 0.054932 | 113.4201 | 121.9299 | -121.6324 | -0.24262 | 0.064087 | 113.6856 | 121.5546 | 121.8796 | 0.28839 | 121.9757 | 113.4201 | 121.9849 | -0.18311 | -0.24262 | 121.9757 | 113.4201 | -0.18311 | 0.28839 | 121.9849 | -122.1863 | -122.1634
810.5312 | 122.0398 | -121.7239 | 0.1236 | -0.005951 | 0.019386 | 0.013108 | -0.013742 | -0.0094656 | 0.063162 | 0.069443 | -8.4091 | 0.1831 | -122.0215 | 0.12817 | -121.4951 | -121.9803 | -0.2243 | 0.073242 | 0.20599 | -122.0398 | -0.29755 | 0.059509 | 113.3148 | 121.8521 | -121.6187 | -0.31586 | 0.082398 | 113.6124 | 121.4996 | 121.7972 | 0.22888 | 121.907 | 113.3148 | 121.9299 | -0.25635 | -0.31586 | 121.907 | 113.3148 | -0.25635 | 0.22888 | 121.9299 | -122.1451 | -122.1634
812.2656 | 121.9025 | -121.756 | 0.15564 | 0.0016785 | 0.018532 | 0.018662 | -0.010538 | -0.007543 | 0.06188 | 0.067947 | -8.3633 | 0.15564 | -122.0306 | 0.17853 | -121.4539 | -121.8933 | -0.40741 | 0.07782 | 0.16479 | -122.0078 | -0.27466 | 0 | 113.3926 | 121.9345 | -121.6095 | -0.25177 | 0.009155 | 113.6673 | 121.3486 | 121.8338 | 0.30212 | 121.9116 | 113.3926 | 121.9208 | -0.13733 | -0.25177 | 121.9116 | 113.3926 | -0.13733 | 0.30212 | 121.9208 | -122.1863 | -122.1634
813.9375 | 122.0398 | -121.7056 | 0.11444 | -0.005951 | 0.019386 | 0.012253 | -0.01716 | -0.010534 | 0.067007 | 0.069015 | -8.4732 | 0.16937 | -121.994 | 0.1236 | -121.4813 | -121.9345 | -0.36621 | 0.041199 | 0.17853 | -122.0398 | -0.28839 | 0.054932 | 113.2324 | 121.8292 | -121.5958 | -0.33417 | 0.064087 | 113.5208 | 121.3394 | 121.7468 | 0.2243 | 121.875 | 113.2324 | 121.8842 | -0.22888 | -0.33417 | 121.875 | 113.2324 | -0.22888 | 0.2243 | 121.8842 | -122.1085 | -122.1542
815.6719 | 122.0123 | -121.7285 | 0.13275 | -0.013581 | 0.017677 | 0.012253 | -0.013742 | -0.0073294 | 0.063589 | 0.068588 | -8.3862 | 0.1831 | -122.0032 | 0.20142 | -121.431 | -121.8933 | -0.34332 | 0.15106 | 0.17395 | -122.0352 | -0.27466 | 0.050354 | 113.3423 | 121.9299 | -121.5637 | -0.3067 | 0.041199 | 113.6169 | 121.3852 | 121.8796 | 0.29755 | 121.9116 | 113.3423 | 121.9025 | -0.16479 | -0.3067 | 121.9116 | 113.3423 | -0.16479 | 0.29755 | 121.9025 | -122.1359 | -122.168
817.4062 | 121.9757 | -121.756 | 0.13733 | -0.013581 | 0.020027 | 0.014603 | -0.0051974 | -0.0096794 | 0.062094 | 0.070724 | -8.4641 | 0.21057 | -122.0993 | 0.082397 | -121.5683 | -122.0444 | -0.2243 | -0.041199 | 0.19684 | -122.0261 | -0.34332 | 0.073242 | 113.2919 | 121.8384 | -121.7056 | -0.27008 | 0.059509 | 113.6353 | 121.5317 | 121.7148 | 0.18768 | 121.9666 | 113.2919 | 121.9528 | -0.28839 | -0.27008 | 121.9666 | 113.2919 | -0.28839 | 0.18768 | 121.9528 | -122.2366 | -122.1634
819.0938 | 121.9574 | -121.7606 | 0.11902 | 0.009308 | 0.021309 | 0.01439 | -0.0081882 | -0.0060478 | 0.063162 | 0.07222 | -8.4869 | 0.20142 | -122.0901 | 0.054932 | -121.582 | -122.0581 | -0.20599 | -0.022888 | 0.19226 | -122.0535 | -0.32959 | 0.082397 | 113.2736 | 121.8155 | -121.701 | -0.29297 | 0.073242 | 113.6032 | 121.5546 | 121.7377 | 0.17853 | 121.962 | 113.2736 | 121.9528 | -0.29755 | -0.29297 | 121.962 | 113.2736 | -0.29755 | 0.17853 | 121.9528 | -122.2092 | -122.1725
820.8438 | 121.9116 | -121.8063 | 0.14648 | 0.009308 | 0.018959 | 0.014817 | -0.0098972 | -0.0062614 | 0.060598 | 0.06987 | -8.4183 | 0.19684 | -122.0764 | 0.13733 | -121.5225 | -121.9803 | -0.22888 | 0.073242 | 0.19226 | -122.0078 | -0.27008 | 0.050354 | 113.3881 | 121.9437 | -121.669 | -0.20142 | 0.045777 | 113.6581 | 121.5775 | 121.8796 | 0.28381 | 122.0032 | 113.3881 | 121.9986 | -0.17395 | -0.20142 | 122.0032 | 113.3881 | -0.17395 | 0.28381 | 121.9986 | -122.2229 | -122.1542
822.5781 | 122.0032 | -121.7102 | 0.14648 | 0.0016785 | 0.01725 | 0.013749 | -0.015024 | -0.010107 | 0.065725 | 0.069015 | -8.4137 | 0.16022 | -122.0215 | 0.20142 | -121.3989 | -121.8979 | -0.37994 | 0.14648 | 0.16937 | -122.0352 | -0.31128 | 0.013733 | 113.2965 | 121.9116 | -121.5454 | -0.32501 | 0.022889 | 113.6078 | 121.3303 | 121.8567 | 0.31128 | 121.8704 | 113.2965 | 121.8796 | -0.18768 | -0.32501 | 121.8704 | 113.2965 | -0.18768 | 0.31128 | 121.8796 | -122.168 | -122.1817
824.25 | 122.0398 | -121.7331 | 0.12817 | 0.0016785 | 0.015114 | 0.010972 | -0.015451 | -0.0096794 | 0.062307 | 0.068161 | -8.4503 | 0.16022 | -122.0398 | 0.16022 | -121.463 | -121.9482 | -0.26093 | 0.10986 | 0.17853 | -122.0261 | -0.3067 | 0.032043 | 113.2828 | 121.8933 | -121.5912 | -0.29297 | 0.050354 | 113.5895 | 121.4722 | 121.843 | 0.27008 | 121.8933 | 113.2828 | 121.9116 | -0.21515 | -0.29297 | 121.8933 | 113.2828 | -0.21515 | 0.27008 | 121.9116 | -122.168 | -122.1542
826 | 122.049 | -121.7194 | 0.10071 | 0.0016785 | 0.018318 | 0.012253 | -0.012674 | -0.011388 | 0.066153 | 0.069443 | -8.4824 | 0.15564 | -122.0215 | 0.13733 | -121.4905 | -121.9391 | -0.38452 | 0.022888 | 0.16479 | -122.0352 | -0.30212 | 0.054932 | 113.237 | 121.8567 | -121.5912 | -0.31586 | 0.064087 | 113.5391 | 121.3348 | 121.7422 | 0.22888 | 121.875 | 113.237 | 121.8842 | -0.21973 | -0.31586 | 121.875 | 113.237 | -0.21973 | 0.22888 | 121.8842 | -122.1222 | -122.1359
827.6719 | 122.0123 | -121.7331 | 0.13733 | -0.013581 | 0.019173 | 0.012253 | -0.012247 | -0.0079704 | 0.06188 | 0.069015 | -8.4915 | 0.15564 | -122.0444 | 0.12817 | -121.5042 | -121.9574 | -0.3891 | 0.041199 | 0.17395 | -122.0306 | -0.31128 | 0.018311 | 113.2416 | 121.8613 | -121.6415 | -0.29755 | 0.036621 | 113.5529 | 121.344 | 121.7743 | 0.22888 | 121.8887 | 113.2416 | 121.907 | -0.2243 | -0.29755 | 121.8887 | 113.2416 | -0.2243 | 0.22888 | 121.907 | -122.1817 | -122.168
829.4062 | 121.9711 | -121.7834 | 0.14648 | -0.005951 | 0.021736 | 0.01439 | -0.006052 | -0.0094656 | 0.061026 | 0.069656 | -8.5098 | 0.20599 | -122.081 | 0.068665 | -121.582 | -122.0581 | -0.1831 | -0.018311 | 0.21973 | -122.0444 | -0.29755 | 0.05951 | 113.2736 | 121.8521 | -121.7285 | -0.26093 | 0.073243 | 113.5712 | 121.6003 | 121.7651 | 0.20142 | 121.9894 | 113.2736 | 122.0032 | -0.27466 | -0.26093 | 121.9894 | 113.2736 | -0.27466 | 0.20142 | 122.0032 | -122.2275 | -122.1909
831.0938 | 122.0261 | -121.7102 | 0.10986 | -0.013581 | 0.018105 | 0.011399 | -0.015879 | -0.0096794 | 0.062521 | 0.068161 | -8.4961 | 0.15564 | -122.0261 | 0.18768 | -121.4539 | -121.9116 | -0.37994 | 0.10529 | 0.16937 | -122.0306 | -0.31586 | 0.045777 | 113.2141 | 121.8979 | -121.5637 | -0.32044 | 0.05951 | 113.53 | 121.3303 | 121.8155 | 0.25635 | 121.8658 | 113.2141 | 121.8796 | -0.20142 | -0.32044 | 121.8658 | 113.2141 | -0.20142 | 0.25635 | 121.8796 | -122.1359 | -122.1405
832.8281 | 121.9986 | -121.756 | 0.13733 | 0.016937 | 0.016823 | 0.01204 | -0.006052 | -0.0077566 | 0.061453 | 0.068161 | -8.5144 | 0.19684 | -122.0901 | 0.064087 | -121.5729 | -122.0352 | -0.24719 | -0.027466 | 0.22888 | -122.0444 | -0.33417 | 0.059509 | 113.2416 | 121.8201 | -121.7102 | -0.28839 | 0.091553 | 113.5757 | 121.5088 | 121.7285 | 0.18311 | 121.9528 | 113.2416 | 121.9849 | -0.27924 | -0.28839 | 121.9528 | 113.2416 | -0.27924 | 0.18311 | 121.9849 | -122.2275 | -122.1817
834.5156 | 121.9437 | -121.7697 | 0.14648 | -0.005951 | 0.018532 | 0.014176 | -0.010965 | -0.008184 | 0.064871 | 0.06987 | -8.432 | 0.15106 | -122.0123 | 0.20142 | -121.4493 | -121.907 | -0.43488 | 0.086975 | 0.14648 | -122.0581 | -0.24262 | 0.004578 | 113.3377 | 121.9711 | -121.5958 | -0.28839 | 0 | 113.5803 | 121.3348 | 121.8567 | 0.32043 | 121.9208 | 113.3377 | 121.9162 | -0.13733 | -0.28839 | 121.9208 | 113.3377 | -0.13733 | 0.32043 | 121.9162 | -122.1588 | -122.2046
836.2656 | 122.0398 | -121.7056 | 0.10529 | -0.005951 | 0.017891 | 0.0094763 | -0.013102 | -0.0090384 | 0.063803 | 0.069229 | -8.551 | 0.16937 | -122.0261 | 0.14191 | -121.5042 | -121.962 | -0.35706 | 0.018311 | 0.17853 | -122.0444 | -0.32043 | 0.064087 | 113.1546 | 121.8475 | -121.6095 | -0.33875 | 0.073242 | 113.475 | 121.3486 | 121.7239 | 0.20142 | 121.875 | 113.1546 | 121.8842 | -0.25635 | -0.33875 | 121.875 | 113.1546 | -0.25635 | 0.20142 | 121.8842 | -122.1313 | -122.1497
838 | 121.9254 | -121.7606 | 0.13733 | -0.013581 | 0.018745 | 0.011826 | -0.00947 | -0.0079704 | 0.063803 | 0.06987 | -8.4915 | 0.15564 | -122.0627 | 0.15564 | -121.4996 | -121.9391 | -0.38452 | 0.054932 | 0.18768 | -121.9986 | -0.30212 | 0.018311 | 113.269 | 121.9162 | -121.637 | -0.23804 | 0.050354 | 113.5712 | 121.376 | 121.8155 | 0.26093 | 121.9162 | 113.269 | 121.9482 | -0.17853 | -0.23804 | 121.9162 | 113.269 | -0.17853 | 0.26093 | 121.9482 | -122.2 | -122.1359
839.6719 | 122.0261 | -121.7377 | 0.13275 | -0.013581 | 0.017464 | 0.016953 | -0.0079746 | -0.0079704 | 0.060171 | 0.068161 | -8.5556 | 0.19226 | -122.1085 | 0.1236 | -121.5134 | -122.0123 | -0.18768 | 0.064087 | 0.20599 | -122.0123 | -0.37079 | 0.05951 | 113.1821 | 121.8613 | -121.6461 | -0.27466 | 0.073243 | 113.5529 | 121.55 | 121.8018 | 0.2243 | 121.9299 | 113.1821 | 121.9437 | -0.27466 | -0.27466 | 121.9299 | 113.1821 | -0.27466 | 0.2243 | 121.9437 | -122.2412 | -122.1451
841.4219 | 121.9345 | -121.7972 | 0.15106 | 0.0016785 | 0.01725 | 0.017167 | -0.013102 | -0.006475 | 0.06423 | 0.070297 | -8.4641 | 0.14191 | -122.0169 | 0.19684 | -121.4584 | -121.9025 | -0.44861 | 0.086975 | 0.16479 | -122.0215 | -0.21973 | -0.009155 | 113.3331 | 121.994 | -121.6095 | -0.2243 | 0.013733 | 113.5529 | 121.3486 | 121.8842 | 0.33875 | 121.9391 | 113.3331 | 121.962 | -0.10529 | -0.2243 | 121.9391 | 113.3331 | -0.10529 | 0.33875 | 121.962 | -122.168 | -122.1725
843.1094 | 122.0078 | -121.7102 | 0.1236 | -0.013581 | 0.0196 | 0.013321 | -0.016947 | -0.009893 | 0.063589 | 0.069656 | -8.5052 | 0.16022 | -122.0123 | 0.19684 | -121.4584 | -121.9162 | -0.40741 | 0.11902 | 0.17853 | -122.0581 | -0.30212 | 0.036621 | 113.205 | 121.907 | -121.582 | -0.3479 | 0.054932 | 113.5071 | 121.3028 | 121.8292 | 0.25177 | 121.8704 | 113.205 | 121.8887 | -0.20599 | -0.3479 | 121.8704 | 113.205 | -0.20599 | 0.25177 | 121.8887 | -122.1359 | -122.1817
844.8438 | 122.0123 | -121.7514 | 0.11902 | 0.0016785 | 0.019173 | 0.018448 | -0.0081882 | -0.009252 | 0.062948 | 0.068161 | -8.5602 | 0.20599 | -122.0993 | 0.12817 | -121.5363 | -121.9986 | -0.19684 | 0.050354 | 0.18768 | -122.0215 | -0.3479 | 0.086975 | 113.1912 | 121.8796 | -121.6553 | -0.27008 | 0.068664 | 113.5391 | 121.5546 | 121.8018 | 0.21515 | 121.9574 | 113.1912 | 121.9391 | -0.24719 | -0.27008 | 121.9574 | 113.1912 | -0.24719 | 0.21515 | 121.9391 | -122.2183 | -122.1405
846.5312 | 121.994 | -121.7651 | 0.13275 | 0.009308 | 0.019386 | 0.014817 | -0.0084018 | -0.0073294 | 0.062094 | 0.071151 | -8.5693 | 0.20142 | -122.1222 | 0.07782 | -121.582 | -122.0535 | -0.22888 | -0.045776 | 0.19684 | -122.0718 | -0.35706 | 0.068665 | 113.1958 | 121.843 | -121.7148 | -0.3067 | 0.064087 | 113.5529 | 121.5363 | 121.7194 | 0.18311 | 121.9666 | 113.1958 | 121.962 | -0.28839 | -0.3067 | 121.9666 | 113.1958 | -0.28839 | 0.18311 | 121.962 | -122.2549 | -122.2046
848.2812 | 121.9894 | -121.7743 | 0.14191 | 0.0016785 | 0.020454 | 0.011826 | -0.0084018 | -0.006475 | 0.060171 | 0.070938 | -8.5876 | 0.18768 | -122.0993 | 0.073242 | -121.5775 | -122.0535 | -0.21973 | -0.027466 | 0.21057 | -122.049 | -0.32501 | 0.045776 | 113.1866 | 121.8475 | -121.7194 | -0.27466 | 0.068664 | 113.5117 | 121.5546 | 121.7468 | 0.19684 | 121.962 | 113.1866 | 121.9849 | -0.27924 | -0.27466 | 121.962 | 113.1866 | -0.27924 | 0.19684 | 121.9849 | -122.2412 | -122.1909
850.0156 | 122.0123 | -121.7422 | 0.12817 | -0.013581 | 0.020241 | 0.0099037 | -0.011393 | -0.0069022 | 0.059103 | 0.06987 | -8.5602 | 0.19226 | -122.0581 | 0.13275 | -121.5134 | -121.9986 | -0.20599 | 0.059509 | 0.21057 | -122.0169 | -0.31586 | 0.064087 | 113.1821 | 121.875 | -121.6415 | -0.27466 | 0.082397 | 113.4979 | 121.5363 | 121.8018 | 0.22888 | 121.9345 | 113.1821 | 121.9528 | -0.25635 | -0.27466 | 121.9345 | 113.1821 | -0.25635 | 0.22888 | 121.9528 | -122.1863 | -122.1451
851.7031 | 122.0673 | -121.7239 | 0.10071 | -0.013581 | 0.020027 | 0.011826 | -0.016733 | -0.0086112 | 0.066153 | 0.069656 | -8.5876 | 0.1831 | -122.0215 | 0.16479 | -121.4859 | -121.9482 | -0.37994 | 0.050354 | 0.18768 | -122.0352 | -0.29755 | 0.082397 | 113.1363 | 121.8887 | -121.5866 | -0.31128 | 0.086975 | 113.4338 | 121.344 | 121.7743 | 0.23804 | 121.907 | 113.1363 | 121.9116 | -0.2243 | -0.31128 | 121.907 | 113.1363 | -0.2243 | 0.23804 | 121.9116 | -122.1222 | -122.1359
853.4375 | 122.0215 | -121.7422 | 0.12817 | -0.013581 | 0.017464 | 0.013749 | -0.011606 | -0.0073294 | 0.064016 | 0.071151 | -8.5739 | 0.17853 | -122.0261 | 0.14648 | -121.5088 | -121.9528 | -0.3891 | 0.018311 | 0.16937 | -122.0673 | -0.28381 | 0.050354 | 113.1683 | 121.8887 | -121.637 | -0.32501 | 0.041199 | 113.4521 | 121.3531 | 121.7606 | 0.23346 | 121.9208 | 113.1683 | 121.9116 | -0.21057 | -0.32501 | 121.9208 | 113.1683 | -0.21057 | 0.23346 | 121.9116 | -122.1542 | -122.1954
855.1094 | 122.0718 | -121.7148 | 0.1236 | -0.013581 | 0.018745 | 0.01738 | -0.014383 | -0.01032 | 0.063589 | 0.069015 | -8.606 | 0.16937 | -122.0581 | 0.13733 | -121.4996 | -121.9666 | -0.37537 | 0.004578 | 0.18768 | -122.0627 | -0.34332 | 0.045777 | 113.1088 | 121.8521 | -121.6232 | -0.3479 | 0.064087 | 113.4521 | 121.3394 | 121.7194 | 0.21515 | 121.8842 | 113.1088 | 121.9025 | -0.25177 | -0.3479 | 121.8842 | 113.1088 | -0.25177 | 0.21515 | 121.9025 | -122.1817 | -122.1863
856.8594 | 122.0673 | -121.7422 | 0.11444 | -0.02121 | 0.019386 | 0.010972 | -0.0079746 | -0.0083976 | 0.062307 | 0.068374 | -8.6014 | 0.21057 | -122.1222 | 0.11902 | -121.55 | -122.0398 | -0.1831 | 0.022888 | 0.20599 | -122.0261 | -0.37994 | 0.09613 | 113.1409 | 121.8613 | -121.6644 | -0.28381 | 0.091553 | 113.5208 | 121.5591 | 121.7651 | 0.19226 | 121.9528 | 113.1409 | 121.9482 | -0.29755 | -0.28381 | 121.9528 | 113.1409 | -0.29755 | 0.19226 | 121.9482 | -122.2366 | -122.1405
858.6094 | 121.8979 | -121.7743 | 0.15106 | 0.0016785 | 0.020454 | 0.017167 | -0.01182 | -0.0062614 | 0.062521 | 0.07222 | -8.5144 | 0.15106 | -122.0444 | 0.20142 | -121.4722 | -121.9116 | -0.46692 | 0.07782 | 0.14648 | -122.0078 | -0.27008 | 0 | 113.2599 | 121.9757 | -121.6232 | -0.23346 | -0.004578 | 113.53 | 121.3074 | 121.8521 | 0.30212 | 121.9254 | 113.2599 | 121.9208 | -0.13733 | -0.23346 | 121.9254 | 113.2599 | -0.13733 | 0.30212 | 121.9208 | -122.1954 | -122.1588
860.3438 | 121.9345 | -121.7834 | 0.16022 | -0.005951 | 0.017036 | 0.011612 | -0.0079746 | -0.0083976 | 0.061239 | 0.068802 | -8.5419 | 0.17853 | -122.0993 | 0.16022 | -121.5179 | -122.0032 | -0.24261 | 0.064087 | 0.19684 | -122.0306 | -0.31586 | 0.018311 | 113.2416 | 121.9437 | -121.6782 | -0.24719 | 0.036621 | 113.5574 | 121.5408 | 121.8475 | 0.2655 | 121.962 | 113.2416 | 121.9803 | -0.21973 | -0.24719 | 121.962 | 113.2416 | -0.21973 | 0.2655 | 121.9803 | -122.2595 | -122.1909
862.0938 | 122.081 | -121.7377 | 0.13275 | -0.013581 | 0.017677 | 0.01503 | -0.014811 | -0.0094656 | 0.063376 | 0.068588 | -8.6151 | 0.19684 | -122.0718 | 0.091553 | -121.5408 | -122.0306 | -0.19226 | 0.018311 | 0.21973 | -122.0535 | -0.33417 | 0.064087 | 113.1226 | 121.8292 | -121.6736 | -0.31586 | 0.086976 | 113.4567 | 121.5454 | 121.756 | 0.19684 | 121.9345 | 113.1226 | 121.9574 | -0.29297 | -0.31586 | 121.9345 | 113.1226 | -0.29297 | 0.19684 | 121.9574 | -122.2046 | -122.1863
863.8438 | 121.9345 | -121.7834 | 0.14648 | 0.0016785 | 0.018959 | 0.012253 | -0.0047702 | -0.0073294 | 0.058676 | 0.070511 | -8.5556 | 0.18768 | -122.0901 | 0.15106 | -121.4951 | -122.0032 | -0.25635 | 0.073242 | 0.20599 | -122.0032 | -0.3067 | 0.041199 | 113.2278 | 121.9345 | -121.6415 | -0.21973 | 0.05951 | 113.5345 | 121.5271 | 121.8567 | 0.28839 | 121.9711 | 113.2278 | 121.9894 | -0.21973 | -0.21973 | 121.9711 | 113.2278 | -0.21973 | 0.28839 | 121.9894 | -122.2366 | -122.1497
865.5312 | 122.0581 | -121.7377 | 0.11444 | -0.013581 | 0.020668 | 0.011826 | -0.012247 | -0.0086112 | 0.062735 | 0.067734 | -8.638 | 0.20142 | -122.0718 | 0.091553 | -121.5637 | -122.0535 | -0.17853 | 0.018311 | 0.19226 | -122.0306 | -0.33417 | 0.086975 | 113.0997 | 121.8292 | -121.6782 | -0.29297 | 0.07782 | 113.4338 | 121.5591 | 121.756 | 0.17395 | 121.9391 | 113.0997 | 121.9299 | -0.31586 | -0.29297 | 121.9391 | 113.0997 | -0.31586 | 0.17395 | 121.9299 | -122.1863 | -122.1451
867.2656 | 122.0261 | -121.7331 | 0.11444 | -0.005951 | 0.018745 | 0.01503 | -0.015879 | -0.008184 | 0.06188 | 0.067306 | -8.5602 | 0.17395 | -122.0261 | 0.20599 | -121.4401 | -121.9208 | -0.36163 | 0.11902 | 0.17395 | -122.0215 | -0.29297 | 0.059509 | 113.1729 | 121.9391 | -121.5546 | -0.28839 | 0.059509 | 113.4659 | 121.3715 | 121.8521 | 0.29297 | 121.907 | 113.1729 | 121.907 | -0.18768 | -0.28839 | 121.907 | 113.1729 | -0.18768 | 0.29297 | 121.907 | -122.1405 | -122.1359
869 | 121.994 | -121.7789 | 0.1236 | 0.0016785 | 0.017036 | 0.014817 | -0.014597 | -0.010534 | 0.063803 | 0.068161 | -8.5831 | 0.16937 | -122.0215 | 0.14191 | -121.5042 | -121.9528 | -0.41657 | 0 | 0.16479 | -122.0261 | -0.24261 | 0.045777 | 113.1958 | 121.9208 | -121.6278 | -0.24719 | 0.041199 | 113.4384 | 121.3623 | 121.7789 | 0.27466 | 121.9482 | 113.1958 | 121.9437 | -0.17395 | -0.24719 | 121.9482 | 113.1958 | -0.17395 | 0.27466 | 121.9437 | -122.1451 | -122.1497
870.75 | 122.0123 | -121.7514 | 0.13733 | 0.0016785 | 0.018318 | 0.010758 | -0.012888 | -0.011388 | 0.063162 | 0.070083 | -8.5693 | 0.17853 | -122.0398 | 0.22888 | -121.4493 | -121.9254 | -0.40283 | 0.11444 | 0.16022 | -122.0535 | -0.28839 | 0.041199 | 113.1821 | 121.9803 | -121.5866 | -0.30212 | 0.022888 | 113.4705 | 121.3486 | 121.8658 | 0.30212 | 121.9299 | 113.1821 | 121.9116 | -0.17395 | -0.30212 | 121.9299 | 113.1821 | -0.17395 | 0.30212 | 121.9116 | -122.1771 | -122.1909
872.4219 | 121.9208 | -121.7972 | 0.14191 | -0.005951 | 0.019386 | 0.01204 | -0.0069064 | -0.0071158 | 0.062307 | 0.071579 | -8.5693 | 0.18768 | -122.0947 | 0.16022 | -121.5317 | -121.9986 | -0.25635 | 0.045776 | 0.19684 | -122.0261 | -0.29755 | 0.045776 | 113.2278 | 121.9574 | -121.6736 | -0.22888 | 0.054931 | 113.5254 | 121.5408 | 121.843 | 0.2655 | 121.9849 | 113.2278 | 121.994 | -0.20142 | -0.22888 | 121.9849 | 113.2278 | -0.20142 | 0.2655 | 121.994 | -122.2366 | -122.168
874.1562 | 121.9757 | -121.788 | 0.16479 | 0.0016785 | 0.017891 | 0.013962 | -0.0079746 | -0.0083976 | 0.061026 | 0.070724 | -8.6288 | 0.19226 | -122.081 | 0.10071 | -121.5729 | -122.0444 | -0.21973 | -0.018311 | 0.19684 | -122.0535 | -0.29297 | 0.027466 | 113.1592 | 121.8887 | -121.7377 | -0.2655 | 0.032043 | 113.4521 | 121.5683 | 121.7697 | 0.21515 | 121.9803 | 113.1592 | 121.9849 | -0.25635 | -0.2655 | 121.9803 | 113.1592 | -0.25635 | 0.21515 | 121.9849 | -122.2458 | -122.2183
875.9062 | 121.9574 | -121.8018 | 0.15564 | -0.005951 | 0.0196 | 0.014176 | -0.00712 | -0.0071158 | 0.061453 | 0.070511 | -8.5968 | 0.17853 | -122.0993 | 0.1236 | -121.55 | -122.0352 | -0.23804 | 0.022888 | 0.20599 | -122.0261 | -0.29755 | 0.022888 | 113.205 | 121.9254 | -121.7056 | -0.2243 | 0.050354 | 113.5025 | 121.5637 | 121.8246 | 0.25177 | 121.9803 | 113.205 | 122.0078 | -0.23346 | -0.2243 | 121.9803 | 113.205 | -0.23346 | 0.25177 | 122.0078 | -122.2549 | -122.1817
877.6562 | 121.9391 | -121.788 | 0.14191 | 0.0016785 | 0.019173 | 0.010972 | -0.015451 | -0.008184 | 0.066366 | 0.071792 | -8.606 | 0.16022 | -122.0444 | 0.19226 | -121.4722 | -121.9345 | -0.43488 | 0.054932 | 0.15564 | -122.0535 | -0.25635 | 0.01831 | 113.1821 | 121.9803 | -121.6141 | -0.2655 | 0.013733 | 113.4384 | 121.3531 | 121.843 | 0.31586 | 121.9482 | 113.1821 | 121.9437 | -0.14648 | -0.2655 | 121.9482 | 113.1821 | -0.14648 | 0.31586 | 121.9437 | -122.1863 | -122.1954
879.3281 | 121.9437 | -121.7606 | 0.12817 | -0.005951 | 0.019813 | 0.01204 | -0.013102 | -0.010747 | 0.060598 | 0.068588 | -8.6014 | 0.14191 | -122.0306 | 0.19226 | -121.4676 | -121.9116 | -0.4303 | 0.064087 | 0.16479 | -122.0306 | -0.27008 | 0.013733 | 113.1592 | 121.9528 | -121.5958 | -0.27008 | 0.036621 | 113.4293 | 121.3303 | 121.8246 | 0.29297 | 121.9025 | 113.1592 | 121.9254 | -0.15106 | -0.27008 | 121.9025 | 113.1592 | -0.15106 | 0.29297 | 121.9254 | -122.1588 | -122.1588
881 | 121.9849 | -121.756 | 0.13733 | -0.005951 | 0.021309 | 0.015885 | -0.0086154 | -0.0086112 | 0.061026 | 0.071792 | -8.6838 | 0.19684 | -122.0901 | 0.073242 | -121.582 | -122.0444 | -0.24261 | -0.041199 | 0.21057 | -122.081 | -0.33417 | 0.059509 | 113.0722 | 121.8292 | -121.7194 | -0.32501 | 0.073242 | 113.4064 | 121.5134 | 121.7148 | 0.17395 | 121.9528 | 113.0722 | 121.9666 | -0.28839 | -0.32501 | 121.9528 | 113.0722 | -0.28839 | 0.17395 | 121.9666 | -122.2275 | -122.2183
882.75 | 122.0306 | -121.7148 | 0.10986 | -0.005951 | 0.016182 | 0.01439 | -0.015451 | -0.0090384 | 0.062307 | 0.070083 | -8.6609 | 0.16479 | -122.0627 | 0.14191 | -121.5179 | -121.9711 | -0.37994 | 0.022888 | 0.17395 | -122.0673 | -0.3479 | 0.054932 | 113.0539 | 121.8567 | -121.6278 | -0.35248 | 0.064087 | 113.4018 | 121.3348 | 121.7377 | 0.19684 | 121.8796 | 113.0539 | 121.8887 | -0.25635 | -0.35248 | 121.8796 | 113.0539 | -0.25635 | 0.19684 | 121.8887 | -122.1725 | -122.1771
884.4844 | 121.9437 | -121.8018 | 0.14191 | -0.005951 | 0.018318 | 0.011399 | -0.0090426 | -0.0094656 | 0.061026 | 0.071365 | -8.6288 | 0.1831 | -122.1039 | 0.15564 | -121.5271 | -122.0123 | -0.23804 | 0.068665 | 0.19684 | -122.049 | -0.30212 | 0.041198 | 113.1729 | 121.9574 | -121.669 | -0.24719 | 0.054931 | 113.475 | 121.5637 | 121.8704 | 0.27466 | 121.9849 | 113.1729 | 121.9986 | -0.21057 | -0.24719 | 121.9849 | 113.1729 | -0.21057 | 0.27466 | 121.9986 | -122.2458 | -122.1909
886.1562 | 122.0078 | -121.7743 | 0.12817 | -0.005951 | 0.017891 | 0.014603 | -0.010752 | -0.0077566 | 0.061453 | 0.068374 | -8.6792 | 0.1831 | -122.1222 | 0.059509 | -121.5866 | -122.0627 | -0.2243 | -0.050354 | 0.20142 | -122.049 | -0.3479 | 0.054931 | 113.0951 | 121.8338 | -121.7148 | -0.27466 | 0.073242 | 113.443 | 121.55 | 121.7239 | 0.18768 | 121.9574 | 113.0951 | 121.9757 | -0.28839 | -0.27466 | 121.9574 | 113.0951 | -0.28839 | 0.18768 | 121.9757 | -122.2504 | -122.1771
887.9062 | 122.0535 | -121.7377 | 0.11902 | -0.013581 | 0.020027 | 0.013962 | -0.015879 | -0.0094656 | 0.065084 | 0.06987 | -8.6838 | 0.15106 | -122.049 | 0.11444 | -121.5134 | -121.9666 | -0.37079 | 0.009155 | 0.17853 | -122.0627 | -0.31128 | 0.032043 | 113.0539 | 121.8521 | -121.6324 | -0.32501 | 0.059509 | 113.3652 | 121.3669 | 121.7468 | 0.2243 | 121.8887 | 113.0539 | 121.9162 | -0.22888 | -0.32501 | 121.8887 | 113.0539 | -0.22888 | 0.2243 | 121.9162 | -122.168 | -122.1817
889.5938 | 122.0627 | -121.7422 | 0.11902 | -0.005951 | 0.018745 | 0.0092627 | -0.013742 | -0.012456 | 0.065298 | 0.067947 | -8.6792 | 0.16937 | -122.0581 | 0.17395 | -121.463 | -121.9299 | -0.3891 | 0.082397 | 0.18768 | -122.0764 | -0.31586 | 0.050354 | 113.0631 | 121.9162 | -121.582 | -0.33417 | 0.068664 | 113.3789 | 121.3531 | 121.8246 | 0.27924 | 121.9116 | 113.0631 | 121.9299 | -0.18768 | -0.33417 | 121.9116 | 113.0631 | -0.18768 | 0.27924 | 121.9299 | -122.1771 | -122.1954
891.3438 | 122.0901 | -121.7331 | 0.1236 | 0.0016785 | 0.02195 | 0.0077673 | -0.007761 | -0.010107 | 0.062735 | 0.068588 | -8.7067 | 0.20142 | -122.1085 | 0.10071 | -121.5729 | -122.0581 | -0.17395 | 0.022888 | 0.21057 | -122.0901 | -0.37537 | 0.07782 | 113.0264 | 121.8338 | -121.6965 | -0.35706 | 0.086975 | 113.4018 | 121.5591 | 121.756 | 0.16022 | 121.9345 | 113.0264 | 121.9437 | -0.32501 | -0.35706 | 121.9345 | 113.0264 | -0.32501 | 0.16022 | 121.9437 | -122.2321 | -122.2137
893.0938 | 122.0215 | -121.7377 | 0.13275 | -0.013581 | 0.01725 | 0.0088355 | -0.013956 | -0.0096794 | 0.064871 | 0.070297 | -8.638 | 0.14648 | -122.0581 | 0.21973 | -121.4539 | -121.9254 | -0.3891 | 0.13275 | 0.17395 | -122.0352 | -0.32043 | 0.013733 | 113.0997 | 121.9574 | -121.5866 | -0.29755 | 0.041199 | 113.4201 | 121.3486 | 121.8704 | 0.28381 | 121.8842 | 113.0997 | 121.9116 | -0.18768 | -0.29755 | 121.8842 | 113.0997 | -0.18768 | 0.28381 | 121.9116 | -122.1909 | -122.168
894.8281 | 122.0856 | -121.7102 | 0.11902 | -0.005951 | 0.016609 | 0.010544 | -0.01417 | -0.0088248 | 0.062094 | 0.070724 | -8.7021 | 0.16479 | -122.0398 | 0.16479 | -121.4813 | -121.962 | -0.38452 | 0.064087 | 0.16937 | -122.0535 | -0.32959 | 0.045776 | 113.0081 | 121.875 | -121.6003 | -0.34332 | 0.050354 | 113.3377 | 121.3257 | 121.7743 | 0.22888 | 121.875 | 113.0081 | 121.8796 | -0.25177 | -0.34332 | 121.875 | 113.0081 | -0.25177 | 0.22888 | 121.8796 | -122.1588 | -122.1725
896.5156 | 122.0535 | -121.756 | 0.10529 | -0.013581 | 0.021522 | 0.013962 | -0.0092564 | -0.0086112 | 0.062094 | 0.06752 | -8.7341 | 0.20142 | -122.1313 | 0.10986 | -121.5637 | -122.0398 | -0.17853 | 0.032043 | 0.19226 | -122.0764 | -0.37537 | 0.09613 | 113.0219 | 121.8658 | -121.669 | -0.32043 | 0.086975 | 113.3972 | 121.5775 | 121.788 | 0.19226 | 121.9574 | 113.0219 | 121.9482 | -0.28381 | -0.32043 | 121.9574 | 113.0219 | -0.28381 | 0.19226 | 121.9482 | -122.2366 | -122.1817
898.25 | 121.9803 | -121.7743 | 0.16937 | -0.005951 | 0.018959 | 0.014817 | -0.0075474 | -0.0066886 | 0.063376 | 0.069443 | -8.6884 | 0.19226 | -122.1085 | 0.14648 | -121.5363 | -122.0169 | -0.22888 | 0.059509 | 0.20142 | -122.0856 | -0.33417 | 0.022888 | 113.0859 | 121.9208 | -121.7056 | -0.31128 | 0.032043 | 113.4201 | 121.5454 | 121.8338 | 0.23804 | 121.9666 | 113.0859 | 121.9757 | -0.24262 | -0.31128 | 121.9666 | 113.0859 | -0.24262 | 0.23804 | 121.9757 | -122.2778 | -122.2549
900 | 122.0032 | -121.7926 | 0.14648 | 0.0016785 | 0.019813 | 0.013749 | -0.0096836 | -0.0083976 | 0.061666 | 0.070297 | -8.6975 | 0.17853 | -122.0993 | 0.14191 | -121.5363 | -122.0306 | -0.22888 | 0.059509 | 0.21057 | -122.0444 | -0.3067 | 0.032044 | 113.0951 | 121.9345 | -121.6827 | -0.25177 | 0.064087 | 113.4018 | 121.5637 | 121.8521 | 0.25635 | 121.9711 | 113.0951 | 122.0032 | -0.23804 | -0.25177 | 121.9711 | 113.0951 | -0.23804 | 0.25635 | 122.0032 | -122.2458 | -122.1909
901.6719 | 121.9254 | -121.7972 | 0.13275 | 0.009308 | 0.015968 | 0.011185 | -0.012674 | -0.0071158 | 0.06188 | 0.068802 | -8.6655 | 0.15564 | -122.0398 | 0.19226 | -121.463 | -121.9299 | -0.4715 | 0.068665 | 0.1831 | -122.0261 | -0.24262 | 0.022889 | 113.1317 | 121.9894 | -121.5958 | -0.22888 | 0.050354 | 113.3743 | 121.3257 | 121.8658 | 0.33417 | 121.9528 | 113.1317 | 121.9803 | -0.13275 | -0.22888 | 121.9528 | 113.1317 | -0.13275 | 0.33417 | 121.9803 | -122.1725 | -122.1588
903.4062 | 121.9849 | -121.7606 | 0.15106 | -0.005951 | 0.020241 | 0.016953 | -0.0098972 | -0.0069022 | 0.060171 | 0.070083 | -8.7524 | 0.20599 | -122.1085 | 0.068665 | -121.5958 | -122.0673 | -0.23804 | -0.059509 | 0.20142 | -122.049 | -0.3479 | 0.054932 | 113.0081 | 121.8292 | -121.7468 | -0.28839 | 0.050354 | 113.356 | 121.5225 | 121.701 | 0.16479 | 121.9666 | 113.0081 | 121.962 | -0.3067 | -0.28839 | 121.9666 | 113.0081 | -0.3067 | 0.16479 | 121.962 | -122.2595 | -122.2
905.1406 | 122.0352 | -121.7194 | 0.10071 | -0.013581 | 0.017036 | 0.011612 | -0.016947 | -0.0079704 | 0.061453 | 0.068161 | -8.7021 | 0.15106 | -122.0398 | 0.20599 | -121.4539 | -121.9116 | -0.41657 | 0.11444 | 0.15564 | -122.049 | -0.32044 | 0.050354 | 113.0173 | 121.9254 | -121.5546 | -0.32959 | 0.054932 | 113.3377 | 121.3028 | 121.8338 | 0.2655 | 121.8704 | 113.0173 | 121.875 | -0.19226 | -0.32959 | 121.8704 | 113.0173 | -0.19226 | 0.2655 | 121.875 | -122.1405 | -122.1497
906.8281 | 122.0718 | -121.756 | 0.11902 | 0.0016785 | 0.017891 | 0.014176 | -0.010324 | -0.0090384 | 0.061453 | 0.069015 | -8.7982 | 0.18768 | -122.1176 | 0.086975 | -121.5546 | -122.0581 | -0.1831 | 0.013733 | 0.20599 | -122.0673 | -0.36163 | 0.068664 | 112.9578 | 121.843 | -121.6736 | -0.31128 | 0.086975 | 113.3194 | 121.5729 | 121.7697 | 0.20142 | 121.9437 | 112.9578 | 121.962 | -0.30212 | -0.31128 | 121.9437 | 112.9578 | -0.30212 | 0.20142 | 121.962 | -122.2366 | -122.1863
908.5625 | 122.049 | -121.7651 | 0.11444 | -0.013581 | 0.018105 | 0.015244 | -0.015879 | -0.0094656 | 0.065298 | 0.069443 | -8.6975 | 0.14648 | -122.0261 | 0.20142 | -121.463 | -121.9437 | -0.35706 | 0.11444 | 0.16479 | -122.0718 | -0.26093 | 0.032043 | 113.0676 | 121.9666 | -121.5775 | -0.3067 | 0.050354 | 113.3286 | 121.4081 | 121.8796 | 0.30212 | 121.9116 | 113.0676 | 121.9299 | -0.17853 | -0.3067 | 121.9116 | 113.0676 | -0.17853 | 0.30212 | 121.9299 | -122.1405 | -122.1863
910.2969 | 122.0581 | -121.756 | 0.1236 | -0.013581 | 0.016823 | 0.014603 | -0.012461 | -0.0090384 | 0.063162 | 0.070724 | -8.725 | 0.17395 | -122.0535 | 0.20142 | -121.4813 | -121.962 | -0.31128 | 0.11902 | 0.1831 | -122.0535 | -0.29755 | 0.050354 | 113.031 | 121.9574 | -121.6049 | -0.29755 | 0.059509 | 113.3286 | 121.4447 | 121.875 | 0.27466 | 121.9299 | 113.031 | 121.9391 | -0.20599 | -0.29755 | 121.9299 | 113.031 | -0.20599 | 0.27466 | 121.9391 | -122.1771 | -122.1771
911.9844 | 122.0032 | -121.7926 | 0.13733 | -0.013581 | 0.019813 | 0.019089 | -0.0066928 | -0.0083976 | 0.062521 | 0.070297 | -8.7936 | 0.21057 | -122.1085 | 0.068665 | -121.6003 | -122.0673 | -0.21973 | -0.054932 | 0.21515 | -122.0673 | -0.31586 | 0.073242 | 112.999 | 121.8613 | -121.7377 | -0.27466 | 0.07782 | 113.3148 | 121.5729 | 121.7377 | 0.19226 | 122.0032 | 112.999 | 122.0078 | -0.27466 | -0.27466 | 122.0032 | 112.999 | -0.27466 | 0.19226 | 122.0078 | -122.2458 | -122.2046
913.7188 | 122.0947 | -121.7285 | 0.11902 | 0.0016785 | 0.019813 | 0.012253 | -0.012888 | -0.0086112 | 0.064657 | 0.069656 | -8.812 | 0.20599 | -122.0947 | 0.073242 | -121.5591 | -122.0627 | -0.14191 | 0.004578 | 0.2243 | -122.0856 | -0.36621 | 0.086975 | 112.9166 | 121.8018 | -121.6782 | -0.35706 | 0.10529 | 113.2828 | 121.5866 | 121.7331 | 0.16937 | 121.9345 | 112.9166 | 121.9528 | -0.33417 | -0.35706 | 121.9345 | 112.9166 | -0.33417 | 0.16937 | 121.9528 | -122.2137 | -122.2046
915.3906 | 121.9666 | -121.7743 | 0.13733 | 0.0016785 | 0.0196 | 0.013962 | -0.0096836 | -0.0069022 | 0.061239 | 0.069443 | -8.7891 | 0.18768 | -122.1359 | 0.10529 | -121.5454 | -122.0215 | -0.33417 | -0.004578 | 0.18768 | -122.0581 | -0.36163 | 0.050354 | 112.9852 | 121.8796 | -121.6827 | -0.28381 | 0.050354 | 113.3469 | 121.4401 | 121.7697 | 0.22888 | 121.962 | 112.9852 | 121.962 | -0.24719 | -0.28381 | 121.962 | 112.9852 | -0.24719 | 0.22888 | 121.962 | -122.2733 | -122.1954
917.1406 | 121.9437 | -121.7926 | 0.15106 | -0.02121 | 0.019813 | 0.0099037 | -0.0098972 | -0.005834 | 0.060598 | 0.070297 | -8.7021 | 0.16022 | -122.049 | 0.21057 | -121.463 | -121.9208 | -0.46234 | 0.073242 | 0.15564 | -122.0581 | -0.25635 | 0.009155 | 113.0905 | 122.0032 | -121.6141 | -0.2655 | 0.004578 | 113.3469 | 121.3303 | 121.8658 | 0.32959 | 121.9528 | 113.0905 | 121.9482 | -0.12817 | -0.2655 | 121.9528 | 113.0905 | -0.12817 | 0.32959 | 121.9482 | -122.2 | -122.2092
918.875 | 122.0535 | -121.7422 | 0.12817 | -0.005951 | 0.017036 | 0.012253 | -0.015879 | -0.0096794 | 0.062735 | 0.06987 | -8.8028 | 0.16022 | -122.0627 | 0.13275 | -121.5134 | -121.9757 | -0.37537 | 0.004578 | 0.1831 | -122.113 | -0.32043 | 0.032043 | 112.9395 | 121.875 | -121.6415 | -0.37079 | 0.054931 | 113.2599 | 121.3669 | 121.7468 | 0.22888 | 121.9025 | 112.9395 | 121.9254 | -0.23346 | -0.37079 | 121.9025 | 112.9395 | -0.23346 | 0.22888 | 121.9254 | -122.1909 | -122.2412
920.625 | 122.0718 | -121.7514 | 0.11444 | 0.0016785 | 0.018745 | 0.010758 | -0.012888 | -0.01032 | 0.065939 | 0.070511 | -8.844 | 0.16937 | -122.0627 | 0.13275 | -121.5225 | -121.9849 | -0.37079 | 0.022888 | 0.16479 | -122.0764 | -0.31128 | 0.054932 | 112.9074 | 121.8842 | -121.637 | -0.32501 | 0.050354 | 113.2187 | 121.3806 | 121.7743 | 0.22888 | 121.9208 | 112.9074 | 121.9162 | -0.23346 | -0.32501 | 121.9208 | 112.9074 | -0.23346 | 0.22888 | 121.9162 | -122.1771 | -122.1909
922.3125 | 122.0947 | -121.7514 | 0.09613 | -0.013581 | 0.016396 | 0.011612 | -0.010324 | -0.0094656 | 0.062521 | 0.068588 | -8.8028 | 0.17853 | -122.1222 | 0.12817 | -121.5591 | -122.0398 | -0.2243 | 0.022888 | 0.19684 | -122.0901 | -0.37079 | 0.082398 | 112.9486 | 121.8796 | -121.6553 | -0.33875 | 0.10071 | 113.3194 | 121.5271 | 121.7743 | 0.19226 | 121.9299 | 112.9486 | 121.9482 | -0.28839 | -0.33875 | 121.9299 | 112.9486 | -0.28839 | 0.19226 | 121.9482 | -122.2183 | -122.1863
923.9844 | 122.0261 | -121.7468 | 0.13275 | -0.005951 | 0.020454 | 0.017808 | -0.0064792 | -0.0077566 | 0.059957 | 0.070938 | -8.8211 | 0.19684 | -122.1085 | 0.1236 | -121.5408 | -122.0352 | -0.21057 | 0.027466 | 0.20599 | -122.0856 | -0.36163 | 0.064087 | 112.9257 | 121.8704 | -121.6736 | -0.33875 | 0.073243 | 113.2874 | 121.5363 | 121.7743 | 0.20599 | 121.9437 | 112.9257 | 121.9528 | -0.28839 | -0.33875 | 121.9437 | 112.9257 | -0.28839 | 0.20599 | 121.9528 | -122.2412 | -122.2183
925.7344 | 122.0993 | -121.7606 | 0.12817 | 0.0016785 | 0.016182 | 0.011612 | -0.01182 | -0.0079704 | 0.063162 | 0.070724 | -8.8852 | 0.18768 | -122.1359 | 0.091553 | -121.582 | -122.0856 | -0.15106 | -0.004578 | 0.2243 | -122.0673 | -0.37537 | 0.059509 | 112.8754 | 121.8521 | -121.7102 | -0.3067 | 0.09613 | 113.2507 | 121.6095 | 121.756 | 0.17853 | 121.9482 | 112.8754 | 121.9849 | -0.32501 | -0.3067 | 121.9482 | 112.8754 | -0.32501 | 0.17853 | 121.9849 | -122.2641 | -122.1954
927.4688 | 122.0398 | -121.7514 | 0.11444 | 0.0016785 | 0.017891 | 0.01439 | -0.013742 | -0.0079704 | 0.063803 | 0.070083 | -8.7891 | 0.15564 | -122.049 | 0.20142 | -121.4676 | -121.9437 | -0.36163 | 0.091553 | 0.16022 | -122.0856 | -0.29755 | 0.041199 | 112.9623 | 121.9528 | -121.582 | -0.33417 | 0.045776 | 113.2599 | 121.3898 | 121.843 | 0.28381 | 121.907 | 112.9623 | 121.9116 | -0.19226 | -0.33417 | 121.907 | 112.9623 | -0.19226 | 0.28381 | 121.9116 | -122.1634 | -122.2
929.2031 | 121.962 | -121.7697 | 0.15564 | -0.005951 | 0.021095 | 0.018662 | -0.011179 | -0.0083976 | 0.063376 | 0.070083 | -8.844 | 0.18768 | -122.1039 | 0.11444 | -121.5591 | -122.0123 | -0.35706 | -0.027466 | 0.17853 | -122.0627 | -0.33417 | 0.032043 | 112.9257 | 121.8842 | -121.7148 | -0.29297 | 0.022888 | 113.2599 | 121.4127 | 121.7422 | 0.21057 | 121.9574 | 112.9257 | 121.9482 | -0.24262 | -0.29297 | 121.9574 | 112.9257 | -0.24262 | 0.21057 | 121.9482 | -122.2595 | -122.2183
930.9531 | 122.0352 | -121.756 | 0.11444 | -0.02121 | 0.018318 | 0.010758 | -0.014811 | -0.009893 | 0.064657 | 0.070938 | -8.8028 | 0.16479 | -122.0581 | 0.21515 | -121.4584 | -121.9299 | -0.42572 | 0.086975 | 0.15106 | -122.0535 | -0.30212 | 0.050354 | 112.9532 | 121.9711 | -121.5729 | -0.29755 | 0.036621 | 113.2553 | 121.3303 | 121.843 | 0.29755 | 121.9208 | 112.9532 | 121.907 | -0.17395 | -0.29755 | 121.9208 | 112.9532 | -0.17395 | 0.29755 | 121.907 | -122.1725 | -122.168
932.7031 | 121.9986 | -121.7834 | 0.13275 | 0.0016785 | 0.020241 | 0.015244 | -0.0064792 | -0.0077566 | 0.058889 | 0.070297 | -8.8623 | 0.20599 | -122.1313 | 0.07782 | -121.5958 | -122.0856 | -0.21973 | -0.064087 | 0.21057 | -122.0856 | -0.3479 | 0.073243 | 112.9211 | 121.8613 | -121.7285 | -0.30212 | 0.07782 | 113.269 | 121.5637 | 121.7194 | 0.18768 | 121.9894 | 112.9211 | 121.994 | -0.30212 | -0.30212 | 121.9894 | 112.9211 | -0.30212 | 0.18768 | 121.994 | -122.2641 | -122.2183
934.4531 | 122.0627 | -121.7514 | 0.13275 | -0.013581 | 0.01725 | 0.015885 | -0.0075474 | -0.0083976 | 0.06188 | 0.069443 | -8.876 | 0.21515 | -122.1497 | 0.11444 | -121.5637 | -122.0306 | -0.1831 | 0.004578 | 0.20142 | -122.0993 | -0.39825 | 0.082398 | 112.8754 | 121.8658 | -121.6965 | -0.3479 | 0.068665 | 113.2736 | 121.5683 | 121.756 | 0.18768 | 121.9666 | 112.8754 | 121.9528 | -0.27924 | -0.3479 | 121.9666 | 112.8754 | -0.27924 | 0.18768 | 121.9528 | -122.2824 | -122.2321
936.125 | 121.962 | -121.7834 | 0.16479 | 0.0016785 | 0.018959 | 0.01439 | -0.0096836 | -0.0066886 | 0.060385 | 0.06987 | -8.7982 | 0.20142 | -122.113 | 0.15564 | -121.5179 | -122.0215 | -0.2655 | 0.036621 | 0.21515 | -122.0627 | -0.32959 | 0.036621 | 112.9852 | 121.9391 | -121.6827 | -0.27924 | 0.050354 | 113.3148 | 121.5179 | 121.8201 | 0.2655 | 121.9849 | 112.9852 | 121.9986 | -0.23804 | -0.27924 | 121.9849 | 112.9852 | -0.23804 | 0.2655 | 121.9986 | -122.2778 | -122.2275
937.875 | 121.9528 | -121.7972 | 0.14648 | -0.005951 | 0.020454 | 0.010758 | -0.015879 | -0.0071158 | 0.063589 | 0.067947 | -8.8257 | 0.14648 | -122.0581 | 0.18768 | -121.4905 | -121.962 | -0.46234 | 0.009155 | 0.14648 | -122.1039 | -0.26093 | 0 | 112.9715 | 121.9849 | -121.637 | -0.3067 | 0 | 113.2324 | 121.3348 | 121.8063 | 0.3067 | 121.9437 | 112.9715 | 121.9437 | -0.16479 | -0.3067 | 121.9437 | 112.9715 | -0.16479 | 0.3067 | 121.9437 | -122.2046 | -122.2504
939.5469 | 121.9711 | -121.8063 | 0.15106 | -0.005951 | 0.017891 | 0.014817 | -0.013529 | -0.008184 | 0.063162 | 0.06987 | -8.8303 | 0.15564 | -122.0627 | 0.17853 | -121.4813 | -121.9391 | -0.4715 | 0.013733 | 0.16022 | -122.081 | -0.25635 | 0.004578 | 112.9761 | 121.9849 | -121.6324 | -0.27466 | 0.009155 | 113.2324 | 121.3348 | 121.8201 | 0.32501 | 121.962 | 112.9761 | 121.9666 | -0.13275 | -0.27466 | 121.962 | 112.9761 | -0.13275 | 0.32501 | 121.9666 | -122.2137 | -122.2321
941.2969 | 122.0901 | -121.7468 | 0.12817 | 0.0016785 | 0.021736 | 0.011399 | -0.01417 | -0.0073294 | 0.063376 | 0.070511 | -8.9172 | 0.17395 | -122.081 | 0.15106 | -121.5088 | -121.9757 | -0.42114 | -0.022888 | 0.1831 | -122.0901 | -0.33417 | 0.045776 | 112.8296 | 121.8979 | -121.637 | -0.34332 | 0.054931 | 113.1638 | 121.3257 | 121.7239 | 0.23804 | 121.9208 | 112.8296 | 121.9299 | -0.22888 | -0.34332 | 121.9208 | 112.8296 | -0.22888 | 0.23804 | 121.9299 | -122.2092 | -122.2183
943.0469 | 122.0306 | -121.7697 | 0.1236 | -0.005951 | 0.0196 | 0.015244 | -0.012674 | -0.011816 | 0.062948 | 0.070938 | -8.8577 | 0.14191 | -122.0627 | 0.22888 | -121.4539 | -121.9391 | -0.42572 | 0.086975 | 0.16479 | -122.0901 | -0.29297 | 0.018311 | 112.912 | 121.9986 | -121.5775 | -0.32044 | 0.041199 | 113.205 | 121.344 | 121.8567 | 0.31586 | 121.9116 | 112.912 | 121.9345 | -0.16937 | -0.32044 | 121.9116 | 112.912 | -0.16937 | 0.31586 | 121.9345 | -122.1863 | -122.2137
944.7344 | 122.0627 | -121.7239 | 0.11444 | 0.009308 | 0.019386 | 0.012894 | -0.010538 | -0.009893 | 0.062521 | 0.070724 | -8.8943 | 0.16022 | -122.0947 | 0.14191 | -121.5363 | -122.0306 | -0.28839 | -0.018311 | 0.20142 | -122.0901 | -0.37079 | 0.045776 | 112.8296 | 121.8658 | -121.6507 | -0.36621 | 0.086975 | 113.2004 | 121.4355 | 121.7056 | 0.18768 | 121.8842 | 112.8296 | 121.9254 | -0.3067 | -0.36621 | 121.8842 | 112.8296 | -0.3067 | 0.18768 | 121.9254 | -122.2092 | -122.2046
946.4844 | 122.0627 | -121.7468 | 0.11902 | 0.0016785 | 0.01725 | 0.01204 | -0.012033 | -0.007543 | 0.059317 | 0.070511 | -8.8669 | 0.16937 | -122.0856 | 0.16479 | -121.5042 | -121.9894 | -0.3479 | -0.013733 | 0.19684 | -122.0764 | -0.33875 | 0.050354 | 112.8799 | 121.9116 | -121.6232 | -0.32959 | 0.077819 | 113.2187 | 121.3989 | 121.7331 | 0.24262 | 121.9162 | 112.8799 | 121.9437 | -0.24262 | -0.32959 | 121.9162 | 112.8799 | -0.24262 | 0.24262 | 121.9437 | -122.2046 | -122.1954
948.2344 | 121.9757 | -121.7972 | 0.13733 | 0.009308 | 0.017891 | 0.018235 | -0.0081882 | -0.008184 | 0.060385 | 0.070083 | -8.8943 | 0.1831 | -122.1268 | 0.15564 | -121.55 | -122.0261 | -0.30212 | -0.018311 | 0.20599 | -122.049 | -0.32959 | 0.045776 | 112.9028 | 121.9528 | -121.6873 | -0.25177 | 0.068665 | 113.2324 | 121.4951 | 121.7789 | 0.24719 | 121.9803 | 112.9028 | 122.0032 | -0.22888 | -0.25177 | 121.9803 | 112.9028 | -0.22888 | 0.24719 | 122.0032 | -122.2641 | -122.1863
949.9688 | 122.0581 | -121.7422 | 0.10529 | -0.013581 | 0.020241 | 0.013962 | -0.015238 | -0.0079704 | 0.065298 | 0.070511 | -8.9493 | 0.16022 | -122.0627 | 0.16937 | -121.4905 | -121.962 | -0.46692 | 0 | 0.1831 | -122.0856 | -0.32043 | 0.054931 | 112.793 | 121.9116 | -121.5958 | -0.34332 | 0.077819 | 113.1134 | 121.2753 | 121.7422 | 0.25177 | 121.9025 | 112.793 | 121.9254 | -0.21973 | -0.34332 | 121.9025 | 112.793 | -0.21973 | 0.25177 | 121.9254 | -122.168 | -122.1909
951.6406 | 121.9849 | -121.7834 | 0.14191 | -0.005951 | 0.019173 | 0.013321 | -0.012033 | -0.0077566 | 0.064444 | 0.069015 | -8.8898 | 0.16022 | -122.0718 | 0.17395 | -121.5088 | -121.9803 | -0.50812 | -0.045776 | 0.15564 | -122.0947 | -0.28839 | 0.01831 | 112.8937 | 121.9574 | -121.6507 | -0.31128 | 0.013733 | 113.1821 | 121.2753 | 121.7377 | 0.27466 | 121.9437 | 112.8937 | 121.9391 | -0.19684 | -0.31128 | 121.9437 | 112.8937 | -0.19684 | 0.27466 | 121.9391 | -122.2137 | -122.2366
953.4062 | 122.0306 | -121.7789 | 0.12817 | 0.0016785 | 0.021095 | 0.015885 | -0.0062656 | -0.006475 | 0.059103 | 0.067734 | -8.931 | 0.17853 | -122.1588 | 0.12817 | -121.5546 | -122.0261 | -0.28839 | -0.091553 | 0.21057 | -122.0673 | -0.37994 | 0.050354 | 112.8479 | 121.907 | -121.6827 | -0.28839 | 0.082397 | 113.2278 | 121.4905 | 121.6873 | 0.22431 | 121.9574 | 112.8479 | 121.9894 | -0.24719 | -0.28839 | 121.9574 | 112.8479 | -0.24719 | 0.22431 | 121.9894 | -122.287 | -122.1954
955.0781 | 122.0215 | -121.7377 | 0.1236 | 0.0016785 | 0.018745 | 0.011185 | -0.015665 | -0.0083976 | 0.063376 | 0.069015 | -8.8989 | 0.16479 | -122.0535 | 0.19684 | -121.4447 | -121.9162 | -0.46234 | -0.054932 | 0.16022 | -122.0627 | -0.31586 | 0.041199 | 112.8387 | 121.9345 | -121.5683 | -0.32501 | 0.036621 | 113.1546 | 121.2753 | 121.6827 | 0.29297 | 121.9025 | 112.8387 | 121.8979 | -0.17853 | -0.32501 | 121.9025 | 112.8387 | -0.17853 | 0.29297 | 121.8979 | -122.1771 | -122.1863
956.8281 | 121.9803 | -121.8155 | 0.14191 | -0.005951 | 0.018532 | 0.012253 | -0.013102 | -0.006475 | 0.062521 | 0.071792 | -8.8852 | 0.13275 | -122.0718 | 0.19226 | -121.4859 | -121.9528 | -0.49896 | -0.086975 | 0.16479 | -122.0535 | -0.25635 | -0.009156 | 112.9303 | 122.0078 | -121.6278 | -0.23804 | 0.022888 | 113.1866 | 121.3165 | 121.7285 | 0.32959 | 121.9482 | 112.9303 | 121.9803 | -0.13733 | -0.23804 | 121.9482 | 112.9303 | -0.13733 | 0.32959 | 121.9803 | -122.2137 | -122.1954
958.5938 | 122.0032 | -121.7697 | 0.13275 | 0.0016785 | 0.017891 | 0.015244 | -0.0098972 | -0.0051932 | 0.059317 | 0.068588 | -8.9767 | 0.18768 | -122.1497 | 0.09613 | -121.6003 | -122.0627 | -0.33417 | -0.31586 | 0.20599 | -122.0764 | -0.37994 | 0.054932 | 112.793 | 121.8658 | -121.7331 | -0.3067 | 0.073243 | 113.1729 | 121.4355 | 121.4539 | 0.16937 | 121.9574 | 112.793 | 121.9757 | -0.29297 | -0.3067 | 121.9574 | 112.793 | -0.29297 | 0.16937 | 121.9757 | -122.2824 | -122.2092
960.2656 | 121.9528 | -121.8063 | 0.14648 | 0.0016785 | 0.01725 | 0.012681 | -0.0084018 | -0.0062614 | 0.059317 | 0.069656 | -8.931 | 0.16937 | -122.0856 | 0.16479 | -121.4996 | -121.962 | -0.48065 | -0.25177 | 0.16479 | -122.049 | -0.27924 | 0.022889 | 112.8754 | 121.9711 | -121.6461 | -0.24262 | 0.018311 | 113.1546 | 121.3257 | 121.5546 | 0.3067 | 121.9757 | 112.8754 | 121.9711 | -0.15564 | -0.24262 | 121.9757 | 112.8754 | -0.15564 | 0.3067 | 121.9711 | -122.2321 | -122.1954
962 | 122.0261 | -121.788 | 0.12817 | -0.005951 | 0.016396 | 0.0088355 | -0.014811 | -0.0090384 | 0.065298 | 0.071151 | -8.9355 | 0.15106 | -122.0535 | 0.20142 | -121.4493 | -121.9345 | -0.45776 | -0.25177 | 0.15564 | -122.0718 | -0.2655 | 0.022888 | 112.8525 | 121.9894 | -121.5775 | -0.28381 | 0.027466 | 113.118 | 121.3303 | 121.5363 | 0.33875 | 121.9391 | 112.8525 | 121.9437 | -0.14648 | -0.28381 | 121.9391 | 112.8525 | -0.14648 | 0.33875 | 121.9437 | -122.1817 | -122.2
963.7031 | 121.9574 | -121.8109 | 0.16937 | 0.0016785 | 0.01725 | 0.013108 | -0.0069064 | -0.0069022 | 0.061453 | 0.069015 | -8.9172 | 0.16479 | -122.1405 | 0.15106 | -121.55 | -122.0352 | -0.3067 | -0.27008 | 0.19226 | -122.0901 | -0.32959 | -0.004578 | 112.8937 | 121.962 | -121.7194 | -0.27924 | 0.022888 | 113.2233 | 121.5042 | 121.5408 | 0.26093 | 121.9757 | 112.8937 | 122.0032 | -0.2243 | -0.27924 | 121.9757 | 112.8937 | -0.2243 | 0.26093 | 122.0032 | -122.3099 | -122.2595
965.4375 | 122.0444 | -121.7743 | 0.1236 | -0.005951 | 0.018105 | 0.011185 | -0.013102 | -0.011175 | 0.063376 | 0.069229 | -8.9493 | 0.16022 | -122.0673 | 0.21973 | -121.4767 | -121.9528 | -0.42114 | -0.14648 | 0.15564 | -122.113 | -0.29297 | 0.036621 | 112.825 | 121.994 | -121.6003 | -0.33875 | 0.032044 | 113.118 | 121.3531 | 121.6278 | 0.29755 | 121.9345 | 112.825 | 121.9299 | -0.17853 | -0.33875 | 121.9345 | 112.825 | -0.17853 | 0.29755 | 121.9299 | -122.1909 | -122.2366
967.1094 | 121.9849 | -121.8063 | 0.15106 | 0.0016785 | 0.018318 | 0.013321 | -0.0073336 | -0.0077566 | 0.061666 | 0.070511 | -8.9722 | 0.19684 | -122.1222 | 0.15564 | -121.5591 | -122.0215 | -0.27924 | -0.16937 | 0.20142 | -122.0856 | -0.31586 | 0.045776 | 112.8342 | 121.962 | -121.7102 | -0.27924 | 0.050354 | 113.15 | 121.5271 | 121.637 | 0.24719 | 122.0032 | 112.8342 | 122.0078 | -0.21515 | -0.27924 | 122.0032 | 112.8342 | -0.21515 | 0.24719 | 122.0078 | -122.2733 | -122.2366
968.8438 | 121.9345 | -121.7743 | 0.13733 | 0.0016785 | 0.017891 | 0.01439 | -0.011393 | -0.0066886 | 0.062735 | 0.070083 | -8.9401 | 0.17853 | -122.0856 | 0.1831 | -121.4859 | -121.9528 | -0.4715 | -0.17853 | 0.16479 | -122.0901 | -0.31128 | 0.041199 | 112.8342 | 121.9574 | -121.6232 | -0.31586 | 0.027466 | 113.1454 | 121.3028 | 121.5958 | 0.28839 | 121.9528 | 112.8342 | 121.9391 | -0.17853 | -0.31586 | 121.9528 | 112.8342 | -0.17853 | 0.28839 | 121.9391 | -122.2229 | -122.2275
970.5781 | 122.0444 | -121.7651 | 0.1236 | 0.0016785 | 0.018318 | 0.012467 | -0.010111 | -0.0088248 | 0.059744 | 0.069656 | -9.0363 | 0.19226 | -122.1313 | 0.10986 | -121.55 | -122.0352 | -0.21515 | -0.23804 | 0.20599 | -122.0901 | -0.36621 | 0.068665 | 112.7289 | 121.875 | -121.6736 | -0.32501 | 0.082398 | 113.0951 | 121.55 | 121.5271 | 0.21515 | 121.9574 | 112.7289 | 121.9711 | -0.27008 | -0.32501 | 121.9574 | 112.7289 | -0.27008 | 0.21515 | 121.9711 | -122.2549 | -122.2137
972.3125 | 121.9894 | -121.7789 | 0.12817 | 0.0016785 | 0.018318 | 0.010117 | -0.011393 | -0.0073294 | 0.061239 | 0.070297 | -9.0454 | 0.18768 | -122.1313 | 0.091553 | -121.5866 | -122.0535 | -0.3479 | -0.2655 | 0.20599 | -122.0901 | -0.35248 | 0.059509 | 112.7335 | 121.8704 | -121.7148 | -0.31128 | 0.07782 | 113.0859 | 121.431 | 121.5134 | 0.19226 | 121.9666 | 112.7335 | 121.9849 | -0.27466 | -0.31128 | 121.9666 | 112.7335 | -0.27466 | 0.19226 | 121.9849 | -122.2595 | -122.2183
973.9844 | 121.9894 | -121.7834 | 0.16937 | -0.02121 | 0.021309 | 0.01439 | -0.0092564 | -0.0071158 | 0.060812 | 0.070938 | -9.0179 | 0.21515 | -122.1222 | 0.10071 | -121.5775 | -122.0627 | -0.27008 | -0.26093 | 0.2243 | -122.1085 | -0.33875 | 0.045776 | 112.7655 | 121.8842 | -121.7468 | -0.32501 | 0.054931 | 113.1042 | 121.5134 | 121.5225 | 0.20599 | 121.9986 | 112.7655 | 122.0078 | -0.27924 | -0.32501 | 121.9986 | 112.7655 | -0.27924 | 0.20599 | 122.0078 | -122.2916 | -122.2778
975.7188 | 122.0581 | -121.7789 | 0.1236 | -0.013581 | 0.019173 | 0.010758 | -0.01417 | -0.0073294 | 0.063589 | 0.070938 | -8.9996 | 0.14648 | -122.0627 | 0.17853 | -121.4905 | -121.9894 | -0.36163 | -0.059509 | 0.19226 | -122.1359 | -0.28381 | 0.022888 | 112.7792 | 121.9574 | -121.6141 | -0.35706 | 0.068665 | 113.063 | 121.4172 | 121.7194 | 0.28839 | 121.9254 | 112.7792 | 121.9711 | -0.21057 | -0.35706 | 121.9254 | 112.7792 | -0.21057 | 0.28839 | 121.9711 | -122.1863 | -122.2595
977.4688 | 122.0993 | -121.7697 | 0.10986 | -0.005951 | 0.017464 | 0.0073401 | -0.011606 | -0.0096794 | 0.063589 | 0.068161 | -9.0912 | 0.18768 | -122.1405 | 0.07782 | -121.582 | -122.0947 | -0.21973 | -0.22888 | 0.22888 | -122.0947 | -0.37079 | 0.07782 | 112.6785 | 121.8475 | -121.6919 | -0.32501 | 0.11902 | 113.0493 | 121.55 | 121.5408 | 0.18768 | 121.9574 | 112.6785 | 121.9986 | -0.32501 | -0.32501 | 121.9574 | 112.6785 | -0.32501 | 0.18768 | 121.9986 | -122.2504 | -122.2046
979.1406 | 121.9986 | -121.8063 | 0.1236 | -0.005951 | 0.020454 | 0.016953 | -0.01182 | -0.0066886 | 0.061239 | 0.068802 | -9.0042 | 0.18768 | -122.1176 | 0.13733 | -121.5637 | -122.0261 | -0.29755 | -0.17395 | 0.18768 | -122.081 | -0.31128 | 0.064087 | 112.8021 | 121.9437 | -121.6873 | -0.27466 | 0.064087 | 113.1134 | 121.5088 | 121.6324 | 0.24261 | 121.994 | 112.8021 | 121.994 | -0.21973 | -0.27466 | 121.994 | 112.8021 | -0.21973 | 0.24261 | 121.994 | -122.2412 | -122.2046
980.8906 | 122.0078 | -121.788 | 0.13733 | -0.005951 | 0.0196 | 0.012894 | -0.0075474 | -0.0077566 | 0.062948 | 0.069656 | -9.0866 | 0.20142 | -122.1359 | 0.054932 | -121.6324 | -122.0764 | -0.39368 | -0.32959 | 0.21057 | -122.113 | -0.3479 | 0.064087 | 112.7014 | 121.843 | -121.7697 | -0.32501 | 0.073242 | 113.0493 | 121.3943 | 121.4584 | 0.15564 | 121.9894 | 112.7014 | 121.9986 | -0.28839 | -0.32501 | 121.9894 | 112.7014 | -0.28839 | 0.15564 | 121.9986 | -122.2733 | -122.2504
982.5781 | 122.0673 | -121.7514 | 0.10986 | -0.005951 | 0.019386 | 0.011612 | -0.016092 | -0.0086112 | 0.061239 | 0.069229 | -9.0454 | 0.16479 | -122.0581 | 0.17853 | -121.4813 | -121.9437 | -0.6546 | -0.20599 | 0.16937 | -122.0901 | -0.3067 | 0.054932 | 112.706 | 121.9299 | -121.5912 | -0.33875 | 0.05951 | 113.0127 | 121.0968 | 121.5454 | 0.27008 | 121.9162 | 112.706 | 121.9208 | -0.19226 | -0.33875 | 121.9162 | 112.706 | -0.19226 | 0.27008 | 121.9208 | -122.168 | -122.2
984.3125 | 122.0032 | -121.7697 | 0.14191 | 0.0016785 | 0.021309 | 0.015885 | -0.008829 | -0.008184 | 0.064016 | 0.070511 | -9.0729 | 0.18768 | -122.1268 | 0.054932 | -121.6141 | -122.0856 | -0.32501 | -0.3067 | 0.21515 | -122.113 | -0.35706 | 0.045776 | 112.6968 | 121.8246 | -121.756 | -0.34332 | 0.073242 | 113.0539 | 121.4447 | 121.463 | 0.15564 | 121.9574 | 112.6968 | 121.9849 | -0.31586 | -0.34332 | 121.9574 | 112.6968 | -0.31586 | 0.15564 | 121.9849 | -122.2687 | -122.2549
985.9844 | 122.0078 | -121.7926 | 0.12817 | -0.005951 | 0.017891 | 0.016739 | -0.0090426 | -0.0062614 | 0.059957 | 0.069443 | -9.0729 | 0.2243 | -122.1359 | 0.045776 | -121.6232 | -122.1085 | -0.35248 | -0.29755 | 0.20142 | -122.1359 | -0.34332 | 0.09613 | 112.7197 | 121.8384 | -121.7514 | -0.34332 | 0.073242 | 113.063 | 121.4401 | 121.4951 | 0.16937 | 122.0169 | 112.7197 | 121.994 | -0.31586 | -0.34332 | 122.0169 | 112.7197 | -0.31586 | 0.16937 | 121.994 | -122.2641 | -122.2641
987.7188 | 122.081 | -121.7468 | 0.10529 | -0.013581 | 0.015968 | 0.0096899 | -0.016092 | -0.0096794 | 0.064871 | 0.071792 | -9.0775 | 0.16937 | -122.0627 | 0.11902 | -121.5271 | -121.9986 | -0.53101 | -0.27466 | 0.1831 | -122.1176 | -0.31586 | 0.064087 | 112.6694 | 121.8658 | -121.6324 | -0.37079 | 0.077819 | 112.9852 | 121.2158 | 121.4722 | 0.21973 | 121.9162 | 112.6694 | 121.9299 | -0.25177 | -0.37079 | 121.9162 | 112.6694 | -0.25177 | 0.21973 | 121.9299 | -122.168 | -122.2229
989.3906 | 122.0444 | -121.7697 | 0.10986 | -0.005951 | 0.019813 | 0.013321 | -0.012461 | -0.010534 | 0.06423 | 0.067947 | -9.0225 | 0.15564 | -122.0718 | 0.20142 | -121.4722 | -121.9482 | -0.50812 | -0.14191 | 0.17853 | -122.0901 | -0.30212 | 0.045777 | 112.7472 | 121.9711 | -121.582 | -0.32044 | 0.068665 | 113.0493 | 121.2616 | 121.6278 | 0.29755 | 121.9254 | 112.7472 | 121.9482 | -0.17853 | -0.32044 | 121.9254 | 112.7472 | -0.17853 | 0.29755 | 121.9482 | -122.1817 | -122.2
991.0625 | 122.0947 | -121.7743 | 0.1236 | -0.013581 | 0.021736 | 0.012894 | -0.0092564 | -0.008184 | 0.062094 | 0.068588 | -9.1095 | 0.2243 | -122.1176 | 0.10986 | -121.5958 | -122.0764 | -0.34332 | -0.27924 | 0.19684 | -122.1176 | -0.34332 | 0.10071 | 112.6648 | 121.8842 | -121.7194 | -0.34332 | 0.073242 | 113.0081 | 121.431 | 121.4951 | 0.17853 | 121.9986 | 112.6648 | 121.9711 | -0.30212 | -0.34332 | 121.9986 | 112.6648 | -0.30212 | 0.17853 | 121.9711 | -122.2412 | -122.2412
992.8125 | 122.0078 | -121.756 | 0.13733 | -0.005951 | 0.021736 | 0.016312 | -0.0084018 | -0.0088248 | 0.05953 | 0.070297 | -9.1232 | 0.19684 | -122.1497 | 0.068665 | -121.6278 | -122.1085 | -0.38452 | -0.37079 | 0.21057 | -122.1176 | -0.39368 | 0.059509 | 112.6328 | 121.8246 | -121.7651 | -0.36163 | 0.073242 | 113.0264 | 121.3715 | 121.3852 | 0.12817 | 121.9528 | 112.6328 | 121.9666 | -0.35248 | -0.36163 | 121.9528 | 112.6328 | -0.35248 | 0.12817 | 121.9666 | -122.287 | -122.2549
994.5469 | 122.0215 | -121.7743 | 0.11902 | 0.0016785 | 0.015968 | 0.016526 | -0.015879 | -0.0083976 | 0.06423 | 0.069229 | -9.0591 | 0.16022 | -122.0581 | 0.14191 | -121.5317 | -121.994 | -0.53558 | -0.32501 | 0.17395 | -122.1176 | -0.28381 | 0.041198 | 112.7151 | 121.9162 | -121.6507 | -0.34332 | 0.054931 | 112.999 | 121.2387 | 121.4493 | 0.24262 | 121.9345 | 112.7151 | 121.9482 | -0.21973 | -0.34332 | 121.9345 | 112.7151 | -0.21973 | 0.24262 | 121.9482 | -122.1771 | -122.2366
996.2969 | 122.0123 | -121.7972 | 0.13275 | -0.013581 | 0.019386 | 0.010117 | -0.011606 | -0.0088248 | 0.062948 | 0.06987 | -9.0866 | 0.18768 | -122.1359 | 0.068665 | -121.6003 | -122.0764 | -0.40741 | -0.41199 | 0.21057 | -122.1634 | -0.33875 | 0.054932 | 112.7106 | 121.8658 | -121.7331 | -0.36621 | 0.07782 | 113.0493 | 121.3898 | 121.3852 | 0.19684 | 121.9849 | 112.7106 | 122.0078 | -0.27924 | -0.36621 | 121.9849 | 112.7106 | -0.27924 | 0.19684 | 122.0078 | -122.2687 | -122.2961
998.0312 | 122.0078 | -121.7926 | 0.13733 | 0.009308 | 0.020668 | 0.011612 | -0.0084018 | -0.008184 | 0.06423 | 0.070511 | -9.1003 | 0.20599 | -122.1313 | 0.082397 | -121.5958 | -122.0627 | -0.44403 | -0.37079 | 0.21057 | -122.0901 | -0.33875 | 0.068665 | 112.6923 | 121.875 | -121.7331 | -0.29755 | 0.073242 | 113.031 | 121.3486 | 121.4218 | 0.19684 | 121.9986 | 112.6923 | 122.0032 | -0.27008 | -0.29755 | 121.9986 | 112.6923 | -0.27008 | 0.19684 | 122.0032 | -122.2687 | -122.2275
999.7812 | 122.0123 | -121.7834 | 0.1236 | 0.0016785 | 0.018105 | 0.016099 | -0.014811 | -0.009252 | 0.065512 | 0.068588 | -9.0225 | 0.16937 | -122.0627 | 0.15106 | -121.5271 | -122.0032 | -0.58136 | -0.27924 | 0.17853 | -122.1176 | -0.27924 | 0.045777 | 112.7609 | 121.9345 | -121.6507 | -0.33417 | 0.054932 | 113.0402 | 121.2021 | 121.5042 | 0.25635 | 121.9528 | 112.7609 | 121.962 | -0.21973 | -0.33417 | 121.9528 | 112.7609 | -0.21973 | 0.25635 | 121.962 | -122.1863 | -122.2412
1001.5312 | 122.049 | -121.7743 | 0.13275 | -0.005951 | 0.018959 | 0.010544 | -0.015451 | -0.0088248 | 0.062307 | 0.068161 | -9.0958 | 0.16937 | -122.0947 | 0.13733 | -121.5363 | -122.0078 | -0.57678 | -0.38452 | 0.16479 | -122.0993 | -0.32044 | 0.036622 | 112.6785 | 121.9116 | -121.669 | -0.32501 | 0.032044 | 112.999 | 121.1975 | 121.3898 | 0.23804 | 121.9437 | 112.6785 | 121.9391 | -0.23346 | -0.32501 | 121.9437 | 112.6785 | -0.23346 | 0.23804 | 121.9391 | -122.2275 | -122.2321
1003.2188 | 122.0078 | -121.8109 | 0.13733 | 0.0016785 | 0.021522 | 0.013535 | -0.0064792 | -0.007543 | 0.062307 | 0.069656 | -9.1553 | 0.19226 | -122.1359 | 0.068665 | -121.637 | -122.1222 | -0.44861 | -0.737 | 0.21973 | -122.1085 | -0.32501 | 0.054932 | 112.6556 | 121.8796 | -121.7743 | -0.29755 | 0.082398 | 112.9807 | 121.3623 | 121.0739 | 0.17395 | 122.0032 | 112.6556 | 122.0306 | -0.31128 | -0.29755 | 122.0032 | 112.6556 | -0.31128 | 0.17395 | 122.0306 | -122.2733 | -122.2458
1004.9531 | 122.0535 | -121.7926 | 0.11444 | -0.013581 | 0.017891 | 0.011185 | -0.014811 | -0.01032 | 0.063376 | 0.070724 | -9.0775 | 0.15564 | -122.0901 | 0.20599 | -121.4676 | -121.962 | -0.61798 | -0.67291 | 0.17395 | -122.0856 | -0.29755 | 0.041199 | 112.7151 | 121.9986 | -121.582 | -0.29297 | 0.059509 | 113.0127 | 121.1746 | 121.1197 | 0.32501 | 121.9482 | 112.7151 | 121.9666 | -0.16937 | -0.29297 | 121.9482 | 112.7151 | -0.16937 | 0.32501 | 121.9666 | -122.2046 | -122.2
1006.625 | 122.081 | -121.7514 | 0.1236 | -0.02121 | 0.01725 | 0.013749 | -0.012247 | -0.010107 | 0.064016 | 0.069443 | -9.1187 | 0.15564 | -122.1039 | 0.16937 | -121.5179 | -122.0078 | -0.53558 | -0.7782 | 0.18768 | -122.1222 | -0.35248 | 0.032044 | 112.6328 | 121.9208 | -121.6415 | -0.37079 | 0.064087 | 112.9852 | 121.2158 | 120.9732 | 0.23346 | 121.907 | 112.6328 | 121.9391 | -0.25635 | -0.37079 | 121.907 | 112.6328 | -0.25635 | 0.23346 | 121.9391 | -122.2275 | -122.2458
1008.3125 | 122.1222 | -121.756 | 0.11902 | 0.0016785 | 0.018959 | 0.0094763 | -0.012247 | -0.0088248 | 0.063803 | 0.070724 | -9.2377 | 0.19226 | -122.1176 | 0.091553 | -121.5958 | -122.0764 | -0.4715 | -0.56305 | 0.2243 | -122.1176 | -0.36163 | 0.073242 | 112.5183 | 121.8475 | -121.7148 | -0.36163 | 0.10529 | 112.8799 | 121.2845 | 121.1929 | 0.16022 | 121.9482 | 112.5183 | 121.9803 | -0.32043 | -0.36163 | 121.9482 | 112.5183 | -0.32043 | 0.16022 | 121.9803 | -122.2366 | -122.2366
1010.0469 | 122.0673 | -121.7422 | 0.10529 | -0.005951 | 0.016823 | 0.0092627 | -0.013742 | -0.0077566 | 0.063162 | 0.070724 | -9.2194 | 0.16937 | -122.081 | 0.17395 | -121.4905 | -121.9666 | -1.0162 | -0.76446 | 0.17853 | -122.1039 | -0.33875 | 0.064087 | 112.5229 | 121.9162 | -121.5958 | -0.36163 | 0.073242 | 112.8616 | 120.726 | 120.9778 | 0.25177 | 121.9116 | 112.5229 | 121.9208 | -0.2243 | -0.36163 | 121.9116 | 112.5229 | -0.2243 | 0.25177 | 121.9208 | -122.1863 | -122.2092
1011.7812 | 122.0673 | -121.7743 | 0.11444 | -0.013581 | 0.017677 | 0.012467 | -0.013102 | -0.0096794 | 0.064871 | 0.068161 | -9.2377 | 0.15564 | -122.081 | 0.19226 | -121.4951 | -121.9711 | -1.2451 | -1.0849 | 0.16937 | -122.1039 | -0.3067 | 0.041199 | 112.5366 | 121.9666 | -121.6095 | -0.32959 | 0.054932 | 112.8433 | 120.5292 | 120.6894 | 0.27924 | 121.9299 | 112.5366 | 121.9437 | -0.19684 | -0.32959 | 121.9299 | 112.5366 | -0.19684 | 0.27924 | 121.9437 | -122.1954 | -122.2183
1013.4688 | 122.0306 | -121.7743 | 0.11902 | -0.013581 | 0.022591 | 0.013962 | -0.012461 | -0.0094656 | 0.062735 | 0.069015 | -9.2972 | 0.16022 | -122.0673 | 0.15106 | -121.5271 | -121.9986 | -1.4282 | -1.1261 | 0.18768 | -122.1039 | -0.29297 | 0.041198 | 112.4771 | 121.9254 | -121.6461 | -0.32959 | 0.068664 | 112.7701 | 120.3461 | 120.6482 | 0.24719 | 121.9345 | 112.4771 | 121.962 | -0.2243 | -0.32959 | 121.9345 | 112.4771 | -0.2243 | 0.24719 | 121.962 | -122.1863 | -122.2229
1015.2031 | 121.994 | -121.7743 | 0.14648 | -0.005951 | 0.020668 | 0.01503 | -0.0069064 | -0.004766 | 0.060598 | 0.067734 | -9.2468 | 0.18768 | -122.1313 | 0.13733 | -121.55 | -122.0535 | -1.3458 | -0.95673 | 0.19226 | -122.0764 | -0.35706 | 0.041199 | 112.5275 | 121.9116 | -121.6965 | -0.30212 | 0.045777 | 112.8845 | 120.4285 | 120.8176 | 0.2243 | 121.962 | 112.5275 | 121.9666 | -0.27924 | -0.30212 | 121.962 | 112.5275 | -0.27924 | 0.2243 | 121.9666 | -122.2778 | -122.2229
1016.9375 | 122.0673 | -121.7789 | 0.1236 | 0.0016785 | 0.017891 | 0.0092627 | -0.013956 | -0.0090384 | 0.060171 | 0.069656 | -9.2651 | 0.17395 | -122.0856 | 0.19226 | -121.4951 | -121.9894 | -1.767 | -0.81482 | 0.17395 | -122.0764 | -0.3067 | 0.050354 | 112.5137 | 121.9711 | -121.6187 | -0.29755 | 0.050354 | 112.8204 | 120.0119 | 120.9641 | 0.28381 | 121.9528 | 112.5137 | 121.9528 | -0.21057 | -0.29755 | 121.9528 | 112.5137 | -0.21057 | 0.28381 | 121.9528 | -122.2092 | -122.2
1018.6875 | 122.0078 | -121.7697 | 0.13275 | 0.0016785 | 0.018105 | 0.016526 | -0.010324 | -0.0060478 | 0.060385 | 0.068588 | -9.343 | 0.19684 | -122.1497 | 0.07782 | -121.6141 | -122.0901 | -2.3117 | -0.68207 | 0.20142 | -122.0993 | -0.37994 | 0.064087 | 112.4268 | 121.8475 | -121.7468 | -0.32959 | 0.068665 | 112.8067 | 119.458 | 121.0876 | 0.15564 | 121.9666 | 112.4268 | 121.9711 | -0.32044 | -0.32959 | 121.9666 | 112.4268 | -0.32044 | 0.15564 | 121.9711 | -122.2824 | -122.2321
1020.4375 | 122.0444 | -121.788 | 0.12817 | -0.013581 | 0.017464 | 0.013535 | -0.013315 | -0.0086112 | 0.060171 | 0.070083 | -9.2377 | 0.15106 | -122.049 | 0.20599 | -121.4767 | -121.9666 | -2.6093 | -0.47607 | 0.17395 | -122.0901 | -0.26093 | 0.022888 | 112.5504 | 121.994 | -121.6049 | -0.30212 | 0.045776 | 112.8113 | 119.1788 | 121.312 | 0.31128 | 121.9391 | 112.5504 | 121.962 | -0.17853 | -0.30212 | 121.9391 | 112.5504 | -0.17853 | 0.31128 | 121.962 | -122.1771 | -122.2183
1022.125 | 122.0764 | -121.7606 | 0.11902 | -0.013581 | 0.018745 | 0.015244 | -0.010752 | -0.010107 | 0.062094 | 0.070083 | -9.256 | 0.16479 | -122.113 | 0.15564 | -121.5179 | -122.0261 | -2.6459 | -0.55847 | 0.18768 | -122.1313 | -0.35248 | 0.045776 | 112.5046 | 121.9162 | -121.637 | -0.37079 | 0.068664 | 112.8571 | 119.1147 | 121.2021 | 0.24262 | 121.9254 | 112.5046 | 121.9482 | -0.2655 | -0.37079 | 121.9254 | 112.5046 | -0.2655 | 0.24262 | 121.9482 | -122.2321 | -122.2504
1023.875 | 121.9711 | -121.8201 | 0.16022 | -0.005951 | 0.017891 | 0.015244 | -0.012461 | -0.0071158 | 0.064657 | 0.06987 | -9.1782 | 0.13275 | -122.0764 | 0.20599 | -121.5042 | -121.9574 | -2.5314 | -0.50354 | 0.15106 | -122.0764 | -0.25635 | -0.027466 | 112.6419 | 122.0261 | -121.6644 | -0.25635 | -0.009155 | 112.8983 | 119.2886 | 121.3165 | 0.31586 | 121.9528 | 112.6419 | 121.9711 | -0.13733 | -0.25635 | 121.9528 | 112.6419 | -0.13733 | 0.31586 | 121.9711 | -122.2366 | -122.2366
1025.5469 | 122.0856 | -121.7743 | 0.09613 | -0.005951 | 0.017464 | 0.012894 | -0.013529 | -0.0096794 | 0.063589 | 0.073288 | -9.2697 | 0.16022 | -122.0901 | 0.16937 | -121.4996 | -121.9757 | -2.4399 | -0.52185 | 0.16937 | -122.1085 | -0.31586 | 0.064087 | 112.5046 | 121.9437 | -121.5958 | -0.33417 | 0.073243 | 112.8204 | 119.3344 | 121.2524 | 0.27466 | 121.9345 | 112.5046 | 121.9437 | -0.20142 | -0.33417 | 121.9345 | 112.5046 | -0.20142 | 0.27466 | 121.9437 | -122.1863 | -122.2046
1027.2812 | 121.9849 | -121.8109 | 0.15564 | -0.005951 | 0.015541 | 0.0099037 | -0.013102 | -0.010534 | 0.062735 | 0.070297 | -9.2331 | 0.15564 | -122.113 | 0.1831 | -121.5042 | -121.9711 | -2.6459 | -0.54474 | 0.16479 | -122.0764 | -0.30212 | 0 | 112.5778 | 121.994 | -121.6599 | -0.2655 | 0.009155 | 112.8799 | 119.165 | 121.2662 | 0.3067 | 121.9666 | 112.5778 | 121.9757 | -0.16022 | -0.2655 | 121.9666 | 112.5778 | -0.16022 | 0.3067 | 121.9757 | -122.2687 | -122.2321
1028.9531 | 122.0947 | -121.7834 | 0.13733 | -0.005951 | 0.019386 | 0.012681 | -0.0090426 | -0.0096794 | 0.061453 | 0.069443 | -9.3338 | 0.21515 | -122.1359 | 0.091553 | -121.6049 | -122.1085 | -2.4628 | -0.62714 | 0.22888 | -122.1222 | -0.35248 | 0.07782 | 112.4496 | 121.875 | -121.7422 | -0.33875 | 0.091553 | 112.8021 | 119.3207 | 121.1563 | 0.17853 | 121.9986 | 112.4496 | 122.0123 | -0.32501 | -0.33875 | 121.9986 | 112.4496 | -0.32501 | 0.17853 | 122.0123 | -122.2733 | -122.2595
1030.6875 | 122.0764 | -121.7697 | 0.10071 | -0.013581 | 0.018105 | 0.011826 | -0.015665 | -0.0094656 | 0.063376 | 0.069015 | -9.4299 | 0.17395 | -122.081 | 0.17395 | -121.4996 | -121.9894 | -2.4673 | -1.2726 | 0.18768 | -122.1222 | -0.31128 | 0.073242 | 112.3398 | 121.9437 | -121.6003 | -0.35248 | 0.086975 | 112.6511 | 119.3024 | 120.4971 | 0.27008 | 121.9437 | 112.3398 | 121.9574 | -0.21973 | -0.35248 | 121.9437 | 112.3398 | -0.21973 | 0.27008 | 121.9574 | -122.1817 | -122.2229
1032.4219 | 122.0169 | -121.7834 | 0.13275 | -0.013581 | 0.020882 | 0.015244 | -0.0058384 | -0.0066886 | 0.06188 | 0.070297 | -9.4711 | 0.18768 | -122.1725 | 0.082397 | -121.6461 | -122.1268 | -3.0075 | -1.7303 | 0.20142 | -122.1176 | -0.3891 | 0.054932 | 112.3123 | 121.8658 | -121.7789 | -0.33417 | 0.068665 | 112.7014 | 118.7759 | 120.0531 | 0.13733 | 121.9711 | 112.3123 | 121.9849 | -0.34332 | -0.33417 | 121.9711 | 112.3123 | -0.34332 | 0.13733 | 121.9849 | -122.3053 | -122.2504
1034.1562 | 122.0123 | -121.7926 | 0.13275 | -0.005951 | 0.018318 | 0.012894 | -0.0081882 | -0.0054068 | 0.059744 | 0.070297 | -9.5169 | 0.19226 | -122.1725 | 0.082397 | -121.6324 | -122.113 | -3.9185 | -2.0462 | 0.20142 | -122.0947 | -0.37994 | 0.05951 | 112.2757 | 121.875 | -121.7651 | -0.30212 | 0.068665 | 112.6556 | 117.8741 | 119.7464 | 0.16022 | 121.9849 | 112.2757 | 121.994 | -0.32043 | -0.30212 | 121.9849 | 112.2757 | -0.32043 | 0.16022 | 121.994 | -122.3053 | -122.2275
1035.9062 | 122.0306 | -121.7926 | 0.14191 | 0.0016785 | 0.018959 | 0.010544 | -0.0092564 | -0.0071158 | 0.062307 | 0.071579 | -9.6268 | 0.19684 | -122.1359 | 0.054932 | -121.6141 | -122.1039 | -3.5156 | -2.4078 | 0.21057 | -122.1176 | -0.34332 | 0.054931 | 112.1658 | 121.8475 | -121.756 | -0.32501 | 0.068664 | 112.5092 | 118.277 | 119.3848 | 0.17853 | 121.9894 | 112.1658 | 122.0032 | -0.31128 | -0.32501 | 121.9894 | 112.1658 | -0.31128 | 0.17853 | 122.0032 | -122.2778 | -122.2595
1037.5781 | 122.0123 | -121.8109 | 0.14648 | -0.013581 | 0.021736 | 0.01503 | -0.010324 | -0.0060478 | 0.060385 | 0.06987 | -9.6817 | 0.20599 | -122.1176 | 0.068665 | -121.6003 | -122.0993 | -3.5202 | -2.0462 | 0.21515 | -122.1359 | -0.3067 | 0.05951 | 112.1292 | 121.8796 | -121.7468 | -0.32501 | 0.068665 | 112.4359 | 118.2907 | 119.7647 | 0.21057 | 122.0169 | 112.1292 | 122.0261 | -0.28839 | -0.32501 | 122.0169 | 112.1292 | -0.28839 | 0.21057 | 122.0261 | -122.2641 | -122.2824
1039.3125 | 121.962 | -121.7789 | 0.13275 | -0.013581 | 0.017036 | 0.016953 | -0.013529 | -0.0071158 | 0.062094 | 0.070511 | -9.7275 | 0.17853 | -122.113 | 0.15106 | -121.5179 | -121.9894 | -4.0604 | -2.0508 | 0.17853 | -122.0993 | -0.33417 | 0.045777 | 112.0514 | 121.9299 | -121.6507 | -0.32043 | 0.045777 | 112.3856 | 117.7185 | 119.7281 | 0.26093 | 121.9574 | 112.0514 | 121.9574 | -0.21057 | -0.32043 | 121.9574 | 112.0514 | -0.21057 | 0.26093 | 121.9574 | -122.2458 | -122.2321
1040.9844 | 121.962 | -121.8155 | 0.14191 | -0.005951 | 0.018745 | 0.018876 | -0.015665 | -0.010747 | 0.065298 | 0.071365 | -9.7687 | 0.15106 | -122.0993 | 0.16937 | -121.5088 | -121.9711 | -3.4378 | -1.9363 | 0.16022 | -122.113 | -0.28381 | 0.009155 | 112.0468 | 121.9849 | -121.6507 | -0.29755 | 0.01831 | 112.3306 | 118.3777 | 119.8792 | 0.3067 | 121.9666 | 112.0468 | 121.9757 | -0.15564 | -0.29755 | 121.9666 | 112.0468 | -0.15564 | 0.3067 | 121.9757 | -122.2412 | -122.2549
1042.7188 | 121.9894 | -121.8018 | 0.15106 | -0.005951 | 0.018959 | 0.014603 | -0.0084018 | -0.0069022 | 0.061239 | 0.069443 | -9.7412 | 0.1831 | -122.1451 | 0.064087 | -121.6187 | -122.1039 | -3.2547 | -2.1378 | 0.20599 | -122.0993 | -0.34332 | 0.032043 | 112.0605 | 121.8658 | -121.7697 | -0.29755 | 0.054932 | 112.4039 | 118.5471 | 119.664 | 0.18311 | 121.9849 | 112.0605 | 122.0078 | -0.30212 | -0.29755 | 121.9849 | 112.0605 | -0.30212 | 0.18311 | 122.0078 | -122.2961 | -122.2504
1044.4688 | 122.0078 | -121.8018 | 0.15106 | -0.005951 | 0.019386 | 0.017594 | -0.0090426 | -0.006475 | 0.062521 | 0.069229 | -9.2926 | 0.1831 | -122.1313 | 0.036621 | -121.6232 | -122.1085 | -3.1494 | -2.2293 | 0.20142 | -122.1268 | -0.32959 | 0.032043 | 112.5092 | 121.8384 | -121.7743 | -0.32501 | 0.050354 | 112.8387 | 118.6523 | 119.5724 | 0.17853 | 121.9849 | 112.5092 | 122.0032 | -0.3067 | -0.32501 | 121.9849 | 112.5092 | -0.3067 | 0.17853 | 122.0032 | -122.2824 | -122.2778
1046.2188 | 122.0169 | -121.7972 | 0.1236 | -0.013581 | 0.020027 | 0.015885 | -0.011393 | -0.007543 | 0.062307 | 0.068802 | -9.4849 | 0.19226 | -122.1085 | 0.027466 | -121.6049 | -122.0856 | -3.2501 | -2.417 | 0.20599 | -122.113 | -0.31128 | 0.068665 | 112.3123 | 121.8246 | -121.7285 | -0.31586 | 0.082398 | 112.6236 | 118.5471 | 119.3802 | 0.19226 | 121.9894 | 112.3123 | 122.0032 | -0.28839 | -0.31586 | 121.9894 | 112.3123 | -0.28839 | 0.19226 | 122.0032 | -122.2321 | -122.2366
1047.9688 | 122.0993 | -121.7789 | 0.12817 | -0.005951 | 0.019813 | 0.012253 | -0.013102 | -0.0066886 | 0.061239 | 0.070511 | -9.5032 | 0.19684 | -122.1497 | 0.041199 | -121.5912 | -122.0901 | -3.4561 | -2.6688 | 0.2243 | -122.113 | -0.37079 | 0.068664 | 112.2757 | 121.8201 | -121.7194 | -0.33417 | 0.09613 | 112.6465 | 118.3228 | 119.1101 | 0.18768 | 121.9757 | 112.2757 | 122.0032 | -0.31128 | -0.33417 | 121.9757 | 112.2757 | -0.31128 | 0.18768 | 122.0032 | -122.2778 | -122.2412
1049.6562 | 121.9711 | -121.788 | 0.14648 | -0.005951 | 0.019813 | 0.015671 | -0.01182 | -0.0060478 | 0.063162 | 0.068374 | -9.3842 | 0.14648 | -122.0718 | 0.15564 | -121.4951 | -121.962 | -3.1357 | -2.8473 | 0.17853 | -122.0535 | -0.28381 | 0 | 112.4039 | 121.9437 | -121.6415 | -0.2655 | 0.032044 | 112.6877 | 118.6523 | 118.9407 | 0.29297 | 121.9345 | 112.4039 | 121.9666 | -0.17395 | -0.2655 | 121.9345 | 112.4039 | -0.17395 | 0.29297 | 121.9666 | -122.2183 | -122.2
1051.4062 | 121.9803 | -121.8018 | 0.13275 | 0.0016785 | 0.021309 | 0.015885 | -0.0092564 | -0.0079704 | 0.064444 | 0.070938 | -9.5627 | 0.17395 | -122.113 | 0.10529 | -121.5271 | -122.0032 | -3.6484 | -3.1677 | 0.1831 | -122.113 | -0.31128 | 0.041199 | 112.2391 | 121.907 | -121.6599 | -0.31128 | 0.050354 | 112.5504 | 118.1534 | 118.634 | 0.27466 | 121.9757 | 112.2391 | 121.9849 | -0.20142 | -0.31128 | 121.9757 | 112.2391 | -0.20142 | 0.27466 | 121.9849 | -122.2458 | -122.2458
1053.1562 | 121.9711 | -121.8292 | 0.14648 | -0.005951 | 0.01725 | 0.011399 | -0.01417 | -0.007543 | 0.062948 | 0.068374 | -9.462 | 0.13275 | -122.1039 | 0.16022 | -121.4951 | -121.9666 | -3.2959 | -3.2639 | 0.15564 | -122.0444 | -0.27466 | -0.013733 | 112.3672 | 121.9894 | -121.6415 | -0.21515 | 0.009156 | 112.6419 | 118.5333 | 118.5654 | 0.33417 | 121.962 | 112.3672 | 121.9849 | -0.13733 | -0.21515 | 121.962 | 112.3672 | -0.13733 | 0.33417 | 121.9849 | -122.2504 | -122.1909
1054.9062 | 122.0535 | -121.7606 | 0.1236 | -0.005951 | 0.01725 | 0.0056311 | -0.014811 | -0.0088248 | 0.062521 | 0.068802 | -9.4757 | 0.16479 | -122.0764 | 0.14191 | -121.4859 | -121.9528 | -3.3142 | -2.9892 | 0.16022 | -122.0947 | -0.31586 | 0.041199 | 112.2849 | 121.9025 | -121.6095 | -0.33417 | 0.036621 | 112.6007 | 118.4463 | 118.7714 | 0.27466 | 121.9254 | 112.2849 | 121.9208 | -0.19226 | -0.33417 | 121.9254 | 112.2849 | -0.19226 | 0.27466 | 121.9208 | -122.2 | -122.2183
1056.6406 | 122.0032 | -121.8201 | 0.13275 | -0.005951 | 0.018959 | 0.017808 | -0.011606 | -0.0069022 | 0.06423 | 0.068161 | -9.5078 | 0.15106 | -122.1085 | 0.13275 | -121.5271 | -121.9757 | -3.6987 | -3.035 | 0.16479 | -122.0993 | -0.28839 | 0.018311 | 112.3123 | 121.9528 | -121.6599 | -0.27924 | 0.032044 | 112.6007 | 118.1213 | 118.7851 | 0.29297 | 121.9711 | 112.3123 | 121.9849 | -0.15564 | -0.27924 | 121.9711 | 112.3123 | -0.15564 | 0.29297 | 121.9849 | -122.2412 | -122.2321
1058.3438 | 121.9986 | -121.8063 | 0.14648 | -0.005951 | 0.017677 | 0.013321 | -0.010965 | -0.011175 | 0.062094 | 0.069015 | -9.7137 | 0.19226 | -122.1405 | 0.064087 | -121.5912 | -122.0581 | -3.9734 | -3.8589 | 0.1831 | -122.1039 | -0.33417 | 0.045777 | 112.0926 | 121.8704 | -121.7377 | -0.29755 | 0.036621 | 112.4268 | 117.8329 | 117.9474 | 0.21515 | 121.9986 | 112.0926 | 121.9894 | -0.25177 | -0.29755 | 121.9986 | 112.0926 | -0.25177 | 0.21515 | 121.9894 | -122.287 | -122.2504
1060.0781 | 122.0993 | -121.7606 | 0.10986 | -0.02121 | 0.018745 | 0.0090491 | -0.01417 | -0.009252 | 0.065084 | 0.06752 | -9.6497 | 0.16022 | -122.0856 | 0.086975 | -121.5546 | -122.0306 | -4.1153 | -3.8864 | 0.16479 | -122.113 | -0.32501 | 0.050354 | 112.1109 | 121.8475 | -121.6644 | -0.35248 | 0.054932 | 112.4359 | 117.6453 | 117.8741 | 0.20599 | 121.9208 | 112.1109 | 121.9254 | -0.27008 | -0.35248 | 121.9208 | 112.1109 | -0.27008 | 0.20599 | 121.9254 | -122.1954 | -122.2229
1061.8281 | 122.0673 | -121.7468 | 0.11902 | -0.02121 | 0.018959 | 0.0099037 | -0.01417 | -0.0096794 | 0.064444 | 0.069229 | -9.613 | 0.15106 | -122.1085 | 0.14648 | -121.4767 | -121.9711 | -4.5044 | -3.6438 | 0.17853 | -122.1313 | -0.36163 | 0.032043 | 112.1338 | 121.8933 | -121.5958 | -0.38452 | 0.059509 | 112.4954 | 117.2424 | 118.103 | 0.27008 | 121.8979 | 112.1338 | 121.9254 | -0.2243 | -0.38452 | 121.8979 | 112.1338 | -0.2243 | 0.27008 | 121.9254 | -122.2275 | -122.2504
1063.5156 | 121.9666 | -121.8063 | 0.13733 | -0.013581 | 0.018532 | 0.013535 | -0.010111 | -0.0083976 | 0.062094 | 0.071792 | -9.4894 | 0.14191 | -122.0993 | 0.15564 | -121.5225 | -121.962 | -4.7104 | -3.4515 | 0.16479 | -122.0627 | -0.29297 | 0.004578 | 112.3169 | 121.962 | -121.6599 | -0.25635 | 0.027466 | 112.6099 | 117.0959 | 118.3548 | 0.28381 | 121.9482 | 112.3169 | 121.9711 | -0.15564 | -0.25635 | 121.9482 | 112.3169 | -0.15564 | 0.28381 | 121.9711 | -122.2366 | -122.2
1065.25 | 122.1176 | -121.756 | 0.10986 | 0.0016785 | 0.020241 | 0.013108 | -0.011179 | -0.0077566 | 0.06188 | 0.069443 | -9.5993 | 0.1831 | -122.1359 | 0.041199 | -121.6095 | -122.1085 | -4.2847 | -3.186 | 0.21515 | -122.1176 | -0.37994 | 0.073242 | 112.1567 | 121.7972 | -121.7194 | -0.36163 | 0.10529 | 112.5366 | 117.4713 | 118.5699 | 0.14648 | 121.9391 | 112.1567 | 121.9711 | -0.35248 | -0.36163 | 121.9391 | 112.1567 | -0.35248 | 0.14648 | 121.9711 | -122.2458 | -122.2275
1066.9844 | 121.9803 | -121.788 | 0.14191 | -0.013581 | 0.020027 | 0.012253 | -0.012247 | -0.0077566 | 0.062094 | 0.070511 | -9.581 | 0.16022 | -122.0856 | 0.15564 | -121.5088 | -121.9666 | -4.7424 | -3.392 | 0.14648 | -122.0856 | -0.29755 | 0.01831 | 112.207 | 121.9437 | -121.6507 | -0.29755 | 0.004577 | 112.5046 | 117.0456 | 118.396 | 0.27924 | 121.9482 | 112.207 | 121.9345 | -0.17853 | -0.29755 | 121.9482 | 112.207 | -0.17853 | 0.27924 | 121.9345 | -122.2275 | -122.2275
1068.6719 | 121.9894 | -121.8246 | 0.13733 | 0.0016785 | 0.019386 | 0.016953 | -0.0084018 | -0.008184 | 0.06423 | 0.070724 | -9.5261 | 0.18768 | -122.1405 | 0.091553 | -121.5637 | -122.0398 | -4.1565 | -3.2043 | 0.18768 | -122.1405 | -0.31586 | 0.050354 | 112.2986 | 121.9162 | -121.701 | -0.31586 | 0.050354 | 112.6144 | 117.6682 | 118.6203 | 0.26093 | 122.0123 | 112.2986 | 122.0123 | -0.21515 | -0.31586 | 122.0123 | 112.2986 | -0.21515 | 0.26093 | 122.0123 | -122.2778 | -122.2778
1070.4219 | 122.0444 | -121.8063 | 0.1236 | -0.005951 | 0.019386 | 0.014603 | -0.0084018 | -0.0073294 | 0.064657 | 0.06987 | -9.7458 | 0.19226 | -122.1405 | 0.009155 | -121.6324 | -122.113 | -4.4266 | -3.6346 | 0.21057 | -122.1359 | -0.33417 | 0.068665 | 112.0605 | 121.8155 | -121.756 | -0.32959 | 0.086975 | 112.3947 | 117.3798 | 118.1717 | 0.17395 | 121.9986 | 112.0605 | 122.0169 | -0.3067 | -0.32959 | 121.9986 | 112.0605 | -0.3067 | 0.17395 | 122.0169 | -122.2641 | -122.2595
1072.1562 | 122.0764 | -121.7972 | 0.12817 | 0.009308 | 0.018959 | 0.015458 | -0.013102 | -0.0079704 | 0.061666 | 0.068588 | -9.7229 | 0.20599 | -122.1405 | 0.041199 | -121.5775 | -122.0673 | -4.8614 | -4.0649 | 0.20142 | -122.1451 | -0.34332 | 0.07782 | 112.0743 | 121.8384 | -121.7056 | -0.3479 | 0.073242 | 112.4176 | 116.9357 | 117.7322 | 0.21973 | 122.0032 | 112.0743 | 121.9986 | -0.27008 | -0.3479 | 122.0032 | 112.0743 | -0.27008 | 0.21973 | 121.9986 | -122.2687 | -122.2733
1073.9219 | 122.0718 | -121.7651 | 0.10986 | 0.0016785 | 0.019173 | 0.0094763 | -0.01716 | -0.009252 | 0.063376 | 0.06987 | -9.6497 | 0.14191 | -122.0947 | 0.1236 | -121.4676 | -121.9574 | -5.4886 | -3.9917 | 0.17395 | -122.1085 | -0.32959 | 0.032044 | 112.1155 | 121.8887 | -121.5775 | -0.34332 | 0.064087 | 112.4451 | 116.2766 | 117.7734 | 0.29755 | 121.907 | 112.1155 | 121.9391 | -0.19226 | -0.34332 | 121.907 | 112.1155 | -0.19226 | 0.29755 | 121.9391 | -122.2046 | -122.2183
1075.6562 | 122.0993 | -121.7651 | 0.11902 | -0.005951 | 0.018105 | 0.010544 | -0.016092 | -0.0079704 | 0.062307 | 0.070511 | -9.6405 | 0.16937 | -122.081 | 0.086975 | -121.5179 | -121.9986 | -5.8136 | -4.2389 | 0.16479 | -122.1588 | -0.31586 | 0.050354 | 112.1246 | 121.8521 | -121.637 | -0.39368 | 0.045776 | 112.4405 | 115.9515 | 117.5262 | 0.24719 | 121.9345 | 112.1246 | 121.9299 | -0.23346 | -0.39368 | 121.9345 | 112.1246 | -0.23346 | 0.24719 | 121.9299 | -122.2 | -122.2778
1077.3281 | 122.0764 | -121.7606 | 0.10529 | -0.028839 | 0.019813 | 0.010758 | -0.013315 | -0.009252 | 0.061026 | 0.069656 | -9.6634 | 0.13275 | -122.0901 | 0.11902 | -121.5042 | -121.994 | -6.1523 | -5.1224 | 0.19684 | -122.1176 | -0.32959 | 0.027465 | 112.0972 | 121.8796 | -121.6095 | -0.35706 | 0.091552 | 112.4268 | 115.6082 | 116.6382 | 0.25635 | 121.8933 | 112.0972 | 121.9574 | -0.23346 | -0.35706 | 121.8933 | 112.0972 | -0.23346 | 0.25635 | 121.9574 | -122.1954 | -122.2229
1079.0625 | 121.9849 | -121.8292 | 0.15106 | -0.013581 | 0.018318 | 0.013962 | -0.0090426 | -0.0079704 | 0.059744 | 0.068588 | -9.7641 | 0.18768 | -122.1451 | 0.11444 | -121.55 | -122.0535 | -6.1615 | -6.0974 | 0.18768 | -122.0947 | -0.31586 | 0.036621 | 112.0651 | 121.9437 | -121.701 | -0.2655 | 0.036621 | 112.381 | 115.6677 | 115.7318 | 0.27924 | 122.0169 | 112.0651 | 122.0169 | -0.2243 | -0.2655 | 122.0169 | 112.0651 | -0.2243 | 0.27924 | 122.0169 | -122.2961 | -122.2458
1080.7969 | 122.0993 | -121.7468 | 0.1236 | -0.02121 | 0.018105 | 0.014176 | -0.0090426 | -0.0066886 | 0.061453 | 0.067093 | -9.938 | 0.20599 | -122.1405 | 0.041199 | -121.5958 | -122.0856 | -6.0471 | -6.1798 | 0.20142 | -122.1313 | -0.39368 | 0.082398 | 111.8088 | 121.788 | -121.7194 | -0.38452 | 0.07782 | 112.2025 | 115.6998 | 115.567 | 0.15106 | 121.9528 | 111.8088 | 121.9482 | -0.33875 | -0.38452 | 121.9528 | 111.8088 | -0.33875 | 0.15106 | 121.9482 | -122.2641 | -122.2549
1082.4688 | 122.113 | -121.7926 | 0.12817 | -0.02121 | 0.017891 | 0.0099037 | -0.013742 | -0.0071158 | 0.05953 | 0.070083 | -9.8053 | 0.17395 | -122.1268 | 0.059509 | -121.5866 | -122.0764 | -6.7932 | -6.546 | 0.20599 | -122.113 | -0.33417 | 0.045776 | 111.9873 | 121.8521 | -121.7148 | -0.32043 | 0.07782 | 112.3215 | 114.9994 | 115.2466 | 0.20599 | 121.9666 | 111.9873 | 121.9986 | -0.28381 | -0.32043 | 121.9666 | 111.9873 | -0.28381 | 0.20599 | 121.9986 | -122.2549 | -122.2412
1084.2188 | 121.994 | -121.8292 | 0.14648 | 0.0016785 | 0.019173 | 0.013108 | -0.015238 | -0.008184 | 0.06188 | 0.06987 | -9.4849 | 0.15564 | -122.081 | 0.12817 | -121.5042 | -121.9757 | -6.8573 | -7.0175 | 0.15106 | -122.1176 | -0.25177 | 0.009156 | 112.3444 | 121.9574 | -121.6507 | -0.28839 | 0.004578 | 112.5961 | 114.9719 | 114.8117 | 0.32501 | 121.9849 | 112.3444 | 121.9803 | -0.14648 | -0.28839 | 121.9849 | 112.3444 | -0.14648 | 0.32501 | 121.9803 | -122.2275 | -122.2641
1085.9531 | 121.9757 | -121.7926 | 0.13733 | -0.013581 | 0.019173 | 0.012467 | -0.0092564 | -0.006475 | 0.064444 | 0.069443 | -9.5261 | 0.16937 | -122.1451 | 0.11444 | -121.5363 | -122.0123 | -6.7841 | -6.6605 | 0.17395 | -122.0993 | -0.35248 | 0.032044 | 112.2665 | 121.907 | -121.6736 | -0.3067 | 0.036621 | 112.619 | 115.0085 | 115.1321 | 0.25635 | 121.962 | 112.2665 | 121.9666 | -0.21973 | -0.3067 | 121.962 | 112.2665 | -0.21973 | 0.25635 | 121.9666 | -122.2824 | -122.2366
1087.625 | 122.0352 | -121.8063 | 0.13733 | -0.013581 | 0.022163 | 0.015671 | -0.0086154 | -0.0094656 | 0.061239 | 0.070083 | -9.5078 | 0.19684 | -122.1497 | 0.018311 | -121.6553 | -122.1451 | -6.5002 | -6.4728 | 0.20599 | -122.168 | -0.34332 | 0.059509 | 112.2986 | 121.8246 | -121.7926 | -0.36163 | 0.068665 | 112.6419 | 115.3061 | 115.3336 | 0.15106 | 122.0032 | 112.2986 | 122.0123 | -0.33875 | -0.36163 | 122.0032 | 112.2986 | -0.33875 | 0.15106 | 122.0123 | -122.287 | -122.3053
1089.375 | 122.0993 | -121.7926 | 0.10071 | -0.005951 | 0.017036 | 0.010758 | -0.015024 | -0.009252 | 0.061026 | 0.068802 | -9.1553 | 0.16479 | -122.113 | 0.11444 | -121.5363 | -122.0215 | -6.1066 | -6.5552 | 0.1831 | -122.1405 | -0.32043 | 0.064087 | 112.6373 | 121.907 | -121.637 | -0.3479 | 0.082397 | 112.9578 | 115.686 | 115.2374 | 0.25635 | 121.9574 | 112.6373 | 121.9757 | -0.22888 | -0.3479 | 121.9574 | 112.6373 | -0.22888 | 0.25635 | 121.9757 | -122.2137 | -122.2412
1091.1094 | 122.0444 | -121.8155 | 0.13275 | 0.0016785 | 0.018532 | 0.010758 | -0.016306 | -0.010534 | 0.064657 | 0.069656 | -9.1919 | 0.14191 | -122.0856 | 0.16937 | -121.4722 | -121.9666 | -5.6946 | -6.8161 | 0.17853 | -122.1176 | -0.27008 | 0.009156 | 112.6236 | 121.9849 | -121.6049 | -0.30212 | 0.045777 | 112.8937 | 116.1209 | 114.9994 | 0.34332 | 121.9574 | 112.6236 | 121.994 | -0.15106 | -0.30212 | 121.9574 | 112.6236 | -0.15106 | 0.34332 | 121.994 | -122.2183 | -122.2504
1092.8594 | 122.0718 | -121.8109 | 0.11902 | -0.005951 | 0.019386 | 0.0092627 | -0.012888 | -0.008184 | 0.060812 | 0.068588 | -9.1415 | 0.14648 | -122.0947 | 0.15106 | -121.4996 | -121.9803 | -5.777 | -6.8893 | 0.16937 | -122.113 | -0.28381 | 0.027465 | 112.6694 | 121.962 | -121.6187 | -0.30212 | 0.050354 | 112.9532 | 116.0339 | 114.9216 | 0.31128 | 121.9574 | 112.6694 | 121.9803 | -0.16937 | -0.30212 | 121.9574 | 112.6694 | -0.16937 | 0.31128 | 121.9803 | -122.2137 | -122.2321
1094.5469 | 121.9894 | -121.8155 | 0.11444 | 0.0016785 | 0.018318 | 0.011612 | 0.0027066 | 0.059321 | -0.0060519 | 0.083328 | -121.7743 | 0.15564 | -122.1268 | -121.6965 | -0.10071 | 0.050354 | -5.9372 | -7.4203 | 0.19684 | -122.113 | -0.31128 | 0.041199 | 0.041199 | 0.11902 | -0.21515 | -0.29755 | 0.082397 | 0.35248 | 115.8783 | 114.3951 | 121.7148 | 121.9711 | 0.041199 | 122.0123 | 121.8658 | -0.29755 | 121.9711 | 0.041199 | 121.8658 | 121.7148 | 122.0123 | -122.2412 | -122.2275
1096.2812 | 122.0123 | -121.8292 | 0.1236 | 0.009308 | 0.017677 | 0.01503 | 0.00527 | 0.060603 | -0.0081881 | 0.079483 | -121.7377 | 0.16022 | -122.1405 | -121.6507 | -0.045776 | 0.091553 | -5.4062 | -5.6442 | 0.21057 | -122.1222 | -0.31128 | 0.036621 | 0.091553 | 0.17853 | -0.16937 | -0.29297 | 0.086975 | 0.40283 | 116.423 | 116.185 | 121.7834 | 121.9894 | 0.091553 | 122.0398 | 121.9208 | -0.29297 | 121.9894 | 0.091553 | 121.9208 | 121.7834 | 122.0398 | -122.2641 | -122.2458
1098.0156 | 122.081 | -121.8201 | 0.11902 | -0.005951 | 0.01725 | 0.012253 | 0.0014248 | 0.059321 | -0.0075473 | 0.079483 | -121.788 | 0.14648 | -122.1313 | -121.6873 | -0.054932 | 0.068665 | -4.3579 | -5.2826 | 0.19684 | -122.1176 | -0.31128 | 0.027465 | 0.032043 | 0.13275 | -0.17395 | -0.29755 | 0.077819 | 0.34332 | 117.4622 | 116.5375 | 121.7651 | 121.9666 | 0.032043 | 122.0169 | 121.8887 | -0.29755 | 121.9666 | 0.032043 | 121.8887 | 121.7651 | 122.0169 | -122.2504 | -122.2366
1099.75 | 121.9711 | -121.8384 | 0.15106 | 0.0016785 | 0.017677 | 0.011399 | 0.0048428 | 0.05868 | -0.0066929 | 0.081833 | -121.7377 | 0.16022 | -122.1451 | -121.6507 | -0.022888 | 0.10071 | -4.6555 | -5.0262 | 0.19684 | -122.1085 | -0.3067 | 0.009155 | 0.10071 | 0.18768 | -0.17395 | -0.27008 | 0.045776 | 0.40741 | 117.1829 | 116.8121 | 121.8155 | 121.9986 | 0.10071 | 122.0352 | 121.9391 | -0.27008 | 121.9986 | 0.10071 | 121.9391 | 121.8155 | 122.0352 | -122.2961 | -122.2595
1101.5 | 121.7239 | -121.5134 | 0.13733 | -0.005951 | 0.094795 | 0.084031 | -0.0019932 | 0.057398 | -0.0047703 | 0.083542 | 0.054932 | 0.16022 | -121.8109 | -121.3898 | 0.027466 | 0.15564 | -4.7699 | -5.191 | 0.15106 | -121.8613 | -0.29755 | 0.022888 | 121.5683 | 0.1236 | -0.10986 | -0.3479 | 0.013733 | 121.8658 | 116.7435 | 116.3223 | 121.5408 | 121.6736 | 121.5683 | 121.6644 | 121.669 | -0.3479 | 121.6736 | 121.5683 | 121.669 | 121.5408 | 121.6644 | -121.9482 | -121.9986
1103.1719 | 121.9208 | -121.5912 | 0.09613 | 0.0016785 | 0.091804 | 0.084031 | -0.00071139 | 0.057612 | -0.0039157 | 0.081833 | 0.013733 | 0.15106 | -121.9528 | -121.5042 | 0.004578 | 0.14648 | -5.1773 | -5.7724 | 0.18768 | -121.9711 | -0.36163 | 0.054932 | 121.6049 | 0.086976 | -0.091552 | -0.37994 | 0.091553 | 121.9666 | 116.4139 | 115.8188 | 121.5958 | 121.7422 | 121.6049 | 121.7789 | 121.7377 | -0.37994 | 121.7422 | 121.6049 | 121.7377 | 121.5958 | 121.7789 | -122.049 | -122.0673
1104.9375 | 121.8842 | -121.6827 | 0.13733 | 0.0016785 | 0.091591 | 0.084031 | 0.0056974 | 0.058466 | -0.0071201 | 0.079696 | -0.027466 | 0.1831 | -122.0123 | -121.5775 | -0.082397 | 0.068665 | -5.4108 | -6.0791 | 0.19684 | -121.9757 | -0.32959 | 0.045776 | 121.6553 | 0.10528 | -0.21973 | -0.29297 | 0.059509 | 121.9849 | 116.272 | 115.6036 | 121.6003 | 121.8658 | 121.6553 | 121.8796 | 121.7514 | -0.29297 | 121.8658 | 121.6553 | 121.7514 | 121.6003 | 121.8796 | -122.1497 | -122.113
1106.6719 | 121.8475 | -121.7102 | 0.13275 | -0.005951 | 0.088386 | 0.081467 | 0.0050564 | 0.059962 | -0.0056247 | 0.083969 | 0.050354 | 0.16479 | -121.9894 | -121.5225 | 0.022888 | 0.16022 | -5.809 | -5.8914 | 0.16479 | -121.9757 | -0.27924 | 0.032044 | 121.7606 | 0.18768 | -0.10986 | -0.2655 | 0.032044 | 122.0398 | 115.9012 | 115.8188 | 121.7331 | 121.875 | 121.7606 | 121.875 | 121.8704 | -0.2655 | 121.875 | 121.7606 | 121.8704 | 121.7331 | 121.875 | -122.1222 | -122.1085
1108.3438 | 121.8704 | -121.6736 | 0.13733 | -0.005951 | 0.092018 | 0.087449 | 0.004202 | 0.060175 | -0.0062655 | 0.083755 | 0.022888 | 0.19226 | -122.0078 | -121.5729 | -0.032043 | 0.11444 | -5.7587 | -5.9372 | 0.16479 | -121.994 | -0.33417 | 0.054932 | 121.6965 | 0.10071 | -0.16937 | -0.32043 | 0.027466 | 122.0306 | 115.9149 | 115.7364 | 121.6415 | 121.8658 | 121.6965 | 121.8384 | 121.788 | -0.32043 | 121.8658 | 121.6965 | 121.788 | 121.6415 | 121.8384 | -122.1451 | -122.1313
1110.0938 | 121.9437 | -121.6736 | 0.13275 | -0.005951 | 0.089668 | 0.085526 | -0.0015658 | 0.058253 | -0.0060519 | 0.081619 | 0.10529 | 0.14191 | -121.9757 | -121.5134 | 0.064087 | 0.21057 | -5.8685 | -6.0013 | 0.16022 | -121.9894 | -0.30212 | 0.009156 | 121.7789 | 0.16022 | -0.068664 | -0.31586 | 0.027466 | 122.081 | 115.8051 | 115.6723 | 121.7377 | 121.8155 | 121.7789 | 121.8338 | 121.8842 | -0.31586 | 121.8155 | 121.7789 | 121.8842 | 121.7377 | 121.8338 | -122.1085 | -122.1222
1111.8281 | 122.0169 | -121.6507 | 0.09613 | -0.005951 | 0.089882 | 0.081467 | 0.0020658 | 0.057826 | -0.0062655 | 0.08226 | -0.027466 | 0.21057 | -122.0581 | -121.6187 | -0.050354 | 0.059509 | -5.6305 | -6.0699 | 0.2243 | -122.0398 | -0.40741 | 0.11444 | 121.6232 | 0.032044 | -0.14648 | -0.3891 | 0.12817 | 122.0306 | 116.0202 | 115.5807 | 121.6003 | 121.8613 | 121.6232 | 121.875 | 121.7102 | -0.3891 | 121.8613 | 121.6232 | 121.7102 | 121.6003 | 121.875 | -122.1542 | -122.1359
1113.5156 | 121.875 | -121.7102 | 0.13733 | -0.005951 | 0.087532 | 0.081681 | -0.00028419 | 0.059748 | -0.0043429 | 0.082474 | 0.10529 | 0.15564 | -121.9849 | -121.5179 | 0.068665 | 0.21515 | -5.9326 | -6.0791 | 0.16022 | -122.0078 | -0.27466 | 0.018311 | 121.8155 | 0.19226 | -0.068664 | -0.29755 | 0.022888 | 122.0901 | 115.7776 | 115.6311 | 121.7789 | 121.8658 | 121.8155 | 121.8704 | 121.9254 | -0.29755 | 121.8658 | 121.8155 | 121.9254 | 121.7789 | 121.8704 | -122.1222 | -122.1451
1115.2656 | 122.0261 | -121.6553 | 0.10986 | -0.005951 | 0.088173 | 0.079117 | 0.0016384 | 0.056757 | -0.0051975 | 0.081619 | -0.004578 | 0.1831 | -122.0444 | -121.6049 | -0.036621 | 0.064087 | -5.4291 | -5.5527 | 0.20142 | -122.0215 | -0.3891 | 0.073242 | 121.6507 | 0.050354 | -0.14648 | -0.36621 | 0.091553 | 122.0398 | 116.2262 | 116.1026 | 121.6187 | 121.8384 | 121.6507 | 121.8567 | 121.7194 | -0.36621 | 121.8384 | 121.6507 | 121.7194 | 121.6187 | 121.8567 | -122.1542 | -122.1313
1117 | 121.9482 | -121.6827 | 0.11902 | -0.005951 | 0.087532 | 0.081681 | -0.00049779 | 0.057612 | -0.0034885 | 0.083542 | 0.068665 | 0.14648 | -121.9986 | -121.5637 | 0.018311 | 0.14191 | -5.8182 | -5.2872 | 0.17853 | -122.0169 | -0.31586 | 0.027465 | 121.7514 | 0.11902 | -0.10071 | -0.33417 | 0.059509 | 122.0673 | 115.8646 | 116.3956 | 121.701 | 121.8292 | 121.7514 | 121.8613 | 121.8246 | -0.33417 | 121.8292 | 121.7514 | 121.8246 | 121.701 | 121.8613 | -122.1176 | -122.1359
1118.6875 | 122.0215 | -121.6553 | 0.11444 | 0.0016785 | 0.085396 | 0.078263 | 0.0016384 | 0.057612 | -0.0054111 | 0.082474 | 0.050354 | 0.14648 | -122.0627 | -121.5912 | 0 | 0.09613 | -5.3741 | -5.4886 | 0.16937 | -122.0261 | -0.40741 | 0.032043 | 121.7056 | 0.064086 | -0.11444 | -0.37079 | 0.054932 | 122.113 | 116.2811 | 116.1667 | 121.6553 | 121.8018 | 121.7056 | 121.8246 | 121.7514 | -0.37079 | 121.8018 | 121.7056 | 121.7514 | 121.6553 | 121.8246 | -122.1771 | -122.1405
1120.4531 | 121.9208 | -121.6919 | 0.12817 | -0.013581 | 0.085396 | 0.081467 | 0.0020658 | 0.060175 | -0.0054111 | 0.083969 | 0.086975 | 0.15106 | -121.9986 | -121.5729 | 0.022888 | 0.16022 | -5.7816 | -5.4611 | 0.17395 | -122.0078 | -0.3067 | 0.022888 | 121.7789 | 0.11902 | -0.10529 | -0.31586 | 0.045776 | 122.0856 | 115.9103 | 116.2308 | 121.7148 | 121.843 | 121.7789 | 121.8658 | 121.8521 | -0.31586 | 121.843 | 121.7789 | 121.8521 | 121.7148 | 121.8658 | -122.1268 | -122.1359
1122.125 | 121.9528 | -121.7056 | 0.11902 | -0.005951 | 0.087959 | 0.079117 | 0.0063382 | 0.058253 | -0.0051975 | 0.083755 | 0 | 0.18768 | -122.0444 | -121.6415 | -0.068665 | 0.050354 | -5.5847 | -6.0562 | 0.21057 | -122.0535 | -0.33875 | 0.068664 | 121.7056 | 0.064086 | -0.18768 | -0.3479 | 0.091552 | 122.0444 | 116.1209 | 115.6494 | 121.637 | 121.8933 | 121.7056 | 121.9162 | 121.756 | -0.3479 | 121.8933 | 121.7056 | 121.756 | 121.637 | 121.9162 | -122.1634 | -122.1725
1123.875 | 121.9757 | -121.7056 | 0.10986 | 0.0016785 | 0.08326 | 0.074845 | 0.00035681 | 0.059107 | -0.0066929 | 0.08226 | 0.082397 | 0.15106 | -122.0215 | -121.5088 | 0.07782 | 0.20599 | -5.3696 | -5.4428 | 0.14648 | -122.0535 | -0.31586 | 0.041199 | 121.788 | 0.19684 | -0.032043 | -0.3479 | 0.036621 | 122.1039 | 116.3361 | 116.2628 | 121.7834 | 121.8567 | 121.788 | 121.8521 | 121.9116 | -0.3479 | 121.8567 | 121.788 | 121.9116 | 121.7834 | 121.8521 | -122.1313 | -122.1634
1125.625 | 121.9666 | -121.6965 | 0.11902 | 0.0016785 | 0.084969 | 0.084672 | 0.001852 | 0.059962 | -0.0062655 | 0.083328 | 0.054932 | 0.15564 | -122.0261 | -121.5775 | 0.009155 | 0.15564 | -5.2872 | -5.3238 | 0.16479 | -122.0261 | -0.32959 | 0.036621 | 121.7514 | 0.11902 | -0.10986 | -0.32959 | 0.045776 | 122.081 | 116.4093 | 116.3727 | 121.7056 | 121.8521 | 121.7514 | 121.8613 | 121.8521 | -0.32959 | 121.8521 | 121.7514 | 121.8521 | 121.7056 | 121.8613 | -122.1451 | -122.1451
1127.2969 | 121.8933 | -121.7377 | 0.13275 | -0.005951 | 0.086678 | 0.079758 | 0.0020658 | 0.056971 | -0.0054111 | 0.08226 | 0.11902 | 0.15106 | -122.0078 | -121.5363 | 0.045776 | 0.20599 | -5.3696 | -5.2689 | 0.16937 | -122.0352 | -0.27008 | 0.018311 | 121.8567 | 0.20142 | -0.086975 | -0.29755 | 0.036622 | 122.1268 | 116.3681 | 116.4688 | 121.7834 | 121.8887 | 121.8567 | 121.907 | 121.9437 | -0.29755 | 121.8887 | 121.8567 | 121.9437 | 121.7834 | 121.907 | -122.1405 | -122.168
1129.0469 | 121.9162 | -121.7331 | 0.14191 | 0.0016785 | 0.086678 | 0.079331 | 0.0044156 | 0.060816 | -0.0056247 | 0.08461 | 0.018311 | 0.19226 | -122.0627 | -121.5775 | -0.041199 | 0.10529 | -5.3329 | -5.4794 | 0.20142 | -122.0673 | -0.32959 | 0.050354 | 121.7514 | 0.15564 | -0.18311 | -0.33417 | 0.059509 | 122.081 | 116.4001 | 116.2537 | 121.6919 | 121.9254 | 121.7514 | 121.9345 | 121.8384 | -0.33417 | 121.9254 | 121.7514 | 121.8384 | 121.6919 | 121.9345 | -122.2046 | -122.2092
1130.7969 | 122.0169 | -121.6919 | 0.11902 | 0.0016785 | 0.084328 | 0.075059 | 0.003561 | 0.059321 | -0.0051975 | 0.080124 | -0.004578 | 0.18768 | -122.1039 | -121.6232 | -0.050354 | 0.073242 | -5.0034 | -5.5344 | 0.21515 | -122.0581 | -0.41199 | 0.068664 | 121.6873 | 0.068665 | -0.16937 | -0.36621 | 0.09613 | 122.0993 | 116.6885 | 116.1575 | 121.6415 | 121.8796 | 121.6873 | 121.907 | 121.7651 | -0.36621 | 121.8796 | 121.6873 | 121.7651 | 121.6415 | 121.907 | -122.2229 | -122.1771
1132.5312 | 121.9574 | -121.7239 | 0.1236 | -0.02121 | 0.085396 | 0.082108 | 0.0061246 | 0.062739 | -0.0069065 | 0.08461 | -0.027466 | 0.18768 | -122.081 | -121.6553 | -0.091553 | 0.059509 | -4.9301 | -5.5618 | 0.21515 | -122.0444 | -0.35706 | 0.064087 | 121.6965 | 0.068665 | -0.21515 | -0.32043 | 0.091553 | 122.0535 | 116.7938 | 116.1621 | 121.6324 | 121.9116 | 121.6965 | 121.9391 | 121.7834 | -0.32043 | 121.9116 | 121.6965 | 121.7834 | 121.6324 | 121.9391 | -122.2046 | -122.168
1134.2031 | 122.0352 | -121.6919 | 0.10529 | -0.013581 | 0.081978 | 0.073777 | -0.002634 | 0.057612 | -0.0041293 | 0.081405 | 0.022888 | 0.16022 | -122.0078 | -121.6095 | 0 | 0.15106 | -5.0217 | -5.5481 | 0.17853 | -122.0444 | -0.31586 | 0.054931 | 121.7148 | 0.082398 | -0.10529 | -0.35248 | 0.073242 | 122.0306 | 116.6702 | 116.1438 | 121.6919 | 121.8521 | 121.7148 | 121.8704 | 121.843 | -0.35248 | 121.8521 | 121.7148 | 121.843 | 121.6919 | 121.8704 | -122.113 | -122.1497
1135.9531 | 121.9116 | -121.7377 | 0.14191 | 0.0016785 | 0.086037 | 0.078263 | 0.0065518 | 0.060816 | -0.0081881 | 0.083969 | 0.050354 | 0.1831 | -122.0947 | -121.5637 | -0.004578 | 0.1236 | -4.921 | -5.69 | 0.20599 | -122.0398 | -0.35706 | 0.041198 | 121.788 | 0.17395 | -0.14649 | -0.30212 | 0.064087 | 122.1451 | 116.8167 | 116.0477 | 121.7331 | 121.9208 | 121.788 | 121.9437 | 121.8613 | -0.30212 | 121.9208 | 121.788 | 121.8613 | 121.7331 | 121.9437 | -122.2366 | -122.1817
1137.7031 | 122.0123 | -121.7194 | 0.11902 | -0.013581 | 0.083046 | 0.07634 | -0.0019932 | 0.061457 | -0.0064791 | 0.083114 | 0.07782 | 0.1831 | -121.9986 | -121.5546 | 0.036621 | 0.1831 | -4.8981 | -5.5756 | 0.16937 | -122.0535 | -0.27924 | 0.064086 | 121.7972 | 0.16479 | -0.082398 | -0.33417 | 0.050354 | 122.0764 | 116.8213 | 116.1438 | 121.756 | 121.9025 | 121.7972 | 121.8887 | 121.9025 | -0.33417 | 121.9025 | 121.7972 | 121.9025 | 121.756 | 121.8887 | -122.1176 | -122.1725
1139.3906 | 122.0032 | -121.7056 | 0.1236 | 0.0016785 | 0.080269 | 0.074204 | 0.0056974 | 0.05633 | -0.0079745 | 0.082046 | -0.013733 | 0.18768 | -122.0718 | -121.5958 | -0.059509 | 0.091553 | -5.3696 | -5.7724 | 0.20599 | -122.0306 | -0.36621 | 0.064087 | 121.6919 | 0.10986 | -0.1831 | -0.32501 | 0.082398 | 122.0581 | 116.3361 | 115.9332 | 121.6461 | 121.8933 | 121.6919 | 121.9116 | 121.7972 | -0.32501 | 121.8933 | 121.6919 | 121.7972 | 121.6461 | 121.9116 | -122.1954 | -122.1542
1141.0625 | 121.9437 | -121.7285 | 0.13275 | -0.005951 | 0.080055 | 0.077408 | 0.0061246 | 0.061671 | -0.0071201 | 0.083542 | 0.013733 | 0.17853 | -122.081 | -121.6415 | -0.068665 | 0.054932 | -5.1086 | -5.7587 | 0.21515 | -122.0444 | -0.35248 | 0.045777 | 121.7422 | 0.086975 | -0.20142 | -0.31586 | 0.082398 | 122.0947 | 116.6199 | 115.9698 | 121.6599 | 121.907 | 121.7422 | 121.9437 | 121.7834 | -0.31586 | 121.907 | 121.7422 | 121.7834 | 121.6599 | 121.9437 | -122.2137 | -122.1771
1142.8125 | 122.0032 | -121.7285 | 0.1236 | -0.013581 | 0.079628 | 0.076768 | -0.002634 | 0.057398 | -0.0037021 | 0.083542 | 0.054932 | 0.15106 | -122.0032 | -121.6095 | 0.013733 | 0.15564 | -5.0766 | -5.8731 | 0.17853 | -122.0352 | -0.27466 | 0.027466 | 121.7834 | 0.11902 | -0.10986 | -0.3067 | 0.054932 | 122.0581 | 116.6519 | 115.8554 | 121.7422 | 121.8796 | 121.7834 | 121.907 | 121.8842 | -0.3067 | 121.8796 | 121.7834 | 121.8842 | 121.7422 | 121.907 | -122.1268 | -122.1588
1144.5625 | 121.9574 | -121.7514 | 0.1236 | -0.005951 | 0.082405 | 0.077622 | 0.0063382 | 0.059107 | -0.0073337 | 0.07991 | -0.009155 | 0.17853 | -122.1176 | -121.6644 | -0.073242 | 0.045776 | -4.9667 | -6.0379 | 0.21515 | -122.0627 | -0.36621 | 0.054932 | 121.7422 | 0.086975 | -0.19684 | -0.31128 | 0.091553 | 122.1085 | 116.7847 | 115.7135 | 121.6782 | 121.9299 | 121.7422 | 121.9666 | 121.7972 | -0.31128 | 121.9299 | 121.7422 | 121.7972 | 121.6782 | 121.9666 | -122.2412 | -122.1863
1146.25 | 121.9894 | -121.7194 | 0.10529 | 0.009308 | 0.079842 | 0.076768 | -0.0028476 | 0.056757 | -0.0060519 | 0.083755 | 0.09613 | 0.14191 | -122.0169 | -121.5363 | 0.068665 | 0.20599 | -5.1361 | -5.9647 | 0.16937 | -122.0627 | -0.29755 | 0.036621 | 121.8155 | 0.1831 | -0.036621 | -0.34332 | 0.064087 | 122.113 | 116.5833 | 115.7547 | 121.788 | 121.8613 | 121.8155 | 121.8887 | 121.9254 | -0.34332 | 121.8613 | 121.8155 | 121.9254 | 121.788 | 121.8887 | -122.1222 | -122.168
1147.9844 | 121.907 | -121.7514 | 0.15564 | -0.005951 | 0.081123 | 0.07399 | 0.0039884 | 0.060603 | -0.0049839 | 0.084396 | 0.064087 | 0.16022 | -122.0398 | -121.5637 | 0.022888 | 0.17395 | -5.2002 | -5.9647 | 0.16479 | -122.0352 | -0.28839 | 0.004577 | 121.8155 | 0.18768 | -0.13275 | -0.28381 | 0.009155 | 122.1039 | 116.5512 | 115.7867 | 121.7743 | 121.9116 | 121.8155 | 121.9162 | 121.9254 | -0.28381 | 121.9116 | 121.8155 | 121.9254 | 121.7743 | 121.9162 | -122.1954 | -122.1909
1149.7344 | 122.049 | -121.7056 | 0.10986 | -0.005951 | 0.08326 | 0.075699 | 0.00057041 | 0.057398 | -0.0062655 | 0.084182 | -0.022888 | 0.20142 | -122.1222 | -121.637 | -0.064087 | 0.064087 | -5.0766 | -6.1386 | 0.21515 | -122.081 | -0.41656 | 0.091553 | 121.6827 | 0.068664 | -0.17395 | -0.37537 | 0.10529 | 122.0993 | 116.629 | 115.567 | 121.6415 | 121.907 | 121.6827 | 121.9208 | 121.7697 | -0.37537 | 121.907 | 121.6827 | 121.7697 | 121.6415 | 121.9208 | -122.2321 | -122.1909
1151.4219 | 122.0673 | -121.6965 | 0.10529 | -0.005951 | 0.080269 | 0.073563 | 0.003561 | 0.057826 | -0.0028475 | 0.081833 | -0.013733 | 0.19226 | -122.0901 | -121.6507 | -0.064087 | 0.07782 | -5.1315 | -6.4499 | 0.2243 | -122.049 | -0.39368 | 0.086975 | 121.6827 | 0.045776 | -0.16937 | -0.35248 | 0.11902 | 122.0764 | 116.5649 | 115.2466 | 121.6324 | 121.8887 | 121.6827 | 121.9208 | 121.7743 | -0.35248 | 121.8887 | 121.6827 | 121.7743 | 121.6324 | 121.9208 | -122.1954 | -122.1542
1153.0938 | 121.9208 | -121.7651 | 0.15106 | -0.013581 | 0.083046 | 0.074845 | 0.005911 | 0.05868 | -0.0090427 | 0.080337 | 0.054932 | 0.1831 | -122.0901 | -121.5912 | 0 | 0.11444 | -5.0583 | -6.0928 | 0.19226 | -122.049 | -0.32501 | 0.032043 | 121.8201 | 0.17395 | -0.15106 | -0.28381 | 0.041199 | 122.1451 | 116.7068 | 115.6723 | 121.7651 | 121.9482 | 121.8201 | 121.9574 | 121.8796 | -0.28381 | 121.9482 | 121.8201 | 121.8796 | 121.7651 | 121.9574 | -122.2412 | -122.2
1154.8438 | 122.0261 | -121.7102 | 0.10986 | -0.013581 | 0.083473 | 0.080399 | 0.002493 | 0.059962 | -0.0098971 | 0.081619 | 0.004578 | 0.19226 | -122.0673 | -121.6187 | -0.032043 | 0.07782 | -4.953 | -6.4224 | 0.21973 | -122.0306 | -0.35706 | 0.082398 | 121.7148 | 0.091553 | -0.14191 | -0.32044 | 0.10986 | 122.0718 | 116.7572 | 115.2878 | 121.6782 | 121.9025 | 121.7148 | 121.9299 | 121.788 | -0.32044 | 121.9025 | 121.7148 | 121.788 | 121.6782 | 121.9299 | -122.1771 | -122.1405
1156.5938 | 121.9025 | -121.7743 | 0.12817 | 0.009308 | 0.081337 | 0.074845 | 0.0029202 | 0.062312 | -0.0090427 | 0.082474 | 0.036621 | 0.16479 | -122.0764 | -121.6095 | -0.018311 | 0.10071 | -5.0674 | -6.6833 | 0.20599 | -122.049 | -0.30212 | 0.036621 | 121.8109 | 0.16479 | -0.14649 | -0.27466 | 0.07782 | 122.113 | 116.7068 | 115.0909 | 121.756 | 121.9391 | 121.8109 | 121.9803 | 121.875 | -0.27466 | 121.9391 | 121.8109 | 121.875 | 121.756 | 121.9803 | -122.2046 | -122.1771
1158.2656 | 121.8887 | -121.7422 | 0.14648 | -0.005951 | 0.082405 | 0.074845 | -0.00049779 | 0.063807 | -0.0066929 | 0.08461 | 0.09613 | 0.13733 | -122.0581 | -121.5683 | 0.032043 | 0.20599 | -5.4153 | -7.1686 | 0.16479 | -122.0444 | -0.31586 | -0.009155 | 121.8384 | 0.17395 | -0.11444 | -0.30212 | 0.018311 | 122.1542 | 116.3269 | 114.5737 | 121.7743 | 121.8796 | 121.8384 | 121.907 | 121.9482 | -0.30212 | 121.8796 | 121.8384 | 121.9482 | 121.7743 | 121.907 | -122.2046 | -122.1909
1159.9375 | 122.0078 | -121.7056 | 0.10529 | -0.005951 | 0.08091 | 0.074204 | -0.0032748 | 0.057612 | -0.0062655 | 0.084182 | 0.10529 | 0.16937 | -122.0032 | -121.5408 | 0.07782 | 0.21515 | -5.5618 | -7.6401 | 0.17395 | -122.0718 | -0.29755 | 0.064087 | 121.8109 | 0.16479 | -0.027466 | -0.36621 | 0.068664 | 122.1085 | 116.1438 | 114.0656 | 121.7834 | 121.875 | 121.8109 | 121.8796 | 121.9208 | -0.36621 | 121.875 | 121.8109 | 121.9208 | 121.7834 | 121.8796 | -122.1085 | -122.1771
1161.625 | 121.9299 | -121.7514 | 0.15106 | -0.005951 | 0.081978 | 0.07335 | 0.0050564 | 0.060389 | -0.0064791 | 0.081619 | 0.036621 | 0.18768 | -122.0993 | -121.6003 | -0.022888 | 0.10986 | -5.7175 | -7.7499 | 0.21057 | -122.049 | -0.3479 | 0.036621 | 121.788 | 0.15106 | -0.17395 | -0.29755 | 0.059509 | 122.1359 | 116.0339 | 114.0015 | 121.7285 | 121.9391 | 121.788 | 121.962 | 121.8613 | -0.29755 | 121.9391 | 121.788 | 121.8613 | 121.7285 | 121.962 | -122.2504 | -122.2
1164.7656 | 121.9894 | -121.7194 | 0.12817 | -0.005951 | 0.080055 | 0.073563 | -0.0032748 | 0.057185 | -0.0039157 | 0.081619 | 0.10986 | 0.14648 | -122.049 | -121.5546 | 0.068665 | 0.21973 | -5.7175 | -7.457 | 0.15564 | -122.0444 | -0.32959 | 0.01831 | 121.8292 | 0.16479 | -0.059509 | -0.32501 | 0.027466 | 122.1588 | 116.0019 | 114.2624 | 121.788 | 121.8658 | 121.8292 | 121.875 | 121.9391 | -0.32501 | 121.8658 | 121.8292 | 121.9391 | 121.788 | 121.875 | -122.1771 | -122.1725
1168.5 | 121.9162 | -121.756 | 0.13275 | 0.0016785 | 0.081551 | 0.078477 | 0.0033474 | 0.058039 | -0.0060519 | 0.080124 | 0.10529 | 0.13733 | -122.0078 | -121.5729 | 0.032043 | 0.19684 | -5.9006 | -7.7362 | 0.16022 | -122.0673 | -0.25177 | 0.004578 | 121.8613 | 0.18311 | -0.10071 | -0.31128 | 0.027466 | 122.113 | 115.8554 | 114.0198 | 121.788 | 121.8933 | 121.8613 | 121.9162 | 121.9528 | -0.31128 | 121.8933 | 121.8613 | 121.9528 | 121.788 | 121.9162 | -122.1405 | -122.2
1173.7812 | 122.0627 | -121.7239 | 0.10986 | -0.013581 | 0.078987 | 0.073563 | 0.0012112 | 0.056971 | -0.0071201 | 0.081833 | -0.11902 | 0.17853 | -122.113 | -121.6599 | -0.068665 | 0.07782 | -16.0629 | -8.5419 | 0.21057 | -122.0718 | -0.3891 | 0.068665 | 121.6049 | 0.064087 | -0.17853 | -0.3479 | 0.10071 | 121.994 | 105.661 | 113.1821 | 121.6553 | 121.9025 | 121.6049 | 121.9345 | 121.8018 | -0.3479 | 121.9025 | 121.6049 | 121.8018 | 121.6553 | 121.9345 | -122.2229 | -122.1817
1176.4062 | 121.962 | -121.7468 | 0.13733 | -0.005951 | 0.023872 | 0.068223 | 0.0039884 | 0.059748 | -0.0066929 | 0.081405 | -7.4753 | 0.21057 | -122.0993 | -121.6553 | -0.07782 | 0.091553 | -15.9439 | -8.6151 | 0.21057 | -122.0718 | -0.35248 | 0.073242 | 114.2715 | 0.091553 | -0.21515 | -0.32501 | 0.073242 | 114.624 | 105.8029 | 113.1317 | 121.669 | 121.9574 | 114.2715 | 121.9574 | 121.8384 | -0.32501 | 121.9574 | 114.2715 | 121.8384 | 121.669 | 121.9574 | -122.2366 | -122.2092
1178.0938 | 121.9391 | -121.7422 | 0.14191 | -0.005951 | 0.019813 | 0.070359 | 0.00099761 | 0.058894 | -0.0045565 | 0.081619 | -6.926 | 0.15564 | -122.0398 | -121.5637 | 0.032043 | 0.19684 | -17.4637 | -8.8165 | 0.16022 | -122.0581 | -0.29755 | 0.013733 | 114.8163 | 0.17853 | -0.10986 | -0.31586 | 0.01831 | 115.1138 | 104.2786 | 112.9257 | 121.7743 | 121.8979 | 114.8163 | 121.9025 | 121.9391 | -0.31586 | 121.8979 | 114.8163 | 121.9391 | 121.7743 | 121.9025 | -122.1817 | -122.2
1179.8438 | 121.9391 | -121.7789 | 0.14648 | -0.005951 | 0.076424 | 0.071213 | 0.0046292 | 0.059107 | -0.0062655 | 0.082046 | 0.045776 | 0.17395 | -122.1085 | -121.6049 | -0.050354 | 0.11444 | -17.3859 | -9.2239 | 0.21057 | -122.0718 | -0.32959 | 0.027466 | 121.8246 | 0.17395 | -0.19684 | -0.29297 | 0.064087 | 122.1542 | 104.393 | 112.5549 | 121.7285 | 121.9528 | 121.8246 | 121.9894 | 121.8933 | -0.29297 | 121.9528 | 121.8246 | 121.8933 | 121.7285 | 121.9894 | -122.2549 | -122.2183
1181.5781 | 121.9345 | -121.7285 | 0.14648 | -0.013581 | 0.075783 | 0.071427 | 0.0029202 | 0.061244 | -0.0096835 | 0.082687 | 0.004578 | 0.18768 | -122.113 | -121.6415 | -0.073242 | 0.11444 | -17.395 | -9.3658 | 0.19226 | -122.0398 | -0.38452 | 0.041199 | 121.7331 | 0.086975 | -0.21973 | -0.31128 | 0.045777 | 122.1176 | 104.3335 | 112.3627 | 121.6553 | 121.9162 | 121.7331 | 121.9208 | 121.843 | -0.31128 | 121.9162 | 121.7331 | 121.843 | 121.6553 | 121.9208 | -122.2595 | -122.1863
1183.2812 | 121.962 | -121.7377 | 0.11902 | -0.005951 | 0.075142 | 0.07335 | 0.002493 | 0.062525 | -0.0069065 | 0.082687 | -0.009155 | 0.19684 | -122.1039 | -121.6827 | -0.10986 | -0.018311 | -7.4341 | -8.4686 | 0.19684 | -122.0718 | -0.36621 | 0.077819 | 121.7285 | 0.054932 | -0.22888 | -0.33417 | 0.077819 | 122.0947 | 114.3036 | 113.269 | 121.6278 | 121.9345 | 121.7285 | 121.9345 | 121.7194 | -0.33417 | 121.9345 | 121.7285 | 121.7194 | 121.6278 | 121.9345 | -122.2229 | -122.1909
1185.0156 | 121.9116 | -121.7834 | 0.14191 | -0.005951 | 0.077919 | 0.072495 | 0.0022794 | 0.060603 | -0.0075473 | 0.081405 | 0.054932 | 0.16937 | -122.081 | -121.6278 | -0.068665 | 0.10986 | -7.5027 | -8.6197 | 0.21973 | -122.0352 | -0.29755 | 0.027466 | 121.8384 | 0.15564 | -0.21057 | -0.25177 | 0.07782 | 122.1359 | 114.2807 | 113.1638 | 121.7148 | 121.9528 | 121.8384 | 122.0032 | 121.8933 | -0.25177 | 121.9528 | 121.8384 | 121.8933 | 121.7148 | 122.0032 | -122.2229 | -122.1771
1186.6875 | 122.0078 | -121.7285 | 0.1236 | -0.005951 | 0.073006 | 0.071427 | -0.0051974 | 0.062525 | -0.0047703 | 0.083114 | 0.09613 | 0.14191 | -121.9894 | -121.5363 | 0.032043 | 0.19226 | -7.5165 | -8.9401 | 0.16022 | -122.0673 | -0.26093 | 0.018311 | 121.8246 | 0.19226 | -0.091553 | -0.33875 | 0.036621 | 122.0856 | 114.212 | 112.7884 | 121.7606 | 121.8704 | 121.8246 | 121.8887 | 121.9208 | -0.33875 | 121.8704 | 121.8246 | 121.9208 | 121.7606 | 121.8887 | -122.113 | -122.1909
1188.4219 | 122.049 | -121.701 | 0.10529 | -0.005951 | 0.018318 | 0.066727 | -0.0015658 | 0.057185 | -0.0049839 | 0.081619 | -6.4133 | 0.17853 | -122.0169 | -121.6095 | 0 | 0.17853 | -7.4387 | -8.876 | 0.1831 | -122.0398 | -0.31586 | 0.073242 | 115.2878 | 0.091553 | -0.10529 | -0.33875 | 0.077819 | 115.6036 | 114.2624 | 112.825 | 121.701 | 121.8796 | 115.2878 | 121.8842 | 121.8796 | -0.33875 | 121.8796 | 115.2878 | 121.8796 | 121.701 | 121.8842 | -122.1222 | -122.1451
1190.0938 | 122.0169 | -121.701 | 0.12817 | -0.013581 | 0.018745 | 0.070359 | -0.0022068 | 0.05633 | -0.0037021 | 0.080337 | -5.9692 | 0.16022 | -122.049 | -121.5729 | 0.013733 | -15.3625 | -8.194 | -10.1028 | 0.1831 | -122.081 | -0.3479 | 0.032043 | 115.7318 | 0.12817 | -0.11444 | -0.37994 | 0.054931 | 116.0797 | 113.5071 | 111.5982 | 121.7148 | 121.8613 | 115.7318 | 121.8842 | 106.3385 | -0.37994 | 121.8613 | 115.7318 | 106.3385 | 121.7148 | 121.8842 | -122.1771 | -122.2092
1191.8438 | 121.9666 | -121.7606 | 0.14648 | 0.0016785 | 0.021095 | 0.070359 | 0.0071926 | 0.059535 | -0.0049839 | 0.08226 | -7.2235 | 0.19684 | -122.0947 | -121.6873 | -0.10986 | -10.2997 | -7.6218 | -10.6293 | 0.21973 | -122.049 | -0.33417 | 0.050354 | 114.537 | 0.073242 | -0.25635 | -0.28839 | 0.073243 | 114.8712 | 114.1388 | 111.1313 | 121.6507 | 121.9574 | 114.537 | 121.9803 | 111.4609 | -0.28839 | 121.9574 | 114.537 | 111.4609 | 121.6507 | 121.9803 | -122.2412 | -122.1954
1193.5781 | 121.9345 | -121.756 | 0.16022 | 0.0016785 | 0.019386 | 0.0663 | 0.006979 | 0.059321 | -0.0056247 | 0.082901 | -7.0267 | 0.19226 | -122.0764 | -121.5912 | -0.054932 | -16.0904 | -8.4183 | -11.3983 | 0.20142 | -122.0718 | -0.32043 | 0.032044 | 114.7293 | 0.16479 | -0.21515 | -0.31586 | 0.041199 | 115.0497 | 113.3377 | 110.3577 | 121.701 | 121.9482 | 114.7293 | 121.9574 | 105.6656 | -0.31586 | 121.9482 | 114.7293 | 105.6656 | 121.701 | 121.9574 | -122.2366 | -122.2321
1195.25 | 121.9391 | -121.7743 | 0.15564 | -0.005951 | 0.022591 | 0.067795 | 0.0061246 | 0.060175 | -0.0060519 | 0.082474 | -6.7291 | 0.1831 | -122.081 | -121.6049 | -0.054932 | 0.10529 | -8.4732 | -11.5631 | 0.19684 | -122.049 | -0.3067 | 0.027465 | 115.0452 | 0.16937 | -0.21057 | -0.27466 | 0.041198 | 115.3519 | 113.3011 | 110.2112 | 121.7194 | 121.9574 | 115.0452 | 121.9711 | 121.8796 | -0.27466 | 121.9574 | 115.0452 | 121.8796 | 121.7194 | 121.9711 | -122.2366 | -122.2046
1197 | 121.9803 | -121.7285 | 0.13275 | -0.013581 | 0.020454 | 0.06865 | 0.0014248 | 0.061671 | -0.0079745 | 0.082046 | -7.1228 | 0.1831 | -122.0993 | -121.6965 | -0.10529 | -0.036621 | -8.8898 | -11.4716 | 0.20142 | -122.0535 | -0.37079 | 0.050354 | 114.6057 | 0.032044 | -0.23804 | -0.32501 | 0.068665 | 114.9765 | 112.8387 | 110.257 | 121.6232 | 121.9116 | 114.6057 | 121.9299 | 121.6919 | -0.32501 | 121.9116 | 114.6057 | 121.6919 | 121.6232 | 121.9299 | -122.2321 | -122.1863
1198.7344 | 121.9666 | -121.7651 | 0.12817 | -0.005951 | 0.074501 | 0.071854 | 0.002493 | 0.06103 | -0.0041293 | 0.079696 | 0.027466 | 0.18768 | -122.0718 | -121.6187 | -0.050354 | 0.10529 | -8.9813 | -11.3525 | 0.20142 | -122.0581 | -0.3067 | 0.059509 | 121.7926 | 0.14648 | -0.17853 | -0.29297 | 0.073242 | 122.0993 | 112.7838 | 110.4126 | 121.7148 | 121.9528 | 121.7926 | 121.9666 | 121.8704 | -0.29297 | 121.9528 | 121.7926 | 121.8704 | 121.7148 | 121.9666 | -122.2 | -122.1863
1200.4844 | 121.9162 | -121.7789 | 0.1236 | -0.013581 | 0.07386 | 0.070359 | -0.0017794 | 0.061671 | -0.0069065 | 0.082474 | 0.09613 | 0.16022 | -122.0306 | -121.5866 | -0.018311 | -16.214 | -10.1212 | -13.4262 | 0.15564 | -122.0261 | -0.25177 | 0.036621 | 121.875 | 0.19226 | -0.14191 | -0.24719 | 0.032044 | 122.1268 | 111.6577 | 108.3527 | 121.7606 | 121.9391 | 121.875 | 121.9345 | 105.5649 | -0.24719 | 121.9391 | 121.875 | 105.5649 | 121.7606 | 121.9345 | -122.1542 | -122.1497
1202.1562 | 122.0078 | -121.7102 | 0.13275 | -0.005951 | 0.073006 | 0.065873 | -0.0022068 | 0.058466 | -0.0047703 | 0.081619 | 0.09613 | 0.15564 | -122.0169 | -121.582 | -0.027466 | -16.7175 | -10.2402 | -13.9206 | 0.16022 | -122.0718 | -0.3067 | 0.022889 | 121.8063 | 0.12817 | -0.16022 | -0.36163 | 0.027466 | 122.113 | 111.47 | 107.7896 | 121.6827 | 121.8658 | 121.8063 | 121.8704 | 104.9927 | -0.36163 | 121.8658 | 121.8063 | 104.9927 | 121.6827 | 121.8704 | -122.1497 | -122.2046
1203.8906 | 121.9574 | -121.7377 | 0.13275 | -0.005951 | 0.075996 | 0.067368 | 0.0037748 | 0.060175 | -0.0049839 | 0.084182 | 0 | 0.19226 | -122.1085 | -121.6782 | -0.16022 | -17.07 | -10.9085 | -15.2985 | 0.21057 | -122.113 | -0.37079 | 0.05951 | 121.7377 | 0.059509 | -0.29297 | -0.37537 | 0.07782 | 122.1085 | 110.8292 | 106.4392 | 121.5775 | 121.9299 | 121.7377 | 121.9482 | 104.6677 | -0.37537 | 121.9299 | 121.7377 | 104.6677 | 121.5775 | 121.9482 | -122.2412 | -122.2458
1205.625 | 122.0535 | -121.7331 | 0.11444 | -0.005951 | 0.073647 | 0.067795 | 0.00057041 | 0.057826 | -0.0079745 | 0.080765 | -0.027466 | 0.18768 | -122.0947 | -121.6827 | -0.14648 | -17.1204 | -10.9039 | -15.0879 | 0.19684 | -122.0947 | -0.36163 | 0.073242 | 121.7056 | 0.050354 | -0.26093 | -0.36163 | 0.082397 | 122.0673 | 110.8292 | 106.6452 | 121.5866 | 121.9208 | 121.7056 | 121.9299 | 104.6127 | -0.36163 | 121.9208 | 121.7056 | 104.6127 | 121.5866 | 121.9299 | -122.2092 | -122.2092
1207.375 | 122.0032 | -121.7285 | 0.10529 | -0.013581 | 0.075355 | 0.066086 | -0.0028476 | 0.058894 | -0.0060519 | 0.081833 | 0.086975 | 0.15564 | -122.0123 | -121.5591 | -0.032043 | -17.0792 | -11.705 | -15.2893 | 0.15564 | -122.049 | -0.28381 | 0.050354 | 121.8155 | 0.16937 | -0.13733 | -0.32043 | 0.050354 | 122.0993 | 110.0235 | 106.4392 | 121.6965 | 121.8842 | 121.8155 | 121.8842 | 104.6494 | -0.32043 | 121.8842 | 121.8155 | 104.6494 | 121.6965 | 121.8842 | -122.1176 | -122.1542
1209.0625 | 122.0215 | -121.7377 | 0.13275 | -0.028839 | 0.071938 | 0.066727 | 0.0016384 | 0.058894 | -0.0062655 | 0.082901 | 0.10529 | 0.15106 | -122.0627 | -121.5637 | -0.027466 | 0.19684 | -11.3251 | -15.5548 | 0.16022 | -122.0444 | -0.32501 | 0.018311 | 121.843 | 0.17395 | -0.16022 | -0.3067 | 0.027466 | 122.168 | 110.4126 | 106.1829 | 121.7102 | 121.8887 | 121.843 | 121.8979 | 121.9345 | -0.3067 | 121.8887 | 121.843 | 121.9345 | 121.7102 | 121.8979 | -122.1954 | -122.1771
1210.7969 | 122.0078 | -121.7102 | 0.1236 | -0.013581 | 0.074074 | 0.070145 | 0.0014248 | 0.057398 | -0.0049839 | 0.082474 | 0.054932 | 0.16937 | -122.0673 | -121.6324 | -0.09613 | -17.8528 | -12.0071 | -16.6534 | 0.16479 | -122.0856 | -0.35706 | 0.045777 | 121.7651 | 0.07782 | -0.21973 | -0.37537 | 0.041199 | 122.1222 | 109.7031 | 105.0568 | 121.6141 | 121.8796 | 121.7651 | 121.875 | 103.8574 | -0.37537 | 121.8796 | 121.7651 | 103.8574 | 121.6141 | 121.875 | -122.1909 | -122.2092
1212.5469 | 122.0398 | -121.7102 | 0.11902 | -0.005951 | 0.070015 | 0.073777 | 0.00014321 | 0.05633 | -0.0039157 | 0.080765 | 0.054932 | 0.16479 | -122.0398 | -121.6003 | -0.086975 | -17.5873 | -12.1536 | -16.951 | 0.16022 | -122.0718 | -0.32959 | 0.045776 | 121.7651 | 0.10986 | -0.20599 | -0.36163 | 0.041198 | 122.0947 | 109.5566 | 104.7592 | 121.6232 | 121.875 | 121.7651 | 121.8704 | 104.1229 | -0.36163 | 121.875 | 121.7651 | 104.1229 | 121.6232 | 121.8704 | -122.1588 | -122.1909
1214.2188 | 122.049 | -121.6919 | 0.082397 | -0.013581 | 0.072578 | 0.067154 | -7.059e-05 | 0.055903 | -0.0045565 | 0.082901 | 0.036621 | 0.15564 | -122.0352 | -121.6278 | -0.082397 | 0.15564 | -11.7554 | -17.4362 | 0.17395 | -122.0856 | -0.34332 | 0.073243 | 121.7285 | 0.064087 | -0.16479 | -0.39368 | 0.091553 | 122.0718 | 109.9365 | 104.2557 | 121.6095 | 121.8475 | 121.7285 | 121.8658 | 121.8475 | -0.39368 | 121.8475 | 121.7285 | 121.8475 | 121.6095 | 121.8658 | -122.1176 | -122.168
1215.9531 | 121.9208 | -121.8018 | 0.15564 | -0.005951 | 0.075569 | 0.071 | 0.0067654 | 0.058894 | -0.0079745 | 0.081619 | 0.054932 | 0.17395 | -122.1039 | -121.6095 | -0.10986 | 0.1236 | -12.1582 | -18.045 | 0.18768 | -122.0718 | -0.30212 | 0.01831 | 121.8567 | 0.19226 | -0.2655 | -0.27008 | 0.032043 | 122.1588 | 109.6436 | 103.7567 | 121.6919 | 121.9757 | 121.8567 | 121.9894 | 121.9254 | -0.27008 | 121.9757 | 121.8567 | 121.9254 | 121.6919 | 121.9894 | -122.2595 | -122.2275
1217.6406 | 122.0581 | -121.7651 | 0.10986 | -0.005951 | 0.072365 | 0.071854 | 0.0022794 | 0.057398 | -0.0066929 | 0.08226 | 0.013733 | 0.19684 | -122.0993 | -121.6507 | -0.13733 | 0.082397 | -12.8357 | -19.7662 | 0.19226 | -122.1176 | -0.33417 | 0.086975 | 121.7789 | 0.11444 | -0.24719 | -0.35248 | 0.082398 | 122.113 | 108.9294 | 101.9989 | 121.6278 | 121.962 | 121.7789 | 121.9574 | 121.8475 | -0.35248 | 121.962 | 121.7789 | 121.8475 | 121.6278 | 121.9574 | -122.2092 | -122.2275
1219.375 | 122.0581 | -121.6919 | 0.11902 | -0.005951 | 0.073647 | 0.069504 | -0.0019932 | 0.057612 | -0.0028475 | 0.083328 | 0.050354 | 0.15564 | -122.0581 | -121.6232 | -0.091553 | 0.15564 | -13.5498 | -19.6564 | 0.17395 | -122.0856 | -0.36621 | 0.036621 | 121.7422 | 0.068665 | -0.21057 | -0.39368 | 0.054931 | 122.1085 | 108.1421 | 102.0355 | 121.6003 | 121.8475 | 121.7422 | 121.8658 | 121.8475 | -0.39368 | 121.8475 | 121.7422 | 121.8475 | 121.6003 | 121.8658 | -122.1771 | -122.2046
1221.125 | 122.0673 | -121.7285 | 0.09613 | -0.005951 | 0.070869 | 0.068436 | -7.059e-05 | 0.058253 | -0.0019931 | 0.081619 | 0.050354 | 0.14648 | -122.0352 | -121.5866 | -0.054932 | 0.1831 | -14.2593 | -20.7138 | 0.16937 | -122.0993 | -0.3067 | 0.050354 | 121.7789 | 0.14191 | -0.15106 | -0.37079 | 0.073243 | 122.0856 | 107.4692 | 101.0147 | 121.6736 | 121.875 | 121.7789 | 121.8979 | 121.9116 | -0.37079 | 121.875 | 121.7789 | 121.9116 | 121.6736 | 121.8979 | -122.1313 | -122.1954
1222.8906 | 121.9254 | -121.7789 | 0.14191 | -0.005951 | 0.074287 | 0.069077 | 0.0050564 | 0.05868 | -0.0056247 | 0.081833 | 0.09613 | 0.15106 | -122.0398 | -121.5683 | -0.064087 | 0.19226 | -14.4379 | -22.1329 | 0.16937 | -122.0123 | -0.26093 | 0.009155 | 121.875 | 0.21057 | -0.20599 | -0.23346 | 0.027466 | 122.1359 | 107.341 | 99.646 | 121.7148 | 121.9299 | 121.875 | 121.9482 | 121.9711 | -0.23346 | 121.9299 | 121.875 | 121.9711 | 121.7148 | 121.9482 | -122.1817 | -122.1542
1224.5625 | 121.9025 | -121.7697 | 0.14648 | -0.005951 | 0.073433 | 0.069077 | 0.0044156 | 0.059321 | -0.0056247 | 0.080978 | 0.11444 | 0.14648 | -122.0444 | -121.5591 | -0.027466 | 0.19684 | -14.859 | -22.7692 | 0.16479 | -122.0215 | -0.27466 | 0 | 121.8842 | 0.21057 | -0.17395 | -0.25177 | 0.018311 | 122.1588 | 106.9107 | 99.0005 | 121.7422 | 121.9162 | 121.8842 | 121.9345 | 121.9666 | -0.25177 | 121.9162 | 121.8842 | 121.9666 | 121.7422 | 121.9345 | -122.1909 | -122.168
1226.2969 | 121.9894 | -121.7285 | 0.11444 | 0.0016785 | 0.073006 | 0.070359 | -0.0017794 | 0.057612 | -0.0037021 | 0.081405 | 0.10529 | 0.14648 | -122.0535 | -121.5454 | -0.032043 | 0.20142 | -15.1245 | -23.6664 | 0.15106 | -122.0764 | -0.32501 | 0.032043 | 121.8338 | 0.18311 | -0.14648 | -0.3479 | 0.036621 | 122.1588 | 106.604 | 98.0621 | 121.6965 | 121.875 | 121.8338 | 121.8796 | 121.9299 | -0.3479 | 121.875 | 121.8338 | 121.9299 | 121.6965 | 121.8796 | -122.168 | -122.1909
1228.0312 | 121.994 | -121.7468 | 0.1236 | 0.0016785 | 0.073006 | 0.063523 | -0.0011386 | 0.05868 | -0.0069065 | 0.082046 | 0.11444 | 0.16022 | -122.0581 | -121.5454 | -0.059509 | 0.20599 | -16.1728 | -24.3805 | 0.14648 | -122.0673 | -0.31128 | 0.036621 | 121.8613 | 0.20142 | -0.1831 | -0.32044 | 0.022888 | 122.1725 | 105.574 | 97.3663 | 121.6873 | 121.907 | 121.8613 | 121.8933 | 121.9528 | -0.32044 | 121.907 | 121.8613 | 121.9528 | 121.6873 | 121.8933 | -122.1817 | -122.1909
1229.7031 | 122.0398 | -121.7422 | 0.10529 | 0.009308 | 0.075142 | 0.067582 | 0.004202 | 0.059535 | -0.0041293 | 0.080124 | 0.009155 | 0.19684 | -122.0993 | -121.6324 | -0.12817 | 0.073242 | -16.3376 | -24.3301 | 0.19684 | -122.0764 | -0.35706 | 0.091552 | 121.7514 | 0.10986 | -0.23346 | -0.33417 | 0.091552 | 122.1085 | 105.4047 | 97.4121 | 121.6141 | 121.9391 | 121.7514 | 121.9391 | 121.8155 | -0.33417 | 121.9391 | 121.7514 | 121.8155 | 121.6141 | 121.9391 | -122.2046 | -122.1817
1231.4531 | 121.9711 | -121.7514 | 0.1236 | 0.0016785 | 0.075142 | 0.075059 | 0.0050564 | 0.060816 | -0.0064791 | 0.083755 | 0.009155 | 0.19226 | -122.1268 | -121.6782 | -0.17853 | 0.073242 | -17.1295 | -25.6393 | 0.21057 | -122.0627 | -0.37537 | 0.068665 | 121.7606 | 0.073242 | -0.30212 | -0.31128 | 0.086975 | 122.1359 | 104.6219 | 96.1121 | 121.5729 | 121.9437 | 121.7606 | 121.962 | 121.8246 | -0.31128 | 121.9437 | 121.7606 | 121.8246 | 121.5729 | 121.962 | -122.2504 | -122.1863
1233.1406 | 122.0123 | -121.7606 | 0.1236 | -0.013581 | 0.074074 | 0.068223 | 0.0056974 | 0.060816 | -0.0073337 | 0.084396 | 0.022888 | 0.20142 | -122.1039 | -121.6141 | -0.1236 | 0.10986 | -17.0425 | -25.6439 | 0.21057 | -122.0901 | -0.34332 | 0.07782 | 121.7834 | 0.14648 | -0.24719 | -0.32959 | 0.086975 | 122.1268 | 104.718 | 96.1166 | 121.637 | 121.962 | 121.7834 | 121.9711 | 121.8704 | -0.32959 | 121.962 | 121.7834 | 121.8704 | 121.637 | 121.9711 | -122.2275 | -122.2137
1234.875 | 121.9803 | -121.7468 | 0.15106 | 0.0016785 | 0.073433 | 0.068223 | 0.0022794 | 0.060816 | -0.0060519 | 0.082687 | -0.022888 | 0.18768 | -122.113 | -121.6919 | -0.16937 | 0.073242 | -17.8894 | -26.3947 | 0.21515 | -122.0764 | -0.36621 | 0.036621 | 121.7239 | 0.054931 | -0.32044 | -0.32959 | 0.064087 | 122.0901 | 103.8574 | 95.3522 | 121.5775 | 121.9345 | 121.7239 | 121.962 | 121.8201 | -0.32959 | 121.9345 | 121.7239 | 121.8201 | 121.5775 | 121.962 | -122.2641 | -122.2275
1236.5469 | 121.962 | -121.7331 | 0.13275 | -0.005951 | 0.075142 | 0.070786 | 0.0033474 | 0.05868 | -0.0064791 | 0.08226 | -0.013733 | 0.19684 | -122.0947 | -121.7056 | -0.20599 | 0.064087 | -18.6859 | -27.7771 | 0.21057 | -122.081 | -0.36163 | 0.064087 | 121.7194 | 0.027466 | -0.33875 | -0.3479 | 0.07782 | 122.081 | 103.0472 | 93.956 | 121.5271 | 121.9299 | 121.7194 | 121.9437 | 121.7972 | -0.3479 | 121.9299 | 121.7194 | 121.7972 | 121.5271 | 121.9437 | -122.2275 | -122.2137
1238.2969 | 121.9711 | -121.7377 | 0.12817 | -0.02121 | 0.070869 | 0.069504 | -0.0034884 | 0.059535 | -0.0060519 | 0.084182 | 0.07782 | 0.14648 | -122.0673 | -121.6232 | -0.10071 | 0.16937 | -18.9423 | -27.7313 | 0.15564 | -122.0673 | -0.32959 | 0.01831 | 121.8155 | 0.11444 | -0.22888 | -0.32959 | 0.027466 | 122.1451 | 102.7954 | 94.0063 | 121.637 | 121.8842 | 121.8155 | 121.8933 | 121.907 | -0.32959 | 121.8842 | 121.8155 | 121.907 | 121.637 | 121.8933 | -122.1954 | -122.1954
1239.9688 | 122.0123 | -121.7056 | 0.10986 | -0.005951 | 0.072151 | 0.066086 | 0.00035681 | 0.058894 | -0.0041293 | 0.083328 | 0.091553 | 0.14191 | -122.0444 | -121.5637 | -0.054932 | 0.2243 | -19.5328 | -27.6031 | 0.16479 | -122.0627 | -0.33875 | 0.032044 | 121.7972 | 0.14191 | -0.16479 | -0.35706 | 0.054932 | 122.1359 | 102.1729 | 94.1025 | 121.6507 | 121.8475 | 121.7972 | 121.8704 | 121.9299 | -0.35706 | 121.8475 | 121.7972 | 121.9299 | 121.6507 | 121.8704 | -122.1542 | -122.1725
1241.7031 | 121.9711 | -121.7651 | 0.13733 | 0.009308 | 0.075142 | 0.065873 | 0.0067654 | 0.060816 | -0.0056247 | 0.084182 | -0.022888 | 0.19684 | -122.1268 | -121.6827 | -0.2243 | 0.054932 | -19.249 | -28.3493 | 0.20599 | -122.0627 | -0.36163 | 0.059509 | 121.7422 | 0.082398 | -0.36163 | -0.29755 | 0.068665 | 122.1039 | 102.5162 | 93.4158 | 121.5408 | 121.962 | 121.7422 | 121.9711 | 121.8201 | -0.29755 | 121.962 | 121.7422 | 121.8201 | 121.5408 | 121.9711 | -122.2641 | -122.2
1243.3906 | 122.0169 | -121.7148 | 0.10071 | -0.013581 | 0.075142 | 0.069718 | -0.002634 | 0.058466 | -0.0054111 | 0.081405 | 0.064087 | 0.15564 | -122.0306 | -121.6415 | -0.14191 | 0.15106 | -19.5374 | -28.7155 | 0.16937 | -122.0764 | -0.31586 | 0.054932 | 121.7789 | 0.073242 | -0.24262 | -0.36163 | 0.068665 | 122.0947 | 102.1774 | 92.9993 | 121.5729 | 121.8704 | 121.7789 | 121.8842 | 121.8658 | -0.36163 | 121.8704 | 121.7789 | 121.8658 | 121.5729 | 121.8842 | -122.1313 | -122.1771
1245.125 | 121.962 | -121.7422 | 0.12817 | -0.005951 | 0.072151 | 0.065018 | -7.059e-05 | 0.058253 | -0.0077609 | 0.083328 | 0.07782 | 0.15106 | -122.0535 | -121.6187 | -0.13275 | 0.16479 | -19.4733 | -28.3859 | 0.15564 | -122.0398 | -0.31128 | 0.022888 | 121.8201 | 0.1236 | -0.26093 | -0.29755 | 0.027466 | 122.1313 | 102.269 | 93.3563 | 121.6095 | 121.8933 | 121.8201 | 121.8979 | 121.907 | -0.29755 | 121.8933 | 121.8201 | 121.907 | 121.6095 | 121.8979 | -122.1817 | -122.168
1246.875 | 122.081 | -121.7148 | 0.10529 | -0.005951 | 0.071724 | 0.063737 | 0.0033474 | 0.057398 | -0.0041293 | 0.081833 | -0.022888 | 0.17395 | -122.1359 | -121.6782 | -0.21057 | 0.064087 | -20.0088 | -28.8757 | 0.21973 | -122.0856 | -0.42114 | 0.068664 | 121.6919 | 0.036621 | -0.31586 | -0.37079 | 0.11444 | 122.113 | 101.7059 | 92.8391 | 121.5042 | 121.8887 | 121.6919 | 121.9345 | 121.7789 | -0.37079 | 121.8887 | 121.6919 | 121.7789 | 121.5042 | 121.9345 | -122.2412 | -122.1909
1248.5625 | 122.0123 | -121.7468 | 0.1236 | 0.009308 | 0.072365 | 0.065659 | 0.005911 | 0.059321 | -0.0084017 | 0.082046 | 0.018311 | 0.1831 | -122.1451 | -121.637 | -0.19684 | 0.09613 | -20.4254 | -28.5828 | 0.18768 | -122.049 | -0.39826 | 0.059509 | 121.7651 | 0.10986 | -0.32043 | -0.30212 | 0.064087 | 122.1634 | 101.3214 | 93.1641 | 121.55 | 121.9299 | 121.7651 | 121.9345 | 121.843 | -0.30212 | 121.9299 | 121.7651 | 121.843 | 121.55 | 121.9345 | -122.2687 | -122.1725
1250.2969 | 122.0398 | -121.7056 | 0.10986 | -0.013581 | 0.070656 | 0.068223 | -0.0032748 | 0.058894 | -0.0054111 | 0.082474 | 0.059509 | 0.15564 | -122.0352 | -121.5775 | -0.10529 | 0.19226 | -21.1395 | -29.0314 | 0.14648 | -122.0764 | -0.32959 | 0.045777 | 121.7651 | 0.12817 | -0.21515 | -0.37079 | 0.036621 | 122.0947 | 100.5661 | 92.6743 | 121.6003 | 121.8613 | 121.7651 | 121.8521 | 121.8979 | -0.37079 | 121.8613 | 121.7651 | 121.8979 | 121.6003 | 121.8521 | -122.1451 | -122.1863
1252.0312 | 122.081 | -121.7331 | 0.11444 | -0.005951 | 0.074501 | 0.068863 | 0.0029202 | 0.057185 | -0.0062655 | 0.082901 | -0.004578 | 0.1831 | -122.1039 | -121.6919 | -0.23346 | 0.073242 | -21.817 | -29.4159 | 0.20599 | -122.1405 | -0.37079 | 0.068664 | 121.7285 | 0.041198 | -0.3479 | -0.40741 | 0.091553 | 122.0993 | 99.9161 | 92.3172 | 121.4996 | 121.9162 | 121.7285 | 121.9391 | 121.8063 | -0.40741 | 121.9162 | 121.7285 | 121.8063 | 121.4996 | 121.9391 | -122.2183 | -122.2549
1253.7656 | 122.0535 | -121.7285 | 0.10071 | -0.005951 | 0.072578 | 0.06395 | 0.0031338 | 0.057398 | -0.0056247 | 0.083114 | 0.004578 | 0.18768 | -122.0901 | -121.6736 | -0.2243 | 0.068665 | -21.8079 | -29.8828 | 0.20142 | -122.0993 | -0.36163 | 0.086975 | 121.7331 | 0.054932 | -0.32501 | -0.37079 | 0.10071 | 122.0947 | 99.9207 | 91.8457 | 121.5042 | 121.9162 | 121.7331 | 121.9299 | 121.7972 | -0.37079 | 121.9162 | 121.7331 | 121.7972 | 121.5042 | 121.9299 | -122.1909 | -122.2
1255.4375 | 121.962 | -121.756 | 0.12817 | 0.0016785 | 0.072365 | 0.063096 | 0.0074062 | 0.061884 | -0.0073337 | 0.085464 | 0 | 0.19226 | -122.0947 | -121.6782 | -0.27924 | 0.059509 | -22.1375 | -29.6539 | 0.20142 | -122.0627 | -0.33875 | 0.064087 | 121.756 | 0.077819 | -0.40741 | -0.3067 | 0.073242 | 122.0947 | 99.6185 | 92.1021 | 121.4767 | 121.9482 | 121.756 | 121.9574 | 121.8155 | -0.3067 | 121.9482 | 121.756 | 121.8155 | 121.4767 | 121.9574 | -122.2229 | -122.1909
1257.1094 | 122.0352 | -121.7285 | 0.10986 | 0.009308 | 0.072151 | 0.061387 | -0.0017794 | 0.061457 | -0.0060519 | 0.081619 | 0.045776 | 0.14191 | -122.0398 | -121.6415 | -0.17853 | 0.16022 | -22.7005 | -29.7226 | 0.17853 | -122.049 | -0.31128 | 0.032044 | 121.7743 | 0.086975 | -0.28839 | -0.32043 | 0.068665 | 122.0856 | 99.028 | 92.0059 | 121.55 | 121.8704 | 121.7743 | 121.907 | 121.8887 | -0.32043 | 121.8704 | 121.7743 | 121.8887 | 121.55 | 121.907 | -122.1497 | -122.1588
1258.8438 | 121.9528 | -121.7514 | 0.13733 | -0.005951 | 0.072365 | 0.069932 | 0.00035681 | 0.058466 | -0.0060519 | 0.083328 | 0.086975 | 0.13733 | -122.081 | -121.6187 | -0.14648 | 0.18768 | -23.1125 | -30.3452 | 0.15106 | -122.0535 | -0.32959 | 0 | 121.8384 | 0.13275 | -0.28381 | -0.30212 | 0.013733 | 122.168 | 98.6389 | 91.4062 | 121.6049 | 121.8887 | 121.8384 | 121.9025 | 121.9391 | -0.30212 | 121.8887 | 121.8384 | 121.9391 | 121.6049 | 121.9025 | -122.2183 | -122.1909
1260.5781 | 121.907 | -121.7514 | 0.13733 | -0.013581 | 0.072578 | 0.0663 | 0.0031338 | 0.060816 | -0.0064791 | 0.082687 | 0.09613 | 0.13275 | -122.0535 | -121.5729 | -0.15564 | 0.19684 | -23.6206 | -29.9515 | 0.15564 | -122.0261 | -0.30212 | -0.004578 | 121.8475 | 0.17853 | -0.29297 | -0.27466 | 0.018311 | 122.1497 | 98.1308 | 91.7999 | 121.5958 | 121.8842 | 121.8475 | 121.907 | 121.9482 | -0.27466 | 121.8842 | 121.8475 | 121.9482 | 121.5958 | 121.907 | -122.1909 | -122.1634
1262.3125 | 122.0169 | -121.7606 | 0.12817 | 0.0016785 | 0.071938 | 0.068863 | 0.0027066 | 0.058039 | -0.0051975 | 0.086532 | 0.064087 | 0.15106 | -122.0581 | -121.6278 | -0.17853 | 0.15564 | -24.2706 | -30.5786 | 0.16937 | -122.0856 | -0.29755 | 0.022888 | 121.8246 | 0.13275 | -0.3067 | -0.32501 | 0.041199 | 122.1222 | 97.4899 | 91.1819 | 121.582 | 121.9116 | 121.8246 | 121.9299 | 121.9162 | -0.32501 | 121.9116 | 121.8246 | 121.9162 | 121.582 | 121.9299 | -122.1863 | -122.2137
1263.9844 | 122.049 | -121.7468 | 0.11902 | -0.005951 | 0.072578 | 0.065445 | 0.0029202 | 0.056757 | -0.0069065 | 0.085037 | 0.091553 | 0.16479 | -122.0444 | -121.5866 | -0.20142 | 0.16022 | -24.7375 | -30.8945 | 0.16937 | -122.0856 | -0.29755 | 0.045776 | 121.8384 | 0.16022 | -0.32044 | -0.33875 | 0.050354 | 122.1359 | 97.0093 | 90.8524 | 121.5454 | 121.9116 | 121.8384 | 121.9162 | 121.907 | -0.33875 | 121.9116 | 121.8384 | 121.907 | 121.5454 | 121.9162 | -122.1634 | -122.2046
1265.7188 | 122.0123 | -121.7422 | 0.10071 | -0.005951 | 0.070869 | 0.066727 | -0.00049779 | 0.056117 | -0.0058383 | 0.084182 | 0.10986 | 0.15564 | -122.0352 | -121.55 | -0.17395 | 0.21057 | -25.2777 | -31.2103 | 0.15106 | -122.081 | -0.29297 | 0.054932 | 121.8521 | 0.19226 | -0.27466 | -0.33875 | 0.050354 | 122.1451 | 96.4645 | 90.5319 | 121.5683 | 121.8979 | 121.8521 | 121.8933 | 121.9528 | -0.33875 | 121.8979 | 121.8521 | 121.9528 | 121.5683 | 121.8933 | -122.1359 | -122.1817
1267.4531 | 122.0535 | -121.7285 | 0.10529 | -0.013581 | 0.070229 | 0.061387 | 0.00527 | 0.05868 | -0.0054111 | 0.085251 | 0.041199 | 0.18768 | -122.081 | -121.6461 | -0.27008 | 0.073242 | -24.559 | -31.2195 | 0.20142 | -122.1085 | -0.35248 | 0.082397 | 121.7697 | 0.082398 | -0.37537 | -0.37994 | 0.09613 | 122.1222 | 97.1695 | 90.509 | 121.4584 | 121.9162 | 121.7697 | 121.9299 | 121.8018 | -0.37994 | 121.9162 | 121.7697 | 121.8018 | 121.4584 | 121.9299 | -122.1863 | -122.2137
1269.1875 | 122.0078 | -121.7331 | 0.12817 | 0.0016785 | 0.073433 | 0.066514 | 0.0063382 | 0.058039 | -0.0086155 | 0.085678 | 0.022888 | 0.20142 | -122.113 | -121.6141 | -0.27008 | 0.091553 | -25.0854 | -31.1783 | 0.19684 | -122.0627 | -0.37994 | 0.073242 | 121.756 | 0.11902 | -0.39826 | -0.32959 | 0.068664 | 122.1359 | 96.6476 | 90.5548 | 121.463 | 121.9345 | 121.756 | 121.9299 | 121.8246 | -0.32959 | 121.9345 | 121.756 | 121.8246 | 121.463 | 121.9299 | -122.2412 | -122.1909
1270.9531 | 121.9666 | -121.7697 | 0.1236 | -0.005951 | 0.072151 | 0.062028 | 0.0065518 | 0.060603 | -0.0090427 | 0.085464 | 0.018311 | 0.17395 | -122.1176 | -121.6599 | -0.31586 | 0.054932 | -25.1404 | -30.6839 | 0.19226 | -122.0673 | -0.3479 | 0.050354 | 121.788 | 0.10986 | -0.43945 | -0.29755 | 0.068665 | 122.1359 | 96.6293 | 91.0858 | 121.4539 | 121.9437 | 121.788 | 121.962 | 121.8246 | -0.29755 | 121.9437 | 121.788 | 121.8246 | 121.4539 | 121.962 | -122.2412 | -122.1909
1272.6406 | 122.0306 | -121.7285 | 0.11902 | -0.005951 | 0.070869 | 0.067582 | -0.0024204 | 0.057612 | 0.060598 | 0.15404 | 0.07782 | 0.16479 | -122.0306 | -121.5591 | -121.4401 | 0.1831 | -32.4738 | -41.1301 | 0.15106 | -122.0444 | -0.30212 | 0.045776 | 121.8063 | 0.16937 | -121.5591 | -0.31586 | 0.032043 | 122.1085 | 89.2548 | 80.5984 | 0.28839 | 121.8933 | 121.8063 | 121.8796 | 121.9116 | -0.31586 | 121.8933 | 121.8063 | 121.9116 | 0.28839 | 121.8796 | -122.1497 | -122.1634
1274.3906 | 122.0627 | -121.7148 | 0.10986 | -0.005951 | 0.073219 | 0.067795 | 0.0037748 | 0.061244 | 0.062735 | 0.15468 | -0.009155 | 0.19226 | -122.0856 | -121.6507 | -121.5591 | 0.064087 | -32.9132 | -41.098 | 0.20599 | -122.0993 | -0.37079 | 0.082398 | 121.7056 | 0.064087 | -121.669 | -0.38452 | 0.096131 | 122.0764 | 88.8016 | 80.6168 | 0.15564 | 121.907 | 121.7056 | 121.9208 | 121.7789 | -0.38452 | 121.907 | 121.7056 | 121.7789 | 0.15564 | 121.9208 | -122.1954 | -122.2092
1276.0625 | 121.9986 | -121.7194 | 0.11902 | 0.0016785 | 0.071083 | 0.068223 | 0.006979 | 0.059107 | 0.060812 | 0.1566 | 0.018311 | 0.17853 | -122.081 | -121.6095 | -121.5317 | 0.086975 | -33.3115 | -39.7064 | 0.20142 | -122.081 | -0.36163 | 0.059509 | 121.7377 | 0.10986 | -121.6507 | -0.36163 | 0.082397 | 122.0993 | 88.4079 | 82.0129 | 0.18768 | 121.8979 | 121.7377 | 121.9208 | 121.8063 | -0.36163 | 121.8979 | 121.7377 | 121.8063 | 0.18768 | 121.9208 | -122.2 | -122.2
1277.8125 | 122.0261 | -121.7194 | 0.11444 | -0.013581 | 0.070015 | 0.068863 | -0.00028419 | 0.059107 | 0.059103 | 0.15489 | 0.041199 | 0.15564 | -122.0444 | -121.6095 | -121.5225 | 0.10071 | -33.1467 | -39.0152 | 0.1831 | -122.0581 | -0.32501 | 0.041199 | 121.7606 | 0.10986 | -121.637 | -0.33875 | 0.068664 | 122.0856 | 88.5727 | 82.7042 | 0.19684 | 121.875 | 121.7606 | 121.9025 | 121.8201 | -0.33875 | 121.875 | 121.7606 | 121.8201 | 0.19684 | 121.9025 | -122.1588 | -122.1725
1279.5625 | 121.994 | -121.7239 | 0.09613 | -0.005951 | 0.073219 | 0.06395 | -0.0017794 | 0.058039 | 0.063803 | 0.15553 | 0.11444 | 0.13275 | -122.0352 | -121.5179 | -121.4218 | 0.21515 | -33.4167 | -38.237 | 0.15106 | -122.0215 | -0.31128 | 0.036621 | 121.8384 | 0.20599 | -121.5179 | -0.29755 | 0.054932 | 122.1497 | 88.3072 | 83.4869 | 0.30212 | 121.8567 | 121.8384 | 121.875 | 121.9391 | -0.29755 | 121.8567 | 121.8384 | 121.9391 | 0.30212 | 121.875 | -122.1313 | -122.1176
1281.2969 | 121.9803 | -121.7285 | 0.1236 | -0.013581 | 0.069588 | 0.067795 | 0.0050564 | 0.059535 | 0.06188 | 0.15468 | -0.018311 | 0.19226 | -122.0901 | -121.6507 | -121.5729 | 0.054932 | -34.1721 | -38.0905 | 0.19226 | -122.0352 | -0.36163 | 0.068665 | 121.7102 | 0.07782 | -121.6965 | -0.3067 | 0.068665 | 122.0718 | 87.5565 | 83.638 | 0.15564 | 121.9208 | 121.7102 | 121.9208 | 121.7834 | -0.3067 | 121.9208 | 121.7102 | 121.7834 | 0.15564 | 121.9208 | -122.2137 | -122.1588
1282.9844 | 121.8933 | -121.7285 | 0.13733 | 0.009308 | 0.073219 | 0.069291 | 0.0050564 | 0.058039 | 0.061239 | 0.16258 | 0.050354 | 0.16937 | -122.0535 | -121.5729 | -121.4905 | 0.17395 | -34.6939 | -38.2828 | 0.16022 | -122.0215 | -0.32501 | 0.032044 | 121.7789 | 0.15564 | -121.6278 | -0.29297 | 0.022888 | 122.1039 | 87.0346 | 83.4457 | 0.23804 | 121.8979 | 121.7789 | 121.8887 | 121.9025 | -0.29297 | 121.8979 | 121.7789 | 121.9025 | 0.23804 | 121.8887 | -122.1909 | -122.1588
1284.7344 | 121.8155 | -120.8679 | 0.79651 | 0.0016785 | 0.071938 | 0.066514 | 0.00527 | 0.056757 | 0.058248 | 5.3793 | 0.50812 | 0.69122 | -121.431 | -119.5724 | -119.5679 | 0.60425 | -33.9661 | -36.6989 | 0.71869 | -120.8038 | -0.56305 | -0.10529 | 121.376 | 1.2955 | -120.3644 | 0.064087 | -0.07782 | 121.9391 | 86.9019 | 84.169 | 1.3 | 121.5591 | 121.376 | 121.5866 | 121.4722 | 0.064087 | 121.5591 | 121.376 | 121.4722 | 1.3 | 121.5866 | -122.2275 | -121.6003
1286.4844 | 121.4813 | -9.1187 | 112.5916 | -0.005951 | 0.01725 | 0.021012 | 0.0044156 | 0.062312 | 0.061453 | 0.1566 | -9.1049 | -8.1573 | -9.3521 | -8.9355 | -9.0546 | 112.381 | 11.4761 | 11.0321 | 112.7426 | -9.3292 | -0.23346 | -120.7489 | 0.013733 | 0.18311 | -121.6461 | -0.21057 | 0.15106 | 0.24719 | 20.5948 | 20.1508 | 0.064087 | 0.9613 | 0.013733 | 121.8613 | 121.4996 | -0.21057 | 0.9613 | 0.013733 | 121.4996 | 0.064087 | 121.8613 | -121.9437 | -121.9208
1288.2344 | 121.6873 | -8.7753 | 112.9669 | 0.0016785 | 0.021309 | 0.020157 | 0.0044156 | 0.058039 | 0.062307 | 0.15404 | -8.8577 | -8.1848 | -9.0683 | -9.2834 | -9.3201 | 112.175 | 11.9522 | 11.0596 | 112.6877 | -9.4894 | -0.29297 | -121.1517 | -0.082397 | -0.50812 | -122.287 | -0.71411 | -0.27924 | 0.21057 | 20.7275 | 19.8349 | -0.54474 | 0.59052 | -0.082397 | 121.463 | 120.9503 | -0.71411 | 0.59052 | -0.082397 | 120.9503 | -0.54474 | 121.463 | -122.0352 | -122.4564
1289.9219 | 121.7194 | -9.2148 | 112.5229 | 0.009308 | 0.01725 | 0.021226 | 0.0074062 | 0.05868 | 0.059744 | 0.15553 | -9.3018 | -8.226 | -9.5215 | -9.0775 | -9.1965 | 112.3352 | 12.0071 | 11.0733 | 112.6602 | -9.4849 | -0.3067 | -120.7489 | -0.086975 | 0.13733 | -121.7194 | -0.27008 | 0.13733 | 0.21973 | 21.2219 | 20.2881 | 0.018311 | 0.98877 | -0.086975 | 121.875 | 121.55 | -0.27008 | 0.98877 | -0.086975 | 121.55 | 0.018311 | 121.875 | -122.0444 | -122.0078
1291.6719 | 121.6919 | -8.8806 | 112.8845 | 0.0016785 | 0.015114 | 0.020585 | 0.0037748 | 0.059962 | 0.060385 | 0.15489 | -8.5281 | -7.901 | -8.7982 | -8.3038 | -8.4229 | 113.1317 | 11.7004 | 11.055 | 113.2462 | -8.7799 | 0.082397 | -120.7855 | 0.35248 | 0.57678 | -121.3074 | 0.10071 | 0.36163 | 0.27008 | 20.5811 | 19.9356 | 0.45776 | 0.97961 | 0.35248 | 122.1268 | 122.0123 | 0.10071 | 0.97961 | 0.35248 | 122.0123 | 0.45776 | 122.1268 | -121.6827 | -121.6644
1293.4219 | 121.8796 | -8.6472 | 113.0859 | -0.013581 | 0.014687 | 0.020371 | 0.001852 | 0.058253 | 0.061666 | 0.15788 | -8.7204 | -7.9422 | -8.9401 | -8.5007 | -8.6243 | 112.9166 | 11.6547 | 10.6064 | 113.2462 | -8.9172 | -0.29297 | -121.0281 | -0.073242 | 0.14649 | -121.7102 | -0.27008 | 0.16022 | 0.21973 | 20.3018 | 19.2535 | 0.022888 | 0.70496 | -0.073242 | 121.8933 | 121.5637 | -0.27008 | 0.70496 | -0.073242 | 121.5637 | 0.022888 | 121.8933 | -122.0261 | -122.0032
1295.1562 | 121.7972 | -9.2514 | 112.4771 | -0.005951 | 0.016823 | 0.020798 | 0.0065518 | 0.058894 | 0.062307 | 0.15617 | -9.3338 | -8.2764 | -9.5398 | -9.1324 | -9.2377 | 112.3398 | 12.2177 | 10.8673 | 112.6694 | -9.4986 | -0.28839 | -120.7535 | -0.082397 | 0.11902 | -121.7148 | -0.24719 | 0.19226 | 0.20599 | 21.4691 | 20.1187 | 0.013733 | 0.97504 | -0.082397 | 121.9208 | 121.5912 | -0.24719 | 0.97504 | -0.082397 | 121.5912 | 0.013733 | 121.9208 | -122.0169 | -121.9757
1296.9062 | 121.8155 | -9.3063 | 112.4634 | -0.005951 | 0.017036 | 0.020798 | 0.0089016 | 0.05868 | 0.06188 | 0.15532 | -9.3979 | -8.2626 | -9.6085 | -9.2011 | -9.3201 | 112.2986 | 12.5931 | 10.3546 | 112.5961 | -9.5581 | -0.30212 | -120.726 | -0.091553 | 0.10529 | -121.7834 | -0.25177 | 0.13275 | 0.21057 | 21.8994 | 19.6609 | -0.013733 | 1.0437 | -0.091553 | 121.9025 | 121.6049 | -0.25177 | 1.0437 | -0.091553 | 121.6049 | -0.013733 | 121.9025 | -122.0718 | -122.0215
1298.5938 | 121.8384 | -8.8486 | 112.9028 | -0.005951 | 0.012337 | 0.021226 | -7.059e-05 | 0.057612 | 0.062735 | 0.15511 | -8.8852 | -8.1024 | -9.1141 | -8.6426 | -8.7387 | 112.8342 | 13.3621 | 11.0733 | 112.9944 | -9.1095 | -0.2655 | -121.0052 | -0.036621 | 0.20599 | -121.6415 | -0.26092 | 0.091553 | 0.22888 | 22.2107 | 19.9219 | 0.10986 | 0.74615 | -0.036621 | 121.843 | 121.6827 | -0.26092 | 0.74615 | -0.036621 | 121.6827 | 0.10986 | 121.843 | -122.0169 | -122.0123
1300.3438 | 121.8246 | -8.3817 | 113.4064 | -0.005951 | 0.014046 | 0.016526 | 0.0082608 | 0.062098 | 0.059957 | 0.15446 | -8.4457 | -7.7591 | -8.67 | -8.2443 | -8.3633 | 113.237 | 14.0945 | 10.8536 | 113.5986 | -8.6014 | -0.28839 | -121.1655 | -0.064087 | 0.13733 | -121.7697 | -0.21973 | 0.19226 | 0.2243 | 22.4762 | 19.2352 | 0.018311 | 0.62256 | -0.064087 | 121.9803 | 121.6187 | -0.21973 | 0.62256 | -0.064087 | 121.6187 | 0.018311 | 121.9803 | -122.0764 | -122.0078
1302.0625 | 121.7743 | -8.8989 | 112.9211 | 0.0016785 | 0.016609 | 0.019944 | 0.0067654 | 0.058253 | 0.061666 | 0.15489 | -8.8531 | -8.0795 | -9.1187 | -8.6288 | -8.7524 | 112.8525 | 13.4033 | 10.7117 | 113.0035 | -9.1049 | -0.21973 | -121.0007 | 0.045777 | 0.27008 | -121.6736 | -0.20599 | 0.082397 | 0.2655 | 22.3022 | 19.6106 | 0.14649 | 0.8194 | 0.045777 | 121.9025 | 121.7514 | -0.20599 | 0.8194 | 0.045777 | 121.7514 | 0.14649 | 121.9025 | -122.0398 | -122.0261
1303.7656 | 121.9162 | -8.1116 | 113.6261 | -0.005951 | 0.015968 | 0.017167 | 0.0037748 | 0.059321 | 0.06423 | 0.15404 | -8.1436 | -7.608 | -8.3679 | -7.9239 | -8.0246 | 113.5529 | 14.4974 | 11.0596 | 113.7909 | -8.345 | -0.25635 | -121.2341 | -0.032044 | 0.18768 | -121.6507 | -0.23346 | 0.16479 | 0.2243 | 22.6089 | 19.1711 | 0.086975 | 0.50354 | -0.032044 | 121.9025 | 121.6644 | -0.23346 | 0.50354 | -0.032044 | 121.6644 | 0.086975 | 121.9025 | -121.994 | -121.9711
1305.4531 | 121.9574 | -8.4457 | 113.2874 | 0.0016785 | 0.015541 | 0.018662 | 0.0067654 | 0.060175 | 0.061453 | 0.15468 | -8.4961 | -7.8232 | -8.7204 | -8.3038 | -8.4091 | 113.1729 | 15.596 | 10.9497 | 113.4796 | -8.7158 | -0.27466 | -121.1105 | -0.050354 | 0.14191 | -121.6965 | -0.27008 | 0.19226 | 0.2243 | 24.0417 | 19.3954 | 0.036621 | 0.62256 | -0.050354 | 121.9254 | 121.6187 | -0.27008 | 0.62256 | -0.050354 | 121.6187 | 0.036621 | 121.9254 | -122.0078 | -122.0032
1307.1562 | 121.907 | -8.8852 | 112.8616 | -0.005951 | 0.015327 | 0.020798 | 0.0054836 | 0.059748 | 0.064016 | 0.15532 | -8.8623 | -8.1024 | -9.137 | -8.638 | -8.7616 | 112.8433 | 15.3259 | 10.8994 | 112.9944 | -9.1095 | -0.25177 | -120.9641 | 0.022888 | 0.24719 | -121.6232 | -0.2243 | 0.13275 | 0.27466 | 24.2111 | 19.7845 | 0.1236 | 0.78278 | 0.022888 | 121.8796 | 121.7285 | -0.2243 | 0.78278 | 0.022888 | 121.7285 | 0.1236 | 121.8796 | -121.9986 | -121.9711
1308.8438 | 121.9345 | -8.2855 | 113.4842 | -0.013581 | 0.014687 | 0.020157 | 0.0048428 | 0.056971 | 0.061666 | 0.15681 | -8.2718 | -7.7179 | -8.5373 | -8.0521 | -8.1665 | 113.3881 | 15.9348 | 10.556 | 113.6627 | -8.5098 | -0.25177 | -121.2021 | 0.013732 | 0.23346 | -121.6507 | -0.2243 | 0.17853 | 0.2655 | 24.2203 | 18.8416 | 0.11902 | 0.56763 | 0.013732 | 121.9482 | 121.6736 | -0.2243 | 0.56763 | 0.013732 | 121.6736 | 0.11902 | 121.9482 | -122.0215 | -121.994
1310.5469 | 121.9666 | -8.931 | 112.8204 | 0.0016785 | 0.01725 | 0.019089 | 0.0039884 | 0.05633 | 0.06423 | 0.15788 | -8.9951 | -8.1345 | -9.1965 | -8.7753 | -8.8806 | 112.7289 | 15.5594 | 9.9884 | 112.944 | -9.2148 | -0.2655 | -120.9549 | -0.064087 | 0.15564 | -121.7011 | -0.28381 | 0.1236 | 0.20142 | 24.4904 | 18.9194 | 0.050354 | 0.79651 | -0.064087 | 121.875 | 121.6599 | -0.28381 | 0.79651 | -0.064087 | 121.6599 | 0.050354 | 121.875 | -122.0169 | -122.0352
1312.2344 | 121.8658 | -8.6197 | 113.1821 | 0.0016785 | 0.017464 | 0.020585 | 0.0093288 | 0.059535 | 0.062948 | 0.15895 | -8.6746 | -7.9147 | -8.8989 | -8.4686 | -8.6105 | 112.999 | 16.571 | 10.0479 | 113.3652 | -8.8669 | -0.27924 | -121.0968 | -0.054932 | 0.15106 | -121.7926 | -0.24719 | 0.1831 | 0.2243 | 25.1907 | 18.6676 | 0.009155 | 0.70496 | -0.054932 | 121.9849 | 121.6187 | -0.24719 | 0.70496 | -0.054932 | 121.6187 | 0.009155 | 121.9849 | -122.081 | -122.049
1313.9375 | 121.8704 | -8.9539 | 112.8708 | -0.013581 | 0.017036 | 0.021012 | 0.0097562 | 0.059321 | 0.060385 | 0.15532 | -9.0408 | -8.0795 | -9.2514 | -8.8348 | -8.9767 | 112.6282 | 15.6464 | 9.7092 | 113.0173 | -9.2102 | -0.29755 | -120.9503 | -0.086976 | 0.11902 | -121.8475 | -0.25635 | 0.14648 | 0.21057 | 24.6002 | 18.663 | -0.022889 | 0.87433 | -0.086976 | 121.9711 | 121.582 | -0.25635 | 0.87433 | -0.086976 | 121.582 | -0.022889 | 121.9711 | -122.1222 | -122.081
1315.6094 | 121.8658 | -8.9722 | 112.8662 | 0.0016785 | 0.015327 | 0.023148 | 0.0080472 | 0.061244 | 0.061239 | 0.15575 | -9.05 | -8.107 | -9.2194 | -8.8394 | -8.9493 | 112.6648 | 16.5573 | 10.2905 | 113.031 | -9.1965 | -0.24719 | -120.9732 | -0.07782 | 0.13275 | -121.8155 | -0.2243 | 0.16479 | 0.16937 | 25.5295 | 19.2627 | 0.022888 | 0.86517 | -0.07782 | 122.0032 | 121.637 | -0.2243 | 0.86517 | -0.07782 | 121.637 | 0.022888 | 122.0032 | -122.0856 | -122.0627
1317.2812 | 121.907 | -8.5281 | 113.2507 | -0.005951 | 0.014687 | 0.018876 | 0.0027066 | 0.058466 | 0.063589 | 0.15767 | -8.5739 | -7.9102 | -8.7845 | -8.3405 | -8.4595 | 113.1729 | 16.507 | 10.0845 | 113.356 | -8.7799 | -0.25635 | -121.1609 | -0.045777 | 0.18768 | -121.7102 | -0.25177 | 0.10529 | 0.21057 | 25.0351 | 18.6127 | 0.068664 | 0.61798 | -0.045777 | 121.8842 | 121.701 | -0.25177 | 0.61798 | -0.045777 | 121.701 | 0.068664 | 121.8842 | -122.0352 | -122.0306
1318.9688 | 121.9711 | -8.725 | 113.0493 | -0.005951 | 0.015541 | 0.013108 | 0.0061246 | 0.056971 | 0.064016 | 0.15788 | -8.8028 | -8.0521 | -9.0271 | -8.5648 | -8.7021 | 112.9028 | 17.157 | 9.9289 | 113.1729 | -9.0271 | -0.30212 | -121.1014 | -0.077819 | 0.16022 | -121.7514 | -0.30212 | 0.1236 | 0.22431 | 25.882 | 18.6539 | 0.022889 | 0.67291 | -0.077819 | 121.8979 | 121.6278 | -0.30212 | 0.67291 | -0.077819 | 121.6278 | 0.022889 | 121.8979 | -122.0764 | -122.0764
1320.6406 | 121.9666 | -9.05 | 112.7563 | -0.005951 | 0.017464 | 0.019944 | 0.008688 | 0.057826 | 0.062307 | 0.15767 | -9.0454 | -8.1665 | -9.2789 | -8.9035 | -9.0271 | 112.5916 | 15.9622 | 9.4208 | 112.9257 | -9.2972 | -0.22888 | -120.9229 | 0.004578 | 0.14649 | -121.7834 | -0.24719 | 0.16937 | 0.23346 | 25.0122 | 18.4708 | 0.022888 | 0.88348 | 0.004578 | 121.9757 | 121.6415 | -0.24719 | 0.88348 | 0.004578 | 121.6415 | 0.022888 | 121.9757 | -122.0352 | -122.0535
1322.3281 | 121.9803 | -8.6929 | 113.0676 | 0.0016785 | 0.015755 | 0.02208 | 0.0050564 | 0.057398 | 0.064444 | 0.15724 | -8.757 | -8.0292 | -8.963 | -8.5144 | -8.6288 | 112.9898 | 15.9531 | 9.613 | 113.2141 | -8.931 | -0.27008 | -121.0968 | -0.064087 | 0.17853 | -121.6965 | -0.23804 | 0.14648 | 0.20599 | 24.646 | 18.306 | 0.064087 | 0.66376 | -0.064087 | 121.907 | 121.6827 | -0.23804 | 0.66376 | -0.064087 | 121.6827 | 0.064087 | 121.907 | -122.0306 | -121.9986
1324 | 121.962 | -8.6746 | 113.0722 | 0.0016785 | 0.013405 | 0.019944 | 0.00527 | 0.057826 | 0.062948 | 0.15575 | -8.7662 | -8.0154 | -8.9722 | -8.519 | -8.638 | 112.9898 | 15.9119 | 9.5123 | 113.2187 | -8.963 | -0.29755 | -121.0876 | -0.091552 | 0.15564 | -121.7102 | -0.28839 | 0.14648 | 0.20599 | 24.5865 | 18.187 | 0.036622 | 0.65918 | -0.091552 | 121.8933 | 121.6644 | -0.28839 | 0.65918 | -0.091552 | 121.6644 | 0.036622 | 121.8933 | -122.0444 | -122.0352
1325.6875 | 121.9162 | -8.7341 | 113.0402 | -0.013581 | 0.013618 | 0.01738 | 0.0065518 | 0.056544 | 0.061666 | 0.15788 | -8.6792 | -7.9926 | -8.963 | -8.4412 | -8.5373 | 113.0722 | 15.9027 | 9.9289 | 113.2141 | -8.9264 | -0.22888 | -121.0327 | 0.054932 | 0.29297 | -121.5775 | -0.19226 | 0.17395 | 0.28381 | 24.6368 | 18.663 | 0.19684 | 0.74158 | 0.054932 | 121.9482 | 121.8063 | -0.19226 | 0.74158 | 0.054932 | 121.8063 | 0.19684 | 121.9482 | -122.0032 | -121.9666
1327.4062 | 121.9299 | -14.6896 | 107.1259 | -0.005951 | 0.015114 | 0.018448 | 0.0071926 | 0.055903 | 0.062307 | 0.15831 | -14.5844 | -8.8348 | -14.7446 | -14.3372 | -14.4653 | 107.2632 | 13.5406 | 7.37 | 107.4005 | -14.74 | -0.054932 | -115.9607 | 0.10529 | 0.35248 | -121.5912 | -0.050354 | 0.27466 | 0.16022 | 28.2303 | 22.0596 | 0.2243 | 5.8548 | 0.10529 | 122.0901 | 121.9528 | -0.050354 | 5.8548 | 0.10529 | 121.9528 | 0.2243 | 122.0901 | -121.8704 | -121.8658
1329.0938 | 121.8567 | -12.4008 | 109.4604 | 0.0016785 | 0.017036 | 0.019944 | 0.011679 | 0.061671 | 0.058676 | 0.15788 | -12.3688 | -8.7936 | -12.5244 | -12.1033 | -12.2223 | 109.4604 | 13.7283 | 8.107 | 109.7031 | -12.442 | -0.1236 | -118.2541 | 0.032044 | 0.29755 | -121.6827 | -0.041199 | 0.24262 | 0.15564 | 26.1292 | 20.5078 | 0.17853 | 3.6072 | 0.032044 | 122.1039 | 121.8613 | -0.041199 | 3.6072 | 0.032044 | 121.8613 | 0.17853 | 122.1039 | -121.9849 | -121.9025
1330.8594 | 121.843 | -11.3068 | 110.5362 | 0.0016785 | 0.014687 | 0.023362 | 0.0078336 | 0.059321 | 0.065725 | 0.15916 | -11.2381 | -8.7296 | -11.467 | -11.0321 | -11.2885 | 110.5041 | 14.3417 | 8.7936 | 110.6735 | -11.4578 | -0.16022 | -119.2657 | 0.068665 | 0.27466 | -121.8246 | -0.15106 | 0.13733 | 0.22888 | 25.6485 | 20.1004 | 0.018311 | 2.5772 | 0.068665 | 121.9803 | 121.8109 | -0.15106 | 2.5772 | 0.068665 | 121.8109 | 0.018311 | 121.9803 | -122.0032 | -121.994
1332.5938 | 121.8384 | -11.5036 | 110.3806 | -0.013581 | 0.015114 | 0.020371 | 0.0078336 | 0.057612 | 0.063803 | 0.15852 | -11.499 | -8.7524 | -11.6867 | -11.2701 | -11.4212 | 110.3165 | 14.0625 | 8.4824 | 110.4858 | -11.6501 | -0.18311 | -119.133 | 0.004578 | 0.23346 | -121.8018 | -0.14648 | 0.10529 | 0.18768 | 25.5661 | 19.986 | 0.082397 | 2.7512 | 0.004578 | 121.9894 | 121.8201 | -0.14648 | 2.7512 | 0.004578 | 121.8201 | 0.082397 | 121.9894 | -122.0673 | -122.0306
1334.2812 | 121.9254 | -11.2015 | 110.5728 | -0.005951 | 0.014046 | 0.019089 | 0.005911 | 0.057826 | 0.060812 | 0.15639 | -11.4258 | -8.7387 | -11.6226 | -11.174 | -11.3113 | 110.3622 | 14.6805 | 8.8486 | 110.5591 | -11.586 | -0.42114 | -119.3115 | -0.2243 | 0.027466 | -121.8842 | -0.38452 | -0.013733 | 0.19684 | 25.882 | 20.05 | -0.10986 | 2.4628 | -0.2243 | 121.7606 | 121.5637 | -0.38452 | 2.4628 | -0.2243 | 121.5637 | -0.10986 | 121.7606 | -122.1954 | -122.1588
1336.0312 | 121.8521 | -11.1786 | 110.6873 | -0.005951 | 0.018318 | 0.025498 | 0.014456 | 0.061884 | 0.059317 | 0.15959 | -11.2289 | -8.7112 | -11.4395 | -11.0229 | -11.1649 | 110.5041 | 14.2136 | 8.6838 | 110.8383 | -11.3983 | -0.26093 | -119.3985 | -0.050354 | 0.15564 | -121.8521 | -0.21973 | 0.15106 | 0.21057 | 25.3922 | 19.8624 | 0.013733 | 2.4673 | -0.050354 | 122.0169 | 121.6827 | -0.21973 | 2.4673 | -0.050354 | 121.6827 | 0.013733 | 122.0169 | -122.1268 | -122.0856
1337.7812 | 121.9757 | -11.3388 | 110.4538 | -0.013581 | 0.012978 | 0.016312 | 0.0084744 | 0.05868 | 0.060812 | 0.16002 | -11.4258 | -8.7387 | -11.6272 | -11.174 | -11.2976 | 110.3348 | 14.3143 | 8.6792 | 110.5911 | -11.618 | -0.28839 | -119.1925 | -0.086975 | 0.16479 | -121.7514 | -0.27924 | 0.13733 | 0.20142 | 25.6531 | 20.018 | 0.041199 | 2.6001 | -0.086975 | 121.9299 | 121.6736 | -0.27924 | 2.6001 | -0.086975 | 121.6736 | 0.041199 | 121.9299 | -122.081 | -122.0718
1339.5312 | 121.8384 | -11.2473 | 110.582 | 0.0016785 | 0.015541 | 0.018662 | 0.012747 | 0.059107 | 0.05953 | 0.16002 | -11.3022 | -8.725 | -11.5173 | -11.0916 | -11.2198 | 110.4401 | 14.122 | 8.7112 | 110.7651 | -11.467 | -0.27008 | -119.3069 | -0.054932 | 0.15564 | -121.8018 | -0.21973 | 0.18311 | 0.21515 | 25.3693 | 19.9585 | 0.027465 | 2.5223 | -0.054932 | 122.0123 | 121.6873 | -0.21973 | 2.5223 | -0.054932 | 121.6873 | 0.027465 | 122.0123 | -122.0993 | -122.0489
1341.2188 | 121.8796 | -11.1832 | 110.6598 | 0.0016785 | 0.014687 | 0.023575 | 0.014029 | 0.061457 | 0.062094 | 0.15916 | -11.3205 | -8.7204 | -11.4944 | -11.1511 | -11.3022 | 110.3439 | 13.4079 | 8.9081 | 110.6644 | -11.554 | -0.31128 | -119.3802 | -0.13733 | 0.032044 | -121.962 | -0.37079 | 0.004578 | 0.17395 | 24.5911 | 20.0912 | -0.11902 | 2.4628 | -0.13733 | 121.8475 | 121.5271 | -0.37079 | 2.4628 | -0.13733 | 121.5271 | -0.11902 | 121.8475 | -122.1542 | -122.2137
1342.9531 | 121.9666 | -9.6359 | 112.1384 | -0.005951 | 0.010841 | 0.015885 | 0.0033474 | 0.059107 | 0.062094 | 0.16023 | -9.7321 | -8.4229 | -9.8831 | -9.4894 | -9.5718 | 112.0743 | 14.0671 | 9.6359 | 112.3123 | -9.8648 | -0.24719 | -120.5612 | -0.096131 | 0.14648 | -121.7102 | -0.22888 | 0.17395 | 0.15106 | 23.703 | 19.2719 | 0.064087 | 1.2131 | -0.096131 | 121.9482 | 121.7102 | -0.22888 | 1.2131 | -0.096131 | 121.7102 | 0.064087 | 121.9482 | -122.0215 | -122.0032
1344.7031 | 121.8658 | -9.4711 | 112.3856 | -0.005951 | 0.015541 | 0.020585 | 0.012533 | 0.062312 | 0.061453 | 0.16023 | -9.5489 | -8.3313 | -9.7275 | -9.3338 | -9.4299 | 112.2253 | 13.0966 | 9.7549 | 112.5 | -9.6909 | -0.25635 | -120.7169 | -0.07782 | 0.13733 | -121.8155 | -0.21973 | 0.11444 | 0.17853 | 22.5677 | 19.2261 | 0.041198 | 1.1398 | -0.07782 | 121.9711 | 121.6965 | -0.21973 | 1.1398 | -0.07782 | 121.6965 | 0.041198 | 121.9711 | -122.113 | -122.0764
1346.4531 | 121.8658 | -9.8923 | 111.9781 | -0.005951 | 0.017036 | 0.018448 | 0.012533 | 0.060816 | 0.061666 | 0.16215 | -9.9152 | -8.4595 | -10.1028 | -9.7412 | -9.8648 | 111.7767 | 13.2614 | 10.0616 | 112.1384 | -10.0983 | -0.21057 | -120.4376 | -0.022888 | 0.15106 | -121.843 | -0.20599 | 0.16022 | 0.18768 | 23.1537 | 19.9539 | 0.027466 | 1.4328 | -0.022888 | 122.0306 | 121.669 | -0.20599 | 1.4328 | -0.022888 | 121.669 | 0.027466 | 122.0306 | -122.081 | -122.0764
1348.1406 | 117.5903 | -7.814 | 109.8175 | 0.0016785 | 0.014259 | 0.021653 | 6.9544 | -0.00049356 | 0.040304 | 7.0237 | -9.5947 | -8.3588 | -9.7458 | 83.6884 | 14.9368 | 86.3297 | 26.9119 | 17.7017 | 101.9348 | -1.4374 | -1.9318 | -118.1763 | -1.7807 | 91.5024 | -94.8807 | 6.3766 | -7.8827 | 0.15106 | 34.726 | 25.5157 | 22.7509 | -0.54474 | -1.7807 | 109.7488 | 94.1437 | 6.3766 | -0.54474 | -1.7807 | 94.1437 | 22.7509 | 109.7488 | -119.5633 | -111.2549
1349.875 | 116.9998 | -9.7595 | 107.2861 | 0.0016785 | 0.017036 | 0.022294 | 6.9544 | 0.0010018 | 0.037741 | 7.0237 | -9.7412 | -8.4274 | -9.9609 | 82.9147 | 13.4995 | 83.8348 | 26.889 | 17.2394 | 99.9161 | -2.5085 | -0.20142 | -115.7135 | 0.01831 | 92.6743 | -93.7866 | 7.251 | -7.37 | 0.21973 | 36.6486 | 26.9989 | 23.259 | 1.3321 | 0.01831 | 109.6756 | 93.5944 | 7.251 | 1.3321 | 0.01831 | 93.5944 | 23.259 | 109.6756 | -117.247 | -109.7946
1351.5469 | 116.7206 | -9.5673 | 107.0206 | -0.005951 | 0.013832 | 0.017808 | 6.9544 | 0.00078824 | 0.040945 | 7.0237 | -9.6176 | -8.4 | -9.8099 | 82.7362 | 13.6093 | 83.7112 | 29.0726 | 17.9764 | 99.6231 | -2.4033 | -0.24261 | -115.4205 | -0.050354 | 92.3035 | -93.4113 | 7.164 | -7.3975 | 0.19226 | 38.6398 | 27.5436 | 23.1766 | 1.1673 | -0.050354 | 109.1904 | 93.2785 | 7.164 | 1.1673 | -0.050354 | 93.2785 | 23.1766 | 109.1904 | -116.8304 | -109.4238
1353.2812 | 116.4322 | -9.0866 | 107.1487 | 0.0016785 | 0.018959 | 0.020371 | 6.9544 | -0.00070716 | -0.0047703 | 7.0237 | -9.2102 | -8.1985 | -9.407 | 82.8781 | 97.0184 | 83.8211 | 32.6431 | 21.2448 | 99.8199 | -2.0279 | -0.32043 | -115.3473 | -0.1236 | 91.9647 | -10.1303 | 7.0587 | -7.3288 | 0.19684 | 41.7297 | 30.3314 | 106.105 | 0.88806 | -0.1236 | 108.9066 | 92.9077 | 7.0587 | 0.88806 | -0.1236 | 92.9077 | 106.105 | 108.9066 | -116.5558 | -109.1766
1354.9531 | 116.0568 | -9.1461 | 106.9199 | -0.005951 | 0.015327 | 0.023362 | 6.9544 | 0.0018564 | -0.0071201 | 7.0237 | -9.1324 | -8.194 | -9.3613 | 82.7957 | 96.4691 | 83.7021 | 33.7143 | 22.1558 | 99.6597 | -2.0096 | -0.21515 | -115.1138 | 0.013733 | 91.9418 | -10.4507 | 7.1365 | -7.2601 | 0.22888 | 42.8604 | 31.3019 | 105.6152 | 0.95215 | 0.013733 | 108.8058 | 92.8482 | 7.1365 | 0.95215 | 0.013733 | 92.8482 | 105.6152 | 108.8058 | -116.2811 | -108.9294
1356.6875 | 115.9012 | -9.137 | 106.6315 | -0.005951 | 0.014687 | 0.020798 | 6.9544 | -0.0024162 | -0.0051975 | 7.0237 | -9.1415 | -8.2443 | -9.3796 | 82.6035 | 96.048 | 83.5876 | 33.7967 | 22.348 | 99.3027 | -2.092 | -0.24262 | -114.8758 | -0.004578 | 91.7404 | -10.5835 | 7.045 | -7.3288 | 0.23804 | 42.9337 | 31.485 | 105.1849 | 0.89264 | -0.004578 | 108.4396 | 92.7246 | 7.045 | 0.89264 | -0.004578 | 92.7246 | 105.1849 | 108.4396 | -116.011 | -108.7234
1358.375 | 115.6998 | -89.6942 | 25.795 | -0.005951 | 0.018318 | 0.01204 | 6.9544 | 0.0018564 | 0.0039883 | 7.0237 | -0.004578 | 0.14648 | -0.32959 | 1.5106 | 2.092 | 0.54474 | -3.3829 | -10.3226 | 18.4891 | -82.695 | 89.3646 | -25.6485 | 89.6896 | 91.2048 | -23.703 | 6.9992 | -7.3059 | 0.32501 | 86.3113 | 79.3716 | 91.7862 | 89.8407 | 89.6896 | 108.1833 | 90.239 | 6.9992 | 89.8407 | 89.6896 | 90.239 | 91.7862 | 108.1833 | -26.1246 | -108.49
1360.0469 | 115.6952 | -89.5706 | 25.7172 | -0.005951 | 0.013618 | 0.014176 | 6.9544 | -0.00049356 | 0.0022793 | 7.0237 | 0.013733 | 0.14648 | -0.27924 | 1.5335 | 1.8997 | 0.48523 | -3.4836 | -10.0754 | 18.4616 | -82.6401 | 89.2914 | -25.5707 | 89.5844 | 91.1041 | -23.8174 | 6.9305 | -7.2556 | 0.29297 | 86.087 | 79.4952 | 91.4703 | 89.7171 | 89.5844 | 108.0322 | 90.0558 | 6.9305 | 89.7171 | 89.5844 | 90.0558 | 91.4703 | 108.0322 | -25.9964 | -108.3572
1361.7812 | 115.5487 | -89.5569 | 25.6897 | -0.005951 | 0.015755 | 0.017808 | 6.9544 | -0.00049356 | 0.0018521 | 7.0237 | 0.004578 | 0.15106 | -0.32501 | 1.5427 | 1.1719 | 0.032043 | -2.7374 | -10.6842 | 18.457 | -82.5806 | 89.2319 | -25.5386 | 89.5615 | 91.0995 | -24.5178 | 6.9763 | -7.2327 | 0.32959 | 86.8195 | 78.8727 | 90.7288 | 89.7079 | 89.5615 | 108.0139 | 89.5889 | 6.9763 | 89.7079 | 89.5615 | 89.5889 | 90.7288 | 108.0139 | -26.0147 | -108.2703
1363.4688 | 115.3473 | -89.4974 | 25.7034 | 0.0016785 | 0.014687 | 0.014817 | 6.9544 | 0.00078824 | 0.0037747 | 7.0237 | 0.082397 | 0.1236 | -0.2655 | 1.5976 | 0.98877 | 0.11444 | -3.5751 | -10.3455 | 18.3929 | -82.5027 | 89.2319 | -25.5798 | 89.5798 | 91.095 | -24.7147 | 6.9946 | -7.3105 | 0.3479 | 85.9222 | 79.1519 | 90.4861 | 89.621 | 89.5798 | 107.8903 | 89.6118 | 6.9946 | 89.621 | 89.5798 | 89.6118 | 90.4861 | 107.8903 | -25.9689 | -108.2062
1365.2188 | 115.2237 | -89.4608 | 25.6668 | 0.0016785 | 0.0149 | 0.013962 | 6.9544 | 0.00057464 | 0.0016385 | 7.0237 | 0.091553 | 0.11444 | -0.2655 | 1.6205 | 2.4765 | 0.67749 | -3.6942 | -12.4237 | 18.3701 | -82.457 | 89.1953 | -25.5524 | 89.5523 | 91.0812 | -23.1903 | 7.0038 | -7.2968 | 0.35706 | 85.7666 | 77.037 | 91.9373 | 89.5752 | 89.5523 | 107.8308 | 90.1382 | 7.0038 | 89.5752 | 89.5523 | 90.1382 | 91.9373 | 107.8308 | -25.9323 | -108.1238
1366.9531 | 115.1733 | -89.4012 | 25.6348 | 0.0016785 | 0.016182 | 0.01204 | 6.9544 | 0.0022836 | 0.0005703 | 7.0237 | 0.018311 | 0.14191 | -0.29755 | 1.5701 | 1.1993 | 0.036621 | -3.6758 | -13.4399 | 18.3884 | -82.4203 | 89.1037 | -25.4929 | 89.4196 | 90.9714 | -24.4354 | 6.9809 | -7.2464 | 0.31586 | 85.7254 | 75.9613 | 90.6006 | 89.5432 | 89.4196 | 107.7896 | 89.4379 | 6.9809 | 89.5432 | 89.4196 | 89.4379 | 90.6006 | 107.7896 | -25.9323 | -108.0551
1368.6406 | 115.2145 | -89.3143 | 25.6073 | 0.0016785 | 0.017891 | 0.0081947 | 6.9544 | 0.00036104 | 0.0016385 | 7.0237 | -0.022888 | 0.15106 | -0.32044 | 1.5381 | 0.81482 | -0.23804 | -3.7994 | -14.8224 | 18.3929 | -82.4295 | 88.9938 | -25.4562 | 89.2914 | 90.8524 | -24.7925 | 6.8848 | -7.2144 | 0.29755 | 85.5148 | 74.4919 | 90.1291 | 89.4653 | 89.2914 | 107.7072 | 89.0762 | 6.8848 | 89.4653 | 89.2914 | 89.0762 | 90.1291 | 107.7072 | -25.9277 | -108.0368
1370.3906 | 115.1047 | -89.3417 | 25.6256 | 0.0016785 | 0.016182 | 0.013108 | 6.9544 | 0.0016428 | 0.0018521 | 7.0237 | -0.022888 | 0.15564 | -0.31586 | 1.474 | 0.72784 | -0.3891 | -4.1153 | -16.6626 | 18.3838 | -82.4203 | 89.0259 | -25.47 | 89.3188 | 90.8157 | -24.8978 | 6.9214 | -7.2418 | 0.29297 | 85.2264 | 72.6791 | 90.0696 | 89.4974 | 89.3188 | 107.7255 | 88.9526 | 6.9214 | 89.4974 | 89.3188 | 88.9526 | 90.0696 | 107.7255 | -25.9415 | -108.046
1372.125 | 115.0269 | -89.2868 | 25.589 | -0.005951 | 0.016823 | 0.012681 | 6.9544 | 0.0010018 | 0.0007839 | 7.0237 | 0.004578 | 0.16479 | -0.31586 | 1.5381 | 1.6846 | -0.022888 | -4.0146 | -15.8936 | 18.3792 | -82.37 | 88.9709 | -25.4242 | 89.2914 | 90.8249 | -23.9044 | 6.9168 | -7.2098 | 0.32044 | 85.2722 | 73.3932 | 90.9714 | 89.4516 | 89.2914 | 107.666 | 89.2639 | 6.9168 | 89.4516 | 89.2914 | 89.2639 | 90.9714 | 107.666 | -25.9048 | -107.959
1373.875 | 115.0772 | -89.2685 | 25.5569 | -0.005951 | 0.016182 | 0.016099 | 6.9544 | -0.00027976 | 0.0027067 | 7.0237 | -0.018311 | 0.16937 | -0.32501 | 1.5427 | 1.1215 | -0.42114 | -3.6621 | -15.1062 | 18.3792 | -82.3883 | 88.9435 | -25.3876 | 89.2502 | 90.8112 | -24.4354 | 6.8802 | -7.1777 | 0.3067 | 85.6064 | 74.1623 | 90.39 | 89.4379 | 89.2502 | 107.6477 | 88.8474 | 6.8802 | 89.4379 | 89.2502 | 88.8474 | 90.39 | 107.6477 | -25.882 | -107.9453
1375.5625 | 114.9673 | -89.2593 | 25.5341 | -0.013581 | 0.019173 | 0.016099 | 6.9544 | 0.0018564 | 0.0016385 | 7.0237 | 0.018311 | 0.15106 | -0.28839 | 1.5427 | 1.355 | -0.37079 | -3.5431 | -13.5727 | 18.3517 | -82.37 | 88.9709 | -25.383 | 89.2776 | 90.802 | -24.1791 | 6.8893 | -7.1823 | 0.3067 | 85.7162 | 75.6866 | 90.6143 | 89.4104 | 89.2776 | 107.6111 | 88.8885 | 6.8893 | 89.4104 | 89.2776 | 88.8885 | 90.6143 | 107.6111 | -25.8224 | -107.9041
1377.3125 | 114.9765 | -89.2731 | 25.5753 | -0.013581 | 0.014259 | 0.010117 | 6.9544 | 0.00036104 | 0.0035611 | 7.0237 | 0.009155 | 0.16937 | -0.30212 | 1.5747 | 1.7578 | -0.43488 | -3.2822 | -12.648 | 18.338 | -82.3654 | 88.9709 | -25.4059 | 89.2822 | 90.8478 | -23.8174 | 6.9077 | -7.2372 | 0.31128 | 85.9909 | 76.6251 | 91.0309 | 89.4424 | 89.2822 | 107.6111 | 88.8382 | 6.9077 | 89.4424 | 89.2822 | 88.8382 | 91.0309 | 107.6111 | -25.8774 | -107.9407
1379.0625 | 115.004 | -89.2365 | 25.5203 | -0.005951 | 0.017677 | 0.010331 | 6.9544 | 0.00057464 | 0.0018521 | 7.0237 | 0.09613 | 0.11444 | -0.2655 | 1.6342 | 2.1606 | -0.20599 | -3.4241 | -12.5656 | 18.3151 | -82.3608 | 88.9709 | -25.4059 | 89.3326 | 90.8707 | -23.3597 | 6.8756 | -7.2052 | 0.36163 | 85.8124 | 76.6708 | 91.3971 | 89.3509 | 89.3326 | 107.5516 | 89.0305 | 6.8756 | 89.3509 | 89.3326 | 89.0305 | 91.3971 | 107.5516 | -25.7858 | -107.8812
1380.75 | 114.8895 | -89.2502 | 25.5524 | -0.013581 | 0.015541 | 0.015458 | 6.9544 | 0.0016428 | 0.0003567 | 7.0237 | 0.073242 | 0.13275 | -0.28381 | 1.6296 | 2.2568 | -0.20599 | -3.4836 | -13.3484 | 18.3517 | -82.3334 | 88.9664 | -25.4196 | 89.3234 | 90.8798 | -23.2956 | 6.9168 | -7.2006 | 0.35706 | 85.7666 | 75.9018 | 91.507 | 89.3829 | 89.3234 | 107.6019 | 89.0442 | 6.9168 | 89.3829 | 89.3234 | 89.0442 | 91.507 | 107.6019 | -25.8362 | -107.8857
1382.4844 | 114.949 | -89.2456 | 25.5249 | -0.013581 | 0.018318 | 0.0096899 | 6.9544 | 0.0024972 | 0.0005703 | 7.0237 | -0.009155 | 0.16022 | -0.29755 | 1.5289 | 2.211 | -0.37994 | -3.2227 | -13.0875 | 18.3655 | -82.3791 | 88.9481 | -25.3647 | 89.2364 | 90.7745 | -23.3139 | 6.8665 | -7.1594 | 0.28839 | 86.0229 | 76.1581 | 91.4566 | 89.4058 | 89.2364 | 107.6111 | 88.8657 | 6.8665 | 89.4058 | 89.2364 | 88.8657 | 91.4566 | 107.6111 | -25.8224 | -107.9041
1384.1719 | 114.9902 | -89.2227 | 25.502 | -0.005951 | 0.013832 | 0.010758 | 6.9544 | 0.00078824 | 0.0039883 | 7.0237 | 0.073242 | 0.13275 | -0.25635 | 1.6571 | 1.68 | -0.81024 | -3.2501 | -12.4603 | 18.3105 | -82.338 | 88.9664 | -25.3693 | 89.296 | 90.8798 | -23.822 | 6.8848 | -7.1915 | 0.32959 | 85.9726 | 76.7624 | 90.9027 | 89.3555 | 89.296 | 107.5333 | 88.4125 | 6.8848 | 89.3555 | 89.296 | 88.4125 | 90.9027 | 107.5333 | -25.7584 | -107.84
1385.9375 | 115.004 | -89.2639 | 25.5249 | 0.0016785 | 0.014046 | 0.011612 | 6.9544 | 0.00014744 | 0.0014249 | 7.0237 | 0.086975 | 0.12817 | -0.27466 | 1.6571 | 2.1103 | -0.82855 | -3.0853 | -12.3001 | 18.306 | -82.3608 | 88.9893 | -25.3967 | 89.3509 | 90.921 | -23.4146 | 6.9031 | -7.2189 | 0.36163 | 86.1786 | 76.9638 | 91.3742 | 89.3921 | 89.3509 | 107.5699 | 88.4354 | 6.9031 | 89.3921 | 89.3509 | 88.4354 | 91.3742 | 107.5699 | -25.7996 | -107.8857
1387.6875 | 118.0756 | -117.6453 | 0.32044 | 0.0016785 | 0.013832 | 0.012253 | 0.026205 | -0.0039114 | -0.0039157 | 0.015823 | 0.09613 | 0.14191 | -0.27008 | 0.18768 | 0.10986 | 0.23346 | -0.004578 | 0.46692 | 0.35706 | -0.050354 | 117.3752 | -0.17853 | 117.7414 | 117.8329 | -0.21057 | 117.5949 | 0.036621 | 0.36621 | 117.6407 | 118.1122 | 117.7551 | 117.7872 | 117.7414 | 118.0023 | 117.8787 | 117.5949 | 117.7872 | 117.7414 | 117.8787 | 117.7551 | 118.0023 | -0.59052 | -0.37079
1389.3594 | 118.5196 | -117.9565 | 0.27008 | 0.0016785 | 0.0149 | 0.0090491 | 0.025564 | -0.0096794 | -0.0051975 | 0.016891 | 0 | 0.18768 | -0.27924 | 0.09613 | 0.032043 | 0.10071 | 0.18768 | 0.39368 | 0.41657 | -0.11902 | 117.6773 | -0.082398 | 117.9565 | 118.0527 | -0.23804 | 117.8375 | 0.14648 | 0.27924 | 118.1442 | 118.3502 | 117.9886 | 118.1442 | 117.9565 | 118.3731 | 118.0573 | 117.8375 | 118.1442 | 117.9565 | 118.0573 | 117.9886 | 118.3731 | -0.54932 | -0.3891
1391.0312 | 118.5425 | -118.2083 | 0.3067 | 0.0016785 | 0.016396 | 0.011826 | 0.029623 | -0.0066886 | -0.0056247 | 0.017105 | 0.050354 | 0.15564 | -0.28839 | 0.13275 | 0.041199 | 0.11444 | 0.091553 | 0.37079 | 0.37994 | -0.10529 | 117.9199 | -0.15106 | 118.2587 | 118.3411 | -0.2655 | 118.103 | 0.073242 | 0.33875 | 118.2999 | 118.5791 | 118.2495 | 118.364 | 118.2587 | 118.5883 | 118.3228 | 118.103 | 118.364 | 118.2587 | 118.3228 | 118.2495 | 118.5883 | -0.59509 | -0.41199
1392.7656 | 118.689 | -118.2495 | 0.32501 | -0.005951 | 0.015114 | 0.01204 | 0.0277 | -0.0045524 | -0.0064791 | 0.016464 | -0.013733 | 0.16937 | -0.31128 | 0.086975 | -0.004578 | 0.068665 | 0.11444 | 0.37079 | 0.4303 | -0.064087 | 117.9382 | -0.15564 | 118.2358 | 118.3365 | -0.32959 | 118.1854 | 0.10529 | 0.29755 | 118.364 | 118.6203 | 118.2449 | 118.4189 | 118.2358 | 118.6798 | 118.3182 | 118.1854 | 118.4189 | 118.2358 | 118.3182 | 118.2449 | 118.6798 | -0.63629 | -0.3891
1394.5156 | 118.8263 | -118.3228 | 0.3479 | -0.013581 | 0.015541 | 0.011185 | 0.021292 | -0.0088248 | -0.0034885 | 0.017318 | 0.059509 | 0.15106 | -0.25177 | 0.15106 | 0.09613 | 0.16937 | 0.022888 | 0.49439 | 0.43488 | -0.009155 | 118.071 | -0.19684 | 118.3823 | 118.4738 | -0.25177 | 118.3136 | 0.086975 | 0.31128 | 118.3456 | 118.8171 | 118.4189 | 118.4738 | 118.3823 | 118.7576 | 118.4921 | 118.3136 | 118.4738 | 118.3823 | 118.4921 | 118.4189 | 118.7576 | -0.59967 | -0.35706
1396.1875 | 118.8538 | -118.5242 | 0.27466 | -0.013581 | 0.014046 | 0.010117 | 0.02706 | -0.009893 | -0.0043429 | 0.014969 | 0.073242 | 0.14191 | -0.23804 | 0.17853 | 0.15564 | 0.31586 | -0.10071 | 0.42114 | 0.31128 | -0.082397 | 118.2861 | -0.13275 | 118.5974 | 118.7027 | -0.11902 | 118.4418 | 0.036621 | 0.31128 | 118.4235 | 118.9453 | 118.6798 | 118.6661 | 118.5974 | 118.8354 | 118.84 | 118.4418 | 118.6661 | 118.5974 | 118.84 | 118.6798 | 118.8354 | -0.5127 | -0.35706
1397.9375 | 119.0369 | -118.5791 | 0.24719 | -0.005951 | 0.014046 | 0.0090491 | 0.026846 | -0.012029 | -0.0034885 | 0.013687 | 0.068665 | 0.13733 | -0.25635 | 0.19684 | 0.12817 | 0.28381 | 0.041199 | 0.42114 | 0.32959 | -0.10986 | 118.3228 | -0.10986 | 118.6478 | 118.7759 | -0.11902 | 118.4692 | 0.082398 | 0.32501 | 118.6203 | 119.0002 | 118.7073 | 118.7164 | 118.6478 | 118.9087 | 118.8629 | 118.4692 | 118.7164 | 118.6478 | 118.8629 | 118.7073 | 118.9087 | -0.50354 | -0.35706
1399.6875 | 119.0231 | -118.7119 | 0.27466 | -0.005951 | 0.014687 | 0.01503 | 0.030905 | -0.0062614 | -0.0034885 | 0.013473 | 0.027466 | 0.16479 | -0.27924 | 0.14648 | 0.073242 | 0.2655 | -0.013733 | 0.37994 | 0.34332 | -0.09613 | 118.4326 | -0.10986 | 118.7393 | 118.8583 | -0.20142 | 118.6157 | 0.068665 | 0.3067 | 118.6981 | 119.0918 | 118.7851 | 118.8766 | 118.7393 | 119.0552 | 118.9774 | 118.6157 | 118.8766 | 118.7393 | 118.9774 | 118.7851 | 119.0552 | -0.55389 | -0.37079
1401.4219 | 119.0964 | -118.7668 | 0.27466 | 0.016937 | 0.015968 | 0.012253 | 0.029196 | -0.007543 | -0.0062655 | 0.014114 | 0.036621 | 0.16479 | -0.28381 | 0.13733 | 0.054932 | 0.21973 | 0.086975 | 0.34332 | 0.36163 | -0.10529 | 118.483 | -0.10986 | 118.8034 | 118.9041 | -0.21973 | 118.6615 | 0.086975 | 0.32043 | 118.8538 | 119.1101 | 118.8217 | 118.9316 | 118.8034 | 119.1284 | 118.9865 | 118.6615 | 118.9316 | 118.8034 | 118.9865 | 118.8217 | 119.1284 | -0.55847 | -0.37994
1403.1094 | 119.1925 | -118.8538 | 0.29755 | 0.0016785 | 0.015327 | 0.012253 | 0.030478 | -0.0051932 | -0.0088291 | 0.012405 | 0.054932 | 0.16937 | -0.27924 | 0.16022 | 0.10071 | 0.27008 | 0.073242 | 0.40741 | 0.37537 | -0.10529 | 118.5745 | -0.12817 | 118.9087 | 119.014 | -0.19684 | 118.7485 | 0.07782 | 0.33417 | 118.927 | 119.2612 | 118.9545 | 119.0231 | 118.9087 | 119.2291 | 119.1238 | 118.7485 | 119.0231 | 118.9087 | 119.1238 | 118.9545 | 119.2291 | -0.57678 | -0.40283
1404.8594 | 119.3253 | -118.9041 | 0.27008 | -0.013581 | 0.016823 | 0.0071265 | 0.024069 | -0.0094656 | -0.0045565 | 0.010696 | 0.10071 | 0.16022 | -0.23804 | 0.21973 | 0.20142 | 0.35248 | -0.022888 | 0.50354 | 0.33417 | -0.045776 | 118.6661 | -0.10986 | 119.0048 | 119.1238 | -0.068665 | 118.8583 | 0.064086 | 0.33875 | 118.8812 | 119.4077 | 119.1055 | 119.0643 | 119.0048 | 119.2383 | 119.2566 | 118.8583 | 119.0643 | 119.0048 | 119.2566 | 119.1055 | 119.2383 | -0.50812 | -0.31586
1406.5938 | 119.4397 | -118.9728 | 0.2655 | 0.0016785 | 0.015968 | 0.0084083 | 0.026846 | -0.0083976 | -0.0049839 | 0.011551 | 0.054932 | 0.16479 | -0.27466 | 0.1236 | 0.10071 | 0.26093 | 0.1236 | 0.40283 | 0.39368 | -0.09613 | 118.6981 | -0.10071 | 119.0277 | 119.0964 | -0.16479 | 118.8766 | 0.12817 | 0.32959 | 119.0964 | 119.3756 | 119.0735 | 119.1376 | 119.0277 | 119.3665 | 119.2337 | 118.8766 | 119.1376 | 119.0277 | 119.2337 | 119.0735 | 119.3665 | -0.54016 | -0.36163
1408.2656 | 119.4214 | -118.9865 | 0.31128 | 0.0016785 | 0.015114 | 0.016099 | 0.031759 | -0.0060478 | -0.0084017 | 0.010055 | -0.022888 | 0.1831 | -0.27924 | 0.068665 | 0.032043 | 0.2243 | 0.13733 | 0.34332 | 0.39368 | -0.064087 | 118.7073 | -0.12817 | 118.9636 | 119.0552 | -0.27924 | 118.9224 | 0.082398 | 0.25635 | 119.1238 | 119.3298 | 119.0186 | 119.1696 | 118.9636 | 119.3802 | 119.2108 | 118.9224 | 119.1696 | 118.9636 | 119.2108 | 119.0186 | 119.3802 | -0.59051 | -0.37537
1410.0156 | 119.5541 | -119.0552 | 0.29755 | -0.013581 | 0.013191 | 0.0064857 | 0.025778 | -0.007543 | -0.0069065 | 0.01091 | 0.082397 | 0.13733 | -0.24261 | 0.21057 | 0.1831 | 0.36163 | 0.10529 | 0.51727 | 0.37537 | -0.050354 | 118.8126 | -0.16022 | 119.1376 | 119.2657 | -0.11444 | 119.0048 | 0.07782 | 0.32501 | 119.1605 | 119.5724 | 119.2383 | 119.1925 | 119.1376 | 119.4305 | 119.4168 | 119.0048 | 119.1925 | 119.1376 | 119.4168 | 119.2383 | 119.4305 | -0.54016 | -0.3479
1411.75 | 119.4946 | -119.1422 | 0.32501 | -0.005951 | 0.014259 | 0.010972 | 0.028341 | -0.0069022 | -0.0069065 | 0.011764 | 0.10529 | 0.12817 | -0.23804 | 0.21973 | 0.19226 | 0.3891 | -0.064087 | 0.49439 | 0.37079 | -0.027466 | 118.9041 | -0.19684 | 119.2474 | 119.3619 | -0.13275 | 119.1147 | 0.045777 | 0.34332 | 119.0781 | 119.6365 | 119.3344 | 119.2703 | 119.2474 | 119.5129 | 119.5312 | 119.1147 | 119.2703 | 119.2474 | 119.5312 | 119.3344 | 119.5129 | -0.56305 | -0.35248
1413.4219 | 119.6548 | -119.1742 | 0.31128 | -0.005951 | 0.012764 | 0.013749 | 0.024283 | -0.01032 | -0.0066929 | 0.01091 | 0.10071 | 0.13733 | -0.23804 | 0.21973 | 0.20142 | 0.38452 | 0.027466 | 0.54016 | 0.37994 | -0.054932 | 118.9362 | -0.17395 | 119.2749 | 119.3939 | -0.10986 | 119.1193 | 0.068665 | 0.33875 | 119.2017 | 119.7144 | 119.3756 | 119.3115 | 119.2749 | 119.5541 | 119.5587 | 119.1193 | 119.3115 | 119.2749 | 119.5587 | 119.3756 | 119.5541 | -0.54932 | -0.36621
1415.1719 | 119.7876 | -119.252 | 0.27924 | -0.005951 | 0.013191 | 0.011185 | 0.029623 | -0.0090384 | -0.0041293 | 0.011978 | -0.009155 | 0.17395 | -0.29297 | 0.11902 | 0.064087 | 0.22888 | 0.19684 | 0.39368 | 0.38452 | -0.082397 | 118.959 | -0.10529 | 119.2429 | 119.371 | -0.21515 | 119.1696 | 0.10529 | 0.28381 | 119.4489 | 119.6457 | 119.3161 | 119.426 | 119.2429 | 119.6365 | 119.4809 | 119.1696 | 119.426 | 119.2429 | 119.4809 | 119.3161 | 119.6365 | -0.5722 | -0.36163
1416.9219 | 119.8059 | -119.2474 | 0.28839 | -0.005951 | 0.013832 | 0.014603 | 0.022574 | -0.0094656 | -0.0060519 | 0.010055 | 0.045776 | 0.15564 | -0.23346 | 0.14191 | 0.13733 | 0.34332 | 0.045776 | 0.44861 | 0.39368 | -0.032043 | 119.014 | -0.13275 | 119.2932 | 119.3893 | -0.15106 | 119.2154 | 0.10529 | 0.27924 | 119.2932 | 119.696 | 119.3848 | 119.4031 | 119.2932 | 119.6411 | 119.5908 | 119.2154 | 119.4031 | 119.2932 | 119.5908 | 119.3848 | 119.6411 | -0.52185 | -0.32043
1418.6562 | 119.8471 | -119.3344 | 0.3067 | 0.009308 | 0.015327 | 0.0099037 | 0.021078 | -0.010747 | -0.0058383 | 0.010055 | 0.064087 | 0.16937 | -0.27008 | 0.17853 | 0.16937 | 0.39825 | 0.041199 | 0.53101 | 0.3891 | 0.004578 | 119.0643 | -0.13733 | 119.3985 | 119.5129 | -0.13733 | 119.339 | 0.082397 | 0.33417 | 119.3756 | 119.8654 | 119.5038 | 119.5038 | 119.3985 | 119.7235 | 119.7327 | 119.339 | 119.5038 | 119.3985 | 119.7327 | 119.5038 | 119.7235 | -0.57678 | -0.30212
1420.4062 | 119.8242 | -119.426 | 0.32959 | 0.0016785 | 0.012764 | 0.010331 | 0.030691 | -0.0086112 | -0.0079745 | 0.012192 | 0.09613 | 0.13733 | -0.26093 | 0.19684 | 0.17395 | 0.39368 | -0.032043 | 0.50354 | 0.38452 | -0.004578 | 119.165 | -0.19226 | 119.5221 | 119.6228 | -0.15564 | 119.4214 | 0.054931 | 0.35706 | 119.3939 | 119.9295 | 119.5999 | 119.5633 | 119.5221 | 119.8105 | 119.8196 | 119.4214 | 119.5633 | 119.5221 | 119.8196 | 119.5999 | 119.8105 | -0.59052 | -0.33417
1422.0781 | 119.8425 | -119.4855 | 0.34332 | 0.0016785 | 0.015541 | 0.011185 | 0.028341 | -0.0071158 | -0.0045565 | 0.0089871 | 0.11444 | 0.1236 | -0.22888 | 0.21973 | 0.19226 | 0.41199 | -0.032043 | 0.52185 | 0.39825 | 0.009155 | 119.2566 | -0.21973 | 119.5999 | 119.7052 | -0.15106 | 119.4946 | 0.054931 | 0.34332 | 119.4534 | 120.0073 | 119.6777 | 119.6091 | 119.5999 | 119.8837 | 119.8975 | 119.4946 | 119.6091 | 119.5999 | 119.8975 | 119.6777 | 119.8837 | -0.5722 | -0.33417
1423.8281 | 119.9707 | -119.5038 | 0.35248 | 0.009308 | 0.0196 | 0.016526 | 0.033682 | -0.0079704 | -0.0051975 | 0.0096279 | -0.004578 | 0.1831 | -0.28839 | 0.10986 | 0.073242 | 0.27008 | 0.15564 | 0.37079 | 0.44403 | -0.022888 | 119.2154 | -0.16937 | 119.4992 | 119.6136 | -0.27924 | 119.4809 | 0.091553 | 0.28381 | 119.6594 | 119.8746 | 119.577 | 119.6869 | 119.4992 | 119.9478 | 119.7739 | 119.4809 | 119.6869 | 119.4992 | 119.7739 | 119.577 | 119.9478 | -0.64087 | -0.37537
1425.5781 | 119.9203 | -119.6182 | 0.30212 | -0.005951 | 0.015541 | 0.011826 | 0.023428 | -0.0062614 | -0.0051975 | 0.0072781 | 0.1236 | 0.11902 | -0.2243 | 0.21515 | 0.16479 | 0.35248 | -0.082397 | 0.47607 | 0.32959 | -0.041199 | 119.3939 | -0.18311 | 119.7418 | 119.8334 | -0.13733 | 119.577 | 0.027466 | 0.3479 | 119.5358 | 120.0943 | 119.783 | 119.7372 | 119.7418 | 119.9478 | 119.9707 | 119.577 | 119.7372 | 119.7418 | 119.9707 | 119.783 | 119.9478 | -0.52643 | -0.34332
1427.3281 | 120.0485 | -119.664 | 0.29297 | 0.009308 | 0.015968 | 0.011185 | 0.025778 | -0.0071158 | -0.0079745 | 0.011337 | 0.004578 | 0.17853 | -0.28839 | 0.086975 | 0.041199 | 0.23346 | 0.1236 | 0.33417 | 0.40283 | -0.068665 | 119.3756 | -0.11444 | 119.6686 | 119.751 | -0.25177 | 119.5953 | 0.10986 | 0.29297 | 119.7876 | 119.9982 | 119.7052 | 119.8425 | 119.6686 | 120.0668 | 119.8975 | 119.5953 | 119.8425 | 119.6686 | 119.8975 | 119.7052 | 120.0668 | -0.58136 | -0.36163
1429.0781 | 120.0806 | -119.7372 | 0.31586 | 0.0016785 | 0.016823 | 0.011612 | 0.025137 | -0.0062614 | -0.0054111 | 0.01091 | 0 | 0.17395 | -0.28839 | 0.11902 | 0.09613 | 0.25635 | 0.045776 | 0.36621 | 0.38452 | -0.041199 | 119.4489 | -0.14191 | 119.7372 | 119.8563 | -0.21973 | 119.696 | 0.068664 | 0.28839 | 119.783 | 120.1035 | 119.8334 | 119.9112 | 119.7372 | 120.1218 | 119.9936 | 119.696 | 119.9112 | 119.7372 | 119.9936 | 119.8334 | 120.1218 | -0.60425 | -0.35706
1430.8281 | 120.2545 | -119.7189 | 0.27924 | -0.02121 | 0.015755 | 0.011399 | 0.019156 | -0.008184 | -0.0043429 | 0.012832 | 0.032043 | 0.16022 | -0.26093 | 0.15106 | 0.13733 | 0.32501 | 0.036621 | 0.43488 | 0.37079 | -0.054932 | 119.458 | -0.11902 | 119.751 | 119.87 | -0.14191 | 119.664 | 0.091553 | 0.29297 | 119.7556 | 120.1538 | 119.8563 | 119.8792 | 119.751 | 120.0897 | 120.0439 | 119.664 | 119.8792 | 119.751 | 120.0439 | 119.8563 | 120.0897 | -0.54016 | -0.33417
1432.5156 | 120.2774 | -119.7556 | 0.28839 | 0.0016785 | 0.016609 | 0.0096899 | 0.021933 | -0.0090384 | -0.0043429 | 0.0085599 | 0.036621 | 0.16022 | -0.25177 | 0.18768 | 0.16022 | 0.34332 | 0.009155 | 0.48065 | 0.35248 | -0.032043 | 119.5038 | -0.12817 | 119.7922 | 119.9432 | -0.12817 | 119.7235 | 0.064087 | 0.28839 | 119.7647 | 120.2362 | 119.9158 | 119.9158 | 119.7922 | 120.108 | 120.0989 | 119.7235 | 119.9158 | 119.7922 | 120.0989 | 119.9158 | 120.108 | -0.54016 | -0.32043
1434.2656 | 120.3323 | -119.783 | 0.27924 | -0.005951 | 0.015327 | 0.012467 | 0.025351 | -0.010534 | -0.0062655 | 0.0079189 | 0 | 0.16937 | -0.28381 | 0.11444 | 0.07782 | 0.2655 | 0.1831 | 0.39825 | 0.41199 | -0.07782 | 119.4992 | -0.10986 | 119.783 | 119.8975 | -0.20142 | 119.7052 | 0.13275 | 0.28381 | 119.9661 | 120.1813 | 119.8608 | 119.9524 | 119.783 | 120.195 | 120.0485 | 119.7052 | 119.9524 | 119.783 | 120.0485 | 119.8608 | 120.195 | -0.56305 | -0.35706
1436.0156 | 120.2545 | -119.8975 | 0.30212 | 0.009308 | 0.016823 | 0.017167 | 0.0277 | -0.007543 | -0.0086155 | 0.0096279 | 0.045776 | 0.16022 | -0.30212 | 0.13275 | 0.09613 | 0.26093 | 0.13275 | 0.37994 | 0.41657 | -0.054932 | 119.5953 | -0.14191 | 119.9432 | 120.0302 | -0.20599 | 119.8425 | 0.11444 | 0.3479 | 120.0302 | 120.2774 | 119.9936 | 120.0577 | 119.9432 | 120.314 | 120.1584 | 119.8425 | 120.0577 | 119.9432 | 120.1584 | 119.9936 | 120.314 | -0.60425 | -0.35706
1437.6875 | 120.3049 | -119.9158 | 0.31586 | 0.0016785 | 0.014687 | 0.011826 | 0.027487 | -0.006475 | -0.0075473 | 0.010269 | -0.004578 | 0.18768 | -0.28381 | 0.10071 | 0.064087 | 0.24719 | 0.14648 | 0.35706 | 0.37994 | -0.059509 | 119.632 | -0.12817 | 119.9112 | 120.0165 | -0.25177 | 119.8563 | 0.064087 | 0.27923 | 120.0623 | 120.2728 | 119.9799 | 120.1035 | 119.9112 | 120.2957 | 120.163 | 119.8563 | 120.1035 | 119.9112 | 120.163 | 119.9799 | 120.2957 | -0.59967 | -0.37537
1439.4375 | 120.4239 | -119.9112 | 0.29297 | -0.005951 | 0.014687 | 0.010331 | 0.019369 | -0.0073294 | -0.0043429 | 0.01091 | 0.045776 | 0.14648 | -0.24261 | 0.13275 | 0.13275 | 0.32959 | 0.054932 | 0.44403 | 0.37994 | -0.045776 | 119.6686 | -0.14648 | 119.957 | 120.0439 | -0.16022 | 119.8654 | 0.086975 | 0.28839 | 119.9661 | 120.3552 | 120.0439 | 120.0577 | 119.957 | 120.2911 | 120.2408 | 119.8654 | 120.0577 | 119.957 | 120.2408 | 120.0439 | 120.2911 | -0.53558 | -0.33874
1441.1094 | 120.4285 | -119.957 | 0.31128 | 0.0016785 | 0.013191 | 0.010117 | 0.024069 | -0.009252 | -0.0030613 | 0.010055 | 0.10071 | 0.14648 | -0.23346 | 0.23346 | 0.23346 | 0.41199 | 0.004578 | 0.52643 | 0.36621 | -0.032043 | 119.7235 | -0.16479 | 120.0577 | 120.1904 | -0.07782 | 119.9249 | 0.054932 | 0.33417 | 119.9615 | 120.4834 | 120.1904 | 120.1035 | 120.0577 | 120.3232 | 120.369 | 119.9249 | 120.1035 | 120.0577 | 120.369 | 120.1904 | 120.3232 | -0.54474 | -0.34332
1442.8594 | 120.4514 | -120.0348 | 0.33417 | -0.005951 | 0.015755 | 0.013535 | 0.029409 | -0.007543 | -0.0075473 | 0.0081325 | -0.009155 | 0.16937 | -0.29755 | 0.07782 | 0.064087 | 0.22888 | 0.16022 | 0.33875 | 0.41199 | -0.054932 | 119.7372 | -0.16479 | 120.0256 | 120.1126 | -0.27008 | 119.9799 | 0.07782 | 0.28839 | 120.195 | 120.3735 | 120.0989 | 120.2042 | 120.0256 | 120.4468 | 120.2637 | 119.9799 | 120.2042 | 120.0256 | 120.2637 | 120.0989 | 120.4468 | -0.63171 | -0.3891
1444.5469 | 120.5154 | -120.0485 | 0.30212 | 0.0016785 | 0.015755 | 0.0092627 | 0.021719 | -0.0086112 | -0.0066929 | 0.0083463 | 0.1236 | 0.1236 | -0.26093 | 0.21973 | 0.19684 | 0.40741 | 0.018311 | 0.54932 | 0.37079 | -0.027466 | 119.7876 | -0.17853 | 120.1721 | 120.2683 | -0.10529 | 120.0211 | 0.068665 | 0.38452 | 120.0668 | 120.5978 | 120.2454 | 120.1721 | 120.1721 | 120.4193 | 120.4559 | 120.0211 | 120.1721 | 120.1721 | 120.4559 | 120.2454 | 120.4193 | -0.56305 | -0.32959
1446.2969 | 120.5887 | -120.0623 | 0.29755 | -0.013581 | 0.014687 | 0.013321 | 0.021933 | -0.009893 | -0.0032749 | 0.0079189 | 0.036621 | 0.14191 | -0.24719 | 0.16479 | 0.15106 | 0.3479 | 0.036621 | 0.4715 | 0.37994 | -0.041199 | 119.8151 | -0.15564 | 120.0989 | 120.2271 | -0.14648 | 120.0211 | 0.082398 | 0.28381 | 120.0989 | 120.5338 | 120.2133 | 120.2042 | 120.0989 | 120.4422 | 120.4102 | 120.0211 | 120.2042 | 120.0989 | 120.4102 | 120.2133 | 120.4422 | -0.54474 | -0.33874
1447.9844 | 120.5154 | -120.1492 | 0.32044 | -0.005951 | 0.015327 | 0.012467 | 0.031118 | -0.0088248 | -0.0077609 | 0.010483 | 0.041199 | 0.15106 | -0.28839 | 0.16479 | 0.11902 | 0.27924 | 0.12817 | 0.42572 | 0.39825 | -0.032043 | 119.8608 | -0.16937 | 120.1904 | 120.314 | -0.20142 | 120.1172 | 0.077819 | 0.32959 | 120.2774 | 120.575 | 120.2682 | 120.3003 | 120.1904 | 120.5475 | 120.4285 | 120.1172 | 120.3003 | 120.1904 | 120.4285 | 120.2682 | 120.5475 | -0.60883 | -0.35248
1449.7344 | 120.6299 | -120.1538 | 0.32044 | -0.005951 | 0.017036 | 0.01204 | 0.023428 | -0.0083976 | -0.0062655 | 0.0092007 | 0.10071 | 0.13275 | -0.25177 | 0.21057 | 0.18768 | 0.37537 | 0.068665 | 0.52185 | 0.37079 | -0.032043 | 119.902 | -0.18768 | 120.2545 | 120.3644 | -0.13275 | 120.1218 | 0.050354 | 0.35248 | 120.2225 | 120.6757 | 120.3415 | 120.2866 | 120.2545 | 120.5246 | 120.5292 | 120.1218 | 120.2866 | 120.2545 | 120.5292 | 120.3415 | 120.5246 | -0.57221 | -0.35248
1451.4062 | 120.5658 | -120.2316 | 0.32501 | -0.005951 | 0.016182 | 0.013535 | 0.026419 | -0.0054068 | -0.0064791 | 0.0087735 | 0.050354 | 0.16937 | -0.27008 | 0.14648 | 0.09613 | 0.29297 | 0.1236 | 0.39825 | 0.41199 | -0.041199 | 119.9615 | -0.15564 | 120.282 | 120.3781 | -0.22888 | 120.1904 | 0.086975 | 0.32044 | 120.3552 | 120.6299 | 120.3278 | 120.401 | 120.282 | 120.6436 | 120.5246 | 120.1904 | 120.401 | 120.282 | 120.5246 | 120.3278 | 120.6436 | -0.59509 | -0.36621
1453.0938 | 120.7031 | -120.2179 | 0.27924 | -0.013581 | 0.017036 | 0.0084083 | 0.019583 | -0.008184 | -0.0077609 | 0.0096279 | 0.064087 | 0.15564 | -0.26093 | 0.1831 | 0.19226 | 0.37994 | 0.027466 | 0.51727 | 0.3891 | -0.041199 | 119.957 | -0.1236 | 120.282 | 120.401 | -0.086975 | 120.1767 | 0.10986 | 0.32501 | 120.2454 | 120.7352 | 120.4102 | 120.3735 | 120.282 | 120.607 | 120.5978 | 120.1767 | 120.3735 | 120.282 | 120.5978 | 120.4102 | 120.607 | -0.54016 | -0.32043
1454.8281 | 120.6207 | -120.2316 | 0.31586 | -0.005951 | 0.014687 | 0.012681 | 0.023428 | -0.008184 | -0.0069065 | 0.0092007 | 0.10986 | 0.12817 | -0.22888 | 0.20599 | 0.19684 | 0.39825 | -0.022888 | 0.49439 | 0.37079 | -0.009155 | 120.0027 | -0.18768 | 120.3415 | 120.4376 | -0.11902 | 120.2225 | 0.054932 | 0.33875 | 120.2087 | 120.726 | 120.4285 | 120.3598 | 120.3415 | 120.6024 | 120.6299 | 120.2225 | 120.3598 | 120.3415 | 120.6299 | 120.4285 | 120.6024 | -0.54474 | -0.32501
1456.5 | 120.7169 | -120.2637 | 0.3067 | -0.013581 | 0.016609 | 0.0084083 | 0.022787 | -0.010534 | -0.0062655 | 0.0068509 | 0.09613 | 0.13275 | -0.21515 | 0.2243 | 0.23804 | 0.41199 | 0.004578 | 0.54474 | 0.38452 | -0.018311 | 120.0485 | -0.17395 | 120.3598 | 120.488 | -0.068665 | 120.2454 | 0.077819 | 0.31128 | 120.2682 | 120.8084 | 120.5017 | 120.3964 | 120.3598 | 120.6482 | 120.6757 | 120.2454 | 120.3964 | 120.3598 | 120.6757 | 120.5017 | 120.6482 | -0.52185 | -0.32501
1458.25 | 120.6528 | -120.314 | 0.33875 | 0.0016785 | 0.013405 | 0.011612 | 0.027487 | -0.0088248 | -0.0060519 | 0.0081325 | 0.11444 | 0.13275 | -0.25177 | 0.21057 | 0.19684 | 0.3891 | -0.059509 | 0.49896 | 0.37079 | -0.009155 | 120.0623 | -0.20599 | 120.4285 | 120.5246 | -0.14191 | 120.3049 | 0.032044 | 0.36621 | 120.2545 | 120.813 | 120.5109 | 120.4468 | 120.4285 | 120.6848 | 120.7031 | 120.3049 | 120.4468 | 120.4285 | 120.7031 | 120.5109 | 120.6848 | -0.59052 | -0.3479
1459.9844 | 120.7031 | -120.369 | 0.31586 | -0.013581 | 0.013405 | 0.01204 | 0.026846 | -0.0060478 | -0.0058383 | 0.0092007 | 0.10071 | 0.12817 | -0.23346 | 0.21057 | 0.20599 | 0.3891 | -0.036621 | 0.50354 | 0.36621 | 0 | 120.1355 | -0.18768 | 120.4697 | 120.5795 | -0.10986 | 120.369 | 0.050354 | 0.33417 | 120.3323 | 120.8725 | 120.575 | 120.4971 | 120.4697 | 120.7352 | 120.7581 | 120.369 | 120.4971 | 120.4697 | 120.7581 | 120.575 | 120.7352 | -0.54932 | -0.31586
1461.6562 | 120.8588 | -120.3369 | 0.3067 | -0.013581 | 0.015755 | 0.012467 | 0.024496 | -0.0094656 | -0.0041293 | 0.010269 | 0.041199 | 0.14648 | -0.24719 | 0.15564 | 0.14648 | 0.3479 | 0.036621 | 0.45776 | 0.36621 | -0.022888 | 120.0897 | -0.16022 | 120.3781 | 120.4926 | -0.16022 | 120.314 | 0.059509 | 0.28839 | 120.3735 | 120.7947 | 120.4834 | 120.4834 | 120.3781 | 120.7031 | 120.6848 | 120.314 | 120.4834 | 120.3781 | 120.6848 | 120.4834 | 120.7031 | -0.55389 | -0.32959
1463.4062 | 120.813 | -120.3644 | 0.34332 | -0.005951 | 0.018105 | 0.0084083 | 0.027487 | -0.006475 | -0.0079745 | 0.0087735 | 0 | 0.17395 | -0.29297 | 0.07782 | 0.073242 | 0.25177 | 0.12817 | 0.33417 | 0.42114 | -0.059509 | 120.0714 | -0.16937 | 120.3644 | 120.4422 | -0.27008 | 120.3049 | 0.07782 | 0.29297 | 120.4926 | 120.6985 | 120.4376 | 120.5383 | 120.3644 | 120.7855 | 120.6161 | 120.3049 | 120.5383 | 120.3644 | 120.6161 | 120.4376 | 120.7855 | -0.63629 | -0.40283
1465.0938 | 120.8862 | -120.3873 | 0.28381 | 0.0016785 | 0.014473 | 0.010972 | 0.021078 | -0.0090384 | -0.0049839 | 0.0089871 | 0.059509 | 0.11902 | -0.24261 | 0.17395 | 0.18768 | 0.33417 | 0.091553 | 0.49439 | 0.37994 | -0.032043 | 120.1447 | -0.16479 | 120.4468 | 120.5612 | -0.09613 | 120.3552 | 0.096131 | 0.30212 | 120.4788 | 120.8817 | 120.575 | 120.5063 | 120.4468 | 120.7672 | 120.7214 | 120.3552 | 120.5063 | 120.4468 | 120.7214 | 120.575 | 120.7672 | -0.52643 | -0.31586
1466.8438 | 120.8176 | -120.4514 | 0.32501 | 0.0016785 | 0.014687 | 0.017594 | 0.028341 | -0.006475 | -0.0084017 | 0.0085599 | 0.036621 | 0.15106 | -0.27924 | 0.14191 | 0.10986 | 0.28839 | 0.1236 | 0.39368 | 0.39825 | -0.041199 | 120.1721 | -0.17395 | 120.488 | 120.5933 | -0.21515 | 120.4102 | 0.073242 | 0.31586 | 120.575 | 120.845 | 120.5612 | 120.6024 | 120.488 | 120.8496 | 120.7397 | 120.4102 | 120.6024 | 120.488 | 120.7397 | 120.5612 | 120.8496 | -0.60425 | -0.36621
1468.5781 | 120.8313 | -120.4651 | 0.32501 | -0.013581 | 0.014046 | 0.0086219 | 0.022574 | -0.0071158 | -0.0060519 | 0.0079189 | 0.086975 | 0.13733 | -0.22888 | 0.19684 | 0.19684 | 0.3891 | -0.050354 | 0.49896 | 0.37537 | 0 | 120.2362 | -0.18768 | 120.5521 | 120.6619 | -0.12817 | 120.4651 | 0.050354 | 0.31586 | 120.4147 | 120.9641 | 120.6619 | 120.6024 | 120.5521 | 120.8405 | 120.8542 | 120.4651 | 120.6024 | 120.5521 | 120.8542 | 120.6619 | 120.8405 | -0.55389 | -0.32501
1470.2656 | 120.9412 | -120.4559 | 0.32501 | -0.02121 | 0.013405 | 0.011612 | 0.024069 | -0.009252 | -0.0054111 | 0.0079189 | 0.10071 | 0.14191 | -0.24719 | 0.2243 | 0.24719 | 0.40741 | 0 | 0.54932 | 0.37537 | 0.004578 | 120.2087 | -0.18311 | 120.5566 | 120.6802 | -0.07782 | 120.4605 | 0.050354 | 0.3479 | 120.4559 | 121.0052 | 120.7031 | 120.5978 | 120.5566 | 120.8313 | 120.8633 | 120.4605 | 120.5978 | 120.5566 | 120.8633 | 120.7031 | 120.8313 | -0.5722 | -0.32043
1472 | 120.9915 | -120.4697 | 0.28839 | 0.009308 | 0.015541 | 0.011399 | 0.024283 | -0.0086112 | -0.0062655 | 0.0083463 | 0.032043 | 0.15106 | -0.23804 | 0.13733 | 0.17853 | 0.35248 | 0.036621 | 0.44403 | 0.40283 | -0.027466 | 120.2316 | -0.13733 | 120.5017 | 120.607 | -0.10986 | 120.4422 | 0.11444 | 0.27008 | 120.5063 | 120.9137 | 120.6482 | 120.6207 | 120.5017 | 120.8725 | 120.8221 | 120.4422 | 120.6207 | 120.5017 | 120.8221 | 120.6482 | 120.8725 | -0.52643 | -0.31586
1473.7344 | 121.0007 | -120.52 | 0.30212 | -0.005951 | 0.015114 | 0.0079809 | 0.024923 | -0.01032 | -0.0047703 | 0.010269 | 0.082397 | 0.13275 | -0.25177 | 0.20142 | 0.18768 | 0.33875 | 0.10529 | 0.49439 | 0.40283 | -0.022888 | 120.2683 | -0.16937 | 120.6024 | 120.7214 | -0.11444 | 120.4971 | 0.10071 | 0.33417 | 120.6253 | 121.0144 | 120.7077 | 120.6528 | 120.6024 | 120.9229 | 120.8588 | 120.4971 | 120.6528 | 120.6024 | 120.8588 | 120.7077 | 120.9229 | -0.55389 | -0.32501
1475.4844 | 121.019 | -120.5475 | 0.32044 | -0.013581 | 0.017036 | 0.0071265 | 0.024283 | -0.0088248 | -0.0037021 | 0.0083463 | 0.10986 | 0.14648 | -0.21973 | 0.21515 | 0.21515 | 0.36163 | 0.068665 | 0.54016 | 0.3891 | -0.013733 | 120.3278 | -0.17395 | 120.6573 | 120.7626 | -0.10529 | 120.5338 | 0.068664 | 0.32959 | 120.6161 | 121.0876 | 120.7626 | 120.694 | 120.6573 | 120.9366 | 120.9091 | 120.5338 | 120.694 | 120.6573 | 120.9091 | 120.7626 | 120.9366 | -0.54016 | -0.33417
1477.1562 | 120.9457 | -120.5658 | 0.3479 | -0.005951 | 0.014473 | 0.014603 | 0.029837 | -0.0077566 | -0.0056247 | 0.0066373 | 0.064087 | 0.1831 | -0.26093 | 0.16022 | 0.14648 | 0.31586 | 0.11902 | 0.45776 | 0.42114 | -0.027466 | 120.3049 | -0.16479 | 120.6299 | 120.726 | -0.20142 | 120.5383 | 0.073243 | 0.32501 | 120.6848 | 121.0236 | 120.7123 | 120.7489 | 120.6299 | 120.9869 | 120.8817 | 120.5383 | 120.7489 | 120.6299 | 120.8817 | 120.7123 | 120.9869 | -0.60882 | -0.37537
1478.9062 | 120.9686 | -120.6162 | 0.33875 | -0.005951 | 0.018959 | 0.014817 | 0.026632 | -0.0071158 | -0.0073337 | 0.0085599 | 0.009155 | 0.15564 | -0.29755 | 0.11902 | 0.13275 | 0.31586 | 0.059509 | 0.40283 | 0.40741 | -0.022888 | 120.3186 | -0.18311 | 120.6253 | 120.7352 | -0.20599 | 120.5933 | 0.068665 | 0.3067 | 120.6757 | 121.019 | 120.7489 | 120.7718 | 120.6253 | 121.0236 | 120.932 | 120.5933 | 120.7718 | 120.6253 | 120.932 | 120.7489 | 121.0236 | -0.63629 | -0.36163
1480.6719 | 120.9732 | -120.6345 | 0.33417 | -0.013581 | 0.015114 | 0.016099 | 0.029196 | -0.006475 | -0.0079745 | 0.0062099 | 0.059509 | 0.16479 | -0.27008 | 0.1831 | 0.16022 | 0.32501 | 0.09613 | 0.45776 | 0.42114 | -0.013733 | 120.3644 | -0.16937 | 120.694 | 120.8176 | -0.17395 | 120.6207 | 0.086976 | 0.32959 | 120.7306 | 121.0922 | 120.7947 | 120.7993 | 120.694 | 121.0556 | 120.9595 | 120.6207 | 120.7993 | 120.694 | 120.9595 | 120.7947 | 121.0556 | -0.60425 | -0.3479
1482.3438 | 121.019 | -120.639 | 0.33875 | -0.005951 | 0.015755 | 0.014603 | 0.026419 | -0.0066886 | -0.0071201 | 0.0079189 | 0.009155 | 0.15564 | -0.29755 | 0.11902 | 0.13733 | 0.31128 | 0.050354 | 0.42572 | 0.39368 | -0.022888 | 120.3415 | -0.18311 | 120.6482 | 120.7581 | -0.20142 | 120.6162 | 0.054932 | 0.3067 | 120.6894 | 121.0648 | 120.7764 | 120.7947 | 120.6482 | 121.0327 | 120.9503 | 120.6162 | 120.7947 | 120.6482 | 120.9503 | 120.7764 | 121.0327 | -0.63629 | -0.36163
1484.0156 | 121.1243 | -120.6024 | 0.29755 | -0.005951 | 0.015968 | 0.011399 | 0.021719 | -0.0094656 | -0.0037021 | 0.0079189 | 0.068665 | 0.10529 | -0.25635 | 0.21973 | 0.24719 | 0.40283 | 0.004578 | 0.56763 | 0.37994 | 0 | 120.3461 | -0.19226 | 120.6711 | 120.8221 | -0.050354 | 120.6024 | 0.082398 | 0.32501 | 120.607 | 121.17 | 120.8496 | 120.7077 | 120.6711 | 120.9824 | 121.0052 | 120.6024 | 120.7077 | 120.6711 | 121.0052 | 120.8496 | 120.9824 | -0.55389 | -0.29755
1485.7656 | 121.1746 | -120.6299 | 0.31128 | 0.009308 | 0.016609 | 0.010117 | 0.025137 | -0.009893 | -0.0047703 | 0.0070645 | 0.041199 | 0.15106 | -0.2655 | 0.1236 | 0.13733 | 0.28839 | 0.17853 | 0.44861 | 0.41657 | -0.032043 | 120.3644 | -0.16022 | 120.6711 | 120.7535 | -0.17395 | 120.5978 | 0.10529 | 0.3067 | 120.8084 | 121.0785 | 120.7672 | 120.7809 | 120.6711 | 121.0464 | 120.9183 | 120.5978 | 120.7809 | 120.6711 | 120.9183 | 120.7672 | 121.0464 | -0.57678 | -0.34332
1487.5 | 121.1746 | -120.6619 | 0.30212 | -0.013581 | 0.017036 | 0.012253 | 0.022146 | -0.011388 | -0.0034885 | 0.0074917 | 0.013733 | 0.13733 | -0.24261 | 0.12817 | 0.16479 | 0.3479 | 0.059509 | 0.4715 | 0.3891 | -0.009155 | 120.4193 | -0.16479 | 120.6757 | 120.7901 | -0.13733 | 120.6528 | 0.086975 | 0.25635 | 120.7214 | 121.1334 | 120.8267 | 120.7993 | 120.6757 | 121.051 | 121.0098 | 120.6528 | 120.7993 | 120.6757 | 121.0098 | 120.8267 | 121.051 | -0.54474 | -0.31128
1489.2344 | 121.0922 | -120.7214 | 0.34332 | -0.013581 | 0.016396 | 0.015671 | 0.028341 | -0.0088248 | -0.0075473 | 0.0081325 | 0.032043 | 0.16022 | -0.25635 | 0.1236 | 0.10529 | 0.2655 | 0.14648 | 0.39825 | 0.4303 | -0.050354 | 120.4651 | -0.18311 | 120.7535 | 120.845 | -0.23804 | 120.6711 | 0.086975 | 0.28839 | 120.8679 | 121.1197 | 120.8267 | 120.8817 | 120.7535 | 121.1517 | 120.9869 | 120.6711 | 120.8817 | 120.7535 | 120.9869 | 120.8267 | 121.1517 | -0.59967 | -0.39368
1490.9844 | 121.2021 | -120.6802 | 0.3067 | -0.005951 | 0.016182 | 0.010117 | 0.023001 | -0.009252 | -0.0054111 | 0.0074917 | 0.009155 | 0.10529 | -0.27466 | 0.12817 | 0.15106 | 0.35248 | 0.036621 | 0.45319 | 0.39825 | -0.009155 | 120.4056 | -0.20142 | 120.6894 | 120.8084 | -0.15564 | 120.6711 | 0.091552 | 0.28381 | 120.7169 | 121.1334 | 120.8313 | 120.7855 | 120.6894 | 121.0785 | 121.0327 | 120.6711 | 120.7855 | 120.6894 | 121.0327 | 120.8313 | 121.0785 | -0.58136 | -0.31586
1492.6562 | 121.2387 | -120.6985 | 0.29755 | -0.005951 | 0.016182 | 0.0088355 | 0.026419 | -0.011175 | -0.0077609 | 0.0081325 | -0.009155 | 0.19684 | -0.27924 | 0.09613 | 0.10071 | 0.27466 | 0.19684 | 0.38452 | 0.42572 | -0.050354 | 120.4193 | -0.10071 | 120.6894 | 120.7947 | -0.19684 | 120.6482 | 0.12817 | 0.27008 | 120.8954 | 121.0831 | 120.7993 | 120.8954 | 120.6894 | 121.1243 | 120.9732 | 120.6482 | 120.8954 | 120.6894 | 120.9732 | 120.7993 | 121.1243 | -0.57678 | -0.3479
1494.3906 | 121.2204 | -120.7306 | 0.32959 | 0.0016785 | 0.013405 | 0.012253 | 0.024496 | -0.012243 | -0.0037021 | 0.0094143 | 0.09613 | 0.13275 | -0.23804 | 0.21057 | 0.21515 | 0.38452 | 0.041199 | 0.55389 | 0.37994 | -0.013733 | 120.4926 | -0.19684 | 120.8267 | 120.9412 | -0.11444 | 120.7169 | 0.050354 | 0.33417 | 120.7718 | 121.2845 | 120.9457 | 120.8633 | 120.8267 | 121.1105 | 121.1151 | 120.7169 | 120.8633 | 120.8267 | 121.1151 | 120.9457 | 121.1105 | -0.56763 | -0.34332
1496.125 | 121.2158 | -120.7764 | 0.31128 | 0.0016785 | 0.018318 | 0.011826 | 0.029409 | -0.0079704 | -0.0064791 | 0.0087735 | 0.041199 | 0.1831 | -0.25635 | 0.14648 | 0.086975 | 0.28839 | 0.14191 | 0.4303 | 0.40283 | -0.041199 | 120.52 | -0.12817 | 120.8176 | 120.9229 | -0.2243 | 120.7352 | 0.091553 | 0.29755 | 120.9183 | 121.2067 | 120.8633 | 120.9595 | 120.8176 | 121.1792 | 121.0648 | 120.7352 | 120.9595 | 120.8176 | 121.0648 | 120.8633 | 121.1792 | -0.56763 | -0.35248
1497.7969 | 121.2799 | -120.7718 | 0.27924 | -0.005951 | 0.015114 | 0.012253 | 0.023642 | -0.010107 | -0.0056247 | 0.0096279 | 0.027466 | 0.11902 | -0.24719 | 0.16937 | 0.09613 | 0.3479 | 0.018311 | 0.46692 | 0.36163 | -0.027466 | 120.5246 | -0.16022 | 120.7993 | 120.9412 | -0.18311 | 120.7443 | 0.082397 | 0.27466 | 120.7901 | 121.2387 | 120.8679 | 120.8908 | 120.7993 | 121.1334 | 121.1197 | 120.7443 | 120.8908 | 120.7993 | 121.1197 | 120.8679 | 121.1334 | -0.52643 | -0.3067
1499.5312 | 121.3074 | -120.8084 | 0.2655 | -0.005951 | 0.014473 | 0.010331 | 0.023001 | -0.010107 | -0.0056247 | 0.0074917 | 0.009155 | 0.11444 | -0.27008 | 0.15106 | 0.064087 | 0.33875 | 0.036621 | 0.45776 | 0.36621 | -0.032043 | 120.5383 | -0.15106 | 120.8176 | 120.9595 | -0.20142 | 120.7764 | 0.10071 | 0.27924 | 120.845 | 121.2662 | 120.8725 | 120.9229 | 120.8176 | 121.1746 | 121.1472 | 120.7764 | 120.9229 | 120.8176 | 121.1472 | 120.8725 | 121.1746 | -0.53558 | -0.29755
1501.2188 | 121.2845 | -120.7993 | 0.28381 | 0.009308 | 0.013191 | 0.0099037 | 0.025778 | -0.0094656 | -0.0060519 | 0.0077053 | 0.036621 | 0.082397 | -0.27466 | 0.16479 | 0.068665 | 0.32501 | 0 | 0.44403 | 0.36621 | -0.013733 | 120.5246 | -0.20142 | 120.8359 | 120.9641 | -0.21515 | 120.7855 | 0.082398 | 0.31128 | 120.7993 | 121.2433 | 120.8679 | 120.8817 | 120.8359 | 121.1655 | 121.1243 | 120.7855 | 120.8817 | 120.8359 | 121.1243 | 120.8679 | 121.1655 | -0.55847 | -0.29755
1502.9531 | 121.2524 | -120.8725 | 0.28381 | 0.0016785 | 0.017464 | 0.010972 | 0.027487 | -0.0066886 | -0.0084017 | 0.0057827 | -0.018311 | 0.16479 | -0.30212 | 0.10986 | -0.018311 | 0.26093 | 0.10529 | 0.35706 | 0.41199 | -0.041199 | 120.5704 | -0.11902 | 120.8542 | 120.9824 | -0.30212 | 120.8313 | 0.12817 | 0.28381 | 120.9778 | 121.2296 | 120.8542 | 121.0373 | 120.8542 | 121.2845 | 121.1334 | 120.8313 | 121.0373 | 120.8542 | 121.1334 | 120.8542 | 121.2845 | -0.58594 | -0.32501
1504.625 | 121.2067 | -120.9091 | 0.29755 | -0.013581 | 0.015755 | 0.017594 | 0.026205 | -0.0056204 | -0.0069065 | 0.0074917 | 0.073242 | 0.12817 | -0.25635 | 0.20142 | 0.082397 | 0.37079 | -0.050354 | 0.47607 | 0.34332 | -0.018311 | 120.6528 | -0.16937 | 120.9824 | 121.1105 | -0.21515 | 120.8908 | 0.045777 | 0.32959 | 120.8588 | 121.3852 | 120.9915 | 121.0373 | 120.9824 | 121.2524 | 121.2799 | 120.8908 | 121.0373 | 120.9824 | 121.2799 | 120.9915 | 121.2524 | -0.55389 | -0.31586
1506.375 | 121.2341 | -120.8908 | 0.31586 | 0.0016785 | 0.018318 | 0.015244 | 0.030691 | -0.0079704 | -0.0066929 | 0.0055691 | 0.050354 | 0.16937 | -0.27008 | 0.15106 | 0.022888 | 0.28381 | 0.1236 | 0.39368 | 0.3891 | -0.041199 | 120.6207 | -0.14648 | 120.9412 | 121.0419 | -0.29297 | 120.8496 | 0.073242 | 0.32044 | 121.0144 | 121.2845 | 120.9137 | 121.0602 | 120.9412 | 121.2799 | 121.1746 | 120.8496 | 121.0602 | 120.9412 | 121.1746 | 120.9137 | 121.2799 | -0.58594 | -0.35706
1508.1094 | 121.2708 | -120.9274 | 0.27924 | -0.005951 | 0.013832 | 0.01439 | 0.024283 | -0.005834 | -0.0069065 | 0.0089871 | 0.064087 | 0.10529 | -0.2655 | 0.1831 | 0.13733 | 0.36163 | -0.17395 | 0.46234 | 0.33417 | -0.036621 | 120.6619 | -0.17395 | 120.9915 | 121.1105 | -0.14191 | 120.8908 | 0.054931 | 0.32959 | 120.7535 | 121.3898 | 121.0648 | 121.0327 | 120.9915 | 121.2616 | 121.2891 | 120.8908 | 121.0327 | 120.9915 | 121.2891 | 121.0648 | 121.2616 | -0.54474 | -0.31586
1509.8594 | 121.3531 | -120.9183 | 0.29297 | -0.005951 | 0.015114 | 0.011612 | 0.021719 | -0.010961 | -0.0051975 | 0.0094143 | 0.009155 | 0.10071 | -0.27466 | 0.15106 | 0.059509 | 0.31128 | -0.10529 | 0.41657 | 0.35248 | -0.041199 | 120.6436 | -0.19226 | 120.9274 | 121.0693 | -0.23346 | 120.8771 | 0.059509 | 0.28381 | 120.813 | 121.3348 | 120.9778 | 121.019 | 120.9274 | 121.2708 | 121.2296 | 120.8771 | 121.019 | 120.9274 | 121.2296 | 120.9778 | 121.2708 | -0.56763 | -0.33417
1511.5469 | 121.2891 | -120.9869 | 0.3067 | 0.0016785 | 0.016823 | 0.0096899 | 0.029196 | -0.0079704 | -0.0069065 | 0.0064237 | 0.073242 | 0.16937 | -0.25177 | 0.17395 | 0.045776 | 0.2655 | -0.032043 | 0.42114 | 0.37537 | -0.064087 | 120.7352 | -0.13733 | 121.0602 | 121.1609 | -0.26093 | 120.9229 | 0.068664 | 0.32501 | 120.9549 | 121.4081 | 121.0327 | 121.1563 | 121.0602 | 121.3623 | 121.2524 | 120.9229 | 121.1563 | 121.0602 | 121.2524 | 121.0327 | 121.3623 | -0.55847 | -0.37079
1513.2969 | 121.4218 | -120.9229 | 0.27008 | 0.0016785 | 0.011696 | 0.010972 | 0.022787 | -0.010107 | -0.0062655 | 0.0087735 | 0.009155 | 0.11902 | -0.25635 | 0.16479 | 0.073242 | 0.32959 | -0.10529 | 0.44403 | 0.35248 | -0.050354 | 120.6665 | -0.15106 | 120.932 | 121.0876 | -0.19684 | 120.8725 | 0.082397 | 0.2655 | 120.8176 | 121.3669 | 120.9961 | 121.0419 | 120.932 | 121.2753 | 121.2524 | 120.8725 | 121.0419 | 120.932 | 121.2524 | 120.9961 | 121.2753 | -0.52643 | -0.32044
1514.9688 | 121.4447 | -120.9503 | 0.25635 | -0.02121 | 0.014473 | 0.0086219 | 0.0277 | -0.010107 | -0.0056247 | 0.0085599 | 0.036621 | 0.16022 | -0.25177 | 0.1236 | 0.027466 | 0.25177 | 0.032043 | 0.40741 | 0.37537 | -0.064087 | 120.6985 | -0.096131 | 120.9869 | 121.0739 | -0.22888 | 120.8862 | 0.11902 | 0.28839 | 120.9824 | 121.3577 | 120.9778 | 121.1105 | 120.9869 | 121.3257 | 121.2021 | 120.8862 | 121.1105 | 120.9869 | 121.2021 | 120.9778 | 121.3257 | -0.50812 | -0.32044
1516.7188 | 121.3715 | -120.9778 | 0.27008 | -0.005951 | 0.01725 | 0.012894 | 0.028341 | -0.005834 | -0.0073337 | 0.0074917 | 0 | 0.14191 | -0.30212 | 0.14648 | 0.045776 | 0.27924 | -0.009155 | 0.41199 | 0.3891 | -0.064087 | 120.6757 | -0.12817 | 120.9778 | 121.1243 | -0.22431 | 120.9137 | 0.11902 | 0.30212 | 120.9686 | 121.3898 | 121.0236 | 121.1197 | 120.9778 | 121.3669 | 121.257 | 120.9137 | 121.1197 | 120.9778 | 121.257 | 121.0236 | 121.3669 | -0.57221 | -0.33417
1518.4531 | 121.4264 | -120.9686 | 0.28381 | 0.009308 | 0.01725 | 0.01738 | 0.024069 | -0.0083976 | -0.0069065 | 0.0070645 | 0.064087 | 0.10986 | -0.25635 | 0.21515 | 0.11902 | 0.35706 | -0.10986 | 0.52185 | 0.37079 | -0.054932 | 120.7123 | -0.17395 | 121.0327 | 121.1838 | -0.16479 | 120.9137 | 0.086976 | 0.32044 | 120.8588 | 121.4905 | 121.0876 | 121.0785 | 121.0327 | 121.3394 | 121.3257 | 120.9137 | 121.0785 | 121.0327 | 121.3257 | 121.0876 | 121.3394 | -0.54016 | -0.33874
1520.125 | 121.344 | -121.2158 | 0.14191 | 0.0016785 | 0.015541 | 0.010758 | 0.028982 | -0.0066886 | -0.0090427 | 0.0068509 | 0.032043 | 0.13275 | -0.29297 | 0.16937 | 0.050354 | 0.11902 | -0.041199 | 0.23804 | 0.21515 | -0.23346 | 120.9229 | -0.009156 | 121.2479 | 121.3852 | -0.091553 | 120.9824 | 0.073242 | 0.32501 | 121.1746 | 121.4539 | 121.2662 | 121.3486 | 121.2479 | 121.431 | 121.3348 | 120.9824 | 121.3486 | 121.2479 | 121.3348 | 121.2662 | 121.431 | -0.43488 | -0.37537
1521.875 | 121.4355 | -121.1563 | 0.10986 | -0.005951 | 0.014259 | 0.0094763 | 0.021933 | -0.0096794 | -0.0037021 | 0.0077053 | 0.054932 | 0.10529 | -0.27008 | 0.20599 | 0.1236 | 0.21515 | -0.1236 | 0.3479 | 0.17853 | -0.17853 | 120.8862 | -0.004577 | 121.2112 | 121.3623 | 0.013733 | 120.9778 | 0.068665 | 0.32501 | 121.0327 | 121.5042 | 121.2799 | 121.2616 | 121.2112 | 121.3348 | 121.3715 | 120.9778 | 121.2616 | 121.2112 | 121.3715 | 121.2799 | 121.3348 | -0.37994 | -0.28839
1523.625 | 121.3898 | -121.2296 | 0.14191 | -0.005951 | 0.014046 | 0.011612 | 0.02471 | -0.0079704 | -0.0032749 | 0.0081325 | 0.059509 | 0.10529 | -0.2655 | 0.20142 | 0.082397 | 0.19684 | -0.1831 | 0.29755 | 0.16937 | -0.20599 | 120.9641 | -0.036621 | 121.2891 | 121.431 | -0.05951 | 121.0236 | 0.027466 | 0.32501 | 121.0464 | 121.5271 | 121.3119 | 121.3348 | 121.2891 | 121.3989 | 121.4264 | 121.0236 | 121.3348 | 121.2891 | 121.4264 | 121.3119 | 121.3989 | -0.40741 | -0.3479
1525.375 | 121.4264 | -121.2158 | 0.13733 | 0.0016785 | 0.015114 | 0.013535 | 0.031332 | -0.0088248 | -0.0090427 | 0.0081325 | -0.013733 | 0.14648 | -0.29297 | 0.10986 | -0.013733 | 0.068665 | 0 | 0.19226 | 0.23346 | -0.20599 | 120.9229 | 0.009155 | 121.2021 | 121.3257 | -0.15106 | 121.0098 | 0.09613 | 0.27924 | 121.2158 | 121.4081 | 121.2021 | 121.3623 | 121.2021 | 121.4493 | 121.2845 | 121.0098 | 121.3623 | 121.2021 | 121.2845 | 121.2021 | 121.4493 | -0.4303 | -0.34332
1527.0469 | 121.4035 | -121.2479 | 0.13275 | -0.013581 | 0.015541 | 0.013321 | 0.02706 | -0.0069022 | -0.0075473 | 0.0068509 | 0.013733 | 0.11444 | -0.28839 | 0.13275 | 0.018311 | 0.073242 | -0.013733 | 0.21057 | 0.21057 | -0.23346 | 120.9595 | -0.01831 | 121.2616 | 121.3806 | -0.11444 | 121.0144 | 0.07782 | 0.30212 | 121.2341 | 121.4584 | 121.2662 | 121.3623 | 121.2616 | 121.4584 | 121.3211 | 121.0144 | 121.3623 | 121.2616 | 121.3211 | 121.2662 | 121.4584 | -0.42114 | -0.36621
1528.7969 | 121.4172 | -121.2387 | 0.14648 | 0.009308 | 0.015968 | 0.010331 | 0.027273 | -0.0056204 | -0.0062655 | 0.0087735 | 0.009155 | 0.12817 | -0.29297 | 0.12817 | 0.036621 | 0.09613 | -0.032043 | 0.2243 | 0.23804 | -0.23346 | 120.9457 | -0.01831 | 121.2479 | 121.3669 | -0.10986 | 121.0052 | 0.091553 | 0.30212 | 121.2067 | 121.463 | 121.2753 | 121.3669 | 121.2479 | 121.4767 | 121.3348 | 121.0052 | 121.3669 | 121.2479 | 121.3348 | 121.2753 | 121.4767 | -0.43945 | -0.37994
1530.5625 | 121.5042 | -121.2662 | 0.10071 | -0.005951 | 0.015755 | 0.010117 | 0.022146 | -0.0077566 | -0.0066929 | 0.0083463 | 0.073242 | 0.10986 | -0.24719 | 0.20599 | 0.12817 | 0.20142 | -0.10986 | 0.35706 | 0.17395 | -0.21057 | 121.019 | 0.009155 | 121.3394 | 121.4722 | 0.027466 | 121.0556 | 0.073242 | 0.32043 | 121.1563 | 121.6232 | 121.3943 | 121.376 | 121.3394 | 121.4401 | 121.4676 | 121.0556 | 121.376 | 121.3394 | 121.4676 | 121.3943 | 121.4401 | -0.3479 | -0.31128
1532.25 | 121.5042 | -121.2616 | 0.10071 | 0.0016785 | 0.014473 | 0.011185 | 0.027914 | -0.01032 | -0.0073337 | 0.0070645 | -0.013733 | 0.15564 | -0.27924 | 0.13275 | 0.036621 | 0.09613 | 0 | 0.23346 | 0.20599 | -0.2243 | 120.9824 | 0.054932 | 121.2479 | 121.3943 | -0.064087 | 121.0373 | 0.10529 | 0.2655 | 121.2616 | 121.4951 | 121.2982 | 121.4172 | 121.2479 | 121.4676 | 121.3577 | 121.0373 | 121.4172 | 121.2479 | 121.3577 | 121.2982 | 121.4676 | -0.37994 | -0.32501
1534 | 121.4447 | -121.2753 | 0.13733 | 0.0016785 | 0.017464 | 0.0099037 | 0.029196 | -0.0086112 | -0.0092563 | 0.0077053 | 0.013733 | 0.15106 | -0.27008 | 0.15106 | 0.059509 | 0.11902 | -0.041199 | 0.27008 | 0.21973 | -0.23346 | 121.0052 | 0.013733 | 121.2891 | 121.4264 | -0.07782 | 121.0419 | 0.082398 | 0.28381 | 121.2341 | 121.5454 | 121.3348 | 121.4264 | 121.2891 | 121.4951 | 121.3943 | 121.0419 | 121.4264 | 121.2891 | 121.3943 | 121.3348 | 121.4951 | -0.40741 | -0.37079
1535.6875 | 121.4584 | -121.2936 | 0.11444 | 0.0016785 | 0.0149 | 0.013321 | 0.0277 | -0.005834 | -0.0081881 | 0.0068509 | 0.018311 | 0.14191 | -0.30212 | 0.15106 | 0.045776 | 0.10986 | -0.027466 | 0.25635 | 0.19684 | -0.20599 | 120.9915 | 0.027466 | 121.312 | 121.4447 | -0.068665 | 121.0876 | 0.082397 | 0.32044 | 121.2662 | 121.55 | 121.3394 | 121.4355 | 121.312 | 121.4905 | 121.4035 | 121.0876 | 121.4355 | 121.312 | 121.4035 | 121.3394 | 121.4905 | -0.41657 | -0.32044
1537.4219 | 121.5363 | -121.2845 | 0.10529 | -0.005951 | 0.015755 | 0.0077673 | 0.020865 | -0.0094656 | -0.0073337 | 0.0064237 | 0.045776 | 0.09613 | -0.26093 | 0.18768 | 0.12817 | 0.21973 | -0.15106 | 0.35248 | 0.16479 | -0.20142 | 121.0236 | -0.009156 | 121.3303 | 121.4722 | 0.022888 | 121.0831 | 0.059509 | 0.3067 | 121.1334 | 121.637 | 121.4127 | 121.3806 | 121.3303 | 121.4493 | 121.5042 | 121.0831 | 121.3806 | 121.3303 | 121.5042 | 121.4127 | 121.4493 | -0.36621 | -0.3067
1539.1719 | 121.4539 | -121.3165 | 0.13275 | -0.005951 | 0.015968 | 0.01503 | 0.025991 | -0.009252 | -0.0051975 | 0.0077053 | 0.068665 | 0.10529 | -0.25177 | 0.19684 | 0.10986 | 0.21057 | -0.19226 | 0.3067 | 0.16022 | -0.19226 | 121.0648 | -0.027465 | 121.3852 | 121.5134 | -0.022888 | 121.1243 | 0.027466 | 0.32044 | 121.1243 | 121.6232 | 121.4264 | 121.4218 | 121.3852 | 121.4767 | 121.5271 | 121.1243 | 121.4218 | 121.3852 | 121.5271 | 121.4264 | 121.4767 | -0.38452 | -0.32501
1540.9375 | 121.5729 | -121.2708 | 0.082397 | -0.005951 | 0.015327 | 0.0094763 | 0.023214 | -0.010747 | -0.0034885 | 0.0083463 | 0.045776 | 0.10529 | -0.2655 | 0.20599 | 0.10071 | 0.19226 | -0.12817 | 0.34332 | 0.19226 | -0.20599 | 121.0052 | 0.022889 | 121.3165 | 121.4767 | 0.018311 | 121.0648 | 0.10986 | 0.31128 | 121.1426 | 121.6141 | 121.3715 | 121.376 | 121.3165 | 121.463 | 121.463 | 121.0648 | 121.376 | 121.3165 | 121.463 | 121.3715 | 121.463 | -0.3479 | -0.28839
1542.625 | 121.637 | -121.2845 | 0.10986 | 0.0016785 | 0.016609 | 0.010758 | 0.027487 | -0.009893 | -0.0054111 | 0.0064237 | -0.045776 | 0.14648 | -0.28381 | 0.09613 | 0 | 0.050354 | 0.073242 | 0.21057 | 0.21973 | -0.24261 | 121.0007 | 0.036621 | 121.2387 | 121.3806 | -0.10986 | 121.0419 | 0.10986 | 0.23804 | 121.3577 | 121.4951 | 121.2845 | 121.431 | 121.2387 | 121.5042 | 121.3348 | 121.0419 | 121.431 | 121.2387 | 121.3348 | 121.2845 | 121.5042 | -0.39368 | -0.35248
1544.375 | 121.6324 | -121.3028 | 0.086975 | 0.009308 | 0.014473 | 0.013535 | 0.023214 | -0.012029 | -0.0037021 | 0.0074917 | -0.009155 | 0.11444 | -0.25177 | 0.13733 | 0.050354 | 0.13275 | -0.09613 | 0.2655 | 0.17853 | -0.23346 | 121.051 | 0.027466 | 121.2936 | 121.4401 | -0.036621 | 121.0693 | 0.091553 | 0.24261 | 121.2067 | 121.5683 | 121.3531 | 121.4172 | 121.2936 | 121.4813 | 121.4355 | 121.0693 | 121.4172 | 121.2936 | 121.4355 | 121.3531 | 121.4813 | -0.33874 | -0.32043
1546.0469 | 121.6553 | -121.3074 | 0.09613 | -0.005951 | 0.014046 | 0.0039221 | 0.026205 | -0.010534 | -0.0047703 | 0.0070645 | -0.050354 | 0.16022 | -0.29755 | 0.10986 | -0.009155 | 0.054932 | 0.064087 | 0.20142 | 0.23346 | -0.25177 | 121.0098 | 0.064087 | 121.257 | 121.4172 | -0.10528 | 121.0556 | 0.13733 | 0.24719 | 121.3715 | 121.5088 | 121.2982 | 121.4676 | 121.257 | 121.5408 | 121.3623 | 121.0556 | 121.4676 | 121.257 | 121.3623 | 121.2982 | 121.5408 | -0.39368 | -0.3479
1547.7969 | 121.5271 | -121.3531 | 0.1236 | -0.005951 | 0.0149 | 0.011612 | 0.028555 | -0.0079704 | -0.0081881 | 0.0096279 | 0.018311 | 0.13275 | -0.28839 | 0.15106 | 0.036621 | 0.10986 | -0.009155 | 0.25635 | 0.21973 | -0.22888 | 121.0648 | 0.009155 | 121.3715 | 121.5042 | -0.086975 | 121.1243 | 0.096131 | 0.3067 | 121.344 | 121.6095 | 121.3898 | 121.4859 | 121.3715 | 121.5729 | 121.463 | 121.1243 | 121.4859 | 121.3715 | 121.463 | 121.3898 | 121.5729 | -0.41199 | -0.35248
1549.5312 | 121.6278 | -121.3486 | 0.11444 | 0.0016785 | 0.014259 | 0.011612 | 0.024283 | -0.010534 | -0.0045565 | 0.0083463 | 0.059509 | 0.10071 | -0.24261 | 0.20142 | 0.1236 | 0.19226 | -0.12817 | 0.35248 | 0.19226 | -0.19226 | 121.106 | -0.013733 | 121.4081 | 121.55 | 0.009155 | 121.1563 | 0.07782 | 0.30212 | 121.2204 | 121.7011 | 121.4722 | 121.4493 | 121.4081 | 121.5408 | 121.5408 | 121.1563 | 121.4493 | 121.4081 | 121.5408 | 121.4722 | 121.5408 | -0.35706 | -0.3067
1551.2656 | 121.6141 | -121.3669 | 0.11444 | -0.005951 | 0.015541 | 0.012681 | 0.028769 | -0.007543 | -0.0056247 | 0.0064237 | -0.009155 | 0.14648 | -0.27466 | 0.13733 | 0.032043 | 0.10071 | -0.009155 | 0.24719 | 0.21057 | -0.22888 | 121.0922 | 0.032043 | 121.3577 | 121.5042 | -0.082398 | 121.138 | 0.09613 | 0.2655 | 121.3577 | 121.6141 | 121.3989 | 121.5134 | 121.3577 | 121.5775 | 121.4676 | 121.138 | 121.5134 | 121.3577 | 121.4676 | 121.3989 | 121.5775 | -0.3891 | -0.34332
1552.9375 | 121.5408 | -121.4127 | 0.14191 | -0.013581 | 0.017891 | 0.010544 | 0.026846 | -0.0066886 | -0.0064791 | 0.0081325 | 0.07782 | 0.10071 | -0.24719 | 0.20142 | 0.10071 | 0.20142 | -0.1831 | 0.31128 | 0.1831 | -0.16479 | 121.1655 | -0.041199 | 121.4905 | 121.6141 | -0.041199 | 121.2479 | 0.041198 | 0.32501 | 121.2296 | 121.7239 | 121.5134 | 121.5134 | 121.4905 | 121.5958 | 121.6141 | 121.2479 | 121.5134 | 121.4905 | 121.6141 | 121.5134 | 121.5958 | -0.3891 | -0.3067
1554.6719 | 121.5729 | -121.3943 | 0.14191 | 0.0016785 | 0.015327 | 0.011612 | 0.026419 | -0.006475 | -0.0090427 | 0.0077053 | 0.059509 | 0.1236 | -0.27008 | 0.20599 | 0.10986 | 0.19226 | -0.17395 | 0.29755 | 0.1831 | -0.19226 | 121.1243 | -0.018311 | 121.4539 | 121.6003 | -0.032044 | 121.2021 | 0.041198 | 0.32959 | 121.2204 | 121.6919 | 121.5042 | 121.5179 | 121.4539 | 121.5775 | 121.5866 | 121.2021 | 121.5179 | 121.4539 | 121.5866 | 121.5042 | 121.5775 | -0.41199 | -0.33417
1556.4219 | 121.6644 | -121.3943 | 0.09613 | 0.0016785 | 0.016182 | 0.0099037 | 0.023001 | -0.0077566 | -0.0051975 | 0.0077053 | 0.059509 | 0.11444 | -0.24261 | 0.21515 | 0.11444 | 0.20142 | -0.14648 | 0.34332 | 0.18768 | -0.21515 | 121.1517 | 0.018311 | 121.4539 | 121.6095 | 0.018311 | 121.1792 | 0.091553 | 0.30212 | 121.2479 | 121.7377 | 121.5088 | 121.5088 | 121.4539 | 121.582 | 121.5958 | 121.1792 | 121.5088 | 121.4539 | 121.5958 | 121.5088 | 121.582 | -0.33874 | -0.31128
1558.1719 | 121.582 | -121.4355 | 0.13275 | 0.0016785 | 0.014687 | 0.013108 | 0.031118 | -0.0079704 | -0.0075473 | 0.0081325 | 0.032043 | 0.15106 | -0.27924 | 0.16022 | 0.041199 | 0.11902 | -0.045776 | 0.25635 | 0.19684 | -0.2243 | 121.1563 | 0.018311 | 121.4676 | 121.5958 | -0.091552 | 121.2112 | 0.064087 | 0.31128 | 121.3898 | 121.6919 | 121.4767 | 121.5866 | 121.4676 | 121.6324 | 121.5546 | 121.2112 | 121.5866 | 121.4676 | 121.5546 | 121.4767 | 121.6324 | -0.41199 | -0.35706
1559.9062 | 121.6461 | -121.4264 | 0.12817 | 0.009308 | 0.01725 | 0.012253 | 0.029196 | -0.0062614 | -0.0058383 | 0.0083463 | -0.013733 | 0.16022 | -0.30212 | 0.10529 | -0.022888 | 0.059509 | 0 | 0.16479 | 0.21515 | -0.21515 | 121.1243 | 0.032043 | 121.4127 | 121.5317 | -0.15106 | 121.2112 | 0.086975 | 0.28839 | 121.4264 | 121.5912 | 121.4035 | 121.5866 | 121.4127 | 121.6415 | 121.4859 | 121.2112 | 121.5866 | 121.4127 | 121.4859 | 121.4035 | 121.6415 | -0.4303 | -0.34332
1561.5781 | 121.6965 | -121.4081 | 0.11444 | 0.0016785 | 0.014259 | 0.011185 | 0.019796 | -0.01032 | -0.0030613 | 0.0064237 | 0.073242 | 0.12817 | -0.23346 | 0.20142 | 0.10986 | 0.16479 | -0.073242 | 0.33417 | 0.18768 | -0.21057 | 121.1746 | 0.013733 | 121.4813 | 121.6095 | -0.004578 | 121.1975 | 0.073242 | 0.3067 | 121.3348 | 121.7422 | 121.5179 | 121.5363 | 121.4813 | 121.5958 | 121.5729 | 121.1975 | 121.5363 | 121.4813 | 121.5729 | 121.5179 | 121.5958 | -0.3479 | -0.32501
1563.3438 | 121.6095 | -121.4493 | 0.15106 | -0.013581 | 0.015327 | 0.012894 | 0.026632 | -0.007543 | -0.0088291 | 0.0092007 | 0.027466 | 0.14191 | -0.28839 | 0.17853 | 0.059509 | 0.11902 | -0.036621 | 0.26093 | 0.20599 | -0.2243 | 121.1609 | -0.009155 | 121.4767 | 121.6278 | -0.091553 | 121.225 | 0.054932 | 0.31586 | 121.4127 | 121.7102 | 121.5088 | 121.5912 | 121.4767 | 121.6553 | 121.5683 | 121.225 | 121.5912 | 121.4767 | 121.5683 | 121.5088 | 121.6553 | -0.43945 | -0.37537
1565.0312 | 121.6141 | -121.4676 | 0.12817 | -0.013581 | 0.018318 | 0.01204 | 0.025778 | -0.007543 | -0.0049839 | 0.0087735 | 0.091553 | 0.10529 | -0.23804 | 0.19226 | 0.11902 | 0.21057 | -0.1831 | 0.30212 | 0.17395 | -0.17853 | 121.2296 | -0.022888 | 121.5591 | 121.6599 | -0.009155 | 121.2891 | 0.045776 | 0.32959 | 121.2845 | 121.7697 | 121.5866 | 121.5729 | 121.5591 | 121.6415 | 121.6782 | 121.2891 | 121.5729 | 121.5591 | 121.6782 | 121.5866 | 121.6415 | -0.36621 | -0.3067
1566.7812 | 121.7056 | -121.4447 | 0.11902 | 0.0016785 | 0.015541 | 0.010117 | 0.025991 | -0.0066886 | -0.0056247 | 0.0070645 | -0.004578 | 0.16022 | -0.28839 | 0.12817 | 0.036621 | 0.09613 | 0.018311 | 0.24261 | 0.21515 | -0.21973 | 121.1563 | 0.041198 | 121.4401 | 121.5729 | -0.082398 | 121.225 | 0.09613 | 0.28381 | 121.463 | 121.6873 | 121.4813 | 121.6049 | 121.4401 | 121.6599 | 121.5408 | 121.225 | 121.6049 | 121.4401 | 121.5408 | 121.4813 | 121.6599 | -0.40741 | -0.33875
1568.5156 | 121.6736 | -121.4676 | 0.13275 | -0.005951 | 0.016182 | 0.011612 | 0.02706 | -0.004766 | -0.0086155 | 0.0098415 | -0.036621 | 0.17853 | -0.28381 | 0.082397 | -0.013733 | 0.050354 | 0 | 0.16022 | 0.23804 | -0.24261 | 121.1838 | 0.045777 | 121.431 | 121.55 | -0.14648 | 121.225 | 0.10529 | 0.24719 | 121.4676 | 121.6278 | 121.4539 | 121.6461 | 121.431 | 121.7056 | 121.5179 | 121.225 | 121.6461 | 121.431 | 121.5179 | 121.4539 | 121.7056 | -0.41656 | -0.37537
1570.25 | 121.7194 | -121.4676 | 0.10071 | -0.013581 | 0.013405 | 0.0099037 | 0.021505 | -0.0086112 | -0.0056247 | 0.0070645 | 0.07782 | 0.10986 | -0.21973 | 0.2243 | 0.12817 | 0.20599 | -0.14648 | 0.35248 | 0.17395 | -0.20599 | 121.2479 | 0.009155 | 121.5454 | 121.6919 | 0.027466 | 121.2616 | 0.073242 | 0.29755 | 121.3211 | 121.8201 | 121.5958 | 121.5775 | 121.5454 | 121.6415 | 121.6736 | 121.2616 | 121.5775 | 121.5454 | 121.6736 | 121.5958 | 121.6415 | -0.32044 | -0.3067
1571.9375 | 121.6599 | -121.4767 | 0.11444 | 0.0016785 | 0.015755 | 0.016953 | 0.027273 | -0.0077566 | -0.0086155 | 0.0068509 | 0.013733 | 0.15564 | -0.2655 | 0.1236 | 0.022888 | 0.11444 | -0.10071 | 0.2243 | 0.18768 | -0.19684 | 121.2112 | 0.041199 | 121.4905 | 121.6003 | -0.091553 | 121.2799 | 0.073242 | 0.27924 | 121.376 | 121.7011 | 121.4996 | 121.6324 | 121.4905 | 121.6644 | 121.5912 | 121.2799 | 121.6324 | 121.4905 | 121.5912 | 121.4996 | 121.6644 | -0.37994 | -0.31128
1573.6719 | 121.788 | -121.4813 | 0.13733 | -0.005951 | 0.016609 | 0.01204 | 0.025351 | -0.006475 | -0.0081881 | 0.0066373 | -0.013733 | 0.15106 | -0.27008 | 0.10529 | -0.009155 | 0.091553 | -0.07782 | 0.21057 | 0.21515 | -0.23346 | 121.2112 | 0.013733 | 121.4676 | 121.5866 | -0.14648 | 121.2479 | 0.07782 | 0.25635 | 121.4035 | 121.6919 | 121.4722 | 121.6324 | 121.4676 | 121.6965 | 121.5729 | 121.2479 | 121.6324 | 121.4676 | 121.5729 | 121.4722 | 121.6965 | -0.40741 | -0.37079
1575.4062 | 121.7972 | -121.4447 | 0.086975 | -0.013581 | 0.016182 | 0.011826 | 0.02236 | -0.009893 | -0.0060519 | 0.0085599 | 0.027466 | 0.1236 | -0.24261 | 0.14648 | 0.064087 | 0.14648 | -0.09613 | 0.2655 | 0.20142 | -0.20599 | 121.2021 | 0.036621 | 121.4722 | 121.5912 | -0.022888 | 121.2387 | 0.11444 | 0.27008 | 121.3486 | 121.7102 | 121.5088 | 121.5683 | 121.4722 | 121.6461 | 121.5912 | 121.2387 | 121.5683 | 121.4722 | 121.5912 | 121.5088 | 121.6461 | -0.32959 | -0.29297
1577.0938 | 121.7331 | -121.4996 | 0.11902 | -0.005951 | 0.017677 | 0.013749 | 0.030478 | -0.0049796 | -0.0084017 | 0.0087735 | -0.009155 | 0.16937 | -0.27466 | 0.086975 | -0.027466 | 0.050354 | -0.009155 | 0.15564 | 0.2243 | -0.23804 | 121.225 | 0.050354 | 121.4905 | 121.5866 | -0.14649 | 121.2616 | 0.10529 | 0.2655 | 121.4905 | 121.6553 | 121.4722 | 121.669 | 121.4905 | 121.7239 | 121.55 | 121.2616 | 121.669 | 121.4905 | 121.55 | 121.4722 | 121.7239 | -0.39368 | -0.35706
1578.8438 | 121.6919 | -121.5179 | 0.11444 | -0.02121 | 0.015541 | 0.012253 | 0.026846 | -0.0045524 | -0.0056247 | 0.0083463 | -0.013733 | 0.14191 | -0.2655 | 0.09613 | 0 | 0.082397 | -0.045776 | 0.1831 | 0.20599 | -0.21973 | 121.2524 | 0.027466 | 121.5042 | 121.6141 | -0.11444 | 121.2982 | 0.091553 | 0.25177 | 121.4722 | 121.701 | 121.5179 | 121.6599 | 121.5042 | 121.7239 | 121.6003 | 121.2982 | 121.6599 | 121.5042 | 121.6003 | 121.5179 | 121.7239 | -0.37994 | -0.33417
1580.5938 | 121.7331 | -121.5271 | 0.11902 | -0.005951 | 0.0149 | 0.010544 | 0.025351 | -0.0094656 | -0.0058383 | 0.0087735 | -0.009155 | 0.16022 | -0.26093 | 0.10071 | 0.004578 | 0.082397 | -0.041199 | 0.17853 | 0.21515 | -0.23346 | 121.2662 | 0.041198 | 121.5179 | 121.6278 | -0.11444 | 121.2936 | 0.09613 | 0.25177 | 121.4859 | 121.7056 | 121.5317 | 121.6873 | 121.5179 | 121.7422 | 121.6095 | 121.2936 | 121.6873 | 121.5179 | 121.6095 | 121.5317 | 121.7422 | -0.37994 | -0.35248
1582.3438 | 121.7926 | -121.5134 | 0.11444 | 0.009308 | 0.014473 | 0.010972 | 0.021933 | -0.0094656 | -0.0071201 | 0.0072781 | 0.022888 | 0.12817 | -0.21515 | 0.14648 | 0.068665 | 0.16479 | -0.10986 | 0.27008 | 0.18768 | -0.2243 | 121.2982 | 0.013733 | 121.5363 | 121.6599 | -0.045776 | 121.2891 | 0.073242 | 0.23804 | 121.4035 | 121.7834 | 121.582 | 121.6415 | 121.5363 | 121.7011 | 121.6782 | 121.2891 | 121.6415 | 121.5363 | 121.6782 | 121.582 | 121.7011 | -0.32959 | -0.33875
1584.0938 | 121.7834 | -121.4996 | 0.10529 | -0.005951 | 0.015114 | 0.012894 | 0.023214 | -0.011602 | -0.0045565 | 0.0072781 | 0.09613 | 0.12817 | -0.23346 | 0.21973 | 0.12817 | 0.19684 | -0.12817 | 0.36621 | 0.19226 | -0.19226 | 121.2662 | 0.022888 | 121.5958 | 121.7194 | 0.022888 | 121.3074 | 0.086975 | 0.32959 | 121.3715 | 121.8658 | 121.6278 | 121.6278 | 121.5958 | 121.6919 | 121.6965 | 121.3074 | 121.6278 | 121.5958 | 121.6965 | 121.6278 | 121.6919 | -0.33875 | -0.29755
1585.8594 | 121.7239 | -121.5546 | 0.13275 | 0.0016785 | 0.015755 | 0.013962 | 0.030691 | -0.0086112 | -0.0081881 | 0.0081325 | 0.054932 | 0.15106 | -0.27924 | 0.16479 | 0.027466 | 0.10529 | -0.032043 | 0.25177 | 0.21057 | -0.21973 | 121.2753 | 0.018311 | 121.6095 | 121.7194 | -0.10529 | 121.3348 | 0.07782 | 0.33417 | 121.5225 | 121.8063 | 121.582 | 121.7056 | 121.6095 | 121.7651 | 121.6599 | 121.3348 | 121.7056 | 121.6095 | 121.6599 | 121.582 | 121.7651 | -0.41199 | -0.35248
1587.5469 | 121.7514 | -121.5363 | 0.11444 | 0.0016785 | 0.015755 | 0.016099 | 0.023642 | -0.0096794 | -0.0047703 | 0.0089871 | 0.086975 | 0.13733 | -0.21973 | 0.1831 | 0.086975 | 0.17395 | -0.16022 | 0.28381 | 0.17853 | -0.19684 | 121.3165 | 0.022888 | 121.6232 | 121.7194 | -0.027466 | 121.3394 | 0.064087 | 0.3067 | 121.376 | 121.8201 | 121.6232 | 121.6736 | 121.6232 | 121.7148 | 121.7102 | 121.3394 | 121.6736 | 121.6232 | 121.7102 | 121.6232 | 121.7148 | -0.33417 | -0.31128
1589.2969 | 121.8155 | -121.5271 | 0.10529 | -0.005951 | 0.014687 | 0.010758 | 0.023428 | -0.010747 | -0.0066929 | 0.0053555 | 0.036621 | 0.13275 | -0.23804 | 0.17853 | 0.082397 | 0.17853 | -0.10529 | 0.32044 | 0.1831 | -0.21515 | 121.2891 | 0.027465 | 121.5637 | 121.7056 | -0.022889 | 121.312 | 0.077819 | 0.27466 | 121.4218 | 121.8475 | 121.6095 | 121.6599 | 121.5637 | 121.7102 | 121.7056 | 121.312 | 121.6599 | 121.5637 | 121.7056 | 121.6095 | 121.7102 | -0.34332 | -0.32044
1591.0469 | 121.8246 | -121.5363 | 0.13275 | -0.005951 | 0.013405 | 0.0066993 | 0.025137 | -0.010961 | -0.0034885 | 0.0072781 | 0.073242 | 0.1236 | -0.23346 | 0.22888 | 0.12817 | 0.20599 | -0.15106 | 0.3479 | 0.17853 | -0.20599 | 121.3028 | -0.009155 | 121.6095 | 121.7651 | -0.004577 | 121.3303 | 0.045777 | 0.3067 | 121.3852 | 121.8842 | 121.6644 | 121.6599 | 121.6095 | 121.7148 | 121.7422 | 121.3303 | 121.6599 | 121.6095 | 121.7422 | 121.6644 | 121.7148 | -0.36621 | -0.33875
1592.7344 | 121.7148 | -121.5683 | 0.13733 | 0.0016785 | 0.014473 | 0.012894 | 0.02706 | -0.0077566 | -0.0081881 | 0.0051419 | 0.10071 | 0.1236 | -0.22888 | 0.21057 | 0.10071 | 0.19684 | -0.20142 | 0.31128 | 0.16937 | -0.18768 | 121.3394 | -0.013733 | 121.669 | 121.7789 | -0.036621 | 121.3806 | 0.032044 | 0.32959 | 121.3669 | 121.8796 | 121.669 | 121.6919 | 121.669 | 121.7377 | 121.7651 | 121.3806 | 121.6919 | 121.669 | 121.7651 | 121.669 | 121.7377 | -0.36621 | -0.32501
1594.4688 | 121.8521 | -121.5317 | 0.10529 | -0.005951 | 0.015114 | 0.01204 | 0.022146 | -0.010961 | -0.0062655 | 0.0066373 | 0.027466 | 0.13275 | -0.23346 | 0.16479 | 0.059509 | 0.14191 | -0.11444 | 0.27008 | 0.19226 | -0.19684 | 121.2982 | 0.027465 | 121.5591 | 121.6965 | -0.045777 | 121.3348 | 0.086975 | 0.26093 | 121.4172 | 121.8018 | 121.5912 | 121.6644 | 121.5591 | 121.7239 | 121.6736 | 121.3348 | 121.6644 | 121.5591 | 121.6736 | 121.5912 | 121.7239 | -0.33875 | -0.30212
1596.2344 | 121.843 | -121.5317 | 0.10071 | -0.005951 | 0.013405 | 0.011399 | 0.023214 | -0.0088248 | -0.0071201 | 0.0083463 | 0.068665 | 0.11902 | -0.23346 | 0.2243 | 0.10986 | 0.18768 | -0.1236 | 0.32501 | 0.18768 | -0.19684 | 121.2982 | 0.018311 | 121.6003 | 121.756 | 0.009155 | 121.3348 | 0.086975 | 0.30212 | 121.4081 | 121.8567 | 121.6415 | 121.6507 | 121.6003 | 121.7194 | 121.7194 | 121.3348 | 121.6507 | 121.6003 | 121.7194 | 121.6415 | 121.7194 | -0.33417 | -0.29755
1597.9375 | 121.8338 | -121.5775 | 0.13275 | -0.005951 | 0.0149 | 0.0073401 | 0.027914 | -0.0079704 | -0.0090427 | 0.0070645 | 0.013733 | 0.14648 | -0.29297 | 0.16937 | 0.013733 | 0.086975 | -0.009155 | 0.23804 | 0.20599 | -0.22888 | 121.2845 | 0.013733 | 121.5912 | 121.7468 | -0.11902 | 121.3486 | 0.073243 | 0.3067 | 121.5683 | 121.8155 | 121.5912 | 121.7239 | 121.5912 | 121.7834 | 121.6644 | 121.3486 | 121.7239 | 121.5912 | 121.6644 | 121.5912 | 121.7834 | -0.42572 | -0.36163
1599.6875 | 121.7651 | -121.6278 | 0.12817 | -0.005951 | 0.017036 | 0.014176 | 0.029409 | -0.005834 | -0.0090427 | 0.0066373 | 0.073242 | 0.15564 | -0.2655 | 0.17395 | 0.036621 | 0.10529 | -0.027466 | 0.23804 | 0.20142 | -0.21515 | 121.3623 | 0.027466 | 121.701 | 121.8018 | -0.091553 | 121.4127 | 0.073242 | 0.33874 | 121.6003 | 121.8658 | 121.6644 | 121.7834 | 121.701 | 121.8292 | 121.7331 | 121.4127 | 121.7834 | 121.701 | 121.7331 | 121.6644 | 121.8292 | -0.39368 | -0.34332
1601.375 | 121.8887 | -121.5729 | 0.10071 | -0.005951 | 0.014473 | 0.0092627 | 0.023214 | -0.007543 | -0.0084017 | 0.0057827 | 0.050354 | 0.13733 | -0.23804 | 0.16479 | 0.073242 | 0.13275 | -0.036621 | 0.27466 | 0.21973 | -0.20599 | 121.3348 | 0.036621 | 121.6232 | 121.7377 | -0.027466 | 121.3669 | 0.11902 | 0.28839 | 121.5363 | 121.8475 | 121.6461 | 121.7102 | 121.6232 | 121.7926 | 121.7056 | 121.3669 | 121.7102 | 121.6232 | 121.7056 | 121.6461 | 121.7926 | -0.33875 | -0.3067
1603.1094 | 121.9116 | -121.5775 | 0.10071 | 0.009308 | 0.015541 | 0.011612 | 0.025564 | -0.0096794 | -0.0034885 | 0.0079189 | 0.032043 | 0.16022 | -0.24261 | 0.13275 | 0.054932 | 0.091553 | -0.004578 | 0.24719 | 0.21057 | -0.23346 | 121.3348 | 0.059509 | 121.6095 | 121.7102 | -0.045776 | 121.344 | 0.10986 | 0.27466 | 121.5729 | 121.8246 | 121.6324 | 121.7377 | 121.6095 | 121.788 | 121.669 | 121.344 | 121.7377 | 121.6095 | 121.669 | 121.6324 | 121.788 | -0.34332 | -0.33417
1604.8594 | 121.8475 | -121.6141 | 0.11444 | 0.009308 | 0.014473 | 0.0066993 | 0.025778 | -0.007543 | -0.010111 | 0.0070645 | 0.018311 | 0.16022 | -0.26093 | 0.14648 | 0.041199 | 0.10071 | -0.004578 | 0.26093 | 0.21515 | -0.2243 | 121.3531 | 0.045776 | 121.6324 | 121.7606 | -0.073242 | 121.3898 | 0.10071 | 0.27924 | 121.6095 | 121.875 | 121.6553 | 121.7743 | 121.6324 | 121.8292 | 121.7148 | 121.3898 | 121.7743 | 121.6324 | 121.7148 | 121.6553 | 121.8292 | -0.37537 | -0.33875
1606.6094 | 121.8292 | -121.5958 | 0.12817 | 0.0016785 | 0.018318 | 0.012681 | 0.026632 | -0.007543 | -0.0075473 | 0.0070645 | 0 | 0.1831 | -0.27008 | 0.10529 | -0.004578 | 0.073242 | -0.032043 | 0.17853 | 0.23346 | -0.2243 | 121.3257 | 0.054931 | 121.5958 | 121.7011 | -0.13275 | 121.3715 | 0.10528 | 0.27008 | 121.5637 | 121.7743 | 121.5912 | 121.7789 | 121.5958 | 121.8292 | 121.669 | 121.3715 | 121.7789 | 121.5958 | 121.669 | 121.5912 | 121.8292 | -0.39826 | -0.35248
1608.3125 | 121.843 | -121.6278 | 0.1236 | -0.005951 | 0.016182 | 0.010972 | 0.025778 | -0.006475 | -0.0077609 | 0.0074917 | -0.022888 | 0.17853 | -0.27924 | 0.082397 | -0.013733 | 0.068665 | -0.013733 | 0.15564 | 0.22888 | -0.21973 | 121.3486 | 0.054932 | 121.6049 | 121.7102 | -0.13733 | 121.4081 | 0.10529 | 0.25635 | 121.6141 | 121.7834 | 121.6141 | 121.8063 | 121.6049 | 121.8567 | 121.6965 | 121.4081 | 121.8063 | 121.6049 | 121.6965 | 121.6141 | 121.8567 | -0.40283 | -0.34332
1610.0469 | 121.8109 | -121.6599 | 0.13733 | -0.005951 | 0.015541 | 0.012467 | 0.026419 | -0.0077566 | -0.0086155 | 0.0092007 | 0.022888 | 0.15564 | -0.27466 | 0.13275 | 0.032043 | 0.091553 | -0.018311 | 0.21057 | 0.2243 | -0.2243 | 121.3852 | 0.018311 | 121.6827 | 121.7926 | -0.10529 | 121.4355 | 0.086975 | 0.29755 | 121.6415 | 121.8704 | 121.6919 | 121.8155 | 121.6827 | 121.8842 | 121.7514 | 121.4355 | 121.8155 | 121.6827 | 121.7514 | 121.6919 | 121.8842 | -0.41199 | -0.36163
1611.7344 | 121.9025 | -121.6278 | 0.07782 | -0.005951 | 0.014687 | 0.011826 | 0.021505 | -0.0079704 | -0.0043429 | 0.0066373 | 0.082397 | 0.1236 | -0.21973 | 0.21973 | 0.13275 | 0.21973 | -0.14191 | 0.36163 | 0.1831 | -0.20142 | 121.4081 | 0.045776 | 121.7102 | 121.8475 | 0.054931 | 121.4264 | 0.10528 | 0.30212 | 121.4859 | 121.9894 | 121.7606 | 121.7514 | 121.7102 | 121.8109 | 121.8475 | 121.4264 | 121.7514 | 121.7102 | 121.8475 | 121.7606 | 121.8109 | -0.29755 | -0.27924
1613.4844 | 121.9482 | -121.582 | 0.10529 | 0.0016785 | 0.014259 | 0.0094763 | 0.025991 | -0.0086112 | -0.0069065 | 0.0072781 | -0.009155 | 0.16479 | -0.27924 | 0.10986 | 0.018311 | 0.073242 | 0.041199 | 0.21515 | 0.2243 | -0.23346 | 121.3028 | 0.059509 | 121.5729 | 121.6919 | -0.086975 | 121.3486 | 0.11902 | 0.27008 | 121.6232 | 121.7972 | 121.6003 | 121.7468 | 121.5729 | 121.8063 | 121.6553 | 121.3486 | 121.7468 | 121.5729 | 121.6553 | 121.6003 | 121.8063 | -0.38452 | -0.33875
1615.1719 | 121.9437 | -121.6187 | 0.10986 | -0.005951 | 0.014259 | 0.013321 | 0.021292 | -0.010107 | -0.0077609 | 0.0072781 | 0.045776 | 0.13275 | -0.23804 | 0.15106 | 0.045776 | 0.11902 | 0 | 0.25635 | 0.21515 | -0.21515 | 121.3806 | 0.022888 | 121.6644 | 121.7697 | -0.064087 | 121.4035 | 0.10529 | 0.28381 | 121.6187 | 121.875 | 121.6644 | 121.7514 | 121.6644 | 121.8338 | 121.7377 | 121.4035 | 121.7514 | 121.6644 | 121.7377 | 121.6644 | 121.8338 | -0.3479 | -0.32501
1616.9219 | 121.9574 | -121.6049 | 0.082397 | -0.005951 | 0.017036 | 0.0092627 | 0.022574 | -0.0090384 | -0.0058383 | 0.0072781 | 0.027466 | 0.13275 | -0.23346 | 0.13275 | 0.059509 | 0.15564 | -0.086975 | 0.26093 | 0.20599 | -0.20599 | 121.3715 | 0.050354 | 121.6324 | 121.7377 | -0.022888 | 121.3989 | 0.1236 | 0.26093 | 121.5179 | 121.8658 | 121.6644 | 121.7377 | 121.6324 | 121.8109 | 121.7606 | 121.3989 | 121.7377 | 121.6324 | 121.7606 | 121.6644 | 121.8109 | -0.31586 | -0.28839
1618.6562 | 121.9666 | -121.6324 | 0.082397 | -0.005951 | 0.013618 | 0.0077673 | 0.025991 | -0.008184 | -0.0064791 | 0.0053555 | 0.032043 | 0.13733 | -0.20142 | 0.15106 | 0.059509 | 0.16022 | -0.10529 | 0.27924 | 0.17853 | -0.19226 | 121.431 | 0.054932 | 121.6644 | 121.7834 | -0.022888 | 121.4401 | 0.096131 | 0.23346 | 121.5271 | 121.9116 | 121.6919 | 121.7697 | 121.6644 | 121.8109 | 121.7926 | 121.4401 | 121.7697 | 121.6644 | 121.7926 | 121.6919 | 121.8109 | -0.28381 | -0.27466
1620.3281 | 121.9437 | -121.669 | 0.10071 | -0.005951 | 0.015755 | 0.014603 | 0.026419 | -0.011602 | -0.0058383 | 0.0053555 | 0.086975 | 0.14191 | -0.21973 | 0.20599 | 0.10529 | 0.17395 | -0.082397 | 0.33417 | 0.19684 | -0.21057 | 121.4493 | 0.041199 | 121.756 | 121.875 | 0.004578 | 121.4584 | 0.09613 | 0.3067 | 121.5866 | 122.0032 | 121.7743 | 121.8109 | 121.756 | 121.8658 | 121.843 | 121.4584 | 121.8109 | 121.756 | 121.843 | 121.7743 | 121.8658 | -0.32044 | -0.31128
1622.0781 | 121.9757 | -121.6415 | 0.068665 | 0.0016785 | 0.017036 | 0.010117 | 0.022574 | -0.010961 | -0.0071201 | 0.0059963 | 0.032043 | 0.16479 | -0.23346 | 0.15106 | 0.059509 | 0.14191 | -0.091553 | 0.25177 | 0.1831 | -0.17853 | 121.4081 | 0.09613 | 121.6736 | 121.7926 | -0.009156 | 121.463 | 0.11444 | 0.2655 | 121.55 | 121.8933 | 121.7011 | 121.8063 | 121.6736 | 121.8246 | 121.7834 | 121.463 | 121.8063 | 121.6736 | 121.7834 | 121.7011 | 121.8246 | -0.30212 | -0.24719
1623.7656 | 121.9711 | -121.6232 | 0.082397 | -0.005951 | 0.014473 | 0.015244 | 0.023855 | -0.008184 | -0.0051975 | 0.0074917 | 0.036621 | 0.15106 | -0.22888 | 0.15564 | 0.050354 | 0.1236 | -0.091553 | 0.26093 | 0.17853 | -0.20142 | 121.3943 | 0.068665 | 121.6599 | 121.7789 | -0.032043 | 121.4218 | 0.096131 | 0.2655 | 121.5317 | 121.8842 | 121.6736 | 121.7743 | 121.6599 | 121.8018 | 121.7468 | 121.4218 | 121.7743 | 121.6599 | 121.7468 | 121.6736 | 121.8018 | -0.31128 | -0.28381
1625.5156 | 121.9162 | -121.6827 | 0.11444 | -0.013581 | 0.016823 | 0.0096899 | 0.025778 | -0.0094656 | -0.0056247 | 0.0072781 | 0.073242 | 0.13733 | -0.23346 | 0.16937 | 0.064087 | 0.16937 | -0.14191 | 0.27466 | 0.1831 | -0.18768 | 121.4493 | 0.022888 | 121.756 | 121.8521 | -0.050354 | 121.4951 | 0.068664 | 0.3067 | 121.5408 | 121.9574 | 121.7468 | 121.8201 | 121.756 | 121.8658 | 121.8521 | 121.4951 | 121.8201 | 121.756 | 121.8521 | 121.7468 | 121.8658 | -0.3479 | -0.30212
1627.25 | 121.875 | -121.7102 | 0.11444 | 0.0016785 | 0.015114 | 0.0096899 | 0.024923 | -0.0073294 | -0.0086155 | 0.0072781 | 0.10529 | 0.13275 | -0.23804 | 0.21057 | 0.07782 | 0.17853 | -0.18768 | 0.30212 | 0.16937 | -0.16937 | 121.4722 | 0.01831 | 121.8155 | 121.9208 | -0.036621 | 121.5408 | 0.054932 | 0.34332 | 121.5225 | 122.0123 | 121.788 | 121.843 | 121.8155 | 121.8796 | 121.8887 | 121.5408 | 121.843 | 121.8155 | 121.8887 | 121.788 | 121.8796 | -0.35248 | -0.28381
1629 | 121.994 | -121.6507 | 0.086975 | -0.005951 | 0.016182 | 0.011185 | 0.025351 | -0.009893 | -0.0051975 | 0.0074917 | 0.041199 | 0.16022 | -0.24261 | 0.15564 | 0.036621 | 0.13275 | -0.10529 | 0.2655 | 0.19226 | -0.20599 | 121.4081 | 0.073242 | 121.6919 | 121.8063 | -0.050354 | 121.4447 | 0.10529 | 0.28381 | 121.5454 | 121.9162 | 121.6873 | 121.8109 | 121.6919 | 121.843 | 121.7834 | 121.4447 | 121.8109 | 121.6919 | 121.7834 | 121.6873 | 121.843 | -0.32959 | -0.29297
1630.75 | 122.0078 | -121.6644 | 0.10529 | 0.0016785 | 0.014259 | 0.013749 | 0.026632 | -0.009893 | -0.0069065 | 0.0087735 | 0.036621 | 0.13733 | -0.23804 | 0.15106 | 0.045776 | 0.10071 | 0.004578 | 0.25177 | 0.21057 | -0.2243 | 121.4264 | 0.032043 | 121.701 | 121.8155 | -0.05951 | 121.4401 | 0.10529 | 0.27466 | 121.669 | 121.9162 | 121.7102 | 121.8018 | 121.701 | 121.875 | 121.7651 | 121.4401 | 121.8018 | 121.701 | 121.7651 | 121.7102 | 121.875 | -0.34332 | -0.32959
1632.4375 | 122.0123 | -121.6736 | 0.10071 | -0.013581 | 0.015114 | 0.015244 | 0.021719 | -0.010961 | -0.0045565 | 0.0072781 | 0.041199 | 0.13733 | -0.21973 | 0.1831 | 0.086975 | 0.16022 | -0.10529 | 0.3067 | 0.17853 | -0.20142 | 121.4539 | 0.036621 | 121.7148 | 121.8567 | -0.013733 | 121.4722 | 0.07782 | 0.26093 | 121.5683 | 121.9803 | 121.7606 | 121.8109 | 121.7148 | 121.8521 | 121.8338 | 121.4722 | 121.8109 | 121.7148 | 121.8338 | 121.7606 | 121.8521 | -0.32044 | -0.30212
1634.1875 | 121.9025 | -121.7285 | 0.10986 | -0.005951 | 0.016396 | 0.010972 | 0.026632 | -0.0096794 | -0.0054111 | 0.0072781 | 0.068665 | 0.13275 | -0.2243 | 0.20142 | 0.086975 | 0.17395 | -0.16937 | 0.28839 | 0.17395 | -0.19226 | 121.5042 | 0.022888 | 121.7972 | 121.9299 | -0.022888 | 121.5363 | 0.064087 | 0.29297 | 121.5591 | 122.0169 | 121.8155 | 121.8613 | 121.7972 | 121.9025 | 121.9025 | 121.5363 | 121.8613 | 121.7972 | 121.9025 | 121.8155 | 121.9025 | -0.33417 | -0.30212
1635.875 | 121.8933 | -121.7377 | 0.13733 | -0.005951 | 0.015755 | 0.010331 | 0.027273 | -0.010747 | -0.0069065 | 0.0077053 | 0.050354 | 0.16022 | -0.25635 | 0.17853 | 0.041199 | 0.11902 | -0.041199 | 0.25635 | 0.20142 | -0.21973 | 121.4813 | 0.022888 | 121.788 | 121.9162 | -0.09613 | 121.5179 | 0.064087 | 0.3067 | 121.6965 | 121.994 | 121.7789 | 121.8979 | 121.788 | 121.9391 | 121.8567 | 121.5179 | 121.8979 | 121.788 | 121.8567 | 121.7789 | 121.9391 | -0.39368 | -0.35706
1637.625 | 121.9345 | -121.7285 | 0.1236 | -0.005951 | 0.017891 | 0.0086219 | 0.023428 | -0.0066886 | -0.0081881 | 0.0094143 | -0.009155 | 0.16479 | -0.25635 | 0.11444 | 0 | 0.082397 | -0.082397 | 0.19684 | 0.18768 | -0.19684 | 121.4722 | 0.041199 | 121.7194 | 121.843 | -0.1236 | 121.5317 | 0.064087 | 0.24719 | 121.6461 | 121.9254 | 121.7285 | 121.8933 | 121.7194 | 121.9162 | 121.8109 | 121.5317 | 121.8933 | 121.7194 | 121.8109 | 121.7285 | 121.9162 | -0.37994 | -0.32043
1639.375 | 122.0215 | -121.6873 | 0.09613 | -0.005951 | 0.014687 | 0.012467 | 0.022787 | -0.012029 | -0.0064791 | 0.0049283 | 0.022888 | 0.15106 | -0.2243 | 0.15106 | 0.059509 | 0.16022 | -0.091553 | 0.26093 | 0.20599 | -0.20142 | 121.463 | 0.054932 | 121.7102 | 121.8384 | -0.036621 | 121.4859 | 0.10986 | 0.24719 | 121.5958 | 121.9482 | 121.7468 | 121.8384 | 121.7102 | 121.8933 | 121.8475 | 121.4859 | 121.8384 | 121.7102 | 121.8475 | 121.7468 | 121.8933 | -0.32043 | -0.29755
1641.0469 | 122.0352 | -121.6965 | 0.086975 | -0.013581 | 0.015327 | 0.010331 | 0.024069 | -0.0094656 | -0.0037021 | 0.0059963 | 0.041199 | 0.13733 | -0.22888 | 0.15106 | 0.059509 | 0.15106 | -0.09613 | 0.27466 | 0.18768 | -0.2243 | 121.4676 | 0.050354 | 121.7377 | 121.8475 | -0.027466 | 121.4722 | 0.10071 | 0.27008 | 121.6003 | 121.9711 | 121.756 | 121.8338 | 121.7377 | 121.8842 | 121.8475 | 121.4722 | 121.8338 | 121.7377 | 121.8475 | 121.756 | 121.8842 | -0.31586 | -0.31128
1642.7969 | 121.9574 | -121.7285 | 0.13275 | 0.016937 | 0.013618 | 0.011612 | 0.029623 | -0.0066886 | -0.0081881 | 0.0079189 | -0.022888 | 0.16022 | -0.28381 | 0.10529 | -0.027466 | 0.041199 | -0.004578 | 0.16022 | 0.21057 | -0.21973 | 121.4447 | 0.027466 | 121.7056 | 121.8338 | -0.16022 | 121.5088 | 0.07782 | 0.26092 | 121.7239 | 121.8887 | 121.701 | 121.8887 | 121.7056 | 121.9391 | 121.7697 | 121.5088 | 121.8887 | 121.7056 | 121.7697 | 121.701 | 121.9391 | -0.41656 | -0.35248
1644.5312 | 121.9254 | -121.7194 | 0.14191 | 0.0016785 | 0.015327 | 0.014176 | 0.025991 | -0.007543 | -0.0071201 | 0.0066373 | -0.009155 | 0.17395 | -0.26093 | 0.12817 | 0.013733 | 0.10529 | -0.07782 | 0.20599 | 0.21515 | -0.19684 | 121.4584 | 0.032043 | 121.7102 | 121.8475 | -0.12817 | 121.5225 | 0.073242 | 0.25177 | 121.6415 | 121.9254 | 121.7331 | 121.8933 | 121.7102 | 121.9345 | 121.8246 | 121.5225 | 121.8933 | 121.7102 | 121.8246 | 121.7331 | 121.9345 | -0.40283 | -0.33875
1646.2031 | 122.049 | -121.7148 | 0.10529 | -0.005951 | 0.014259 | 0.012253 | 0.021292 | -0.008184 | -0.0041293 | 0.0062099 | 0.036621 | 0.13733 | -0.22888 | 0.17853 | 0.09613 | 0.17853 | -0.10529 | 0.28381 | 0.1831 | -0.21973 | 121.4859 | 0.032043 | 121.7514 | 121.8933 | -0.009156 | 121.4951 | 0.077819 | 0.2655 | 121.6095 | 121.9986 | 121.8109 | 121.8521 | 121.7514 | 121.8979 | 121.8933 | 121.4951 | 121.8521 | 121.7514 | 121.8933 | 121.8109 | 121.8979 | -0.33417 | -0.32501
1647.9531 | 121.962 | -121.7468 | 0.1236 | 0.0016785 | 0.01725 | 0.0092627 | 0.027273 | -0.0086112 | -0.0081881 | 0.0072781 | -0.013733 | 0.17395 | -0.26093 | 0.082397 | -0.027466 | 0.050354 | 0.018311 | 0.14648 | 0.21515 | -0.22888 | 121.4859 | 0.050354 | 121.7331 | 121.8292 | -0.15106 | 121.5179 | 0.091553 | 0.24719 | 121.7651 | 121.8933 | 121.7194 | 121.9208 | 121.7331 | 121.962 | 121.7972 | 121.5179 | 121.9208 | 121.7331 | 121.7972 | 121.7194 | 121.962 | -0.38452 | -0.35248
1649.6875 | 121.9666 | -121.7743 | 0.11902 | 0.009308 | 0.016396 | 0.0088355 | 0.021933 | -0.0083976 | -0.0058383 | 0.0057827 | 0.064087 | 0.1236 | -0.21057 | 0.1831 | 0.086975 | 0.19226 | -0.16022 | 0.28839 | 0.19684 | -0.18768 | 121.5637 | 0.004577 | 121.8384 | 121.9574 | -0.032044 | 121.5866 | 0.077819 | 0.27466 | 121.6141 | 122.0627 | 121.8613 | 121.8979 | 121.8384 | 121.9711 | 121.9666 | 121.5866 | 121.8979 | 121.8384 | 121.9666 | 121.8613 | 121.9711 | -0.32959 | -0.3067
1651.3594 | 121.9528 | -121.7697 | 0.11444 | 0.0016785 | 0.01725 | 0.0096899 | 0.028341 | -0.0073294 | -0.0066929 | 0.0087735 | 0.054932 | 0.17395 | -0.23804 | 0.16479 | 0.041199 | 0.11444 | -0.032043 | 0.2655 | 0.19684 | -0.21973 | 121.5317 | 0.059509 | 121.8246 | 121.9345 | -0.073242 | 121.55 | 0.082397 | 0.29297 | 121.7377 | 122.0352 | 121.8109 | 121.9437 | 121.8246 | 121.9666 | 121.8842 | 121.55 | 121.9437 | 121.8246 | 121.8842 | 121.8109 | 121.9666 | -0.35248 | -0.33417
1653.1094 | 122.081 | -121.7239 | 0.091553 | 0.0016785 | 0.013405 | 0.0071265 | 0.02001 | -0.011175 | -0.0043429 | 0.0072781 | 0.041199 | 0.14648 | -0.2243 | 0.16022 | 0.086975 | 0.16937 | -0.10529 | 0.27924 | 0.1831 | -0.19226 | 121.4996 | 0.054931 | 121.7651 | 121.8842 | -0.004578 | 121.5317 | 0.091552 | 0.2655 | 121.6187 | 122.0032 | 121.8109 | 121.8704 | 121.7651 | 121.907 | 121.8933 | 121.5317 | 121.8704 | 121.7651 | 121.8933 | 121.8109 | 121.907 | -0.31586 | -0.28381
1654.8438 | 122.0215 | -121.756 | 0.10071 | -0.005951 | 0.015968 | 0.0071265 | 0.029623 | -0.0088248 | -0.0069065 | 0.0059963 | 0.086975 | 0.13275 | -0.21515 | 0.21515 | 0.11444 | 0.17853 | -0.13275 | 0.3479 | 0.19684 | -0.19684 | 121.5408 | 0.032043 | 121.843 | 121.9711 | 0.013733 | 121.5591 | 0.09613 | 0.30212 | 121.6232 | 122.1039 | 121.8704 | 121.8887 | 121.843 | 121.9528 | 121.9345 | 121.5591 | 121.8887 | 121.843 | 121.9345 | 121.8704 | 121.9528 | -0.31586 | -0.29755
1656.5781 | 122.0306 | -121.7697 | 0.1236 | -0.005951 | 0.014259 | 0.010544 | 0.025351 | -0.0096794 | -0.0081881 | 0.0064237 | 0.10071 | 0.14191 | -0.21515 | 0.2243 | 0.1236 | 0.21515 | -0.12817 | 0.36163 | 0.18768 | -0.20142 | 121.5546 | 0.018311 | 121.8704 | 121.994 | 0 | 121.5683 | 0.064087 | 0.31586 | 121.6415 | 122.1313 | 121.8933 | 121.9116 | 121.8704 | 121.9574 | 121.9849 | 121.5683 | 121.9116 | 121.8704 | 121.9849 | 121.8933 | 121.9574 | -0.33875 | -0.32501
1658.25 | 121.9437 | -121.8018 | 0.1236 | 0.0016785 | 0.014046 | 0.011399 | 0.030691 | -0.007543 | -0.0058383 | 0.0066373 | 0.11902 | 0.11444 | -0.20599 | 0.21973 | 0.10986 | 0.19684 | -0.20142 | 0.32044 | 0.17853 | -0.17853 | 121.5958 | -0.009155 | 121.9208 | 122.0215 | -0.013733 | 121.6232 | 0.054932 | 0.32501 | 121.6003 | 122.1222 | 121.9116 | 121.9162 | 121.9208 | 121.9803 | 121.9986 | 121.6232 | 121.9162 | 121.9208 | 121.9986 | 121.9116 | 121.9803 | -0.32959 | -0.30212
1659.9844 | 121.9849 | -121.8109 | 0.13733 | -0.005951 | 0.015327 | 0.010972 | 0.027273 | -0.0066886 | -0.0073337 | 0.0081325 | 0.10529 | 0.12817 | -0.20599 | 0.21057 | 0.091553 | 0.19226 | -0.17395 | 0.29755 | 0.16479 | -0.19684 | 121.6049 | -0.009155 | 121.9162 | 122.0215 | -0.045776 | 121.6141 | 0.027466 | 0.31128 | 121.637 | 122.1085 | 121.9025 | 121.9391 | 121.9162 | 121.9757 | 122.0032 | 121.6141 | 121.9391 | 121.9162 | 122.0032 | 121.9025 | 121.9757 | -0.34332 | -0.33417
1661.7188 | 122.0856 | -121.7514 | 0.10529 | -0.005951 | 0.015968 | 0.013535 | 0.0277 | -0.0096794 | -0.0075473 | 0.0089871 | 0.036621 | 0.14191 | -0.21973 | 0.16022 | 0.059509 | 0.14191 | -0.10529 | 0.26093 | 0.19684 | -0.19684 | 121.5317 | 0.036621 | 121.788 | 121.9116 | -0.045777 | 121.5546 | 0.091552 | 0.25635 | 121.6461 | 122.0123 | 121.8109 | 121.8933 | 121.788 | 121.9482 | 121.8933 | 121.5546 | 121.8933 | 121.788 | 121.8933 | 121.8109 | 121.9482 | -0.32501 | -0.30212
1663.4844 | 122.0627 | -121.7789 | 0.073242 | -0.013581 | 0.015327 | 0.0088355 | 0.027273 | -0.009893 | -0.0064791 | 0.0077053 | 0.064087 | 0.13275 | -0.21515 | 0.23346 | 0.11444 | 0.19684 | -0.14648 | 0.3479 | 0.17853 | -0.1831 | 121.5637 | 0.059509 | 121.843 | 122.0123 | 0.041199 | 121.5958 | 0.10529 | 0.27924 | 121.6324 | 122.1268 | 121.8933 | 121.9116 | 121.843 | 121.9574 | 121.9757 | 121.5958 | 121.9116 | 121.843 | 121.9757 | 121.8933 | 121.9574 | -0.28839 | -0.25635
1665.1562 | 122.0947 | -121.7789 | 0.11444 | -0.005951 | 0.01725 | 0.0099037 | 0.029409 | -0.009252 | -0.0069065 | 0.0092007 | 0.027466 | 0.14191 | -0.21973 | 0.13275 | 0.004578 | 0.10071 | 0.018311 | 0.22888 | 0.21973 | -0.2243 | 121.5591 | 0.027466 | 121.8063 | 121.9116 | -0.10986 | 121.5546 | 0.10529 | 0.24719 | 121.7972 | 122.0078 | 121.7834 | 121.9208 | 121.8063 | 121.9986 | 121.8796 | 121.5546 | 121.9208 | 121.8063 | 121.8796 | 121.7834 | 121.9986 | -0.33417 | -0.33875
1666.9062 | 122.0856 | -121.7697 | 0.11444 | -0.005951 | 0.015968 | 0.013321 | 0.032614 | -0.0077566 | -0.0084017 | 0.0085599 | -0.009155 | 0.17395 | -0.27466 | 0.11444 | 0.018311 | 0.064087 | 0.041199 | 0.21973 | 0.22888 | -0.23346 | 121.4951 | 0.059509 | 121.7606 | 121.8842 | -0.09613 | 121.5363 | 0.11444 | 0.2655 | 121.8109 | 121.9894 | 121.788 | 121.9437 | 121.7606 | 121.9986 | 121.8338 | 121.5363 | 121.9437 | 121.7606 | 121.8338 | 121.788 | 121.9986 | -0.3891 | -0.3479
1668.5938 | 121.994 | -121.8246 | 0.14648 | 0.0016785 | 0.015968 | 0.0088355 | 0.029623 | -0.010534 | -0.0066929 | 0.0066373 | 0.09613 | 0.1236 | -0.21057 | 0.19684 | 0.11444 | 0.1831 | -0.17853 | 0.30212 | 0.17395 | -0.18768 | 121.6141 | -0.022888 | 121.9208 | 122.0215 | -0.032043 | 121.637 | 0.027466 | 0.3067 | 121.6461 | 122.1268 | 121.9391 | 121.9482 | 121.9208 | 121.9986 | 122.0078 | 121.637 | 121.9482 | 121.9208 | 122.0078 | 121.9391 | 121.9986 | -0.35706 | -0.33417
1670.3438 | 122.1222 | -121.8018 | 0.11902 | 0.009308 | 0.014259 | 0.0096899 | 0.031759 | -0.011175 | -0.0054111 | 0.0064237 | 0.013733 | 0.16022 | -0.27008 | 0.12817 | 0.041199 | 0.073242 | 0.027466 | 0.21973 | 0.20599 | -0.22888 | 121.5317 | 0.041198 | 121.8155 | 121.9299 | -0.07782 | 121.5729 | 0.086975 | 0.28381 | 121.8292 | 122.0215 | 121.843 | 121.962 | 121.8155 | 122.0078 | 121.875 | 121.5729 | 121.962 | 121.8155 | 121.875 | 121.843 | 122.0078 | -0.3891 | -0.3479
1672.0156 | 122.0078 | -121.8246 | 0.11902 | 0.0016785 | 0.015327 | 0.012253 | 0.035177 | -0.0083976 | -0.0086155 | 0.0077053 | 0.045776 | 0.16479 | -0.25177 | 0.15564 | 0.054932 | 0.11444 | -0.032043 | 0.25177 | 0.21057 | -0.19684 | 121.5729 | 0.045776 | 121.8704 | 121.9803 | -0.064087 | 121.6278 | 0.091552 | 0.29755 | 121.7926 | 122.0764 | 121.8796 | 121.9894 | 121.8704 | 122.0352 | 121.9391 | 121.6278 | 121.9894 | 121.8704 | 121.9391 | 121.8796 | 122.0352 | -0.37079 | -0.31586
1673.75 | 122.0352 | -121.8109 | 0.11902 | 0.0016785 | 0.017036 | 0.012681 | 0.036673 | -0.0054068 | -0.0094699 | 0.0083463 | -0.013733 | 0.17395 | -0.25177 | 0.086975 | -0.013733 | 0.041199 | -0.004578 | 0.16937 | 0.21057 | -0.21057 | 121.5591 | 0.054931 | 121.7972 | 121.8979 | -0.13275 | 121.6003 | 0.091552 | 0.23804 | 121.8063 | 121.9803 | 121.7972 | 121.9849 | 121.7972 | 122.0215 | 121.8521 | 121.6003 | 121.9849 | 121.7972 | 121.8521 | 121.7972 | 122.0215 | -0.37079 | -0.32959
1675.5 | 122.0352 | -121.7789 | 0.10986 | 0.009308 | 0.01725 | 0.013535 | 0.033041 | -0.005834 | -0.0077609 | 0.0079189 | -0.013733 | 0.16937 | -0.26093 | 0.082397 | -0.018311 | 0.064087 | -0.004578 | 0.15106 | 0.21515 | -0.2243 | 121.5179 | 0.05951 | 121.7651 | 121.8613 | -0.12817 | 121.5546 | 0.10529 | 0.24719 | 121.7743 | 121.9299 | 121.7606 | 121.9482 | 121.7651 | 121.994 | 121.843 | 121.5546 | 121.9482 | 121.7651 | 121.843 | 121.7606 | 121.994 | -0.37079 | -0.33417
1677.2188 | 122.113 | -121.7926 | 0.10986 | -0.005951 | 0.014473 | 0.010544 | 0.026846 | -0.0083976 | -0.0075473 | 0.0085599 | 0.050354 | 0.13733 | -0.23804 | 0.15564 | 0.059509 | 0.11902 | -0.009155 | 0.25635 | 0.20599 | -0.21515 | 121.5546 | 0.027466 | 121.843 | 121.9482 | -0.050354 | 121.5775 | 0.096131 | 0.28839 | 121.7834 | 122.049 | 121.8521 | 121.9299 | 121.843 | 121.9986 | 121.9116 | 121.5775 | 121.9299 | 121.843 | 121.9116 | 121.8521 | 121.9986 | -0.3479 | -0.32501
1678.9062 | 122.1039 | -121.7697 | 0.16479 | -0.005951 | 0.018318 | 0.010544 | 0.1845 | -0.0094656 | -0.0064791 | 0.0079189 | 0.018311 | 0.19226 | -0.2243 | 0.12817 | 0.032043 | 0.082397 | 0.032043 | 0.23346 | 0.24261 | -0.23346 | 121.5454 | 0.027466 | 121.788 | 121.8979 | -0.13275 | 121.5363 | 0.07782 | 0.24261 | 121.8018 | 122.0032 | 121.8018 | 121.962 | 121.788 | 122.0123 | 121.8521 | 121.5363 | 121.962 | 121.788 | 121.8521 | 121.8018 | 122.0123 | -0.3891 | -0.39825
1680.6562 | 122.1359 | -121.8475 | 0.09613 | 0.0016785 | 0.013405 | 0.01204 | 0.024496 | -0.011602 | -0.0054111 | 0.0068509 | -0.032043 | 0.17853 | -0.25177 | 0.10071 | 0.004578 | 0.050354 | 0.054932 | 0.20142 | 0.2243 | -0.24261 | 121.5958 | 0.082398 | 121.8155 | 121.9482 | -0.091552 | 121.6049 | 0.12817 | 0.21973 | 121.9025 | 122.0489 | 121.8521 | 122.0261 | 121.8155 | 122.0718 | 121.8979 | 121.6049 | 122.0261 | 121.8155 | 121.8979 | 121.8521 | 122.0718 | -0.3479 | -0.33874
1682.3906 | 122.1222 | -121.8292 | 0.10986 | -0.005951 | 0.017036 | 0.0094763 | 0.021933 | -0.008184 | -0.0060519 | 0.0062099 | 0.045776 | 0.14648 | -0.2243 | 0.1236 | 0.036621 | 0.091553 | 0.009155 | 0.23804 | 0.21515 | -0.21515 | 121.6049 | 0.036621 | 121.875 | 121.9528 | -0.073242 | 121.6141 | 0.10529 | 0.27008 | 121.8384 | 122.0673 | 121.8658 | 121.9757 | 121.875 | 122.0444 | 121.9208 | 121.6141 | 121.9757 | 121.875 | 121.9208 | 121.8658 | 122.0444 | -0.33417 | -0.32501
1684.0781 | 122.1313 | -121.8338 | 0.10986 | -0.005951 | 0.016182 | 0.010544 | 0.026419 | -0.011602 | -0.0056247 | 0.0070645 | -0.018311 | 0.1831 | -0.25635 | 0.082397 | -0.013733 | 0.064087 | 0.064087 | 0.20599 | 0.2243 | -0.23804 | 121.5775 | 0.073242 | 121.8155 | 121.9162 | -0.1236 | 121.5958 | 0.11444 | 0.23804 | 121.8979 | 122.0398 | 121.8201 | 122.0169 | 121.8155 | 122.0581 | 121.8979 | 121.5958 | 122.0169 | 121.8155 | 121.8979 | 121.8201 | 122.0581 | -0.36621 | -0.3479
1685.75 | 122.0215 | -121.8521 | 0.14191 | 0.0016785 | 0.015755 | 0.013535 | 0.036245 | -0.0086112 | -0.0062655 | 0.0064237 | 0.091553 | 0.1236 | -0.20142 | 0.19684 | 0.10529 | 0.18768 | -0.17395 | 0.30212 | 0.17395 | -0.18768 | 121.6507 | -0.018311 | 121.9437 | 122.049 | -0.036621 | 121.6644 | 0.032043 | 0.29297 | 121.6782 | 122.1542 | 121.9574 | 121.9757 | 121.9437 | 122.0261 | 122.0398 | 121.6644 | 121.9757 | 121.9437 | 122.0398 | 121.9574 | 122.0261 | -0.34332 | -0.32959
1687.4844 | 122.1405 | -121.8338 | 0.10529 | -0.005951 | 0.013405 | 0.010331 | 0.02471 | -0.010534 | -0.0062655 | 0.0066373 | 0.036621 | 0.13733 | -0.23346 | 0.16022 | 0.068665 | 0.11444 | -0.022888 | 0.27466 | 0.20599 | -0.21057 | 121.6003 | 0.032043 | 121.8704 | 121.994 | -0.036621 | 121.6232 | 0.10071 | 0.27008 | 121.8109 | 122.1085 | 121.9025 | 121.9711 | 121.8704 | 122.0398 | 121.9482 | 121.6232 | 121.9711 | 121.8704 | 121.9482 | 121.9025 | 122.0398 | -0.33875 | -0.31586
1689.1719 | 122.0398 | -121.8567 | 0.14648 | 0.009308 | 0.014687 | 0.0081947 | 0.033896 | -0.0079704 | -0.0092563 | 0.0068509 | 0.022888 | 0.15564 | -0.25635 | 0.1236 | 0 | 0.064087 | -0.004578 | 0.19226 | 0.22888 | -0.21057 | 121.6003 | 0.009156 | 121.8796 | 121.9803 | -0.14648 | 121.6461 | 0.082398 | 0.27924 | 121.8521 | 122.049 | 121.8567 | 122.0123 | 121.8796 | 122.0856 | 121.9208 | 121.6461 | 122.0123 | 121.8796 | 121.9208 | 121.8567 | 122.0856 | -0.40283 | -0.35706
1690.9375 | 122.0764 | -121.8567 | 0.1236 | 0.0016785 | 0.017677 | 0.014176 | 0.081747 | -0.0069022 | -0.0075473 | 0.0072781 | -0.018311 | 0.18768 | -0.25635 | 0.086975 | -0.018311 | 0.059509 | -0.004578 | 0.16479 | 0.23804 | -0.21973 | 121.6003 | 0.064087 | 121.8384 | 121.9437 | -0.14191 | 121.637 | 0.11444 | 0.23804 | 121.8521 | 122.0215 | 121.8384 | 122.0444 | 121.8384 | 122.0947 | 121.9162 | 121.637 | 122.0444 | 121.8384 | 121.9162 | 121.8384 | 122.0947 | -0.37994 | -0.34332
1692.6875 | 122.1313 | -121.7834 | 0.14191 | 0.009308 | 0.014259 | 0.011399 | 0.15716 | -0.010107 | -0.0045565 | 0.0087735 | 0.073242 | 0.14191 | -0.21515 | 0.21973 | 0.13275 | 0.20599 | -0.13275 | 0.32501 | 0.20599 | -0.19684 | 121.5683 | 0 | 121.8567 | 122.0032 | -0.009156 | 121.5866 | 0.064087 | 0.28839 | 121.6507 | 122.1085 | 121.9162 | 121.9254 | 121.8567 | 121.9894 | 121.9894 | 121.5866 | 121.9254 | 121.8567 | 121.9894 | 121.9162 | 121.9894 | -0.35706 | -0.33875
1694.4219 | 122.113 | -121.843 | 0.13733 | -0.013581 | 0.0149 | 0.0094763 | 0.079397 | -0.0086112 | -0.0043429 | 0.0059963 | 0.09613 | 0.14191 | -0.21515 | 0.21973 | 0.1236 | 0.22888 | -0.15564 | 0.37079 | 0.19684 | -0.19684 | 121.6278 | 0.004578 | 121.9391 | 122.0627 | -0.013733 | 121.6461 | 0.059509 | 0.31128 | 121.6873 | 122.2137 | 121.9666 | 121.9849 | 121.9391 | 122.0398 | 122.0718 | 121.6461 | 121.9849 | 121.9391 | 122.0718 | 121.9666 | 122.0398 | -0.35248 | -0.33417
1696.0938 | 122.049 | -121.8201 | 0.22888 | -0.005951 | 0.015541 | 0.012467 | 0.085806 | -0.0073294 | -0.0090427 | 0.0074917 | 0.064087 | 0.16937 | -0.25177 | 0.16937 | 0.050354 | 0.11444 | -0.050354 | 0.2655 | 0.21515 | -0.21057 | 121.5683 | -0.059509 | 121.8842 | 121.9894 | -0.17853 | 121.6095 | -0.013733 | 0.31586 | 121.7697 | 122.0856 | 121.8704 | 121.9894 | 121.8842 | 122.0352 | 121.9345 | 121.6095 | 121.9894 | 121.8842 | 121.9345 | 121.8704 | 122.0352 | -0.48065 | -0.43945
1697.8438 | 122.113 | -121.875 | 0.13275 | 0.0016785 | 0.014046 | 0.0099037 | 0.079611 | -0.0088248 | -0.0060519 | 0.0062099 | 0.10529 | 0.13275 | -0.21515 | 0.21057 | 0.1236 | 0.1831 | -0.11902 | 0.32501 | 0.17853 | -0.17853 | 121.6599 | 0 | 121.9803 | 122.0856 | -0.009155 | 121.6965 | 0.045777 | 0.32044 | 121.756 | 122.2 | 121.9986 | 122.0078 | 121.9803 | 122.0535 | 122.0581 | 121.6965 | 122.0078 | 121.9803 | 122.0581 | 121.9986 | 122.0535 | -0.3479 | -0.31128
1699.5156 | 122.0306 | -121.8842 | 0.14191 | -0.005951 | 0.01725 | 0.0099037 | 0.085165 | -0.0077566 | -0.0094699 | 0.0079189 | 0.059509 | 0.16022 | -0.25177 | 0.15106 | 0.050354 | 0.10529 | -0.050354 | 0.23346 | 0.22888 | -0.20142 | 121.6324 | 0.01831 | 121.9437 | 122.0352 | -0.091553 | 121.6827 | 0.086975 | 0.31128 | 121.8338 | 122.1176 | 121.9345 | 122.0444 | 121.9437 | 122.113 | 121.9894 | 121.6827 | 122.0444 | 121.9437 | 121.9894 | 121.9345 | 122.113 | -0.39368 | -0.34332
1701.25 | 122.0261 | -121.8887 | 0.14648 | -0.005951 | 0.012337 | 0.011399 | 0.083456 | -0.004766 | -0.0077609 | 0.0064237 | 0.091553 | 0.12817 | -0.2243 | 0.21515 | 0.11444 | 0.19684 | -0.19226 | 0.3067 | 0.18768 | -0.19226 | 121.6644 | -0.01831 | 121.9803 | 122.1039 | -0.032043 | 121.6965 | 0.041199 | 0.31586 | 121.6965 | 122.1954 | 122.0032 | 122.0169 | 121.9803 | 122.0764 | 122.0856 | 121.6965 | 122.0169 | 121.9803 | 122.0856 | 122.0032 | 122.0764 | -0.37079 | -0.33874
1703 | 122.0627 | -121.8887 | 0.13275 | 0.0016785 | 0.014046 | 0.013962 | 0.083883 | -0.0071158 | -0.010325 | 0.0059963 | 0.004578 | 0.16022 | -0.25635 | 0.11444 | 0.004578 | 0.1236 | -0.086975 | 0.2243 | 0.2243 | -0.19226 | 121.6324 | 0.027466 | 121.8933 | 122.0032 | -0.12817 | 121.6965 | 0.091553 | 0.26093 | 121.8018 | 122.113 | 121.8933 | 122.049 | 121.8933 | 122.113 | 122.0123 | 121.6965 | 122.049 | 121.8933 | 122.0123 | 121.8933 | 122.113 | -0.3891 | -0.32501
1704.6719 | 122.1405 | -121.8704 | 0.11902 | -0.013581 | 0.016823 | 0.010972 | 0.080679 | -0.009252 | -0.0043429 | 0.0074917 | 0.086975 | 0.13275 | -0.22888 | 0.21973 | 0.14191 | 0.21057 | -0.14648 | 0.35706 | 0.19226 | -0.19684 | 121.6415 | 0.013732 | 121.9574 | 122.0901 | 0.022888 | 121.6736 | 0.073242 | 0.31586 | 121.7239 | 122.2275 | 122.0123 | 122.0032 | 121.9574 | 122.0627 | 122.081 | 121.6736 | 122.0032 | 121.9574 | 122.081 | 122.0123 | 122.0627 | -0.3479 | -0.31586
1706.4219 | 122.2 | -121.8658 | 0.1236 | -0.005951 | 0.015755 | 0.012681 | 0.080679 | -0.009252 | -0.0066929 | 0.0062099 | 0.036621 | 0.14191 | -0.21515 | 0.13733 | 0.064087 | 0.13733 | -0.09613 | 0.25635 | 0.18768 | -0.17395 | 121.6507 | 0.018311 | 121.9025 | 122.0032 | -0.059509 | 121.6919 | 0.064087 | 0.25177 | 121.7697 | 122.1222 | 121.9299 | 122.0078 | 121.9025 | 122.0535 | 122.0032 | 121.6919 | 122.0078 | 121.9025 | 122.0032 | 121.9299 | 122.0535 | -0.33875 | -0.29755
1708.1094 | 122.0947 | -121.8842 | 0.13733 | 0.0016785 | 0.017677 | 0.014176 | 0.087515 | -0.008184 | -0.0090427 | 0.0068509 | 0 | 0.17395 | -0.2655 | 0.10071 | -0.013733 | 0.064087 | -0.022888 | 0.16937 | 0.22888 | -0.23346 | 121.6187 | 0.036621 | 121.8842 | 121.9849 | -0.15106 | 121.6507 | 0.091553 | 0.2655 | 121.8613 | 122.0535 | 121.8704 | 122.0581 | 121.8842 | 122.113 | 121.9482 | 121.6507 | 122.0581 | 121.8842 | 121.9482 | 121.8704 | 122.113 | -0.40283 | -0.37079
1709.8594 | 122.1771 | -121.8475 | 0.11902 | -0.013581 | 0.016609 | 0.0077673 | 0.08132 | -0.010534 | -0.0039157 | 0.0085599 | 0.032043 | 0.14191 | -0.2243 | 0.15106 | 0.064087 | 0.13733 | -0.082397 | 0.25635 | 0.20142 | -0.18768 | 121.6232 | 0.022888 | 121.8796 | 121.9986 | -0.054932 | 121.6599 | 0.082397 | 0.25635 | 121.7651 | 122.1039 | 121.9116 | 121.9894 | 121.8796 | 122.0489 | 121.9849 | 121.6599 | 121.9894 | 121.8796 | 121.9849 | 121.9116 | 122.0489 | -0.34332 | -0.3067
1711.5469 | 122.0581 | -121.9025 | 0.14648 | 0.0016785 | 0.018745 | 0.011399 | 0.10097 | -0.0073294 | -0.0086155 | 0.0094143 | 0.059509 | 0.16022 | -0.26093 | 0.15564 | 0.036621 | 0.10986 | -0.036621 | 0.24261 | 0.22888 | -0.21057 | 121.6415 | 0.013733 | 121.962 | 122.0581 | -0.10986 | 121.6919 | 0.082398 | 0.32043 | 121.8658 | 122.1451 | 121.9391 | 122.0627 | 121.962 | 122.1313 | 122.0123 | 121.6919 | 122.0627 | 121.962 | 122.0123 | 121.9391 | 122.1313 | -0.40741 | -0.35706
1713.2969 | 122.1268 | -121.7972 | 0.10986 | -0.005951 | 0.015327 | 0.010544 | 0.088797 | -0.0094656 | -0.0058383 | 0.0081325 | 0.027466 | 0.13275 | -0.2243 | 0.14648 | 0.064087 | 0.15106 | -0.091553 | 0.2655 | 0.18768 | -0.20599 | 121.5729 | 0.022888 | 121.8246 | 121.9437 | -0.045776 | 121.5912 | 0.07782 | 0.25177 | 121.7056 | 122.0627 | 121.8613 | 121.9299 | 121.8246 | 121.9849 | 121.9482 | 121.5912 | 121.9299 | 121.8246 | 121.9482 | 121.8613 | 121.9849 | -0.33417 | -0.31586
1715.0469 | 122.1268 | -121.7926 | 0.11902 | -0.005951 | 0.014687 | 0.012467 | 0.093496 | -0.010534 | -0.0071201 | 0.0094143 | 0.059509 | 0.13733 | -0.21057 | 0.16937 | 0.059509 | 0.1236 | -0.022888 | 0.26093 | 0.21515 | -0.2243 | 121.582 | 0.01831 | 121.8521 | 121.962 | -0.05951 | 121.5683 | 0.09613 | 0.27008 | 121.7697 | 122.0535 | 121.8521 | 121.9299 | 121.8521 | 122.0078 | 121.9162 | 121.5683 | 121.9299 | 121.8521 | 121.9162 | 121.8521 | 122.0078 | -0.32959 | -0.34332
1716.7344 | 122.0718 | -121.8384 | 0.14191 | 0.0016785 | 0.016182 | 0.013108 | 0.095633 | -0.0069022 | -0.0086155 | 0.0062099 | 0.013733 | 0.16022 | -0.2655 | 0.15106 | 0.022888 | 0.091553 | -0.004578 | 0.23346 | 0.22888 | -0.21057 | 121.5729 | 0.01831 | 121.8521 | 121.9894 | -0.11902 | 121.6278 | 0.086975 | 0.27924 | 121.8338 | 122.0718 | 121.8613 | 121.9986 | 121.8521 | 122.0673 | 121.9299 | 121.6278 | 121.9986 | 121.8521 | 121.9299 | 121.8613 | 122.0673 | -0.40741 | -0.35248
1718.5 | 122.0947 | -121.8109 | 0.11444 | -0.005951 | 0.011909 | 0.014176 | 0.085592 | -0.010107 | -0.0064791 | 0.0072781 | 0.032043 | 0.16479 | -0.22888 | 0.12817 | 0.041199 | 0.091553 | 0.018311 | 0.23804 | 0.21973 | -0.2243 | 121.582 | 0.050354 | 121.843 | 121.9391 | -0.073242 | 121.5866 | 0.10529 | 0.26093 | 121.8292 | 122.049 | 121.8521 | 121.9757 | 121.843 | 122.0306 | 121.9025 | 121.5866 | 121.9757 | 121.843 | 121.9025 | 121.8521 | 122.0306 | -0.34332 | -0.33875
1720.2344 | 122.1085 | -121.788 | 0.12817 | 0.0016785 | 0.015968 | 0.010758 | 0.08901 | -0.011388 | -0.0058383 | 0.0087735 | -0.027466 | 0.16479 | -0.27924 | 0.091553 | -0.009155 | 0.050354 | 0.059509 | 0.21057 | 0.22888 | -0.23346 | 121.5088 | 0.036621 | 121.7606 | 121.8796 | -0.13733 | 121.5546 | 0.10071 | 0.25177 | 121.8475 | 121.9986 | 121.7789 | 121.9528 | 121.7606 | 122.0169 | 121.8384 | 121.5546 | 121.9528 | 121.7606 | 121.8384 | 121.7789 | 122.0169 | -0.40741 | -0.36163
1721.9219 | 122.0306 | -121.7972 | 0.13733 | -0.005951 | 0.015968 | 0.014603 | 0.11272 | -0.0079704 | -0.0079745 | 0.0062099 | 0.004578 | 0.16022 | -0.24719 | 0.07782 | -0.018311 | 0.059509 | -0.013733 | 0.16022 | 0.23804 | -0.20599 | 121.55 | 0.022888 | 121.8018 | 121.875 | -0.15564 | 121.5912 | 0.10071 | 0.25177 | 121.7834 | 121.9574 | 121.7789 | 121.9574 | 121.8018 | 122.0352 | 121.8567 | 121.5912 | 121.9574 | 121.8018 | 121.8567 | 121.7789 | 122.0352 | -0.38452 | -0.34332
1723.6719 | 121.9345 | -121.8109 | 0.16479 | 0.0016785 | 0.015327 | 0.012467 | 0.091787 | -0.0071158 | -0.0060519 | 0.0062099 | 0.091553 | 0.15106 | -0.21515 | 0.19684 | 0.091553 | 0.18768 | -0.1831 | 0.3067 | 0.17853 | -0.18768 | 121.5958 | -0.013733 | 121.9025 | 122.0078 | -0.073242 | 121.6232 | 0.013733 | 0.3067 | 121.6278 | 122.1176 | 121.9025 | 121.962 | 121.9025 | 121.9894 | 121.9986 | 121.6232 | 121.962 | 121.9025 | 121.9986 | 121.9025 | 121.9894 | -0.37994 | -0.35248
1725.4219 | 122.0718 | -121.6461 | 0.2243 | -0.005951 | 0.016182 | 0.010544 | 0.4573 | -0.0088248 | -0.0081881 | 0.0062099 | -0.018311 | 0.18768 | -0.24719 | 0.10986 | 0.009155 | 0.07782 | 0.045776 | 0.23346 | 0.29297 | -0.21515 | 121.3989 | -0.036621 | 121.6278 | 121.756 | -0.21515 | 121.431 | 0.068665 | 0.22888 | 121.6919 | 121.8796 | 121.6553 | 121.8338 | 121.6278 | 121.9391 | 121.7239 | 121.431 | 121.8338 | 121.6278 | 121.7239 | 121.6553 | 121.9391 | -0.4715 | -0.43945
1727.0938 | 121.9711 | -121.8475 | 0.14191 | 0.0016785 | 0.018532 | 0.01204 | 0.092428 | -0.0073294 | -0.0092563 | 0.0079189 | 0.050354 | 0.12817 | -0.25177 | 0.16479 | 0.045776 | 0.10071 | -0.045776 | 0.23346 | 0.19684 | -0.21515 | 121.5958 | -0.013733 | 121.8979 | 122.0123 | -0.096131 | 121.6324 | 0.054931 | 0.30212 | 121.8018 | 122.081 | 121.8933 | 121.9757 | 121.8979 | 122.0444 | 121.9482 | 121.6324 | 121.9757 | 121.8979 | 121.9482 | 121.8933 | 122.0444 | -0.39368 | -0.35706
1728.8438 | 121.9757 | -121.8567 | 0.15564 | 0.0016785 | 0.014046 | 0.016526 | 0.094564 | -0.008184 | -0.0073337 | 0.0083463 | 0.041199 | 0.16479 | -0.24719 | 0.14648 | 0.036621 | 0.10986 | -0.027466 | 0.25177 | 0.21057 | -0.21515 | 121.6095 | 0.009155 | 121.8979 | 122.0032 | -0.11902 | 121.6415 | 0.054931 | 0.28839 | 121.8292 | 122.1085 | 121.8933 | 122.0215 | 121.8979 | 122.0673 | 121.9666 | 121.6415 | 122.0215 | 121.8979 | 121.9666 | 121.8933 | 122.0673 | -0.40283 | -0.37079
1730.5938 | 122.0581 | -121.7972 | 0.12817 | 0.0016785 | 0.013618 | 0.0077673 | 0.083242 | -0.0077566 | -0.0051975 | 0.0085599 | 0.086975 | 0.11902 | -0.20599 | 0.21057 | 0.10986 | 0.20142 | -0.10986 | 0.3479 | 0.18768 | -0.17853 | 121.5912 | -0.009155 | 121.8842 | 122.0078 | -0.018311 | 121.6187 | 0.059509 | 0.29297 | 121.6873 | 122.1451 | 121.907 | 121.9162 | 121.8842 | 121.9849 | 121.9986 | 121.6187 | 121.9162 | 121.8842 | 121.9986 | 121.907 | 121.9849 | -0.33417 | -0.3067
1732.2812 | 121.962 | -121.8246 | 0.16022 | -0.013581 | 0.014687 | 0.012681 | 0.091574 | -0.0073294 | -0.0090427 | 0.0079189 | 0.036621 | 0.14648 | -0.24719 | 0.14648 | 0.041199 | 0.1236 | -0.041199 | 0.26093 | 0.21973 | -0.19684 | 121.5775 | -0.013733 | 121.8613 | 121.9711 | -0.11902 | 121.6278 | 0.05951 | 0.28381 | 121.7834 | 122.0856 | 121.8658 | 121.9711 | 121.8613 | 122.0444 | 121.9482 | 121.6278 | 121.9711 | 121.8613 | 121.9482 | 121.8658 | 122.0444 | -0.40741 | -0.35706
1734.0312 | 121.9986 | -121.7834 | 0.18768 | -0.005951 | 0.01725 | 0.012894 | 0.20543 | -0.0071158 | -0.0090427 | 0.0062099 | 0.027466 | 0.16937 | -0.2243 | 0.10529 | 0 | 0.091553 | -0.018311 | 0.19684 | 0.25177 | -0.19226 | 121.5591 | -0.01831 | 121.8109 | 121.8887 | -0.18768 | 121.5912 | 0.064087 | 0.25177 | 121.7651 | 121.9803 | 121.7834 | 121.9528 | 121.8109 | 122.0352 | 121.875 | 121.5912 | 121.9528 | 121.8109 | 121.875 | 121.7834 | 122.0352 | -0.41199 | -0.37994
1735.7812 | 122.0581 | -121.7972 | 0.10529 | -0.013581 | 0.016609 | 0.0084083 | 0.080252 | -0.007543 | -0.0077609 | 0.0049283 | 0.10071 | 0.14191 | -0.20142 | 0.21057 | 0.13275 | 0.20142 | -0.1236 | 0.35248 | 0.19684 | -0.20599 | 121.5958 | 0.036621 | 121.8979 | 122.0078 | 0.027465 | 121.5912 | 0.091552 | 0.30212 | 121.6736 | 122.1497 | 121.9299 | 121.9391 | 121.8979 | 121.994 | 121.9986 | 121.5912 | 121.9391 | 121.8979 | 121.9986 | 121.9299 | 121.994 | -0.3067 | -0.31128
1737.4531 | 121.9437 | -121.8292 | 0.16937 | 0.0016785 | 0.017891 | 0.013749 | 0.093069 | -0.0062614 | -0.0084017 | 0.0077053 | 0.041199 | 0.13733 | -0.25635 | 0.11902 | 0.018311 | 0.09613 | -0.036621 | 0.21515 | 0.2243 | -0.21515 | 121.5729 | -0.032044 | 121.8704 | 121.9482 | -0.15106 | 121.6141 | 0.054931 | 0.29755 | 121.7926 | 122.0444 | 121.8475 | 121.9666 | 121.8704 | 122.0535 | 121.9254 | 121.6141 | 121.9666 | 121.8704 | 121.9254 | 121.8475 | 122.0535 | -0.42572 | -0.38452
1739.2031 | 122.0947 | -121.7606 | 0.11902 | -0.013581 | 0.014687 | 0.012467 | 0.08132 | -0.0094656 | -0.0041293 | 0.0087735 | 0.050354 | 0.14648 | -0.21057 | 0.13275 | 0.054932 | 0.14191 | -0.10071 | 0.2655 | 0.20142 | -0.20599 | 121.55 | 0.027465 | 121.8109 | 121.8933 | -0.064087 | 121.5546 | 0.082397 | 0.26093 | 121.6599 | 122.0261 | 121.8155 | 121.907 | 121.8109 | 121.962 | 121.9025 | 121.5546 | 121.907 | 121.8109 | 121.9025 | 121.8155 | 121.962 | -0.32959 | -0.32501
1740.8906 | 121.9757 | -121.8292 | 0.13275 | 0.0016785 | 0.015755 | 0.014817 | 0.096701 | -0.0071158 | -0.0062655 | 0.0081325 | 0.09613 | 0.12817 | -0.20142 | 0.19684 | 0.10071 | 0.19684 | -0.19684 | 0.3067 | 0.17853 | -0.1831 | 121.6278 | -0.004577 | 121.9254 | 122.0261 | -0.032043 | 121.6461 | 0.045777 | 0.29755 | 121.6324 | 122.1359 | 121.9299 | 121.9574 | 121.9254 | 122.0078 | 122.0261 | 121.6461 | 121.9574 | 121.9254 | 122.0261 | 121.9299 | 122.0078 | -0.33417 | -0.31586
1742.6406 | 121.9803 | -121.7743 | 0.12817 | -0.005951 | 0.015327 | 0.011399 | 0.086233 | -0.01032 | -0.0054111 | 0.0070645 | 0.082397 | 0.13733 | -0.21057 | 0.20599 | 0.11902 | 0.20142 | -0.14648 | 0.34332 | 0.19684 | -0.16479 | 121.5637 | 0.009155 | 121.8567 | 121.9803 | -0.009155 | 121.6095 | 0.068664 | 0.29297 | 121.6278 | 122.1176 | 121.8933 | 121.9116 | 121.8567 | 121.9711 | 121.9757 | 121.6095 | 121.9116 | 121.8567 | 121.9757 | 121.8933 | 121.9711 | -0.33875 | -0.29297
1744.3906 | 122.0901 | -121.7834 | 0.10071 | -0.005951 | 0.016182 | 0.015885 | 0.089865 | -0.0096794 | -0.0084017 | 0.0055691 | -0.022888 | 0.16937 | -0.25177 | 0.10071 | -0.013733 | 0.050354 | 0.068665 | 0.19226 | 0.24261 | -0.2243 | 121.5317 | 0.068665 | 121.7606 | 121.8842 | -0.11444 | 121.5591 | 0.14191 | 0.22888 | 121.8521 | 121.9757 | 121.7697 | 121.9528 | 121.7606 | 122.0261 | 121.8338 | 121.5591 | 121.9528 | 121.7606 | 121.8338 | 121.7697 | 122.0261 | -0.35248 | -0.32501
1746.1406 | 121.9803 | -121.788 | 0.14648 | 0.0016785 | 0.0149 | 0.013535 | 0.092428 | -0.0071158 | -0.0098971 | 0.0077053 | 0.041199 | 0.16937 | -0.23346 | 0.11902 | -0.004578 | 0.07782 | -0.027466 | 0.19684 | 0.2243 | -0.23346 | 121.5546 | 0.022889 | 121.8292 | 121.907 | -0.15106 | 121.5546 | 0.07782 | 0.27466 | 121.7606 | 121.9849 | 121.7834 | 121.9574 | 121.8292 | 122.0123 | 121.8658 | 121.5546 | 121.9574 | 121.8292 | 121.8658 | 121.7834 | 122.0123 | -0.37994 | -0.37994
1747.875 | 121.962 | -121.8018 | 0.14648 | -0.005951 | 0.013618 | 0.011612 | 0.089651 | -0.007543 | -0.0084017 | 0.0085599 | 0.09613 | 0.11902 | -0.20599 | 0.19684 | 0.10071 | 0.20142 | -0.20142 | 0.31586 | 0.18768 | -0.17853 | 121.5958 | -0.027465 | 121.8979 | 121.9986 | -0.045776 | 121.6232 | 0.041199 | 0.30212 | 121.6003 | 122.1176 | 121.9025 | 121.9208 | 121.8979 | 121.9894 | 122.0032 | 121.6232 | 121.9208 | 121.8979 | 122.0032 | 121.9025 | 121.9894 | -0.35248 | -0.32501
1749.5469 | 122.0627 | -121.5363 | 0.32501 | 0.0016785 | 0.015327 | 0.013108 | 0.77111 | -0.0071158 | -0.0073337 | 0.0074917 | 0.013733 | 0.1831 | -0.24719 | 0.13275 | 0.022888 | 0.09613 | 0.041199 | 0.24719 | 0.36621 | -0.20599 | 121.2891 | -0.14191 | 121.55 | 121.669 | -0.30212 | 121.3303 | 0.041199 | 0.26093 | 121.5775 | 121.7834 | 121.5591 | 121.7194 | 121.55 | 121.9025 | 121.6324 | 121.3303 | 121.7194 | 121.55 | 121.6324 | 121.5591 | 121.9025 | -0.5722 | -0.53101
1751.2344 | 122.0169 | -121.7789 | 0.14191 | -0.02121 | 0.017891 | 0.012894 | 0.092642 | -0.0071158 | -0.0081881 | 0.0081325 | -0.004578 | 0.16022 | -0.25635 | 0.068665 | -0.027466 | 0.059509 | -0.009155 | 0.16022 | 0.21515 | -0.21515 | 121.5225 | 0.01831 | 121.7743 | 121.8475 | -0.16937 | 121.5637 | 0.073242 | 0.25177 | 121.7697 | 121.9391 | 121.7514 | 121.9391 | 121.7743 | 121.994 | 121.8384 | 121.5637 | 121.9391 | 121.7743 | 121.8384 | 121.7514 | 121.994 | -0.39826 | -0.35706
1752.9844 | 122.0169 | -121.7651 | 0.13275 | -0.013581 | 0.019386 | 0.012894 | 0.091147 | -0.0041252 | -0.0066929 | 0.0074917 | -0.004578 | 0.17395 | -0.24261 | 0.073242 | -0.022888 | 0.059509 | -0.009155 | 0.15564 | 0.23804 | -0.20599 | 121.5225 | 0.041199 | 121.7606 | 121.8384 | -0.15564 | 121.5591 | 0.10529 | 0.23804 | 121.756 | 121.9208 | 121.7422 | 121.9391 | 121.7606 | 122.0032 | 121.8246 | 121.5591 | 121.9391 | 121.7606 | 121.8246 | 121.7422 | 122.0032 | -0.37537 | -0.33875
1754.6719 | 122.0764 | -121.7697 | 0.13275 | 0.0016785 | 0.016182 | 0.0096899 | 0.084097 | -0.009893 | -0.0054111 | 0.0068509 | 0.050354 | 0.14191 | -0.21057 | 0.17853 | 0.10986 | 0.18768 | -0.11902 | 0.33875 | 0.19226 | -0.19226 | 121.5591 | 0.009156 | 121.8201 | 121.9482 | -0.022888 | 121.5775 | 0.05951 | 0.26093 | 121.6507 | 122.1085 | 121.8796 | 121.9116 | 121.8201 | 121.962 | 121.9574 | 121.5775 | 121.9116 | 121.8201 | 121.9574 | 121.8796 | 121.962 | -0.34332 | -0.32501
1756.4219 | 122.049 | -121.7606 | 0.10529 | -0.005951 | 0.014259 | 0.0075537 | 0.083883 | -0.010534 | -0.0066929 | 0.0087735 | 0.086975 | 0.14648 | -0.18768 | 0.2243 | 0.1236 | 0.21515 | -0.14648 | 0.36163 | 0.17853 | -0.17853 | 121.5729 | 0.041198 | 121.8475 | 121.9849 | 0.01831 | 121.582 | 0.073242 | 0.27466 | 121.6141 | 122.1222 | 121.8842 | 121.907 | 121.8475 | 121.9391 | 121.9757 | 121.582 | 121.907 | 121.8475 | 121.9757 | 121.8842 | 121.9391 | -0.29297 | -0.28381
1758.1719 | 121.994 | -121.8063 | 0.14191 | 0.0016785 | 0.016609 | 0.017167 | 0.092215 | -0.0079704 | -0.0086155 | 0.0079189 | 0.027466 | 0.14648 | -0.24719 | 0.10529 | -0.013733 | 0.059509 | -0.018311 | 0.20142 | 0.23346 | -0.21515 | 121.5591 | 0.004577 | 121.8338 | 121.9116 | -0.15564 | 121.5912 | 0.091552 | 0.27466 | 121.788 | 122.0078 | 121.7926 | 121.9528 | 121.8338 | 122.0398 | 121.8658 | 121.5912 | 121.9528 | 121.8338 | 121.8658 | 121.7926 | 122.0398 | -0.3891 | -0.35706
1759.8438 | 122.0764 | -121.7651 | 0.11444 | -0.005951 | 0.01255 | 0.0058447 | 0.084311 | -0.011602 | -0.0051975 | 0.0083463 | 0.036621 | 0.15106 | -0.21057 | 0.1831 | 0.10071 | 0.17395 | -0.10529 | 0.31128 | 0.17395 | -0.18768 | 121.5546 | 0.036621 | 121.8018 | 121.9482 | -0.013733 | 121.5775 | 0.059509 | 0.24719 | 121.6599 | 122.0764 | 121.8658 | 121.9162 | 121.8018 | 121.9391 | 121.9391 | 121.5775 | 121.9162 | 121.8018 | 121.9391 | 121.8658 | 121.9391 | -0.32501 | -0.30212
1761.5938 | 122.1039 | -121.8704 | 0.10529 | -0.005951 | 0.014046 | 0.012253 | 0.011465 | -0.009893 | -0.0081881 | 0.0083463 | 0 | 0.16479 | -0.25635 | 0.12817 | 0.018311 | 0.07782 | 0 | 0.23346 | 0.21973 | -0.21515 | 121.6141 | 0.059509 | 121.8704 | 121.9986 | -0.086975 | 121.6553 | 0.11444 | 0.25635 | 121.8704 | 122.1039 | 121.8887 | 122.0352 | 121.8704 | 122.0901 | 121.9482 | 121.6553 | 122.0352 | 121.8704 | 121.9482 | 121.8887 | 122.0901 | -0.36163 | -0.32044
1763.3438 | 122.081 | -121.8979 | 0.10071 | -0.005951 | 0.015755 | 0.016312 | 0.0065518 | -0.008184 | -0.0060519 | 0.0070645 | 0.064087 | 0.10529 | -0.20142 | 0.14648 | 0.068665 | 0.15564 | -0.14648 | 0.27924 | 0.18768 | -0.19684 | 121.6965 | 0.004578 | 121.962 | 122.0444 | -0.032043 | 121.701 | 0.086975 | 0.2655 | 121.7514 | 122.1771 | 121.9666 | 122.0032 | 121.962 | 122.0856 | 122.0535 | 121.701 | 122.0032 | 121.962 | 122.0535 | 121.9666 | 122.0856 | -0.30212 | -0.29755
1765.0312 | 122.0581 | -121.8887 | 0.1236 | -0.013581 | 0.017677 | 0.0066993 | 0.013601 | -0.0079704 | -0.0071201 | 0.0087735 | 0.004578 | 0.17395 | -0.24719 | 0.11902 | 0 | 0.10986 | -0.09613 | 0.19684 | 0.20142 | -0.21515 | 121.6415 | 0.050354 | 121.8933 | 122.0078 | -0.1236 | 121.6736 | 0.07782 | 0.25177 | 121.7926 | 122.0856 | 121.8887 | 122.0627 | 121.8933 | 122.0901 | 121.9986 | 121.6736 | 122.0627 | 121.8933 | 121.9986 | 121.8887 | 122.0901 | -0.37079 | -0.33875
1766.7812 | 122.1634 | -121.8704 | 0.10071 | -0.005951 | 0.015541 | 0.0096899 | 0.0065518 | -0.0073294 | -0.0058383 | 0.0085599 | 0.054932 | 0.13275 | -0.21057 | 0.18768 | 0.086975 | 0.1831 | -0.13275 | 0.31586 | 0.16479 | -0.19684 | 121.6599 | 0.032043 | 121.9254 | 122.0581 | -0.013733 | 121.6736 | 0.064087 | 0.2655 | 121.7377 | 122.1863 | 121.9574 | 122.0032 | 121.9254 | 122.0352 | 122.0535 | 121.6736 | 122.0032 | 121.9254 | 122.0535 | 121.9574 | 122.0352 | -0.31128 | -0.29755
1768.5156 | 122.0901 | -121.9299 | 0.13733 | 0.0016785 | 0.015755 | 0.013321 | 0.015097 | -0.0054068 | -0.010538 | 0.0072781 | 0.027466 | 0.15564 | -0.26093 | 0.10071 | -0.009155 | 0.059509 | -0.032043 | 0.18768 | 0.20142 | -0.21515 | 121.669 | 0.018311 | 121.9574 | 122.0306 | -0.14648 | 121.7148 | 0.064087 | 0.28839 | 121.8979 | 122.1176 | 121.9208 | 122.0856 | 121.9574 | 122.1313 | 121.9894 | 121.7148 | 122.0856 | 121.9574 | 121.9894 | 121.9208 | 122.1313 | -0.39825 | -0.35248
1770.1875 | 122.1268 | -121.8979 | 0.10071 | -0.013581 | 0.015968 | 0.010544 | 0.010824 | -0.005834 | -0.0084017 | 0.0070645 | -0.009155 | 0.16937 | -0.25177 | 0.07782 | -0.013733 | 0.054932 | -0.027466 | 0.16479 | 0.21057 | -0.2243 | 121.6461 | 0.068665 | 121.8887 | 121.9757 | -0.11444 | 121.6736 | 0.10986 | 0.24261 | 121.8704 | 122.0627 | 121.8842 | 122.0673 | 121.8887 | 122.1085 | 121.9528 | 121.6736 | 122.0673 | 121.8887 | 121.9528 | 121.8842 | 122.1085 | -0.35248 | -0.32501
1771.9219 | 122.1222 | -121.9254 | 0.10529 | 0.0016785 | 0.015114 | 0.013535 | 0.013601 | -0.0071158 | -0.0064791 | 0.0081325 | 0.004578 | 0.15106 | -0.25177 | 0.09613 | -0.009155 | 0.07782 | -0.059509 | 0.16479 | 0.18768 | -0.21515 | 121.6736 | 0.045776 | 121.9299 | 122.0215 | -0.11444 | 121.7102 | 0.082397 | 0.25635 | 121.8658 | 122.0901 | 121.9162 | 122.0764 | 121.9299 | 122.113 | 122.0032 | 121.7102 | 122.0764 | 121.9299 | 122.0032 | 121.9162 | 122.113 | -0.35706 | -0.32044
1773.6094 | 122.0993 | -121.9391 | 0.11444 | -0.005951 | 0.014046 | 0.0096899 | 0.0065518 | -0.0088248 | -0.0034885 | 0.0070645 | 0.082397 | 0.10529 | -0.19226 | 0.17853 | 0.10986 | 0.19684 | -0.17853 | 0.31128 | 0.15106 | -0.18768 | 121.7468 | -0.009155 | 122.0215 | 122.1176 | -0.004578 | 121.7514 | 0.036621 | 0.27466 | 121.7606 | 122.2504 | 122.049 | 122.0444 | 122.0215 | 122.0901 | 122.1359 | 121.7514 | 122.0444 | 122.0215 | 122.1359 | 122.049 | 122.0901 | -0.3067 | -0.30212
1775.3438 | 122.1725 | -121.9162 | 0.10071 | -0.005951 | 0.014687 | 0.012253 | 0.0063382 | -0.010107 | -0.0058383 | 0.0047147 | 0.10986 | 0.14648 | -0.20599 | 0.21973 | 0.12817 | 0.21515 | -0.16022 | 0.35248 | 0.16937 | -0.19226 | 121.7102 | 0.045776 | 122.0261 | 122.1359 | 0.027466 | 121.7239 | 0.068665 | 0.31586 | 121.756 | 122.2687 | 122.0444 | 122.0627 | 122.0261 | 122.0856 | 122.1313 | 121.7239 | 122.0627 | 122.0261 | 122.1313 | 122.0444 | 122.0856 | -0.3067 | -0.29297
1777.0781 | 122.1863 | -121.9162 | 0.086975 | -0.02121 | 0.014687 | 0.0086219 | 0.0084744 | -0.0086112 | -0.0039157 | 0.0059963 | 0.073242 | 0.13275 | -0.21057 | 0.19226 | 0.10986 | 0.18768 | -0.15564 | 0.35248 | 0.16022 | -0.18768 | 121.7056 | 0.045776 | 121.9894 | 122.1085 | 0.022888 | 121.7285 | 0.073242 | 0.28381 | 121.7606 | 122.2687 | 122.0261 | 122.049 | 121.9894 | 122.0764 | 122.1039 | 121.7285 | 122.049 | 121.9894 | 122.1039 | 122.0261 | 122.0764 | -0.29755 | -0.27466
1778.7656 | 122.1634 | -121.9437 | 0.11444 | 0.0016785 | 0.013191 | 0.013962 | 0.014242 | -0.007543 | -0.0086155 | 0.0074917 | -0.009155 | 0.15106 | -0.2655 | 0.082397 | -0.022888 | 0.041199 | 0.009155 | 0.17395 | 0.19226 | -0.21515 | 121.6782 | 0.036621 | 121.9345 | 122.0261 | -0.13733 | 121.7285 | 0.07782 | 0.25635 | 121.9528 | 122.1176 | 121.9208 | 122.0947 | 121.9345 | 122.1359 | 121.9849 | 121.7285 | 122.0947 | 121.9345 | 121.9849 | 121.9208 | 122.1359 | -0.37994 | -0.32959
1780.5156 | 122.2366 | -121.9025 | 0.10071 | -0.005951 | 0.016609 | 0.011185 | 0.0095426 | -0.008184 | -0.0073337 | 0.0062099 | -0.018311 | 0.19684 | -0.25635 | 0.086975 | 0.004578 | 0.059509 | 0.041199 | 0.19684 | 0.20142 | -0.22888 | 121.6461 | 0.09613 | 121.8842 | 121.9894 | -0.09613 | 121.6736 | 0.10071 | 0.23804 | 121.9437 | 122.0993 | 121.907 | 122.0993 | 121.8842 | 122.1039 | 121.962 | 121.6736 | 122.0993 | 121.8842 | 121.962 | 121.907 | 122.1039 | -0.35706 | -0.32959
1782.25 | 122.287 | -121.9345 | 0.07782 | 0.009308 | 0.015755 | 0.010758 | 0.0089016 | -0.010107 | -0.0094699 | 0.0057827 | -0.041199 | 0.16937 | -0.25635 | 0.091553 | -0.013733 | 0.036621 | 0.059509 | 0.19684 | 0.21515 | -0.24719 | 121.6782 | 0.091553 | 121.8933 | 122.0261 | -0.091553 | 121.6873 | 0.13733 | 0.21515 | 121.994 | 122.1313 | 121.9208 | 122.1039 | 121.8933 | 122.1497 | 121.9711 | 121.6873 | 122.1039 | 121.8933 | 121.9711 | 121.9208 | 122.1497 | -0.33417 | -0.32501
1783.9219 | 122.2412 | -121.9025 | 0.082397 | -0.013581 | 0.014687 | 0.010972 | 0.0063382 | -0.0083976 | -0.0060519 | 0.0079189 | 0.032043 | 0.14191 | -0.21057 | 0.13275 | 0.064087 | 0.12817 | -0.11444 | 0.24719 | 0.17395 | -0.17395 | 121.6919 | 0.05951 | 121.9345 | 122.0352 | -0.01831 | 121.7285 | 0.091553 | 0.24261 | 121.788 | 122.1497 | 121.9666 | 122.0444 | 121.9345 | 122.0764 | 122.0306 | 121.7285 | 122.0444 | 121.9345 | 122.0306 | 121.9666 | 122.0764 | -0.29297 | -0.25635
1785.6719 | 122.2229 | -121.9254 | 0.09613 | -0.013581 | 0.016396 | 0.0081947 | 0.006979 | -0.0079704 | -0.0071201 | 0.0057827 | 0.091553 | 0.13733 | -0.20599 | 0.20142 | 0.10986 | 0.18768 | -0.15106 | 0.3479 | 0.15564 | -0.18768 | 121.7194 | 0.041199 | 122.0169 | 122.1268 | 0.013733 | 121.7377 | 0.05951 | 0.29755 | 121.7743 | 122.2733 | 122.0352 | 122.0627 | 122.0169 | 122.081 | 122.113 | 121.7377 | 122.0627 | 122.0169 | 122.113 | 122.0352 | 122.081 | -0.30212 | -0.28381
1787.4219 | 122.1542 | -122.0032 | 0.11444 | 0.0016785 | 0.013191 | 0.013749 | 0.013601 | -0.008184 | -0.0066929 | 0.0079189 | 0 | 0.15106 | -0.24261 | 0.09613 | -0.013733 | 0.082397 | -0.082397 | 0.19226 | 0.1831 | -0.21515 | 121.7606 | 0.036621 | 122.0032 | 122.0993 | -0.12817 | 121.788 | 0.068664 | 0.24261 | 121.9208 | 122.1954 | 121.9894 | 122.1542 | 122.0032 | 122.1863 | 122.0856 | 121.788 | 122.1542 | 122.0032 | 122.0856 | 121.9894 | 122.1863 | -0.35706 | -0.32959
1789.1094 | 122.2092 | -121.9528 | 0.11444 | -0.005951 | 0.013618 | 0.012253 | 0.0078336 | -0.01032 | -0.0081881 | 0.0079189 | 0.073242 | 0.10986 | -0.19684 | 0.21515 | 0.10529 | 0.19226 | -0.12817 | 0.35706 | 0.19226 | -0.19226 | 121.756 | -0.004578 | 122.0261 | 122.168 | -0.009155 | 121.7606 | 0.07782 | 0.27008 | 121.8246 | 122.3099 | 122.0581 | 122.0627 | 122.0261 | 122.1451 | 122.1451 | 121.7606 | 122.0627 | 122.0261 | 122.1451 | 122.0581 | 122.1451 | -0.31128 | -0.3067
1790.875 | 122.1817 | -121.962 | 0.1236 | -0.005951 | 0.015755 | 0.015244 | 0.012106 | -0.0071158 | -0.0045565 | 0.0083463 | -0.009155 | 0.16022 | -0.2655 | 0.10071 | -0.009155 | 0.073242 | -0.059509 | 0.17395 | 0.21973 | -0.20142 | 121.6965 | 0.036621 | 121.9528 | 122.0627 | -0.13275 | 121.7606 | 0.096131 | 0.25635 | 121.9025 | 122.1359 | 121.9528 | 122.1222 | 121.9528 | 122.1817 | 122.0352 | 121.7606 | 122.1222 | 121.9528 | 122.0352 | 121.9528 | 122.1817 | -0.3891 | -0.32501
1792.6094 | 122.2366 | -121.962 | 0.086975 | -0.005951 | 0.017464 | 0.010544 | 0.0067654 | -0.010534 | -0.0060519 | 0.0045011 | 0.086975 | 0.12817 | -0.20599 | 0.21057 | 0.13275 | 0.19226 | -0.14648 | 0.36163 | 0.16937 | -0.21057 | 121.756 | 0.041199 | 122.0489 | 122.1725 | 0.045776 | 121.7514 | 0.082398 | 0.29297 | 121.8155 | 122.3236 | 122.0947 | 122.0901 | 122.0489 | 122.1313 | 122.1542 | 121.7514 | 122.0901 | 122.0489 | 122.1542 | 122.0947 | 122.1313 | -0.29297 | -0.29755
1794.2969 | 122.1863 | -121.9894 | 0.10529 | 0.009308 | 0.018532 | 0.011185 | 0.014456 | -0.0039114 | -0.0049839 | 0.0070645 | 0.009155 | 0.17395 | -0.23346 | 0.10071 | 0.013733 | 0.09613 | -0.09613 | 0.21973 | 0.19226 | -0.21515 | 121.756 | 0.068664 | 121.9986 | 122.0901 | -0.091553 | 121.7743 | 0.086975 | 0.24261 | 121.8933 | 122.2092 | 122.0032 | 122.1634 | 121.9986 | 122.1817 | 122.0856 | 121.7743 | 122.1634 | 121.9986 | 122.0856 | 122.0032 | 122.1817 | -0.33875 | -0.32044
1796.0469 | 122.1542 | -121.9803 | 0.13275 | 0.0016785 | 0.015541 | 0.013321 | 0.0097562 | -0.0088248 | -0.0069065 | 0.0059963 | 0.09613 | 0.13733 | -0.21057 | 0.18768 | 0.10986 | 0.20142 | -0.18768 | 0.32044 | 0.16937 | -0.18768 | 121.7697 | 0.004578 | 122.0764 | 122.168 | -0.022888 | 121.7926 | 0.036622 | 0.3067 | 121.7926 | 122.3007 | 122.0901 | 122.1176 | 122.0764 | 122.1497 | 122.1817 | 121.7926 | 122.1176 | 122.0764 | 122.1817 | 122.0901 | 122.1497 | -0.34332 | -0.32043
1797.7344 | 122.2916 | -121.962 | 0.086975 | -0.005951 | 0.016396 | 0.013962 | 0.0082608 | -0.010107 | -0.0047703 | 0.0077053 | 0.027466 | 0.13275 | -0.2243 | 0.12817 | 0.041199 | 0.13275 | -0.09613 | 0.25635 | 0.1831 | -0.19684 | 121.7377 | 0.045776 | 121.9894 | 122.0901 | -0.045776 | 121.7651 | 0.09613 | 0.25177 | 121.8658 | 122.2183 | 122.0032 | 122.0947 | 121.9894 | 122.1451 | 122.0947 | 121.7651 | 122.0947 | 121.9894 | 122.0947 | 122.0032 | 122.1451 | -0.31128 | -0.28381
1799.4844 | 122.1634 | -121.9757 | 0.1236 | -0.005951 | 0.015968 | 0.013321 | 0.011892 | -0.0094656 | -0.0062655 | 0.0096279 | 0.036621 | 0.14648 | -0.2243 | 0.1831 | 0.064087 | 0.15106 | -0.15564 | 0.27466 | 0.16937 | -0.19226 | 121.7514 | 0.022888 | 122.0123 | 122.1588 | -0.059509 | 121.7834 | 0.045777 | 0.26093 | 121.8201 | 122.2504 | 122.0398 | 122.1222 | 122.0123 | 122.1451 | 122.1268 | 121.7834 | 122.1222 | 122.0123 | 122.1268 | 122.0398 | 122.1451 | -0.3479 | -0.31586
1801.1562 | 122.3007 | -121.9574 | 0.07782 | 0.0016785 | 0.015114 | 0.0066993 | 0.00762 | -0.011816 | -0.0064791 | 0.0051419 | 0.027466 | 0.13275 | -0.23346 | 0.15106 | 0.064087 | 0.14648 | -0.09613 | 0.27008 | 0.16479 | -0.20599 | 121.7239 | 0.054931 | 121.9849 | 122.1085 | -0.013733 | 121.7514 | 0.086975 | 0.26093 | 121.8613 | 122.2275 | 122.0215 | 122.0901 | 121.9849 | 122.1222 | 122.1039 | 121.7514 | 122.0901 | 121.9849 | 122.1039 | 122.0215 | 122.1222 | -0.31128 | -0.28381
1802.9062 | 122.3099 | -121.9666 | 0.10071 | -0.013581 | 0.015968 | 0.012681 | 0.013174 | -0.010747 | -0.0049839 | 0.0079189 | -0.018311 | 0.16937 | -0.27008 | 0.09613 | 0.004578 | 0.036621 | 0.054932 | 0.19226 | 0.24719 | -0.22888 | 121.6965 | 0.068665 | 121.9482 | 122.0627 | -0.09613 | 121.7377 | 0.14648 | 0.25177 | 122.0215 | 122.1588 | 121.9711 | 122.1359 | 121.9482 | 122.2137 | 122.0032 | 121.7377 | 122.1359 | 121.9482 | 122.0032 | 121.9711 | 122.2137 | -0.37079 | -0.32959
1804.5938 | 122.1863 | -121.9849 | 0.1236 | -0.005951 | 0.017464 | 0.013962 | 0.011892 | -0.005834 | -0.0075473 | 0.0083463 | 0.013733 | 0.15564 | -0.23804 | 0.10986 | 0.018311 | 0.10071 | -0.10529 | 0.2243 | 0.19226 | -0.19684 | 121.7468 | 0.032044 | 121.9986 | 122.0947 | -0.10528 | 121.788 | 0.068665 | 0.25177 | 121.8796 | 122.2092 | 122.0032 | 122.1405 | 121.9986 | 122.1771 | 122.0856 | 121.788 | 122.1405 | 121.9986 | 122.0856 | 122.0032 | 122.1771 | -0.36163 | -0.32043
1806.3438 | 122.1451 | -122.0261 | 0.12817 | -0.005951 | 0.017464 | 0.016099 | 0.011892 | -0.006475 | -0.0051975 | 0.0070645 | 0.10071 | 0.1236 | -0.20599 | 0.21973 | 0.10071 | 0.1831 | -0.19684 | 0.30212 | 0.17395 | -0.18768 | 121.8201 | -0.004578 | 122.1268 | 122.2458 | -0.027466 | 121.8384 | 0.045776 | 0.3067 | 121.8292 | 122.3282 | 122.1268 | 122.1497 | 122.1268 | 122.2 | 122.2092 | 121.8384 | 122.1497 | 122.1268 | 122.2092 | 122.1268 | 122.2 | -0.33417 | -0.31586
1808.0938 | 122.168 | -122.0261 | 0.11444 | -0.005951 | 0.018532 | 0.010972 | 0.012533 | -0.0071158 | -0.0062655 | 0.0074917 | 0.10986 | 0.11902 | -0.18768 | 0.20599 | 0.10529 | 0.19684 | -0.20599 | 0.30212 | 0.17395 | -0.1831 | 121.8384 | 0.004578 | 122.1359 | 122.2321 | -0.009155 | 121.843 | 0.059509 | 0.29755 | 121.8201 | 122.3282 | 122.1313 | 122.1451 | 122.1359 | 122.2 | 122.2229 | 121.843 | 122.1451 | 122.1359 | 122.2229 | 122.1313 | 122.2 | -0.30212 | -0.29755
1809.8438 | 122.2824 | -122.0078 | 0.10071 | 0.0016785 | 0.015541 | 0.017594 | 0.011892 | -0.0083976 | -0.0086155 | 0.0074917 | 0 | 0.17853 | -0.26093 | 0.1236 | 0.022888 | 0.073242 | 0.004578 | 0.2243 | 0.2243 | -0.2243 | 121.7468 | 0.07782 | 122.0078 | 122.1313 | -0.07782 | 121.7834 | 0.1236 | 0.26093 | 122.0123 | 122.2321 | 122.0306 | 122.1863 | 122.0078 | 122.2321 | 122.081 | 121.7834 | 122.1863 | 122.0078 | 122.081 | 122.0306 | 122.2321 | -0.36163 | -0.32501
1811.5781 | 122.1909 | -122.0718 | 0.11444 | -0.005951 | 0.017036 | 0.010331 | 0.012106 | -0.0069022 | -0.0069065 | 0.0068509 | 0.045776 | 0.14648 | -0.25177 | 0.14191 | 0.036621 | 0.09613 | -0.041199 | 0.22888 | 0.20599 | -0.20142 | 121.8201 | 0.032043 | 122.1176 | 122.2137 | -0.07782 | 121.8704 | 0.091553 | 0.29755 | 122.0306 | 122.3007 | 122.1085 | 122.2183 | 122.1176 | 122.2778 | 122.168 | 121.8704 | 122.2183 | 122.1176 | 122.168 | 122.1085 | 122.2778 | -0.36621 | -0.31586
1813.2656 | 122.319 | -121.9849 | 0.07782 | -0.013581 | 0.014687 | 0.0073401 | 0.0046292 | -0.0060478 | -0.0051975 | 0.0070645 | 0.032043 | 0.14191 | -0.19684 | 0.12817 | 0.059509 | 0.14191 | -0.10071 | 0.26093 | 0.20142 | -0.20599 | 121.788 | 0.064087 | 122.0169 | 122.113 | -0.018311 | 121.7789 | 0.1236 | 0.22888 | 121.8842 | 122.2458 | 122.0444 | 122.1268 | 122.0169 | 122.1863 | 122.1268 | 121.7789 | 122.1268 | 122.0169 | 122.1268 | 122.0444 | 122.1863 | -0.27466 | -0.28381
1815.0156 | 122.3145 | -121.9757 | 0.10071 | 0.0016785 | 0.0149 | 0.014817 | 0.0056974 | -0.0088248 | -0.0054111 | 0.0074917 | 0.027466 | 0.14648 | -0.23346 | 0.16937 | 0.07782 | 0.15564 | -0.11444 | 0.29755 | 0.1831 | -0.20599 | 121.7422 | 0.045776 | 122.0032 | 122.1451 | -0.022888 | 121.7697 | 0.082397 | 0.26093 | 121.8613 | 122.2733 | 122.0535 | 122.1222 | 122.0032 | 122.1588 | 122.1313 | 121.7697 | 122.1222 | 122.0032 | 122.1313 | 122.0535 | 122.1588 | -0.33417 | -0.3067
1816.7031 | 122.287 | -122.0352 | 0.086975 | -0.005951 | 0.013832 | 0.012681 | 0.0082608 | -0.0086112 | -0.0062655 | 0.0072781 | 0.073242 | 0.11902 | -0.2243 | 0.20142 | 0.09613 | 0.1831 | -0.10071 | 0.34332 | 0.17395 | -0.18768 | 121.8109 | 0.032044 | 122.1085 | 122.2366 | 0.009155 | 121.8475 | 0.086975 | 0.29755 | 121.9345 | 122.3785 | 122.1313 | 122.1542 | 122.1085 | 122.2092 | 122.2183 | 121.8475 | 122.1542 | 122.1085 | 122.2183 | 122.1313 | 122.2092 | -0.31128 | -0.27466
1818.4531 | 122.2137 | -122.049 | 0.10986 | 0.0016785 | 0.014473 | 0.013321 | 0.011038 | -0.0083976 | -0.0092563 | 0.0087735 | 0.086975 | 0.13275 | -0.21057 | 0.20599 | 0.10071 | 0.17853 | -0.19684 | 0.30212 | 0.16479 | -0.18768 | 121.8384 | 0.022888 | 122.1359 | 122.2549 | -0.009155 | 121.8613 | 0.054932 | 0.29755 | 121.8521 | 122.3511 | 122.1497 | 122.1817 | 122.1359 | 122.2137 | 122.2275 | 121.8613 | 122.1817 | 122.1359 | 122.2275 | 122.1497 | 122.2137 | -0.32043 | -0.29755
1820.1406 | 122.2229 | -122.0673 | 0.12817 | -0.005951 | 0.017036 | 0.011612 | 0.01232 | -0.0079704 | -0.0079745 | 0.0081325 | 0.041199 | 0.16022 | -0.23804 | 0.15564 | 0.022888 | 0.09613 | -0.045776 | 0.24261 | 0.21057 | -0.23346 | 121.8292 | 0.032043 | 122.1085 | 122.2229 | -0.10529 | 121.8338 | 0.082397 | 0.27924 | 122.0215 | 122.3099 | 122.0901 | 122.2275 | 122.1085 | 122.2778 | 122.1634 | 121.8338 | 122.2275 | 122.1085 | 122.1634 | 122.0901 | 122.2778 | -0.36621 | -0.36163
1821.8906 | 122.3328 | -122.0032 | 0.082397 | -0.013581 | 0.015114 | 0.010544 | 0.0056974 | -0.0071158 | -0.0073337 | 0.0074917 | 0.041199 | 0.13733 | -0.21057 | 0.16479 | 0.068665 | 0.15564 | -0.11444 | 0.3067 | 0.18768 | -0.20599 | 121.7926 | 0.054932 | 122.0444 | 122.168 | -0.013732 | 121.7972 | 0.10529 | 0.25177 | 121.8887 | 122.3099 | 122.0718 | 122.1405 | 122.0444 | 122.1909 | 122.1588 | 121.7972 | 122.1405 | 122.0444 | 122.1588 | 122.0718 | 122.1909 | -0.29297 | -0.28839
1823.6406 | 122.2137 | -122.0947 | 0.11902 | 0.0016785 | 0.015327 | 0.012894 | 0.014669 | -0.0056204 | -0.0075473 | 0.0083463 | 0.036621 | 0.14648 | -0.24261 | 0.14191 | 0.027466 | 0.073242 | -0.036621 | 0.2243 | 0.20142 | -0.2243 | 121.8521 | 0.027465 | 122.1313 | 122.2366 | -0.091553 | 121.8704 | 0.082397 | 0.27924 | 122.0581 | 122.319 | 122.1222 | 122.2412 | 122.1313 | 122.2961 | 122.168 | 121.8704 | 122.2412 | 122.1313 | 122.168 | 122.1222 | 122.2961 | -0.36163 | -0.34332
1825.3906 | 122.2961 | -122.0352 | 0.09613 | 0.0016785 | 0.015541 | 0.010972 | 0.0061246 | -0.009252 | -0.0049839 | 0.0081325 | 0.09613 | 0.13275 | -0.21057 | 0.21973 | 0.10986 | 0.20142 | -0.14191 | 0.34332 | 0.17395 | -0.1831 | 121.8246 | 0.036621 | 122.1313 | 122.2549 | 0.013733 | 121.8521 | 0.07782 | 0.3067 | 121.8933 | 122.3785 | 122.1451 | 122.168 | 122.1313 | 122.2092 | 122.2366 | 121.8521 | 122.168 | 122.1313 | 122.2366 | 122.1451 | 122.2092 | -0.3067 | -0.27924
1827.125 | 122.2824 | -122.0627 | 0.10986 | -0.005951 | 0.014473 | 0.010117 | 0.013601 | -0.0062614 | -0.0081881 | 0.0074917 | 0.022888 | 0.15564 | -0.24719 | 0.14648 | 0.032043 | 0.10529 | -0.009155 | 0.25177 | 0.21973 | -0.2243 | 121.8155 | 0.045777 | 122.0856 | 122.2092 | -0.07782 | 121.8384 | 0.10986 | 0.27008 | 122.0535 | 122.3145 | 122.0947 | 122.2183 | 122.0856 | 122.2824 | 122.168 | 121.8384 | 122.2183 | 122.0856 | 122.168 | 122.0947 | 122.2824 | -0.35706 | -0.33417
1828.8594 | 122.2458 | -122.0764 | 0.10986 | -0.005951 | 0.016396 | 0.013108 | 0.010397 | -0.0056204 | -0.0071201 | 0.0079189 | -0.004578 | 0.16937 | -0.25635 | 0.11444 | 0 | 0.086975 | -0.086975 | 0.19226 | 0.19684 | -0.21057 | 121.8201 | 0.05951 | 122.0718 | 122.1909 | -0.10986 | 121.8658 | 0.086975 | 0.25177 | 121.9894 | 122.2687 | 122.0764 | 122.2458 | 122.0718 | 122.2733 | 122.1634 | 121.8658 | 122.2458 | 122.0718 | 122.1634 | 122.0764 | 122.2733 | -0.36621 | -0.32043
1830.5469 | 122.2458 | -122.0718 | 0.10529 | 0.0016785 | 0.017036 | 0.0094763 | 0.011892 | -0.0066886 | -0.0064791 | 0.0089871 | -0.013733 | 0.16022 | -0.25635 | 0.09613 | 0.022888 | 0.09613 | -0.07782 | 0.20142 | 0.20599 | -0.18768 | 121.8155 | 0.054931 | 122.0581 | 122.168 | -0.082398 | 121.8842 | 0.10071 | 0.24262 | 121.994 | 122.2733 | 122.0947 | 122.2321 | 122.0581 | 122.2778 | 122.168 | 121.8842 | 122.2321 | 122.0581 | 122.168 | 122.0947 | 122.2778 | -0.36163 | -0.29297
1832.2812 | 122.2641 | -122.0856 | 0.10529 | -0.005951 | 0.016823 | 0.017808 | 0.011679 | -0.0073294 | -0.0079745 | 0.0072781 | 0.022888 | 0.14648 | -0.26093 | 0.14191 | 0.050354 | 0.10071 | -0.022888 | 0.23804 | 0.19684 | -0.22888 | 121.8246 | 0.041198 | 122.1085 | 122.2275 | -0.054932 | 121.8567 | 0.091552 | 0.28381 | 122.0627 | 122.3236 | 122.1359 | 122.2321 | 122.1085 | 122.2824 | 122.1863 | 121.8567 | 122.2321 | 122.1085 | 122.1863 | 122.1359 | 122.2824 | -0.36621 | -0.33417
1834.0312 | 122.2961 | -122.0581 | 0.10986 | -0.005951 | 0.016823 | 0.015671 | 0.011892 | -0.0066886 | -0.0086155 | 0.0092007 | -0.032043 | 0.16937 | -0.24719 | 0.064087 | -0.018311 | 0.068665 | -0.009155 | 0.16022 | 0.21973 | -0.20599 | 121.8109 | 0.05951 | 122.0261 | 122.1222 | -0.12817 | 121.8521 | 0.10986 | 0.21515 | 122.0489 | 122.2183 | 122.0398 | 122.2275 | 122.0261 | 122.2778 | 122.1268 | 121.8521 | 122.2275 | 122.0261 | 122.1268 | 122.0398 | 122.2778 | -0.35706 | -0.31586
1835.7188 | 122.2321 | -122.0993 | 0.15106 | 0.0016785 | 0.014687 | 0.012467 | 0.0095426 | -0.005834 | -0.0071201 | 0.0066373 | 0.054932 | 0.15106 | -0.26093 | 0.13733 | 0.045776 | 0.10071 | -0.050354 | 0.25177 | 0.18768 | -0.21973 | 121.8384 | 0 | 122.1542 | 122.2366 | -0.10529 | 121.8796 | 0.036621 | 0.31586 | 122.049 | 122.3511 | 122.1451 | 122.2504 | 122.1542 | 122.287 | 122.2 | 121.8796 | 122.2504 | 122.1542 | 122.2 | 122.1451 | 122.287 | -0.41199 | -0.37079
1837.4688 | 122.2458 | -122.0993 | 0.1236 | -0.013581 | 0.015327 | 0.011399 | 0.012106 | -0.004766 | -0.0098971 | 0.0070645 | 0.054932 | 0.14648 | -0.25177 | 0.14648 | 0.036621 | 0.10986 | -0.041199 | 0.24261 | 0.21515 | -0.21057 | 121.8475 | 0.022888 | 122.1542 | 122.2458 | -0.086975 | 121.8887 | 0.091553 | 0.3067 | 122.0581 | 122.3419 | 122.1359 | 122.2458 | 122.1542 | 122.3145 | 122.2092 | 121.8887 | 122.2458 | 122.1542 | 122.2092 | 122.1359 | 122.3145 | -0.37537 | -0.33417
1839.1562 | 122.2412 | -122.0947 | 0.13275 | -0.02121 | 0.017677 | 0.010972 | 0.0082608 | -0.0060478 | -0.0058383 | 0.0066373 | 0.10071 | 0.11444 | -0.19684 | 0.17395 | 0.10071 | 0.19684 | -0.1831 | 0.29297 | 0.17395 | -0.19684 | 121.8979 | -0.01831 | 122.1954 | 122.2687 | -0.032043 | 121.8979 | 0.041199 | 0.29755 | 121.9116 | 122.3877 | 122.1954 | 122.2092 | 122.1954 | 122.2687 | 122.2916 | 121.8979 | 122.2092 | 122.1954 | 122.2916 | 122.1954 | 122.2687 | -0.32959 | -0.32959
1840.9219 | 122.3465 | -122.0718 | 0.086975 | 0.0016785 | 0.014473 | 0.0090491 | 0.0065518 | -0.0083976 | -0.0064791 | 0.0070645 | 0.082397 | 0.13275 | -0.19684 | 0.17853 | 0.09613 | 0.16937 | -0.073242 | 0.32959 | 0.17395 | -0.19684 | 121.875 | 0.045776 | 122.1542 | 122.2504 | 0.009155 | 121.875 | 0.086975 | 0.27924 | 121.9986 | 122.4014 | 122.168 | 122.2046 | 122.1542 | 122.2458 | 122.2412 | 121.875 | 122.2046 | 122.1542 | 122.2412 | 122.168 | 122.2458 | -0.28381 | -0.28381
1842.6562 | 122.3099 | -122.0993 | 0.10986 | 0.0016785 | 0.015541 | 0.015458 | 0.012106 | -0.0069022 | -0.0075473 | 0.0079189 | -0.013733 | 0.16937 | -0.26093 | 0.073242 | -0.032043 | 0.045776 | -0.018311 | 0.15564 | 0.19684 | -0.21057 | 121.8384 | 0.05951 | 122.0856 | 122.1725 | -0.14191 | 121.8887 | 0.086975 | 0.24719 | 122.081 | 122.2549 | 122.0673 | 122.2687 | 122.0856 | 122.2961 | 122.1451 | 121.8887 | 122.2687 | 122.0856 | 122.1451 | 122.0673 | 122.2961 | -0.37079 | -0.32043
1844.4062 | 122.374 | -122.081 | 0.086975 | 0.0016785 | 0.015755 | 0.013962 | 0.006979 | -0.0094656 | -0.0066929 | 0.0055691 | 0.045776 | 0.13733 | -0.21515 | 0.12817 | 0.041199 | 0.10529 | 0.004578 | 0.24261 | 0.20142 | -0.21515 | 121.8658 | 0.050354 | 122.1268 | 122.2092 | -0.045776 | 121.8658 | 0.11444 | 0.26093 | 122.0856 | 122.3236 | 122.1222 | 122.2183 | 122.1268 | 122.2824 | 122.1863 | 121.8658 | 122.2183 | 122.1268 | 122.1863 | 122.1222 | 122.2824 | -0.30212 | -0.30212
1846.0781 | 122.2321 | -122.1085 | 0.13275 | -0.013581 | 0.016396 | 0.0088355 | 0.010183 | -0.0066886 | -0.0066929 | 0.0074917 | 0.091553 | 0.12817 | -0.18768 | 0.18768 | 0.10529 | 0.19226 | -0.20142 | 0.3067 | 0.17853 | -0.17853 | 121.9208 | -0.004577 | 122.2 | 122.2961 | -0.027465 | 121.9299 | 0.045777 | 0.27924 | 121.907 | 122.4152 | 122.2137 | 122.2366 | 122.2 | 122.287 | 122.3007 | 121.9299 | 122.2366 | 122.2 | 122.3007 | 122.2137 | 122.287 | -0.32043 | -0.31128
1847.8125 | 122.2687 | -122.1085 | 0.11902 | -0.005951 | 0.012978 | 0.014603 | 0.0095426 | -0.0060478 | -0.0064791 | 0.0066373 | 0.09613 | 0.1236 | -0.20599 | 0.20142 | 0.10071 | 0.19226 | -0.20599 | 0.31586 | 0.14648 | -0.17853 | 121.9025 | 0.004577 | 122.2046 | 122.3099 | -0.018311 | 121.9299 | 0.027465 | 0.30212 | 121.9025 | 122.4243 | 122.2092 | 122.2321 | 122.2046 | 122.2549 | 122.3007 | 121.9299 | 122.2321 | 122.2046 | 122.3007 | 122.2092 | 122.2549 | -0.32501 | -0.29755
1849.5625 | 122.3785 | -122.0627 | 0.09613 | -0.005951 | 0.015327 | 0.0092627 | 0.010397 | -0.009252 | -0.0064791 | 0.0074917 | -0.032043 | 0.16479 | -0.26093 | 0.091553 | -0.013733 | 0.059509 | 0.032043 | 0.21057 | 0.20599 | -0.2243 | 121.8018 | 0.068665 | 122.0306 | 122.1542 | -0.10986 | 121.8384 | 0.10986 | 0.22888 | 122.0947 | 122.2733 | 122.049 | 122.2275 | 122.0306 | 122.2687 | 122.1222 | 121.8384 | 122.2275 | 122.0306 | 122.1222 | 122.049 | 122.2687 | -0.35706 | -0.32043
1851.25 | 122.2824 | -122.113 | 0.09613 | -0.005951 | 0.016396 | 0.01204 | 0.012747 | -0.0066886 | -0.010538 | 0.0057827 | 0.045776 | 0.16022 | -0.25177 | 0.15564 | 0.045776 | 0.10529 | -0.041199 | 0.27008 | 0.20142 | -0.21973 | 121.8613 | 0.064087 | 122.1588 | 122.2687 | -0.050354 | 121.8933 | 0.10529 | 0.29755 | 122.0718 | 122.3831 | 122.1588 | 122.2733 | 122.1588 | 122.3145 | 122.2183 | 121.8933 | 122.2733 | 122.1588 | 122.2183 | 122.1588 | 122.3145 | -0.3479 | -0.31586
1852.9844 | 122.2687 | -122.1039 | 0.11444 | 0.016937 | 0.019386 | 0.015458 | 0.01232 | -0.007543 | -0.0084017 | 0.0062099 | 0.050354 | 0.16022 | -0.23804 | 0.10529 | 0.018311 | 0.073242 | -0.032043 | 0.22888 | 0.20142 | -0.21973 | 121.8658 | 0.045776 | 122.1542 | 122.2092 | -0.09613 | 121.8842 | 0.086975 | 0.28839 | 122.0718 | 122.3328 | 122.1222 | 122.2641 | 122.1542 | 122.3053 | 122.1771 | 121.8842 | 122.2641 | 122.1542 | 122.1771 | 122.1222 | 122.3053 | -0.35248 | -0.33417
1854.7344 | 122.3602 | -122.0764 | 0.10529 | -0.02121 | 0.018105 | 0.012681 | 0.0033474 | -0.0094656 | -0.0060519 | 0.0072781 | 0.091553 | 0.13733 | -0.20599 | 0.20599 | 0.12817 | 0.20142 | -0.15564 | 0.36163 | 0.17395 | -0.20599 | 121.8704 | 0.032043 | 122.168 | 122.2824 | 0.022888 | 121.8704 | 0.068664 | 0.29755 | 121.9208 | 122.438 | 122.2046 | 122.2137 | 122.168 | 122.2504 | 122.2778 | 121.8704 | 122.2137 | 122.168 | 122.2778 | 122.2046 | 122.2504 | -0.31128 | -0.31128
1856.4688 | 122.3694 | -122.1313 | 0.10529 | 0.0016785 | 0.015968 | 0.010117 | 0.0061246 | -0.009893 | -0.0047703 | 0.0059963 | 0.086975 | 0.1236 | -0.21973 | 0.20599 | 0.10071 | 0.1831 | -0.11444 | 0.33875 | 0.16937 | -0.21973 | 121.9116 | 0.01831 | 122.2183 | 122.3373 | -0.004578 | 121.9116 | 0.064087 | 0.3067 | 122.0169 | 122.4701 | 122.2321 | 122.2549 | 122.2183 | 122.3007 | 122.3145 | 121.9116 | 122.2549 | 122.2183 | 122.3145 | 122.2321 | 122.3007 | -0.32501 | -0.32501
1858.1406 | 122.3328 | -122.1176 | 0.11444 | -0.005951 | 0.015755 | 0.012681 | 0.013601 | -0.0066886 | -0.0086155 | 0.0062099 | -0.036621 | 0.16479 | -0.25635 | 0.091553 | -0.027466 | 0.045776 | -0.009155 | 0.15564 | 0.21973 | -0.23346 | 121.8613 | 0.050354 | 122.081 | 122.2092 | -0.14191 | 121.8842 | 0.10529 | 0.21973 | 122.1085 | 122.2733 | 122.0901 | 122.2824 | 122.081 | 122.3373 | 122.1634 | 121.8842 | 122.2824 | 122.081 | 122.1634 | 122.0901 | 122.3373 | -0.37079 | -0.3479
1859.8906 | 122.3831 | -122.0947 | 0.10529 | -0.005951 | 0.0149 | 0.0090491 | 0.0050564 | -0.0088248 | -0.0051975 | 0.0064237 | 0.07782 | 0.11902 | -0.20142 | 0.18768 | 0.091553 | 0.15564 | -0.068665 | 0.32044 | 0.1831 | -0.19684 | 121.8933 | 0.013733 | 122.1725 | 122.2824 | -0.013733 | 121.8979 | 0.077819 | 0.27924 | 122.0261 | 122.4152 | 122.1863 | 122.2137 | 122.1725 | 122.2778 | 122.2504 | 121.8979 | 122.2137 | 122.1725 | 122.2504 | 122.1863 | 122.2778 | -0.3067 | -0.30212
1861.6406 | 122.3145 | -122.1359 | 0.10529 | 0.0016785 | 0.016609 | 0.016953 | 0.011892 | -0.006475 | -0.0092563 | 0.0051419 | -0.027466 | 0.14648 | -0.25635 | 0.068665 | -0.041199 | 0.027466 | 0.018311 | 0.17395 | 0.23346 | -0.22888 | 121.8796 | 0.041198 | 122.1085 | 122.2046 | -0.14649 | 121.907 | 0.12817 | 0.22888 | 122.1542 | 122.3099 | 122.0947 | 122.2824 | 122.1085 | 122.3694 | 122.1634 | 121.907 | 122.2824 | 122.1085 | 122.1634 | 122.0947 | 122.3694 | -0.36163 | -0.33417
1863.3281 | 122.4152 | -122.0901 | 0.10071 | 0.0016785 | 0.012337 | 0.0075537 | 0.0056974 | -0.0083976 | -0.0079745 | 0.0077053 | 0.059509 | 0.13733 | -0.21515 | 0.16479 | 0.07782 | 0.15106 | -0.050354 | 0.31128 | 0.19226 | -0.18768 | 121.875 | 0.036621 | 122.1497 | 122.2549 | -0.022888 | 121.9025 | 0.091553 | 0.27466 | 122.0398 | 122.4014 | 122.168 | 122.2275 | 122.1497 | 122.2824 | 122.2412 | 121.9025 | 122.2275 | 122.1497 | 122.2412 | 122.168 | 122.2824 | -0.31586 | -0.28839
1865.0781 | 122.4014 | -122.1039 | 0.07782 | -0.005951 | 0.013832 | 0.010544 | 0.0080472 | -0.0069022 | -0.0096835 | 0.0051419 | -0.009155 | 0.15106 | -0.26093 | 0.10986 | 0.004578 | 0.068665 | 0.027466 | 0.23346 | 0.21515 | -0.21515 | 121.843 | 0.073242 | 122.0947 | 122.2137 | -0.073242 | 121.8887 | 0.13733 | 0.25177 | 122.1313 | 122.3373 | 122.1085 | 122.2549 | 122.0947 | 122.319 | 122.1725 | 121.8887 | 122.2549 | 122.0947 | 122.1725 | 122.1085 | 122.319 | -0.33875 | -0.29297
1866.8281 | 122.3557 | -122.1268 | 0.10986 | 0.0016785 | 0.015755 | 0.011399 | 0.010824 | -0.0077566 | -0.0064791 | 0.0092007 | -0.018311 | 0.17853 | -0.23346 | 0.059509 | -0.027466 | 0.041199 | -0.009155 | 0.15564 | 0.21973 | -0.21973 | 121.8933 | 0.068665 | 122.1085 | 122.1863 | -0.13733 | 121.907 | 0.10986 | 0.21515 | 122.1176 | 122.2824 | 122.0993 | 122.3053 | 122.1085 | 122.3465 | 122.168 | 121.907 | 122.3053 | 122.1085 | 122.168 | 122.0993 | 122.3465 | -0.34332 | -0.32959
1868.5 | 122.4014 | -122.0901 | 0.11902 | -0.005951 | 0.015327 | 0.0081947 | 0.005911 | -0.008184 | -0.0062655 | 0.0055691 | 0.073242 | 0.14191 | -0.19684 | 0.16937 | 0.082397 | 0.14648 | -0.050354 | 0.29297 | 0.21057 | -0.20599 | 121.8933 | 0.022888 | 122.1634 | 122.2595 | -0.036622 | 121.8842 | 0.091552 | 0.27008 | 122.0398 | 122.3831 | 122.1725 | 122.2321 | 122.1634 | 122.3007 | 122.2366 | 121.8842 | 122.2321 | 122.1634 | 122.2366 | 122.1725 | 122.3007 | -0.31586 | -0.32501
1870.25 | 122.2916 | -122.1588 | 0.13733 | 0.0016785 | 0.014473 | 0.011185 | 0.01296 | -0.0073294 | -0.0069065 | 0.0055691 | 0.036621 | 0.13733 | -0.24261 | 0.14648 | 0.045776 | 0.11444 | -0.050354 | 0.25635 | 0.20142 | -0.21515 | 121.9162 | 0 | 122.1954 | 122.3053 | -0.091553 | 121.9437 | 0.064087 | 0.27924 | 122.1085 | 122.4152 | 122.2046 | 122.2961 | 122.1954 | 122.3602 | 122.2733 | 121.9437 | 122.2961 | 122.1954 | 122.2733 | 122.2046 | 122.3602 | -0.37994 | -0.35248
1871.9844 | 122.3099 | -122.1588 | 0.11902 | 0.009308 | 0.01725 | 0.013535 | 0.010183 | -0.0069022 | -0.0081881 | 0.0072781 | 0.036621 | 0.15564 | -0.22888 | 0.13275 | 0.041199 | 0.11444 | -0.022888 | 0.24719 | 0.19226 | -0.23804 | 121.9299 | 0.036621 | 122.1954 | 122.2916 | -0.07782 | 121.9208 | 0.073242 | 0.2655 | 122.1359 | 122.406 | 122.2 | 122.3145 | 122.1954 | 122.3511 | 122.2733 | 121.9208 | 122.3145 | 122.1954 | 122.2733 | 122.2 | 122.3511 | -0.3479 | -0.35706
1873.7344 | 122.3877 | -122.1222 | 0.11444 | 0.0016785 | 0.015114 | 0.0079809 | 0.005911 | -0.0071158 | -0.0047703 | 0.0047147 | 0.09613 | 0.14191 | -0.18768 | 0.21057 | 0.13733 | 0.19226 | -0.13733 | 0.34332 | 0.1831 | -0.19684 | 121.9345 | 0.027466 | 122.2183 | 122.3328 | 0.022888 | 121.9254 | 0.068664 | 0.28381 | 121.9849 | 122.4655 | 122.2595 | 122.2641 | 122.2183 | 122.3053 | 122.3145 | 121.9254 | 122.2641 | 122.2183 | 122.3145 | 122.2595 | 122.3053 | -0.30212 | -0.31128
1875.4219 | 122.4335 | -122.1222 | 0.091553 | 0.009308 | 0.0149 | 0.0084083 | 0.0061246 | -0.008184 | -0.0051975 | 0.0070645 | 0.045776 | 0.14191 | -0.2243 | 0.13733 | 0.068665 | 0.11444 | -0.018311 | 0.27008 | 0.19226 | -0.21515 | 121.8979 | 0.050354 | 122.168 | 122.2595 | -0.022888 | 121.907 | 0.10071 | 0.27008 | 122.1039 | 122.3923 | 122.1909 | 122.2641 | 122.168 | 122.3145 | 122.2366 | 121.907 | 122.2641 | 122.168 | 122.2366 | 122.1909 | 122.3145 | -0.31586 | -0.3067
1877.1562 | 122.4472 | -122.1222 | 0.091553 | 0.0016785 | 0.014046 | 0.0090491 | 0.008688 | -0.010107 | -0.0054111 | 0.0066373 | -0.027466 | 0.16479 | -0.2655 | 0.091553 | 0.004578 | 0.050354 | 0.059509 | 0.19684 | 0.20599 | -0.23346 | 121.8567 | 0.073242 | 122.0947 | 122.2137 | -0.086975 | 121.8887 | 0.11444 | 0.23804 | 122.1817 | 122.319 | 122.1268 | 122.287 | 122.0947 | 122.3282 | 122.1725 | 121.8887 | 122.287 | 122.0947 | 122.1725 | 122.1268 | 122.3282 | -0.35706 | -0.32501
1878.9062 | 122.3053 | -122.1542 | 0.14191 | -0.013581 | 0.015541 | 0.010331 | 0.010183 | -0.0054068 | -0.0079745 | 0.0068509 | 0.064087 | 0.13733 | -0.20599 | 0.17853 | 0.073242 | 0.17395 | -0.16479 | 0.28381 | 0.18768 | -0.17853 | 121.9482 | -0.004578 | 122.2183 | 122.3328 | -0.068665 | 121.9757 | 0.045776 | 0.27008 | 121.9894 | 122.438 | 122.2275 | 122.2916 | 122.2183 | 122.3419 | 122.3282 | 121.9757 | 122.2916 | 122.2183 | 122.3282 | 122.2275 | 122.3419 | -0.3479 | -0.32044
1880.5938 | 122.3145 | -122.168 | 0.10986 | -0.005951 | 0.012337 | 0.0092627 | 0.012533 | -0.0060478 | -0.0064791 | 0.0087735 | 0.054932 | 0.15106 | -0.23804 | 0.15106 | 0.054932 | 0.086975 | -0.041199 | 0.24719 | 0.20142 | -0.21515 | 121.9299 | 0.041199 | 122.2229 | 122.319 | -0.054931 | 121.9528 | 0.091553 | 0.29297 | 122.1268 | 122.4152 | 122.2229 | 122.319 | 122.2229 | 122.3694 | 122.2549 | 121.9528 | 122.319 | 122.2229 | 122.2549 | 122.2229 | 122.3694 | -0.3479 | -0.32501
1882.3281 | 122.4106 | -122.1497 | 0.10071 | 0.009308 | 0.013832 | 0.010544 | 0.004202 | -0.0083976 | -0.0062655 | 0.0064237 | 0.068665 | 0.11444 | -0.2243 | 0.17853 | 0.10529 | 0.16937 | -0.091553 | 0.33875 | 0.1831 | -0.19226 | 121.9254 | 0.013733 | 122.2183 | 122.3282 | 0.004578 | 121.9574 | 0.082397 | 0.29297 | 122.0581 | 122.4884 | 122.2549 | 122.2641 | 122.2183 | 122.3328 | 122.319 | 121.9574 | 122.2641 | 122.2183 | 122.319 | 122.2549 | 122.3328 | -0.32501 | -0.29297
1884.0781 | 122.3877 | -122.1176 | 0.09613 | -0.005951 | 0.014046 | 0.013962 | 0.0063382 | -0.0073294 | -0.0066929 | 0.0064237 | 0.091553 | 0.1236 | -0.21515 | 0.20599 | 0.11444 | 0.1831 | -0.13733 | 0.35248 | 0.16479 | -0.19684 | 121.9025 | 0.027466 | 122.2092 | 122.3236 | 0.018311 | 121.9208 | 0.068665 | 0.3067 | 121.9803 | 122.4701 | 122.2321 | 122.2412 | 122.2092 | 122.2824 | 122.3007 | 121.9208 | 122.2412 | 122.2092 | 122.3007 | 122.2321 | 122.2824 | -0.31128 | -0.29297
1885.8594 | 122.4609 | -122.1039 | 0.10071 | -0.013581 | 0.014687 | 0.010544 | 0.0071926 | -0.010961 | -0.0056247 | 0.0036465 | 0.027466 | 0.14191 | -0.19684 | 0.15106 | 0.064087 | 0.14648 | -0.10986 | 0.29297 | 0.17395 | -0.21515 | 121.907 | 0.041199 | 122.1313 | 122.2549 | -0.036621 | 121.8887 | 0.073242 | 0.2243 | 121.994 | 122.3969 | 122.168 | 122.2458 | 122.1313 | 122.2778 | 122.2504 | 121.8887 | 122.2458 | 122.1313 | 122.2504 | 122.168 | 122.2778 | -0.29755 | -0.31586
1887.5469 | 122.3969 | -122.1588 | 0.091553 | -0.005951 | 0.015114 | 0.0058447 | 0.0074062 | -0.0088248 | -0.0071201 | 0.0070645 | 0.09613 | 0.12817 | -0.20599 | 0.21057 | 0.11902 | 0.1831 | -0.14191 | 0.35248 | 0.17395 | -0.20142 | 121.9528 | 0.036621 | 122.2549 | 122.3694 | 0.027466 | 121.9574 | 0.082397 | 0.30212 | 122.0169 | 122.5113 | 122.2778 | 122.287 | 122.2549 | 122.3328 | 122.3419 | 121.9574 | 122.287 | 122.2549 | 122.3419 | 122.2778 | 122.3328 | -0.29755 | -0.29297
1889.2969 | 122.4518 | -122.1405 | 0.07782 | -0.013581 | 0.015755 | 0.0079809 | 0.0065518 | -0.010961 | -0.0073337 | 0.0062099 | 0.018311 | 0.13733 | -0.21515 | 0.15106 | 0.059509 | 0.12817 | -0.10529 | 0.27466 | 0.17853 | -0.19684 | 121.9254 | 0.059509 | 122.1588 | 122.2916 | -0.018311 | 121.9437 | 0.10071 | 0.23346 | 122.0352 | 122.4152 | 122.2 | 122.2778 | 122.1588 | 122.319 | 122.2687 | 121.9437 | 122.2778 | 122.1588 | 122.2687 | 122.2 | 122.319 | -0.29297 | -0.27466
1891.0469 | 122.3419 | -122.168 | 0.10986 | -0.013581 | 0.016823 | 0.013962 | 0.010824 | -0.0086112 | -0.0064791 | 0.0049283 | 0.027466 | 0.15106 | -0.23346 | 0.15564 | 0.054932 | 0.13275 | -0.15106 | 0.28381 | 0.17853 | -0.19226 | 121.9345 | 0.041199 | 122.1954 | 122.3236 | -0.054931 | 121.9757 | 0.068665 | 0.26093 | 122.0169 | 122.4518 | 122.2229 | 122.319 | 122.1954 | 122.3465 | 122.3007 | 121.9757 | 122.319 | 122.1954 | 122.3007 | 122.2229 | 122.3465 | -0.34332 | -0.30212
1892.7188 | 122.4243 | -122.1542 | 0.10986 | -0.005951 | 0.014687 | 0.01204 | 0.0067654 | -0.0094656 | -0.0060519 | 0.0072781 | 0.050354 | 0.12817 | -0.21515 | 0.16022 | 0.059509 | 0.12817 | -0.12817 | 0.26093 | 0.18768 | -0.19684 | 121.9391 | 0.018311 | 122.2046 | 122.3145 | -0.050354 | 121.9574 | 0.07782 | 0.2655 | 122.0261 | 122.4152 | 122.2137 | 122.2824 | 122.2046 | 122.3419 | 122.2824 | 121.9574 | 122.2824 | 122.2046 | 122.2824 | 122.2137 | 122.3419 | -0.32501 | -0.3067
1894.4531 | 122.4609 | -122.1634 | 0.091553 | -0.005951 | 0.015968 | 0.0081947 | 0.011252 | -0.0073294 | -0.0043429 | 0.0068509 | -0.013733 | 0.16937 | -0.24719 | 0.10986 | -0.009155 | 0.054932 | 0.027466 | 0.21057 | 0.18768 | -0.22888 | 121.9162 | 0.07782 | 122.1497 | 122.2733 | -0.10071 | 121.9345 | 0.09613 | 0.23346 | 122.1909 | 122.374 | 122.1542 | 122.3328 | 122.1497 | 122.3511 | 122.2183 | 121.9345 | 122.3328 | 122.1497 | 122.2183 | 122.1542 | 122.3511 | -0.33874 | -0.32044
1896.1406 | 122.4792 | -122.1542 | 0.09613 | -0.013581 | 0.015541 | 0.0088355 | 0.0095426 | -0.009893 | -0.0058383 | 0.0083463 | -0.032043 | 0.18768 | -0.25177 | 0.09613 | 0.013733 | 0.041199 | 0.059509 | 0.1831 | 0.23346 | -0.23346 | 121.9025 | 0.091553 | 122.1222 | 122.2504 | -0.082397 | 121.9208 | 0.13733 | 0.21973 | 122.2137 | 122.3373 | 122.168 | 122.3419 | 122.1222 | 122.3877 | 122.1954 | 121.9208 | 122.3419 | 122.1222 | 122.1954 | 122.168 | 122.3877 | -0.3479 | -0.32959
1897.875 | 122.4518 | -122.1085 | 0.091553 | -0.005951 | 0.013405 | 0.0090491 | 0.0048428 | -0.010961 | -0.0049839 | 0.0051419 | 0.050354 | 0.13733 | -0.21057 | 0.1831 | 0.09613 | 0.17395 | -0.13733 | 0.32959 | 0.17853 | -0.19226 | 121.8979 | 0.045776 | 122.1588 | 122.2916 | 0.004577 | 121.9162 | 0.086975 | 0.26093 | 121.9711 | 122.438 | 122.2046 | 122.2458 | 122.1588 | 122.287 | 122.2824 | 121.9162 | 122.2458 | 122.1588 | 122.2824 | 122.2046 | 122.287 | -0.30212 | -0.28381
1899.5625 | 122.4335 | -122.1313 | 0.086975 | -0.005951 | 0.012978 | 0.0084083 | 0.0046292 | -0.013738 | -0.0054111 | 0.0064237 | 0.054932 | 0.1236 | -0.20599 | 0.21515 | 0.10071 | 0.17395 | -0.13733 | 0.32959 | 0.16937 | -0.19226 | 121.9254 | 0.036621 | 122.1863 | 122.3465 | 0.013733 | 121.9391 | 0.082398 | 0.26093 | 121.994 | 122.4609 | 122.2321 | 122.2549 | 122.1863 | 122.3007 | 122.3053 | 121.9391 | 122.2549 | 122.1863 | 122.3053 | 122.2321 | 122.3007 | -0.29297 | -0.27924
1901.25 | 122.3328 | -122.1909 | 0.12817 | -0.013581 | 0.013832 | 0.016526 | 0.010397 | -0.0056204 | -0.0077609 | 0.0059963 | 0.082397 | 0.13275 | -0.20142 | 0.19684 | 0.082397 | 0.17853 | -0.19226 | 0.29755 | 0.17395 | -0.19226 | 121.9894 | 0.004577 | 122.2733 | 122.3877 | -0.045777 | 121.9986 | 0.045776 | 0.28381 | 121.9986 | 122.4884 | 122.2733 | 122.3236 | 122.2733 | 122.3648 | 122.3694 | 121.9986 | 122.3236 | 122.2733 | 122.3694 | 122.2733 | 122.3648 | -0.32959 | -0.32044
1902.9844 | 122.3648 | -122.1771 | 0.10529 | -0.005951 | 0.014259 | 0.016953 | 0.0095426 | -0.0060478 | -0.0069065 | 0.0057827 | 0 | 0.15106 | -0.24261 | 0.11444 | 0 | 0.091553 | -0.09613 | 0.21057 | 0.19684 | -0.20599 | 121.9345 | 0.045776 | 122.1771 | 122.2916 | -0.10529 | 121.9711 | 0.091552 | 0.24261 | 122.081 | 122.3877 | 122.1771 | 122.3282 | 122.1771 | 122.374 | 122.2687 | 121.9711 | 122.3282 | 122.1771 | 122.2687 | 122.1771 | 122.374 | -0.3479 | -0.31128
1904.7188 | 122.4152 | -122.1863 | 0.086975 | -0.013581 | 0.015755 | 0.0069129 | 0.0054836 | -0.0094656 | -0.0088291 | 0.0079189 | 0.086975 | 0.1236 | -0.20142 | 0.21515 | 0.13275 | 0.19226 | -0.13733 | 0.37079 | 0.16937 | -0.19684 | 121.9849 | 0.036621 | 122.2733 | 122.4014 | 0.045776 | 121.9894 | 0.082398 | 0.28839 | 122.049 | 122.5571 | 122.319 | 122.3099 | 122.2733 | 122.3557 | 122.3785 | 121.9894 | 122.3099 | 122.2733 | 122.3785 | 122.319 | 122.3557 | -0.28839 | -0.28381
1906.4688 | 122.3831 | -122.2092 | 0.11444 | 0.0016785 | 0.015755 | 0.010544 | 0.013174 | -0.0086112 | -0.0098971 | 0.0042873 | 0.032043 | 0.16022 | -0.24719 | 0.13275 | 0.059509 | 0.10986 | -0.036621 | 0.25177 | 0.20142 | -0.2243 | 121.962 | 0.045776 | 122.2412 | 122.3419 | -0.054932 | 121.9849 | 0.086975 | 0.27924 | 122.1725 | 122.4609 | 122.2687 | 122.3694 | 122.2412 | 122.4106 | 122.319 | 121.9849 | 122.3694 | 122.2412 | 122.319 | 122.2687 | 122.4106 | -0.36163 | -0.33875
1908.1562 | 122.3877 | -122.1817 | 0.10529 | 0.0016785 | 0.017891 | 0.01204 | 0.011465 | -0.0049796 | -0.0075473 | 0.0062099 | -0.013733 | 0.17395 | -0.24719 | 0.086975 | 0 | 0.068665 | -0.041199 | 0.16022 | 0.20599 | -0.22888 | 121.9345 | 0.068664 | 122.168 | 122.2687 | -0.10529 | 121.9528 | 0.10071 | 0.23346 | 122.1405 | 122.3419 | 122.1817 | 122.3557 | 122.168 | 122.3877 | 122.2504 | 121.9528 | 122.3557 | 122.168 | 122.2504 | 122.1817 | 122.3877 | -0.35248 | -0.33417
1909.9062 | 122.4243 | -122.1863 | 0.13275 | 0.009308 | 0.015541 | 0.0090491 | 0.008688 | -0.006475 | -0.0092563 | 0.0074917 | 0.009155 | 0.17395 | -0.24719 | 0.15106 | 0.050354 | 0.10986 | -0.018311 | 0.23346 | 0.21973 | -0.21515 | 121.9391 | 0.041199 | 122.1954 | 122.3373 | -0.082397 | 121.9711 | 0.086976 | 0.25635 | 122.168 | 122.4197 | 122.2366 | 122.3602 | 122.1954 | 122.406 | 122.2961 | 121.9711 | 122.3602 | 122.1954 | 122.2961 | 122.2366 | 122.406 | -0.37994 | -0.3479
1911.6562 | 122.4792 | -122.1634 | 0.059509 | -0.013581 | 0.017036 | 0.012467 | 0.0039884 | -0.0079704 | -0.0043429 | 0.0057827 | 0.032043 | 0.1236 | -0.19684 | 0.14191 | 0.10071 | 0.16479 | -0.11902 | 0.29297 | 0.1831 | -0.19684 | 121.9666 | 0.064087 | 122.1954 | 122.3053 | 0.041199 | 121.9666 | 0.1236 | 0.22888 | 122.0444 | 122.4564 | 122.2641 | 122.287 | 122.1954 | 122.3465 | 122.3282 | 121.9666 | 122.287 | 122.1954 | 122.3282 | 122.2641 | 122.3465 | -0.25635 | -0.25635
1913.3438 | 122.3465 | -122.2 | 0.11902 | -0.005951 | 0.016182 | 0.012467 | 0.008688 | -0.004766 | -0.0077609 | 0.0053555 | 0.086975 | 0.14648 | -0.21973 | 0.1831 | 0.09613 | 0.1831 | -0.16937 | 0.28839 | 0.17853 | -0.19226 | 121.9803 | 0.027465 | 122.287 | 122.3831 | -0.022889 | 122.0078 | 0.059509 | 0.3067 | 122.0306 | 122.4884 | 122.2961 | 122.3465 | 122.287 | 122.3785 | 122.3831 | 122.0078 | 122.3465 | 122.287 | 122.3831 | 122.2961 | 122.3785 | -0.33875 | -0.31128
1915.0312 | 122.4106 | -122.1909 | 0.10986 | 0.0016785 | 0.014046 | 0.010544 | 0.00527 | -0.007543 | -0.0051975 | 0.0074917 | 0.07782 | 0.13733 | -0.19226 | 0.15106 | 0.082397 | 0.15564 | -0.13733 | 0.27924 | 0.17853 | -0.19684 | 121.9986 | 0.027466 | 122.2687 | 122.3419 | -0.027466 | 121.994 | 0.068665 | 0.27008 | 122.0535 | 122.4701 | 122.2733 | 122.3282 | 122.2687 | 122.3694 | 122.3465 | 121.994 | 122.3282 | 122.2687 | 122.3465 | 122.2733 | 122.3694 | -0.30212 | -0.3067
1916.7812 | 122.4701 | -122.1725 | 0.10986 | -0.02121 | 0.014259 | 0.010117 | 0.005911 | -0.0079704 | -0.0064791 | 0.0068509 | 0.036621 | 0.13275 | -0.20142 | 0.15564 | 0.068665 | 0.14648 | -0.11902 | 0.26093 | 0.16479 | -0.19226 | 121.9711 | 0.022888 | 122.2092 | 122.3282 | -0.041198 | 121.9803 | 0.054932 | 0.23804 | 122.0535 | 122.4335 | 122.2412 | 122.3053 | 122.2092 | 122.3373 | 122.319 | 121.9803 | 122.3053 | 122.2092 | 122.319 | 122.2412 | 122.3373 | -0.31128 | -0.30212
1918.5312 | 122.4976 | -122.1909 | 0.073242 | 0.0016785 | 0.012337 | 0.010544 | 0.0093288 | -0.0083976 | -0.0084017 | 0.0068509 | -0.027466 | 0.14191 | -0.24261 | 0.10529 | 0 | 0.059509 | 0.041199 | 0.23346 | 0.21973 | -0.21515 | 121.9482 | 0.068665 | 122.1634 | 122.2961 | -0.073242 | 121.9757 | 0.14649 | 0.21515 | 122.2321 | 122.4243 | 122.1909 | 122.3328 | 122.1634 | 122.4106 | 122.2504 | 121.9757 | 122.3328 | 122.1634 | 122.2504 | 122.1909 | 122.4106 | -0.31586 | -0.28839
1920.2188 | 122.374 | -122.2229 | 0.1236 | -0.005951 | 0.012123 | 0.011612 | 0.0065518 | -0.0083976 | -0.0081881 | 0.0077053 | 0.07782 | 0.1236 | -0.19684 | 0.1831 | 0.091553 | 0.17853 | -0.17853 | 0.29297 | 0.16937 | -0.19226 | 122.0261 | 0 | 122.3007 | 122.406 | -0.032043 | 122.0306 | 0.045777 | 0.27466 | 122.0444 | 122.5159 | 122.3145 | 122.3465 | 122.3007 | 122.3923 | 122.4014 | 122.0306 | 122.3465 | 122.3007 | 122.4014 | 122.3145 | 122.3923 | -0.32043 | -0.31586
1921.9531 | 122.4518 | -122.1954 | 0.10529 | 0.0016785 | 0.016396 | 0.01738 | 0.0074062 | -0.0079704 | -0.0066929 | 0.0072781 | 0.10529 | 0.1236 | -0.20142 | 0.21057 | 0.11902 | 0.20142 | -0.14191 | 0.3479 | 0.16022 | -0.18768 | 121.994 | 0.01831 | 122.3007 | 122.406 | 0.013733 | 122.0078 | 0.054931 | 0.3067 | 122.0535 | 122.5433 | 122.3145 | 122.319 | 122.3007 | 122.3557 | 122.3969 | 122.0078 | 122.319 | 122.3007 | 122.3969 | 122.3145 | 122.3557 | -0.3067 | -0.29297
1923.625 | 122.3785 | -122.2137 | 0.1236 | 0.0016785 | 0.016823 | 0.019089 | 0.014242 | -0.0083976 | -0.0081881 | 0.0051419 | 0.050354 | 0.15564 | -0.23346 | 0.16937 | 0.036621 | 0.11444 | -0.054932 | 0.25635 | 0.20599 | -0.21515 | 121.9803 | 0.032044 | 122.2641 | 122.3831 | -0.086975 | 121.9986 | 0.082398 | 0.28381 | 122.1588 | 122.4701 | 122.2504 | 122.3694 | 122.2641 | 122.4197 | 122.3282 | 121.9986 | 122.3694 | 122.2641 | 122.3282 | 122.2504 | 122.4197 | -0.35706 | -0.33875
1925.3594 | 122.3694 | -122.2275 | 0.12817 | 0.0016785 | 0.012337 | 0.0081947 | 0.006979 | -0.007543 | -0.0058383 | 0.0079189 | 0.09613 | 0.12817 | -0.17853 | 0.1831 | 0.10986 | 0.20142 | -0.17395 | 0.29755 | 0.15106 | -0.19226 | 122.049 | 0 | 122.3236 | 122.4106 | -0.018311 | 122.0352 | 0.022888 | 0.27466 | 122.0535 | 122.525 | 122.3373 | 122.3557 | 122.3236 | 122.3785 | 122.4289 | 122.0352 | 122.3557 | 122.3236 | 122.4289 | 122.3373 | 122.3785 | -0.3067 | -0.32044
1927.0469 | 122.4472 | -122.1863 | 0.10529 | -0.005951 | 0.013832 | 0.016526 | 0.0067654 | -0.01032 | -0.0066929 | 0.0057827 | 0.091553 | 0.13275 | -0.20599 | 0.21515 | 0.10986 | 0.20599 | -0.14648 | 0.35706 | 0.15564 | -0.18768 | 121.9803 | 0.027465 | 122.2778 | 122.4014 | 0.004577 | 121.9986 | 0.050354 | 0.29755 | 122.0398 | 122.5433 | 122.2961 | 122.319 | 122.2778 | 122.3419 | 122.3923 | 121.9986 | 122.319 | 122.2778 | 122.3923 | 122.2961 | 122.3419 | -0.31128 | -0.29297
1928.7969 | 122.4518 | -122.1909 | 0.10071 | -0.005951 | 0.014473 | 0.011612 | 0.0061246 | -0.009252 | -0.0056247 | 0.0064237 | 0.07782 | 0.13275 | -0.1831 | 0.21515 | 0.12817 | 0.19684 | -0.13733 | 0.35706 | 0.14648 | -0.19684 | 122.0078 | 0.032043 | 122.2687 | 122.406 | 0.027466 | 121.994 | 0.045776 | 0.26092 | 122.0535 | 122.5479 | 122.319 | 122.3236 | 122.2687 | 122.3373 | 122.3877 | 121.994 | 122.3236 | 122.2687 | 122.3877 | 122.319 | 122.3373 | -0.28381 | -0.29755
1930.5469 | 122.4243 | -122.2275 | 0.1236 | 0.0016785 | 0.014687 | 0.014817 | 0.012747 | -0.010107 | -0.0062655 | 0.0092007 | -0.032043 | 0.1831 | -0.24261 | 0.086975 | 0 | 0.050354 | -0.013733 | 0.15106 | 0.20142 | -0.23346 | 121.9849 | 0.059509 | 122.1954 | 122.3145 | -0.1236 | 121.994 | 0.07782 | 0.21057 | 122.2137 | 122.3785 | 122.2275 | 122.4106 | 122.1954 | 122.4289 | 122.2778 | 121.994 | 122.4106 | 122.1954 | 122.2778 | 122.2275 | 122.4289 | -0.36621 | -0.35706
1932.2812 | 122.4518 | -122.2275 | 0.10071 | 0.0016785 | 0.014687 | 0.01439 | 0.010183 | -0.0077566 | -0.0084017 | 0.0051419 | 0.022888 | 0.16937 | -0.24261 | 0.13733 | 0.036621 | 0.10529 | -0.009155 | 0.24261 | 0.1831 | -0.2243 | 121.9849 | 0.068665 | 122.2504 | 122.3648 | -0.064087 | 122.0032 | 0.082397 | 0.2655 | 122.2183 | 122.4701 | 122.2641 | 122.3969 | 122.2504 | 122.4106 | 122.3328 | 122.0032 | 122.3969 | 122.2504 | 122.3328 | 122.2641 | 122.4106 | -0.34332 | -0.32501
1934.0156 | 122.493 | -122.2046 | 0.086975 | -0.005951 | 0.010628 | 0.0066993 | 0.005911 | -0.0096794 | -0.0073337 | 0.0049283 | 0.064087 | 0.13275 | -0.21973 | 0.20599 | 0.10529 | 0.1831 | -0.068665 | 0.32501 | 0.1831 | -0.19684 | 121.9849 | 0.045776 | 122.2687 | 122.4106 | 0.018311 | 122.0078 | 0.09613 | 0.28381 | 122.1359 | 122.5296 | 122.3099 | 122.3373 | 122.2687 | 122.3877 | 122.3877 | 122.0078 | 122.3373 | 122.2687 | 122.3877 | 122.3099 | 122.3877 | -0.3067 | -0.28381
1935.7812 | 122.3969 | -122.2366 | 0.10529 | 0.0016785 | 0.014473 | 0.013321 | 0.011038 | -0.0069022 | -0.0075473 | 0.0070645 | 0.027466 | 0.14648 | -0.25177 | 0.1236 | 0.004578 | 0.07782 | -0.027466 | 0.19684 | 0.20142 | -0.21057 | 121.9849 | 0.041198 | 122.2641 | 122.3602 | -0.10071 | 122.0261 | 0.09613 | 0.27924 | 122.2092 | 122.4335 | 122.2412 | 122.3831 | 122.2641 | 122.438 | 122.3145 | 122.0261 | 122.3831 | 122.2641 | 122.3145 | 122.2412 | 122.438 | -0.35706 | -0.31586
1937.4531 | 122.5113 | -122.1863 | 0.073242 | -0.013581 | 0.013618 | 0.014176 | 0.0029202 | -0.0066886 | -0.0058383 | 0.0074917 | 0.036621 | 0.13275 | -0.21057 | 0.14191 | 0.050354 | 0.13275 | -0.10529 | 0.25635 | 0.17853 | -0.20599 | 121.9757 | 0.059509 | 122.2229 | 122.3282 | -0.022888 | 121.9803 | 0.10529 | 0.24719 | 122.081 | 122.4426 | 122.2366 | 122.319 | 122.2229 | 122.3648 | 122.319 | 121.9803 | 122.319 | 122.2229 | 122.319 | 122.2366 | 122.3648 | -0.28381 | -0.27924
1939.1875 | 122.4701 | -122.2229 | 0.082397 | 0.0016785 | 0.015968 | 0.0081947 | 0.0048428 | -0.008184 | -0.0066929 | 0.0070645 | 0.10986 | 0.14191 | -0.19684 | 0.21973 | 0.15564 | 0.21515 | -0.15564 | 0.3479 | 0.17395 | -0.17853 | 122.0261 | 0.05951 | 122.3328 | 122.4426 | 0.073243 | 122.0444 | 0.091553 | 0.3067 | 122.0673 | 122.5708 | 122.3785 | 122.3648 | 122.3328 | 122.3969 | 122.438 | 122.0444 | 122.3648 | 122.3328 | 122.438 | 122.3785 | 122.3969 | -0.27924 | -0.26092
1940.9531 | 122.4106 | -122.2275 | 0.11902 | 0.016937 | 0.015755 | 0.0096899 | 0.008688 | -0.0083976 | -0.0064791 | 0.0066373 | 0 | 0.16022 | -0.22888 | 0.1236 | 0.036621 | 0.10986 | -0.11902 | 0.21515 | 0.17853 | -0.19226 | 121.9986 | 0.041198 | 122.2275 | 122.3511 | -0.082398 | 122.0352 | 0.059509 | 0.22888 | 122.1085 | 122.4426 | 122.2641 | 122.3877 | 122.2275 | 122.406 | 122.3373 | 122.0352 | 122.3877 | 122.2275 | 122.3373 | 122.2641 | 122.406 | -0.3479 | -0.31128
1942.625 | 122.5204 | -122.1771 | 0.07782 | -0.005951 | 0.014259 | 0.0073401 | 0.0048428 | -0.0086112 | -0.0054111 | 0.0085599 | 0.032043 | 0.13733 | -0.21057 | 0.14191 | 0.082397 | 0.14191 | -0.11444 | 0.28839 | 0.16937 | -0.21057 | 121.9666 | 0.059509 | 122.2092 | 122.319 | 0.004577 | 121.9666 | 0.091553 | 0.24261 | 122.0627 | 122.4655 | 122.2595 | 122.3145 | 122.2092 | 122.3465 | 122.319 | 121.9666 | 122.3145 | 122.2092 | 122.319 | 122.2595 | 122.3465 | -0.28839 | -0.28839
1944.2969 | 122.5159 | -122.2321 | 0.10071 | -0.005951 | 0.013618 | 0.01204 | 0.006979 | -0.0079704 | -0.0054111 | 0.0070645 | 0.045776 | 0.14191 | -0.21515 | 0.16022 | 0.059509 | 0.11444 | -0.013733 | 0.25635 | 0.21057 | -0.21973 | 122.0169 | 0.041199 | 122.2778 | 122.3923 | -0.041199 | 122.0123 | 0.10986 | 0.26093 | 122.2183 | 122.4884 | 122.2916 | 122.374 | 122.2778 | 122.4426 | 122.3465 | 122.0123 | 122.374 | 122.2778 | 122.3465 | 122.2916 | 122.4426 | -0.31586 | -0.32044
1946.0469 | 122.3969 | -122.2458 | 0.10986 | -0.013581 | 0.016609 | 0.0096899 | 0.010824 | -0.0069022 | -0.0073337 | 0.0068509 | 0.045776 | 0.16022 | -0.2243 | 0.14648 | 0.045776 | 0.12817 | -0.12817 | 0.24719 | 0.20142 | -0.19226 | 122.0215 | 0.050354 | 122.2916 | 122.3923 | -0.064087 | 122.0535 | 0.091553 | 0.27008 | 122.1176 | 122.493 | 122.2916 | 122.406 | 122.2916 | 122.4472 | 122.374 | 122.0535 | 122.406 | 122.2916 | 122.374 | 122.2916 | 122.4472 | -0.33417 | -0.30212
1947.7344 | 122.493 | -122.2137 | 0.086975 | 0.0016785 | 0.013191 | 0.0081947 | 0.0063382 | -0.0086112 | -0.0045565 | 0.0059963 | 0.09613 | 0.13733 | -0.21057 | 0.23346 | 0.12817 | 0.19226 | -0.14191 | 0.33875 | 0.16022 | -0.19684 | 122.0032 | 0.050354 | 122.3099 | 122.4472 | 0.041199 | 122.0169 | 0.073242 | 0.3067 | 122.0718 | 122.5525 | 122.3419 | 122.3511 | 122.3099 | 122.374 | 122.406 | 122.0169 | 122.3511 | 122.3099 | 122.406 | 122.3419 | 122.374 | -0.29755 | -0.28381
1949.4688 | 122.3877 | -122.2778 | 0.13275 | -0.005951 | 0.015968 | 0.012681 | 0.0089016 | -0.0060478 | -0.0060519 | 0.0083463 | 0.11444 | 0.1236 | -0.21515 | 0.21057 | 0.10071 | 0.19684 | -0.21057 | 0.3067 | 0.17853 | -0.16022 | 122.0627 | -0.009155 | 122.3923 | 122.4884 | -0.032043 | 122.1176 | 0.045777 | 0.32959 | 122.0673 | 122.5845 | 122.3785 | 122.4014 | 122.3923 | 122.4564 | 122.4747 | 122.1176 | 122.4014 | 122.3923 | 122.4747 | 122.3785 | 122.4564 | -0.3479 | -0.29297
1951.1562 | 122.4289 | -122.2687 | 0.11444 | 0.0016785 | 0.014046 | 0.010117 | 0.011038 | -0.0069022 | -0.0032749 | 0.0049283 | 0 | 0.16022 | -0.24719 | 0.11902 | 0.041199 | 0.1236 | -0.1236 | 0.21515 | 0.1831 | -0.19226 | 122.0215 | 0.045776 | 122.2687 | 122.3877 | -0.073242 | 122.0764 | 0.068664 | 0.24719 | 122.1451 | 122.4838 | 122.3099 | 122.4289 | 122.2687 | 122.4518 | 122.3923 | 122.0764 | 122.4289 | 122.2687 | 122.3923 | 122.3099 | 122.4518 | -0.36163 | -0.3067
1952.9062 | 122.5388 | -122.2229 | 0.091553 | 0.0016785 | 0.015968 | 0.0094763 | 0.0044156 | -0.008184 | -0.0049839 | 0.0068509 | -0.018311 | 0.17395 | -0.24719 | 0.10071 | 0.022888 | 0.059509 | 0.050354 | 0.20599 | 0.23346 | -0.22888 | 121.9757 | 0.082397 | 122.2046 | 122.3236 | -0.068665 | 121.994 | 0.14191 | 0.22888 | 122.2733 | 122.4289 | 122.2458 | 122.3969 | 122.2046 | 122.4564 | 122.2824 | 121.994 | 122.3969 | 122.2046 | 122.2824 | 122.2458 | 122.4564 | -0.33874 | -0.32044
1954.6562 | 122.5204 | -122.2 | 0.10529 | -0.013581 | 0.014046 | 0.010544 | 0.0061246 | -0.0051932 | -0.0026339 | 0.0055691 | 0.036621 | 0.12817 | -0.20142 | 0.12817 | 0.054932 | 0.13733 | -0.1236 | 0.2655 | 0.18768 | -0.20142 | 121.9986 | 0.022888 | 122.2366 | 122.3282 | -0.050354 | 121.9986 | 0.082397 | 0.23804 | 122.0764 | 122.4655 | 122.2549 | 122.3282 | 122.2366 | 122.3877 | 122.3373 | 121.9986 | 122.3282 | 122.2366 | 122.3373 | 122.2549 | 122.3877 | -0.3067 | -0.3067
1956.3438 | 122.4564 | -122.2504 | 0.13275 | -0.005951 | 0.014687 | 0.014603 | 0.011679 | -0.0062614 | -0.0071201 | 0.0077053 | -0.013733 | 0.16479 | -0.24261 | 0.086975 | -0.022888 | 0.041199 | -0.004578 | 0.16479 | 0.19684 | -0.21057 | 122.0078 | 0.032044 | 122.2366 | 122.3373 | -0.15564 | 122.0398 | 0.064087 | 0.22888 | 122.2458 | 122.4152 | 122.2275 | 122.4152 | 122.2366 | 122.4472 | 122.2916 | 122.0398 | 122.4152 | 122.2366 | 122.2916 | 122.2275 | 122.4472 | -0.37537 | -0.34332
1958.0938 | 122.4152 | -122.2778 | 0.11902 | 0.009308 | 0.016823 | 0.0073401 | 0.012106 | -0.0062614 | -0.0092563 | 0.0072781 | 0.054932 | 0.16022 | -0.23804 | 0.15564 | 0.050354 | 0.10071 | -0.050354 | 0.26093 | 0.20599 | -0.21057 | 122.0398 | 0.041198 | 122.3328 | 122.4335 | -0.068665 | 122.0673 | 0.086975 | 0.29297 | 122.2275 | 122.5388 | 122.3282 | 122.438 | 122.3328 | 122.4838 | 122.3785 | 122.0673 | 122.438 | 122.3328 | 122.3785 | 122.3282 | 122.4838 | -0.35706 | -0.32959
1959.8438 | 122.5388 | -122.2504 | 0.073242 | -0.005951 | 0.015327 | 0.011826 | 0.002493 | -0.0071158 | -0.0073337 | 0.0066373 | 0.045776 | 0.14191 | -0.20599 | 0.15564 | 0.09613 | 0.15106 | -0.11444 | 0.28381 | 0.19226 | -0.20599 | 122.0444 | 0.068665 | 122.2961 | 122.406 | 0.022888 | 122.0444 | 0.11902 | 0.25177 | 122.1359 | 122.5342 | 122.3465 | 122.3923 | 122.2961 | 122.4426 | 122.4014 | 122.0444 | 122.3923 | 122.2961 | 122.4014 | 122.3465 | 122.4426 | -0.27924 | -0.27924
1961.5312 | 122.4609 | -122.2458 | 0.09613 | 0.0016785 | 0.015327 | 0.015244 | 0.010397 | -0.0043388 | -0.0071201 | 0.0057827 | -0.022888 | 0.16937 | -0.24261 | 0.068665 | -0.027466 | 0.059509 | -0.013733 | 0.14191 | 0.2243 | -0.21515 | 122.0032 | 0.073243 | 122.2229 | 122.3145 | -0.1236 | 122.0306 | 0.12817 | 0.21973 | 122.2321 | 122.3877 | 122.2183 | 122.4152 | 122.2229 | 122.4701 | 122.3053 | 122.0306 | 122.4152 | 122.2229 | 122.3053 | 122.2183 | 122.4701 | -0.33874 | -0.31128
1963.2812 | 122.4701 | -122.2549 | 0.10529 | -0.005951 | 0.015327 | 0.011826 | 0.0095426 | -0.0041252 | -0.0069065 | 0.0068509 | -0.018311 | 0.17395 | -0.26093 | 0.082397 | -0.018311 | 0.059509 | -0.013733 | 0.15564 | 0.21057 | -0.22888 | 121.994 | 0.068664 | 122.2366 | 122.3373 | -0.1236 | 122.0261 | 0.10529 | 0.24261 | 122.2412 | 122.4106 | 122.2366 | 122.4289 | 122.2366 | 122.4655 | 122.3145 | 122.0261 | 122.4289 | 122.2366 | 122.3145 | 122.2366 | 122.4655 | -0.36621 | -0.33417
1965.0312 | 122.4747 | -122.2641 | 0.091553 | 0.0016785 | 0.016182 | 0.011399 | 0.0095426 | -0.0054068 | -0.0081881 | 0.0087735 | -0.009155 | 0.1831 | -0.25635 | 0.059509 | -0.018311 | 0.064087 | -0.009155 | 0.15564 | 0.21973 | -0.24261 | 122.0078 | 0.091552 | 122.2549 | 122.3236 | -0.10986 | 122.0215 | 0.12817 | 0.24719 | 122.2549 | 122.4197 | 122.2458 | 122.4472 | 122.2549 | 122.4838 | 122.3282 | 122.0215 | 122.4472 | 122.2549 | 122.3282 | 122.2458 | 122.4838 | -0.3479 | -0.33417
1966.7188 | 122.4609 | -122.2916 | 0.1236 | -0.005951 | 0.0149 | 0.012894 | 0.0099698 | -0.0062614 | -0.0054111 | 0.0057827 | -0.004578 | 0.14648 | -0.23804 | 0.091553 | 0.004578 | 0.059509 | 0.004578 | 0.17853 | 0.1831 | -0.21515 | 122.0535 | 0.022888 | 122.287 | 122.3831 | -0.11902 | 122.0764 | 0.059509 | 0.23346 | 122.2961 | 122.4701 | 122.2961 | 122.438 | 122.287 | 122.4747 | 122.3511 | 122.0764 | 122.438 | 122.287 | 122.3511 | 122.2961 | 122.4747 | -0.36163 | -0.33875
1968.4688 | 122.5479 | -122.2046 | 0.09613 | -0.02121 | 0.016396 | 0.010117 | 0.00099761 | -0.0079704 | -0.0051975 | 0.0077053 | 0.041199 | 0.12817 | -0.19684 | 0.15564 | 0.09613 | 0.16022 | -0.11444 | 0.3067 | 0.1831 | -0.21515 | 122.0078 | 0.032044 | 122.2458 | 122.3602 | 0 | 121.9894 | 0.086975 | 0.23804 | 122.0901 | 122.5113 | 122.3007 | 122.3328 | 122.2458 | 122.3877 | 122.3648 | 121.9894 | 122.3328 | 122.2458 | 122.3648 | 122.3007 | 122.3877 | -0.29297 | -0.31128
1970.1562 | 122.5433 | -122.2412 | 0.082397 | -0.013581 | 0.015755 | 0.010758 | 0.0071926 | -0.0083976 | -0.0084017 | 0.0062099 | -0.013733 | 0.1831 | -0.24719 | 0.10071 | 0 | 0.054932 | 0.036621 | 0.21973 | 0.21515 | -0.2243 | 121.994 | 0.10071 | 122.2275 | 122.3419 | -0.082397 | 122.0169 | 0.13275 | 0.23346 | 122.2778 | 122.4609 | 122.2412 | 122.4243 | 122.2275 | 122.4564 | 122.2961 | 122.0169 | 122.4243 | 122.2275 | 122.2961 | 122.2412 | 122.4564 | -0.32959 | -0.3067
1971.9062 | 122.4152 | -122.2778 | 0.13275 | -0.013581 | 0.012978 | 0.011185 | 0.0056974 | -0.0069022 | -0.0060519 | 0.0068509 | 0.091553 | 0.09613 | -0.20142 | 0.19226 | 0.10529 | 0.20142 | -0.20142 | 0.32501 | 0.16479 | -0.17853 | 122.0764 | -0.036621 | 122.3694 | 122.4701 | -0.027465 | 122.0993 | 0.032044 | 0.29297 | 122.0764 | 122.6028 | 122.3831 | 122.374 | 122.3694 | 122.4426 | 122.4792 | 122.0993 | 122.374 | 122.3694 | 122.4792 | 122.3831 | 122.4426 | -0.33417 | -0.31128
1973.6562 | 122.5662 | -122.2641 | 0.09613 | 0.0016785 | 0.013832 | 0.0088355 | 0.0020658 | -0.008184 | -0.0047703 | 0.0051419 | 0.041199 | 0.14648 | -0.21973 | 0.15106 | 0.082397 | 0.16022 | -0.10986 | 0.28381 | 0.17853 | -0.18768 | 122.0444 | 0.050354 | 122.3053 | 122.4152 | -0.013733 | 122.0764 | 0.082398 | 0.26093 | 122.1542 | 122.5479 | 122.3465 | 122.4106 | 122.3053 | 122.4426 | 122.4243 | 122.0764 | 122.4106 | 122.3053 | 122.4243 | 122.3465 | 122.4426 | -0.31586 | -0.28381
1975.4062 | 122.4335 | -122.2961 | 0.11902 | -0.005951 | 0.015755 | 0.0096899 | 0.0089016 | -0.0079704 | -0.0069065 | 0.0059963 | 0.059509 | 0.11444 | -0.21515 | 0.1831 | 0.09613 | 0.17395 | -0.17853 | 0.28839 | 0.16937 | -0.1831 | 122.081 | -0.004578 | 122.3557 | 122.4792 | -0.022889 | 122.113 | 0.050354 | 0.27466 | 122.1176 | 122.5845 | 122.3923 | 122.4106 | 122.3557 | 122.4655 | 122.4701 | 122.113 | 122.4106 | 122.3557 | 122.4701 | 122.3923 | 122.4655 | -0.33417 | -0.30212
1977.0938 | 122.5708 | -122.2366 | 0.086975 | 0.0016785 | 0.016609 | 0.010331 | 0.0054836 | -0.010961 | -0.0075473 | 0.0074917 | -0.004578 | 0.14648 | -0.22888 | 0.10529 | 0.013733 | 0.059509 | 0.036621 | 0.23804 | 0.2243 | -0.2243 | 122.0078 | 0.059509 | 122.2321 | 122.3419 | -0.073242 | 122.0123 | 0.13733 | 0.2243 | 122.2733 | 122.4747 | 122.2504 | 122.3831 | 122.2321 | 122.4609 | 122.2961 | 122.0123 | 122.3831 | 122.2321 | 122.2961 | 122.2504 | 122.4609 | -0.31586 | -0.31128
1978.8281 | 122.525 | -122.2595 | 0.10529 | -0.013581 | 0.013191 | 0.0099037 | 0.0039884 | -0.009252 | -0.0054111 | 0.0064237 | 0.10071 | 0.11902 | -0.21057 | 0.19684 | 0.11902 | 0.19226 | -0.14648 | 0.33875 | 0.17395 | -0.19226 | 122.049 | 0.013733 | 122.3602 | 122.4564 | 0.013733 | 122.0673 | 0.068664 | 0.31128 | 122.113 | 122.5983 | 122.3785 | 122.3785 | 122.3602 | 122.4335 | 122.4518 | 122.0673 | 122.3785 | 122.3602 | 122.4518 | 122.3785 | 122.4335 | -0.31586 | -0.29755
1980.5781 | 122.493 | -122.2824 | 0.11902 | -0.005951 | 0.015541 | 0.013749 | 0.011465 | -0.0060478 | -0.0086155 | 0.0066373 | 0.004578 | 0.1831 | -0.24719 | 0.082397 | -0.018311 | 0.036621 | -0.027466 | 0.16022 | 0.22888 | -0.2243 | 122.0352 | 0.064086 | 122.287 | 122.3648 | -0.13733 | 122.0581 | 0.10986 | 0.25177 | 122.2549 | 122.4426 | 122.2641 | 122.4655 | 122.287 | 122.5113 | 122.319 | 122.0581 | 122.4655 | 122.287 | 122.319 | 122.2641 | 122.5113 | -0.36621 | -0.34332
1982.2656 | 122.5388 | -122.2641 | 0.07782 | 0.0016785 | 0.013405 | 0.0090491 | 0.002493 | -0.0094656 | -0.0056247 | 0.0049283 | 0.07782 | 0.13275 | -0.19684 | 0.21515 | 0.11902 | 0.20599 | -0.14191 | 0.33417 | 0.16022 | -0.20142 | 122.0673 | 0.054931 | 122.3419 | 122.4792 | 0.041199 | 122.0627 | 0.082397 | 0.27466 | 122.1222 | 122.5983 | 122.3831 | 122.3969 | 122.3419 | 122.4243 | 122.4701 | 122.0627 | 122.3969 | 122.3419 | 122.4701 | 122.3831 | 122.4243 | -0.27466 | -0.27924
1984 | 122.5525 | -122.2641 | 0.10071 | -0.005951 | 0.016396 | 0.011612 | 0.0065518 | -0.008184 | -0.0062655 | 0.0074917 | 0.064087 | 0.12817 | -0.21973 | 0.17395 | 0.086975 | 0.13733 | -0.045776 | 0.27008 | 0.19684 | -0.21973 | 122.0444 | 0.027466 | 122.3282 | 122.438 | -0.013733 | 122.0444 | 0.09613 | 0.28381 | 122.2183 | 122.5342 | 122.3511 | 122.3923 | 122.3282 | 122.4609 | 122.4014 | 122.0444 | 122.3923 | 122.3282 | 122.4014 | 122.3511 | 122.4609 | -0.32044 | -0.32044
1985.6719 | 122.4472 | -122.2778 | 0.10986 | -0.02121 | 0.014046 | 0.01503 | 0.0091152 | -0.006475 | -0.0077609 | 0.0053555 | 0.086975 | 0.09613 | -0.21057 | 0.20599 | 0.11444 | 0.18768 | -0.20599 | 0.31586 | 0.16479 | -0.17853 | 122.0673 | -0.013733 | 122.3648 | 122.4838 | 0.004578 | 122.0993 | 0.054932 | 0.29755 | 122.0718 | 122.5937 | 122.3923 | 122.374 | 122.3648 | 122.4426 | 122.4655 | 122.0993 | 122.374 | 122.3648 | 122.4655 | 122.3923 | 122.4426 | -0.32043 | -0.28839
1987.4219 | 122.5296 | -122.2641 | 0.09613 | 0.0016785 | 0.013405 | 0.010331 | 0.0044156 | -0.011602 | -0.0039157 | 0.0066373 | 0.073242 | 0.11902 | -0.19684 | 0.21515 | 0.11444 | 0.20599 | -0.16022 | 0.3479 | 0.16479 | -0.19684 | 122.0673 | 0.022889 | 122.3373 | 122.4792 | 0.018311 | 122.0673 | 0.068665 | 0.27008 | 122.1039 | 122.612 | 122.3785 | 122.3831 | 122.3373 | 122.4289 | 122.4701 | 122.0673 | 122.3831 | 122.3373 | 122.4701 | 122.3785 | 122.4289 | -0.29297 | -0.29297
1989.1094 | 122.5479 | -122.3099 | 0.10529 | 0.0016785 | 0.014046 | 0.013535 | 0.0099698 | -0.0083976 | -0.0079745 | 0.0049283 | 0.009155 | 0.16479 | -0.26093 | 0.12817 | 0.032043 | 0.086975 | 0 | 0.22888 | 0.20142 | -0.21515 | 122.049 | 0.059509 | 122.319 | 122.438 | -0.073243 | 122.0947 | 0.09613 | 0.27008 | 122.3099 | 122.5388 | 122.3419 | 122.4747 | 122.319 | 122.5113 | 122.3969 | 122.0947 | 122.4747 | 122.319 | 122.3969 | 122.3419 | 122.5113 | -0.36621 | -0.32044
1990.8594 | 122.5388 | -122.2549 | 0.082397 | 0.009308 | 0.015541 | 0.011612 | 0.003561 | -0.009893 | -0.0039157 | 0.0064237 | 0.073242 | 0.15106 | -0.20142 | 0.19226 | 0.12817 | 0.18768 | -0.13275 | 0.31586 | 0.16022 | -0.20599 | 122.0535 | 0.068665 | 122.3282 | 122.4472 | 0.045777 | 122.0489 | 0.07782 | 0.27466 | 122.1222 | 122.5708 | 122.3831 | 122.406 | 122.3282 | 122.4152 | 122.4426 | 122.0489 | 122.406 | 122.3282 | 122.4426 | 122.3831 | 122.4152 | -0.28381 | -0.28839
1992.6094 | 122.5891 | -122.2687 | 0.068665 | 0.0016785 | 0.015541 | 0.010331 | 0.005911 | -0.0088248 | -0.0043429 | 0.0055691 | -0.022888 | 0.15564 | -0.24261 | 0.10529 | 0.018311 | 0.054932 | 0.045776 | 0.21057 | 0.20599 | -0.2243 | 122.0261 | 0.086975 | 122.2458 | 122.374 | -0.050354 | 122.0444 | 0.13733 | 0.21973 | 122.3145 | 122.4792 | 122.287 | 122.4243 | 122.2458 | 122.4747 | 122.3236 | 122.0444 | 122.4243 | 122.2458 | 122.3236 | 122.287 | 122.4747 | -0.31128 | -0.29297
1994.375 | 122.5891 | -122.2778 | 0.086975 | -0.005951 | 0.014473 | 0.012894 | 0.0046292 | -0.008184 | -0.0034885 | 0.0062099 | 0.050354 | 0.12817 | -0.21973 | 0.16479 | 0.086975 | 0.16479 | -0.1236 | 0.31586 | 0.1831 | -0.19684 | 122.0581 | 0.041199 | 122.3282 | 122.4426 | 0 | 122.081 | 0.09613 | 0.27008 | 122.1542 | 122.5937 | 122.3648 | 122.406 | 122.3282 | 122.4609 | 122.4426 | 122.081 | 122.406 | 122.3282 | 122.4426 | 122.3648 | 122.4609 | -0.3067 | -0.28381
1996.0625 | 122.5342 | -122.2961 | 0.1236 | 0.0016785 | 0.013618 | 0.012253 | 0.0091152 | -0.006475 | -0.0092563 | 0.0062099 | 0.018311 | 0.17853 | -0.24719 | 0.14648 | 0.032043 | 0.082397 | -0.009155 | 0.22888 | 0.19684 | -0.21973 | 122.049 | 0.054932 | 122.3145 | 122.4426 | -0.091553 | 122.0764 | 0.073242 | 0.2655 | 122.287 | 122.525 | 122.3282 | 122.4747 | 122.3145 | 122.493 | 122.3785 | 122.0764 | 122.4747 | 122.3145 | 122.3785 | 122.3282 | 122.493 | -0.37079 | -0.34332
1997.8125 | 122.4838 | -122.287 | 0.10529 | -0.005951 | 0.016823 | 0.01503 | 0.0089016 | -0.0066886 | -0.0096835 | 0.0072781 | 0.045776 | 0.15564 | -0.24261 | 0.16022 | 0.054932 | 0.091553 | -0.032043 | 0.25177 | 0.20142 | -0.21515 | 122.0444 | 0.050354 | 122.3328 | 122.4472 | -0.050354 | 122.0718 | 0.09613 | 0.28839 | 122.2549 | 122.5388 | 122.3419 | 122.4426 | 122.3328 | 122.4884 | 122.3785 | 122.0718 | 122.4426 | 122.3328 | 122.3785 | 122.3419 | 122.4884 | -0.3479 | -0.32044
1999.5625 | 122.4655 | -122.3007 | 0.1236 | 0.0016785 | 0.015327 | 0.011612 | 0.0056974 | -0.0022024 | -0.0081881 | 0.0068509 | 0.10529 | 0.1236 | -0.20599 | 0.20599 | 0.10529 | 0.19684 | -0.23346 | 0.3067 | 0.16022 | -0.17853 | 122.0947 | 0 | 122.406 | 122.5067 | -0.01831 | 122.1222 | 0.036621 | 0.31128 | 122.0673 | 122.6074 | 122.406 | 122.4243 | 122.406 | 122.4609 | 122.4976 | 122.1222 | 122.4243 | 122.406 | 122.4976 | 122.406 | 122.4609 | -0.32959 | -0.30212
2001.2344 | 122.5708 | -122.2733 | 0.07782 | 0.0016785 | 0.016396 | 0.0079809 | 0.0044156 | -0.01032 | -0.0071201 | 0.0074917 | 0.064087 | 0.1236 | -0.20599 | 0.17395 | 0.086975 | 0.13275 | -0.054932 | 0.29297 | 0.19226 | -0.2243 | 122.0673 | 0.045776 | 122.3373 | 122.4472 | 0.009155 | 122.0489 | 0.11444 | 0.27008 | 122.2183 | 122.5662 | 122.3602 | 122.3969 | 122.3373 | 122.4655 | 122.406 | 122.0489 | 122.3969 | 122.3373 | 122.406 | 122.3602 | 122.4655 | -0.28381 | -0.30212
2002.9688 | 122.4701 | -122.3373 | 0.12817 | 0.0016785 | 0.01725 | 0.015244 | 0.0097562 | -0.0060478 | -0.0073337 | 0.0081325 | 0.036621 | 0.15106 | -0.22888 | 0.12817 | 0.018311 | 0.064087 | -0.036621 | 0.20599 | 0.20142 | -0.21515 | 122.1085 | 0.022888 | 122.374 | 122.4655 | -0.10986 | 122.1222 | 0.073242 | 0.2655 | 122.3007 | 122.5433 | 122.3557 | 122.4884 | 122.374 | 122.5388 | 122.4014 | 122.1222 | 122.4884 | 122.374 | 122.4014 | 122.3557 | 122.5388 | -0.35706 | -0.34332
2004.7031 | 122.4976 | -122.2916 | 0.11444 | 0.016937 | 0.016182 | 0.010117 | 0.008688 | -0.005834 | -0.0092563 | 0.0047147 | -0.032043 | 0.16479 | -0.24719 | 0.064087 | -0.018311 | 0.027466 | 0.018311 | 0.16479 | 0.19684 | -0.21515 | 122.0444 | 0.050354 | 122.2595 | 122.3557 | -0.13275 | 122.0764 | 0.082397 | 0.21515 | 122.3099 | 122.4564 | 122.2733 | 122.4564 | 122.2595 | 122.4884 | 122.319 | 122.0764 | 122.4564 | 122.2595 | 122.319 | 122.2733 | 122.4884 | -0.36163 | -0.32959
2006.4531 | 122.6212 | -122.2824 | 0.07782 | -0.005951 | 0.015327 | 0.0096899 | 0.0033474 | -0.0066886 | -0.0069065 | 0.0068509 | -0.013733 | 0.17853 | -0.24261 | 0.091553 | 0.018311 | 0.059509 | 0.054932 | 0.20599 | 0.2243 | -0.2243 | 122.0398 | 0.10071 | 122.2687 | 122.374 | -0.059509 | 122.0581 | 0.14648 | 0.22888 | 122.3373 | 122.4884 | 122.3007 | 122.4609 | 122.2687 | 122.5067 | 122.3419 | 122.0581 | 122.4609 | 122.2687 | 122.3419 | 122.3007 | 122.5067 | -0.32044 | -0.30212
2008.125 | 122.5296 | -122.3053 | 0.11444 | 0.0016785 | 0.015114 | 0.011826 | 0.00762 | -0.0045524 | -0.0079745 | 0.0070645 | -0.018311 | 0.16937 | -0.23346 | 0.073242 | -0.013733 | 0.050354 | -0.004578 | 0.15564 | 0.21515 | -0.21515 | 122.0718 | 0.054932 | 122.287 | 122.3785 | -0.12817 | 122.0901 | 0.10071 | 0.21515 | 122.3007 | 122.4609 | 122.2916 | 122.4747 | 122.287 | 122.5204 | 122.3557 | 122.0901 | 122.4747 | 122.287 | 122.3557 | 122.2916 | 122.5204 | -0.3479 | -0.32959
2009.875 | 122.5571 | -122.2961 | 0.086975 | -0.013581 | 0.0149 | 0.010544 | 0.00057041 | -0.0073294 | -0.0066929 | 0.0038601 | 0.073242 | 0.13733 | -0.16937 | 0.20599 | 0.13275 | 0.20599 | -0.15106 | 0.35706 | 0.17853 | -0.20599 | 122.1268 | 0.050354 | 122.3694 | 122.5021 | 0.045776 | 122.0901 | 0.091553 | 0.24261 | 122.1451 | 122.6532 | 122.4289 | 122.4335 | 122.3694 | 122.4747 | 122.5021 | 122.0901 | 122.4335 | 122.3694 | 122.5021 | 122.4289 | 122.4747 | -0.25635 | -0.29297
2011.5625 | 122.4564 | -122.3236 | 0.11444 | 0.0016785 | 0.015327 | 0.011399 | 0.0063382 | -0.0071158 | -0.0071201 | 0.0053555 | 0.09613 | 0.13733 | -0.21515 | 0.20142 | 0.11444 | 0.19684 | -0.20599 | 0.29297 | 0.14191 | -0.17853 | 122.1085 | 0.022888 | 122.4197 | 122.525 | 0 | 122.1451 | 0.027466 | 0.31128 | 122.1176 | 122.6166 | 122.438 | 122.4609 | 122.4197 | 122.4655 | 122.5204 | 122.1451 | 122.4609 | 122.4197 | 122.5204 | 122.438 | 122.4655 | -0.32959 | -0.29297
2013.2344 | 122.5983 | -122.2733 | 0.07782 | -0.013581 | 0.016182 | 0.013749 | 0.0091152 | -0.0079704 | -0.0077609 | 0.0070645 | -0.004578 | 0.15106 | -0.23804 | 0.10529 | 0.018311 | 0.07782 | 0.022888 | 0.23346 | 0.20599 | -0.21057 | 122.0352 | 0.073242 | 122.2687 | 122.3785 | -0.059509 | 122.0627 | 0.12817 | 0.23346 | 122.2961 | 122.5067 | 122.2916 | 122.4243 | 122.2687 | 122.4792 | 122.3511 | 122.0627 | 122.4243 | 122.2687 | 122.3511 | 122.2916 | 122.4792 | -0.31586 | -0.28839
2014.9688 | 122.6028 | -122.2916 | 0.082397 | -0.02121 | 0.014259 | 0.0090491 | 0.006979 | -0.0090384 | -0.0054111 | 0.0064237 | -0.013733 | 0.1831 | -0.2243 | 0.09613 | 0.018311 | 0.050354 | 0.036621 | 0.22888 | 0.21515 | -0.24719 | 122.0673 | 0.10071 | 122.2778 | 122.3877 | -0.064086 | 122.0444 | 0.13275 | 0.21057 | 122.3282 | 122.5204 | 122.3099 | 122.4747 | 122.2778 | 122.5067 | 122.3419 | 122.0444 | 122.4747 | 122.2778 | 122.3419 | 122.3099 | 122.5067 | -0.3067 | -0.32959
2016.6562 | 122.4655 | -122.3282 | 0.1236 | -0.005951 | 0.016182 | 0.014176 | 0.006979 | -0.0039114 | -0.0045565 | 0.0077053 | 0.10529 | 0.10529 | -0.1831 | 0.20142 | 0.10986 | 0.18768 | -0.21057 | 0.31128 | 0.16479 | -0.17395 | 122.1451 | -0.01831 | 122.4335 | 122.5296 | -0.013733 | 122.1542 | 0.041199 | 0.28839 | 122.1176 | 122.6395 | 122.438 | 122.4335 | 122.4335 | 122.493 | 122.5159 | 122.1542 | 122.4335 | 122.4335 | 122.5159 | 122.438 | 122.493 | -0.3067 | -0.29755
2018.4062 | 122.6028 | -122.3145 | 0.091553 | 0.0016785 | 0.016182 | 0.0073401 | 0.0074062 | -0.0069022 | -0.0066929 | 0.0055691 | -0.004578 | 0.19226 | -0.25177 | 0.10529 | 0.004578 | 0.041199 | 0.036621 | 0.20599 | 0.20142 | -0.22888 | 122.0627 | 0.10071 | 122.3099 | 122.4197 | -0.086975 | 122.0856 | 0.10986 | 0.24719 | 122.3511 | 122.5204 | 122.319 | 122.5067 | 122.3099 | 122.5159 | 122.3557 | 122.0856 | 122.5067 | 122.3099 | 122.3557 | 122.319 | 122.5159 | -0.34332 | -0.32044
2020.1406 | 122.6166 | -122.3145 | 0.091553 | 0.0016785 | 0.015541 | 0.011612 | 0.0046292 | -0.0077566 | -0.0062655 | 0.0072781 | 0.045776 | 0.14191 | -0.21057 | 0.1236 | 0.059509 | 0.091553 | 0 | 0.26093 | 0.19684 | -0.21973 | 122.1039 | 0.050354 | 122.3602 | 122.438 | -0.032044 | 122.0947 | 0.10529 | 0.25635 | 122.3145 | 122.5754 | 122.374 | 122.4564 | 122.3602 | 122.5113 | 122.406 | 122.0947 | 122.4564 | 122.3602 | 122.406 | 122.374 | 122.5113 | -0.30212 | -0.31128
2021.8906 | 122.4838 | -122.3328 | 0.11444 | 0.009308 | 0.014473 | 0.0094763 | 0.0063382 | -0.0049796 | -0.0058383 | 0.0068509 | 0.09613 | 0.1236 | -0.1831 | 0.17853 | 0.091553 | 0.18768 | -0.1831 | 0.28839 | 0.16022 | -0.18768 | 122.1497 | 0.009155 | 122.4289 | 122.5113 | -0.022888 | 122.1451 | 0.045776 | 0.27924 | 122.1497 | 122.6212 | 122.4243 | 122.4564 | 122.4289 | 122.493 | 122.5204 | 122.1451 | 122.4564 | 122.4289 | 122.5204 | 122.4243 | 122.493 | -0.29755 | -0.30212
2023.5781 | 122.5296 | -122.3328 | 0.11444 | -0.005951 | 0.015327 | 0.012253 | 0.01232 | -0.005834 | -0.0066929 | 0.0072781 | -0.004578 | 0.15106 | -0.24261 | 0.086975 | -0.018311 | 0.054932 | 0.013733 | 0.17853 | 0.19684 | -0.21515 | 122.0901 | 0.036621 | 122.3282 | 122.4197 | -0.13275 | 122.1176 | 0.082397 | 0.23804 | 122.3465 | 122.5113 | 122.3145 | 122.4838 | 122.3282 | 122.5296 | 122.3877 | 122.1176 | 122.4838 | 122.3282 | 122.3877 | 122.3145 | 122.5296 | -0.35706 | -0.32959
2025.3125 | 122.525 | -122.3328 | 0.10986 | 0.0016785 | 0.016823 | 0.0079809 | 0.0078336 | -0.0036978 | -0.0077609 | 0.0064237 | -0.004578 | 0.16479 | -0.25177 | 0.10071 | -0.018311 | 0.054932 | -0.004578 | 0.16937 | 0.20599 | -0.21515 | 122.081 | 0.054932 | 122.3282 | 122.4335 | -0.12817 | 122.1176 | 0.096131 | 0.24719 | 122.3282 | 122.5021 | 122.3145 | 122.4976 | 122.3282 | 122.5388 | 122.3877 | 122.1176 | 122.4976 | 122.3282 | 122.3877 | 122.3145 | 122.5388 | -0.36163 | -0.32501
2027.0469 | 122.5845 | -122.3053 | 0.09613 | -0.005951 | 0.012978 | 0.01204 | 0.0016384 | -0.0062614 | -0.0058383 | 0.0053555 | 0.036621 | 0.11902 | -0.19226 | 0.13733 | 0.054932 | 0.14648 | -0.1236 | 0.2655 | 0.1831 | -0.21057 | 122.113 | 0.022889 | 122.3419 | 122.4426 | -0.041198 | 122.0947 | 0.086975 | 0.22888 | 122.1817 | 122.5708 | 122.3602 | 122.4243 | 122.3419 | 122.4884 | 122.4518 | 122.0947 | 122.4243 | 122.3419 | 122.4518 | 122.3602 | 122.4884 | -0.28839 | -0.3067
2028.7969 | 122.5433 | -122.3282 | 0.09613 | 0.0016785 | 0.015541 | 0.013108 | 0.0037748 | -0.0079704 | -0.0075473 | 0.0070645 | 0.082397 | 0.14648 | -0.20599 | 0.15564 | 0.07782 | 0.15564 | -0.14648 | 0.27008 | 0.16022 | -0.19684 | 122.1222 | 0.050354 | 122.4106 | 122.4838 | -0.01831 | 122.1313 | 0.064087 | 0.28839 | 122.1817 | 122.5983 | 122.406 | 122.4747 | 122.4106 | 122.4884 | 122.4838 | 122.1313 | 122.4747 | 122.4106 | 122.4838 | 122.406 | 122.4884 | -0.30212 | -0.29297
2030.4688 | 122.5983 | -122.3145 | 0.086975 | -0.005951 | 0.014046 | 0.013535 | 0.0014248 | -0.009893 | -0.0062655 | 0.0057827 | 0.073242 | 0.12817 | -0.19684 | 0.19226 | 0.10986 | 0.17853 | -0.13275 | 0.32959 | 0.18768 | -0.21057 | 122.1176 | 0.041199 | 122.3877 | 122.5067 | 0.022888 | 122.1039 | 0.10071 | 0.27008 | 122.1817 | 122.644 | 122.4243 | 122.4426 | 122.3877 | 122.5021 | 122.493 | 122.1039 | 122.4426 | 122.3877 | 122.493 | 122.4243 | 122.5021 | -0.28381 | -0.29755
2032.2031 | 122.5662 | -122.3236 | 0.10071 | -0.013581 | 0.015114 | 0.011399 | 0.0056974 | -0.008184 | -0.0088291 | 0.0053555 | 0.09613 | 0.11444 | -0.18768 | 0.2243 | 0.1236 | 0.18768 | -0.13275 | 0.36163 | 0.14648 | -0.19684 | 122.1359 | 0.013733 | 122.4197 | 122.5479 | 0.022888 | 122.1268 | 0.045776 | 0.28381 | 122.1909 | 122.6852 | 122.4472 | 122.438 | 122.4197 | 122.4701 | 122.5113 | 122.1268 | 122.438 | 122.4197 | 122.5113 | 122.4472 | 122.4701 | -0.28839 | -0.29755
2033.9531 | 122.5754 | -122.319 | 0.09613 | -0.005951 | 0.013618 | 0.010117 | 0.006979 | -0.0062614 | -0.0045565 | 0.0053555 | 0.09613 | 0.14191 | -0.20599 | 0.23804 | 0.11444 | 0.18768 | -0.14191 | 0.3479 | 0.17395 | -0.17395 | 122.113 | 0.045777 | 122.4152 | 122.5571 | 0.018311 | 122.1451 | 0.07782 | 0.30212 | 122.1771 | 122.6669 | 122.4335 | 122.4609 | 122.4152 | 122.493 | 122.5067 | 122.1451 | 122.4609 | 122.4152 | 122.5067 | 122.4335 | 122.493 | -0.30212 | -0.27008
2035.625 | 122.5021 | -122.3511 | 0.13733 | -0.005951 | 0.016182 | 0.012253 | 0.011252 | -0.0060478 | -0.010752 | 0.0064237 | 0.041199 | 0.15564 | -0.24719 | 0.16937 | 0.045776 | 0.10071 | -0.045776 | 0.26093 | 0.19226 | -0.19684 | 122.1039 | 0.018311 | 122.3923 | 122.5204 | -0.091553 | 122.1542 | 0.054932 | 0.28839 | 122.3053 | 122.612 | 122.3969 | 122.5067 | 122.3923 | 122.5433 | 122.4518 | 122.1542 | 122.5067 | 122.3923 | 122.4518 | 122.3969 | 122.5433 | -0.38452 | -0.33417
2037.3906 | 122.5754 | -122.3145 | 0.091553 | -0.005951 | 0.012978 | 0.010544 | 0.0046292 | -0.0079704 | -0.0075473 | 0.0057827 | 0.091553 | 0.12817 | -0.19684 | 0.2243 | 0.1236 | 0.18768 | -0.13275 | 0.35706 | 0.16937 | -0.19226 | 122.1176 | 0.036621 | 122.406 | 122.5388 | 0.032043 | 122.1222 | 0.07782 | 0.28839 | 122.1817 | 122.6715 | 122.438 | 122.4426 | 122.406 | 122.4838 | 122.5021 | 122.1222 | 122.4426 | 122.406 | 122.5021 | 122.438 | 122.4838 | -0.28839 | -0.28381
2039.0625 | 122.5067 | -122.374 | 0.11902 | -0.013581 | 0.016823 | 0.0094763 | 0.011465 | -0.004766 | -0.0096835 | 0.0068509 | 0.041199 | 0.14191 | -0.25177 | 0.15106 | 0.032043 | 0.09613 | -0.050354 | 0.2243 | 0.18768 | -0.2243 | 122.1222 | 0.022888 | 122.4152 | 122.525 | -0.086976 | 122.1497 | 0.068664 | 0.29297 | 122.3236 | 122.5983 | 122.406 | 122.5159 | 122.4152 | 122.5616 | 122.4701 | 122.1497 | 122.5159 | 122.4152 | 122.4701 | 122.406 | 122.5616 | -0.37079 | -0.34332
2040.7969 | 122.5571 | -122.3602 | 0.13275 | 0.009308 | 0.0149 | 0.012253 | 0.0084744 | -0.0069022 | -0.0058383 | 0.0062099 | -0.013733 | 0.15564 | -0.23804 | 0.091553 | -0.013733 | 0.032043 | 0.004578 | 0.16479 | 0.21515 | -0.2243 | 122.1222 | 0.022889 | 122.3465 | 122.4518 | -0.14648 | 122.1359 | 0.082398 | 0.2243 | 122.3648 | 122.525 | 122.3465 | 122.5159 | 122.3465 | 122.5754 | 122.3923 | 122.1359 | 122.5159 | 122.3465 | 122.3923 | 122.3465 | 122.5754 | -0.37079 | -0.35706
2042.5 | 122.5845 | -122.3373 | 0.091553 | 0.009308 | 0.014687 | 0.0075537 | 0.0014248 | -0.009252 | -0.0043429 | 0.0070645 | 0.086975 | 0.12817 | -0.19226 | 0.21515 | 0.15106 | 0.19226 | -0.15106 | 0.3479 | 0.16937 | -0.17395 | 122.1451 | 0.036621 | 122.4243 | 122.5525 | 0.059509 | 122.1634 | 0.07782 | 0.27924 | 122.1863 | 122.6852 | 122.4884 | 122.4655 | 122.4243 | 122.5067 | 122.5296 | 122.1634 | 122.4655 | 122.4243 | 122.5296 | 122.4884 | 122.5067 | -0.28381 | -0.2655
2044.25 | 122.6395 | -122.3282 | 0.09613 | 0.0016785 | 0.016396 | 0.010331 | 0.0078336 | -0.010961 | -0.0062655 | 0.0066373 | -0.027466 | 0.16479 | -0.27008 | 0.10071 | 0.022888 | 0.050354 | 0.041199 | 0.20142 | 0.21515 | -0.24261 | 122.0581 | 0.068665 | 122.3007 | 122.4289 | -0.073242 | 122.0856 | 0.11902 | 0.24262 | 122.3694 | 122.5296 | 122.3511 | 122.493 | 122.3007 | 122.5433 | 122.3785 | 122.0856 | 122.493 | 122.3007 | 122.3785 | 122.3511 | 122.5433 | -0.36621 | -0.33874
2046 | 122.5204 | -122.374 | 0.11444 | -0.005951 | 0.013618 | 0.01738 | 0.0093288 | -0.0079704 | -0.0069065 | 0.0057827 | 0.027466 | 0.15564 | -0.2243 | 0.11444 | 0.009155 | 0.07782 | -0.036621 | 0.19684 | 0.21973 | -0.21057 | 122.1497 | 0.041199 | 122.4014 | 122.4884 | -0.10529 | 122.1634 | 0.10529 | 0.25177 | 122.3373 | 122.5708 | 122.3831 | 122.5296 | 122.4014 | 122.5937 | 122.4518 | 122.1634 | 122.5296 | 122.4014 | 122.4518 | 122.3831 | 122.5937 | -0.33875 | -0.32501
2047.6719 | 122.5891 | -122.3557 | 0.09613 | 0.0016785 | 0.015327 | 0.0071265 | 0.0014248 | -0.0077566 | -0.0056247 | 0.0055691 | 0.082397 | 0.11444 | -0.18768 | 0.20599 | 0.1236 | 0.19684 | -0.13275 | 0.35706 | 0.17395 | -0.19684 | 122.168 | 0.018311 | 122.438 | 122.5616 | 0.027466 | 122.1588 | 0.07782 | 0.27008 | 122.2229 | 122.7127 | 122.4792 | 122.4701 | 122.438 | 122.5296 | 122.5525 | 122.1588 | 122.4701 | 122.438 | 122.5525 | 122.4792 | 122.5296 | -0.28381 | -0.29297
2049.4219 | 122.5891 | -122.3419 | 0.10071 | -0.013581 | 0.0149 | 0.016953 | 0.0095426 | -0.0054068 | -0.0073337 | 0.0077053 | 0.004578 | 0.15564 | -0.24261 | 0.13275 | 0.032043 | 0.086975 | 0.004578 | 0.23346 | 0.21515 | -0.21515 | 122.0993 | 0.054932 | 122.3465 | 122.4747 | -0.068665 | 122.1268 | 0.11444 | 0.24719 | 122.3465 | 122.5754 | 122.374 | 122.4976 | 122.3465 | 122.5571 | 122.4289 | 122.1268 | 122.4976 | 122.3465 | 122.4289 | 122.374 | 122.5571 | -0.34332 | -0.31586
2051.1562 | 122.5159 | -122.3877 | 0.13733 | -0.005951 | 0.018105 | 0.012681 | 0.0097562 | -0.0056204 | -0.0069065 | 0.0057827 | 0.050354 | 0.14648 | -0.2243 | 0.15106 | 0.050354 | 0.10986 | -0.045776 | 0.24261 | 0.20599 | -0.21515 | 122.1634 | 0.009155 | 122.438 | 122.5388 | -0.086975 | 122.1725 | 0.068665 | 0.27466 | 122.3419 | 122.6303 | 122.438 | 122.5342 | 122.438 | 122.5937 | 122.4976 | 122.1725 | 122.5342 | 122.438 | 122.4976 | 122.438 | 122.5937 | -0.36163 | -0.35248
2052.9062 | 122.6212 | -122.3373 | 0.082397 | -0.005951 | 0.014046 | 0.015885 | 0.0029202 | -0.0062614 | -0.0045565 | 0.0066373 | 0.091553 | 0.12817 | -0.19684 | 0.18768 | 0.10986 | 0.16937 | -0.09613 | 0.32959 | 0.16479 | -0.18768 | 122.1405 | 0.045777 | 122.4289 | 122.525 | 0.027466 | 122.1497 | 0.082398 | 0.28839 | 122.2412 | 122.6669 | 122.4472 | 122.4655 | 122.4289 | 122.5021 | 122.5067 | 122.1497 | 122.4655 | 122.4289 | 122.5067 | 122.4472 | 122.5021 | -0.27924 | -0.27008
2054.5781 | 122.5662 | -122.3557 | 0.1236 | -0.005951 | 0.015327 | 0.01204 | 0.0089016 | -0.0049796 | -0.0081881 | 0.0079189 | -0.036621 | 0.17395 | -0.25177 | 0.064087 | -0.041199 | 0.022888 | 0.022888 | 0.14648 | 0.20142 | -0.21057 | 122.1039 | 0.050354 | 122.319 | 122.4197 | -0.16479 | 122.1451 | 0.07782 | 0.21515 | 122.3785 | 122.5021 | 122.3145 | 122.5296 | 122.319 | 122.5571 | 122.3785 | 122.1451 | 122.5296 | 122.319 | 122.3785 | 122.3145 | 122.5571 | -0.37537 | -0.33417
2056.3281 | 122.6349 | -122.3099 | 0.07782 | -0.005951 | 0.015755 | 0.011185 | 0.0020658 | -0.0088248 | -0.0047703 | 0.0062099 | 0.013733 | 0.15106 | -0.21973 | 0.13733 | 0.07782 | 0.14648 | -0.11902 | 0.27008 | 0.1831 | -0.20142 | 122.0901 | 0.073242 | 122.3236 | 122.4472 | 0 | 122.1085 | 0.10528 | 0.23346 | 122.1909 | 122.58 | 122.3877 | 122.4609 | 122.3236 | 122.493 | 122.4564 | 122.1085 | 122.4609 | 122.3236 | 122.4564 | 122.3877 | 122.493 | -0.29755 | -0.27924
2058.0781 | 122.6486 | -122.3419 | 0.086975 | -0.005951 | 0.014687 | 0.0088355 | 0.008688 | -0.007543 | -0.0086155 | 0.0045011 | -0.032043 | 0.17395 | -0.23804 | 0.07782 | -0.009155 | 0.041199 | 0.068665 | 0.19684 | 0.21057 | -0.2243 | 122.1039 | 0.086975 | 122.3099 | 122.4197 | -0.09613 | 122.1176 | 0.1236 | 0.20599 | 122.4106 | 122.5388 | 122.3328 | 122.5159 | 122.3099 | 122.5525 | 122.3831 | 122.1176 | 122.5159 | 122.3099 | 122.3831 | 122.3328 | 122.5525 | -0.32501 | -0.31128
2059.8281 | 122.5159 | -122.3465 | 0.10529 | 0.0016785 | 0.015114 | 0.012467 | 0.00527 | -0.0045524 | -0.0066929 | 0.0059963 | 0.10529 | 0.11902 | -0.1831 | 0.21057 | 0.11444 | 0.19684 | -0.20599 | 0.31586 | 0.16022 | -0.18768 | 122.1634 | 0.013733 | 122.4518 | 122.5571 | 0.009155 | 122.1588 | 0.054931 | 0.28839 | 122.1405 | 122.6624 | 122.4609 | 122.4655 | 122.4518 | 122.5067 | 122.5433 | 122.1588 | 122.4655 | 122.4518 | 122.5433 | 122.4609 | 122.5067 | -0.28839 | -0.29297
2061.5156 | 122.5708 | -122.3557 | 0.1236 | -0.005951 | 0.015327 | 0.013962 | 0.0091152 | -0.0071158 | -0.0064791 | 0.0045011 | 0.022888 | 0.16479 | -0.24261 | 0.14648 | 0.027466 | 0.10071 | -0.027466 | 0.23804 | 0.21973 | -0.2243 | 122.113 | 0.041199 | 122.3785 | 122.5021 | -0.09613 | 122.1313 | 0.096131 | 0.2655 | 122.3282 | 122.5937 | 122.3831 | 122.5204 | 122.3785 | 122.5754 | 122.4564 | 122.1313 | 122.5204 | 122.3785 | 122.4564 | 122.3831 | 122.5754 | -0.36621 | -0.3479
2063.2656 | 122.5616 | -122.3602 | 0.11444 | 0.0016785 | 0.016823 | 0.011826 | 0.0044156 | -0.0086112 | -0.0064791 | 0.0074917 | 0.073242 | 0.1236 | -0.19684 | 0.16937 | 0.086975 | 0.17395 | -0.18768 | 0.29297 | 0.15564 | -0.1831 | 122.1634 | 0.009155 | 122.4335 | 122.5296 | -0.027466 | 122.1771 | 0.041199 | 0.27008 | 122.1725 | 122.6532 | 122.4472 | 122.4838 | 122.4335 | 122.5159 | 122.5342 | 122.1771 | 122.4838 | 122.4335 | 122.5342 | 122.4472 | 122.5159 | -0.31128 | -0.29755
2065.0156 | 122.5983 | -122.3511 | 0.09613 | -0.005951 | 0.015114 | 0.0077673 | 0.0012112 | -0.008184 | -0.0032749 | 0.0072781 | 0.082397 | 0.11902 | -0.20142 | 0.21057 | 0.13733 | 0.19684 | -0.15106 | 0.35706 | 0.17395 | -0.1831 | 122.1497 | 0.022889 | 122.4335 | 122.5616 | 0.041199 | 122.168 | 0.07782 | 0.28381 | 122.2 | 122.7081 | 122.4884 | 122.4701 | 122.4335 | 122.525 | 122.5479 | 122.168 | 122.4701 | 122.4335 | 122.5479 | 122.4884 | 122.525 | -0.29755 | -0.27924
2066.7031 | 122.6395 | -122.3465 | 0.091553 | -0.013581 | 0.015327 | 0.0086219 | 0.004202 | -0.008184 | -0.0066929 | 0.0081325 | 0.036621 | 0.12817 | -0.20599 | 0.14648 | 0.054932 | 0.13275 | -0.11902 | 0.24719 | 0.16479 | -0.21515 | 122.1405 | 0.036621 | 122.3831 | 122.493 | -0.036621 | 122.1313 | 0.073242 | 0.24262 | 122.2275 | 122.5937 | 122.4014 | 122.4747 | 122.3831 | 122.5113 | 122.4792 | 122.1313 | 122.4747 | 122.3831 | 122.4792 | 122.4014 | 122.5113 | -0.29755 | -0.3067
2068.4531 | 122.5021 | -122.3877 | 0.10071 | 0.0016785 | 0.015541 | 0.0084083 | 0.0078336 | -0.0056204 | -0.0066929 | 0.0066373 | 0.10529 | 0.12817 | -0.18768 | 0.21515 | 0.10071 | 0.20142 | -0.2243 | 0.30212 | 0.16479 | -0.16022 | 122.2 | 0.027466 | 122.493 | 122.6028 | 0 | 122.2275 | 0.064087 | 0.29297 | 122.1634 | 122.6898 | 122.4884 | 122.5159 | 122.493 | 122.5525 | 122.5891 | 122.2275 | 122.5159 | 122.493 | 122.5891 | 122.4884 | 122.5525 | -0.28839 | -0.26093
2070.125 | 122.644 | -122.3511 | 0.086975 | -0.005951 | 0.0149 | 0.012467 | 0.002493 | -0.0094656 | -0.0056247 | 0.0051419 | 0.045776 | 0.13733 | -0.20142 | 0.17853 | 0.086975 | 0.16937 | -0.12817 | 0.30212 | 0.17395 | -0.20599 | 122.1497 | 0.050354 | 122.3969 | 122.5296 | 0 | 122.1451 | 0.086975 | 0.24719 | 122.2229 | 122.6532 | 122.438 | 122.4884 | 122.3969 | 122.525 | 122.5204 | 122.1451 | 122.4884 | 122.3969 | 122.5204 | 122.438 | 122.525 | -0.28839 | -0.29297
2071.8594 | 122.612 | -122.3557 | 0.10071 | -0.013581 | 0.015541 | 0.013321 | 0.011252 | -0.0069022 | -0.0041293 | 0.0068509 | 0.027466 | 0.16937 | -0.23346 | 0.14191 | 0.027466 | 0.086975 | -0.018311 | 0.23346 | 0.20599 | -0.19684 | 122.1222 | 0.068665 | 122.3831 | 122.4976 | -0.073242 | 122.1588 | 0.10529 | 0.26093 | 122.3373 | 122.5891 | 122.3831 | 122.525 | 122.3831 | 122.5616 | 122.4426 | 122.1588 | 122.525 | 122.3831 | 122.4426 | 122.3831 | 122.5616 | -0.33417 | -0.29755
2073.6094 | 122.612 | -122.3557 | 0.10529 | 0.0016785 | 0.014259 | 0.0096899 | 0.0016384 | -0.0083976 | -0.0060519 | 0.0051419 | 0.11902 | 0.11444 | -0.21515 | 0.21973 | 0.11902 | 0.19684 | -0.15106 | 0.36621 | 0.16937 | -0.21057 | 122.1405 | 0.009155 | 122.4747 | 122.5754 | 0.013733 | 122.1451 | 0.064087 | 0.33417 | 122.2046 | 122.7219 | 122.4747 | 122.4701 | 122.4747 | 122.525 | 122.5525 | 122.1451 | 122.4701 | 122.4747 | 122.5525 | 122.4747 | 122.525 | -0.32044 | -0.31586
2075.3438 | 122.5571 | -122.3831 | 0.09613 | -0.005951 | 0.017036 | 0.014817 | 0.010183 | -0.006475 | -0.010538 | 0.0083463 | 0.045776 | 0.17395 | -0.23346 | 0.16937 | 0.032043 | 0.10071 | -0.041199 | 0.25177 | 0.20599 | -0.21973 | 122.1497 | 0.07782 | 122.4289 | 122.5525 | -0.064087 | 122.1634 | 0.10986 | 0.27924 | 122.3419 | 122.6349 | 122.4152 | 122.5571 | 122.4289 | 122.5891 | 122.4838 | 122.1634 | 122.5571 | 122.4289 | 122.4838 | 122.4152 | 122.5891 | -0.32959 | -0.31586
2077.0938 | 122.6669 | -122.3602 | 0.082397 | 0.0016785 | 0.014259 | 0.0092627 | 0.0046292 | -0.0077566 | -0.0096835 | 0.0062099 | -0.022888 | 0.17395 | -0.25177 | 0.10071 | 0.009155 | 0.054932 | 0.045776 | 0.19226 | 0.20142 | -0.2243 | 122.1085 | 0.091553 | 122.3373 | 122.4609 | -0.073242 | 122.1359 | 0.11902 | 0.22888 | 122.406 | 122.5525 | 122.3694 | 122.5342 | 122.3373 | 122.5616 | 122.4152 | 122.1359 | 122.5342 | 122.3373 | 122.4152 | 122.3694 | 122.5616 | -0.33417 | -0.3067
2078.7812 | 122.6028 | -122.3694 | 0.11444 | -0.005951 | 0.018532 | 0.010758 | 0.0089016 | -0.0054068 | -0.0066929 | 0.0062099 | 0 | 0.16479 | -0.2243 | 0.13733 | 0.036621 | 0.10071 | -0.013733 | 0.23346 | 0.21057 | -0.20142 | 122.1451 | 0.050354 | 122.3694 | 122.5067 | -0.07782 | 122.168 | 0.09613 | 0.2243 | 122.3557 | 122.6028 | 122.406 | 122.5342 | 122.3694 | 122.58 | 122.4701 | 122.168 | 122.5342 | 122.3694 | 122.4701 | 122.406 | 122.58 | -0.33875 | -0.31586
2080.5312 | 122.6852 | -122.374 | 0.073242 | -0.013581 | 0.015541 | 0.0092627 | 0.0067654 | -0.0060478 | -0.0075473 | 0.0074917 | -0.013733 | 0.17853 | -0.23346 | 0.07782 | 0.004578 | 0.041199 | 0.054932 | 0.20599 | 0.21057 | -0.23346 | 122.1405 | 0.10529 | 122.3602 | 122.4518 | -0.068664 | 122.1405 | 0.13733 | 0.21973 | 122.4289 | 122.58 | 122.3785 | 122.5525 | 122.3602 | 122.5845 | 122.4152 | 122.1405 | 122.5525 | 122.3602 | 122.4152 | 122.3785 | 122.5845 | -0.3067 | -0.3067
2082.2656 | 122.612 | -122.374 | 0.10071 | -0.005951 | 0.014046 | 0.0075537 | 0.00057041 | -0.0073294 | -0.0069065 | 0.0057827 | 0.082397 | 0.1236 | -0.21057 | 0.21057 | 0.1236 | 0.19226 | -0.1236 | 0.33875 | 0.17395 | -0.18768 | 122.1634 | 0.022888 | 122.4564 | 122.5845 | 0.022888 | 122.1863 | 0.073242 | 0.29297 | 122.2504 | 122.7127 | 122.4976 | 122.4976 | 122.4564 | 122.5479 | 122.5662 | 122.1863 | 122.4976 | 122.4564 | 122.5662 | 122.4976 | 122.5479 | -0.31128 | -0.28839
2083.9375 | 122.6395 | -122.3511 | 0.086975 | -0.005951 | 0.014259 | 0.012894 | 0.0031338 | -0.0056204 | -0.0058383 | 0.0066373 | 0.045776 | 0.1236 | -0.19226 | 0.15106 | 0.054932 | 0.15106 | -0.11444 | 0.25635 | 0.20599 | -0.19684 | 122.1588 | 0.036621 | 122.3969 | 122.5021 | -0.032043 | 122.1542 | 0.11902 | 0.23804 | 122.2366 | 122.6074 | 122.406 | 122.4747 | 122.3969 | 122.5571 | 122.5021 | 122.1542 | 122.4747 | 122.3969 | 122.5021 | 122.406 | 122.5571 | -0.27924 | -0.28381
2085.6875 | 122.5479 | -122.3969 | 0.1236 | 0.0016785 | 0.015327 | 0.012253 | 0.0080472 | -0.0073294 | -0.0086155 | 0.0072781 | 0.11902 | 0.10529 | -0.18768 | 0.20142 | 0.11444 | 0.1831 | -0.19226 | 0.3067 | 0.16022 | -0.17853 | 122.2092 | -0.01831 | 122.5159 | 122.5983 | -0.009155 | 122.2183 | 0.036621 | 0.3067 | 122.2046 | 122.7036 | 122.5113 | 122.5021 | 122.5159 | 122.5571 | 122.58 | 122.2183 | 122.5021 | 122.5159 | 122.58 | 122.5113 | 122.5571 | -0.31128 | -0.30212
2087.4531 | 122.5708 | -122.3923 | 0.1236 | 0.0016785 | 0.021736 | 0.011399 | 0.010824 | -0.006475 | -0.0056247 | 0.0053555 | 0.041199 | 0.1831 | -0.2243 | 0.091553 | -0.022888 | 0.036621 | -0.013733 | 0.17395 | 0.19684 | -0.20599 | 122.168 | 0.059509 | 122.4335 | 122.4838 | -0.14648 | 122.1863 | 0.073242 | 0.2655 | 122.3785 | 122.5662 | 122.3694 | 122.5754 | 122.4335 | 122.5891 | 122.4289 | 122.1863 | 122.5754 | 122.4335 | 122.4289 | 122.3694 | 122.5891 | -0.3479 | -0.32959
2089.125 | 122.5433 | -122.4197 | 0.13275 | -0.005951 | 0.012764 | 0.010758 | 0.0048428 | -0.006475 | -0.0062655 | 0.0053555 | 0.086975 | 0.11444 | -0.21973 | 0.20599 | 0.11444 | 0.18768 | -0.1831 | 0.3067 | 0.16022 | -0.17395 | 122.2 | -0.01831 | 122.5067 | 122.6257 | -0.01831 | 122.2458 | 0.027466 | 0.3067 | 122.2366 | 122.7264 | 122.5342 | 122.5342 | 122.5067 | 122.58 | 122.6074 | 122.2458 | 122.5342 | 122.5067 | 122.6074 | 122.5342 | 122.58 | -0.35248 | -0.3067
2090.875 | 122.612 | -122.3877 | 0.09613 | -0.005951 | 0.013191 | 0.014176 | 0.001852 | -0.0079704 | -0.0047703 | 0.0051419 | 0.073242 | 0.1236 | -0.20142 | 0.2243 | 0.1236 | 0.19684 | -0.13733 | 0.34332 | 0.16022 | -0.19684 | 122.1863 | 0.027466 | 122.4609 | 122.612 | 0.027466 | 122.1909 | 0.064087 | 0.27466 | 122.2504 | 122.731 | 122.5113 | 122.5113 | 122.4609 | 122.5479 | 122.5845 | 122.1909 | 122.5113 | 122.4609 | 122.5845 | 122.5113 | 122.5479 | -0.29755 | -0.29297
2092.625 | 122.5937 | -122.3602 | 0.10986 | -0.005951 | 0.017036 | 0.01503 | 0.0099698 | -0.0051932 | -0.0084017 | 0.0079189 | -0.027466 | 0.16479 | -0.24719 | 0.086975 | -0.027466 | 0.036621 | -0.009155 | 0.14191 | 0.21515 | -0.21515 | 122.113 | 0.054932 | 122.3328 | 122.4472 | -0.13733 | 122.1451 | 0.10529 | 0.21973 | 122.3511 | 122.5021 | 122.3328 | 122.525 | 122.3328 | 122.5754 | 122.3969 | 122.1451 | 122.525 | 122.3328 | 122.3969 | 122.3328 | 122.5754 | -0.35706 | -0.32501
2094.3594 | 122.5433 | -122.3877 | 0.13275 | -0.013581 | 0.015541 | 0.01439 | 0.0074062 | -0.005834 | -0.0064791 | 0.0066373 | 0.054932 | 0.14648 | -0.21057 | 0.16937 | 0.07782 | 0.16937 | -0.15564 | 0.27466 | 0.18768 | -0.1831 | 122.1771 | 0.013733 | 122.4426 | 122.5571 | -0.054931 | 122.2046 | 0.054932 | 0.2655 | 122.2321 | 122.6624 | 122.4655 | 122.5342 | 122.4426 | 122.5754 | 122.5571 | 122.2046 | 122.5342 | 122.4426 | 122.5571 | 122.4655 | 122.5754 | -0.34332 | -0.31586
2096.0938 | 122.6578 | -122.3694 | 0.07782 | -0.005951 | 0.015541 | 0.0096899 | 0.002493 | -0.0077566 | -0.0051975 | 0.0059963 | 0.032043 | 0.11444 | -0.21057 | 0.13275 | 0.064087 | 0.15106 | -0.10986 | 0.24719 | 0.16479 | -0.19226 | 122.1588 | 0.036621 | 122.4014 | 122.5021 | -0.013733 | 122.1771 | 0.086975 | 0.24261 | 122.2595 | 122.6166 | 122.4335 | 122.4838 | 122.4014 | 122.5342 | 122.5204 | 122.1771 | 122.4838 | 122.4014 | 122.5204 | 122.4335 | 122.5342 | -0.28839 | -0.27008
2097.8594 | 122.6761 | -122.3694 | 0.086975 | -0.005951 | 0.014046 | 0.0075537 | 0.001852 | -0.010107 | -0.0039157 | 0.0066373 | 0.041199 | 0.14191 | -0.19684 | 0.17853 | 0.07782 | 0.17395 | -0.1236 | 0.29755 | 0.16022 | -0.20142 | 122.1725 | 0.054932 | 122.4106 | 122.5479 | -0.009155 | 122.168 | 0.073242 | 0.23804 | 122.2458 | 122.6669 | 122.4472 | 122.5113 | 122.4106 | 122.5296 | 122.5433 | 122.168 | 122.5113 | 122.4106 | 122.5433 | 122.4472 | 122.5296 | -0.28381 | -0.28839
2099.5469 | 122.6624 | -122.406 | 0.086975 | 0.009308 | 0.016823 | 0.0096899 | 0.0093288 | -0.0088248 | -0.0075473 | 0.0042873 | -0.009155 | 0.16937 | -0.22888 | 0.1236 | 0.027466 | 0.082397 | 0.022888 | 0.22888 | 0.21973 | -0.21057 | 122.1771 | 0.082398 | 122.3969 | 122.5296 | -0.059509 | 122.1954 | 0.13275 | 0.21973 | 122.4289 | 122.6349 | 122.4335 | 122.5754 | 122.3969 | 122.6257 | 122.4884 | 122.1954 | 122.5754 | 122.3969 | 122.4884 | 122.4335 | 122.6257 | -0.31586 | -0.29755
2101.2969 | 122.5662 | -122.406 | 0.11444 | 0.0016785 | 0.013405 | 0.0094763 | 0.0037748 | -0.0066886 | -0.0069065 | 0.0053555 | 0.086975 | 0.10986 | -0.21057 | 0.18768 | 0.10071 | 0.16937 | -0.17853 | 0.29297 | 0.16479 | -0.20599 | 122.1954 | -0.004578 | 122.493 | 122.5937 | -0.013733 | 122.2 | 0.050354 | 0.29755 | 122.2275 | 122.699 | 122.5067 | 122.5159 | 122.493 | 122.5708 | 122.5754 | 122.2 | 122.5159 | 122.493 | 122.5754 | 122.5067 | 122.5708 | -0.32501 | -0.32044
2103.0312 | 122.6486 | -122.374 | 0.086975 | 0.0016785 | 0.016182 | 0.0081947 | 0.0044156 | -0.006475 | -0.0054111 | 0.0038601 | 0.091553 | 0.11902 | -0.19226 | 0.2243 | 0.11444 | 0.18768 | -0.12817 | 0.34332 | 0.16937 | -0.18768 | 122.1817 | 0.032044 | 122.4655 | 122.5983 | 0.027466 | 122.1863 | 0.082398 | 0.28381 | 122.2458 | 122.7173 | 122.4884 | 122.493 | 122.4655 | 122.5433 | 122.5616 | 122.1863 | 122.493 | 122.4655 | 122.5616 | 122.4884 | 122.5433 | -0.27924 | -0.27466
2104.7031 | 122.6532 | -122.3511 | 0.10071 | -0.005951 | 0.0149 | 0.013108 | 0.011038 | -0.0073294 | -0.0066929 | 0.0042873 | 0.004578 | 0.16479 | -0.2243 | 0.13275 | 0.018311 | 0.082397 | 0 | 0.2243 | 0.21515 | -0.21973 | 122.1268 | 0.064087 | 122.3557 | 122.4838 | -0.082397 | 122.1313 | 0.11444 | 0.22888 | 122.3511 | 122.5754 | 122.3694 | 122.5159 | 122.3557 | 122.5662 | 122.4335 | 122.1313 | 122.5159 | 122.3557 | 122.4335 | 122.3694 | 122.5662 | -0.32501 | -0.32044
2106.4531 | 122.612 | -122.4243 | 0.1236 | 0.0016785 | 0.015968 | 0.013749 | 0.0080472 | -0.0051932 | -0.0060519 | 0.0072781 | -0.013733 | 0.17395 | -0.23804 | 0.086975 | -0.022888 | 0.045776 | 0.004578 | 0.15106 | 0.20599 | -0.21057 | 122.1863 | 0.050354 | 122.4106 | 122.5113 | -0.14648 | 122.2137 | 0.082398 | 0.2243 | 122.4289 | 122.5754 | 122.4014 | 122.5983 | 122.4106 | 122.6303 | 122.4701 | 122.2137 | 122.5983 | 122.4106 | 122.4701 | 122.4014 | 122.6303 | -0.36163 | -0.33417
2108.2031 | 122.644 | -122.3694 | 0.10529 | 0.0016785 | 0.015968 | 0.013108 | -0.00049779 | -0.0073294 | -0.0045565 | 0.0066373 | 0.09613 | 0.12817 | -0.19684 | 0.2243 | 0.12817 | 0.19684 | -0.15564 | 0.35706 | 0.17395 | -0.19226 | 122.1725 | 0.022888 | 122.4655 | 122.5937 | 0.022888 | 122.1771 | 0.068664 | 0.29297 | 122.2137 | 122.7264 | 122.4976 | 122.4976 | 122.4655 | 122.5433 | 122.5662 | 122.1771 | 122.4976 | 122.4655 | 122.5662 | 122.4976 | 122.5433 | -0.30212 | -0.29755
2109.8906 | 122.7173 | -122.3831 | 0.086975 | -0.013581 | 0.016609 | 0.0090491 | 0.0048428 | -0.0066886 | -0.0071201 | 0.0072781 | -0.009155 | 0.17853 | -0.22888 | 0.09613 | 0.004578 | 0.054932 | 0.050354 | 0.20142 | 0.20142 | -0.22888 | 122.1542 | 0.091553 | 122.374 | 122.4792 | -0.082397 | 122.1542 | 0.11444 | 0.21973 | 122.4335 | 122.5845 | 122.3877 | 122.5616 | 122.374 | 122.5845 | 122.438 | 122.1542 | 122.5616 | 122.374 | 122.438 | 122.3877 | 122.5845 | -0.31586 | -0.31586
2111.625 | 122.6898 | -122.3557 | 0.086975 | -0.005951 | 0.016609 | 0.012253 | 0.0080472 | -0.0069022 | -0.0054111 | 0.0051419 | -0.013733 | 0.16479 | -0.21515 | 0.10986 | 0.013733 | 0.068665 | 0.036621 | 0.21057 | 0.20599 | -0.21973 | 122.1405 | 0.07782 | 122.3419 | 122.4655 | -0.073242 | 122.1359 | 0.11902 | 0.20142 | 122.3923 | 122.5662 | 122.3694 | 122.5204 | 122.3419 | 122.5616 | 122.4243 | 122.1359 | 122.5204 | 122.3419 | 122.4243 | 122.3694 | 122.5616 | -0.30212 | -0.3067
2113.375 | 122.7081 | -122.3694 | 0.07782 | 0.009308 | 0.015541 | 0.0094763 | 0.00057041 | -0.0079704 | -0.0047703 | 0.0066373 | 0.032043 | 0.13275 | -0.20599 | 0.14191 | 0.073242 | 0.14648 | -0.10529 | 0.28381 | 0.17853 | -0.19684 | 122.1634 | 0.054931 | 122.4014 | 122.5113 | -0.004578 | 122.1725 | 0.10071 | 0.23804 | 122.2641 | 122.6532 | 122.4426 | 122.5021 | 122.4014 | 122.5479 | 122.5159 | 122.1725 | 122.5021 | 122.4014 | 122.5159 | 122.4426 | 122.5479 | -0.28381 | -0.27466
2115.0625 | 122.6532 | -122.3831 | 0.09613 | -0.005951 | 0.015755 | 0.0054175 | 0.0029202 | -0.0083976 | -0.0051975 | 0.0053555 | 0.082397 | 0.14191 | -0.19226 | 0.23346 | 0.13275 | 0.19684 | -0.14648 | 0.36163 | 0.17395 | -0.17853 | 122.1909 | 0.045777 | 122.4655 | 122.6166 | 0.036621 | 122.2046 | 0.07782 | 0.27466 | 122.2366 | 122.7448 | 122.5159 | 122.525 | 122.4655 | 122.5571 | 122.58 | 122.2046 | 122.525 | 122.4655 | 122.58 | 122.5159 | 122.5571 | -0.28839 | -0.27466
2116.8125 | 122.5571 | -122.4106 | 0.11902 | -0.005951 | 0.014687 | 0.010331 | 0.0078336 | -0.0041252 | -0.0077609 | 0.0081325 | 0.073242 | 0.1236 | -0.17853 | 0.20142 | 0.091553 | 0.18768 | -0.18768 | 0.29297 | 0.15564 | -0.17853 | 122.2321 | 0.004577 | 122.4838 | 122.612 | -0.027466 | 122.2321 | 0.036621 | 0.25177 | 122.2229 | 122.7036 | 122.5021 | 122.5342 | 122.4838 | 122.5662 | 122.5983 | 122.2321 | 122.5342 | 122.4838 | 122.5983 | 122.5021 | 122.5662 | -0.29755 | -0.29755
2118.5625 | 122.612 | -122.4243 | 0.12817 | -0.005951 | 0.015968 | 0.013749 | 0.0080472 | -0.0073294 | -0.0084017 | 0.0081325 | 0.009155 | 0.17395 | -0.2243 | 0.091553 | -0.013733 | 0.041199 | -0.009155 | 0.1831 | 0.18768 | -0.21515 | 122.2 | 0.045776 | 122.4335 | 122.5159 | -0.14191 | 122.2092 | 0.059509 | 0.23346 | 122.4152 | 122.6074 | 122.4106 | 122.5983 | 122.4335 | 122.612 | 122.4655 | 122.2092 | 122.5983 | 122.4335 | 122.4655 | 122.4106 | 122.612 | -0.35248 | -0.34332
2120.2969 | 122.5983 | -122.4197 | 0.09613 | 0.0016785 | 0.017036 | 0.012894 | 0.00762 | -0.0056204 | -0.0088291 | 0.0064237 | 0.009155 | 0.16022 | -0.24719 | 0.09613 | -0.004578 | 0.082397 | -0.07782 | 0.1831 | 0.18768 | -0.21057 | 122.1725 | 0.064087 | 122.4289 | 122.5159 | -0.10071 | 122.2092 | 0.091553 | 0.25635 | 122.3419 | 122.6028 | 122.4152 | 122.58 | 122.4289 | 122.6074 | 122.5021 | 122.2092 | 122.58 | 122.4289 | 122.5021 | 122.4152 | 122.6074 | -0.34332 | -0.3067
2122.0312 | 122.6624 | -122.406 | 0.086975 | -0.005951 | 0.015327 | 0.012467 | 0.0014248 | -0.0088248 | -0.0054111 | 0.0066373 | 0.082397 | 0.1236 | -0.18768 | 0.21973 | 0.13733 | 0.19226 | -0.13275 | 0.35706 | 0.17395 | -0.19226 | 122.2183 | 0.036621 | 122.4884 | 122.6257 | 0.050354 | 122.2137 | 0.086975 | 0.27008 | 122.2733 | 122.7631 | 122.5433 | 122.5296 | 122.4884 | 122.58 | 122.5983 | 122.2137 | 122.5296 | 122.4884 | 122.5983 | 122.5433 | 122.58 | -0.27466 | -0.27924
2123.7188 | 122.6624 | -122.3923 | 0.086975 | -0.005951 | 0.016182 | 0.012681 | 0.0044156 | -0.0066886 | -0.0032749 | 0.0032193 | 0.036621 | 0.13733 | -0.17853 | 0.14191 | 0.059509 | 0.13733 | -0.13733 | 0.25177 | 0.18768 | -0.20142 | 122.2137 | 0.050354 | 122.4289 | 122.5342 | -0.027466 | 122.1909 | 0.10071 | 0.21515 | 122.2549 | 122.644 | 122.4518 | 122.5296 | 122.4289 | 122.58 | 122.5296 | 122.1909 | 122.5296 | 122.4289 | 122.5296 | 122.4518 | 122.58 | -0.2655 | -0.28839
2125.4531 | 122.7081 | -122.3831 | 0.091553 | -0.005951 | 0.016823 | 0.013749 | 0.0080472 | -0.0071158 | -0.0056247 | 0.0042873 | -0.004578 | 0.16479 | -0.23804 | 0.09613 | 0.004578 | 0.059509 | 0.036621 | 0.21057 | 0.20599 | -0.25177 | 122.1451 | 0.073242 | 122.3785 | 122.4792 | -0.086975 | 122.1313 | 0.11444 | 0.23346 | 122.4197 | 122.5937 | 122.3877 | 122.5479 | 122.3785 | 122.5891 | 122.4426 | 122.1313 | 122.5479 | 122.3785 | 122.4426 | 122.3877 | 122.5891 | -0.32959 | -0.34332
2127.1875 | 122.5662 | -122.4518 | 0.12817 | 0.0016785 | 0.017891 | 0.014603 | 0.0089016 | -0.0054068 | -0.0069065 | 0.0051419 | 0.050354 | 0.12817 | -0.2243 | 0.15106 | 0.041199 | 0.11444 | -0.064087 | 0.23804 | 0.21057 | -0.21057 | 122.2275 | 0 | 122.5021 | 122.6028 | -0.086975 | 122.2412 | 0.082397 | 0.27466 | 122.3877 | 122.6898 | 122.493 | 122.58 | 122.5021 | 122.6624 | 122.5662 | 122.2412 | 122.58 | 122.5021 | 122.5662 | 122.493 | 122.6624 | -0.35248 | -0.33875
2128.875 | 122.5937 | -122.4472 | 0.11444 | -0.005951 | 0.015541 | 0.013749 | 0.006979 | -0.005834 | -0.0081881 | 0.0077053 | 0.032043 | 0.16022 | -0.22888 | 0.15106 | 0.045776 | 0.10071 | -0.027466 | 0.24719 | 0.21515 | -0.19684 | 122.2183 | 0.045776 | 122.4792 | 122.5983 | -0.068665 | 122.2504 | 0.10071 | 0.26093 | 122.4197 | 122.6944 | 122.493 | 122.6074 | 122.4792 | 122.6624 | 122.5479 | 122.2504 | 122.6074 | 122.4792 | 122.5479 | 122.493 | 122.6624 | -0.34332 | -0.31128
2130.6094 | 122.6212 | -122.4197 | 0.10071 | 0.0016785 | 0.015968 | 0.011399 | 0.0056974 | -0.0045524 | -0.0092563 | 0.0055691 | -0.013733 | 0.16479 | -0.22888 | 0.045776 | -0.027466 | 0.050354 | 0.004578 | 0.16022 | 0.21057 | -0.21057 | 122.1909 | 0.064087 | 122.406 | 122.4655 | -0.12817 | 122.2092 | 0.10986 | 0.21515 | 122.4243 | 122.58 | 122.3923 | 122.5845 | 122.406 | 122.6303 | 122.4701 | 122.2092 | 122.5845 | 122.406 | 122.4701 | 122.3923 | 122.6303 | -0.32959 | -0.31128
2132.3594 | 122.5845 | -122.4472 | 0.11902 | 0.009308 | 0.017464 | 0.0099037 | 0.0061246 | -0.0060478 | -0.0066929 | 0.0077053 | 0.041199 | 0.16479 | -0.2243 | 0.16022 | 0.050354 | 0.10071 | -0.045776 | 0.26093 | 0.21057 | -0.21515 | 122.2229 | 0.045776 | 122.4884 | 122.6074 | -0.068665 | 122.2321 | 0.091552 | 0.2655 | 122.4014 | 122.7081 | 122.4976 | 122.612 | 122.4884 | 122.6578 | 122.5479 | 122.2321 | 122.612 | 122.4884 | 122.5479 | 122.4976 | 122.6578 | -0.34332 | -0.33417
2134.0469 | 122.7127 | -122.3923 | 0.091553 | 0.0016785 | 0.015541 | 0.010331 | 0.0016384 | -0.0083976 | -0.0081881 | 0.0062099 | -0.013733 | 0.15564 | -0.22888 | 0.10071 | 0.018311 | 0.068665 | 0.027466 | 0.21973 | 0.21973 | -0.2243 | 122.1634 | 0.064087 | 122.3785 | 122.493 | -0.073242 | 122.168 | 0.12817 | 0.21515 | 122.4197 | 122.612 | 122.4106 | 122.5479 | 122.3785 | 122.612 | 122.4609 | 122.168 | 122.5479 | 122.3785 | 122.4609 | 122.4106 | 122.612 | -0.32044 | -0.31586
2135.7969 | 122.6395 | -122.4289 | 0.10071 | -0.013581 | 0.016609 | 0.013749 | 0.0063382 | -0.0045524 | -0.0071201 | 0.0047147 | -0.022888 | 0.17853 | -0.23804 | 0.064087 | -0.009155 | 0.045776 | -0.018311 | 0.15106 | 0.21515 | -0.2243 | 122.1909 | 0.07782 | 122.406 | 122.493 | -0.10986 | 122.2046 | 0.11444 | 0.21515 | 122.4106 | 122.58 | 122.4197 | 122.6074 | 122.406 | 122.644 | 122.4747 | 122.2046 | 122.6074 | 122.406 | 122.4747 | 122.4197 | 122.644 | -0.33875 | -0.32501
2137.5312 | 122.7219 | -122.4197 | 0.086975 | -0.005951 | 0.015114 | 0.0081947 | -0.0015658 | -0.0079704 | -0.0030613 | 0.0062099 | 0.027466 | 0.12817 | -0.16937 | 0.11444 | 0.07782 | 0.13733 | -0.10071 | 0.25635 | 0.19684 | -0.20599 | 122.2504 | 0.041199 | 122.4472 | 122.5342 | -0.009155 | 122.2137 | 0.10986 | 0.19684 | 122.319 | 122.6761 | 122.4976 | 122.5479 | 122.4472 | 122.6166 | 122.5571 | 122.2137 | 122.5479 | 122.4472 | 122.5571 | 122.4976 | 122.6166 | -0.25635 | -0.29297
2139.2812 | 122.6761 | -122.4014 | 0.064087 | 0.0016785 | 0.013405 | 0.0096899 | 0.0014248 | -0.008184 | -0.0054111 | 0.0051419 | 0.064087 | 0.11902 | -0.19226 | 0.18768 | 0.10986 | 0.19684 | -0.13275 | 0.32959 | 0.16937 | -0.20599 | 122.2092 | 0.054932 | 122.4655 | 122.5891 | 0.045776 | 122.1954 | 0.10529 | 0.25635 | 122.2687 | 122.731 | 122.5113 | 122.5204 | 122.4655 | 122.5708 | 122.5983 | 122.1954 | 122.5204 | 122.4655 | 122.5983 | 122.5113 | 122.5708 | -0.25635 | -0.27008
2141.0312 | 122.6852 | -122.3831 | 0.07782 | -0.005951 | 0.014259 | 0.010117 | 0.0039884 | -0.010107 | -0.0047703 | 0.0055691 | 0.073242 | 0.11902 | -0.18768 | 0.20599 | 0.10986 | 0.21057 | -0.15106 | 0.35706 | 0.15564 | -0.18768 | 122.1954 | 0.041199 | 122.4564 | 122.5891 | 0.032043 | 122.1954 | 0.07782 | 0.26092 | 122.2321 | 122.7402 | 122.493 | 122.5021 | 122.4564 | 122.5388 | 122.5937 | 122.1954 | 122.5021 | 122.4564 | 122.5937 | 122.493 | 122.5388 | -0.2655 | -0.2655
2142.7656 | 122.7036 | -122.3923 | 0.082397 | -0.005951 | 0.016396 | 0.011185 | 0.0031338 | -0.0090384 | -0.0060519 | 0.0055691 | 0.050354 | 0.13275 | -0.20142 | 0.17395 | 0.091553 | 0.16022 | -0.1236 | 0.32501 | 0.16937 | -0.20142 | 122.1909 | 0.050354 | 122.4426 | 122.5662 | 0.009156 | 122.1909 | 0.086976 | 0.25177 | 122.2687 | 122.7173 | 122.4838 | 122.525 | 122.4426 | 122.5616 | 122.5525 | 122.1909 | 122.525 | 122.4426 | 122.5525 | 122.4838 | 122.5616 | -0.28381 | -0.28381
2144.4531 | 122.5983 | -122.4335 | 0.11902 | -0.005951 | 0.015968 | 0.013962 | 0.011038 | -0.0049796 | -0.0088291 | 0.0055691 | 0.041199 | 0.15564 | -0.23346 | 0.14191 | 0.027466 | 0.07782 | -0.027466 | 0.21057 | 0.20142 | -0.20142 | 122.2 | 0.036621 | 122.4747 | 122.5754 | -0.091553 | 122.2321 | 0.082397 | 0.27466 | 122.406 | 122.644 | 122.4609 | 122.5891 | 122.4747 | 122.6349 | 122.5113 | 122.2321 | 122.5891 | 122.4747 | 122.5113 | 122.4609 | 122.6349 | -0.35248 | -0.32044
2146.2031 | 122.6669 | -122.4335 | 0.09613 | -0.005951 | 0.014046 | 0.0069129 | 0.0027066 | -0.0073294 | -0.0034885 | 0.0072781 | 0.086975 | 0.13733 | -0.19226 | 0.21973 | 0.10529 | 0.20599 | -0.14191 | 0.35248 | 0.16022 | -0.19226 | 122.2412 | 0.041199 | 122.5204 | 122.6532 | 0.009156 | 122.2412 | 0.064087 | 0.27924 | 122.2916 | 122.7859 | 122.5388 | 122.5708 | 122.5204 | 122.5937 | 122.6395 | 122.2412 | 122.5708 | 122.5204 | 122.6395 | 122.5388 | 122.5937 | -0.28839 | -0.28839
2147.9531 | 122.6578 | -122.4335 | 0.1236 | -0.013581 | 0.016609 | 0.013749 | 0.006979 | -0.0083976 | -0.0084017 | 0.0053555 | 0.004578 | 0.15106 | -0.25177 | 0.14648 | 0.027466 | 0.09613 | -0.004578 | 0.23804 | 0.1831 | -0.23346 | 122.1817 | 0.027466 | 122.438 | 122.58 | -0.09613 | 122.2 | 0.059509 | 0.25635 | 122.4289 | 122.6715 | 122.4609 | 122.5845 | 122.438 | 122.6166 | 122.5296 | 122.2 | 122.5845 | 122.438 | 122.5296 | 122.4609 | 122.6166 | -0.37537 | -0.35706
2149.6406 | 122.7264 | -122.4106 | 0.086975 | 0.0016785 | 0.0149 | 0.011399 | 0.00057041 | -0.0066886 | -0.0056247 | 0.0066373 | 0.032043 | 0.1236 | -0.19684 | 0.14648 | 0.064087 | 0.14191 | -0.10986 | 0.25635 | 0.17853 | -0.18768 | 122.2137 | 0.036621 | 122.4426 | 122.5571 | -0.022888 | 122.2229 | 0.091553 | 0.22888 | 122.3007 | 122.6669 | 122.4747 | 122.5342 | 122.4426 | 122.5891 | 122.5525 | 122.2229 | 122.5342 | 122.4426 | 122.5525 | 122.4747 | 122.5891 | -0.28381 | -0.27466
2151.3906 | 122.7081 | -122.4243 | 0.10071 | -0.013581 | 0.015114 | 0.0094763 | 0.00762 | -0.0083976 | -0.0066929 | 0.0053555 | 0 | 0.17395 | -0.24261 | 0.11902 | 0.009155 | 0.068665 | 0.027466 | 0.23346 | 0.20142 | -0.21515 | 122.1817 | 0.073242 | 122.4243 | 122.5433 | -0.091553 | 122.2092 | 0.10071 | 0.24261 | 122.4518 | 122.6578 | 122.4335 | 122.5983 | 122.4243 | 122.6257 | 122.493 | 122.2092 | 122.5983 | 122.4243 | 122.493 | 122.4335 | 122.6257 | -0.34332 | -0.31586
2153.0625 | 122.644 | -122.4243 | 0.10986 | -0.013581 | 0.0149 | 0.012681 | 0.0061246 | -0.004766 | -0.0069065 | 0.0066373 | -0.013733 | 0.16022 | -0.24719 | 0.07782 | -0.022888 | 0.068665 | -0.013733 | 0.16022 | 0.21515 | -0.21973 | 122.1771 | 0.050354 | 122.4106 | 122.5021 | -0.13275 | 122.2046 | 0.10529 | 0.23346 | 122.4106 | 122.5845 | 122.4014 | 122.5845 | 122.4106 | 122.6395 | 122.493 | 122.2046 | 122.5845 | 122.4106 | 122.493 | 122.4014 | 122.6395 | -0.35706 | -0.32959
2154.8125 | 122.6898 | -122.4197 | 0.09613 | -0.013581 | 0.013405 | 0.0079809 | 0.001852 | -0.0079704 | -0.0066929 | 0.0064237 | 0.10071 | 0.11902 | -0.1831 | 0.20599 | 0.14191 | 0.20599 | -0.13275 | 0.33875 | 0.17395 | -0.20142 | 122.2366 | 0.022889 | 122.5204 | 122.6257 | 0.045777 | 122.2183 | 0.07782 | 0.28381 | 122.287 | 122.7585 | 122.5616 | 122.5388 | 122.5204 | 122.5937 | 122.6257 | 122.2183 | 122.5388 | 122.5204 | 122.6257 | 122.5616 | 122.5937 | -0.27924 | -0.29755
2156.5625 | 122.7173 | -122.406 | 0.064087 | -0.02121 | 0.019173 | 0.0099037 | 0.002493 | -0.0083976 | -0.0041293 | 0.0072781 | 0.032043 | 0.14648 | -0.20142 | 0.14191 | 0.054932 | 0.13733 | -0.10986 | 0.25177 | 0.1831 | -0.20599 | 122.2046 | 0.082397 | 122.438 | 122.5479 | -0.009155 | 122.2 | 0.11902 | 0.23346 | 122.2961 | 122.6578 | 122.4609 | 122.5525 | 122.438 | 122.5891 | 122.5433 | 122.2 | 122.5525 | 122.438 | 122.5433 | 122.4609 | 122.5891 | -0.2655 | -0.27008
2158.25 | 122.5983 | -122.4655 | 0.10529 | -0.013581 | 0.013832 | 0.011399 | 0.0061246 | -0.0071158 | -0.0047703 | 0.0049283 | 0.091553 | 0.10071 | -0.1831 | 0.20142 | 0.10071 | 0.19684 | -0.1831 | 0.31128 | 0.1831 | -0.19226 | 122.2824 | -0.004578 | 122.5571 | 122.6669 | -0.004578 | 122.2733 | 0.077819 | 0.27466 | 122.2824 | 122.7768 | 122.5662 | 122.5662 | 122.5571 | 122.6486 | 122.6624 | 122.2733 | 122.5662 | 122.5571 | 122.6624 | 122.5662 | 122.6486 | -0.28839 | -0.29755
2160 | 122.644 | -122.4655 | 0.10986 | -0.013581 | 0.016182 | 0.011826 | 0.0099698 | -0.0073294 | -0.0096835 | 0.0068509 | 0.018311 | 0.14648 | -0.2243 | 0.11444 | -0.013733 | 0.054932 | -0.027466 | 0.16937 | 0.19226 | -0.21515 | 122.2412 | 0.036621 | 122.4838 | 122.58 | -0.1236 | 122.2504 | 0.082398 | 0.24261 | 122.438 | 122.6349 | 122.4518 | 122.612 | 122.4838 | 122.6578 | 122.5204 | 122.2504 | 122.612 | 122.4838 | 122.5204 | 122.4518 | 122.6578 | -0.33417 | -0.32501
2161.6719 | 122.731 | -122.4152 | 0.07782 | -0.005951 | 0.015755 | 0.015671 | 0.001852 | -0.0083976 | -0.0045565 | 0.0068509 | 0.022888 | 0.13733 | -0.19684 | 0.14648 | 0.059509 | 0.12817 | -0.10071 | 0.24261 | 0.16937 | -0.20142 | 122.2183 | 0.059509 | 122.438 | 122.5616 | -0.018311 | 122.2137 | 0.091553 | 0.21973 | 122.3145 | 122.6578 | 122.4747 | 122.5525 | 122.438 | 122.5845 | 122.5433 | 122.2137 | 122.5525 | 122.438 | 122.5433 | 122.4747 | 122.5845 | -0.27466 | -0.27924
2163.4219 | 122.6852 | -122.4335 | 0.09613 | -0.005951 | 0.0149 | 0.010544 | 0.003561 | -0.0096794 | -0.0049839 | 0.0049283 | 0.086975 | 0.13733 | -0.18768 | 0.21057 | 0.1236 | 0.17395 | -0.13275 | 0.3479 | 0.16022 | -0.18768 | 122.2458 | 0.041199 | 122.5204 | 122.644 | 0.027466 | 122.2458 | 0.064087 | 0.27466 | 122.3007 | 122.7814 | 122.5571 | 122.5708 | 122.5204 | 122.5937 | 122.6074 | 122.2458 | 122.5708 | 122.5204 | 122.6074 | 122.5571 | 122.5937 | -0.28381 | -0.28381
2165.0938 | 122.699 | -122.4197 | 0.10529 | 0.009308 | 0.015968 | 0.0079809 | 0.0061246 | -0.006475 | -0.0060519 | 0.0062099 | -0.004578 | 0.16937 | -0.22888 | 0.13733 | 0.036621 | 0.086975 | 0.009155 | 0.2243 | 0.21973 | -0.20142 | 122.1909 | 0.064087 | 122.4152 | 122.5571 | -0.068665 | 122.2183 | 0.11444 | 0.2243 | 122.4289 | 122.644 | 122.4564 | 122.5891 | 122.4152 | 122.6395 | 122.5067 | 122.2183 | 122.5891 | 122.4152 | 122.5067 | 122.4564 | 122.6395 | -0.33417 | -0.3067
2166.8281 | 122.6944 | -122.4472 | 0.10986 | -0.005951 | 0.017464 | 0.0099037 | 0.0065518 | -0.0060478 | -0.0058383 | 0.0062099 | 0.009155 | 0.16479 | -0.2243 | 0.13275 | 0.032043 | 0.082397 | -0.004578 | 0.23346 | 0.19226 | -0.20599 | 122.2229 | 0.054932 | 122.4564 | 122.58 | -0.07782 | 122.2412 | 0.082398 | 0.23346 | 122.4426 | 122.6807 | 122.4792 | 122.612 | 122.4564 | 122.6395 | 122.5296 | 122.2412 | 122.612 | 122.4564 | 122.5296 | 122.4792 | 122.6395 | -0.33417 | -0.31586
2168.5938 | 122.6257 | -122.4564 | 0.10071 | 0.0016785 | 0.017464 | 0.012253 | 0.0063382 | -0.0069022 | -0.0045565 | 0.0057827 | 0.091553 | 0.15106 | -0.1831 | 0.17853 | 0.10071 | 0.17853 | -0.17853 | 0.28839 | 0.15564 | -0.16022 | 122.2733 | 0.050354 | 122.5479 | 122.6349 | 0 | 122.2961 | 0.054932 | 0.27466 | 122.2778 | 122.7448 | 122.5571 | 122.6074 | 122.5479 | 122.612 | 122.6349 | 122.2961 | 122.6074 | 122.5479 | 122.6349 | 122.5571 | 122.612 | -0.28381 | -0.26093
2170.2812 | 122.7585 | -122.4289 | 0.10071 | -0.005951 | 0.016182 | 0.011826 | 0.0027066 | -0.0086112 | -0.0075473 | 0.0049283 | -0.022888 | 0.17395 | -0.24261 | 0.09613 | 0.004578 | 0.054932 | 0.064087 | 0.20599 | 0.20142 | -0.21973 | 122.1863 | 0.073242 | 122.406 | 122.525 | -0.09613 | 122.2092 | 0.10071 | 0.21973 | 122.493 | 122.6349 | 122.4335 | 122.6028 | 122.406 | 122.6303 | 122.4838 | 122.2092 | 122.6028 | 122.406 | 122.4838 | 122.4335 | 122.6303 | -0.34332 | -0.32044
2172.0156 | 122.6257 | -122.4609 | 0.10071 | -0.013581 | 0.015327 | 0.017594 | 0.0063382 | -0.005834 | -0.0075473 | 0.0059963 | 0.022888 | 0.16479 | -0.23346 | 0.15106 | 0.045776 | 0.10071 | -0.032043 | 0.24719 | 0.21057 | -0.21057 | 122.2275 | 0.064087 | 122.4838 | 122.612 | -0.054932 | 122.2504 | 0.10986 | 0.25635 | 122.4289 | 122.7081 | 122.5067 | 122.6257 | 122.4838 | 122.6715 | 122.5616 | 122.2504 | 122.6257 | 122.4838 | 122.5616 | 122.5067 | 122.6715 | -0.33417 | -0.31128
2173.7031 | 122.7356 | -122.4197 | 0.082397 | -0.005951 | 0.013618 | 0.0099037 | 0.002493 | -0.0083976 | -0.0051975 | 0.0055691 | 0.064087 | 0.13275 | -0.18768 | 0.17395 | 0.082397 | 0.1236 | -0.032043 | 0.28381 | 0.20599 | -0.20142 | 122.2321 | 0.050354 | 122.4838 | 122.5937 | 0 | 122.2183 | 0.1236 | 0.25177 | 122.3877 | 122.7036 | 122.5021 | 122.5525 | 122.4838 | 122.6257 | 122.5433 | 122.2183 | 122.5525 | 122.4838 | 122.5433 | 122.5021 | 122.6257 | -0.27008 | -0.28381
2175.4375 | 122.699 | -122.4518 | 0.091553 | -0.005951 | 0.016182 | 0.011826 | -0.00028419 | -0.0077566 | -0.0064791 | 0.0042873 | 0.10986 | 0.1236 | -0.18768 | 0.21057 | 0.12817 | 0.21057 | -0.13275 | 0.3479 | 0.16937 | -0.1831 | 122.2641 | 0.032043 | 122.5616 | 122.6624 | 0.036621 | 122.2687 | 0.07782 | 0.29755 | 122.319 | 122.7997 | 122.58 | 122.5754 | 122.5616 | 122.6212 | 122.6624 | 122.2687 | 122.5754 | 122.5616 | 122.6624 | 122.58 | 122.6212 | -0.27924 | -0.27466
2177.1094 | 122.731 | -122.4243 | 0.10071 | -0.005951 | 0.018318 | 0.0079809 | 0.0067654 | -0.008184 | -0.0049839 | 0.0055691 | -0.004578 | 0.15106 | -0.24719 | 0.13275 | 0.013733 | 0.059509 | 0.032043 | 0.20599 | 0.20599 | -0.23346 | 122.1771 | 0.050354 | 122.4197 | 122.5571 | -0.086975 | 122.1909 | 0.10529 | 0.24261 | 122.4564 | 122.6303 | 122.438 | 122.5754 | 122.4197 | 122.6303 | 122.4838 | 122.1909 | 122.5754 | 122.4197 | 122.4838 | 122.438 | 122.6303 | -0.3479 | -0.33417
2178.875 | 122.7539 | -122.4243 | 0.091553 | 0.009308 | 0.012978 | 0.013321 | 0.0054836 | -0.0079704 | -0.0056247 | 0.0068509 | -0.045776 | 0.16022 | -0.23804 | 0.082397 | 0.004578 | 0.059509 | 0.050354 | 0.19226 | 0.21057 | -0.22888 | 122.1863 | 0.068664 | 122.3785 | 122.5067 | -0.086975 | 122.1954 | 0.11902 | 0.19226 | 122.4747 | 122.6166 | 122.4289 | 122.5845 | 122.3785 | 122.6349 | 122.4838 | 122.1954 | 122.5845 | 122.3785 | 122.4838 | 122.4289 | 122.6349 | -0.32959 | -0.32044
2180.5625 | 122.6257 | -122.493 | 0.091553 | -0.005951 | 0.0149 | 0.0099037 | 0.003561 | -0.0066886 | -0.0073337 | 0.0059963 | 0.10071 | 0.12817 | -0.17395 | 0.21057 | 0.12817 | 0.18768 | -0.20599 | 0.31586 | 0.16022 | -0.17853 | 122.319 | 0.036621 | 122.5937 | 122.7036 | 0.036621 | 122.3145 | 0.068664 | 0.27466 | 122.287 | 122.8088 | 122.6212 | 122.6212 | 122.5937 | 122.6532 | 122.6807 | 122.3145 | 122.6212 | 122.5937 | 122.6807 | 122.6212 | 122.6532 | -0.2655 | -0.27008
2182.3125 | 122.7493 | -122.4106 | 0.073242 | 0.0016785 | 0.016182 | 0.011399 | -0.00028419 | -0.0073294 | -0.0041293 | 0.0066373 | 0.018311 | 0.13275 | -0.19684 | 0.14648 | 0.059509 | 0.1236 | -0.091553 | 0.26093 | 0.16022 | -0.20599 | 122.2137 | 0.059509 | 122.4289 | 122.5571 | -0.013733 | 122.2046 | 0.086975 | 0.21515 | 122.319 | 122.6715 | 122.4701 | 122.5433 | 122.4289 | 122.5708 | 122.5342 | 122.2046 | 122.5433 | 122.4289 | 122.5342 | 122.4701 | 122.5708 | -0.27008 | -0.27924
2184.0156 | 122.7448 | -122.438 | 0.09613 | 0.0016785 | 0.014046 | 0.010331 | 0.0020658 | -0.008184 | -0.0043429 | 0.0059963 | 0.032043 | 0.14648 | -0.18768 | 0.15564 | 0.059509 | 0.14648 | -0.10529 | 0.26093 | 0.17853 | -0.21973 | 122.2504 | 0.050354 | 122.4701 | 122.5937 | -0.036621 | 122.2183 | 0.082398 | 0.21973 | 122.3328 | 122.699 | 122.4976 | 122.5845 | 122.4701 | 122.6166 | 122.5845 | 122.2183 | 122.5845 | 122.4701 | 122.5845 | 122.4976 | 122.6166 | -0.28381 | -0.31586
2185.7656 | 122.7356 | -122.4472 | 0.082397 | 0.009308 | 0.015541 | 0.0099037 | 0.0016384 | -0.0083976 | -0.0054111 | 0.0047147 | 0.045776 | 0.14191 | -0.20142 | 0.17395 | 0.091553 | 0.16937 | -0.1236 | 0.31128 | 0.16937 | -0.19684 | 122.2458 | 0.05951 | 122.493 | 122.6212 | 0.009156 | 122.2504 | 0.086976 | 0.24719 | 122.3236 | 122.7585 | 122.5388 | 122.5891 | 122.493 | 122.6166 | 122.6166 | 122.2504 | 122.5891 | 122.493 | 122.6166 | 122.5388 | 122.6166 | -0.28381 | -0.27924
2187.5 | 122.612 | -122.4472 | 0.10986 | 0.0016785 | 0.015968 | 0.010758 | 0.0074062 | -0.004766 | -0.0058383 | 0.0047147 | 0.091553 | 0.12817 | -0.19226 | 0.19684 | 0.082397 | 0.16937 | -0.19226 | 0.29755 | 0.16022 | -0.17853 | 122.2549 | 0.018311 | 122.5388 | 122.644 | -0.027466 | 122.2687 | 0.050354 | 0.28381 | 122.2549 | 122.7448 | 122.5296 | 122.5754 | 122.5388 | 122.6074 | 122.6166 | 122.2687 | 122.5754 | 122.5388 | 122.6166 | 122.5296 | 122.6074 | -0.30212 | -0.28839
2189.2344 | 122.7036 | -122.4564 | 0.07782 | 0.0016785 | 0.011482 | 0.010972 | 0.00099761 | -0.0056204 | -0.0058383 | 0.0057827 | 0.036621 | 0.1236 | -0.1831 | 0.15106 | 0.059509 | 0.14191 | -0.13275 | 0.26093 | 0.16937 | -0.18768 | 122.2733 | 0.045776 | 122.493 | 122.6074 | -0.018311 | 122.2687 | 0.091553 | 0.21973 | 122.3236 | 122.7173 | 122.5159 | 122.58 | 122.493 | 122.6257 | 122.5983 | 122.2687 | 122.58 | 122.493 | 122.5983 | 122.5159 | 122.6257 | -0.26092 | -0.2655
2190.9375 | 122.7814 | -122.4289 | 0.09613 | 0.009308 | 0.015114 | 0.0096899 | 0.0061246 | -0.0069022 | -0.0062655 | 0.0055691 | -0.018311 | 0.15106 | -0.24261 | 0.10986 | 0.004578 | 0.045776 | 0.050354 | 0.19684 | 0.21057 | -0.23346 | 122.1863 | 0.054932 | 122.4106 | 122.5388 | -0.091552 | 122.1954 | 0.11444 | 0.2243 | 122.4792 | 122.6257 | 122.4335 | 122.58 | 122.4106 | 122.6395 | 122.4747 | 122.1954 | 122.58 | 122.4106 | 122.4747 | 122.4335 | 122.6395 | -0.33874 | -0.32959
2192.6875 | 122.6166 | -122.4838 | 0.13275 | -0.005951 | 0.015541 | 0.010331 | 0.00762 | -0.004766 | -0.0062655 | 0.0070645 | 0.059509 | 0.15564 | -0.24261 | 0.14648 | 0.027466 | 0.091553 | -0.041199 | 0.23346 | 0.20599 | -0.19684 | 122.2412 | 0.022889 | 122.5433 | 122.6303 | -0.10529 | 122.287 | 0.073243 | 0.30212 | 122.4426 | 122.7173 | 122.5113 | 122.6395 | 122.5433 | 122.6898 | 122.5754 | 122.287 | 122.6395 | 122.5433 | 122.5754 | 122.5113 | 122.6898 | -0.37537 | -0.32959
2194.3906 | 122.6669 | -122.4609 | 0.10529 | -0.005951 | 0.015968 | 0.01204 | 0.00762 | -0.005834 | -0.0069065 | 0.0057827 | -0.027466 | 0.15564 | -0.22888 | 0.091553 | -0.009155 | 0.050354 | 0 | 0.16022 | 0.21973 | -0.21057 | 122.2321 | 0.050354 | 122.4335 | 122.5525 | -0.11444 | 122.2504 | 0.11444 | 0.20142 | 122.4609 | 122.6212 | 122.4518 | 122.6166 | 122.4335 | 122.6807 | 122.5113 | 122.2504 | 122.6166 | 122.4335 | 122.5113 | 122.4518 | 122.6807 | -0.33417 | -0.31586
2196.1562 | 122.6486 | -122.4701 | 0.10986 | -0.005951 | 0.016182 | 0.013535 | 0.0031338 | -0.0045524 | -0.0073337 | 0.0064237 | -0.009155 | 0.16022 | -0.2243 | 0.10986 | -0.004578 | 0.086975 | -0.068665 | 0.1831 | 0.20142 | -0.20599 | 122.2458 | 0.050354 | 122.4609 | 122.58 | -0.11444 | 122.2641 | 0.091553 | 0.21515 | 122.4014 | 122.6532 | 122.4655 | 122.6303 | 122.4609 | 122.6715 | 122.5571 | 122.2641 | 122.6303 | 122.4609 | 122.5571 | 122.4655 | 122.6715 | -0.33417 | -0.31586
2197.9062 | 122.6715 | -122.4747 | 0.10529 | 0.0016785 | 0.018532 | 0.010972 | 0.005911 | -0.006475 | -0.0077609 | 0.0053555 | 0 | 0.16022 | -0.2243 | 0.09613 | 0 | 0.059509 | -0.059509 | 0.17853 | 0.20599 | -0.21515 | 122.2504 | 0.054931 | 122.4747 | 122.5708 | -0.10529 | 122.2595 | 0.10071 | 0.2243 | 122.4152 | 122.6532 | 122.4747 | 122.6349 | 122.4747 | 122.6807 | 122.5342 | 122.2595 | 122.6349 | 122.4747 | 122.5342 | 122.4747 | 122.6807 | -0.32959 | -0.32044
2199.6094 | 122.6669 | -122.4701 | 0.12817 | 0.0016785 | 0.014259 | 0.015244 | 0.005911 | -0.0041252 | -0.010111 | 0.0057827 | -0.009155 | 0.15106 | -0.2243 | 0.091553 | -0.004578 | 0.059509 | -0.004578 | 0.16022 | 0.21515 | -0.2243 | 122.2458 | 0.022888 | 122.4609 | 122.5616 | -0.13275 | 122.2458 | 0.086975 | 0.21515 | 122.4655 | 122.6303 | 122.4655 | 122.6212 | 122.4609 | 122.6852 | 122.5296 | 122.2458 | 122.6212 | 122.4609 | 122.5296 | 122.4655 | 122.6852 | -0.35248 | -0.35248
2201.2969 | 122.7173 | -122.4564 | 0.10071 | -0.005951 | 0.016396 | 0.0096899 | -0.0022068 | -0.0073294 | -0.0043429 | 0.0062099 | 0.064087 | 0.15106 | -0.1831 | 0.20599 | 0.1236 | 0.20599 | -0.16022 | 0.33417 | 0.15564 | -0.18768 | 122.2733 | 0.050354 | 122.5204 | 122.6624 | 0.022888 | 122.2687 | 0.054932 | 0.24719 | 122.2961 | 122.7905 | 122.58 | 122.6074 | 122.5204 | 122.612 | 122.6624 | 122.2687 | 122.6074 | 122.5204 | 122.6624 | 122.58 | 122.612 | -0.28381 | -0.28839
2203.0469 | 122.7219 | -122.4884 | 0.10986 | 0.0016785 | 0.012978 | 0.012467 | 0.00099761 | -0.0083976 | -0.0043429 | 0.0051419 | 0.086975 | 0.11902 | -0.21515 | 0.20142 | 0.1236 | 0.17853 | -0.10986 | 0.33875 | 0.16479 | -0.17853 | 122.2733 | 0.009156 | 122.5754 | 122.6898 | 0.013733 | 122.3099 | 0.054932 | 0.30212 | 122.3785 | 122.8271 | 122.612 | 122.6074 | 122.5754 | 122.6532 | 122.6669 | 122.3099 | 122.6074 | 122.5754 | 122.6669 | 122.612 | 122.6532 | -0.32501 | -0.28839
2204.7344 | 122.6807 | -122.4564 | 0.10071 | -0.005951 | 0.017036 | 0.014817 | 0.00078401 | -0.0043388 | -0.0054111 | 0.0047147 | 0.054932 | 0.11902 | -0.1831 | 0.14191 | 0.073242 | 0.15106 | -0.13733 | 0.27466 | 0.16937 | -0.19226 | 122.2733 | 0.018311 | 122.5113 | 122.5983 | -0.027466 | 122.2641 | 0.068665 | 0.23804 | 122.319 | 122.731 | 122.5296 | 122.5754 | 122.5113 | 122.6257 | 122.6074 | 122.2641 | 122.5754 | 122.5113 | 122.6074 | 122.5296 | 122.6257 | -0.28381 | -0.29297
2206.4844 | 122.7722 | -122.4335 | 0.082397 | -0.005951 | 0.015755 | 0.0071265 | 0.0037748 | -0.0086112 | -0.0051975 | 0.0059963 | -0.018311 | 0.16479 | -0.23804 | 0.091553 | -0.004578 | 0.054932 | 0.064087 | 0.20599 | 0.19684 | -0.23804 | 122.1954 | 0.082398 | 122.4152 | 122.525 | -0.086975 | 122.1954 | 0.11444 | 0.21973 | 122.4976 | 122.6395 | 122.4289 | 122.5983 | 122.4152 | 122.6303 | 122.4884 | 122.1954 | 122.5983 | 122.4152 | 122.4884 | 122.4289 | 122.6303 | -0.32043 | -0.32043
2208.1719 | 122.644 | -122.4792 | 0.10986 | -0.02121 | 0.013618 | 0.011612 | 0.0080472 | -0.005834 | -0.0086155 | 0.0053555 | 0.059509 | 0.13275 | -0.21515 | 0.13733 | 0.041199 | 0.09613 | -0.036621 | 0.22888 | 0.19226 | -0.21057 | 122.2641 | 0.022888 | 122.5388 | 122.6166 | -0.068664 | 122.2687 | 0.082398 | 0.27466 | 122.4426 | 122.7081 | 122.5204 | 122.612 | 122.5388 | 122.6715 | 122.5754 | 122.2687 | 122.612 | 122.5388 | 122.5754 | 122.5204 | 122.6715 | -0.32501 | -0.32043
2209.9219 | 122.6761 | -122.4838 | 0.091553 | -0.013581 | 0.01255 | 0.01204 | -7.059e-05 | -0.0039114 | -0.0066929 | 0.0059963 | 0.091553 | 0.10986 | -0.1831 | 0.15106 | 0.091553 | 0.17395 | -0.15564 | 0.27466 | 0.18768 | -0.17853 | 122.3007 | 0.01831 | 122.5754 | 122.6349 | 0 | 122.3053 | 0.09613 | 0.27466 | 122.3282 | 122.7585 | 122.5754 | 122.5937 | 122.5754 | 122.6715 | 122.6578 | 122.3053 | 122.5937 | 122.5754 | 122.6578 | 122.5754 | 122.6715 | -0.27466 | -0.27008
2211.6562 | 122.7264 | -122.4747 | 0.086975 | 0.0016785 | 0.015114 | 0.011826 | -7.059e-05 | -0.0094656 | -0.0060519 | 0.0055691 | 0.09613 | 0.14648 | -0.1831 | 0.22888 | 0.12817 | 0.19684 | -0.15564 | 0.35248 | 0.15564 | -0.19226 | 122.2916 | 0.059509 | 122.5708 | 122.7036 | 0.041199 | 122.2824 | 0.068665 | 0.27924 | 122.319 | 122.8271 | 122.6028 | 122.6212 | 122.5708 | 122.6303 | 122.6715 | 122.2824 | 122.6212 | 122.5708 | 122.6715 | 122.6028 | 122.6303 | -0.27008 | -0.27924
2213.4062 | 122.6898 | -122.4655 | 0.10071 | 0.009308 | 0.019173 | 0.010117 | 0.0065518 | -0.0051932 | -0.0060519 | 0.0055691 | -0.009155 | 0.16479 | -0.22888 | 0.09613 | -0.018311 | 0.050354 | -0.022888 | 0.16937 | 0.19226 | -0.21515 | 122.2366 | 0.064087 | 122.4564 | 122.5616 | -0.11902 | 122.2504 | 0.091553 | 0.21973 | 122.4426 | 122.6349 | 122.4472 | 122.6303 | 122.4564 | 122.6578 | 122.5159 | 122.2504 | 122.6303 | 122.4564 | 122.5159 | 122.4472 | 122.6578 | -0.32959 | -0.31586
2215.0938 | 122.7493 | -122.493 | 0.064087 | -0.013581 | 0.016396 | 0.011826 | 0.001852 | -0.0086112 | -0.0060519 | 0.0053555 | 0.064087 | 0.13733 | -0.1831 | 0.1831 | 0.10071 | 0.15106 | -0.050354 | 0.30212 | 0.16479 | -0.19226 | 122.3099 | 0.073242 | 122.5571 | 122.6761 | 0.036621 | 122.3007 | 0.10071 | 0.24719 | 122.4426 | 122.7951 | 122.5937 | 122.6303 | 122.5571 | 122.6578 | 122.644 | 122.3007 | 122.6303 | 122.5571 | 122.644 | 122.5937 | 122.6578 | -0.24719 | -0.25635
2216.8281 | 122.7264 | -122.4564 | 0.10071 | 0.0016785 | 0.016396 | 0.010758 | 0.0020658 | -0.0094656 | -0.0060519 | 0.0066373 | 0.07782 | 0.12817 | -0.17853 | 0.20599 | 0.1236 | 0.1831 | -0.1236 | 0.33875 | 0.17395 | -0.17853 | 122.2778 | 0.027466 | 122.5342 | 122.6624 | 0.022888 | 122.2778 | 0.073242 | 0.25635 | 122.3328 | 122.7951 | 122.58 | 122.5845 | 122.5342 | 122.6303 | 122.6395 | 122.2778 | 122.5845 | 122.5342 | 122.6395 | 122.58 | 122.6303 | -0.27924 | -0.27924
2218.5 | 122.6486 | -122.4701 | 0.11902 | 0.009308 | 0.016182 | 0.012894 | 0.0046292 | -0.006475 | -0.0066929 | 0.0070645 | 0.10071 | 0.11444 | -0.17395 | 0.21057 | 0.091553 | 0.19226 | -0.20142 | 0.3067 | 0.15106 | -0.16937 | 122.2961 | -0.004578 | 122.5708 | 122.6807 | -0.027466 | 122.3007 | 0.032043 | 0.27466 | 122.2687 | 122.7768 | 122.5616 | 122.5845 | 122.5708 | 122.6212 | 122.6624 | 122.3007 | 122.5845 | 122.5708 | 122.6624 | 122.5616 | 122.6212 | -0.29297 | -0.28839
2220.1875 | 122.6303 | -122.4976 | 0.12817 | -0.013581 | 0.012764 | 0.010331 | 0.0054836 | -0.0062614 | -0.0056247 | 0.0074917 | 0.10071 | 0.11902 | -0.16937 | 0.20599 | 0.10071 | 0.19226 | -0.20142 | 0.3067 | 0.16479 | -0.17395 | 122.3282 | -0.009155 | 122.5983 | 122.7036 | -0.027466 | 122.3236 | 0.036621 | 0.27008 | 122.2961 | 122.8043 | 122.5983 | 122.6166 | 122.5983 | 122.6624 | 122.6898 | 122.3236 | 122.6166 | 122.5983 | 122.6898 | 122.5983 | 122.6624 | -0.29755 | -0.30212
2221.9219 | 122.6944 | -122.5067 | 0.13275 | -0.005951 | 0.015541 | 0.017594 | 0.0054836 | -0.0039114 | -0.0094699 | 0.0042873 | 0 | 0.16937 | -0.22888 | 0.086975 | -0.022888 | 0.036621 | 0.018311 | 0.15564 | 0.21973 | -0.21515 | 122.2778 | 0.036622 | 122.5067 | 122.5937 | -0.15564 | 122.2916 | 0.086976 | 0.22888 | 122.525 | 122.6624 | 122.4838 | 122.6761 | 122.5067 | 122.7264 | 122.5433 | 122.2916 | 122.6761 | 122.5067 | 122.5433 | 122.4838 | 122.7264 | -0.36163 | -0.3479
2223.6875 | 122.7676 | -122.4701 | 0.086975 | -0.005951 | 0.0149 | 0.010544 | 0.0027066 | -0.005834 | -0.0073337 | 0.0066373 | -0.027466 | 0.17395 | -0.24261 | 0.09613 | 0.009155 | 0.059509 | 0.036621 | 0.19684 | 0.21515 | -0.21515 | 122.2275 | 0.086975 | 122.4426 | 122.5662 | -0.07782 | 122.2549 | 0.12817 | 0.21515 | 122.5067 | 122.6669 | 122.4792 | 122.644 | 122.4426 | 122.6852 | 122.5296 | 122.2549 | 122.644 | 122.4426 | 122.5296 | 122.4792 | 122.6852 | -0.32959 | -0.30212
2225.375 | 122.8043 | -122.4701 | 0.091553 | -0.005951 | 0.018105 | 0.013108 | 0.0022794 | -0.0062614 | -0.0058383 | 0.0045011 | -0.022888 | 0.1831 | -0.23346 | 0.073242 | 0.004578 | 0.050354 | 0.059509 | 0.19684 | 0.21973 | -0.21973 | 122.2366 | 0.091552 | 122.4472 | 122.5433 | -0.086975 | 122.2504 | 0.12817 | 0.21057 | 122.5296 | 122.6669 | 122.4747 | 122.6532 | 122.4472 | 122.6898 | 122.5204 | 122.2504 | 122.6532 | 122.4472 | 122.5204 | 122.4747 | 122.6898 | -0.32501 | -0.31128
2227.1094 | 122.7951 | -122.4426 | 0.082397 | -0.005951 | 0.015114 | 0.0075537 | 0.0065518 | -0.009893 | -0.0047703 | 0.0036465 | -0.018311 | 0.18768 | -0.22888 | 0.07782 | 0.004578 | 0.041199 | 0.054932 | 0.19226 | 0.21515 | -0.24719 | 122.2137 | 0.10529 | 122.4243 | 122.5204 | -0.077819 | 122.1954 | 0.13275 | 0.21057 | 122.4976 | 122.6349 | 122.4472 | 122.6303 | 122.4243 | 122.6578 | 122.4838 | 122.1954 | 122.6303 | 122.4243 | 122.4838 | 122.4472 | 122.6578 | -0.31128 | -0.32959
2228.875 | 122.7722 | -122.438 | 0.082397 | -0.013581 | 0.0149 | 0.01439 | -0.00028419 | -0.0066886 | -0.0060519 | 0.0053555 | 0.027466 | 0.14648 | -0.19226 | 0.13275 | 0.068665 | 0.13733 | -0.10071 | 0.2655 | 0.17853 | -0.20599 | 122.2458 | 0.064087 | 122.4655 | 122.5708 | -0.013732 | 122.2321 | 0.096131 | 0.21973 | 122.3373 | 122.7036 | 122.5067 | 122.5845 | 122.4655 | 122.6166 | 122.5754 | 122.2321 | 122.5845 | 122.4655 | 122.5754 | 122.5067 | 122.6166 | -0.27466 | -0.28839
2230.5625 | 122.7814 | -122.4609 | 0.086975 | -0.005951 | 0.015114 | 0.015671 | 0.0012112 | -0.0079704 | -0.0060519 | 0.0059963 | 0.032043 | 0.13733 | -0.21057 | 0.15106 | 0.073242 | 0.15106 | -0.091553 | 0.27924 | 0.17395 | -0.19226 | 122.2504 | 0.050354 | 122.493 | 122.612 | -0.013733 | 122.2687 | 0.086975 | 0.24261 | 122.3694 | 122.7402 | 122.5342 | 122.5983 | 122.493 | 122.6349 | 122.612 | 122.2687 | 122.5983 | 122.493 | 122.612 | 122.5342 | 122.6349 | -0.29755 | -0.27924
2232.3125 | 122.644 | -122.4976 | 0.1236 | -0.005951 | 0.015541 | 0.014603 | 0.0016384 | -0.0051932 | -0.0045565 | 0.0059963 | 0.11444 | 0.13733 | -0.17853 | 0.2243 | 0.11444 | 0.19226 | -0.20599 | 0.31128 | 0.16937 | -0.1831 | 122.319 | 0.013733 | 122.612 | 122.7219 | -0.009155 | 122.3145 | 0.045777 | 0.29297 | 122.2916 | 122.8088 | 122.612 | 122.6349 | 122.612 | 122.6669 | 122.6898 | 122.3145 | 122.6349 | 122.612 | 122.6898 | 122.612 | 122.6669 | -0.30212 | -0.3067
2234 | 122.6624 | -122.5021 | 0.12817 | 0.016937 | 0.014473 | 0.010758 | 0.0093288 | -0.0060478 | -0.0079745 | 0.0045011 | 0.050354 | 0.14191 | -0.21057 | 0.16022 | 0.027466 | 0.10986 | -0.045776 | 0.23804 | 0.19226 | -0.20142 | 122.2916 | 0.013733 | 122.5525 | 122.6624 | -0.10071 | 122.3007 | 0.064087 | 0.26093 | 122.4564 | 122.7402 | 122.5296 | 122.644 | 122.5525 | 122.6944 | 122.612 | 122.3007 | 122.644 | 122.5525 | 122.612 | 122.5296 | 122.6944 | -0.33875 | -0.32959
2235.75 | 122.7127 | -122.4701 | 0.10529 | -0.005951 | 0.016609 | 0.013535 | -0.0013522 | -0.0077566 | -0.0032749 | 0.0057827 | 0.068665 | 0.14191 | -0.18768 | 0.16479 | 0.086975 | 0.14648 | -0.15106 | 0.27924 | 0.16022 | -0.19226 | 122.2824 | 0.036621 | 122.5388 | 122.6349 | -0.018311 | 122.2778 | 0.054931 | 0.25635 | 122.319 | 122.7493 | 122.5571 | 122.612 | 122.5388 | 122.6303 | 122.6166 | 122.2778 | 122.612 | 122.5388 | 122.6166 | 122.5571 | 122.6303 | -0.29297 | -0.29755
2237.4375 | 122.7402 | -122.4838 | 0.091553 | 0.0016785 | 0.011055 | 0.011826 | 0.0020658 | -0.010107 | -0.0060519 | 0.0079189 | 0.07782 | 0.10986 | -0.1831 | 0.21973 | 0.11444 | 0.1831 | -0.12817 | 0.33417 | 0.16937 | -0.17853 | 122.3007 | 0.01831 | 122.5616 | 122.7036 | 0.022888 | 122.3053 | 0.07782 | 0.26092 | 122.3557 | 122.818 | 122.5983 | 122.5937 | 122.5616 | 122.6532 | 122.6669 | 122.3053 | 122.5937 | 122.5616 | 122.6669 | 122.5983 | 122.6532 | -0.27466 | -0.27008
2239.1875 | 122.7905 | -122.4609 | 0.073242 | -0.005951 | 0.014473 | 0.0079809 | 0.0071926 | -0.0069022 | -0.0077609 | 0.0074917 | -0.013733 | 0.16479 | -0.24261 | 0.09613 | 0.004578 | 0.045776 | 0.036621 | 0.18768 | 0.21973 | -0.21057 | 122.2183 | 0.091553 | 122.4472 | 122.5571 | -0.068664 | 122.2504 | 0.14649 | 0.22888 | 122.4976 | 122.6486 | 122.4655 | 122.6257 | 122.4472 | 122.6807 | 122.5067 | 122.2504 | 122.6257 | 122.4472 | 122.5067 | 122.4655 | 122.6807 | -0.31586 | -0.28381
2240.9531 | 122.6761 | -122.5296 | 0.11444 | -0.013581 | 0.014473 | 0.010758 | 0.004202 | -0.0077566 | -0.0062655 | 0.0055691 | 0.050354 | 0.15564 | -0.21973 | 0.16937 | 0.050354 | 0.10529 | -0.059509 | 0.25635 | 0.20599 | -0.20142 | 122.3099 | 0.041199 | 122.58 | 122.699 | -0.064087 | 122.3282 | 0.091553 | 0.27008 | 122.4701 | 122.7859 | 122.58 | 122.6852 | 122.58 | 122.7356 | 122.6349 | 122.3282 | 122.6852 | 122.58 | 122.6349 | 122.58 | 122.7356 | -0.33417 | -0.31586
2242.7031 | 122.644 | -122.525 | 0.11444 | -0.005951 | 0.014259 | 0.017167 | 0.0037748 | -0.0051932 | -0.0054111 | 0.0077053 | 0.10071 | 0.11444 | -0.17395 | 0.18768 | 0.1236 | 0.1831 | -0.21973 | 0.30212 | 0.16479 | -0.17853 | 122.3511 | 0 | 122.6257 | 122.7127 | 0.009155 | 122.3465 | 0.050354 | 0.27466 | 122.3053 | 122.8271 | 122.6486 | 122.6395 | 122.6257 | 122.6898 | 122.7081 | 122.3465 | 122.6395 | 122.6257 | 122.7081 | 122.6486 | 122.6898 | -0.28839 | -0.29297
2244.375 | 122.731 | -122.493 | 0.11444 | -0.005951 | 0.016182 | 0.010972 | 0.0054836 | -0.0086112 | -0.0077609 | 0.0059963 | 0.027466 | 0.17395 | -0.21515 | 0.14191 | 0.050354 | 0.082397 | 0.004578 | 0.24719 | 0.20142 | -0.21515 | 122.2778 | 0.059509 | 122.5204 | 122.6349 | -0.064087 | 122.2778 | 0.086975 | 0.24261 | 122.4976 | 122.7402 | 122.5433 | 122.6669 | 122.5204 | 122.6944 | 122.5754 | 122.2778 | 122.6669 | 122.5204 | 122.5754 | 122.5433 | 122.6944 | -0.32959 | -0.32959
2246.125 | 122.6532 | -122.525 | 0.11902 | -0.005951 | 0.0149 | 0.01204 | 0.0014248 | -0.004766 | -0.0069065 | 0.0055691 | 0.10071 | 0.12817 | -0.17853 | 0.19226 | 0.10986 | 0.19226 | -0.21057 | 0.31586 | 0.16022 | -0.16022 | 122.3465 | 0.009155 | 122.6257 | 122.7173 | -0.009156 | 122.3648 | 0.041198 | 0.27924 | 122.3145 | 122.8409 | 122.6349 | 122.6532 | 122.6257 | 122.6852 | 122.7173 | 122.3648 | 122.6532 | 122.6257 | 122.7173 | 122.6349 | 122.6852 | -0.29755 | -0.27924
2247.875 | 122.7585 | -122.4884 | 0.09613 | 0.0016785 | 0.014259 | 0.011612 | 0.00057041 | -0.008184 | -0.0043429 | 0.0077053 | 0.086975 | 0.12817 | -0.18768 | 0.20599 | 0.10529 | 0.17395 | -0.091553 | 0.32501 | 0.17853 | -0.19226 | 122.3007 | 0.032044 | 122.5754 | 122.6944 | 0.009156 | 122.2961 | 0.082398 | 0.27466 | 122.3969 | 122.8134 | 122.5937 | 122.6166 | 122.5754 | 122.6669 | 122.6624 | 122.2961 | 122.6166 | 122.5754 | 122.6624 | 122.5937 | 122.6669 | -0.28381 | -0.28839
2249.625 | 122.6624 | -122.4838 | 0.10529 | 0.0016785 | 0.015327 | 0.013108 | 0.0046292 | -0.0062614 | -0.0037021 | 0.0036465 | 0.027466 | 0.17395 | -0.2243 | 0.11902 | 0.027466 | 0.10071 | -0.11444 | 0.21057 | 0.18768 | -0.19684 | 122.2595 | 0.068664 | 122.5113 | 122.6028 | -0.07782 | 122.287 | 0.082397 | 0.25177 | 122.3694 | 122.6944 | 122.5113 | 122.6578 | 122.5113 | 122.6715 | 122.5845 | 122.287 | 122.6578 | 122.5113 | 122.5845 | 122.5113 | 122.6715 | -0.32959 | -0.30212
2251.3125 | 122.7997 | -122.4792 | 0.07782 | 0.0016785 | 0.014046 | 0.0092627 | -0.00049779 | -0.0066886 | -0.0049839 | 0.0047147 | 0.027466 | 0.13275 | -0.1831 | 0.13733 | 0.054932 | 0.13275 | -0.082397 | 0.2655 | 0.18768 | -0.20142 | 122.2961 | 0.054931 | 122.5067 | 122.6166 | -0.022888 | 122.2778 | 0.10986 | 0.21057 | 122.3969 | 122.7448 | 122.5342 | 122.612 | 122.5067 | 122.6669 | 122.612 | 122.2778 | 122.612 | 122.5067 | 122.612 | 122.5342 | 122.6669 | -0.26092 | -0.27924
2253.0625 | 122.7997 | -122.4655 | 0.086975 | -0.005951 | 0.013832 | 0.0099037 | -0.0017794 | -0.0079704 | -0.0043429 | 0.0064237 | 0.027466 | 0.11902 | -0.1831 | 0.14191 | 0.059509 | 0.13275 | -0.10071 | 0.25635 | 0.18768 | -0.21057 | 122.2824 | 0.032044 | 122.493 | 122.6074 | -0.027466 | 122.2549 | 0.10071 | 0.21057 | 122.3648 | 122.7219 | 122.525 | 122.5845 | 122.493 | 122.6532 | 122.5983 | 122.2549 | 122.5845 | 122.493 | 122.5983 | 122.525 | 122.6532 | -0.27008 | -0.29755
2254.8281 | 122.7219 | -122.4976 | 0.11444 | 0.0016785 | 0.01725 | 0.012467 | 0.0054836 | -0.0060478 | -0.0073337 | 0.0045011 | -0.009155 | 0.16022 | -0.23804 | 0.091553 | -0.018311 | 0.054932 | -0.022888 | 0.16022 | 0.20599 | -0.23346 | 122.2595 | 0.045776 | 122.4884 | 122.5891 | -0.13275 | 122.2641 | 0.091553 | 0.22888 | 122.4747 | 122.6578 | 122.4792 | 122.6578 | 122.4884 | 122.7036 | 122.5525 | 122.2641 | 122.6578 | 122.4884 | 122.5525 | 122.4792 | 122.7036 | -0.35248 | -0.3479
2256.5156 | 122.7448 | -122.493 | 0.10071 | -0.005951 | 0.013405 | 0.011185 | 0.00035681 | -0.0051932 | -0.0056247 | 0.0055691 | 0.07782 | 0.1236 | -0.18768 | 0.21057 | 0.11444 | 0.1831 | -0.12817 | 0.35248 | 0.16479 | -0.18768 | 122.3053 | 0.022888 | 122.5708 | 122.7036 | 0.013733 | 122.3053 | 0.064087 | 0.2655 | 122.3648 | 122.8455 | 122.6074 | 122.6166 | 122.5708 | 122.6578 | 122.6761 | 122.3053 | 122.6166 | 122.5708 | 122.6761 | 122.6074 | 122.6578 | -0.28839 | -0.28839
2258.2656 | 122.6761 | -122.5296 | 0.1236 | 0.0016785 | 0.013832 | 0.01503 | 0.0014248 | -0.0051932 | -0.0062655 | 0.0068509 | 0.09613 | 0.11444 | -0.17395 | 0.20142 | 0.10529 | 0.17853 | -0.1831 | 0.30212 | 0.15106 | -0.16937 | 122.3557 | -0.009155 | 122.6257 | 122.731 | -0.01831 | 122.3602 | 0.027466 | 0.27008 | 122.3465 | 122.8317 | 122.6349 | 122.644 | 122.6257 | 122.6807 | 122.7081 | 122.3602 | 122.644 | 122.6257 | 122.7081 | 122.6349 | 122.6807 | -0.29755 | -0.29297
2260.0156 | 122.6669 | -122.5204 | 0.12817 | -0.005951 | 0.014473 | 0.012467 | 0.0044156 | -0.0079704 | -0.0058383 | 0.0081325 | 0.073242 | 0.13275 | -0.19226 | 0.20599 | 0.10529 | 0.20142 | -0.19684 | 0.3067 | 0.16479 | -0.17395 | 122.3282 | 0.004577 | 122.5937 | 122.7264 | -0.022888 | 122.3465 | 0.036621 | 0.2655 | 122.3236 | 122.8271 | 122.6257 | 122.6532 | 122.5937 | 122.6852 | 122.7219 | 122.3465 | 122.6532 | 122.5937 | 122.7219 | 122.6257 | 122.6852 | -0.32044 | -0.30212
2261.7031 | 122.7768 | -122.4884 | 0.10529 | 0.0016785 | 0.012123 | 0.011399 | 0.00057041 | -0.0083976 | -0.0079745 | 0.0064237 | 0.050354 | 0.13275 | -0.19684 | 0.16022 | 0.073242 | 0.14191 | -0.036621 | 0.27924 | 0.19684 | -0.18768 | 122.2916 | 0.027465 | 122.5388 | 122.6486 | -0.032044 | 122.3007 | 0.091552 | 0.24719 | 122.4518 | 122.7676 | 122.5616 | 122.6212 | 122.5388 | 122.6852 | 122.6303 | 122.3007 | 122.6212 | 122.5388 | 122.6303 | 122.5616 | 122.6852 | -0.30212 | -0.29297
2263.4531 | 122.8134 | -122.4976 | 0.082397 | 0.009308 | 0.013832 | 0.0049903 | 0.001852 | -0.0079704 | -0.0062655 | 0.0066373 | -0.018311 | 0.16022 | -0.21973 | 0.10986 | 0.022888 | 0.059509 | 0.050354 | 0.21057 | 0.21515 | -0.21973 | 122.2778 | 0.07782 | 122.4792 | 122.6074 | -0.059509 | 122.2778 | 0.13275 | 0.20142 | 122.5479 | 122.7081 | 122.5204 | 122.6578 | 122.4792 | 122.7127 | 122.5571 | 122.2778 | 122.6578 | 122.4792 | 122.5571 | 122.5204 | 122.7127 | -0.30212 | -0.30212
2265.1406 | 122.7722 | -122.4701 | 0.091553 | 0.0016785 | 0.0149 | 0.0075537 | -0.00028419 | -0.0077566 | -0.0047703 | 0.0070645 | 0.064087 | 0.14648 | -0.18768 | 0.20142 | 0.11444 | 0.1831 | -0.12817 | 0.33875 | 0.17853 | -0.19684 | 122.2824 | 0.054931 | 122.5342 | 122.6715 | 0.022888 | 122.2733 | 0.086975 | 0.25177 | 122.3419 | 122.8088 | 122.5845 | 122.6166 | 122.5342 | 122.6486 | 122.6532 | 122.2733 | 122.6166 | 122.5342 | 122.6532 | 122.5845 | 122.6486 | -0.27924 | -0.28839
2266.875 | 122.7951 | -122.4838 | 0.091553 | 0.0016785 | 0.012978 | 0.010117 | 0.00078401 | -0.0079704 | -0.0037021 | 0.0025783 | 0.036621 | 0.11902 | -0.19226 | 0.16479 | 0.07782 | 0.16479 | -0.12817 | 0.29755 | 0.17395 | -0.1831 | 122.2916 | 0.027466 | 122.5204 | 122.6486 | -0.013733 | 122.3007 | 0.082397 | 0.22888 | 122.3557 | 122.7814 | 122.5616 | 122.6028 | 122.5204 | 122.6578 | 122.6486 | 122.3007 | 122.6028 | 122.5204 | 122.6486 | 122.5616 | 122.6578 | -0.28381 | -0.27466
2268.6094 | 122.7951 | -122.4884 | 0.068665 | 0.009308 | 0.017036 | 0.012681 | 0.0050564 | -0.0069022 | -0.0056247 | 0.0053555 | -0.013733 | 0.16022 | -0.24261 | 0.1236 | -0.004578 | 0.050354 | 0.032043 | 0.20142 | 0.20142 | -0.2243 | 122.2458 | 0.091552 | 122.4747 | 122.612 | -0.073243 | 122.2641 | 0.13275 | 0.22888 | 122.5204 | 122.6898 | 122.4838 | 122.6486 | 122.4747 | 122.6898 | 122.5388 | 122.2641 | 122.6486 | 122.4747 | 122.5388 | 122.4838 | 122.6898 | -0.31128 | -0.29297
2270.3594 | 122.7219 | -122.5204 | 0.10071 | 0.009308 | 0.014473 | 0.013535 | 0.006979 | -0.0069022 | -0.0066929 | 0.0057827 | -0.022888 | 0.15564 | -0.2243 | 0.091553 | -0.004578 | 0.045776 | -0.009155 | 0.16479 | 0.20599 | -0.22888 | 122.2961 | 0.054932 | 122.4976 | 122.612 | -0.10529 | 122.2916 | 0.10529 | 0.20142 | 122.5113 | 122.6852 | 122.5159 | 122.6761 | 122.4976 | 122.7264 | 122.5662 | 122.2916 | 122.6761 | 122.4976 | 122.5662 | 122.5159 | 122.7264 | -0.32501 | -0.32959
2272.1094 | 122.6761 | -122.5204 | 0.1236 | -0.005951 | 0.015114 | 0.011399 | 0.0014248 | -0.004766 | -0.0049839 | 0.0053555 | 0.10071 | 0.1236 | -0.17853 | 0.20142 | 0.10529 | 0.19684 | -0.19684 | 0.30212 | 0.15564 | -0.17853 | 122.3419 | 0 | 122.6212 | 122.7219 | -0.01831 | 122.3419 | 0.032044 | 0.27924 | 122.3236 | 122.8226 | 122.6257 | 122.644 | 122.6212 | 122.6761 | 122.7173 | 122.3419 | 122.644 | 122.6212 | 122.7173 | 122.6257 | 122.6761 | -0.30212 | -0.30212
2273.875 | 122.8134 | -122.4838 | 0.091553 | 0.0016785 | 0.015968 | 0.012894 | 0.00035681 | -0.0094656 | -0.0034885 | 0.0064237 | 0.059509 | 0.1236 | -0.21057 | 0.15106 | 0.073242 | 0.10986 | -0.027466 | 0.27466 | 0.19684 | -0.20599 | 122.2733 | 0.032043 | 122.5433 | 122.6349 | -0.018311 | 122.2778 | 0.10529 | 0.27008 | 122.4564 | 122.7585 | 122.5571 | 122.6074 | 122.5433 | 122.6807 | 122.5937 | 122.2778 | 122.6074 | 122.5433 | 122.5937 | 122.5571 | 122.6807 | -0.30212 | -0.29755
2275.5625 | 122.7264 | -122.5159 | 0.10071 | 0.009308 | 0.016396 | 0.018235 | 0.0046292 | -0.0062614 | -0.0073337 | 0.0072781 | 0.036621 | 0.15106 | -0.22888 | 0.14191 | 0.036621 | 0.09613 | -0.027466 | 0.24261 | 0.21973 | -0.20599 | 122.287 | 0.050354 | 122.5525 | 122.6578 | -0.064087 | 122.3099 | 0.11902 | 0.2655 | 122.4884 | 122.7585 | 122.5525 | 122.6669 | 122.5525 | 122.7356 | 122.612 | 122.3099 | 122.6669 | 122.5525 | 122.612 | 122.5525 | 122.7356 | -0.32959 | -0.3067
2277.2969 | 122.7173 | -122.5479 | 0.086975 | 0.0016785 | 0.017891 | 0.012681 | 0.0054836 | -0.005834 | -0.0062655 | 0.0055691 | 0.050354 | 0.16937 | -0.21973 | 0.14648 | 0.036621 | 0.091553 | -0.027466 | 0.23346 | 0.21515 | -0.20599 | 122.3282 | 0.082398 | 122.5983 | 122.6944 | -0.050354 | 122.3419 | 0.12817 | 0.27008 | 122.5204 | 122.7814 | 122.5845 | 122.7173 | 122.5983 | 122.7631 | 122.6395 | 122.3419 | 122.7173 | 122.5983 | 122.6395 | 122.5845 | 122.7631 | -0.3067 | -0.29297
2279.0625 | 122.7081 | -122.5342 | 0.10986 | 0.0016785 | 0.017036 | 0.012253 | 0.0012112 | -0.0056204 | -0.0060519 | 0.0038601 | 0 | 0.16937 | -0.2243 | 0.10071 | 0.004578 | 0.068665 | -0.068665 | 0.17395 | 0.20599 | -0.2243 | 122.3099 | 0.05951 | 122.5342 | 122.6349 | -0.10529 | 122.3099 | 0.096131 | 0.2243 | 122.4655 | 122.7081 | 122.5388 | 122.7036 | 122.5342 | 122.7402 | 122.6028 | 122.3099 | 122.7036 | 122.5342 | 122.6028 | 122.5388 | 122.7402 | -0.33417 | -0.33417
2280.75 | 122.7173 | -122.525 | 0.11444 | 0.0016785 | 0.016609 | 0.016526 | 0.0037748 | -0.004766 | -0.0081881 | 0.0074917 | -0.027466 | 0.15106 | -0.22888 | 0.07782 | -0.027466 | 0.059509 | -0.004578 | 0.14191 | 0.21057 | -0.21057 | 122.2961 | 0.036621 | 122.4976 | 122.6028 | -0.14191 | 122.3145 | 0.09613 | 0.20142 | 122.5204 | 122.6669 | 122.4976 | 122.6761 | 122.4976 | 122.7356 | 122.5845 | 122.3145 | 122.6761 | 122.4976 | 122.5845 | 122.4976 | 122.7356 | -0.34332 | -0.32501
2282.4844 | 122.731 | -122.5388 | 0.10986 | 0.0016785 | 0.016609 | 0.013108 | 0.0033474 | -0.0045524 | -0.0071201 | 0.0066373 | -0.009155 | 0.12817 | -0.23346 | 0.064087 | -0.009155 | 0.041199 | 0 | 0.15564 | 0.19684 | -0.21515 | 122.3053 | 0.018311 | 122.5296 | 122.6028 | -0.11902 | 122.3236 | 0.086975 | 0.2243 | 122.5388 | 122.6944 | 122.5296 | 122.6669 | 122.5296 | 122.7356 | 122.58 | 122.3236 | 122.6669 | 122.5296 | 122.58 | 122.5296 | 122.7356 | -0.34332 | -0.32501
2284.2031 | 122.6669 | -122.5525 | 0.10529 | -0.005951 | 0.016609 | 0.011185 | -0.0011386 | -0.0051932 | -0.0043429 | 0.0074917 | 0.086975 | 0.14191 | -0.19226 | 0.18768 | 0.10529 | 0.19226 | -0.17395 | 0.28839 | 0.16937 | -0.17395 | 122.3602 | 0.036621 | 122.6395 | 122.7402 | 0 | 122.3785 | 0.064087 | 0.27924 | 122.3785 | 122.8409 | 122.6578 | 122.6944 | 122.6395 | 122.7219 | 122.7448 | 122.3785 | 122.6944 | 122.6395 | 122.7448 | 122.6578 | 122.7219 | -0.29755 | -0.27924
2285.9219 | 122.7676 | -122.5021 | 0.091553 | -0.005951 | 0.014687 | 0.013108 | -0.0019932 | -0.0056204 | -0.0045565 | 0.0059963 | 0.091553 | 0.11902 | -0.1831 | 0.1831 | 0.11902 | 0.19226 | -0.1236 | 0.3479 | 0.16479 | -0.19684 | 122.319 | 0.027466 | 122.5937 | 122.6852 | 0.027466 | 122.3053 | 0.073242 | 0.27466 | 122.3785 | 122.85 | 122.6212 | 122.6212 | 122.5937 | 122.6669 | 122.6944 | 122.3053 | 122.6212 | 122.5937 | 122.6944 | 122.6212 | 122.6669 | -0.27466 | -0.28839
2287.6719 | 122.7859 | -122.4976 | 0.086975 | -0.02121 | 0.013832 | 0.0077673 | -0.0022068 | -0.007543 | -0.0043429 | 0.0072781 | 0.07782 | 0.13275 | -0.19226 | 0.21515 | 0.12817 | 0.20142 | -0.14191 | 0.35706 | 0.13733 | -0.18768 | 122.3053 | 0.045776 | 122.5754 | 122.7127 | 0.041199 | 122.3099 | 0.050354 | 0.27008 | 122.3557 | 122.8546 | 122.6257 | 122.6303 | 122.5754 | 122.6349 | 122.699 | 122.3099 | 122.6303 | 122.5754 | 122.699 | 122.6257 | 122.6349 | -0.27924 | -0.27466
2289.4219 | 122.7676 | -122.5021 | 0.10529 | 0.0016785 | 0.014046 | 0.011399 | -0.00092499 | -0.0073294 | -0.0056247 | 0.0051419 | 0.10529 | 0.11902 | -0.19226 | 0.2243 | 0.13733 | 0.21515 | -0.16022 | 0.36163 | 0.16937 | -0.17395 | 122.3099 | 0.013733 | 122.6074 | 122.7264 | 0.032043 | 122.3282 | 0.064087 | 0.29755 | 122.3419 | 122.8638 | 122.6395 | 122.6212 | 122.6074 | 122.6715 | 122.7173 | 122.3282 | 122.6212 | 122.6074 | 122.7173 | 122.6395 | 122.6715 | -0.29755 | -0.27924
2291.125 | 122.6944 | -122.5525 | 0.13275 | 0.009308 | 0.016396 | 0.015458 | 0.006979 | -0.0060478 | -0.0084017 | 0.0064237 | 0.064087 | 0.13275 | -0.23346 | 0.13275 | 0.036621 | 0.10071 | -0.045776 | 0.24261 | 0.20142 | -0.21057 | 122.319 | 0 | 122.6166 | 122.6852 | -0.09613 | 122.3419 | 0.068665 | 0.29755 | 122.5067 | 122.7951 | 122.5891 | 122.6852 | 122.6166 | 122.7539 | 122.6532 | 122.3419 | 122.6852 | 122.6166 | 122.6532 | 122.5891 | 122.7539 | -0.36621 | -0.34332
2292.875 | 122.699 | -122.5021 | 0.11444 | -0.013581 | 0.016182 | 0.012681 | 0.00057041 | -0.0054068 | -0.0069065 | 0.0072781 | 0.082397 | 0.1236 | -0.19684 | 0.16937 | 0.09613 | 0.16937 | -0.19684 | 0.30212 | 0.15564 | -0.16937 | 122.3053 | 0.009155 | 122.5845 | 122.6715 | -0.018311 | 122.3328 | 0.041199 | 0.27924 | 122.3053 | 122.8043 | 122.5983 | 122.6257 | 122.5845 | 122.6578 | 122.6715 | 122.3328 | 122.6257 | 122.5845 | 122.6715 | 122.5983 | 122.6578 | -0.31128 | -0.28381
2294.5469 | 122.8546 | -122.4792 | 0.068665 | 0.0016785 | 0.015541 | 0.0079809 | 0.0022794 | -0.0086112 | -0.0058383 | 0.0055691 | -0.022888 | 0.16479 | -0.23346 | 0.082397 | 0.009155 | 0.045776 | 0.059509 | 0.21057 | 0.21973 | -0.21973 | 122.2458 | 0.09613 | 122.4564 | 122.5616 | -0.05951 | 122.2595 | 0.15106 | 0.21057 | 122.5388 | 122.6898 | 122.4884 | 122.644 | 122.4564 | 122.699 | 122.525 | 122.2595 | 122.644 | 122.4564 | 122.525 | 122.4884 | 122.699 | -0.30212 | -0.28839
2296.2969 | 122.699 | -122.5479 | 0.13275 | -0.02121 | 0.0149 | 0.0094763 | 0.003561 | -0.0066886 | -0.0075473 | 0.0059963 | 0.036621 | 0.15564 | -0.20599 | 0.15564 | 0.045776 | 0.10986 | -0.032043 | 0.25177 | 0.19684 | -0.21973 | 122.3419 | 0.022889 | 122.5845 | 122.7036 | -0.086975 | 122.3282 | 0.064087 | 0.24262 | 122.5159 | 122.7997 | 122.5937 | 122.7036 | 122.5845 | 122.7448 | 122.6578 | 122.3282 | 122.7036 | 122.5845 | 122.6578 | 122.5937 | 122.7448 | -0.33875 | -0.35248
2297.9688 | 122.6898 | -122.5616 | 0.11902 | 0.009308 | 0.014259 | 0.0092627 | 0.00057041 | -0.0034842 | -0.0064791 | 0.0055691 | 0.091553 | 0.13275 | -0.16937 | 0.20142 | 0.10071 | 0.1831 | -0.20142 | 0.29297 | 0.16479 | -0.1831 | 122.3923 | 0.013732 | 122.6532 | 122.7631 | -0.018311 | 122.3785 | 0.045776 | 0.26093 | 122.3602 | 122.8546 | 122.6624 | 122.6944 | 122.6532 | 122.7264 | 122.7448 | 122.3785 | 122.6944 | 122.6532 | 122.7448 | 122.6624 | 122.7264 | -0.28839 | -0.30212
2299.7188 | 122.7264 | -122.5388 | 0.091553 | -0.005951 | 0.015541 | 0.010117 | -0.0013522 | -0.005834 | -0.0058383 | 0.0051419 | 0.091553 | 0.1236 | -0.19226 | 0.16937 | 0.073242 | 0.15106 | -0.16022 | 0.29755 | 0.15564 | -0.16937 | 122.3465 | 0.032043 | 122.6303 | 122.7081 | -0.018311 | 122.3694 | 0.064087 | 0.28381 | 122.3785 | 122.8363 | 122.612 | 122.6624 | 122.6303 | 122.6944 | 122.6898 | 122.3694 | 122.6624 | 122.6303 | 122.6898 | 122.612 | 122.6944 | -0.28381 | -0.26093
2301.4062 | 122.731 | -122.5296 | 0.10071 | 0.0016785 | 0.015327 | 0.01204 | 0.0071926 | -0.0034842 | -0.0079745 | 0.0064237 | -0.032043 | 0.15106 | -0.24719 | 0.086975 | -0.022888 | 0.036621 | -0.013733 | 0.16022 | 0.22888 | -0.21973 | 122.2824 | 0.050354 | 122.4976 | 122.6166 | -0.1236 | 122.3099 | 0.12817 | 0.21515 | 122.5159 | 122.6898 | 122.5067 | 122.6807 | 122.4976 | 122.7585 | 122.5662 | 122.3099 | 122.6807 | 122.4976 | 122.5662 | 122.5067 | 122.7585 | -0.3479 | -0.32044
2303.1406 | 122.6852 | -122.5662 | 0.11444 | -0.005951 | 0.012978 | 0.014176 | 0.005911 | -0.0039114 | -0.0075473 | 0.0053555 | 0.059509 | 0.13733 | -0.21515 | 0.13733 | 0.036621 | 0.10529 | -0.032043 | 0.2243 | 0.20142 | -0.21515 | 122.3511 | 0.022888 | 122.6257 | 122.7036 | -0.07782 | 122.3511 | 0.086975 | 0.27466 | 122.5342 | 122.7905 | 122.6028 | 122.7036 | 122.6257 | 122.7676 | 122.6715 | 122.3511 | 122.7036 | 122.6257 | 122.6715 | 122.6028 | 122.7676 | -0.32959 | -0.32959
2304.8906 | 122.7768 | -122.525 | 0.10529 | -0.013581 | 0.016609 | 0.0069129 | -0.0032748 | -0.0051932 | -0.0062655 | 0.0055691 | 0.064087 | 0.11902 | -0.19226 | 0.14648 | 0.068665 | 0.15106 | -0.12817 | 0.26093 | 0.16937 | -0.19684 | 122.3328 | 0.013733 | 122.5891 | 122.6715 | -0.036621 | 122.3282 | 0.064087 | 0.25635 | 122.3969 | 122.7859 | 122.5937 | 122.644 | 122.5891 | 122.6944 | 122.6761 | 122.3282 | 122.644 | 122.5891 | 122.6761 | 122.5937 | 122.6944 | -0.29755 | -0.30212
2306.5781 | 122.6898 | -122.5433 | 0.1236 | 0.0016785 | 0.015327 | 0.0090491 | 0.002493 | -0.0041252 | -0.0058383 | 0.0053555 | 0.10529 | 0.11902 | -0.1831 | 0.19684 | 0.10986 | 0.19226 | -0.21515 | 0.31128 | 0.17395 | -0.17853 | 122.3602 | -0.004577 | 122.6486 | 122.7402 | -0.013733 | 122.3648 | 0.050354 | 0.28839 | 122.3282 | 122.8546 | 122.6532 | 122.6624 | 122.6486 | 122.7173 | 122.7356 | 122.3648 | 122.6624 | 122.6486 | 122.7356 | 122.6532 | 122.7173 | -0.3067 | -0.30212
2308.3281 | 122.7493 | -122.5342 | 0.10529 | 0.0016785 | 0.015327 | 0.010331 | 0.0029202 | -0.003057 | -0.0081881 | 0.0066373 | 0 | 0.16479 | -0.21515 | 0.082397 | -0.009155 | 0.054932 | -0.027466 | 0.16022 | 0.20142 | -0.20599 | 122.319 | 0.059509 | 122.5342 | 122.6166 | -0.11444 | 122.3282 | 0.09613 | 0.21515 | 122.5067 | 122.6944 | 122.525 | 122.699 | 122.5342 | 122.7356 | 122.5891 | 122.3282 | 122.699 | 122.5342 | 122.5891 | 122.525 | 122.7356 | -0.32044 | -0.31128
2310.0781 | 122.7814 | -122.5204 | 0.073242 | -0.013581 | 0.014046 | 0.013108 | -0.0019932 | -0.0066886 | -0.0066929 | 0.0047147 | 0.082397 | 0.14191 | -0.20142 | 0.21057 | 0.11444 | 0.19684 | -0.14648 | 0.32959 | 0.16479 | -0.15564 | 122.319 | 0.068665 | 122.6028 | 122.731 | 0.041199 | 122.3648 | 0.091553 | 0.28381 | 122.374 | 122.85 | 122.6349 | 122.6624 | 122.6028 | 122.6852 | 122.7173 | 122.3648 | 122.6624 | 122.6028 | 122.7173 | 122.6349 | 122.6852 | -0.27466 | -0.22888
2311.8281 | 122.7859 | -122.5113 | 0.086975 | 0.0016785 | 0.015755 | 0.0094763 | -0.0013522 | -0.0054068 | -0.0047703 | 0.0070645 | 0.054932 | 0.11444 | -0.16937 | 0.14648 | 0.068665 | 0.14648 | -0.11902 | 0.27008 | 0.1831 | -0.18768 | 122.3419 | 0.027466 | 122.5662 | 122.6578 | -0.01831 | 122.3236 | 0.09613 | 0.22431 | 122.3923 | 122.7814 | 122.58 | 122.6257 | 122.5662 | 122.6944 | 122.6578 | 122.3236 | 122.6257 | 122.5662 | 122.6578 | 122.58 | 122.6944 | -0.25635 | -0.27466
2313.5938 | 122.7402 | -122.5479 | 0.11444 | 0.0016785 | 0.017677 | 0.010117 | 0.005911 | -0.0051932 | -0.0049839 | 0.0070645 | -0.004578 | 0.16479 | -0.22888 | 0.10071 | -0.009155 | 0.073242 | -0.068665 | 0.18768 | 0.1831 | -0.20142 | 122.319 | 0.050354 | 122.5433 | 122.6486 | -0.1236 | 122.3465 | 0.068664 | 0.2243 | 122.4792 | 122.7356 | 122.5388 | 122.7127 | 122.5433 | 122.731 | 122.6212 | 122.3465 | 122.7127 | 122.5433 | 122.6212 | 122.5388 | 122.731 | -0.34332 | -0.31586
2315.2812 | 122.8409 | -122.525 | 0.086975 | -0.005951 | 0.015327 | 0.013321 | 0.00014321 | -0.0073294 | -0.0054111 | 0.0077053 | -0.036621 | 0.15564 | -0.2243 | 0.07782 | -0.013733 | 0.041199 | 0.059509 | 0.19226 | 0.19684 | -0.24261 | 122.3007 | 0.068665 | 122.4884 | 122.6028 | -0.10071 | 122.2824 | 0.10986 | 0.18768 | 122.5845 | 122.7173 | 122.5113 | 122.6807 | 122.4884 | 122.7219 | 122.5662 | 122.2824 | 122.6807 | 122.4884 | 122.5662 | 122.5113 | 122.7219 | -0.31128 | -0.32959
2317.0312 | 122.7219 | -122.5662 | 0.10529 | -0.005951 | 0.016182 | 0.0090491 | -0.0015658 | -0.0069022 | -0.0054111 | 0.0055691 | 0.10071 | 0.12817 | -0.1831 | 0.1831 | 0.091553 | 0.17853 | -0.17853 | 0.30212 | 0.16022 | -0.18768 | 122.3831 | 0.022888 | 122.6669 | 122.7493 | -0.013733 | 122.3785 | 0.054931 | 0.28381 | 122.3877 | 122.8683 | 122.6578 | 122.6944 | 122.6669 | 122.7264 | 122.7448 | 122.3785 | 122.6944 | 122.6669 | 122.7448 | 122.6578 | 122.7264 | -0.28839 | -0.29297
2318.7812 | 122.7448 | -122.5388 | 0.10529 | 0.0016785 | 0.015541 | 0.010758 | 0.003561 | -0.004766 | -0.0081881 | 0.0057827 | -0.041199 | 0.16022 | -0.21973 | 0.064087 | -0.027466 | 0.032043 | -0.004578 | 0.14191 | 0.21057 | -0.21973 | 122.319 | 0.054931 | 122.4976 | 122.6028 | -0.13275 | 122.319 | 0.10529 | 0.17853 | 122.5342 | 122.6807 | 122.5113 | 122.699 | 122.4976 | 122.7493 | 122.5708 | 122.319 | 122.699 | 122.4976 | 122.5708 | 122.5113 | 122.7493 | -0.32501 | -0.32501
2320.4688 | 122.699 | -122.5433 | 0.12817 | 0.0016785 | 0.014687 | 0.01503 | 0.002493 | -0.0051932 | -0.0039157 | 0.0070645 | 0.059509 | 0.1236 | -0.20599 | 0.17853 | 0.07782 | 0.16022 | -0.16022 | 0.28839 | 0.16479 | -0.17853 | 122.3373 | -0.004578 | 122.6028 | 122.7219 | -0.050354 | 122.3648 | 0.036621 | 0.2655 | 122.3831 | 122.8317 | 122.6212 | 122.6669 | 122.6028 | 122.7081 | 122.7036 | 122.3648 | 122.6669 | 122.6028 | 122.7036 | 122.6212 | 122.7081 | -0.33417 | -0.3067
2322.2031 | 122.7585 | -122.5388 | 0.10986 | -0.005951 | 0.015968 | 0.0096899 | -0.0030612 | -0.006475 | -0.0054111 | 0.0051419 | 0.07782 | 0.11902 | -0.19684 | 0.15564 | 0.10529 | 0.15564 | -0.14191 | 0.27008 | 0.1831 | -0.17853 | 122.3419 | 0.009156 | 122.6166 | 122.6944 | -0.004577 | 122.3602 | 0.073242 | 0.27466 | 122.3969 | 122.8088 | 122.644 | 122.6578 | 122.6166 | 122.7219 | 122.6944 | 122.3602 | 122.6578 | 122.6166 | 122.6944 | 122.644 | 122.7219 | -0.3067 | -0.28839
2323.9531 | 122.7951 | -122.5204 | 0.09613 | 0.0016785 | 0.013618 | 0.0099037 | -0.0032748 | -0.009252 | -0.0056247 | 0.0057827 | 0.064087 | 0.13275 | -0.17853 | 0.19684 | 0.10986 | 0.17853 | -0.15106 | 0.33875 | 0.16937 | -0.19684 | 122.3419 | 0.036621 | 122.5845 | 122.7173 | 0.013733 | 122.3236 | 0.073243 | 0.24261 | 122.3694 | 122.8592 | 122.6303 | 122.6532 | 122.5845 | 122.6898 | 122.699 | 122.3236 | 122.6532 | 122.5845 | 122.699 | 122.6303 | 122.6898 | -0.27466 | -0.29297
2325.7188 | 122.8363 | -122.4976 | 0.09613 | -0.005951 | 0.015968 | 0.011399 | -7.059e-05 | -0.0096794 | -0.0058383 | 0.0059963 | 0.036621 | 0.14191 | -0.19226 | 0.16937 | 0.07782 | 0.14648 | -0.11444 | 0.28839 | 0.17395 | -0.19684 | 122.3053 | 0.045777 | 122.5342 | 122.6669 | -0.01831 | 122.3007 | 0.07782 | 0.22888 | 122.3831 | 122.7859 | 122.5754 | 122.6395 | 122.5342 | 122.6715 | 122.644 | 122.3007 | 122.6395 | 122.5342 | 122.644 | 122.5754 | 122.6715 | -0.28839 | -0.29297
2327.3906 | 122.8455 | -122.5067 | 0.10986 | -0.005951 | 0.016396 | 0.0090491 | 0.0050564 | -0.0088248 | -0.0039157 | 0.0062099 | -0.022888 | 0.16479 | -0.23804 | 0.091553 | -0.004578 | 0.041199 | 0.050354 | 0.19226 | 0.21057 | -0.2243 | 122.2687 | 0.054932 | 122.4838 | 122.5983 | -0.11444 | 122.2824 | 0.10071 | 0.21515 | 122.5571 | 122.699 | 122.5021 | 122.6715 | 122.4838 | 122.7173 | 122.5479 | 122.2824 | 122.6715 | 122.4838 | 122.5479 | 122.5021 | 122.7173 | -0.3479 | -0.33417
2329.0781 | 122.8226 | -122.5113 | 0.082397 | -0.013581 | 0.014046 | 0.010117 | -0.00049779 | -0.0066886 | -0.0054111 | 0.0049283 | 0.022888 | 0.12817 | -0.19226 | 0.13733 | 0.059509 | 0.13275 | -0.11902 | 0.24261 | 0.18768 | -0.1831 | 122.319 | 0.045777 | 122.5342 | 122.6486 | -0.022888 | 122.3282 | 0.10529 | 0.21515 | 122.3923 | 122.7539 | 122.5708 | 122.6395 | 122.5342 | 122.699 | 122.644 | 122.3282 | 122.6395 | 122.5342 | 122.644 | 122.5708 | 122.699 | -0.27466 | -0.2655
2330.8438 | 122.7722 | -122.5433 | 0.082397 | 0.0016785 | 0.014259 | 0.0066993 | -0.00071139 | -0.0088248 | -0.0056247 | 0.0055691 | 0.086975 | 0.12817 | -0.20599 | 0.16937 | 0.073242 | 0.14648 | -0.15564 | 0.27924 | 0.16479 | -0.19684 | 122.3373 | 0.045777 | 122.6303 | 122.7127 | -0.009155 | 122.3465 | 0.082398 | 0.29297 | 122.3877 | 122.8226 | 122.6166 | 122.6715 | 122.6303 | 122.7081 | 122.6898 | 122.3465 | 122.6715 | 122.6303 | 122.6898 | 122.6166 | 122.7081 | -0.28839 | -0.27924
2332.5938 | 122.731 | -122.5571 | 0.11444 | -0.005951 | 0.015114 | 0.014817 | 0.002493 | -0.0062614 | -0.0049839 | 0.0057827 | 0.07782 | 0.10986 | -0.18768 | 0.20142 | 0.07782 | 0.17853 | -0.18768 | 0.27924 | 0.15564 | -0.17395 | 122.3694 | -0.004578 | 122.6349 | 122.7585 | -0.036621 | 122.3831 | 0.041199 | 0.2655 | 122.3694 | 122.8363 | 122.6349 | 122.6669 | 122.6349 | 122.7127 | 122.7356 | 122.3831 | 122.6669 | 122.6349 | 122.7356 | 122.6349 | 122.7127 | -0.30212 | -0.28839
2334.3438 | 122.7356 | -122.5479 | 0.091553 | -0.005951 | 0.017036 | 0.010972 | 0.001852 | -0.0069022 | -0.0058383 | 0.0053555 | 0.10529 | 0.11902 | -0.15564 | 0.21057 | 0.10071 | 0.17853 | -0.20142 | 0.29297 | 0.16937 | -0.19684 | 122.3923 | 0.027466 | 122.6532 | 122.7585 | 0.009155 | 122.3511 | 0.07782 | 0.26093 | 122.3465 | 122.8409 | 122.6486 | 122.6669 | 122.6532 | 122.7173 | 122.7264 | 122.3511 | 122.6669 | 122.6532 | 122.7264 | 122.6486 | 122.7173 | -0.24719 | -0.28839
2336.1094 | 122.7448 | -122.5388 | 0.1236 | -0.005951 | 0.016182 | 0.013535 | 0.0061246 | -0.0071158 | -0.0062655 | 0.0077053 | 0.022888 | 0.17395 | -0.21057 | 0.10986 | -0.013733 | 0.068665 | -0.027466 | 0.17853 | 0.1831 | -0.21515 | 122.3282 | 0.050354 | 122.5616 | 122.6486 | -0.13733 | 122.3236 | 0.059509 | 0.23346 | 122.5113 | 122.7173 | 122.525 | 122.7127 | 122.5616 | 122.7219 | 122.6074 | 122.3236 | 122.7127 | 122.5616 | 122.6074 | 122.525 | 122.7219 | -0.33417 | -0.33875
2337.7969 | 122.7356 | -122.5708 | 0.10529 | -0.005951 | 0.017464 | 0.011399 | 0.00099761 | -0.0039114 | -0.0047703 | 0.0042873 | 0.082397 | 0.13275 | -0.16479 | 0.17395 | 0.09613 | 0.16937 | -0.17853 | 0.27924 | 0.16022 | -0.17853 | 122.406 | 0.027465 | 122.6532 | 122.7448 | -0.009156 | 122.3923 | 0.054931 | 0.24719 | 122.3923 | 122.85 | 122.6669 | 122.7036 | 122.6532 | 122.731 | 122.7402 | 122.3923 | 122.7036 | 122.6532 | 122.7402 | 122.6669 | 122.731 | -0.27008 | -0.28381
2339.5469 | 122.85 | -122.5388 | 0.082397 | 0.0016785 | 0.015541 | 0.0092627 | 0.002493 | -0.0079704 | -0.0039157 | 0.0049283 | 0.027466 | 0.15106 | -0.21057 | 0.11902 | 0.045776 | 0.091553 | 0.018311 | 0.24719 | 0.19684 | -0.23346 | 122.3282 | 0.068665 | 122.5662 | 122.6578 | -0.036621 | 122.3053 | 0.11444 | 0.23804 | 122.5571 | 122.7859 | 122.5845 | 122.6898 | 122.5662 | 122.7356 | 122.6303 | 122.3053 | 122.6898 | 122.5662 | 122.6303 | 122.5845 | 122.7356 | -0.29297 | -0.31586
2341.2969 | 122.7448 | -122.5616 | 0.086975 | 0.0016785 | 0.015968 | 0.013108 | 0.0014248 | -0.007543 | -0.0032749 | 0.0040737 | 0.073242 | 0.11444 | -0.19226 | 0.1831 | 0.082397 | 0.16022 | -0.16022 | 0.28381 | 0.16479 | -0.20142 | 122.3694 | 0.027466 | 122.6349 | 122.7448 | -0.004578 | 122.3602 | 0.07782 | 0.2655 | 122.4014 | 122.8455 | 122.644 | 122.6761 | 122.6349 | 122.7264 | 122.7219 | 122.3602 | 122.6761 | 122.6349 | 122.7219 | 122.644 | 122.7264 | -0.27924 | -0.28839
2343.0469 | 122.7814 | -122.5571 | 0.1236 | -0.005951 | 0.016396 | 0.014176 | 0.0050564 | -0.0051932 | -0.0086155 | 0.0079189 | -0.032043 | 0.15106 | -0.22888 | 0.086975 | -0.009155 | 0.045776 | -0.004578 | 0.16022 | 0.19226 | -0.22888 | 122.3282 | 0.027466 | 122.525 | 122.644 | -0.13275 | 122.3282 | 0.068665 | 0.19684 | 122.5525 | 122.7173 | 122.5479 | 122.7081 | 122.525 | 122.7493 | 122.6028 | 122.3282 | 122.7081 | 122.525 | 122.6028 | 122.5479 | 122.7493 | -0.35248 | -0.35248
2344.7344 | 122.8455 | -122.5113 | 0.082397 | 0.009308 | 0.013618 | 0.010544 | -0.0013522 | -0.0054068 | -0.0056247 | 0.0051419 | 0.018311 | 0.13275 | -0.19684 | 0.15564 | 0.068665 | 0.14648 | -0.10529 | 0.28381 | 0.17395 | -0.19684 | 122.3145 | 0.050354 | 122.5296 | 122.6669 | -0.013732 | 122.3145 | 0.091553 | 0.21515 | 122.406 | 122.7951 | 122.58 | 122.644 | 122.5296 | 122.6852 | 122.6578 | 122.3145 | 122.644 | 122.5296 | 122.6578 | 122.58 | 122.6852 | -0.27924 | -0.27924
2346.5 | 122.7127 | -122.5891 | 0.11902 | -0.005951 | 0.016609 | 0.014603 | 0.0065518 | -0.008184 | -0.0058383 | 0.0055691 | 0.059509 | 0.15564 | -0.21973 | 0.16022 | 0.054932 | 0.10071 | -0.045776 | 0.25635 | 0.19684 | -0.19684 | 122.3694 | 0.036621 | 122.6486 | 122.7493 | -0.064087 | 122.3923 | 0.077819 | 0.27924 | 122.5433 | 122.8455 | 122.644 | 122.7448 | 122.6486 | 122.7859 | 122.6898 | 122.3923 | 122.7448 | 122.6486 | 122.6898 | 122.644 | 122.7859 | -0.33875 | -0.31586
2348.1719 | 122.7173 | -122.58 | 0.10529 | 0.009308 | 0.014046 | 0.014817 | 0.002493 | -0.005834 | -0.0049839 | 0.0087735 | 0.086975 | 0.12817 | -0.1831 | 0.20142 | 0.10529 | 0.17395 | -0.19226 | 0.30212 | 0.16937 | -0.17853 | 122.3969 | 0.022888 | 122.6669 | 122.7814 | 0 | 122.4014 | 0.064087 | 0.27008 | 122.3877 | 122.8821 | 122.6852 | 122.7081 | 122.6669 | 122.7493 | 122.7539 | 122.4014 | 122.7081 | 122.6669 | 122.7539 | 122.6852 | 122.7493 | -0.28839 | -0.28381
2349.9062 | 122.8592 | -122.5021 | 0.064087 | -0.005951 | 0.015114 | 0.0096899 | -0.0019932 | -0.0079704 | -0.0045565 | 0.0066373 | 0.009155 | 0.12817 | -0.18768 | 0.1236 | 0.064087 | 0.13733 | -0.10529 | 0.26093 | 0.18768 | -0.20599 | 122.3145 | 0.064087 | 122.5113 | 122.6257 | 0 | 122.2961 | 0.1236 | 0.19684 | 122.3968 | 122.7631 | 122.5662 | 122.6303 | 122.5113 | 122.6898 | 122.6395 | 122.2961 | 122.6303 | 122.5113 | 122.6395 | 122.5662 | 122.6898 | -0.25177 | -0.27008
2351.5938 | 122.818 | -122.525 | 0.082397 | -0.013581 | 0.013618 | 0.011185 | -0.012674 | -0.0079704 | -0.0045565 | 0.0049283 | 0.068665 | 0.1236 | -0.17395 | 0.20142 | 0.1236 | 0.18768 | -0.14191 | 0.32501 | 0.16479 | -0.17853 | 122.3511 | 0.041199 | 122.5937 | 122.7264 | 0.041199 | 122.3465 | 0.082398 | 0.24261 | 122.3831 | 122.85 | 122.6486 | 122.6486 | 122.5937 | 122.6898 | 122.7127 | 122.3465 | 122.6486 | 122.5937 | 122.7127 | 122.6486 | 122.6898 | -0.25635 | -0.26092
2353.3281 | 122.8592 | -122.5479 | 0.054932 | 0.0016785 | 0.016396 | 0.01204 | 0.0044156 | -0.007543 | -0.0058383 | 0.0053555 | -0.013733 | 0.16479 | -0.23804 | 0.10529 | 0.009155 | 0.054932 | 0.036621 | 0.21057 | 0.20599 | -0.24261 | 122.3099 | 0.10986 | 122.5342 | 122.6532 | -0.045777 | 122.3053 | 0.15106 | 0.2243 | 122.5845 | 122.7585 | 122.5571 | 122.7127 | 122.5342 | 122.7539 | 122.6028 | 122.3053 | 122.7127 | 122.5342 | 122.6028 | 122.5571 | 122.7539 | -0.29297 | -0.29755
2355.0625 | 122.7448 | -122.5616 | 0.11902 | -0.005951 | 0.015541 | 0.018235 | 0.0061246 | -0.0069022 | -0.0064791 | 0.0036465 | 0.027466 | 0.14648 | -0.21973 | 0.13275 | 0.036621 | 0.091553 | -0.032043 | 0.24719 | 0.18768 | -0.20599 | 122.3419 | 0.027465 | 122.5891 | 122.6944 | -0.082398 | 122.3557 | 0.068664 | 0.24719 | 122.5296 | 122.8088 | 122.5983 | 122.7081 | 122.5891 | 122.7493 | 122.6532 | 122.3557 | 122.7081 | 122.5891 | 122.6532 | 122.5983 | 122.7493 | -0.33875 | -0.32501
2356.8125 | 122.8271 | -122.5479 | 0.073242 | -0.02121 | 0.013618 | 0.012253 | -7.059e-05 | -0.0066886 | -0.0037021 | 0.0059963 | 0.027466 | 0.12817 | -0.19226 | 0.13733 | 0.054932 | 0.1236 | -0.10071 | 0.24261 | 0.16022 | -0.17853 | 122.3557 | 0.054932 | 122.5754 | 122.6852 | -0.01831 | 122.3694 | 0.086975 | 0.21973 | 122.4472 | 122.7905 | 122.6028 | 122.6761 | 122.5754 | 122.7081 | 122.6715 | 122.3694 | 122.6761 | 122.5754 | 122.6715 | 122.6028 | 122.7081 | -0.2655 | -0.25177
2358.5 | 122.8043 | -122.5433 | 0.09613 | 0.0016785 | 0.013832 | 0.010331 | -0.0013522 | -0.010534 | -0.0056247 | 0.0068509 | 0.091553 | 0.11902 | -0.16022 | 0.22888 | 0.14191 | 0.21057 | -0.17395 | 0.35248 | 0.16022 | -0.19684 | 122.3831 | 0.022889 | 122.6349 | 122.7722 | 0.045777 | 122.3465 | 0.064087 | 0.25177 | 122.3694 | 122.8958 | 122.6852 | 122.6624 | 122.6349 | 122.7036 | 122.7539 | 122.3465 | 122.6624 | 122.6349 | 122.7539 | 122.6852 | 122.7036 | -0.25635 | -0.29297
2360.25 | 122.7402 | -122.5571 | 0.11444 | -0.005951 | 0.013832 | 0.0077673 | 0.0029202 | -0.0079704 | -0.0047703 | 0.0066373 | 0.082397 | 0.10529 | -0.18768 | 0.1831 | 0.10529 | 0.1831 | -0.1831 | 0.30212 | 0.14648 | -0.16022 | 122.3694 | -0.009155 | 122.6395 | 122.7402 | -0.009155 | 122.3969 | 0.032043 | 0.27008 | 122.374 | 122.8592 | 122.6624 | 122.6624 | 122.6395 | 122.7036 | 122.7402 | 122.3969 | 122.6624 | 122.6395 | 122.7402 | 122.6624 | 122.7036 | -0.30212 | -0.27466
2362 | 122.7814 | -122.5525 | 0.10529 | -0.013581 | 0.016823 | 0.013108 | 0.0074062 | -0.005834 | -0.0062655 | 0.0064237 | 0 | 0.17395 | -0.23346 | 0.09613 | -0.009155 | 0.064087 | -0.027466 | 0.17853 | 0.20142 | -0.20599 | 122.319 | 0.068664 | 122.5525 | 122.6486 | -0.11444 | 122.3465 | 0.09613 | 0.23346 | 122.525 | 122.731 | 122.5433 | 122.7264 | 122.5525 | 122.7539 | 122.6166 | 122.3465 | 122.7264 | 122.5525 | 122.6166 | 122.5433 | 122.7539 | -0.33875 | -0.31128
2363.75 | 122.7356 | -122.5891 | 0.11444 | 0.0016785 | 0.014687 | 0.01204 | 0.0027066 | -0.0036978 | -0.0081881 | 0.0051419 | 0.027466 | 0.15106 | -0.20599 | 0.16937 | 0.059509 | 0.15106 | -0.15106 | 0.25177 | 0.15564 | -0.17853 | 122.3831 | 0.036621 | 122.6166 | 122.7585 | -0.054932 | 122.4106 | 0.041199 | 0.23346 | 122.438 | 122.8409 | 122.6486 | 122.7402 | 122.6166 | 122.7448 | 122.7402 | 122.4106 | 122.7402 | 122.6166 | 122.7402 | 122.6486 | 122.7448 | -0.32044 | -0.29297
2365.4219 | 122.8134 | -122.5342 | 0.086975 | -0.013581 | 0.016609 | 0.0086219 | 0.00014321 | -0.0077566 | -0.0028475 | 0.0066373 | 0.059509 | 0.11902 | -0.19684 | 0.19684 | 0.11902 | 0.20142 | -0.15106 | 0.33417 | 0.15106 | -0.19684 | 122.3373 | 0.032044 | 122.5937 | 122.731 | 0.032044 | 122.3373 | 0.064087 | 0.25635 | 122.3831 | 122.8683 | 122.6532 | 122.6532 | 122.5937 | 122.6852 | 122.7356 | 122.3373 | 122.6532 | 122.5937 | 122.7356 | 122.6532 | 122.6852 | -0.28381 | -0.28381
2367.1719 | 122.7402 | -122.5845 | 0.1236 | 0.0016785 | 0.015968 | 0.010117 | 0.0093288 | -0.0049796 | -0.0090427 | 0.0045011 | 0.054932 | 0.15564 | -0.2243 | 0.16022 | 0.050354 | 0.11444 | -0.059509 | 0.24261 | 0.21057 | -0.20142 | 122.3602 | 0.032044 | 122.6395 | 122.7448 | -0.073242 | 122.3831 | 0.086975 | 0.27924 | 122.525 | 122.8271 | 122.6349 | 122.7402 | 122.6395 | 122.7951 | 122.699 | 122.3831 | 122.7402 | 122.6395 | 122.699 | 122.6349 | 122.7951 | -0.3479 | -0.32501
2368.8594 | 122.8638 | -122.5616 | 0.09613 | 0.009308 | 0.017036 | 0.0086219 | 0.002493 | -0.0045524 | -0.0069065 | 0.0032193 | -0.009155 | 0.15106 | -0.25177 | 0.082397 | 0.009155 | 0.054932 | 0.032043 | 0.19684 | 0.21057 | -0.21515 | 122.3099 | 0.054932 | 122.5525 | 122.644 | -0.086975 | 122.3465 | 0.11444 | 0.24261 | 122.5937 | 122.7585 | 122.5708 | 122.7127 | 122.5525 | 122.7722 | 122.6166 | 122.3465 | 122.7127 | 122.5525 | 122.6166 | 122.5708 | 122.7722 | -0.3479 | -0.31128
2370.6094 | 122.731 | -122.5571 | 0.10529 | -0.013581 | 0.015968 | 0.014817 | 0.0029202 | -0.0034842 | -0.0064791 | 0.0059963 | 0.10986 | 0.11444 | -0.16022 | 0.21515 | 0.10071 | 0.18768 | -0.20599 | 0.3067 | 0.17853 | -0.16022 | 122.3969 | 0.009155 | 122.6669 | 122.7722 | -0.004578 | 122.3969 | 0.073242 | 0.27008 | 122.3511 | 122.8638 | 122.6578 | 122.6715 | 122.6669 | 122.7356 | 122.7448 | 122.3969 | 122.6715 | 122.6669 | 122.7448 | 122.6578 | 122.7356 | -0.2655 | -0.2655
2372.2969 | 122.7768 | -122.5708 | 0.11444 | 0.009308 | 0.014046 | 0.011399 | 0.0063382 | -0.0041252 | -0.0077609 | 0.0066373 | -0.018311 | 0.15564 | -0.21973 | 0.073242 | -0.032043 | 0.036621 | -0.022888 | 0.16937 | 0.21515 | -0.21057 | 122.3511 | 0.041199 | 122.5525 | 122.644 | -0.14648 | 122.3602 | 0.10071 | 0.20142 | 122.5479 | 122.7402 | 122.5388 | 122.7264 | 122.5525 | 122.7859 | 122.6074 | 122.3602 | 122.7264 | 122.5525 | 122.6074 | 122.5388 | 122.7859 | -0.33417 | -0.32501
2373.9688 | 122.7448 | -122.5845 | 0.1236 | 0.0016785 | 0.013191 | 0.0088355 | -0.0011386 | -0.0049796 | -0.0045565 | 0.0072781 | 0.091553 | 0.13733 | -0.17853 | 0.1831 | 0.09613 | 0.17853 | -0.17395 | 0.29297 | 0.16937 | -0.17853 | 122.406 | 0.013733 | 122.6761 | 122.7676 | -0.027466 | 122.406 | 0.045777 | 0.27008 | 122.4106 | 122.8775 | 122.6807 | 122.7219 | 122.6761 | 122.7539 | 122.7631 | 122.406 | 122.7219 | 122.6761 | 122.7631 | 122.6807 | 122.7539 | -0.30212 | -0.30212
2375.6562 | 122.8683 | -122.5342 | 0.082397 | 0.0016785 | 0.014046 | 0.011185 | -0.0022068 | -0.0079704 | -0.0030613 | 0.0066373 | 0.027466 | 0.12817 | -0.19226 | 0.15564 | 0.073242 | 0.15106 | -0.10986 | 0.28839 | 0.17853 | -0.19684 | 122.3419 | 0.045777 | 122.5616 | 122.6898 | -0.009155 | 122.3373 | 0.096131 | 0.21973 | 122.4243 | 122.8226 | 122.6074 | 122.6624 | 122.5616 | 122.7127 | 122.6852 | 122.3373 | 122.6624 | 122.5616 | 122.6852 | 122.6074 | 122.7127 | -0.27466 | -0.27924
2377.3906 | 122.8546 | -122.5433 | 0.091553 | -0.005951 | 0.015541 | 0.0049903 | 0.0048428 | -0.0077566 | -0.0073337 | 0.0038601 | -0.022888 | 0.17395 | -0.24261 | 0.091553 | 0.009155 | 0.064087 | 0.032043 | 0.21057 | 0.20599 | -0.21973 | 122.3007 | 0.082397 | 122.5204 | 122.6349 | -0.082398 | 122.3236 | 0.11444 | 0.21973 | 122.5754 | 122.7539 | 122.5525 | 122.7173 | 122.5204 | 122.7493 | 122.6074 | 122.3236 | 122.7173 | 122.5204 | 122.6074 | 122.5525 | 122.7493 | -0.33417 | -0.31128
2379.0781 | 122.7219 | -122.5845 | 0.1236 | 0.0016785 | 0.017036 | 0.013535 | 0.0027066 | -0.0036978 | -0.0056247 | 0.0066373 | 0.10529 | 0.12817 | -0.18768 | 0.21515 | 0.10529 | 0.19684 | -0.20599 | 0.30212 | 0.16937 | -0.17395 | 122.3969 | 0.004578 | 122.6898 | 122.7997 | -0.01831 | 122.4106 | 0.045777 | 0.29297 | 122.3785 | 122.8867 | 122.6898 | 122.7127 | 122.6898 | 122.7539 | 122.7814 | 122.4106 | 122.7127 | 122.6898 | 122.7814 | 122.6898 | 122.7539 | -0.31128 | -0.29755
2380.8281 | 122.8271 | -122.5616 | 0.07782 | -0.005951 | 0.016182 | 0.0071265 | -0.0017794 | -0.0054068 | -0.0051975 | 0.0057827 | 0.082397 | 0.11444 | -0.16937 | 0.21057 | 0.13275 | 0.1831 | -0.14191 | 0.33875 | 0.16937 | -0.16937 | 122.3923 | 0.036621 | 122.644 | 122.7722 | 0.054931 | 122.3923 | 0.091553 | 0.25177 | 122.4197 | 122.9004 | 122.6944 | 122.6761 | 122.644 | 122.731 | 122.7448 | 122.3923 | 122.6761 | 122.644 | 122.7448 | 122.6944 | 122.731 | -0.24719 | -0.24719
2382.5781 | 122.7493 | -122.58 | 0.13275 | -0.005951 | 0.016182 | 0.0099037 | 0.0063382 | -0.004766 | -0.0081881 | 0.0057827 | 0.036621 | 0.14648 | -0.21515 | 0.16022 | 0.050354 | 0.10986 | -0.036621 | 0.24719 | 0.21057 | -0.20142 | 122.3648 | 0.013733 | 122.6166 | 122.7402 | -0.082397 | 122.3785 | 0.07782 | 0.25177 | 122.5433 | 122.8271 | 122.6303 | 122.7264 | 122.6166 | 122.7905 | 122.6898 | 122.3785 | 122.7264 | 122.6166 | 122.6898 | 122.6303 | 122.7905 | -0.3479 | -0.33417
2384.3281 | 122.8683 | -122.5433 | 0.086975 | 0.0016785 | 0.015327 | 0.01204 | -0.0030612 | -0.0069022 | -0.0054111 | 0.0045011 | 0.032043 | 0.1236 | -0.19226 | 0.14648 | 0.054932 | 0.12817 | -0.10529 | 0.26093 | 0.17853 | -0.18768 | 122.3511 | 0.036621 | 122.5754 | 122.6898 | -0.032043 | 122.3557 | 0.091553 | 0.2243 | 122.438 | 122.8043 | 122.5983 | 122.6669 | 122.5754 | 122.7219 | 122.6715 | 122.3557 | 122.6669 | 122.5754 | 122.6715 | 122.5983 | 122.7219 | -0.27924 | -0.27466
2386.0781 | 122.8134 | -122.5845 | 0.09613 | 0.009308 | 0.01725 | 0.011185 | 0.0046292 | -0.0045524 | -0.0071201 | 0.0059963 | 0.009155 | 0.16022 | -0.21057 | 0.14191 | 0.036621 | 0.086975 | -0.004578 | 0.23804 | 0.21515 | -0.20599 | 122.374 | 0.064087 | 122.5937 | 122.7264 | -0.059509 | 122.3785 | 0.11902 | 0.21973 | 122.58 | 122.8226 | 122.6212 | 122.7448 | 122.5937 | 122.7997 | 122.6715 | 122.3785 | 122.7448 | 122.5937 | 122.6715 | 122.6212 | 122.7997 | -0.3067 | -0.30212
2387.8125 | 122.7402 | -122.6074 | 0.11902 | -0.005951 | 0.015327 | 0.010972 | 0.0039884 | -0.005834 | -0.0092563 | 0.0047147 | 0.022888 | 0.14191 | -0.22888 | 0.12817 | 0.027466 | 0.091553 | -0.032043 | 0.21057 | 0.19226 | -0.21057 | 122.3785 | 0.022888 | 122.6303 | 122.7356 | -0.091553 | 122.3969 | 0.073242 | 0.25177 | 122.5754 | 122.818 | 122.6349 | 122.7493 | 122.6303 | 122.7997 | 122.699 | 122.3969 | 122.7493 | 122.6303 | 122.699 | 122.6349 | 122.7997 | -0.3479 | -0.32959
2389.4844 | 122.7448 | -122.5937 | 0.091553 | -0.005951 | 0.016182 | 0.012253 | -0.0019932 | -0.0039114 | -0.0054111 | 0.0077053 | 0.07782 | 0.11444 | -0.17853 | 0.17853 | 0.086975 | 0.16937 | -0.19226 | 0.29755 | 0.15106 | -0.17395 | 122.4152 | 0.022888 | 122.6715 | 122.7722 | -0.004578 | 122.4197 | 0.059509 | 0.25635 | 122.4014 | 122.8912 | 122.6807 | 122.7081 | 122.6715 | 122.7448 | 122.7631 | 122.4197 | 122.7081 | 122.6715 | 122.7631 | 122.6807 | 122.7448 | -0.27008 | -0.2655
2391.2344 | 122.8683 | -122.5388 | 0.086975 | 0.0016785 | 0.013191 | 0.0075537 | -0.0024204 | -0.0062614 | -0.0037021 | 0.0059963 | 0.013733 | 0.11444 | -0.19226 | 0.13733 | 0.059509 | 0.13733 | -0.11902 | 0.25635 | 0.17395 | -0.18768 | 122.3465 | 0.027466 | 122.5525 | 122.6761 | -0.027466 | 122.3511 | 0.086975 | 0.20599 | 122.4197 | 122.7951 | 122.5983 | 122.6532 | 122.5525 | 122.7127 | 122.6761 | 122.3511 | 122.6532 | 122.5525 | 122.6761 | 122.5983 | 122.7127 | -0.27924 | -0.27466
2392.9219 | 122.7356 | -122.5845 | 0.11444 | -0.005951 | 0.0149 | 0.013535 | 0.00035681 | -0.0060478 | -0.0062655 | 0.0030057 | 0.10529 | 0.10986 | -0.1831 | 0.20142 | 0.09613 | 0.1831 | -0.18768 | 0.29755 | 0.15564 | -0.17853 | 122.4014 | -0.004578 | 122.6898 | 122.7859 | -0.018311 | 122.406 | 0.041199 | 0.28839 | 122.3969 | 122.8821 | 122.6807 | 122.6944 | 122.6898 | 122.7402 | 122.7676 | 122.406 | 122.6944 | 122.6898 | 122.7676 | 122.6807 | 122.7402 | -0.29755 | -0.29297
2394.6719 | 122.8821 | -122.5525 | 0.086975 | -0.005951 | 0.015968 | 0.0099037 | 0.0027066 | -0.0069022 | -0.0043429 | 0.0059963 | -0.036621 | 0.16937 | -0.21973 | 0.10986 | -0.009155 | 0.054932 | 0.059509 | 0.19684 | 0.20142 | -0.2243 | 122.3328 | 0.082398 | 122.5159 | 122.6624 | -0.09613 | 122.3282 | 0.11444 | 0.18311 | 122.612 | 122.7493 | 122.5433 | 122.7219 | 122.5159 | 122.7539 | 122.6074 | 122.3282 | 122.7219 | 122.5159 | 122.6074 | 122.5433 | 122.7539 | -0.3067 | -0.31128
2396.4375 | 122.8729 | -122.5571 | 0.07782 | 0.009308 | 0.014259 | 0.0075537 | -0.0041294 | -0.005834 | -0.0058383 | 0.0055691 | 0.045776 | 0.13275 | -0.19684 | 0.16937 | 0.09613 | 0.16022 | -0.10529 | 0.31128 | 0.16937 | -0.19226 | 122.3602 | 0.054931 | 122.6028 | 122.7264 | 0.01831 | 122.3648 | 0.091553 | 0.24261 | 122.4518 | 122.8683 | 122.6532 | 122.6898 | 122.6028 | 122.7264 | 122.7173 | 122.3648 | 122.6898 | 122.6028 | 122.7173 | 122.6532 | 122.7264 | -0.27466 | -0.27008
2398.1094 | 122.8729 | -122.5479 | 0.11444 | -0.005951 | 0.016609 | 0.013535 | 0.0020658 | -0.0083976 | -0.0062655 | 0.0070645 | 0.022888 | 0.14648 | -0.20599 | 0.1236 | 0.045776 | 0.068665 | 0.018311 | 0.23346 | 0.18768 | -0.22888 | 122.3419 | 0.032043 | 122.5708 | 122.6715 | -0.068665 | 122.319 | 0.073242 | 0.22888 | 122.5662 | 122.7814 | 122.5937 | 122.6944 | 122.5708 | 122.7356 | 122.6166 | 122.319 | 122.6944 | 122.5708 | 122.6166 | 122.5937 | 122.7356 | -0.32044 | -0.34332
2399.8594 | 122.8958 | -122.5479 | 0.073242 | 0.0016785 | 0.014473 | 0.0090491 | 0.002493 | -0.0066886 | -0.0056247 | 0.0049283 | -0.027466 | 0.17395 | -0.25177 | 0.10071 | -0.004578 | 0.027466 | 0.054932 | 0.19684 | 0.21515 | -0.23346 | 122.2961 | 0.10071 | 122.5204 | 122.6486 | -0.07782 | 122.3145 | 0.14191 | 0.2243 | 122.6028 | 122.7448 | 122.5433 | 122.7219 | 122.5204 | 122.7631 | 122.5754 | 122.3145 | 122.7219 | 122.5204 | 122.5754 | 122.5433 | 122.7631 | -0.32501 | -0.3067
2401.5625 | 122.8317 | -122.5754 | 0.07782 | 0.0016785 | 0.013832 | 0.0099037 | -0.0037022 | -0.0062614 | -0.0051975 | 0.0047147 | 0.10529 | 0.10986 | -0.1831 | 0.22888 | 0.12817 | 0.20142 | -0.15564 | 0.3479 | 0.16479 | -0.16937 | 122.3923 | 0.032043 | 122.6807 | 122.8043 | 0.050354 | 122.406 | 0.086975 | 0.28839 | 122.4197 | 122.9233 | 122.7036 | 122.6852 | 122.6807 | 122.7402 | 122.7768 | 122.406 | 122.6852 | 122.6807 | 122.7768 | 122.7036 | 122.7402 | -0.26092 | -0.24719

## Thermal Data
Fire Time | D Position - 3' | D Position - Middle | D Position - 7'
-0.6521 | 8.7226 | 8.9391 | 9.1304
0.3479 | 8.7223 | 8.9368 | 9.1227
1.3479 | 8.7281 | 8.9402 | 9.1225
2.3479 | 8.7265 | 8.9472 | 9.1288
3.3479 | 8.7247 | 8.9364 | 9.1283
4.3479 | 8.7228 | 8.9467 | 9.1309
5.3479 | 8.7287 | 8.9466 | 9.1313
6.3479 | 8.7159 | 8.9431 | 9.1419
7.3479 | 8.7214 | 8.9591 | 9.1373
8.3479 | 8.7182 | 8.9509 | 9.1418
9.3479 | 8.735 | 9.0033 | 9.138
10.3479 | 8.8056 | 9.3678 | 9.1769
11.3479 | 8.8167 | 10.1256 | 9.1933
12.3479 | 8.8896 | 10.7955 | 9.4277
13.3479 | 9.6256 | 12.2755 | 10.0204
14.3479 | 11.1179 | 14.9358 | 11.1338
15.3479 | 12.9705 | 17.6633 | 11.6566
16.3479 | 15.9452 | 21.4652 | 12.4693
17.3479 | 18.7013 | 25.8345 | 13.6754
18.3479 | 21.3915 | 31.1198 | 15.2184
19.3479 | 24.7169 | 35.6621 | 16.4091
20.3479 | 28.602 | 40.2139 | 17.8927
21.3479 | 31.4608 | 45.3636 | 19.4871
22.3479 | 35.3153 | 49.8693 | 22.5897
23.3479 | 37.9095 | 56.8248 | 24.9875
24.3479 | 41.1215 | 61.1181 | 26.654
25.3479 | 44.0889 | 66.0871 | 29.465
26.3479 | 46.4959 | 71.7811 | 32.0977
27.3479 | 49.1573 | 76.2848 | 33.87
28.3635 | 52.1088 | 82.1126 | 37.683
29.3479 | 54.9021 | 85.1065 | 40.2315
30.3479 | 57.981 | 88.7704 | 42.9183
31.3479 | 61.249 | 93.6723 | 46.0203
32.3479 | 63.3538 | 98.0333 | 50.5142
33.3479 | 67.0195 | 101.7869 | 53.9619
34.3479 | 69.0416 | 107.0979 | 56.6008
35.3479 | 73.0635 | 111.9718 | 58.8709
36.3479 | 76.4136 | 114.3823 | 61.9838
37.3479 | 80.1321 | 116.4689 | 65.016
38.3479 | 81.6728 | 119.7646 | 67.8479
39.3479 | 83.1728 | 122.2224 | 70.5556
40.3479 | 84.9189 | 124.8157 | 72.3135
41.3479 | 87.1484 | 127.2985 | 74.4399
42.3479 | 89.1051 | 129.3108 | 77.238
43.3479 | 92.7118 | 130.6121 | 80.5044
44.3479 | 94.6574 | 132.1059 | 82.9248
45.3479 | 96.2465 | 132.8888 | 85.3105
46.3479 | 98.0403 | 134.1165 | 88.8757
47.3479 | 98.6193 | 136.5777 | 90.9358
48.3479 | 99.8119 | 137.6981 | 93.1927
49.3479 | 100.6305 | 139.7043 | 96.2432
50.3479 | 101.8538 | 142.2219 | 98.6324
51.3479 | 103.4459 | 143.2724 | 100.2478
52.3479 | 103.9747 | 144.5491 | 102.7187
53.3479 | 104.9835 | 146.3396 | 105.1657
54.3479 | 105.6452 | 147.5398 | 106.5805
55.3635 | 105.9526 | 148.5046 | 108.0742
56.3479 | 107.6457 | 149.6477 | 109.4381
57.3479 | 109.3352 | 151.7362 | 110.5242
58.3479 | 111.1894 | 153.8676 | 112.3351
59.3479 | 113.7384 | 154.6317 | 114.4619
60.3479 | 116.6468 | 155.6816 | 115.7475
61.3479 | 119.8053 | 156.9683 | 117.1797
62.3479 | 121.425 | 158.4194 | 119.4354
63.3479 | 123.6866 | 159.8112 | 120.7854
64.3479 | 126.3207 | 160.8386 | 122.7156
65.3479 | 128.9539 | 162.2039 | 123.9187
66.3479 | 130.0008 | 163.4423 | 125.4131
67.3479 | 131.0526 | 164.456 | 126.355
68.3479 | 131.83 | 164.469 | 127.2466
69.3479 | 133.4563 | 164.8365 | 128.1043
70.3479 | 134.4525 | 166.0062 | 129.1022
71.3479 | 134.616 | 167.494 | 130.1829
72.3479 | 134.559 | 167.8232 | 131.5561
73.3479 | 134.3585 | 166.8863 | 131.8026
74.3479 | 134.3843 | 167.2491 | 132.3367
75.3479 | 134.663 | 167.967 | 132.4935
76.3479 | 135.1286 | 167.9419 | 132.9796
77.3479 | 135.2904 | 167.1524 | 133.7348
78.3479 | 136.2712 | 167.389 | 134.7921
79.3479 | 136.4738 | 168.1451 | 135.7726
80.3479 | 136.8341 | 168.4328 | 136.7967
81.3479 | 136.7278 | 168.7336 | 137.7923
82.3479 | 136.8249 | 168.5174 | 138.1884
83.3479 | 136.5669 | 168.6751 | 138.9324
84.3479 | 137.1731 | 169.6073 | 140.1688
85.3479 | 137.5295 | 168.7527 | 140.493
86.3479 | 137.445 | 167.8261 | 141.2247
87.3479 | 137.5194 | 166.8316 | 141.9395
88.3479 | 137.8127 | 165.723 | 141.8682
89.3479 | 138.0481 | 165.3183 | 142.8423
90.3479 | 139.1142 | 166.0071 | 143.2404
91.3479 | 139.6624 | 166.1055 | 143.6051
92.3479 | 140.0061 | 166.4634 | 145.5674
93.3479 | 139.7809 | 167.6406 | 145.9994
94.3479 | 139.7144 | 167.0327 | 147.6564
95.3479 | 139.6099 | 166.2426 | 148.4702
96.3479 | 139.3024 | 165.716 | 148.9304
97.3479 | 139.4059 | 165.6803 | 149.8226
98.3479 | 139.5043 | 166.2373 | 150.6795
99.3479 | 139.3313 | 166.4777 | 152.051
100.3479 | 139.0033 | 166.196 | 153.0321
101.3479 | 138.8393 | 166.0558 | 153.8671
102.3479 | 138.6934 | 166.859 | 155.2063
103.3479 | 138.9057 | 167.7154 | 156.3842
104.3479 | 139.1839 | 167.5743 | 157.1762
105.3479 | 139.0078 | 168.5746 | 157.7732
106.3479 | 140.0965 | 169.3239 | 158.7353
107.3479 | 140.3515 | 170.3351 | 160.3964
108.3479 | 140.8524 | 171.3593 | 160.9092
109.3479 | 141.2878 | 172.4878 | 161.1332
110.3479 | 141.5629 | 174.1133 | 161.5756
111.3479 | 141.4854 | 175.1104 | 161.5117
112.3479 | 141.9609 | 175.8999 | 162.2069
113.3479 | 141.5767 | 176.1124 | 162.4563
114.3479 | 141.9451 | 177.1473 | 162.7495
115.3479 | 143.798 | 179.8261 | 163.6402
116.3479 | 144.5353 | 181.7759 | 164.0637
117.3479 | 146.4075 | 182.8628 | 165.1952
118.3479 | 146.2616 | 183.8242 | 165.3308
119.3479 | 146.6573 | 184.0302 | 165.8568
120.3479 | 148.163 | 184.9292 | 166.5644
121.3479 | 149.0475 | 186.2124 | 167.278
122.3479 | 149.878 | 186.7774 | 167.7688
123.3479 | 150.2125 | 187.0667 | 168.8107
124.3479 | 150.5083 | 187.5204 | 169.0978
125.3479 | 150.5193 | 187.16 | 169.8762
126.3479 | 151.1727 | 188.4868 | 170.2154
127.3479 | 150.8693 | 187.7761 | 171.1633
128.3479 | 151.1251 | 188.5501 | 170.5116
129.3479 | 151.4198 | 187.1017 | 172.343
130.3479 | 151.5345 | 186.8438 | 174.0333
131.3479 | 151.7222 | 187.2208 | 175.7962
132.3479 | 151.6481 | 187.8773 | 177.0193
133.3479 | 151.9734 | 188.4942 | 177.9299
134.3479 | 151.9671 | 188.2603 | 178.1149
135.3479 | 152.5876 | 189.705 | 178.6601
136.3479 | 152.6716 | 191.1539 | 179.3745
137.3479 | 153.5089 | 191.9667 | 179.6908
138.3479 | 153.5178 | 192.9221 | 181.7078
139.3479 | 153.2328 | 192.5441 | 182.1631
140.3479 | 152.7173 | 193.3484 | 183.2284
141.3479 | 152.5808 | 194.9709 | 184.4299
142.3479 | 152.2404 | 193.9012 | 183.6215
143.3479 | 151.8782 | 193.8503 | 183.5916
144.3479 | 151.4596 | 193.399 | 183.2769
145.3479 | 151.7598 | 194.3163 | 183.0771
146.3479 | 152.0663 | 196.4921 | 182.7023
147.3479 | 153.61 | 197.7916 | 182.4215
148.3479 | 154.4318 | 198.978 | 182.9248
149.3479 | 154.693 | 199.0486 | 182.4632
150.3479 | 155.309 | 198.9485 | 182.9571
151.3479 | 155.7713 | 199.7988 | 182.8983
152.3479 | 156.2359 | 201.4818 | 184.3492
153.3479 | 157.0189 | 202.5758 | 185.0311
154.3479 | 157.1672 | 202.4136 | 186.1167
155.3479 | 156.9276 | 202.3295 | 186.2659
156.3479 | 156.7651 | 201.8391 | 187.4606
157.3479 | 156.5073 | 201.1097 | 189.2217
158.3479 | 156.1803 | 200.4409 | 190.2869
159.3479 | 156.8026 | 201.024 | 190.9673
160.3479 | 157.4391 | 201.8369 | 192.4305
161.3479 | 157.8387 | 202.2779 | 191.7081
162.3479 | 157.5158 | 202.3421 | 192.6645
163.3479 | 157.1784 | 202.3877 | 192.1069
164.3479 | 157.4975 | 201.6871 | 193.4614
165.3479 | 158.1076 | 201.5318 | 194.253
166.3479 | 158.1016 | 200.8388 | 195.5481
167.3479 | 158.2218 | 200.5867 | 195.1583
168.3479 | 157.8369 | 200.0011 | 195.4199
169.3479 | 157.677 | 200.173 | 195.2936
170.3479 | 157.7509 | 199.5164 | 194.767
171.3479 | 157.8244 | 199.3896 | 194.8959
172.3479 | 158.2402 | 199.2665 | 194.8901
173.3479 | 157.9671 | 199.9392 | 195.2387
174.3479 | 157.8977 | 200.9832 | 194.7116
175.3479 | 157.8065 | 200.6448 | 193.6457
176.3479 | 157.4012 | 200.8381 | 192.5413
177.3479 | 157.2119 | 201.1702 | 192.8206
178.3479 | 157.5819 | 202.3467 | 192.8496
179.3479 | 157.4408 | 201.5243 | 193.0459
180.3479 | 157.2109 | 201.803 | 192.9411
181.3479 | 156.9567 | 202.2049 | 194.4982
182.3479 | 157.2417 | 201.7919 | 194.8077
183.3479 | 157.0645 | 202.222 | 194.3431
184.3479 | 157.658 | 202.3878 | 193.8114
185.3479 | 158.0952 | 203.9823 | 193.5983
186.3479 | 158.4589 | 205.5938 | 193.6313
187.3479 | 159.1133 | 206.5751 | 194.2403
188.3479 | 159.793 | 207.7249 | 194.3761
189.3479 | 160.2997 | 207.6643 | 195.1094
190.3479 | 161.204 | 207.4329 | 196.4245
191.3479 | 162.008 | 207.3296 | 197.5991
192.3479 | 162.5836 | 208.1516 | 197.5586
193.3479 | 163.5961 | 209.2692 | 197.2522
194.3479 | 163.9007 | 210.5903 | 196.8699
195.3479 | 165.486 | 213.8387 | 197.0144
196.3479 | 166.6153 | 214.8957 | 196.8865
197.3479 | 167.0404 | 213.9312 | 197.4273
198.3479 | 167.9166 | 213.7337 | 198.0883
199.3479 | 168.7263 | 214.1414 | 198.5532
200.3479 | 169.2348 | 213.5065 | 198.8787
201.3479 | 168.8678 | 212.3324 | 200.1974
202.3479 | 168.3566 | 213.2903 | 200.6144
203.3479 | 168.5906 | 212.0504 | 201.6042
204.3479 | 169.0434 | 212.8292 | 202.5589
205.3479 | 169.4412 | 213.7125 | 202.9676
206.3479 | 169.3467 | 213.7142 | 203.4314
207.3479 | 169.217 | 214.2501 | 203.5344
208.3479 | 169.8121 | 214.0582 | 203.8521
209.3479 | 170.6716 | 214.3099 | 204.7941
210.3479 | 170.8915 | 215.0883 | 205.7181
211.3479 | 171.3537 | 215.3895 | 206.1766
212.3479 | 171.9282 | 215.4358 | 206.3801
213.3479 | 171.6605 | 215.9165 | 206.1135
214.3479 | 171.7992 | 216.1702 | 205.5547
215.3479 | 172.8746 | 216.5805 | 205.9219
216.3479 | 172.79 | 217.1683 | 206.5572
217.3479 | 173.3431 | 217.3126 | 206.1234
218.3479 | 173.5486 | 217.5292 | 207.4268
219.3479 | 173.9384 | 217.7448 | 207.6269
220.3479 | 173.5075 | 216.5876 | 209.0169
221.3479 | 173.2056 | 217.0029 | 211.6851
222.3479 | 173.1771 | 218.0622 | 212.2486
223.3479 | 173.1161 | 217.8468 | 213.6861
224.3479 | 173.1047 | 218.0953 | 213.6053
225.3479 | 174.0247 | 219.1606 | 213.6734
226.3479 | 174.5317 | 219.0059 | 214.203
227.3479 | 175.1198 | 221.0144 | 214.081
228.3479 | 175.3542 | 221.5289 | 213.7005
229.3479 | 176.3786 | 222.6032 | 214.4489
230.3479 | 177.1959 | 222.8491 | 215.4508
231.3479 | 176.5632 | 225.3559 | 215.9041
232.3479 | 176.7223 | 226.2728 | 216.9702
233.3479 | 177.8801 | 227.8729 | 217.8766
234.3479 | 178.355 | 229.7113 | 219.6432
235.3479 | 179.1173 | 230.2028 | 220.177
236.3479 | 179.6454 | 230.9997 | 220.9313
237.3479 | 179.9763 | 231.5552 | 221.908
238.3479 | 180.2733 | 232.3659 | 222.9476
239.3479 | 180.3464 | 232.6439 | 224.1592
240.3479 | 180.0727 | 232.922 | 225.3354
241.3479 | 179.9788 | 233.0249 | 227.5
242.3479 | 179.8192 | 233.3825 | 228.5113
243.3479 | 180.4116 | 233.7147 | 227.7509
244.3479 | 181.4143 | 234.3488 | 228.7649
245.3479 | 181.5636 | 234.3473 | 229.6005
246.3479 | 182.2246 | 235.1323 | 229.7394
247.3479 | 182.1019 | 235.5228 | 230.8644
248.3479 | 182.1929 | 235.9406 | 230.438
249.3479 | 182.478 | 237.4305 | 232.8633
250.3479 | 182.9965 | 237.4693 | 232.5117
251.3479 | 183.0463 | 238.2579 | 232.4721
252.3479 | 184.0332 | 238.9521 | 233.336
253.3479 | 184.2128 | 238.8229 | 236.2831
254.3479 | 183.6466 | 238.9683 | 236.7215
255.3479 | 184.2251 | 238.3597 | 236.2334
256.3479 | 184.4452 | 238.5434 | 237.6316
257.3479 | 185.5941 | 238.6304 | 238.1686
258.3479 | 185.6576 | 238.9278 | 238.583
259.3479 | 186.4817 | 239.5676 | 239.1586
260.3479 | 186.2003 | 240.8805 | 239.1029
261.3479 | 186.4425 | 241.9298 | 241.3513
262.3479 | 188.6556 | 244.3272 | 241.8022
263.3479 | 188.8781 | 244.6204 | 241.8732
264.3479 | 189.9312 | 245.0933 | 242.6932
265.3479 | 190.2767 | 245.3448 | 242.9005
266.3479 | 191.8988 | 246.438 | 245.5208
267.3479 | 191.7219 | 246.2611 | 245.4339
268.3479 | 191.8446 | 246.2735 | 245.1372
269.3479 | 191.8289 | 246.8294 | 245.7139
270.3479 | 191.5156 | 248.2588 | 246.2554
271.3479 | 195.0934 | 248.8436 | 239.7669
272.3479 | 191.8783 | 247.8768 | 246.9871
273.3479 | 192.9537 | 248.4937 | 247.0124
274.3479 | 193.2411 | 250.1631 | 246.6604
275.3479 | 193.7448 | 250.1362 | 247.4756
276.3479 | 193.904 | 251.1123 | 247.9281
277.3479 | 194.1254 | 251.4556 | 248.0009
278.3479 | 193.6602 | 250.564 | 249.3495
279.3479 | 193.3885 | 250.0825 | 248.6639
280.3479 | 193.2679 | 251.8791 | 248.8151
281.3479 | 193.4572 | 252.6952 | 248.5123
282.3479 | 195.0215 | 253.9792 | 247.9477
283.3479 | 195.3265 | 254.4307 | 247.349
284.3479 | 195.2522 | 253.9764 | 247.3789
285.3479 | 195.2039 | 253.9151 | 247.0866
286.3479 | 195.8042 | 254.9207 | 246.0614
287.3479 | 196.3916 | 256.4481 | 245.6099
288.3479 | 197.0881 | 257.7852 | 245.6943
289.3479 | 197.5294 | 259.4495 | 245.4802
290.3479 | 199.3611 | 262.7592 | 246.104
291.3479 | 200.3141 | 264.1192 | 246.5766
292.3479 | 200.2901 | 263.5014 | 247.4392
293.3479 | 200.2958 | 262.8304 | 248.1738
294.3479 | 199.9473 | 262.4232 | 249.3043
295.3479 | 199.6608 | 262.3886 | 248.9798
296.3479 | 200.4255 | 263.2605 | 249.1293
297.3479 | 202.5962 | 264.1339 | 250.1522
298.3479 | 203.0444 | 265.3614 | 250.6728
299.3479 | 203.5302 | 265.7898 | 252.0311
300.3479 | 203.3695 | 264.9433 | 253.7833
301.3479 | 203.3753 | 265.4226 | 254.2368
302.3479 | 203.7057 | 264.2363 | 255.3294
303.3479 | 203.6162 | 264.0876 | 255.0803
304.3479 | 204.4587 | 265.9639 | 255.1046
305.3479 | 205.597 | 267.9737 | 255.4617
306.3479 | 206.6869 | 268.4945 | 256.3787
307.3479 | 206.937 | 269.1598 | 256.8192
308.3479 | 206.7863 | 269.2264 | 257.6421
309.3479 | 206.99 | 268.7643 | 258.4871
310.3479 | 208.2942 | 268.5789 | 259.6565
311.3479 | 208.551 | 269.2956 | 260.3193
312.3479 | 209.1747 | 270.142 | 262.0873
313.3479 | 210.0268 | 270.4454 | 262.5127
314.3479 | 210.9794 | 270.6517 | 263.2197
315.3479 | 211.4042 | 270.3683 | 263.9209
316.3479 | 211.4204 | 272.5238 | 265.0239
317.3479 | 212.5303 | 273.5319 | 265.8442
318.3479 | 213.4981 | 274.5919 | 265.3723
319.3479 | 213.4509 | 274.7559 | 265.5697
320.3479 | 213.9068 | 276.2546 | 265.1246
321.3479 | 215.1961 | 277.2086 | 264.4626
322.3479 | 216.288 | 278.7781 | 264.6939
323.3479 | 218.017 | 281.122 | 265.0814
324.3479 | 218.3343 | 283.6002 | 265.4953
325.3479 | 219.0909 | 284.8217 | 267.0139
326.3479 | 220.6773 | 288.0042 | 267.8117
327.3479 | 221.3824 | 289.5353 | 267.81
328.3479 | 223.1208 | 291.0963 | 268.1381
329.3479 | 223.4596 | 291.7298 | 268.4054
330.3479 | 223.072 | 292.3004 | 267.9247
331.3479 | 223.4117 | 292.3792 | 268.3895
332.3479 | 224.0186 | 291.5656 | 269.4739
333.3479 | 224.9044 | 292.0478 | 269.0004
334.3479 | 224.4392 | 291.3454 | 270.2657
335.3479 | 224.7078 | 290.5231 | 271.0717
336.3479 | 224.6245 | 291.4331 | 271.4822
337.3479 | 224.265 | 292.4939 | 271.8048
338.3479 | 224.741 | 293.5505 | 272.6659
339.3479 | 224.2409 | 293.5632 | 273.2346
340.3479 | 224.4143 | 294.8739 | 273.3445
341.3479 | 224.4008 | 294.8986 | 273.7469
342.3479 | 224.2486 | 295.1423 | 273.6973
343.3479 | 223.6009 | 295.1331 | 272.6058
344.3479 | 223.7557 | 293.7843 | 272.1199
345.3479 | 223.7676 | 293.782 | 271.1602
346.3479 | 224.2634 | 293.6383 | 270.6293
347.3479 | 224.7482 | 295.446 | 271.4041
348.3479 | 225.5847 | 296.4158 | 272.9905
349.3479 | 226.8816 | 296.084 | 273.5397
350.3479 | 228.0931 | 299.1888 | 274.0245
351.3479 | 228.6909 | 299.4883 | 275.565
352.3479 | 228.8475 | 298.6738 | 275.641
353.3479 | 228.999 | 299.3672 | 275.1038
354.3479 | 228.959 | 298.6113 | 275.7084
355.3479 | 228.7639 | 299.2111 | 276.7082
356.3479 | 228.7905 | 299.7171 | 278.3401
357.3479 | 228.4732 | 299.8469 | 280.7942
358.3479 | 229.0606 | 301.0253 | 282.4579
359.3479 | 229.6131 | 299.8325 | 282.3141
360.3479 | 229.3317 | 299.7123 | 281.8736
361.3479 | 230.0516 | 300.8124 | 281.1263
362.3479 | 231.089 | 301.5987 | 280.9972
363.3479 | 231.5637 | 302.9818 | 280.8344
364.3479 | 232.7666 | 304.0607 | 280.8587
365.3479 | 232.3296 | 305.1453 | 281.3943
366.3479 | 233.3042 | 306.4291 | 281.2272
367.3479 | 233.7261 | 306.941 | 280.7077
368.3479 | 235.3877 | 307.5972 | 281.9134
369.3479 | 235.901 | 308.4597 | 282.1476
370.3479 | 236.9514 | 308.1669 | 282.2372
371.3479 | 237.3945 | 308.3383 | 281.4344
372.3479 | 237.7943 | 309.9212 | 281.5142
373.3479 | 238.72 | 310.9969 | 279.9848
374.3479 | 243.0175 | 311.0735 | 280.2069
375.3479 | 244.4231 | 315.2026 | 280.0475
376.3479 | 246.2886 | 317.1537 | 280.426
377.3479 | 245.5345 | 318.8249 | 281.1647
378.3479 | 245.9137 | 318.4998 | 281.7129
379.3479 | 245.2442 | 319.0919 | 282.1797
380.3479 | 245.4125 | 318.4085 | 282.237
381.3479 | 244.7761 | 318.7847 | 281.5821
382.3479 | 245.6972 | 318.4971 | 281.9354
383.3479 | 247.4153 | 320.0255 | 282.777
384.3479 | 249.2144 | 322.1132 | 282.6958
385.3479 | 249.7026 | 322.8424 | 282.3267
386.3479 | 250.3817 | 325.7852 | 283.6334
387.3479 | 249.9266 | 325.9347 | 283.3466
388.3479 | 249.464 | 329.1666 | 283.0408
389.3479 | 249.8116 | 330.1538 | 283.7563
390.3479 | 250.0685 | 329.4597 | 284.5256
391.3479 | 250.4405 | 329.2956 | 285.9041
392.3479 | 249.9986 | 329.8138 | 286.492
393.3479 | 249.2988 | 329.7365 | 286.269
394.3479 | 249.6972 | 331.6639 | 287.5608
395.3479 | 249.8314 | 332.8052 | 288.1247
396.3479 | 250.09 | 335.3682 | 288.2563
397.3479 | 249.8566 | 335.7221 | 290.2073
398.3479 | 251.3917 | 337.6197 | 289.8713
399.3479 | 251.9418 | 338.7129 | 289.6502
400.3479 | 252.198 | 339.4525 | 289.7856
401.3479 | 252.5376 | 340.2605 | 290.6898
402.3479 | 252.375 | 339.3748 | 291.4648
403.3479 | 251.9914 | 342.661 | 292.0122
404.3479 | 252.8086 | 345.3418 | 291.3777
405.3479 | 254.038 | 349.4902 | 292.1861
406.3479 | 253.8951 | 353.8368 | 292.7704
407.3479 | 253.8146 | 352.8113 | 294.8443
408.3479 | 254.1966 | 352.6615 | 296.0135
409.3479 | 255.002 | 361.7826 | 296.4583
410.3479 | 255.7304 | 366.4485 | 297.2773
411.3479 | 256.0143 | 363.947 | 298.115
412.3479 | 256.6161 | 360.1146 | 299.3023
413.3479 | 255.7431 | 356.7563 | 303.8799
414.3479 | 255.5099 | 357.5135 | 305.5458
415.3479 | 255.2071 | 359.6212 | 307.8777
416.3479 | 254.5275 | 356.3761 | 308.9459
417.3479 | 255.1129 | 355.5748 | 309.2381
418.3479 | 254.9661 | 356.4979 | 309.8256
419.3479 | 255.1611 | 357.0494 | 309.2793
420.3479 | 256.2094 | 357.9493 | 308.2871
421.3479 | 257.705 | 366.1226 | 307.3204
422.3479 | 257.5386 | 363.455 | 307.7173
423.3479 | 257.5569 | 362.8193 | 308.475
424.3479 | 257.7709 | 360.6149 | 307.6459
425.3479 | 258.4819 | 359.8905 | 308.6065
426.3479 | 258.7896 | 360.4433 | 309.4338
427.3479 | 259.2153 | 360.4516 | 311.3252
428.3479 | 260.0777 | 360.9264 | 311.0789
429.3479 | 260.5491 | 363.0799 | 310.6723
430.3479 | 260.8896 | 363.6374 | 309.7038
431.3479 | 261.6003 | 362.5666 | 308.8577
432.3479 | 260.9119 | 362.5597 | 308.7223
433.3479 | 260.8274 | 365.8255 | 310.2546
434.3479 | 261.896 | 368.064 | 310.8571
435.3479 | 263.0539 | 369.0251 | 311.448
436.3479 | 262.7694 | 371.611 | 312.4811
437.3479 | 262.6003 | 376.8464 | 311.6088
438.3479 | 264.698 | 377.4823 | 313.0713
439.3479 | 267.1488 | 378.6588 | 312.0569
440.3479 | 268.651 | 376.7817 | 313.4958
441.3479 | 269.3604 | 374.6997 | 313.6429
442.3479 | 270.6368 | 375.6939 | 312.4261
443.3479 | 270.9869 | 375.198 | 312.0125
444.3479 | 270.5714 | 375.5576 | 312.0537
445.3479 | 271.1165 | 379.4833 | 313.3071
446.3479 | 272.8574 | 387.1369 | 314.5482
447.3479 | 273.6433 | 396.6055 | 315.3136
448.3479 | 274.0968 | 406.9608 | 317.2308
449.3479 | 274.3485 | 412.5415 | 319.01
450.3479 | 275.8139 | 418.3042 | 320.3622
451.3479 | 276.1672 | 420.9163 | 323.3026
452.3479 | 277.6845 | 424.0973 | 322.7998
453.3479 | 277.5198 | 432.0934 | 328.8968
454.3479 | 277.2798 | 434.3509 | 329.2754
455.3479 | 277.7561 | 439.8517 | 330.9761
456.3479 | 279.0661 | 438.7399 | 333.9856
457.3479 | 279.361 | 443.2214 | 335.4155
458.3479 | 279.9941 | 446.5465 | 336.6495
459.3479 | 279.8738 | 447.4749 | 334.5769
460.3479 | 281.4137 | 443.7621 | 332.3831
461.3479 | 283.4746 | 440.349 | 329.4763
462.3479 | 286.1269 | 437.344 | 328.7686
463.3479 | 286.028 | 430.8099 | 328.1674
464.3479 | 285.3341 | 427.3715 | 327.6945
465.3479 | 285.4421 | 424.9872 | 329.5207
466.3479 | 285.0387 | 427.4035 | 331.5486
467.3479 | 284.061 | 424.5618 | 332.8435
468.3479 | 283.1563 | 424.5943 | 335.7756
469.3479 | 283.1948 | 427.8091 | 334.3845
470.3479 | 284.7249 | 430.9316 | 335.9045
471.3479 | 285.4111 | 432.6555 | 335.4713
472.3479 | 285.0329 | 442.2822 | 337.2263
473.3479 | 286.5775 | 446.362 | 338.111
474.3479 | 287.172 | 448.8334 | 339.5177
475.3479 | 287.0907 | 447.6634 | 338.7877
476.3479 | 287.6197 | 446.8277 | 338.0469
477.3479 | 287.9931 | 440.7981 | 339.2378
478.3479 | 287.5468 | 436.1187 | 340.9947
479.3479 | 286.1819 | 434.0949 | 342.2684
480.3479 | 286.8715 | 431.5091 | 344.6597
481.3479 | 285.6869 | 431.8782 | 343.6404
482.3479 | 285.1956 | 434.3456 | 344.6798
483.3479 | 284.2637 | 433.2451 | 345.3306
484.3479 | 283.7191 | 436.9658 | 346.1896
485.3479 | 282.976 | 441.9703 | 348.1104
486.3479 | 281.9468 | 444.2995 | 349.1159
487.3479 | 282.2939 | 449.1899 | 352.3844
488.3479 | 282.0024 | 458.0403 | 351.572
489.3479 | 282.3102 | 462.6571 | 352.5893
490.3479 | 283.1091 | 466.3813 | 353.3082
491.3479 | 284.3054 | 466.2996 | 354.0455
492.3479 | 284.0907 | 465.23 | 351.0349
493.3479 | 284.5356 | 458.6134 | 349.0739
494.3479 | 284.7037 | 450.9197 | 347.9211
495.3479 | 283.7339 | 446.0854 | 346.8493
496.3479 | 283.3545 | 444.7035 | 345.1051
497.3479 | 284.7391 | 446.615 | 343.4892
498.3479 | 284.2096 | 448.8387 | 344.142
499.3479 | 284.7165 | 451.2986 | 343.3025
500.3479 | 284.1324 | 453.0598 | 344.5655
501.3479 | 283.4259 | 461.4945 | 342.7255
502.3479 | 282.5757 | 466.0105 | 341.4773
503.3479 | 283.6392 | 463.9283 | 339.5567
504.3479 | 284.7026 | 471.2514 | 339.7237
505.3479 | 284.2893 | 472.1391 | 339.9237
506.3479 | 283.9459 | 474.401 | 341.2723
507.3479 | 284.4361 | 466.7045 | 340.7526
508.3479 | 284.7921 | 467.5705 | 340.7595
509.3479 | 285.6596 | 466.5045 | 339.7942
510.3479 | 287.0477 | 468.8791 | 338.7459
511.3479 | 287.4617 | 475.2016 | 340.3205
512.3479 | 289.1349 | 471.1489 | 340.3596
513.3479 | 288.4204 | 468.4642 | 341.9676
514.3479 | 288.7688 | 464.6441 | 342.1217
515.3479 | 288.5264 | 461.0916 | 344.6499
516.3479 | 288.1112 | 461.2983 | 344.5876
517.3479 | 289.1956 | 460.443 | 345.4901
518.3479 | 288.2803 | 461.3896 | 347.0741
519.3479 | 288.8857 | 469.1374 | 344.9217
520.3479 | 289.3071 | 467.0116 | 344.8
521.3479 | 289.5523 | 469.9554 | 346.1982
522.3479 | 289.1148 | 471.3022 | 345.0216
523.3479 | 288.5824 | 478.276 | 345.1113
524.3479 | 288.204 | 491.6939 | 343.9308
525.3479 | 289.402 | 493.4751 | 344.093
526.3479 | 290.7876 | 502.6495 | 344.6776
527.3479 | 291.2965 | 515.433 | 346.6993
528.3479 | 292.3096 | 515.6192 | 346.8965
529.3479 | 292.8103 | 523.6727 | 347.1114
530.3479 | 293.7396 | 529.5978 | 349.3388
531.3479 | 295.1994 | 525.2462 | 350.3058
532.3479 | 295.8338 | 527.2008 | 350.2097
533.3479 | 296.865 | 527.5124 | 350.4822
534.3479 | 299.8342 | 531.279 | 351.4774
535.3479 | 300.1756 | 532.532 | 350.6619
536.3479 | 302.5804 | 537.8056 | 351.9817
537.3479 | 303.9287 | 540.7348 | 353.431
538.3479 | 304.1208 | 536.9051 | 353.6534
539.3479 | 305.3229 | 542.735 | 355.1475
540.3479 | 306.6292 | 547.8165 | 355.4807
541.3479 | 307.0451 | 546.7366 | 356.1591
542.3479 | 308.4345 | 546.3862 | 357.9608
543.3479 | 309.7823 | 541.5546 | 357.7336
544.3479 | 309.6439 | 542.8529 | 357.5384
545.3479 | 309.6008 | 540.3419 | 356.7922
546.3479 | 308.634 | 544.7939 | 357.6043
547.3479 | 308.6866 | 544.3488 | 358.3158
548.3479 | 309.4133 | 541.1254 | 359.4827
549.3479 | 310.7142 | 544.398 | 358.0449
550.3479 | 313.6497 | 546.5919 | 357.7835
551.3479 | 312.6526 | 545.7551 | 357.7576
552.3479 | 314.9066 | 548.3709 | 355.9974
553.3479 | 315.797 | 546.0338 | 357.0722
554.3479 | 314.7908 | 548.2167 | 361.7638
555.3479 | 314.8428 | 543.8431 | 364.9665
556.3479 | 313.7278 | 549.7579 | 366.0244
557.3479 | 314.5208 | 551.3584 | 366.1205
558.3479 | 316.0213 | 552.5637 | 366.9174
559.3479 | 318.3627 | 553.0536 | 366.2177
560.3479 | 321.0501 | 555.7746 | 366.4267
561.3479 | 323.7567 | 560.0455 | 368.0545
562.3479 | 325.9923 | 559.4582 | 368.8242
563.3479 | 327.2804 | 558.7818 | 368.7824
564.3479 | 327.1527 | 564.5085 | 371.0291
565.3479 | 327.927 | 563.3468 | 373.9823
566.3635 | 328.7772 | 560.0487 | 378.6222
567.3479 | 329.6922 | 564.8487 | 383.4688
568.3479 | 331.8001 | 569.3561 | 387.0861
569.3479 | 332.5218 | 565.5646 | 387.4646
570.3479 | 335.6647 | 567.6756 | 388.4215
571.3479 | 337.0934 | 571.5693 | 389.2101
572.3479 | 338.8257 | 580.3464 | 395.9938
573.3479 | 338.2916 | 583.9599 | 395.4405
574.3479 | 339.5886 | 580.8529 | 399.5458
575.3479 | 340.5468 | 587.3069 | 399.58
576.3479 | 340.0973 | 584.1498 | 398.7285
577.3479 | 339.0487 | 583.0658 | 403.3994
578.3479 | 337.0961 | 584.2486 | 404.1423
579.3479 | 341.6011 | 583.2806 | 404.4372
580.3479 | 341.2646 | 587.22 | 403.2984
581.3479 | 342.7294 | 587.6856 | 405.9461
582.3479 | 344.3914 | 584.0798 | 404.9968
583.3479 | 343.2991 | 584.8847 | 402.3497
584.3479 | 346.9251 | 587.7371 | 401.2344
585.3479 | 347.0262 | 588.3357 | 399.1285
586.3479 | 348.2395 | 592.9066 | 396.7895
587.3479 | 347.7395 | 597.6727 | 398.8429
588.3479 | 347.419 | 598.4445 | 396.8312
589.3479 | 349.7716 | 601.2519 | 395.374
590.3479 | 350.4331 | 601.2562 | 394.2255
591.3479 | 353.325 | 599.3257 | 392.0251
592.3479 | 354.0848 | 598.925 | 392.3254
593.3479 | 355.6588 | 601.4059 | 394.9463
594.3479 | 355.1756 | 603.1734 | 395.9215
595.3479 | 355.8788 | 601.3678 | 395.656
596.3635 | 356.5266 | 599.9106 | 395.4184
597.3479 | 363.2296 | 602.2829 | 393.4463
598.3479 | 365.9104 | 601.2081 | 392.2743
599.3479 | 369.1467 | 595.7325 | 391.8996
600.3479 | 369.1541 | 596.6804 | 391.5034
601.3479 | 369.6307 | 594.8481 | 391.0846
602.3479 | 369.9933 | 599.1016 | 394.3084
603.3479 | 370.0032 | 597.2567 | 392.9723
604.3479 | 369.2862 | 595.168 | 395.5956
605.3479 | 370.3134 | 601.9694 | 395.1232
606.3479 | 370.8203 | 599.2543 | 398.2785
607.3479 | 371.8164 | 603.462 | 398.0296
608.3479 | 370.4298 | 598.9815 | 396.8014
609.3479 | 368.9974 | 598.3274 | 395.6203
610.3479 | 372.6724 | 598.7044 | 398.3405
611.3479 | 371.0994 | 599.2035 | 399.8835
612.3479 | 370.0399 | 602.0528 | 400.2473
613.3479 | 368.537 | 599.1731 | 398.5337
614.3479 | 370.6999 | 601.6773 | 399.2553
615.3479 | 377.0665 | 605.2033 | 398.1672
616.3479 | 376.8722 | 606.8632 | 397.6733
617.3479 | 377.2198 | 608.619 | 398.4548
618.3479 | 375.5379 | 610.1154 | 401.0655
619.3479 | 374.1618 | 612.3174 | 403.317
620.3479 | 374.8841 | 609.2851 | 404.2093
621.3479 | 376.8329 | 611.6504 | 403.5022
622.3479 | 377.463 | 612.7889 | 402.8373
623.3479 | 379.6637 | 611.3048 | 404.6122
624.3479 | 380.2503 | 605.077 | 403.375
625.3479 | 383.4795 | 605.0627 | 401.538
626.3479 | 385.8447 | 605.7752 | 400.9474
627.3479 | 386.268 | 607.9325 | 401.3757
628.3479 | 384.9385 | 606.6395 | 400.1776
629.3479 | 386.3581 | 613.6442 | 401.1667
630.3479 | 384.861 | 618.1006 | 399.9819
631.3479 | 385.7275 | 623.1423 | 399.1972
632.3479 | 388.7197 | 619.4591 | 398.0461
633.3479 | 388.9152 | 624.0496 | 397.2548
634.3479 | 389.5371 | 625.5584 | 397.2221
635.3479 | 392.4683 | 628.7942 | 395.6946
636.3479 | 394.3932 | 624.7093 | 394.6351
637.3479 | 394.3905 | 617.8712 | 394.435
638.3479 | 395.184 | 616.4526 | 393.8304
639.3479 | 396.1181 | 614.9149 | 398.3097
640.3479 | 394.2998 | 618.5246 | 398.8065
641.3479 | 393.8548 | 612.9908 | 399.1184
642.3479 | 391.4846 | 611.0955 | 398.026
643.3479 | 390.1136 | 612.6322 | 398.277
644.3479 | 388.0243 | 614.8175 | 403.2309
645.3479 | 387.794 | 614.0108 | 406.6521
646.3479 | 385.6008 | 614.067 | 404.849
647.3479 | 385.3334 | 610.0373 | 402.4625
648.3479 | 386.8103 | 615.9973 | 401.03
649.3479 | 387.4127 | 616.5288 | 400.3301
650.3479 | 388.3225 | 617.6478 | 400.3727
651.3479 | 389.1816 | 615.9475 | 400.4676
652.3479 | 387.6886 | 616.8771 | 400.3026
653.3479 | 389.6189 | 613.7775 | 398.7474
654.3479 | 392.2603 | 611.6076 | 396.7823
655.3479 | 390.6853 | 608.4749 | 396.1594
656.3479 | 392.2935 | 611.6338 | 396.149
657.3479 | 393.9335 | 612.4554 | 395.2837
658.3479 | 398.0033 | 612.5403 | 395.3452
659.3479 | 398.8439 | 616.206 | 393.5856
660.3479 | 397.9543 | 614.4449 | 392.6114
661.3479 | 398.5695 | 613.7358 | 391.0705
662.3479 | 398.909 | 612.0038 | 390.5341
663.3479 | 398.0208 | 613.2062 | 390.6106
664.3479 | 396.5412 | 611.7355 | 393.3594
665.3479 | 395.6113 | 605.3917 | 392.3947
666.3479 | 393.514 | 608.6772 | 397.242
667.3479 | 395.4842 | 616.314 | 396.4272
668.3479 | 394.54 | 613.348 | 395.4114
669.3479 | 393.0701 | 612.5309 | 394.7867
670.3479 | 392.4264 | 618.3931 | 395.0455
671.3479 | 394.1666 | 616.573 | 395.9469
672.3479 | 393.1714 | 615.9435 | 396.1623
673.3479 | 390.8388 | 615.2022 | 396.3009
674.3479 | 391.6707 | 611.5808 | 394.7524
675.3479 | 393.8453 | 605.6708 | 394.6807
676.3479 | 393.3443 | 602.7904 | 393.7778
677.3479 | 393.0216 | 600.1168 | 391.8836
678.3479 | 391.5573 | 609.276 | 392.6784
679.3479 | 390.134 | 619.698 | 392.723
680.3479 | 388.4557 | 620.8322 | 392.8238
681.3479 | 385.7298 | 616.0132 | 393.7356
682.3479 | 385.8009 | 621.9857 | 393.5989
683.3479 | 383.8998 | 628.8195 | 393.6951
684.3479 | 381.9582 | 627.6326 | 391.8172
685.3479 | 385.6322 | 627.1085 | 392.3386
686.3479 | 387.314 | 629.1025 | 391.4611
687.3479 | 389.4423 | 630.6846 | 389.9472
688.3479 | 389.4295 | 630.2955 | 388.5036
689.3479 | 389.4782 | 635.8263 | 389.2244
690.3479 | 388.1984 | 637.2405 | 388.9748
691.3479 | 387.0567 | 627.3114 | 388.9072
692.3479 | 385.9503 | 621.8344 | 392.356
693.3479 | 383.5253 | 627.1747 | 392.5366
694.3479 | 383.4975 | 622.244 | 392.057
695.3479 | 386.1319 | 629.4344 | 390.4949
696.3479 | 390.3928 | 628.0703 | 391.1029
697.3479 | 393.1689 | 626.7709 | 391.5361
698.3479 | 391.587 | 629.8594 | 390.6085
699.3479 | 392.2226 | 628.7223 | 390.0863
700.3479 | 392.7455 | 622.8834 | 388.6885
701.3479 | 394.2934 | 619.851 | 389.4507
702.3479 | 397.1668 | 623.6504 | 390.1159
703.3479 | 397.4805 | 629.3646 | 390.6375
704.3479 | 396.593 | 628.7423 | 390.5895
705.3479 | 399.6001 | 626.2963 | 390.5294
706.3479 | 400.8683 | 625.4579 | 390.4929
707.3479 | 403.4927 | 620.3831 | 389.8352
708.3479 | 403.0279 | 623.2124 | 389.0408
709.3479 | 402.5401 | 623.0767 | 390.5497
710.3479 | 401.4428 | 628.5032 | 391.2556
711.3479 | 398.4828 | 630.622 | 390.9777
712.3479 | 396.5342 | 633.4594 | 391.9572
713.3479 | 396.364 | 632.3577 | 391.6207
714.3479 | 394.2391 | 632.6892 | 389.7309
715.3479 | 398.6565 | 630.4158 | 390.5573
716.3479 | 399.9003 | 628.1685 | 390.4238
717.3479 | 398.3177 | 636.3457 | 391.7412
718.3479 | 398.621 | 637.0385 | 391.4071
719.3479 | 397.2688 | 628.0165 | 390.6843
720.3479 | 399.2981 | 622.3387 | 392.093
721.3479 | 402.8111 | 617.611 | 391.4499
722.3479 | 403.8231 | 611.2992 | 390.354
723.3479 | 405.0712 | 605.872 | 391.3539
724.3479 | 407.3 | 604.6414 | 390.0995
725.3479 | 413.0669 | 602.7885 | 389.2201
726.3479 | 414.0304 | 601.3868 | 388.0897
727.3479 | 412.4579 | 593.3826 | 387.8267
728.3479 | 411.9061 | 602.5481 | 388.0376
729.3479 | 413.5991 | 606.608 | 389.1193
730.3479 | 413.7434 | 608.1458 | 388.3868
731.3479 | 414.2819 | 611.5557 | 388.8283
732.3479 | 414.3551 | 610.9198 | 389.9246
733.3479 | 413.7605 | 613.0012 | 391.6458
734.3479 | 412.6408 | 629.298 | 395.527
735.3479 | 409.6731 | 631.6304 | 397.3226
736.3479 | 407.9564 | 630.109 | 397.9841
737.3479 | 410.2728 | 631.8397 | 397.2871
738.3479 | 408.9681 | 624.8289 | 396.4441
739.3479 | 409.7069 | 627.074 | 396.3728
740.3479 | 415.5153 | 622.3517 | 395.6153
741.3479 | 414.9769 | 620.8093 | 395.6064
742.3479 | 416.7071 | 623.4863 | 401.4619
743.3479 | 417.4918 | 623.1731 | 399.6321
744.3479 | 418.0818 | 616.9847 | 398.4031
745.3479 | 417.1509 | 615.4936 | 400.1506
746.3479 | 415.7894 | 616.6982 | 399.4765
747.3479 | 413.8894 | 622.4594 | 399.2963
748.3479 | 415.4611 | 629.0987 | 400.1612
749.3479 | 414.9232 | 631.4199 | 400.4512
750.3479 | 414.2808 | 633.2665 | 400.0303
751.3479 | 412.83 | 629.9 | 397.731
752.3479 | 412.8868 | 628.7034 | 397.001
753.3479 | 412.9814 | 629.0964 | 396.2652
754.3479 | 412.6757 | 627.1338 | 396.9666
755.3479 | 416.3482 | 621.8612 | 398.7929
756.3479 | 415.3992 | 618.44 | 399.5705
757.3479 | 415.6963 | 618.5616 | 400.441
758.3479 | 416.3332 | 634.1796 | 400.5245
759.3479 | 417.4677 | 636.8188 | 399.8531
760.3479 | 415.7649 | 637.0424 | 399.3473
761.3479 | 413.6138 | 644.7025 | 397.6397
762.3479 | 412.1753 | 649.1093 | 395.851
763.3479 | 412.5258 | 656.4976 | 396.0174
764.3479 | 412.481 | 657.7434 | 396.5188
765.3479 | 411.773 | 653.1807 | 398.715
766.3479 | 412.6624 | 647.8486 | 400.4665
767.3479 | 411.5404 | 654.8634 | 399.7056
768.3479 | 412.0683 | 657.9214 | 399.3502
769.3479 | 415.4575 | 656.091 | 398.4892
770.3479 | 414.9971 | 653.5101 | 400.8117
771.3479 | 416.885 | 656.325 | 399.399
772.3479 | 417.8839 | 652.2158 | 400.1601
773.3479 | 417.7147 | 652.1523 | 399.1419
774.3479 | 419.0999 | 657.2949 | 399.7412
775.3479 | 419.1176 | 662.9876 | 399.0867
776.3479 | 418.9949 | 659.6067 | 398.7087
777.3479 | 419.0909 | 658.8225 | 399.6712
778.3479 | 419.4544 | 656.5824 | 399.4523
779.3479 | 421.0192 | 663.0434 | 400.7399
780.3479 | 419.3072 | 659.0613 | 399.8568
781.3479 | 416.1973 | 669.1445 | 401.5071
782.3479 | 416.1673 | 667.5261 | 400.6682
783.3479 | 414.6587 | 666.5488 | 401.4935
784.3479 | 416.1772 | 663.739 | 402.0214
785.3479 | 415.2141 | 669.1706 | 403.1277
786.3479 | 414.0071 | 674.189 | 403.0058
787.3479 | 415.8966 | 669.9045 | 402.6894
788.3479 | 420.1982 | 666.859 | 405.2247
789.3479 | 420.3772 | 659.348 | 404.8755
790.3479 | 420.1978 | 659.9887 | 404.4771
791.3479 | 421.5454 | 657.6201 | 403.4674
792.3479 | 420.815 | 661.8726 | 402.8104
793.3479 | 421.9063 | 660.3898 | 402.7501
794.3479 | 421.1027 | 661.2212 | 404.1703
795.3479 | 422.8804 | 663.8378 | 404.0567
796.3479 | 424.7598 | 667.2563 | 403.0614
797.3479 | 432.1073 | 661.6652 | 402.7298
798.3479 | 431.7213 | 673.8907 | 401.5731
799.3479 | 431.6406 | 667.2229 | 400.5261
800.3479 | 432.2153 | 669.3306 | 399.5991
801.3479 | 433.7369 | 668.1192 | 402.8796
802.3479 | 433.6391 | 670.2919 | 404.3832
803.3479 | 434.1206 | 663.1772 | 404.3819
804.3479 | 435.3786 | 662.5837 | 405.61
805.3479 | 432.5128 | 655.6552 | 404.5544
806.3479 | 431.9269 | 653.0362 | 404.667
807.3479 | 430.502 | 655.0695 | 405.0139
808.3479 | 430.1224 | 655.1469 | 404.5727
809.3479 | 429.428 | 653.1816 | 403.6656
810.3479 | 432.3478 | 655.6026 | 408.0144
811.3479 | 431.3753 | 660.5131 | 409.5231
812.3479 | 432.0271 | 665.3217 | 407.7857
813.3479 | 432.6072 | 663.7465 | 407.2647
814.3479 | 433.2748 | 662.0827 | 407.3913
815.3479 | 431.7961 | 656.5134 | 406.7248
816.3479 | 432.7556 | 664.1741 | 405.7633
817.3479 | 432.6503 | 663.6536 | 405.3007
818.3479 | 432.8347 | 663.9133 | 403.6635
819.3479 | 430.4605 | 668.1357 | 404.3116
820.3479 | 429.8426 | 664.8536 | 403.9368
821.3479 | 429.4823 | 662.3142 | 404.1869
822.3479 | 428.5595 | 661.9327 | 405.5383
823.3479 | 426.4741 | 666.0211 | 405.3449
824.3479 | 425.4627 | 662.3227 | 408.2081
825.3479 | 423.8862 | 662.4919 | 410.451
826.3479 | 423.2038 | 664.6382 | 415.7207
827.3479 | 421.3074 | 659.335 | 417.4984
828.3479 | 418.782 | 654.0568 | 419.264
829.3479 | 420.9102 | 659.6681 | 418.2671
830.3479 | 419.752 | 660.0305 | 419.3905
831.3479 | 422.8017 | 655.9813 | 418.5145
832.3479 | 423.7262 | 655.5508 | 417.9833
833.3479 | 427.0522 | 660.8569 | 419.6396
834.3479 | 426.4895 | 661.6325 | 419.1074
835.3479 | 426.5132 | 656.3046 | 419.9018
836.3479 | 426.689 | 651.0455 | 418.0144
837.3479 | 426.9958 | 651.3149 | 418.0502
838.3479 | 431.0232 | 645.37 | 418.4756
839.3479 | 433.9044 | 642.3977 | 416.7485
840.3479 | 434.9283 | 641.626 | 418.7491
841.3479 | 435.738 | 640.4609 | 417.6844
842.3479 | 435.3235 | 638.2096 | 417.5842
843.3479 | 433.481 | 643.6377 | 417.6829
844.3479 | 434.3779 | 641.996 | 417.4462
845.3479 | 435.4836 | 647.2867 | 415.3043
846.3479 | 438.3984 | 644.165 | 411.9333
847.3479 | 443.2141 | 655.0694 | 412.4119
848.3479 | 445.2553 | 654.6307 | 412.6976
849.3479 | 447.0868 | 653.4953 | 413.0722
850.3479 | 448.3125 | 656.8596 | 410.0657
851.3479 | 448.0093 | 665.0174 | 408.8517
852.3479 | 445.5934 | 664.2121 | 408.5957
853.3479 | 446.6789 | 662.8364 | 411.8745
854.3479 | 444.5495 | 656.4705 | 411.845
855.3479 | 445.6199 | 653.7195 | 410.5234
856.3479 | 443.5393 | 651.6911 | 418.0164
857.3479 | 441.7745 | 654.4866 | 416.2952
858.3479 | 442.0823 | 650.2787 | 416.171
859.3479 | 441.0797 | 655.8132 | 416.593
860.3479 | 441.3791 | 655.0171 | 416.2914
861.3479 | 438.9141 | 658.2651 | 417.5247
862.3479 | 440.1995 | 658.7948 | 414.7659
863.3479 | 440.8503 | 658.6312 | 413.7225
864.3479 | 439.7175 | 671.4394 | 412.517
865.3479 | 439.0047 | 665.0229 | 411.1816
866.3479 | 438.4202 | 650.6754 | 408.7904
867.3479 | 440.2801 | 647.1496 | 407.5996
868.3479 | 439.5114 | 643.1982 | 406.5312
869.3479 | 444.6482 | 652.352 | 406.0683
870.3479 | 443.339 | 653.7212 | 405.3427
871.3479 | 444.5096 | 650.0854 | 405.5143
872.3479 | 446.3632 | 653.0935 | 404.9655
873.3479 | 444.9842 | 646.505 | 404.6959
874.3479 | 445.2605 | 642.5433 | 403.7802
875.3635 | 444.555 | 646.6236 | 404.8996
876.3479 | 444.3205 | 645.7269 | 404.5501
877.3479 | 441.657 | 643.8564 | 403.7909
878.3479 | 439.8285 | 638.3578 | 403.984
879.3479 | 441.504 | 631.0101 | 403.346
880.3479 | 443.0792 | 638.4586 | 404.4724
881.3479 | 443.5926 | 634.5535 | 403.4664
882.3479 | 443.0976 | 638.3973 | 403.1515
883.3479 | 447.6266 | 639.1107 | 402.4531
884.3479 | 447.1898 | 646.3825 | 402.2924
885.3479 | 446.3191 | 644.4101 | 403.8045
886.3479 | 444.7283 | 647.1519 | 402.2931
887.3479 | 444.9098 | 642.2227 | 402.0106
888.3479 | 448.1207 | 652.1635 | 402.3271
889.3479 | 451.224 | 657.8524 | 402.4335
890.3479 | 449.697 | 652.3786 | 403.4404
891.3479 | 448.8594 | 655.6802 | 403.392
892.3479 | 447.4492 | 661.4413 | 403.9259
893.3479 | 448.2614 | 653.7768 | 403.6377
894.3479 | 444.6442 | 659.7373 | 402.4355
895.3479 | 442.6745 | 661.475 | 401.6558
896.3479 | 442.3083 | 670.5191 | 406.0905
897.3479 | 442.3371 | 670.7915 | 406.1971
898.3479 | 443.4445 | 666.286 | 409.7328
899.3479 | 442.8906 | 662.1221 | 411.7607
900.3479 | 444.028 | 660.1495 | 410.8506
901.3479 | 443.3993 | 658.0671 | 413.1613
902.3479 | 443.7398 | 659.8373 | 410.6673
903.3479 | 443.2769 | 653.6064 | 409.0406
904.3479 | 445.9414 | 646.3697 | 408.7496
905.3479 | 445.6978 | 643.0304 | 408.3814
906.3479 | 450.5186 | 645.7615 | 407.0255
907.3479 | 450.7024 | 637.5609 | 405.2773
908.3479 | 452.0599 | 633.993 | 403.6437
909.3479 | 450.7041 | 644.0667 | 402.7377
910.3479 | 450.5865 | 647.5406 | 402.3181
911.3479 | 449.5712 | 648.5613 | 401.5045
912.3479 | 447.8106 | 650.5127 | 400.378
913.3479 | 448.1316 | 652.1141 | 401.592
914.3479 | 445.7067 | 659.1909 | 405.3622
915.3479 | 443.6469 | 652.8492 | 404.7839
916.3479 | 449.4369 | 660.0925 | 405.2913
917.3479 | 452.4561 | 664.7125 | 404.4534
918.3479 | 453.666 | 678.3307 | 407.0938
919.3479 | 453.8284 | 672.9971 | 406.3255
920.3479 | 453.9132 | 673.9898 | 407.9871
921.3479 | 455.7068 | 669.585 | 407.1441
922.3479 | 459.4999 | 671.3404 | 406.4902
923.3479 | 458.8006 | 670.7373 | 407.1249
924.3479 | 457.1456 | 669.7705 | 406.966
925.3479 | 459.028 | 669.7964 | 407.4362
926.3479 | 461.5146 | 668.8109 | 406.068
927.3479 | 461.8978 | 666.0673 | 406.817
928.3479 | 458.34 | 669.0538 | 410.2493
929.3479 | 455.9279 | 665.2962 | 411.1069
930.3479 | 456.0299 | 666.5193 | 411.2276
931.3479 | 458.4454 | 663.3531 | 410.9942
932.3479 | 460.8606 | 669.3306 | 411.2295
933.3479 | 462.0079 | 668.0654 | 410.5448
934.3479 | 460.5658 | 661.5619 | 414.916
935.3479 | 458.3571 | 662.2482 | 416.4959
936.3479 | 457.8059 | 659.9933 | 419.8227
937.3479 | 456.5556 | 665.3047 | 419.9137
938.3479 | 459.1881 | 660.0946 | 419.0111
939.3479 | 466.3223 | 664.2533 | 420.2131
940.3479 | 467.9917 | 671.3564 | 419.7972
941.3479 | 466.8872 | 662.9854 | 421.0562
942.3479 | 466.7989 | 653.8214 | 420.7796
943.3479 | 467.9181 | 650.6586 | 419.7362
944.3479 | 468.7334 | 664.4422 | 420.0625
945.3479 | 467.8368 | 672.1879 | 418.9042
946.3479 | 466.3251 | 675.5135 | 421.9658
947.3479 | 465.9859 | 675.6626 | 422.7843
948.3479 | 464.3784 | 677.7159 | 423.8093
949.3479 | 464.3193 | 678.5421 | 422.9691
950.3479 | 464.0394 | 679.0978 | 421.1797
951.3479 | 467.721 | 692.1937 | 420.9642
952.3479 | 465.966 | 690.8765 | 422.7515
953.3479 | 468.381 | 692.6586 | 423.0561
954.3479 | 470.6989 | 689.0099 | 422.999
955.3479 | 473.3635 | 690.6648 | 422.8217
956.3479 | 473.7079 | 685.9333 | 422.8476
957.3479 | 475.9389 | 686.7913 | 424.0889
958.3479 | 480.98 | 696.7306 | 424.125
959.3479 | 481.9076 | 701.5113 | 426.3132
960.3479 | 485.9883 | 705.63 | 427.8448
961.3479 | 485.6834 | 710.8018 | 428.57
962.3479 | 484.7456 | 705.6658 | 427.6425
963.3479 | 489.9908 | 697.5187 | 428.7519
964.3479 | 495.1446 | 695.5757 | 427.6033
965.3479 | 495.3472 | 692.2259 | 426.0412
966.3479 | 494.7773 | 688.6777 | 424.5474
967.3479 | 492.3345 | 694.7768 | 424.2371
968.3479 | 492.2812 | 694.1706 | 423.6735
969.3479 | 488.143 | 700.6323 | 422.8273
970.3479 | 487.1625 | 701.7185 | 421.8883
971.3479 | 487.081 | 698.2886 | 419.6284
972.3479 | 487.4646 | 699.1895 | 418.9997
973.3479 | 489.3796 | 695.1403 | 419.4772
974.3479 | 486.6602 | 691.1355 | 417.8062
975.3479 | 490.3325 | 702.1211 | 416.6047
976.3479 | 493.0937 | 710.9624 | 418.9986
977.3479 | 497.936 | 718.3715 | 417.8972
978.3479 | 496.7838 | 707.4845 | 417.9861
979.3479 | 496.7357 | 704.8056 | 419.8742
980.3479 | 495.4219 | 694.6032 | 420.3905
981.3479 | 497.9507 | 697.1166 | 419.3958
982.3479 | 500.2957 | 697.6349 | 419.397
983.3479 | 499.6908 | 698.7481 | 419.0359
984.3479 | 503.2446 | 698.6048 | 421.6521
985.3479 | 504.9166 | 685.9058 | 422.3001
986.3479 | 503.3261 | 697.0911 | 425.5585
987.3479 | 503.0311 | 692.2941 | 426.2149
988.3479 | 505.3676 | 701.7955 | 429.5196
989.3479 | 505.1956 | 701.0702 | 431.5794
990.3479 | 505.3345 | 682.7997 | 430.9826
991.3479 | 508.4303 | 681.0497 | 433.0817
992.3479 | 512.8162 | 691.3804 | 434.0717
993.3479 | 517.4255 | 698.3638 | 435.5932
994.3479 | 519.5189 | 690.3273 | 436.6784
995.3479 | 518.1521 | 696.2506 | 435.3398
996.3479 | 516.256 | 695.5665 | 434.3569
997.3479 | 522.5917 | 689.2742 | 434.1235
998.3479 | 519.1411 | 697.3507 | 432.242
999.3479 | 516.5788 | 698.7615 | 432.4317
1000.3479 | 515.59 | 709.3654 | 433.4027
1001.3479 | 511.7585 | 705.0277 | 432.4393
1002.3479 | 511.8875 | 697.0364 | 429.8438
1003.3479 | 511.5287 | 698.403 | 428.7594
1004.3479 | 508.8502 | 700.7474 | 427.4544
1005.3479 | 505.5822 | 705.802 | 425.3949
1006.3479 | 505.8057 | 704.955 | 424.8335
1007.3479 | 503.2021 | 707.5373 | 424.187
1008.3479 | 502.9181 | 713.3802 | 423.5946
1009.3479 | 500.6223 | 718.94 | 423.1686
1010.3479 | 500.0181 | 724.0175 | 422.6726
1011.3479 | 501.0855 | 722.4857 | 422.4201
1012.3479 | 503.5622 | 722.6925 | 423.075
1013.3479 | 503.3443 | 716.4585 | 423.1348
1014.3479 | 503.7195 | 716.4749 | 421.7207
1015.3479 | 502.7183 | 715.9431 | 422.1046
1016.3479 | 504.1194 | 705.6658 | 421.8207
1017.3479 | 509.1483 | 707.8189 | 423.83
1018.3479 | 511.1659 | 719.1964 | 423.1097
1019.3479 | 511.9627 | 713.5721 | 422.7298
1020.3479 | 516.9491 | 721.752 | 423.7313
1021.3479 | 520.0494 | 719.6348 | 422.9362
1022.3479 | 521.2489 | 713.447 | 423.0515
1023.3479 | 526.3606 | 721.3791 | 423.3693
1024.3479 | 528.0363 | 710.8905 | 423.9929
1025.3479 | 531.7981 | 721.1178 | 424.6832
1026.3479 | 534.986 | 722.7533 | 427.0315
1027.3479 | 541.2829 | 720.6355 | 427.5639
1028.3479 | 540.7384 | 714.0092 | 426.9497
1029.3479 | 542.6012 | 712.6981 | 427.6803
1030.3479 | 543.6563 | 706.256 | 426.4552
1031.3479 | 538.06 | 702.6114 | 425.5935
1032.3479 | 537 | 702.9776 | 424.3224
1033.3479 | 537.5242 | 704.0032 | 423.4942
1034.3479 | 538.035 | 705.0096 | 422.4333
1035.3479 | 535.6955 | 712.0569 | 421.9219
1036.3479 | 535.076 | 708.9413 | 421.5434
1037.3479 | 536.6006 | 715.6393 | 422.6133
1038.3479 | 536.6576 | 711.7163 | 423.5072
1039.3479 | 538.1438 | 719.4956 | 425.5066
1040.3479 | 539.2655 | 721.5323 | 428.8982
1041.3479 | 539.3799 | 718.9549 | 429.2176
1042.3479 | 539.4134 | 721.0141 | 429.0028
1043.3479 | 543.4528 | 720.1746 | 428.5812
1044.3479 | 546.5597 | 714.1839 | 431.1104
1045.3479 | 550.4567 | 713.4278 | 429.1064
1046.3479 | 554.0221 | 707.6218 | 429.7003
1047.3479 | 557.0984 | 705.7996 | 429.03
1048.3479 | 559.7943 | 709.0931 | 430.4371
1049.3479 | 562.8731 | 702.2501 | 430.1553
1050.3479 | 565.1336 | 705.5543 | 430.6258
1051.3479 | 560.913 | 709.5008 | 430.5604
1052.3479 | 562.4689 | 700.8827 | 431.9879
1053.3479 | 561.5347 | 708.6376 | 434.0604
1054.3479 | 565.8219 | 700.3507 | 434.0716
1055.3479 | 567.7621 | 695.9405 | 432.3563
1056.3479 | 565.8353 | 696.4519 | 431.5556
1057.3479 | 569.394 | 697.3224 | 430.9432
1058.3479 | 572.7906 | 694.9623 | 429.5691
1059.3479 | 574.5736 | 691.4194 | 429.4541
1060.3479 | 575.1417 | 683.7278 | 429.8296
1061.3479 | 571.6147 | 682.614 | 430.3646
1062.3479 | 568.2018 | 679.9829 | 430.5787
1063.3479 | 568.5045 | 684.8315 | 430.6523
1064.3479 | 568.1848 | 686.2401 | 430.1663
1065.3479 | 566.9883 | 681.0838 | 429.3493
1066.3479 | 569.3289 | 677.1044 | 430.182
1067.3479 | 570.8544 | 681.7209 | 430.4748
1068.3479 | 573.7024 | 682.2862 | 431.2421
1069.3479 | 575.1922 | 669.833 | 430.4851
1070.3479 | 577.9232 | 667.6203 | 429.9246
1071.3479 | 584.9041 | 670.901 | 429.0836
1072.3479 | 588.6029 | 682.5207 | 429.8898
1073.3479 | 592.157 | 685.1942 | 431.2764
1074.3479 | 597.5249 | 684.0279 | 430.677
1075.3479 | 589.361 | 688.5519 | 430.3072
1076.3479 | 590.7421 | 684.0253 | 430.3425
1077.3479 | 594.0336 | 679.1007 | 429.3871
1078.3479 | 591.2 | 678.0317 | 429.8152
1079.3479 | 588.7166 | 676.6045 | 431.9172
1080.3479 | 590.972 | 689.5966 | 433.0679
1081.3479 | 591.8245 | 685.6585 | 433.6777
1082.3479 | 590.6111 | 681.6224 | 432.6803
1083.3479 | 590.2408 | 687.7535 | 433.1484
1084.3479 | 588.6547 | 684.9154 | 433.4715
1085.3479 | 585.7536 | 676.9535 | 432.9424
1086.3479 | 578.1748 | 677.4074 | 431.5327
1087.3479 | 575.1833 | 679.9934 | 430.2198
1088.3479 | 571.0987 | 673.2879 | 429.6831
1089.3479 | 567.838 | 670.7857 | 430.3732
1090.3479 | 569.2467 | 673.9546 | 430.1798
1091.3479 | 573.9239 | 673.1032 | 430.4754
1092.3479 | 581.4067 | 666.0173 | 429.8421
1093.3479 | 584.0086 | 675.4586 | 429.5905
1094.3479 | 582.8331 | 682.1118 | 429.9395
1095.3479 | 586.2045 | 677.9695 | 429.4296
1096.3479 | 591.1682 | 681.4728 | 429.304
1097.3479 | 589.6895 | 680.8215 | 428.4273
1098.3479 | 588.8143 | 690.1919 | 428.3384
1099.3479 | 585.7355 | 696.4756 | 430.1192
1100.3479 | 585.1644 | 696.8214 | 431.4875
1101.3479 | 583.9487 | 696.497 | 432.2459
1102.3479 | 583.0507 | 698.0648 | 434.3785
1103.3479 | 581.651 | 710.3399 | 433.5157
1104.3479 | 583.152 | 714.2205 | 433.585
1105.3479 | 583.3386 | 707.7553 | 433.7798
1106.3479 | 584.3404 | 718.1738 | 433.8925
1107.3479 | 586.7018 | 721.6909 | 434.0313
1108.3479 | 588.2715 | 721.5529 | 434.167
1109.3479 | 589.168 | 720.8235 | 434.8796
1110.3479 | 590.1566 | 719.4637 | 435.4436
1111.3479 | 593.934 | 717.0044 | 434.9683
1112.3479 | 591.5671 | 712.6207 | 435.3714
1113.3479 | 589.8947 | 709.6861 | 435.4627
1114.3479 | 590.6004 | 705.8115 | 435.3776
1115.3479 | 597.4252 | 698.1367 | 436.444
1116.3479 | 594.3606 | 699.5494 | 437.3147
1117.3479 | 593.0475 | 702.967 | 436.64
1118.3479 | 594.3661 | 718.4636 | 437.5855
1119.3479 | 594.6197 | 711.2321 | 437.8586
1120.3479 | 597.3222 | 704.2352 | 438.9489
1121.3479 | 598.8656 | 706.855 | 440.1821
1122.3479 | 601.0833 | 714.0868 | 439.8712
1123.3479 | 600.0438 | 715.1355 | 441.4835
1124.3479 | 598.3285 | 702.12 | 440.9198
1125.3479 | 603.4907 | 703.7136 | 440.1197
1126.3479 | 606.2268 | 707.1056 | 440.4396
1127.3479 | 602.8914 | 710.2458 | 441.2661
1128.3479 | 606.2766 | 707.5035 | 440.7099
1129.3479 | 604.946 | 704.6357 | 441.3877
1130.3479 | 606.2451 | 702.171 | 441.9894
1131.3479 | 609.259 | 690.72 | 441.5114
1132.3479 | 609.738 | 689.3676 | 441.4626
1133.3479 | 618.0057 | 696.0805 | 442.0281
1134.3479 | 626.2987 | 683.7549 | 442.9269
1135.3479 | 626.0812 | 673.0922 | 443.6142
1136.3479 | 621.4766 | 688.0302 | 445.3142
1137.3479 | 624.9289 | 686.2696 | 448.062
1138.3479 | 630.9167 | 685.6655 | 448.4374
1139.3479 | 632.745 | 691.6385 | 449.2227
1140.3479 | 631.0587 | 684.2449 | 449.2712
1141.3479 | 633.5772 | 691.2059 | 452.5876
1142.3479 | 634.8446 | 693.3415 | 453.8475
1143.3479 | 631.33 | 686.1898 | 456.7474
1144.3479 | 637.7446 | 694.0466 | 458.1133
1145.3479 | 637.5373 | 686.3021 | 457.0637
1146.3479 | 632.4312 | 690.9189 | 456.462
1147.3479 | 636.739 | 691.6064 | 456.1834
1148.3479 | 637.4381 | 684.0217 | 456.6016
1149.3479 | 638.8865 | 689.9799 | 456.5673
1150.3479 | 645.8405 | 681.7606 | 457.6338
1151.3479 | 641.87 | 686.1616 | 457.0951
1152.3479 | 646.6917 | 679.0222 | 459.6644
1153.3479 | 646.5194 | 677.5189 | 461.4722
1154.3479 | 643.5618 | 692.4553 | 461.2003
1155.3479 | 645.4036 | 692.1469 | 460.9223
1156.3479 | 641.7423 | 685.3307 | 460.2666
1157.3479 | 639.3997 | 686.6286 | 459.6723
1158.3479 | 640.9359 | 697.8022 | 460.0197
1159.3479 | 637.5026 | 698.6994 | 462.1265
1160.3479 | 634.9276 | 694.7046 | 464.3098
1161.3479 | 641.7568 | 695.8916 | 466.8418
1162.3479 | 644.1298 | 697.3975 | 467.4853
1163.3479 | 644.5437 | 700.1235 | 467.8534
1164.3479 | 645.9626 | 701.3372 | 468.3856
1165.3479 | 651.5309 | 701.6031 | 471.449
1166.3479 | 647.9004 | 694.8695 | 470.8427
1167.3479 | 648.4986 | 698.2246 | 473.0066
1168.3479 | 646.1708 | 695.4706 | 474.3214
1169.3479 | 646.2734 | 693.501 | 474.3268
1170.3479 | 649.2042 | 685.803 | 474.9411
1171.3479 | 648.9886 | 680.6924 | 475.0979
1172.3479 | 644.9162 | 681.1444 | 475.9112
1173.3479 | 647.0284 | 681.7315 | 474.5647
1174.3479 | 648.8033 | 670.0457 | 472.7806
1175.3479 | 644.475 | 669.8448 | 471.6983
1176.3479 | 644.2398 | 677.0086 | 470.8001
1177.3479 | 644.5514 | 677.4925 | 470.4866
1178.3479 | 651.7232 | 676.493 | 472.783
1179.3479 | 648.5813 | 676.9215 | 470.2724
1180.3479 | 646.1074 | 674.0747 | 470.2481
1181.3479 | 648.5061 | 687.5277 | 468.2503
1182.3479 | 648.9168 | 687.2261 | 469.3881
1183.3479 | 646.917 | 682.5854 | 470.5589
1184.3479 | 649.6875 | 675.9314 | 470.9344
1185.3479 | 651.8799 | 682.0152 | 473.3066
1186.3479 | 660.1393 | 676.1919 | 471.9007
1187.3479 | 658.44 | 682.3108 | 470.9712
1188.3479 | 656.554 | 685.2563 | 472.2359
1189.3479 | 650.2029 | 676.0313 | 472.3695
1190.3479 | 646.8561 | 680.3974 | 471.501
1191.3479 | 643.4 | 682.8891 | 471.5999
1192.3479 | 643.2942 | 694.0147 | 470.9381
1193.3479 | 640.0717 | 696.3985 | 469.7874
1194.3479 | 641.2557 | 687.5675 | 469.6696
1195.3479 | 645.3878 | 693.815 | 469.4345
1196.3479 | 645.9182 | 682.0796 | 469.3937
1197.3479 | 648.9901 | 673.6519 | 470.7504
1198.3479 | 650.3846 | 669.1219 | 469.9412
1199.3479 | 652.112 | 678.1018 | 467.5362
1200.3479 | 650.204 | 684.3347 | 466.4242
1201.3479 | 648.5753 | 682.8852 | 466.0978
1202.3479 | 646.832 | 674.2959 | 465.4466
1203.3479 | 645.744 | 674.9558 | 467.6485
1204.3479 | 648.6823 | 674.5761 | 471.5867
1205.3479 | 648.6436 | 671.1805 | 472.8183
1206.3479 | 649.3599 | 676.8313 | 473.3452
1207.3479 | 651.9453 | 672.227 | 472.8372
1208.3479 | 649.3149 | 661.5013 | 475.4578
1209.3479 | 653.2436 | 668.9213 | 476.5214
1210.3479 | 651.5785 | 673.6939 | 478.0904
1211.3479 | 656.5912 | 665.3732 | 479.629
1212.3479 | 659.6288 | 661.9069 | 482.6436
1213.3479 | 664.7414 | 667.9854 | 484.0778
1214.3479 | 671.2471 | 660.6261 | 484.9769
1215.3479 | 674.663 | 654.9753 | 483.2486
1216.3479 | 674.2797 | 654.8259 | 482.8359
1217.3479 | 682.091 | 657.0848 | 481.2994
1218.3479 | 681.8833 | 659.4384 | 479.4225
1219.3479 | 674.5565 | 671.9828 | 479.843
1220.3479 | 675.2665 | 669.8726 | 479.0763
1221.3479 | 674.742 | 668.5893 | 480.0782
1222.3479 | 679.0124 | 665.246 | 477.98
1223.3479 | 671.8469 | 670.5271 | 479.9445
1224.3479 | 670.4598 | 675.7597 | 477.2578
1225.3479 | 668.9694 | 679.0438 | 477.7639
1226.3479 | 667.5752 | 684.8986 | 478.8563
1227.3479 | 665.9831 | 683.1136 | 480.1465
1228.3479 | 660.3896 | 685.0272 | 479.1208
1229.3479 | 668.7515 | 680.3438 | 478.2185
1230.3479 | 674.1368 | 678.8013 | 477.5294
1231.3479 | 668.8213 | 677.0611 | 476.5437
1232.3479 | 661.9043 | 668.7883 | 477.2241
1233.3479 | 652.0935 | 672.424 | 477.2719
1234.3479 | 650.4606 | 682.4516 | 478.0317
1235.3479 | 657.6076 | 690.7333 | 478.2622
1236.3479 | 659.1158 | 683.5929 | 479.4488
1237.3479 | 663.9537 | 691.172 | 480.4646
1238.3479 | 663.8807 | 686.0869 | 480.1139
1239.3479 | 663.6944 | 683.9844 | 485.1732
1240.3479 | 668.1926 | 687.7918 | 483.638
1241.3479 | 677.8606 | 678.1644 | 483.5398
1242.3479 | 676.167 | 669.652 | 483.6474
1243.3479 | 675.3791 | 665.6295 | 487.8434
1244.3479 | 677.3425 | 676.2212 | 489.0812
1245.3479 | 681.7626 | 671.2775 | 488.0883
1246.3479 | 682.7445 | 664.4021 | 488.727
1247.3479 | 674.2945 | 665.2744 | 487.6618
1248.3479 | 679.6836 | 659.4512 | 489.8369
1249.3479 | 673.0688 | 658.6015 | 488.8599
1250.3479 | 675.2017 | 652.1552 | 487.4811
1251.3479 | 671.2373 | 641.7531 | 486.1695
1252.3479 | 672.5076 | 635.1192 | 486.7757
1253.3479 | 666.4193 | 647.614 | 486.1476
1254.3479 | 668.8427 | 646.9825 | 485.8429
1255.3479 | 674.6568 | 640.5198 | 483.6135
1256.3479 | 675.6246 | 637.7847 | 480.5733
1257.3479 | 677.836 | 633.5004 | 483.0449
1258.3479 | 672.4733 | 628.8653 | 482.9594
1259.3479 | 671.1038 | 631.8654 | 483.3702
1260.3479 | 678.0435 | 628.4472 | 483.3019
1261.3479 | 688.3945 | 635.4917 | 481.8181
1262.3479 | 683.3571 | 645.4056 | 484.8905
1263.3479 | 678.538 | 638.1803 | 483.2569
1264.3479 | 687.7158 | 630.2144 | 482.76
1265.3479 | 692.5487 | 629.0797 | 481.7121
1266.3479 | 692.9056 | 623.5611 | 483.3321
1267.3479 | 694.5424 | 621.2092 | 483.4236
1268.3479 | 701.3881 | 624.2674 | 483.3721
1269.3479 | 698.9958 | 621.1257 | 484.6588
1270.3479 | 694.7746 | 614.5724 | 484.3912
1271.3479 | 688.9775 | 623.5178 | 486.7347
1272.3479 | 689.2642 | 629.0898 | 484.9634
1273.3479 | 693.9257 | 642.6037 | 486.6894
1274.3479 | 699.2141 | 644.0776 | 489.7931
1275.3479 | 697.7513 | 654.0434 | 489.6326
1276.3479 | 698.4864 | 650.6638 | 488.907
1277.3479 | 697.9662 | 642.4647 | 488.0871
1278.3479 | 700.9858 | 643.0511 | 487.6055
1279.3479 | 697.3459 | 646.4799 | 486.6471
1280.3479 | 700.2555 | 648.3144 | 488.1121
1281.3479 | 699.4346 | 659.7873 | 488.3477
1282.3479 | 700.7155 | 668.3122 | 488.5103
1283.3479 | 697.9565 | 670.0838 | 490.6842
1284.3479 | 697.7694 | 685.0792 | 491.6053
1285.3479 | 697.2974 | 688.1361 | 489.7454
1286.3479 | 689.3966 | 688.2235 | 492.0057
1287.3479 | 686.9618 | 689.9264 | 491.1043
1288.3479 | 690.5692 | 695.268 | 491.1944
1289.3479 | 700.5807 | 687.9692 | 490.5234
1290.3479 | 700.62 | 688.0004 | 492.1637
1291.3479 | 700.7497 | 684.3294 | 493.4055
1292.3479 | 694.5947 | 685.249 | 496.1207
1293.3479 | 687.4768 | 682.2536 | 493.3921
1294.3479 | 689.0752 | 686.4081 | 493.0623
1295.3479 | 689.7442 | 688.4017 | 491.6181
1296.3479 | 686.7169 | 685.6267 | 490.406
1297.3479 | 683.9438 | 688.3434 | 490.5108
1298.3479 | 692.1939 | 691.0613 | 490.647
1299.3479 | 693.8472 | 682.883 | 493.4166
1300.3479 | 690.2682 | 670.7435 | 495.2393
1301.3479 | 691.2278 | 673.5439 | 495.5504
1302.3479 | 694.9082 | 661.5113 | 495.8841
1303.3479 | 686.1918 | 650.5003 | 496.4046
1304.3479 | 684.6863 | 643.4042 | 496.4878
1305.3479 | 677.5458 | 638.9626 | 498.8378
1306.3479 | 683.3932 | 632.6367 | 499.1866
1307.3479 | 677.6665 | 623.7288 | 497.057
1308.3479 | 669.9686 | 617.273 | 495.1072
1309.3479 | 679.1426 | 622.2406 | 497.4895
1310.3479 | 685.9143 | 628.078 | 500.9411
1311.3479 | 687.8856 | 633.1171 | 501.4872
1312.3479 | 698.712 | 630.9641 | 502.0652
1313.3479 | 708.9117 | 626.44 | 499.9152
1314.3479 | 707.0777 | 622.3128 | 499.7609
1315.3479 | 711.8165 | 622.1432 | 498.4182
1316.3479 | 718.0113 | 620.893 | 500.86
1317.3479 | 720.1471 | 618.4717 | 501.0168
1318.3479 | 712.7395 | 611.5569 | 502.933
1319.3479 | 712.8274 | 604.6145 | 513.8425
1320.3479 | 711.3421 | 612.5014 | 514.9805
1321.3479 | 723.069 | 617.4719 | 515.2813
1322.3479 | 727.3288 | 622.6283 | 514.298
1323.3479 | 727.4856 | 629.4973 | 515.5057
1324.3479 | 727.1333 | 625.7943 | 519.9185
1325.3479 | 722.3384 | 621.5164 | 520.83
1326.3479 | 714.8308 | 616.3673 | 518.4045
1327.3479 | 719.7156 | 611.2713 | 518.4295
1328.3479 | 716.8335 | 607.9008 | 519.1348
1329.3479 | 708.8797 | 606.6015 | 516.5363
1330.3479 | 719.216 | 607.8964 | 518.1976
1331.3479 | 720.9513 | 612.8655 | 523.3548
1332.3479 | 728.9485 | 611.6344 | 524.3084
1333.3479 | 731.6285 | 609.6974 | 521.495
1334.3479 | 735.9917 | 613.3684 | 519.386
1335.3479 | 731.7179 | 618.6578 | 515.9403
1336.3479 | 723.7348 | 620.9212 | 513.0225
1337.3479 | 729.6627 | 629.4729 | 514.1267
1338.3479 | 740.4916 | 629.6772 | 512.7856
1339.3479 | 738.9679 | 629.1072 | 511.1297
1340.3479 | 727.8973 | 643.6365 | 512.4386
1341.3479 | 731.7133 | 649.609 | 512.1055
1342.3479 | 732.7257 | 649.5991 | 510.6196
1343.3479 | 734.7749 | 654.2377 | 512.216
1344.3479 | 727.0084 | 650.5315 | 510.4607
1345.3479 | 730.2576 | 651.0704 | 510.4367
1346.3479 | 730.6996 | 640.4869 | 509.4502
1347.3479 | 719.1187 | 634.5374 | 511.1659
1348.3479 | 713.0639 | 629.4666 | 509.7075
1349.3479 | 714.7009 | 636.8519 | 508.7984
1350.3479 | 715.8237 | 632.1632 | 506.8798
1351.3479 | 713.2718 | 624.3871 | 505.346
1352.3479 | 710.4126 | 630.0279 | 503.5931
1353.3479 | 713.4822 | 639.2518 | 505.5569
1354.3479 | 715.7077 | 633.6569 | 506.0675
1355.3479 | 720.3027 | 626.6698 | 505.6327
1356.3479 | 719.1691 | 618.4513 | 507.6472
1357.3479 | 718.2986 | 612.0931 | 509.6471
1358.3479 | 730.6373 | 611.727 | 507.4275
1359.3479 | 733.4748 | 622.6638 | 505.3188
1360.3479 | 732.3924 | 628.3994 | 505.3632
1361.3479 | 732.9107 | 621.7013 | 504.528
1362.3479 | 729.2654 | 615.2436 | 503.4978
1363.3479 | 741.0612 | 612.4115 | 504.8605
1364.3479 | 740.9705 | 606.5185 | 508.6148
1365.3479 | 744.0398 | 603.1607 | 508.5218
1366.3479 | 745.6981 | 615.7924 | 508.6376
1367.3479 | 749.8692 | 628.0821 | 509.2638
1368.3479 | 747.4202 | 644.2936 | 509.7674
1369.3479 | 744.826 | 637.3266 | 510.2602
1370.3479 | 735.2244 | 629.6754 | 514.4854
1371.3479 | 734.2575 | 639.6754 | 513.6006
1372.3479 | 737.9175 | 648.4429 | 514.9426
1373.3479 | 738.4559 | 656.848 | 514.5246
1374.3479 | 742.7162 | 664.2651 | 513.3416
1375.3479 | 745.1815 | 666.8699 | 512.8142
1376.3479 | 742.9171 | 674.0867 | 511.2949
1377.3479 | 743.1088 | 677.3185 | 512.2743
1378.3479 | 746.953 | 685.6872 | 511.9931
1379.3479 | 746.5366 | 693.2426 | 511.0007
1380.3479 | 743.6044 | 694.2753 | 511.514
1381.3479 | 739.4131 | 697.6097 | 511.5839
1382.3479 | 745.7873 | 697.9851 | 516.5879
1383.3479 | 739.9322 | 695.9112 | 516.6744
1384.3479 | 738.9245 | 701.5963 | 520.1644
1385.3479 | 737.075 | 689.3465 | 519.2118
1386.3479 | 738.4778 | 676.5076 | 520.5075
1387.3479 | 736.3421 | 666.1222 | 522.738
1388.3479 | 740.3952 | 657.2165 | 524.7468
1389.3479 | 737.4641 | 666.4176 | 522.3259
1390.3479 | 747.1617 | 670.071 | 520.1065
1391.3479 | 747.2827 | 664.4365 | 520.4449
1392.3479 | 749.1089 | 669.2446 | 522.1351
1393.3479 | 755.4091 | 678.8539 | 524.4362
1394.3479 | 747.6783 | 685.6647 | 524.1997
1395.3479 | 754.3503 | 692.5826 | 522.5483
1396.3479 | 756.0487 | 690.5984 | 520.444
1397.3479 | 754.6873 | 695.2456 | 520.4586
1398.3479 | 748.8502 | 697.7565 | 518.9101
1399.3479 | 751.7333 | 708.8043 | 517.9421
1400.3479 | 757.462 | 704.5169 | 514.3141
1401.3479 | 749.5499 | 701.3049 | 513.7768
1402.3479 | 750.7895 | 704.4515 | 512.6829
1403.3479 | 745.6313 | 709.7811 | 513.5
1404.3479 | 732.8338 | 720.674 | 515.2947
1405.3479 | 738.3016 | 712.0041 | 514.7901
1406.3479 | 740.3089 | 715.2771 | 516.8416
1407.3479 | 747.1941 | 718.825 | 514.9675
1408.3479 | 758.3952 | 723.4056 | 517.9074
1409.3479 | 762.4003 | 717.3714 | 517.9253
1410.3479 | 762.916 | 724.2777 | 519.5047
1411.3479 | 762.7124 | 722.313 | 519.7526
1412.3479 | 760.6463 | 711.0046 | 522.644
1413.3479 | 754.0676 | 715.0055 | 524.9405
1414.3479 | 757.677 | 710.2412 | 523.4341
1415.3479 | 768.1027 | 720.5556 | 525.4312
1416.3479 | 761.5021 | 709.0637 | 524.3745
1417.3479 | 762.3765 | 716.8336 | 523.5041
1418.3479 | 764.2337 | 726.0737 | 523.3988
1419.3479 | 761.7763 | 736.9084 | 523.0335
1420.3479 | 766.2371 | 724.9079 | 524.6079
1421.3479 | 770.6396 | 720.3815 | 533.5104
1422.3479 | 776.7997 | 723.4605 | 538.7431
1423.3479 | 776.2145 | 724.3255 | 542.0632
1424.3479 | 783.0404 | 723.49 | 549.6065
1425.3479 | 778.0059 | 722.5303 | 546.7798
1426.3479 | 775.7301 | 717.0075 | 543.5596
1427.3479 | 772.8249 | 716.761 | 540.3275
1428.3479 | 770.3032 | 714.4261 | 541.0065
1429.3479 | 770.899 | 710.356 | 541.0949
1430.3479 | 766.5185 | 707.9329 | 538.9678
1431.3479 | 762.6289 | 708.9942 | 537.5198
1432.3479 | 759.0394 | 707.5162 | 536.9716
1433.3479 | 761.1091 | 701.9452 | 537.9598
1434.3479 | 753.2491 | 697.274 | 540.1995
1435.3479 | 754.2922 | 689.8212 | 537.6098
1436.3479 | 748.3936 | 685.614 | 535.5856
1437.3479 | 752.1832 | 689.0933 | 533.3751
1438.3479 | 754.8192 | 691.8401 | 535.0479
1439.3479 | 746.8658 | 682.6513 | 534.7293
1440.3479 | 748.7813 | 680.9319 | 534.1909
1441.3479 | 748.8243 | 678.8138 | 538.1934
1442.3479 | 749.1108 | 673.5616 | 535.361
1443.3479 | 754.1015 | 669.7006 | 534.2354
1444.3479 | 751.716 | 667.195 | 534.7586
1445.3479 | 752.1055 | 672.3428 | 533.9481
1446.3479 | 753.2862 | 675.0959 | 531.7092
1447.3479 | 743.481 | 675.1348 | 529.2748
1448.3479 | 741.0511 | 669.9211 | 527.0576
1449.3479 | 739.0079 | 674.6396 | 534.8318
1450.3479 | 744.1916 | 671.3296 | 538.9216
1451.3479 | 744.1358 | 661.9011 | 535.8852
1452.3479 | 747.5649 | 667.6889 | 535.996
1453.3479 | 751.7933 | 679.8488 | 534.7273
1454.3479 | 754.6494 | 674.8582 | 532.5323
1455.3479 | 760.5814 | 673.6821 | 530.7473
1456.3479 | 748.1058 | 679.3389 | 528.4775
1457.3479 | 741.469 | 680.6945 | 526.6302
1458.3479 | 734.0821 | 677.0918 | 529.5277
1459.3479 | 733.0268 | 680.6957 | 528.8104
1460.3479 | 731.6796 | 683.8805 | 527.2052
1461.3479 | 730.4831 | 672.4101 | 525.3422
1462.3479 | 727.0752 | 676.2968 | 523.2785
1463.3479 | 728.1938 | 675.9843 | 522.1632
1464.3479 | 730.3888 | 686.6372 | 524.9382
1465.3479 | 738.2525 | 682.2131 | 526.0163
1466.3479 | 735.3634 | 672.6154 | 528.8802
1467.3479 | 736.6589 | 666.5912 | 527.1089
1468.3479 | 744.6399 | 663.5413 | 526.778
1469.3479 | 747.0735 | 653.5359 | 523.5328
1470.3479 | 745.0565 | 647.1381 | 524.491
1471.3479 | 752.6492 | 641.8924 | 525.2342
1472.3479 | 747.6387 | 647.8446 | 523.119
1473.3479 | 738.2408 | 636.0623 | 521.2635
1474.3479 | 738.4875 | 633.43 | 521.507
1475.3479 | 740.8614 | 631.157 | 522.304
1476.3479 | 748.0939 | 630.864 | 525.1489
1477.3479 | 744.988 | 631.6025 | 524.5858
1478.3479 | 750.7642 | 641.9333 | 523.6717
1479.3479 | 749.1029 | 648.2182 | 524.2657
1480.3479 | 748.6698 | 643.4072 | 527.3164
1481.3479 | 750.1181 | 644.5578 | 526.8434
1482.3479 | 752.4072 | 642.2511 | 525.6216
1483.3479 | 743.959 | 637.5374 | 530.5002
1484.3479 | 754.1064 | 633.0237 | 529.3911
1485.3479 | 749.0757 | 635.505 | 530.6487
1486.3479 | 749.8915 | 633.2257 | 531.6663
1487.3479 | 752.9481 | 635.1549 | 530.6951
1488.3479 | 756.196 | 630.7964 | 529.4741
1489.3479 | 757.0418 | 631.4679 | 530.845
1490.3479 | 759.557 | 630.4008 | 529.4101
1491.3479 | 758.3915 | 631.2153 | 527.0123
1492.3479 | 760.7569 | 624.8088 | 526.864
1493.3479 | 758.1247 | 626.8031 | 527.3435
1494.3479 | 754.0099 | 619.832 | 526.9992
1495.3479 | 746.9647 | 614.7821 | 526.1611
1496.3479 | 753.0537 | 608.4181 | 525.8803
1497.3479 | 754.4366 | 602.6519 | 527.1539
1498.3479 | 763.3561 | 601.9884 | 527.3927
1499.3479 | 761.0156 | 602.7081 | 528.5437
1500.3479 | 771.1737 | 599.9385 | 531.2699
1501.3479 | 769.68 | 599.9754 | 531.3621
1502.3479 | 774.8142 | 598.4322 | 529.9932
1503.3479 | 774.989 | 601.1105 | 536.5315
1504.3479 | 775.1921 | 603.4183 | 532.7003
1505.3479 | 768.0751 | 602.9364 | 530.545
1506.3479 | 773.6968 | 598.8892 | 531.2112
1507.3479 | 771.6418 | 594.826 | 530.3675
1508.3479 | 780.9921 | 592.1815 | 530.3635
1509.3479 | 781.6513 | 593.5706 | 529.6066
1510.3479 | 776.3751 | 594.94 | 527.6328
1511.3479 | 779.3894 | 593.1466 | 526.1843
1512.3479 | 778.2671 | 597.7345 | 525.1177
1513.3479 | 779.7622 | 597.1606 | 523.6536
1514.3479 | 777.0955 | 601.6607 | 523.6119
1515.3479 | 780.5721 | 599.7117 | 524.2841
1516.3479 | 777.4616 | 596.9245 | 526.0607
1517.3479 | 777.2902 | 596.1552 | 526.4759
1518.3479 | 777.8519 | 593.2009 | 527.9001
1519.3479 | 768.3887 | 589.0563 | 528.2354
1520.3479 | 755.684 | 585.2763 | 527.4723
1521.3479 | 761.2758 | 585.1765 | 528.1753
1522.3479 | 757.9418 | 588.1754 | 531.7921
1523.3479 | 762.8747 | 585.5606 | 529.2328
1524.3479 | 760.5311 | 583.4605 | 528.3606
1525.3479 | 760.5585 | 583.3529 | 525.8711
1526.3479 | 756.7519 | 583.1714 | 527.9493
1527.3479 | 754.076 | 581.8121 | 528.5035
1528.3479 | 752.5588 | 580.97 | 527.875
1529.3479 | 752.3569 | 584.1559 | 529.1985
1530.3479 | 748.9055 | 585.6155 | 529.7542
1531.3479 | 749.9655 | 587.8864 | 529.7302
1532.3479 | 756.0672 | 595.6114 | 529.9863
1533.3479 | 751.1049 | 591.798 | 530.1654
1534.3479 | 748.5908 | 589.5774 | 538.849
1535.3479 | 748.0464 | 586.6218 | 539.7287
1536.3479 | 749.2233 | 588.1155 | 537.8097
1537.3479 | 752.3165 | 587.0604 | 535.829
1538.3479 | 752.4787 | 585.4118 | 534.654
1539.3479 | 745.8204 | 584.0921 | 532.3356
1540.3479 | 745.6885 | 582.7277 | 530.9813
1541.3479 | 744.6262 | 582.5614 | 527.7886
1542.3479 | 750.311 | 581.8501 | 528.4967
1543.3479 | 748.0942 | 580.2971 | 527.9623
1544.3479 | 737.3237 | 576.0789 | 527.935
1545.3479 | 734.0683 | 573.856 | 529.2937
1546.3479 | 738.9732 | 573.2292 | 527.2152
1547.3479 | 744.0211 | 573.1749 | 528.7717
1548.3479 | 746.9246 | 571.6875 | 526.1691
1549.3479 | 751.9116 | 571.0437 | 525.3082
1550.3479 | 753.7425 | 570.4715 | 525.5294
1551.3479 | 753.9484 | 568.625 | 524.5905
1552.3479 | 750.3836 | 567.3598 | 525.6299
1553.3479 | 749.382 | 566.7078 | 527.5201
1554.3479 | 749.3979 | 565.718 | 529.2299
1555.3479 | 749.1351 | 565.8926 | 528.9625
1556.3479 | 754.4976 | 565.6311 | 533.6771
1557.3479 | 749.5121 | 565.3923 | 534.0431
1558.3479 | 746.8683 | 564.1858 | 533.8265
1559.3479 | 746.1194 | 564.093 | 535.27
1560.3479 | 753.4546 | 564.5382 | 535.2511
1561.3479 | 752.0492 | 564.9782 | 536.4669
1562.3479 | 754.8369 | 566.3127 | 535.3267
1563.3479 | 754.2038 | 565.7919 | 533.8356
1564.3479 | 752.9953 | 565.0942 | 533.2401
1565.3479 | 749.561 | 565.409 | 534.1366
1566.3479 | 757.859 | 567.7316 | 532.5374
1567.3479 | 757.0013 | 566.846 | 533.6921
1568.3479 | 754.0656 | 565.556 | 532.8599
1569.3479 | 751.6325 | 564.5055 | 530.7127
1570.3479 | 755.2873 | 564.3372 | 532.765
1571.3479 | 757.3933 | 565.153 | 532.8321
1572.3479 | 766.1936 | 564.423 | 534.5073
1573.3479 | 764.4879 | 565.4027 | 532.549
1574.3479 | 764.8049 | 564.4734 | 531.2537
1575.3479 | 754.6236 | 564.5359 | 537.3419
1576.3479 | 756.6186 | 567.9012 | 541.5346
1577.3479 | 742.5883 | 567.6396 | 541.5145
1578.3479 | 738.5484 | 566.6295 | 540.5875
1579.3479 | 746.4221 | 566.3938 | 536.9864
1580.3479 | 747.9923 | 566.0854 | 536.7155
1581.3479 | 757.3169 | 566.2736 | 540.2897
1582.3479 | 754.8573 | 566.0354 | 541.8269
1583.3479 | 755.1886 | 565.8129 | 541.1984
1584.3479 | 751.3824 | 565.0345 | 540.3237
1585.3479 | 745.3997 | 563.1877 | 537.2396
1586.3479 | 737.3795 | 560.782 | 539.4673
1587.3479 | 723.334 | 559.9247 | 542.7169
1588.3479 | 744.3024 | 559.4085 | 540.1508
1589.3479 | 733.9576 | 559.1305 | 539.1687
1590.3479 | 745.2202 | 560.4803 | 537.3863
1591.3479 | 746.8061 | 559.9294 | 536.7484
1592.3479 | 759.0341 | 559.7829 | 535.3973
1593.3479 | 758.5217 | 559.9478 | 534.2218
1594.3479 | 748.356 | 559.9286 | 536.6141
1595.3479 | 738.2222 | 557.2663 | 534.5809
1596.3479 | 742.0768 | 557.1576 | 533.8509
1597.3479 | 741.5356 | 556.6542 | 533.3162
1598.3479 | 745.5115 | 557.7922 | 531.9494
1599.3479 | 743.0026 | 558.3023 | 530.9981
1600.3479 | 735.0461 | 559.3243 | 530.6175
1601.3479 | 730.4215 | 561.2703 | 532.8898
1602.3479 | 734.6462 | 564.0534 | 530.7389
1603.3479 | 731.8981 | 563.5615 | 529.7116
1604.3479 | 726.0546 | 562.6322 | 528.8555
1605.3479 | 735.8399 | 561.7871 | 527.6653
1606.3479 | 736.5505 | 561.8713 | 526.5661
1607.3479 | 743.7868 | 561.8521 | 524.2264
1608.3479 | 742.1831 | 560.4289 | 524.186
1609.3479 | 735.9052 | 559.9171 | 521.8173
1610.3479 | 728.6595 | 560.3532 | 521.0669
1611.3479 | 722.3465 | 559.469 | 522.3387
1612.3479 | 724.1448 | 559.4784 | 522.4997
1613.3479 | 734.2864 | 560.4965 | 524.8142
1614.3479 | 742.416 | 559.1789 | 523.3445
1615.3479 | 749.5582 | 560.0224 | 521.638
1616.3479 | 753.0097 | 562.1595 | 521.9291
1617.3635 | 748.2989 | 564.8015 | 523.2754
1618.3479 | 750.2151 | 562.1257 | 523.5455
1619.3479 | 749.8318 | 560.7195 | 522.7508
1620.3479 | 760.1782 | 560.9117 | 523.9084
1621.3479 | 746.2916 | 560.131 | 524.4558
1622.3479 | 745.0754 | 559.1221 | 522.6736
1623.3479 | 745.4813 | 559.2657 | 523.5467
1624.3479 | 756.1795 | 559.7096 | 522.0845
1625.3479 | 744.3558 | 560.9754 | 526.1472
1626.3479 | 741.3151 | 561.7078 | 525.716
1627.3479 | 731.7703 | 560.4711 | 526.5878
1628.3479 | 717.1888 | 560.2165 | 525.0571
1629.3479 | 714.7503 | 560.3521 | 522.9464
1630.3479 | 720.8904 | 559.7126 | 522.3052
1631.3479 | 707.8176 | 559.7279 | 520.7961
1632.3479 | 702.8347 | 559.6987 | 524.2202
1633.3479 | 715.298 | 559.025 | 523.1396
1634.3479 | 726.1309 | 558.3954 | 521.0081
1635.3479 | 728.0848 | 558.235 | 520.0669
1636.3479 | 729.485 | 558.8802 | 519.0109
1637.3479 | 728.6339 | 557.6281 | 518.8374
1638.3479 | 730.9079 | 556.8233 | 519.9792
1639.3479 | 735.7156 | 557.4507 | 521.0357
1640.3479 | 741.1731 | 556.6305 | 520.7388
1641.3479 | 738.9354 | 555.395 | 521.3059
1642.3479 | 740.3081 | 555.4138 | 519.7032
1643.3479 | 739.8716 | 555.221 | 518.613
1644.3479 | 732.1562 | 555.2586 | 519.1368
1645.3479 | 741.9808 | 554.0307 | 521.3626
1646.3479 | 739.1902 | 553.7337 | 521.5078
1647.3635 | 736.4309 | 553.0837 | 522.7744
1648.3479 | 732.3629 | 552.7999 | 521.7874
1649.3479 | 727.7843 | 552.6467 | 522.9409
1650.3479 | 733.5521 | 552.3609 | 526.9202
1651.3479 | 739.7019 | 554.4507 | 528.6309
1652.3479 | 738.3623 | 555.3862 | 528.3828
1653.3479 | 744.2398 | 554.085 | 526.714
1654.3479 | 749.1731 | 554.091 | 525.8351
1655.3479 | 737.6388 | 556.102 | 526.9876
1656.3479 | 745.1288 | 556.5546 | 525.8439
1657.3479 | 743.081 | 556.5624 | 525.2073
1658.3479 | 743.7516 | 556.7548 | 524.3626
1659.3479 | 731.4038 | 556.6027 | 522.4963
1660.3479 | 727.9185 | 556.7445 | 521.7949
1661.3479 | 732.0233 | 556.3064 | 520.3958
1662.3479 | 723.9542 | 556.8288 | 523.0985
1663.3479 | 715.0548 | 556.602 | 522.3753
1664.3479 | 698.6734 | 556.4539 | 522.5669
1665.3479 | 695.7122 | 557.099 | 522.558
1666.3479 | 695.2049 | 558.1171 | 520.6449
1667.3479 | 704.2844 | 556.5321 | 519.4058
1668.3479 | 700.3493 | 555.1007 | 520.9929
1669.3479 | 689.4074 | 552.1352 | 523.6022
1670.3479 | 692.0602 | 550.98 | 527.4928
1671.3479 | 700.8293 | 551.2026 | 526.7351
1672.3479 | 698.1456 | 551.1265 | 526.1222
1673.3479 | 689.9345 | 551.3242 | 523.3826
1674.3479 | 685.6274 | 551.068 | 522.8013
1675.3479 | 687.6431 | 551.1764 | 521.5969
1676.3479 | 691.2406 | 550.901 | 519.2037
1677.3479 | 685.7321 | 549.8394 | 519.0096
1678.3479 | 693.3904 | 548.0514 | 519.7429
1679.3479 | 684.7592 | 546.468 | 518.9596
1680.3479 | 683.7188 | 544.8679 | 519.6381
1681.3479 | 674.8471 | 543.4239 | 519.4694
1682.3479 | 677.4093 | 542.8519 | 520.1815
1683.3479 | 677.5882 | 544.0243 | 519.5096
1684.3479 | 678.7527 | 545.8831 | 518.3439
1685.3479 | 680.4555 | 546.3021 | 518.4245
1686.3479 | 685.7526 | 547.9301 | 516.9325
1687.3479 | 685.064 | 547.7556 | 516.5988
1688.3479 | 681.048 | 547.7124 | 517.0437
1689.3479 | 678.0663 | 547.5337 | 517.3316
1690.3479 | 670.5572 | 547.7751 | 516.5029
1691.3479 | 671.9029 | 548.6561 | 517.4407
1692.3479 | 667.2136 | 548.9771 | 517.9995
1693.3479 | 674.4058 | 549.6253 | 516.1463
1694.3479 | 678.399 | 548.791 | 514.3149
1695.3479 | 672.1956 | 548.9929 | 516.0908
1696.3479 | 678.5923 | 549.3656 | 513.7837
1697.3479 | 676.1575 | 548.3958 | 512.6801
1698.3479 | 671.693 | 549.3665 | 519.3448
1699.3479 | 668.8065 | 548.682 | 523.4151
1700.3479 | 682.4997 | 549.9493 | 522.3976
1701.3479 | 689.9282 | 549.1597 | 521.2712
1702.3479 | 703.2718 | 548.6426 | 518.6988
1703.3479 | 702.2745 | 548.9929 | 517.4341
1704.3479 | 703.05 | 549.4956 | 518.0962
1705.3479 | 694.5077 | 548.2741 | 518.5121
1706.3479 | 685.0544 | 546.7968 | 518.9479
1707.3479 | 686.9855 | 545.6877 | 519.3563
1708.3479 | 682.3292 | 544.1155 | 519.3238
1709.3479 | 676.8395 | 541.7294 | 517.6277
1710.3479 | 692.9493 | 539.6483 | 517.1588
1711.3479 | 692.5586 | 539.5035 | 515.2687
1712.3479 | 684.7662 | 539.0776 | 513.3223
1713.3479 | 680.3579 | 538.6649 | 513.2728
1714.3479 | 669.7611 | 538.7435 | 514.3753
1715.3479 | 671.8035 | 540.3953 | 515.469
1716.3479 | 675.4329 | 540.5672 | 515.2272
1717.3479 | 665.016 | 538.7085 | 512.9601
1718.3479 | 657.6716 | 538.9343 | 512.9349
1719.3479 | 667.5117 | 539.9993 | 511.1447
1720.3479 | 681.4565 | 541.096 | 512.3153
1721.3479 | 686.2297 | 542.5421 | 512.3886
1722.3479 | 685.1606 | 542.9093 | 510.7022
1723.3479 | 690.8842 | 543.8316 | 507.9816
1724.3479 | 699.8935 | 543.8448 | 507.8019
1725.3479 | 706.0756 | 542.9825 | 505.2394
1726.3479 | 708.3799 | 543.7075 | 505.0956
1727.3479 | 718.0149 | 543.5977 | 503.5866
1728.3479 | 718.5714 | 542.4324 | 502.2983
1729.3479 | 710.1402 | 541.4062 | 504.6284
1730.3479 | 698.9179 | 541.9081 | 503.3598
1731.3479 | 686.9736 | 541.851 | 504.7583
1732.3479 | 681.5148 | 542.0332 | 504.9514
1733.3479 | 682.5917 | 542.6399 | 505.7144
1734.3479 | 676.0931 | 542.0968 | 506.8526
1735.3479 | 677.8213 | 542.9038 | 508.3859
1736.3479 | 672.7861 | 543.9017 | 509.2543
1737.3479 | 672.1973 | 544.7304 | 510.9381
1738.3479 | 673.5255 | 545.3947 | 511.6177
1739.3479 | 667.2697 | 543.3187 | 510.8749
1740.3479 | 662.3504 | 539.8132 | 511.7755
1741.3479 | 660.1571 | 538.5338 | 513.5804
1742.3479 | 659.653 | 538.0693 | 515.4258
1743.3479 | 659.856 | 538.9682 | 514.8378
1744.3479 | 671.0102 | 539.8105 | 513.3785
1745.3479 | 668.5579 | 540.7774 | 511.2633
1746.3479 | 662.0571 | 540.2644 | 513.7179
1747.3479 | 655.144 | 539.6373 | 511.7487
1748.3479 | 647.8814 | 539.8068 | 511.7557
1749.3479 | 640.8146 | 538.773 | 512.1896
1750.3479 | 635.2241 | 538.1646 | 512.6107
1751.3479 | 632.5108 | 537.5983 | 510.6412
1752.3479 | 628.2324 | 536.287 | 510.3573
1753.3479 | 629.9231 | 537.0503 | 514.187
1754.3479 | 625.9861 | 537.0139 | 512.3018
1755.3479 | 629.4737 | 539.1437 | 512.2008
1756.3479 | 633.3278 | 539.6778 | 510.6893
1757.3479 | 641.2507 | 539.2378 | 510.232
1758.3479 | 645.5537 | 538.8374 | 508.625
1759.3479 | 652.7382 | 538.2569 | 506.6846
1760.3479 | 655.1208 | 539.7847 | 506.9115
1761.3479 | 659.9697 | 539.9791 | 505.7517
1762.3479 | 662.7309 | 540.0498 | 503.6949
1763.3479 | 654.8111 | 540.2376 | 503.8351
1764.3479 | 658.709 | 540.3836 | 502.466
1765.3479 | 655.5252 | 539.6963 | 501.5692
1766.3479 | 649.8911 | 540.5813 | 500.729
1767.3479 | 645.5263 | 541.198 | 500.1899
1768.3479 | 646.3883 | 541.7648 | 501.7584
1769.3479 | 642.3889 | 541.7222 | 500.4339
1770.3479 | 648.0924 | 542.5911 | 500.5335
1771.3479 | 651.3292 | 543.5553 | 502.0294
1772.3479 | 644.0642 | 543.3156 | 502.9154
1773.3479 | 647.5819 | 540.9256 | 503.8182
1774.3479 | 648.0338 | 541.2673 | 507.5973
1775.3479 | 645.386 | 540.4811 | 505.896
1776.3479 | 644.896 | 541.0258 | 505.6289
1777.3479 | 639.158 | 540.5377 | 505.1059
1778.3479 | 643.5013 | 540.7193 | 504.9424
1779.3479 | 641.434 | 542.5704 | 503.287
1780.3479 | 639.4673 | 542.4247 | 505.256
1781.3479 | 638.2792 | 541.4632 | 504.1892
1782.3479 | 643.6431 | 540.9181 | 504.4506
1783.3479 | 640.4309 | 540.376 | 506.2659
1784.3479 | 635.9351 | 540.3988 | 505.9047
1785.3479 | 631.2246 | 540.5062 | 505.1802
1786.3479 | 626.3282 | 540.0612 | 507.3653
1787.3479 | 623.0914 | 539.7961 | 506.7402
1788.3479 | 625.5185 | 540.4925 | 508.5266
1789.3479 | 623.0392 | 540.2012 | 509.2527
1790.3479 | 620.9504 | 541.0396 | 509.2922
1791.3479 | 619.8889 | 541.1198 | 509.3105
1792.3479 | 617.4349 | 541.971 | 507.4373
1793.3479 | 618.8356 | 541.3941 | 505.9606
1794.3479 | 613.7666 | 540.7681 | 505.5394
1795.3479 | 613.4712 | 539.7901 | 503.7947
1796.3479 | 616.6016 | 540.5276 | 501.7826
1797.3635 | 618.8608 | 542.2922 | 500.8502
1798.3479 | 622.65 | 543.0668 | 499.3346
1799.3479 | 620.0719 | 542.612 | 498.7441
1800.3479 | 618.552 | 542.2289 | 496.4402
1801.3479 | 617.1259 | 542.8767 | 495.0614
1802.3479 | 617.8668 | 543.2151 | 493.989
1803.3479 | 613.9931 | 542.7604 | 493.9075
1804.3479 | 618.4229 | 543.5958 | 493.7308
1805.3479 | 616.8565 | 543.3449 | 492.6263
1806.3479 | 617.6267 | 541.8358 | 491.343
1807.3479 | 618.0387 | 541.4759 | 491.7316
1808.3479 | 614.3568 | 541.0727 | 491.2843
1809.3479 | 614.9778 | 540.5168 | 490.7141
1810.3479 | 613.4045 | 540.9525 | 489.7729
1811.3479 | 611.5509 | 539.783 | 487.8642
1812.3479 | 609.8939 | 540.5589 | 486.5985
1813.3479 | 608.9764 | 541.5759 | 486.1754
1814.3479 | 610.0101 | 541.3757 | 486.3199
1815.3479 | 607.6451 | 540.9356 | 485.401
1816.3479 | 611.4635 | 541.3532 | 484.3248
1817.3479 | 610.9589 | 541.7283 | 484.204
1818.3479 | 609.6703 | 540.4465 | 484.4419
1819.3479 | 609.202 | 539.1763 | 484.3557
1820.3479 | 622.2294 | 540.1577 | 485.2256
1821.3479 | 627.9848 | 538.47 | 487.208
1822.3479 | 636.1585 | 538.215 | 491.2251
1823.3479 | 634.4608 | 538.2659 | 492.6804
1824.3479 | 631.481 | 539.772 | 493.0179
1825.3479 | 628.6581 | 538.1935 | 497.0945
1826.3479 | 628.6004 | 539.6195 | 496.3044
1827.3479 | 623.8217 | 540.2902 | 495.0991
1828.3479 | 622.5962 | 539.7215 | 494.8676
1829.3479 | 625.5623 | 538.9694 | 493.4343
1830.3479 | 624.4175 | 537.8257 | 492.4621
1831.3479 | 619.1965 | 538.4963 | 492.7666
1832.3479 | 618.0165 | 537.6176 | 497.5631
1833.3479 | 621.5234 | 539.45 | 497.7684
1834.3479 | 624 | 538.3953 | 496.6591
1835.3479 | 627.6411 | 536.2874 | 499.6388
1836.3479 | 624.7986 | 536.0147 | 499.2511
1837.3479 | 619.7833 | 536.5932 | 498.5161
1838.3479 | 613.1954 | 536.5868 | 498.2994
1839.3479 | 613.1246 | 536.6126 | 498.409
1840.3479 | 611.3236 | 535.3268 | 498.1977
1841.3479 | 608.7072 | 535.0864 | 498.8872
1842.3479 | 611.431 | 535.0878 | 496.8091
1843.3479 | 607.7759 | 535.4951 | 495.5119
1844.3479 | 606.3569 | 534.2433 | 496.0632
1845.3479 | 602.961 | 532.9991 | 496.6303
1846.3479 | 601.4352 | 533.1602 | 495.4351
1847.3479 | 602.509 | 534.409 | 496.9856
1848.3479 | 621.5657 | 529.784 | 496.8848
1849.3479 | 629.4141 | 528.2821 | 496.5058
1850.3479 | 633.0609 | 525.9493 | 494.5147
1851.3479 | 638.7687 | 526.3916 | 492.8576
1852.3479 | 641.8965 | 527.1312 | 492.6004
1853.3479 | 635.6747 | 528.3813 | 492.7734
1854.3479 | 631.4105 | 530.2893 | 491.2603
1855.3479 | 626.533 | 531.683 | 491.4844
1856.3479 | 622.9445 | 530.6745 | 491.7693
1857.3479 | 618.1386 | 532.9656 | 491.0553
1858.3479 | 625.3866 | 533.0123 | 490.0552
1859.3479 | 623.6104 | 534.0063 | 489.6575
1860.3479 | 621.956 | 532.8446 | 489.9445
1861.3479 | 616.8284 | 534.6072 | 490.3906
1862.3479 | 610.6525 | 536.3392 | 490.0934
1863.3479 | 615.2527 | 536.6108 | 489.822
1864.3479 | 611.0821 | 535.7211 | 489.2892
1865.3479 | 607.0477 | 536.2839 | 489.251
1866.3479 | 613.9438 | 537.4582 | 489.5676
1867.3479 | 616.1146 | 535.5239 | 488.8489
1868.3479 | 627.9038 | 533.8471 | 488.2588
1869.3479 | 625.4419 | 532.4682 | 488.0698
1870.3479 | 626.0963 | 534.1167 | 490.4344
1871.3479 | 632.3616 | 534.599 | 489.7775
1872.3479 | 638.2436 | 535.238 | 489.4004
1873.3479 | 643.582 | 533.3714 | 489.0872
1874.3479 | 650.7753 | 530.3176 | 487.4391
1875.3479 | 667.0401 | 529.3909 | 489.9496
1876.3479 | 661.64 | 529.4822 | 489.4448
1877.3479 | 652.2028 | 530.9107 | 493.2938
1878.3479 | 648.3496 | 532.0134 | 492.1833
1879.3479 | 668.2466 | 532.7588 | 493.0867
1880.3479 | 664.9598 | 532.6916 | 491.5282
1881.3479 | 658.3212 | 531.1433 | 490.6098
1882.3479 | 652.8709 | 529.2903 | 491.2851
1883.3479 | 661.6257 | 529.4982 | 491.0817
1884.3479 | 666.9024 | 529.4452 | 490.3702
1885.3479 | 661.1666 | 529.1228 | 488.7674
1886.3479 | 655.9032 | 527.9213 | 488.021
1887.3479 | 652.3339 | 530.1182 | 486.6946
1888.3479 | 662.7215 | 533.8677 | 486.0489
1889.3479 | 661.7988 | 534.9801 | 485.9496
1890.3479 | 659.9922 | 534.9718 | 485.2964
1891.3479 | 661.2641 | 537.7597 | 484.9354
1892.3479 | 656.8392 | 539.1838 | 484.9386
1893.3479 | 662.5713 | 539.5499 | 483.5736
1894.3479 | 656.2915 | 541.5057 | 482.8687
1895.3479 | 650.0098 | 542.1768 | 483.0237
1896.3479 | 642.7952 | 542.0309 | 481.9254
1897.3479 | 636.095 | 541.8525 | 480.8019
1898.3479 | 640.7397 | 542.2478 | 480.9977
1899.3479 | 634.5514 | 541.6185 | 479.5681
1900.3479 | 641.6194 | 539.379 | 478.4752
1901.3479 | 659.8475 | 538.1492 | 477.5526
1902.3479 | 649.8319 | 538.6566 | 477.0266
1903.3479 | 643.7364 | 538.7112 | 475.8489
1904.3479 | 636.2874 | 538.1408 | 474.173
1905.3479 | 632.8165 | 538.8852 | 473.281
1906.3479 | 633.3633 | 539.0869 | 473.0388
1907.3479 | 634.6226 | 539.8585 | 473.1719
1908.3479 | 637.911 | 538.7835 | 472.823
1909.3479 | 630.3924 | 538.2463 | 472.5109
1910.3479 | 635.0904 | 538.1789 | 471.5193
1911.3479 | 631.6224 | 537.4326 | 470.9568
1912.3479 | 626.5055 | 537.0231 | 470.934
1913.3479 | 619.1656 | 535.7569 | 471.1014
1914.3479 | 622.6937 | 533.6043 | 470.6789
1915.3479 | 627.4052 | 533.6872 | 470.0275
1916.3479 | 630.9806 | 530.9582 | 469.0594
1917.3479 | 630.9871 | 532.6866 | 468.4144
1918.3479 | 633.4931 | 533.302 | 468.0684
1919.3479 | 629.8828 | 534.8601 | 468.085
1920.3479 | 628.6977 | 534.3789 | 468.1787
1921.3479 | 633.8386 | 532.5888 | 467.6149
1922.3479 | 638.5308 | 530.3328 | 467.492
1923.3479 | 641.2198 | 530.2976 | 467.6304
1924.3479 | 646.1704 | 531.7965 | 467.7861
1925.3479 | 651.7599 | 533.6487 | 468.6566
1926.3479 | 645.8318 | 534.4149 | 472.1468
1927.3479 | 637.0165 | 535.5078 | 472.7371
1928.3479 | 633.2762 | 535.4792 | 474.0707
1929.3479 | 630.216 | 536.5504 | 473.7523
1930.3479 | 626.2259 | 535.6193 | 472.5548
1931.3479 | 621.4285 | 535.1204 | 473.4496
1932.3479 | 616.9482 | 535.5051 | 472.7381
1933.3479 | 615.2669 | 535.5927 | 472.7871
1934.3479 | 612.6736 | 537.5436 | 471.5463
1935.3479 | 609.6865 | 537.0215 | 471.5252
1936.3479 | 614.4149 | 535.9696 | 471.9475
1937.3479 | 620.1055 | 535.0995 | 472.6141
1938.3479 | 620.2958 | 534.7128 | 473.4556
1939.3479 | 633.9809 | 531.7069 | 473.0487
1940.3479 | 651.5166 | 531.069 | 472.4355
1941.3479 | 651.8182 | 531.9726 | 472.1558
1942.3479 | 655.03 | 532.7832 | 474.0134
1943.3479 | 652.8822 | 532.6115 | 473.6985
1944.3479 | 657.2292 | 532.0415 | 472.9199
1945.3479 | 654.8001 | 533.1864 | 474.3458
1946.3479 | 647.6264 | 534.1121 | 474.2677
1947.3479 | 644.8709 | 536.1252 | 474.0636
1948.3479 | 644.0638 | 536.0744 | 472.5055
1949.3479 | 647.4328 | 537.6693 | 472.559
1950.3479 | 642.2788 | 536.0885 | 471.2786
1951.3479 | 637.5833 | 536.5136 | 471.4194
1952.3479 | 643.0832 | 537.2337 | 471.2434
1953.3479 | 641.7601 | 536.3999 | 470.9908
1954.3479 | 647.65 | 537.2417 | 471.3614
1955.3479 | 648.9798 | 538.1028 | 471.4204
1956.3479 | 645.9123 | 539.2471 | 470.1796
1957.3479 | 640.5681 | 538.0483 | 471.3845
1958.3479 | 637.8164 | 538.219 | 473.4388
1959.3479 | 634.5912 | 537.8117 | 471.6391
1960.3479 | 634.5572 | 538.3823 | 471.0848
1961.3479 | 636.1324 | 539.4015 | 470.338
1962.3479 | 635.2803 | 540.7444 | 470.3187
1963.3479 | 629.5282 | 541.5491 | 473.8712
1964.3479 | 622.4063 | 540.6398 | 473.6999
1965.3479 | 626.8805 | 539.5094 | 472.3208
1966.3479 | 629.9383 | 540.8336 | 474.4866
1967.3479 | 625.8038 | 539.4882 | 474.4715
1968.3479 | 623.3461 | 539.1438 | 472.912
1969.3479 | 622.3351 | 537.804 | 473.0229
1970.3479 | 633.0797 | 538.5563 | 473.8587
1971.3479 | 635.7074 | 536.507 | 472.8284
1972.3479 | 642.3577 | 535.1623 | 472.6539
1973.3479 | 634.1271 | 535.7093 | 474.4097
1974.3479 | 632.0811 | 537.7656 | 474.8957
1975.3479 | 631.8882 | 537.1228 | 473.9992
1976.3479 | 626.1522 | 539.0691 | 475.2645
1977.3479 | 629.1547 | 539.7685 | 474.9968
1978.3479 | 625.7426 | 539.1732 | 475.403
1979.3479 | 626.0599 | 540.3077 | 474.5556
1980.3479 | 626.1652 | 540.5558 | 475.375
1981.3479 | 622.4291 | 541.3959 | 474.5494
1982.3479 | 617.2679 | 540.6514 | 474.3591
1983.3479 | 612.5498 | 539.3796 | 473.5596
1984.3479 | 610.5267 | 539.9534 | 473.2058
1985.3479 | 622.0498 | 538.4639 | 472.9117
1986.3479 | 616.8935 | 540.3074 | 473.4153
1987.3479 | 618.6902 | 540.6166 | 472.4056
1988.3479 | 621.2845 | 538.6968 | 473.0433
1989.3479 | 624.2193 | 539.0927 | 473.8073
1990.3479 | 622.1433 | 540.037 | 473.9733
1991.3479 | 622.9391 | 540.8517 | 473.7833
1992.3479 | 616.8387 | 539.6913 | 473.7016
1993.3479 | 610.7949 | 539.3067 | 472.5542
1994.3479 | 604.9307 | 539.2796 | 471.7114
1995.3479 | 602.8481 | 538.8617 | 471.7345
1996.3479 | 598.5811 | 538.5801 | 472.4861
1997.3479 | 595.1869 | 538.5093 | 471.4497
1998.3479 | 593.2906 | 537.5386 | 470.4474
1999.3479 | 590.6373 | 537.1357 | 471.159
2000.3479 | 588.219 | 539.765 | 471.762
2001.3479 | 583.8855 | 541.58 | 472.1924
2002.3479 | 581.573 | 540.8427 | 472.2957
2003.3479 | 579.928 | 539.4709 | 471.0321
2004.3479 | 579.4957 | 539.9895 | 475.7301
2005.3479 | 577.3798 | 540.0161 | 476.2982
2006.3479 | 575.2055 | 540.8918 | 475.5537
2007.3479 | 572.1324 | 540.6963 | 474.1505
2008.3479 | 569.0541 | 540.4812 | 473.445
2009.3479 | 567.3916 | 541.22 | 472.986
2010.3479 | 567.1323 | 541.3489 | 473.5149
2011.3479 | 565.5132 | 540.463 | 473.2132
2012.3479 | 564.2031 | 541.2665 | 472.3328
2013.3479 | 564.8629 | 542.632 | 473.0312
2014.3479 | 563.3948 | 543.6167 | 473.1536
2015.3479 | 563.2828 | 544.9096 | 472.9027
2016.3479 | 563.4641 | 543.9403 | 471.4819
2017.3479 | 561.9411 | 543.8286 | 471.2455
2018.3479 | 561.122 | 543.5284 | 470.5933
2019.3479 | 559.5179 | 545.0296 | 471.1552
2020.3479 | 558.4387 | 545.7084 | 470.6007
2021.3479 | 557.3921 | 544.0859 | 470.6186
2022.3479 | 556.0263 | 543.4589 | 470.1979
2023.3479 | 556.218 | 543.5989 | 471.0805
2024.3479 | 556.2663 | 542.3384 | 471.8716
2025.3479 | 555.2099 | 541.5784 | 471.6161
2026.3479 | 554.9378 | 543.0043 | 471.7879
2027.3479 | 554.1336 | 542.912 | 470.6293
2028.3479 | 553.7543 | 541.7798 | 471.1025
2029.3479 | 552.7853 | 541.2725 | 470.5554
2030.3479 | 552.8274 | 541.1598 | 471.2177
2031.3479 | 553.1414 | 541.6305 | 472.2511
2032.3479 | 551.4698 | 540.7027 | 471.59
2033.3479 | 551.9592 | 540.7721 | 471.432
2034.3479 | 551.0335 | 541.4355 | 473.907
2035.3479 | 550.3026 | 541.3525 | 473.3739
2036.3479 | 548.8292 | 539.6296 | 472.3988
2037.3479 | 549.2932 | 538.921 | 472.7352
2038.3479 | 548.7276 | 539.5214 | 472.6338
2039.3479 | 548.097 | 538.2722 | 471.8509
2040.3479 | 546.131 | 539.3589 | 470.3605
2041.3479 | 545.1653 | 539.8098 | 469.6113
2042.3479 | 545.1491 | 538.3591 | 469.69
2043.3479 | 546.1848 | 539.8062 | 468.8937
2044.3479 | 544.8982 | 540.0234 | 469.5389
2045.3479 | 543.8207 | 541.2111 | 469.1882
2046.3479 | 543.5744 | 540.4491 | 468.9771
2047.3479 | 543.0917 | 539.9595 | 467.7867
2048.3479 | 542.4204 | 539.3646 | 467.0628
2049.3479 | 544.4877 | 540.2794 | 466.0302
2050.3479 | 544.1073 | 538.7723 | 465.8002
2051.3479 | 543.793 | 539.2067 | 465.4228
2052.3479 | 541.9015 | 536.5752 | 465.6446
2053.3479 | 542.2904 | 536.2451 | 467.2145
2054.3479 | 543.1211 | 537.4201 | 466.5762
2055.3479 | 543.4754 | 535.2232 | 466.5207
2056.3479 | 543.6103 | 535.4801 | 466.0229
2057.3479 | 542.803 | 533.0012 | 464.8661
2058.3479 | 540.7605 | 533.9921 | 464.4702
2059.3479 | 539.8439 | 535.188 | 464.3657
2060.3479 | 538.7468 | 534.0398 | 465.1839
2061.3479 | 536.6437 | 533.5784 | 467.756
2062.3479 | 535.7054 | 535.9547 | 467.0007
2063.3479 | 533.8233 | 535.5742 | 467.8821
2064.3479 | 533.0095 | 535.4557 | 467.5054
2065.3479 | 533.3043 | 535.1732 | 466.9899
2066.3479 | 534.4157 | 534.7132 | 465.9939
2067.3479 | 536.8203 | 532.0347 | 465.0052
2068.3479 | 537.4314 | 532.2916 | 464.1007
2069.3479 | 537.3625 | 533.108 | 463.7752
2070.3479 | 537.2012 | 534.8977 | 463.5514
2071.3479 | 536.9016 | 533.4479 | 463.4804
2072.3479 | 538.0161 | 532.1252 | 463.162
2073.3479 | 538.594 | 533.4197 | 463.2539
2074.3479 | 538.047 | 532.1151 | 462.8033
2075.3479 | 538.4356 | 532.1737 | 462.3088
2076.3479 | 537.6257 | 532.236 | 462.2717
2077.3479 | 537.0609 | 531.8368 | 461.5458
2078.3479 | 536.7032 | 533.001 | 461.4341
2079.3479 | 536.4823 | 532.6856 | 460.959
2080.3479 | 535.7509 | 531.8106 | 461.1855
2081.3479 | 535.7383 | 530.4795 | 461.7657
2082.3479 | 535.5772 | 532.0178 | 461.4909
2083.3479 | 535.3252 | 531.6568 | 462.1836
2084.3479 | 534.8915 | 530.4894 | 464.0645
2085.3479 | 533.8675 | 532.0848 | 463.4883
2086.3479 | 533.7066 | 530.8408 | 463.6405
2087.3479 | 533.5993 | 530.6273 | 464.1344
2088.3479 | 533.7627 | 532.4045 | 465.2542
2089.3479 | 534.4038 | 530.9506 | 464.5108
2090.3479 | 535.0024 | 533.3098 | 463.5748
2091.3479 | 535.5241 | 534.3328 | 463.1769
2092.3479 | 534.6888 | 535.9067 | 462.4792
2093.3479 | 534.1091 | 536.2452 | 461.5088
2094.3479 | 533.6777 | 537.1002 | 460.6051
2095.3479 | 534.1184 | 537.1769 | 459.9672
2096.3479 | 534.4894 | 538.3699 | 459.8409
2097.3635 | 533.4745 | 537.8304 | 459.7951
2098.3479 | 533.2564 | 540.3003 | 459.3767
2099.3479 | 532.2048 | 542.2568 | 458.728
2100.3479 | 530.5533 | 541.0526 | 458.3777
2101.3479 | 529.4568 | 539.9171 | 459.6652
2102.3479 | 527.8832 | 538.5447 | 458.449
2103.3479 | 527.7466 | 538.113 | 457.6073
2104.3479 | 528.7117 | 538.0044 | 457.9021
2105.3479 | 528.7415 | 538.2766 | 457.7716
2106.3479 | 528.4229 | 539.183 | 457.5231
2107.3479 | 527.2465 | 539.3509 | 457.5204
2108.3479 | 526.6808 | 536.043 | 456.0443
2109.3479 | 527.0005 | 536.7388 | 455.6245
2110.3479 | 526.9146 | 537.192 | 455.9908
2111.3479 | 526.9099 | 536.7832 | 457.3671
2112.3479 | 527.4227 | 536.0811 | 456.6498
2113.3479 | 527.6643 | 536.3984 | 456.4811
2114.3479 | 526.1663 | 536.048 | 456.5401
2115.3479 | 525.6006 | 535.8299 | 456.5773
2116.3479 | 525.6782 | 534.9672 | 456.7338
2117.3479 | 525.6598 | 535.6052 | 457.0614
2118.3479 | 525.7977 | 535.7449 | 456.9059
2119.3479 | 525.2861 | 536.1241 | 456.5927
2120.3479 | 525.7741 | 537.0012 | 457.2896
2121.3479 | 525.7264 | 536.8532 | 456.5353
2122.3479 | 524.9803 | 536.0018 | 455.7173
2123.3479 | 524.7048 | 534.0004 | 455.3627
2124.3479 | 523.7978 | 532.7467 | 455.353
2125.3479 | 523.6615 | 532.5589 | 455.3371
2126.3479 | 525.0047 | 532.3118 | 455.124
2127.3479 | 526.2658 | 533.9238 | 455.1697
2128.3479 | 526.875 | 534.097 | 454.801
2129.3479 | 527.0279 | 533.4621 | 454.3055
2130.3479 | 527.1847 | 533.3623 | 455.7547
2131.3479 | 527.2481 | 536.5994 | 457.3458
2132.3479 | 528.9249 | 536.9143 | 458.4462
2133.3479 | 530.2673 | 537.9612 | 458.4213
2134.3479 | 529.9458 | 540.9837 | 458.9428
2135.3479 | 531.3 | 543.3435 | 459.2044
2136.3479 | 532.5014 | 544.1329 | 458.9888
2137.3479 | 533.0067 | 546.7801 | 459.9344
2138.3479 | 534.6946 | 547.7034 | 460.8081
2139.3479 | 535.5909 | 550.2437 | 461.1426
2140.3479 | 537.4109 | 554.1695 | 461.0086
2141.3479 | 538.2833 | 557.0293 | 461.8076
2142.3479 | 538.5252 | 556.3255 | 461.8647
2143.3479 | 539.6291 | 556.8316 | 462.0417
2144.3479 | 540.8914 | 557.2537 | 461.9709
2145.3479 | 541.7791 | 557.7367 | 461.925
2146.3479 | 542.1476 | 559.3251 | 462.8069
2147.3479 | 541.9423 | 562.4008 | 465.4153
2148.3479 | 541.7206 | 560.5711 | 464.7217
2149.3479 | 543.1132 | 563.1369 | 465.1214
2150.3479 | 545.1124 | 562.5118 | 465.1671
2151.3479 | 545.8396 | 563.2454 | 466.6693
2152.3479 | 545.253 | 562.7281 | 467.4351
2153.3479 | 545.9932 | 564.5237 | 468.0871
2154.3479 | 544.1695 | 565.2408 | 468.0122
2155.3479 | 544.5773 | 564.9807 | 467.3653
2156.3479 | 543.4389 | 564.5646 | 466.4678
2157.3479 | 543.6011 | 566.5806 | 465.9394
2158.3479 | 542.9832 | 566.1147 | 465.8419
2159.3479 | 542.7648 | 565.5283 | 464.8885
2160.3479 | 543.2975 | 566.0979 | 464.977
2161.3479 | 543.579 | 566.9142 | 465.2959
2162.3479 | 543.3627 | 567.9885 | 464.5043
2163.3479 | 545.0527 | 569.1555 | 464.4957
2164.3479 | 544.7333 | 568.9417 | 464.2452
2165.3479 | 543.6856 | 568.8056 | 464.9829
2166.3479 | 543.3485 | 568.1145 | 465.2066
2167.3479 | 542.6872 | 569.0898 | 464.9383
2168.3479 | 542.7877 | 571.1033 | 464.8066
2169.3479 | 542.1395 | 571.7756 | 465.1409
2170.3479 | 541.3076 | 571.9314 | 464.7088
2171.3479 | 541.2469 | 571.7681 | 464.7669
2172.3479 | 540.6654 | 569.4487 | 465.0727
2173.3479 | 539.3814 | 567.336 | 465.9633
2174.3479 | 538.2072 | 566.3833 | 467.0586
2175.3479 | 536.4931 | 565.8132 | 469.8758
2176.3479 | 535.4328 | 569.0507 | 470.9723
2177.3479 | 534.2711 | 569.063 | 471.4734
2178.3479 | 534.2382 | 569.4297 | 474.3219
2179.3479 | 532.6649 | 568.0146 | 474.694
2180.3479 | 530.5942 | 567.0471 | 473.906
2181.3479 | 530.074 | 567.8881 | 473.3358
2182.3479 | 529.812 | 566.4579 | 472.5125
2183.3479 | 529.6237 | 565.5232 | 471.733
2184.3479 | 529.383 | 565.8103 | 471.2476
2185.3479 | 529.155 | 565.5695 | 470.9516
2186.3479 | 529.0552 | 566.1218 | 469.8811
2187.3479 | 529.6633 | 563.8081 | 468.2519
2188.3479 | 530.3776 | 563.5236 | 467.7831
2189.3479 | 530.2185 | 563.2496 | 467.3586
2190.3479 | 531.1867 | 563.0345 | 466.4518
2191.3479 | 532.7782 | 561.4523 | 465.8667
2192.3479 | 532.7635 | 558.7232 | 465.8308
2193.3479 | 532.2441 | 559.0016 | 465.6585
2194.3479 | 532.0208 | 561.0643 | 465.1397
2195.3479 | 533.1593 | 562.5412 | 464.5436
2196.3479 | 534.312 | 563.8674 | 464.3354
2197.3479 | 535.0685 | 565.1765 | 464.3141
2198.3635 | 535.3207 | 567.0823 | 464.1694
2199.3479 | 535.5423 | 566.2195 | 464.6763
2200.3479 | 535.9568 | 563.5497 | 463.5662
2201.3479 | 536.9258 | 563.141 | 462.8354
2202.3479 | 538.193 | 561.2382 | 463.1665
2203.3479 | 539.0939 | 561.1023 | 462.6947
2204.3479 | 539.462 | 561.9408 | 463.9197
2205.3479 | 538.5054 | 561.8086 | 463.4681
2206.3479 | 539.475 | 562.362 | 462.1518
2207.3479 | 538.9102 | 561.6394 | 463.3586
2208.3479 | 538.2064 | 560.28 | 462.6432
2209.3479 | 538.4975 | 560.6936 | 462.027
2210.3479 | 537.8021 | 560.5077 | 464.0535
2211.3479 | 536.7551 | 562.2902 | 464.8294
2212.3479 | 535.7657 | 564.1303 | 466.0709
2213.3479 | 535.1973 | 564.1181 | 465.55
2214.3479 | 534.5612 | 564.7147 | 464.8741
2215.3479 | 535.4337 | 565.6267 | 463.9938
2216.3479 | 535.8202 | 564.7389 | 463.2743
2217.3479 | 535.541 | 563.3608 | 463.5026
2218.3479 | 536.367 | 563.5379 | 462.4834
2219.3479 | 537.1586 | 564.9434 | 461.8078
2220.3479 | 537.6314 | 565.2082 | 461.3886
2221.3479 | 539.4852 | 566.0455 | 460.5763
2222.3479 | 540.1993 | 566.5615 | 460.5565
2223.3479 | 540.2483 | 567.9116 | 460.5008
2224.3479 | 541.2365 | 567.9082 | 459.7867
2225.3479 | 542.0881 | 567.8779 | 459.0387
2226.3479 | 542.4259 | 568.401 | 459.3427
2227.3479 | 544.1215 | 568.6945 | 458.5025
2228.3479 | 545.219 | 566.4193 | 457.5845
2229.3479 | 544.3884 | 564.3442 | 456.9067
2230.3479 | 543.6999 | 561.5669 | 456.5383
2231.3479 | 541.802 | 559.642 | 456.8857
2232.3479 | 540.7826 | 559.3117 | 456.3631
2233.3479 | 540.0591 | 559.4974 | 456.0067
2234.3479 | 539.2563 | 559.234 | 455.9875
2235.3479 | 538.9609 | 561.4133 | 458.2193
2236.3479 | 539.6799 | 562.8197 | 458.7837
2237.3479 | 540.0153 | 562.1946 | 457.6692
2238.3479 | 540.2204 | 563.233 | 457.712
2239.3479 | 540.4183 | 564.1484 | 457.3552
2240.3479 | 541.5581 | 564.7306 | 457.1853
2241.3479 | 542.4546 | 564.0893 | 456.2727
2242.3479 | 543.0566 | 563.0962 | 456.2584
2243.3479 | 542.2687 | 564.1452 | 457.7134
2244.3479 | 541.8832 | 564.0856 | 457.4675
2245.3479 | 541.7146 | 563.8618 | 457.5963
2246.3479 | 540.8808 | 562.7188 | 457.781
2247.3479 | 540.9587 | 562.2464 | 458.2859
2248.3479 | 541.6224 | 563.9708 | 458.5386
2249.3479 | 542.263 | 563.2135 | 457.6853
2250.3479 | 541.6568 | 562.3909 | 456.8619
2251.3479 | 540.7886 | 560.0216 | 456.4041
2252.3479 | 540.0463 | 562.0692 | 457.0133
2253.3479 | 539.9952 | 561.2039 | 455.9008
2254.3479 | 541.0684 | 560.0593 | 455.575
2255.3479 | 541.5167 | 560.6857 | 455.2383
2256.3479 | 542.7054 | 559.6623 | 455.219
2257.3479 | 542.8553 | 560.6137 | 455.0493
2258.3479 | 543.3323 | 564.1246 | 456.0962
2259.3479 | 544.5079 | 563.7857 | 455.8068
2260.3479 | 544.4575 | 564.991 | 456.7695
2261.3479 | 543.8106 | 566.0711 | 458.4431
2262.3479 | 542.1585 | 566.3163 | 458.7999
2263.3479 | 542.363 | 568.3339 | 458.7697
2264.3479 | 542.2652 | 568.4906 | 458.2662
2265.3479 | 542.5818 | 568.3412 | 458.4403
2266.3479 | 542.4672 | 569.8169 | 458.9269
2267.3479 | 543.539 | 568.0054 | 459.5087
2268.3479 | 543.8273 | 567.4979 | 458.6936
2269.3479 | 545.3296 | 568.4906 | 458.5071
2270.3479 | 546.1518 | 571.8969 | 458.7746
2271.3479 | 546.6436 | 571.1194 | 458.729
2272.3479 | 546.8022 | 570.1081 | 458.694
2273.3479 | 546.2111 | 569.2442 | 458.871
2274.3479 | 545.056 | 568.0028 | 460.9855
2275.3479 | 543.7218 | 568.3746 | 460.9797
2276.3479 | 543.1993 | 568.7895 | 461.1492
2277.3479 | 543.1888 | 568.55 | 460.6769
2278.3479 | 543.5836 | 568.2186 | 460.3056
2279.3479 | 543.7705 | 567.8395 | 460.8136
2280.3479 | 544.1625 | 564.4589 | 459.775
2281.3479 | 545.069 | 564.8208 | 460.1089
2282.3479 | 546.946 | 566.6861 | 459.7549
2283.3479 | 547.5518 | 568.3086 | 460.0922
2284.3479 | 547.7097 | 568.4042 | 460.9853
2285.3479 | 548.138 | 569.3877 | 460.4071
2286.3479 | 547.3065 | 569.7854 | 460.8557
2287.3479 | 547.4165 | 568.6729 | 460.3726
2288.3479 | 546.914 | 567.4056 | 460.8283
2289.3479 | 546.0609 | 568.7773 | 460.6081
2290.3479 | 545.6677 | 570.7133 | 461.1722
2291.3479 | 545.0212 | 571.9746 | 464.3903
2292.3479 | 544.5836 | 570.5217 | 466.4749
2293.3479 | 544.3136 | 571.9031 | 467.3443
2294.3479 | 543.3273 | 571.0473 | 467.2607
2295.3479 | 542.512 | 569.7543 | 468.7905
2296.3479 | 541.0593 | 568.5624 | 469.4018
2297.3479 | 539.5852 | 569.5475 | 470.2149
2298.3479 | 538.6358 | 569.5471 | 469.4465
2299.3479 | 539.823 | 569.7528 | 470.0568
2300.3479 | 540.2478 | 568.4391 | 471.5615
2301.3479 | 539.2392 | 569.0506 | 474.2283
2302.3479 | 538.1556 | 568.0848 | 472.9392
2303.3479 | 538.1236 | 566.7455 | 471.3417
2304.3479 | 538.1467 | 567.2964 | 470.3163
2305.3479 | 537.6477 | 567.5085 | 469.2663
2306.3479 | 537.3054 | 567.8566 | 469.5107
2307.3479 | 538.0718 | 568.4895 | 468.9908
2308.3479 | 539.4471 | 568.4719 | 468.2059
2309.3479 | 540.6772 | 568.8404 | 467.8906
2310.3479 | 540.673 | 569.2103 | 468.6794
2311.3479 | 539.8899 | 571.1203 | 468.7392
2312.3479 | 540.8674 | 571.0027 | 468.1283
2313.3479 | 540.7374 | 570.6447 | 468.2748
2314.3479 | 540.6853 | 571.5079 | 467.4145
2315.3479 | 542.4227 | 572.9489 | 466.3729
2316.3479 | 543.9996 | 571.1352 | 465.1856
2317.3479 | 544.7534 | 569.023 | 464.7435
2318.3479 | 544.6924 | 568.9707 | 464.4087
2319.3479 | 543.3197 | 571.3679 | 464.1595
2320.3479 | 542.9258 | 571.5936 | 463.4479
2321.3479 | 544.0023 | 571.0537 | 462.6893
2322.3479 | 544.8621 | 570.1793 | 461.4619
2323.3479 | 545.474 | 565.2591 | 460.6117
2324.3479 | 547.3377 | 565.9304 | 460.3293
2325.3479 | 548.5731 | 565.3244 | 459.8356
2326.3479 | 549.3297 | 565.1204 | 459.2687
2327.3479 | 549.7368 | 566.0205 | 458.9421
2328.3479 | 550.0133 | 566.8806 | 460.179
2329.3479 | 549.0479 | 568.2847 | 461.6067
2330.3479 | 547.3733 | 569.4538 | 463.6419
2331.3479 | 545.9882 | 568.6768 | 465.8158
2332.3479 | 544.8838 | 569.2979 | 466.2726
2333.3479 | 545.0371 | 569.1631 | 465.4485
2334.3479 | 545.1149 | 569.28 | 466.677
2335.3479 | 544.3818 | 569.1407 | 467.4341
2336.3479 | 543.9943 | 569.8967 | 467.7319
2337.3479 | 543.7441 | 570.8719 | 468.8835
2338.3479 | 543.3472 | 570.6308 | 468.4616
2339.3479 | 543.7993 | 569.4259 | 467.729
2340.3479 | 544.8407 | 568.9009 | 467.5664
2341.3479 | 544.2909 | 570.6445 | 468.7007
2342.3479 | 542.7567 | 570.8144 | 469.3831
2343.3479 | 542.2156 | 571.575 | 469.4765
2344.3479 | 542.312 | 571.9903 | 469.7277
2345.3479 | 541.6728 | 572.7907 | 470.9577
2346.3479 | 540.5597 | 572.2168 | 471.5779
2347.3479 | 540.5387 | 571.42 | 470.7636
2348.3479 | 540.4028 | 571.9723 | 473.4917
2349.3479 | 540.0463 | 572.4542 | 474.9811
2350.3479 | 538.8835 | 572.7975 | 477.6909
2351.3479 | 536.7513 | 571.7962 | 477.6492
2352.3479 | 535.5078 | 571.8531 | 479.1471
2353.3479 | 535.0856 | 571.618 | 481.5405
2354.3479 | 534.3077 | 571.1716 | 480.5527
2355.3479 | 534.3213 | 571.7365 | 480.1873
2356.3479 | 534.221 | 569.8615 | 478.1496
2357.3479 | 535.404 | 567.4641 | 476.6185
2358.3479 | 536.9454 | 568.1555 | 475.3138
2359.3479 | 537.0288 | 568.5703 | 474.5937
2360.3479 | 537.05 | 568.5165 | 473.676
2361.3479 | 537.4584 | 568.3064 | 472.3111
2362.3479 | 537.4818 | 567.2122 | 470.8117
2363.3479 | 537.512 | 565.3408 | 469.6864
2364.3479 | 536.8108 | 565.7696 | 469.955
2365.3479 | 537.3911 | 566.5052 | 469.1072
2366.3479 | 537.7026 | 564.4071 | 467.9011
2367.3479 | 538.0807 | 562.3012 | 466.5752
2368.3479 | 537.588 | 560.6406 | 465.3742
2369.3479 | 538.0787 | 560.8505 | 464.9127
2370.3479 | 539.1555 | 560.0885 | 463.5545
2371.3479 | 540.0836 | 557.3124 | 462.7636
2372.3479 | 540.1959 | 558.1436 | 462.6037
2373.3479 | 539.1578 | 560.6616 | 462.6389
2374.3479 | 538.9052 | 562.4215 | 463.2337
2375.3479 | 537.9771 | 560.9396 | 463.7277
2376.3479 | 537.5885 | 561.8058 | 464.3149
2377.3479 | 537.277 | 561.7472 | 464.2329
2378.3635 | 536.7988 | 561.303 | 463.9632
2379.3479 | 538.0889 | 560.3762 | 462.766
2380.3479 | 540.3942 | 561.4145 | 463.2138
2381.3479 | 542.2293 | 565.0538 | 462.5182
2382.3479 | 541.5432 | 566.1001 | 462.2044
2383.3479 | 542.1168 | 567.6245 | 462.1032
2384.3479 | 541.9933 | 566.2842 | 464.2496
2385.3479 | 541.0565 | 569.0827 | 466.3294
2386.3479 | 540.4597 | 568.3546 | 467.1046
2387.3479 | 540.9641 | 569.0315 | 467.6878
2388.3479 | 540.9607 | 569.6337 | 467.7416
2389.3479 | 541.8923 | 570.1485 | 467.3394
2390.3479 | 542.4249 | 568.6534 | 466.9228
2391.3479 | 543.2328 | 567.5859 | 465.9539
2392.3479 | 544.4463 | 566.8835 | 465.0679
2393.3479 | 545.6081 | 566.7564 | 464.5001
2394.3479 | 546.3025 | 566.3553 | 463.7331
2395.3479 | 545.8319 | 565.3549 | 462.575
2396.3479 | 546.9765 | 566.2847 | 461.4278
2397.3479 | 546.5073 | 565.3149 | 460.4949
2398.3479 | 546.7026 | 566.0282 | 460.0586
2399.3479 | 546.4213 | 565.0673 | 461.8111
2400.3479 | 544.7421 | 564.0988 | 461.4068