## Test Conditions
DESIREE-FIRE Intermediate Scale Test 7 - Circuit Simulator Data Only
Test Date: | 2010-03-09
DCSim DAQ Start Time | 13:14
DCSim Time for Synchronization | 13:16
Heat Source Synchronization | 0:00 | hours:minutes:seconds
Heat Source DAQ Start Time | 13:15
Fire Time | 14:00
Offset | 0:46 | hours:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 2760 | seconds
Heat Source Offset | 0:45 | hours:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 2695 | seconds
Heat Source Stop Time | 14:40
Test Duration | 0:40 | hours:minutes:seconds
| 2400 | seconds
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
Intercable Configuration | PE/PVC, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 0 represents the air temperature in the middle of the tray located in A Position. It is labeled as "A Position - Middle".
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds.
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | Int-Cab_VT7-T1 | Int-Cab_VT7-T2 | Int-Cab_VT7-T3 | Int-Cab_VT7-T4 | Int-Cab_VT7-T5 | Int-Cab_VT7-T6 | Int-Cab_VT7-T7 | Int-Cab_VTU-S1+a | Int-Cab_VTU-S1+b | Int-Cab_VTU-S2+a | Int-Cab_VTU-S2+b | Int-Cab_VTU-S1-a | Int-Cab_VTU-S1-b | Int-Cab_VTU-S2-a | Int-Cab_VTU-S2-b | T1-V(Batt -) | T2 -V(Batt -) | T3 - V(Batt -) | T4 - V(Batt -) | T5 - V(Batt -) | T6 - V(Batt -) | T7 - V(Batt -) | {S1+a} - V(Batt - ) | {S1+b} - V(Batt - ) | {S2+a} - V(Batt - ) | {S2+b} - V(Batt - ) | {S1-a} - V(Batt -) | {S1-b} - V(Batt - ) | {S2-a} - V(Batt - ) | {S2-b} - V(Batt - ) | {S1+a} - {S1-a} | {S1+a} - {S2-a} | {S2+a} - {S1-a} | {S2+a} - {S2-a}
-0.8125 | 121.9803 | -60.9421 | 60.9146 | 0.085224 | -0.040521 | 0.033786 | -0.047909 | 0.06831 | 0.053534 | -0.08103 | 60.7771 | 60.7898 | 60.7953 | 60.749 | 60.8693 | 61.0351 | 60.5203 | 60.7355 | 0.11269 | -0.013055 | 0.061252 | -0.020443 | 0.095776 | 0.081 | -0.053564 | 60.8045 | 60.8172 | 60.8228 | 60.7764 | 60.8967 | 61.0626 | 60.5477 | 60.7629 | -0.092197 | 0.2568 | -0.073921 | 0.27507
0.9375 | 122.0352 | -60.9192 | 60.9375 | 0.089802 | -0.049678 | 0.038365 | -0.043331 | 0.063733 | 0.053534 | -0.085608 | 60.7771 | 60.7943 | 60.7908 | 60.7444 | 60.8784 | 61.0397 | 60.5065 | 60.7309 | 0.11727 | -0.022212 | 0.065831 | -0.015865 | 0.091199 | 0.081 | -0.058142 | 60.8045 | 60.8218 | 60.8182 | 60.7719 | 60.9059 | 61.0671 | 60.534 | 60.7583 | -0.10135 | 0.27053 | -0.087655 | 0.28423
2.6094 | 122.0718 | -60.8917 | 60.9055 | 0.080646 | -0.054257 | 0.038365 | -0.052488 | 0.06831 | 0.053534 | -0.085608 | 60.7816 | 60.7898 | 60.7862 | 60.7398 | 60.8738 | 61.0397 | 60.5111 | 60.7309 | 0.10811 | -0.026791 | 0.065831 | -0.025022 | 0.095776 | 0.081 | -0.058142 | 60.8091 | 60.8172 | 60.8137 | 60.7673 | 60.9013 | 61.0671 | 60.5386 | 60.7583 | -0.092197 | 0.27053 | -0.087655 | 0.27507
4.3438 | 121.9666 | -60.9375 | 60.9375 | 0.089802 | -0.040521 | 0.042944 | -0.052488 | 0.06831 | 0.053534 | -0.08103 | 60.7862 | 60.7852 | 60.7953 | 60.7398 | 60.8738 | 61.0397 | 60.502 | 60.74 | 0.11727 | -0.013055 | 0.07041 | -0.025022 | 0.095776 | 0.081 | -0.053564 | 60.8137 | 60.8126 | 60.8228 | 60.7673 | 60.9013 | 61.0671 | 60.5294 | 60.7675 | -0.087618 | 0.28427 | -0.078499 | 0.29339
6.0938 | 122.1222 | -60.9146 | 60.8826 | 0.085224 | -0.0451 | 0.042944 | -0.052488 | 0.063733 | 0.048956 | -0.08103 | 60.7816 | 60.7852 | 60.7953 | 60.7398 | 60.8738 | 61.0351 | 60.5157 | 60.7263 | 0.11269 | -0.017634 | 0.07041 | -0.025022 | 0.091199 | 0.076422 | -0.053564 | 60.8091 | 60.8126 | 60.8228 | 60.7673 | 60.9013 | 61.0626 | 60.5432 | 60.7538 | -0.092197 | 0.26595 | -0.078499 | 0.27965
7.8281 | 121.9894 | -60.9695 | 60.9238 | 0.089802 | -0.026784 | 0.038365 | -0.043331 | 0.063733 | 0.053534 | -0.08103 | 60.7771 | 60.7852 | 60.7953 | 60.7444 | 60.8647 | 61.0397 | 60.5203 | 60.7217 | 0.11727 | 0.000682 | 0.065831 | -0.015865 | 0.091199 | 0.081 | -0.053564 | 60.8045 | 60.8126 | 60.8228 | 60.7719 | 60.8922 | 61.0671 | 60.5477 | 60.7492 | -0.087619 | 0.2568 | -0.069343 | 0.27507
9.5469 | 122.0993 | -60.878 | 60.9375 | 0.080646 | -0.040521 | 0.047522 | -0.047909 | 0.063733 | 0.053534 | -0.085608 | 60.7771 | 60.7943 | 60.7953 | 60.7398 | 60.8693 | 61.0351 | 60.5386 | 60.74 | 0.10811 | -0.013055 | 0.074988 | -0.020443 | 0.091199 | 0.081 | -0.058142 | 60.8045 | 60.8218 | 60.8228 | 60.7673 | 60.8967 | 61.0626 | 60.5661 | 60.7675 | -0.092197 | 0.23848 | -0.073921 | 0.25676
11.2188 | 122.0261 | -60.9421 | 60.91 | 0.089802 | -0.040521 | 0.038365 | -0.038752 | 0.063733 | 0.048956 | -0.076452 | 60.7771 | 60.7943 | 60.7953 | 60.7352 | 60.8784 | 61.0305 | 60.5294 | 60.7309 | 0.11727 | -0.013055 | 0.065831 | -0.011286 | 0.091199 | 0.076422 | -0.048986 | 60.8045 | 60.8218 | 60.8228 | 60.7627 | 60.9059 | 61.058 | 60.5569 | 60.7583 | -0.10135 | 0.24764 | -0.083077 | 0.26592
12.9531 | 122.0718 | -60.8917 | 60.9055 | 0.085224 | -0.035942 | 0.033786 | -0.052488 | 0.06831 | 0.053534 | -0.08103 | 60.7725 | 60.7852 | 60.7999 | 60.7307 | 60.8601 | 61.0397 | 60.5157 | 60.7263 | 0.11269 | -0.008476 | 0.061252 | -0.025022 | 0.095776 | 0.081 | -0.053564 | 60.8 | 60.8126 | 60.8274 | 60.7581 | 60.8876 | 61.0671 | 60.5432 | 60.7538 | -0.08762 | 0.2568 | -0.060186 | 0.28423
14.625 | 122.0856 | -60.9146 | 60.878 | 0.080646 | -0.035942 | 0.038365 | -0.043331 | 0.063733 | 0.053534 | -0.08103 | 60.7725 | 60.7898 | 60.7908 | 60.7307 | 60.8647 | 61.0397 | 60.5294 | 60.7217 | 0.10811 | -0.008476 | 0.065831 | -0.015865 | 0.091199 | 0.081 | -0.053564 | 60.8 | 60.8172 | 60.8182 | 60.7581 | 60.8922 | 61.0671 | 60.5569 | 60.7492 | -0.092198 | 0.24306 | -0.073921 | 0.26134
16.375 | 122.1085 | -60.8826 | 60.9009 | 0.076067 | -0.035942 | 0.033786 | -0.043331 | 0.059155 | 0.053534 | -0.090186 | 60.7725 | 60.7852 | 60.7953 | 60.7352 | 60.8738 | 61.0397 | 60.534 | 60.7217 | 0.10353 | -0.008476 | 0.061252 | -0.015865 | 0.086621 | 0.081 | -0.06272 | 60.8 | 60.8126 | 60.8228 | 60.7627 | 60.9013 | 61.0671 | 60.5615 | 60.7492 | -0.10135 | 0.23848 | -0.078499 | 0.26134
18.1094 | 122.0856 | -60.9055 | 60.8734 | 0.085224 | -0.040521 | 0.038365 | -0.052488 | 0.06831 | 0.053534 | -0.094765 | 60.7816 | 60.7806 | 60.7999 | 60.7352 | 60.8647 | 61.0351 | 60.534 | 60.7171 | 0.11269 | -0.013055 | 0.065831 | -0.025022 | 0.095776 | 0.081 | -0.067299 | 60.8091 | 60.8081 | 60.8274 | 60.7627 | 60.8922 | 61.0626 | 60.5615 | 60.7446 | -0.083041 | 0.24764 | -0.064764 | 0.26592
19.8438 | 121.9986 | -60.9375 | 60.9009 | 0.080646 | -0.040521 | 0.042944 | -0.052488 | 0.06831 | 0.053534 | -0.085608 | 60.7725 | 60.7852 | 60.7953 | 60.7398 | 60.8647 | 61.0305 | 60.5386 | 60.7263 | 0.10811 | -0.013055 | 0.07041 | -0.025022 | 0.095776 | 0.081 | -0.058142 | 60.8 | 60.8126 | 60.8228 | 60.7673 | 60.8922 | 61.058 | 60.5661 | 60.7538 | -0.092198 | 0.2339 | -0.069343 | 0.25676
21.5312 | 122.0627 | -60.9329 | 60.878 | 0.085224 | -0.040521 | 0.038365 | -0.047909 | 0.059155 | 0.048956 | -0.08103 | 60.7725 | 60.7806 | 60.7953 | 60.7307 | 60.8647 | 61.0351 | 60.5294 | 60.7171 | 0.11269 | -0.013055 | 0.065831 | -0.020443 | 0.086621 | 0.076422 | -0.053564 | 60.8 | 60.8081 | 60.8228 | 60.7581 | 60.8922 | 61.0626 | 60.5569 | 60.7446 | -0.092198 | 0.24306 | -0.069343 | 0.26592
23.2812 | 121.9986 | -60.9604 | 60.9192 | 0.085224 | -0.035942 | 0.047522 | -0.043331 | 0.06831 | 0.053534 | -0.08103 | 60.7771 | 60.7852 | 60.7953 | 60.7352 | 60.8647 | 61.0259 | 60.5432 | 60.7126 | 0.11269 | -0.008476 | 0.074988 | -0.015865 | 0.095776 | 0.081 | -0.053564 | 60.8045 | 60.8126 | 60.8228 | 60.7627 | 60.8922 | 61.0534 | 60.5706 | 60.74 | -0.087619 | 0.23391 | -0.069343 | 0.25218
25.0156 | 121.9528 | -60.965 | 60.878 | 0.089802 | -0.031363 | 0.038365 | -0.043331 | 0.063733 | 0.058113 | -0.085608 | 60.7771 | 60.7852 | 60.7908 | 60.7261 | 60.8647 | 61.0305 | 60.534 | 60.7217 | 0.11727 | -0.003897 | 0.065831 | -0.015865 | 0.091199 | 0.085579 | -0.058142 | 60.8045 | 60.8126 | 60.8182 | 60.7535 | 60.8922 | 61.058 | 60.5615 | 60.7492 | -0.087619 | 0.24306 | -0.073921 | 0.25676
26.6875 | 121.9849 | -60.9375 | 60.8963 | 0.085224 | -0.035942 | 0.047522 | -0.052488 | 0.06831 | 0.053534 | -0.085608 | 60.7725 | 60.7806 | 60.7908 | 60.7352 | 60.8601 | 61.0305 | 60.5294 | 60.7126 | 0.11269 | -0.008476 | 0.074988 | -0.025022 | 0.095776 | 0.081 | -0.058142 | 60.8 | 60.8081 | 60.8182 | 60.7627 | 60.8876 | 61.058 | 60.5569 | 60.74 | -0.08762 | 0.24306 | -0.069343 | 0.26134
28.4219 | 122.0398 | -60.8871 | 60.9238 | 0.085224 | -0.035942 | 0.029208 | -0.052488 | 0.06831 | 0.048956 | -0.08103 | 60.7725 | 60.7806 | 60.7862 | 60.7307 | 60.8601 | 61.0351 | 60.5294 | 60.7217 | 0.11269 | -0.008476 | 0.056674 | -0.025022 | 0.095776 | 0.076422 | -0.053564 | 60.8 | 60.8081 | 60.8137 | 60.7581 | 60.8876 | 61.0626 | 60.5569 | 60.7492 | -0.08762 | 0.24306 | -0.073921 | 0.25676
30.0938 | 121.962 | -60.9375 | 60.8826 | 0.085224 | -0.031363 | 0.047522 | -0.047909 | 0.06831 | 0.048956 | -0.076452 | 60.7725 | 60.7806 | 60.7908 | 60.7398 | 60.8555 | 61.0259 | 60.5294 | 60.7171 | 0.11269 | -0.003897 | 0.074988 | -0.020443 | 0.095776 | 0.076422 | -0.048986 | 60.8 | 60.8081 | 60.8182 | 60.7673 | 60.883 | 61.0534 | 60.5569 | 60.7446 | -0.083041 | 0.24306 | -0.064764 | 0.26134
31.8594 | 121.9391 | -60.9375 | 60.9421 | 0.080646 | -0.035942 | 0.033786 | -0.047909 | 0.06831 | 0.048956 | -0.08103 | 60.7725 | 60.7806 | 60.7953 | 60.7307 | 60.8647 | 61.0305 | 60.534 | 60.7171 | 0.10811 | -0.008476 | 0.061252 | -0.020443 | 0.095776 | 0.076422 | -0.053564 | 60.8 | 60.8081 | 60.8228 | 60.7581 | 60.8922 | 61.058 | 60.5615 | 60.7446 | -0.092198 | 0.23848 | -0.069343 | 0.26134
33.5938 | 122.0581 | -60.878 | 60.9192 | 0.080646 | -0.040521 | 0.038365 | -0.043331 | 0.072888 | 0.053534 | -0.076452 | 60.7633 | 60.7806 | 60.7862 | 60.7215 | 60.8601 | 61.0305 | 60.534 | 60.7171 | 0.10811 | -0.013055 | 0.065831 | -0.015865 | 0.10035 | 0.081 | -0.048986 | 60.7908 | 60.8081 | 60.8137 | 60.749 | 60.8876 | 61.058 | 60.5615 | 60.7446 | -0.096777 | 0.22933 | -0.073921 | 0.25218
35.3281 | 121.9528 | -60.9467 | 60.8963 | 0.089802 | -0.040521 | 0.038365 | -0.047909 | 0.072888 | 0.048956 | -0.085608 | 60.7679 | 60.7852 | 60.7908 | 60.7215 | 60.8555 | 61.0305 | 60.5249 | 60.7126 | 0.11727 | -0.013055 | 0.065831 | -0.020443 | 0.10035 | 0.076422 | -0.058142 | 60.7954 | 60.8126 | 60.8182 | 60.749 | 60.883 | 61.058 | 60.5523 | 60.74 | -0.087619 | 0.24306 | -0.064764 | 0.26592
37 | 122.0718 | -60.8917 | 60.8643 | 0.089802 | -0.0451 | 0.042944 | -0.047909 | 0.059155 | 0.048956 | -0.08103 | 60.7679 | 60.7852 | 60.7862 | 60.7169 | 60.8647 | 61.0305 | 60.5203 | 60.7126 | 0.11727 | -0.017634 | 0.07041 | -0.020443 | 0.086621 | 0.076422 | -0.053564 | 60.7954 | 60.8126 | 60.8137 | 60.7444 | 60.8922 | 61.058 | 60.5477 | 60.74 | -0.096776 | 0.24764 | -0.078499 | 0.26592
38.75 | 122.0581 | -60.9055 | 60.878 | 0.085224 | -0.049678 | 0.033786 | -0.052488 | 0.06831 | 0.048956 | -0.08103 | 60.7679 | 60.7852 | 60.7862 | 60.7261 | 60.8555 | 61.0305 | 60.5294 | 60.708 | 0.11269 | -0.022212 | 0.061252 | -0.025022 | 0.095776 | 0.076422 | -0.053564 | 60.7954 | 60.8126 | 60.8137 | 60.7535 | 60.883 | 61.058 | 60.5569 | 60.7354 | -0.087619 | 0.23848 | -0.069342 | 0.25676
40.4844 | 122.0856 | -60.9055 | 60.8551 | 0.080646 | -0.035942 | 0.033786 | -0.043331 | 0.063733 | 0.048956 | -0.085608 | 60.7725 | 60.776 | 60.7908 | 60.7307 | 60.8555 | 61.0305 | 60.5294 | 60.7126 | 0.10811 | -0.008476 | 0.061252 | -0.015865 | 0.091199 | 0.076422 | -0.058142 | 60.8 | 60.8035 | 60.8182 | 60.7581 | 60.883 | 61.058 | 60.5569 | 60.74 | -0.083041 | 0.24306 | -0.064764 | 0.26134
42.1562 | 121.9803 | -60.9421 | 60.8871 | 0.085224 | -0.035942 | 0.042944 | -0.047909 | 0.059155 | 0.053534 | -0.076452 | 60.7679 | 60.776 | 60.7908 | 60.7261 | 60.8601 | 61.0214 | 60.5203 | 60.7034 | 0.11269 | -0.008476 | 0.07041 | -0.020443 | 0.086621 | 0.081 | -0.048986 | 60.7954 | 60.8035 | 60.8182 | 60.7535 | 60.8876 | 61.0488 | 60.5477 | 60.7309 | -0.092198 | 0.24764 | -0.069343 | 0.27049
43.9062 | 121.9482 | -60.9329 | 60.9329 | 0.085224 | -0.049678 | 0.033786 | -0.043331 | 0.06831 | 0.053534 | -0.085608 | 60.7633 | 60.776 | 60.7862 | 60.7261 | 60.8601 | 61.0305 | 60.534 | 60.7126 | 0.11269 | -0.022212 | 0.061252 | -0.015865 | 0.095776 | 0.081 | -0.058142 | 60.7908 | 60.8035 | 60.8137 | 60.7535 | 60.8876 | 61.058 | 60.5615 | 60.74 | -0.096777 | 0.22933 | -0.073921 | 0.25218
45.6562 | 121.9391 | -60.9604 | 60.8917 | 0.085224 | -0.054257 | 0.033786 | -0.052488 | 0.072888 | 0.048956 | -0.08103 | 60.7679 | 60.7714 | 60.7816 | 60.7352 | 60.851 | 61.0214 | 60.5203 | 60.7034 | 0.11269 | -0.026791 | 0.061252 | -0.025022 | 0.10035 | 0.076422 | -0.053564 | 60.7954 | 60.7989 | 60.8091 | 60.7627 | 60.8784 | 61.0488 | 60.5477 | 60.7309 | -0.083041 | 0.24764 | -0.069343 | 0.26134
47.4062 | 121.9666 | -60.9238 | 60.9238 | 0.080646 | -0.0451 | 0.042944 | -0.047909 | 0.06831 | 0.044377 | -0.08103 | 60.7725 | 60.776 | 60.7862 | 60.7307 | 60.883 | 61.0259 | 60.5294 | 60.74 | 0.10811 | -0.017634 | 0.07041 | -0.020443 | 0.095776 | 0.071843 | -0.053564 | 60.8 | 60.8035 | 60.8137 | 60.7581 | 60.9105 | 61.0534 | 60.5569 | 60.7675 | -0.11051 | 0.24306 | -0.096811 | 0.25676
49.0781 | 121.9482 | -60.9283 | 60.9009 | 0.085224 | -0.058836 | 0.038365 | -0.047909 | 0.06831 | 0.053534 | -0.08103 | 60.7679 | 60.776 | 60.7816 | 60.7307 | 60.8555 | 61.0305 | 60.5249 | 60.708 | 0.11269 | -0.03137 | 0.065831 | -0.020443 | 0.095776 | 0.081 | -0.053564 | 60.7954 | 60.8035 | 60.8091 | 60.7581 | 60.883 | 61.058 | 60.5523 | 60.7354 | -0.087619 | 0.24306 | -0.073921 | 0.25676
50.8281 | 121.9849 | -60.9192 | 60.9055 | 0.076067 | -0.058836 | 0.038365 | -0.047909 | 0.063733 | 0.053534 | -0.085608 | 60.7633 | 60.7806 | 60.7862 | 60.7261 | 60.851 | 61.0168 | 60.5249 | 60.7126 | 0.10353 | -0.03137 | 0.065831 | -0.020443 | 0.091199 | 0.081 | -0.058142 | 60.7908 | 60.8081 | 60.8137 | 60.7535 | 60.8784 | 61.0443 | 60.5523 | 60.74 | -0.08762 | 0.23848 | -0.064764 | 0.26134
52.4844 | 122.0444 | -60.8871 | 60.9146 | 0.080646 | -0.054257 | 0.042944 | -0.052488 | 0.063733 | 0.044377 | -0.085608 | 60.7679 | 60.7623 | 60.7908 | 60.7261 | 60.8464 | 61.0168 | 60.5203 | 60.708 | 0.10811 | -0.026791 | 0.07041 | -0.025022 | 0.091199 | 0.071843 | -0.058142 | 60.7954 | 60.7897 | 60.8182 | 60.7535 | 60.8738 | 61.0443 | 60.5477 | 60.7354 | -0.078463 | 0.24764 | -0.055608 | 0.27049
54.2188 | 122.0718 | -60.8963 | 60.8688 | 0.089802 | -0.040521 | 0.029208 | -0.047909 | 0.059155 | 0.053534 | -0.08103 | 60.7633 | 60.776 | 60.7816 | 60.7261 | 60.8464 | 61.0214 | 60.5203 | 60.7034 | 0.11727 | -0.013055 | 0.056674 | -0.020443 | 0.086621 | 0.081 | -0.053564 | 60.7908 | 60.8035 | 60.8091 | 60.7535 | 60.8738 | 61.0488 | 60.5477 | 60.7309 | -0.083042 | 0.24306 | -0.064765 | 0.26134
55.8906 | 121.9757 | -60.9283 | 60.9329 | 0.076067 | -0.0451 | 0.038365 | -0.047909 | 0.072888 | 0.044377 | -0.08103 | 60.7679 | 60.776 | 60.7816 | 60.7215 | 60.851 | 61.0214 | 60.5249 | 60.708 | 0.10353 | -0.017634 | 0.065831 | -0.020443 | 0.10035 | 0.071843 | -0.053564 | 60.7954 | 60.8035 | 60.8091 | 60.749 | 60.8784 | 61.0488 | 60.5523 | 60.7354 | -0.083041 | 0.24306 | -0.069343 | 0.25676
57.625 | 122.0901 | -60.8688 | 60.8826 | 0.089802 | -0.040521 | 0.038365 | -0.047909 | 0.063733 | 0.053534 | -0.076452 | 60.7588 | 60.7806 | 60.7816 | 60.7261 | 60.8464 | 61.0259 | 60.5249 | 60.7034 | 0.11727 | -0.013055 | 0.065831 | -0.020443 | 0.091199 | 0.081 | -0.048986 | 60.7862 | 60.8081 | 60.8091 | 60.7535 | 60.8738 | 61.0534 | 60.5523 | 60.7309 | -0.08762 | 0.2339 | -0.064765 | 0.25676
59.2969 | 122.0261 | -60.8963 | 60.8597 | 0.085224 | -0.035942 | 0.033786 | -0.047909 | 0.063733 | 0.048956 | -0.08103 | 60.7588 | 60.7669 | 60.7816 | 60.7215 | 60.8464 | 61.0214 | 60.5157 | 60.7034 | 0.11269 | -0.008476 | 0.061252 | -0.020443 | 0.091199 | 0.076422 | -0.053564 | 60.7862 | 60.7943 | 60.8091 | 60.749 | 60.8738 | 61.0488 | 60.5432 | 60.7309 | -0.08762 | 0.24306 | -0.064765 | 0.26592
61.0469 | 122.0993 | -60.8643 | 60.9146 | 0.089802 | -0.0451 | 0.042944 | -0.038752 | 0.06831 | 0.053534 | -0.090186 | 60.7679 | 60.776 | 60.7816 | 60.7215 | 60.851 | 61.0214 | 60.5294 | 60.7126 | 0.11727 | -0.017634 | 0.07041 | -0.011286 | 0.095776 | 0.081 | -0.06272 | 60.7954 | 60.8035 | 60.8091 | 60.749 | 60.8784 | 61.0488 | 60.5569 | 60.74 | -0.083041 | 0.23848 | -0.069343 | 0.25218
62.7188 | 122.0123 | -60.8963 | 60.8597 | 0.089802 | -0.035942 | 0.042944 | -0.047909 | 0.059155 | 0.053534 | -0.08103 | 60.7679 | 60.7714 | 60.7816 | 60.7215 | 60.8464 | 61.0214 | 60.5157 | 60.7034 | 0.11727 | -0.008476 | 0.07041 | -0.020443 | 0.086621 | 0.081 | -0.053564 | 60.7954 | 60.7989 | 60.8091 | 60.749 | 60.8738 | 61.0488 | 60.5432 | 60.7309 | -0.078463 | 0.25222 | -0.064765 | 0.26592
64.4531 | 121.9345 | -60.9146 | 60.9467 | 0.085224 | -0.0451 | 0.042944 | -0.047909 | 0.06831 | 0.053534 | -0.085608 | 60.7633 | 60.776 | 60.7862 | 60.7215 | 60.8464 | 61.0168 | 60.5249 | 60.708 | 0.11269 | -0.017634 | 0.07041 | -0.020443 | 0.095776 | 0.081 | -0.058142 | 60.7908 | 60.8035 | 60.8137 | 60.749 | 60.8738 | 61.0443 | 60.5523 | 60.7354 | -0.083042 | 0.23848 | -0.060186 | 0.26134
66.2031 | 121.9482 | -60.8917 | 60.91 | 0.080646 | -0.049678 | 0.047522 | -0.061645 | 0.063733 | 0.062691 | -0.08103 | 60.7633 | 60.776 | 60.7862 | 60.7169 | 60.851 | 61.0076 | 60.5249 | 60.6988 | 0.10811 | -0.022212 | 0.074988 | -0.034179 | 0.091199 | 0.090157 | -0.053564 | 60.7908 | 60.8035 | 60.8137 | 60.7444 | 60.8784 | 61.0351 | 60.5523 | 60.7263 | -0.08762 | 0.23848 | -0.064764 | 0.26134
67.9375 | 121.9208 | -60.9421 | 60.8826 | 0.094381 | -0.0451 | 0.042944 | -0.052488 | 0.072888 | 0.053534 | -0.076452 | 60.7679 | 60.7669 | 60.7816 | 60.7215 | 60.8464 | 61.0168 | 60.5249 | 60.6988 | 0.12185 | -0.017634 | 0.07041 | -0.025022 | 0.10035 | 0.081 | -0.048986 | 60.7954 | 60.7943 | 60.8091 | 60.749 | 60.8738 | 61.0443 | 60.5523 | 60.7263 | -0.078463 | 0.24306 | -0.064765 | 0.25676
69.6719 | 121.9711 | -60.8826 | 60.9283 | 0.094381 | -0.035942 | 0.038365 | -0.052488 | 0.06831 | 0.053534 | -0.085608 | 60.7633 | 60.7669 | 60.7816 | 60.7261 | 60.851 | 61.0259 | 60.5203 | 60.7034 | 0.12185 | -0.008476 | 0.065831 | -0.025022 | 0.095776 | 0.081 | -0.058142 | 60.7908 | 60.7943 | 60.8091 | 60.7535 | 60.8784 | 61.0534 | 60.5477 | 60.7309 | -0.08762 | 0.24306 | -0.069343 | 0.26134
71.3438 | 121.9208 | -60.9604 | 60.8688 | 0.080646 | -0.049678 | 0.042944 | -0.052488 | 0.072888 | 0.048956 | -0.08103 | 60.7588 | 60.7714 | 60.777 | 60.7169 | 60.8464 | 61.0168 | 60.5157 | 60.6988 | 0.10811 | -0.022212 | 0.07041 | -0.025022 | 0.10035 | 0.076422 | -0.053564 | 60.7862 | 60.7989 | 60.8045 | 60.7444 | 60.8738 | 61.0443 | 60.5432 | 60.7263 | -0.08762 | 0.24306 | -0.069343 | 0.26134
73.0781 | 121.9666 | -60.9283 | 60.8963 | 0.094381 | -0.035942 | 0.042944 | -0.047909 | 0.06831 | 0.058113 | -0.076452 | 60.7588 | 60.7714 | 60.777 | 60.7123 | 60.8418 | 61.0122 | 60.5203 | 60.708 | 0.12185 | -0.008476 | 0.07041 | -0.020443 | 0.095776 | 0.085579 | -0.048986 | 60.7862 | 60.7989 | 60.8045 | 60.7398 | 60.8693 | 61.0397 | 60.5477 | 60.7354 | -0.083042 | 0.23848 | -0.064765 | 0.25676
74.75 | 121.9528 | -60.9009 | 60.9192 | 0.085224 | -0.040521 | 0.042944 | -0.052488 | 0.063733 | 0.053534 | -0.08103 | 60.7542 | 60.7623 | 60.7816 | 60.7123 | 60.8464 | 61.0122 | 60.5203 | 60.6942 | 0.11269 | -0.013055 | 0.07041 | -0.025022 | 0.091199 | 0.081 | -0.053564 | 60.7816 | 60.7897 | 60.8091 | 60.7398 | 60.8738 | 61.0397 | 60.5477 | 60.7217 | -0.092199 | 0.2339 | -0.064765 | 0.26134
76.5 | 121.9254 | -60.91 | 60.9329 | 0.080646 | -0.054257 | 0.038365 | -0.047909 | 0.06831 | 0.053534 | -0.08103 | 60.7633 | 60.7623 | 60.7816 | 60.7123 | 60.8464 | 61.0168 | 60.5203 | 60.708 | 0.10811 | -0.026791 | 0.065831 | -0.020443 | 0.095776 | 0.081 | -0.053564 | 60.7908 | 60.7897 | 60.8091 | 60.7398 | 60.8738 | 61.0443 | 60.5477 | 60.7354 | -0.083042 | 0.24306 | -0.064765 | 0.26134
78.2344 | 121.994 | -60.878 | 60.9238 | 0.080646 | -0.0451 | 0.038365 | -0.047909 | 0.06831 | 0.048956 | -0.085608 | 60.7588 | 60.7714 | 60.7725 | 60.7123 | 60.8418 | 61.0076 | 60.5111 | 60.7034 | 0.10811 | -0.017634 | 0.065831 | -0.020443 | 0.095776 | 0.076422 | -0.058142 | 60.7862 | 60.7989 | 60.7999 | 60.7398 | 60.8693 | 61.0351 | 60.5386 | 60.7309 | -0.083042 | 0.24764 | -0.069343 | 0.26134
79.9531 | 121.9299 | -60.9146 | 60.9283 | 0.089802 | -0.054257 | 0.033786 | -0.047909 | 0.06831 | 0.053534 | -0.090186 | 60.7633 | 60.776 | 60.7725 | 60.7215 | 60.8464 | 61.0122 | 60.5249 | 60.7034 | 0.11727 | -0.026791 | 0.061252 | -0.020443 | 0.095776 | 0.081 | -0.06272 | 60.7908 | 60.8035 | 60.7999 | 60.749 | 60.8738 | 61.0397 | 60.5523 | 60.7309 | -0.083042 | 0.23848 | -0.073921 | 0.2476
81.625 | 121.9299 | -60.9375 | 60.8643 | 0.089802 | -0.0451 | 0.038365 | -0.052488 | 0.06831 | 0.058113 | -0.076452 | 60.7633 | 60.7623 | 60.7816 | 60.7169 | 60.8372 | 61.0122 | 60.5203 | 60.6851 | 0.11727 | -0.017634 | 0.065831 | -0.025022 | 0.095776 | 0.085579 | -0.048986 | 60.7908 | 60.7897 | 60.8091 | 60.7444 | 60.8647 | 61.0397 | 60.5477 | 60.7126 | -0.073886 | 0.24306 | -0.055609 | 0.26134
83.3594 | 121.907 | -60.9421 | 60.8734 | 0.089802 | -0.049678 | 0.029208 | -0.047909 | 0.06831 | 0.058113 | -0.08103 | 60.7633 | 60.7623 | 60.7725 | 60.7169 | 60.8372 | 61.0076 | 60.5065 | 60.6988 | 0.11727 | -0.022212 | 0.056674 | -0.020443 | 0.095776 | 0.085579 | -0.053564 | 60.7908 | 60.7897 | 60.7999 | 60.7444 | 60.8647 | 61.0351 | 60.534 | 60.7263 | -0.073886 | 0.2568 | -0.064765 | 0.26592
85.0938 | 122.0581 | -60.8734 | 60.8963 | 0.085224 | -0.049678 | 0.038365 | -0.047909 | 0.06831 | 0.044377 | -0.085608 | 60.7633 | 60.7669 | 60.7725 | 60.7123 | 60.851 | 61.0122 | 60.5111 | 60.6942 | 0.11269 | -0.022212 | 0.065831 | -0.020443 | 0.095776 | 0.071843 | -0.058142 | 60.7908 | 60.7943 | 60.7999 | 60.7398 | 60.8784 | 61.0397 | 60.5386 | 60.7217 | -0.08762 | 0.25222 | -0.078499 | 0.26134
86.7812 | 121.9299 | -60.91 | 60.9146 | 0.085224 | -0.035942 | 0.029208 | -0.047909 | 0.063733 | 0.048956 | -0.08103 | 60.7588 | 60.7623 | 60.7725 | 60.7123 | 60.8418 | 61.0122 | 60.5249 | 60.6988 | 0.11269 | -0.008476 | 0.056674 | -0.020443 | 0.091199 | 0.076422 | -0.053564 | 60.7862 | 60.7897 | 60.7999 | 60.7398 | 60.8693 | 61.0397 | 60.5523 | 60.7263 | -0.083042 | 0.2339 | -0.069343 | 0.2476
88.5312 | 122.0169 | -60.9055 | 60.8322 | 0.089802 | -0.035942 | 0.038365 | -0.052488 | 0.063733 | 0.053534 | -0.08103 | 60.7679 | 60.7714 | 60.7725 | 60.7123 | 60.8372 | 61.0122 | 60.5111 | 60.6805 | 0.11727 | -0.008476 | 0.065831 | -0.025022 | 0.091199 | 0.081 | -0.053564 | 60.7954 | 60.7989 | 60.7999 | 60.7398 | 60.8647 | 61.0397 | 60.5386 | 60.708 | -0.069307 | 0.2568 | -0.064765 | 0.26134
90.2031 | 121.962 | -60.9283 | 60.8917 | 0.089802 | -0.040521 | 0.033786 | -0.043331 | 0.063733 | 0.053534 | -0.085608 | 60.7542 | 60.7669 | 60.7725 | 60.7169 | 60.851 | 61.0076 | 60.5111 | 60.6897 | 0.11727 | -0.013055 | 0.061252 | -0.015865 | 0.091199 | 0.081 | -0.058142 | 60.7816 | 60.7943 | 60.7999 | 60.7444 | 60.8784 | 61.0351 | 60.5386 | 60.7171 | -0.096777 | 0.24306 | -0.078499 | 0.26134
91.9062 | 121.8933 | -60.9558 | 60.878 | 0.085224 | -0.040521 | 0.038365 | -0.057066 | 0.063733 | 0.053534 | -0.085608 | 60.7588 | 60.7623 | 60.7725 | 60.7169 | 60.8326 | 61.0122 | 60.5065 | 60.6897 | 0.11269 | -0.013055 | 0.065831 | -0.0296 | 0.091199 | 0.081 | -0.058142 | 60.7862 | 60.7897 | 60.7999 | 60.7444 | 60.8601 | 61.0397 | 60.534 | 60.7171 | -0.073886 | 0.25222 | -0.060187 | 0.26592
93.6406 | 122.049 | -60.8414 | 60.8917 | 0.089802 | -0.049678 | 0.029208 | -0.052488 | 0.063733 | 0.048956 | -0.085608 | 60.7496 | 60.776 | 60.7679 | 60.7123 | 60.8418 | 61.0076 | 60.5111 | 60.6988 | 0.11727 | -0.022212 | 0.056674 | -0.025022 | 0.091199 | 0.076422 | -0.058142 | 60.7771 | 60.8035 | 60.7953 | 60.7398 | 60.8693 | 61.0351 | 60.5386 | 60.7263 | -0.092199 | 0.23848 | -0.073921 | 0.25676
95.3906 | 121.907 | -60.9512 | 60.878 | 0.089802 | -0.040521 | 0.038365 | -0.057066 | 0.06831 | 0.053534 | -0.08103 | 60.7496 | 60.7577 | 60.7633 | 60.7078 | 60.8326 | 61.0122 | 60.5111 | 60.6897 | 0.11727 | -0.013055 | 0.065831 | -0.0296 | 0.095776 | 0.081 | -0.053564 | 60.7771 | 60.7852 | 60.7908 | 60.7352 | 60.8601 | 61.0397 | 60.5386 | 60.7171 | -0.083043 | 0.23848 | -0.069344 | 0.25218
97.0781 | 122.0078 | -60.8734 | 60.8734 | 0.080646 | -0.040521 | 0.029208 | -0.043331 | 0.06831 | 0.048956 | -0.076452 | 60.7588 | 60.7623 | 60.7633 | 60.7123 | 60.8326 | 61.0076 | 60.5157 | 60.6942 | 0.10811 | -0.013055 | 0.056674 | -0.015865 | 0.095776 | 0.076422 | -0.048986 | 60.7862 | 60.7897 | 60.7908 | 60.7398 | 60.8601 | 61.0351 | 60.5432 | 60.7217 | -0.073886 | 0.24306 | -0.069344 | 0.2476
98.8281 | 121.9666 | -60.878 | 60.8734 | 0.089802 | -0.0451 | 0.038365 | -0.052488 | 0.063733 | 0.053534 | -0.076452 | 60.7542 | 60.7669 | 60.777 | 60.7123 | 60.8372 | 61.0031 | 60.5157 | 60.6988 | 0.11727 | -0.017634 | 0.065831 | -0.025022 | 0.091199 | 0.081 | -0.048986 | 60.7816 | 60.7943 | 60.8045 | 60.7398 | 60.8647 | 61.0305 | 60.5432 | 60.7263 | -0.083043 | 0.23848 | -0.060187 | 0.26134
100.5469 | 121.9528 | -60.9146 | 60.8643 | 0.085224 | -0.049678 | 0.038365 | -0.052488 | 0.059155 | 0.048956 | -0.08103 | 60.7588 | 60.7714 | 60.7633 | 60.7078 | 60.8281 | 61.0076 | 60.5111 | 60.6851 | 0.11269 | -0.022212 | 0.065831 | -0.025022 | 0.086621 | 0.076422 | -0.053564 | 60.7862 | 60.7989 | 60.7908 | 60.7352 | 60.8555 | 61.0351 | 60.5386 | 60.7126 | -0.069307 | 0.24764 | -0.064765 | 0.25218
102.2188 | 122.0398 | -60.8414 | 60.8597 | 0.085224 | -0.0451 | 0.033786 | -0.047909 | 0.059155 | 0.053534 | -0.085608 | 60.7588 | 60.7623 | 60.7679 | 60.7169 | 60.8372 | 61.0076 | 60.5157 | 60.6942 | 0.11269 | -0.017634 | 0.061252 | -0.020443 | 0.086621 | 0.081 | -0.058142 | 60.7862 | 60.7897 | 60.7953 | 60.7444 | 60.8647 | 61.0351 | 60.5432 | 60.7217 | -0.078464 | 0.24306 | -0.069343 | 0.25218
103.9531 | 122.0352 | -60.8368 | 60.878 | 0.085224 | -0.049678 | 0.029208 | -0.052488 | 0.059155 | 0.058113 | -0.090186 | 60.7542 | 60.7623 | 60.7679 | 60.7078 | 60.8418 | 61.0031 | 60.5157 | 60.6897 | 0.11269 | -0.022212 | 0.056674 | -0.025022 | 0.086621 | 0.085579 | -0.06272 | 60.7816 | 60.7897 | 60.7953 | 60.7352 | 60.8693 | 61.0305 | 60.5432 | 60.7171 | -0.087621 | 0.23848 | -0.073921 | 0.25218
105.6875 | 121.9711 | -60.8643 | 60.8917 | 0.085224 | -0.049678 | 0.024629 | -0.047909 | 0.06831 | 0.053534 | -0.090186 | 60.7633 | 60.7623 | 60.7679 | 60.7078 | 60.8281 | 61.0031 | 60.5065 | 60.6851 | 0.11269 | -0.022212 | 0.052095 | -0.020443 | 0.095776 | 0.081 | -0.06272 | 60.7908 | 60.7897 | 60.7953 | 60.7352 | 60.8555 | 61.0305 | 60.534 | 60.7126 | -0.064729 | 0.2568 | -0.060186 | 0.26134
107.3594 | 121.9574 | -60.9055 | 60.8734 | 0.085224 | -0.049678 | 0.029208 | -0.047909 | 0.063733 | 0.053534 | -0.076452 | 60.7542 | 60.7623 | 60.777 | 60.7032 | 60.851 | 61.0031 | 60.5065 | 60.6897 | 0.11269 | -0.022212 | 0.056674 | -0.020443 | 0.091199 | 0.081 | -0.048986 | 60.7816 | 60.7897 | 60.8045 | 60.7306 | 60.8784 | 61.0305 | 60.534 | 60.7171 | -0.096777 | 0.24764 | -0.073921 | 0.2705
109.0312 | 121.8933 | -60.8917 | 60.9146 | 0.085224 | -0.049678 | 0.033786 | -0.052488 | 0.063733 | 0.048956 | -0.076452 | 60.745 | 60.7623 | 60.7679 | 60.7123 | 60.8372 | 60.9985 | 60.5157 | 60.6897 | 0.11269 | -0.022212 | 0.061252 | -0.025022 | 0.091199 | 0.076422 | -0.048986 | 60.7725 | 60.7897 | 60.7953 | 60.7398 | 60.8647 | 61.0259 | 60.5432 | 60.7171 | -0.0922 | 0.22932 | -0.069343 | 0.25218
110.7812 | 122.0444 | -60.8322 | 60.8734 | 0.085224 | -0.054257 | 0.024629 | -0.047909 | 0.063733 | 0.058113 | -0.085608 | 60.7542 | 60.7623 | 60.7679 | 60.7078 | 60.8418 | 61.0031 | 60.5111 | 60.6942 | 0.11269 | -0.026791 | 0.052095 | -0.020443 | 0.091199 | 0.085579 | -0.058142 | 60.7816 | 60.7897 | 60.7953 | 60.7352 | 60.8693 | 61.0305 | 60.5386 | 60.7217 | -0.087621 | 0.24306 | -0.073921 | 0.25676
112.5312 | 122.0078 | -60.8597 | 60.8871 | 0.085224 | -0.054257 | 0.029208 | -0.052488 | 0.072888 | 0.058113 | -0.08103 | 60.7496 | 60.7623 | 60.7725 | 60.7078 | 60.8464 | 60.9985 | 60.5065 | 60.6942 | 0.11269 | -0.026791 | 0.056674 | -0.025022 | 0.10035 | 0.085579 | -0.053564 | 60.7771 | 60.7897 | 60.7999 | 60.7352 | 60.8738 | 61.0259 | 60.534 | 60.7217 | -0.096777 | 0.24306 | -0.073921 | 0.26592
114.2031 | 122.0352 | -60.8459 | 60.8734 | 0.085224 | -0.0451 | 0.033786 | -0.052488 | 0.059155 | 0.053534 | -0.08103 | 60.7542 | 60.7623 | 60.7679 | 60.7078 | 60.8235 | 61.0031 | 60.5065 | 60.6942 | 0.11269 | -0.017634 | 0.061252 | -0.025022 | 0.086621 | 0.081 | -0.053564 | 60.7816 | 60.7897 | 60.7953 | 60.7352 | 60.851 | 61.0305 | 60.534 | 60.7217 | -0.069308 | 0.24764 | -0.055608 | 0.26134
115.9531 | 121.9711 | -60.8505 | 60.8643 | 0.085224 | -0.049678 | 0.033786 | -0.047909 | 0.06831 | 0.053534 | -0.08103 | 60.7496 | 60.7531 | 60.7679 | 60.7078 | 60.8326 | 60.9985 | 60.502 | 60.6897 | 0.11269 | -0.022212 | 0.061252 | -0.020443 | 0.095776 | 0.081 | -0.053564 | 60.7771 | 60.7806 | 60.7953 | 60.7352 | 60.8601 | 61.0259 | 60.5294 | 60.7171 | -0.083043 | 0.24764 | -0.064765 | 0.26592
117.7031 | 121.9025 | -60.9192 | 60.9009 | 0.089802 | -0.0451 | 0.038365 | -0.043331 | 0.059155 | 0.058113 | -0.076452 | 60.7496 | 60.7623 | 60.7587 | 60.7078 | 60.8372 | 60.9939 | 60.5111 | 60.6897 | 0.11727 | -0.017634 | 0.065831 | -0.015865 | 0.086621 | 0.085579 | -0.048986 | 60.7771 | 60.7897 | 60.7862 | 60.7352 | 60.8647 | 61.0214 | 60.5386 | 60.7171 | -0.087621 | 0.23848 | -0.0785 | 0.2476
119.375 | 121.907 | -60.8963 | 60.9146 | 0.089802 | -0.054257 | 0.033786 | -0.052488 | 0.063733 | 0.048956 | -0.090186 | 60.7496 | 60.7577 | 60.7679 | 60.7032 | 60.8372 | 61.0076 | 60.5111 | 60.6897 | 0.11727 | -0.026791 | 0.061252 | -0.025022 | 0.091199 | 0.076422 | -0.06272 | 60.7771 | 60.7852 | 60.7953 | 60.7306 | 60.8647 | 61.0351 | 60.5386 | 60.7171 | -0.087621 | 0.23848 | -0.069343 | 0.25676
121.1094 | 122.0215 | -60.8414 | 60.8963 | 0.085224 | -0.054257 | 0.038365 | -0.052488 | 0.059155 | 0.048956 | -0.090186 | 60.7496 | 60.7669 | 60.7587 | 60.6986 | 60.8372 | 60.9939 | 60.5111 | 60.6851 | 0.11269 | -0.026791 | 0.065831 | -0.025022 | 0.086621 | 0.076422 | -0.06272 | 60.7771 | 60.7943 | 60.7862 | 60.7261 | 60.8647 | 61.0214 | 60.5386 | 60.7126 | -0.087621 | 0.23848 | -0.0785 | 0.2476
122.8594 | 121.9391 | -60.91 | 60.8551 | 0.085224 | -0.0451 | 0.038365 | -0.052488 | 0.063733 | 0.058113 | -0.085608 | 60.7542 | 60.7577 | 60.7679 | 60.6986 | 60.8281 | 60.9939 | 60.5111 | 60.6942 | 0.11269 | -0.017634 | 0.065831 | -0.025022 | 0.091199 | 0.085579 | -0.058142 | 60.7816 | 60.7852 | 60.7953 | 60.7261 | 60.8555 | 61.0214 | 60.5386 | 60.7217 | -0.073886 | 0.24306 | -0.060186 | 0.25676
124.5312 | 121.8796 | -60.8871 | 60.91 | 0.089802 | -0.040521 | 0.038365 | -0.047909 | 0.063733 | 0.062691 | -0.076452 | 60.745 | 60.7577 | 60.7679 | 60.7032 | 60.8281 | 60.9985 | 60.502 | 60.6897 | 0.11727 | -0.013055 | 0.065831 | -0.020443 | 0.091199 | 0.090157 | -0.048986 | 60.7725 | 60.7852 | 60.7953 | 60.7306 | 60.8555 | 61.0259 | 60.5294 | 60.7171 | -0.083043 | 0.24306 | -0.060186 | 0.26592
126.2656 | 122.0123 | -60.8597 | 60.878 | 0.089802 | -0.035942 | 0.024629 | -0.047909 | 0.063733 | 0.053534 | -0.090186 | 60.745 | 60.7577 | 60.7633 | 60.694 | 60.8281 | 60.9985 | 60.502 | 60.6851 | 0.11727 | -0.008476 | 0.052095 | -0.020443 | 0.091199 | 0.081 | -0.06272 | 60.7725 | 60.7852 | 60.7908 | 60.7215 | 60.8555 | 61.0259 | 60.5294 | 60.7126 | -0.083043 | 0.24306 | -0.064765 | 0.26134
127.9375 | 122.0352 | -60.8414 | 60.878 | 0.089802 | -0.0451 | 0.029208 | -0.052488 | 0.06831 | 0.053534 | -0.090186 | 60.7542 | 60.7531 | 60.7633 | 60.6986 | 60.8372 | 61.0031 | 60.502 | 60.6805 | 0.11727 | -0.017634 | 0.056674 | -0.025022 | 0.095776 | 0.081 | -0.06272 | 60.7816 | 60.7806 | 60.7908 | 60.7261 | 60.8647 | 61.0305 | 60.5294 | 60.708 | -0.083043 | 0.25222 | -0.073922 | 0.26134
129.6719 | 122.0169 | -60.8322 | 60.8551 | 0.089802 | -0.0451 | 0.029208 | -0.047909 | 0.063733 | 0.058113 | -0.085608 | 60.7496 | 60.7577 | 60.7633 | 60.694 | 60.8326 | 60.9939 | 60.5065 | 60.6851 | 0.11727 | -0.017634 | 0.056674 | -0.020443 | 0.091199 | 0.085579 | -0.058142 | 60.7771 | 60.7852 | 60.7908 | 60.7215 | 60.8601 | 61.0214 | 60.534 | 60.7126 | -0.083043 | 0.24306 | -0.069344 | 0.25676
131.4062 | 122.0169 | -60.8551 | 60.8231 | 0.089802 | -0.040521 | 0.038365 | -0.052488 | 0.063733 | 0.053534 | -0.08103 | 60.745 | 60.7577 | 60.7587 | 60.694 | 60.8281 | 60.9985 | 60.4974 | 60.6805 | 0.11727 | -0.013055 | 0.065831 | -0.025022 | 0.091199 | 0.081 | -0.053564 | 60.7725 | 60.7852 | 60.7862 | 60.7215 | 60.8555 | 61.0259 | 60.5248 | 60.708 | -0.083043 | 0.24764 | -0.069343 | 0.26134
133.1562 | 121.8887 | -60.9238 | 60.878 | 0.085224 | -0.035942 | 0.033786 | -0.043331 | 0.063733 | 0.048956 | -0.08103 | 60.7542 | 60.7531 | 60.7587 | 60.6986 | 60.8235 | 60.9985 | 60.502 | 60.6851 | 0.11269 | -0.008476 | 0.061252 | -0.015865 | 0.091199 | 0.076422 | -0.053564 | 60.7816 | 60.7806 | 60.7862 | 60.7261 | 60.851 | 61.0259 | 60.5294 | 60.7126 | -0.069308 | 0.25222 | -0.064765 | 0.25676
134.9062 | 121.9025 | -60.9329 | 60.8414 | 0.089802 | -0.040521 | 0.033786 | -0.047909 | 0.072888 | 0.053534 | -0.08103 | 60.7542 | 60.7531 | 60.7633 | 60.7078 | 60.8326 | 60.9893 | 60.4974 | 60.6759 | 0.11727 | -0.013055 | 0.061252 | -0.020443 | 0.10035 | 0.081 | -0.053564 | 60.7816 | 60.7806 | 60.7908 | 60.7352 | 60.8601 | 61.0168 | 60.5248 | 60.7034 | -0.078465 | 0.2568 | -0.069344 | 0.26592
136.6562 | 121.9025 | -60.9055 | 60.9238 | 0.085224 | -0.031363 | 0.042944 | -0.052488 | 0.06831 | 0.058113 | -0.076452 | 60.7496 | 60.7623 | 60.7541 | 60.6986 | 60.8372 | 60.9985 | 60.4974 | 60.6805 | 0.11269 | -0.003897 | 0.07041 | -0.025022 | 0.095776 | 0.085579 | -0.048986 | 60.7771 | 60.7897 | 60.7816 | 60.7261 | 60.8647 | 61.0259 | 60.5248 | 60.708 | -0.087621 | 0.25222 | -0.083078 | 0.25676
138.3906 | 121.9162 | -60.8643 | 60.8871 | 0.085224 | -0.040521 | 0.038365 | -0.052488 | 0.063733 | 0.053534 | -0.08103 | 60.745 | 60.7577 | 60.7587 | 60.7032 | 60.8281 | 60.9893 | 60.502 | 60.6805 | 0.11269 | -0.013055 | 0.065831 | -0.025022 | 0.091199 | 0.081 | -0.053564 | 60.7725 | 60.7852 | 60.7862 | 60.7306 | 60.8555 | 61.0168 | 60.5294 | 60.708 | -0.083043 | 0.24306 | -0.069343 | 0.25676
140.0625 | 121.9986 | -60.8459 | 60.8368 | 0.080646 | -0.040521 | 0.029208 | -0.061645 | 0.063733 | 0.058113 | -0.085608 | 60.745 | 60.7577 | 60.7587 | 60.694 | 60.8189 | 60.9939 | 60.4836 | 60.6668 | 0.10811 | -0.013055 | 0.056674 | -0.034179 | 0.091199 | 0.085579 | -0.058142 | 60.7725 | 60.7852 | 60.7862 | 60.7215 | 60.8464 | 61.0214 | 60.5111 | 60.6942 | -0.073887 | 0.26137 | -0.060187 | 0.27507
141.8125 | 121.9849 | -60.8871 | 60.8597 | 0.089802 | -0.031363 | 0.033786 | -0.052488 | 0.06831 | 0.053534 | -0.085608 | 60.7404 | 60.7531 | 60.7679 | 60.694 | 60.8235 | 60.9939 | 60.4928 | 60.6759 | 0.11727 | -0.003897 | 0.061252 | -0.025022 | 0.095776 | 0.081 | -0.058142 | 60.7679 | 60.7806 | 60.7953 | 60.7215 | 60.851 | 61.0214 | 60.5203 | 60.7034 | -0.083043 | 0.24764 | -0.055608 | 0.27507
143.5469 | 121.8979 | -60.9192 | 60.8688 | 0.089802 | -0.0451 | 0.029208 | -0.052488 | 0.06831 | 0.044377 | -0.076452 | 60.745 | 60.7577 | 60.7541 | 60.694 | 60.8235 | 60.9939 | 60.4928 | 60.6759 | 0.11727 | -0.017634 | 0.056674 | -0.025022 | 0.095776 | 0.071843 | -0.048986 | 60.7725 | 60.7852 | 60.7816 | 60.7215 | 60.851 | 61.0214 | 60.5203 | 60.7034 | -0.078465 | 0.25222 | -0.069343 | 0.26134
145.2812 | 121.9986 | -60.8414 | 60.8917 | 0.094381 | -0.031363 | 0.038365 | -0.043331 | 0.06831 | 0.048956 | -0.08103 | 60.745 | 60.7485 | 60.7496 | 60.694 | 60.8464 | 60.9985 | 60.4974 | 60.6851 | 0.12185 | -0.003897 | 0.065831 | -0.015865 | 0.095776 | 0.076422 | -0.053564 | 60.7725 | 60.776 | 60.777 | 60.7215 | 60.8738 | 61.0259 | 60.5248 | 60.7126 | -0.10136 | 0.24764 | -0.096813 | 0.25218
146.9531 | 121.8842 | -60.9009 | 60.8826 | 0.085224 | -0.035942 | 0.029208 | -0.052488 | 0.063733 | 0.048956 | -0.08103 | 60.745 | 60.744 | 60.7633 | 60.6986 | 60.8235 | 61.0031 | 60.5111 | 60.6805 | 0.11269 | -0.008476 | 0.056674 | -0.025022 | 0.091199 | 0.076422 | -0.053564 | 60.7725 | 60.7714 | 60.7908 | 60.7261 | 60.851 | 61.0305 | 60.5386 | 60.708 | -0.078465 | 0.2339 | -0.060187 | 0.25218
148.6875 | 121.9208 | -60.8963 | 60.9055 | 0.089802 | -0.035942 | 0.038365 | -0.047909 | 0.077466 | 0.044377 | -0.071874 | 60.7404 | 60.7531 | 60.7633 | 60.6986 | 60.8281 | 60.9985 | 60.502 | 60.6851 | 0.11727 | -0.008476 | 0.065831 | -0.020443 | 0.10493 | 0.071843 | -0.044408 | 60.7679 | 60.7806 | 60.7908 | 60.7261 | 60.8555 | 61.0259 | 60.5294 | 60.7126 | -0.087621 | 0.23848 | -0.064765 | 0.26134
150.4219 | 121.9391 | -60.9283 | 60.8414 | 0.085224 | -0.026784 | 0.029208 | -0.052488 | 0.072888 | 0.058113 | -0.071874 | 60.7313 | 60.744 | 60.7541 | 60.6849 | 60.8281 | 60.9985 | 60.5065 | 60.6851 | 0.11269 | 0.000682 | 0.056674 | -0.025022 | 0.10035 | 0.085579 | -0.044408 | 60.7588 | 60.7714 | 60.7816 | 60.7123 | 60.8555 | 61.0259 | 60.534 | 60.7126 | -0.096778 | 0.22475 | -0.073921 | 0.2476
152.1094 | 122.0398 | -60.8368 | 60.8597 | 0.094381 | -0.040521 | 0.029208 | -0.052488 | 0.06831 | 0.044377 | -0.085608 | 60.7359 | 60.7348 | 60.7496 | 60.6803 | 60.8372 | 60.9985 | 60.502 | 60.6851 | 0.12185 | -0.013055 | 0.056674 | -0.025022 | 0.095776 | 0.071843 | -0.058142 | 60.7633 | 60.7623 | 60.777 | 60.7077 | 60.8647 | 61.0259 | 60.5294 | 60.7126 | -0.10136 | 0.2339 | -0.087657 | 0.2476
153.8594 | 121.9116 | -69.2276 | 52.4963 | 0.089802 | -0.022205 | 0.038365 | -0.043331 | 0.077466 | 0.048956 | -0.076452 | 52.6228 | 52.6257 | 52.5819 | 52.525 | 68.9818 | 69.1566 | 68.6515 | 68.8159 | 0.11727 | 0.005261 | 0.065831 | -0.015865 | 0.10493 | 0.076422 | -0.048986 | 52.6502 | 52.6532 | 52.6094 | 52.5525 | 69.0093 | 69.1841 | 68.679 | 68.8434 | -16.359 | -16.0287 | -16.3999 | -16.0696
155.5938 | 121.875 | -70.4224 | 51.3428 | 0.094381 | -0.031363 | 0.033786 | -0.043331 | 0.082044 | 0.058113 | -0.076452 | 51.2721 | 51.2338 | 51.2405 | 51.1834 | 70.3324 | 70.5025 | 69.9884 | 70.1665 | 0.12185 | -0.003897 | 0.061252 | -0.015865 | 0.10951 | 0.085579 | -0.048986 | 51.2996 | 51.2612 | 51.2679 | 51.2108 | 70.3598 | 70.53 | 70.0158 | 70.194 | -19.0602 | -18.7163 | -19.0919 | -18.7479
157.3594 | 122.0215 | -70.5139 | 51.1688 | 0.085224 | -0.022205 | 0.042944 | -0.043331 | 0.072888 | 0.058113 | -0.067295 | 51.1073 | 51.0735 | 51.0573 | 51.0048 | 70.5017 | 70.6811 | 70.1669 | 70.345 | 0.11269 | 0.005261 | 0.07041 | -0.015865 | 0.10035 | 0.085579 | -0.039829 | 51.1348 | 51.101 | 51.0848 | 51.0323 | 70.5292 | 70.7086 | 70.1944 | 70.3725 | -19.3945 | -19.0596 | -19.4444 | -19.1096
159.0312 | 121.8887 | -70.784 | 50.9811 | 0.089802 | -0.022205 | 0.042944 | -0.043331 | 0.072888 | 0.062691 | -0.071874 | 50.8784 | 50.8354 | 50.8376 | 50.7758 | 70.7261 | 70.8963 | 70.3913 | 70.5694 | 0.11727 | 0.005261 | 0.07041 | -0.015865 | 0.10035 | 0.090157 | -0.044408 | 50.9058 | 50.8629 | 50.8651 | 50.8033 | 70.7535 | 70.9237 | 70.4187 | 70.5968 | -19.8477 | -19.5129 | -19.8885 | -19.5537
160.75 | 121.9757 | -60.8963 | 60.8368 | 0.089802 | -0.035942 | 0.033786 | -0.057066 | 0.063733 | 0.053534 | -0.071874 | 60.6992 | 60.7073 | 60.7129 | 60.6528 | 60.8601 | 61.0214 | 60.534 | 60.7126 | 0.11727 | -0.008476 | 0.061252 | -0.0296 | 0.091199 | 0.081 | -0.044408 | 60.7267 | 60.7348 | 60.7404 | 60.6803 | 60.8876 | 61.0488 | 60.5615 | 60.74 | -0.16088 | 0.16523 | -0.14717 | 0.17893
162.4219 | 121.8567 | -60.9558 | 60.8368 | 0.089802 | -0.035942 | 0.033786 | -0.047909 | 0.072888 | 0.044377 | -0.08103 | 60.7084 | 60.7165 | 60.7129 | 60.6437 | 60.8601 | 61.0214 | 60.534 | 60.7171 | 0.11727 | -0.008476 | 0.061252 | -0.020443 | 0.10035 | 0.071843 | -0.053564 | 60.7359 | 60.744 | 60.7404 | 60.6711 | 60.8876 | 61.0488 | 60.5615 | 60.7446 | -0.15172 | 0.17438 | -0.14717 | 0.17893
164.0938 | 121.994 | -60.8871 | 60.8231 | 0.094381 | -0.040521 | 0.029208 | -0.052488 | 0.063733 | 0.048956 | -0.085608 | 60.6992 | 60.7028 | 60.6992 | 60.6437 | 60.8647 | 61.0351 | 60.534 | 60.7126 | 0.12185 | -0.013055 | 0.056674 | -0.025022 | 0.091199 | 0.076422 | -0.058142 | 60.7267 | 60.7302 | 60.7267 | 60.6711 | 60.8922 | 61.0626 | 60.5615 | 60.74 | -0.16545 | 0.16523 | -0.16549 | 0.16519
165.8281 | 121.8887 | -60.9558 | 60.8093 | 0.085224 | -0.0451 | 0.038365 | -0.052488 | 0.072888 | 0.048956 | -0.085608 | 60.6992 | 60.6982 | 60.6992 | 60.6482 | 60.8647 | 61.0305 | 60.534 | 60.7171 | 0.11269 | -0.017634 | 0.065831 | -0.025022 | 0.10035 | 0.076422 | -0.058142 | 60.7267 | 60.7256 | 60.7267 | 60.6757 | 60.8922 | 61.058 | 60.5615 | 60.7446 | -0.16545 | 0.16523 | -0.16549 | 0.16519
167.5 | 121.8658 | -60.9604 | 60.8002 | 0.080646 | -0.040521 | 0.033786 | -0.052488 | 0.072888 | 0.058113 | -0.076452 | 60.6809 | 60.6844 | 60.69 | 60.6299 | 60.883 | 61.0534 | 60.5569 | 60.7309 | 0.10811 | -0.013055 | 0.061252 | -0.025022 | 0.10035 | 0.085579 | -0.048986 | 60.7084 | 60.7119 | 60.7175 | 60.6574 | 60.9105 | 61.0809 | 60.5844 | 60.7583 | -0.20208 | 0.12402 | -0.19295 | 0.13315
169.2344 | 121.8842 | -61.0062 | 60.7773 | 0.080646 | -0.0451 | 0.042944 | -0.043331 | 0.072888 | 0.048956 | -0.08103 | 60.6397 | 60.657 | 60.658 | 60.5933 | 60.915 | 61.0809 | 60.5889 | 60.7675 | 0.10811 | -0.017634 | 0.07041 | -0.015865 | 0.10035 | 0.076422 | -0.053564 | 60.6672 | 60.6844 | 60.6855 | 60.6207 | 60.9425 | 61.1084 | 60.6164 | 60.795 | -0.27533 | 0.050766 | -0.25705 | 0.069049
170.9062 | 121.8658 | -60.9833 | 60.791 | 0.094381 | -0.0451 | 0.038365 | -0.047909 | 0.077466 | 0.058113 | -0.08103 | 60.6351 | 60.6387 | 60.6305 | 60.5795 | 60.9425 | 61.09 | 60.5981 | 60.7904 | 0.12185 | -0.017634 | 0.065831 | -0.020443 | 0.10493 | 0.085579 | -0.053564 | 60.6626 | 60.6661 | 60.658 | 60.607 | 60.97 | 61.1175 | 60.6256 | 60.8179 | -0.30738 | 0.03703 | -0.31199 | 0.032422
172.6406 | 121.8979 | -61.084 | 60.6766 | 0.089802 | -0.040521 | 0.038365 | -0.047909 | 0.072888 | 0.062691 | -0.08103 | 59.2021 | 59.2375 | 59.2067 | 59.1509 | 62.5449 | 62.5367 | 62.0586 | 62.26 | 0.11727 | -0.013055 | 0.065831 | -0.020443 | 0.10035 | 0.090157 | -0.053564 | 59.2295 | 59.265 | 59.2341 | 59.1784 | 62.5723 | 62.5642 | 62.0861 | 62.2874 | -3.3428 | -2.8565 | -3.3382 | -2.8519
174.375 | 121.8063 | -70.9488 | 50.8301 | 0.094381 | -0.017627 | 0.065837 | -0.020438 | 0.095778 | 0.071848 | -0.053561 | 27.1206 | 26.9752 | 27.0534 | 26.9969 | 94.4135 | 94.4596 | 94.1211 | 94.1927 | 0.12185 | 0.009839 | 0.093303 | 0.007028 | 0.12324 | 0.099314 | -0.026095 | 27.148 | 27.0027 | 27.0809 | 27.0244 | 94.441 | 94.487 | 94.1485 | 94.2202 | -67.293 | -67.0005 | -67.3601 | -67.0676
176.0625 | 121.9528 | -70.3995 | 51.329 | 0.089802 | -0.026784 | 0.042944 | -0.038752 | 0.077466 | 0.062691 | -0.071874 | 51.0844 | 51.0369 | 51.039 | 50.9819 | 70.5338 | 70.6994 | 70.2493 | 70.4229 | 0.11727 | 0.000682 | 0.07041 | -0.011286 | 0.10493 | 0.090157 | -0.044408 | 51.1119 | 51.0643 | 51.0665 | 51.0094 | 70.5613 | 70.7269 | 70.2768 | 70.4503 | -19.4494 | -19.165 | -19.4948 | -19.2103
177.8125 | 121.907 | -69.7861 | 52.034 | 0.094381 | -0.026784 | 0.042944 | -0.038752 | 0.072888 | 0.053534 | -0.067295 | 50.3335 | 50.4645 | 50.3431 | 50.3271 | 71.2526 | 71.3861 | 70.9178 | 71.1462 | 0.12185 | 0.000682 | 0.07041 | -0.011286 | 0.10035 | 0.081 | -0.039829 | 50.361 | 50.492 | 50.3706 | 50.3546 | 71.28 | 71.4136 | 70.9453 | 71.1737 | -20.919 | -20.5843 | -20.9094 | -20.5747
179.5625 | 121.9482 | -71.4386 | 50.2533 | 0.094381 | -0.031363 | 0.042944 | -0.047909 | 0.077466 | 0.062691 | -0.067295 | 50.3289 | 50.3455 | 50.3431 | 50.2859 | 71.2205 | 71.3815 | 70.8857 | 71.0638 | 0.12185 | -0.003897 | 0.07041 | -0.020443 | 0.10493 | 0.090157 | -0.039829 | 50.3564 | 50.3729 | 50.3706 | 50.3133 | 71.248 | 71.409 | 70.9132 | 71.0913 | -20.8916 | -20.5568 | -20.8774 | -20.5426
181.2344 | 121.8979 | -73.2422 | 48.4177 | 0.089802 | -0.026784 | 0.042944 | -0.038752 | 0.077466 | 0.062691 | -0.067295 | 48.264 | 48.2804 | 48.2783 | 48.2253 | 73.2807 | 73.4462 | 72.946 | 73.1194 | 0.11727 | 0.000682 | 0.07041 | -0.011286 | 0.10493 | 0.090157 | -0.039829 | 48.2915 | 48.3079 | 48.3058 | 48.2528 | 73.3082 | 73.4737 | 72.9735 | 73.1469 | -25.0167 | -24.682 | -25.0024 | -24.6677
182.9844 | 121.8887 | -72.3358 | 49.4064 | 0.089802 | -0.035942 | 0.047522 | -0.034174 | 0.077466 | 0.062691 | -0.067295 | 48.9829 | 48.9993 | 48.9788 | 48.9305 | 72.5894 | 72.7412 | 72.2409 | 72.4281 | 0.11727 | -0.008476 | 0.074988 | -0.006708 | 0.10493 | 0.090157 | -0.039829 | 49.0103 | 49.0268 | 49.0063 | 48.958 | 72.6169 | 72.7687 | 72.2684 | 72.4556 | -23.6065 | -23.2581 | -23.6106 | -23.2621
184.7188 | 122.0078 | -109.5612 | 12.0758 | 0.085224 | -0.00389 | 0.079572 | -0.006703 | 0.10493 | 0.09474 | -0.039826 | 12.071 | 12.1169 | 12.0275 | 12.051 | 109.7413 | 109.7183 | 109.3579 | 109.5662 | 0.11269 | 0.023576 | 0.10704 | 0.020763 | 0.1324 | 0.12221 | -0.01236 | 12.0985 | 12.1444 | 12.055 | 12.0784 | 109.7687 | 109.7457 | 109.3854 | 109.5937 | -97.6702 | -97.2869 | -97.7138 | -97.3304
186.4062 | 122.0032 | -110.2295 | 11.4395 | 0.085224 | -0.008469 | 0.079572 | -0.006703 | 0.10493 | 0.090161 | -0.035248 | 11.3339 | 11.3843 | 11.2767 | 11.1306 | 110.2723 | 110.4599 | 109.9302 | 110.3125 | 0.11269 | 0.018997 | 0.10704 | 0.020763 | 0.1324 | 0.11763 | -0.007782 | 11.3614 | 11.4118 | 11.3041 | 11.158 | 110.2998 | 110.4874 | 109.9577 | 110.34 | -98.9384 | -98.5963 | -98.9957 | -98.6536
188.1562 | 121.9162 | -110.4584 | 11.261 | 0.085224 | -0.008469 | 0.074994 | -0.002124 | 0.11409 | 0.09474 | -0.039826 | 11.3156 | 11.3752 | 11.2629 | 11.1123 | 110.2769 | 110.4828 | 109.9485 | 110.3262 | 0.11269 | 0.018997 | 0.10246 | 0.025342 | 0.14156 | 0.12221 | -0.01236 | 11.3431 | 11.4026 | 11.2904 | 11.1397 | 110.3044 | 110.5103 | 109.976 | 110.3537 | -98.9613 | -98.633 | -99.014 | -98.6856
189.8906 | 121.9345 | -110.8337 | 10.9177 | 0.094381 | -0.013048 | 0.079572 | -0.002124 | 0.11867 | 0.090161 | -0.044405 | 10.8394 | 10.899 | 10.7914 | 10.636 | 110.7576 | 110.9452 | 110.4247 | 110.7978 | 0.12185 | 0.014418 | 0.10704 | 0.025342 | 0.14613 | 0.11763 | -0.016939 | 10.8669 | 10.9264 | 10.8188 | 10.6635 | 110.7851 | 110.9726 | 110.4522 | 110.8252 | -99.9182 | -99.5853 | -99.9663 | -99.6333
191.5625 | 121.8658 | -111.0718 | 10.7071 | 0.089802 | -0.00389 | 0.074994 | -0.011281 | 0.11409 | 0.09474 | -0.035248 | 10.5922 | 10.6471 | 10.5441 | 10.3934 | 110.9957 | 111.1924 | 110.6674 | 110.8161 | 0.11727 | 0.023576 | 0.10246 | 0.016185 | 0.14156 | 0.12221 | -0.007782 | 10.6197 | 10.6746 | 10.5716 | 10.4208 | 111.0232 | 111.2199 | 110.6948 | 110.8436 | -100.4035 | -100.0752 | -100.4515 | -100.1232
193.3125 | 121.8521 | -111.4426 | 10.3455 | 0.089802 | -0.013048 | 0.079572 | -0.011281 | 0.11409 | 0.09474 | -0.039826 | 10.2992 | 10.3541 | 10.2511 | 10.1003 | 111.3345 | 111.4808 | 110.9833 | 111.1366 | 0.11727 | 0.014418 | 0.10704 | 0.016185 | 0.14156 | 0.12221 | -0.01236 | 10.3266 | 10.3815 | 10.2786 | 10.1278 | 111.3619 | 111.5083 | 111.0107 | 111.164 | -101.0353 | -100.6841 | -101.0833 | -100.7321
195.0469 | 121.9574 | -111.0764 | 10.6064 | 0.094381 | -0.008469 | 0.079572 | -0.011281 | 0.11867 | 0.090161 | -0.035248 | 10.4869 | 10.551 | 10.4297 | 10.2789 | 111.0964 | 111.2931 | 110.7772 | 110.9214 | 0.12185 | 0.018997 | 0.10704 | 0.016185 | 0.14613 | 0.11763 | -0.007782 | 10.5143 | 10.5784 | 10.4571 | 10.3063 | 111.1239 | 111.3206 | 110.8047 | 110.9489 | -100.6095 | -100.2904 | -100.6667 | -100.3476
196.7188 | 121.8567 | -111.5112 | 10.2539 | 0.094381 | -0.008469 | 0.074994 | -0.011281 | 0.10951 | 0.085583 | -0.044405 | 10.2717 | 10.322 | 10.2145 | 10.0637 | 111.3116 | 111.5083 | 110.9878 | 111.1274 | 0.12185 | 0.018997 | 0.10246 | 0.016185 | 0.13698 | 0.11305 | -0.016939 | 10.2992 | 10.3495 | 10.242 | 10.0911 | 111.339 | 111.5357 | 111.0153 | 111.1549 | -101.0399 | -100.7162 | -101.0971 | -100.7733
198.4531 | 121.8704 | -111.4151 | 10.3775 | 0.089802 | -0.013048 | 0.074994 | -0.002124 | 0.10951 | 0.081005 | -0.035248 | 10.3358 | 10.3816 | 10.2832 | 10.1232 | 111.2566 | 111.4533 | 110.9283 | 111.0725 | 0.11727 | 0.014418 | 0.10246 | 0.025342 | 0.13698 | 0.10847 | -0.007782 | 10.3633 | 10.409 | 10.3106 | 10.1507 | 111.2841 | 111.4808 | 110.9558 | 111.0999 | -100.9209 | -100.5925 | -100.9735 | -100.6451
200.1875 | 121.9528 | -111.8271 | 9.8969 | 0.089802 | -0.017627 | 0.074994 | -0.011281 | 0.10493 | 0.090161 | -0.039826 | 9.9649 | 10.0198 | 9.9169 | 9.766 | 111.6321 | 111.8104 | 111.2992 | 111.4387 | 0.11727 | 0.009839 | 0.10246 | 0.016185 | 0.1324 | 0.11763 | -0.01236 | 9.9924 | 10.0473 | 9.9444 | 9.7935 | 111.6595 | 111.8379 | 111.3266 | 111.4662 | -101.6671 | -101.3342 | -101.7151 | -101.3823
201.9219 | 121.8567 | -111.969 | 9.8328 | 0.089802 | -0.017627 | 0.074994 | -0.006703 | 0.10951 | 0.090161 | -0.044405 | 9.7131 | 9.768 | 9.656 | 9.505 | 111.9113 | 112.0668 | 111.5739 | 111.7317 | 0.11727 | 0.009839 | 0.10246 | 0.020763 | 0.13698 | 0.11763 | -0.016939 | 9.7406 | 9.7955 | 9.6834 | 9.5325 | 111.9388 | 112.0943 | 111.6013 | 111.7592 | -102.1982 | -101.8608 | -102.2554 | -101.9179
203.5938 | 121.7606 | -67.2272 | 54.6341 | 0.089802 | -0.040521 | 0.047522 | -0.047909 | 0.077466 | 0.058113 | -0.071874 | 53.4515 | 53.5369 | 53.4793 | 53.4454 | 68.0662 | 68.2227 | 67.745 | 67.9461 | 0.11727 | -0.013055 | 0.074988 | -0.020443 | 0.10493 | 0.085579 | -0.044408 | 53.4789 | 53.5644 | 53.5067 | 53.4729 | 68.0936 | 68.2501 | 67.7724 | 67.9735 | -14.6147 | -14.2935 | -14.5869 | -14.2657
205.3281 | 121.8109 | -67.7353 | 54.0665 | 0.098959 | -0.040521 | 0.042944 | -0.043331 | 0.06831 | 0.067269 | -0.067295 | 53.9139 | 53.9261 | 53.9233 | 53.8713 | 67.6083 | 67.7878 | 67.278 | 67.4471 | 0.12643 | -0.013055 | 0.07041 | -0.015865 | 0.095776 | 0.094735 | -0.039829 | 53.9414 | 53.9536 | 53.9508 | 53.8987 | 67.6358 | 67.8152 | 67.3054 | 67.4745 | -13.6944 | -13.3641 | -13.685 | -13.3546
207 | 121.7834 | -65.4602 | 56.3416 | 0.094381 | -0.054257 | 0.033786 | -0.043331 | 0.072888 | 0.062691 | -0.067295 | 55.5622 | 55.5882 | 55.5761 | 55.5243 | 65.9373 | 66.1076 | 65.6023 | 65.7806 | 0.12185 | -0.026791 | 0.061252 | -0.015865 | 0.10035 | 0.090157 | -0.039829 | 55.5896 | 55.6157 | 55.6036 | 55.5518 | 65.9648 | 66.1351 | 65.6298 | 65.8081 | -10.3751 | -10.0401 | -10.3612 | -10.0262
208.7344 | 121.8887 | -61.1252 | 60.5804 | 0.094381 | -0.049678 | 0.029208 | -0.052488 | 0.063733 | 0.053534 | -0.071874 | 60.4428 | 60.4555 | 60.452 | 60.4055 | 61.0707 | 61.2365 | 60.74 | 60.9232 | 0.12185 | -0.022212 | 0.056674 | -0.025022 | 0.091199 | 0.081 | -0.044408 | 60.4703 | 60.483 | 60.4794 | 60.433 | 61.0982 | 61.264 | 60.7675 | 60.9506 | -0.62787 | -0.2972 | -0.61873 | -0.28806
210.4219 | 121.8704 | -61.0977 | 60.5896 | 0.094381 | -0.058836 | 0.029208 | -0.047909 | 0.06831 | 0.053534 | -0.071874 | 60.4428 | 60.4509 | 60.452 | 60.3918 | 61.0799 | 61.2457 | 60.7538 | 60.9323 | 0.12185 | -0.03137 | 0.056674 | -0.020443 | 0.095776 | 0.081 | -0.044408 | 60.4703 | 60.4784 | 60.4794 | 60.4193 | 61.1073 | 61.2732 | 60.7812 | 60.9598 | -0.63702 | -0.31093 | -0.62789 | -0.3018
212.1562 | 121.875 | -61.084 | 60.6171 | 0.094381 | -0.022205 | 0.070415 | -0.020438 | 0.095778 | 0.081005 | -0.044405 | 60.4474 | 60.4555 | 60.4566 | 60.3918 | 61.0799 | 61.2503 | 60.74 | 60.9323 | 0.12185 | 0.005261 | 0.097881 | 0.007028 | 0.12324 | 0.10847 | -0.016939 | 60.4749 | 60.483 | 60.484 | 60.4193 | 61.1073 | 61.2777 | 60.7675 | 60.9598 | -0.63245 | -0.29262 | -0.62331 | -0.28348
213.9062 | 121.8613 | -61.1526 | 60.5759 | 0.094381 | -0.022205 | 0.061258 | -0.020438 | 0.095778 | 0.085583 | -0.048983 | 60.4291 | 60.4418 | 60.452 | 60.3918 | 61.0936 | 61.2503 | 60.7721 | 60.9415 | 0.12185 | 0.005261 | 0.088724 | 0.007028 | 0.12324 | 0.11305 | -0.021517 | 60.4566 | 60.4692 | 60.4794 | 60.4193 | 61.1211 | 61.2777 | 60.7996 | 60.9689 | -0.66449 | -0.34298 | -0.64162 | -0.32011
215.5938 | 121.8155 | -61.1801 | 60.553 | 0.094381 | -0.022205 | 0.065837 | -0.020438 | 0.10036 | 0.076426 | -0.044405 | 60.4154 | 60.4234 | 60.4291 | 60.3735 | 61.1028 | 61.2823 | 60.7812 | 60.9552 | 0.12185 | 0.005261 | 0.093303 | 0.007028 | 0.12782 | 0.10389 | -0.016939 | 60.4428 | 60.4509 | 60.4566 | 60.401 | 61.1302 | 61.3098 | 60.8087 | 60.9827 | -0.68739 | -0.36587 | -0.67367 | -0.35216
217.3281 | 121.9391 | -61.1114 | 60.5392 | 0.094381 | 0.005267 | 0.10247 | 0.01619 | 0.1324 | 0.11305 | -0.026092 | 60.4016 | 60.4143 | 60.4199 | 60.3643 | 61.1165 | 61.2777 | 60.7858 | 60.9644 | 0.12185 | 0.032733 | 0.12993 | 0.043656 | 0.15987 | 0.14052 | 0.001374 | 60.4291 | 60.4418 | 60.4474 | 60.3918 | 61.144 | 61.3052 | 60.8133 | 60.9918 | -0.71486 | -0.38419 | -0.69656 | -0.36589
219 | 121.8567 | -61.203 | 60.5576 | 0.094381 | 0.019004 | 0.10247 | 0.011611 | 0.1324 | 0.11763 | -0.012357 | 60.3971 | 60.4189 | 60.4108 | 60.3506 | 61.1211 | 61.2915 | 60.795 | 60.9735 | 0.12185 | 0.04647 | 0.12993 | 0.039077 | 0.15987 | 0.1451 | 0.015109 | 60.4245 | 60.4463 | 60.4382 | 60.3781 | 61.1485 | 61.3189 | 60.8224 | 61.001 | -0.72401 | -0.39792 | -0.7103 | -0.38421
220.7344 | 121.9711 | -61.171 | 60.4477 | 0.094381 | -0.013048 | 0.065837 | -0.011281 | 0.10036 | 0.090161 | -0.044405 | 60.3879 | 60.396 | 60.397 | 60.3369 | 61.1302 | 61.3098 | 60.8087 | 60.9781 | 0.12185 | 0.014418 | 0.093303 | 0.016185 | 0.12782 | 0.11763 | -0.016939 | 60.4154 | 60.4234 | 60.4245 | 60.3643 | 61.1577 | 61.3373 | 60.8362 | 61.0056 | -0.74233 | -0.42081 | -0.73319 | -0.41168
222.4844 | 121.8613 | -61.2076 | 60.4523 | 0.094381 | -0.017627 | 0.074994 | -0.006703 | 0.10951 | 0.090161 | -0.044405 | 60.3696 | 60.3777 | 60.3879 | 60.3277 | 61.1348 | 61.3189 | 60.8224 | 60.9964 | 0.12185 | 0.009839 | 0.10246 | 0.020763 | 0.13698 | 0.11763 | -0.016939 | 60.397 | 60.4051 | 60.4153 | 60.3552 | 61.1623 | 61.3464 | 60.8499 | 61.0239 | -0.76522 | -0.45286 | -0.74692 | -0.43457
224.2188 | 121.8521 | -61.2579 | 60.4752 | 0.094381 | -0.00389 | 0.079572 | 0.007033 | 0.11409 | 0.1039 | -0.035248 | 60.3558 | 60.3639 | 60.3696 | 60.314 | 61.1577 | 61.3281 | 60.8316 | 61.0101 | 0.12185 | 0.023576 | 0.10704 | 0.034499 | 0.14156 | 0.13136 | -0.007782 | 60.3833 | 60.3914 | 60.397 | 60.3414 | 61.1852 | 61.3556 | 60.8591 | 61.0376 | -0.80184 | -0.47576 | -0.78813 | -0.46204
225.9062 | 121.8658 | -61.5234 | 60.1685 | 0.089802 | -0.00389 | 0.084151 | -0.002124 | 0.11409 | 0.099318 | -0.03067 | 59.8614 | 59.8694 | 59.8705 | 59.8103 | 61.6613 | 61.8317 | 61.3398 | 61.5092 | 0.11727 | 0.023576 | 0.11162 | 0.025342 | 0.14156 | 0.12678 | -0.003204 | 59.8888 | 59.8969 | 59.898 | 59.8377 | 61.6888 | 61.8592 | 61.3673 | 61.5366 | -1.7999 | -1.4784 | -1.7908 | -1.4693
227.6562 | 121.8292 | -61.8896 | 59.8434 | 0.094381 | 0.005267 | 0.093308 | 0.011611 | 0.1324 | 0.11763 | -0.012357 | 59.7744 | 59.7916 | 59.7881 | 59.7324 | 61.7529 | 61.9049 | 61.4131 | 61.5916 | 0.12185 | 0.032733 | 0.12077 | 0.039077 | 0.15987 | 0.1451 | 0.015109 | 59.8018 | 59.819 | 59.8156 | 59.7599 | 61.7803 | 61.9324 | 61.4405 | 61.619 | -1.9785 | -1.6387 | -1.9647 | -1.6249
229.4062 | 121.907 | -61.6608 | 60.0082 | 0.098959 | 0.028162 | 0.12994 | 0.034504 | 0.15529 | 0.14052 | -0.003201 | 59.8797 | 59.8969 | 59.8843 | 59.8377 | 61.6567 | 61.8042 | 61.3169 | 61.4954 | 0.12643 | 0.055628 | 0.1574 | 0.06197 | 0.18276 | 0.16799 | 0.024265 | 59.9071 | 59.9244 | 59.9117 | 59.8652 | 61.6842 | 61.8317 | 61.3444 | 61.5229 | -1.777 | -1.4372 | -1.7724 | -1.4326
231.1406 | 121.9482 | -61.4365 | 60.2234 | 0.089802 | 0.041898 | 0.14367 | 0.057396 | 0.1736 | 0.14968 | 0.01969 | 60.0537 | 60.0709 | 60.0674 | 60.0117 | 61.4553 | 61.6211 | 61.1292 | 61.3077 | 0.11727 | 0.069364 | 0.17114 | 0.084862 | 0.20107 | 0.17715 | 0.047156 | 60.0811 | 60.0983 | 60.0949 | 60.0392 | 61.4827 | 61.6486 | 61.1567 | 61.3352 | -1.4016 | -1.0755 | -1.3879 | -1.0618
232.875 | 121.8338 | -61.9858 | 59.761 | 0.094381 | -0.017627 | 0.061258 | -0.020438 | 0.10493 | 0.085583 | -0.044405 | 59.6187 | 59.6267 | 59.6325 | 59.5676 | 61.9039 | 62.0697 | 61.5733 | 61.7564 | 0.12185 | 0.009839 | 0.088724 | 0.007028 | 0.1324 | 0.11305 | -0.016939 | 59.6462 | 59.6542 | 59.6599 | 59.595 | 61.9314 | 62.0972 | 61.6008 | 61.7839 | -2.2852 | -1.9546 | -2.2715 | -1.9408
234.6094 | 121.8613 | -62.1872 | 59.5505 | 0.089802 | -0.026784 | 0.056679 | -0.034174 | 0.086622 | 0.071848 | -0.058139 | 59.5088 | 59.5214 | 59.5226 | 59.4623 | 62.0138 | 62.1705 | 61.6832 | 61.8617 | 0.11727 | 0.000682 | 0.084145 | -0.006708 | 0.11409 | 0.099314 | -0.030673 | 59.5363 | 59.5489 | 59.55 | 59.4897 | 62.0413 | 62.1979 | 61.7106 | 61.8891 | -2.505 | -2.1744 | -2.4912 | -2.1606
236.3438 | 121.8796 | -64.6408 | 57.0786 | 0.094381 | -0.026784 | 0.056679 | -0.034174 | 0.095778 | 0.081005 | -0.048983 | 57.0181 | 57.0305 | 57.0366 | 56.9667 | 64.4998 | 64.6609 | 64.1692 | 64.3431 | 0.12185 | 0.000682 | 0.084145 | -0.006708 | 0.12324 | 0.10847 | -0.021517 | 57.0456 | 57.058 | 57.064 | 56.9942 | 64.5272 | 64.6884 | 64.1967 | 64.3705 | -7.4816 | -7.1511 | -7.4632 | -7.1327
238.0156 | 121.9299 | -65.2771 | 56.3324 | 0.098959 | -0.026784 | 0.052101 | -0.034174 | 0.095778 | 0.076426 | -0.058139 | 56.4641 | 56.4765 | 56.478 | 56.4172 | 65.0491 | 65.224 | 64.7187 | 64.8924 | 0.12643 | 0.000682 | 0.079567 | -0.006708 | 0.12324 | 0.10389 | -0.030673 | 56.4916 | 56.504 | 56.5055 | 56.4447 | 65.0766 | 65.2515 | 64.7461 | 64.9199 | -8.585 | -8.2545 | -8.5711 | -8.2406
239.75 | 121.8887 | -65.0299 | 56.6666 | 0.098959 | -0.035942 | 0.052101 | -0.029595 | 0.086622 | 0.071848 | -0.053561 | 56.5923 | 56.5956 | 56.6062 | 56.5408 | 64.9301 | 65.1004 | 64.5905 | 64.7734 | 0.12643 | -0.008476 | 0.079567 | -0.002129 | 0.11409 | 0.099314 | -0.026095 | 56.6198 | 56.623 | 56.6337 | 56.5683 | 64.9576 | 65.1279 | 64.6179 | 64.8009 | -8.3378 | -7.9981 | -8.3239 | -7.9842
241.4688 | 121.8887 | -65.6616 | 56.0211 | 0.094381 | -0.031363 | 0.047522 | -0.020438 | 0.086622 | 0.071848 | -0.053561 | 56.9952 | 56.9985 | 57.0091 | 56.9392 | 64.5181 | 64.6838 | 64.1784 | 64.3751 | 0.12185 | -0.003897 | 0.074988 | 0.007028 | 0.11409 | 0.099314 | -0.026095 | 57.0227 | 57.026 | 57.0366 | 56.9667 | 64.5455 | 64.7113 | 64.2059 | 64.4026 | -7.5228 | -7.1832 | -7.509 | -7.1693
243.1562 | 121.8979 | -65.0482 | 56.6071 | 0.098959 | -0.026784 | 0.065837 | -0.025017 | 0.095778 | 0.085583 | -0.048983 | 56.6244 | 56.6322 | 56.6337 | 56.5866 | 64.8843 | 65.0546 | 64.5538 | 64.7276 | 0.12643 | 0.000682 | 0.093303 | 0.002449 | 0.12324 | 0.11305 | -0.021517 | 56.6518 | 56.6597 | 56.6612 | 56.6141 | 64.9118 | 65.0821 | 64.5813 | 64.7551 | -8.26 | -7.9295 | -8.2506 | -7.9201
244.8906 | 121.9666 | -64.801 | 56.8176 | 0.098959 | -0.031363 | 0.056679 | -0.034174 | 0.082044 | 0.067269 | -0.058139 | 56.9494 | 56.9664 | 56.9679 | 56.9026 | 64.5639 | 64.7296 | 64.2288 | 64.4117 | 0.12643 | -0.003897 | 0.084145 | -0.006708 | 0.10951 | 0.094735 | -0.030673 | 56.9769 | 56.9939 | 56.9954 | 56.93 | 64.5913 | 64.7571 | 64.2562 | 64.4392 | -7.6144 | -7.2793 | -7.5959 | -7.2609
246.5625 | 121.9116 | -65.5014 | 56.1401 | 0.11727 | -0.040521 | 0.056679 | -0.025017 | 0.082044 | 0.058113 | -0.067295 | 56.1574 | 56.1651 | 56.1667 | 56.1013 | 65.3605 | 65.5262 | 65.03 | 65.2083 | 0.14474 | -0.013055 | 0.084145 | 0.002449 | 0.10951 | 0.085579 | -0.039829 | 56.1848 | 56.1926 | 56.1942 | 56.1287 | 65.3879 | 65.5537 | 65.0575 | 65.2358 | -9.2031 | -8.8726 | -9.1938 | -8.8633
248.3125 | 121.9025 | -65.1581 | 56.5063 | 0.11727 | -0.035942 | 0.042944 | -0.025017 | 0.082044 | 0.071848 | -0.058139 | 56.2901 | 56.2934 | 56.2903 | 56.234 | 65.214 | 65.398 | 64.9018 | 65.071 | 0.14474 | -0.008476 | 0.07041 | 0.002449 | 0.10951 | 0.099314 | -0.030673 | 56.3176 | 56.3208 | 56.3178 | 56.2615 | 65.2414 | 65.4255 | 64.9293 | 65.0984 | -8.9238 | -8.6116 | -8.9236 | -8.6115
249.9844 | 121.9025 | -65.4144 | 56.282 | 0.11727 | -0.031363 | 0.056679 | -0.025017 | 0.0912 | 0.071848 | -0.058139 | 56.1803 | 56.188 | 56.1942 | 56.1333 | 65.3376 | 65.4941 | 64.9979 | 65.1809 | 0.14474 | -0.003897 | 0.084145 | 0.002449 | 0.11867 | 0.099314 | -0.030673 | 56.2077 | 56.2155 | 56.2216 | 56.1608 | 65.365 | 65.5216 | 65.0254 | 65.2083 | -9.1573 | -8.8177 | -9.1434 | -8.8038
251.7188 | 121.9574 | -65.2496 | 56.3599 | 0.14017 | -0.031363 | 0.052101 | -0.029595 | 0.086622 | 0.071848 | -0.058139 | 56.4687 | 56.4719 | 56.4734 | 56.4172 | 65.0446 | 65.2057 | 64.7141 | 64.897 | 0.16763 | -0.003897 | 0.079567 | -0.002129 | 0.11409 | 0.099314 | -0.030673 | 56.4962 | 56.4994 | 56.5009 | 56.4447 | 65.072 | 65.2332 | 64.7415 | 64.9245 | -8.5759 | -8.2454 | -8.5711 | -8.2406
253.3906 | 121.8887 | -65.062 | 56.5842 | 0.10812 | -0.026784 | 0.052101 | -0.029595 | 0.10036 | 0.081005 | -0.053561 | 56.5557 | 56.5589 | 56.565 | 56.5042 | 64.9484 | 65.1187 | 64.6134 | 64.8009 | 0.13558 | 0.000682 | 0.079567 | -0.002129 | 0.12782 | 0.10847 | -0.026095 | 56.5832 | 56.5864 | 56.5925 | 56.5317 | 64.9759 | 65.1462 | 64.6408 | 64.8283 | -8.3927 | -8.0577 | -8.3834 | -8.0483
255.0625 | 121.9482 | -64.9658 | 56.6757 | 0.11727 | -0.017627 | 0.061258 | -0.025017 | 0.095778 | 0.071848 | -0.048983 | 56.487 | 56.4948 | 56.4872 | 56.4355 | 65.0217 | 65.1966 | 64.6958 | 64.8695 | 0.14474 | 0.009839 | 0.088724 | 0.002449 | 0.12324 | 0.099314 | -0.021517 | 56.5145 | 56.5223 | 56.5146 | 56.463 | 65.0491 | 65.224 | 64.7232 | 64.897 | -8.5346 | -8.2087 | -8.5345 | -8.2086
256.7969 | 121.8292 | -65.0665 | 56.6299 | 0.10812 | -0.035942 | 0.056679 | -0.034174 | 0.077466 | 0.062691 | -0.058139 | 56.6427 | 56.6551 | 56.6612 | 56.6049 | 64.8523 | 65.018 | 64.5218 | 64.7047 | 0.13558 | -0.008476 | 0.084145 | -0.006708 | 0.10493 | 0.090157 | -0.030673 | 56.6702 | 56.6825 | 56.6886 | 56.6324 | 64.8797 | 65.0455 | 64.5493 | 64.7322 | -8.2096 | -7.8791 | -8.1911 | -7.8606
258.5312 | 121.7972 | -64.1693 | 57.5134 | 0.098959 | -0.031363 | 0.052101 | -0.034174 | 0.082044 | 0.067269 | -0.048983 | 57.3615 | 57.3648 | 57.3616 | 57.3055 | 64.1472 | 64.3176 | 63.8213 | 63.9951 | 0.12643 | -0.003897 | 0.079567 | -0.006708 | 0.10951 | 0.094735 | -0.021517 | 57.389 | 57.3923 | 57.3891 | 57.333 | 64.1747 | 64.345 | 63.8488 | 64.0226 | -6.7857 | -6.4598 | -6.7856 | -6.4597
260.2656 | 121.907 | -63.8855 | 57.7606 | 0.10812 | -0.022205 | 0.052101 | -0.038752 | 0.0912 | 0.081005 | -0.048983 | 57.7415 | 57.754 | 57.7599 | 57.6902 | 63.7627 | 63.9284 | 63.4275 | 63.6105 | 0.13558 | 0.005261 | 0.079567 | -0.011286 | 0.11867 | 0.10847 | -0.021517 | 57.769 | 57.7815 | 57.7874 | 57.7176 | 63.7901 | 63.9559 | 63.455 | 63.638 | -6.0211 | -5.686 | -6.0027 | -5.6676
262 | 121.4676 | -28.775 | 93.0588 | 0.089802 | -0.031363 | 0.038365 | -0.047909 | 0.06831 | 0.062691 | -0.053561 | 92.387 | 92.434 | 92.4221 | 92.3672 | 29.0693 | 29.2175 | 28.7875 | 29.0179 | 0.11727 | -0.003897 | 0.065831 | -0.020443 | 0.095776 | 0.090157 | -0.026095 | 92.4145 | 92.4614 | 92.4496 | 92.3946 | 29.0967 | 29.245 | 28.8149 | 29.0453 | 63.3177 | 63.5995 | 63.3528 | 63.6346
263.7344 | 121.9528 | -63.5651 | 57.962 | 0.10812 | -0.022205 | 0.061258 | -0.020438 | 0.0912 | 0.076426 | -0.048983 | 58.7808 | 58.7934 | 58.7351 | 58.7159 | 62.9752 | 62.9304 | 62.4478 | 62.8368 | 0.13558 | 0.005261 | 0.088724 | 0.007028 | 0.11867 | 0.10389 | -0.021517 | 58.8083 | 58.8209 | 58.7626 | 58.7433 | 63.0027 | 62.9579 | 62.4752 | 62.8643 | -4.1944 | -3.6669 | -4.2401 | -3.7127
265.4062 | 122.0261 | -47.9462 | 73.732 | 0.080646 | -0.026784 | 0.038365 | -0.043331 | 0.072888 | 0.062691 | -0.062717 | 73.5785 | 73.5967 | 73.5504 | 73.5016 | 48.1053 | 48.1158 | 47.8427 | 48.0081 | 0.10811 | 0.000682 | 0.065831 | -0.015865 | 0.10035 | 0.090157 | -0.035251 | 73.606 | 73.6242 | 73.5779 | 73.529 | 48.1328 | 48.1433 | 47.8702 | 48.0356 | 25.4732 | 25.7358 | 25.4451 | 25.7077
267.1406 | 121.7148 | -27.4521 | 94.3542 | 0.06691 | -0.035942 | 0.038365 | -0.061645 | 0.06831 | 0.058113 | -0.062717 | 94.2184 | 94.2289 | 94.2397 | 94.1851 | 27.3021 | 27.4413 | 27.0019 | 27.2324 | 0.094376 | -0.008476 | 0.065831 | -0.034179 | 0.095776 | 0.085579 | -0.035251 | 94.2459 | 94.2563 | 94.2672 | 94.2125 | 27.3296 | 27.4687 | 27.0294 | 27.2598 | 66.9163 | 67.2165 | 66.9376 | 67.2378
268.8906 | 121.7926 | -27.0813 | 94.6838 | 0.06691 | -0.040521 | 0.033786 | -0.057066 | 0.063733 | 0.053534 | -0.058139 | 94.4656 | 94.4624 | 94.4869 | 94.4323 | 27.0457 | 27.1895 | 26.7638 | 26.9943 | 0.094376 | -0.013055 | 0.061252 | -0.0296 | 0.091199 | 0.081 | -0.030673 | 94.4931 | 94.4898 | 94.5144 | 94.4598 | 27.0732 | 27.2169 | 26.7913 | 27.0218 | 67.4199 | 67.7018 | 67.4412 | 67.7231
270.5781 | 121.8933 | -26.6647 | 95.0226 | 0.25005 | 0.11974 | 0.21235 | 0.10318 | 0.23769 | 0.22293 | 0.097519 | 95.0288 | 95.0164 | 95.0363 | 94.9818 | 26.4918 | 26.6447 | 26.219 | 26.4404 | 0.27751 | 0.1472 | 0.23982 | 0.13065 | 0.26516 | 0.2504 | 0.12498 | 95.0563 | 95.0439 | 95.0638 | 95.0093 | 26.5192 | 26.6721 | 26.2465 | 26.4678 | 68.537 | 68.8098 | 68.5445 | 68.8173
272.3125 | 121.7697 | -26.564 | 95.2148 | 0.19053 | 0.060213 | 0.14825 | 0.052818 | 0.1736 | 0.16799 | 0.042581 | 95.0608 | 95.0439 | 95.0684 | 95.0093 | 26.4643 | 26.6172 | 26.2007 | 26.422 | 0.21799 | 0.087679 | 0.17572 | 0.080284 | 0.20107 | 0.19546 | 0.070047 | 95.0883 | 95.0714 | 95.0958 | 95.0368 | 26.4918 | 26.6447 | 26.2281 | 26.4495 | 68.5965 | 68.8602 | 68.6041 | 68.8677
274.0469 | 121.8658 | -26.619 | 95.1187 | 0.31872 | 0.21131 | 0.29935 | 0.20391 | 0.3201 | 0.30992 | 0.1845 | 94.9098 | 94.8974 | 94.9264 | 94.8673 | 26.62 | 26.7591 | 26.3472 | 26.564 | 0.34619 | 0.23878 | 0.32681 | 0.23137 | 0.34756 | 0.33739 | 0.21197 | 94.9372 | 94.9248 | 94.9539 | 94.8948 | 26.6474 | 26.7866 | 26.3747 | 26.5914 | 68.2898 | 68.5626 | 68.3065 | 68.5792
275.7812 | 121.8246 | -26.683 | 95.0455 | 0.19511 | 0.092265 | 0.17572 | 0.071132 | 0.20107 | 0.19546 | 0.065472 | 94.9876 | 94.9752 | 94.9997 | 94.936 | 26.5421 | 26.6905 | 26.2739 | 26.4953 | 0.22257 | 0.11973 | 0.20319 | 0.098598 | 0.22854 | 0.22293 | 0.092938 | 95.0151 | 95.0027 | 95.0271 | 94.9635 | 26.5696 | 26.7179 | 26.3014 | 26.5228 | 68.4455 | 68.7137 | 68.4576 | 68.7257
277.4531 | 121.8109 | -26.5091 | 95.2286 | 0.21342 | 0.10142 | 0.18946 | 0.094024 | 0.2148 | 0.2092 | 0.083784 | 95.1204 | 95.1126 | 95.1416 | 95.0688 | 26.4139 | 26.5531 | 26.1366 | 26.3396 | 0.24088 | 0.12889 | 0.21692 | 0.12149 | 0.24227 | 0.23666 | 0.11125 | 95.1478 | 95.14 | 95.1691 | 95.0963 | 26.4414 | 26.5806 | 26.164 | 26.3671 | 68.7064 | 68.9838 | 68.7277 | 69.005
279.125 | 121.907 | -26.6876 | 94.9768 | 0.46981 | 0.37157 | 0.46418 | 0.36416 | 0.47575 | 0.47017 | 0.34474 | 94.9098 | 94.9019 | 94.9173 | 94.8582 | 26.6245 | 26.7637 | 26.3426 | 26.5685 | 0.49727 | 0.39904 | 0.49164 | 0.39162 | 0.50321 | 0.49763 | 0.37221 | 94.9372 | 94.9294 | 94.9447 | 94.8856 | 26.652 | 26.7912 | 26.3701 | 26.596 | 68.2852 | 68.5671 | 68.2927 | 68.5747
280.8594 | 121.8704 | -27.1912 | 94.4962 | 0.598 | 0.46315 | 0.5878 | 0.47404 | 0.60393 | 0.58005 | 0.44088 | 94.9281 | 94.9157 | 94.9447 | 94.8857 | 26.6016 | 26.7408 | 26.3151 | 26.5365 | 0.62547 | 0.49061 | 0.61526 | 0.5015 | 0.6314 | 0.60752 | 0.46835 | 94.9555 | 94.9431 | 94.9722 | 94.9131 | 26.6291 | 26.7683 | 26.3426 | 26.564 | 68.3264 | 68.6129 | 68.3431 | 68.6296
282.5938 | 121.8109 | -26.8341 | 94.9356 | 0.41945 | 0.33952 | 0.44586 | 0.30463 | 0.4437 | 0.4427 | 0.32643 | 94.777 | 94.7737 | 94.8028 | 94.7254 | 26.7619 | 26.8827 | 26.4754 | 26.6967 | 0.44691 | 0.36699 | 0.47333 | 0.3321 | 0.47117 | 0.47016 | 0.35389 | 94.8044 | 94.8012 | 94.8303 | 94.7529 | 26.7893 | 26.9102 | 26.5028 | 26.7242 | 68.0151 | 68.3016 | 68.0409 | 68.3274
284.3281 | 121.7651 | -26.9348 | 94.7983 | 0.39198 | 0.33952 | 0.45044 | 0.27259 | 0.42997 | 0.45185 | 0.34932 | 94.6442 | 94.641 | 94.6655 | 94.6018 | 26.8718 | 27.0201 | 26.5898 | 26.8203 | 0.41944 | 0.36699 | 0.4779 | 0.30005 | 0.45743 | 0.47932 | 0.37678 | 94.6717 | 94.6684 | 94.6929 | 94.6292 | 26.8992 | 27.0475 | 26.6173 | 26.8478 | 67.7724 | 68.0544 | 67.7937 | 68.0756
286.0625 | 121.7926 | -26.8295 | 94.9722 | 0.46523 | 0.36699 | 0.47791 | 0.34126 | 0.47575 | 0.47017 | 0.34932 | 94.7449 | 94.7325 | 94.757 | 94.6979 | 26.7802 | 26.9148 | 26.4983 | 26.715 | 0.4927 | 0.39446 | 0.50538 | 0.36873 | 0.50321 | 0.49763 | 0.37678 | 94.7724 | 94.76 | 94.7845 | 94.7254 | 26.8077 | 26.9422 | 26.5257 | 26.7425 | 67.9647 | 68.2467 | 67.9768 | 68.2588
287.7969 | 121.7514 | -26.6098 | 95.1462 | 1.0192 | 0.86608 | 0.99529 | 0.87695 | 1.0159 | 0.98752 | 0.85292 | 94.9738 | 94.9798 | 94.9951 | 94.936 | 26.533 | 26.6859 | 26.2739 | 26.4861 | 1.0467 | 0.89355 | 1.0228 | 0.90441 | 1.0434 | 1.015 | 0.88038 | 95.0013 | 95.0072 | 95.0226 | 94.9635 | 26.5604 | 26.7133 | 26.3014 | 26.5136 | 68.4409 | 68.6999 | 68.4621 | 68.7212
289.5312 | 121.7606 | -26.7105 | 95.0821 | 0.42402 | 0.30747 | 0.42297 | 0.30006 | 0.43912 | 0.42438 | 0.30812 | 94.9326 | 94.9203 | 94.9493 | 94.8902 | 26.5925 | 26.7317 | 26.3197 | 26.5365 | 0.45149 | 0.33493 | 0.45043 | 0.32752 | 0.46659 | 0.45185 | 0.33558 | 94.9601 | 94.9477 | 94.9768 | 94.9177 | 26.6199 | 26.7591 | 26.3472 | 26.564 | 68.3402 | 68.6129 | 68.3568 | 68.6296
291.2031 | 121.8063 | -26.6602 | 95.0638 | 0.48354 | 0.37615 | 0.49165 | 0.355 | 0.50322 | 0.50222 | 0.38594 | 94.8869 | 94.8745 | 94.8898 | 94.8353 | 26.6337 | 26.7774 | 26.3701 | 26.596 | 0.51101 | 0.40362 | 0.51911 | 0.38246 | 0.53068 | 0.52968 | 0.41341 | 94.9143 | 94.9019 | 94.9173 | 94.8627 | 26.6612 | 26.8049 | 26.3975 | 26.6235 | 68.2532 | 68.5168 | 68.2561 | 68.5197
292.9375 | 121.8842 | -26.4038 | 95.3064 | 0.19511 | 0.069371 | 0.16199 | 0.066553 | 0.20565 | 0.19089 | 0.060893 | 94.9693 | 94.9615 | 94.9768 | 94.9223 | 26.5467 | 26.695 | 26.2648 | 26.5045 | 0.22257 | 0.096837 | 0.18945 | 0.094019 | 0.23311 | 0.21835 | 0.088359 | 94.9967 | 94.9889 | 95.0043 | 94.9497 | 26.5742 | 26.7225 | 26.2922 | 26.5319 | 68.4226 | 68.7045 | 68.4301 | 68.712
294.6094 | 121.8979 | -21.373 | 100.2914 | 0.085224 | -0.040521 | 0.042944 | -0.038752 | 0.0912 | 0.076426 | -0.048983 | 100.0377 | 100.0256 | 100.0404 | 99.9867 | 21.4787 | 21.6271 | 21.224 | 21.4364 | 0.11269 | -0.013055 | 0.07041 | -0.011286 | 0.11867 | 0.10389 | -0.021517 | 100.0651 | 100.0531 | 100.0678 | 100.0142 | 21.5061 | 21.6546 | 21.2514 | 21.4639 | 78.559 | 78.8137 | 78.5617 | 78.8164
296.3438 | 121.8842 | -20.9381 | 100.7492 | 0.044018 | -0.077151 | 0.001736 | -0.07538 | 0.059155 | 0.044377 | -0.08103 | 100.523 | 100.511 | 100.5302 | 100.4766 | 20.9934 | 21.1418 | 20.7387 | 20.9557 | 0.071484 | -0.049685 | 0.029202 | -0.047914 | 0.086621 | 0.071843 | -0.053564 | 100.5505 | 100.5385 | 100.5577 | 100.5041 | 21.0208 | 21.1693 | 20.7661 | 20.9832 | 79.5296 | 79.7843 | 79.5369 | 79.7916
298.0156 | 89.4928 | -0.15106 | 69.1818 | 0.03944 | -0.086309 | -0.002842 | -0.07538 | 0.059155 | 0.044377 | -0.085608 | 99.5478 | 99.6639 | 99.5505 | 99.5563 | 22.17 | 22.1353 | 21.9245 | 22.0682 | 0.066906 | -0.058843 | 0.024624 | -0.047914 | 0.086621 | 0.071843 | -0.058142 | 99.5752 | 99.6914 | 99.578 | 99.5837 | 22.1974 | 22.1627 | 21.9519 | 22.0957 | 77.3778 | 77.6233 | 77.3805 | 77.626
299.7656 | 121.9162 | -20.2515 | 97.9935 | 0.048597 | -0.077151 | -0.007421 | -0.07538 | 0.063733 | 0.044377 | -0.08103 | 101.4707 | 101.4817 | 101.4734 | 101.4382 | 20.0823 | 20.2445 | 19.8321 | 20.0446 | 0.076063 | -0.049685 | 0.020045 | -0.047914 | 0.091199 | 0.071843 | -0.053564 | 101.4982 | 101.5092 | 101.5008 | 101.4657 | 20.1098 | 20.272 | 19.8596 | 20.0721 | 81.3884 | 81.6386 | 81.391 | 81.6412
301.5 | 121.9711 | -118.2312 | 3.3875 | 0.13101 | -0.00389 | 0.08873 | 0.002454 | 0.12325 | 0.099318 | -0.03067 | 3.4726 | 3.5133 | 3.4524 | 3.4424 | 118.3024 | 118.2792 | 117.979 | 118.1091 | 0.15847 | 0.023576 | 0.1162 | 0.02992 | 0.15071 | 0.12678 | -0.003204 | 3.5001 | 3.5408 | 3.4798 | 3.4699 | 118.3299 | 118.3067 | 118.0065 | 118.1366 | -114.8298 | -114.5064 | -114.8501 | -114.5267
303.2344 | 121.9116 | -119.6594 | 1.9913 | 0.13559 | -0.00389 | 0.093308 | 0.002454 | 0.11867 | 0.099318 | -0.03067 | 2.0258 | 2.0847 | 2.0102 | 2.0046 | 119.7446 | 119.7259 | 119.435 | 119.5604 | 0.16305 | 0.023576 | 0.12077 | 0.02992 | 0.14613 | 0.12678 | -0.003204 | 2.0533 | 2.1122 | 2.0377 | 2.032 | 119.772 | 119.7534 | 119.4624 | 119.5879 | -117.7188 | -117.4091 | -117.7344 | -117.4247
304.9688 | 121.9116 | -119.6777 | 2.0279 | 0.12643 | -0.008469 | 0.093308 | 0.011611 | 0.12325 | 0.1039 | -0.026092 | 1.9846 | 2.0527 | 1.9416 | 1.9542 | 119.7904 | 119.7625 | 119.4762 | 119.6062 | 0.1539 | 0.018997 | 0.12077 | 0.039077 | 0.15071 | 0.13136 | 0.001374 | 2.0121 | 2.0802 | 1.969 | 1.9817 | 119.8178 | 119.79 | 119.5036 | 119.6336 | -117.8057 | -117.4916 | -117.8488 | -117.5346
306.6406 | 121.8109 | -119.7372 | 1.9958 | 0.12185 | 0.000689 | 0.08873 | 0.011611 | 0.12325 | 0.1039 | -0.016936 | 2.0487 | 2.1076 | 1.9736 | 1.8351 | 119.7263 | 119.6893 | 119.1694 | 119.5329 | 0.14932 | 0.028155 | 0.1162 | 0.039077 | 0.15071 | 0.13136 | 0.01053 | 2.0762 | 2.1351 | 2.0011 | 1.8626 | 119.7537 | 119.7168 | 119.1969 | 119.5604 | -117.6776 | -117.1207 | -117.7527 | -117.1958
308.375 | 121.8063 | -119.7693 | 1.9409 | 0.12185 | 0.005267 | 0.093308 | 0.007033 | 0.11867 | 0.099318 | -0.03067 | 1.8885 | 1.9474 | 1.8225 | 1.6795 | 119.8682 | 119.8404 | 119.3159 | 119.684 | 0.14932 | 0.032733 | 0.12077 | 0.034499 | 0.14613 | 0.12678 | -0.003204 | 1.9159 | 1.9748 | 1.85 | 1.7069 | 119.8957 | 119.8678 | 119.3434 | 119.7115 | -117.9797 | -117.4275 | -118.0457 | -117.4934
310.0469 | 121.8796 | -119.8242 | 1.8539 | 0.12643 | -0.008469 | 0.084151 | 0.011611 | 0.11867 | 0.1039 | -0.03067 | 1.8381 | 1.9016 | 1.7813 | 1.6382 | 119.9094 | 119.877 | 119.3571 | 119.7206 | 0.1539 | 0.018997 | 0.11162 | 0.039077 | 0.14613 | 0.13136 | -0.003204 | 1.8656 | 1.9291 | 1.8088 | 1.6657 | 119.9369 | 119.9045 | 119.3846 | 119.7481 | -118.0713 | -117.519 | -118.1281 | -117.5758
311.7812 | 121.8704 | -119.8608 | 1.8173 | 0.12185 | -0.008469 | 0.08873 | 0.007033 | 0.11867 | 0.1039 | -0.021514 | 1.7557 | 1.8283 | 1.6989 | 1.5696 | 119.7492 | 119.9502 | 119.4258 | 119.7939 | 0.14932 | 0.018997 | 0.1162 | 0.034499 | 0.14613 | 0.13136 | 0.005952 | 1.7832 | 1.8558 | 1.7264 | 1.597 | 119.7766 | 119.9777 | 119.4533 | 119.8214 | -117.9935 | -117.6701 | -118.0503 | -117.7269
313.5156 | 121.7651 | -119.7556 | 1.9913 | 0.12643 | 0.000689 | 0.093308 | 0.007033 | 0.11867 | 0.09474 | -0.026092 | 1.9068 | 1.9748 | 1.8408 | 1.6978 | 119.5981 | 119.8037 | 119.2839 | 119.6657 | 0.1539 | 0.028155 | 0.12077 | 0.034499 | 0.14613 | 0.12221 | 0.001374 | 1.9342 | 2.0023 | 1.8683 | 1.7252 | 119.6255 | 119.8312 | 119.3113 | 119.6932 | -117.6913 | -117.3771 | -117.7572 | -117.4431
315.2031 | 121.843 | -119.3893 | 2.2659 | 0.12185 | -0.00389 | 0.08873 | 0.007033 | 0.11867 | 0.1039 | -0.026092 | 2.1952 | 2.2587 | 2.1338 | 2.0046 | 119.3188 | 119.5107 | 118.9909 | 119.3544 | 0.14932 | 0.023576 | 0.1162 | 0.034499 | 0.14613 | 0.13136 | 0.001374 | 2.2227 | 2.2862 | 2.1613 | 2.032 | 119.3463 | 119.5382 | 119.0183 | 119.3818 | -117.1236 | -116.7956 | -117.185 | -116.857
316.9531 | 121.756 | -119.1834 | 2.5406 | 0.12185 | -0.008469 | 0.093308 | 0.002454 | 0.12325 | 0.1039 | -0.03067 | 2.447 | 2.5106 | 2.3902 | 2.2518 | 119.0578 | 119.2498 | 118.7345 | 119.098 | 0.14932 | 0.018997 | 0.12077 | 0.02992 | 0.15071 | 0.13136 | -0.003204 | 2.4745 | 2.538 | 2.4177 | 2.2793 | 119.0853 | 119.2773 | 118.7619 | 119.1255 | -116.6108 | -116.2874 | -116.6676 | -116.3443
318.625 | 121.7468 | -118.8766 | 2.8381 | 0.11727 | 0.000689 | 0.079572 | 0.002454 | 0.11409 | 0.1039 | -0.026092 | 2.589 | 2.6434 | 2.523 | 2.38 | 118.9159 | 119.1216 | 118.5971 | 118.9652 | 0.14474 | 0.028155 | 0.10704 | 0.02992 | 0.14156 | 0.13136 | 0.001374 | 2.6164 | 2.6708 | 2.5505 | 2.4075 | 118.9434 | 119.1491 | 118.6246 | 118.9927 | -116.327 | -116.0081 | -116.3929 | -116.0741
320.3594 | 121.8155 | -119.4351 | 2.2247 | 0.12185 | -0.008469 | 0.084151 | 0.007033 | 0.11867 | 0.099318 | -0.03067 | 2.1403 | 2.2038 | 2.0652 | 1.9267 | 119.3509 | 119.5519 | 119.0321 | 119.4002 | 0.14932 | 0.018997 | 0.11162 | 0.034499 | 0.14613 | 0.12678 | -0.003204 | 2.1677 | 2.2313 | 2.0926 | 1.9542 | 119.3783 | 119.5794 | 119.0595 | 119.4276 | -117.2106 | -116.8918 | -117.2857 | -116.9669
322.0312 | 121.8658 | -119.5679 | 2.0462 | 0.12643 | -0.00389 | 0.084151 | 0.007033 | 0.12325 | 0.099318 | -0.021514 | 2.0853 | 2.1626 | 2.024 | 1.8809 | 119.3966 | 119.6069 | 119.087 | 119.4551 | 0.1539 | 0.023576 | 0.11162 | 0.034499 | 0.15071 | 0.12678 | 0.005952 | 2.1128 | 2.19 | 2.0514 | 1.9084 | 119.4241 | 119.6343 | 119.1145 | 119.4826 | -117.3113 | -117.0017 | -117.3727 | -117.0631
323.75 | 121.5591 | -118.4921 | 3.0212 | 0.15848 | 0.037319 | 0.12078 | 0.048239 | 0.15529 | 0.14968 | 0.028846 | 5.6474 | 5.8119 | 5.0136 | 4.9351 | 115.5555 | 115.6789 | 115.2229 | 115.582 | 0.18594 | 0.064785 | 0.14825 | 0.075705 | 0.18276 | 0.17715 | 0.056312 | 5.6749 | 5.8394 | 5.041 | 4.9626 | 115.583 | 115.7064 | 115.2503 | 115.6094 | -109.9081 | -109.5754 | -110.542 | -110.2093
325.4844 | 121.3486 | -118.602 | 3.1128 | 0.12185 | -0.008469 | 0.084151 | 0.007033 | 0.11409 | 0.1039 | -0.03067 | 3.0102 | 3.0738 | 2.9625 | 2.9936 | 118.6962 | 118.6638 | 118.3819 | 118.5074 | 0.14932 | 0.018997 | 0.11162 | 0.034499 | 0.14156 | 0.13136 | -0.003204 | 3.0377 | 3.1012 | 2.99 | 3.0211 | 118.7236 | 118.6913 | 118.4094 | 118.5349 | -115.686 | -115.3717 | -115.7337 | -115.4194
327.2188 | 121.8338 | -118.6569 | 2.9846 | 0.11727 | -0.017627 | 0.079572 | 0.007033 | 0.12325 | 0.1039 | -0.03067 | 2.969 | 3.0371 | 2.9121 | 2.7738 | 118.7374 | 118.7096 | 118.1851 | 118.5532 | 0.14474 | 0.009839 | 0.10704 | 0.034499 | 0.15071 | 0.13136 | -0.003204 | 2.9965 | 3.0646 | 2.9396 | 2.8013 | 118.7648 | 118.737 | 118.2125 | 118.5807 | -115.7684 | -115.2161 | -115.8252 | -115.2729
328.9531 | 121.8384 | -118.8309 | 2.7878 | 0.11269 | -0.008469 | 0.084151 | -0.002124 | 0.11867 | 0.1039 | -0.035248 | 2.7584 | 2.8219 | 2.7015 | 2.5541 | 118.7328 | 118.9431 | 118.4094 | 118.7775 | 0.14016 | 0.018997 | 0.11162 | 0.025342 | 0.14613 | 0.13136 | -0.007782 | 2.7858 | 2.8494 | 2.729 | 2.5815 | 118.7603 | 118.9705 | 118.4369 | 118.805 | -115.9744 | -115.651 | -116.0313 | -115.7079
330.7188 | 121.7789 | -118.808 | 2.8748 | 0.11727 | -0.00389 | 0.074994 | 0.007033 | 0.12325 | 0.099318 | -0.03067 | 2.8179 | 2.886 | 2.7702 | 2.6319 | 118.6779 | 118.8698 | 118.3545 | 118.7043 | 0.14474 | 0.023576 | 0.10246 | 0.034499 | 0.15071 | 0.12678 | -0.003204 | 2.8454 | 2.9135 | 2.7977 | 2.6594 | 118.7053 | 118.8973 | 118.3819 | 118.7317 | -115.86 | -115.5366 | -115.9076 | -115.5842
332.3906 | 121.7056 | -119.1055 | 2.5681 | 0.12185 | -0.008469 | 0.084151 | 0.002454 | 0.10951 | 0.09474 | -0.035248 | 2.4791 | 2.5564 | 2.436 | 2.2839 | 119.0029 | 119.2086 | 118.6887 | 119.0522 | 0.14932 | 0.018997 | 0.11162 | 0.02992 | 0.13698 | 0.12221 | -0.007782 | 2.5066 | 2.5838 | 2.4635 | 2.3114 | 119.0304 | 119.2361 | 118.7162 | 119.0797 | -116.5238 | -116.2096 | -116.5669 | -116.2527
334.0625 | 121.6965 | -118.721 | 2.9709 | 0.11269 | -0.008469 | 0.084151 | 0.002454 | 0.10951 | 0.090161 | -0.026092 | 2.9461 | 3.0051 | 2.8801 | 2.7464 | 118.5588 | 118.7508 | 118.2354 | 118.5944 | 0.14016 | 0.018997 | 0.11162 | 0.02992 | 0.13698 | 0.11763 | 0.001374 | 2.9736 | 3.0325 | 2.9076 | 2.7738 | 118.5863 | 118.7782 | 118.2629 | 118.6219 | -115.6127 | -115.2893 | -115.6787 | -115.3553
335.7969 | 121.7285 | -119.1879 | 2.5269 | 0.12643 | -0.013048 | 0.093308 | 0.002454 | 0.11409 | 0.09474 | -0.03067 | 2.4058 | 2.4785 | 2.3536 | 2.2152 | 119.0899 | 119.291 | 118.7711 | 118.9011 | 0.1539 | 0.014418 | 0.12077 | 0.02992 | 0.14156 | 0.12221 | -0.003204 | 2.4333 | 2.506 | 2.3811 | 2.2427 | 119.1174 | 119.3185 | 118.7986 | 118.9286 | -116.6841 | -116.3653 | -116.7363 | -116.4175
337.5312 | 121.7377 | -119.3298 | 2.4033 | 0.12185 | -0.008469 | 0.093308 | 0.011611 | 0.12325 | 0.099318 | -0.039826 | 2.3143 | 2.3732 | 2.2575 | 2.1099 | 119.1906 | 119.3963 | 118.8718 | 119.011 | 0.14932 | 0.018997 | 0.12077 | 0.039077 | 0.15071 | 0.12678 | -0.01236 | 2.3417 | 2.4007 | 2.2849 | 2.1374 | 119.2181 | 119.4238 | 118.8993 | 119.0385 | -116.8764 | -116.5576 | -116.9332 | -116.6144
339.2656 | 121.8155 | -118.8171 | 2.8107 | 0.12643 | -0.00389 | 0.079572 | 0.002454 | 0.11867 | 0.09474 | -0.035248 | 2.8271 | 2.9043 | 2.7748 | 2.6365 | 118.6641 | 118.8698 | 118.3407 | 118.48 | 0.1539 | 0.023576 | 0.10704 | 0.02992 | 0.14613 | 0.12221 | -0.007782 | 2.8545 | 2.9318 | 2.8023 | 2.6639 | 118.6916 | 118.8973 | 118.3682 | 118.5074 | -115.8371 | -115.5137 | -115.8893 | -115.5659
341 | 121.8338 | -119.2612 | 2.3621 | 0.11727 | 0.000689 | 0.079572 | 0.002454 | 0.11409 | 0.10848 | -0.026092 | 2.328 | 2.4007 | 2.2803 | 2.1374 | 119.1723 | 119.3734 | 118.8489 | 118.979 | 0.14474 | 0.028155 | 0.10704 | 0.02992 | 0.14156 | 0.13594 | 0.001374 | 2.3555 | 2.4281 | 2.3078 | 2.1648 | 119.1998 | 119.4009 | 118.8764 | 119.0064 | -116.8443 | -116.5209 | -116.892 | -116.5686
342.6719 | 121.7514 | -119.3436 | 2.3438 | 0.12643 | -0.00389 | 0.08873 | 0.020768 | 0.11409 | 0.099318 | -0.035248 | 2.2776 | 2.3457 | 2.2208 | 2.0824 | 119.2272 | 119.4283 | 118.9085 | 119.0385 | 0.1539 | 0.023576 | 0.1162 | 0.048234 | 0.14156 | 0.12678 | -0.007782 | 2.3051 | 2.3732 | 2.2483 | 2.1099 | 119.2547 | 119.4558 | 118.9359 | 119.066 | -116.9496 | -116.6308 | -117.0064 | -116.6876
344.4062 | 121.7422 | -119.252 | 2.449 | 0.11727 | -0.00389 | 0.08873 | 0.011611 | 0.12325 | 0.1039 | -0.026092 | 2.3692 | 2.4556 | 2.317 | 2.1786 | 119.1311 | 119.3276 | 118.7986 | 118.9378 | 0.14474 | 0.023576 | 0.1162 | 0.039077 | 0.15071 | 0.13136 | 0.001374 | 2.3967 | 2.4831 | 2.3444 | 2.206 | 119.1586 | 119.3551 | 118.826 | 118.9652 | -116.7619 | -116.4294 | -116.8141 | -116.4816
346.1562 | 121.7331 | -119.1055 | 2.5955 | 0.13101 | -0.008469 | 0.08873 | 0.011611 | 0.11867 | 0.1039 | -0.026092 | 2.5157 | 2.5884 | 2.4681 | 2.3297 | 118.9754 | 119.1857 | 118.6566 | 118.7958 | 0.15847 | 0.018997 | 0.1162 | 0.039077 | 0.14613 | 0.13136 | 0.001374 | 2.5432 | 2.6159 | 2.4955 | 2.3571 | 119.0029 | 119.2132 | 118.6841 | 118.8233 | -116.4597 | -116.1409 | -116.5074 | -116.1886
347.8906 | 121.7834 | -119.133 | 2.5772 | 0.12643 | -0.008469 | 0.08873 | 0.007033 | 0.12325 | 0.10848 | -0.021514 | 2.4516 | 2.5151 | 2.3948 | 2.2564 | 119.0533 | 119.2544 | 118.7345 | 118.8691 | 0.1539 | 0.018997 | 0.1162 | 0.034499 | 0.15071 | 0.13594 | 0.005952 | 2.4791 | 2.5426 | 2.4223 | 2.2839 | 119.0807 | 119.2818 | 118.7619 | 118.8966 | -116.6017 | -116.2829 | -116.6585 | -116.3397
349.5625 | 121.8475 | -119.2062 | 2.4078 | 0.12185 | -0.008469 | 0.08873 | 0.007033 | 0.11867 | 0.099318 | -0.03067 | 2.3784 | 2.4465 | 2.3215 | 2.1923 | 119.1265 | 119.3185 | 118.7986 | 118.9332 | 0.14932 | 0.018997 | 0.1162 | 0.034499 | 0.14613 | 0.12678 | -0.003204 | 2.4058 | 2.4739 | 2.349 | 2.2198 | 119.154 | 119.3459 | 118.826 | 118.9607 | -116.7482 | -116.4202 | -116.805 | -116.477
351.2969 | 121.8658 | -119.2062 | 2.4445 | 0.12643 | -0.013048 | 0.093308 | 0.002454 | 0.12325 | 0.1039 | -0.03067 | 2.3326 | 2.4053 | 2.2803 | 2.1511 | 119.154 | 119.3642 | 118.8398 | 118.9744 | 0.1539 | 0.014418 | 0.12077 | 0.02992 | 0.15071 | 0.13136 | -0.003204 | 2.36 | 2.4327 | 2.3078 | 2.1786 | 119.1815 | 119.3917 | 118.8672 | 119.0019 | -116.8214 | -116.5072 | -116.8736 | -116.5594
353.0469 | 121.7422 | -119.0964 | 2.5772 | 0.12185 | -0.013048 | 0.084151 | 0.011611 | 0.11867 | 0.10848 | -0.026092 | 2.5111 | 2.5838 | 2.4635 | 2.3205 | 118.9938 | 119.1857 | 118.6704 | 118.7913 | 0.14932 | 0.014418 | 0.11162 | 0.039077 | 0.14613 | 0.13594 | 0.001374 | 2.5386 | 2.6113 | 2.4909 | 2.348 | 119.0212 | 119.2132 | 118.6978 | 118.8187 | -116.4826 | -116.1592 | -116.5303 | -116.2069
354.7188 | 121.7331 | -118.7485 | 2.9663 | 0.11727 | 0.000689 | 0.08873 | 0.002454 | 0.11867 | 0.1039 | -0.03067 | 2.8362 | 2.9043 | 2.7702 | 2.6456 | 118.6687 | 118.8652 | 118.3453 | 118.4845 | 0.14474 | 0.028155 | 0.1162 | 0.02992 | 0.14613 | 0.13136 | -0.003204 | 2.8637 | 2.9318 | 2.7977 | 2.6731 | 118.6962 | 118.8927 | 118.3728 | 118.512 | -115.8325 | -115.5091 | -115.8985 | -115.5751
356.4688 | 121.756 | -118.9362 | 2.774 | 0.12185 | -0.008469 | 0.079572 | 0.011611 | 0.12325 | 0.1039 | -0.026092 | 2.6897 | 2.7578 | 2.6374 | 2.5037 | 118.8106 | 119.0117 | 118.4781 | 118.6265 | 0.14932 | 0.018997 | 0.10704 | 0.039077 | 0.15071 | 0.13136 | 0.001374 | 2.7172 | 2.7853 | 2.6649 | 2.5311 | 118.8381 | 119.0392 | 118.5056 | 118.6539 | -116.1209 | -115.7884 | -116.1732 | -115.8406
358.1562 | 121.7377 | -118.6981 | 2.9846 | 0.11727 | -0.008469 | 0.084151 | 0.011611 | 0.11409 | 0.1039 | -0.03067 | 2.8912 | 2.9639 | 2.8389 | 2.696 | 118.6 | 118.7966 | 118.2766 | 118.4159 | 0.14474 | 0.018997 | 0.11162 | 0.039077 | 0.14156 | 0.13136 | -0.003204 | 2.9186 | 2.9913 | 2.8664 | 2.7235 | 118.6275 | 118.824 | 118.3041 | 118.4433 | -115.7089 | -115.3855 | -115.7611 | -115.4377
359.9062 | 121.8475 | -118.5104 | 3.067 | 0.13101 | 0.000689 | 0.093308 | 0.007033 | 0.12782 | 0.099318 | -0.03067 | 3.0102 | 3.0783 | 2.9671 | 2.8288 | 118.4856 | 118.6867 | 118.1622 | 118.306 | 0.15847 | 0.028155 | 0.12077 | 0.034499 | 0.15529 | 0.12678 | -0.003204 | 3.0377 | 3.1058 | 2.9946 | 2.8563 | 118.513 | 118.7142 | 118.1896 | 118.3334 | -115.4754 | -115.152 | -115.5185 | -115.1951
361.5781 | 121.8567 | -118.5883 | 3.0167 | 0.12185 | -0.008469 | 0.074994 | 0.01619 | 0.12325 | 0.10848 | -0.026092 | 3.0102 | 3.0783 | 2.9579 | 2.8196 | 118.4856 | 118.6821 | 118.1622 | 118.306 | 0.14932 | 0.018997 | 0.10246 | 0.043656 | 0.15071 | 0.13594 | 0.001374 | 3.0377 | 3.1058 | 2.9854 | 2.8471 | 118.513 | 118.7096 | 118.1896 | 118.3334 | -115.4754 | -115.152 | -115.5276 | -115.2042
363.25 | 121.8155 | -118.0115 | 3.5843 | 0.12643 | -0.008469 | 0.084151 | 0.01619 | 0.12325 | 0.1039 | -0.03067 | 3.3215 | 3.3943 | 3.3242 | 3.3142 | 118.394 | 118.3616 | 118.0843 | 118.2236 | 0.1539 | 0.018997 | 0.11162 | 0.043656 | 0.15071 | 0.13136 | -0.003204 | 3.349 | 3.4217 | 3.3517 | 3.3416 | 118.4215 | 118.3891 | 118.1118 | 118.251 | -115.0725 | -114.7628 | -115.0698 | -114.7602
364.9844 | 121.8063 | -119.3619 | 2.2888 | 0.11727 | -0.008469 | 0.084151 | 0.011611 | 0.12782 | 0.099318 | -0.03067 | 2.6027 | 2.6708 | 2.555 | 2.5815 | 119.1448 | 119.0987 | 118.6109 | 118.9469 | 0.14474 | 0.018997 | 0.11162 | 0.039077 | 0.15529 | 0.12678 | -0.003204 | 2.6302 | 2.6983 | 2.5825 | 2.609 | 119.1723 | 119.1262 | 118.6383 | 118.9744 | -116.5421 | -116.0081 | -116.5898 | -116.0558
366.7188 | 121.9025 | -119.6045 | 2.0325 | 0.12643 | -0.008469 | 0.084151 | 0.007033 | 0.11867 | 0.1039 | -0.03067 | 1.9342 | 2.0023 | 1.8775 | 1.7436 | 119.5889 | 119.7854 | 119.2701 | 119.6337 | 0.1539 | 0.018997 | 0.11162 | 0.034499 | 0.14613 | 0.13136 | -0.003204 | 1.9617 | 2.0298 | 1.9049 | 1.771 | 119.6164 | 119.8129 | 119.2976 | 119.6611 | -117.6547 | -117.3359 | -117.7115 | -117.3927
368.3906 | 121.9116 | -120.1996 | 1.4603 | 0.12643 | -0.008469 | 0.084151 | 0.002454 | 0.12325 | 0.099318 | -0.039826 | 1.5222 | 1.5948 | 1.4608 | 1.3315 | 120.001 | 120.202 | 119.6914 | 120.0457 | 0.1539 | 0.018997 | 0.11162 | 0.02992 | 0.15071 | 0.12678 | -0.01236 | 1.5497 | 1.6223 | 1.4883 | 1.3589 | 120.0284 | 120.2295 | 119.7188 | 120.0732 | -118.4788 | -118.1692 | -118.5401 | -118.2305
370.0625 | 121.8613 | -120.3644 | 1.3229 | 0.11727 | -0.00389 | 0.084151 | 0.007033 | 0.12782 | 0.11305 | -0.026092 | 1.3299 | 1.3979 | 1.2777 | 1.1346 | 120.2161 | 120.4035 | 119.8791 | 120.2471 | 0.14474 | 0.023576 | 0.11162 | 0.034499 | 0.15529 | 0.14052 | 0.001374 | 1.3574 | 1.4254 | 1.3052 | 1.162 | 120.2436 | 120.4309 | 119.9065 | 120.2746 | -118.8862 | -118.5492 | -118.9384 | -118.6014
371.7969 | 121.8796 | -120.1263 | 1.5656 | 0.12185 | -0.008469 | 0.079572 | 0.007033 | 0.12325 | 0.1039 | -0.03067 | 1.6092 | 1.6772 | 1.557 | 1.4368 | 119.914 | 120.1105 | 119.5952 | 119.9633 | 0.14932 | 0.018997 | 0.10704 | 0.034499 | 0.15071 | 0.13136 | -0.003204 | 1.6366 | 1.7047 | 1.5844 | 1.4642 | 119.9414 | 120.1379 | 119.6227 | 119.9907 | -118.3048 | -117.986 | -118.357 | -118.0382
373.4688 | 121.9345 | -120.1309 | 1.5427 | 0.12185 | -0.008469 | 0.084151 | 0.01619 | 0.12325 | 0.09474 | -0.03067 | 1.4947 | 1.5628 | 1.4425 | 1.3086 | 120.0467 | 120.2432 | 119.7143 | 119.8626 | 0.14932 | 0.018997 | 0.11162 | 0.043656 | 0.15071 | 0.12221 | -0.003204 | 1.5222 | 1.5902 | 1.47 | 1.336 | 120.0742 | 120.2707 | 119.7417 | 119.89 | -118.552 | -118.2195 | -118.6042 | -118.2717
375.2031 | 121.9254 | -120.0485 | 1.6525 | 0.12185 | -0.008469 | 0.079572 | 0.025347 | 0.12782 | 0.1039 | -0.035248 | 1.5909 | 1.6635 | 1.5341 | 1.4001 | 119.9506 | 120.1425 | 119.6227 | 119.7664 | 0.14932 | 0.018997 | 0.10704 | 0.052813 | 0.15529 | 0.13136 | -0.007782 | 1.6183 | 1.691 | 1.5615 | 1.4276 | 119.9781 | 120.17 | 119.6501 | 119.7939 | -118.3597 | -118.0318 | -118.4165 | -118.0886
376.9375 | 121.9116 | -120.5566 | 1.1124 | 0.11727 | -0.013048 | 0.08873 | 0.01619 | 0.1324 | 0.11305 | -0.03067 | 1.0643 | 1.1415 | 1.0076 | 0.8827 | 120.4817 | 120.6919 | 120.1446 | 120.2883 | 0.14474 | 0.014418 | 0.1162 | 0.043656 | 0.15987 | 0.14052 | -0.003204 | 1.0918 | 1.169 | 1.035 | 0.91017 | 120.5091 | 120.7193 | 120.1721 | 120.3158 | -119.4173 | -119.0803 | -119.4741 | -119.137
378.6719 | 121.8018 | -120.2911 | 1.4191 | 0.12643 | -0.013048 | 0.079572 | 0.011611 | 0.14156 | 0.11305 | -0.026092 | 1.2704 | 1.3521 | 1.2228 | 1.0842 | 120.2711 | 120.4721 | 119.9477 | 120.0869 | 0.1539 | 0.014418 | 0.10704 | 0.039077 | 0.16902 | 0.14052 | 0.001374 | 1.2978 | 1.3796 | 1.2502 | 1.1116 | 120.2985 | 120.4996 | 119.9752 | 120.1144 | -119.0007 | -118.6774 | -119.0483 | -118.725
380.3594 | 121.9345 | -120.4697 | 1.2451 | 0.12643 | -0.00389 | 0.08873 | 0.029925 | 0.12782 | 0.1039 | -0.03067 | 1.2063 | 1.2972 | 1.1541 | 1.0247 | 120.3397 | 120.5408 | 120.0164 | 120.151 | 0.1539 | 0.023576 | 0.1162 | 0.057391 | 0.15529 | 0.13136 | -0.003204 | 1.2337 | 1.3246 | 1.1816 | 1.0521 | 120.3672 | 120.5683 | 120.0439 | 120.1784 | -119.1335 | -118.8102 | -119.1857 | -118.8623
382.0938 | 121.8521 | -120.2637 | 1.4648 | 0.11727 | -0.008469 | 0.074994 | 0.025347 | 0.13698 | 0.11763 | -0.03067 | 1.4489 | 1.5261 | 1.4059 | 1.2673 | 120.0971 | 120.2936 | 119.7738 | 119.9083 | 0.14474 | 0.018997 | 0.10246 | 0.052813 | 0.16445 | 0.1451 | -0.003204 | 1.4764 | 1.5536 | 1.4334 | 1.2948 | 120.1246 | 120.3211 | 119.8012 | 119.9358 | -118.6482 | -118.3248 | -118.6912 | -118.3679
383.8438 | 121.7743 | -120.314 | 1.4557 | 0.12643 | -0.008469 | 0.084151 | 0.01619 | 0.14156 | 0.11763 | -0.03067 | 1.3528 | 1.43 | 1.3052 | 1.1712 | 120.1932 | 120.3943 | 119.8745 | 120.0045 | 0.1539 | 0.018997 | 0.11162 | 0.043656 | 0.16902 | 0.1451 | -0.003204 | 1.3802 | 1.4574 | 1.3326 | 1.1986 | 120.2207 | 120.4218 | 119.902 | 120.0319 | -118.8405 | -118.5217 | -118.8881 | -118.5693
385.5312 | 121.875 | -120.3278 | 1.3504 | 0.12643 | -0.00389 | 0.08873 | 0.020768 | 0.13698 | 0.12221 | -0.03067 | 1.3894 | 1.4574 | 1.3372 | 1.1987 | 120.152 | 120.3577 | 119.8333 | 119.9679 | 0.1539 | 0.023576 | 0.1162 | 0.048234 | 0.16445 | 0.14968 | -0.003204 | 1.4169 | 1.4849 | 1.3647 | 1.2261 | 120.1795 | 120.3851 | 119.8608 | 119.9953 | -118.7626 | -118.4439 | -118.8148 | -118.4961
387.2656 | 121.8567 | -120.0577 | 1.6571 | 0.11727 | -0.013048 | 0.08873 | 0.020768 | 0.14156 | 0.12679 | -0.03067 | 1.5771 | 1.6498 | 1.5203 | 1.3864 | 119.9735 | 120.1746 | 119.6547 | 119.7847 | 0.14474 | 0.014418 | 0.1162 | 0.048234 | 0.16902 | 0.15425 | -0.003204 | 1.6046 | 1.6772 | 1.5478 | 1.4139 | 120.0009 | 120.202 | 119.6822 | 119.8122 | -118.3964 | -118.0776 | -118.4531 | -118.1344
389 | 121.7468 | -120.1492 | 1.6022 | 0.11727 | -0.008469 | 0.079572 | 0.025347 | 0.15529 | 0.13595 | -0.026092 | 1.4993 | 1.5719 | 1.4517 | 1.3131 | 120.0422 | 120.2478 | 119.7234 | 119.858 | 0.14474 | 0.018997 | 0.10704 | 0.052813 | 0.18276 | 0.16341 | 0.001374 | 1.5268 | 1.5994 | 1.4791 | 1.3406 | 120.0696 | 120.2753 | 119.7509 | 119.8854 | -118.5429 | -118.2241 | -118.5905 | -118.2717
390.75 | 121.7606 | -120.1813 | 1.5472 | 0.12185 | -0.013048 | 0.084151 | 0.034504 | 0.14614 | 0.12679 | -0.03067 | 1.4581 | 1.5353 | 1.4105 | 1.2719 | 120.0879 | 120.2936 | 119.7692 | 119.9038 | 0.14932 | 0.014418 | 0.11162 | 0.06197 | 0.1736 | 0.15425 | -0.003204 | 1.4856 | 1.5627 | 1.4379 | 1.2994 | 120.1154 | 120.3211 | 119.7967 | 119.9312 | -118.6299 | -118.3111 | -118.6775 | -118.3587
392.4375 | 121.8246 | -120.1035 | 1.6205 | 0.12185 | -0.008469 | 0.08873 | 0.034504 | 0.14614 | 0.13595 | -0.03067 | 1.5405 | 1.6223 | 1.4975 | 1.3727 | 120.0055 | 120.202 | 119.6868 | 119.8259 | 0.14932 | 0.018997 | 0.1162 | 0.06197 | 0.1736 | 0.16341 | -0.003204 | 1.568 | 1.6497 | 1.5249 | 1.4001 | 120.033 | 120.2295 | 119.7142 | 119.8534 | -118.465 | -118.1463 | -118.5081 | -118.1893
394.1875 | 121.9025 | -120.0943 | 1.6113 | 0.12185 | -0.00389 | 0.079572 | 0.043661 | 0.15987 | 0.13595 | -0.035248 | 1.5771 | 1.6406 | 1.5203 | 1.3818 | 119.9826 | 120.1883 | 119.6639 | 119.7985 | 0.14932 | 0.023576 | 0.10704 | 0.071127 | 0.18734 | 0.16341 | -0.007782 | 1.6046 | 1.6681 | 1.5478 | 1.4093 | 120.0101 | 120.2158 | 119.6914 | 119.8259 | -118.4055 | -118.0868 | -118.4623 | -118.1435
395.9531 | 121.7789 | -120.1172 | 1.6388 | 0.13101 | -0.008469 | 0.079572 | 0.039082 | 0.15529 | 0.13137 | -0.026092 | 1.5634 | 1.636 | 1.502 | 1.3727 | 120.0055 | 120.1975 | 119.6776 | 119.8168 | 0.15847 | 0.018997 | 0.10704 | 0.066548 | 0.18276 | 0.15883 | 0.001374 | 1.5909 | 1.6635 | 1.5295 | 1.4001 | 120.033 | 120.2249 | 119.7051 | 119.8442 | -118.4421 | -118.1142 | -118.5035 | -118.1756
397.6406 | 121.8338 | -120.1218 | 1.5701 | 0.12185 | -0.00389 | 0.084151 | 0.039082 | 0.15529 | 0.13595 | -0.026092 | 1.5313 | 1.6223 | 1.4883 | 1.3589 | 120.0193 | 120.2203 | 119.7051 | 119.8397 | 0.14932 | 0.023576 | 0.11162 | 0.066548 | 0.18276 | 0.16341 | 0.001374 | 1.5588 | 1.6497 | 1.5158 | 1.3864 | 120.0467 | 120.2478 | 119.7326 | 119.8671 | -118.4879 | -118.1738 | -118.531 | -118.2168
399.375 | 121.9025 | -120.3918 | 1.2955 | 0.13101 | -0.008469 | 0.084151 | 0.043661 | 0.15071 | 0.13137 | -0.026092 | 1.2292 | 1.3063 | 1.1724 | 1.0384 | 120.3306 | 120.5316 | 120.0073 | 120.1464 | 0.15847 | 0.018997 | 0.11162 | 0.071127 | 0.17818 | 0.15883 | 0.001374 | 1.2566 | 1.3338 | 1.1999 | 1.0659 | 120.358 | 120.5591 | 120.0347 | 120.1739 | -119.1014 | -118.7781 | -119.1582 | -118.8349
401.0469 | 121.8475 | -120.1813 | 1.5106 | 0.10812 | -0.013048 | 0.093308 | 0.043661 | 0.14614 | 0.13137 | -0.03067 | 1.4215 | 1.4987 | 1.3693 | 1.2399 | 120.1246 | 120.3394 | 119.8104 | 119.9495 | 0.13558 | 0.014418 | 0.12077 | 0.071127 | 0.1736 | 0.15883 | -0.003204 | 1.4489 | 1.5261 | 1.3967 | 1.2673 | 120.152 | 120.3668 | 119.8379 | 119.977 | -118.7031 | -118.3889 | -118.7553 | -118.4411
402.7969 | 121.8704 | -120.4742 | 1.2085 | 0.12185 | -0.008469 | 0.08873 | 0.034504 | 0.14614 | 0.13137 | -0.03067 | 1.1651 | 1.2331 | 1.1175 | 0.96971 | 120.3993 | 120.6049 | 120.0759 | 120.2197 | 0.14932 | 0.018997 | 0.1162 | 0.06197 | 0.1736 | 0.15883 | -0.003204 | 1.1925 | 1.2605 | 1.1449 | 0.99717 | 120.4267 | 120.6324 | 120.1034 | 120.2471 | -119.2342 | -118.9109 | -119.2818 | -118.9585
404.5312 | 121.7834 | -120.5017 | 1.2589 | 0.13101 | -0.00389 | 0.08873 | 0.048239 | 0.15071 | 0.12679 | -0.026092 | 1.4764 | 1.5399 | 1.4242 | 1.2811 | 120.0925 | 120.2982 | 119.7692 | 119.8946 | 0.15847 | 0.023576 | 0.1162 | 0.075705 | 0.17818 | 0.15425 | 0.001374 | 1.5039 | 1.5673 | 1.4517 | 1.3085 | 120.12 | 120.3256 | 119.7967 | 119.9221 | -118.6161 | -118.2928 | -118.6683 | -118.345
406.2812 | 121.8567 | -120.0302 | 1.6708 | 0.12185 | -0.008469 | 0.08873 | 0.039082 | 0.15529 | 0.12679 | -0.026092 | 1.7282 | 1.8009 | 1.6714 | 1.5329 | 119.8361 | 120.0281 | 119.5128 | 119.6428 | 0.14932 | 0.018997 | 0.1162 | 0.066548 | 0.18276 | 0.15425 | 0.001374 | 1.7557 | 1.8283 | 1.6989 | 1.5604 | 119.8636 | 120.0555 | 119.5403 | 119.6703 | -118.1079 | -117.7846 | -118.1647 | -117.8414
408.0156 | 121.8155 | -120.52 | 1.2222 | 0.12185 | -0.008469 | 0.08873 | 0.048239 | 0.15529 | 0.14052 | -0.026092 | 1.1605 | 1.2285 | 1.0991 | 0.96971 | 120.4038 | 120.6095 | 120.0897 | 120.2197 | 0.14932 | 0.018997 | 0.1162 | 0.075705 | 0.18276 | 0.16799 | 0.001374 | 1.188 | 1.256 | 1.1266 | 0.99717 | 120.4313 | 120.6369 | 120.1171 | 120.2471 | -119.2433 | -118.9292 | -119.3047 | -118.9905
409.75 | 121.8292 | -120.5475 | 1.236 | 0.12643 | -0.00389 | 0.08873 | 0.043661 | 0.15071 | 0.13137 | -0.03067 | 1.1422 | 1.2193 | 1.0854 | 0.96055 | 120.4267 | 120.6278 | 120.108 | 120.238 | 0.1539 | 0.023576 | 0.1162 | 0.071127 | 0.17818 | 0.15883 | -0.003204 | 1.1696 | 1.2468 | 1.1129 | 0.98801 | 120.4542 | 120.6553 | 120.1355 | 120.2654 | -119.2846 | -118.9658 | -119.3413 | -119.0226
411.4219 | 121.8063 | -120.4697 | 1.3138 | 0.11727 | -0.00389 | 0.084151 | 0.048239 | 0.15071 | 0.13137 | -0.026092 | 1.1925 | 1.2697 | 1.1404 | 0.99718 | 120.3672 | 120.5683 | 120.0576 | 120.1922 | 0.14474 | 0.023576 | 0.11162 | 0.075705 | 0.17818 | 0.15883 | 0.001374 | 1.22 | 1.2972 | 1.1678 | 1.0246 | 120.3947 | 120.5957 | 120.0851 | 120.2197 | -119.1747 | -118.8651 | -119.2269 | -118.9173
413.1719 | 121.7834 | -120.4742 | 1.3046 | 0.12185 | -0.00389 | 0.08873 | 0.01619 | 0.12782 | 0.1039 | -0.026092 | 1.2429 | 1.3155 | 1.1953 | 1.0659 | 120.3168 | 120.5179 | 119.989 | 120.1372 | 0.14932 | 0.023576 | 0.1162 | 0.043656 | 0.15529 | 0.13136 | 0.001374 | 1.2704 | 1.343 | 1.2228 | 1.0933 | 120.3443 | 120.5454 | 120.0164 | 120.1647 | -119.0739 | -118.7461 | -119.1216 | -118.7937
414.9219 | 121.9025 | -120.5383 | 1.1627 | 0.12643 | -0.00389 | 0.08873 | 0.048239 | 0.15071 | 0.14052 | -0.016936 | 1.101 | 1.1781 | 1.0534 | 0.92392 | 120.4771 | 120.6598 | 120.1492 | 120.2792 | 0.1539 | 0.023576 | 0.1162 | 0.075705 | 0.17818 | 0.16799 | 0.01053 | 1.1284 | 1.2056 | 1.0808 | 0.95138 | 120.5045 | 120.6873 | 120.1767 | 120.3066 | -119.3761 | -119.0482 | -119.4237 | -119.0958
416.6094 | 121.7514 | -120.6482 | 1.1261 | 0.12643 | -0.00389 | 0.08873 | 0.052818 | 0.14614 | 0.12679 | -0.021514 | 1.101 | 1.1919 | 1.0579 | 0.92392 | 120.4542 | 120.6598 | 120.1355 | 120.27 | 0.1539 | 0.023576 | 0.1162 | 0.080284 | 0.1736 | 0.15425 | 0.005952 | 1.1284 | 1.2193 | 1.0854 | 0.95138 | 120.4817 | 120.6873 | 120.1629 | 120.2975 | -119.3532 | -119.0345 | -119.3962 | -119.0775
418.3438 | 121.8384 | -120.5566 | 1.181 | 0.13101 | -0.008469 | 0.08873 | 0.01619 | 0.12325 | 0.10848 | -0.016936 | 1.101 | 1.1552 | 1.0351 | 0.9056 | 120.4908 | 120.6781 | 120.1675 | 120.3112 | 0.15847 | 0.018997 | 0.1162 | 0.043656 | 0.15071 | 0.13594 | 0.01053 | 1.1284 | 1.1827 | 1.0625 | 0.93307 | 120.5183 | 120.7056 | 120.195 | 120.3387 | -119.3899 | -119.0665 | -119.4558 | -119.1325
420.0781 | 121.8155 | -120.6299 | 1.1536 | 0.13101 | -0.008469 | 0.08873 | 0.034504 | 0.15071 | 0.13595 | -0.026092 | 1.0735 | 1.1461 | 1.0259 | 0.88728 | 120.4954 | 120.6919 | 120.1858 | 120.3112 | 0.15847 | 0.018997 | 0.1162 | 0.06197 | 0.17818 | 0.16341 | 0.001374 | 1.101 | 1.1735 | 1.0534 | 0.91475 | 120.5229 | 120.7193 | 120.2133 | 120.3387 | -119.4219 | -119.1123 | -119.4695 | -119.1599
421.75 | 121.8109 | -120.4605 | 1.3092 | 0.12643 | -0.00389 | 0.08873 | 0.039082 | 0.15529 | 0.13137 | -0.026092 | 1.2337 | 1.3018 | 1.1816 | 1.0476 | 120.3352 | 120.5316 | 120.0164 | 120.1647 | 0.1539 | 0.023576 | 0.1162 | 0.066548 | 0.18276 | 0.15883 | 0.001374 | 1.2612 | 1.3292 | 1.209 | 1.075 | 120.3626 | 120.5591 | 120.0439 | 120.1922 | -119.1014 | -118.7827 | -119.1536 | -118.8349
423.4844 | 121.9025 | -120.4788 | 1.2268 | 0.12643 | 0.000689 | 0.093308 | 0.034504 | 0.15071 | 0.13137 | -0.021514 | 1.1651 | 1.2422 | 1.1129 | 0.97429 | 120.3947 | 120.6049 | 120.0805 | 120.2105 | 0.1539 | 0.028155 | 0.12077 | 0.06197 | 0.17818 | 0.15883 | 0.005952 | 1.1925 | 1.2697 | 1.1403 | 1.0018 | 120.4221 | 120.6324 | 120.108 | 120.238 | -119.2296 | -118.9155 | -119.2818 | -118.9676
425.2188 | 121.9208 | -120.4239 | 1.2589 | 0.12643 | 0.000689 | 0.093308 | 0.025347 | 0.12782 | 0.10848 | -0.016936 | 1.22 | 1.2972 | 1.1632 | 1.0338 | 120.3443 | 120.5454 | 120.0256 | 120.1601 | 0.1539 | 0.028155 | 0.12077 | 0.052813 | 0.15529 | 0.13594 | 0.01053 | 1.2475 | 1.3246 | 1.1907 | 1.0613 | 120.3718 | 120.5728 | 120.053 | 120.1876 | -119.1243 | -118.8056 | -119.1811 | -118.8623
426.8906 | 121.788 | -120.5566 | 1.2314 | 0.12643 | -0.00389 | 0.093308 | 0.029925 | 0.14156 | 0.12221 | -0.021514 | 1.1696 | 1.2331 | 1.1129 | 0.97886 | 120.4084 | 120.6003 | 120.0851 | 120.2288 | 0.1539 | 0.023576 | 0.12077 | 0.057391 | 0.16902 | 0.14968 | 0.005952 | 1.1971 | 1.2605 | 1.1403 | 1.0063 | 120.4359 | 120.6278 | 120.1126 | 120.2563 | -119.2388 | -118.9155 | -119.2955 | -118.9722
428.625 | 121.8704 | -120.5933 | 1.1581 | 0.13101 | 0.005267 | 0.097887 | 0.020768 | 0.1324 | 0.10848 | -0.016936 | 1.0048 | 1.0866 | 0.94806 | 0.8186 | 120.5686 | 120.7606 | 120.2499 | 120.3845 | 0.15847 | 0.032733 | 0.12535 | 0.048234 | 0.15987 | 0.13594 | 0.01053 | 1.0323 | 1.114 | 0.97553 | 0.84606 | 120.5961 | 120.788 | 120.2774 | 120.4119 | -119.5638 | -119.2451 | -119.6206 | -119.3019
430.3594 | 121.7789 | -120.5658 | 1.1627 | 0.13101 | -0.00389 | 0.097887 | 0.025347 | 0.1324 | 0.11763 | -0.012357 | 1.1055 | 1.1873 | 1.0625 | 0.92392 | 120.4633 | 120.6507 | 120.1446 | 120.2792 | 0.15847 | 0.023576 | 0.12535 | 0.052813 | 0.15987 | 0.1451 | 0.015109 | 1.133 | 1.2148 | 1.09 | 0.95138 | 120.4908 | 120.6781 | 120.1721 | 120.3066 | -119.3578 | -119.0391 | -119.4008 | -119.0821
432.1094 | 121.7468 | -120.6299 | 1.1307 | 0.071489 | -0.054257 | 0.033786 | -0.15321 | -0.059872 | -0.065504 | -0.085608 | 1.6275 | 1.6864 | 1.557 | 1.423 | 119.9552 | 120.1471 | 119.6364 | 119.7618 | 0.098955 | -0.026791 | 0.061252 | -0.12575 | -0.032406 | -0.038038 | -0.058142 | 1.655 | 1.7138 | 1.5844 | 1.4505 | 119.9826 | 120.1746 | 119.6639 | 119.7893 | -118.3277 | -118.0089 | -118.3982 | -118.0794
433.8438 | 121.8292 | -119.9066 | 1.8402 | -0.07502 | -0.20078 | -0.12646 | -0.18069 | -0.069028 | -0.083817 | -0.2138 | 1.7145 | 1.7825 | 1.6531 | 1.5238 | 119.859 | 120.051 | 119.5448 | 119.684 | -0.047554 | -0.17331 | -0.098999 | -0.15322 | -0.041562 | -0.056351 | -0.18633 | 1.7419 | 1.81 | 1.6806 | 1.5512 | 119.8865 | 120.0784 | 119.5723 | 119.7115 | -118.1445 | -117.8304 | -118.2059 | -117.8917
435.5156 | 121.8842 | -121.0007 | 0.71411 | 0.12643 | 0.000689 | 0.097887 | 0.01619 | 0.12782 | 0.1039 | -0.016936 | 0.65227 | 0.72941 | 0.60469 | 0.47517 | 120.9257 | 121.1131 | 120.607 | 120.7278 | 0.1539 | 0.028155 | 0.12535 | 0.043656 | 0.15529 | 0.13136 | 0.01053 | 0.67974 | 0.75687 | 0.63216 | 0.50264 | 120.9532 | 121.1405 | 120.6345 | 120.7553 | -120.2735 | -119.9548 | -120.3211 | -120.0023
437.25 | 121.8704 | -120.8084 | 0.90637 | 0.12185 | -0.00389 | 0.08873 | 0.01619 | 0.11867 | 0.10848 | -0.021514 | 0.84915 | 0.9263 | 0.78782 | 0.66291 | 120.7335 | 120.9254 | 120.4102 | 120.5493 | 0.14932 | 0.023576 | 0.1162 | 0.043656 | 0.14613 | 0.13594 | 0.005952 | 0.87661 | 0.95376 | 0.81529 | 0.69038 | 120.7609 | 120.9528 | 120.4376 | 120.5768 | -119.8843 | -119.561 | -119.9456 | -119.6223
438.9844 | 121.7972 | -121.2479 | 0.49896 | 0.13101 | -0.00389 | 0.08873 | 0.01619 | 0.1324 | 0.10848 | -0.026092 | 0.43708 | 0.52336 | 0.38951 | 0.26911 | 121.1363 | 121.3328 | 120.8176 | 120.9522 | 0.15847 | 0.023576 | 0.1162 | 0.043656 | 0.15987 | 0.13594 | 0.001374 | 0.46455 | 0.55083 | 0.41698 | 0.29658 | 121.1638 | 121.3603 | 120.8451 | 120.9796 | -120.6993 | -120.3806 | -120.7468 | -120.4281
440.7188 | 121.9162 | -121.2067 | 0.48065 | 0.11727 | -0.00389 | 0.093308 | 0.01619 | 0.12325 | 0.1039 | -0.026092 | 0.43708 | 0.50963 | 0.38951 | 0.27369 | 121.1409 | 121.3374 | 120.8222 | 120.9567 | 0.14474 | 0.023576 | 0.12077 | 0.043656 | 0.15071 | 0.13136 | 0.001374 | 0.46455 | 0.53709 | 0.41698 | 0.30116 | 121.1684 | 121.3649 | 120.8497 | 120.9842 | -120.7038 | -120.3851 | -120.7514 | -120.4327
442.3906 | 121.7789 | -121.4172 | 0.36163 | 0.12643 | 0.000689 | 0.08873 | 0.020768 | 0.12325 | 0.10848 | -0.026092 | 0.3043 | 0.37226 | 0.26132 | 0.17296 | 121.2783 | 121.4793 | 120.9596 | 121.0895 | 0.1539 | 0.028155 | 0.1162 | 0.048234 | 0.15071 | 0.13594 | 0.001374 | 0.33177 | 0.39973 | 0.28879 | 0.20042 | 121.3057 | 121.5068 | 120.987 | 121.117 | -120.974 | -120.6553 | -121.0169 | -120.6983
444.0781 | 121.788 | -121.4218 | 0.37537 | 0.11727 | -0.00389 | 0.084151 | 0.007033 | 0.12325 | 0.11305 | -0.016936 | 0.28141 | 0.34937 | 0.24301 | 0.15464 | 121.3286 | 121.493 | 120.987 | 121.1078 | 0.14474 | 0.023576 | 0.11162 | 0.034499 | 0.15071 | 0.14052 | 0.01053 | 0.30888 | 0.37683 | 0.27047 | 0.1821 | 121.3561 | 121.5205 | 121.0145 | 121.1353 | -121.0472 | -120.7056 | -121.0856 | -120.744
445.8281 | 121.8246 | -121.1838 | 0.55847 | 0.044018 | -0.08173 | 0.006315 | -0.061645 | 0.036265 | 0.030642 | -0.099343 | 0.38214 | 0.46384 | 0.32999 | 0.24622 | 121.2508 | 121.374 | 120.9184 | 121.0392 | 0.071484 | -0.054264 | 0.033781 | -0.034179 | 0.063731 | 0.058108 | -0.071877 | 0.40961 | 0.4913 | 0.35746 | 0.27369 | 121.2783 | 121.4015 | 120.9458 | 121.0666 | -120.8687 | -120.5362 | -120.9208 | -120.5884
447.5625 | 121.6003 | -121.3989 | 0.17853 | 0.11269 | -0.017627 | 0.070415 | 0.002454 | 0.10951 | 0.1039 | -0.03067 | 2.6805 | 2.7853 | 2.2391 | 2.1923 | 71.0786 | 70.9649 | 118.3453 | 118.4983 | 0.14016 | 0.009839 | 0.097881 | 0.02992 | 0.13698 | 0.13136 | -0.003204 | 2.708 | 2.8128 | 2.2666 | 2.2198 | 71.1061 | 70.9924 | 118.3728 | 118.5257 | -68.398 | -115.6648 | -68.8395 | -116.1062
449.2344 | 121.788 | -121.5866 | 0.16479 | 0.12185 | -0.008469 | 0.079572 | 0.01619 | 0.11867 | 0.1039 | -0.026092 | 0.093694 | 0.17079 | 0.069033 | 0.095112 | 0.043657 | 0.055266 | 121.1519 | 121.5107 | 0.14932 | 0.018997 | 0.10704 | 0.043656 | 0.14613 | 0.13136 | 0.001374 | 0.12116 | 0.19826 | 0.096499 | 0.12258 | 0.071123 | 0.082732 | 121.1793 | 121.5382 | 0.050037 | -121.0582 | 0.025376 | -121.0828
450.9844 | 121.7697 | -121.5866 | 0.16937 | 0.11727 | -0.008469 | 0.079572 | 0.011611 | 0.12782 | 0.099318 | -0.026092 | 0.098273 | 0.17995 | 0.069033 | -0.033101 | 0.025345 | 0.050688 | 121.1473 | 121.5153 | 0.14474 | 0.018997 | 0.10704 | 0.039077 | 0.15529 | 0.12678 | 0.001374 | 0.12574 | 0.20742 | 0.096499 | -0.005635 | 0.052811 | 0.078154 | 121.1748 | 121.5427 | 0.072928 | -121.049 | 0.043688 | -121.0783
452.6719 | 121.8613 | -121.55 | 0.14648 | 0.11269 | 0.000689 | 0.084151 | 0.007033 | 0.12325 | 0.1039 | -0.026092 | 0.10285 | 0.17995 | 0.07819 | -0.055996 | 0.01161 | 0.041532 | 121.1564 | 121.2864 | 0.14016 | 0.028155 | 0.11162 | 0.034499 | 0.15071 | 0.13136 | 0.001374 | 0.13032 | 0.20742 | 0.10566 | -0.02853 | 0.039076 | 0.068998 | 121.1839 | 121.3138 | 0.091241 | -121.0536 | 0.06658 | -121.0783
454.4062 | 121.7972 | -121.5866 | 0.1831 | 0.12643 | -0.013048 | 0.079572 | 0.01619 | 0.12325 | 0.1039 | -0.021514 | 0.098273 | 0.17537 | 0.073611 | -0.042259 | 0.01161 | 0.036954 | 121.1473 | 121.2909 | 0.1539 | 0.014418 | 0.10704 | 0.043656 | 0.15071 | 0.13136 | 0.005952 | 0.12574 | 0.20284 | 0.10108 | -0.014793 | 0.039076 | 0.06442 | 121.1748 | 121.3184 | 0.086663 | -121.049 | 0.062001 | -121.0737
456.1562 | 121.7606 | -121.5866 | 0.19226 | 0.11269 | -0.008469 | 0.08873 | 0.011611 | 0.12782 | 0.09474 | -0.03067 | 0.098273 | 0.17537 | 0.07819 | -0.092628 | 0.020767 | 0.032376 | 121.1519 | 121.2864 | 0.14016 | 0.018997 | 0.1162 | 0.039077 | 0.15529 | 0.12221 | -0.003204 | 0.12574 | 0.20284 | 0.10566 | -0.065162 | 0.048233 | 0.059842 | 121.1793 | 121.3138 | 0.077506 | -121.0536 | 0.057423 | -121.0737
457.9062 | 121.8338 | -121.5729 | 0.16479 | 0.12185 | -0.008469 | 0.079572 | 0.01619 | 0.12325 | 0.1039 | -0.021514 | 0.098273 | 0.17537 | 0.07819 | -0.069733 | 0.016188 | 0.041532 | 121.1519 | 121.2909 | 0.14932 | 0.018997 | 0.10704 | 0.043656 | 0.15071 | 0.13136 | 0.005952 | 0.12574 | 0.20284 | 0.10566 | -0.042267 | 0.043654 | 0.068998 | 121.1793 | 121.3184 | 0.082085 | -121.0536 | 0.062002 | -121.0737
459.5938 | 121.7789 | -121.5866 | 0.17395 | 0.12185 | -0.013048 | 0.084151 | 0.011611 | 0.12325 | 0.099318 | -0.021514 | 0.093694 | 0.16622 | 0.069033 | -0.074312 | 0.020767 | 0.032376 | 121.1519 | 121.2955 | 0.14932 | 0.014418 | 0.11162 | 0.039077 | 0.15071 | 0.12678 | 0.005952 | 0.12116 | 0.19368 | 0.096499 | -0.046846 | 0.048233 | 0.059842 | 121.1793 | 121.323 | 0.072927 | -121.0582 | 0.048266 | -121.0828
461.3438 | 121.843 | -121.5729 | 0.16479 | 0.12643 | -0.017627 | 0.084151 | 0.011611 | 0.11867 | 0.1039 | -0.03067 | 0.093694 | 0.17079 | 0.073611 | -0.060575 | 0.01161 | 0.032376 | 121.1519 | 121.2909 | 0.1539 | 0.009839 | 0.11162 | 0.039077 | 0.14613 | 0.13136 | -0.003204 | 0.12116 | 0.19826 | 0.10108 | -0.033109 | 0.039076 | 0.059842 | 121.1793 | 121.3184 | 0.082084 | -121.0582 | 0.062001 | -121.0783
463.0156 | 121.9116 | -121.5408 | 0.13733 | 0.11727 | -0.00389 | 0.084151 | 0.007033 | 0.12325 | 0.09474 | -0.021514 | 0.098273 | 0.16622 | 0.073611 | -0.097207 | 0.016188 | 0.032376 | 121.161 | 121.2909 | 0.14474 | 0.023576 | 0.11162 | 0.034499 | 0.15071 | 0.12221 | 0.005952 | 0.12574 | 0.19368 | 0.10108 | -0.069741 | 0.043654 | 0.059842 | 121.1885 | 121.3184 | 0.082085 | -121.0627 | 0.057423 | -121.0874
464.75 | 121.7743 | -121.5729 | 0.18768 | 0.11727 | -0.00389 | 0.084151 | 0.020768 | 0.12782 | 0.099318 | -0.021514 | 0.089116 | 0.16622 | 0.064455 | -0.069733 | 0.007032 | 0.032376 | 121.161 | 121.3047 | 0.14474 | 0.023576 | 0.11162 | 0.048234 | 0.15529 | 0.12678 | 0.005952 | 0.11658 | 0.19368 | 0.091921 | -0.042267 | 0.034498 | 0.059842 | 121.1885 | 121.3321 | 0.082084 | -121.0719 | 0.057423 | -121.0966
466.4844 | 121.8521 | -121.6187 | 0.16022 | 0.11269 | -0.008469 | 0.079572 | 0.011611 | 0.12782 | 0.099318 | -0.026092 | 0.093694 | 0.17079 | 0.073611 | 0.090533 | 0.080283 | 0.032376 | 121.3945 | 121.5199 | 0.14016 | 0.018997 | 0.10704 | 0.039077 | 0.15529 | 0.12678 | 0.001374 | 0.12116 | 0.19826 | 0.10108 | 0.118 | 0.10775 | 0.059842 | 121.422 | 121.5473 | 0.013411 | -121.3008 | -0.006672 | -121.3209
468.1719 | 121.875 | -121.5637 | 0.13275 | 0.11727 | -0.008469 | 0.08873 | 0.002454 | 0.12782 | 0.090161 | -0.035248 | 0.093694 | 0.17537 | 0.069033 | -0.074312 | 0.007032 | 0.027798 | 121.2251 | 121.5336 | 0.14474 | 0.018997 | 0.1162 | 0.02992 | 0.15529 | 0.11763 | -0.007782 | 0.12116 | 0.20284 | 0.096499 | -0.046846 | 0.034498 | 0.055264 | 121.2526 | 121.5611 | 0.086662 | -121.1314 | 0.062001 | -121.1561
469.8906 | 121.8658 | -121.5683 | 0.15106 | 0.12643 | -0.013048 | 0.084151 | 0.002454 | 0.11867 | 0.099318 | -0.026092 | 0.098273 | 0.16622 | 0.064455 | -0.097207 | 0.01161 | 0.036954 | 121.1793 | 121.5382 | 0.1539 | 0.014418 | 0.11162 | 0.02992 | 0.14613 | 0.12678 | 0.001374 | 0.12574 | 0.19368 | 0.091921 | -0.069741 | 0.039076 | 0.06442 | 121.2068 | 121.5656 | 0.086663 | -121.0811 | 0.052845 | -121.1149
471.5781 | 121.7606 | -121.6095 | 0.16937 | 0.12643 | -0.00389 | 0.084151 | 0.011611 | 0.11409 | 0.09474 | -0.026092 | 0.079959 | 0.16622 | 0.059877 | -0.092628 | 0.01161 | 0.02322 | 121.1793 | 121.5427 | 0.1539 | 0.023576 | 0.11162 | 0.039077 | 0.14156 | 0.12221 | 0.001374 | 0.10743 | 0.19368 | 0.087343 | -0.065162 | 0.039076 | 0.050686 | 121.2068 | 121.5702 | 0.068349 | -121.0994 | 0.048267 | -121.1195
473.25 | 121.8018 | -121.6049 | 0.17395 | 0.11727 | -0.008469 | 0.084151 | 0.011611 | 0.11867 | 0.11305 | -0.03067 | 0.089116 | 0.16622 | 0.064455 | -0.088049 | 0.01161 | 0.027798 | 121.1839 | 121.5382 | 0.14474 | 0.018997 | 0.11162 | 0.039077 | 0.14613 | 0.14052 | -0.003204 | 0.11658 | 0.19368 | 0.091921 | -0.060583 | 0.039076 | 0.055264 | 121.2114 | 121.5656 | 0.077506 | -121.0948 | 0.052845 | -121.1195
474.9844 | 121.8521 | -121.5729 | 0.15106 | 0.11727 | -0.00389 | 0.079572 | 0.011611 | 0.11867 | 0.09474 | -0.026092 | 0.093694 | 0.17079 | 0.073611 | -0.069733 | 0.01161 | 0.032376 | 121.1839 | 121.323 | 0.14474 | 0.023576 | 0.10704 | 0.039077 | 0.14613 | 0.12221 | 0.001374 | 0.12116 | 0.19826 | 0.10108 | -0.042267 | 0.039076 | 0.059842 | 121.2114 | 121.3505 | 0.082084 | -121.0902 | 0.062001 | -121.1103
476.6562 | 121.8567 | -121.5775 | 0.16937 | 0.11727 | -0.013048 | 0.079572 | 0.011611 | 0.12325 | 0.090161 | -0.026092 | 0.093694 | 0.17537 | 0.064455 | -0.08347 | 0.007032 | 0.027798 | 121.1931 | 121.3276 | 0.14474 | 0.014418 | 0.10704 | 0.039077 | 0.15071 | 0.11763 | 0.001374 | 0.12116 | 0.20284 | 0.091921 | -0.056004 | 0.034498 | 0.055264 | 121.2205 | 121.355 | 0.086662 | -121.0994 | 0.057423 | -121.1286
478.3906 | 121.7972 | -121.6003 | 0.1831 | 0.11269 | -0.008469 | 0.08873 | 0.020768 | 0.12325 | 0.1039 | -0.021514 | 0.098273 | 0.17079 | 0.064455 | -0.097207 | 0.002454 | 0.027798 | 121.1931 | 121.323 | 0.14016 | 0.018997 | 0.1162 | 0.048234 | 0.15071 | 0.13136 | 0.005952 | 0.12574 | 0.19826 | 0.091921 | -0.069741 | 0.02992 | 0.055264 | 121.2205 | 121.3505 | 0.095819 | -121.0948 | 0.062001 | -121.1286
480.125 | 121.8201 | -121.6095 | 0.17853 | 0.11269 | -0.008469 | 0.084151 | 0.01619 | 0.12782 | 0.090161 | -0.026092 | 0.089116 | 0.16164 | 0.064455 | -0.08347 | 0.002454 | 0.02322 | 121.1931 | 121.3322 | 0.14016 | 0.018997 | 0.11162 | 0.043656 | 0.15529 | 0.11763 | 0.001374 | 0.11658 | 0.1891 | 0.091921 | -0.056004 | 0.02992 | 0.050686 | 121.2205 | 121.3596 | 0.086662 | -121.104 | 0.062001 | -121.1286
481.875 | 121.7926 | -121.6095 | 0.16937 | 0.12185 | -0.008469 | 0.084151 | 0.011611 | 0.12782 | 0.099318 | -0.016936 | 0.089116 | 0.17079 | 0.064455 | -0.10179 | 0.007032 | 0.02322 | 121.1931 | 121.3276 | 0.14932 | 0.018997 | 0.11162 | 0.039077 | 0.15529 | 0.12678 | 0.01053 | 0.11658 | 0.19826 | 0.091921 | -0.07432 | 0.034498 | 0.050686 | 121.2205 | 121.355 | 0.082084 | -121.104 | 0.057423 | -121.1286
483.5625 | 121.9299 | -121.5546 | 0.14648 | 0.12643 | 0.000689 | 0.079572 | 0.011611 | 0.11409 | 0.10848 | -0.03067 | 0.084537 | 0.17079 | 0.069033 | -0.092628 | 0.002454 | 0.027798 | 121.1931 | 121.3276 | 0.1539 | 0.028155 | 0.10704 | 0.039077 | 0.14156 | 0.13594 | -0.003204 | 0.112 | 0.19826 | 0.096499 | -0.065162 | 0.02992 | 0.055264 | 121.2205 | 121.355 | 0.082083 | -121.1085 | 0.066579 | -121.124
485.2969 | 121.843 | -121.6003 | 0.16479 | 0.11727 | -0.013048 | 0.084151 | 0.007033 | 0.11409 | 0.099318 | -0.021514 | 0.089116 | 0.17995 | 0.059877 | -0.065154 | 0.002454 | 0.027798 | 121.1885 | 121.3276 | 0.14474 | 0.014418 | 0.11162 | 0.034499 | 0.14156 | 0.12678 | 0.005952 | 0.11658 | 0.20742 | 0.087343 | -0.037688 | 0.02992 | 0.055264 | 121.216 | 121.355 | 0.086662 | -121.0994 | 0.057423 | -121.1286
487.0312 | 121.8018 | -121.6187 | 0.15564 | 0.12643 | -0.008469 | 0.084151 | 0.011611 | 0.12325 | 0.11305 | -0.021514 | 0.089116 | 0.17537 | 0.064455 | -0.092628 | 0.002454 | 0.027798 | 121.1885 | 121.3184 | 0.1539 | 0.018997 | 0.11162 | 0.039077 | 0.15071 | 0.14052 | 0.005952 | 0.11658 | 0.20284 | 0.091921 | -0.065162 | 0.02992 | 0.055264 | 121.216 | 121.3459 | 0.086662 | -121.0994 | 0.062001 | -121.124
488.7031 | 121.9254 | -121.5683 | 0.14191 | 0.11727 | -0.013048 | 0.079572 | 0.01619 | 0.12325 | 0.1039 | -0.03067 | 0.089116 | 0.17079 | 0.069033 | -0.088049 | 0.002454 | 0.02322 | 121.1885 | 121.3322 | 0.14474 | 0.014418 | 0.10704 | 0.043656 | 0.15071 | 0.13136 | -0.003204 | 0.11658 | 0.19826 | 0.096499 | -0.060583 | 0.02992 | 0.050686 | 121.216 | 121.3596 | 0.086662 | -121.0994 | 0.066579 | -121.1195
490.4375 | 121.9299 | -121.582 | 0.15564 | 0.11727 | -0.008469 | 0.084151 | 0.020768 | 0.11409 | 0.09474 | -0.026092 | 0.10285 | 0.17079 | 0.069033 | -0.078891 | 0.002454 | 0.02322 | 121.1931 | 121.323 | 0.14474 | 0.018997 | 0.11162 | 0.048234 | 0.14156 | 0.12221 | 0.001374 | 0.13032 | 0.19826 | 0.096499 | -0.051425 | 0.02992 | 0.050686 | 121.2205 | 121.3505 | 0.1004 | -121.0902 | 0.066579 | -121.124
492.1094 | 121.8063 | -121.6187 | 0.20142 | 0.12643 | -0.00389 | 0.08873 | 0.01619 | 0.12325 | 0.1039 | -0.021514 | 0.093694 | 0.16622 | 0.069033 | -0.060575 | 0.002454 | 0.032376 | 121.1885 | 121.3367 | 0.1539 | 0.023576 | 0.1162 | 0.043656 | 0.15071 | 0.13136 | 0.005952 | 0.12116 | 0.19368 | 0.096499 | -0.033109 | 0.02992 | 0.059842 | 121.216 | 121.3642 | 0.09124 | -121.0948 | 0.066579 | -121.1195
493.8438 | 121.8292 | -121.6187 | 0.16937 | 0.12185 | -0.00389 | 0.084151 | 0.020768 | 0.12325 | 0.09474 | -0.03067 | 0.089116 | 0.17537 | 0.073611 | -0.078891 | 0.007032 | 0.018642 | 121.1931 | 121.3322 | 0.14932 | 0.023576 | 0.11162 | 0.048234 | 0.15071 | 0.12221 | -0.003204 | 0.11658 | 0.20284 | 0.10108 | -0.051425 | 0.034498 | 0.046108 | 121.2205 | 121.3596 | 0.082084 | -121.104 | 0.066579 | -121.1195
495.5938 | 121.8384 | -121.6324 | 0.15106 | 0.12643 | -0.00389 | 0.084151 | 0.011611 | 0.12782 | 0.1039 | -0.03067 | 0.093694 | 0.17995 | 0.073611 | -0.08347 | 0.002454 | 0.02322 | 121.1931 | 121.3322 | 0.1539 | 0.023576 | 0.11162 | 0.039077 | 0.15529 | 0.13136 | -0.003204 | 0.12116 | 0.20742 | 0.10108 | -0.056004 | 0.02992 | 0.050686 | 121.2205 | 121.3596 | 0.09124 | -121.0994 | 0.071157 | -121.1195
497.2812 | 121.9391 | -121.582 | 0.14648 | 0.12185 | -0.008469 | 0.08873 | 0.020768 | 0.12782 | 0.1039 | -0.026092 | 0.098273 | 0.17995 | 0.069033 | -0.088049 | 0.002454 | 0.018642 | 121.2022 | 121.3367 | 0.14932 | 0.018997 | 0.1162 | 0.048234 | 0.15529 | 0.13136 | 0.001374 | 0.12574 | 0.20742 | 0.096499 | -0.060583 | 0.02992 | 0.046108 | 121.2297 | 121.3642 | 0.095819 | -121.104 | 0.066579 | -121.1332
499.0156 | 121.8201 | -121.6049 | 0.17395 | 0.11727 | -0.013048 | 0.084151 | 0.011611 | 0.12782 | 0.099318 | -0.03067 | 0.098273 | 0.17079 | 0.069033 | -0.097207 | 0.016188 | 0.02322 | 121.1976 | 121.3367 | 0.14474 | 0.014418 | 0.11162 | 0.039077 | 0.15529 | 0.12678 | -0.003204 | 0.12574 | 0.19826 | 0.096499 | -0.069741 | 0.043654 | 0.050686 | 121.2251 | 121.3642 | 0.082085 | -121.0994 | 0.052845 | -121.1286
500.7656 | 121.9437 | -121.582 | 0.13733 | 0.11727 | -0.008469 | 0.08873 | 0.01619 | 0.12325 | 0.099318 | -0.026092 | 0.093694 | 0.16622 | 0.073611 | -0.088049 | 0.002454 | 0.018642 | 121.1976 | 121.3367 | 0.14474 | 0.018997 | 0.1162 | 0.043656 | 0.15071 | 0.12678 | 0.001374 | 0.12116 | 0.19368 | 0.10108 | -0.060583 | 0.02992 | 0.046108 | 121.2251 | 121.3642 | 0.09124 | -121.104 | 0.071157 | -121.124
502.4531 | 121.9391 | -121.5683 | 0.14191 | 0.11269 | -0.00389 | 0.084151 | 0.01619 | 0.12325 | 0.099318 | -0.021514 | 0.093694 | 0.17537 | 0.064455 | -0.088049 | 0.007032 | 0.02322 | 121.2068 | 121.3459 | 0.14016 | 0.023576 | 0.11162 | 0.043656 | 0.15071 | 0.12678 | 0.005952 | 0.12116 | 0.20284 | 0.091921 | -0.060583 | 0.034498 | 0.050686 | 121.2343 | 121.3734 | 0.086662 | -121.1131 | 0.057423 | -121.1423
504.1875 | 121.8658 | -121.5912 | 0.16022 | 0.12185 | -0.008469 | 0.08873 | 0.020768 | 0.11867 | 0.090161 | -0.026092 | 0.098273 | 0.16622 | 0.064455 | -0.10179 | 0.002454 | 0.032376 | 121.2022 | 121.3367 | 0.14932 | 0.018997 | 0.1162 | 0.048234 | 0.14613 | 0.11763 | 0.001374 | 0.12574 | 0.19368 | 0.091921 | -0.07432 | 0.02992 | 0.059842 | 121.2297 | 121.3642 | 0.095819 | -121.104 | 0.062001 | -121.1378
505.9375 | 121.8658 | -121.582 | 0.15564 | 0.11269 | -0.00389 | 0.084151 | 0.011611 | 0.11867 | 0.099318 | -0.021514 | 0.084537 | 0.16622 | 0.064455 | -0.055996 | 0.007032 | 0.027798 | 121.2114 | 121.3459 | 0.14016 | 0.023576 | 0.11162 | 0.039077 | 0.14613 | 0.12678 | 0.005952 | 0.112 | 0.19368 | 0.091921 | -0.02853 | 0.034498 | 0.055264 | 121.2388 | 121.3734 | 0.077505 | -121.1268 | 0.057423 | -121.1469
507.6094 | 121.9666 | -121.5729 | 0.14191 | 0.11727 | -0.00389 | 0.084151 | 0.011611 | 0.12325 | 0.090161 | -0.021514 | 0.093694 | 0.17079 | 0.069033 | -0.078891 | 0.007032 | 0.02322 | 121.2068 | 121.3459 | 0.14474 | 0.023576 | 0.11162 | 0.039077 | 0.15071 | 0.11763 | 0.005952 | 0.12116 | 0.19826 | 0.096499 | -0.051425 | 0.034498 | 0.050686 | 121.2343 | 121.3734 | 0.086662 | -121.1131 | 0.062001 | -121.1378
509.3438 | 121.9299 | -121.5958 | 0.12817 | 0.12185 | -0.013048 | 0.079572 | 0.007033 | 0.11409 | 0.09474 | -0.026092 | 0.093694 | 0.17537 | 0.059877 | -0.10637 | 0.002454 | 0.02322 | 121.2022 | 121.3322 | 0.14932 | 0.014418 | 0.10704 | 0.034499 | 0.14156 | 0.12221 | 0.001374 | 0.12116 | 0.20284 | 0.087343 | -0.078899 | 0.02992 | 0.050686 | 121.2297 | 121.3596 | 0.09124 | -121.1085 | 0.057423 | -121.1423
511.0781 | 121.9162 | -121.6095 | 0.16479 | 0.11269 | -0.008469 | 0.08873 | 0.01619 | 0.12325 | 0.09474 | -0.03067 | 0.098273 | 0.16164 | 0.059877 | -0.097207 | 0.002454 | 0.02322 | 121.2114 | 121.3367 | 0.14016 | 0.018997 | 0.1162 | 0.043656 | 0.15071 | 0.12221 | -0.003204 | 0.12574 | 0.1891 | 0.087343 | -0.069741 | 0.02992 | 0.050686 | 121.2388 | 121.3642 | 0.095819 | -121.1131 | 0.057423 | -121.1515
512.8281 | 121.7972 | -121.6141 | 0.16022 | 0.11727 | -0.00389 | 0.084151 | 0.011611 | 0.12325 | 0.09474 | -0.021514 | 0.093694 | 0.17079 | 0.059877 | -0.10637 | -0.002124 | 0.02322 | 121.2114 | 121.3413 | 0.14474 | 0.023576 | 0.11162 | 0.039077 | 0.15071 | 0.12221 | 0.005952 | 0.12116 | 0.19826 | 0.087343 | -0.078899 | 0.025342 | 0.050686 | 121.2388 | 121.3688 | 0.095818 | -121.1177 | 0.062001 | -121.1515
514.5156 | 121.875 | -121.6049 | 0.15106 | 0.11727 | -0.008469 | 0.079572 | 0.025347 | 0.12325 | 0.099318 | -0.021514 | 0.093694 | 0.16622 | 0.07819 | -0.097207 | 0.007032 | 0.032376 | 121.2022 | 121.3459 | 0.14474 | 0.018997 | 0.10704 | 0.052813 | 0.15071 | 0.12678 | 0.005952 | 0.12116 | 0.19368 | 0.10566 | -0.069741 | 0.034498 | 0.059842 | 121.2297 | 121.3734 | 0.086662 | -121.1085 | 0.071158 | -121.124
516.25 | 121.8658 | -121.6141 | 0.16022 | 0.12185 | -0.008469 | 0.079572 | 0.007033 | 0.11867 | 0.09474 | -0.026092 | 0.093694 | 0.17537 | 0.069033 | -0.10179 | -0.006702 | 0.02322 | 121.2114 | 121.3459 | 0.14932 | 0.018997 | 0.10704 | 0.034499 | 0.14613 | 0.12221 | 0.001374 | 0.12116 | 0.20284 | 0.096499 | -0.07432 | 0.020764 | 0.050686 | 121.2388 | 121.3734 | 0.1004 | -121.1177 | 0.075735 | -121.1423
518 | 121.8933 | -121.6095 | 0.14191 | 0.11727 | -0.013048 | 0.079572 | 0.011611 | 0.11409 | 0.099318 | -0.021514 | 0.093694 | 0.17995 | 0.064455 | -0.092628 | 0.002454 | 0.032376 | 121.2022 | 121.3367 | 0.14474 | 0.014418 | 0.10704 | 0.039077 | 0.14156 | 0.12678 | 0.005952 | 0.12116 | 0.20742 | 0.091921 | -0.065162 | 0.02992 | 0.059842 | 121.2297 | 121.3642 | 0.09124 | -121.1085 | 0.062001 | -121.1378
519.6719 | 121.907 | -121.6003 | 0.14648 | 0.12185 | -0.013048 | 0.08873 | 0.011611 | 0.11867 | 0.09474 | -0.026092 | 0.093694 | 0.16622 | 0.064455 | -0.051417 | 0.002454 | 0.02322 | 121.2022 | 121.3413 | 0.14932 | 0.014418 | 0.1162 | 0.039077 | 0.14613 | 0.12221 | 0.001374 | 0.12116 | 0.19368 | 0.091921 | -0.023951 | 0.02992 | 0.050686 | 121.2297 | 121.3688 | 0.09124 | -121.1085 | 0.062001 | -121.1378
521.4062 | 121.9482 | -121.5591 | 0.12817 | 0.12185 | -0.013048 | 0.084151 | 0.01619 | 0.10951 | 0.099318 | -0.021514 | 0.093694 | 0.17079 | 0.069033 | -0.097207 | 0.002454 | 0.02322 | 121.2022 | 121.3413 | 0.14932 | 0.014418 | 0.11162 | 0.043656 | 0.13698 | 0.12678 | 0.005952 | 0.12116 | 0.19826 | 0.096499 | -0.069741 | 0.02992 | 0.050686 | 121.2297 | 121.3688 | 0.09124 | -121.1085 | 0.066579 | -121.1332
523.1562 | 121.9574 | -121.5683 | 0.13733 | 0.11269 | -0.008469 | 0.08873 | 0.011611 | 0.12325 | 0.09474 | -0.03067 | 0.10285 | 0.17537 | 0.064455 | -0.088049 | 0.002454 | 0.02322 | 121.2114 | 121.3459 | 0.14016 | 0.018997 | 0.1162 | 0.039077 | 0.15071 | 0.12221 | -0.003204 | 0.13032 | 0.20284 | 0.091921 | -0.060583 | 0.02992 | 0.050686 | 121.2388 | 121.3734 | 0.1004 | -121.1085 | 0.062001 | -121.1469
524.8906 | 121.8933 | -121.6049 | 0.15564 | 0.11727 | -0.008469 | 0.084151 | 0.01619 | 0.11409 | 0.09474 | -0.026092 | 0.10285 | 0.17537 | 0.064455 | -0.097207 | -0.006702 | 0.02322 | 121.2068 | 121.3413 | 0.14474 | 0.018997 | 0.11162 | 0.043656 | 0.14156 | 0.12221 | 0.001374 | 0.13032 | 0.20284 | 0.091921 | -0.069741 | 0.020764 | 0.050686 | 121.2343 | 121.3688 | 0.10955 | -121.104 | 0.071157 | -121.1423
526.5625 | 121.9345 | -121.5454 | 0.12817 | 0.12185 | -0.008469 | 0.079572 | 0.011611 | 0.12325 | 0.09474 | -0.026092 | 0.093694 | 0.17079 | 0.069033 | -0.074312 | 0.002454 | 0.027798 | 121.1976 | 121.3322 | 0.14932 | 0.018997 | 0.10704 | 0.039077 | 0.15071 | 0.12221 | 0.001374 | 0.12116 | 0.19826 | 0.096499 | -0.046846 | 0.02992 | 0.055264 | 121.2251 | 121.3596 | 0.09124 | -121.104 | 0.066579 | -121.1286
528.3125 | 121.8201 | -121.6324 | 0.1831 | 0.11727 | -0.013048 | 0.084151 | 0.020768 | 0.12325 | 0.099318 | -0.021514 | 0.10285 | 0.17537 | 0.073611 | -0.092628 | 0.007032 | 0.02322 | 121.2114 | 121.3505 | 0.14474 | 0.014418 | 0.11162 | 0.048234 | 0.15071 | 0.12678 | 0.005952 | 0.13032 | 0.20284 | 0.10108 | -0.065162 | 0.034498 | 0.050686 | 121.2388 | 121.3779 | 0.095819 | -121.1085 | 0.066579 | -121.1378
529.9844 | 121.8475 | -121.6415 | 0.16937 | 0.11727 | -0.008469 | 0.084151 | 0.011611 | 0.12325 | 0.09474 | -0.035248 | 0.098273 | 0.17995 | 0.073611 | -0.097207 | 0.002454 | 0.02322 | 121.2205 | 121.3413 | 0.14474 | 0.018997 | 0.11162 | 0.039077 | 0.15071 | 0.12221 | -0.007782 | 0.12574 | 0.20742 | 0.10108 | -0.069741 | 0.02992 | 0.050686 | 121.248 | 121.3688 | 0.095819 | -121.1223 | 0.071157 | -121.1469
531.7188 | 121.8201 | -121.6415 | 0.1831 | 0.12185 | -0.008469 | 0.084151 | 0.01619 | 0.12782 | 0.085583 | -0.026092 | 0.098273 | 0.16622 | 0.073611 | -0.055996 | 0.007032 | 0.02322 | 121.216 | 121.355 | 0.14932 | 0.018997 | 0.11162 | 0.043656 | 0.15529 | 0.11305 | 0.001374 | 0.12574 | 0.19368 | 0.10108 | -0.02853 | 0.034498 | 0.050686 | 121.2434 | 121.3825 | 0.091241 | -121.1177 | 0.066579 | -121.1423
533.4531 | 121.8201 | -121.6324 | 0.17853 | 0.11727 | -0.008469 | 0.079572 | 0.01619 | 0.12325 | 0.090161 | -0.026092 | 0.10285 | 0.17995 | 0.07819 | -0.03768 | -0.011281 | 0.018642 | 121.2068 | 121.355 | 0.14474 | 0.018997 | 0.10704 | 0.043656 | 0.15071 | 0.11763 | 0.001374 | 0.13032 | 0.20742 | 0.10566 | -0.010214 | 0.016185 | 0.046108 | 121.2343 | 121.3825 | 0.11413 | -121.104 | 0.089471 | -121.1286
535.125 | 121.8155 | -121.6232 | 0.1831 | 0.12185 | -0.008469 | 0.079572 | 0.020768 | 0.12325 | 0.10848 | -0.021514 | 0.10743 | 0.17995 | 0.082768 | 0.099691 | 0.002454 | 0.014064 | 121.2709 | 121.5336 | 0.14932 | 0.018997 | 0.10704 | 0.048234 | 0.15071 | 0.13594 | 0.005952 | 0.1349 | 0.20742 | 0.11023 | 0.12716 | 0.02992 | 0.04153 | 121.2984 | 121.5611 | 0.10498 | -121.1635 | 0.080314 | -121.1881
536.875 | 121.8246 | -121.6187 | 0.18768 | 0.12185 | -0.008469 | 0.084151 | 0.007033 | 0.12325 | 0.099318 | -0.021514 | 0.098273 | 0.17995 | 0.064455 | -0.046838 | 0.007032 | 0.018642 | 121.2022 | 121.3322 | 0.14932 | 0.018997 | 0.11162 | 0.034499 | 0.15071 | 0.12678 | 0.005952 | 0.12574 | 0.20742 | 0.091921 | -0.019372 | 0.034498 | 0.046108 | 121.2297 | 121.3596 | 0.091241 | -121.104 | 0.057423 | -121.1378
538.5469 | 121.8201 | -121.6278 | 0.19684 | 0.12185 | -0.013048 | 0.084151 | 0.01619 | 0.12325 | 0.1039 | -0.026092 | 0.10285 | 0.17995 | 0.073611 | -0.078891 | 0.007032 | 0.018642 | 121.2114 | 121.3413 | 0.14932 | 0.014418 | 0.11162 | 0.043656 | 0.15071 | 0.13136 | 0.001374 | 0.13032 | 0.20742 | 0.10108 | -0.051425 | 0.034498 | 0.046108 | 121.2388 | 121.3688 | 0.095819 | -121.1085 | 0.066579 | -121.1378
540.2812 | 121.9528 | -121.6003 | 0.13275 | 0.12185 | -0.00389 | 0.079572 | 0.01619 | 0.11867 | 0.099318 | -0.021514 | 0.10285 | 0.17537 | 0.073611 | -0.042259 | -0.002124 | 0.018642 | 121.2022 | 121.3367 | 0.14932 | 0.023576 | 0.10704 | 0.043656 | 0.14613 | 0.12678 | 0.005952 | 0.13032 | 0.20284 | 0.10108 | -0.014793 | 0.025342 | 0.046108 | 121.2297 | 121.3642 | 0.10497 | -121.0994 | 0.075735 | -121.1286
542.0312 | 121.9391 | -121.5958 | 0.15106 | 0.11727 | 0.000689 | 0.079572 | 0.01619 | 0.11867 | 0.1039 | -0.03067 | 0.10743 | 0.17537 | 0.07819 | -0.03768 | 0.002454 | 0.014064 | 121.2068 | 121.3413 | 0.14474 | 0.028155 | 0.10704 | 0.043656 | 0.14613 | 0.13136 | -0.003204 | 0.1349 | 0.20284 | 0.10566 | -0.010214 | 0.02992 | 0.04153 | 121.2343 | 121.3688 | 0.10498 | -121.0994 | 0.075736 | -121.1286
543.7656 | 121.8475 | -121.637 | 0.19684 | 0.12643 | -0.008469 | 0.084151 | 0.011611 | 0.12782 | 0.1039 | -0.021514 | 0.10285 | 0.18453 | 0.082768 | -0.051417 | 0.002454 | 0.018642 | 121.2114 | 121.3505 | 0.1539 | 0.018997 | 0.11162 | 0.039077 | 0.15529 | 0.13136 | 0.005952 | 0.13032 | 0.212 | 0.11023 | -0.023951 | 0.02992 | 0.046108 | 121.2388 | 121.3779 | 0.1004 | -121.1085 | 0.080314 | -121.1286
545.4375 | 121.8384 | -121.637 | 0.17853 | 0.12643 | -0.013048 | 0.084151 | 0.01619 | 0.11867 | 0.099318 | -0.016936 | 0.10285 | 0.18453 | 0.07819 | -0.03768 | 0.002454 | 0.02322 | 121.216 | 121.3459 | 0.1539 | 0.014418 | 0.11162 | 0.043656 | 0.14613 | 0.12678 | 0.01053 | 0.13032 | 0.212 | 0.10566 | -0.010214 | 0.02992 | 0.050686 | 121.2434 | 121.3734 | 0.1004 | -121.1131 | 0.075736 | -121.1378
547.1719 | 121.8201 | -121.637 | 0.17395 | 0.11727 | 0.000689 | 0.084151 | 0.01619 | 0.12325 | 0.099318 | -0.026092 | 0.098273 | 0.18453 | 0.07819 | -0.055996 | 0.002454 | 0.02322 | 121.2114 | 121.355 | 0.14474 | 0.028155 | 0.11162 | 0.043656 | 0.15071 | 0.12678 | 0.001374 | 0.12574 | 0.212 | 0.10566 | -0.02853 | 0.02992 | 0.050686 | 121.2388 | 121.3825 | 0.095819 | -121.1131 | 0.075736 | -121.1332
548.9219 | 121.8338 | -121.6553 | 0.17853 | 0.11727 | -0.008469 | 0.084151 | 0.025347 | 0.12325 | 0.1039 | -0.026092 | 0.098273 | 0.17537 | 0.082768 | -0.060575 | 0.002454 | 0.02322 | 121.2251 | 121.3505 | 0.14474 | 0.018997 | 0.11162 | 0.052813 | 0.15071 | 0.13136 | 0.001374 | 0.12574 | 0.20284 | 0.11023 | -0.033109 | 0.02992 | 0.050686 | 121.2526 | 121.3779 | 0.095819 | -121.1268 | 0.080314 | -121.1423
550.5938 | 121.8338 | -121.6461 | 0.19226 | 0.11269 | -0.00389 | 0.08873 | 0.011611 | 0.12325 | 0.099318 | -0.016936 | 0.10743 | 0.17537 | 0.07819 | -0.023943 | -0.002124 | 0.02322 | 121.2251 | 121.3505 | 0.14016 | 0.023576 | 0.1162 | 0.039077 | 0.15071 | 0.12678 | 0.01053 | 0.1349 | 0.20284 | 0.10566 | 0.003523 | 0.025342 | 0.050686 | 121.2526 | 121.3779 | 0.10955 | -121.1177 | 0.080314 | -121.1469
552.3281 | 121.9757 | -121.6232 | 0.13275 | 0.11727 | -0.013048 | 0.084151 | 0.020768 | 0.11867 | 0.099318 | -0.026092 | 0.10285 | 0.17537 | 0.07819 | -0.028522 | -0.006702 | 0.014064 | 121.2205 | 121.3596 | 0.14474 | 0.014418 | 0.11162 | 0.048234 | 0.14613 | 0.12678 | 0.001374 | 0.13032 | 0.20284 | 0.10566 | -0.001056 | 0.020764 | 0.04153 | 121.248 | 121.3871 | 0.10955 | -121.1177 | 0.084892 | -121.1423
554.0625 | 121.8384 | -121.6324 | 0.16022 | 0.12185 | -0.00389 | 0.08873 | 0.020768 | 0.12782 | 0.09474 | -0.021514 | 0.098273 | 0.17995 | 0.082768 | -0.055996 | -0.002124 | 0.018642 | 121.2251 | 121.355 | 0.14932 | 0.023576 | 0.1162 | 0.048234 | 0.15529 | 0.12221 | 0.005952 | 0.12574 | 0.20742 | 0.11023 | -0.02853 | 0.025342 | 0.046108 | 121.2526 | 121.3825 | 0.1004 | -121.1268 | 0.084892 | -121.1423
555.8125 | 121.9437 | -121.6232 | 0.16479 | 0.11727 | -0.00389 | 0.079572 | 0.011611 | 0.12782 | 0.1039 | -0.021514 | 0.10285 | 0.17995 | 0.073611 | -0.060575 | -0.006702 | 0.014064 | 121.2205 | 121.355 | 0.14474 | 0.023576 | 0.10704 | 0.039077 | 0.15529 | 0.13136 | 0.005952 | 0.13032 | 0.20742 | 0.10108 | -0.033109 | 0.020764 | 0.04153 | 121.248 | 121.3825 | 0.10955 | -121.1177 | 0.080313 | -121.1469
557.4844 | 121.8567 | -121.6232 | 0.19226 | 0.12643 | -0.00389 | 0.084151 | 0.020768 | 0.12325 | 0.09474 | -0.021514 | 0.10285 | 0.17995 | 0.073611 | -0.042259 | -0.002124 | 0.014064 | 121.2389 | 121.3642 | 0.1539 | 0.023576 | 0.11162 | 0.048234 | 0.15071 | 0.12221 | 0.005952 | 0.13032 | 0.20742 | 0.10108 | -0.014793 | 0.025342 | 0.04153 | 121.2663 | 121.3917 | 0.10497 | -121.136 | 0.075735 | -121.1652
559.2188 | 121.8796 | -121.6599 | 0.1831 | 0.12643 | -0.00389 | 0.08873 | 0.011611 | 0.11867 | 0.099318 | -0.021514 | 0.10743 | 0.18453 | 0.07819 | -0.046838 | -0.011281 | 0.009486 | 121.2297 | 121.3642 | 0.1539 | 0.023576 | 0.1162 | 0.039077 | 0.14613 | 0.12678 | 0.005952 | 0.1349 | 0.212 | 0.10566 | -0.019372 | 0.016185 | 0.036952 | 121.2572 | 121.3917 | 0.11871 | -121.1223 | 0.089471 | -121.1515
560.9688 | 121.8979 | -121.6415 | 0.17395 | 0.12643 | 0.000689 | 0.084151 | 0.020768 | 0.12325 | 0.099318 | -0.016936 | 0.10285 | 0.17995 | 0.07819 | -0.051417 | -0.006702 | 0.014064 | 121.2389 | 121.3779 | 0.1539 | 0.028155 | 0.11162 | 0.048234 | 0.15071 | 0.12678 | 0.01053 | 0.13032 | 0.20742 | 0.10566 | -0.023951 | 0.020764 | 0.04153 | 121.2663 | 121.4054 | 0.10955 | -121.136 | 0.084892 | -121.1607
562.6406 | 121.994 | -121.6141 | 0.15106 | 0.12185 | -0.008469 | 0.08873 | 0.011611 | 0.12782 | 0.09474 | -0.021514 | 0.098273 | 0.18453 | 0.073611 | -0.069733 | -0.011281 | 0.009486 | 121.2297 | 121.3642 | 0.14932 | 0.018997 | 0.1162 | 0.039077 | 0.15529 | 0.12221 | 0.005952 | 0.12574 | 0.212 | 0.10108 | -0.042267 | 0.016185 | 0.036952 | 121.2572 | 121.3917 | 0.10955 | -121.1314 | 0.084892 | -121.1561
564.3906 | 121.9345 | -121.6278 | 0.15106 | 0.12185 | -0.008469 | 0.074994 | 0.01619 | 0.11867 | 0.099318 | -0.026092 | 0.098273 | 0.17079 | 0.07819 | -0.019364 | -0.011281 | -0.004248 | 121.2343 | 121.3642 | 0.14932 | 0.018997 | 0.10246 | 0.043656 | 0.14613 | 0.12678 | 0.001374 | 0.12574 | 0.19826 | 0.10566 | 0.008102 | 0.016185 | 0.023218 | 121.2617 | 121.3917 | 0.10955 | -121.136 | 0.089471 | -121.1561
566.0625 | 121.9391 | -121.6187 | 0.14648 | 0.12185 | -0.00389 | 0.084151 | 0.020768 | 0.12325 | 0.1039 | -0.021514 | 0.093694 | 0.18453 | 0.073611 | -0.033101 | -0.020437 | 0.004908 | 121.2297 | 121.3688 | 0.14932 | 0.023576 | 0.11162 | 0.048234 | 0.15071 | 0.13136 | 0.005952 | 0.12116 | 0.212 | 0.10108 | -0.005635 | 0.007029 | 0.032374 | 121.2572 | 121.3962 | 0.11413 | -121.136 | 0.094048 | -121.1561
567.8125 | 121.9528 | -121.5958 | 0.15564 | 0.12643 | -0.00389 | 0.084151 | 0.01619 | 0.12782 | 0.10848 | -0.026092 | 0.10285 | 0.17537 | 0.07819 | 0.00811 | -0.015859 | 0.004908 | 121.2389 | 121.3734 | 0.1539 | 0.023576 | 0.11162 | 0.043656 | 0.15529 | 0.13594 | 0.001374 | 0.13032 | 0.20284 | 0.10566 | 0.035576 | 0.011607 | 0.032374 | 121.2663 | 121.4008 | 0.11871 | -121.136 | 0.094049 | -121.1607
569.4844 | 121.8475 | -121.6873 | 0.16937 | 0.12185 | -0.00389 | 0.084151 | 0.020768 | 0.12325 | 0.099318 | -0.016936 | 0.098273 | 0.17995 | 0.082768 | -0.078891 | -0.015859 | 0.00033 | 121.2434 | 121.3871 | 0.14932 | 0.023576 | 0.11162 | 0.048234 | 0.15071 | 0.12678 | 0.01053 | 0.12574 | 0.20742 | 0.11023 | -0.051425 | 0.011607 | 0.027796 | 121.2709 | 121.4146 | 0.11413 | -121.1452 | 0.098627 | -121.1607
571.2188 | 121.8979 | -121.6507 | 0.16937 | 0.12185 | -0.008469 | 0.084151 | 0.01619 | 0.12325 | 0.099318 | -0.021514 | 0.098273 | 0.17537 | 0.073611 | -0.069733 | -0.015859 | 0.00033 | 121.2434 | 121.3825 | 0.14932 | 0.018997 | 0.11162 | 0.043656 | 0.15071 | 0.12678 | 0.005952 | 0.12574 | 0.20284 | 0.10108 | -0.042267 | 0.011607 | 0.027796 | 121.2709 | 121.41 | 0.11413 | -121.1452 | 0.08947 | -121.1698
572.9844 | 121.9666 | -121.6232 | 0.14191 | 0.13101 | -0.00389 | 0.084151 | 0.011611 | 0.12325 | 0.099318 | -0.021514 | 0.10285 | 0.17995 | 0.07819 | -0.069733 | -0.011281 | 0.004908 | 121.2343 | 121.3734 | 0.15847 | 0.023576 | 0.11162 | 0.039077 | 0.15071 | 0.12678 | 0.005952 | 0.13032 | 0.20742 | 0.10566 | -0.042267 | 0.016185 | 0.032374 | 121.2617 | 121.4008 | 0.11413 | -121.1314 | 0.089471 | -121.1561
574.6562 | 121.9849 | -121.6141 | 0.15106 | 0.12185 | -0.00389 | 0.074994 | 0.01619 | 0.11867 | 0.099318 | -0.016936 | 0.098273 | 0.17537 | 0.07819 | -0.08347 | -0.011281 | 0.00033 | 121.2389 | 121.3688 | 0.14932 | 0.023576 | 0.10246 | 0.043656 | 0.14613 | 0.12678 | 0.01053 | 0.12574 | 0.20284 | 0.10566 | -0.056004 | 0.016185 | 0.027796 | 121.2663 | 121.3962 | 0.10955 | -121.1406 | 0.089471 | -121.1607
576.3906 | 121.9208 | -121.6507 | 0.16937 | 0.12643 | 0.005267 | 0.079572 | 0.01619 | 0.11867 | 0.10848 | -0.026092 | 0.10285 | 0.17537 | 0.07819 | -0.03768 | -0.011281 | 0.00033 | 121.248 | 121.3779 | 0.1539 | 0.032733 | 0.10704 | 0.043656 | 0.14613 | 0.13594 | 0.001374 | 0.13032 | 0.20284 | 0.10566 | -0.010214 | 0.016185 | 0.027796 | 121.2755 | 121.4054 | 0.11413 | -121.1452 | 0.089471 | -121.1698
578.125 | 122.0032 | -121.6141 | 0.16479 | 0.12643 | -0.008469 | 0.084151 | 0.020768 | 0.12325 | 0.09474 | -0.021514 | 0.10743 | 0.17995 | 0.07819 | -0.023943 | -0.015859 | 0.00033 | 121.2434 | 121.3779 | 0.1539 | 0.018997 | 0.11162 | 0.048234 | 0.15071 | 0.12221 | 0.005952 | 0.1349 | 0.20742 | 0.10566 | 0.003523 | 0.011607 | 0.027796 | 121.2709 | 121.4054 | 0.12329 | -121.136 | 0.094049 | -121.1652
579.8594 | 121.994 | -121.6324 | 0.14191 | 0.11727 | -0.008469 | 0.084151 | 0.011611 | 0.11867 | 0.1039 | -0.03067 | 0.098273 | 0.18911 | 0.082768 | -0.03768 | -0.015859 | 0.004908 | 121.2434 | 121.3779 | 0.14474 | 0.018997 | 0.11162 | 0.039077 | 0.14613 | 0.13136 | -0.003204 | 0.12574 | 0.21657 | 0.11023 | -0.010214 | 0.011607 | 0.032374 | 121.2709 | 121.4054 | 0.11413 | -121.1452 | 0.098627 | -121.1607
581.5938 | 121.9574 | -121.6187 | 0.16022 | 0.12643 | -0.008469 | 0.084151 | 0.01619 | 0.12325 | 0.09474 | -0.021514 | 0.098273 | 0.17995 | 0.073611 | 0.00811 | -0.025015 | 0.00033 | 121.2434 | 121.3779 | 0.1539 | 0.018997 | 0.11162 | 0.043656 | 0.15071 | 0.12221 | 0.005952 | 0.12574 | 0.20742 | 0.10108 | 0.035576 | 0.002451 | 0.027796 | 121.2709 | 121.4054 | 0.12329 | -121.1452 | 0.098626 | -121.1698
583.2812 | 121.9849 | -121.6049 | 0.14191 | 0.11727 | -0.00389 | 0.079572 | 0.01619 | 0.12325 | 0.099318 | -0.026092 | 0.10743 | 0.17537 | 0.082768 | -0.051417 | -0.015859 | 0.00033 | 121.248 | 121.3871 | 0.14474 | 0.023576 | 0.10704 | 0.043656 | 0.15071 | 0.12678 | 0.001374 | 0.1349 | 0.20284 | 0.11023 | -0.023951 | 0.011607 | 0.027796 | 121.2755 | 121.4146 | 0.12329 | -121.1406 | 0.098627 | -121.1652
585.0312 | 121.9208 | -121.6599 | 0.17395 | 0.12643 | -0.00389 | 0.093308 | 0.020768 | 0.12325 | 0.1039 | -0.021514 | 0.10743 | 0.17537 | 0.082768 | -0.03768 | -0.025015 | -0.004248 | 121.2526 | 121.3779 | 0.1539 | 0.023576 | 0.12077 | 0.048234 | 0.15071 | 0.13136 | 0.005952 | 0.1349 | 0.20284 | 0.11023 | -0.010214 | 0.002451 | 0.023218 | 121.2801 | 121.4054 | 0.13245 | -121.1452 | 0.10778 | -121.1698
586.7031 | 121.9116 | -121.6644 | 0.17853 | 0.12185 | -0.00389 | 0.084151 | 0.01619 | 0.12325 | 0.1039 | -0.021514 | 0.10285 | 0.17995 | 0.07819 | -0.001048 | -0.015859 | -0.004248 | 121.2526 | 121.3917 | 0.14932 | 0.023576 | 0.11162 | 0.043656 | 0.15071 | 0.13136 | 0.005952 | 0.13032 | 0.20742 | 0.10566 | 0.026418 | 0.011607 | 0.023218 | 121.2801 | 121.4191 | 0.11871 | -121.1497 | 0.094049 | -121.1744
588.4375 | 121.9162 | -121.6461 | 0.17853 | 0.12643 | -0.008469 | 0.08873 | 0.01619 | 0.12782 | 0.1039 | -0.021514 | 0.10285 | 0.17995 | 0.082768 | -0.033101 | -0.015859 | 0.00033 | 121.2572 | 121.3825 | 0.1539 | 0.018997 | 0.1162 | 0.043656 | 0.15529 | 0.13136 | 0.005952 | 0.13032 | 0.20742 | 0.11023 | -0.005635 | 0.011607 | 0.027796 | 121.2846 | 121.41 | 0.11871 | -121.1543 | 0.098627 | -121.1744
590.1719 | 121.9757 | -121.6232 | 0.16022 | 0.13101 | -0.017627 | 0.079572 | 0.01619 | 0.11867 | 0.099318 | -0.021514 | 0.10743 | 0.18453 | 0.07819 | -0.033101 | -0.006702 | -0.004248 | 121.2434 | 121.3917 | 0.15847 | 0.009839 | 0.10704 | 0.043656 | 0.14613 | 0.12678 | 0.005952 | 0.1349 | 0.212 | 0.10566 | -0.005635 | 0.020764 | 0.023218 | 121.2709 | 121.4191 | 0.11413 | -121.136 | 0.084892 | -121.1652
591.9219 | 121.8796 | -121.6736 | 0.19684 | 0.12185 | -0.008469 | 0.084151 | 0.011611 | 0.12325 | 0.1039 | -0.021514 | 0.11201 | 0.18453 | 0.087346 | -0.023943 | -0.011281 | 0.00033 | 121.2434 | 121.3962 | 0.14932 | 0.018997 | 0.11162 | 0.039077 | 0.15071 | 0.13136 | 0.005952 | 0.13947 | 0.212 | 0.11481 | 0.003523 | 0.016185 | 0.027796 | 121.2709 | 121.4237 | 0.12329 | -121.1314 | 0.098627 | -121.1561
593.6094 | 121.875 | -121.6782 | 0.17853 | 0.12185 | -0.00389 | 0.084151 | 0.01619 | 0.12325 | 0.1039 | -0.026092 | 0.07538 | 0.17995 | 0.073611 | -0.028522 | -0.020437 | 0.004908 | 121.2526 | 121.3825 | 0.14932 | 0.023576 | 0.11162 | 0.043656 | 0.15071 | 0.13136 | 0.001374 | 0.10285 | 0.20742 | 0.10108 | -0.001056 | 0.007029 | 0.032374 | 121.2801 | 121.41 | 0.095817 | -121.1772 | 0.094048 | -121.179
595.3438 | 121.8704 | -121.6782 | 0.18768 | 0.12643 | -0.00389 | 0.08873 | 0.01619 | 0.12782 | 0.1039 | -0.026092 | 0.084537 | 0.18911 | 0.073611 | -0.010206 | -0.015859 | 0.004908 | 121.248 | 121.3825 | 0.1539 | 0.023576 | 0.1162 | 0.043656 | 0.15529 | 0.13136 | 0.001374 | 0.112 | 0.21657 | 0.10108 | 0.01726 | 0.011607 | 0.032374 | 121.2755 | 121.41 | 0.1004 | -121.1635 | 0.08947 | -121.1744
597.0938 | 121.9299 | -121.6461 | 0.1831 | 0.12185 | -0.008469 | 0.08873 | 0.025347 | 0.12325 | 0.1039 | -0.021514 | 0.084537 | 0.18453 | 0.082768 | -0.042259 | -0.015859 | 0.004908 | 121.248 | 121.3871 | 0.14932 | 0.018997 | 0.1162 | 0.052813 | 0.15071 | 0.13136 | 0.005952 | 0.112 | 0.212 | 0.11023 | -0.014793 | 0.011607 | 0.032374 | 121.2755 | 121.4146 | 0.1004 | -121.1635 | 0.098627 | -121.1652
598.7812 | 121.8887 | -121.6461 | 0.1831 | 0.12185 | -0.017627 | 0.08873 | 0.01619 | 0.11867 | 0.099318 | -0.021514 | 0.079959 | 0.17995 | 0.082768 | -0.019364 | -0.015859 | 0.004908 | 121.248 | 121.3871 | 0.14932 | 0.009839 | 0.1162 | 0.043656 | 0.14613 | 0.12678 | 0.005952 | 0.10743 | 0.20742 | 0.11023 | 0.008102 | 0.011607 | 0.032374 | 121.2755 | 121.4146 | 0.095818 | -121.1681 | 0.098627 | -121.1652
600.5156 | 121.9254 | -121.6873 | 0.17853 | 0.12185 | -0.008469 | 0.084151 | 0.025347 | 0.12325 | 0.1039 | -0.021514 | 0.079959 | 0.19369 | 0.082768 | 0.00811 | -0.011281 | 0.004908 | 121.2526 | 121.3962 | 0.14932 | 0.018997 | 0.11162 | 0.052813 | 0.15071 | 0.13136 | 0.005952 | 0.10743 | 0.22115 | 0.11023 | 0.035576 | 0.016185 | 0.032374 | 121.2801 | 121.4237 | 0.09124 | -121.1726 | 0.094049 | -121.1698
602.25 | 121.962 | -121.6278 | 0.15106 | 0.12185 | -0.013048 | 0.084151 | 0.011611 | 0.12325 | 0.099318 | -0.016936 | 0.079959 | 0.17995 | 0.07819 | -0.010206 | -0.011281 | 0.004908 | 121.2526 | 121.3917 | 0.14932 | 0.014418 | 0.11162 | 0.039077 | 0.15071 | 0.12678 | 0.01053 | 0.10743 | 0.20742 | 0.10566 | 0.01726 | 0.016185 | 0.032374 | 121.2801 | 121.4191 | 0.09124 | -121.1726 | 0.089471 | -121.1744
604 | 121.875 | -121.669 | 0.20142 | 0.12643 | -0.00389 | 0.08873 | 0.011611 | 0.11867 | 0.1039 | -0.012357 | 0.084537 | 0.18453 | 0.091925 | -0.088049 | -0.011281 | 0.004908 | 121.2617 | 121.3962 | 0.1539 | 0.023576 | 0.1162 | 0.039077 | 0.14613 | 0.13136 | 0.015109 | 0.112 | 0.212 | 0.11939 | -0.060583 | 0.016185 | 0.032374 | 121.2892 | 121.4237 | 0.095818 | -121.1772 | 0.10321 | -121.1698
605.6875 | 122.0169 | -121.6278 | 0.15106 | 0.12185 | -0.00389 | 0.093308 | 0.020768 | 0.12325 | 0.1039 | -0.016936 | 0.084537 | 0.17995 | 0.082768 | -0.042259 | -0.020437 | 0.004908 | 121.2526 | 121.4008 | 0.14932 | 0.023576 | 0.12077 | 0.048234 | 0.15071 | 0.13136 | 0.01053 | 0.112 | 0.20742 | 0.11023 | -0.014793 | 0.007029 | 0.032374 | 121.2801 | 121.4283 | 0.10497 | -121.1681 | 0.1032 | -121.1698
607.4219 | 122.0123 | -121.6187 | 0.14191 | 0.12185 | 0.000689 | 0.08873 | 0.020768 | 0.11867 | 0.09474 | -0.026092 | 0.079959 | 0.18453 | 0.087346 | 0.031006 | -0.011281 | -0.004248 | 121.2572 | 121.3871 | 0.14932 | 0.028155 | 0.1162 | 0.048234 | 0.14613 | 0.12221 | 0.001374 | 0.10743 | 0.212 | 0.11481 | 0.058472 | 0.016185 | 0.023218 | 121.2846 | 121.4146 | 0.09124 | -121.1772 | 0.098627 | -121.1698
609.1094 | 122.0078 | -121.6232 | 0.15106 | 0.12643 | -0.013048 | 0.08873 | 0.01619 | 0.12325 | 0.1039 | -0.012357 | 0.079959 | 0.18911 | 0.07819 | -0.014785 | -0.011281 | 0.00033 | 121.2572 | 121.3917 | 0.1539 | 0.014418 | 0.1162 | 0.043656 | 0.15071 | 0.13136 | 0.015109 | 0.10743 | 0.21657 | 0.10566 | 0.012681 | 0.016185 | 0.027796 | 121.2846 | 121.4191 | 0.09124 | -121.1772 | 0.089471 | -121.179
610.8438 | 121.9757 | -121.6461 | 0.15564 | 0.12643 | -0.008469 | 0.093308 | 0.01619 | 0.12325 | 0.099318 | -0.035248 | 0.079959 | 0.17995 | 0.082768 | -0.019364 | -0.011281 | 0.00033 | 121.2572 | 121.3917 | 0.1539 | 0.018997 | 0.12077 | 0.043656 | 0.15071 | 0.12678 | -0.007782 | 0.10743 | 0.20742 | 0.11023 | 0.008102 | 0.016185 | 0.027796 | 121.2846 | 121.4191 | 0.09124 | -121.1772 | 0.094049 | -121.1744
612.5781 | 121.9574 | -121.6415 | 0.16937 | 0.12185 | -0.00389 | 0.08873 | 0.011611 | 0.12325 | 0.1039 | -0.016936 | 0.084537 | 0.18453 | 0.087346 | -0.019364 | -0.015859 | 0.00033 | 121.2663 | 121.3962 | 0.14932 | 0.023576 | 0.1162 | 0.039077 | 0.15071 | 0.13136 | 0.01053 | 0.112 | 0.212 | 0.11481 | 0.008102 | 0.011607 | 0.027796 | 121.2938 | 121.4237 | 0.1004 | -121.1818 | 0.1032 | -121.179
614.25 | 121.8842 | -121.669 | 0.18768 | 0.13101 | -0.013048 | 0.08873 | 0.020768 | 0.1324 | 0.10848 | -0.016936 | 0.079959 | 0.18453 | 0.087346 | 0.021847 | -0.011281 | -0.004248 | 121.2572 | 121.3871 | 0.15847 | 0.014418 | 0.1162 | 0.048234 | 0.15987 | 0.13594 | 0.01053 | 0.10743 | 0.212 | 0.11481 | 0.049313 | 0.016185 | 0.023218 | 121.2846 | 121.4146 | 0.09124 | -121.1772 | 0.098627 | -121.1698
615.9844 | 121.8979 | -121.6553 | 0.1831 | 0.13101 | -0.013048 | 0.08873 | 0.011611 | 0.12782 | 0.099318 | -0.016936 | 0.079959 | 0.18453 | 0.082768 | 0.026427 | -0.015859 | -0.004248 | 121.2526 | 121.4008 | 0.15847 | 0.014418 | 0.1162 | 0.039077 | 0.15529 | 0.12678 | 0.01053 | 0.10743 | 0.212 | 0.11023 | 0.053893 | 0.011607 | 0.023218 | 121.2801 | 121.4283 | 0.095818 | -121.1726 | 0.098627 | -121.1698
617.7344 | 121.8933 | -121.701 | 0.18768 | 0.12643 | -0.00389 | 0.093308 | 0.020768 | 0.12325 | 0.099318 | -0.016936 | 0.089116 | 0.18911 | 0.091925 | 0.021847 | -0.006702 | -0.004248 | 121.2572 | 121.4008 | 0.1539 | 0.023576 | 0.12077 | 0.048234 | 0.15071 | 0.12678 | 0.01053 | 0.11658 | 0.21657 | 0.11939 | 0.049313 | 0.020764 | 0.023218 | 121.2846 | 121.4283 | 0.095818 | -121.1681 | 0.098627 | -121.1652
619.4844 | 122.0032 | -121.6141 | 0.14648 | 0.12643 | -0.008469 | 0.08873 | 0.025347 | 0.12782 | 0.1039 | -0.016936 | 0.084537 | 0.17995 | 0.07819 | -0.001048 | -0.025015 | -0.004248 | 121.2617 | 121.4008 | 0.1539 | 0.018997 | 0.1162 | 0.052813 | 0.15529 | 0.13136 | 0.01053 | 0.112 | 0.20742 | 0.10566 | 0.026418 | 0.002451 | 0.023218 | 121.2892 | 121.4283 | 0.10955 | -121.1772 | 0.1032 | -121.1836
621.1562 | 122.0123 | -121.6049 | 0.13733 | 0.12643 | -0.008469 | 0.08873 | 0.020768 | 0.1324 | 0.09474 | -0.021514 | 0.079959 | 0.19827 | 0.082768 | -0.014785 | -0.015859 | -0.004248 | 121.2617 | 121.3917 | 0.1539 | 0.018997 | 0.1162 | 0.048234 | 0.15987 | 0.12221 | 0.005952 | 0.10743 | 0.22573 | 0.11023 | 0.012681 | 0.011607 | 0.023218 | 121.2892 | 121.4191 | 0.095818 | -121.1818 | 0.098627 | -121.179
622.9062 | 121.9711 | -121.6507 | 0.16479 | 0.13101 | 0.000689 | 0.08873 | 0.025347 | 0.12782 | 0.099318 | -0.021514 | 0.084537 | 0.18453 | 0.087346 | -0.010206 | -0.006702 | 0.004908 | 121.2709 | 121.4054 | 0.15847 | 0.028155 | 0.1162 | 0.052813 | 0.15529 | 0.12678 | 0.005952 | 0.112 | 0.212 | 0.11481 | 0.01726 | 0.020764 | 0.032374 | 121.2984 | 121.4329 | 0.091239 | -121.1864 | 0.094048 | -121.1836
624.5781 | 121.962 | -121.6644 | 0.16022 | 0.13101 | -0.008469 | 0.08873 | 0.020768 | 0.12782 | 0.1039 | -0.021514 | 0.079959 | 0.18911 | 0.082768 | 0.021847 | -0.020437 | 0.009486 | 121.2572 | 121.4054 | 0.15847 | 0.018997 | 0.1162 | 0.048234 | 0.15529 | 0.13136 | 0.005952 | 0.10743 | 0.21657 | 0.11023 | 0.049313 | 0.007029 | 0.036952 | 121.2846 | 121.4329 | 0.1004 | -121.1772 | 0.1032 | -121.1744
626.3125 | 121.9391 | -121.6461 | 0.17853 | 0.12643 | 0.000689 | 0.084151 | 0.025347 | 0.12325 | 0.10848 | -0.016936 | 0.079959 | 0.18911 | 0.082768 | -0.046838 | -0.015859 | -0.004248 | 121.2709 | 121.4008 | 0.1539 | 0.028155 | 0.11162 | 0.052813 | 0.15071 | 0.13594 | 0.01053 | 0.10743 | 0.21657 | 0.11023 | -0.019372 | 0.011607 | 0.023218 | 121.2984 | 121.4283 | 0.095818 | -121.1909 | 0.098627 | -121.1881
628 | 122.0123 | -121.6232 | 0.15564 | 0.13101 | -0.008469 | 0.084151 | 0.020768 | 0.12325 | 0.1039 | -0.016936 | 0.079959 | 0.18453 | 0.082768 | -0.028522 | -0.011281 | 0.00033 | 121.2709 | 121.3962 | 0.15847 | 0.018997 | 0.11162 | 0.048234 | 0.15071 | 0.13136 | 0.01053 | 0.10743 | 0.212 | 0.11023 | -0.001056 | 0.016185 | 0.027796 | 121.2984 | 121.4237 | 0.09124 | -121.1909 | 0.094049 | -121.1881
629.7344 | 122.0078 | -121.6278 | 0.15106 | 0.13101 | -0.008469 | 0.08873 | 0.020768 | 0.12325 | 0.1039 | -0.016936 | 0.079959 | 0.19369 | 0.087346 | -0.033101 | -0.020437 | 0.004908 | 121.2663 | 121.4008 | 0.15847 | 0.018997 | 0.1162 | 0.048234 | 0.15071 | 0.13136 | 0.01053 | 0.10743 | 0.22115 | 0.11481 | -0.005635 | 0.007029 | 0.032374 | 121.2938 | 121.4283 | 0.1004 | -121.1864 | 0.10778 | -121.179
631.4062 | 122.0032 | -121.6278 | 0.14648 | 0.12185 | 0.000689 | 0.093308 | 0.01619 | 0.12782 | 0.10848 | -0.021514 | 0.089116 | 0.18911 | 0.082768 | -0.028522 | -0.011281 | 0.00033 | 121.2617 | 121.4054 | 0.14932 | 0.028155 | 0.12077 | 0.043656 | 0.15529 | 0.13594 | 0.005952 | 0.11658 | 0.21657 | 0.11023 | -0.001056 | 0.016185 | 0.027796 | 121.2892 | 121.4329 | 0.1004 | -121.1726 | 0.094049 | -121.179
633.0938 | 122.0215 | -121.637 | 0.16022 | 0.13101 | -0.00389 | 0.093308 | 0.025347 | 0.12782 | 0.1039 | -0.026092 | 0.07538 | 0.18911 | 0.082768 | -0.014785 | -0.020437 | -0.004248 | 121.2617 | 121.4008 | 0.15847 | 0.023576 | 0.12077 | 0.052813 | 0.15529 | 0.13136 | 0.001374 | 0.10285 | 0.21657 | 0.11023 | 0.012681 | 0.007029 | 0.023218 | 121.2892 | 121.4283 | 0.095817 | -121.1864 | 0.1032 | -121.179
634.8438 | 121.9528 | -121.6507 | 0.16022 | 0.13101 | -0.00389 | 0.08873 | 0.020768 | 0.12325 | 0.11305 | -0.012357 | 0.084537 | 0.18453 | 0.087346 | -0.03768 | -0.011281 | -0.004248 | 121.2663 | 121.3962 | 0.15847 | 0.023576 | 0.1162 | 0.048234 | 0.15071 | 0.14052 | 0.015109 | 0.112 | 0.212 | 0.11481 | -0.010214 | 0.016185 | 0.023218 | 121.2938 | 121.4237 | 0.095818 | -121.1818 | 0.098627 | -121.179
636.5156 | 121.9528 | -121.6736 | 0.16937 | 0.13101 | 0.000689 | 0.08873 | 0.020768 | 0.12325 | 0.1039 | -0.016936 | 0.07538 | 0.19369 | 0.087346 | -0.033101 | -0.011281 | -0.008827 | 121.2709 | 121.4008 | 0.15847 | 0.028155 | 0.1162 | 0.048234 | 0.15071 | 0.13136 | 0.01053 | 0.10285 | 0.22115 | 0.11481 | -0.005635 | 0.016185 | 0.018639 | 121.2984 | 121.4283 | 0.086661 | -121.1955 | 0.098627 | -121.1836
638.2656 | 122.0352 | -121.6415 | 0.13275 | 0.12643 | -0.00389 | 0.093308 | 0.025347 | 0.12325 | 0.10848 | -0.016936 | 0.079959 | 0.19827 | 0.082768 | -0.001048 | -0.020437 | -0.008827 | 121.2663 | 121.41 | 0.1539 | 0.023576 | 0.12077 | 0.052813 | 0.15071 | 0.13594 | 0.01053 | 0.10743 | 0.22573 | 0.11023 | 0.026418 | 0.007029 | 0.018639 | 121.2938 | 121.4374 | 0.1004 | -121.1864 | 0.1032 | -121.1836
640 | 121.8887 | -121.7285 | 0.19684 | 0.13101 | -0.00389 | 0.093308 | 0.025347 | 0.12325 | 0.10848 | -0.016936 | 0.079959 | 0.17995 | 0.082768 | -0.03768 | -0.011281 | 0.00033 | 121.2846 | 121.4146 | 0.15847 | 0.023576 | 0.12077 | 0.052813 | 0.15071 | 0.13594 | 0.01053 | 0.10743 | 0.20742 | 0.11023 | -0.010214 | 0.016185 | 0.027796 | 121.3121 | 121.442 | 0.09124 | -121.2047 | 0.094049 | -121.2019
641.6562 | 122.0169 | -121.6599 | 0.12817 | 0.12643 | 0.000689 | 0.08873 | 0.029925 | 0.12782 | 0.1039 | -0.016936 | 0.084537 | 0.18911 | 0.07819 | -0.010206 | -0.015859 | -0.008827 | 121.2846 | 121.4191 | 0.1539 | 0.028155 | 0.1162 | 0.057391 | 0.15529 | 0.13136 | 0.01053 | 0.112 | 0.21657 | 0.10566 | 0.01726 | 0.011607 | 0.018639 | 121.3121 | 121.4466 | 0.1004 | -121.2001 | 0.094049 | -121.2064
643.4062 | 122.0215 | -121.6736 | 0.14191 | 0.13101 | -0.00389 | 0.08873 | 0.020768 | 0.1324 | 0.10848 | -0.016936 | 0.07538 | 0.17995 | 0.07819 | -0.088049 | -0.011281 | -0.008827 | 121.2938 | 121.4283 | 0.15847 | 0.023576 | 0.1162 | 0.048234 | 0.15987 | 0.13594 | 0.01053 | 0.10285 | 0.20742 | 0.10566 | -0.060583 | 0.016185 | 0.018639 | 121.3213 | 121.4558 | 0.086661 | -121.2184 | 0.089471 | -121.2156
645.0781 | 122.0261 | -121.6599 | 0.15106 | 0.13101 | -0.00389 | 0.084151 | 0.020768 | 0.11867 | 0.10848 | -0.026092 | 0.070802 | 0.17995 | 0.07819 | -0.10179 | -0.020437 | -0.013405 | 121.2755 | 121.4283 | 0.15847 | 0.023576 | 0.11162 | 0.048234 | 0.14613 | 0.13594 | 0.001374 | 0.098268 | 0.20742 | 0.10566 | -0.07432 | 0.007029 | 0.014061 | 121.3029 | 121.4558 | 0.091239 | -121.2047 | 0.098627 | -121.1973
646.8125 | 122.0215 | -121.6873 | 0.13733 | 0.12643 | -0.013048 | 0.08873 | 0.020768 | 0.12782 | 0.1039 | -0.026092 | 0.07538 | 0.17079 | 0.073611 | -0.055996 | -0.015859 | -0.004248 | 121.2892 | 121.4329 | 0.1539 | 0.014418 | 0.1162 | 0.048234 | 0.15529 | 0.13136 | 0.001374 | 0.10285 | 0.19826 | 0.10108 | -0.02853 | 0.011607 | 0.023218 | 121.3167 | 121.4603 | 0.091239 | -121.2138 | 0.08947 | -121.2156
648.5469 | 121.9025 | -121.7239 | 0.16022 | 0.12185 | -0.008469 | 0.08873 | 0.01619 | 0.11867 | 0.10848 | -0.016936 | 0.052488 | 0.1479 | 0.064455 | -0.10179 | -0.011281 | 0.004908 | 121.3121 | 121.4466 | 0.14932 | 0.018997 | 0.1162 | 0.043656 | 0.14613 | 0.13594 | 0.01053 | 0.079954 | 0.17536 | 0.091921 | -0.07432 | 0.016185 | 0.032374 | 121.3396 | 121.4741 | 0.063769 | -121.2596 | 0.075736 | -121.2477
650.2188 | 121.9803 | -121.7056 | 0.13275 | 0.12185 | -0.00389 | 0.079572 | 0.020768 | 0.12325 | 0.099318 | -0.021514 | 0.052488 | 0.15248 | 0.059877 | -0.10637 | -0.006702 | 0.00033 | 121.3213 | 121.4558 | 0.14932 | 0.023576 | 0.10704 | 0.048234 | 0.15071 | 0.12678 | 0.005952 | 0.079954 | 0.17994 | 0.087343 | -0.078899 | 0.020764 | 0.027796 | 121.3487 | 121.4832 | 0.05919 | -121.2688 | 0.066579 | -121.2614
651.9688 | 122.0078 | -121.6873 | 0.10071 | 0.12643 | -0.00389 | 0.084151 | 0.007033 | 0.11867 | 0.10848 | -0.016936 | 0.052488 | 0.15248 | 0.046142 | -0.11094 | -0.015859 | 0.009486 | 121.3121 | 121.4466 | 0.1539 | 0.023576 | 0.11162 | 0.034499 | 0.14613 | 0.13594 | 0.01053 | 0.079954 | 0.17994 | 0.073608 | -0.083478 | 0.011607 | 0.036952 | 121.3396 | 121.4741 | 0.068347 | -121.2596 | 0.062001 | -121.266
653.7188 | 121.9986 | -121.7102 | 0.14191 | 0.12643 | -0.008469 | 0.074994 | 0.011611 | 0.11867 | 0.090161 | -0.026092 | 0.057066 | 0.15248 | 0.046142 | -0.10637 | -0.015859 | 0.004908 | 121.3121 | 121.4466 | 0.1539 | 0.018997 | 0.10246 | 0.039077 | 0.14613 | 0.11763 | 0.001374 | 0.084532 | 0.17994 | 0.073608 | -0.078899 | 0.011607 | 0.032374 | 121.3396 | 121.4741 | 0.072925 | -121.255 | 0.062001 | -121.266
655.4062 | 122.0078 | -121.6873 | 0.13275 | 0.12643 | -0.008469 | 0.08873 | 0.01619 | 0.11867 | 0.09474 | -0.021514 | 0.057066 | 0.1479 | 0.055298 | -0.10179 | -0.020437 | 0.00033 | 121.3121 | 121.4512 | 0.1539 | 0.018997 | 0.1162 | 0.043656 | 0.14613 | 0.12221 | 0.005952 | 0.084532 | 0.17536 | 0.082764 | -0.07432 | 0.007029 | 0.027796 | 121.3396 | 121.4787 | 0.077503 | -121.255 | 0.075735 | -121.2568
657.1406 | 121.9986 | -121.6919 | 0.1236 | 0.12643 | -0.00389 | 0.084151 | 0.011611 | 0.12325 | 0.099318 | -0.016936 | 0.057066 | 0.15706 | 0.059877 | -0.10179 | -0.020437 | 0.004908 | 121.3075 | 121.442 | 0.1539 | 0.023576 | 0.11162 | 0.039077 | 0.15071 | 0.12678 | 0.01053 | 0.084532 | 0.18452 | 0.087343 | -0.07432 | 0.007029 | 0.032374 | 121.335 | 121.4695 | 0.077503 | -121.2505 | 0.080314 | -121.2477
658.8906 | 121.9894 | -121.6965 | 0.13733 | 0.12643 | -0.008469 | 0.08873 | 0.01619 | 0.12325 | 0.099318 | -0.026092 | 0.052488 | 0.15706 | 0.055298 | -0.11094 | -0.002124 | 0.004908 | 121.3167 | 121.4512 | 0.1539 | 0.018997 | 0.1162 | 0.043656 | 0.15071 | 0.12678 | 0.001374 | 0.079954 | 0.18452 | 0.082764 | -0.083478 | 0.025342 | 0.032374 | 121.3442 | 121.4787 | 0.054612 | -121.2642 | 0.057422 | -121.2614
660.5625 | 121.9894 | -121.6919 | 0.13733 | 0.12643 | -0.00389 | 0.079572 | 0.011611 | 0.12325 | 0.1039 | -0.021514 | 0.052488 | 0.1479 | 0.059877 | -0.11094 | -0.011281 | -0.004248 | 121.3258 | 121.4558 | 0.1539 | 0.023576 | 0.10704 | 0.039077 | 0.15071 | 0.13136 | 0.005952 | 0.079954 | 0.17536 | 0.087343 | -0.083478 | 0.016185 | 0.023218 | 121.3533 | 121.4832 | 0.063769 | -121.2734 | 0.071158 | -121.266
662.2969 | 121.9894 | -121.7148 | 0.13275 | 0.12643 | -0.008469 | 0.084151 | 0.01619 | 0.12325 | 0.099318 | -0.021514 | 0.052488 | 0.1479 | 0.05072 | -0.10637 | -0.011281 | 0.004908 | 121.3213 | 121.4558 | 0.1539 | 0.018997 | 0.11162 | 0.043656 | 0.15071 | 0.12678 | 0.005952 | 0.079954 | 0.17536 | 0.078186 | -0.078899 | 0.016185 | 0.032374 | 121.3487 | 121.4832 | 0.063769 | -121.2688 | 0.062001 | -121.2705
664.0312 | 121.907 | -121.7514 | 0.15106 | 0.12185 | -0.013048 | 0.08873 | 0.020768 | 0.12782 | 0.099318 | -0.012357 | 0.052488 | 0.15248 | 0.055298 | -0.10637 | -0.006702 | 0.004908 | 121.3213 | 121.4649 | 0.14932 | 0.014418 | 0.1162 | 0.048234 | 0.15529 | 0.12678 | 0.015109 | 0.079954 | 0.17994 | 0.082764 | -0.078899 | 0.020764 | 0.032374 | 121.3487 | 121.4924 | 0.05919 | -121.2688 | 0.062 | -121.266
665.7812 | 121.8933 | -121.7377 | 0.16022 | 0.12643 | -0.008469 | 0.08873 | 0.020768 | 0.11867 | 0.1039 | -0.021514 | 0.047909 | 0.15248 | 0.055298 | -0.11094 | -0.006702 | 0.00033 | 121.3258 | 121.4558 | 0.1539 | 0.018997 | 0.1162 | 0.048234 | 0.14613 | 0.13136 | 0.005952 | 0.075375 | 0.17994 | 0.082764 | -0.083478 | 0.020764 | 0.027796 | 121.3533 | 121.4832 | 0.054611 | -121.2779 | 0.062 | -121.2705
667.5156 | 121.8842 | -121.7239 | 0.15564 | 0.12643 | -0.008469 | 0.079572 | 0.025347 | 0.1324 | 0.099318 | -0.021514 | 0.043331 | 0.1479 | 0.05072 | -0.10179 | -0.011281 | 0.009486 | 121.3167 | 121.4558 | 0.1539 | 0.018997 | 0.10704 | 0.052813 | 0.15987 | 0.12678 | 0.005952 | 0.070797 | 0.17536 | 0.078186 | -0.07432 | 0.016185 | 0.036952 | 121.3442 | 121.4832 | 0.054612 | -121.2734 | 0.062001 | -121.266
669.1875 | 121.9849 | -121.6919 | 0.09613 | 0.13559 | -0.008469 | 0.084151 | 0.01619 | 0.12325 | 0.099318 | -0.012357 | 0.047909 | 0.15706 | 0.055298 | -0.10637 | -0.015859 | 0.00033 | 121.3075 | 121.4558 | 0.16305 | 0.018997 | 0.11162 | 0.043656 | 0.15071 | 0.12678 | 0.015109 | 0.075375 | 0.18452 | 0.082764 | -0.078899 | 0.011607 | 0.027796 | 121.335 | 121.4832 | 0.063768 | -121.2596 | 0.071157 | -121.2522
670.9375 | 121.8979 | -121.7422 | 0.15106 | 0.12643 | -0.00389 | 0.093308 | 0.025347 | 0.12782 | 0.09474 | -0.016936 | 0.052488 | 0.15248 | 0.055298 | -0.10637 | -0.015859 | 0.00033 | 121.3213 | 121.4558 | 0.1539 | 0.023576 | 0.12077 | 0.052813 | 0.15529 | 0.12221 | 0.01053 | 0.079954 | 0.17994 | 0.082764 | -0.078899 | 0.011607 | 0.027796 | 121.3487 | 121.4832 | 0.068347 | -121.2688 | 0.071157 | -121.266
672.6094 | 121.9345 | -121.7285 | 0.13733 | 0.12643 | -0.008469 | 0.08873 | 0.025347 | 0.11867 | 0.1039 | -0.007779 | 0.043331 | 0.15248 | 0.055298 | -0.10637 | -0.015859 | 0.009486 | 121.3213 | 121.4603 | 0.1539 | 0.018997 | 0.1162 | 0.052813 | 0.14613 | 0.13136 | 0.019687 | 0.070797 | 0.17994 | 0.082764 | -0.078899 | 0.011607 | 0.036952 | 121.3487 | 121.4878 | 0.05919 | -121.2779 | 0.071157 | -121.266
674.3594 | 121.9528 | -121.7239 | 0.12817 | 0.13559 | -0.008469 | 0.084151 | 0.01619 | 0.12782 | 0.1039 | -0.016936 | 0.057066 | 0.15706 | 0.05072 | -0.10179 | -0.011281 | 0.004908 | 121.3258 | 121.4649 | 0.16305 | 0.018997 | 0.11162 | 0.043656 | 0.15529 | 0.13136 | 0.01053 | 0.084532 | 0.18452 | 0.078186 | -0.07432 | 0.016185 | 0.032374 | 121.3533 | 121.4924 | 0.068347 | -121.2688 | 0.062001 | -121.2751
676.1094 | 121.9391 | -121.7194 | 0.15564 | 0.13559 | -0.008469 | 0.084151 | 0.011611 | 0.1324 | 0.09474 | -0.007779 | 0.047909 | 0.15248 | 0.05072 | -0.10179 | -0.011281 | 0.00033 | 121.3304 | 121.4649 | 0.16305 | 0.018997 | 0.11162 | 0.039077 | 0.15987 | 0.12221 | 0.019687 | 0.075375 | 0.17994 | 0.078186 | -0.07432 | 0.016185 | 0.027796 | 121.3579 | 121.4924 | 0.05919 | -121.2825 | 0.062001 | -121.2797
677.8594 | 121.994 | -121.7148 | 0.1236 | 0.12643 | -0.00389 | 0.084151 | 0.020768 | 0.12782 | 0.099318 | -0.021514 | 0.052488 | 0.15706 | 0.055298 | -0.10179 | -0.015859 | -0.004248 | 121.3213 | 121.4603 | 0.1539 | 0.023576 | 0.11162 | 0.048234 | 0.15529 | 0.12678 | 0.005952 | 0.079954 | 0.18452 | 0.082764 | -0.07432 | 0.011607 | 0.023218 | 121.3487 | 121.4878 | 0.068347 | -121.2688 | 0.071157 | -121.266
679.5938 | 121.9894 | -121.7194 | 0.12817 | 0.13101 | -0.00389 | 0.084151 | 0.01619 | 0.12782 | 0.099318 | -0.021514 | 0.052488 | 0.15706 | 0.05072 | -0.10637 | -0.011281 | 0.009486 | 121.3213 | 121.4649 | 0.15847 | 0.023576 | 0.11162 | 0.043656 | 0.15529 | 0.12678 | 0.005952 | 0.079954 | 0.18452 | 0.078186 | -0.078899 | 0.016185 | 0.036952 | 121.3487 | 121.4924 | 0.063769 | -121.2688 | 0.062001 | -121.2705
681.2656 | 122.0261 | -121.6736 | 0.12817 | 0.12185 | -0.008469 | 0.093308 | 0.01619 | 0.12325 | 0.099318 | -0.021514 | 0.043331 | 0.15248 | 0.055298 | -0.11094 | -0.011281 | 0.004908 | 121.3213 | 121.4649 | 0.14932 | 0.018997 | 0.12077 | 0.043656 | 0.15071 | 0.12678 | 0.005952 | 0.070797 | 0.17994 | 0.082764 | -0.083478 | 0.016185 | 0.032374 | 121.3487 | 121.4924 | 0.054612 | -121.2779 | 0.066579 | -121.266
683 | 121.9254 | -121.6965 | 0.16479 | 0.13101 | -0.00389 | 0.093308 | 0.025347 | 0.1324 | 0.09474 | -0.016936 | 0.061645 | 0.16622 | 0.059877 | -0.10179 | -0.015859 | 0.00033 | 121.3075 | 121.4512 | 0.15847 | 0.023576 | 0.12077 | 0.052813 | 0.15987 | 0.12221 | 0.01053 | 0.089111 | 0.19368 | 0.087343 | -0.07432 | 0.011607 | 0.027796 | 121.335 | 121.4787 | 0.077504 | -121.2459 | 0.075736 | -121.2477
684.75 | 121.9482 | -121.7285 | 0.13733 | 0.12185 | -0.008469 | 0.08873 | 0.025347 | 0.12782 | 0.1039 | -0.021514 | 0.047909 | 0.15706 | 0.055298 | -0.10179 | -0.011281 | 0.004908 | 121.3258 | 121.4649 | 0.14932 | 0.018997 | 0.1162 | 0.052813 | 0.15529 | 0.13136 | 0.005952 | 0.075375 | 0.18452 | 0.082764 | -0.07432 | 0.016185 | 0.032374 | 121.3533 | 121.4924 | 0.05919 | -121.2779 | 0.066579 | -121.2705
686.4219 | 122.0261 | -121.6965 | 0.11444 | 0.12643 | -0.00389 | 0.084151 | 0.01619 | 0.12782 | 0.099318 | -0.016936 | 0.047909 | 0.15248 | 0.055298 | -0.097207 | -0.015859 | 0.004908 | 121.3213 | 121.4649 | 0.1539 | 0.023576 | 0.11162 | 0.043656 | 0.15529 | 0.12678 | 0.01053 | 0.075375 | 0.17994 | 0.082764 | -0.069741 | 0.011607 | 0.032374 | 121.3487 | 121.4924 | 0.063768 | -121.2734 | 0.071157 | -121.266
688.1562 | 122.0123 | -121.7102 | 0.11444 | 0.12643 | -0.008469 | 0.084151 | 0.011611 | 0.12325 | 0.09474 | -0.012357 | 0.057066 | 0.15248 | 0.055298 | -0.10637 | -0.025015 | 0.00033 | 121.3213 | 121.4603 | 0.1539 | 0.018997 | 0.11162 | 0.039077 | 0.15071 | 0.12221 | 0.015109 | 0.084532 | 0.17994 | 0.082764 | -0.078899 | 0.002451 | 0.027796 | 121.3487 | 121.4878 | 0.082081 | -121.2642 | 0.080313 | -121.266
689.9062 | 122.0078 | -121.7285 | 0.11902 | 0.11727 | 0.000689 | 0.084151 | 0.011611 | 0.12782 | 0.1039 | -0.012357 | 0.052488 | 0.16164 | 0.055298 | -0.10637 | -0.006702 | 0.009486 | 121.3304 | 121.4741 | 0.14474 | 0.028155 | 0.11162 | 0.039077 | 0.15529 | 0.13136 | 0.015109 | 0.079954 | 0.1891 | 0.082764 | -0.078899 | 0.020764 | 0.036952 | 121.3579 | 121.5015 | 0.05919 | -121.2779 | 0.062 | -121.2751
691.5781 | 122.0261 | -121.6965 | 0.1236 | 0.12185 | 0.000689 | 0.084151 | 0.025347 | 0.12325 | 0.09474 | -0.021514 | 0.047909 | 0.15248 | 0.046142 | -0.11094 | -0.002124 | 0.00033 | 121.335 | 121.4741 | 0.14932 | 0.028155 | 0.11162 | 0.052813 | 0.15071 | 0.12221 | 0.005952 | 0.075375 | 0.17994 | 0.073608 | -0.083478 | 0.025342 | 0.027796 | 121.3625 | 121.5015 | 0.050033 | -121.2871 | 0.048266 | -121.2889
693.3281 | 121.9711 | -121.7331 | 0.14191 | 0.12185 | -0.008469 | 0.08873 | 0.020768 | 0.12782 | 0.1039 | -0.016936 | 0.061645 | 0.16622 | 0.064455 | -0.088049 | -0.025015 | 0.009486 | 121.3213 | 121.4603 | 0.14932 | 0.018997 | 0.1162 | 0.048234 | 0.15529 | 0.13136 | 0.01053 | 0.089111 | 0.19368 | 0.091921 | -0.060583 | 0.002451 | 0.036952 | 121.3487 | 121.4878 | 0.08666 | -121.2596 | 0.08947 | -121.2568
695.0156 | 121.9254 | -121.7514 | 0.17395 | 0.13559 | -0.00389 | 0.093308 | 0.01619 | 0.12325 | 0.1039 | -0.016936 | 0.066223 | 0.17079 | 0.059877 | -0.097207 | -0.015859 | 0.00033 | 121.3258 | 121.4466 | 0.16305 | 0.023576 | 0.12077 | 0.043656 | 0.15071 | 0.13136 | 0.01053 | 0.093689 | 0.19826 | 0.087343 | -0.069741 | 0.011607 | 0.027796 | 121.3533 | 121.4741 | 0.082082 | -121.2596 | 0.075736 | -121.266
696.75 | 121.9254 | -121.7514 | 0.15106 | 0.12643 | -0.008469 | 0.08873 | 0.01619 | 0.12325 | 0.1039 | -0.016936 | 0.052488 | 0.15706 | 0.05072 | -0.10637 | -0.011281 | 0.00033 | 121.3396 | 121.4787 | 0.1539 | 0.018997 | 0.1162 | 0.043656 | 0.15071 | 0.13136 | 0.01053 | 0.079954 | 0.18452 | 0.078186 | -0.078899 | 0.016185 | 0.027796 | 121.367 | 121.5061 | 0.063769 | -121.2871 | 0.062001 | -121.2889
698.5 | 121.9666 | -121.7239 | 0.13275 | 0.12185 | -0.008469 | 0.08873 | 0.01619 | 0.12782 | 0.09474 | -0.021514 | 0.047909 | 0.1479 | 0.05072 | -0.10179 | -0.011281 | 0.014064 | 121.335 | 121.4787 | 0.14932 | 0.018997 | 0.1162 | 0.043656 | 0.15529 | 0.12221 | 0.005952 | 0.075375 | 0.17536 | 0.078186 | -0.07432 | 0.016185 | 0.04153 | 121.3625 | 121.5061 | 0.05919 | -121.2871 | 0.062001 | -121.2843
700.2344 | 121.994 | -121.6827 | 0.13275 | 0.12185 | -0.008469 | 0.084151 | 0.01619 | 0.12782 | 0.1039 | -0.016936 | 0.057066 | 0.16164 | 0.073611 | -0.11094 | -0.015859 | 0.009486 | 121.3258 | 121.4649 | 0.14932 | 0.018997 | 0.11162 | 0.043656 | 0.15529 | 0.13136 | 0.01053 | 0.084532 | 0.1891 | 0.10108 | -0.083478 | 0.011607 | 0.036952 | 121.3533 | 121.4924 | 0.072925 | -121.2688 | 0.08947 | -121.2522
701.9219 | 121.9849 | -121.7148 | 0.15106 | 0.12185 | -0.00389 | 0.08873 | 0.01619 | 0.12325 | 0.099318 | -0.021514 | 0.061645 | 0.16622 | 0.059877 | -0.10179 | -0.011281 | 0.00033 | 121.3304 | 121.4741 | 0.14932 | 0.023576 | 0.1162 | 0.043656 | 0.15071 | 0.12678 | 0.005952 | 0.089111 | 0.19368 | 0.087343 | -0.07432 | 0.016185 | 0.027796 | 121.3579 | 121.5015 | 0.072926 | -121.2688 | 0.071158 | -121.2705
703.6719 | 121.9345 | -121.7285 | 0.16937 | 0.12643 | -0.00389 | 0.08873 | 0.01619 | 0.12782 | 0.10848 | -0.026092 | 0.057066 | 0.15248 | 0.05072 | -0.10179 | -0.011281 | 0.00033 | 121.335 | 121.4741 | 0.1539 | 0.023576 | 0.1162 | 0.043656 | 0.15529 | 0.13594 | 0.001374 | 0.084532 | 0.17994 | 0.078186 | -0.07432 | 0.016185 | 0.027796 | 121.3625 | 121.5015 | 0.068347 | -121.2779 | 0.062001 | -121.2843
705.4219 | 121.907 | -121.7422 | 0.17853 | 0.12643 | -0.00389 | 0.079572 | 0.020768 | 0.12782 | 0.09474 | -0.021514 | 0.052488 | 0.15706 | 0.05072 | -0.10179 | -0.015859 | 0.009486 | 121.3304 | 121.4695 | 0.1539 | 0.023576 | 0.10704 | 0.048234 | 0.15529 | 0.12221 | 0.005952 | 0.079954 | 0.18452 | 0.078186 | -0.07432 | 0.011607 | 0.036952 | 121.3579 | 121.497 | 0.068347 | -121.2779 | 0.066579 | -121.2797
707.1406 | 122.0352 | -121.7102 | 0.10071 | 0.12185 | -0.00389 | 0.08873 | 0.01619 | 0.12782 | 0.099318 | -0.026092 | 0.047909 | 0.16164 | 0.05072 | -0.11094 | -0.006702 | 0.004908 | 121.3396 | 121.4787 | 0.14932 | 0.023576 | 0.1162 | 0.043656 | 0.15529 | 0.12678 | 0.001374 | 0.075375 | 0.1891 | 0.078186 | -0.083478 | 0.020764 | 0.032374 | 121.367 | 121.5061 | 0.054611 | -121.2917 | 0.057422 | -121.2889
708.875 | 121.994 | -121.7102 | 0.13275 | 0.13101 | -0.00389 | 0.093308 | 0.01619 | 0.12782 | 0.099318 | -0.016936 | 0.057066 | 0.16622 | 0.055298 | -0.10179 | -0.015859 | 0.004908 | 121.3304 | 121.4695 | 0.15847 | 0.023576 | 0.12077 | 0.043656 | 0.15529 | 0.12678 | 0.01053 | 0.084532 | 0.19368 | 0.082764 | -0.07432 | 0.011607 | 0.032374 | 121.3579 | 121.497 | 0.072925 | -121.2734 | 0.071157 | -121.2751
710.5469 | 121.9116 | -121.7331 | 0.15564 | 0.12643 | -0.00389 | 0.084151 | 0.01619 | 0.12782 | 0.1039 | -0.016936 | 0.057066 | 0.16164 | 0.055298 | -0.10179 | -0.006702 | 0.004908 | 121.3213 | 121.4649 | 0.1539 | 0.023576 | 0.11162 | 0.043656 | 0.15529 | 0.13136 | 0.01053 | 0.084532 | 0.1891 | 0.082764 | -0.07432 | 0.020764 | 0.032374 | 121.3487 | 121.4924 | 0.063768 | -121.2642 | 0.062 | -121.266
712.2812 | 121.9208 | -121.756 | 0.16937 | 0.12643 | -0.008469 | 0.08873 | 0.020768 | 0.12325 | 0.1039 | -0.012357 | 0.052488 | 0.16164 | 0.069033 | -0.10179 | -0.015859 | 0.004908 | 121.3304 | 121.4787 | 0.1539 | 0.018997 | 0.1162 | 0.048234 | 0.15071 | 0.13136 | 0.015109 | 0.079954 | 0.1891 | 0.096499 | -0.07432 | 0.011607 | 0.032374 | 121.3579 | 121.5061 | 0.068347 | -121.2779 | 0.084892 | -121.2614
714 | 122.0306 | -121.6919 | 0.12817 | 0.12643 | -0.00389 | 0.08873 | 0.020768 | 0.12325 | 0.09474 | -0.016936 | 0.061645 | 0.16622 | 0.064455 | -0.10637 | -0.015859 | 0.00033 | 121.3304 | 121.4741 | 0.1539 | 0.023576 | 0.1162 | 0.048234 | 0.15071 | 0.12221 | 0.01053 | 0.089111 | 0.19368 | 0.091921 | -0.078899 | 0.011607 | 0.027796 | 121.3579 | 121.5015 | 0.077504 | -121.2688 | 0.080314 | -121.266
715.6875 | 121.9666 | -121.7422 | 0.16937 | 0.13101 | 0.000689 | 0.084151 | 0.020768 | 0.12325 | 0.09474 | -0.012357 | 0.057066 | 0.16164 | 0.059877 | -0.097207 | -0.015859 | 0.004908 | 121.3396 | 121.4695 | 0.15847 | 0.028155 | 0.11162 | 0.048234 | 0.15071 | 0.12221 | 0.015109 | 0.084532 | 0.1891 | 0.087343 | -0.069741 | 0.011607 | 0.032374 | 121.367 | 121.497 | 0.072925 | -121.2825 | 0.075736 | -121.2797
717.4375 | 122.0444 | -121.6965 | 0.13275 | 0.13101 | -0.00389 | 0.08873 | 0.01619 | 0.12782 | 0.099318 | -0.021514 | 0.052488 | 0.16622 | 0.055298 | -0.10179 | -0.011281 | 0.00033 | 121.3304 | 121.4787 | 0.15847 | 0.023576 | 0.1162 | 0.043656 | 0.15529 | 0.12678 | 0.005952 | 0.079954 | 0.19368 | 0.082764 | -0.07432 | 0.016185 | 0.027796 | 121.3579 | 121.5061 | 0.063769 | -121.2779 | 0.066579 | -121.2751
719.1875 | 121.907 | -121.7331 | 0.16937 | 0.12643 | -0.013048 | 0.093308 | 0.011611 | 0.12325 | 0.099318 | -0.021514 | 0.061645 | 0.16164 | 0.064455 | -0.10179 | -0.011281 | 0.009486 | 121.3442 | 121.4695 | 0.1539 | 0.014418 | 0.12077 | 0.039077 | 0.15071 | 0.12678 | 0.005952 | 0.089111 | 0.1891 | 0.091921 | -0.07432 | 0.016185 | 0.036952 | 121.3716 | 121.497 | 0.072926 | -121.2825 | 0.075736 | -121.2797
720.9375 | 122.0215 | -121.6782 | 0.12817 | 0.12643 | -0.008469 | 0.08873 | 0.011611 | 0.12782 | 0.099318 | -0.012357 | 0.052488 | 0.16622 | 0.059877 | -0.097207 | -0.011281 | 0.004908 | 121.335 | 121.4787 | 0.1539 | 0.018997 | 0.1162 | 0.039077 | 0.15529 | 0.12678 | 0.015109 | 0.079954 | 0.19368 | 0.087343 | -0.069741 | 0.016185 | 0.032374 | 121.3625 | 121.5061 | 0.063769 | -121.2825 | 0.071158 | -121.2751
722.6094 | 122.0398 | -121.6782 | 0.11902 | 0.12185 | -0.00389 | 0.08873 | 0.01619 | 0.1324 | 0.099318 | -0.012357 | 0.066223 | 0.17079 | 0.064455 | -0.10179 | -0.015859 | -0.004248 | 121.335 | 121.4787 | 0.14932 | 0.023576 | 0.1162 | 0.043656 | 0.15987 | 0.12678 | 0.015109 | 0.093689 | 0.19826 | 0.091921 | -0.07432 | 0.011607 | 0.023218 | 121.3625 | 121.5061 | 0.082082 | -121.2688 | 0.080314 | -121.2705
724.3438 | 122.0215 | -121.7331 | 0.13733 | 0.12643 | -0.00389 | 0.08873 | 0.01619 | 0.1324 | 0.099318 | -0.016936 | 0.066223 | 0.16164 | 0.059877 | -0.10637 | -0.015859 | 0.004908 | 121.3442 | 121.4558 | 0.1539 | 0.023576 | 0.1162 | 0.043656 | 0.15987 | 0.12678 | 0.01053 | 0.093689 | 0.1891 | 0.087343 | -0.078899 | 0.011607 | 0.032374 | 121.3716 | 121.4832 | 0.082082 | -121.2779 | 0.075736 | -121.2843
726.0938 | 122.0169 | -121.6873 | 0.1236 | 0.12643 | 0.000689 | 0.093308 | 0.011611 | 0.12325 | 0.099318 | -0.016936 | 0.057066 | 0.16622 | 0.059877 | -0.10179 | -0.011281 | 0.009486 | 121.3258 | 121.4695 | 0.1539 | 0.028155 | 0.12077 | 0.039077 | 0.15071 | 0.12678 | 0.01053 | 0.084532 | 0.19368 | 0.087343 | -0.07432 | 0.016185 | 0.036952 | 121.3533 | 121.497 | 0.068347 | -121.2688 | 0.071158 | -121.266
727.8438 | 121.9894 | -121.701 | 0.14648 | 0.13559 | -0.008469 | 0.084151 | 0.011611 | 0.12782 | 0.099318 | -0.012357 | 0.061645 | 0.16622 | 0.059877 | -0.10637 | -0.011281 | 0.004908 | 121.3396 | 121.4832 | 0.16305 | 0.018997 | 0.11162 | 0.039077 | 0.15529 | 0.12678 | 0.015109 | 0.089111 | 0.19368 | 0.087343 | -0.078899 | 0.016185 | 0.032374 | 121.367 | 121.5107 | 0.072926 | -121.2779 | 0.071158 | -121.2797
729.5156 | 121.9025 | -121.7331 | 0.16022 | 0.13101 | 0.000689 | 0.08873 | 0.007033 | 0.12782 | 0.1039 | -0.016936 | 0.052488 | 0.17079 | 0.055298 | -0.092628 | -0.020437 | 0.004908 | 121.3396 | 121.4832 | 0.15847 | 0.028155 | 0.1162 | 0.034499 | 0.15529 | 0.13136 | 0.01053 | 0.079954 | 0.19826 | 0.082764 | -0.065162 | 0.007029 | 0.032374 | 121.367 | 121.5107 | 0.072925 | -121.2871 | 0.075735 | -121.2843
731.25 | 121.9299 | -121.7377 | 0.15106 | 0.12643 | 0.000689 | 0.08873 | 0.020768 | 0.12782 | 0.1039 | -0.007779 | 0.061645 | 0.16164 | 0.064455 | -0.097207 | -0.011281 | -0.004248 | 121.3396 | 121.4741 | 0.1539 | 0.028155 | 0.1162 | 0.048234 | 0.15529 | 0.13136 | 0.019687 | 0.089111 | 0.1891 | 0.091921 | -0.069741 | 0.016185 | 0.023218 | 121.367 | 121.5015 | 0.072926 | -121.2779 | 0.075736 | -121.2751
733.0156 | 121.9391 | -121.7606 | 0.13733 | 0.12643 | -0.00389 | 0.08873 | 0.01619 | 0.12325 | 0.099318 | -0.007779 | 0.061645 | 0.15706 | 0.059877 | -0.10637 | -0.015859 | 0.009486 | 121.3487 | 121.4878 | 0.1539 | 0.023576 | 0.1162 | 0.043656 | 0.15071 | 0.12678 | 0.019687 | 0.089111 | 0.18452 | 0.087343 | -0.078899 | 0.011607 | 0.036952 | 121.3762 | 121.5153 | 0.077504 | -121.2871 | 0.075736 | -121.2889
734.7031 | 121.9162 | -121.7651 | 0.16022 | 0.12643 | -0.00389 | 0.084151 | 0.011611 | 0.1324 | 0.099318 | -0.021514 | 0.066223 | 0.16164 | 0.059877 | -0.097207 | -0.015859 | 0.009486 | 121.3396 | 121.4787 | 0.1539 | 0.023576 | 0.11162 | 0.039077 | 0.15987 | 0.12678 | 0.005952 | 0.093689 | 0.1891 | 0.087343 | -0.069741 | 0.011607 | 0.036952 | 121.367 | 121.5061 | 0.082082 | -121.2734 | 0.075736 | -121.2797
736.4531 | 121.9208 | -121.7606 | 0.16479 | 0.12643 | 0.000689 | 0.08873 | 0.011611 | 0.1324 | 0.1039 | -0.016936 | 0.061645 | 0.17079 | 0.055298 | -0.11552 | -0.015859 | 0.00033 | 121.3396 | 121.4878 | 0.1539 | 0.028155 | 0.1162 | 0.039077 | 0.15987 | 0.13136 | 0.01053 | 0.089111 | 0.19826 | 0.082764 | -0.088057 | 0.011607 | 0.027796 | 121.367 | 121.5153 | 0.077504 | -121.2779 | 0.071157 | -121.2843
738.2031 | 121.9208 | -121.7468 | 0.16022 | 0.13101 | -0.00389 | 0.08873 | 0.011611 | 0.12782 | 0.09474 | -0.007779 | 0.057066 | 0.16622 | 0.064455 | -0.11094 | -0.011281 | 0.00033 | 121.3487 | 121.4832 | 0.15847 | 0.023576 | 0.1162 | 0.039077 | 0.15529 | 0.12221 | 0.019687 | 0.084532 | 0.19368 | 0.091921 | -0.083478 | 0.016185 | 0.027796 | 121.3762 | 121.5107 | 0.068347 | -121.2917 | 0.075736 | -121.2843
739.9531 | 121.962 | -121.7468 | 0.15106 | 0.13101 | -0.00389 | 0.070415 | 0.020768 | 0.12782 | 0.099318 | -0.012357 | 0.061645 | 0.16164 | 0.059877 | -0.10179 | -0.011281 | 0.004908 | 121.3487 | 121.4832 | 0.15847 | 0.023576 | 0.097881 | 0.048234 | 0.15529 | 0.12678 | 0.015109 | 0.089111 | 0.1891 | 0.087343 | -0.07432 | 0.016185 | 0.032374 | 121.3762 | 121.5107 | 0.072926 | -121.2871 | 0.071158 | -121.2889
741.625 | 121.9254 | -121.7468 | 0.15106 | 0.12643 | -0.008469 | 0.079572 | 0.011611 | 0.1324 | 0.099318 | -0.012357 | 0.061645 | 0.16622 | 0.064455 | -0.10179 | -0.020437 | -0.008827 | 121.3442 | 121.4832 | 0.1539 | 0.018997 | 0.10704 | 0.039077 | 0.15987 | 0.12678 | 0.015109 | 0.089111 | 0.19368 | 0.091921 | -0.07432 | 0.007029 | 0.018639 | 121.3716 | 121.5107 | 0.082082 | -121.2825 | 0.084892 | -121.2797
743.3594 | 121.9894 | -121.7239 | 0.14191 | 0.12643 | -0.008469 | 0.093308 | 0.01619 | 0.12782 | 0.099318 | -0.012357 | 0.066223 | 0.15706 | 0.059877 | -0.10179 | -0.011281 | 0.004908 | 121.3487 | 121.4787 | 0.1539 | 0.018997 | 0.12077 | 0.043656 | 0.15529 | 0.12678 | 0.015109 | 0.093689 | 0.18452 | 0.087343 | -0.07432 | 0.016185 | 0.032374 | 121.3762 | 121.5061 | 0.077504 | -121.2825 | 0.071158 | -121.2889
745.0938 | 121.9528 | -121.7468 | 0.16022 | 0.12185 | -0.00389 | 0.08873 | 0.01619 | 0.12782 | 0.09474 | -0.016936 | 0.070802 | 0.15706 | 0.059877 | -0.10179 | -0.006702 | 0.004908 | 121.3442 | 121.4878 | 0.14932 | 0.023576 | 0.1162 | 0.043656 | 0.15529 | 0.12221 | 0.01053 | 0.098268 | 0.18452 | 0.087343 | -0.07432 | 0.020764 | 0.032374 | 121.3716 | 121.5153 | 0.077504 | -121.2734 | 0.066579 | -121.2843
746.8281 | 122.0673 | -121.7056 | 0.12817 | 0.13559 | -0.008469 | 0.084151 | 0.011611 | 0.13698 | 0.090161 | -0.016936 | 0.057066 | 0.16622 | 0.064455 | -0.088049 | -0.015859 | 0.009486 | 121.3442 | 121.4741 | 0.16305 | 0.018997 | 0.11162 | 0.039077 | 0.16445 | 0.11763 | 0.01053 | 0.084532 | 0.19368 | 0.091921 | -0.060583 | 0.011607 | 0.036952 | 121.3716 | 121.5015 | 0.072925 | -121.2871 | 0.080314 | -121.2797
748.5156 | 121.9894 | -121.7239 | 0.12817 | 0.13101 | -0.00389 | 0.093308 | 0.007033 | 0.12782 | 0.099318 | -0.021514 | 0.061645 | 0.16164 | 0.059877 | -0.10637 | 0.007032 | 0.009486 | 121.3808 | 121.5107 | 0.15847 | 0.023576 | 0.12077 | 0.034499 | 0.15529 | 0.12678 | 0.005952 | 0.089111 | 0.1891 | 0.087343 | -0.078899 | 0.034498 | 0.036952 | 121.4082 | 121.5382 | 0.054613 | -121.3191 | 0.052845 | -121.3209
750.25 | 121.9803 | -121.7285 | 0.15106 | 0.12643 | -0.008469 | 0.079572 | 0.01619 | 0.13698 | 0.10848 | -0.007779 | 0.057066 | 0.16164 | 0.055298 | -0.10637 | -0.025015 | -0.013405 | 121.3121 | 121.4512 | 0.1539 | 0.018997 | 0.10704 | 0.043656 | 0.16445 | 0.13594 | 0.019687 | 0.084532 | 0.1891 | 0.082764 | -0.078899 | 0.002451 | 0.014061 | 121.3396 | 121.4787 | 0.082081 | -121.255 | 0.080313 | -121.2568
751.9375 | 121.9528 | -121.7514 | 0.15106 | 0.11727 | -0.00389 | 0.093308 | 0.011611 | 0.1324 | 0.1039 | -0.012357 | 0.052488 | 0.16622 | 0.059877 | -0.10637 | 0.016188 | -0.004248 | 121.4128 | 121.5473 | 0.14474 | 0.023576 | 0.12077 | 0.039077 | 0.15987 | 0.13136 | 0.015109 | 0.079954 | 0.19368 | 0.087343 | -0.078899 | 0.043654 | 0.023218 | 121.4403 | 121.5748 | 0.0363 | -121.3603 | 0.043689 | -121.353
753.6719 | 121.962 | -121.7422 | 0.15106 | 0.13559 | -0.00389 | 0.08873 | 0.011611 | 0.12325 | 0.099318 | -0.016936 | 0.052488 | 0.16622 | 0.059877 | -0.10179 | -0.006702 | 0.004908 | 121.3625 | 121.4878 | 0.16305 | 0.023576 | 0.1162 | 0.039077 | 0.15071 | 0.12678 | 0.01053 | 0.079954 | 0.19368 | 0.087343 | -0.07432 | 0.020764 | 0.032374 | 121.3899 | 121.5153 | 0.05919 | -121.31 | 0.066579 | -121.3026
755.4219 | 121.9162 | -121.7743 | 0.16937 | 0.12643 | -0.00389 | 0.093308 | 0.01619 | 0.12325 | 0.099318 | -0.021514 | 0.047909 | 0.16164 | 0.069033 | -0.10179 | 0.020767 | -0.013405 | 121.4403 | 121.5382 | 0.1539 | 0.023576 | 0.12077 | 0.043656 | 0.15071 | 0.12678 | 0.005952 | 0.075375 | 0.1891 | 0.096499 | -0.07432 | 0.048233 | 0.014061 | 121.4678 | 121.5656 | 0.027142 | -121.3924 | 0.048266 | -121.3713
757.1562 | 122.0398 | -121.7331 | 0.1236 | 0.13101 | -0.00389 | 0.08873 | 0.011611 | 0.12782 | 0.099318 | -0.012357 | 0.066223 | 0.17079 | 0.055298 | -0.10637 | 0.01161 | 0.00033 | 121.3808 | 121.5015 | 0.15847 | 0.023576 | 0.1162 | 0.039077 | 0.15529 | 0.12678 | 0.015109 | 0.093689 | 0.19826 | 0.082764 | -0.078899 | 0.039076 | 0.027796 | 121.4082 | 121.529 | 0.054613 | -121.3146 | 0.043688 | -121.3255
758.8906 | 122.0078 | -121.7194 | 0.15106 | 0.13101 | -0.008469 | 0.08873 | 0.007033 | 0.12325 | 0.099318 | -0.012357 | 0.061645 | 0.16622 | 0.055298 | -0.11094 | -0.020437 | 0.009486 | 121.3579 | 121.4878 | 0.15847 | 0.018997 | 0.1162 | 0.034499 | 0.15071 | 0.12678 | 0.015109 | 0.089111 | 0.19368 | 0.082764 | -0.083478 | 0.007029 | 0.036952 | 121.3854 | 121.5153 | 0.082082 | -121.2962 | 0.075735 | -121.3026
760.5625 | 121.9574 | -121.7606 | 0.14648 | 0.12185 | -0.013048 | 0.08873 | 0.01619 | 0.1324 | 0.1039 | -0.016936 | 0.061645 | 0.16164 | 0.059877 | -0.10179 | -0.006702 | 0.009486 | 121.3487 | 121.4787 | 0.14932 | 0.014418 | 0.1162 | 0.043656 | 0.15987 | 0.13136 | 0.01053 | 0.089111 | 0.1891 | 0.087343 | -0.07432 | 0.020764 | 0.036952 | 121.3762 | 121.5061 | 0.068347 | -121.2871 | 0.066579 | -121.2889
762.2969 | 122.0078 | -121.7148 | 0.14648 | 0.13101 | 0.000689 | 0.084151 | 0.007033 | 0.12782 | 0.099318 | -0.016936 | 0.052488 | 0.16622 | 0.064455 | -0.10637 | -0.015859 | 0.009486 | 121.3442 | 121.4878 | 0.15847 | 0.028155 | 0.11162 | 0.034499 | 0.15529 | 0.12678 | 0.01053 | 0.079954 | 0.19368 | 0.091921 | -0.078899 | 0.011607 | 0.036952 | 121.3716 | 121.5153 | 0.068347 | -121.2917 | 0.080314 | -121.2797
763.9688 | 122.0718 | -121.7102 | 0.13733 | 0.12643 | -0.008469 | 0.084151 | 0.01619 | 0.1324 | 0.09474 | -0.021514 | 0.057066 | 0.16622 | 0.055298 | -0.10637 | -0.006702 | 0.004908 | 121.3487 | 121.4832 | 0.1539 | 0.018997 | 0.11162 | 0.043656 | 0.15987 | 0.12221 | 0.005952 | 0.084532 | 0.19368 | 0.082764 | -0.078899 | 0.020764 | 0.032374 | 121.3762 | 121.5107 | 0.063768 | -121.2917 | 0.062 | -121.2934
765.7188 | 121.9391 | -121.7606 | 0.16022 | 0.12643 | 0.005267 | 0.08873 | 0.011611 | 0.12325 | 0.09474 | -0.012357 | 0.057066 | 0.16622 | 0.059877 | -0.10179 | -0.011281 | 0.009486 | 121.367 | 121.5107 | 0.1539 | 0.032733 | 0.1162 | 0.039077 | 0.15071 | 0.12221 | 0.015109 | 0.084532 | 0.19368 | 0.087343 | -0.07432 | 0.016185 | 0.036952 | 121.3945 | 121.5382 | 0.068347 | -121.31 | 0.071158 | -121.3072
767.4531 | 122.0215 | -121.7239 | 0.14191 | 0.12643 | -0.00389 | 0.084151 | 0.011611 | 0.11867 | 0.09474 | -0.016936 | 0.057066 | 0.16622 | 0.059877 | -0.10179 | -0.011281 | 0.009486 | 121.3487 | 121.4878 | 0.1539 | 0.023576 | 0.11162 | 0.039077 | 0.14613 | 0.12221 | 0.01053 | 0.084532 | 0.19368 | 0.087343 | -0.07432 | 0.016185 | 0.036952 | 121.3762 | 121.5153 | 0.068347 | -121.2917 | 0.071158 | -121.2889
769.1875 | 122.0398 | -121.7056 | 0.10529 | 0.13101 | -0.00389 | 0.084151 | 0.007033 | 0.11867 | 0.09474 | -0.012357 | 0.061645 | 0.16622 | 0.059877 | -0.11094 | -0.011281 | 0.014064 | 121.3487 | 121.4924 | 0.15847 | 0.023576 | 0.11162 | 0.034499 | 0.14613 | 0.12221 | 0.015109 | 0.089111 | 0.19368 | 0.087343 | -0.083478 | 0.016185 | 0.04153 | 121.3762 | 121.5199 | 0.072926 | -121.2871 | 0.071158 | -121.2889
770.9375 | 122.0352 | -121.701 | 0.12817 | 0.13101 | 0.000689 | 0.08873 | 0.01619 | 0.12325 | 0.090161 | -0.007779 | 0.057066 | 0.16164 | 0.059877 | -0.10637 | -0.006702 | 0.004908 | 121.3533 | 121.4924 | 0.15847 | 0.028155 | 0.1162 | 0.043656 | 0.15071 | 0.11763 | 0.019687 | 0.084532 | 0.1891 | 0.087343 | -0.078899 | 0.020764 | 0.032374 | 121.3808 | 121.5199 | 0.063768 | -121.2962 | 0.066579 | -121.2934
772.6094 | 121.9254 | -121.7697 | 0.16937 | 0.12643 | -0.008469 | 0.093308 | 0.007033 | 0.12782 | 0.099318 | -0.012357 | 0.066223 | 0.16622 | 0.059877 | -0.10179 | -0.015859 | 0.004908 | 121.3533 | 121.497 | 0.1539 | 0.018997 | 0.12077 | 0.034499 | 0.15529 | 0.12678 | 0.015109 | 0.093689 | 0.19368 | 0.087343 | -0.07432 | 0.011607 | 0.032374 | 121.3808 | 121.5244 | 0.082082 | -121.2871 | 0.075736 | -121.2934
774.3438 | 121.9757 | -121.7514 | 0.14648 | 0.12643 | -0.008469 | 0.08873 | 0.002454 | 0.11867 | 0.099318 | -0.012357 | 0.057066 | 0.16622 | 0.055298 | -0.10179 | -0.006702 | 0.009486 | 121.3625 | 121.4924 | 0.1539 | 0.018997 | 0.1162 | 0.02992 | 0.14613 | 0.12678 | 0.015109 | 0.084532 | 0.19368 | 0.082764 | -0.07432 | 0.020764 | 0.036952 | 121.3899 | 121.5199 | 0.063768 | -121.3054 | 0.062 | -121.3072
776.0938 | 122.1085 | -121.7239 | 0.12817 | 0.13101 | -0.00389 | 0.08873 | 0.020768 | 0.1324 | 0.1039 | -0.016936 | 0.057066 | 0.17079 | 0.059877 | -0.10179 | 0.020767 | -0.017983 | 121.4037 | 121.5015 | 0.15847 | 0.023576 | 0.1162 | 0.048234 | 0.15987 | 0.13136 | 0.01053 | 0.084532 | 0.19826 | 0.087343 | -0.07432 | 0.048233 | 0.009483 | 121.4311 | 121.529 | 0.036299 | -121.3466 | 0.03911 | -121.3438
777.8281 | 122.0169 | -121.7239 | 0.09613 | 0.13101 | -0.013048 | 0.08873 | 0.01619 | 0.12782 | 0.099318 | -0.016936 | 0.066223 | 0.16164 | 0.059877 | -0.10179 | 0.016188 | -0.017983 | 121.4403 | 121.5748 | 0.15847 | 0.014418 | 0.1162 | 0.043656 | 0.15529 | 0.12678 | 0.01053 | 0.093689 | 0.1891 | 0.087343 | -0.07432 | 0.043654 | 0.009483 | 121.4678 | 121.6023 | 0.050035 | -121.3741 | 0.043689 | -121.3804
779.5156 | 122.0398 | -121.7285 | 0.12817 | 0.11727 | 0.000689 | 0.08873 | 0.011611 | 0.12325 | 0.09474 | -0.026092 | 0.052488 | 0.15706 | 0.064455 | -0.10637 | -0.011281 | 0.00033 | 121.3533 | 121.4878 | 0.14474 | 0.028155 | 0.1162 | 0.039077 | 0.15071 | 0.12221 | 0.001374 | 0.079954 | 0.18452 | 0.091921 | -0.078899 | 0.016185 | 0.027796 | 121.3808 | 121.5153 | 0.063769 | -121.3008 | 0.075736 | -121.2889
781.2656 | 121.9299 | -121.7377 | 0.14648 | 0.12643 | -0.00389 | 0.08873 | 0.007033 | 0.1324 | 0.099318 | -0.016936 | 0.061645 | 0.16622 | 0.059877 | -0.10179 | -0.006702 | 0.004908 | 121.3533 | 121.4832 | 0.1539 | 0.023576 | 0.1162 | 0.034499 | 0.15987 | 0.12678 | 0.01053 | 0.089111 | 0.19368 | 0.087343 | -0.07432 | 0.020764 | 0.032374 | 121.3808 | 121.5107 | 0.068347 | -121.2917 | 0.066579 | -121.2934
783 | 121.9574 | -121.7514 | 0.16022 | 0.13559 | -0.013048 | 0.084151 | 0.011611 | 0.12782 | 0.099318 | -0.012357 | 0.057066 | 0.15706 | 0.064455 | -0.10637 | -0.011281 | 0.004908 | 121.3579 | 121.497 | 0.16305 | 0.014418 | 0.11162 | 0.039077 | 0.15529 | 0.12678 | 0.015109 | 0.084532 | 0.18452 | 0.091921 | -0.078899 | 0.016185 | 0.032374 | 121.3854 | 121.5244 | 0.068347 | -121.3008 | 0.075736 | -121.2934
784.6719 | 121.9528 | -121.756 | 0.16022 | 0.11727 | 0.000689 | 0.08873 | 0.007033 | 0.12325 | 0.09474 | -0.016936 | 0.057066 | 0.15706 | 0.064455 | -0.11094 | -0.011281 | 0.004908 | 121.367 | 121.5015 | 0.14474 | 0.028155 | 0.1162 | 0.034499 | 0.15071 | 0.12221 | 0.01053 | 0.084532 | 0.18452 | 0.091921 | -0.083478 | 0.016185 | 0.032374 | 121.3945 | 121.529 | 0.068347 | -121.31 | 0.075736 | -121.3026
786.4219 | 121.9757 | -121.7422 | 0.14648 | 0.12643 | -0.00389 | 0.08873 | 0.011611 | 0.12782 | 0.09474 | -0.012357 | 0.066223 | 0.17537 | 0.069033 | -0.097207 | -0.015859 | 0.004908 | 121.3487 | 121.4924 | 0.1539 | 0.023576 | 0.1162 | 0.039077 | 0.15529 | 0.12221 | 0.015109 | 0.093689 | 0.20284 | 0.096499 | -0.069741 | 0.011607 | 0.032374 | 121.3762 | 121.5199 | 0.082082 | -121.2825 | 0.084892 | -121.2797
788.1719 | 121.9391 | -121.6827 | 0.14191 | 0.13559 | -0.00389 | 0.074994 | 0.002454 | 0.11867 | 0.09474 | -0.021514 | 0.07538 | 0.14332 | 0.046142 | -0.10637 | -0.002124 | 0.004908 | 0.048926 | 0.1067 | 0.16305 | 0.023576 | 0.10246 | 0.02992 | 0.14613 | 0.12221 | 0.005952 | 0.10285 | 0.17079 | 0.073608 | -0.078899 | 0.025342 | 0.032374 | 0.076392 | 0.13417 | 0.077504 | 0.026454 | 0.048266 | -0.002784
789.9219 | 122.0215 | -121.6461 | 0.11444 | 0.13101 | -0.013048 | 0.079572 | 0.002454 | 0.11867 | 0.085583 | -0.021514 | 0.079959 | 0.15706 | 0.055298 | -0.11094 | -0.006702 | 0.00033 | 0.012299 | 0.070079 | 0.15847 | 0.014418 | 0.10704 | 0.02992 | 0.14613 | 0.11305 | 0.005952 | 0.10743 | 0.18452 | 0.082764 | -0.083478 | 0.020764 | 0.027796 | 0.039765 | 0.097545 | 0.086661 | 0.06766 | 0.062 | 0.042999
791.5938 | 121.9162 | -121.7194 | 0.16022 | 0.14474 | -0.008469 | 0.084151 | 0.007033 | 0.12325 | 0.09474 | -0.016936 | 0.070802 | 0.15248 | 0.046142 | -0.10179 | -0.006702 | 0.009486 | 0.007721 | 0.060923 | 0.17221 | 0.018997 | 0.11162 | 0.034499 | 0.15071 | 0.12221 | 0.01053 | 0.098268 | 0.17994 | 0.073608 | -0.07432 | 0.020764 | 0.036952 | 0.035187 | 0.088389 | 0.077504 | 0.063081 | 0.052844 | 0.038421
793.3281 | 121.9025 | -121.7285 | 0.13733 | 0.13101 | -0.008469 | 0.084151 | 0.002454 | 0.12325 | 0.090161 | -0.016936 | 0.070802 | 0.1479 | 0.046142 | -0.11094 | -0.006702 | 0.009486 | -0.006014 | 0.051766 | 0.15847 | 0.018997 | 0.11162 | 0.02992 | 0.15071 | 0.11763 | 0.01053 | 0.098268 | 0.17536 | 0.073608 | -0.083478 | 0.020764 | 0.036952 | 0.021452 | 0.079232 | 0.077504 | 0.076816 | 0.052844 | 0.052156
795 | 121.907 | -121.7514 | 0.13733 | 0.14017 | -0.013048 | 0.084151 | 0.007033 | 0.12325 | 0.099318 | -0.021514 | 0.07538 | 0.15706 | 0.05072 | -0.10179 | -0.006702 | 0.014064 | -0.010593 | 0.038032 | 0.16763 | 0.014418 | 0.11162 | 0.034499 | 0.15071 | 0.12678 | 0.005952 | 0.10285 | 0.18452 | 0.078186 | -0.07432 | 0.020764 | 0.04153 | 0.016873 | 0.065498 | 0.082082 | 0.085973 | 0.057422 | 0.061313
796.7344 | 122.0261 | -121.7148 | 0.11444 | 0.14932 | -0.013048 | 0.079572 | 0.002454 | 0.11867 | 0.090161 | -0.021514 | 0.084537 | 0.15248 | 0.046142 | -0.11552 | -0.011281 | 0.014064 | -0.015171 | 0.04261 | 0.17679 | 0.014418 | 0.10704 | 0.02992 | 0.14613 | 0.11763 | 0.005952 | 0.112 | 0.17994 | 0.073608 | -0.088057 | 0.016185 | 0.04153 | 0.012295 | 0.070076 | 0.095818 | 0.099708 | 0.057423 | 0.061313
798.4688 | 121.994 | -121.7239 | 0.11444 | 0.14017 | -0.017627 | 0.084151 | 0.007033 | 0.11867 | 0.081005 | -0.03067 | 0.070802 | 0.15706 | 0.05072 | -0.11552 | -0.006702 | 0.014064 | -0.010593 | 0.04261 | 0.16763 | 0.009839 | 0.11162 | 0.034499 | 0.14613 | 0.10847 | -0.003204 | 0.098268 | 0.18452 | 0.078186 | -0.088057 | 0.020764 | 0.04153 | 0.016873 | 0.070076 | 0.077504 | 0.081395 | 0.057422 | 0.061313
800.2031 | 122.0352 | -121.6873 | 0.10529 | 0.14474 | -0.013048 | 0.074994 | 0.002454 | 0.11867 | 0.085583 | -0.021514 | 0.07538 | 0.15706 | 0.055298 | -0.10179 | -0.002124 | 0.014064 | -0.019749 | 0.033454 | 0.17221 | 0.014418 | 0.10246 | 0.02992 | 0.14613 | 0.11305 | 0.005952 | 0.10285 | 0.18452 | 0.082764 | -0.07432 | 0.025342 | 0.04153 | 0.007717 | 0.06092 | 0.077504 | 0.095129 | 0.057422 | 0.075047
801.9375 | 121.9482 | -121.7606 | 0.13275 | 0.14017 | -0.013048 | 0.079572 | 0.002454 | 0.11867 | 0.090161 | -0.016936 | 0.07538 | 0.16164 | 0.041563 | -0.10179 | -0.006702 | 0.009486 | -0.019749 | 0.028875 | 0.16763 | 0.014418 | 0.10704 | 0.02992 | 0.14613 | 0.11763 | 0.01053 | 0.10285 | 0.1891 | 0.069029 | -0.07432 | 0.020764 | 0.036952 | 0.007717 | 0.056341 | 0.082082 | 0.095129 | 0.048265 | 0.061312
803.625 | 121.9528 | -121.7422 | 0.12817 | 0.14474 | -0.008469 | 0.079572 | 0.007033 | 0.11867 | 0.09474 | -0.012357 | 0.070802 | 0.15248 | 0.05072 | -0.10637 | -0.006702 | 0.018642 | -0.019749 | 0.024297 | 0.17221 | 0.018997 | 0.10704 | 0.034499 | 0.14613 | 0.12221 | 0.015109 | 0.098268 | 0.17994 | 0.078186 | -0.078899 | 0.020764 | 0.046108 | 0.007717 | 0.051763 | 0.077504 | 0.090551 | 0.057422 | 0.070469
805.375 | 121.9711 | -121.7422 | 0.13733 | 0.14017 | -0.013048 | 0.079572 | 0.01619 | 0.11867 | 0.085583 | -0.03067 | 0.070802 | 0.15248 | 0.05072 | -0.11094 | -0.006702 | 0.018642 | -0.019749 | 0.028875 | 0.16763 | 0.014418 | 0.10704 | 0.043656 | 0.14613 | 0.11305 | -0.003204 | 0.098268 | 0.17994 | 0.078186 | -0.083478 | 0.020764 | 0.046108 | 0.007717 | 0.056341 | 0.077504 | 0.090551 | 0.057422 | 0.070469
807.1094 | 121.9208 | -121.756 | 0.14191 | 0.14017 | -0.00389 | 0.074994 | 0.007033 | 0.11867 | 0.090161 | -0.021514 | 0.07538 | 0.15248 | 0.055298 | -0.10637 | -0.011281 | 0.014064 | -0.024328 | 0.024297 | 0.16763 | 0.023576 | 0.10246 | 0.034499 | 0.14613 | 0.11763 | 0.005952 | 0.10285 | 0.17994 | 0.082764 | -0.078899 | 0.016185 | 0.04153 | 0.003138 | 0.051763 | 0.086661 | 0.099708 | 0.066579 | 0.079626
808.8438 | 121.9162 | -121.7834 | 0.13733 | 0.13101 | -0.013048 | 0.079572 | 0.002454 | 0.11867 | 0.090161 | -0.016936 | 0.052488 | 0.15248 | 0.05072 | -0.10179 | -0.006702 | 0.009486 | -0.024328 | 0.019719 | 0.15847 | 0.014418 | 0.10704 | 0.02992 | 0.14613 | 0.11763 | 0.01053 | 0.079954 | 0.17994 | 0.078186 | -0.07432 | 0.020764 | 0.036952 | 0.003138 | 0.047185 | 0.05919 | 0.076816 | 0.057422 | 0.075048
810.5312 | 122.0398 | -121.7239 | 0.1236 | 0.14017 | -0.008469 | 0.084151 | 0.007033 | 0.11867 | 0.090161 | -0.026092 | 0.052488 | 0.15248 | 0.055298 | -0.10637 | -0.006702 | 0.009486 | -0.024328 | 0.028875 | 0.16763 | 0.018997 | 0.11162 | 0.034499 | 0.14613 | 0.11763 | 0.001374 | 0.079954 | 0.17994 | 0.082764 | -0.078899 | 0.020764 | 0.036952 | 0.003138 | 0.056341 | 0.05919 | 0.076816 | 0.062 | 0.079626
812.2656 | 121.9025 | -121.756 | 0.15564 | 0.13559 | -0.017627 | 0.084151 | 0.007033 | 0.11409 | 0.099318 | -0.012357 | 0.057066 | 0.16164 | 0.05072 | -0.10179 | -0.015859 | 0.009486 | -0.028906 | 0.019719 | 0.16305 | 0.009839 | 0.11162 | 0.034499 | 0.14156 | 0.12678 | 0.015109 | 0.084532 | 0.1891 | 0.078186 | -0.07432 | 0.011607 | 0.036952 | -0.00144 | 0.047185 | 0.072925 | 0.085972 | 0.066579 | 0.079626
813.9375 | 122.0398 | -121.7056 | 0.11444 | 0.13559 | -0.013048 | 0.079572 | 0.007033 | 0.11867 | 0.090161 | -0.016936 | 0.047909 | 0.15706 | 0.05072 | -0.10637 | -0.006702 | 0.018642 | -0.033484 | 0.024297 | 0.16305 | 0.014418 | 0.10704 | 0.034499 | 0.14613 | 0.11763 | 0.01053 | 0.075375 | 0.18452 | 0.078186 | -0.078899 | 0.020764 | 0.046108 | -0.006018 | 0.051763 | 0.054611 | 0.081393 | 0.057422 | 0.084204
815.6719 | 122.0123 | -121.7285 | 0.13275 | 0.13559 | 0.000689 | 0.074994 | 0.002454 | 0.11867 | 0.085583 | -0.026092 | 0.047909 | 0.15248 | 0.055298 | -0.11094 | -0.006702 | 0.009486 | -0.024328 | 0.019719 | 0.16305 | 0.028155 | 0.10246 | 0.02992 | 0.14613 | 0.11305 | 0.001374 | 0.075375 | 0.17994 | 0.082764 | -0.083478 | 0.020764 | 0.036952 | 0.003138 | 0.047185 | 0.054611 | 0.072237 | 0.062 | 0.079626
817.4062 | 121.9757 | -121.756 | 0.13733 | 0.14017 | -0.00389 | 0.079572 | 0.002454 | 0.11867 | 0.090161 | -0.016936 | 0.052488 | 0.15248 | 0.055298 | -0.11094 | -0.011281 | 0.009486 | -0.033484 | 0.015141 | 0.16763 | 0.023576 | 0.10704 | 0.02992 | 0.14613 | 0.11763 | 0.01053 | 0.079954 | 0.17994 | 0.082764 | -0.083478 | 0.016185 | 0.036952 | -0.006018 | 0.042607 | 0.063769 | 0.085972 | 0.066579 | 0.088782
819.0938 | 121.9574 | -121.7606 | 0.11902 | 0.14017 | -0.008469 | 0.074994 | 0.007033 | 0.11409 | 0.081005 | -0.021514 | 0.047909 | 0.15706 | 0.055298 | -0.10179 | -0.002124 | 0.014064 | -0.033484 | 0.019719 | 0.16763 | 0.018997 | 0.10246 | 0.034499 | 0.14156 | 0.10847 | 0.005952 | 0.075375 | 0.18452 | 0.082764 | -0.07432 | 0.025342 | 0.04153 | -0.006018 | 0.047185 | 0.050033 | 0.081393 | 0.057422 | 0.088782
820.8438 | 121.9116 | -121.8063 | 0.14648 | 0.14017 | -0.013048 | 0.079572 | 0.007033 | 0.11867 | 0.09474 | -0.021514 | 0.047909 | 0.1479 | 0.046142 | -0.11094 | -0.011281 | 0.009486 | -0.028906 | 0.015141 | 0.16763 | 0.014418 | 0.10704 | 0.034499 | 0.14613 | 0.12221 | 0.005952 | 0.075375 | 0.17536 | 0.073608 | -0.083478 | 0.016185 | 0.036952 | -0.00144 | 0.042607 | 0.05919 | 0.076815 | 0.057423 | 0.075048
822.5781 | 122.0032 | -121.7102 | 0.14648 | 0.13559 | -0.008469 | 0.074994 | 0.007033 | 0.11867 | 0.09474 | -0.021514 | 0.047909 | 0.1479 | 0.055298 | -0.1201 | -0.006702 | 0.009486 | -0.038063 | 0.015141 | 0.16305 | 0.018997 | 0.10246 | 0.034499 | 0.14613 | 0.12221 | 0.005952 | 0.075375 | 0.17536 | 0.082764 | -0.092637 | 0.020764 | 0.036952 | -0.010597 | 0.042607 | 0.054611 | 0.085972 | 0.062 | 0.093361
824.25 | 122.0398 | -121.7331 | 0.12817 | 0.13559 | -0.013048 | 0.079572 | 0.011611 | 0.11867 | 0.090161 | -0.03067 | 0.047909 | 0.15248 | 0.05072 | -0.11094 | -0.002124 | 0.018642 | -0.033484 | 0.015141 | 0.16305 | 0.014418 | 0.10704 | 0.039077 | 0.14613 | 0.11763 | -0.003204 | 0.075375 | 0.17994 | 0.078186 | -0.083478 | 0.025342 | 0.046108 | -0.006018 | 0.042607 | 0.050033 | 0.081393 | 0.052844 | 0.084204
826 | 122.049 | -121.7194 | 0.10071 | 0.14017 | -0.013048 | 0.074994 | 0.011611 | 0.10951 | 0.090161 | -0.021514 | 0.043331 | 0.15706 | 0.055298 | -0.11094 | -0.011281 | 0.014064 | -0.038063 | 0.010563 | 0.16763 | 0.014418 | 0.10246 | 0.039077 | 0.13698 | 0.11763 | 0.005952 | 0.070797 | 0.18452 | 0.082764 | -0.083478 | 0.016185 | 0.04153 | -0.010597 | 0.038029 | 0.054612 | 0.081394 | 0.066579 | 0.093361
827.6719 | 122.0123 | -121.7331 | 0.13733 | 0.14017 | -0.013048 | 0.070415 | 0.011611 | 0.11867 | 0.09474 | -0.016936 | 0.057066 | 0.15706 | 0.059877 | -0.10637 | -0.006702 | 0.014064 | -0.038063 | 0.010563 | 0.16763 | 0.014418 | 0.097881 | 0.039077 | 0.14613 | 0.12221 | 0.01053 | 0.084532 | 0.18452 | 0.087343 | -0.078899 | 0.020764 | 0.04153 | -0.010597 | 0.038029 | 0.063768 | 0.095129 | 0.066579 | 0.09794
829.4062 | 121.9711 | -121.7834 | 0.14648 | 0.14017 | -0.008469 | 0.074994 | 0.007033 | 0.12325 | 0.09474 | -0.021514 | 0.047909 | 0.15248 | 0.046142 | -0.10637 | -0.006702 | 0.014064 | -0.033484 | 0.010563 | 0.16763 | 0.018997 | 0.10246 | 0.034499 | 0.15071 | 0.12221 | 0.005952 | 0.075375 | 0.17994 | 0.073608 | -0.078899 | 0.020764 | 0.04153 | -0.006018 | 0.038029 | 0.054611 | 0.081393 | 0.052844 | 0.079626
831.0938 | 122.0261 | -121.7102 | 0.10986 | 0.14017 | -0.013048 | 0.074994 | 0.011611 | 0.11867 | 0.085583 | -0.021514 | 0.052488 | 0.15706 | 0.05072 | -0.11094 | -0.006702 | 0.009486 | -0.04722 | 0.010563 | 0.16763 | 0.014418 | 0.10246 | 0.039077 | 0.14613 | 0.11305 | 0.005952 | 0.079954 | 0.18452 | 0.078186 | -0.083478 | 0.020764 | 0.036952 | -0.019754 | 0.038029 | 0.05919 | 0.099708 | 0.057422 | 0.09794
832.8281 | 121.9986 | -121.756 | 0.13733 | 0.14474 | -0.00389 | 0.079572 | 0.011611 | 0.11867 | 0.090161 | -0.016936 | 0.043331 | 0.16164 | 0.046142 | -0.10179 | -0.002124 | 0.018642 | -0.038063 | 0.005985 | 0.17221 | 0.023576 | 0.10704 | 0.039077 | 0.14613 | 0.11763 | 0.01053 | 0.070797 | 0.1891 | 0.073608 | -0.07432 | 0.025342 | 0.046108 | -0.010597 | 0.033451 | 0.045455 | 0.081394 | 0.048266 | 0.084205
834.5156 | 121.9437 | -121.7697 | 0.14648 | 0.13559 | -0.008469 | 0.074994 | 0.007033 | 0.11867 | 0.085583 | -0.016936 | 0.047909 | 0.15248 | 0.041563 | -0.10637 | -0.011281 | 0.014064 | -0.042641 | 0.005985 | 0.16305 | 0.018997 | 0.10246 | 0.034499 | 0.14613 | 0.11305 | 0.01053 | 0.075375 | 0.17994 | 0.069029 | -0.078899 | 0.016185 | 0.04153 | -0.015175 | 0.033451 | 0.05919 | 0.09055 | 0.052844 | 0.084204
836.2656 | 122.0398 | -121.7056 | 0.10529 | 0.14017 | -0.017627 | 0.070415 | 0.01619 | 0.11867 | 0.081005 | -0.026092 | 0.052488 | 0.15706 | 0.05072 | -0.11552 | -0.020437 | 0.009486 | -0.042641 | 0.005985 | 0.16763 | 0.009839 | 0.097881 | 0.043656 | 0.14613 | 0.10847 | 0.001374 | 0.079954 | 0.18452 | 0.078186 | -0.088057 | 0.007029 | 0.036952 | -0.015175 | 0.033451 | 0.072925 | 0.095129 | 0.071157 | 0.093361
838 | 121.9254 | -121.7606 | 0.13733 | 0.14017 | -0.013048 | 0.079572 | 0.002454 | 0.11409 | 0.085583 | -0.016936 | 0.047909 | 0.15248 | 0.05072 | -0.11094 | -0.006702 | 0.009486 | -0.042641 | 0.001406 | 0.16763 | 0.014418 | 0.10704 | 0.02992 | 0.14156 | 0.11305 | 0.01053 | 0.075375 | 0.17994 | 0.078186 | -0.083478 | 0.020764 | 0.036952 | -0.015175 | 0.028872 | 0.054611 | 0.09055 | 0.057422 | 0.093361
839.6719 | 122.0261 | -121.7377 | 0.13275 | 0.13559 | -0.013048 | 0.079572 | 0.011611 | 0.11867 | 0.085583 | -0.026092 | 0.047909 | 0.16164 | 0.055298 | -0.11094 | -0.011281 | 0.018642 | -0.042641 | 0.015141 | 0.16305 | 0.014418 | 0.10704 | 0.039077 | 0.14613 | 0.11305 | 0.001374 | 0.075375 | 0.1891 | 0.082764 | -0.083478 | 0.016185 | 0.046108 | -0.015175 | 0.042607 | 0.05919 | 0.09055 | 0.066579 | 0.097939
841.4219 | 121.9345 | -121.7972 | 0.15106 | 0.14017 | -0.013048 | 0.079572 | 0.011611 | 0.11867 | 0.09474 | -0.021514 | 0.057066 | 0.1479 | 0.055298 | -0.10637 | -0.002124 | 0.014064 | -0.04722 | 0.001406 | 0.16763 | 0.014418 | 0.10704 | 0.039077 | 0.14613 | 0.12221 | 0.005952 | 0.084532 | 0.17536 | 0.082764 | -0.078899 | 0.025342 | 0.04153 | -0.019754 | 0.028872 | 0.05919 | 0.10429 | 0.057422 | 0.10252
843.1094 | 122.0078 | -121.7102 | 0.1236 | 0.14017 | -0.017627 | 0.079572 | 0.011611 | 0.11409 | 0.081005 | -0.021514 | 0.052488 | 0.15248 | 0.046142 | -0.11094 | -0.011281 | 0.014064 | -0.042641 | 0.005985 | 0.16763 | 0.009839 | 0.10704 | 0.039077 | 0.14156 | 0.10847 | 0.005952 | 0.079954 | 0.17994 | 0.073608 | -0.083478 | 0.016185 | 0.04153 | -0.015175 | 0.033451 | 0.063769 | 0.095129 | 0.057423 | 0.088783
844.8438 | 122.0123 | -121.7514 | 0.11902 | 0.14017 | -0.008469 | 0.079572 | 0.020768 | 0.11867 | 0.090161 | -0.021514 | 0.047909 | 0.15706 | 0.055298 | -0.10637 | -0.006702 | 0.009486 | -0.042641 | 0.005985 | 0.16763 | 0.018997 | 0.10704 | 0.048234 | 0.14613 | 0.11763 | 0.005952 | 0.075375 | 0.18452 | 0.082764 | -0.078899 | 0.020764 | 0.036952 | -0.015175 | 0.033451 | 0.054611 | 0.09055 | 0.062 | 0.097939
846.5312 | 121.994 | -121.7651 | 0.13275 | 0.13559 | -0.017627 | 0.074994 | 0.01619 | 0.11409 | 0.09474 | -0.016936 | 0.052488 | 0.15248 | 0.055298 | -0.11094 | -0.011281 | 0.004908 | -0.04722 | -0.003172 | 0.16305 | 0.009839 | 0.10246 | 0.043656 | 0.14156 | 0.12221 | 0.01053 | 0.079954 | 0.17994 | 0.082764 | -0.083478 | 0.016185 | 0.032374 | -0.019754 | 0.024294 | 0.063769 | 0.099708 | 0.066579 | 0.10252
848.2812 | 121.9894 | -121.7743 | 0.14191 | 0.14017 | -0.013048 | 0.074994 | 0.01619 | 0.10951 | 0.09474 | -0.021514 | 0.057066 | 0.15706 | 0.055298 | -0.097207 | -0.002124 | 0.014064 | -0.051798 | 0.001406 | 0.16763 | 0.014418 | 0.10246 | 0.043656 | 0.13698 | 0.12221 | 0.005952 | 0.084532 | 0.18452 | 0.082764 | -0.069741 | 0.025342 | 0.04153 | -0.024332 | 0.028872 | 0.05919 | 0.10886 | 0.057422 | 0.1071
850.0156 | 122.0123 | -121.7422 | 0.12817 | 0.14017 | -0.008469 | 0.070415 | 0.011611 | 0.12325 | 0.090161 | -0.026092 | 0.057066 | 0.1479 | 0.055298 | -0.11552 | -0.002124 | 0.009486 | -0.04722 | -0.003172 | 0.16763 | 0.018997 | 0.097881 | 0.039077 | 0.15071 | 0.11763 | 0.001374 | 0.084532 | 0.17536 | 0.082764 | -0.088057 | 0.025342 | 0.036952 | -0.019754 | 0.024294 | 0.05919 | 0.10429 | 0.057422 | 0.10252
851.7031 | 122.0673 | -121.7239 | 0.10071 | 0.13559 | -0.008469 | 0.074994 | 0.01619 | 0.10951 | 0.090161 | -0.021514 | 0.047909 | 0.15248 | 0.055298 | -0.10637 | -0.011281 | 0.009486 | -0.051798 | -0.00775 | 0.16305 | 0.018997 | 0.10246 | 0.043656 | 0.13698 | 0.11763 | 0.005952 | 0.075375 | 0.17994 | 0.082764 | -0.078899 | 0.016185 | 0.036952 | -0.024332 | 0.019716 | 0.05919 | 0.099707 | 0.066579 | 0.1071
853.4375 | 122.0215 | -121.7422 | 0.12817 | 0.14017 | -0.008469 | 0.070415 | 0.01619 | 0.11867 | 0.085583 | -0.021514 | 0.043331 | 0.15706 | 0.046142 | -0.11094 | -0.011281 | 0.014064 | -0.051798 | 0.001406 | 0.16763 | 0.018997 | 0.097881 | 0.043656 | 0.14613 | 0.11305 | 0.005952 | 0.070797 | 0.18452 | 0.073608 | -0.083478 | 0.016185 | 0.04153 | -0.024332 | 0.028872 | 0.054612 | 0.095129 | 0.057423 | 0.09794
855.1094 | 122.0718 | -121.7148 | 0.1236 | 0.14017 | -0.008469 | 0.070415 | 0.01619 | 0.12325 | 0.090161 | -0.012357 | 0.047909 | 0.15706 | 0.05072 | -0.11094 | -0.006702 | 0.009486 | -0.051798 | -0.003172 | 0.16763 | 0.018997 | 0.097881 | 0.043656 | 0.15071 | 0.11763 | 0.015109 | 0.075375 | 0.18452 | 0.078186 | -0.083478 | 0.020764 | 0.036952 | -0.024332 | 0.024294 | 0.054611 | 0.099707 | 0.057422 | 0.10252
856.8594 | 122.0673 | -121.7422 | 0.11444 | 0.14017 | -0.008469 | 0.074994 | 0.011611 | 0.12325 | 0.09474 | -0.021514 | 0.052488 | 0.15248 | 0.055298 | -0.11094 | -0.006702 | 0.014064 | -0.051798 | 0.001406 | 0.16763 | 0.018997 | 0.10246 | 0.039077 | 0.15071 | 0.12221 | 0.005952 | 0.079954 | 0.17994 | 0.082764 | -0.083478 | 0.020764 | 0.04153 | -0.024332 | 0.028872 | 0.05919 | 0.10429 | 0.062 | 0.1071
858.6094 | 121.8979 | -121.7743 | 0.15106 | 0.14017 | -0.00389 | 0.074994 | 0.020768 | 0.11867 | 0.090161 | -0.016936 | 0.052488 | 0.16164 | 0.046142 | -0.11552 | -0.011281 | 0.009486 | -0.060955 | 0.001406 | 0.16763 | 0.023576 | 0.10246 | 0.048234 | 0.14613 | 0.11763 | 0.01053 | 0.079954 | 0.1891 | 0.073608 | -0.088057 | 0.016185 | 0.036952 | -0.033489 | 0.028872 | 0.063769 | 0.11344 | 0.057423 | 0.1071
860.3438 | 121.9345 | -121.7834 | 0.16022 | 0.14474 | -0.013048 | 0.070415 | 0.011611 | 0.11867 | 0.090161 | -0.026092 | 0.052488 | 0.15706 | 0.055298 | -0.11094 | -0.002124 | 0.018642 | -0.056376 | -0.00775 | 0.17221 | 0.014418 | 0.097881 | 0.039077 | 0.14613 | 0.11763 | 0.001374 | 0.079954 | 0.18452 | 0.082764 | -0.083478 | 0.025342 | 0.046108 | -0.02891 | 0.019716 | 0.054612 | 0.10886 | 0.057422 | 0.11167
862.0938 | 122.081 | -121.7377 | 0.13275 | 0.14017 | -0.013048 | 0.070415 | 0.011611 | 0.10951 | 0.081005 | -0.021514 | 0.052488 | 0.1479 | 0.046142 | -0.11094 | -0.006702 | 0.009486 | -0.056376 | -0.00775 | 0.16763 | 0.014418 | 0.097881 | 0.039077 | 0.13698 | 0.10847 | 0.005952 | 0.079954 | 0.17536 | 0.073608 | -0.083478 | 0.020764 | 0.036952 | -0.02891 | 0.019716 | 0.05919 | 0.10886 | 0.052844 | 0.10252
863.8438 | 121.9345 | -121.7834 | 0.14648 | 0.13559 | -0.017627 | 0.079572 | 0.01619 | 0.12325 | 0.090161 | -0.026092 | 0.052488 | 0.15248 | 0.046142 | -0.11094 | -0.006702 | 0.009486 | -0.04722 | -0.00775 | 0.16305 | 0.009839 | 0.10704 | 0.043656 | 0.15071 | 0.11763 | 0.001374 | 0.079954 | 0.17994 | 0.073608 | -0.083478 | 0.020764 | 0.036952 | -0.019754 | 0.019716 | 0.05919 | 0.099708 | 0.052844 | 0.093362
865.5312 | 122.0581 | -121.7377 | 0.11444 | 0.13559 | -0.013048 | 0.079572 | 0.01619 | 0.10951 | 0.081005 | -0.021514 | 0.047909 | 0.16164 | 0.05072 | -0.10637 | 0.002454 | 0.018642 | -0.060955 | -0.00775 | 0.16305 | 0.014418 | 0.10704 | 0.043656 | 0.13698 | 0.10847 | 0.005952 | 0.075375 | 0.1891 | 0.078186 | -0.078899 | 0.02992 | 0.046108 | -0.033489 | 0.019716 | 0.045455 | 0.10886 | 0.048266 | 0.11167
867.2656 | 122.0261 | -121.7331 | 0.11444 | 0.13101 | -0.013048 | 0.070415 | 0.011611 | 0.11409 | 0.081005 | -0.016936 | 0.047909 | 0.15248 | 0.05072 | -0.11094 | -0.002124 | 0.014064 | -0.056376 | -0.00775 | 0.15847 | 0.014418 | 0.097881 | 0.039077 | 0.14156 | 0.10847 | 0.01053 | 0.075375 | 0.17994 | 0.078186 | -0.083478 | 0.025342 | 0.04153 | -0.02891 | 0.019716 | 0.050033 | 0.10429 | 0.052844 | 0.1071
869 | 121.994 | -121.7789 | 0.1236 | 0.14017 | -0.013048 | 0.065837 | 0.011611 | 0.10951 | 0.09474 | -0.016936 | 0.052488 | 0.15706 | 0.046142 | -0.11552 | -0.015859 | 0.009486 | -0.060955 | -0.00775 | 0.16763 | 0.014418 | 0.093303 | 0.039077 | 0.13698 | 0.12221 | 0.01053 | 0.079954 | 0.18452 | 0.073608 | -0.088057 | 0.011607 | 0.036952 | -0.033489 | 0.019716 | 0.068347 | 0.11344 | 0.062001 | 0.1071
870.75 | 122.0123 | -121.7514 | 0.13733 | 0.14017 | -0.017627 | 0.070415 | 0.020768 | 0.10493 | 0.085583 | -0.016936 | 0.052488 | 0.16164 | 0.05072 | -0.10637 | -0.002124 | 0.014064 | -0.065533 | -0.012328 | 0.16763 | 0.009839 | 0.097881 | 0.048234 | 0.1324 | 0.11305 | 0.01053 | 0.079954 | 0.1891 | 0.078186 | -0.078899 | 0.025342 | 0.04153 | -0.038067 | 0.015138 | 0.054612 | 0.11802 | 0.052844 | 0.11625
872.4219 | 121.9208 | -121.7972 | 0.14191 | 0.13559 | -0.013048 | 0.074994 | 0.007033 | 0.11409 | 0.085583 | -0.021514 | 0.052488 | 0.15706 | 0.05072 | -0.11094 | -0.011281 | 0.018642 | -0.060955 | -0.00775 | 0.16305 | 0.014418 | 0.10246 | 0.034499 | 0.14156 | 0.11305 | 0.005952 | 0.079954 | 0.18452 | 0.078186 | -0.083478 | 0.016185 | 0.046108 | -0.033489 | 0.019716 | 0.063769 | 0.11344 | 0.062001 | 0.11167
874.1562 | 121.9757 | -121.788 | 0.16479 | 0.14017 | -0.013048 | 0.079572 | 0.011611 | 0.11409 | 0.09474 | -0.016936 | 0.047909 | 0.15706 | 0.046142 | -0.11552 | -0.006702 | 0.014064 | -0.060955 | -0.012328 | 0.16763 | 0.014418 | 0.10704 | 0.039077 | 0.14156 | 0.12221 | 0.01053 | 0.075375 | 0.18452 | 0.073608 | -0.088057 | 0.020764 | 0.04153 | -0.033489 | 0.015138 | 0.054611 | 0.10886 | 0.052844 | 0.1071
875.9062 | 121.9574 | -121.8018 | 0.15564 | 0.13559 | -0.013048 | 0.074994 | 0.020768 | 0.11409 | 0.09474 | -0.021514 | 0.052488 | 0.15248 | 0.046142 | -0.11094 | -0.011281 | 0.018642 | -0.060955 | -0.012328 | 0.16305 | 0.014418 | 0.10246 | 0.048234 | 0.14156 | 0.12221 | 0.005952 | 0.079954 | 0.17994 | 0.073608 | -0.083478 | 0.016185 | 0.046108 | -0.033489 | 0.015138 | 0.063769 | 0.11344 | 0.057423 | 0.1071
877.6562 | 121.9391 | -121.788 | 0.14191 | 0.13559 | -0.00389 | 0.074994 | 0.020768 | 0.11409 | 0.085583 | -0.021514 | 0.047909 | 0.15706 | 0.027829 | -0.10637 | -0.011281 | 0.018642 | -0.065533 | -0.012328 | 0.16305 | 0.023576 | 0.10246 | 0.048234 | 0.14156 | 0.11305 | 0.005952 | 0.075375 | 0.18452 | 0.055295 | -0.078899 | 0.016185 | 0.046108 | -0.038067 | 0.015138 | 0.05919 | 0.11344 | 0.03911 | 0.093362
879.3281 | 121.9437 | -121.7606 | 0.12817 | 0.14017 | -0.00389 | 0.070415 | 0.01619 | 0.11867 | 0.090161 | -0.021514 | 0.047909 | 0.15248 | 0.046142 | -0.11552 | -0.006702 | 0.014064 | -0.065533 | -0.012328 | 0.16763 | 0.023576 | 0.097881 | 0.043656 | 0.14613 | 0.11763 | 0.005952 | 0.075375 | 0.17994 | 0.073608 | -0.088057 | 0.020764 | 0.04153 | -0.038067 | 0.015138 | 0.054611 | 0.11344 | 0.052844 | 0.11167
881 | 121.9849 | -121.756 | 0.13733 | 0.13559 | -0.00389 | 0.084151 | 0.011611 | 0.11409 | 0.085583 | -0.021514 | 0.052488 | 0.16164 | 0.05072 | -0.10637 | -0.006702 | 0.014064 | -0.060955 | -0.012328 | 0.16305 | 0.023576 | 0.11162 | 0.039077 | 0.14156 | 0.11305 | 0.005952 | 0.079954 | 0.1891 | 0.078186 | -0.078899 | 0.020764 | 0.04153 | -0.033489 | 0.015138 | 0.05919 | 0.11344 | 0.057422 | 0.11167
882.75 | 122.0306 | -121.7148 | 0.10986 | 0.14017 | -0.013048 | 0.079572 | 0.007033 | 0.12325 | 0.09474 | -0.026092 | 0.057066 | 0.16164 | 0.055298 | -0.10637 | -0.002124 | 0.014064 | -0.065533 | -0.012328 | 0.16763 | 0.014418 | 0.10704 | 0.034499 | 0.15071 | 0.12221 | 0.001374 | 0.084532 | 0.1891 | 0.082764 | -0.078899 | 0.025342 | 0.04153 | -0.038067 | 0.015138 | 0.05919 | 0.1226 | 0.057422 | 0.12083
884.4844 | 121.9437 | -121.8018 | 0.14191 | 0.14017 | -0.008469 | 0.074994 | 0.011611 | 0.11409 | 0.099318 | -0.016936 | 0.047909 | 0.1479 | 0.05072 | -0.11094 | -0.002124 | 0.004908 | -0.070112 | -0.016906 | 0.16763 | 0.018997 | 0.10246 | 0.039077 | 0.14156 | 0.12678 | 0.01053 | 0.075375 | 0.17536 | 0.078186 | -0.083478 | 0.025342 | 0.032374 | -0.042646 | 0.01056 | 0.050033 | 0.11802 | 0.052844 | 0.12083
886.1562 | 122.0078 | -121.7743 | 0.12817 | 0.13559 | -0.00389 | 0.074994 | 0.020768 | 0.12325 | 0.085583 | -0.012357 | 0.052488 | 0.15248 | 0.05072 | -0.11094 | -0.006702 | 0.014064 | -0.070112 | -0.012328 | 0.16305 | 0.023576 | 0.10246 | 0.048234 | 0.15071 | 0.11305 | 0.015109 | 0.079954 | 0.17994 | 0.078186 | -0.083478 | 0.020764 | 0.04153 | -0.042646 | 0.015138 | 0.05919 | 0.1226 | 0.057422 | 0.12083
887.9062 | 122.0535 | -121.7377 | 0.11902 | 0.13559 | -0.013048 | 0.079572 | 0.007033 | 0.11409 | 0.090161 | -0.026092 | 0.052488 | 0.15706 | 0.05072 | -0.10637 | -0.015859 | 0.009486 | -0.056376 | -0.012328 | 0.16305 | 0.014418 | 0.10704 | 0.034499 | 0.14156 | 0.11763 | 0.001374 | 0.079954 | 0.18452 | 0.078186 | -0.078899 | 0.011607 | 0.036952 | -0.02891 | 0.015138 | 0.068347 | 0.10886 | 0.066579 | 0.1071
889.5938 | 122.0627 | -121.7422 | 0.11902 | 0.13559 | -0.017627 | 0.08873 | 0.007033 | 0.10951 | 0.090161 | -0.021514 | 0.052488 | 0.16164 | 0.059877 | -0.11094 | -0.011281 | 0.02322 | -0.070112 | -0.016906 | 0.16305 | 0.009839 | 0.1162 | 0.034499 | 0.13698 | 0.11763 | 0.005952 | 0.079954 | 0.1891 | 0.087343 | -0.083478 | 0.016185 | 0.050686 | -0.042646 | 0.01056 | 0.063769 | 0.1226 | 0.071158 | 0.12999
891.3438 | 122.0901 | -121.7331 | 0.1236 | 0.13559 | -0.013048 | 0.074994 | 0.011611 | 0.11409 | 0.090161 | -0.016936 | 0.052488 | 0.15706 | 0.059877 | -0.11094 | -0.006702 | 0.014064 | -0.065533 | -0.016906 | 0.16305 | 0.014418 | 0.10246 | 0.039077 | 0.14156 | 0.11763 | 0.01053 | 0.079954 | 0.18452 | 0.087343 | -0.083478 | 0.020764 | 0.04153 | -0.038067 | 0.01056 | 0.05919 | 0.11802 | 0.066579 | 0.12541
893.0938 | 122.0215 | -121.7377 | 0.13275 | 0.13559 | -0.017627 | 0.070415 | 0.011611 | 0.10951 | 0.090161 | -0.021514 | 0.052488 | 0.15706 | 0.055298 | -0.11094 | -0.006702 | 0.014064 | -0.060955 | -0.016906 | 0.16305 | 0.009839 | 0.097881 | 0.039077 | 0.13698 | 0.11763 | 0.005952 | 0.079954 | 0.18452 | 0.082764 | -0.083478 | 0.020764 | 0.04153 | -0.033489 | 0.01056 | 0.05919 | 0.11344 | 0.062 | 0.11625
894.8281 | 122.0856 | -121.7102 | 0.11902 | 0.13101 | -0.013048 | 0.074994 | 0.01619 | 0.12325 | 0.090161 | -0.016936 | 0.047909 | 0.15706 | 0.055298 | -0.10637 | -0.006702 | 0.009486 | -0.07469 | -0.012328 | 0.15847 | 0.014418 | 0.10246 | 0.043656 | 0.15071 | 0.11763 | 0.01053 | 0.075375 | 0.18452 | 0.082764 | -0.078899 | 0.020764 | 0.036952 | -0.047224 | 0.015138 | 0.054611 | 0.1226 | 0.062 | 0.12999
896.5156 | 122.0535 | -121.756 | 0.10529 | 0.13559 | -0.017627 | 0.084151 | 0.01619 | 0.11409 | 0.09474 | -0.026092 | 0.061645 | 0.16164 | 0.05072 | -0.11552 | -0.015859 | 0.014064 | -0.070112 | -0.016906 | 0.16305 | 0.009839 | 0.11162 | 0.043656 | 0.14156 | 0.12221 | 0.001374 | 0.089111 | 0.1891 | 0.078186 | -0.088057 | 0.011607 | 0.04153 | -0.042646 | 0.01056 | 0.077504 | 0.13176 | 0.066579 | 0.12083
898.25 | 121.9803 | -121.7743 | 0.16937 | 0.14474 | -0.008469 | 0.065837 | 0.011611 | 0.10951 | 0.090161 | -0.016936 | 0.057066 | 0.15706 | 0.055298 | -0.11094 | -0.011281 | 0.014064 | -0.070112 | -0.021484 | 0.17221 | 0.018997 | 0.093303 | 0.039077 | 0.13698 | 0.11763 | 0.01053 | 0.084532 | 0.18452 | 0.082764 | -0.083478 | 0.016185 | 0.04153 | -0.042646 | 0.005982 | 0.068347 | 0.12718 | 0.066579 | 0.12541
900 | 122.0032 | -121.7926 | 0.14648 | 0.14474 | -0.017627 | 0.070415 | 0.01619 | 0.11409 | 0.090161 | -0.026092 | 0.052488 | 0.15248 | 0.046142 | -0.1201 | -0.002124 | 0.014064 | -0.07469 | -0.012328 | 0.17221 | 0.009839 | 0.097881 | 0.043656 | 0.14156 | 0.11763 | 0.001374 | 0.079954 | 0.17994 | 0.073608 | -0.092637 | 0.025342 | 0.04153 | -0.047224 | 0.015138 | 0.054612 | 0.12718 | 0.048266 | 0.12083
901.6719 | 121.9254 | -121.7972 | 0.13275 | 0.13559 | -0.013048 | 0.074994 | 0.01619 | 0.11867 | 0.09474 | -0.021514 | 0.052488 | 0.15248 | 0.055298 | -0.11094 | -0.002124 | 0.014064 | -0.070112 | -0.026063 | 0.16305 | 0.014418 | 0.10246 | 0.043656 | 0.14613 | 0.12221 | 0.005952 | 0.079954 | 0.17994 | 0.082764 | -0.083478 | 0.025342 | 0.04153 | -0.042646 | 0.001403 | 0.054612 | 0.1226 | 0.057422 | 0.12541
903.4062 | 121.9849 | -121.7606 | 0.15106 | 0.14017 | -0.017627 | 0.074994 | 0.020768 | 0.10951 | 0.090161 | -0.03067 | 0.052488 | 0.15248 | 0.055298 | -0.10637 | -0.011281 | 0.02322 | -0.065533 | -0.021484 | 0.16763 | 0.009839 | 0.10246 | 0.048234 | 0.13698 | 0.11763 | -0.003204 | 0.079954 | 0.17994 | 0.082764 | -0.078899 | 0.016185 | 0.050686 | -0.038067 | 0.005982 | 0.063769 | 0.11802 | 0.066579 | 0.12083
905.1406 | 122.0352 | -121.7194 | 0.10071 | 0.13101 | -0.017627 | 0.079572 | 0.01619 | 0.11867 | 0.090161 | -0.012357 | 0.057066 | 0.16164 | 0.055298 | -0.11094 | -0.011281 | 0.014064 | -0.07469 | -0.016906 | 0.15847 | 0.009839 | 0.10704 | 0.043656 | 0.14613 | 0.11763 | 0.015109 | 0.084532 | 0.1891 | 0.082764 | -0.083478 | 0.016185 | 0.04153 | -0.047224 | 0.01056 | 0.068347 | 0.13176 | 0.066579 | 0.12999
906.8281 | 122.0718 | -121.756 | 0.11902 | 0.13559 | -0.013048 | 0.074994 | 0.020768 | 0.12782 | 0.09474 | -0.012357 | 0.057066 | 0.16164 | 0.055298 | -0.10637 | -0.011281 | 0.014064 | -0.07469 | -0.026063 | 0.16305 | 0.014418 | 0.10246 | 0.048234 | 0.15529 | 0.12221 | 0.015109 | 0.084532 | 0.1891 | 0.082764 | -0.078899 | 0.016185 | 0.04153 | -0.047224 | 0.001403 | 0.068347 | 0.13176 | 0.066579 | 0.12999
908.5625 | 122.049 | -121.7651 | 0.11444 | 0.14017 | -0.013048 | 0.079572 | 0.007033 | 0.11867 | 0.090161 | -0.021514 | 0.047909 | 0.15706 | 0.046142 | -0.11552 | -0.002124 | 0.014064 | -0.070112 | -0.021484 | 0.16763 | 0.014418 | 0.10704 | 0.034499 | 0.14613 | 0.11763 | 0.005952 | 0.075375 | 0.18452 | 0.073608 | -0.088057 | 0.025342 | 0.04153 | -0.042646 | 0.005982 | 0.050033 | 0.11802 | 0.048266 | 0.11625
910.2969 | 122.0581 | -121.756 | 0.1236 | 0.13559 | -0.017627 | 0.070415 | 0.011611 | 0.11409 | 0.09474 | -0.026092 | 0.052488 | 0.15706 | 0.05072 | -0.10637 | -0.002124 | 0.018642 | -0.070112 | -0.026063 | 0.16305 | 0.009839 | 0.097881 | 0.039077 | 0.14156 | 0.12221 | 0.001374 | 0.079954 | 0.18452 | 0.078186 | -0.078899 | 0.025342 | 0.046108 | -0.042646 | 0.001403 | 0.054612 | 0.1226 | 0.052844 | 0.12083
911.9844 | 122.0032 | -121.7926 | 0.13733 | 0.14474 | -0.013048 | 0.079572 | 0.011611 | 0.11409 | 0.099318 | -0.021514 | 0.052488 | 0.15706 | 0.055298 | -0.10637 | -0.006702 | 0.009486 | -0.07469 | -0.026063 | 0.17221 | 0.014418 | 0.10704 | 0.039077 | 0.14156 | 0.12678 | 0.005952 | 0.079954 | 0.18452 | 0.082764 | -0.078899 | 0.020764 | 0.036952 | -0.047224 | 0.001403 | 0.05919 | 0.12718 | 0.062 | 0.12999
913.7188 | 122.0947 | -121.7285 | 0.11902 | 0.14017 | -0.017627 | 0.070415 | 0.01619 | 0.11867 | 0.090161 | -0.021514 | 0.047909 | 0.15706 | 0.05072 | -0.10637 | -0.006702 | 0.018642 | -0.07469 | -0.026063 | 0.16763 | 0.009839 | 0.097881 | 0.043656 | 0.14613 | 0.11763 | 0.005952 | 0.075375 | 0.18452 | 0.078186 | -0.078899 | 0.020764 | 0.046108 | -0.047224 | 0.001403 | 0.054611 | 0.1226 | 0.057422 | 0.12541
915.3906 | 121.9666 | -121.7743 | 0.13733 | 0.13559 | -0.022205 | 0.074994 | 0.01619 | 0.10951 | 0.090161 | -0.016936 | 0.052488 | 0.16622 | 0.055298 | -0.11094 | -0.011281 | 0.02322 | -0.07469 | -0.021484 | 0.16305 | 0.005261 | 0.10246 | 0.043656 | 0.13698 | 0.11763 | 0.01053 | 0.079954 | 0.19368 | 0.082764 | -0.083478 | 0.016185 | 0.050686 | -0.047224 | 0.005982 | 0.063769 | 0.12718 | 0.066579 | 0.12999
917.1406 | 121.9437 | -121.7926 | 0.15106 | 0.13559 | -0.008469 | 0.074994 | 0.007033 | 0.11409 | 0.090161 | -0.016936 | 0.052488 | 0.15248 | 0.055298 | -0.11094 | -0.006702 | 0.014064 | -0.079268 | -0.021484 | 0.16305 | 0.018997 | 0.10246 | 0.034499 | 0.14156 | 0.11763 | 0.01053 | 0.079954 | 0.17994 | 0.082764 | -0.083478 | 0.020764 | 0.04153 | -0.051802 | 0.005982 | 0.05919 | 0.13176 | 0.062 | 0.13457
918.875 | 122.0535 | -121.7422 | 0.12817 | 0.14017 | -0.008469 | 0.074994 | 0.011611 | 0.12325 | 0.09474 | -0.026092 | 0.047909 | 0.15706 | 0.055298 | -0.10637 | -0.015859 | 0.02322 | -0.079268 | -0.021484 | 0.16763 | 0.018997 | 0.10246 | 0.039077 | 0.15071 | 0.12221 | 0.001374 | 0.075375 | 0.18452 | 0.082764 | -0.078899 | 0.011607 | 0.050686 | -0.051802 | 0.005982 | 0.063768 | 0.12718 | 0.071157 | 0.13457
920.625 | 122.0718 | -121.7514 | 0.11444 | 0.13559 | -0.017627 | 0.074994 | 0.011611 | 0.11867 | 0.081005 | -0.016936 | 0.052488 | 0.16164 | 0.05072 | -0.10179 | -0.006702 | 0.018642 | -0.065533 | -0.021484 | 0.16305 | 0.009839 | 0.10246 | 0.039077 | 0.14613 | 0.10847 | 0.01053 | 0.079954 | 0.1891 | 0.078186 | -0.07432 | 0.020764 | 0.046108 | -0.038067 | 0.005982 | 0.05919 | 0.11802 | 0.057422 | 0.11625
922.3125 | 122.0947 | -121.7514 | 0.09613 | 0.14017 | -0.022205 | 0.079572 | 0.011611 | 0.11409 | 0.09474 | -0.021514 | 0.052488 | 0.15706 | 0.055298 | -0.11094 | -0.006702 | 0.009486 | -0.070112 | -0.030641 | 0.16763 | 0.005261 | 0.10704 | 0.039077 | 0.14156 | 0.12221 | 0.005952 | 0.079954 | 0.18452 | 0.082764 | -0.083478 | 0.020764 | 0.036952 | -0.042646 | -0.003175 | 0.05919 | 0.1226 | 0.062 | 0.12541
923.9844 | 122.0261 | -121.7468 | 0.13275 | 0.13101 | -0.017627 | 0.074994 | 0.01619 | 0.10951 | 0.090161 | -0.026092 | 0.043331 | 0.15706 | 0.05072 | -0.11094 | -0.002124 | 0.014064 | -0.079268 | -0.026063 | 0.15847 | 0.009839 | 0.10246 | 0.043656 | 0.13698 | 0.11763 | 0.001374 | 0.070797 | 0.18452 | 0.078186 | -0.083478 | 0.025342 | 0.04153 | -0.051802 | 0.001403 | 0.045455 | 0.1226 | 0.052844 | 0.12999
925.7344 | 122.0993 | -121.7606 | 0.12817 | 0.13559 | -0.013048 | 0.079572 | 0.011611 | 0.11867 | 0.090161 | -0.021514 | 0.052488 | 0.16164 | 0.055298 | -0.11094 | -0.006702 | 0.014064 | -0.07469 | -0.016906 | 0.16305 | 0.014418 | 0.10704 | 0.039077 | 0.14613 | 0.11763 | 0.005952 | 0.079954 | 0.1891 | 0.082764 | -0.083478 | 0.020764 | 0.04153 | -0.047224 | 0.01056 | 0.05919 | 0.12718 | 0.062 | 0.12999
927.4688 | 122.0398 | -121.7514 | 0.11444 | 0.13559 | -0.008469 | 0.070415 | 0.011611 | 0.11409 | 0.085583 | -0.021514 | 0.043331 | 0.16164 | 0.046142 | -0.10637 | -0.011281 | 0.018642 | -0.07469 | -0.026063 | 0.16305 | 0.018997 | 0.097881 | 0.039077 | 0.14156 | 0.11305 | 0.005952 | 0.070797 | 0.1891 | 0.073608 | -0.078899 | 0.016185 | 0.046108 | -0.047224 | 0.001403 | 0.054612 | 0.11802 | 0.057423 | 0.12083
929.2031 | 121.962 | -121.7697 | 0.15564 | 0.13559 | -0.008469 | 0.070415 | 0.020768 | 0.11867 | 0.090161 | -0.012357 | 0.057066 | 0.15248 | 0.055298 | -0.11094 | -0.006702 | 0.018642 | -0.07469 | -0.030641 | 0.16305 | 0.018997 | 0.097881 | 0.048234 | 0.14613 | 0.11763 | 0.015109 | 0.084532 | 0.17994 | 0.082764 | -0.083478 | 0.020764 | 0.046108 | -0.047224 | -0.003175 | 0.063768 | 0.13176 | 0.062 | 0.12999
930.9531 | 122.0352 | -121.756 | 0.11444 | 0.13101 | -0.017627 | 0.074994 | 0.01619 | 0.11867 | 0.09474 | -0.021514 | 0.043331 | 0.15706 | 0.046142 | -0.11094 | -0.002124 | 0.014064 | -0.079268 | -0.026063 | 0.15847 | 0.009839 | 0.10246 | 0.043656 | 0.14613 | 0.12221 | 0.005952 | 0.070797 | 0.18452 | 0.073608 | -0.083478 | 0.025342 | 0.04153 | -0.051802 | 0.001403 | 0.045455 | 0.1226 | 0.048266 | 0.12541
932.7031 | 121.9986 | -121.7834 | 0.13275 | 0.13559 | -0.013048 | 0.079572 | 0.01619 | 0.11867 | 0.090161 | -0.021514 | 0.047909 | 0.15706 | 0.059877 | -0.10637 | -0.011281 | 0.009486 | -0.079268 | -0.026063 | 0.16305 | 0.014418 | 0.10704 | 0.043656 | 0.14613 | 0.11763 | 0.005952 | 0.075375 | 0.18452 | 0.087343 | -0.078899 | 0.016185 | 0.036952 | -0.051802 | 0.001403 | 0.05919 | 0.12718 | 0.071158 | 0.13915
934.4531 | 122.0627 | -121.7514 | 0.13275 | 0.13559 | -0.013048 | 0.079572 | 0.007033 | 0.11867 | 0.090161 | -0.016936 | 0.047909 | 0.15248 | 0.046142 | -0.11094 | -0.006702 | 0.014064 | -0.070112 | -0.026063 | 0.16305 | 0.014418 | 0.10704 | 0.034499 | 0.14613 | 0.11763 | 0.01053 | 0.075375 | 0.17994 | 0.073608 | -0.083478 | 0.020764 | 0.04153 | -0.042646 | 0.001403 | 0.054611 | 0.11802 | 0.052844 | 0.11625
936.125 | 121.962 | -121.7834 | 0.16479 | 0.14017 | -0.013048 | 0.074994 | 0.011611 | 0.10951 | 0.090161 | -0.021514 | 0.052488 | 0.15248 | 0.046142 | -0.10637 | -0.006702 | 0.014064 | -0.079268 | -0.026063 | 0.16763 | 0.014418 | 0.10246 | 0.039077 | 0.13698 | 0.11763 | 0.005952 | 0.079954 | 0.17994 | 0.073608 | -0.078899 | 0.020764 | 0.04153 | -0.051802 | 0.001403 | 0.05919 | 0.13176 | 0.052844 | 0.12541
937.875 | 121.9528 | -121.7972 | 0.14648 | 0.14017 | -0.008469 | 0.074994 | 0.011611 | 0.11867 | 0.085583 | -0.016936 | 0.057066 | 0.15248 | 0.05072 | -0.11094 | -0.006702 | 0.018642 | -0.07469 | -0.026063 | 0.16763 | 0.018997 | 0.10246 | 0.039077 | 0.14613 | 0.11305 | 0.01053 | 0.084532 | 0.17994 | 0.078186 | -0.083478 | 0.020764 | 0.046108 | -0.047224 | 0.001403 | 0.063768 | 0.13176 | 0.057422 | 0.12541
939.5469 | 121.9711 | -121.8063 | 0.15106 | 0.12643 | -0.013048 | 0.079572 | 0.011611 | 0.11409 | 0.099318 | -0.026092 | 0.052488 | 0.15706 | 0.046142 | -0.11094 | -0.015859 | 0.014064 | -0.070112 | -0.026063 | 0.1539 | 0.014418 | 0.10704 | 0.039077 | 0.14156 | 0.12678 | 0.001374 | 0.079954 | 0.18452 | 0.073608 | -0.083478 | 0.011607 | 0.04153 | -0.042646 | 0.001403 | 0.068347 | 0.1226 | 0.062001 | 0.11625
941.2969 | 122.0901 | -121.7468 | 0.12817 | 0.13559 | -0.013048 | 0.070415 | 0.007033 | 0.11409 | 0.099318 | -0.012357 | 0.052488 | 0.15706 | 0.055298 | -0.11094 | -0.006702 | 0.009486 | -0.070112 | -0.021484 | 0.16305 | 0.014418 | 0.097881 | 0.034499 | 0.14156 | 0.12678 | 0.015109 | 0.079954 | 0.18452 | 0.082764 | -0.083478 | 0.020764 | 0.036952 | -0.042646 | 0.005982 | 0.05919 | 0.1226 | 0.062 | 0.12541
943.0469 | 122.0306 | -121.7697 | 0.1236 | 0.14017 | -0.013048 | 0.074994 | 0.011611 | 0.12325 | 0.085583 | -0.016936 | 0.052488 | 0.15248 | 0.055298 | -0.10637 | -0.006702 | 0.009486 | -0.070112 | -0.030641 | 0.16763 | 0.014418 | 0.10246 | 0.039077 | 0.15071 | 0.11305 | 0.01053 | 0.079954 | 0.17994 | 0.082764 | -0.078899 | 0.020764 | 0.036952 | -0.042646 | -0.003175 | 0.05919 | 0.1226 | 0.062 | 0.12541
944.7344 | 122.0627 | -121.7239 | 0.11444 | 0.14474 | -0.017627 | 0.079572 | 0.007033 | 0.11867 | 0.09474 | -0.016936 | 0.043331 | 0.16164 | 0.05072 | -0.10637 | -0.002124 | 0.014064 | -0.07469 | -0.021484 | 0.17221 | 0.009839 | 0.10704 | 0.034499 | 0.14613 | 0.12221 | 0.01053 | 0.070797 | 0.1891 | 0.078186 | -0.078899 | 0.025342 | 0.04153 | -0.047224 | 0.005982 | 0.045455 | 0.11802 | 0.052844 | 0.12541
946.4844 | 122.0627 | -121.7468 | 0.11902 | 0.14474 | -0.013048 | 0.074994 | 0.011611 | 0.11409 | 0.090161 | -0.021514 | 0.047909 | 0.15706 | 0.055298 | -0.1201 | -0.002124 | 0.02322 | -0.070112 | -0.021484 | 0.17221 | 0.014418 | 0.10246 | 0.039077 | 0.14156 | 0.11763 | 0.005952 | 0.075375 | 0.18452 | 0.082764 | -0.092637 | 0.025342 | 0.050686 | -0.042646 | 0.005982 | 0.050033 | 0.11802 | 0.057422 | 0.12541
948.2344 | 121.9757 | -121.7972 | 0.13733 | 0.13559 | -0.008469 | 0.074994 | 0.011611 | 0.11867 | 0.09474 | -0.016936 | 0.052488 | 0.15248 | 0.055298 | -0.11094 | -0.011281 | 0.014064 | -0.07469 | -0.026063 | 0.16305 | 0.018997 | 0.10246 | 0.039077 | 0.14613 | 0.12221 | 0.01053 | 0.079954 | 0.17994 | 0.082764 | -0.083478 | 0.016185 | 0.04153 | -0.047224 | 0.001403 | 0.063769 | 0.12718 | 0.066579 | 0.12999
949.9688 | 122.0581 | -121.7422 | 0.10529 | 0.13559 | -0.00389 | 0.079572 | 0.011611 | 0.12325 | 0.090161 | -0.016936 | 0.061645 | 0.15706 | 0.05072 | -0.10637 | -0.011281 | 0.014064 | -0.065533 | -0.026063 | 0.16305 | 0.023576 | 0.10704 | 0.039077 | 0.15071 | 0.11763 | 0.01053 | 0.089111 | 0.18452 | 0.078186 | -0.078899 | 0.016185 | 0.04153 | -0.038067 | 0.001403 | 0.072926 | 0.12718 | 0.062001 | 0.11625
951.6406 | 121.9849 | -121.7834 | 0.14191 | 0.13559 | -0.00389 | 0.070415 | 0.011611 | 0.11867 | 0.09474 | -0.012357 | 0.043331 | 0.16164 | 0.05072 | -0.10637 | -0.011281 | 0.014064 | -0.070112 | -0.021484 | 0.16305 | 0.023576 | 0.097881 | 0.039077 | 0.14613 | 0.12221 | 0.015109 | 0.070797 | 0.1891 | 0.078186 | -0.078899 | 0.016185 | 0.04153 | -0.042646 | 0.005982 | 0.054612 | 0.11344 | 0.062001 | 0.12083
953.4062 | 122.0306 | -121.7789 | 0.12817 | 0.13559 | 0.000689 | 0.079572 | 0.011611 | 0.11409 | 0.090161 | -0.021514 | 0.047909 | 0.15248 | 0.05072 | -0.11552 | -0.006702 | 0.009486 | -0.07469 | -0.021484 | 0.16305 | 0.028155 | 0.10704 | 0.039077 | 0.14156 | 0.11763 | 0.005952 | 0.075375 | 0.17994 | 0.078186 | -0.088057 | 0.020764 | 0.036952 | -0.047224 | 0.005982 | 0.054611 | 0.1226 | 0.057422 | 0.12541
955.0781 | 122.0215 | -121.7377 | 0.1236 | 0.14017 | -0.008469 | 0.079572 | 0.011611 | 0.11409 | 0.09474 | -0.026092 | 0.047909 | 0.15706 | 0.05072 | -0.11552 | -0.002124 | 0.009486 | -0.070112 | -0.026063 | 0.16763 | 0.018997 | 0.10704 | 0.039077 | 0.14156 | 0.12221 | 0.001374 | 0.075375 | 0.18452 | 0.078186 | -0.088057 | 0.025342 | 0.036952 | -0.042646 | 0.001403 | 0.050033 | 0.11802 | 0.052844 | 0.12083
956.8281 | 121.9803 | -121.8155 | 0.14191 | 0.14017 | -0.008469 | 0.079572 | 0.011611 | 0.11867 | 0.1039 | -0.021514 | 0.057066 | 0.15706 | 0.05072 | -0.10637 | -0.002124 | 0.014064 | -0.060955 | -0.026063 | 0.16763 | 0.018997 | 0.10704 | 0.039077 | 0.14613 | 0.13136 | 0.005952 | 0.084532 | 0.18452 | 0.078186 | -0.078899 | 0.025342 | 0.04153 | -0.033489 | 0.001403 | 0.05919 | 0.11802 | 0.052844 | 0.11167
958.5938 | 122.0032 | -121.7697 | 0.13275 | 0.13559 | -0.00389 | 0.079572 | 0.011611 | 0.11409 | 0.090161 | -0.016936 | 0.043331 | 0.16622 | 0.05072 | -0.11094 | -0.006702 | 0.009486 | -0.070112 | -0.016906 | 0.16305 | 0.023576 | 0.10704 | 0.039077 | 0.14156 | 0.11763 | 0.01053 | 0.070797 | 0.19368 | 0.078186 | -0.083478 | 0.020764 | 0.036952 | -0.042646 | 0.01056 | 0.050033 | 0.11344 | 0.057422 | 0.12083
960.2656 | 121.9528 | -121.8063 | 0.14648 | 0.14017 | -0.017627 | 0.079572 | 0.011611 | 0.11867 | 0.09474 | -0.021514 | 0.057066 | 0.15248 | 0.05072 | -0.11094 | -0.002124 | 0.027798 | -0.070112 | -0.012328 | 0.16763 | 0.009839 | 0.10704 | 0.039077 | 0.14613 | 0.12221 | 0.005952 | 0.084532 | 0.17994 | 0.078186 | -0.083478 | 0.025342 | 0.055264 | -0.042646 | 0.015138 | 0.05919 | 0.12718 | 0.052844 | 0.12083
962 | 122.0261 | -121.788 | 0.12817 | 0.13559 | -0.008469 | 0.074994 | 0.01619 | 0.11867 | 0.09474 | -0.016936 | 0.047909 | 0.16164 | 0.05072 | -0.11552 | -0.006702 | 0.009486 | -0.07469 | -0.012328 | 0.16305 | 0.018997 | 0.10246 | 0.043656 | 0.14613 | 0.12221 | 0.01053 | 0.075375 | 0.1891 | 0.078186 | -0.088057 | 0.020764 | 0.036952 | -0.047224 | 0.015138 | 0.054611 | 0.1226 | 0.057422 | 0.12541
963.7031 | 121.9574 | -121.8109 | 0.16937 | 0.14017 | -0.008469 | 0.074994 | 0.011611 | 0.11409 | 0.085583 | -0.026092 | 0.043331 | 0.15706 | 0.041563 | -0.11094 | -0.006702 | 0.018642 | -0.065533 | -0.016906 | 0.16763 | 0.018997 | 0.10246 | 0.039077 | 0.14156 | 0.11305 | 0.001374 | 0.070797 | 0.18452 | 0.069029 | -0.083478 | 0.020764 | 0.046108 | -0.038067 | 0.01056 | 0.050033 | 0.10886 | 0.048265 | 0.1071
965.4375 | 122.0444 | -121.7743 | 0.1236 | 0.14017 | -0.00389 | 0.074994 | 0.007033 | 0.11867 | 0.099318 | -0.016936 | 0.052488 | 0.15706 | 0.05072 | -0.11094 | -0.006702 | 0.014064 | -0.07469 | -0.021484 | 0.16763 | 0.023576 | 0.10246 | 0.034499 | 0.14613 | 0.12678 | 0.01053 | 0.079954 | 0.18452 | 0.078186 | -0.083478 | 0.020764 | 0.04153 | -0.047224 | 0.005982 | 0.05919 | 0.12718 | 0.057422 | 0.12541
967.1094 | 121.9849 | -121.8063 | 0.15106 | 0.14017 | -0.008469 | 0.074994 | 0.011611 | 0.11867 | 0.09474 | -0.021514 | 0.047909 | 0.15706 | 0.05072 | -0.10637 | -0.002124 | 0.014064 | -0.060955 | -0.021484 | 0.16763 | 0.018997 | 0.10246 | 0.039077 | 0.14613 | 0.12221 | 0.005952 | 0.075375 | 0.18452 | 0.078186 | -0.078899 | 0.025342 | 0.04153 | -0.033489 | 0.005982 | 0.050033 | 0.10886 | 0.052844 | 0.11167
968.8438 | 121.9345 | -121.7743 | 0.13733 | 0.13559 | -0.00389 | 0.084151 | 0.002454 | 0.11867 | 0.090161 | -0.016936 | 0.043331 | 0.15706 | 0.046142 | -0.10179 | -0.011281 | 0.018642 | -0.079268 | -0.026063 | 0.16305 | 0.023576 | 0.11162 | 0.02992 | 0.14613 | 0.11763 | 0.01053 | 0.070797 | 0.18452 | 0.073608 | -0.07432 | 0.016185 | 0.046108 | -0.051802 | 0.001403 | 0.054612 | 0.1226 | 0.057423 | 0.12541
970.5781 | 122.0444 | -121.7651 | 0.1236 | 0.14474 | -0.008469 | 0.079572 | 0.011611 | 0.11867 | 0.090161 | -0.016936 | 0.052488 | 0.15248 | 0.055298 | -0.10637 | -0.011281 | 0.014064 | -0.07469 | -0.016906 | 0.17221 | 0.018997 | 0.10704 | 0.039077 | 0.14613 | 0.11763 | 0.01053 | 0.079954 | 0.17994 | 0.082764 | -0.078899 | 0.016185 | 0.04153 | -0.047224 | 0.01056 | 0.063769 | 0.12718 | 0.066579 | 0.12999
972.3125 | 121.9894 | -121.7789 | 0.12817 | 0.14474 | 0.000689 | 0.074994 | 0.01619 | 0.12325 | 0.090161 | -0.021514 | 0.052488 | 0.15706 | 0.05072 | -0.10637 | -0.006702 | 0.018642 | -0.070112 | -0.016906 | 0.17221 | 0.028155 | 0.10246 | 0.043656 | 0.15071 | 0.11763 | 0.005952 | 0.079954 | 0.18452 | 0.078186 | -0.078899 | 0.020764 | 0.046108 | -0.042646 | 0.01056 | 0.05919 | 0.1226 | 0.057422 | 0.12083
973.9844 | 121.9894 | -121.7834 | 0.16937 | 0.14474 | -0.008469 | 0.074994 | 0.01619 | 0.12325 | 0.09474 | -0.021514 | 0.047909 | 0.15706 | 0.055298 | -0.10637 | -0.002124 | 0.009486 | -0.07469 | -0.016906 | 0.17221 | 0.018997 | 0.10246 | 0.043656 | 0.15071 | 0.12221 | 0.005952 | 0.075375 | 0.18452 | 0.082764 | -0.078899 | 0.025342 | 0.036952 | -0.047224 | 0.01056 | 0.050033 | 0.1226 | 0.057422 | 0.12999
975.7188 | 122.0581 | -121.7789 | 0.1236 | 0.13559 | -0.008469 | 0.074994 | 0.002454 | 0.12325 | 0.09474 | -0.026092 | 0.047909 | 0.16164 | 0.05072 | -0.10637 | -0.006702 | 0.018642 | -0.079268 | -0.021484 | 0.16305 | 0.018997 | 0.10246 | 0.02992 | 0.15071 | 0.12221 | 0.001374 | 0.075375 | 0.1891 | 0.078186 | -0.078899 | 0.020764 | 0.046108 | -0.051802 | 0.005982 | 0.054611 | 0.12718 | 0.057422 | 0.12999
977.4688 | 122.0993 | -121.7697 | 0.10986 | 0.13559 | -0.008469 | 0.079572 | 0.002454 | 0.10951 | 0.09474 | -0.016936 | 0.052488 | 0.15248 | 0.059877 | -0.1201 | -0.006702 | 0.014064 | -0.070112 | -0.030641 | 0.16305 | 0.018997 | 0.10704 | 0.02992 | 0.13698 | 0.12221 | 0.01053 | 0.079954 | 0.17994 | 0.087343 | -0.092637 | 0.020764 | 0.04153 | -0.042646 | -0.003175 | 0.05919 | 0.1226 | 0.066579 | 0.12999
979.1406 | 121.9986 | -121.8063 | 0.1236 | 0.13559 | -0.008469 | 0.074994 | 0.01619 | 0.12325 | 0.09474 | -0.007779 | 0.052488 | 0.15248 | 0.05072 | -0.11094 | -0.002124 | 0.009486 | -0.079268 | -0.012328 | 0.16305 | 0.018997 | 0.10246 | 0.043656 | 0.15071 | 0.12221 | 0.019687 | 0.079954 | 0.17994 | 0.078186 | -0.083478 | 0.025342 | 0.036952 | -0.051802 | 0.015138 | 0.054612 | 0.13176 | 0.052844 | 0.12999
980.8906 | 122.0078 | -121.788 | 0.13733 | 0.13559 | -0.008469 | 0.074994 | 0.01619 | 0.12325 | 0.09474 | -0.021514 | 0.057066 | 0.17079 | 0.05072 | -0.10637 | 0.002454 | 0.014064 | -0.065533 | -0.030641 | 0.16305 | 0.018997 | 0.10246 | 0.043656 | 0.15071 | 0.12221 | 0.005952 | 0.084532 | 0.19826 | 0.078186 | -0.078899 | 0.02992 | 0.04153 | -0.038067 | -0.003175 | 0.054612 | 0.1226 | 0.048266 | 0.11625
982.5781 | 122.0673 | -121.7514 | 0.10986 | 0.14017 | -0.008469 | 0.074994 | 0.007033 | 0.11867 | 0.09474 | -0.021514 | 0.047909 | 0.16164 | 0.05072 | -0.11094 | -0.011281 | 0.018642 | -0.07469 | -0.026063 | 0.16763 | 0.018997 | 0.10246 | 0.034499 | 0.14613 | 0.12221 | 0.005952 | 0.075375 | 0.1891 | 0.078186 | -0.083478 | 0.016185 | 0.046108 | -0.047224 | 0.001403 | 0.05919 | 0.1226 | 0.062001 | 0.12541
984.3125 | 122.0032 | -121.7697 | 0.14191 | 0.13559 | -0.008469 | 0.079572 | 0.020768 | 0.10951 | 0.09474 | -0.021514 | 0.052488 | 0.16164 | 0.055298 | -0.10637 | -0.002124 | 0.014064 | -0.079268 | -0.026063 | 0.16305 | 0.018997 | 0.10704 | 0.048234 | 0.13698 | 0.12221 | 0.005952 | 0.079954 | 0.1891 | 0.082764 | -0.078899 | 0.025342 | 0.04153 | -0.051802 | 0.001403 | 0.054612 | 0.13176 | 0.057422 | 0.13457
985.9844 | 122.0078 | -121.7926 | 0.12817 | 0.14017 | -0.013048 | 0.079572 | 0.01619 | 0.11867 | 0.09474 | -0.016936 | 0.052488 | 0.16164 | 0.055298 | -0.10637 | 0.002454 | 0.014064 | -0.070112 | -0.016906 | 0.16763 | 0.014418 | 0.10704 | 0.043656 | 0.14613 | 0.12221 | 0.01053 | 0.079954 | 0.1891 | 0.082764 | -0.078899 | 0.02992 | 0.04153 | -0.042646 | 0.01056 | 0.050034 | 0.1226 | 0.052844 | 0.12541
987.7188 | 122.081 | -121.7468 | 0.10529 | 0.14017 | -0.013048 | 0.074994 | 0.007033 | 0.10951 | 0.090161 | -0.016936 | 0.052488 | 0.15248 | 0.055298 | -0.11552 | -0.006702 | 0.014064 | -0.07469 | -0.021484 | 0.16763 | 0.014418 | 0.10246 | 0.034499 | 0.13698 | 0.11763 | 0.01053 | 0.079954 | 0.17994 | 0.082764 | -0.088057 | 0.020764 | 0.04153 | -0.047224 | 0.005982 | 0.05919 | 0.12718 | 0.062 | 0.12999
989.3906 | 122.0444 | -121.7697 | 0.10986 | 0.13559 | -0.00389 | 0.074994 | 0.01619 | 0.11409 | 0.090161 | -0.021514 | 0.047909 | 0.15706 | 0.055298 | -0.10179 | -0.011281 | 0.014064 | -0.065533 | -0.030641 | 0.16305 | 0.023576 | 0.10246 | 0.043656 | 0.14156 | 0.11763 | 0.005952 | 0.075375 | 0.18452 | 0.082764 | -0.07432 | 0.016185 | 0.04153 | -0.038067 | -0.003175 | 0.05919 | 0.11344 | 0.066579 | 0.12083
991.0625 | 122.0947 | -121.7743 | 0.1236 | 0.13559 | -0.008469 | 0.074994 | 0.011611 | 0.11409 | 0.09474 | -0.016936 | 0.052488 | 0.15248 | 0.055298 | -0.11094 | -0.002124 | 0.009486 | -0.07469 | -0.021484 | 0.16305 | 0.018997 | 0.10246 | 0.039077 | 0.14156 | 0.12221 | 0.01053 | 0.079954 | 0.17994 | 0.082764 | -0.083478 | 0.025342 | 0.036952 | -0.047224 | 0.005982 | 0.054612 | 0.12718 | 0.057422 | 0.12999
992.8125 | 122.0078 | -121.756 | 0.13733 | 0.14017 | -0.013048 | 0.074994 | 0.01619 | 0.12325 | 0.09474 | -0.021514 | 0.052488 | 0.16164 | 0.055298 | -0.11552 | -0.002124 | 0.014064 | -0.079268 | -0.026063 | 0.16763 | 0.014418 | 0.10246 | 0.043656 | 0.15071 | 0.12221 | 0.005952 | 0.079954 | 0.1891 | 0.082764 | -0.088057 | 0.025342 | 0.04153 | -0.051802 | 0.001403 | 0.054612 | 0.13176 | 0.057422 | 0.13457
994.5469 | 122.0215 | -121.7743 | 0.11902 | 0.13559 | -0.013048 | 0.074994 | 0.011611 | 0.12325 | 0.099318 | -0.016936 | 0.052488 | 0.15706 | 0.059877 | -0.10179 | -0.011281 | 0.018642 | -0.083847 | -0.021484 | 0.16305 | 0.014418 | 0.10246 | 0.039077 | 0.15071 | 0.12678 | 0.01053 | 0.079954 | 0.18452 | 0.087343 | -0.07432 | 0.016185 | 0.046108 | -0.056381 | 0.005982 | 0.063769 | 0.13634 | 0.071158 | 0.14372
996.2969 | 122.0123 | -121.7972 | 0.13275 | 0.14017 | -0.013048 | 0.079572 | 0.01619 | 0.12325 | 0.099318 | -0.016936 | 0.052488 | 0.15248 | 0.055298 | -0.11552 | -0.002124 | 0.02322 | -0.079268 | -0.026063 | 0.16763 | 0.014418 | 0.10704 | 0.043656 | 0.15071 | 0.12678 | 0.01053 | 0.079954 | 0.17994 | 0.082764 | -0.088057 | 0.025342 | 0.050686 | -0.051802 | 0.001403 | 0.054612 | 0.13176 | 0.057422 | 0.13457
998.0312 | 122.0078 | -121.7926 | 0.13733 | 0.14017 | -0.008469 | 0.079572 | 0.020768 | 0.11409 | 0.090161 | -0.012357 | 0.047909 | 0.16622 | 0.055298 | -0.11094 | -0.015859 | 0.009486 | -0.07469 | -0.021484 | 0.16763 | 0.018997 | 0.10704 | 0.048234 | 0.14156 | 0.11763 | 0.015109 | 0.075375 | 0.19368 | 0.082764 | -0.083478 | 0.011607 | 0.036952 | -0.047224 | 0.005982 | 0.063768 | 0.1226 | 0.071157 | 0.12999
999.7812 | 122.0123 | -121.7834 | 0.1236 | 0.14474 | -0.00389 | 0.065837 | 0.01619 | 0.11867 | 0.090161 | -0.016936 | 0.052488 | 0.15248 | 0.05072 | -0.11094 | -0.006702 | 0.018642 | -0.079268 | -0.026063 | 0.17221 | 0.023576 | 0.093303 | 0.043656 | 0.14613 | 0.11763 | 0.01053 | 0.079954 | 0.17994 | 0.078186 | -0.083478 | 0.020764 | 0.046108 | -0.051802 | 0.001403 | 0.05919 | 0.13176 | 0.057422 | 0.12999
1001.5312 | 122.049 | -121.7743 | 0.13275 | 0.14474 | -0.008469 | 0.084151 | 0.01619 | 0.11867 | 0.09474 | -0.016936 | 0.057066 | 0.15248 | 0.059877 | -0.10637 | -0.006702 | 0.018642 | -0.065533 | -0.016906 | 0.17221 | 0.018997 | 0.11162 | 0.043656 | 0.14613 | 0.12221 | 0.01053 | 0.084532 | 0.17994 | 0.087343 | -0.078899 | 0.020764 | 0.046108 | -0.038067 | 0.01056 | 0.063768 | 0.1226 | 0.066579 | 0.12541
1003.2188 | 122.0078 | -121.8109 | 0.13733 | 0.14017 | -0.008469 | 0.074994 | 0.011611 | 0.12325 | 0.09474 | -0.016936 | 0.057066 | 0.16164 | 0.059877 | -0.11552 | -0.011281 | 0.014064 | -0.079268 | -0.016906 | 0.16763 | 0.018997 | 0.10246 | 0.039077 | 0.15071 | 0.12221 | 0.01053 | 0.084532 | 0.1891 | 0.087343 | -0.088057 | 0.016185 | 0.04153 | -0.051802 | 0.01056 | 0.068347 | 0.13633 | 0.071158 | 0.13915
1004.9531 | 122.0535 | -121.7926 | 0.11444 | 0.13101 | -0.013048 | 0.079572 | 0.007033 | 0.11409 | 0.099318 | -0.012357 | 0.052488 | 0.16164 | 0.05072 | -0.1201 | -0.006702 | 0.018642 | -0.07469 | -0.021484 | 0.15847 | 0.014418 | 0.10704 | 0.034499 | 0.14156 | 0.12678 | 0.015109 | 0.079954 | 0.1891 | 0.078186 | -0.092637 | 0.020764 | 0.046108 | -0.047224 | 0.005982 | 0.05919 | 0.12718 | 0.057422 | 0.12541
1006.625 | 122.081 | -121.7514 | 0.1236 | 0.14017 | -0.008469 | 0.074994 | 0.007033 | 0.11867 | 0.085583 | -0.016936 | 0.047909 | 0.16164 | 0.046142 | -0.11094 | -0.015859 | 0.018642 | -0.07469 | -0.026063 | 0.16763 | 0.018997 | 0.10246 | 0.034499 | 0.14613 | 0.11305 | 0.01053 | 0.075375 | 0.1891 | 0.073608 | -0.083478 | 0.011607 | 0.046108 | -0.047224 | 0.001403 | 0.063768 | 0.1226 | 0.062001 | 0.12083
1008.3125 | 122.1222 | -121.756 | 0.11902 | 0.14474 | -0.013048 | 0.074994 | 0.002454 | 0.11409 | 0.09474 | -0.021514 | 0.057066 | 0.16164 | 0.05072 | -0.11094 | -0.006702 | 0.014064 | -0.07469 | -0.021484 | 0.17221 | 0.014418 | 0.10246 | 0.02992 | 0.14156 | 0.12221 | 0.005952 | 0.084532 | 0.1891 | 0.078186 | -0.083478 | 0.020764 | 0.04153 | -0.047224 | 0.005982 | 0.063768 | 0.13176 | 0.057422 | 0.12541
1010.0469 | 122.0673 | -121.7422 | 0.10529 | 0.13559 | -0.017627 | 0.074994 | 0.007033 | 0.11409 | 0.090161 | -0.016936 | 0.057066 | 0.15706 | 0.055298 | -0.10179 | -0.002124 | 0.009486 | -0.070112 | -0.012328 | 0.16305 | 0.009839 | 0.10246 | 0.034499 | 0.14156 | 0.11763 | 0.01053 | 0.084532 | 0.18452 | 0.082764 | -0.07432 | 0.025342 | 0.036952 | -0.042646 | 0.015138 | 0.05919 | 0.12718 | 0.057422 | 0.12541
1011.7812 | 122.0673 | -121.7743 | 0.11444 | 0.14017 | -0.013048 | 0.074994 | 0.007033 | 0.10951 | 0.1039 | -0.016936 | 0.052488 | 0.15706 | 0.05072 | -0.10637 | -0.011281 | 0.018642 | -0.07469 | -0.016906 | 0.16763 | 0.014418 | 0.10246 | 0.034499 | 0.13698 | 0.13136 | 0.01053 | 0.079954 | 0.18452 | 0.078186 | -0.078899 | 0.016185 | 0.046108 | -0.047224 | 0.01056 | 0.063769 | 0.12718 | 0.062001 | 0.12541
1013.4688 | 122.0306 | -121.7743 | 0.11902 | 0.14474 | -0.008469 | 0.074994 | 0.007033 | 0.11409 | 0.099318 | -0.012357 | 0.052488 | 0.15706 | 0.05072 | -0.10637 | 0.002454 | 0.014064 | -0.070112 | -0.026063 | 0.17221 | 0.018997 | 0.10246 | 0.034499 | 0.14156 | 0.12678 | 0.015109 | 0.079954 | 0.18452 | 0.078186 | -0.078899 | 0.02992 | 0.04153 | -0.042646 | 0.001403 | 0.050034 | 0.1226 | 0.048266 | 0.12083
1015.2031 | 121.994 | -121.7743 | 0.14648 | 0.14017 | -0.013048 | 0.074994 | 0.011611 | 0.12782 | 0.099318 | -0.012357 | 0.057066 | 0.1479 | 0.05072 | -0.11094 | -0.006702 | 0.018642 | -0.065533 | -0.021484 | 0.16763 | 0.014418 | 0.10246 | 0.039077 | 0.15529 | 0.12678 | 0.015109 | 0.084532 | 0.17536 | 0.078186 | -0.083478 | 0.020764 | 0.046108 | -0.038067 | 0.005982 | 0.063768 | 0.1226 | 0.057422 | 0.11625
1016.9375 | 122.0673 | -121.7789 | 0.1236 | 0.13559 | -0.008469 | 0.070415 | 0.007033 | 0.10951 | 0.090161 | -0.026092 | 0.052488 | 0.15248 | 0.055298 | -0.10637 | -0.002124 | 0.009486 | -0.07469 | -0.021484 | 0.16305 | 0.018997 | 0.097881 | 0.034499 | 0.13698 | 0.11763 | 0.001374 | 0.079954 | 0.17994 | 0.082764 | -0.078899 | 0.025342 | 0.036952 | -0.047224 | 0.005982 | 0.054612 | 0.12718 | 0.057422 | 0.12999
1018.6875 | 122.0078 | -121.7697 | 0.13275 | 0.14017 | -0.008469 | 0.074994 | 0.007033 | 0.11867 | 0.099318 | -0.016936 | 0.047909 | 0.1479 | 0.05072 | -0.10637 | -0.011281 | 0.018642 | -0.079268 | -0.016906 | 0.16763 | 0.018997 | 0.10246 | 0.034499 | 0.14613 | 0.12678 | 0.01053 | 0.075375 | 0.17536 | 0.078186 | -0.078899 | 0.016185 | 0.046108 | -0.051802 | 0.01056 | 0.05919 | 0.12718 | 0.062001 | 0.12999
1020.4375 | 122.0444 | -121.788 | 0.12817 | 0.13559 | -0.008469 | 0.074994 | 0.011611 | 0.12325 | 0.09474 | -0.021514 | 0.043331 | 0.15706 | 0.055298 | -0.11094 | -0.011281 | 0.004908 | -0.07469 | -0.021484 | 0.16305 | 0.018997 | 0.10246 | 0.039077 | 0.15071 | 0.12221 | 0.005952 | 0.070797 | 0.18452 | 0.082764 | -0.083478 | 0.016185 | 0.032374 | -0.047224 | 0.005982 | 0.054612 | 0.11802 | 0.066579 | 0.12999
1022.125 | 122.0764 | -121.7606 | 0.11902 | 0.13101 | -0.017627 | 0.074994 | 0.007033 | 0.11867 | 0.09474 | -0.016936 | 0.057066 | 0.15706 | 0.05072 | -0.11094 | -0.015859 | 0.018642 | -0.079268 | -0.026063 | 0.15847 | 0.009839 | 0.10246 | 0.034499 | 0.14613 | 0.12221 | 0.01053 | 0.084532 | 0.18452 | 0.078186 | -0.083478 | 0.011607 | 0.046108 | -0.051802 | 0.001403 | 0.072925 | 0.13633 | 0.066579 | 0.12999
1023.875 | 121.9711 | -121.8201 | 0.16022 | 0.14017 | -0.008469 | 0.070415 | 0.01619 | 0.11867 | 0.09474 | -0.026092 | 0.047909 | 0.15706 | 0.059877 | -0.11552 | -0.002124 | 0.02322 | -0.079268 | -0.026063 | 0.16763 | 0.018997 | 0.097881 | 0.043656 | 0.14613 | 0.12221 | 0.001374 | 0.075375 | 0.18452 | 0.087343 | -0.088057 | 0.025342 | 0.050686 | -0.051802 | 0.001403 | 0.050033 | 0.12718 | 0.062001 | 0.13915
1025.5469 | 122.0856 | -121.7743 | 0.09613 | 0.14474 | -0.013048 | 0.070415 | 0.01619 | 0.10951 | 0.09474 | -0.021514 | 0.052488 | 0.1479 | 0.055298 | -0.11552 | -0.011281 | 0.014064 | -0.07469 | -0.026063 | 0.17221 | 0.014418 | 0.097881 | 0.043656 | 0.13698 | 0.12221 | 0.005952 | 0.079954 | 0.17536 | 0.082764 | -0.088057 | 0.016185 | 0.04153 | -0.047224 | 0.001403 | 0.063769 | 0.12718 | 0.066579 | 0.12999
1027.2812 | 121.9849 | -121.8109 | 0.15564 | 0.14017 | -0.017627 | 0.079572 | 0.011611 | 0.12782 | 0.090161 | -0.016936 | 0.047909 | 0.16164 | 0.05072 | -0.10637 | -0.015859 | 0.009486 | -0.079268 | -0.026063 | 0.16763 | 0.009839 | 0.10704 | 0.039077 | 0.15529 | 0.11763 | 0.01053 | 0.075375 | 0.1891 | 0.078186 | -0.078899 | 0.011607 | 0.036952 | -0.051802 | 0.001403 | 0.063768 | 0.12718 | 0.066579 | 0.12999
1028.9531 | 122.0947 | -121.7834 | 0.13733 | 0.14017 | -0.00389 | 0.079572 | 0.011611 | 0.11867 | 0.099318 | -0.016936 | 0.057066 | 0.15706 | 0.05072 | -0.10179 | -0.006702 | 0.018642 | -0.083847 | -0.030641 | 0.16763 | 0.023576 | 0.10704 | 0.039077 | 0.14613 | 0.12678 | 0.01053 | 0.084532 | 0.18452 | 0.078186 | -0.07432 | 0.020764 | 0.046108 | -0.056381 | -0.003175 | 0.063768 | 0.14091 | 0.057422 | 0.13457
1030.6875 | 122.0764 | -121.7697 | 0.10071 | 0.13559 | -0.008469 | 0.070415 | 0.011611 | 0.11409 | 0.09474 | -0.021514 | 0.057066 | 0.15706 | 0.05072 | -0.11552 | -0.006702 | 0.004908 | -0.083847 | -0.030641 | 0.16305 | 0.018997 | 0.097881 | 0.039077 | 0.14156 | 0.12221 | 0.005952 | 0.084532 | 0.18452 | 0.078186 | -0.088057 | 0.020764 | 0.032374 | -0.056381 | -0.003175 | 0.063768 | 0.14091 | 0.057422 | 0.13457
1032.4219 | 122.0169 | -121.7834 | 0.13275 | 0.14017 | -0.013048 | 0.074994 | 0.01619 | 0.11867 | 0.09474 | -0.016936 | 0.047909 | 0.15706 | 0.05072 | -0.10637 | -0.011281 | 0.009486 | -0.079268 | -0.030641 | 0.16763 | 0.014418 | 0.10246 | 0.043656 | 0.14613 | 0.12221 | 0.01053 | 0.075375 | 0.18452 | 0.078186 | -0.078899 | 0.016185 | 0.036952 | -0.051802 | -0.003175 | 0.05919 | 0.12718 | 0.062001 | 0.12999
1034.1562 | 122.0123 | -121.7926 | 0.13275 | 0.13101 | -0.00389 | 0.070415 | 0.007033 | 0.10493 | 0.09474 | -0.016936 | 0.052488 | 0.15248 | 0.055298 | -0.11094 | -0.002124 | 0.018642 | -0.079268 | -0.035219 | 0.15847 | 0.023576 | 0.097881 | 0.034499 | 0.1324 | 0.12221 | 0.01053 | 0.079954 | 0.17994 | 0.082764 | -0.083478 | 0.025342 | 0.046108 | -0.051802 | -0.007753 | 0.054612 | 0.13176 | 0.057422 | 0.13457
1035.9062 | 122.0306 | -121.7926 | 0.14191 | 0.13559 | -0.00389 | 0.074994 | 0.01619 | 0.12325 | 0.099318 | -0.021514 | 0.052488 | 0.16164 | 0.055298 | -0.10637 | -0.011281 | 0.02322 | -0.079268 | -0.030641 | 0.16305 | 0.023576 | 0.10246 | 0.043656 | 0.15071 | 0.12678 | 0.005952 | 0.079954 | 0.1891 | 0.082764 | -0.078899 | 0.016185 | 0.050686 | -0.051802 | -0.003175 | 0.063769 | 0.13176 | 0.066579 | 0.13457
1037.5781 | 122.0123 | -121.8109 | 0.14648 | 0.13101 | -0.008469 | 0.074994 | 0.007033 | 0.12325 | 0.09474 | -0.021514 | 0.043331 | 0.16164 | 0.05072 | -0.10179 | -0.006702 | 0.018642 | -0.083847 | -0.030641 | 0.15847 | 0.018997 | 0.10246 | 0.034499 | 0.15071 | 0.12221 | 0.005952 | 0.070797 | 0.1891 | 0.078186 | -0.07432 | 0.020764 | 0.046108 | -0.056381 | -0.003175 | 0.050033 | 0.12718 | 0.057422 | 0.13457
1039.3125 | 121.962 | -121.7789 | 0.13275 | 0.14017 | -0.008469 | 0.079572 | 0.007033 | 0.11409 | 0.09474 | -0.021514 | 0.052488 | 0.15706 | 0.046142 | -0.10637 | -0.002124 | 0.014064 | -0.083847 | -0.039797 | 0.16763 | 0.018997 | 0.10704 | 0.034499 | 0.14156 | 0.12221 | 0.005952 | 0.079954 | 0.18452 | 0.073608 | -0.078899 | 0.025342 | 0.04153 | -0.056381 | -0.012331 | 0.054612 | 0.13634 | 0.048266 | 0.12999
1040.9844 | 121.962 | -121.8155 | 0.14191 | 0.14017 | -0.008469 | 0.079572 | 0.011611 | 0.12325 | 0.09474 | -0.021514 | 0.047909 | 0.15248 | 0.059877 | -0.10637 | -0.002124 | 0.02322 | -0.088425 | -0.039797 | 0.16763 | 0.018997 | 0.10704 | 0.039077 | 0.15071 | 0.12221 | 0.005952 | 0.075375 | 0.17994 | 0.087343 | -0.078899 | 0.025342 | 0.050686 | -0.060959 | -0.012331 | 0.050033 | 0.13633 | 0.062001 | 0.1483
1042.7188 | 121.9894 | -121.8018 | 0.15106 | 0.13559 | -0.008469 | 0.079572 | 0.01619 | 0.11867 | 0.090161 | -0.016936 | 0.057066 | 0.15706 | 0.05072 | -0.10637 | -0.002124 | 0.014064 | -0.079268 | -0.035219 | 0.16305 | 0.018997 | 0.10704 | 0.043656 | 0.14613 | 0.11763 | 0.01053 | 0.084532 | 0.18452 | 0.078186 | -0.078899 | 0.025342 | 0.04153 | -0.051802 | -0.007753 | 0.05919 | 0.13633 | 0.052844 | 0.12999
1044.4688 | 122.0078 | -121.8018 | 0.15106 | 0.13559 | -0.008469 | 0.074994 | 0.01619 | 0.11409 | 0.09474 | -0.016936 | 0.052488 | 0.15706 | 0.055298 | -0.10637 | -0.006702 | 0.018642 | -0.093004 | -0.039797 | 0.16305 | 0.018997 | 0.10246 | 0.043656 | 0.14156 | 0.12221 | 0.01053 | 0.079954 | 0.18452 | 0.082764 | -0.078899 | 0.020764 | 0.046108 | -0.065538 | -0.012331 | 0.05919 | 0.14549 | 0.062 | 0.1483
1046.2188 | 122.0169 | -121.7972 | 0.1236 | 0.14017 | -0.008469 | 0.074994 | 0.007033 | 0.12325 | 0.099318 | -0.021514 | 0.052488 | 0.16164 | 0.055298 | -0.10637 | -0.002124 | 0.014064 | -0.088425 | -0.053532 | 0.16763 | 0.018997 | 0.10246 | 0.034499 | 0.15071 | 0.12678 | 0.005952 | 0.079954 | 0.1891 | 0.082764 | -0.078899 | 0.025342 | 0.04153 | -0.060959 | -0.026066 | 0.054612 | 0.14091 | 0.057422 | 0.14372
1047.9688 | 122.0993 | -121.7789 | 0.12817 | 0.14017 | -0.008469 | 0.074994 | 0.002454 | 0.11867 | 0.09474 | -0.03067 | 0.047909 | 0.16164 | 0.059877 | -0.10637 | -0.006702 | 0.018642 | -0.097582 | -0.044375 | 0.16763 | 0.018997 | 0.10246 | 0.02992 | 0.14613 | 0.12221 | -0.003204 | 0.075375 | 0.1891 | 0.087343 | -0.078899 | 0.020764 | 0.046108 | -0.070116 | -0.016909 | 0.054611 | 0.14549 | 0.066579 | 0.15746
1049.6562 | 121.9711 | -121.788 | 0.14648 | 0.13559 | -0.008469 | 0.084151 | 0.01619 | 0.12782 | 0.099318 | -0.021514 | 0.043331 | 0.15706 | 0.055298 | -0.11094 | -0.006702 | 0.014064 | -0.093004 | -0.053532 | 0.16305 | 0.018997 | 0.11162 | 0.043656 | 0.15529 | 0.12678 | 0.005952 | 0.070797 | 0.18452 | 0.082764 | -0.083478 | 0.020764 | 0.04153 | -0.065538 | -0.026066 | 0.050033 | 0.13634 | 0.062 | 0.1483
1051.4062 | 121.9803 | -121.8018 | 0.13275 | 0.13559 | -0.013048 | 0.074994 | 0.01619 | 0.12782 | 0.099318 | -0.021514 | 0.047909 | 0.16164 | 0.05072 | -0.10637 | -0.006702 | 0.009486 | -0.088425 | -0.039797 | 0.16305 | 0.014418 | 0.10246 | 0.043656 | 0.15529 | 0.12678 | 0.005952 | 0.075375 | 0.1891 | 0.078186 | -0.078899 | 0.020764 | 0.036952 | -0.060959 | -0.012331 | 0.054611 | 0.13633 | 0.057422 | 0.13915
1053.1562 | 121.9711 | -121.8292 | 0.14648 | 0.13559 | -0.013048 | 0.084151 | 0.007033 | 0.12325 | 0.085583 | -0.021514 | 0.047909 | 0.15248 | 0.046142 | -0.11094 | -0.006702 | 0.014064 | -0.093004 | -0.044375 | 0.16305 | 0.014418 | 0.11162 | 0.034499 | 0.15071 | 0.11305 | 0.005952 | 0.075375 | 0.17994 | 0.073608 | -0.083478 | 0.020764 | 0.04153 | -0.065538 | -0.016909 | 0.054611 | 0.14091 | 0.052844 | 0.13915
1054.9062 | 122.0535 | -121.7606 | 0.1236 | 0.13559 | -0.013048 | 0.074994 | 0.01619 | 0.11409 | 0.09474 | -0.021514 | 0.052488 | 0.1479 | 0.059877 | -0.10637 | -0.006702 | 0.014064 | -0.093004 | -0.039797 | 0.16305 | 0.014418 | 0.10246 | 0.043656 | 0.14156 | 0.12221 | 0.005952 | 0.079954 | 0.17536 | 0.087343 | -0.078899 | 0.020764 | 0.04153 | -0.065538 | -0.012331 | 0.05919 | 0.14549 | 0.066579 | 0.15288
1056.6406 | 122.0032 | -121.8201 | 0.13275 | 0.13101 | -0.008469 | 0.074994 | 0.01619 | 0.11867 | 0.099318 | -0.012357 | 0.047909 | 0.16164 | 0.046142 | -0.11552 | -0.002124 | 0.02322 | -0.093004 | -0.044375 | 0.15847 | 0.018997 | 0.10246 | 0.043656 | 0.14613 | 0.12678 | 0.015109 | 0.075375 | 0.1891 | 0.073608 | -0.088057 | 0.025342 | 0.050686 | -0.065538 | -0.016909 | 0.050033 | 0.14091 | 0.048266 | 0.13915
1058.3438 | 121.9986 | -121.8063 | 0.14648 | 0.13559 | -0.017627 | 0.074994 | 0.007033 | 0.11867 | 0.09474 | -0.021514 | 0.052488 | 0.15706 | 0.059877 | -0.11094 | -0.002124 | 0.018642 | -0.10216 | -0.048953 | 0.16305 | 0.009839 | 0.10246 | 0.034499 | 0.14613 | 0.12221 | 0.005952 | 0.079954 | 0.18452 | 0.087343 | -0.083478 | 0.025342 | 0.046108 | -0.074694 | -0.021487 | 0.054612 | 0.15465 | 0.062001 | 0.16204
1060.0781 | 122.0993 | -121.7606 | 0.10986 | 0.14474 | -0.013048 | 0.070415 | 0.007033 | 0.11409 | 0.09474 | -0.021514 | 0.052488 | 0.16164 | 0.046142 | -0.10637 | -0.006702 | 0.009486 | -0.088425 | -0.035219 | 0.17221 | 0.014418 | 0.097881 | 0.034499 | 0.14156 | 0.12221 | 0.005952 | 0.079954 | 0.1891 | 0.073608 | -0.078899 | 0.020764 | 0.036952 | -0.060959 | -0.007753 | 0.05919 | 0.14091 | 0.052844 | 0.13457
1061.8281 | 122.0673 | -121.7468 | 0.11902 | 0.14017 | -0.013048 | 0.065837 | 0.007033 | 0.11867 | 0.099318 | -0.016936 | 0.047909 | 0.16164 | 0.055298 | -0.11094 | -0.015859 | 0.014064 | -0.097582 | -0.044375 | 0.16763 | 0.014418 | 0.093303 | 0.034499 | 0.14613 | 0.12678 | 0.01053 | 0.075375 | 0.1891 | 0.082764 | -0.083478 | 0.011607 | 0.04153 | -0.070116 | -0.016909 | 0.063768 | 0.14549 | 0.071157 | 0.15288
1063.5156 | 121.9666 | -121.8063 | 0.13733 | 0.14017 | -0.008469 | 0.070415 | 0.011611 | 0.11867 | 0.09474 | -0.021514 | 0.052488 | 0.15706 | 0.055298 | -0.10637 | -0.011281 | 0.02322 | -0.097582 | -0.044375 | 0.16763 | 0.018997 | 0.097881 | 0.039077 | 0.14613 | 0.12221 | 0.005952 | 0.079954 | 0.18452 | 0.082764 | -0.078899 | 0.016185 | 0.050686 | -0.070116 | -0.016909 | 0.063769 | 0.15007 | 0.066579 | 0.15288
1065.25 | 122.1176 | -121.756 | 0.10986 | 0.13559 | -0.013048 | 0.074994 | 0.007033 | 0.12325 | 0.09474 | -0.026092 | 0.057066 | 0.15706 | 0.05072 | -0.11094 | -0.006702 | 0.009486 | -0.10674 | -0.053532 | 0.16305 | 0.014418 | 0.10246 | 0.034499 | 0.15071 | 0.12221 | 0.001374 | 0.084532 | 0.18452 | 0.078186 | -0.083478 | 0.020764 | 0.036952 | -0.079273 | -0.026066 | 0.063768 | 0.16381 | 0.057422 | 0.15746
1066.9844 | 121.9803 | -121.788 | 0.14191 | 0.13559 | -0.013048 | 0.074994 | 0.011611 | 0.10951 | 0.09474 | -0.026092 | 0.057066 | 0.15706 | 0.05072 | -0.11094 | -0.011281 | 0.014064 | -0.097582 | -0.048953 | 0.16305 | 0.014418 | 0.10246 | 0.039077 | 0.13698 | 0.12221 | 0.001374 | 0.084532 | 0.18452 | 0.078186 | -0.083478 | 0.016185 | 0.04153 | -0.070116 | -0.021487 | 0.068347 | 0.15465 | 0.062001 | 0.1483
1068.6719 | 121.9894 | -121.8246 | 0.13733 | 0.13559 | -0.013048 | 0.074994 | 0.011611 | 0.11867 | 0.099318 | -0.016936 | 0.057066 | 0.16622 | 0.05072 | -0.11094 | -0.006702 | 0.018642 | -0.097582 | -0.053532 | 0.16305 | 0.014418 | 0.10246 | 0.039077 | 0.14613 | 0.12678 | 0.01053 | 0.084532 | 0.19368 | 0.078186 | -0.083478 | 0.020764 | 0.046108 | -0.070116 | -0.026066 | 0.063768 | 0.15465 | 0.057422 | 0.1483
1070.4219 | 122.0444 | -121.8063 | 0.1236 | 0.14017 | -0.013048 | 0.079572 | 0.007033 | 0.12325 | 0.10848 | -0.021514 | 0.047909 | 0.16164 | 0.05072 | -0.11094 | -0.006702 | 0.018642 | -0.10674 | -0.048953 | 0.16763 | 0.014418 | 0.10704 | 0.034499 | 0.15071 | 0.13594 | 0.005952 | 0.075375 | 0.1891 | 0.078186 | -0.083478 | 0.020764 | 0.046108 | -0.079273 | -0.021487 | 0.054611 | 0.15465 | 0.057422 | 0.15746
1072.1562 | 122.0764 | -121.7972 | 0.12817 | 0.13559 | -0.008469 | 0.070415 | 0.011611 | 0.11409 | 0.099318 | -0.016936 | 0.052488 | 0.15248 | 0.05072 | -0.11094 | -0.011281 | 0.014064 | -0.097582 | -0.044375 | 0.16305 | 0.018997 | 0.097881 | 0.039077 | 0.14156 | 0.12678 | 0.01053 | 0.079954 | 0.17994 | 0.078186 | -0.083478 | 0.016185 | 0.04153 | -0.070116 | -0.016909 | 0.063769 | 0.15007 | 0.062001 | 0.1483
1073.9219 | 122.0718 | -121.7651 | 0.10986 | 0.13559 | -0.008469 | 0.070415 | 0.002454 | 0.11409 | 0.09474 | -0.016936 | 0.052488 | 0.15706 | 0.059877 | -0.11094 | -0.011281 | 0.009486 | -0.093004 | -0.039797 | 0.16305 | 0.018997 | 0.097881 | 0.02992 | 0.14156 | 0.12221 | 0.01053 | 0.079954 | 0.18452 | 0.087343 | -0.083478 | 0.016185 | 0.036952 | -0.065538 | -0.012331 | 0.063769 | 0.14549 | 0.071158 | 0.15288
1075.6562 | 122.0993 | -121.7651 | 0.11902 | 0.14017 | -0.022205 | 0.065837 | 0.01619 | 0.11867 | 0.090161 | -0.016936 | 0.047909 | 0.16622 | 0.055298 | -0.11094 | -0.011281 | 0.018642 | -0.097582 | -0.030641 | 0.16763 | 0.005261 | 0.093303 | 0.043656 | 0.14613 | 0.11763 | 0.01053 | 0.075375 | 0.19368 | 0.082764 | -0.083478 | 0.016185 | 0.046108 | -0.070116 | -0.003175 | 0.05919 | 0.14549 | 0.066579 | 0.15288
1077.3281 | 122.0764 | -121.7606 | 0.10529 | 0.14017 | -0.013048 | 0.070415 | 0.01619 | 0.11867 | 0.090161 | -0.021514 | 0.043331 | 0.16164 | 0.064455 | -0.11094 | -0.002124 | 0.014064 | -0.088425 | -0.044375 | 0.16763 | 0.014418 | 0.097881 | 0.043656 | 0.14613 | 0.11763 | 0.005952 | 0.070797 | 0.1891 | 0.091921 | -0.083478 | 0.025342 | 0.04153 | -0.060959 | -0.016909 | 0.045455 | 0.13176 | 0.066579 | 0.15288
1079.0625 | 121.9849 | -121.8292 | 0.15106 | 0.14017 | -0.013048 | 0.074994 | 0.011611 | 0.12325 | 0.1039 | -0.016936 | 0.052488 | 0.16164 | 0.05072 | -0.10179 | -0.006702 | 0.02322 | -0.083847 | -0.030641 | 0.16763 | 0.014418 | 0.10246 | 0.039077 | 0.15071 | 0.13136 | 0.01053 | 0.079954 | 0.1891 | 0.078186 | -0.07432 | 0.020764 | 0.050686 | -0.056381 | -0.003175 | 0.05919 | 0.13634 | 0.057422 | 0.13457
1080.7969 | 122.0993 | -121.7468 | 0.1236 | 0.14017 | -0.008469 | 0.070415 | 0.002454 | 0.11867 | 0.090161 | -0.021514 | 0.052488 | 0.15706 | 0.05072 | -0.11094 | -0.015859 | 0.014064 | -0.088425 | -0.039797 | 0.16763 | 0.018997 | 0.097881 | 0.02992 | 0.14613 | 0.11763 | 0.005952 | 0.079954 | 0.18452 | 0.078186 | -0.083478 | 0.011607 | 0.04153 | -0.060959 | -0.012331 | 0.068347 | 0.14091 | 0.066579 | 0.13915
1082.4688 | 122.113 | -121.7926 | 0.12817 | 0.14017 | -0.008469 | 0.074994 | 0.007033 | 0.10951 | 0.09474 | -0.026092 | 0.052488 | 0.15706 | 0.05072 | -0.11094 | -0.006702 | 0.018642 | -0.093004 | -0.035219 | 0.16763 | 0.018997 | 0.10246 | 0.034499 | 0.13698 | 0.12221 | 0.001374 | 0.079954 | 0.18452 | 0.078186 | -0.083478 | 0.020764 | 0.046108 | -0.065538 | -0.007753 | 0.05919 | 0.14549 | 0.057422 | 0.14372
1084.2188 | 121.994 | -121.8292 | 0.14648 | 0.14017 | -0.013048 | 0.074994 | 0.002454 | 0.11409 | 0.09474 | -0.021514 | 0.047909 | 0.15706 | 0.055298 | -0.11552 | -0.006702 | 0.014064 | -0.088425 | -0.035219 | 0.16763 | 0.014418 | 0.10246 | 0.02992 | 0.14156 | 0.12221 | 0.005952 | 0.075375 | 0.18452 | 0.082764 | -0.088057 | 0.020764 | 0.04153 | -0.060959 | -0.007753 | 0.054611 | 0.13633 | 0.062 | 0.14372
1085.9531 | 121.9757 | -121.7926 | 0.13733 | 0.14474 | -0.008469 | 0.079572 | 0.007033 | 0.11409 | 0.090161 | -0.016936 | 0.052488 | 0.16164 | 0.064455 | -0.10179 | -0.006702 | 0.014064 | -0.088425 | -0.030641 | 0.17221 | 0.018997 | 0.10704 | 0.034499 | 0.14156 | 0.11763 | 0.01053 | 0.079954 | 0.1891 | 0.091921 | -0.07432 | 0.020764 | 0.04153 | -0.060959 | -0.003175 | 0.05919 | 0.14091 | 0.071157 | 0.15288
1087.625 | 122.0352 | -121.8063 | 0.13733 | 0.14017 | -0.013048 | 0.070415 | 0.007033 | 0.11867 | 0.099318 | -0.012357 | 0.047909 | 0.15706 | 0.059877 | -0.10637 | -0.006702 | 0.018642 | -0.088425 | -0.044375 | 0.16763 | 0.014418 | 0.097881 | 0.034499 | 0.14613 | 0.12678 | 0.015109 | 0.075375 | 0.18452 | 0.087343 | -0.078899 | 0.020764 | 0.046108 | -0.060959 | -0.016909 | 0.054611 | 0.13633 | 0.066579 | 0.1483
1089.375 | 122.0993 | -121.7926 | 0.10071 | 0.14017 | -0.008469 | 0.070415 | 0.002454 | 0.11409 | 0.09474 | -0.016936 | 0.052488 | 0.15706 | 0.055298 | -0.11094 | -0.011281 | 0.009486 | -0.083847 | -0.039797 | 0.16763 | 0.018997 | 0.097881 | 0.02992 | 0.14156 | 0.12221 | 0.01053 | 0.079954 | 0.18452 | 0.082764 | -0.083478 | 0.016185 | 0.036952 | -0.056381 | -0.012331 | 0.063769 | 0.13634 | 0.066579 | 0.13915
1091.1094 | 122.0444 | -121.8155 | 0.13275 | 0.14017 | -0.008469 | 0.065837 | 0.01619 | 0.11867 | 0.09474 | -0.016936 | 0.052488 | 0.15706 | 0.05072 | -0.10637 | -0.002124 | 0.02322 | -0.083847 | -0.030641 | 0.16763 | 0.018997 | 0.093303 | 0.043656 | 0.14613 | 0.12221 | 0.01053 | 0.079954 | 0.18452 | 0.078186 | -0.078899 | 0.025342 | 0.050686 | -0.056381 | -0.003175 | 0.054612 | 0.13634 | 0.052844 | 0.13457
1092.8594 | 122.0718 | -121.8109 | 0.11902 | 0.14017 | -0.008469 | 0.074994 | 0.002454 | 0.11867 | 0.099318 | -0.021514 | 0.047909 | 0.16164 | 0.055298 | -0.097207 | -0.011281 | 0.009486 | -0.088425 | -0.039797 | 0.16763 | 0.018997 | 0.10246 | 0.02992 | 0.14613 | 0.12678 | 0.005952 | 0.075375 | 0.1891 | 0.082764 | -0.069741 | 0.016185 | 0.036952 | -0.060959 | -0.012331 | 0.05919 | 0.13633 | 0.066579 | 0.14372
1094.5469 | 121.9894 | -121.8155 | 0.11444 | 0.13101 | -0.013048 | 0.074994 | 0.002454 | 0.11867 | 0.09474 | -0.016936 | 0.043331 | 0.15248 | 0.055298 | -0.11094 | -0.002124 | 0.014064 | -0.07469 | -0.030641 | 0.15847 | 0.014418 | 0.10246 | 0.02992 | 0.14613 | 0.12221 | 0.01053 | 0.070797 | 0.17994 | 0.082764 | -0.083478 | 0.025342 | 0.04153 | -0.047224 | -0.003175 | 0.045455 | 0.11802 | 0.057422 | 0.12999
1096.2812 | 122.0123 | -121.8292 | 0.1236 | 0.13559 | -0.017627 | 0.074994 | 0.007033 | 0.11867 | 0.09474 | -0.021514 | 0.047909 | 0.15248 | 0.059877 | -0.11094 | -0.006702 | 0.018642 | -0.083847 | -0.035219 | 0.16305 | 0.009839 | 0.10246 | 0.034499 | 0.14613 | 0.12221 | 0.005952 | 0.075375 | 0.17994 | 0.087343 | -0.083478 | 0.020764 | 0.046108 | -0.056381 | -0.007753 | 0.054611 | 0.13176 | 0.066579 | 0.14372
1098.0156 | 122.081 | -121.8201 | 0.11902 | 0.13559 | -0.00389 | 0.070415 | 0.011611 | 0.11867 | 0.1039 | -0.026092 | 0.047909 | 0.1479 | 0.055298 | -0.11094 | -0.006702 | 0.018642 | -0.083847 | -0.021484 | 0.16305 | 0.023576 | 0.097881 | 0.039077 | 0.14613 | 0.13136 | 0.001374 | 0.075375 | 0.17536 | 0.082764 | -0.083478 | 0.020764 | 0.046108 | -0.056381 | 0.005982 | 0.054611 | 0.13176 | 0.062 | 0.13915
1099.75 | 121.9711 | -121.8384 | 0.15106 | 0.13559 | -0.013048 | 0.065837 | 0.007033 | 0.11867 | 0.09474 | -0.016936 | 0.052488 | 0.15706 | 0.055298 | -0.11552 | -0.002124 | 0.02322 | -0.083847 | -0.021484 | 0.16305 | 0.014418 | 0.093303 | 0.034499 | 0.14613 | 0.12221 | 0.01053 | 0.079954 | 0.18452 | 0.082764 | -0.088057 | 0.025342 | 0.050686 | -0.056381 | 0.005982 | 0.054612 | 0.13634 | 0.057422 | 0.13915
1101.5 | 121.7239 | -121.5134 | 0.13733 | 0.13101 | -0.008469 | 0.074994 | 0.002454 | 0.12325 | 0.09474 | -0.03067 | 0.047909 | 0.16164 | 0.05072 | -0.11552 | -0.002124 | 0.014064 | -0.079268 | -0.021484 | 0.15847 | 0.018997 | 0.10246 | 0.02992 | 0.15071 | 0.12221 | -0.003204 | 0.075375 | 0.1891 | 0.078186 | -0.088057 | 0.025342 | 0.04153 | -0.051802 | 0.005982 | 0.050033 | 0.12718 | 0.052844 | 0.12999
1103.1719 | 121.9208 | -121.5912 | 0.09613 | 0.14017 | -0.022205 | 0.065837 | 0.007033 | 0.10951 | 0.090161 | -0.021514 | 0.047909 | 0.15248 | 0.05072 | -0.10637 | -0.002124 | 0.018642 | -0.079268 | -0.026063 | 0.16763 | 0.005261 | 0.093303 | 0.034499 | 0.13698 | 0.11763 | 0.005952 | 0.075375 | 0.17994 | 0.078186 | -0.078899 | 0.025342 | 0.046108 | -0.051802 | 0.001403 | 0.050033 | 0.12718 | 0.052844 | 0.12999
1104.9375 | 121.8842 | -121.6827 | 0.13733 | 0.14017 | -0.013048 | 0.065837 | 0.011611 | 0.11867 | 0.09474 | -0.026092 | 0.047909 | 0.16164 | 0.046142 | -0.11094 | -0.011281 | 0.018642 | -0.079268 | -0.030641 | 0.16763 | 0.014418 | 0.093303 | 0.039077 | 0.14613 | 0.12221 | 0.001374 | 0.075375 | 0.1891 | 0.073608 | -0.083478 | 0.016185 | 0.046108 | -0.051802 | -0.003175 | 0.05919 | 0.12718 | 0.057423 | 0.12541
1106.6719 | 121.8475 | -121.7102 | 0.13275 | 0.13101 | -0.013048 | 0.070415 | 0.011611 | 0.11867 | 0.09474 | -0.026092 | 0.047909 | 0.15248 | 0.046142 | -0.10637 | -0.006702 | 0.014064 | -0.079268 | -0.026063 | 0.15847 | 0.014418 | 0.097881 | 0.039077 | 0.14613 | 0.12221 | 0.001374 | 0.075375 | 0.17994 | 0.073608 | -0.078899 | 0.020764 | 0.04153 | -0.051802 | 0.001403 | 0.054611 | 0.12718 | 0.052844 | 0.12541
1108.3438 | 121.8704 | -121.6736 | 0.13733 | 0.14017 | -0.008469 | 0.079572 | 0.007033 | 0.11867 | 0.090161 | -0.012357 | 0.047909 | 0.15706 | 0.055298 | -0.11094 | -0.002124 | 0.02322 | -0.079268 | -0.026063 | 0.16763 | 0.018997 | 0.10704 | 0.034499 | 0.14613 | 0.11763 | 0.015109 | 0.075375 | 0.18452 | 0.082764 | -0.083478 | 0.025342 | 0.050686 | -0.051802 | 0.001403 | 0.050033 | 0.12718 | 0.057422 | 0.13457
1110.0938 | 121.9437 | -121.6736 | 0.13275 | 0.14474 | -0.008469 | 0.074994 | 0.007033 | 0.10951 | 0.09474 | -0.026092 | 0.038752 | 0.15706 | 0.046142 | -0.11094 | -0.002124 | 0.014064 | -0.07469 | -0.026063 | 0.17221 | 0.018997 | 0.10246 | 0.034499 | 0.13698 | 0.12221 | 0.001374 | 0.066218 | 0.18452 | 0.073608 | -0.083478 | 0.025342 | 0.04153 | -0.047224 | 0.001403 | 0.040876 | 0.11344 | 0.048266 | 0.12083
1111.8281 | 122.0169 | -121.6507 | 0.09613 | 0.13559 | -0.013048 | 0.070415 | 0.007033 | 0.11409 | 0.085583 | -0.021514 | 0.043331 | 0.1479 | 0.055298 | -0.10637 | -0.006702 | 0.02322 | -0.07469 | -0.021484 | 0.16305 | 0.014418 | 0.097881 | 0.034499 | 0.14156 | 0.11305 | 0.005952 | 0.070797 | 0.17536 | 0.082764 | -0.078899 | 0.020764 | 0.050686 | -0.047224 | 0.005982 | 0.050033 | 0.11802 | 0.062 | 0.12999
1113.5156 | 121.875 | -121.7102 | 0.13733 | 0.13101 | -0.013048 | 0.070415 | 0.002454 | 0.11867 | 0.09474 | -0.026092 | 0.047909 | 0.15706 | 0.055298 | -0.11094 | -0.002124 | 0.02322 | -0.079268 | -0.021484 | 0.15847 | 0.014418 | 0.097881 | 0.02992 | 0.14613 | 0.12221 | 0.001374 | 0.075375 | 0.18452 | 0.082764 | -0.083478 | 0.025342 | 0.050686 | -0.051802 | 0.005982 | 0.050033 | 0.12718 | 0.057422 | 0.13457
1115.2656 | 122.0261 | -121.6553 | 0.10986 | 0.13559 | -0.013048 | 0.070415 | 0.007033 | 0.12325 | 0.090161 | -0.021514 | 0.043331 | 0.15706 | 0.055298 | -0.10637 | -0.002124 | 0.02322 | -0.07469 | -0.026063 | 0.16305 | 0.014418 | 0.097881 | 0.034499 | 0.15071 | 0.11763 | 0.005952 | 0.070797 | 0.18452 | 0.082764 | -0.078899 | 0.025342 | 0.050686 | -0.047224 | 0.001403 | 0.045455 | 0.11802 | 0.057422 | 0.12999
1117 | 121.9482 | -121.6827 | 0.11902 | 0.14017 | -0.008469 | 0.074994 | 0.011611 | 0.11867 | 0.090161 | -0.021514 | 0.052488 | 0.15706 | 0.055298 | -0.10179 | -0.002124 | 0.018642 | -0.07469 | -0.030641 | 0.16763 | 0.018997 | 0.10246 | 0.039077 | 0.14613 | 0.11763 | 0.005952 | 0.079954 | 0.18452 | 0.082764 | -0.07432 | 0.025342 | 0.046108 | -0.047224 | -0.003175 | 0.054612 | 0.12718 | 0.057422 | 0.12999
1118.6875 | 122.0215 | -121.6553 | 0.11444 | 0.13101 | -0.017627 | 0.074994 | 0.011611 | 0.11409 | 0.085583 | -0.026092 | 0.052488 | 0.15706 | 0.05072 | -0.1201 | -0.002124 | 0.014064 | -0.079268 | -0.021484 | 0.15847 | 0.009839 | 0.10246 | 0.039077 | 0.14156 | 0.11305 | 0.001374 | 0.079954 | 0.18452 | 0.078186 | -0.092637 | 0.025342 | 0.04153 | -0.051802 | 0.005982 | 0.054612 | 0.13176 | 0.052844 | 0.12999
1120.4531 | 121.9208 | -121.6919 | 0.12817 | 0.13559 | -0.017627 | 0.070415 | 0.011611 | 0.11409 | 0.085583 | -0.021514 | 0.052488 | 0.15706 | 0.05072 | -0.10179 | -0.006702 | 0.02322 | -0.083847 | -0.026063 | 0.16305 | 0.009839 | 0.097881 | 0.039077 | 0.14156 | 0.11305 | 0.005952 | 0.079954 | 0.18452 | 0.078186 | -0.07432 | 0.020764 | 0.050686 | -0.056381 | 0.001403 | 0.05919 | 0.13634 | 0.057422 | 0.13457
1122.125 | 121.9528 | -121.7056 | 0.11902 | 0.13559 | -0.00389 | 0.070415 | 0.011611 | 0.11867 | 0.09474 | -0.012357 | 0.047909 | 0.15248 | 0.055298 | -0.10179 | -0.006702 | 0.02322 | -0.070112 | -0.026063 | 0.16305 | 0.023576 | 0.097881 | 0.039077 | 0.14613 | 0.12221 | 0.015109 | 0.075375 | 0.17994 | 0.082764 | -0.07432 | 0.020764 | 0.050686 | -0.042646 | 0.001403 | 0.054611 | 0.11802 | 0.062 | 0.12541
1123.875 | 121.9757 | -121.7056 | 0.10986 | 0.13101 | -0.013048 | 0.065837 | 0.011611 | 0.11867 | 0.090161 | -0.03067 | 0.047909 | 0.16164 | 0.05072 | -0.11094 | -0.006702 | 0.014064 | -0.070112 | -0.021484 | 0.15847 | 0.014418 | 0.093303 | 0.039077 | 0.14613 | 0.11763 | -0.003204 | 0.075375 | 0.1891 | 0.078186 | -0.083478 | 0.020764 | 0.04153 | -0.042646 | 0.005982 | 0.054611 | 0.11802 | 0.057422 | 0.12083
1125.625 | 121.9666 | -121.6965 | 0.11902 | 0.13101 | -0.013048 | 0.065837 | 0.002454 | 0.11409 | 0.09474 | -0.021514 | 0.052488 | 0.15706 | 0.055298 | -0.10637 | -0.006702 | 0.014064 | -0.07469 | -0.030641 | 0.15847 | 0.014418 | 0.093303 | 0.02992 | 0.14156 | 0.12221 | 0.005952 | 0.079954 | 0.18452 | 0.082764 | -0.078899 | 0.020764 | 0.04153 | -0.047224 | -0.003175 | 0.05919 | 0.12718 | 0.062 | 0.12999
1127.2969 | 121.8933 | -121.7377 | 0.13275 | 0.14017 | -0.017627 | 0.074994 | 0.01619 | 0.11409 | 0.090161 | -0.021514 | 0.047909 | 0.16164 | 0.05072 | -0.11094 | -0.011281 | 0.02322 | -0.083847 | -0.021484 | 0.16763 | 0.009839 | 0.10246 | 0.043656 | 0.14156 | 0.11763 | 0.005952 | 0.075375 | 0.1891 | 0.078186 | -0.083478 | 0.016185 | 0.050686 | -0.056381 | 0.005982 | 0.05919 | 0.13176 | 0.062001 | 0.13457
1129.0469 | 121.9162 | -121.7331 | 0.14191 | 0.13559 | -0.017627 | 0.070415 | 0.01619 | 0.12325 | 0.090161 | -0.016936 | 0.047909 | 0.1479 | 0.059877 | -0.10637 | -0.006702 | 0.018642 | -0.07469 | -0.021484 | 0.16305 | 0.009839 | 0.097881 | 0.043656 | 0.15071 | 0.11763 | 0.01053 | 0.075375 | 0.17536 | 0.087343 | -0.078899 | 0.020764 | 0.046108 | -0.047224 | 0.005982 | 0.054611 | 0.1226 | 0.066579 | 0.13457
1130.7969 | 122.0169 | -121.6919 | 0.11902 | 0.13559 | -0.017627 | 0.070415 | 0.002454 | 0.11409 | 0.090161 | -0.021514 | 0.047909 | 0.15706 | 0.059877 | -0.11094 | -0.006702 | 0.009486 | -0.070112 | -0.030641 | 0.16305 | 0.009839 | 0.097881 | 0.02992 | 0.14156 | 0.11763 | 0.005952 | 0.075375 | 0.18452 | 0.087343 | -0.083478 | 0.020764 | 0.036952 | -0.042646 | -0.003175 | 0.054611 | 0.11802 | 0.066579 | 0.12999
1132.5312 | 121.9574 | -121.7239 | 0.1236 | 0.14017 | -0.013048 | 0.074994 | 0.007033 | 0.11867 | 0.090161 | -0.016936 | 0.052488 | 0.15706 | 0.055298 | -0.11094 | -0.006702 | 0.014064 | -0.07469 | -0.021484 | 0.16763 | 0.014418 | 0.10246 | 0.034499 | 0.14613 | 0.11763 | 0.01053 | 0.079954 | 0.18452 | 0.082764 | -0.083478 | 0.020764 | 0.04153 | -0.047224 | 0.005982 | 0.05919 | 0.12718 | 0.062 | 0.12999
1134.2031 | 122.0352 | -121.6919 | 0.10529 | 0.14017 | -0.017627 | 0.065837 | 0.011611 | 0.11867 | 0.085583 | -0.021514 | 0.047909 | 0.16164 | 0.05072 | -0.10637 | -0.011281 | 0.018642 | -0.083847 | -0.026063 | 0.16763 | 0.009839 | 0.093303 | 0.039077 | 0.14613 | 0.11305 | 0.005952 | 0.075375 | 0.1891 | 0.078186 | -0.078899 | 0.016185 | 0.046108 | -0.056381 | 0.001403 | 0.05919 | 0.13176 | 0.062001 | 0.13457
1135.9531 | 121.9116 | -121.7377 | 0.14191 | 0.14474 | -0.013048 | 0.074994 | 0.01619 | 0.11867 | 0.090161 | -0.016936 | 0.043331 | 0.15248 | 0.055298 | -0.10637 | -0.006702 | 0.018642 | -0.070112 | -0.026063 | 0.17221 | 0.014418 | 0.10246 | 0.043656 | 0.14613 | 0.11763 | 0.01053 | 0.070797 | 0.17994 | 0.082764 | -0.078899 | 0.020764 | 0.046108 | -0.042646 | 0.001403 | 0.050033 | 0.11344 | 0.062 | 0.12541
1137.7031 | 122.0123 | -121.7194 | 0.11902 | 0.13559 | -0.017627 | 0.074994 | 0.007033 | 0.10951 | 0.085583 | -0.016936 | 0.052488 | 0.15706 | 0.055298 | -0.11552 | -0.006702 | 0.014064 | -0.079268 | -0.012328 | 0.16305 | 0.009839 | 0.10246 | 0.034499 | 0.13698 | 0.11305 | 0.01053 | 0.079954 | 0.18452 | 0.082764 | -0.088057 | 0.020764 | 0.04153 | -0.051802 | 0.015138 | 0.05919 | 0.13176 | 0.062 | 0.13457
1139.3906 | 122.0032 | -121.7056 | 0.1236 | 0.13101 | -0.013048 | 0.070415 | 0.011611 | 0.12325 | 0.090161 | -0.012357 | 0.047909 | 0.16164 | 0.059877 | -0.10637 | -0.006702 | 0.014064 | -0.07469 | -0.021484 | 0.15847 | 0.014418 | 0.097881 | 0.039077 | 0.15071 | 0.11763 | 0.015109 | 0.075375 | 0.1891 | 0.087343 | -0.078899 | 0.020764 | 0.04153 | -0.047224 | 0.005982 | 0.054611 | 0.1226 | 0.066579 | 0.13457
1141.0625 | 121.9437 | -121.7285 | 0.13275 | 0.13101 | -0.022205 | 0.065837 | 0.01619 | 0.11409 | 0.085583 | -0.021514 | 0.038752 | 0.15248 | 0.05072 | -0.11094 | -0.002124 | 0.02322 | -0.079268 | -0.021484 | 0.15847 | 0.005261 | 0.093303 | 0.043656 | 0.14156 | 0.11305 | 0.005952 | 0.066218 | 0.17994 | 0.078186 | -0.083478 | 0.025342 | 0.050686 | -0.051802 | 0.005982 | 0.040876 | 0.11802 | 0.052844 | 0.12999
1142.8125 | 122.0032 | -121.7285 | 0.1236 | 0.13559 | -0.017627 | 0.065837 | 0.011611 | 0.11867 | 0.090161 | -0.012357 | 0.047909 | 0.16164 | 0.055298 | -0.10637 | -0.006702 | 0.02322 | -0.079268 | -0.016906 | 0.16305 | 0.009839 | 0.093303 | 0.039077 | 0.14613 | 0.11763 | 0.015109 | 0.075375 | 0.1891 | 0.082764 | -0.078899 | 0.020764 | 0.050686 | -0.051802 | 0.01056 | 0.054611 | 0.12718 | 0.062 | 0.13457
1144.5625 | 121.9574 | -121.7514 | 0.1236 | 0.14017 | -0.017627 | 0.065837 | 0.002454 | 0.10951 | 0.09474 | -0.021514 | 0.052488 | 0.15706 | 0.069033 | -0.10637 | -0.006702 | 0.014064 | -0.070112 | -0.030641 | 0.16763 | 0.009839 | 0.093303 | 0.02992 | 0.13698 | 0.12221 | 0.005952 | 0.079954 | 0.18452 | 0.096499 | -0.078899 | 0.020764 | 0.04153 | -0.042646 | -0.003175 | 0.05919 | 0.1226 | 0.075735 | 0.13914
1146.25 | 121.9894 | -121.7194 | 0.10529 | 0.13101 | -0.022205 | 0.070415 | 0.011611 | 0.10951 | 0.085583 | -0.021514 | 0.043331 | 0.15248 | 0.05072 | -0.11094 | -0.015859 | 0.018642 | -0.079268 | -0.021484 | 0.15847 | 0.005261 | 0.097881 | 0.039077 | 0.13698 | 0.11305 | 0.005952 | 0.070797 | 0.17994 | 0.078186 | -0.083478 | 0.011607 | 0.046108 | -0.051802 | 0.005982 | 0.05919 | 0.1226 | 0.066579 | 0.12999
1147.9844 | 121.907 | -121.7514 | 0.15564 | 0.13101 | -0.017627 | 0.070415 | 0.01619 | 0.12325 | 0.09474 | -0.016936 | 0.047909 | 0.15706 | 0.05072 | -0.10637 | -0.006702 | 0.02322 | -0.07469 | -0.021484 | 0.15847 | 0.009839 | 0.097881 | 0.043656 | 0.15071 | 0.12221 | 0.01053 | 0.075375 | 0.18452 | 0.078186 | -0.078899 | 0.020764 | 0.050686 | -0.047224 | 0.005982 | 0.054611 | 0.1226 | 0.057422 | 0.12541
1149.7344 | 122.049 | -121.7056 | 0.10986 | 0.13559 | -0.022205 | 0.065837 | 0.007033 | 0.12325 | 0.090161 | -0.021514 | 0.047909 | 0.16164 | 0.05072 | -0.11094 | -0.006702 | 0.018642 | -0.070112 | -0.021484 | 0.16305 | 0.005261 | 0.093303 | 0.034499 | 0.15071 | 0.11763 | 0.005952 | 0.075375 | 0.1891 | 0.078186 | -0.083478 | 0.020764 | 0.046108 | -0.042646 | 0.005982 | 0.054611 | 0.11802 | 0.057422 | 0.12083
1151.4219 | 122.0673 | -121.6965 | 0.10529 | 0.13559 | -0.017627 | 0.074994 | 0.007033 | 0.11409 | 0.090161 | -0.021514 | 0.052488 | 0.16164 | 0.055298 | -0.10637 | -0.002124 | 0.02322 | -0.070112 | -0.021484 | 0.16305 | 0.009839 | 0.10246 | 0.034499 | 0.14156 | 0.11763 | 0.005952 | 0.079954 | 0.1891 | 0.082764 | -0.078899 | 0.025342 | 0.050686 | -0.042646 | 0.005982 | 0.054612 | 0.1226 | 0.057422 | 0.12541
1153.0938 | 121.9208 | -121.7651 | 0.15106 | 0.14474 | -0.017627 | 0.070415 | 0.01619 | 0.12782 | 0.085583 | -0.012357 | 0.043331 | 0.15248 | 0.05072 | -0.10637 | -0.006702 | 0.014064 | -0.07469 | -0.016906 | 0.17221 | 0.009839 | 0.097881 | 0.043656 | 0.15529 | 0.11305 | 0.015109 | 0.070797 | 0.17994 | 0.078186 | -0.078899 | 0.020764 | 0.04153 | -0.047224 | 0.01056 | 0.050033 | 0.11802 | 0.057422 | 0.12541
1154.8438 | 122.0261 | -121.7102 | 0.10986 | 0.14017 | -0.017627 | 0.070415 | 0.011611 | 0.12325 | 0.09474 | -0.021514 | 0.043331 | 0.15248 | 0.059877 | -0.11552 | -0.002124 | 0.014064 | -0.07469 | -0.026063 | 0.16763 | 0.009839 | 0.097881 | 0.039077 | 0.15071 | 0.12221 | 0.005952 | 0.070797 | 0.17994 | 0.087343 | -0.088057 | 0.025342 | 0.04153 | -0.047224 | 0.001403 | 0.045455 | 0.11802 | 0.062001 | 0.13457
1156.5938 | 121.9025 | -121.7743 | 0.12817 | 0.14017 | -0.017627 | 0.065837 | 0.011611 | 0.11409 | 0.10848 | -0.016936 | 0.043331 | 0.16164 | 0.055298 | -0.10637 | -0.006702 | 0.02322 | -0.07469 | -0.026063 | 0.16763 | 0.009839 | 0.093303 | 0.039077 | 0.14156 | 0.13594 | 0.01053 | 0.070797 | 0.1891 | 0.082764 | -0.078899 | 0.020764 | 0.050686 | -0.047224 | 0.001403 | 0.050033 | 0.11802 | 0.062 | 0.12999
1158.2656 | 121.8887 | -121.7422 | 0.14648 | 0.13101 | -0.017627 | 0.070415 | 0.011611 | 0.11409 | 0.09474 | -0.021514 | 0.047909 | 0.16622 | 0.05072 | -0.10637 | -0.006702 | 0.014064 | -0.079268 | -0.026063 | 0.15847 | 0.009839 | 0.097881 | 0.039077 | 0.14156 | 0.12221 | 0.005952 | 0.075375 | 0.19368 | 0.078186 | -0.078899 | 0.020764 | 0.04153 | -0.051802 | 0.001403 | 0.054611 | 0.12718 | 0.057422 | 0.12999
1159.9375 | 122.0078 | -121.7056 | 0.10529 | 0.13559 | -0.022205 | 0.074994 | 0.007033 | 0.10493 | 0.090161 | -0.016936 | 0.052488 | 0.16164 | 0.046142 | -0.10637 | -0.015859 | 0.02322 | -0.070112 | -0.030641 | 0.16305 | 0.005261 | 0.10246 | 0.034499 | 0.1324 | 0.11763 | 0.01053 | 0.079954 | 0.1891 | 0.073608 | -0.078899 | 0.011607 | 0.050686 | -0.042646 | -0.003175 | 0.068347 | 0.1226 | 0.062001 | 0.11625
1161.625 | 121.9299 | -121.7514 | 0.15106 | 0.13101 | -0.022205 | 0.070415 | 0.011611 | 0.11867 | 0.085583 | -0.016936 | 0.047909 | 0.15706 | 0.05072 | -0.10637 | -0.006702 | 0.02322 | -0.065533 | -0.021484 | 0.15847 | 0.005261 | 0.097881 | 0.039077 | 0.14613 | 0.11305 | 0.01053 | 0.075375 | 0.18452 | 0.078186 | -0.078899 | 0.020764 | 0.050686 | -0.038067 | 0.005982 | 0.054611 | 0.11344 | 0.057422 | 0.11625
1164.7656 | 121.9894 | -121.7194 | 0.12817 | 0.14474 | -0.017627 | 0.070415 | 0.007033 | 0.11867 | 0.085583 | -0.021514 | 0.052488 | 0.16164 | 0.059877 | -0.10637 | -0.002124 | 0.018642 | -0.070112 | -0.021484 | 0.17221 | 0.009839 | 0.097881 | 0.034499 | 0.14613 | 0.11305 | 0.005952 | 0.079954 | 0.1891 | 0.087343 | -0.078899 | 0.025342 | 0.046108 | -0.042646 | 0.005982 | 0.054612 | 0.1226 | 0.062001 | 0.12999
1168.5 | 121.9162 | -121.756 | 0.13275 | 0.13559 | -0.017627 | 0.079572 | 0.007033 | 0.10951 | 0.090161 | -0.026092 | 0.047909 | 0.15706 | 0.059877 | -0.11094 | -0.002124 | 0.018642 | -0.07469 | -0.030641 | 0.16305 | 0.009839 | 0.10704 | 0.034499 | 0.13698 | 0.11763 | 0.001374 | 0.075375 | 0.18452 | 0.087343 | -0.083478 | 0.025342 | 0.046108 | -0.047224 | -0.003175 | 0.050033 | 0.1226 | 0.062001 | 0.13457
1173.7812 | 122.0627 | -121.7239 | 0.10986 | 0.13101 | -0.013048 | 0.070415 | 0.007033 | 0.11409 | 0.090161 | -0.021514 | 0.047909 | 0.15248 | 0.055298 | -0.10637 | -0.006702 | 0.014064 | -0.07469 | -0.021484 | 0.15847 | 0.014418 | 0.097881 | 0.034499 | 0.14156 | 0.11763 | 0.005952 | 0.075375 | 0.17994 | 0.082764 | -0.078899 | 0.020764 | 0.04153 | -0.047224 | 0.005982 | 0.054611 | 0.1226 | 0.062 | 0.12999
1176.4062 | 121.962 | -121.7468 | 0.13733 | 0.13559 | -0.017627 | 0.074994 | 0.007033 | 0.11867 | 0.099318 | -0.016936 | 0.061645 | 0.16164 | 0.059877 | -0.11094 | -0.002124 | 0.009486 | -0.079268 | -0.026063 | 0.16305 | 0.009839 | 0.10246 | 0.034499 | 0.14613 | 0.12678 | 0.01053 | 0.089111 | 0.1891 | 0.087343 | -0.083478 | 0.025342 | 0.036952 | -0.051802 | 0.001403 | 0.063769 | 0.14091 | 0.062001 | 0.13915
1178.0938 | 121.9391 | -121.7422 | 0.14191 | 0.14017 | -0.013048 | 0.070415 | 0.007033 | 0.11867 | 0.099318 | -0.012357 | 0.061645 | 0.16164 | 0.059877 | -0.11094 | -0.006702 | 0.018642 | -0.07469 | -0.026063 | 0.16763 | 0.014418 | 0.097881 | 0.034499 | 0.14613 | 0.12678 | 0.015109 | 0.089111 | 0.1891 | 0.087343 | -0.083478 | 0.020764 | 0.046108 | -0.047224 | 0.001403 | 0.068347 | 0.13634 | 0.066579 | 0.13457
1179.8438 | 121.9391 | -121.7789 | 0.14648 | 0.14017 | -0.013048 | 0.079572 | 0.011611 | 0.12325 | 0.09474 | -0.021514 | 0.047909 | 0.15706 | 0.041563 | -0.10637 | -0.002124 | 0.018642 | -0.070112 | -0.021484 | 0.16763 | 0.014418 | 0.10704 | 0.039077 | 0.15071 | 0.12221 | 0.005952 | 0.075375 | 0.18452 | 0.069029 | -0.078899 | 0.025342 | 0.046108 | -0.042646 | 0.005982 | 0.050033 | 0.11802 | 0.043687 | 0.11167
1181.5781 | 121.9345 | -121.7285 | 0.14648 | 0.14017 | -0.017627 | 0.070415 | 0.01619 | 0.10951 | 0.099318 | -0.021514 | 0.052488 | 0.16622 | 0.055298 | -0.10637 | -0.006702 | 0.018642 | -0.070112 | -0.026063 | 0.16763 | 0.009839 | 0.097881 | 0.043656 | 0.13698 | 0.12678 | 0.005952 | 0.079954 | 0.19368 | 0.082764 | -0.078899 | 0.020764 | 0.046108 | -0.042646 | 0.001403 | 0.05919 | 0.1226 | 0.062 | 0.12541
1183.2812 | 121.962 | -121.7377 | 0.11902 | 0.13559 | -0.022205 | 0.074994 | 0.011611 | 0.12325 | 0.099318 | -0.026092 | 0.052488 | 0.15706 | 0.055298 | -0.11094 | -0.011281 | 0.027798 | -0.079268 | -0.021484 | 0.16305 | 0.005261 | 0.10246 | 0.039077 | 0.15071 | 0.12678 | 0.001374 | 0.079954 | 0.18452 | 0.082764 | -0.083478 | 0.016185 | 0.055264 | -0.051802 | 0.005982 | 0.063769 | 0.13176 | 0.066579 | 0.13457
1185.0156 | 121.9116 | -121.7834 | 0.14191 | 0.14017 | -0.013048 | 0.074994 | 0.01619 | 0.11409 | 0.09474 | -0.016936 | 0.047909 | 0.15706 | 0.055298 | -0.10637 | -0.002124 | 0.014064 | -0.079268 | -0.030641 | 0.16763 | 0.014418 | 0.10246 | 0.043656 | 0.14156 | 0.12221 | 0.01053 | 0.075375 | 0.18452 | 0.082764 | -0.078899 | 0.025342 | 0.04153 | -0.051802 | -0.003175 | 0.050033 | 0.12718 | 0.057422 | 0.13457
1186.6875 | 122.0078 | -121.7285 | 0.1236 | 0.13559 | -0.008469 | 0.065837 | 0.002454 | 0.11409 | 0.099318 | -0.012357 | 0.047909 | 0.16164 | 0.055298 | -0.11094 | 0.002454 | 0.014064 | -0.079268 | -0.030641 | 0.16305 | 0.018997 | 0.093303 | 0.02992 | 0.14156 | 0.12678 | 0.015109 | 0.075375 | 0.1891 | 0.082764 | -0.083478 | 0.02992 | 0.04153 | -0.051802 | -0.003175 | 0.045455 | 0.12718 | 0.052844 | 0.13457
1188.4219 | 122.049 | -121.701 | 0.10529 | 0.14017 | -0.017627 | 0.074994 | 0.007033 | 0.12325 | 0.090161 | -0.026092 | 0.047909 | 0.17079 | 0.064455 | -0.10179 | -0.006702 | 0.014064 | -0.070112 | -0.026063 | 0.16763 | 0.009839 | 0.10246 | 0.034499 | 0.15071 | 0.11763 | 0.001374 | 0.075375 | 0.19826 | 0.091921 | -0.07432 | 0.020764 | 0.04153 | -0.042646 | 0.001403 | 0.054611 | 0.11802 | 0.071157 | 0.13457
1190.0938 | 122.0169 | -121.701 | 0.12817 | 0.13559 | -0.022205 | 0.065837 | 0.011611 | 0.11867 | 0.09474 | -0.021514 | 0.061645 | 0.16164 | 0.064455 | -0.11094 | -0.011281 | 0.009486 | -0.079268 | -0.021484 | 0.16305 | 0.005261 | 0.093303 | 0.039077 | 0.14613 | 0.12221 | 0.005952 | 0.089111 | 0.1891 | 0.091921 | -0.083478 | 0.016185 | 0.036952 | -0.051802 | 0.005982 | 0.072926 | 0.14091 | 0.075736 | 0.14372
1191.8438 | 121.9666 | -121.7606 | 0.14648 | 0.13101 | -0.022205 | 0.074994 | 0.011611 | 0.12782 | 0.09474 | -0.012357 | 0.052488 | 0.16622 | 0.059877 | -0.10637 | -0.006702 | 0.014064 | -0.088425 | -0.026063 | 0.15847 | 0.005261 | 0.10246 | 0.039077 | 0.15529 | 0.12221 | 0.015109 | 0.079954 | 0.19368 | 0.087343 | -0.078899 | 0.020764 | 0.04153 | -0.060959 | 0.001403 | 0.05919 | 0.14091 | 0.066579 | 0.1483
1193.5781 | 121.9345 | -121.756 | 0.16022 | 0.14017 | -0.017627 | 0.074994 | 0.011611 | 0.12325 | 0.085583 | -0.026092 | 0.061645 | 0.17079 | 0.069033 | -0.10637 | -0.006702 | 0.02322 | -0.07469 | -0.021484 | 0.16763 | 0.009839 | 0.10246 | 0.039077 | 0.15071 | 0.11305 | 0.001374 | 0.089111 | 0.19826 | 0.096499 | -0.078899 | 0.020764 | 0.050686 | -0.047224 | 0.005982 | 0.068347 | 0.13634 | 0.075735 | 0.14372
1195.25 | 121.9391 | -121.7743 | 0.15564 | 0.14017 | -0.022205 | 0.074994 | 0.007033 | 0.11867 | 0.085583 | -0.016936 | 0.047909 | 0.16164 | 0.064455 | -0.10179 | -0.002124 | 0.009486 | -0.07469 | -0.021484 | 0.16763 | 0.005261 | 0.10246 | 0.034499 | 0.14613 | 0.11305 | 0.01053 | 0.075375 | 0.1891 | 0.091921 | -0.07432 | 0.025342 | 0.036952 | -0.047224 | 0.005982 | 0.050033 | 0.1226 | 0.066579 | 0.13915
1197 | 121.9803 | -121.7285 | 0.13275 | 0.14017 | -0.022205 | 0.074994 | 0.01619 | 0.12325 | 0.090161 | -0.021514 | 0.052488 | 0.16164 | 0.059877 | -0.11552 | -0.006702 | 0.009486 | -0.07469 | -0.021484 | 0.16763 | 0.005261 | 0.10246 | 0.043656 | 0.15071 | 0.11763 | 0.005952 | 0.079954 | 0.1891 | 0.087343 | -0.088057 | 0.020764 | 0.036952 | -0.047224 | 0.005982 | 0.05919 | 0.12718 | 0.066579 | 0.13457
1198.7344 | 121.9666 | -121.7651 | 0.12817 | 0.13101 | -0.022205 | 0.065837 | 0.007033 | 0.11867 | 0.099318 | -0.016936 | 0.047909 | 0.16164 | 0.055298 | -0.10637 | -0.006702 | 0.02322 | -0.079268 | -0.021484 | 0.15847 | 0.005261 | 0.093303 | 0.034499 | 0.14613 | 0.12678 | 0.01053 | 0.075375 | 0.1891 | 0.082764 | -0.078899 | 0.020764 | 0.050686 | -0.051802 | 0.005982 | 0.054611 | 0.12718 | 0.062 | 0.13457
1200.4844 | 121.9162 | -121.7789 | 0.1236 | 0.13559 | -0.022205 | 0.070415 | 0.011611 | 0.12325 | 0.09474 | -0.021514 | 0.047909 | 0.16622 | 0.064455 | -0.10637 | -0.006702 | 0.014064 | -0.07469 | -0.021484 | 0.16305 | 0.005261 | 0.097881 | 0.039077 | 0.15071 | 0.12221 | 0.005952 | 0.075375 | 0.19368 | 0.091921 | -0.078899 | 0.020764 | 0.04153 | -0.047224 | 0.005982 | 0.054611 | 0.1226 | 0.071157 | 0.13915
1202.1562 | 122.0078 | -121.7102 | 0.13275 | 0.14017 | -0.022205 | 0.074994 | 0.011611 | 0.11409 | 0.090161 | -0.021514 | 0.052488 | 0.15706 | 0.064455 | -0.11094 | -0.002124 | 0.018642 | -0.07469 | -0.026063 | 0.16763 | 0.005261 | 0.10246 | 0.039077 | 0.14156 | 0.11763 | 0.005952 | 0.079954 | 0.18452 | 0.091921 | -0.083478 | 0.025342 | 0.046108 | -0.047224 | 0.001403 | 0.054612 | 0.12718 | 0.066579 | 0.13915
1203.8906 | 121.9574 | -121.7377 | 0.13275 | 0.14017 | -0.022205 | 0.070415 | 0.011611 | 0.12782 | 0.09474 | -0.016936 | 0.047909 | 0.16164 | 0.05072 | -0.10637 | -0.006702 | 0.02322 | -0.079268 | -0.021484 | 0.16763 | 0.005261 | 0.097881 | 0.039077 | 0.15529 | 0.12221 | 0.01053 | 0.075375 | 0.1891 | 0.078186 | -0.078899 | 0.020764 | 0.050686 | -0.051802 | 0.005982 | 0.054611 | 0.12718 | 0.057422 | 0.12999
1205.625 | 122.0535 | -121.7331 | 0.11444 | 0.13101 | -0.026784 | 0.061258 | 0.011611 | 0.11867 | 0.09474 | -0.021514 | 0.047909 | 0.15248 | 0.05072 | -0.11552 | -0.002124 | 0.02322 | -0.070112 | -0.026063 | 0.15847 | 0.000682 | 0.088724 | 0.039077 | 0.14613 | 0.12221 | 0.005952 | 0.075375 | 0.17994 | 0.078186 | -0.088057 | 0.025342 | 0.050686 | -0.042646 | 0.001403 | 0.050033 | 0.11802 | 0.052844 | 0.12083
1207.375 | 122.0032 | -121.7285 | 0.10529 | 0.13559 | -0.022205 | 0.070415 | 0.011611 | 0.12325 | 0.085583 | -0.021514 | 0.052488 | 0.15248 | 0.059877 | -0.10179 | -0.011281 | 0.009486 | -0.079268 | -0.016906 | 0.16305 | 0.005261 | 0.097881 | 0.039077 | 0.15071 | 0.11305 | 0.005952 | 0.079954 | 0.17994 | 0.087343 | -0.07432 | 0.016185 | 0.036952 | -0.051802 | 0.01056 | 0.063769 | 0.13176 | 0.071158 | 0.13915
1209.0625 | 122.0215 | -121.7377 | 0.13275 | 0.13559 | -0.017627 | 0.070415 | 0.011611 | 0.12325 | 0.090161 | -0.016936 | 0.047909 | 0.16164 | 0.059877 | -0.10179 | 0.002454 | 0.018642 | -0.07469 | -0.021484 | 0.16305 | 0.009839 | 0.097881 | 0.039077 | 0.15071 | 0.11763 | 0.01053 | 0.075375 | 0.1891 | 0.087343 | -0.07432 | 0.02992 | 0.046108 | -0.047224 | 0.005982 | 0.045455 | 0.1226 | 0.057423 | 0.13457
1210.7969 | 122.0078 | -121.7102 | 0.1236 | 0.14017 | -0.017627 | 0.079572 | 0.011611 | 0.12325 | 0.09474 | -0.016936 | 0.047909 | 0.15706 | 0.055298 | -0.10179 | -0.006702 | 0.014064 | -0.070112 | -0.021484 | 0.16763 | 0.009839 | 0.10704 | 0.039077 | 0.15071 | 0.12221 | 0.01053 | 0.075375 | 0.18452 | 0.082764 | -0.07432 | 0.020764 | 0.04153 | -0.042646 | 0.005982 | 0.054611 | 0.11802 | 0.062 | 0.12541
1212.5469 | 122.0398 | -121.7102 | 0.11902 | 0.14017 | -0.026784 | 0.074994 | 0.011611 | 0.11409 | 0.090161 | -0.016936 | 0.043331 | 0.15706 | 0.055298 | -0.11094 | -0.006702 | 0.018642 | -0.079268 | -0.026063 | 0.16763 | 0.000682 | 0.10246 | 0.039077 | 0.14156 | 0.11763 | 0.01053 | 0.070797 | 0.18452 | 0.082764 | -0.083478 | 0.020764 | 0.046108 | -0.051802 | 0.001403 | 0.050033 | 0.1226 | 0.062 | 0.13457
1214.2188 | 122.049 | -121.6919 | 0.082397 | 0.14017 | -0.022205 | 0.074994 | 0.007033 | 0.11409 | 0.090161 | -0.012357 | 0.047909 | 0.15706 | 0.055298 | -0.11094 | -0.006702 | 0.014064 | -0.070112 | -0.016906 | 0.16763 | 0.005261 | 0.10246 | 0.034499 | 0.14156 | 0.11763 | 0.015109 | 0.075375 | 0.18452 | 0.082764 | -0.083478 | 0.020764 | 0.04153 | -0.042646 | 0.01056 | 0.054611 | 0.11802 | 0.062 | 0.12541
1215.9531 | 121.9208 | -121.8018 | 0.15564 | 0.14017 | -0.013048 | 0.070415 | 0.011611 | 0.12325 | 0.090161 | -0.012357 | 0.052488 | 0.15706 | 0.064455 | -0.10637 | 0.007032 | 0.014064 | -0.07469 | -0.026063 | 0.16763 | 0.014418 | 0.097881 | 0.039077 | 0.15071 | 0.11763 | 0.015109 | 0.079954 | 0.18452 | 0.091921 | -0.078899 | 0.034498 | 0.04153 | -0.047224 | 0.001403 | 0.045456 | 0.12718 | 0.057423 | 0.13915
1217.6406 | 122.0581 | -121.7651 | 0.10986 | 0.13101 | -0.017627 | 0.074994 | 0.01619 | 0.11409 | 0.09474 | -0.016936 | 0.043331 | 0.15706 | 0.055298 | -0.10637 | -0.011281 | 0.018642 | -0.07469 | -0.016906 | 0.15847 | 0.009839 | 0.10246 | 0.043656 | 0.14156 | 0.12221 | 0.01053 | 0.070797 | 0.18452 | 0.082764 | -0.078899 | 0.016185 | 0.046108 | -0.047224 | 0.01056 | 0.054612 | 0.11802 | 0.066579 | 0.12999
1219.375 | 122.0581 | -121.6919 | 0.11902 | 0.13559 | -0.022205 | 0.079572 | 0.002454 | 0.11409 | 0.09474 | -0.016936 | 0.043331 | 0.16164 | 0.041563 | -0.11094 | -0.002124 | 0.02322 | -0.070112 | -0.026063 | 0.16305 | 0.005261 | 0.10704 | 0.02992 | 0.14156 | 0.12221 | 0.01053 | 0.070797 | 0.1891 | 0.069029 | -0.083478 | 0.025342 | 0.050686 | -0.042646 | 0.001403 | 0.045455 | 0.11344 | 0.043687 | 0.11167
1221.125 | 122.0673 | -121.7285 | 0.09613 | 0.13559 | -0.017627 | 0.074994 | 0.01619 | 0.11867 | 0.09474 | -0.021514 | 0.052488 | 0.15706 | 0.05072 | -0.10637 | -0.011281 | 0.014064 | -0.07469 | -0.021484 | 0.16305 | 0.009839 | 0.10246 | 0.043656 | 0.14613 | 0.12221 | 0.005952 | 0.079954 | 0.18452 | 0.078186 | -0.078899 | 0.016185 | 0.04153 | -0.047224 | 0.005982 | 0.063769 | 0.12718 | 0.062001 | 0.12541
1222.8906 | 121.9254 | -121.7789 | 0.14191 | 0.14474 | -0.026784 | 0.079572 | 0.011611 | 0.11867 | 0.085583 | -0.026092 | 0.052488 | 0.15706 | 0.059877 | -0.10179 | -0.011281 | 0.02322 | -0.083847 | -0.026063 | 0.17221 | 0.000682 | 0.10704 | 0.039077 | 0.14613 | 0.11305 | 0.001374 | 0.079954 | 0.18452 | 0.087343 | -0.07432 | 0.016185 | 0.050686 | -0.056381 | 0.001403 | 0.063769 | 0.13634 | 0.071158 | 0.14372
1224.5625 | 121.9025 | -121.7697 | 0.14648 | 0.14017 | -0.022205 | 0.065837 | 0.01619 | 0.12325 | 0.09474 | -0.021514 | 0.047909 | 0.16622 | 0.05072 | -0.11094 | -0.006702 | 0.027798 | -0.07469 | -0.021484 | 0.16763 | 0.005261 | 0.093303 | 0.043656 | 0.15071 | 0.12221 | 0.005952 | 0.075375 | 0.19368 | 0.078186 | -0.083478 | 0.020764 | 0.055264 | -0.047224 | 0.005982 | 0.054611 | 0.1226 | 0.057422 | 0.12541
1226.2969 | 121.9894 | -121.7285 | 0.11444 | 0.14017 | -0.017627 | 0.070415 | 0.002454 | 0.11409 | 0.085583 | -0.016936 | 0.038752 | 0.15706 | 0.041563 | -0.10179 | -0.011281 | 0.014064 | -0.083847 | -0.030641 | 0.16763 | 0.009839 | 0.097881 | 0.02992 | 0.14156 | 0.11305 | 0.01053 | 0.066218 | 0.18452 | 0.069029 | -0.07432 | 0.016185 | 0.04153 | -0.056381 | -0.003175 | 0.050033 | 0.1226 | 0.052844 | 0.12541
1228.0312 | 121.994 | -121.7468 | 0.1236 | 0.13101 | -0.013048 | 0.074994 | 0.011611 | 0.11867 | 0.085583 | -0.021514 | 0.052488 | 0.15248 | 0.055298 | -0.10637 | -0.006702 | 0.02322 | -0.079268 | -0.030641 | 0.15847 | 0.014418 | 0.10246 | 0.039077 | 0.14613 | 0.11305 | 0.005952 | 0.079954 | 0.17994 | 0.082764 | -0.078899 | 0.020764 | 0.050686 | -0.051802 | -0.003175 | 0.05919 | 0.13176 | 0.062 | 0.13457
1229.7031 | 122.0398 | -121.7422 | 0.10529 | 0.13101 | -0.022205 | 0.074994 | 0.011611 | 0.12325 | 0.090161 | -0.021514 | 0.043331 | 0.15706 | 0.055298 | -0.10637 | -0.002124 | 0.018642 | -0.07469 | -0.030641 | 0.15847 | 0.005261 | 0.10246 | 0.039077 | 0.15071 | 0.11763 | 0.005952 | 0.070797 | 0.18452 | 0.082764 | -0.078899 | 0.025342 | 0.046108 | -0.047224 | -0.003175 | 0.045455 | 0.11802 | 0.057422 | 0.12999
1231.4531 | 121.9711 | -121.7514 | 0.1236 | 0.13559 | -0.022205 | 0.070415 | 0.011611 | 0.12325 | 0.09474 | -0.016936 | 0.047909 | 0.15706 | 0.055298 | -0.11094 | -0.002124 | 0.02322 | -0.07469 | -0.016906 | 0.16305 | 0.005261 | 0.097881 | 0.039077 | 0.15071 | 0.12221 | 0.01053 | 0.075375 | 0.18452 | 0.082764 | -0.083478 | 0.025342 | 0.050686 | -0.047224 | 0.01056 | 0.050033 | 0.1226 | 0.057422 | 0.12999
1233.1406 | 122.0123 | -121.7606 | 0.1236 | 0.13101 | -0.022205 | 0.074994 | 0.01619 | 0.11409 | 0.090161 | -0.026092 | 0.047909 | 0.15248 | 0.05072 | -0.11094 | -0.002124 | 0.018642 | -0.079268 | -0.026063 | 0.15847 | 0.005261 | 0.10246 | 0.043656 | 0.14156 | 0.11763 | 0.001374 | 0.075375 | 0.17994 | 0.078186 | -0.083478 | 0.025342 | 0.046108 | -0.051802 | 0.001403 | 0.050033 | 0.12718 | 0.052844 | 0.12999
1234.875 | 121.9803 | -121.7468 | 0.15106 | 0.13559 | -0.017627 | 0.070415 | 0.007033 | 0.12325 | 0.09474 | -0.016936 | 0.043331 | 0.15248 | 0.059877 | -0.11552 | -0.002124 | 0.014064 | -0.079268 | -0.016906 | 0.16305 | 0.009839 | 0.097881 | 0.034499 | 0.15071 | 0.12221 | 0.01053 | 0.070797 | 0.17994 | 0.087343 | -0.088057 | 0.025342 | 0.04153 | -0.051802 | 0.01056 | 0.045455 | 0.1226 | 0.062001 | 0.13915
1236.5469 | 121.962 | -121.7331 | 0.13275 | 0.14017 | -0.022205 | 0.074994 | 0.011611 | 0.11409 | 0.09474 | -0.016936 | 0.052488 | 0.16622 | 0.059877 | -0.11094 | -0.006702 | 0.018642 | -0.070112 | -0.026063 | 0.16763 | 0.005261 | 0.10246 | 0.039077 | 0.14156 | 0.12221 | 0.01053 | 0.079954 | 0.19368 | 0.087343 | -0.083478 | 0.020764 | 0.046108 | -0.042646 | 0.001403 | 0.05919 | 0.1226 | 0.066579 | 0.12999
1238.2969 | 121.9711 | -121.7377 | 0.12817 | 0.13559 | -0.017627 | 0.074994 | 0.002454 | 0.11867 | 0.090161 | -0.021514 | 0.043331 | 0.16164 | 0.059877 | -0.10637 | -0.006702 | 0.018642 | -0.079268 | -0.021484 | 0.16305 | 0.009839 | 0.10246 | 0.02992 | 0.14613 | 0.11763 | 0.005952 | 0.070797 | 0.1891 | 0.087343 | -0.078899 | 0.020764 | 0.046108 | -0.051802 | 0.005982 | 0.050033 | 0.1226 | 0.066579 | 0.13915
1239.9688 | 122.0123 | -121.7056 | 0.10986 | 0.13101 | -0.022205 | 0.065837 | 0.007033 | 0.11409 | 0.090161 | -0.026092 | 0.052488 | 0.15706 | 0.05072 | -0.11094 | -0.002124 | 0.02322 | -0.070112 | -0.021484 | 0.15847 | 0.005261 | 0.093303 | 0.034499 | 0.14156 | 0.11763 | 0.001374 | 0.079954 | 0.18452 | 0.078186 | -0.083478 | 0.025342 | 0.050686 | -0.042646 | 0.005982 | 0.054612 | 0.1226 | 0.052844 | 0.12083
1241.7031 | 121.9711 | -121.7651 | 0.13733 | 0.13101 | -0.017627 | 0.070415 | 0.01619 | 0.11867 | 0.090161 | -0.016936 | 0.052488 | 0.15706 | 0.055298 | -0.11094 | -0.002124 | 0.018642 | -0.079268 | -0.016906 | 0.15847 | 0.009839 | 0.097881 | 0.043656 | 0.14613 | 0.11763 | 0.01053 | 0.079954 | 0.18452 | 0.082764 | -0.083478 | 0.025342 | 0.046108 | -0.051802 | 0.01056 | 0.054612 | 0.13176 | 0.057422 | 0.13457
1243.3906 | 122.0169 | -121.7148 | 0.10071 | 0.13559 | -0.022205 | 0.070415 | 0.007033 | 0.11867 | 0.099318 | -0.021514 | 0.052488 | 0.16164 | 0.064455 | -0.10637 | -0.011281 | 0.02322 | -0.070112 | -0.021484 | 0.16305 | 0.005261 | 0.097881 | 0.034499 | 0.14613 | 0.12678 | 0.005952 | 0.079954 | 0.1891 | 0.091921 | -0.078899 | 0.016185 | 0.050686 | -0.042646 | 0.005982 | 0.063769 | 0.1226 | 0.075736 | 0.13457
1245.125 | 121.962 | -121.7422 | 0.12817 | 0.13559 | -0.022205 | 0.070415 | 0.011611 | 0.11867 | 0.09474 | -0.021514 | 0.038752 | 0.15706 | 0.059877 | -0.10637 | -0.006702 | 0.018642 | -0.079268 | -0.030641 | 0.16305 | 0.005261 | 0.097881 | 0.039077 | 0.14613 | 0.12221 | 0.005952 | 0.066218 | 0.18452 | 0.087343 | -0.078899 | 0.020764 | 0.046108 | -0.051802 | -0.003175 | 0.045454 | 0.11802 | 0.066579 | 0.13915
1246.875 | 122.081 | -121.7148 | 0.10529 | 0.13559 | -0.022205 | 0.065837 | 0.011611 | 0.12325 | 0.09474 | -0.016936 | 0.047909 | 0.16164 | 0.064455 | -0.11552 | -0.006702 | 0.018642 | -0.079268 | -0.021484 | 0.16305 | 0.005261 | 0.093303 | 0.039077 | 0.15071 | 0.12221 | 0.01053 | 0.075375 | 0.1891 | 0.091921 | -0.088057 | 0.020764 | 0.046108 | -0.051802 | 0.005982 | 0.054611 | 0.12718 | 0.071157 | 0.14372
1248.5625 | 122.0123 | -121.7468 | 0.1236 | 0.12643 | -0.022205 | 0.070415 | 0.002454 | 0.11867 | 0.090161 | -0.021514 | 0.047909 | 0.16164 | 0.059877 | -0.10637 | -0.002124 | 0.02322 | -0.07469 | -0.021484 | 0.1539 | 0.005261 | 0.097881 | 0.02992 | 0.14613 | 0.11763 | 0.005952 | 0.075375 | 0.1891 | 0.087343 | -0.078899 | 0.025342 | 0.050686 | -0.047224 | 0.005982 | 0.050033 | 0.1226 | 0.062001 | 0.13457
1250.2969 | 122.0398 | -121.7056 | 0.10986 | 0.14017 | -0.022205 | 0.070415 | 0.002454 | 0.11409 | 0.085583 | -0.021514 | 0.047909 | 0.16164 | 0.055298 | -0.11094 | -0.006702 | 0.018642 | -0.07469 | -0.021484 | 0.16763 | 0.005261 | 0.097881 | 0.02992 | 0.14156 | 0.11305 | 0.005952 | 0.075375 | 0.1891 | 0.082764 | -0.083478 | 0.020764 | 0.046108 | -0.047224 | 0.005982 | 0.054611 | 0.1226 | 0.062 | 0.12999
1252.0312 | 122.081 | -121.7331 | 0.11444 | 0.13559 | -0.017627 | 0.074994 | 0.002454 | 0.11867 | 0.09474 | -0.016936 | 0.047909 | 0.16164 | 0.055298 | -0.10637 | -0.002124 | 0.018642 | -0.070112 | -0.021484 | 0.16305 | 0.009839 | 0.10246 | 0.02992 | 0.14613 | 0.12221 | 0.01053 | 0.075375 | 0.1891 | 0.082764 | -0.078899 | 0.025342 | 0.046108 | -0.042646 | 0.005982 | 0.050033 | 0.11802 | 0.057422 | 0.12541
1253.7656 | 122.0535 | -121.7285 | 0.10071 | 0.13559 | -0.026784 | 0.079572 | 0.011611 | 0.10951 | 0.09474 | -0.012357 | 0.047909 | 0.15248 | 0.05072 | -0.10637 | -0.006702 | 0.018642 | -0.07469 | -0.026063 | 0.16305 | 0.000682 | 0.10704 | 0.039077 | 0.13698 | 0.12221 | 0.015109 | 0.075375 | 0.17994 | 0.078186 | -0.078899 | 0.020764 | 0.046108 | -0.047224 | 0.001403 | 0.054611 | 0.1226 | 0.057422 | 0.12541
1255.4375 | 121.962 | -121.756 | 0.12817 | 0.14017 | -0.022205 | 0.074994 | 0.01619 | 0.12325 | 0.099318 | -0.021514 | 0.047909 | 0.16164 | 0.059877 | -0.10637 | -0.002124 | 0.014064 | -0.070112 | -0.026063 | 0.16763 | 0.005261 | 0.10246 | 0.043656 | 0.15071 | 0.12678 | 0.005952 | 0.075375 | 0.1891 | 0.087343 | -0.078899 | 0.025342 | 0.04153 | -0.042646 | 0.001403 | 0.050033 | 0.11802 | 0.062001 | 0.12999
1257.1094 | 122.0352 | -121.7285 | 0.10986 | 0.13101 | -0.026784 | 0.074994 | 0.011611 | 0.11867 | 0.085583 | -0.016936 | 0.057066 | 0.1479 | 0.05072 | -0.10637 | -0.011281 | 0.02322 | -0.07469 | -0.021484 | 0.15847 | 0.000682 | 0.10246 | 0.039077 | 0.14613 | 0.11305 | 0.01053 | 0.084532 | 0.17536 | 0.078186 | -0.078899 | 0.016185 | 0.050686 | -0.047224 | 0.005982 | 0.068347 | 0.13176 | 0.062001 | 0.12541
1258.8438 | 121.9528 | -121.7514 | 0.13733 | 0.14017 | -0.026784 | 0.070415 | 0.007033 | 0.12782 | 0.099318 | -0.021514 | 0.052488 | 0.16164 | 0.064455 | -0.11094 | -0.002124 | 0.009486 | -0.079268 | -0.016906 | 0.16763 | 0.000682 | 0.097881 | 0.034499 | 0.15529 | 0.12678 | 0.005952 | 0.079954 | 0.1891 | 0.091921 | -0.083478 | 0.025342 | 0.036952 | -0.051802 | 0.01056 | 0.054612 | 0.13176 | 0.066579 | 0.14372
1260.5781 | 121.907 | -121.7514 | 0.13733 | 0.13101 | -0.022205 | 0.074994 | 0.011611 | 0.12325 | 0.09474 | -0.021514 | 0.047909 | 0.15706 | 0.055298 | -0.11094 | -0.011281 | 0.018642 | -0.07469 | -0.021484 | 0.15847 | 0.005261 | 0.10246 | 0.039077 | 0.15071 | 0.12221 | 0.005952 | 0.075375 | 0.18452 | 0.082764 | -0.083478 | 0.016185 | 0.046108 | -0.047224 | 0.005982 | 0.05919 | 0.1226 | 0.066579 | 0.12999
1262.3125 | 122.0169 | -121.7606 | 0.12817 | 0.12643 | -0.022205 | 0.074994 | 0.007033 | 0.11867 | 0.09474 | -0.026092 | 0.052488 | 0.15706 | 0.05072 | -0.097207 | -0.006702 | 0.018642 | -0.079268 | -0.026063 | 0.1539 | 0.005261 | 0.10246 | 0.034499 | 0.14613 | 0.12221 | 0.001374 | 0.079954 | 0.18452 | 0.078186 | -0.069741 | 0.020764 | 0.046108 | -0.051802 | 0.001403 | 0.05919 | 0.13176 | 0.057422 | 0.12999
1263.9844 | 122.049 | -121.7468 | 0.11902 | 0.12643 | -0.017627 | 0.065837 | 0.002454 | 0.11409 | 0.09474 | -0.021514 | 0.052488 | 0.16622 | 0.059877 | -0.10637 | -0.002124 | 0.014064 | -0.079268 | -0.021484 | 0.1539 | 0.009839 | 0.093303 | 0.02992 | 0.14156 | 0.12221 | 0.005952 | 0.079954 | 0.19368 | 0.087343 | -0.078899 | 0.025342 | 0.04153 | -0.051802 | 0.005982 | 0.054612 | 0.13176 | 0.062001 | 0.13915
1265.7188 | 122.0123 | -121.7422 | 0.10071 | 0.13559 | -0.031363 | 0.074994 | 0.002454 | 0.12325 | 0.09474 | -0.021514 | 0.038752 | 0.16164 | 0.05072 | -0.11094 | -0.006702 | 0.018642 | -0.07469 | -0.030641 | 0.16305 | -0.003897 | 0.10246 | 0.02992 | 0.15071 | 0.12221 | 0.005952 | 0.066218 | 0.1891 | 0.078186 | -0.083478 | 0.020764 | 0.046108 | -0.047224 | -0.003175 | 0.045454 | 0.11344 | 0.057422 | 0.12541
1267.4531 | 122.0535 | -121.7285 | 0.10529 | 0.13101 | -0.022205 | 0.070415 | 0.002454 | 0.11867 | 0.09474 | -0.016936 | 0.047909 | 0.16164 | 0.055298 | -0.10637 | -0.006702 | 0.018642 | -0.07469 | -0.026063 | 0.15847 | 0.005261 | 0.097881 | 0.02992 | 0.14613 | 0.12221 | 0.01053 | 0.075375 | 0.1891 | 0.082764 | -0.078899 | 0.020764 | 0.046108 | -0.047224 | 0.001403 | 0.054611 | 0.1226 | 0.062 | 0.12999
1269.1875 | 122.0078 | -121.7331 | 0.12817 | 0.13559 | -0.022205 | 0.079572 | 0.007033 | 0.11867 | 0.090161 | -0.021514 | 0.047909 | 0.16164 | 0.055298 | -0.10179 | -0.002124 | 0.018642 | -0.070112 | -0.026063 | 0.16305 | 0.005261 | 0.10704 | 0.034499 | 0.14613 | 0.11763 | 0.005952 | 0.075375 | 0.1891 | 0.082764 | -0.07432 | 0.025342 | 0.046108 | -0.042646 | 0.001403 | 0.050033 | 0.11802 | 0.057422 | 0.12541
1270.9531 | 121.9666 | -121.7697 | 0.1236 | 0.13101 | -0.017627 | 0.070415 | 0.011611 | 0.11409 | 0.099318 | -0.016936 | 0.038752 | 0.15706 | 0.055298 | -0.11552 | -0.002124 | 0.018642 | -0.07469 | -0.021484 | 0.15847 | 0.009839 | 0.097881 | 0.039077 | 0.14156 | 0.12678 | 0.01053 | 0.066218 | 0.18452 | 0.082764 | -0.088057 | 0.025342 | 0.046108 | -0.047224 | 0.005982 | 0.040876 | 0.11344 | 0.057422 | 0.12999
1272.6406 | 122.0306 | -121.7285 | 0.11902 | 0.13101 | -0.022205 | 0.074994 | 0.007033 | 0.11409 | 0.09474 | -0.016936 | 0.052488 | 0.16164 | 0.05072 | -0.11552 | -0.011281 | 0.018642 | -0.07469 | -0.021484 | 0.15847 | 0.005261 | 0.10246 | 0.034499 | 0.14156 | 0.12221 | 0.01053 | 0.079954 | 0.1891 | 0.078186 | -0.088057 | 0.016185 | 0.046108 | -0.047224 | 0.005982 | 0.063769 | 0.12718 | 0.062001 | 0.12541
1274.3906 | 122.0627 | -121.7148 | 0.10986 | 0.13559 | -0.013048 | 0.070415 | 0.007033 | 0.11867 | 0.09474 | -0.007779 | 0.052488 | 0.16622 | 0.055298 | -0.10637 | -0.006702 | 0.014064 | -0.070112 | -0.021484 | 0.16305 | 0.014418 | 0.097881 | 0.034499 | 0.14613 | 0.12221 | 0.019687 | 0.079954 | 0.19368 | 0.082764 | -0.078899 | 0.020764 | 0.04153 | -0.042646 | 0.005982 | 0.05919 | 0.1226 | 0.062 | 0.12541
1276.0625 | 121.9986 | -121.7194 | 0.11902 | 0.14017 | -0.022205 | 0.074994 | 0.007033 | 0.12325 | 0.090161 | -0.021514 | 0.052488 | 0.16164 | 0.055298 | -0.10637 | -0.002124 | 0.018642 | -0.079268 | -0.026063 | 0.16763 | 0.005261 | 0.10246 | 0.034499 | 0.15071 | 0.11763 | 0.005952 | 0.079954 | 0.1891 | 0.082764 | -0.078899 | 0.025342 | 0.046108 | -0.051802 | 0.001403 | 0.054612 | 0.13176 | 0.057422 | 0.13457
1277.8125 | 122.0261 | -121.7194 | 0.11444 | 0.14017 | -0.022205 | 0.074994 | 0.007033 | 0.11409 | 0.090161 | -0.026092 | 0.057066 | 0.15706 | 0.05072 | -0.11094 | -0.002124 | 0.014064 | -0.079268 | -0.030641 | 0.16763 | 0.005261 | 0.10246 | 0.034499 | 0.14156 | 0.11763 | 0.001374 | 0.084532 | 0.18452 | 0.078186 | -0.083478 | 0.025342 | 0.04153 | -0.051802 | -0.003175 | 0.05919 | 0.13633 | 0.052844 | 0.12999
1279.5625 | 121.994 | -121.7239 | 0.09613 | 0.13559 | -0.013048 | 0.074994 | 0.011611 | 0.11409 | 0.090161 | -0.016936 | 0.052488 | 0.16164 | 0.055298 | -0.10179 | -0.011281 | 0.018642 | -0.079268 | -0.016906 | 0.16305 | 0.014418 | 0.10246 | 0.039077 | 0.14156 | 0.11763 | 0.01053 | 0.079954 | 0.1891 | 0.082764 | -0.07432 | 0.016185 | 0.046108 | -0.051802 | 0.01056 | 0.063769 | 0.13176 | 0.066579 | 0.13457
1281.2969 | 121.9803 | -121.7285 | 0.1236 | 0.14017 | -0.022205 | 0.074994 | 0.011611 | 0.12325 | 0.09474 | -0.012357 | 0.052488 | 0.15706 | 0.055298 | -0.11094 | -0.006702 | 0.018642 | -0.079268 | -0.021484 | 0.16763 | 0.005261 | 0.10246 | 0.039077 | 0.15071 | 0.12221 | 0.015109 | 0.079954 | 0.18452 | 0.082764 | -0.083478 | 0.020764 | 0.046108 | -0.051802 | 0.005982 | 0.05919 | 0.13176 | 0.062 | 0.13457
1282.9844 | 121.8933 | -121.7285 | 0.13733 | 0.13559 | -0.022205 | 0.074994 | 0.007033 | 0.12325 | 0.09474 | -0.012357 | 0.057066 | 0.16164 | 0.059877 | -0.10637 | -0.006702 | 0.018642 | -0.083847 | -0.021484 | 0.16305 | 0.005261 | 0.10246 | 0.034499 | 0.15071 | 0.12221 | 0.015109 | 0.084532 | 0.1891 | 0.087343 | -0.078899 | 0.020764 | 0.046108 | -0.056381 | 0.005982 | 0.063768 | 0.14091 | 0.066579 | 0.14372
1284.7344 | 121.8155 | -120.8679 | 0.79651 | 0.16306 | -0.00389 | 0.093308 | 0.034504 | 0.14614 | 0.11763 | 0.005955 | 0.17153 | 0.30358 | 0.17891 | 0.05848 | -0.020437 | -0.013405 | -0.093004 | -0.035219 | 0.19052 | 0.023576 | 0.12077 | 0.06197 | 0.1736 | 0.1451 | 0.033421 | 0.19899 | 0.33104 | 0.20638 | 0.085946 | 0.007029 | 0.014061 | -0.065538 | -0.007753 | 0.19197 | 0.26453 | 0.19935 | 0.27192
1286.4844 | 121.4813 | -9.1187 | 112.5916 | 0.076067 | -0.08173 | 0.006315 | -0.052488 | 0.054577 | 0.035221 | -0.076452 | 0.011281 | 0.092954 | -0.036267 | -0.092628 | 0.034501 | 0.082735 | -0.033484 | 0.005985 | 0.10353 | -0.054264 | 0.033781 | -0.025022 | 0.082043 | 0.062687 | -0.048986 | 0.038747 | 0.12042 | -0.008801 | -0.065162 | 0.061967 | 0.1102 | -0.006018 | 0.033451 | -0.02322 | 0.044765 | -0.070768 | -0.002783
1288.2344 | 121.6873 | -8.7753 | 112.9669 | 0.071489 | -0.086309 | 0.006315 | -0.052488 | 0.049999 | 0.030642 | -0.085608 | 0.002124 | 0.083796 | -0.022532 | -0.088049 | 0.039079 | 0.087313 | -0.038063 | 0.015141 | 0.098955 | -0.058843 | 0.033781 | -0.025022 | 0.077465 | 0.058108 | -0.058142 | 0.02959 | 0.11126 | 0.004934 | -0.060583 | 0.066545 | 0.11478 | -0.010597 | 0.042607 | -0.036955 | 0.040187 | -0.061611 | 0.015531
1289.9219 | 121.7194 | -9.2148 | 112.5229 | 0.06691 | -0.077151 | 0.010893 | -0.057066 | 0.049999 | 0.035221 | -0.076452 | 0.006703 | 0.092954 | -0.027111 | -0.092628 | 0.039079 | 0.087313 | -0.038063 | 0.010563 | 0.094376 | -0.049685 | 0.038359 | -0.0296 | 0.077465 | 0.062687 | -0.048986 | 0.034169 | 0.12042 | 0.000355 | -0.065162 | 0.066545 | 0.11478 | -0.010597 | 0.038029 | -0.032376 | 0.044766 | -0.06619 | 0.010952
1291.6719 | 121.6919 | -8.8806 | 112.8845 | 0.071489 | -0.090888 | 0.006315 | -0.057066 | 0.054577 | 0.026064 | -0.08103 | 0.006703 | 0.079217 | -0.036267 | -0.088049 | 0.043657 | 0.091891 | -0.038063 | 0.010563 | 0.098955 | -0.063422 | 0.033781 | -0.0296 | 0.082043 | 0.05353 | -0.053564 | 0.034169 | 0.10668 | -0.008801 | -0.060583 | 0.071123 | 0.11936 | -0.010597 | 0.038029 | -0.036954 | 0.044766 | -0.079924 | 0.001796
1293.4219 | 121.8796 | -8.6472 | 113.0859 | 0.062332 | -0.086309 | 0.010893 | -0.052488 | 0.049999 | 0.030642 | -0.085608 | 0.002124 | 0.088375 | -0.036267 | -0.088049 | 0.039079 | 0.10105 | -0.038063 | 0.019719 | 0.089798 | -0.058843 | 0.038359 | -0.025022 | 0.077465 | 0.058108 | -0.058142 | 0.02959 | 0.11584 | -0.008801 | -0.060583 | 0.066545 | 0.12851 | -0.010597 | 0.047185 | -0.036955 | 0.040187 | -0.075346 | 0.001796
1295.1562 | 121.7972 | -9.2514 | 112.4771 | 0.071489 | -0.08173 | 0.010893 | -0.057066 | 0.054577 | 0.030642 | -0.08103 | 0.006703 | 0.088375 | -0.031689 | -0.10179 | 0.039079 | 0.082735 | -0.042641 | 0.010563 | 0.098955 | -0.054264 | 0.038359 | -0.0296 | 0.082043 | 0.058108 | -0.053564 | 0.034169 | 0.11584 | -0.004223 | -0.07432 | 0.066545 | 0.1102 | -0.015175 | 0.038029 | -0.032376 | 0.049344 | -0.070768 | 0.010952
1296.9062 | 121.8155 | -9.3063 | 112.4634 | 0.071489 | -0.086309 | -0.002842 | -0.057066 | 0.059155 | 0.035221 | -0.08103 | 0.006703 | 0.083796 | -0.036267 | -0.092628 | 0.034501 | 0.082735 | -0.04722 | 0.019719 | 0.098955 | -0.058843 | 0.024624 | -0.0296 | 0.086621 | 0.062687 | -0.053564 | 0.034169 | 0.11126 | -0.008801 | -0.065162 | 0.061967 | 0.1102 | -0.019754 | 0.047185 | -0.027798 | 0.053923 | -0.070768 | 0.010953
1298.5938 | 121.8384 | -8.8486 | 112.9028 | 0.06691 | -0.08173 | 0.001736 | -0.052488 | 0.045421 | 0.021485 | -0.08103 | 0.011281 | 0.088375 | -0.031689 | -0.092628 | 0.039079 | 0.087313 | -0.038063 | 0.024297 | 0.094376 | -0.054264 | 0.029202 | -0.025022 | 0.072887 | 0.048951 | -0.053564 | 0.038747 | 0.11584 | -0.004223 | -0.065162 | 0.066545 | 0.11478 | -0.010597 | 0.051763 | -0.027798 | 0.049344 | -0.070768 | 0.006374
1300.3438 | 121.8246 | -8.3817 | 113.4064 | 0.071489 | -0.086309 | 0.001736 | -0.052488 | 0.063733 | 0.030642 | -0.076452 | 0.011281 | 0.088375 | -0.031689 | -0.097207 | 0.034501 | 0.082735 | -0.042641 | 0.015141 | 0.098955 | -0.058843 | 0.029202 | -0.025022 | 0.091199 | 0.058108 | -0.048986 | 0.038747 | 0.11584 | -0.004223 | -0.069741 | 0.061967 | 0.1102 | -0.015175 | 0.042607 | -0.02322 | 0.053922 | -0.06619 | 0.010952
1302.0625 | 121.7743 | -8.8989 | 112.9211 | 0.062332 | -0.077151 | 0.001736 | -0.052488 | 0.049999 | 0.035221 | -0.076452 | -0.002454 | 0.088375 | -0.031689 | -0.097207 | 0.039079 | 0.078157 | -0.042641 | 0.015141 | 0.089798 | -0.049685 | 0.029202 | -0.025022 | 0.077465 | 0.062687 | -0.048986 | 0.025012 | 0.11584 | -0.004223 | -0.069741 | 0.066545 | 0.10562 | -0.015175 | 0.042607 | -0.041533 | 0.040187 | -0.070768 | 0.010952
1303.7656 | 121.9162 | -8.1116 | 113.6261 | 0.062332 | -0.086309 | -0.007421 | -0.061645 | 0.045421 | 0.026064 | -0.08103 | 0.002124 | 0.088375 | -0.031689 | -0.097207 | 0.043657 | 0.087313 | -0.042641 | 0.019719 | 0.089798 | -0.058843 | 0.020045 | -0.034179 | 0.072887 | 0.05353 | -0.053564 | 0.02959 | 0.11584 | -0.004223 | -0.069741 | 0.071123 | 0.11478 | -0.015175 | 0.047185 | -0.041533 | 0.044765 | -0.075346 | 0.010952
1305.4531 | 121.9574 | -8.4457 | 113.2874 | 0.06691 | -0.086309 | -0.002842 | -0.057066 | 0.054577 | 0.021485 | -0.08103 | 0.011281 | 0.088375 | -0.036267 | -0.092628 | 0.039079 | 0.082735 | -0.042641 | 0.024297 | 0.094376 | -0.058843 | 0.024624 | -0.0296 | 0.082043 | 0.048951 | -0.053564 | 0.038747 | 0.11584 | -0.008801 | -0.065162 | 0.066545 | 0.1102 | -0.015175 | 0.051763 | -0.027798 | 0.053922 | -0.075346 | 0.006374
1307.1562 | 121.907 | -8.8852 | 112.8616 | 0.071489 | -0.08173 | -0.002842 | -0.052488 | 0.059155 | 0.026064 | -0.076452 | 0.002124 | 0.083796 | -0.031689 | -0.092628 | 0.043657 | 0.087313 | -0.033484 | 0.010563 | 0.098955 | -0.054264 | 0.024624 | -0.025022 | 0.086621 | 0.05353 | -0.048986 | 0.02959 | 0.11126 | -0.004223 | -0.065162 | 0.071123 | 0.11478 | -0.006018 | 0.038029 | -0.041533 | 0.035608 | -0.075346 | 0.001795
1308.8438 | 121.9345 | -8.2855 | 113.4842 | 0.06691 | -0.086309 | 0.006315 | -0.052488 | 0.054577 | 0.026064 | -0.08103 | 0.002124 | 0.092954 | -0.036267 | -0.097207 | 0.034501 | 0.082735 | -0.038063 | 0.019719 | 0.094376 | -0.058843 | 0.033781 | -0.025022 | 0.082043 | 0.05353 | -0.053564 | 0.02959 | 0.12042 | -0.008801 | -0.069741 | 0.061967 | 0.1102 | -0.010597 | 0.047185 | -0.032377 | 0.040187 | -0.070768 | 0.001796
1310.5469 | 121.9666 | -8.931 | 112.8204 | 0.071489 | -0.090888 | 0.006315 | -0.052488 | 0.045421 | 0.026064 | -0.085608 | 0.011281 | 0.083796 | -0.036267 | -0.092628 | 0.039079 | 0.082735 | -0.033484 | 0.019719 | 0.098955 | -0.063422 | 0.033781 | -0.025022 | 0.072887 | 0.05353 | -0.058142 | 0.038747 | 0.11126 | -0.008801 | -0.065162 | 0.066545 | 0.1102 | -0.006018 | 0.047185 | -0.027798 | 0.044765 | -0.075346 | -0.002783
1312.2344 | 121.8658 | -8.6197 | 113.1821 | 0.06691 | -0.077151 | 0.006315 | -0.052488 | 0.049999 | 0.030642 | -0.076452 | 0.006703 | 0.092954 | -0.031689 | -0.088049 | 0.029923 | 0.082735 | -0.038063 | 0.019719 | 0.094376 | -0.049685 | 0.033781 | -0.025022 | 0.077465 | 0.058108 | -0.048986 | 0.034169 | 0.12042 | -0.004223 | -0.060583 | 0.057389 | 0.1102 | -0.010597 | 0.047185 | -0.02322 | 0.044766 | -0.061612 | 0.006374
1313.9375 | 121.8704 | -8.9539 | 112.8708 | 0.06691 | -0.077151 | 0.001736 | -0.066223 | 0.054577 | 0.035221 | -0.08103 | 0.006703 | 0.088375 | -0.027111 | -0.092628 | 0.029923 | 0.091891 | -0.038063 | 0.015141 | 0.094376 | -0.049685 | 0.029202 | -0.038757 | 0.082043 | 0.062687 | -0.053564 | 0.034169 | 0.11584 | 0.000355 | -0.065162 | 0.057389 | 0.11936 | -0.010597 | 0.042607 | -0.02322 | 0.044766 | -0.057034 | 0.010952
1315.6094 | 121.8658 | -8.9722 | 112.8662 | 0.071489 | -0.08173 | 0.001736 | -0.047909 | 0.059155 | 0.021485 | -0.085608 | 0.006703 | 0.092954 | -0.027111 | -0.088049 | 0.039079 | 0.087313 | -0.038063 | 0.015141 | 0.098955 | -0.054264 | 0.029202 | -0.020443 | 0.086621 | 0.048951 | -0.058142 | 0.034169 | 0.12042 | 0.000355 | -0.060583 | 0.066545 | 0.11478 | -0.010597 | 0.042607 | -0.032376 | 0.044766 | -0.06619 | 0.010952
1317.2812 | 121.907 | -8.5281 | 113.2507 | 0.062332 | -0.086309 | 0.001736 | -0.057066 | 0.054577 | 0.026064 | -0.08103 | 0.002124 | 0.083796 | -0.031689 | -0.092628 | 0.043657 | 0.087313 | -0.042641 | 0.019719 | 0.089798 | -0.058843 | 0.029202 | -0.0296 | 0.082043 | 0.05353 | -0.053564 | 0.02959 | 0.11126 | -0.004223 | -0.065162 | 0.071123 | 0.11478 | -0.015175 | 0.047185 | -0.041533 | 0.044765 | -0.075346 | 0.010952
1318.9688 | 121.9711 | -8.725 | 113.0493 | 0.071489 | -0.08173 | 0.006315 | -0.061645 | 0.054577 | 0.026064 | -0.08103 | 0.002124 | 0.088375 | -0.040846 | -0.088049 | 0.039079 | 0.087313 | -0.033484 | 0.015141 | 0.098955 | -0.054264 | 0.033781 | -0.034179 | 0.082043 | 0.05353 | -0.053564 | 0.02959 | 0.11584 | -0.01338 | -0.060583 | 0.066545 | 0.11478 | -0.006018 | 0.042607 | -0.036955 | 0.035608 | -0.079925 | -0.007362
1320.6406 | 121.9666 | -9.05 | 112.7563 | 0.06691 | -0.08173 | -0.002842 | -0.047909 | 0.054577 | 0.030642 | -0.076452 | 0.011281 | 0.092954 | -0.031689 | -0.092628 | 0.039079 | 0.082735 | -0.033484 | 0.019719 | 0.094376 | -0.054264 | 0.024624 | -0.020443 | 0.082043 | 0.058108 | -0.048986 | 0.038747 | 0.12042 | -0.004223 | -0.065162 | 0.066545 | 0.1102 | -0.006018 | 0.047185 | -0.027798 | 0.044765 | -0.070768 | 0.001795
1322.3281 | 121.9803 | -8.6929 | 113.0676 | 0.06691 | -0.08173 | 0.001736 | -0.052488 | 0.054577 | 0.026064 | -0.08103 | 0.002124 | 0.088375 | -0.040846 | -0.088049 | 0.039079 | 0.082735 | -0.042641 | 0.015141 | 0.094376 | -0.054264 | 0.029202 | -0.025022 | 0.082043 | 0.05353 | -0.053564 | 0.02959 | 0.11584 | -0.01338 | -0.060583 | 0.066545 | 0.1102 | -0.015175 | 0.042607 | -0.036955 | 0.044765 | -0.079925 | 0.001795
1324 | 121.962 | -8.6746 | 113.0722 | 0.062332 | -0.08173 | 0.001736 | -0.061645 | 0.059155 | 0.030642 | -0.076452 | -0.002454 | 0.083796 | -0.031689 | -0.092628 | 0.034501 | 0.082735 | -0.042641 | 0.015141 | 0.089798 | -0.054264 | 0.029202 | -0.034179 | 0.086621 | 0.058108 | -0.048986 | 0.025012 | 0.11126 | -0.004223 | -0.065162 | 0.061967 | 0.1102 | -0.015175 | 0.042607 | -0.036955 | 0.040187 | -0.06619 | 0.010952
1325.6875 | 121.9162 | -8.7341 | 113.0402 | 0.06691 | -0.08173 | 0.001736 | -0.047909 | 0.054577 | 0.030642 | -0.08103 | 0.011281 | 0.088375 | -0.036267 | -0.097207 | 0.039079 | 0.087313 | -0.042641 | 0.019719 | 0.094376 | -0.054264 | 0.029202 | -0.020443 | 0.082043 | 0.058108 | -0.053564 | 0.038747 | 0.11584 | -0.008801 | -0.069741 | 0.066545 | 0.11478 | -0.015175 | 0.047185 | -0.027798 | 0.053922 | -0.075346 | 0.006374
1327.4062 | 121.9299 | -14.6896 | 107.1259 | 0.06691 | -0.086309 | 0.010893 | -0.047909 | 0.059155 | 0.039799 | -0.067295 | 0.011281 | 0.092954 | -0.027111 | -0.092628 | 0.020767 | 0.087313 | -0.042641 | 0.015141 | 0.094376 | -0.058843 | 0.038359 | -0.020443 | 0.086621 | 0.067265 | -0.039829 | 0.038747 | 0.12042 | 0.000355 | -0.065162 | 0.048233 | 0.11478 | -0.015175 | 0.042607 | -0.009486 | 0.053922 | -0.047878 | 0.01553
1329.0938 | 121.8567 | -12.4008 | 109.4604 | 0.071489 | -0.08173 | 0.001736 | -0.052488 | 0.059155 | 0.035221 | -0.08103 | 0.006703 | 0.088375 | -0.027111 | -0.088049 | 0.039079 | 0.082735 | -0.038063 | 0.015141 | 0.098955 | -0.054264 | 0.029202 | -0.025022 | 0.086621 | 0.062687 | -0.053564 | 0.034169 | 0.11584 | 0.000355 | -0.060583 | 0.066545 | 0.1102 | -0.010597 | 0.042607 | -0.032376 | 0.044766 | -0.06619 | 0.010952
1330.8594 | 121.843 | -11.3068 | 110.5362 | 0.071489 | -0.08173 | -0.002842 | -0.047909 | 0.059155 | 0.026064 | -0.08103 | 0.006703 | 0.092954 | -0.036267 | -0.097207 | 0.029923 | 0.082735 | -0.042641 | 0.015141 | 0.098955 | -0.054264 | 0.024624 | -0.020443 | 0.086621 | 0.05353 | -0.053564 | 0.034169 | 0.12042 | -0.008801 | -0.069741 | 0.057389 | 0.1102 | -0.015175 | 0.042607 | -0.02322 | 0.049344 | -0.06619 | 0.006374
1332.5938 | 121.8384 | -11.5036 | 110.3806 | 0.076067 | -0.086309 | 0.006315 | -0.052488 | 0.049999 | 0.035221 | -0.076452 | 0.002124 | 0.088375 | -0.031689 | -0.092628 | 0.029923 | 0.082735 | -0.038063 | 0.010563 | 0.10353 | -0.058843 | 0.033781 | -0.025022 | 0.077465 | 0.062687 | -0.048986 | 0.02959 | 0.11584 | -0.004223 | -0.065162 | 0.057389 | 0.1102 | -0.010597 | 0.038029 | -0.027799 | 0.040187 | -0.061612 | 0.006374
1334.2812 | 121.9254 | -11.2015 | 110.5728 | 0.062332 | -0.077151 | -0.007421 | -0.057066 | 0.049999 | 0.030642 | -0.076452 | 0.011281 | 0.088375 | -0.031689 | -0.088049 | 0.039079 | 0.087313 | -0.033484 | 0.010563 | 0.089798 | -0.049685 | 0.020045 | -0.0296 | 0.077465 | 0.058108 | -0.048986 | 0.038747 | 0.11584 | -0.004223 | -0.060583 | 0.066545 | 0.11478 | -0.006018 | 0.038029 | -0.027798 | 0.044765 | -0.070768 | 0.001795
1336.0312 | 121.8521 | -11.1786 | 110.6873 | 0.06691 | -0.077151 | 0.001736 | -0.043331 | 0.054577 | 0.030642 | -0.08103 | 0.002124 | 0.088375 | -0.031689 | -0.088049 | 0.043657 | 0.087313 | -0.042641 | 0.015141 | 0.094376 | -0.049685 | 0.029202 | -0.015865 | 0.082043 | 0.058108 | -0.053564 | 0.02959 | 0.11584 | -0.004223 | -0.060583 | 0.071123 | 0.11478 | -0.015175 | 0.042607 | -0.041533 | 0.044765 | -0.075346 | 0.010952
1337.7812 | 121.9757 | -11.3388 | 110.4538 | 0.06691 | -0.086309 | 0.006315 | -0.052488 | 0.059155 | 0.030642 | -0.08103 | 0.002124 | 0.097532 | -0.031689 | -0.088049 | 0.034501 | 0.087313 | -0.038063 | 0.015141 | 0.094376 | -0.058843 | 0.033781 | -0.025022 | 0.086621 | 0.058108 | -0.053564 | 0.02959 | 0.125 | -0.004223 | -0.060583 | 0.061967 | 0.11478 | -0.010597 | 0.042607 | -0.032377 | 0.040187 | -0.06619 | 0.006374
1339.5312 | 121.8384 | -11.2473 | 110.582 | 0.071489 | -0.077151 | 0.006315 | -0.047909 | 0.054577 | 0.039799 | -0.076452 | 0.006703 | 0.088375 | -0.027111 | -0.097207 | 0.039079 | 0.078157 | -0.042641 | 0.019719 | 0.098955 | -0.049685 | 0.033781 | -0.020443 | 0.082043 | 0.067265 | -0.048986 | 0.034169 | 0.11584 | 0.000355 | -0.069741 | 0.066545 | 0.10562 | -0.015175 | 0.047185 | -0.032376 | 0.049344 | -0.06619 | 0.01553
1341.2188 | 121.8796 | -11.1832 | 110.6598 | 0.071489 | -0.077151 | 0.010893 | -0.047909 | 0.063733 | 0.030642 | -0.08103 | 0.006703 | 0.097532 | -0.027111 | -0.092628 | 0.039079 | 0.082735 | -0.042641 | 0.024297 | 0.098955 | -0.049685 | 0.038359 | -0.020443 | 0.091199 | 0.058108 | -0.053564 | 0.034169 | 0.125 | 0.000355 | -0.065162 | 0.066545 | 0.1102 | -0.015175 | 0.051763 | -0.032376 | 0.049344 | -0.06619 | 0.01553
1342.9531 | 121.9666 | -9.6359 | 112.1384 | 0.071489 | -0.08173 | 0.006315 | -0.052488 | 0.059155 | 0.035221 | -0.076452 | 0.002124 | 0.092954 | -0.027111 | -0.092628 | 0.039079 | 0.087313 | -0.038063 | 0.015141 | 0.098955 | -0.054264 | 0.033781 | -0.025022 | 0.086621 | 0.062687 | -0.048986 | 0.02959 | 0.12042 | 0.000355 | -0.065162 | 0.066545 | 0.11478 | -0.010597 | 0.042607 | -0.036955 | 0.040187 | -0.06619 | 0.010952
1344.7031 | 121.8658 | -9.4711 | 112.3856 | 0.062332 | -0.08173 | 0.006315 | -0.047909 | 0.054577 | 0.035221 | -0.090186 | 0.002124 | 0.088375 | -0.027111 | -0.092628 | 0.029923 | 0.091891 | -0.038063 | 0.019719 | 0.089798 | -0.054264 | 0.033781 | -0.020443 | 0.082043 | 0.062687 | -0.06272 | 0.02959 | 0.11584 | 0.000355 | -0.065162 | 0.057389 | 0.11936 | -0.010597 | 0.047185 | -0.027799 | 0.040187 | -0.057034 | 0.010952
1346.4531 | 121.8658 | -9.8923 | 111.9781 | 0.06691 | -0.077151 | 0.006315 | -0.047909 | 0.054577 | 0.030642 | -0.076452 | 0.002124 | 0.083796 | -0.036267 | -0.097207 | 0.039079 | 0.087313 | -0.042641 | 0.015141 | 0.094376 | -0.049685 | 0.033781 | -0.020443 | 0.082043 | 0.058108 | -0.048986 | 0.02959 | 0.11126 | -0.008801 | -0.069741 | 0.066545 | 0.11478 | -0.015175 | 0.042607 | -0.036955 | 0.044765 | -0.075346 | 0.006374
1348.1406 | 117.5903 | -7.814 | 109.8175 | 0.06691 | -0.086309 | 0.006315 | -0.052488 | 0.059155 | 0.035221 | -0.08103 | 0.002124 | 0.088375 | -0.027111 | -0.092628 | 0.034501 | 0.078157 | -0.033484 | 0.010563 | 0.094376 | -0.058843 | 0.033781 | -0.025022 | 0.086621 | 0.062687 | -0.053564 | 0.02959 | 0.11584 | 0.000355 | -0.065162 | 0.061967 | 0.10562 | -0.006018 | 0.038029 | -0.032377 | 0.035608 | -0.061612 | 0.006373
1349.875 | 116.9998 | -9.7595 | 107.2861 | 0.071489 | -0.077151 | 0.001736 | -0.043331 | 0.059155 | 0.035221 | -0.076452 | 0.002124 | 0.088375 | -0.027111 | -0.097207 | 0.039079 | 0.087313 | -0.038063 | 0.015141 | 0.098955 | -0.049685 | 0.029202 | -0.015865 | 0.086621 | 0.062687 | -0.048986 | 0.02959 | 0.11584 | 0.000355 | -0.069741 | 0.066545 | 0.11478 | -0.010597 | 0.042607 | -0.036955 | 0.040187 | -0.06619 | 0.010952
1351.5469 | 116.7206 | -9.5673 | 107.0206 | 0.062332 | -0.086309 | 0.001736 | -0.052488 | 0.054577 | 0.026064 | -0.08103 | 0.002124 | 0.088375 | -0.031689 | -0.097207 | 0.034501 | 0.091891 | -0.042641 | 0.015141 | 0.089798 | -0.058843 | 0.029202 | -0.025022 | 0.082043 | 0.05353 | -0.053564 | 0.02959 | 0.11584 | -0.004223 | -0.069741 | 0.061967 | 0.11936 | -0.015175 | 0.042607 | -0.032377 | 0.044765 | -0.06619 | 0.010952
1353.2812 | 116.4322 | -9.0866 | 107.1487 | 0.06691 | -0.08173 | 0.010893 | -0.061645 | 0.054577 | 0.030642 | -0.076452 | 0.006703 | 0.088375 | -0.027111 | -0.088049 | 0.039079 | 0.091891 | -0.033484 | 0.010563 | 0.094376 | -0.054264 | 0.038359 | -0.034179 | 0.082043 | 0.058108 | -0.048986 | 0.034169 | 0.11584 | 0.000355 | -0.060583 | 0.066545 | 0.11936 | -0.006018 | 0.038029 | -0.032376 | 0.040187 | -0.06619 | 0.006373
1354.9531 | 116.0568 | -9.1461 | 106.9199 | 0.06691 | -0.077151 | 0.006315 | -0.057066 | 0.054577 | 0.026064 | -0.08103 | 0.011281 | 0.088375 | -0.031689 | -0.10179 | 0.039079 | 0.087313 | -0.042641 | 0.019719 | 0.094376 | -0.049685 | 0.033781 | -0.0296 | 0.082043 | 0.05353 | -0.053564 | 0.038747 | 0.11584 | -0.004223 | -0.07432 | 0.066545 | 0.11478 | -0.015175 | 0.047185 | -0.027798 | 0.053922 | -0.070768 | 0.010952
1356.6875 | 115.9012 | -9.137 | 106.6315 | 0.071489 | -0.08173 | 0.001736 | -0.057066 | 0.049999 | 0.030642 | -0.08103 | 0.006703 | 0.092954 | -0.027111 | -0.097207 | 0.034501 | 0.082735 | -0.042641 | 0.019719 | 0.098955 | -0.054264 | 0.029202 | -0.0296 | 0.077465 | 0.058108 | -0.053564 | 0.034169 | 0.12042 | 0.000355 | -0.069741 | 0.061967 | 0.1102 | -0.015175 | 0.047185 | -0.027798 | 0.049344 | -0.061612 | 0.01553
1358.375 | 115.6998 | -89.6942 | 25.795 | 0.11727 | -0.031363 | 0.052101 | -0.011281 | 0.10493 | 0.076426 | -0.035248 | 0.052488 | 0.13874 | 0.032407 | -0.10637 | 0.007032 | 0.04611 | -0.060955 | -0.012328 | 0.14474 | -0.003897 | 0.079567 | 0.016185 | 0.1324 | 0.10389 | -0.007782 | 0.079954 | 0.16621 | 0.059873 | -0.078899 | 0.034498 | 0.073576 | -0.033489 | 0.015138 | 0.045456 | 0.11344 | 0.025375 | 0.093362
1360.0469 | 115.6952 | -89.5706 | 25.7172 | 0.11269 | -0.0451 | 0.061258 | -0.006703 | 0.0912 | 0.067269 | -0.039826 | 0.057066 | 0.13874 | 0.046142 | -0.11552 | 0.007032 | 0.04611 | -0.065533 | -0.00775 | 0.14016 | -0.017634 | 0.088724 | 0.020763 | 0.11867 | 0.094735 | -0.01236 | 0.084532 | 0.16621 | 0.073608 | -0.088057 | 0.034498 | 0.073576 | -0.038067 | 0.019716 | 0.050034 | 0.1226 | 0.03911 | 0.11167
1361.7812 | 115.5487 | -89.5569 | 25.6897 | 0.11727 | -0.040521 | 0.052101 | -0.006703 | 0.10036 | 0.076426 | -0.03067 | 0.043331 | 0.13416 | 0.041563 | -0.10637 | 0.01161 | 0.036954 | -0.060955 | -0.00775 | 0.14474 | -0.013055 | 0.079567 | 0.020763 | 0.12782 | 0.10389 | -0.003204 | 0.070797 | 0.16163 | 0.069029 | -0.078899 | 0.039076 | 0.06442 | -0.033489 | 0.019716 | 0.031721 | 0.10429 | 0.029953 | 0.10252
1363.4688 | 115.3473 | -89.4974 | 25.7034 | 0.12185 | -0.035942 | 0.047522 | -0.006703 | 0.10951 | 0.076426 | -0.039826 | 0.047909 | 0.13416 | 0.041563 | -0.10637 | 0.002454 | 0.036954 | -0.060955 | -0.00775 | 0.14932 | -0.008476 | 0.074988 | 0.020763 | 0.13698 | 0.10389 | -0.01236 | 0.075375 | 0.16163 | 0.069029 | -0.078899 | 0.02992 | 0.06442 | -0.033489 | 0.019716 | 0.045455 | 0.10886 | 0.039109 | 0.10252
1365.2188 | 115.2237 | -89.4608 | 25.6668 | 0.12185 | -0.035942 | 0.047522 | -0.006703 | 0.10493 | 0.067269 | -0.039826 | 0.057066 | 0.13874 | 0.041563 | -0.11094 | 0.002454 | 0.032376 | -0.065533 | -0.016906 | 0.14932 | -0.008476 | 0.074988 | 0.020763 | 0.1324 | 0.094735 | -0.01236 | 0.084532 | 0.16621 | 0.069029 | -0.083478 | 0.02992 | 0.059842 | -0.038067 | 0.01056 | 0.054612 | 0.1226 | 0.039109 | 0.1071
1366.9531 | 115.1733 | -89.4012 | 25.6348 | 0.11727 | -0.031363 | 0.052101 | -0.006703 | 0.10036 | 0.071848 | -0.039826 | 0.047909 | 0.14332 | 0.032407 | -0.11094 | 0.01161 | 0.032376 | -0.070112 | -0.00775 | 0.14474 | -0.003897 | 0.079567 | 0.020763 | 0.12782 | 0.099314 | -0.01236 | 0.075375 | 0.17079 | 0.059873 | -0.083478 | 0.039076 | 0.059842 | -0.042646 | 0.019716 | 0.036299 | 0.11802 | 0.020797 | 0.10252
1368.6406 | 115.2145 | -89.3143 | 25.6073 | 0.11727 | -0.0451 | 0.052101 | -0.006703 | 0.10036 | 0.071848 | -0.035248 | 0.047909 | 0.13874 | 0.02325 | -0.10179 | 0.01161 | 0.041532 | -0.056376 | -0.016906 | 0.14474 | -0.017634 | 0.079567 | 0.020763 | 0.12782 | 0.099314 | -0.007782 | 0.075375 | 0.16621 | 0.050716 | -0.07432 | 0.039076 | 0.068998 | -0.02891 | 0.01056 | 0.036299 | 0.10429 | 0.01164 | 0.079626
1370.3906 | 115.1047 | -89.3417 | 25.6256 | 0.11727 | -0.040521 | 0.047522 | -0.01586 | 0.10036 | 0.071848 | -0.035248 | 0.052488 | 0.13874 | 0.032407 | -0.10179 | 0.01161 | 0.036954 | -0.065533 | 0.001406 | 0.14474 | -0.013055 | 0.074988 | 0.011606 | 0.12782 | 0.099314 | -0.007782 | 0.079954 | 0.16621 | 0.059873 | -0.07432 | 0.039076 | 0.06442 | -0.038067 | 0.028872 | 0.040878 | 0.11802 | 0.020797 | 0.09794
1372.125 | 115.0269 | -89.2868 | 25.589 | 0.10812 | -0.040521 | 0.056679 | -0.006703 | 0.10036 | 0.081005 | -0.035248 | 0.057066 | 0.12958 | 0.041563 | -0.10637 | 0.007032 | 0.036954 | -0.060955 | -0.016906 | 0.13558 | -0.013055 | 0.084145 | 0.020763 | 0.12782 | 0.10847 | -0.007782 | 0.084532 | 0.15705 | 0.069029 | -0.078899 | 0.034498 | 0.06442 | -0.033489 | 0.01056 | 0.050034 | 0.11802 | 0.034531 | 0.10252
1373.875 | 115.0772 | -89.2685 | 25.5569 | 0.11727 | -0.040521 | 0.061258 | -0.011281 | 0.0912 | 0.076426 | -0.035248 | 0.052488 | 0.13416 | 0.02325 | -0.11094 | 0.007032 | 0.036954 | -0.065533 | -0.021484 | 0.14474 | -0.013055 | 0.088724 | 0.016185 | 0.11867 | 0.10389 | -0.007782 | 0.079954 | 0.16163 | 0.050716 | -0.083478 | 0.034498 | 0.06442 | -0.038067 | 0.005982 | 0.045456 | 0.11802 | 0.016218 | 0.088783
1375.5625 | 114.9673 | -89.2593 | 25.5341 | 0.10812 | -0.0451 | 0.047522 | -0.011281 | 0.095778 | 0.076426 | -0.039826 | 0.052488 | 0.13874 | 0.041563 | -0.10637 | 0.002454 | 0.036954 | -0.060955 | -0.012328 | 0.13558 | -0.017634 | 0.074988 | 0.016185 | 0.12324 | 0.10389 | -0.01236 | 0.079954 | 0.16621 | 0.069029 | -0.078899 | 0.02992 | 0.06442 | -0.033489 | 0.015138 | 0.050034 | 0.11344 | 0.039109 | 0.10252
1377.3125 | 114.9765 | -89.2731 | 25.5753 | 0.10812 | -0.0451 | 0.052101 | -0.006703 | 0.10036 | 0.076426 | -0.035248 | 0.057066 | 0.13416 | 0.027829 | -0.10637 | 0.007032 | 0.036954 | -0.065533 | -0.00775 | 0.13558 | -0.017634 | 0.079567 | 0.020763 | 0.12782 | 0.10389 | -0.007782 | 0.084532 | 0.16163 | 0.055295 | -0.078899 | 0.034498 | 0.06442 | -0.038067 | 0.019716 | 0.050034 | 0.1226 | 0.020797 | 0.093362
1379.0625 | 115.004 | -89.2365 | 25.5203 | 0.11727 | -0.049678 | 0.047522 | -0.006703 | 0.095778 | 0.076426 | -0.035248 | 0.043331 | 0.12958 | 0.032407 | -0.10179 | 0.01161 | 0.04611 | -0.065533 | -0.012328 | 0.14474 | -0.022212 | 0.074988 | 0.020763 | 0.12324 | 0.10389 | -0.007782 | 0.070797 | 0.15705 | 0.059873 | -0.07432 | 0.039076 | 0.073576 | -0.038067 | 0.015138 | 0.031721 | 0.10886 | 0.020797 | 0.09794
1380.75 | 114.8895 | -89.2502 | 25.5524 | 0.11727 | -0.035942 | 0.052101 | -0.011281 | 0.095778 | 0.076426 | -0.035248 | 0.047909 | 0.13874 | 0.032407 | -0.10637 | 0.007032 | 0.036954 | -0.060955 | -0.016906 | 0.14474 | -0.008476 | 0.079567 | 0.016185 | 0.12324 | 0.10389 | -0.007782 | 0.075375 | 0.16621 | 0.059873 | -0.078899 | 0.034498 | 0.06442 | -0.033489 | 0.01056 | 0.040877 | 0.10886 | 0.025375 | 0.093362
1382.4844 | 114.949 | -89.2456 | 25.5249 | 0.11269 | -0.040521 | 0.056679 | -0.006703 | 0.10036 | 0.071848 | -0.035248 | 0.057066 | 0.13874 | 0.032407 | -0.10179 | 0.007032 | 0.041532 | -0.065533 | -0.016906 | 0.14016 | -0.013055 | 0.084145 | 0.020763 | 0.12782 | 0.099314 | -0.007782 | 0.084532 | 0.16621 | 0.059873 | -0.07432 | 0.034498 | 0.068998 | -0.038067 | 0.01056 | 0.050034 | 0.1226 | 0.025375 | 0.09794
1384.1719 | 114.9902 | -89.2227 | 25.502 | 0.11727 | -0.049678 | 0.047522 | -0.01586 | 0.095778 | 0.067269 | -0.044405 | 0.052488 | 0.13874 | 0.032407 | -0.10637 | 0.002454 | 0.032376 | -0.065533 | -0.00775 | 0.14474 | -0.022212 | 0.074988 | 0.011606 | 0.12324 | 0.094735 | -0.016939 | 0.079954 | 0.16621 | 0.059873 | -0.078899 | 0.02992 | 0.059842 | -0.038067 | 0.019716 | 0.050034 | 0.11802 | 0.029953 | 0.09794
1385.9375 | 115.004 | -89.2639 | 25.5249 | 0.11727 | -0.035942 | 0.052101 | -0.002124 | 0.10493 | 0.081005 | -0.035248 | 0.052488 | 0.13874 | 0.032407 | -0.10179 | 0.007032 | 0.036954 | -0.065533 | -0.00775 | 0.14474 | -0.008476 | 0.079567 | 0.025342 | 0.1324 | 0.10847 | -0.007782 | 0.079954 | 0.16621 | 0.059873 | -0.07432 | 0.034498 | 0.06442 | -0.038067 | 0.019716 | 0.045456 | 0.11802 | 0.025375 | 0.09794
1387.6875 | 118.0756 | -117.6453 | 0.32044 | 0.12643 | -0.022205 | 0.070415 | 0.011611 | 0.10493 | 0.085583 | -0.026092 | 0.066223 | 0.14332 | 0.055298 | -0.10637 | -0.006702 | 0.027798 | -0.070112 | -0.021484 | 0.1539 | 0.005261 | 0.097881 | 0.039077 | 0.1324 | 0.11305 | 0.001374 | 0.093689 | 0.17079 | 0.082764 | -0.078899 | 0.020764 | 0.055264 | -0.042646 | 0.005982 | 0.072925 | 0.13633 | 0.062 | 0.12541
1389.3594 | 118.5196 | -117.9565 | 0.27008 | 0.12643 | -0.026784 | 0.061258 | 0.002454 | 0.10951 | 0.085583 | -0.021514 | 0.061645 | 0.15248 | 0.055298 | -0.11552 | -0.002124 | 0.027798 | -0.065533 | -0.021484 | 0.1539 | 0.000682 | 0.088724 | 0.02992 | 0.13698 | 0.11305 | 0.005952 | 0.089111 | 0.17994 | 0.082764 | -0.088057 | 0.025342 | 0.055264 | -0.038067 | 0.005982 | 0.063769 | 0.12718 | 0.057422 | 0.12083
1391.0312 | 118.5425 | -118.2083 | 0.3067 | 0.12643 | -0.022205 | 0.070415 | 0.002454 | 0.11409 | 0.09474 | -0.021514 | 0.070802 | 0.1479 | 0.046142 | -0.10637 | -0.002124 | 0.027798 | -0.07469 | -0.016906 | 0.1539 | 0.005261 | 0.097881 | 0.02992 | 0.14156 | 0.12221 | 0.005952 | 0.098268 | 0.17536 | 0.073608 | -0.078899 | 0.025342 | 0.055264 | -0.047224 | 0.01056 | 0.072926 | 0.14549 | 0.048266 | 0.12083
1392.7656 | 118.689 | -118.2495 | 0.32501 | 0.13101 | -0.026784 | 0.070415 | 0.011611 | 0.10951 | 0.09474 | -0.016936 | 0.061645 | 0.1479 | 0.05072 | -0.11552 | -0.002124 | 0.027798 | -0.065533 | -0.026063 | 0.15847 | 0.000682 | 0.097881 | 0.039077 | 0.13698 | 0.12221 | 0.01053 | 0.089111 | 0.17536 | 0.078186 | -0.088057 | 0.025342 | 0.055264 | -0.038067 | 0.001403 | 0.063769 | 0.12718 | 0.052844 | 0.11625
1394.5156 | 118.8263 | -118.3228 | 0.3479 | 0.12643 | -0.026784 | 0.065837 | 0.011611 | 0.10951 | 0.090161 | -0.026092 | 0.061645 | 0.15248 | 0.05072 | -0.11552 | -0.002124 | 0.032376 | -0.065533 | -0.012328 | 0.1539 | 0.000682 | 0.093303 | 0.039077 | 0.13698 | 0.11763 | 0.001374 | 0.089111 | 0.17994 | 0.078186 | -0.088057 | 0.025342 | 0.059842 | -0.038067 | 0.015138 | 0.063769 | 0.12718 | 0.052844 | 0.11625
1396.1875 | 118.8538 | -118.5242 | 0.27466 | 0.13101 | -0.031363 | 0.070415 | 0.002454 | 0.11409 | 0.090161 | -0.026092 | 0.061645 | 0.1479 | 0.046142 | -0.11094 | -0.002124 | 0.014064 | -0.070112 | -0.021484 | 0.15847 | -0.003897 | 0.097881 | 0.02992 | 0.14156 | 0.11763 | 0.001374 | 0.089111 | 0.17536 | 0.073608 | -0.083478 | 0.025342 | 0.04153 | -0.042646 | 0.005982 | 0.063769 | 0.13176 | 0.048266 | 0.11625
1397.9375 | 119.0369 | -118.5791 | 0.24719 | 0.13559 | -0.026784 | 0.065837 | -0.002124 | 0.11409 | 0.085583 | -0.026092 | 0.061645 | 0.15706 | 0.046142 | -0.11552 | -0.006702 | 0.02322 | -0.07469 | -0.021484 | 0.16305 | 0.000682 | 0.093303 | 0.025342 | 0.14156 | 0.11305 | 0.001374 | 0.089111 | 0.18452 | 0.073608 | -0.088057 | 0.020764 | 0.050686 | -0.047224 | 0.005982 | 0.068347 | 0.13634 | 0.052844 | 0.12083
1399.6875 | 119.0231 | -118.7119 | 0.27466 | 0.13101 | -0.026784 | 0.074994 | 0.007033 | 0.11409 | 0.085583 | -0.026092 | 0.061645 | 0.1479 | 0.046142 | -0.10179 | -0.002124 | 0.02322 | -0.070112 | -0.016906 | 0.15847 | 0.000682 | 0.10246 | 0.034499 | 0.14156 | 0.11305 | 0.001374 | 0.089111 | 0.17536 | 0.073608 | -0.07432 | 0.025342 | 0.050686 | -0.042646 | 0.01056 | 0.063769 | 0.13176 | 0.048266 | 0.11625
1401.4219 | 119.0964 | -118.7668 | 0.27466 | 0.13101 | -0.026784 | 0.061258 | 0.007033 | 0.10951 | 0.085583 | -0.021514 | 0.066223 | 0.15706 | 0.046142 | -0.10637 | 0.002454 | 0.02322 | -0.07469 | -0.021484 | 0.15847 | 0.000682 | 0.088724 | 0.034499 | 0.13698 | 0.11305 | 0.005952 | 0.093689 | 0.18452 | 0.073608 | -0.078899 | 0.02992 | 0.050686 | -0.047224 | 0.005982 | 0.063769 | 0.14091 | 0.043688 | 0.12083
1403.1094 | 119.1925 | -118.8538 | 0.29755 | 0.13101 | -0.031363 | 0.070415 | 0.011611 | 0.10951 | 0.085583 | -0.026092 | 0.07538 | 0.1479 | 0.046142 | -0.11094 | -0.006702 | 0.027798 | -0.07469 | -0.016906 | 0.15847 | -0.003897 | 0.097881 | 0.039077 | 0.13698 | 0.11305 | 0.001374 | 0.10285 | 0.17536 | 0.073608 | -0.083478 | 0.020764 | 0.055264 | -0.047224 | 0.01056 | 0.082082 | 0.15007 | 0.052844 | 0.12083
1404.8594 | 119.3253 | -118.9041 | 0.27008 | 0.12185 | -0.031363 | 0.070415 | -0.002124 | 0.10951 | 0.085583 | -0.021514 | 0.066223 | 0.15248 | 0.059877 | -0.11094 | -0.002124 | 0.027798 | -0.070112 | -0.021484 | 0.14932 | -0.003897 | 0.097881 | 0.025342 | 0.13698 | 0.11305 | 0.005952 | 0.093689 | 0.17994 | 0.087343 | -0.083478 | 0.025342 | 0.055264 | -0.042646 | 0.005982 | 0.068347 | 0.13633 | 0.062001 | 0.12999
1406.5938 | 119.4397 | -118.9728 | 0.2655 | 0.12643 | -0.035942 | 0.061258 | 0.01619 | 0.11867 | 0.081005 | -0.03067 | 0.070802 | 0.15706 | 0.05072 | -0.10179 | -0.011281 | 0.02322 | -0.065533 | -0.021484 | 0.1539 | -0.008476 | 0.088724 | 0.043656 | 0.14613 | 0.10847 | -0.003204 | 0.098268 | 0.18452 | 0.078186 | -0.07432 | 0.016185 | 0.050686 | -0.038067 | 0.005982 | 0.082083 | 0.13633 | 0.062001 | 0.11625
1408.2656 | 119.4214 | -118.9865 | 0.31128 | 0.12185 | -0.031363 | 0.065837 | 0.011611 | 0.11409 | 0.085583 | -0.026092 | 0.066223 | 0.15248 | 0.05072 | -0.10179 | -0.006702 | 0.027798 | -0.07469 | -0.016906 | 0.14932 | -0.003897 | 0.093303 | 0.039077 | 0.14156 | 0.11305 | 0.001374 | 0.093689 | 0.17994 | 0.078186 | -0.07432 | 0.020764 | 0.055264 | -0.047224 | 0.01056 | 0.072925 | 0.14091 | 0.057422 | 0.12541
1410.0156 | 119.5541 | -119.0552 | 0.29755 | 0.13559 | -0.026784 | 0.061258 | 0.002454 | 0.10951 | 0.085583 | -0.026092 | 0.066223 | 0.1479 | 0.05072 | -0.10637 | 0.002454 | 0.027798 | -0.07469 | -0.016906 | 0.16305 | 0.000682 | 0.088724 | 0.02992 | 0.13698 | 0.11305 | 0.001374 | 0.093689 | 0.17536 | 0.078186 | -0.078899 | 0.02992 | 0.055264 | -0.047224 | 0.01056 | 0.063769 | 0.14091 | 0.048266 | 0.12541
1411.75 | 119.4946 | -119.1422 | 0.32501 | 0.13559 | -0.026784 | 0.074994 | 0.002454 | 0.10951 | 0.090161 | -0.026092 | 0.070802 | 0.1479 | 0.05072 | -0.11094 | 0.002454 | 0.02322 | -0.07469 | -0.016906 | 0.16305 | 0.000682 | 0.10246 | 0.02992 | 0.13698 | 0.11763 | 0.001374 | 0.098268 | 0.17536 | 0.078186 | -0.083478 | 0.02992 | 0.050686 | -0.047224 | 0.01056 | 0.068348 | 0.14549 | 0.048266 | 0.12541
1413.4219 | 119.6548 | -119.1742 | 0.31128 | 0.12643 | -0.026784 | 0.065837 | 0.002454 | 0.11867 | 0.085583 | -0.03067 | 0.070802 | 0.15706 | 0.05072 | -0.10637 | -0.002124 | 0.027798 | -0.070112 | -0.016906 | 0.1539 | 0.000682 | 0.093303 | 0.02992 | 0.14613 | 0.11305 | -0.003204 | 0.098268 | 0.18452 | 0.078186 | -0.078899 | 0.025342 | 0.055264 | -0.042646 | 0.01056 | 0.072926 | 0.14091 | 0.052844 | 0.12083
1415.1719 | 119.7876 | -119.252 | 0.27924 | 0.12643 | -0.035942 | 0.061258 | 0.002454 | 0.10951 | 0.085583 | -0.03067 | 0.070802 | 0.15248 | 0.055298 | -0.11094 | -0.011281 | 0.027798 | -0.070112 | -0.012328 | 0.1539 | -0.008476 | 0.088724 | 0.02992 | 0.13698 | 0.11305 | -0.003204 | 0.098268 | 0.17994 | 0.082764 | -0.083478 | 0.016185 | 0.055264 | -0.042646 | 0.015138 | 0.082083 | 0.14091 | 0.066579 | 0.12541
1416.9219 | 119.8059 | -119.2474 | 0.28839 | 0.13101 | -0.022205 | 0.065837 | 0.007033 | 0.10951 | 0.085583 | -0.026092 | 0.070802 | 0.1479 | 0.059877 | -0.10637 | -0.002124 | 0.02322 | -0.070112 | -0.021484 | 0.15847 | 0.005261 | 0.093303 | 0.034499 | 0.13698 | 0.11305 | 0.001374 | 0.098268 | 0.17536 | 0.087343 | -0.078899 | 0.025342 | 0.050686 | -0.042646 | 0.005982 | 0.072926 | 0.14091 | 0.062001 | 0.12999
1418.6562 | 119.8471 | -119.3344 | 0.3067 | 0.12643 | -0.031363 | 0.065837 | 0.002454 | 0.10951 | 0.09474 | -0.021514 | 0.070802 | 0.1479 | 0.055298 | -0.11094 | -0.002124 | 0.027798 | -0.07469 | -0.021484 | 0.1539 | -0.003897 | 0.093303 | 0.02992 | 0.13698 | 0.12221 | 0.005952 | 0.098268 | 0.17536 | 0.082764 | -0.083478 | 0.025342 | 0.055264 | -0.047224 | 0.005982 | 0.072926 | 0.14549 | 0.057422 | 0.12999
1420.4062 | 119.8242 | -119.426 | 0.32959 | 0.12643 | -0.031363 | 0.065837 | 0.002454 | 0.11409 | 0.085583 | -0.026092 | 0.070802 | 0.15248 | 0.05072 | -0.10637 | -0.006702 | 0.02322 | -0.070112 | -0.012328 | 0.1539 | -0.003897 | 0.093303 | 0.02992 | 0.14156 | 0.11305 | 0.001374 | 0.098268 | 0.17994 | 0.078186 | -0.078899 | 0.020764 | 0.050686 | -0.042646 | 0.015138 | 0.077504 | 0.14091 | 0.057422 | 0.12083
1422.0781 | 119.8425 | -119.4855 | 0.34332 | 0.13101 | -0.026784 | 0.070415 | 0.007033 | 0.11867 | 0.090161 | -0.03067 | 0.070802 | 0.15706 | 0.05072 | -0.10637 | -0.011281 | 0.032376 | -0.07469 | -0.021484 | 0.15847 | 0.000682 | 0.097881 | 0.034499 | 0.14613 | 0.11763 | -0.003204 | 0.098268 | 0.18452 | 0.078186 | -0.078899 | 0.016185 | 0.059842 | -0.047224 | 0.005982 | 0.082083 | 0.14549 | 0.062001 | 0.12541
1423.8281 | 119.9707 | -119.5038 | 0.35248 | 0.12643 | -0.026784 | 0.065837 | 0.011611 | 0.11409 | 0.090161 | -0.026092 | 0.066223 | 0.15248 | 0.046142 | -0.10637 | -0.006702 | 0.027798 | -0.07469 | -0.012328 | 0.1539 | 0.000682 | 0.093303 | 0.039077 | 0.14156 | 0.11763 | 0.001374 | 0.093689 | 0.17994 | 0.073608 | -0.078899 | 0.020764 | 0.055264 | -0.047224 | 0.015138 | 0.072925 | 0.14091 | 0.052844 | 0.12083
1425.5781 | 119.9203 | -119.6182 | 0.30212 | 0.12185 | -0.035942 | 0.056679 | -0.002124 | 0.10493 | 0.085583 | -0.03067 | 0.070802 | 0.14332 | 0.046142 | -0.11094 | 0.002454 | 0.02322 | -0.070112 | -0.016906 | 0.14932 | -0.008476 | 0.084145 | 0.025342 | 0.1324 | 0.11305 | -0.003204 | 0.098268 | 0.17079 | 0.073608 | -0.083478 | 0.02992 | 0.050686 | -0.042646 | 0.01056 | 0.068348 | 0.14091 | 0.043688 | 0.11625
1427.3281 | 120.0485 | -119.664 | 0.29297 | 0.12643 | -0.035942 | 0.070415 | 0.007033 | 0.10951 | 0.090161 | -0.035248 | 0.052488 | 0.13874 | 0.055298 | -0.11094 | -0.002124 | 0.02322 | -0.07469 | -0.016906 | 0.1539 | -0.008476 | 0.097881 | 0.034499 | 0.13698 | 0.11763 | -0.007782 | 0.079954 | 0.16621 | 0.082764 | -0.083478 | 0.025342 | 0.050686 | -0.047224 | 0.01056 | 0.054612 | 0.12718 | 0.057422 | 0.12999
1429.0781 | 120.0806 | -119.7372 | 0.31586 | 0.12643 | -0.031363 | 0.061258 | 0.007033 | 0.10951 | 0.085583 | -0.021514 | 0.066223 | 0.14332 | 0.041563 | -0.10179 | 0.007032 | 0.032376 | -0.07469 | -0.012328 | 0.1539 | -0.003897 | 0.088724 | 0.034499 | 0.13698 | 0.11305 | 0.005952 | 0.093689 | 0.17079 | 0.069029 | -0.07432 | 0.034498 | 0.059842 | -0.047224 | 0.015138 | 0.059191 | 0.14091 | 0.034531 | 0.11625
1430.8281 | 120.2545 | -119.7189 | 0.27924 | 0.12185 | -0.031363 | 0.061258 | -0.002124 | 0.10493 | 0.085583 | -0.026092 | 0.066223 | 0.1479 | 0.059877 | -0.10637 | -0.002124 | 0.036954 | -0.065533 | -0.016906 | 0.14932 | -0.003897 | 0.088724 | 0.025342 | 0.1324 | 0.11305 | 0.001374 | 0.093689 | 0.17536 | 0.087343 | -0.078899 | 0.025342 | 0.06442 | -0.038067 | 0.01056 | 0.068347 | 0.13176 | 0.062001 | 0.12541
1432.5156 | 120.2774 | -119.7556 | 0.28839 | 0.12643 | -0.031363 | 0.065837 | 0.007033 | 0.11409 | 0.081005 | -0.035248 | 0.061645 | 0.1479 | 0.05072 | -0.10637 | 0.007032 | 0.027798 | -0.07469 | -0.012328 | 0.1539 | -0.003897 | 0.093303 | 0.034499 | 0.14156 | 0.10847 | -0.007782 | 0.089111 | 0.17536 | 0.078186 | -0.078899 | 0.034498 | 0.055264 | -0.047224 | 0.015138 | 0.054613 | 0.13634 | 0.043688 | 0.12541
1434.2656 | 120.3323 | -119.783 | 0.27924 | 0.12185 | -0.031363 | 0.056679 | 0.007033 | 0.10951 | 0.081005 | -0.035248 | 0.057066 | 0.1479 | 0.041563 | -0.10179 | -0.002124 | 0.032376 | -0.060955 | -0.021484 | 0.14932 | -0.003897 | 0.084145 | 0.034499 | 0.13698 | 0.10847 | -0.007782 | 0.084532 | 0.17536 | 0.069029 | -0.07432 | 0.025342 | 0.059842 | -0.033489 | 0.005982 | 0.05919 | 0.11802 | 0.043687 | 0.10252
1436.0156 | 120.2545 | -119.8975 | 0.30212 | 0.12185 | -0.035942 | 0.065837 | -0.002124 | 0.11409 | 0.076426 | -0.026092 | 0.061645 | 0.1479 | 0.046142 | -0.10637 | -0.002124 | 0.02322 | -0.070112 | -0.016906 | 0.14932 | -0.008476 | 0.093303 | 0.025342 | 0.14156 | 0.10389 | 0.001374 | 0.089111 | 0.17536 | 0.073608 | -0.078899 | 0.025342 | 0.050686 | -0.042646 | 0.01056 | 0.063769 | 0.13176 | 0.048266 | 0.11625
1437.6875 | 120.3049 | -119.9158 | 0.31586 | 0.13101 | -0.031363 | 0.070415 | 0.002454 | 0.10951 | 0.081005 | -0.026092 | 0.057066 | 0.1479 | 0.041563 | -0.11094 | 0.007032 | 0.027798 | -0.065533 | -0.012328 | 0.15847 | -0.003897 | 0.097881 | 0.02992 | 0.13698 | 0.10847 | 0.001374 | 0.084532 | 0.17536 | 0.069029 | -0.083478 | 0.034498 | 0.055264 | -0.038067 | 0.015138 | 0.050034 | 0.1226 | 0.034531 | 0.1071
1439.4375 | 120.4239 | -119.9112 | 0.29297 | 0.13101 | -0.026784 | 0.061258 | -0.002124 | 0.10951 | 0.081005 | -0.03067 | 0.061645 | 0.1479 | 0.05072 | -0.11094 | -0.002124 | 0.02322 | -0.070112 | -0.016906 | 0.15847 | 0.000682 | 0.088724 | 0.025342 | 0.13698 | 0.10847 | -0.003204 | 0.089111 | 0.17536 | 0.078186 | -0.083478 | 0.025342 | 0.050686 | -0.042646 | 0.01056 | 0.063769 | 0.13176 | 0.052844 | 0.12083
1441.1094 | 120.4285 | -119.957 | 0.31128 | 0.12185 | -0.035942 | 0.065837 | 0.002454 | 0.10493 | 0.081005 | -0.03067 | 0.057066 | 0.1479 | 0.046142 | -0.11094 | 0.002454 | 0.027798 | -0.07469 | -0.016906 | 0.14932 | -0.008476 | 0.093303 | 0.02992 | 0.1324 | 0.10847 | -0.003204 | 0.084532 | 0.17536 | 0.073608 | -0.083478 | 0.02992 | 0.055264 | -0.047224 | 0.01056 | 0.054612 | 0.13176 | 0.043688 | 0.12083
1442.8594 | 120.4514 | -120.0348 | 0.33417 | 0.12185 | -0.026784 | 0.061258 | 0.007033 | 0.10951 | 0.085583 | -0.03067 | 0.061645 | 0.14332 | 0.036985 | -0.11552 | 0.007032 | 0.032376 | -0.065533 | -0.016906 | 0.14932 | 0.000682 | 0.088724 | 0.034499 | 0.13698 | 0.11305 | -0.003204 | 0.089111 | 0.17079 | 0.064451 | -0.088057 | 0.034498 | 0.059842 | -0.038067 | 0.01056 | 0.054613 | 0.12718 | 0.029953 | 0.10252
1444.5469 | 120.5154 | -120.0485 | 0.30212 | 0.13101 | -0.035942 | 0.061258 | 0.002454 | 0.10951 | 0.081005 | -0.03067 | 0.066223 | 0.15706 | 0.046142 | -0.10637 | -0.002124 | 0.027798 | -0.079268 | -0.016906 | 0.15847 | -0.008476 | 0.088724 | 0.02992 | 0.13698 | 0.10847 | -0.003204 | 0.093689 | 0.18452 | 0.073608 | -0.078899 | 0.025342 | 0.055264 | -0.051802 | 0.01056 | 0.068347 | 0.14549 | 0.048266 | 0.12541
1446.2969 | 120.5887 | -120.0623 | 0.29755 | 0.12643 | -0.040521 | 0.056679 | 0.002454 | 0.10493 | 0.081005 | -0.035248 | 0.061645 | 0.15248 | 0.036985 | -0.10637 | 0.002454 | 0.027798 | -0.07469 | -0.016906 | 0.1539 | -0.013055 | 0.084145 | 0.02992 | 0.1324 | 0.10847 | -0.007782 | 0.089111 | 0.17994 | 0.064451 | -0.078899 | 0.02992 | 0.055264 | -0.047224 | 0.01056 | 0.059191 | 0.13634 | 0.034531 | 0.11167
1447.9844 | 120.5154 | -120.1492 | 0.32044 | 0.12185 | -0.026784 | 0.065837 | 0.002454 | 0.10493 | 0.085583 | -0.021514 | 0.066223 | 0.14332 | 0.041563 | -0.10637 | 0.002454 | 0.027798 | -0.070112 | -0.016906 | 0.14932 | 0.000682 | 0.093303 | 0.02992 | 0.1324 | 0.11305 | 0.005952 | 0.093689 | 0.17079 | 0.069029 | -0.078899 | 0.02992 | 0.055264 | -0.042646 | 0.01056 | 0.063769 | 0.13633 | 0.039109 | 0.11167
1449.7344 | 120.6299 | -120.1538 | 0.32044 | 0.11727 | -0.035942 | 0.065837 | 0.007033 | 0.10951 | 0.081005 | -0.026092 | 0.061645 | 0.15248 | 0.046142 | -0.10637 | 0.007032 | 0.036954 | -0.065533 | -0.016906 | 0.14474 | -0.008476 | 0.093303 | 0.034499 | 0.13698 | 0.10847 | 0.001374 | 0.089111 | 0.17994 | 0.073608 | -0.078899 | 0.034498 | 0.06442 | -0.038067 | 0.01056 | 0.054613 | 0.12718 | 0.03911 | 0.11167
1451.4062 | 120.5658 | -120.2316 | 0.32501 | 0.12643 | -0.022205 | 0.061258 | 0.002454 | 0.11409 | 0.085583 | -0.021514 | 0.061645 | 0.1479 | 0.046142 | -0.11094 | 0.01161 | 0.032376 | -0.079268 | -0.016906 | 0.1539 | 0.005261 | 0.088724 | 0.02992 | 0.14156 | 0.11305 | 0.005952 | 0.089111 | 0.17536 | 0.073608 | -0.083478 | 0.039076 | 0.059842 | -0.051802 | 0.01056 | 0.050035 | 0.14091 | 0.034532 | 0.12541
1453.0938 | 120.7031 | -120.2179 | 0.27924 | 0.13101 | -0.031363 | 0.065837 | 0.007033 | 0.10493 | 0.081005 | -0.026092 | 0.057066 | 0.15248 | 0.046142 | -0.11094 | 0.002454 | 0.032376 | -0.07469 | -0.026063 | 0.15847 | -0.003897 | 0.093303 | 0.034499 | 0.1324 | 0.10847 | 0.001374 | 0.084532 | 0.17994 | 0.073608 | -0.083478 | 0.02992 | 0.059842 | -0.047224 | 0.001403 | 0.054612 | 0.13176 | 0.043688 | 0.12083
1454.8281 | 120.6207 | -120.2316 | 0.31586 | 0.12185 | -0.035942 | 0.061258 | 0.011611 | 0.10951 | 0.081005 | -0.03067 | 0.061645 | 0.1479 | 0.046142 | -0.10179 | 0.002454 | 0.036954 | -0.070112 | -0.016906 | 0.14932 | -0.008476 | 0.088724 | 0.039077 | 0.13698 | 0.10847 | -0.003204 | 0.089111 | 0.17536 | 0.073608 | -0.07432 | 0.02992 | 0.06442 | -0.042646 | 0.01056 | 0.059191 | 0.13176 | 0.043688 | 0.11625
1456.5 | 120.7169 | -120.2637 | 0.3067 | 0.11727 | -0.031363 | 0.065837 | 0.007033 | 0.10493 | 0.076426 | -0.03067 | 0.066223 | 0.14332 | 0.041563 | -0.11552 | -0.002124 | 0.027798 | -0.065533 | -0.016906 | 0.14474 | -0.003897 | 0.093303 | 0.034499 | 0.1324 | 0.10389 | -0.003204 | 0.093689 | 0.17079 | 0.069029 | -0.088057 | 0.025342 | 0.055264 | -0.038067 | 0.01056 | 0.068347 | 0.13176 | 0.043687 | 0.1071
1458.25 | 120.6528 | -120.314 | 0.33875 | 0.12643 | -0.026784 | 0.070415 | -0.002124 | 0.11867 | 0.081005 | -0.03067 | 0.061645 | 0.15248 | 0.05072 | -0.11094 | 0.002454 | 0.032376 | -0.065533 | -0.012328 | 0.1539 | 0.000682 | 0.097881 | 0.025342 | 0.14613 | 0.10847 | -0.003204 | 0.089111 | 0.17994 | 0.078186 | -0.083478 | 0.02992 | 0.059842 | -0.038067 | 0.015138 | 0.059191 | 0.12718 | 0.048266 | 0.11625
1459.9844 | 120.7031 | -120.369 | 0.31586 | 0.12185 | -0.022205 | 0.061258 | 0.002454 | 0.10951 | 0.085583 | -0.021514 | 0.066223 | 0.15706 | 0.046142 | -0.10637 | -0.002124 | 0.032376 | -0.070112 | -0.016906 | 0.14932 | 0.005261 | 0.088724 | 0.02992 | 0.13698 | 0.11305 | 0.005952 | 0.093689 | 0.18452 | 0.073608 | -0.078899 | 0.025342 | 0.059842 | -0.042646 | 0.01056 | 0.068347 | 0.13633 | 0.048266 | 0.11625
1461.6562 | 120.8588 | -120.3369 | 0.3067 | 0.12185 | -0.040521 | 0.065837 | 0.011611 | 0.10951 | 0.081005 | -0.026092 | 0.061645 | 0.1479 | 0.046142 | -0.11552 | 0.002454 | 0.032376 | -0.079268 | -0.026063 | 0.14932 | -0.013055 | 0.093303 | 0.039077 | 0.13698 | 0.10847 | 0.001374 | 0.089111 | 0.17536 | 0.073608 | -0.088057 | 0.02992 | 0.059842 | -0.051802 | 0.001403 | 0.059191 | 0.14091 | 0.043688 | 0.12541
1463.4062 | 120.813 | -120.3644 | 0.34332 | 0.12643 | -0.031363 | 0.061258 | 0.002454 | 0.10493 | 0.085583 | -0.026092 | 0.061645 | 0.1479 | 0.05072 | -0.11094 | 0.002454 | 0.032376 | -0.065533 | -0.012328 | 0.1539 | -0.003897 | 0.088724 | 0.02992 | 0.1324 | 0.11305 | 0.001374 | 0.089111 | 0.17536 | 0.078186 | -0.083478 | 0.02992 | 0.059842 | -0.038067 | 0.015138 | 0.059191 | 0.12718 | 0.048266 | 0.11625
1465.0938 | 120.8862 | -120.3873 | 0.28381 | 0.12643 | -0.035942 | 0.061258 | 0.011611 | 0.10951 | 0.09474 | -0.026092 | 0.061645 | 0.14332 | 0.055298 | -0.11094 | -0.006702 | 0.02322 | -0.070112 | -0.026063 | 0.1539 | -0.008476 | 0.088724 | 0.039077 | 0.13698 | 0.12221 | 0.001374 | 0.089111 | 0.17079 | 0.082764 | -0.083478 | 0.020764 | 0.050686 | -0.042646 | 0.001403 | 0.068347 | 0.13176 | 0.062 | 0.12541
1466.8438 | 120.8176 | -120.4514 | 0.32501 | 0.12185 | -0.031363 | 0.061258 | -0.002124 | 0.10951 | 0.081005 | -0.035248 | 0.061645 | 0.14332 | 0.055298 | -0.11094 | -0.002124 | 0.027798 | -0.060955 | -0.016906 | 0.14932 | -0.003897 | 0.088724 | 0.025342 | 0.13698 | 0.10847 | -0.007782 | 0.089111 | 0.17079 | 0.082764 | -0.083478 | 0.025342 | 0.055264 | -0.033489 | 0.01056 | 0.063769 | 0.1226 | 0.057422 | 0.11625
1468.5781 | 120.8313 | -120.4651 | 0.32501 | 0.13101 | -0.035942 | 0.065837 | -0.002124 | 0.10951 | 0.076426 | -0.021514 | 0.061645 | 0.1479 | 0.046142 | -0.1201 | 0.002454 | 0.02322 | -0.065533 | -0.016906 | 0.15847 | -0.008476 | 0.093303 | 0.025342 | 0.13698 | 0.10389 | 0.005952 | 0.089111 | 0.17536 | 0.073608 | -0.092637 | 0.02992 | 0.050686 | -0.038067 | 0.01056 | 0.059191 | 0.12718 | 0.043688 | 0.11167
1470.2656 | 120.9412 | -120.4559 | 0.32501 | 0.12185 | -0.031363 | 0.065837 | 0.002454 | 0.11409 | 0.076426 | -0.026092 | 0.066223 | 0.1479 | 0.05072 | -0.11094 | -0.002124 | 0.027798 | -0.070112 | -0.016906 | 0.14932 | -0.003897 | 0.093303 | 0.02992 | 0.14156 | 0.10389 | 0.001374 | 0.093689 | 0.17536 | 0.078186 | -0.083478 | 0.025342 | 0.055264 | -0.042646 | 0.01056 | 0.068347 | 0.13633 | 0.052844 | 0.12083
1472 | 120.9915 | -120.4697 | 0.28839 | 0.11727 | -0.026784 | 0.056679 | -0.002124 | 0.10493 | 0.085583 | -0.03067 | 0.061645 | 0.15248 | 0.041563 | -0.11094 | -0.002124 | 0.036954 | -0.070112 | -0.012328 | 0.14474 | 0.000682 | 0.084145 | 0.025342 | 0.1324 | 0.11305 | -0.003204 | 0.089111 | 0.17994 | 0.069029 | -0.083478 | 0.025342 | 0.06442 | -0.042646 | 0.015138 | 0.063769 | 0.13176 | 0.043687 | 0.11167
1473.7344 | 121.0007 | -120.52 | 0.30212 | 0.12185 | -0.035942 | 0.065837 | 0.002454 | 0.11409 | 0.085583 | -0.035248 | 0.066223 | 0.1479 | 0.046142 | -0.11094 | 0.007032 | 0.032376 | -0.056376 | -0.016906 | 0.14932 | -0.008476 | 0.093303 | 0.02992 | 0.14156 | 0.11305 | -0.007782 | 0.093689 | 0.17536 | 0.073608 | -0.083478 | 0.034498 | 0.059842 | -0.02891 | 0.01056 | 0.059191 | 0.1226 | 0.03911 | 0.10252
1475.4844 | 121.019 | -120.5475 | 0.32044 | 0.11727 | -0.031363 | 0.061258 | 0.002454 | 0.10951 | 0.081005 | -0.03067 | 0.061645 | 0.1479 | 0.041563 | -0.10637 | 0.002454 | 0.032376 | -0.065533 | -0.021484 | 0.14474 | -0.003897 | 0.088724 | 0.02992 | 0.13698 | 0.10847 | -0.003204 | 0.089111 | 0.17536 | 0.069029 | -0.078899 | 0.02992 | 0.059842 | -0.038067 | 0.005982 | 0.059191 | 0.12718 | 0.039109 | 0.1071
1477.1562 | 120.9457 | -120.5658 | 0.3479 | 0.12185 | -0.031363 | 0.061258 | 0.011611 | 0.11409 | 0.085583 | -0.026092 | 0.057066 | 0.1479 | 0.046142 | -0.11094 | 0.002454 | 0.027798 | -0.065533 | -0.021484 | 0.14932 | -0.003897 | 0.088724 | 0.039077 | 0.14156 | 0.11305 | 0.001374 | 0.084532 | 0.17536 | 0.073608 | -0.083478 | 0.02992 | 0.055264 | -0.038067 | 0.005982 | 0.054612 | 0.1226 | 0.043688 | 0.11167
1478.9062 | 120.9686 | -120.6162 | 0.33875 | 0.12185 | -0.026784 | 0.052101 | 0.011611 | 0.10951 | 0.081005 | -0.026092 | 0.061645 | 0.1479 | 0.059877 | -0.11094 | 0.007032 | 0.027798 | -0.070112 | -0.021484 | 0.14932 | 0.000682 | 0.079567 | 0.039077 | 0.13698 | 0.10847 | 0.001374 | 0.089111 | 0.17536 | 0.087343 | -0.083478 | 0.034498 | 0.055264 | -0.042646 | 0.005982 | 0.054613 | 0.13176 | 0.052845 | 0.12999
1480.6719 | 120.9732 | -120.6345 | 0.33417 | 0.12185 | -0.035942 | 0.065837 | 0.007033 | 0.10493 | 0.090161 | -0.03067 | 0.057066 | 0.1479 | 0.046142 | -0.10637 | 0.007032 | 0.036954 | -0.07469 | -0.021484 | 0.14932 | -0.008476 | 0.093303 | 0.034499 | 0.1324 | 0.11763 | -0.003204 | 0.084532 | 0.17536 | 0.073608 | -0.078899 | 0.034498 | 0.06442 | -0.047224 | 0.005982 | 0.050034 | 0.13176 | 0.03911 | 0.12083
1482.3438 | 121.019 | -120.639 | 0.33875 | 0.12185 | -0.026784 | 0.056679 | 0.007033 | 0.10951 | 0.081005 | -0.026092 | 0.066223 | 0.15248 | 0.046142 | -0.11094 | 0.007032 | 0.027798 | -0.070112 | -0.021484 | 0.14932 | 0.000682 | 0.084145 | 0.034499 | 0.13698 | 0.10847 | 0.001374 | 0.093689 | 0.17994 | 0.073608 | -0.083478 | 0.034498 | 0.055264 | -0.042646 | 0.005982 | 0.059191 | 0.13633 | 0.03911 | 0.11625
1484.0156 | 121.1243 | -120.6024 | 0.29755 | 0.11727 | -0.031363 | 0.065837 | 0.007033 | 0.11409 | 0.081005 | -0.03067 | 0.061645 | 0.14332 | 0.05072 | -0.10637 | 0.007032 | 0.032376 | -0.070112 | -0.016906 | 0.14474 | -0.003897 | 0.093303 | 0.034499 | 0.14156 | 0.10847 | -0.003204 | 0.089111 | 0.17079 | 0.078186 | -0.078899 | 0.034498 | 0.059842 | -0.042646 | 0.01056 | 0.054613 | 0.13176 | 0.043688 | 0.12083
1485.7656 | 121.1746 | -120.6299 | 0.31128 | 0.12185 | -0.035942 | 0.070415 | 0.002454 | 0.10493 | 0.076426 | -0.03067 | 0.066223 | 0.15248 | 0.055298 | -0.11552 | -0.002124 | 0.036954 | -0.070112 | -0.016906 | 0.14932 | -0.008476 | 0.097881 | 0.02992 | 0.1324 | 0.10389 | -0.003204 | 0.093689 | 0.17994 | 0.082764 | -0.088057 | 0.025342 | 0.06442 | -0.042646 | 0.01056 | 0.068347 | 0.13633 | 0.057422 | 0.12541
1487.5 | 121.1746 | -120.6619 | 0.30212 | 0.11727 | -0.035942 | 0.065837 | 0.002454 | 0.10036 | 0.085583 | -0.03067 | 0.066223 | 0.15248 | 0.046142 | -0.11094 | 0.002454 | 0.032376 | -0.079268 | -0.012328 | 0.14474 | -0.008476 | 0.093303 | 0.02992 | 0.12782 | 0.11305 | -0.003204 | 0.093689 | 0.17994 | 0.073608 | -0.083478 | 0.02992 | 0.059842 | -0.051802 | 0.015138 | 0.063769 | 0.14549 | 0.043688 | 0.12541
1489.2344 | 121.0922 | -120.7214 | 0.34332 | 0.12185 | -0.022205 | 0.061258 | 0.007033 | 0.10951 | 0.081005 | -0.03067 | 0.066223 | 0.14332 | 0.046142 | -0.11552 | 0.002454 | 0.036954 | -0.07469 | -0.016906 | 0.14932 | 0.005261 | 0.088724 | 0.034499 | 0.13698 | 0.10847 | -0.003204 | 0.093689 | 0.17079 | 0.073608 | -0.088057 | 0.02992 | 0.06442 | -0.047224 | 0.01056 | 0.063769 | 0.14091 | 0.043688 | 0.12083
1490.9844 | 121.2021 | -120.6802 | 0.3067 | 0.12185 | -0.026784 | 0.065837 | 0.002454 | 0.10951 | 0.076426 | -0.021514 | 0.061645 | 0.15706 | 0.05072 | -0.11094 | 0.002454 | 0.027798 | -0.07469 | -0.021484 | 0.14932 | 0.000682 | 0.093303 | 0.02992 | 0.13698 | 0.10389 | 0.005952 | 0.089111 | 0.18452 | 0.078186 | -0.083478 | 0.02992 | 0.055264 | -0.047224 | 0.005982 | 0.059191 | 0.13634 | 0.048266 | 0.12541
1492.6562 | 121.2387 | -120.6985 | 0.29755 | 0.12643 | -0.022205 | 0.070415 | -0.002124 | 0.10951 | 0.081005 | -0.026092 | 0.057066 | 0.14332 | 0.05072 | -0.11094 | -0.002124 | 0.02322 | -0.070112 | -0.021484 | 0.1539 | 0.005261 | 0.097881 | 0.025342 | 0.13698 | 0.10847 | 0.001374 | 0.084532 | 0.17079 | 0.078186 | -0.083478 | 0.025342 | 0.050686 | -0.042646 | 0.005982 | 0.05919 | 0.12718 | 0.052844 | 0.12083
1494.3906 | 121.2204 | -120.7306 | 0.32959 | 0.12185 | -0.035942 | 0.065837 | -0.006703 | 0.10951 | 0.085583 | -0.026092 | 0.070802 | 0.1479 | 0.05072 | -0.10637 | -0.002124 | 0.032376 | -0.07469 | -0.012328 | 0.14932 | -0.008476 | 0.093303 | 0.020763 | 0.13698 | 0.11305 | 0.001374 | 0.098268 | 0.17536 | 0.078186 | -0.078899 | 0.025342 | 0.059842 | -0.047224 | 0.015138 | 0.072926 | 0.14549 | 0.052844 | 0.12541
1496.125 | 121.2158 | -120.7764 | 0.31128 | 0.11727 | -0.035942 | 0.065837 | 0.002454 | 0.10951 | 0.085583 | -0.021514 | 0.070802 | 0.14332 | 0.05072 | -0.11094 | 0.007032 | 0.027798 | -0.065533 | -0.012328 | 0.14474 | -0.008476 | 0.093303 | 0.02992 | 0.13698 | 0.11305 | 0.005952 | 0.098268 | 0.17079 | 0.078186 | -0.083478 | 0.034498 | 0.055264 | -0.038067 | 0.015138 | 0.06377 | 0.13633 | 0.043688 | 0.11625
1497.7969 | 121.2799 | -120.7718 | 0.27924 | 0.12185 | -0.022205 | 0.061258 | 0.002454 | 0.11409 | 0.081005 | -0.035248 | 0.070802 | 0.15248 | 0.05072 | -0.11552 | -0.002124 | 0.032376 | -0.07469 | -0.021484 | 0.14932 | 0.005261 | 0.088724 | 0.02992 | 0.14156 | 0.10847 | -0.007782 | 0.098268 | 0.17994 | 0.078186 | -0.088057 | 0.025342 | 0.059842 | -0.047224 | 0.005982 | 0.072926 | 0.14549 | 0.052844 | 0.12541
1499.5312 | 121.3074 | -120.8084 | 0.2655 | 0.12185 | -0.026784 | 0.061258 | 0.002454 | 0.11867 | 0.085583 | -0.03067 | 0.066223 | 0.15248 | 0.05072 | -0.10637 | -0.002124 | 0.027798 | -0.070112 | -0.016906 | 0.14932 | 0.000682 | 0.088724 | 0.02992 | 0.14613 | 0.11305 | -0.003204 | 0.093689 | 0.17994 | 0.078186 | -0.078899 | 0.025342 | 0.055264 | -0.042646 | 0.01056 | 0.068347 | 0.13633 | 0.052844 | 0.12083
1501.2188 | 121.2845 | -120.7993 | 0.28381 | 0.12643 | -0.031363 | 0.061258 | 0.002454 | 0.10493 | 0.076426 | -0.026092 | 0.066223 | 0.1479 | 0.046142 | -0.11094 | 0.002454 | 0.027798 | -0.07469 | -0.016906 | 0.1539 | -0.003897 | 0.088724 | 0.02992 | 0.1324 | 0.10389 | 0.001374 | 0.093689 | 0.17536 | 0.073608 | -0.083478 | 0.02992 | 0.055264 | -0.047224 | 0.01056 | 0.063769 | 0.14091 | 0.043688 | 0.12083
1502.9531 | 121.2524 | -120.8725 | 0.28381 | 0.11727 | -0.035942 | 0.065837 | 0.002454 | 0.10951 | 0.085583 | -0.026092 | 0.066223 | 0.15248 | 0.046142 | -0.11094 | 0.01161 | 0.018642 | -0.060955 | -0.021484 | 0.14474 | -0.008476 | 0.093303 | 0.02992 | 0.13698 | 0.11305 | 0.001374 | 0.093689 | 0.17994 | 0.073608 | -0.083478 | 0.039076 | 0.046108 | -0.033489 | 0.005982 | 0.054613 | 0.12718 | 0.034532 | 0.1071
1504.625 | 121.2067 | -120.9091 | 0.29755 | 0.12185 | -0.031363 | 0.065837 | 0.007033 | 0.11409 | 0.085583 | -0.03067 | 0.061645 | 0.1479 | 0.055298 | -0.10637 | -0.002124 | 0.02322 | -0.065533 | -0.016906 | 0.14932 | -0.003897 | 0.093303 | 0.034499 | 0.14156 | 0.11305 | -0.003204 | 0.089111 | 0.17536 | 0.082764 | -0.078899 | 0.025342 | 0.050686 | -0.038067 | 0.01056 | 0.063769 | 0.12718 | 0.057422 | 0.12083
1506.375 | 121.2341 | -120.8908 | 0.31586 | 0.12643 | -0.031363 | 0.065837 | 0.002454 | 0.11409 | 0.081005 | -0.021514 | 0.066223 | 0.15248 | 0.055298 | -0.11094 | 0.002454 | 0.032376 | -0.07469 | -0.016906 | 0.1539 | -0.003897 | 0.093303 | 0.02992 | 0.14156 | 0.10847 | 0.005952 | 0.093689 | 0.17994 | 0.082764 | -0.083478 | 0.02992 | 0.059842 | -0.047224 | 0.01056 | 0.063769 | 0.14091 | 0.052844 | 0.12999
1508.1094 | 121.2708 | -120.9274 | 0.27924 | 0.11727 | -0.035942 | 0.061258 | 0.01619 | 0.10951 | 0.081005 | -0.03067 | 0.066223 | 0.14332 | 0.046142 | -0.11552 | -0.011281 | 0.027798 | -0.079268 | -0.012328 | 0.14474 | -0.008476 | 0.088724 | 0.043656 | 0.13698 | 0.10847 | -0.003204 | 0.093689 | 0.17079 | 0.073608 | -0.088057 | 0.016185 | 0.055264 | -0.051802 | 0.015138 | 0.077504 | 0.14549 | 0.057423 | 0.12541
1509.8594 | 121.3531 | -120.9183 | 0.29297 | 0.12643 | -0.031363 | 0.061258 | -0.006703 | 0.10493 | 0.085583 | -0.026092 | 0.057066 | 0.14332 | 0.05072 | -0.10637 | 0.002454 | 0.02322 | -0.07469 | -0.012328 | 0.1539 | -0.003897 | 0.088724 | 0.020763 | 0.1324 | 0.11305 | 0.001374 | 0.084532 | 0.17079 | 0.078186 | -0.078899 | 0.02992 | 0.050686 | -0.047224 | 0.015138 | 0.054612 | 0.13176 | 0.048266 | 0.12541
1511.5469 | 121.2891 | -120.9869 | 0.3067 | 0.11269 | -0.035942 | 0.065837 | 0.002454 | 0.10951 | 0.081005 | -0.026092 | 0.052488 | 0.1479 | 0.05072 | -0.11552 | 0.002454 | 0.032376 | -0.070112 | -0.016906 | 0.14016 | -0.008476 | 0.093303 | 0.02992 | 0.13698 | 0.10847 | 0.001374 | 0.079954 | 0.17536 | 0.078186 | -0.088057 | 0.02992 | 0.059842 | -0.042646 | 0.01056 | 0.050034 | 0.1226 | 0.048266 | 0.12083
1513.2969 | 121.4218 | -120.9229 | 0.27008 | 0.12185 | -0.031363 | 0.061258 | -0.002124 | 0.10951 | 0.085583 | -0.026092 | 0.066223 | 0.15248 | 0.046142 | -0.11094 | -0.002124 | 0.036954 | -0.070112 | -0.012328 | 0.14932 | -0.003897 | 0.088724 | 0.025342 | 0.13698 | 0.11305 | 0.001374 | 0.093689 | 0.17994 | 0.073608 | -0.083478 | 0.025342 | 0.06442 | -0.042646 | 0.015138 | 0.068347 | 0.13633 | 0.048266 | 0.11625
1514.9688 | 121.4447 | -120.9503 | 0.25635 | 0.11727 | -0.035942 | 0.061258 | 0.002454 | 0.10951 | 0.076426 | -0.026092 | 0.066223 | 0.1479 | 0.046142 | -0.1201 | -0.002124 | 0.032376 | -0.070112 | -0.016906 | 0.14474 | -0.008476 | 0.088724 | 0.02992 | 0.13698 | 0.10389 | 0.001374 | 0.093689 | 0.17536 | 0.073608 | -0.092637 | 0.025342 | 0.059842 | -0.042646 | 0.01056 | 0.068347 | 0.13633 | 0.048266 | 0.11625
1516.7188 | 121.3715 | -120.9778 | 0.27008 | 0.12643 | -0.031363 | 0.070415 | 0.011611 | 0.11409 | 0.081005 | -0.026092 | 0.057066 | 0.1479 | 0.05072 | -0.10179 | -0.002124 | 0.032376 | -0.065533 | -0.021484 | 0.1539 | -0.003897 | 0.097881 | 0.039077 | 0.14156 | 0.10847 | 0.001374 | 0.084532 | 0.17536 | 0.078186 | -0.07432 | 0.025342 | 0.059842 | -0.038067 | 0.005982 | 0.05919 | 0.1226 | 0.052844 | 0.11625
1518.4531 | 121.4264 | -120.9686 | 0.28381 | 0.11727 | -0.035942 | 0.056679 | -0.002124 | 0.11409 | 0.085583 | -0.026092 | 0.070802 | 0.15248 | 0.046142 | -0.11094 | -0.002124 | 0.032376 | -0.070112 | -0.012328 | 0.14474 | -0.008476 | 0.084145 | 0.025342 | 0.14156 | 0.11305 | 0.001374 | 0.098268 | 0.17994 | 0.073608 | -0.083478 | 0.025342 | 0.059842 | -0.042646 | 0.015138 | 0.072926 | 0.14091 | 0.048266 | 0.11625
1520.125 | 121.344 | -121.2158 | 0.14191 | 0.12185 | -0.031363 | 0.065837 | 0.007033 | 0.10951 | 0.081005 | -0.026092 | 0.057066 | 0.15248 | 0.036985 | -0.10637 | 0.002454 | 0.02322 | -0.060955 | -0.012328 | 0.14932 | -0.003897 | 0.093303 | 0.034499 | 0.13698 | 0.10847 | 0.001374 | 0.084532 | 0.17994 | 0.064451 | -0.078899 | 0.02992 | 0.050686 | -0.033489 | 0.015138 | 0.054612 | 0.11802 | 0.034531 | 0.09794
1521.875 | 121.4355 | -121.1563 | 0.10986 | 0.11727 | -0.031363 | 0.065837 | -0.002124 | 0.10951 | 0.085583 | -0.03067 | 0.070802 | 0.1479 | 0.046142 | -0.11094 | 0.002454 | 0.027798 | -0.070112 | -0.021484 | 0.14474 | -0.003897 | 0.093303 | 0.025342 | 0.13698 | 0.11305 | -0.003204 | 0.098268 | 0.17536 | 0.073608 | -0.083478 | 0.02992 | 0.055264 | -0.042646 | 0.005982 | 0.068348 | 0.14091 | 0.043688 | 0.11625
1523.625 | 121.3898 | -121.2296 | 0.14191 | 0.11727 | -0.040521 | 0.061258 | -0.002124 | 0.11409 | 0.081005 | -0.03067 | 0.061645 | 0.1479 | 0.05072 | -0.11094 | 0.002454 | 0.027798 | -0.07469 | -0.016906 | 0.14474 | -0.013055 | 0.088724 | 0.025342 | 0.14156 | 0.10847 | -0.003204 | 0.089111 | 0.17536 | 0.078186 | -0.083478 | 0.02992 | 0.055264 | -0.047224 | 0.01056 | 0.059191 | 0.13634 | 0.048266 | 0.12541
1525.375 | 121.4264 | -121.2158 | 0.13733 | 0.11269 | -0.035942 | 0.061258 | 0.011611 | 0.11867 | 0.090161 | -0.03067 | 0.057066 | 0.15706 | 0.05072 | -0.11552 | 0.007032 | 0.02322 | -0.065533 | -0.021484 | 0.14016 | -0.008476 | 0.088724 | 0.039077 | 0.14613 | 0.11763 | -0.003204 | 0.084532 | 0.18452 | 0.078186 | -0.088057 | 0.034498 | 0.050686 | -0.038067 | 0.005982 | 0.050034 | 0.1226 | 0.043688 | 0.11625
1527.0469 | 121.4035 | -121.2479 | 0.13275 | 0.11727 | -0.031363 | 0.056679 | 0.002454 | 0.10951 | 0.081005 | -0.026092 | 0.061645 | 0.15248 | 0.05072 | -0.10637 | 0.002454 | 0.027798 | -0.070112 | -0.016906 | 0.14474 | -0.003897 | 0.084145 | 0.02992 | 0.13698 | 0.10847 | 0.001374 | 0.089111 | 0.17994 | 0.078186 | -0.078899 | 0.02992 | 0.055264 | -0.042646 | 0.01056 | 0.059191 | 0.13176 | 0.048266 | 0.12083
1528.7969 | 121.4172 | -121.2387 | 0.14648 | 0.12643 | -0.035942 | 0.056679 | 0.002454 | 0.10951 | 0.085583 | -0.026092 | 0.061645 | 0.14332 | 0.055298 | -0.1201 | 0.002454 | 0.027798 | -0.07469 | -0.016906 | 0.1539 | -0.008476 | 0.084145 | 0.02992 | 0.13698 | 0.11305 | 0.001374 | 0.089111 | 0.17079 | 0.082764 | -0.092637 | 0.02992 | 0.055264 | -0.047224 | 0.01056 | 0.059191 | 0.13634 | 0.052844 | 0.12999
1530.5625 | 121.5042 | -121.2662 | 0.10071 | 0.11269 | -0.031363 | 0.061258 | 0.002454 | 0.11409 | 0.081005 | -0.03067 | 0.061645 | 0.1479 | 0.05072 | -0.11094 | 0.002454 | 0.02322 | -0.070112 | -0.016906 | 0.14016 | -0.003897 | 0.088724 | 0.02992 | 0.14156 | 0.10847 | -0.003204 | 0.089111 | 0.17536 | 0.078186 | -0.083478 | 0.02992 | 0.050686 | -0.042646 | 0.01056 | 0.059191 | 0.13176 | 0.048266 | 0.12083
1532.25 | 121.5042 | -121.2616 | 0.10071 | 0.11269 | -0.031363 | 0.070415 | 0.002454 | 0.10493 | 0.085583 | -0.035248 | 0.066223 | 0.1479 | 0.046142 | -0.11552 | 0.002454 | 0.032376 | -0.065533 | -0.016906 | 0.14016 | -0.003897 | 0.097881 | 0.02992 | 0.1324 | 0.11305 | -0.007782 | 0.093689 | 0.17536 | 0.073608 | -0.088057 | 0.02992 | 0.059842 | -0.038067 | 0.01056 | 0.063769 | 0.13176 | 0.043688 | 0.11167
1534 | 121.4447 | -121.2753 | 0.13733 | 0.11269 | -0.026784 | 0.065837 | 0.007033 | 0.10951 | 0.085583 | -0.026092 | 0.057066 | 0.1479 | 0.055298 | -0.11552 | 0.002454 | 0.032376 | -0.070112 | -0.012328 | 0.14016 | 0.000682 | 0.093303 | 0.034499 | 0.13698 | 0.11305 | 0.001374 | 0.084532 | 0.17536 | 0.082764 | -0.088057 | 0.02992 | 0.059842 | -0.042646 | 0.015138 | 0.054612 | 0.12718 | 0.052844 | 0.12541
1535.6875 | 121.4584 | -121.2936 | 0.11444 | 0.11727 | -0.031363 | 0.065837 | 0.007033 | 0.11409 | 0.085583 | -0.03067 | 0.057066 | 0.14332 | 0.036985 | -0.11552 | -0.002124 | 0.027798 | -0.065533 | -0.00775 | 0.14474 | -0.003897 | 0.093303 | 0.034499 | 0.14156 | 0.11305 | -0.003204 | 0.084532 | 0.17079 | 0.064451 | -0.088057 | 0.025342 | 0.055264 | -0.038067 | 0.019716 | 0.05919 | 0.1226 | 0.039109 | 0.10252
1537.4219 | 121.5363 | -121.2845 | 0.10529 | 0.12185 | -0.035942 | 0.065837 | 0.002454 | 0.10951 | 0.081005 | -0.026092 | 0.066223 | 0.1479 | 0.055298 | -0.10637 | 0.002454 | 0.036954 | -0.07469 | -0.012328 | 0.14932 | -0.008476 | 0.093303 | 0.02992 | 0.13698 | 0.10847 | 0.001374 | 0.093689 | 0.17536 | 0.082764 | -0.078899 | 0.02992 | 0.06442 | -0.047224 | 0.015138 | 0.063769 | 0.14091 | 0.052844 | 0.12999
1539.1719 | 121.4539 | -121.3165 | 0.13275 | 0.11727 | -0.031363 | 0.065837 | -0.002124 | 0.11409 | 0.076426 | -0.039826 | 0.061645 | 0.14332 | 0.05072 | -0.11094 | 0.007032 | 0.032376 | -0.070112 | -0.021484 | 0.14474 | -0.003897 | 0.093303 | 0.025342 | 0.14156 | 0.10389 | -0.01236 | 0.089111 | 0.17079 | 0.078186 | -0.083478 | 0.034498 | 0.059842 | -0.042646 | 0.005982 | 0.054613 | 0.13176 | 0.043688 | 0.12083
1540.9375 | 121.5729 | -121.2708 | 0.082397 | 0.11269 | -0.031363 | 0.052101 | 0.007033 | 0.10951 | 0.076426 | -0.035248 | 0.070802 | 0.14332 | 0.046142 | -0.10179 | 0.002454 | 0.027798 | -0.07469 | -0.021484 | 0.14016 | -0.003897 | 0.079567 | 0.034499 | 0.13698 | 0.10389 | -0.007782 | 0.098268 | 0.17079 | 0.073608 | -0.07432 | 0.02992 | 0.055264 | -0.047224 | 0.005982 | 0.068348 | 0.14549 | 0.043688 | 0.12083
1542.625 | 121.637 | -121.2845 | 0.10986 | 0.10812 | -0.031363 | 0.061258 | 0.002454 | 0.10036 | 0.085583 | -0.039826 | 0.070802 | 0.15248 | 0.055298 | -0.10179 | 0.002454 | 0.027798 | -0.07469 | -0.016906 | 0.13558 | -0.003897 | 0.088724 | 0.02992 | 0.12782 | 0.11305 | -0.01236 | 0.098268 | 0.17994 | 0.082764 | -0.07432 | 0.02992 | 0.055264 | -0.047224 | 0.01056 | 0.068348 | 0.14549 | 0.052844 | 0.12999
1544.375 | 121.6324 | -121.3028 | 0.086975 | 0.11269 | -0.026784 | 0.070415 | 0.002454 | 0.10493 | 0.081005 | -0.03067 | 0.061645 | 0.15248 | 0.055298 | -0.10637 | -0.002124 | 0.027798 | -0.070112 | -0.021484 | 0.14016 | 0.000682 | 0.097881 | 0.02992 | 0.1324 | 0.10847 | -0.003204 | 0.089111 | 0.17994 | 0.082764 | -0.078899 | 0.025342 | 0.055264 | -0.042646 | 0.005982 | 0.063769 | 0.13176 | 0.057422 | 0.12541
1546.0469 | 121.6553 | -121.3074 | 0.09613 | 0.12185 | -0.031363 | 0.061258 | 0.007033 | 0.10951 | 0.090161 | -0.026092 | 0.066223 | 0.1479 | 0.05072 | -0.10179 | 0.002454 | 0.032376 | -0.070112 | -0.012328 | 0.14932 | -0.003897 | 0.088724 | 0.034499 | 0.13698 | 0.11763 | 0.001374 | 0.093689 | 0.17536 | 0.078186 | -0.07432 | 0.02992 | 0.059842 | -0.042646 | 0.015138 | 0.063769 | 0.13633 | 0.048266 | 0.12083
1547.7969 | 121.5271 | -121.3531 | 0.1236 | 0.12185 | -0.035942 | 0.061258 | 0.002454 | 0.11409 | 0.081005 | -0.03067 | 0.070802 | 0.14332 | 0.05072 | -0.11094 | -0.002124 | 0.032376 | -0.07469 | -0.012328 | 0.14932 | -0.008476 | 0.088724 | 0.02992 | 0.14156 | 0.10847 | -0.003204 | 0.098268 | 0.17079 | 0.078186 | -0.083478 | 0.025342 | 0.059842 | -0.047224 | 0.015138 | 0.072926 | 0.14549 | 0.052844 | 0.12541
1549.5312 | 121.6278 | -121.3486 | 0.11444 | 0.11727 | -0.035942 | 0.056679 | 0.007033 | 0.10493 | 0.081005 | -0.03067 | 0.061645 | 0.15706 | 0.05072 | -0.11094 | 0.002454 | 0.032376 | -0.065533 | -0.016906 | 0.14474 | -0.008476 | 0.084145 | 0.034499 | 0.1324 | 0.10847 | -0.003204 | 0.089111 | 0.18452 | 0.078186 | -0.083478 | 0.02992 | 0.059842 | -0.038067 | 0.01056 | 0.059191 | 0.12718 | 0.048266 | 0.11625
1551.2656 | 121.6141 | -121.3669 | 0.11444 | 0.12185 | -0.026784 | 0.070415 | 0.002454 | 0.10951 | 0.085583 | -0.026092 | 0.061645 | 0.15248 | 0.055298 | -0.11552 | 0.007032 | 0.032376 | -0.070112 | -0.00775 | 0.14932 | 0.000682 | 0.097881 | 0.02992 | 0.13698 | 0.11305 | 0.001374 | 0.089111 | 0.17994 | 0.082764 | -0.088057 | 0.034498 | 0.059842 | -0.042646 | 0.019716 | 0.054613 | 0.13176 | 0.048266 | 0.12541
1552.9375 | 121.5408 | -121.4127 | 0.14191 | 0.12185 | -0.031363 | 0.065837 | 0.002454 | 0.10951 | 0.085583 | -0.03067 | 0.066223 | 0.15248 | 0.055298 | -0.10637 | 0.002454 | 0.02322 | -0.070112 | -0.012328 | 0.14932 | -0.003897 | 0.093303 | 0.02992 | 0.13698 | 0.11305 | -0.003204 | 0.093689 | 0.17994 | 0.082764 | -0.078899 | 0.02992 | 0.050686 | -0.042646 | 0.015138 | 0.063769 | 0.13633 | 0.052844 | 0.12541
1554.6719 | 121.5729 | -121.3943 | 0.14191 | 0.10812 | -0.026784 | 0.065837 | 0.007033 | 0.10951 | 0.081005 | -0.03067 | 0.066223 | 0.15248 | 0.046142 | -0.11094 | 0.002454 | 0.02322 | -0.065533 | -0.012328 | 0.13558 | 0.000682 | 0.093303 | 0.034499 | 0.13698 | 0.10847 | -0.003204 | 0.093689 | 0.17994 | 0.073608 | -0.083478 | 0.02992 | 0.050686 | -0.038067 | 0.015138 | 0.063769 | 0.13176 | 0.043688 | 0.11167
1556.4219 | 121.6644 | -121.3943 | 0.09613 | 0.11727 | -0.035942 | 0.065837 | 0.007033 | 0.10493 | 0.081005 | -0.026092 | 0.070802 | 0.14332 | 0.055298 | -0.10179 | 0.002454 | 0.02322 | -0.079268 | -0.021484 | 0.14474 | -0.008476 | 0.093303 | 0.034499 | 0.1324 | 0.10847 | 0.001374 | 0.098268 | 0.17079 | 0.082764 | -0.07432 | 0.02992 | 0.050686 | -0.051802 | 0.005982 | 0.068348 | 0.15007 | 0.052844 | 0.13457
1558.1719 | 121.582 | -121.4355 | 0.13275 | 0.11727 | -0.026784 | 0.070415 | 0.007033 | 0.10493 | 0.081005 | -0.03067 | 0.061645 | 0.15248 | 0.055298 | -0.11094 | 0.007032 | 0.032376 | -0.065533 | -0.021484 | 0.14474 | 0.000682 | 0.097881 | 0.034499 | 0.1324 | 0.10847 | -0.003204 | 0.089111 | 0.17994 | 0.082764 | -0.083478 | 0.034498 | 0.059842 | -0.038067 | 0.005982 | 0.054613 | 0.12718 | 0.048266 | 0.12083
1559.9062 | 121.6461 | -121.4264 | 0.12817 | 0.11727 | -0.035942 | 0.061258 | 0.002454 | 0.10951 | 0.081005 | -0.026092 | 0.066223 | 0.1479 | 0.05072 | -0.10637 | -0.002124 | 0.027798 | -0.079268 | -0.016906 | 0.14474 | -0.008476 | 0.088724 | 0.02992 | 0.13698 | 0.10847 | 0.001374 | 0.093689 | 0.17536 | 0.078186 | -0.078899 | 0.025342 | 0.055264 | -0.051802 | 0.01056 | 0.068347 | 0.14549 | 0.052844 | 0.12999
1561.5781 | 121.6965 | -121.4081 | 0.11444 | 0.11727 | -0.035942 | 0.056679 | 0.007033 | 0.11409 | 0.081005 | -0.03067 | 0.066223 | 0.1479 | 0.05072 | -0.10179 | 0.007032 | 0.027798 | -0.07469 | -0.016906 | 0.14474 | -0.008476 | 0.084145 | 0.034499 | 0.14156 | 0.10847 | -0.003204 | 0.093689 | 0.17536 | 0.078186 | -0.07432 | 0.034498 | 0.055264 | -0.047224 | 0.01056 | 0.059191 | 0.14091 | 0.043688 | 0.12541
1563.3438 | 121.6095 | -121.4493 | 0.15106 | 0.11727 | -0.031363 | 0.070415 | 0.002454 | 0.10951 | 0.081005 | -0.03067 | 0.070802 | 0.15248 | 0.041563 | -0.11094 | 0.002454 | 0.027798 | -0.065533 | -0.016906 | 0.14474 | -0.003897 | 0.097881 | 0.02992 | 0.13698 | 0.10847 | -0.003204 | 0.098268 | 0.17994 | 0.069029 | -0.083478 | 0.02992 | 0.055264 | -0.038067 | 0.01056 | 0.068348 | 0.13633 | 0.039109 | 0.1071
1565.0312 | 121.6141 | -121.4676 | 0.12817 | 0.11727 | -0.035942 | 0.070415 | 0.011611 | 0.11409 | 0.085583 | -0.021514 | 0.061645 | 0.15706 | 0.05072 | -0.10179 | 0.002454 | 0.032376 | -0.07469 | -0.021484 | 0.14474 | -0.008476 | 0.097881 | 0.039077 | 0.14156 | 0.11305 | 0.005952 | 0.089111 | 0.18452 | 0.078186 | -0.07432 | 0.02992 | 0.059842 | -0.047224 | 0.005982 | 0.059191 | 0.13634 | 0.048266 | 0.12541
1566.7812 | 121.7056 | -121.4447 | 0.11902 | 0.11727 | -0.031363 | 0.065837 | 0.007033 | 0.10951 | 0.081005 | -0.03067 | 0.070802 | 0.1479 | 0.046142 | -0.10637 | 0.002454 | 0.032376 | -0.070112 | -0.016906 | 0.14474 | -0.003897 | 0.093303 | 0.034499 | 0.13698 | 0.10847 | -0.003204 | 0.098268 | 0.17536 | 0.073608 | -0.078899 | 0.02992 | 0.059842 | -0.042646 | 0.01056 | 0.068348 | 0.14091 | 0.043688 | 0.11625
1568.5156 | 121.6736 | -121.4676 | 0.13275 | 0.11727 | -0.031363 | 0.065837 | -0.002124 | 0.11867 | 0.085583 | -0.03067 | 0.066223 | 0.15248 | 0.046142 | -0.11552 | 0.007032 | 0.032376 | -0.07469 | -0.012328 | 0.14474 | -0.003897 | 0.093303 | 0.025342 | 0.14613 | 0.11305 | -0.003204 | 0.093689 | 0.17994 | 0.073608 | -0.088057 | 0.034498 | 0.059842 | -0.047224 | 0.015138 | 0.059191 | 0.14091 | 0.03911 | 0.12083
1570.25 | 121.7194 | -121.4676 | 0.10071 | 0.11269 | -0.026784 | 0.056679 | -0.002124 | 0.10951 | 0.081005 | -0.03067 | 0.066223 | 0.1479 | 0.041563 | -0.11094 | 0.002454 | 0.027798 | -0.07469 | -0.016906 | 0.14016 | 0.000682 | 0.084145 | 0.025342 | 0.13698 | 0.10847 | -0.003204 | 0.093689 | 0.17536 | 0.069029 | -0.083478 | 0.02992 | 0.055264 | -0.047224 | 0.01056 | 0.063769 | 0.14091 | 0.039109 | 0.11625
1571.9375 | 121.6599 | -121.4767 | 0.11444 | 0.11727 | -0.035942 | 0.065837 | 0.011611 | 0.10493 | 0.071848 | -0.026092 | 0.061645 | 0.1479 | 0.05072 | -0.11094 | -0.002124 | 0.032376 | -0.065533 | -0.016906 | 0.14474 | -0.008476 | 0.093303 | 0.039077 | 0.1324 | 0.099314 | 0.001374 | 0.089111 | 0.17536 | 0.078186 | -0.083478 | 0.025342 | 0.059842 | -0.038067 | 0.01056 | 0.063769 | 0.12718 | 0.052844 | 0.11625
1573.6719 | 121.788 | -121.4813 | 0.13733 | 0.11727 | -0.031363 | 0.070415 | 0.002454 | 0.10951 | 0.085583 | -0.035248 | 0.061645 | 0.15248 | 0.05072 | -0.1201 | 0.002454 | 0.027798 | -0.065533 | -0.016906 | 0.14474 | -0.003897 | 0.097881 | 0.02992 | 0.13698 | 0.11305 | -0.007782 | 0.089111 | 0.17994 | 0.078186 | -0.092637 | 0.02992 | 0.055264 | -0.038067 | 0.01056 | 0.059191 | 0.12718 | 0.048266 | 0.11625
1575.4062 | 121.7972 | -121.4447 | 0.086975 | 0.11727 | -0.031363 | 0.061258 | -0.002124 | 0.10493 | 0.076426 | -0.03067 | 0.066223 | 0.1479 | 0.046142 | -0.11094 | 0.002454 | 0.027798 | -0.07469 | -0.016906 | 0.14474 | -0.003897 | 0.088724 | 0.025342 | 0.1324 | 0.10389 | -0.003204 | 0.093689 | 0.17536 | 0.073608 | -0.083478 | 0.02992 | 0.055264 | -0.047224 | 0.01056 | 0.063769 | 0.14091 | 0.043688 | 0.12083
1577.0938 | 121.7331 | -121.4996 | 0.11902 | 0.11727 | -0.026784 | 0.070415 | 0.002454 | 0.10951 | 0.081005 | -0.03067 | 0.061645 | 0.15248 | 0.046142 | -0.10637 | 0.002454 | 0.032376 | -0.065533 | -0.021484 | 0.14474 | 0.000682 | 0.097881 | 0.02992 | 0.13698 | 0.10847 | -0.003204 | 0.089111 | 0.17994 | 0.073608 | -0.078899 | 0.02992 | 0.059842 | -0.038067 | 0.005982 | 0.059191 | 0.12718 | 0.043688 | 0.11167
1578.8438 | 121.6919 | -121.5179 | 0.11444 | 0.11269 | -0.035942 | 0.074994 | 0.007033 | 0.10951 | 0.085583 | -0.03067 | 0.061645 | 0.16164 | 0.05072 | -0.11094 | -0.002124 | 0.02322 | -0.07469 | -0.016906 | 0.14016 | -0.008476 | 0.10246 | 0.034499 | 0.13698 | 0.11305 | -0.003204 | 0.089111 | 0.1891 | 0.078186 | -0.083478 | 0.025342 | 0.050686 | -0.047224 | 0.01056 | 0.063769 | 0.13634 | 0.052844 | 0.12541
1580.5938 | 121.7331 | -121.5271 | 0.11902 | 0.11727 | -0.026784 | 0.061258 | 0.002454 | 0.10951 | 0.090161 | -0.021514 | 0.061645 | 0.15248 | 0.055298 | -0.11094 | 0.002454 | 0.032376 | -0.065533 | -0.016906 | 0.14474 | 0.000682 | 0.088724 | 0.02992 | 0.13698 | 0.11763 | 0.005952 | 0.089111 | 0.17994 | 0.082764 | -0.083478 | 0.02992 | 0.059842 | -0.038067 | 0.01056 | 0.059191 | 0.12718 | 0.052844 | 0.12083
1582.3438 | 121.7926 | -121.5134 | 0.11444 | 0.11727 | -0.031363 | 0.061258 | 0.011611 | 0.11409 | 0.085583 | -0.03067 | 0.070802 | 0.15248 | 0.055298 | -0.10637 | 0.002454 | 0.036954 | -0.070112 | -0.016906 | 0.14474 | -0.003897 | 0.088724 | 0.039077 | 0.14156 | 0.11305 | -0.003204 | 0.098268 | 0.17994 | 0.082764 | -0.078899 | 0.02992 | 0.06442 | -0.042646 | 0.01056 | 0.068348 | 0.14091 | 0.052844 | 0.12541
1584.0938 | 121.7834 | -121.4996 | 0.10529 | 0.11727 | -0.040521 | 0.065837 | 0.002454 | 0.10493 | 0.076426 | -0.03067 | 0.070802 | 0.1479 | 0.05072 | -0.11094 | -0.002124 | 0.027798 | -0.070112 | -0.012328 | 0.14474 | -0.013055 | 0.093303 | 0.02992 | 0.1324 | 0.10389 | -0.003204 | 0.098268 | 0.17536 | 0.078186 | -0.083478 | 0.025342 | 0.055264 | -0.042646 | 0.015138 | 0.072926 | 0.14091 | 0.052844 | 0.12083
1585.8594 | 121.7239 | -121.5546 | 0.13275 | 0.10812 | -0.031363 | 0.074994 | 0.002454 | 0.10951 | 0.085583 | -0.026092 | 0.057066 | 0.15248 | 0.05072 | -0.11552 | -0.002124 | 0.032376 | -0.070112 | -0.016906 | 0.13558 | -0.003897 | 0.10246 | 0.02992 | 0.13698 | 0.11305 | 0.001374 | 0.084532 | 0.17994 | 0.078186 | -0.088057 | 0.025342 | 0.059842 | -0.042646 | 0.01056 | 0.05919 | 0.12718 | 0.052844 | 0.12083
1587.5469 | 121.7514 | -121.5363 | 0.11444 | 0.11727 | -0.031363 | 0.070415 | 0.002454 | 0.11409 | 0.081005 | -0.03067 | 0.066223 | 0.1479 | 0.046142 | -0.10637 | 0.007032 | 0.032376 | -0.065533 | -0.012328 | 0.14474 | -0.003897 | 0.097881 | 0.02992 | 0.14156 | 0.10847 | -0.003204 | 0.093689 | 0.17536 | 0.073608 | -0.078899 | 0.034498 | 0.059842 | -0.038067 | 0.015138 | 0.059191 | 0.13176 | 0.03911 | 0.11167
1589.2969 | 121.8155 | -121.5271 | 0.10529 | 0.12185 | -0.026784 | 0.056679 | 0.002454 | 0.10493 | 0.085583 | -0.026092 | 0.066223 | 0.15248 | 0.05072 | -0.10637 | 0.002454 | 0.027798 | -0.065533 | -0.016906 | 0.14932 | 0.000682 | 0.084145 | 0.02992 | 0.1324 | 0.11305 | 0.001374 | 0.093689 | 0.17994 | 0.078186 | -0.078899 | 0.02992 | 0.055264 | -0.038067 | 0.01056 | 0.063769 | 0.13176 | 0.048266 | 0.11625
1591.0469 | 121.8246 | -121.5363 | 0.13275 | 0.11727 | -0.040521 | 0.061258 | 0.002454 | 0.10951 | 0.085583 | -0.03067 | 0.066223 | 0.15248 | 0.055298 | -0.1201 | 0.002454 | 0.036954 | -0.070112 | -0.016906 | 0.14474 | -0.013055 | 0.088724 | 0.02992 | 0.13698 | 0.11305 | -0.003204 | 0.093689 | 0.17994 | 0.082764 | -0.092637 | 0.02992 | 0.06442 | -0.042646 | 0.01056 | 0.063769 | 0.13633 | 0.052844 | 0.12541
1592.7344 | 121.7148 | -121.5683 | 0.13733 | 0.12185 | -0.031363 | 0.061258 | 0.007033 | 0.11409 | 0.081005 | -0.026092 | 0.057066 | 0.1479 | 0.05072 | -0.10637 | 0.002454 | 0.018642 | -0.083847 | -0.035219 | 0.14932 | -0.003897 | 0.088724 | 0.034499 | 0.14156 | 0.10847 | 0.001374 | 0.084532 | 0.17536 | 0.078186 | -0.078899 | 0.02992 | 0.046108 | -0.056381 | -0.007753 | 0.054612 | 0.14091 | 0.048266 | 0.13457
1594.4688 | 121.8521 | -121.5317 | 0.10529 | 0.11727 | -0.035942 | 0.061258 | -0.002124 | 0.11409 | 0.076426 | -0.03067 | 0.066223 | 0.15248 | 0.046142 | -0.11552 | 0.007032 | 0.032376 | -0.070112 | -0.012328 | 0.14474 | -0.008476 | 0.088724 | 0.025342 | 0.14156 | 0.10389 | -0.003204 | 0.093689 | 0.17994 | 0.073608 | -0.088057 | 0.034498 | 0.059842 | -0.042646 | 0.015138 | 0.059191 | 0.13633 | 0.03911 | 0.11625
1596.2344 | 121.843 | -121.5317 | 0.10071 | 0.11269 | -0.026784 | 0.065837 | 0.011611 | 0.11409 | 0.081005 | -0.026092 | 0.061645 | 0.1479 | 0.046142 | -0.10637 | -0.002124 | 0.02322 | -0.065533 | -0.021484 | 0.14016 | 0.000682 | 0.093303 | 0.039077 | 0.14156 | 0.10847 | 0.001374 | 0.089111 | 0.17536 | 0.073608 | -0.078899 | 0.025342 | 0.050686 | -0.038067 | 0.005982 | 0.063769 | 0.12718 | 0.048266 | 0.11167
1597.9375 | 121.8338 | -121.5775 | 0.13275 | 0.11727 | -0.031363 | 0.065837 | 0.007033 | 0.10951 | 0.090161 | -0.03067 | 0.061645 | 0.13874 | 0.05072 | -0.11094 | -0.002124 | 0.032376 | -0.065533 | -0.016906 | 0.14474 | -0.003897 | 0.093303 | 0.034499 | 0.13698 | 0.11763 | -0.003204 | 0.089111 | 0.16621 | 0.078186 | -0.083478 | 0.025342 | 0.059842 | -0.038067 | 0.01056 | 0.063769 | 0.12718 | 0.052844 | 0.11625
1599.6875 | 121.7651 | -121.6278 | 0.12817 | 0.12185 | -0.031363 | 0.065837 | -0.002124 | 0.10951 | 0.090161 | -0.016936 | 0.066223 | 0.15248 | 0.05072 | -0.11094 | 0.007032 | 0.032376 | -0.070112 | -0.016906 | 0.14932 | -0.003897 | 0.093303 | 0.025342 | 0.13698 | 0.11763 | 0.01053 | 0.093689 | 0.17994 | 0.078186 | -0.083478 | 0.034498 | 0.059842 | -0.042646 | 0.01056 | 0.059191 | 0.13633 | 0.043688 | 0.12083
1601.375 | 121.8887 | -121.5729 | 0.10071 | 0.12185 | -0.035942 | 0.065837 | 0.007033 | 0.10951 | 0.081005 | -0.03067 | 0.066223 | 0.15706 | 0.046142 | -0.11094 | -0.002124 | 0.036954 | -0.065533 | -0.021484 | 0.14932 | -0.008476 | 0.093303 | 0.034499 | 0.13698 | 0.10847 | -0.003204 | 0.093689 | 0.18452 | 0.073608 | -0.083478 | 0.025342 | 0.06442 | -0.038067 | 0.005982 | 0.068347 | 0.13176 | 0.048266 | 0.11167
1603.1094 | 121.9116 | -121.5775 | 0.10071 | 0.12185 | -0.031363 | 0.070415 | 0.011611 | 0.10493 | 0.085583 | -0.021514 | 0.066223 | 0.15706 | 0.064455 | -0.10637 | 0.002454 | 0.027798 | -0.07469 | -0.016906 | 0.14932 | -0.003897 | 0.097881 | 0.039077 | 0.1324 | 0.11305 | 0.005952 | 0.093689 | 0.18452 | 0.091921 | -0.078899 | 0.02992 | 0.055264 | -0.047224 | 0.01056 | 0.063769 | 0.14091 | 0.062001 | 0.13915
1604.8594 | 121.8475 | -121.6141 | 0.11444 | 0.11727 | -0.026784 | 0.070415 | 0.002454 | 0.11867 | 0.081005 | -0.026092 | 0.061645 | 0.15706 | 0.05072 | -0.11094 | 0.002454 | 0.036954 | -0.065533 | -0.016906 | 0.14474 | 0.000682 | 0.097881 | 0.02992 | 0.14613 | 0.10847 | 0.001374 | 0.089111 | 0.18452 | 0.078186 | -0.083478 | 0.02992 | 0.06442 | -0.038067 | 0.01056 | 0.059191 | 0.12718 | 0.048266 | 0.11625
1606.6094 | 121.8292 | -121.5958 | 0.12817 | 0.11727 | -0.031363 | 0.065837 | 0.002454 | 0.11867 | 0.085583 | -0.026092 | 0.057066 | 0.15248 | 0.055298 | -0.11094 | 0.007032 | 0.032376 | -0.070112 | -0.026063 | 0.14474 | -0.003897 | 0.093303 | 0.02992 | 0.14613 | 0.11305 | 0.001374 | 0.084532 | 0.17994 | 0.082764 | -0.083478 | 0.034498 | 0.059842 | -0.042646 | 0.001403 | 0.050034 | 0.12718 | 0.048266 | 0.12541
1608.3125 | 121.843 | -121.6278 | 0.1236 | 0.11727 | -0.031363 | 0.070415 | 0.011611 | 0.10951 | 0.090161 | -0.021514 | 0.066223 | 0.1479 | 0.055298 | -0.11094 | -0.002124 | 0.027798 | -0.07469 | -0.026063 | 0.14474 | -0.003897 | 0.097881 | 0.039077 | 0.13698 | 0.11763 | 0.005952 | 0.093689 | 0.17536 | 0.082764 | -0.083478 | 0.025342 | 0.055264 | -0.047224 | 0.001403 | 0.068347 | 0.14091 | 0.057422 | 0.12999
1610.0469 | 121.8109 | -121.6599 | 0.13733 | 0.12185 | -0.026784 | 0.061258 | 0.007033 | 0.11867 | 0.085583 | -0.021514 | 0.061645 | 0.1479 | 0.055298 | -0.11094 | 0.002454 | 0.027798 | -0.070112 | -0.021484 | 0.14932 | 0.000682 | 0.088724 | 0.034499 | 0.14613 | 0.11305 | 0.005952 | 0.089111 | 0.17536 | 0.082764 | -0.083478 | 0.02992 | 0.055264 | -0.042646 | 0.005982 | 0.059191 | 0.13176 | 0.052844 | 0.12541
1611.7344 | 121.9025 | -121.6278 | 0.07782 | 0.11727 | -0.026784 | 0.061258 | 0.011611 | 0.10951 | 0.085583 | -0.021514 | 0.066223 | 0.15248 | 0.05072 | -0.10637 | -0.002124 | 0.032376 | -0.065533 | -0.021484 | 0.14474 | 0.000682 | 0.088724 | 0.039077 | 0.13698 | 0.11305 | 0.005952 | 0.093689 | 0.17994 | 0.078186 | -0.078899 | 0.025342 | 0.059842 | -0.038067 | 0.005982 | 0.068347 | 0.13176 | 0.052844 | 0.11625
1613.4844 | 121.9482 | -121.582 | 0.10529 | 0.11269 | -0.031363 | 0.065837 | 0.011611 | 0.10036 | 0.085583 | -0.021514 | 0.066223 | 0.1479 | 0.046142 | -0.10637 | 0.007032 | 0.032376 | -0.070112 | -0.012328 | 0.14016 | -0.003897 | 0.093303 | 0.039077 | 0.12782 | 0.11305 | 0.005952 | 0.093689 | 0.17536 | 0.073608 | -0.078899 | 0.034498 | 0.059842 | -0.042646 | 0.015138 | 0.059191 | 0.13633 | 0.03911 | 0.11625
1615.1719 | 121.9437 | -121.6187 | 0.10986 | 0.11727 | -0.031363 | 0.065837 | 0.002454 | 0.10951 | 0.081005 | -0.03067 | 0.061645 | 0.15248 | 0.05072 | -0.11552 | 0.007032 | 0.032376 | -0.070112 | -0.016906 | 0.14474 | -0.003897 | 0.093303 | 0.02992 | 0.13698 | 0.10847 | -0.003204 | 0.089111 | 0.17994 | 0.078186 | -0.088057 | 0.034498 | 0.059842 | -0.042646 | 0.01056 | 0.054613 | 0.13176 | 0.043688 | 0.12083
1616.9219 | 121.9574 | -121.6049 | 0.082397 | 0.12185 | -0.026784 | 0.065837 | 0.002454 | 0.11409 | 0.085583 | -0.021514 | 0.066223 | 0.15248 | 0.055298 | -0.11094 | -0.006702 | 0.027798 | -0.070112 | -0.016906 | 0.14932 | 0.000682 | 0.093303 | 0.02992 | 0.14156 | 0.11305 | 0.005952 | 0.093689 | 0.17994 | 0.082764 | -0.083478 | 0.020764 | 0.055264 | -0.042646 | 0.01056 | 0.072925 | 0.13633 | 0.062 | 0.12541
1618.6562 | 121.9666 | -121.6324 | 0.082397 | 0.12185 | -0.031363 | 0.056679 | 0.007033 | 0.11409 | 0.076426 | -0.021514 | 0.066223 | 0.15248 | 0.05072 | -0.11094 | 0.007032 | 0.02322 | -0.070112 | -0.016906 | 0.14932 | -0.003897 | 0.084145 | 0.034499 | 0.14156 | 0.10389 | 0.005952 | 0.093689 | 0.17994 | 0.078186 | -0.083478 | 0.034498 | 0.050686 | -0.042646 | 0.01056 | 0.059191 | 0.13633 | 0.043688 | 0.12083
1620.3281 | 121.9437 | -121.669 | 0.10071 | 0.12185 | -0.035942 | 0.061258 | 0.007033 | 0.10036 | 0.085583 | -0.03067 | 0.070802 | 0.1479 | 0.05072 | -0.11094 | -0.002124 | 0.036954 | -0.070112 | -0.012328 | 0.14932 | -0.008476 | 0.088724 | 0.034499 | 0.12782 | 0.11305 | -0.003204 | 0.098268 | 0.17536 | 0.078186 | -0.083478 | 0.025342 | 0.06442 | -0.042646 | 0.015138 | 0.072926 | 0.14091 | 0.052844 | 0.12083
1622.0781 | 121.9757 | -121.6415 | 0.068665 | 0.11727 | -0.026784 | 0.065837 | 0.007033 | 0.10951 | 0.081005 | -0.021514 | 0.066223 | 0.15248 | 0.055298 | -0.11552 | 0.007032 | 0.02322 | -0.070112 | -0.016906 | 0.14474 | 0.000682 | 0.093303 | 0.034499 | 0.13698 | 0.10847 | 0.005952 | 0.093689 | 0.17994 | 0.082764 | -0.088057 | 0.034498 | 0.050686 | -0.042646 | 0.01056 | 0.059191 | 0.13633 | 0.048266 | 0.12541
1623.7656 | 121.9711 | -121.6232 | 0.082397 | 0.11269 | -0.031363 | 0.056679 | 0.011611 | 0.11409 | 0.085583 | -0.03067 | 0.070802 | 0.15706 | 0.05072 | -0.11094 | -0.002124 | 0.027798 | -0.065533 | -0.012328 | 0.14016 | -0.003897 | 0.084145 | 0.039077 | 0.14156 | 0.11305 | -0.003204 | 0.098268 | 0.18452 | 0.078186 | -0.083478 | 0.025342 | 0.055264 | -0.038067 | 0.015138 | 0.072926 | 0.13633 | 0.052844 | 0.11625
1625.5156 | 121.9162 | -121.6827 | 0.11444 | 0.11727 | -0.031363 | 0.056679 | 0.01619 | 0.10951 | 0.085583 | -0.026092 | 0.061645 | 0.1479 | 0.046142 | -0.10637 | 0.002454 | 0.036954 | -0.065533 | -0.016906 | 0.14474 | -0.003897 | 0.084145 | 0.043656 | 0.13698 | 0.11305 | 0.001374 | 0.089111 | 0.17536 | 0.073608 | -0.078899 | 0.02992 | 0.06442 | -0.038067 | 0.01056 | 0.059191 | 0.12718 | 0.043688 | 0.11167
1627.25 | 121.875 | -121.7102 | 0.11444 | 0.11727 | -0.031363 | 0.061258 | 0.002454 | 0.11409 | 0.081005 | -0.026092 | 0.066223 | 0.14332 | 0.046142 | -0.11094 | 0.007032 | 0.032376 | -0.07469 | -0.021484 | 0.14474 | -0.003897 | 0.088724 | 0.02992 | 0.14156 | 0.10847 | 0.001374 | 0.093689 | 0.17079 | 0.073608 | -0.083478 | 0.034498 | 0.059842 | -0.047224 | 0.005982 | 0.059191 | 0.14091 | 0.03911 | 0.12083
1629 | 121.994 | -121.6507 | 0.086975 | 0.11727 | -0.035942 | 0.052101 | 0.007033 | 0.10493 | 0.090161 | -0.026092 | 0.070802 | 0.1479 | 0.046142 | -0.10179 | 0.002454 | 0.032376 | -0.07469 | -0.016906 | 0.14474 | -0.008476 | 0.079567 | 0.034499 | 0.1324 | 0.11763 | 0.001374 | 0.098268 | 0.17536 | 0.073608 | -0.07432 | 0.02992 | 0.059842 | -0.047224 | 0.01056 | 0.068348 | 0.14549 | 0.043688 | 0.12083
1630.75 | 122.0078 | -121.6644 | 0.10529 | 0.11727 | -0.026784 | 0.070415 | 0.01619 | 0.10493 | 0.076426 | -0.021514 | 0.061645 | 0.15248 | 0.046142 | -0.10179 | -0.006702 | 0.027798 | -0.070112 | -0.016906 | 0.14474 | 0.000682 | 0.097881 | 0.043656 | 0.1324 | 0.10389 | 0.005952 | 0.089111 | 0.17994 | 0.073608 | -0.07432 | 0.020764 | 0.055264 | -0.042646 | 0.01056 | 0.068347 | 0.13176 | 0.052844 | 0.11625
1632.4375 | 122.0123 | -121.6736 | 0.10071 | 0.11727 | -0.031363 | 0.061258 | 0.002454 | 0.10951 | 0.081005 | -0.026092 | 0.066223 | 0.15248 | 0.05072 | -0.10179 | 0.002454 | 0.027798 | -0.065533 | -0.016906 | 0.14474 | -0.003897 | 0.088724 | 0.02992 | 0.13698 | 0.10847 | 0.001374 | 0.093689 | 0.17994 | 0.078186 | -0.07432 | 0.02992 | 0.055264 | -0.038067 | 0.01056 | 0.063769 | 0.13176 | 0.048266 | 0.11625
1634.1875 | 121.9025 | -121.7285 | 0.10986 | 0.11727 | -0.031363 | 0.056679 | 0.002454 | 0.11409 | 0.085583 | -0.035248 | 0.061645 | 0.15248 | 0.046142 | -0.11552 | 0.002454 | 0.027798 | -0.070112 | -0.021484 | 0.14474 | -0.003897 | 0.084145 | 0.02992 | 0.14156 | 0.11305 | -0.007782 | 0.089111 | 0.17994 | 0.073608 | -0.088057 | 0.02992 | 0.055264 | -0.042646 | 0.005982 | 0.059191 | 0.13176 | 0.043688 | 0.11625
1635.875 | 121.8933 | -121.7377 | 0.13733 | 0.12185 | -0.031363 | 0.061258 | 0.01619 | 0.10493 | 0.081005 | -0.026092 | 0.070802 | 0.14332 | 0.064455 | -0.11094 | 0.002454 | 0.032376 | -0.065533 | -0.016906 | 0.14932 | -0.003897 | 0.088724 | 0.043656 | 0.1324 | 0.10847 | 0.001374 | 0.098268 | 0.17079 | 0.091921 | -0.083478 | 0.02992 | 0.059842 | -0.038067 | 0.01056 | 0.068348 | 0.13633 | 0.062001 | 0.12999
1637.625 | 121.9345 | -121.7285 | 0.1236 | 0.11727 | -0.026784 | 0.070415 | 0.007033 | 0.11409 | 0.085583 | -0.021514 | 0.066223 | 0.1479 | 0.05072 | -0.11094 | -0.002124 | 0.02322 | -0.060955 | -0.021484 | 0.14474 | 0.000682 | 0.097881 | 0.034499 | 0.14156 | 0.11305 | 0.005952 | 0.093689 | 0.17536 | 0.078186 | -0.083478 | 0.025342 | 0.050686 | -0.033489 | 0.005982 | 0.068347 | 0.12718 | 0.052844 | 0.11167
1639.375 | 122.0215 | -121.6873 | 0.09613 | 0.11727 | -0.031363 | 0.061258 | 0.007033 | 0.10951 | 0.085583 | -0.026092 | 0.057066 | 0.1479 | 0.05072 | -0.11094 | 0.002454 | 0.02322 | -0.070112 | -0.026063 | 0.14474 | -0.003897 | 0.088724 | 0.034499 | 0.13698 | 0.11305 | 0.001374 | 0.084532 | 0.17536 | 0.078186 | -0.083478 | 0.02992 | 0.050686 | -0.042646 | 0.001403 | 0.054612 | 0.12718 | 0.048266 | 0.12083
1641.0469 | 122.0352 | -121.6965 | 0.086975 | 0.11727 | -0.031363 | 0.061258 | 0.011611 | 0.11409 | 0.081005 | -0.03067 | 0.066223 | 0.15248 | 0.059877 | -0.10637 | -0.002124 | 0.027798 | -0.065533 | -0.012328 | 0.14474 | -0.003897 | 0.088724 | 0.039077 | 0.14156 | 0.10847 | -0.003204 | 0.093689 | 0.17994 | 0.087343 | -0.078899 | 0.025342 | 0.055264 | -0.038067 | 0.015138 | 0.068347 | 0.13176 | 0.062001 | 0.12541
1642.7969 | 121.9574 | -121.7285 | 0.13275 | 0.11269 | -0.035942 | 0.056679 | 0.011611 | 0.10951 | 0.085583 | -0.026092 | 0.066223 | 0.16164 | 0.055298 | -0.11094 | 0.007032 | 0.032376 | -0.060955 | -0.012328 | 0.14016 | -0.008476 | 0.084145 | 0.039077 | 0.13698 | 0.11305 | 0.001374 | 0.093689 | 0.1891 | 0.082764 | -0.083478 | 0.034498 | 0.059842 | -0.033489 | 0.015138 | 0.059191 | 0.12718 | 0.048266 | 0.11625
1644.5312 | 121.9254 | -121.7194 | 0.14191 | 0.12185 | -0.026784 | 0.070415 | 0.011611 | 0.11409 | 0.081005 | -0.026092 | 0.057066 | 0.1479 | 0.05072 | -0.10637 | 0.007032 | 0.02322 | -0.070112 | -0.021484 | 0.14932 | 0.000682 | 0.097881 | 0.039077 | 0.14156 | 0.10847 | 0.001374 | 0.084532 | 0.17536 | 0.078186 | -0.078899 | 0.034498 | 0.050686 | -0.042646 | 0.005982 | 0.050034 | 0.12718 | 0.043688 | 0.12083
1646.2031 | 122.049 | -121.7148 | 0.10529 | 0.10812 | -0.035942 | 0.065837 | 0.011611 | 0.10951 | 0.081005 | -0.03067 | 0.061645 | 0.15706 | 0.055298 | -0.11552 | 0.002454 | 0.027798 | -0.070112 | -0.016906 | 0.13558 | -0.008476 | 0.093303 | 0.039077 | 0.13698 | 0.10847 | -0.003204 | 0.089111 | 0.18452 | 0.082764 | -0.088057 | 0.02992 | 0.055264 | -0.042646 | 0.01056 | 0.059191 | 0.13176 | 0.052844 | 0.12541
1647.9531 | 121.962 | -121.7468 | 0.1236 | 0.11269 | -0.026784 | 0.061258 | 0.002454 | 0.10493 | 0.085583 | -0.026092 | 0.057066 | 0.15248 | 0.055298 | -0.11094 | -0.002124 | 0.02322 | -0.070112 | -0.012328 | 0.14016 | 0.000682 | 0.088724 | 0.02992 | 0.1324 | 0.11305 | 0.001374 | 0.084532 | 0.17994 | 0.082764 | -0.083478 | 0.025342 | 0.050686 | -0.042646 | 0.015138 | 0.05919 | 0.12718 | 0.057422 | 0.12541
1649.6875 | 121.9666 | -121.7743 | 0.11902 | 0.11727 | -0.035942 | 0.052101 | 0.011611 | 0.11409 | 0.076426 | -0.021514 | 0.070802 | 0.14332 | 0.046142 | -0.10637 | -0.006702 | 0.032376 | -0.070112 | -0.026063 | 0.14474 | -0.008476 | 0.079567 | 0.039077 | 0.14156 | 0.10389 | 0.005952 | 0.098268 | 0.17079 | 0.073608 | -0.078899 | 0.020764 | 0.059842 | -0.042646 | 0.001403 | 0.077504 | 0.14091 | 0.052844 | 0.11625
1651.3594 | 121.9528 | -121.7697 | 0.11444 | 0.12185 | -0.031363 | 0.056679 | 0.002454 | 0.10951 | 0.081005 | -0.03067 | 0.061645 | 0.1479 | 0.055298 | -0.11094 | -0.002124 | 0.036954 | -0.079268 | -0.016906 | 0.14932 | -0.003897 | 0.084145 | 0.02992 | 0.13698 | 0.10847 | -0.003204 | 0.089111 | 0.17536 | 0.082764 | -0.083478 | 0.025342 | 0.06442 | -0.051802 | 0.01056 | 0.063769 | 0.14091 | 0.057422 | 0.13457
1653.1094 | 122.081 | -121.7239 | 0.091553 | 0.12185 | -0.026784 | 0.056679 | 0.007033 | 0.10951 | 0.076426 | -0.026092 | 0.061645 | 0.15706 | 0.055298 | -0.10637 | 0.002454 | 0.027798 | -0.070112 | -0.012328 | 0.14932 | 0.000682 | 0.084145 | 0.034499 | 0.13698 | 0.10389 | 0.001374 | 0.089111 | 0.18452 | 0.082764 | -0.078899 | 0.02992 | 0.055264 | -0.042646 | 0.015138 | 0.059191 | 0.13176 | 0.052844 | 0.12541
1654.8438 | 122.0215 | -121.756 | 0.10071 | 0.12185 | -0.035942 | 0.065837 | 0.007033 | 0.10493 | 0.076426 | -0.03067 | 0.066223 | 0.15706 | 0.046142 | -0.10637 | 0.007032 | 0.02322 | -0.070112 | -0.016906 | 0.14932 | -0.008476 | 0.093303 | 0.034499 | 0.1324 | 0.10389 | -0.003204 | 0.093689 | 0.18452 | 0.073608 | -0.078899 | 0.034498 | 0.050686 | -0.042646 | 0.01056 | 0.059191 | 0.13633 | 0.03911 | 0.11625
1656.5781 | 122.0306 | -121.7697 | 0.1236 | 0.12185 | -0.035942 | 0.061258 | 0.002454 | 0.10951 | 0.090161 | -0.026092 | 0.066223 | 0.15248 | 0.032407 | -0.10637 | -0.002124 | 0.027798 | -0.070112 | -0.012328 | 0.14932 | -0.008476 | 0.088724 | 0.02992 | 0.13698 | 0.11763 | 0.001374 | 0.093689 | 0.17994 | 0.059873 | -0.078899 | 0.025342 | 0.055264 | -0.042646 | 0.015138 | 0.068347 | 0.13633 | 0.034531 | 0.10252
1658.25 | 121.9437 | -121.8018 | 0.1236 | 0.12185 | -0.035942 | 0.065837 | 0.011611 | 0.10951 | 0.081005 | -0.021514 | 0.061645 | 0.15248 | 0.05072 | -0.10637 | -0.006702 | 0.027798 | -0.070112 | -0.021484 | 0.14932 | -0.008476 | 0.093303 | 0.039077 | 0.13698 | 0.10847 | 0.005952 | 0.089111 | 0.17994 | 0.078186 | -0.078899 | 0.020764 | 0.055264 | -0.042646 | 0.005982 | 0.068347 | 0.13176 | 0.057422 | 0.12083
1659.9844 | 121.9849 | -121.8109 | 0.13733 | 0.11269 | -0.026784 | 0.065837 | 0.007033 | 0.11409 | 0.076426 | -0.026092 | 0.061645 | 0.1479 | 0.046142 | -0.11094 | 0.002454 | 0.02322 | -0.070112 | -0.021484 | 0.14016 | 0.000682 | 0.093303 | 0.034499 | 0.14156 | 0.10389 | 0.001374 | 0.089111 | 0.17536 | 0.073608 | -0.083478 | 0.02992 | 0.050686 | -0.042646 | 0.005982 | 0.059191 | 0.13176 | 0.043688 | 0.11625
1661.7188 | 122.0856 | -121.7514 | 0.10529 | 0.11727 | -0.031363 | 0.065837 | 0.007033 | 0.10951 | 0.076426 | -0.021514 | 0.061645 | 0.15248 | 0.046142 | -0.11094 | 0.002454 | 0.02322 | -0.07469 | -0.012328 | 0.14474 | -0.003897 | 0.093303 | 0.034499 | 0.13698 | 0.10389 | 0.005952 | 0.089111 | 0.17994 | 0.073608 | -0.083478 | 0.02992 | 0.050686 | -0.047224 | 0.015138 | 0.059191 | 0.13634 | 0.043688 | 0.12083
1663.4844 | 122.0627 | -121.7789 | 0.073242 | 0.11727 | -0.026784 | 0.065837 | 0.007033 | 0.10493 | 0.085583 | -0.03067 | 0.066223 | 0.1479 | 0.05072 | -0.11552 | 0.002454 | 0.036954 | -0.070112 | -0.012328 | 0.14474 | 0.000682 | 0.093303 | 0.034499 | 0.1324 | 0.11305 | -0.003204 | 0.093689 | 0.17536 | 0.078186 | -0.088057 | 0.02992 | 0.06442 | -0.042646 | 0.015138 | 0.063769 | 0.13633 | 0.048266 | 0.12083
1665.1562 | 122.0947 | -121.7789 | 0.11444 | 0.10812 | -0.035942 | 0.065837 | -0.002124 | 0.10493 | 0.081005 | -0.021514 | 0.070802 | 0.1479 | 0.046142 | -0.10637 | -0.002124 | 0.032376 | -0.070112 | -0.012328 | 0.13558 | -0.008476 | 0.093303 | 0.025342 | 0.1324 | 0.10847 | 0.005952 | 0.098268 | 0.17536 | 0.073608 | -0.078899 | 0.025342 | 0.059842 | -0.042646 | 0.015138 | 0.072926 | 0.14091 | 0.048266 | 0.11625
1666.9062 | 122.0856 | -121.7697 | 0.11444 | 0.11727 | -0.031363 | 0.065837 | 0.002454 | 0.11409 | 0.081005 | -0.026092 | 0.052488 | 0.15248 | 0.046142 | -0.10179 | 0.002454 | 0.02322 | -0.070112 | -0.012328 | 0.14474 | -0.003897 | 0.093303 | 0.02992 | 0.14156 | 0.10847 | 0.001374 | 0.079954 | 0.17994 | 0.073608 | -0.07432 | 0.02992 | 0.050686 | -0.042646 | 0.015138 | 0.050034 | 0.1226 | 0.043688 | 0.11625
1668.5938 | 121.994 | -121.8246 | 0.14648 | 0.11727 | -0.026784 | 0.065837 | -0.002124 | 0.10951 | 0.081005 | -0.021514 | 0.066223 | 0.15248 | 0.046142 | -0.11552 | 0.002454 | 0.027798 | -0.07469 | -0.016906 | 0.14474 | 0.000682 | 0.093303 | 0.025342 | 0.13698 | 0.10847 | 0.005952 | 0.093689 | 0.17994 | 0.073608 | -0.088057 | 0.02992 | 0.055264 | -0.047224 | 0.01056 | 0.063769 | 0.14091 | 0.043688 | 0.12083
1670.3438 | 122.1222 | -121.8018 | 0.11902 | 0.11269 | -0.035942 | 0.065837 | 0.002454 | 0.10951 | 0.081005 | -0.016936 | 0.066223 | 0.15706 | 0.05072 | -0.11552 | -0.002124 | 0.027798 | -0.070112 | -0.012328 | 0.14016 | -0.008476 | 0.093303 | 0.02992 | 0.13698 | 0.10847 | 0.01053 | 0.093689 | 0.18452 | 0.078186 | -0.088057 | 0.025342 | 0.055264 | -0.042646 | 0.015138 | 0.068347 | 0.13633 | 0.052844 | 0.12083
1672.0156 | 122.0078 | -121.8246 | 0.11902 | 0.11269 | -0.022205 | 0.070415 | 0.007033 | 0.10951 | 0.076426 | -0.021514 | 0.061645 | 0.15706 | 0.055298 | -0.10637 | 0.002454 | 0.032376 | -0.070112 | -0.016906 | 0.14016 | 0.005261 | 0.097881 | 0.034499 | 0.13698 | 0.10389 | 0.005952 | 0.089111 | 0.18452 | 0.082764 | -0.078899 | 0.02992 | 0.059842 | -0.042646 | 0.01056 | 0.059191 | 0.13176 | 0.052844 | 0.12541
1673.75 | 122.0352 | -121.8109 | 0.11902 | 0.11269 | -0.031363 | 0.065837 | 0.002454 | 0.10493 | 0.081005 | -0.021514 | 0.066223 | 0.1479 | 0.059877 | -0.11552 | 0.007032 | 0.032376 | -0.07469 | -0.021484 | 0.14016 | -0.003897 | 0.093303 | 0.02992 | 0.1324 | 0.10847 | 0.005952 | 0.093689 | 0.17536 | 0.087343 | -0.088057 | 0.034498 | 0.059842 | -0.047224 | 0.005982 | 0.059191 | 0.14091 | 0.052845 | 0.13457
1675.5 | 122.0352 | -121.7789 | 0.10986 | 0.11727 | -0.035942 | 0.056679 | 0.002454 | 0.10951 | 0.090161 | -0.012357 | 0.061645 | 0.15248 | 0.055298 | -0.11552 | 0.002454 | 0.032376 | -0.07469 | -0.021484 | 0.14474 | -0.008476 | 0.084145 | 0.02992 | 0.13698 | 0.11763 | 0.015109 | 0.089111 | 0.17994 | 0.082764 | -0.088057 | 0.02992 | 0.059842 | -0.047224 | 0.005982 | 0.059191 | 0.13634 | 0.052844 | 0.12999
1677.2188 | 122.113 | -121.7926 | 0.10986 | 0.11727 | -0.026784 | 0.065837 | 0.002454 | 0.10493 | 0.076426 | -0.021514 | 0.066223 | 0.1479 | 0.055298 | -0.11552 | 0.002454 | 0.032376 | -0.070112 | -0.021484 | 0.14474 | 0.000682 | 0.093303 | 0.02992 | 0.1324 | 0.10389 | 0.005952 | 0.093689 | 0.17536 | 0.082764 | -0.088057 | 0.02992 | 0.059842 | -0.042646 | 0.005982 | 0.063769 | 0.13633 | 0.052844 | 0.12541
1678.9062 | 122.1039 | -121.7697 | 0.16479 | 0.12643 | -0.031363 | 0.061258 | -0.002124 | 0.10951 | 0.081005 | -0.026092 | 0.070802 | 0.15248 | 0.059877 | -0.11552 | 0.007032 | 0.02322 | -0.07469 | -0.012328 | 0.1539 | -0.003897 | 0.088724 | 0.025342 | 0.13698 | 0.10847 | 0.001374 | 0.098268 | 0.17994 | 0.087343 | -0.088057 | 0.034498 | 0.050686 | -0.047224 | 0.015138 | 0.06377 | 0.14549 | 0.052845 | 0.13457
1680.6562 | 122.1359 | -121.8475 | 0.09613 | 0.12185 | -0.035942 | 0.056679 | -0.002124 | 0.10951 | 0.081005 | -0.021514 | 0.057066 | 0.15248 | 0.055298 | -0.10637 | -0.002124 | 0.027798 | -0.065533 | -0.012328 | 0.14932 | -0.008476 | 0.084145 | 0.025342 | 0.13698 | 0.10847 | 0.005952 | 0.084532 | 0.17994 | 0.082764 | -0.078899 | 0.025342 | 0.055264 | -0.038067 | 0.015138 | 0.05919 | 0.1226 | 0.057422 | 0.12083
1682.3906 | 122.1222 | -121.8292 | 0.10986 | 0.12185 | -0.026784 | 0.061258 | 0.002454 | 0.10951 | 0.081005 | -0.03067 | 0.057066 | 0.1479 | 0.046142 | -0.11552 | 0.002454 | 0.018642 | -0.070112 | -0.021484 | 0.14932 | 0.000682 | 0.088724 | 0.02992 | 0.13698 | 0.10847 | -0.003204 | 0.084532 | 0.17536 | 0.073608 | -0.088057 | 0.02992 | 0.046108 | -0.042646 | 0.005982 | 0.054612 | 0.12718 | 0.043688 | 0.11625
1684.0781 | 122.1313 | -121.8338 | 0.10986 | 0.11727 | -0.031363 | 0.061258 | 0.002454 | 0.10036 | 0.076426 | -0.021514 | 0.066223 | 0.15706 | 0.05072 | -0.10637 | 0.002454 | 0.036954 | -0.070112 | -0.016906 | 0.14474 | -0.003897 | 0.088724 | 0.02992 | 0.12782 | 0.10389 | 0.005952 | 0.093689 | 0.18452 | 0.078186 | -0.078899 | 0.02992 | 0.06442 | -0.042646 | 0.01056 | 0.063769 | 0.13633 | 0.048266 | 0.12083
1685.75 | 122.0215 | -121.8521 | 0.14191 | 0.12643 | -0.035942 | 0.061258 | 0.002454 | 0.10951 | 0.081005 | -0.026092 | 0.061645 | 0.1479 | 0.055298 | -0.11094 | -0.006702 | 0.032376 | -0.065533 | -0.016906 | 0.1539 | -0.008476 | 0.088724 | 0.02992 | 0.13698 | 0.10847 | 0.001374 | 0.089111 | 0.17536 | 0.082764 | -0.083478 | 0.020764 | 0.059842 | -0.038067 | 0.01056 | 0.068347 | 0.12718 | 0.062 | 0.12083
1687.4844 | 122.1405 | -121.8338 | 0.10529 | 0.11727 | -0.035942 | 0.065837 | 0.007033 | 0.10493 | 0.081005 | -0.026092 | 0.066223 | 0.15706 | 0.05072 | -0.10637 | 0.002454 | 0.032376 | -0.070112 | -0.021484 | 0.14474 | -0.008476 | 0.093303 | 0.034499 | 0.1324 | 0.10847 | 0.001374 | 0.093689 | 0.18452 | 0.078186 | -0.078899 | 0.02992 | 0.059842 | -0.042646 | 0.005982 | 0.063769 | 0.13633 | 0.048266 | 0.12083
1689.1719 | 122.0398 | -121.8567 | 0.14648 | 0.12643 | -0.031363 | 0.061258 | 0.007033 | 0.10951 | 0.081005 | -0.016936 | 0.061645 | 0.1479 | 0.055298 | -0.10637 | -0.006702 | 0.032376 | -0.065533 | -0.016906 | 0.1539 | -0.003897 | 0.088724 | 0.034499 | 0.13698 | 0.10847 | 0.01053 | 0.089111 | 0.17536 | 0.082764 | -0.078899 | 0.020764 | 0.059842 | -0.038067 | 0.01056 | 0.068347 | 0.12718 | 0.062 | 0.12083
1690.9375 | 122.0764 | -121.8567 | 0.1236 | 0.11727 | -0.022205 | 0.065837 | 0.002454 | 0.10493 | 0.090161 | -0.021514 | 0.070802 | 0.1479 | 0.055298 | -0.11094 | 0.002454 | 0.027798 | -0.070112 | -0.026063 | 0.14474 | 0.005261 | 0.093303 | 0.02992 | 0.1324 | 0.11763 | 0.005952 | 0.098268 | 0.17536 | 0.082764 | -0.083478 | 0.02992 | 0.055264 | -0.042646 | 0.001403 | 0.068348 | 0.14091 | 0.052844 | 0.12541
1692.6875 | 122.1313 | -121.7834 | 0.14191 | 0.11727 | -0.035942 | 0.056679 | 0.002454 | 0.11409 | 0.085583 | -0.03067 | 0.066223 | 0.1479 | 0.059877 | -0.10637 | 0.007032 | 0.032376 | -0.070112 | -0.016906 | 0.14474 | -0.008476 | 0.084145 | 0.02992 | 0.14156 | 0.11305 | -0.003204 | 0.093689 | 0.17536 | 0.087343 | -0.078899 | 0.034498 | 0.059842 | -0.042646 | 0.01056 | 0.059191 | 0.13633 | 0.052845 | 0.12999
1694.4219 | 122.113 | -121.843 | 0.13733 | 0.11269 | -0.031363 | 0.061258 | 0.011611 | 0.10951 | 0.076426 | -0.026092 | 0.066223 | 0.15248 | 0.055298 | -0.11552 | 0.002454 | 0.02322 | -0.065533 | -0.016906 | 0.14016 | -0.003897 | 0.088724 | 0.039077 | 0.13698 | 0.10389 | 0.001374 | 0.093689 | 0.17994 | 0.082764 | -0.088057 | 0.02992 | 0.050686 | -0.038067 | 0.01056 | 0.063769 | 0.13176 | 0.052844 | 0.12083
1696.0938 | 122.049 | -121.8201 | 0.22888 | 0.11727 | -0.022205 | 0.061258 | 0.007033 | 0.10951 | 0.090161 | -0.03067 | 0.066223 | 0.1479 | 0.046142 | -0.11094 | 0.01161 | 0.032376 | -0.07469 | -0.021484 | 0.14474 | 0.005261 | 0.088724 | 0.034499 | 0.13698 | 0.11763 | -0.003204 | 0.093689 | 0.17536 | 0.073608 | -0.083478 | 0.039076 | 0.059842 | -0.047224 | 0.005982 | 0.054613 | 0.14091 | 0.034532 | 0.12083
1697.8438 | 122.113 | -121.875 | 0.13275 | 0.12185 | -0.026784 | 0.061258 | 0.002454 | 0.10951 | 0.076426 | -0.03067 | 0.066223 | 0.15248 | 0.055298 | -0.11094 | -0.002124 | 0.032376 | -0.07469 | -0.021484 | 0.14932 | 0.000682 | 0.088724 | 0.02992 | 0.13698 | 0.10389 | -0.003204 | 0.093689 | 0.17994 | 0.082764 | -0.083478 | 0.025342 | 0.059842 | -0.047224 | 0.005982 | 0.068347 | 0.14091 | 0.057422 | 0.12999
1699.5156 | 122.0306 | -121.8842 | 0.14191 | 0.12185 | -0.031363 | 0.065837 | 0.007033 | 0.11409 | 0.085583 | -0.021514 | 0.070802 | 0.14332 | 0.05072 | -0.11552 | 0.002454 | 0.027798 | -0.070112 | -0.012328 | 0.14932 | -0.003897 | 0.093303 | 0.034499 | 0.14156 | 0.11305 | 0.005952 | 0.098268 | 0.17079 | 0.078186 | -0.088057 | 0.02992 | 0.055264 | -0.042646 | 0.015138 | 0.068348 | 0.14091 | 0.048266 | 0.12083
1701.25 | 122.0261 | -121.8887 | 0.14648 | 0.11727 | -0.031363 | 0.065837 | 0.002454 | 0.11409 | 0.085583 | -0.035248 | 0.057066 | 0.1479 | 0.05072 | -0.11552 | -0.002124 | 0.027798 | -0.065533 | -0.021484 | 0.14474 | -0.003897 | 0.093303 | 0.02992 | 0.14156 | 0.11305 | -0.007782 | 0.084532 | 0.17536 | 0.078186 | -0.088057 | 0.025342 | 0.055264 | -0.038067 | 0.005982 | 0.05919 | 0.1226 | 0.052844 | 0.11625
1703 | 122.0627 | -121.8887 | 0.13275 | 0.12185 | -0.022205 | 0.056679 | 0.011611 | 0.11409 | 0.085583 | -0.03067 | 0.061645 | 0.15248 | 0.05072 | -0.11552 | 0.002454 | 0.032376 | -0.070112 | -0.021484 | 0.14932 | 0.005261 | 0.084145 | 0.039077 | 0.14156 | 0.11305 | -0.003204 | 0.089111 | 0.17994 | 0.078186 | -0.088057 | 0.02992 | 0.059842 | -0.042646 | 0.005982 | 0.059191 | 0.13176 | 0.048266 | 0.12083
1704.6719 | 122.1405 | -121.8704 | 0.11902 | 0.11727 | -0.035942 | 0.061258 | 0.007033 | 0.10951 | 0.081005 | -0.03067 | 0.061645 | 0.15248 | 0.041563 | -0.11552 | 0.002454 | 0.032376 | -0.070112 | -0.021484 | 0.14474 | -0.008476 | 0.088724 | 0.034499 | 0.13698 | 0.10847 | -0.003204 | 0.089111 | 0.17994 | 0.069029 | -0.088057 | 0.02992 | 0.059842 | -0.042646 | 0.005982 | 0.059191 | 0.13176 | 0.039109 | 0.11167
1706.4219 | 122.2 | -121.8658 | 0.1236 | 0.11727 | -0.026784 | 0.070415 | 0.007033 | 0.10036 | 0.085583 | -0.021514 | 0.061645 | 0.15248 | 0.064455 | -0.10637 | 0.002454 | 0.02322 | -0.07469 | -0.016906 | 0.14474 | 0.000682 | 0.097881 | 0.034499 | 0.12782 | 0.11305 | 0.005952 | 0.089111 | 0.17994 | 0.091921 | -0.078899 | 0.02992 | 0.050686 | -0.047224 | 0.01056 | 0.059191 | 0.13634 | 0.062001 | 0.13915
1708.1094 | 122.0947 | -121.8842 | 0.13733 | 0.12185 | -0.031363 | 0.065837 | 0.002454 | 0.10493 | 0.076426 | -0.021514 | 0.066223 | 0.15248 | 0.055298 | -0.1201 | 0.01161 | 0.018642 | -0.070112 | -0.016906 | 0.14932 | -0.003897 | 0.093303 | 0.02992 | 0.1324 | 0.10389 | 0.005952 | 0.093689 | 0.17994 | 0.082764 | -0.092637 | 0.039076 | 0.046108 | -0.042646 | 0.01056 | 0.054613 | 0.13633 | 0.043688 | 0.12541
1709.8594 | 122.1771 | -121.8475 | 0.11902 | 0.11727 | -0.031363 | 0.061258 | 0.007033 | 0.10951 | 0.081005 | -0.026092 | 0.034174 | 0.1479 | 0.05072 | -0.10637 | -0.002124 | 0.032376 | -0.070112 | -0.016906 | 0.14474 | -0.003897 | 0.088724 | 0.034499 | 0.13698 | 0.10847 | 0.001374 | 0.06164 | 0.17536 | 0.078186 | -0.078899 | 0.025342 | 0.059842 | -0.042646 | 0.01056 | 0.036298 | 0.10429 | 0.052844 | 0.12083
1711.5469 | 122.0581 | -121.9025 | 0.14648 | 0.12185 | -0.022205 | 0.065837 | 0.011611 | 0.10493 | 0.085583 | -0.03067 | 0.038752 | 0.14332 | 0.046142 | -0.10637 | -0.002124 | 0.032376 | -0.070112 | -0.021484 | 0.14932 | 0.005261 | 0.093303 | 0.039077 | 0.1324 | 0.11305 | -0.003204 | 0.066218 | 0.17079 | 0.073608 | -0.078899 | 0.025342 | 0.059842 | -0.042646 | 0.005982 | 0.040876 | 0.10886 | 0.048266 | 0.11625
1713.2969 | 122.1268 | -121.7972 | 0.10986 | 0.11727 | -0.031363 | 0.056679 | 0.007033 | 0.10951 | 0.076426 | -0.026092 | 0.038752 | 0.1479 | 0.05072 | -0.10637 | -0.006702 | 0.027798 | -0.060955 | -0.016906 | 0.14474 | -0.003897 | 0.084145 | 0.034499 | 0.13698 | 0.10389 | 0.001374 | 0.066218 | 0.17536 | 0.078186 | -0.078899 | 0.020764 | 0.055264 | -0.033489 | 0.01056 | 0.045454 | 0.099707 | 0.057422 | 0.11167
1715.0469 | 122.1268 | -121.7926 | 0.11902 | 0.11269 | -0.031363 | 0.056679 | 0.002454 | 0.10951 | 0.081005 | -0.026092 | 0.043331 | 0.15248 | 0.041563 | -0.10637 | -0.002124 | 0.032376 | -0.065533 | -0.016906 | 0.14016 | -0.003897 | 0.084145 | 0.02992 | 0.13698 | 0.10847 | 0.001374 | 0.070797 | 0.17994 | 0.069029 | -0.078899 | 0.025342 | 0.059842 | -0.038067 | 0.01056 | 0.045455 | 0.10886 | 0.043687 | 0.1071
1716.7344 | 122.0718 | -121.8384 | 0.14191 | 0.11269 | -0.026784 | 0.065837 | 0.002454 | 0.10493 | 0.081005 | -0.035248 | 0.038752 | 0.1479 | 0.041563 | -0.11094 | 0.007032 | 0.032376 | -0.065533 | -0.016906 | 0.14016 | 0.000682 | 0.093303 | 0.02992 | 0.1324 | 0.10847 | -0.007782 | 0.066218 | 0.17536 | 0.069029 | -0.083478 | 0.034498 | 0.059842 | -0.038067 | 0.01056 | 0.03172 | 0.10428 | 0.034531 | 0.1071
1718.5 | 122.0947 | -121.8109 | 0.11444 | 0.11727 | -0.031363 | 0.070415 | 0.007033 | 0.10493 | 0.090161 | -0.03067 | 0.038752 | 0.1479 | 0.041563 | -0.11094 | -0.002124 | 0.032376 | -0.065533 | -0.016906 | 0.14474 | -0.003897 | 0.097881 | 0.034499 | 0.1324 | 0.11763 | -0.003204 | 0.066218 | 0.17536 | 0.069029 | -0.083478 | 0.025342 | 0.059842 | -0.038067 | 0.01056 | 0.040876 | 0.10428 | 0.043687 | 0.1071
1720.2344 | 122.1085 | -121.788 | 0.12817 | 0.11269 | -0.035942 | 0.056679 | 0.007033 | 0.11409 | 0.081005 | -0.026092 | 0.043331 | 0.15248 | 0.046142 | -0.11094 | 0.007032 | 0.032376 | -0.079268 | -0.021484 | 0.14016 | -0.008476 | 0.084145 | 0.034499 | 0.14156 | 0.10847 | 0.001374 | 0.070797 | 0.17994 | 0.073608 | -0.083478 | 0.034498 | 0.059842 | -0.051802 | 0.005982 | 0.036299 | 0.1226 | 0.03911 | 0.12541
1721.9219 | 122.0306 | -121.7972 | 0.13733 | 0.11727 | -0.031363 | 0.065837 | 0.002454 | 0.11409 | 0.085583 | -0.026092 | 0.038752 | 0.14332 | 0.041563 | -0.11094 | 0.002454 | 0.02322 | -0.065533 | -0.012328 | 0.14474 | -0.003897 | 0.093303 | 0.02992 | 0.14156 | 0.11305 | 0.001374 | 0.066218 | 0.17079 | 0.069029 | -0.083478 | 0.02992 | 0.050686 | -0.038067 | 0.015138 | 0.036298 | 0.10428 | 0.039109 | 0.1071
1723.6719 | 121.9345 | -121.8109 | 0.16479 | 0.12185 | -0.022205 | 0.061258 | 0.002454 | 0.10036 | 0.076426 | -0.026092 | 0.047909 | 0.1479 | 0.041563 | -0.097207 | -0.002124 | 0.032376 | -0.079268 | -0.021484 | 0.14932 | 0.005261 | 0.088724 | 0.02992 | 0.12782 | 0.10389 | 0.001374 | 0.075375 | 0.17536 | 0.069029 | -0.069741 | 0.025342 | 0.059842 | -0.051802 | 0.005982 | 0.050033 | 0.12718 | 0.043687 | 0.12083
1725.4219 | 122.0718 | -121.6461 | 0.2243 | 0.11727 | -0.031363 | 0.056679 | 0.002454 | 0.11409 | 0.090161 | -0.021514 | 0.057066 | 0.15248 | 0.046142 | -0.10179 | 0.01161 | 0.036954 | -0.070112 | -0.021484 | 0.14474 | -0.003897 | 0.084145 | 0.02992 | 0.14156 | 0.11763 | 0.005952 | 0.084532 | 0.17994 | 0.073608 | -0.07432 | 0.039076 | 0.06442 | -0.042646 | 0.005982 | 0.045456 | 0.12718 | 0.034532 | 0.11625
1727.0938 | 121.9711 | -121.8475 | 0.14191 | 0.12185 | -0.031363 | 0.065837 | 0.002454 | 0.10951 | 0.081005 | -0.03067 | 0.038752 | 0.1479 | 0.046142 | -0.10637 | 0.039079 | 0.02322 | -0.07469 | -0.012328 | 0.14932 | -0.003897 | 0.093303 | 0.02992 | 0.13698 | 0.10847 | -0.003204 | 0.066218 | 0.17536 | 0.073608 | -0.078899 | 0.066545 | 0.050686 | -0.047224 | 0.015138 | -0.000327 | 0.11344 | 0.007063 | 0.12083
1728.8438 | 121.9757 | -121.8567 | 0.15564 | 0.11727 | -0.026784 | 0.065837 | 0.011611 | 0.10951 | 0.090161 | -0.026092 | 0.038752 | 0.15248 | 0.05072 | -0.10179 | 0.002454 | 0.027798 | -0.070112 | -0.021484 | 0.14474 | 0.000682 | 0.093303 | 0.039077 | 0.13698 | 0.11763 | 0.001374 | 0.066218 | 0.17994 | 0.078186 | -0.07432 | 0.02992 | 0.055264 | -0.042646 | 0.005982 | 0.036298 | 0.10886 | 0.048266 | 0.12083
1730.5938 | 122.0581 | -121.7972 | 0.12817 | 0.11269 | -0.031363 | 0.056679 | 0.007033 | 0.11409 | 0.081005 | -0.021514 | 0.043331 | 0.15248 | 0.05072 | -0.11094 | 0.007032 | 0.032376 | -0.07469 | -0.026063 | 0.14016 | -0.003897 | 0.084145 | 0.034499 | 0.14156 | 0.10847 | 0.005952 | 0.070797 | 0.17994 | 0.078186 | -0.083478 | 0.034498 | 0.059842 | -0.047224 | 0.001403 | 0.036299 | 0.11802 | 0.043688 | 0.12541
1732.2812 | 121.962 | -121.8246 | 0.16022 | 0.11269 | -0.031363 | 0.056679 | -0.002124 | 0.10493 | 0.081005 | -0.03067 | 0.047909 | 0.14332 | 0.05072 | -0.11094 | 0.002454 | 0.027798 | -0.065533 | -0.012328 | 0.14016 | -0.003897 | 0.084145 | 0.025342 | 0.1324 | 0.10847 | -0.003204 | 0.075375 | 0.17079 | 0.078186 | -0.083478 | 0.02992 | 0.055264 | -0.038067 | 0.015138 | 0.045455 | 0.11344 | 0.048266 | 0.11625
1734.0312 | 121.9986 | -121.7834 | 0.18768 | 0.11727 | -0.026784 | 0.056679 | -0.002124 | 0.10951 | 0.081005 | -0.035248 | 0.043331 | 0.1479 | 0.05072 | -0.11094 | 0.002454 | 0.036954 | -0.070112 | -0.016906 | 0.14474 | 0.000682 | 0.084145 | 0.025342 | 0.13698 | 0.10847 | -0.007782 | 0.070797 | 0.17536 | 0.078186 | -0.083478 | 0.02992 | 0.06442 | -0.042646 | 0.01056 | 0.040877 | 0.11344 | 0.048266 | 0.12083
1735.7812 | 122.0581 | -121.7972 | 0.10529 | 0.12185 | -0.026784 | 0.061258 | 0.007033 | 0.10951 | 0.081005 | -0.021514 | 0.038752 | 0.15248 | 0.055298 | -0.11094 | 0.002454 | 0.027798 | -0.060955 | -0.012328 | 0.14932 | 0.000682 | 0.088724 | 0.034499 | 0.13698 | 0.10847 | 0.005952 | 0.066218 | 0.17994 | 0.082764 | -0.083478 | 0.02992 | 0.055264 | -0.033489 | 0.015138 | 0.036298 | 0.099707 | 0.052844 | 0.11625
1737.4531 | 121.9437 | -121.8292 | 0.16937 | 0.11269 | -0.031363 | 0.070415 | 0.007033 | 0.10493 | 0.090161 | -0.03067 | 0.038752 | 0.1479 | 0.041563 | -0.11094 | 0.002454 | 0.036954 | -0.079268 | -0.016906 | 0.14016 | -0.003897 | 0.097881 | 0.034499 | 0.1324 | 0.11763 | -0.003204 | 0.066218 | 0.17536 | 0.069029 | -0.083478 | 0.02992 | 0.06442 | -0.051802 | 0.01056 | 0.036298 | 0.11802 | 0.039109 | 0.12083
1739.2031 | 122.0947 | -121.7606 | 0.11902 | 0.12643 | -0.022205 | 0.061258 | 0.002454 | 0.10951 | 0.085583 | -0.026092 | 0.043331 | 0.1479 | 0.05072 | -0.11094 | 0.002454 | 0.032376 | -0.065533 | -0.012328 | 0.1539 | 0.005261 | 0.088724 | 0.02992 | 0.13698 | 0.11305 | 0.001374 | 0.070797 | 0.17536 | 0.078186 | -0.083478 | 0.02992 | 0.059842 | -0.038067 | 0.015138 | 0.040877 | 0.10886 | 0.048266 | 0.11625
1740.8906 | 121.9757 | -121.8292 | 0.13275 | 0.12185 | -0.031363 | 0.061258 | 0.002454 | 0.10951 | 0.081005 | -0.026092 | 0.034174 | 0.15248 | 0.05072 | -0.11094 | 0.002454 | 0.02322 | -0.07469 | -0.016906 | 0.14932 | -0.003897 | 0.088724 | 0.02992 | 0.13698 | 0.10847 | 0.001374 | 0.06164 | 0.17994 | 0.078186 | -0.083478 | 0.02992 | 0.050686 | -0.047224 | 0.01056 | 0.03172 | 0.10886 | 0.048266 | 0.12541
1742.6406 | 121.9803 | -121.7743 | 0.12817 | 0.11727 | -0.031363 | 0.061258 | 0.002454 | 0.10951 | 0.076426 | -0.03067 | 0.047909 | 0.14332 | 0.055298 | -0.10637 | 0.007032 | 0.02322 | -0.079268 | -0.021484 | 0.14474 | -0.003897 | 0.088724 | 0.02992 | 0.13698 | 0.10389 | -0.003204 | 0.075375 | 0.17079 | 0.082764 | -0.078899 | 0.034498 | 0.050686 | -0.051802 | 0.005982 | 0.040877 | 0.12718 | 0.048266 | 0.13457
1744.3906 | 122.0901 | -121.7834 | 0.10071 | 0.11727 | -0.031363 | 0.061258 | 0.002454 | 0.10493 | 0.085583 | -0.03067 | 0.038752 | 0.1479 | 0.055298 | -0.11552 | 0.002454 | 0.036954 | -0.07469 | -0.016906 | 0.14474 | -0.003897 | 0.088724 | 0.02992 | 0.1324 | 0.11305 | -0.003204 | 0.066218 | 0.17536 | 0.082764 | -0.088057 | 0.02992 | 0.06442 | -0.047224 | 0.01056 | 0.036298 | 0.11344 | 0.052844 | 0.12999
1746.1406 | 121.9803 | -121.788 | 0.14648 | 0.12185 | -0.026784 | 0.065837 | 0.007033 | 0.10036 | 0.081005 | -0.021514 | 0.034174 | 0.15248 | 0.046142 | -0.10637 | 0.007032 | 0.027798 | -0.070112 | -0.012328 | 0.14932 | 0.000682 | 0.093303 | 0.034499 | 0.12782 | 0.10847 | 0.005952 | 0.06164 | 0.17994 | 0.073608 | -0.078899 | 0.034498 | 0.055264 | -0.042646 | 0.015138 | 0.027142 | 0.10429 | 0.03911 | 0.11625
1747.875 | 121.962 | -121.8018 | 0.14648 | 0.11727 | -0.026784 | 0.061258 | 0.007033 | 0.10493 | 0.081005 | -0.026092 | 0.043331 | 0.15248 | 0.055298 | -0.10637 | -0.006702 | 0.027798 | -0.070112 | -0.016906 | 0.14474 | 0.000682 | 0.088724 | 0.034499 | 0.1324 | 0.10847 | 0.001374 | 0.070797 | 0.17994 | 0.082764 | -0.078899 | 0.020764 | 0.055264 | -0.042646 | 0.01056 | 0.050033 | 0.11344 | 0.062 | 0.12541
1749.5469 | 122.0627 | -121.5363 | 0.32501 | 0.11727 | -0.031363 | 0.056679 | -0.006703 | 0.10493 | 0.076426 | -0.03067 | 0.043331 | 0.14332 | 0.059877 | -0.11552 | -0.002124 | 0.032376 | -0.07469 | -0.012328 | 0.14474 | -0.003897 | 0.084145 | 0.020763 | 0.1324 | 0.10389 | -0.003204 | 0.070797 | 0.17079 | 0.087343 | -0.088057 | 0.025342 | 0.059842 | -0.047224 | 0.015138 | 0.045455 | 0.11802 | 0.062001 | 0.13457
1751.2344 | 122.0169 | -121.7789 | 0.14191 | 0.11727 | -0.035942 | 0.056679 | 0.002454 | 0.11409 | 0.081005 | -0.021514 | 0.043331 | 0.1479 | 0.041563 | -0.11552 | -0.002124 | 0.032376 | -0.07469 | -0.016906 | 0.14474 | -0.008476 | 0.084145 | 0.02992 | 0.14156 | 0.10847 | 0.005952 | 0.070797 | 0.17536 | 0.069029 | -0.088057 | 0.025342 | 0.059842 | -0.047224 | 0.01056 | 0.045455 | 0.11802 | 0.043687 | 0.11625
1752.9844 | 122.0169 | -121.7651 | 0.13275 | 0.11727 | -0.031363 | 0.065837 | -0.002124 | 0.11409 | 0.085583 | -0.026092 | 0.038752 | 0.1479 | 0.036985 | -0.10637 | 0.01161 | 0.032376 | -0.07469 | -0.021484 | 0.14474 | -0.003897 | 0.093303 | 0.025342 | 0.14156 | 0.11305 | 0.001374 | 0.066218 | 0.17536 | 0.064451 | -0.078899 | 0.039076 | 0.059842 | -0.047224 | 0.005982 | 0.027142 | 0.11344 | 0.025375 | 0.11167
1754.6719 | 122.0764 | -121.7697 | 0.13275 | 0.12185 | -0.040521 | 0.061258 | 0.002454 | 0.10493 | 0.081005 | -0.026092 | 0.034174 | 0.15248 | 0.055298 | -0.11094 | 0.002454 | 0.027798 | -0.070112 | -0.016906 | 0.14932 | -0.013055 | 0.088724 | 0.02992 | 0.1324 | 0.10847 | 0.001374 | 0.06164 | 0.17994 | 0.082764 | -0.083478 | 0.02992 | 0.055264 | -0.042646 | 0.01056 | 0.03172 | 0.10429 | 0.052844 | 0.12541
1756.4219 | 122.049 | -121.7606 | 0.10529 | 0.11727 | -0.026784 | 0.061258 | 0.002454 | 0.10493 | 0.081005 | -0.035248 | 0.047909 | 0.15248 | 0.046142 | -0.11094 | -0.002124 | 0.027798 | -0.07469 | -0.021484 | 0.14474 | 0.000682 | 0.088724 | 0.02992 | 0.1324 | 0.10847 | -0.007782 | 0.075375 | 0.17994 | 0.073608 | -0.083478 | 0.025342 | 0.055264 | -0.047224 | 0.005982 | 0.050033 | 0.1226 | 0.048266 | 0.12083
1758.1719 | 121.994 | -121.8063 | 0.14191 | 0.11727 | -0.031363 | 0.061258 | 0.002454 | 0.11409 | 0.081005 | -0.021514 | 0.038752 | 0.1479 | 0.05072 | -0.10179 | 0.007032 | 0.027798 | -0.070112 | -0.016906 | 0.14474 | -0.003897 | 0.088724 | 0.02992 | 0.14156 | 0.10847 | 0.005952 | 0.066218 | 0.17536 | 0.078186 | -0.07432 | 0.034498 | 0.055264 | -0.042646 | 0.01056 | 0.03172 | 0.10886 | 0.043688 | 0.12083
1759.8438 | 122.0764 | -121.7651 | 0.11444 | 0.11269 | -0.026784 | 0.061258 | 0.002454 | 0.11409 | 0.081005 | -0.03067 | 0.038752 | 0.1479 | 0.041563 | -0.10637 | 0.007032 | 0.032376 | -0.070112 | -0.012328 | 0.14016 | 0.000682 | 0.088724 | 0.02992 | 0.14156 | 0.10847 | -0.003204 | 0.066218 | 0.17536 | 0.069029 | -0.078899 | 0.034498 | 0.059842 | -0.042646 | 0.015138 | 0.03172 | 0.10886 | 0.034531 | 0.11167
1761.5938 | 122.1039 | -121.8704 | 0.10529 | 0.11727 | -0.040521 | 0.061258 | 0.011611 | 0.10493 | 0.076426 | -0.035248 | 0.038752 | 0.14332 | 0.046142 | -0.11094 | 0.002454 | 0.02322 | -0.070112 | -0.012328 | 0.14474 | -0.013055 | 0.088724 | 0.039077 | 0.1324 | 0.10389 | -0.007782 | 0.066218 | 0.17079 | 0.073608 | -0.083478 | 0.02992 | 0.050686 | -0.042646 | 0.015138 | 0.036298 | 0.10886 | 0.043688 | 0.11625
1763.3438 | 122.081 | -121.8979 | 0.10071 | 0.12185 | -0.026784 | 0.056679 | 0.002454 | 0.10036 | 0.076426 | -0.03067 | 0.034174 | 0.15248 | 0.032407 | -0.11094 | 0.007032 | 0.036954 | -0.07469 | -0.012328 | 0.14932 | 0.000682 | 0.084145 | 0.02992 | 0.12782 | 0.10389 | -0.003204 | 0.06164 | 0.17994 | 0.059873 | -0.083478 | 0.034498 | 0.06442 | -0.047224 | 0.015138 | 0.027142 | 0.10886 | 0.025375 | 0.1071
1765.0312 | 122.0581 | -121.8887 | 0.1236 | 0.11269 | -0.031363 | 0.061258 | 0.002454 | 0.10951 | 0.076426 | -0.026092 | 0.034174 | 0.1479 | 0.055298 | -0.11094 | 0.007032 | 0.036954 | -0.060955 | -0.012328 | 0.14016 | -0.003897 | 0.088724 | 0.02992 | 0.13698 | 0.10389 | 0.001374 | 0.06164 | 0.17536 | 0.082764 | -0.083478 | 0.034498 | 0.06442 | -0.033489 | 0.015138 | 0.027142 | 0.095129 | 0.048266 | 0.11625
1766.7812 | 122.1634 | -121.8704 | 0.10071 | 0.11269 | -0.031363 | 0.056679 | 0.007033 | 0.10493 | 0.071848 | -0.03067 | 0.038752 | 0.14332 | 0.046142 | -0.10637 | 0.007032 | 0.032376 | -0.070112 | -0.016906 | 0.14016 | -0.003897 | 0.084145 | 0.034499 | 0.1324 | 0.099314 | -0.003204 | 0.066218 | 0.17079 | 0.073608 | -0.078899 | 0.034498 | 0.059842 | -0.042646 | 0.01056 | 0.03172 | 0.10886 | 0.03911 | 0.11625
1768.5156 | 122.0901 | -121.9299 | 0.13733 | 0.11269 | -0.035942 | 0.061258 | -0.002124 | 0.10493 | 0.081005 | -0.03067 | 0.038752 | 0.1479 | 0.041563 | -0.10637 | 0.007032 | 0.027798 | -0.070112 | -0.016906 | 0.14016 | -0.008476 | 0.088724 | 0.025342 | 0.1324 | 0.10847 | -0.003204 | 0.066218 | 0.17536 | 0.069029 | -0.078899 | 0.034498 | 0.055264 | -0.042646 | 0.01056 | 0.03172 | 0.10886 | 0.034531 | 0.11167
1770.1875 | 122.1268 | -121.8979 | 0.10071 | 0.12185 | -0.031363 | 0.061258 | -0.002124 | 0.10951 | 0.081005 | -0.021514 | 0.043331 | 0.1479 | 0.05072 | -0.11094 | 0.007032 | 0.032376 | -0.070112 | -0.00775 | 0.14932 | -0.003897 | 0.088724 | 0.025342 | 0.13698 | 0.10847 | 0.005952 | 0.070797 | 0.17536 | 0.078186 | -0.083478 | 0.034498 | 0.059842 | -0.042646 | 0.019716 | 0.036299 | 0.11344 | 0.043688 | 0.12083
1771.9219 | 122.1222 | -121.9254 | 0.10529 | 0.11727 | -0.035942 | 0.061258 | 0.002454 | 0.10951 | 0.071848 | -0.026092 | 0.034174 | 0.1479 | 0.041563 | -0.11552 | 0.007032 | 0.032376 | -0.065533 | -0.012328 | 0.14474 | -0.008476 | 0.088724 | 0.02992 | 0.13698 | 0.099314 | 0.001374 | 0.06164 | 0.17536 | 0.069029 | -0.088057 | 0.034498 | 0.059842 | -0.038067 | 0.015138 | 0.027142 | 0.099707 | 0.034531 | 0.1071
1773.6094 | 122.0993 | -121.9391 | 0.11444 | 0.11269 | -0.031363 | 0.061258 | -0.002124 | 0.10036 | 0.071848 | -0.03067 | 0.029595 | 0.14332 | 0.041563 | -0.10637 | 0.01161 | 0.036954 | -0.065533 | -0.016906 | 0.14016 | -0.003897 | 0.088724 | 0.025342 | 0.12782 | 0.099314 | -0.003204 | 0.057061 | 0.17079 | 0.069029 | -0.078899 | 0.039076 | 0.06442 | -0.038067 | 0.01056 | 0.017985 | 0.095128 | 0.029953 | 0.1071
1775.3438 | 122.1725 | -121.9162 | 0.10071 | 0.11727 | -0.031363 | 0.056679 | 0.002454 | 0.10493 | 0.071848 | -0.021514 | 0.034174 | 0.14332 | 0.032407 | -0.10179 | 0.002454 | 0.036954 | -0.070112 | -0.012328 | 0.14474 | -0.003897 | 0.084145 | 0.02992 | 0.1324 | 0.099314 | 0.005952 | 0.06164 | 0.17079 | 0.059873 | -0.07432 | 0.02992 | 0.06442 | -0.042646 | 0.015138 | 0.03172 | 0.10429 | 0.029953 | 0.10252
1777.0781 | 122.1863 | -121.9162 | 0.086975 | 0.11269 | -0.035942 | 0.056679 | 0.002454 | 0.10493 | 0.076426 | -0.026092 | 0.025017 | 0.15248 | 0.036985 | -0.10637 | 0.01161 | 0.036954 | -0.065533 | -0.012328 | 0.14016 | -0.008476 | 0.084145 | 0.02992 | 0.1324 | 0.10389 | 0.001374 | 0.052483 | 0.17994 | 0.064451 | -0.078899 | 0.039076 | 0.06442 | -0.038067 | 0.015138 | 0.013407 | 0.09055 | 0.025375 | 0.10252
1778.7656 | 122.1634 | -121.9437 | 0.11444 | 0.11269 | -0.035942 | 0.052101 | -0.002124 | 0.10493 | 0.081005 | -0.03067 | 0.034174 | 0.14332 | 0.041563 | -0.11094 | 0.007032 | 0.032376 | -0.065533 | -0.016906 | 0.14016 | -0.008476 | 0.079567 | 0.025342 | 0.1324 | 0.10847 | -0.003204 | 0.06164 | 0.17079 | 0.069029 | -0.083478 | 0.034498 | 0.059842 | -0.038067 | 0.01056 | 0.027142 | 0.099707 | 0.034531 | 0.1071
1780.5156 | 122.2366 | -121.9025 | 0.10071 | 0.11727 | -0.031363 | 0.061258 | -0.006703 | 0.10036 | 0.081005 | -0.03067 | 0.034174 | 0.14332 | 0.036985 | -0.11094 | 0.007032 | 0.041532 | -0.056376 | -0.026063 | 0.14474 | -0.003897 | 0.088724 | 0.020763 | 0.12782 | 0.10847 | -0.003204 | 0.06164 | 0.17079 | 0.064451 | -0.083478 | 0.034498 | 0.068998 | -0.02891 | 0.001403 | 0.027142 | 0.09055 | 0.029953 | 0.093361
1782.25 | 122.287 | -121.9345 | 0.07782 | 0.10812 | -0.035942 | 0.056679 | 0.002454 | 0.10036 | 0.076426 | -0.03067 | 0.029595 | 0.1479 | 0.032407 | -0.10637 | -0.002124 | 0.036954 | -0.070112 | -0.021484 | 0.13558 | -0.008476 | 0.084145 | 0.02992 | 0.12782 | 0.10389 | -0.003204 | 0.057061 | 0.17536 | 0.059873 | -0.078899 | 0.025342 | 0.06442 | -0.042646 | 0.005982 | 0.031719 | 0.099707 | 0.034531 | 0.10252
1783.9219 | 122.2412 | -121.9025 | 0.082397 | 0.10812 | -0.031363 | 0.061258 | 0.002454 | 0.10036 | 0.076426 | -0.026092 | 0.043331 | 0.15248 | 0.041563 | -0.11094 | 0.002454 | 0.032376 | -0.065533 | -0.016906 | 0.13558 | -0.003897 | 0.088724 | 0.02992 | 0.12782 | 0.10389 | 0.001374 | 0.070797 | 0.17994 | 0.069029 | -0.083478 | 0.02992 | 0.059842 | -0.038067 | 0.01056 | 0.040877 | 0.10886 | 0.039109 | 0.1071
1785.6719 | 122.2229 | -121.9254 | 0.09613 | 0.11269 | -0.031363 | 0.056679 | 0.002454 | 0.10493 | 0.071848 | -0.039826 | 0.029595 | 0.14332 | 0.046142 | -0.10637 | 0.002454 | 0.027798 | -0.065533 | -0.016906 | 0.14016 | -0.003897 | 0.084145 | 0.02992 | 0.1324 | 0.099314 | -0.01236 | 0.057061 | 0.17079 | 0.073608 | -0.078899 | 0.02992 | 0.055264 | -0.038067 | 0.01056 | 0.027141 | 0.095128 | 0.043688 | 0.11167
1787.4219 | 122.1542 | -122.0032 | 0.11444 | 0.10812 | -0.026784 | 0.061258 | -0.002124 | 0.11409 | 0.085583 | -0.026092 | 0.038752 | 0.1479 | 0.046142 | -0.11094 | 0.002454 | 0.050688 | -0.07469 | -0.012328 | 0.13558 | 0.000682 | 0.088724 | 0.025342 | 0.14156 | 0.11305 | 0.001374 | 0.066218 | 0.17536 | 0.073608 | -0.083478 | 0.02992 | 0.078154 | -0.047224 | 0.015138 | 0.036298 | 0.11344 | 0.043688 | 0.12083
1789.1094 | 122.2092 | -121.9528 | 0.11444 | 0.11727 | -0.031363 | 0.056679 | 0.002454 | 0.10493 | 0.076426 | -0.039826 | 0.034174 | 0.15248 | 0.046142 | -0.11552 | 0.007032 | 0.036954 | -0.065533 | -0.012328 | 0.14474 | -0.003897 | 0.084145 | 0.02992 | 0.1324 | 0.10389 | -0.01236 | 0.06164 | 0.17994 | 0.073608 | -0.088057 | 0.034498 | 0.06442 | -0.038067 | 0.015138 | 0.027142 | 0.099707 | 0.03911 | 0.11167
1790.875 | 122.1817 | -121.962 | 0.1236 | 0.11269 | -0.035942 | 0.056679 | -0.006703 | 0.10951 | 0.085583 | -0.03067 | 0.034174 | 0.1479 | 0.041563 | -0.11094 | 0.007032 | 0.027798 | -0.065533 | -0.016906 | 0.14016 | -0.008476 | 0.084145 | 0.020763 | 0.13698 | 0.11305 | -0.003204 | 0.06164 | 0.17536 | 0.069029 | -0.083478 | 0.034498 | 0.055264 | -0.038067 | 0.01056 | 0.027142 | 0.099707 | 0.034531 | 0.1071
1792.6094 | 122.2366 | -121.962 | 0.086975 | 0.11727 | -0.035942 | 0.061258 | -0.002124 | 0.10036 | 0.076426 | -0.03067 | 0.038752 | 0.1479 | 0.032407 | -0.11094 | 0.002454 | 0.041532 | -0.065533 | -0.012328 | 0.14474 | -0.008476 | 0.088724 | 0.025342 | 0.12782 | 0.10389 | -0.003204 | 0.066218 | 0.17536 | 0.059873 | -0.083478 | 0.02992 | 0.068998 | -0.038067 | 0.015138 | 0.036298 | 0.10428 | 0.029953 | 0.09794
1794.2969 | 122.1863 | -121.9894 | 0.10529 | 0.10812 | -0.026784 | 0.056679 | 0.002454 | 0.10951 | 0.085583 | -0.021514 | 0.038752 | 0.1479 | 0.032407 | -0.11094 | 0.002454 | 0.032376 | -0.070112 | -0.016906 | 0.13558 | 0.000682 | 0.084145 | 0.02992 | 0.13698 | 0.11305 | 0.005952 | 0.066218 | 0.17536 | 0.059873 | -0.083478 | 0.02992 | 0.059842 | -0.042646 | 0.01056 | 0.036298 | 0.10886 | 0.029953 | 0.10252
1796.0469 | 122.1542 | -121.9803 | 0.13275 | 0.11269 | -0.031363 | 0.042944 | 0.002454 | 0.10493 | 0.085583 | -0.035248 | 0.029595 | 0.14332 | 0.041563 | -0.11552 | 0.002454 | 0.041532 | -0.065533 | -0.026063 | 0.14016 | -0.003897 | 0.07041 | 0.02992 | 0.1324 | 0.11305 | -0.007782 | 0.057061 | 0.17079 | 0.069029 | -0.088057 | 0.02992 | 0.068998 | -0.038067 | 0.001403 | 0.027141 | 0.095128 | 0.039109 | 0.1071
1797.7344 | 122.2916 | -121.962 | 0.086975 | 0.10812 | -0.035942 | 0.056679 | 0.007033 | 0.11409 | 0.076426 | -0.035248 | 0.034174 | 0.1479 | 0.032407 | -0.11552 | 0.007032 | 0.036954 | -0.070112 | -0.012328 | 0.13558 | -0.008476 | 0.084145 | 0.034499 | 0.14156 | 0.10389 | -0.007782 | 0.06164 | 0.17536 | 0.059873 | -0.088057 | 0.034498 | 0.06442 | -0.042646 | 0.015138 | 0.027142 | 0.10429 | 0.025375 | 0.10252
1799.4844 | 122.1634 | -121.9757 | 0.1236 | 0.11727 | -0.026784 | 0.052101 | 0.002454 | 0.10951 | 0.081005 | -0.021514 | 0.034174 | 0.14332 | 0.041563 | -0.10179 | 0.002454 | 0.036954 | -0.065533 | -0.016906 | 0.14474 | 0.000682 | 0.079567 | 0.02992 | 0.13698 | 0.10847 | 0.005952 | 0.06164 | 0.17079 | 0.069029 | -0.07432 | 0.02992 | 0.06442 | -0.038067 | 0.01056 | 0.03172 | 0.099707 | 0.039109 | 0.1071
1801.1562 | 122.3007 | -121.9574 | 0.07782 | 0.11269 | -0.035942 | 0.052101 | 0.002454 | 0.095778 | 0.076426 | -0.03067 | 0.034174 | 0.14332 | 0.05072 | -0.11094 | 0.002454 | 0.027798 | -0.065533 | -0.021484 | 0.14016 | -0.008476 | 0.079567 | 0.02992 | 0.12324 | 0.10389 | -0.003204 | 0.06164 | 0.17079 | 0.078186 | -0.083478 | 0.02992 | 0.055264 | -0.038067 | 0.005982 | 0.03172 | 0.099707 | 0.048266 | 0.11625
1802.9062 | 122.3099 | -121.9666 | 0.10071 | 0.11269 | -0.026784 | 0.061258 | 0.002454 | 0.10951 | 0.081005 | -0.035248 | 0.043331 | 0.15248 | 0.036985 | -0.10637 | 0.007032 | 0.032376 | -0.060955 | -0.012328 | 0.14016 | 0.000682 | 0.088724 | 0.02992 | 0.13698 | 0.10847 | -0.007782 | 0.070797 | 0.17994 | 0.064451 | -0.078899 | 0.034498 | 0.059842 | -0.033489 | 0.015138 | 0.036299 | 0.10429 | 0.029953 | 0.09794
1804.5938 | 122.1863 | -121.9849 | 0.1236 | 0.11269 | -0.031363 | 0.056679 | 0.002454 | 0.10493 | 0.085583 | -0.03067 | 0.043331 | 0.1479 | 0.05072 | -0.11094 | 0.002454 | 0.032376 | -0.070112 | -0.016906 | 0.14016 | -0.003897 | 0.084145 | 0.02992 | 0.1324 | 0.11305 | -0.003204 | 0.070797 | 0.17536 | 0.078186 | -0.083478 | 0.02992 | 0.059842 | -0.042646 | 0.01056 | 0.040877 | 0.11344 | 0.048266 | 0.12083
1806.3438 | 122.1451 | -122.0261 | 0.12817 | 0.11269 | -0.031363 | 0.061258 | -0.002124 | 0.10493 | 0.081005 | -0.03067 | 0.043331 | 0.14332 | 0.036985 | -0.11552 | 0.002454 | 0.041532 | -0.065533 | -0.016906 | 0.14016 | -0.003897 | 0.088724 | 0.025342 | 0.1324 | 0.10847 | -0.003204 | 0.070797 | 0.17079 | 0.064451 | -0.088057 | 0.02992 | 0.068998 | -0.038067 | 0.01056 | 0.040877 | 0.10886 | 0.034531 | 0.10252
1808.0938 | 122.168 | -122.0261 | 0.11444 | 0.11269 | -0.026784 | 0.052101 | 0.002454 | 0.10951 | 0.076426 | -0.03067 | 0.043331 | 0.1479 | 0.036985 | -0.11094 | 0.002454 | 0.027798 | -0.065533 | -0.016906 | 0.14016 | 0.000682 | 0.079567 | 0.02992 | 0.13698 | 0.10389 | -0.003204 | 0.070797 | 0.17536 | 0.064451 | -0.083478 | 0.02992 | 0.055264 | -0.038067 | 0.01056 | 0.040877 | 0.10886 | 0.034531 | 0.10252
1809.8438 | 122.2824 | -122.0078 | 0.10071 | 0.11269 | -0.031363 | 0.056679 | 0.007033 | 0.10951 | 0.085583 | -0.026092 | 0.038752 | 0.1479 | 0.032407 | -0.10637 | 0.007032 | 0.032376 | -0.065533 | -0.016906 | 0.14016 | -0.003897 | 0.084145 | 0.034499 | 0.13698 | 0.11305 | 0.001374 | 0.066218 | 0.17536 | 0.059873 | -0.078899 | 0.034498 | 0.059842 | -0.038067 | 0.01056 | 0.03172 | 0.10428 | 0.025375 | 0.09794
1811.5781 | 122.1909 | -122.0718 | 0.11444 | 0.11269 | -0.040521 | 0.052101 | -0.002124 | 0.10036 | 0.071848 | -0.03067 | 0.038752 | 0.15248 | 0.05072 | -0.11094 | 0.002454 | 0.041532 | -0.07469 | -0.012328 | 0.14016 | -0.013055 | 0.079567 | 0.025342 | 0.12782 | 0.099314 | -0.003204 | 0.066218 | 0.17994 | 0.078186 | -0.083478 | 0.02992 | 0.068998 | -0.047224 | 0.015138 | 0.036298 | 0.11344 | 0.048266 | 0.12541
1813.2656 | 122.319 | -121.9849 | 0.07782 | 0.10812 | -0.031363 | 0.061258 | 0.007033 | 0.10951 | 0.076426 | -0.026092 | 0.038752 | 0.1479 | 0.032407 | -0.10637 | 0.002454 | 0.032376 | -0.065533 | -0.016906 | 0.13558 | -0.003897 | 0.088724 | 0.034499 | 0.13698 | 0.10389 | 0.001374 | 0.066218 | 0.17536 | 0.059873 | -0.078899 | 0.02992 | 0.059842 | -0.038067 | 0.01056 | 0.036298 | 0.10428 | 0.029953 | 0.09794
1815.0156 | 122.3145 | -121.9757 | 0.10071 | 0.11727 | -0.031363 | 0.042944 | -0.002124 | 0.10493 | 0.076426 | -0.026092 | 0.034174 | 0.1479 | 0.032407 | -0.097207 | 0.007032 | 0.032376 | -0.065533 | -0.012328 | 0.14474 | -0.003897 | 0.07041 | 0.025342 | 0.1324 | 0.10389 | 0.001374 | 0.06164 | 0.17536 | 0.059873 | -0.069741 | 0.034498 | 0.059842 | -0.038067 | 0.015138 | 0.027142 | 0.099707 | 0.025375 | 0.09794
1816.7031 | 122.287 | -122.0352 | 0.086975 | 0.11269 | -0.035942 | 0.056679 | 0.007033 | 0.10951 | 0.076426 | -0.03067 | 0.034174 | 0.14332 | 0.036985 | -0.10637 | 0.007032 | 0.036954 | -0.065533 | -0.016906 | 0.14016 | -0.008476 | 0.084145 | 0.034499 | 0.13698 | 0.10389 | -0.003204 | 0.06164 | 0.17079 | 0.064451 | -0.078899 | 0.034498 | 0.06442 | -0.038067 | 0.01056 | 0.027142 | 0.099707 | 0.029953 | 0.10252
1818.4531 | 122.2137 | -122.049 | 0.10986 | 0.10812 | -0.035942 | 0.056679 | 0.002454 | 0.10036 | 0.076426 | -0.026092 | 0.034174 | 0.14332 | 0.046142 | -0.11094 | 0.002454 | 0.036954 | -0.070112 | -0.003172 | 0.13558 | -0.008476 | 0.084145 | 0.02992 | 0.12782 | 0.10389 | 0.001374 | 0.06164 | 0.17079 | 0.073608 | -0.083478 | 0.02992 | 0.06442 | -0.042646 | 0.024294 | 0.03172 | 0.10429 | 0.043688 | 0.11625
1820.1406 | 122.2229 | -122.0673 | 0.12817 | 0.11269 | -0.035942 | 0.061258 | 0.002454 | 0.10493 | 0.081005 | -0.03067 | 0.038752 | 0.15248 | 0.041563 | -0.10637 | 0.002454 | 0.032376 | -0.065533 | -0.016906 | 0.14016 | -0.008476 | 0.088724 | 0.02992 | 0.1324 | 0.10847 | -0.003204 | 0.066218 | 0.17994 | 0.069029 | -0.078899 | 0.02992 | 0.059842 | -0.038067 | 0.01056 | 0.036298 | 0.10428 | 0.039109 | 0.1071
1821.8906 | 122.3328 | -122.0032 | 0.082397 | 0.11269 | -0.031363 | 0.052101 | 0.002454 | 0.10951 | 0.076426 | -0.039826 | 0.034174 | 0.15706 | 0.046142 | -0.10637 | 0.002454 | 0.036954 | -0.060955 | -0.021484 | 0.14016 | -0.003897 | 0.079567 | 0.02992 | 0.13698 | 0.10389 | -0.01236 | 0.06164 | 0.18452 | 0.073608 | -0.078899 | 0.02992 | 0.06442 | -0.033489 | 0.005982 | 0.03172 | 0.095129 | 0.043688 | 0.1071
1823.6406 | 122.2137 | -122.0947 | 0.11902 | 0.10812 | -0.026784 | 0.056679 | 0.002454 | 0.10493 | 0.081005 | -0.026092 | 0.034174 | 0.15248 | 0.041563 | -0.11552 | 0.01161 | 0.032376 | -0.065533 | -0.012328 | 0.13558 | 0.000682 | 0.084145 | 0.02992 | 0.1324 | 0.10847 | 0.001374 | 0.06164 | 0.17994 | 0.069029 | -0.088057 | 0.039076 | 0.059842 | -0.038067 | 0.015138 | 0.022564 | 0.099707 | 0.029953 | 0.1071
1825.3906 | 122.2961 | -122.0352 | 0.09613 | 0.11269 | -0.031363 | 0.065837 | -0.002124 | 0.11409 | 0.081005 | -0.03067 | 0.038752 | 0.14332 | 0.046142 | -0.11094 | 0.002454 | 0.036954 | -0.070112 | -0.016906 | 0.14016 | -0.003897 | 0.093303 | 0.025342 | 0.14156 | 0.10847 | -0.003204 | 0.066218 | 0.17079 | 0.073608 | -0.083478 | 0.02992 | 0.06442 | -0.042646 | 0.01056 | 0.036298 | 0.10886 | 0.043688 | 0.11625
1827.125 | 122.2824 | -122.0627 | 0.10986 | 0.10812 | -0.040521 | 0.065837 | -0.002124 | 0.10951 | 0.085583 | -0.035248 | 0.038752 | 0.14332 | 0.036985 | -0.10637 | 0.002454 | 0.036954 | -0.065533 | -0.026063 | 0.13558 | -0.013055 | 0.093303 | 0.025342 | 0.13698 | 0.11305 | -0.007782 | 0.066218 | 0.17079 | 0.064451 | -0.078899 | 0.02992 | 0.06442 | -0.038067 | 0.001403 | 0.036298 | 0.10428 | 0.034531 | 0.10252
1828.8594 | 122.2458 | -122.0764 | 0.10986 | 0.11269 | -0.026784 | 0.061258 | -0.002124 | 0.10493 | 0.076426 | -0.03067 | 0.038752 | 0.15706 | 0.036985 | -0.11094 | 0.002454 | 0.041532 | -0.070112 | -0.012328 | 0.14016 | 0.000682 | 0.088724 | 0.025342 | 0.1324 | 0.10389 | -0.003204 | 0.066218 | 0.18452 | 0.064451 | -0.083478 | 0.02992 | 0.068998 | -0.042646 | 0.015138 | 0.036298 | 0.10886 | 0.034531 | 0.1071
1830.5469 | 122.2458 | -122.0718 | 0.10529 | 0.12185 | -0.031363 | 0.056679 | 0.007033 | 0.11409 | 0.081005 | -0.026092 | 0.038752 | 0.14332 | 0.036985 | -0.11552 | 0.002454 | 0.036954 | -0.070112 | -0.012328 | 0.14932 | -0.003897 | 0.084145 | 0.034499 | 0.14156 | 0.10847 | 0.001374 | 0.066218 | 0.17079 | 0.064451 | -0.088057 | 0.02992 | 0.06442 | -0.042646 | 0.015138 | 0.036298 | 0.10886 | 0.034531 | 0.1071
1832.2812 | 122.2641 | -122.0856 | 0.10529 | 0.11269 | -0.022205 | 0.052101 | -0.002124 | 0.10951 | 0.076426 | -0.03067 | 0.043331 | 0.1479 | 0.046142 | -0.10179 | 0.007032 | 0.036954 | -0.060955 | -0.016906 | 0.14016 | 0.005261 | 0.079567 | 0.025342 | 0.13698 | 0.10389 | -0.003204 | 0.070797 | 0.17536 | 0.073608 | -0.07432 | 0.034498 | 0.06442 | -0.033489 | 0.01056 | 0.036299 | 0.10429 | 0.03911 | 0.1071
1834.0312 | 122.2961 | -122.0581 | 0.10986 | 0.11269 | -0.022205 | 0.056679 | 0.002454 | 0.10951 | 0.076426 | -0.026092 | 0.038752 | 0.14332 | 0.041563 | -0.11094 | 0.007032 | 0.032376 | -0.065533 | -0.016906 | 0.14016 | 0.005261 | 0.084145 | 0.02992 | 0.13698 | 0.10389 | 0.001374 | 0.066218 | 0.17079 | 0.069029 | -0.083478 | 0.034498 | 0.059842 | -0.038067 | 0.01056 | 0.03172 | 0.10428 | 0.034531 | 0.1071
1835.7188 | 122.2321 | -122.0993 | 0.15106 | 0.11269 | -0.031363 | 0.052101 | 0.002454 | 0.10036 | 0.076426 | -0.026092 | 0.034174 | 0.14332 | 0.05072 | -0.11094 | -0.002124 | 0.036954 | -0.07469 | -0.016906 | 0.14016 | -0.003897 | 0.079567 | 0.02992 | 0.12782 | 0.10389 | 0.001374 | 0.06164 | 0.17079 | 0.078186 | -0.083478 | 0.025342 | 0.06442 | -0.047224 | 0.01056 | 0.036298 | 0.10886 | 0.052844 | 0.12541
1837.4688 | 122.2458 | -122.0993 | 0.1236 | 0.11727 | -0.031363 | 0.061258 | 0.002454 | 0.10493 | 0.076426 | -0.026092 | 0.038752 | 0.14332 | 0.032407 | -0.11552 | 0.007032 | 0.027798 | -0.070112 | -0.012328 | 0.14474 | -0.003897 | 0.088724 | 0.02992 | 0.1324 | 0.10389 | 0.001374 | 0.066218 | 0.17079 | 0.059873 | -0.088057 | 0.034498 | 0.055264 | -0.042646 | 0.015138 | 0.03172 | 0.10886 | 0.025375 | 0.10252
1839.1562 | 122.2412 | -122.0947 | 0.13275 | 0.10812 | -0.031363 | 0.061258 | -0.002124 | 0.10036 | 0.081005 | -0.03067 | 0.038752 | 0.1479 | 0.046142 | -0.11094 | 0.002454 | 0.032376 | -0.070112 | -0.012328 | 0.13558 | -0.003897 | 0.088724 | 0.025342 | 0.12782 | 0.10847 | -0.003204 | 0.066218 | 0.17536 | 0.073608 | -0.083478 | 0.02992 | 0.059842 | -0.042646 | 0.015138 | 0.036298 | 0.10886 | 0.043688 | 0.11625
1840.9219 | 122.3465 | -122.0718 | 0.086975 | 0.11727 | -0.040521 | 0.065837 | -0.002124 | 0.10493 | 0.081005 | -0.03067 | 0.025017 | 0.15248 | 0.041563 | -0.10637 | 0.01161 | 0.041532 | -0.065533 | -0.012328 | 0.14474 | -0.013055 | 0.093303 | 0.025342 | 0.1324 | 0.10847 | -0.003204 | 0.052483 | 0.17994 | 0.069029 | -0.078899 | 0.039076 | 0.068998 | -0.038067 | 0.015138 | 0.013407 | 0.09055 | 0.029953 | 0.1071
1842.6562 | 122.3099 | -122.0993 | 0.10986 | 0.12185 | -0.035942 | 0.056679 | 0.007033 | 0.10493 | 0.085583 | -0.03067 | 0.034174 | 0.13874 | 0.059877 | -0.11094 | 0.002454 | 0.041532 | -0.060955 | -0.012328 | 0.14932 | -0.008476 | 0.084145 | 0.034499 | 0.1324 | 0.11305 | -0.003204 | 0.06164 | 0.16621 | 0.087343 | -0.083478 | 0.02992 | 0.068998 | -0.033489 | 0.015138 | 0.03172 | 0.095129 | 0.057423 | 0.12083
1844.4062 | 122.374 | -122.081 | 0.086975 | 0.11269 | -0.035942 | 0.052101 | -0.002124 | 0.10036 | 0.081005 | -0.026092 | 0.029595 | 0.13874 | 0.041563 | -0.10637 | -0.002124 | 0.036954 | -0.070112 | -0.00775 | 0.14016 | -0.008476 | 0.079567 | 0.025342 | 0.12782 | 0.10847 | 0.001374 | 0.057061 | 0.16621 | 0.069029 | -0.078899 | 0.025342 | 0.06442 | -0.042646 | 0.019716 | 0.031719 | 0.099707 | 0.043687 | 0.11167
1846.0781 | 122.2321 | -122.1085 | 0.13275 | 0.10812 | -0.031363 | 0.056679 | 0.007033 | 0.10493 | 0.081005 | -0.026092 | 0.043331 | 0.15248 | 0.027829 | -0.11552 | 0.002454 | 0.032376 | -0.060955 | -0.016906 | 0.13558 | -0.003897 | 0.084145 | 0.034499 | 0.1324 | 0.10847 | 0.001374 | 0.070797 | 0.17994 | 0.055295 | -0.088057 | 0.02992 | 0.059842 | -0.033489 | 0.01056 | 0.040877 | 0.10429 | 0.025375 | 0.088784
1847.8125 | 122.2687 | -122.1085 | 0.11902 | 0.10812 | -0.026784 | 0.061258 | -0.002124 | 0.10493 | 0.076426 | -0.03067 | 0.038752 | 0.15248 | 0.027829 | -0.10179 | 0.007032 | 0.027798 | -0.07469 | -0.012328 | 0.13558 | 0.000682 | 0.088724 | 0.025342 | 0.1324 | 0.10389 | -0.003204 | 0.066218 | 0.17994 | 0.055295 | -0.07432 | 0.034498 | 0.055264 | -0.047224 | 0.015138 | 0.03172 | 0.11344 | 0.020797 | 0.10252
1849.5625 | 122.3785 | -122.0627 | 0.09613 | 0.10812 | -0.031363 | 0.061258 | 0.007033 | 0.10951 | 0.081005 | -0.021514 | 0.034174 | 0.14332 | 0.046142 | -0.11094 | 0.002454 | 0.036954 | -0.060955 | -0.016906 | 0.13558 | -0.003897 | 0.088724 | 0.034499 | 0.13698 | 0.10847 | 0.005952 | 0.06164 | 0.17079 | 0.073608 | -0.083478 | 0.02992 | 0.06442 | -0.033489 | 0.01056 | 0.03172 | 0.095129 | 0.043688 | 0.1071
1851.25 | 122.2824 | -122.113 | 0.09613 | 0.10354 | -0.031363 | 0.061258 | -0.002124 | 0.11409 | 0.081005 | -0.03067 | 0.043331 | 0.1479 | 0.032407 | -0.10637 | 0.002454 | 0.036954 | -0.065533 | -0.021484 | 0.131 | -0.003897 | 0.088724 | 0.025342 | 0.14156 | 0.10847 | -0.003204 | 0.070797 | 0.17536 | 0.059873 | -0.078899 | 0.02992 | 0.06442 | -0.038067 | 0.005982 | 0.040877 | 0.10886 | 0.029953 | 0.09794
1852.9844 | 122.2687 | -122.1039 | 0.11444 | 0.11727 | -0.026784 | 0.052101 | 0.011611 | 0.10951 | 0.081005 | -0.03067 | 0.038752 | 0.14332 | 0.041563 | -0.10637 | 0.002454 | 0.036954 | -0.070112 | -0.012328 | 0.14474 | 0.000682 | 0.079567 | 0.039077 | 0.13698 | 0.10847 | -0.003204 | 0.066218 | 0.17079 | 0.069029 | -0.078899 | 0.02992 | 0.06442 | -0.042646 | 0.015138 | 0.036298 | 0.10886 | 0.039109 | 0.11167
1854.7344 | 122.3602 | -122.0764 | 0.10529 | 0.11727 | -0.031363 | 0.061258 | 0.002454 | 0.10493 | 0.081005 | -0.03067 | 0.038752 | 0.15248 | 0.055298 | -0.11552 | 0.002454 | 0.036954 | -0.070112 | -0.016906 | 0.14474 | -0.003897 | 0.088724 | 0.02992 | 0.1324 | 0.10847 | -0.003204 | 0.066218 | 0.17994 | 0.082764 | -0.088057 | 0.02992 | 0.06442 | -0.042646 | 0.01056 | 0.036298 | 0.10886 | 0.052844 | 0.12541
1856.4688 | 122.3694 | -122.1313 | 0.10529 | 0.10812 | -0.040521 | 0.056679 | 0.002454 | 0.10036 | 0.076426 | -0.026092 | 0.038752 | 0.1479 | 0.05072 | -0.10637 | 0.007032 | 0.036954 | -0.070112 | -0.016906 | 0.13558 | -0.013055 | 0.084145 | 0.02992 | 0.12782 | 0.10389 | 0.001374 | 0.066218 | 0.17536 | 0.078186 | -0.078899 | 0.034498 | 0.06442 | -0.042646 | 0.01056 | 0.03172 | 0.10886 | 0.043688 | 0.12083
1858.1406 | 122.3328 | -122.1176 | 0.11444 | 0.11269 | -0.031363 | 0.070415 | 0.007033 | 0.11409 | 0.081005 | -0.03067 | 0.043331 | 0.14332 | 0.041563 | -0.10637 | 0.002454 | 0.032376 | -0.065533 | -0.016906 | 0.14016 | -0.003897 | 0.097881 | 0.034499 | 0.14156 | 0.10847 | -0.003204 | 0.070797 | 0.17079 | 0.069029 | -0.078899 | 0.02992 | 0.059842 | -0.038067 | 0.01056 | 0.040877 | 0.10886 | 0.039109 | 0.1071
1859.8906 | 122.3831 | -122.0947 | 0.10529 | 0.12185 | -0.031363 | 0.052101 | 0.002454 | 0.10951 | 0.076426 | -0.03067 | 0.029595 | 0.1479 | 0.041563 | -0.10637 | 0.002454 | 0.032376 | -0.060955 | -0.016906 | 0.14932 | -0.003897 | 0.079567 | 0.02992 | 0.13698 | 0.10389 | -0.003204 | 0.057061 | 0.17536 | 0.069029 | -0.078899 | 0.02992 | 0.059842 | -0.033489 | 0.01056 | 0.027141 | 0.09055 | 0.039109 | 0.10252
1861.6406 | 122.3145 | -122.1359 | 0.10529 | 0.11727 | -0.031363 | 0.056679 | 0.007033 | 0.10493 | 0.090161 | -0.026092 | 0.043331 | 0.15248 | 0.05072 | -0.10637 | 0.007032 | 0.027798 | -0.070112 | -0.016906 | 0.14474 | -0.003897 | 0.084145 | 0.034499 | 0.1324 | 0.11763 | 0.001374 | 0.070797 | 0.17994 | 0.078186 | -0.078899 | 0.034498 | 0.055264 | -0.042646 | 0.01056 | 0.036299 | 0.11344 | 0.043688 | 0.12083
1863.3281 | 122.4152 | -122.0901 | 0.10071 | 0.11269 | -0.031363 | 0.052101 | -0.002124 | 0.10493 | 0.081005 | -0.035248 | 0.043331 | 0.13874 | 0.032407 | -0.11094 | 0.007032 | 0.032376 | -0.070112 | -0.012328 | 0.14016 | -0.003897 | 0.079567 | 0.025342 | 0.1324 | 0.10847 | -0.007782 | 0.070797 | 0.16621 | 0.059873 | -0.083478 | 0.034498 | 0.059842 | -0.042646 | 0.015138 | 0.036299 | 0.11344 | 0.025375 | 0.10252
1865.0781 | 122.4014 | -122.1039 | 0.07782 | 0.10812 | -0.035942 | 0.056679 | 0.007033 | 0.10493 | 0.081005 | -0.03067 | 0.034174 | 0.14332 | 0.046142 | -0.11094 | 0.002454 | 0.027798 | -0.060955 | -0.012328 | 0.13558 | -0.008476 | 0.084145 | 0.034499 | 0.1324 | 0.10847 | -0.003204 | 0.06164 | 0.17079 | 0.073608 | -0.083478 | 0.02992 | 0.055264 | -0.033489 | 0.015138 | 0.03172 | 0.095129 | 0.043688 | 0.1071
1866.8281 | 122.3557 | -122.1268 | 0.10986 | 0.12185 | -0.031363 | 0.056679 | 0.002454 | 0.11409 | 0.076426 | -0.03067 | 0.029595 | 0.1479 | 0.036985 | -0.11094 | 0.007032 | 0.032376 | -0.065533 | -0.016906 | 0.14932 | -0.003897 | 0.084145 | 0.02992 | 0.14156 | 0.10389 | -0.003204 | 0.057061 | 0.17536 | 0.064451 | -0.083478 | 0.034498 | 0.059842 | -0.038067 | 0.01056 | 0.022563 | 0.095128 | 0.029953 | 0.10252
1868.5 | 122.4014 | -122.0901 | 0.11902 | 0.10812 | -0.022205 | 0.061258 | 0.007033 | 0.10493 | 0.076426 | -0.03067 | 0.034174 | 0.14332 | 0.041563 | -0.10637 | 0.007032 | 0.027798 | -0.065533 | -0.016906 | 0.13558 | 0.005261 | 0.088724 | 0.034499 | 0.1324 | 0.10389 | -0.003204 | 0.06164 | 0.17079 | 0.069029 | -0.078899 | 0.034498 | 0.055264 | -0.038067 | 0.01056 | 0.027142 | 0.099707 | 0.034531 | 0.1071
1870.25 | 122.2916 | -122.1588 | 0.13733 | 0.10812 | -0.031363 | 0.070415 | 0.007033 | 0.11409 | 0.081005 | -0.026092 | 0.034174 | 0.13874 | 0.041563 | -0.10179 | 0.002454 | 0.032376 | -0.060955 | -0.016906 | 0.13558 | -0.003897 | 0.097881 | 0.034499 | 0.14156 | 0.10847 | 0.001374 | 0.06164 | 0.16621 | 0.069029 | -0.07432 | 0.02992 | 0.059842 | -0.033489 | 0.01056 | 0.03172 | 0.095129 | 0.039109 | 0.10252
1871.9844 | 122.3099 | -122.1588 | 0.11902 | 0.12185 | -0.040521 | 0.061258 | -0.006703 | 0.10036 | 0.071848 | -0.026092 | 0.034174 | 0.1479 | 0.036985 | -0.10637 | 0.007032 | 0.032376 | -0.070112 | -0.016906 | 0.14932 | -0.013055 | 0.088724 | 0.020763 | 0.12782 | 0.099314 | 0.001374 | 0.06164 | 0.17536 | 0.064451 | -0.078899 | 0.034498 | 0.059842 | -0.042646 | 0.01056 | 0.027142 | 0.10429 | 0.029953 | 0.1071
1873.7344 | 122.3877 | -122.1222 | 0.11444 | 0.11727 | -0.035942 | 0.052101 | -0.002124 | 0.10493 | 0.076426 | -0.035248 | 0.034174 | 0.15706 | 0.046142 | -0.11094 | 0.007032 | 0.032376 | -0.070112 | -0.012328 | 0.14474 | -0.008476 | 0.079567 | 0.025342 | 0.1324 | 0.10389 | -0.007782 | 0.06164 | 0.18452 | 0.073608 | -0.083478 | 0.034498 | 0.059842 | -0.042646 | 0.015138 | 0.027142 | 0.10429 | 0.03911 | 0.11625
1875.4219 | 122.4335 | -122.1222 | 0.091553 | 0.11269 | -0.031363 | 0.061258 | 0.002454 | 0.10951 | 0.076426 | -0.035248 | 0.034174 | 0.1479 | 0.046142 | -0.11094 | 0.002454 | 0.041532 | -0.060955 | -0.00775 | 0.14016 | -0.003897 | 0.088724 | 0.02992 | 0.13698 | 0.10389 | -0.007782 | 0.06164 | 0.17536 | 0.073608 | -0.083478 | 0.02992 | 0.068998 | -0.033489 | 0.019716 | 0.03172 | 0.095129 | 0.043688 | 0.1071
1877.1562 | 122.4472 | -122.1222 | 0.091553 | 0.11727 | -0.031363 | 0.056679 | 0.002454 | 0.10951 | 0.076426 | -0.03067 | 0.038752 | 0.13874 | 0.027829 | -0.10179 | 0.007032 | 0.036954 | -0.065533 | -0.021484 | 0.14474 | -0.003897 | 0.084145 | 0.02992 | 0.13698 | 0.10389 | -0.003204 | 0.066218 | 0.16621 | 0.055295 | -0.07432 | 0.034498 | 0.06442 | -0.038067 | 0.005982 | 0.03172 | 0.10428 | 0.020797 | 0.093362
1878.9062 | 122.3053 | -122.1542 | 0.14191 | 0.11727 | -0.035942 | 0.061258 | -0.002124 | 0.10493 | 0.085583 | -0.026092 | 0.038752 | 0.14332 | 0.041563 | -0.10637 | 0.002454 | 0.032376 | -0.060955 | -0.012328 | 0.14474 | -0.008476 | 0.088724 | 0.025342 | 0.1324 | 0.11305 | 0.001374 | 0.066218 | 0.17079 | 0.069029 | -0.078899 | 0.02992 | 0.059842 | -0.033489 | 0.015138 | 0.036298 | 0.099707 | 0.039109 | 0.10252
1880.5938 | 122.3145 | -122.168 | 0.10986 | 0.11727 | -0.026784 | 0.061258 | 0.007033 | 0.10036 | 0.076426 | -0.03067 | 0.038752 | 0.14332 | 0.041563 | -0.10637 | 0.007032 | 0.032376 | -0.07469 | -0.016906 | 0.14474 | 0.000682 | 0.088724 | 0.034499 | 0.12782 | 0.10389 | -0.003204 | 0.066218 | 0.17079 | 0.069029 | -0.078899 | 0.034498 | 0.059842 | -0.047224 | 0.01056 | 0.03172 | 0.11344 | 0.034531 | 0.11625
1882.3281 | 122.4106 | -122.1497 | 0.10071 | 0.11727 | -0.035942 | 0.056679 | 0.002454 | 0.10951 | 0.085583 | -0.035248 | 0.038752 | 0.1479 | 0.036985 | -0.11094 | 0.007032 | 0.036954 | -0.070112 | -0.021484 | 0.14474 | -0.008476 | 0.084145 | 0.02992 | 0.13698 | 0.11305 | -0.007782 | 0.066218 | 0.17536 | 0.064451 | -0.083478 | 0.034498 | 0.06442 | -0.042646 | 0.005982 | 0.03172 | 0.10886 | 0.029953 | 0.1071
1884.0781 | 122.3877 | -122.1176 | 0.09613 | 0.10812 | -0.026784 | 0.056679 | -0.002124 | 0.10951 | 0.081005 | -0.03067 | 0.034174 | 0.1479 | 0.041563 | -0.10179 | 0.01161 | 0.032376 | -0.065533 | -0.012328 | 0.13558 | 0.000682 | 0.084145 | 0.025342 | 0.13698 | 0.10847 | -0.003204 | 0.06164 | 0.17536 | 0.069029 | -0.07432 | 0.039076 | 0.059842 | -0.038067 | 0.015138 | 0.022564 | 0.099707 | 0.029953 | 0.1071
1885.8594 | 122.4609 | -122.1039 | 0.10071 | 0.10812 | -0.031363 | 0.061258 | -0.002124 | 0.10036 | 0.081005 | -0.03067 | 0.038752 | 0.14332 | 0.046142 | -0.10637 | 0.002454 | 0.032376 | -0.065533 | -0.012328 | 0.13558 | -0.003897 | 0.088724 | 0.025342 | 0.12782 | 0.10847 | -0.003204 | 0.066218 | 0.17079 | 0.073608 | -0.078899 | 0.02992 | 0.059842 | -0.038067 | 0.015138 | 0.036298 | 0.10428 | 0.043688 | 0.11167
1887.5469 | 122.3969 | -122.1588 | 0.091553 | 0.11727 | -0.040521 | 0.056679 | 0.002454 | 0.10493 | 0.081005 | -0.035248 | 0.034174 | 0.1479 | 0.055298 | -0.11094 | -0.002124 | 0.032376 | -0.070112 | -0.012328 | 0.14474 | -0.013055 | 0.084145 | 0.02992 | 0.1324 | 0.10847 | -0.007782 | 0.06164 | 0.17536 | 0.082764 | -0.083478 | 0.025342 | 0.059842 | -0.042646 | 0.015138 | 0.036298 | 0.10429 | 0.057422 | 0.12541
1889.2969 | 122.4518 | -122.1405 | 0.07782 | 0.11269 | -0.035942 | 0.056679 | 0.002454 | 0.095778 | 0.071848 | -0.03067 | 0.038752 | 0.1479 | 0.05072 | -0.11094 | 0.002454 | 0.032376 | -0.07469 | -0.012328 | 0.14016 | -0.008476 | 0.084145 | 0.02992 | 0.12324 | 0.099314 | -0.003204 | 0.066218 | 0.17536 | 0.078186 | -0.083478 | 0.02992 | 0.059842 | -0.047224 | 0.015138 | 0.036298 | 0.11344 | 0.048266 | 0.12541
1891.0469 | 122.3419 | -122.168 | 0.10986 | 0.11727 | -0.040521 | 0.061258 | 0.002454 | 0.10951 | 0.081005 | -0.03067 | 0.034174 | 0.1479 | 0.05072 | -0.10637 | 0.007032 | 0.041532 | -0.070112 | -0.016906 | 0.14474 | -0.013055 | 0.088724 | 0.02992 | 0.13698 | 0.10847 | -0.003204 | 0.06164 | 0.17536 | 0.078186 | -0.078899 | 0.034498 | 0.068998 | -0.042646 | 0.01056 | 0.027142 | 0.10429 | 0.043688 | 0.12083
1892.7188 | 122.4243 | -122.1542 | 0.10986 | 0.12185 | -0.035942 | 0.061258 | -0.002124 | 0.10493 | 0.076426 | -0.021514 | 0.038752 | 0.1479 | 0.036985 | -0.11094 | 0.007032 | 0.027798 | -0.070112 | -0.012328 | 0.14932 | -0.008476 | 0.088724 | 0.025342 | 0.1324 | 0.10389 | 0.005952 | 0.066218 | 0.17536 | 0.064451 | -0.083478 | 0.034498 | 0.055264 | -0.042646 | 0.015138 | 0.03172 | 0.10886 | 0.029953 | 0.1071
1894.4531 | 122.4609 | -122.1634 | 0.091553 | 0.11269 | -0.035942 | 0.061258 | 0.002454 | 0.10036 | 0.081005 | -0.03067 | 0.029595 | 0.14332 | 0.05072 | -0.10179 | 0.01161 | 0.032376 | -0.070112 | -0.016906 | 0.14016 | -0.008476 | 0.088724 | 0.02992 | 0.12782 | 0.10847 | -0.003204 | 0.057061 | 0.17079 | 0.078186 | -0.07432 | 0.039076 | 0.059842 | -0.042646 | 0.01056 | 0.017985 | 0.099707 | 0.03911 | 0.12083
1896.1406 | 122.4792 | -122.1542 | 0.09613 | 0.10812 | -0.035942 | 0.056679 | 0.007033 | 0.10951 | 0.071848 | -0.03067 | 0.038752 | 0.1479 | 0.046142 | -0.097207 | 0.002454 | 0.032376 | -0.065533 | -0.016906 | 0.13558 | -0.008476 | 0.084145 | 0.034499 | 0.13698 | 0.099314 | -0.003204 | 0.066218 | 0.17536 | 0.073608 | -0.069741 | 0.02992 | 0.059842 | -0.038067 | 0.01056 | 0.036298 | 0.10428 | 0.043688 | 0.11167
1897.875 | 122.4518 | -122.1085 | 0.091553 | 0.11727 | -0.035942 | 0.056679 | 0.007033 | 0.11409 | 0.076426 | -0.03067 | 0.034174 | 0.14332 | 0.041563 | -0.11094 | 0.007032 | 0.032376 | -0.070112 | -0.016906 | 0.14474 | -0.008476 | 0.084145 | 0.034499 | 0.14156 | 0.10389 | -0.003204 | 0.06164 | 0.17079 | 0.069029 | -0.083478 | 0.034498 | 0.059842 | -0.042646 | 0.01056 | 0.027142 | 0.10429 | 0.034531 | 0.11167
1899.5625 | 122.4335 | -122.1313 | 0.086975 | 0.11269 | -0.031363 | 0.052101 | -0.002124 | 0.10951 | 0.081005 | -0.026092 | 0.034174 | 0.1479 | 0.036985 | -0.11552 | -0.002124 | 0.036954 | -0.065533 | -0.012328 | 0.14016 | -0.003897 | 0.079567 | 0.025342 | 0.13698 | 0.10847 | 0.001374 | 0.06164 | 0.17536 | 0.064451 | -0.088057 | 0.025342 | 0.06442 | -0.038067 | 0.015138 | 0.036298 | 0.099707 | 0.039109 | 0.10252
1901.25 | 122.3328 | -122.1909 | 0.12817 | 0.11727 | -0.035942 | 0.065837 | 0.011611 | 0.10493 | 0.085583 | -0.03067 | 0.038752 | 0.14332 | 0.041563 | -0.10637 | 0.007032 | 0.036954 | -0.065533 | -0.012328 | 0.14474 | -0.008476 | 0.093303 | 0.039077 | 0.1324 | 0.11305 | -0.003204 | 0.066218 | 0.17079 | 0.069029 | -0.078899 | 0.034498 | 0.06442 | -0.038067 | 0.015138 | 0.03172 | 0.10428 | 0.034531 | 0.1071
1902.9844 | 122.3648 | -122.1771 | 0.10529 | 0.11269 | -0.031363 | 0.061258 | -0.002124 | 0.10036 | 0.081005 | -0.035248 | 0.038752 | 0.1479 | 0.046142 | -0.10637 | -0.002124 | 0.032376 | -0.060955 | -0.012328 | 0.14016 | -0.003897 | 0.088724 | 0.025342 | 0.12782 | 0.10847 | -0.007782 | 0.066218 | 0.17536 | 0.073608 | -0.078899 | 0.025342 | 0.059842 | -0.033489 | 0.015138 | 0.040876 | 0.099707 | 0.048266 | 0.1071
1904.7188 | 122.4152 | -122.1863 | 0.086975 | 0.10812 | -0.031363 | 0.056679 | 0.002454 | 0.10493 | 0.076426 | -0.026092 | 0.034174 | 0.15248 | 0.05072 | -0.11094 | -0.002124 | 0.032376 | -0.079268 | -0.012328 | 0.13558 | -0.003897 | 0.084145 | 0.02992 | 0.1324 | 0.10389 | 0.001374 | 0.06164 | 0.17994 | 0.078186 | -0.083478 | 0.025342 | 0.059842 | -0.051802 | 0.015138 | 0.036298 | 0.11344 | 0.052844 | 0.12999
1906.4688 | 122.3831 | -122.2092 | 0.11444 | 0.11727 | -0.026784 | 0.056679 | 0.011611 | 0.10951 | 0.076426 | -0.026092 | 0.038752 | 0.14332 | 0.041563 | -0.1201 | 0.002454 | 0.036954 | -0.065533 | -0.016906 | 0.14474 | 0.000682 | 0.084145 | 0.039077 | 0.13698 | 0.10389 | 0.001374 | 0.066218 | 0.17079 | 0.069029 | -0.092637 | 0.02992 | 0.06442 | -0.038067 | 0.01056 | 0.036298 | 0.10428 | 0.039109 | 0.1071
1908.1562 | 122.3877 | -122.1817 | 0.10529 | 0.10812 | -0.035942 | 0.065837 | 0.011611 | 0.10493 | 0.076426 | -0.035248 | 0.038752 | 0.1479 | 0.046142 | -0.10637 | 0.007032 | 0.036954 | -0.07469 | -0.012328 | 0.13558 | -0.008476 | 0.093303 | 0.039077 | 0.1324 | 0.10389 | -0.007782 | 0.066218 | 0.17536 | 0.073608 | -0.078899 | 0.034498 | 0.06442 | -0.047224 | 0.015138 | 0.03172 | 0.11344 | 0.03911 | 0.12083
1909.9062 | 122.4243 | -122.1863 | 0.13275 | 0.11727 | -0.031363 | 0.052101 | 0.002454 | 0.10951 | 0.076426 | -0.026092 | 0.038752 | 0.14332 | 0.046142 | -0.11094 | 0.002454 | 0.032376 | -0.070112 | -0.012328 | 0.14474 | -0.003897 | 0.079567 | 0.02992 | 0.13698 | 0.10389 | 0.001374 | 0.066218 | 0.17079 | 0.073608 | -0.083478 | 0.02992 | 0.059842 | -0.042646 | 0.015138 | 0.036298 | 0.10886 | 0.043688 | 0.11625
1911.6562 | 122.4792 | -122.1634 | 0.059509 | 0.11727 | -0.031363 | 0.056679 | 0.002454 | 0.10036 | 0.071848 | -0.03067 | 0.038752 | 0.14332 | 0.027829 | -0.10637 | -0.002124 | 0.036954 | -0.07469 | -0.016906 | 0.14474 | -0.003897 | 0.084145 | 0.02992 | 0.12782 | 0.099314 | -0.003204 | 0.066218 | 0.17079 | 0.055295 | -0.078899 | 0.025342 | 0.06442 | -0.047224 | 0.01056 | 0.040876 | 0.11344 | 0.029953 | 0.10252
1913.3438 | 122.3465 | -122.2 | 0.11902 | 0.11727 | -0.031363 | 0.052101 | 0.002454 | 0.10493 | 0.081005 | -0.03067 | 0.034174 | 0.1479 | 0.041563 | -0.11094 | 0.002454 | 0.036954 | -0.065533 | -0.016906 | 0.14474 | -0.003897 | 0.079567 | 0.02992 | 0.1324 | 0.10847 | -0.003204 | 0.06164 | 0.17536 | 0.069029 | -0.083478 | 0.02992 | 0.06442 | -0.038067 | 0.01056 | 0.03172 | 0.099707 | 0.039109 | 0.1071
1915.0312 | 122.4106 | -122.1909 | 0.10986 | 0.11269 | -0.026784 | 0.061258 | 0.002454 | 0.10493 | 0.071848 | -0.026092 | 0.034174 | 0.1479 | 0.041563 | -0.10637 | 0.007032 | 0.036954 | -0.065533 | -0.016906 | 0.14016 | 0.000682 | 0.088724 | 0.02992 | 0.1324 | 0.099314 | 0.001374 | 0.06164 | 0.17536 | 0.069029 | -0.078899 | 0.034498 | 0.06442 | -0.038067 | 0.01056 | 0.027142 | 0.099707 | 0.034531 | 0.1071
1916.7812 | 122.4701 | -122.1725 | 0.10986 | 0.11727 | -0.035942 | 0.052101 | 0.002454 | 0.10036 | 0.076426 | -0.03067 | 0.043331 | 0.14332 | 0.032407 | -0.10637 | 0.007032 | 0.032376 | -0.065533 | -0.012328 | 0.14474 | -0.008476 | 0.079567 | 0.02992 | 0.12782 | 0.10389 | -0.003204 | 0.070797 | 0.17079 | 0.059873 | -0.078899 | 0.034498 | 0.059842 | -0.038067 | 0.015138 | 0.036299 | 0.10886 | 0.025375 | 0.09794
1918.5312 | 122.4976 | -122.1909 | 0.073242 | 0.11269 | -0.035942 | 0.056679 | -0.002124 | 0.10951 | 0.081005 | -0.03067 | 0.043331 | 0.15248 | 0.032407 | -0.10637 | 0.007032 | 0.027798 | -0.065533 | -0.016906 | 0.14016 | -0.008476 | 0.084145 | 0.025342 | 0.13698 | 0.10847 | -0.003204 | 0.070797 | 0.17994 | 0.059873 | -0.078899 | 0.034498 | 0.055264 | -0.038067 | 0.01056 | 0.036299 | 0.10886 | 0.025375 | 0.09794
1920.2188 | 122.374 | -122.2229 | 0.1236 | 0.11269 | -0.031363 | 0.056679 | -0.002124 | 0.10493 | 0.081005 | -0.03067 | 0.034174 | 0.1479 | 0.046142 | -0.10637 | 0.007032 | 0.036954 | -0.070112 | -0.012328 | 0.14016 | -0.003897 | 0.084145 | 0.025342 | 0.1324 | 0.10847 | -0.003204 | 0.06164 | 0.17536 | 0.073608 | -0.078899 | 0.034498 | 0.06442 | -0.042646 | 0.015138 | 0.027142 | 0.10429 | 0.03911 | 0.11625
1921.9531 | 122.4518 | -122.1954 | 0.10529 | 0.11269 | -0.031363 | 0.056679 | -0.002124 | 0.10951 | 0.076426 | -0.03067 | 0.038752 | 0.15248 | 0.05072 | -0.11094 | 0.002454 | 0.032376 | -0.065533 | -0.016906 | 0.14016 | -0.003897 | 0.084145 | 0.025342 | 0.13698 | 0.10389 | -0.003204 | 0.066218 | 0.17994 | 0.078186 | -0.083478 | 0.02992 | 0.059842 | -0.038067 | 0.01056 | 0.036298 | 0.10428 | 0.048266 | 0.11625
1923.625 | 122.3785 | -122.2137 | 0.1236 | 0.11727 | -0.031363 | 0.056679 | 0.007033 | 0.10951 | 0.071848 | -0.03067 | 0.029595 | 0.14332 | 0.046142 | -0.11094 | 0.007032 | 0.032376 | -0.07469 | -0.021484 | 0.14474 | -0.003897 | 0.084145 | 0.034499 | 0.13698 | 0.099314 | -0.003204 | 0.057061 | 0.17079 | 0.073608 | -0.083478 | 0.034498 | 0.059842 | -0.047224 | 0.005982 | 0.022563 | 0.10429 | 0.03911 | 0.12083
1925.3594 | 122.3694 | -122.2275 | 0.12817 | 0.11727 | -0.026784 | 0.056679 | 0.002454 | 0.10036 | 0.076426 | -0.026092 | 0.034174 | 0.1479 | 0.046142 | -0.11094 | 0.01161 | 0.036954 | -0.070112 | -0.012328 | 0.14474 | 0.000682 | 0.084145 | 0.02992 | 0.12782 | 0.10389 | 0.001374 | 0.06164 | 0.17536 | 0.073608 | -0.083478 | 0.039076 | 0.06442 | -0.042646 | 0.015138 | 0.022564 | 0.10429 | 0.034532 | 0.11625
1927.0469 | 122.4472 | -122.1863 | 0.10529 | 0.11269 | -0.031363 | 0.052101 | -0.006703 | 0.10493 | 0.076426 | -0.035248 | 0.034174 | 0.1479 | 0.05072 | -0.10637 | -0.002124 | 0.036954 | -0.070112 | -0.016906 | 0.14016 | -0.003897 | 0.079567 | 0.020763 | 0.1324 | 0.10389 | -0.007782 | 0.06164 | 0.17536 | 0.078186 | -0.078899 | 0.025342 | 0.06442 | -0.042646 | 0.01056 | 0.036298 | 0.10429 | 0.052844 | 0.12083
1928.7969 | 122.4518 | -122.1909 | 0.10071 | 0.11269 | -0.040521 | 0.061258 | 0.002454 | 0.10493 | 0.076426 | -0.035248 | 0.034174 | 0.1479 | 0.041563 | -0.11094 | -0.002124 | 0.032376 | -0.065533 | -0.026063 | 0.14016 | -0.013055 | 0.088724 | 0.02992 | 0.1324 | 0.10389 | -0.007782 | 0.06164 | 0.17536 | 0.069029 | -0.083478 | 0.025342 | 0.059842 | -0.038067 | 0.001403 | 0.036298 | 0.099707 | 0.043687 | 0.1071
1930.5469 | 122.4243 | -122.2275 | 0.1236 | 0.11727 | -0.026784 | 0.052101 | 0.011611 | 0.10951 | 0.076426 | -0.03067 | 0.034174 | 0.1479 | 0.032407 | -0.11094 | 0.002454 | 0.032376 | -0.065533 | -0.021484 | 0.14474 | 0.000682 | 0.079567 | 0.039077 | 0.13698 | 0.10389 | -0.003204 | 0.06164 | 0.17536 | 0.059873 | -0.083478 | 0.02992 | 0.059842 | -0.038067 | 0.005982 | 0.03172 | 0.099707 | 0.029953 | 0.09794
1932.2812 | 122.4518 | -122.2275 | 0.10071 | 0.11727 | -0.031363 | 0.052101 | -0.002124 | 0.11867 | 0.076426 | -0.03067 | 0.034174 | 0.14332 | 0.05072 | -0.11094 | 0.002454 | 0.032376 | -0.070112 | -0.021484 | 0.14474 | -0.003897 | 0.079567 | 0.025342 | 0.14613 | 0.10389 | -0.003204 | 0.06164 | 0.17079 | 0.078186 | -0.083478 | 0.02992 | 0.059842 | -0.042646 | 0.005982 | 0.03172 | 0.10429 | 0.048266 | 0.12083
1934.0156 | 122.493 | -122.2046 | 0.086975 | 0.11727 | -0.031363 | 0.052101 | 0.002454 | 0.10036 | 0.081005 | -0.03067 | 0.034174 | 0.14332 | 0.032407 | -0.10179 | 0.01161 | 0.032376 | -0.070112 | -0.012328 | 0.14474 | -0.003897 | 0.079567 | 0.02992 | 0.12782 | 0.10847 | -0.003204 | 0.06164 | 0.17079 | 0.059873 | -0.07432 | 0.039076 | 0.059842 | -0.042646 | 0.015138 | 0.022564 | 0.10429 | 0.020797 | 0.10252
1935.7812 | 122.3969 | -122.2366 | 0.10529 | 0.11269 | -0.035942 | 0.052101 | 0.002454 | 0.11409 | 0.081005 | -0.026092 | 0.029595 | 0.1479 | 0.041563 | -0.11552 | 0.002454 | 0.027798 | -0.070112 | -0.012328 | 0.14016 | -0.008476 | 0.079567 | 0.02992 | 0.14156 | 0.10847 | 0.001374 | 0.057061 | 0.17536 | 0.069029 | -0.088057 | 0.02992 | 0.055264 | -0.042646 | 0.015138 | 0.027141 | 0.099707 | 0.039109 | 0.11167
1937.4531 | 122.5113 | -122.1863 | 0.073242 | 0.10812 | -0.026784 | 0.061258 | 0.002454 | 0.10951 | 0.081005 | -0.03067 | 0.034174 | 0.14332 | 0.036985 | -0.11552 | 0.002454 | 0.036954 | -0.079268 | -0.00775 | 0.13558 | 0.000682 | 0.088724 | 0.02992 | 0.13698 | 0.10847 | -0.003204 | 0.06164 | 0.17079 | 0.064451 | -0.088057 | 0.02992 | 0.06442 | -0.051802 | 0.019716 | 0.03172 | 0.11344 | 0.034531 | 0.11625
1939.1875 | 122.4701 | -122.2229 | 0.082397 | 0.12185 | -0.035942 | 0.052101 | 0.011611 | 0.10493 | 0.071848 | -0.021514 | 0.038752 | 0.1479 | 0.036985 | -0.10637 | 0.007032 | 0.032376 | -0.065533 | -0.012328 | 0.14932 | -0.008476 | 0.079567 | 0.039077 | 0.1324 | 0.099314 | 0.005952 | 0.066218 | 0.17536 | 0.064451 | -0.078899 | 0.034498 | 0.059842 | -0.038067 | 0.015138 | 0.03172 | 0.10428 | 0.029953 | 0.10252
1940.9531 | 122.4106 | -122.2275 | 0.11902 | 0.11269 | -0.026784 | 0.052101 | 0.002454 | 0.11409 | 0.081005 | -0.03067 | 0.034174 | 0.15248 | 0.032407 | -0.11552 | 0.002454 | 0.036954 | -0.060955 | -0.00775 | 0.14016 | 0.000682 | 0.079567 | 0.02992 | 0.14156 | 0.10847 | -0.003204 | 0.06164 | 0.17994 | 0.059873 | -0.088057 | 0.02992 | 0.06442 | -0.033489 | 0.019716 | 0.03172 | 0.095129 | 0.029953 | 0.093362
1942.625 | 122.5204 | -122.1771 | 0.07782 | 0.11727 | -0.031363 | 0.056679 | 0.007033 | 0.10493 | 0.071848 | -0.026092 | 0.038752 | 0.1479 | 0.041563 | -0.11094 | 0.002454 | 0.027798 | -0.070112 | -0.012328 | 0.14474 | -0.003897 | 0.084145 | 0.034499 | 0.1324 | 0.099314 | 0.001374 | 0.066218 | 0.17536 | 0.069029 | -0.083478 | 0.02992 | 0.055264 | -0.042646 | 0.015138 | 0.036298 | 0.10886 | 0.039109 | 0.11167
1944.2969 | 122.5159 | -122.2321 | 0.10071 | 0.12185 | -0.031363 | 0.052101 | 0.002454 | 0.10951 | 0.076426 | -0.03067 | 0.038752 | 0.1479 | 0.027829 | -0.1201 | 0.007032 | 0.036954 | -0.065533 | -0.021484 | 0.14932 | -0.003897 | 0.079567 | 0.02992 | 0.13698 | 0.10389 | -0.003204 | 0.066218 | 0.17536 | 0.055295 | -0.092637 | 0.034498 | 0.06442 | -0.038067 | 0.005982 | 0.03172 | 0.10428 | 0.020797 | 0.093362
1946.0469 | 122.3969 | -122.2458 | 0.10986 | 0.11727 | -0.026784 | 0.061258 | 0.007033 | 0.11409 | 0.081005 | -0.026092 | 0.038752 | 0.14332 | 0.046142 | -0.11094 | 0.007032 | 0.032376 | -0.070112 | -0.021484 | 0.14474 | 0.000682 | 0.088724 | 0.034499 | 0.14156 | 0.10847 | 0.001374 | 0.066218 | 0.17079 | 0.073608 | -0.083478 | 0.034498 | 0.059842 | -0.042646 | 0.005982 | 0.03172 | 0.10886 | 0.03911 | 0.11625
1947.7344 | 122.493 | -122.2137 | 0.086975 | 0.11269 | -0.026784 | 0.061258 | 0.002454 | 0.10036 | 0.071848 | -0.026092 | 0.034174 | 0.1479 | 0.05072 | -0.10637 | 0.002454 | 0.036954 | -0.065533 | -0.012328 | 0.14016 | 0.000682 | 0.088724 | 0.02992 | 0.12782 | 0.099314 | 0.001374 | 0.06164 | 0.17536 | 0.078186 | -0.078899 | 0.02992 | 0.06442 | -0.038067 | 0.015138 | 0.03172 | 0.099707 | 0.048266 | 0.11625
1949.4688 | 122.3877 | -122.2778 | 0.13275 | 0.10812 | -0.026784 | 0.061258 | 0.002454 | 0.10493 | 0.085583 | -0.026092 | 0.038752 | 0.1479 | 0.05072 | -0.10637 | 0.007032 | 0.032376 | -0.065533 | -0.012328 | 0.13558 | 0.000682 | 0.088724 | 0.02992 | 0.1324 | 0.11305 | 0.001374 | 0.066218 | 0.17536 | 0.078186 | -0.078899 | 0.034498 | 0.059842 | -0.038067 | 0.015138 | 0.03172 | 0.10428 | 0.043688 | 0.11625
1951.1562 | 122.4289 | -122.2687 | 0.11444 | 0.12185 | -0.026784 | 0.056679 | -0.002124 | 0.11409 | 0.071848 | -0.026092 | 0.029595 | 0.1479 | 0.055298 | -0.10179 | 0.007032 | 0.032376 | -0.07469 | -0.016906 | 0.14932 | 0.000682 | 0.084145 | 0.025342 | 0.14156 | 0.099314 | 0.001374 | 0.057061 | 0.17536 | 0.082764 | -0.07432 | 0.034498 | 0.059842 | -0.047224 | 0.01056 | 0.022563 | 0.10429 | 0.048266 | 0.12999
1952.9062 | 122.5388 | -122.2229 | 0.091553 | 0.10812 | -0.026784 | 0.056679 | 0.007033 | 0.10493 | 0.081005 | -0.026092 | 0.038752 | 0.14332 | 0.046142 | -0.11094 | 0.01161 | 0.041532 | -0.060955 | -0.016906 | 0.13558 | 0.000682 | 0.084145 | 0.034499 | 0.1324 | 0.10847 | 0.001374 | 0.066218 | 0.17079 | 0.073608 | -0.083478 | 0.039076 | 0.068998 | -0.033489 | 0.01056 | 0.027142 | 0.099707 | 0.034532 | 0.1071
1954.6562 | 122.5204 | -122.2 | 0.10529 | 0.10812 | -0.031363 | 0.056679 | 0.007033 | 0.10493 | 0.071848 | -0.03067 | 0.038752 | 0.1479 | 0.05072 | -0.10637 | 0.01161 | 0.032376 | -0.065533 | -0.016906 | 0.13558 | -0.003897 | 0.084145 | 0.034499 | 0.1324 | 0.099314 | -0.003204 | 0.066218 | 0.17536 | 0.078186 | -0.078899 | 0.039076 | 0.059842 | -0.038067 | 0.01056 | 0.027142 | 0.10428 | 0.03911 | 0.11625
1956.3438 | 122.4564 | -122.2504 | 0.13275 | 0.11727 | -0.022205 | 0.056679 | 0.007033 | 0.11409 | 0.081005 | -0.03067 | 0.025017 | 0.14332 | 0.046142 | -0.10637 | 0.002454 | 0.036954 | -0.07469 | -0.016906 | 0.14474 | 0.005261 | 0.084145 | 0.034499 | 0.14156 | 0.10847 | -0.003204 | 0.052483 | 0.17079 | 0.073608 | -0.078899 | 0.02992 | 0.06442 | -0.047224 | 0.01056 | 0.022563 | 0.099707 | 0.043688 | 0.12083
1958.0938 | 122.4152 | -122.2778 | 0.11902 | 0.10812 | -0.031363 | 0.061258 | 0.007033 | 0.10493 | 0.076426 | -0.035248 | 0.043331 | 0.15248 | 0.041563 | -0.10637 | 0.007032 | 0.036954 | -0.065533 | -0.016906 | 0.13558 | -0.003897 | 0.088724 | 0.034499 | 0.1324 | 0.10389 | -0.007782 | 0.070797 | 0.17994 | 0.069029 | -0.078899 | 0.034498 | 0.06442 | -0.038067 | 0.01056 | 0.036299 | 0.10886 | 0.034531 | 0.1071
1959.8438 | 122.5388 | -122.2504 | 0.073242 | 0.11727 | -0.031363 | 0.065837 | 0.002454 | 0.10036 | 0.071848 | -0.03067 | 0.038752 | 0.1479 | 0.059877 | -0.11094 | 0.002454 | 0.036954 | -0.065533 | -0.012328 | 0.14474 | -0.003897 | 0.093303 | 0.02992 | 0.12782 | 0.099314 | -0.003204 | 0.066218 | 0.17536 | 0.087343 | -0.083478 | 0.02992 | 0.06442 | -0.038067 | 0.015138 | 0.036298 | 0.10428 | 0.057423 | 0.12541
1961.5312 | 122.4609 | -122.2458 | 0.09613 | 0.12185 | -0.031363 | 0.061258 | 0.007033 | 0.11409 | 0.076426 | -0.021514 | 0.029595 | 0.1479 | 0.059877 | -0.10637 | 0.002454 | 0.032376 | -0.065533 | -0.016906 | 0.14932 | -0.003897 | 0.088724 | 0.034499 | 0.14156 | 0.10389 | 0.005952 | 0.057061 | 0.17536 | 0.087343 | -0.078899 | 0.02992 | 0.059842 | -0.038067 | 0.01056 | 0.027141 | 0.095128 | 0.057423 | 0.12541
1963.2812 | 122.4701 | -122.2549 | 0.10529 | 0.11727 | -0.035942 | 0.052101 | 0.002454 | 0.10951 | 0.09474 | -0.03067 | 0.038752 | 0.13874 | 0.036985 | -0.11094 | 0.007032 | 0.032376 | -0.065533 | -0.016906 | 0.14474 | -0.008476 | 0.079567 | 0.02992 | 0.13698 | 0.12221 | -0.003204 | 0.066218 | 0.16621 | 0.064451 | -0.083478 | 0.034498 | 0.059842 | -0.038067 | 0.01056 | 0.03172 | 0.10428 | 0.029953 | 0.10252
1965.0312 | 122.4747 | -122.2641 | 0.091553 | 0.11727 | -0.026784 | 0.070415 | 0.002454 | 0.10493 | 0.085583 | -0.03067 | 0.038752 | 0.14332 | 0.036985 | -0.10637 | -0.002124 | 0.036954 | -0.07469 | -0.016906 | 0.14474 | 0.000682 | 0.097881 | 0.02992 | 0.1324 | 0.11305 | -0.003204 | 0.066218 | 0.17079 | 0.064451 | -0.078899 | 0.025342 | 0.06442 | -0.047224 | 0.01056 | 0.040876 | 0.11344 | 0.039109 | 0.11167
1966.7188 | 122.4609 | -122.2916 | 0.1236 | 0.12185 | -0.026784 | 0.047522 | -0.002124 | 0.10493 | 0.081005 | -0.03067 | 0.047909 | 0.14332 | 0.046142 | -0.10637 | 0.007032 | 0.032376 | -0.065533 | -0.021484 | 0.14932 | 0.000682 | 0.074988 | 0.025342 | 0.1324 | 0.10847 | -0.003204 | 0.075375 | 0.17079 | 0.073608 | -0.078899 | 0.034498 | 0.059842 | -0.038067 | 0.005982 | 0.040877 | 0.11344 | 0.03911 | 0.11167
1968.4688 | 122.5479 | -122.2046 | 0.09613 | 0.11727 | -0.031363 | 0.056679 | 0.002454 | 0.10951 | 0.085583 | -0.03067 | 0.034174 | 0.14332 | 0.036985 | -0.11094 | 0.002454 | 0.041532 | -0.065533 | -0.012328 | 0.14474 | -0.003897 | 0.084145 | 0.02992 | 0.13698 | 0.11305 | -0.003204 | 0.06164 | 0.17079 | 0.064451 | -0.083478 | 0.02992 | 0.068998 | -0.038067 | 0.015138 | 0.03172 | 0.099707 | 0.034531 | 0.10252
1970.1562 | 122.5433 | -122.2412 | 0.082397 | 0.12185 | -0.035942 | 0.047522 | 0.007033 | 0.10493 | 0.085583 | -0.026092 | 0.038752 | 0.1479 | 0.046142 | -0.11094 | 0.007032 | 0.041532 | -0.065533 | -0.012328 | 0.14932 | -0.008476 | 0.074988 | 0.034499 | 0.1324 | 0.11305 | 0.001374 | 0.066218 | 0.17536 | 0.073608 | -0.083478 | 0.034498 | 0.068998 | -0.038067 | 0.015138 | 0.03172 | 0.10428 | 0.03911 | 0.11167
1971.9062 | 122.4152 | -122.2778 | 0.13275 | 0.11269 | -0.031363 | 0.056679 | -0.002124 | 0.10493 | 0.085583 | -0.03067 | 0.038752 | 0.14332 | 0.041563 | -0.11094 | -0.002124 | 0.041532 | -0.060955 | -0.016906 | 0.14016 | -0.003897 | 0.084145 | 0.025342 | 0.1324 | 0.11305 | -0.003204 | 0.066218 | 0.17079 | 0.069029 | -0.083478 | 0.025342 | 0.068998 | -0.033489 | 0.01056 | 0.040876 | 0.099707 | 0.043687 | 0.10252
1973.6562 | 122.5662 | -122.2641 | 0.09613 | 0.11269 | -0.035942 | 0.052101 | 0.007033 | 0.10951 | 0.076426 | -0.03067 | 0.029595 | 0.15248 | 0.05072 | -0.10637 | 0.007032 | 0.036954 | -0.060955 | -0.016906 | 0.14016 | -0.008476 | 0.079567 | 0.034499 | 0.13698 | 0.10389 | -0.003204 | 0.057061 | 0.17994 | 0.078186 | -0.078899 | 0.034498 | 0.06442 | -0.033489 | 0.01056 | 0.022563 | 0.09055 | 0.043688 | 0.11167
1975.4062 | 122.4335 | -122.2961 | 0.11902 | 0.10812 | -0.035942 | 0.052101 | 0.002454 | 0.10951 | 0.085583 | -0.026092 | 0.034174 | 0.14332 | 0.05072 | -0.10637 | 0.002454 | 0.041532 | -0.065533 | -0.021484 | 0.13558 | -0.008476 | 0.079567 | 0.02992 | 0.13698 | 0.11305 | 0.001374 | 0.06164 | 0.17079 | 0.078186 | -0.078899 | 0.02992 | 0.068998 | -0.038067 | 0.005982 | 0.03172 | 0.099707 | 0.048266 | 0.11625
1977.0938 | 122.5708 | -122.2366 | 0.086975 | 0.11269 | -0.035942 | 0.056679 | -0.002124 | 0.10036 | 0.076426 | -0.03067 | 0.034174 | 0.13874 | 0.036985 | -0.11094 | 0.002454 | 0.041532 | -0.070112 | -0.016906 | 0.14016 | -0.008476 | 0.084145 | 0.025342 | 0.12782 | 0.10389 | -0.003204 | 0.06164 | 0.16621 | 0.064451 | -0.083478 | 0.02992 | 0.068998 | -0.042646 | 0.01056 | 0.03172 | 0.10429 | 0.034531 | 0.1071
1978.8281 | 122.525 | -122.2595 | 0.10529 | 0.10812 | -0.040521 | 0.052101 | 0.002454 | 0.10493 | 0.076426 | -0.039826 | 0.029595 | 0.14332 | 0.05072 | -0.11094 | 0.01161 | 0.041532 | -0.065533 | -0.012328 | 0.13558 | -0.013055 | 0.079567 | 0.02992 | 0.1324 | 0.10389 | -0.01236 | 0.057061 | 0.17079 | 0.078186 | -0.083478 | 0.039076 | 0.068998 | -0.038067 | 0.015138 | 0.017985 | 0.095128 | 0.03911 | 0.11625
1980.5781 | 122.493 | -122.2824 | 0.11902 | 0.10812 | -0.026784 | 0.056679 | -0.002124 | 0.10951 | 0.081005 | -0.03067 | 0.029595 | 0.1479 | 0.055298 | -0.097207 | 0.01161 | 0.041532 | -0.065533 | -0.00775 | 0.13558 | 0.000682 | 0.084145 | 0.025342 | 0.13698 | 0.10847 | -0.003204 | 0.057061 | 0.17536 | 0.082764 | -0.069741 | 0.039076 | 0.068998 | -0.038067 | 0.019716 | 0.017985 | 0.095128 | 0.043688 | 0.12083
1982.2656 | 122.5388 | -122.2641 | 0.07782 | 0.11269 | -0.035942 | 0.065837 | -0.002124 | 0.10493 | 0.076426 | -0.03067 | 0.038752 | 0.13874 | 0.05072 | -0.11094 | 0.002454 | 0.032376 | -0.065533 | -0.00775 | 0.14016 | -0.008476 | 0.093303 | 0.025342 | 0.1324 | 0.10389 | -0.003204 | 0.066218 | 0.16621 | 0.078186 | -0.083478 | 0.02992 | 0.059842 | -0.038067 | 0.019716 | 0.036298 | 0.10428 | 0.048266 | 0.11625
1984 | 122.5525 | -122.2641 | 0.10071 | 0.11727 | -0.022205 | 0.056679 | 0.007033 | 0.10951 | 0.085583 | -0.026092 | 0.029595 | 0.13874 | 0.036985 | -0.10637 | 0.01161 | 0.041532 | -0.070112 | -0.00775 | 0.14474 | 0.005261 | 0.084145 | 0.034499 | 0.13698 | 0.11305 | 0.001374 | 0.057061 | 0.16621 | 0.064451 | -0.078899 | 0.039076 | 0.068998 | -0.042646 | 0.019716 | 0.017985 | 0.099707 | 0.025375 | 0.1071
1985.6719 | 122.4472 | -122.2778 | 0.10986 | 0.11727 | -0.026784 | 0.056679 | 0.002454 | 0.10951 | 0.081005 | -0.03067 | 0.038752 | 0.14332 | 0.046142 | -0.11094 | 0.007032 | 0.032376 | -0.070112 | -0.012328 | 0.14474 | 0.000682 | 0.084145 | 0.02992 | 0.13698 | 0.10847 | -0.003204 | 0.066218 | 0.17079 | 0.073608 | -0.083478 | 0.034498 | 0.059842 | -0.042646 | 0.015138 | 0.03172 | 0.10886 | 0.03911 | 0.11625
1987.4219 | 122.5296 | -122.2641 | 0.09613 | 0.11269 | -0.022205 | 0.047522 | 0.002454 | 0.10951 | 0.081005 | -0.03067 | 0.038752 | 0.14332 | 0.032407 | -0.10179 | 0.01161 | 0.036954 | -0.065533 | -0.016906 | 0.14016 | 0.005261 | 0.074988 | 0.02992 | 0.13698 | 0.10847 | -0.003204 | 0.066218 | 0.17079 | 0.059873 | -0.07432 | 0.039076 | 0.06442 | -0.038067 | 0.01056 | 0.027142 | 0.10428 | 0.020797 | 0.09794
1989.1094 | 122.5479 | -122.3099 | 0.10529 | 0.11727 | -0.035942 | 0.056679 | 0.002454 | 0.10493 | 0.081005 | -0.021514 | 0.034174 | 0.1479 | 0.046142 | -0.10637 | 0.007032 | 0.027798 | -0.070112 | -0.016906 | 0.14474 | -0.008476 | 0.084145 | 0.02992 | 0.1324 | 0.10847 | 0.005952 | 0.06164 | 0.17536 | 0.073608 | -0.078899 | 0.034498 | 0.055264 | -0.042646 | 0.01056 | 0.027142 | 0.10429 | 0.03911 | 0.11625
1990.8594 | 122.5388 | -122.2549 | 0.082397 | 0.11269 | -0.035942 | 0.052101 | 0.002454 | 0.10951 | 0.071848 | -0.026092 | 0.029595 | 0.14332 | 0.036985 | -0.11094 | 0.01161 | 0.036954 | -0.065533 | -0.016906 | 0.14016 | -0.008476 | 0.079567 | 0.02992 | 0.13698 | 0.099314 | 0.001374 | 0.057061 | 0.17079 | 0.064451 | -0.083478 | 0.039076 | 0.06442 | -0.038067 | 0.01056 | 0.017985 | 0.095128 | 0.025375 | 0.10252
1992.6094 | 122.5891 | -122.2687 | 0.068665 | 0.11269 | -0.026784 | 0.056679 | -0.002124 | 0.10493 | 0.071848 | -0.026092 | 0.034174 | 0.14332 | 0.046142 | -0.10637 | 0.002454 | 0.041532 | -0.060955 | -0.021484 | 0.14016 | 0.000682 | 0.084145 | 0.025342 | 0.1324 | 0.099314 | 0.001374 | 0.06164 | 0.17079 | 0.073608 | -0.078899 | 0.02992 | 0.068998 | -0.033489 | 0.005982 | 0.03172 | 0.095129 | 0.043688 | 0.1071
1994.375 | 122.5891 | -122.2778 | 0.086975 | 0.10812 | -0.035942 | 0.056679 | -0.002124 | 0.10951 | 0.076426 | -0.026092 | 0.029595 | 0.1479 | 0.055298 | -0.097207 | 0.002454 | 0.032376 | -0.065533 | -0.012328 | 0.13558 | -0.008476 | 0.084145 | 0.025342 | 0.13698 | 0.10389 | 0.001374 | 0.057061 | 0.17536 | 0.082764 | -0.069741 | 0.02992 | 0.059842 | -0.038067 | 0.015138 | 0.027141 | 0.095128 | 0.052844 | 0.12083
1996.0625 | 122.5342 | -122.2961 | 0.1236 | 0.11727 | -0.026784 | 0.056679 | 0.007033 | 0.10951 | 0.076426 | -0.026092 | 0.034174 | 0.1479 | 0.05072 | -0.10637 | 0.007032 | 0.041532 | -0.070112 | -0.012328 | 0.14474 | 0.000682 | 0.084145 | 0.034499 | 0.13698 | 0.10389 | 0.001374 | 0.06164 | 0.17536 | 0.078186 | -0.078899 | 0.034498 | 0.068998 | -0.042646 | 0.015138 | 0.027142 | 0.10429 | 0.043688 | 0.12083
1997.8125 | 122.4838 | -122.287 | 0.10529 | 0.12185 | -0.031363 | 0.056679 | 0.002454 | 0.10951 | 0.085583 | -0.021514 | 0.034174 | 0.1479 | 0.036985 | -0.10637 | 0.01161 | 0.041532 | -0.07469 | -0.016906 | 0.14932 | -0.003897 | 0.084145 | 0.02992 | 0.13698 | 0.11305 | 0.005952 | 0.06164 | 0.17536 | 0.064451 | -0.078899 | 0.039076 | 0.068998 | -0.047224 | 0.01056 | 0.022564 | 0.10886 | 0.025375 | 0.11167
1999.5625 | 122.4655 | -122.3007 | 0.1236 | 0.11269 | -0.026784 | 0.056679 | -0.002124 | 0.11409 | 0.081005 | -0.03067 | 0.034174 | 0.1479 | 0.032407 | -0.10637 | 0.01161 | 0.036954 | -0.070112 | -0.021484 | 0.14016 | 0.000682 | 0.084145 | 0.025342 | 0.14156 | 0.10847 | -0.003204 | 0.06164 | 0.17536 | 0.059873 | -0.078899 | 0.039076 | 0.06442 | -0.042646 | 0.005982 | 0.022564 | 0.10429 | 0.020797 | 0.10252
2001.2344 | 122.5708 | -122.2733 | 0.07782 | 0.11269 | -0.026784 | 0.061258 | 0.002454 | 0.10951 | 0.085583 | -0.03067 | 0.029595 | 0.14332 | 0.055298 | -0.10637 | 0.002454 | 0.032376 | -0.065533 | -0.016906 | 0.14016 | 0.000682 | 0.088724 | 0.02992 | 0.13698 | 0.11305 | -0.003204 | 0.057061 | 0.17079 | 0.082764 | -0.078899 | 0.02992 | 0.059842 | -0.038067 | 0.01056 | 0.027141 | 0.095128 | 0.052844 | 0.12083
2002.9688 | 122.4701 | -122.3373 | 0.12817 | 0.11269 | -0.031363 | 0.056679 | 0.002454 | 0.10951 | 0.076426 | -0.016936 | 0.034174 | 0.1479 | 0.046142 | -0.1201 | 0.002454 | 0.036954 | -0.065533 | -0.016906 | 0.14016 | -0.003897 | 0.084145 | 0.02992 | 0.13698 | 0.10389 | 0.01053 | 0.06164 | 0.17536 | 0.073608 | -0.092637 | 0.02992 | 0.06442 | -0.038067 | 0.01056 | 0.03172 | 0.099707 | 0.043688 | 0.11167
2004.7031 | 122.4976 | -122.2916 | 0.11444 | 0.10812 | -0.026784 | 0.052101 | 0.002454 | 0.10951 | 0.081005 | -0.026092 | 0.038752 | 0.1479 | 0.041563 | -0.10179 | 0.007032 | 0.041532 | -0.065533 | -0.016906 | 0.13558 | 0.000682 | 0.079567 | 0.02992 | 0.13698 | 0.10847 | 0.001374 | 0.066218 | 0.17536 | 0.069029 | -0.07432 | 0.034498 | 0.068998 | -0.038067 | 0.01056 | 0.03172 | 0.10428 | 0.034531 | 0.1071
2006.4531 | 122.6212 | -122.2824 | 0.07782 | 0.11727 | -0.035942 | 0.061258 | 0.002454 | 0.10036 | 0.081005 | -0.03067 | 0.038752 | 0.14332 | 0.046142 | -0.11094 | 0.002454 | 0.036954 | -0.07469 | -0.012328 | 0.14474 | -0.008476 | 0.088724 | 0.02992 | 0.12782 | 0.10847 | -0.003204 | 0.066218 | 0.17079 | 0.073608 | -0.083478 | 0.02992 | 0.06442 | -0.047224 | 0.015138 | 0.036298 | 0.11344 | 0.043688 | 0.12083
2008.125 | 122.5296 | -122.3053 | 0.11444 | 0.11269 | -0.026784 | 0.065837 | 0.002454 | 0.10951 | 0.076426 | -0.03067 | 0.034174 | 0.1479 | 0.046142 | -0.11094 | 0.007032 | 0.036954 | -0.070112 | -0.021484 | 0.14016 | 0.000682 | 0.093303 | 0.02992 | 0.13698 | 0.10389 | -0.003204 | 0.06164 | 0.17536 | 0.073608 | -0.083478 | 0.034498 | 0.06442 | -0.042646 | 0.005982 | 0.027142 | 0.10429 | 0.03911 | 0.11625
2009.875 | 122.5571 | -122.2961 | 0.086975 | 0.12643 | -0.031363 | 0.056679 | -0.002124 | 0.10951 | 0.071848 | -0.035248 | 0.034174 | 0.15248 | 0.055298 | -0.11094 | 0.007032 | 0.041532 | -0.070112 | -0.012328 | 0.1539 | -0.003897 | 0.084145 | 0.025342 | 0.13698 | 0.099314 | -0.007782 | 0.06164 | 0.17994 | 0.082764 | -0.083478 | 0.034498 | 0.068998 | -0.042646 | 0.015138 | 0.027142 | 0.10429 | 0.048266 | 0.12541
2011.5625 | 122.4564 | -122.3236 | 0.11444 | 0.11727 | -0.035942 | 0.056679 | 0.007033 | 0.10493 | 0.085583 | -0.03067 | 0.034174 | 0.13874 | 0.036985 | -0.11552 | 0.002454 | 0.032376 | -0.07469 | -0.016906 | 0.14474 | -0.008476 | 0.084145 | 0.034499 | 0.1324 | 0.11305 | -0.003204 | 0.06164 | 0.16621 | 0.064451 | -0.088057 | 0.02992 | 0.059842 | -0.047224 | 0.01056 | 0.03172 | 0.10886 | 0.034531 | 0.11167
2013.2344 | 122.5983 | -122.2733 | 0.07782 | 0.11269 | -0.026784 | 0.047522 | 0.007033 | 0.10493 | 0.071848 | -0.03067 | 0.047909 | 0.14332 | 0.05072 | -0.10637 | 0.002454 | 0.036954 | -0.060955 | -0.012328 | 0.14016 | 0.000682 | 0.074988 | 0.034499 | 0.1324 | 0.099314 | -0.003204 | 0.075375 | 0.17079 | 0.078186 | -0.078899 | 0.02992 | 0.06442 | -0.033489 | 0.015138 | 0.045455 | 0.10886 | 0.048266 | 0.11167
2014.9688 | 122.6028 | -122.2916 | 0.082397 | 0.11727 | -0.035942 | 0.056679 | 0.002454 | 0.10493 | 0.071848 | -0.026092 | 0.034174 | 0.14332 | 0.046142 | -0.10637 | 0.007032 | 0.036954 | -0.065533 | -0.016906 | 0.14474 | -0.008476 | 0.084145 | 0.02992 | 0.1324 | 0.099314 | 0.001374 | 0.06164 | 0.17079 | 0.073608 | -0.078899 | 0.034498 | 0.06442 | -0.038067 | 0.01056 | 0.027142 | 0.099707 | 0.03911 | 0.11167
2016.6562 | 122.4655 | -122.3282 | 0.1236 | 0.11727 | -0.031363 | 0.052101 | 0.007033 | 0.10493 | 0.076426 | -0.03067 | 0.038752 | 0.1479 | 0.041563 | -0.10637 | 0.01161 | 0.032376 | -0.07469 | -0.016906 | 0.14474 | -0.003897 | 0.079567 | 0.034499 | 0.1324 | 0.10389 | -0.003204 | 0.066218 | 0.17536 | 0.069029 | -0.078899 | 0.039076 | 0.059842 | -0.047224 | 0.01056 | 0.027142 | 0.11344 | 0.029953 | 0.11625
2018.4062 | 122.6028 | -122.3145 | 0.091553 | 0.10812 | -0.031363 | 0.052101 | -0.002124 | 0.10493 | 0.081005 | -0.035248 | 0.038752 | 0.14332 | 0.055298 | -0.10637 | 0.007032 | 0.041532 | -0.065533 | -0.012328 | 0.13558 | -0.003897 | 0.079567 | 0.025342 | 0.1324 | 0.10847 | -0.007782 | 0.066218 | 0.17079 | 0.082764 | -0.078899 | 0.034498 | 0.068998 | -0.038067 | 0.015138 | 0.03172 | 0.10428 | 0.048266 | 0.12083
2020.1406 | 122.6166 | -122.3145 | 0.091553 | 0.11727 | -0.035942 | 0.047522 | 0.002454 | 0.10951 | 0.076426 | -0.03067 | 0.034174 | 0.1479 | 0.05072 | -0.10179 | -0.002124 | 0.036954 | -0.065533 | -0.021484 | 0.14474 | -0.008476 | 0.074988 | 0.02992 | 0.13698 | 0.10389 | -0.003204 | 0.06164 | 0.17536 | 0.078186 | -0.07432 | 0.025342 | 0.06442 | -0.038067 | 0.005982 | 0.036298 | 0.099707 | 0.052844 | 0.11625
2021.8906 | 122.4838 | -122.3328 | 0.11444 | 0.12185 | -0.031363 | 0.056679 | 0.002454 | 0.10493 | 0.071848 | -0.026092 | 0.038752 | 0.14332 | 0.046142 | -0.10637 | 0.002454 | 0.027798 | -0.07469 | -0.016906 | 0.14932 | -0.003897 | 0.084145 | 0.02992 | 0.1324 | 0.099314 | 0.001374 | 0.066218 | 0.17079 | 0.073608 | -0.078899 | 0.02992 | 0.055264 | -0.047224 | 0.01056 | 0.036298 | 0.11344 | 0.043688 | 0.12083
2023.5781 | 122.5296 | -122.3328 | 0.11444 | 0.11727 | -0.026784 | 0.052101 | 0.002454 | 0.10951 | 0.076426 | -0.026092 | 0.029595 | 0.14332 | 0.046142 | -0.11094 | 0.007032 | 0.032376 | -0.065533 | -0.012328 | 0.14474 | 0.000682 | 0.079567 | 0.02992 | 0.13698 | 0.10389 | 0.001374 | 0.057061 | 0.17079 | 0.073608 | -0.083478 | 0.034498 | 0.059842 | -0.038067 | 0.015138 | 0.022563 | 0.095128 | 0.03911 | 0.11167
2025.3125 | 122.525 | -122.3328 | 0.10986 | 0.10812 | -0.026784 | 0.065837 | 0.002454 | 0.10493 | 0.071848 | -0.03067 | 0.038752 | 0.1479 | 0.055298 | -0.11094 | 0.007032 | 0.032376 | -0.065533 | -0.016906 | 0.13558 | 0.000682 | 0.093303 | 0.02992 | 0.1324 | 0.099314 | -0.003204 | 0.066218 | 0.17536 | 0.082764 | -0.083478 | 0.034498 | 0.059842 | -0.038067 | 0.01056 | 0.03172 | 0.10428 | 0.048266 | 0.12083
2027.0469 | 122.5845 | -122.3053 | 0.09613 | 0.11269 | -0.031363 | 0.056679 | 0.007033 | 0.11409 | 0.076426 | -0.026092 | 0.034174 | 0.15248 | 0.05072 | -0.10179 | 0.007032 | 0.036954 | -0.060955 | -0.016906 | 0.14016 | -0.003897 | 0.084145 | 0.034499 | 0.14156 | 0.10389 | 0.001374 | 0.06164 | 0.17994 | 0.078186 | -0.07432 | 0.034498 | 0.06442 | -0.033489 | 0.01056 | 0.027142 | 0.095129 | 0.043688 | 0.11167
2028.7969 | 122.5433 | -122.3282 | 0.09613 | 0.10812 | -0.026784 | 0.056679 | 0.002454 | 0.10951 | 0.076426 | -0.03067 | 0.038752 | 0.14332 | 0.036985 | -0.11552 | 0.002454 | 0.036954 | -0.070112 | -0.021484 | 0.13558 | 0.000682 | 0.084145 | 0.02992 | 0.13698 | 0.10389 | -0.003204 | 0.066218 | 0.17079 | 0.064451 | -0.088057 | 0.02992 | 0.06442 | -0.042646 | 0.005982 | 0.036298 | 0.10886 | 0.034531 | 0.1071
2030.4688 | 122.5983 | -122.3145 | 0.086975 | 0.11269 | -0.031363 | 0.056679 | 0.002454 | 0.10951 | 0.071848 | -0.03067 | 0.034174 | 0.1479 | 0.046142 | -0.11094 | 0.007032 | 0.036954 | -0.065533 | -0.012328 | 0.14016 | -0.003897 | 0.084145 | 0.02992 | 0.13698 | 0.099314 | -0.003204 | 0.06164 | 0.17536 | 0.073608 | -0.083478 | 0.034498 | 0.06442 | -0.038067 | 0.015138 | 0.027142 | 0.099707 | 0.03911 | 0.11167
2032.2031 | 122.5662 | -122.3236 | 0.10071 | 0.11269 | -0.035942 | 0.056679 | 0.002454 | 0.10493 | 0.076426 | -0.026092 | 0.034174 | 0.14332 | 0.041563 | -0.10179 | 0.002454 | 0.036954 | -0.070112 | -0.012328 | 0.14016 | -0.008476 | 0.084145 | 0.02992 | 0.1324 | 0.10389 | 0.001374 | 0.06164 | 0.17079 | 0.069029 | -0.07432 | 0.02992 | 0.06442 | -0.042646 | 0.015138 | 0.03172 | 0.10429 | 0.039109 | 0.11167
2033.9531 | 122.5754 | -122.319 | 0.09613 | 0.11269 | -0.026784 | 0.052101 | 0.002454 | 0.10036 | 0.081005 | -0.03067 | 0.038752 | 0.1479 | 0.05072 | -0.11094 | 0.007032 | 0.032376 | -0.065533 | -0.021484 | 0.14016 | 0.000682 | 0.079567 | 0.02992 | 0.12782 | 0.10847 | -0.003204 | 0.066218 | 0.17536 | 0.078186 | -0.083478 | 0.034498 | 0.059842 | -0.038067 | 0.005982 | 0.03172 | 0.10428 | 0.043688 | 0.11625
2035.625 | 122.5021 | -122.3511 | 0.13733 | 0.11269 | -0.022205 | 0.056679 | 0.007033 | 0.10493 | 0.081005 | -0.026092 | 0.038752 | 0.14332 | 0.036985 | -0.11552 | 0.016188 | 0.032376 | -0.070112 | -0.012328 | 0.14016 | 0.005261 | 0.084145 | 0.034499 | 0.1324 | 0.10847 | 0.001374 | 0.066218 | 0.17079 | 0.064451 | -0.088057 | 0.043654 | 0.059842 | -0.042646 | 0.015138 | 0.022564 | 0.10886 | 0.020797 | 0.1071
2037.3906 | 122.5754 | -122.3145 | 0.091553 | 0.11727 | -0.031363 | 0.047522 | 0.002454 | 0.10493 | 0.081005 | -0.03067 | 0.038752 | 0.14332 | 0.046142 | -0.10637 | 0.002454 | 0.032376 | -0.07469 | -0.016906 | 0.14474 | -0.003897 | 0.074988 | 0.02992 | 0.1324 | 0.10847 | -0.003204 | 0.066218 | 0.17079 | 0.073608 | -0.078899 | 0.02992 | 0.059842 | -0.047224 | 0.01056 | 0.036298 | 0.11344 | 0.043688 | 0.12083
2039.0625 | 122.5067 | -122.374 | 0.11902 | 0.11269 | -0.040521 | 0.047522 | 0.007033 | 0.10493 | 0.081005 | -0.026092 | 0.038752 | 0.14332 | 0.041563 | -0.10637 | 0.007032 | 0.036954 | -0.07469 | -0.012328 | 0.14016 | -0.013055 | 0.074988 | 0.034499 | 0.1324 | 0.10847 | 0.001374 | 0.066218 | 0.17079 | 0.069029 | -0.078899 | 0.034498 | 0.06442 | -0.047224 | 0.015138 | 0.03172 | 0.11344 | 0.034531 | 0.11625
2040.7969 | 122.5571 | -122.3602 | 0.13275 | 0.12185 | -0.031363 | 0.056679 | 0.002454 | 0.10951 | 0.076426 | -0.035248 | 0.034174 | 0.14332 | 0.046142 | -0.11094 | 0.002454 | 0.032376 | -0.065533 | -0.016906 | 0.14932 | -0.003897 | 0.084145 | 0.02992 | 0.13698 | 0.10389 | -0.007782 | 0.06164 | 0.17079 | 0.073608 | -0.083478 | 0.02992 | 0.059842 | -0.038067 | 0.01056 | 0.03172 | 0.099707 | 0.043688 | 0.11167
2042.5 | 122.5845 | -122.3373 | 0.091553 | 0.12185 | -0.0451 | 0.052101 | 0.002454 | 0.10493 | 0.076426 | -0.026092 | 0.038752 | 0.15248 | 0.041563 | -0.10179 | 0.01161 | 0.036954 | -0.070112 | -0.012328 | 0.14932 | -0.017634 | 0.079567 | 0.02992 | 0.1324 | 0.10389 | 0.001374 | 0.066218 | 0.17994 | 0.069029 | -0.07432 | 0.039076 | 0.06442 | -0.042646 | 0.015138 | 0.027142 | 0.10886 | 0.029953 | 0.11167
2044.25 | 122.6395 | -122.3282 | 0.09613 | 0.11269 | -0.022205 | 0.056679 | 0.007033 | 0.10493 | 0.085583 | -0.035248 | 0.038752 | 0.14332 | 0.05072 | -0.11552 | 0.007032 | 0.041532 | -0.065533 | -0.012328 | 0.14016 | 0.005261 | 0.084145 | 0.034499 | 0.1324 | 0.11305 | -0.007782 | 0.066218 | 0.17079 | 0.078186 | -0.088057 | 0.034498 | 0.068998 | -0.038067 | 0.015138 | 0.03172 | 0.10428 | 0.043688 | 0.11625
2046 | 122.5204 | -122.374 | 0.11444 | 0.11269 | -0.026784 | 0.061258 | 0.007033 | 0.10951 | 0.085583 | -0.026092 | 0.038752 | 0.14332 | 0.046142 | -0.10637 | 0.007032 | 0.041532 | -0.065533 | -0.00775 | 0.14016 | 0.000682 | 0.088724 | 0.034499 | 0.13698 | 0.11305 | 0.001374 | 0.066218 | 0.17079 | 0.073608 | -0.078899 | 0.034498 | 0.068998 | -0.038067 | 0.019716 | 0.03172 | 0.10428 | 0.03911 | 0.11167
2047.6719 | 122.5891 | -122.3557 | 0.09613 | 0.11269 | -0.035942 | 0.052101 | 0.007033 | 0.10493 | 0.081005 | -0.026092 | 0.034174 | 0.1479 | 0.041563 | -0.10179 | 0.002454 | 0.041532 | -0.060955 | -0.021484 | 0.14016 | -0.008476 | 0.079567 | 0.034499 | 0.1324 | 0.10847 | 0.001374 | 0.06164 | 0.17536 | 0.069029 | -0.07432 | 0.02992 | 0.068998 | -0.033489 | 0.005982 | 0.03172 | 0.095129 | 0.039109 | 0.10252
2049.4219 | 122.5891 | -122.3419 | 0.10071 | 0.11269 | -0.035942 | 0.056679 | -0.002124 | 0.10493 | 0.085583 | -0.026092 | 0.034174 | 0.1479 | 0.041563 | -0.1201 | 0.01161 | 0.036954 | -0.065533 | -0.00775 | 0.14016 | -0.008476 | 0.084145 | 0.025342 | 0.1324 | 0.11305 | 0.001374 | 0.06164 | 0.17536 | 0.069029 | -0.092637 | 0.039076 | 0.06442 | -0.038067 | 0.019716 | 0.022564 | 0.099707 | 0.029953 | 0.1071
2051.1562 | 122.5159 | -122.3877 | 0.13733 | 0.11727 | -0.026784 | 0.056679 | 0.007033 | 0.11409 | 0.076426 | -0.021514 | 0.038752 | 0.14332 | 0.046142 | -0.11094 | -0.002124 | 0.036954 | -0.07469 | -0.016906 | 0.14474 | 0.000682 | 0.084145 | 0.034499 | 0.14156 | 0.10389 | 0.005952 | 0.066218 | 0.17079 | 0.073608 | -0.083478 | 0.025342 | 0.06442 | -0.047224 | 0.01056 | 0.040876 | 0.11344 | 0.048266 | 0.12083
2052.9062 | 122.6212 | -122.3373 | 0.082397 | 0.11269 | -0.031363 | 0.061258 | 0.002454 | 0.10493 | 0.081005 | -0.026092 | 0.038752 | 0.13874 | 0.041563 | -0.11094 | 0.007032 | 0.036954 | -0.065533 | -0.016906 | 0.14016 | -0.003897 | 0.088724 | 0.02992 | 0.1324 | 0.10847 | 0.001374 | 0.066218 | 0.16621 | 0.069029 | -0.083478 | 0.034498 | 0.06442 | -0.038067 | 0.01056 | 0.03172 | 0.10428 | 0.034531 | 0.1071
2054.5781 | 122.5662 | -122.3557 | 0.1236 | 0.11269 | -0.031363 | 0.056679 | 0.002454 | 0.11867 | 0.076426 | -0.026092 | 0.038752 | 0.15248 | 0.046142 | -0.10637 | 0.007032 | 0.036954 | -0.065533 | -0.016906 | 0.14016 | -0.003897 | 0.084145 | 0.02992 | 0.14613 | 0.10389 | 0.001374 | 0.066218 | 0.17994 | 0.073608 | -0.078899 | 0.034498 | 0.06442 | -0.038067 | 0.01056 | 0.03172 | 0.10428 | 0.03911 | 0.11167
2056.3281 | 122.6349 | -122.3099 | 0.07782 | 0.11727 | -0.031363 | 0.061258 | 0.002454 | 0.10493 | 0.076426 | -0.021514 | 0.034174 | 0.1479 | 0.055298 | -0.10637 | 0.007032 | 0.036954 | -0.065533 | -0.00775 | 0.14474 | -0.003897 | 0.088724 | 0.02992 | 0.1324 | 0.10389 | 0.005952 | 0.06164 | 0.17536 | 0.082764 | -0.078899 | 0.034498 | 0.06442 | -0.038067 | 0.019716 | 0.027142 | 0.099707 | 0.048266 | 0.12083
2058.0781 | 122.6486 | -122.3419 | 0.086975 | 0.11727 | -0.026784 | 0.052101 | 0.002454 | 0.10951 | 0.076426 | -0.03067 | 0.034174 | 0.15248 | 0.05072 | -0.11094 | 0.007032 | 0.032376 | -0.07469 | -0.012328 | 0.14474 | 0.000682 | 0.079567 | 0.02992 | 0.13698 | 0.10389 | -0.003204 | 0.06164 | 0.17994 | 0.078186 | -0.083478 | 0.034498 | 0.059842 | -0.047224 | 0.015138 | 0.027142 | 0.10886 | 0.043688 | 0.12541
2059.8281 | 122.5159 | -122.3465 | 0.10529 | 0.10812 | -0.031363 | 0.056679 | 0.007033 | 0.10951 | 0.081005 | -0.03067 | 0.034174 | 0.14332 | 0.046142 | -0.11094 | 0.007032 | 0.041532 | -0.070112 | -0.021484 | 0.13558 | -0.003897 | 0.084145 | 0.034499 | 0.13698 | 0.10847 | -0.003204 | 0.06164 | 0.17079 | 0.073608 | -0.083478 | 0.034498 | 0.068998 | -0.042646 | 0.005982 | 0.027142 | 0.10429 | 0.03911 | 0.11625
2061.5156 | 122.5708 | -122.3557 | 0.1236 | 0.11269 | -0.035942 | 0.056679 | 0.002454 | 0.10951 | 0.076426 | -0.021514 | 0.038752 | 0.14332 | 0.055298 | -0.10637 | 0.01161 | 0.036954 | -0.065533 | -0.012328 | 0.14016 | -0.008476 | 0.084145 | 0.02992 | 0.13698 | 0.10389 | 0.005952 | 0.066218 | 0.17079 | 0.082764 | -0.078899 | 0.039076 | 0.06442 | -0.038067 | 0.015138 | 0.027142 | 0.10428 | 0.043688 | 0.12083
2063.2656 | 122.5616 | -122.3602 | 0.11444 | 0.11727 | -0.026784 | 0.056679 | -0.002124 | 0.10951 | 0.076426 | -0.03067 | 0.038752 | 0.14332 | 0.046142 | -0.10179 | 0.007032 | 0.032376 | -0.065533 | -0.021484 | 0.14474 | 0.000682 | 0.084145 | 0.025342 | 0.13698 | 0.10389 | -0.003204 | 0.066218 | 0.17079 | 0.073608 | -0.07432 | 0.034498 | 0.059842 | -0.038067 | 0.005982 | 0.03172 | 0.10428 | 0.03911 | 0.11167
2065.0156 | 122.5983 | -122.3511 | 0.09613 | 0.11269 | -0.031363 | 0.052101 | 0.002454 | 0.10493 | 0.081005 | -0.035248 | 0.038752 | 0.1479 | 0.055298 | -0.10179 | 0.002454 | 0.036954 | -0.065533 | -0.012328 | 0.14016 | -0.003897 | 0.079567 | 0.02992 | 0.1324 | 0.10847 | -0.007782 | 0.066218 | 0.17536 | 0.082764 | -0.07432 | 0.02992 | 0.06442 | -0.038067 | 0.015138 | 0.036298 | 0.10428 | 0.052844 | 0.12083
2066.7031 | 122.6395 | -122.3465 | 0.091553 | 0.11269 | -0.026784 | 0.056679 | 0.002454 | 0.11409 | 0.085583 | -0.026092 | 0.043331 | 0.14332 | 0.05072 | -0.11094 | 0.002454 | 0.032376 | -0.070112 | -0.00775 | 0.14016 | 0.000682 | 0.084145 | 0.02992 | 0.14156 | 0.11305 | 0.001374 | 0.070797 | 0.17079 | 0.078186 | -0.083478 | 0.02992 | 0.059842 | -0.042646 | 0.019716 | 0.040877 | 0.11344 | 0.048266 | 0.12083
2068.4531 | 122.5021 | -122.3877 | 0.10071 | 0.11727 | -0.026784 | 0.052101 | -0.006703 | 0.10493 | 0.090161 | -0.021514 | 0.034174 | 0.14332 | 0.046142 | -0.11094 | 0.002454 | 0.041532 | -0.060955 | -0.012328 | 0.14474 | 0.000682 | 0.079567 | 0.020763 | 0.1324 | 0.11763 | 0.005952 | 0.06164 | 0.17079 | 0.073608 | -0.083478 | 0.02992 | 0.068998 | -0.033489 | 0.015138 | 0.03172 | 0.095129 | 0.043688 | 0.1071
2070.125 | 122.644 | -122.3511 | 0.086975 | 0.11269 | -0.026784 | 0.056679 | 0.007033 | 0.11409 | 0.081005 | -0.026092 | 0.034174 | 0.15248 | 0.055298 | -0.10637 | 0.007032 | 0.041532 | -0.065533 | -0.012328 | 0.14016 | 0.000682 | 0.084145 | 0.034499 | 0.14156 | 0.10847 | 0.001374 | 0.06164 | 0.17994 | 0.082764 | -0.078899 | 0.034498 | 0.068998 | -0.038067 | 0.015138 | 0.027142 | 0.099707 | 0.048266 | 0.12083
2071.8594 | 122.612 | -122.3557 | 0.10071 | 0.11269 | -0.040521 | 0.056679 | 0.002454 | 0.11409 | 0.081005 | -0.026092 | 0.038752 | 0.1479 | 0.046142 | -0.11094 | 0.002454 | 0.036954 | -0.070112 | -0.012328 | 0.14016 | -0.013055 | 0.084145 | 0.02992 | 0.14156 | 0.10847 | 0.001374 | 0.066218 | 0.17536 | 0.073608 | -0.083478 | 0.02992 | 0.06442 | -0.042646 | 0.015138 | 0.036298 | 0.10886 | 0.043688 | 0.11625
2073.6094 | 122.612 | -122.3557 | 0.10529 | 0.11727 | -0.026784 | 0.056679 | 0.007033 | 0.10493 | 0.076426 | -0.026092 | 0.043331 | 0.1479 | 0.055298 | -0.10637 | 0.007032 | 0.032376 | -0.070112 | -0.012328 | 0.14474 | 0.000682 | 0.084145 | 0.034499 | 0.1324 | 0.10389 | 0.001374 | 0.070797 | 0.17536 | 0.082764 | -0.078899 | 0.034498 | 0.059842 | -0.042646 | 0.015138 | 0.036299 | 0.11344 | 0.048266 | 0.12541
2075.3438 | 122.5571 | -122.3831 | 0.09613 | 0.11269 | -0.031363 | 0.061258 | 0.007033 | 0.10951 | 0.085583 | -0.026092 | 0.038752 | 0.1479 | 0.05072 | -0.11552 | 0.007032 | 0.027798 | -0.07469 | -0.016906 | 0.14016 | -0.003897 | 0.088724 | 0.034499 | 0.13698 | 0.11305 | 0.001374 | 0.066218 | 0.17536 | 0.078186 | -0.088057 | 0.034498 | 0.055264 | -0.047224 | 0.01056 | 0.03172 | 0.11344 | 0.043688 | 0.12541
2077.0938 | 122.6669 | -122.3602 | 0.082397 | 0.11727 | -0.031363 | 0.056679 | 0.002454 | 0.10493 | 0.076426 | -0.03067 | 0.034174 | 0.14332 | 0.046142 | -0.10179 | 0.01161 | 0.036954 | -0.065533 | -0.012328 | 0.14474 | -0.003897 | 0.084145 | 0.02992 | 0.1324 | 0.10389 | -0.003204 | 0.06164 | 0.17079 | 0.073608 | -0.07432 | 0.039076 | 0.06442 | -0.038067 | 0.015138 | 0.022564 | 0.099707 | 0.034532 | 0.11167
2078.7812 | 122.6028 | -122.3694 | 0.11444 | 0.11727 | -0.026784 | 0.056679 | 0.002454 | 0.10951 | 0.081005 | -0.03067 | 0.034174 | 0.14332 | 0.055298 | -0.10637 | 0.007032 | 0.036954 | -0.070112 | -0.012328 | 0.14474 | 0.000682 | 0.084145 | 0.02992 | 0.13698 | 0.10847 | -0.003204 | 0.06164 | 0.17079 | 0.082764 | -0.078899 | 0.034498 | 0.06442 | -0.042646 | 0.015138 | 0.027142 | 0.10429 | 0.048266 | 0.12541
2080.5312 | 122.6852 | -122.374 | 0.073242 | 0.11269 | -0.035942 | 0.052101 | 0.002454 | 0.10951 | 0.076426 | -0.021514 | 0.038752 | 0.14332 | 0.046142 | -0.10179 | 0.007032 | 0.036954 | -0.07469 | -0.012328 | 0.14016 | -0.008476 | 0.079567 | 0.02992 | 0.13698 | 0.10389 | 0.005952 | 0.066218 | 0.17079 | 0.073608 | -0.07432 | 0.034498 | 0.06442 | -0.047224 | 0.015138 | 0.03172 | 0.11344 | 0.03911 | 0.12083
2082.2656 | 122.612 | -122.374 | 0.10071 | 0.10812 | -0.035942 | 0.056679 | 0.002454 | 0.10951 | 0.071848 | -0.03067 | 0.043331 | 0.1479 | 0.055298 | -0.10179 | -0.006702 | 0.036954 | -0.070112 | -0.012328 | 0.13558 | -0.008476 | 0.084145 | 0.02992 | 0.13698 | 0.099314 | -0.003204 | 0.070797 | 0.17536 | 0.082764 | -0.07432 | 0.020764 | 0.06442 | -0.042646 | 0.015138 | 0.050033 | 0.11344 | 0.062 | 0.12541
2083.9375 | 122.6395 | -122.3511 | 0.086975 | 0.11269 | -0.031363 | 0.052101 | 0.002454 | 0.10493 | 0.071848 | -0.026092 | 0.034174 | 0.15248 | 0.055298 | -0.10179 | 0.01161 | 0.041532 | -0.065533 | -0.016906 | 0.14016 | -0.003897 | 0.079567 | 0.02992 | 0.1324 | 0.099314 | 0.001374 | 0.06164 | 0.17994 | 0.082764 | -0.07432 | 0.039076 | 0.068998 | -0.038067 | 0.01056 | 0.022564 | 0.099707 | 0.043688 | 0.12083
2085.6875 | 122.5479 | -122.3969 | 0.1236 | 0.11727 | -0.031363 | 0.056679 | -0.002124 | 0.10493 | 0.081005 | -0.021514 | 0.034174 | 0.14332 | 0.046142 | -0.10637 | 0.002454 | 0.036954 | -0.065533 | -0.012328 | 0.14474 | -0.003897 | 0.084145 | 0.025342 | 0.1324 | 0.10847 | 0.005952 | 0.06164 | 0.17079 | 0.073608 | -0.078899 | 0.02992 | 0.06442 | -0.038067 | 0.015138 | 0.03172 | 0.099707 | 0.043688 | 0.11167
2087.4531 | 122.5708 | -122.3923 | 0.1236 | 0.11727 | -0.026784 | 0.061258 | -0.002124 | 0.10951 | 0.076426 | -0.035248 | 0.034174 | 0.14332 | 0.041563 | -0.10637 | 0.007032 | 0.032376 | -0.065533 | -0.016906 | 0.14474 | 0.000682 | 0.088724 | 0.025342 | 0.13698 | 0.10389 | -0.007782 | 0.06164 | 0.17079 | 0.069029 | -0.078899 | 0.034498 | 0.059842 | -0.038067 | 0.01056 | 0.027142 | 0.099707 | 0.034531 | 0.1071
2089.125 | 122.5433 | -122.4197 | 0.13275 | 0.11269 | -0.031363 | 0.056679 | 0.002454 | 0.10493 | 0.085583 | -0.035248 | 0.029595 | 0.15248 | 0.041563 | -0.11094 | 0.002454 | 0.036954 | -0.070112 | -0.026063 | 0.14016 | -0.003897 | 0.084145 | 0.02992 | 0.1324 | 0.11305 | -0.007782 | 0.057061 | 0.17994 | 0.069029 | -0.083478 | 0.02992 | 0.06442 | -0.042646 | 0.001403 | 0.027141 | 0.099707 | 0.039109 | 0.11167
2090.875 | 122.612 | -122.3877 | 0.09613 | 0.11727 | -0.026784 | 0.052101 | 0.007033 | 0.10951 | 0.081005 | -0.035248 | 0.029595 | 0.13874 | 0.05072 | -0.10179 | -0.002124 | 0.032376 | -0.070112 | -0.016906 | 0.14474 | 0.000682 | 0.079567 | 0.034499 | 0.13698 | 0.10847 | -0.007782 | 0.057061 | 0.16621 | 0.078186 | -0.07432 | 0.025342 | 0.059842 | -0.042646 | 0.01056 | 0.031719 | 0.099707 | 0.052844 | 0.12083
2092.625 | 122.5937 | -122.3602 | 0.10986 | 0.11727 | -0.031363 | 0.061258 | 0.007033 | 0.10493 | 0.076426 | -0.026092 | 0.034174 | 0.1479 | 0.055298 | -0.10637 | 0.007032 | 0.032376 | -0.065533 | -0.016906 | 0.14474 | -0.003897 | 0.088724 | 0.034499 | 0.1324 | 0.10389 | 0.001374 | 0.06164 | 0.17536 | 0.082764 | -0.078899 | 0.034498 | 0.059842 | -0.038067 | 0.01056 | 0.027142 | 0.099707 | 0.048266 | 0.12083
2094.3594 | 122.5433 | -122.3877 | 0.13275 | 0.11269 | -0.031363 | 0.056679 | 0.002454 | 0.10036 | 0.081005 | -0.03067 | 0.034174 | 0.15248 | 0.046142 | -0.10637 | 0.002454 | 0.041532 | -0.07469 | -0.016906 | 0.14016 | -0.003897 | 0.084145 | 0.02992 | 0.12782 | 0.10847 | -0.003204 | 0.06164 | 0.17994 | 0.073608 | -0.078899 | 0.02992 | 0.068998 | -0.047224 | 0.01056 | 0.03172 | 0.10886 | 0.043688 | 0.12083
2096.0938 | 122.6578 | -122.3694 | 0.07782 | 0.11727 | -0.026784 | 0.056679 | 0.002454 | 0.12325 | 0.085583 | -0.026092 | 0.034174 | 0.1479 | 0.041563 | -0.11094 | 0.007032 | 0.036954 | -0.060955 | -0.00775 | 0.14474 | 0.000682 | 0.084145 | 0.02992 | 0.15071 | 0.11305 | 0.001374 | 0.06164 | 0.17536 | 0.069029 | -0.083478 | 0.034498 | 0.06442 | -0.033489 | 0.019716 | 0.027142 | 0.095129 | 0.034531 | 0.10252
2097.8594 | 122.6761 | -122.3694 | 0.086975 | 0.11269 | -0.026784 | 0.056679 | 0.007033 | 0.10951 | 0.076426 | -0.021514 | 0.038752 | 0.15248 | 0.046142 | -0.11552 | 0.002454 | 0.032376 | -0.060955 | -0.016906 | 0.14016 | 0.000682 | 0.084145 | 0.034499 | 0.13698 | 0.10389 | 0.005952 | 0.066218 | 0.17994 | 0.073608 | -0.088057 | 0.02992 | 0.059842 | -0.033489 | 0.01056 | 0.036298 | 0.099707 | 0.043688 | 0.1071
2099.5469 | 122.6624 | -122.406 | 0.086975 | 0.12185 | -0.031363 | 0.056679 | -0.002124 | 0.10493 | 0.071848 | -0.026092 | 0.029595 | 0.13874 | 0.046142 | -0.10179 | 0.002454 | 0.036954 | -0.065533 | -0.00775 | 0.14932 | -0.003897 | 0.084145 | 0.025342 | 0.1324 | 0.099314 | 0.001374 | 0.057061 | 0.16621 | 0.073608 | -0.07432 | 0.02992 | 0.06442 | -0.038067 | 0.019716 | 0.027141 | 0.095128 | 0.043688 | 0.11167
2101.2969 | 122.5662 | -122.406 | 0.11444 | 0.11269 | -0.035942 | 0.052101 | 0.002454 | 0.10036 | 0.076426 | -0.03067 | 0.034174 | 0.1479 | 0.041563 | -0.11552 | 0.007032 | 0.036954 | -0.070112 | -0.016906 | 0.14016 | -0.008476 | 0.079567 | 0.02992 | 0.12782 | 0.10389 | -0.003204 | 0.06164 | 0.17536 | 0.069029 | -0.088057 | 0.034498 | 0.06442 | -0.042646 | 0.01056 | 0.027142 | 0.10429 | 0.034531 | 0.11167
2103.0312 | 122.6486 | -122.374 | 0.086975 | 0.11269 | -0.031363 | 0.047522 | 0.002454 | 0.10951 | 0.076426 | -0.026092 | 0.034174 | 0.14332 | 0.046142 | -0.11094 | 0.002454 | 0.036954 | -0.070112 | -0.012328 | 0.14016 | -0.003897 | 0.074988 | 0.02992 | 0.13698 | 0.10389 | 0.001374 | 0.06164 | 0.17079 | 0.073608 | -0.083478 | 0.02992 | 0.06442 | -0.042646 | 0.015138 | 0.03172 | 0.10429 | 0.043688 | 0.11625
2104.7031 | 122.6532 | -122.3511 | 0.10071 | 0.11269 | -0.031363 | 0.061258 | 0.007033 | 0.10493 | 0.076426 | -0.035248 | 0.034174 | 0.14332 | 0.046142 | -0.10637 | 0.002454 | 0.036954 | -0.065533 | -0.016906 | 0.14016 | -0.003897 | 0.088724 | 0.034499 | 0.1324 | 0.10389 | -0.007782 | 0.06164 | 0.17079 | 0.073608 | -0.078899 | 0.02992 | 0.06442 | -0.038067 | 0.01056 | 0.03172 | 0.099707 | 0.043688 | 0.11167
2106.4531 | 122.612 | -122.4243 | 0.1236 | 0.11269 | -0.026784 | 0.061258 | -0.002124 | 0.11409 | 0.081005 | -0.03067 | 0.038752 | 0.1479 | 0.046142 | -0.10637 | 0.007032 | 0.041532 | -0.060955 | -0.00775 | 0.14016 | 0.000682 | 0.088724 | 0.025342 | 0.14156 | 0.10847 | -0.003204 | 0.066218 | 0.17536 | 0.073608 | -0.078899 | 0.034498 | 0.068998 | -0.033489 | 0.019716 | 0.03172 | 0.099707 | 0.03911 | 0.1071
2108.2031 | 122.644 | -122.3694 | 0.10529 | 0.10812 | -0.026784 | 0.047522 | -0.002124 | 0.10951 | 0.081005 | -0.03067 | 0.034174 | 0.15706 | 0.046142 | -0.11094 | 0.01161 | 0.041532 | -0.070112 | -0.016906 | 0.13558 | 0.000682 | 0.074988 | 0.025342 | 0.13698 | 0.10847 | -0.003204 | 0.06164 | 0.18452 | 0.073608 | -0.083478 | 0.039076 | 0.068998 | -0.042646 | 0.01056 | 0.022564 | 0.10429 | 0.034532 | 0.11625
2109.8906 | 122.7173 | -122.3831 | 0.086975 | 0.11727 | -0.026784 | 0.061258 | 0.002454 | 0.11409 | 0.081005 | -0.026092 | 0.034174 | 0.15248 | 0.046142 | -0.10637 | 0.007032 | 0.036954 | -0.070112 | -0.016906 | 0.14474 | 0.000682 | 0.088724 | 0.02992 | 0.14156 | 0.10847 | 0.001374 | 0.06164 | 0.17994 | 0.073608 | -0.078899 | 0.034498 | 0.06442 | -0.042646 | 0.01056 | 0.027142 | 0.10429 | 0.03911 | 0.11625
2111.625 | 122.6898 | -122.3557 | 0.086975 | 0.10812 | -0.026784 | 0.056679 | 0.007033 | 0.10951 | 0.081005 | -0.026092 | 0.038752 | 0.13874 | 0.041563 | -0.11094 | 0.016188 | 0.027798 | -0.070112 | -0.012328 | 0.13558 | 0.000682 | 0.084145 | 0.034499 | 0.13698 | 0.10847 | 0.001374 | 0.066218 | 0.16621 | 0.069029 | -0.083478 | 0.043654 | 0.055264 | -0.042646 | 0.015138 | 0.022564 | 0.10886 | 0.025375 | 0.11167
2113.375 | 122.7081 | -122.3694 | 0.07782 | 0.10812 | -0.026784 | 0.052101 | -0.006703 | 0.11409 | 0.076426 | -0.035248 | 0.038752 | 0.1479 | 0.046142 | -0.10637 | 0.002454 | 0.041532 | -0.07469 | -0.016906 | 0.13558 | 0.000682 | 0.079567 | 0.020763 | 0.14156 | 0.10389 | -0.007782 | 0.066218 | 0.17536 | 0.073608 | -0.078899 | 0.02992 | 0.068998 | -0.047224 | 0.01056 | 0.036298 | 0.11344 | 0.043688 | 0.12083
2115.0625 | 122.6532 | -122.3831 | 0.09613 | 0.12185 | -0.026784 | 0.061258 | 0.002454 | 0.10951 | 0.071848 | -0.03067 | 0.034174 | 0.14332 | 0.046142 | -0.11094 | 0.002454 | 0.036954 | -0.07469 | -0.016906 | 0.14932 | 0.000682 | 0.088724 | 0.02992 | 0.13698 | 0.099314 | -0.003204 | 0.06164 | 0.17079 | 0.073608 | -0.083478 | 0.02992 | 0.06442 | -0.047224 | 0.01056 | 0.03172 | 0.10886 | 0.043688 | 0.12083
2116.8125 | 122.5571 | -122.4106 | 0.11902 | 0.11269 | -0.026784 | 0.056679 | 0.007033 | 0.11409 | 0.081005 | -0.026092 | 0.038752 | 0.1479 | 0.05072 | -0.10637 | 0.002454 | 0.032376 | -0.065533 | -0.012328 | 0.14016 | 0.000682 | 0.084145 | 0.034499 | 0.14156 | 0.10847 | 0.001374 | 0.066218 | 0.17536 | 0.078186 | -0.078899 | 0.02992 | 0.059842 | -0.038067 | 0.015138 | 0.036298 | 0.10428 | 0.048266 | 0.11625
2118.5625 | 122.612 | -122.4243 | 0.12817 | 0.10812 | -0.026784 | 0.056679 | 0.002454 | 0.10951 | 0.076426 | -0.021514 | 0.038752 | 0.14332 | 0.046142 | -0.11094 | 0.007032 | 0.027798 | -0.065533 | -0.012328 | 0.13558 | 0.000682 | 0.084145 | 0.02992 | 0.13698 | 0.10389 | 0.005952 | 0.066218 | 0.17079 | 0.073608 | -0.083478 | 0.034498 | 0.055264 | -0.038067 | 0.015138 | 0.03172 | 0.10428 | 0.03911 | 0.11167
2120.2969 | 122.5983 | -122.4197 | 0.09613 | 0.11269 | -0.031363 | 0.052101 | 0.007033 | 0.10493 | 0.076426 | -0.026092 | 0.034174 | 0.1479 | 0.046142 | -0.097207 | 0.007032 | 0.032376 | -0.065533 | -0.016906 | 0.14016 | -0.003897 | 0.079567 | 0.034499 | 0.1324 | 0.10389 | 0.001374 | 0.06164 | 0.17536 | 0.073608 | -0.069741 | 0.034498 | 0.059842 | -0.038067 | 0.01056 | 0.027142 | 0.099707 | 0.03911 | 0.11167
2122.0312 | 122.6624 | -122.406 | 0.086975 | 0.11269 | -0.026784 | 0.056679 | 0.002454 | 0.10493 | 0.071848 | -0.026092 | 0.034174 | 0.1479 | 0.05072 | -0.10179 | 0.007032 | 0.036954 | -0.060955 | -0.00775 | 0.14016 | 0.000682 | 0.084145 | 0.02992 | 0.1324 | 0.099314 | 0.001374 | 0.06164 | 0.17536 | 0.078186 | -0.07432 | 0.034498 | 0.06442 | -0.033489 | 0.019716 | 0.027142 | 0.095129 | 0.043688 | 0.11167
2123.7188 | 122.6624 | -122.3923 | 0.086975 | 0.10812 | -0.031363 | 0.061258 | -0.002124 | 0.10493 | 0.081005 | -0.021514 | 0.038752 | 0.1479 | 0.055298 | -0.10637 | 0.007032 | 0.041532 | -0.060955 | -0.016906 | 0.13558 | -0.003897 | 0.088724 | 0.025342 | 0.1324 | 0.10847 | 0.005952 | 0.066218 | 0.17536 | 0.082764 | -0.078899 | 0.034498 | 0.068998 | -0.033489 | 0.01056 | 0.03172 | 0.099707 | 0.048266 | 0.11625
2125.4531 | 122.7081 | -122.3831 | 0.091553 | 0.10812 | -0.035942 | 0.056679 | 0.002454 | 0.10493 | 0.071848 | -0.021514 | 0.034174 | 0.14332 | 0.05072 | -0.10637 | 0.007032 | 0.032376 | -0.07469 | -0.016906 | 0.13558 | -0.008476 | 0.084145 | 0.02992 | 0.1324 | 0.099314 | 0.005952 | 0.06164 | 0.17079 | 0.078186 | -0.078899 | 0.034498 | 0.059842 | -0.047224 | 0.01056 | 0.027142 | 0.10886 | 0.043688 | 0.12541
2127.1875 | 122.5662 | -122.4518 | 0.12817 | 0.11727 | -0.031363 | 0.056679 | 0.002454 | 0.10951 | 0.085583 | -0.026092 | 0.034174 | 0.1479 | 0.055298 | -0.10637 | 0.002454 | 0.036954 | -0.065533 | -0.016906 | 0.14474 | -0.003897 | 0.084145 | 0.02992 | 0.13698 | 0.11305 | 0.001374 | 0.06164 | 0.17536 | 0.082764 | -0.078899 | 0.02992 | 0.06442 | -0.038067 | 0.01056 | 0.03172 | 0.099707 | 0.052844 | 0.12083
2128.875 | 122.5937 | -122.4472 | 0.11444 | 0.10812 | -0.026784 | 0.056679 | 0.002454 | 0.11409 | 0.081005 | -0.035248 | 0.043331 | 0.14332 | 0.05072 | -0.11094 | 0.002454 | 0.036954 | -0.060955 | -0.012328 | 0.13558 | 0.000682 | 0.084145 | 0.02992 | 0.14156 | 0.10847 | -0.007782 | 0.070797 | 0.17079 | 0.078186 | -0.083478 | 0.02992 | 0.06442 | -0.033489 | 0.015138 | 0.040877 | 0.10429 | 0.048266 | 0.11167
2130.6094 | 122.6212 | -122.4197 | 0.10071 | 0.10812 | -0.026784 | 0.052101 | -0.002124 | 0.10951 | 0.081005 | -0.03067 | 0.038752 | 0.1479 | 0.05072 | -0.10179 | 0.007032 | 0.04611 | -0.065533 | -0.021484 | 0.13558 | 0.000682 | 0.079567 | 0.025342 | 0.13698 | 0.10847 | -0.003204 | 0.066218 | 0.17536 | 0.078186 | -0.07432 | 0.034498 | 0.073576 | -0.038067 | 0.005982 | 0.03172 | 0.10428 | 0.043688 | 0.11625
2132.3594 | 122.5845 | -122.4472 | 0.11902 | 0.10812 | -0.026784 | 0.056679 | -0.002124 | 0.10493 | 0.076426 | -0.026092 | 0.038752 | 0.14332 | 0.041563 | -0.10179 | 0.01161 | 0.032376 | -0.070112 | -0.012328 | 0.13558 | 0.000682 | 0.084145 | 0.025342 | 0.1324 | 0.10389 | 0.001374 | 0.066218 | 0.17079 | 0.069029 | -0.07432 | 0.039076 | 0.059842 | -0.042646 | 0.015138 | 0.027142 | 0.10886 | 0.029953 | 0.11167
2134.0469 | 122.7127 | -122.3923 | 0.091553 | 0.11269 | -0.035942 | 0.047522 | 0.002454 | 0.10493 | 0.071848 | -0.035248 | 0.038752 | 0.15248 | 0.05072 | -0.10637 | 0.002454 | 0.041532 | -0.065533 | -0.012328 | 0.14016 | -0.008476 | 0.074988 | 0.02992 | 0.1324 | 0.099314 | -0.007782 | 0.066218 | 0.17994 | 0.078186 | -0.078899 | 0.02992 | 0.068998 | -0.038067 | 0.015138 | 0.036298 | 0.10428 | 0.048266 | 0.11625
2135.7969 | 122.6395 | -122.4289 | 0.10071 | 0.11269 | -0.031363 | 0.047522 | 0.007033 | 0.10951 | 0.081005 | -0.026092 | 0.034174 | 0.14332 | 0.05072 | -0.10637 | 0.007032 | 0.032376 | -0.070112 | -0.00775 | 0.14016 | -0.003897 | 0.074988 | 0.034499 | 0.13698 | 0.10847 | 0.001374 | 0.06164 | 0.17079 | 0.078186 | -0.078899 | 0.034498 | 0.059842 | -0.042646 | 0.019716 | 0.027142 | 0.10429 | 0.043688 | 0.12083
2137.5312 | 122.7219 | -122.4197 | 0.086975 | 0.11269 | -0.026784 | 0.052101 | 0.002454 | 0.11409 | 0.081005 | -0.026092 | 0.043331 | 0.13874 | 0.055298 | -0.11552 | -0.002124 | 0.036954 | -0.065533 | -0.00775 | 0.14016 | 0.000682 | 0.079567 | 0.02992 | 0.14156 | 0.10847 | 0.001374 | 0.070797 | 0.16621 | 0.082764 | -0.088057 | 0.025342 | 0.06442 | -0.038067 | 0.019716 | 0.045455 | 0.10886 | 0.057422 | 0.12083
2139.2812 | 122.6761 | -122.4014 | 0.064087 | 0.11269 | -0.031363 | 0.056679 | -0.002124 | 0.10493 | 0.067269 | -0.03067 | 0.034174 | 0.15248 | 0.05072 | -0.10179 | 0.002454 | 0.041532 | -0.070112 | -0.012328 | 0.14016 | -0.003897 | 0.084145 | 0.025342 | 0.1324 | 0.094735 | -0.003204 | 0.06164 | 0.17994 | 0.078186 | -0.07432 | 0.02992 | 0.068998 | -0.042646 | 0.015138 | 0.03172 | 0.10429 | 0.048266 | 0.12083
2141.0312 | 122.6852 | -122.3831 | 0.07782 | 0.10354 | -0.031363 | 0.052101 | 0.002454 | 0.10036 | 0.076426 | -0.035248 | 0.038752 | 0.14332 | 0.041563 | -0.10179 | 0.002454 | 0.036954 | -0.060955 | -0.016906 | 0.131 | -0.003897 | 0.079567 | 0.02992 | 0.12782 | 0.10389 | -0.007782 | 0.066218 | 0.17079 | 0.069029 | -0.07432 | 0.02992 | 0.06442 | -0.033489 | 0.01056 | 0.036298 | 0.099707 | 0.039109 | 0.10252
2142.7656 | 122.7036 | -122.3923 | 0.082397 | 0.10812 | -0.035942 | 0.052101 | 0.002454 | 0.10493 | 0.076426 | -0.026092 | 0.034174 | 0.14332 | 0.041563 | -0.10179 | 0.007032 | 0.036954 | -0.060955 | -0.021484 | 0.13558 | -0.008476 | 0.079567 | 0.02992 | 0.1324 | 0.10389 | 0.001374 | 0.06164 | 0.17079 | 0.069029 | -0.07432 | 0.034498 | 0.06442 | -0.033489 | 0.005982 | 0.027142 | 0.095129 | 0.034531 | 0.10252
2144.4531 | 122.5983 | -122.4335 | 0.11902 | 0.11727 | -0.026784 | 0.056679 | 0.007033 | 0.10036 | 0.081005 | -0.03067 | 0.034174 | 0.14332 | 0.046142 | -0.10637 | 0.002454 | 0.036954 | -0.065533 | -0.016906 | 0.14474 | 0.000682 | 0.084145 | 0.034499 | 0.12782 | 0.10847 | -0.003204 | 0.06164 | 0.17079 | 0.073608 | -0.078899 | 0.02992 | 0.06442 | -0.038067 | 0.01056 | 0.03172 | 0.099707 | 0.043688 | 0.11167
2146.2031 | 122.6669 | -122.4335 | 0.09613 | 0.11269 | -0.031363 | 0.056679 | -0.002124 | 0.10951 | 0.067269 | -0.03067 | 0.034174 | 0.14332 | 0.055298 | -0.10637 | 0.002454 | 0.041532 | -0.065533 | -0.012328 | 0.14016 | -0.003897 | 0.084145 | 0.025342 | 0.13698 | 0.094735 | -0.003204 | 0.06164 | 0.17079 | 0.082764 | -0.078899 | 0.02992 | 0.068998 | -0.038067 | 0.015138 | 0.03172 | 0.099707 | 0.052844 | 0.12083
2147.9531 | 122.6578 | -122.4335 | 0.1236 | 0.11269 | -0.026784 | 0.052101 | -0.002124 | 0.10951 | 0.071848 | -0.03067 | 0.034174 | 0.14332 | 0.05072 | -0.11094 | 0.01161 | 0.041532 | -0.070112 | -0.012328 | 0.14016 | 0.000682 | 0.079567 | 0.025342 | 0.13698 | 0.099314 | -0.003204 | 0.06164 | 0.17079 | 0.078186 | -0.083478 | 0.039076 | 0.068998 | -0.042646 | 0.015138 | 0.022564 | 0.10429 | 0.03911 | 0.12083
2149.6406 | 122.7264 | -122.4106 | 0.086975 | 0.11727 | -0.035942 | 0.061258 | 0.007033 | 0.10493 | 0.081005 | -0.035248 | 0.034174 | 0.14332 | 0.055298 | -0.10637 | 0.002454 | 0.041532 | -0.060955 | -0.012328 | 0.14474 | -0.008476 | 0.088724 | 0.034499 | 0.1324 | 0.10847 | -0.007782 | 0.06164 | 0.17079 | 0.082764 | -0.078899 | 0.02992 | 0.068998 | -0.033489 | 0.015138 | 0.03172 | 0.095129 | 0.052844 | 0.11625
2151.3906 | 122.7081 | -122.4243 | 0.10071 | 0.11269 | -0.035942 | 0.061258 | -0.002124 | 0.10493 | 0.081005 | -0.035248 | 0.038752 | 0.13874 | 0.046142 | -0.11094 | 0.002454 | 0.036954 | -0.070112 | -0.012328 | 0.14016 | -0.008476 | 0.088724 | 0.025342 | 0.1324 | 0.10847 | -0.007782 | 0.066218 | 0.16621 | 0.073608 | -0.083478 | 0.02992 | 0.06442 | -0.042646 | 0.015138 | 0.036298 | 0.10886 | 0.043688 | 0.11625
2153.0625 | 122.644 | -122.4243 | 0.10986 | 0.10812 | -0.035942 | 0.056679 | -0.002124 | 0.10493 | 0.076426 | -0.016936 | 0.034174 | 0.13416 | 0.05072 | -0.10637 | 0.007032 | 0.036954 | -0.070112 | -0.016906 | 0.13558 | -0.008476 | 0.084145 | 0.025342 | 0.1324 | 0.10389 | 0.01053 | 0.06164 | 0.16163 | 0.078186 | -0.078899 | 0.034498 | 0.06442 | -0.042646 | 0.01056 | 0.027142 | 0.10429 | 0.043688 | 0.12083
2154.8125 | 122.6898 | -122.4197 | 0.09613 | 0.11269 | -0.035942 | 0.052101 | 0.002454 | 0.10493 | 0.071848 | -0.03067 | 0.038752 | 0.13416 | 0.05072 | -0.10637 | 0.007032 | 0.032376 | -0.065533 | -0.012328 | 0.14016 | -0.008476 | 0.079567 | 0.02992 | 0.1324 | 0.099314 | -0.003204 | 0.066218 | 0.16163 | 0.078186 | -0.078899 | 0.034498 | 0.059842 | -0.038067 | 0.015138 | 0.03172 | 0.10428 | 0.043688 | 0.11625
2156.5625 | 122.7173 | -122.406 | 0.064087 | 0.11269 | -0.031363 | 0.056679 | -0.006703 | 0.10951 | 0.076426 | -0.035248 | 0.034174 | 0.1479 | 0.055298 | -0.10637 | 0.007032 | 0.036954 | -0.070112 | -0.016906 | 0.14016 | -0.003897 | 0.084145 | 0.020763 | 0.13698 | 0.10389 | -0.007782 | 0.06164 | 0.17536 | 0.082764 | -0.078899 | 0.034498 | 0.06442 | -0.042646 | 0.01056 | 0.027142 | 0.10429 | 0.048266 | 0.12541
2158.25 | 122.5983 | -122.4655 | 0.10529 | 0.11727 | -0.035942 | 0.056679 | 0.002454 | 0.10036 | 0.081005 | -0.03067 | 0.038752 | 0.14332 | 0.041563 | -0.11094 | 0.002454 | 0.032376 | -0.060955 | -0.00775 | 0.14474 | -0.008476 | 0.084145 | 0.02992 | 0.12782 | 0.10847 | -0.003204 | 0.066218 | 0.17079 | 0.069029 | -0.083478 | 0.02992 | 0.059842 | -0.033489 | 0.019716 | 0.036298 | 0.099707 | 0.039109 | 0.10252
2160 | 122.644 | -122.4655 | 0.10986 | 0.11727 | -0.026784 | 0.052101 | -0.002124 | 0.10493 | 0.081005 | -0.026092 | 0.038752 | 0.14332 | 0.055298 | -0.11094 | 0.007032 | 0.036954 | -0.065533 | -0.021484 | 0.14474 | 0.000682 | 0.079567 | 0.025342 | 0.1324 | 0.10847 | 0.001374 | 0.066218 | 0.17079 | 0.082764 | -0.083478 | 0.034498 | 0.06442 | -0.038067 | 0.005982 | 0.03172 | 0.10428 | 0.048266 | 0.12083
2161.6719 | 122.731 | -122.4152 | 0.07782 | 0.11269 | -0.040521 | 0.052101 | -0.002124 | 0.11409 | 0.076426 | -0.035248 | 0.034174 | 0.1479 | 0.046142 | -0.10637 | 0.002454 | 0.036954 | -0.065533 | -0.00775 | 0.14016 | -0.013055 | 0.079567 | 0.025342 | 0.14156 | 0.10389 | -0.007782 | 0.06164 | 0.17536 | 0.073608 | -0.078899 | 0.02992 | 0.06442 | -0.038067 | 0.019716 | 0.03172 | 0.099707 | 0.043688 | 0.11167
2163.4219 | 122.6852 | -122.4335 | 0.09613 | 0.11727 | -0.035942 | 0.061258 | -0.002124 | 0.10493 | 0.081005 | -0.03067 | 0.034174 | 0.14332 | 0.05072 | -0.10179 | 0.007032 | 0.04611 | -0.065533 | -0.012328 | 0.14474 | -0.008476 | 0.088724 | 0.025342 | 0.1324 | 0.10847 | -0.003204 | 0.06164 | 0.17079 | 0.078186 | -0.07432 | 0.034498 | 0.073576 | -0.038067 | 0.015138 | 0.027142 | 0.099707 | 0.043688 | 0.11625
2165.0938 | 122.699 | -122.4197 | 0.10529 | 0.11727 | -0.040521 | 0.052101 | -0.006703 | 0.10951 | 0.076426 | -0.021514 | 0.034174 | 0.14332 | 0.046142 | -0.10179 | 0.002454 | 0.032376 | -0.070112 | -0.012328 | 0.14474 | -0.013055 | 0.079567 | 0.020763 | 0.13698 | 0.10389 | 0.005952 | 0.06164 | 0.17079 | 0.073608 | -0.07432 | 0.02992 | 0.059842 | -0.042646 | 0.015138 | 0.03172 | 0.10429 | 0.043688 | 0.11625
2166.8281 | 122.6944 | -122.4472 | 0.10986 | 0.11269 | -0.035942 | 0.056679 | -0.002124 | 0.095778 | 0.081005 | -0.03067 | 0.038752 | 0.1479 | 0.046142 | -0.10637 | 0.007032 | 0.041532 | -0.060955 | -0.016906 | 0.14016 | -0.008476 | 0.084145 | 0.025342 | 0.12324 | 0.10847 | -0.003204 | 0.066218 | 0.17536 | 0.073608 | -0.078899 | 0.034498 | 0.068998 | -0.033489 | 0.01056 | 0.03172 | 0.099707 | 0.03911 | 0.1071
2168.5938 | 122.6257 | -122.4564 | 0.10071 | 0.12185 | -0.031363 | 0.052101 | 0.007033 | 0.10493 | 0.085583 | -0.016936 | 0.029595 | 0.1479 | 0.046142 | -0.10637 | 0.01161 | 0.041532 | -0.060955 | -0.00775 | 0.14932 | -0.003897 | 0.079567 | 0.034499 | 0.1324 | 0.11305 | 0.01053 | 0.057061 | 0.17536 | 0.073608 | -0.078899 | 0.039076 | 0.068998 | -0.033489 | 0.019716 | 0.017985 | 0.09055 | 0.034532 | 0.1071
2170.2812 | 122.7585 | -122.4289 | 0.10071 | 0.11269 | -0.035942 | 0.052101 | 0.002454 | 0.10036 | 0.076426 | -0.026092 | 0.034174 | 0.14332 | 0.05072 | -0.11094 | 0.007032 | 0.041532 | -0.051798 | -0.021484 | 0.14016 | -0.008476 | 0.079567 | 0.02992 | 0.12782 | 0.10389 | 0.001374 | 0.06164 | 0.17079 | 0.078186 | -0.083478 | 0.034498 | 0.068998 | -0.024332 | 0.005982 | 0.027142 | 0.085972 | 0.043688 | 0.10252
2172.0156 | 122.6257 | -122.4609 | 0.10071 | 0.11727 | -0.035942 | 0.056679 | 0.007033 | 0.10951 | 0.076426 | -0.035248 | 0.043331 | 0.14332 | 0.05072 | -0.10637 | 0.007032 | 0.036954 | -0.070112 | -0.00775 | 0.14474 | -0.008476 | 0.084145 | 0.034499 | 0.13698 | 0.10389 | -0.007782 | 0.070797 | 0.17079 | 0.078186 | -0.078899 | 0.034498 | 0.06442 | -0.042646 | 0.019716 | 0.036299 | 0.11344 | 0.043688 | 0.12083
2173.7031 | 122.7356 | -122.4197 | 0.082397 | 0.11269 | -0.022205 | 0.056679 | 0.002454 | 0.10036 | 0.076426 | -0.03067 | 0.034174 | 0.15248 | 0.05072 | -0.11094 | 0.01161 | 0.036954 | -0.060955 | -0.016906 | 0.14016 | 0.005261 | 0.084145 | 0.02992 | 0.12782 | 0.10389 | -0.003204 | 0.06164 | 0.17994 | 0.078186 | -0.083478 | 0.039076 | 0.06442 | -0.033489 | 0.01056 | 0.022564 | 0.095129 | 0.03911 | 0.11167
2175.4375 | 122.699 | -122.4518 | 0.091553 | 0.11727 | -0.031363 | 0.056679 | -0.006703 | 0.11409 | 0.076426 | -0.035248 | 0.034174 | 0.14332 | 0.046142 | -0.11094 | 0.007032 | 0.036954 | -0.065533 | -0.021484 | 0.14474 | -0.003897 | 0.084145 | 0.020763 | 0.14156 | 0.10389 | -0.007782 | 0.06164 | 0.17079 | 0.073608 | -0.083478 | 0.034498 | 0.06442 | -0.038067 | 0.005982 | 0.027142 | 0.099707 | 0.03911 | 0.11167
2177.1094 | 122.731 | -122.4243 | 0.10071 | 0.11727 | -0.035942 | 0.052101 | -0.002124 | 0.10493 | 0.067269 | -0.039826 | 0.034174 | 0.13874 | 0.055298 | -0.10637 | 0.007032 | 0.036954 | -0.060955 | -0.012328 | 0.14474 | -0.008476 | 0.079567 | 0.025342 | 0.1324 | 0.094735 | -0.01236 | 0.06164 | 0.16621 | 0.082764 | -0.078899 | 0.034498 | 0.06442 | -0.033489 | 0.015138 | 0.027142 | 0.095129 | 0.048266 | 0.11625
2178.875 | 122.7539 | -122.4243 | 0.091553 | 0.10812 | -0.026784 | 0.056679 | -0.002124 | 0.10036 | 0.076426 | -0.026092 | 0.034174 | 0.14332 | 0.05072 | -0.10179 | 0.007032 | 0.036954 | -0.065533 | -0.012328 | 0.13558 | 0.000682 | 0.084145 | 0.025342 | 0.12782 | 0.10389 | 0.001374 | 0.06164 | 0.17079 | 0.078186 | -0.07432 | 0.034498 | 0.06442 | -0.038067 | 0.015138 | 0.027142 | 0.099707 | 0.043688 | 0.11625
2180.5625 | 122.6257 | -122.493 | 0.091553 | 0.11269 | -0.035942 | 0.052101 | 0.007033 | 0.11409 | 0.071848 | -0.026092 | 0.034174 | 0.14332 | 0.055298 | -0.10179 | 0.002454 | 0.036954 | -0.065533 | -0.016906 | 0.14016 | -0.008476 | 0.079567 | 0.034499 | 0.14156 | 0.099314 | 0.001374 | 0.06164 | 0.17079 | 0.082764 | -0.07432 | 0.02992 | 0.06442 | -0.038067 | 0.01056 | 0.03172 | 0.099707 | 0.052844 | 0.12083
2182.3125 | 122.7493 | -122.4106 | 0.073242 | 0.11269 | -0.026784 | 0.056679 | -0.002124 | 0.10493 | 0.081005 | -0.03067 | 0.034174 | 0.14332 | 0.05072 | -0.10637 | 0.01161 | 0.041532 | -0.060955 | -0.021484 | 0.14016 | 0.000682 | 0.084145 | 0.025342 | 0.1324 | 0.10847 | -0.003204 | 0.06164 | 0.17079 | 0.078186 | -0.078899 | 0.039076 | 0.068998 | -0.033489 | 0.005982 | 0.022564 | 0.095129 | 0.03911 | 0.11167
2184.0156 | 122.7448 | -122.438 | 0.09613 | 0.10812 | -0.031363 | 0.061258 | -0.006703 | 0.10493 | 0.071848 | -0.03067 | 0.029595 | 0.1479 | 0.059877 | -0.11094 | 0.002454 | 0.036954 | -0.065533 | -0.012328 | 0.13558 | -0.003897 | 0.088724 | 0.020763 | 0.1324 | 0.099314 | -0.003204 | 0.057061 | 0.17536 | 0.087343 | -0.083478 | 0.02992 | 0.06442 | -0.038067 | 0.015138 | 0.027141 | 0.095128 | 0.057423 | 0.12541
2185.7656 | 122.7356 | -122.4472 | 0.082397 | 0.11269 | -0.035942 | 0.056679 | -0.002124 | 0.11409 | 0.071848 | -0.03067 | 0.034174 | 0.1479 | 0.05072 | -0.10637 | -0.002124 | 0.036954 | -0.065533 | -0.012328 | 0.14016 | -0.008476 | 0.084145 | 0.025342 | 0.14156 | 0.099314 | -0.003204 | 0.06164 | 0.17536 | 0.078186 | -0.078899 | 0.025342 | 0.06442 | -0.038067 | 0.015138 | 0.036298 | 0.099707 | 0.052844 | 0.11625
2187.5 | 122.612 | -122.4472 | 0.10986 | 0.11727 | -0.031363 | 0.056679 | 0.007033 | 0.10493 | 0.076426 | -0.026092 | 0.038752 | 0.14332 | 0.05072 | -0.10637 | 0.01161 | 0.036954 | -0.060955 | -0.012328 | 0.14474 | -0.003897 | 0.084145 | 0.034499 | 0.1324 | 0.10389 | 0.001374 | 0.066218 | 0.17079 | 0.078186 | -0.078899 | 0.039076 | 0.06442 | -0.033489 | 0.015138 | 0.027142 | 0.099707 | 0.03911 | 0.11167
2189.2344 | 122.7036 | -122.4564 | 0.07782 | 0.098959 | -0.040521 | 0.052101 | -0.006703 | 0.10036 | 0.067269 | -0.035248 | 0.038752 | 0.1479 | 0.05072 | -0.11094 | 0.007032 | 0.036954 | -0.070112 | -0.012328 | 0.12643 | -0.013055 | 0.079567 | 0.020763 | 0.12782 | 0.094735 | -0.007782 | 0.066218 | 0.17536 | 0.078186 | -0.083478 | 0.034498 | 0.06442 | -0.042646 | 0.015138 | 0.03172 | 0.10886 | 0.043688 | 0.12083
2190.9375 | 122.7814 | -122.4289 | 0.09613 | 0.11727 | -0.031363 | 0.052101 | 0.002454 | 0.10493 | 0.076426 | -0.03067 | 0.034174 | 0.14332 | 0.05072 | -0.10179 | 0.002454 | 0.04611 | -0.060955 | -0.00775 | 0.14474 | -0.003897 | 0.079567 | 0.02992 | 0.1324 | 0.10389 | -0.003204 | 0.06164 | 0.17079 | 0.078186 | -0.07432 | 0.02992 | 0.073576 | -0.033489 | 0.019716 | 0.03172 | 0.095129 | 0.048266 | 0.11167
2192.6875 | 122.6166 | -122.4838 | 0.13275 | 0.10812 | -0.031363 | 0.056679 | 0.002454 | 0.10493 | 0.076426 | -0.021514 | 0.034174 | 0.1479 | 0.055298 | -0.10179 | 0.007032 | 0.036954 | -0.070112 | -0.00775 | 0.13558 | -0.003897 | 0.084145 | 0.02992 | 0.1324 | 0.10389 | 0.005952 | 0.06164 | 0.17536 | 0.082764 | -0.07432 | 0.034498 | 0.06442 | -0.042646 | 0.019716 | 0.027142 | 0.10429 | 0.048266 | 0.12541
2194.3906 | 122.6669 | -122.4609 | 0.10529 | 0.10812 | -0.031363 | 0.056679 | 0.002454 | 0.10493 | 0.081005 | -0.026092 | 0.043331 | 0.1479 | 0.05072 | -0.10637 | 0.01161 | 0.041532 | -0.065533 | -0.016906 | 0.13558 | -0.003897 | 0.084145 | 0.02992 | 0.1324 | 0.10847 | 0.001374 | 0.070797 | 0.17536 | 0.078186 | -0.078899 | 0.039076 | 0.068998 | -0.038067 | 0.01056 | 0.031721 | 0.10886 | 0.03911 | 0.11625
2196.1562 | 122.6486 | -122.4701 | 0.10986 | 0.11269 | -0.026784 | 0.061258 | -0.006703 | 0.10036 | 0.081005 | -0.03067 | 0.029595 | 0.15248 | 0.046142 | -0.11094 | 0.007032 | 0.036954 | -0.070112 | -0.012328 | 0.14016 | 0.000682 | 0.088724 | 0.020763 | 0.12782 | 0.10847 | -0.003204 | 0.057061 | 0.17994 | 0.073608 | -0.083478 | 0.034498 | 0.06442 | -0.042646 | 0.015138 | 0.022563 | 0.099707 | 0.03911 | 0.11625
2197.9062 | 122.6715 | -122.4747 | 0.10529 | 0.11727 | -0.026784 | 0.052101 | -0.002124 | 0.10951 | 0.081005 | -0.026092 | 0.038752 | 0.1479 | 0.05072 | -0.10637 | 0.01161 | 0.036954 | -0.065533 | -0.012328 | 0.14474 | 0.000682 | 0.079567 | 0.025342 | 0.13698 | 0.10847 | 0.001374 | 0.066218 | 0.17536 | 0.078186 | -0.078899 | 0.039076 | 0.06442 | -0.038067 | 0.015138 | 0.027142 | 0.10428 | 0.03911 | 0.11625
2199.6094 | 122.6669 | -122.4701 | 0.12817 | 0.10812 | -0.031363 | 0.056679 | 0.002454 | 0.11409 | 0.085583 | -0.03067 | 0.038752 | 0.14332 | 0.05072 | -0.11094 | 0.007032 | 0.036954 | -0.065533 | -0.012328 | 0.13558 | -0.003897 | 0.084145 | 0.02992 | 0.14156 | 0.11305 | -0.003204 | 0.066218 | 0.17079 | 0.078186 | -0.083478 | 0.034498 | 0.06442 | -0.038067 | 0.015138 | 0.03172 | 0.10428 | 0.043688 | 0.11625
2201.2969 | 122.7173 | -122.4564 | 0.10071 | 0.11269 | -0.035942 | 0.052101 | -0.002124 | 0.10493 | 0.076426 | -0.035248 | 0.038752 | 0.1479 | 0.046142 | -0.11094 | 0.007032 | 0.036954 | -0.065533 | -0.012328 | 0.14016 | -0.008476 | 0.079567 | 0.025342 | 0.1324 | 0.10389 | -0.007782 | 0.066218 | 0.17536 | 0.073608 | -0.083478 | 0.034498 | 0.06442 | -0.038067 | 0.015138 | 0.03172 | 0.10428 | 0.03911 | 0.11167
2203.0469 | 122.7219 | -122.4884 | 0.10986 | 0.11269 | -0.040521 | 0.052101 | 0.002454 | 0.10036 | 0.081005 | -0.03067 | 0.034174 | 0.1479 | 0.055298 | -0.10637 | 0.007032 | 0.036954 | -0.060955 | -0.016906 | 0.14016 | -0.013055 | 0.079567 | 0.02992 | 0.12782 | 0.10847 | -0.003204 | 0.06164 | 0.17536 | 0.082764 | -0.078899 | 0.034498 | 0.06442 | -0.033489 | 0.01056 | 0.027142 | 0.095129 | 0.048266 | 0.11625
2204.7344 | 122.6807 | -122.4564 | 0.10071 | 0.11727 | -0.031363 | 0.052101 | 0.002454 | 0.10951 | 0.076426 | -0.03067 | 0.029595 | 0.13874 | 0.055298 | -0.10637 | 0.007032 | 0.041532 | -0.070112 | -0.021484 | 0.14474 | -0.003897 | 0.079567 | 0.02992 | 0.13698 | 0.10389 | -0.003204 | 0.057061 | 0.16621 | 0.082764 | -0.078899 | 0.034498 | 0.068998 | -0.042646 | 0.005982 | 0.022563 | 0.099707 | 0.048266 | 0.12541
2206.4844 | 122.7722 | -122.4335 | 0.082397 | 0.11269 | -0.031363 | 0.052101 | -0.002124 | 0.10493 | 0.076426 | -0.039826 | 0.034174 | 0.14332 | 0.05072 | -0.10637 | 0.01161 | 0.036954 | -0.070112 | -0.016906 | 0.14016 | -0.003897 | 0.079567 | 0.025342 | 0.1324 | 0.10389 | -0.01236 | 0.06164 | 0.17079 | 0.078186 | -0.078899 | 0.039076 | 0.06442 | -0.042646 | 0.01056 | 0.022564 | 0.10429 | 0.03911 | 0.12083
2208.1719 | 122.644 | -122.4792 | 0.10986 | 0.12185 | -0.031363 | 0.052101 | 0.007033 | 0.10493 | 0.081005 | -0.03067 | 0.034174 | 0.14332 | 0.046142 | -0.10637 | 0.01161 | 0.04611 | -0.065533 | -0.012328 | 0.14932 | -0.003897 | 0.079567 | 0.034499 | 0.1324 | 0.10847 | -0.003204 | 0.06164 | 0.17079 | 0.073608 | -0.078899 | 0.039076 | 0.073576 | -0.038067 | 0.015138 | 0.022564 | 0.099707 | 0.034532 | 0.11167
2209.9219 | 122.6761 | -122.4838 | 0.091553 | 0.10354 | -0.031363 | 0.056679 | -0.006703 | 0.10493 | 0.081005 | -0.021514 | 0.029595 | 0.13874 | 0.046142 | -0.10179 | 0.007032 | 0.036954 | -0.060955 | -0.00775 | 0.131 | -0.003897 | 0.084145 | 0.020763 | 0.1324 | 0.10847 | 0.005952 | 0.057061 | 0.16621 | 0.073608 | -0.07432 | 0.034498 | 0.06442 | -0.033489 | 0.019716 | 0.022563 | 0.09055 | 0.03911 | 0.1071
2211.6562 | 122.7264 | -122.4747 | 0.086975 | 0.10812 | -0.031363 | 0.061258 | -0.006703 | 0.10951 | 0.071848 | -0.016936 | 0.029595 | 0.1479 | 0.05072 | -0.11094 | 0.002454 | 0.036954 | -0.065533 | -0.021484 | 0.13558 | -0.003897 | 0.088724 | 0.020763 | 0.13698 | 0.099314 | 0.01053 | 0.057061 | 0.17536 | 0.078186 | -0.083478 | 0.02992 | 0.06442 | -0.038067 | 0.005982 | 0.027141 | 0.095128 | 0.048266 | 0.11625
2213.4062 | 122.6898 | -122.4655 | 0.10071 | 0.10354 | -0.035942 | 0.056679 | 0.002454 | 0.10951 | 0.076426 | -0.026092 | 0.029595 | 0.14332 | 0.046142 | -0.10637 | 0.007032 | 0.036954 | -0.070112 | -0.012328 | 0.131 | -0.008476 | 0.084145 | 0.02992 | 0.13698 | 0.10389 | 0.001374 | 0.057061 | 0.17079 | 0.073608 | -0.078899 | 0.034498 | 0.06442 | -0.042646 | 0.015138 | 0.022563 | 0.099707 | 0.03911 | 0.11625
2215.0938 | 122.7493 | -122.493 | 0.064087 | 0.10812 | -0.040521 | 0.047522 | 0.002454 | 0.10493 | 0.076426 | -0.026092 | 0.034174 | 0.14332 | 0.05072 | -0.10179 | 0.007032 | 0.036954 | -0.065533 | -0.012328 | 0.13558 | -0.013055 | 0.074988 | 0.02992 | 0.1324 | 0.10389 | 0.001374 | 0.06164 | 0.17079 | 0.078186 | -0.07432 | 0.034498 | 0.06442 | -0.038067 | 0.015138 | 0.027142 | 0.099707 | 0.043688 | 0.11625
2216.8281 | 122.7264 | -122.4564 | 0.10071 | 0.11269 | -0.031363 | 0.052101 | 0.002454 | 0.10036 | 0.076426 | -0.035248 | 0.038752 | 0.15248 | 0.05072 | -0.11094 | 0.002454 | 0.036954 | -0.070112 | -0.012328 | 0.14016 | -0.003897 | 0.079567 | 0.02992 | 0.12782 | 0.10389 | -0.007782 | 0.066218 | 0.17994 | 0.078186 | -0.083478 | 0.02992 | 0.06442 | -0.042646 | 0.015138 | 0.036298 | 0.10886 | 0.048266 | 0.12083
2218.5 | 122.6486 | -122.4701 | 0.11902 | 0.12185 | -0.022205 | 0.052101 | 0.002454 | 0.10951 | 0.081005 | -0.021514 | 0.034174 | 0.14332 | 0.046142 | -0.10637 | 0.002454 | 0.032376 | -0.070112 | -0.026063 | 0.14932 | 0.005261 | 0.079567 | 0.02992 | 0.13698 | 0.10847 | 0.005952 | 0.06164 | 0.17079 | 0.073608 | -0.078899 | 0.02992 | 0.059842 | -0.042646 | 0.001403 | 0.03172 | 0.10429 | 0.043688 | 0.11625
2220.1875 | 122.6303 | -122.4976 | 0.12817 | 0.10812 | -0.031363 | 0.056679 | 0.002454 | 0.10951 | 0.071848 | -0.03067 | 0.038752 | 0.14332 | 0.055298 | -0.10637 | 0.002454 | 0.041532 | -0.070112 | -0.021484 | 0.13558 | -0.003897 | 0.084145 | 0.02992 | 0.13698 | 0.099314 | -0.003204 | 0.066218 | 0.17079 | 0.082764 | -0.078899 | 0.02992 | 0.068998 | -0.042646 | 0.005982 | 0.036298 | 0.10886 | 0.052844 | 0.12541
2221.9219 | 122.6944 | -122.5067 | 0.13275 | 0.11269 | -0.035942 | 0.052101 | 0.007033 | 0.11409 | 0.081005 | -0.03067 | 0.038752 | 0.1479 | 0.05072 | -0.10637 | 0.002454 | 0.036954 | -0.060955 | -0.00775 | 0.14016 | -0.008476 | 0.079567 | 0.034499 | 0.14156 | 0.10847 | -0.003204 | 0.066218 | 0.17536 | 0.078186 | -0.078899 | 0.02992 | 0.06442 | -0.033489 | 0.019716 | 0.036298 | 0.099707 | 0.048266 | 0.11167
2223.6875 | 122.7676 | -122.4701 | 0.086975 | 0.11269 | -0.026784 | 0.056679 | 0.007033 | 0.11409 | 0.076426 | -0.035248 | 0.034174 | 0.14332 | 0.046142 | -0.10637 | 0.007032 | 0.036954 | -0.065533 | -0.012328 | 0.14016 | 0.000682 | 0.084145 | 0.034499 | 0.14156 | 0.10389 | -0.007782 | 0.06164 | 0.17079 | 0.073608 | -0.078899 | 0.034498 | 0.06442 | -0.038067 | 0.015138 | 0.027142 | 0.099707 | 0.03911 | 0.11167
2225.375 | 122.8043 | -122.4701 | 0.091553 | 0.10812 | -0.031363 | 0.052101 | 0.007033 | 0.11409 | 0.071848 | -0.026092 | 0.034174 | 0.13874 | 0.055298 | -0.10179 | 0.01161 | 0.032376 | -0.070112 | -0.012328 | 0.13558 | -0.003897 | 0.079567 | 0.034499 | 0.14156 | 0.099314 | 0.001374 | 0.06164 | 0.16621 | 0.082764 | -0.07432 | 0.039076 | 0.059842 | -0.042646 | 0.015138 | 0.022564 | 0.10429 | 0.043688 | 0.12541
2227.1094 | 122.7951 | -122.4426 | 0.082397 | 0.11269 | -0.031363 | 0.052101 | 0.007033 | 0.10951 | 0.076426 | -0.03067 | 0.029595 | 0.14332 | 0.041563 | -0.10637 | 0.007032 | 0.041532 | -0.060955 | -0.021484 | 0.14016 | -0.003897 | 0.079567 | 0.034499 | 0.13698 | 0.10389 | -0.003204 | 0.057061 | 0.17079 | 0.069029 | -0.078899 | 0.034498 | 0.068998 | -0.033489 | 0.005982 | 0.022563 | 0.09055 | 0.034531 | 0.10252
2228.875 | 122.7722 | -122.438 | 0.082397 | 0.11269 | -0.035942 | 0.052101 | -0.002124 | 0.10036 | 0.081005 | -0.03067 | 0.029595 | 0.14332 | 0.036985 | -0.10637 | 0.002454 | 0.041532 | -0.065533 | -0.012328 | 0.14016 | -0.008476 | 0.079567 | 0.025342 | 0.12782 | 0.10847 | -0.003204 | 0.057061 | 0.17079 | 0.064451 | -0.078899 | 0.02992 | 0.068998 | -0.038067 | 0.015138 | 0.027141 | 0.095128 | 0.034531 | 0.10252
2230.5625 | 122.7814 | -122.4609 | 0.086975 | 0.11727 | -0.026784 | 0.056679 | 0.002454 | 0.10951 | 0.071848 | -0.039826 | 0.025017 | 0.14332 | 0.055298 | -0.11552 | 0.007032 | 0.041532 | -0.070112 | -0.012328 | 0.14474 | 0.000682 | 0.084145 | 0.02992 | 0.13698 | 0.099314 | -0.01236 | 0.052483 | 0.17079 | 0.082764 | -0.088057 | 0.034498 | 0.068998 | -0.042646 | 0.015138 | 0.017985 | 0.095129 | 0.048266 | 0.12541
2232.3125 | 122.644 | -122.4976 | 0.1236 | 0.11269 | -0.026784 | 0.061258 | 0.007033 | 0.10951 | 0.076426 | -0.026092 | 0.029595 | 0.14332 | 0.041563 | -0.10637 | 0.007032 | 0.041532 | -0.060955 | -0.00775 | 0.14016 | 0.000682 | 0.088724 | 0.034499 | 0.13698 | 0.10389 | 0.001374 | 0.057061 | 0.17079 | 0.069029 | -0.078899 | 0.034498 | 0.068998 | -0.033489 | 0.019716 | 0.022563 | 0.09055 | 0.034531 | 0.10252
2234 | 122.6624 | -122.5021 | 0.12817 | 0.11727 | -0.035942 | 0.061258 | 0.002454 | 0.10951 | 0.081005 | -0.03067 | 0.029595 | 0.14332 | 0.05072 | -0.11094 | 0.007032 | 0.036954 | -0.065533 | -0.00775 | 0.14474 | -0.008476 | 0.088724 | 0.02992 | 0.13698 | 0.10847 | -0.003204 | 0.057061 | 0.17079 | 0.078186 | -0.083478 | 0.034498 | 0.06442 | -0.038067 | 0.019716 | 0.022563 | 0.095128 | 0.043688 | 0.11625
2235.75 | 122.7127 | -122.4701 | 0.10529 | 0.11269 | -0.026784 | 0.052101 | 0.002454 | 0.10951 | 0.081005 | -0.026092 | 0.029595 | 0.13874 | 0.036985 | -0.097207 | 0.007032 | 0.041532 | -0.065533 | -0.012328 | 0.14016 | 0.000682 | 0.079567 | 0.02992 | 0.13698 | 0.10847 | 0.001374 | 0.057061 | 0.16621 | 0.064451 | -0.069741 | 0.034498 | 0.068998 | -0.038067 | 0.015138 | 0.022563 | 0.095128 | 0.029953 | 0.10252
2237.4375 | 122.7402 | -122.4838 | 0.091553 | 0.10812 | -0.031363 | 0.052101 | 0.011611 | 0.10493 | 0.081005 | -0.026092 | 0.029595 | 0.13874 | 0.046142 | -0.10637 | 0.002454 | 0.036954 | -0.070112 | -0.003172 | 0.13558 | -0.003897 | 0.079567 | 0.039077 | 0.1324 | 0.10847 | 0.001374 | 0.057061 | 0.16621 | 0.073608 | -0.078899 | 0.02992 | 0.06442 | -0.042646 | 0.024294 | 0.027141 | 0.099707 | 0.043688 | 0.11625
2239.1875 | 122.7905 | -122.4609 | 0.073242 | 0.098959 | -0.035942 | 0.052101 | 0.002454 | 0.10493 | 0.076426 | -0.03067 | 0.029595 | 0.13874 | 0.046142 | -0.10637 | 0.007032 | 0.032376 | -0.060955 | -0.012328 | 0.12643 | -0.008476 | 0.079567 | 0.02992 | 0.1324 | 0.10389 | -0.003204 | 0.057061 | 0.16621 | 0.073608 | -0.078899 | 0.034498 | 0.059842 | -0.033489 | 0.015138 | 0.022563 | 0.09055 | 0.03911 | 0.1071
2240.9531 | 122.6761 | -122.5296 | 0.11444 | 0.10812 | -0.031363 | 0.052101 | -0.002124 | 0.10951 | 0.085583 | -0.03067 | 0.034174 | 0.14332 | 0.05072 | -0.10179 | 0.007032 | 0.041532 | -0.065533 | -0.016906 | 0.13558 | -0.003897 | 0.079567 | 0.025342 | 0.13698 | 0.11305 | -0.003204 | 0.06164 | 0.17079 | 0.078186 | -0.07432 | 0.034498 | 0.068998 | -0.038067 | 0.01056 | 0.027142 | 0.099707 | 0.043688 | 0.11625
2242.7031 | 122.644 | -122.525 | 0.11444 | 0.11727 | -0.035942 | 0.052101 | 0.002454 | 0.10493 | 0.076426 | -0.021514 | 0.029595 | 0.14332 | 0.046142 | -0.11094 | -0.002124 | 0.041532 | -0.070112 | -0.012328 | 0.14474 | -0.008476 | 0.079567 | 0.02992 | 0.1324 | 0.10389 | 0.005952 | 0.057061 | 0.17079 | 0.073608 | -0.083478 | 0.025342 | 0.068998 | -0.042646 | 0.015138 | 0.031719 | 0.099707 | 0.048266 | 0.11625
2244.375 | 122.731 | -122.493 | 0.11444 | 0.10812 | -0.035942 | 0.056679 | 0.007033 | 0.10493 | 0.076426 | -0.026092 | 0.029595 | 0.1479 | 0.046142 | -0.11094 | 0.002454 | 0.036954 | -0.065533 | -0.016906 | 0.13558 | -0.008476 | 0.084145 | 0.034499 | 0.1324 | 0.10389 | 0.001374 | 0.057061 | 0.17536 | 0.073608 | -0.083478 | 0.02992 | 0.06442 | -0.038067 | 0.01056 | 0.027141 | 0.095128 | 0.043688 | 0.11167
2246.125 | 122.6532 | -122.525 | 0.11902 | 0.10812 | -0.026784 | 0.052101 | -0.006703 | 0.10036 | 0.071848 | -0.026092 | 0.043331 | 0.1479 | 0.05072 | -0.10179 | 0.007032 | 0.036954 | -0.065533 | -0.012328 | 0.13558 | 0.000682 | 0.079567 | 0.020763 | 0.12782 | 0.099314 | 0.001374 | 0.070797 | 0.17536 | 0.078186 | -0.07432 | 0.034498 | 0.06442 | -0.038067 | 0.015138 | 0.036299 | 0.10886 | 0.043688 | 0.11625
2247.875 | 122.7585 | -122.4884 | 0.09613 | 0.11727 | -0.026784 | 0.052101 | -0.006703 | 0.10951 | 0.071848 | -0.03067 | 0.034174 | 0.1479 | 0.05072 | -0.10637 | 0.01161 | 0.041532 | -0.065533 | -0.016906 | 0.14474 | 0.000682 | 0.079567 | 0.020763 | 0.13698 | 0.099314 | -0.003204 | 0.06164 | 0.17536 | 0.078186 | -0.078899 | 0.039076 | 0.068998 | -0.038067 | 0.01056 | 0.022564 | 0.099707 | 0.03911 | 0.11625
2249.625 | 122.6624 | -122.4838 | 0.10529 | 0.10812 | -0.031363 | 0.061258 | -0.002124 | 0.10951 | 0.081005 | -0.026092 | 0.034174 | 0.14332 | 0.059877 | -0.11094 | 0.007032 | 0.036954 | -0.07469 | -0.016906 | 0.13558 | -0.003897 | 0.088724 | 0.025342 | 0.13698 | 0.10847 | 0.001374 | 0.06164 | 0.17079 | 0.087343 | -0.083478 | 0.034498 | 0.06442 | -0.047224 | 0.01056 | 0.027142 | 0.10886 | 0.052845 | 0.13457
2251.3125 | 122.7997 | -122.4792 | 0.07782 | 0.11269 | -0.031363 | 0.052101 | 0.002454 | 0.10951 | 0.081005 | -0.026092 | 0.034174 | 0.14332 | 0.05072 | -0.10637 | 0.007032 | 0.041532 | -0.065533 | -0.016906 | 0.14016 | -0.003897 | 0.079567 | 0.02992 | 0.13698 | 0.10847 | 0.001374 | 0.06164 | 0.17079 | 0.078186 | -0.078899 | 0.034498 | 0.068998 | -0.038067 | 0.01056 | 0.027142 | 0.099707 | 0.043688 | 0.11625
2253.0625 | 122.7997 | -122.4655 | 0.086975 | 0.11269 | -0.031363 | 0.056679 | 0.002454 | 0.10036 | 0.076426 | -0.03067 | 0.038752 | 0.14332 | 0.041563 | -0.11094 | -0.006702 | 0.032376 | -0.070112 | -0.021484 | 0.14016 | -0.003897 | 0.084145 | 0.02992 | 0.12782 | 0.10389 | -0.003204 | 0.066218 | 0.17079 | 0.069029 | -0.083478 | 0.020764 | 0.059842 | -0.042646 | 0.005982 | 0.045454 | 0.10886 | 0.048265 | 0.11167
2254.8281 | 122.7219 | -122.4976 | 0.11444 | 0.11269 | -0.026784 | 0.052101 | 0.002454 | 0.10951 | 0.076426 | -0.03067 | 0.034174 | 0.1479 | 0.046142 | -0.10637 | 0.002454 | 0.032376 | -0.065533 | -0.012328 | 0.14016 | 0.000682 | 0.079567 | 0.02992 | 0.13698 | 0.10389 | -0.003204 | 0.06164 | 0.17536 | 0.073608 | -0.078899 | 0.02992 | 0.059842 | -0.038067 | 0.015138 | 0.03172 | 0.099707 | 0.043688 | 0.11167
2256.5156 | 122.7448 | -122.493 | 0.10071 | 0.10812 | -0.031363 | 0.056679 | 0.002454 | 0.10036 | 0.076426 | -0.021514 | 0.038752 | 0.13874 | 0.055298 | -0.11094 | 0.007032 | 0.041532 | -0.065533 | -0.021484 | 0.13558 | -0.003897 | 0.084145 | 0.02992 | 0.12782 | 0.10389 | 0.005952 | 0.066218 | 0.16621 | 0.082764 | -0.083478 | 0.034498 | 0.068998 | -0.038067 | 0.005982 | 0.03172 | 0.10428 | 0.048266 | 0.12083
2258.2656 | 122.6761 | -122.5296 | 0.1236 | 0.10354 | -0.031363 | 0.052101 | 0.002454 | 0.10951 | 0.076426 | -0.035248 | 0.029595 | 0.15248 | 0.046142 | -0.10637 | 0.007032 | 0.036954 | -0.070112 | -0.012328 | 0.131 | -0.003897 | 0.079567 | 0.02992 | 0.13698 | 0.10389 | -0.007782 | 0.057061 | 0.17994 | 0.073608 | -0.078899 | 0.034498 | 0.06442 | -0.042646 | 0.015138 | 0.022563 | 0.099707 | 0.03911 | 0.11625
2260.0156 | 122.6669 | -122.5204 | 0.12817 | 0.10812 | -0.031363 | 0.056679 | 0.007033 | 0.10036 | 0.076426 | -0.026092 | 0.034174 | 0.1479 | 0.05072 | -0.11094 | 0.007032 | 0.041532 | -0.07469 | -0.016906 | 0.13558 | -0.003897 | 0.084145 | 0.034499 | 0.12782 | 0.10389 | 0.001374 | 0.06164 | 0.17536 | 0.078186 | -0.083478 | 0.034498 | 0.068998 | -0.047224 | 0.01056 | 0.027142 | 0.10886 | 0.043688 | 0.12541
2261.7031 | 122.7768 | -122.4884 | 0.10529 | 0.11269 | -0.035942 | 0.052101 | -0.006703 | 0.10036 | 0.076426 | -0.03067 | 0.029595 | 0.1479 | 0.05072 | -0.10637 | 0.01161 | 0.032376 | -0.065533 | -0.00775 | 0.14016 | -0.008476 | 0.079567 | 0.020763 | 0.12782 | 0.10389 | -0.003204 | 0.057061 | 0.17536 | 0.078186 | -0.078899 | 0.039076 | 0.059842 | -0.038067 | 0.019716 | 0.017985 | 0.095128 | 0.03911 | 0.11625
2263.4531 | 122.8134 | -122.4976 | 0.082397 | 0.11269 | -0.031363 | 0.052101 | 0.007033 | 0.10036 | 0.071848 | -0.03067 | 0.038752 | 0.15248 | 0.05072 | -0.11094 | 0.007032 | 0.036954 | -0.070112 | -0.012328 | 0.14016 | -0.003897 | 0.079567 | 0.034499 | 0.12782 | 0.099314 | -0.003204 | 0.066218 | 0.17994 | 0.078186 | -0.083478 | 0.034498 | 0.06442 | -0.042646 | 0.015138 | 0.03172 | 0.10886 | 0.043688 | 0.12083
2265.1406 | 122.7722 | -122.4701 | 0.091553 | 0.11269 | -0.040521 | 0.056679 | 0.007033 | 0.10951 | 0.071848 | -0.03067 | 0.043331 | 0.14332 | 0.046142 | -0.1201 | 0.007032 | 0.04611 | -0.070112 | -0.016906 | 0.14016 | -0.013055 | 0.084145 | 0.034499 | 0.13698 | 0.099314 | -0.003204 | 0.070797 | 0.17079 | 0.073608 | -0.092637 | 0.034498 | 0.073576 | -0.042646 | 0.01056 | 0.036299 | 0.11344 | 0.03911 | 0.11625
2266.875 | 122.7951 | -122.4838 | 0.091553 | 0.10812 | -0.026784 | 0.052101 | 0.002454 | 0.10036 | 0.076426 | -0.035248 | 0.038752 | 0.14332 | 0.05072 | -0.11094 | 0.01161 | 0.032376 | -0.060955 | -0.00775 | 0.13558 | 0.000682 | 0.079567 | 0.02992 | 0.12782 | 0.10389 | -0.007782 | 0.066218 | 0.17079 | 0.078186 | -0.083478 | 0.039076 | 0.059842 | -0.033489 | 0.019716 | 0.027142 | 0.099707 | 0.03911 | 0.11167
2268.6094 | 122.7951 | -122.4884 | 0.068665 | 0.11727 | -0.031363 | 0.065837 | 0.002454 | 0.10493 | 0.081005 | -0.03067 | 0.034174 | 0.1479 | 0.046142 | -0.11094 | 0.007032 | 0.041532 | -0.065533 | -0.00775 | 0.14474 | -0.003897 | 0.093303 | 0.02992 | 0.1324 | 0.10847 | -0.003204 | 0.06164 | 0.17536 | 0.073608 | -0.083478 | 0.034498 | 0.068998 | -0.038067 | 0.019716 | 0.027142 | 0.099707 | 0.03911 | 0.11167
2270.3594 | 122.7219 | -122.5204 | 0.10071 | 0.11727 | -0.035942 | 0.056679 | 0.007033 | 0.10493 | 0.081005 | -0.026092 | 0.034174 | 0.1479 | 0.046142 | -0.10637 | 0.01161 | 0.041532 | -0.065533 | -0.012328 | 0.14474 | -0.008476 | 0.084145 | 0.034499 | 0.1324 | 0.10847 | 0.001374 | 0.06164 | 0.17536 | 0.073608 | -0.078899 | 0.039076 | 0.068998 | -0.038067 | 0.015138 | 0.022564 | 0.099707 | 0.034532 | 0.11167
2272.1094 | 122.6761 | -122.5204 | 0.1236 | 0.10812 | -0.031363 | 0.061258 | -0.002124 | 0.10493 | 0.081005 | -0.026092 | 0.034174 | 0.14332 | 0.05072 | -0.11552 | 0.002454 | 0.04611 | -0.070112 | -0.012328 | 0.13558 | -0.003897 | 0.088724 | 0.025342 | 0.1324 | 0.10847 | 0.001374 | 0.06164 | 0.17079 | 0.078186 | -0.088057 | 0.02992 | 0.073576 | -0.042646 | 0.015138 | 0.03172 | 0.10429 | 0.048266 | 0.12083
2273.875 | 122.8134 | -122.4838 | 0.091553 | 0.11269 | -0.031363 | 0.052101 | -0.002124 | 0.10493 | 0.085583 | -0.03067 | 0.034174 | 0.14332 | 0.041563 | -0.10637 | 0.007032 | 0.036954 | -0.07469 | -0.021484 | 0.14016 | -0.003897 | 0.079567 | 0.025342 | 0.1324 | 0.11305 | -0.003204 | 0.06164 | 0.17079 | 0.069029 | -0.078899 | 0.034498 | 0.06442 | -0.047224 | 0.005982 | 0.027142 | 0.10886 | 0.034531 | 0.11625
2275.5625 | 122.7264 | -122.5159 | 0.10071 | 0.11269 | -0.031363 | 0.056679 | 0.002454 | 0.10951 | 0.076426 | -0.03067 | 0.029595 | 0.1479 | 0.05072 | -0.11094 | 0.007032 | 0.036954 | -0.065533 | -0.012328 | 0.14016 | -0.003897 | 0.084145 | 0.02992 | 0.13698 | 0.10389 | -0.003204 | 0.057061 | 0.17536 | 0.078186 | -0.083478 | 0.034498 | 0.06442 | -0.038067 | 0.015138 | 0.022563 | 0.095128 | 0.043688 | 0.11625
2277.2969 | 122.7173 | -122.5479 | 0.086975 | 0.10812 | -0.035942 | 0.056679 | 0.002454 | 0.10036 | 0.076426 | -0.021514 | 0.034174 | 0.14332 | 0.05072 | -0.10637 | 0.007032 | 0.032376 | -0.065533 | -0.012328 | 0.13558 | -0.008476 | 0.084145 | 0.02992 | 0.12782 | 0.10389 | 0.005952 | 0.06164 | 0.17079 | 0.078186 | -0.078899 | 0.034498 | 0.059842 | -0.038067 | 0.015138 | 0.027142 | 0.099707 | 0.043688 | 0.11625
2279.0625 | 122.7081 | -122.5342 | 0.10986 | 0.11269 | -0.035942 | 0.052101 | 0.007033 | 0.10493 | 0.081005 | -0.03067 | 0.034174 | 0.14332 | 0.05072 | -0.097207 | 0.007032 | 0.036954 | -0.070112 | -0.012328 | 0.14016 | -0.008476 | 0.079567 | 0.034499 | 0.1324 | 0.10847 | -0.003204 | 0.06164 | 0.17079 | 0.078186 | -0.069741 | 0.034498 | 0.06442 | -0.042646 | 0.015138 | 0.027142 | 0.10429 | 0.043688 | 0.12083
2280.75 | 122.7173 | -122.525 | 0.11444 | 0.11269 | -0.026784 | 0.056679 | 0.002454 | 0.11409 | 0.085583 | -0.03067 | 0.038752 | 0.13874 | 0.041563 | -0.11094 | 0.002454 | 0.027798 | -0.065533 | -0.016906 | 0.14016 | 0.000682 | 0.084145 | 0.02992 | 0.14156 | 0.11305 | -0.003204 | 0.066218 | 0.16621 | 0.069029 | -0.083478 | 0.02992 | 0.055264 | -0.038067 | 0.01056 | 0.036298 | 0.10428 | 0.039109 | 0.1071
2282.4844 | 122.731 | -122.5388 | 0.10986 | 0.11269 | -0.031363 | 0.052101 | -0.002124 | 0.10493 | 0.076426 | -0.03067 | 0.034174 | 0.14332 | 0.046142 | -0.10637 | -0.002124 | 0.036954 | -0.065533 | -0.016906 | 0.14016 | -0.003897 | 0.079567 | 0.025342 | 0.1324 | 0.10389 | -0.003204 | 0.06164 | 0.17079 | 0.073608 | -0.078899 | 0.025342 | 0.06442 | -0.038067 | 0.01056 | 0.036298 | 0.099707 | 0.048266 | 0.11167
2284.2031 | 122.6669 | -122.5525 | 0.10529 | 0.11727 | -0.040521 | 0.056679 | 0.002454 | 0.10951 | 0.076426 | -0.026092 | 0.034174 | 0.14332 | 0.041563 | -0.11552 | 0.007032 | 0.036954 | -0.065533 | -0.016906 | 0.14474 | -0.013055 | 0.084145 | 0.02992 | 0.13698 | 0.10389 | 0.001374 | 0.06164 | 0.17079 | 0.069029 | -0.088057 | 0.034498 | 0.06442 | -0.038067 | 0.01056 | 0.027142 | 0.099707 | 0.034531 | 0.1071
2285.9219 | 122.7676 | -122.5021 | 0.091553 | 0.11269 | -0.035942 | 0.056679 | -0.002124 | 0.10951 | 0.071848 | -0.026092 | 0.034174 | 0.14332 | 0.046142 | -0.10637 | 0.007032 | 0.032376 | -0.07469 | -0.012328 | 0.14016 | -0.008476 | 0.084145 | 0.025342 | 0.13698 | 0.099314 | 0.001374 | 0.06164 | 0.17079 | 0.073608 | -0.078899 | 0.034498 | 0.059842 | -0.047224 | 0.015138 | 0.027142 | 0.10886 | 0.03911 | 0.12083
2287.6719 | 122.7859 | -122.4976 | 0.086975 | 0.10812 | -0.035942 | 0.052101 | 0.007033 | 0.10951 | 0.081005 | -0.03067 | 0.034174 | 0.14332 | 0.046142 | -0.11094 | 0.002454 | 0.036954 | -0.07469 | -0.012328 | 0.13558 | -0.008476 | 0.079567 | 0.034499 | 0.13698 | 0.10847 | -0.003204 | 0.06164 | 0.17079 | 0.073608 | -0.083478 | 0.02992 | 0.06442 | -0.047224 | 0.015138 | 0.03172 | 0.10886 | 0.043688 | 0.12083
2289.4219 | 122.7676 | -122.5021 | 0.10529 | 0.11269 | -0.035942 | 0.052101 | -0.002124 | 0.11867 | 0.071848 | -0.026092 | 0.034174 | 0.1479 | 0.041563 | -0.10637 | -0.002124 | 0.036954 | -0.065533 | -0.012328 | 0.14016 | -0.008476 | 0.079567 | 0.025342 | 0.14613 | 0.099314 | 0.001374 | 0.06164 | 0.17536 | 0.069029 | -0.078899 | 0.025342 | 0.06442 | -0.038067 | 0.015138 | 0.036298 | 0.099707 | 0.043687 | 0.1071
2291.125 | 122.6944 | -122.5525 | 0.13275 | 0.11727 | -0.031363 | 0.061258 | 0.002454 | 0.11409 | 0.081005 | -0.026092 | 0.034174 | 0.13874 | 0.046142 | -0.11094 | 0.007032 | 0.041532 | -0.065533 | -0.016906 | 0.14474 | -0.003897 | 0.088724 | 0.02992 | 0.14156 | 0.10847 | 0.001374 | 0.06164 | 0.16621 | 0.073608 | -0.083478 | 0.034498 | 0.068998 | -0.038067 | 0.01056 | 0.027142 | 0.099707 | 0.03911 | 0.11167
2292.875 | 122.699 | -122.5021 | 0.11444 | 0.11727 | -0.035942 | 0.052101 | 0.007033 | 0.10036 | 0.071848 | -0.03067 | 0.043331 | 0.13874 | 0.05072 | -0.11094 | 0.007032 | 0.036954 | -0.070112 | -0.012328 | 0.14474 | -0.008476 | 0.079567 | 0.034499 | 0.12782 | 0.099314 | -0.003204 | 0.070797 | 0.16621 | 0.078186 | -0.083478 | 0.034498 | 0.06442 | -0.042646 | 0.015138 | 0.036299 | 0.11344 | 0.043688 | 0.12083
2294.5469 | 122.8546 | -122.4792 | 0.068665 | 0.11727 | -0.040521 | 0.056679 | 0.002454 | 0.10951 | 0.081005 | -0.03067 | 0.029595 | 0.15248 | 0.05072 | -0.10637 | 0.016188 | 0.027798 | -0.070112 | -0.00775 | 0.14474 | -0.013055 | 0.084145 | 0.02992 | 0.13698 | 0.10847 | -0.003204 | 0.057061 | 0.17994 | 0.078186 | -0.078899 | 0.043654 | 0.055264 | -0.042646 | 0.019716 | 0.013407 | 0.099707 | 0.034532 | 0.12083
2296.2969 | 122.699 | -122.5479 | 0.13275 | 0.11269 | -0.035942 | 0.056679 | -0.002124 | 0.10951 | 0.085583 | -0.03067 | 0.034174 | 0.15248 | 0.041563 | -0.10637 | 0.01161 | 0.032376 | -0.065533 | -0.021484 | 0.14016 | -0.008476 | 0.084145 | 0.025342 | 0.13698 | 0.11305 | -0.003204 | 0.06164 | 0.17994 | 0.069029 | -0.078899 | 0.039076 | 0.059842 | -0.038067 | 0.005982 | 0.022564 | 0.099707 | 0.029953 | 0.1071
2297.9688 | 122.6898 | -122.5616 | 0.11902 | 0.11269 | -0.031363 | 0.052101 | -0.002124 | 0.10951 | 0.076426 | -0.03067 | 0.025017 | 0.14332 | 0.05072 | -0.10637 | 0.007032 | 0.041532 | -0.065533 | -0.012328 | 0.14016 | -0.003897 | 0.079567 | 0.025342 | 0.13698 | 0.10389 | -0.003204 | 0.052483 | 0.17079 | 0.078186 | -0.078899 | 0.034498 | 0.068998 | -0.038067 | 0.015138 | 0.017985 | 0.09055 | 0.043688 | 0.11625
2299.7188 | 122.7264 | -122.5388 | 0.091553 | 0.10812 | -0.040521 | 0.052101 | 0.002454 | 0.10493 | 0.076426 | -0.03067 | 0.034174 | 0.13874 | 0.036985 | -0.097207 | 0.007032 | 0.032376 | -0.070112 | -0.016906 | 0.13558 | -0.013055 | 0.079567 | 0.02992 | 0.1324 | 0.10389 | -0.003204 | 0.06164 | 0.16621 | 0.064451 | -0.069741 | 0.034498 | 0.059842 | -0.042646 | 0.01056 | 0.027142 | 0.10429 | 0.029953 | 0.1071
2301.4062 | 122.731 | -122.5296 | 0.10071 | 0.11269 | -0.031363 | 0.056679 | -0.002124 | 0.11409 | 0.076426 | -0.026092 | 0.029595 | 0.14332 | 0.055298 | -0.10179 | 0.007032 | 0.036954 | -0.070112 | -0.012328 | 0.14016 | -0.003897 | 0.084145 | 0.025342 | 0.14156 | 0.10389 | 0.001374 | 0.057061 | 0.17079 | 0.082764 | -0.07432 | 0.034498 | 0.06442 | -0.042646 | 0.015138 | 0.022563 | 0.099707 | 0.048266 | 0.12541
2303.1406 | 122.6852 | -122.5662 | 0.11444 | 0.12185 | -0.031363 | 0.052101 | 0.007033 | 0.10493 | 0.076426 | -0.026092 | 0.043331 | 0.15248 | 0.055298 | -0.11094 | 0.01161 | 0.032376 | -0.070112 | -0.012328 | 0.14932 | -0.003897 | 0.079567 | 0.034499 | 0.1324 | 0.10389 | 0.001374 | 0.070797 | 0.17994 | 0.082764 | -0.083478 | 0.039076 | 0.059842 | -0.042646 | 0.015138 | 0.031721 | 0.11344 | 0.043688 | 0.12541
2304.8906 | 122.7768 | -122.525 | 0.10529 | 0.11727 | -0.031363 | 0.052101 | 0.002454 | 0.10036 | 0.076426 | -0.016936 | 0.029595 | 0.15248 | 0.041563 | -0.11094 | 0.01161 | 0.036954 | -0.070112 | -0.016906 | 0.14474 | -0.003897 | 0.079567 | 0.02992 | 0.12782 | 0.10389 | 0.01053 | 0.057061 | 0.17994 | 0.069029 | -0.083478 | 0.039076 | 0.06442 | -0.042646 | 0.01056 | 0.017985 | 0.099707 | 0.029953 | 0.11167
2306.5781 | 122.6898 | -122.5433 | 0.1236 | 0.12185 | -0.035942 | 0.047522 | 0.002454 | 0.10493 | 0.076426 | -0.026092 | 0.038752 | 0.14332 | 0.046142 | -0.11094 | 0.002454 | 0.036954 | -0.07469 | -0.012328 | 0.14932 | -0.008476 | 0.074988 | 0.02992 | 0.1324 | 0.10389 | 0.001374 | 0.066218 | 0.17079 | 0.073608 | -0.083478 | 0.02992 | 0.06442 | -0.047224 | 0.015138 | 0.036298 | 0.11344 | 0.043688 | 0.12083
2308.3281 | 122.7493 | -122.5342 | 0.10529 | 0.11727 | -0.031363 | 0.056679 | 0.011611 | 0.10951 | 0.081005 | -0.021514 | 0.038752 | 0.15248 | 0.041563 | -0.10637 | 0.002454 | 0.036954 | -0.065533 | -0.012328 | 0.14474 | -0.003897 | 0.084145 | 0.039077 | 0.13698 | 0.10847 | 0.005952 | 0.066218 | 0.17994 | 0.069029 | -0.078899 | 0.02992 | 0.06442 | -0.038067 | 0.015138 | 0.036298 | 0.10428 | 0.039109 | 0.1071
2310.0781 | 122.7814 | -122.5204 | 0.073242 | 0.11269 | -0.035942 | 0.052101 | -0.002124 | 0.10951 | 0.076426 | -0.035248 | 0.034174 | 0.1479 | 0.036985 | -0.11094 | 0.002454 | 0.036954 | -0.065533 | -0.012328 | 0.14016 | -0.008476 | 0.079567 | 0.025342 | 0.13698 | 0.10389 | -0.007782 | 0.06164 | 0.17536 | 0.064451 | -0.083478 | 0.02992 | 0.06442 | -0.038067 | 0.015138 | 0.03172 | 0.099707 | 0.034531 | 0.10252
2311.8281 | 122.7859 | -122.5113 | 0.086975 | 0.11269 | -0.031363 | 0.052101 | 0.007033 | 0.10951 | 0.076426 | -0.03067 | 0.034174 | 0.15248 | 0.041563 | -0.11094 | -0.002124 | 0.032376 | -0.065533 | -0.012328 | 0.14016 | -0.003897 | 0.079567 | 0.034499 | 0.13698 | 0.10389 | -0.003204 | 0.06164 | 0.17994 | 0.069029 | -0.083478 | 0.025342 | 0.059842 | -0.038067 | 0.015138 | 0.036298 | 0.099707 | 0.043687 | 0.1071
2313.5938 | 122.7402 | -122.5479 | 0.11444 | 0.10812 | -0.026784 | 0.061258 | 0.002454 | 0.11409 | 0.085583 | -0.03067 | 0.034174 | 0.1479 | 0.032407 | -0.11094 | 0.01161 | 0.036954 | -0.070112 | -0.016906 | 0.13558 | 0.000682 | 0.088724 | 0.02992 | 0.14156 | 0.11305 | -0.003204 | 0.06164 | 0.17536 | 0.059873 | -0.083478 | 0.039076 | 0.06442 | -0.042646 | 0.01056 | 0.022564 | 0.10429 | 0.020797 | 0.10252
2315.2812 | 122.8409 | -122.525 | 0.086975 | 0.11269 | -0.031363 | 0.056679 | 0.002454 | 0.10493 | 0.081005 | -0.026092 | 0.043331 | 0.1479 | 0.046142 | -0.10637 | 0.007032 | 0.036954 | -0.065533 | -0.016906 | 0.14016 | -0.003897 | 0.084145 | 0.02992 | 0.1324 | 0.10847 | 0.001374 | 0.070797 | 0.17536 | 0.073608 | -0.078899 | 0.034498 | 0.06442 | -0.038067 | 0.01056 | 0.036299 | 0.10886 | 0.03911 | 0.11167
2317.0312 | 122.7219 | -122.5662 | 0.10529 | 0.10812 | -0.022205 | 0.056679 | 0.002454 | 0.10493 | 0.076426 | -0.03067 | 0.038752 | 0.14332 | 0.046142 | -0.11094 | 0.002454 | 0.036954 | -0.065533 | -0.012328 | 0.13558 | 0.005261 | 0.084145 | 0.02992 | 0.1324 | 0.10389 | -0.003204 | 0.066218 | 0.17079 | 0.073608 | -0.083478 | 0.02992 | 0.06442 | -0.038067 | 0.015138 | 0.036298 | 0.10428 | 0.043688 | 0.11167
2318.7812 | 122.7448 | -122.5388 | 0.10529 | 0.11727 | -0.026784 | 0.061258 | 0.007033 | 0.10493 | 0.076426 | -0.021514 | 0.038752 | 0.1479 | 0.055298 | -0.10637 | 0.002454 | 0.036954 | -0.070112 | -0.016906 | 0.14474 | 0.000682 | 0.088724 | 0.034499 | 0.1324 | 0.10389 | 0.005952 | 0.066218 | 0.17536 | 0.082764 | -0.078899 | 0.02992 | 0.06442 | -0.042646 | 0.01056 | 0.036298 | 0.10886 | 0.052844 | 0.12541
2320.4688 | 122.699 | -122.5433 | 0.12817 | 0.11727 | -0.031363 | 0.056679 | 0.011611 | 0.10951 | 0.081005 | -0.035248 | 0.034174 | 0.1479 | 0.036985 | -0.10179 | 0.007032 | 0.032376 | -0.060955 | -0.012328 | 0.14474 | -0.003897 | 0.084145 | 0.039077 | 0.13698 | 0.10847 | -0.007782 | 0.06164 | 0.17536 | 0.064451 | -0.07432 | 0.034498 | 0.059842 | -0.033489 | 0.015138 | 0.027142 | 0.095129 | 0.029953 | 0.09794
2322.2031 | 122.7585 | -122.5388 | 0.10986 | 0.10812 | -0.035942 | 0.061258 | 0.002454 | 0.10951 | 0.081005 | -0.035248 | 0.034174 | 0.14332 | 0.046142 | -0.11094 | 0.002454 | 0.032376 | -0.065533 | -0.012328 | 0.13558 | -0.008476 | 0.088724 | 0.02992 | 0.13698 | 0.10847 | -0.007782 | 0.06164 | 0.17079 | 0.073608 | -0.083478 | 0.02992 | 0.059842 | -0.038067 | 0.015138 | 0.03172 | 0.099707 | 0.043688 | 0.11167
2323.9531 | 122.7951 | -122.5204 | 0.09613 | 0.11269 | -0.035942 | 0.056679 | -0.006703 | 0.10493 | 0.076426 | -0.03067 | 0.034174 | 0.1479 | 0.046142 | -0.11094 | -0.002124 | 0.036954 | -0.070112 | -0.00775 | 0.14016 | -0.008476 | 0.084145 | 0.020763 | 0.1324 | 0.10389 | -0.003204 | 0.06164 | 0.17536 | 0.073608 | -0.083478 | 0.025342 | 0.06442 | -0.042646 | 0.019716 | 0.036298 | 0.10429 | 0.048266 | 0.11625
2325.7188 | 122.8363 | -122.4976 | 0.09613 | 0.11269 | -0.035942 | 0.056679 | 0.002454 | 0.10951 | 0.071848 | -0.026092 | 0.034174 | 0.1479 | 0.05072 | -0.10637 | 0.01161 | 0.041532 | -0.070112 | -0.00775 | 0.14016 | -0.008476 | 0.084145 | 0.02992 | 0.13698 | 0.099314 | 0.001374 | 0.06164 | 0.17536 | 0.078186 | -0.078899 | 0.039076 | 0.068998 | -0.042646 | 0.019716 | 0.022564 | 0.10429 | 0.03911 | 0.12083
2327.3906 | 122.8455 | -122.5067 | 0.10986 | 0.12185 | -0.031363 | 0.052101 | 0.007033 | 0.11409 | 0.071848 | -0.03067 | 0.034174 | 0.15248 | 0.055298 | -0.10637 | 0.01161 | 0.036954 | -0.070112 | -0.026063 | 0.14932 | -0.003897 | 0.079567 | 0.034499 | 0.14156 | 0.099314 | -0.003204 | 0.06164 | 0.17994 | 0.082764 | -0.078899 | 0.039076 | 0.06442 | -0.042646 | 0.001403 | 0.022564 | 0.10429 | 0.043688 | 0.12541
2329.0781 | 122.8226 | -122.5113 | 0.082397 | 0.11269 | -0.031363 | 0.052101 | 0.002454 | 0.10951 | 0.076426 | -0.026092 | 0.029595 | 0.1479 | 0.046142 | -0.10179 | 0.002454 | 0.032376 | -0.065533 | -0.016906 | 0.14016 | -0.003897 | 0.079567 | 0.02992 | 0.13698 | 0.10389 | 0.001374 | 0.057061 | 0.17536 | 0.073608 | -0.07432 | 0.02992 | 0.059842 | -0.038067 | 0.01056 | 0.027141 | 0.095128 | 0.043688 | 0.11167
2330.8438 | 122.7722 | -122.5433 | 0.082397 | 0.10812 | -0.040521 | 0.056679 | 0.002454 | 0.10036 | 0.071848 | -0.026092 | 0.034174 | 0.15248 | 0.05072 | -0.10637 | 0.002454 | 0.032376 | -0.070112 | -0.012328 | 0.13558 | -0.013055 | 0.084145 | 0.02992 | 0.12782 | 0.099314 | 0.001374 | 0.06164 | 0.17994 | 0.078186 | -0.078899 | 0.02992 | 0.059842 | -0.042646 | 0.015138 | 0.03172 | 0.10429 | 0.048266 | 0.12083
2332.5938 | 122.731 | -122.5571 | 0.11444 | 0.11727 | -0.035942 | 0.056679 | 0.002454 | 0.10951 | 0.076426 | -0.026092 | 0.038752 | 0.1479 | 0.046142 | -0.11094 | -0.002124 | 0.036954 | -0.065533 | -0.016906 | 0.14474 | -0.008476 | 0.084145 | 0.02992 | 0.13698 | 0.10389 | 0.001374 | 0.066218 | 0.17536 | 0.073608 | -0.083478 | 0.025342 | 0.06442 | -0.038067 | 0.01056 | 0.040876 | 0.10428 | 0.048266 | 0.11167
2334.3438 | 122.7356 | -122.5479 | 0.091553 | 0.11727 | -0.031363 | 0.065837 | 0.007033 | 0.10493 | 0.076426 | -0.026092 | 0.029595 | 0.1479 | 0.046142 | -0.10637 | 0.007032 | 0.036954 | -0.070112 | -0.012328 | 0.14474 | -0.003897 | 0.093303 | 0.034499 | 0.1324 | 0.10389 | 0.001374 | 0.057061 | 0.17536 | 0.073608 | -0.078899 | 0.034498 | 0.06442 | -0.042646 | 0.015138 | 0.022563 | 0.099707 | 0.03911 | 0.11625
2336.1094 | 122.7448 | -122.5388 | 0.1236 | 0.11727 | -0.031363 | 0.056679 | 0.007033 | 0.11409 | 0.071848 | -0.026092 | 0.038752 | 0.14332 | 0.055298 | -0.10637 | 0.01161 | 0.041532 | -0.065533 | -0.016906 | 0.14474 | -0.003897 | 0.084145 | 0.034499 | 0.14156 | 0.099314 | 0.001374 | 0.066218 | 0.17079 | 0.082764 | -0.078899 | 0.039076 | 0.068998 | -0.038067 | 0.01056 | 0.027142 | 0.10428 | 0.043688 | 0.12083
2337.7969 | 122.7356 | -122.5708 | 0.10529 | 0.10812 | -0.035942 | 0.052101 | 0.002454 | 0.10036 | 0.076426 | -0.039826 | 0.034174 | 0.1479 | 0.05072 | -0.11094 | 0.007032 | 0.036954 | -0.070112 | -0.012328 | 0.13558 | -0.008476 | 0.079567 | 0.02992 | 0.12782 | 0.10389 | -0.01236 | 0.06164 | 0.17536 | 0.078186 | -0.083478 | 0.034498 | 0.06442 | -0.042646 | 0.015138 | 0.027142 | 0.10429 | 0.043688 | 0.12083
2339.5469 | 122.85 | -122.5388 | 0.082397 | 0.10812 | -0.026784 | 0.047522 | 0.002454 | 0.10951 | 0.071848 | -0.03067 | 0.034174 | 0.14332 | 0.046142 | -0.10179 | 0.01161 | 0.036954 | -0.056376 | -0.012328 | 0.13558 | 0.000682 | 0.074988 | 0.02992 | 0.13698 | 0.099314 | -0.003204 | 0.06164 | 0.17079 | 0.073608 | -0.07432 | 0.039076 | 0.06442 | -0.02891 | 0.015138 | 0.022564 | 0.09055 | 0.034532 | 0.10252
2341.2969 | 122.7448 | -122.5616 | 0.086975 | 0.11727 | -0.040521 | 0.052101 | 0.002454 | 0.10493 | 0.071848 | -0.026092 | 0.025017 | 0.14332 | 0.046142 | -0.10637 | 0.007032 | 0.032376 | -0.070112 | -0.012328 | 0.14474 | -0.013055 | 0.079567 | 0.02992 | 0.1324 | 0.099314 | 0.001374 | 0.052483 | 0.17079 | 0.073608 | -0.078899 | 0.034498 | 0.059842 | -0.042646 | 0.015138 | 0.017985 | 0.095129 | 0.03911 | 0.11625
2343.0469 | 122.7814 | -122.5571 | 0.1236 | 0.11269 | -0.035942 | 0.052101 | -0.002124 | 0.11409 | 0.081005 | -0.035248 | 0.043331 | 0.13874 | 0.046142 | -0.10637 | 0.01161 | 0.036954 | -0.065533 | -0.012328 | 0.14016 | -0.008476 | 0.079567 | 0.025342 | 0.14156 | 0.10847 | -0.007782 | 0.070797 | 0.16621 | 0.073608 | -0.078899 | 0.039076 | 0.06442 | -0.038067 | 0.015138 | 0.031721 | 0.10886 | 0.034532 | 0.11167
2344.7344 | 122.8455 | -122.5113 | 0.082397 | 0.10812 | -0.0451 | 0.047522 | -0.002124 | 0.11409 | 0.081005 | -0.03067 | 0.034174 | 0.1479 | 0.046142 | -0.10179 | -0.002124 | 0.041532 | -0.070112 | -0.016906 | 0.13558 | -0.017634 | 0.074988 | 0.025342 | 0.14156 | 0.10847 | -0.003204 | 0.06164 | 0.17536 | 0.073608 | -0.07432 | 0.025342 | 0.068998 | -0.042646 | 0.01056 | 0.036298 | 0.10429 | 0.048266 | 0.11625
2346.5 | 122.7127 | -122.5891 | 0.11902 | 0.11269 | -0.040521 | 0.052101 | 0.002454 | 0.10951 | 0.076426 | -0.021514 | 0.029595 | 0.14332 | 0.041563 | -0.10179 | 0.002454 | 0.032376 | -0.065533 | -0.021484 | 0.14016 | -0.013055 | 0.079567 | 0.02992 | 0.13698 | 0.10389 | 0.005952 | 0.057061 | 0.17079 | 0.069029 | -0.07432 | 0.02992 | 0.059842 | -0.038067 | 0.005982 | 0.027141 | 0.095128 | 0.039109 | 0.1071
2348.1719 | 122.7173 | -122.58 | 0.10529 | 0.11727 | -0.035942 | 0.056679 | 0.007033 | 0.10951 | 0.076426 | -0.026092 | 0.034174 | 0.14332 | 0.05072 | -0.10637 | 0.007032 | 0.032376 | -0.060955 | -0.016906 | 0.14474 | -0.008476 | 0.084145 | 0.034499 | 0.13698 | 0.10389 | 0.001374 | 0.06164 | 0.17079 | 0.078186 | -0.078899 | 0.034498 | 0.059842 | -0.033489 | 0.01056 | 0.027142 | 0.095129 | 0.043688 | 0.11167
2349.9062 | 122.8592 | -122.5021 | 0.064087 | 0.11269 | -0.031363 | 0.047522 | 0.002454 | 0.10951 | 0.076426 | -0.026092 | 0.038752 | 0.14332 | 0.05072 | -0.11094 | 0.002454 | 0.036954 | -0.070112 | -0.012328 | 0.14016 | -0.003897 | 0.074988 | 0.02992 | 0.13698 | 0.10389 | 0.001374 | 0.066218 | 0.17079 | 0.078186 | -0.083478 | 0.02992 | 0.06442 | -0.042646 | 0.015138 | 0.036298 | 0.10886 | 0.048266 | 0.12083
2351.5938 | 122.818 | -122.525 | 0.082397 | 0.11727 | -0.035942 | 0.052101 | 0.007033 | 0.10036 | 0.071848 | -0.021514 | 0.034174 | 0.13874 | 0.046142 | -0.10637 | 0.01161 | 0.041532 | -0.070112 | -0.016906 | 0.14474 | -0.008476 | 0.079567 | 0.034499 | 0.12782 | 0.099314 | 0.005952 | 0.06164 | 0.16621 | 0.073608 | -0.078899 | 0.039076 | 0.068998 | -0.042646 | 0.01056 | 0.022564 | 0.10429 | 0.034532 | 0.11625
2353.3281 | 122.8592 | -122.5479 | 0.054932 | 0.10812 | -0.035942 | 0.056679 | -0.002124 | 0.10951 | 0.081005 | -0.03067 | 0.043331 | 0.1479 | 0.046142 | -0.10637 | 0.002454 | 0.041532 | -0.070112 | -0.026063 | 0.13558 | -0.008476 | 0.084145 | 0.025342 | 0.13698 | 0.10847 | -0.003204 | 0.070797 | 0.17536 | 0.073608 | -0.078899 | 0.02992 | 0.068998 | -0.042646 | 0.001403 | 0.040877 | 0.11344 | 0.043688 | 0.11625
2355.0625 | 122.7448 | -122.5616 | 0.11902 | 0.11727 | -0.031363 | 0.061258 | 0.01619 | 0.10951 | 0.076426 | -0.03067 | 0.038752 | 0.13874 | 0.046142 | -0.11094 | 0.002454 | 0.036954 | -0.065533 | -0.012328 | 0.14474 | -0.003897 | 0.088724 | 0.043656 | 0.13698 | 0.10389 | -0.003204 | 0.066218 | 0.16621 | 0.073608 | -0.083478 | 0.02992 | 0.06442 | -0.038067 | 0.015138 | 0.036298 | 0.10428 | 0.043688 | 0.11167
2356.8125 | 122.8271 | -122.5479 | 0.073242 | 0.12185 | -0.031363 | 0.056679 | -0.006703 | 0.10493 | 0.071848 | -0.03067 | 0.038752 | 0.15248 | 0.036985 | -0.10637 | 0.002454 | 0.036954 | -0.070112 | -0.012328 | 0.14932 | -0.003897 | 0.084145 | 0.020763 | 0.1324 | 0.099314 | -0.003204 | 0.066218 | 0.17994 | 0.064451 | -0.078899 | 0.02992 | 0.06442 | -0.042646 | 0.015138 | 0.036298 | 0.10886 | 0.034531 | 0.1071
2358.5 | 122.8043 | -122.5433 | 0.09613 | 0.11727 | -0.035942 | 0.056679 | -0.002124 | 0.10493 | 0.081005 | -0.035248 | 0.038752 | 0.15248 | 0.032407 | -0.10179 | 0.002454 | 0.036954 | -0.070112 | -0.012328 | 0.14474 | -0.008476 | 0.084145 | 0.025342 | 0.1324 | 0.10847 | -0.007782 | 0.066218 | 0.17994 | 0.059873 | -0.07432 | 0.02992 | 0.06442 | -0.042646 | 0.015138 | 0.036298 | 0.10886 | 0.029953 | 0.10252
2360.25 | 122.7402 | -122.5571 | 0.11444 | 0.11727 | -0.035942 | 0.052101 | 0.002454 | 0.10493 | 0.076426 | -0.026092 | 0.029595 | 0.1479 | 0.05072 | -0.11094 | 0.002454 | 0.032376 | -0.070112 | -0.016906 | 0.14474 | -0.008476 | 0.079567 | 0.02992 | 0.1324 | 0.10389 | 0.001374 | 0.057061 | 0.17536 | 0.078186 | -0.083478 | 0.02992 | 0.059842 | -0.042646 | 0.01056 | 0.027141 | 0.099707 | 0.048266 | 0.12083
2362 | 122.7814 | -122.5525 | 0.10529 | 0.11727 | -0.022205 | 0.061258 | 0.007033 | 0.10493 | 0.081005 | -0.021514 | 0.029595 | 0.14332 | 0.05072 | -0.10637 | 0.01161 | 0.036954 | -0.07469 | -0.016906 | 0.14474 | 0.005261 | 0.088724 | 0.034499 | 0.1324 | 0.10847 | 0.005952 | 0.057061 | 0.17079 | 0.078186 | -0.078899 | 0.039076 | 0.06442 | -0.047224 | 0.01056 | 0.017985 | 0.10429 | 0.03911 | 0.12541
2363.75 | 122.7356 | -122.5891 | 0.11444 | 0.11727 | -0.035942 | 0.056679 | -0.002124 | 0.10493 | 0.076426 | -0.021514 | 0.029595 | 0.14332 | 0.055298 | -0.10179 | 0.002454 | 0.041532 | -0.065533 | -0.016906 | 0.14474 | -0.008476 | 0.084145 | 0.025342 | 0.1324 | 0.10389 | 0.005952 | 0.057061 | 0.17079 | 0.082764 | -0.07432 | 0.02992 | 0.068998 | -0.038067 | 0.01056 | 0.027141 | 0.095128 | 0.052844 | 0.12083
2365.4219 | 122.8134 | -122.5342 | 0.086975 | 0.11727 | -0.031363 | 0.047522 | 0.002454 | 0.10036 | 0.085583 | -0.026092 | 0.029595 | 0.14332 | 0.05072 | -0.11094 | 0.007032 | 0.041532 | -0.070112 | -0.016906 | 0.14474 | -0.003897 | 0.074988 | 0.02992 | 0.12782 | 0.11305 | 0.001374 | 0.057061 | 0.17079 | 0.078186 | -0.083478 | 0.034498 | 0.068998 | -0.042646 | 0.01056 | 0.022563 | 0.099707 | 0.043688 | 0.12083
2367.1719 | 122.7402 | -122.5845 | 0.1236 | 0.10812 | -0.031363 | 0.056679 | 0.002454 | 0.10951 | 0.076426 | -0.03067 | 0.034174 | 0.1479 | 0.059877 | -0.10637 | 0.002454 | 0.041532 | -0.060955 | -0.012328 | 0.13558 | -0.003897 | 0.084145 | 0.02992 | 0.13698 | 0.10389 | -0.003204 | 0.06164 | 0.17536 | 0.087343 | -0.078899 | 0.02992 | 0.068998 | -0.033489 | 0.015138 | 0.03172 | 0.095129 | 0.057423 | 0.12083
2368.8594 | 122.8638 | -122.5616 | 0.09613 | 0.11727 | -0.031363 | 0.061258 | 0.007033 | 0.10493 | 0.081005 | -0.026092 | 0.029595 | 0.14332 | 0.041563 | -0.10637 | 0.007032 | 0.036954 | -0.065533 | -0.016906 | 0.14474 | -0.003897 | 0.088724 | 0.034499 | 0.1324 | 0.10847 | 0.001374 | 0.057061 | 0.17079 | 0.069029 | -0.078899 | 0.034498 | 0.06442 | -0.038067 | 0.01056 | 0.022563 | 0.095128 | 0.034531 | 0.1071
2370.6094 | 122.731 | -122.5571 | 0.10529 | 0.11269 | -0.031363 | 0.056679 | 0.002454 | 0.11409 | 0.071848 | -0.021514 | 0.034174 | 0.13874 | 0.05072 | -0.10179 | -0.002124 | 0.036954 | -0.065533 | -0.016906 | 0.14016 | -0.003897 | 0.084145 | 0.02992 | 0.14156 | 0.099314 | 0.005952 | 0.06164 | 0.16621 | 0.078186 | -0.07432 | 0.025342 | 0.06442 | -0.038067 | 0.01056 | 0.036298 | 0.099707 | 0.052844 | 0.11625
2372.2969 | 122.7768 | -122.5708 | 0.11444 | 0.11727 | -0.026784 | 0.047522 | 0.007033 | 0.10493 | 0.081005 | -0.03067 | 0.034174 | 0.1479 | 0.046142 | -0.11094 | 0.01161 | 0.032376 | -0.070112 | -0.012328 | 0.14474 | 0.000682 | 0.074988 | 0.034499 | 0.1324 | 0.10847 | -0.003204 | 0.06164 | 0.17536 | 0.073608 | -0.083478 | 0.039076 | 0.059842 | -0.042646 | 0.015138 | 0.022564 | 0.10429 | 0.034532 | 0.11625
2373.9688 | 122.7448 | -122.5845 | 0.1236 | 0.12185 | -0.031363 | 0.061258 | 0.002454 | 0.10951 | 0.071848 | -0.021514 | 0.025017 | 0.1479 | 0.05072 | -0.10637 | 0.01161 | 0.036954 | -0.065533 | -0.016906 | 0.14932 | -0.003897 | 0.088724 | 0.02992 | 0.13698 | 0.099314 | 0.005952 | 0.052483 | 0.17536 | 0.078186 | -0.078899 | 0.039076 | 0.06442 | -0.038067 | 0.01056 | 0.013407 | 0.09055 | 0.03911 | 0.11625
2375.6562 | 122.8683 | -122.5342 | 0.082397 | 0.11269 | -0.026784 | 0.047522 | 0.002454 | 0.10951 | 0.076426 | -0.026092 | 0.038752 | 0.1479 | 0.05072 | -0.10179 | 0.002454 | 0.036954 | -0.065533 | -0.012328 | 0.14016 | 0.000682 | 0.074988 | 0.02992 | 0.13698 | 0.10389 | 0.001374 | 0.066218 | 0.17536 | 0.078186 | -0.07432 | 0.02992 | 0.06442 | -0.038067 | 0.015138 | 0.036298 | 0.10428 | 0.048266 | 0.11625
2377.3906 | 122.8546 | -122.5433 | 0.091553 | 0.11269 | -0.031363 | 0.052101 | 0.002454 | 0.10493 | 0.071848 | -0.026092 | 0.029595 | 0.15248 | 0.05072 | -0.11094 | 0.002454 | 0.036954 | -0.065533 | -0.016906 | 0.14016 | -0.003897 | 0.079567 | 0.02992 | 0.1324 | 0.099314 | 0.001374 | 0.057061 | 0.17994 | 0.078186 | -0.083478 | 0.02992 | 0.06442 | -0.038067 | 0.01056 | 0.027141 | 0.095128 | 0.048266 | 0.11625
2379.0781 | 122.7219 | -122.5845 | 0.1236 | 0.11269 | -0.031363 | 0.056679 | -0.002124 | 0.10951 | 0.076426 | -0.021514 | 0.034174 | 0.14332 | 0.046142 | -0.10637 | 0.002454 | 0.032376 | -0.060955 | -0.012328 | 0.14016 | -0.003897 | 0.084145 | 0.025342 | 0.13698 | 0.10389 | 0.005952 | 0.06164 | 0.17079 | 0.073608 | -0.078899 | 0.02992 | 0.059842 | -0.033489 | 0.015138 | 0.03172 | 0.095129 | 0.043688 | 0.1071
2380.8281 | 122.8271 | -122.5616 | 0.07782 | 0.11269 | -0.026784 | 0.047522 | -0.002124 | 0.10493 | 0.085583 | -0.026092 | 0.034174 | 0.15248 | 0.046142 | -0.10179 | 0.007032 | 0.036954 | -0.065533 | -0.016906 | 0.14016 | 0.000682 | 0.074988 | 0.025342 | 0.1324 | 0.11305 | 0.001374 | 0.06164 | 0.17994 | 0.073608 | -0.07432 | 0.034498 | 0.06442 | -0.038067 | 0.01056 | 0.027142 | 0.099707 | 0.03911 | 0.11167
2382.5781 | 122.7493 | -122.58 | 0.13275 | 0.11269 | -0.031363 | 0.056679 | 0.002454 | 0.10493 | 0.081005 | -0.021514 | 0.034174 | 0.1479 | 0.059877 | -0.11094 | 0.007032 | 0.041532 | -0.065533 | -0.016906 | 0.14016 | -0.003897 | 0.084145 | 0.02992 | 0.1324 | 0.10847 | 0.005952 | 0.06164 | 0.17536 | 0.087343 | -0.083478 | 0.034498 | 0.068998 | -0.038067 | 0.01056 | 0.027142 | 0.099707 | 0.052845 | 0.12541
2384.3281 | 122.8683 | -122.5433 | 0.086975 | 0.11727 | -0.031363 | 0.056679 | 0.007033 | 0.10493 | 0.081005 | -0.026092 | 0.034174 | 0.15248 | 0.046142 | -0.10637 | 0.002454 | 0.036954 | -0.070112 | -0.012328 | 0.14474 | -0.003897 | 0.084145 | 0.034499 | 0.1324 | 0.10847 | 0.001374 | 0.06164 | 0.17994 | 0.073608 | -0.078899 | 0.02992 | 0.06442 | -0.042646 | 0.015138 | 0.03172 | 0.10429 | 0.043688 | 0.11625
2386.0781 | 122.8134 | -122.5845 | 0.09613 | 0.12185 | -0.035942 | 0.052101 | 0.002454 | 0.11409 | 0.076426 | -0.021514 | 0.034174 | 0.13874 | 0.046142 | -0.10637 | 0.01161 | 0.041532 | -0.070112 | -0.012328 | 0.14932 | -0.008476 | 0.079567 | 0.02992 | 0.14156 | 0.10389 | 0.005952 | 0.06164 | 0.16621 | 0.073608 | -0.078899 | 0.039076 | 0.068998 | -0.042646 | 0.015138 | 0.022564 | 0.10429 | 0.034532 | 0.11625
2387.8125 | 122.7402 | -122.6074 | 0.11902 | 0.11269 | -0.040521 | 0.061258 | 0.007033 | 0.10493 | 0.076426 | -0.03067 | 0.038752 | 0.15248 | 0.055298 | -0.11094 | 0.007032 | 0.041532 | -0.056376 | -0.016906 | 0.14016 | -0.013055 | 0.088724 | 0.034499 | 0.1324 | 0.10389 | -0.003204 | 0.066218 | 0.17994 | 0.082764 | -0.083478 | 0.034498 | 0.068998 | -0.02891 | 0.01056 | 0.03172 | 0.095128 | 0.048266 | 0.11167
2389.4844 | 122.7448 | -122.5937 | 0.091553 | 0.10812 | -0.035942 | 0.052101 | 0.002454 | 0.11409 | 0.071848 | -0.03067 | 0.029595 | 0.15248 | 0.05072 | -0.10179 | 0.002454 | 0.041532 | -0.070112 | -0.012328 | 0.13558 | -0.008476 | 0.079567 | 0.02992 | 0.14156 | 0.099314 | -0.003204 | 0.057061 | 0.17994 | 0.078186 | -0.07432 | 0.02992 | 0.068998 | -0.042646 | 0.015138 | 0.027141 | 0.099707 | 0.048266 | 0.12083
2391.2344 | 122.8683 | -122.5388 | 0.086975 | 0.11727 | -0.031363 | 0.052101 | 0.002454 | 0.10951 | 0.076426 | -0.039826 | 0.034174 | 0.15248 | 0.046142 | -0.11094 | 0.007032 | 0.036954 | -0.060955 | -0.00775 | 0.14474 | -0.003897 | 0.079567 | 0.02992 | 0.13698 | 0.10389 | -0.01236 | 0.06164 | 0.17994 | 0.073608 | -0.083478 | 0.034498 | 0.06442 | -0.033489 | 0.019716 | 0.027142 | 0.095129 | 0.03911 | 0.1071
2392.9219 | 122.7356 | -122.5845 | 0.11444 | 0.11269 | -0.022205 | 0.061258 | 0.002454 | 0.10951 | 0.076426 | -0.016936 | 0.038752 | 0.1479 | 0.041563 | -0.10637 | -0.002124 | 0.036954 | -0.070112 | -0.012328 | 0.14016 | 0.005261 | 0.088724 | 0.02992 | 0.13698 | 0.10389 | 0.01053 | 0.066218 | 0.17536 | 0.069029 | -0.078899 | 0.025342 | 0.06442 | -0.042646 | 0.015138 | 0.040876 | 0.10886 | 0.043687 | 0.11167
2394.6719 | 122.8821 | -122.5525 | 0.086975 | 0.11727 | -0.031363 | 0.061258 | 0.002454 | 0.11409 | 0.071848 | -0.026092 | 0.034174 | 0.14332 | 0.046142 | -0.10637 | 0.007032 | 0.036954 | -0.070112 | -0.016906 | 0.14474 | -0.003897 | 0.088724 | 0.02992 | 0.14156 | 0.099314 | 0.001374 | 0.06164 | 0.17079 | 0.073608 | -0.078899 | 0.034498 | 0.06442 | -0.042646 | 0.01056 | 0.027142 | 0.10429 | 0.03911 | 0.11625
2396.4375 | 122.8729 | -122.5571 | 0.07782 | 0.11269 | -0.031363 | 0.052101 | -0.002124 | 0.10493 | 0.076426 | -0.021514 | 0.029595 | 0.1479 | 0.055298 | -0.11094 | 0.007032 | 0.036954 | -0.070112 | -0.016906 | 0.14016 | -0.003897 | 0.079567 | 0.025342 | 0.1324 | 0.10389 | 0.005952 | 0.057061 | 0.17536 | 0.082764 | -0.083478 | 0.034498 | 0.06442 | -0.042646 | 0.01056 | 0.022563 | 0.099707 | 0.048266 | 0.12541
2398.1094 | 122.8729 | -122.5479 | 0.11444 | 0.11727 | -0.026784 | 0.061258 | -0.006703 | 0.10493 | 0.071848 | -0.03067 | 0.029595 | 0.1479 | 0.046142 | -0.11094 | 0.007032 | 0.036954 | -0.060955 | -0.012328 | 0.14474 | 0.000682 | 0.088724 | 0.020763 | 0.1324 | 0.099314 | -0.003204 | 0.057061 | 0.17536 | 0.073608 | -0.083478 | 0.034498 | 0.06442 | -0.033489 | 0.015138 | 0.022563 | 0.09055 | 0.03911 | 0.1071
2399.8594 | 122.8958 | -122.5479 | 0.073242 | 0.11269 | -0.031363 | 0.056679 | 0.002454 | 0.10036 | 0.081005 | -0.03067 | 0.038752 | 0.14332 | 0.036985 | -0.11552 | 0.002454 | 0.036954 | -0.070112 | -0.012328 | 0.14016 | -0.003897 | 0.084145 | 0.02992 | 0.12782 | 0.10847 | -0.003204 | 0.066218 | 0.17079 | 0.064451 | -0.088057 | 0.02992 | 0.06442 | -0.042646 | 0.015138 | 0.036298 | 0.10886 | 0.034531 | 0.1071
2401.5625 | 122.8317 | -122.5754 | 0.07782 | 0.11269 | -0.035942 | 0.061258 | -0.006703 | 0.10493 | 0.071848 | -0.026092 | 0.034174 | 0.14332 | 0.041563 | -0.10179 | -0.002124 | 0.032376 | -0.065533 | -0.016906 | 0.14016 | -0.008476 | 0.088724 | 0.020763 | 0.1324 | 0.099314 | 0.001374 | 0.06164 | 0.17079 | 0.069029 | -0.07432 | 0.025342 | 0.059842 | -0.038067 | 0.01056 | 0.036298 | 0.099707 | 0.043687 | 0.1071

## Thermal Data
Fire Time | A Position - Middle
-0.6521 | 9.2862
0.3479 | 9.2909
1.3479 | 9.2983
2.3479 | 9.2934
3.3479 | 9.2902
4.3479 | 9.2971
5.3479 | 9.2973
6.3479 | 9.296
7.3479 | 9.2924
8.3479 | 9.2954
9.3479 | 9.3638
10.3479 | 9.6132
11.3479 | 13.6096
12.3479 | 16.3253
13.3479 | 20.8667
14.3479 | 25.7199
15.3479 | 32.6527
16.3479 | 42.2605
17.3479 | 51.8484
18.3479 | 64.7306
19.3479 | 76.7266
20.3479 | 87.8851
21.3479 | 100.2592
22.3479 | 108.7204
23.3479 | 117.7087
24.3479 | 125.5252
25.3479 | 134.7369
26.3479 | 143.0979
27.3479 | 149.0054
28.3635 | 155.4602
29.3479 | 165.4235
30.3479 | 171.2199
31.3479 | 178.7843
32.3479 | 185.9363
33.3479 | 193.4513
34.3479 | 202.0987
35.3479 | 205.1765
36.3479 | 209.782
37.3479 | 213.5956
38.3479 | 219.0557
39.3479 | 225.7243
40.3479 | 233.2234
41.3479 | 236.7986
42.3479 | 241.3699
43.3479 | 243.4178
44.3479 | 244.4432
45.3479 | 248.041
46.3479 | 249.1228
47.3479 | 249.0045
48.3479 | 250.3705
49.3479 | 254.9553
50.3479 | 259.6681
51.3479 | 263.8475
52.3479 | 267.9464
53.3479 | 269.343
54.3479 | 270.1037
55.3635 | 270.7769
56.3479 | 271.3744
57.3479 | 272.6783
58.3479 | 272.9866
59.3479 | 274.8155
60.3479 | 280.7107
61.3479 | 281.9635
62.3479 | 284.3505
63.3479 | 284.1518
64.3479 | 286.8527
65.3479 | 288.6954
66.3479 | 289.2455
67.3479 | 290.3921
68.3479 | 288.8101
69.3479 | 289.3834
70.3479 | 290.3467
71.3479 | 292.7513
72.3479 | 292.992
73.3479 | 295.1206
74.3479 | 296.3464
75.3479 | 298.2549
76.3479 | 297.607
77.3479 | 295.4881
78.3479 | 295.3005
79.3479 | 294.8416
80.3479 | 296.3298
81.3479 | 295.4227
82.3479 | 293.3443
83.3479 | 293.5765
84.3479 | 292.1079
85.3479 | 292.1484
86.3479 | 290.4305
87.3479 | 289.5429
88.3479 | 291.2453
89.3479 | 293.6972
90.3479 | 293.3576
91.3479 | 293.3373
92.3479 | 294.6383
93.3479 | 295.368
94.3479 | 293.649
95.3479 | 292.9267
96.3479 | 289.9154
97.3479 | 289.8072
98.3479 | 288.3989
99.3479 | 286.2625
100.3479 | 285.2165
101.3479 | 283.9626
102.3479 | 281.2393
103.3479 | 278.8541
104.3479 | 279.6832
105.3479 | 280.9031
106.3479 | 283.1144
107.3479 | 285.9787
108.3479 | 288.0314
109.3479 | 289.5151
110.3479 | 291.1176
111.3479 | 294.5533
112.3479 | 296.7908
113.3479 | 297.9006
114.3479 | 300.6726
115.3479 | 301.2307
116.3479 | 302.9271
117.3479 | 303.3465
118.3479 | 305.2274
119.3479 | 306.8682
120.3479 | 306.5563
121.3479 | 309.9044
122.3479 | 311.8098
123.3479 | 318.1052
124.3479 | 318.3918
125.3479 | 322.2255
126.3479 | 323.4348
127.3479 | 325.5631
128.3479 | 328.9425
129.3479 | 332.5345
130.3479 | 332.501
131.3479 | 332.5953
132.3479 | 333.9869
133.3479 | 335.9282
134.3479 | 340.1194
135.3479 | 339.9107
136.3479 | 340.7587
137.3479 | 339.2971
138.3479 | 338.7229
139.3479 | 339.9863
140.3479 | 340.9187
141.3479 | 339.7945
142.3479 | 338.696
143.3479 | 338.6403
144.3479 | 336.2847
145.3479 | 334.6251
146.3479 | 334.1288
147.3479 | 334.5536
148.3479 | 334.7674
149.3479 | 334.0958
150.3479 | 333.0523
151.3479 | 332.1975
152.3479 | 334.5003
153.3479 | 335.1359
154.3479 | 336.1339
155.3479 | 337.9099
156.3479 | 337.9195
157.3479 | 338.6148
158.3479 | 338.6812
159.3479 | 340.1179
160.3479 | 340.74
161.3479 | 342.2402
162.3479 | 344.4738
163.3479 | 345.0198
164.3479 | 344.914
165.3479 | 346.6307
166.3479 | 351.9557
167.3479 | 352.6498
168.3479 | 352.8605
169.3479 | 353.2966
170.3479 | 353.6765
171.3479 | 353.1348
172.3479 | 352.2476
173.3479 | 352.7199
174.3479 | 353.5297
175.3479 | 352.0892
176.3479 | 354.2794
177.3479 | 355.2614
178.3479 | 355.8771
179.3479 | 358.9101
180.3479 | 362.7188
181.3479 | 362.3339
182.3479 | 364.417
183.3479 | 363.544
184.3479 | 364.0621
185.3479 | 363.6374
186.3479 | 362.5578
187.3479 | 364.893
188.3479 | 366.8239
189.3479 | 374.0875
190.3479 | 376.7673
191.3479 | 381.0962
192.3479 | 382.1404
193.3479 | 381.6006
194.3479 | 382.0652
195.3479 | 382.8122
196.3479 | 382.2127
197.3479 | 384.2891
198.3479 | 388.0628
199.3479 | 387.8816
200.3479 | 389.2122
201.3479 | 388.9337
202.3479 | 388.4168
203.3479 | 391.5823
204.3479 | 389.4954
205.3479 | 390.9472
206.3479 | 393.8829
207.3479 | 394.7601
208.3479 | 395.6481
209.3479 | 395.9645
210.3479 | 398.0734
211.3479 | 397.1458
212.3479 | 400.8789
213.3479 | 405.9957
214.3479 | 408.1692
215.3479 | 413.1192
216.3479 | 415.4943
217.3479 | 419.0679
218.3479 | 429.0724
219.3479 | 433.744
220.3479 | 441.0096
221.3479 | 441.2709
222.3479 | 452.0676
223.3479 | 450.6997
224.3479 | 449.3445
225.3479 | 448.9578
226.3479 | 446.6506
227.3479 | 452.8871
228.3479 | 453.1461
229.3479 | 459.869
230.3479 | 461.0819
231.3479 | 463.7784
232.3479 | 465.6643
233.3479 | 477.4471
234.3479 | 488.2971
235.3479 | 496.856
236.3479 | 499.8854
237.3479 | 501.5299
238.3479 | 515.6719
239.3479 | 511.1021
240.3479 | 509.0225
241.3479 | 503.4047
242.3479 | 500.8903
243.3479 | 509.2364
244.3479 | 523.8244
245.3479 | 522.9079
246.3479 | 522.7098
247.3479 | 520.212
248.3479 | 527.9137
249.3479 | 535.211
250.3479 | 541.1059
251.3479 | 542.9546
252.3479 | 543.1762
253.3479 | 539.4017
254.3479 | 542.8116
255.3479 | 545.7176
256.3479 | 542.4512
257.3479 | 545.058
258.3479 | 550.1896
259.3479 | 546.5975
260.3479 | 546.2964
261.3479 | 548.3865
262.3479 | 557.0458
263.3479 | 557.7204
264.3479 | 558.8422
265.3479 | 556.0729
266.3479 | 552.2243
267.3479 | 554.0069
268.3479 | 552.8801
269.3479 | 554.5931
270.3479 | 558.3503
271.3479 | 566.1113
272.3479 | 570.56
273.3479 | 575.0584
274.3479 | 570.7935
275.3479 | 575.262
276.3479 | 575.9755
277.3479 | 577.2868
278.3479 | 590.3644
279.3479 | 593.0548
280.3479 | 594.9922
281.3479 | 598.1769
282.3479 | 598.5574
283.3479 | 607.8027
284.3479 | 614.6805
285.3479 | 612.4158
286.3479 | 612.2894
287.3479 | 614.4234
288.3479 | 616.3944
289.3479 | 616.8231
290.3479 | 618.4696
291.3479 | 617.7082
292.3479 | 620.5072
293.3479 | 625.0499
294.3479 | 626.8166
295.3479 | 628.37
296.3479 | 634.0485
297.3479 | 635.3958
298.3479 | 632.8288
299.3479 | 632.2646
300.3479 | 640.4822
301.3479 | 641.7821
302.3479 | 643.3848
303.3479 | 649.5871
304.3479 | 652.3888
305.3479 | 648.7345
306.3479 | 650.3039
307.3479 | 645.7567
308.3479 | 655.4544
309.3479 | 652.5207
310.3479 | 649.8311
311.3479 | 647.4546
312.3479 | 647.2982
313.3479 | 645.2023
314.3479 | 645.6615
315.3479 | 646.2001
316.3479 | 644.9099
317.3479 | 641.4332
318.3479 | 639.4184
319.3479 | 639.0047
320.3479 | 637.7371
321.3479 | 637.9372
322.3479 | 638.8318
323.3479 | 636.5137
324.3479 | 633.9835
325.3479 | 632.0541
326.3479 | 633.6783
327.3479 | 632.0744
328.3479 | 631.7107
329.3479 | 633.8105
330.3479 | 633.9835
331.3479 | 641.1063
332.3479 | 644.2926
333.3479 | 647.0274
334.3479 | 649.564
335.3479 | 654.7136
336.3479 | 660.0169
337.3479 | 665.2188
338.3479 | 670.0259
339.3479 | 672.1715
340.3479 | 674.1607
341.3479 | 678.0738
342.3479 | 682.9847
343.3479 | 685.0246
344.3479 | 683.3674
345.3479 | 686.1485
346.3479 | 686.1964
347.3479 | 687.1259
348.3479 | 687.0935
349.3479 | 686.8147
350.3479 | 687.1526
351.3479 | 682.4444
352.3479 | 677.9589
353.3479 | 682.8209
354.3479 | 686.2361
355.3479 | 681.6835
356.3479 | 682.0622
357.3479 | 683.4325
358.3479 | 682.962
359.3479 | 687.742
360.3479 | 688.6052
361.3479 | 691.5981
362.3479 | 686.5872
363.3479 | 687.2374
364.3479 | 691.7841
365.3479 | 690.8103
366.3479 | 686.5035
367.3479 | 689.695
368.3479 | 690.6676
369.3479 | 690.8795
370.3479 | 695.0515
371.3479 | 694.4798
372.3479 | 696.4282
373.3479 | 702.238
374.3479 | 701.762
375.3479 | 699.6696
376.3479 | 697.157
377.3479 | 693.6449
378.3479 | 695.9964
379.3479 | 696.9844
380.3479 | 695.6747
381.3479 | 694.1495
382.3479 | 693.9855
383.3479 | 691.0421
384.3479 | 698.3342
385.3479 | 697.8365
386.3479 | 698.398
387.3479 | 698.0797
388.3479 | 695.1555
389.3479 | 693.9434
390.3479 | 699.1039
391.3479 | 695.6754
392.3479 | 697.8949
393.3479 | 699.669
394.3479 | 699.0972
395.3479 | 697.9779
396.3479 | 696.1588
397.3479 | 697.3652
398.3479 | 696.4032
399.3479 | 695.1305
400.3479 | 695.3138
401.3479 | 700.1489
402.3479 | 697.2671
403.3479 | 697.4231
404.3479 | 693.5465
405.3479 | 692.0364
406.3479 | 692.394
407.3479 | 693.5205
408.3479 | 693.2262
409.3479 | 689.5898
410.3479 | 688.7847
411.3479 | 694.8096
412.3479 | 697.4545
413.3479 | 701.1178
414.3479 | 709.1525
415.3479 | 715.1052
416.3479 | 713.7718
417.3479 | 710.4307
418.3479 | 707.8203
419.3479 | 703.2234
420.3479 | 703.8988
421.3479 | 704.877
422.3479 | 710.9704
423.3479 | 708.2584
424.3479 | 709.622
425.3479 | 705.466
426.3479 | 710.8312
427.3479 | 710.908
428.3479 | 717.175
429.3479 | 715.877
430.3479 | 712.1228
431.3479 | 711.5924
432.3479 | 712.8981
433.3479 | 710.6204
434.3479 | 714.9839
435.3479 | 714.4483
436.3479 | 713.4001
437.3479 | 715.117
438.3479 | 714.7936
439.3479 | 712.9757
440.3479 | 707.91
441.3479 | 702.7198
442.3479 | 700.5306
443.3479 | 706.4515
444.3479 | 703.1196
445.3479 | 699.3276
446.3479 | 698.7735
447.3479 | 698.0759
448.3479 | 700.2037
449.3479 | 702.0659
450.3479 | 704.2312
451.3479 | 704.2919
452.3479 | 705.3871
453.3479 | 704.3741
454.3479 | 703.4176
455.3479 | 708.7361
456.3479 | 708.7156
457.3479 | 710.532
458.3479 | 710.9295
459.3479 | 710.0236
460.3479 | 713.4182
461.3479 | 714.1119
462.3479 | 715.8135
463.3479 | 713.8058
464.3479 | 712.2283
465.3479 | 711.2961
466.3479 | 712.1769
467.3479 | 710.4168
468.3479 | 710.8802
469.3479 | 708.188
470.3479 | 707.9757
471.3479 | 708.0241
472.3479 | 707.9301
473.3479 | 709.6914
474.3479 | 712.4108
475.3479 | 713.7096
476.3479 | 713.9781
477.3479 | 714.7669
478.3479 | 715.7792
479.3479 | 713.3842
480.3479 | 711.7156
481.3479 | 707.1589
482.3479 | 705.3495
483.3479 | 702.7495
484.3479 | 701.0505
485.3479 | 703.3658
486.3479 | 704.3759
487.3479 | 702.4384
488.3479 | 700.5962
489.3479 | 699.3574
490.3479 | 700.6414
491.3479 | 702.332
492.3479 | 700.2098
493.3479 | 697.0778
494.3479 | 697.2585
495.3479 | 697.6728
496.3479 | 697.5486
497.3479 | 699.7062
498.3479 | 701.0455
499.3479 | 701.3383
500.3479 | 703.6334
501.3479 | 705.8586
502.3479 | 704.0765
503.3479 | 707.2792
504.3479 | 711.4397
505.3479 | 712.5584
506.3479 | 715.3819
507.3479 | 713.9782
508.3479 | 709.5954
509.3479 | 706.5898
510.3479 | 707.9888
511.3479 | 710.4407
512.3479 | 715.5057
513.3479 | 718.2798
514.3479 | 717.4677
515.3479 | 717.4283
516.3479 | 714.2876
517.3479 | 710.7434
518.3479 | 710.602
519.3479 | 711.2545
520.3479 | 713.5589
521.3479 | 713.2236
522.3479 | 710.4097
523.3479 | 708.1876
524.3479 | 705.832
525.3479 | 703.3949
526.3479 | 703.6329
527.3479 | 706.6226
528.3479 | 707.9256
529.3479 | 709.8739
530.3479 | 711.9796
531.3479 | 710.3084
532.3479 | 704.5348
533.3479 | 700.4174
534.3479 | 697.9986
535.3479 | 695.7386
536.3479 | 693.2579
537.3479 | 689.7991
538.3479 | 686.9843
539.3479 | 685.7744
540.3479 | 684.9386
541.3479 | 684.6727
542.3479 | 683.5847
543.3479 | 682.0891
544.3479 | 681.1421
545.3479 | 679.133
546.3479 | 680.937
547.3479 | 683.6234
548.3479 | 684.5183
549.3479 | 684.9167
550.3479 | 686.2894
551.3479 | 685.2844
552.3479 | 685.7673
553.3479 | 686.7755
554.3479 | 687.3861
555.3479 | 687.977
556.3479 | 687.7586
557.3479 | 687.8688
558.3479 | 688.7108
559.3479 | 689.0544
560.3479 | 690.7222
561.3479 | 689.8595
562.3479 | 690.778
563.3479 | 690.9455
564.3479 | 691.1123
565.3479 | 692.439
566.3635 | 691.5178
567.3479 | 690.3211
568.3479 | 689.5557
569.3479 | 689.3344
570.3479 | 688.9608
571.3479 | 689.5882
572.3479 | 689.9094
573.3479 | 689.6469
574.3479 | 689.049
575.3479 | 688.2971
576.3479 | 687.1576
577.3479 | 685.5245
578.3479 | 685.2433
579.3479 | 686.8182
580.3479 | 688.3446
581.3479 | 690.7207
582.3479 | 691.3105
583.3479 | 691.2421
584.3479 | 692.3496
585.3479 | 692.9343
586.3479 | 692.4729
587.3479 | 692.5517
588.3479 | 692.8276
589.3479 | 692.8468
590.3479 | 691.6558
591.3479 | 692.7313
592.3479 | 695.5526
593.3479 | 695.846
594.3479 | 693.3589
595.3479 | 693.0782
596.3635 | 692.1383
597.3479 | 692.9976
598.3479 | 691.2624
599.3479 | 690.004
600.3479 | 690.7189
601.3479 | 692.2476
602.3479 | 693.3542
603.3479 | 693.2151
604.3479 | 692.8395
605.3479 | 692.907
606.3479 | 692.7978
607.3479 | 690.0554
608.3479 | 688.9524
609.3479 | 687.7166
610.3479 | 687.398
611.3479 | 688.4728
612.3479 | 688.4122
613.3479 | 687.9491
614.3479 | 688.5627
615.3479 | 686.5568
616.3479 | 684.4868
617.3479 | 683.6409
618.3479 | 684.0656
619.3479 | 681.2543
620.3479 | 679.9241
621.3479 | 679.8005
622.3479 | 678.5954
623.3479 | 676.8821
624.3479 | 677.1656
625.3479 | 679.9113
626.3479 | 680.3958
627.3479 | 680.3644
628.3479 | 679.9416
629.3479 | 679.3217
630.3479 | 680.515
631.3479 | 681.1767
632.3479 | 682.1871
633.3479 | 682.8263
634.3479 | 682.1404
635.3479 | 681.9518
636.3479 | 682.1308
637.3479 | 682.7112
638.3479 | 683.9546
639.3479 | 684.071
640.3479 | 684.9878
641.3479 | 686.12
642.3479 | 685.1479
643.3479 | 685.0954
644.3479 | 685.9554
645.3479 | 685.3599
646.3479 | 686.1353
647.3479 | 687.6729
648.3479 | 687.0411
649.3479 | 686.5311
650.3479 | 686.2801
651.3479 | 688.0998
652.3479 | 689.7981
653.3479 | 691.9077
654.3479 | 691.1943
655.3479 | 692.3455
656.3479 | 693.1472
657.3479 | 692.0572
658.3479 | 690.6238
659.3479 | 688.1885
660.3479 | 685.8803
661.3479 | 687.0846
662.3479 | 686.3392
663.3479 | 685.7452
664.3479 | 685.9429
665.3479 | 686.4111
666.3479 | 685.5748
667.3479 | 684.9787
668.3479 | 685.1661
669.3479 | 685.349
670.3479 | 684.1576
671.3479 | 685.3259
672.3479 | 685.6765
673.3479 | 685.7773
674.3479 | 686.7824
675.3479 | 687.0795
676.3479 | 686.4614
677.3479 | 686.6136
678.3479 | 685.9897
679.3479 | 684.6433
680.3479 | 683.7449
681.3479 | 686.1771
682.3479 | 687.5763
683.3479 | 688.0905
684.3479 | 688.5226
685.3479 | 689.5946
686.3479 | 689.8687
687.3479 | 689.3595
688.3479 | 691.3496
689.3479 | 691.8056
690.3479 | 689.6346
691.3479 | 688.822
692.3479 | 688.9011
693.3479 | 687.5421
694.3479 | 688.3665
695.3479 | 689.1989
696.3479 | 688.8541
697.3479 | 688.5538
698.3479 | 688.3753
699.3479 | 688.8249
700.3479 | 689.8065
701.3479 | 690.3269
702.3479 | 690.7491
703.3479 | 689.6475
704.3479 | 690.4245
705.3479 | 689.7724
706.3479 | 688.5989
707.3479 | 686.837
708.3479 | 684.5489
709.3479 | 681.8468
710.3479 | 680.2114
711.3479 | 679.8182
712.3479 | 680.8005
713.3479 | 682.7228
714.3479 | 685.4812
715.3479 | 688.0869
716.3479 | 689.7238
717.3479 | 689.6978
718.3479 | 691.3361
719.3479 | 692.7268
720.3479 | 694.464
721.3479 | 694.2829
722.3479 | 696.0057
723.3479 | 697.475
724.3479 | 697.9123
725.3479 | 696.5952
726.3479 | 695.919
727.3479 | 694.5863
728.3479 | 694.0644
729.3479 | 693.8407
730.3479 | 693.1107
731.3479 | 692.371
732.3479 | 690.6993
733.3479 | 687.4413
734.3479 | 684.851
735.3479 | 683.8457
736.3479 | 684.0319
737.3479 | 683.6837
738.3479 | 683.2332
739.3479 | 683.1112
740.3479 | 683.449
741.3479 | 683.6047
742.3479 | 683.7963
743.3479 | 684.5871
744.3479 | 685.6665
745.3479 | 685.1665
746.3479 | 685.2293
747.3479 | 686.1407
748.3479 | 686.0628
749.3479 | 687.5277
750.3479 | 688.2956
751.3479 | 689.2444
752.3479 | 692.1443
753.3479 | 692.3453
754.3479 | 692.3114
755.3479 | 693.5655
756.3479 | 693.925
757.3479 | 693.2964
758.3479 | 692.0619
759.3479 | 690.5594
760.3479 | 688.7855
761.3479 | 686.4773
762.3479 | 686.917
763.3479 | 686.032
764.3479 | 684.1327
765.3479 | 683.3457
766.3479 | 682.4983
767.3479 | 681.8113
768.3479 | 683.9847
769.3479 | 685.7962
770.3479 | 685.3281
771.3479 | 686.8902
772.3479 | 687.1339
773.3479 | 688.6474
774.3479 | 689.011
775.3479 | 688.2808
776.3479 | 688.8417
777.3479 | 689.3536
778.3479 | 689.7262
779.3479 | 688.6991
780.3479 | 687.4472
781.3479 | 686.5434
782.3479 | 685.6887
783.3479 | 686.6828
784.3479 | 687.7114
785.3479 | 689.0115
786.3479 | 689.8279
787.3479 | 690.0068
788.3479 | 688.8285
789.3479 | 688.4333
790.3479 | 687.9564
791.3479 | 687.4914
792.3479 | 689.4631
793.3479 | 690.1884
794.3479 | 690.8263
795.3479 | 690.8212
796.3479 | 690.1126
797.3479 | 690.2743
798.3479 | 689.2401
799.3479 | 688.9833
800.3479 | 689.8968
801.3479 | 690.4642
802.3479 | 689.1434
803.3479 | 689.1663
804.3479 | 688.1321
805.3479 | 687.6368
806.3479 | 686.0999
807.3479 | 685.752
808.3479 | 685.1832
809.3479 | 684.9899
810.3479 | 686.1039
811.3479 | 689.9293
812.3479 | 692.0942
813.3479 | 692.6038
814.3479 | 692.5189
815.3479 | 692.3774
816.3479 | 693.5294
817.3479 | 693.7741
818.3479 | 692.8792
819.3479 | 690.9789
820.3479 | 690.7802
821.3479 | 691.6164
822.3479 | 689.493
823.3479 | 690.4801
824.3479 | 691.788
825.3479 | 690.7818
826.3479 | 691.9487
827.3479 | 690.5904
828.3479 | 690.4674
829.3479 | 688.8306
830.3479 | 687.8276
831.3479 | 690.4811
832.3479 | 692.5709
833.3479 | 693.4115
834.3479 | 694.5251
835.3479 | 693.9272
836.3479 | 694.018
837.3479 | 694.1399
838.3479 | 694.0724
839.3479 | 693.9897
840.3479 | 693.3682
841.3479 | 693.1871
842.3479 | 691.5724
843.3479 | 689.5597
844.3479 | 686.9036
845.3479 | 685.295
846.3479 | 685.5116
847.3479 | 687.3173
848.3479 | 692.0095
849.3479 | 690.8888
850.3479 | 690.8861
851.3479 | 690.0092
852.3479 | 689.3672
853.3479 | 689.2333
854.3479 | 689.7036
855.3479 | 689.4177
856.3479 | 690.3313
857.3479 | 690.337
858.3479 | 689.2807
859.3479 | 688.8342
860.3479 | 688.5757
861.3479 | 692.2317
862.3479 | 694.876
863.3479 | 695.3003
864.3479 | 693.253
865.3479 | 693.2788
866.3479 | 692.8779
867.3479 | 691.8936
868.3479 | 692.4648
869.3479 | 690.8356
870.3479 | 688.4357
871.3479 | 686.8425
872.3479 | 685.0825
873.3479 | 684.8418
874.3479 | 682.6326
875.3635 | 679.8769
876.3479 | 678.3306
877.3479 | 678.0982
878.3479 | 676.7249
879.3479 | 674.0216
880.3479 | 673.7281
881.3479 | 673.8217
882.3479 | 673.2196
883.3479 | 671.975
884.3479 | 672.0866
885.3479 | 671.6767
886.3479 | 673.2262
887.3479 | 674.3962
888.3479 | 677.4741
889.3479 | 677.1616
890.3479 | 675.057
891.3479 | 673.0686
892.3479 | 671.9324
893.3479 | 669.6457
894.3479 | 669.4605
895.3479 | 667.5567
896.3479 | 667.2353
897.3479 | 667.7556
898.3479 | 668.3585
899.3479 | 667.0292
900.3479 | 666.9471
901.3479 | 666.1038
902.3479 | 666.5986
903.3479 | 668.8158
904.3479 | 671.2803
905.3479 | 672.9256
906.3479 | 672.9583
907.3479 | 673.7505
908.3479 | 674.1255
909.3479 | 673.6403
910.3479 | 673.1794
911.3479 | 673.0928
912.3479 | 672.8353
913.3479 | 672.0109
914.3479 | 672.2552
915.3479 | 672.0405
916.3479 | 672.8933
917.3479 | 674.15
918.3479 | 672.4646
919.3479 | 671.8953
920.3479 | 672.7753
921.3479 | 676.4429
922.3479 | 678.3924
923.3479 | 680.145
924.3479 | 681.7768
925.3479 | 682.461
926.3479 | 684.4348
927.3479 | 682.8345
928.3479 | 682.6075
929.3479 | 682.589
930.3479 | 683.4435
931.3479 | 683.1055
932.3479 | 682.3429
933.3479 | 682.0644
934.3479 | 681.7729
935.3479 | 680.1
936.3479 | 679.7468
937.3479 | 681.5423
938.3479 | 683.5242
939.3479 | 685.9471
940.3479 | 687.2734
941.3479 | 688.3583
942.3479 | 689.356
943.3479 | 687.9564
944.3479 | 687.6298
945.3479 | 687.256
946.3479 | 686.6754
947.3479 | 684.9527
948.3479 | 684.6323
949.3479 | 684.9713
950.3479 | 684.8888
951.3479 | 686.3626
952.3479 | 686.731
953.3479 | 687.3755
954.3479 | 686.8279
955.3479 | 686.358
956.3479 | 687.1326
957.3479 | 686.1375
958.3479 | 688.0198
959.3479 | 689.799
960.3479 | 692.2668
961.3479 | 693.2747
962.3479 | 694.5084
963.3479 | 694.6813
964.3479 | 694.5738
965.3479 | 693.0216
966.3479 | 691.1846
967.3479 | 688.4329
968.3479 | 687.6106
969.3479 | 687.2756
970.3479 | 686.8167
971.3479 | 687.7763
972.3479 | 689.6048
973.3479 | 689.5644
974.3479 | 689.616
975.3479 | 689.4228
976.3479 | 687.6568
977.3479 | 688.3355
978.3479 | 690.6826
979.3479 | 690.8754
980.3479 | 690.8084
981.3479 | 692.6761
982.3479 | 695.1958
983.3479 | 696.5313
984.3479 | 697.2369
985.3479 | 696.2279
986.3479 | 697.7969
987.3479 | 698.2543
988.3479 | 699.1644
989.3479 | 701.1105
990.3479 | 700.0186
991.3479 | 700.2222
992.3479 | 699.2593
993.3479 | 698.0405
994.3479 | 696.3511
995.3479 | 693.8638
996.3479 | 692.826
997.3479 | 691.4873
998.3479 | 689.8701
999.3479 | 689.2472
1000.3479 | 688.7458
1001.3479 | 686.9837
1002.3479 | 685.3566
1003.3479 | 683.864
1004.3479 | 683.5389
1005.3479 | 683.2891
1006.3479 | 683.882
1007.3479 | 684.3544
1008.3479 | 684.7285
1009.3479 | 685.9973
1010.3479 | 686.8574
1011.3479 | 689.1981
1012.3479 | 692.1932
1013.3479 | 693.4366
1014.3479 | 693.2974
1015.3479 | 694.5398
1016.3479 | 696.9589
1017.3479 | 698.0926
1018.3479 | 698.3019
1019.3479 | 699.58
1020.3479 | 700.7325
1021.3479 | 703.9256
1022.3479 | 704.891
1023.3479 | 707.8199
1024.3479 | 711.3452
1025.3479 | 718.4203
1026.3479 | 718.8627
1027.3479 | 717.705
1028.3479 | 714.9213
1029.3479 | 711.3125
1030.3479 | 708.4295
1031.3479 | 703.7936
1032.3479 | 700.7142
1033.3479 | 702.3434
1034.3479 | 700.9127
1035.3479 | 700.2273
1036.3479 | 701.5874
1037.3479 | 706.6578
1038.3479 | 705.7358
1039.3479 | 704.836
1040.3479 | 708.433
1041.3479 | 707.8447
1042.3479 | 703.3001
1043.3479 | 700.4221
1044.3479 | 696.8936
1045.3479 | 693.337
1046.3479 | 690.6705
1047.3479 | 689.7021
1048.3479 | 693.5114
1049.3479 | 698.0648
1050.3479 | 698.5807
1051.3479 | 696.5813
1052.3479 | 694.4177
1053.3479 | 693.4925
1054.3479 | 690.5099
1055.3479 | 688.43
1056.3479 | 686.9276
1057.3479 | 686.7711
1058.3479 | 686.6139
1059.3479 | 686.904
1060.3479 | 686.6013
1061.3479 | 686.7337
1062.3479 | 686.241
1063.3479 | 685.9423
1064.3479 | 686.0717
1065.3479 | 687.8035
1066.3479 | 688.5338
1067.3479 | 690.3694
1068.3479 | 692.953
1069.3479 | 693.0198
1070.3479 | 693.4524
1071.3479 | 695.8265
1072.3479 | 695.7353
1073.3479 | 696.0043
1074.3479 | 693.3241
1075.3479 | 692.5219
1076.3479 | 692.4764
1077.3479 | 691.0833
1078.3479 | 689.0621
1079.3479 | 687.9752
1080.3479 | 687.6451
1081.3479 | 688.1941
1082.3479 | 686.9905
1083.3479 | 687.0489
1084.3479 | 686.3433
1085.3479 | 686.4203
1086.3479 | 686.0052
1087.3479 | 685.4947
1088.3479 | 686.5249
1089.3479 | 688.3696
1090.3479 | 691.884
1091.3479 | 692.4185
1092.3479 | 693.2813
1093.3479 | 692.6806
1094.3479 | 692.6523
1095.3479 | 692.8552
1096.3479 | 691.7367
1097.3479 | 691.6402
1098.3479 | 693.1404
1099.3479 | 699.529
1100.3479 | 702.5175
1101.3479 | 701.3163
1102.3479 | 702.7848
1103.3479 | 702.8824
1104.3479 | 702.4606
1105.3479 | 701.2792
1106.3479 | 698.5265
1107.3479 | 697.0065
1108.3479 | 701.8691
1109.3479 | 699.8853
1110.3479 | 698.6934
1111.3479 | 700.0261
1112.3479 | 701.8893
1113.3479 | 702.7972
1114.3479 | 702.6872
1115.3479 | 701.5549
1116.3479 | 700.91
1117.3479 | 701.3141
1118.3479 | 701.7836
1119.3479 | 702.6985
1120.3479 | 703.2612
1121.3479 | 701.6367
1122.3479 | 704.0472
1123.3479 | 706.8471
1124.3479 | 711.3996
1125.3479 | 713.2441
1126.3479 | 712.3825
1127.3479 | 714.4823
1128.3479 | 714.9449
1129.3479 | 715.1944
1130.3479 | 714.6704
1131.3479 | 713.7277
1132.3479 | 714.0725
1133.3479 | 713.8024
1134.3479 | 715.6149
1135.3479 | 718.7861
1136.3479 | 719.6487
1137.3479 | 716.9748
1138.3479 | 717.0144
1139.3479 | 718.2199
1140.3479 | 719.6987
1141.3479 | 725.7872
1142.3479 | 730.9256
1143.3479 | 728.9945
1144.3479 | 726.096
1145.3479 | 723.4503
1146.3479 | 723.1557
1147.3479 | 720.8214
1148.3479 | 719.7492
1149.3479 | 718.4973
1150.3479 | 716.8818
1151.3479 | 716.8277
1152.3479 | 715.9883
1153.3479 | 714.5498
1154.3479 | 714.1875
1155.3479 | 712.9638
1156.3479 | 710.3527
1157.3479 | 709.8384
1158.3479 | 712.9081
1159.3479 | 714.0518
1160.3479 | 713.7728
1161.3479 | 714.3387
1162.3479 | 712.821
1163.3479 | 710.944
1164.3479 | 709.835
1165.3479 | 711.0738
1166.3479 | 714.6226
1167.3479 | 717.6016
1168.3479 | 719.8657
1169.3479 | 726.3497
1170.3479 | 725.9232
1171.3479 | 725.4325
1172.3479 | 725.4979
1173.3479 | 730.6414
1174.3479 | 731.468
1175.3479 | 728.6089
1176.3479 | 725.0859
1177.3479 | 722.7107
1178.3479 | 722.743
1179.3479 | 723.2486
1180.3479 | 720.7796
1181.3479 | 718.235
1182.3479 | 717.7879
1183.3479 | 718.2537
1184.3479 | 720.0474
1185.3479 | 721.5519
1186.3479 | 722.8943
1187.3479 | 723.0255
1188.3479 | 722.5646
1189.3479 | 723.5944
1190.3479 | 726.5084
1191.3479 | 732.2622
1192.3479 | 731.5449
1193.3479 | 732.4038
1194.3479 | 733.8554
1195.3479 | 732.9863
1196.3479 | 733.5239
1197.3479 | 734.4513
1198.3479 | 735.583
1199.3479 | 737.8856
1200.3479 | 739.8596
1201.3479 | 738.1198
1202.3479 | 739.8224
1203.3479 | 738.7151
1204.3479 | 743.0579
1205.3479 | 743.4939
1206.3479 | 742.9604
1207.3479 | 753.9044
1208.3479 | 759.815
1209.3479 | 756.7417
1210.3479 | 754.2775
1211.3479 | 750.7649
1212.3479 | 747.1576
1213.3479 | 743.264
1214.3479 | 739.6643
1215.3479 | 735.491
1216.3479 | 731.3346
1217.3479 | 729.273
1218.3479 | 726.9097
1219.3479 | 725.619
1220.3479 | 727.7366
1221.3479 | 726.0251
1222.3479 | 726.245
1223.3479 | 726.8749
1224.3479 | 730.187
1225.3479 | 729.7696
1226.3479 | 730.0566
1227.3479 | 733.3935
1228.3479 | 732.2094
1229.3479 | 732.3074
1230.3479 | 734.4501
1231.3479 | 734.3644
1232.3479 | 733.1811
1233.3479 | 735.7119
1234.3479 | 736.8251
1235.3479 | 737.9398
1236.3479 | 739.0536
1237.3479 | 736.8627
1238.3479 | 737.6126
1239.3479 | 736.6552
1240.3479 | 735.8076
1241.3479 | 740.1126
1242.3479 | 741.4586
1243.3479 | 741.9159
1244.3479 | 742.2524
1245.3479 | 740.8631
1246.3479 | 740.8278
1247.3479 | 741.7435
1248.3479 | 743.7059
1249.3479 | 742.8124
1250.3479 | 744.6759
1251.3479 | 754.2152
1252.3479 | 751.6487
1253.3479 | 750.0552
1254.3479 | 746.2696
1255.3479 | 742.9476
1256.3479 | 744.1611
1257.3479 | 745.06
1258.3479 | 747.4279
1259.3479 | 746.1577
1260.3479 | 748.4523
1261.3479 | 751.5199
1262.3479 | 750.934
1263.3479 | 747.0229
1264.3479 | 744.8048
1265.3479 | 743.9617
1266.3479 | 741.6607
1267.3479 | 744.2976
1268.3479 | 746.3416
1269.3479 | 748.08
1270.3479 | 749.6001
1271.3479 | 746.9066
1272.3479 | 744.3968
1273.3479 | 742.4435
1274.3479 | 745.3713
1275.3479 | 743.6366
1276.3479 | 741.1416
1277.3479 | 741.553
1278.3479 | 739.8537
1279.3479 | 738.3715
1280.3479 | 736.4097
1281.3479 | 735.7277
1282.3479 | 733.5078
1283.3479 | 741.7125
1284.3479 | 745.0434
1285.3479 | 745.6498
1286.3479 | 755.3036
1287.3479 | 753.7149
1288.3479 | 753.2596
1289.3479 | 751.1607
1290.3479 | 752.6098
1291.3479 | 748.1124
1292.3479 | 751.6212
1293.3479 | 753.324
1294.3479 | 750.0614
1295.3479 | 746.3758
1296.3479 | 745.8785
1297.3479 | 741.6177
1298.3479 | 736.853
1299.3479 | 734.9504
1300.3479 | 738.9999
1301.3479 | 745.2017
1302.3479 | 746.9766
1303.3479 | 748.4409
1304.3479 | 751.3056
1305.3479 | 753.7206
1306.3479 | 748.2781
1307.3479 | 752.6227
1308.3479 | 747.9813
1309.3479 | 746.2018
1310.3479 | 744.5286
1311.3479 | 746.6591
1312.3479 | 744.9548
1313.3479 | 742.8438
1314.3479 | 744.3443
1315.3479 | 748.9541
1316.3479 | 750.0085
1317.3479 | 753.9671
1318.3479 | 759.6482
1319.3479 | 762.3104
1320.3479 | 759.659
1321.3479 | 759.9196
1322.3479 | 760.4925
1323.3479 | 764.8184
1324.3479 | 763.6784
1325.3479 | 762.3401
1326.3479 | 759.8319
1327.3479 | 759.7082
1328.3479 | 761.7941
1329.3479 | 759.253
1330.3479 | 759.4334
1331.3479 | 762.5003
1332.3479 | 760.0241
1333.3479 | 756.2505
1334.3479 | 753.1839
1335.3479 | 750.6883
1336.3479 | 748.3566
1337.3479 | 746.542
1338.3479 | 743.8846
1339.3479 | 748.4807
1340.3479 | 747.9623
1341.3479 | 746.5965
1342.3479 | 751.1595
1343.3479 | 750.6093
1344.3479 | 750.1089
1345.3479 | 755.2278
1346.3479 | 757.4804
1347.3479 | 754.4663
1348.3479 | 754.9538
1349.3479 | 759.7496
1350.3479 | 761.8272
1351.3479 | 766.4646
1352.3479 | 769.101
1353.3479 | 771.6918
1354.3479 | 775.5428
1355.3479 | 776.7462
1356.3479 | 778.3267
1357.3479 | 773.9801
1358.3479 | 778.2321
1359.3479 | 784.0456
1360.3479 | 778.7983
1361.3479 | 774.3742
1362.3479 | 769.8309
1363.3479 | 769.3263
1364.3479 | 768.4332
1365.3479 | 764.001
1366.3479 | 763.84
1367.3479 | 763.5622
1368.3479 | 760.3311
1369.3479 | 757.6872
1370.3479 | 753.9958
1371.3479 | 751.5018
1372.3479 | 749.8068
1373.3479 | 747.147
1374.3479 | 745.1371
1375.3479 | 742.3404
1376.3479 | 743.238
1377.3479 | 741.1809
1378.3479 | 740.1612
1379.3479 | 739.979
1380.3479 | 739.8637
1381.3479 | 740.3668
1382.3479 | 740.2269
1383.3479 | 744.1087
1384.3479 | 745.5042
1385.3479 | 743.281
1386.3479 | 744.5622
1387.3479 | 746.0423
1388.3479 | 746.7664
1389.3479 | 744.7139
1390.3479 | 744.188
1391.3479 | 747.0772
1392.3479 | 746.5235
1393.3479 | 745.5408
1394.3479 | 744.8063
1395.3479 | 743.5481
1396.3479 | 745.2621
1397.3479 | 744.4517
1398.3479 | 741.7752
1399.3479 | 746.8598
1400.3479 | 745.5934
1401.3479 | 744.8057
1402.3479 | 744.7484
1403.3479 | 739.4917
1404.3479 | 736.9726
1405.3479 | 737.9635
1406.3479 | 739.4237
1407.3479 | 739.1286
1408.3479 | 737.765
1409.3479 | 734.1608
1410.3479 | 726.9619
1411.3479 | 721.3417
1412.3479 | 723.3037
1413.3479 | 720.1057
1414.3479 | 721.126
1415.3479 | 723.6726
1416.3479 | 726.1808
1417.3479 | 725.6577
1418.3479 | 722.5308
1419.3479 | 721.2829
1420.3479 | 721.337
1421.3479 | 720.6471
1422.3479 | 720.3075
1423.3479 | 716.8711
1424.3479 | 713.2581
1425.3479 | 713.4968
1426.3479 | 715.1829
1427.3479 | 713.9658
1428.3479 | 712.9782
1429.3479 | 713.074
1430.3479 | 710.6534
1431.3479 | 711.8534
1432.3479 | 713.2946
1433.3479 | 713.4284
1434.3479 | 713.0781
1435.3479 | 711.9763
1436.3479 | 708.9599
1437.3479 | 708.4323
1438.3479 | 712.6813
1439.3479 | 714.2628
1440.3479 | 713.4385
1441.3479 | 709.4131
1442.3479 | 708.2112
1443.3479 | 708.1345
1444.3479 | 708.9759
1445.3479 | 707.1536
1446.3479 | 706.0131
1447.3479 | 706.9728
1448.3479 | 706.5429
1449.3479 | 704.7857
1450.3479 | 703.5363
1451.3479 | 703.4014
1452.3479 | 698.4711
1453.3479 | 699.5383
1454.3479 | 702.7481
1455.3479 | 704.3427
1456.3479 | 706.8733
1457.3479 | 706.0029
1458.3479 | 704.5153
1459.3479 | 705.1351
1460.3479 | 707.1228
1461.3479 | 710.5421
1462.3479 | 712.0185
1463.3479 | 710.3159
1464.3479 | 709.6627
1465.3479 | 710.7437
1466.3479 | 710.8472
1467.3479 | 708.6034
1468.3479 | 706.7048
1469.3479 | 706.7172
1470.3479 | 705.3292
1471.3479 | 703.9357
1472.3479 | 698.7501
1473.3479 | 698.7552
1474.3479 | 698.2925
1475.3479 | 699.6111
1476.3479 | 702.3534
1477.3479 | 703.1759
1478.3479 | 704.2214
1479.3479 | 706.1922
1480.3479 | 708.8177
1481.3479 | 707.9766
1482.3479 | 706.3146
1483.3479 | 704.7664
1484.3479 | 710.397
1485.3479 | 711.98
1486.3479 | 713.3846
1487.3479 | 713.2933
1488.3479 | 711.4277
1489.3479 | 714.5379
1490.3479 | 713.7751
1491.3479 | 713.9016
1492.3479 | 711.7791
1493.3479 | 711.1714
1494.3479 | 709.9764
1495.3479 | 711.9287
1496.3479 | 719.6151
1497.3479 | 720.6734
1498.3479 | 723.1313
1499.3479 | 723.5537
1500.3479 | 726.1078
1501.3479 | 727.3035
1502.3479 | 724.8158
1503.3479 | 724.3925
1504.3479 | 723.7652
1505.3479 | 725.5667
1506.3479 | 723.4788
1507.3479 | 723.0028
1508.3479 | 725.3466
1509.3479 | 727.7539
1510.3479 | 728.7601
1511.3479 | 731.3812
1512.3479 | 732.5548
1513.3479 | 731.4824
1514.3479 | 731.5587
1515.3479 | 731.9957
1516.3479 | 732.5185
1517.3479 | 735.9944
1518.3479 | 735.9385
1519.3479 | 731.4071
1520.3479 | 732.7197
1521.3479 | 734.8116
1522.3479 | 734.4867
1523.3479 | 735.7017
1524.3479 | 735.9956
1525.3479 | 735.5858
1526.3479 | 736.1995
1527.3479 | 736.9064
1528.3479 | 738.8982
1529.3479 | 737.4677
1530.3479 | 742.9193
1531.3479 | 745.0076
1532.3479 | 748.8842
1533.3479 | 745.9686
1534.3479 | 747.2043
1535.3479 | 747.3141
1536.3479 | 753.2442
1537.3479 | 753.4865
1538.3479 | 750.1323
1539.3479 | 747.489
1540.3479 | 750.2248
1541.3479 | 751.1068
1542.3479 | 754.4981
1543.3479 | 746.9756
1544.3479 | 745.7207
1545.3479 | 746.5129
1546.3479 | 746.8999
1547.3479 | 748.2129
1548.3479 | 747.9631
1549.3479 | 750.5486
1550.3479 | 748.4023
1551.3479 | 744.9512
1552.3479 | 745.2919
1553.3479 | 746.4239
1554.3479 | 749.0328
1555.3479 | 748.419
1556.3479 | 747.2808
1557.3479 | 745.9122
1558.3479 | 745.4399
1559.3479 | 747.1107
1560.3479 | 745.4175
1561.3479 | 749.4483
1562.3479 | 751.6733
1563.3479 | 750.7858
1564.3479 | 751.1138
1565.3479 | 756.4004
1566.3479 | 762.1062
1567.3479 | 763.1141
1568.3479 | 761.0257
1569.3479 | 758.7191
1570.3479 | 760.4137
1571.3479 | 760.1104
1572.3479 | 758.69
1573.3479 | 761.429
1574.3479 | 765.6694
1575.3479 | 768.307
1576.3479 | 766.2787
1577.3479 | 761.373
1578.3479 | 758.7945
1579.3479 | 756.3686
1580.3479 | 755.7668
1581.3479 | 757.3166
1582.3479 | 755.8013
1583.3479 | 752.4611
1584.3479 | 749.7618
1585.3479 | 743.4284
1586.3479 | 740.5123
1587.3479 | 741.027
1588.3479 | 738.6558
1589.3479 | 745.2001
1590.3479 | 746.5656
1591.3479 | 749.03
1592.3479 | 750.212
1593.3479 | 752.7263
1594.3479 | 750.015
1595.3479 | 744.9233
1596.3479 | 745.2415
1597.3479 | 742.3083
1598.3479 | 742.1976
1599.3479 | 747.2054
1600.3479 | 754.4406
1601.3479 | 760.5232
1602.3479 | 761.1891
1603.3479 | 757.062
1604.3479 | 753.828
1605.3479 | 757.6403
1606.3479 | 754.3322
1607.3479 | 749.759
1608.3479 | 747.4608
1609.3479 | 742.4418
1610.3479 | 738.4406
1611.3479 | 737.0091
1612.3479 | 741.0108
1613.3479 | 747.9997
1614.3479 | 748.6251
1615.3479 | 753.302
1616.3479 | 752.78
1617.3635 | 751.9879
1618.3479 | 758.1165
1619.3479 | 762.3902
1620.3479 | 764.1063
1621.3479 | 764.0935
1622.3479 | 763.8527
1623.3479 | 765.5348
1624.3479 | 767.7908
1625.3479 | 763.9896
1626.3479 | 758.8688
1627.3479 | 754.9049
1628.3479 | 755.781
1629.3479 | 753.8032
1630.3479 | 754.0308
1631.3479 | 759.2211
1632.3479 | 761.8596
1633.3479 | 758.9414
1634.3479 | 759.2318
1635.3479 | 760.0895
1636.3479 | 758.0444
1637.3479 | 755.1406
1638.3479 | 757.9299
1639.3479 | 756.3414
1640.3479 | 754.9872
1641.3479 | 755.4306
1642.3479 | 755.4179
1643.3479 | 752.0979
1644.3479 | 748.3638
1645.3479 | 748.8618
1646.3479 | 749.1649
1647.3635 | 752.0897
1648.3479 | 750.0044
1649.3479 | 750.0892
1650.3479 | 756.3857
1651.3479 | 751.1322
1652.3479 | 743.4844
1653.3479 | 748.365
1654.3479 | 758.4648
1655.3479 | 759.5028
1656.3479 | 754.6194
1657.3479 | 753.1335
1658.3479 | 747.9044
1659.3479 | 752.9454
1660.3479 | 756.3043
1661.3479 | 756.9057
1662.3479 | 765.2066
1663.3479 | 772.9341
1664.3479 | 778.6534
1665.3479 | 779.7333
1666.3479 | 772.3535
1667.3479 | 761.7264
1668.3479 | 750.7147
1669.3479 | 747.416
1670.3479 | 750.2299
1671.3479 | 757.5313
1672.3479 | 763.1372
1673.3479 | 763.0563
1674.3479 | 759.8054
1675.3479 | 759.2393
1676.3479 | 752.7723
1677.3479 | 748.1674
1678.3479 | 742.4588
1679.3479 | 737.1945
1680.3479 | 732.6475
1681.3479 | 731.2078
1682.3479 | 732.5797
1683.3479 | 733.609
1684.3479 | 734.163
1685.3479 | 738.1005
1686.3479 | 736.5628
1687.3479 | 733.4776
1688.3479 | 738.6751
1689.3479 | 741.0256
1690.3479 | 742.0576
1691.3479 | 741.2295
1692.3479 | 741.9334
1693.3479 | 737.043
1694.3479 | 744.0013
1695.3479 | 743.541
1696.3479 | 741.9642
1697.3479 | 742.1056
1698.3479 | 747.7861
1699.3479 | 747.9606
1700.3479 | 744.7107
1701.3479 | 741.8105
1702.3479 | 751.2961
1703.3479 | 751.8388
1704.3479 | 746.1547
1705.3479 | 738.443
1706.3479 | 731.9946
1707.3479 | 728.1491
1708.3479 | 724.0974
1709.3479 | 725.9578
1710.3479 | 727.8299
1711.3479 | 728.2638
1712.3479 | 727.8695
1713.3479 | 727.2505
1714.3479 | 730.1586
1715.3479 | 736.1885
1716.3479 | 733.4776
1717.3479 | 736.0887
1718.3479 | 738.1573
1719.3479 | 737.7804
1720.3479 | 739.9118
1721.3479 | 743.401
1722.3479 | 737.6754
1723.3479 | 734.1502
1724.3479 | 735.3726
1725.3479 | 732.5353
1726.3479 | 727.4849
1727.3479 | 727.1541
1728.3479 | 725.5627
1729.3479 | 733.094
1730.3479 | 738.6499
1731.3479 | 739.351
1732.3479 | 737.2873
1733.3479 | 733.9103
1734.3479 | 732.5239
1735.3479 | 729.5879
1736.3479 | 727.4514
1737.3479 | 727.0005
1738.3479 | 732.3114
1739.3479 | 725.257
1740.3479 | 718.8433
1741.3479 | 717.6536
1742.3479 | 718.1027
1743.3479 | 718.4883
1744.3479 | 718.3515
1745.3479 | 718.0145
1746.3479 | 717.0605
1747.3479 | 715.9211
1748.3479 | 715.0336
1749.3479 | 713.5395
1750.3479 | 713.4641
1751.3479 | 709.4577
1752.3479 | 706.0174
1753.3479 | 705.6849
1754.3479 | 706.7262
1755.3479 | 707.326
1756.3479 | 705.2975
1757.3479 | 702.1836
1758.3479 | 705.3739
1759.3479 | 710.6814
1760.3479 | 714.7293
1761.3479 | 716.4606
1762.3479 | 717.8309
1763.3479 | 720.2012
1764.3479 | 722.6917
1765.3479 | 720.1556
1766.3479 | 721.93
1767.3479 | 715.7681
1768.3479 | 719.5229
1769.3479 | 722.994
1770.3479 | 730.4181
1771.3479 | 730.8791
1772.3479 | 729.9824
1773.3479 | 738.656
1774.3479 | 743.1818
1775.3479 | 744.6885
1776.3479 | 750.7904
1777.3479 | 747.3792
1778.3479 | 744.1582
1779.3479 | 744.6905
1780.3479 | 747.7302
1781.3479 | 740.8941
1782.3479 | 734.7115
1783.3479 | 730.5217
1784.3479 | 727.6215
1785.3479 | 724.7067
1786.3479 | 724.2244
1787.3479 | 722.5349
1788.3479 | 722.9603
1789.3479 | 727.1901
1790.3479 | 725.9302
1791.3479 | 728.8314
1792.3479 | 727.0474
1793.3479 | 724.3912
1794.3479 | 727.0477
1795.3479 | 726.6568
1796.3479 | 732.1008
1797.3635 | 738.1088
1798.3479 | 742.5537
1799.3479 | 737.0968
1800.3479 | 739.6845
1801.3479 | 743.5961
1802.3479 | 746.19
1803.3479 | 744.1517
1804.3479 | 735.4647
1805.3479 | 733.8912
1806.3479 | 732.0009
1807.3479 | 737.2043
1808.3479 | 739.9597
1809.3479 | 736.5615
1810.3479 | 737.7801
1811.3479 | 736.3213
1812.3479 | 743.7015
1813.3479 | 750.034
1814.3479 | 751.3113
1815.3479 | 745.705
1816.3479 | 740.9682
1817.3479 | 735.3589
1818.3479 | 730.6028
1819.3479 | 730.8766
1820.3479 | 732.3591
1821.3479 | 729.04
1822.3479 | 727.7901
1823.3479 | 727.3736
1824.3479 | 723.6685
1825.3479 | 726.9258
1826.3479 | 727.2547
1827.3479 | 725.0168
1828.3479 | 722.4754
1829.3479 | 720.9686
1830.3479 | 720.717
1831.3479 | 722.8668
1832.3479 | 724.401
1833.3479 | 724.8167
1834.3479 | 722.6011
1835.3479 | 720.7817
1836.3479 | 718.3377
1837.3479 | 716.0219
1838.3479 | 716.5
1839.3479 | 712.2629
1840.3479 | 711.0771
1841.3479 | 713.2244
1842.3479 | 715.2058
1843.3479 | 713.3393
1844.3479 | 710.1029
1845.3479 | 707.3175
1846.3479 | 703.0808
1847.3479 | 696.973
1848.3479 | 694.0176
1849.3479 | 695.2473
1850.3479 | 702.4766
1851.3479 | 704.9082
1852.3479 | 707.0315
1853.3479 | 710.2922
1854.3479 | 706.4928
1855.3479 | 703.0376
1856.3479 | 709.0989
1857.3479 | 710.8416
1858.3479 | 709.913
1859.3479 | 706.7413
1860.3479 | 712.874
1861.3479 | 723.3595
1862.3479 | 726.5622
1863.3479 | 722.3251
1864.3479 | 719.07
1865.3479 | 717.631
1866.3479 | 711.5988
1867.3479 | 710.5211
1868.3479 | 711.5553
1869.3479 | 714.5292
1870.3479 | 713.7596
1871.3479 | 708.3528
1872.3479 | 703.1343
1873.3479 | 697.937
1874.3479 | 697.0789
1875.3479 | 700.9127
1876.3479 | 706.4845
1877.3479 | 705.5346
1878.3479 | 705.3539
1879.3479 | 703.7814
1880.3479 | 700.8172
1881.3479 | 698.0246
1882.3479 | 699.1344
1883.3479 | 700.7274
1884.3479 | 702.6803
1885.3479 | 700.9827
1886.3479 | 706.2081
1887.3479 | 712.4149
1888.3479 | 721.8381
1889.3479 | 726.0045
1890.3479 | 724.208
1891.3479 | 720.8824
1892.3479 | 716.6998
1893.3479 | 716.6672
1894.3479 | 718.5244
1895.3479 | 731.559
1896.3479 | 739.8087
1897.3479 | 741.0928
1898.3479 | 738.1263
1899.3479 | 727.6411
1900.3479 | 724.7695
1901.3479 | 722.073
1902.3479 | 723.7899
1903.3479 | 719.5361
1904.3479 | 714.6982
1905.3479 | 712.1463
1906.3479 | 716.5536
1907.3479 | 714.0635
1908.3479 | 716.6409
1909.3479 | 730.1338
1910.3479 | 726.8495
1911.3479 | 727.3756
1912.3479 | 725.0484
1913.3479 | 719.79
1914.3479 | 716.299
1915.3479 | 710.7514
1916.3479 | 713.8846
1917.3479 | 724.0811
1918.3479 | 731.6263
1919.3479 | 733.5677
1920.3479 | 723.436
1921.3479 | 717.171
1922.3479 | 718.6794
1923.3479 | 725.7327
1924.3479 | 736.9488
1925.3479 | 739.1193
1926.3479 | 734.2462
1927.3479 | 735.7241
1928.3479 | 733.4926
1929.3479 | 730.5795
1930.3479 | 728.3773
1931.3479 | 729.1369
1932.3479 | 727.9389
1933.3479 | 725.7717
1934.3479 | 723.2444
1935.3479 | 718.7492
1936.3479 | 713.5881
1937.3479 | 711.1841
1938.3479 | 705.7809
1939.3479 | 704.0709
1940.3479 | 705.5227
1941.3479 | 702.3684
1942.3479 | 699.5358
1943.3479 | 693.6277
1944.3479 | 691.457
1945.3479 | 706.9933
1946.3479 | 717.1018
1947.3479 | 720.2947
1948.3479 | 718.0852
1949.3479 | 711.6035
1950.3479 | 713.6212
1951.3479 | 710.2595
1952.3479 | 715.7822
1953.3479 | 722.8383
1954.3479 | 723.2395
1955.3479 | 726.4854
1956.3479 | 720.1057
1957.3479 | 719.0796
1958.3479 | 719.1353
1959.3479 | 716.386
1960.3479 | 714.9503
1961.3479 | 710.3993
1962.3479 | 710.2322
1963.3479 | 714.485
1964.3479 | 717.3571
1965.3479 | 716.6462
1966.3479 | 718.2558
1967.3479 | 718.5591
1968.3479 | 720.6136
1969.3479 | 720.5476
1970.3479 | 719.1252
1971.3479 | 714.2599
1972.3479 | 709.6056
1973.3479 | 717.4624
1974.3479 | 727.6855
1975.3479 | 734.3174
1976.3479 | 737.0817
1977.3479 | 740.0614
1978.3479 | 745.7978
1979.3479 | 744.1116
1980.3479 | 743.5394
1981.3479 | 742.5196
1982.3479 | 740.2952
1983.3479 | 742.5241
1984.3479 | 739.776
1985.3479 | 749.7363
1986.3479 | 746.5961
1987.3479 | 739.1304
1988.3479 | 731.0178
1989.3479 | 727.0194
1990.3479 | 729.5298
1991.3479 | 731.0722
1992.3479 | 733.6164
1993.3479 | 738.8084
1994.3479 | 747.0629
1995.3479 | 748.0485
1996.3479 | 753.8061
1997.3479 | 746.3277
1998.3479 | 740.9141
1999.3479 | 737.3707
2000.3479 | 745.5658
2001.3479 | 746.1218
2002.3479 | 742.4746
2003.3479 | 735.5909
2004.3479 | 732.1856
2005.3479 | 733.6553
2006.3479 | 733.4652
2007.3479 | 756.692
2008.3479 | 768.5378
2009.3479 | 774.4401
2010.3479 | 763.4329
2011.3479 | 756.3487
2012.3479 | 752.4358
2013.3479 | 748.6702
2014.3479 | 746.0004
2015.3479 | 741.8768
2016.3479 | 746.0162
2017.3479 | 747.7451
2018.3479 | 745.9416
2019.3479 | 746.6234
2020.3479 | 742.8875
2021.3479 | 740.1369
2022.3479 | 734.6146
2023.3479 | 731.5527
2024.3479 | 730.4217
2025.3479 | 732.6316
2026.3479 | 734.3146
2027.3479 | 735.3024
2028.3479 | 731.4906
2029.3479 | 725.8088
2030.3479 | 726.2423
2031.3479 | 724.0099
2032.3479 | 722.5065
2033.3479 | 724.3583
2034.3479 | 725.4033
2035.3479 | 720.3517
2036.3479 | 716.1741
2037.3479 | 711.9358
2038.3479 | 716.4514
2039.3479 | 721.6071
2040.3479 | 721.7595
2041.3479 | 724.0493
2042.3479 | 728.1421
2043.3479 | 732.2707
2044.3479 | 745.7182
2045.3479 | 747.3093
2046.3479 | 741.9805
2047.3479 | 741.9262
2048.3479 | 734.5717
2049.3479 | 726.8857
2050.3479 | 724.9305
2051.3479 | 720.6279
2052.3479 | 720.087
2053.3479 | 720.9457
2054.3479 | 716.7477
2055.3479 | 711.5243
2056.3479 | 707.8672
2057.3479 | 711.1812
2058.3479 | 718.1255
2059.3479 | 717.7972
2060.3479 | 726.8467
2061.3479 | 733.4841
2062.3479 | 738.8685
2063.3479 | 737.5415
2064.3479 | 737.7744
2065.3479 | 732.0362
2066.3479 | 721.7327
2067.3479 | 716.1421
2068.3479 | 715.3514
2069.3479 | 718.2445
2070.3479 | 722.9821
2071.3479 | 724.5922
2072.3479 | 721.9057
2073.3479 | 717.9674
2074.3479 | 716.9663
2075.3479 | 716.7071
2076.3479 | 718.4359
2077.3479 | 718.1148
2078.3479 | 715.7999
2079.3479 | 711.2058
2080.3479 | 709.7837
2081.3479 | 711.6527
2082.3479 | 712.9846
2083.3479 | 716.7681
2084.3479 | 718.3306
2085.3479 | 712.2914
2086.3479 | 711.4471
2087.3479 | 715.6248
2088.3479 | 717.1218
2089.3479 | 717.8246
2090.3479 | 722.4577
2091.3479 | 727.0696
2092.3479 | 729.9198
2093.3479 | 732.7414
2094.3479 | 733.6371
2095.3479 | 743.3324
2096.3479 | 744.6043
2097.3635 | 752.757
2098.3479 | 750.2154
2099.3479 | 750.4164
2100.3479 | 750.4418
2101.3479 | 749.046
2102.3479 | 742.0686
2103.3479 | 735.1131
2104.3479 | 738.3556
2105.3479 | 739.0721
2106.3479 | 737.377
2107.3479 | 744.3373
2108.3479 | 743.2703
2109.3479 | 741.3535
2110.3479 | 741.16
2111.3479 | 738.4613
2112.3479 | 737.0612
2113.3479 | 744.9819
2114.3479 | 752.8796
2115.3479 | 755.6915
2116.3479 | 753.0877
2117.3479 | 750.3694
2118.3479 | 750.1098
2119.3479 | 747.9065
2120.3479 | 746.4507
2121.3479 | 746.0449
2122.3479 | 743.9054
2123.3479 | 739.4356
2124.3479 | 738.9222
2125.3479 | 734.6833
2126.3479 | 735.9181
2127.3479 | 733.8647
2128.3479 | 736.7845
2129.3479 | 745.8893
2130.3479 | 744.6095
2131.3479 | 743.9118
2132.3479 | 750.9574
2133.3479 | 748.8241
2134.3479 | 760.5801
2135.3479 | 777.3384
2136.3479 | 793.3457
2137.3479 | 787.4247
2138.3479 | 790.6138
2139.3479 | 792.1739
2140.3479 | 788.9708
2141.3479 | 789.1961
2142.3479 | 784.4065
2143.3479 | 780.7546
2144.3479 | 785.4871
2145.3479 | 788.5352
2146.3479 | 798.2445
2147.3479 | 803.6905
2148.3479 | 807.8225
2149.3479 | 802.6747
2150.3479 | 800.2367
2151.3479 | 812.6157
2152.3479 | 824.4385
2153.3479 | 834.0941
2154.3479 | 835.919
2155.3479 | 827.6676
2156.3479 | 819.4512
2157.3479 | 820.7259
2158.3479 | 818.743
2159.3479 | 813.9902
2160.3479 | 825.8267
2161.3479 | 826.9656
2162.3479 | 818.9701
2163.3479 | 825.8785
2164.3479 | 836.6386
2165.3479 | 842.2846
2166.3479 | 839.6299
2167.3479 | 847.0823
2168.3479 | 847.5898
2169.3479 | 850.7233
2170.3479 | 847.0156
2171.3479 | 840.8387
2172.3479 | 847.1027
2173.3479 | 848.2582
2174.3479 | 846.5141
2175.3479 | 851.5887
2176.3479 | 847.9341
2177.3479 | 851.8087
2178.3479 | 853.1681
2179.3479 | 853.4266
2180.3479 | 844.258
2181.3479 | 840.552
2182.3479 | 846.1584
2183.3479 | 845.449
2184.3479 | 846.6697
2185.3479 | 846.9653
2186.3479 | 843.9277
2187.3479 | 847.4867
2188.3479 | 848.0998
2189.3479 | 838.931
2190.3479 | 828.4383
2191.3479 | 827.068
2192.3479 | 827.7271
2193.3479 | 833.7493
2194.3479 | 828.9148
2195.3479 | 825.5849
2196.3479 | 827.24
2197.3479 | 836.3193
2198.3635 | 842.3878
2199.3479 | 843.6696
2200.3479 | 835.8661
2201.3479 | 824.6459
2202.3479 | 819.6723
2203.3479 | 816.592
2204.3479 | 813.1654
2205.3479 | 805.7694
2206.3479 | 806.9915
2207.3479 | 813.4695
2208.3479 | 811.6383
2209.3479 | 813.1161
2210.3479 | 820.3629
2211.3479 | 829.6578
2212.3479 | 834.1381
2213.3479 | 835.8934
2214.3479 | 835.4041
2215.3479 | 842.0246
2216.3479 | 840.7035
2217.3479 | 836.1455
2218.3479 | 829.6448
2219.3479 | 823.8635
2220.3479 | 815.6334
2221.3479 | 822.2302
2222.3479 | 829.7683
2223.3479 | 821.2641
2224.3479 | 813.5162
2225.3479 | 811.2628
2226.3479 | 809.9724
2227.3479 | 802.7749
2228.3479 | 794.7355
2229.3479 | 792.6646
2230.3479 | 792.9495
2231.3479 | 797.1754
2232.3479 | 806.3809
2233.3479 | 812.7107
2234.3479 | 819.3159
2235.3479 | 821.4646
2236.3479 | 815.5562
2237.3479 | 807.5353
2238.3479 | 818.1303
2239.3479 | 814.2672
2240.3479 | 822.6575
2241.3479 | 821.1903
2242.3479 | 828.9798
2243.3479 | 830.7345
2244.3479 | 840.179
2245.3479 | 844.483
2246.3479 | 853.0725
2247.3479 | 852.1126
2248.3479 | 836.8711
2249.3479 | 827.9049
2250.3479 | 826.4933
2251.3479 | 830.1674
2252.3479 | 831.829
2253.3479 | 828.6202
2254.3479 | 831.7832
2255.3479 | 823.9664
2256.3479 | 817.2402
2257.3479 | 823.4291
2258.3479 | 837.4841
2259.3479 | 846.2735
2260.3479 | 849.7797
2261.3479 | 849.0557
2262.3479 | 851.5859
2263.3479 | 847.3714
2264.3479 | 850.3438
2265.3479 | 853.7895
2266.3479 | 852.0156
2267.3479 | 838.8439
2268.3479 | 837.0418
2269.3479 | 839.686
2270.3479 | 839.6853
2271.3479 | 837.8201
2272.3479 | 827.7113
2273.3479 | 837.6665
2274.3479 | 848.2945
2275.3479 | 851.7863
2276.3479 | 849.7242
2277.3479 | 841.7082
2278.3479 | 835.7713
2279.3479 | 829.8271
2280.3479 | 827.8093
2281.3479 | 831.4896
2282.3479 | 829.9961
2283.3479 | 827.7296
2284.3479 | 822.162
2285.3479 | 822.5204
2286.3479 | 811.0689
2287.3479 | 813.6985
2288.3479 | 827.8174
2289.3479 | 836.5997
2290.3479 | 842.6862
2291.3479 | 844.179
2292.3479 | 851.9119
2293.3479 | 847.884
2294.3479 | 848.1946
2295.3479 | 857.5339
2296.3479 | 853.5552
2297.3479 | 851.1657
2298.3479 | 853.4262
2299.3479 | 859.4024
2300.3479 | 858.1115
2301.3479 | 861.0133
2302.3479 | 849.2709
2303.3479 | 847.8347
2304.3479 | 854.2782
2305.3479 | 854.1612
2306.3479 | 851.75
2307.3479 | 846.1877
2308.3479 | 848.6294
2309.3479 | 848.1518
2310.3479 | 853.5639
2311.3479 | 853.2753
2312.3479 | 859.2569
2313.3479 | 866.3902
2314.3479 | 859.87
2315.3479 | 842.6314
2316.3479 | 828.8645
2317.3479 | 825.9138
2318.3479 | 830.5159
2319.3479 | 834.571
2320.3479 | 835.9629
2321.3479 | 818.0967
2322.3479 | 805.5471
2323.3479 | 795.0677
2324.3479 | 788.6877
2325.3479 | 784.1728
2326.3479 | 789.8495
2327.3479 | 806.3076
2328.3479 | 814.8026
2329.3479 | 825.5851
2330.3479 | 825.7514
2331.3479 | 828.3309
2332.3479 | 838.218
2333.3479 | 844.0511
2334.3479 | 852.7142
2335.3479 | 857.5318
2336.3479 | 857.9097
2337.3479 | 854.6666
2338.3479 | 855.3502
2339.3479 | 848.681
2340.3479 | 839.1719
2341.3479 | 838.0594
2342.3479 | 840.4894
2343.3479 | 846.6333
2344.3479 | 848.0378
2345.3479 | 853.9902
2346.3479 | 854.6175
2347.3479 | 852.6243
2348.3479 | 860.0178
2349.3479 | 863.571
2350.3479 | 867.4513
2351.3479 | 871.3075
2352.3479 | 872.5902
2353.3479 | 871.2201
2354.3479 | 871.5104
2355.3479 | 865.0594
2356.3479 | 855.3792
2357.3479 | 860.1077
2358.3479 | 858.1406
2359.3479 | 854.3766
2360.3479 | 848.669
2361.3479 | 846.6777
2362.3479 | 847.5142
2363.3479 | 838.892
2364.3479 | 840.1926
2365.3479 | 841.4234
2366.3479 | 839.4155
2367.3479 | 829.9872
2368.3479 | 837.3195
2369.3479 | 831.3655
2370.3479 | 821.4225
2371.3479 | 821.2349
2372.3479 | 829.9075
2373.3479 | 845.6199
2374.3479 | 845.0769
2375.3479 | 844.2397
2376.3479 | 851.9127
2377.3479 | 856.7037
2378.3635 | 853.8191
2379.3479 | 847.2976
2380.3479 | 845.7686
2381.3479 | 845.7677
2382.3479 | 837.6675
2383.3479 | 833.2973
2384.3479 | 847.5521
2385.3479 | 850.9097
2386.3479 | 861.504
2387.3479 | 865.6781
2388.3479 | 862.6739
2389.3479 | 876.0449
2390.3479 | 861.7796
2391.3479 | 856.4639
2392.3479 | 847.7859
2393.3479 | 842.9344
2394.3479 | 837.9308
2395.3479 | 836.9972
2396.3479 | 841.2984
2397.3479 | 845.8638
2398.3479 | 848.0209
2399.3479 | 850.7201
2400.3479 | 842.1634