## Test Conditions
DESIREE-FIRE Intermediate Scale Test 8 - Circuit Simulator Data Only
Test Date: | 2009-11-17
DCSim DAQ Start Time | 10:35
DCSim Time for Synchronization | 10:38
Heat Source Synchronization | 0:03 | hour:minutes:seconds
Heat Source DAQ Start Time | 10:35
Fire Time | 11:34
Offset | 0:59 | hour:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 3565 | seconds
Heat Source Offset | 0:59 | hour:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 3568 | seconds
Heat Source Stop Time | 12:16
Test Duration | 0:42 | hour:minutes:seconds
| 2495 | seconds
CT500 turns | 2 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 turns | 5 | 1 or 5
Pre-Test Baseline: | Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
SOV 1 | PE/PVC, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 0 which is defined as "A Position - Middle" in the Temperature Data File respresents the temperature in the center of the cable tray.
SOV 2 | PE/PVC, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 2, 3, and 4 represents the air temperature 3', 5', and 7' down the cable tray located in C-Position. These are labeled as "C-Position - 3'", "C-Position - Middle", " C-Position - 7'", respectively.
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | SOV-1_CT500 | SOV-1_CT35_1_P | SOV-1_CT35_2_S1 | SOV-1_CT35_3_G | SOV-1_CT35_4_S2 | SOV-1_CT35_5_N | SOV-2_CT500 | SOV-2_CT35_1_P | SOV-2_CT35_2_S1 | SOV-2_CT35_3_G | SOV-2_CT35_4_S2 | SOV-2_CT35_5_N | SOV-1_VT7_1_R | SOV-1_VT7_2_SP | SOV-1_VT7_3_S | SOV-1_VTU_1_P | SOV-1_VTU_2_S1 | SOV-1_VTU_3_G | SOV-1_VTU_4_N | SOV-2_VT7_1_R | SOV-2_VT7_2_SP | SOV-2_VT7_3_S | SOV-2_VTU_1_P | SOV-2_VTU_2_S1 | SOV-2_VTU_3_G | SOV-2_VTU_4_N | {SOV1} V(N) - V(Batt -) | {SOV1} V(P) - V(Batt +) | {SOV1} V(R) - V(Batt -) | {SOV1} V(S) - V(Batt -) | {SOV1} V(S) - V(N) | {SOV1} V(S1) - V(Batt +) | {SOV1} V(G) - V(Batt +) | {SOV2} V(N) - V(Batt -) | {SOV2} V(P) - V(Batt +) | {SOV2} V(R) - V(Batt -) | {SOV2} V(S) - V(Batt -) | {SOV2} V(S) - V(N) | {SOV2} V(S1) - V(Batt +) | {SOV2} V(G) - V(Batt +) | {SOV1} V(P) - V(Batt -) | {SOV1} V(S1) - V(Batt -) | {SOV1} V(G) - V(Batt -) | {SOV1} V(SP) - V(Batt -) | {SOV1} V(N) - V(Batt +) | {SOV2} V(P) - V(Batt -) | {SOV2} V(S1) - V(Batt -) | {SOV1} V(G) - V(Batt -) | {SOV2} V(SP) - V(Batt -) | {SOV2} V(N) - V(Batt +)
-1.5156 | 121.7834 | -61.7889 | 59.8022 | 0.002213 | -0.024532 | 0.00092741 | 0.05644 | -0.0040233 | 0.052888 | -0.011751 | -0.00094006 | -0.0012306 | -0.0030915 | 0.011869 | -0.0068945 | -59.0556 | -0.021486 | -61.7328 | 59.7406 | 59.5264 | 59.3525 | -61.7274 | 0.074307 | 0.050725 | -61.8598 | 59.4813 | 59.5722 | 59.7036 | -61.6989 | 0.061506 | -0.061676 | 2.7334 | 0.056152 | -0.005354 | -0.27587 | -0.44979 | 0.090067 | -0.32092 | 61.8632 | -0.070837 | -0.1609 | -0.23008 | -0.098676 | 121.5295 | 121.3153 | 121.1414 | 61.7675 | -121.5297 | 121.2703 | 121.3611 | 121.4925 | 61.8397 | -121.5011
0.23438 | 121.8613 | -61.7935 | 59.7427 | -0.005418 | -0.024318 | 0.001141 | 0.056227 | -0.0042369 | 0.052674 | -0.019381 | -0.0011537 | -0.001017 | -0.0033051 | 0.012083 | -0.0068945 | -59.0785 | -0.016908 | -61.7282 | 59.7406 | 59.531 | 59.3479 | -61.7274 | 0.083464 | 0.064461 | -61.8598 | 59.4813 | 59.5767 | 59.7127 | -61.6943 | 0.066084 | -0.002167 | 2.715 | 0.065309 | -0.000775 | -0.21178 | -0.39486 | 0.099224 | -0.26141 | 61.877 | -0.066259 | -0.16548 | -0.16599 | -0.03001 | 121.5341 | 121.3245 | 121.1414 | 61.7766 | -121.4702 | 121.2748 | 121.3703 | 121.5062 | 61.858 | -121.437
1.9844 | 121.8979 | -61.6882 | 59.8434 | -0.005418 | -0.024318 | 0.00092741 | 0.05644 | -0.0038097 | 0.052888 | -0.0041205 | -0.00072626 | -0.0012306 | -0.0028779 | 0.012083 | -0.0071083 | -59.1609 | -0.021486 | -61.7328 | 59.7406 | 59.5264 | 59.3479 | -61.7229 | 0.078886 | 0.055303 | -61.8598 | 59.4859 | 59.5722 | 59.7081 | -61.6989 | -0.034623 | -0.10288 | 2.5274 | -0.044556 | -0.009933 | -0.31707 | -0.49557 | -0.010641 | -0.35754 | 61.7671 | -0.17155 | -0.1609 | -0.27128 | -0.1353 | 121.4288 | 121.2146 | 121.0361 | 61.6667 | -121.5663 | 121.1741 | 121.2604 | 121.3964 | 61.7435 | -121.5423
3.6562 | 121.8567 | -61.7889 | 59.7427 | -0.005418 | -0.024104 | 0.00071361 | 0.056227 | -0.0040233 | 0.052888 | -0.011751 | -0.00072626 | -0.001017 | -0.0030915 | 0.012083 | -0.0071083 | -59.0739 | -0.012329 | -61.7236 | 59.7451 | 59.5264 | 59.3525 | -61.7229 | 0.088043 | 0.059882 | -61.8506 | 59.4859 | 59.5767 | 59.7036 | -61.7035 | 0.066085 | 0.002412 | 2.715 | 0.065309 | -0.000776 | -0.21636 | -0.39028 | 0.085488 | -0.25683 | 61.877 | -0.061679 | -0.14717 | -0.16599 | -0.039167 | 121.5341 | 121.3153 | 121.1414 | 61.7766 | -121.4656 | 121.2748 | 121.3657 | 121.4925 | 61.8488 | -121.4462
5.3906 | 121.8704 | -61.7661 | 59.7244 | 0.009844 | -0.024104 | 0.00092741 | 0.056654 | -0.0040233 | 0.052888 | -0.011751 | -0.00094006 | -0.0014444 | -0.0030915 | 0.011869 | -0.0071083 | -59.0785 | -0.016908 | -61.7328 | 59.736 | 59.5264 | 59.3479 | -61.7274 | 0.078886 | 0.059882 | -61.8415 | 59.4813 | 59.5676 | 59.7036 | -61.6943 | 0.038618 | 0.011566 | 2.6876 | 0.033264 | -0.005354 | -0.19805 | -0.37655 | 0.071758 | -0.2431 | 61.8449 | -0.07541 | -0.14717 | -0.15684 | -0.020856 | 121.502 | 121.2924 | 121.1139 | 61.7491 | -121.4519 | 121.2474 | 121.3336 | 121.4696 | 61.8259 | -121.4187
7.125 | 121.8796 | -61.7615 | 59.761 | -0.005418 | -0.023677 | 0.00050001 | 0.056654 | -0.0042369 | 0.053102 | -0.011751 | -0.00094006 | -0.0012306 | -0.0028779 | 0.011869 | -0.0068945 | -59.1014 | -0.026065 | -61.7282 | 59.736 | 59.5264 | 59.3479 | -61.7183 | 0.078886 | 0.064461 | -61.8598 | 59.4813 | 59.5767 | 59.7081 | -61.6989 | 0.043199 | -0.025055 | 2.6601 | 0.033266 | -0.009933 | -0.23467 | -0.41317 | 0.062602 | -0.27972 | 61.8404 | -0.098302 | -0.1609 | -0.1843 | -0.052898 | 121.4975 | 121.2879 | 121.1094 | 61.7354 | -121.4793 | 121.2428 | 121.3382 | 121.4696 | 61.8259 | -121.4599
8.875 | 121.7743 | -61.8073 | 59.7519 | -0.005418 | -0.024532 | 0.00092741 | 0.056227 | -0.0040233 | 0.053315 | 0.00351 | -0.00072626 | -0.0012306 | -0.0030915 | 0.011869 | -0.0071083 | -59.0464 | -0.021486 | -61.7191 | 59.7314 | 59.5264 | 59.3525 | -61.7183 | 0.074307 | 0.064461 | -61.8506 | 59.4813 | 59.5767 | 59.7081 | -61.6989 | 0.088975 | -0.020479 | 2.7608 | 0.088198 | -0.000777 | -0.22551 | -0.39944 | 0.10838 | -0.27057 | 61.8816 | -0.043368 | -0.15175 | -0.17515 | -0.043743 | 121.5387 | 121.3336 | 121.1597 | 61.7858 | -121.4702 | 121.2886 | 121.384 | 121.5154 | 61.8717 | -121.4508
10.5469 | 121.8842 | -61.6745 | 59.8251 | -0.005418 | -0.024532 | 0.00071361 | 0.05644 | -0.0038097 | 0.052888 | -0.011751 | -0.0011537 | -0.0014444 | -0.0028779 | 0.011869 | -0.0071083 | -59.1655 | -0.021486 | -61.7282 | 59.7314 | 59.531 | 59.3433 | -61.7229 | 0.074307 | 0.059882 | -61.8552 | 59.4813 | 59.5813 | 59.7081 | -61.7035 | -0.048355 | -0.093721 | 2.509 | -0.053709 | -0.005354 | -0.29418 | -0.48184 | -0.028952 | -0.34381 | 61.7488 | -0.1807 | -0.15175 | -0.24381 | -0.11698 | 121.4059 | 121.2055 | 121.0178 | 61.653 | -121.548 | 121.1558 | 121.2558 | 121.3826 | 61.7344 | -121.5286
12.2812 | 121.8796 | -61.7111 | 59.8251 | 0.002213 | -0.024745 | 0.00071361 | 0.056227 | -0.0042369 | 0.052888 | -0.019381 | -0.0011537 | -0.001017 | -0.0030915 | 0.011656 | -0.0068945 | -59.1746 | -0.016908 | -61.7282 | 59.7268 | 59.531 | 59.3525 | -61.7183 | 0.083464 | 0.064461 | -61.8552 | 59.4767 | 59.5813 | 59.7036 | -61.6943 | -0.007155 | -0.098299 | 2.5365 | -0.017088 | -0.009933 | -0.29418 | -0.47268 | 0.016827 | -0.34839 | 61.7946 | -0.14408 | -0.1609 | -0.24381 | -0.12156 | 121.438 | 121.2421 | 121.0636 | 61.6942 | -121.5434 | 121.1879 | 121.2924 | 121.4147 | 61.7756 | -121.5194
14.0312 | 121.7514 | -61.7294 | 59.8709 | 0.002213 | -0.024318 | 0.00092741 | 0.05644 | -0.0042369 | 0.053102 | -0.0041205 | -0.0011537 | -0.00080338 | -0.0028779 | 0.012083 | -0.0071083 | -59.1014 | -0.016908 | -61.7282 | 59.7268 | 59.531 | 59.357 | -61.7229 | 0.078886 | 0.055303 | -61.8552 | 59.4813 | 59.5722 | 59.7036 | -61.708 | 0.006576 | -0.14408 | 2.6281 | 0.001222 | -0.005354 | -0.33995 | -0.51388 | 0.0214 | -0.38958 | 61.8083 | -0.12577 | -0.14717 | -0.29874 | -0.16734 | 121.4563 | 121.2604 | 121.0865 | 61.7125 | -121.5938 | 121.2108 | 121.3016 | 121.433 | 61.7847 | -121.5789
15.7812 | 121.8338 | -61.734 | 59.7977 | 0.002213 | -0.024745 | 0.00092741 | 0.05644 | -0.0042369 | 0.052674 | -0.0041205 | -0.00094006 | -0.0014444 | -0.0030915 | 0.011869 | -0.0068945 | -59.1288 | -0.021486 | -61.7282 | 59.7314 | 59.5264 | 59.3525 | -61.7183 | 0.069728 | 0.059882 | -61.8506 | 59.4905 | 59.5722 | 59.7081 | -61.6989 | 0.015733 | -0.066255 | 2.6052 | 0.0058 | -0.009933 | -0.27129 | -0.44521 | 0.035136 | -0.30719 | 61.8037 | -0.11661 | -0.15175 | -0.2255 | -0.089519 | 121.4654 | 121.2604 | 121.0865 | 61.7125 | -121.5159 | 121.2245 | 121.3062 | 121.4422 | 61.7939 | -121.4965
17.4688 | 121.7468 | -61.8347 | 59.7519 | -0.005418 | -0.024745 | 0.001141 | 0.05644 | -0.0040233 | 0.052674 | -0.019381 | -0.00072626 | -0.001017 | -0.0030915 | 0.012083 | -0.0068945 | -59.051 | -0.021486 | -61.7328 | 59.7314 | 59.5264 | 59.3479 | -61.7274 | 0.074307 | 0.059882 | -61.8552 | 59.4859 | 59.5767 | 59.7036 | -61.7035 | 0.10728 | -0.020479 | 2.7837 | 0.10193 | -0.005354 | -0.22551 | -0.40402 | 0.13126 | -0.26599 | 61.909 | -0.020481 | -0.15175 | -0.17515 | -0.048322 | 121.5661 | 121.3611 | 121.1826 | 61.8132 | -121.4793 | 121.3206 | 121.4115 | 121.5383 | 61.8946 | -121.4553
19.2188 | 121.875 | -61.6699 | 59.8526 | 0.017475 | -0.024532 | 0.00092741 | 0.056227 | -0.0038097 | 0.052888 | -0.0041205 | -0.0013673 | -0.001017 | -0.0030915 | 0.011869 | -0.0071083 | -59.1746 | -0.016908 | -61.7282 | 59.7314 | 59.5218 | 59.3479 | -61.7229 | 0.083464 | 0.055303 | -61.8644 | 59.4905 | 59.5813 | 59.7036 | -61.6943 | -0.052933 | -0.12119 | 2.4953 | -0.058287 | -0.005354 | -0.3308 | -0.50473 | -0.024372 | -0.36212 | 61.7534 | -0.19443 | -0.17006 | -0.27128 | -0.14903 | 121.4013 | 121.1917 | 121.0178 | 61.653 | -121.5755 | 121.1604 | 121.2512 | 121.3735 | 61.7252 | -121.5469
20.8906 | 121.7697 | -61.821 | 59.7427 | 0.002213 | -0.024745 | 0.00092741 | 0.056654 | -0.0042369 | 0.053102 | 0.01114 | -0.00094006 | -0.001017 | -0.0033051 | 0.011869 | -0.0068945 | -59.051 | -0.016908 | -61.7282 | 59.7314 | 59.5264 | 59.3479 | -61.7229 | 0.078886 | 0.064461 | -61.8506 | 59.4813 | 59.5859 | 59.7036 | -61.6897 | 0.098129 | -0.011324 | 2.77 | 0.092775 | -0.005354 | -0.21636 | -0.39486 | 0.13127 | -0.26141 | 61.8999 | -0.029635 | -0.1609 | -0.15683 | -0.039167 | 121.5524 | 121.3474 | 121.1689 | 61.8041 | -121.4656 | 121.3023 | 121.4069 | 121.5246 | 61.8854 | -121.4325
22.6406 | 121.756 | -61.8439 | 59.7565 | -0.005418 | -0.024104 | 0.00092741 | 0.05644 | -0.0040233 | 0.053102 | -0.0041205 | -0.00094006 | -0.0012306 | -0.0030915 | 0.011442 | -0.0071083 | -59.0602 | -0.016908 | -61.7328 | 59.7406 | 59.531 | 59.3525 | -61.7274 | 0.074307 | 0.059882 | -61.8552 | 59.4813 | 59.5859 | 59.7081 | -61.6943 | 0.11644 | -0.0159 | 2.7837 | 0.11108 | -0.005354 | -0.22551 | -0.40402 | 0.14958 | -0.27514 | 61.9182 | -0.011326 | -0.1609 | -0.17057 | -0.048321 | 121.5844 | 121.3748 | 121.1963 | 61.827 | -121.4839 | 121.3252 | 121.4298 | 121.552 | 61.9038 | -121.4508
24.3906 | 121.8475 | -61.6608 | 59.8434 | -0.005418 | -0.024532 | 0.00050001 | 0.056227 | -0.0042369 | 0.052674 | 0.00351 | -0.00072626 | -0.001017 | -0.0028779 | 0.012083 | -0.0071083 | -59.1426 | -0.021486 | -61.7282 | 59.7314 | 59.5218 | 59.3479 | -61.7274 | 0.074307 | 0.059882 | -61.8552 | 59.4813 | 59.5813 | 59.7081 | -61.6943 | -0.066667 | -0.11203 | 2.5182 | -0.067442 | -0.000775 | -0.32165 | -0.49557 | -0.033527 | -0.36212 | 61.7351 | -0.19443 | -0.1609 | -0.26212 | -0.1353 | 121.3922 | 121.1826 | 121.0086 | 61.6393 | -121.5709 | 121.1421 | 121.2421 | 121.3689 | 61.7206 | -121.5377
26.0625 | 121.8475 | -61.6882 | 59.8434 | -0.005418 | -0.024532 | 0.00071361 | 0.056227 | -0.0042369 | 0.053315 | -0.0041205 | -0.00094006 | -0.001017 | -0.0030915 | 0.011869 | -0.0071083 | -59.1426 | -0.016908 | -61.7236 | 59.736 | 59.5355 | 59.3479 | -61.7274 | 0.078886 | 0.064461 | -61.8506 | 59.4859 | 59.5767 | 59.7036 | -61.6943 | -0.039202 | -0.10745 | 2.5457 | -0.035399 | 0.003803 | -0.30791 | -0.49557 | -0.006062 | -0.35754 | 61.7671 | -0.16239 | -0.15633 | -0.2667 | -0.13988 | 121.4242 | 121.2238 | 121.0361 | 61.6713 | -121.5709 | 121.1741 | 121.265 | 121.3918 | 61.7527 | -121.5377
27.8125 | 121.875 | -61.7569 | 59.7336 | 0.002213 | -0.024532 | 0.001141 | 0.056227 | -0.0040233 | 0.052888 | -0.019381 | -0.00094006 | -0.001017 | -0.0033051 | 0.012083 | -0.0068945 | -59.1105 | -0.012329 | -61.7191 | 59.7314 | 59.5264 | 59.3433 | -61.7183 | 0.074307 | 0.064461 | -61.8506 | 59.4813 | 59.5813 | 59.7127 | -61.6943 | 0.038621 | -0.002169 | 2.6464 | 0.037844 | -0.000777 | -0.2072 | -0.39028 | 0.062603 | -0.25226 | 61.8312 | -0.093722 | -0.15633 | -0.15226 | -0.020855 | 121.4883 | 121.2833 | 121.1002 | 61.7446 | -121.4519 | 121.2382 | 121.3382 | 121.4696 | 61.8214 | -121.4279
29.5625 | 121.8384 | -61.7432 | 59.7427 | -0.013049 | -0.024532 | 0.00092741 | 0.05644 | -0.0042369 | 0.052888 | -0.0041205 | -0.00094006 | -0.0014444 | -0.0028779 | 0.011656 | -0.0068945 | -59.1105 | -0.021486 | -61.7282 | 59.736 | 59.5264 | 59.3525 | -61.7183 | 0.083464 | 0.050725 | -61.8552 | 59.4813 | 59.5767 | 59.7081 | -61.6943 | 0.024888 | -0.006745 | 2.6326 | 0.014955 | -0.009933 | -0.21636 | -0.39028 | 0.04887 | -0.26141 | 61.8266 | -0.11203 | -0.1609 | -0.16599 | -0.034588 | 121.4792 | 121.2695 | 121.0956 | 61.7217 | -121.461 | 121.2245 | 121.3199 | 121.4513 | 61.7939 | -121.437
31.25 | 121.8887 | -61.6653 | 59.8526 | 0.002213 | -0.024318 | 0.00092741 | 0.05644 | -0.0040233 | 0.052888 | -0.011751 | -0.0011537 | -0.001017 | -0.0030915 | 0.012297 | -0.0066809 | -59.1746 | -0.026065 | -61.7282 | 59.736 | 59.5264 | 59.3479 | -61.7274 | 0.074307 | 0.059882 | -61.8552 | 59.4813 | 59.5676 | 59.699 | -61.6989 | -0.06209 | -0.11661 | 2.4907 | -0.062865 | -0.000775 | -0.32622 | -0.50473 | -0.033529 | -0.37127 | 61.7397 | -0.18985 | -0.15633 | -0.28501 | -0.15361 | 121.4013 | 121.1917 | 121.0132 | 61.6393 | -121.58 | 121.1467 | 121.2329 | 121.3643 | 61.7252 | -121.5515
33 | 121.788 | -61.8256 | 59.7061 | -0.013049 | -0.024959 | 0.00050001 | 0.05644 | -0.0038097 | 0.052888 | 0.00351 | -0.0011537 | -0.00080338 | -0.0030915 | 0.012083 | -0.0068945 | -59.0693 | -0.012329 | -61.7236 | 59.7406 | 59.5264 | 59.3479 | -61.7229 | 0.078886 | 0.06904 | -61.8552 | 59.4767 | 59.5722 | 59.7127 | -61.6897 | 0.10271 | 0.034454 | 2.7562 | 0.10193 | -0.000776 | -0.17974 | -0.35824 | 0.13585 | -0.22937 | 61.9044 | -0.029636 | -0.16548 | -0.13395 | 0.006611 | 121.5661 | 121.3519 | 121.1734 | 61.8132 | -121.429 | 121.3023 | 121.3977 | 121.5383 | 61.8946 | -121.3958
34.6719 | 121.7697 | -61.6974 | 59.8755 | -0.013049 | -0.024959 | 0.001141 | 0.056654 | -0.0042369 | 0.052888 | -0.0041205 | -0.0011537 | -0.0014444 | -0.0033051 | 0.011869 | -0.0071083 | -59.1288 | -0.016908 | -61.7191 | 59.736 | 59.5264 | 59.3433 | -61.7183 | 0.074307 | 0.050725 | -61.8506 | 59.4859 | 59.5676 | 59.699 | -61.6897 | -0.020888 | -0.1395 | 2.5686 | -0.021665 | -0.000777 | -0.34911 | -0.53219 | 0.007673 | -0.38958 | 61.7717 | -0.15323 | -0.1609 | -0.3079 | -0.1765 | 121.4334 | 121.2238 | 121.0407 | 61.6805 | -121.5938 | 121.1833 | 121.265 | 121.3964 | 61.7481 | -121.5652
36.4219 | 121.7377 | -61.7111 | 59.8755 | -0.005418 | -0.024959 | 0.00092741 | 0.056654 | -0.0044507 | 0.052674 | -0.0041205 | -0.0011537 | -0.0012306 | -0.0030915 | 0.011869 | -0.0071083 | -59.083 | -0.026065 | -61.7191 | 59.7177 | 59.5264 | 59.3433 | -61.7229 | 0.074307 | 0.059882 | -61.8506 | 59.4767 | 59.5676 | 59.7036 | -61.6989 | -0.011734 | -0.15781 | 2.6281 | -0.007932 | 0.003802 | -0.34911 | -0.53219 | 0.012248 | -0.39874 | 61.7854 | -0.1395 | -0.15175 | -0.3079 | -0.17192 | 121.4288 | 121.2375 | 121.0544 | 61.6851 | -121.5983 | 121.1879 | 121.2787 | 121.4147 | 61.771 | -121.5744
38.1719 | 121.8658 | -61.6745 | 59.8389 | 0.009844 | -0.024532 | 0.001141 | 0.05644 | -0.0040233 | 0.052888 | -0.0041205 | -0.00072626 | -0.0012306 | -0.0028779 | 0.012083 | -0.0066809 | -59.1517 | -0.016908 | -61.7145 | 59.7314 | 59.5218 | 59.357 | -61.7137 | 0.06515 | 0.050725 | -61.8552 | 59.4722 | 59.5676 | 59.7081 | -61.6897 | -0.039197 | -0.10745 | 2.5228 | -0.039974 | -0.000777 | -0.31707 | -0.48184 | -0.015215 | -0.3667 | 61.7397 | -0.1807 | -0.16548 | -0.27128 | -0.13072 | 121.4059 | 121.1963 | 121.0315 | 61.6576 | -121.5526 | 121.1467 | 121.2421 | 121.3826 | 61.7252 | -121.5286
39.9062 | 121.7514 | -61.7477 | 59.8389 | 0.002213 | -0.024532 | 0.00092741 | 0.056227 | -0.0040233 | 0.052888 | -0.0041205 | -0.00094006 | -0.0014444 | -0.0030915 | 0.012511 | -0.0071083 | -59.0739 | -0.021486 | -61.7236 | 59.736 | 59.5264 | 59.3433 | -61.7229 | 0.074307 | 0.055303 | -61.846 | 59.4813 | 59.5722 | 59.7036 | -61.6851 | 0.024887 | -0.10287 | 2.6739 | 0.024111 | -0.000776 | -0.31249 | -0.49557 | 0.062605 | -0.35754 | 61.822 | -0.098299 | -0.1609 | -0.2667 | -0.1353 | 121.4837 | 121.2741 | 121.091 | 61.7263 | -121.5617 | 121.2291 | 121.3199 | 121.4513 | 61.803 | -121.524
41.5938 | 121.8292 | -61.7386 | 59.761 | -0.005418 | -0.024745 | 0.001141 | 0.05644 | -0.0040233 | 0.052888 | -0.019381 | -0.0011537 | -0.001658 | -0.0033051 | 0.011869 | -0.0068945 | -59.1197 | -0.016908 | -61.7191 | 59.7314 | 59.531 | 59.3525 | -61.7229 | 0.083464 | 0.050725 | -61.8506 | 59.4767 | 59.5722 | 59.7081 | -61.6897 | 0.015731 | -0.029634 | 2.6189 | 0.019533 | 0.003802 | -0.23009 | -0.40859 | 0.048871 | -0.2843 | 61.822 | -0.11203 | -0.1609 | -0.18888 | -0.052898 | 121.47 | 121.2695 | 121.091 | 61.7217 | -121.4839 | 121.2153 | 121.3108 | 121.4467 | 61.7893 | -121.4508
43.3438 | 121.7789 | -61.7844 | 59.7794 | -0.005418 | -0.024959 | 0.00071361 | 0.05644 | -0.0042369 | 0.052888 | -0.011751 | -0.0013673 | -0.0012306 | -0.0030915 | 0.012297 | -0.0068945 | -59.0556 | -0.016908 | -61.7191 | 59.7314 | 59.5218 | 59.3433 | -61.7229 | 0.083464 | 0.055303 | -61.846 | 59.4813 | 59.5722 | 59.699 | -61.6943 | 0.061508 | -0.047945 | 2.7288 | 0.06531 | 0.003802 | -0.25756 | -0.43606 | 0.090069 | -0.29803 | 61.8678 | -0.061678 | -0.15175 | -0.20719 | -0.080366 | 121.5158 | 121.3062 | 121.1277 | 61.7675 | -121.5022 | 121.2657 | 121.3565 | 121.4834 | 61.8397 | -121.4737
45.0781 | 121.7239 | -61.8256 | 59.7519 | -0.005418 | -0.024959 | 0.00092741 | 0.056654 | -0.0040233 | 0.052888 | -0.011751 | -0.0011537 | -0.001017 | -0.0030915 | 0.012297 | -0.0068945 | -59.051 | -0.021486 | -61.7191 | 59.7314 | 59.5218 | 59.3479 | -61.7091 | 0.074307 | 0.059882 | -61.8506 | 59.4813 | 59.5722 | 59.7036 | -61.6943 | 0.11644 | -0.020479 | 2.7746 | 0.10651 | -0.009935 | -0.23009 | -0.40402 | 0.13127 | -0.27057 | 61.8999 | -0.025057 | -0.15633 | -0.17972 | -0.048322 | 121.557 | 121.3474 | 121.1734 | 61.8041 | -121.461 | 121.3069 | 121.3977 | 121.5291 | 61.8854 | -121.4462
46.75 | 121.8201 | -61.7477 | 59.7839 | -0.013049 | -0.024745 | 0.001141 | 0.056227 | -0.0042369 | 0.052674 | -0.011751 | -0.00094006 | -0.001017 | -0.0033051 | 0.011869 | -0.0071083 | -59.1197 | -0.016908 | -61.7191 | 59.7268 | 59.531 | 59.357 | -61.7137 | 0.078886 | 0.059882 | -61.846 | 59.4767 | 59.5813 | 59.699 | -61.6897 | 0.034045 | -0.057101 | 2.6281 | 0.028689 | -0.005356 | -0.25298 | -0.4269 | 0.058027 | -0.30719 | 61.8266 | -0.098299 | -0.15633 | -0.20261 | -0.084944 | 121.4746 | 121.2787 | 121.1048 | 61.7308 | -121.4976 | 121.2245 | 121.3291 | 121.4467 | 61.8076 | -121.4737
48.5 | 121.7514 | -61.8164 | 59.7336 | -0.005418 | -0.024745 | 0.0013548 | 0.056227 | -0.0046643 | 0.052461 | -0.0041205 | -0.00094006 | -0.0014444 | -0.0030915 | 0.012083 | -0.0071083 | -59.051 | -0.016908 | -61.7236 | 59.736 | 59.5264 | 59.3433 | -61.7137 | 0.078886 | 0.059882 | -61.846 | 59.4813 | 59.5722 | 59.7081 | -61.6989 | 0.10271 | 0.00241 | 2.7654 | 0.092775 | -0.009934 | -0.2072 | -0.39028 | 0.11753 | -0.25226 | 61.8953 | -0.029635 | -0.14717 | -0.16141 | -0.025433 | 121.5524 | 121.3428 | 121.1597 | 61.7995 | -121.4473 | 121.2977 | 121.3886 | 121.5246 | 61.8763 | -121.4325
50.2344 | 121.875 | -61.7752 | 59.7153 | -0.02068 | -0.024745 | 0.00071361 | 0.056654 | -0.0040233 | 0.052888 | -0.011751 | -0.0011537 | -0.001017 | -0.0030915 | 0.012297 | -0.0073219 | -59.0968 | -0.021486 | -61.7145 | 59.736 | 59.531 | 59.3525 | -61.7229 | 0.078886 | 0.059882 | -61.846 | 59.4813 | 59.5722 | 59.7036 | -61.6943 | 0.052353 | 0.020721 | 2.6784 | 0.060734 | 0.008381 | -0.18431 | -0.36282 | 0.080914 | -0.23394 | 61.8541 | -0.070833 | -0.15175 | -0.1431 | -0.011701 | 121.5112 | 121.3062 | 121.1277 | 61.7537 | -121.4381 | 121.2565 | 121.3474 | 121.4788 | 61.8351 | -121.4096
51.9844 | 121.7606 | -61.6928 | 59.8526 | 0.002213 | -0.024959 | 0.00092741 | 0.056013 | -0.0042369 | 0.053102 | 0.01114 | -0.00094006 | -0.0012306 | -0.0028779 | 0.012297 | -0.0075355 | -59.1197 | -0.021486 | -61.7236 | 59.7314 | 59.5172 | 59.3479 | -61.7274 | 0.074307 | 0.055303 | -61.846 | 59.4767 | 59.5722 | 59.7036 | -61.6851 | -0.034624 | -0.12119 | 2.5731 | -0.030821 | 0.003803 | -0.33538 | -0.50473 | 0.007673 | -0.37585 | 61.7671 | -0.15323 | -0.1609 | -0.28043 | -0.14903 | 121.4242 | 121.21 | 121.0407 | 61.6713 | -121.58 | 121.1696 | 121.265 | 121.3964 | 61.7481 | -121.5377
53.6875 | 121.7468 | -61.7065 | 59.8892 | 0.009844 | -0.025173 | 0.00092741 | 0.056227 | -0.0042369 | 0.052461 | 0.01114 | -0.00072626 | -0.001017 | -0.0028779 | 0.012297 | -0.0071083 | -59.1059 | -0.021486 | -61.7236 | 59.736 | 59.5218 | 59.3525 | -61.7229 | 0.078886 | 0.059882 | -61.8552 | 59.4722 | 59.5722 | 59.7127 | -61.6989 | -0.016312 | -0.15323 | 2.6006 | -0.017088 | -0.000776 | -0.36742 | -0.53677 | 0.00767 | -0.41705 | 61.7854 | -0.14865 | -0.15633 | -0.31705 | -0.17649 | 121.4425 | 121.2283 | 121.059 | 61.6851 | -121.6121 | 121.1787 | 121.2787 | 121.4193 | 61.7664 | -121.5881
55.4531 | 121.8613 | -61.7706 | 59.6924 | 0.002213 | -0.024959 | 0.00092741 | 0.05644 | -0.0044507 | 0.052674 | -0.011751 | -0.00094006 | -0.0014444 | -0.0030915 | 0.012297 | -0.0073219 | -59.0739 | -0.021486 | -61.7236 | 59.7314 | 59.5264 | 59.3479 | -61.7183 | 0.078886 | 0.06904 | -61.846 | 59.4722 | 59.5767 | 59.7036 | -61.6851 | 0.052354 | 0.03903 | 2.6967 | 0.046999 | -0.005355 | -0.166 | -0.34451 | 0.085493 | -0.22021 | 61.8495 | -0.075411 | -0.1609 | -0.11564 | 0.011187 | 121.502 | 121.297 | 121.1185 | 61.7491 | -121.4107 | 121.2428 | 121.3474 | 121.4742 | 61.8397 | -121.3775
57.1406 | 121.7834 | -61.7477 | 59.8022 | -0.013049 | -0.025173 | 0.00071361 | 0.056013 | -0.0042369 | 0.052674 | -0.011751 | -0.0013673 | -0.001017 | -0.0030915 | 0.011656 | -0.0073219 | -59.0647 | -0.016908 | -61.7145 | 59.7268 | 59.5264 | 59.3525 | -61.7137 | 0.069728 | 0.055303 | -61.8552 | 59.4767 | 59.5722 | 59.7036 | -61.6943 | 0.034045 | -0.075411 | 2.683 | 0.033268 | -0.000777 | -0.27587 | -0.44979 | 0.053448 | -0.3255 | 61.8175 | -0.10746 | -0.1609 | -0.23008 | -0.098676 | 121.4746 | 121.2741 | 121.1002 | 61.7308 | -121.5159 | 121.2245 | 121.3199 | 121.4513 | 61.803 | -121.4965
58.8906 | 121.7972 | -61.6928 | 59.8709 | 0.002213 | -0.024959 | 0.00092741 | 0.056227 | -0.0038097 | 0.052674 | 0.00351 | -0.00094006 | -0.0012306 | -0.0035187 | 0.012297 | -0.0071083 | -59.138 | -0.016908 | -61.7191 | 59.7314 | 59.5264 | 59.3525 | -61.7274 | 0.074307 | 0.055303 | -61.8552 | 59.4767 | 59.5676 | 59.7036 | -61.6943 | -0.034624 | -0.1395 | 2.5548 | -0.026243 | 0.008381 | -0.34453 | -0.51846 | -0.001484 | -0.39416 | 61.7671 | -0.16239 | -0.1609 | -0.30332 | -0.16734 | 121.4242 | 121.2192 | 121.0453 | 61.6759 | -121.5983 | 121.1696 | 121.2604 | 121.3964 | 61.7481 | -121.5652
60.625 | 121.843 | -61.6791 | 59.8343 | 0.009844 | -0.025173 | 0.00092741 | 0.05644 | -0.0042369 | 0.052888 | -0.011751 | -0.00094006 | -0.0014444 | -0.0030915 | 0.012297 | -0.0073219 | -59.1563 | -0.026065 | -61.7236 | 59.7314 | 59.5264 | 59.3433 | -61.7229 | 0.06515 | 0.059882 | -61.8506 | 59.4767 | 59.5767 | 59.7036 | -61.6897 | -0.043778 | -0.10288 | 2.5228 | -0.044554 | -0.000776 | -0.30791 | -0.49099 | -0.010638 | -0.35754 | 61.7442 | -0.17154 | -0.1609 | -0.25754 | -0.13072 | 121.4105 | 121.2055 | 121.0224 | 61.653 | -121.5571 | 121.1558 | 121.2558 | 121.3826 | 61.739 | -121.524
62.3594 | 121.7377 | -61.702 | 59.8801 | 0.002213 | -0.025173 | 0.00092741 | 0.056227 | -0.0042369 | 0.052247 | -0.011751 | -0.00094006 | -0.001017 | -0.0026641 | 0.012083 | -0.0073219 | -59.1151 | -0.016908 | -61.7191 | 59.7268 | 59.5264 | 59.3433 | -61.7229 | 0.074307 | 0.055303 | -61.846 | 59.4813 | 59.5722 | 59.7036 | -61.6943 | -0.02089 | -0.15323 | 2.5869 | -0.017088 | 0.003802 | -0.35369 | -0.53677 | 0.007671 | -0.39874 | 61.7763 | -0.14408 | -0.15175 | -0.3079 | -0.1765 | 121.4288 | 121.2283 | 121.0453 | 61.6851 | -121.6029 | 121.1833 | 121.2741 | 121.4055 | 61.7573 | -121.5744
64.1094 | 121.843 | -61.7798 | 59.6924 | -0.013049 | -0.025173 | 0.00092741 | 0.056227 | -0.0040233 | 0.052888 | -0.0041205 | -0.0011537 | -0.001017 | -0.0030915 | 0.012297 | -0.0073219 | -59.083 | -0.021486 | -61.7145 | 59.7268 | 59.5218 | 59.3525 | -61.7183 | 0.078886 | 0.059882 | -61.8415 | 59.4813 | 59.5722 | 59.7036 | -61.6943 | 0.061509 | 0.034452 | 2.6967 | 0.065311 | 0.003802 | -0.17058 | -0.33993 | 0.085491 | -0.21106 | 61.8587 | -0.061677 | -0.14717 | -0.12022 | 0.011187 | 121.5066 | 121.3016 | 121.1322 | 61.7583 | -121.4107 | 121.2611 | 121.352 | 121.4834 | 61.8397 | -121.3867
65.7969 | 121.8063 | -61.7203 | 59.8068 | -0.005418 | -0.025387 | 0.00071361 | 0.05644 | -0.0044507 | 0.053102 | -0.011751 | -0.00094006 | -0.0012306 | -0.0033051 | 0.012297 | -0.0075355 | -59.138 | -0.026065 | -61.7145 | 59.7268 | 59.5172 | 59.3479 | -61.7137 | 0.074307 | 0.06904 | -61.8506 | 59.4813 | 59.5722 | 59.699 | -61.6897 | 0.006579 | -0.079989 | 2.5823 | 0.005802 | -0.000777 | -0.2896 | -0.45895 | 0.030561 | -0.3255 | 61.7946 | -0.13034 | -0.1609 | -0.23466 | -0.10783 | 121.4471 | 121.2375 | 121.0682 | 61.6942 | -121.5205 | 121.2016 | 121.2924 | 121.4193 | 61.7893 | -121.4965
67.5469 | 121.7102 | -61.821 | 59.7427 | 0.002213 | -0.024959 | 0.00092741 | 0.05644 | -0.0042369 | 0.052674 | 0.00351 | -0.0011537 | -0.001017 | -0.0028779 | 0.012083 | -0.0073219 | -59.051 | -0.021486 | -61.7145 | 59.7314 | 59.5218 | 59.3433 | -61.7183 | 0.083464 | 0.059882 | -61.846 | 59.4767 | 59.5676 | 59.7036 | -61.6897 | 0.10271 | -0.011324 | 2.77 | 0.10651 | 0.003802 | -0.22094 | -0.39944 | 0.13127 | -0.26599 | 61.9044 | -0.025057 | -0.15633 | -0.17515 | -0.039167 | 121.5524 | 121.3428 | 121.1643 | 61.7995 | -121.461 | 121.2977 | 121.3886 | 121.5246 | 61.8809 | -121.4325
69.2969 | 121.8109 | -61.6974 | 59.7931 | -0.005418 | -0.025173 | 0.001141 | 0.05644 | -0.0038097 | 0.052247 | -0.0041205 | -0.0011537 | -0.0012306 | -0.0030915 | 0.012083 | -0.0068945 | -59.1197 | -0.016908 | -61.7236 | 59.736 | 59.5218 | 59.3387 | -61.7137 | 0.074307 | 0.055303 | -61.8415 | 59.4767 | 59.5722 | 59.7036 | -61.6897 | -0.016309 | -0.057099 | 2.5777 | -0.026243 | -0.009934 | -0.27129 | -0.45437 | 0.007673 | -0.31634 | 61.7717 | -0.14407 | -0.15175 | -0.22092 | -0.089521 | 121.4334 | 121.2192 | 121.0361 | 61.6805 | -121.5068 | 121.1741 | 121.2696 | 121.401 | 61.7527 | -121.4828
71.0469 | 121.8475 | -61.6653 | 59.8389 | 0.009844 | -0.024959 | 0.00071361 | 0.056227 | -0.0042369 | 0.052674 | 0.01114 | -0.00094006 | -0.001017 | -0.0033051 | 0.011869 | -0.0075355 | -59.1563 | -0.021486 | -61.7145 | 59.7268 | 59.5264 | 59.3525 | -61.7229 | 0.074307 | 0.064461 | -61.8552 | 59.4767 | 59.5813 | 59.699 | -61.6897 | -0.057511 | -0.11203 | 2.509 | -0.04913 | 0.008381 | -0.31249 | -0.48641 | -0.024371 | -0.36212 | 61.7397 | -0.18985 | -0.16548 | -0.25754 | -0.13988 | 121.3922 | 121.1917 | 121.0178 | 61.6439 | -121.5617 | 121.1421 | 121.2467 | 121.3643 | 61.7298 | -121.5286
72.7188 | 121.7239 | -61.7203 | 59.8572 | 0.009844 | -0.025387 | 0.001141 | 0.056227 | -0.0040233 | 0.052674 | 0.00351 | -0.00072626 | -0.001017 | -0.0033051 | 0.012297 | -0.0073219 | -59.0922 | -0.016908 | -61.7191 | 59.7268 | 59.5264 | 59.3525 | -61.7137 | 0.078886 | 0.059882 | -61.846 | 59.4722 | 59.5767 | 59.6898 | -61.6989 | 0.006579 | -0.13034 | 2.6281 | 0.001223 | -0.005356 | -0.3308 | -0.50472 | 0.021403 | -0.38501 | 61.7992 | -0.12577 | -0.14717 | -0.28043 | -0.16734 | 121.4471 | 121.2467 | 121.0727 | 61.7034 | -121.5709 | 121.1924 | 121.297 | 121.4101 | 61.7802 | -121.5561
74.4688 | 121.7056 | -61.8347 | 59.761 | -0.005418 | -0.025173 | 0.00092741 | 0.056227 | -0.0044507 | 0.052461 | 0.00351 | -0.0011537 | -0.0012306 | -0.0030915 | 0.012511 | -0.0071083 | -59.0418 | -0.021486 | -61.7145 | 59.7314 | 59.531 | 59.3525 | -61.7137 | 0.078886 | 0.059882 | -61.8415 | 59.4722 | 59.5767 | 59.7081 | -61.6897 | 0.12102 | -0.029634 | 2.7929 | 0.12024 | -0.000777 | -0.23009 | -0.40859 | 0.145 | -0.28888 | 61.9136 | -0.006745 | -0.15175 | -0.1843 | -0.052898 | 121.5661 | 121.3657 | 121.1872 | 61.8132 | -121.4747 | 121.3069 | 121.4115 | 121.5429 | 61.8946 | -121.4508
76.2031 | 121.8246 | -61.734 | 59.7565 | 0.002213 | -0.025387 | 0.001141 | 0.05644 | -0.0040233 | 0.052674 | -0.0041205 | -0.0015809 | -0.001017 | -0.0033051 | 0.012511 | -0.0073219 | -59.1151 | -0.016908 | -61.7099 | 59.7314 | 59.5218 | 59.357 | -61.7183 | 0.074307 | 0.055303 | -61.8506 | 59.4813 | 59.5813 | 59.699 | -61.6943 | 0.015733 | -0.025057 | 2.6189 | 0.024113 | 0.00838 | -0.23467 | -0.39944 | 0.039715 | -0.27514 | 61.8083 | -0.11661 | -0.15633 | -0.17515 | -0.057478 | 121.4654 | 121.2558 | 121.091 | 61.7171 | -121.4747 | 121.2153 | 121.3153 | 121.433 | 61.7893 | -121.4508
77.9688 | 121.8796 | -61.6562 | 59.8206 | -0.013049 | -0.025173 | 0.00092741 | 0.05644 | -0.0042369 | 0.052461 | -0.0041205 | -0.0013673 | -0.0014444 | -0.0030915 | 0.012511 | -0.0071083 | -59.1655 | -0.026065 | -61.7099 | 59.7314 | 59.5218 | 59.3525 | -61.7137 | 0.069728 | 0.064461 | -61.846 | 59.4767 | 59.5813 | 59.7036 | -61.6943 | -0.057508 | -0.089144 | 2.4907 | -0.053707 | 0.003801 | -0.29876 | -0.4681 | -0.038105 | -0.34381 | 61.7259 | -0.18985 | -0.15175 | -0.23923 | -0.11699 | 121.3876 | 121.178 | 121.0086 | 61.6301 | -121.5343 | 121.1329 | 121.2375 | 121.3598 | 61.7206 | -121.5149
79.6562 | 121.8155 | -61.7111 | 59.8206 | -0.005418 | -0.025173 | 0.00092741 | 0.056227 | -0.0042369 | 0.052888 | -0.0041205 | -0.0011537 | -0.0014444 | -0.0028779 | 0.012724 | -0.0068945 | -59.1334 | -0.021486 | -61.7099 | 59.7314 | 59.531 | 59.3479 | -61.7183 | 0.074307 | 0.059882 | -61.846 | 59.4767 | 59.5767 | 59.699 | -61.6989 | -0.007155 | -0.089144 | 2.5777 | 0.001225 | 0.00838 | -0.2896 | -0.47268 | 0.012248 | -0.34381 | 61.7854 | -0.13492 | -0.14717 | -0.24381 | -0.12157 | 121.4425 | 121.2421 | 121.059 | 61.6896 | -121.5388 | 121.1879 | 121.2879 | 121.4101 | 61.771 | -121.5194
81.3906 | 121.8201 | -61.7065 | 59.8206 | -0.005418 | -0.025387 | 0.00071361 | 0.056227 | -0.0040233 | 0.052247 | -0.019381 | -0.00094006 | -0.0014444 | -0.0030915 | 0.012297 | -0.0071083 | -59.1563 | -0.030644 | -61.7145 | 59.7314 | 59.5264 | 59.3525 | -61.7137 | 0.074307 | 0.064461 | -61.846 | 59.4767 | 59.5767 | 59.7036 | -61.6897 | -0.007154 | -0.089144 | 2.5502 | -0.007931 | -0.000777 | -0.29418 | -0.4681 | 0.016828 | -0.34381 | 61.7809 | -0.1395 | -0.15633 | -0.24381 | -0.11699 | 121.438 | 121.2329 | 121.059 | 61.6759 | -121.5343 | 121.1833 | 121.2833 | 121.4101 | 61.771 | -121.5103
83.1406 | 121.7285 | -61.8347 | 59.7382 | -0.005418 | -0.025173 | 0.00092741 | 0.05644 | -0.0042369 | 0.052888 | -0.0041205 | -0.0013673 | -0.0014444 | -0.0030915 | 0.012297 | -0.0071083 | -59.0647 | -0.021486 | -61.7145 | 59.7314 | 59.5264 | 59.3525 | -61.7137 | 0.074307 | 0.064461 | -61.846 | 59.4767 | 59.5813 | 59.7036 | -61.6943 | 0.12102 | -0.006746 | 2.77 | 0.12024 | -0.000777 | -0.21178 | -0.38571 | 0.14042 | -0.26141 | 61.909 | -0.011324 | -0.15175 | -0.15683 | -0.034589 | 121.5661 | 121.3611 | 121.1872 | 61.8132 | -121.4519 | 121.3115 | 121.416 | 121.5383 | 61.8992 | -121.4325
84.8906 | 121.7331 | -61.7203 | 59.848 | -0.005418 | -0.025173 | 0.00028641 | 0.05644 | -0.0040233 | 0.052674 | -0.011751 | -0.0011537 | -0.001017 | -0.0033051 | 0.012297 | -0.0075355 | -59.1151 | -0.026065 | -61.7191 | 59.7268 | 59.5218 | 59.357 | -61.7229 | 0.069728 | 0.055303 | -61.8506 | 59.4813 | 59.5767 | 59.699 | -61.6897 | -0.002579 | -0.12119 | 2.6052 | 0.001223 | 0.003802 | -0.32622 | -0.49099 | 0.030561 | -0.3667 | 61.79 | -0.13034 | -0.1609 | -0.27128 | -0.14903 | 121.4471 | 121.2421 | 121.0773 | 61.6942 | -121.5709 | 121.2016 | 121.297 | 121.4193 | 61.7756 | -121.5377
86.5781 | 121.8063 | -61.7432 | 59.761 | -0.02068 | -0.025173 | 0.00071361 | 0.05644 | -0.0042369 | 0.053102 | -0.0041205 | -0.00094006 | -0.0012306 | -0.0030915 | 0.012511 | -0.0066809 | -59.1197 | -0.021486 | -61.7191 | 59.7314 | 59.5218 | 59.3479 | -61.7183 | 0.069728 | 0.059882 | -61.846 | 59.4767 | 59.5813 | 59.7036 | -61.6897 | 0.024888 | -0.029634 | 2.6235 | 0.024111 | -0.000777 | -0.23925 | -0.41317 | 0.053449 | -0.2843 | 61.8129 | -0.10288 | -0.15633 | -0.17972 | -0.057477 | 121.4746 | 121.265 | 121.091 | 61.7217 | -121.4793 | 121.2199 | 121.3245 | 121.4467 | 61.803 | -121.4508
88.3281 | 121.7331 | -61.7432 | 59.8434 | -0.005418 | -0.025387 | 0.001141 | 0.056654 | -0.0040233 | 0.052888 | -0.0041205 | -0.0013673 | -0.0014444 | -0.0035187 | 0.012297 | -0.0075355 | -59.083 | -0.021486 | -61.7053 | 59.7268 | 59.5218 | 59.3525 | -61.7183 | 0.069728 | 0.064461 | -61.846 | 59.4722 | 59.5676 | 59.699 | -61.6851 | 0.024888 | -0.11661 | 2.6601 | 0.037846 | 0.012958 | -0.32165 | -0.49099 | 0.058027 | -0.37128 | 61.8129 | -0.10288 | -0.1609 | -0.27586 | -0.14445 | 121.47 | 121.265 | 121.0956 | 61.7217 | -121.5617 | 121.2153 | 121.3108 | 121.4422 | 61.8076 | -121.5286
90.0781 | 121.8704 | -61.7569 | 59.7061 | -0.005418 | -0.025173 | 0.00071361 | 0.056013 | -0.0040233 | 0.052674 | -0.011751 | -0.0013673 | -0.0012306 | -0.0028779 | 0.012297 | -0.0071083 | -59.1014 | -0.012329 | -61.7145 | 59.7223 | 59.5218 | 59.3479 | -61.7183 | 0.074307 | 0.064461 | -61.8506 | 59.4813 | 59.5722 | 59.6898 | -61.6851 | 0.038621 | 0.016141 | 2.6555 | 0.042423 | 0.003802 | -0.18432 | -0.35824 | 0.07176 | -0.22479 | 61.8312 | -0.093722 | -0.16548 | -0.13395 | -0.016282 | 121.4792 | 121.2787 | 121.1048 | 61.7446 | -121.4244 | 121.2382 | 121.3291 | 121.4467 | 61.8214 | -121.3913
91.75 | 121.843 | -61.6333 | 59.8343 | 0.002213 | -0.025387 | 0.00092741 | 0.056227 | -0.0040233 | 0.052461 | -0.0041205 | -0.00072626 | -0.001017 | -0.0028779 | 0.012297 | -0.0068945 | -59.1609 | -0.021486 | -61.7099 | 59.7268 | 59.5172 | 59.3479 | -61.7183 | 0.078886 | 0.059882 | -61.8415 | 59.4722 | 59.5767 | 59.699 | -61.6897 | -0.084975 | -0.10746 | 2.4724 | -0.076595 | 0.00838 | -0.31707 | -0.48642 | -0.056414 | -0.36212 | 61.7122 | -0.20816 | -0.15175 | -0.25754 | -0.1353 | 121.3601 | 121.1505 | 120.9812 | 61.6118 | -121.5526 | 121.1055 | 121.21 | 121.3323 | 61.6932 | -121.524
93.5 | 121.6965 | -61.8439 | 59.7336 | 0.002213 | -0.025173 | 0.00092741 | 0.056654 | -0.0042369 | 0.052888 | -0.011751 | -0.0013673 | -0.001017 | -0.0030915 | 0.012297 | -0.0071083 | -59.051 | -0.012329 | -61.7145 | 59.7223 | 59.5264 | 59.3525 | -61.7183 | 0.083464 | 0.064461 | -61.8323 | 59.4859 | 59.563 | 59.7036 | -61.6897 | 0.1256 | -0.011325 | 2.7929 | 0.1294 | 0.003802 | -0.2072 | -0.38113 | 0.15416 | -0.24768 | 61.9273 | 0.011568 | -0.14259 | -0.17057 | -0.030012 | 121.5661 | 121.3702 | 121.1963 | 61.8315 | -121.4519 | 121.3298 | 121.4069 | 121.5474 | 61.9083 | -121.4233
95.25 | 121.8613 | -61.6562 | 59.8434 | -0.013049 | -0.025387 | 0.00071361 | 0.05644 | -0.0042369 | 0.052888 | 0.00351 | -0.00094006 | -0.0014444 | -0.0033051 | 0.012511 | -0.0073219 | -59.1609 | -0.021486 | -61.7099 | 59.7314 | 59.5264 | 59.3479 | -61.7183 | 0.069728 | 0.059882 | -61.846 | 59.4813 | 59.5722 | 59.699 | -61.6897 | -0.062087 | -0.11203 | 2.4953 | -0.053707 | 0.00838 | -0.31707 | -0.49557 | -0.033526 | -0.36212 | 61.7259 | -0.18985 | -0.15633 | -0.27128 | -0.14445 | 121.3876 | 121.1826 | 121.0041 | 61.6347 | -121.5617 | 121.1375 | 121.2284 | 121.3552 | 61.7161 | -121.5332
97 | 121.7743 | -61.7569 | 59.8022 | 0.002213 | -0.025173 | 0.00092741 | 0.056227 | -0.0040233 | 0.052888 | -0.0041205 | -0.0011537 | -0.0012306 | -0.0033051 | 0.012297 | -0.0068945 | -59.0556 | -0.016908 | -61.7191 | 59.7223 | 59.5264 | 59.3525 | -61.7183 | 0.074307 | 0.050725 | -61.846 | 59.4767 | 59.5676 | 59.699 | -61.6897 | 0.038621 | -0.079989 | 2.7013 | 0.037844 | -0.000777 | -0.27587 | -0.44979 | 0.067182 | -0.3255 | 61.8312 | -0.089144 | -0.15633 | -0.23466 | -0.10325 | 121.4792 | 121.2833 | 121.1094 | 61.74 | -121.5205 | 121.2336 | 121.3245 | 121.4559 | 61.8076 | -121.492
98.75 | 121.8567 | -61.7844 | 59.7015 | 0.009844 | -0.025387 | 0.00071361 | 0.05644 | -0.0044507 | 0.052461 | -0.011751 | -0.0011537 | -0.0012306 | -0.0035187 | 0.012511 | -0.0066809 | -59.0876 | -0.016908 | -61.7145 | 59.736 | 59.531 | 59.3525 | -61.7137 | 0.078886 | 0.064461 | -61.8415 | 59.4767 | 59.5813 | 59.7036 | -61.6943 | 0.070666 | 0.034454 | 2.6967 | 0.069889 | -0.000777 | -0.17058 | -0.34908 | 0.090069 | -0.22479 | 61.8632 | -0.057099 | -0.14717 | -0.12021 | 0.002032 | 121.5204 | 121.3153 | 121.1368 | 61.7675 | -121.4152 | 121.2611 | 121.3657 | 121.4879 | 61.8488 | -121.3958
100.4531 | 121.875 | -61.6379 | 59.8343 | 0.002213 | -0.025387 | 0.00071361 | 0.056654 | -0.0040233 | 0.052674 | 0.00351 | -0.0011537 | -0.0012306 | -0.0033051 | 0.012511 | -0.0071083 | -59.17 | -0.021486 | -61.7099 | 59.7314 | 59.5218 | 59.3525 | -61.7137 | 0.069728 | 0.064461 | -61.8415 | 59.4722 | 59.5722 | 59.7036 | -61.6897 | -0.075819 | -0.10288 | 2.4678 | -0.072018 | 0.003801 | -0.31249 | -0.48184 | -0.051837 | -0.36212 | 61.7076 | -0.20358 | -0.15175 | -0.26212 | -0.13072 | 121.3693 | 121.1597 | 120.9903 | 61.6164 | -121.548 | 121.11 | 121.21 | 121.3414 | 61.7023 | -121.524
102.1875 | 121.7606 | -61.7569 | 59.7794 | 0.002213 | -0.025814 | 0.00050001 | 0.05644 | -0.0046643 | 0.052674 | 0.01114 | -0.0011537 | -0.0012306 | -0.0033051 | 0.012083 | -0.0071083 | -59.0602 | -0.012329 | -61.7191 | 59.7314 | 59.5172 | 59.3525 | -61.7137 | 0.074307 | 0.050725 | -61.8369 | 59.4767 | 59.563 | 59.699 | -61.6943 | 0.0432 | -0.047945 | 2.6967 | 0.037844 | -0.005356 | -0.26214 | -0.4269 | 0.062603 | -0.30261 | 61.8312 | -0.079986 | -0.14259 | -0.21635 | -0.080366 | 121.4883 | 121.2741 | 121.1094 | 61.7446 | -121.4931 | 121.2336 | 121.3199 | 121.4559 | 61.8076 | -121.4737
103.9375 | 121.7606 | -61.7889 | 59.7656 | 0.002213 | -0.025387 | 0.00092741 | 0.056227 | -0.0040233 | 0.052888 | -0.0041205 | -0.0011537 | -0.0012306 | -0.0030915 | 0.012297 | -0.0075355 | -59.0464 | -0.016908 | -61.7191 | 59.7314 | 59.5218 | 59.3433 | -61.7183 | 0.083464 | 0.064461 | -61.8415 | 59.4767 | 59.5676 | 59.6944 | -61.6897 | 0.070664 | -0.034212 | 2.7425 | 0.069887 | -0.000777 | -0.24383 | -0.42233 | 0.099225 | -0.28888 | 61.8724 | -0.052522 | -0.15175 | -0.19804 | -0.071212 | 121.5204 | 121.3107 | 121.1322 | 61.772 | -121.4839 | 121.2657 | 121.3565 | 121.4834 | 61.8534 | -121.4553
105.6875 | 121.7834 | -61.7844 | 59.7336 | -0.005418 | -0.025387 | 0.00092741 | 0.056654 | -0.0044507 | 0.052033 | -0.011751 | -0.00094006 | -0.0014444 | -0.0033051 | 0.012724 | -0.0071083 | -59.0693 | -0.016908 | -61.7145 | 59.7223 | 59.5355 | 59.3479 | -61.7137 | 0.074307 | 0.055303 | -61.8506 | 59.4767 | 59.5722 | 59.699 | -61.6897 | 0.070666 | -0.011325 | 2.715 | 0.069889 | -0.000777 | -0.19805 | -0.38571 | 0.094648 | -0.25683 | 61.8587 | -0.066256 | -0.1609 | -0.16141 | -0.03459 | 121.5066 | 121.3199 | 121.1322 | 61.7675 | -121.4473 | 121.2611 | 121.3565 | 121.4834 | 61.8397 | -121.4233
107.375 | 121.8292 | -61.6608 | 59.8343 | 0.009844 | -0.0256 | 0.00071361 | 0.056227 | -0.0042369 | 0.052247 | -0.0041205 | -0.0013673 | -0.001017 | -0.0035187 | 0.012297 | -0.0071083 | -59.1517 | -0.030644 | -61.7236 | 59.7314 | 59.5218 | 59.3525 | -61.7183 | 0.069728 | 0.055303 | -61.8415 | 59.4767 | 59.5722 | 59.699 | -61.6989 | -0.057509 | -0.10288 | 2.509 | -0.062864 | -0.005355 | -0.31249 | -0.48184 | -0.038106 | -0.35754 | 61.7305 | -0.1807 | -0.14259 | -0.26212 | -0.1353 | 121.3922 | 121.1826 | 121.0132 | 61.6301 | -121.5526 | 121.1375 | 121.2329 | 121.3598 | 61.7161 | -121.5332
109.125 | 121.7743 | -61.7477 | 59.7931 | 0.002213 | -0.0256 | 0.00092741 | 0.05644 | -0.0040233 | 0.052674 | -0.0041205 | -0.00094006 | -0.001658 | -0.0033051 | 0.012511 | -0.0073219 | -59.0647 | -0.021486 | -61.7099 | 59.736 | 59.5218 | 59.3479 | -61.7137 | 0.069728 | 0.059882 | -61.8369 | 59.4767 | 59.5676 | 59.7036 | -61.6897 | 0.034045 | -0.057099 | 2.683 | 0.037846 | 0.003801 | -0.27129 | -0.44522 | 0.058027 | -0.31634 | 61.8175 | -0.089141 | -0.14717 | -0.2255 | -0.089521 | 121.4837 | 121.2695 | 121.0956 | 61.7263 | -121.5068 | 121.2245 | 121.3153 | 121.4513 | 61.8076 | -121.4828
110.7969 | 121.8475 | -61.6241 | 59.8434 | 0.002213 | -0.025814 | 0.00092741 | 0.056227 | -0.0042369 | 0.052674 | -0.011751 | -0.00094006 | -0.0012306 | -0.0030915 | 0.012297 | -0.0071083 | -59.1746 | -0.021486 | -61.7236 | 59.7268 | 59.5172 | 59.3433 | -61.7137 | 0.078886 | 0.059882 | -61.846 | 59.4722 | 59.5584 | 59.699 | -61.6943 | -0.089551 | -0.11661 | 2.4495 | -0.099485 | -0.009934 | -0.32623 | -0.50015 | -0.070148 | -0.37128 | 61.703 | -0.22189 | -0.15175 | -0.28501 | -0.14445 | 121.351 | 121.1414 | 120.9674 | 61.6027 | -121.5571 | 121.0963 | 121.1826 | 121.3231 | 61.684 | -121.5377
112.5469 | 121.7377 | -61.7432 | 59.8663 | -0.005418 | -0.025387 | 0.00050001 | 0.056013 | -0.0040233 | 0.052888 | -0.011751 | -0.00094006 | -0.001017 | -0.0035187 | 0.012511 | -0.0073219 | -59.0876 | -0.026065 | -61.7191 | 59.7223 | 59.5218 | 59.3479 | -61.7137 | 0.069728 | 0.059882 | -61.8369 | 59.4722 | 59.5722 | 59.699 | -61.6943 | 0.029467 | -0.14408 | 2.6555 | 0.024111 | -0.005356 | -0.34453 | -0.51846 | 0.04887 | -0.39416 | 61.8129 | -0.093719 | -0.14259 | -0.29416 | -0.16734 | 121.4654 | 121.265 | 121.091 | 61.7171 | -121.58 | 121.2153 | 121.3153 | 121.4422 | 61.803 | -121.5606
114.2969 | 121.843 | -61.7432 | 59.7336 | 0.002213 | -0.0256 | 0.00071361 | 0.056227 | -0.0042369 | 0.052674 | -0.011751 | -0.00094006 | -0.001017 | -0.0028779 | 0.012297 | -0.0073219 | -59.0922 | -0.012329 | -61.7099 | 59.7268 | 59.5172 | 59.3479 | -61.7137 | 0.074307 | 0.059882 | -61.8415 | 59.4722 | 59.5722 | 59.699 | -61.6851 | 0.029467 | -0.006747 | 2.651 | 0.033268 | 0.003801 | -0.21636 | -0.38571 | 0.058027 | -0.26141 | 61.8175 | -0.098298 | -0.15633 | -0.16141 | -0.03459 | 121.47 | 121.2604 | 121.091 | 61.7308 | -121.4473 | 121.2153 | 121.3153 | 121.4422 | 61.803 | -121.4187
116.0312 | 121.8384 | -61.7844 | 59.6878 | 0.002213 | -0.025814 | 0.00050001 | 0.056227 | -0.0042369 | 0.052674 | -0.0041205 | -0.0011537 | -0.0014444 | -0.0030915 | 0.012511 | -0.0071083 | -59.083 | -0.016908 | -61.7191 | 59.7268 | 59.5264 | 59.3525 | -61.7137 | 0.074307 | 0.06904 | -61.846 | 59.4722 | 59.5676 | 59.699 | -61.6897 | 0.070666 | 0.03903 | 2.7013 | 0.06531 | -0.005356 | -0.16143 | -0.33535 | 0.094648 | -0.21564 | 61.8587 | -0.061678 | -0.15633 | -0.12022 | 0.011187 | 121.5112 | 121.3107 | 121.1368 | 61.7675 | -121.4015 | 121.2565 | 121.352 | 121.4834 | 61.8534 | -121.3775
117.7188 | 121.7056 | -61.8301 | 59.7565 | -0.005418 | -0.025814 | 0.001141 | 0.056227 | -0.0044507 | 0.052674 | -0.011751 | -0.00094006 | -0.001017 | -0.0035187 | 0.012724 | -0.0073219 | -59.0556 | -0.007751 | -61.7145 | 59.7268 | 59.5218 | 59.3525 | -61.7137 | 0.074307 | 0.064461 | -61.8369 | 59.4722 | 59.5722 | 59.699 | -61.6851 | 0.11644 | -0.029635 | 2.7746 | 0.11566 | -0.000777 | -0.23467 | -0.40402 | 0.145 | -0.2843 | 61.9044 | -0.006744 | -0.15175 | -0.1843 | -0.057478 | 121.557 | 121.3519 | 121.1826 | 61.8224 | -121.4702 | 121.3023 | 121.4023 | 121.5291 | 61.8946 | -121.4416
119.4688 | 121.7422 | -61.7065 | 59.8526 | 0.009844 | -0.026028 | 0.00071361 | 0.05644 | -0.0040233 | 0.052674 | -0.0041205 | -0.0011537 | -0.001658 | -0.0033051 | 0.012511 | -0.0073219 | -59.1105 | -0.012329 | -61.7145 | 59.7223 | 59.5218 | 59.3479 | -61.7045 | 0.069728 | 0.064461 | -61.846 | 59.4767 | 59.5767 | 59.6944 | -61.6897 | 0.002004 | -0.13034 | 2.596 | -0.007931 | -0.009935 | -0.3308 | -0.50473 | 0.016828 | -0.37585 | 61.7763 | -0.1395 | -0.15633 | -0.27585 | -0.15819 | 121.4288 | 121.2283 | 121.0544 | 61.6942 | -121.5571 | 121.1833 | 121.2833 | 121.401 | 61.771 | -121.5423
121.2188 | 121.7651 | -61.7981 | 59.761 | 0.002213 | -0.026028 | 0.00071361 | 0.05644 | -0.0042369 | 0.052461 | -0.011751 | -0.00094006 | -0.00080338 | -0.0030915 | 0.012297 | -0.0071083 | -59.051 | -0.007751 | -61.7145 | 59.7314 | 59.5172 | 59.3525 | -61.7183 | 0.074307 | 0.064461 | -61.846 | 59.4722 | 59.5676 | 59.699 | -61.6897 | 0.07982 | -0.029634 | 2.7471 | 0.083622 | 0.003802 | -0.24383 | -0.40859 | 0.10838 | -0.28888 | 61.8724 | -0.047945 | -0.15633 | -0.19346 | -0.062055 | 121.5295 | 121.3153 | 121.1506 | 61.7903 | -121.4793 | 121.2703 | 121.3657 | 121.4971 | 61.8626 | -121.4508
122.9844 | 121.8521 | -61.6562 | 59.8022 | -0.005418 | -0.0256 | 0.00092741 | 0.05644 | -0.0042369 | 0.052888 | 0.00351 | -0.00094006 | -0.0014444 | -0.0035187 | 0.012297 | -0.0071083 | -59.1609 | -0.016908 | -61.7145 | 59.7177 | 59.5218 | 59.3525 | -61.7183 | 0.069728 | 0.064461 | -61.846 | 59.4767 | 59.5722 | 59.6944 | -61.6806 | -0.062087 | -0.084568 | 2.4953 | -0.058285 | 0.003802 | -0.28045 | -0.44979 | -0.024369 | -0.3255 | 61.7259 | -0.18985 | -0.16548 | -0.23008 | -0.10783 | 121.3739 | 121.178 | 121.0086 | 61.6393 | -121.5205 | 121.1329 | 121.2284 | 121.3506 | 61.7206 | -121.4828
124.7344 | 121.8475 | -61.7661 | 59.7198 | -0.013049 | -0.025814 | 0.00071361 | 0.056227 | -0.0046643 | 0.052461 | -0.011751 | -0.0011537 | -0.0012306 | -0.0033051 | 0.012511 | -0.0071083 | -59.1014 | -0.007751 | -61.7191 | 59.7268 | 59.5218 | 59.3525 | -61.7137 | 0.074307 | 0.059882 | -61.8369 | 59.4722 | 59.5676 | 59.699 | -61.6897 | 0.052355 | 0.006986 | 2.6647 | 0.046999 | -0.005356 | -0.19805 | -0.3674 | 0.076337 | -0.24768 | 61.8404 | -0.070831 | -0.14717 | -0.15226 | -0.020857 | 121.4929 | 121.2879 | 121.1185 | 61.7583 | -121.4335 | 121.2382 | 121.3336 | 121.465 | 61.8259 | -121.4096
126.4062 | 121.7102 | -61.7157 | 59.8434 | -0.005418 | -0.026241 | 0.00071361 | 0.056227 | -0.0044507 | 0.052033 | -0.011751 | -0.0013673 | -0.0014444 | -0.0033051 | 0.012724 | -0.0073219 | -59.0876 | -0.021486 | -61.7191 | 59.736 | 59.531 | 59.3525 | -61.7137 | 0.06515 | 0.059882 | -61.8415 | 59.4813 | 59.5767 | 59.699 | -61.6943 | 0.002001 | -0.10745 | 2.6281 | -0.003355 | -0.005356 | -0.31249 | -0.49099 | 0.021404 | -0.36212 | 61.7808 | -0.12576 | -0.14717 | -0.2667 | -0.14445 | 121.4517 | 121.2467 | 121.0682 | 61.6942 | -121.5571 | 121.197 | 121.2924 | 121.4147 | 61.7756 | -121.5377
128.1562 | 121.8155 | -61.7157 | 59.7839 | -0.005418 | -0.0256 | 0.00092741 | 0.056013 | -0.0046643 | 0.052674 | -0.011751 | -0.0011537 | -0.0012306 | -0.0033051 | 0.012297 | -0.0075355 | -59.1151 | -0.016908 | -61.7191 | 59.7223 | 59.5264 | 59.3525 | -61.7137 | 0.074307 | 0.055303 | -61.8415 | 59.4676 | 59.5722 | 59.6898 | -61.6897 | 0.002001 | -0.061679 | 2.6006 | -0.003355 | -0.005356 | -0.25756 | -0.43148 | 0.025983 | -0.31634 | 61.79 | -0.12576 | -0.15175 | -0.21177 | -0.094102 | 121.438 | 121.2421 | 121.0682 | 61.6988 | -121.4976 | 121.1833 | 121.2879 | 121.4055 | 61.771 | -121.4737
129.9219 | 121.8521 | -61.7661 | 59.6924 | -0.005418 | -0.025814 | 0.00092741 | 0.056013 | -0.0046643 | 0.052247 | -0.011751 | -0.0011537 | -0.001017 | -0.0033051 | 0.012511 | -0.0073219 | -59.0693 | -0.003172 | -61.7099 | 59.7223 | 59.5218 | 59.3525 | -61.7137 | 0.069728 | 0.06904 | -61.8369 | 59.4767 | 59.5722 | 59.6944 | -61.6897 | 0.052355 | 0.029874 | 2.6967 | 0.056156 | 0.003801 | -0.17058 | -0.33993 | 0.076337 | -0.21563 | 61.8358 | -0.070831 | -0.14717 | -0.12022 | 0.00203 | 121.4883 | 121.2879 | 121.1185 | 61.7629 | -121.4061 | 121.2428 | 121.3382 | 121.4605 | 61.8351 | -121.3821
131.6094 | 121.7056 | -61.8393 | 59.7427 | -0.005418 | -0.026028 | 0.00092741 | 0.056227 | -0.0044507 | 0.052674 | -0.0041205 | -0.00094006 | -0.0012306 | -0.0035187 | 0.012724 | -0.0073219 | -59.0464 | -0.012329 | -61.7145 | 59.7223 | 59.5218 | 59.3479 | -61.7137 | 0.083464 | 0.073618 | -61.8369 | 59.4722 | 59.5813 | 59.7036 | -61.6851 | 0.1256 | -0.02048 | 2.7929 | 0.12482 | -0.000777 | -0.22094 | -0.39486 | 0.15416 | -0.27057 | 61.9228 | 0.002411 | -0.15175 | -0.16141 | -0.039167 | 121.5616 | 121.3611 | 121.1872 | 61.827 | -121.4564 | 121.3115 | 121.4206 | 121.5429 | 61.9129 | -121.4279
133.3594 | 121.7972 | -61.7203 | 59.7931 | -0.013049 | -0.025814 | 0.00092741 | 0.05644 | -0.0042369 | 0.052461 | -0.011751 | -0.0011537 | -0.0012306 | -0.0033051 | 0.012724 | -0.0071083 | -59.1243 | -0.012329 | -61.7145 | 59.7223 | 59.5218 | 59.3525 | -61.7137 | 0.074307 | 0.059882 | -61.8369 | 59.4767 | 59.5722 | 59.6944 | -61.6851 | 0.006579 | -0.070834 | 2.596 | 0.005802 | -0.000777 | -0.27129 | -0.44064 | 0.035139 | -0.31634 | 61.7946 | -0.11661 | -0.15175 | -0.22092 | -0.098678 | 121.4425 | 121.2421 | 121.0727 | 61.7079 | -121.5068 | 121.197 | 121.2924 | 121.4147 | 61.7802 | -121.4782
135.1094 | 121.7056 | -61.7844 | 59.7519 | 0.009844 | -0.026028 | 0.0013548 | 0.056654 | -0.0046643 | 0.052033 | -0.011751 | -0.00094006 | -0.001658 | -0.0035187 | 0.012297 | -0.0071083 | -59.0464 | -0.016908 | -61.7191 | 59.7314 | 59.5218 | 59.3525 | -61.7137 | 0.078886 | 0.059882 | -61.8369 | 59.4722 | 59.5767 | 59.699 | -61.6897 | 0.070666 | -0.020479 | 2.7379 | 0.06531 | -0.005356 | -0.23009 | -0.39944 | 0.094648 | -0.27972 | 61.8632 | -0.05252 | -0.14717 | -0.17515 | -0.0529 | 121.5158 | 121.3062 | 121.1368 | 61.7675 | -121.4656 | 121.2565 | 121.3611 | 121.4834 | 61.8442 | -121.4416
136.7812 | 121.8063 | -61.7065 | 59.7977 | -0.013049 | -0.026028 | 0.00050001 | 0.056227 | -0.0042369 | 0.052674 | -0.011751 | -0.00094006 | -0.0012306 | -0.0035187 | 0.012297 | -0.0073219 | -59.1288 | -0.016908 | -61.7282 | 59.7223 | 59.531 | 59.3433 | -61.7137 | 0.069728 | 0.064461 | -61.8369 | 59.4767 | 59.5676 | 59.699 | -61.6897 | -0.007154 | -0.075411 | 2.5777 | -0.021666 | -0.014512 | -0.26671 | -0.45437 | 0.016828 | -0.32092 | 61.7763 | -0.13034 | -0.14717 | -0.23008 | -0.098676 | 121.4288 | 121.2375 | 121.0498 | 61.6896 | -121.5114 | 121.1833 | 121.2741 | 121.4055 | 61.771 | -121.4874
138.5312 | 121.8384 | -61.6653 | 59.848 | -0.005418 | -0.026028 | 0.00092741 | 0.056227 | -0.0044507 | 0.052461 | 0.01114 | -0.00094006 | -0.0012306 | -0.0035187 | 0.012724 | -0.0073219 | -59.1609 | -0.016908 | -61.7191 | 59.7268 | 59.5218 | 59.357 | -61.7045 | 0.069728 | 0.06904 | -61.8369 | 59.4722 | 59.5722 | 59.7036 | -61.6897 | -0.039195 | -0.12119 | 2.5045 | -0.053709 | -0.014514 | -0.32622 | -0.49099 | -0.024371 | -0.37585 | 61.7351 | -0.17154 | -0.14717 | -0.27585 | -0.14445 | 121.3922 | 121.1871 | 121.0224 | 61.6484 | -121.5526 | 121.1375 | 121.2375 | 121.3689 | 61.7344 | -121.5377
140.2812 | 121.8384 | -61.7706 | 59.7198 | -0.005418 | -0.026028 | 0.00071361 | 0.056227 | -0.0044507 | 0.052247 | -0.0041205 | -0.00094006 | -0.00080338 | -0.0030915 | 0.012511 | -0.0073219 | -59.0739 | -0.012329 | -61.7191 | 59.7223 | 59.5218 | 59.3525 | -61.7183 | 0.078886 | 0.064461 | -61.8369 | 59.4767 | 59.5722 | 59.6944 | -61.6851 | 0.052354 | 0.002408 | 2.6967 | 0.051577 | -0.000777 | -0.19805 | -0.3674 | 0.085493 | -0.2431 | 61.8495 | -0.066253 | -0.15175 | -0.14768 | -0.025436 | 121.4929 | 121.2924 | 121.1231 | 61.7583 | -121.4381 | 121.2474 | 121.3428 | 121.465 | 61.8351 | -121.405
142.0156 | 121.7468 | -61.7889 | 59.7473 | -0.005418 | -0.026028 | 0.00071361 | 0.05644 | -0.0046643 | 0.052461 | -0.0041205 | -0.0011537 | -0.0012306 | -0.0035187 | 0.013152 | -0.0073219 | -59.051 | -0.012329 | -61.7236 | 59.7268 | 59.5172 | 59.3479 | -61.7045 | 0.069728 | 0.06904 | -61.8369 | 59.4722 | 59.5722 | 59.6944 | -61.6851 | 0.084401 | -0.020479 | 2.7379 | 0.065309 | -0.019092 | -0.23009 | -0.39944 | 0.1038 | -0.27515 | 61.8587 | -0.047943 | -0.15175 | -0.17515 | -0.052901 | 121.5158 | 121.3062 | 121.1368 | 61.7766 | -121.4519 | 121.2611 | 121.3611 | 121.4834 | 61.858 | -121.4325
143.75 | 121.8338 | -61.7523 | 59.7382 | 0.009844 | -0.026241 | 0.00092741 | 0.056013 | -0.0046643 | 0.052674 | -0.011751 | -0.0011537 | -0.0014444 | -0.0030915 | 0.012724 | -0.0073219 | -59.1014 | -0.012329 | -61.7145 | 59.7268 | 59.5172 | 59.3479 | -61.7137 | 0.083464 | 0.06904 | -61.8415 | 59.4813 | 59.5722 | 59.6944 | -61.6851 | 0.038622 | -0.011324 | 2.651 | 0.037845 | -0.000777 | -0.22094 | -0.39028 | 0.067182 | -0.25683 | 61.8358 | -0.089143 | -0.15633 | -0.16599 | -0.043746 | 121.4792 | 121.2695 | 121.1002 | 61.74 | -121.4519 | 121.2336 | 121.3245 | 121.4467 | 61.8214 | -121.4233
145.5156 | 121.7148 | -61.7294 | 59.8206 | 0.002213 | -0.026028 | 0.00092741 | 0.056013 | -0.0044507 | 0.052247 | -0.011751 | -0.00094006 | -0.0012306 | -0.0030915 | 0.012938 | -0.0075355 | -59.0647 | -0.016908 | -61.7099 | 59.7268 | 59.5264 | 59.3525 | -61.7137 | 0.074307 | 0.059882 | -61.8369 | 59.4767 | 59.5676 | 59.699 | -61.6897 | 0.015734 | -0.093722 | 2.6647 | 0.019535 | 0.003801 | -0.29418 | -0.4681 | 0.039716 | -0.34381 | 61.8037 | -0.10745 | -0.14717 | -0.25297 | -0.12157 | 121.4563 | 121.2558 | 121.0819 | 61.7125 | -121.5343 | 121.2062 | 121.297 | 121.4284 | 61.7893 | -121.5103
147.2031 | 121.8155 | -61.7569 | 59.7198 | -0.005418 | -0.026028 | 0.00092741 | 0.056227 | -0.0044507 | 0.052247 | 0.00351 | -0.0011537 | -0.0014444 | -0.0035187 | 0.012724 | -0.0075355 | -59.0968 | -0.016908 | -61.7099 | 59.7223 | 59.5264 | 59.3525 | -61.7183 | 0.078886 | 0.064461 | -61.846 | 59.4767 | 59.5722 | 59.6944 | -61.6851 | 0.038621 | 0.002408 | 2.6601 | 0.047001 | 0.00838 | -0.19347 | -0.3674 | 0.07176 | -0.2431 | 61.8358 | -0.089144 | -0.1609 | -0.14768 | -0.025436 | 121.4792 | 121.2833 | 121.1094 | 61.74 | -121.4381 | 121.2336 | 121.3291 | 121.4513 | 61.8214 | -121.405
148.9375 | 121.7285 | -61.7111 | 59.8663 | -0.005418 | -0.026241 | 0.001141 | 0.056227 | -0.0042369 | 0.052461 | 0.00351 | -0.00072626 | -0.00080338 | -0.0033051 | 0.012938 | -0.0068945 | -59.0922 | -0.012329 | -61.7053 | 59.7223 | 59.5264 | 59.3525 | -61.7091 | 0.069728 | 0.059882 | -61.8415 | 59.4722 | 59.5676 | 59.699 | -61.6943 | 0.002003 | -0.14408 | 2.6189 | 0.005803 | 0.0038 | -0.33995 | -0.51388 | 0.016827 | -0.39416 | 61.7808 | -0.13034 | -0.14717 | -0.29874 | -0.16734 | 121.4334 | 121.2375 | 121.0636 | 61.6988 | -121.5755 | 121.1833 | 121.2787 | 121.4101 | 61.771 | -121.5606
150.625 | 121.8613 | -61.7935 | 59.6924 | -0.005418 | -0.026028 | 0.00071361 | 0.055799 | -0.0044507 | 0.052461 | -0.0041205 | -0.0011537 | -0.0012306 | -0.0030915 | 0.012938 | -0.0073219 | -59.083 | -0.012329 | -61.7099 | 59.7223 | 59.5264 | 59.3479 | -61.7 | 0.074307 | 0.064461 | -61.8369 | 59.4676 | 59.5722 | 59.6944 | -61.6851 | 0.093557 | 0.029874 | 2.7105 | 0.083622 | -0.009935 | -0.166 | -0.34451 | 0.10838 | -0.22479 | 61.8678 | -0.043365 | -0.15175 | -0.12022 | 0.00203 | 121.5158 | 121.3199 | 121.1414 | 61.7812 | -121.3923 | 121.2611 | 121.3657 | 121.4879 | 61.858 | -121.3775
152.375 | 121.7514 | -61.8256 | 59.7107 | 0.002213 | -0.026028 | 0.00071361 | 0.056013 | -0.0046643 | 0.052674 | -0.0041205 | -0.00094006 | -0.001017 | -0.0033051 | 0.012724 | -0.0075355 | -59.0602 | -0.007751 | -61.7053 | 59.7268 | 59.5264 | 59.3525 | -61.7137 | 0.083464 | 0.06904 | -61.8415 | 59.4767 | 59.5722 | 59.7036 | -61.6897 | 0.11186 | 0.016142 | 2.7654 | 0.12024 | 0.008379 | -0.18431 | -0.35824 | 0.13585 | -0.23394 | 61.909 | -0.0159 | -0.15175 | -0.13853 | -0.007123 | 121.5524 | 121.3519 | 121.178 | 61.8178 | -121.4244 | 121.3023 | 121.3977 | 121.5291 | 61.8946 | -121.4004
154.125 | 121.701 | -61.853 | 59.7107 | -0.005418 | -0.026028 | 0.00071361 | 0.055585 | -0.0044507 | 0.052461 | -0.0041205 | -0.00094006 | -0.001017 | -0.0033051 | 0.012938 | -0.0073219 | -59.0556 | -0.016908 | -61.7145 | 59.7177 | 59.5218 | 59.3525 | -61.7091 | 0.069728 | 0.064461 | -61.8369 | 59.4767 | 59.5676 | 59.6898 | -61.6851 | 0.14391 | 0.006985 | 2.7974 | 0.13855 | -0.005356 | -0.18889 | -0.35824 | 0.16789 | -0.23394 | 61.9228 | 0.016144 | -0.15175 | -0.1431 | -0.020859 | 121.5707 | 121.3748 | 121.2055 | 61.8361 | -121.4198 | 121.3298 | 121.4206 | 121.5429 | 61.9175 | -121.3958
155.8125 | 121.788 | -61.6562 | 59.848 | 0.002213 | -0.026028 | 0.00071361 | 0.056013 | -0.0044507 | 0.052247 | -0.011751 | -0.0011537 | -0.00080338 | -0.0030915 | 0.012511 | -0.0068945 | -59.1288 | -0.016908 | -61.7099 | 59.7268 | 59.5218 | 59.3525 | -61.7137 | 0.06515 | 0.059882 | -61.8323 | 59.4767 | 59.5722 | 59.699 | -61.6989 | -0.057508 | -0.12119 | 2.5274 | -0.053707 | 0.003801 | -0.32622 | -0.49557 | -0.042684 | -0.37127 | 61.7213 | -0.17612 | -0.13343 | -0.27585 | -0.14903 | 121.383 | 121.178 | 121.0086 | 61.6393 | -121.5617 | 121.1329 | 121.2284 | 121.3552 | 61.7161 | -121.5469
157.5625 | 121.7194 | -61.7386 | 59.8434 | 0.009844 | -0.026241 | 0.00092741 | 0.056227 | -0.0042369 | 0.052461 | -0.0041205 | -0.0013673 | -0.001017 | -0.0030915 | 0.012724 | -0.0071083 | -59.0739 | -0.026065 | -61.7007 | 59.7223 | 59.531 | 59.3525 | -61.7137 | 0.06515 | 0.059882 | -61.8415 | 59.4813 | 59.5676 | 59.7036 | -61.6897 | 0.024889 | -0.12119 | 2.6647 | 0.037846 | 0.012957 | -0.31249 | -0.49099 | 0.048871 | -0.36212 | 61.8037 | -0.10288 | -0.15175 | -0.27586 | -0.13988 | 121.4608 | 121.2695 | 121.091 | 61.7125 | -121.5571 | 121.2199 | 121.3062 | 121.4422 | 61.7985 | -121.5332
159.2969 | 121.7194 | -61.8393 | 59.7153 | -0.013049 | -0.026241 | 0.00050001 | 0.055799 | -0.0046643 | 0.052674 | -0.0041205 | -0.00094006 | -0.0012306 | -0.0035187 | 0.012938 | -0.0073219 | -59.0464 | -0.016908 | -61.7053 | 59.7223 | 59.5218 | 59.357 | -61.7045 | 0.069728 | 0.064461 | -61.8323 | 59.4722 | 59.5676 | 59.7036 | -61.6897 | 0.13476 | 0.006986 | 2.7929 | 0.13398 | -0.000779 | -0.19347 | -0.35824 | 0.14958 | -0.2431 | 61.909 | 0.00699 | -0.14259 | -0.14768 | -0.011701 | 121.5616 | 121.3611 | 121.1963 | 61.8224 | -121.4198 | 121.3115 | 121.4069 | 121.5429 | 61.9038 | -121.405
161.0312 | 121.8109 | -61.7432 | 59.7794 | -0.013049 | -0.026241 | 0.00071361 | 0.056227 | -0.0044507 | 0.052247 | -0.011751 | -0.0011537 | -0.0012306 | -0.0030915 | 0.012724 | -0.0071083 | -59.1014 | -0.016908 | -61.6962 | 59.7268 | 59.5172 | 59.3433 | -61.7091 | 0.074307 | 0.059882 | -61.8277 | 59.4813 | 59.5722 | 59.699 | -61.6943 | 0.034046 | -0.052523 | 2.6418 | 0.047003 | 0.012957 | -0.26214 | -0.43606 | 0.04887 | -0.29803 | 61.8175 | -0.084562 | -0.13343 | -0.20719 | -0.080366 | 121.47 | 121.2604 | 121.0865 | 61.7263 | -121.4885 | 121.2245 | 121.3153 | 121.4422 | 61.803 | -121.4737
162.7812 | 121.7926 | -61.7249 | 59.7794 | 0.002213 | -0.026241 | 0.00050001 | 0.056013 | -0.0046643 | 0.052033 | -0.011751 | -0.00094006 | -0.0012306 | -0.0033051 | 0.012938 | -0.0073219 | -59.1059 | -0.021486 | -61.7007 | 59.7177 | 59.5218 | 59.3433 | -61.7045 | 0.074307 | 0.06904 | -61.8369 | 59.4722 | 59.5676 | 59.699 | -61.6897 | 0.020315 | -0.06168 | 2.6189 | 0.024114 | 0.003799 | -0.25756 | -0.43606 | 0.035139 | -0.30719 | 61.7992 | -0.11203 | -0.14717 | -0.21177 | -0.080366 | 121.4425 | 121.2467 | 121.0682 | 61.7034 | -121.4839 | 121.197 | 121.2924 | 121.4238 | 61.7939 | -121.4691
164.5312 | 121.8384 | -61.6379 | 59.8343 | 0.009844 | -0.026455 | 0.00071361 | 0.056013 | -0.0042369 | 0.052461 | 0.00351 | -0.00094006 | -0.0012306 | -0.0037325 | 0.013152 | -0.0071083 | -59.1288 | -0.016908 | -61.6962 | 59.7268 | 59.5264 | 59.3525 | -61.7137 | 0.06515 | 0.055303 | -61.8323 | 59.4676 | 59.563 | 59.6944 | -61.6897 | -0.075819 | -0.10746 | 2.509 | -0.058283 | 0.017536 | -0.30791 | -0.48184 | -0.051837 | -0.3667 | 61.703 | -0.19443 | -0.14259 | -0.27128 | -0.13988 | 121.3647 | 121.1643 | 120.9903 | 61.621 | -121.548 | 121.1055 | 121.2009 | 121.3323 | 61.6932 | -121.524
166.2812 | 121.7468 | -61.7752 | 59.7656 | -0.005418 | -0.026455 | 0.00071361 | 0.056013 | -0.0046643 | 0.052247 | -0.011751 | -0.0011537 | -0.001017 | -0.0030915 | 0.012724 | -0.0071083 | -59.0373 | -0.016908 | -61.7007 | 59.7268 | 59.5264 | 59.3525 | -61.7137 | 0.069728 | 0.064461 | -61.8323 | 59.4676 | 59.5722 | 59.6944 | -61.6989 | 0.061511 | -0.03879 | 2.7379 | 0.074468 | 0.012957 | -0.23925 | -0.41317 | 0.076335 | -0.29803 | 61.8449 | -0.057096 | -0.13343 | -0.19346 | -0.071212 | 121.502 | 121.3016 | 121.1277 | 61.7583 | -121.4793 | 121.2428 | 121.3474 | 121.4696 | 61.8397 | -121.4645
167.9688 | 121.7422 | -61.7523 | 59.7656 | -0.005418 | -0.026241 | 0.00050001 | 0.056013 | -0.0044507 | 0.052461 | 0.00351 | -0.00094006 | -0.001017 | -0.0035187 | 0.013152 | -0.0073219 | -59.0373 | -0.012329 | -61.7007 | 59.7268 | 59.5264 | 59.3525 | -61.7137 | 0.074307 | 0.06904 | -61.8323 | 59.4722 | 59.563 | 59.6898 | -61.6897 | 0.038622 | -0.03879 | 2.7151 | 0.051579 | 0.012957 | -0.23925 | -0.41317 | 0.062604 | -0.29346 | 61.8266 | -0.079985 | -0.14259 | -0.20261 | -0.075791 | 121.4792 | 121.2787 | 121.1048 | 61.74 | -121.4793 | 121.2245 | 121.3153 | 121.4422 | 61.8214 | -121.4553
169.7188 | 121.7789 | -61.7569 | 59.7931 | 0.002213 | -0.026455 | 0.00071361 | 0.056013 | -0.0042369 | 0.052461 | -0.0041205 | -0.00072626 | -0.0014444 | -0.0030915 | 0.012938 | -0.0073219 | -59.0327 | -0.012329 | -61.7007 | 59.7223 | 59.5218 | 59.357 | -61.7091 | 0.060571 | 0.059882 | -61.8277 | 59.4676 | 59.5584 | 59.699 | -61.6897 | 0.047779 | -0.070834 | 2.7242 | 0.056157 | 0.008378 | -0.27129 | -0.43606 | 0.067182 | -0.3255 | 61.8175 | -0.070829 | -0.13801 | -0.23466 | -0.094099 | 121.4792 | 121.2787 | 121.1139 | 61.7446 | -121.5022 | 121.2245 | 121.3153 | 121.4559 | 61.8168 | -121.4828
171.4844 | 121.8338 | -61.6333 | 59.8297 | -0.005418 | -0.026028 | 0.00050001 | 0.056227 | -0.0042369 | 0.052247 | -0.011751 | -0.0011537 | -0.0012306 | -0.0035187 | 0.012724 | -0.0073219 | -59.1334 | -0.016908 | -61.7053 | 59.7223 | 59.531 | 59.3387 | -61.7137 | 0.069728 | 0.059882 | -61.8369 | 59.4722 | 59.5722 | 59.6944 | -61.6897 | -0.080396 | -0.10746 | 2.4999 | -0.072017 | 0.008379 | -0.29875 | -0.49099 | -0.056414 | -0.35754 | 61.703 | -0.20358 | -0.14717 | -0.25754 | -0.1353 | 121.3556 | 121.1643 | 120.972 | 61.6164 | -121.5434 | 121.1055 | 121.2055 | 121.3277 | 61.6932 | -121.5194
173.2344 | 121.7102 | -61.7065 | 59.848 | -0.005418 | -0.026669 | 0.00071361 | 0.055585 | -0.0046643 | 0.052461 | 0.00351 | -0.00094006 | -0.0012306 | -0.0030915 | 0.013152 | -0.0073219 | -59.0693 | -0.016908 | -61.7053 | 59.7223 | 59.531 | 59.3479 | -61.7091 | 0.069728 | 0.064461 | -61.8369 | 59.463 | 59.5722 | 59.6944 | -61.6851 | -0.002575 | -0.12577 | 2.6372 | 0.001225 | 0.0038 | -0.31706 | -0.50015 | 0.021406 | -0.38501 | 61.7763 | -0.13034 | -0.15175 | -0.27585 | -0.15361 | 121.4288 | 121.2375 | 121.0544 | 61.6896 | -121.5571 | 121.1696 | 121.2787 | 121.401 | 61.771 | -121.5332
175 | 121.6919 | -61.8118 | 59.7244 | 0.002213 | -0.026241 | 0.00092741 | 0.056013 | -0.0040233 | 0.052461 | -0.0041205 | -0.0011537 | -0.0012306 | -0.0035187 | 0.012724 | -0.0077491 | -59.0281 | -0.012329 | -61.7099 | 59.7223 | 59.5218 | 59.3525 | -61.7045 | 0.083464 | 0.064461 | -61.8369 | 59.4722 | 59.5722 | 59.699 | -61.6943 | 0.10729 | -0.002169 | 2.7837 | 0.10193 | -0.005357 | -0.20263 | -0.37197 | 0.11754 | -0.25226 | 61.8953 | -0.025054 | -0.14259 | -0.15226 | -0.025434 | 121.5341 | 121.3336 | 121.1643 | 61.7995 | -121.429 | 121.284 | 121.384 | 121.5108 | 61.8763 | -121.4187
176.6719 | 121.8521 | -61.6379 | 59.8251 | -0.005418 | -0.026455 | 0.00050001 | 0.056013 | -0.0046643 | 0.052247 | -0.011751 | -0.00094006 | -0.0012306 | -0.0030915 | 0.013152 | -0.0075355 | -59.138 | -0.021486 | -61.7099 | 59.7223 | 59.5218 | 59.357 | -61.7091 | 0.069728 | 0.064461 | -61.8369 | 59.4722 | 59.5722 | 59.699 | -61.6897 | -0.07124 | -0.10288 | 2.4999 | -0.072018 | -0.000778 | -0.30333 | -0.4681 | -0.051837 | -0.35296 | 61.7076 | -0.199 | -0.14717 | -0.25297 | -0.12614 | 121.3601 | 121.1597 | 120.9949 | 61.6164 | -121.5343 | 121.11 | 121.21 | 121.3369 | 61.7023 | -121.5148
178.4219 | 121.8155 | -61.7615 | 59.6786 | -0.005418 | -0.026455 | 0.00092741 | 0.055799 | -0.0044507 | 0.052461 | -0.011751 | -0.00094006 | -0.001017 | -0.0030915 | 0.012938 | -0.0075355 | -59.051 | -0.012329 | -61.7007 | 59.7223 | 59.5172 | 59.3525 | -61.7091 | 0.078886 | 0.073618 | -61.8323 | 59.463 | 59.5722 | 59.699 | -61.6851 | 0.052357 | 0.043607 | 2.7105 | 0.060735 | 0.008378 | -0.16143 | -0.3262 | 0.076338 | -0.21564 | 61.8404 | -0.070829 | -0.14717 | -0.10648 | 0.020342 | 121.4837 | 121.2787 | 121.1139 | 61.7491 | -121.3878 | 121.2245 | 121.3336 | 121.4605 | 61.8351 | -121.3638
180.1094 | 121.7651 | -61.7661 | 59.7794 | -0.005418 | -0.026669 | 0.00092741 | 0.056227 | -0.0046643 | 0.052033 | -0.011751 | -0.00094006 | -0.001017 | -0.0030915 | 0.012724 | -0.0073219 | -59.0373 | -0.012329 | -61.7053 | 59.7223 | 59.5218 | 59.3433 | -61.7137 | 0.074307 | 0.06904 | -61.8323 | 59.4767 | 59.5722 | 59.699 | -61.6851 | 0.052355 | -0.057101 | 2.7288 | 0.060734 | 0.008379 | -0.25756 | -0.43606 | 0.080915 | -0.30261 | 61.8404 | -0.066252 | -0.14717 | -0.20719 | -0.080366 | 121.4883 | 121.2879 | 121.1093 | 61.7537 | -121.4931 | 121.2428 | 121.3382 | 121.465 | 61.8351 | -121.4645
181.8438 | 121.843 | -61.6699 | 59.816 | -0.005418 | -0.026669 | 0.00071361 | 0.055799 | -0.0046643 | 0.052461 | -0.0041205 | -0.00072626 | -0.00080338 | -0.0033051 | 0.012724 | -0.0073219 | -59.138 | -0.016908 | -61.7099 | 59.7177 | 59.5264 | 59.3479 | -61.7045 | 0.074307 | 0.064461 | -61.8369 | 59.4676 | 59.5722 | 59.6944 | -61.6943 | -0.034617 | -0.098301 | 2.5319 | -0.039974 | -0.005357 | -0.2896 | -0.4681 | -0.024372 | -0.34839 | 61.7442 | -0.16696 | -0.14259 | -0.24381 | -0.12157 | 121.3876 | 121.1963 | 121.0178 | 61.653 | -121.5205 | 121.1375 | 121.2421 | 121.3643 | 61.7344 | -121.5103
183.5781 | 121.8796 | -61.6562 | 59.8343 | -0.005418 | -0.026455 | 0.00071361 | 0.055799 | -0.0044507 | 0.052674 | -0.0041205 | -0.00094006 | -0.0012306 | -0.0030915 | 0.013152 | -0.0071083 | -59.1334 | -0.016908 | -61.7007 | 59.7223 | 59.5218 | 59.3525 | -61.7137 | 0.06515 | 0.064461 | -61.8323 | 59.4722 | 59.5722 | 59.699 | -61.6989 | -0.057508 | -0.11203 | 2.5228 | -0.044551 | 0.012957 | -0.31249 | -0.48184 | -0.042684 | -0.36212 | 61.7213 | -0.17612 | -0.13343 | -0.26212 | -0.1353 | 121.3784 | 121.178 | 121.0086 | 61.6393 | -121.548 | 121.1284 | 121.2284 | 121.3552 | 61.7206 | -121.5332
185.2656 | 121.7194 | -61.7203 | 59.8343 | 0.002213 | -0.026455 | 0.00071361 | 0.055799 | -0.0044507 | 0.052461 | -0.011751 | -0.0011537 | -0.0014444 | -0.0035187 | 0.012724 | -0.0073219 | -59.051 | -0.016908 | -61.7007 | 59.7177 | 59.5218 | 59.357 | -61.7091 | 0.06515 | 0.06904 | -61.8277 | 59.463 | 59.5722 | 59.6944 | -61.6897 | 0.011158 | -0.11661 | 2.6693 | 0.019536 | 0.008378 | -0.31249 | -0.47726 | 0.030561 | -0.37128 | 61.7854 | -0.10745 | -0.13801 | -0.26212 | -0.13988 | 121.438 | 121.2421 | 121.0773 | 61.7034 | -121.5434 | 121.1833 | 121.2924 | 121.4147 | 61.7893 | -121.524
187 | 121.6965 | -61.8118 | 59.7244 | 0.002213 | -0.026455 | 0.00092741 | 0.055799 | -0.0044507 | 0.052247 | -0.0041205 | -0.00094006 | -0.001017 | -0.0033051 | 0.012724 | -0.0077491 | -59.0235 | -0.021486 | -61.7099 | 59.7223 | 59.5218 | 59.3525 | -61.7091 | 0.078886 | 0.073618 | -61.8277 | 59.4722 | 59.563 | 59.699 | -61.6851 | 0.10271 | -0.002169 | 2.7883 | 0.10193 | -0.000778 | -0.20263 | -0.37197 | 0.12669 | -0.25226 | 61.8907 | -0.015897 | -0.14259 | -0.16141 | -0.025434 | 121.5341 | 121.3336 | 121.1643 | 61.7903 | -121.4335 | 121.284 | 121.3748 | 121.5108 | 61.8854 | -121.4096
188.7344 | 121.7102 | -61.8073 | 59.7382 | -0.005418 | -0.026669 | 0.00092741 | 0.055585 | -0.0046643 | 0.052247 | -0.0041205 | -0.0011537 | -0.0012306 | -0.0033051 | 0.013152 | -0.0075355 | -59.0235 | -0.016908 | -61.7099 | 59.7223 | 59.5264 | 59.3525 | -61.7091 | 0.078886 | 0.064461 | -61.8323 | 59.4722 | 59.5722 | 59.6898 | -61.6851 | 0.098133 | -0.015902 | 2.7837 | 0.097355 | -0.000778 | -0.21178 | -0.38571 | 0.12211 | -0.26599 | 61.8861 | -0.025053 | -0.14717 | -0.16599 | -0.048325 | 121.5295 | 121.3336 | 121.1597 | 61.7903 | -121.4473 | 121.2794 | 121.3794 | 121.4971 | 61.8717 | -121.4233
190.5 | 121.8521 | -61.6333 | 59.816 | 0.009844 | -0.026669 | 0.00071361 | 0.056013 | -0.0044507 | 0.052033 | 0.00351 | -0.00051266 | -0.0012306 | -0.0035187 | 0.012938 | -0.0073219 | -59.1288 | -0.016908 | -61.7007 | 59.7177 | 59.5264 | 59.3525 | -61.7045 | 0.069728 | 0.06904 | -61.8277 | 59.4722 | 59.563 | 59.6944 | -61.6897 | -0.071238 | -0.098301 | 2.5045 | -0.067439 | 0.003799 | -0.2896 | -0.46352 | -0.056414 | -0.34381 | 61.703 | -0.19442 | -0.13801 | -0.25297 | -0.12157 | 121.351 | 121.1597 | 120.9858 | 61.6164 | -121.5205 | 121.1055 | 121.1963 | 121.3277 | 61.7023 | -121.5057
192.1719 | 121.8201 | -61.7706 | 59.7153 | -0.013049 | -0.026455 | 0.00071361 | 0.056013 | -0.0040233 | 0.052461 | -0.0041205 | -0.0011537 | -0.001017 | -0.0035187 | 0.012938 | -0.0075355 | -59.0785 | -0.012329 | -61.7007 | 59.7177 | 59.5218 | 59.3479 | -61.7137 | 0.083464 | 0.06904 | -61.8369 | 59.4676 | 59.563 | 59.6944 | -61.6943 | 0.056933 | 0.002407 | 2.6922 | 0.06989 | 0.012957 | -0.19347 | -0.3674 | 0.076336 | -0.24768 | 61.8541 | -0.066253 | -0.14259 | -0.15226 | -0.020858 | 121.4883 | 121.2924 | 121.1185 | 61.7583 | -121.429 | 121.2382 | 121.3336 | 121.465 | 61.8397 | -121.4096
193.9219 | 121.8384 | -61.6562 | 59.8206 | 0.002213 | -0.026882 | 0.00028641 | 0.056013 | -0.0042369 | 0.052461 | -0.0041205 | -0.00094006 | -0.0014444 | -0.0033051 | 0.013152 | -0.0073219 | -59.1426 | -0.012329 | -61.7053 | 59.7177 | 59.5264 | 59.3479 | -61.7045 | 0.069728 | 0.064461 | -61.8323 | 59.4722 | 59.5722 | 59.699 | -61.6897 | -0.04835 | -0.10288 | 2.5136 | -0.049129 | -0.000779 | -0.29418 | -0.47268 | -0.033526 | -0.34839 | 61.7259 | -0.17612 | -0.14259 | -0.24839 | -0.12157 | 121.3739 | 121.1826 | 121.0041 | 61.6439 | -121.5251 | 121.1284 | 121.2284 | 121.3552 | 61.7206 | -121.5103
195.6719 | 121.7972 | -61.7706 | 59.7015 | -0.005418 | -0.026882 | 0.00092741 | 0.056013 | -0.0044507 | 0.052461 | -0.0041205 | -0.00094006 | -0.0014444 | -0.0035187 | 0.012724 | -0.0073219 | -59.0464 | -0.012329 | -61.6962 | 59.7177 | 59.5218 | 59.357 | -61.7137 | 0.074307 | 0.073618 | -61.8231 | 59.4722 | 59.5722 | 59.6944 | -61.6851 | 0.056933 | 0.01614 | 2.7242 | 0.074469 | 0.017536 | -0.17974 | -0.34451 | 0.085493 | -0.22937 | 61.8449 | -0.052517 | -0.13801 | -0.12937 | -0.007125 | 121.4883 | 121.2924 | 121.1277 | 61.7583 | -121.4152 | 121.2428 | 121.3428 | 121.465 | 61.8442 | -121.3867
197.3594 | 121.7056 | -61.702 | 59.8343 | 0.002213 | -0.026669 | 0.00092741 | 0.056013 | -0.0042369 | 0.052461 | 0.00351 | -0.0013673 | -0.0012306 | -0.0033051 | 0.013152 | -0.0077491 | -59.0602 | -0.016908 | -61.7007 | 59.7177 | 59.5218 | 59.3525 | -61.7045 | 0.06515 | 0.059882 | -61.8369 | 59.463 | 59.5676 | 59.6853 | -61.6897 | -0.002574 | -0.11661 | 2.6418 | 0.001225 | 0.003799 | -0.31249 | -0.48184 | 0.01225 | -0.37128 | 61.7671 | -0.13492 | -0.14717 | -0.2667 | -0.14903 | 121.4196 | 121.2238 | 121.0544 | 61.6851 | -121.5388 | 121.165 | 121.2696 | 121.3872 | 61.7618 | -121.524
199.1094 | 121.7834 | -61.647 | 59.8663 | 0.002213 | -0.026882 | 0.00071361 | 0.055799 | -0.0044507 | 0.052247 | -0.019381 | -0.0011537 | -0.0014444 | -0.0033051 | 0.012938 | -0.0075355 | -59.1105 | -0.012329 | -61.7007 | 59.7223 | 59.5264 | 59.3525 | -61.7137 | 0.069728 | 0.059882 | -61.814 | 59.4676 | 59.5722 | 59.6944 | -61.6851 | -0.066663 | -0.14408 | 2.5365 | -0.053706 | 0.012957 | -0.33995 | -0.51388 | -0.038103 | -0.39874 | 61.7168 | -0.16696 | -0.12885 | -0.29416 | -0.17192 | 121.3693 | 121.1734 | 120.9995 | 61.6347 | -121.58 | 121.1146 | 121.2192 | 121.3414 | 61.7069 | -121.5515
200.8594 | 121.8246 | -61.6425 | 59.8297 | -0.013049 | -0.026882 | 0.00071361 | 0.056013 | -0.0044507 | 0.052033 | -0.019381 | -0.00094006 | -0.0012306 | -0.0033051 | 0.013365 | -0.0075355 | -59.1334 | -0.012329 | -61.7007 | 59.7223 | 59.5218 | 59.3525 | -61.7091 | 0.06515 | 0.06904 | -61.8323 | 59.4767 | 59.5676 | 59.6898 | -61.6897 | -0.066662 | -0.10746 | 2.509 | -0.058284 | 0.008378 | -0.30791 | -0.47726 | -0.047259 | -0.35296 | 61.7076 | -0.18985 | -0.14259 | -0.26212 | -0.13988 | 121.3647 | 121.1643 | 120.9949 | 61.6301 | -121.5388 | 121.1192 | 121.21 | 121.3323 | 61.7115 | -121.5194
202.6094 | 121.7422 | -61.7615 | 59.7427 | -0.005418 | -0.026882 | 0.00071361 | 0.056013 | -0.0048779 | 0.052674 | -0.019381 | -0.0013673 | -0.001658 | -0.0033051 | 0.012938 | -0.0073219 | -59.0327 | -0.003172 | -61.7007 | 59.7223 | 59.5264 | 59.357 | -61.7091 | 0.069728 | 0.06904 | -61.8323 | 59.4676 | 59.5722 | 59.6944 | -61.6851 | 0.052357 | -0.02048 | 2.7288 | 0.060735 | 0.008378 | -0.21636 | -0.38571 | 0.076338 | -0.27515 | 61.8312 | -0.070829 | -0.14717 | -0.17057 | -0.048324 | 121.4837 | 121.2879 | 121.1185 | 61.7583 | -121.4519 | 121.2291 | 121.3336 | 121.4559 | 61.8305 | -121.4279
204.3594 | 121.8155 | -61.647 | 59.8068 | -0.005418 | -0.026882 | 0.00092741 | 0.055799 | -0.0044507 | 0.05182 | -0.011751 | -0.00094006 | -0.0014444 | -0.0033051 | 0.013365 | -0.0073219 | -59.138 | -0.012329 | -61.6962 | 59.7223 | 59.531 | 59.3479 | -61.7091 | 0.074307 | 0.064461 | -61.8277 | 59.4676 | 59.5722 | 59.6898 | -61.6943 | -0.062084 | -0.084567 | 2.509 | -0.049127 | 0.012957 | -0.27587 | -0.45895 | -0.04726 | -0.33923 | 61.7213 | -0.18069 | -0.13343 | -0.23466 | -0.11699 | 121.3693 | 121.178 | 120.9949 | 61.6347 | -121.5159 | 121.1146 | 121.2192 | 121.3369 | 61.7115 | -121.5011
206.0469 | 121.7285 | -61.8073 | 59.6924 | -0.005418 | -0.026669 | 0.00071361 | 0.055799 | -0.0046643 | 0.052461 | -0.011751 | -0.00094006 | -0.0014444 | -0.0033051 | 0.013152 | -0.0071083 | -59.0373 | -0.007751 | -61.6962 | 59.7223 | 59.5264 | 59.3525 | -61.7045 | 0.083464 | 0.06904 | -61.8277 | 59.4676 | 59.5722 | 59.6898 | -61.6851 | 0.10271 | 0.029874 | 2.77 | 0.11109 | 0.008378 | -0.166 | -0.33993 | 0.12211 | -0.22479 | 61.8907 | -0.020475 | -0.14259 | -0.12022 | -0.002549 | 121.5295 | 121.3336 | 121.1597 | 61.7995 | -121.3969 | 121.2748 | 121.3794 | 121.4971 | 61.8763 | -121.3775
207.7969 | 121.8384 | -61.7523 | 59.6924 | 0.009844 | -0.026882 | 0.00071361 | 0.056013 | -0.0044507 | 0.052461 | -0.0041205 | -0.00094006 | -0.001017 | -0.0037325 | 0.013152 | -0.0073219 | -59.0647 | -0.012329 | -61.6962 | 59.7223 | 59.5264 | 59.3525 | -61.7091 | 0.074307 | 0.064461 | -61.8323 | 59.4676 | 59.5722 | 59.6944 | -61.6897 | 0.043201 | 0.029874 | 2.6876 | 0.056158 | 0.012957 | -0.166 | -0.33993 | 0.062604 | -0.22479 | 61.8266 | -0.079985 | -0.14259 | -0.12022 | 0.00203 | 121.4746 | 121.2787 | 121.1048 | 61.74 | -121.4015 | 121.2199 | 121.3245 | 121.4467 | 61.8168 | -121.3821
209.4844 | 121.7285 | -61.8027 | 59.7061 | -0.013049 | -0.027096 | 0.00092741 | 0.055372 | -0.0046643 | 0.052033 | -0.011751 | -0.0011537 | -0.0012306 | -0.0033051 | 0.012938 | -0.0073219 | -59.0373 | -0.012329 | -61.6916 | 59.7223 | 59.5264 | 59.3525 | -61.7091 | 0.078886 | 0.078197 | -61.8277 | 59.4676 | 59.5676 | 59.699 | -61.6806 | 0.093555 | 0.016141 | 2.7654 | 0.11109 | 0.017535 | -0.17974 | -0.35366 | 0.12212 | -0.23853 | 61.8816 | -0.025053 | -0.14717 | -0.13853 | -0.007124 | 121.5249 | 121.3291 | 121.1551 | 61.7903 | -121.4152 | 121.2703 | 121.3703 | 121.5017 | 61.8809 | -121.3867
211.2344 | 121.7102 | -61.6882 | 59.8434 | 0.002213 | -0.027096 | 0.00071361 | 0.056013 | -0.0042369 | 0.052033 | -0.0041205 | -0.00094006 | -0.0014444 | -0.0030915 | 0.013152 | -0.0073219 | -59.083 | -0.016908 | -61.6962 | 59.7131 | 59.5172 | 59.3479 | -61.7137 | 0.074307 | 0.064461 | -61.8323 | 59.4722 | 59.5722 | 59.6898 | -61.6943 | -0.025465 | -0.13035 | 2.6052 | -0.007929 | 0.017536 | -0.32623 | -0.49557 | -0.006062 | -0.37128 | 61.7625 | -0.14407 | -0.13801 | -0.27128 | -0.15361 | 121.4013 | 121.2055 | 121.0361 | 61.6713 | -121.5571 | 121.1604 | 121.2604 | 121.3781 | 61.7527 | -121.5377
212.9844 | 121.8155 | -61.734 | 59.7107 | -0.013049 | -0.026882 | 0.00071361 | 0.055799 | -0.0046643 | 0.05182 | -0.0041205 | -0.00072626 | -0.001017 | -0.0030915 | 0.013365 | -0.0075355 | -59.0739 | -0.007751 | -61.6916 | 59.7223 | 59.531 | 59.357 | -61.7 | 0.078886 | 0.073618 | -61.8277 | 59.4722 | 59.5722 | 59.6898 | -61.6851 | 0.034048 | 0.011564 | 2.6601 | 0.042426 | 0.008378 | -0.17974 | -0.35366 | 0.048872 | -0.23852 | 61.8129 | -0.093717 | -0.14259 | -0.13853 | -0.020859 | 121.4563 | 121.265 | 121.091 | 61.7263 | -121.4107 | 121.2062 | 121.3062 | 121.4238 | 61.8076 | -121.3958
214.6719 | 121.701 | -61.8073 | 59.729 | 0.002213 | -0.026669 | 0.00071361 | 0.055799 | -0.0046643 | 0.052461 | -0.0041205 | -0.00094006 | -0.001017 | -0.0033051 | 0.013152 | -0.0075355 | -59.0235 | -0.016908 | -61.7007 | 59.7177 | 59.5264 | 59.3479 | -61.7091 | 0.078886 | 0.073618 | -61.8231 | 59.4676 | 59.563 | 59.699 | -61.6806 | 0.098133 | -0.011326 | 2.7837 | 0.10651 | 0.008378 | -0.20263 | -0.38113 | 0.12669 | -0.26141 | 61.8861 | -0.015896 | -0.14259 | -0.16599 | -0.030012 | 121.5249 | 121.3336 | 121.1551 | 61.7903 | -121.4381 | 121.2748 | 121.3703 | 121.5062 | 61.8809 | -121.4096
216.4219 | 121.7056 | -61.8073 | 59.7198 | 0.002213 | -0.026882 | 0.00050001 | 0.055799 | -0.0044507 | 0.052247 | -0.011751 | -0.00094006 | -0.0014444 | -0.0033051 | 0.013152 | -0.0075355 | -59.0189 | -0.003172 | -61.6962 | 59.7177 | 59.5218 | 59.3479 | -61.7045 | 0.083464 | 0.06904 | -61.8369 | 59.4722 | 59.5676 | 59.6944 | -61.6989 | 0.10271 | -0.002171 | 2.7883 | 0.11109 | 0.008378 | -0.19805 | -0.37197 | 0.10838 | -0.24768 | 61.8907 | -0.029632 | -0.13801 | -0.15226 | -0.025436 | 121.5249 | 121.329 | 121.1551 | 61.8041 | -121.4244 | 121.2794 | 121.3748 | 121.5017 | 61.8763 | -121.4187
218.1094 | 121.7972 | -61.6608 | 59.848 | 0.002213 | -0.026882 | 0.00050001 | 0.055799 | -0.0044507 | 0.052247 | 0.00351 | -0.00094006 | -0.0012306 | -0.0030915 | 0.013365 | -0.0073219 | -59.1105 | -0.016908 | -61.7007 | 59.7177 | 59.5264 | 59.3479 | -61.7091 | 0.069728 | 0.073618 | -61.8323 | 59.4676 | 59.5676 | 59.6944 | -61.6851 | -0.048351 | -0.13034 | 2.5502 | -0.039973 | 0.008378 | -0.32164 | -0.50015 | -0.02437 | -0.38043 | 61.7305 | -0.17154 | -0.14717 | -0.28043 | -0.15361 | 121.3784 | 121.1871 | 121.0086 | 61.6439 | -121.5571 | 121.1284 | 121.2284 | 121.3552 | 61.7344 | -121.5332
219.8594 | 121.7239 | -61.702 | 59.8114 | 0.002213 | -0.026882 | 0.00071361 | 0.056013 | -0.0046643 | 0.052461 | -0.0041205 | -0.0011537 | -0.0012306 | -0.0033051 | 0.013152 | -0.0073219 | -59.0418 | -0.016908 | -61.7053 | 59.7223 | 59.5218 | 59.357 | -61.7 | 0.074307 | 0.064461 | -61.8277 | 59.4722 | 59.5676 | 59.6853 | -61.6897 | 0.002004 | -0.089144 | 2.6601 | -0.003353 | -0.005357 | -0.2896 | -0.45437 | 0.01225 | -0.33923 | 61.7763 | -0.12576 | -0.13801 | -0.24381 | -0.12614 | 121.4242 | 121.2238 | 121.059 | 61.6851 | -121.5114 | 121.1741 | 121.2696 | 121.3872 | 61.7664 | -121.5011
221.5469 | 121.8246 | -61.615 | 59.8251 | 0.002213 | -0.026882 | 0.00092741 | 0.056013 | -0.0046643 | 0.052461 | -0.011751 | -0.0011537 | -0.0012306 | -0.0030915 | 0.013152 | -0.0073219 | -59.1334 | -0.016908 | -61.7007 | 59.7223 | 59.5264 | 59.3525 | -61.7045 | 0.069728 | 0.064461 | -61.8231 | 59.4722 | 59.5722 | 59.6944 | -61.6943 | -0.089549 | -0.10288 | 2.4816 | -0.08575 | 0.003799 | -0.29876 | -0.47268 | -0.079304 | -0.35296 | 61.6847 | -0.20816 | -0.12885 | -0.25297 | -0.13072 | 121.3372 | 121.1414 | 120.9674 | 61.5981 | -121.5297 | 121.0872 | 121.1872 | 121.3094 | 61.6795 | -121.5194
223.2812 | 121.7194 | -61.7477 | 59.8251 | 0.002213 | -0.027096 | 0.00092741 | 0.055585 | -0.0046643 | 0.052247 | 0.00351 | -0.0011537 | -0.0014444 | -0.0030915 | 0.013152 | -0.0073219 | -59.051 | -0.016908 | -61.7053 | 59.7177 | 59.5264 | 59.357 | -61.7 | 0.06515 | 0.064461 | -61.8323 | 59.4767 | 59.5767 | 59.6853 | -61.6851 | 0.047781 | -0.10746 | 2.6967 | 0.042424 | -0.005357 | -0.29876 | -0.4681 | 0.062605 | -0.34839 | 61.8129 | -0.084562 | -0.14717 | -0.24839 | -0.13988 | 121.4654 | 121.2741 | 121.1048 | 61.7308 | -121.5251 | 121.2245 | 121.3245 | 121.433 | 61.8122 | -121.5103
225.0312 | 121.7789 | -61.6653 | 59.816 | 0.009844 | -0.027096 | 0.00071361 | 0.055799 | -0.0044507 | 0.052033 | 0.00351 | -0.0011537 | -0.0014444 | -0.0035187 | 0.013365 | -0.0073219 | -59.1014 | -0.012329 | -61.7053 | 59.7177 | 59.5264 | 59.3525 | -61.7045 | 0.074307 | 0.06904 | -61.8231 | 59.4676 | 59.5676 | 59.6853 | -61.6851 | -0.039195 | -0.098301 | 2.564 | -0.039974 | -0.000779 | -0.2896 | -0.46352 | -0.019793 | -0.34839 | 61.7397 | -0.1578 | -0.13801 | -0.24839 | -0.13072 | 121.383 | 121.1917 | 121.0178 | 61.653 | -121.5205 | 121.1329 | 121.2329 | 121.3506 | 61.7344 | -121.5011
226.7031 | 121.7468 | -61.8073 | 59.6924 | -0.013049 | -0.027096 | 0.00071361 | 0.055799 | -0.0044507 | 0.052247 | -0.0041205 | -0.0013673 | -0.001017 | -0.0030915 | 0.013152 | -0.0071083 | -59.0418 | -0.007751 | -61.7007 | 59.7177 | 59.531 | 59.3525 | -61.7091 | 0.078886 | 0.073618 | -61.8231 | 59.4676 | 59.5722 | 59.6898 | -61.6851 | 0.098133 | 0.025295 | 2.7654 | 0.10651 | 0.008378 | -0.16143 | -0.33993 | 0.12211 | -0.22479 | 61.8861 | -0.015896 | -0.13801 | -0.12022 | -0.002549 | 121.5249 | 121.3382 | 121.1597 | 61.7995 | -121.4015 | 121.2748 | 121.3794 | 121.4971 | 61.8809 | -121.3775
228.4531 | 121.7743 | -61.6653 | 59.816 | -0.005418 | -0.02731 | 0.00071361 | 0.055799 | -0.0046643 | 0.052247 | 0.00351 | -0.00094006 | -0.0012306 | -0.0033051 | 0.013365 | -0.0075355 | -59.1014 | -0.016908 | -61.7053 | 59.7131 | 59.5172 | 59.357 | -61.7045 | 0.069728 | 0.064461 | -61.8323 | 59.4676 | 59.5722 | 59.6898 | -61.6851 | -0.039195 | -0.10288 | 2.564 | -0.039974 | -0.000779 | -0.29876 | -0.45895 | -0.019793 | -0.34839 | 61.7351 | -0.16696 | -0.14717 | -0.24381 | -0.12615 | 121.3784 | 121.1826 | 121.0224 | 61.6484 | -121.5205 | 121.1329 | 121.2375 | 121.3552 | 61.7298 | -121.5011
230.125 | 121.7377 | -61.7889 | 59.697 | 0.009844 | -0.026882 | 0.00050001 | 0.055585 | -0.0046643 | 0.052247 | -0.0041205 | -0.00094006 | -0.001017 | -0.0033051 | 0.013579 | -0.0073219 | -59.0418 | -0.007751 | -61.7007 | 59.7131 | 59.5218 | 59.357 | -61.7091 | 0.069728 | 0.064461 | -61.8323 | 59.4676 | 59.5722 | 59.6898 | -61.6851 | 0.079822 | 0.01614 | 2.7471 | 0.0882 | 0.008378 | -0.17516 | -0.33993 | 0.1038 | -0.22937 | 61.8587 | -0.043364 | -0.14717 | -0.12479 | -0.007126 | 121.502 | 121.3107 | 121.146 | 61.7812 | -121.4061 | 121.2565 | 121.3611 | 121.4788 | 61.8534 | -121.3821
231.8594 | 121.7834 | -61.6974 | 59.7656 | 0.002213 | -0.02731 | 0.00071361 | 0.055585 | -0.0048779 | 0.052033 | -0.011751 | -0.0011537 | -0.0014444 | -0.0035187 | 0.012938 | -0.0077491 | -59.0922 | -0.003172 | -61.7053 | 59.7223 | 59.5218 | 59.3616 | -61.6954 | 0.078886 | 0.06904 | -61.8277 | 59.4676 | 59.5722 | 59.6944 | -61.6851 | 0.002006 | -0.043368 | 2.6052 | -0.00793 | -0.009936 | -0.24383 | -0.40401 | 0.012251 | -0.29803 | 61.7763 | -0.13034 | -0.14259 | -0.19346 | -0.071212 | 121.4196 | 121.2192 | 121.059 | 61.6942 | -121.461 | 121.165 | 121.2696 | 121.3918 | 61.7664 | -121.4508
233.5938 | 121.788 | -61.6837 | 59.7839 | 0.002213 | -0.026882 | 0.00092741 | 0.055799 | -0.0046643 | 0.052247 | 0.00351 | -0.00094006 | -0.0012306 | -0.0033051 | 0.013152 | -0.0075355 | -59.1197 | -0.007751 | -61.7145 | 59.7177 | 59.5264 | 59.3525 | -61.7 | 0.074307 | 0.059882 | -61.8231 | 59.4676 | 59.5722 | 59.699 | -61.6943 | -0.016306 | -0.066258 | 2.564 | -0.030819 | -0.014513 | -0.25756 | -0.43148 | -0.010639 | -0.31634 | 61.758 | -0.13949 | -0.12885 | -0.21177 | -0.084944 | 121.4013 | 121.21 | 121.0361 | 61.6759 | -121.4839 | 121.1512 | 121.2558 | 121.3826 | 61.7435 | -121.4782
235.3438 | 121.7468 | -61.7615 | 59.7427 | -0.005418 | -0.027096 | 0.00092741 | 0.055585 | -0.0044507 | 0.052033 | -0.011751 | -0.0011537 | -0.0014444 | -0.0039461 | 0.013365 | -0.0073219 | -59.0189 | -0.016908 | -61.7145 | 59.7131 | 59.5264 | 59.357 | -61.7091 | 0.078886 | 0.06904 | -61.8231 | 59.4722 | 59.5767 | 59.6898 | -61.6897 | 0.052357 | -0.029637 | 2.7425 | 0.047001 | -0.005356 | -0.21636 | -0.38571 | 0.07176 | -0.27057 | 61.8404 | -0.061672 | -0.13343 | -0.16599 | -0.052903 | 121.4746 | 121.2879 | 121.1185 | 61.7446 | -121.4519 | 121.2336 | 121.3382 | 121.4513 | 61.8305 | -121.4325
237.0469 | 121.6782 | -61.8256 | 59.729 | 0.002213 | -0.027096 | 0.00071361 | 0.055372 | -0.0046643 | 0.052247 | -0.0041205 | -0.0011537 | -0.00080338 | -0.0037325 | 0.013793 | -0.0075355 | -59.0235 | -0.007751 | -61.7145 | 59.7223 | 59.5126 | 59.357 | -61.7091 | 0.078886 | 0.064461 | -61.8231 | 59.4676 | 59.5676 | 59.6944 | -61.6851 | 0.11644 | -0.006747 | 2.802 | 0.11109 | -0.005356 | -0.21636 | -0.37197 | 0.14043 | -0.26141 | 61.9044 | 0.002415 | -0.13801 | -0.16142 | -0.034591 | 121.5478 | 121.3382 | 121.1826 | 61.8178 | -121.4381 | 121.2932 | 121.3932 | 121.52 | 61.89 | -121.4141
238.7969 | 121.7285 | -61.7981 | 59.7015 | -0.005418 | -0.02731 | 0.00071361 | 0.055585 | -0.0046643 | 0.052033 | -0.0041205 | -0.0011537 | -0.001658 | -0.0037325 | 0.013579 | -0.0079629 | -59.0327 | -0.012329 | -61.7099 | 59.7131 | 59.5218 | 59.3525 | -61.7 | 0.078886 | 0.059882 | -61.8277 | 59.4722 | 59.5676 | 59.6944 | -61.6897 | 0.098135 | 0.011562 | 2.7654 | 0.0882 | -0.009935 | -0.17974 | -0.34908 | 0.10838 | -0.22937 | 61.877 | -0.02963 | -0.13801 | -0.13395 | -0.007125 | 121.5112 | 121.3199 | 121.1506 | 61.7858 | -121.4015 | 121.2703 | 121.3657 | 121.4925 | 61.858 | -121.3913
240.5469 | 121.8292 | -61.6516 | 59.8343 | -0.013049 | -0.027096 | 0.00092741 | 0.055372 | -0.0046643 | 0.05182 | 0.00351 | -0.0011537 | -0.0014444 | -0.0030915 | 0.012938 | -0.0073219 | -59.138 | -0.007751 | -61.7191 | 59.7177 | 59.5218 | 59.3616 | -61.7091 | 0.074307 | 0.06904 | -61.8231 | 59.4722 | 59.563 | 59.6898 | -61.6897 | -0.057507 | -0.11661 | 2.5136 | -0.067442 | -0.009935 | -0.31249 | -0.47268 | -0.038104 | -0.36212 | 61.7259 | -0.17154 | -0.13343 | -0.27128 | -0.14446 | 121.3693 | 121.1734 | 121.0132 | 61.6439 | -121.5434 | 121.1238 | 121.2146 | 121.3414 | 61.7207 | -121.524
242.2344 | 121.8246 | -61.7432 | 59.7107 | 0.002213 | -0.026882 | 0.00050001 | 0.055799 | -0.0046643 | 0.052247 | -0.0041205 | -0.0011537 | -0.001017 | -0.0033051 | 0.013579 | -0.0077491 | -59.0693 | -0.007751 | -61.7282 | 59.7177 | 59.531 | 59.3525 | -61.7091 | 0.069728 | 0.064461 | -61.8231 | 59.4676 | 59.5722 | 59.6898 | -61.6897 | 0.034046 | 0.006985 | 2.6739 | 0.014955 | -0.019091 | -0.17974 | -0.35824 | 0.053449 | -0.2431 | 61.8129 | -0.079983 | -0.13343 | -0.13853 | -0.020859 | 121.4608 | 121.2741 | 121.0956 | 61.7354 | -121.4198 | 121.2108 | 121.3153 | 121.433 | 61.8076 | -121.4004
243.9844 | 121.7056 | -61.7065 | 59.8297 | -0.005418 | -0.027737 | 0.00071361 | 0.055585 | -0.0048779 | 0.052247 | -0.0041205 | -0.00094006 | -0.0014444 | -0.0035187 | 0.013579 | -0.0077491 | -59.0785 | -0.012329 | -61.7191 | 59.7177 | 59.5218 | 59.3525 | -61.7091 | 0.06515 | 0.059882 | -61.8277 | 59.4676 | 59.5722 | 59.6898 | -61.6897 | -0.002575 | -0.11203 | 2.6281 | -0.01251 | -0.009935 | -0.30791 | -0.47726 | 0.016828 | -0.36212 | 61.7717 | -0.12118 | -0.13801 | -0.25754 | -0.13988 | 121.4242 | 121.2283 | 121.059 | 61.6942 | -121.5388 | 121.1741 | 121.2787 | 121.3964 | 61.7664 | -121.5194
245.7344 | 121.7056 | -61.8118 | 59.7427 | -0.005418 | -0.02731 | 0.00071361 | 0.056227 | -0.0046643 | 0.052247 | 0.00351 | -0.00094006 | -0.0012306 | -0.0035187 | 0.013152 | -0.0077491 | -59.0189 | -0.007751 | -61.7236 | 59.7177 | 59.5264 | 59.3525 | -61.7 | 0.074307 | 0.064461 | -61.8323 | 59.4676 | 59.563 | 59.6944 | -61.6897 | 0.11187 | -0.025059 | 2.7929 | 0.088198 | -0.02367 | -0.21636 | -0.39028 | 0.12211 | -0.27515 | 61.8861 | -0.020475 | -0.14259 | -0.17973 | -0.048324 | 121.5295 | 121.3382 | 121.1643 | 61.8041 | -121.4427 | 121.2794 | 121.3748 | 121.5062 | 61.8763 | -121.4325
247.4219 | 121.7148 | -61.8256 | 59.7198 | 0.002213 | -0.027523 | 0.00050001 | 0.055585 | -0.0044507 | 0.05182 | -0.011751 | -0.00094006 | -0.001017 | -0.0033051 | 0.013365 | -0.0075355 | -59.0189 | -0.007751 | -61.7191 | 59.7177 | 59.5264 | 59.3525 | -61.7 | 0.074307 | 0.064461 | -61.8323 | 59.4722 | 59.5722 | 59.6898 | -61.6851 | 0.1256 | -0.002171 | 2.8066 | 0.10651 | -0.019092 | -0.19347 | -0.3674 | 0.14043 | -0.24768 | 61.8999 | -0.006742 | -0.14717 | -0.14768 | -0.030015 | 121.5432 | 121.3519 | 121.178 | 61.8178 | -121.4198 | 121.2977 | 121.3977 | 121.5154 | 61.89 | -121.405
249.1562 | 121.6965 | -61.8439 | 59.729 | 0.009844 | -0.02731 | 0.00050001 | 0.055585 | -0.0048779 | 0.05182 | -0.0041205 | -0.00094006 | -0.0012306 | -0.0030915 | 0.013152 | -0.0073219 | -59.0235 | -0.007751 | -61.7145 | 59.7131 | 59.5218 | 59.357 | -61.7045 | 0.069728 | 0.06904 | -61.8186 | 59.463 | 59.5722 | 59.6898 | -61.6851 | 0.13933 | -0.015904 | 2.8203 | 0.1294 | -0.009935 | -0.20721 | -0.37197 | 0.15874 | -0.26599 | 61.9136 | 0.025304 | -0.13343 | -0.15684 | -0.03917 | 121.557 | 121.3657 | 121.2009 | 61.8361 | -121.4335 | 121.3069 | 121.416 | 121.5337 | 61.9129 | -121.4141
250.8438 | 121.8475 | -61.6425 | 59.8022 | 0.009844 | -0.027737 | 0.00050001 | 0.055585 | -0.0048779 | 0.052461 | -0.011751 | -0.00094006 | -0.0012306 | -0.0037325 | 0.013152 | -0.0073219 | -59.1334 | -0.012329 | -61.7053 | 59.7223 | 59.5218 | 59.357 | -61.7091 | 0.069728 | 0.055303 | -61.8231 | 59.463 | 59.5722 | 59.6898 | -61.6897 | -0.066662 | -0.079989 | 2.509 | -0.062862 | 0.0038 | -0.28045 | -0.44521 | -0.047259 | -0.33923 | 61.7122 | -0.18069 | -0.13343 | -0.23008 | -0.11241 | 121.3647 | 121.1643 | 120.9995 | 61.6301 | -121.5114 | 121.1055 | 121.2146 | 121.3323 | 61.6978 | -121.492
252.5938 | 121.7056 | -61.8073 | 59.7153 | -0.005418 | -0.027096 | 0.00028641 | 0.055585 | -0.0044507 | 0.052247 | -0.0041205 | -0.0011537 | -0.001017 | -0.0035187 | 0.013579 | -0.0075355 | -59.0235 | -0.012329 | -61.7145 | 59.7223 | 59.5264 | 59.3479 | -61.7045 | 0.083464 | 0.073618 | -61.8231 | 59.4722 | 59.5676 | 59.6853 | -61.6897 | 0.10271 | 0.006986 | 2.7837 | 0.092777 | -0.009935 | -0.18889 | -0.3674 | 0.11754 | -0.2431 | 61.8907 | -0.015896 | -0.13343 | -0.14768 | -0.030015 | 121.5295 | 121.3336 | 121.1551 | 61.7949 | -121.4198 | 121.2794 | 121.3748 | 121.4925 | 61.8809 | -121.405
254.3281 | 121.8292 | -61.7523 | 59.7107 | -0.005418 | -0.027096 | 0.00092741 | 0.056013 | -0.0044507 | 0.052033 | 0.00351 | -0.00094006 | -0.0014444 | -0.0033051 | 0.013365 | -0.0075355 | -59.0556 | -0.007751 | -61.7053 | 59.7223 | 59.531 | 59.3525 | -61.7091 | 0.078886 | 0.06904 | -61.8277 | 59.4676 | 59.5722 | 59.699 | -61.6943 | 0.043201 | 0.011564 | 2.6967 | 0.047001 | 0.0038 | -0.17974 | -0.35824 | 0.058025 | -0.2431 | 61.8312 | -0.075407 | -0.13343 | -0.13853 | -0.011701 | 121.4746 | 121.2833 | 121.1048 | 61.7446 | -121.4198 | 121.2199 | 121.3245 | 121.4513 | 61.8214 | -121.405
256 | 121.8384 | -61.6379 | 59.8297 | -0.005418 | -0.027523 | 0.00050001 | 0.055799 | -0.0046643 | 0.052247 | -0.0041205 | -0.00072626 | -0.0012306 | -0.0035187 | 0.013365 | -0.0075355 | -59.1426 | -0.007751 | -61.7053 | 59.7223 | 59.5264 | 59.3525 | -61.7045 | 0.06515 | 0.064461 | -61.8231 | 59.4676 | 59.5722 | 59.6898 | -61.6943 | -0.066661 | -0.10746 | 2.4953 | -0.06744 | -0.000779 | -0.30333 | -0.47726 | -0.056416 | -0.36212 | 61.703 | -0.18527 | -0.12885 | -0.25754 | -0.13988 | 121.3601 | 121.1643 | 120.9903 | 61.6301 | -121.5343 | 121.1055 | 121.21 | 121.3277 | 61.7023 | -121.524
257.7344 | 121.6919 | -61.6974 | 59.8526 | -0.005418 | -0.027523 | 0.00050001 | 0.055799 | -0.0046643 | 0.052247 | -0.0041205 | -0.00094006 | -0.0014444 | -0.0033051 | 0.013579 | -0.0075355 | -59.1197 | -0.012329 | -61.7099 | 59.7085 | 59.5264 | 59.3525 | -61.7045 | 0.069728 | 0.059882 | -61.8231 | 59.4676 | 59.5722 | 59.6944 | -61.6851 | -0.007151 | -0.14408 | 2.5777 | -0.012508 | -0.005357 | -0.32622 | -0.50015 | 0.012251 | -0.38501 | 61.7671 | -0.12576 | -0.13801 | -0.28043 | -0.15819 | 121.4059 | 121.2238 | 121.0498 | 61.6851 | -121.5571 | 121.165 | 121.2696 | 121.3918 | 61.7573 | -121.5377
259.4844 | 121.7743 | -61.6882 | 59.7565 | -0.013049 | -0.02731 | 0.00071361 | 0.055585 | -0.0046643 | 0.052033 | -0.011751 | -0.0013673 | -0.0012306 | -0.0037325 | 0.013152 | -0.0075355 | -59.1471 | -0.012329 | -61.7007 | 59.7177 | 59.5218 | 59.357 | -61.7091 | 0.06515 | 0.059882 | -61.8277 | 59.463 | 59.5676 | 59.699 | -61.6897 | -0.020886 | -0.038792 | 2.5411 | -0.012508 | 0.008378 | -0.23467 | -0.39944 | -0.001483 | -0.29346 | 61.7534 | -0.13949 | -0.13801 | -0.18888 | -0.057478 | 121.4059 | 121.21 | 121.0453 | 61.6759 | -121.4656 | 121.1512 | 121.2558 | 121.3872 | 61.7481 | -121.4462
261.1719 | 121.8246 | -61.7523 | 59.7107 | -0.005418 | -0.027737 | 0.00071361 | 0.055799 | -0.0044507 | 0.05182 | -0.019381 | -0.00094006 | -0.001017 | -0.0037325 | 0.013579 | -0.0079629 | -59.1059 | -0.007751 | -61.7145 | 59.7131 | 59.5218 | 59.3616 | -61.7 | 0.078886 | 0.06904 | -61.8277 | 59.4722 | 59.5722 | 59.6944 | -61.6897 | 0.052358 | 0.002407 | 2.6464 | 0.037845 | -0.014513 | -0.18889 | -0.34908 | 0.062604 | -0.23852 | 61.8312 | -0.075407 | -0.13801 | -0.13853 | -0.01628 | 121.4654 | 121.2741 | 121.1139 | 61.7446 | -121.4107 | 121.2245 | 121.3245 | 121.4467 | 61.8214 | -121.4004
262.9219 | 121.6873 | -61.7157 | 59.8434 | -0.005418 | -0.027523 | 0.00050001 | 0.055372 | -0.0046643 | 0.052247 | -0.0041205 | -0.00072626 | -0.0014444 | -0.0030915 | 0.013579 | -0.0079629 | -59.1197 | -0.007751 | -61.7099 | 59.7131 | 59.5218 | 59.357 | -61.7 | 0.069728 | 0.064461 | -61.8231 | 59.4676 | 59.5722 | 59.6853 | -61.6897 | 0.015737 | -0.13035 | 2.596 | 0.005802 | -0.009935 | -0.32165 | -0.48641 | 0.025983 | -0.37585 | 61.7854 | -0.10745 | -0.13343 | -0.27128 | -0.15819 | 121.4288 | 121.2375 | 121.0727 | 61.7079 | -121.5434 | 121.1833 | 121.2879 | 121.401 | 61.7802 | -121.5332
264.6719 | 121.6919 | -61.6699 | 59.8389 | 0.002213 | -0.027737 | 0.00071361 | 0.055799 | -0.0046643 | 0.052247 | -0.0041205 | -0.0011537 | -0.0014444 | -0.0037325 | 0.013365 | -0.0077491 | -59.1243 | -0.003172 | -61.7145 | 59.7131 | 59.5218 | 59.3525 | -61.7045 | 0.074307 | 0.059882 | -61.8277 | 59.4676 | 59.5676 | 59.6898 | -61.6943 | -0.034617 | -0.12577 | 2.5457 | -0.044552 | -0.009935 | -0.31707 | -0.48641 | -0.024372 | -0.37128 | 61.7442 | -0.1578 | -0.13343 | -0.27128 | -0.14903 | 121.383 | 121.1917 | 121.0224 | 61.6668 | -121.5434 | 121.1375 | 121.2375 | 121.3598 | 61.7298 | -121.5332
266.3594 | 121.7743 | -61.7111 | 59.7702 | -0.005418 | -0.027737 | 0.00071361 | 0.055585 | -0.0044507 | 0.052033 | -0.0041205 | -0.00072626 | -0.001658 | -0.0037325 | 0.013365 | -0.0075355 | -59.1609 | -0.007751 | -61.7099 | 59.7177 | 59.5172 | 59.3525 | -61.6954 | 0.069728 | 0.055303 | -61.8186 | 59.463 | 59.5676 | 59.6898 | -61.6851 | 0.015739 | -0.052525 | 2.5502 | 0.001225 | -0.014514 | -0.25298 | -0.41775 | 0.025984 | -0.30719 | 61.7808 | -0.10745 | -0.13343 | -0.20261 | -0.080369 | 121.4288 | 121.2283 | 121.0636 | 61.7034 | -121.4656 | 121.1741 | 121.2787 | 121.401 | 61.7664 | -121.4553
268.1094 | 121.7743 | -61.6974 | 59.761 | -0.005418 | -0.027737 | 0.00071361 | 0.055585 | -0.0044507 | 0.051606 | -0.011751 | -0.0013673 | -0.0012306 | -0.0035187 | 0.013579 | -0.0073219 | -59.1517 | -0.012329 | -61.7007 | 59.7177 | 59.5218 | 59.357 | -61.7091 | 0.078886 | 0.059882 | -61.8323 | 59.4676 | 59.5722 | 59.6853 | -61.6943 | -0.01173 | -0.043369 | 2.5457 | -0.003352 | 0.008378 | -0.23925 | -0.40402 | 0.003094 | -0.29346 | 61.7763 | -0.13492 | -0.13801 | -0.18888 | -0.075791 | 121.4151 | 121.2192 | 121.0544 | 61.6851 | -121.4702 | 121.165 | 121.2696 | 121.3826 | 61.7573 | -121.4553
269.7969 | 121.8384 | -61.6516 | 59.8114 | 0.009844 | -0.027523 | 0.00050001 | 0.055372 | -0.0044507 | 0.052033 | -0.0041205 | -0.00072626 | -0.001017 | -0.0035187 | 0.013579 | -0.0079629 | -59.1929 | -0.012329 | -61.7099 | 59.7085 | 59.5264 | 59.3525 | -61.7045 | 0.074307 | 0.055303 | -61.8231 | 59.4584 | 59.5722 | 59.6898 | -61.6851 | -0.052928 | -0.10288 | 2.4587 | -0.058285 | -0.005357 | -0.28502 | -0.45895 | -0.033526 | -0.35297 | 61.7259 | -0.17154 | -0.13801 | -0.23923 | -0.12157 | 121.3601 | 121.178 | 121.0041 | 61.6393 | -121.5159 | 121.11 | 121.2238 | 121.3414 | 61.7069 | -121.4965
271.5469 | 121.8109 | -61.6562 | 59.8206 | -0.005418 | -0.027737 | 0.00071361 | 0.055585 | -0.0046643 | 0.05182 | 0.00351 | -0.0011537 | -0.0012306 | -0.0030915 | 0.013579 | -0.0077491 | -59.1884 | -0.016908 | -61.7053 | 59.7177 | 59.5218 | 59.357 | -61.7 | 0.074307 | 0.055303 | -61.8277 | 59.4722 | 59.5722 | 59.6853 | -61.6851 | -0.043772 | -0.10288 | 2.4678 | -0.049129 | -0.005357 | -0.29876 | -0.46353 | -0.028948 | -0.34839 | 61.7305 | -0.17154 | -0.14259 | -0.24839 | -0.1353 | 121.3739 | 121.178 | 121.0132 | 61.6393 | -121.5205 | 121.1284 | 121.2284 | 121.3414 | 61.7115 | -121.5057
273.2812 | 121.7834 | -61.7157 | 59.7656 | -0.005418 | -0.027523 | 0.00028641 | 0.055585 | -0.0044507 | 0.05182 | -0.011751 | -0.0011537 | -0.001017 | -0.0030915 | 0.013365 | -0.0075355 | -59.1471 | -0.012329 | -61.6916 | 59.7177 | 59.5172 | 59.357 | -61.7045 | 0.074307 | 0.064461 | -61.8231 | 59.4584 | 59.5813 | 59.6944 | -61.6806 | 0.011159 | -0.047947 | 2.5686 | 0.024115 | 0.012956 | -0.2484 | -0.40859 | 0.03514 | -0.30719 | 61.79 | -0.10745 | -0.14259 | -0.1843 | -0.071212 | 121.4334 | 121.2329 | 121.0727 | 61.7034 | -121.4702 | 121.1741 | 121.297 | 121.4101 | 61.7802 | -121.4462
275.0312 | 121.843 | -61.6516 | 59.8114 | -0.005418 | -0.027951 | 0.00071361 | 0.055799 | -0.0046643 | 0.052033 | -0.0041205 | -0.00094006 | -0.0012306 | -0.0030915 | 0.013579 | -0.0077491 | -59.1929 | -0.016908 | -61.6824 | 59.7131 | 59.531 | 59.3616 | -61.7045 | 0.074307 | 0.055303 | -61.8277 | 59.4584 | 59.563 | 59.6853 | -61.6851 | -0.052928 | -0.098301 | 2.4587 | -0.030816 | 0.022112 | -0.28044 | -0.44979 | -0.033526 | -0.35297 | 61.7259 | -0.17611 | -0.14259 | -0.24839 | -0.12614 | 121.3647 | 121.1826 | 121.0132 | 61.6347 | -121.5159 | 121.11 | 121.2146 | 121.3369 | 61.7069 | -121.4965
276.7812 | 121.7972 | -61.7752 | 59.6832 | -0.005418 | -0.02731 | 0.00050001 | 0.056013 | -0.0044507 | 0.052033 | 0.00351 | -0.0013673 | -0.001017 | -0.0033051 | 0.013579 | -0.0077491 | -59.1014 | -0.007751 | -61.6962 | 59.7177 | 59.5264 | 59.357 | -61.7 | 0.074307 | 0.064461 | -61.8277 | 59.4676 | 59.5722 | 59.6807 | -61.6897 | 0.075247 | 0.03445 | 2.6738 | 0.079047 | 0.0038 | -0.15685 | -0.3262 | 0.085493 | -0.21564 | 61.8495 | -0.052518 | -0.13801 | -0.11106 | -0.002551 | 121.4929 | 121.3016 | 121.1322 | 61.7675 | -121.3832 | 121.2428 | 121.3474 | 121.4559 | 61.8397 | -121.3729
278.4531 | 121.7377 | -61.7249 | 59.7931 | -0.005418 | -0.027523 | 0.00071361 | 0.055372 | -0.0046643 | 0.05182 | -0.011751 | -0.0011537 | -0.0014444 | -0.0033051 | 0.013579 | -0.0075355 | -59.0968 | -0.012329 | -61.6824 | 59.7085 | 59.5264 | 59.3525 | -61.7183 | 0.074307 | 0.064461 | -61.8277 | 59.463 | 59.5676 | 59.6898 | -61.676 | 0.006578 | -0.084569 | 2.6281 | 0.042427 | 0.035849 | -0.26671 | -0.44064 | 0.048875 | -0.33008 | 61.7992 | -0.10287 | -0.15175 | -0.2255 | -0.10326 | 121.4334 | 121.2512 | 121.0773 | 61.7125 | -121.5114 | 121.1879 | 121.2924 | 121.4147 | 61.7893 | -121.4691
280.1875 | 121.7056 | -61.702 | 59.8297 | -0.005418 | -0.027737 | 0.00028641 | 0.055372 | -0.0042369 | 0.05182 | -0.0041205 | -0.00094006 | -0.001017 | -0.0037325 | 0.013793 | -0.0079629 | -59.1105 | -0.012329 | -61.6962 | 59.7131 | 59.5264 | 59.357 | -61.7045 | 0.06515 | 0.059882 | -61.8231 | 59.4584 | 59.563 | 59.699 | -61.6806 | -0.002574 | -0.11661 | 2.5914 | 0.005804 | 0.008378 | -0.30333 | -0.47268 | 0.021407 | -0.37128 | 61.7671 | -0.12118 | -0.14259 | -0.2667 | -0.13072 | 121.4151 | 121.2283 | 121.059 | 61.6896 | -121.5343 | 121.1604 | 121.265 | 121.401 | 61.7618 | -121.5103
281.9375 | 121.6919 | -61.702 | 59.816 | 0.002213 | -0.027737 | 0.00071361 | 0.055372 | -0.0046643 | 0.05182 | 0.01114 | -0.0013673 | -0.0012306 | -0.0033051 | 0.013579 | -0.0073219 | -59.1059 | -0.012329 | -61.7007 | 59.7177 | 59.5264 | 59.3616 | -61.7045 | 0.069728 | 0.059882 | -61.8277 | 59.4584 | 59.563 | 59.6898 | -61.6851 | -0.002574 | -0.098301 | 2.596 | 0.001225 | 0.003799 | -0.2896 | -0.45437 | 0.016828 | -0.35755 | 61.7717 | -0.12576 | -0.14259 | -0.25297 | -0.12615 | 121.4196 | 121.2283 | 121.0636 | 61.6896 | -121.5205 | 121.1604 | 121.265 | 121.3918 | 61.7618 | -121.5011
283.6875 | 121.701 | -61.7981 | 59.7198 | -0.005418 | -0.027737 | 7.2612e-05 | 0.055585 | -0.0044507 | 0.05182 | -0.0041205 | -0.00094006 | -0.0014444 | -0.0035187 | 0.014006 | -0.0077491 | -59.0785 | -0.016908 | -61.687 | 59.7177 | 59.5264 | 59.357 | -61.7091 | 0.074307 | 0.059882 | -61.8231 | 59.463 | 59.563 | 59.6853 | -61.6806 | 0.088978 | -0.002171 | 2.7196 | 0.11109 | 0.022113 | -0.19347 | -0.36282 | 0.11754 | -0.25684 | 61.8724 | -0.025051 | -0.14259 | -0.15684 | -0.034593 | 121.5158 | 121.3245 | 121.1551 | 61.7812 | -121.429 | 121.2611 | 121.3611 | 121.4834 | 61.858 | -121.4004
285.375 | 121.7697 | -61.702 | 59.7702 | -0.005418 | -0.027951 | 0.00050001 | 0.055585 | -0.0046643 | 0.051606 | -0.011751 | -0.00094006 | -0.0012306 | -0.0030915 | 0.013579 | -0.0077491 | -59.1426 | 0.001407 | -61.6916 | 59.7177 | 59.5264 | 59.3616 | -61.7045 | 0.074307 | 0.059882 | -61.8231 | 59.463 | 59.5676 | 59.6944 | -61.676 | -0.002574 | -0.052525 | 2.5594 | 0.010382 | 0.012956 | -0.24383 | -0.40859 | 0.025986 | -0.30719 | 61.7763 | -0.12118 | -0.14717 | -0.20261 | -0.07579 | 121.4196 | 121.2283 | 121.0636 | 61.7034 | -121.4747 | 121.165 | 121.2696 | 121.3964 | 61.7618 | -121.4462
287.1406 | 121.7651 | -61.7889 | 59.7153 | -0.013049 | -0.028164 | 0.00050001 | 0.055372 | -0.0046643 | 0.052033 | -0.0041205 | -0.0013673 | -0.0012306 | -0.0035187 | 0.013793 | -0.0077491 | -59.0922 | -0.007751 | -61.6916 | 59.7177 | 59.531 | 59.3616 | -61.7091 | 0.074307 | 0.059882 | -61.814 | 59.4676 | 59.5722 | 59.6853 | -61.6851 | 0.079822 | 0.002407 | 2.6967 | 0.097357 | 0.017535 | -0.18431 | -0.35366 | 0.1038 | -0.24768 | 61.8632 | -0.02505 | -0.12885 | -0.1431 | -0.030015 | 121.5066 | 121.3199 | 121.1506 | 61.7812 | -121.4244 | 121.2565 | 121.3611 | 121.4742 | 61.8488 | -121.4004
288.8281 | 121.7148 | -61.7294 | 59.8114 | 0.002213 | -0.027737 | 0.00071361 | 0.055585 | -0.0048779 | 0.052033 | -0.011751 | -0.00072626 | -0.0012306 | -0.0037325 | 0.013579 | -0.0075355 | -59.1059 | -0.016908 | -61.687 | 59.7177 | 59.5172 | 59.357 | -61.7045 | 0.074307 | 0.064461 | -61.8186 | 59.463 | 59.563 | 59.6898 | -61.6897 | 0.024892 | -0.093723 | 2.6235 | 0.042426 | 0.017534 | -0.29418 | -0.45437 | 0.039716 | -0.34839 | 61.8037 | -0.089137 | -0.12885 | -0.24839 | -0.12157 | 121.4471 | 121.2467 | 121.0865 | 61.7125 | -121.5159 | 121.1924 | 121.2924 | 121.4193 | 61.7939 | -121.5011
290.5781 | 121.7789 | -61.7065 | 59.7519 | -0.005418 | -0.027951 | 0.00092741 | 0.055585 | -0.0048779 | 0.05182 | 0.00351 | -0.0011537 | -0.0012306 | -0.0039461 | 0.013365 | -0.0075355 | -59.1426 | -0.012329 | -61.6916 | 59.7223 | 59.5264 | 59.3616 | -61.7 | 0.078886 | 0.059882 | -61.8231 | 59.4676 | 59.5676 | 59.6853 | -61.6851 | 0.006582 | -0.029635 | 2.564 | 0.01496 | 0.008378 | -0.22551 | -0.39028 | 0.021406 | -0.2843 | 61.7854 | -0.1166 | -0.13801 | -0.1843 | -0.066636 | 121.4288 | 121.2329 | 121.0682 | 61.6942 | -121.4519 | 121.1741 | 121.2741 | 121.3918 | 61.7664 | -121.437
292.3281 | 121.7697 | -61.702 | 59.7702 | -0.013049 | -0.027737 | 0.00050001 | 0.055585 | -0.0044507 | 0.05182 | -0.019381 | -0.0015809 | -0.0012306 | -0.0035187 | 0.013579 | -0.0075355 | -59.1746 | -0.016908 | -61.6962 | 59.7131 | 59.5218 | 59.3616 | -61.7091 | 0.078886 | 0.059882 | -61.8231 | 59.4676 | 59.5722 | 59.6898 | -61.6851 | -0.007153 | -0.057103 | 2.5273 | 0.005804 | 0.012957 | -0.2484 | -0.40859 | 0.016828 | -0.30261 | 61.7809 | -0.12118 | -0.13801 | -0.19804 | -0.080369 | 121.4151 | 121.2238 | 121.0636 | 61.6851 | -121.4793 | 121.1696 | 121.2741 | 121.3918 | 61.7618 | -121.4553
294 | 121.6827 | -61.7111 | 59.8389 | -0.005418 | -0.028164 | 0.00050001 | 0.055585 | -0.0044507 | 0.052033 | -0.011751 | -0.00094006 | -0.0012306 | -0.0035187 | 0.014006 | -0.0077491 | -59.1151 | -0.012329 | -61.6916 | 59.7177 | 59.5264 | 59.3616 | -61.7091 | 0.078886 | 0.059882 | -61.8186 | 59.463 | 59.5676 | 59.6898 | -61.6943 | 0.002003 | -0.12119 | 2.596 | 0.019538 | 0.017535 | -0.31249 | -0.47726 | 0.016827 | -0.37586 | 61.79 | -0.10745 | -0.12427 | -0.27128 | -0.14903 | 121.4288 | 121.2375 | 121.0727 | 61.6988 | -121.548 | 121.1741 | 121.2787 | 121.401 | 61.771 | -121.5332
295.7344 | 121.7239 | -61.7111 | 59.7656 | -0.005418 | -0.027737 | 0.00071361 | 0.055372 | -0.0046643 | 0.05182 | -0.0041205 | -0.0011537 | -0.0014444 | -0.0035187 | 0.013579 | -0.0075355 | -59.0968 | -0.007751 | -61.6916 | 59.7177 | 59.5218 | 59.357 | -61.7045 | 0.078886 | 0.06904 | -61.8231 | 59.4676 | 59.5722 | 59.6853 | -61.6806 | 0.006582 | -0.047947 | 2.6143 | 0.019538 | 0.012956 | -0.24383 | -0.40859 | 0.030563 | -0.29803 | 61.79 | -0.11203 | -0.14259 | -0.19346 | -0.080369 | 121.4288 | 121.2329 | 121.0682 | 61.7034 | -121.4702 | 121.1787 | 121.2833 | 121.3964 | 61.7802 | -121.4462
297.4219 | 121.6827 | -61.702 | 59.848 | 0.002213 | -0.027951 | 0.00092741 | 0.055158 | -0.0048779 | 0.051606 | -0.0041205 | -0.0013673 | -0.0014444 | -0.0035187 | 0.013793 | -0.0075355 | -59.1151 | -0.012329 | -61.6916 | 59.7177 | 59.5264 | 59.357 | -61.7045 | 0.074307 | 0.059882 | -61.8186 | 59.4676 | 59.5676 | 59.6807 | -61.6897 | -0.002574 | -0.13034 | 2.5869 | 0.010382 | 0.012956 | -0.32164 | -0.49099 | 0.01225 | -0.38043 | 61.7763 | -0.1166 | -0.12885 | -0.28043 | -0.16734 | 121.4196 | 121.2283 | 121.059 | 61.6896 | -121.5526 | 121.1696 | 121.2696 | 121.3826 | 61.7618 | -121.5377
299.1562 | 121.7285 | -61.7294 | 59.7656 | 0.002213 | -0.027951 | 0.00092741 | 0.055372 | -0.0046643 | 0.051606 | -0.0041205 | -0.0013673 | -0.0014444 | -0.0033051 | 0.013793 | -0.0075355 | -59.0968 | -0.007751 | -61.6916 | 59.7039 | 59.5172 | 59.3616 | -61.7 | 0.069728 | 0.055303 | -61.8231 | 59.4676 | 59.5676 | 59.6944 | -61.6851 | 0.02947 | -0.061682 | 2.6326 | 0.037848 | 0.008378 | -0.2484 | -0.40401 | 0.044294 | -0.29803 | 61.7992 | -0.093716 | -0.13801 | -0.19804 | -0.071212 | 121.4334 | 121.2467 | 121.091 | 61.7217 | -121.4656 | 121.197 | 121.297 | 121.4238 | 61.7847 | -121.4508
300.9062 | 121.7743 | -61.6699 | 59.7794 | 0.002213 | -0.028164 | 0.00071361 | 0.055372 | -0.0046643 | 0.051606 | -0.011751 | -0.0011537 | -0.0014444 | -0.0035187 | 0.014006 | -0.0073219 | -59.1746 | -0.012329 | -61.6916 | 59.7131 | 59.5218 | 59.3616 | -61.7 | 0.069728 | 0.059882 | -61.8186 | 59.463 | 59.5676 | 59.6898 | -61.6897 | -0.030039 | -0.066258 | 2.4953 | -0.021661 | 0.008378 | -0.25756 | -0.41775 | -0.019793 | -0.31635 | 61.7396 | -0.14865 | -0.12885 | -0.21177 | -0.089524 | 121.383 | 121.1917 | 121.0315 | 61.6576 | -121.4793 | 121.1329 | 121.2375 | 121.3598 | 61.7298 | -121.4691
302.5938 | 121.7651 | -61.6974 | 59.7702 | -0.02068 | -0.027951 | 0.00071361 | 0.055585 | -0.0050917 | 0.051392 | -0.0041205 | -0.0011537 | -0.0014444 | -0.0035187 | 0.013793 | -0.0073219 | -59.1517 | -0.003172 | -61.6916 | 59.7177 | 59.5218 | 59.3525 | -61.7045 | 0.074307 | 0.064461 | -61.8231 | 59.4676 | 59.5676 | 59.6853 | -61.6897 | -0.007151 | -0.052525 | 2.5457 | 0.005805 | 0.012956 | -0.2484 | -0.41775 | 0.007673 | -0.30261 | 61.7717 | -0.12576 | -0.13343 | -0.20261 | -0.084947 | 121.4151 | 121.2192 | 121.0498 | 61.6942 | -121.4747 | 121.165 | 121.265 | 121.3826 | 61.7618 | -121.4599
304.3438 | 121.8201 | -61.6287 | 59.816 | 0.002213 | -0.027737 | 0.00071361 | 0.055585 | -0.0046643 | 0.051392 | -0.0041205 | -0.00094006 | -0.0012306 | -0.0033051 | 0.013579 | -0.0077491 | -59.1929 | 0.001407 | -61.687 | 59.7177 | 59.531 | 59.357 | -61.7 | 0.074307 | 0.059882 | -61.8231 | 59.4676 | 59.5722 | 59.6853 | -61.6943 | -0.071238 | -0.098301 | 2.4358 | -0.058282 | 0.012956 | -0.28502 | -0.45895 | -0.065571 | -0.34839 | 61.703 | -0.19442 | -0.12885 | -0.24381 | -0.13072 | 121.3464 | 121.1597 | 120.9858 | 61.6301 | -121.5159 | 121.0963 | 121.2009 | 121.314 | 61.6886 | -121.5103
306.0312 | 121.8109 | -61.7386 | 59.6878 | -0.005418 | -0.027951 | 0.00050001 | 0.055585 | -0.0048779 | 0.051179 | -0.0041205 | -0.0011537 | -0.001658 | -0.0030915 | 0.013793 | -0.0077491 | -59.1288 | 0.001407 | -61.687 | 59.7177 | 59.5218 | 59.3616 | -61.7045 | 0.083464 | 0.064461 | -61.8186 | 59.463 | 59.5676 | 59.6898 | -61.6943 | 0.034047 | 0.029873 | 2.6098 | 0.051581 | 0.017534 | -0.16601 | -0.32619 | 0.044292 | -0.22479 | 61.822 | -0.079982 | -0.12427 | -0.12022 | 0.002029 | 121.4563 | 121.2604 | 121.1002 | 61.74 | -121.3923 | 121.2016 | 121.3062 | 121.4284 | 61.803 | -121.3821
307.7812 | 121.7239 | -61.702 | 59.8068 | -0.013049 | -0.028164 | 0.00071361 | 0.055585 | -0.0046643 | 0.051392 | -0.0041205 | -0.0011537 | -0.001017 | -0.0037325 | 0.014006 | -0.0077491 | -59.0968 | -0.012329 | -61.6824 | 59.7131 | 59.5218 | 59.3525 | -61.7045 | 0.074307 | 0.050725 | -61.8186 | 59.4676 | 59.5676 | 59.6853 | -61.6897 | -0.002574 | -0.093724 | 2.6052 | 0.019538 | 0.022112 | -0.28502 | -0.45437 | 0.01225 | -0.33923 | 61.7763 | -0.1166 | -0.12885 | -0.23924 | -0.12157 | 121.4151 | 121.2238 | 121.0544 | 61.6896 | -121.5114 | 121.1696 | 121.2696 | 121.3872 | 61.7527 | -121.4965
309.4688 | 121.8201 | -61.6425 | 59.7839 | -0.005418 | -0.028164 | 0.00050001 | 0.055585 | -0.0046643 | 0.05182 | -0.0041205 | -0.00094006 | -0.0012306 | -0.0035187 | 0.013579 | -0.0079629 | -59.1929 | -0.003172 | -61.6824 | 59.7177 | 59.5218 | 59.357 | -61.7091 | 0.069728 | 0.050725 | -61.8231 | 59.4676 | 59.563 | 59.6898 | -61.6851 | -0.066662 | -0.066258 | 2.4495 | -0.039971 | 0.026691 | -0.26214 | -0.4269 | -0.042681 | -0.31634 | 61.7122 | -0.18069 | -0.13801 | -0.22092 | -0.094102 | 121.3601 | 121.1643 | 120.9995 | 61.6393 | -121.4931 | 121.11 | 121.2055 | 121.3323 | 61.6932 | -121.4691
311.2188 | 121.7056 | -61.8073 | 59.7107 | -0.005418 | -0.027951 | 0.00071361 | 0.055158 | -0.0046643 | 0.051179 | -0.011751 | -0.00072626 | -0.001658 | -0.0033051 | 0.013793 | -0.0077491 | -59.0785 | -0.003172 | -61.687 | 59.7177 | 59.5126 | 59.357 | -61.7 | 0.078886 | 0.059882 | -61.8231 | 59.463 | 59.5722 | 59.6853 | -61.6851 | 0.10729 | 0.006985 | 2.7288 | 0.12025 | 0.012956 | -0.19805 | -0.35366 | 0.12211 | -0.24768 | 61.8861 | -0.015896 | -0.13801 | -0.13853 | -0.025437 | 121.5249 | 121.3199 | 121.1643 | 61.8041 | -121.4107 | 121.2703 | 121.3794 | 121.4925 | 61.8671 | -121.3958
312.9062 | 121.7285 | -61.7615 | 59.761 | -0.005418 | -0.028378 | 0.00050001 | 0.055372 | -0.0046643 | 0.051392 | 0.00351 | -0.0013673 | -0.0014444 | -0.0035187 | 0.013793 | -0.0073219 | -59.0785 | -0.012329 | -61.687 | 59.7177 | 59.531 | 59.3616 | -61.7091 | 0.083464 | 0.059882 | -61.8186 | 59.4584 | 59.5722 | 59.6898 | -61.6897 | 0.052357 | -0.043369 | 2.683 | 0.07447 | 0.022113 | -0.23009 | -0.39944 | 0.07176 | -0.30261 | 61.8449 | -0.057093 | -0.12885 | -0.18888 | -0.071213 | 121.4792 | 121.2924 | 121.1231 | 61.7491 | -121.4702 | 121.2199 | 121.3336 | 121.4513 | 61.8214 | -121.4508
314.6562 | 121.8201 | -61.7432 | 59.697 | -0.005418 | -0.028378 | 0.00028641 | 0.055585 | -0.0044507 | 0.051606 | 0.00351 | -0.00072626 | -0.0012306 | -0.0033051 | 0.013579 | -0.0077491 | -59.1059 | -0.003172 | -61.6916 | 59.7223 | 59.5218 | 59.357 | -61.7 | 0.078886 | 0.064461 | -61.8277 | 59.463 | 59.5676 | 59.6853 | -61.6806 | 0.043203 | 0.025297 | 2.6372 | 0.051581 | 0.008378 | -0.17516 | -0.33993 | 0.062606 | -0.23395 | 61.822 | -0.084562 | -0.14717 | -0.12937 | -0.011704 | 121.4654 | 121.265 | 121.1002 | 61.74 | -121.3969 | 121.2062 | 121.3108 | 121.4284 | 61.8076 | -121.3775
316.3438 | 121.7743 | -61.6425 | 59.8251 | -0.013049 | -0.028164 | 0.00092741 | 0.055585 | -0.0044507 | 0.051392 | 0.00351 | -0.00094006 | -0.00080338 | -0.0037325 | 0.013579 | -0.0075355 | -59.1655 | -0.012329 | -61.687 | 59.7177 | 59.5218 | 59.357 | -61.6954 | 0.069728 | 0.050725 | -61.8186 | 59.4584 | 59.5676 | 59.6853 | -61.6897 | -0.052926 | -0.10746 | 2.477 | -0.044549 | 0.008377 | -0.30333 | -0.4681 | -0.047259 | -0.3667 | 61.7122 | -0.17611 | -0.12885 | -0.25755 | -0.13988 | 121.3601 | 121.1643 | 120.9995 | 61.6301 | -121.5205 | 121.1009 | 121.21 | 121.3277 | 61.6932 | -121.5148
318.0938 | 121.6827 | -61.8118 | 59.729 | -0.005418 | -0.028378 | 0.00050001 | 0.055372 | -0.0046643 | 0.051606 | -0.0041205 | -0.0011537 | -0.0012306 | -0.0035187 | 0.013793 | -0.0077491 | -59.0785 | -0.007751 | -61.6916 | 59.7177 | 59.531 | 59.357 | -61.7 | 0.074307 | 0.064461 | -61.814 | 59.463 | 59.5584 | 59.6898 | -61.6851 | 0.11187 | -0.011326 | 2.7334 | 0.12025 | 0.008378 | -0.19805 | -0.37197 | 0.12669 | -0.26599 | 61.8861 | -0.002161 | -0.12885 | -0.17057 | -0.03917 | 121.5295 | 121.3428 | 121.1689 | 61.8041 | -121.429 | 121.2748 | 121.3703 | 121.5017 | 61.8763 | -121.4141
319.7812 | 121.7056 | -61.702 | 59.8572 | 0.009844 | -0.027951 | 0.00028641 | 0.055372 | -0.0046643 | 0.051179 | -0.011751 | -0.00094006 | -0.0012306 | -0.0030915 | 0.014006 | -0.0077491 | -59.1334 | -0.016908 | -61.687 | 59.7131 | 59.5218 | 59.3525 | -61.6954 | 0.078886 | 0.055303 | -61.8231 | 59.4722 | 59.5584 | 59.6807 | -61.6851 | 0.006583 | -0.14408 | 2.5686 | 0.01496 | 0.008377 | -0.33538 | -0.50472 | 0.016828 | -0.38501 | 61.7809 | -0.12118 | -0.13801 | -0.29875 | -0.1765 | 121.4151 | 121.2238 | 121.0544 | 61.6851 | -121.5526 | 121.1741 | 121.2604 | 121.3826 | 61.7573 | -121.5423
321.5156 | 121.7697 | -61.7065 | 59.7565 | 0.002213 | -0.028164 | 0.00071361 | 0.055372 | -0.0048779 | 0.051392 | -0.019381 | -0.00094006 | -0.0012306 | -0.0035187 | 0.014006 | -0.0079629 | -59.1746 | -0.012329 | -61.687 | 59.7177 | 59.531 | 59.3616 | -61.6954 | 0.06515 | 0.055303 | -61.8186 | 59.463 | 59.563 | 59.6853 | -61.6943 | 0.011161 | -0.038792 | 2.5319 | 0.019538 | 0.008377 | -0.22551 | -0.39486 | 0.012249 | -0.29346 | 61.7717 | -0.11202 | -0.12427 | -0.19346 | -0.071214 | 121.4242 | 121.2375 | 121.0682 | 61.6942 | -121.4519 | 121.1696 | 121.2696 | 121.3918 | 61.7618 | -121.4508
323.2656 | 121.701 | -61.6882 | 59.8297 | 0.009844 | -0.028378 | 0.00092741 | 0.055372 | -0.0044507 | 0.050965 | 0.00351 | -0.00072626 | -0.00080338 | -0.0037325 | 0.014006 | -0.0077491 | -59.1334 | -0.007751 | -61.6962 | 59.7131 | 59.5218 | 59.3616 | -61.7 | 0.069728 | 0.055303 | -61.8186 | 59.4584 | 59.563 | 59.6898 | -61.6897 | -0.011729 | -0.11661 | 2.5548 | -0.007929 | 0.0038 | -0.30791 | -0.4681 | -0.001483 | -0.37128 | 61.758 | -0.13034 | -0.12885 | -0.2667 | -0.13988 | 121.4013 | 121.21 | 121.0498 | 61.6805 | -121.5297 | 121.1467 | 121.2512 | 121.3781 | 61.7435 | -121.5194
325.0156 | 121.7056 | -61.7935 | 59.729 | -0.013049 | -0.028164 | 0.00071361 | 0.055372 | -0.0046643 | 0.051392 | -0.019381 | -0.00094006 | -0.001017 | -0.0030915 | 0.013793 | -0.0075355 | -59.0739 | -0.012329 | -61.6824 | 59.7177 | 59.5264 | 59.3525 | -61.7 | 0.074307 | 0.055303 | -61.8186 | 59.463 | 59.5676 | 59.6853 | -61.6851 | 0.093557 | -0.011326 | 2.7196 | 0.11109 | 0.017534 | -0.20263 | -0.37655 | 0.10838 | -0.26599 | 61.8678 | -0.02505 | -0.13343 | -0.16142 | -0.043748 | 121.5112 | 121.3199 | 121.146 | 61.7812 | -121.429 | 121.2565 | 121.3611 | 121.4788 | 61.8488 | -121.4141
326.7656 | 121.8155 | -61.7706 | 59.7153 | -0.013049 | -0.028592 | 0.00050001 | 0.055372 | -0.0046643 | 0.051179 | -0.011751 | -0.0011537 | -0.0012306 | -0.0035187 | 0.013793 | -0.0073219 | -59.1151 | -0.012329 | -61.687 | 59.7131 | 59.5264 | 59.357 | -61.6954 | 0.074307 | 0.064461 | -61.814 | 59.4722 | 59.5676 | 59.6898 | -61.6851 | 0.075248 | -0.002171 | 2.6555 | 0.083625 | 0.008377 | -0.18889 | -0.35824 | 0.085493 | -0.2431 | 61.8449 | -0.04336 | -0.12885 | -0.14768 | -0.025437 | 121.4837 | 121.297 | 121.1277 | 61.7583 | -121.4107 | 121.2428 | 121.3382 | 121.4605 | 61.8351 | -121.4004
328.4531 | 121.6736 | -61.821 | 59.6832 | 0.002213 | -0.028592 | 0.00028641 | 0.055372 | -0.0044507 | 0.051606 | -0.0041205 | -0.00094006 | -0.0014444 | -0.0037325 | 0.01422 | -0.0075355 | -59.0739 | -0.012329 | -61.687 | 59.7131 | 59.5264 | 59.357 | -61.7 | 0.078886 | 0.06904 | -61.8186 | 59.4676 | 59.5584 | 59.6944 | -61.6943 | 0.12102 | 0.029872 | 2.7471 | 0.13398 | 0.012956 | -0.15685 | -0.3262 | 0.12669 | -0.21564 | 61.8999 | 0.002416 | -0.12427 | -0.1248 | 0.011185 | 121.5341 | 121.3474 | 121.178 | 61.8087 | -121.3832 | 121.2886 | 121.3794 | 121.5154 | 61.89 | -121.3775
330.2188 | 121.6644 | -61.8301 | 59.6878 | -0.013049 | -0.028378 | 0.00050001 | 0.055158 | -0.0046643 | 0.051392 | -0.0041205 | -0.00094006 | -0.0014444 | -0.0035187 | 0.013793 | -0.0071083 | -59.083 | -0.007751 | -61.6916 | 59.7177 | 59.5264 | 59.3525 | -61.7 | 0.074307 | 0.059882 | -61.8186 | 59.4676 | 59.563 | 59.699 | -61.6806 | 0.13018 | 0.029873 | 2.7471 | 0.13856 | 0.008378 | -0.16143 | -0.33535 | 0.14958 | -0.22021 | 61.9044 | 0.011571 | -0.13801 | -0.12479 | 0.011187 | 121.5478 | 121.3565 | 121.1826 | 61.8224 | -121.3878 | 121.2977 | 121.3932 | 121.5291 | 61.89 | -121.3684
331.9844 | 121.7377 | -61.7569 | 59.7656 | 0.009844 | -0.028805 | 0.00071361 | 0.055158 | -0.0046643 | 0.051606 | -0.0041205 | -0.0011537 | -0.0012306 | -0.0035187 | 0.013579 | -0.0079629 | -59.083 | -0.007751 | -61.6916 | 59.7131 | 59.5264 | 59.3525 | -61.7091 | 0.078886 | 0.064461 | -61.814 | 59.463 | 59.5676 | 59.6898 | -61.6851 | 0.047779 | -0.052525 | 2.6738 | 0.065314 | 0.017535 | -0.23925 | -0.41317 | 0.07176 | -0.30261 | 61.8358 | -0.057093 | -0.12885 | -0.19804 | -0.075791 | 121.47 | 121.2833 | 121.1094 | 61.7491 | -121.4747 | 121.2199 | 121.3245 | 121.4467 | 61.8214 | -121.4508
333.6719 | 121.6919 | -61.702 | 59.8297 | -0.005418 | -0.028164 | 0.00071361 | 0.055372 | -0.0046643 | 0.051392 | -0.0041205 | -0.00094006 | -0.0014444 | -0.0035187 | 0.013793 | -0.0079629 | -59.1288 | -0.012329 | -61.687 | 59.7177 | 59.5264 | 59.3525 | -61.7 | 0.069728 | 0.059882 | -61.8231 | 59.463 | 59.5722 | 59.6807 | -61.6851 | 0.002004 | -0.11203 | 2.5731 | 0.01496 | 0.012956 | -0.30333 | -0.47726 | 0.016828 | -0.3667 | 61.7717 | -0.12118 | -0.13801 | -0.25754 | -0.14903 | 121.4196 | 121.2283 | 121.0544 | 61.6896 | -121.5297 | 121.165 | 121.2741 | 121.3826 | 61.7618 | -121.5148
335.4219 | 121.7148 | -61.8027 | 59.729 | -0.005418 | -0.028592 | 0.00050001 | 0.055158 | -0.0050917 | 0.050965 | -0.011751 | -0.0011537 | -0.0012306 | -0.0033051 | 0.014006 | -0.0077491 | -59.083 | -0.003172 | -61.6824 | 59.7131 | 59.531 | 59.357 | -61.7 | 0.078886 | 0.06904 | -61.8048 | 59.463 | 59.5676 | 59.6807 | -61.6897 | 0.10271 | -0.015904 | 2.7196 | 0.12025 | 0.017534 | -0.19805 | -0.37197 | 0.11296 | -0.26599 | 61.8816 | -0.002159 | -0.11512 | -0.16142 | -0.048327 | 121.5158 | 121.3336 | 121.1597 | 61.7995 | -121.429 | 121.2657 | 121.3703 | 121.4834 | 61.8717 | -121.4187
337.125 | 121.6782 | -61.8118 | 59.7153 | 0.002213 | -0.028378 | 0.00028641 | 0.055372 | -0.0050917 | 0.051392 | -0.0041205 | -0.00094006 | -0.001017 | -0.0037325 | 0.013793 | -0.0079629 | -59.0785 | -0.007751 | -61.6916 | 59.7131 | 59.531 | 59.3616 | -61.6954 | 0.074307 | 0.055303 | -61.8231 | 59.4676 | 59.5767 | 59.6898 | -61.6851 | 0.11645 | -0.002171 | 2.7334 | 0.12025 | 0.003799 | -0.18431 | -0.35366 | 0.12669 | -0.24768 | 61.8861 | -0.011318 | -0.13801 | -0.13852 | -0.025437 | 121.5249 | 121.3428 | 121.1734 | 61.8041 | -121.4107 | 121.2794 | 121.3886 | 121.5017 | 61.8671 | -121.4004
338.8594 | 121.7834 | -61.7111 | 59.7427 | -0.005418 | -0.028592 | 0.00050001 | 0.055372 | -0.0048779 | 0.051392 | -0.011751 | -0.00094006 | -0.0014444 | -0.0033051 | 0.014006 | -0.0077491 | -59.1288 | -0.003172 | -61.687 | 59.7177 | 59.5264 | 59.357 | -61.7 | 0.078886 | 0.064461 | -61.8094 | 59.4676 | 59.5722 | 59.6898 | -61.6897 | 0.01116 | -0.025059 | 2.5823 | 0.024116 | 0.012956 | -0.21636 | -0.38571 | 0.021406 | -0.27515 | 61.79 | -0.09829 | -0.1197 | -0.17057 | -0.052903 | 121.4288 | 121.2375 | 121.0682 | 61.7079 | -121.4427 | 121.1787 | 121.2833 | 121.401 | 61.7756 | -121.4325
340.5938 | 121.7651 | -61.7752 | 59.6832 | -0.005418 | -0.028592 | 0.00028641 | 0.055158 | -0.0048779 | 0.051392 | -0.011751 | -0.0011537 | -0.001017 | -0.0035187 | 0.014006 | -0.0075355 | -59.0922 | 0.001407 | -61.687 | 59.7131 | 59.5264 | 59.3616 | -61.7 | 0.074307 | 0.064461 | -61.8186 | 59.4767 | 59.5722 | 59.6898 | -61.6806 | 0.075247 | 0.029872 | 2.683 | 0.088203 | 0.012956 | -0.15685 | -0.32162 | 0.09465 | -0.20648 | 61.8495 | -0.04336 | -0.13801 | -0.11106 | 0.006606 | 121.4883 | 121.3016 | 121.1368 | 61.7766 | -121.3832 | 121.252 | 121.3474 | 121.465 | 61.8397 | -121.3638
342.3438 | 121.7697 | -61.6928 | 59.7748 | -0.013049 | -0.028592 | 0.00050001 | 0.055585 | -0.0044507 | 0.051179 | -0.011751 | -0.00094006 | -0.0014444 | -0.0035187 | 0.014006 | -0.0073219 | -59.1838 | -0.003172 | -61.6962 | 59.7177 | 59.5264 | 59.357 | -61.7 | 0.078886 | 0.064461 | -61.8231 | 59.4584 | 59.563 | 59.6898 | -61.6897 | -0.007151 | -0.057102 | 2.509 | -0.003351 | 0.0038 | -0.2484 | -0.41775 | 0.003095 | -0.31635 | 61.7717 | -0.13034 | -0.13343 | -0.21177 | -0.084946 | 121.4105 | 121.2192 | 121.0498 | 61.6896 | -121.4747 | 121.1512 | 121.2558 | 121.3826 | 61.7573 | -121.4645
344.0781 | 121.7651 | -61.7157 | 59.761 | -0.005418 | -0.028164 | 0.00071361 | 0.054944 | -0.0048779 | 0.051606 | -0.011751 | -0.0011537 | -0.001017 | -0.0035187 | 0.01422 | -0.0077491 | -59.1517 | -0.007751 | -61.687 | 59.7177 | 59.531 | 59.357 | -61.7045 | 0.078886 | 0.059882 | -61.814 | 59.463 | 59.5676 | 59.6807 | -61.6943 | 0.011159 | -0.043369 | 2.564 | 0.028693 | 0.017534 | -0.23009 | -0.40402 | 0.021404 | -0.29803 | 61.7946 | -0.098292 | -0.1197 | -0.19346 | -0.08037 | 121.4334 | 121.2467 | 121.0727 | 61.7079 | -121.4656 | 121.1787 | 121.2833 | 121.3964 | 61.7756 | -121.4553
345.8281 | 121.8246 | -61.6516 | 59.7794 | 0.002213 | -0.028592 | 0.00028641 | 0.055372 | -0.0048779 | 0.051179 | -0.0041205 | -0.00094006 | -0.0012306 | -0.0037325 | 0.013793 | -0.0073219 | -59.1884 | -0.012329 | -61.6962 | 59.7085 | 59.5172 | 59.357 | -61.7 | 0.078886 | 0.059882 | -61.814 | 59.4584 | 59.563 | 59.6898 | -61.6897 | -0.04835 | -0.070836 | 2.4633 | -0.04455 | 0.0038 | -0.26214 | -0.42233 | -0.038104 | -0.32092 | 61.7305 | -0.16238 | -0.12427 | -0.21635 | -0.089524 | 121.3601 | 121.1688 | 121.0086 | 61.6393 | -121.4793 | 121.11 | 121.2146 | 121.3414 | 61.7115 | -121.4691
347.5312 | 121.7377 | -61.7065 | 59.7473 | 0.002213 | -0.028378 | 0.00028641 | 0.055372 | -0.0046643 | 0.051179 | -0.0041205 | -0.0011537 | -0.0012306 | -0.0035187 | 0.014006 | -0.0079629 | -59.083 | -0.007751 | -61.6962 | 59.7131 | 59.5218 | 59.357 | -61.7045 | 0.069728 | 0.050725 | -61.8186 | 59.463 | 59.5767 | 59.6898 | -61.6943 | 0.002004 | -0.034214 | 2.6235 | 0.010382 | 0.008378 | -0.22552 | -0.39028 | 0.012249 | -0.2843 | 61.7763 | -0.11202 | -0.12427 | -0.17057 | -0.05748 | 121.4196 | 121.2283 | 121.0636 | 61.6988 | -121.4519 | 121.1696 | 121.2833 | 121.3964 | 61.7573 | -121.4416
349.2656 | 121.8109 | -61.6333 | 59.8114 | 0.009844 | -0.028805 | 0.00050001 | 0.055158 | -0.0048779 | 0.051179 | -0.019381 | -0.00094006 | -0.0012306 | -0.0035187 | 0.013579 | -0.0079629 | -59.1838 | -0.003172 | -61.7007 | 59.7177 | 59.531 | 59.3616 | -61.6908 | 0.069728 | 0.059882 | -61.814 | 59.463 | 59.5767 | 59.6898 | -61.6897 | -0.057502 | -0.093723 | 2.4495 | -0.067439 | -0.009937 | -0.28044 | -0.44979 | -0.056414 | -0.34839 | 61.703 | -0.18069 | -0.12427 | -0.23465 | -0.12157 | 121.351 | 121.1643 | 120.9949 | 61.6301 | -121.5022 | 121.0963 | 121.21 | 121.3231 | 61.6932 | -121.5011
351.0156 | 121.7377 | -61.7615 | 59.761 | 0.009844 | -0.028592 | 0.00092741 | 0.055372 | -0.0050917 | 0.051179 | -0.0041205 | -0.0011537 | -0.0014444 | -0.0035187 | 0.014006 | -0.0077491 | -59.0785 | -0.012329 | -61.6962 | 59.7085 | 59.531 | 59.357 | -61.7045 | 0.074307 | 0.064461 | -61.8186 | 59.4584 | 59.5676 | 59.6898 | -61.6806 | 0.056936 | -0.052525 | 2.683 | 0.065314 | 0.008378 | -0.23009 | -0.40402 | 0.080917 | -0.30261 | 61.8358 | -0.057093 | -0.13801 | -0.19346 | -0.071213 | 121.47 | 121.2924 | 121.1185 | 61.7491 | -121.4656 | 121.2199 | 121.3291 | 121.4513 | 61.8259 | -121.4416
352.7188 | 121.7377 | -61.7981 | 59.6878 | -0.005418 | -0.028592 | 0.00028641 | 0.055158 | -0.0044507 | 0.050752 | -0.019381 | -0.00094006 | -0.0012306 | -0.0037325 | 0.014006 | -0.0079629 | -59.1014 | -0.007751 | -61.6916 | 59.7131 | 59.531 | 59.3616 | -61.7 | 0.074307 | 0.059882 | -61.8231 | 59.4584 | 59.5676 | 59.6853 | -61.6897 | 0.098135 | 0.025295 | 2.6967 | 0.10651 | 0.008378 | -0.15685 | -0.32619 | 0.10838 | -0.22937 | 61.8724 | -0.025051 | -0.13343 | -0.12022 | -0.002549 | 121.5112 | 121.3291 | 121.1597 | 61.7903 | -121.3878 | 121.2565 | 121.3657 | 121.4834 | 61.858 | -121.3775
354.4688 | 121.6965 | -61.8256 | 59.7107 | 0.002213 | -0.028592 | 0.00071361 | 0.055158 | -0.0044507 | 0.051179 | -0.0041205 | -0.0011537 | -0.00080338 | -0.0037325 | 0.014006 | -0.0077491 | -59.0876 | -0.007751 | -61.6916 | 59.7085 | 59.5218 | 59.3616 | -61.6954 | 0.078886 | 0.055303 | -61.814 | 59.4539 | 59.5722 | 59.6898 | -61.6897 | 0.13018 | -0.002171 | 2.7379 | 0.13398 | 0.003799 | -0.18889 | -0.34908 | 0.13585 | -0.25684 | 61.9044 | 0.011572 | -0.12427 | -0.13853 | -0.020859 | 121.5341 | 121.3474 | 121.1872 | 61.8178 | -121.4061 | 121.2794 | 121.3977 | 121.5154 | 61.8809 | -121.4004
356.2188 | 121.8018 | -61.6013 | 59.8068 | -0.013049 | -0.029019 | 0.00050001 | 0.055158 | -0.0048779 | 0.050965 | 0.00351 | -0.00072626 | -0.0012306 | -0.0037325 | 0.014006 | -0.0077491 | -59.1975 | -0.012329 | -61.6916 | 59.7039 | 59.5218 | 59.357 | -61.7 | 0.069728 | 0.059882 | -61.8186 | 59.4584 | 59.5767 | 59.6807 | -61.6897 | -0.098704 | -0.10288 | 2.4037 | -0.090326 | 0.008378 | -0.28502 | -0.44979 | -0.088458 | -0.34839 | 61.671 | -0.21731 | -0.12885 | -0.23008 | -0.12615 | 121.3052 | 121.1231 | 120.9583 | 61.5889 | -121.5068 | 121.0597 | 121.178 | 121.2819 | 61.6611 | -121.4965
357.9062 | 121.7468 | -61.6928 | 59.7473 | -0.013049 | -0.028592 | 0.00028641 | 0.055585 | -0.0050917 | 0.051392 | -0.0041205 | -0.00094006 | -0.0012306 | -0.0035187 | 0.014434 | -0.0079629 | -59.1563 | -0.003172 | -61.6916 | 59.7131 | 59.5264 | 59.3662 | -61.6954 | 0.074307 | 0.064461 | -61.8186 | 59.463 | 59.5676 | 59.6761 | -61.6851 | -0.002572 | -0.034214 | 2.5365 | 0.001227 | 0.003799 | -0.22094 | -0.38112 | 0.007673 | -0.2843 | 61.7671 | -0.12576 | -0.13343 | -0.17973 | -0.071215 | 121.4059 | 121.2192 | 121.059 | 61.6896 | -121.4427 | 121.1558 | 121.2604 | 121.3689 | 61.7573 | -121.4325
359.6562 | 121.843 | -61.6425 | 59.8114 | 0.002213 | -0.028805 | 0.00050001 | 0.054944 | -0.0050917 | 0.050965 | -0.011751 | -0.0011537 | -0.0012306 | -0.0037325 | 0.014006 | -0.0075355 | -59.1929 | -0.007751 | -61.6962 | 59.7177 | 59.5264 | 59.357 | -61.7045 | 0.060571 | 0.050725 | -61.814 | 59.4584 | 59.5676 | 59.6898 | -61.6897 | -0.062083 | -0.093723 | 2.4495 | -0.053705 | 0.008378 | -0.28502 | -0.45437 | -0.047259 | -0.35297 | 61.703 | -0.17153 | -0.12427 | -0.24381 | -0.12157 | 121.3601 | 121.1688 | 120.9995 | 61.6347 | -121.5159 | 121.1009 | 121.21 | 121.3323 | 61.6932 | -121.5011
361.3438 | 121.7148 | -61.702 | 59.7977 | 0.002213 | -0.029019 | 0.00050001 | 0.054944 | -0.0048779 | 0.050965 | 0.00351 | -0.0011537 | -0.0012306 | -0.0033051 | 0.014006 | -0.0077491 | -59.0968 | -0.012329 | -61.6962 | 59.7177 | 59.531 | 59.3616 | -61.7045 | 0.069728 | 0.055303 | -61.814 | 59.4584 | 59.5676 | 59.6807 | -61.6851 | -0.002574 | -0.07999 | 2.6052 | 0.005804 | 0.008378 | -0.26671 | -0.43606 | 0.016828 | -0.33923 | 61.7717 | -0.11202 | -0.12885 | -0.23008 | -0.11699 | 121.4196 | 121.2329 | 121.0636 | 61.6896 | -121.5022 | 121.1604 | 121.2696 | 121.3826 | 61.7573 | -121.4828
363.0938 | 121.669 | -61.6745 | 59.8526 | -0.005418 | -0.028592 | 0.00028641 | 0.055372 | -0.0046643 | 0.051179 | -0.0041205 | -0.00094006 | -0.0012306 | -0.0037325 | 0.013793 | -0.0079629 | -59.1243 | -0.003172 | -61.687 | 59.7131 | 59.531 | 59.357 | -61.7 | 0.069728 | 0.055303 | -61.8186 | 59.463 | 59.5676 | 59.6853 | -61.676 | -0.025461 | -0.1395 | 2.5502 | -0.012505 | 0.012956 | -0.32164 | -0.49557 | -0.001479 | -0.38959 | 61.7442 | -0.14407 | -0.14259 | -0.28501 | -0.16734 | 121.3876 | 121.2055 | 121.0315 | 61.6713 | -121.5526 | 121.1375 | 121.2421 | 121.3598 | 61.7298 | -121.5286
364.7812 | 121.7926 | -61.6699 | 59.7794 | -0.013049 | -0.028805 | 0.00050001 | 0.055158 | -0.0048779 | 0.051179 | -0.011751 | -0.0013673 | -0.0014444 | -0.0039461 | 0.014006 | -0.0079629 | -59.1884 | -0.007751 | -61.6916 | 59.7177 | 59.5218 | 59.3616 | -61.6954 | 0.074307 | 0.064461 | -61.8231 | 59.4584 | 59.563 | 59.6944 | -61.6851 | -0.02546 | -0.06168 | 2.4816 | -0.021661 | 0.003799 | -0.25756 | -0.41775 | -0.015215 | -0.32092 | 61.7442 | -0.15322 | -0.13801 | -0.21635 | -0.084945 | 121.3876 | 121.1917 | 121.0315 | 61.6622 | -121.4747 | 121.1284 | 121.2329 | 121.3643 | 61.7344 | -121.4645
366.5156 | 121.8155 | -61.6516 | 59.8114 | -0.005418 | -0.029019 | 0.00071361 | 0.055372 | -0.0048779 | 0.051392 | -0.0041205 | -0.00072626 | -0.0014444 | -0.0035187 | 0.01422 | -0.0077491 | -59.1929 | -0.012329 | -61.6916 | 59.7131 | 59.5264 | 59.3616 | -61.7045 | 0.074307 | 0.055303 | -61.8186 | 59.4676 | 59.5676 | 59.6898 | -61.6851 | -0.052928 | -0.098301 | 2.4587 | -0.039972 | 0.012956 | -0.28502 | -0.44979 | -0.033526 | -0.34381 | 61.7259 | -0.16696 | -0.13343 | -0.24381 | -0.12157 | 121.3647 | 121.178 | 121.0132 | 61.6393 | -121.5159 | 121.1192 | 121.2192 | 121.3414 | 61.7069 | -121.4965
368.2031 | 121.6736 | -61.6882 | 59.8572 | 0.009844 | -0.029019 | 0.00028641 | 0.055158 | -0.0048779 | 0.051179 | -0.0041205 | -0.0013673 | -0.0014444 | -0.0037325 | 0.014006 | -0.0077491 | -59.1197 | -0.007751 | -61.6916 | 59.7131 | 59.5264 | 59.3616 | -61.7 | 0.078886 | 0.059882 | -61.814 | 59.4584 | 59.5722 | 59.6898 | -61.6851 | -0.011729 | -0.14408 | 2.5686 | -0.003351 | 0.008378 | -0.3308 | -0.49557 | 0.003095 | -0.39874 | 61.7671 | -0.12576 | -0.12885 | -0.28501 | -0.16734 | 121.4013 | 121.2146 | 121.0498 | 61.6805 | -121.5571 | 121.1467 | 121.2604 | 121.3781 | 61.7481 | -121.5423
369.9375 | 121.8063 | -61.6241 | 59.8251 | 0.002213 | -0.028805 | 0.00050001 | 0.055158 | -0.0046643 | 0.050965 | -0.0041205 | -0.0013673 | -0.0012306 | -0.0033051 | 0.01422 | -0.0079629 | -59.1838 | 0.005985 | -61.6962 | 59.7131 | 59.531 | 59.357 | -61.7045 | 0.074307 | 0.055303 | -61.814 | 59.4539 | 59.563 | 59.6853 | -61.6851 | -0.080393 | -0.11203 | 2.4404 | -0.072015 | 0.008378 | -0.29418 | -0.4681 | -0.060991 | -0.37128 | 61.6985 | -0.18984 | -0.12885 | -0.26212 | -0.13988 | 121.3372 | 121.1551 | 120.9812 | 61.6301 | -121.5297 | 121.078 | 121.1872 | 121.3094 | 61.6794 | -121.5103
371.6719 | 121.8018 | -61.6241 | 59.8068 | -0.005418 | -0.029019 | 0.00050001 | 0.055585 | -0.0048779 | 0.051179 | -0.0041205 | -0.0011537 | -0.0014444 | -0.0033051 | 0.014006 | -0.0077491 | -59.1884 | -0.007751 | -61.6962 | 59.7039 | 59.531 | 59.357 | -61.6954 | 0.074307 | 0.059882 | -61.8186 | 59.463 | 59.5676 | 59.6853 | -61.6851 | -0.071236 | -0.10288 | 2.4358 | -0.072015 | -0.000779 | -0.27587 | -0.44979 | -0.060991 | -0.34381 | 61.6985 | -0.19442 | -0.13343 | -0.23924 | -0.12157 | 121.3281 | 121.1551 | 120.9812 | 61.6164 | -121.5022 | 121.0872 | 121.1917 | 121.3094 | 61.684 | -121.492
373.3594 | 121.7972 | -61.6287 | 59.816 | 0.002213 | -0.028805 | 0.00071361 | 0.055158 | -0.0050917 | 0.051179 | -0.011751 | -0.00072626 | -0.0014444 | -0.0033051 | 0.01422 | -0.0079629 | -59.1884 | -0.003172 | -61.6916 | 59.7131 | 59.5172 | 59.357 | -61.7045 | 0.078886 | 0.064461 | -61.8186 | 59.463 | 59.5722 | 59.6807 | -61.6897 | -0.075816 | -0.10288 | 2.4404 | -0.06286 | 0.012956 | -0.29876 | -0.45895 | -0.060992 | -0.35297 | 61.7076 | -0.18984 | -0.12885 | -0.24381 | -0.1353 | 121.3418 | 121.1459 | 120.9858 | 61.6256 | -121.5205 | 121.0917 | 121.2009 | 121.3094 | 61.6932 | -121.5057
375.1094 | 121.8338 | -61.615 | 59.7977 | 0.002213 | -0.029019 | 0.00050001 | 0.054944 | -0.0050917 | 0.050965 | -0.0041205 | -0.0011537 | -0.0012306 | -0.0037325 | 0.014434 | -0.0079629 | -59.1884 | -0.012329 | -61.6962 | 59.7131 | 59.5264 | 59.357 | -61.6954 | 0.074307 | 0.055303 | -61.8186 | 59.4584 | 59.5676 | 59.6853 | -61.6897 | -0.080392 | -0.084568 | 2.4266 | -0.081171 | -0.000779 | -0.27129 | -0.44064 | -0.074725 | -0.33923 | 61.6893 | -0.20358 | -0.12885 | -0.23008 | -0.11241 | 121.3281 | 121.1414 | 120.972 | 61.6027 | -121.4931 | 121.0734 | 121.1826 | 121.3002 | 61.6703 | -121.4874
376.7969 | 121.701 | -61.7111 | 59.8206 | 0.002213 | -0.028805 | 0.00050001 | 0.055158 | -0.0048779 | 0.051392 | -0.0041205 | -0.00094006 | -0.0012306 | -0.0033051 | 0.014006 | -0.0079629 | -59.1014 | -0.007751 | -61.6962 | 59.7131 | 59.5264 | 59.357 | -61.7 | 0.06515 | 0.064461 | -61.8094 | 59.4493 | 59.5676 | 59.6853 | -61.6851 | 0.01116 | -0.10746 | 2.6098 | 0.01496 | 0.0038 | -0.29418 | -0.46353 | 0.025984 | -0.37128 | 61.7763 | -0.09829 | -0.12427 | -0.25297 | -0.1353 | 121.4242 | 121.2375 | 121.0682 | 61.7034 | -121.5205 | 121.1604 | 121.2787 | 121.3964 | 61.7756 | -121.5057
378.5469 | 121.7697 | -61.7523 | 59.7015 | -0.02068 | -0.028805 | 0.00050001 | 0.055372 | -0.0048779 | 0.051392 | -0.019381 | -0.00072626 | -0.0012306 | -0.0035187 | 0.014434 | -0.0075355 | -59.1014 | -0.016908 | -61.6916 | 59.7131 | 59.531 | 59.357 | -61.7 | 0.074307 | 0.050725 | -61.814 | 59.4584 | 59.563 | 59.6807 | -61.6806 | 0.052358 | 0.011562 | 2.651 | 0.060736 | 0.008378 | -0.17058 | -0.34451 | 0.071761 | -0.2431 | 61.8266 | -0.061671 | -0.13343 | -0.13853 | -0.020861 | 121.4654 | 121.2833 | 121.1094 | 61.7354 | -121.4015 | 121.2108 | 121.3153 | 121.433 | 61.803 | -121.3821
380.2812 | 121.7606 | -61.6974 | 59.7702 | 0.002213 | -0.028805 | 0.00092741 | 0.055158 | -0.0048779 | 0.050752 | 0.00351 | -0.0011537 | -0.001017 | -0.0037325 | 0.01422 | -0.0075355 | -59.1746 | -0.007751 | -61.6962 | 59.7177 | 59.5264 | 59.3662 | -61.7045 | 0.074307 | 0.059882 | -61.814 | 59.4584 | 59.563 | 59.6807 | -61.6943 | -0.007151 | -0.052525 | 2.5228 | 0.001227 | 0.008378 | -0.24383 | -0.40401 | 0.003094 | -0.31177 | 61.7717 | -0.1166 | -0.1197 | -0.20719 | -0.089526 | 121.4151 | 121.2238 | 121.0636 | 61.6896 | -121.4747 | 121.1558 | 121.2604 | 121.3781 | 61.7573 | -121.4645
382.0156 | 121.7926 | -61.6333 | 59.8297 | 0.002213 | -0.029233 | 0.00071361 | 0.054944 | -0.0048779 | 0.051179 | -0.011751 | -0.0011537 | -0.0014444 | -0.0039461 | 0.014434 | -0.0073219 | -59.1975 | -0.007751 | -61.7007 | 59.7085 | 59.531 | 59.3525 | -61.6954 | 0.069728 | 0.055303 | -61.814 | 59.4676 | 59.563 | 59.6807 | -61.6897 | -0.062081 | -0.12119 | 2.4358 | -0.067439 | -0.005358 | -0.29875 | -0.47726 | -0.056414 | -0.36212 | 61.703 | -0.18069 | -0.12427 | -0.2667 | -0.14903 | 121.3418 | 121.1643 | 120.9858 | 61.6256 | -121.5251 | 121.1009 | 121.1963 | 121.314 | 61.6886 | -121.5194
383.7031 | 121.6461 | -61.7889 | 59.729 | 0.002213 | -0.029019 | 7.2612e-05 | 0.055585 | -0.0050917 | 0.050965 | -0.0041205 | -0.0013673 | -0.0012306 | -0.0035187 | 0.01422 | -0.0077491 | -59.083 | -0.003172 | -61.7007 | 59.7085 | 59.5264 | 59.3662 | -61.7 | 0.069728 | 0.06904 | -61.814 | 59.463 | 59.563 | 59.6853 | -61.6897 | 0.088979 | -0.020482 | 2.7059 | 0.0882 | -0.000779 | -0.20263 | -0.36281 | 0.099225 | -0.26599 | 61.8587 | -0.02505 | -0.12427 | -0.16599 | -0.043748 | 121.4975 | 121.3153 | 121.1551 | 61.7858 | -121.429 | 121.252 | 121.352 | 121.4742 | 61.858 | -121.4187
385.4688 | 121.701 | -61.7065 | 59.8297 | -0.005418 | -0.029233 | 0.00028641 | 0.055158 | -0.0048779 | 0.050752 | -0.0041205 | -0.00072626 | -0.001658 | -0.0035187 | 0.01422 | -0.0079629 | -59.1014 | -0.007751 | -61.7007 | 59.7039 | 59.5355 | 59.3616 | -61.7 | 0.069728 | 0.050725 | -61.8186 | 59.4584 | 59.5584 | 59.6761 | -61.6851 | 0.006582 | -0.12577 | 2.6052 | 0.005803 | -0.000779 | -0.29418 | -0.4681 | 0.021406 | -0.37128 | 61.7763 | -0.11202 | -0.13343 | -0.27128 | -0.15361 | 121.4105 | 121.2421 | 121.0682 | 61.6988 | -121.5297 | 121.165 | 121.265 | 121.3826 | 61.7573 | -121.5148
387.1562 | 121.7651 | -61.6791 | 59.761 | -0.005418 | -0.028592 | 0.00028641 | 0.055372 | -0.0050917 | 0.050965 | -0.0041205 | -0.0013673 | -0.0014444 | -0.0035187 | 0.014647 | -0.0075355 | -59.17 | -0.003172 | -61.6962 | 59.7177 | 59.5218 | 59.3616 | -61.7 | 0.074307 | 0.064461 | -61.814 | 59.4676 | 59.5676 | 59.6853 | -61.6897 | -0.020884 | -0.043369 | 2.509 | -0.017084 | 0.0038 | -0.23925 | -0.39944 | -0.010638 | -0.29346 | 61.7534 | -0.13491 | -0.12427 | -0.19346 | -0.075791 | 121.3968 | 121.2009 | 121.0407 | 61.6759 | -121.461 | 121.1467 | 121.2467 | 121.3643 | 61.7435 | -121.4508
388.9062 | 121.6827 | -61.6837 | 59.8206 | 0.002213 | -0.029446 | 0.00050001 | 0.054944 | -0.0048779 | 0.050965 | -0.011751 | -0.0011537 | -0.0012306 | -0.0039461 | 0.01422 | -0.0075355 | -59.1243 | 0.001407 | -61.6962 | 59.7131 | 59.5264 | 59.3616 | -61.7 | 0.074307 | 0.064461 | -61.8094 | 59.4676 | 59.5676 | 59.6807 | -61.6897 | -0.016306 | -0.10746 | 2.5594 | -0.012506 | 0.0038 | -0.29418 | -0.45895 | -0.00606 | -0.35297 | 61.758 | -0.12576 | -0.1197 | -0.25297 | -0.13988 | 121.3968 | 121.21 | 121.0453 | 61.6851 | -121.5205 | 121.1512 | 121.2512 | 121.3643 | 61.7481 | -121.5103
390.6406 | 121.6507 | -61.7935 | 59.6924 | 0.002213 | -0.029233 | 0.00028641 | 0.054944 | -0.0046643 | 0.051606 | 0.00351 | -0.00094006 | -0.0012306 | -0.0037325 | 0.014434 | -0.0077491 | -59.0785 | -0.003172 | -61.7007 | 59.7039 | 59.5218 | 59.3616 | -61.7 | 0.074307 | 0.059882 | -61.8094 | 59.4584 | 59.5722 | 59.6807 | -61.6851 | 0.093557 | 0.01156 | 2.715 | 0.092778 | -0.000779 | -0.17058 | -0.33077 | 0.10838 | -0.23395 | 61.8678 | -0.015893 | -0.12427 | -0.12022 | -0.011706 | 121.4975 | 121.3153 | 121.1551 | 61.7903 | -121.3923 | 121.252 | 121.3657 | 121.4742 | 61.8534 | -121.3775
392.3281 | 121.7102 | -61.6562 | 59.8297 | 0.002213 | -0.029019 | 0.00050001 | 0.055158 | -0.0048779 | 0.051179 | -0.0041205 | -0.0011537 | -0.0012306 | -0.0033051 | 0.014434 | -0.0079629 | -59.1563 | -0.003172 | -61.7053 | 59.7177 | 59.5264 | 59.3616 | -61.7 | 0.069728 | 0.064461 | -61.8186 | 59.4539 | 59.563 | 59.6898 | -61.6806 | -0.043772 | -0.11203 | 2.4999 | -0.049129 | -0.005357 | -0.30333 | -0.4681 | -0.024369 | -0.37586 | 61.7259 | -0.16238 | -0.13801 | -0.2667 | -0.13988 | 121.3739 | 121.1826 | 121.0178 | 61.653 | -121.5297 | 121.11 | 121.2192 | 121.346 | 61.7206 | -121.5103
394.0781 | 121.669 | -61.8118 | 59.697 | 0.002213 | -0.029233 | 0.00050001 | 0.054944 | -0.0048779 | 0.051179 | -0.011751 | -0.0013673 | -0.0012306 | -0.0037325 | 0.01422 | -0.0079629 | -59.0739 | -0.007751 | -61.7007 | 59.7085 | 59.5264 | 59.3662 | -61.7091 | 0.074307 | 0.059882 | -61.8094 | 59.4539 | 59.563 | 59.6898 | -61.6897 | 0.10271 | 0.011562 | 2.7379 | 0.11109 | 0.008378 | -0.17058 | -0.33077 | 0.12211 | -0.2431 | 61.8861 | 0.002418 | -0.1197 | -0.13395 | -0.007126 | 121.5204 | 121.3382 | 121.178 | 61.8041 | -121.4061 | 121.2657 | 121.3748 | 121.5017 | 61.8717 | -121.3867
395.8125 | 121.7468 | -61.7111 | 59.7244 | -0.005418 | -0.029233 | 0.00028641 | 0.054731 | -0.0050917 | 0.050965 | -0.011751 | -0.0011537 | -0.0012306 | -0.0035187 | 0.014647 | -0.0073219 | -59.1243 | -0.003172 | -61.7053 | 59.7131 | 59.5264 | 59.3616 | -61.7 | 0.069728 | 0.059882 | -61.814 | 59.4676 | 59.5676 | 59.6853 | -61.6897 | 0.01116 | -0.011326 | 2.5869 | 0.005803 | -0.005357 | -0.19805 | -0.36281 | 0.021406 | -0.25684 | 61.7808 | -0.10287 | -0.12427 | -0.15684 | -0.03917 | 121.4242 | 121.2375 | 121.0727 | 61.7079 | -121.4244 | 121.1787 | 121.2787 | 121.3964 | 61.771 | -121.4141
397.5625 | 121.6965 | -61.702 | 59.8022 | -0.005418 | -0.029233 | 0.00050001 | 0.055158 | -0.0046643 | 0.050752 | -0.011751 | -0.0013673 | -0.0014444 | -0.0037325 | 0.014434 | -0.0077491 | -59.0968 | -0.016908 | -61.7007 | 59.7177 | 59.5264 | 59.3616 | -61.7 | 0.069728 | 0.059882 | -61.8094 | 59.4584 | 59.563 | 59.6853 | -61.6851 | 0.002004 | -0.084568 | 2.6052 | 0.001225 | -0.000779 | -0.27587 | -0.44063 | 0.016828 | -0.34381 | 61.7717 | -0.10745 | -0.12427 | -0.23923 | -0.11699 | 121.4196 | 121.2283 | 121.0636 | 61.6851 | -121.5022 | 121.1604 | 121.265 | 121.3872 | 61.7618 | -121.4874
399.2656 | 121.8063 | -61.6287 | 59.7885 | 0.002213 | -0.029446 | 0.00050001 | 0.055158 | -0.0046643 | 0.050752 | -0.0041205 | -0.0013673 | -0.0014444 | -0.0035187 | 0.01422 | -0.0077491 | -59.1792 | -0.007751 | -61.7099 | 59.7085 | 59.5218 | 59.3525 | -61.7 | 0.074307 | 0.059882 | -61.8231 | 59.4676 | 59.5584 | 59.6898 | -61.6851 | -0.071238 | -0.079991 | 2.4495 | -0.081173 | -0.009935 | -0.26671 | -0.43606 | -0.056414 | -0.32092 | 61.703 | -0.19442 | -0.13801 | -0.23008 | -0.098679 | 121.3372 | 121.1505 | 120.9812 | 61.621 | -121.4885 | 121.0963 | 121.1872 | 121.3186 | 61.6886 | -121.4736
401.0156 | 121.7422 | -61.7569 | 59.697 | -0.005418 | -0.029019 | 0.00050001 | 0.055372 | -0.0048779 | 0.051392 | -0.0041205 | -0.0011537 | -0.0014444 | -0.0035187 | 0.014434 | -0.0075355 | -59.0922 | -0.003172 | -61.7099 | 59.7177 | 59.5218 | 59.3616 | -61.7 | 0.078886 | 0.06904 | -61.8094 | 59.463 | 59.5676 | 59.6761 | -61.6851 | 0.056936 | 0.020718 | 2.6647 | 0.047001 | -0.009935 | -0.17516 | -0.33535 | 0.07176 | -0.23395 | 61.8358 | -0.052514 | -0.12427 | -0.12937 | -0.020861 | 121.4746 | 121.2787 | 121.1185 | 61.7537 | -121.3969 | 121.2199 | 121.3245 | 121.433 | 61.8259 | -121.3821
402.6875 | 121.6965 | -61.8073 | 59.7244 | -0.005418 | -0.029019 | 0.00071361 | 0.054944 | -0.0048779 | 0.051179 | -0.0041205 | -0.0013673 | -0.001017 | -0.0037325 | 0.01422 | -0.0077491 | -59.0876 | -0.003172 | -61.7053 | 59.7131 | 59.5264 | 59.357 | -61.7045 | 0.078886 | 0.064461 | -61.8094 | 59.4676 | 59.5676 | 59.6853 | -61.6851 | 0.10271 | -0.011326 | 2.7196 | 0.10193 | -0.000779 | -0.19805 | -0.36739 | 0.12211 | -0.25684 | 61.8861 | -0.00216 | -0.12427 | -0.15684 | -0.03917 | 121.5204 | 121.3336 | 121.1643 | 61.8041 | -121.429 | 121.2748 | 121.3748 | 121.4925 | 61.8717 | -121.4096
404.4375 | 121.7972 | -61.7523 | 59.6603 | -0.013049 | -0.029233 | 0.00071361 | 0.054944 | -0.0048779 | 0.051179 | -0.011751 | -0.0011537 | -0.0014444 | -0.0035187 | 0.01422 | -0.0079629 | -59.1059 | -0.003172 | -61.7053 | 59.7085 | 59.5264 | 59.3616 | -61.7045 | 0.069728 | 0.059882 | -61.814 | 59.4584 | 59.5722 | 59.6898 | -61.6851 | 0.04778 | 0.048183 | 2.6464 | 0.047001 | -0.000779 | -0.13396 | -0.29873 | 0.067182 | -0.20191 | 61.822 | -0.061671 | -0.12885 | -0.088171 | 0.029495 | 121.4608 | 121.2787 | 121.1139 | 61.7491 | -121.3649 | 121.2108 | 121.3245 | 121.4422 | 61.8122 | -121.3455
406.1875 | 121.8018 | -61.7386 | 59.7153 | 0.002213 | -0.029446 | 0.00050001 | 0.055158 | -0.0046643 | 0.050965 | -0.011751 | -0.0013673 | -0.001017 | -0.0039461 | 0.01422 | -0.0075355 | -59.1288 | -0.007751 | -61.7099 | 59.7085 | 59.5218 | 59.3616 | -61.7 | 0.078886 | 0.059882 | -61.8094 | 59.463 | 59.563 | 59.6853 | -61.6897 | 0.038625 | -0.006749 | 2.6098 | 0.02869 | -0.009935 | -0.19347 | -0.35366 | 0.048871 | -0.25226 | 61.8175 | -0.070825 | -0.1197 | -0.15226 | -0.030015 | 121.4471 | 121.2604 | 121.1002 | 61.7308 | -121.4152 | 121.2016 | 121.3016 | 121.4238 | 61.7985 | -121.405
407.8906 | 121.6599 | -61.8118 | 59.7427 | -0.005418 | -0.028805 | 0.00028641 | 0.054944 | -0.0048779 | 0.051179 | 0.00351 | -0.0011537 | -0.0014444 | -0.0037325 | 0.014434 | -0.0079629 | -59.0739 | -0.003172 | -61.7099 | 59.7085 | 59.5218 | 59.3708 | -61.6908 | 0.074307 | 0.064461 | -61.814 | 59.4584 | 59.563 | 59.6853 | -61.6851 | 0.12103 | -0.034215 | 2.7379 | 0.10193 | -0.019093 | -0.22094 | -0.37197 | 0.12669 | -0.2843 | 61.8861 | -0.002161 | -0.12885 | -0.17973 | -0.057481 | 121.5204 | 121.3336 | 121.1826 | 61.8087 | -121.4335 | 121.2703 | 121.3748 | 121.4971 | 61.8763 | -121.4279
409.625 | 121.6553 | -61.8027 | 59.7107 | 0.002213 | -0.029446 | 0.00050001 | 0.054731 | -0.0048779 | 0.051179 | -0.011751 | -0.00094006 | -0.001017 | -0.0035187 | 0.01422 | -0.0079629 | -59.0785 | -0.007751 | -61.7099 | 59.7131 | 59.5172 | 59.357 | -61.7 | 0.069728 | 0.064461 | -61.814 | 59.463 | 59.5722 | 59.6853 | -61.6851 | 0.10271 | 0.002407 | 2.7242 | 0.092777 | -0.009935 | -0.19347 | -0.35366 | 0.11754 | -0.24768 | 61.8724 | -0.011317 | -0.12885 | -0.13853 | -0.025437 | 121.5158 | 121.3199 | 121.1597 | 61.7949 | -121.4107 | 121.2657 | 121.3748 | 121.4879 | 61.8671 | -121.3958
411.3125 | 121.8201 | -61.6379 | 59.8251 | -0.005418 | -0.029233 | 0.00050001 | 0.054731 | -0.0048779 | 0.050965 | -0.0041205 | -0.00094006 | -0.0014444 | -0.0035187 | 0.014434 | -0.0077491 | -59.2021 | -0.007751 | -61.7099 | 59.7085 | 59.5264 | 59.3616 | -61.7 | 0.074307 | 0.059882 | -61.8186 | 59.463 | 59.5676 | 59.6853 | -61.6943 | -0.062083 | -0.11661 | 2.4358 | -0.072018 | -0.009935 | -0.29876 | -0.46352 | -0.056416 | -0.36212 | 61.7122 | -0.18069 | -0.12427 | -0.25755 | -0.13988 | 121.3464 | 121.1643 | 120.9995 | 61.6301 | -121.5251 | 121.1009 | 121.2055 | 121.3231 | 61.6978 | -121.5194
413.0625 | 121.7972 | -61.7294 | 59.7107 | -0.005418 | -0.02966 | 0.00050001 | 0.054731 | -0.0048779 | 0.051179 | -0.0041205 | -0.0011537 | -0.0012306 | -0.0037325 | 0.014434 | -0.0081765 | -59.1151 | -0.012329 | -61.7007 | 59.7223 | 59.5355 | 59.3662 | -61.6954 | 0.074307 | 0.064461 | -61.814 | 59.463 | 59.563 | 59.6853 | -61.676 | 0.034049 | 0.011564 | 2.6143 | 0.028691 | -0.005358 | -0.17516 | -0.3445 | 0.053452 | -0.24768 | 61.8037 | -0.084559 | -0.13801 | -0.14768 | -0.025437 | 121.4517 | 121.265 | 121.0956 | 61.7171 | -121.4061 | 121.1924 | 121.2924 | 121.4147 | 61.7939 | -121.3867
414.8125 | 121.6827 | -61.8347 | 59.7198 | -0.013049 | -0.029446 | 7.2612e-05 | 0.054944 | -0.0050917 | 0.050965 | -0.0041205 | -0.0013673 | -0.0012306 | -0.0035187 | 0.014647 | -0.0077491 | -59.0785 | -0.007751 | -61.7099 | 59.7177 | 59.5172 | 59.3662 | -61.6954 | 0.074307 | 0.059882 | -61.814 | 59.4584 | 59.563 | 59.6853 | -61.6851 | 0.13933 | -0.002171 | 2.7562 | 0.12482 | -0.014514 | -0.20263 | -0.35366 | 0.14958 | -0.26142 | 61.909 | 0.020727 | -0.12885 | -0.15684 | -0.034593 | 121.5524 | 121.3519 | 121.2009 | 61.827 | -121.4152 | 121.2932 | 121.3977 | 121.52 | 61.8946 | -121.405
416.5469 | 121.7468 | -61.6653 | 59.7702 | -0.005418 | -0.02966 | 0.00050001 | 0.054944 | -0.0048779 | 0.050965 | -0.019381 | -0.0011537 | -0.0012306 | -0.0037325 | 0.01422 | -0.0077491 | -59.1609 | -0.007751 | -61.7099 | 59.7131 | 59.5218 | 59.3662 | -61.7 | 0.069728 | 0.059882 | -61.814 | 59.4584 | 59.563 | 59.6807 | -61.6897 | -0.034617 | -0.057103 | 2.5045 | -0.044552 | -0.009935 | -0.2484 | -0.40401 | -0.024371 | -0.31177 | 61.7351 | -0.14865 | -0.12427 | -0.20719 | -0.089526 | 121.3784 | 121.1871 | 121.0315 | 61.6576 | -121.4702 | 121.1238 | 121.2284 | 121.346 | 61.7252 | -121.4599
418.2344 | 121.8201 | -61.615 | 59.8206 | 0.002213 | -0.029019 | 0.00050001 | 0.054731 | -0.0048779 | 0.051179 | -0.0041205 | -0.0013673 | -0.0012306 | -0.0037325 | 0.014647 | -0.0081765 | -59.1792 | -0.003172 | -61.7145 | 59.7085 | 59.5264 | 59.3616 | -61.6954 | 0.074307 | 0.064461 | -61.8231 | 59.4676 | 59.5584 | 59.6761 | -61.6897 | -0.080392 | -0.11203 | 2.4358 | -0.099484 | -0.019092 | -0.29418 | -0.45895 | -0.074725 | -0.35297 | 61.6893 | -0.20816 | -0.13343 | -0.26212 | -0.14446 | 121.3235 | 121.1414 | 120.9766 | 61.6118 | -121.5159 | 121.0826 | 121.1734 | 121.2911 | 61.6795 | -121.5103
419.9844 | 121.7102 | -61.7249 | 59.7473 | -0.005418 | -0.029233 | 0.00050001 | 0.054731 | -0.0048779 | 0.051392 | -0.0041205 | -0.00094006 | -0.001017 | -0.0037325 | 0.014434 | -0.0077491 | -59.0785 | -0.012329 | -61.7007 | 59.7039 | 59.5264 | 59.3616 | -61.6954 | 0.074307 | 0.059882 | -61.8094 | 59.4584 | 59.5584 | 59.6898 | -61.6851 | 0.029472 | -0.043371 | 2.6464 | 0.024114 | -0.005358 | -0.22094 | -0.3857 | 0.039717 | -0.28888 | 61.7992 | -0.084557 | -0.12427 | -0.18888 | -0.05748 | 121.4288 | 121.2512 | 121.0865 | 61.7125 | -121.4427 | 121.1833 | 121.2833 | 121.4147 | 61.7847 | -121.4325
421.7344 | 121.6553 | -61.8256 | 59.7336 | -0.005418 | -0.029446 | 0.00071361 | 0.054731 | -0.0050917 | 0.050965 | -0.0041205 | -0.00094006 | -0.0014444 | -0.0035187 | 0.014434 | -0.0077491 | -59.0693 | -0.003172 | -61.7053 | 59.7085 | 59.5218 | 59.3616 | -61.7 | 0.078886 | 0.064461 | -61.814 | 59.463 | 59.5584 | 59.6853 | -61.6806 | 0.1256 | -0.02506 | 2.7562 | 0.12024 | -0.005357 | -0.21178 | -0.37197 | 0.145 | -0.27057 | 61.9044 | 0.011572 | -0.13343 | -0.17515 | -0.048326 | 121.5341 | 121.3474 | 121.1872 | 61.8224 | -121.4335 | 121.2886 | 121.384 | 121.5108 | 61.89 | -121.4141
423.4375 | 121.6736 | -61.7706 | 59.729 | 0.009844 | -0.029446 | 0.00050001 | 0.055158 | -0.0046643 | 0.050538 | -0.011751 | -0.0013673 | -0.0014444 | -0.0035187 | 0.01422 | -0.0077491 | -59.0647 | -0.007751 | -61.7053 | 59.7085 | 59.5218 | 59.357 | -61.6954 | 0.078886 | 0.073618 | -61.814 | 59.463 | 59.5584 | 59.6807 | -61.6806 | 0.075248 | -0.020482 | 2.7059 | 0.065312 | -0.009936 | -0.20721 | -0.37197 | 0.090072 | -0.26599 | 61.8495 | -0.04336 | -0.13343 | -0.17057 | -0.048327 | 121.4792 | 121.2924 | 121.1277 | 61.7629 | -121.4244 | 121.2336 | 121.3291 | 121.4513 | 61.8442 | -121.4096
425.1875 | 121.8063 | -61.615 | 59.8068 | 0.002213 | -0.029446 | 0.00050001 | 0.054731 | -0.0048779 | 0.050752 | 0.01114 | -0.00094006 | -0.0012306 | -0.0037325 | 0.014647 | -0.0077491 | -59.1838 | -0.007751 | -61.7145 | 59.7177 | 59.5355 | 59.3616 | -61.7045 | 0.069728 | 0.059882 | -61.814 | 59.4584 | 59.5584 | 59.6853 | -61.6851 | -0.089549 | -0.089146 | 2.4312 | -0.099484 | -0.009935 | -0.27129 | -0.44521 | -0.070147 | -0.34839 | 61.6847 | -0.199 | -0.12885 | -0.24839 | -0.12157 | 121.3327 | 121.1505 | 120.9766 | 61.6072 | -121.5114 | 121.0734 | 121.1734 | 121.3002 | 61.6749 | -121.492
426.9219 | 121.7285 | -61.7477 | 59.729 | -0.005418 | -0.029446 | 0.00050001 | 0.054731 | -0.0044507 | 0.050752 | -0.0041205 | -0.0011537 | -0.0012306 | -0.0033051 | 0.014434 | -0.0079629 | -59.0785 | -0.007751 | -61.7191 | 59.7131 | 59.5264 | 59.3662 | -61.6954 | 0.078886 | 0.059882 | -61.8094 | 59.4539 | 59.563 | 59.6853 | -61.6897 | 0.05236 | -0.015904 | 2.6693 | 0.028689 | -0.023671 | -0.20263 | -0.36281 | 0.058027 | -0.27515 | 61.8266 | -0.061669 | -0.1197 | -0.16599 | -0.043748 | 121.4608 | 121.2741 | 121.1139 | 61.74 | -121.4244 | 121.2016 | 121.3108 | 121.433 | 61.8076 | -121.4187
428.6719 | 121.756 | -61.6425 | 59.8251 | -0.005418 | -0.029446 | 0.00028641 | 0.054731 | -0.0048779 | 0.050752 | 0.00351 | -0.0011537 | -0.0014444 | -0.0035187 | 0.014434 | -0.0075355 | -59.1655 | -0.007751 | -61.7145 | 59.7131 | 59.5172 | 59.3616 | -61.7045 | 0.069728 | 0.055303 | -61.814 | 59.463 | 59.563 | 59.6807 | -61.6851 | -0.062083 | -0.11203 | 2.477 | -0.072018 | -0.009935 | -0.30791 | -0.46352 | -0.042681 | -0.36212 | 61.7122 | -0.17153 | -0.12885 | -0.26212 | -0.14446 | 121.3556 | 121.1597 | 121.0041 | 61.6347 | -121.5297 | 121.1055 | 121.2055 | 121.3231 | 61.6978 | -121.5103
430.4219 | 121.6782 | -61.7706 | 59.7153 | -0.013049 | -0.02966 | 0.00071361 | 0.054944 | -0.0050917 | 0.051179 | -0.019381 | -0.00094006 | -0.0012306 | -0.0035187 | 0.014434 | -0.0081765 | -59.0739 | -0.007751 | -61.7145 | 59.7131 | 59.531 | 59.3662 | -61.7 | 0.074307 | 0.064461 | -61.814 | 59.4539 | 59.5584 | 59.6761 | -61.6851 | 0.070669 | -0.002171 | 2.6967 | 0.056156 | -0.014513 | -0.18431 | -0.34908 | 0.085493 | -0.26142 | 61.8449 | -0.04336 | -0.12885 | -0.15684 | -0.039172 | 121.4837 | 121.3016 | 121.1368 | 61.7629 | -121.4152 | 121.2245 | 121.3291 | 121.4467 | 61.8351 | -121.4004
432.1094 | 121.8246 | -61.6013 | 59.7885 | 0.002213 | -0.029874 | 0.00050001 | 0.054944 | -0.0050917 | 0.050965 | -0.0041205 | -0.0013673 | -0.001658 | -0.0037325 | 0.014434 | -0.0075355 | -59.1975 | -0.007751 | -61.7145 | 59.7131 | 59.531 | 59.3708 | -61.7 | 0.074307 | 0.055303 | -61.814 | 59.4584 | 59.5584 | 59.6807 | -61.6897 | -0.098704 | -0.075413 | 2.4037 | -0.11322 | -0.014513 | -0.25756 | -0.41775 | -0.088458 | -0.33008 | 61.6756 | -0.21273 | -0.12427 | -0.23008 | -0.10784 | 121.3144 | 121.1322 | 120.972 | 61.5935 | -121.4885 | 121.0597 | 121.1597 | 121.2819 | 61.6566 | -121.4782
433.8594 | 121.6873 | -61.7935 | 59.729 | 0.002213 | -0.029446 | 0.00050001 | 0.054731 | -0.0048779 | 0.050752 | -0.0041205 | -0.0013673 | -0.0012306 | -0.0037325 | 0.014647 | -0.0075355 | -59.0739 | -0.003172 | -61.7145 | 59.7131 | 59.5264 | 59.3662 | -61.6954 | 0.069728 | 0.059882 | -61.8186 | 59.463 | 59.563 | 59.6807 | -61.6806 | 0.098136 | -0.015904 | 2.7196 | 0.079044 | -0.019092 | -0.20263 | -0.36281 | 0.11296 | -0.26599 | 61.8632 | -0.02505 | -0.13801 | -0.16599 | -0.048327 | 121.5066 | 121.3199 | 121.1597 | 61.7903 | -121.4244 | 121.2565 | 121.3565 | 121.4742 | 61.8534 | -121.4096
435.6094 | 121.7102 | -61.6837 | 59.8251 | 0.002213 | -0.02966 | 0.00028641 | 0.054944 | -0.0048779 | 0.050965 | -0.0041205 | -0.0013673 | -0.0012306 | -0.0030915 | 0.014861 | -0.0081765 | -59.1517 | -0.012329 | -61.7053 | 59.7131 | 59.531 | 59.3616 | -61.6954 | 0.074307 | 0.055303 | -61.8186 | 59.463 | 59.563 | 59.6761 | -61.6897 | -0.011727 | -0.11203 | 2.5319 | -0.021663 | -0.009936 | -0.29418 | -0.46352 | -0.00606 | -0.36212 | 61.758 | -0.13491 | -0.12885 | -0.26212 | -0.14903 | 121.3968 | 121.2146 | 121.0453 | 61.6713 | -121.5205 | 121.1467 | 121.2467 | 121.3598 | 61.739 | -121.5148
437.2969 | 121.788 | -61.6745 | 59.8068 | -0.005418 | -0.029446 | 0.00050001 | 0.054944 | -0.0046643 | 0.050538 | -0.0041205 | -0.0013673 | -0.0012306 | -0.0037325 | 0.014434 | -0.0079629 | -59.1792 | -0.012329 | -61.7099 | 59.6994 | 59.531 | 59.3662 | -61.6954 | 0.074307 | 0.059882 | -61.814 | 59.463 | 59.5584 | 59.6898 | -61.6897 | -0.020882 | -0.10746 | 2.4953 | -0.035396 | -0.014514 | -0.27587 | -0.44063 | -0.015215 | -0.34381 | 61.7488 | -0.13949 | -0.12427 | -0.24839 | -0.11699 | 121.3739 | 121.2055 | 121.0407 | 61.6622 | -121.5022 | 121.1375 | 121.2329 | 121.3643 | 61.7344 | -121.4965
439.0469 | 121.6873 | -61.8164 | 59.7015 | 0.002213 | -0.029446 | 0.00050001 | 0.055158 | -0.0048779 | 0.050752 | -0.0041205 | -0.0015809 | -0.001658 | -0.0041597 | 0.014647 | -0.0081765 | -59.0785 | -0.007751 | -61.7099 | 59.7131 | 59.531 | 59.3662 | -61.6954 | 0.074307 | 0.059882 | -61.814 | 59.4676 | 59.563 | 59.6807 | -61.6806 | 0.12102 | 0.011562 | 2.7379 | 0.10651 | -0.014514 | -0.17058 | -0.33535 | 0.13585 | -0.23395 | 61.8907 | 0.002416 | -0.13343 | -0.13853 | -0.020861 | 121.5295 | 121.3474 | 121.1826 | 61.8087 | -121.3969 | 121.284 | 121.3794 | 121.4971 | 61.8763 | -121.3821
440.7812 | 121.7606 | -61.6974 | 59.7473 | -0.013049 | -0.030087 | 0.00050001 | 0.054731 | -0.0046643 | 0.050752 | -0.0041205 | -0.0015809 | -0.0014444 | -0.0037325 | 0.014647 | -0.0081765 | -59.1334 | -0.007751 | -61.7099 | 59.7131 | 59.531 | 59.3708 | -61.6954 | 0.083464 | 0.059882 | -61.8094 | 59.4676 | 59.563 | 59.6807 | -61.6806 | 0.002006 | -0.034214 | 2.564 | -0.012508 | -0.014514 | -0.21636 | -0.37655 | 0.01683 | -0.27972 | 61.7809 | -0.11202 | -0.12885 | -0.1843 | -0.066637 | 121.4105 | 121.2283 | 121.0682 | 61.6896 | -121.4427 | 121.165 | 121.2604 | 121.3781 | 61.7573 | -121.4279
442.4688 | 121.7651 | -61.6653 | 59.7656 | -0.005418 | -0.029874 | 0.00071361 | 0.054731 | -0.0050917 | 0.050752 | -0.011751 | -0.0013673 | -0.0014444 | -0.0037325 | 0.014434 | -0.0079629 | -59.1609 | -0.012329 | -61.7145 | 59.7085 | 59.5264 | 59.3662 | -61.6954 | 0.078886 | 0.059882 | -61.814 | 59.463 | 59.5539 | 59.6807 | -61.6897 | -0.030038 | -0.057103 | 2.5045 | -0.04913 | -0.019092 | -0.23925 | -0.39943 | -0.024371 | -0.30261 | 61.7442 | -0.14865 | -0.12427 | -0.21177 | -0.084948 | 121.3739 | 121.1917 | 121.0315 | 61.653 | -121.461 | 121.1284 | 121.2192 | 121.346 | 61.7252 | -121.4553
444.2188 | 121.8018 | -61.6745 | 59.7931 | -0.005418 | -0.029874 | 0.00071361 | 0.054731 | -0.0046643 | 0.051179 | -0.011751 | -0.0015809 | -0.0012306 | -0.0035187 | 0.014434 | -0.0081765 | -59.1838 | -0.007751 | -61.7099 | 59.7131 | 59.5172 | 59.357 | -61.6954 | 0.069728 | 0.064461 | -61.8094 | 59.4676 | 59.5584 | 59.6853 | -61.676 | -0.020882 | -0.079991 | 2.4907 | -0.035396 | -0.014514 | -0.27587 | -0.43606 | -0.001479 | -0.3255 | 61.7442 | -0.13491 | -0.13343 | -0.23466 | -0.10783 | 121.3876 | 121.1917 | 121.0315 | 61.6667 | -121.4885 | 121.1421 | 121.2329 | 121.3598 | 61.739 | -121.4691
445.9062 | 121.7239 | -61.7157 | 59.7794 | -0.005418 | -0.02966 | 0.00028641 | 0.054944 | -0.0050917 | 0.050752 | -0.011751 | -0.0013673 | -0.0014444 | -0.0037325 | 0.014434 | -0.0081765 | -59.0785 | -0.012329 | -61.7145 | 59.7085 | 59.531 | 59.3662 | -61.7045 | 0.074307 | 0.064461 | -61.8094 | 59.4539 | 59.5584 | 59.6807 | -61.6897 | 0.011159 | -0.070836 | 2.6372 | 0.001224 | -0.009935 | -0.2484 | -0.41317 | 0.025983 | -0.3255 | 61.79 | -0.093713 | -0.1197 | -0.22093 | -0.098681 | 121.4242 | 121.2467 | 121.0819 | 61.7034 | -121.4839 | 121.1696 | 121.2741 | 121.3964 | 61.7802 | -121.4691
447.6406 | 121.701 | -61.6837 | 59.8297 | 0.002213 | -0.029874 | 0.00028641 | 0.054944 | -0.0050917 | 0.051179 | -0.0041205 | -0.0011537 | -0.0014444 | -0.0037325 | 0.014647 | -0.0081765 | -59.138 | -0.012329 | -61.7145 | 59.7085 | 59.531 | 59.3708 | -61.6954 | 0.069728 | 0.050725 | -61.8186 | 59.4584 | 59.563 | 59.6761 | -61.6943 | -0.011727 | -0.12119 | 2.5457 | -0.030819 | -0.019092 | -0.29875 | -0.45894 | -0.010639 | -0.37128 | 61.7534 | -0.13491 | -0.12427 | -0.2667 | -0.15361 | 121.3922 | 121.2146 | 121.0544 | 61.6713 | -121.5251 | 121.1421 | 121.2467 | 121.3598 | 61.7344 | -121.524
449.3281 | 121.8246 | -61.6379 | 59.7931 | -0.02068 | -0.02966 | 0.00071361 | 0.054944 | -0.0048779 | 0.050752 | -0.0041205 | -0.00094006 | -0.0012306 | -0.0037325 | 0.014647 | -0.0079629 | -59.1838 | -0.012329 | -61.7191 | 59.7085 | 59.531 | 59.3616 | -61.7 | 0.069728 | 0.055303 | -61.8186 | 59.4584 | 59.563 | 59.6807 | -61.6851 | -0.062083 | -0.084569 | 2.4541 | -0.081175 | -0.019092 | -0.26213 | -0.43148 | -0.047259 | -0.33466 | 61.7076 | -0.18069 | -0.13343 | -0.23008 | -0.11241 | 121.3464 | 121.1688 | 120.9995 | 61.6255 | -121.4931 | 121.0963 | 121.2009 | 121.3186 | 61.6932 | -121.4782
451.0781 | 121.7194 | -61.7477 | 59.7519 | -0.013049 | -0.02966 | 0.00050001 | 0.054944 | -0.0046643 | 0.050538 | -0.011751 | -0.0013673 | -0.001658 | -0.0035187 | 0.014647 | -0.0079629 | -59.0693 | -0.012329 | -61.7191 | 59.7131 | 59.5218 | 59.3708 | -61.6954 | 0.083464 | 0.055303 | -61.814 | 59.4584 | 59.563 | 59.6853 | -61.6897 | 0.05236 | -0.038792 | 2.6784 | 0.028689 | -0.023671 | -0.23009 | -0.38112 | 0.058027 | -0.29346 | 61.8312 | -0.066248 | -0.12427 | -0.18888 | -0.066636 | 121.4608 | 121.2695 | 121.1185 | 61.7354 | -121.4473 | 121.2062 | 121.3108 | 121.433 | 61.803 | -121.4416
452.8125 | 121.7697 | -61.7203 | 59.7015 | -0.005418 | -0.02966 | 0.00028641 | 0.054731 | -0.0053053 | 0.050752 | -0.0041205 | -0.0015809 | -0.0014444 | -0.0037325 | 0.014434 | -0.0081765 | -59.1288 | -0.007751 | -61.7145 | 59.7085 | 59.5218 | 59.3708 | -61.6908 | 0.078886 | 0.064461 | -61.814 | 59.4676 | 59.563 | 59.6853 | -61.6806 | 0.029473 | 0.006984 | 2.5914 | 0.005802 | -0.023671 | -0.17974 | -0.33077 | 0.039718 | -0.23395 | 61.7992 | -0.093714 | -0.13343 | -0.13853 | -0.016282 | 121.4288 | 121.2421 | 121.091 | 61.7125 | -121.3923 | 121.1879 | 121.2833 | 121.4055 | 61.7847 | -121.3821
454.5625 | 121.7194 | -61.7523 | 59.7336 | -0.005418 | -0.029874 | 0.00050001 | 0.054944 | -0.0048779 | 0.050538 | 0.01114 | -0.0011537 | -0.0012306 | -0.0035187 | 0.014647 | -0.0079629 | -59.083 | -0.012329 | -61.7145 | 59.7085 | 59.5355 | 59.3616 | -61.6954 | 0.074307 | 0.055303 | -61.814 | 59.4493 | 59.5584 | 59.6807 | -61.6806 | 0.056937 | -0.02506 | 2.6693 | 0.037845 | -0.019092 | -0.19805 | -0.37197 | 0.071761 | -0.2843 | 61.8266 | -0.061671 | -0.13343 | -0.17515 | -0.052905 | 121.4608 | 121.2879 | 121.1139 | 61.74 | -121.429 | 121.2016 | 121.3108 | 121.433 | 61.8076 | -121.4141
456.2344 | 121.7514 | -61.6699 | 59.7748 | 0.002213 | -0.02966 | 0.00050001 | 0.054731 | -0.0048779 | 0.050752 | -0.011751 | -0.0011537 | -0.001017 | -0.0039461 | 0.014861 | -0.0083901 | -59.1609 | -0.007751 | -61.7099 | 59.7039 | 59.5218 | 59.3662 | -61.7 | 0.083464 | 0.050725 | -61.814 | 59.463 | 59.5676 | 59.6898 | -61.6851 | -0.030039 | -0.070837 | 2.509 | -0.039974 | -0.009935 | -0.25298 | -0.40859 | -0.015215 | -0.31177 | 61.7534 | -0.14407 | -0.12885 | -0.20719 | -0.084946 | 121.3739 | 121.1917 | 121.0361 | 61.6622 | -121.4747 | 121.1329 | 121.2375 | 121.3598 | 61.7206 | -121.4599
457.9844 | 121.7148 | -61.7203 | 59.7794 | 0.002213 | -0.030301 | 7.2612e-05 | 0.054517 | -0.0050917 | 0.050752 | 0.00351 | -0.0011537 | -0.001017 | -0.0037325 | 0.014861 | -0.0081765 | -59.1014 | -0.012329 | -61.7099 | 59.7131 | 59.531 | 59.3662 | -61.6908 | 0.074307 | 0.055303 | -61.8094 | 59.4584 | 59.563 | 59.6807 | -61.6897 | 0.029473 | -0.066258 | 2.6189 | 0.01038 | -0.019093 | -0.2484 | -0.41317 | 0.030561 | -0.32092 | 61.7946 | -0.089135 | -0.1197 | -0.21635 | -0.098681 | 121.4334 | 121.2512 | 121.0865 | 61.7079 | -121.4702 | 121.1787 | 121.2833 | 121.401 | 61.7756 | -121.4691
459.75 | 121.7606 | -61.6333 | 59.8297 | 0.009844 | -0.030087 | 0.00071361 | 0.054517 | -0.0048779 | 0.050538 | -0.011751 | -0.0011537 | -0.001017 | -0.0035187 | 0.014647 | -0.0081765 | -59.1655 | -0.007751 | -61.7145 | 59.7085 | 59.5355 | 59.3662 | -61.6954 | 0.074307 | 0.055303 | -61.814 | 59.4584 | 59.563 | 59.6853 | -61.6943 | -0.062081 | -0.12119 | 2.4678 | -0.081173 | -0.019092 | -0.29418 | -0.46352 | -0.060993 | -0.37128 | 61.7076 | -0.18069 | -0.1197 | -0.2667 | -0.14446 | 121.3418 | 121.1688 | 120.9995 | 61.6256 | -121.5251 | 121.0917 | 121.1963 | 121.3186 | 61.6886 | -121.524
461.4375 | 121.7514 | -61.7157 | 59.7748 | 0.002213 | -0.029874 | 0.00050001 | 0.054944 | -0.0053053 | 0.050324 | -0.0041205 | -0.0011537 | -0.0012306 | -0.0035187 | 0.014647 | -0.0083901 | -59.1655 | -0.012329 | -61.7145 | 59.7085 | 59.5218 | 59.3662 | -61.7 | 0.069728 | 0.059882 | -61.8094 | 59.4676 | 59.5722 | 59.6853 | -61.6897 | 0.015737 | -0.066258 | 2.5502 | 0.001224 | -0.014513 | -0.25298 | -0.40859 | 0.025983 | -0.30719 | 61.7854 | -0.093713 | -0.1197 | -0.20261 | -0.089524 | 121.4242 | 121.2375 | 121.0819 | 61.7034 | -121.4747 | 121.1833 | 121.2879 | 121.401 | 61.7756 | -121.4645
463.1875 | 121.6644 | -61.7065 | 59.816 | -0.005418 | -0.02966 | 0.00071361 | 0.054731 | -0.0046643 | 0.050965 | -0.019381 | -0.0011537 | -0.0012306 | -0.0037325 | 0.014647 | -0.0081765 | -59.1059 | -0.016908 | -61.7053 | 59.7085 | 59.531 | 59.3662 | -61.7 | 0.074307 | 0.055303 | -61.8094 | 59.4584 | 59.5676 | 59.6761 | -61.6897 | 0.006582 | -0.10746 | 2.6006 | 0.001225 | -0.005357 | -0.28502 | -0.44979 | 0.016828 | -0.35755 | 61.7809 | -0.10287 | -0.1197 | -0.24839 | -0.13988 | 121.4151 | 121.2375 | 121.0727 | 61.6896 | -121.5159 | 121.165 | 121.2741 | 121.3826 | 61.7618 | -121.5057
464.9531 | 121.7194 | -61.734 | 59.7656 | -0.013049 | -0.030301 | 0.00050001 | 0.054731 | -0.0053053 | 0.050965 | 0.00351 | -0.00094006 | -0.001017 | -0.0035187 | 0.014861 | -0.0079629 | -59.0876 | -0.007751 | -61.7191 | 59.7131 | 59.5218 | 59.3616 | -61.7045 | 0.074307 | 0.046146 | -61.8048 | 59.463 | 59.5539 | 59.6761 | -61.6943 | 0.02947 | -0.052525 | 2.6464 | 0.014956 | -0.014514 | -0.24383 | -0.40401 | 0.039715 | -0.30261 | 61.8083 | -0.070823 | -0.11054 | -0.21177 | -0.089526 | 121.4471 | 121.2558 | 121.0956 | 61.7263 | -121.4702 | 121.197 | 121.2879 | 121.4101 | 61.7802 | -121.4599
466.6406 | 121.8155 | -61.6425 | 59.8022 | 0.002213 | -0.030301 | 0.00071361 | 0.055158 | -0.0048779 | 0.050111 | -0.0041205 | -0.0011537 | -0.0014444 | -0.0037325 | 0.014434 | -0.0079629 | -59.1884 | -0.007751 | -61.7053 | 59.7039 | 59.5218 | 59.3662 | -61.7 | 0.074307 | 0.050725 | -61.8003 | 59.4584 | 59.5584 | 59.6807 | -61.6851 | -0.057505 | -0.098303 | 2.4541 | -0.062862 | -0.005357 | -0.28045 | -0.43606 | -0.042681 | -0.34381 | 61.7168 | -0.1578 | -0.11512 | -0.24381 | -0.12157 | 121.3464 | 121.1643 | 121.0086 | 61.6347 | -121.5022 | 121.1009 | 121.2009 | 121.3231 | 61.6932 | -121.4874
468.375 | 121.7789 | -61.6196 | 59.816 | -0.005418 | -0.030301 | 0.00050001 | 0.054944 | -0.0055189 | 0.050538 | -0.011751 | -0.0013673 | -0.0014444 | -0.0037325 | 0.014861 | -0.0081765 | -59.1838 | -0.007751 | -61.7099 | 59.7131 | 59.5264 | 59.3616 | -61.7 | 0.069728 | 0.055303 | -61.8094 | 59.4539 | 59.5676 | 59.6853 | -61.6897 | -0.080393 | -0.10288 | 2.4358 | -0.090328 | -0.009935 | -0.2896 | -0.45437 | -0.070147 | -0.36212 | 61.6893 | -0.18984 | -0.1197 | -0.24839 | -0.13072 | 121.3327 | 121.1459 | 120.9812 | 61.6118 | -121.5159 | 121.0734 | 121.1872 | 121.3048 | 61.6749 | -121.5057
470.125 | 121.701 | -61.8027 | 59.7061 | -0.005418 | -0.029874 | 0.00071361 | 0.054731 | -0.0053053 | 0.050538 | -0.0041205 | -0.00094006 | -0.0012306 | -0.0037325 | 0.014861 | -0.0079629 | -59.0876 | -0.007751 | -61.7053 | 59.7085 | 59.5264 | 59.3662 | -61.6954 | 0.074307 | 0.055303 | -61.8094 | 59.4539 | 59.5676 | 59.6853 | -61.6897 | 0.10729 | 0.002406 | 2.715 | 0.097355 | -0.009936 | -0.17974 | -0.33993 | 0.11296 | -0.25226 | 61.877 | -0.006738 | -0.1197 | -0.13853 | -0.02086 | 121.5112 | 121.3291 | 121.1689 | 61.7949 | -121.4015 | 121.2565 | 121.3703 | 121.4879 | 61.858 | -121.3958
471.875 | 121.6919 | -61.7661 | 59.7107 | -0.005418 | -0.030301 | 0.00028641 | 0.054517 | -0.0050917 | 0.050538 | -0.011751 | -0.00094006 | -0.0012306 | -0.0037325 | 0.014861 | -0.0083901 | -59.0785 | -0.003172 | -61.7099 | 59.7131 | 59.531 | 59.3616 | -61.7091 | 0.083464 | 0.059882 | -61.814 | 59.463 | 59.563 | 59.6898 | -61.6897 | 0.056934 | 0.002407 | 2.6876 | 0.056156 | -0.000778 | -0.17974 | -0.34908 | 0.076337 | -0.24768 | 61.8495 | -0.047938 | -0.12427 | -0.14768 | -0.020859 | 121.4792 | 121.297 | 121.1277 | 61.7629 | -121.4198 | 121.2291 | 121.3291 | 121.4559 | 61.8259 | -121.4004
473.625 | 121.6919 | -61.7569 | 59.697 | -0.005418 | -0.030087 | 0.00071361 | 0.054731 | -0.0050917 | 0.050538 | -0.0041205 | -0.0013673 | -0.0012306 | -0.0037325 | 0.014647 | -0.0079629 | -59.0693 | -0.007751 | -61.7099 | 59.7039 | 59.531 | 59.3662 | -61.7 | 0.069728 | 0.064461 | -61.8094 | 59.4539 | 59.563 | 59.6853 | -61.6806 | 0.056936 | 0.006983 | 2.6876 | 0.047001 | -0.009935 | -0.166 | -0.33077 | 0.076339 | -0.2431 | 61.8266 | -0.052514 | -0.12885 | -0.13395 | -0.011704 | 121.4608 | 121.2879 | 121.1231 | 61.7491 | -121.3969 | 121.2108 | 121.3199 | 121.4422 | 61.8214 | -121.3775
475.3125 | 121.7422 | -61.7615 | 59.6832 | -0.013049 | -0.029874 | 0.00050001 | 0.054731 | -0.0050917 | 0.050752 | -0.011751 | -0.0013673 | -0.0012306 | -0.0037325 | 0.014861 | -0.0083901 | -59.0968 | -0.003172 | -61.7145 | 59.7085 | 59.531 | 59.3708 | -61.6954 | 0.078886 | 0.059882 | -61.8094 | 59.463 | 59.563 | 59.6807 | -61.6851 | 0.066093 | 0.025294 | 2.6647 | 0.047001 | -0.019092 | -0.15227 | -0.31246 | 0.076338 | -0.22022 | 61.8404 | -0.047936 | -0.12427 | -0.12022 | -0.002551 | 121.47 | 121.2924 | 121.1322 | 61.7583 | -121.3786 | 121.2245 | 121.3245 | 121.4422 | 61.8214 | -121.3684
477.0469 | 121.6553 | -61.821 | 59.6924 | -0.005418 | -0.030087 | 0.00050001 | 0.054731 | -0.0050917 | 0.050752 | -0.0041205 | -0.0011537 | -0.001017 | -0.0035187 | 0.014647 | -0.0081765 | -59.0785 | -0.003172 | -61.7145 | 59.6994 | 59.531 | 59.3662 | -61.6908 | 0.074307 | 0.059882 | -61.8094 | 59.4584 | 59.5584 | 59.6761 | -61.6851 | 0.13018 | 0.006982 | 2.7425 | 0.10651 | -0.023671 | -0.16143 | -0.32619 | 0.13585 | -0.23395 | 61.8953 | 0.011573 | -0.12427 | -0.13395 | -0.016284 | 121.5203 | 121.3519 | 121.1872 | 61.8178 | -121.3832 | 121.2794 | 121.3794 | 121.4971 | 61.8809 | -121.3775
478.7969 | 121.7697 | -61.6608 | 59.7794 | -0.005418 | -0.030087 | 0.00050001 | 0.055158 | -0.0050917 | 0.050752 | -0.0041205 | -0.00094006 | -0.0012306 | -0.0039461 | 0.015075 | -0.0081765 | -59.17 | -0.007751 | -61.7145 | 59.7039 | 59.5264 | 59.3662 | -61.6954 | 0.069728 | 0.059882 | -61.814 | 59.4584 | 59.5584 | 59.6807 | -61.6943 | -0.034615 | -0.075415 | 2.4907 | -0.053707 | -0.019092 | -0.25298 | -0.41317 | -0.033527 | -0.32092 | 61.7305 | -0.15322 | -0.1197 | -0.22093 | -0.098681 | 121.3647 | 121.1871 | 121.027 | 61.653 | -121.4747 | 121.1192 | 121.2192 | 121.3414 | 61.7206 | -121.4737
480.5469 | 121.6782 | -61.7661 | 59.7107 | -0.005418 | -0.030515 | 0.00028641 | 0.054944 | -0.0053053 | 0.050965 | -0.0041205 | -0.0013673 | -0.00080338 | -0.0039461 | 0.014647 | -0.0083901 | -59.0693 | -0.007751 | -61.7053 | 59.7131 | 59.5218 | 59.3616 | -61.6954 | 0.083464 | 0.059882 | -61.8094 | 59.4584 | 59.563 | 59.6807 | -61.6851 | 0.07067 | 0.002407 | 2.6967 | 0.060734 | -0.009936 | -0.18889 | -0.34908 | 0.080915 | -0.25226 | 61.8495 | -0.043359 | -0.12427 | -0.14768 | -0.030016 | 121.4792 | 121.2879 | 121.1277 | 61.7583 | -121.4061 | 121.2245 | 121.3291 | 121.4467 | 61.8259 | -121.3958
482.2188 | 121.8018 | -61.5784 | 59.7977 | 0.002213 | -0.030301 | 0.00071361 | 0.054517 | -0.0050917 | 0.050752 | 0.00351 | -0.00094006 | -0.0012306 | -0.0039461 | 0.014861 | -0.0079629 | -59.1884 | -0.012329 | -61.7053 | 59.7039 | 59.5264 | 59.3662 | -61.6954 | 0.074307 | 0.050725 | -61.8094 | 59.463 | 59.5584 | 59.6853 | -61.6897 | -0.11701 | -0.093725 | 2.39 | -0.12695 | -0.009936 | -0.27129 | -0.43148 | -0.11135 | -0.33466 | 61.6527 | -0.23104 | -0.1197 | -0.23924 | -0.11241 | 121.2823 | 121.1047 | 120.9446 | 61.566 | -121.4931 | 121.0414 | 121.1368 | 121.2636 | 61.6291 | -121.4874
483.9688 | 121.7514 | -61.7065 | 59.7107 | -0.005418 | -0.030728 | 0.00050001 | 0.054517 | -0.0050917 | 0.050752 | -0.011751 | -0.00094006 | -0.0014444 | -0.0033051 | 0.014861 | -0.0083901 | -59.1288 | -0.007751 | -61.7053 | 59.7177 | 59.531 | 59.357 | -61.7045 | 0.078886 | 0.055303 | -61.814 | 59.4584 | 59.563 | 59.6898 | -61.6851 | 0.002004 | 0.006985 | 2.5777 | 0.001225 | -0.000779 | -0.17974 | -0.35366 | 0.021406 | -0.25226 | 61.7854 | -0.10745 | -0.12885 | -0.14768 | -0.020859 | 121.4242 | 121.2375 | 121.0636 | 61.6988 | -121.4152 | 121.165 | 121.2696 | 121.3964 | 61.7618 | -121.3958
485.7188 | 121.701 | -61.734 | 59.7198 | -0.005418 | -0.030301 | 0.00050001 | 0.054731 | -0.0050917 | 0.050538 | -0.0041205 | -0.0015809 | -0.0014444 | -0.0037325 | 0.015075 | -0.0079629 | -59.0693 | -0.007751 | -61.7053 | 59.7177 | 59.531 | 59.3616 | -61.7 | 0.069728 | 0.059882 | -61.814 | 59.4584 | 59.5584 | 59.6807 | -61.6851 | 0.034048 | -0.002171 | 2.6647 | 0.028691 | -0.005357 | -0.18889 | -0.35824 | 0.048872 | -0.26142 | 61.8037 | -0.079981 | -0.12885 | -0.16142 | -0.039172 | 121.4517 | 121.265 | 121.0956 | 61.7263 | -121.4198 | 121.1924 | 121.2924 | 121.4147 | 61.7939 | -121.405
487.4062 | 121.8063 | -61.5967 | 59.8206 | 0.002213 | -0.030301 | 0.00092741 | 0.054517 | -0.0048779 | 0.050752 | -0.0041205 | -0.00072626 | -0.00080338 | -0.0035187 | 0.014861 | -0.0079629 | -59.1792 | -0.007751 | -61.7099 | 59.7085 | 59.531 | 59.3662 | -61.6908 | 0.078886 | 0.055303 | -61.814 | 59.4539 | 59.5584 | 59.6807 | -61.6851 | -0.094123 | -0.11203 | 2.4175 | -0.11322 | -0.019093 | -0.2896 | -0.45437 | -0.088457 | -0.3667 | 61.6756 | -0.21731 | -0.12885 | -0.26212 | -0.13988 | 121.3052 | 121.1276 | 120.9629 | 61.5889 | -121.5114 | 121.0505 | 121.1551 | 121.2774 | 61.652 | -121.5057
489.1562 | 121.7148 | -61.734 | 59.7382 | -0.005418 | -0.030515 | 0.00050001 | 0.054517 | -0.0050917 | 0.050111 | -0.0041205 | -0.0011537 | -0.001658 | -0.0035187 | 0.015075 | -0.0081765 | -59.0785 | -0.012329 | -61.7007 | 59.7039 | 59.5264 | 59.3662 | -61.6954 | 0.074307 | 0.059882 | -61.8048 | 59.463 | 59.5584 | 59.6761 | -61.6897 | 0.038627 | -0.034216 | 2.6555 | 0.033269 | -0.005358 | -0.21178 | -0.37197 | 0.044294 | -0.27515 | 61.8083 | -0.070823 | -0.11512 | -0.17973 | -0.06206 | 121.438 | 121.2604 | 121.1002 | 61.7217 | -121.4335 | 121.197 | 121.2924 | 121.4101 | 61.7939 | -121.4279
490.9062 | 121.7194 | -61.7294 | 59.7656 | 0.002213 | -0.030301 | 0.00071361 | 0.054731 | -0.0050917 | 0.050538 | -0.011751 | -0.0011537 | -0.0012306 | -0.0039461 | 0.014861 | -0.0083901 | -59.0739 | -0.003172 | -61.7053 | 59.7085 | 59.5218 | 59.3662 | -61.6954 | 0.074307 | 0.050725 | -61.814 | 59.4584 | 59.5584 | 59.6853 | -61.6806 | 0.034049 | -0.057103 | 2.6555 | 0.024113 | -0.009936 | -0.24383 | -0.39943 | 0.048873 | -0.30719 | 61.8037 | -0.084559 | -0.13343 | -0.20719 | -0.080369 | 121.438 | 121.2512 | 121.0956 | 61.7263 | -121.461 | 121.1879 | 121.2879 | 121.4147 | 61.7802 | -121.4462
492.5938 | 121.7422 | -61.6882 | 59.7519 | 0.002213 | -0.030087 | 0.00071361 | 0.054517 | -0.0050917 | 0.050965 | -0.011751 | -0.0011537 | -0.0014444 | -0.0039461 | 0.014861 | -0.0086037 | -59.1334 | -0.003172 | -61.7053 | 59.7085 | 59.5218 | 59.3662 | -61.6908 | 0.078886 | 0.055303 | -61.8094 | 59.4676 | 59.563 | 59.6761 | -61.6851 | -0.002571 | -0.04337 | 2.5548 | -0.017086 | -0.014515 | -0.23009 | -0.3857 | 0.003095 | -0.2843 | 61.7671 | -0.12118 | -0.12427 | -0.18888 | -0.075793 | 121.3968 | 121.21 | 121.0544 | 61.6851 | -121.4427 | 121.1558 | 121.2512 | 121.3643 | 61.7435 | -121.437
494.3438 | 121.6736 | -61.8073 | 59.6924 | -0.028311 | -0.030728 | 0.00071361 | 0.054731 | -0.0053053 | 0.050538 | -0.019381 | -0.0015809 | -0.00080338 | -0.0037325 | 0.015075 | -0.0081765 | -59.0693 | -0.003172 | -61.6962 | 59.7177 | 59.531 | 59.3708 | -61.7045 | 0.078886 | 0.055303 | -61.8094 | 59.463 | 59.5584 | 59.6807 | -61.6897 | 0.10271 | 0.025295 | 2.7379 | 0.11109 | 0.008378 | -0.16143 | -0.32162 | 0.11754 | -0.22937 | 61.8861 | -0.00216 | -0.1197 | -0.13395 | -0.011706 | 121.5249 | 121.3382 | 121.178 | 61.8041 | -121.3969 | 121.2703 | 121.3657 | 121.4879 | 61.8626 | -121.3821
496.0938 | 121.7926 | -61.7569 | 59.6649 | -0.005418 | -0.030515 | 0.00028641 | 0.054517 | -0.0048779 | 0.050111 | 0.00351 | -0.0015809 | -0.001017 | -0.0039461 | 0.015075 | -0.0081765 | -59.1014 | 0.001407 | -61.7007 | 59.7085 | 59.5264 | 59.3753 | -61.6862 | 0.078886 | 0.059882 | -61.8094 | 59.4584 | 59.563 | 59.6761 | -61.6851 | 0.070673 | 0.043605 | 2.6555 | 0.056157 | -0.014516 | -0.13854 | -0.28957 | 0.07176 | -0.20648 | 61.8358 | -0.052514 | -0.12427 | -0.10191 | 0.011182 | 121.4654 | 121.2833 | 121.1322 | 61.7583 | -121.3511 | 121.2153 | 121.3199 | 121.433 | 61.8168 | -121.3501
497.7812 | 121.7972 | -61.6287 | 59.8022 | 0.002213 | -0.030728 | 0.00071361 | 0.054944 | -0.0055189 | 0.050111 | -0.011751 | -0.0013673 | -0.0014444 | -0.0033051 | 0.014861 | -0.0083901 | -59.1884 | -0.003172 | -61.7053 | 59.7039 | 59.5264 | 59.3616 | -61.6908 | 0.069728 | 0.059882 | -61.8094 | 59.4539 | 59.5584 | 59.6761 | -61.6943 | -0.06208 | -0.098303 | 2.4404 | -0.076595 | -0.014515 | -0.27587 | -0.44063 | -0.065571 | -0.34839 | 61.6985 | -0.18069 | -0.11512 | -0.24381 | -0.12615 | 121.3327 | 121.1551 | 120.9903 | 61.6256 | -121.493 | 121.0826 | 121.1872 | 121.3048 | 61.6886 | -121.4965
499.5312 | 121.6873 | -61.7935 | 59.7153 | -0.02068 | -0.030728 | 0.00050001 | 0.054731 | -0.0053053 | 0.050538 | -0.011751 | -0.0011537 | -0.0012306 | -0.0039461 | 0.014861 | -0.0086037 | -59.0785 | -0.012329 | -61.7007 | 59.7131 | 59.5264 | 59.3616 | -61.6954 | 0.083464 | 0.055303 | -61.8094 | 59.4676 | 59.563 | 59.6807 | -61.6851 | 0.098136 | -0.002171 | 2.715 | 0.092778 | -0.005358 | -0.18889 | -0.35366 | 0.10838 | -0.24768 | 61.877 | -0.015893 | -0.12427 | -0.15226 | -0.034594 | 121.5066 | 121.3199 | 121.1551 | 61.7812 | -121.4107 | 121.2611 | 121.3565 | 121.4742 | 61.8488 | -121.4004
501.2812 | 121.8246 | -61.6287 | 59.7656 | -0.013049 | -0.030515 | 7.2612e-05 | 0.054731 | -0.0050917 | 0.050752 | -0.019381 | -0.0013673 | -0.0014444 | -0.0037325 | 0.014861 | -0.0081765 | -59.1792 | -0.007751 | -61.7007 | 59.7039 | 59.5264 | 59.3616 | -61.6954 | 0.069728 | 0.055303 | -61.8003 | 59.463 | 59.5584 | 59.6807 | -61.6851 | -0.066659 | -0.061682 | 2.4495 | -0.072017 | -0.005358 | -0.23925 | -0.40401 | -0.056414 | -0.30261 | 61.6985 | -0.17153 | -0.11512 | -0.20719 | -0.084948 | 121.3327 | 121.1551 | 120.9903 | 61.621 | -121.461 | 121.0917 | 121.1872 | 121.3094 | 61.684 | -121.4508
503.0312 | 121.7331 | -61.734 | 59.7473 | -0.005418 | -0.030515 | 0.00028641 | 0.054517 | -0.0053053 | 0.050324 | -0.0041205 | -0.0013673 | -0.001017 | -0.0039461 | 0.015075 | -0.0081765 | -59.0785 | -0.003172 | -61.7099 | 59.7085 | 59.5264 | 59.3753 | -61.7045 | 0.069728 | 0.064461 | -61.8094 | 59.4676 | 59.5493 | 59.6761 | -61.6897 | 0.02947 | -0.038792 | 2.6555 | 0.024113 | -0.005357 | -0.22094 | -0.37197 | 0.044294 | -0.27972 | 61.8037 | -0.075402 | -0.1197 | -0.19804 | -0.071215 | 121.4425 | 121.2604 | 121.1094 | 61.7308 | -121.4519 | 121.2016 | 121.2833 | 121.4101 | 61.7985 | -121.437
504.7031 | 121.7239 | -61.7294 | 59.7702 | 0.002213 | -0.030515 | 0.00050001 | 0.054517 | -0.0053053 | 0.050538 | 0.00351 | -0.0011537 | -0.0012306 | -0.0037325 | 0.015288 | -0.0081765 | -59.0876 | -0.012329 | -61.7007 | 59.7085 | 59.5264 | 59.3616 | -61.6954 | 0.069728 | 0.059882 | -61.8048 | 59.4539 | 59.5584 | 59.6807 | -61.6897 | 0.034049 | -0.061681 | 2.6418 | 0.028691 | -0.005358 | -0.24383 | -0.40859 | 0.039716 | -0.31635 | 61.7992 | -0.075401 | -0.11512 | -0.21177 | -0.089526 | 121.438 | 121.2558 | 121.091 | 61.7171 | -121.4656 | 121.1833 | 121.2879 | 121.4101 | 61.7893 | -121.4599
506.4531 | 121.7926 | -61.6104 | 59.8297 | 0.002213 | -0.030728 | 0.00050001 | 0.054731 | -0.0050917 | 0.050324 | -0.019381 | -0.0011537 | -0.0012306 | -0.0035187 | 0.015288 | -0.0079629 | -59.1884 | -0.012329 | -61.7053 | 59.6948 | 59.5172 | 59.3616 | -61.7 | 0.074307 | 0.059882 | -61.8094 | 59.4584 | 59.5584 | 59.6807 | -61.6897 | -0.089548 | -0.13493 | 2.4221 | -0.094905 | -0.005357 | -0.31249 | -0.4681 | -0.079302 | -0.37128 | 61.6847 | -0.199 | -0.1197 | -0.27128 | -0.14903 | 121.3052 | 121.1276 | 120.972 | 61.5981 | -121.5297 | 121.0688 | 121.1688 | 121.2911 | 61.6703 | -121.5194
508.1406 | 121.788 | -61.7294 | 59.6649 | -0.005418 | -0.030728 | 0.00050001 | 0.054731 | -0.0053053 | 0.050752 | -0.011751 | -0.0013673 | -0.0014444 | -0.0037325 | 0.015075 | -0.0079629 | -59.0876 | -0.012329 | -61.6916 | 59.7131 | 59.5218 | 59.3708 | -61.6954 | 0.069728 | 0.064461 | -61.8094 | 59.4584 | 59.5584 | 59.6807 | -61.6897 | 0.034049 | 0.048183 | 2.6418 | 0.037848 | 0.003799 | -0.14312 | -0.29415 | 0.039716 | -0.20648 | 61.7992 | -0.07998 | -0.1197 | -0.10648 | 0.01576 | 121.4425 | 121.2512 | 121.1002 | 61.7171 | -121.3603 | 121.1879 | 121.2879 | 121.4101 | 61.7939 | -121.3546
509.8906 | 121.701 | -61.7111 | 59.7794 | -0.005418 | -0.030515 | 0.00050001 | 0.054517 | -0.0050917 | 0.050538 | 0.00351 | -0.0013673 | -0.0014444 | -0.0035187 | 0.014861 | -0.0086037 | -59.083 | -0.016908 | -61.7007 | 59.7085 | 59.531 | 59.3753 | -61.6908 | 0.074307 | 0.059882 | -61.8048 | 59.4584 | 59.563 | 59.6807 | -61.6806 | 0.020318 | -0.070836 | 2.6281 | 0.010381 | -0.009937 | -0.2484 | -0.40401 | 0.030563 | -0.32092 | 61.7854 | -0.093711 | -0.12427 | -0.21635 | -0.098681 | 121.4196 | 121.2421 | 121.0865 | 61.6942 | -121.4702 | 121.1696 | 121.2741 | 121.3918 | 61.771 | -121.4599
511.5781 | 121.756 | -61.7111 | 59.7519 | -0.005418 | -0.030728 | 0.00071361 | 0.054731 | -0.0048779 | 0.050324 | -0.019381 | -0.0011537 | -0.0012306 | -0.0039461 | 0.015075 | -0.0086037 | -59.1288 | -0.007751 | -61.7053 | 59.7085 | 59.5264 | 59.3708 | -61.7 | 0.078886 | 0.064461 | -61.8094 | 59.4584 | 59.563 | 59.6669 | -61.6897 | 0.01116 | -0.04337 | 2.5823 | 0.005803 | -0.005357 | -0.22551 | -0.38112 | 0.021406 | -0.29346 | 61.79 | -0.09829 | -0.1197 | -0.18888 | -0.084951 | 121.4196 | 121.2375 | 121.0819 | 61.7034 | -121.4519 | 121.1696 | 121.2741 | 121.3781 | 61.7756 | -121.4416
513.3281 | 121.6736 | -61.7111 | 59.8251 | 0.002213 | -0.030728 | 0.00071361 | 0.054517 | -0.0053053 | 0.050324 | -0.011751 | -0.0013673 | -0.0014444 | -0.0037325 | 0.014861 | -0.0083901 | -59.138 | -0.012329 | -61.7053 | 59.7039 | 59.5218 | 59.3708 | -61.6908 | 0.074307 | 0.055303 | -61.8094 | 59.4539 | 59.5584 | 59.6761 | -61.6851 | 0.020318 | -0.12119 | 2.5731 | 0.005803 | -0.014515 | -0.30333 | -0.45437 | 0.025984 | -0.37128 | 61.7854 | -0.09829 | -0.12427 | -0.2667 | -0.14903 | 121.4151 | 121.2329 | 121.0819 | 61.6988 | -121.5159 | 121.165 | 121.2696 | 121.3872 | 61.7664 | -121.5103
515.0781 | 121.7834 | -61.734 | 59.6786 | -0.005418 | -0.030515 | 0.00071361 | 0.054731 | -0.0053053 | 0.050111 | -0.0041205 | -0.0011537 | -0.0012306 | -0.0037325 | 0.015075 | -0.0083901 | -59.1059 | -0.007751 | -61.7007 | 59.7039 | 59.5218 | 59.3616 | -61.6954 | 0.074307 | 0.059882 | -61.8048 | 59.4584 | 59.5676 | 59.6853 | -61.6897 | 0.038627 | 0.025293 | 2.6281 | 0.033269 | -0.005358 | -0.15685 | -0.31704 | 0.044294 | -0.22022 | 61.8083 | -0.070823 | -0.11512 | -0.11106 | 0.006606 | 121.438 | 121.2558 | 121.0956 | 61.7263 | -121.374 | 121.1924 | 121.3016 | 121.4193 | 61.7939 | -121.3684
516.7656 | 121.7148 | -61.7065 | 59.7748 | -0.005418 | -0.030728 | 0.00050001 | 0.054517 | -0.0057325 | 0.050538 | -0.0041205 | -0.0013673 | -0.0012306 | -0.0037325 | 0.014861 | -0.0081765 | -59.083 | -0.003172 | -61.6962 | 59.7039 | 59.5264 | 59.3753 | -61.7045 | 0.074307 | 0.050725 | -61.8048 | 59.4676 | 59.563 | 59.6761 | -61.6897 | 0.002004 | -0.070837 | 2.6235 | 0.010382 | 0.008378 | -0.2484 | -0.39943 | 0.016828 | -0.30719 | 61.7809 | -0.098289 | -0.11512 | -0.21177 | -0.098681 | 121.4105 | 121.2329 | 121.0819 | 61.7034 | -121.4793 | 121.1741 | 121.2696 | 121.3826 | 61.7573 | -121.4645
518.5 | 121.669 | -61.7752 | 59.7153 | -0.005418 | -0.031156 | 0.00028641 | 0.054944 | -0.0053053 | 0.050538 | 0.00351 | -0.0015809 | -0.0014444 | -0.0037325 | 0.015075 | -0.0086037 | -59.0876 | -0.012329 | -61.7053 | 59.7039 | 59.5218 | 59.3708 | -61.7 | 0.078886 | 0.055303 | -61.8048 | 59.4584 | 59.5584 | 59.6898 | -61.6851 | 0.075247 | -0.011328 | 2.6876 | 0.06989 | -0.005357 | -0.19347 | -0.3445 | 0.090071 | -0.25684 | 61.8541 | -0.029624 | -0.1197 | -0.15684 | -0.025437 | 121.4792 | 121.297 | 121.146 | 61.7629 | -121.4152 | 121.2336 | 121.3336 | 121.465 | 61.8305 | -121.4004
520.2031 | 121.7926 | -61.6241 | 59.8068 | -0.005418 | -0.030942 | 0.00050001 | 0.054517 | -0.0055189 | 0.050324 | -0.019381 | -0.00072626 | -0.0014444 | -0.0037325 | 0.015075 | -0.0083901 | -59.1838 | -0.012329 | -61.6962 | 59.6994 | 59.531 | 59.3662 | -61.7 | 0.069728 | 0.059882 | -61.814 | 59.463 | 59.5676 | 59.6853 | -61.6851 | -0.075815 | -0.10746 | 2.4404 | -0.072015 | 0.0038 | -0.27587 | -0.44063 | -0.060991 | -0.34381 | 61.6939 | -0.18984 | -0.12885 | -0.23924 | -0.12157 | 121.3235 | 121.1551 | 120.9903 | 61.6118 | -121.5068 | 121.0872 | 121.1917 | 121.3094 | 61.684 | -121.492
521.9375 | 121.8063 | -61.6058 | 59.8251 | -0.005418 | -0.030728 | 0.00050001 | 0.054731 | -0.0055189 | 0.050538 | -0.0041205 | -0.0011537 | -0.001658 | -0.0037325 | 0.015075 | -0.0083901 | -59.1838 | -0.016908 | -61.6962 | 59.7039 | 59.531 | 59.3753 | -61.6954 | 0.074307 | 0.059882 | -61.8048 | 59.4584 | 59.5539 | 59.6807 | -61.6897 | -0.089547 | -0.12119 | 2.4221 | -0.090326 | -0.000779 | -0.29418 | -0.44979 | -0.08388 | -0.3667 | 61.6801 | -0.199 | -0.11512 | -0.27128 | -0.14446 | 121.3098 | 121.1368 | 120.9812 | 61.5889 | -121.5205 | 121.0643 | 121.1597 | 121.2865 | 61.6657 | -121.5148
523.6875 | 121.7056 | -61.7157 | 59.7931 | -0.005418 | -0.031156 | 0.00071361 | 0.054731 | -0.0055189 | 0.050324 | -0.0041205 | -0.0013673 | -0.0012306 | -0.0041597 | 0.015075 | -0.0083901 | -59.0922 | -0.003172 | -61.7007 | 59.7085 | 59.5264 | 59.3662 | -61.7 | 0.074307 | 0.055303 | -61.814 | 59.4584 | 59.563 | 59.6807 | -61.6897 | 0.015737 | -0.084569 | 2.6235 | 0.014958 | -0.000779 | -0.26671 | -0.4269 | 0.025983 | -0.33466 | 61.79 | -0.098292 | -0.12427 | -0.23008 | -0.11241 | 121.4242 | 121.2421 | 121.0819 | 61.7125 | -121.4931 | 121.1741 | 121.2787 | 121.3964 | 61.771 | -121.4828
525.4531 | 121.7834 | -61.734 | 59.6924 | -0.013049 | -0.031156 | 0.00071361 | 0.054731 | -0.0053053 | 0.050965 | -0.0041205 | -0.0011537 | -0.0014444 | -0.0037325 | 0.015075 | -0.0083901 | -59.1151 | -0.012329 | -61.6962 | 59.7085 | 59.531 | 59.3708 | -61.6908 | 0.078886 | 0.055303 | -61.8003 | 59.4493 | 59.5676 | 59.6761 | -61.6806 | 0.043206 | 0.016139 | 2.6189 | 0.037848 | -0.005358 | -0.16143 | -0.32162 | 0.053451 | -0.24311 | 61.8129 | -0.066244 | -0.1197 | -0.12479 | -0.016284 | 121.4425 | 121.265 | 121.1048 | 61.7217 | -121.3832 | 121.1833 | 121.3016 | 121.4101 | 61.7893 | -121.3729
527.1406 | 121.7148 | -61.7523 | 59.7748 | 0.002213 | -0.030728 | 0.00050001 | 0.054944 | -0.0050917 | 0.050538 | -0.0041205 | -0.0013673 | -0.001658 | -0.0037325 | 0.015075 | -0.0083901 | -59.0235 | -0.012329 | -61.7007 | 59.7039 | 59.531 | 59.3753 | -61.6954 | 0.069728 | 0.055303 | -61.8003 | 59.4584 | 59.563 | 59.6807 | -61.6851 | 0.056937 | -0.070837 | 2.7288 | 0.051579 | -0.005358 | -0.24382 | -0.39943 | 0.067182 | -0.31635 | 61.822 | -0.047934 | -0.11512 | -0.21177 | -0.094103 | 121.4563 | 121.2833 | 121.1277 | 61.74 | -121.4702 | 121.2108 | 121.3153 | 121.433 | 61.8076 | -121.4599
528.875 | 121.6782 | -61.6837 | 59.8297 | -0.005418 | -0.030728 | 0.00050001 | 0.054517 | -0.0053053 | 0.050538 | -0.011751 | -0.0011537 | -0.0012306 | -0.0039461 | 0.015502 | -0.0081765 | -59.083 | -0.007751 | -61.7053 | 59.7085 | 59.5264 | 59.3708 | -61.6954 | 0.069728 | 0.059882 | -61.8003 | 59.4539 | 59.5584 | 59.6807 | -61.6851 | -0.011727 | -0.12119 | 2.6006 | -0.021663 | -0.009936 | -0.30333 | -0.45894 | -0.001482 | -0.37586 | 61.7534 | -0.1166 | -0.11512 | -0.27128 | -0.14903 | 121.3922 | 121.21 | 121.0544 | 61.6759 | -121.5251 | 121.1375 | 121.2421 | 121.3643 | 61.7435 | -121.5148
530.625 | 121.6599 | -61.6608 | 59.8343 | 0.002213 | -0.031369 | 0.00050001 | 0.054731 | -0.0053053 | 0.050324 | -0.0041205 | -0.0013673 | -0.001017 | -0.0037325 | 0.014861 | -0.0081765 | -59.0602 | -0.003172 | -61.7007 | 59.7039 | 59.5218 | 59.3708 | -61.7 | 0.069728 | 0.059882 | -61.8094 | 59.4539 | 59.5676 | 59.6715 | -61.6897 | -0.039194 | -0.13035 | 2.6006 | -0.039973 | -0.000779 | -0.31249 | -0.46352 | -0.028948 | -0.38044 | 61.7305 | -0.14864 | -0.1197 | -0.2667 | -0.16277 | 121.3647 | 121.1826 | 121.0315 | 61.6576 | -121.5343 | 121.1146 | 121.2284 | 121.3323 | 61.7206 | -121.524
532.3281 | 121.7056 | -61.7249 | 59.7336 | -0.013049 | -0.031369 | 0.00071361 | 0.054731 | -0.0053053 | 0.050752 | -0.0041205 | -0.0011537 | -0.0012306 | -0.0037325 | 0.015288 | -0.0083901 | -59.0144 | -0.007751 | -61.6962 | 59.7085 | 59.531 | 59.3708 | -61.6954 | 0.078886 | 0.059882 | -61.8094 | 59.463 | 59.563 | 59.6807 | -61.6851 | 0.029472 | -0.02506 | 2.7105 | 0.028693 | -0.000779 | -0.20262 | -0.36281 | 0.039717 | -0.27057 | 61.8037 | -0.084557 | -0.12427 | -0.17057 | -0.052905 | 121.4334 | 121.2558 | 121.0956 | 61.7171 | -121.429 | 121.1879 | 121.2879 | 121.4055 | 61.7847 | -121.4187
534.0625 | 121.6278 | -61.7798 | 59.7244 | -0.013049 | -0.030942 | 0.00050001 | 0.054731 | -0.0057325 | 0.050538 | -0.0041205 | -0.0013673 | -0.0012306 | -0.0035187 | 0.015075 | -0.0083901 | -59.0098 | -0.003172 | -61.7053 | 59.7085 | 59.5355 | 59.3708 | -61.7 | 0.078886 | 0.059882 | -61.8094 | 59.4584 | 59.5676 | 59.6807 | -61.6806 | 0.079824 | -0.015904 | 2.77 | 0.074467 | -0.005357 | -0.18889 | -0.35366 | 0.099227 | -0.26599 | 61.8587 | -0.029626 | -0.12885 | -0.15684 | -0.043749 | 121.4883 | 121.3153 | 121.1506 | 61.7766 | -121.4244 | 121.2382 | 121.3474 | 121.4605 | 61.8397 | -121.405
535.75 | 121.7239 | -61.7294 | 59.7565 | 0.002213 | -0.031156 | 0.00050001 | 0.054944 | -0.0053053 | 0.050752 | -0.0041205 | -0.0013673 | -0.0014444 | -0.0039461 | 0.015288 | -0.0086037 | -59.0785 | -0.012329 | -61.687 | 59.7039 | 59.5355 | 59.3662 | -61.7 | 0.069728 | 0.059882 | -61.8048 | 59.463 | 59.563 | 59.6761 | -61.6897 | 0.02947 | -0.052527 | 2.651 | 0.042426 | 0.012956 | -0.22093 | -0.39028 | 0.039716 | -0.29346 | 61.7992 | -0.075401 | -0.11512 | -0.19346 | -0.080371 | 121.4334 | 121.265 | 121.0956 | 61.7171 | -121.4564 | 121.1924 | 121.2924 | 121.4055 | 61.7893 | -121.4462
537.5 | 121.756 | -61.6974 | 59.729 | -0.005418 | -0.031369 | 0.00050001 | 0.054944 | -0.0055189 | 0.050538 | -0.011751 | -0.0013673 | -0.001658 | -0.0037325 | 0.015075 | -0.0088175 | -59.138 | -0.007751 | -61.7053 | 59.7039 | 59.531 | 59.3662 | -61.7045 | 0.074307 | 0.055303 | -61.8094 | 59.4676 | 59.5722 | 59.6807 | -61.6851 | -0.007151 | -0.025061 | 2.5594 | -0.00793 | -0.000779 | -0.19805 | -0.36281 | 0.012251 | -0.26141 | 61.7717 | -0.11202 | -0.12427 | -0.15684 | -0.048327 | 121.4013 | 121.2283 | 121.0636 | 61.6896 | -121.4335 | 121.165 | 121.2696 | 121.3781 | 61.7527 | -121.4141
539.25 | 121.788 | -61.6379 | 59.8114 | 0.002213 | -0.031369 | 0.00028641 | 0.054517 | -0.0050917 | 0.050324 | -0.011751 | -0.0013673 | -0.001017 | -0.0041597 | 0.015288 | -0.0086037 | -59.1792 | -0.007751 | -61.7053 | 59.7085 | 59.5264 | 59.3799 | -61.6954 | 0.06515 | 0.050725 | -61.8048 | 59.4539 | 59.563 | 59.6807 | -61.6897 | -0.057504 | -0.10288 | 2.4587 | -0.06744 | -0.009936 | -0.28502 | -0.43148 | -0.051837 | -0.35755 | 61.703 | -0.16695 | -0.11512 | -0.24839 | -0.13072 | 121.3464 | 121.1643 | 121.0178 | 61.6301 | -121.5068 | 121.0917 | 121.2009 | 121.3186 | 61.6886 | -121.5011
540.9375 | 121.7743 | -61.615 | 59.7931 | 0.002213 | -0.031156 | 0.00050001 | 0.054731 | -0.0053053 | 0.050324 | -0.019381 | -0.0013673 | -0.0014444 | -0.0037325 | 0.015716 | -0.0086037 | -59.1655 | -0.016908 | -61.7053 | 59.7131 | 59.531 | 59.3616 | -61.7 | 0.069728 | 0.059882 | -61.8094 | 59.4539 | 59.5676 | 59.6807 | -61.6851 | -0.084971 | -0.079991 | 2.4495 | -0.090328 | -0.005357 | -0.26213 | -0.43148 | -0.070147 | -0.33924 | 61.6847 | -0.19442 | -0.12427 | -0.2255 | -0.11241 | 121.3281 | 121.1459 | 120.9766 | 61.5981 | -121.4931 | 121.0688 | 121.1826 | 121.2957 | 61.6749 | -121.4782
542.6875 | 121.788 | -61.7111 | 59.7198 | -0.005418 | -0.031583 | 0.00050001 | 0.054303 | -0.0055189 | 0.050752 | -0.0041205 | -0.0013673 | -0.0012306 | -0.0039461 | 0.015502 | -0.0081765 | -59.1197 | 0.001407 | -61.7007 | 59.7085 | 59.5264 | 59.3799 | -61.6862 | 0.069728 | 0.064461 | -61.8003 | 59.4722 | 59.5722 | 59.6761 | -61.6897 | 0.024897 | -0.011327 | 2.5914 | 0.010381 | -0.014516 | -0.19347 | -0.33992 | 0.021406 | -0.24768 | 61.7808 | -0.089132 | -0.11054 | -0.14768 | -0.04375 | 121.4196 | 121.2375 | 121.091 | 61.7125 | -121.4061 | 121.1833 | 121.2833 | 121.3872 | 61.7756 | -121.4096
544.4531 | 121.7926 | -61.7249 | 59.7244 | -0.005418 | -0.031156 | 0.00050001 | 0.054731 | -0.0053053 | 0.050111 | -0.019381 | -0.0013673 | -0.0014444 | -0.0037325 | 0.015288 | -0.0083901 | -59.1151 | -0.007751 | -61.6962 | 59.7085 | 59.5355 | 59.3753 | -61.6862 | 0.069728 | 0.064461 | -61.8003 | 59.463 | 59.5767 | 59.6807 | -61.6806 | 0.03863 | -0.015904 | 2.6098 | 0.028693 | -0.009937 | -0.18889 | -0.34908 | 0.044296 | -0.26141 | 61.7946 | -0.075399 | -0.1197 | -0.14768 | -0.043749 | 121.4334 | 121.2604 | 121.1002 | 61.7171 | -121.4107 | 121.1879 | 121.3016 | 121.4055 | 61.7893 | -121.405
546.1406 | 121.7468 | -61.6791 | 59.761 | -0.005418 | -0.031369 | 0.00050001 | 0.054731 | -0.0050917 | 0.050324 | -0.019381 | -0.0015809 | -0.001017 | -0.0037325 | 0.015288 | -0.0083901 | -59.138 | -0.003172 | -61.6962 | 59.7131 | 59.531 | 59.3845 | -61.6908 | 0.074307 | 0.055303 | -61.7957 | 59.4676 | 59.5767 | 59.6898 | -61.6851 | -0.011726 | -0.047947 | 2.5411 | -0.017084 | -0.005358 | -0.23009 | -0.37654 | -0.00606 | -0.29346 | 61.7534 | -0.1166 | -0.11054 | -0.1843 | -0.071213 | 121.3922 | 121.21 | 121.0636 | 61.6759 | -121.4519 | 121.1467 | 121.2558 | 121.3689 | 61.7344 | -121.4462
547.875 | 121.701 | -61.7065 | 59.7382 | 0.002213 | -0.031369 | 0.00071361 | 0.054731 | -0.0053053 | 0.050538 | 0.00351 | -0.0013673 | -0.001017 | -0.0035187 | 0.015288 | -0.0081765 | -59.0602 | -0.003172 | -61.6962 | 59.7131 | 59.5401 | 59.3799 | -61.6908 | 0.060571 | 0.064461 | -61.7957 | 59.4676 | 59.5813 | 59.6898 | -61.6714 | 0.01574 | -0.025059 | 2.6464 | 0.010382 | -0.005358 | -0.19804 | -0.35823 | 0.035143 | -0.27057 | 61.7671 | -0.089132 | -0.12428 | -0.15683 | -0.048325 | 121.4196 | 121.2467 | 121.0865 | 61.7034 | -121.429 | 121.1741 | 121.2879 | 121.3964 | 61.771 | -121.4096
549.625 | 121.7697 | -61.7203 | 59.7015 | -0.005418 | -0.031156 | 0.00050001 | 0.054731 | -0.0055189 | 0.050324 | -0.011751 | -0.0011537 | -0.0014444 | -0.0037325 | 0.015075 | -0.0083901 | -59.1105 | -0.007751 | -61.6824 | 59.7177 | 59.5355 | 59.3937 | -61.6816 | 0.074307 | 0.059882 | -61.7911 | 59.4676 | 59.5767 | 59.6944 | -61.6806 | 0.038631 | 0.01614 | 2.6098 | 0.037849 | -0.000782 | -0.166 | -0.30788 | 0.039718 | -0.23395 | 61.7946 | -0.07082 | -0.11054 | -0.12479 | -0.007125 | 121.438 | 121.2558 | 121.1139 | 61.7125 | -121.3832 | 121.1879 | 121.297 | 121.4147 | 61.7802 | -121.3821
551.3594 | 121.756 | -61.6745 | 59.7748 | -0.005418 | -0.031156 | 0.00050001 | 0.054517 | -0.0053053 | 0.050324 | -0.011751 | -0.0011537 | -0.0012306 | -0.0039461 | 0.015288 | -0.0083901 | -59.138 | -0.003172 | -61.6824 | 59.7223 | 59.5401 | 59.3845 | -61.6816 | 0.083464 | 0.055303 | -61.7911 | 59.4722 | 59.5813 | 59.6944 | -61.6806 | -0.007145 | -0.052523 | 2.5365 | -0.007927 | -0.000782 | -0.23466 | -0.39028 | -0.006058 | -0.30261 | 61.758 | -0.1166 | -0.11054 | -0.19346 | -0.080367 | 121.3968 | 121.2146 | 121.059 | 61.6713 | -121.4564 | 121.1467 | 121.2558 | 121.3689 | 61.7298 | -121.4553
553.0938 | 121.756 | -61.6745 | 59.7931 | -0.005418 | -0.031156 | 0.00050001 | 0.054731 | -0.0055189 | 0.050538 | -0.0041205 | -0.0013673 | -0.001658 | -0.0035187 | 0.015288 | -0.0083901 | -59.1563 | -0.007751 | -61.6916 | 59.7223 | 59.5447 | 59.3937 | -61.6816 | 0.069728 | 0.064461 | -61.7911 | 59.4813 | 59.5722 | 59.6944 | -61.6714 | -0.007145 | -0.070834 | 2.5182 | -0.017083 | -0.009938 | -0.2484 | -0.39943 | 0.0031 | -0.31176 | 61.7442 | -0.1166 | -0.1197 | -0.22092 | -0.098678 | 121.3968 | 121.2192 | 121.0682 | 61.6667 | -121.4747 | 121.1558 | 121.2467 | 121.3689 | 61.739 | -121.4645
554.8438 | 121.7422 | -61.6699 | 59.7977 | -0.005418 | -0.031369 | 0.00028641 | 0.054731 | -0.0053053 | 0.050538 | -0.019381 | -0.0013673 | -0.001017 | -0.0035187 | 0.015075 | -0.0083901 | -59.1471 | 0.001407 | -61.687 | 59.7268 | 59.5401 | 59.3937 | -61.6771 | 0.069728 | 0.059882 | -61.7911 | 59.4722 | 59.5767 | 59.699 | -61.6806 | -0.007144 | -0.070833 | 2.5228 | -0.017083 | -0.009939 | -0.25755 | -0.40401 | -0.010636 | -0.3255 | 61.7396 | -0.12117 | -0.11054 | -0.22092 | -0.098676 | 121.3968 | 121.21 | 121.0636 | 61.6713 | -121.4747 | 121.1421 | 121.2467 | 121.3689 | 61.7298 | -121.4782
556.5312 | 121.701 | -61.7661 | 59.7061 | -0.005418 | -0.030942 | 0.00050001 | 0.054731 | -0.0053053 | 0.050538 | -0.011751 | -0.0011537 | -0.0012306 | -0.0033051 | 0.015288 | -0.0083901 | -59.0647 | -0.007751 | -61.6824 | 59.7314 | 59.5493 | 59.3891 | -61.6862 | 0.088043 | 0.06904 | -61.7819 | 59.4767 | 59.5813 | 59.6944 | -61.676 | 0.079828 | 0.025297 | 2.7013 | 0.083625 | 0.003797 | -0.15684 | -0.31703 | 0.090073 | -0.22937 | 61.8541 | -0.015887 | -0.10596 | -0.12479 | -0.011703 | 121.4975 | 121.3153 | 121.1551 | 61.7583 | -121.3923 | 121.2428 | 121.3474 | 121.4605 | 61.8351 | -121.3821
558.2812 | 121.7972 | -61.7249 | 59.7015 | 0.002213 | -0.031369 | 0.00028641 | 0.054731 | -0.0053053 | 0.050538 | -0.0041205 | -0.0013673 | -0.0012306 | -0.0037325 | 0.015502 | -0.0086037 | -59.1014 | -0.007751 | -61.6916 | 59.7268 | 59.5493 | 59.3891 | -61.6771 | 0.074307 | 0.064461 | -61.7865 | 59.4767 | 59.5722 | 59.699 | -61.6714 | 0.047788 | 0.025297 | 2.6235 | 0.033271 | -0.014517 | -0.15226 | -0.31245 | 0.053454 | -0.22479 | 61.7992 | -0.061663 | -0.11512 | -0.12937 | -0.002546 | 121.4517 | 121.2741 | 121.1139 | 61.7171 | -121.3786 | 121.2016 | 121.297 | 121.4238 | 61.7893 | -121.3729
560.0312 | 121.701 | -61.7065 | 59.7839 | -0.005418 | -0.031369 | 0.00071361 | 0.054517 | -0.0053053 | 0.050538 | -0.0041205 | -0.0013673 | -0.0012306 | -0.0037325 | 0.015075 | -0.0083901 | -59.0693 | 0.001407 | -61.687 | 59.7223 | 59.5493 | 59.3937 | -61.6725 | 0.083464 | 0.06904 | -61.7865 | 59.4767 | 59.5859 | 59.7036 | -61.676 | 0.034056 | -0.061679 | 2.6372 | 0.019538 | -0.014518 | -0.23466 | -0.39027 | 0.030564 | -0.30719 | 61.79 | -0.079974 | -0.11054 | -0.19803 | -0.080366 | 121.4288 | 121.2558 | 121.1002 | 61.708 | -121.4564 | 121.1833 | 121.2924 | 121.4101 | 61.7756 | -121.4599
561.7812 | 121.6736 | -61.7798 | 59.7473 | -0.005418 | -0.030942 | 0.00028641 | 0.054731 | -0.0055189 | 0.050752 | -0.011751 | -0.0011537 | -0.0012306 | -0.0041597 | 0.015288 | -0.0083901 | -59.0602 | -0.007751 | -61.6916 | 59.7314 | 59.5493 | 59.3891 | -61.6679 | 0.078886 | 0.064461 | -61.7865 | 59.4813 | 59.5859 | 59.7081 | -61.6668 | 0.11188 | -0.015901 | 2.7196 | 0.088202 | -0.023675 | -0.19804 | -0.35823 | 0.11296 | -0.26599 | 61.8587 | -0.006732 | -0.1197 | -0.16141 | -0.039165 | 121.5112 | 121.3291 | 121.1689 | 61.772 | -121.4152 | 121.2611 | 121.3657 | 121.4879 | 61.8442 | -121.4141
563.4688 | 121.756 | -61.6562 | 59.7931 | 0.002213 | -0.031369 | 0.00050001 | 0.054517 | -0.0055189 | 0.050324 | -0.011751 | -0.0011537 | -0.0012306 | -0.0037325 | 0.015288 | -0.0083901 | -59.0922 | -0.003172 | -61.6824 | 59.736 | 59.5539 | 59.3937 | -61.6725 | 0.078886 | 0.059882 | -61.7819 | 59.4813 | 59.5905 | 59.7036 | -61.6577 | -0.016298 | -0.057099 | 2.564 | -0.026238 | -0.00994 | -0.23924 | -0.39943 | -0.001475 | -0.31176 | 61.7351 | -0.12575 | -0.12428 | -0.20261 | -0.089521 | 121.3922 | 121.21 | 121.0498 | 61.653 | -121.4656 | 121.1375 | 121.2467 | 121.3598 | 61.7161 | -121.4508
565.2344 | 121.7926 | -61.5967 | 59.8206 | -0.005418 | -0.031369 | 0.00050001 | 0.054517 | -0.0053053 | 0.050324 | -0.0041205 | -0.0013673 | -0.0014444 | -0.0039461 | 0.015288 | -0.0083901 | -59.0968 | -0.003172 | -61.6824 | 59.7314 | 59.5584 | 59.4028 | -61.6679 | 0.06515 | 0.059882 | -61.7728 | 59.4859 | 59.5859 | 59.7127 | -61.6577 | -0.071228 | -0.089144 | 2.4999 | -0.085747 | -0.014519 | -0.26213 | -0.41774 | -0.060984 | -0.33465 | 61.6618 | -0.1761 | -0.11512 | -0.23465 | -0.10783 | 121.3281 | 121.1551 | 120.9995 | 61.5935 | -121.4885 | 121.0826 | 121.1826 | 121.3094 | 61.6566 | -121.4782
566.9219 | 121.7194 | -61.6974 | 59.7656 | 0.002213 | -0.031583 | 0.00050001 | 0.054517 | -0.0055189 | 0.050538 | -0.011751 | -0.0013673 | -0.0014444 | -0.0037325 | 0.015288 | -0.0079629 | -59.0006 | -0.007751 | -61.6733 | 59.736 | 59.5539 | 59.4028 | -61.6633 | 0.074307 | 0.055303 | -61.7728 | 59.4905 | 59.5859 | 59.7127 | -61.6622 | 0.034059 | -0.029633 | 2.6968 | 0.024118 | -0.009941 | -0.21177 | -0.36281 | 0.035145 | -0.27514 | 61.7717 | -0.075393 | -0.11054 | -0.17972 | -0.052898 | 121.4334 | 121.2512 | 121.1002 | 61.6896 | -121.429 | 121.1879 | 121.2833 | 121.4101 | 61.7527 | -121.4279
568.6719 | 121.7743 | -61.6928 | 59.7244 | 0.002213 | -0.031156 | 0.00050001 | 0.054731 | -0.0055189 | 0.050752 | -0.0041205 | -0.0013673 | -0.001017 | -0.0037325 | 0.015075 | -0.0083901 | -59.0327 | -0.007751 | -61.6733 | 59.736 | 59.5584 | 59.4028 | -61.6679 | 0.078886 | 0.06904 | -61.7728 | 59.4905 | 59.5996 | 59.699 | -61.6577 | 0.024902 | 0.011566 | 2.6601 | 0.01954 | -0.005362 | -0.166 | -0.32161 | 0.035146 | -0.23394 | 61.7717 | -0.079971 | -0.11512 | -0.12479 | -0.025434 | 121.4288 | 121.2512 | 121.0956 | 61.6851 | -121.3923 | 121.1833 | 121.2925 | 121.3918 | 61.7619 | -121.3821
570.4375 | 121.6919 | -61.6745 | 59.8251 | 0.002213 | -0.031156 | 0.00028641 | 0.054517 | -0.0055189 | 0.050111 | -0.0041205 | -0.0015809 | -0.0012306 | -0.0039461 | 0.015288 | -0.0086037 | -59.0144 | -0.003172 | -61.6824 | 59.7406 | 59.563 | 59.4028 | -61.6633 | 0.06515 | 0.059882 | -61.7774 | 59.4905 | 59.5951 | 59.7173 | -61.6622 | 0.011171 | -0.084564 | 2.6601 | -0.007927 | -0.019098 | -0.26212 | -0.42232 | 0.012257 | -0.33465 | 61.7397 | -0.10286 | -0.11512 | -0.23007 | -0.10783 | 121.4151 | 121.2375 | 121.0773 | 61.6713 | -121.4885 | 121.165 | 121.2696 | 121.3918 | 61.7344 | -121.4874
572.125 | 121.756 | -61.6653 | 59.7382 | -0.013049 | -0.031156 | 0.00071361 | 0.054731 | -0.0053053 | 0.050324 | -0.019381 | -0.0011537 | -0.0014444 | -0.0037325 | 0.015288 | -0.0081765 | -59.0418 | -0.007751 | -61.6733 | 59.7406 | 59.5676 | 59.412 | -61.6587 | 0.078886 | 0.059882 | -61.7728 | 59.5042 | 59.5996 | 59.7173 | -61.6577 | 0.006594 | 0.002411 | 2.6235 | -0.007926 | -0.01452 | -0.17057 | -0.32618 | 0.00768 | -0.23394 | 61.7442 | -0.10744 | -0.11512 | -0.13852 | -0.020853 | 121.4059 | 121.2329 | 121.0773 | 61.6576 | -121.3969 | 121.1696 | 121.265 | 121.3826 | 61.7252 | -121.3958
573.8594 | 121.7789 | -61.6104 | 59.8297 | 0.002213 | -0.031583 | 7.2612e-05 | 0.054517 | -0.0055189 | 0.050324 | 0.00351 | -0.0011537 | -0.0014444 | -0.0035187 | 0.015288 | -0.0083901 | -59.0876 | 0.001407 | -61.6733 | 59.7406 | 59.563 | 59.412 | -61.6633 | 0.06515 | 0.064461 | -61.7636 | 59.4996 | 59.5951 | 59.7173 | -61.6622 | -0.052916 | -0.089142 | 2.5228 | -0.062857 | -0.009941 | -0.2667 | -0.41774 | -0.05183 | -0.33007 | 61.6756 | -0.15321 | -0.10138 | -0.23465 | -0.11241 | 121.351 | 121.1734 | 121.0224 | 61.6118 | -121.493 | 121.1101 | 121.2055 | 121.3277 | 61.6749 | -121.492
575.5938 | 121.701 | -61.734 | 59.761 | 0.002213 | -0.031583 | 0.00071361 | 0.054303 | -0.0055189 | 0.050111 | -0.0041205 | -0.0011537 | -0.0014444 | -0.0039461 | 0.015502 | -0.0086037 | -58.9823 | -0.003172 | -61.6733 | 59.7406 | 59.5676 | 59.412 | -61.6633 | 0.074307 | 0.064461 | -61.7636 | 59.4996 | 59.6042 | 59.7173 | -61.6531 | 0.07068 | -0.020477 | 2.7517 | 0.060739 | -0.009941 | -0.19346 | -0.34907 | 0.080924 | -0.26141 | 61.8083 | -0.029615 | -0.11054 | -0.15683 | -0.043741 | 121.4746 | 121.3016 | 121.146 | 61.7308 | -121.4244 | 121.2336 | 121.3382 | 121.4513 | 61.7985 | -121.4141
577.3281 | 121.6736 | -61.7386 | 59.7519 | -0.005418 | -0.031583 | 0.00028641 | 0.054731 | -0.0055189 | 0.050538 | 0.00351 | -0.0011537 | -0.0014444 | -0.0039461 | 0.015502 | -0.0081765 | -58.9869 | -0.007751 | -61.6641 | 59.7451 | 59.5722 | 59.4166 | -61.6542 | 0.078886 | 0.059882 | -61.759 | 59.4996 | 59.6088 | 59.7173 | -61.6531 | 0.084415 | -0.006743 | 2.7517 | 0.074473 | -0.009942 | -0.17972 | -0.33534 | 0.085501 | -0.25225 | 61.8175 | -0.020459 | -0.10596 | -0.14309 | -0.034586 | 121.4837 | 121.3108 | 121.1551 | 61.7308 | -121.4061 | 121.2382 | 121.3474 | 121.4559 | 61.7985 | -121.405
579.0781 | 121.6644 | -61.7432 | 59.7519 | -0.005418 | -0.031583 | 0.00050001 | 0.054303 | -0.0055189 | 0.050324 | -0.0041205 | -0.0011537 | -0.001017 | -0.0039461 | 0.015502 | -0.0086037 | -58.9869 | 0.001407 | -61.6687 | 59.7497 | 59.5767 | 59.4211 | -61.6587 | 0.078886 | 0.064461 | -61.759 | 59.5042 | 59.6088 | 59.7265 | -61.6485 | 0.084414 | -0.002165 | 2.7563 | 0.074472 | -0.009942 | -0.17515 | -0.33076 | 0.094658 | -0.24767 | 61.822 | -0.015881 | -0.11054 | -0.14309 | -0.025429 | 121.4929 | 121.3199 | 121.1643 | 61.7446 | -121.4106 | 121.2474 | 121.352 | 121.4696 | 61.8076 | -121.4004
580.7656 | 121.7468 | -61.6608 | 59.7702 | -0.005418 | -0.031583 | 0.00050001 | 0.054731 | -0.0057325 | 0.050538 | -0.011751 | -0.0013673 | -0.0014444 | -0.0041597 | 0.015502 | -0.0086037 | -59.0327 | -0.003172 | -61.6687 | 59.7589 | 59.5767 | 59.4211 | -61.6496 | 0.074307 | 0.059882 | -61.7636 | 59.4951 | 59.6088 | 59.731 | -61.6439 | 0.011175 | -0.011319 | 2.6281 | -0.007925 | -0.0191 | -0.19346 | -0.34907 | 0.01684 | -0.27514 | 61.7351 | -0.10286 | -0.1197 | -0.16141 | -0.039161 | 121.4197 | 121.2375 | 121.0819 | 61.6576 | -121.4198 | 121.1558 | 121.2696 | 121.3918 | 61.7206 | -121.4141
582.5156 | 121.8018 | -61.5875 | 59.8343 | -0.005418 | -0.03201 | 0.00050001 | 0.054517 | -0.0055189 | 0.049683 | -0.011751 | -0.0011537 | -0.0014444 | -0.0035187 | 0.015502 | -0.0083901 | -59.0876 | -0.003172 | -61.655 | 59.7543 | 59.5722 | 59.4166 | -61.6496 | 0.074307 | 0.055303 | -61.7636 | 59.4996 | 59.6134 | 59.7265 | -61.6439 | -0.062068 | -0.079985 | 2.4999 | -0.067433 | -0.005365 | -0.26212 | -0.41774 | -0.056403 | -0.33465 | 61.6618 | -0.1761 | -0.1197 | -0.22092 | -0.10783 | 121.3418 | 121.1597 | 121.0041 | 61.5844 | -121.4839 | 121.0872 | 121.2009 | 121.314 | 61.6428 | -121.4782
584.2656 | 121.6782 | -61.7386 | 59.7656 | 0.002213 | -0.032224 | 0.00050001 | 0.054944 | -0.0057325 | 0.050324 | -0.019381 | -0.0013673 | -0.0014444 | -0.0033051 | 0.015502 | -0.0083901 | -58.9732 | -0.003172 | -61.6641 | 59.7589 | 59.5859 | 59.4166 | -61.6496 | 0.083464 | 0.064461 | -61.7499 | 59.5088 | 59.6088 | 59.7265 | -61.6485 | 0.088994 | -0.006741 | 2.7654 | 0.074473 | -0.014521 | -0.17972 | -0.34907 | 0.09008 | -0.25683 | 61.822 | -0.011302 | -0.10138 | -0.15683 | -0.039162 | 121.4975 | 121.3245 | 121.1551 | 61.7354 | -121.4152 | 121.2474 | 121.3474 | 121.465 | 61.803 | -121.4141
585.9531 | 121.7102 | -61.6653 | 59.8114 | -0.005418 | -0.031797 | 0.00050001 | 0.054517 | -0.0055189 | 0.050111 | 0.00351 | -0.0011537 | -0.0014444 | -0.0039461 | 0.015502 | -0.0086037 | -58.9823 | -0.012329 | -61.6687 | 59.7589 | 59.5813 | 59.4257 | -61.645 | 0.074307 | 0.059882 | -61.7453 | 59.5134 | 59.618 | 59.731 | -61.6302 | 0.020331 | -0.052517 | 2.683 | -0.003348 | -0.023679 | -0.23008 | -0.38569 | 0.035153 | -0.29802 | 61.7397 | -0.079965 | -0.11512 | -0.19345 | -0.080359 | 121.4242 | 121.2467 | 121.0911 | 61.653 | -121.4564 | 121.1787 | 121.2833 | 121.3964 | 61.7252 | -121.4416
587.7031 | 121.6461 | -61.7111 | 59.7519 | -0.005418 | -0.031583 | 0.00028641 | 0.054944 | -0.0053053 | 0.050538 | -0.0041205 | -0.0011537 | -0.0014444 | -0.0041597 | 0.015716 | -0.0083901 | -58.964 | 0.001407 | -61.6595 | 59.768 | 59.5859 | 59.4303 | -61.645 | 0.074307 | 0.064461 | -61.7453 | 59.518 | 59.618 | 59.731 | -61.6393 | 0.066108 | 0.016149 | 2.7471 | 0.051586 | -0.014522 | -0.16599 | -0.3216 | 0.071773 | -0.23394 | 61.7854 | -0.034188 | -0.10596 | -0.13394 | -0.02085 | 121.4792 | 121.297 | 121.1414 | 61.7125 | -121.3969 | 121.2291 | 121.3291 | 121.4422 | 61.7756 | -121.3912
589.4688 | 121.6965 | -61.6928 | 59.7656 | 0.002213 | -0.031583 | 0.00028641 | 0.054517 | -0.0055189 | 0.050324 | -0.0041205 | -0.0013673 | -0.0014444 | -0.0041597 | 0.015502 | -0.0083901 | -58.964 | 0.001407 | -61.6504 | 59.7589 | 59.5905 | 59.4349 | -61.6359 | 0.078886 | 0.064461 | -61.7407 | 59.5134 | 59.618 | 59.7448 | -61.6348 | 0.056954 | -0.006741 | 2.7288 | 0.042431 | -0.014523 | -0.17514 | -0.33076 | 0.05804 | -0.25225 | 61.7717 | -0.04792 | -0.10596 | -0.14767 | -0.020847 | 121.4517 | 121.2833 | 121.1277 | 61.6942 | -121.4015 | 121.2062 | 121.3108 | 121.4376 | 61.7573 | -121.4004
591.1562 | 121.7056 | -61.6516 | 59.8434 | 0.009844 | -0.031797 | 0.00071361 | 0.054944 | -0.0055189 | 0.049897 | -0.0041205 | -0.0013673 | -0.001017 | -0.0037325 | 0.015502 | -0.0083901 | -58.9732 | -0.007751 | -61.6458 | 59.7726 | 59.5905 | 59.4303 | -61.6359 | 0.083464 | 0.064461 | -61.7362 | 59.518 | 59.6271 | 59.7448 | -61.6302 | 0.015755 | -0.070826 | 2.6784 | 0.005811 | -0.009944 | -0.25296 | -0.41316 | 0.02142 | -0.32549 | 61.7351 | -0.084541 | -0.10596 | -0.21633 | -0.098667 | 121.4242 | 121.2421 | 121.0819 | 61.6439 | -121.4793 | 121.1696 | 121.2787 | 121.3964 | 61.7161 | -121.4736
592.9219 | 121.7148 | -61.6791 | 59.8068 | -0.005418 | -0.03201 | 0.00071361 | 0.054731 | -0.0053053 | 0.050538 | -0.019381 | -0.0015809 | -0.0014444 | -0.0037325 | 0.015502 | -0.0083901 | -58.9594 | -0.007751 | -61.6458 | 59.7726 | 59.5951 | 59.444 | -61.6359 | 0.083464 | 0.064461 | -61.7316 | 59.5225 | 59.6271 | 59.7448 | -61.6302 | 0.043221 | -0.034205 | 2.7196 | 0.033277 | -0.009944 | -0.21176 | -0.3628 | 0.048886 | -0.28429 | 61.7625 | -0.052496 | -0.10138 | -0.17971 | -0.062046 | 121.4517 | 121.2741 | 121.1231 | 61.6713 | -121.4427 | 121.2016 | 121.3062 | 121.4239 | 61.7435 | -121.437
594.6719 | 121.6736 | -61.7294 | 59.7839 | -0.005418 | -0.03201 | 0.00071361 | 0.054517 | -0.0055189 | 0.050538 | -0.011751 | -0.0011537 | -0.0012306 | -0.0035187 | 0.015502 | -0.0088175 | -58.964 | 0.001407 | -61.6458 | 59.7772 | 59.5996 | 59.444 | -61.6221 | 0.074307 | 0.064461 | -61.7362 | 59.5363 | 59.6317 | 59.7448 | -61.6165 | 0.10731 | -0.006739 | 2.7654 | 0.083631 | -0.023681 | -0.18429 | -0.33991 | 0.11298 | -0.24767 | 61.8037 | -0.006721 | -0.1197 | -0.15225 | -0.039158 | 121.5066 | 121.3291 | 121.1735 | 61.7308 | -121.4061 | 121.2657 | 121.3611 | 121.4742 | 61.7939 | -121.4004
596.3594 | 121.7194 | -61.7111 | 59.7702 | -0.005418 | -0.031797 | 0.00050001 | 0.054517 | -0.0057325 | 0.050538 | -0.011751 | -0.0013673 | -0.0014444 | -0.0039461 | 0.015288 | -0.0086037 | -58.964 | 0.005985 | -61.6366 | 59.7864 | 59.6134 | 59.4532 | -61.6175 | 0.069728 | 0.064461 | -61.727 | 59.5317 | 59.6408 | 59.7585 | -61.6119 | 0.093581 | 0.016151 | 2.7471 | 0.074477 | -0.019104 | -0.15683 | -0.31702 | 0.099245 | -0.23851 | 61.7808 | -0.015873 | -0.11512 | -0.12936 | -0.011689 | 121.4975 | 121.3245 | 121.1643 | 61.7171 | -121.3877 | 121.2428 | 121.352 | 121.4696 | 61.7756 | -121.3821
598.1094 | 121.7697 | -61.647 | 59.7839 | -0.005418 | -0.031797 | 0.00050001 | 0.054517 | -0.0053053 | 0.050324 | -0.0041205 | -0.0013673 | -0.001017 | -0.0039461 | 0.015716 | -0.0086037 | -58.9869 | -0.007751 | -61.6321 | 59.7864 | 59.618 | 59.4578 | -61.613 | 0.069728 | 0.064461 | -61.7178 | 59.5408 | 59.65 | 59.7677 | -61.6073 | 0.034073 | 0.002418 | 2.6601 | 0.014969 | -0.019104 | -0.16598 | -0.32617 | 0.039737 | -0.24309 | 61.7168 | -0.070803 | -0.11054 | -0.13393 | -0.016265 | 121.4334 | 121.265 | 121.1048 | 61.6393 | -121.3969 | 121.1879 | 121.297 | 121.4147 | 61.7115 | -121.3912
599.8594 | 121.7514 | -61.6379 | 59.848 | -0.005418 | -0.03201 | 7.2612e-05 | 0.054731 | -0.0053053 | 0.050324 | -0.011751 | -0.0011537 | -0.0012306 | -0.0039461 | 0.015716 | -0.0086037 | -58.9961 | -0.003172 | -61.6229 | 59.8001 | 59.6225 | 59.4623 | -61.6175 | 0.078886 | 0.064461 | -61.7178 | 59.5454 | 59.6546 | 59.7631 | -61.6073 | 0.020338 | -0.047933 | 2.6418 | 0.014969 | -0.005369 | -0.22549 | -0.38568 | 0.030581 | -0.3026 | 61.7168 | -0.079959 | -0.11054 | -0.19344 | -0.08493 | 121.438 | 121.2604 | 121.1002 | 61.6347 | -121.4656 | 121.1833 | 121.2925 | 121.401 | 61.7023 | -121.4553
601.5625 | 121.8018 | -61.5372 | 59.8801 | -0.005418 | -0.032224 | 0.00028641 | 0.054731 | -0.0053053 | 0.050538 | 0.00351 | -0.0015809 | -0.0014444 | -0.0035187 | 0.015288 | -0.0086037 | -59.0418 | 0.001407 | -61.6229 | 59.8001 | 59.6317 | 59.4715 | -61.6084 | 0.069728 | 0.059882 | -61.7041 | 59.5592 | 59.6637 | 59.7768 | -61.5981 | -0.071212 | -0.079977 | 2.4953 | -0.085739 | -0.014527 | -0.24837 | -0.40857 | -0.060969 | -0.3209 | 61.6069 | -0.16693 | -0.10596 | -0.21633 | -0.10324 | 121.3373 | 121.1689 | 121.0087 | 61.5386 | -121.4884 | 121.0963 | 121.2009 | 121.314 | 61.5971 | -121.4782
603.3281 | 121.7148 | -61.6196 | 59.8709 | 0.009844 | -0.032224 | 7.2612e-05 | 0.054517 | -0.0055189 | 0.049897 | -0.0041205 | -0.0013673 | -0.0014444 | -0.0037325 | 0.015502 | -0.0081765 | -58.9228 | -0.003172 | -61.6046 | 59.8092 | 59.6317 | 59.4852 | -61.5901 | 0.069728 | 0.064461 | -61.6995 | 59.5683 | 59.6729 | 59.7814 | -61.5936 | 0.029502 | -0.061665 | 2.6968 | 0.014972 | -0.01453 | -0.23922 | -0.38568 | 0.026008 | -0.30259 | 61.6893 | -0.079954 | -0.10596 | -0.19801 | -0.089504 | 121.4288 | 121.2513 | 121.1048 | 61.6164 | -121.461 | 121.1879 | 121.2925 | 121.401 | 61.684 | -121.4645
605 | 121.756 | -61.6013 | 59.7794 | -0.005418 | -0.03201 | 0.00050001 | 0.055158 | -0.0055189 | 0.050111 | -0.0041205 | -0.0011537 | -0.0012306 | -0.0041597 | 0.015716 | -0.0083901 | -58.9594 | -0.007751 | -61.6046 | 59.8184 | 59.6409 | 59.4898 | -61.5809 | 0.078886 | 0.06904 | -61.6904 | 59.5729 | 59.6775 | 59.7951 | -61.589 | 0.020349 | 0.039045 | 2.6418 | -0.003339 | -0.023688 | -0.13851 | -0.28955 | 0.012276 | -0.20646 | 61.6801 | -0.089107 | -0.10138 | -0.10188 | 0.015784 | 121.4197 | 121.2421 | 121.0911 | 61.5935 | -121.3603 | 121.1742 | 121.2787 | 121.3964 | 61.6703 | -121.3683
606.75 | 121.6782 | -61.5692 | 59.9533 | -0.005418 | -0.03201 | 0.00071361 | 0.054517 | -0.0055189 | 0.049897 | -0.011751 | -0.0011537 | -0.001658 | -0.0037325 | 0.015929 | -0.0086037 | -58.964 | -0.003172 | -61.5954 | 59.8321 | 59.6592 | 59.499 | -61.5763 | 0.078886 | 0.059882 | -61.6904 | 59.5775 | 59.6775 | 59.7951 | -61.5798 | -0.007116 | -0.12117 | 2.6052 | -0.026225 | -0.019109 | -0.29414 | -0.45434 | -0.01061 | -0.37583 | 61.6481 | -0.12115 | -0.11054 | -0.27583 | -0.15817 | 121.4014 | 121.2284 | 121.0682 | 61.566 | -121.5296 | 121.1467 | 121.2467 | 121.3644 | 61.6291 | -121.5331
608.5 | 121.7697 | -61.6104 | 59.7977 | 0.002213 | -0.032224 | 0.00028641 | 0.054517 | -0.0055189 | 0.050111 | -0.0041205 | -0.0015809 | -0.0012306 | -0.0039461 | 0.015502 | -0.0088175 | -58.9228 | 0.005985 | -61.5817 | 59.8321 | 59.65 | 59.5127 | -61.5672 | 0.083464 | 0.059882 | -61.6812 | 59.5912 | 59.6958 | 59.8089 | -61.5661 | 0.043241 | 0.03447 | 2.6876 | 0.028709 | -0.014532 | -0.14766 | -0.28496 | 0.044326 | -0.20646 | 61.6939 | -0.070794 | -0.11512 | -0.10188 | 0.01121 | 121.4426 | 121.2604 | 121.1231 | 61.6164 | -121.3648 | 121.2016 | 121.3062 | 121.4193 | 61.6703 | -121.3638
610.2344 | 121.6919 | -61.5326 | 59.9854 | -0.013049 | -0.03201 | -0.00014099 | 0.054517 | -0.0055189 | 0.050752 | -0.011751 | -0.0013673 | -0.0012306 | -0.0035187 | 0.015929 | -0.0083901 | -58.9732 | 0.001407 | -61.5725 | 59.8367 | 59.6592 | 59.5035 | -61.5672 | 0.078886 | 0.064461 | -61.672 | 59.5958 | 59.7049 | 59.8135 | -61.5707 | -0.034579 | -0.14864 | 2.5594 | -0.039955 | -0.005376 | -0.32619 | -0.4818 | -0.038073 | -0.38956 | 61.6115 | -0.13946 | -0.10138 | -0.2804 | -0.17189 | 121.3693 | 121.1918 | 121.0361 | 61.534 | -121.5525 | 121.1284 | 121.2375 | 121.346 | 61.5971 | -121.556
611.9219 | 121.7331 | -61.5005 | 59.9716 | -0.005418 | -0.031797 | 0.00028641 | 0.054731 | -0.0055189 | 0.050324 | -0.011751 | -0.0015809 | -0.0014444 | -0.0041597 | 0.015929 | -0.0086037 | -58.9686 | -0.003172 | -61.5725 | 59.8367 | 59.6683 | 59.5173 | -61.5672 | 0.060571 | 0.064461 | -61.6629 | 59.5958 | 59.6958 | 59.818 | -61.5615 | -0.066623 | -0.1349 | 2.532 | -0.071999 | -0.005376 | -0.30329 | -0.45434 | -0.06096 | -0.37583 | 61.5611 | -0.16234 | -0.10138 | -0.27583 | -0.15358 | 121.3373 | 121.1689 | 121.0178 | 61.4974 | -121.5388 | 121.0963 | 121.1963 | 121.3186 | 61.565 | -121.5331
613.6562 | 121.6873 | -61.5143 | 59.9579 | -0.005418 | -0.032438 | 0.00050001 | 0.054517 | -0.0057325 | 0.050324 | 0.00351 | -0.0011537 | -0.00080338 | -0.0039461 | 0.015502 | -0.0088175 | -58.9228 | -0.007751 | -61.5634 | 59.8459 | 59.6775 | 59.5219 | -61.5534 | 0.074307 | 0.055303 | -61.6583 | 59.6049 | 59.7095 | 59.8272 | -61.5524 | -0.039153 | -0.11201 | 2.5915 | -0.049109 | -0.009956 | -0.2804 | -0.43602 | -0.038069 | -0.35294 | 61.5886 | -0.14403 | -0.10596 | -0.24836 | -0.13069 | 121.3602 | 121.1918 | 121.0361 | 61.5065 | -121.5113 | 121.1192 | 121.2238 | 121.3415 | 61.5696 | -121.5102
615.3438 | 121.7468 | -61.5509 | 59.9167 | -0.005418 | -0.032224 | 0.00050001 | 0.054517 | -0.0055189 | 0.050324 | -0.011751 | -0.0013673 | -0.0014444 | -0.0039461 | 0.015929 | -0.0086037 | -58.9503 | 0.001407 | -61.568 | 59.855 | 59.6821 | 59.5264 | -61.5443 | 0.078886 | 0.064461 | -61.6537 | 59.6049 | 59.7141 | 59.8272 | -61.5432 | 0.006626 | -0.061657 | 2.6006 | -0.017067 | -0.023693 | -0.23463 | -0.39025 | 0.00771 | -0.31174 | 61.6298 | -0.10283 | -0.11054 | -0.20258 | -0.089494 | 121.4059 | 121.233 | 121.0773 | 61.5523 | -121.461 | 121.1558 | 121.265 | 121.3781 | 61.6154 | -121.4599
617.0938 | 121.788 | -61.5829 | 59.8297 | -0.005418 | -0.03201 | 0.00050001 | 0.054517 | -0.0055189 | 0.050538 | -0.011751 | -0.0013673 | -0.0012306 | -0.0039461 | 0.015502 | -0.0088175 | -58.9045 | 0.005985 | -61.568 | 59.8459 | 59.6775 | 59.5264 | -61.558 | 0.069728 | 0.055303 | -61.6583 | 59.6095 | 59.7141 | 59.8318 | -61.5478 | 0.024933 | 0.016161 | 2.6785 | 0.014977 | -0.009956 | -0.15223 | -0.30327 | 0.035175 | -0.22019 | 61.6527 | -0.075366 | -0.11054 | -0.11561 | 0.002059 | 121.4288 | 121.2604 | 121.1094 | 61.5889 | -121.3877 | 121.1925 | 121.2971 | 121.4147 | 61.6382 | -121.3775
618.7812 | 121.6644 | -61.5326 | 59.9716 | -0.005418 | -0.032438 | 0.00050001 | 0.054303 | -0.0050917 | 0.050752 | -0.011751 | -0.0011537 | -0.0012306 | -0.0039461 | 0.015716 | -0.0092447 | -58.9503 | -0.007751 | -61.5588 | 59.8596 | 59.6821 | 59.531 | -61.5397 | 0.074307 | 0.059882 | -61.6583 | 59.6141 | 59.7187 | 59.8272 | -61.5432 | -0.007105 | -0.11201 | 2.5823 | -0.02622 | -0.019115 | -0.28956 | -0.4406 | -0.0106 | -0.35752 | 61.6069 | -0.12572 | -0.11512 | -0.25294 | -0.14443 | 121.3922 | 121.2147 | 121.0636 | 61.5248 | -121.5113 | 121.1467 | 121.2513 | 121.3598 | 61.5925 | -121.5148
620.5312 | 121.6507 | -61.6241 | 59.9121 | -0.013049 | -0.032438 | 0.00071361 | 0.054731 | -0.0053053 | 0.050111 | -0.011751 | -0.0013673 | -0.00080338 | -0.0037325 | 0.015716 | -0.0090311 | -58.9136 | 0.001407 | -61.5451 | 59.8596 | 59.6912 | 59.5448 | -61.5397 | 0.069728 | 0.064461 | -61.6446 | 59.6141 | 59.7278 | 59.8364 | -61.534 | 0.084448 | -0.052501 | 2.7105 | 0.079068 | -0.00538 | -0.22089 | -0.36735 | 0.09011 | -0.29801 | 61.6939 | -0.020431 | -0.11054 | -0.18427 | -0.075759 | 121.4838 | 121.3154 | 121.1689 | 61.6256 | -121.4518 | 121.2382 | 121.352 | 121.4605 | 61.6886 | -121.4461
622.2812 | 121.7789 | -61.4594 | 59.9487 | 0.009844 | -0.032651 | 7.2612e-05 | 0.054517 | -0.0055189 | 0.050324 | -0.011751 | -0.0013673 | -0.001017 | -0.0037325 | 0.015716 | -0.0088175 | -59.0235 | -0.003172 | -61.5542 | 59.8733 | 59.6958 | 59.5402 | -61.5214 | 0.074307 | 0.059882 | -61.64 | 59.6324 | 59.7324 | 59.8501 | -61.5295 | -0.062031 | -0.075387 | 2.4358 | -0.094884 | -0.032853 | -0.25293 | -0.40855 | -0.070106 | -0.31631 | 61.5337 | -0.18065 | -0.11054 | -0.21631 | -0.098644 | 121.3327 | 121.1551 | 120.9995 | 61.4562 | -121.4701 | 121.0918 | 121.1918 | 121.3094 | 61.5192 | -121.4782
623.9688 | 121.7239 | -61.6058 | 59.8618 | -0.005418 | -0.032224 | 0.00071361 | 0.054303 | -0.0057325 | 0.050111 | -0.011751 | -0.0013673 | -0.0014444 | -0.0037325 | 0.015929 | -0.0088175 | -58.9274 | 0.001407 | -61.5451 | 59.8779 | 59.7004 | 59.5493 | -61.5351 | 0.078886 | 0.064461 | -61.6354 | 59.6324 | 59.737 | 59.8455 | -61.534 | 0.070716 | 0.016167 | 2.6785 | 0.060757 | -0.009959 | -0.16138 | -0.31242 | 0.071799 | -0.22934 | 61.6847 | -0.029585 | -0.10138 | -0.12476 | -0.016248 | 121.4838 | 121.3062 | 121.1552 | 61.6072 | -121.3969 | 121.2383 | 121.3428 | 121.4513 | 61.6703 | -121.3958
625.7188 | 121.788 | -61.4502 | 59.967 | -0.005418 | -0.032651 | 0.00050001 | 0.054731 | -0.0055189 | 0.050324 | -0.0041205 | -0.0015809 | -0.0012306 | -0.0037325 | 0.015716 | -0.0086037 | -59.0098 | -0.003172 | -61.5405 | 59.8871 | 59.7095 | 59.5539 | -61.5168 | 0.074307 | 0.059882 | -61.6308 | 59.637 | 59.737 | 59.8547 | -61.5203 | -0.066609 | -0.079962 | 2.4404 | -0.090305 | -0.023696 | -0.25751 | -0.41313 | -0.070104 | -0.33005 | 61.5245 | -0.18065 | -0.11054 | -0.23004 | -0.11238 | 121.3373 | 121.1597 | 121.0041 | 61.447 | -121.4838 | 121.0872 | 121.1872 | 121.3049 | 61.5101 | -121.4873
627.4844 | 121.6507 | -61.6013 | 59.9121 | 0.002213 | -0.032438 | 0.00028641 | 0.05409 | -0.0057325 | 0.050111 | -0.011751 | -0.0015809 | -0.0012306 | -0.0039461 | 0.015502 | -0.0088175 | -58.8908 | -0.003172 | -61.5222 | 59.8917 | 59.7233 | 59.5676 | -61.5168 | 0.074307 | 0.06904 | -61.6171 | 59.6507 | 59.7553 | 59.8592 | -61.502 | 0.084453 | -0.020452 | 2.7105 | 0.07907 | -0.005383 | -0.18884 | -0.34446 | 0.099273 | -0.26138 | 61.6756 | -0.015848 | -0.11512 | -0.1568 | -0.052866 | 121.4929 | 121.3245 | 121.1689 | 61.5981 | -121.4289 | 121.252 | 121.3566 | 121.4605 | 61.6703 | -121.4141
629.1719 | 121.6736 | -61.496 | 60.0174 | 0.002213 | -0.032438 | 0.00050001 | 0.054303 | -0.0055189 | 0.050111 | -0.0041205 | -0.0011537 | -0.0012306 | -0.0039461 | 0.015502 | -0.0086037 | -58.9228 | -0.003172 | -61.5268 | 59.8962 | 59.7141 | 59.5676 | -61.5031 | 0.069728 | 0.055303 | -61.6079 | 59.6462 | 59.7553 | 59.8638 | -61.502 | -0.007095 | -0.12116 | 2.5732 | -0.030793 | -0.023698 | -0.30328 | -0.44975 | -0.006012 | -0.37124 | 61.5657 | -0.11198 | -0.10596 | -0.26208 | -0.15357 | 121.3922 | 121.2101 | 121.0636 | 61.4928 | -121.5205 | 121.1421 | 121.2513 | 121.3598 | 61.5513 | -121.5194
630.9219 | 121.7697 | -61.528 | 59.8984 | 0.009844 | -0.032651 | 0.00050001 | 0.05409 | -0.0055189 | 0.050324 | -0.0041205 | -0.0013673 | -0.0012306 | -0.0041597 | 0.015716 | -0.0086037 | -58.932 | -0.003172 | -61.5222 | 59.9008 | 59.7324 | 59.5722 | -61.5031 | 0.074307 | 0.06904 | -61.6171 | 59.6507 | 59.7599 | 59.8638 | -61.4974 | 0.024948 | 0.002438 | 2.5961 | 0.005828 | -0.01912 | -0.16595 | -0.32615 | 0.03061 | -0.24765 | 61.6023 | -0.08909 | -0.1197 | -0.13848 | -0.034555 | 121.4288 | 121.2604 | 121.1002 | 61.5248 | -121.4014 | 121.1787 | 121.2879 | 121.3918 | 61.5971 | -121.3958
632.6719 | 121.7834 | -61.4868 | 59.8938 | -0.02068 | -0.032438 | 0.00050001 | 0.054517 | -0.0055189 | 0.050324 | -0.011751 | -0.0015809 | -0.0014444 | -0.0041597 | 0.015716 | -0.0088175 | -58.9274 | -0.003172 | -61.5176 | 59.9008 | 59.737 | 59.5768 | -61.5076 | 0.074307 | 0.059882 | -61.6079 | 59.6507 | 59.7645 | 59.873 | -61.4974 | -0.02083 | 0.007015 | 2.5594 | -0.030792 | -0.009962 | -0.15679 | -0.31699 | -0.010589 | -0.24307 | 61.5611 | -0.12113 | -0.11054 | -0.12933 | -0.02082 | 121.3876 | 121.2238 | 121.0636 | 61.4836 | -121.4014 | 121.1375 | 121.2513 | 121.3598 | 61.5467 | -121.3912
634.3594 | 121.7056 | -61.5967 | 59.8984 | -0.005418 | -0.032438 | 0.00050001 | 0.054517 | -0.0057325 | 0.049897 | -0.011751 | -0.0015809 | -0.001017 | -0.0037325 | 0.016143 | -0.0086037 | -58.8953 | 0.005985 | -61.5085 | 59.9008 | 59.7279 | 59.5814 | -61.4985 | 0.074307 | 0.06904 | -61.6034 | 59.6599 | 59.769 | 59.8821 | -61.502 | 0.098192 | 0.002438 | 2.7013 | 0.088228 | -0.009964 | -0.17052 | -0.31699 | 0.094696 | -0.23849 | 61.671 | -0.006689 | -0.10139 | -0.12933 | -0.01624 | 121.4975 | 121.3245 | 121.1781 | 61.6027 | -121.3969 | 121.2566 | 121.3657 | 121.4788 | 61.6657 | -121.4004
636.1094 | 121.7743 | -61.4319 | 59.9808 | 0.002213 | -0.032438 | 7.2612e-05 | 0.054303 | -0.0057325 | 0.050111 | -0.011751 | -0.0013673 | -0.0014444 | -0.0037325 | 0.015716 | -0.0090311 | -58.9869 | -0.007751 | -61.5222 | 59.9008 | 59.7324 | 59.5768 | -61.5076 | 0.069728 | 0.064461 | -61.6079 | 59.6507 | 59.7645 | 59.873 | -61.502 | -0.075761 | -0.07996 | 2.445 | -0.090302 | -0.014541 | -0.24834 | -0.40397 | -0.070099 | -0.33004 | 61.5016 | -0.17606 | -0.10596 | -0.2163 | -0.10779 | 121.3327 | 121.1643 | 121.0087 | 61.4241 | -121.4884 | 121.0826 | 121.1964 | 121.3049 | 61.4963 | -121.4828
637.8594 | 121.7194 | -61.5784 | 59.8892 | -0.005418 | -0.032438 | 0.00050001 | 0.054303 | -0.0055189 | 0.049897 | -0.011751 | -0.0013673 | -0.0012306 | -0.0039461 | 0.016143 | -0.0083901 | -58.8862 | -0.003172 | -61.5039 | 59.9145 | 59.7416 | 59.586 | -61.4985 | 0.074307 | 0.06904 | -61.5896 | 59.6645 | 59.7782 | 59.8913 | -61.4882 | 0.079881 | 0.025328 | 2.6922 | 0.074495 | -0.005386 | -0.14763 | -0.30326 | 0.090122 | -0.22476 | 61.6527 | -0.011264 | -0.10139 | -0.11102 | 0.002072 | 121.4929 | 121.32 | 121.1643 | 61.5752 | -121.3877 | 121.2428 | 121.3566 | 121.4697 | 61.6474 | -121.3775
639.5469 | 121.6599 | -61.4594 | 60.054 | -0.005418 | -0.032651 | 0.00028641 | 0.054517 | -0.0055189 | 0.050111 | -0.0041205 | -0.00094006 | -0.0012306 | -0.0039461 | 0.016143 | -0.0083901 | -58.9091 | -0.007751 | -61.4856 | 59.9329 | 59.7462 | 59.6089 | -61.4756 | 0.074307 | 0.055303 | -61.5851 | 59.6874 | 59.7919 | 59.8959 | -61.4745 | -0.016242 | -0.12115 | 2.5503 | -0.026209 | -0.009967 | -0.30785 | -0.44516 | -0.01516 | -0.36666 | 61.5337 | -0.1257 | -0.11054 | -0.26207 | -0.15814 | 121.3922 | 121.2055 | 121.0682 | 61.4516 | -121.5296 | 121.1467 | 121.2513 | 121.3552 | 61.5147 | -121.5285
641.3125 | 121.6644 | -61.441 | 60.0677 | 0.002213 | -0.032438 | 0.00028641 | 0.054944 | -0.0057325 | 0.049897 | -0.011751 | -0.0015809 | -0.0018716 | -0.0039461 | 0.015929 | -0.0083901 | -58.9045 | -0.007751 | -61.4764 | 59.9329 | 59.7599 | 59.618 | -61.4756 | 0.069728 | 0.059882 | -61.5713 | 59.6919 | 59.7919 | 59.905 | -61.4699 | -0.034553 | -0.13489 | 2.5365 | -0.035364 | -0.000811 | -0.30785 | -0.44974 | -0.028892 | -0.37581 | 61.5108 | -0.13028 | -0.10139 | -0.27581 | -0.16272 | 121.3739 | 121.2009 | 121.0591 | 61.4333 | -121.5433 | 121.133 | 121.233 | 121.3461 | 61.5009 | -121.5377
643.0625 | 121.669 | -61.5738 | 59.9396 | 0.002213 | -0.032865 | 0.00028641 | 0.054731 | -0.0055189 | 0.050111 | -0.0041205 | -0.00094006 | -0.0012306 | -0.0037325 | 0.015716 | -0.0088175 | -58.8633 | 0.001407 | -61.4672 | 59.9283 | 59.7599 | 59.6043 | -61.4756 | 0.074307 | 0.06904 | -61.5759 | 59.6782 | 59.7919 | 59.9004 | -61.4699 | 0.098199 | -0.011291 | 2.7105 | 0.10654 | 0.008346 | -0.17967 | -0.3353 | 0.10386 | -0.26137 | 61.6481 | -0.002105 | -0.10596 | -0.14763 | -0.039125 | 121.5021 | 121.3337 | 121.1781 | 61.5752 | -121.4152 | 121.252 | 121.3657 | 121.4742 | 61.6428 | -121.4095
644.7344 | 121.788 | -61.3861 | 60.0174 | -0.013049 | -0.032651 | 0.00028641 | 0.05409 | -0.0055189 | 0.049897 | -0.0041205 | -0.0013673 | -0.001017 | -0.0037325 | 0.015716 | -0.0088175 | -58.9594 | -0.003172 | -61.481 | 59.9329 | 59.7599 | 59.6043 | -61.4802 | 0.069728 | 0.064461 | -61.5805 | 59.6828 | 59.7874 | 59.9096 | -61.4699 | -0.094064 | -0.084532 | 2.4267 | -0.094874 | -0.00081 | -0.25749 | -0.41312 | -0.083824 | -0.33461 | 61.4558 | -0.19437 | -0.11054 | -0.23003 | -0.10779 | 121.319 | 121.146 | 120.9904 | 61.3829 | -121.4976 | 121.0689 | 121.1735 | 121.2957 | 61.4506 | -121.4873
646.5 | 121.7514 | -61.4594 | 59.9396 | -0.005418 | -0.032651 | 0.00028641 | 0.054731 | -0.0055189 | 0.049897 | -0.0041205 | -0.0015809 | -0.001658 | -0.0039461 | 0.015929 | -0.0086037 | -58.9136 | 0.005985 | -61.4718 | 59.9374 | 59.7645 | 59.6226 | -61.471 | 0.078886 | 0.073618 | -61.5667 | 59.6965 | 59.8011 | 59.9096 | -61.4654 | -0.011663 | -0.002134 | 2.5457 | -0.012475 | -0.000812 | -0.17509 | -0.31698 | -0.006002 | -0.24306 | 61.5382 | -0.10739 | -0.10139 | -0.13848 | -0.029968 | 121.3968 | 121.2238 | 121.0819 | 61.4653 | -121.4106 | 121.1559 | 121.2604 | 121.369 | 61.533 | -121.4049
648.1875 | 121.669 | -61.4273 | 60.1089 | -0.005418 | -0.032651 | 0.00050001 | 0.054517 | -0.0053053 | 0.050111 | 0.00351 | -0.0015809 | -0.0012306 | -0.0037325 | 0.016143 | -0.0086037 | -58.8862 | 0.001407 | -61.4672 | 59.9466 | 59.7782 | 59.6226 | -61.4619 | 0.078886 | 0.064461 | -61.553 | 59.7011 | 59.8103 | 59.9188 | -61.4516 | -0.034549 | -0.16235 | 2.5411 | -0.03994 | -0.005391 | -0.33073 | -0.48636 | -0.02431 | -0.40785 | 61.5062 | -0.1257 | -0.10139 | -0.29869 | -0.19018 | 121.3739 | 121.2055 | 121.0499 | 61.4287 | -121.5708 | 121.1284 | 121.2376 | 121.3461 | 61.4918 | -121.5606
649.9375 | 121.6324 | -61.5417 | 59.9762 | 0.002213 | -0.032651 | 7.2612e-05 | 0.054303 | -0.0055189 | 0.050111 | -0.011751 | -0.0011537 | -0.0012306 | -0.0041597 | 0.015716 | -0.0086037 | -58.7855 | 0.001407 | -61.4627 | 59.9466 | 59.7736 | 59.6134 | -61.4619 | 0.074307 | 0.064461 | -61.5713 | 59.6919 | 59.7965 | 59.9188 | -61.4608 | 0.079892 | -0.029598 | 2.7563 | 0.079079 | -0.000813 | -0.20256 | -0.36276 | 0.080973 | -0.28426 | 61.6161 | -0.02957 | -0.11054 | -0.17968 | -0.057431 | 121.4883 | 121.3154 | 121.1552 | 61.5432 | -121.4381 | 121.2337 | 121.3383 | 121.4605 | 61.6062 | -121.437
652.1094 | 121.788 | -61.4639 | 59.9304 | 0.009844 | -0.032438 | 0.00028641 | 0.054517 | -0.0055189 | 0.049897 | -0.0041205 | -0.0013673 | -0.0012306 | -0.0037325 | 0.015929 | -0.0088175 | -58.8221 | 0.005985 | -61.4535 | 59.9512 | 59.7736 | 59.6272 | -61.4527 | 0.069728 | 0.064461 | -61.5622 | 59.7011 | 59.8103 | 59.9233 | -61.4516 | 0.011229 | 0.020756 | 2.6418 | 0.010415 | -0.000814 | -0.15678 | -0.30325 | 0.012311 | -0.22933 | 61.5337 | -0.098233 | -0.11054 | -0.12017 | -0.007077 | 121.4151 | 121.2376 | 121.0911 | 61.4699 | -121.3831 | 121.165 | 121.2742 | 121.3873 | 61.5284 | -121.382
654 | 121.6644 | -61.4456 | 60.054 | -0.005418 | -0.032438 | 7.2612e-05 | 0.054517 | -0.0057325 | 0.050324 | -0.011751 | -0.0011537 | -0.001017 | -0.0041597 | 0.016143 | -0.0086037 | -58.8221 | -0.003172 | -61.4581 | 59.9466 | 59.7828 | 59.6317 | -61.4573 | 0.078886 | 0.059882 | -61.5576 | 59.7011 | 59.8103 | 59.9188 | -61.4562 | -0.01166 | -0.10742 | 2.6235 | -0.012473 | -0.000813 | -0.27122 | -0.42227 | -0.010578 | -0.35292 | 61.5245 | -0.11196 | -0.10139 | -0.24376 | -0.13525 | 121.3922 | 121.2284 | 121.0774 | 61.4424 | -121.5113 | 121.1467 | 121.2559 | 121.3644 | 61.5055 | -121.5102
655.7031 | 121.7972 | -61.377 | 60.0311 | 0.002213 | -0.032865 | 0.00050001 | 0.054517 | -0.0055189 | 0.050324 | -0.011751 | -0.0015809 | -0.0012306 | -0.0041597 | 0.016143 | -0.0088175 | -58.8816 | -0.003172 | -61.4444 | 59.9603 | 59.7874 | 59.6363 | -61.439 | 0.074307 | 0.059882 | -61.5438 | 59.7148 | 59.8194 | 59.9371 | -61.4333 | -0.062009 | -0.070795 | 2.4954 | -0.067403 | -0.005394 | -0.24375 | -0.3948 | -0.056349 | -0.3163 | 61.4513 | -0.16689 | -0.11054 | -0.21172 | -0.094049 | 121.3373 | 121.1643 | 121.0133 | 61.3738 | -121.4701 | 121.0918 | 121.1964 | 121.314 | 61.4368 | -121.4644
657.4062 | 121.7606 | -61.4639 | 59.9167 | 0.002213 | -0.032651 | 0.00028641 | 0.054303 | -0.0057325 | 0.050111 | -0.011751 | -0.0017945 | -0.0012306 | -0.0037325 | 0.015929 | -0.0086037 | -58.79 | 0.001407 | -61.4444 | 59.9695 | 59.8011 | 59.6501 | -61.439 | 0.078886 | 0.06904 | -61.5438 | 59.724 | 59.8286 | 59.9417 | -61.4287 | 0.024966 | 0.052803 | 2.6739 | 0.019572 | -0.005394 | -0.11557 | -0.26662 | 0.035205 | -0.1927 | 61.5428 | -0.079918 | -0.11512 | -0.088117 | 0.024971 | 121.4334 | 121.265 | 121.114 | 61.4653 | -121.3556 | 121.1879 | 121.2925 | 121.4056 | 61.533 | -121.3454
659.2344 | 121.8201 | -61.3541 | 60.1135 | -0.005418 | -0.032865 | 0.00028641 | 0.05409 | -0.0053053 | 0.050111 | -0.0041205 | -0.0015809 | -0.0012306 | -0.0039461 | 0.015929 | -0.0088175 | -58.877 | -0.003172 | -61.4352 | 59.9832 | 59.8057 | 59.6546 | -61.4252 | 0.074307 | 0.06904 | -61.5347 | 59.724 | 59.8377 | 59.9462 | -61.4196 | -0.07116 | -0.1303 | 2.477 | -0.081134 | -0.009974 | -0.30783 | -0.45888 | -0.0655 | -0.38954 | 61.4284 | -0.18062 | -0.11512 | -0.2758 | -0.16729 | 121.3373 | 121.1598 | 121.0087 | 61.3509 | -121.5387 | 121.0781 | 121.1918 | 121.3003 | 61.4231 | -121.5331
660.9688 | 121.6782 | -61.3724 | 60.0906 | -0.005418 | -0.032651 | 0.00028641 | 0.054303 | -0.0053053 | 0.050111 | -0.0041205 | -0.0013673 | -0.0012306 | -0.0041597 | 0.015929 | -0.0088175 | -58.8175 | 0.005985 | -61.426 | 59.9832 | 59.8103 | 59.6592 | -61.4252 | 0.074307 | 0.064461 | -61.5255 | 59.7331 | 59.8469 | 59.9508 | -61.4196 | -0.05285 | -0.10741 | 2.5549 | -0.053668 | -0.000818 | -0.28037 | -0.43142 | -0.04719 | -0.35749 | 61.4467 | -0.15316 | -0.10597 | -0.24375 | -0.13982 | 121.3556 | 121.1826 | 121.0316 | 61.3784 | -121.5159 | 121.1055 | 121.2193 | 121.3232 | 61.4368 | -121.5102
662.6562 | 121.788 | -61.4319 | 59.967 | -0.005418 | -0.032651 | 0.00028641 | 0.054303 | -0.0055189 | 0.050111 | -0.019381 | -0.0011537 | -0.0012306 | -0.0039461 | 0.016143 | -0.0086037 | -58.7809 | 0.005985 | -61.426 | 59.9786 | 59.8194 | 59.6684 | -61.4206 | 0.074307 | 0.064461 | -61.521 | 59.7286 | 59.8469 | 59.9554 | -61.4241 | 0.011239 | 0.011605 | 2.651 | 0.005842 | -0.005397 | -0.14761 | -0.29866 | 0.007741 | -0.23848 | 61.5062 | -0.089067 | -0.096808 | -0.12016 | -0.011648 | 121.4105 | 121.2513 | 121.1003 | 61.4379 | -121.3877 | 121.1604 | 121.2788 | 121.3873 | 61.4963 | -121.3912
664.3594 | 121.7056 | -61.4502 | 60.0174 | -0.005418 | -0.032651 | 0.00050001 | 0.05409 | -0.0055189 | 0.049683 | -0.011751 | -0.0011537 | -0.001017 | -0.0041597 | 0.016143 | -0.0086037 | -58.7214 | -0.003172 | -61.4123 | 59.997 | 59.8332 | 59.673 | -61.4023 | 0.078886 | 0.055303 | -61.5164 | 59.7515 | 59.8652 | 59.9829 | -61.4012 | 0.047865 | -0.020435 | 2.7288 | 0.037887 | -0.009978 | -0.18423 | -0.34444 | 0.048945 | -0.26594 | 61.5291 | -0.066178 | -0.11512 | -0.1522 | -0.03453 | 121.4472 | 121.2834 | 121.1232 | 61.447 | -121.4197 | 121.2017 | 121.3154 | 121.4331 | 61.5055 | -121.4186
666.1094 | 121.7377 | -61.3815 | 60.0494 | 0.002213 | -0.033079 | 0.00028641 | 0.05409 | -0.0055189 | 0.049897 | -0.011751 | -0.0011537 | -0.001658 | -0.0043733 | 0.01657 | -0.0090311 | -58.8175 | -0.007751 | -61.4077 | 59.9924 | 59.8332 | 59.6775 | -61.4069 | 0.074307 | 0.064461 | -61.5164 | 59.7469 | 59.8606 | 59.9737 | -61.3967 | -0.025378 | -0.057056 | 2.564 | -0.026199 | -0.000821 | -0.21627 | -0.3719 | -0.01514 | -0.30256 | 61.4558 | -0.13484 | -0.1197 | -0.18882 | -0.07573 | 121.3739 | 121.2147 | 121.0591 | 61.3738 | -121.4563 | 121.1284 | 121.2422 | 121.3552 | 61.446 | -121.4461
667.8125 | 121.7834 | -61.3358 | 60.0952 | -0.005418 | -0.032651 | 0.00028641 | 0.054517 | -0.0057325 | 0.050111 | 0.00351 | -0.0013673 | -0.0012306 | -0.0037325 | 0.015716 | -0.0088175 | -58.8404 | 0.010564 | -61.4032 | 60.0015 | 59.8286 | 59.6775 | -61.4023 | 0.078886 | 0.06904 | -61.5072 | 59.7515 | 59.8515 | 59.9783 | -61.4058 | -0.066576 | -0.093677 | 2.4954 | -0.067397 | -0.000821 | -0.26663 | -0.41768 | -0.070075 | -0.34376 | 61.4146 | -0.17146 | -0.10139 | -0.24375 | -0.11693 | 121.3373 | 121.1643 | 121.0133 | 61.3463 | -121.4975 | 121.0872 | 121.1872 | 121.314 | 61.4048 | -121.501
669.5156 | 121.7148 | -61.3861 | 60.0677 | 0.002213 | -0.032865 | 0.00028641 | 0.054517 | -0.0055189 | 0.050111 | -0.011751 | -0.0013673 | -0.0012306 | -0.0041597 | 0.016143 | -0.0088175 | -58.7076 | -0.007751 | -61.3803 | 60.029 | 59.8561 | 59.7096 | -61.3749 | 0.074307 | 0.059882 | -61.4889 | 59.7835 | 59.8881 | 60.0103 | -61.3692 | 0.011251 | -0.03874 | 2.6785 | 0.005848 | -0.005403 | -0.21169 | -0.35816 | 0.01691 | -0.28424 | 61.4604 | -0.10279 | -0.1197 | -0.17966 | -0.057412 | 121.4151 | 121.2422 | 121.0957 | 61.3784 | -121.4426 | 121.1696 | 121.2742 | 121.3964 | 61.446 | -121.4369
671.2031 | 121.6553 | -61.3861 | 60.141 | 0.002213 | -0.033292 | 0.00028641 | 0.054517 | -0.0057325 | 0.050111 | -0.0041205 | -0.0013673 | -0.0014444 | -0.0039461 | 0.016143 | -0.0086037 | -58.7397 | 0.001407 | -61.3757 | 60.0382 | 59.8606 | 59.7004 | -61.3794 | 0.074307 | 0.064461 | -61.4752 | 59.7881 | 59.8835 | 60.0012 | -61.3692 | 0.006672 | -0.10283 | 2.6464 | 0.010426 | 0.003754 | -0.28035 | -0.44056 | 0.01691 | -0.35291 | 61.4604 | -0.089057 | -0.10597 | -0.25748 | -0.13981 | 121.4243 | 121.2467 | 121.0865 | 61.3875 | -121.5204 | 121.1742 | 121.2696 | 121.3873 | 61.4506 | -121.5102
672.9375 | 121.7148 | -61.3678 | 60.0998 | 0.002213 | -0.032865 | 0.00071361 | 0.05409 | -0.0055189 | 0.049683 | -0.019381 | -0.0015809 | -0.0012306 | -0.0039461 | 0.016143 | -0.0086037 | -58.6573 | -0.003172 | -61.3299 | 60.0794 | 59.9019 | 59.7554 | -61.3291 | 0.074307 | 0.059882 | -61.434 | 59.8293 | 59.9385 | 60.0515 | -61.328 | 0.03873 | -0.020421 | 2.7105 | 0.037899 | -0.000831 | -0.19794 | -0.34442 | 0.039809 | -0.2705 | 61.4421 | -0.066159 | -0.10597 | -0.16134 | -0.048248 | 121.4472 | 121.2696 | 121.1232 | 61.3646 | -121.4289 | 121.1971 | 121.3063 | 121.4193 | 61.4277 | -121.4278
674.625 | 121.7697 | -61.3632 | 60.0494 | -0.013049 | -0.032651 | 0.00050001 | 0.054303 | -0.0057325 | 0.050111 | -0.019381 | -0.0013673 | -0.0014444 | -0.0039461 | 0.016143 | -0.0088175 | -58.7259 | 0.001407 | -61.3574 | 60.0656 | 59.8881 | 59.7371 | -61.3382 | 0.078886 | 0.059882 | -61.4431 | 59.811 | 59.9201 | 60.0378 | -61.3371 | 0.024995 | 0.016198 | 2.6373 | 0.005851 | -0.019144 | -0.16133 | -0.31238 | 0.026074 | -0.23846 | 61.4421 | -0.079894 | -0.10597 | -0.1293 | -0.01163 | 121.4289 | 121.2513 | 121.1003 | 61.3646 | -121.3877 | 121.1742 | 121.2834 | 121.401 | 61.4231 | -121.3866
676.3438 | 121.7789 | -61.377 | 60.0266 | -0.005418 | -0.033079 | 0.00028641 | 0.054731 | -0.0057325 | 0.050111 | -0.0041205 | -0.0011537 | -0.0012306 | -0.0043733 | 0.016143 | -0.0086037 | -58.6985 | 0.005985 | -61.3574 | 60.0565 | 59.8835 | 59.7279 | -61.352 | 0.083464 | 0.064461 | -61.4431 | 59.8064 | 59.911 | 60.0378 | -61.3509 | 0.024991 | 0.029929 | 2.6785 | 0.019584 | -0.005407 | -0.14302 | -0.29865 | 0.02607 | -0.22015 | 61.4604 | -0.066161 | -0.092231 | -0.11557 | 0.011258 | 121.4334 | 121.2605 | 121.1049 | 61.3829 | -121.3785 | 121.1834 | 121.2879 | 121.4148 | 61.4414 | -121.3774
678.0312 | 121.7972 | -61.2442 | 60.1547 | -0.013049 | -0.032651 | 0.00050001 | 0.054303 | -0.0057325 | 0.050111 | -0.011751 | -0.0015809 | -0.0012306 | -0.0039461 | 0.015929 | -0.0086037 | -58.7534 | 0.005985 | -61.3299 | 60.0931 | 59.9202 | 59.7645 | -61.3108 | 0.074307 | 0.064461 | -61.4156 | 59.8476 | 59.9522 | 60.0699 | -61.3143 | -0.06655 | -0.061618 | 2.4908 | -0.085697 | -0.019147 | -0.23456 | -0.3902 | -0.07005 | -0.30712 | 61.3185 | -0.17144 | -0.10139 | -0.20253 | -0.084866 | 121.3373 | 121.1644 | 121.0087 | 61.2502 | -121.4655 | 121.0918 | 121.1964 | 121.3141 | 61.3087 | -121.469
679.7188 | 121.6507 | -61.3998 | 60.0723 | -0.013049 | -0.033079 | 0.00028641 | 0.054517 | -0.0057325 | 0.049897 | -0.011751 | -0.0013673 | -0.0014444 | -0.0039461 | 0.016143 | -0.0090311 | -58.6573 | -0.003172 | -61.3436 | 60.0748 | 59.9019 | 59.7554 | -61.3336 | 0.083464 | 0.064461 | -61.434 | 59.8201 | 59.9201 | 60.0424 | -61.328 | 0.066194 | 0.002466 | 2.7426 | 0.056207 | -0.009987 | -0.17048 | -0.31696 | 0.071852 | -0.25219 | 61.4833 | -0.034116 | -0.10597 | -0.15219 | -0.02994 | 121.4746 | 121.3017 | 121.1552 | 61.3967 | -121.406 | 121.22 | 121.32 | 121.4422 | 61.4643 | -121.4003
681.4531 | 121.6873 | -61.2854 | 60.2097 | 0.002213 | -0.032651 | 0.00050001 | 0.054517 | -0.0057325 | 0.049897 | -0.011751 | -0.0013673 | -0.0012306 | -0.0039461 | 0.016143 | -0.0086037 | -58.7168 | -0.003172 | -61.3299 | 60.0839 | 59.9247 | 59.7737 | -61.3153 | 0.069728 | 0.059882 | -61.4202 | 59.8384 | 59.9476 | 60.0744 | -61.3143 | -0.029931 | -0.12571 | 2.5686 | -0.044499 | -0.014568 | -0.28491 | -0.43597 | -0.028852 | -0.37121 | 61.3551 | -0.13482 | -0.10597 | -0.26204 | -0.13522 | 121.3693 | 121.2101 | 121.0591 | 61.2822 | -121.525 | 121.1238 | 121.233 | 121.3598 | 61.3453 | -121.5239
683.2031 | 121.701 | -61.3266 | 60.1776 | 0.009844 | -0.033506 | 0.00028641 | 0.054303 | -0.0057325 | 0.050324 | -0.0041205 | -0.0015809 | -0.0014444 | -0.0039461 | 0.016143 | -0.0088175 | -58.6389 | 0.005985 | -61.3116 | 60.1023 | 59.9293 | 59.7828 | -61.3016 | 0.074307 | 0.064461 | -61.4065 | 59.843 | 59.9568 | 60.079 | -61.3005 | 0.025005 | -0.075349 | 2.6877 | 0.015013 | -0.009992 | -0.24829 | -0.39477 | 0.026083 | -0.33459 | 61.4009 | -0.079885 | -0.10597 | -0.22084 | -0.098596 | 121.4289 | 121.2559 | 121.1094 | 61.3326 | -121.4792 | 121.1696 | 121.2834 | 121.4056 | 61.3911 | -121.4781
684.9688 | 121.7834 | -61.2213 | 60.1959 | 0.002213 | -0.033079 | 7.2612e-05 | 0.054303 | -0.0057325 | 0.049897 | -0.0041205 | -0.0013673 | -0.0012306 | -0.0037325 | 0.016357 | -0.0088175 | -58.7442 | -0.003172 | -61.3116 | 60.1023 | 59.9293 | 59.7874 | -61.3016 | 0.074307 | 0.06904 | -61.4065 | 59.8568 | 59.9613 | 60.0836 | -61.3005 | -0.080281 | -0.09366 | 2.4771 | -0.090273 | -0.009992 | -0.2666 | -0.4085 | -0.079203 | -0.33916 | 61.2956 | -0.18517 | -0.10597 | -0.23457 | -0.11233 | 121.3236 | 121.1506 | 121.0087 | 61.2181 | -121.4975 | 121.0781 | 121.1827 | 121.3049 | 61.2904 | -121.4964
686.7188 | 121.6736 | -61.4319 | 60.0677 | -0.005418 | -0.033292 | 0.00050001 | 0.054517 | -0.0059463 | 0.050111 | -0.027012 | -0.0015809 | -0.0014444 | -0.0037325 | 0.016143 | -0.0086037 | -58.6618 | 0.015142 | -61.3299 | 60.0794 | 59.9064 | 59.7599 | -61.3199 | 0.078886 | 0.064461 | -61.4202 | 59.8339 | 59.9385 | 60.0561 | -61.3188 | 0.11198 | 0.011622 | 2.77 | 0.10199 | -0.009989 | -0.16132 | -0.3078 | 0.11305 | -0.23388 | 61.5108 | 0.011664 | -0.10139 | -0.12929 | -0.011626 | 121.5113 | 121.3383 | 121.1918 | 61.447 | -121.3877 | 121.2658 | 121.3703 | 121.488 | 61.4963 | -121.3866
688.4688 | 121.6736 | -61.4136 | 60.0769 | -0.005418 | -0.033079 | 0.00028641 | 0.054303 | -0.0057325 | 0.050111 | -0.0041205 | -0.0013673 | -0.0014444 | -0.0041597 | 0.015929 | -0.0088175 | -58.6389 | 0.010564 | -61.3116 | 60.1023 | 59.9293 | 59.7828 | -61.3016 | 0.074307 | 0.059882 | -61.4019 | 59.8568 | 59.9613 | 60.0699 | -61.3005 | 0.11198 | 0.025359 | 2.7746 | 0.10199 | -0.009992 | -0.14758 | -0.29406 | 0.11306 | -0.22014 | 61.4879 | 0.011668 | -0.10139 | -0.11556 | -0.007046 | 121.5158 | 121.3429 | 121.1964 | 61.4241 | -121.3785 | 121.2703 | 121.3749 | 121.4834 | 61.4735 | -121.3774
690.2344 | 121.7972 | -61.171 | 60.2554 | -0.013049 | -0.033506 | -0.00014099 | 0.054517 | -0.0061599 | 0.050111 | -0.011751 | -0.0015809 | -0.0014444 | -0.0041597 | 0.016143 | -0.0086037 | -58.5291 | 0.005985 | -61.1742 | 60.2442 | 60.0758 | 59.911 | -61.1688 | 0.078886 | 0.064461 | -61.2691 | 59.9941 | 60.0941 | 60.2164 | -61.1632 | 0.002154 | -0.011239 | 2.6419 | -0.003278 | -0.005432 | -0.17958 | -0.34439 | 0.007808 | -0.26131 | 61.2498 | -0.098164 | -0.10597 | -0.1613 | -0.039058 | 121.4152 | 121.2468 | 121.082 | 61.1769 | -121.4242 | 121.1651 | 121.2651 | 121.3873 | 61.2354 | -121.4186
691.9844 | 121.6782 | -61.0336 | 60.4843 | 0.009844 | -0.032865 | 0.00050001 | 0.054517 | -0.0057325 | 0.049897 | -0.019381 | -0.0011537 | -0.0014444 | -0.0041597 | 0.016357 | -0.0088175 | -58.3826 | 0.001407 | -61.0415 | 60.377 | 60.2086 | 60.0576 | -61.0269 | 0.078886 | 0.064461 | -61.1272 | 60.1269 | 60.2315 | 60.3537 | -61.0166 | 0.006771 | -0.10735 | 2.6511 | -0.007837 | -0.014608 | -0.27568 | -0.42675 | 0.017001 | -0.35742 | 61.1125 | -0.093553 | -0.11055 | -0.25283 | -0.13058 | 121.4106 | 121.2423 | 121.0912 | 61.035 | -121.5112 | 121.1605 | 121.2651 | 121.3874 | 61.0981 | -121.5009
693.7344 | 121.6644 | -61.1023 | 60.3882 | -0.005418 | -0.033292 | 0.00028641 | 0.05409 | -0.0055189 | 0.049897 | 0.00351 | -0.0013673 | -0.001017 | -0.0041597 | 0.016143 | -0.0090311 | -58.3368 | 0.010564 | -61.0277 | 60.3999 | 60.2224 | 60.0667 | -61.0085 | 0.078886 | 0.064461 | -61.118 | 60.1452 | 60.2544 | 60.3629 | -61.0075 | 0.093752 | 0.011674 | 2.7655 | 0.074563 | -0.019189 | -0.16581 | -0.32147 | 0.094823 | -0.24298 | 61.1812 | -0.015731 | -0.11055 | -0.1338 | -0.025295 | 121.5022 | 121.3247 | 121.169 | 61.1129 | -121.3967 | 121.2475 | 121.3567 | 121.4652 | 61.1668 | -121.3957
695.4219 | 121.788 | -60.965 | 60.4752 | -0.02068 | -0.033292 | 7.2612e-05 | 0.054303 | -0.0057325 | 0.049897 | -0.011751 | -0.0015809 | -0.0012306 | -0.0039461 | 0.016143 | -0.0088175 | -58.4512 | 0.001407 | -61.0186 | 60.3953 | 60.2224 | 60.0667 | -61.0131 | 0.074307 | 0.059882 | -61.1272 | 60.1544 | 60.2498 | 60.3675 | -61.0075 | -0.048156 | -0.079879 | 2.5137 | -0.05361 | -0.005454 | -0.25278 | -0.40844 | -0.042506 | -0.32079 | 61.0393 | -0.16222 | -0.11971 | -0.22536 | -0.10769 | 121.3602 | 121.1873 | 121.0317 | 60.9664 | -121.4883 | 121.1193 | 121.2148 | 121.3324 | 61.0248 | -121.4826
697.1719 | 121.7514 | -61.0794 | 60.3882 | 0.002213 | -0.033079 | 0.00028641 | 0.054303 | -0.0057325 | 0.049897 | -0.019381 | -0.0015809 | -0.0012306 | -0.0037325 | 0.016143 | -0.0088175 | -58.3826 | 0.001407 | -61.0369 | 60.377 | 60.2086 | 60.053 | -61.0406 | 0.078886 | 0.064461 | -61.1363 | 60.1269 | 60.2315 | 60.3446 | -61.0304 | 0.038812 | -0.011218 | 2.6969 | 0.042518 | 0.003706 | -0.17955 | -0.3352 | 0.049041 | -0.26129 | 61.1583 | -0.056934 | -0.10598 | -0.1567 | -0.043609 | 121.4564 | 121.288 | 121.1324 | 61.0808 | -121.4288 | 121.2063 | 121.3109 | 121.424 | 61.1439 | -121.4186
698.9219 | 121.6553 | -61.0519 | 60.4706 | 0.002213 | -0.033292 | 0.00028641 | 0.054517 | -0.0057325 | 0.049897 | -0.0041205 | -0.0011537 | -0.001017 | -0.0039461 | 0.016357 | -0.0088175 | -58.4421 | 0.001407 | -61.0827 | 60.3449 | 60.172 | 60.0118 | -61.0681 | 0.083464 | 0.059882 | -61.1775 | 60.0903 | 60.1903 | 60.3125 | -61.0624 | -0.016128 | -0.12566 | 2.6099 | -0.030731 | -0.014603 | -0.29857 | -0.45881 | -0.010476 | -0.38032 | 61.1354 | -0.12561 | -0.11513 | -0.2803 | -0.15806 | 121.3969 | 121.2239 | 121.0637 | 61.0533 | -121.5387 | 121.1422 | 121.2422 | 121.3645 | 61.1118 | -121.533
700.6094 | 121.7377 | -61.116 | 60.3012 | 0.002213 | -0.033079 | 0.00071361 | 0.05409 | -0.0061599 | 0.049897 | -0.0041205 | -0.0015809 | -0.0012306 | -0.0041597 | 0.016357 | -0.0088175 | -58.5474 | 0.005985 | -61.1513 | 60.2717 | 60.0987 | 59.9523 | -61.1413 | 0.069728 | 0.055303 | -61.2462 | 60.017 | 60.1262 | 60.2393 | -61.1357 | -0.025304 | -0.029545 | 2.5687 | -0.035318 | -0.010014 | -0.20246 | -0.34896 | -0.019651 | -0.2842 | 61.1858 | -0.1302 | -0.11055 | -0.17503 | -0.061941 | 121.3877 | 121.2148 | 121.0683 | 61.122 | -121.4425 | 121.133 | 121.2422 | 121.3553 | 61.1713 | -121.4369
702.3906 | 121.788 | -61.1618 | 60.2646 | -0.005418 | -0.033079 | 0.00050001 | 0.054517 | -0.0059463 | 0.050111 | 0.00351 | -0.0015809 | -0.0012306 | -0.0037325 | 0.01657 | -0.0083901 | -58.4695 | 0.010564 | -61.1239 | 60.2946 | 60.1262 | 59.9706 | -61.1139 | 0.078886 | 0.06904 | -61.2096 | 60.0491 | 60.1582 | 60.2713 | -61.1128 | 0.047946 | 0.029968 | 2.6923 | 0.037928 | -0.010018 | -0.13837 | -0.29402 | 0.04902 | -0.21553 | 61.2407 | -0.047796 | -0.096816 | -0.10636 | 0.00673 | 121.4564 | 121.288 | 121.1324 | 61.1724 | -121.3784 | 121.2109 | 121.32 | 121.4331 | 61.2308 | -121.3774
704.0781 | 121.6507 | -61.0886 | 60.3836 | 0.002213 | -0.033292 | 0.00028641 | 0.054303 | -0.0061599 | 0.049683 | -0.011751 | -0.0013673 | -0.0014444 | -0.0043733 | 0.016357 | -0.0088175 | -58.378 | 0.005985 | -61.0506 | 60.3724 | 60.1949 | 60.0484 | -61.0452 | 0.078886 | 0.06904 | -61.1455 | 60.1177 | 60.2223 | 60.3354 | -61.0441 | 0.043388 | -0.011218 | 2.7106 | 0.037938 | -0.00545 | -0.1887 | -0.33521 | 0.04446 | -0.26587 | 61.1674 | -0.056936 | -0.1014 | -0.16128 | -0.048189 | 121.4609 | 121.2835 | 121.137 | 61.0945 | -121.4288 | 121.2063 | 121.3109 | 121.424 | 61.1576 | -121.4277
705.8125 | 121.6736 | -61.0657 | 60.4156 | -0.005418 | -0.033506 | 0.00028641 | 0.054303 | -0.0057325 | 0.050111 | -0.0041205 | -0.0013673 | -0.001017 | -0.0041597 | 0.015929 | -0.0088175 | -58.323 | 0.001407 | -60.9865 | 60.4319 | 60.259 | 60.0988 | -60.9811 | 0.078886 | 0.059882 | -61.0768 | 60.1818 | 60.2864 | 60.3949 | -60.9754 | 0.084605 | 0.016258 | 2.7426 | 0.079146 | -0.005459 | -0.15664 | -0.31688 | 0.090254 | -0.23381 | 61.1446 | -0.011143 | -0.1014 | -0.12922 | -0.02071 | 121.4976 | 121.3247 | 121.1644 | 61.0671 | -121.3967 | 121.2475 | 121.3521 | 121.4606 | 61.1256 | -121.3911
707.5625 | 121.6507 | -60.8826 | 60.6308 | 0.002213 | -0.03372 | 7.2612e-05 | 0.054517 | -0.0059463 | 0.04947 | 0.00351 | -0.0015809 | -0.0014444 | -0.0039461 | 0.016143 | -0.0090311 | -58.2818 | 0.001407 | -60.9041 | 60.5143 | 60.3414 | 60.1812 | -60.8941 | 0.083464 | 0.055303 | -61.0036 | 60.2551 | 60.3734 | 60.4774 | -60.893 | -0.011502 | -0.11648 | 2.6007 | -0.021551 | -0.010049 | -0.28937 | -0.44962 | -0.010433 | -0.37571 | 60.966 | -0.12099 | -0.11056 | -0.25737 | -0.15344 | 121.3969 | 121.224 | 121.0637 | 60.884 | -121.5249 | 121.1377 | 121.256 | 121.3599 | 60.9379 | -121.5238
709.25 | 121.7651 | -60.7452 | 60.6308 | -0.013049 | -0.033292 | 0.00050001 | 0.054517 | -0.0061599 | 0.049683 | -0.0041205 | -0.0017945 | -0.0012306 | -0.0041597 | 0.01657 | -0.0086037 | -57.8835 | -0.012329 | -60.4417 | 60.9813 | 60.8039 | 60.6665 | -60.4362 | 0.055992 | 0.036989 | -60.5457 | 60.7313 | 60.845 | 60.9398 | -60.4351 | 0.30906 | 0.35052 | 2.8617 | 0.30353 | -0.005536 | 0.1731 | 0.035715 | 0.31012 | 0.10046 | 60.8012 | 0.19955 | -0.11057 | 0.21422 | 0.309 | 121.7266 | 121.5491 | 121.4118 | 60.7329 | -121.067 | 121.4765 | 121.5903 | 121.685 | 60.7822 | -121.0659
711 | 121.6827 | -6.7383 | 114.917 | -0.005418 | -0.033079 | 0.001141 | 0.054731 | -0.0048779 | 0.049256 | -0.019381 | -0.00029906 | -0.00058958 | -0.0035187 | 0.016357 | -0.0096721 | -11.2893 | 0.56915 | -11.7975 | 109.2421 | 109.0841 | 108.5129 | -11.3318 | 0.45434 | 0.55438 | -11.6084 | 109.0298 | 109.0485 | 109.5325 | -11.4372 | -4.5935 | -5.6749 | -4.551 | -5.0592 | -0.46569 | -5.8329 | -6.4041 | -4.6989 | -5.8872 | 7.1926 | -4.8702 | -0.17124 | -5.8684 | -5.3845 | 115.9804 | 115.8224 | 115.2512 | 7.3074 | -126.2488 | 115.7681 | 115.7868 | 116.2708 | 7.2927 | -126.3542
712.7656 | 121.6141 | -5.603 | 116.1209 | 0.002213 | -0.032865 | 0.00092741 | 0.054731 | -0.0048779 | 0.049256 | -0.019381 | 0.00012814 | -0.00058958 | -0.0037325 | 0.01657 | -0.0092447 | -5.58 | 0.24407 | -5.6534 | 115.9815 | 115.6594 | 115.4129 | -5.4982 | 0.19793 | 0.2705 | -5.6882 | 115.5954 | 115.8066 | 115.851 | -5.5488 | 0.10479 | -0.13942 | 0.02302 | -0.050402 | -0.15519 | -0.4615 | -0.70805 | 0.054189 | -0.52555 | 5.801 | -0.085137 | -0.13933 | -0.31435 | -0.26994 | 121.5845 | 121.2624 | 121.0159 | 5.8471 | -121.6192 | 121.1984 | 121.4096 | 121.454 | 5.8735 | -121.6697
714.4688 | 121.6553 | -5.0079 | 116.6702 | 0.009844 | -0.032651 | 0.00092741 | 0.054731 | -0.0050917 | 0.049042 | -0.011751 | -8.5458e-05 | -0.00080338 | -0.0035187 | 0.01657 | -0.0092447 | -4.9711 | 0.22118 | -5.0354 | 116.5996 | 116.2776 | 116.031 | -4.8892 | 0.19335 | 0.24761 | -5.0792 | 116.1997 | 116.4109 | 116.4599 | -4.9444 | 0.11869 | -0.070658 | 0.036853 | -0.027426 | -0.14612 | -0.39266 | -0.63925 | 0.063501 | -0.4705 | 5.2013 | -0.071261 | -0.13476 | -0.25929 | -0.2103 | 121.6075 | 121.2855 | 121.0389 | 5.2291 | -121.5595 | 121.2077 | 121.4189 | 121.4679 | 5.2555 | -121.6147
716.2344 | 121.7422 | -4.9438 | 116.6565 | -0.005418 | -0.032865 | 0.001141 | 0.054731 | -0.0048779 | 0.049256 | -0.027012 | -8.5458e-05 | -0.00058958 | -0.0037325 | 0.01657 | -0.0094585 | -4.8246 | 0.19371 | -4.8705 | 116.7507 | 116.4333 | 116.1866 | -4.7381 | 0.16588 | 0.22014 | -4.9189 | 116.3645 | 116.5758 | 116.611 | -4.7888 | 0.20571 | 0.094162 | 0.11928 | 0.073305 | -0.1324 | -0.22324 | -0.46985 | 0.15509 | -0.29194 | 5.1097 | 0.024907 | -0.13019 | -0.080725 | -0.045473 | 121.6945 | 121.3771 | 121.1305 | 5.1376 | -121.3946 | 121.3084 | 121.5196 | 121.5549 | 5.164 | -121.4452
717.9844 | 121.7422 | -5.2597 | 116.3406 | -0.013049 | -0.033079 | 0.001141 | 0.054731 | -0.0050917 | 0.049256 | -0.027012 | -0.00029906 | -0.00058958 | -0.0039461 | 0.016357 | -0.0092447 | -5.3236 | 0.18913 | -5.3925 | 116.2333 | 115.9158 | 115.6738 | -5.2968 | 0.17046 | 0.22014 | -5.4363 | 115.8563 | 116.063 | 116.0982 | -5.297 | -0.037063 | -0.10734 | -0.063913 | -0.13276 | -0.095699 | -0.4248 | -0.66679 | -0.037298 | -0.4843 | 5.4302 | -0.17663 | -0.13933 | -0.27767 | -0.24242 | 121.493 | 121.1755 | 120.9335 | 5.4488 | -121.6374 | 121.116 | 121.3227 | 121.3579 | 5.4798 | -121.6376
719.6719 | 121.6324 | -4.2618 | 117.4438 | -0.005418 | -0.032865 | 0.00071361 | 0.054517 | -0.0050917 | 0.04947 | -0.011751 | -0.00029906 | -0.001017 | -0.0035187 | 0.01657 | -0.0092447 | -4.1653 | 0.18455 | -4.2296 | 117.4008 | 117.0789 | 116.8368 | -4.152 | 0.1613 | 0.21556 | -4.2733 | 117.0055 | 117.2122 | 117.2612 | -4.1477 | 0.10974 | -0.043061 | 0.096495 | 0.032196 | -0.077547 | -0.36497 | -0.60704 | 0.11406 | -0.43831 | 4.4231 | -0.011563 | -0.12562 | -0.23165 | -0.18267 | 121.6626 | 121.3407 | 121.0986 | 4.4463 | -121.5959 | 121.2673 | 121.474 | 121.523 | 4.4773 | -121.5916
721.4375 | 121.6644 | -4.3854 | 117.2562 | -0.013049 | -0.033079 | 0.001141 | 0.054944 | -0.0048779 | 0.049256 | -0.0041205 | -0.00029906 | -0.00037598 | -0.0037325 | 0.01657 | -0.0094585 | -4.4034 | 0.17997 | -4.4722 | 117.1673 | 116.8454 | 116.5987 | -4.3718 | 0.15672 | 0.20182 | -4.5023 | 116.7766 | 116.9878 | 117.0277 | -4.3767 | 0.013551 | -0.088876 | -0.017986 | -0.086857 | -0.10041 | -0.41081 | -0.65744 | 0.008715 | -0.47955 | 4.5421 | -0.1169 | -0.12562 | -0.26832 | -0.22849 | 121.5527 | 121.2307 | 120.9841 | 4.5653 | -121.628 | 121.162 | 121.3732 | 121.413 | 4.5872 | -121.6328
723.1875 | 121.7422 | -4.0329 | 117.5491 | -0.005418 | -0.032865 | 0.00092741 | 0.054731 | -0.0048779 | 0.049042 | -0.019381 | -8.5458e-05 | -0.00058958 | -0.0035187 | 0.016357 | -0.0092447 | -3.9776 | 0.17081 | -4.0419 | 117.5885 | 117.2758 | 117.0245 | -3.9506 | 0.15215 | 0.20182 | -4.0719 | 117.1978 | 117.4137 | 117.4489 | -3.9554 | 0.082334 | 0.039368 | 0.055326 | -0.008977 | -0.091311 | -0.27336 | -0.5246 | 0.077489 | -0.3513 | 4.185 | -0.038982 | -0.11647 | -0.13548 | -0.10023 | 121.6214 | 121.3087 | 121.0574 | 4.2037 | -121.4997 | 121.2307 | 121.4466 | 121.4818 | 4.2347 | -121.5045
724.9375 | 121.6415 | -4.747 | 116.9128 | -0.005418 | -0.032865 | 0.00071361 | 0.054731 | -0.0050917 | 0.049683 | -0.0041205 | -8.5458e-05 | -0.00080338 | -0.0033051 | 0.016357 | -0.0088175 | -4.6185 | 0.16624 | -4.6783 | 116.9567 | 116.6347 | 116.3973 | -4.587 | 0.14757 | 0.18809 | -4.7129 | 116.566 | 116.7772 | 116.8171 | -4.5873 | 0.15997 | 0.043841 | 0.12846 | 0.068753 | -0.091221 | -0.27812 | -0.51558 | 0.15972 | -0.34684 | 4.8946 | 0.03411 | -0.12561 | -0.13561 | -0.095784 | 121.7037 | 121.3817 | 121.1443 | 4.9132 | -121.4999 | 121.313 | 121.5242 | 121.5641 | 4.9351 | -121.5001
726.6875 | 121.7102 | -4.6326 | 116.9769 | -0.005418 | -0.032865 | 0.00071361 | 0.054517 | -0.0048779 | 0.048829 | -0.019381 | 0.00012814 | -0.00080338 | -0.0035187 | 0.016784 | -0.0090311 | -4.4858 | 0.16166 | -4.5546 | 117.0803 | 116.7584 | 116.5163 | -4.468 | 0.13841 | 0.19267 | -4.5939 | 116.6805 | 116.9009 | 116.9453 | -4.4591 | 0.16458 | 0.10337 | 0.1468 | 0.077926 | -0.086659 | -0.21857 | -0.46062 | 0.17349 | -0.29646 | 4.771 | 0.038715 | -0.13477 | -0.076079 | -0.03167 | 121.7129 | 121.3909 | 121.1489 | 4.7942 | -121.4449 | 121.313 | 121.5334 | 121.5778 | 4.8252 | -121.436
728.375 | 121.6461 | -4.7287 | 116.9083 | -0.005418 | -0.032865 | 0.00050001 | 0.054517 | -0.0053053 | 0.049042 | -0.019381 | 0.00034194 | -0.001017 | -0.0035187 | 0.016357 | -0.0094585 | -4.5453 | 0.16624 | -4.6096 | 117.0208 | 116.708 | 116.4659 | -4.5138 | 0.14757 | 0.19267 | -4.6534 | 116.6301 | 116.8413 | 116.8812 | -4.5232 | 0.21493 | 0.11252 | 0.18341 | 0.11912 | -0.095809 | -0.20028 | -0.44232 | 0.20552 | -0.27816 | 4.8763 | 0.075323 | -0.13019 | -0.066936 | -0.027105 | 121.7495 | 121.4367 | 121.1946 | 4.8949 | -121.422 | 121.3588 | 121.57 | 121.6099 | 4.9214 | -121.4314
730.125 | 121.6461 | -4.2068 | 117.4438 | 0.002213 | -0.033292 | 0.00092741 | 0.054517 | -0.0050917 | 0.049256 | -0.011751 | -8.5458e-05 | -0.00037598 | -0.0037325 | 0.016143 | -0.0092447 | -4.2706 | 0.17081 | -4.3395 | 117.2863 | 116.969 | 116.7178 | -4.2482 | 0.14299 | 0.19267 | -4.3741 | 116.9002 | 117.1069 | 117.1513 | -4.2485 | -0.041346 | -0.15752 | -0.06374 | -0.13262 | -0.091269 | -0.47486 | -0.72608 | -0.041606 | -0.54361 | 4.3498 | -0.16723 | -0.12562 | -0.33696 | -0.29255 | 121.4932 | 121.1758 | 120.9246 | 4.3777 | -121.692 | 121.1071 | 121.3137 | 121.3581 | 4.3995 | -121.6923
731.8125 | 121.7194 | -4.4586 | 117.1051 | -0.013049 | -0.033292 | 0.00050001 | 0.054731 | -0.0048779 | 0.049256 | -0.011751 | 0.00012814 | -0.00080338 | -0.0039461 | 0.016357 | -0.0094585 | -4.472 | 0.17081 | -4.5318 | 117.1032 | 116.7812 | 116.5392 | -4.4405 | 0.13841 | 0.19724 | -4.571 | 116.7034 | 116.9192 | 116.9636 | -4.4408 | 0.018109 | -0.001911 | -0.013419 | -0.073133 | -0.091242 | -0.32385 | -0.5659 | 0.017854 | -0.40174 | 4.597 | -0.11234 | -0.1302 | -0.18594 | -0.14153 | 121.5618 | 121.2399 | 120.9978 | 4.6294 | -121.5456 | 121.162 | 121.3778 | 121.4222 | 4.6559 | -121.5459
733.5625 | 121.6965 | -4.5181 | 117.1143 | -0.005418 | -0.033079 | 0.00050001 | 0.054731 | -0.0055189 | 0.049256 | -0.034642 | -8.5458e-05 | -0.00080338 | -0.0035187 | 0.016357 | -0.0090311 | -4.4904 | 0.16166 | -4.5501 | 117.0803 | 116.7629 | 116.5255 | -4.4588 | 0.13383 | 0.18809 | -4.5939 | 116.6896 | 116.9054 | 116.9544 | -4.4545 | 0.059302 | -0.033958 | 0.027776 | -0.031937 | -0.091239 | -0.35132 | -0.5888 | 0.063627 | -0.42464 | 4.652 | -0.075726 | -0.13935 | -0.20883 | -0.15984 | 121.5984 | 121.2811 | 121.0436 | 4.6798 | -121.5731 | 121.2078 | 121.4236 | 121.4725 | 4.7062 | -121.5688
735.2969 | 121.6965 | -4.2252 | 117.3981 | -0.013049 | -0.033506 | 0.00071361 | 0.054303 | -0.0050917 | 0.049042 | -0.011751 | -8.5458e-05 | -0.00058958 | -0.0035187 | 0.016357 | -0.0094585 | -4.1928 | 0.16166 | -4.2571 | 117.3779 | 117.0697 | 116.8139 | -4.1566 | 0.13841 | 0.19267 | -4.2871 | 116.9964 | 117.1985 | 117.2383 | -4.1615 | 0.068543 | -0.020176 | 0.032403 | -0.031895 | -0.10044 | -0.32835 | -0.58416 | 0.063703 | -0.40169 | 4.3636 | -0.06192 | -0.12562 | -0.19961 | -0.15978 | 121.6031 | 121.2949 | 121.0391 | 4.3868 | -121.5547 | 121.2215 | 121.4236 | 121.4634 | 4.4178 | -121.5595
737.0469 | 121.8887 | -58.8135 | 62.4115 | 0.002213 | -0.033506 | 0.00050001 | 0.054303 | -0.0061599 | 0.049897 | -0.0041205 | -0.0011537 | -0.0012306 | -0.0037325 | 0.01657 | -0.0090311 | -59.0281 | -0.14969 | -58.9538 | 62.4647 | 62.2966 | 62.1362 | -58.9572 | -0.003531 | -0.082058 | -59.0622 | 62.2055 | 62.3102 | 62.4278 | -58.9378 | -0.14371 | 0.053212 | -0.21463 | -0.14029 | 0.003414 | -0.11487 | -0.27526 | -0.12437 | -0.20597 | 58.8099 | -0.24871 | -0.12434 | -0.10133 | 0.01634 | 121.2782 | 121.1101 | 120.9497 | 58.6638 | -121.3687 | 121.019 | 121.1236 | 121.2413 | 58.7314 | -121.3493
738.8125 | 121.7239 | -5.0812 | 116.5558 | -0.013049 | -0.033292 | 0.001782 | 0.054303 | -0.0053053 | 0.049042 | -0.011751 | -8.5458e-05 | -0.00058958 | -0.0037325 | 0.016357 | -0.0094585 | -5.0993 | 0.17539 | -5.1636 | 116.4714 | 116.1585 | 115.9211 | -5.0083 | 0.14299 | 0.2064 | -5.1982 | 116.0853 | 116.2965 | 116.3363 | -5.0589 | 0.072881 | -0.084412 | -0.0181 | -0.082376 | -0.15526 | -0.39727 | -0.6347 | 0.022273 | -0.47052 | 5.2242 | -0.11706 | -0.13934 | -0.25931 | -0.21948 | 121.5526 | 121.2397 | 121.0023 | 5.2566 | -121.5641 | 121.1664 | 121.3777 | 121.4175 | 5.2876 | -121.6147
740.5 | 121.7148 | -59.2804 | 62.1231 | 0.002213 | -0.033933 | 0.00050001 | 0.054303 | -0.0057325 | 0.049683 | 0.00351 | -0.0013673 | -0.0012306 | -0.0037325 | 0.01657 | -0.0090311 | -59.399 | -0.11764 | -59.3109 | 62.0939 | 61.9166 | 61.7654 | -59.3281 | 0.001048 | -0.059164 | -59.4331 | 61.8347 | 61.9439 | 62.0616 | -59.3042 | -0.047682 | -0.029246 | -0.11856 | -0.030481 | 0.017201 | -0.20653 | -0.35773 | -0.023756 | -0.28843 | 59.2814 | -0.15266 | -0.12891 | -0.17922 | -0.061557 | 121.3743 | 121.197 | 121.0458 | 59.1628 | -121.4512 | 121.1151 | 121.2243 | 121.3419 | 59.2212 | -121.4273
742.25 | 121.7972 | -58.4518 | 62.9059 | 0.002213 | -0.03372 | 0.00050001 | 0.054517 | -0.0057325 | 0.049683 | -0.011751 | -0.0017945 | -0.001017 | -0.0041597 | 0.01657 | -0.0086037 | -55.9194 | -0.053537 | -58.5051 | 62.8997 | 62.7225 | 62.5712 | -58.513 | 0.037677 | 0.009516 | -58.6272 | 62.6359 | 62.7543 | 62.8674 | -58.5029 | -0.061186 | -0.006226 | 2.5325 | -0.053257 | 0.007929 | -0.18342 | -0.33467 | -0.051016 | -0.26998 | 58.4895 | -0.17537 | -0.12435 | -0.15159 | -0.038499 | 121.3515 | 121.1743 | 121.0231 | 58.3983 | -121.4189 | 121.0878 | 121.2061 | 121.3192 | 58.4614 | -121.4087
744 | 121.8063 | -57.8796 | 63.5284 | 0.009844 | -0.033933 | 0.00071361 | 0.054303 | -0.0061599 | 0.050111 | -0.0041205 | -0.0011537 | -0.0012306 | -0.0039461 | 0.01657 | -0.0088175 | -55.4615 | -0.035222 | -57.9969 | 63.4124 | 63.2399 | 63.084 | -58.0048 | 0.037677 | 0.023253 | -58.1281 | 63.1487 | 63.2579 | 63.3802 | -57.99 | -0.12513 | -0.11601 | 2.4181 | -0.11727 | 0.007857 | -0.28856 | -0.44443 | -0.11039 | -0.37974 | 57.9173 | -0.24849 | -0.1381 | -0.2705 | -0.14825 | 121.2921 | 121.1195 | 120.9637 | 57.8444 | -121.5332 | 121.0283 | 121.1376 | 121.2598 | 57.9029 | -121.5185
745.6875 | 121.8292 | -57.399 | 64.0228 | -0.013049 | -0.033933 | 0.00028641 | 0.054303 | -0.0061599 | 0.049256 | -0.0041205 | -0.0017945 | -0.0012306 | -0.0037325 | 0.01657 | -0.0090311 | -54.99 | -0.016908 | -57.5253 | 63.884 | 63.7253 | 63.5602 | -57.5148 | 0.051413 | 0.041567 | -57.6474 | 63.6294 | 63.7433 | 63.8655 | -57.5047 | -0.11584 | -0.13882 | 2.409 | -0.12636 | -0.010524 | -0.29758 | -0.46264 | -0.10569 | -0.39338 | 57.4504 | -0.24838 | -0.14269 | -0.27955 | -0.15731 | 121.283 | 121.1242 | 120.9592 | 57.3821 | -121.5377 | 121.0284 | 121.1423 | 121.2645 | 57.4406 | -121.5275
747.4219 | 121.1014 | -7.0496 | 114.7018 | -0.005418 | -0.033506 | 0.00071361 | 0.054303 | -0.0059463 | 0.049042 | -0.0041205 | -0.00094006 | -0.001017 | -0.0037325 | 0.01657 | -0.0090311 | -21.4624 | 0.77061 | -22.3275 | 99.2109 | 99.07 | 98.6826 | -21.8404 | 0.70159 | 0.77416 | -22.1944 | 99.099 | 99.1817 | 99.4092 | -21.8952 | -14.7909 | -15.491 | -14.4129 | -15.278 | -0.4871 | -15.6319 | -16.0192 | -14.8457 | -15.6028 | 7.7512 | -15.1449 | -0.2992 | -15.5202 | -15.2926 | 106.2604 | 106.1195 | 105.7322 | 7.8202 | -136.5423 | 106.1486 | 106.2312 | 106.4588 | 7.8237 | -136.5971
749.1719 | 121.6232 | -5.3833 | 116.3498 | -0.005418 | -0.03372 | 0.0013548 | 0.054731 | -0.0057325 | 0.049042 | -0.0041205 | -0.00051266 | -0.00080338 | -0.0033051 | 0.016784 | -0.0094585 | -3.886 | 0.2166 | -5.3742 | 116.2653 | 115.9616 | 115.7105 | -5.2143 | 0.17046 | 0.24303 | -5.4089 | 115.8747 | 116.0813 | 116.1257 | -5.2695 | 0.16895 | -0.084445 | 1.4973 | 0.009147 | -0.15981 | -0.38817 | -0.63932 | 0.11377 | -0.47514 | 5.5538 | -0.025562 | -0.13933 | -0.26851 | -0.2241 | 121.6486 | 121.3449 | 121.0938 | 5.5999 | -121.5641 | 121.258 | 121.4646 | 121.509 | 5.6263 | -121.6193
750.9219 | 121.7239 | -5.127 | 116.5009 | 0.002213 | -0.033292 | 0.001782 | 0.054517 | -0.0057325 | 0.048829 | -0.019381 | -0.0011537 | -0.00058958 | -0.0035187 | 0.016357 | -0.0092447 | -3.7853 | 0.20286 | -5.2505 | 116.389 | 116.0715 | 115.8341 | -5.0999 | 0.1613 | 0.22929 | -5.2852 | 115.9937 | 116.2049 | 116.2539 | -5.1505 | 0.027079 | -0.11189 | 1.3417 | -0.12359 | -0.15067 | -0.42934 | -0.66676 | -0.023528 | -0.50716 | 5.2883 | -0.15828 | -0.13476 | -0.29595 | -0.24696 | 121.5159 | 121.1985 | 120.961 | 5.3298 | -121.6007 | 121.1206 | 121.3319 | 121.3808 | 5.3562 | -121.6513
752.625 | 121.6324 | -4.9484 | 116.7709 | -0.013049 | -0.033292 | 0.0015684 | 0.054944 | -0.0059463 | 0.049042 | -0.011751 | -0.00094006 | -0.00058958 | -0.0035187 | 0.01657 | -0.0094585 | -3.5655 | 0.17997 | -4.9713 | 116.6774 | 116.36 | 116.1134 | -4.8206 | 0.15672 | 0.21556 | -5.0014 | 116.2776 | 116.4934 | 116.5332 | -4.862 | 0.12786 | -0.093533 | 1.3829 | -0.02284 | -0.1507 | -0.41095 | -0.65755 | 0.08641 | -0.49338 | 5.1051 | -0.052933 | -0.13934 | -0.27758 | -0.23775 | 121.6258 | 121.3084 | 121.0618 | 5.1284 | -121.5915 | 121.226 | 121.4418 | 121.4816 | 5.164 | -121.6329
754.3594 | 121.6278 | -4.9393 | 116.7389 | -0.005418 | -0.033292 | 0.0015684 | 0.054731 | -0.0059463 | 0.049042 | -0.011751 | -0.00094006 | -0.00058958 | -0.0033051 | 0.01657 | -0.0090311 | -3.5701 | 0.16624 | -4.985 | 116.6499 | 116.3417 | 116.0997 | -4.8343 | 0.14757 | 0.2064 | -5.0243 | 116.2684 | 116.4796 | 116.5149 | -4.8895 | 0.10497 | -0.088961 | 1.3692 | -0.04573 | -0.1507 | -0.39722 | -0.63924 | 0.049782 | -0.47049 | 5.0868 | -0.084981 | -0.13476 | -0.25927 | -0.22402 | 121.5892 | 121.2809 | 121.0389 | 5.1055 | -121.5732 | 121.2077 | 121.4189 | 121.4541 | 5.1457 | -121.6284
756.0938 | 121.7514 | -4.6097 | 116.9678 | -0.02068 | -0.033079 | 0.0015684 | 0.054517 | -0.0059463 | 0.049042 | -0.011751 | -0.00094006 | -0.00058958 | -0.0037325 | 0.01657 | -0.0094585 | -3.5518 | 0.17997 | -4.9392 | 116.6911 | 116.3829 | 116.1409 | -4.7793 | 0.1613 | 0.2064 | -4.9739 | 116.3096 | 116.5208 | 116.5607 | -4.8345 | -0.16967 | -0.27664 | 1.0579 | -0.32954 | -0.15987 | -0.58489 | -0.82691 | -0.22486 | -0.65816 | 4.771 | -0.36421 | -0.13934 | -0.44695 | -0.40712 | 121.3008 | 120.9926 | 120.7505 | 4.7897 | -121.7471 | 120.9193 | 121.1305 | 121.1703 | 4.8161 | -121.8023
757.7812 | 121.6965 | -4.8248 | 116.8121 | -0.005418 | -0.03372 | 0.001782 | 0.054731 | -0.0063735 | 0.049256 | -0.019381 | -0.0011537 | -0.00080338 | -0.0033051 | 0.016998 | -0.0094585 | -3.419 | 0.16166 | -4.7698 | 116.8743 | 116.5569 | 116.3103 | -4.6237 | 0.14757 | 0.19724 | -4.7999 | 116.479 | 116.6902 | 116.7301 | -4.6697 | 0.20116 | 0.062138 | 1.4058 | 0.055008 | -0.14616 | -0.25525 | -0.50186 | 0.15512 | -0.33312 | 4.9724 | 0.024934 | -0.13019 | -0.1219 | -0.082069 | 121.6991 | 121.3817 | 121.1351 | 4.9865 | -121.4358 | 121.3038 | 121.5151 | 121.5549 | 5.0221 | -121.4818
759.5312 | 121.7697 | -4.8294 | 116.7526 | -0.005418 | -0.033506 | 0.0019958 | 0.054731 | -0.0059463 | 0.048829 | -0.019381 | -0.0013673 | -0.00080338 | -0.0035187 | 0.016357 | -0.0096721 | -3.5564 | 0.15708 | -4.9392 | 116.6957 | 116.3875 | 116.1363 | -4.7885 | 0.15215 | 0.19267 | -4.9785 | 116.3142 | 116.5254 | 116.5515 | -4.8391 | 0.0409 | -0.05691 | 1.273 | -0.10981 | -0.15071 | -0.36516 | -0.61634 | -0.009714 | -0.43844 | 4.9816 | -0.14906 | -0.13934 | -0.22722 | -0.20113 | 121.5251 | 121.2169 | 120.9657 | 4.9865 | -121.5411 | 121.1436 | 121.3548 | 121.3809 | 5.0221 | -121.5917
761.2188 | 121.637 | -5.8182 | 115.8417 | 0.002213 | -0.033933 | 0.00092741 | 0.054944 | -0.0057325 | 0.049256 | -0.019381 | -0.0011537 | -0.00080338 | -0.0037325 | 0.01657 | -0.0098857 | -4.2156 | 0.17539 | -5.8274 | 115.8121 | 115.5129 | 115.2618 | -5.6631 | 0.14757 | 0.21556 | -5.8667 | 115.426 | 115.6372 | 115.677 | -5.7183 | 0.15509 | -0.029589 | 1.6025 | -0.009228 | -0.16432 | -0.32879 | -0.57991 | 0.099922 | -0.41572 | 5.9657 | -0.048558 | -0.14848 | -0.20452 | -0.16469 | 121.6303 | 121.3311 | 121.0799 | 5.9936 | -121.5048 | 121.2441 | 121.4553 | 121.4952 | 6.0337 | -121.5599
762.9844 | 121.5912 | -5.3055 | 116.3956 | 0.009844 | -0.033506 | 0.00092741 | 0.054731 | -0.0057325 | 0.049256 | -0.0041205 | -0.0011537 | -0.001017 | -0.0035187 | 0.016784 | -0.0092447 | -3.8402 | 0.14792 | -5.3421 | 116.2928 | 115.9845 | 115.7288 | -5.1869 | 0.14299 | 0.19724 | -5.3768 | 115.9021 | 116.1271 | 116.1577 | -5.2466 | 0.11861 | -0.10275 | 1.4653 | -0.036625 | -0.15523 | -0.41105 | -0.66678 | 0.058845 | -0.49345 | 5.4485 | -0.071331 | -0.13018 | -0.2685 | -0.23783 | 121.5983 | 121.29 | 121.0343 | 5.4534 | -121.5824 | 121.2076 | 121.4325 | 121.4632 | 5.5027 | -121.6422
764.6719 | 121.6095 | -5.0079 | 116.7114 | 0.002213 | -0.03372 | 0.001141 | 0.054731 | -0.0061599 | 0.049042 | -0.0041205 | -0.00072626 | -0.001017 | -0.0035187 | 0.01657 | -0.0092447 | -3.6617 | 0.14334 | -5.0766 | 116.5675 | 116.2409 | 116.0035 | -4.9167 | 0.13841 | 0.20182 | -5.1158 | 116.1768 | 116.3835 | 116.4233 | -4.9765 | 0.091218 | -0.14391 | 1.3463 | -0.068631 | -0.15985 | -0.47049 | -0.70792 | 0.031449 | -0.53459 | 5.1463 | -0.10789 | -0.13934 | -0.32796 | -0.28813 | 121.5755 | 121.2489 | 121.0114 | 5.1513 | -121.6281 | 121.1848 | 121.3914 | 121.4312 | 5.2098 | -121.6879
766.4219 | 121.7194 | -8.6792 | 112.9349 | -0.013049 | -0.033506 | 0.00071361 | 0.054517 | -0.0061599 | 0.049256 | -0.0041205 | -0.00094006 | -0.00080338 | -0.0033051 | 0.016784 | -0.0094585 | -8.1256 | 0.10671 | -8.8262 | 112.8819 | 112.5732 | 112.3681 | -8.6898 | 0.12467 | 0.16977 | -8.8933 | 112.4637 | 112.6885 | 112.7375 | -8.6853 | -0.010552 | -0.052957 | 0.55361 | -0.14698 | -0.13643 | -0.36166 | -0.56678 | -0.006129 | -0.4712 | 8.8039 | -0.21406 | -0.20793 | -0.24634 | -0.19735 | 121.5611 | 121.2524 | 121.0473 | 8.7859 | -121.6246 | 121.1429 | 121.3677 | 121.4167 | 8.849 | -121.6202
768.1719 | 121.669 | -6.9305 | 114.7339 | -0.005418 | -0.033506 | 0.00071361 | 0.054731 | -0.0063735 | 0.049042 | -0.019381 | -0.00094006 | -0.00080338 | -0.0037325 | 0.01657 | -0.0092447 | -5.1405 | 0.13876 | -7.0406 | 114.6583 | 114.359 | 114.1217 | -6.904 | 0.14299 | 0.17893 | -7.0755 | 114.2356 | 114.4376 | 114.5461 | -6.8996 | 0.026571 | -0.075554 | 1.7901 | -0.11011 | -0.13668 | -0.37489 | -0.61219 | 0.030953 | -0.49834 | 7.0735 | -0.14497 | -0.17592 | -0.29632 | -0.18782 | 121.5889 | 121.2895 | 121.0522 | 7.0693 | -121.6379 | 121.1661 | 121.3681 | 121.4766 | 7.1095 | -121.6335
769.9219 | 121.669 | -6.6742 | 114.9673 | -0.005418 | -0.033506 | 0.00092741 | 0.054517 | -0.0057325 | 0.049256 | -0.011751 | -0.00094006 | -0.001017 | -0.0037325 | 0.016784 | -0.0094585 | -4.852 | 0.13876 | -6.6744 | 115.0292 | 114.7299 | 114.4788 | -6.5377 | 0.13383 | 0.19724 | -6.7092 | 114.5973 | 114.8084 | 114.9078 | -6.5424 | 0.13654 | 0.061836 | 1.8221 | -0.000192 | -0.13673 | -0.23745 | -0.48852 | 0.13175 | -0.3701 | 6.808 | -0.035023 | -0.16678 | -0.15892 | -0.059565 | 121.7034 | 121.4041 | 121.153 | 6.813 | -121.505 | 121.2714 | 121.4826 | 121.582 | 6.8714 | -121.5098
771.625 | 121.701 | -6.4682 | 115.1276 | -0.005418 | -0.03372 | 0.00050001 | 0.054731 | -0.0059463 | 0.049256 | -0.011751 | -0.00094006 | -0.00080338 | -0.0037325 | 0.016784 | -0.0098857 | -4.7696 | 0.13876 | -6.5096 | 115.1894 | 114.881 | 114.6437 | -6.382 | 0.13383 | 0.18351 | -6.5444 | 114.7621 | 114.9687 | 115.0726 | -6.3822 | 0.086228 | 0.061863 | 1.6986 | -0.041367 | -0.12759 | -0.24657 | -0.4839 | 0.086018 | -0.36549 | 6.602 | -0.076182 | -0.1622 | -0.15888 | -0.054952 | 121.6576 | 121.3492 | 121.1119 | 6.607 | -121.5095 | 121.2303 | 121.4369 | 121.5408 | 6.6517 | -121.5097
773.3906 | 121.7514 | -6.1707 | 115.3839 | -0.013049 | -0.03372 | 0.00071361 | 0.054731 | -0.0063735 | 0.049042 | -0.019381 | -0.00094006 | -0.001017 | -0.0035187 | 0.016357 | -0.0098857 | -4.6094 | 0.14792 | -6.3264 | 115.3634 | 115.0642 | 114.8222 | -6.2034 | 0.14757 | 0.18809 | -6.3658 | 114.9406 | 115.1518 | 115.242 | -6.2128 | -0.032741 | -0.020507 | 1.5613 | -0.15578 | -0.12304 | -0.31976 | -0.56169 | -0.042112 | -0.44327 | 6.3182 | -0.19516 | -0.15305 | -0.23209 | -0.14189 | 121.5341 | 121.2348 | 120.9929 | 6.3186 | -121.5873 | 121.1113 | 121.3225 | 121.4127 | 6.3587 | -121.5967
775.1406 | 121.7514 | -5.777 | 115.8005 | 0.002213 | -0.03372 | 0.00092741 | 0.05409 | -0.0061599 | 0.049042 | -0.0041205 | -0.00072626 | -0.001017 | -0.0035187 | 0.01657 | -0.0094585 | -4.3896 | 0.14792 | -5.9831 | 115.7022 | 115.403 | 115.161 | -5.86 | 0.13841 | 0.19267 | -6.0178 | 115.284 | 115.4906 | 115.5808 | -5.8602 | -0.082998 | -0.098271 | 1.3874 | -0.20609 | -0.12309 | -0.39748 | -0.63944 | -0.083219 | -0.51645 | 5.9154 | -0.24085 | -0.15763 | -0.30984 | -0.21964 | 121.4792 | 121.18 | 120.938 | 5.9249 | -121.6605 | 121.061 | 121.2676 | 121.3578 | 5.9696 | -121.6607
776.8438 | 121.7194 | -6.0425 | 115.5441 | -0.005418 | -0.033506 | 0.00071361 | 0.054944 | -0.0061599 | 0.049042 | -0.019381 | -0.00094006 | -0.00058958 | -0.0035187 | 0.016784 | -0.0094585 | -4.472 | 0.13876 | -6.1387 | 115.5603 | 115.261 | 115.0099 | -6.0065 | 0.13383 | 0.19267 | -6.1735 | 115.1238 | 115.335 | 115.4481 | -6.0113 | 0.035979 | 0.016147 | 1.5704 | -0.096247 | -0.13223 | -0.28308 | -0.53418 | 0.031182 | -0.42035 | 6.1763 | -0.13103 | -0.16221 | -0.20916 | -0.096072 | 121.6028 | 121.3035 | 121.0524 | 6.1812 | -121.5506 | 121.1663 | 121.3774 | 121.4905 | 6.2351 | -121.5554
778.5938 | 121.6599 | -5.9921 | 115.6677 | 0.002213 | -0.03372 | 0.00092741 | 0.054731 | -0.0059463 | 0.048829 | 0.00351 | -0.0011537 | -0.00080338 | -0.0035187 | 0.01657 | -0.0094585 | -4.4125 | 0.13419 | -6.0563 | 115.6335 | 115.3389 | 115.0924 | -5.9287 | 0.12467 | 0.18351 | -6.0957 | 115.2153 | 115.4174 | 115.5122 | -5.938 | 0.063466 | -0.034196 | 1.5796 | -0.064192 | -0.12766 | -0.32884 | -0.57536 | 0.054089 | -0.45238 | 6.1168 | -0.10354 | -0.15763 | -0.25034 | -0.15557 | 121.6257 | 121.331 | 121.0845 | 6.1263 | -121.5964 | 121.2075 | 121.4095 | 121.5043 | 6.1756 | -121.6058
780.3594 | 121.7697 | -5.7632 | 115.8096 | -0.02068 | -0.03372 | 0.00092741 | 0.054944 | -0.0059463 | 0.048829 | -0.011751 | -0.0011537 | -0.00080338 | -0.0039461 | 0.016998 | -0.0096721 | -4.2019 | 0.13419 | -5.8045 | 115.8853 | 115.5907 | 115.3533 | -5.686 | 0.13383 | 0.18351 | -5.8393 | 115.458 | 115.6692 | 115.7686 | -5.6862 | 0.077268 | 0.07571 | 1.5613 | -0.041268 | -0.11854 | -0.2189 | -0.45629 | 0.077043 | -0.35162 | 5.8971 | -0.076017 | -0.15306 | -0.14042 | -0.041073 | 121.6486 | 121.354 | 121.1166 | 5.8974 | -121.4956 | 121.2213 | 121.4325 | 121.5318 | 5.9468 | -121.4958
782.0469 | 121.6919 | -5.8273 | 115.7776 | 0.002213 | -0.033506 | 0.00071361 | 0.054731 | -0.0057325 | 0.049256 | -0.019381 | -0.0011537 | -0.00080338 | -0.0039461 | 0.016784 | -0.0090311 | -4.2156 | 0.12961 | -5.8366 | 115.8487 | 115.5495 | 115.3076 | -5.7318 | 0.12467 | 0.18351 | -5.8759 | 115.4214 | 115.628 | 115.7228 | -5.7228 | 0.095566 | 0.071125 | 1.6117 | -0.009229 | -0.10479 | -0.22807 | -0.47003 | 0.1045 | -0.35621 | 5.952 | -0.048559 | -0.15306 | -0.14959 | -0.054816 | 121.676 | 121.3769 | 121.1349 | 5.9569 | -121.5094 | 121.2487 | 121.4553 | 121.5501 | 6.0108 | -121.5004
783.7969 | 121.7285 | -6.015 | 115.5762 | -0.013049 | -0.033506 | 0.00071361 | 0.054731 | -0.0057325 | 0.049042 | -0.011751 | -0.0011537 | -0.00058958 | -0.0037325 | 0.01657 | -0.0096721 | -4.4308 | 0.14334 | -6.0701 | 115.6106 | 115.3252 | 115.0832 | -5.947 | 0.13383 | 0.18809 | -6.1094 | 115.1925 | 115.4128 | 115.4984 | -5.9472 | 0.06804 | 0.034465 | 1.5842 | -0.055038 | -0.12308 | -0.25102 | -0.49297 | 0.06782 | -0.38372 | 6.1488 | -0.094391 | -0.16221 | -0.16337 | -0.077751 | 121.6257 | 121.3402 | 121.0982 | 6.1584 | -121.5231 | 121.2075 | 121.4278 | 121.5134 | 6.2031 | -121.5234
785.4844 | 121.637 | -5.7037 | 115.9515 | 0.002213 | -0.03372 | 0.00092741 | 0.054731 | -0.0057325 | 0.049042 | -0.011751 | -0.0011537 | -0.001017 | -0.0030915 | 0.016998 | -0.0094585 | -4.1973 | 0.14792 | -5.8182 | 115.8716 | 115.5678 | 115.3304 | -5.7043 | 0.12925 | 0.18809 | -5.853 | 115.4443 | 115.6509 | 115.7411 | -5.6954 | -0.000557 | -0.079933 | 1.5064 | -0.11451 | -0.11396 | -0.3837 | -0.62109 | 0.008375 | -0.50727 | 5.833 | -0.14926 | -0.15764 | -0.30065 | -0.21045 | 121.5753 | 121.2716 | 121.0342 | 5.8517 | -121.6558 | 121.148 | 121.3546 | 121.4448 | 5.8918 | -121.6469
787.2344 | 121.7331 | -5.6854 | 115.9332 | -0.005418 | -0.03372 | 0.00050001 | 0.054517 | -0.0059463 | 0.048829 | -0.011751 | -0.00094006 | -0.00080338 | -0.0035187 | 0.016784 | -0.0094585 | -4.179 | 0.14792 | -5.7404 | 115.9449 | 115.6548 | 115.4129 | -5.6219 | 0.13383 | 0.17893 | -5.7797 | 115.5221 | 115.7333 | 115.8372 | -5.6267 | 0.063553 | 0.011632 | 1.5064 | -0.054992 | -0.11855 | -0.27839 | -0.52036 | 0.058747 | -0.41112 | 5.8193 | -0.094313 | -0.15306 | -0.19992 | -0.095991 | 121.6303 | 121.3403 | 121.0983 | 5.8333 | -121.5551 | 121.2075 | 121.4187 | 121.5227 | 5.8644 | -121.5599
789 | 121.6461 | -5.658 | 116.0477 | -0.005418 | -0.033933 | 0.00092741 | 0.054303 | -0.0057325 | 0.048401 | -0.011751 | -0.00094006 | -0.00080338 | -0.0035187 | 0.01657 | -0.0096721 | -4.1103 | 0.14334 | -5.6809 | 116.0135 | 115.7052 | 115.4678 | -5.5715 | 0.13383 | 0.18351 | -5.7156 | 115.577 | 115.7883 | 115.8922 | -5.5672 | 0.086455 | -0.034133 | 1.5476 | -0.02294 | -0.1094 | -0.34247 | -0.57986 | 0.090806 | -0.47062 | 5.7918 | -0.057677 | -0.14848 | -0.25942 | -0.15549 | 121.6715 | 121.3632 | 121.1258 | 5.8013 | -121.6192 | 121.235 | 121.4462 | 121.5501 | 5.8415 | -121.6148
790.75 | 121.8018 | -5.4611 | 116.1163 | -0.005418 | -0.03372 | 0.00092741 | 0.054303 | -0.0059463 | 0.049042 | -0.011751 | -0.00072626 | -0.00080338 | -0.0039461 | 0.016784 | -0.0098857 | -4.0234 | 0.14334 | -5.5207 | 116.1738 | 115.8746 | 115.6372 | -5.4021 | 0.12925 | 0.19267 | -5.5508 | 115.7419 | 115.9485 | 116.0524 | -5.3977 | 0.059038 | 0.057446 | 1.4378 | -0.059538 | -0.11858 | -0.24171 | -0.47912 | 0.063384 | -0.37446 | 5.5904 | -0.089682 | -0.15307 | -0.16783 | -0.063902 | 121.6349 | 121.3357 | 121.0983 | 5.6045 | -121.5184 | 121.203 | 121.4096 | 121.5136 | 5.6538 | -121.5141
792.5 | 121.6782 | -5.7953 | 115.8188 | -0.005418 | -0.03372 | 0.00071361 | 0.054303 | -0.0063735 | 0.048615 | 0.00351 | -0.0011537 | -0.001017 | -0.0035187 | 0.016784 | -0.0096721 | -4.2385 | 0.13419 | -5.864 | 115.8304 | 115.5266 | 115.2938 | -5.7455 | 0.12467 | 0.17893 | -5.9079 | 115.3985 | 115.6051 | 115.7045 | -5.7457 | 0.049785 | 0.011613 | 1.5567 | -0.068742 | -0.11853 | -0.29216 | -0.52497 | 0.049561 | -0.4203 | 5.92 | -0.11265 | -0.16222 | -0.21368 | -0.11433 | 121.6257 | 121.3219 | 121.0891 | 5.9295 | -121.5643 | 121.1938 | 121.4004 | 121.4997 | 5.9742 | -121.5645
794.2031 | 121.7834 | -5.6396 | 115.9195 | -0.005418 | -0.03372 | 0.00050001 | 0.054517 | -0.0059463 | 0.048829 | -0.019381 | -0.00072626 | -0.00058958 | -0.0035187 | 0.01657 | -0.0096721 | -4.1744 | 0.1525 | -5.7725 | 115.922 | 115.6228 | 115.39 | -5.6448 | 0.12925 | 0.19267 | -5.8118 | 115.4901 | 115.7013 | 115.7915 | -5.645 | -0.005118 | 0.002473 | 1.4652 | -0.13282 | -0.1277 | -0.29671 | -0.52952 | -0.005345 | -0.42944 | 5.7689 | -0.17214 | -0.1668 | -0.21824 | -0.12804 | 121.5616 | 121.2624 | 121.0296 | 5.7921 | -121.5643 | 121.1297 | 121.3409 | 121.4311 | 5.8323 | -121.5645
795.9531 | 121.7285 | -5.7678 | 115.8325 | -0.005418 | -0.034147 | 0.00092741 | 0.054517 | -0.0061599 | 0.049042 | -0.0041205 | -0.00094006 | -0.001017 | -0.0037325 | 0.016784 | -0.0094585 | -4.2385 | 0.14334 | -5.8182 | 115.867 | 115.5678 | 115.3304 | -5.7089 | 0.12925 | 0.17893 | -5.8622 | 115.4397 | 115.6463 | 115.7457 | -5.7045 | 0.058951 | 0.034507 | 1.5293 | -0.050425 | -0.10938 | -0.26469 | -0.50207 | 0.063304 | -0.39283 | 5.8971 | -0.094333 | -0.15764 | -0.18621 | -0.086855 | 121.6348 | 121.3357 | 121.0983 | 5.9112 | -121.5414 | 121.2075 | 121.4141 | 121.5135 | 5.9468 | -121.537
797.6406 | 121.7743 | -5.6808 | 115.8875 | -0.013049 | -0.034361 | 0.00050001 | 0.054303 | -0.0063735 | 0.048829 | -0.0041205 | -0.00072626 | -0.00080338 | -0.0033051 | 0.016784 | -0.0094585 | -4.1424 | 0.14334 | -5.7313 | 115.9494 | 115.6548 | 115.4174 | -5.6081 | 0.13383 | 0.18809 | -5.7752 | 115.5175 | 115.7241 | 115.8327 | -5.6221 | 0.072712 | 0.061987 | 1.5385 | -0.050413 | -0.12312 | -0.23262 | -0.47001 | 0.058748 | -0.36992 | 5.8147 | -0.094313 | -0.15306 | -0.1633 | -0.054792 | 121.6303 | 121.3357 | 121.0983 | 5.8242 | -121.4956 | 121.1984 | 121.405 | 121.5135 | 5.8689 | -121.5096
799.4062 | 121.6324 | -5.6213 | 116.0248 | -0.005418 | -0.033506 | 0.00071361 | 0.054303 | -0.0059463 | 0.048615 | -0.027012 | -0.00072626 | -0.00058958 | -0.0037325 | 0.016784 | -0.0092447 | -4.0188 | 0.15708 | -5.5802 | 116.1097 | 115.8151 | 115.5777 | -5.4616 | 0.12925 | 0.17893 | -5.6149 | 115.6824 | 115.8798 | 115.9929 | -5.4664 | 0.15973 | 0.084902 | 1.6026 | 0.041161 | -0.11857 | -0.20968 | -0.44709 | 0.15492 | -0.34243 | 5.7506 | 0.006433 | -0.14849 | -0.14496 | -0.03187 | 121.731 | 121.4364 | 121.199 | 5.7784 | -121.4864 | 121.3037 | 121.5012 | 121.6142 | 5.8003 | -121.4912
801.0938 | 121.7743 | -5.5206 | 116.0843 | -0.013049 | -0.03372 | 0.001141 | 0.054517 | -0.0061599 | 0.048829 | -0.011751 | -0.00072626 | -0.001017 | -0.0037325 | 0.016784 | -0.0094585 | -4.0691 | 0.1525 | -5.5756 | 116.1097 | 115.8197 | 115.5777 | -5.4616 | 0.12925 | 0.18351 | -5.6057 | 115.6778 | 115.889 | 115.9929 | -5.4573 | 0.059021 | 0.025392 | 1.4515 | -0.054969 | -0.11399 | -0.26461 | -0.5066 | 0.063369 | -0.40651 | 5.6499 | -0.085117 | -0.14849 | -0.19531 | -0.09138 | 121.6303 | 121.3403 | 121.0983 | 5.6731 | -121.5459 | 121.1984 | 121.4096 | 121.5135 | 5.7041 | -121.5416
802.8438 | 121.637 | -5.159 | 116.5237 | -0.005418 | -0.033933 | 0.001141 | 0.054517 | -0.0061599 | 0.049256 | -0.0041205 | -0.0011537 | -0.00058958 | -0.0033051 | 0.016784 | -0.0092447 | -3.767 | 0.16166 | -5.2551 | 116.4347 | 116.1356 | 115.8982 | -5.1365 | 0.13383 | 0.18809 | -5.2852 | 116.0028 | 116.2095 | 116.318 | -5.1322 | 0.022491 | -0.088996 | 1.392 | -0.096122 | -0.11861 | -0.38812 | -0.62555 | 0.026832 | -0.52089 | 5.2928 | -0.12624 | -0.15307 | -0.31426 | -0.20575 | 121.5937 | 121.2946 | 121.0572 | 5.3207 | -121.6602 | 121.1618 | 121.3685 | 121.477 | 5.3471 | -121.6559
804.5938 | 121.788 | -5.2597 | 116.3315 | -0.005418 | -0.033933 | 0.00092741 | 0.054303 | -0.0063735 | 0.049042 | -0.019381 | -0.00094006 | -0.001017 | -0.0039461 | 0.016784 | -0.0096721 | -3.7944 | 0.16166 | -5.2551 | 116.4302 | 116.1265 | 115.9028 | -5.1411 | 0.12925 | 0.18351 | -5.2898 | 115.9983 | 116.2049 | 116.3088 | -5.1367 | 0.11862 | 0.098687 | 1.4653 | 0.004586 | -0.11403 | -0.20502 | -0.42871 | 0.12296 | -0.33321 | 5.389 | -0.030111 | -0.15307 | -0.12658 | -0.022649 | 121.6899 | 121.3862 | 121.1625 | 5.4214 | -121.4726 | 121.258 | 121.4646 | 121.5685 | 5.4432 | -121.4682
806.3438 | 121.6873 | -5.2872 | 116.3864 | 0.002213 | -0.033933 | 0.00092741 | 0.054517 | -0.0063735 | 0.049042 | 0.00351 | -0.00094006 | -0.00058958 | -0.0035187 | 0.016998 | -0.0094585 | -3.8082 | 0.16624 | -5.2872 | 116.389 | 116.0898 | 115.8524 | -5.1915 | 0.12925 | 0.18351 | -5.3264 | 115.9616 | 116.1637 | 116.2676 | -5.1917 | 0.095717 | 0.002549 | 1.479 | 3e-06 | -0.095714 | -0.29658 | -0.53401 | 0.09548 | -0.42477 | 5.4164 | -0.039276 | -0.13476 | -0.22272 | -0.11879 | 121.6761 | 121.377 | 121.1396 | 5.4534 | -121.5779 | 121.2488 | 121.4509 | 121.5548 | 5.4707 | -121.5781
808.0156 | 121.8109 | -5.3192 | 116.2491 | -0.005418 | -0.033933 | 0.00050001 | 0.054517 | -0.0057325 | 0.048615 | -0.011751 | -0.0011537 | -0.001017 | -0.0039461 | 0.016998 | -0.0096721 | -3.9501 | 0.16166 | -5.4199 | 116.2699 | 115.9662 | 115.7334 | -5.3059 | 0.13383 | 0.17893 | -5.4546 | 115.8334 | 116.0492 | 116.1486 | -5.3062 | 0.013288 | 0.020841 | 1.3691 | -0.10072 | -0.11401 | -0.28288 | -0.51572 | 0.013054 | -0.41564 | 5.453 | -0.13544 | -0.14849 | -0.19985 | -0.1005 | 121.5891 | 121.2854 | 121.0526 | 5.4809 | -121.555 | 121.1527 | 121.3684 | 121.4678 | 5.4981 | -121.5552
809.7656 | 121.7377 | -5.2322 | 116.3315 | -0.005418 | -0.03372 | 0.00050001 | 0.05409 | -0.0061599 | 0.048829 | -0.0041205 | -0.0011537 | -0.00058958 | -0.0035187 | 0.016784 | -0.0098857 | -3.854 | 0.17081 | -5.3146 | 116.3615 | 116.0669 | 115.8433 | -5.2052 | 0.13841 | 0.18809 | -5.3539 | 115.9433 | 116.1408 | 116.2493 | -5.2008 | 0.027049 | 0.030011 | 1.3783 | -0.082398 | -0.10945 | -0.26454 | -0.48823 | 0.031391 | -0.38815 | 5.3706 | -0.12168 | -0.15307 | -0.19068 | -0.082171 | 121.5937 | 121.2992 | 121.0755 | 5.4031 | -121.5367 | 121.1756 | 121.373 | 121.4815 | 5.4203 | -121.5323
811.5156 | 121.6461 | -5.3329 | 116.3086 | -0.005418 | -0.034147 | 0.00092741 | 0.054303 | -0.0059463 | 0.048401 | -0.011751 | -0.00094006 | -0.00080338 | -0.0030915 | 0.016998 | -0.0096721 | -3.8814 | 0.16166 | -5.365 | 116.3203 | 116.0166 | 115.7883 | -5.2601 | 0.12925 | 0.17893 | -5.3951 | 115.9021 | 116.0996 | 116.1989 | -5.2558 | 0.07281 | 0.011693 | 1.4515 | -0.032051 | -0.10486 | -0.29202 | -0.52029 | 0.077154 | -0.40647 | 5.4622 | -0.06218 | -0.13933 | -0.209 | -0.10965 | 121.6532 | 121.3495 | 121.1213 | 5.4946 | -121.5687 | 121.2351 | 121.4325 | 121.5319 | 5.5119 | -121.5644
813.2656 | 121.6782 | -5.2963 | 116.3544 | 0.009844 | -0.033933 | 0.001141 | 0.054303 | -0.0063735 | 0.048829 | -0.011751 | -0.00072626 | -0.001017 | -0.0037325 | 0.016998 | -0.0096721 | -3.8173 | 0.16166 | -5.2826 | 116.4073 | 116.1081 | 115.8707 | -5.1777 | 0.12925 | 0.17435 | -5.3264 | 115.9708 | 116.182 | 116.2859 | -5.1688 | 0.11861 | 0.052907 | 1.479 | 0.013737 | -0.10487 | -0.24622 | -0.48365 | 0.12753 | -0.38357 | 5.4256 | -0.03012 | -0.15765 | -0.17236 | -0.06843 | 121.7036 | 121.4045 | 121.167 | 5.458 | -121.5321 | 121.2671 | 121.4783 | 121.5823 | 5.4707 | -121.5232
815.0156 | 121.7697 | -4.7699 | 116.803 | -0.013049 | -0.034147 | 0.00071361 | 0.054303 | -0.0061599 | 0.048829 | -0.0041205 | -0.00094006 | -0.00080338 | -0.0035187 | 0.016998 | -0.0094585 | -3.4648 | 0.17081 | -4.779 | 116.9063 | 116.6027 | 116.3698 | -4.6786 | 0.13383 | 0.18351 | -4.8136 | 116.4653 | 116.6811 | 116.7804 | -4.6743 | 0.091284 | 0.10334 | 1.3051 | -0.009081 | -0.10037 | -0.20031 | -0.43319 | 0.095613 | -0.3377 | 4.9037 | -0.043734 | -0.13935 | -0.1219 | -0.02255 | 121.6762 | 121.3726 | 121.1397 | 4.9407 | -121.4816 | 121.2352 | 121.451 | 121.5503 | 4.9534 | -121.4773
816.7031 | 121.7422 | -5.2689 | 116.3177 | 0.002213 | -0.033933 | 0.00092741 | 0.054303 | -0.0061599 | 0.048829 | 0.00351 | -0.0011537 | -0.00080338 | -0.0035187 | 0.016998 | -0.0094585 | -3.8402 | 0.16624 | -5.2963 | 116.3981 | 116.0898 | 115.8661 | -5.1869 | 0.12925 | 0.17893 | -5.331 | 115.9754 | 116.1774 | 116.2722 | -5.178 | 0.081986 | 0.080371 | 1.4286 | -0.027463 | -0.10945 | -0.22792 | -0.4516 | 0.090906 | -0.34237 | 5.3981 | -0.062165 | -0.15307 | -0.14032 | -0.045545 | 121.667 | 121.3587 | 121.135 | 5.4351 | -121.5046 | 121.2442 | 121.4463 | 121.5411 | 5.4478 | -121.4957
818.4375 | 121.7056 | -5.2917 | 116.3589 | 0.002213 | -0.033933 | 0.001141 | 0.054303 | -0.0061599 | 0.049042 | -0.011751 | -0.0011537 | -0.00058958 | -0.0035187 | 0.016998 | -0.0096721 | -3.8585 | 0.17539 | -5.365 | 116.3157 | 116.0211 | 115.7929 | -5.251 | 0.13383 | 0.18351 | -5.4043 | 115.893 | 116.1042 | 116.1989 | -5.2558 | 0.040769 | -0.043239 | 1.4332 | -0.07325 | -0.11402 | -0.3378 | -0.56606 | 0.035955 | -0.46598 | 5.4256 | -0.11254 | -0.14849 | -0.25477 | -0.16 | 121.6075 | 121.3129 | 121.0846 | 5.4671 | -121.6099 | 121.1847 | 121.3959 | 121.4907 | 5.4753 | -121.6147
820.1875 | 121.669 | -5.0903 | 116.5512 | -0.013049 | -0.034361 | 0.00092741 | 0.054517 | -0.0059463 | 0.048401 | -0.0041205 | -0.0011537 | -0.00080338 | -0.0035187 | 0.016784 | -0.0096721 | -3.7212 | 0.18455 | -5.1773 | 116.5034 | 116.2089 | 115.9669 | -5.0724 | 0.12925 | 0.18351 | -5.2166 | 116.0761 | 116.2873 | 116.3867 | -5.0772 | 0.017931 | -0.047785 | 1.3691 | -0.086956 | -0.10489 | -0.34232 | -0.58433 | 0.013112 | -0.4751 | 5.2196 | -0.12622 | -0.13934 | -0.26389 | -0.16454 | 121.5938 | 121.2992 | 121.0572 | 5.2749 | -121.6236 | 121.1664 | 121.3776 | 121.477 | 5.2738 | -121.6284
821.9375 | 121.7239 | -5.3192 | 116.2994 | -0.005418 | -0.034147 | 0.001141 | 0.054303 | -0.0061599 | 0.048829 | -0.011751 | -0.0011537 | -0.0012306 | -0.0037325 | 0.016998 | -0.0098857 | -3.8219 | 0.17997 | -5.2689 | 116.4164 | 116.1127 | 115.889 | -5.1686 | 0.13383 | 0.18351 | -5.3036 | 115.9891 | 116.1957 | 116.2905 | -5.1642 | 0.15066 | 0.117 | 1.4973 | 0.05036 | -0.1003 | -0.18671 | -0.4104 | 0.155 | -0.31032 | 5.453 | 0.015661 | -0.13934 | -0.10369 | -0.008919 | 121.7356 | 121.4319 | 121.2083 | 5.4992 | -121.468 | 121.3083 | 121.515 | 121.6097 | 5.5027 | -121.4637
823.6406 | 121.6415 | -5.2734 | 116.3818 | -0.005418 | -0.034147 | 0.00071361 | 0.05409 | -0.0061599 | 0.048615 | -0.0041205 | -0.00094006 | -0.00058958 | -0.0039461 | 0.016998 | -0.0094585 | -3.8356 | 0.17997 | -5.3146 | 116.3752 | 116.0715 | 115.8387 | -5.2006 | 0.13383 | 0.18351 | -5.3448 | 115.9433 | 116.1545 | 116.2447 | -5.2008 | 0.072826 | -0.006608 | 1.4378 | -0.0412 | -0.11403 | -0.31032 | -0.54316 | 0.072589 | -0.43851 | 5.4073 | -0.071324 | -0.14391 | -0.2273 | -0.1371 | 121.6487 | 121.345 | 121.1121 | 5.4534 | -121.5824 | 121.2168 | 121.428 | 121.5182 | 5.4569 | -121.5827
825.375 | 121.6553 | -5.2963 | 116.3498 | -0.02068 | -0.034361 | 0.00092741 | 0.054303 | -0.0059463 | 0.048829 | -0.011751 | -0.00094006 | -0.00080338 | -0.0037325 | 0.017211 | -0.0096721 | -3.7624 | 0.18455 | -5.2231 | 116.4576 | 116.1631 | 115.9257 | -5.1182 | 0.13841 | 0.18351 | -5.2669 | 116.0441 | 116.237 | 116.3455 | -5.1093 | 0.17814 | 0.10785 | 1.5339 | 0.073255 | -0.10488 | -0.1867 | -0.42413 | 0.18705 | -0.30574 | 5.4347 | 0.029403 | -0.15765 | -0.11284 | -0.00433 | 121.754 | 121.4594 | 121.222 | 5.4809 | -121.468 | 121.3404 | 121.5333 | 121.6418 | 5.4798 | -121.4591
827.125 | 121.7972 | -5.2185 | 116.3589 | -0.005418 | -0.034361 | 0.00092741 | 0.054303 | -0.0059463 | 0.048829 | -0.0041205 | -0.00094006 | -0.001017 | -0.0035187 | 0.016784 | -0.0096721 | -3.8219 | 0.18455 | -5.2505 | 116.4302 | 116.1356 | 115.9074 | -5.1411 | 0.12925 | 0.18351 | -5.2898 | 116.012 | 116.2141 | 116.3134 | -5.1413 | 0.077421 | 0.071221 | 1.3966 | -0.032035 | -0.10946 | -0.22333 | -0.4516 | 0.077183 | -0.34694 | 5.3478 | -0.07131 | -0.14849 | -0.14489 | -0.045536 | 121.6487 | 121.3541 | 121.1259 | 5.4031 | -121.5 | 121.2305 | 121.4326 | 121.5319 | 5.402 | -121.5003
828.8281 | 121.7789 | -4.8065 | 116.7801 | 0.002213 | -0.034361 | 0.00071361 | 0.054303 | -0.0061599 | 0.048829 | -0.011751 | -0.0011537 | -0.00058958 | -0.0037325 | 0.016998 | -0.0096721 | -3.5518 | 0.19371 | -4.8843 | 116.7827 | 116.4836 | 116.2553 | -4.7839 | 0.12925 | 0.17893 | -4.9327 | 116.3508 | 116.562 | 116.6705 | -4.7888 | 0.022591 | 0.002615 | 1.2547 | -0.077759 | -0.10035 | -0.29647 | -0.52476 | 0.017765 | -0.42928 | 4.9358 | -0.12616 | -0.14392 | -0.21806 | -0.10955 | 121.5892 | 121.2901 | 121.0618 | 5.0002 | -121.564 | 121.1573 | 121.3686 | 121.4771 | 4.9854 | -121.5688
830.5781 | 121.7697 | -5.0171 | 116.5192 | -0.005418 | -0.034147 | 0.00071361 | 0.054303 | -0.0061599 | 0.049042 | -0.011751 | -0.00094006 | -0.00058958 | -0.0035187 | 0.016784 | -0.0094585 | -3.6846 | 0.19829 | -5.072 | 116.6087 | 116.3234 | 116.0859 | -4.9625 | 0.12925 | 0.17893 | -5.1112 | 116.1814 | 116.3972 | 116.4874 | -4.9582 | 0.054583 | 0.089561 | 1.3325 | -0.054898 | -0.10948 | -0.19581 | -0.43325 | 0.05892 | -0.33776 | 5.1463 | -0.094157 | -0.15308 | -0.12196 | -0.031766 | 121.6258 | 121.3404 | 121.103 | 5.2154 | -121.4817 | 121.1985 | 121.4143 | 121.5045 | 5.196 | -121.4773
832.3281 | 121.6507 | -4.953 | 116.7389 | -0.005418 | -0.034147 | 0.00071361 | 0.054303 | -0.0061599 | 0.048615 | -0.011751 | -0.0013673 | -0.00080338 | -0.0037325 | 0.017211 | -0.0094585 | -3.5655 | 0.20744 | -4.9438 | 116.7278 | 116.4378 | 116.2004 | -4.8435 | 0.12925 | 0.17893 | -4.9876 | 116.3005 | 116.5162 | 116.6064 | -4.8437 | 0.10955 | -0.011128 | 1.3875 | 0.009207 | -0.10034 | -0.30106 | -0.53851 | 0.1093 | -0.43844 | 5.0823 | -0.034619 | -0.14392 | -0.22264 | -0.13245 | 121.6808 | 121.3908 | 121.1534 | 5.1604 | -121.5823 | 121.2535 | 121.4693 | 121.5594 | 5.1319 | -121.5826
834.0938 | 121.7834 | -5.0446 | 116.5466 | -0.005418 | -0.034574 | 0.001141 | 0.054303 | -0.0061599 | 0.048615 | -0.0041205 | -0.00094006 | -0.00080338 | -0.0035187 | 0.016998 | -0.0096721 | -3.625 | 0.2166 | -4.9804 | 116.6957 | 116.4058 | 116.1729 | -4.8755 | 0.12467 | 0.18809 | -5.0288 | 116.2638 | 116.4842 | 116.5744 | -4.8803 | 0.16905 | 0.14908 | 1.4195 | 0.064134 | -0.10492 | -0.14085 | -0.37372 | 0.16423 | -0.28281 | 5.1692 | 0.015726 | -0.1485 | -0.062434 | 0.027761 | 121.7403 | 121.4503 | 121.2175 | 5.2612 | -121.4221 | 121.3084 | 121.5288 | 121.6189 | 5.2326 | -121.427
835.7812 | 121.6827 | -4.9667 | 116.6611 | 0.002213 | -0.034361 | 0.00071361 | 0.054303 | -0.0059463 | 0.049042 | -0.0041205 | -0.0011537 | -0.001017 | -0.0035187 | 0.016998 | -0.0096721 | -3.5884 | 0.22576 | -5.0033 | 116.6774 | 116.3829 | 116.1546 | -4.8984 | 0.13383 | 0.18809 | -5.0426 | 116.2501 | 116.4613 | 116.5515 | -4.8986 | 0.068334 | 0.01633 | 1.3783 | -0.036577 | -0.10491 | -0.27819 | -0.50648 | 0.06809 | -0.41098 | 5.1006 | -0.07583 | -0.14392 | -0.19977 | -0.10957 | 121.6441 | 121.3496 | 121.1213 | 5.1925 | -121.5595 | 121.2168 | 121.428 | 121.5182 | 5.1548 | -121.5597
837.5312 | 121.7834 | -4.921 | 116.6565 | -0.005418 | -0.034574 | 0.001141 | 0.054303 | -0.0059463 | 0.048829 | -0.011751 | -0.0011537 | -0.00080338 | -0.0037325 | 0.016998 | -0.0096721 | -3.6067 | 0.25323 | -5.0033 | 116.6637 | 116.3737 | 116.1409 | -4.9121 | 0.14299 | 0.18809 | -5.0517 | 116.2364 | 116.4476 | 116.5423 | -4.9078 | 0.008821 | 0.007172 | 1.3142 | -0.082354 | -0.091175 | -0.28277 | -0.51563 | 0.013156 | -0.42014 | 5.0639 | -0.13077 | -0.14392 | -0.20892 | -0.11415 | 121.5846 | 121.2947 | 121.0618 | 5.1742 | -121.5686 | 121.1573 | 121.3685 | 121.4633 | 5.109 | -121.5643
839.2188 | 121.7606 | -4.9484 | 116.6382 | -0.013049 | -0.034147 | 0.0013548 | 0.05409 | -0.0061599 | 0.048829 | -0.011751 | -0.00094006 | -0.00080338 | -0.0041597 | 0.017211 | -0.0098857 | -3.6067 | 0.23949 | -4.953 | 116.7049 | 116.4149 | 116.1775 | -4.8755 | 0.12925 | 0.18809 | -5.0151 | 116.2821 | 116.4888 | 116.5881 | -4.8712 | 0.072918 | 0.066688 | 1.3417 | -0.004527 | -0.077445 | -0.22325 | -0.46069 | 0.077252 | -0.35605 | 5.0777 | -0.066669 | -0.14392 | -0.14941 | -0.050056 | 121.6533 | 121.3634 | 121.1259 | 5.1879 | -121.5137 | 121.2306 | 121.4372 | 121.5366 | 5.1365 | -121.5094
840.9688 | 121.7239 | -4.8111 | 116.7572 | -0.005418 | -0.034788 | 0.00092741 | 0.054303 | -0.0061599 | 0.048829 | -0.011751 | -0.0011537 | -0.001017 | -0.0041597 | 0.017425 | -0.0096721 | -3.4831 | 0.25781 | -4.8156 | 116.8468 | 116.5477 | 116.3148 | -4.7427 | 0.13841 | 0.19267 | -4.8777 | 116.4058 | 116.6353 | 116.7255 | -4.7338 | 0.068378 | 0.0896 | 1.328 | -0.004508 | -0.072886 | -0.20948 | -0.44235 | 0.077288 | -0.35145 | 4.9495 | -0.066637 | -0.14393 | -0.12191 | -0.031716 | 121.6579 | 121.3588 | 121.1259 | 5.0689 | -121.4999 | 121.2169 | 121.4464 | 121.5366 | 5.0038 | -121.491
842.6562 | 121.6553 | -4.7287 | 116.954 | -0.005418 | -0.034361 | 0.00071361 | 0.054303 | -0.0059463 | 0.048829 | -0.011751 | -0.0011537 | -0.00058958 | -0.0041597 | 0.016998 | -0.0096721 | -3.4419 | 0.26697 | -4.7927 | 116.8697 | 116.5798 | 116.3469 | -4.7061 | 0.13841 | 0.18809 | -4.8411 | 116.4424 | 116.6582 | 116.7575 | -4.7063 | 0.022612 | -0.084347 | 1.2868 | -0.064014 | -0.086626 | -0.37426 | -0.60714 | 0.022364 | -0.51166 | 4.8671 | -0.1124 | -0.13477 | -0.29586 | -0.19651 | 121.5984 | 121.3085 | 121.0756 | 4.9957 | -121.6601 | 121.1711 | 121.3869 | 121.4862 | 4.9168 | -121.6604
844.4062 | 121.6553 | -4.8523 | 116.7984 | 0.002213 | -0.034574 | 0.00071361 | 0.054303 | -0.0059463 | 0.048615 | -0.011751 | -0.00094006 | -0.00058958 | -0.0037325 | 0.017211 | -0.0098857 | -3.506 | 0.27154 | -4.8751 | 116.7964 | 116.4928 | 116.2691 | -4.7839 | 0.12925 | 0.19724 | -4.9327 | 116.3645 | 116.5758 | 116.6751 | -4.7842 | 0.068367 | -0.001961 | 1.3463 | -0.022827 | -0.091194 | -0.30562 | -0.52934 | 0.06812 | -0.43385 | 4.9815 | -0.080382 | -0.1485 | -0.22263 | -0.12328 | 121.6487 | 121.3451 | 121.1214 | 5.1238 | -121.5823 | 121.2168 | 121.4281 | 121.5274 | 5.0495 | -121.5826
846.1406 | 121.7651 | -4.7424 | 116.7984 | -0.005418 | -0.034361 | 0.00071361 | 0.054303 | -0.0061599 | 0.048829 | -0.0041205 | -0.00094006 | -0.00080338 | -0.0037325 | 0.017211 | -0.0096721 | -3.4831 | 0.27612 | -4.8385 | 116.8285 | 116.534 | 116.3011 | -4.7473 | 0.12925 | 0.18351 | -4.8915 | 116.4058 | 116.617 | 116.7117 | -4.7338 | -0.004865 | 0.030087 | 1.2593 | -0.096063 | -0.091198 | -0.26441 | -0.49729 | 0.008624 | -0.39264 | 4.8717 | -0.14904 | -0.15766 | -0.18142 | -0.086651 | 121.5709 | 121.2764 | 121.0435 | 5.0186 | -121.5457 | 121.1482 | 121.3594 | 121.4542 | 4.9259 | -121.5322
847.8906 | 121.7102 | -4.5547 | 117.0456 | -0.005418 | -0.034147 | 0.00071361 | 0.054303 | -0.0061599 | 0.048829 | -0.011751 | -0.0011537 | -0.00080338 | -0.0037325 | 0.016998 | -0.0098857 | -3.2771 | 0.27612 | -4.5546 | 117.1078 | 116.8225 | 116.585 | -4.468 | 0.13383 | 0.18809 | -4.6076 | 116.6805 | 116.8963 | 116.991 | -4.4637 | 0.086766 | 0.062177 | 1.2777 | 0.000107 | -0.086659 | -0.22313 | -0.46061 | 0.091091 | -0.36513 | 4.6886 | -0.05284 | -0.14393 | -0.14932 | -0.054548 | 121.6625 | 121.3772 | 121.1397 | 4.8309 | -121.5136 | 121.2352 | 121.451 | 121.5458 | 4.7428 | -121.5093
849.5781 | 121.7194 | -4.5364 | 117.0639 | -0.013049 | -0.034361 | 0.00071361 | 0.054303 | -0.0061599 | 0.048829 | -0.0041205 | -0.00094006 | -0.001017 | -0.0041597 | 0.017211 | -0.0096721 | -3.2633 | 0.29444 | -4.5089 | 117.1536 | 116.8591 | 116.6308 | -4.4314 | 0.13841 | 0.18351 | -4.571 | 116.7171 | 116.9421 | 117.0368 | -4.4316 | 0.10509 | 0.08965 | 1.2731 | 0.027579 | -0.077508 | -0.20481 | -0.43313 | 0.10483 | -0.34681 | 4.6748 | -0.034521 | -0.13935 | -0.12185 | -0.027073 | 121.69 | 121.3955 | 121.1672 | 4.8309 | -121.4953 | 121.2535 | 121.4785 | 121.5733 | 4.7199 | -121.4955
851.3281 | 121.7102 | -3.8956 | 117.7368 | 0.002213 | -0.034574 | 0.001141 | 0.054303 | -0.0059463 | 0.049042 | -0.019381 | -0.0011537 | -0.00058958 | -0.0039461 | 0.017211 | -0.0098857 | -2.9062 | 0.2807 | -4.0281 | 117.5931 | 117.3445 | 117.1161 | -3.9002 | 0.13383 | 0.19724 | -4.0765 | 117.2024 | 117.4182 | 117.4626 | -3.9417 | -0.004627 | -0.14374 | 0.98934 | -0.13257 | -0.12794 | -0.39236 | -0.62071 | -0.046104 | -0.5344 | 4.0294 | -0.18089 | -0.13478 | -0.31858 | -0.27417 | 121.4886 | 121.24 | 121.0117 | 4.1763 | -121.637 | 121.098 | 121.3138 | 121.3582 | 4.0928 | -121.6785
853.0156 | 121.6644 | -6.6971 | 114.9399 | -0.005418 | -0.034574 | 0.00071361 | 0.054303 | -0.0057325 | 0.048829 | 0.00351 | -0.00094006 | -0.00080338 | -0.0039461 | 0.016998 | -0.0098857 | -2.6636 | 0.28528 | -3.6985 | 117.9319 | 117.6604 | 117.432 | -3.6163 | 0.13383 | 0.19267 | -3.7514 | 117.5366 | 117.7479 | 117.8427 | -3.6166 | 3.0808 | 2.992 | 4.0335 | 2.9986 | -0.082201 | 2.7205 | 2.4921 | 3.0805 | 2.5968 | 6.8309 | 2.9457 | -0.13479 | 2.808 | 2.9028 | 124.629 | 124.3575 | 124.1291 | 6.9824 | -118.5562 | 124.2337 | 124.445 | 124.5397 | 6.8897 | -118.5565
854.7812 | 121.7651 | -2.1378 | 119.4992 | -0.013049 | -0.034361 | 0.001141 | 0.054303 | -0.0061599 | 0.048829 | -0.019381 | -0.0013673 | -0.00080338 | -0.0037325 | 0.016998 | -0.0098857 | -1.519 | 0.29902 | -2.1419 | 119.4748 | 119.1669 | 118.9384 | -2.032 | 0.14299 | 0.20182 | -2.1946 | 119.0796 | 119.2955 | 119.3353 | -2.0781 | 0.10576 | -0.02441 | 0.61878 | -0.004132 | -0.10989 | -0.33234 | -0.56082 | 0.059662 | -0.41961 | 2.2807 | -0.056853 | -0.11651 | -0.20375 | -0.16392 | 121.6126 | 121.3046 | 121.0761 | 2.4368 | -121.5312 | 121.2174 | 121.4332 | 121.473 | 2.3396 | -121.5773
856.4688 | 121.7606 | -5.7632 | 116.6656 | 0.002213 | -0.034574 | 0.00092741 | 0.054517 | -0.0061599 | 0.048829 | -0.011751 | -0.00094006 | -0.00058958 | -0.0037325 | 0.016998 | -0.0094585 | -5.8776 | 0.32191 | -7.3291 | 114.3287 | 114.0751 | 113.8195 | -7.1787 | 0.19335 | 0.22472 | -7.3731 | 113.9471 | 114.14 | 114.2576 | -7.1743 | -1.4155 | -2.337 | -0.11436 | -1.5658 | -0.15037 | -2.5905 | -2.8461 | -1.4111 | -2.7185 | 5.9566 | -1.6099 | -0.19881 | -2.5257 | -2.408 | 120.0919 | 119.8384 | 119.5828 | 6.0852 | -123.8444 | 119.7103 | 119.9032 | 120.0209 | 5.988 | -123.84
858.2188 | 121.6553 | -1.2543 | 120.4559 | -0.005418 | -0.034574 | 0.00071361 | 0.054517 | -0.0063735 | 0.048829 | -0.019381 | -0.00094006 | -0.00080338 | -0.0037325 | 0.017425 | -0.0098857 | -0.85969 | 0.30359 | -1.24 | 120.3859 | 120.1147 | 119.8862 | -1.1345 | 0.14757 | 0.2064 | -1.2834 | 119.9861 | 120.202 | 120.2464 | -1.1761 | 0.11975 | -0.070037 | 0.39458 | 0.014305 | -0.10544 | -0.34123 | -0.56978 | 0.078205 | -0.46979 | 1.4018 | -0.029173 | -0.10738 | -0.25391 | -0.2095 | 121.6402 | 121.369 | 121.1404 | 1.5579 | -121.5905 | 121.2404 | 121.4563 | 121.5007 | 1.4607 | -121.632
859.9688 | 121.6827 | -37.1658 | 84.8511 | -0.005418 | -0.035002 | 0.00071361 | 0.05409 | -0.0059463 | 0.049256 | -0.019381 | -0.00094006 | -0.001017 | -0.0037325 | 0.017425 | -0.0098857 | -28.7375 | -0.053537 | -29.8496 | 91.8259 | 91.5147 | 91.4439 | -29.7665 | -0.053897 | -0.054586 | -30.0286 | 91.3934 | 91.6178 | 91.6164 | -29.7433 | 7.3993 | 6.9748 | 8.4283 | 7.3162 | -0.083101 | 6.6637 | 6.5928 | 7.4225 | 6.5424 | 37.1119 | 7.1372 | -0.28528 | 6.7667 | 6.7654 | 128.9917 | 128.6806 | 128.6097 | 37.1123 | -114.6176 | 128.5593 | 128.7836 | 128.7823 | 37.1112 | -114.5944
861.6562 | 121.6278 | -0.89264 | 120.7993 | -0.005418 | -0.034574 | 0.001782 | 0.054303 | -0.0055189 | 0.048829 | -0.011751 | -0.00051266 | -0.001017 | -0.0037325 | 0.017211 | -0.0098857 | -1.1481 | 0.35396 | -1.6245 | 119.9693 | 119.7026 | 119.41 | -1.5146 | 0.1842 | 0.25219 | -1.6452 | 119.5787 | 119.7808 | 119.8618 | -1.5424 | -0.62194 | -0.82999 | -0.25549 | -0.7319 | -0.10997 | -1.0967 | -1.3893 | -0.64973 | -1.2206 | 1.0768 | -0.75252 | -0.10279 | -1.0185 | -0.93743 | 120.8619 | 120.5952 | 120.3026 | 1.2466 | -122.3138 | 120.4713 | 120.6734 | 120.7545 | 1.1448 | -122.3416
863.4062 | 121.7468 | -0.82398 | 120.7901 | -0.013049 | -0.034788 | 0.0015684 | 0.054517 | -0.0053053 | 0.048829 | -0.011751 | -8.5458e-05 | -0.001017 | -0.0035187 | 0.016998 | -0.0096721 | -0.54836 | 0.30817 | -0.7684 | 120.8346 | 120.5772 | 120.2937 | -0.67205 | 0.14757 | 0.21098 | -0.81642 | 120.4348 | 120.6553 | 120.6906 | -0.72276 | 0.15192 | 0.044478 | 0.27562 | 0.055571 | -0.09635 | -0.21292 | -0.49645 | 0.10121 | -0.35527 | 0.97154 | 0.007558 | -0.093653 | -0.1348 | -0.099544 | 121.6586 | 121.4012 | 121.1176 | 1.1321 | -121.4622 | 121.2588 | 121.4793 | 121.5145 | 1.035 | -121.5129
865.1719 | 121.7422 | -1.1444 | 120.4468 | -0.013049 | -0.034574 | 0.0015684 | 0.054517 | -0.0053053 | 0.048615 | -0.019381 | 0.00034194 | -0.00080338 | -0.0037325 | 0.017211 | -0.0098857 | -0.78186 | 0.29902 | -1.1026 | 120.4912 | 120.2338 | 119.9594 | -1.0063 | 0.14757 | 0.2064 | -1.1552 | 120.1052 | 120.3165 | 120.3517 | -1.0524 | 0.13809 | 0.044422 | 0.36255 | 0.041791 | -0.096302 | -0.21302 | -0.48736 | 0.09197 | -0.3416 | 1.292 | -0.010832 | -0.1028 | -0.13029 | -0.095038 | 121.6356 | 121.3782 | 121.1038 | 1.4434 | -121.4531 | 121.2496 | 121.4609 | 121.4961 | 1.3508 | -121.4992
866.9219 | 121.6782 | -1.181 | 120.4926 | 0.002213 | -0.034574 | 0.0019958 | 0.054303 | -0.0053053 | 0.048829 | -0.011751 | -0.00051266 | -0.001017 | -0.0037325 | 0.017211 | -0.0098857 | -0.87343 | 0.30359 | -1.2445 | 120.3584 | 120.1101 | 119.8266 | -1.1437 | 0.14299 | 0.2064 | -1.3018 | 119.9678 | 120.1883 | 120.2235 | -1.1898 | 0.037347 | -0.13413 | 0.30761 | -0.063515 | -0.10086 | -0.38242 | -0.66592 | -0.008774 | -0.52473 | 1.324 | -0.12073 | -0.11196 | -0.30427 | -0.26902 | 121.5395 | 121.2912 | 121.0077 | 1.4846 | -121.6362 | 121.1489 | 121.3693 | 121.4046 | 1.3874 | -121.6824
868.6094 | 121.7285 | -1.2451 | 120.3644 | -0.005418 | -0.034788 | 0.0015684 | 0.054303 | -0.0053053 | 0.049042 | -0.019381 | -0.00029906 | -0.00058958 | -0.0039461 | 0.017425 | -0.0096721 | -0.88716 | 0.30359 | -1.2491 | 120.3584 | 120.1055 | 119.8175 | -1.1437 | 0.13841 | 0.2064 | -1.2926 | 119.9632 | 120.17 | 120.219 | -1.1944 | 0.10143 | -0.005954 | 0.35796 | -0.004006 | -0.10544 | -0.25883 | -0.5469 | 0.050734 | -0.40113 | 1.3835 | -0.047486 | -0.09822 | -0.19441 | -0.14542 | 121.6035 | 121.3507 | 121.0626 | 1.5487 | -121.5081 | 121.2084 | 121.4151 | 121.4641 | 1.4515 | -121.5588
870.3594 | 121.6827 | -0.78278 | 120.8817 | -0.005418 | -0.034574 | 0.0015684 | 0.054517 | -0.0055189 | 0.048615 | -0.011751 | -0.00029906 | -0.00080338 | -0.0039461 | 0.017211 | -0.010099 | -0.52089 | 0.31733 | -0.75467 | 120.8575 | 120.6047 | 120.3211 | -0.64458 | 0.14757 | 0.21098 | -0.7981 | 120.4669 | 120.6782 | 120.718 | -0.69529 | 0.1382 | -0.024183 | 0.26189 | 0.028107 | -0.11009 | -0.277 | -0.56053 | 0.087484 | -0.41477 | 0.93034 | -0.015326 | -0.10281 | -0.20346 | -0.16363 | 121.6402 | 121.3874 | 121.1039 | 1.1001 | -121.5262 | 121.2497 | 121.461 | 121.5008 | 0.99376 | -121.5769
872.1094 | 121.701 | -0.50354 | 121.138 | -0.005418 | -0.034574 | 0.0015684 | 0.05409 | -0.0050917 | 0.048615 | -0.019381 | -0.00029906 | -0.00058958 | -0.0037325 | 0.017211 | -0.010099 | -0.33775 | 0.31733 | -0.47997 | 121.1368 | 120.8794 | 120.6004 | -0.42937 | 0.13383 | 0.20182 | -0.52338 | 120.737 | 120.9621 | 120.9973 | -0.42514 | 0.074169 | -0.001249 | 0.16579 | 0.023568 | -0.050601 | -0.25861 | -0.53758 | 0.078399 | -0.40099 | 0.63737 | -0.01984 | -0.098239 | -0.17593 | -0.14068 | 121.6403 | 121.3829 | 121.104 | 0.82087 | -121.5674 | 121.2406 | 121.4656 | 121.5009 | 0.70536 | -121.5631
873.7969 | 121.7377 | -0.66834 | 120.9412 | -0.013049 | -0.034788 | 0.0013548 | 0.054303 | -0.0050917 | 0.048829 | -0.011751 | -8.5458e-05 | -0.00080338 | -0.0035187 | 0.017425 | -0.010099 | -0.46595 | 0.30817 | -0.66768 | 120.9445 | 120.6825 | 120.4035 | -0.62169 | 0.14299 | 0.20182 | -0.71569 | 120.5493 | 120.7652 | 120.8004 | -0.61287 | 0.046649 | 0.003297 | 0.20239 | 0.000653 | -0.045996 | -0.25867 | -0.53762 | 0.055462 | -0.39187 | 0.81132 | -0.04735 | -0.10281 | -0.17597 | -0.14072 | 121.6128 | 121.3508 | 121.0719 | 0.97651 | -121.5628 | 121.2176 | 121.4335 | 121.4688 | 0.87016 | -121.554
875.5469 | 121.6827 | -0.77362 | 120.9229 | -0.005418 | -0.034788 | 0.0019958 | 0.054517 | -0.0055189 | 0.048401 | -0.019381 | -0.00029906 | -0.00080338 | -0.0039461 | 0.017211 | -0.0098857 | -0.49342 | 0.32649 | -0.70889 | 120.9033 | 120.6459 | 120.3623 | -0.65374 | 0.13841 | 0.19724 | -0.75231 | 120.5081 | 120.7286 | 120.773 | -0.65408 | 0.11988 | -0.019598 | 0.2802 | 0.064735 | -0.055147 | -0.27699 | -0.56052 | 0.11954 | -0.41476 | 0.91203 | 0.021306 | -0.098233 | -0.19429 | -0.14988 | 121.6769 | 121.4195 | 121.136 | 1.1001 | -121.5766 | 121.2817 | 121.5022 | 121.5466 | 0.97086 | -121.5769
877.2969 | 121.7834 | -0.59052 | 121.0007 | 0.002213 | -0.035002 | 0.0013548 | 0.054303 | -0.0050917 | 0.048615 | -0.019381 | -8.5458e-05 | -0.001017 | -0.0035187 | 0.017211 | -0.0098857 | -0.6445 | 0.34022 | -0.93322 | 120.6835 | 120.4261 | 120.1288 | -0.86895 | 0.1613 | 0.22014 | -0.97667 | 120.2883 | 120.4996 | 120.544 | -0.86471 | -0.27843 | -0.31718 | -0.05399 | -0.34271 | -0.064274 | -0.5746 | -0.87185 | -0.27419 | -0.71235 | 0.75182 | -0.38616 | -0.11196 | -0.50104 | -0.45663 | 121.274 | 121.0166 | 120.7193 | 0.93074 | -121.8696 | 120.8788 | 121.0901 | 121.1346 | 0.81065 | -121.8654
879.0469 | 121.669 | -0.59052 | 121.106 | -0.005418 | -0.034788 | 0.001782 | 0.05409 | -0.0055189 | 0.048829 | -0.019381 | -0.00029906 | -0.00058958 | -0.0035187 | 0.017639 | -0.0096721 | -0.3698 | 0.33107 | -0.53033 | 121.0864 | 120.8336 | 120.5501 | -0.47516 | 0.14757 | 0.20182 | -0.56917 | 120.6958 | 120.9117 | 120.947 | -0.47093 | 0.11535 | -0.019568 | 0.22071 | 0.060182 | -0.055173 | -0.27236 | -0.5559 | 0.11958 | -0.41015 | 0.73808 | 0.021348 | -0.098237 | -0.19425 | -0.159 | 121.6769 | 121.4241 | 121.1406 | 0.92158 | -121.5811 | 121.2863 | 121.5022 | 121.5375 | 0.79234 | -121.5769
880.75 | 121.6415 | -0.5722 | 121.1288 | -0.013049 | -0.034788 | 0.0015684 | 0.054303 | -0.0053053 | 0.048615 | -0.019381 | -0.00029906 | -0.001017 | -0.0037325 | 0.017425 | -0.0096721 | -0.3698 | 0.34022 | -0.53033 | 121.0864 | 120.8244 | 120.5455 | -0.47974 | 0.15215 | 0.21098 | -0.57832 | 120.6821 | 120.9071 | 120.9424 | -0.48009 | 0.092466 | -0.042456 | 0.2024 | 0.041872 | -0.050594 | -0.3044 | -0.58337 | 0.092118 | -0.44677 | 0.72435 | -0.006119 | -0.098237 | -0.22172 | -0.18647 | 121.6586 | 121.3966 | 121.1177 | 0.91243 | -121.6086 | 121.2543 | 121.4793 | 121.5146 | 0.78319 | -121.6089
882.5 | 121.7102 | -0.48065 | 121.17 | -0.005418 | -0.034788 | 0.001782 | 0.05409 | -0.0050917 | 0.049042 | -0.011751 | -0.00029906 | -0.00058958 | -0.0037325 | 0.017425 | -0.0096721 | -0.5392 | 0.35396 | -0.75467 | 120.8666 | 120.6092 | 120.3211 | -0.68121 | 0.15215 | 0.22014 | -0.78895 | 120.476 | 120.6919 | 120.7363 | -0.68613 | -0.20056 | -0.30342 | -0.05855 | -0.27402 | -0.073457 | -0.56081 | -0.84892 | -0.20548 | -0.69401 | 0.6328 | -0.30829 | -0.10281 | -0.47811 | -0.4337 | 121.3473 | 121.0899 | 120.8018 | 0.83461 | -121.8513 | 120.9567 | 121.1726 | 121.217 | 0.70079 | -121.8562
884.1719 | 121.6919 | -0.63629 | 121.0327 | 0.002213 | -0.034788 | 0.0015684 | 0.05409 | -0.0050917 | 0.049042 | -0.011751 | 0.00034194 | -0.00080338 | -0.0039461 | 0.017639 | -0.0098857 | -0.4339 | 0.35396 | -0.63106 | 120.9902 | 120.7374 | 120.4539 | -0.5759 | 0.14299 | 0.20182 | -0.6699 | 120.5905 | 120.811 | 120.8554 | -0.57166 | 0.060395 | -0.042472 | 0.20239 | 0.005236 | -0.055159 | -0.29527 | -0.57881 | 0.064629 | -0.44221 | 0.77928 | -0.033606 | -0.098235 | -0.22174 | -0.17733 | 121.6265 | 121.3737 | 121.0902 | 0.99025 | -121.6086 | 121.2268 | 121.4473 | 121.4917 | 0.83811 | -121.6044
885.9219 | 121.7056 | -1.0162 | 120.639 | 0.002213 | -0.034788 | 0.0015684 | 0.054303 | -0.0055189 | 0.048615 | -0.0041205 | -0.00029906 | -0.001017 | -0.0039461 | 0.017211 | -0.0098857 | -0.68571 | 0.35396 | -0.96985 | 120.6423 | 120.3849 | 120.1059 | -0.91474 | 0.13841 | 0.20182 | -1.0133 | 120.2471 | 120.463 | 120.5074 | -0.91507 | 0.1015 | 0.003248 | 0.33052 | 0.046387 | -0.055111 | -0.25417 | -0.53311 | 0.10116 | -0.39192 | 1.1546 | 0.002934 | -0.098226 | -0.17603 | -0.13163 | 121.6585 | 121.4011 | 121.1222 | 1.3702 | -121.5538 | 121.2633 | 121.4792 | 121.5236 | 1.2181 | -121.5541
887.6094 | 121.7194 | -0.46234 | 121.1792 | 0.002213 | -0.034788 | 0.001782 | 0.054517 | -0.0055189 | 0.048829 | -0.019381 | -0.00029906 | -0.00058958 | -0.0039461 | 0.017639 | -0.0096721 | -0.69029 | 0.39059 | -1.066 | 120.5553 | 120.2933 | 120.0189 | -1.0155 | 0.14299 | 0.19724 | -1.1095 | 120.1647 | 120.376 | 120.4113 | -1.0112 | -0.55313 | -0.6239 | -0.22795 | -0.60365 | -0.050518 | -0.88591 | -1.1603 | -0.54889 | -1.0145 | 0.60533 | -0.64711 | -0.098224 | -0.80319 | -0.76794 | 121.0176 | 120.7556 | 120.4813 | 0.85293 | -122.1947 | 120.627 | 120.8383 | 120.8736 | 0.65958 | -122.1904
889.3594 | 121.6278 | -0.64545 | 121.0556 | -0.02068 | -0.035002 | 0.001782 | 0.05409 | -0.0053053 | 0.048615 | -0.019381 | 0.00012814 | -0.00080338 | -0.0039461 | 0.017425 | -0.010099 | -0.45679 | 0.40432 | -0.64479 | 120.9719 | 120.71 | 120.4356 | -0.58505 | 0.13841 | 0.2064 | -0.68821 | 120.5768 | 120.7881 | 120.8279 | -0.5854 | 0.060392 | -0.083674 | 0.18866 | 0.000657 | -0.059735 | -0.34564 | -0.62001 | 0.060047 | -0.47884 | 0.78386 | -0.042766 | -0.10281 | -0.26752 | -0.22769 | 121.6174 | 121.3554 | 121.081 | 1.0498 | -121.6407 | 121.2222 | 121.4335 | 121.4734 | 0.85185 | -121.641
891.1094 | 121.6827 | -0.74616 | 120.8908 | -0.013049 | -0.034788 | 0.0015684 | 0.054303 | -0.0055189 | 0.048401 | -0.019381 | -0.00029906 | -0.001017 | -0.0037325 | 0.017639 | -0.0098857 | -0.6674 | 0.41348 | -0.95154 | 120.6606 | 120.4032 | 120.1334 | -0.88269 | 0.14299 | 0.2064 | -0.99041 | 120.2654 | 120.4813 | 120.5303 | -0.88302 | -0.13653 | -0.23021 | 0.078758 | -0.20538 | -0.06885 | -0.48763 | -0.75741 | -0.13687 | -0.62538 | 0.88914 | -0.24425 | -0.10738 | -0.40949 | -0.3605 | 121.4068 | 121.1493 | 120.8796 | 1.1596 | -121.7735 | 121.0116 | 121.2275 | 121.2765 | 0.95256 | -121.7738
892.8125 | 121.637 | -0.76446 | 120.9183 | -0.005418 | -0.035002 | 0.001782 | 0.054303 | -0.0050917 | 0.048829 | -0.011751 | -8.5458e-05 | -0.00080338 | -0.0039461 | 0.017211 | -0.010099 | -0.40185 | 0.40432 | -0.57154 | 121.0314 | 120.7741 | 120.4997 | -0.47974 | 0.13383 | 0.19267 | -0.61038 | 120.6363 | 120.8568 | 120.8966 | -0.51672 | 0.28473 | 0.11317 | 0.36261 | 0.19293 | -0.091799 | -0.1442 | -0.41858 | 0.24775 | -0.28199 | 0.89829 | 0.15409 | -0.093657 | -0.061511 | -0.021681 | 121.7959 | 121.5385 | 121.2642 | 1.1688 | -121.398 | 121.4008 | 121.6212 | 121.6611 | 0.95713 | -121.435
894.5625 | 121.7377 | -0.86517 | 120.7306 | 0.002213 | -0.035002 | 0.0019958 | 0.054517 | -0.0053053 | 0.048829 | -0.027012 | -0.00051266 | -0.00037598 | -0.0037325 | 0.017425 | -0.010099 | -0.52547 | 0.39975 | -0.74093 | 120.8758 | 120.6092 | 120.3394 | -0.68579 | 0.12467 | 0.19267 | -0.78895 | 120.476 | 120.6874 | 120.7318 | -0.69071 | 0.17938 | 0.14519 | 0.33971 | 0.12424 | -0.055143 | -0.12136 | -0.39115 | 0.17446 | -0.25455 | 0.98985 | 0.076228 | -0.098232 | -0.043237 | 0.001172 | 121.741 | 121.4744 | 121.2046 | 1.2649 | -121.4164 | 121.3412 | 121.5525 | 121.5969 | 1.0578 | -121.4213
896.25 | 121.6827 | -0.55847 | 121.0327 | -0.005418 | -0.035002 | 0.0019958 | 0.05409 | -0.0050917 | 0.048829 | -0.011751 | -8.5458e-05 | -0.00058958 | -0.0037325 | 0.017211 | -0.0098857 | -0.3698 | 0.39975 | -0.53033 | 121.0818 | 120.8153 | 120.5409 | -0.43395 | 0.14299 | 0.19724 | -0.56917 | 120.6821 | 120.898 | 120.9424 | -0.47551 | 0.12452 | 0.049096 | 0.18867 | 0.028139 | -0.096383 | -0.21743 | -0.49182 | 0.082964 | -0.35064 | 0.70146 | -0.010695 | -0.093659 | -0.13474 | -0.090336 | 121.6403 | 121.3738 | 121.0994 | 0.95822 | -121.4667 | 121.2405 | 121.4564 | 121.5009 | 0.75571 | -121.5082
897.9844 | 121.6095 | -3.2547 | 118.3456 | 0.002213 | -0.035429 | 0.0015684 | 0.054517 | -0.0053053 | 0.048829 | -0.011751 | 0.00012814 | -0.001017 | -0.0033051 | 0.017639 | -0.010099 | -1.1115 | 0.33107 | -1.5879 | 120.0288 | 119.7392 | 119.5107 | -1.5466 | 0.069728 | 0.13314 | -1.6681 | 119.6015 | 119.8174 | 119.8527 | -1.5561 | 1.7081 | 1.6831 | 2.1432 | 1.6668 | -0.041287 | 1.3936 | 1.1651 | 1.6986 | 1.2559 | 3.3244 | 1.5866 | -0.11195 | 1.4718 | 1.507 | 123.2835 | 122.9939 | 122.7654 | 3.5858 | -119.8923 | 122.8562 | 123.0721 | 123.1074 | 3.3878 | -119.9018
899.6875 | 121.6919 | -98.8403 | 22.4854 | -0.005418 | -0.034361 | 0.00050001 | 0.053876 | -0.0061599 | 0.049683 | -0.011751 | -0.0015809 | -0.0014444 | -0.0039461 | 0.016784 | -0.0094585 | -55.5485 | -1.6698 | -58.1663 | 63.4033 | 62.8324 | 63.345 | -58.7282 | -1.3222 | -1.4282 | -58.879 | 62.6496 | 63.0565 | 62.4965 | -58.7455 | 40.1121 | 40.9179 | 43.2918 | 40.674 | 0.56193 | 40.347 | 40.8596 | 40.0948 | 40.1643 | 97.5181 | 39.9613 | -0.1335 | 40.5711 | 40.0112 | 162.2436 | 161.6727 | 162.1853 | 97.1705 | -81.2136 | 161.49 | 161.8968 | 161.3368 | 97.4121 | -81.2309
901.4531 | 121.701 | -109.758 | 11.7004 | -0.005418 | -0.035856 | -0.00014099 | 0.053449 | -0.0059463 | 0.049683 | -0.011751 | -0.0022219 | -0.001658 | -0.0048007 | 0.017639 | -0.0090311 | -106.6937 | -0.72659 | -109.3194 | 11.7362 | 11.672 | 11.6434 | -109.6321 | -0.13631 | -0.26521 | -109.4829 | 11.6223 | 11.6754 | 11.7519 | -109.5933 | 0.12585 | 0.035735 | 3.0643 | 0.43856 | 0.31271 | -0.028401 | -0.057023 | 0.1647 | -0.078123 | 109.6217 | 0.27506 | 0.11036 | -0.025032 | 0.051427 | 121.4942 | 121.43 | 121.4014 | 109.0314 | -121.3326 | 121.3803 | 121.4334 | 121.5099 | 109.4928 | -121.2937
903.2031 | 121.669 | -110.8475 | 10.6155 | 0.002213 | -0.035856 | 7.2612e-05 | 0.053235 | -0.0059463 | 0.050111 | -0.011751 | -0.0017945 | -0.0018716 | -0.0048007 | 0.017639 | -0.0092447 | -107.7742 | -0.64875 | -110.4732 | 10.5962 | 10.541 | 10.5125 | -110.7769 | -0.090527 | -0.2011 | -110.6322 | 10.4823 | 10.5445 | 10.621 | -110.7426 | 0.070599 | -0.019385 | 3.0733 | 0.37431 | 0.30371 | -0.074497 | -0.10304 | 0.10489 | -0.13327 | 110.7569 | 0.21528 | 0.11039 | -0.071048 | 0.005411 | 121.4436 | 121.3885 | 121.36 | 110.1987 | -121.3924 | 121.3297 | 121.392 | 121.4684 | 110.6464 | -121.3581
904.9688 | 121.8063 | -111.3281 | 10.1028 | -0.013049 | -0.03607 | 7.2612e-05 | 0.053449 | -0.0061599 | 0.050324 | -0.019381 | -0.0017945 | -0.001658 | -0.0052279 | 0.017852 | -0.0090311 | -108.4381 | -0.62128 | -111.0317 | 10.0422 | 9.9962 | 9.9722 | -111.3309 | -0.067633 | -0.16448 | -111.1816 | 9.9466 | 9.9996 | 10.0853 | -111.3012 | -0.002799 | -0.060674 | 2.8901 | 0.29641 | 0.29921 | -0.10669 | -0.13062 | 0.026925 | -0.15626 | 111.2605 | 0.14649 | 0.11956 | -0.1032 | -0.017589 | 121.3703 | 121.3243 | 121.3004 | 110.7068 | -121.4338 | 121.2747 | 121.3278 | 121.4134 | 111.1637 | -121.404
906.6562 | 121.8475 | -111.6394 | 9.7916 | -0.005418 | -0.036284 | -0.00035479 | 0.053449 | -0.0057325 | 0.050324 | -0.0041205 | -0.0017945 | -0.001658 | -0.0045871 | 0.017639 | -0.0092447 | -108.7723 | -0.6167 | -111.3476 | 9.7263 | 9.6848 | 9.6563 | -111.6606 | -0.049318 | -0.137 | -111.5067 | 9.6307 | 9.6837 | 9.7693 | -111.6263 | -0.021202 | -0.065304 | 2.8671 | 0.29179 | 0.31299 | -0.10678 | -0.13526 | 0.013108 | -0.1609 | 111.5901 | 0.13268 | 0.11957 | -0.10785 | -0.022234 | 121.3657 | 121.3242 | 121.2957 | 111.0227 | -121.4522 | 121.2701 | 121.3231 | 121.4087 | 111.5024 | -121.4179
908.4062 | 121.7239 | -111.8042 | 9.7137 | 0.002213 | -0.03607 | -0.00014099 | 0.053449 | -0.0061599 | 0.050324 | -0.019381 | -0.0022219 | -0.0018716 | -0.0045871 | 0.017852 | -0.0092447 | -108.8501 | -0.61213 | -111.4712 | 9.6072 | 9.5612 | 9.5418 | -111.7797 | -0.044739 | -0.12327 | -111.6258 | 9.5162 | 9.5647 | 9.6549 | -111.7499 | 0.024541 | -0.10652 | 2.9541 | 0.33297 | 0.30843 | -0.15259 | -0.17191 | 0.054275 | -0.19754 | 111.7595 | 0.17842 | 0.12415 | -0.14907 | -0.058879 | 121.4114 | 121.3654 | 121.346 | 111.1921 | -121.4934 | 121.3204 | 121.3689 | 121.4591 | 111.6809 | -121.4637
910.0938 | 121.7468 | -111.9919 | 9.4666 | 0.002213 | -0.03607 | 7.2612e-05 | 0.053449 | -0.0061599 | 0.050324 | 0.00351 | -0.0020083 | -0.0018716 | -0.0045871 | 0.017639 | -0.0096721 | -108.9646 | -0.62128 | -111.6589 | 9.4287 | 9.378 | 9.345 | -111.972 | -0.031003 | -0.11411 | -111.8181 | 9.3285 | 9.3815 | 9.4717 | -111.9422 | 0.019909 | -0.037887 | 3.0273 | 0.33295 | 0.31304 | -0.088557 | -0.1216 | 0.049648 | -0.13806 | 111.9609 | 0.1738 | 0.12415 | -0.085026 | 0.005169 | 121.4205 | 121.3699 | 121.3368 | 111.3706 | -121.4385 | 121.3204 | 121.3734 | 121.4636 | 111.8778 | -121.4088
911.8438 | 121.6827 | -111.9415 | 9.581 | -0.005418 | -0.03607 | 7.2612e-05 | 0.053449 | -0.0059463 | 0.050538 | -0.011751 | -0.0017945 | -0.0014444 | -0.0043733 | 0.018066 | -0.0090311 | -108.9051 | -0.61213 | -111.5948 | 9.5065 | 9.4513 | 9.432 | -111.8987 | -0.021846 | -0.10495 | -111.7402 | 9.4063 | 9.4594 | 9.545 | -111.8781 | 0.042818 | -0.074495 | 3.0365 | 0.34669 | 0.30387 | -0.12974 | -0.14904 | 0.063397 | -0.17467 | 111.9197 | 0.20129 | 0.13789 | -0.12163 | -0.036014 | 121.448 | 121.3928 | 121.3735 | 111.3294 | -121.4797 | 121.3479 | 121.4009 | 121.4865 | 111.8366 | -121.4591
913.5938 | 121.7834 | -112.0148 | 9.4437 | -0.013049 | -0.035856 | -0.00014099 | 0.053449 | -0.0059463 | 0.050111 | -0.0041205 | -0.0020083 | -0.0014444 | -0.0045871 | 0.018066 | -0.0094585 | -109.0928 | -0.60755 | -111.7093 | 9.3829 | 9.3276 | 9.2992 | -112.0269 | -0.003531 | -0.10037 | -111.8822 | 9.2781 | 9.3312 | 9.4214 | -112.0018 | -0.012149 | -0.060783 | 2.922 | 0.30547 | 0.31762 | -0.11604 | -0.14449 | 0.013012 | -0.16554 | 112.0112 | 0.13259 | 0.11958 | -0.1125 | -0.022308 | 121.3977 | 121.3424 | 121.3139 | 111.4072 | -121.4706 | 121.2929 | 121.3459 | 121.4361 | 111.9144 | -121.4454
915.3438 | 121.7285 | -111.9049 | 9.5856 | -0.005418 | -0.03607 | 7.2612e-05 | 0.053449 | -0.0057325 | 0.050324 | -0.0041205 | -0.0017945 | -0.001658 | -0.0045871 | 0.018066 | -0.0092447 | -108.9737 | -0.61213 | -111.6589 | 9.4424 | 9.4009 | 9.3587 | -111.9674 | -0.00811 | -0.086637 | -111.8135 | 9.3331 | 9.3998 | 9.4855 | -111.9468 | -0.062487 | -0.14317 | 2.9312 | 0.24597 | 0.30846 | -0.18468 | -0.22688 | -0.041906 | -0.2525 | 111.8968 | 0.091406 | 0.13331 | -0.18573 | -0.10011 | 121.3473 | 121.3058 | 121.2636 | 111.2928 | -121.553 | 121.238 | 121.3047 | 121.3904 | 111.8183 | -121.5324
917.0938 | 121.701 | -111.9324 | 9.5901 | -0.005418 | -0.035856 | -0.00014099 | 0.053235 | -0.0061599 | 0.050538 | -0.0041205 | -0.0017945 | -0.0020852 | -0.0048007 | 0.017425 | -0.0092447 | -108.8822 | -0.59381 | -111.5811 | 9.5248 | 9.4787 | 9.4548 | -111.83 | -0.00811 | -0.086637 | -111.7265 | 9.4292 | 9.4868 | 9.5725 | -111.8598 | 0.10235 | -0.065337 | 3.0502 | 0.35127 | 0.24892 | -0.11142 | -0.13531 | 0.072558 | -0.16093 | 111.9243 | 0.20587 | 0.13331 | -0.10331 | -0.017698 | 121.4572 | 121.4111 | 121.3872 | 111.3386 | -121.4202 | 121.3616 | 121.4192 | 121.5048 | 111.8457 | -121.45
918.8438 | 121.6827 | -111.8729 | 9.668 | -0.005418 | -0.03607 | -0.00014099 | 0.053662 | -0.0061599 | 0.050538 | -0.0041205 | -0.0017945 | -0.001658 | -0.0048007 | 0.017852 | -0.0090311 | -108.7448 | -0.58923 | -111.4529 | 9.6576 | 9.6069 | 9.5785 | -111.7018 | 0.001048 | -0.077479 | -111.5937 | 9.562 | 9.615 | 9.7007 | -111.7362 | 0.17105 | -0.010384 | 3.128 | 0.41995 | 0.2489 | -0.061026 | -0.089503 | 0.13668 | -0.10598 | 111.8739 | 0.27914 | 0.14246 | -0.052933 | 0.032683 | 121.5304 | 121.4798 | 121.4513 | 111.2836 | -121.3698 | 121.4349 | 121.4879 | 121.5735 | 111.7954 | -121.4042
920.5469 | 121.8155 | -111.6852 | 9.7595 | 0.002213 | -0.03607 | 0.00028641 | 0.053021 | -0.0061599 | 0.050324 | -0.019381 | -0.0022219 | -0.0018716 | -0.0045871 | 0.017639 | -0.0088175 | -108.7723 | -0.58923 | -111.43 | 9.6896 | 9.6253 | 9.6059 | -111.7384 | 0.001048 | -0.077479 | -111.5708 | 9.5849 | 9.6334 | 9.719 | -111.7133 | -0.053267 | -0.069887 | 2.9129 | 0.25516 | 0.30842 | -0.13426 | -0.15358 | -0.028112 | -0.17464 | 111.6862 | 0.11435 | 0.14246 | -0.12617 | -0.040554 | 121.3748 | 121.3104 | 121.2911 | 111.0959 | -121.498 | 121.2701 | 121.3185 | 121.4041 | 111.6077 | -121.4728
922.2969 | 121.7789 | -111.6852 | 9.7961 | -0.005418 | -0.036711 | 7.2612e-05 | 0.053235 | -0.0057325 | 0.050538 | -0.011751 | -0.0017945 | -0.001658 | -0.0048007 | 0.017852 | -0.0092447 | -108.786 | -0.56634 | -111.3934 | 9.7263 | 9.671 | 9.6426 | -111.7018 | -0.003531 | -0.077479 | -111.5434 | 9.6307 | 9.6746 | 9.7648 | -111.6721 | -0.016636 | -0.069882 | 2.8992 | 0.29178 | 0.30842 | -0.12509 | -0.15358 | 0.013097 | -0.16547 | 111.6817 | 0.14182 | 0.12873 | -0.12159 | -0.03139 | 121.4114 | 121.3562 | 121.3277 | 111.1188 | -121.498 | 121.3159 | 121.3597 | 121.4499 | 111.6077 | -121.4682
923.9844 | 121.6736 | -111.9965 | 9.5535 | 0.002213 | -0.036284 | 7.2612e-05 | 0.053449 | -0.0061599 | 0.049897 | -0.011751 | -0.0020083 | -0.001658 | -0.0048007 | 0.017639 | -0.0092447 | -108.9371 | -0.58008 | -111.6498 | 9.4836 | 9.4329 | 9.3953 | -111.9445 | 0.001048 | -0.082058 | -111.786 | 9.3697 | 9.4319 | 9.5175 | -111.9239 | 0.05196 | -0.069921 | 3.0593 | 0.34668 | 0.29472 | -0.12058 | -0.15821 | 0.072541 | -0.18383 | 111.9975 | 0.21043 | 0.13789 | -0.12164 | -0.03602 | 121.4801 | 121.4294 | 121.3918 | 111.4164 | -121.498 | 121.3662 | 121.4284 | 121.514 | 111.9144 | -121.4774
925.7344 | 121.701 | -112.1979 | 9.3384 | -0.005418 | -0.036284 | 7.2612e-05 | 0.053662 | -0.0061599 | 0.050111 | -0.011751 | -0.0022219 | -0.001658 | -0.0045871 | 0.017852 | -0.0090311 | -109.2301 | 9.2822 | -111.8879 | 9.2318 | 9.1857 | 9.1572 | -112.1918 | 0.010205 | -0.077479 | -112.0333 | 9.1408 | 9.1938 | 9.2748 | -112.1712 | 0.006115 | -0.10658 | 2.9677 | 0.31002 | 0.30391 | -0.1527 | -0.18114 | 0.026701 | -0.19761 | 112.2081 | 0.1646 | 0.1379 | -0.14457 | -0.063537 | 121.4297 | 121.3836 | 121.3551 | 121.4801 | -121.5301 | 121.3386 | 121.3917 | 121.4727 | 112.1204 | -121.5096
927.4844 | 121.6873 | -112.3123 | 9.2011 | 0.002213 | -0.035856 | 7.2612e-05 | 0.053449 | -0.0061599 | 0.050538 | -0.011751 | -0.0020083 | -0.001658 | -0.0052279 | 0.017852 | -0.0092447 | -109.3263 | 9.209 | -111.9886 | 9.1356 | 9.0895 | 9.0565 | -112.2925 | 0.005626 | -0.0729 | -112.134 | 9.0446 | 9.0931 | 9.1741 | -112.2628 | 0.019819 | -0.065401 | 2.986 | 0.32374 | 0.30392 | -0.11153 | -0.14455 | 0.049566 | -0.15643 | 112.3179 | 0.17831 | 0.12874 | -0.10797 | -0.026937 | 121.448 | 121.4018 | 121.3688 | 121.5213 | -121.4935 | 121.3569 | 121.4054 | 121.4864 | 112.2394 | -121.4638
929.2344 | 121.6644 | -112.4222 | 9.1324 | -0.02068 | -0.036284 | -0.00035479 | 0.053021 | -0.0059463 | 0.050111 | 0.00351 | -0.0020083 | -0.0018716 | -0.0045871 | 0.018066 | -0.0092447 | -109.4087 | 9.1082 | -112.0801 | 9.0532 | 9.0025 | 8.9695 | -112.3795 | 0.010205 | -0.077479 | -112.2164 | 8.9576 | 9.0061 | 9.0963 | -112.3635 | 0.042683 | -0.079147 | 3.0135 | 0.34204 | 0.29936 | -0.12986 | -0.16287 | 0.058695 | -0.17475 | 112.4324 | 0.20575 | 0.14706 | -0.1263 | -0.036108 | 121.4754 | 121.4247 | 121.3917 | 121.5304 | -121.5119 | 121.3798 | 121.4283 | 121.5185 | 112.3447 | -121.4959
930.9844 | 121.8109 | -112.2345 | 9.2331 | 0.002213 | -0.036284 | 0.00028641 | 0.053235 | -0.0057325 | 0.049897 | -0.011751 | -0.0017945 | -0.0014444 | -0.0048007 | 0.017852 | -0.0090311 | -109.4545 | 9.1128 | -112.0801 | 9.0532 | 8.9979 | 8.9741 | -112.3795 | 0.014784 | -0.068322 | -112.2164 | 8.9668 | 9.0061 | 9.0963 | -112.3589 | -0.145 | -0.17985 | 2.78 | 0.15436 | 0.29936 | -0.23515 | -0.259 | -0.12441 | -0.2663 | 112.2493 | 0.018069 | 0.14248 | -0.22701 | -0.13682 | 121.2877 | 121.2324 | 121.2086 | 121.3473 | -121.6126 | 121.2013 | 121.2406 | 121.3308 | 112.1662 | -121.592
932.6719 | 121.7468 | -111.5616 | 9.9792 | -0.005418 | -0.03607 | 7.2612e-05 | 0.053662 | -0.0059463 | 0.050111 | -0.011751 | -0.0020083 | -0.0014444 | -0.0045871 | 0.017639 | -0.0092447 | -108.5663 | 9.9873 | -111.2194 | 9.9094 | 9.8634 | 9.8257 | -111.5187 | 0.023941 | -0.063743 | -111.3602 | 9.8184 | 9.8623 | 9.9479 | -111.4981 | 0.042924 | -0.069851 | 2.9953 | 0.34216 | 0.29924 | -0.11589 | -0.15354 | 0.063495 | -0.16086 | 111.5855 | 0.20137 | 0.13788 | -0.11697 | -0.031351 | 121.471 | 121.4249 | 121.3873 | 121.5489 | -121.4979 | 121.38 | 121.4239 | 121.5095 | 111.4978 | -121.4773
934.4219 | 121.7834 | -111.2366 | 10.2722 | 0.002213 | -0.036498 | 7.2612e-05 | 0.053449 | -0.0059463 | 0.050324 | -0.011751 | -0.0017945 | -0.001658 | -0.0048007 | 0.018066 | -0.0094585 | -108.4014 | 10.2208 | -110.9951 | 10.1429 | 10.0969 | 10.0592 | -111.2943 | 0.014784 | -0.059164 | -111.1404 | 10.0427 | 10.0912 | 10.186 | -111.2691 | -0.05772 | -0.12932 | 2.8351 | 0.24149 | 0.29921 | -0.17533 | -0.213 | -0.032576 | -0.22948 | 111.2514 | 0.096141 | 0.12872 | -0.18101 | -0.086233 | 121.3795 | 121.3335 | 121.2958 | 121.4574 | -121.5665 | 121.2793 | 121.3278 | 121.4226 | 111.1774 | -121.5414
936.1719 | 121.7972 | -110.9894 | 10.5194 | 0.002213 | -0.036284 | -0.00035479 | 0.053235 | -0.0059463 | 0.050111 | 0.00351 | -0.0020083 | -0.001658 | -0.0045871 | 0.01828 | -0.0090311 | -108.1222 | 10.5185 | -110.7021 | 10.4405 | 10.3899 | 10.3568 | -110.9967 | 0.023941 | -0.063743 | -110.8382 | 10.3449 | 10.3888 | 10.4882 | -110.9761 | -0.007282 | -0.078919 | 2.8672 | 0.2873 | 0.29459 | -0.12947 | -0.16258 | 0.013276 | -0.17449 | 111.0133 | 0.15114 | 0.13787 | -0.13059 | -0.031237 | 121.4299 | 121.3793 | 121.3462 | 121.5078 | -121.5161 | 121.3343 | 121.3782 | 121.4776 | 110.9256 | -121.4955
937.8594 | 121.7422 | -111.6028 | 9.9243 | -0.005418 | -0.03607 | -0.00014099 | 0.053235 | -0.0063735 | 0.049897 | -0.0041205 | -0.0017945 | -0.0014444 | -0.0045871 | 0.018066 | -0.0094585 | -108.5846 | 10.0194 | -111.2332 | 9.8957 | 9.8496 | 9.8211 | -111.5416 | 0.010205 | -0.068322 | -111.3785 | 9.8092 | 9.8531 | 9.9433 | -111.5256 | 0.061229 | -0.028654 | 3.0182 | 0.36963 | 0.3084 | -0.07469 | -0.10318 | 0.077221 | -0.11508 | 111.613 | 0.22426 | 0.14704 | -0.071193 | 0.019002 | 121.4984 | 121.4524 | 121.4239 | 121.6222 | -121.4659 | 121.412 | 121.4559 | 121.5461 | 111.5345 | -121.4499
939.5938 | 121.6187 | -83.931 | 37.3215 | 0.002213 | -0.035856 | 0.00028641 | 0.053662 | -0.0053053 | 0.049897 | -0.011751 | -0.00094006 | -0.0012306 | -0.0043733 | 0.017639 | -0.0094585 | -81.3569 | 40.1649 | -81.3049 | 39.8841 | 39.7225 | 39.6919 | -81.4763 | 0.001048 | -0.022535 | -81.475 | 39.6381 | 39.7514 | 39.8141 | -81.461 | 2.4546 | 2.5626 | 2.5741 | 2.626 | 0.1714 | 2.4011 | 2.3705 | 2.4699 | 2.3167 | 83.932 | 2.456 | -0.013922 | 2.4299 | 2.4926 | 123.8151 | 123.6535 | 123.6229 | 124.0959 | -118.7978 | 123.5691 | 123.6824 | 123.7451 | 83.9084 | -118.7825
941.3438 | 121.582 | -96.7163 | 24.5087 | -0.005418 | -0.03607 | 0.00050001 | 0.053235 | -0.0059463 | 0.049897 | -0.011751 | -0.0013673 | -0.0014444 | -0.0048007 | 0.017425 | -0.0092447 | -95.6323 | 25.5821 | -95.635 | 25.3569 | 25.2485 | 25.2098 | -95.845 | 0.019362 | -0.050007 | -95.7514 | 25.2021 | 25.2784 | 25.3503 | -95.8294 | 0.87131 | 0.84821 | 1.084 | 1.0814 | 0.21005 | 0.73988 | 0.70115 | 0.88693 | 0.69347 | 96.7357 | 0.96492 | 0.077989 | 0.76977 | 0.84165 | 122.0732 | 121.9649 | 121.9261 | 122.2984 | -120.3537 | 121.9184 | 121.9947 | 122.0666 | 96.6663 | -120.338
943.0312 | 121.4722 | -113.9832 | 7.0404 | 0.002213 | -0.036284 | 7.2612e-05 | 0.053021 | -0.0061599 | 0.050324 | -0.011751 | -0.0011537 | -0.0020852 | -0.0048007 | 0.017852 | -0.0094585 | -111.1485 | 7.1807 | -113.6505 | 7.112 | 7.0473 | 7.0282 | -113.9684 | -0.00811 | -0.10953 | -113.7961 | 7.0164 | 7.0556 | 7.1412 | -113.9386 | 0.01477 | 0.071597 | 2.8347 | 0.33267 | 0.3179 | 0.006919 | -0.012221 | 0.044556 | -0.024055 | 113.975 | 0.18707 | 0.14252 | 0.015192 | 0.10081 | 121.0952 | 121.0305 | 121.0113 | 121.1638 | -121.0088 | 120.9995 | 121.0388 | 121.1244 | 113.8736 | -120.979
944.7812 | 121.4172 | -114.8666 | 6.1981 | 0.002213 | -0.036284 | 0.00028641 | 0.053021 | -0.0061599 | 0.049897 | -0.0041205 | -0.0013673 | -0.0018716 | -0.0048007 | 0.017852 | -0.0092447 | -111.8902 | 6.2191 | -114.5433 | 6.1505 | 6.0995 | 6.0804 | -114.8521 | 0.001048 | -0.091215 | -114.6844 | 6.064 | 6.1078 | 6.1889 | -114.8269 | 0.014521 | -0.04758 | 2.9765 | 0.32338 | 0.30886 | -0.098634 | -0.11771 | 0.039749 | -0.1341 | 114.8677 | 0.18229 | 0.14254 | -0.090294 | -0.009256 | 121.0172 | 120.9661 | 120.9471 | 121.0858 | -121.0502 | 120.9307 | 120.9745 | 121.0555 | 114.7754 | -121.025
946.5312 | 121.2296 | -115.2283 | 5.8319 | 0.009844 | -0.036498 | -0.00014099 | 0.053021 | -0.0061599 | 0.050111 | -0.0041205 | -0.0011537 | -0.001658 | -0.0050143 | 0.017852 | -0.0094585 | -112.1923 | 5.8254 | -114.882 | 5.7614 | 5.7194 | 5.6912 | -115.1955 | 0.014784 | -0.086637 | -115.0278 | 5.6794 | 5.7278 | 5.8043 | -115.1795 | 0.032735 | -0.070532 | 3.0359 | 0.34623 | 0.31349 | -0.11247 | -0.14068 | 0.048813 | -0.15248 | 115.2431 | 0.20052 | 0.1517 | -0.10411 | -0.027648 | 120.9896 | 120.9477 | 120.9195 | 121.0537 | -121.0274 | 120.9077 | 120.9561 | 121.0325 | 115.1416 | -121.0114
948.2344 | 121.2433 | -115.3839 | 5.658 | -0.005418 | -0.036284 | 7.2612e-05 | 0.053021 | -0.0061599 | 0.049897 | -0.0041205 | -0.00094006 | -0.0018716 | -0.0052279 | 0.018066 | -0.0092447 | -112.3984 | 5.5873 | -115.0926 | 5.5187 | 5.4768 | 5.4577 | -115.4062 | 0.014784 | -0.082058 | -115.243 | 5.4368 | 5.4851 | 5.5708 | -115.3947 | -0.022255 | -0.13924 | 2.9855 | 0.29126 | 0.31352 | -0.18121 | -0.20024 | -0.010751 | -0.22119 | 115.3987 | 0.14096 | 0.15171 | -0.17282 | -0.087206 | 120.9026 | 120.8607 | 120.8416 | 120.9712 | -121.0641 | 120.8207 | 120.869 | 120.9547 | 115.3019 | -121.0526
949.9844 | 121.2524 | -115.5167 | 5.4611 | -0.013049 | -0.036711 | 7.2612e-05 | 0.052594 | -0.0061599 | 0.049897 | -0.011751 | -0.0015809 | -0.001658 | -0.0050143 | 0.018066 | -0.0094585 | -112.5632 | 5.4591 | -115.1934 | 5.4043 | 5.3485 | 5.3249 | -115.5069 | 0.005626 | -0.077479 | -115.3391 | 5.3132 | 5.3615 | 5.4471 | -115.4954 | 0.00976 | -0.056858 | 2.9535 | 0.32329 | 0.31353 | -0.11258 | -0.13618 | 0.021267 | -0.14797 | 115.5223 | 0.17755 | 0.15629 | -0.099607 | -0.013991 | 120.9209 | 120.8652 | 120.8416 | 120.9758 | -120.968 | 120.8298 | 120.8782 | 120.9638 | 115.4392 | -120.9565
951.6875 | 121.1609 | -115.7181 | 5.3009 | -0.005418 | -0.036284 | -0.00035479 | 0.053235 | -0.0057325 | 0.050324 | -0.011751 | -0.0015809 | -0.0018716 | -0.0045871 | 0.01828 | -0.0092447 | -112.6914 | 5.2897 | -115.3353 | 5.2257 | 5.1837 | 5.1555 | -115.658 | 0.001048 | -0.082058 | -115.481 | 5.1392 | 5.1875 | 5.2777 | -115.6373 | 0.060072 | -0.075197 | 3.0267 | 0.38278 | 0.32271 | -0.1172 | -0.14537 | 0.080739 | -0.16174 | 115.7191 | 0.23703 | 0.15629 | -0.11338 | -0.023181 | 120.9438 | 120.9018 | 120.8736 | 121.0078 | -120.9589 | 120.8572 | 120.9056 | 120.9958 | 115.636 | -120.9382
953.4375 | 121.1563 | -115.7318 | 5.2048 | -0.005418 | -0.036498 | -0.00014099 | 0.052808 | -0.0061599 | 0.050111 | 0.00351 | -0.0013673 | -0.0018716 | -0.0050143 | 0.018066 | -0.0094585 | -112.7234 | 5.1981 | -115.404 | 5.1296 | 5.0875 | 5.064 | -115.7221 | 0.005626 | -0.082058 | -115.5497 | 5.0522 | 5.096 | 5.1861 | -115.7152 | 0.0097 | -0.075213 | 3.0084 | 0.32784 | 0.31814 | -0.11723 | -0.14081 | 0.016633 | -0.1526 | 115.7374 | 0.18208 | 0.16545 | -0.10882 | -0.018623 | 120.8614 | 120.8194 | 120.7958 | 120.9299 | -120.9269 | 120.784 | 120.8278 | 120.918 | 115.6498 | -120.92
955.1875 | 121.1792 | -115.773 | 5.0858 | -0.005418 | -0.036925 | -0.00035479 | 0.053021 | -0.0059463 | 0.049897 | -0.011751 | -0.0011537 | -0.0018716 | -0.0052279 | 0.017639 | -0.0096721 | -112.8608 | 5.0974 | -115.4864 | 5.038 | 4.996 | 4.9678 | -115.8091 | 0.010205 | -0.0729 | -115.6367 | 4.9469 | 4.9952 | 5.0763 | -115.793 | -0.036102 | -0.047762 | 2.9122 | 0.28663 | 0.32273 | -0.089788 | -0.11794 | -0.020009 | -0.13888 | 115.7832 | 0.13629 | 0.1563 | -0.090528 | -0.00949 | 120.811 | 120.769 | 120.7408 | 120.8704 | -120.8949 | 120.7199 | 120.7682 | 120.8493 | 115.7001 | -120.8788
956.9531 | 121.1838 | -115.7776 | 5.0812 | -0.013049 | -0.036498 | -0.00014099 | 0.053021 | -0.0059463 | 0.049683 | -0.027012 | -0.0011537 | -0.0020852 | -0.0045871 | 0.018066 | -0.0092447 | -112.8287 | 5.0928 | -115.4589 | 5.0151 | 4.9868 | 4.9587 | -115.7908 | 0.023941 | -0.0729 | -115.6184 | 4.9469 | 4.9906 | 5.0671 | -115.7747 | -0.013208 | -0.066077 | 2.9488 | 0.31868 | 0.33189 | -0.094369 | -0.12252 | 0.002884 | -0.13431 | 115.8015 | 0.15918 | 0.1563 | -0.09053 | -0.014071 | 120.7927 | 120.7644 | 120.7362 | 120.8704 | -120.872 | 120.7245 | 120.7682 | 120.8447 | 115.7047 | -120.8559
958.6562 | 121.0281 | -115.892 | 5.0262 | 0.002213 | -0.036711 | 7.2612e-05 | 0.053021 | -0.0057325 | 0.049897 | 0.00351 | -0.0011537 | -0.0018716 | -0.0045871 | 0.017852 | -0.0092447 | -112.8883 | 4.9783 | -115.5413 | 4.9144 | 4.8723 | 4.8579 | -115.8732 | 0.014784 | -0.0729 | -115.6917 | 4.837 | 4.8899 | 4.971 | -115.8571 | 0.018812 | -0.11187 | 3.0038 | 0.35071 | 0.3319 | -0.15391 | -0.16832 | 0.034906 | -0.18926 | 115.9068 | 0.20036 | 0.16545 | -0.13633 | -0.055289 | 120.8064 | 120.7644 | 120.75 | 120.8704 | -120.8995 | 120.729 | 120.7819 | 120.863 | 115.8191 | -120.8834
960.4219 | 121.0327 | -115.8188 | 5.0674 | 0.002213 | 0.014784 | 0.046013 | 0.052594 | 0.090843 | 0.04947 | -0.0041205 | -0.00072626 | -0.0018716 | -0.0048007 | 0.01828 | -0.0092447 | -112.8425 | 4.9921 | 4.8904 | 4.951 | 4.8998 | 4.8762 | -115.8 | 0.014784 | -0.077479 | -115.6413 | 4.8782 | 4.9174 | 4.9984 | -115.7839 | 0.018833 | -0.11644 | 2.9763 | 120.7091 | 120.6903 | -0.16764 | -0.1912 | 0.034925 | -0.18925 | 115.8336 | 0.17748 | 0.14256 | -0.15005 | -0.069017 | 120.7698 | 120.7186 | 120.695 | 120.8109 | -120.8674 | 120.697 | 120.7362 | 120.8172 | 115.7413 | -120.8513
962.1094 | 120.9915 | -115.9103 | 4.9347 | -0.005418 | 0.048758 | 0.012039 | 0.052808 | 0.09063 | 0.049683 | -0.0041205 | -0.00094006 | -0.0018716 | -0.0048007 | 0.017852 | -0.0090311 | -112.8883 | 4.8776 | 4.8217 | 4.8411 | 4.7899 | 4.7664 | -115.887 | 0.019362 | -0.063743 | -115.7237 | 4.7637 | 4.8121 | 4.8885 | -115.88 | 0.023385 | -0.093571 | 3.0221 | 120.732 | 120.7086 | -0.14478 | -0.16834 | 0.030322 | -0.17096 | 115.9297 | 0.18662 | 0.1563 | -0.12261 | -0.046151 | 120.7515 | 120.7003 | 120.6767 | 120.788 | -120.8216 | 120.6741 | 120.7224 | 120.7989 | 115.8466 | -120.8147
963.8594 | 120.9686 | -115.9103 | 4.9393 | 0.002213 | 0.03316 | 0.028278 | 0.052594 | 0.09063 | 0.049897 | -0.0041205 | -0.0013673 | -0.0018716 | -0.0050143 | 0.01828 | -0.0092447 | -112.8562 | 4.8685 | 4.8125 | 4.8228 | 4.7762 | 4.7572 | -115.8824 | 0.023941 | -0.077479 | -115.7146 | 4.7408 | 4.7983 | 4.8794 | -115.8754 | 0.027964 | -0.11646 | 3.0541 | 120.7229 | 120.6949 | -0.16309 | -0.18207 | 0.034901 | -0.19843 | 115.9343 | 0.19578 | 0.16088 | -0.14092 | -0.059886 | 120.7331 | 120.6865 | 120.6675 | 120.7788 | -120.8216 | 120.6512 | 120.7087 | 120.7897 | 115.8329 | -120.8147
965.5469 | 120.9503 | -115.7776 | 5.0354 | -0.013049 | 0.060937 | -0.00035479 | 0.052594 | 0.090416 | 0.049897 | -0.0041205 | -0.0011537 | -0.0018716 | -0.0050143 | 0.017852 | -0.0092447 | -112.7051 | 4.9783 | 4.927 | 4.9418 | 4.8998 | 4.8671 | -115.7404 | 0.019362 | -0.059164 | -115.5726 | 4.869 | 4.9174 | 4.9938 | -115.7381 | 0.03716 | -0.093554 | 3.0725 | 120.7046 | 120.6674 | -0.13559 | -0.16832 | 0.039514 | -0.16636 | 115.7969 | 0.20497 | 0.16545 | -0.11801 | -0.041551 | 120.7194 | 120.6774 | 120.6447 | 120.7559 | -120.7758 | 120.6466 | 120.695 | 120.7714 | 115.7184 | -120.7735
967.2969 | 121.0236 | -115.8508 | 4.8706 | -0.013049 | 0.060724 | -0.00035479 | 0.05238 | 0.090202 | 0.049683 | -0.011751 | -0.00094006 | -0.001658 | -0.0050143 | 0.018066 | -0.0092447 | -112.8791 | 4.8318 | 4.7851 | 4.7999 | 4.7487 | 4.7251 | -115.8641 | 0.023941 | -0.068322 | -115.71 | 4.7225 | 4.7663 | 4.8473 | -115.8663 | -0.013229 | -0.070689 | 2.9717 | 120.6359 | 120.6491 | -0.1219 | -0.14546 | -0.01545 | -0.14808 | 115.8748 | 0.14085 | 0.1563 | -0.10431 | -0.023271 | 120.6507 | 120.5995 | 120.576 | 120.6827 | -120.7347 | 120.5734 | 120.6171 | 120.6982 | 115.7825 | -120.7369
969.0469 | 120.9686 | -115.8417 | 4.8294 | -0.013049 | 0.1244 | -0.00078199 | 0.05238 | 0.089775 | 0.11293 | -0.019381 | -0.0013673 | -0.0018716 | -0.0050143 | 0.018066 | -0.0094585 | -0.82764 | 4.7906 | 4.7347 | 4.7679 | 4.7121 | 4.6885 | -115.8641 | 0.019362 | -0.068322 | -115.7054 | 4.6905 | 4.7434 | 4.829 | -115.8754 | -0.022384 | -0.06154 | 115.014 | 120.5764 | 120.5987 | -0.11733 | -0.14089 | -0.033763 | -0.13893 | 115.861 | 0.13627 | 0.17003 | -0.086004 | -0.000388 | 120.6095 | 120.5537 | 120.5302 | 120.6323 | -120.6935 | 120.5321 | 120.5851 | 120.6707 | 115.7734 | -120.7048
970.8125 | 120.932 | -115.8417 | 4.8614 | -0.005418 | 0.12696 | -0.00056839 | 0.052167 | 0.089561 | 0.11528 | -0.011751 | -0.00094006 | -0.0020852 | -0.0048007 | 0.018066 | -0.0092447 | 4.7717 | 4.7769 | 4.7301 | 4.7541 | 4.7167 | 4.6839 | -115.8503 | 0.023941 | -0.068322 | -115.6825 | 4.6859 | 4.7251 | 4.8199 | -115.8571 | -0.008647 | -0.10732 | 120.6134 | 120.5718 | 120.5804 | -0.1448 | -0.17751 | -0.015448 | -0.17555 | 115.8656 | 0.15916 | 0.17461 | -0.13636 | -0.041588 | 120.5958 | 120.5583 | 120.5256 | 120.6186 | -120.7118 | 120.5276 | 120.5668 | 120.6615 | 115.7734 | -120.7186
972.5 | 120.8771 | -115.8508 | 4.8843 | -0.005418 | 0.12632 | -0.00078199 | 0.05238 | 0.089775 | 0.11485 | -0.0041205 | -0.0011537 | -0.0018716 | -0.0045871 | 0.017852 | -0.0094585 | 4.7717 | 4.7815 | 4.7301 | 4.745 | 4.7029 | 4.6885 | -115.832 | 0.02852 | -0.063743 | -115.6688 | 4.6813 | 4.7342 | 4.8107 | -115.8388 | 0.018824 | -0.13936 | 120.6226 | 120.5809 | 120.5621 | -0.18142 | -0.19582 | 0.012022 | -0.20302 | 115.8794 | 0.18206 | 0.17003 | -0.15009 | -0.073633 | 120.5958 | 120.5537 | 120.5393 | 120.6323 | -120.7163 | 120.5321 | 120.5851 | 120.6615 | 115.7871 | -120.7231
974.25 | 120.8954 | -115.8829 | 4.8065 | 0.009844 | 0.12632 | -0.00035479 | 0.05238 | 0.089348 | 0.11485 | 0.00351 | -0.0011537 | -0.0018716 | -0.0050143 | 0.017852 | -0.0094585 | 4.6939 | 4.6899 | 4.6431 | 4.6626 | 4.6297 | 4.6061 | -115.9007 | 0.019362 | -0.068322 | -115.7375 | 4.5989 | 4.6473 | 4.7237 | -115.8983 | -0.017816 | -0.14396 | 120.5768 | 120.526 | 120.5438 | -0.17687 | -0.20042 | -0.015458 | -0.20761 | 115.9022 | 0.14542 | 0.16088 | -0.15927 | -0.082808 | 120.5454 | 120.5125 | 120.489 | 120.5728 | -120.7072 | 120.4818 | 120.5301 | 120.6066 | 115.8146 | -120.7049
976 | 120.9412 | -115.8096 | 4.8203 | 0.002213 | 0.12589 | -0.00035479 | 0.05238 | 0.08892 | 0.11464 | -0.011751 | -0.0011537 | -0.0018716 | -0.0050143 | 0.018493 | -0.0092447 | 4.7488 | 4.754 | 4.7072 | 4.7221 | 4.68 | 4.6519 | -115.8183 | 0.014784 | -0.068322 | -115.6596 | 4.6584 | 4.7068 | 4.7924 | -115.8205 | -0.008639 | -0.098168 | 120.5585 | 120.5169 | 120.5255 | -0.14023 | -0.16836 | -0.010861 | -0.16183 | 115.8244 | 0.15001 | 0.16088 | -0.11348 | -0.027861 | 120.5317 | 120.4897 | 120.4615 | 120.5636 | -120.6385 | 120.4681 | 120.5164 | 120.602 | 115.7413 | -120.6407
977.7656 | 120.8633 | -115.7043 | 4.9347 | -0.005418 | 0.12611 | -0.00056839 | 0.052167 | 0.089134 | 0.11485 | -0.011751 | -0.0013673 | -0.0020852 | -0.0050143 | 0.017852 | -0.0092447 | 4.7809 | 4.7723 | 4.721 | 4.7267 | 4.6938 | 4.6748 | -115.7908 | 0.023941 | -0.068322 | -115.623 | 4.6767 | 4.7297 | 4.8107 | -115.7884 | -0.08645 | -0.20803 | 120.4852 | 120.4253 | 120.5118 | -0.24094 | -0.25991 | -0.084095 | -0.25795 | 115.7283 | 0.081358 | 0.16545 | -0.20503 | -0.12399 | 120.431 | 120.3981 | 120.3791 | 120.4767 | -120.7255 | 120.3811 | 120.434 | 120.5151 | 115.636 | -120.7231
979.5312 | 120.9045 | -115.8691 | 4.6921 | -0.005418 | 0.12547 | -0.00056839 | 0.051953 | 0.08892 | 0.11485 | -0.019381 | -0.0013673 | -0.001658 | -0.0048007 | 0.018066 | -0.0094585 | 4.6435 | 4.6441 | 4.6019 | 4.6168 | 4.5655 | 4.5557 | -115.8915 | 0.023941 | -0.068322 | -115.7329 | 4.5485 | 4.6015 | 4.6825 | -115.8938 | -0.022391 | -0.075298 | 120.5127 | 120.4711 | 120.4935 | -0.12653 | -0.13634 | -0.024612 | -0.14354 | 115.8931 | 0.13626 | 0.16088 | -0.090612 | -0.009574 | 120.4859 | 120.4347 | 120.4249 | 120.5132 | -120.5836 | 120.4177 | 120.4706 | 120.5516 | 115.8008 | -120.5858
981.2188 | 120.8954 | -115.7501 | 4.7836 | -0.013049 | 0.12504 | -0.00056839 | 0.05238 | 0.088707 | 0.11442 | -0.0041205 | -0.0011537 | -0.001658 | -0.0048007 | 0.018493 | -0.0094585 | 4.7534 | 4.7403 | 4.6981 | 4.7221 | 4.6754 | 4.6427 | -115.7771 | 0.023941 | -0.063743 | -115.6184 | 4.6447 | 4.6976 | 4.7741 | -115.7701 | -0.026937 | -0.061547 | 120.5035 | 120.4482 | 120.4751 | -0.10819 | -0.1409 | -0.020003 | -0.13894 | 115.7741 | 0.13171 | 0.15172 | -0.086013 | -0.009554 | 120.4722 | 120.4256 | 120.3929 | 120.4904 | -120.5607 | 120.3948 | 120.4477 | 120.5242 | 115.6864 | -120.5538
982.9062 | 120.7352 | -115.7867 | 4.8386 | -0.013049 | 0.12525 | -0.00035479 | 0.052167 | 0.088707 | 0.11485 | -0.0041205 | -0.0011537 | -0.0018716 | -0.0045871 | 0.01828 | -0.0092447 | 4.7397 | 4.7403 | 4.6935 | 4.7038 | 4.6754 | 4.6382 | -115.7633 | 0.02852 | -0.063743 | -115.6047 | 4.6447 | 4.6885 | 4.7649 | -115.7655 | 0.02342 | -0.13479 | 120.5264 | 120.4802 | 120.4568 | -0.16312 | -0.20041 | 0.021197 | -0.19387 | 115.8153 | 0.18207 | 0.16087 | -0.1501 | -0.073643 | 120.4905 | 120.4622 | 120.4249 | 120.527 | -120.6019 | 120.4314 | 120.4752 | 120.5517 | 115.723 | -120.6041
984.6406 | 120.8496 | -115.7089 | 4.8111 | -0.005418 | 0.12483 | -0.00014099 | 0.052167 | 0.088493 | 0.11442 | -0.019381 | -0.0013673 | -0.0014444 | -0.0048007 | 0.018066 | -0.0092447 | 4.7671 | 4.7586 | 4.7072 | 4.7312 | 4.6938 | 4.6656 | -115.713 | 0.023941 | -0.0729 | -115.5635 | 4.663 | 4.7159 | 4.797 | -115.7427 | -0.004031 | -0.079856 | 120.4761 | 120.4161 | 120.4202 | -0.11734 | -0.14547 | -0.033729 | -0.14809 | 115.7329 | 0.14546 | 0.17919 | -0.095165 | -0.014127 | 120.4402 | 120.4027 | 120.3745 | 120.4675 | -120.5241 | 120.3719 | 120.4249 | 120.5059 | 115.636 | -120.5537
986.4062 | 120.7123 | -115.9058 | 4.6692 | 0.002213 | 0.12483 | -0.00078199 | 0.052594 | 0.088493 | 0.114 | 0.00351 | -0.0011537 | -0.0018716 | -0.0050143 | 0.018707 | -0.0094585 | 4.6115 | 4.6075 | 4.5561 | 4.5756 | 4.5335 | 4.5054 | -115.8641 | 0.019362 | -0.068322 | -115.7054 | 4.5073 | 4.5603 | 4.6413 | -115.8617 | 0.041703 | -0.093614 | 120.5172 | 120.4619 | 120.4202 | -0.1357 | -0.16382 | 0.04406 | -0.16186 | 115.9251 | 0.20036 | 0.1563 | -0.10893 | -0.027893 | 120.4813 | 120.4393 | 120.4111 | 120.5132 | -120.5332 | 120.4131 | 120.466 | 120.5471 | 115.8374 | -120.5309
988.1562 | 120.8313 | -115.6769 | 4.7974 | 0.002213 | 0.1244 | -0.00035479 | 0.052167 | 0.088279 | 0.114 | -0.011751 | -0.0011537 | -0.0018716 | -0.0045871 | 0.01828 | -0.0094585 | 4.7717 | 4.7723 | 4.7301 | 4.745 | 4.6938 | 4.6748 | -115.6763 | 0.02852 | -0.059164 | -115.5177 | 4.6767 | 4.7251 | 4.8015 | -115.6831 | 0.000557 | -0.052388 | 120.4486 | 120.407 | 120.4064 | -0.10361 | -0.12258 | -0.006248 | -0.12062 | 115.7054 | 0.1592 | 0.16545 | -0.072275 | 0.004184 | 120.4219 | 120.3706 | 120.3517 | 120.4492 | -120.4737 | 120.3536 | 120.402 | 120.4784 | 115.6177 | -120.4805
989.8438 | 120.7077 | -115.8463 | 4.7012 | 0.002213 | 0.12461 | -0.00056839 | 0.052594 | 0.088066 | 0.11442 | -0.019381 | -0.0013673 | -0.0018716 | -0.0050143 | 0.017852 | -0.0094585 | 4.6344 | 4.6212 | 4.5744 | 4.603 | 4.5518 | 4.5237 | -115.8137 | 0.019362 | -0.068322 | -115.6505 | 4.5302 | 4.5786 | 4.655 | -115.8159 | 0.032561 | -0.098188 | 120.4806 | 120.4207 | 120.3881 | -0.14942 | -0.17754 | 0.030339 | -0.17101 | 115.8656 | 0.19579 | 0.16545 | -0.12266 | -0.046201 | 120.4493 | 120.3981 | 120.3699 | 120.4675 | -120.5149 | 120.3765 | 120.4248 | 120.5013 | 115.7779 | -120.5171
991.6094 | 120.6619 | -115.686 | 4.8706 | 0.009844 | 0.1244 | -0.00099579 | 0.052167 | 0.088066 | 0.114 | 0.00351 | -0.0013673 | -0.001658 | -0.0048007 | 0.018066 | -0.0092447 | 4.7534 | 4.7494 | 4.6981 | 4.7129 | 4.6709 | 4.6473 | -115.6763 | 0.023941 | -0.077479 | -115.5085 | 4.6493 | 4.7022 | 4.7787 | -115.6785 | 0.009712 | -0.15768 | 120.4394 | 120.3841 | 120.3744 | -0.19974 | -0.22329 | 0.007486 | -0.22134 | 115.71 | 0.17751 | 0.17003 | -0.16841 | -0.091951 | 120.399 | 120.3569 | 120.3333 | 120.4355 | -120.5469 | 120.3353 | 120.3882 | 120.4647 | 115.6086 | -120.5492
993.3594 | 120.7214 | -115.8691 | 4.6005 | 0.002213 | 0.12397 | -0.00035479 | 0.052167 | 0.088066 | 0.11421 | -0.011751 | -0.00094006 | -0.001658 | -0.0045871 | 0.018493 | -0.0094585 | 4.5291 | 4.5251 | 4.4691 | 4.4932 | 4.4511 | 4.4275 | -115.8778 | 0.02852 | -0.063743 | -115.7237 | 4.4341 | 4.4778 | 4.5589 | -115.8938 | -0.008655 | -0.10736 | 120.3982 | 120.3383 | 120.3469 | -0.14945 | -0.17299 | -0.024612 | -0.16645 | 115.8977 | 0.14542 | 0.17003 | -0.12268 | -0.041643 | 120.3623 | 120.3202 | 120.2967 | 120.3942 | -120.4783 | 120.3032 | 120.347 | 120.428 | 115.8054 | -120.4943
995.1094 | 120.7489 | -115.9744 | 4.4586 | 0.002213 | 0.12376 | -0.00035479 | 0.052167 | 0.087638 | 0.114 | -0.0041205 | -0.0011537 | -0.0018716 | -0.0050143 | 0.01828 | -0.0092447 | 4.4055 | 4.3969 | 4.3547 | 4.3741 | 4.3229 | 4.3039 | -115.9877 | 0.02852 | -0.077479 | -115.8245 | 4.3013 | 4.3542 | 4.4353 | -115.9945 | -0.013264 | -0.084492 | 120.3799 | 120.3291 | 120.3424 | -0.13575 | -0.1547 | -0.020061 | -0.15732 | 116.0029 | 0.14997 | 0.17004 | -0.1044 | -0.023359 | 120.3486 | 120.2973 | 120.2783 | 120.3713 | -120.4463 | 120.2757 | 120.3286 | 120.4097 | 115.8969 | -120.4531
996.8125 | 120.6619 | -116.0202 | 4.4403 | -0.013049 | 0.12333 | -0.00056839 | 0.052167 | 0.087425 | 0.114 | 0.00351 | -0.0011537 | -0.002299 | -0.0048007 | 0.018493 | -0.0092447 | 4.378 | 4.3786 | 4.3226 | 4.3421 | 4.2954 | 4.2719 | -116.0014 | 0.023941 | -0.068322 | -115.8382 | 4.2738 | 4.3313 | 4.4169 | -116.0036 | 0.018776 | -0.098231 | 120.3982 | 120.3428 | 120.3241 | -0.14492 | -0.16844 | 0.016558 | -0.16648 | 116.0441 | 0.18202 | 0.16546 | -0.10898 | -0.023363 | 120.3623 | 120.3156 | 120.2921 | 120.3988 | -120.4417 | 120.294 | 120.3515 | 120.4371 | 115.9519 | -120.444
998.5625 | 120.5841 | -116.0294 | 4.4083 | 0.002213 | 0.12333 | -0.00035479 | 0.052167 | 0.087425 | 0.11378 | -0.0041205 | -0.0011537 | -0.0020852 | -0.0052279 | 0.01828 | -0.0094585 | 4.5337 | 4.5388 | 4.4783 | 4.4932 | 4.4511 | 4.4321 | -115.8274 | 0.019362 | -0.0729 | -115.6505 | 4.4295 | 4.487 | 4.5589 | -115.8251 | 0.20193 | 0.0849 | 120.563 | 120.5077 | 120.3057 | 0.04281 | 0.023853 | 0.20429 | 0.021236 | 116.0487 | 0.3789 | 0.17461 | 0.078737 | 0.15062 | 120.5225 | 120.4804 | 120.4615 | 120.5682 | -120.2357 | 120.4589 | 120.5164 | 120.5882 | 115.9565 | -120.2333
1000.25 | 120.5795 | -115.8829 | 4.5776 | -0.005418 | 0.12312 | -0.00078199 | 0.051953 | 0.087425 | 0.11378 | -0.0041205 | -0.0011537 | -0.0018716 | -0.0050143 | 0.018707 | -0.0094585 | 4.5291 | 4.5159 | 4.4737 | 4.4932 | 4.4419 | 4.4184 | -115.7679 | 0.019362 | -0.068322 | -115.655 | 4.4249 | 4.4687 | 4.5543 | -115.8205 | 0.11497 | -0.084473 | 120.4119 | 120.3566 | 120.2416 | -0.13572 | -0.15926 | 0.062382 | -0.15272 | 115.9022 | 0.22783 | 0.16545 | -0.10895 | -0.023334 | 120.376 | 120.3248 | 120.3013 | 120.3988 | -120.3455 | 120.3078 | 120.3516 | 120.4372 | 115.8146 | -120.3981
1002.0156 | 120.6207 | -115.9607 | 4.4632 | 0.002213 | 0.12312 | -0.00056839 | 0.052167 | 0.087211 | 0.114 | -0.011751 | -0.0011537 | -0.002299 | -0.0048007 | 0.018707 | -0.0096721 | 4.3826 | 4.3786 | 4.3272 | 4.3512 | 4.3137 | 4.281 | -115.9511 | 0.023941 | -0.068322 | -115.7878 | 4.283 | 4.3313 | 4.4078 | -115.9533 | 0.009634 | -0.11196 | 120.3433 | 120.2879 | 120.2783 | -0.14949 | -0.18217 | 0.007415 | -0.18021 | 115.9846 | 0.17287 | 0.16546 | -0.13187 | -0.055408 | 120.3119 | 120.2744 | 120.2417 | 120.3392 | -120.4143 | 120.2437 | 120.292 | 120.3685 | 115.8924 | -120.4165
1003.7656 | 120.6848 | -115.9698 | 4.3808 | -0.005418 | 0.12269 | -0.00056839 | 0.052167 | 0.086997 | 0.11378 | -0.0041205 | -0.00094006 | -0.0020852 | -0.0045871 | 0.01828 | -0.0096721 | 4.3276 | 4.319 | 4.2723 | 4.2871 | 4.2496 | 4.2169 | -115.9923 | 0.023941 | -0.068322 | -115.8199 | 4.2235 | 4.2764 | 4.3574 | -115.9945 | -0.02242 | -0.093662 | 120.2975 | 120.2421 | 120.2646 | -0.1312 | -0.16388 | -0.024638 | -0.15733 | 115.9938 | 0.14998 | 0.17462 | -0.10441 | -0.023375 | 120.257 | 120.2194 | 120.1868 | 120.2889 | -120.3731 | 120.1933 | 120.2462 | 120.3273 | 115.9015 | -120.3753
1005.4531 | 120.6573 | -115.8829 | 4.4449 | -0.005418 | 0.12077 | 0.001141 | 0.05238 | 0.086997 | 0.11357 | -0.011751 | -0.0013673 | -0.0025126 | -0.0050143 | 0.01828 | -0.0094585 | 4.4238 | 4.4106 | 4.373 | 4.3833 | 4.3458 | 4.3177 | -115.887 | 0.023941 | -0.068322 | -115.7191 | 4.315 | 4.3725 | 4.449 | -115.8938 | -0.00408 | -0.061602 | 120.3066 | 120.2559 | 120.26 | -0.099127 | -0.12723 | -0.010879 | -0.12985 | 115.9068 | 0.16373 | 0.17461 | -0.072349 | 0.00411 | 120.2662 | 120.2286 | 120.2005 | 120.2935 | -120.3318 | 120.1979 | 120.2554 | 120.3319 | 115.8146 | -120.3386
1007.2188 | 120.5612 | -115.8234 | 4.5319 | -0.02068 | 0.044271 | 0.076997 | 0.052167 | 0.086356 | 0.11357 | -0.0041205 | -0.0013673 | -0.0018716 | -0.0048007 | 0.01828 | -0.0094585 | 4.4787 | 4.4747 | 4.4279 | 4.4291 | 4.3824 | 4.3497 | -115.832 | 0.014784 | -0.063743 | -115.6688 | 4.3608 | 4.4 | 4.4856 | -115.8342 | -0.008642 | -0.10279 | 120.3021 | 120.2513 | 120.26 | -0.14947 | -0.18216 | -0.010865 | -0.17104 | 115.8381 | 0.15459 | 0.16545 | -0.13185 | -0.046236 | 120.2524 | 120.2058 | 120.1731 | 120.2981 | -120.3639 | 120.1842 | 120.2234 | 120.309 | 115.7596 | -120.3661
1008.9688 | 120.52 | -115.8966 | 4.4861 | 0.002213 | 0.063074 | 0.058407 | 0.052167 | 0.086997 | 0.11378 | -0.0041205 | -0.0011537 | -0.0018716 | -0.0048007 | 0.018707 | -0.0092447 | 4.4146 | 4.406 | 4.3638 | 4.3558 | 4.3183 | 4.2902 | -115.8824 | 0.02852 | -0.068322 | -115.7191 | 4.2967 | 4.3451 | 4.4261 | -115.8892 | 0.014231 | -0.13027 | 120.3112 | 120.2605 | 120.2462 | -0.1678 | -0.1959 | 0.007431 | -0.18936 | 115.9251 | 0.17747 | 0.17003 | -0.14102 | -0.059982 | 120.2524 | 120.2149 | 120.1868 | 120.3026 | -120.3685 | 120.1933 | 120.2417 | 120.3227 | 115.8283 | -120.3753
1010.6562 | 120.5063 | -115.947 | 4.422 | -0.013049 | 0.12226 | -0.00078199 | 0.05238 | 0.08657 | 0.11357 | -0.019381 | -0.0015809 | -0.001658 | -0.0052279 | 0.01828 | -0.0096721 | 4.3276 | 4.3328 | 4.2814 | 4.2917 | 4.2496 | 4.2307 | -115.8824 | 0.02852 | -0.068322 | -115.7695 | 4.228 | 4.2672 | 4.3528 | -115.9441 | 0.064585 | -0.13028 | 120.2746 | 120.2284 | 120.1638 | -0.1724 | -0.19134 | 0.00284 | -0.19395 | 115.9755 | 0.17745 | 0.17461 | -0.15477 | -0.069153 | 120.2387 | 120.1966 | 120.1776 | 120.2797 | -120.3044 | 120.175 | 120.2142 | 120.2998 | 115.8786 | -120.3661
1012.4062 | 120.6116 | -115.9744 | 4.2938 | -0.013049 | 0.12183 | -0.00056839 | 0.052167 | 0.08657 | 0.11335 | -0.019381 | -0.00094006 | -0.0020852 | -0.0050143 | 0.018493 | -0.0098857 | 4.2452 | 4.232 | 4.1807 | 4.2047 | 4.158 | 4.1345 | -115.9602 | 0.02852 | -0.068322 | -115.8428 | 4.1456 | 4.1848 | 4.2659 | -116.022 | 0.01421 | -0.089098 | 120.2196 | 120.1551 | 120.1409 | -0.1358 | -0.15932 | -0.047534 | -0.14819 | 116.0029 | 0.13166 | 0.17919 | -0.10901 | -0.027972 | 120.1792 | 120.1324 | 120.1089 | 120.2065 | -120.254 | 120.1201 | 120.1592 | 120.2403 | 115.9061 | -120.3158
1014.1562 | 120.5933 | -115.9287 | 4.3213 | -0.005418 | 0.12183 | -0.00078199 | 0.05238 | 0.08657 | 0.11314 | -0.0041205 | -0.0011537 | -0.001658 | -0.0050143 | 0.018493 | -0.0092447 | 4.2589 | 4.2504 | 4.1945 | 4.2139 | 4.1763 | 4.1437 | -115.9785 | 0.023941 | -0.063743 | -115.8153 | 4.1548 | 4.2077 | 4.2796 | -115.9945 | -0.049882 | -0.10741 | 120.1876 | 120.1231 | 120.173 | -0.14495 | -0.17762 | -0.065837 | -0.1665 | 115.9526 | 0.11336 | 0.17919 | -0.11358 | -0.041702 | 120.1425 | 120.105 | 120.0723 | 120.179 | -120.2998 | 120.0834 | 120.1364 | 120.2082 | 115.8649 | -120.3158
1015.9062 | 120.4376 | -115.8279 | 4.4724 | -0.005418 | 0.04363 | 0.076783 | 0.051953 | 0.086356 | 0.11335 | -0.0041205 | -0.0013673 | -0.0020852 | -0.0050143 | 0.018066 | -0.0096721 | 4.4009 | 4.4014 | 4.3501 | 4.3467 | 4.3 | 4.2856 | -115.832 | 0.019362 | -0.063743 | -115.6688 | 4.283 | 4.3313 | 4.4124 | -115.8342 | -0.004064 | -0.12569 | 120.2288 | 120.1781 | 120.1821 | -0.17238 | -0.18675 | -0.006287 | -0.18936 | 115.8473 | 0.15917 | 0.16545 | -0.14102 | -0.059985 | 120.1746 | 120.1279 | 120.1135 | 120.2294 | -120.3044 | 120.1109 | 120.1593 | 120.2403 | 115.7642 | -120.3066
1017.5938 | 120.4788 | -115.9195 | 4.3671 | -0.013049 | 0.055168 | 0.065886 | 0.052167 | 0.086356 | 0.11314 | 0.00351 | -0.0011537 | -0.0018716 | -0.0052279 | 0.018493 | -0.0094585 | 4.3322 | 4.319 | 4.2723 | 4.2734 | 4.2313 | 4.2032 | -115.8595 | 0.023941 | -0.068322 | -115.742 | 4.2097 | 4.2581 | 4.3391 | -115.9029 | 0.060015 | -0.093664 | 120.2517 | 120.1918 | 120.1318 | -0.13578 | -0.16388 | 0.016584 | -0.15733 | 115.9434 | 0.17746 | 0.16088 | -0.10899 | -0.027956 | 120.1929 | 120.1508 | 120.1227 | 120.2385 | -120.2265 | 120.1292 | 120.1776 | 120.2586 | 115.8512 | -120.27
1019.3438 | 120.575 | -115.9058 | 4.303 | 0.002213 | 0.042989 | 0.077638 | 0.052167 | 0.086356 | 0.11357 | -0.0041205 | -0.0013673 | -0.0018716 | -0.0050143 | 0.018493 | -0.0094585 | 4.2818 | 4.2778 | 4.2265 | 4.223 | 4.1809 | 4.1574 | -115.8915 | 0.019362 | -0.068322 | -115.7695 | 4.1594 | 4.1985 | 4.2887 | -115.9395 | 0.01423 | -0.07994 | 120.1876 | 120.1323 | 120.118 | -0.12206 | -0.14558 | -0.03378 | -0.14361 | 115.9251 | 0.13625 | 0.17003 | -0.10443 | -0.014235 | 120.1288 | 120.0867 | 120.0632 | 120.1836 | -120.1945 | 120.0651 | 120.1043 | 120.1945 | 115.8374 | -120.2425
1021.0312 | 120.4193 | -115.86 | 4.4037 | -0.013049 | 0.042775 | 0.077638 | 0.052167 | 0.086356 | 0.11314 | -0.011751 | -0.00072626 | -0.001658 | -0.0050143 | 0.018707 | -0.0094585 | 4.3597 | 4.3419 | 4.2952 | 4.2963 | 4.2404 | 4.2261 | -115.8091 | 0.019362 | -0.063743 | -115.6734 | 4.2326 | 4.281 | 4.3574 | -115.8617 | 0.050873 | -0.10739 | 120.2197 | 120.1552 | 120.1043 | -0.16324 | -0.17761 | -0.001717 | -0.17106 | 115.8793 | 0.18663 | 0.18835 | -0.12272 | -0.046264 | 120.1563 | 120.1004 | 120.0861 | 120.2019 | -120.2128 | 120.0926 | 120.1409 | 120.2174 | 115.7962 | -120.2654
1022.7812 | 120.4468 | -115.8646 | 4.3533 | 0.002213 | 0.042348 | 0.077851 | 0.051953 | 0.085929 | 0.11335 | 0.01114 | -0.0011537 | -0.0020852 | -0.0050143 | 0.018493 | -0.0094585 | 4.3139 | 4.3053 | 4.2585 | 4.2642 | 4.2084 | 4.1895 | -115.832 | 0.019362 | -0.0729 | -115.71 | 4.2006 | 4.2398 | 4.3162 | -115.8846 | 0.032557 | -0.089088 | 120.1785 | 120.1231 | 120.0906 | -0.14494 | -0.16388 | -0.020033 | -0.15276 | 115.8839 | 0.15458 | 0.17461 | -0.11358 | -0.037117 | 120.1288 | 120.073 | 120.054 | 120.1699 | -120.1853 | 120.0651 | 120.1043 | 120.1808 | 115.7917 | -120.2379
1024.4688 | 120.3918 | -115.9332 | 4.3304 | 0.002213 | 0.042348 | 0.077851 | 0.051739 | 0.086143 | 0.11314 | -0.0041205 | -0.0013673 | -0.0018716 | -0.0048007 | 0.01828 | -0.0094585 | 4.2589 | 4.2504 | 4.2036 | 4.2001 | 4.1443 | 4.1299 | -115.8778 | 0.019362 | -0.068322 | -115.7558 | 4.1319 | 4.1757 | 4.2613 | -115.9395 | 0.055432 | -0.1303 | 120.1922 | 120.1368 | 120.0814 | -0.18616 | -0.20052 | -0.006314 | -0.19855 | 115.9526 | 0.17746 | 0.18377 | -0.15479 | -0.069172 | 120.1334 | 120.0775 | 120.0632 | 120.1836 | -120.2082 | 120.0651 | 120.1089 | 120.1945 | 115.8649 | -120.27
1026.2031 | 120.3873 | -115.8554 | 4.39 | -0.013049 | 0.042134 | 0.077638 | 0.052167 | 0.086356 | 0.11293 | -0.011751 | -0.0011537 | -0.0018716 | -0.0050143 | 0.018493 | -0.0094585 | 4.4329 | 4.4289 | 4.3822 | 4.3741 | 4.332 | 4.2993 | -115.6855 | 0.019362 | -0.063743 | -115.568 | 4.3059 | 4.3496 | 4.4398 | -115.7472 | 0.16993 | -0.015828 | 120.2883 | 120.2376 | 120.0676 | -0.057932 | -0.090617 | 0.10818 | -0.084073 | 115.8748 | 0.28736 | 0.17919 | -0.040311 | 0.049884 | 120.2295 | 120.1874 | 120.1547 | 120.2843 | -120.0754 | 120.1613 | 120.2051 | 120.2952 | 115.7917 | -120.1372
1027.9531 | 120.369 | -115.7639 | 4.4907 | -0.005418 | 0.042348 | 0.077638 | 0.05238 | 0.085715 | 0.11293 | 0.00351 | -0.00094006 | -0.0020852 | -0.0048007 | 0.018493 | -0.0094585 | 4.4467 | 4.4427 | 4.3959 | 4.3879 | 4.3412 | 4.3222 | -115.6672 | 0.023941 | -0.063743 | -115.5497 | 4.3288 | 4.3634 | 4.449 | -115.7289 | 0.09669 | -0.1028 | 120.2105 | 120.1598 | 120.0631 | -0.14948 | -0.16843 | 0.034939 | -0.16189 | 115.7878 | 0.21413 | 0.17919 | -0.12728 | -0.041667 | 120.1517 | 120.105 | 120.0861 | 120.2065 | -120.1578 | 120.0926 | 120.1272 | 120.2129 | 115.7001 | -120.2196
1029.7031 | 120.3964 | -115.7043 | 4.4815 | 0.002213 | 0.041921 | 0.077638 | 0.051739 | 0.085929 | 0.11293 | 0.00351 | -0.0013673 | -0.0020852 | -0.0050143 | 0.018493 | -0.0096721 | 4.5153 | 4.5205 | 4.4646 | 4.4657 | 4.4144 | 4.3909 | -115.6214 | 0.023941 | -0.0729 | -115.4582 | 4.3883 | 4.4412 | 4.5177 | -115.6236 | 0.08297 | -0.015812 | 120.2197 | 120.1689 | 120.0859 | -0.067064 | -0.090597 | 0.080743 | -0.093212 | 115.7283 | 0.24619 | 0.16545 | -0.040291 | 0.036168 | 120.17 | 120.1188 | 120.0953 | 120.2248 | -120.1029 | 120.0926 | 120.1456 | 120.222 | 115.6314 | -120.1051
1031.3906 | 120.3232 | -115.892 | 4.3167 | 0.009844 | 0.042134 | 0.07721 | 0.05238 | 0.085502 | 0.11271 | -0.0041205 | -0.00094006 | -0.0014444 | -0.0052279 | 0.018707 | -0.0096721 | 4.3643 | 4.3557 | 4.3135 | 4.3192 | 4.2588 | 4.2444 | -115.7404 | 0.019362 | -0.0729 | -115.5772 | 4.2372 | 4.2901 | 4.3666 | -115.761 | 0.1516 | 0.002474 | 120.2563 | 120.2055 | 120.0539 | -0.057952 | -0.072317 | 0.13106 | -0.079508 | 115.9114 | 0.31483 | 0.18377 | -0.02659 | 0.049869 | 120.2112 | 120.1508 | 120.1364 | 120.2477 | -120.0571 | 120.1292 | 120.1821 | 120.2586 | 115.8191 | -120.0777
1033.1406 | 120.401 | -115.6586 | 4.4724 | -0.005418 | 0.042348 | 0.07721 | 0.052167 | 0.085929 | 0.11271 | -0.011751 | -0.0011537 | -0.0018716 | -0.0052279 | 0.01828 | -0.0096721 | 4.4741 | 4.4747 | 4.4234 | 4.4291 | 4.3687 | 4.3497 | -115.6488 | 0.02852 | -0.068322 | -115.4765 | 4.3471 | 4.4 | 4.4765 | -115.6465 | 0.00972 | -0.043285 | 120.1327 | 120.0819 | 120.0722 | -0.1037 | -0.12265 | 0.012072 | -0.12526 | 115.6871 | 0.1821 | 0.17003 | -0.072343 | 0.004116 | 120.0876 | 120.0272 | 120.0083 | 120.1333 | -120.1212 | 120.0057 | 120.0586 | 120.135 | 115.5902 | -120.1188
1034.8906 | 120.401 | -115.741 | 4.4128 | -0.005418 | 0.041921 | 0.077424 | 0.052167 | 0.085288 | 0.11271 | -0.019381 | -0.0011537 | -0.0020852 | -0.0048007 | 0.018707 | -0.0094585 | 4.4055 | 4.4014 | 4.3501 | 4.3512 | 4.3045 | 4.2764 | -115.7084 | 0.023941 | -0.0729 | -115.5314 | 4.2876 | 4.3267 | 4.4032 | -115.7198 | 0.032591 | -0.061608 | 120.1464 | 120.0911 | 120.0585 | -0.10829 | -0.1364 | 0.021209 | -0.12528 | 115.7649 | 0.20955 | 0.18834 | -0.086092 | -0.009633 | 120.0922 | 120.0455 | 120.0174 | 120.1424 | -120.1212 | 120.0285 | 120.0677 | 120.1442 | 115.6681 | -120.1326
1036.5938 | 120.3323 | -115.6219 | 4.5044 | -0.005418 | 0.041921 | 0.07721 | 0.051953 | 0.085502 | 0.1125 | -0.011751 | -0.0011537 | -0.0018716 | -0.0050143 | 0.018707 | -0.0098857 | 4.5153 | 4.5068 | 4.4508 | 4.452 | 4.4099 | 4.3818 | -115.571 | 0.019362 | -0.0729 | -115.4124 | 4.3791 | 4.4321 | 4.5131 | -115.587 | 0.05094 | -0.052437 | 120.1373 | 120.0728 | 120.0218 | -0.094532 | -0.12264 | 0.034975 | -0.12526 | 115.6413 | 0.20958 | 0.17461 | -0.072337 | 0.008701 | 120.0739 | 120.0318 | 120.0037 | 120.1287 | -120.0754 | 120.0011 | 120.054 | 120.135 | 115.549 | -120.0914
1038.3438 | 120.3735 | -115.6265 | 4.4586 | -0.013049 | 0.041921 | 0.077424 | 0.051953 | 0.085502 | 0.11314 | -0.011751 | -0.0011537 | -0.0014444 | -0.0050143 | 0.01828 | -0.0094585 | 4.4879 | 4.4884 | 4.4279 | 4.4291 | 4.387 | 4.3634 | -115.5481 | 0.02852 | -0.063743 | -115.4261 | 4.3562 | 4.4137 | 4.4994 | -115.6099 | 0.078413 | -0.029552 | 120.1144 | 120.0545 | 119.9761 | -0.071649 | -0.09518 | 0.016659 | -0.10237 | 115.655 | 0.20042 | 0.18376 | -0.044874 | 0.040742 | 120.0556 | 120.0135 | 119.99 | 120.115 | -120.0067 | 119.9828 | 120.0403 | 120.1259 | 115.5628 | -120.0685
1040.0781 | 120.3049 | -115.6357 | 4.5273 | -0.005418 | 0.041707 | 0.07721 | 0.052167 | 0.085288 | 0.11271 | -0.0041205 | -0.00094006 | -0.002299 | -0.0050143 | 0.018493 | -0.0098857 | 4.4558 | 4.4472 | 4.3959 | 4.4016 | 4.3458 | 4.3131 | -115.626 | 0.019362 | -0.068322 | -115.4536 | 4.3288 | 4.3771 | 4.4582 | -115.6282 | 0.009726 | -0.12569 | 120.0915 | 120.0316 | 120.0219 | -0.18152 | -0.21421 | 0.007499 | -0.19851 | 115.655 | 0.18211 | 0.17461 | -0.15017 | -0.069131 | 120.0373 | 119.9814 | 119.9488 | 120.0829 | -120.1532 | 119.9645 | 120.0128 | 120.0938 | 115.5674 | -120.1555
1041.8438 | 120.3186 | -115.7455 | 4.4174 | 0.002213 | 0.041279 | 0.077424 | 0.052167 | 0.085074 | 0.11335 | -0.0041205 | -0.0015809 | -0.0018716 | -0.0050143 | 0.018493 | -0.0096721 | 4.3368 | 4.3328 | 4.2814 | 4.2871 | 4.2313 | 4.2123 | -115.7221 | 0.023941 | -0.068322 | -115.5635 | 4.2097 | 4.2626 | 4.3483 | -115.7381 | 0.023432 | -0.13028 | 120.0823 | 120.027 | 120.0036 | -0.18613 | -0.20507 | 0.00747 | -0.20769 | 115.7695 | 0.18208 | 0.17461 | -0.15477 | -0.069153 | 120.0327 | 119.9768 | 119.9579 | 120.0783 | -120.1395 | 119.9553 | 120.0082 | 120.0938 | 115.6772 | -120.1555
1043.5312 | 120.3827 | -115.6815 | 4.3991 | 0.002213 | 0.041707 | 0.077424 | 0.052167 | 0.085074 | 0.1125 | 0.00351 | -0.0011537 | -0.0018716 | -0.0052279 | 0.01828 | -0.0096721 | 4.3688 | 4.3648 | 4.3135 | 4.31 | 4.2633 | 4.2352 | -115.6534 | 0.014784 | -0.0729 | -115.5223 | 4.2509 | 4.2947 | 4.3757 | -115.706 | 0.02803 | -0.089081 | 120.0503 | 119.9949 | 119.9669 | -0.13577 | -0.16387 | -0.024564 | -0.14817 | 115.6962 | 0.1592 | 0.18377 | -0.10441 | -0.023372 | 119.9915 | 119.9448 | 119.9167 | 120.0463 | -120.0525 | 119.9324 | 119.9762 | 120.0572 | 115.6086 | -120.1051
1045.2656 | 120.2774 | -115.7135 | 4.4128 | -0.013049 | 0.041493 | 0.077424 | 0.052167 | 0.084861 | 0.1125 | -0.0041205 | -0.00094006 | -0.0018716 | -0.0045871 | 0.018493 | -0.0094585 | 4.3551 | 4.3557 | 4.3043 | 4.3009 | 4.2588 | 4.2261 | -115.6443 | 0.023941 | -0.068322 | -115.5177 | 4.2372 | 4.2718 | 4.362 | -115.7014 | 0.06923 | -0.11197 | 120.0686 | 120.0178 | 119.9486 | -0.15408 | -0.18676 | 0.012058 | -0.17564 | 115.7374 | 0.19582 | 0.18377 | -0.14104 | -0.05084 | 120.0144 | 119.9723 | 119.9396 | 120.0692 | -120.0571 | 119.9507 | 119.9853 | 120.0755 | 115.6452 | -120.1143
1047.0312 | 120.2728 | -115.6174 | 4.4769 | 0.009844 | 0.041493 | 0.077424 | 0.051953 | 0.085074 | 0.11271 | 0.00351 | -0.0011537 | -0.0018716 | -0.0052279 | 0.01828 | -0.0092447 | 4.4375 | 4.4198 | 4.3822 | 4.3741 | 4.3229 | 4.3039 | -115.5619 | 0.02852 | -0.068322 | -115.4398 | 4.315 | 4.3588 | 4.4353 | -115.6236 | 0.055521 | -0.1028 | 120.0549 | 119.9995 | 119.944 | -0.15407 | -0.17301 | -0.006232 | -0.16189 | 115.6459 | 0.17753 | 0.18376 | -0.11813 | -0.04167 | 119.9915 | 119.9402 | 119.9213 | 120.0371 | -120.0388 | 119.9324 | 119.9762 | 120.0526 | 115.549 | -120.1005
1048.7031 | 120.369 | -115.6357 | 4.39 | 0.002213 | 0.041066 | 0.076997 | 0.052167 | 0.085074 | 0.11229 | -0.011751 | -0.00094006 | -0.0018716 | -0.0048007 | 0.018493 | -0.0094585 | 4.3871 | 4.3831 | 4.3364 | 4.3283 | 4.2862 | 4.2627 | -115.5985 | 0.019362 | -0.063743 | -115.4765 | 4.2601 | 4.3039 | 4.3849 | -115.6557 | 0.0372 | -0.061612 | 120.0228 | 119.9721 | 119.9349 | -0.10372 | -0.12725 | -0.019974 | -0.12986 | 115.655 | 0.15921 | 0.17919 | -0.086097 | -0.005059 | 119.964 | 119.9219 | 119.8984 | 120.0188 | -119.9884 | 119.8958 | 119.9395 | 120.0206 | 115.5719 | -120.0456
1050.4531 | 120.2271 | -115.7593 | 4.3533 | 0.002213 | 0.041066 | 0.07721 | 0.052167 | 0.084647 | 0.1125 | 0.00351 | -0.0011537 | -0.0018716 | -0.0048007 | 0.018493 | -0.0094585 | 4.2727 | 4.2595 | 4.2082 | 4.2047 | 4.1626 | 4.1345 | -115.7175 | 0.019362 | -0.068322 | -115.5864 | 4.1411 | 4.1848 | 4.2659 | -115.7655 | 0.041744 | -0.14861 | 120.032 | 119.9675 | 119.9257 | -0.19073 | -0.21883 | -0.006269 | -0.21228 | 115.7786 | 0.17292 | 0.17919 | -0.16852 | -0.087482 | 119.964 | 119.9219 | 119.8938 | 120.0188 | -120.0709 | 119.9003 | 119.9441 | 120.0251 | 115.691 | -120.1189
1052.2031 | 120.2728 | -115.4022 | 4.5959 | -0.013049 | 0.1947 | 0.27315 | 0.031226 | 0.067127 | 0.2751 | -0.0041205 | -0.0011537 | -0.0018716 | -0.0050143 | 0.018707 | -0.0094585 | -8.0752 | -7.8051 | -7.9655 | 1.2288 | 1.0856 | 1.1401 | -90.103 | 0.023941 | -0.063743 | -115.2613 | 4.4112 | 4.4504 | 4.536 | -115.4313 | 25.2992 | -3.3672 | 107.327 | 107.4368 | 82.1376 | -3.5104 | -3.4558 | -0.029071 | -0.18476 | 115.4262 | 0.14095 | 0.17002 | -0.14558 | -0.059958 | 116.631 | 116.4878 | 116.5423 | 107.5971 | -94.699 | 119.8134 | 119.8526 | 119.9382 | 115.3385 | -120.0272
1053.9531 | 120.2499 | -115.6906 | 4.39 | -0.005418 | -0.051241 | 0.069091 | -0.0098017 | -0.0055189 | 0.011224 | -0.0041205 | -0.0011537 | -0.0018716 | -0.0045871 | 0.018493 | -0.0092447 | -0.52547 | -0.54803 | -0.57612 | -0.598 | -0.63611 | -0.64555 | -0.51637 | 0.023941 | -0.063743 | -115.5177 | 4.2052 | 4.2489 | 4.3345 | -115.6969 | 115.1742 | -4.988 | 115.1651 | 115.1145 | -0.059745 | -5.0261 | -5.0355 | -0.006251 | -0.1848 | 115.7146 | 0.17294 | 0.17919 | -0.14104 | -0.055424 | 115.0926 | 115.0545 | 115.0451 | 115.1426 | -4.9063 | 119.8958 | 119.9395 | 120.0251 | 115.6269 | -120.0868
1055.6406 | 120.2957 | -115.6815 | 4.335 | -0.005418 | -0.051241 | 0.069091 | -0.010015 | -0.0057325 | 0.011437 | -0.027012 | -0.0015809 | -0.0020852 | -0.0048007 | 0.018707 | -0.0096721 | -0.57583 | -0.59381 | -0.61274 | -0.63005 | -0.67274 | -0.68218 | -0.58505 | 0.033099 | -0.068322 | -115.5452 | 4.1685 | 4.2169 | 4.2979 | -115.7243 | 115.0964 | -4.9651 | 115.1056 | 115.0687 | -0.027687 | -5.0078 | -5.0172 | -0.042879 | -0.1665 | 115.7146 | 0.13631 | 0.17919 | -0.11816 | -0.037121 | 115.0514 | 115.0087 | 114.9993 | 115.0876 | -4.9201 | 119.85 | 119.8983 | 119.9794 | 115.6131 | -120.0594
1057.3906 | 120.1492 | -115.6952 | 4.39 | -0.005418 | -0.051241 | 0.069304 | -0.0098017 | -0.0055189 | 0.01101 | 0.00351 | -0.00094006 | -0.0018716 | -0.0052279 | 0.018707 | -0.0096721 | -0.58041 | -0.58923 | -0.61274 | -0.64379 | -0.6819 | -0.7005 | -0.58505 | 0.023941 | -0.068322 | -115.4994 | 4.2006 | 4.2398 | 4.3208 | -115.6877 | 115.1101 | -5.0337 | 115.1148 | 115.0824 | -0.027687 | -5.0719 | -5.0905 | 0.007483 | -0.18938 | 115.7191 | 0.19583 | 0.18834 | -0.1502 | -0.06916 | 115.0514 | 115.0133 | 114.9947 | 115.106 | -4.975 | 119.8958 | 119.9349 | 120.016 | 115.6269 | -120.0777
1059.1406 | 120.2957 | -115.7501 | 4.2938 | -0.005418 | -0.051882 | 0.069091 | -0.010229 | -0.0055189 | 0.011224 | -0.0041205 | -0.0011537 | -0.0018716 | -0.0048007 | 0.018921 | -0.0094585 | -0.58499 | -0.60297 | -0.62648 | -0.65294 | -0.69106 | -0.69592 | -0.58963 | 0.019362 | -0.063743 | -115.568 | 4.1319 | 4.1665 | 4.2567 | -115.7472 | 115.1605 | -4.9468 | 115.1651 | 115.1236 | -0.036843 | -4.9849 | -4.9897 | 0.002891 | -0.16193 | 115.7695 | 0.18208 | 0.17919 | -0.12732 | -0.037129 | 115.0972 | 115.0591 | 115.0542 | 115.1472 | -4.8835 | 119.882 | 119.9166 | 120.0068 | 115.6864 | -120.0411
1060.8906 | 120.3094 | -115.7364 | 4.2114 | -0.02068 | -0.051455 | 0.069304 | -0.010015 | -0.0055189 | 0.01101 | 0.00351 | -0.0013673 | -0.0018716 | -0.0050143 | 0.018921 | -0.0096721 | -0.62161 | -0.63502 | -0.65395 | -0.68041 | -0.71853 | -0.72797 | -0.61711 | 0.023941 | -0.068322 | -115.6047 | 4.0724 | 4.1253 | 4.2109 | -115.7884 | 115.1193 | -4.8918 | 115.1148 | 115.0824 | -0.03684 | -4.93 | -4.9394 | -0.052052 | -0.13905 | 115.7603 | 0.13172 | 0.18377 | -0.086134 | -0.000518 | 115.056 | 115.0179 | 115.0084 | 115.1014 | -4.8285 | 119.8088 | 119.8617 | 119.9473 | 115.6681 | -119.9999
1062.5781 | 118.2083 | -67.6392 | 50.5096 | -0.013049 | -0.052523 | 0.069091 | -0.010015 | -0.0057325 | 0.011224 | 0.00351 | -0.00094006 | -0.0012306 | -0.0045871 | 0.018707 | -0.010313 | -0.17293 | -0.20463 | -0.21901 | -0.24547 | -0.28353 | -0.30216 | -0.18669 | 0.38566 | 0.38497 | -80.0418 | 38.5576 | 38.593 | 38.761 | -80.1195 | 67.4525 | -50.7551 | 67.4662 | 67.4202 | -0.032322 | -50.7932 | -50.8118 | -12.4803 | -11.952 | 68.0248 | -12.4027 | 0.077621 | -11.9166 | -11.7486 | 67.3937 | 67.3556 | 67.337 | 67.4345 | -50.6963 | 106.1968 | 106.2322 | 106.4002 | 68.0241 | -130.6291
1064.3281 | 116.2766 | -63.8626 | 52.5101 | -0.005418 | -0.053378 | 0.068877 | -0.010015 | -0.0057325 | 0.01101 | -0.027012 | -0.00094006 | -0.0012306 | -0.0045871 | 0.018707 | -0.010313 | -0.049315 | -0.062694 | -0.090818 | -0.12185 | -0.1599 | -0.16938 | -0.049321 | 0.23456 | 0.26592 | -65.5594 | 50.86 | 50.9369 | 51.0821 | -65.5313 | 63.8133 | -52.6319 | 63.8133 | 63.7718 | -0.041497 | -52.67 | -52.6795 | -1.6687 | -1.6501 | 64.0972 | -1.6968 | -0.028031 | -1.5731 | -1.428 | 63.7408 | 63.7027 | 63.6932 | 63.7999 | -52.5594 | 114.7226 | 114.7995 | 114.9447 | 64.1285 | -118.0414
1066.0625 | 120.2637 | -118.689 | 1.1948 | -0.005418 | -0.05295 | 0.069091 | -0.010229 | -0.0055189 | 0.011437 | -0.011751 | -0.0013673 | -0.0018716 | -0.0052279 | 0.018707 | -0.0096721 | -0.24161 | -0.26873 | -0.28768 | -0.31872 | -0.3568 | -0.37084 | -0.25537 | -0.003531 | -0.11411 | -118.4984 | 1.133 | 1.1812 | 1.2577 | -118.6914 | 118.4336 | -1.5135 | 118.4474 | 118.4013 | -0.032312 | -1.5516 | -1.5656 | -0.002446 | -0.06178 | 118.6854 | 0.19055 | 0.19299 | -0.013513 | 0.062946 | 118.3702 | 118.3322 | 118.3181 | 118.4202 | -1.4501 | 119.8219 | 119.8702 | 119.9467 | 118.5749 | -119.8862
1067.7656 | 120.401 | -119.5908 | 0.3891 | -0.013049 | -0.052737 | 0.069091 | -0.010015 | -0.0057325 | 0.010797 | -0.0041205 | -0.0013673 | -0.0018716 | -0.0050143 | 0.018707 | -0.0094585 | -0.26908 | -0.28704 | -0.306 | -0.33246 | -0.37511 | -0.38915 | -0.26911 | 0.010205 | -0.095794 | -119.5012 | 0.26765 | 0.32047 | 0.38777 | -119.685 | 119.3217 | -0.72156 | 119.3217 | 119.2848 | -0.036889 | -0.76421 | -0.77825 | -0.094255 | -0.12145 | 119.601 | 0.089604 | 0.18386 | -0.068626 | -0.001324 | 119.2583 | 119.2156 | 119.2016 | 119.3037 | -0.65821 | 119.8584 | 119.9112 | 119.9785 | 119.495 | -120.0741
1069.5156 | 120.369 | -119.7189 | 0.43945 | -0.005418 | -0.052737 | 0.068877 | -0.010229 | -0.0055189 | 0.011224 | -0.0041205 | -0.00094006 | -0.001658 | -0.0048007 | 0.018493 | -0.0096721 | -0.27366 | -0.29162 | -0.31973 | -0.34619 | -0.38427 | -0.39831 | -0.27369 | 0.005626 | -0.091215 | -119.5698 | 0.26765 | 0.32047 | 0.39693 | -119.7629 | 119.4452 | -0.78564 | 119.4453 | 119.3992 | -0.046044 | -0.82372 | -0.83776 | -0.043921 | -0.1718 | 119.7246 | 0.1491 | 0.19302 | -0.11898 | -0.042521 | 119.3727 | 119.3347 | 119.3206 | 119.4273 | -0.71314 | 119.9866 | 120.0394 | 120.1159 | 119.6277 | -120.2023
1071.2031 | 120.433 | -119.8059 | 0.42114 | -0.013049 | -0.052737 | 0.069304 | -0.0095879 | -0.0055189 | 0.011224 | -0.0041205 | -0.0011537 | -0.0020852 | -0.0050143 | 0.018707 | -0.0096721 | -0.26908 | -0.28704 | -0.30142 | -0.34619 | -0.37511 | -0.38915 | -0.26453 | 0.010205 | -0.091215 | -119.6202 | 0.25849 | 0.30216 | 0.39235 | -119.827 | 119.5414 | -0.76733 | 119.5368 | 119.5045 | -0.036889 | -0.79626 | -0.81029 | -0.021049 | -0.16265 | 119.8161 | 0.18571 | 0.20675 | -0.11899 | -0.02879 | 119.4597 | 119.4308 | 119.4168 | 119.5189 | -0.68567 | 120.0644 | 120.1081 | 120.1983 | 119.7147 | -120.2481
1072.9688 | 120.5246 | -119.8013 | 0.43488 | -0.013049 | -0.053164 | 0.068877 | -0.010229 | -0.0057325 | 0.011437 | -0.011751 | -0.0011537 | -0.0020852 | -0.0048007 | 0.018921 | -0.0096721 | -0.2645 | -0.27789 | -0.306 | -0.33246 | -0.36595 | -0.38457 | -0.26911 | 0.023941 | -0.077479 | -119.6294 | 0.2997 | 0.34337 | 0.41525 | -119.8315 | 119.5322 | -0.76733 | 119.5368 | 119.4953 | -0.036889 | -0.80083 | -0.81945 | -0.030205 | -0.13518 | 119.8253 | 0.17197 | 0.20218 | -0.091509 | -0.019629 | 119.4689 | 119.4354 | 119.4168 | 119.5234 | -0.70398 | 120.101 | 120.1447 | 120.2166 | 119.7239 | -120.2664
1074.7188 | 120.4742 | -119.902 | 0.42572 | 0.009844 | -0.05295 | 0.068877 | -0.010015 | -0.0059463 | 0.011437 | -0.011751 | -0.0013673 | -0.0014444 | -0.0050143 | 0.018707 | -0.0096721 | -0.24618 | -0.26415 | -0.27853 | -0.30499 | -0.34764 | -0.36626 | -0.23706 | 0.010205 | -0.091215 | -119.698 | 0.26765 | 0.30216 | 0.3832 | -119.8956 | 119.665 | -0.73071 | 119.6559 | 119.6235 | -0.041472 | -0.77336 | -0.79198 | 0.006399 | -0.15807 | 119.9122 | 0.204 | 0.1976 | -0.12356 | -0.042524 | 119.5971 | 119.5544 | 119.5358 | 119.6379 | -0.66278 | 120.1697 | 120.2042 | 120.2852 | 119.8108 | -120.3214
1076.4062 | 120.5063 | -119.8791 | 0.4303 | -0.02068 | -0.05295 | 0.069091 | -0.010229 | -0.0055189 | 0.011224 | -0.0041205 | -0.0011537 | -0.0018716 | -0.0050143 | 0.019134 | -0.0098857 | -0.24618 | -0.255 | -0.28311 | -0.30956 | -0.3568 | -0.36168 | -0.24621 | 0.014784 | -0.086637 | -119.6935 | 0.28138 | 0.32963 | 0.40609 | -119.9048 | 119.6329 | -0.73986 | 119.633 | 119.596 | -0.036892 | -0.78709 | -0.79198 | -0.025647 | -0.14892 | 119.8939 | 0.18569 | 0.21134 | -0.10067 | -0.024209 | 119.5696 | 119.5224 | 119.5175 | 119.6242 | -0.67651 | 120.1605 | 120.2088 | 120.2852 | 119.7925 | -120.3351
1078.1562 | 120.575 | -119.8791 | 0.44861 | -0.005418 | -0.052737 | 0.068663 | -0.010443 | -0.0053053 | 0.011224 | -0.0041205 | -0.00094006 | -0.0014444 | -0.0050143 | 0.019134 | -0.0098857 | -0.24618 | -0.25957 | -0.28311 | -0.31414 | -0.35222 | -0.37084 | -0.23706 | 0.023941 | -0.082058 | -119.698 | 0.30428 | 0.34794 | 0.42898 | -119.9094 | 119.6421 | -0.76275 | 119.633 | 119.596 | -0.04605 | -0.80083 | -0.81945 | -0.030226 | -0.14433 | 119.9031 | 0.18111 | 0.21134 | -0.10066 | -0.019626 | 119.565 | 119.5269 | 119.5083 | 119.6196 | -0.68566 | 120.1834 | 120.2271 | 120.3081 | 119.7971 | -120.358
1079.8906 | 120.6345 | -119.838 | 0.48523 | 0.002213 | -0.05295 | 0.068877 | -0.010229 | -0.0061599 | 0.011224 | -0.0041205 | -0.0011537 | -0.0018716 | -0.0050143 | 0.019134 | -0.0098857 | -0.25992 | -0.28247 | -0.306 | -0.33246 | -0.36595 | -0.38457 | -0.25537 | 0.019362 | -0.082058 | -119.6889 | 0.3409 | 0.38457 | 0.47019 | -119.8911 | 119.5826 | -0.81769 | 119.578 | 119.532 | -0.050626 | -0.85118 | -0.8698 | -0.053109 | -0.14433 | 119.8573 | 0.14907 | 0.20218 | -0.10066 | -0.015039 | 119.5055 | 119.472 | 119.4534 | 119.5555 | -0.7406 | 120.1789 | 120.2225 | 120.3081 | 119.7559 | -120.3763
1081.6406 | 120.6299 | -119.8425 | 0.53558 | -0.013049 | -0.05295 | 0.068877 | -0.010015 | -0.0057325 | 0.01101 | -0.019381 | -0.00094006 | -0.0018716 | -0.0050143 | 0.018921 | -0.0098857 | -0.25992 | -0.26873 | -0.28768 | -0.31872 | -0.36138 | -0.37084 | -0.23706 | 0.014784 | -0.091215 | -119.6568 | 0.39127 | 0.43036 | 0.50682 | -119.859 | 119.6055 | -0.85431 | 119.5826 | 119.5548 | -0.050628 | -0.89696 | -0.90642 | -0.01648 | -0.14432 | 119.8573 | 0.1857 | 0.20218 | -0.10522 | -0.028765 | 119.5238 | 119.4812 | 119.4717 | 119.5738 | -0.77264 | 120.2338 | 120.2729 | 120.3493 | 119.7513 | -120.3946
1083.3906 | 120.6024 | -119.8425 | 0.5722 | -0.005418 | -0.053164 | 0.069091 | -0.0098017 | -0.0053053 | 0.01101 | -0.0041205 | -0.0015809 | -0.001658 | -0.0052279 | 0.018707 | -0.0094585 | -0.29197 | -0.30536 | -0.33805 | -0.35535 | -0.40259 | -0.4212 | -0.292 | 0.019362 | -0.077479 | -119.6477 | 0.40958 | 0.45325 | 0.54345 | -119.8544 | 119.5505 | -0.92755 | 119.5506 | 119.5045 | -0.046042 | -0.97479 | -0.99341 | -0.011901 | -0.16262 | 119.8619 | 0.19486 | 0.20676 | -0.11895 | -0.028758 | 119.4872 | 119.4399 | 119.4213 | 119.5372 | -0.86421 | 120.2521 | 120.2958 | 120.386 | 119.7651 | -120.4266
1085.0781 | 120.5841 | -119.8746 | 0.59967 | 0.002213 | -0.053164 | 0.068663 | -0.010015 | -0.0057325 | 0.011224 | -0.011751 | -0.00094006 | -0.0018716 | -0.0048007 | 0.018921 | -0.0096721 | -0.28739 | -0.2962 | -0.32889 | -0.35535 | -0.39343 | -0.40289 | -0.26911 | 0.019362 | -0.086637 | -119.6614 | 0.42332 | 0.47157 | 0.54803 | -119.859 | 119.6055 | -0.95502 | 119.5872 | 119.5457 | -0.05978 | -0.9931 | -1.0026 | 0.015564 | -0.17635 | 119.8939 | 0.21316 | 0.1976 | -0.1281 | -0.051644 | 119.5192 | 119.4811 | 119.4717 | 119.5784 | -0.86878 | 120.2979 | 120.3461 | 120.4226 | 119.7879 | -120.4587
1086.8281 | 120.7123 | -119.8013 | 0.60883 | -0.013049 | -0.05295 | 0.068877 | -0.010229 | -0.0057325 | 0.011224 | -0.011751 | -0.0011537 | -0.0020852 | -0.0050143 | 0.018493 | -0.0098857 | -0.28281 | -0.2962 | -0.31973 | -0.35535 | -0.38885 | -0.39373 | -0.26911 | 0.019362 | -0.077479 | -119.6431 | 0.45994 | 0.49446 | 0.5755 | -119.8453 | 119.5322 | -0.96418 | 119.5185 | 119.4816 | -0.050623 | -0.99768 | -1.0026 | -0.043942 | -0.14888 | 119.8207 | 0.15824 | 0.20218 | -0.11437 | -0.033329 | 119.446 | 119.4125 | 119.4076 | 119.5051 | -0.87793 | 120.2613 | 120.2958 | 120.3768 | 119.7239 | -120.4541
1088.5938 | 120.6162 | -119.8059 | 0.70496 | 0.009844 | -0.053378 | 0.068663 | -0.010229 | -0.0053053 | 0.01101 | -0.0041205 | -0.0013673 | -0.0018716 | -0.0048007 | 0.018921 | -0.0094585 | -0.2645 | -0.27331 | -0.29684 | -0.32788 | -0.36138 | -0.38457 | -0.25079 | 0.023941 | -0.082058 | -119.611 | 0.51031 | 0.55398 | 0.63044 | -119.8178 | 119.5551 | -1.0328 | 119.5414 | 119.5091 | -0.046048 | -1.0663 | -1.0895 | -0.011892 | -0.19465 | 119.8298 | 0.19486 | 0.20676 | -0.15097 | -0.074515 | 119.478 | 119.4445 | 119.4213 | 119.5326 | -0.95575 | 120.3162 | 120.3599 | 120.4363 | 119.7238 | -120.5228
1090.3438 | 120.6894 | -119.751 | 0.66834 | -0.005418 | -0.053164 | 0.06845 | -0.010443 | -0.0055189 | 0.011224 | -0.019381 | -0.0011537 | -0.0018716 | -0.0048007 | 0.018493 | -0.0096721 | -0.24618 | -0.25957 | -0.28768 | -0.31872 | -0.3568 | -0.37542 | -0.24163 | 0.02852 | -0.082058 | -119.6019 | 0.5332 | 0.56314 | 0.65333 | -119.7995 | 119.5093 | -0.98706 | 119.5048 | 119.4633 | -0.046049 | -1.0251 | -1.0438 | -0.048507 | -0.13513 | 119.7795 | 0.14909 | 0.1976 | -0.1052 | -0.015001 | 119.4323 | 119.3942 | 119.3756 | 119.4914 | -0.90997 | 120.2842 | 120.3141 | 120.4043 | 119.6689 | -120.4678
1092.0938 | 120.639 | -119.7922 | 0.72784 | -0.013049 | -0.053164 | 0.06845 | -0.010015 | -0.0059463 | 0.01101 | 0.00351 | -0.0011537 | -0.0018716 | -0.0050143 | 0.018707 | -0.0096721 | -0.25076 | -0.26415 | -0.28768 | -0.31872 | -0.35222 | -0.37084 | -0.23706 | 0.019362 | -0.082058 | -119.611 | 0.54236 | 0.58145 | 0.66249 | -119.8086 | 119.5551 | -1.0466 | 119.5414 | 119.5045 | -0.050628 | -1.0801 | -1.0987 | -0.016467 | -0.18549 | 119.8115 | 0.18113 | 0.1976 | -0.14639 | -0.065353 | 119.4735 | 119.44 | 119.4213 | 119.528 | -0.9649 | 120.3345 | 120.3736 | 120.4547 | 119.7101 | -120.5365
1093.8438 | 120.7489 | -119.7968 | 0.68207 | -0.005418 | -0.053164 | 0.068663 | -0.010015 | -0.0059463 | 0.01101 | -0.011751 | -0.00094006 | -0.001658 | -0.0050143 | 0.018921 | -0.0096721 | -0.25992 | -0.28247 | -0.29684 | -0.33703 | -0.37511 | -0.38 | -0.25537 | 0.023941 | -0.077479 | -119.6156 | 0.54236 | 0.59061 | 0.67165 | -119.827 | 119.5414 | -1.0191 | 119.5368 | 119.4999 | -0.041469 | -1.0572 | -1.0621 | -0.030204 | -0.13971 | 119.8207 | 0.18113 | 0.21133 | -0.091458 | -0.01042 | 119.4597 | 119.4216 | 119.4168 | 119.5143 | -0.93744 | 120.3391 | 120.3874 | 120.4684 | 119.7193 | -120.509
1095.5312 | 120.7077 | -119.8654 | 0.70038 | -0.013049 | -0.053164 | 0.068663 | -0.0098017 | -0.0053053 | 0.011224 | 0.01114 | -0.0011537 | -0.001658 | -0.0048007 | 0.018921 | -0.0096721 | -0.25992 | -0.28247 | -0.30142 | -0.32788 | -0.36595 | -0.38915 | -0.25537 | 0.019362 | -0.086637 | -119.6477 | 0.5332 | 0.5723 | 0.64875 | -119.8544 | 119.61 | -1.0283 | 119.6055 | 119.564 | -0.046047 | -1.0663 | -1.0895 | 0.010987 | -0.16718 | 119.8848 | 0.21774 | 0.20676 | -0.12808 | -0.051623 | 119.5375 | 119.4995 | 119.4763 | 119.5829 | -0.95575 | 120.3986 | 120.4377 | 120.5142 | 119.7788 | -120.5548
1097.2656 | 120.7718 | -119.8196 | 0.66376 | -0.013049 | -0.053164 | 0.068877 | -0.010229 | -0.0055189 | 0.010797 | 0.00351 | -0.0011537 | -0.0018716 | -0.0052279 | 0.018921 | -0.0098857 | -0.27366 | -0.29162 | -0.31515 | -0.34161 | -0.38427 | -0.39831 | -0.25995 | 0.019362 | -0.082058 | -119.6568 | 0.5332 | 0.56772 | 0.6396 | -119.8636 | 119.5597 | -1.0054 | 119.546 | 119.5045 | -0.055203 | -1.048 | -1.0621 | -0.043947 | -0.13056 | 119.839 | 0.16281 | 0.20676 | -0.09604 | -0.024159 | 119.478 | 119.4354 | 119.4213 | 119.528 | -0.92371 | 120.3528 | 120.3874 | 120.4592 | 119.7376 | -120.5273
1099.0312 | 120.7764 | -119.9158 | 0.62256 | -0.02068 | -0.053591 | 0.068663 | -0.010229 | -0.0055189 | 0.010797 | -0.011751 | -0.0013673 | -0.0018716 | -0.0052279 | 0.019134 | -0.0096721 | -0.27823 | -0.29162 | -0.31515 | -0.34619 | -0.38885 | -0.39831 | -0.26453 | 0.023941 | -0.091215 | -119.7072 | 0.50115 | 0.53109 | 0.6167 | -119.914 | 119.6512 | -0.96875 | 119.6375 | 119.6006 | -0.050624 | -1.0114 | -1.0209 | 0.001816 | -0.12141 | 119.9397 | 0.20857 | 0.20676 | -0.09147 | -0.005854 | 119.5696 | 119.5269 | 119.5175 | 119.6241 | -0.88709 | 120.4169 | 120.4469 | 120.5325 | 119.8246 | -120.5365
1100.7188 | 120.8176 | -119.8608 | 0.59052 | -0.005418 | -0.05295 | 0.068877 | -0.0098017 | -0.0059463 | 0.01101 | -0.011751 | -0.0013673 | -0.0018716 | -0.0045871 | 0.018921 | -0.0094585 | -0.27823 | -0.2962 | -0.32431 | -0.35993 | -0.39343 | -0.41662 | -0.27369 | 0.023941 | -0.086637 | -119.7392 | 0.47368 | 0.51735 | 0.59381 | -119.9506 | 119.5872 | -0.95044 | 119.5826 | 119.5365 | -0.050623 | -0.98394 | -1.0071 | -0.089745 | -0.11684 | 119.8848 | 0.12159 | 0.21134 | -0.073162 | 0.003297 | 119.5009 | 119.4674 | 119.4442 | 119.5646 | -0.8642 | 120.3345 | 120.3782 | 120.4547 | 119.7742 | -120.5411
1102.4688 | 116.3315 | -95.4666 | 20.7275 | 0.002213 | -0.053164 | 0.06845 | -0.01087 | -0.0053053 | 0.010156 | -0.019381 | -0.0013673 | -0.0014444 | -0.0048007 | 0.018707 | -0.0096721 | 0.010204 | 0.005985 | -0.026723 | -0.062332 | -0.10038 | -0.11444 | 0.028521 | 0.069728 | 0.03241 | -94.941 | 20.9396 | 21.0112 | 21.1014 | -95.0601 | 95.4951 | -20.7899 | 95.4768 | 95.4399 | -0.055244 | -20.8279 | -20.842 | 0.40648 | 0.21202 | 95.5363 | 0.52566 | 0.11918 | 0.28364 | 0.37383 | 95.4043 | 95.3662 | 95.3522 | 95.4726 | -20.699 | 116.4062 | 116.4778 | 116.568 | 95.499 | -115.7877
1104.2344 | 116.0065 | -94.3222 | 21.4188 | -0.005418 | -0.053591 | 0.06845 | -0.010656 | -0.0055189 | 0.010156 | -0.019381 | -0.0013673 | -0.001658 | -0.0050143 | 0.019134 | -0.0094585 | -0.008109 | -0.026065 | -0.035879 | -0.080646 | -0.10953 | -0.12817 | 0.010206 | 0.092622 | 0.041567 | -94.6067 | 20.8434 | 20.9013 | 21.0098 | -94.735 | 94.3324 | -21.4994 | 94.3141 | 94.2863 | -0.046085 | -21.5283 | -21.5469 | -0.41283 | -0.57536 | 94.4148 | -0.28451 | 0.12833 | -0.51747 | -0.40896 | 94.2416 | 94.2127 | 94.194 | 94.2961 | -21.4086 | 115.1656 | 115.2235 | 115.332 | 94.3638 | -116.1538
1106 | 115.7181 | -93.1 | 22.3434 | -0.005418 | -0.053378 | 0.06845 | -0.010656 | -0.0055189 | 0.010369 | -0.019381 | -0.0011537 | -0.0012306 | -0.0050143 | 0.018921 | -0.0098857 | 0.010204 | -0.012329 | -0.035879 | -0.076067 | -0.10496 | -0.11444 | 0.014784 | 0.069728 | 0.014095 | -93.1324 | 22.0704 | 22.1467 | 22.2414 | -93.2469 | 93.1148 | -22.4195 | 93.1102 | 93.0641 | -0.050663 | -22.4484 | -22.4579 | -0.14695 | -0.273 | 93.1697 | -0.032389 | 0.11456 | -0.19677 | -0.102 | 93.0239 | 92.995 | 92.9855 | 93.0876 | -22.3287 | 115.1704 | 115.2466 | 115.3414 | 93.1141 | -115.5904
1107.6875 | 115.4388 | -93.4204 | 21.9086 | 0.002213 | -0.053378 | 0.06845 | -0.010443 | -0.0053053 | 0.010583 | -0.019381 | -0.0013673 | -0.001658 | -0.0050143 | 0.018921 | -0.0096721 | 0.023939 | 0.010564 | -0.012988 | -0.053175 | -0.086641 | -0.1007 | 0.037679 | 0.060571 | 0.000359 | -93.3567 | 21.6263 | 21.6934 | 21.7836 | -93.4804 | 93.4581 | -21.9617 | 93.4443 | 93.4074 | -0.050667 | -21.9952 | -22.0093 | -0.060033 | -0.28224 | 93.481 | 0.063688 | 0.12372 | -0.21518 | -0.12498 | 93.3672 | 93.3338 | 93.3197 | 93.431 | -21.8709 | 115.0467 | 115.1138 | 115.204 | 93.4208 | -115.389
1109.4375 | 115.3931 | -94.0109 | 20.993 | -0.005418 | -0.053591 | 0.068663 | -0.010443 | -0.0057325 | 0.010583 | -0.019381 | -0.0011537 | -0.0014444 | -0.0045871 | 0.018707 | -0.0098857 | 0.037675 | 0.010564 | -0.012988 | -0.03944 | -0.082062 | -0.091543 | 0.042258 | 0.06515 | 0.000359 | -93.6955 | 21.1135 | 21.1623 | 21.257 | -93.8147 | 94.0532 | -21.0325 | 94.0486 | 93.9979 | -0.055246 | -21.0751 | -21.0846 | 0.19623 | 0.12049 | 94.0761 | 0.31538 | 0.11915 | 0.16923 | 0.264 | 93.9715 | 93.9289 | 93.9194 | 94.0215 | -20.9508 | 115.1245 | 115.1732 | 115.268 | 94.0113 | -114.8077
1111.1875 | 115.21 | -94.0292 | 20.9335 | -0.013049 | -0.053378 | 0.06845 | -0.010229 | -0.0055189 | 0.010156 | -0.027012 | -0.0013673 | -0.001658 | -0.0048007 | 0.019134 | -0.0098857 | 0.046831 | 0.042614 | 0.009904 | -0.025705 | -0.059167 | -0.077807 | 0.065153 | 0.051413 | -0.008798 | -94.0069 | 20.6603 | 20.7136 | 20.8175 | -94.1261 | 94.0944 | -20.9592 | 94.0761 | 94.0391 | -0.055249 | -20.9927 | -21.0113 | -0.09682 | -0.27327 | 94.0806 | 0.022337 | 0.11916 | -0.21997 | -0.11603 | 94.0035 | 93.9701 | 93.9514 | 94.0718 | -20.8684 | 114.6895 | 114.7428 | 114.8467 | 94.0204 | -115.0596
1112.9375 | 115.1505 | -94.455 | 20.3247 | -0.005418 | -0.053378 | 0.068663 | -0.010443 | -0.0055189 | 0.010156 | -0.019381 | -0.0011537 | -0.0012306 | -0.0048007 | 0.019134 | -0.0098857 | 0.05141 | 0.038035 | 0.014482 | -0.021127 | -0.059167 | -0.077807 | 0.060574 | 0.051413 | -0.017956 | -94.3824 | 20.1612 | 20.2282 | 20.3276 | -94.5015 | 94.5155 | -20.3458 | 94.5064 | 94.4694 | -0.046092 | -20.3839 | -20.4025 | -0.046563 | -0.1635 | 94.5064 | 0.072603 | 0.11917 | -0.09647 | 0.002882 | 94.4338 | 94.3958 | 94.3771 | 94.493 | -20.2641 | 114.6162 | 114.6832 | 114.7825 | 94.437 | -114.8262
1114.625 | 115.0269 | -94.5557 | 20.137 | -0.013049 | -0.053591 | 0.068663 | -0.010656 | -0.0057325 | 0.010369 | -0.011751 | -0.00094006 | -0.0014444 | -0.0048007 | 0.019134 | -0.0096721 | 0.019361 | 0.010564 | -0.012988 | -0.048597 | -0.095798 | -0.1007 | 0.0331 | 0.046835 | -0.017956 | -94.5335 | 19.9277 | 19.9856 | 20.0849 | -94.6526 | 94.5888 | -20.1856 | 94.575 | 94.5427 | -0.046088 | -20.2328 | -20.2377 | -0.096956 | -0.20932 | 94.6025 | 0.022214 | 0.11917 | -0.15145 | -0.052101 | 94.5071 | 94.4599 | 94.455 | 94.5662 | -20.1039 | 114.4834 | 114.5412 | 114.6406 | 94.5377 | -114.7896
1116.3594 | 114.83 | -94.043 | 20.6955 | 0.002213 | -0.053805 | 0.06845 | -0.010443 | -0.0053053 | 0.010156 | -0.019381 | -0.0011537 | -0.0018716 | -0.0048007 | 0.019134 | -0.010099 | 0.097194 | 0.083821 | 0.051108 | 0.024657 | -0.022536 | -0.0366 | 0.11094 | 0.051413 | -0.008798 | -93.952 | 20.468 | 20.5167 | 20.6206 | -94.062 | 94.1539 | -20.6708 | 94.1402 | 94.0941 | -0.059834 | -20.718 | -20.7321 | -0.018984 | -0.22753 | 94.0944 | 0.091015 | 0.11 | -0.17881 | -0.074877 | 94.0676 | 94.0204 | 94.0064 | 94.1268 | -20.5846 | 114.5109 | 114.5597 | 114.6636 | 94.0342 | -114.7574
1118.1094 | 114.8117 | -96.6568 | 17.8894 | 0.002213 | -0.053378 | 0.068236 | -0.010443 | -0.0053053 | 0.0097281 | -0.019381 | -0.00094006 | -0.0014444 | -0.0052279 | 0.019134 | -0.0096721 | 0.097194 | 0.060928 | 0.04653 | 0.015501 | -0.027115 | -0.045757 | 0.097205 | 0.037677 | -0.036271 | -96.571 | 17.73 | 17.7833 | 17.8826 | -96.6948 | 96.754 | -17.8739 | 96.754 | 96.7033 | -0.050675 | -17.9165 | -17.9352 | -0.037974 | -0.15938 | 96.6945 | 0.085823 | 0.1238 | -0.10614 | -0.006789 | 96.6723 | 96.6297 | 96.611 | 96.7177 | -17.7922 | 114.3868 | 114.4401 | 114.5394 | 96.6205 | -114.5842
1119.7969 | 114.8987 | -95.9518 | 18.5806 | -0.005418 | -0.053591 | 0.06845 | -0.01087 | -0.0055189 | 0.010156 | -0.019381 | -0.0013673 | -0.001658 | -0.0050143 | 0.019348 | -0.010099 | 0.074302 | 0.060928 | 0.04653 | 0.006344 | -0.031693 | -0.045757 | 0.10636 | 0.046835 | -0.022535 | -95.9391 | 18.339 | 18.4014 | 18.5007 | -96.0629 | 96.0582 | -18.5743 | 96.0261 | 95.9984 | -0.059833 | -18.6123 | -18.6264 | -0.11105 | -0.24166 | 95.9987 | 0.012729 | 0.12378 | -0.17925 | -0.079901 | 95.9582 | 95.9201 | 95.9061 | 96.0128 | -18.4743 | 114.2908 | 114.3532 | 114.4526 | 95.9293 | -114.6435
1121.5469 | 114.8117 | -97.8561 | 16.6306 | -0.005418 | -0.053378 | 0.068236 | -0.010229 | -0.0057325 | 0.010369 | -0.011751 | -0.0013673 | -0.0014444 | -0.0045871 | 0.019134 | -0.0094585 | 0.042253 | 0.028878 | 0.000747 | -0.030283 | -0.068325 | -0.086964 | 0.060574 | 0.037677 | -0.040849 | -97.7065 | 16.5121 | 16.5699 | 16.6555 | -97.8395 | 97.9167 | -16.6608 | 97.8984 | 97.8569 | -0.059827 | -16.6989 | -16.7175 | 0.016663 | -0.1184 | 97.8938 | 0.14964 | 0.13298 | -0.060621 | 0.024995 | 97.8259 | 97.7878 | 97.7692 | 97.885 | -16.57 | 114.3683 | 114.4261 | 114.5117 | 97.8153 | -114.47
1123.2969 | 114.7934 | -98.3414 | 16.0584 | 0.002213 | -0.053591 | 0.06845 | -0.010656 | -0.0059463 | 0.0099417 | -0.019381 | -0.0011537 | -0.0018716 | -0.0050143 | 0.019134 | -0.0096721 | 0.046831 | 0.038035 | 0.023639 | -0.016548 | -0.059167 | -0.077807 | 0.065153 | 0.037677 | -0.036271 | -98.0728 | 16.1092 | 16.167 | 16.2618 | -98.2149 | 98.4065 | -16.0749 | 98.3882 | 98.365 | -0.041514 | -16.1175 | -16.1362 | 0.12643 | 0.050891 | 98.379 | 0.26858 | 0.14215 | 0.10867 | 0.20344 | 98.3248 | 98.2822 | 98.2636 | 98.3794 | -15.9932 | 114.4506 | 114.5084 | 114.6032 | 98.3051 | -114.2733
1124.9844 | 114.7705 | -95.0958 | 19.455 | -0.005418 | -0.053591 | 0.068877 | -0.010443 | -0.0055189 | 0.0097281 | -0.019381 | -0.0011537 | -0.001658 | -0.0045871 | 0.019134 | -0.0096721 | 0.092615 | 0.074664 | 0.060265 | 0.024657 | -0.022536 | -0.041178 | 0.10178 | 0.051413 | -0.00422 | -95.1287 | 19.1265 | 19.1706 | 19.2745 | -95.257 | 95.1976 | -19.4303 | 95.1884 | 95.1561 | -0.041519 | -19.4775 | -19.4961 | -0.1612 | -0.32849 | 95.1472 | -0.032858 | 0.12834 | -0.28438 | -0.18045 | 95.1205 | 95.0733 | 95.0546 | 95.1705 | -19.3532 | 114.2223 | 114.2664 | 114.3703 | 95.0916 | -114.712
1126.7344 | 114.8117 | -97.4945 | 16.9464 | 0.002213 | -0.053591 | 0.068663 | -0.01087 | -0.0057325 | 0.0099417 | -0.027012 | -0.0011537 | -0.001658 | -0.0048007 | 0.019348 | -0.010099 | 0.074302 | 0.065507 | 0.037373 | 0.010922 | -0.027115 | -0.050335 | 0.092626 | 0.023941 | -0.036271 | -97.3127 | 16.8876 | 16.9591 | 17.0356 | -97.4411 | 97.5871 | -16.9355 | 97.5688 | 97.5319 | -0.055253 | -16.9735 | -16.9967 | 0.053387 | -0.058826 | 97.5184 | 0.18178 | 0.12839 | 0.012703 | 0.089162 | 97.5054 | 97.4674 | 97.4442 | 97.56 | -16.8538 | 114.3821 | 114.4536 | 114.5301 | 97.4582 | -114.3875
1128.4844 | 114.8438 | -95.7413 | 18.75 | -0.005418 | -0.053378 | 0.068236 | -0.010443 | -0.0059463 | 0.0099417 | -0.019381 | -0.0013673 | -0.001658 | -0.0050143 | 0.019134 | -0.010099 | 0.10635 | 0.092979 | 0.069421 | 0.038393 | -0.013378 | -0.022864 | 0.1201 | 0.051413 | -0.013377 | -95.7651 | 18.4763 | 18.525 | 18.6243 | -95.8843 | 95.8614 | -18.7116 | 95.8476 | 95.8107 | -0.050679 | -18.7634 | -18.7729 | -0.14305 | -0.27368 | 95.7927 | -0.023851 | 0.1192 | -0.225 | -0.12565 | 95.7797 | 95.7279 | 95.7184 | 95.8343 | -18.6299 | 114.2176 | 114.2663 | 114.3656 | 95.7279 | -114.6343
1130.2344 | 114.8483 | -95.668 | 18.8004 | -0.005418 | -0.053378 | 0.068022 | -0.010229 | -0.0057325 | 0.010156 | -0.027012 | -0.0013673 | -0.001658 | -0.0050143 | 0.019348 | -0.0098857 | 0.10635 | 0.0884 | 0.060265 | 0.033814 | -0.008799 | -0.022864 | 0.11552 | 0.042256 | -0.022535 | -95.3942 | 18.8563 | 18.9004 | 19.0044 | -95.518 | 95.7836 | -18.7665 | 95.7744 | 95.7283 | -0.055256 | -18.8092 | -18.8232 | 0.15001 | 0.055984 | 95.7103 | 0.27378 | 0.12377 | 0.10009 | 0.20402 | 95.7018 | 95.6592 | 95.6452 | 95.7564 | -18.6848 | 114.5244 | 114.5685 | 114.6724 | 95.6455 | -114.3184
1132 | 114.7202 | -97.9614 | 16.5207 | -0.013049 | -0.053805 | 0.06845 | -0.010443 | -0.0053053 | 0.0097281 | -0.011751 | -0.0011537 | -0.0014444 | -0.0048007 | 0.019348 | -0.0098857 | 0.07888 | 0.070086 | 0.041952 | 0.015501 | -0.027115 | -0.045757 | 0.097205 | 0.042256 | -0.031692 | -97.995 | 16.2008 | 16.2494 | 16.3534 | -98.1279 | 98.0586 | -16.5052 | 98.0403 | 98.0034 | -0.055253 | -16.5478 | -16.5664 | -0.16652 | -0.31988 | 98.0037 | -0.033529 | 0.13299 | -0.27126 | -0.16733 | 97.9769 | 97.9343 | 97.9157 | 98.0315 | -16.4235 | 114.1622 | 114.2109 | 114.3148 | 97.9297 | -114.6486
1133.7031 | 114.7018 | -99.5636 | 14.8956 | -0.005418 | -0.053591 | 0.06845 | -0.010229 | -0.0057325 | 0.0097281 | -0.011751 | -0.0013673 | -0.001658 | -0.0050143 | 0.019134 | -0.0098857 | -0.053893 | -0.048958 | -0.081662 | -0.11269 | -0.1599 | -0.17854 | -0.026426 | 0.02852 | -0.045428 | -99.4006 | 14.7632 | 14.8163 | 14.9111 | -99.5474 | 99.5372 | -15.0083 | 99.5097 | 99.4819 | -0.055236 | -15.0555 | -15.0742 | 0.016223 | -0.13247 | 99.5921 | 0.16298 | 0.14676 | -0.079302 | 0.015472 | 99.4509 | 99.4037 | 99.3851 | 99.5146 | -14.9221 | 114.3268 | 114.3799 | 114.4747 | 99.5182 | -114.443
1135.4531 | 114.7568 | -99.9207 | 14.5157 | -0.013049 | -0.053805 | 0.06845 | -0.010229 | -0.0055189 | 0.0097281 | -0.011751 | -0.0013673 | -0.0012306 | -0.0050143 | 0.019134 | -0.0098857 | -0.049315 | -0.053537 | -0.08624 | -0.11727 | -0.16448 | -0.17396 | -0.035584 | 0.033099 | -0.045428 | -99.7898 | 14.3877 | 14.4271 | 14.5311 | -99.9228 | 99.8851 | -14.633 | 99.8713 | 99.8344 | -0.050656 | -14.6802 | -14.6896 | -0.002185 | -0.12796 | 99.9538 | 0.13084 | 0.13303 | -0.088539 | 0.015392 | 99.8034 | 99.7562 | 99.7467 | 99.8671 | -14.5513 | 114.3084 | 114.3478 | 114.4517 | 99.8752 | -114.4385
1137.2031 | 118.0984 | -117.7231 | 0.032043 | 0.002213 | -0.053378 | 0.06845 | -0.010229 | -0.0055189 | 0.010797 | -0.019381 | -0.0013673 | -0.001658 | -0.0050143 | 0.019134 | -0.010313 | -0.32402 | -0.34199 | -0.36551 | -0.40113 | -0.43464 | -0.45325 | -0.31032 | -0.003531 | -0.13242 | -117.5964 | -0.11237 | -0.073287 | 0.012329 | -117.8077 | 117.4128 | -0.43318 | 117.3991 | 117.3576 | -0.055196 | -0.46668 | -0.48529 | -0.084616 | -0.14441 | 117.7196 | 0.12667 | 0.21129 | -0.10533 | -0.019714 | 117.322 | 117.2884 | 117.2698 | 117.3811 | -0.34236 | 117.6107 | 117.6498 | 117.7354 | 117.5907 | -117.8397
1138.9531 | 118.3456 | -117.9932 | 0.045776 | -0.005418 | -0.053591 | 0.06845 | -0.0098017 | -0.0059463 | 0.010797 | -0.011751 | -0.0011537 | -0.001658 | -0.0052279 | 0.019134 | -0.010099 | -0.32402 | -0.33741 | -0.36094 | -0.39655 | -0.43006 | -0.45325 | -0.30574 | -0.003531 | -0.11411 | -117.8253 | -0.11237 | -0.077866 | 0.007751 | -118.0366 | 117.6874 | -0.44233 | 117.6691 | 117.6322 | -0.055197 | -0.47584 | -0.49903 | -0.043476 | -0.15814 | 117.9896 | 0.16782 | 0.21129 | -0.12364 | -0.038025 | 117.5966 | 117.5631 | 117.5399 | 117.6558 | -0.35152 | 117.8808 | 117.9153 | 118.0009 | 117.8791 | -118.0824
1140.6406 | 118.5013 | -118.1305 | 0.018311 | -0.005418 | -0.053378 | 0.06845 | -0.0098017 | -0.0059463 | 0.010797 | -0.0041205 | -0.0011537 | -0.001658 | -0.0052279 | 0.019134 | -0.010099 | -0.40185 | -0.40609 | -0.43419 | -0.46981 | -0.5079 | -0.52193 | -0.379 | 0.001048 | -0.10495 | -117.9764 | -0.11237 | -0.073287 | 0.007751 | -118.1832 | 117.7515 | -0.48812 | 117.7286 | 117.6963 | -0.055186 | -0.52621 | -0.54024 | -0.052669 | -0.13068 | 118.1315 | 0.15405 | 0.20672 | -0.091598 | -0.01056 | 117.6607 | 117.6226 | 117.6086 | 117.7244 | -0.39731 | 118.0181 | 118.0572 | 118.1382 | 118.0255 | -118.2015
1142.375 | 118.5242 | -118.2953 | 0.059509 | -0.013049 | -0.053805 | 0.068022 | -0.010229 | -0.0061599 | 0.010583 | -0.0041205 | -0.0011537 | -0.0020852 | -0.0052279 | 0.019348 | -0.0098857 | -0.28739 | -0.30994 | -0.33805 | -0.37366 | -0.41174 | -0.42578 | -0.27827 | 0.005626 | -0.10495 | -118.0955 | -0.12152 | -0.082444 | -0.001407 | -118.2931 | 118.017 | -0.43317 | 118.0079 | 117.9572 | -0.059779 | -0.47125 | -0.48529 | 0.002234 | -0.18103 | 118.3009 | 0.1998 | 0.19756 | -0.14195 | -0.060916 | 117.9216 | 117.8835 | 117.8695 | 117.9853 | -0.33778 | 118.1738 | 118.2128 | 118.2939 | 118.1903 | -118.3526
1144.125 | 118.6111 | -118.3914 | 0.041199 | -0.005418 | -0.053591 | 0.068663 | -0.0098017 | -0.0057325 | 0.010797 | -0.011751 | -0.0013673 | -0.0020852 | -0.0052279 | 0.019348 | -0.010099 | -0.32402 | -0.33741 | -0.36094 | -0.40113 | -0.43922 | -0.45325 | -0.30574 | 0.001048 | -0.10495 | -118.1916 | -0.12152 | -0.073287 | 0.012329 | -118.3984 | 118.0857 | -0.44233 | 118.0674 | 118.0305 | -0.055197 | -0.48042 | -0.49445 | -0.006948 | -0.16272 | 118.3925 | 0.19977 | 0.20672 | -0.11449 | -0.02887 | 117.9903 | 117.9522 | 117.9382 | 118.054 | -0.34694 | 118.2699 | 118.3181 | 118.4037 | 118.2865 | -118.4396
1145.875 | 118.7347 | -118.4555 | 0.022888 | -0.013049 | -0.053591 | 0.06845 | -0.010015 | -0.0057325 | 0.01101 | -0.011751 | -0.0011537 | -0.0018716 | -0.0052279 | 0.019562 | -0.0098857 | -0.30113 | -0.30994 | -0.34262 | -0.37366 | -0.41174 | -0.42578 | -0.27827 | 0.010205 | -0.091215 | -118.2832 | -0.11695 | -0.073287 | 0.012329 | -118.4945 | 118.1772 | -0.39655 | 118.1544 | 118.1129 | -0.064357 | -0.43463 | -0.44867 | -0.039017 | -0.13983 | 118.4657 | 0.17229 | 0.2113 | -0.096175 | -0.010559 | 118.0818 | 118.0438 | 118.0297 | 118.1456 | -0.30116 | 118.3386 | 118.3822 | 118.4678 | 118.3643 | -118.5174
1147.625 | 118.7668 | -118.5791 | 0.032043 | 0.002213 | -0.053805 | 0.068663 | -0.010015 | -0.0057325 | 0.01101 | -0.019381 | -0.0013673 | -0.001658 | -0.0050143 | 0.019348 | -0.010099 | -0.2645 | -0.28704 | -0.306 | -0.32788 | -0.37969 | -0.39373 | -0.25079 | 0.014784 | -0.091215 | -118.3794 | -0.11695 | -0.077866 | 0.003172 | -118.5769 | 118.3283 | -0.35992 | 118.3146 | 118.2731 | -0.055205 | -0.41173 | -0.42577 | 0.002162 | -0.14899 | 118.5939 | 0.19973 | 0.19757 | -0.10991 | -0.028871 | 118.2512 | 118.1994 | 118.1854 | 118.2921 | -0.28284 | 118.4622 | 118.5012 | 118.5823 | 118.4879 | -118.609
1149.3281 | 118.9362 | -118.6157 | 0.009155 | -0.005418 | -0.053591 | 0.068663 | -0.010443 | -0.0059463 | 0.010369 | -0.019381 | -0.00094006 | -0.0018716 | -0.0052279 | 0.019562 | -0.0098857 | -0.24618 | -0.25957 | -0.28311 | -0.31414 | -0.3568 | -0.37084 | -0.23706 | 0.010205 | -0.095794 | -118.4572 | -0.11695 | -0.077866 | 0.003172 | -118.6639 | 118.3787 | -0.3233 | 118.3695 | 118.3326 | -0.04605 | -0.36595 | -0.37999 | -0.048215 | -0.1261 | 118.6259 | 0.15851 | 0.20673 | -0.087021 | -0.005983 | 118.3016 | 118.2589 | 118.2449 | 118.3561 | -0.24621 | 118.4988 | 118.5379 | 118.6189 | 118.5199 | -118.6731
1151.0781 | 118.9545 | -118.7622 | 0.004578 | -0.005418 | -0.053591 | 0.068663 | -0.010229 | -0.0059463 | 0.01101 | -0.011751 | -0.0011537 | -0.001658 | -0.0052279 | 0.019134 | -0.010099 | 0.028518 | 0.019721 | -0.012988 | -0.048597 | -0.082062 | -0.1007 | 0.042258 | 0.010205 | -0.091215 | -118.5579 | -0.13526 | -0.091601 | -0.010564 | -118.7738 | 118.8045 | -0.053175 | 118.7907 | 118.7492 | -0.055246 | -0.08664 | -0.10528 | -0.011622 | -0.13984 | 118.7724 | 0.20427 | 0.21589 | -0.096179 | -0.015142 | 118.7136 | 118.6801 | 118.6615 | 118.7819 | 0.03768 | 118.6269 | 118.6706 | 118.7516 | 118.671 | -118.7784
1152.7656 | 119.0689 | -118.8217 | -0.009155 | 0.002213 | -0.053805 | 0.068663 | -0.010015 | -0.0061599 | 0.01101 | -0.019381 | -0.0013673 | -0.001658 | -0.0050143 | 0.019348 | -0.010099 | 0.023939 | 0.015142 | -0.008409 | -0.03944 | -0.086641 | -0.10528 | 0.051416 | 0.014784 | -0.082058 | -118.6358 | -0.13984 | -0.09618 | -0.015142 | -118.8517 | 118.8731 | -0.030285 | 118.8457 | 118.8133 | -0.059825 | -0.077486 | -0.096124 | -0.029953 | -0.13068 | 118.8365 | 0.18594 | 0.21589 | -0.087025 | -0.005987 | 118.7823 | 118.7351 | 118.7164 | 118.8369 | 0.060571 | 118.6819 | 118.7255 | 118.8066 | 118.7397 | -118.8425
1154.5312 | 119.1696 | -118.8721 | -0.018311 | 0.009844 | -0.053805 | 0.068236 | -0.010229 | -0.0059463 | 0.010583 | -0.011751 | -0.0013673 | -0.0018716 | -0.0048007 | 0.019348 | -0.010099 | 0.028518 | 0.015142 | -0.012988 | -0.044018 | -0.086641 | -0.1007 | 0.046837 | 0.010205 | -0.095794 | -118.7136 | -0.13984 | -0.091601 | -0.015142 | -118.9204 | 118.9189 | -0.025707 | 118.9006 | 118.8591 | -0.059825 | -0.06833 | -0.082389 | -0.048282 | -0.12153 | 118.8823 | 0.15845 | 0.20673 | -0.07329 | 0.003169 | 118.8281 | 118.7854 | 118.7714 | 118.8872 | 0.065148 | 118.7322 | 118.7805 | 118.8569 | 118.7763 | -118.902
1156.2812 | 119.1101 | -118.9911 | 0.045776 | -0.005418 | -0.053805 | 0.068663 | -0.010015 | -0.0061599 | 0.010583 | -0.011751 | -0.0015809 | -0.001658 | -0.0052279 | 0.019348 | -0.0096721 | 0.023939 | 0.0243 | -0.012988 | -0.048597 | -0.086641 | -0.10528 | 0.037679 | 0.014784 | -0.095794 | -118.7731 | -0.13526 | -0.10076 | -0.010564 | -118.9936 | 119.0288 | -0.094373 | 119.015 | 118.9781 | -0.050667 | -0.13242 | -0.15105 | -0.002524 | -0.18104 | 119.0059 | 0.21795 | 0.22047 | -0.14653 | -0.05634 | 118.9425 | 118.9044 | 118.8858 | 119.0154 | -0.008097 | 118.8558 | 118.8903 | 118.9805 | 118.8953 | -119.0394
1158.0156 | 119.2474 | -119.0094 | -0.009155 | -0.02068 | -0.053805 | 0.068877 | -0.010229 | -0.0059463 | 0.010583 | -0.019381 | -0.0015809 | -0.001658 | -0.0050143 | 0.019348 | -0.0098857 | 0.028518 | 0.019721 | -0.008409 | -0.048597 | -0.095798 | -0.096121 | 0.042258 | 0.005626 | -0.082058 | -118.8556 | -0.13068 | -0.082444 | -0.015142 | -119.0623 | 119.0517 | -0.039442 | 119.0379 | 119.001 | -0.050667 | -0.086643 | -0.086966 | -0.052896 | -0.12153 | 119.015 | 0.15384 | 0.20674 | -0.073289 | -0.005987 | 118.9608 | 118.9136 | 118.9133 | 119.0291 | 0.051413 | 118.8787 | 118.927 | 118.9943 | 118.9273 | -119.0531
1159.7656 | 119.2474 | -119.101 | 0.036621 | -0.005418 | -0.053805 | 0.067809 | -0.010443 | -0.0059463 | 0.010583 | -0.011751 | -0.0017945 | -0.0018716 | -0.0048007 | 0.019134 | -0.0098857 | 0.028518 | 0.015142 | 0.000747 | -0.048597 | -0.086641 | -0.1007 | 0.042258 | 0.014784 | -0.086637 | -118.9059 | -0.13526 | -0.10076 | -0.010564 | -119.131 | 119.1432 | -0.085218 | 119.1295 | 119.1017 | -0.041511 | -0.12326 | -0.13732 | -0.030025 | -0.17188 | 119.1157 | 0.19503 | 0.22505 | -0.13738 | -0.047185 | 119.0524 | 119.0143 | 119.0003 | 119.1161 | 0.005637 | 118.9657 | 119.0002 | 119.0904 | 119.0143 | -119.1676
1161.4531 | 119.3573 | -119.1834 | 0.018311 | -0.005418 | -0.054019 | 0.068236 | -0.010229 | -0.0059463 | 0.010797 | 0.00351 | -0.0013673 | -0.0018716 | -0.0050143 | 0.019348 | -0.010099 | 0.023939 | 0.019721 | -0.008409 | -0.053175 | -0.09122 | -0.096121 | 0.042258 | 0.014784 | -0.091215 | -118.9792 | -0.13526 | -0.09618 | -0.019721 | -119.1905 | 119.2256 | -0.071486 | 119.2073 | 119.1749 | -0.050667 | -0.10953 | -0.11443 | -0.007152 | -0.15357 | 119.1981 | 0.20417 | 0.21132 | -0.11449 | -0.038032 | 119.1302 | 119.0921 | 119.0872 | 119.2031 | 0.023947 | 119.0481 | 119.0872 | 119.1636 | 119.0921 | -119.2088
1163.2188 | 119.3756 | -119.2474 | 0.018311 | -0.005418 | -0.054019 | 0.068022 | -0.010229 | -0.0057325 | 0.010583 | -0.019381 | -0.0013673 | -0.001658 | -0.0050143 | 0.019348 | -0.0094585 | 0.028518 | 0.019721 | -0.003831 | -0.03944 | -0.082062 | -0.10528 | 0.037679 | 0.010205 | -0.091215 | -119.0387 | -0.13526 | -0.091601 | -0.015142 | -119.2592 | 119.2851 | -0.057751 | 119.276 | 119.2436 | -0.04151 | -0.10037 | -0.12359 | -0.011747 | -0.15357 | 119.2576 | 0.20873 | 0.22048 | -0.10991 | -0.033453 | 119.208 | 119.1654 | 119.1422 | 119.2672 | 0.019368 | 119.1122 | 119.1558 | 119.2323 | 119.1562 | -119.2775
1164.9062 | 119.5587 | -119.2657 | 0.018311 | -0.005418 | -0.054232 | 0.068022 | -0.010443 | -0.0059463 | 0.010797 | -0.011751 | -0.0013673 | -0.001658 | -0.0050143 | 0.019562 | -0.010099 | 0.023939 | 0.010564 | -0.008409 | -0.048597 | -0.09122 | -0.1007 | 0.037679 | 0.010205 | -0.086637 | -119.1028 | -0.13526 | -0.082444 | -0.015142 | -119.3141 | 119.3034 | -0.066908 | 119.2897 | 119.2573 | -0.046088 | -0.10953 | -0.11901 | -0.048383 | -0.15357 | 119.276 | 0.16294 | 0.21132 | -0.10076 | -0.033453 | 119.2172 | 119.1745 | 119.165 | 119.2763 | 0.019368 | 119.1305 | 119.1833 | 119.2506 | 119.1791 | -119.3324
1166.6562 | 119.5267 | -119.3481 | 0.022888 | -0.005418 | -0.053805 | 0.068236 | -0.010443 | -0.0059463 | 0.010797 | -0.011751 | -0.0011537 | -0.0020852 | -0.0048007 | 0.019562 | -0.010099 | 0.033096 | 0.015142 | -0.008409 | -0.048597 | -0.086641 | -0.1007 | 0.046837 | 0.019362 | -0.091215 | -119.1623 | -0.13984 | -0.09618 | -0.015142 | -119.3737 | 119.395 | -0.071485 | 119.3812 | 119.3397 | -0.055246 | -0.10953 | -0.12359 | -0.025509 | -0.16273 | 119.3675 | 0.18581 | 0.21132 | -0.11907 | -0.03803 | 119.2995 | 119.2615 | 119.2474 | 119.3633 | 0.023949 | 119.2083 | 119.252 | 119.333 | 119.2569 | -119.3965
1168.4062 | 119.5862 | -119.4122 | 0.032043 | 0.009844 | -0.053805 | 0.06845 | -0.010015 | -0.0059463 | 0.010797 | -0.0041205 | -0.0011537 | -0.0020852 | -0.0050143 | 0.019562 | -0.0098857 | 0.028518 | 0.015142 | -0.008409 | -0.044018 | -0.09122 | -0.096121 | 0.046837 | 0.010205 | -0.091215 | -119.2127 | -0.13984 | -0.087023 | -0.010564 | -119.4378 | 119.4591 | -0.076061 | 119.4407 | 119.4038 | -0.055246 | -0.12326 | -0.12816 | -0.025527 | -0.17188 | 119.4224 | 0.19954 | 0.22506 | -0.11907 | -0.042607 | 119.3682 | 119.321 | 119.3161 | 119.4274 | 0.014794 | 119.2724 | 119.3252 | 119.4017 | 119.321 | -119.4698
1170.1562 | 119.6045 | -119.4992 | 0.036621 | 0.002213 | -0.053591 | 0.068236 | -0.010229 | -0.0057325 | 0.010583 | -0.011751 | -0.0013673 | -0.0018716 | -0.0052279 | 0.019134 | -0.0098857 | 0.033096 | 0.019721 | -0.003831 | -0.03944 | -0.095798 | -0.10528 | 0.051416 | 0.019362 | -0.095794 | -119.2722 | -0.14442 | -0.09618 | -0.015142 | -119.4881 | 119.5506 | -0.076061 | 119.5323 | 119.4954 | -0.055247 | -0.13242 | -0.1419 | 0.011082 | -0.18104 | 119.5186 | 0.22699 | 0.2159 | -0.1328 | -0.051763 | 119.4598 | 119.4034 | 119.3939 | 119.5189 | 0.014795 | 119.3548 | 119.403 | 119.4841 | 119.4034 | -119.5247
1171.8438 | 119.7006 | -119.5129 | 0.027466 | -0.005418 | -0.053378 | 0.068236 | -0.010229 | -0.0059463 | 0.010797 | -0.011751 | -0.0011537 | -0.0018716 | -0.0052279 | 0.019348 | -0.0098857 | 0.033096 | 0.019721 | -0.003831 | -0.048597 | -0.086641 | -0.1007 | 0.046837 | 0.010205 | -0.091215 | -119.3272 | -0.13526 | -0.09618 | -0.015142 | -119.5385 | 119.5598 | -0.076063 | 119.546 | 119.5091 | -0.050668 | -0.11411 | -0.12817 | -0.025553 | -0.16273 | 119.5231 | 0.18578 | 0.21133 | -0.12365 | -0.042608 | 119.4643 | 119.4263 | 119.4122 | 119.5327 | 0.019371 | 119.3777 | 119.4168 | 119.4978 | 119.4217 | -119.566
1173.5938 | 119.8242 | -119.545 | 0.009155 | -0.013049 | -0.053805 | 0.06845 | -0.010229 | -0.0061599 | 0.010583 | -0.019381 | -0.0011537 | -0.0018716 | -0.0050143 | 0.019562 | -0.0098857 | 0.023939 | 0.015142 | -0.012988 | -0.044018 | -0.09122 | -0.10528 | 0.042258 | 0.010205 | -0.091215 | -119.3821 | -0.13984 | -0.09618 | -0.019721 | -119.5934 | 119.5872 | -0.053173 | 119.5689 | 119.532 | -0.055246 | -0.10037 | -0.11443 | -0.048455 | -0.14899 | 119.5552 | 0.16287 | 0.21133 | -0.10533 | -0.028876 | 119.501 | 119.4538 | 119.4397 | 119.5601 | 0.033103 | 119.4051 | 119.4488 | 119.5253 | 119.4538 | -119.6026
1175.3438 | 119.8105 | -119.6228 | 0.013733 | 0.002213 | -0.054019 | 0.068236 | -0.010229 | -0.0061599 | 0.010369 | -0.011751 | -0.0015809 | -0.0018716 | -0.0052279 | 0.019134 | -0.010099 | 0.023939 | 0.019721 | -0.003831 | -0.044018 | -0.086641 | -0.10986 | 0.042258 | 0.010205 | -0.095794 | -119.4279 | -0.13526 | -0.091601 | -0.019721 | -119.653 | 119.6651 | -0.057751 | 119.6467 | 119.619 | -0.046089 | -0.10037 | -0.12359 | -0.030159 | -0.14899 | 119.633 | 0.19491 | 0.22507 | -0.10533 | -0.033454 | 119.5788 | 119.5362 | 119.5129 | 119.6425 | 0.028525 | 119.4875 | 119.5312 | 119.6031 | 119.527 | -119.6667
1177.1094 | 119.8517 | -119.6457 | 0.018311 | -0.005418 | -0.053805 | 0.06845 | -0.010229 | -0.0061599 | 0.010583 | -0.0041205 | -0.0013673 | -0.001658 | -0.0052279 | 0.019348 | -0.0098857 | 0.023939 | 0.019721 | -0.017566 | -0.034862 | -0.086641 | -0.1007 | 0.042258 | 0.010205 | -0.095794 | -119.4691 | -0.13068 | -0.10534 | -0.0243 | -119.6942 | 119.6879 | -0.053173 | 119.6696 | 119.6281 | -0.059824 | -0.10495 | -0.11901 | -0.048481 | -0.14899 | 119.6559 | 0.17659 | 0.22507 | -0.12365 | -0.042611 | 119.6108 | 119.559 | 119.545 | 119.6654 | 0.023947 | 119.515 | 119.5404 | 119.6214 | 119.5499 | -119.7125
1178.8594 | 119.9112 | -119.7098 | 0 | 0.002213 | -0.054232 | 0.06845 | -0.010443 | -0.0059463 | 0.010583 | 0.00351 | -0.0011537 | -0.0018716 | -0.0048007 | 0.019348 | -0.010099 | 0.023939 | 0.019721 | -0.008409 | -0.044018 | -0.086641 | -0.10528 | 0.042258 | 0.005626 | -0.086637 | -119.524 | -0.13984 | -0.09618 | -0.019721 | -119.7445 | 119.752 | -0.044018 | 119.7337 | 119.7014 | -0.050667 | -0.086641 | -0.10528 | -0.034761 | -0.13984 | 119.7154 | 0.18573 | 0.22049 | -0.09618 | -0.019721 | 119.6658 | 119.6231 | 119.6045 | 119.7295 | 0.042258 | 119.5699 | 119.6136 | 119.6901 | 119.6231 | -119.7445
1180.5469 | 119.9615 | -119.751 | 0.032043 | -0.005418 | -0.054232 | 0.068022 | -0.010015 | -0.0057325 | 0.010797 | -0.0041205 | -0.0013673 | -0.001658 | -0.0054417 | 0.019562 | -0.010099 | 0.023939 | 0.019721 | -0.008409 | -0.044018 | -0.086641 | -0.10528 | 0.042258 | 0.014784 | -0.091215 | -119.5653 | -0.13984 | -0.10076 | -0.015142 | -119.7812 | 119.7932 | -0.076061 | 119.7749 | 119.7426 | -0.050667 | -0.11868 | -0.13732 | -0.030192 | -0.17188 | 119.7658 | 0.18572 | 0.21591 | -0.1328 | -0.047185 | 119.707 | 119.6643 | 119.6457 | 119.7707 | 0.010215 | 119.6111 | 119.6502 | 119.7358 | 119.6598 | -119.8132
1182.2969 | 120.0531 | -119.7693 | 0.009155 | -0.013049 | -0.053805 | 0.068022 | -0.010229 | -0.0061599 | 0.010369 | -0.027012 | -0.0013673 | -0.001658 | -0.0052279 | 0.019562 | -0.010099 | 0.028518 | 0.019721 | -0.003831 | -0.03944 | -0.086641 | -0.1007 | 0.051416 | 0.014784 | -0.086637 | -119.6065 | -0.13984 | -0.09618 | -0.015142 | -119.8361 | 119.8207 | -0.048595 | 119.7978 | 119.7655 | -0.055247 | -0.095796 | -0.10985 | -0.066828 | -0.14899 | 119.7841 | 0.16282 | 0.22965 | -0.10533 | -0.024297 | 119.7298 | 119.6826 | 119.6686 | 119.789 | 0.042261 | 119.6294 | 119.6731 | 119.7541 | 119.6827 | -119.8453
1183.9844 | 120.0897 | -119.8105 | 0.009155 | -0.013049 | -0.054019 | 0.068236 | -0.010015 | -0.0059463 | 0.010156 | -0.019381 | -0.0013673 | -0.0020852 | -0.0048007 | 0.019348 | -0.010099 | 0.028518 | 0.019721 | -0.008409 | -0.03944 | -0.082062 | -0.1007 | 0.042258 | 0.019362 | -0.091215 | -119.6477 | -0.13984 | -0.091601 | -0.015142 | -119.8727 | 119.8527 | -0.048595 | 119.839 | 119.8021 | -0.050667 | -0.091217 | -0.10985 | -0.06226 | -0.14899 | 119.8298 | 0.16281 | 0.22507 | -0.10076 | -0.024297 | 119.771 | 119.7284 | 119.7098 | 119.8302 | 0.033103 | 119.6706 | 119.7189 | 119.7953 | 119.7193 | -119.8819
1185.7344 | 120.1218 | -119.8791 | 0.022888 | -0.013049 | -0.054019 | 0.068022 | -0.010015 | -0.0059463 | 0.010583 | -0.011751 | -0.0011537 | -0.0018716 | -0.0050143 | 0.019562 | -0.010099 | 0.023939 | 0.019721 | -0.012988 | -0.048597 | -0.082062 | -0.1007 | 0.046837 | 0.010205 | -0.095794 | -119.6935 | -0.13984 | -0.10076 | -0.015142 | -119.9185 | 119.926 | -0.071485 | 119.9031 | 119.8662 | -0.059825 | -0.10495 | -0.12359 | -0.039384 | -0.16273 | 119.8894 | 0.18569 | 0.22507 | -0.12365 | -0.03803 | 119.8306 | 119.7971 | 119.7784 | 119.8989 | 0.023949 | 119.7393 | 119.7784 | 119.864 | 119.7834 | -119.9414
1187.4219 | 120.1996 | -119.8975 | 0.004578 | -0.005418 | -0.054019 | 0.068236 | -0.010229 | -0.0059463 | 0.010156 | -0.019381 | -0.00094006 | -0.0020852 | -0.0048007 | 0.019348 | -0.0096721 | 0.028518 | 0.019721 | -0.008409 | -0.044018 | -0.086641 | -0.1007 | 0.051416 | 0.010205 | -0.091215 | -119.7347 | -0.13984 | -0.091601 | -0.015142 | -119.9506 | 119.9489 | -0.048596 | 119.926 | 119.8891 | -0.059825 | -0.091219 | -0.10528 | -0.053124 | -0.14442 | 119.9077 | 0.16279 | 0.21592 | -0.096179 | -0.01972 | 119.8534 | 119.8108 | 119.7968 | 119.9172 | 0.046838 | 119.7576 | 119.8059 | 119.8823 | 119.8062 | -119.9552
1189.1719 | 120.2316 | -119.9249 | 0.009155 | 0.002213 | -0.053805 | 0.068236 | -0.010229 | -0.0059463 | 0.010583 | -0.011751 | -0.0013673 | -0.0018716 | -0.0052279 | 0.019562 | -0.0098857 | 0.028518 | 0.015142 | -0.003831 | -0.03944 | -0.082062 | -0.1007 | 0.051416 | 0.014784 | -0.095794 | -119.7713 | -0.13984 | -0.09618 | -0.015142 | -119.9918 | 119.9763 | -0.048595 | 119.9534 | 119.9211 | -0.055247 | -0.091217 | -0.10985 | -0.066868 | -0.14899 | 119.9397 | 0.15363 | 0.2205 | -0.10533 | -0.024297 | 119.8855 | 119.8429 | 119.8242 | 119.9401 | 0.042261 | 119.7851 | 119.8287 | 119.9098 | 119.8291 | -120.001
1190.9219 | 120.2728 | -119.9615 | 0 | -0.005418 | -0.054232 | 0.068022 | -0.010443 | -0.0059463 | 0.010369 | -0.011751 | -0.0013673 | -0.001658 | -0.0048007 | 0.019775 | -0.0096721 | 0.028518 | 0.019721 | -0.008409 | -0.03944 | -0.082062 | -0.1007 | 0.037679 | 0.019362 | -0.086637 | -119.8125 | -0.13984 | -0.10534 | -0.019721 | -120.0284 | 119.9992 | -0.03944 | 119.9901 | 119.9531 | -0.046088 | -0.082062 | -0.1007 | -0.066877 | -0.13984 | 119.9809 | 0.14904 | 0.21592 | -0.10534 | -0.019721 | 119.9221 | 119.8795 | 119.8608 | 119.9813 | 0.037679 | 119.8217 | 119.8562 | 119.9418 | 119.8749 | -120.0284
1192.6094 | 120.2728 | -120.0256 | 0.018311 | -0.013049 | -0.054232 | 0.068236 | -0.0098017 | -0.0059463 | 0.010583 | -0.0041205 | -0.0013673 | -0.001658 | -0.0048007 | 0.019348 | -0.0098857 | 0.028518 | 0.019721 | 0.000747 | -0.048597 | -0.082062 | -0.10528 | 0.042258 | 0.019362 | -0.086637 | -119.8491 | -0.14442 | -0.10076 | -0.010564 | -120.0696 | 120.0679 | -0.066908 | 120.0542 | 120.0264 | -0.041511 | -0.10037 | -0.12359 | -0.044 | -0.16273 | 120.045 | 0.1765 | 0.2205 | -0.11907 | -0.028875 | 119.977 | 119.9436 | 119.9204 | 120.0454 | 0.023947 | 119.8812 | 119.9249 | 120.0151 | 119.939 | -120.0879
1194.3594 | 120.2499 | -120.0668 | 0.009155 | -0.005418 | -0.054232 | 0.06845 | -0.010015 | -0.0061599 | 0.010583 | -0.019381 | -0.0011537 | -0.0014444 | -0.0052279 | 0.019562 | -0.0094585 | 0.028518 | 0.0243 | -0.008409 | -0.044018 | -0.086641 | -0.1007 | 0.042258 | 0.010205 | -0.091215 | -119.8766 | -0.13526 | -0.09618 | -0.015142 | -120.1063 | 120.1091 | -0.053173 | 120.0954 | 120.0584 | -0.050667 | -0.095796 | -0.10985 | -0.039432 | -0.14441 | 120.077 | 0.19022 | 0.22966 | -0.10533 | -0.024297 | 120.0228 | 119.9802 | 119.9661 | 120.0911 | 0.033103 | 119.9316 | 119.9707 | 120.0517 | 119.9756 | -120.1154
1196.125 | 120.2957 | -120.108 | 0.059509 | 0.009844 | -0.054232 | 0.068236 | -0.010229 | -0.0061599 | 0.010797 | -0.011751 | -0.0011537 | -0.0018716 | -0.0052279 | 0.019562 | -0.0096721 | 0.028518 | 0.015142 | -0.008409 | -0.044018 | -0.09122 | -0.1007 | 0.051416 | 0.010205 | -0.091215 | -119.9178 | -0.13984 | -0.09618 | -0.019721 | -120.1475 | 120.1594 | -0.10353 | 120.1365 | 120.0996 | -0.059825 | -0.15073 | -0.16021 | -0.039443 | -0.19935 | 120.1182 | 0.19021 | 0.22966 | -0.15569 | -0.07923 | 120.064 | 120.0168 | 120.0073 | 120.1232 | -0.008093 | 119.9682 | 120.0119 | 120.0883 | 120.0168 | -120.207
1197.8281 | 120.4422 | -120.1126 | 0.009155 | 0.002213 | -0.054019 | 0.068236 | -0.010229 | -0.0063735 | 0.010583 | -0.011751 | -0.0013673 | -0.001658 | -0.0052279 | 0.019348 | -0.0098857 | 0.033096 | 0.019721 | 0.000747 | -0.048597 | -0.086641 | -0.1007 | 0.042258 | 0.014784 | -0.091215 | -119.9544 | -0.13526 | -0.091601 | -0.015142 | -120.1704 | 120.1549 | -0.057752 | 120.1457 | 120.1134 | -0.041511 | -0.095796 | -0.10985 | -0.057759 | -0.14441 | 120.1274 | 0.15816 | 0.21592 | -0.10076 | -0.024297 | 120.064 | 120.026 | 120.0119 | 120.1323 | 0.033103 | 119.9774 | 120.021 | 120.0975 | 120.0214 | -120.1795
1199.7188 | 120.4742 | -120.1401 | 0 | -0.005418 | -0.054232 | 0.068022 | -0.010443 | -0.0061599 | 0.010156 | -0.0041205 | -0.0011537 | -0.0014444 | -0.0052279 | 0.019562 | -0.0096721 | 0.033096 | 0.015142 | -0.003831 | -0.044018 | -0.086641 | -0.096121 | 0.051416 | 0.019362 | -0.095794 | -119.9865 | -0.13984 | -0.09618 | -0.015142 | -120.2116 | 120.1915 | -0.044018 | 120.1732 | 120.1362 | -0.055247 | -0.086641 | -0.096121 | -0.071502 | -0.13984 | 120.1594 | 0.15358 | 0.22508 | -0.09618 | -0.015142 | 120.0961 | 120.0534 | 120.044 | 120.1552 | 0.051416 | 120.0002 | 120.0439 | 120.1249 | 120.0443 | -120.2116
1201.4688 | 120.4926 | -120.1767 | -0.009155 | -0.005418 | -0.054446 | 0.068022 | -0.010443 | -0.0061599 | 0.010369 | -0.027012 | -0.0011537 | -0.0018716 | -0.0052279 | 0.019775 | -0.010099 | 0.023939 | 0.015142 | -0.012988 | -0.048597 | -0.086641 | -0.1007 | 0.046837 | 0.010205 | -0.091215 | -120.0185 | -0.13526 | -0.10076 | -0.015142 | -120.2436 | 120.2235 | -0.039442 | 120.2006 | 120.1637 | -0.059825 | -0.077486 | -0.091545 | -0.066933 | -0.1261 | 120.1869 | 0.15815 | 0.22508 | -0.091604 | -0.005987 | 120.1281 | 120.0901 | 120.076 | 120.1918 | 0.055992 | 120.0414 | 120.0759 | 120.1616 | 120.0855 | -120.2345
1203.2188 | 120.3873 | -120.2637 | 0.027466 | -0.005418 | -0.054232 | 0.068236 | -0.010443 | -0.0059463 | 0.010156 | -0.011751 | -0.0013673 | -0.0020852 | -0.0054417 | 0.019775 | -0.0098857 | 0.023939 | 0.019721 | -0.008409 | -0.03944 | -0.086641 | -0.10528 | 0.042258 | 0.014784 | -0.095794 | -120.046 | -0.13984 | -0.09618 | -0.019721 | -120.2757 | 120.3059 | -0.066906 | 120.2876 | 120.2553 | -0.050667 | -0.11411 | -0.13275 | -0.012009 | -0.1673 | 120.2785 | 0.21765 | 0.22966 | -0.12365 | -0.047187 | 120.2242 | 120.177 | 120.1584 | 120.2834 | 0.014792 | 120.1238 | 120.1675 | 120.244 | 120.1679 | -120.3031
1204.9688 | 120.4559 | -120.2591 | 0.041199 | -0.005418 | -0.054446 | 0.068022 | -0.010229 | -0.0059463 | 0.010583 | -0.0041205 | -0.0011537 | -0.0018716 | -0.0052279 | 0.019775 | -0.010313 | 0.028518 | 0.019721 | -0.008409 | -0.053175 | -0.086641 | -0.096121 | 0.051416 | 0.010205 | -0.10037 | -120.0781 | -0.13526 | -0.091601 | -0.010564 | -120.3123 | 120.3105 | -0.094374 | 120.2876 | 120.2507 | -0.059825 | -0.12784 | -0.13732 | -0.053218 | -0.17646 | 120.2693 | 0.18102 | 0.23424 | -0.1328 | -0.051763 | 120.2059 | 120.1725 | 120.163 | 120.2788 | 0.010217 | 120.1238 | 120.1675 | 120.2485 | 120.1587 | -120.3535
1206.7188 | 120.575 | -120.2682 | 0 | -0.005418 | -0.054446 | 0.068022 | -0.010656 | -0.0061599 | 0.010369 | -0.019381 | -0.0011537 | -0.0018716 | -0.0052279 | 0.019989 | -0.010313 | 0.023939 | 0.015142 | -0.003831 | -0.048597 | -0.082062 | -0.1007 | 0.042258 | 0.023941 | -0.095794 | -120.1101 | -0.14442 | -0.09618 | -0.015142 | -120.3352 | 120.3105 | -0.048597 | 120.2922 | 120.2644 | -0.046089 | -0.082062 | -0.1007 | -0.066956 | -0.14442 | 120.2922 | 0.15813 | 0.22508 | -0.09618 | -0.015142 | 120.2197 | 120.1862 | 120.1675 | 120.2834 | 0.042258 | 120.1238 | 120.1721 | 120.2531 | 120.1725 | -120.3352
1208.4688 | 120.4559 | -120.3278 | 0.018311 | -0.013049 | -0.054232 | 0.068022 | -0.0098017 | -0.0061599 | 0.010369 | -0.011751 | -0.0015809 | -0.0014444 | -0.0050143 | 0.019775 | -0.010313 | 0.023939 | 0.015142 | -0.008409 | -0.044018 | -0.082062 | -0.1007 | 0.046837 | 0.014784 | -0.091215 | -120.133 | -0.14899 | -0.09618 | -0.019721 | -120.3581 | 120.3746 | -0.062329 | 120.3517 | 120.3194 | -0.055246 | -0.10037 | -0.11901 | -0.030341 | -0.16731 | 120.3425 | 0.19474 | 0.22508 | -0.11449 | -0.038032 | 120.2837 | 120.2457 | 120.2271 | 120.3429 | 0.028526 | 120.1788 | 120.2316 | 120.308 | 120.2365 | -120.3764
1210.1562 | 120.5795 | -120.3415 | -0.013733 | -0.013049 | -0.054446 | 0.068236 | -0.010229 | -0.0061599 | 0.010583 | -0.011751 | -0.0013673 | -0.0018716 | -0.0052279 | 0.019775 | -0.010099 | 0.033096 | 0.019721 | -0.012988 | -0.03944 | -0.086641 | -0.10528 | 0.042258 | 0.019362 | -0.091215 | -120.1651 | -0.13526 | -0.091601 | -0.015142 | -120.3856 | 120.3838 | -0.025707 | 120.3746 | 120.3285 | -0.055246 | -0.072908 | -0.091546 | -0.044081 | -0.12153 | 120.3609 | 0.17642 | 0.2205 | -0.077868 | -0.001409 | 120.3021 | 120.2549 | 120.2362 | 120.3612 | 0.055991 | 120.2062 | 120.2499 | 120.3264 | 120.2503 | -120.3718
1211.9062 | 120.5292 | -120.4285 | 0.032043 | 0.002213 | -0.054446 | 0.068022 | -0.010015 | -0.0061599 | 0.010369 | -0.0041205 | -0.0013673 | -0.0014444 | -0.0050143 | 0.019989 | -0.0098857 | 0.023939 | 0.0243 | -0.012988 | -0.044018 | -0.086641 | -0.10528 | 0.042258 | 0.005626 | -0.10495 | -120.1971 | -0.13984 | -0.091601 | -0.019721 | -120.4222 | 120.4707 | -0.076061 | 120.4524 | 120.4155 | -0.055246 | -0.11868 | -0.13732 | 0.006263 | -0.17188 | 120.4341 | 0.23135 | 0.22508 | -0.12364 | -0.051764 | 120.3844 | 120.3418 | 120.3232 | 120.4528 | 0.010215 | 120.2886 | 120.3369 | 120.4087 | 120.3235 | -120.4542
1213.6562 | 120.6573 | -120.3873 | -0.004578 | -0.013049 | -0.054232 | 0.068236 | -0.010656 | -0.0059463 | 0.010583 | -0.011751 | -0.0013673 | -0.001658 | -0.0054417 | 0.019775 | -0.010099 | 0.028518 | 0.015142 | -0.008409 | -0.048597 | -0.082062 | -0.091543 | 0.046837 | 0.010205 | -0.095794 | -120.2246 | -0.14899 | -0.09618 | -0.019721 | -120.4543 | 120.4341 | -0.044019 | 120.4158 | 120.3789 | -0.055246 | -0.077484 | -0.086965 | -0.066987 | -0.14442 | 120.3975 | 0.16268 | 0.22966 | -0.091602 | -0.015143 | 120.3387 | 120.3052 | 120.2957 | 120.4024 | 0.051415 | 120.2383 | 120.2911 | 120.3675 | 120.2915 | -120.4497
1215.3594 | 120.6665 | -120.4193 | 0.004578 | -0.013049 | -0.054232 | 0.067809 | -0.010229 | -0.0059463 | 0.010583 | -0.0041205 | -0.0015809 | -0.0018716 | -0.0052279 | 0.019348 | -0.010099 | 0.033096 | 0.019721 | -0.012988 | -0.044018 | -0.09122 | -0.10986 | 0.046837 | 0.014784 | -0.10037 | -120.2429 | -0.13526 | -0.10076 | -0.028878 | -120.4817 | 120.4661 | -0.048596 | 120.4524 | 120.4063 | -0.059825 | -0.095798 | -0.11443 | -0.062416 | -0.13984 | 120.4341 | 0.17641 | 0.23882 | -0.10534 | -0.033456 | 120.3753 | 120.3281 | 120.3095 | 120.439 | 0.042259 | 120.2841 | 120.3186 | 120.3904 | 120.3189 | -120.4863
1217.1094 | 120.694 | -120.4514 | 0.004578 | 0.002213 | -0.054232 | 0.068022 | -0.010229 | -0.0059463 | 0.010369 | -0.019381 | -0.0013673 | -0.0014444 | -0.0052279 | 0.019775 | -0.010099 | 0.023939 | 0.015142 | 0.000747 | -0.044018 | -0.082062 | -0.1007 | 0.046837 | 0.019362 | -0.095794 | -120.275 | -0.13984 | -0.09618 | -0.019721 | -120.5 | 120.4982 | -0.048596 | 120.4753 | 120.4521 | -0.04609 | -0.08664 | -0.10528 | -0.048688 | -0.14442 | 120.4707 | 0.1764 | 0.22509 | -0.10076 | -0.024299 | 120.4073 | 120.3693 | 120.3507 | 120.4665 | 0.042259 | 120.3115 | 120.3552 | 120.4316 | 120.3556 | -120.5046
1218.7969 | 120.726 | -120.4605 | 0.004578 | -0.013049 | -0.054446 | 0.068022 | -0.010015 | -0.0059463 | 0.010583 | -0.027012 | -0.0011537 | -0.0020852 | -0.0052279 | 0.020203 | -0.010099 | 0.028518 | 0.019721 | -0.008409 | -0.044018 | -0.082062 | -0.1007 | 0.042258 | 0.019362 | -0.10037 | -120.2979 | -0.13526 | -0.10076 | -0.015142 | -120.5275 | 120.5028 | -0.048596 | 120.489 | 120.4521 | -0.050667 | -0.08664 | -0.10528 | -0.067006 | -0.13984 | 120.4799 | 0.16266 | 0.22967 | -0.10534 | -0.01972 | 120.4165 | 120.3784 | 120.3598 | 120.4802 | 0.03768 | 120.3252 | 120.3598 | 120.4454 | 120.3601 | -120.5321
1220.5469 | 120.6894 | -120.52 | 0.013733 | -0.013049 | -0.054446 | 0.067809 | -0.010015 | -0.0063735 | 0.010369 | -0.019381 | -0.0013673 | -0.0014444 | -0.0052279 | 0.019989 | -0.0098857 | 0.033096 | 0.019721 | -0.003831 | -0.048597 | -0.086641 | -0.1007 | 0.042258 | 0.019362 | -0.095794 | -120.3253 | -0.13526 | -0.10076 | -0.0243 | -120.5504 | 120.5623 | -0.06233 | 120.5531 | 120.5162 | -0.046089 | -0.10037 | -0.11443 | -0.03039 | -0.14899 | 120.5394 | 0.1947 | 0.22509 | -0.11449 | -0.038033 | 120.4714 | 120.4334 | 120.4193 | 120.5397 | 0.028525 | 120.3848 | 120.4193 | 120.4957 | 120.4242 | -120.5641
1222.25 | 120.7397 | -120.5063 | 0.004578 | -0.005418 | -0.054446 | 0.068022 | -0.010656 | -0.0059463 | 0.010797 | -0.019381 | -0.0011537 | -0.001658 | -0.0052279 | 0.019562 | -0.010099 | 0.033096 | 0.0243 | 0.000747 | -0.044018 | -0.077483 | -0.096121 | 0.042258 | 0.014784 | -0.095794 | -120.3436 | -0.14899 | -0.10076 | -0.028878 | -120.5687 | 120.5485 | -0.048596 | 120.5394 | 120.507 | -0.041511 | -0.082061 | -0.1007 | -0.062439 | -0.15357 | 120.5211 | 0.16265 | 0.22509 | -0.10534 | -0.033456 | 120.4623 | 120.4288 | 120.4102 | 120.5306 | 0.03768 | 120.3573 | 120.4055 | 120.4774 | 120.4105 | -120.5733
1224 | 120.7214 | -120.5795 | 0.018311 | 0.002213 | -0.05466 | 0.067809 | -0.010443 | -0.0061599 | 0.010156 | -0.011751 | -0.0015809 | -0.0020852 | -0.0050143 | 0.019989 | -0.0098857 | 0.028518 | 0.019721 | -0.008409 | -0.044018 | -0.077483 | -0.1007 | 0.051416 | 0.010205 | -0.10495 | -120.3665 | -0.13984 | -0.10076 | -0.019721 | -120.6008 | 120.6309 | -0.062329 | 120.608 | 120.5711 | -0.059825 | -0.095794 | -0.11901 | -0.021248 | -0.15815 | 120.5897 | 0.213 | 0.23425 | -0.11907 | -0.038032 | 120.5355 | 120.502 | 120.4788 | 120.5992 | 0.033105 | 120.4397 | 120.4788 | 120.5598 | 120.4746 | -120.6191
1225.75 | 120.8542 | -120.5429 | -0.013733 | -0.005418 | -0.05466 | 0.068236 | -0.010656 | -0.0059463 | 0.0099417 | -0.011751 | -0.0011537 | -0.001658 | -0.0054417 | 0.019989 | -0.0098857 | 0.028518 | 0.015142 | -0.003831 | -0.048597 | -0.086641 | -0.10528 | 0.046837 | 0.010205 | -0.095794 | -120.394 | -0.13984 | -0.09618 | -0.019721 | -120.6145 | 120.5897 | -0.034864 | 120.5714 | 120.5391 | -0.050668 | -0.072908 | -0.091546 | -0.071606 | -0.1261 | 120.5531 | 0.1489 | 0.22051 | -0.082447 | -0.005988 | 120.4943 | 120.4563 | 120.4376 | 120.558 | 0.06057 | 120.4031 | 120.4467 | 120.5232 | 120.4471 | -120.6008
1227.5 | 120.726 | -120.6024 | 0.036621 | -0.005418 | -0.054232 | 0.068022 | -0.010229 | -0.0063735 | 0.010369 | -0.0041205 | -0.0013673 | -0.001658 | -0.0052279 | 0.019775 | -0.010099 | 0.037675 | 0.051771 | -0.012988 | -0.048597 | -0.082062 | -0.1007 | 0.055995 | 0.010205 | -0.091215 | -120.4123 | -0.13526 | -0.09618 | -0.0243 | -120.642 | 120.6584 | -0.085218 | 120.6401 | 120.5894 | -0.068983 | -0.11868 | -0.13732 | -0.03957 | -0.17188 | 120.6126 | 0.1901 | 0.22967 | -0.1328 | -0.060921 | 120.5538 | 120.5204 | 120.5017 | 120.6542 | 0.019374 | 120.4672 | 120.5062 | 120.5781 | 120.5112 | -120.6786
1229.2031 | 120.8359 | -120.6299 | 0.032043 | -0.005418 | -0.05466 | 0.068236 | -0.010229 | -0.0059463 | 0.010583 | 0.00351 | -0.00094006 | -0.001658 | -0.0050143 | 0.019989 | -0.010099 | 0.028518 | 0.028878 | -0.008409 | -0.044018 | -0.082062 | -0.10528 | 0.055995 | 0.010205 | -0.10037 | -120.4352 | -0.13984 | -0.091601 | -0.019721 | -120.6603 | 120.6859 | -0.076061 | 120.6584 | 120.6215 | -0.064404 | -0.1141 | -0.13732 | -0.030419 | -0.17188 | 120.6401 | 0.19467 | 0.22509 | -0.12364 | -0.051764 | 120.5859 | 120.5478 | 120.5246 | 120.6588 | 0.023952 | 120.49 | 120.5383 | 120.6102 | 120.5295 | -120.6923
1230.9375 | 120.7672 | -120.6253 | 0.022888 | -0.013049 | -0.054446 | 0.068022 | -0.010443 | -0.0057325 | 0.010583 | -0.019381 | -0.0013673 | -0.0018716 | -0.0052279 | 0.019775 | -0.010313 | 0.019361 | 0.019721 | -0.008409 | -0.044018 | -0.086641 | -0.091543 | 0.042258 | 0.005626 | -0.10037 | -120.4535 | -0.13984 | -0.091601 | -0.015142 | -120.6832 | 120.6676 | -0.066906 | 120.6447 | 120.6169 | -0.050667 | -0.10953 | -0.11443 | -0.057891 | -0.16273 | 120.6309 | 0.17178 | 0.22967 | -0.11449 | -0.03803 | 120.5813 | 120.5387 | 120.5338 | 120.645 | 0.01937 | 120.4855 | 120.5337 | 120.6102 | 120.5249 | -120.7061
1232.6875 | 120.8954 | -120.6345 | 0.009155 | -0.013049 | -0.054232 | 0.068022 | -0.010656 | -0.0065873 | 0.010156 | -0.019381 | -0.0013673 | -0.001658 | -0.0052279 | 0.019775 | -0.010099 | 0.037675 | 0.015142 | -0.008409 | -0.044018 | -0.077483 | -0.096121 | 0.046837 | 0.014784 | -0.10495 | -120.4718 | -0.13526 | -0.09618 | -0.0243 | -120.7061 | 120.6813 | -0.053173 | 120.6721 | 120.6261 | -0.055246 | -0.086638 | -0.10528 | -0.07163 | -0.14441 | 120.6492 | 0.16262 | 0.23425 | -0.10533 | -0.033455 | 120.5904 | 120.557 | 120.5383 | 120.6496 | 0.037682 | 120.4992 | 120.5383 | 120.6102 | 120.5295 | -120.7152
1234.4531 | 120.8633 | -120.694 | 0.036621 | -0.005418 | -0.054232 | 0.067809 | -0.010443 | -0.0059463 | 0.010369 | -0.011751 | -0.0013673 | -0.0020852 | -0.0052279 | 0.019989 | -0.010099 | 0.028518 | 0.0243 | -0.008409 | -0.048597 | -0.082062 | -0.096121 | 0.046837 | 0.010205 | -0.10495 | -120.4947 | -0.14442 | -0.09618 | -0.019721 | -120.7244 | 120.7408 | -0.085218 | 120.7225 | 120.6856 | -0.055246 | -0.11868 | -0.13274 | -0.030436 | -0.18104 | 120.7042 | 0.19923 | 0.22967 | -0.1328 | -0.056342 | 120.6454 | 120.6119 | 120.5978 | 120.7183 | 0.010216 | 120.5496 | 120.5978 | 120.6742 | 120.589 | -120.761
1236.1406 | 120.9045 | -120.7031 | 0.018311 | -0.005418 | -0.05466 | 0.068022 | -0.010229 | -0.0061599 | 0.010156 | -0.011751 | -0.0015809 | -0.0020852 | -0.0052279 | 0.019348 | -0.010313 | 0.023939 | 0.051771 | -0.008409 | -0.048597 | -0.086641 | -0.10528 | 0.046837 | 0.001048 | -0.095794 | -120.5131 | -0.13526 | -0.09618 | -0.019721 | -120.7473 | 120.75 | -0.066908 | 120.7271 | 120.6947 | -0.055246 | -0.10495 | -0.12359 | -0.044175 | -0.15357 | 120.7042 | 0.19007 | 0.23425 | -0.11449 | -0.038032 | 120.6545 | 120.6165 | 120.5978 | 120.7549 | 0.028526 | 120.5679 | 120.6069 | 120.6834 | 120.6073 | -120.7656
1237.8906 | 120.8862 | -120.7443 | 0.018311 | 0.002213 | -0.05466 | 0.068022 | -0.010443 | -0.0068009 | 0.010156 | -0.011751 | -0.0017945 | -0.0018716 | -0.0052279 | 0.019989 | -0.0098857 | 0.028518 | 0.05635 | -0.008409 | -0.048597 | -0.072904 | -0.10528 | 0.051416 | 0.010205 | -0.10037 | -120.5268 | -0.13984 | -0.09618 | -0.019721 | -120.761 | 120.7957 | -0.066908 | 120.7728 | 120.7359 | -0.059825 | -0.091215 | -0.12359 | -0.016712 | -0.15815 | 120.7545 | 0.21754 | 0.23425 | -0.11449 | -0.038032 | 120.6957 | 120.6714 | 120.639 | 120.8007 | 0.033105 | 120.6045 | 120.6481 | 120.7246 | 120.644 | -120.7793
1239.6562 | 120.9 | -120.7306 | 0.036621 | 0.002213 | -0.05466 | 0.067809 | -0.010443 | -0.0072283 | 0.010156 | -0.0041205 | -0.0015809 | -0.0020852 | -0.0052279 | 0.019989 | -0.010313 | 0.033096 | 0.060928 | -0.008409 | -0.044018 | -0.086641 | -0.10528 | 0.051416 | 0.014784 | -0.10037 | -120.5543 | -0.13526 | -0.09618 | -0.015142 | -120.7794 | 120.782 | -0.080639 | 120.7637 | 120.7222 | -0.059825 | -0.12326 | -0.1419 | -0.04876 | -0.17188 | 120.7454 | 0.17633 | 0.22509 | -0.1328 | -0.051763 | 120.6866 | 120.644 | 120.6253 | 120.7915 | 0.014795 | 120.5953 | 120.6344 | 120.7154 | 120.6302 | -120.816
1241.3438 | 120.9229 | -120.7855 | 0.036621 | 0.002213 | -0.055087 | 0.068022 | -0.010229 | -0.0072283 | 0.010369 | -0.011751 | -0.0015809 | -0.001658 | -0.0054417 | 0.019775 | -0.0098857 | 0.023939 | 0.05635 | -0.003831 | -0.048597 | -0.09122 | -0.10528 | 0.051416 | 0.010205 | -0.10495 | -120.5726 | -0.14442 | -0.09618 | -0.015142 | -120.8022 | 120.8369 | -0.085218 | 120.8095 | 120.7817 | -0.055247 | -0.12784 | -0.1419 | -0.016723 | -0.18104 | 120.7957 | 0.21295 | 0.22967 | -0.1328 | -0.051763 | 120.7369 | 120.6943 | 120.6802 | 120.8419 | 0.014795 | 120.6411 | 120.6893 | 120.7704 | 120.6806 | -120.8389
1243.0938 | 120.9824 | -120.7947 | 0.022888 | -0.005418 | -0.054873 | 0.068022 | -0.010229 | -0.0070145 | 0.010369 | -0.019381 | -0.0013673 | -0.0018716 | -0.0052279 | 0.019775 | -0.010099 | 0.033096 | 0.051771 | -0.008409 | -0.057754 | -0.086641 | -0.096121 | 0.046837 | 0.014784 | -0.10953 | -120.5863 | -0.14442 | -0.09618 | -0.019721 | -120.8206 | 120.8415 | -0.080642 | 120.8278 | 120.7863 | -0.055246 | -0.10953 | -0.11901 | -0.025883 | -0.1673 | 120.8095 | 0.20837 | 0.23425 | -0.11907 | -0.042609 | 120.7369 | 120.708 | 120.6986 | 120.8464 | 0.023949 | 120.6503 | 120.6985 | 120.775 | 120.6851 | -120.8434
1245.4688 | 121.0464 | -120.7718 | 0.018311 | 0.002213 | -0.05466 | 0.067809 | -0.010443 | -0.0070145 | 0.0099417 | -0.011751 | -0.0013673 | -0.0020852 | -0.0052279 | 0.019989 | -0.010313 | 0.033096 | 0.019721 | -0.008409 | -0.044018 | -0.082062 | -0.1007 | 0.046837 | 0.010205 | -0.10495 | -120.6092 | -0.13984 | -0.09618 | -0.019721 | -120.848 | 120.8186 | -0.062329 | 120.8049 | 120.7634 | -0.055246 | -0.10037 | -0.11901 | -0.076244 | -0.15815 | 120.782 | 0.16259 | 0.23883 | -0.11449 | -0.038032 | 120.7278 | 120.6897 | 120.6711 | 120.7915 | 0.028526 | 120.632 | 120.6756 | 120.7521 | 120.6668 | -120.8663
1248.7812 | 121.0648 | -120.8038 | 0 | -0.005418 | -0.05466 | 0.067809 | -0.010015 | -0.0070145 | 0.010156 | -0.011751 | -0.0013673 | -0.0018716 | -0.0050143 | 0.019562 | -0.010099 | 0.037675 | 0.060928 | -0.003831 | -0.044018 | -0.09122 | -0.1007 | 0.046837 | 0.014784 | -0.10495 | -120.6504 | -0.14442 | -0.091601 | -0.015142 | -120.8709 | 120.8507 | -0.044018 | 120.8415 | 120.8 | -0.050668 | -0.09122 | -0.1007 | -0.067095 | -0.14442 | 120.8186 | 0.15342 | 0.22052 | -0.091601 | -0.015142 | 120.7598 | 120.7126 | 120.7031 | 120.8648 | 0.046837 | 120.6594 | 120.7122 | 120.7887 | 120.6989 | -120.8709
1252.2656 | 121.1014 | -120.8405 | 0.009155 | -0.013049 | -0.05466 | 0.067809 | -0.010443 | -0.0072283 | 0.0097281 | -0.011751 | -0.0013673 | -0.001658 | -0.0052279 | 0.019989 | -0.010099 | 0.033096 | 0.060928 | -0.008409 | -0.044018 | -0.095798 | -0.096121 | 0.042258 | 0.019362 | -0.10037 | -120.6641 | -0.12152 | -0.091601 | -0.005985 | -120.9076 | 120.8827 | -0.053173 | 120.8735 | 120.832 | -0.050667 | -0.10495 | -0.10528 | -0.067104 | -0.13068 | 120.8598 | 0.17631 | 0.24341 | -0.10076 | -0.01514 | 120.7964 | 120.7447 | 120.7443 | 120.9014 | 0.033103 | 120.7189 | 120.7489 | 120.8345 | 120.7401 | -120.9167
1257.8594 | 121.1243 | -120.9045 | 0.022888 | -0.005418 | -0.05466 | 0.067595 | -0.010656 | -0.0072283 | 0.0099417 | -0.0041205 | -0.0013673 | -0.0020852 | -0.0050143 | 0.019775 | -0.0096721 | 0.028518 | 0.0243 | -0.003831 | -0.03944 | -0.086641 | -0.091543 | 0.051416 | 0.005626 | -0.10495 | -120.7191 | -0.13068 | -0.087023 | -0.005985 | -120.9488 | 120.956 | -0.062328 | 120.9331 | 120.9007 | -0.055247 | -0.10953 | -0.11443 | -0.044227 | -0.15357 | 120.9102 | 0.18545 | 0.22968 | -0.10991 | -0.028873 | 120.8651 | 120.8179 | 120.813 | 120.9288 | 0.028528 | 120.7739 | 120.8175 | 120.8986 | 120.7996 | -120.9717
1259.6406 | 121.1334 | -120.9229 | 0.054932 | 0.002213 | -0.054873 | 0.067809 | -0.010015 | -0.0072283 | 0.0099417 | -0.0041205 | -0.0013673 | -0.0018716 | -0.0054417 | 0.019775 | -0.010527 | 0.033096 | 0.019721 | 0.000747 | -0.044018 | -0.082062 | -0.1007 | 0.055995 | 0.019362 | -0.10495 | -120.7328 | -0.13068 | -0.087023 | -0.010564 | -120.9717 | 120.9788 | -0.09895 | 120.9559 | 120.9236 | -0.055248 | -0.13699 | -0.15563 | -0.04881 | -0.18561 | 120.9422 | 0.19002 | 0.23883 | -0.14195 | -0.065496 | 120.8788 | 120.8408 | 120.8222 | 120.9426 | 0.001063 | 120.7922 | 120.8358 | 120.9123 | 120.8179 | -121.0266
1261.3438 | 121.1334 | -120.9366 | 0.027466 | -0.013049 | -0.055087 | 0.067381 | -0.010229 | -0.0074419 | 0.010156 | -0.011751 | -0.0013673 | -0.001658 | -0.0054417 | 0.020203 | -0.0098857 | 0.037675 | 0.019721 | 0.005325 | -0.03944 | -0.086641 | -0.096121 | 0.051416 | 0.010205 | -0.10037 | -120.7374 | -0.1261 | -0.091601 | -0.005985 | -120.9808 | 120.988 | -0.066906 | 120.9743 | 120.9419 | -0.046091 | -0.11411 | -0.12359 | -0.044235 | -0.15357 | 120.9468 | 0.19918 | 0.24341 | -0.11907 | -0.033451 | 120.8971 | 120.8499 | 120.8405 | 120.9563 | 0.02395 | 120.8105 | 120.845 | 120.9306 | 120.8362 | -121.0083
1263.0469 | 121.0922 | -120.9641 | 0.032043 | -0.005418 | -0.054873 | 0.067809 | -0.010229 | -0.0072283 | 0.0099417 | -0.019381 | -0.00094006 | -0.0020852 | -0.0054417 | 0.019989 | -0.010099 | 0.033096 | 0.019721 | 0.000747 | -0.034862 | -0.086641 | -0.10528 | 0.051416 | 0.014784 | -0.10037 | -120.7649 | -0.13068 | -0.087023 | -0.005985 | -120.9946 | 121.0155 | -0.066905 | 120.9971 | 120.9648 | -0.050669 | -0.11868 | -0.13732 | -0.030506 | -0.16272 | 120.9788 | 0.19917 | 0.22968 | -0.11907 | -0.038028 | 120.9292 | 120.8774 | 120.8588 | 120.9838 | 0.019373 | 120.8334 | 120.877 | 120.9581 | 120.8637 | -121.0266
1264.7969 | 121.225 | -120.9412 | 0 | -0.013049 | -0.054873 | 0.067595 | -0.010443 | -0.0068009 | 0.010156 | -0.011751 | -0.0013673 | -0.0018716 | -0.0052279 | 0.019775 | -0.0096721 | 0.028518 | 0.015142 | 0.000747 | -0.044018 | -0.072904 | -0.1007 | 0.042258 | 0.005626 | -0.10953 | -120.774 | -0.1261 | -0.087023 | -0.010564 | -121.0174 | 120.9834 | -0.044018 | 120.9697 | 120.9419 | -0.041511 | -0.072904 | -0.1007 | -0.076288 | -0.1261 | 120.9468 | 0.16713 | 0.24341 | -0.087023 | -0.010564 | 120.8971 | 120.8683 | 120.8405 | 120.9563 | 0.042258 | 120.8151 | 120.8541 | 120.9306 | 120.8316 | -121.0174
1266.5625 | 121.1838 | -120.9778 | 0.018311 | -0.013049 | -0.05466 | 0.068022 | -0.010229 | -0.0072283 | 0.010156 | 0.00351 | -0.00094006 | -0.001658 | -0.0052279 | 0.019989 | -0.010099 | 0.033096 | 0.0243 | 0.000747 | -0.034862 | -0.082062 | -0.1007 | 0.051416 | 0.005626 | -0.10037 | -120.7878 | -0.13526 | -0.087023 | -0.001407 | -121.022 | 121.0292 | -0.053173 | 121.0109 | 120.9785 | -0.050669 | -0.10037 | -0.11901 | -0.044246 | -0.15357 | 120.9834 | 0.19001 | 0.23426 | -0.10533 | -0.019718 | 120.9429 | 120.8957 | 120.8771 | 121.0021 | 0.033105 | 120.8425 | 120.8908 | 120.9764 | 120.8774 | -121.0403
1268.25 | 121.1609 | -121.0007 | 0.022888 | 0.009844 | -0.054873 | 0.068022 | -0.010656 | -0.0072283 | 0.0099417 | -0.011751 | -0.0011537 | -0.0020852 | -0.0054417 | 0.020203 | -0.010313 | 0.042253 | 0.028878 | 0.000747 | -0.044018 | -0.072904 | -0.096121 | 0.055995 | 0.010205 | -0.10037 | -120.8015 | -0.1261 | -0.091601 | -0.005985 | -121.0403 | 121.0567 | -0.066906 | 121.0429 | 121.0014 | -0.055248 | -0.095792 | -0.11901 | -0.039673 | -0.14899 | 121.0109 | 0.19916 | 0.23884 | -0.11449 | -0.028873 | 120.9567 | 120.9278 | 120.9046 | 121.0295 | 0.033107 | 120.8746 | 120.9091 | 120.9947 | 120.9003 | -121.0632
1270 | 121.1975 | -121.0327 | 0.027466 | -0.005418 | -0.054446 | 0.067809 | -0.010443 | -0.0070145 | 0.0099417 | -0.019381 | -0.0011537 | -0.001658 | -0.0054417 | 0.020203 | -0.010099 | 0.037675 | 0.0243 | 0.000747 | -0.034862 | -0.086641 | -0.096121 | 0.051416 | 0.019362 | -0.11411 | -120.8152 | -0.13068 | -0.087023 | -0.015142 | -121.0541 | 121.0841 | -0.062328 | 121.0704 | 121.0335 | -0.050669 | -0.11411 | -0.12359 | -0.021365 | -0.15815 | 121.0521 | 0.21747 | 0.23883 | -0.11449 | -0.042608 | 120.9979 | 120.9461 | 120.9366 | 121.057 | 0.02395 | 120.902 | 120.9457 | 121.0176 | 120.9186 | -121.0815
1271.75 | 121.1838 | -121.0419 | 0.045776 | -0.013049 | -0.054873 | 0.068022 | -0.010656 | -0.0072283 | 0.0097281 | -0.011751 | -0.0011537 | -0.0020852 | -0.0052279 | 0.020416 | -0.010313 | 0.037675 | 0.0243 | 0.000747 | -0.03944 | -0.082062 | -0.096121 | 0.051416 | 0.010205 | -0.10953 | -120.8336 | -0.1261 | -0.082444 | -0.010564 | -121.0632 | 121.0933 | -0.085216 | 121.0795 | 121.0426 | -0.050669 | -0.12784 | -0.1419 | -0.021368 | -0.17188 | 121.0521 | 0.20831 | 0.22968 | -0.12822 | -0.05634 | 121.0024 | 120.9598 | 120.9457 | 121.0662 | 0.00564 | 120.9158 | 120.9594 | 121.0313 | 120.9323 | -121.109
1273.4375 | 121.2158 | -121.0419 | 0.018311 | -0.005418 | -0.055087 | 0.068236 | -0.010443 | -0.0070145 | 0.0099417 | -0.0041205 | -0.0015809 | -0.0020852 | -0.0054417 | 0.019775 | -0.010313 | 0.033096 | 0.019721 | 0.000747 | -0.034862 | -0.082062 | -0.10528 | 0.051416 | 0.014784 | -0.10495 | -120.8381 | -0.13068 | -0.082444 | -0.010564 | -121.077 | 121.0933 | -0.053173 | 121.075 | 121.0426 | -0.050669 | -0.10037 | -0.12359 | -0.035104 | -0.14899 | 121.0567 | 0.20373 | 0.23884 | -0.10076 | -0.028875 | 121.007 | 120.9598 | 120.9366 | 121.0616 | 0.033105 | 120.9112 | 120.9594 | 121.0313 | 120.9369 | -121.0953
1275.1094 | 121.257 | -121.0648 | 0.041199 | -0.005418 | -0.055087 | 0.067595 | -0.01087 | -0.0070145 | 0.010156 | -0.0041205 | -0.0011537 | -0.0018716 | -0.0050143 | 0.020203 | -0.0098857 | 0.028518 | 0.019721 | -0.008409 | -0.03944 | -0.082062 | -0.1007 | 0.055995 | 0.010205 | -0.10953 | -120.8565 | -0.13068 | -0.091601 | -0.015142 | -121.0907 | 121.1208 | -0.080639 | 121.0933 | 121.0563 | -0.064404 | -0.12326 | -0.1419 | -0.025953 | -0.17188 | 121.075 | 0.2083 | 0.23426 | -0.1328 | -0.056341 | 121.0253 | 120.9827 | 120.9641 | 121.0845 | 0.014796 | 120.9341 | 120.9732 | 121.0496 | 120.9552 | -121.1319
1276.7969 | 121.225 | -121.0876 | 0.027466 | -0.005418 | -0.055087 | 0.067809 | -0.010229 | -0.0072283 | 0.010369 | -0.019381 | -0.0013673 | -0.001658 | -0.0054417 | 0.020203 | -0.010099 | 0.037675 | 0.019721 | -0.008409 | -0.044018 | -0.082062 | -0.1007 | 0.051416 | 0.005626 | -0.10495 | -120.8748 | -0.13984 | -0.087023 | -0.005985 | -121.1136 | 121.1391 | -0.071484 | 121.1253 | 121.0792 | -0.059825 | -0.10953 | -0.12817 | -0.025959 | -0.1673 | 121.0933 | 0.21288 | 0.23884 | -0.11449 | -0.033451 | 121.0436 | 121.0056 | 120.9869 | 121.1074 | 0.02395 | 120.9478 | 121.0006 | 121.0817 | 120.9827 | -121.1411
1278.4844 | 121.3257 | -121.0327 | 0.022888 | -0.005418 | -0.055087 | 0.067381 | -0.010656 | -0.0072283 | 0.0099417 | -0.0041205 | -0.0011537 | -0.0020852 | -0.0052279 | 0.019989 | -0.0098857 | 0.028518 | 0.019721 | -0.003831 | -0.044018 | -0.077483 | -0.091543 | 0.051416 | 0.010205 | -0.10953 | -120.8839 | -0.13068 | -0.091601 | -0.005985 | -121.1182 | 121.0841 | -0.066906 | 121.0612 | 121.0289 | -0.055247 | -0.10037 | -0.11443 | -0.085469 | -0.15357 | 121.0429 | 0.14879 | 0.23426 | -0.11449 | -0.028873 | 120.9887 | 120.9552 | 120.9412 | 121.0524 | 0.028528 | 120.902 | 120.9411 | 121.0267 | 120.9232 | -121.1411
1280.1875 | 121.4081 | -121.0693 | 0.004578 | -0.005418 | -0.054446 | 0.067809 | -0.010443 | -0.0072283 | 0.0099417 | -0.011751 | -0.0015809 | -0.0020852 | -0.0052279 | 0.020203 | -0.010313 | 0.033096 | 0.019721 | -0.003831 | -0.034862 | -0.082062 | -0.096121 | 0.055995 | 0.010205 | -0.10037 | -120.8931 | -0.13068 | -0.087023 | -0.010564 | -121.1365 | 121.1253 | -0.03944 | 121.1024 | 121.0655 | -0.059826 | -0.08664 | -0.1007 | -0.067163 | -0.13526 | 121.0795 | 0.17625 | 0.24342 | -0.091601 | -0.015142 | 121.0345 | 120.9873 | 120.9732 | 121.0891 | 0.051417 | 120.9387 | 120.9823 | 121.0588 | 120.969 | -121.1411
1281.8906 | 121.376 | -121.0693 | 0.009155 | 0.009844 | -0.055301 | 0.067595 | -0.010656 | -0.0070145 | 0.0099417 | -0.0041205 | -0.0015809 | -0.001658 | -0.0054417 | 0.020203 | -0.010099 | 0.028518 | 0.010564 | 0.005325 | -0.034862 | -0.082062 | -0.096121 | 0.060574 | 0.005626 | -0.10953 | -120.9022 | -0.13526 | -0.087023 | -0.010564 | -121.1411 | 121.1299 | -0.044017 | 121.0979 | 121.0747 | -0.055249 | -0.091217 | -0.10528 | -0.071742 | -0.14441 | 121.075 | 0.1671 | 0.23884 | -0.096178 | -0.019719 | 121.0345 | 120.9873 | 120.9732 | 121.0799 | 0.051419 | 120.9341 | 120.9823 | 121.0588 | 120.9598 | -121.1502
1283.5781 | 121.4218 | -121.0739 | 0.013733 | 0.002213 | -0.055301 | 0.067381 | -0.01087 | -0.0070145 | 0.0099417 | -0.011751 | -0.0013673 | -0.001658 | -0.0052279 | 0.020416 | -0.010099 | 0.028518 | 0.019721 | -0.003831 | -0.034862 | -0.082062 | -0.086964 | 0.051416 | 0.010205 | -0.10953 | -120.9206 | -0.1261 | -0.091601 | -0.010564 | -121.1502 | 121.1253 | -0.048595 | 121.1024 | 121.0701 | -0.055247 | -0.095795 | -0.1007 | -0.076322 | -0.13984 | 121.0841 | 0.15336 | 0.22968 | -0.10533 | -0.024297 | 121.0391 | 120.9919 | 120.987 | 121.0936 | 0.037683 | 120.9478 | 120.9823 | 121.0633 | 120.9644 | -121.164
1285.3125 | 121.3257 | -121.1105 | 0.027466 | -0.013049 | -0.054873 | 0.068022 | -0.01087 | -0.0072283 | 0.0099417 | -0.011751 | -0.0013673 | -0.0020852 | -0.0054417 | 0.019989 | -0.010527 | 0.028518 | 0.0243 | 0.000747 | -0.044018 | -0.086641 | -0.091543 | 0.055995 | 0.010205 | -0.10953 | -120.9297 | -0.13068 | -0.09618 | -0.005985 | -121.1731 | 121.1665 | -0.071484 | 121.1391 | 121.1113 | -0.055248 | -0.11411 | -0.11901 | -0.062595 | -0.15815 | 121.1207 | 0.18082 | 0.24342 | -0.12365 | -0.033451 | 121.0665 | 121.0239 | 121.019 | 121.1348 | 0.028529 | 120.9799 | 121.0144 | 121.1046 | 121.001 | -121.2006
1287.0156 | 121.4035 | -121.106 | 0.009155 | -0.013049 | -0.055087 | 0.067595 | -0.010443 | -0.0070145 | 0.0099417 | -0.011751 | -0.0011537 | -0.0018716 | -0.0052279 | 0.019989 | -0.010099 | 0.042253 | 0.019721 | 0.000747 | -0.03944 | -0.082062 | -0.091543 | 0.060574 | 0.014784 | -0.10495 | -120.9434 | -0.13068 | -0.087023 | -0.015142 | -121.1823 | 121.1665 | -0.048595 | 121.1482 | 121.1067 | -0.059827 | -0.091217 | -0.1007 | -0.07633 | -0.13984 | 121.1207 | 0.16251 | 0.23884 | -0.096178 | -0.024297 | 121.0665 | 121.0239 | 121.0144 | 121.1257 | 0.051419 | 120.9753 | 121.0189 | 121.0908 | 121.001 | -121.1914
1288.7656 | 121.344 | -121.1563 | 0.032043 | 0.002213 | -0.054873 | 0.067809 | -0.010443 | -0.0072283 | 0.0099417 | -0.0041205 | -0.0015809 | -0.0018716 | -0.0052279 | 0.019989 | -0.010099 | 0.033096 | 0.0243 | -0.008409 | -0.048597 | -0.082062 | -0.10528 | 0.055995 | 0.014784 | -0.10953 | -120.9572 | -0.13068 | -0.087023 | -0.010564 | -121.1914 | 121.2123 | -0.08064 | 121.1894 | 121.1479 | -0.064404 | -0.1141 | -0.13732 | -0.035134 | -0.16272 | 121.1711 | 0.19913 | 0.23426 | -0.11907 | -0.042607 | 121.1077 | 121.0742 | 121.051 | 121.1806 | 0.023952 | 121.0256 | 121.0693 | 121.1457 | 121.0468 | -121.2235
1290.5156 | 121.3165 | -121.1792 | 0.041199 | -0.013049 | -0.055087 | 0.067595 | -0.010656 | -0.0074419 | 0.0099417 | -0.011751 | -0.0013673 | -0.0018716 | -0.0052279 | 0.020203 | -0.010099 | 0.023939 | 0.010564 | -0.003831 | -0.048597 | -0.09122 | -0.10528 | 0.046837 | 0.010205 | -0.10953 | -120.9618 | -0.1261 | -0.087023 | -0.010564 | -121.2098 | 121.226 | -0.089796 | 121.2031 | 121.1754 | -0.050668 | -0.13242 | -0.14648 | -0.030561 | -0.1673 | 121.1894 | 0.21744 | 0.248 | -0.12822 | -0.051763 | 121.1306 | 121.088 | 121.0739 | 121.1898 | 0.005638 | 121.0531 | 121.0922 | 121.1686 | 121.0697 | -121.251
1292.2188 | 121.4172 | -121.1517 | -0.004578 | -0.013049 | -0.055301 | 0.067381 | -0.010656 | -0.0072283 | 0.0099417 | -0.011751 | -0.0011537 | -0.0018716 | -0.0054417 | 0.019989 | -0.010099 | 0.023939 | 0.010564 | -0.008409 | -0.048597 | -0.086641 | -0.10986 | 0.051416 | 0.010205 | -0.10953 | -120.9755 | -0.13068 | -0.091601 | -0.005985 | -121.2189 | 121.2031 | -0.044019 | 121.1757 | 121.1433 | -0.059825 | -0.082063 | -0.10528 | -0.067185 | -0.1261 | 121.1619 | 0.17623 | 0.24342 | -0.087023 | -0.001407 | 121.1031 | 121.0651 | 121.0419 | 121.1623 | 0.055994 | 121.0211 | 121.0601 | 121.1457 | 121.0422 | -121.2143
1293.9688 | 121.3577 | -121.17 | 0.041199 | 0.002213 | -0.055301 | 0.067595 | -0.01087 | -0.0072283 | 0.0099417 | -0.011751 | -0.0011537 | -0.0018716 | -0.0050143 | 0.019989 | -0.010099 | 0.019361 | 0.001407 | -0.017566 | -0.053175 | -0.095798 | -0.10528 | 0.037679 | 0.010205 | -0.10953 | -120.9892 | -0.1261 | -0.091601 | -0.005985 | -121.2281 | 121.2077 | -0.094374 | 121.1894 | 121.1525 | -0.055245 | -0.137 | -0.14648 | -0.058031 | -0.1673 | 121.1802 | 0.18081 | 0.23884 | -0.1328 | -0.047184 | 121.1169 | 121.0742 | 121.0648 | 121.1715 | -0.00352 | 121.0439 | 121.0784 | 121.1641 | 121.0605 | -121.2693
1295.6562 | 121.3623 | -121.2067 | 0.036621 | 0.002213 | -0.055087 | 0.067595 | -0.01087 | -0.0074419 | 0.0099417 | -0.019381 | -0.0013673 | -0.0018716 | -0.0052279 | 0.020203 | -0.010313 | 0.023939 | 0.010564 | -0.022144 | -0.053175 | -0.09122 | -0.10986 | 0.042258 | 0.010205 | -0.11411 | -120.9984 | -0.13068 | -0.082444 | -0.010564 | -121.2372 | 121.2489 | -0.089796 | 121.2306 | 121.1845 | -0.064402 | -0.12784 | -0.14648 | -0.030568 | -0.1673 | 121.2169 | 0.20827 | 0.23884 | -0.11907 | -0.047185 | 121.1535 | 121.1154 | 121.0968 | 121.2172 | 0.005637 | 121.076 | 121.1242 | 121.1961 | 121.0926 | -121.2739
1297.4062 | 121.3623 | -121.1975 | 0.054932 | 0.002213 | -0.055301 | 0.067595 | -0.010443 | -0.0072283 | 0.010156 | -0.0041205 | -0.0015809 | -0.0018716 | -0.0052279 | 0.019989 | -0.010099 | 0.023939 | 0.005985 | -0.012988 | -0.044018 | -0.095798 | -0.10986 | 0.037679 | 0.010205 | -0.11411 | -121.003 | -0.13068 | -0.091601 | -0.001407 | -121.251 | 121.2352 | -0.09895 | 121.2214 | 121.1845 | -0.050667 | -0.15073 | -0.16479 | -0.053459 | -0.18561 | 121.2077 | 0.19454 | 0.248 | -0.14653 | -0.056339 | 121.1535 | 121.1017 | 121.0877 | 121.2035 | -0.017253 | 121.0668 | 121.1059 | 121.1961 | 121.0834 | -121.3059
1299.1719 | 121.4996 | -121.1655 | 0.009155 | -0.005418 | -0.055514 | 0.067809 | -0.010656 | -0.0070145 | 0.0099417 | 0.00351 | -0.0013673 | -0.0018716 | -0.0052279 | 0.020203 | -0.010527 | 0.023939 | 0.010564 | -0.012988 | -0.053175 | -0.09122 | -0.10528 | 0.046837 | 0.005626 | -0.10953 | -121.0167 | -0.13526 | -0.091601 | -0.010564 | -121.2601 | 121.2123 | -0.06233 | 121.1894 | 121.1525 | -0.059825 | -0.10037 | -0.11443 | -0.094661 | -0.14441 | 121.1711 | 0.14876 | 0.24342 | -0.10076 | -0.019719 | 121.1123 | 121.0742 | 121.0602 | 121.176 | 0.037682 | 121.0302 | 121.0739 | 121.1549 | 121.0559 | -121.2693
1300.9219 | 121.5088 | -121.1975 | 0 | -0.005418 | -0.055301 | 0.068022 | -0.010656 | -0.0072283 | 0.0099417 | -0.011751 | -0.0013673 | -0.0018716 | -0.0050143 | 0.020203 | -0.010313 | 0.023939 | 0.015142 | -0.003831 | -0.044018 | -0.086641 | -0.10986 | 0.042258 | 0.001048 | -0.10037 | -121.0213 | -0.13068 | -0.087023 | -0.005985 | -121.2693 | 121.2398 | -0.044018 | 121.2214 | 121.1937 | -0.046089 | -0.086641 | -0.10986 | -0.071775 | -0.13068 | 121.1986 | 0.17622 | 0.248 | -0.087023 | -0.005985 | 121.1535 | 121.1109 | 121.0877 | 121.2127 | 0.042258 | 121.0668 | 121.1105 | 121.1915 | 121.0971 | -121.2693
1302.625 | 121.4722 | -121.2021 | 0.013733 | -0.013049 | -0.055728 | 0.067595 | -0.01087 | -0.0070145 | 0.0099417 | -0.019381 | -0.00094006 | -0.0018716 | -0.0050143 | 0.019989 | -0.010527 | 0.033096 | 0.015142 | -0.003831 | -0.044018 | -0.086641 | -0.091543 | 0.055995 | 0.001048 | -0.11411 | -121.0442 | -0.13526 | -0.087023 | -0.010564 | -121.283 | 121.2581 | -0.057751 | 121.2352 | 121.1983 | -0.059826 | -0.10037 | -0.10528 | -0.080934 | -0.14899 | 121.2031 | 0.15791 | 0.23884 | -0.10076 | -0.024297 | 121.1581 | 121.1154 | 121.1105 | 121.2172 | 0.042262 | 121.0668 | 121.1151 | 121.1915 | 121.088 | -121.2968
1304.375 | 121.5271 | -121.2158 | 0.004578 | 0.002213 | -0.055514 | 0.068022 | -0.010656 | -0.0074419 | 0.010156 | -0.019381 | -0.0011537 | -0.0018716 | -0.0054417 | 0.020416 | -0.010313 | 0.023939 | 0.010564 | -0.003831 | -0.053175 | -0.086641 | -0.10528 | 0.051416 | 0.014784 | -0.11411 | -121.0488 | -0.13068 | -0.082444 | -0.005985 | -121.283 | 121.2672 | -0.057753 | 121.2398 | 121.212 | -0.055247 | -0.091219 | -0.10986 | -0.067201 | -0.13526 | 121.2306 | 0.16706 | 0.23426 | -0.087022 | -0.010563 | 121.1626 | 121.1292 | 121.1105 | 121.2264 | 0.046838 | 121.0851 | 121.1334 | 121.2098 | 121.1017 | -121.2876
1306.1406 | 121.5454 | -121.2158 | 0.018311 | -0.013049 | -0.055514 | 0.067381 | -0.010656 | -0.0072283 | 0.0097281 | -0.011751 | -0.0011537 | -0.0018716 | -0.0054417 | 0.02063 | -0.010099 | 0.037675 | 0.015142 | -0.003831 | -0.034862 | -0.082062 | -0.096121 | 0.055995 | 0.010205 | -0.11869 | -121.0579 | -0.13068 | -0.087023 | -0.005985 | -121.3059 | 121.2718 | -0.053173 | 121.2535 | 121.212 | -0.059826 | -0.10037 | -0.11443 | -0.090095 | -0.14899 | 121.226 | 0.1579 | 0.248 | -0.10533 | -0.024296 | 121.181 | 121.1338 | 121.1197 | 121.231 | 0.037684 | 121.0851 | 121.1288 | 121.2098 | 121.0971 | -121.3242
1307.8281 | 121.5134 | -121.2204 | 0.018311 | -0.005418 | -0.055301 | 0.067595 | -0.010656 | -0.0072283 | 0.0095145 | -0.019381 | -0.0015809 | -0.0014444 | -0.0052279 | 0.019775 | -0.010313 | 0.037675 | 0.019721 | 0.000747 | -0.044018 | -0.068325 | -0.10528 | 0.051416 | 0.010205 | -0.11411 | -121.0625 | -0.12152 | -0.082444 | -0.005985 | -121.3197 | 121.2718 | -0.062329 | 121.2581 | 121.2211 | -0.050669 | -0.086636 | -0.12359 | -0.099254 | -0.13983 | 121.2306 | 0.1579 | 0.25716 | -0.10076 | -0.024296 | 121.1764 | 121.1521 | 121.1151 | 121.2401 | 0.033105 | 121.0989 | 121.138 | 121.2144 | 121.1063 | -121.338
1309.5625 | 121.5225 | -121.257 | 0.018311 | -0.005418 | -0.055301 | 0.067595 | -0.010443 | -0.0072283 | 0.0097281 | -0.019381 | -0.0011537 | -0.0018716 | -0.0052279 | 0.020203 | -0.010313 | 0.033096 | 0.019721 | 0.000747 | -0.034862 | -0.077483 | -0.096121 | 0.055995 | 0.010205 | -0.11411 | -121.0854 | -0.13068 | -0.077866 | -0.001407 | -121.3242 | 121.313 | -0.053173 | 121.2901 | 121.2578 | -0.055248 | -0.095794 | -0.11443 | -0.067212 | -0.14899 | 121.2672 | 0.17163 | 0.23884 | -0.096177 | -0.019718 | 121.2222 | 121.1795 | 121.1609 | 121.2767 | 0.037684 | 121.1263 | 121.1792 | 121.2556 | 121.1429 | -121.3425
1311.3281 | 121.5637 | -121.2479 | 0.004578 | -0.02068 | -0.055514 | 0.067381 | -0.010656 | -0.0074419 | 0.0097281 | -0.019381 | -0.0013673 | -0.001658 | -0.0054417 | 0.020416 | -0.010099 | 0.023939 | 0.019721 | 0.000747 | -0.030283 | -0.077483 | -0.091543 | 0.046837 | 0.010205 | -0.11869 | -121.0991 | -0.13526 | -0.087023 | -0.010564 | -121.3334 | 121.2947 | -0.034861 | 121.2718 | 121.2486 | -0.04609 | -0.082061 | -0.096121 | -0.085524 | -0.13984 | 121.2581 | 0.14874 | 0.23426 | -0.091601 | -0.015142 | 121.2176 | 121.1704 | 121.1563 | 121.2676 | 0.042259 | 121.1126 | 121.1608 | 121.2373 | 121.1292 | -121.338
1313.0781 | 121.5683 | -121.2387 | -0.004578 | -0.013049 | -0.055087 | 0.067381 | -0.010443 | -0.0070145 | 0.010156 | -0.011751 | -0.0013673 | -0.0014444 | -0.0052279 | 0.020203 | -0.010099 | 0.037675 | 0.0243 | 0.009904 | -0.034862 | -0.072904 | -0.082386 | 0.060574 | 0.010205 | -0.10953 | -121.1037 | -0.13526 | -0.082444 | -0.005985 | -121.3425 | 121.2993 | -0.030284 | 121.2764 | 121.2486 | -0.05067 | -0.068326 | -0.077808 | -0.10384 | -0.13068 | 121.2489 | 0.135 | 0.23884 | -0.077866 | -0.001407 | 121.2038 | 121.1658 | 121.1563 | 121.263 | 0.065152 | 121.1034 | 121.1563 | 121.2327 | 121.1292 | -121.338
1314.7656 | 121.5637 | -121.2891 | -0.009155 | 0.002213 | -0.055728 | 0.067595 | -0.010656 | -0.0074419 | 0.0097281 | -0.011751 | -0.0011537 | -0.0018716 | -0.0054417 | 0.020203 | -0.010313 | 0.033096 | 0.019721 | 0.005325 | -0.034862 | -0.082062 | -0.1007 | 0.060574 | 0.010205 | -0.11411 | -121.1129 | -0.13068 | -0.082444 | -0.005985 | -121.3517 | 121.3496 | -0.025707 | 121.3222 | 121.2944 | -0.055249 | -0.072907 | -0.091545 | -0.062641 | -0.12153 | 121.2993 | 0.1762 | 0.23884 | -0.073289 | 0.00317 | 121.2542 | 121.207 | 121.1884 | 121.3088 | 0.069729 | 121.1584 | 121.2066 | 121.2831 | 121.175 | -121.3425
1316.5156 | 121.5591 | -121.2845 | 0.018311 | -0.005418 | -0.055087 | 0.067381 | -0.010656 | -0.0072283 | 0.0097281 | -0.019381 | -0.0011537 | -0.0018716 | -0.0056553 | 0.020203 | -0.010099 | 0.033096 | 0.015142 | 0.000747 | -0.048597 | -0.077483 | -0.086964 | 0.055995 | 0.014784 | -0.10495 | -121.122 | -0.13984 | -0.087023 | -0.005985 | -121.37 | 121.3405 | -0.066908 | 121.3176 | 121.2852 | -0.055248 | -0.095794 | -0.10528 | -0.085534 | -0.15815 | 121.2993 | 0.16247 | 0.248 | -0.10533 | -0.024296 | 121.2359 | 121.207 | 121.1975 | 121.2996 | 0.037684 | 121.1446 | 121.1975 | 121.2785 | 121.1795 | -121.3883
1318.2656 | 121.5408 | -121.3257 | 0.018311 | -0.005418 | -0.055514 | 0.067381 | -0.010443 | -0.0076555 | 0.0095145 | -0.011751 | -0.0013673 | -0.0018716 | -0.0054417 | 0.02063 | -0.010527 | 0.033096 | 0.0243 | 0.005325 | -0.030283 | -0.072904 | -0.086964 | 0.055995 | 0.001048 | -0.10953 | -121.1312 | -0.13526 | -0.087023 | -0.010564 | -121.37 | 121.3817 | -0.048594 | 121.3588 | 121.331 | -0.05067 | -0.091215 | -0.10528 | -0.044335 | -0.15357 | 121.3267 | 0.19451 | 0.23884 | -0.10533 | -0.028875 | 121.2954 | 121.2528 | 121.2387 | 121.35 | 0.037684 | 121.1904 | 121.2387 | 121.3151 | 121.2162 | -121.3883
1320.0156 | 121.4767 | -121.3577 | 0.045776 | -0.005418 | -0.055301 | 0.067595 | -0.010656 | -0.0072283 | 0.0095145 | -0.0041205 | -0.0011537 | -0.001658 | -0.0054417 | 0.020203 | -0.010313 | 0.033096 | 0.019721 | 0.005325 | -0.030283 | -0.077483 | -0.10528 | 0.060574 | 0.010205 | -0.11411 | -121.1403 | -0.13526 | -0.087023 | -0.015142 | -121.3838 | 121.4183 | -0.076059 | 121.3908 | 121.3631 | -0.055249 | -0.12326 | -0.15105 | -0.026028 | -0.18104 | 121.3679 | 0.21739 | 0.24342 | -0.1328 | -0.060918 | 121.3274 | 121.2802 | 121.2524 | 121.3774 | 0.014798 | 121.2225 | 121.2707 | 121.3426 | 121.2436 | -121.4295
1321.7188 | 121.5225 | -121.3257 | 0.009155 | -0.013049 | -0.055301 | 0.067168 | -0.010443 | -0.0076555 | 0.0097281 | -0.011751 | -0.0013673 | -0.001658 | -0.0054417 | 0.020416 | -0.010527 | 0.037675 | 0.019721 | -0.003831 | -0.034862 | -0.082062 | -0.091543 | 0.055995 | 0.014784 | -0.10953 | -121.1541 | -0.13526 | -0.087023 | -0.015142 | -121.3883 | 121.3817 | -0.044017 | 121.3634 | 121.3219 | -0.059826 | -0.091217 | -0.1007 | -0.06265 | -0.14441 | 121.3405 | 0.17161 | 0.23426 | -0.096178 | -0.024297 | 121.2908 | 121.2436 | 121.2341 | 121.3454 | 0.04684 | 121.1904 | 121.2387 | 121.3105 | 121.2162 | -121.3975
1323.4844 | 121.6049 | -121.344 | 0.018311 | 0.002213 | -0.055301 | 0.067595 | -0.010656 | -0.0072283 | 0.0097281 | -0.0041205 | -0.0015809 | -0.0018716 | -0.0050143 | 0.02063 | -0.010099 | 0.033096 | 0.019721 | 0.000747 | -0.03944 | -0.082062 | -0.1007 | 0.055995 | 0.010205 | -0.11411 | -121.1495 | -0.13526 | -0.09618 | -0.015142 | -121.4021 | 121.4 | -0.057751 | 121.3771 | 121.3447 | -0.055248 | -0.10037 | -0.11901 | -0.058076 | -0.15357 | 121.3542 | 0.1945 | 0.25258 | -0.11449 | -0.033453 | 121.3046 | 121.2619 | 121.2433 | 121.3637 | 0.037684 | 121.2087 | 121.2478 | 121.3289 | 121.2299 | -121.4204
1325.1719 | 121.6232 | -121.344 | 0 | -0.005418 | -0.055301 | 0.067595 | -0.010443 | -0.0072283 | 0.0097281 | -0.011751 | -0.0011537 | -0.0018716 | -0.0054417 | 0.020416 | -0.010313 | 0.037675 | 0.019721 | 0.009904 | -0.044018 | -0.086641 | -0.096121 | 0.055995 | 0.014784 | -0.10953 | -121.1586 | -0.13526 | -0.091601 | -0.010564 | -121.4112 | 121.4 | -0.044018 | 121.3817 | 121.3539 | -0.046091 | -0.086641 | -0.096121 | -0.067234 | -0.13526 | 121.3588 | 0.18535 | 0.25258 | -0.091601 | -0.010564 | 121.3 | 121.2574 | 121.2479 | 121.3637 | 0.055995 | 121.2087 | 121.2524 | 121.3334 | 121.2345 | -121.4112
1326.9375 | 121.5958 | -121.3531 | 0.009155 | -0.02068 | -0.055514 | 0.067595 | -0.010656 | -0.0072283 | 0.0095145 | -0.019381 | -0.0013673 | -0.0018716 | -0.0054417 | 0.020416 | -0.010099 | 0.033096 | 0.019721 | 0.005325 | -0.034862 | -0.072904 | -0.082386 | 0.051416 | 0.005626 | -0.11869 | -121.177 | -0.13526 | -0.087023 | -0.015142 | -121.4158 | 121.4046 | -0.044017 | 121.3862 | 121.3585 | -0.046091 | -0.082059 | -0.091541 | -0.062658 | -0.14441 | 121.3588 | 0.17619 | 0.23884 | -0.096178 | -0.024297 | 121.3183 | 121.2802 | 121.2708 | 121.3729 | 0.042261 | 121.2179 | 121.2661 | 121.338 | 121.2345 | -121.425
1328.6875 | 121.5363 | -121.3989 | 0.045776 | -0.005418 | -0.055728 | 0.067595 | -0.01087 | -0.0072283 | 0.010156 | -0.011751 | -0.0011537 | -0.0018716 | -0.0052279 | 0.020416 | -0.010313 | 0.028518 | 0.0243 | -0.003831 | -0.034862 | -0.082062 | -0.1007 | 0.051416 | 0.005626 | -0.11869 | -121.1815 | -0.13068 | -0.091601 | -0.015142 | -121.4295 | 121.4503 | -0.080638 | 121.4274 | 121.3951 | -0.055247 | -0.12784 | -0.14648 | -0.030617 | -0.17646 | 121.4046 | 0.21738 | 0.248 | -0.13738 | -0.060918 | 121.3641 | 121.3169 | 121.2982 | 121.4232 | 0.00564 | 121.2682 | 121.3073 | 121.3838 | 121.2802 | -121.4753
1330.375 | 121.6507 | -121.3623 | 0.018311 | -0.005418 | -0.055514 | 0.067381 | -0.01087 | -0.0074419 | 0.0097281 | -0.011751 | -0.0013673 | -0.0018716 | -0.0052279 | 0.020416 | -0.010527 | 0.028518 | 0.015142 | -0.003831 | -0.044018 | -0.086641 | -0.096121 | 0.042258 | 0.001048 | -0.12327 | -121.1861 | -0.13984 | -0.087023 | -0.010564 | -121.4433 | 121.4046 | -0.062329 | 121.3908 | 121.3585 | -0.046089 | -0.10495 | -0.11443 | -0.080975 | -0.15815 | 121.3634 | 0.17619 | 0.25716 | -0.10533 | -0.028875 | 121.3183 | 121.2757 | 121.2662 | 121.3774 | 0.023947 | 121.2225 | 121.2753 | 121.3517 | 121.239 | -121.4616
1332.125 | 121.5454 | -121.4172 | 0.041199 | -0.005418 | -0.055514 | 0.067381 | -0.010656 | -0.0072283 | 0.0093007 | -0.019381 | -0.0015809 | -0.0018716 | -0.0054417 | 0.020416 | -0.010099 | 0.033096 | 0.019721 | 0.000747 | -0.044018 | -0.077483 | -0.096121 | 0.060574 | 0.005626 | -0.12327 | -121.1953 | -0.13068 | -0.082444 | -0.015142 | -121.4479 | 121.4778 | -0.085217 | 121.4503 | 121.418 | -0.059827 | -0.11868 | -0.13732 | -0.030623 | -0.17188 | 121.4229 | 0.22196 | 0.25258 | -0.12364 | -0.056341 | 121.3732 | 121.3398 | 121.3211 | 121.437 | 0.019375 | 121.2866 | 121.3348 | 121.4021 | 121.294 | -121.4891
1333.875 | 121.6599 | -121.376 | 0.004578 | -0.005418 | -0.056155 | 0.067168 | -0.01087 | -0.0070145 | 0.0097281 | -0.027012 | -0.0017945 | -0.001658 | -0.0054417 | 0.02063 | -0.010527 | 0.028518 | 0.0243 | -0.003831 | -0.034862 | -0.077483 | -0.1007 | 0.055995 | 0.010205 | -0.11411 | -121.209 | -0.13068 | -0.10076 | -0.015142 | -121.457 | 121.432 | -0.03944 | 121.4046 | 121.3722 | -0.059826 | -0.082061 | -0.10528 | -0.080978 | -0.13526 | 121.3862 | 0.16702 | 0.248 | -0.10534 | -0.01972 | 121.3412 | 121.2986 | 121.2753 | 121.4003 | 0.051417 | 121.2454 | 121.2753 | 121.3609 | 121.2619 | -121.4616
1335.5625 | 121.5729 | -121.4264 | 0.036621 | -0.005418 | -0.055087 | 0.067381 | -0.010443 | -0.0070145 | 0.0097281 | -0.011751 | -0.0011537 | -0.001658 | -0.0054417 | 0.020416 | -0.010313 | 0.033096 | 0.015142 | 0.009904 | -0.044018 | -0.086641 | -0.096121 | 0.055995 | 0.014784 | -0.11411 | -121.2182 | -0.13526 | -0.091601 | -0.019721 | -121.4616 | 121.4824 | -0.080639 | 121.4595 | 121.4363 | -0.046091 | -0.12326 | -0.13274 | -0.035203 | -0.17188 | 121.4412 | 0.20822 | 0.24342 | -0.12822 | -0.056342 | 121.3824 | 121.3398 | 121.3303 | 121.4415 | 0.019374 | 121.2911 | 121.3348 | 121.4067 | 121.3123 | -121.4982
1337.3125 | 121.6141 | -121.4172 | 0.036621 | -0.005418 | -0.055514 | 0.067595 | -0.010656 | -0.0072283 | 0.0099417 | -0.019381 | -0.00094006 | -0.0018716 | -0.0052279 | 0.02063 | -0.010313 | 0.033096 | 0.0243 | 0.009904 | -0.03944 | -0.072904 | -0.091543 | 0.046837 | 0.005626 | -0.11869 | -121.2273 | -0.13068 | -0.09618 | -0.010564 | -121.4753 | 121.4641 | -0.076061 | 121.4503 | 121.4271 | -0.036933 | -0.10952 | -0.12816 | -0.058096 | -0.1673 | 121.4229 | 0.18991 | 0.248 | -0.1328 | -0.047185 | 121.3778 | 121.3443 | 121.3257 | 121.4415 | 0.010216 | 121.2866 | 121.3211 | 121.4067 | 121.2985 | -121.512
1339.0625 | 121.6599 | -121.4172 | 0.013733 | -0.013049 | -0.055514 | 0.066954 | -0.010656 | -0.0074419 | 0.0095145 | -0.011751 | -0.0013673 | -0.002299 | -0.0054417 | 0.02063 | -0.010527 | 0.028518 | 0.015142 | -0.008409 | -0.044018 | -0.086641 | -0.1007 | 0.042258 | 0.005626 | -0.11411 | -121.2319 | -0.13526 | -0.09618 | -0.015142 | -121.4799 | 121.4595 | -0.057751 | 121.4458 | 121.4088 | -0.050667 | -0.10037 | -0.11443 | -0.062674 | -0.14899 | 121.4229 | 0.18533 | 0.248 | -0.10991 | -0.028875 | 121.3732 | 121.3306 | 121.3165 | 121.4324 | 0.028525 | 121.282 | 121.3211 | 121.4021 | 121.3031 | -121.4936
1340.8125 | 121.6187 | -121.431 | 0.032043 | 0.002213 | -0.055514 | 0.067381 | -0.01087 | -0.0072283 | 0.0099417 | -0.011751 | -0.0011537 | -0.0020852 | -0.0052279 | 0.020416 | -0.010313 | 0.019361 | 0.010564 | 0.005325 | -0.048597 | -0.086641 | -0.1007 | 0.051416 | 0.001048 | -0.11869 | -121.2365 | -0.13526 | -0.09618 | -0.015142 | -121.4845 | 121.4824 | -0.08064 | 121.4503 | 121.4363 | -0.046091 | -0.11868 | -0.13274 | -0.05352 | -0.1673 | 121.432 | 0.19448 | 0.248 | -0.12822 | -0.047185 | 121.3824 | 121.3443 | 121.3303 | 121.4415 | 0.019373 | 121.2957 | 121.3348 | 121.4158 | 121.3123 | -121.5165
1342.5625 | 121.637 | -121.4355 | 0.022888 | -0.02068 | -0.055728 | 0.067381 | -0.01087 | -0.0072283 | 0.0097281 | -0.019381 | -0.0015809 | -0.0018716 | -0.0054417 | 0.020844 | -0.010313 | 0.023939 | 0.010564 | 0.000747 | -0.048597 | -0.086641 | -0.096121 | 0.046837 | 0.014784 | -0.11869 | -121.2548 | -0.13526 | -0.091601 | -0.005985 | -121.4891 | 121.4824 | -0.071485 | 121.4595 | 121.4363 | -0.04609 | -0.10953 | -0.11901 | -0.053521 | -0.15815 | 121.4503 | 0.18075 | 0.23427 | -0.11449 | -0.028873 | 121.3869 | 121.3489 | 121.3394 | 121.4461 | 0.023949 | 121.3003 | 121.3439 | 121.4296 | 121.3169 | -121.512
1344.3125 | 121.6415 | -121.4493 | 0.022888 | -0.013049 | -0.055728 | 0.067595 | -0.010656 | -0.0072283 | 0.0097281 | -0.011751 | -0.0013673 | -0.001658 | -0.0052279 | 0.020203 | -0.010527 | 0.033096 | 0.0243 | -0.003831 | -0.044018 | -0.086641 | -0.1007 | 0.051416 | 0.010205 | -0.12327 | -121.2502 | -0.13526 | -0.091601 | -0.010564 | -121.5028 | 121.5007 | -0.066906 | 121.4824 | 121.4454 | -0.055247 | -0.10953 | -0.12359 | -0.053524 | -0.15815 | 121.4595 | 0.19906 | 0.25258 | -0.11449 | -0.033452 | 121.4053 | 121.3626 | 121.3486 | 121.4736 | 0.028528 | 121.314 | 121.3577 | 121.4387 | 121.326 | -121.5257
1346 | 121.7285 | -121.4355 | 0.022888 | 0.002213 | -0.055942 | 0.067381 | -0.01087 | -0.0074419 | 0.0095145 | -0.0041205 | -0.0011537 | -0.001658 | -0.0052279 | 0.020416 | -0.010527 | 0.019361 | 0.015142 | 0.000747 | -0.053175 | -0.082062 | -0.1007 | 0.046837 | -0.003531 | -0.11869 | -121.2594 | -0.13526 | -0.091601 | -0.019721 | -121.5074 | 121.4824 | -0.076063 | 121.4549 | 121.4363 | -0.04609 | -0.10495 | -0.12359 | -0.071836 | -0.15815 | 121.432 | 0.17617 | 0.248 | -0.11449 | -0.042609 | 121.3824 | 121.3535 | 121.3348 | 121.4507 | 0.023949 | 121.3003 | 121.3439 | 121.4158 | 121.3169 | -121.5303
1347.75 | 121.701 | -121.463 | 0.013733 | -0.005418 | -0.055942 | 0.066954 | -0.010656 | -0.0072283 | 0.0095145 | -0.019381 | -0.0017945 | -0.0018716 | -0.0054417 | 0.020844 | -0.010313 | 0.023939 | 0.010564 | 0.005325 | -0.044018 | -0.09122 | -0.1007 | 0.051416 | 0.005626 | -0.12327 | -121.264 | -0.1261 | -0.10076 | -0.015142 | -121.5165 | 121.5144 | -0.057751 | 121.487 | 121.4683 | -0.046091 | -0.10495 | -0.11443 | -0.053528 | -0.13984 | 121.4686 | 0.19906 | 0.25258 | -0.11449 | -0.028875 | 121.419 | 121.3718 | 121.3623 | 121.4736 | 0.037683 | 121.3369 | 121.3623 | 121.4479 | 121.3397 | -121.5303
1349.4375 | 121.6232 | -121.4676 | 0.041199 | -0.005418 | -0.055728 | 0.067168 | -0.01087 | -0.0072283 | 0.0097281 | -0.019381 | -0.0013673 | -0.0020852 | -0.0054417 | 0.02063 | -0.010099 | 0.019361 | 0.015142 | -0.008409 | -0.048597 | -0.09122 | -0.10528 | 0.046837 | 0.014784 | -0.11869 | -121.2777 | -0.13526 | -0.09618 | -0.015142 | -121.5211 | 121.5144 | -0.089796 | 121.487 | 121.4592 | -0.055246 | -0.13242 | -0.14648 | -0.05353 | -0.17646 | 121.4824 | 0.1899 | 0.24343 | -0.13738 | -0.056341 | 121.419 | 121.3764 | 121.3623 | 121.4827 | 0.005638 | 121.3323 | 121.3714 | 121.4524 | 121.3489 | -121.5623
1351.2031 | 121.6415 | -121.5042 | 0.045776 | -0.013049 | -0.055942 | 0.067381 | -0.010656 | -0.0074419 | 0.0095145 | -0.011751 | -0.0013673 | -0.0018716 | -0.0054417 | 0.020416 | -0.010313 | 0.014783 | 0.005985 | -0.008409 | -0.048597 | -0.086641 | -0.1007 | 0.046837 | 0.001048 | -0.11869 | -121.2823 | -0.13526 | -0.091601 | -0.015142 | -121.5303 | 121.551 | -0.094373 | 121.519 | 121.4958 | -0.055246 | -0.13242 | -0.14648 | -0.026066 | -0.18104 | 121.5053 | 0.22194 | 0.248 | -0.13738 | -0.060918 | 121.4556 | 121.4176 | 121.4035 | 121.5102 | 0.001061 | 121.369 | 121.4126 | 121.4891 | 121.3855 | -121.5761
1352.9688 | 121.6965 | -121.4722 | 0.013733 | -0.005418 | -0.055728 | 0.067168 | -0.010656 | -0.0072283 | 0.0095145 | -0.011751 | -0.0015809 | -0.001658 | -0.0054417 | 0.020203 | -0.010313 | 0.023939 | 0.001407 | -0.003831 | -0.044018 | -0.095798 | -0.10528 | 0.037679 | 0.001048 | -0.11869 | -121.2869 | -0.13984 | -0.10076 | -0.015142 | -121.544 | 121.5098 | -0.057751 | 121.4961 | 121.4683 | -0.04151 | -0.10953 | -0.11901 | -0.071846 | -0.15357 | 121.4732 | 0.18532 | 0.25716 | -0.11449 | -0.028875 | 121.4282 | 121.3764 | 121.3669 | 121.4736 | 0.023946 | 121.3323 | 121.3714 | 121.457 | 121.3535 | -121.5577
1354.7188 | 121.6461 | -121.5134 | 0.032043 | -0.005418 | -0.055728 | 0.067595 | -0.01087 | -0.0074419 | 0.0097281 | -0.0041205 | -0.0011537 | -0.0018716 | -0.0052279 | 0.020416 | -0.010099 | 0.023939 | 0.001407 | -0.008409 | -0.03944 | -0.086641 | -0.10986 | 0.046837 | 0.010205 | -0.11869 | -121.3006 | -0.13526 | -0.09618 | -0.015142 | -121.5532 | 121.5602 | -0.071483 | 121.5373 | 121.505 | -0.055246 | -0.11868 | -0.1419 | -0.039804 | -0.1673 | 121.5236 | 0.21278 | 0.25258 | -0.12822 | -0.047185 | 121.4739 | 121.4267 | 121.4035 | 121.5148 | 0.014794 | 121.3781 | 121.4172 | 121.4982 | 121.3947 | -121.5852
1356.4062 | 121.6507 | -121.5454 | 0.022888 | 0.002213 | -0.056155 | 0.067168 | -0.011297 | -0.0074419 | 0.0095145 | -0.0041205 | -0.0013673 | -0.001658 | -0.0054417 | 0.020844 | -0.010313 | 0.028518 | 0.010564 | -0.008409 | -0.048597 | -0.086641 | -0.10528 | 0.046837 | 0.001048 | -0.11869 | -121.3052 | -0.13984 | -0.09618 | -0.019721 | -121.5532 | 121.5922 | -0.071485 | 121.5739 | 121.537 | -0.055246 | -0.10953 | -0.12817 | -0.007761 | -0.16273 | 121.5465 | 0.24024 | 0.248 | -0.11907 | -0.042609 | 121.4968 | 121.4588 | 121.4401 | 121.556 | 0.023949 | 121.4056 | 121.4492 | 121.5257 | 121.4267 | -121.5761
1358.1562 | 121.6599 | -121.5637 | 0.032043 | -0.005418 | -0.055728 | 0.066954 | -0.01087 | -0.0074419 | 0.0097281 | -0.0041205 | -0.0011537 | -0.0020852 | -0.0054417 | 0.02063 | -0.010313 | 0.023939 | 0.010564 | -0.012988 | -0.048597 | -0.095798 | -0.10986 | 0.042258 | 0.001048 | -0.11869 | -121.3143 | -0.13526 | -0.091601 | -0.019721 | -121.5623 | 121.606 | -0.08064 | 121.5877 | 121.5507 | -0.055246 | -0.12784 | -0.1419 | 0.001392 | -0.1673 | 121.5648 | 0.2494 | 0.24801 | -0.12364 | -0.051764 | 121.5151 | 121.4679 | 121.4539 | 121.5743 | 0.010215 | 121.4285 | 121.4721 | 121.544 | 121.445 | -121.5944
1359.8438 | 121.7926 | -121.4951 | 0 | -0.013049 | -0.055728 | 0.067381 | -0.01087 | -0.0074419 | 0.0097281 | -0.019381 | -0.0011537 | -0.0018716 | -0.0056553 | 0.02063 | -0.010313 | 0.019361 | 0.010564 | -0.008409 | -0.057754 | -0.09122 | -0.10528 | 0.046837 | 0.005626 | -0.12327 | -121.3189 | -0.13068 | -0.09618 | -0.005985 | -121.5761 | 121.5419 | -0.057754 | 121.5144 | 121.4866 | -0.055246 | -0.09122 | -0.10528 | -0.08101 | -0.13068 | 121.5007 | 0.17615 | 0.25716 | -0.09618 | -0.005985 | 121.4373 | 121.4038 | 121.3898 | 121.5056 | 0.046837 | 121.3644 | 121.3989 | 121.4891 | 121.3718 | -121.5761
1361.5938 | 121.7194 | -121.55 | 0.032043 | 0.002213 | -0.055728 | 0.067381 | -0.010656 | -0.0074419 | 0.0095145 | -0.019381 | -0.0011537 | -0.001658 | -0.0056553 | 0.020416 | -0.010099 | 0.023939 | 0.005985 | -0.008409 | -0.048597 | -0.10038 | -0.11444 | 0.046837 | 0.005626 | -0.11869 | -121.3235 | -0.13526 | -0.091601 | -0.019721 | -121.5806 | 121.5968 | -0.08064 | 121.5739 | 121.5416 | -0.055246 | -0.13242 | -0.14648 | -0.030656 | -0.1673 | 121.5556 | 0.22651 | 0.25716 | -0.12364 | -0.051764 | 121.5014 | 121.4496 | 121.4356 | 121.556 | 0.014794 | 121.4147 | 121.4584 | 121.5303 | 121.4313 | -121.6127
1363.3438 | 121.7377 | -121.5271 | 0.032043 | -0.013049 | -0.056155 | 0.066954 | -0.011084 | -0.0070145 | 0.0095145 | -0.011751 | -0.0015809 | -0.0018716 | -0.0054417 | 0.020844 | -0.010527 | 0.023939 | 0.005985 | -0.003831 | -0.044018 | -0.095798 | -0.10528 | 0.046837 | 0.005626 | -0.12327 | -121.3326 | -0.13526 | -0.09618 | -0.005985 | -121.5898 | 121.5739 | -0.076061 | 121.551 | 121.5233 | -0.050668 | -0.12784 | -0.13732 | -0.062702 | -0.1673 | 121.5327 | 0.19446 | 0.25716 | -0.12822 | -0.038028 | 121.4831 | 121.4313 | 121.4218 | 121.5331 | 0.014794 | 121.3918 | 121.4309 | 121.5211 | 121.4038 | -121.6218
1365.0312 | 121.7422 | -121.5408 | 0.027466 | -0.005418 | -0.055942 | 0.067168 | -0.010656 | -0.0070145 | 0.0097281 | -0.019381 | -0.0011537 | -0.0014444 | -0.0054417 | 0.020416 | -0.01074 | 0.023939 | 0.005985 | -0.008409 | -0.053175 | -0.086641 | -0.10528 | 0.042258 | 0.005626 | -0.12784 | -121.3372 | -0.13984 | -0.10076 | -0.019721 | -121.599 | 121.5831 | -0.080641 | 121.5648 | 121.5324 | -0.050667 | -0.11411 | -0.13275 | -0.058127 | -0.1673 | 121.5465 | 0.20362 | 0.26174 | -0.12823 | -0.047187 | 121.4877 | 121.4542 | 121.4356 | 121.5468 | 0.014792 | 121.401 | 121.4401 | 121.5211 | 121.413 | -121.6264
1366.7812 | 121.7606 | -121.5225 | 0.004578 | -0.013049 | -0.056155 | 0.066954 | -0.010656 | -0.0072283 | 0.0095145 | -0.011751 | -0.0011537 | -0.0018716 | -0.0054417 | 0.020203 | -0.01074 | 0.023939 | 0.010564 | -0.003831 | -0.048597 | -0.09122 | -0.10528 | 0.042258 | 0.005626 | -0.12327 | -121.3464 | -0.13984 | -0.091601 | -0.015142 | -121.6035 | 121.5648 | -0.053175 | 121.5465 | 121.5187 | -0.046089 | -0.095798 | -0.10986 | -0.081016 | -0.14442 | 121.5281 | 0.17615 | 0.25716 | -0.096179 | -0.01972 | 121.4739 | 121.4313 | 121.4172 | 121.5331 | 0.03768 | 121.3827 | 121.4309 | 121.5074 | 121.3993 | -121.6081
1368.4688 | 121.7743 | -121.5454 | 0.013733 | -0.013049 | -0.055514 | 0.06674 | -0.011084 | -0.0076555 | 0.0095145 | -0.011751 | -0.0015809 | -0.0020852 | -0.0052279 | 0.02063 | -0.010527 | 0.019361 | 0.005985 | -0.003831 | -0.053175 | -0.086641 | -0.10528 | 0.037679 | 0.005626 | -0.11869 | -121.3555 | -0.13068 | -0.10076 | -0.010564 | -121.6081 | 121.5831 | -0.066908 | 121.5648 | 121.5416 | -0.04151 | -0.10037 | -0.11901 | -0.062707 | -0.14441 | 121.551 | 0.18988 | 0.25258 | -0.11449 | -0.024297 | 121.4922 | 121.4588 | 121.4401 | 121.5514 | 0.023946 | 121.4147 | 121.4447 | 121.5348 | 121.4267 | -121.6218
1370.2188 | 121.7514 | -121.5454 | 0.036621 | -0.02068 | -0.056155 | 0.067168 | -0.011084 | -0.0076555 | 0.0095145 | -0.011751 | -0.0013673 | -0.0018716 | -0.0054417 | 0.020416 | -0.010527 | 0.023939 | 0.015142 | -0.012988 | -0.057754 | -0.09122 | -0.10986 | 0.042258 | 0.010205 | -0.12784 | -121.3601 | -0.13526 | -0.09618 | -0.010564 | -121.6173 | 121.5877 | -0.094375 | 121.5693 | 121.5324 | -0.055246 | -0.12784 | -0.14648 | -0.071865 | -0.17188 | 121.5556 | 0.1853 | 0.25716 | -0.1328 | -0.047185 | 121.4877 | 121.4542 | 121.4356 | 121.5606 | 0.005637 | 121.4102 | 121.4492 | 121.5348 | 121.4176 | -121.6539
1371.9688 | 121.8384 | -121.5546 | -0.009155 | -0.005418 | -0.056369 | 0.067168 | -0.011084 | -0.0074419 | 0.0095145 | -0.019381 | -0.0013673 | -0.0018716 | -0.0052279 | 0.020416 | -0.010099 | 0.019361 | -0.003172 | -0.008409 | -0.053175 | -0.095798 | -0.11444 | 0.042258 | 0.005626 | -0.11869 | -121.3784 | -0.1261 | -0.09618 | -0.015142 | -121.6127 | 121.5968 | -0.04402 | 121.5739 | 121.5462 | -0.050667 | -0.086643 | -0.10528 | -0.058131 | -0.11695 | 121.5602 | 0.17614 | 0.23427 | -0.087025 | -0.005987 | 121.5014 | 121.4588 | 121.4401 | 121.5514 | 0.051413 | 121.4285 | 121.4584 | 121.5394 | 121.4359 | -121.6035
1373.7344 | 121.7972 | -121.5591 | 0.009155 | -0.013049 | -0.056369 | 0.067168 | -0.01087 | -0.0072283 | 0.0095145 | -0.011751 | -0.0013673 | -0.0020852 | -0.0054417 | 0.02063 | -0.010099 | 0.023939 | 0.001407 | -0.003831 | -0.057754 | -0.09122 | -0.10986 | 0.046837 | 0.001048 | -0.12327 | -121.3738 | -0.13526 | -0.09618 | -0.015142 | -121.631 | 121.606 | -0.066909 | 121.5831 | 121.5553 | -0.050668 | -0.10037 | -0.11901 | -0.071868 | -0.14441 | 121.5602 | 0.1853 | 0.25716 | -0.10533 | -0.024297 | 121.5014 | 121.4679 | 121.4493 | 121.5606 | 0.037682 | 121.4239 | 121.463 | 121.544 | 121.4359 | -121.6402
1375.4219 | 121.8658 | -121.5408 | 0 | -0.013049 | -0.056369 | 0.067595 | -0.010656 | -0.0074419 | 0.0095145 | -0.019381 | -0.0011537 | -0.002299 | -0.0052279 | 0.020844 | -0.010527 | 0.019361 | 0.010564 | -0.008409 | -0.053175 | -0.095798 | -0.10986 | 0.0331 | 0.005626 | -0.12327 | -121.3784 | -0.13526 | -0.091601 | -0.019721 | -121.631 | 121.5739 | -0.053175 | 121.5602 | 121.5324 | -0.041509 | -0.095798 | -0.10986 | -0.090178 | -0.13526 | 121.5465 | 0.16241 | 0.25258 | -0.091601 | -0.019721 | 121.4877 | 121.445 | 121.431 | 121.5514 | 0.0331 | 121.4056 | 121.4492 | 121.5211 | 121.4176 | -121.631
1377.1719 | 121.7148 | -121.582 | 0.045776 | -0.013049 | -0.056155 | 0.066954 | -0.01087 | -0.0072283 | 0.0095145 | -0.011751 | -0.0013673 | -0.0018716 | -0.0054417 | 0.020416 | -0.01074 | 0.019361 | 0.001407 | 0.000747 | -0.048597 | -0.086641 | -0.10986 | 0.046837 | 0.005626 | -0.12327 | -121.3922 | -0.13526 | -0.09618 | -0.019721 | -121.6356 | 121.6289 | -0.094373 | 121.6014 | 121.5828 | -0.04609 | -0.13242 | -0.15563 | -0.053559 | -0.18104 | 121.5877 | 0.18987 | 0.24343 | -0.14196 | -0.065497 | 121.5334 | 121.4954 | 121.4722 | 121.5834 | 0.001061 | 121.4468 | 121.4859 | 121.5623 | 121.4588 | -121.6814
1378.9219 | 121.7331 | -121.5958 | 0.036621 | -0.005418 | -0.056155 | 0.066954 | -0.011084 | -0.0074419 | 0.0093007 | -0.011751 | -0.0015809 | -0.0020852 | -0.0056553 | 0.02063 | -0.010527 | 0.028518 | 0.010564 | -0.003831 | -0.057754 | -0.10038 | -0.10528 | 0.046837 | 0.005626 | -0.12327 | -121.3922 | -0.13526 | -0.091601 | -0.010564 | -121.6493 | 121.6426 | -0.094375 | 121.6243 | 121.5919 | -0.050668 | -0.137 | -0.1419 | -0.053563 | -0.17188 | 121.6014 | 0.2036 | 0.25717 | -0.12822 | -0.047185 | 121.538 | 121.4954 | 121.4905 | 121.6063 | 0.010216 | 121.4605 | 121.5042 | 121.5852 | 121.4725 | -121.6859
1380.625 | 121.8613 | -121.5683 | -0.013733 | -0.013049 | -0.056369 | 0.067168 | -0.01087 | -0.0072283 | 0.0095145 | -0.0041205 | -0.0011537 | -0.0018716 | -0.0054417 | 0.020844 | -0.010527 | 0.019361 | 0.010564 | -0.012988 | -0.053175 | -0.095798 | -0.1007 | 0.051416 | 0.005626 | -0.12784 | -121.3876 | -0.13526 | -0.091601 | -0.015142 | -121.6631 | 121.6197 | -0.039442 | 121.5877 | 121.5553 | -0.064404 | -0.082065 | -0.086967 | -0.094765 | -0.12153 | 121.5739 | 0.18071 | 0.27548 | -0.077868 | -0.001409 | 121.5151 | 121.4725 | 121.4676 | 121.5789 | 0.065149 | 121.433 | 121.4767 | 121.5532 | 121.4405 | -121.6493
1382.3906 | 121.8292 | -121.6049 | 0 | 0.002213 | -0.055942 | 0.067381 | -0.011084 | -0.0074419 | 0.0095145 | -0.019381 | -0.0020083 | -0.0020852 | -0.0054417 | 0.020844 | -0.010527 | 0.023939 | 0.005985 | -0.003831 | -0.053175 | -0.09122 | -0.10528 | 0.037679 | -0.003531 | -0.12327 | -121.3967 | -0.13984 | -0.09618 | -0.015142 | -121.6585 | 121.6426 | -0.053175 | 121.6289 | 121.6011 | -0.04151 | -0.09122 | -0.10528 | -0.053565 | -0.13984 | 121.6014 | 0.20818 | 0.26174 | -0.09618 | -0.015142 | 121.5517 | 121.5137 | 121.4996 | 121.6109 | 0.037679 | 121.4651 | 121.5087 | 121.5898 | 121.4817 | -121.6585
1384.1406 | 121.8063 | -121.6095 | 0.027466 | -0.013049 | -0.056369 | 0.067168 | -0.010656 | -0.0072283 | 0.0093007 | -0.011751 | -0.0013673 | -0.0020852 | -0.0056553 | 0.020844 | -0.010527 | 0.014783 | 0.001407 | -0.008409 | -0.057754 | -0.086641 | -0.10528 | 0.037679 | 0.005626 | -0.11869 | -121.4059 | -0.13526 | -0.10076 | -0.015142 | -121.6676 | 121.6472 | -0.08522 | 121.6243 | 121.6011 | -0.046088 | -0.11411 | -0.13275 | -0.058145 | -0.16273 | 121.6151 | 0.2036 | 0.26174 | -0.12823 | -0.042608 | 121.5517 | 121.5229 | 121.5042 | 121.6109 | 0.010213 | 121.4742 | 121.5087 | 121.5944 | 121.4908 | -121.6951
1385.875 | 121.8613 | -121.5775 | -0.004578 | -0.013049 | -0.056155 | 0.066954 | -0.010656 | -0.0076555 | 0.0093007 | -0.0041205 | -0.0013673 | -0.0020852 | -0.0054417 | 0.021271 | -0.010313 | 0.019361 | 0.005985 | -0.003831 | -0.057754 | -0.095798 | -0.11444 | 0.037679 | 0.010205 | -0.12784 | -121.4105 | -0.13984 | -0.09618 | -0.010564 | -121.6722 | 121.6151 | -0.053176 | 121.5968 | 121.5736 | -0.04151 | -0.09122 | -0.10986 | -0.094767 | -0.13526 | 121.5877 | 0.16698 | 0.26174 | -0.091602 | -0.005986 | 121.5197 | 121.4817 | 121.463 | 121.5834 | 0.042257 | 121.4376 | 121.4813 | 121.5669 | 121.4496 | -121.6676
1387.5625 | 121.8796 | -121.5729 | -0.004578 | 0.002213 | -0.056369 | 0.067168 | -0.010656 | -0.0072283 | 0.0088735 | -0.011751 | -0.0013673 | -0.001658 | -0.0052279 | 0.021271 | -0.010527 | 0.019361 | 0.001407 | -0.008409 | -0.053175 | -0.095798 | -0.10528 | 0.037679 | -0.003531 | -0.12327 | -121.4151 | -0.13526 | -0.091601 | -0.015142 | -121.6722 | 121.6106 | -0.048597 | 121.5922 | 121.5645 | -0.046088 | -0.09122 | -0.1007 | -0.099345 | -0.13068 | 121.5693 | 0.15782 | 0.25716 | -0.087023 | -0.010564 | 121.5197 | 121.4771 | 121.4676 | 121.5743 | 0.042257 | 121.4376 | 121.4813 | 121.5577 | 121.4496 | -121.6676
1389.3281 | 121.7926 | -121.637 | 0.018311 | -0.02068 | -0.056796 | 0.066954 | -0.01087 | -0.0078693 | 0.0093007 | -0.0041205 | -0.0017945 | -0.0020852 | -0.0054417 | 0.020844 | -0.010313 | 0.014783 | 0.005985 | 0.000747 | -0.053175 | -0.086641 | -0.10986 | 0.037679 | 0.001048 | -0.12784 | -121.4242 | -0.13526 | -0.09618 | -0.005985 | -121.6814 | 121.6746 | -0.071486 | 121.6517 | 121.6377 | -0.036932 | -0.10495 | -0.12817 | -0.044415 | -0.15357 | 121.638 | 0.21275 | 0.25717 | -0.11449 | -0.024296 | 121.5838 | 121.5503 | 121.5271 | 121.6429 | 0.019368 | 121.5017 | 121.5408 | 121.631 | 121.5091 | -121.6997
1391.0781 | 121.8658 | -121.6095 | 0.027466 | -0.005418 | -0.056369 | 0.067381 | -0.01087 | -0.0072283 | 0.0093007 | -0.019381 | -0.0015809 | -0.001658 | -0.0054417 | 0.021057 | -0.010527 | 0.019361 | 0.001407 | -0.003831 | -0.057754 | -0.095798 | -0.11444 | 0.037679 | 0.001048 | -0.12327 | -121.4242 | -0.13526 | -0.091601 | -0.015142 | -121.686 | 121.6472 | -0.08522 | 121.6289 | 121.6057 | -0.04151 | -0.12326 | -0.1419 | -0.07646 | -0.16273 | 121.6105 | 0.18528 | 0.26174 | -0.11907 | -0.042608 | 121.5517 | 121.5137 | 121.4951 | 121.6109 | 0.010213 | 121.4742 | 121.5179 | 121.5944 | 121.4862 | -121.7134
1392.7812 | 121.7697 | -121.6553 | 0.054932 | -0.005418 | -0.056369 | 0.066954 | -0.011084 | -0.0074419 | 0.0093007 | -0.011751 | -0.0011537 | -0.0020852 | -0.0054417 | 0.020844 | -0.010099 | 0.014783 | 0.005985 | -0.008409 | -0.057754 | -0.10038 | -0.10528 | 0.028521 | 0.001048 | -0.13242 | -121.4334 | -0.13068 | -0.091601 | -0.010564 | -121.6997 | 121.6838 | -0.11269 | 121.6701 | 121.6469 | -0.03693 | -0.15531 | -0.16021 | -0.044421 | -0.18561 | 121.6563 | 0.2219 | 0.26632 | -0.14653 | -0.065496 | 121.5975 | 121.5549 | 121.55 | 121.6613 | -0.026411 | 121.5246 | 121.5637 | 121.6447 | 121.5228 | -121.7546
1394.5312 | 121.8018 | -121.637 | 0.018311 | 0.002213 | -0.056369 | 0.067168 | -0.01087 | -0.0070145 | 0.0090871 | -0.0041205 | -0.0015809 | -0.001658 | -0.0058689 | 0.020844 | -0.01074 | 0.019361 | 0.001407 | -0.017566 | -0.053175 | -0.095798 | -0.11444 | 0.042258 | 0.001048 | -0.12784 | -121.4425 | -0.13526 | -0.10076 | -0.010564 | -121.6951 | 121.6792 | -0.071486 | 121.6563 | 121.6194 | -0.059824 | -0.11411 | -0.13275 | -0.058152 | -0.15357 | 121.638 | 0.19443 | 0.25259 | -0.11907 | -0.028875 | 121.5838 | 121.5412 | 121.5225 | 121.6384 | 0.023947 | 121.5017 | 121.5362 | 121.6264 | 121.5091 | -121.7134
1396.2969 | 121.8384 | -121.6461 | 0.018311 | 0.002213 | -0.056155 | 0.067168 | -0.01087 | -0.0072283 | 0.0090871 | -0.011751 | -0.0013673 | -0.0018716 | -0.0054417 | 0.020844 | -0.010099 | 0.019361 | 0.001407 | -0.008409 | -0.057754 | -0.10038 | -0.10528 | 0.0331 | 0.005626 | -0.12784 | -121.4379 | -0.13068 | -0.09618 | -0.015142 | -121.7089 | 121.6792 | -0.076065 | 121.6655 | 121.6377 | -0.041509 | -0.11869 | -0.12359 | -0.062733 | -0.14899 | 121.6517 | 0.20817 | 0.2709 | -0.11449 | -0.033453 | 121.5884 | 121.5457 | 121.5408 | 121.6475 | 0.014789 | 121.5154 | 121.5499 | 121.631 | 121.5183 | -121.7272
1398 | 121.7926 | -121.6827 | 0.036621 | -0.013049 | -0.056155 | 0.066527 | -0.011084 | -0.0072283 | 0.0088735 | -0.0041205 | -0.0013673 | -0.0018716 | -0.0054417 | 0.020844 | -0.010527 | 0.023939 | -0.003172 | 0.000747 | -0.057754 | -0.09122 | -0.11444 | 0.037679 | 0.005626 | -0.12784 | -121.4517 | -0.13526 | -0.09618 | -0.015142 | -121.718 | 121.7204 | -0.094375 | 121.7067 | 121.6835 | -0.036932 | -0.12784 | -0.15106 | -0.03527 | -0.17188 | 121.6884 | 0.23105 | 0.26632 | -0.1328 | -0.051763 | 121.625 | 121.5915 | 121.5683 | 121.6796 | 0.001058 | 121.5475 | 121.5866 | 121.6676 | 121.5549 | -121.7546
1399.75 | 121.9391 | -121.6324 | -0.013733 | -0.013049 | -0.056369 | 0.066954 | -0.011084 | -0.0074419 | 0.0088735 | -0.011751 | -0.0013673 | -0.001658 | -0.0052279 | 0.020844 | -0.010527 | 0.010204 | -0.003172 | -0.008409 | -0.057754 | -0.09122 | -0.10528 | 0.037679 | 0.005626 | -0.13242 | -121.4563 | -0.13526 | -0.091601 | -0.015142 | -121.7134 | 121.6701 | -0.044021 | 121.6426 | 121.624 | -0.046088 | -0.077487 | -0.091546 | -0.081045 | -0.12153 | 121.638 | 0.17612 | 0.25717 | -0.077868 | -0.001409 | 121.5746 | 121.5412 | 121.5271 | 121.6292 | 0.051412 | 121.4971 | 121.5408 | 121.6172 | 121.5 | -121.6997
1401.5 | 121.907 | -121.6507 | 0.022888 | -0.005418 | -0.056583 | 0.066954 | -0.011084 | -0.0074419 | 0.0088735 | -0.027012 | -0.0011537 | -0.0020852 | -0.0052279 | 0.021057 | -0.010313 | 0.014783 | 0.001407 | -0.008409 | -0.053175 | -0.095798 | -0.10986 | 0.037679 | -0.003531 | -0.12784 | -121.4654 | -0.13984 | -0.09618 | -0.015142 | -121.7317 | 121.6884 | -0.076063 | 121.6655 | 121.6423 | -0.046088 | -0.11869 | -0.13275 | -0.081049 | -0.16273 | 121.6472 | 0.18527 | 0.26632 | -0.11907 | -0.03803 | 121.5975 | 121.5549 | 121.5408 | 121.6521 | 0.014791 | 121.5109 | 121.5545 | 121.6356 | 121.5229 | -121.7546
1403.25 | 121.9299 | -121.6553 | 0.009155 | 0.002213 | -0.056369 | 0.066954 | -0.011084 | -0.0076555 | 0.0090871 | -0.0041205 | -0.0015809 | -0.0018716 | -0.0052279 | 0.021057 | -0.01074 | 0.019361 | 0.001407 | -0.003831 | -0.057754 | -0.09122 | -0.10986 | 0.0331 | 0.005626 | -0.12784 | -121.4654 | -0.13984 | -0.091601 | -0.010564 | -121.7317 | 121.6884 | -0.066909 | 121.6746 | 121.6514 | -0.036931 | -0.10037 | -0.11901 | -0.076472 | -0.14899 | 121.6609 | 0.18985 | 0.26632 | -0.10076 | -0.019719 | 121.5975 | 121.5641 | 121.5454 | 121.6567 | 0.023945 | 121.5154 | 121.5637 | 121.6447 | 121.5274 | -121.7409
1404.9375 | 121.8796 | -121.669 | 0.041199 | -0.005418 | -0.056369 | 0.066954 | -0.01087 | -0.0072283 | 0.0088735 | -0.011751 | -0.0011537 | -0.0018716 | -0.0052279 | 0.021057 | -0.01074 | 0.023939 | 0.005985 | -0.008409 | -0.053175 | -0.09122 | -0.10528 | 0.037679 | 0.005626 | -0.12784 | -121.4746 | -0.13526 | -0.09618 | -0.010564 | -121.7272 | 121.7067 | -0.094374 | 121.6929 | 121.6606 | -0.046088 | -0.13242 | -0.14648 | -0.05816 | -0.17646 | 121.6746 | 0.19443 | 0.25259 | -0.13738 | -0.051763 | 121.6158 | 121.5778 | 121.5637 | 121.675 | -0.00352 | 121.5337 | 121.5728 | 121.6584 | 121.5412 | -121.7684
1406.6875 | 121.8292 | -121.6736 | 0.032043 | -0.013049 | -0.056369 | 0.066954 | -0.011084 | -0.0072283 | 0.0093007 | -0.019381 | -0.0015809 | -0.0020852 | -0.0052279 | 0.020844 | -0.010527 | 0.014783 | -0.003172 | -0.008409 | -0.057754 | -0.095798 | -0.10986 | 0.037679 | 0.005626 | -0.12784 | -121.4792 | -0.13526 | -0.09618 | -0.019721 | -121.7409 | 121.7113 | -0.089797 | 121.6884 | 121.6652 | -0.046088 | -0.12784 | -0.1419 | -0.067319 | -0.1673 | 121.6792 | 0.19443 | 0.26175 | -0.12822 | -0.051764 | 121.6158 | 121.5778 | 121.5637 | 121.6704 | 0.005636 | 121.5383 | 121.5774 | 121.6539 | 121.5457 | -121.7729
1408.4375 | 121.8521 | -121.6873 | 0.027466 | -0.005418 | -0.056369 | 0.06674 | -0.011297 | -0.0074419 | 0.0090871 | -0.011751 | -0.0017945 | -0.0018716 | -0.0052279 | 0.021057 | -0.010313 | 0.010204 | -0.003172 | -0.008409 | -0.053175 | -0.095798 | -0.10986 | 0.037679 | 0.001048 | -0.13242 | -121.4883 | -0.13068 | -0.087023 | -0.015142 | -121.7501 | 121.725 | -0.080641 | 121.6975 | 121.6789 | -0.046088 | -0.12326 | -0.13732 | -0.062744 | -0.15815 | 121.6884 | 0.199 | 0.26175 | -0.11449 | -0.042608 | 121.6341 | 121.5915 | 121.5775 | 121.6841 | 0.010213 | 121.5566 | 121.6003 | 121.6722 | 121.5549 | -121.7775
1410.1875 | 121.962 | -121.669 | -0.009155 | -0.005418 | -0.056369 | 0.066954 | -0.011084 | -0.0074419 | 0.0090871 | -0.011751 | -0.0013673 | -0.001658 | -0.0056553 | 0.020844 | -0.010313 | 0.014783 | 0.001407 | 0.000747 | -0.053175 | -0.09122 | -0.11444 | 0.037679 | 0.005626 | -0.12784 | -121.4975 | -0.13526 | -0.087023 | -0.010564 | -121.7546 | 121.7067 | -0.04402 | 121.6838 | 121.6698 | -0.036932 | -0.082065 | -0.10528 | -0.085633 | -0.1261 | 121.6746 | 0.17153 | 0.25717 | -0.077868 | -0.001409 | 121.6158 | 121.5778 | 121.5546 | 121.6704 | 0.046834 | 121.5337 | 121.582 | 121.6584 | 121.5412 | -121.7455
1411.875 | 121.9482 | -121.6507 | 0.018311 | -0.013049 | -0.056796 | 0.067168 | -0.01087 | -0.0074419 | 0.0090871 | -0.019381 | -0.0015809 | -0.001658 | -0.0056553 | 0.021271 | -0.010527 | 0.014783 | 0.005985 | -0.008409 | -0.057754 | -0.095798 | -0.10528 | 0.042258 | -0.003531 | -0.137 | -121.4975 | -0.13526 | -0.087023 | -0.015142 | -121.7592 | 121.693 | -0.076065 | 121.6655 | 121.6423 | -0.050667 | -0.11411 | -0.12359 | -0.10852 | -0.15357 | 121.6472 | 0.15322 | 0.26175 | -0.10533 | -0.033453 | 121.5929 | 121.5549 | 121.5454 | 121.6567 | 0.023947 | 121.5154 | 121.5637 | 121.6356 | 121.5137 | -121.7775
1413.625 | 121.843 | -121.7056 | 0.032043 | -0.005418 | -0.056369 | 0.06674 | -0.01087 | -0.0076555 | 0.0086597 | -0.011751 | -0.0015809 | -0.0020852 | -0.0058689 | 0.02063 | -0.010313 | 0.010204 | 0.001407 | -0.003831 | -0.062332 | -0.09122 | -0.10986 | 0.0331 | -0.00811 | -0.12784 | -121.4975 | -0.13984 | -0.091601 | -0.010564 | -121.7592 | 121.7387 | -0.094375 | 121.7158 | 121.7018 | -0.036931 | -0.12326 | -0.1419 | -0.053591 | -0.17188 | 121.6975 | 0.20815 | 0.26175 | -0.12364 | -0.042607 | 121.6433 | 121.6144 | 121.5958 | 121.707 | 0.001057 | 121.5658 | 121.614 | 121.6951 | 121.5778 | -121.7913
1415.375 | 121.8338 | -121.7056 | 0.032043 | -0.005418 | -0.056369 | 0.067168 | -0.011297 | -0.0072283 | 0.0093007 | -0.019381 | -0.0013673 | -0.001658 | -0.0054417 | 0.021271 | -0.010527 | 0.014783 | -0.003172 | -0.003831 | -0.053175 | -0.10038 | -0.10986 | 0.0331 | 0.010205 | -0.13242 | -121.5112 | -0.13068 | -0.087023 | -0.010564 | -121.773 | 121.7387 | -0.085218 | 121.7204 | 121.7018 | -0.036931 | -0.13242 | -0.1419 | -0.067328 | -0.16272 | 121.7158 | 0.19442 | 0.26175 | -0.11907 | -0.042607 | 121.6525 | 121.6053 | 121.5958 | 121.7025 | 0.001057 | 121.5749 | 121.6186 | 121.6951 | 121.5732 | -121.805
1417.0625 | 121.9162 | -121.701 | 0.032043 | -0.005418 | -0.056583 | 0.067168 | -0.011084 | -0.0072283 | 0.0090871 | -0.011751 | -0.0013673 | -0.001658 | -0.0052279 | 0.020844 | -0.010527 | 0.014783 | 0.001407 | -0.003831 | -0.062332 | -0.095798 | -0.10986 | 0.042258 | 0.001048 | -0.12784 | -121.5066 | -0.13984 | -0.087023 | -0.015142 | -121.7821 | 121.7433 | -0.094375 | 121.7158 | 121.6972 | -0.046089 | -0.12784 | -0.1419 | -0.081062 | -0.17188 | 121.7021 | 0.19442 | 0.27548 | -0.11907 | -0.047185 | 121.6387 | 121.6053 | 121.5912 | 121.7025 | 0.010215 | 121.5612 | 121.614 | 121.6859 | 121.5732 | -121.8142
1418.8125 | 121.8704 | -121.7148 | 0.054932 | 0.002213 | -0.056796 | 0.066954 | -0.01087 | -0.0074419 | 0.0090871 | -0.0041205 | -0.0011537 | -0.001658 | -0.0052279 | 0.021057 | -0.010527 | 0.014783 | -0.003172 | -0.008409 | -0.053175 | -0.10496 | -0.11444 | 0.0331 | 0.001048 | -0.12327 | -121.5158 | -0.13068 | -0.087023 | -0.019721 | -121.7867 | 121.7479 | -0.10811 | 121.7296 | 121.7064 | -0.041509 | -0.15989 | -0.16937 | -0.071908 | -0.18561 | 121.7158 | 0.199 | 0.2709 | -0.14195 | -0.074653 | 121.6616 | 121.6098 | 121.6003 | 121.7116 | -0.021832 | 121.5841 | 121.6278 | 121.6951 | 121.5915 | -121.8416
1420.5 | 121.907 | -121.701 | 0.018311 | 0.002213 | -0.05701 | 0.066954 | -0.011084 | -0.0074419 | 0.0088735 | -0.019381 | -0.0011537 | -0.0014444 | -0.0054417 | 0.021271 | -0.010527 | 0.010204 | -0.003172 | -0.008409 | -0.062332 | -0.095798 | -0.11444 | 0.0331 | 0.005626 | -0.13242 | -121.5249 | -0.13068 | -0.087023 | -0.015142 | -121.7913 | 121.7341 | -0.080643 | 121.7113 | 121.6926 | -0.041509 | -0.11411 | -0.13275 | -0.09022 | -0.14899 | 121.7067 | 0.1761 | 0.26632 | -0.10533 | -0.033453 | 121.6387 | 121.6053 | 121.5866 | 121.6979 | 0.014789 | 121.5704 | 121.614 | 121.6859 | 121.5686 | -121.8096
1422.25 | 121.9528 | -121.7056 | 0.018311 | -0.013049 | -0.056796 | 0.06674 | -0.01087 | -0.0074419 | 0.0088735 | -0.019381 | -0.0013673 | -0.0020852 | -0.0056553 | 0.021057 | -0.010527 | 0.010204 | 0.001407 | -0.008409 | -0.06691 | -0.095798 | -0.10986 | 0.037679 | 0.010205 | -0.137 | -121.5341 | -0.13068 | -0.087023 | -0.010564 | -121.7867 | 121.7433 | -0.085221 | 121.7158 | 121.6972 | -0.046088 | -0.11411 | -0.12817 | -0.081064 | -0.14899 | 121.7158 | 0.17153 | 0.25259 | -0.10533 | -0.028875 | 121.6387 | 121.6098 | 121.5958 | 121.707 | 0.019368 | 121.5749 | 121.6186 | 121.6951 | 121.5686 | -121.805
1424 | 122.0169 | -121.7056 | -0.018311 | 0.002213 | -0.056796 | 0.066527 | -0.011084 | -0.0076555 | 0.0088735 | -0.0041205 | -0.0013673 | -0.0018716 | -0.0052279 | 0.020844 | -0.010954 | 0.014783 | -0.007751 | -0.012988 | -0.057754 | -0.10038 | -0.11444 | 0.0331 | 0.001048 | -0.137 | -121.5341 | -0.13068 | -0.087023 | -0.015142 | -121.8004 | 121.7387 | -0.039443 | 121.7204 | 121.6926 | -0.046088 | -0.082066 | -0.096125 | -0.094801 | -0.11237 | 121.7067 | 0.17153 | 0.26633 | -0.068712 | 0.003169 | 121.6479 | 121.6053 | 121.5912 | 121.6979 | 0.051411 | 121.5749 | 121.6186 | 121.6905 | 121.5686 | -121.7821
1425.6875 | 121.9025 | -121.7514 | 0.036621 | -0.005418 | -0.056796 | 0.06674 | -0.011084 | -0.0076555 | 0.0090871 | -0.011751 | -0.0011537 | -0.0018716 | -0.0056553 | 0.021271 | -0.010527 | 0.014783 | -0.007751 | -0.008409 | -0.057754 | -0.10038 | -0.11444 | 0.037679 | 0.001048 | -0.137 | -121.5295 | -0.13984 | -0.091601 | -0.015142 | -121.8096 | 121.7891 | -0.094375 | 121.7662 | 121.743 | -0.046088 | -0.137 | -0.15106 | -0.058181 | -0.17646 | 121.7525 | 0.22188 | 0.28006 | -0.12822 | -0.051763 | 121.6936 | 121.651 | 121.637 | 121.7437 | 0.001058 | 121.6116 | 121.6598 | 121.7363 | 121.6144 | -121.8462
1427.4375 | 121.9757 | -121.7285 | 0 | -0.013049 | -0.056796 | 0.066527 | -0.011297 | -0.0078693 | 0.0093007 | -0.011751 | -0.0013673 | -0.0018716 | -0.0054417 | 0.021271 | -0.010954 | 0.010204 | -0.003172 | -0.008409 | -0.057754 | -0.09122 | -0.11901 | 0.042258 | 0.005626 | -0.13242 | -121.5387 | -0.13068 | -0.09618 | -0.010564 | -121.8096 | 121.7708 | -0.057754 | 121.7387 | 121.7201 | -0.050667 | -0.09122 | -0.11901 | -0.081069 | -0.13068 | 121.7341 | 0.18984 | 0.2709 | -0.09618 | -0.010564 | 121.6708 | 121.6373 | 121.6095 | 121.7253 | 0.042258 | 121.5978 | 121.6323 | 121.718 | 121.5961 | -121.8096
1429.2031 | 121.9116 | -121.7422 | 0.009155 | -0.005418 | -0.056796 | 0.06674 | -0.011084 | -0.0078693 | 0.0088735 | -0.011751 | -0.0011537 | -0.0018716 | -0.0054417 | 0.021057 | -0.01074 | 0.014783 | -0.003172 | -0.017566 | -0.057754 | -0.095798 | -0.11444 | 0.028521 | 0.001048 | -0.13242 | -121.5478 | -0.13984 | -0.091601 | -0.010564 | -121.8142 | 121.7708 | -0.066909 | 121.757 | 121.7247 | -0.046087 | -0.10495 | -0.12359 | -0.071915 | -0.14899 | 121.7433 | 0.19441 | 0.26633 | -0.10076 | -0.019719 | 121.6845 | 121.6465 | 121.6278 | 121.7391 | 0.019366 | 121.6024 | 121.6506 | 121.7317 | 121.6098 | -121.8233
1430.8906 | 121.9299 | -121.7606 | 0.036621 | 0.002213 | -0.056583 | 0.06674 | -0.011084 | -0.0074419 | 0.0088735 | -0.0041205 | -0.0015809 | -0.0018716 | -0.0056553 | 0.021057 | -0.010527 | 0.014783 | -0.007751 | -0.008409 | -0.062332 | -0.095798 | -0.10528 | 0.028521 | 0.001048 | -0.14158 | -121.5478 | -0.13984 | -0.091601 | -0.010564 | -121.8187 | 121.7891 | -0.098953 | 121.7753 | 121.7522 | -0.03693 | -0.13242 | -0.1419 | -0.058184 | -0.17646 | 121.7616 | 0.21272 | 0.2709 | -0.12822 | -0.047185 | 121.6982 | 121.6648 | 121.6553 | 121.7528 | -0.0081 | 121.6207 | 121.669 | 121.75 | 121.619 | -121.8554
1432.6406 | 121.8887 | -121.8155 | 0.032043 | -0.005418 | -0.056583 | 0.066527 | -0.01087 | -0.0074419 | 0.0088735 | -0.0041205 | -0.0013673 | -0.0018716 | -0.0052279 | 0.021057 | -0.010527 | 0.019361 | 0.001407 | -0.008409 | -0.057754 | -0.10038 | -0.10986 | 0.042258 | 0.001048 | -0.14158 | -121.5524 | -0.13526 | -0.091601 | -0.015142 | -121.8187 | 121.8577 | -0.089797 | 121.8349 | 121.8071 | -0.050667 | -0.13242 | -0.1419 | -0.003252 | -0.1673 | 121.8165 | 0.26307 | 0.26633 | -0.12364 | -0.047185 | 121.7577 | 121.7151 | 121.7056 | 121.8169 | 0.010215 | 121.6802 | 121.7239 | 121.8003 | 121.6739 | -121.8508
1434.3594 | 122.0261 | -121.7468 | 0.009155 | -0.005418 | -0.056583 | 0.066527 | -0.01087 | -0.0074419 | 0.0090871 | -0.011751 | -0.0015809 | -0.001658 | -0.0056553 | 0.020844 | -0.010527 | 0.014783 | 0.001407 | -0.008409 | -0.053175 | -0.09122 | -0.10986 | 0.0331 | -0.00811 | -0.14158 | -121.5662 | -0.13526 | -0.091601 | -0.015142 | -121.8325 | 121.7799 | -0.06233 | 121.7616 | 121.7384 | -0.041509 | -0.10037 | -0.11901 | -0.085653 | -0.14441 | 121.7387 | 0.18067 | 0.26633 | -0.10076 | -0.024297 | 121.6937 | 121.6556 | 121.637 | 121.7482 | 0.023945 | 121.6116 | 121.6552 | 121.7317 | 121.6052 | -121.8416
1436.1094 | 122.0123 | -121.7606 | 0.013733 | -0.013049 | -0.056796 | 0.066313 | -0.011084 | -0.0072283 | 0.0088735 | -0.011751 | -0.0013673 | -0.0020852 | -0.0054417 | 0.021271 | -0.010527 | 0.019361 | -0.003172 | -0.017566 | -0.062332 | -0.09122 | -0.10986 | 0.0331 | -0.003531 | -0.13242 | -121.5662 | -0.13068 | -0.091601 | -0.010564 | -121.8325 | 121.7937 | -0.076065 | 121.7799 | 121.743 | -0.050666 | -0.10495 | -0.12359 | -0.07192 | -0.14441 | 121.757 | 0.19441 | 0.26633 | -0.10533 | -0.024297 | 121.6982 | 121.6693 | 121.6507 | 121.7574 | 0.019367 | 121.6299 | 121.669 | 121.75 | 121.6281 | -121.8462
1437.8594 | 121.9986 | -121.756 | 0.022888 | -0.005418 | -0.056796 | 0.066527 | -0.011084 | -0.0074419 | 0.0090871 | -0.019381 | -0.0013673 | -0.001658 | -0.0052279 | 0.021057 | -0.010527 | 0.014783 | -0.003172 | -0.008409 | -0.062332 | -0.09122 | -0.11444 | 0.0331 | -0.00811 | -0.137 | -121.5707 | -0.13068 | -0.087023 | -0.010564 | -121.8416 | 121.7891 | -0.08522 | 121.7708 | 121.7476 | -0.041509 | -0.11411 | -0.13732 | -0.085656 | -0.15357 | 121.7479 | 0.18525 | 0.2709 | -0.10991 | -0.033452 | 121.6936 | 121.6648 | 121.6415 | 121.7528 | 0.010212 | 121.6253 | 121.669 | 121.7454 | 121.619 | -121.8645
1439.5469 | 122.0032 | -121.7377 | 0.027466 | -0.013049 | -0.056583 | 0.065886 | -0.010656 | -0.0076555 | 0.0088735 | -0.011751 | -0.0013673 | -0.0018716 | -0.0052279 | 0.021271 | -0.010527 | 0.019361 | -0.003172 | -0.012988 | -0.053175 | -0.09122 | -0.10528 | 0.042258 | 0.001048 | -0.137 | -121.5753 | -0.13526 | -0.09618 | -0.010564 | -121.8371 | 121.7799 | -0.080641 | 121.757 | 121.7247 | -0.055246 | -0.11869 | -0.13275 | -0.099387 | -0.16273 | 121.7387 | 0.16236 | 0.26175 | -0.12365 | -0.03803 | 121.6845 | 121.6465 | 121.6324 | 121.7345 | 0.014792 | 121.6024 | 121.6415 | 121.7271 | 121.6007 | -121.8645
1441.3125 | 121.9482 | -121.7697 | 0.041199 | 0.002213 | -0.056583 | 0.066527 | -0.011297 | -0.0072283 | 0.0088735 | -0.011751 | -0.0015809 | -0.0020852 | -0.0056553 | 0.021271 | -0.010527 | 0.014783 | -0.007751 | -0.017566 | -0.053175 | -0.09122 | -0.10528 | 0.0331 | 0.001048 | -0.137 | -121.5707 | -0.13984 | -0.09618 | -0.010564 | -121.8416 | 121.8028 | -0.094374 | 121.7845 | 121.7521 | -0.050666 | -0.13242 | -0.14648 | -0.071923 | -0.18104 | 121.7708 | 0.19898 | 0.2709 | -0.13738 | -0.051763 | 121.7165 | 121.6785 | 121.6644 | 121.762 | -0.008099 | 121.6299 | 121.6735 | 121.7591 | 121.6327 | -121.8828
1443.0625 | 121.9345 | -121.7972 | 0.041199 | -0.013049 | -0.05701 | 0.066313 | -0.011511 | -0.0072283 | 0.0086597 | -0.019381 | -0.0011537 | -0.001658 | -0.0054417 | 0.021271 | -0.01074 | 0.019361 | -0.003172 | -0.012988 | -0.053175 | -0.095798 | -0.10986 | 0.0331 | -0.003531 | -0.14158 | -121.5845 | -0.13526 | -0.087023 | -0.015142 | -121.8508 | 121.8303 | -0.094374 | 121.8165 | 121.7842 | -0.046088 | -0.137 | -0.15106 | -0.053615 | -0.17646 | 121.7936 | 0.21271 | 0.26633 | -0.12822 | -0.056341 | 121.744 | 121.7014 | 121.6873 | 121.794 | -0.008099 | 121.6619 | 121.7102 | 121.782 | 121.6556 | -121.892
1444.8125 | 122.0535 | -121.7606 | 0 | -0.013049 | -0.05701 | 0.066313 | -0.011297 | -0.0076555 | 0.0088735 | -0.034642 | -0.0017945 | -0.0014444 | -0.0056553 | 0.021057 | -0.010954 | 0.023939 | -0.003172 | -0.012988 | -0.057754 | -0.095798 | -0.11444 | 0.0331 | -0.003531 | -0.14158 | -121.589 | -0.13526 | -0.082444 | -0.015142 | -121.8508 | 121.7937 | -0.057754 | 121.7845 | 121.7476 | -0.046088 | -0.095798 | -0.11444 | -0.090236 | -0.13526 | 121.757 | 0.17151 | 0.26175 | -0.082444 | -0.015142 | 121.7028 | 121.6648 | 121.6461 | 121.7574 | 0.0331 | 121.6253 | 121.6781 | 121.7454 | 121.619 | -121.8508
1446.5156 | 121.9254 | -121.8018 | 0.027466 | -0.005418 | -0.056583 | 0.06674 | -0.01087 | -0.0074419 | 0.0088735 | -0.019381 | -0.0015809 | -0.0020852 | -0.0056553 | 0.021271 | -0.010527 | 0.010204 | -0.003172 | -0.008409 | -0.053175 | -0.09122 | -0.1007 | 0.028521 | -0.00811 | -0.137 | -121.5845 | -0.13068 | -0.082444 | -0.010564 | -121.86 | 121.8303 | -0.080641 | 121.812 | 121.7933 | -0.03693 | -0.11869 | -0.12817 | -0.058194 | -0.15815 | 121.7936 | 0.21729 | 0.27548 | -0.10991 | -0.03803 | 121.7486 | 121.7105 | 121.7011 | 121.7986 | 0.001055 | 121.6711 | 121.7193 | 121.7912 | 121.6648 | -121.8874
1448.2812 | 122.0398 | -121.7651 | 0.022888 | -0.005418 | -0.056369 | 0.066313 | -0.011084 | -0.0074419 | 0.0088735 | -0.034642 | -0.0013673 | -0.0020852 | -0.0054417 | 0.021057 | -0.010527 | 0.010204 | 0.001407 | -0.008409 | -0.057754 | -0.095798 | -0.10986 | 0.042258 | 0.005626 | -0.13242 | -121.5982 | -0.13984 | -0.082444 | -0.001407 | -121.8691 | 121.8074 | -0.080642 | 121.7753 | 121.7567 | -0.050667 | -0.11869 | -0.13275 | -0.10397 | -0.16273 | 121.7708 | 0.16693 | 0.27091 | -0.10533 | -0.024295 | 121.7074 | 121.6693 | 121.6553 | 121.7665 | 0.01937 | 121.6253 | 121.6827 | 121.7637 | 121.6327 | -121.892
1450.0312 | 122.0718 | -121.7697 | 0.009155 | -0.02068 | -0.05701 | 0.066527 | -0.010656 | -0.0072283 | 0.0090871 | -0.011751 | -0.0013673 | -0.0020852 | -0.0056553 | 0.021057 | -0.010313 | 0.014783 | 0.001407 | -0.012988 | -0.053175 | -0.095798 | -0.10528 | 0.0331 | -0.00811 | -0.14158 | -121.6074 | -0.1261 | -0.091601 | -0.010564 | -121.8645 | 121.8028 | -0.06233 | 121.7845 | 121.7567 | -0.046088 | -0.10495 | -0.11443 | -0.094817 | -0.13526 | 121.7616 | 0.16235 | 0.25717 | -0.10076 | -0.019719 | 121.7165 | 121.6739 | 121.6644 | 121.7711 | 0.023945 | 121.6436 | 121.6781 | 121.7591 | 121.6281 | -121.8737
1451.7812 | 121.9803 | -121.7972 | 0.013733 | -0.013049 | -0.056583 | 0.066313 | -0.01087 | -0.0074419 | 0.0088735 | -0.019381 | -0.0011537 | -0.001658 | -0.0056553 | 0.021057 | -0.01074 | 0.014783 | -0.003172 | -0.012988 | -0.053175 | -0.095798 | -0.10528 | 0.037679 | 0.001048 | -0.13242 | -121.5982 | -0.13526 | -0.087023 | -0.010564 | -121.8645 | 121.8349 | -0.066908 | 121.812 | 121.7842 | -0.050667 | -0.10953 | -0.11901 | -0.067351 | -0.14899 | 121.7982 | 0.19898 | 0.26633 | -0.10076 | -0.024297 | 121.744 | 121.7014 | 121.6919 | 121.794 | 0.023946 | 121.6619 | 121.7102 | 121.7866 | 121.6648 | -121.8783
1453.4844 | 122.0306 | -121.7789 | 0.009155 | -0.005418 | -0.05701 | 0.066313 | -0.011297 | -0.0074419 | 0.0088735 | -0.019381 | -0.0013673 | -0.0018716 | -0.0054417 | 0.021485 | -0.010313 | 0.019361 | -0.003172 | -0.017566 | -0.053175 | -0.086641 | -0.11444 | 0.042258 | -0.003531 | -0.14616 | -121.6119 | -0.13984 | -0.091601 | -0.015142 | -121.8828 | 121.8211 | -0.06233 | 121.7982 | 121.7613 | -0.059824 | -0.095796 | -0.12359 | -0.10398 | -0.14899 | 121.7753 | 0.16693 | 0.27091 | -0.10076 | -0.024297 | 121.7257 | 121.6922 | 121.6644 | 121.7757 | 0.033103 | 121.639 | 121.6873 | 121.7637 | 121.6327 | -121.892
1455.2344 | 121.9528 | -121.8246 | 0.027466 | -0.013049 | -0.056796 | 0.066313 | -0.011084 | -0.0078693 | 0.0090871 | -0.0041205 | -0.0011537 | -0.0020852 | -0.0056553 | 0.021057 | -0.010527 | 0.019361 | 0.001407 | -0.008409 | -0.053175 | -0.10038 | -0.10986 | 0.037679 | -0.00811 | -0.137 | -121.6074 | -0.13526 | -0.082444 | -0.019721 | -121.8783 | 121.8623 | -0.080641 | 121.844 | 121.8162 | -0.046088 | -0.12784 | -0.13732 | -0.053621 | -0.16273 | 121.8165 | 0.21728 | 0.2709 | -0.10991 | -0.047187 | 121.7715 | 121.7243 | 121.7148 | 121.8261 | 0.010213 | 121.6894 | 121.7422 | 121.8049 | 121.6876 | -121.9057
1456.9844 | 122.0123 | -121.8155 | 0.032043 | -0.005418 | -0.05701 | 0.066313 | -0.011084 | -0.0072283 | 0.0086597 | -0.011751 | -0.0017945 | -0.0018716 | -0.0054417 | 0.021057 | -0.01074 | 0.005626 | 0.001407 | -0.022144 | -0.053175 | -0.09122 | -0.10986 | 0.0331 | -0.003531 | -0.14158 | -121.6119 | -0.13526 | -0.087023 | -0.010564 | -121.8828 | 121.8486 | -0.085218 | 121.8211 | 121.7933 | -0.055244 | -0.12326 | -0.1419 | -0.067355 | -0.1673 | 121.812 | 0.20355 | 0.27091 | -0.11907 | -0.042607 | 121.7623 | 121.7243 | 121.7056 | 121.8169 | 0.001057 | 121.6802 | 121.7285 | 121.8049 | 121.6739 | -121.9149
1458.6719 | 121.9894 | -121.8338 | 0.027466 | -0.005418 | -0.056583 | 0.066313 | -0.011084 | -0.0076555 | 0.0086597 | -0.0041205 | -0.0013673 | -0.001658 | -0.0056553 | 0.021057 | -0.010527 | 0.010204 | -0.003172 | -0.017566 | -0.053175 | -0.10038 | -0.10986 | 0.037679 | 0.005626 | -0.137 | -121.6303 | -0.13068 | -0.091601 | -0.015142 | -121.8874 | 121.8715 | -0.080641 | 121.844 | 121.8162 | -0.055245 | -0.12784 | -0.13732 | -0.053624 | -0.15815 | 121.8394 | 0.20355 | 0.25717 | -0.11907 | -0.042608 | 121.7806 | 121.7334 | 121.7239 | 121.8306 | 0.010213 | 121.7031 | 121.7422 | 121.8187 | 121.6968 | -121.9149
1460.4219 | 122.0352 | -121.8567 | 0.022888 | -0.013049 | -0.05701 | 0.066313 | -0.011084 | -0.0074419 | 0.0088735 | -0.0041205 | -0.0013673 | -0.0018716 | -0.0056553 | 0.021485 | -0.01074 | 0.010204 | 0.010564 | -0.012988 | -0.053175 | -0.095798 | -0.1007 | 0.037679 | 0.005626 | -0.137 | -121.6303 | -0.13068 | -0.091601 | -0.010564 | -121.9012 | 121.8944 | -0.076063 | 121.8669 | 121.8437 | -0.050667 | -0.11869 | -0.12359 | -0.044473 | -0.15357 | 121.8623 | 0.22643 | 0.27091 | -0.11449 | -0.033452 | 121.8035 | 121.7609 | 121.756 | 121.8673 | 0.014791 | 121.726 | 121.7651 | 121.8461 | 121.7197 | -121.924
1462.1875 | 122.0535 | -121.8109 | -0.022888 | -0.005418 | -0.05701 | 0.066099 | -0.010656 | -0.0076555 | 0.0088735 | -0.019381 | -0.0011537 | -0.0020852 | -0.0054417 | 0.021485 | -0.010527 | 0.014783 | 0.005985 | -0.017566 | -0.053175 | -0.09122 | -0.10986 | 0.0331 | 0.001048 | -0.137 | -121.6303 | -0.13984 | -0.091601 | -0.010564 | -121.9057 | 121.844 | -0.030287 | 121.8257 | 121.7933 | -0.050666 | -0.068332 | -0.086969 | -0.094827 | -0.11695 | 121.812 | 0.18066 | 0.27548 | -0.068713 | 0.012324 | 121.7577 | 121.7197 | 121.7011 | 121.8169 | 0.055988 | 121.6711 | 121.7193 | 121.8003 | 121.6739 | -121.8829
1463.8906 | 121.9849 | -121.8567 | 0.036621 | 0.009844 | -0.05701 | 0.066313 | -0.011511 | -0.0072283 | 0.0088735 | -0.011751 | -0.0011537 | -0.0018716 | -0.0056553 | 0.021485 | -0.01074 | 0.019361 | 0.001407 | -0.022144 | -0.057754 | -0.09122 | -0.1007 | 0.037679 | -0.003531 | -0.15074 | -121.6394 | -0.1261 | -0.09618 | -0.010564 | -121.9012 | 121.8944 | -0.094375 | 121.8761 | 121.8345 | -0.059823 | -0.12784 | -0.13732 | -0.044473 | -0.16272 | 121.8532 | 0.21728 | 0.26175 | -0.1328 | -0.047185 | 121.7989 | 121.7655 | 121.756 | 121.8581 | 0.001058 | 121.7306 | 121.7605 | 121.8461 | 121.706 | -121.9378
1465.6406 | 122.0673 | -121.8063 | -0.013733 | -0.005418 | -0.056796 | 0.066527 | -0.011084 | -0.0078693 | 0.0086597 | -0.011751 | -0.0011537 | -0.001658 | -0.0052279 | 0.021271 | -0.010954 | 0.010204 | 0.001407 | -0.017566 | -0.057754 | -0.09122 | -0.10528 | 0.037679 | -0.003531 | -0.14616 | -121.6303 | -0.13526 | -0.087023 | -0.015142 | -121.9103 | 121.844 | -0.044021 | 121.8165 | 121.7888 | -0.055245 | -0.077487 | -0.091546 | -0.10398 | -0.12153 | 121.8028 | 0.17608 | 0.28006 | -0.07329 | -0.001409 | 121.7486 | 121.7151 | 121.7011 | 121.8077 | 0.051412 | 121.6711 | 121.7193 | 121.7912 | 121.6602 | -121.8966
1467.3281 | 122.0718 | -121.8384 | 0 | 0.002213 | -0.05701 | 0.066313 | -0.011084 | -0.0072283 | 0.0084461 | -0.019381 | -0.0013673 | -0.001658 | -0.0056553 | 0.021485 | -0.01074 | 0.019361 | 0.005985 | -0.012988 | -0.062332 | -0.086641 | -0.10528 | 0.037679 | 0.005626 | -0.14158 | -121.644 | -0.13068 | -0.087023 | -0.010564 | -121.9149 | 121.8761 | -0.062332 | 121.8577 | 121.8254 | -0.050667 | -0.086641 | -0.10528 | -0.076519 | -0.13068 | 121.844 | 0.19439 | 0.27091 | -0.087023 | -0.010564 | 121.776 | 121.7517 | 121.7331 | 121.8444 | 0.037679 | 121.7077 | 121.7514 | 121.8278 | 121.6968 | -121.9149
1469.0781 | 122.0673 | -121.843 | 0.018311 | -0.013049 | -0.056796 | 0.065886 | -0.01087 | -0.0074419 | 0.0086597 | -0.011751 | -0.0015809 | -0.0018716 | -0.0054417 | 0.021271 | -0.010527 | 0.019361 | 0.001407 | -0.012988 | -0.057754 | -0.09122 | -0.1007 | 0.0331 | -0.00811 | -0.14158 | -121.644 | -0.13526 | -0.091601 | -0.010564 | -121.9149 | 121.8761 | -0.076065 | 121.8623 | 121.83 | -0.046088 | -0.10953 | -0.11901 | -0.071941 | -0.15357 | 121.8348 | 0.19897 | 0.27091 | -0.10991 | -0.028875 | 121.7852 | 121.7517 | 121.7423 | 121.8444 | 0.014789 | 121.7077 | 121.7514 | 121.8324 | 121.7014 | -121.9332
1470.7656 | 122.1268 | -121.8246 | 0.013733 | -0.013049 | -0.05701 | 0.066527 | -0.011084 | -0.0076555 | 0.0084461 | -0.011751 | -0.0011537 | -0.0018716 | -0.0056553 | 0.021485 | -0.010954 | 0.010204 | 0.001407 | -0.012988 | -0.057754 | -0.095798 | -0.10986 | 0.037679 | -0.003531 | -0.15074 | -121.6577 | -0.13984 | -0.087023 | -0.010564 | -121.9195 | 121.8623 | -0.071487 | 121.8349 | 121.8117 | -0.050667 | -0.10953 | -0.12359 | -0.094831 | -0.15357 | 121.8211 | 0.16692 | 0.26175 | -0.10076 | -0.024297 | 121.7669 | 121.7288 | 121.7148 | 121.8261 | 0.023946 | 121.6848 | 121.7376 | 121.8141 | 121.6739 | -121.9332
1472.5312 | 122.0993 | -121.8063 | 0.009155 | -0.005418 | -0.05701 | 0.066313 | -0.011297 | -0.0078693 | 0.0088735 | -0.011751 | -0.0013673 | -0.0018716 | -0.0058689 | 0.021485 | -0.01074 | 0.019361 | 0.001407 | -0.017566 | -0.057754 | -0.10496 | -0.10528 | 0.037679 | 0.010205 | -0.14158 | -121.6577 | -0.13984 | -0.091601 | -0.005985 | -121.9241 | 121.844 | -0.066909 | 121.8257 | 121.7888 | -0.055245 | -0.11411 | -0.11443 | -0.11772 | -0.14899 | 121.8165 | 0.14861 | 0.26633 | -0.10076 | -0.01514 | 121.7486 | 121.7014 | 121.7011 | 121.8077 | 0.028524 | 121.6665 | 121.7147 | 121.8004 | 121.6648 | -121.9332
1474.2188 | 121.994 | -121.8704 | 0.027466 | 0.002213 | -0.05701 | 0.066313 | -0.011511 | -0.0076555 | 0.0088735 | -0.027012 | -0.0017945 | -0.0020852 | -0.0052279 | 0.021698 | -0.010954 | 0.019361 | 0.001407 | -0.012988 | -0.057754 | -0.086641 | -0.10986 | 0.0331 | -0.003531 | -0.15074 | -121.6577 | -0.13526 | -0.10076 | -0.010564 | -121.9332 | 121.9035 | -0.08522 | 121.8898 | 121.8574 | -0.046088 | -0.11411 | -0.13732 | -0.062791 | -0.16273 | 121.8669 | 0.2127 | 0.27549 | -0.12823 | -0.03803 | 121.8127 | 121.7838 | 121.7606 | 121.8718 | 0.005634 | 121.7352 | 121.7697 | 121.8599 | 121.7197 | -121.9607
1475.9688 | 122.0627 | -121.8292 | 0.013733 | -0.005418 | -0.05701 | 0.066313 | -0.011297 | -0.0076555 | 0.0086597 | -0.019381 | -0.0015809 | -0.001658 | -0.0054417 | 0.021485 | -0.010527 | 0.014783 | 0.001407 | -0.017566 | -0.053175 | -0.095798 | -0.10986 | 0.0331 | -0.00811 | -0.14616 | -121.6531 | -0.13068 | -0.091601 | -0.010564 | -121.9332 | 121.8623 | -0.066908 | 121.844 | 121.8117 | -0.050666 | -0.10953 | -0.12359 | -0.10399 | -0.14441 | 121.8211 | 0.17607 | 0.28006 | -0.10533 | -0.024297 | 121.776 | 121.7334 | 121.7194 | 121.8306 | 0.019367 | 121.6985 | 121.7376 | 121.8187 | 121.6831 | -121.9469
1477.7188 | 122.049 | -121.8658 | 0.022888 | 0.002213 | -0.057224 | 0.066099 | -0.011511 | -0.0076555 | 0.0088735 | -0.0041205 | -0.0013673 | -0.0018716 | -0.0054417 | 0.021485 | -0.01074 | 0.014783 | 0.005985 | -0.017566 | -0.053175 | -0.095798 | -0.10986 | 0.042258 | -0.003531 | -0.14616 | -121.6623 | -0.13068 | -0.09618 | -0.010564 | -121.9424 | 121.9081 | -0.076063 | 121.8806 | 121.8483 | -0.059824 | -0.11869 | -0.13275 | -0.076526 | -0.15357 | 121.8623 | 0.20354 | 0.28006 | -0.11907 | -0.033452 | 121.8127 | 121.77 | 121.756 | 121.8718 | 0.01937 | 121.7352 | 121.7697 | 121.8553 | 121.7197 | -121.9653
1479.4219 | 122.1634 | -121.8475 | -0.004578 | 0.002213 | -0.057437 | 0.066313 | -0.011297 | -0.0076555 | 0.0090871 | -0.011751 | -0.0017945 | -0.001658 | -0.0054417 | 0.021698 | -0.010954 | 0.014783 | 0.005985 | -0.017566 | -0.057754 | -0.09122 | -0.10986 | 0.028521 | 0.001048 | -0.14616 | -121.6669 | -0.13526 | -0.082444 | -0.010564 | -121.9424 | 121.8761 | -0.053176 | 121.8623 | 121.83 | -0.046087 | -0.086642 | -0.10528 | -0.094837 | -0.13068 | 121.8486 | 0.18065 | 0.27549 | -0.077866 | -0.005986 | 121.7898 | 121.7563 | 121.7377 | 121.8535 | 0.033099 | 121.7123 | 121.7651 | 121.837 | 121.7014 | -121.9378
1481.1875 | 122.049 | -121.8613 | 0.009155 | -0.005418 | -0.057437 | 0.066313 | -0.01087 | -0.0076555 | 0.0084461 | -0.0041205 | -0.0015809 | -0.0018716 | -0.0054417 | 0.021485 | -0.010954 | 0.014783 | 0.001407 | -0.017566 | -0.057754 | -0.095798 | -0.10986 | 0.0331 | -0.00811 | -0.15074 | -121.6715 | -0.13068 | -0.091601 | -0.010564 | -121.9515 | 121.8944 | -0.066909 | 121.876 | 121.8437 | -0.050666 | -0.10495 | -0.11901 | -0.090262 | -0.13984 | 121.8532 | 0.1898 | 0.28006 | -0.10076 | -0.019719 | 121.8035 | 121.7655 | 121.7514 | 121.8627 | 0.023945 | 121.7306 | 121.7697 | 121.8507 | 121.7105 | -121.9607
1482.9375 | 122.0993 | -121.8796 | -0.004578 | -0.013049 | -0.05701 | 0.066313 | -0.011084 | -0.0072283 | 0.0088735 | -0.011751 | -0.0013673 | -0.001658 | -0.0058689 | 0.021485 | -0.010954 | 0.010204 | 0.010564 | -0.017566 | -0.062332 | -0.10038 | -0.10986 | 0.0331 | -0.003531 | -0.15074 | -121.676 | -0.13984 | -0.091601 | -0.010564 | -121.9515 | 121.9127 | -0.057754 | 121.8898 | 121.862 | -0.050666 | -0.095799 | -0.10528 | -0.071951 | -0.13526 | 121.876 | 0.20354 | 0.27549 | -0.087023 | -0.005986 | 121.8172 | 121.7792 | 121.7697 | 121.8901 | 0.037678 | 121.7397 | 121.788 | 121.869 | 121.7288 | -121.947
1484.6406 | 122.1863 | -121.8613 | -0.013733 | -0.02068 | -0.057224 | 0.06674 | -0.011084 | -0.0076555 | 0.0086597 | -0.011751 | -0.0011537 | -0.0020852 | -0.0054417 | 0.021485 | -0.01074 | 0.010204 | 0.005985 | -0.017566 | -0.062332 | -0.09122 | -0.10986 | 0.037679 | -0.00811 | -0.15074 | -121.676 | -0.13984 | -0.091601 | -0.015142 | -121.9515 | 121.8989 | -0.048599 | 121.8715 | 121.8437 | -0.055245 | -0.077487 | -0.096124 | -0.090262 | -0.1261 | 121.8532 | 0.18523 | 0.27549 | -0.077868 | -0.001409 | 121.7989 | 121.77 | 121.7514 | 121.8673 | 0.051412 | 121.7214 | 121.7697 | 121.8461 | 121.7105 | -121.9378
1486.4062 | 122.0856 | -121.9116 | 0.022888 | -0.005418 | -0.057224 | 0.065886 | -0.011297 | -0.0074419 | 0.0086597 | -0.019381 | -0.0013673 | -0.0018716 | -0.0058689 | 0.021271 | -0.010527 | 0.014783 | -0.007751 | -0.012988 | -0.057754 | -0.09122 | -0.10528 | 0.0331 | -0.003531 | -0.15074 | -121.6898 | -0.13526 | -0.091601 | -0.010564 | -121.9653 | 121.9447 | -0.080642 | 121.9264 | 121.8986 | -0.046088 | -0.11411 | -0.12817 | -0.053644 | -0.15815 | 121.9081 | 0.22184 | 0.27549 | -0.11449 | -0.033452 | 121.8539 | 121.8204 | 121.8063 | 121.9039 | 0.010212 | 121.7764 | 121.82 | 121.9011 | 121.7609 | -121.9882
1488.1562 | 122.1405 | -121.8475 | -0.009155 | -0.013049 | -0.057437 | 0.06674 | -0.011084 | -0.0074419 | 0.0086597 | -0.019381 | -0.0013673 | -0.001658 | -0.0058689 | 0.021271 | -0.01074 | 0.014783 | 0.005985 | -0.012988 | -0.053175 | -0.09122 | -0.10528 | 0.037679 | -0.003531 | -0.14616 | -121.6898 | -0.13526 | -0.10534 | -0.010564 | -121.9515 | 121.8852 | -0.04402 | 121.8623 | 121.8345 | -0.050667 | -0.082065 | -0.096124 | -0.10399 | -0.1261 | 121.844 | 0.15776 | 0.26175 | -0.096182 | -0.001409 | 121.7944 | 121.7563 | 121.7423 | 121.8535 | 0.046834 | 121.7123 | 121.7422 | 121.837 | 121.7014 | -121.9424
1489.9062 | 122.1451 | -121.8521 | 0.009155 | -0.005418 | -0.056796 | 0.066527 | -0.011084 | -0.0074419 | 0.0086597 | -0.011751 | -0.0015809 | -0.0018716 | -0.0056553 | 0.021271 | -0.01074 | 0.019361 | 0.005985 | -0.017566 | -0.053175 | -0.10038 | -0.11444 | 0.037679 | -0.003531 | -0.15074 | -121.6898 | -0.13526 | -0.09618 | -0.010564 | -121.9653 | 121.8898 | -0.06233 | 121.8715 | 121.8345 | -0.055245 | -0.10953 | -0.12359 | -0.11315 | -0.14441 | 121.8486 | 0.16233 | 0.27549 | -0.10533 | -0.019719 | 121.7989 | 121.7517 | 121.7377 | 121.8581 | 0.028524 | 121.7169 | 121.7559 | 121.8415 | 121.7014 | -121.9744
1491.5938 | 122.1634 | -121.8521 | -0.018311 | 0.002213 | -0.057224 | 0.065886 | -0.011297 | -0.0074419 | 0.0086597 | -0.0041205 | -0.0013673 | -0.0018716 | -0.0056553 | 0.021485 | -0.01074 | 0.014783 | 0.001407 | -0.012988 | -0.053175 | -0.095798 | -0.10986 | 0.028521 | 0.001048 | -0.15074 | -121.6944 | -0.13526 | -0.087023 | -0.005985 | -121.9698 | 121.8806 | -0.034864 | 121.8669 | 121.8391 | -0.041509 | -0.077487 | -0.091546 | -0.11773 | -0.11695 | 121.8532 | 0.15776 | 0.27549 | -0.068712 | 0.012326 | 121.7989 | 121.7563 | 121.7423 | 121.8535 | 0.046832 | 121.7169 | 121.7651 | 121.8461 | 121.7014 | -121.9515
1493.2812 | 122.1359 | -121.8704 | -0.009155 | -0.013049 | -0.057437 | 0.066527 | -0.011297 | -0.0076555 | 0.0086597 | -0.019381 | -0.0013673 | -0.0018716 | -0.0056553 | 0.021485 | -0.011381 | 0.010204 | -0.003172 | -0.012988 | -0.057754 | -0.09122 | -0.10986 | 0.0331 | -0.003531 | -0.15074 | -121.6989 | -0.13984 | -0.091601 | -0.010564 | -121.9744 | 121.9035 | -0.048599 | 121.8806 | 121.8574 | -0.046088 | -0.082065 | -0.1007 | -0.104 | -0.13068 | 121.8669 | 0.17149 | 0.27549 | -0.082446 | -0.001409 | 121.8127 | 121.7792 | 121.7606 | 121.8672 | 0.042255 | 121.7306 | 121.7788 | 121.8599 | 121.7197 | -121.9653
1495.0469 | 122.0398 | -121.9299 | 0.036621 | -0.005418 | -0.05701 | 0.066099 | -0.011297 | -0.0074419 | 0.0084461 | -0.0041205 | -0.0011537 | -0.0018716 | -0.0056553 | 0.021485 | -0.01074 | 0.014783 | -0.003172 | -0.012988 | -0.053175 | -0.09122 | -0.10986 | 0.037679 | -0.00811 | -0.14158 | -121.6989 | -0.13526 | -0.091601 | -0.015142 | -121.9836 | 121.9676 | -0.089796 | 121.9447 | 121.9169 | -0.050667 | -0.12784 | -0.14648 | -0.053648 | -0.17188 | 121.9218 | 0.231 | 0.28464 | -0.12822 | -0.051763 | 121.8768 | 121.8387 | 121.8201 | 121.9268 | 0.001058 | 121.7947 | 121.8383 | 121.9148 | 121.7884 | -122.0202
1496.7969 | 122.1863 | -121.8842 | 0 | -0.013049 | -0.057224 | 0.066099 | -0.011297 | -0.0076555 | 0.0086597 | -0.034642 | -0.0013673 | -0.0018716 | -0.0056553 | 0.021698 | -0.01074 | 0.014783 | 0.001407 | -0.008409 | -0.057754 | -0.095798 | -0.10986 | 0.037679 | -0.00811 | -0.15532 | -121.7081 | -0.13526 | -0.091601 | -0.010564 | -121.9882 | 121.9218 | -0.057754 | 121.8989 | 121.8757 | -0.046088 | -0.095798 | -0.10986 | -0.104 | -0.13526 | 121.876 | 0.17606 | 0.28007 | -0.091601 | -0.010564 | 121.8264 | 121.7884 | 121.7743 | 121.8856 | 0.037679 | 121.7489 | 121.7926 | 121.8736 | 121.7288 | -121.9882
1498.4844 | 122.1359 | -121.8933 | 0.004578 | -0.02068 | -0.057224 | 0.066099 | -0.011725 | -0.0074419 | 0.0088735 | -0.011751 | -0.0013673 | -0.0014444 | -0.0056553 | 0.021485 | -0.010527 | 0.019361 | -0.003172 | -0.017566 | -0.057754 | -0.086641 | -0.10986 | 0.028521 | -0.00811 | -0.15074 | -121.7081 | -0.13984 | -0.091601 | -0.005985 | -121.9882 | 121.9218 | -0.062332 | 121.9127 | 121.8757 | -0.046087 | -0.091219 | -0.11443 | -0.094848 | -0.14442 | 121.8852 | 0.18522 | 0.28007 | -0.096179 | -0.010563 | 121.8356 | 121.8067 | 121.7835 | 121.8901 | 0.023943 | 121.7535 | 121.8017 | 121.8873 | 121.7426 | -121.9927
1500.25 | 122.1909 | -121.8933 | 0.009155 | -0.005418 | -0.057437 | 0.066313 | -0.011725 | -0.0074419 | 0.0086597 | -0.019381 | -0.0017945 | -0.001658 | -0.0056553 | 0.021912 | -0.010527 | 0.019361 | 0.005985 | -0.017566 | -0.057754 | -0.09122 | -0.10986 | 0.0331 | 0.001048 | -0.14616 | -121.7173 | -0.1261 | -0.087023 | -0.019721 | -121.9836 | 121.9264 | -0.066909 | 121.9127 | 121.8757 | -0.050666 | -0.10037 | -0.11901 | -0.090269 | -0.13526 | 121.8944 | 0.17606 | 0.26633 | -0.096178 | -0.028876 | 121.8356 | 121.8021 | 121.7835 | 121.8993 | 0.023945 | 121.7672 | 121.8063 | 121.8736 | 121.7472 | -121.9927
1502 | 122.113 | -121.9254 | 0.022888 | -0.005418 | -0.057224 | 0.066099 | -0.011297 | -0.0076555 | 0.0086597 | -0.011751 | -0.0013673 | -0.001658 | -0.0054417 | 0.021698 | -0.01074 | 0.010204 | 0.005985 | -0.017566 | -0.053175 | -0.09122 | -0.11444 | 0.037679 | -0.00811 | -0.14616 | -121.7127 | -0.13526 | -0.077866 | -0.015142 | -121.9882 | 121.963 | -0.076063 | 121.9356 | 121.9078 | -0.055245 | -0.11411 | -0.13732 | -0.062805 | -0.15815 | 121.9172 | 0.21268 | 0.27549 | -0.10075 | -0.03803 | 121.8722 | 121.8341 | 121.8109 | 121.9313 | 0.014791 | 121.7901 | 121.8475 | 121.9102 | 121.7792 | -122.011
1503.7031 | 122.0581 | -121.9254 | 0.036621 | -0.005418 | -0.057437 | 0.066099 | -0.011084 | -0.0074419 | 0.0084461 | -0.011751 | -0.0015809 | -0.001658 | -0.0054417 | 0.021485 | -0.01074 | 0.010204 | 0.005985 | -0.017566 | -0.053175 | -0.086641 | -0.096121 | 0.037679 | 0.001048 | -0.1599 | -121.7127 | -0.13068 | -0.091601 | -0.015142 | -121.9973 | 121.963 | -0.089796 | 121.9356 | 121.9078 | -0.055245 | -0.12326 | -0.13274 | -0.071963 | -0.1673 | 121.9264 | 0.21268 | 0.28464 | -0.12822 | -0.051763 | 121.8722 | 121.8387 | 121.8292 | 121.9313 | 0.001058 | 121.7947 | 121.8338 | 121.9102 | 121.7655 | -122.0339
1505.4688 | 122.1497 | -121.9025 | 0 | -0.005418 | -0.057437 | 0.065886 | -0.011297 | -0.0078693 | 0.0086597 | -0.011751 | -0.0013673 | -0.0020852 | -0.0052279 | 0.021698 | -0.01074 | 0.014783 | 0.005985 | -0.012988 | -0.053175 | -0.095798 | -0.10528 | 0.0331 | -0.00811 | -0.15074 | -121.7264 | -0.14442 | -0.091601 | -0.010564 | -122.0019 | 121.9356 | -0.053175 | 121.9172 | 121.8895 | -0.046088 | -0.095798 | -0.10528 | -0.09943 | -0.14442 | 121.8944 | 0.17606 | 0.27549 | -0.091601 | -0.010564 | 121.8493 | 121.8067 | 121.7972 | 121.9085 | 0.0331 | 121.758 | 121.8109 | 121.8919 | 121.7517 | -122.0019
1507.1719 | 122.2137 | -121.8979 | -0.009155 | -0.005418 | -0.057437 | 0.066099 | -0.011297 | -0.0074419 | 0.0084461 | -0.019381 | -0.0013673 | -0.001658 | -0.0054417 | 0.021698 | -0.01074 | 0.019361 | 0.005985 | -0.017566 | -0.062332 | -0.09122 | -0.1007 | 0.0331 | 0.001048 | -0.14616 | -121.7218 | -0.13526 | -0.082444 | -0.005985 | -122.0019 | 121.931 | -0.053177 | 121.9172 | 121.8803 | -0.050666 | -0.082065 | -0.091545 | -0.10401 | -0.1261 | 121.8989 | 0.17606 | 0.28007 | -0.073289 | 0.00317 | 121.8356 | 121.8067 | 121.7972 | 121.9039 | 0.042255 | 121.7626 | 121.8154 | 121.8919 | 121.7517 | -121.9927
1508.9375 | 122.1588 | -121.9116 | 0.022888 | -0.005418 | -0.057651 | 0.066313 | -0.011297 | -0.0078693 | 0.0084461 | -0.011751 | -0.0015809 | -0.001658 | -0.0054417 | 0.021698 | -0.01074 | 0.014783 | 0.001407 | -0.012988 | -0.057754 | -0.095798 | -0.1007 | 0.0331 | -0.003531 | -0.15532 | -121.7356 | -0.13526 | -0.087023 | -0.010564 | -122.0065 | 121.9447 | -0.080642 | 121.9264 | 121.8986 | -0.046088 | -0.11869 | -0.12359 | -0.094853 | -0.15815 | 121.9081 | 0.17606 | 0.27091 | -0.10991 | -0.033452 | 121.8539 | 121.8158 | 121.8109 | 121.913 | 0.010212 | 121.7764 | 121.8246 | 121.9011 | 121.7563 | -122.0294
1510.625 | 122.2275 | -121.8933 | -0.009155 | -0.005418 | -0.057437 | 0.065886 | -0.011297 | -0.0078693 | 0.0084461 | -0.019381 | -0.0013673 | -0.0018716 | -0.0054417 | 0.021698 | -0.010954 | 0.010204 | 0.005985 | -0.017566 | -0.057754 | -0.086641 | -0.10528 | 0.037679 | 0.001048 | -0.15532 | -121.731 | -0.14442 | -0.09618 | -0.015142 | -122.0065 | 121.931 | -0.048599 | 121.9035 | 121.8757 | -0.055245 | -0.077486 | -0.096124 | -0.11316 | -0.13526 | 121.8944 | 0.16232 | 0.27549 | -0.087025 | -0.005987 | 121.8356 | 121.8067 | 121.788 | 121.8993 | 0.046834 | 121.7489 | 121.7971 | 121.8782 | 121.738 | -121.9973
1512.3906 | 122.1954 | -121.8933 | -0.004578 | -0.005418 | -0.057437 | 0.065886 | -0.011297 | -0.0072283 | 0.0088735 | -0.011751 | -0.0013673 | -0.0018716 | -0.0058689 | 0.021698 | -0.01074 | 0.010204 | 0.010564 | -0.012988 | -0.062332 | -0.09122 | -0.10528 | 0.0331 | -0.003531 | -0.15532 | -121.7401 | -0.13526 | -0.091601 | -0.010564 | -122.0202 | 121.9264 | -0.057754 | 121.9035 | 121.8803 | -0.046088 | -0.086642 | -0.1007 | -0.1269 | -0.13068 | 121.8898 | 0.15317 | 0.28007 | -0.087023 | -0.005986 | 121.831 | 121.8021 | 121.788 | 121.9039 | 0.037678 | 121.7581 | 121.8017 | 121.8827 | 121.738 | -122.0156
1514.0781 | 122.2321 | -121.9254 | -0.018311 | 0.002213 | -0.057224 | 0.066099 | -0.011084 | -0.0076555 | 0.0086597 | -0.011751 | -0.0011537 | -0.0018716 | -0.0054417 | 0.021912 | -0.010954 | 0.010204 | 0.001407 | -0.008409 | -0.053175 | -0.095798 | -0.10986 | 0.0331 | -0.012689 | -0.15532 | -121.7447 | -0.13068 | -0.091601 | -0.015142 | -122.0248 | 121.9585 | -0.034864 | 121.9356 | 121.9169 | -0.041509 | -0.077487 | -0.091546 | -0.099436 | -0.11237 | 121.9127 | 0.18063 | 0.28007 | -0.07329 | 0.003169 | 121.8722 | 121.8296 | 121.8155 | 121.9268 | 0.051411 | 121.7947 | 121.8338 | 121.9102 | 121.77 | -122.0065
1515.8281 | 122.1176 | -121.9437 | 0.027466 | -0.013049 | -0.057437 | 0.066099 | -0.011725 | -0.0076555 | 0.0082325 | -0.027012 | -0.0015809 | -0.0018716 | -0.0056553 | 0.021485 | -0.01074 | 0.010204 | 0.001407 | -0.017566 | -0.06691 | -0.10038 | -0.10528 | 0.0331 | -0.003531 | -0.15532 | -121.7493 | -0.13068 | -0.087023 | -0.005985 | -122.0248 | 121.9768 | -0.094376 | 121.9539 | 121.9261 | -0.050666 | -0.12784 | -0.13275 | -0.081125 | -0.15815 | 121.9401 | 0.19436 | 0.27549 | -0.11449 | -0.033451 | 121.8768 | 121.8433 | 121.8384 | 121.9451 | 0.005634 | 121.813 | 121.8566 | 121.9377 | 121.7883 | -122.0523
1517.5156 | 122.0856 | -121.9437 | 0.032043 | -0.013049 | -0.057437 | 0.065886 | -0.011297 | -0.0076555 | 0.0086597 | -0.011751 | -0.0013673 | -0.0020852 | -0.0058689 | 0.021698 | -0.01074 | 0.010204 | 0.005985 | -0.017566 | -0.053175 | -0.10038 | -0.10528 | 0.060574 | -0.00811 | -0.1599 | -121.7539 | -0.13526 | -0.087023 | -0.010564 | -122.0339 | 122.0042 | -0.085218 | 121.9539 | 121.9261 | -0.07814 | -0.13242 | -0.13732 | -0.090282 | -0.1673 | 121.9356 | 0.18979 | 0.28007 | -0.11907 | -0.042607 | 121.8905 | 121.8433 | 121.8384 | 121.9496 | 0.028531 | 121.8084 | 121.8566 | 121.9331 | 121.7838 | -122.066
1519.2812 | 122.1039 | -121.9757 | 0.045776 | 0.002213 | -0.057437 | 0.066099 | -0.011725 | -0.0076555 | 0.0084461 | -0.011751 | -0.0011537 | -0.0018716 | -0.0060825 | 0.021698 | -0.01074 | 0.014783 | 0.001407 | -0.017566 | -0.062332 | -0.095798 | -0.10986 | 0.0331 | -0.003531 | -0.15532 | -121.7493 | -0.14442 | -0.09618 | -0.015142 | -122.0339 | 122.0088 | -0.10811 | 121.9905 | 121.9581 | -0.050666 | -0.14157 | -0.15563 | -0.058239 | -0.19019 | 121.9722 | 0.22641 | 0.28464 | -0.14196 | -0.060918 | 121.9134 | 121.8799 | 121.8659 | 121.9771 | -0.012676 | 121.8313 | 121.8795 | 121.9606 | 121.8204 | -122.0797
1521.0312 | 122.0947 | -121.9849 | 0.036621 | -0.005418 | -0.057651 | 0.066313 | -0.011297 | -0.0078693 | 0.0084461 | 0.00351 | -0.0013673 | -0.001658 | -0.0058689 | 0.021698 | -0.01074 | 0.014783 | 0.001407 | -0.022144 | -0.048597 | -0.09122 | -0.10986 | 0.037679 | -0.00811 | -0.1599 | -121.7539 | -0.13526 | -0.087023 | -0.015142 | -122.0339 | 122.0225 | -0.085218 | 121.9996 | 121.9627 | -0.059823 | -0.12784 | -0.14648 | -0.049084 | -0.17188 | 121.9768 | 0.23098 | 0.28007 | -0.12364 | -0.051763 | 121.9363 | 121.8936 | 121.875 | 121.9863 | 0.001058 | 121.8496 | 121.8978 | 121.9697 | 121.825 | -122.0706
1522.7188 | 122.2366 | -121.9254 | -0.004578 | 0.002213 | -0.057651 | 0.066099 | -0.011297 | -0.0074419 | 0.0084461 | -0.011751 | -0.0013673 | -0.0018716 | -0.0052279 | 0.021912 | -0.01074 | 0.014783 | 0.001407 | -0.022144 | -0.057754 | -0.09122 | -0.10528 | 0.0331 | -0.00811 | -0.16448 | -121.7585 | -0.13526 | -0.091601 | -0.015142 | -122.0385 | 121.9585 | -0.053176 | 121.9401 | 121.9032 | -0.055244 | -0.086642 | -0.1007 | -0.11317 | -0.13068 | 121.9172 | 0.16689 | 0.28007 | -0.087023 | -0.010564 | 121.8676 | 121.8341 | 121.8201 | 121.9268 | 0.037678 | 121.7901 | 121.8338 | 121.9102 | 121.7609 | -122.0339
1524.4688 | 122.2366 | -121.9162 | 0.018311 | -0.005418 | -0.057865 | 0.066313 | -0.011511 | -0.0078693 | 0.0086597 | -0.011751 | -0.0013673 | -0.0020852 | -0.0052279 | 0.021485 | -0.01074 | 0.023939 | 0.005985 | -0.008409 | -0.057754 | -0.086641 | -0.1007 | 0.0331 | -0.003531 | -0.1599 | -121.763 | -0.13984 | -0.091601 | -0.015142 | -122.0431 | 121.9493 | -0.076065 | 121.9401 | 121.9078 | -0.041509 | -0.10495 | -0.11901 | -0.12691 | -0.15815 | 121.9127 | 0.15316 | 0.28007 | -0.10991 | -0.033453 | 121.8584 | 121.8296 | 121.8155 | 121.9222 | 0.014789 | 121.7764 | 121.8246 | 121.9011 | 121.7563 | -122.0614
1526.2188 | 122.1359 | -121.9666 | 0.036621 | -0.013049 | -0.057651 | 0.066099 | -0.011084 | -0.0076555 | 0.0086597 | -0.011751 | -0.0015809 | -0.0018716 | -0.0056553 | 0.021912 | -0.010954 | 0.014783 | 0.005985 | -0.022144 | -0.057754 | -0.09122 | -0.1007 | 0.0331 | -0.003531 | -0.16448 | -121.7676 | -0.13526 | -0.082444 | -0.010564 | -122.0477 | 121.9997 | -0.094375 | 121.9813 | 121.9444 | -0.055244 | -0.12784 | -0.13732 | -0.081131 | -0.17188 | 121.963 | 0.19894 | 0.28007 | -0.11907 | -0.047185 | 121.9088 | 121.8753 | 121.8659 | 121.9725 | -0.003521 | 121.8313 | 121.8841 | 121.956 | 121.8021 | -122.0843
1527.9062 | 122.1954 | -121.9757 | 0.013733 | -0.005418 | -0.057651 | 0.066313 | -0.011511 | -0.0080829 | 0.0084461 | -0.011751 | -0.0017945 | -0.0020852 | -0.0056553 | 0.021912 | -0.010527 | 0.014783 | 0.005985 | -0.017566 | -0.053175 | -0.10496 | -0.11444 | 0.042258 | -0.003531 | -0.1599 | -121.763 | -0.14442 | -0.087023 | -0.019721 | -122.0523 | 122.018 | -0.066908 | 121.9905 | 121.9581 | -0.059824 | -0.11869 | -0.12817 | -0.076554 | -0.15815 | 121.9722 | 0.21267 | 0.28922 | -0.10076 | -0.033454 | 121.9225 | 121.8708 | 121.8613 | 121.9817 | 0.028525 | 121.8313 | 121.8887 | 121.956 | 121.8158 | -122.066
1529.6562 | 122.1954 | -121.9666 | 0.004578 | -0.013049 | -0.057865 | 0.065886 | -0.011725 | -0.0076555 | 0.0086597 | -0.019381 | -0.0013673 | -0.001658 | -0.0056553 | 0.021698 | -0.010954 | 0.014783 | 0.001407 | -0.022144 | -0.053175 | -0.095798 | -0.11444 | 0.0331 | -0.003531 | -0.1599 | -121.7722 | -0.13526 | -0.082444 | -0.010564 | -122.0614 | 121.9997 | -0.057753 | 121.9813 | 121.9444 | -0.055244 | -0.10038 | -0.11901 | -0.094867 | -0.13984 | 121.963 | 0.19436 | 0.28923 | -0.087022 | -0.015142 | 121.9134 | 121.8708 | 121.8521 | 121.968 | 0.028522 | 121.8313 | 121.8841 | 121.956 | 121.8067 | -122.066
1531.4062 | 122.1634 | -121.9757 | 0.032043 | 0.002213 | -0.057865 | 0.066099 | -0.011297 | -0.0074419 | 0.0086597 | -0.019381 | -0.0011537 | -0.0014444 | -0.0056553 | 0.021698 | -0.01074 | 0.014783 | 0.005985 | -0.022144 | -0.053175 | -0.09122 | -0.10986 | 0.023942 | -0.00811 | -0.1599 | -121.7722 | -0.13526 | -0.087023 | -0.015142 | -122.0568 | 121.9997 | -0.085218 | 121.9905 | 121.9536 | -0.046086 | -0.12326 | -0.1419 | -0.081133 | -0.1673 | 121.9676 | 0.20351 | 0.28465 | -0.11907 | -0.047185 | 121.9225 | 121.8845 | 121.8659 | 121.9817 | -0.008101 | 121.8404 | 121.8887 | 121.9606 | 121.8158 | -122.0889
1533.0938 | 122.1313 | -121.9803 | 0.045776 | -0.005418 | -0.057865 | 0.065886 | -0.011725 | -0.0078693 | 0.0084461 | -0.0041205 | -0.0013673 | -0.0020852 | -0.0056553 | 0.021698 | -0.01074 | 0.010204 | 0.001407 | -0.022144 | -0.053175 | -0.09122 | -0.11444 | 0.037679 | -0.003531 | -0.16448 | -121.7722 | -0.13984 | -0.082444 | -0.015142 | -122.0568 | 122.018 | -0.098951 | 121.9905 | 121.9581 | -0.059823 | -0.137 | -0.16021 | -0.076555 | -0.18561 | 121.9768 | 0.20809 | 0.28465 | -0.12822 | -0.060918 | 121.9271 | 121.8891 | 121.8659 | 121.9817 | -0.008097 | 121.8404 | 121.8978 | 121.9651 | 121.8158 | -122.1026
1534.8438 | 122.2458 | -121.9437 | -0.018311 | -0.013049 | -0.057651 | 0.066313 | -0.011725 | -0.0076555 | 0.0084461 | -0.019381 | -0.0013673 | -0.001658 | -0.0056553 | 0.021698 | -0.010954 | 0.010204 | 0.005985 | -0.022144 | -0.057754 | -0.095798 | -0.10986 | 0.0331 | -0.00811 | -0.1599 | -121.7722 | -0.13526 | -0.087023 | -0.019721 | -122.0706 | 121.9768 | -0.039443 | 121.9539 | 121.9215 | -0.055244 | -0.077487 | -0.091546 | -0.12691 | -0.11695 | 121.9356 | 0.17147 | 0.29838 | -0.068712 | -0.00141 | 121.8859 | 121.8479 | 121.8338 | 121.9496 | 0.051411 | 121.8084 | 121.8566 | 121.9239 | 121.7838 | -122.0523
1536.5938 | 122.2275 | -121.9528 | 0.009155 | -0.013049 | -0.057865 | 0.066313 | -0.011511 | -0.0074419 | 0.0088735 | -0.011751 | -0.0013673 | -0.0020852 | -0.0054417 | 0.021912 | -0.01074 | 0.010204 | 0.005985 | -0.026723 | -0.053175 | -0.086641 | -0.10528 | 0.0331 | -0.00811 | -0.16448 | -121.7859 | -0.13526 | -0.087023 | -0.010564 | -122.066 | 121.9859 | -0.06233 | 121.963 | 121.9261 | -0.059823 | -0.095796 | -0.11443 | -0.11318 | -0.14441 | 121.9447 | 0.16689 | 0.28007 | -0.096178 | -0.019719 | 121.8996 | 121.8662 | 121.8475 | 121.9588 | 0.023945 | 121.8176 | 121.8658 | 121.9423 | 121.7883 | -122.0752
1538.3594 | 122.2092 | -121.9666 | 0.009155 | -0.005418 | -0.057865 | 0.066099 | -0.011511 | -0.0078693 | 0.0084461 | -0.019381 | -0.0011537 | -0.0018716 | -0.0054417 | 0.021698 | -0.010954 | 0.014783 | 0.001407 | -0.022144 | -0.062332 | -0.095798 | -0.10986 | 0.028521 | -0.003531 | -0.15532 | -121.7814 | -0.13526 | -0.087023 | -0.015142 | -122.0614 | 121.9951 | -0.071487 | 121.9813 | 121.9444 | -0.050665 | -0.10495 | -0.11901 | -0.094867 | -0.14441 | 121.963 | 0.1852 | 0.28007 | -0.096178 | -0.024297 | 121.9042 | 121.8708 | 121.8567 | 121.968 | 0.019366 | 121.8313 | 121.8795 | 121.9514 | 121.8112 | -122.0706
1540.0625 | 122.1451 | -122.0215 | 0.013733 | -0.02068 | -0.057651 | 0.066313 | -0.011297 | -0.0076555 | 0.0084461 | -0.011751 | -0.0013673 | -0.0020852 | -0.0056553 | 0.021912 | -0.010954 | 0.014783 | 0.001407 | -0.012988 | -0.053175 | -0.09122 | -0.10986 | 0.0331 | -0.00811 | -0.15532 | -121.7905 | -0.13068 | -0.087023 | -0.010564 | -122.0706 | 122.0546 | -0.066908 | 122.0363 | 122.0085 | -0.046088 | -0.10495 | -0.12359 | -0.049094 | -0.14441 | 122.0134 | 0.23097 | 0.28007 | -0.10076 | -0.024297 | 121.9683 | 121.9303 | 121.9116 | 122.0229 | 0.019367 | 121.8908 | 121.9345 | 122.0109 | 121.8662 | -122.0843
1541.7969 | 122.2687 | -121.9574 | 0 | -0.013049 | -0.057651 | 0.066099 | -0.011511 | -0.0076555 | 0.0084461 | -0.011751 | -0.0015809 | -0.001658 | -0.0054417 | 0.021912 | -0.010527 | 0.019361 | 0.001407 | -0.012988 | -0.057754 | -0.09122 | -0.10528 | 0.0331 | -0.00811 | -0.16448 | -121.7905 | -0.13526 | -0.091601 | -0.015142 | -122.0843 | 121.9905 | -0.057754 | 121.9768 | 121.9444 | -0.046088 | -0.09122 | -0.10528 | -0.12692 | -0.13526 | 121.9493 | 0.16689 | 0.2938 | -0.091601 | -0.015142 | 121.8996 | 121.8662 | 121.8521 | 121.9588 | 0.0331 | 121.8221 | 121.8658 | 121.9423 | 121.7929 | -122.0843
1543.5625 | 122.1542 | -122.0078 | 0.041199 | -0.005418 | -0.057865 | 0.066099 | -0.011725 | -0.0076555 | 0.0082325 | -0.011751 | -0.0011537 | -0.0018716 | -0.0054417 | 0.021912 | -0.01074 | 0.014783 | 0.001407 | -0.012988 | -0.057754 | -0.095798 | -0.10528 | 0.0331 | -0.017267 | -0.16448 | -121.7951 | -0.13526 | -0.087023 | -0.010564 | -122.0797 | 122.0409 | -0.098953 | 122.0225 | 121.9948 | -0.046088 | -0.137 | -0.14648 | -0.071984 | -0.17646 | 121.9905 | 0.21266 | 0.28465 | -0.12822 | -0.051763 | 121.95 | 121.912 | 121.9025 | 122.0092 | -0.008099 | 121.8725 | 121.9207 | 121.9972 | 121.8433 | -122.1209
1545.25 | 122.1542 | -122.0123 | 0.013733 | -0.013049 | -0.058079 | 0.066313 | -0.011511 | -0.0074419 | 0.0084461 | -0.011751 | -0.0015809 | -0.0018716 | -0.0054417 | 0.021698 | -0.01074 | 0.010204 | 0.001407 | -0.008409 | -0.062332 | -0.10038 | -0.10528 | 0.0331 | -0.003531 | -0.16448 | -121.7997 | -0.13068 | -0.087023 | -0.015142 | -122.0797 | 122.0454 | -0.076065 | 122.0225 | 122.0039 | -0.041509 | -0.11411 | -0.11901 | -0.067406 | -0.14441 | 122.0088 | 0.21266 | 0.28007 | -0.10076 | -0.028875 | 121.95 | 121.912 | 121.907 | 122.0137 | 0.019367 | 121.8816 | 121.9253 | 121.9972 | 121.8479 | -122.0935
1546.9844 | 122.2778 | -121.9757 | -0.004578 | -0.005418 | -0.058079 | 0.066099 | -0.011511 | -0.0074419 | 0.0086597 | -0.011751 | -0.0013673 | -0.001658 | -0.0054417 | 0.022126 | -0.01074 | 0.010204 | -0.003172 | -0.017566 | -0.062332 | -0.095798 | -0.11444 | 0.0331 | -0.00811 | -0.16905 | -121.8042 | -0.13526 | -0.087023 | -0.015142 | -122.0889 | 122.0088 | -0.057754 | 121.9859 | 121.9581 | -0.050666 | -0.09122 | -0.10986 | -0.11319 | -0.13068 | 121.9676 | 0.17146 | 0.28465 | -0.082445 | -0.010564 | 121.9134 | 121.8799 | 121.8613 | 121.9725 | 0.037678 | 121.8404 | 121.8887 | 121.9606 | 121.8067 | -122.0843
1548.6719 | 122.2366 | -121.9757 | 0.004578 | 0.002213 | -0.057437 | 0.065886 | -0.011511 | -0.0076555 | 0.0084461 | -0.011751 | -0.0013673 | -0.0018716 | -0.0054417 | 0.022126 | -0.010313 | 0.005626 | 0.005985 | -0.017566 | -0.057754 | -0.09122 | -0.10528 | 0.0331 | -0.012689 | -0.16448 | -121.8088 | -0.13068 | -0.087023 | -0.0243 | -122.0843 | 122.0088 | -0.062332 | 121.9813 | 121.9581 | -0.050666 | -0.095798 | -0.10986 | -0.10861 | -0.13526 | 121.963 | 0.16688 | 0.27549 | -0.091601 | -0.028878 | 121.918 | 121.8845 | 121.8704 | 121.9817 | 0.028522 | 121.845 | 121.8887 | 121.9514 | 121.8112 | -122.0889
1550.3594 | 122.1588 | -122.0444 | 0.009155 | -0.005418 | -0.057865 | 0.065886 | -0.011725 | -0.0078693 | 0.0084461 | -0.019381 | -0.0013673 | -0.001658 | -0.0056553 | 0.021912 | -0.010954 | 0.010204 | 0.005985 | -0.017566 | -0.057754 | -0.09122 | -0.10986 | 0.028521 | -0.00811 | -0.16905 | -121.8042 | -0.13526 | -0.091601 | -0.019721 | -122.0935 | 122.0729 | -0.066909 | 122.0546 | 122.0268 | -0.046087 | -0.10037 | -0.11901 | -0.049099 | -0.14441 | 122.0363 | 0.24013 | 0.28923 | -0.10076 | -0.028876 | 121.9866 | 121.9532 | 121.9345 | 122.0504 | 0.019366 | 121.9091 | 121.9528 | 122.0247 | 121.8753 | -122.1026
1552.1094 | 122.2824 | -121.9711 | -0.004578 | -0.005418 | -0.058079 | 0.066313 | -0.011725 | -0.0076555 | 0.0086597 | -0.011751 | -0.0013673 | -0.001658 | -0.0058689 | 0.021912 | -0.010954 | 0.014783 | 0.005985 | -0.017566 | -0.057754 | -0.09122 | -0.10986 | 0.028521 | -0.012689 | -0.16448 | -121.8088 | -0.13984 | -0.087023 | -0.015142 | -122.0981 | 121.9997 | -0.053176 | 121.9859 | 121.9536 | -0.046087 | -0.086642 | -0.10528 | -0.12692 | -0.13526 | 121.9584 | 0.16231 | 0.28923 | -0.082445 | -0.010564 | 121.9134 | 121.8799 | 121.8613 | 121.9771 | 0.033099 | 121.8313 | 121.8841 | 121.956 | 121.8067 | -122.0935
1553.7969 | 122.2687 | -121.9803 | 0.009155 | -0.005418 | -0.057865 | 0.066099 | -0.011938 | -0.0078693 | 0.0082325 | -0.011751 | -0.0013673 | -0.002299 | -0.0058689 | 0.021912 | -0.01074 | 0.014783 | 0.005985 | -0.012988 | -0.057754 | -0.086641 | -0.1007 | 0.028521 | 0.001048 | -0.16448 | -121.8088 | -0.13526 | -0.091601 | -0.019721 | -122.1072 | 122.0088 | -0.066909 | 121.9951 | 121.9673 | -0.041509 | -0.095796 | -0.10985 | -0.12692 | -0.14441 | 121.9813 | 0.17146 | 0.29838 | -0.10076 | -0.028876 | 121.9225 | 121.8936 | 121.8796 | 121.9863 | 0.019366 | 121.845 | 121.8887 | 121.9606 | 121.8158 | -122.1164
1555.5469 | 122.1725 | -122.0215 | 0.018311 | -0.013049 | -0.058079 | 0.066099 | -0.011725 | -0.0078693 | 0.0086597 | -0.011751 | -0.0013673 | -0.0018716 | -0.0054417 | 0.021912 | -0.010954 | 0.005626 | 0.005985 | -0.008409 | -0.057754 | -0.086641 | -0.11444 | 0.0331 | -0.00811 | -0.16448 | -121.8226 | -0.13526 | -0.09618 | -0.019721 | -122.1072 | 122.0546 | -0.076065 | 122.0271 | 122.0131 | -0.041509 | -0.10495 | -0.13275 | -0.085724 | -0.15357 | 122.0134 | 0.19892 | 0.28465 | -0.11449 | -0.038032 | 121.9637 | 121.9348 | 121.907 | 122.0275 | 0.014789 | 121.8862 | 121.9253 | 122.0018 | 121.857 | -122.1255
1557.2344 | 122.1634 | -122.0169 | 0.041199 | 0.002213 | -0.058079 | 0.065886 | -0.011297 | -0.0076555 | 0.0084461 | -0.0041205 | -0.0015809 | -0.0018716 | -0.0054417 | 0.021912 | -0.010954 | 0.010204 | 0.010564 | -0.012988 | -0.053175 | -0.09122 | -0.10528 | 0.028521 | -0.00811 | -0.16448 | -121.818 | -0.13526 | -0.091601 | -0.015142 | -122.1072 | 122.0454 | -0.094374 | 122.0271 | 122.0039 | -0.041509 | -0.13242 | -0.14648 | -0.090301 | -0.17646 | 122.0088 | 0.19893 | 0.28923 | -0.1328 | -0.056341 | 121.9637 | 121.9257 | 121.9116 | 122.0275 | -0.012678 | 121.8816 | 121.9253 | 122.0018 | 121.8524 | -122.1484
1559 | 122.1634 | -122.0398 | 0.027466 | -0.005418 | -0.058079 | 0.066099 | -0.011725 | -0.0080829 | 0.0084461 | 0.00351 | -0.0015809 | -0.0018716 | -0.0056553 | 0.021912 | -0.01074 | 0.014783 | 0.005985 | -0.012988 | -0.057754 | -0.09122 | -0.10528 | 0.0331 | -0.012689 | -0.16448 | -121.8271 | -0.13526 | -0.091601 | -0.015142 | -122.1118 | 122.0729 | -0.08522 | 122.0546 | 122.0268 | -0.046088 | -0.11869 | -0.13275 | -0.071992 | -0.16273 | 122.0271 | 0.21265 | 0.28465 | -0.11907 | -0.042608 | 121.982 | 121.9486 | 121.9345 | 122.0458 | 0.005634 | 121.9045 | 121.9482 | 122.0247 | 121.8753 | -122.1393
1560.7656 | 122.287 | -121.9986 | 0 | -0.013049 | -0.058079 | 0.066099 | -0.011297 | -0.0078693 | 0.0086597 | -0.011751 | -0.0015809 | -0.0020852 | -0.0056553 | 0.021912 | -0.01074 | 0.010204 | 0.005985 | -0.017566 | -0.053175 | -0.09122 | -0.10528 | 0.0331 | -0.012689 | -0.16905 | -121.8271 | -0.13526 | -0.09618 | -0.019721 | -122.1164 | 122.0317 | -0.053175 | 122.0088 | 121.981 | -0.050666 | -0.09122 | -0.10528 | -0.11777 | -0.13526 | 121.9859 | 0.17146 | 0.28923 | -0.09618 | -0.019721 | 121.9454 | 121.9074 | 121.8933 | 122.0046 | 0.0331 | 121.8633 | 121.9024 | 121.9789 | 121.8295 | -122.1164
1562.4688 | 122.2229 | -122.0398 | 0.036621 | 0.009844 | -0.058079 | 0.065886 | -0.011297 | -0.0080829 | 0.0082325 | -0.027012 | -0.0015809 | -0.0020852 | -0.0054417 | 0.021698 | -0.010954 | 0.019361 | 0.005985 | -0.026723 | -0.057754 | -0.10496 | -0.10986 | 0.0331 | -0.00811 | -0.16905 | -121.8271 | -0.14442 | -0.091601 | -0.015142 | -122.1209 | 122.0729 | -0.094375 | 122.0592 | 122.0131 | -0.059823 | -0.14158 | -0.14648 | -0.08115 | -0.18104 | 122.0317 | 0.21265 | 0.29381 | -0.12822 | -0.051763 | 121.982 | 121.9348 | 121.9299 | 122.0458 | -0.003521 | 121.8954 | 121.9482 | 122.0247 | 121.8707 | -122.1576
1564.2188 | 122.2641 | -122.0169 | -0.013733 | -0.005418 | -0.058506 | 0.066099 | -0.011725 | -0.0080829 | 0.0082325 | -0.011751 | -0.0013673 | -0.0020852 | -0.0056553 | 0.021912 | -0.010954 | 0.010204 | -0.003172 | -0.012988 | -0.053175 | -0.09122 | -0.11444 | 0.0331 | -0.00811 | -0.16905 | -121.8317 | -0.13068 | -0.091601 | -0.010564 | -122.1209 | 122.05 | -0.039442 | 122.0271 | 122.0039 | -0.046088 | -0.077487 | -0.1007 | -0.10404 | -0.11695 | 122.0088 | 0.18519 | 0.28923 | -0.077868 | 0.003169 | 121.9637 | 121.9257 | 121.9025 | 122.0137 | 0.046833 | 121.8862 | 121.9253 | 122.0063 | 121.8479 | -122.1072
1565.9062 | 122.1725 | -122.0673 | 0.036621 | -0.005418 | -0.058079 | 0.066099 | -0.011725 | -0.0076555 | 0.0084461 | -0.019381 | -0.0015809 | -0.0018716 | -0.0054417 | 0.022126 | -0.010954 | 0.014783 | 0.001407 | -0.017566 | -0.057754 | -0.095798 | -0.10528 | 0.028521 | -0.00811 | -0.17821 | -121.8317 | -0.14442 | -0.087023 | -0.015142 | -122.1164 | 122.0958 | -0.094375 | 122.082 | 122.0497 | -0.046087 | -0.13242 | -0.1419 | -0.049105 | -0.18104 | 122.0592 | 0.23554 | 0.28465 | -0.12364 | -0.051763 | 122.0095 | 121.9715 | 121.962 | 122.0687 | -0.0081 | 121.9228 | 121.9802 | 122.0521 | 121.889 | -122.153
1567.6562 | 122.2504 | -121.9894 | 0.027466 | -0.005418 | -0.058079 | 0.066099 | -0.011511 | -0.0080829 | 0.0084461 | -0.011751 | -0.0011537 | -0.001658 | -0.0058689 | 0.022126 | -0.010954 | 0.014783 | 0.001407 | -0.017566 | -0.053175 | -0.095798 | -0.10528 | 0.028521 | -0.00811 | -0.16905 | -121.8363 | -0.13984 | -0.09618 | -0.010564 | -122.1301 | 122.018 | -0.080641 | 122.0042 | 121.9719 | -0.046087 | -0.12326 | -0.13275 | -0.14066 | -0.1673 | 121.9813 | 0.15314 | 0.2938 | -0.12365 | -0.03803 | 121.9363 | 121.8936 | 121.8842 | 121.9908 | 0.001055 | 121.8496 | 121.8933 | 121.9789 | 121.8204 | -122.1576
1569.4219 | 122.2595 | -122.0352 | -0.004578 | 0.002213 | -0.058292 | 0.065672 | -0.011725 | -0.0076555 | 0.0084461 | -0.019381 | -0.0013673 | -0.0018716 | -0.0056553 | 0.022339 | -0.011168 | 0.014783 | 0.001407 | -0.008409 | -0.053175 | -0.095798 | -0.10528 | 0.037679 | -0.00811 | -0.16905 | -121.8363 | -0.13984 | -0.091601 | -0.010564 | -122.1301 | 122.0729 | -0.048597 | 122.05 | 122.0268 | -0.046088 | -0.09122 | -0.1007 | -0.094885 | -0.13526 | 122.0271 | 0.19892 | 0.2938 | -0.087023 | -0.005986 | 121.982 | 121.9394 | 121.9299 | 122.0366 | 0.042257 | 121.8954 | 121.9436 | 122.0247 | 121.8662 | -122.1255
1571.1719 | 122.3053 | -122.0261 | -0.004578 | -0.005418 | -0.058079 | 0.066099 | -0.011725 | -0.0078693 | 0.0084461 | -0.011751 | -0.0013673 | -0.0018716 | -0.0056553 | 0.022126 | -0.011381 | 0.014783 | 0.005985 | -0.017566 | -0.057754 | -0.09122 | -0.10528 | 0.028521 | -0.017267 | -0.17821 | -121.8409 | -0.13984 | -0.091601 | -0.015142 | -122.1347 | 122.0546 | -0.053176 | 122.0408 | 122.0085 | -0.046087 | -0.086642 | -0.1007 | -0.10862 | -0.13526 | 122.0088 | 0.18519 | 0.29381 | -0.087023 | -0.010564 | 121.9683 | 121.9348 | 121.9208 | 122.032 | 0.033099 | 121.8862 | 121.9345 | 122.0109 | 121.8479 | -122.1301
1572.9219 | 122.319 | -122.0306 | 0.013733 | -0.005418 | -0.058292 | 0.066313 | -0.011725 | -0.0080829 | 0.0086597 | -0.019381 | -0.0015809 | -0.0018716 | -0.0056553 | 0.021912 | -0.010954 | 0.014783 | 0.001407 | -0.012988 | -0.053175 | -0.09122 | -0.10528 | 0.028521 | -0.017267 | -0.18279 | -121.8455 | -0.13068 | -0.091601 | -0.010564 | -122.1301 | 122.0592 | -0.066908 | 122.0454 | 122.0177 | -0.041509 | -0.10495 | -0.11901 | -0.099462 | -0.14441 | 122.0134 | 0.18519 | 0.28465 | -0.10533 | -0.024297 | 121.9775 | 121.9394 | 121.9254 | 122.032 | 0.014788 | 121.9 | 121.939 | 122.0201 | 121.8479 | -122.1438
1574.6719 | 122.2275 | -122.0627 | 0.027466 | -0.005418 | -0.058292 | 0.066313 | -0.011511 | -0.0076555 | 0.0084461 | -0.019381 | -0.0013673 | -0.0020852 | -0.0056553 | 0.022126 | -0.01074 | 0.019361 | 0.005985 | -0.012988 | -0.057754 | -0.095798 | -0.1007 | 0.023942 | -0.012689 | -0.17363 | -121.8455 | -0.1261 | -0.091601 | -0.015142 | -122.1393 | 122.0866 | -0.08522 | 122.082 | 122.0497 | -0.03693 | -0.12326 | -0.12817 | -0.076577 | -0.15357 | 122.05 | 0.21723 | 0.2938 | -0.11907 | -0.042608 | 122.0049 | 121.9669 | 121.962 | 122.0687 | -0.003524 | 121.9366 | 121.9711 | 122.0475 | 121.8891 | -122.1667
1576.3594 | 122.319 | -122.0123 | 0 | 0.002213 | -0.058079 | 0.065886 | -0.011938 | -0.0080829 | 0.0082325 | -0.0041205 | -0.0017945 | -0.0018716 | -0.0054417 | 0.022126 | -0.010954 | 0.014783 | 0.001407 | -0.012988 | -0.057754 | -0.095798 | -0.10528 | 0.037679 | -0.012689 | -0.16905 | -121.85 | -0.13526 | -0.087023 | -0.010564 | -122.1438 | 122.05 | -0.057754 | 122.0271 | 121.9993 | -0.050667 | -0.095798 | -0.10528 | -0.13151 | -0.13526 | 121.9996 | 0.1623 | 0.29381 | -0.087023 | -0.010564 | 121.9546 | 121.9165 | 121.907 | 122.0137 | 0.037679 | 121.8771 | 121.9253 | 122.0018 | 121.8433 | -122.1438
1578.0938 | 122.1817 | -122.0673 | 0.032043 | -0.005418 | -0.058506 | 0.066313 | -0.011725 | -0.0076555 | 0.0082325 | -0.027012 | -0.0017945 | -0.001658 | -0.0058689 | 0.022126 | -0.010954 | 0.005626 | 0.005985 | -0.012988 | -0.057754 | -0.095798 | -0.11444 | 0.0331 | -0.00811 | -0.17363 | -121.8455 | -0.13068 | -0.09618 | -0.015142 | -122.1438 | 122.1004 | -0.089797 | 122.0729 | 122.0543 | -0.046088 | -0.12784 | -0.14648 | -0.076578 | -0.16272 | 122.0592 | 0.22181 | 0.29838 | -0.12822 | -0.047185 | 122.0095 | 121.9715 | 121.9528 | 122.0732 | 0.001057 | 121.9366 | 121.9711 | 122.0521 | 121.8936 | -122.1759
1579.8594 | 122.3236 | -122.0215 | 0.004578 | -0.013049 | -0.058079 | 0.066313 | -0.011725 | -0.0080829 | 0.0086597 | -0.0041205 | -0.0013673 | -0.001658 | -0.0058689 | 0.022126 | -0.010954 | 0.010204 | 0.005985 | -0.017566 | -0.057754 | -0.09122 | -0.10986 | 0.028521 | -0.00811 | -0.16905 | -121.8546 | -0.13984 | -0.091601 | -0.015142 | -122.1438 | 122.05 | -0.062332 | 122.0317 | 122.0039 | -0.046087 | -0.095798 | -0.11443 | -0.12235 | -0.14442 | 122.0134 | 0.16687 | 0.28923 | -0.096179 | -0.01972 | 121.9637 | 121.9303 | 121.9116 | 122.0275 | 0.023943 | 121.8816 | 121.9299 | 122.0063 | 121.8524 | -122.1484
1581.5469 | 122.3007 | -122.0444 | 0.009155 | -0.005418 | -0.058292 | 0.065886 | -0.011511 | -0.0078693 | 0.0082325 | -0.0041205 | -0.0013673 | -0.001658 | -0.0056553 | 0.022339 | -0.011381 | 0.005626 | 0.005985 | -0.017566 | -0.057754 | -0.09122 | -0.10986 | 0.037679 | -0.00811 | -0.17363 | -121.8546 | -0.13068 | -0.10076 | -0.015142 | -122.153 | 122.0821 | -0.066909 | 122.05 | 122.0268 | -0.055245 | -0.10037 | -0.11901 | -0.10862 | -0.13984 | 122.0363 | 0.18976 | 0.29838 | -0.10991 | -0.024297 | 121.9866 | 121.9532 | 121.9345 | 122.0504 | 0.028524 | 121.9137 | 121.9436 | 122.0292 | 121.8707 | -122.1622
1583.2969 | 122.3053 | -122.0352 | -0.004578 | 0.002213 | -0.058506 | 0.066099 | -0.011938 | -0.0076555 | 0.0086597 | -0.011751 | -0.0013673 | -0.0018716 | -0.0058689 | 0.022126 | -0.010954 | 0.014783 | 0.005985 | -0.022144 | -0.053175 | -0.10038 | -0.10986 | 0.028521 | -0.00811 | -0.17821 | -121.8638 | -0.13984 | -0.10076 | -0.019721 | -122.1576 | 122.0637 | -0.048597 | 122.05 | 122.0131 | -0.050665 | -0.095799 | -0.10528 | -0.12236 | -0.13526 | 122.0271 | 0.17145 | 0.29381 | -0.096181 | -0.015143 | 121.982 | 121.9348 | 121.9254 | 122.0412 | 0.033099 | 121.8954 | 121.9345 | 122.0155 | 121.857 | -122.153
1585 | 122.2137 | -122.0993 | 0.027466 | -0.005418 | -0.05872 | 0.066313 | -0.011725 | -0.0080829 | 0.0080187 | -0.0041205 | -0.0017945 | -0.0018716 | -0.0056553 | 0.022126 | -0.01074 | 0.010204 | 0.001407 | -0.017566 | -0.057754 | -0.086641 | -0.10986 | 0.023942 | -0.00811 | -0.18279 | -121.8638 | -0.13526 | -0.091601 | -0.015142 | -122.153 | 122.1232 | -0.08522 | 122.1095 | 122.0817 | -0.041508 | -0.11411 | -0.13732 | -0.053692 | -0.16273 | 122.0912 | 0.23553 | 0.28923 | -0.11907 | -0.042608 | 122.0416 | 122.0127 | 121.9894 | 122.1007 | -0.003524 | 121.964 | 122.0077 | 122.0842 | 121.9165 | -122.1805
1586.7656 | 122.3007 | -122.049 | 0.004578 | -0.02068 | -0.058506 | 0.065886 | -0.011938 | -0.0078693 | 0.0080187 | -0.019381 | -0.0015809 | -0.001658 | -0.0056553 | 0.022339 | -0.010954 | 0.010204 | 0.001407 | -0.022144 | -0.048597 | -0.09122 | -0.10986 | 0.037679 | -0.012689 | -0.17821 | -121.8729 | -0.13984 | -0.10076 | -0.010564 | -122.1576 | 122.0866 | -0.053175 | 122.0592 | 122.0268 | -0.059823 | -0.095798 | -0.11443 | -0.10862 | -0.14442 | 122.0363 | 0.17602 | 0.28465 | -0.10534 | -0.015142 | 122.0004 | 121.9577 | 121.9391 | 122.0504 | 0.033101 | 121.9091 | 121.9482 | 122.0384 | 121.8707 | -122.1622
1588.5156 | 122.2 | -122.0947 | 0.018311 | -0.005418 | -0.058506 | 0.065886 | -0.011938 | -0.0078693 | 0.0086597 | -0.0041205 | -0.0015809 | -0.001658 | -0.0060825 | 0.022339 | -0.010954 | 0.014783 | 0.005985 | -0.022144 | -0.053175 | -0.095798 | -0.10528 | 0.0331 | -0.012689 | -0.17363 | -121.8729 | -0.14899 | -0.09618 | -0.015142 | -122.1622 | 122.1278 | -0.071486 | 122.1095 | 122.0726 | -0.055244 | -0.11411 | -0.12359 | -0.067427 | -0.16731 | 122.082 | 0.2218 | 0.28923 | -0.11449 | -0.033453 | 122.0416 | 121.9989 | 121.9894 | 122.1007 | 0.014789 | 121.9457 | 121.9985 | 122.0796 | 121.9211 | -122.1805
1590.2656 | 122.2549 | -122.0581 | 0.018311 | 0.002213 | -0.058292 | 0.066099 | -0.011725 | -0.0080829 | 0.0082325 | -0.0041205 | -0.0015809 | -0.0018716 | -0.0056553 | 0.022126 | -0.01074 | 0.010204 | 0.010564 | -0.012988 | -0.057754 | -0.095798 | -0.10986 | 0.023942 | -0.00811 | -0.17363 | -121.8683 | -0.13984 | -0.091601 | -0.0243 | -122.1622 | 122.082 | -0.076065 | 122.0683 | 122.0451 | -0.03693 | -0.11411 | -0.12817 | -0.10405 | -0.15815 | 122.05 | 0.18976 | 0.29381 | -0.10991 | -0.042611 | 122.0004 | 121.9623 | 121.9482 | 122.0687 | 0.005631 | 121.9183 | 121.9665 | 122.0338 | 121.8845 | -122.1805
1592.0156 | 122.3099 | -122.0581 | -0.009155 | -0.02068 | -0.058292 | 0.065458 | -0.011297 | -0.0078693 | 0.0084461 | -0.019381 | -0.0015809 | -0.001658 | -0.0058689 | 0.022126 | -0.011168 | 0.005626 | 0.005985 | -0.017566 | -0.053175 | -0.10038 | -0.1007 | 0.0331 | -0.012689 | -0.17821 | -121.8775 | -0.13984 | -0.09618 | -0.015142 | -122.1759 | 122.0912 | -0.04402 | 122.0637 | 122.0405 | -0.050666 | -0.091222 | -0.091545 | -0.11779 | -0.13068 | 122.0454 | 0.1806 | 0.29839 | -0.087025 | -0.005987 | 122.0049 | 121.9577 | 121.9574 | 122.0641 | 0.042255 | 121.9183 | 121.9619 | 122.043 | 121.8799 | -122.1667
1593.7188 | 122.2916 | -122.0581 | 0 | -0.005418 | -0.058506 | 0.065886 | -0.011511 | -0.0076555 | 0.0082325 | -0.027012 | -0.0015809 | -0.0018716 | -0.0058689 | 0.022339 | -0.011168 | 0.014783 | 0.001407 | -0.012988 | -0.053175 | -0.086641 | -0.10528 | 0.028521 | -0.012689 | -0.17363 | -121.8775 | -0.13984 | -0.087023 | -0.015142 | -122.1667 | 122.0866 | -0.053175 | 122.0729 | 122.0451 | -0.041509 | -0.086641 | -0.10528 | -0.10863 | -0.13984 | 122.0454 | 0.1806 | 0.28923 | -0.087023 | -0.015142 | 122.0049 | 121.9715 | 121.9528 | 122.0595 | 0.028521 | 121.9183 | 121.9711 | 122.043 | 121.8845 | -122.1667
1595.4844 | 122.3648 | -122.0581 | 0 | -0.013049 | -0.058506 | 0.065886 | -0.011725 | -0.0080829 | 0.0084461 | -0.0041205 | -0.0011537 | -0.0018716 | -0.0060825 | 0.021912 | -0.010954 | 0.014783 | 0.001407 | -0.017566 | -0.057754 | -0.09122 | -0.1007 | 0.0331 | -0.00811 | -0.17821 | -121.8775 | -0.14442 | -0.087023 | -0.005985 | -122.1759 | 122.0912 | -0.057754 | 122.0729 | 122.0405 | -0.050666 | -0.09122 | -0.1007 | -0.11779 | -0.14442 | 122.05 | 0.1806 | 0.29839 | -0.087023 | -0.005985 | 122.0004 | 121.9669 | 121.9574 | 122.0595 | 0.0331 | 121.9137 | 121.9711 | 122.0521 | 121.8799 | -122.1759
1597.2344 | 122.2275 | -122.081 | 0.032043 | -0.005418 | -0.05872 | 0.066099 | -0.011725 | -0.0078693 | 0.0084461 | -0.011751 | -0.0015809 | -0.0020852 | -0.0056553 | 0.022126 | -0.011168 | 0.014783 | 0.001407 | -0.012988 | -0.057754 | -0.10038 | -0.096121 | 0.023942 | -0.00811 | -0.17821 | -121.8775 | -0.13526 | -0.091601 | -0.019721 | -122.1713 | 122.1049 | -0.089797 | 122.0958 | 122.068 | -0.03693 | -0.13242 | -0.12816 | -0.090318 | -0.1673 | 122.0729 | 0.20349 | 0.29381 | -0.12364 | -0.051764 | 122.0232 | 121.9806 | 121.9849 | 122.0824 | -0.008101 | 121.9457 | 121.9894 | 122.0613 | 121.9028 | -122.2034
1599 | 122.3465 | -122.0398 | -0.013733 | -0.005418 | -0.058933 | 0.066099 | -0.011725 | -0.0076555 | 0.0080187 | -0.011751 | -0.0015809 | -0.001658 | -0.0056553 | 0.021912 | -0.010954 | 0.019361 | 0.005985 | -0.012988 | -0.048597 | -0.09122 | -0.1007 | 0.028521 | -0.012689 | -0.17821 | -121.8867 | -0.13526 | -0.09618 | -0.015142 | -122.1805 | 122.0683 | -0.034864 | 122.0592 | 122.0268 | -0.041509 | -0.077487 | -0.086967 | -0.14067 | -0.12153 | 122.0271 | 0.15313 | 0.29381 | -0.082447 | -0.001409 | 121.9912 | 121.9486 | 121.9391 | 122.0458 | 0.042254 | 121.9045 | 121.9436 | 122.0247 | 121.8616 | -122.1667
1600.6875 | 122.3373 | -122.0535 | -0.009155 | -0.02068 | -0.058506 | 0.065886 | -0.011511 | -0.0080829 | 0.0082325 | -0.0041205 | -0.0015809 | -0.0018716 | -0.0056553 | 0.022126 | -0.010954 | 0.010204 | 0.001407 | -0.012988 | -0.057754 | -0.086641 | -0.10528 | 0.0331 | -0.003531 | -0.17821 | -121.8867 | -0.13984 | -0.091601 | -0.015142 | -122.185 | 122.0866 | -0.048599 | 122.0637 | 122.0405 | -0.046088 | -0.077486 | -0.096124 | -0.13152 | -0.13068 | 122.05 | 0.16687 | 0.29838 | -0.082446 | -0.005987 | 121.9958 | 121.9669 | 121.9482 | 122.0549 | 0.042255 | 121.9137 | 121.9619 | 122.0384 | 121.8753 | -122.1759
1602.4531 | 122.3511 | -122.0673 | 0.013733 | -0.013049 | -0.058506 | 0.065886 | -0.011725 | -0.0078693 | 0.0082325 | -0.011751 | -0.0013673 | -0.0014444 | -0.0058689 | 0.022126 | -0.011168 | 0.014783 | 0.010564 | -0.017566 | -0.057754 | -0.10038 | -0.10528 | 0.028521 | -0.017267 | -0.18279 | -121.8912 | -0.13984 | -0.087023 | -0.019721 | -122.185 | 122.0958 | -0.071487 | 122.082 | 122.0497 | -0.046087 | -0.11411 | -0.11901 | -0.11779 | -0.15357 | 122.05 | 0.17602 | 0.29381 | -0.10076 | -0.033454 | 122.0095 | 121.9669 | 121.962 | 122.0778 | 0.014788 | 121.9274 | 121.9802 | 122.0475 | 121.8845 | -122.1988
1604.2031 | 122.2412 | -122.1405 | 0.027466 | -0.013049 | -0.058933 | 0.065672 | -0.011511 | -0.0078693 | 0.0082325 | -0.011751 | -0.0011537 | -0.0018716 | -0.0056553 | 0.022553 | -0.010954 | 0.010204 | 0.005985 | -0.012988 | -0.057754 | -0.095798 | -0.10528 | 0.0331 | -0.017267 | -0.17821 | -121.8958 | -0.13984 | -0.09618 | -0.015142 | -122.185 | 122.1736 | -0.08522 | 122.1507 | 122.1275 | -0.046088 | -0.12326 | -0.13275 | -0.044545 | -0.1673 | 122.1232 | 0.24468 | 0.28923 | -0.12365 | -0.042608 | 122.0827 | 122.0447 | 122.0352 | 122.1465 | 0.005634 | 122.0007 | 122.0443 | 122.1254 | 121.9623 | -122.2125
1605.9531 | 122.2595 | -122.0901 | 0.027466 | -0.005418 | -0.058506 | 0.065886 | -0.011725 | -0.0076555 | 0.0080187 | -0.019381 | -0.0017945 | -0.0020852 | -0.0056553 | 0.022339 | -0.011168 | 0.019361 | 0.005985 | -0.008409 | -0.062332 | -0.095798 | -0.1007 | 0.037679 | -0.00811 | -0.17821 | -121.9004 | -0.13984 | -0.091601 | -0.019721 | -122.1896 | 122.1278 | -0.089798 | 122.1095 | 122.0817 | -0.046088 | -0.12326 | -0.12817 | -0.099478 | -0.1673 | 122.082 | 0.18975 | 0.28923 | -0.11907 | -0.047187 | 122.0278 | 121.9944 | 121.9894 | 122.0961 | 0.010213 | 121.9503 | 121.9985 | 122.0704 | 121.9119 | -122.2171
1607.7031 | 122.2595 | -122.1268 | 0.027466 | 0.002213 | -0.05872 | 0.065886 | -0.011725 | -0.0078693 | 0.0082325 | -0.011751 | -0.0013673 | -0.0018716 | -0.0054417 | 0.022339 | -0.010954 | 0.014783 | 0.001407 | -0.017566 | -0.06691 | -0.095798 | -0.10528 | 0.028521 | -0.012689 | -0.17363 | -121.9004 | -0.13984 | -0.091601 | -0.019721 | -122.1988 | 122.1553 | -0.094376 | 122.1416 | 122.1092 | -0.046087 | -0.12326 | -0.13275 | -0.072015 | -0.1673 | 122.1141 | 0.22637 | 0.29839 | -0.11907 | -0.047187 | 122.0599 | 122.031 | 122.0215 | 122.1282 | 0.001055 | 121.9869 | 122.0352 | 122.107 | 121.9531 | -122.2263
1609.4688 | 122.3145 | -122.113 | 0.009155 | 0.002213 | -0.058933 | 0.065886 | -0.011938 | -0.0080829 | 0.0082325 | -0.019381 | -0.0015809 | -0.0020852 | -0.0056553 | 0.022126 | -0.010954 | 0.010204 | 0.010564 | -0.012988 | -0.057754 | -0.10038 | -0.10986 | 0.0331 | -0.012689 | -0.18737 | -121.905 | -0.13984 | -0.091601 | -0.019721 | -122.1942 | 122.1461 | -0.066909 | 122.1232 | 122.1 | -0.046088 | -0.10953 | -0.11901 | -0.081169 | -0.14899 | 122.1003 | 0.20806 | 0.28923 | -0.10076 | -0.028876 | 122.0553 | 122.0127 | 122.0032 | 122.1236 | 0.023945 | 121.9732 | 122.0214 | 122.0933 | 121.9257 | -122.2034
1611.1719 | 122.2916 | -122.0993 | 0.013733 | 0.009844 | -0.058506 | 0.065672 | -0.011725 | -0.0078693 | 0.0078051 | -0.011751 | -0.0013673 | -0.0018716 | -0.0054417 | 0.022339 | -0.010954 | 0.014783 | 0.010564 | -0.017566 | -0.053175 | -0.09122 | -0.10528 | 0.028521 | -0.012689 | -0.18279 | -121.905 | -0.14442 | -0.09618 | -0.0243 | -122.1988 | 122.1278 | -0.066908 | 122.1141 | 122.0817 | -0.046087 | -0.10495 | -0.11901 | -0.099481 | -0.15815 | 122.0866 | 0.19433 | 0.29381 | -0.10991 | -0.038033 | 122.0461 | 122.0081 | 121.994 | 122.1099 | 0.014788 | 121.9549 | 122.0031 | 122.075 | 121.9165 | -122.2125
1612.9375 | 122.3511 | -122.0993 | 0.018311 | 0.002213 | -0.05872 | 0.065886 | -0.011511 | -0.0080829 | 0.0082325 | -0.0041205 | -0.0020083 | -0.0020852 | -0.0054417 | 0.022126 | -0.011168 | 0.014783 | 0.005985 | -0.026723 | -0.062332 | -0.095798 | -0.10528 | 0.023942 | -0.021846 | -0.18737 | -121.905 | -0.14442 | -0.087023 | -0.019721 | -122.2034 | 122.1232 | -0.080643 | 122.1141 | 122.0726 | -0.050665 | -0.11411 | -0.12359 | -0.10406 | -0.16273 | 122.0775 | 0.19433 | 0.29838 | -0.10533 | -0.038032 | 122.037 | 122.0035 | 121.994 | 122.1053 | 0.005631 | 121.9549 | 122.0123 | 122.0796 | 121.9119 | -122.2217
1614.6406 | 122.2961 | -122.1176 | 0.041199 | -0.005418 | -0.05872 | 0.065886 | -0.011511 | -0.0080829 | 0.0080187 | -0.011751 | -0.0015809 | -0.0018716 | -0.0056553 | 0.022339 | -0.011381 | 0.010204 | -0.003172 | -0.017566 | -0.057754 | -0.086641 | -0.10986 | 0.028521 | -0.017267 | -0.18279 | -121.8958 | -0.13526 | -0.091601 | -0.0243 | -122.2034 | 122.1461 | -0.098953 | 122.1278 | 122.1 | -0.046087 | -0.12784 | -0.15106 | -0.085748 | -0.17646 | 122.1003 | 0.2218 | 0.30754 | -0.1328 | -0.065499 | 122.0599 | 122.031 | 122.0078 | 122.1144 | -0.012678 | 121.9824 | 122.026 | 122.0933 | 121.9348 | -122.2446
1616.4062 | 122.3419 | -122.0901 | -0.009155 | -0.013049 | -0.05872 | 0.065672 | -0.011725 | -0.0074419 | 0.0082325 | -0.019381 | -0.0013673 | -0.0018716 | -0.0054417 | 0.022126 | -0.010954 | 0.005626 | 0.001407 | -0.017566 | -0.053175 | -0.095798 | -0.10528 | 0.028521 | -0.00811 | -0.18737 | -121.9096 | -0.14442 | -0.09618 | -0.015142 | -122.2034 | 122.1187 | -0.04402 | 122.0958 | 122.0726 | -0.046087 | -0.086643 | -0.096124 | -0.11321 | -0.13526 | 122.082 | 0.18059 | 0.29381 | -0.087025 | -0.005987 | 122.037 | 121.9944 | 121.9849 | 122.0916 | 0.037676 | 121.9457 | 121.994 | 122.075 | 121.9028 | -122.1942
1618.0938 | 122.3831 | -122.0673 | -0.022888 | -0.005418 | -0.058506 | 0.065886 | -0.011725 | -0.0076555 | 0.0084461 | -0.027012 | -0.0015809 | -0.0018716 | -0.0058689 | 0.022339 | -0.011381 | 0.010204 | 0.010564 | -0.017566 | -0.053175 | -0.095798 | -0.10986 | 0.028521 | -0.00811 | -0.18279 | -121.9096 | -0.13526 | -0.091601 | -0.019721 | -122.2125 | 122.0958 | -0.030287 | 122.0775 | 122.0497 | -0.046087 | -0.07291 | -0.086969 | -0.14526 | -0.11237 | 122.0592 | 0.15771 | 0.30297 | -0.068713 | 0.003167 | 122.0141 | 121.9715 | 121.9574 | 122.0778 | 0.051409 | 121.932 | 121.9757 | 122.0475 | 121.8845 | -122.1896
1619.8438 | 122.3694 | -122.0901 | -0.013733 | -0.005418 | -0.058933 | 0.065458 | -0.011938 | -0.0078693 | 0.0080187 | -0.011751 | -0.0013673 | -0.0020852 | -0.0056553 | 0.022339 | -0.010954 | 0.023939 | 0.001407 | -0.012988 | -0.057754 | -0.09122 | -0.1007 | 0.0331 | -0.00811 | -0.18279 | -121.9141 | -0.13984 | -0.09618 | -0.0243 | -122.2171 | 122.1232 | -0.044021 | 122.1141 | 122.0772 | -0.046088 | -0.077487 | -0.086967 | -0.12695 | -0.1261 | 122.082 | 0.17601 | 0.30297 | -0.082447 | -0.010567 | 122.0324 | 121.9989 | 121.9894 | 122.0916 | 0.046833 | 121.9503 | 121.994 | 122.0658 | 121.9074 | -122.2034
1621.6094 | 122.3602 | -122.1039 | 0.009155 | -0.005418 | -0.058933 | 0.065886 | -0.011938 | -0.0076555 | 0.0082325 | -0.011751 | -0.0013673 | -0.0020852 | -0.0058689 | 0.022339 | -0.011595 | 0.010204 | 0.005985 | -0.017566 | -0.053175 | -0.10038 | -0.10528 | 0.028521 | -0.012689 | -0.17821 | -121.9141 | -0.14442 | -0.091601 | -0.015142 | -122.2079 | 122.1324 | -0.06233 | 122.1141 | 122.0863 | -0.046087 | -0.10953 | -0.11443 | -0.10406 | -0.15357 | 122.0912 | 0.18975 | 0.29381 | -0.10076 | -0.024297 | 122.0507 | 122.0035 | 121.9986 | 122.1099 | 0.019366 | 121.9595 | 122.0123 | 122.0887 | 121.9257 | -122.2171
1623.3594 | 122.2778 | -122.1405 | 0.018311 | -0.013049 | -0.058933 | 0.065672 | -0.011725 | -0.0078693 | 0.0078051 | -0.019381 | -0.0015809 | -0.002299 | -0.0058689 | 0.022553 | -0.01074 | 0.010204 | 0.001407 | -0.012988 | -0.057754 | -0.095798 | -0.1007 | 0.0331 | -0.017267 | -0.18737 | -121.9187 | -0.13984 | -0.091601 | -0.010564 | -122.2171 | 122.1736 | -0.076065 | 122.1507 | 122.1275 | -0.046088 | -0.11411 | -0.11901 | -0.076597 | -0.15815 | 122.1232 | 0.22179 | 0.29839 | -0.10991 | -0.028875 | 122.0827 | 122.0447 | 122.0398 | 122.1419 | 0.014789 | 122.0007 | 122.0489 | 122.1299 | 121.9531 | -122.2354
1625.0469 | 122.2778 | -122.113 | 0.045776 | -0.013049 | -0.058933 | 0.065672 | -0.011511 | -0.0078693 | 0.0082325 | -0.011751 | -0.0015809 | -0.001658 | -0.0056553 | 0.022126 | -0.011168 | 0.023939 | 0.010564 | -0.008409 | -0.062332 | -0.095798 | -0.1007 | 0.0331 | -0.012689 | -0.16905 | -121.9279 | -0.13984 | -0.09618 | -0.019721 | -122.2171 | 122.1461 | -0.10811 | 122.137 | 122.1046 | -0.041509 | -0.14157 | -0.14648 | -0.10406 | -0.18561 | 122.1003 | 0.18517 | 0.28923 | -0.14196 | -0.065497 | 122.0507 | 122.0172 | 122.0123 | 122.1236 | -0.012676 | 121.9732 | 122.0169 | 122.0933 | 121.944 | -122.2629
1626.7969 | 122.3145 | -122.1313 | 0.022888 | 0.009844 | -0.05872 | 0.065458 | -0.011511 | -0.0078693 | 0.0080187 | -0.011751 | -0.0015809 | -0.0018716 | -0.0058689 | 0.022767 | -0.011168 | 0.010204 | -0.003172 | -0.012988 | -0.053175 | -0.086641 | -0.10986 | 0.028521 | -0.012689 | -0.18737 | -121.9233 | -0.14442 | -0.09618 | -0.015142 | -122.2217 | 122.1599 | -0.076063 | 122.1416 | 122.1184 | -0.041509 | -0.10953 | -0.13275 | -0.090331 | -0.1673 | 122.1187 | 0.20806 | 0.29839 | -0.11907 | -0.03803 | 122.0782 | 122.0447 | 122.0215 | 122.1282 | 0.005633 | 121.9869 | 122.0352 | 122.1162 | 121.944 | -122.2446
1628.5469 | 122.3877 | -122.113 | -0.004578 | -0.005418 | -0.058933 | 0.065672 | -0.011511 | -0.0072283 | 0.0078051 | -0.011751 | -0.0013673 | -0.001658 | -0.0058689 | 0.022767 | -0.011168 | 0.014783 | 0.005985 | -0.026723 | -0.057754 | -0.086641 | -0.1007 | 0.023942 | -0.017267 | -0.18279 | -121.9279 | -0.13526 | -0.09618 | -0.015142 | -122.2217 | 122.137 | -0.053176 | 122.1278 | 122.0863 | -0.050665 | -0.082063 | -0.096122 | -0.10864 | -0.13068 | 122.0958 | 0.18517 | 0.29381 | -0.091602 | -0.010564 | 122.0553 | 122.0264 | 122.0123 | 122.119 | 0.02852 | 121.9778 | 122.0169 | 122.0979 | 121.9302 | -122.2171
1630.3125 | 122.3236 | -122.1222 | 0.022888 | -0.005418 | -0.058933 | 0.066099 | -0.011725 | -0.0080829 | 0.0080187 | -0.0041205 | -0.0015809 | -0.001658 | -0.0060825 | 0.022553 | -0.011168 | 0.005626 | 0.001407 | -0.012988 | -0.053175 | -0.09122 | -0.10986 | 0.028521 | -0.021846 | -0.18279 | -121.9279 | -0.13526 | -0.091601 | -0.015142 | -122.2217 | 122.1507 | -0.076063 | 122.1278 | 122.1092 | -0.041509 | -0.11411 | -0.13275 | -0.099487 | -0.15815 | 122.1003 | 0.19432 | 0.29381 | -0.11449 | -0.03803 | 122.069 | 122.031 | 122.0123 | 122.1236 | 0.005633 | 121.9869 | 122.0306 | 122.1071 | 121.9394 | -122.2446
1632.0625 | 122.3648 | -122.1176 | 0 | -0.013049 | -0.05872 | 0.065244 | -0.011511 | -0.0080829 | 0.0082325 | -0.011751 | -0.0017945 | -0.001658 | -0.0056553 | 0.022553 | -0.011168 | 0.010204 | 0.005985 | -0.017566 | -0.053175 | -0.095798 | -0.10528 | 0.028521 | -0.017267 | -0.18279 | -121.9279 | -0.13526 | -0.091601 | -0.015142 | -122.2263 | 122.1461 | -0.053175 | 122.1278 | 122.1 | -0.046087 | -0.095798 | -0.10528 | -0.10864 | -0.13526 | 122.1003 | 0.18974 | 0.29839 | -0.091601 | -0.015142 | 122.0644 | 122.0218 | 122.0123 | 122.1236 | 0.028521 | 121.9824 | 122.026 | 122.1025 | 121.9348 | -122.2263
1633.75 | 122.2916 | -122.1497 | 0.013733 | -0.005418 | -0.058506 | 0.065458 | -0.011297 | -0.0078693 | 0.0082325 | -0.019381 | -0.0017945 | -0.0018716 | -0.0056553 | 0.022767 | -0.010954 | 0.010204 | 0.010564 | -0.012988 | -0.057754 | -0.09122 | -0.10528 | 0.028521 | -0.017267 | -0.18279 | -121.937 | -0.13068 | -0.09618 | -0.0243 | -122.2354 | 122.1782 | -0.071487 | 122.1599 | 122.1367 | -0.041509 | -0.10495 | -0.11901 | -0.085757 | -0.14441 | 122.1324 | 0.21263 | 0.29839 | -0.10991 | -0.038033 | 122.0919 | 122.0584 | 122.0444 | 122.1602 | 0.014788 | 122.019 | 122.0535 | 122.1254 | 121.9669 | -122.2491
1635.5156 | 122.287 | -122.1359 | 0.027466 | -0.013049 | -0.059147 | 0.065886 | -0.011938 | -0.0080829 | 0.0078051 | -0.027012 | -0.0017945 | -0.001658 | -0.0060825 | 0.022339 | -0.011381 | 0.010204 | 0.001407 | -0.017566 | -0.062332 | -0.095798 | -0.10986 | 0.0331 | -0.012689 | -0.18737 | -121.9279 | -0.13526 | -0.091601 | -0.019721 | -122.2308 | 122.169 | -0.089798 | 122.1461 | 122.1184 | -0.050666 | -0.12326 | -0.13732 | -0.094911 | -0.16273 | 122.1232 | 0.20805 | 0.30297 | -0.11907 | -0.047187 | 122.0736 | 122.0401 | 122.0261 | 122.1373 | 0.005634 | 122.0007 | 122.0443 | 122.1162 | 121.9486 | -122.2583
1637.2656 | 122.3282 | -122.1359 | 0.004578 | 0.002213 | -0.058933 | 0.065886 | -0.011725 | -0.0080829 | 0.0080187 | -0.0041205 | -0.0015809 | -0.0020852 | -0.0056553 | 0.022339 | -0.010954 | 0.014783 | 0.010564 | -0.017566 | -0.053175 | -0.09122 | -0.10528 | 0.037679 | -0.021846 | -0.18737 | -121.9325 | -0.14442 | -0.09618 | -0.019721 | -122.24 | 122.1736 | -0.057753 | 122.1507 | 122.1184 | -0.055245 | -0.095798 | -0.10986 | -0.10407 | -0.14899 | 122.1141 | 0.20347 | 0.30754 | -0.10076 | -0.024299 | 122.0828 | 122.0447 | 122.0306 | 122.1465 | 0.033101 | 121.9915 | 122.0397 | 122.1162 | 121.9486 | -122.2446
1639.0156 | 122.4106 | -122.1222 | -0.027466 | -0.013049 | -0.059147 | 0.065458 | -0.011938 | -0.0080829 | 0.0080187 | -0.0041205 | -0.0015809 | -0.001658 | -0.0058689 | 0.022981 | -0.011168 | 0.014783 | 0.005985 | -0.012988 | -0.048597 | -0.095798 | -0.10528 | 0.023942 | -0.021846 | -0.18279 | -121.9416 | -0.13526 | -0.087023 | -0.019721 | -122.2354 | 122.1461 | -0.021131 | 122.137 | 122.1092 | -0.03693 | -0.068332 | -0.077813 | -0.11322 | -0.10779 | 122.1003 | 0.18058 | 0.29381 | -0.059557 | 0.007745 | 122.0736 | 122.0264 | 122.0169 | 122.1282 | 0.051408 | 121.9869 | 122.0352 | 122.1025 | 121.9394 | -122.2079
1640.7031 | 122.3877 | -122.1313 | 0.004578 | -0.013049 | -0.05872 | 0.065672 | -0.011511 | -0.0080829 | 0.0080187 | -0.019381 | -0.0013673 | -0.0018716 | -0.0058689 | 0.022339 | -0.011168 | 0.019361 | 0.005985 | -0.012988 | -0.053175 | -0.10038 | -0.1007 | 0.028521 | -0.012689 | -0.18279 | -121.9416 | -0.14442 | -0.10076 | -0.015142 | -122.24 | 122.1599 | -0.057753 | 122.1507 | 122.1184 | -0.041509 | -0.10495 | -0.10528 | -0.10865 | -0.14899 | 122.1187 | 0.18974 | 0.29839 | -0.10534 | -0.01972 | 122.0782 | 122.031 | 122.0306 | 122.1373 | 0.023943 | 121.9869 | 122.0306 | 122.1162 | 121.9486 | -122.2446
1642.4531 | 122.3145 | -122.1588 | 0.009155 | 0.002213 | -0.058933 | 0.065458 | -0.011725 | -0.0078693 | 0.0080187 | -0.019381 | -0.0017945 | -0.0020852 | -0.0054417 | 0.022339 | -0.011168 | 0.014783 | 0.005985 | -0.022144 | -0.048597 | -0.095798 | -0.10528 | 0.028521 | -0.012689 | -0.18279 | -121.9462 | -0.13526 | -0.09618 | -0.015142 | -122.2492 | 122.1873 | -0.057752 | 122.1736 | 122.1367 | -0.050665 | -0.10495 | -0.11443 | -0.090339 | -0.14441 | 122.1461 | 0.21263 | 0.30297 | -0.10533 | -0.024297 | 122.1102 | 122.063 | 122.0535 | 122.1648 | 0.019366 | 122.0236 | 122.0626 | 122.1437 | 121.976 | -122.2583
1644.2031 | 122.374 | -122.1405 | 0 | -0.005418 | -0.059147 | 0.065458 | -0.011297 | -0.0080829 | 0.0080187 | -0.011751 | -0.0011537 | -0.0020852 | -0.0060825 | 0.022126 | -0.010954 | 0.014783 | 0.001407 | -0.017566 | -0.057754 | -0.09122 | -0.10528 | 0.0331 | -0.00811 | -0.19195 | -121.9462 | -0.13526 | -0.09618 | -0.015142 | -122.2492 | 122.1736 | -0.057754 | 122.1553 | 122.1229 | -0.050666 | -0.09122 | -0.10528 | -0.10865 | -0.13526 | 122.1324 | 0.19432 | 0.30297 | -0.09618 | -0.015142 | 122.0827 | 122.0493 | 122.0352 | 122.1419 | 0.0331 | 122.0052 | 122.0443 | 122.1254 | 121.9486 | -122.2492
1645.9062 | 122.374 | -122.1451 | 0 | 0.002213 | -0.058933 | 0.065458 | -0.011725 | -0.0082965 | 0.0082325 | -0.019381 | -0.0015809 | -0.0018716 | -0.0058689 | 0.022553 | -0.010954 | 0.010204 | 0.005985 | -0.012988 | -0.053175 | -0.10038 | -0.10528 | 0.028521 | -0.017267 | -0.17363 | -121.9508 | -0.13526 | -0.087023 | -0.010564 | -122.2446 | 122.1736 | -0.053175 | 122.1553 | 122.1321 | -0.041509 | -0.10038 | -0.10528 | -0.099492 | -0.13526 | 122.1278 | 0.19432 | 0.29381 | -0.087023 | -0.010564 | 122.0919 | 122.0447 | 122.0398 | 122.1511 | 0.028521 | 122.0098 | 122.0581 | 122.1345 | 121.9714 | -122.2446
1647.6562 | 122.3236 | -122.1542 | 0.013733 | 0.002213 | -0.058506 | 0.065458 | -0.011725 | -0.0078693 | 0.0078051 | -0.019381 | -0.0015809 | -0.0018716 | -0.0054417 | 0.022339 | -0.010954 | 0.010204 | 0.010564 | -0.012988 | -0.053175 | -0.09122 | -0.1007 | 0.028521 | -0.00811 | -0.2011 | -121.9462 | -0.14442 | -0.091601 | -0.0243 | -122.2492 | 122.1828 | -0.066908 | 122.1644 | 122.1412 | -0.041509 | -0.10495 | -0.11443 | -0.094916 | -0.15815 | 122.1461 | 0.20805 | 0.30297 | -0.10533 | -0.038033 | 122.1011 | 122.063 | 122.0535 | 122.1648 | 0.014788 | 122.0098 | 122.0626 | 122.1299 | 121.9531 | -122.2629
1649.4219 | 122.3785 | -122.1176 | 0 | -0.02068 | -0.059361 | 0.065458 | -0.011725 | -0.0080829 | 0.0078051 | -0.011751 | -0.0011537 | -0.0018716 | -0.0058689 | 0.022553 | -0.011168 | 0.010204 | 0.005985 | -0.017566 | -0.053175 | -0.09122 | -0.10528 | 0.0331 | -0.012689 | -0.18279 | -121.9553 | -0.13068 | -0.091601 | -0.019721 | -122.2537 | 122.1507 | -0.053175 | 122.1278 | 122.1 | -0.050666 | -0.09122 | -0.10528 | -0.13612 | -0.13068 | 122.1049 | 0.16227 | 0.29839 | -0.091601 | -0.019721 | 122.0644 | 122.0264 | 122.0123 | 122.1236 | 0.0331 | 121.9869 | 122.026 | 122.0979 | 121.9348 | -122.2537
1651.1719 | 122.3145 | -122.1725 | 0.022888 | -0.005418 | -0.058933 | 0.065458 | -0.011725 | -0.0080829 | 0.0080187 | -0.011751 | -0.0017945 | -0.001658 | -0.0060825 | 0.022553 | -0.011168 | 0.023939 | 0.005985 | -0.022144 | -0.053175 | -0.095798 | -0.1007 | 0.0331 | -0.012689 | -0.19195 | -121.9553 | -0.13068 | -0.09618 | -0.019721 | -122.2537 | 122.2056 | -0.076063 | 122.1965 | 122.1504 | -0.055244 | -0.11869 | -0.12359 | -0.081184 | -0.15357 | 122.1599 | 0.2172 | 0.29839 | -0.11907 | -0.042609 | 122.1194 | 122.0767 | 122.0718 | 122.1785 | 0.010212 | 122.0419 | 122.0764 | 122.1528 | 121.9806 | -122.2766
1652.9219 | 122.3099 | -122.1863 | 0.027466 | -0.013049 | -0.059147 | 0.065886 | -0.011725 | -0.0078693 | 0.0078051 | -0.027012 | -0.0017945 | -0.0018716 | -0.0056553 | 0.022767 | -0.011168 | 0.010204 | 0.010564 | -0.017566 | -0.057754 | -0.09122 | -0.10528 | 0.028521 | -0.021846 | -0.19195 | -121.9599 | -0.13068 | -0.091601 | -0.019721 | -122.2492 | 122.2148 | -0.08522 | 122.1965 | 122.1687 | -0.046087 | -0.11869 | -0.13275 | -0.062873 | -0.15815 | 122.1644 | 0.22636 | 0.28923 | -0.11907 | -0.047187 | 122.1285 | 122.0951 | 122.081 | 122.1968 | 0.001055 | 122.0556 | 122.0947 | 122.1666 | 121.9943 | -122.2766
1654.6094 | 122.4014 | -122.1359 | -0.013733 | 0.002213 | -0.059147 | 0.065672 | -0.012366 | -0.0080829 | 0.0080187 | -0.019381 | -0.0015809 | -0.0020852 | -0.0058689 | 0.022767 | -0.011168 | 0.014783 | 0.005985 | -0.012988 | -0.053175 | -0.09122 | -0.10528 | 0.0331 | -0.012689 | -0.17821 | -121.9599 | -0.13984 | -0.09618 | -0.019721 | -122.2583 | 122.169 | -0.039442 | 122.1507 | 122.1229 | -0.046088 | -0.077487 | -0.091546 | -0.12238 | -0.1261 | 122.1232 | 0.176 | 0.29839 | -0.082447 | -0.005988 | 122.0828 | 122.0447 | 122.0306 | 122.1419 | 0.046833 | 121.9961 | 122.0397 | 122.1162 | 121.9577 | -122.2446
1656.375 | 122.3923 | -122.1588 | 0.004578 | -0.005418 | -0.058933 | 0.065244 | -0.011938 | -0.0078693 | 0.0080187 | -0.011751 | -0.0015809 | -0.0018716 | -0.0056553 | 0.022553 | -0.011381 | 0.010204 | 0.001407 | -0.022144 | -0.053175 | -0.095798 | -0.10528 | 0.0331 | -0.012689 | -0.18737 | -121.9599 | -0.13984 | -0.087023 | -0.015142 | -122.2583 | 122.1919 | -0.057753 | 122.169 | 122.1367 | -0.055244 | -0.10038 | -0.10986 | -0.099496 | -0.14442 | 122.1461 | 0.19889 | 0.29839 | -0.091601 | -0.01972 | 122.1056 | 122.063 | 122.0535 | 122.1602 | 0.028522 | 122.019 | 122.0718 | 122.1437 | 121.9714 | -122.2629
1658.0625 | 122.3831 | -122.1451 | -0.009155 | -0.005418 | -0.058933 | 0.065458 | -0.012152 | -0.0080829 | 0.0080187 | -0.019381 | -0.0013673 | -0.001658 | -0.0058689 | 0.022767 | -0.011381 | 0.014783 | 0.005985 | -0.017566 | -0.057754 | -0.095798 | -0.11444 | 0.0331 | -0.017267 | -0.19653 | -121.9645 | -0.13984 | -0.09618 | -0.019721 | -122.2675 | 122.1782 | -0.048599 | 122.1599 | 122.1275 | -0.050666 | -0.086643 | -0.10528 | -0.12239 | -0.13068 | 122.1278 | 0.18058 | 0.30297 | -0.087025 | -0.010566 | 122.0873 | 122.0493 | 122.0306 | 122.1511 | 0.042255 | 122.0052 | 122.0489 | 122.1254 | 121.9486 | -122.2583
1659.7969 | 122.3877 | -122.1588 | 0 | -0.013049 | -0.059574 | 0.065458 | -0.011725 | -0.0080829 | 0.0078051 | -0.011751 | -0.0015809 | -0.0020852 | -0.0056553 | 0.022126 | -0.011168 | 0.010204 | 0.005985 | -0.022144 | -0.053175 | -0.09122 | -0.10986 | 0.028521 | -0.012689 | -0.19195 | -121.9691 | -0.14899 | -0.091601 | -0.015142 | -122.2675 | 122.1873 | -0.053175 | 122.169 | 122.1367 | -0.050665 | -0.09122 | -0.10986 | -0.10865 | -0.14899 | 122.1461 | 0.18973 | 0.29839 | -0.091601 | -0.015142 | 122.1056 | 122.0676 | 122.049 | 122.1648 | 0.028521 | 122.0098 | 122.0672 | 122.1437 | 121.9669 | -122.2675
1661.5469 | 122.3373 | -122.1863 | 0.009155 | -0.013049 | -0.058933 | 0.065458 | -0.012152 | -0.0078693 | 0.0078051 | -0.011751 | -0.0013673 | -0.0018716 | -0.0056553 | 0.022553 | -0.011168 | 0.014783 | 0.001407 | -0.017566 | -0.048597 | -0.086641 | -0.1007 | 0.028521 | -0.017267 | -0.18737 | -121.9691 | -0.13984 | -0.09618 | -0.019721 | -122.2675 | 122.2148 | -0.057752 | 122.2011 | 122.1687 | -0.046087 | -0.095796 | -0.10985 | -0.081188 | -0.14899 | 122.169 | 0.2172 | 0.29839 | -0.10533 | -0.028876 | 122.1377 | 122.0996 | 122.0856 | 122.1877 | 0.019366 | 122.0464 | 122.0901 | 122.1666 | 121.9989 | -122.2766
1663.2969 | 122.438 | -122.1405 | 0 | -0.013049 | -0.059147 | 0.065244 | -0.011511 | -0.0080829 | 0.0080187 | -0.019381 | -0.0017945 | -0.001658 | -0.0060825 | 0.022767 | -0.011168 | 0.014783 | 0.001407 | -0.012988 | -0.057754 | -0.086641 | -0.10528 | 0.0331 | -0.017267 | -0.19195 | -121.9737 | -0.13984 | -0.091601 | -0.019721 | -122.272 | 122.1736 | -0.057754 | 122.1553 | 122.1275 | -0.046088 | -0.086641 | -0.10528 | -0.13154 | -0.13984 | 122.1232 | 0.16684 | 0.29839 | -0.091601 | -0.019721 | 122.0827 | 122.0539 | 122.0352 | 122.1419 | 0.0331 | 122.0007 | 122.0489 | 122.1208 | 121.9486 | -122.272
1665.0469 | 122.319 | -122.2 | 0.022888 | 0.002213 | -0.059147 | 0.065244 | -0.011725 | -0.0078693 | 0.0080187 | -0.019381 | -0.0015809 | -0.0020852 | -0.0058689 | 0.022553 | -0.01074 | 0.014783 | 0.005985 | -0.017566 | -0.062332 | -0.086641 | -0.10528 | 0.028521 | -0.021846 | -0.18279 | -121.9737 | -0.13526 | -0.09618 | -0.015142 | -122.272 | 122.2285 | -0.08522 | 122.2148 | 122.1824 | -0.046087 | -0.10953 | -0.12817 | -0.072034 | -0.15815 | 122.1782 | 0.22635 | 0.29839 | -0.11907 | -0.03803 | 122.1377 | 122.1134 | 122.0947 | 122.206 | 0.005633 | 122.0648 | 122.1038 | 122.1849 | 122.0172 | -122.2949
1666.7344 | 122.374 | -122.1634 | 0.009155 | -0.005418 | -0.05872 | 0.065244 | -0.011725 | -0.0080829 | 0.0080187 | -0.011751 | -0.0015809 | -0.0020852 | -0.0060825 | 0.022553 | -0.010954 | 0.005626 | 0.010564 | -0.022144 | -0.057754 | -0.095798 | -0.10528 | 0.0331 | -0.017267 | -0.19653 | -121.9737 | -0.13984 | -0.09618 | -0.015142 | -122.2766 | 122.1965 | -0.066909 | 122.169 | 122.1412 | -0.055244 | -0.10495 | -0.11443 | -0.11323 | -0.14899 | 122.1461 | 0.18973 | 0.30297 | -0.10533 | -0.024297 | 122.1056 | 122.0676 | 122.0581 | 122.174 | 0.023945 | 122.0236 | 122.0672 | 122.1482 | 121.9669 | -122.2858
1668.4844 | 122.319 | -122.1909 | 0.032043 | -0.02068 | -0.05872 | 0.065672 | -0.012152 | -0.0078693 | 0.0078051 | -0.0041205 | -0.0015809 | -0.0018716 | -0.0056553 | 0.022339 | -0.010954 | 0.010204 | 0.005985 | -0.008409 | -0.057754 | -0.095798 | -0.10528 | 0.0331 | -0.017267 | -0.19653 | -121.9737 | -0.13984 | -0.091601 | -0.015142 | -122.2766 | 122.224 | -0.089797 | 122.2011 | 122.1824 | -0.041509 | -0.12784 | -0.13732 | -0.085768 | -0.17188 | 122.1736 | 0.2172 | 0.30297 | -0.12364 | -0.047185 | 122.1331 | 122.0951 | 122.0856 | 122.1968 | 0.001057 | 122.051 | 122.0993 | 122.1757 | 121.9943 | -122.3087
1670.2344 | 122.4518 | -122.1588 | -0.004578 | -0.005418 | -0.059361 | 0.065458 | -0.011725 | -0.0080829 | 0.0078051 | -0.011751 | -0.0015809 | -0.0020852 | -0.0056553 | 0.022339 | -0.01074 | 0.010204 | 0.005985 | -0.008409 | -0.053175 | -0.09122 | -0.10528 | 0.037679 | -0.012689 | -0.19195 | -121.9782 | -0.13526 | -0.091601 | -0.019721 | -122.2858 | 122.1965 | -0.048597 | 122.169 | 122.1504 | -0.046088 | -0.086642 | -0.1007 | -0.12697 | -0.13068 | 122.1461 | 0.18058 | 0.30755 | -0.087023 | -0.015143 | 122.1056 | 122.0676 | 122.0535 | 122.1648 | 0.042257 | 122.0236 | 122.0672 | 122.1391 | 121.9669 | -122.2812
1672 | 122.3419 | -122.2137 | 0.041199 | -0.013049 | -0.059574 | 0.065244 | -0.011938 | -0.0078693 | 0.0075915 | -0.019381 | -0.0015809 | -0.0020852 | -0.0058689 | 0.022553 | -0.010954 | 0.010204 | 0.005985 | -0.022144 | -0.053175 | -0.09122 | -0.096121 | 0.037679 | -0.017267 | -0.19653 | -121.9782 | -0.13068 | -0.09618 | -0.015142 | -122.2766 | 122.2514 | -0.094374 | 122.2239 | 122.1916 | -0.059823 | -0.13242 | -0.13732 | -0.06288 | -0.17188 | 122.1965 | 0.23551 | 0.29839 | -0.13738 | -0.056341 | 122.1606 | 122.1225 | 122.1176 | 122.2197 | -0.00352 | 122.0831 | 122.1176 | 122.1986 | 122.0172 | -122.3178
1673.7656 | 122.4564 | -122.1451 | -0.013733 | -0.013049 | -0.059361 | 0.065244 | -0.011938 | -0.0080829 | 0.0080187 | -0.019381 | -0.0015809 | -0.0018716 | -0.0052279 | 0.022767 | -0.010954 | 0.005626 | 0.001407 | -0.008409 | -0.057754 | -0.09122 | -0.10528 | 0.014784 | -0.021846 | -0.19195 | -121.9874 | -0.14442 | -0.09618 | -0.019721 | -122.272 | 122.1599 | -0.044021 | 122.1507 | 122.1367 | -0.023193 | -0.077487 | -0.091546 | -0.12696 | -0.13068 | 122.1232 | 0.15769 | 0.28465 | -0.082447 | -0.005988 | 122.0873 | 122.0539 | 122.0398 | 122.1465 | 0.028517 | 122.0007 | 122.0489 | 122.1254 | 121.9531 | -122.2583
1675.4531 | 122.4747 | -122.1451 | 0 | -0.005418 | -0.059361 | 0.065244 | -0.011938 | -0.0078693 | 0.0080187 | -0.011751 | -0.0020083 | -0.0020852 | -0.0054417 | 0.022767 | -0.011168 | 0.014783 | 0.005985 | -0.012988 | -0.053175 | -0.086641 | -0.10986 | 0.028521 | -0.026425 | -0.19653 | -121.9782 | -0.13526 | -0.09618 | -0.015142 | -122.2858 | 122.1736 | -0.053175 | 122.1599 | 122.1321 | -0.041509 | -0.086641 | -0.10986 | -0.1407 | -0.13526 | 122.1187 | 0.16684 | 0.30755 | -0.09618 | -0.015142 | 122.0919 | 122.0584 | 122.0352 | 122.1511 | 0.028521 | 122.0098 | 122.0489 | 122.1299 | 121.9486 | -122.2858
1677.2188 | 122.3785 | -122.2 | 0.027466 | 0.002213 | -0.059361 | 0.065031 | -0.011725 | -0.0078693 | 0.0078051 | -0.019381 | -0.0017945 | -0.0018716 | -0.0054417 | 0.022553 | -0.010954 | 0.023939 | 0.005985 | -0.017566 | -0.057754 | -0.086641 | -0.10528 | 0.0331 | -0.021846 | -0.19653 | -121.9874 | -0.13526 | -0.09618 | -0.028878 | -122.2858 | 122.2331 | -0.08522 | 122.224 | 122.1824 | -0.050666 | -0.11411 | -0.13275 | -0.08577 | -0.16273 | 122.1782 | 0.21262 | 0.29839 | -0.12365 | -0.056344 | 122.1423 | 122.1134 | 122.0947 | 122.206 | 0.005634 | 122.0648 | 122.1038 | 122.1711 | 122.0035 | -122.3132
1678.9688 | 122.4335 | -122.2046 | 0 | 0.002213 | -0.059574 | 0.065458 | -0.011938 | -0.0082965 | 0.0078051 | -0.019381 | -0.0013673 | -0.0014444 | -0.0058689 | 0.022767 | -0.011381 | 0.014783 | 0.001407 | -0.022144 | -0.053175 | -0.09122 | -0.10528 | 0.028521 | -0.021846 | -0.19653 | -121.992 | -0.13984 | -0.087023 | -0.015142 | -122.2904 | 122.2331 | -0.053175 | 122.2194 | 122.1824 | -0.050665 | -0.09122 | -0.10528 | -0.085771 | -0.13984 | 122.1827 | 0.21262 | 0.29839 | -0.087023 | -0.015142 | 122.1514 | 122.1134 | 122.0993 | 122.206 | 0.028521 | 122.0648 | 122.1176 | 122.1894 | 122.0081 | -122.2904
1680.6562 | 122.4747 | -122.1588 | -0.004578 | -0.02068 | -0.059361 | 0.065458 | -0.011725 | -0.0082965 | 0.0078051 | -0.019381 | -0.0020083 | -0.0018716 | -0.0060825 | 0.022981 | -0.011168 | 0.010204 | 0.001407 | -0.008409 | -0.057754 | -0.086641 | -0.10528 | 0.028521 | -0.026425 | -0.20568 | -121.992 | -0.13526 | -0.10076 | -0.015142 | -122.2949 | 122.1873 | -0.053176 | 122.169 | 122.1504 | -0.03693 | -0.082063 | -0.1007 | -0.13613 | -0.13068 | 122.1324 | 0.16684 | 0.30297 | -0.096181 | -0.010564 | 122.1011 | 122.0722 | 122.0535 | 122.1602 | 0.033099 | 122.0236 | 122.0581 | 122.1437 | 121.9531 | -122.2904
1682.4062 | 122.4197 | -122.1909 | 0.004578 | 0.009844 | -0.059574 | 0.065244 | -0.012152 | -0.0080829 | 0.0080187 | -0.027012 | -0.0015809 | -0.0020852 | -0.0056553 | 0.022553 | -0.011381 | 0.014783 | -0.003172 | -0.008409 | -0.048597 | -0.09122 | -0.10986 | 0.0331 | -0.026425 | -0.19653 | -121.9874 | -0.14442 | -0.091601 | -0.010564 | -122.2995 | 122.224 | -0.053175 | 122.2056 | 122.1824 | -0.041509 | -0.095798 | -0.11443 | -0.10866 | -0.14899 | 122.1644 | 0.20346 | 0.31212 | -0.096179 | -0.015142 | 122.1423 | 122.0996 | 122.081 | 122.1877 | 0.028522 | 122.0464 | 122.0993 | 122.1803 | 121.9943 | -122.3041
1684.1562 | 122.4609 | -122.168 | -0.018311 | -0.005418 | -0.059361 | 0.065672 | -0.011938 | -0.0080829 | 0.0078051 | -0.019381 | -0.0015809 | -0.0018716 | -0.0058689 | 0.022767 | -0.011168 | 0.014783 | 0.015142 | -0.008409 | -0.053175 | -0.095798 | -0.096121 | 0.028521 | -0.021846 | -0.19653 | -121.9874 | -0.13526 | -0.09618 | -0.010564 | -122.2995 | 122.1965 | -0.034864 | 122.1828 | 122.1596 | -0.03693 | -0.077487 | -0.07781 | -0.13155 | -0.11695 | 122.1461 | 0.18057 | 0.31212 | -0.077869 | 0.007747 | 122.1148 | 122.0722 | 122.0718 | 122.1831 | 0.046832 | 122.0327 | 122.0718 | 122.1574 | 121.9714 | -122.2812
1685.9219 | 122.3831 | -122.2 | 0.009155 | 0.002213 | -0.059361 | 0.065244 | -0.011938 | -0.0078693 | 0.0082325 | -0.027012 | -0.0015809 | -0.0018716 | -0.0058689 | 0.022767 | -0.011168 | 0.014783 | 0.005985 | -0.012988 | -0.062332 | -0.086641 | -0.10528 | 0.023942 | -0.021846 | -0.19653 | -122.0011 | -0.13526 | -0.087023 | -0.015142 | -122.3041 | 122.224 | -0.071487 | 122.2148 | 122.187 | -0.03693 | -0.095796 | -0.11443 | -0.10408 | -0.14441 | 122.1782 | 0.19888 | 0.30297 | -0.096178 | -0.024297 | 122.1377 | 122.1134 | 122.0947 | 122.206 | 0.014787 | 122.0648 | 122.113 | 122.1849 | 122.0035 | -122.3133
1687.6094 | 122.3282 | -122.2046 | 0.027466 | -0.005418 | -0.059361 | 0.065244 | -0.011725 | -0.0080829 | 0.0080187 | -0.019381 | -0.0017945 | -0.0020852 | -0.0058689 | 0.022767 | -0.011381 | 0.014783 | 0.015142 | -0.012988 | -0.053175 | -0.09122 | -0.091543 | 0.0331 | -0.021846 | -0.19195 | -122.0011 | -0.14442 | -0.087023 | -0.015142 | -122.3041 | 122.2377 | -0.080641 | 122.2194 | 122.1916 | -0.046088 | -0.11869 | -0.11901 | -0.099507 | -0.17188 | 122.1827 | 0.20346 | 0.30297 | -0.11449 | -0.042608 | 122.1514 | 122.1134 | 122.113 | 122.2197 | 0.005634 | 122.0602 | 122.1176 | 122.1894 | 122.0126 | -122.3316
1689.375 | 122.4609 | -122.1863 | -0.027466 | -0.005418 | -0.059361 | 0.065031 | -0.011938 | -0.0076555 | 0.0080187 | -0.011751 | -0.0017945 | -0.0018716 | -0.0056553 | 0.022553 | -0.011381 | 0.005626 | 0.005985 | -0.012988 | -0.057754 | -0.095798 | -0.10528 | 0.023942 | -0.021846 | -0.19653 | -121.9966 | -0.13984 | -0.082444 | -0.010564 | -122.2995 | 122.2102 | -0.030288 | 122.1919 | 122.1733 | -0.03693 | -0.068332 | -0.077813 | -0.11324 | -0.11237 | 122.1644 | 0.18973 | 0.30297 | -0.054978 | 0.016902 | 122.1285 | 122.0905 | 122.081 | 122.1923 | 0.051408 | 122.0464 | 122.1038 | 122.1757 | 121.9898 | -122.2721
1691.0781 | 122.493 | -122.168 | -0.013733 | 0.002213 | -0.059147 | 0.065031 | -0.011511 | -0.0080829 | 0.0080187 | -0.011751 | -0.0015809 | -0.001658 | -0.0056553 | 0.022981 | -0.011381 | 0.014783 | 0.001407 | -0.012988 | -0.053175 | -0.10038 | -0.096121 | 0.0331 | -0.026425 | -0.20568 | -122.0011 | -0.13984 | -0.087023 | -0.015142 | -122.3041 | 122.2011 | -0.039442 | 122.1828 | 122.155 | -0.046088 | -0.086644 | -0.082388 | -0.13613 | -0.1261 | 122.1415 | 0.16684 | 0.30297 | -0.07329 | -0.001409 | 122.1148 | 122.0676 | 122.0718 | 122.1694 | 0.046833 | 122.0281 | 122.0809 | 122.1528 | 121.9623 | -122.2904
1692.8281 | 122.3419 | -122.2183 | 0.018311 | -0.005418 | -0.058933 | 0.065244 | -0.012152 | -0.0080829 | 0.0080187 | -0.0041205 | -0.0015809 | -0.0020852 | -0.0058689 | 0.023194 | -0.010954 | 0.014783 | 0.001407 | -0.017566 | -0.053175 | -0.095798 | -0.10528 | 0.023942 | -0.017267 | -0.2011 | -122.0011 | -0.13984 | -0.091601 | -0.0243 | -122.3041 | 122.2423 | -0.071486 | 122.2331 | 122.2008 | -0.041508 | -0.11411 | -0.12359 | -0.085774 | -0.15815 | 122.2011 | 0.21719 | 0.30297 | -0.10991 | -0.042611 | 122.1651 | 122.1225 | 122.113 | 122.2197 | 0.005631 | 122.0785 | 122.1267 | 122.194 | 122.0172 | -122.3224
1694.5781 | 122.3419 | -122.2092 | 0.032043 | -0.02068 | -0.059361 | 0.065244 | -0.012152 | -0.0078693 | 0.0082325 | -0.019381 | -0.0015809 | -0.0018716 | -0.0058689 | 0.022553 | -0.011168 | 0.019361 | 0.005985 | -0.017566 | -0.057754 | -0.095798 | -0.1007 | 0.0331 | -0.031003 | -0.2011 | -122.0103 | -0.13526 | -0.082444 | -0.015142 | -122.3041 | 122.2423 | -0.089797 | 122.2285 | 122.1916 | -0.050666 | -0.12784 | -0.13274 | -0.09493 | -0.1673 | 122.1782 | 0.19888 | 0.29381 | -0.11449 | -0.047185 | 122.1514 | 122.1134 | 122.1085 | 122.2152 | 0.001057 | 122.0739 | 122.1267 | 122.194 | 122.0081 | -122.3361
1696.2656 | 122.4655 | -122.1725 | -0.022888 | 0.002213 | -0.059361 | 0.065458 | -0.011938 | -0.0082965 | 0.0080187 | -0.019381 | -0.0015809 | -0.002299 | -0.0058689 | 0.022981 | -0.011168 | 0.019361 | -0.003172 | -0.022144 | -0.053175 | -0.09122 | -0.10528 | 0.0331 | -0.017267 | -0.19653 | -122.0103 | -0.14442 | -0.087023 | -0.015142 | -122.3087 | 122.2056 | -0.030287 | 122.1919 | 122.1504 | -0.055244 | -0.068332 | -0.082391 | -0.13613 | -0.12153 | 122.1553 | 0.16226 | 0.29839 | -0.064135 | 0.007746 | 122.1194 | 122.0813 | 122.0673 | 122.1694 | 0.055988 | 122.0281 | 122.0855 | 122.1574 | 121.976 | -122.2858
1698 | 122.4335 | -122.1771 | 0.004578 | -0.005418 | -0.059361 | 0.065031 | -0.012152 | -0.0080829 | 0.0080187 | -0.019381 | -0.0013673 | -0.0014444 | -0.0056553 | 0.022981 | -0.011381 | 0.014783 | 0.001407 | -0.017566 | -0.062332 | -0.09122 | -0.1007 | 0.019363 | -0.031003 | -0.2011 | -122.0103 | -0.13526 | -0.082444 | -0.010564 | -122.3178 | 122.1965 | -0.06691 | 122.1919 | 122.1596 | -0.036929 | -0.095798 | -0.10528 | -0.14071 | -0.13984 | 122.1461 | 0.16684 | 0.30755 | -0.087022 | -0.015142 | 122.1148 | 122.0859 | 122.0764 | 122.1785 | 0.014785 | 122.0419 | 122.0947 | 122.1666 | 121.976 | -122.3224
1699.6875 | 122.3511 | -122.2321 | 0.027466 | -0.013049 | -0.059574 | 0.065244 | -0.011938 | -0.0082965 | 0.0080187 | -0.019381 | -0.0015809 | -0.0018716 | -0.0060825 | 0.023194 | -0.011381 | 0.014783 | 0.001407 | -0.017566 | -0.062332 | -0.09122 | -0.10528 | 0.028521 | -0.026425 | -0.2011 | -122.0149 | -0.13984 | -0.091601 | -0.015142 | -122.3133 | 122.2606 | -0.089798 | 122.2468 | 122.2145 | -0.046087 | -0.11869 | -0.13275 | -0.081199 | -0.1673 | 122.2056 | 0.21719 | 0.29839 | -0.11907 | -0.042608 | 122.1697 | 122.1408 | 122.1268 | 122.2335 | 0.001055 | 122.0922 | 122.1405 | 122.2169 | 122.031 | -122.3407
1701.4531 | 122.3877 | -122.2229 | 0.009155 | -0.005418 | -0.059361 | 0.065031 | -0.011938 | -0.0080829 | 0.0078051 | -0.011751 | -0.0011537 | -0.0018716 | -0.0058689 | 0.022767 | -0.011168 | 0.014783 | 0.001407 | -0.017566 | -0.057754 | -0.09122 | -0.10528 | 0.028521 | -0.026425 | -0.20568 | -122.0103 | -0.13984 | -0.091601 | -0.010564 | -122.3178 | 122.2514 | -0.066909 | 122.2377 | 122.2053 | -0.046087 | -0.10037 | -0.11443 | -0.094934 | -0.14899 | 122.1965 | 0.21261 | 0.30755 | -0.10076 | -0.019719 | 122.1651 | 122.1317 | 122.1176 | 122.2243 | 0.019366 | 122.0831 | 122.1313 | 122.2123 | 122.0172 | -122.327
1703.1406 | 122.4014 | -122.2137 | 0.022888 | 0.002213 | -0.059788 | 0.065458 | -0.011725 | -0.0080829 | 0.0075915 | -0.011751 | -0.0017945 | -0.0020852 | -0.0060825 | 0.022767 | -0.010954 | 0.010204 | 0.001407 | -0.012988 | -0.048597 | -0.09122 | -0.1007 | 0.0331 | -0.026425 | -0.19653 | -122.0149 | -0.13526 | -0.091601 | -0.010564 | -122.3133 | 122.2468 | -0.071485 | 122.2239 | 122.2008 | -0.046088 | -0.11411 | -0.12359 | -0.09951 | -0.15815 | 122.1873 | 0.19888 | 0.29839 | -0.11449 | -0.033452 | 122.1651 | 122.1225 | 122.113 | 122.2152 | 0.010212 | 122.0785 | 122.1221 | 122.2032 | 122.0172 | -122.3361
1704.8906 | 122.4701 | -122.2 | -0.009155 | -0.005418 | -0.059574 | 0.065031 | -0.011938 | -0.0085103 | 0.0078051 | -0.011751 | -0.0015809 | -0.0018716 | -0.0058689 | 0.022767 | -0.011381 | 0.005626 | 0.005985 | -0.012988 | -0.057754 | -0.09122 | -0.1007 | 0.028521 | -0.021846 | -0.2011 | -122.024 | -0.13984 | -0.09618 | -0.015142 | -122.3224 | 122.2285 | -0.048599 | 122.2056 | 122.187 | -0.041509 | -0.082065 | -0.091545 | -0.1224 | -0.13068 | 122.1782 | 0.17599 | 0.29839 | -0.087025 | -0.005987 | 122.1423 | 122.1088 | 122.0993 | 122.206 | 0.037676 | 122.0602 | 122.1038 | 122.1849 | 121.9989 | -122.3133
1706.6562 | 122.4701 | -122.1954 | -0.004578 | -0.005418 | -0.059788 | 0.065244 | -0.011938 | -0.0082965 | 0.0084461 | -0.011751 | -0.0015809 | -0.001658 | -0.0058689 | 0.022981 | -0.010954 | 0.019361 | 0.010564 | -0.012988 | -0.062332 | -0.095798 | -0.1007 | 0.028521 | -0.021846 | -0.2011 | -122.0194 | -0.13526 | -0.091601 | -0.019721 | -122.3224 | 122.224 | -0.057754 | 122.2148 | 122.1824 | -0.041509 | -0.09122 | -0.096122 | -0.12698 | -0.13068 | 122.1736 | 0.17599 | 0.30297 | -0.087023 | -0.015143 | 122.1331 | 122.0996 | 122.0947 | 122.206 | 0.033099 | 122.0602 | 122.1038 | 122.1757 | 121.9943 | -122.3178
1708.4062 | 122.4106 | -122.2229 | 0.018311 | -0.013049 | -0.059574 | 0.065458 | -0.011938 | -0.0082965 | 0.0080187 | -0.0041205 | -0.0015809 | -0.001658 | -0.0060825 | 0.022981 | -0.011168 | 0.019361 | 0.005985 | -0.017566 | -0.062332 | -0.09122 | -0.10528 | 0.028521 | -0.026425 | -0.20568 | -122.0194 | -0.13526 | -0.091601 | -0.015142 | -122.3133 | 122.2514 | -0.080643 | 122.2423 | 122.2053 | -0.046087 | -0.10953 | -0.12359 | -0.090355 | -0.15357 | 122.1965 | 0.20345 | 0.29381 | -0.10991 | -0.033453 | 122.1606 | 122.1317 | 122.1176 | 122.2289 | 0.01021 | 122.0876 | 122.1313 | 122.2078 | 122.0172 | -122.3316
1710.0938 | 122.3831 | -122.2275 | 0.032043 | -0.02068 | -0.059361 | 0.065031 | -0.011938 | -0.0080829 | 0.0080187 | -0.0041205 | -0.0015809 | -0.0018716 | -0.0056553 | 0.022767 | -0.011168 | 0.010204 | 0.005985 | -0.012988 | -0.057754 | -0.086641 | -0.10528 | 0.0331 | -0.021846 | -0.2011 | -122.024 | -0.13526 | -0.09618 | -0.019721 | -122.3316 | 122.2606 | -0.089797 | 122.2377 | 122.2145 | -0.046088 | -0.11868 | -0.13732 | -0.10409 | -0.1673 | 122.2056 | 0.20345 | 0.30755 | -0.12822 | -0.051764 | 122.1697 | 122.1408 | 122.1222 | 122.2335 | 0.001057 | 122.0922 | 122.1313 | 122.2078 | 122.0264 | -122.3636
1711.8438 | 122.3602 | -122.2412 | 0.018311 | -0.005418 | -0.059788 | 0.065031 | -0.012366 | -0.0082965 | 0.0078051 | -0.011751 | -0.0017945 | -0.0018716 | -0.0060825 | 0.023408 | -0.011168 | 0.014783 | 0.010564 | -0.017566 | -0.062332 | -0.09122 | -0.10528 | 0.028521 | -0.031003 | -0.2011 | -122.0286 | -0.13984 | -0.091601 | -0.019721 | -122.3316 | 122.2697 | -0.080643 | 122.256 | 122.2236 | -0.046087 | -0.10953 | -0.12359 | -0.090359 | -0.15815 | 122.2102 | 0.21261 | 0.30297 | -0.10991 | -0.038032 | 122.1789 | 122.15 | 122.1359 | 122.2518 | 0.01021 | 122.1014 | 122.1496 | 122.2215 | 122.0401 | -122.3499
1713.5938 | 122.4838 | -122.2 | -0.022888 | -0.005418 | -0.059574 | 0.065031 | -0.012152 | -0.0082965 | 0.0078051 | -0.019381 | -0.0015809 | -0.0020852 | -0.0060825 | 0.022981 | -0.011168 | 0.014783 | 0.010564 | -0.008409 | -0.062332 | -0.09122 | -0.10986 | 0.028521 | -0.026425 | -0.21026 | -122.0194 | -0.13526 | -0.091601 | -0.019721 | -122.3316 | 122.2285 | -0.039444 | 122.2148 | 122.1916 | -0.03693 | -0.068332 | -0.086969 | -0.13156 | -0.11237 | 122.1736 | 0.18057 | 0.31212 | -0.068713 | 0.003167 | 122.1377 | 122.1088 | 122.0902 | 122.2106 | 0.051409 | 122.0648 | 122.1084 | 122.1803 | 121.9898 | -122.3087
1715.3594 | 122.3877 | -122.2412 | 0.041199 | -0.005418 | -0.059574 | 0.064817 | -0.012152 | -0.0078693 | 0.0078051 | -0.011751 | -0.0015809 | -0.0018716 | -0.0060825 | 0.022767 | -0.011381 | 0.010204 | 0.001407 | -0.017566 | -0.053175 | -0.086641 | -0.1007 | 0.0331 | -0.026425 | -0.2011 | -122.0286 | -0.13526 | -0.091601 | -0.015142 | -122.3316 | 122.2743 | -0.094374 | 122.2514 | 122.2236 | -0.050666 | -0.12784 | -0.1419 | -0.090359 | -0.17646 | 122.2148 | 0.21261 | 0.30297 | -0.1328 | -0.056341 | 122.188 | 122.1546 | 122.1405 | 122.2426 | -0.008099 | 122.106 | 122.1496 | 122.2261 | 122.0401 | -122.3728
1717.125 | 122.4838 | -122.2229 | 0 | -0.005418 | -0.059574 | 0.065031 | -0.012152 | -0.0078693 | 0.0075915 | -0.019381 | -0.0015809 | -0.0020852 | -0.0060825 | 0.022553 | -0.011595 | 0.005626 | 0.005985 | -0.022144 | -0.057754 | -0.09122 | -0.1007 | 0.023942 | -0.026425 | -0.20568 | -122.0378 | -0.13984 | -0.091601 | -0.015142 | -122.327 | 122.2468 | -0.057754 | 122.2285 | 122.2008 | -0.046086 | -0.09122 | -0.1007 | -0.10409 | -0.13984 | 122.1965 | 0.18514 | 0.28923 | -0.091601 | -0.015142 | 122.1651 | 122.1317 | 122.1222 | 122.2289 | 0.023942 | 122.0831 | 122.1313 | 122.2078 | 122.0172 | -122.327
1718.875 | 122.4152 | -122.2458 | 0.018311 | -0.005418 | -0.059361 | 0.065031 | -0.011938 | -0.0078693 | 0.0078051 | -0.0041205 | -0.0017945 | -0.0018716 | -0.0056553 | 0.022981 | -0.011168 | 0.014783 | 0.005985 | -0.012988 | -0.057754 | -0.09122 | -0.1007 | 0.028521 | -0.026425 | -0.2011 | -122.0332 | -0.13984 | -0.10076 | -0.010564 | -122.3316 | 122.2743 | -0.076065 | 122.2606 | 122.2328 | -0.041509 | -0.10953 | -0.11901 | -0.085781 | -0.15815 | 122.2194 | 0.21261 | 0.29839 | -0.11907 | -0.028875 | 122.188 | 122.1546 | 122.1451 | 122.2518 | 0.01021 | 122.106 | 122.145 | 122.2352 | 122.0447 | -122.3499
1720.5781 | 122.3785 | -122.2366 | 0.022888 | -0.005418 | -0.059574 | 0.065031 | -0.011938 | -0.0082965 | 0.0073777 | -0.011751 | -0.0017945 | -0.002299 | -0.0058689 | 0.022767 | -0.011168 | 0.014783 | 0.010564 | -0.017566 | -0.057754 | -0.10038 | -0.096121 | 0.028521 | -0.026425 | -0.20568 | -122.0378 | -0.13984 | -0.09618 | -0.019721 | -122.3361 | 122.2652 | -0.080642 | 122.2514 | 122.2191 | -0.046087 | -0.12326 | -0.11901 | -0.099516 | -0.16273 | 122.2102 | 0.19887 | 0.29839 | -0.11907 | -0.042609 | 122.1789 | 122.1363 | 122.1405 | 122.2472 | 0.005633 | 122.0968 | 122.1405 | 122.2169 | 122.031 | -122.359
1722.3281 | 122.4106 | -122.2275 | 0.009155 | -0.005418 | -0.059574 | 0.064817 | -0.012366 | -0.0080829 | 0.0075915 | -0.011751 | -0.0015809 | -0.0018716 | -0.0062963 | 0.022981 | -0.011381 | 0.005626 | 0.005985 | -0.012988 | -0.057754 | -0.095798 | -0.10528 | 0.023942 | -0.021846 | -0.21484 | -122.0286 | -0.13984 | -0.091601 | -0.015142 | -122.3361 | 122.2514 | -0.066909 | 122.2331 | 122.2145 | -0.03693 | -0.10495 | -0.11443 | -0.10867 | -0.14899 | 122.2056 | 0.19888 | 0.30755 | -0.10076 | -0.024297 | 122.1697 | 122.1317 | 122.1222 | 122.2335 | 0.014787 | 122.0876 | 122.1359 | 122.2123 | 122.0126 | -122.3453
1724.0781 | 122.4792 | -122.2275 | 0 | -0.02068 | -0.059788 | 0.064817 | -0.011725 | -0.0080829 | 0.0080187 | -0.027012 | -0.0015809 | -0.0018716 | -0.0054417 | 0.022981 | -0.011168 | 0.014783 | -0.003172 | -0.012988 | -0.057754 | -0.09122 | -0.10528 | 0.028521 | -0.021846 | -0.20568 | -122.0332 | -0.13526 | -0.091601 | -0.010564 | -122.3407 | 122.256 | -0.057754 | 122.2423 | 122.2145 | -0.041509 | -0.09122 | -0.10528 | -0.11325 | -0.13526 | 122.2056 | 0.1943 | 0.30755 | -0.091601 | -0.010564 | 122.1697 | 122.1363 | 122.1222 | 122.2243 | 0.028521 | 122.0922 | 122.1359 | 122.2169 | 122.0218 | -122.3407
1725.7656 | 122.3877 | -122.2458 | 0.032043 | -0.005418 | -0.059788 | 0.064817 | -0.011938 | -0.0082965 | 0.0075915 | -0.019381 | -0.0017945 | -0.0020852 | -0.0058689 | 0.022981 | -0.011168 | 0.010204 | 0.005985 | -0.022144 | -0.053175 | -0.09122 | -0.091543 | 0.023942 | -0.026425 | -0.21026 | -122.0378 | -0.14442 | -0.09618 | -0.015142 | -122.3453 | 122.2697 | -0.085218 | 122.256 | 122.2236 | -0.046086 | -0.12326 | -0.12359 | -0.099518 | -0.17646 | 122.2194 | 0.20803 | 0.30755 | -0.12822 | -0.047185 | 122.1926 | 122.1546 | 122.1542 | 122.2518 | -0.008101 | 122.1014 | 122.1496 | 122.2306 | 122.0355 | -122.3774
1727.5469 | 122.5159 | -122.2137 | 0.004578 | -0.005418 | -0.059574 | 0.064603 | -0.012152 | -0.0082965 | 0.0080187 | -0.011751 | -0.0015809 | -0.0018716 | -0.0058689 | 0.023408 | -0.011381 | 0.005626 | 0.001407 | -0.022144 | -0.057754 | -0.09122 | -0.10528 | 0.023942 | -0.035582 | -0.20568 | -122.0469 | -0.13526 | -0.087023 | -0.019721 | -122.3453 | 122.2377 | -0.062332 | 122.2194 | 122.1916 | -0.046086 | -0.095798 | -0.10986 | -0.13156 | -0.13984 | 122.1782 | 0.16683 | 0.29839 | -0.091601 | -0.024299 | 122.156 | 122.1225 | 122.1085 | 122.2152 | 0.019364 | 122.0785 | 122.1267 | 122.194 | 122.0081 | -122.3499
1729.3125 | 122.4838 | -122.2275 | -0.004578 | 0.002213 | -0.059361 | 0.064603 | -0.012152 | -0.0080829 | 0.0075915 | -0.019381 | -0.0017945 | -0.0020852 | -0.0060825 | 0.022981 | -0.011168 | 0.005626 | 0.005985 | -0.017566 | -0.053175 | -0.082062 | -0.10528 | 0.0331 | -0.026425 | -0.21484 | -122.0332 | -0.13526 | -0.09618 | -0.015142 | -122.3499 | 122.2606 | -0.048597 | 122.2331 | 122.2099 | -0.050666 | -0.077484 | -0.1007 | -0.12241 | -0.13068 | 122.2011 | 0.1943 | 0.3167 | -0.091602 | -0.010564 | 122.1743 | 122.1454 | 122.1222 | 122.2335 | 0.037678 | 122.0922 | 122.1313 | 122.2123 | 122.0126 | -122.3453
1731.0156 | 122.4792 | -122.2183 | -0.013733 | 0.002213 | -0.059788 | 0.065031 | -0.011511 | -0.0080829 | 0.0080187 | -0.0041205 | -0.0013673 | -0.0018716 | -0.0060825 | 0.022981 | -0.011168 | 0.005626 | 0.015142 | -0.022144 | -0.057754 | -0.09122 | -0.1007 | 0.028521 | -0.021846 | -0.21026 | -122.0515 | -0.13984 | -0.09618 | -0.019721 | -122.3453 | 122.2468 | -0.044021 | 122.2239 | 122.1962 | -0.050665 | -0.077487 | -0.086967 | -0.12698 | -0.1261 | 122.1965 | 0.16683 | 0.29381 | -0.082447 | -0.005988 | 122.1606 | 122.1271 | 122.1176 | 122.2335 | 0.042254 | 122.0785 | 122.1221 | 122.1986 | 122.0081 | -122.3316
1732.7031 | 122.4838 | -122.2458 | 0.009155 | -0.013049 | -0.059788 | 0.064603 | -0.011725 | -0.0080829 | 0.0075915 | -0.0041205 | -0.0015809 | -0.0020852 | -0.0058689 | 0.022981 | -0.010954 | 0.005626 | 0.001407 | -0.017566 | -0.062332 | -0.086641 | -0.096121 | 0.028521 | -0.031003 | -0.21026 | -122.0378 | -0.13526 | -0.091601 | -0.010564 | -122.3453 | 122.2743 | -0.071487 | 122.2514 | 122.2282 | -0.046087 | -0.095796 | -0.10528 | -0.099518 | -0.14441 | 122.2148 | 0.20803 | 0.30755 | -0.10076 | -0.019719 | 122.1835 | 122.1591 | 122.1497 | 122.2472 | 0.019366 | 122.1105 | 122.1542 | 122.2352 | 122.0355 | -122.3545
1734.4688 | 122.4106 | -122.2595 | 0.032043 | -0.02068 | -0.059788 | 0.065031 | -0.012152 | -0.0082965 | 0.0075915 | -0.011751 | -0.0013673 | -0.001658 | -0.0056553 | 0.022981 | -0.011595 | 0.010204 | 0.001407 | -0.017566 | -0.053175 | -0.09122 | -0.1007 | 0.028521 | -0.031003 | -0.20568 | -122.0469 | -0.13984 | -0.09618 | -0.015142 | -122.3499 | 122.288 | -0.085218 | 122.2697 | 122.242 | -0.046087 | -0.12326 | -0.13274 | -0.090365 | -0.17188 | 122.2285 | 0.2126 | 0.30297 | -0.12822 | -0.047185 | 122.2063 | 122.1683 | 122.1588 | 122.2609 | -0.003522 | 122.1197 | 122.1633 | 122.2444 | 122.0538 | -122.3819
1736.1562 | 122.4106 | -122.2687 | 0.027466 | -0.013049 | -0.060002 | 0.064817 | -0.012152 | -0.0080829 | 0.0080187 | -0.011751 | -0.0015809 | -0.0018716 | -0.0058689 | 0.023194 | -0.011381 | 0.010204 | 0.005985 | -0.012988 | -0.053175 | -0.086641 | -0.1007 | 0.023942 | -0.026425 | -0.20568 | -122.0561 | -0.14442 | -0.091601 | -0.015142 | -122.3499 | 122.2926 | -0.080641 | 122.2789 | 122.2557 | -0.03693 | -0.11411 | -0.12817 | -0.081209 | -0.17188 | 122.2423 | 0.2126 | 0.29381 | -0.11907 | -0.042608 | 122.2155 | 122.182 | 122.168 | 122.2747 | -0.003524 | 122.1243 | 122.1771 | 122.2535 | 122.063 | -122.3774
1737.9375 | 122.4838 | -122.2 | -0.009155 | -0.013049 | -0.059361 | 0.064817 | -0.012152 | -0.0082965 | 0.0078051 | -0.0041205 | -0.0011537 | -0.0018716 | -0.0058689 | 0.022981 | -0.011381 | 0.005626 | 0.005985 | -0.012988 | -0.057754 | -0.086641 | -0.1007 | 0.023942 | -0.026425 | -0.21484 | -122.0515 | -0.13984 | -0.09618 | -0.010564 | -122.3545 | 122.224 | -0.048599 | 122.2056 | 122.187 | -0.03693 | -0.077486 | -0.091545 | -0.15445 | -0.13068 | 122.1736 | 0.14852 | 0.30297 | -0.087025 | -0.001409 | 122.1423 | 122.1134 | 122.0993 | 122.206 | 0.033097 | 122.0602 | 122.1038 | 122.1894 | 121.9852 | -122.3453
1739.6875 | 122.3923 | -122.2961 | 0.036621 | -0.005418 | -0.059574 | 0.064817 | -0.012152 | -0.0082965 | 0.0078051 | -0.019381 | -0.0015809 | -0.0018716 | -0.0058689 | 0.022981 | -0.011381 | 0.010204 | 0.010564 | -0.012988 | -0.062332 | -0.086641 | -0.10986 | 0.023942 | -0.021846 | -0.21026 | -122.0561 | -0.13526 | -0.087023 | -0.010564 | -122.3499 | 122.3201 | -0.098953 | 122.3063 | 122.2832 | -0.03693 | -0.12326 | -0.14648 | -0.053743 | -0.17188 | 122.2743 | 0.24007 | 0.29381 | -0.12364 | -0.047185 | 122.2338 | 122.2095 | 122.1863 | 122.3067 | -0.012679 | 122.1609 | 122.2091 | 122.2856 | 122.0859 | -122.3865
1741.3906 | 122.525 | -122.2137 | -0.027466 | -0.005418 | -0.060002 | 0.064603 | -0.012152 | -0.0085103 | 0.0075915 | -0.011751 | -0.0017945 | -0.0020852 | -0.0058689 | 0.023194 | -0.011381 | 0.010204 | 0.005985 | -0.017566 | -0.057754 | -0.09122 | -0.096121 | 0.0331 | -0.026425 | -0.20568 | -122.0515 | -0.13526 | -0.09618 | -0.015142 | -122.3682 | 122.2468 | -0.030288 | 122.2239 | 122.1962 | -0.050666 | -0.063754 | -0.068655 | -0.15446 | -0.10779 | 122.1873 | 0.16225 | 0.3167 | -0.068714 | 0.012324 | 122.156 | 122.1225 | 122.1176 | 122.2197 | 0.060566 | 122.0785 | 122.1176 | 122.1986 | 122.0081 | -122.3407
1743.1719 | 122.374 | -122.2733 | 0.013733 | -0.013049 | -0.060002 | 0.064817 | -0.011938 | -0.0082965 | 0.0073777 | 0.00351 | -0.0017945 | -0.0020852 | -0.0060825 | 0.022981 | -0.011381 | 0.014783 | 0.001407 | -0.017566 | -0.053175 | -0.09122 | -0.10528 | 0.028521 | -0.026425 | -0.20568 | -122.0561 | -0.13526 | -0.091601 | -0.015142 | -122.359 | 122.3018 | -0.066908 | 122.288 | 122.2557 | -0.046087 | -0.10495 | -0.11901 | -0.085789 | -0.14899 | 122.2468 | 0.21718 | 0.30297 | -0.10533 | -0.028875 | 122.2201 | 122.182 | 122.168 | 122.2747 | 0.014788 | 122.138 | 122.1817 | 122.2581 | 122.0676 | -122.3728
1744.875 | 122.4289 | -122.3145 | -0.013733 | -0.02068 | -0.060002 | 0.064817 | -0.012152 | -0.0082965 | 0.0080187 | -0.011751 | -0.0017945 | -0.0014444 | -0.0058689 | 0.023408 | -0.011381 | 0.010204 | 0.005985 | -0.008409 | -0.057754 | -0.09122 | -0.1007 | 0.028521 | -0.026425 | -0.2011 | -122.0423 | -0.13984 | -0.091601 | -0.010564 | -122.359 | 122.343 | -0.044021 | 122.3247 | 122.306 | -0.03693 | -0.077487 | -0.086967 | -0.04459 | -0.1261 | 122.288 | 0.27211 | 0.3167 | -0.077868 | 0.003169 | 122.2567 | 122.2232 | 122.2138 | 122.3204 | 0.042254 | 122.1746 | 122.2229 | 122.3039 | 122.1133 | -122.3453
1746.625 | 122.3877 | -122.3373 | 0.018311 | 0.002213 | -0.060002 | 0.065031 | -0.011938 | -0.0082965 | 0.0078051 | -0.0041205 | -0.0015809 | -0.0014444 | -0.0060825 | 0.023194 | -0.011168 | 0.010204 | 0.001407 | -0.026723 | -0.048597 | -0.09122 | -0.1007 | 0.0331 | -0.026425 | -0.21026 | -122.0561 | -0.13984 | -0.091601 | -0.010564 | -122.359 | 122.3704 | -0.066908 | 122.3475 | 122.3106 | -0.059823 | -0.10953 | -0.11901 | -0.021702 | -0.15815 | 122.3109 | 0.28127 | 0.30297 | -0.10991 | -0.028875 | 122.2887 | 122.2461 | 122.2366 | 122.3387 | 0.014789 | 122.1975 | 122.2457 | 122.3268 | 122.1271 | -122.3774
1748.375 | 122.3923 | -122.2778 | 0.027466 | 0.002213 | -0.059788 | 0.065031 | -0.012152 | -0.0082965 | 0.0078051 | -0.011751 | -0.0015809 | -0.0018716 | -0.0060825 | 0.022981 | -0.011168 | 0.010204 | -0.003172 | -0.026723 | -0.053175 | -0.09122 | -0.10986 | 0.028521 | -0.026425 | -0.21484 | -122.0607 | -0.13984 | -0.091601 | -0.005985 | -122.3545 | 122.3064 | -0.080641 | 122.288 | 122.2511 | -0.055244 | -0.11869 | -0.13732 | -0.076632 | -0.1673 | 122.2514 | 0.21718 | 0.29381 | -0.11907 | -0.033451 | 122.2247 | 122.1866 | 122.168 | 122.2747 | 0.001055 | 122.138 | 122.1862 | 122.2718 | 122.063 | -122.3819
1750.0625 | 122.5388 | -122.2275 | 0.009155 | -0.013049 | -0.060215 | 0.065031 | -0.011938 | -0.0080829 | 0.0075915 | -0.011751 | -0.0013673 | -0.001658 | -0.0056553 | 0.022981 | -0.011595 | 0.014783 | 0.005985 | -0.026723 | -0.057754 | -0.086641 | -0.1007 | 0.023942 | -0.026425 | -0.21026 | -122.0607 | -0.13526 | -0.087023 | -0.015142 | -122.3636 | 122.2514 | -0.066909 | 122.2423 | 122.2008 | -0.050665 | -0.095796 | -0.10985 | -0.13614 | -0.14441 | 122.2011 | 0.16682 | 0.30297 | -0.096178 | -0.024297 | 122.1697 | 122.1408 | 122.1268 | 122.2335 | 0.014787 | 122.0922 | 122.1405 | 122.2123 | 122.0172 | -122.3728
1751.8125 | 122.5204 | -122.2366 | -0.009155 | 0.002213 | -0.059788 | 0.065031 | -0.011938 | -0.0082965 | 0.0075915 | -0.019381 | -0.0015809 | -0.0020852 | -0.0062963 | 0.022981 | -0.011809 | 0.014783 | 0.005985 | -0.026723 | -0.057754 | -0.082062 | -0.096121 | 0.028521 | -0.026425 | -0.20568 | -122.0607 | -0.13984 | -0.087023 | -0.010564 | -122.3636 | 122.2652 | -0.048599 | 122.2514 | 122.2099 | -0.055244 | -0.072907 | -0.086966 | -0.12699 | -0.13068 | 122.2102 | 0.17598 | 0.30297 | -0.077868 | -0.001409 | 122.1789 | 122.1546 | 122.1405 | 122.2426 | 0.037676 | 122.0968 | 122.1496 | 122.2261 | 122.031 | -122.3545
1753.5625 | 122.3923 | -122.2549 | 0.022888 | -0.013049 | -0.060215 | 0.065031 | -0.012366 | -0.0082965 | 0.0073777 | -0.011751 | -0.0015809 | -0.0018716 | -0.0056553 | 0.023194 | -0.011595 | 0.014783 | 0.015142 | -0.012988 | -0.053175 | -0.077483 | -0.1007 | 0.023942 | -0.031003 | -0.21026 | -122.0652 | -0.13526 | -0.087023 | -0.015142 | -122.3636 | 122.2789 | -0.076063 | 122.2697 | 122.242 | -0.03693 | -0.10037 | -0.12359 | -0.10868 | -0.15815 | 122.2239 | 0.18971 | 0.29839 | -0.10991 | -0.03803 | 122.2018 | 122.1775 | 122.1542 | 122.2701 | 0.001054 | 122.1197 | 122.1679 | 122.2398 | 122.0447 | -122.3865
1755.25 | 122.4014 | -122.2733 | 0.018311 | 0.002213 | -0.060215 | 0.064817 | -0.012152 | -0.0080829 | 0.0075915 | -0.019381 | -0.0013673 | -0.001658 | -0.0058689 | 0.023408 | -0.011595 | 0.019361 | 0.001407 | -0.022144 | -0.057754 | -0.09122 | -0.1007 | 0.028521 | -0.026425 | -0.21026 | -122.0698 | -0.13984 | -0.091601 | -0.010564 | -122.3728 | 122.3018 | -0.076065 | 122.2926 | 122.2511 | -0.050665 | -0.10953 | -0.11901 | -0.099526 | -0.15815 | 122.2468 | 0.20344 | 0.30297 | -0.10991 | -0.028875 | 122.2155 | 122.182 | 122.1726 | 122.2747 | 0.01021 | 122.1334 | 122.1817 | 122.2627 | 122.063 | -122.3911
1757.0156 | 122.5021 | -122.2458 | -0.018311 | -0.013049 | -0.060002 | 0.065031 | -0.012152 | -0.0082965 | 0.0075915 | -0.011751 | -0.0013673 | -0.002299 | -0.0058689 | 0.023194 | -0.011381 | 0.010204 | 0.005985 | -0.022144 | -0.053175 | -0.086641 | -0.086964 | 0.023942 | -0.026425 | -0.21026 | -122.0698 | -0.13984 | -0.087023 | -0.010564 | -122.3774 | 122.2697 | -0.034864 | 122.256 | 122.2236 | -0.046086 | -0.06833 | -0.068653 | -0.13157 | -0.12153 | 122.2194 | 0.17598 | 0.30755 | -0.068712 | 0.007747 | 122.1926 | 122.1591 | 122.1588 | 122.2518 | 0.042253 | 122.106 | 122.1588 | 122.2352 | 122.0355 | -122.359
1758.7188 | 122.4243 | -122.2641 | 0.022888 | 0.002213 | -0.060429 | 0.064817 | -0.012152 | -0.0082965 | 0.0073777 | -0.0041205 | -0.0015809 | -0.0018716 | -0.0058689 | 0.023194 | -0.011381 | 0.010204 | 0.005985 | -0.017566 | -0.044018 | -0.09122 | -0.1007 | 0.023942 | -0.021846 | -0.21026 | -122.0652 | -0.13526 | -0.091601 | -0.015142 | -122.3774 | 122.288 | -0.066906 | 122.2743 | 122.2465 | -0.041508 | -0.11411 | -0.12359 | -0.11326 | -0.15815 | 122.2423 | 0.19887 | 0.31213 | -0.11449 | -0.03803 | 122.2201 | 122.1729 | 122.1634 | 122.2701 | 0.001054 | 122.1288 | 122.1725 | 122.249 | 122.0538 | -122.4002
1760.5156 | 122.4564 | -122.2504 | 0.018311 | -0.005418 | -0.060002 | 0.064603 | -0.012152 | -0.0085103 | 0.0073777 | -0.019381 | -0.0013673 | -0.0018716 | -0.0058689 | 0.023194 | -0.011595 | 0.010204 | 0.010564 | -0.017566 | -0.057754 | -0.086641 | -0.091543 | 0.028521 | -0.031003 | -0.21942 | -122.0652 | -0.13984 | -0.082444 | -0.010564 | -122.3819 | 122.2789 | -0.076065 | 122.2606 | 122.2328 | -0.046087 | -0.10495 | -0.10985 | -0.13157 | -0.15815 | 122.2194 | 0.18513 | 0.3167 | -0.10076 | -0.028875 | 122.1926 | 122.1637 | 122.1588 | 122.2609 | 0.01021 | 122.1105 | 122.1679 | 122.2398 | 122.0309 | -122.4002
1762.2031 | 122.5433 | -122.2137 | -0.027466 | -0.005418 | -0.060002 | 0.06439 | -0.011938 | -0.0082965 | 0.0078051 | -0.019381 | -0.0015809 | -0.001658 | -0.0060825 | 0.023622 | -0.011381 | 0.005626 | 0.001407 | -0.022144 | -0.048597 | -0.10038 | -0.096121 | 0.028521 | -0.026425 | -0.21942 | -122.0698 | -0.13984 | -0.09618 | -0.015142 | -122.3819 | 122.2423 | -0.021131 | 122.2194 | 122.1916 | -0.050665 | -0.072911 | -0.068655 | -0.16819 | -0.11237 | 122.1873 | 0.14393 | 0.31213 | -0.068714 | 0.012324 | 122.1651 | 122.1134 | 122.1176 | 122.2152 | 0.055987 | 122.0739 | 122.1176 | 122.1986 | 121.9943 | -122.3545
1763.9375 | 122.5067 | -122.2549 | 0.022888 | -0.005418 | -0.060643 | 0.064817 | -0.012152 | -0.0082965 | 0.0075915 | -0.027012 | -0.0015809 | -0.0020852 | -0.0062963 | 0.023622 | -0.011595 | 0.010204 | 0.010564 | -0.022144 | -0.053175 | -0.086641 | -0.096121 | 0.023942 | -0.031003 | -0.21484 | -122.0881 | -0.13984 | -0.091601 | -0.015142 | -122.3774 | 122.2789 | -0.076063 | 122.2651 | 122.2328 | -0.046086 | -0.10953 | -0.11901 | -0.12242 | -0.16273 | 122.2239 | 0.16682 | 0.28923 | -0.11449 | -0.03803 | 122.2018 | 122.1683 | 122.1588 | 122.2655 | 0.001054 | 122.1151 | 122.1633 | 122.2398 | 122.0401 | -122.4002
1765.625 | 122.525 | -122.2504 | 0 | -0.005418 | -0.060643 | 0.064817 | -0.012366 | -0.0082965 | 0.0075915 | -0.011751 | -0.0011537 | -0.0018716 | -0.0058689 | 0.023194 | -0.011809 | 0.005626 | 0.005985 | -0.022144 | -0.053175 | -0.086641 | -0.091543 | 0.028521 | -0.026425 | -0.21484 | -122.0744 | -0.13984 | -0.087023 | -0.015142 | -122.3728 | 122.2789 | -0.053175 | 122.256 | 122.2282 | -0.050665 | -0.086641 | -0.091543 | -0.12241 | -0.13984 | 122.2239 | 0.17598 | 0.29839 | -0.087023 | -0.015142 | 122.1972 | 122.1637 | 122.1588 | 122.2564 | 0.028521 | 122.1105 | 122.1633 | 122.2352 | 122.0355 | -122.3728
1767.3125 | 122.4655 | -122.2733 | 0.032043 | -0.013049 | -0.060215 | 0.064817 | -0.012152 | -0.0080829 | 0.0075915 | -0.011751 | -0.0015809 | -0.0020852 | -0.0060825 | 0.023408 | -0.011595 | 0.010204 | 0.005985 | -0.026723 | -0.057754 | -0.09122 | -0.1007 | 0.0331 | -0.026425 | -0.21942 | -122.0652 | -0.14442 | -0.091601 | -0.010564 | -122.3774 | 122.3064 | -0.089797 | 122.2835 | 122.2465 | -0.059823 | -0.12326 | -0.13274 | -0.10411 | -0.17646 | 122.2468 | 0.20802 | 0.31213 | -0.12364 | -0.042607 | 122.2155 | 122.182 | 122.1726 | 122.2792 | 0.001057 | 122.1288 | 122.1817 | 122.2627 | 122.0538 | -122.4094
1769 | 122.5571 | -122.2275 | 0.004578 | -0.005418 | -0.060002 | 0.064817 | -0.011938 | -0.0085103 | 0.0073777 | -0.0041205 | -0.0017945 | -0.001658 | -0.0060825 | 0.023194 | -0.011809 | 0.010204 | -0.003172 | -0.031301 | -0.057754 | -0.086641 | -0.091543 | 0.0331 | -0.026425 | -0.21942 | -122.0835 | -0.13984 | -0.087023 | -0.015142 | -122.3911 | 122.2606 | -0.062332 | 122.2377 | 122.1962 | -0.064401 | -0.091219 | -0.096121 | -0.16362 | -0.14442 | 122.2011 | 0.14393 | 0.30755 | -0.091601 | -0.01972 | 122.1697 | 122.1408 | 122.1359 | 122.2243 | 0.028522 | 122.0876 | 122.1405 | 122.2123 | 122.0081 | -122.3957
1770.6875 | 122.5388 | -122.2458 | -0.004578 | -0.013049 | -0.060215 | 0.064817 | -0.012366 | -0.0082965 | 0.0073777 | -0.019381 | -0.0015809 | -0.001658 | -0.0060825 | 0.023194 | -0.011595 | 0.005626 | -0.003172 | -0.012988 | -0.057754 | -0.086641 | -0.096121 | 0.0331 | -0.035582 | -0.22858 | -122.0881 | -0.13984 | -0.087023 | -0.010564 | -122.3865 | 122.2789 | -0.053176 | 122.2514 | 122.2328 | -0.046088 | -0.082063 | -0.091543 | -0.14073 | -0.13526 | 122.2102 | 0.15766 | 0.29839 | -0.082445 | -0.005986 | 122.188 | 122.1591 | 122.1497 | 122.2426 | 0.037678 | 122.106 | 122.1588 | 122.2352 | 122.0172 | -122.3819
1772.375 | 122.5067 | -122.2549 | -0.004578 | 0.002213 | -0.060215 | 0.064817 | -0.012366 | -0.0080829 | 0.0073777 | -0.011751 | -0.0011537 | -0.001658 | -0.0060825 | 0.023408 | -0.011809 | 0.014783 | 0.001407 | -0.017566 | -0.053175 | -0.086641 | -0.091543 | 0.028521 | -0.026425 | -0.224 | -122.0835 | -0.13984 | -0.077866 | -0.010564 | -122.3865 | 122.2835 | -0.048597 | 122.2697 | 122.2374 | -0.046087 | -0.082063 | -0.086965 | -0.13157 | -0.13526 | 122.2285 | 0.1714 | 0.30297 | -0.073288 | -0.005986 | 122.2018 | 122.1683 | 122.1634 | 122.2564 | 0.033099 | 122.1151 | 122.1771 | 122.2444 | 122.0309 | -122.3819
1774.0625 | 122.4609 | -122.2687 | 0 | 0.002213 | -0.060215 | 0.064817 | -0.011938 | -0.0080829 | 0.0075915 | -0.019381 | -0.0015809 | -0.0020852 | -0.0060825 | 0.022981 | -0.011595 | 0.014783 | 0.015142 | -0.017566 | -0.057754 | -0.095798 | -0.091543 | 0.023942 | -0.026425 | -0.224 | -122.079 | -0.13984 | -0.087023 | -0.015142 | -122.3865 | 122.2926 | -0.057754 | 122.2835 | 122.2511 | -0.041508 | -0.095798 | -0.091543 | -0.11784 | -0.13984 | 122.2423 | 0.18971 | 0.30755 | -0.087023 | -0.015142 | 122.2109 | 122.1729 | 122.1771 | 122.2838 | 0.023942 | 122.1288 | 122.1817 | 122.2535 | 122.0447 | -122.3865
1775.75 | 122.438 | -122.3099 | 0.036621 | -0.013049 | -0.060643 | 0.065031 | -0.011938 | -0.0082965 | 0.0073777 | -0.027012 | -0.0015809 | -0.001658 | -0.0060825 | 0.022981 | -0.011595 | 0.010204 | -0.003172 | -0.017566 | -0.053175 | -0.086641 | -0.096121 | 0.019363 | -0.021846 | -0.224 | -122.0835 | -0.13526 | -0.087023 | -0.015142 | -122.3911 | 122.3292 | -0.089796 | 122.3201 | 122.2923 | -0.036929 | -0.12326 | -0.13274 | -0.08122 | -0.17188 | 122.288 | 0.22633 | 0.30755 | -0.12364 | -0.051763 | 122.2567 | 122.2232 | 122.2138 | 122.3067 | -0.017258 | 122.1746 | 122.2229 | 122.2947 | 122.0859 | -122.4277
1777.4375 | 122.4701 | -122.2961 | 0.013733 | 0.017475 | -0.060429 | 0.064603 | -0.012152 | -0.0080829 | 0.0071641 | -0.019381 | -0.0015809 | -0.0018716 | -0.0060825 | 0.023408 | -0.011809 | 0.014783 | 0.001407 | -0.012988 | -0.057754 | -0.086641 | -0.1007 | 0.019363 | -0.031003 | -0.224 | -122.0835 | -0.13984 | -0.091601 | -0.010564 | -122.3865 | 122.3155 | -0.071487 | 122.3109 | 122.2832 | -0.032351 | -0.10037 | -0.11443 | -0.090373 | -0.15357 | 122.2651 | 0.2126 | 0.30297 | -0.10533 | -0.024297 | 122.2384 | 122.2095 | 122.1954 | 122.2976 | 0.00563 | 122.1563 | 122.2045 | 122.2856 | 122.0721 | -122.4002
1779.1406 | 122.4884 | -122.2733 | 0.032043 | -0.005418 | -0.060215 | 0.064603 | -0.012152 | -0.0082965 | 0.0078051 | -0.0041205 | -0.0015809 | -0.0018716 | -0.0060825 | 0.023194 | -0.011809 | 0.010204 | 0.001407 | -0.022144 | -0.057754 | -0.082062 | -0.091543 | 0.023942 | -0.031003 | -0.224 | -122.0881 | -0.13526 | -0.087023 | -0.019721 | -122.3865 | 122.2972 | -0.089797 | 122.2835 | 122.2511 | -0.046086 | -0.1141 | -0.12359 | -0.11326 | -0.1673 | 122.2423 | 0.18513 | 0.29839 | -0.11907 | -0.051764 | 122.2155 | 122.1912 | 122.1817 | 122.2747 | -0.008101 | 122.138 | 122.1862 | 122.2535 | 122.0493 | -122.4186
1780.8438 | 122.4655 | -122.3053 | 0.027466 | -0.013049 | -0.060429 | 0.064603 | -0.011725 | -0.0080829 | 0.0073777 | -0.027012 | -0.0015809 | -0.001658 | -0.0058689 | 0.023408 | -0.011809 | 0.014783 | 0.001407 | -0.012988 | -0.057754 | -0.09122 | -0.096121 | 0.023942 | -0.026425 | -0.21942 | -122.0835 | -0.13984 | -0.091601 | -0.005985 | -122.4003 | 122.3292 | -0.08522 | 122.3201 | 122.2923 | -0.03693 | -0.11869 | -0.12359 | -0.094955 | -0.1673 | 122.2789 | 0.22175 | 0.31671 | -0.11907 | -0.033451 | 122.2475 | 122.2141 | 122.2092 | 122.3067 | -0.003524 | 122.1655 | 122.2137 | 122.2993 | 122.0859 | -122.4277
1782.5469 | 122.5479 | -122.2549 | -0.018311 | -0.013049 | -0.060643 | 0.064603 | -0.012152 | -0.0082965 | 0.0073777 | -0.019381 | -0.0017945 | -0.0018716 | -0.0060825 | 0.023408 | -0.011809 | 0.014783 | 0.010564 | -0.012988 | -0.053175 | -0.095798 | -0.1007 | 0.023942 | -0.035582 | -0.224 | -122.0881 | -0.13526 | -0.09618 | -0.010564 | -122.4003 | 122.2789 | -0.034864 | 122.2697 | 122.242 | -0.03693 | -0.077487 | -0.082389 | -0.14531 | -0.11695 | 122.2194 | 0.16682 | 0.31213 | -0.077869 | 0.007747 | 122.2018 | 122.1591 | 122.1542 | 122.2655 | 0.042253 | 122.1197 | 122.1588 | 122.2444 | 122.0309 | -122.3819
1784.2656 | 122.4792 | -122.3007 | 0.009155 | -0.005418 | -0.060643 | 0.064817 | -0.012366 | -0.0078693 | 0.0073777 | -0.019381 | -0.0015809 | -0.0018716 | -0.0058689 | 0.023408 | -0.011381 | 0.010204 | 0.005985 | -0.008409 | -0.053175 | -0.086641 | -0.1007 | 0.023942 | -0.035582 | -0.22858 | -122.0927 | -0.13068 | -0.082444 | -0.010564 | -122.3957 | 122.3247 | -0.06233 | 122.3109 | 122.2923 | -0.032351 | -0.095796 | -0.10985 | -0.094954 | -0.13984 | 122.2651 | 0.20802 | 0.30297 | -0.091599 | -0.019719 | 122.2475 | 122.2141 | 122.2 | 122.3067 | 0.014787 | 122.17 | 122.2183 | 122.2902 | 122.0721 | -122.4048
1785.9844 | 122.5296 | -122.2778 | 0 | -0.013049 | -0.060643 | 0.06439 | -0.012152 | -0.0082965 | 0.0073777 | -0.019381 | -0.0015809 | -0.0018716 | -0.0060825 | 0.023408 | -0.011595 | 0.010204 | 0.001407 | -0.017566 | -0.062332 | -0.086641 | -0.096121 | 0.023942 | -0.035582 | -0.21942 | -122.0927 | -0.13984 | -0.082444 | -0.015142 | -122.4048 | 122.3018 | -0.062332 | 122.288 | 122.2603 | -0.041508 | -0.086641 | -0.096121 | -0.127 | -0.13984 | 122.2422 | 0.18513 | 0.31213 | -0.082444 | -0.015142 | 122.2155 | 122.1912 | 122.1817 | 122.2792 | 0.023942 | 122.138 | 122.1954 | 122.2627 | 122.0584 | -122.4048
1787.6719 | 122.4655 | -122.3053 | 0.009155 | 0.002213 | -0.060429 | 0.064603 | -0.012366 | -0.0082965 | 0.0073777 | -0.019381 | -0.0015809 | -0.0018716 | -0.0060825 | 0.023194 | -0.011381 | 0.010204 | 0.010564 | -0.008409 | -0.053175 | -0.086641 | -0.096121 | 0.028521 | -0.035582 | -0.22858 | -122.0927 | -0.13984 | -0.091601 | -0.015142 | -122.3957 | 122.3338 | -0.06233 | 122.3155 | 122.2969 | -0.03693 | -0.095796 | -0.10528 | -0.090376 | -0.14899 | 122.2697 | 0.21259 | 0.30297 | -0.10076 | -0.024297 | 122.2521 | 122.2187 | 122.2092 | 122.3159 | 0.019366 | 122.1655 | 122.2137 | 122.2902 | 122.0767 | -122.4048
1789.4219 | 122.5204 | -122.3053 | 0.009155 | -0.013049 | -0.060429 | 0.064817 | -0.012366 | -0.0082965 | 0.0071641 | -0.011751 | -0.0015809 | -0.0020852 | -0.0058689 | 0.023408 | -0.011809 | 0.005626 | 0.010564 | -0.012988 | -0.048597 | -0.082062 | -0.091543 | 0.023942 | -0.035582 | -0.21942 | -122.1019 | -0.14442 | -0.082444 | -0.010564 | -122.3957 | 122.3292 | -0.057752 | 122.3109 | 122.2923 | -0.03693 | -0.091217 | -0.1007 | -0.090376 | -0.15357 | 122.2697 | 0.20344 | 0.29381 | -0.091599 | -0.019719 | 122.2567 | 122.2232 | 122.2138 | 122.3159 | 0.014787 | 122.1609 | 122.2229 | 122.2947 | 122.0859 | -122.4048
1791.1094 | 122.5708 | -122.2733 | -0.009155 | -0.02068 | -0.060856 | 0.06439 | -0.011938 | -0.0082965 | 0.0071641 | -0.019381 | -0.0013673 | -0.0018716 | -0.0060825 | 0.023194 | -0.011809 | 0.010204 | 0.010564 | -0.017566 | -0.057754 | -0.09122 | -0.086964 | 0.037679 | -0.031003 | -0.23316 | -122.0973 | -0.13984 | -0.087023 | -0.019721 | -122.4048 | 122.3109 | -0.048599 | 122.2835 | 122.2557 | -0.055245 | -0.082065 | -0.077809 | -0.13158 | -0.13068 | 122.2423 | 0.17597 | 0.30755 | -0.077868 | -0.010566 | 122.2155 | 122.182 | 122.1863 | 122.2838 | 0.046834 | 122.1334 | 122.1862 | 122.2535 | 122.0401 | -122.3957
1792.8438 | 122.5708 | -122.2687 | 0 | -0.005418 | -0.060215 | 0.064603 | -0.012366 | -0.0085103 | 0.0069505 | -0.027012 | -0.0017945 | -0.001658 | -0.0060825 | 0.023408 | -0.011381 | 0.010204 | 0.010564 | -0.008409 | -0.053175 | -0.09122 | -0.091543 | 0.019363 | -0.026425 | -0.224 | -122.0927 | -0.13526 | -0.087023 | -0.019721 | -122.4094 | 122.288 | -0.053175 | 122.2789 | 122.2603 | -0.027772 | -0.09122 | -0.091543 | -0.14073 | -0.13526 | 122.2423 | 0.17597 | 0.3167 | -0.087023 | -0.019721 | 122.2155 | 122.1775 | 122.1771 | 122.2792 | 0.019363 | 122.1334 | 122.1817 | 122.249 | 122.0447 | -122.4094
1794.5469 | 122.5708 | -122.2778 | -0.018311 | -0.013049 | -0.060643 | 0.06439 | -0.012152 | -0.0082965 | 0.0073777 | -0.034642 | -0.0017945 | -0.0020852 | -0.0060825 | 0.023408 | -0.011381 | 0.010204 | 0.001407 | -0.008409 | -0.053175 | -0.082062 | -0.096121 | 0.023942 | -0.040161 | -0.21942 | -122.0973 | -0.13984 | -0.087023 | -0.015142 | -122.4048 | 122.3018 | -0.034864 | 122.288 | 122.2694 | -0.032351 | -0.063751 | -0.07781 | -0.127 | -0.12153 | 122.2377 | 0.18055 | 0.30755 | -0.068712 | 0.003169 | 122.2247 | 122.1958 | 122.1817 | 122.2792 | 0.042253 | 122.138 | 122.1908 | 122.2627 | 122.0584 | -122.3865
1796.2812 | 122.5388 | -122.2687 | 0.009155 | -0.02068 | -0.060429 | 0.064603 | -0.012152 | -0.0085103 | 0.0075915 | -0.019381 | -0.0015809 | -0.0018716 | -0.0058689 | 0.023408 | -0.011809 | 0.010204 | 0.005985 | -0.017566 | -0.057754 | -0.082062 | -0.096121 | 0.028521 | -0.035582 | -0.23316 | -122.1019 | -0.13526 | -0.082444 | -0.019721 | -122.414 | 122.2972 | -0.066909 | 122.2789 | 122.2511 | -0.046087 | -0.091217 | -0.10528 | -0.14531 | -0.14441 | 122.2331 | 0.16681 | 0.31213 | -0.091599 | -0.028876 | 122.2109 | 122.1866 | 122.1726 | 122.2747 | 0.019366 | 122.1334 | 122.1862 | 122.249 | 122.0355 | -122.4231
1797.9844 | 122.5891 | -122.2733 | 0 | -0.005418 | -0.060643 | 0.064603 | -0.012152 | -0.0082965 | 0.0075915 | -0.027012 | -0.0013673 | -0.0020852 | -0.0060825 | 0.023622 | -0.011809 | 0.014783 | -0.003172 | -0.012988 | -0.062332 | -0.082062 | -0.091543 | 0.019363 | -0.035582 | -0.23316 | -122.1019 | -0.13526 | -0.077866 | -0.015142 | -122.4094 | 122.2926 | -0.062332 | 122.288 | 122.2603 | -0.032351 | -0.082062 | -0.091543 | -0.13616 | -0.13526 | 122.2377 | 0.17139 | 0.30755 | -0.077866 | -0.015142 | 122.2109 | 122.1912 | 122.1817 | 122.2701 | 0.019363 | 122.138 | 122.1954 | 122.2581 | 122.0401 | -122.4094
1799.6875 | 122.5433 | -122.3007 | 0.004578 | -0.013049 | -0.060856 | 0.064603 | -0.012152 | -0.0082965 | 0.0075915 | -0.019381 | -0.0015809 | -0.0018716 | -0.0060825 | 0.023622 | -0.011381 | 0.005626 | 0.005985 | -0.008409 | -0.053175 | -0.086641 | -0.1007 | 0.023942 | -0.031003 | -0.23316 | -122.1064 | -0.13984 | -0.087023 | -0.015142 | -122.414 | 122.3247 | -0.057753 | 122.3063 | 122.2923 | -0.032351 | -0.091219 | -0.10528 | -0.11327 | -0.14442 | 122.2697 | 0.19428 | 0.30755 | -0.091601 | -0.01972 | 122.2475 | 122.2141 | 122.2 | 122.3067 | 0.019364 | 122.1609 | 122.2137 | 122.2856 | 122.0676 | -122.4186
1801.375 | 122.4655 | -122.3511 | 0.032043 | -0.005418 | -0.060643 | 0.064817 | -0.012152 | -0.0080829 | 0.0071641 | -0.011751 | -0.0013673 | -0.0018716 | -0.0058689 | 0.023622 | -0.011381 | 0.010204 | 0.010564 | -0.012988 | -0.048597 | -0.086641 | -0.1007 | 0.028521 | -0.035582 | -0.23773 | -122.111 | -0.13526 | -0.087023 | -0.019721 | -122.4186 | 122.3796 | -0.08064 | 122.3613 | 122.3381 | -0.041509 | -0.11868 | -0.13274 | -0.067494 | -0.1673 | 122.3155 | 0.24005 | 0.30755 | -0.11907 | -0.051764 | 122.3025 | 122.2644 | 122.2504 | 122.3616 | -0.003522 | 122.2158 | 122.2641 | 122.3314 | 122.1133 | -122.4506
1803.0625 | 122.5571 | -122.3007 | 0.009155 | -0.005418 | -0.060856 | 0.064603 | -0.012152 | -0.0085103 | 0.0071641 | -0.011751 | -0.0015809 | -0.002299 | -0.0060825 | 0.023622 | -0.011595 | 0.010204 | 0.010564 | -0.012988 | -0.048597 | -0.086641 | -0.1007 | 0.019363 | -0.031003 | -0.224 | -122.1064 | -0.13526 | -0.077866 | -0.010564 | -122.4186 | 122.3201 | -0.057752 | 122.3109 | 122.2877 | -0.032351 | -0.095796 | -0.10985 | -0.11785 | -0.14441 | 122.2697 | 0.19428 | 0.31213 | -0.087021 | -0.019719 | 122.2521 | 122.2141 | 122.2 | 122.3113 | 0.010208 | 122.1655 | 122.2229 | 122.2902 | 122.0767 | -122.4277
1804.7656 | 122.4792 | -122.3236 | 0.013733 | -0.013049 | -0.060643 | 0.06439 | -0.011938 | -0.0082965 | 0.0071641 | -0.011751 | -0.0015809 | -0.0018716 | -0.0060825 | 0.023408 | -0.011381 | 0.014783 | 0.005985 | -0.012988 | -0.062332 | -0.086641 | -0.096121 | 0.023942 | -0.040161 | -0.23316 | -122.111 | -0.13526 | -0.082444 | -0.015142 | -122.4186 | 122.3475 | -0.076065 | 122.3384 | 122.3106 | -0.03693 | -0.10037 | -0.10985 | -0.09496 | -0.14899 | 122.2834 | 0.21259 | 0.30755 | -0.096177 | -0.028875 | 122.2613 | 122.237 | 122.2275 | 122.3296 | 0.010209 | 122.1883 | 122.2412 | 122.3085 | 122.0905 | -122.4323
1806.4844 | 122.4518 | -122.3236 | 0.013733 | -0.005418 | -0.060643 | 0.064603 | -0.011725 | -0.0085103 | 0.0069505 | -0.019381 | -0.0017945 | -0.0020852 | -0.0060825 | 0.023622 | -0.011381 | 0.010204 | 0.010564 | -0.012988 | -0.053175 | -0.09122 | -0.096121 | 0.019363 | -0.040161 | -0.23773 | -122.1156 | -0.13984 | -0.087023 | -0.015142 | -122.4277 | 122.343 | -0.066908 | 122.3338 | 122.3106 | -0.032351 | -0.10495 | -0.10985 | -0.10412 | -0.15357 | 122.2834 | 0.20801 | 0.31213 | -0.10076 | -0.028875 | 122.2704 | 122.2324 | 122.2275 | 122.3342 | 0.00563 | 122.1838 | 122.2366 | 122.3085 | 122.0859 | -122.4415
1808.1719 | 122.5937 | -122.3007 | -0.004578 | -0.005418 | -0.06107 | 0.064176 | -0.012366 | -0.0085103 | 0.0069505 | -0.011751 | -0.0013673 | -0.0018716 | -0.0058689 | 0.023622 | -0.011809 | 0.010204 | 0.005985 | -0.017566 | -0.053175 | -0.095798 | -0.091543 | 0.023942 | -0.040161 | -0.23316 | -122.111 | -0.13068 | -0.087023 | -0.015142 | -122.4231 | 122.3247 | -0.048597 | 122.3109 | 122.2832 | -0.041508 | -0.09122 | -0.086965 | -0.12243 | -0.1261 | 122.2606 | 0.1897 | 0.31213 | -0.082445 | -0.010564 | 122.2475 | 122.2049 | 122.2092 | 122.3067 | 0.02852 | 122.17 | 122.2137 | 122.2856 | 122.0676 | -122.4186
1809.875 | 122.493 | -122.3236 | 0.018311 | 0.002213 | -0.060856 | 0.063962 | -0.012366 | -0.0080829 | 0.0071641 | -0.019381 | -0.0013673 | -0.001658 | -0.0056553 | 0.023622 | -0.011809 | 0.010204 | 0.001407 | -0.012988 | -0.057754 | -0.09122 | -0.10528 | 0.023942 | -0.040161 | -0.23773 | -122.1156 | -0.13068 | -0.087023 | -0.015142 | -122.4277 | 122.3475 | -0.076065 | 122.3338 | 122.3106 | -0.03693 | -0.10953 | -0.12359 | -0.10412 | -0.14899 | 122.2834 | 0.20801 | 0.31213 | -0.10533 | -0.033453 | 122.2659 | 122.2324 | 122.2183 | 122.325 | 0.005631 | 122.1929 | 122.2366 | 122.3085 | 122.0859 | -122.446
1811.5781 | 122.4609 | -122.3373 | 0.009155 | -0.013049 | -0.060856 | 0.063962 | -0.012579 | -0.0085103 | 0.0073777 | -0.011751 | -0.0017945 | -0.0018716 | -0.0058689 | 0.023194 | -0.011595 | 0.010204 | 0.001407 | -0.008409 | -0.057754 | -0.09122 | -0.096121 | 0.028521 | -0.035582 | -0.224 | -122.1248 | -0.13526 | -0.09618 | -0.019721 | -122.4277 | 122.3659 | -0.066909 | 122.3475 | 122.3289 | -0.03693 | -0.10037 | -0.10528 | -0.090385 | -0.14441 | 122.3018 | 0.21258 | 0.30297 | -0.10533 | -0.028876 | 122.2796 | 122.2461 | 122.2412 | 122.3387 | 0.019366 | 122.2021 | 122.2412 | 122.3176 | 122.1133 | -122.4369
1813.2969 | 122.4609 | -122.3602 | 0.036621 | -0.013049 | -0.061284 | 0.06439 | -0.012579 | -0.0082965 | 0.0075915 | -0.019381 | -0.0013673 | -0.001658 | -0.0058689 | 0.023622 | -0.011595 | 0.010204 | 0.010564 | -0.008409 | -0.057754 | -0.082062 | -0.096121 | 0.028521 | -0.044739 | -0.23773 | -122.1156 | -0.13526 | -0.077866 | -0.015142 | -122.4277 | 122.3888 | -0.094375 | 122.3704 | 122.3518 | -0.03693 | -0.11868 | -0.13274 | -0.067497 | -0.17188 | 122.3155 | 0.24463 | 0.31213 | -0.11449 | -0.051763 | 122.3025 | 122.2782 | 122.2641 | 122.3708 | -0.0081 | 122.225 | 122.2824 | 122.3451 | 122.1225 | -122.4643
1815 | 122.5983 | -122.2824 | -0.004578 | -0.005418 | -0.060856 | 0.06439 | -0.012366 | -0.0080829 | 0.0071641 | -0.011751 | -0.0013673 | -0.0018716 | -0.0058689 | 0.023835 | -0.011809 | 0.010204 | 0.001407 | -0.008409 | -0.057754 | -0.09122 | -0.096121 | 0.023942 | -0.040161 | -0.24231 | -122.1248 | -0.13984 | -0.082444 | -0.015142 | -122.4323 | 122.3064 | -0.053176 | 122.2926 | 122.274 | -0.032351 | -0.086642 | -0.091543 | -0.14989 | -0.13526 | 122.2422 | 0.15765 | 0.30755 | -0.077866 | -0.010564 | 122.2247 | 122.1912 | 122.1863 | 122.2838 | 0.02852 | 122.1426 | 122.2 | 122.2673 | 122.0401 | -122.4277
1816.7188 | 122.5845 | -122.3145 | 0.009155 | 0.002213 | -0.06107 | 0.06439 | -0.012152 | -0.0080829 | 0.0069505 | -0.019381 | -0.0015809 | -0.0018716 | -0.0060825 | 0.023622 | -0.011595 | 0.005626 | 0.010564 | -0.022144 | -0.057754 | -0.09122 | -0.1007 | 0.028521 | -0.031003 | -0.24689 | -122.1248 | -0.13526 | -0.082444 | -0.010564 | -122.4277 | 122.343 | -0.066909 | 122.3201 | 122.2923 | -0.050665 | -0.10037 | -0.10985 | -0.11327 | -0.14441 | 122.2835 | 0.1897 | 0.30297 | -0.091599 | -0.019719 | 122.2567 | 122.2232 | 122.2138 | 122.325 | 0.019366 | 122.1792 | 122.232 | 122.3039 | 122.0676 | -122.4369
1818.4688 | 122.4747 | -122.3373 | 0.036621 | -0.005418 | -0.06107 | 0.063962 | -0.011938 | -0.0080829 | 0.0071641 | -0.011751 | -0.0015809 | -0.0018716 | -0.0058689 | 0.023622 | -0.011381 | 0.010204 | -0.003172 | -0.017566 | -0.053175 | -0.086641 | -0.091543 | 0.028521 | -0.035582 | -0.23773 | -122.1248 | -0.1261 | -0.087023 | -0.010564 | -122.4415 | 122.3659 | -0.089796 | 122.3475 | 122.3198 | -0.046087 | -0.12326 | -0.12816 | -0.10412 | -0.16272 | 122.3018 | 0.21258 | 0.31671 | -0.12364 | -0.047185 | 122.2842 | 122.2507 | 122.2458 | 122.3342 | -0.0081 | 122.2112 | 122.2503 | 122.3268 | 122.0996 | -122.4781
1820.1719 | 122.4792 | -122.3282 | 0.032043 | -0.005418 | -0.060856 | 0.064176 | -0.012152 | -0.0082965 | 0.0073777 | -0.011751 | -0.0013673 | -0.0018716 | -0.0058689 | 0.023622 | -0.011809 | 0.010204 | 0.001407 | -0.012988 | -0.053175 | -0.09122 | -0.091543 | 0.028521 | -0.031003 | -0.23773 | -122.1202 | -0.13526 | -0.087023 | -0.010564 | -122.4415 | 122.3567 | -0.085218 | 122.3384 | 122.3152 | -0.041509 | -0.12326 | -0.12359 | -0.11328 | -0.1673 | 122.2972 | 0.20801 | 0.32129 | -0.11907 | -0.042607 | 122.275 | 122.237 | 122.2366 | 122.3296 | -0.003522 | 122.1929 | 122.2412 | 122.3176 | 122.0905 | -122.4735
1821.8594 | 122.525 | -122.319 | 0.013733 | -0.013049 | -0.060643 | 0.064176 | -0.012366 | -0.0082965 | 0.0071641 | -0.019381 | -0.0017945 | -0.002299 | -0.0060825 | 0.024049 | -0.012022 | 0.010204 | 0.005985 | -0.012988 | -0.053175 | -0.082062 | -0.091543 | 0.023942 | -0.040161 | -0.23773 | -122.1248 | -0.13526 | -0.082444 | -0.015142 | -122.4415 | 122.343 | -0.066908 | 122.3292 | 122.306 | -0.03693 | -0.095795 | -0.10528 | -0.12243 | -0.14899 | 122.2789 | 0.19427 | 0.31671 | -0.096177 | -0.028875 | 122.2659 | 122.237 | 122.2275 | 122.325 | 0.010209 | 122.1838 | 122.2366 | 122.3039 | 122.0813 | -122.4552
1823.6562 | 122.4792 | -122.3328 | 0.032043 | 0.002213 | -0.060856 | 0.064176 | -0.011938 | -0.0082965 | 0.0071641 | -0.011751 | -0.0017945 | -0.001658 | -0.0062963 | 0.023622 | -0.012022 | 0.001048 | 0.005985 | -0.008409 | -0.057754 | -0.082062 | -0.1007 | 0.023942 | -0.035582 | -0.23316 | -122.1248 | -0.13068 | -0.073287 | -0.010564 | -122.4369 | 122.3567 | -0.089797 | 122.3338 | 122.3244 | -0.032351 | -0.1141 | -0.13274 | -0.10412 | -0.16272 | 122.2972 | 0.20801 | 0.31213 | -0.10533 | -0.042607 | 122.275 | 122.2507 | 122.2321 | 122.3387 | -0.008101 | 122.2021 | 122.2595 | 122.3222 | 122.0996 | -122.4689
1825.375 | 122.5525 | -122.3145 | 0 | -0.013049 | -0.060429 | 0.063962 | -0.011938 | -0.0082965 | 0.0071641 | -0.011751 | -0.0015809 | -0.001658 | -0.0058689 | 0.023835 | -0.011595 | 0.010204 | 0.005985 | -0.017566 | -0.053175 | -0.086641 | -0.10528 | 0.028521 | -0.040161 | -0.23773 | -122.1339 | -0.13526 | -0.087023 | -0.019721 | -122.4369 | 122.343 | -0.053175 | 122.3247 | 122.2969 | -0.046087 | -0.086641 | -0.10528 | -0.12243 | -0.13526 | 122.2743 | 0.18054 | 0.30297 | -0.087023 | -0.019721 | 122.2613 | 122.2278 | 122.2092 | 122.3204 | 0.028521 | 122.1792 | 122.2274 | 122.2947 | 122.0767 | -122.4369
1827.0625 | 122.5159 | -122.3328 | 0.027466 | -0.005418 | -0.061284 | 0.06439 | -0.012152 | -0.0082965 | 0.0071641 | -0.011751 | -0.0015809 | -0.0018716 | -0.0062963 | 0.023194 | -0.011809 | 0.010204 | 0.005985 | -0.012988 | -0.062332 | -0.086641 | -0.096121 | 0.023942 | -0.035582 | -0.24689 | -122.1293 | -0.13068 | -0.087023 | -0.019721 | -122.4415 | 122.3567 | -0.089798 | 122.343 | 122.3198 | -0.03693 | -0.11411 | -0.12359 | -0.1087 | -0.15815 | 122.2972 | 0.20343 | 0.31213 | -0.11449 | -0.047187 | 122.2704 | 122.2461 | 122.2366 | 122.3387 | -0.003524 | 122.2021 | 122.2457 | 122.313 | 122.0859 | -122.4689
1828.75 | 122.5159 | -122.3236 | 0.013733 | -0.005418 | -0.06107 | 0.064176 | -0.012152 | -0.0082965 | 0.0071641 | -0.019381 | -0.0015809 | -0.0018716 | -0.0058689 | 0.023408 | -0.011381 | 0.010204 | 0.001407 | -0.003831 | -0.048597 | -0.086641 | -0.1007 | 0.019363 | -0.035582 | -0.23773 | -122.1293 | -0.13984 | -0.082444 | -0.010564 | -122.4415 | 122.343 | -0.06233 | 122.3338 | 122.3198 | -0.023194 | -0.10037 | -0.11443 | -0.11785 | -0.15357 | 122.288 | 0.19427 | 0.31213 | -0.096177 | -0.024297 | 122.275 | 122.237 | 122.2229 | 122.325 | 0.00563 | 122.1838 | 122.2412 | 122.313 | 122.0859 | -122.4552
1830.4531 | 122.5113 | -122.3282 | 0.036621 | -0.005418 | -0.06107 | 0.06439 | -0.012152 | -0.0085103 | 0.0067369 | -0.011751 | -0.0013673 | -0.0020852 | -0.0060825 | 0.023408 | -0.011809 | 0.010204 | -0.003172 | -0.008409 | -0.053175 | -0.09122 | -0.096121 | 0.028521 | -0.040161 | -0.24689 | -122.1385 | -0.13526 | -0.087023 | -0.015142 | -122.4506 | 122.3567 | -0.089796 | 122.3384 | 122.3198 | -0.03693 | -0.12784 | -0.13274 | -0.12243 | -0.17188 | 122.288 | 0.18969 | 0.31213 | -0.12364 | -0.051763 | 122.275 | 122.237 | 122.2321 | 122.325 | -0.0081 | 122.1929 | 122.2412 | 122.313 | 122.0813 | -122.4872
1832.1719 | 122.4609 | -122.3419 | 0.036621 | 0.002213 | -0.060856 | 0.063749 | -0.011938 | -0.0085103 | 0.0069505 | -0.0041205 | -0.0017945 | -0.0020852 | -0.0056553 | 0.023835 | -0.012236 | 0.014783 | -0.003172 | -0.012988 | -0.048597 | -0.086641 | -0.091543 | 0.023942 | -0.040161 | -0.23773 | -122.1339 | -0.13984 | -0.082444 | -0.019721 | -122.4415 | 122.3659 | -0.085218 | 122.3567 | 122.3289 | -0.03693 | -0.12326 | -0.12816 | -0.099543 | -0.17646 | 122.3018 | 0.20801 | 0.30755 | -0.11907 | -0.056342 | 122.2933 | 122.2553 | 122.2504 | 122.3387 | -0.012679 | 122.2021 | 122.2595 | 122.3222 | 122.1042 | -122.4781
1833.9219 | 122.5662 | -122.319 | -0.009155 | -0.013049 | -0.061497 | 0.064176 | -0.012152 | -0.0089375 | 0.0071641 | -0.019381 | -0.0015809 | -0.001658 | -0.0058689 | 0.023622 | -0.011809 | 0.001048 | 0.015142 | -0.003831 | -0.048597 | -0.086641 | -0.096121 | 0.019363 | -0.040161 | -0.24689 | -122.1385 | -0.14899 | -0.082444 | -0.010564 | -122.4506 | 122.3384 | -0.039442 | 122.3201 | 122.3152 | -0.023194 | -0.077486 | -0.086966 | -0.13159 | -0.13984 | 122.2789 | 0.18054 | 0.31213 | -0.073289 | -0.001409 | 122.2704 | 122.2324 | 122.2229 | 122.3342 | 0.028518 | 122.17 | 122.2366 | 122.3085 | 122.0721 | -122.4415
1835.6094 | 122.525 | -122.3465 | 0.045776 | 0.009844 | -0.060643 | 0.064176 | -0.012152 | -0.0082965 | 0.0071641 | -0.019381 | -0.0015809 | -0.001658 | -0.0056553 | 0.023408 | -0.012022 | 0.005626 | 0.005985 | -0.008409 | -0.053175 | -0.086641 | -0.091543 | 0.019363 | -0.044739 | -0.24231 | -122.1385 | -0.13526 | -0.077866 | -0.019721 | -122.446 | 122.3659 | -0.098951 | 122.3521 | 122.3381 | -0.027772 | -0.13242 | -0.13732 | -0.099544 | -0.18104 | 122.3018 | 0.208 | 0.30755 | -0.12364 | -0.065497 | 122.2933 | 122.2599 | 122.255 | 122.3525 | -0.026413 | 122.2112 | 122.2686 | 122.3268 | 122.1042 | -122.4918
1837.3125 | 122.4792 | -122.3419 | 0.022888 | -0.005418 | -0.06107 | 0.063962 | -0.012366 | -0.0082965 | 0.0071641 | -0.019381 | -0.0017945 | -0.0018716 | -0.0062963 | 0.023408 | -0.012022 | 0.005626 | 0.010564 | -0.012988 | -0.044018 | -0.086641 | -0.091543 | 0.023942 | -0.044739 | -0.24689 | -122.1476 | -0.13984 | -0.073287 | -0.015142 | -122.4506 | 122.3659 | -0.066906 | 122.3475 | 122.3289 | -0.03693 | -0.10953 | -0.11443 | -0.1087 | -0.16273 | 122.2972 | 0.19427 | 0.30297 | -0.096175 | -0.03803 | 122.2979 | 122.2553 | 122.2504 | 122.3525 | 0.001054 | 122.2021 | 122.2686 | 122.3268 | 122.095 | -122.4735
1839.0156 | 122.5754 | -122.3328 | -0.004578 | -0.02068 | -0.061284 | 0.063962 | -0.012366 | -0.0080829 | 0.0071641 | -0.019381 | -0.0015809 | -0.0018716 | -0.0058689 | 0.023622 | -0.011809 | 0.005626 | 0.005985 | -0.012988 | -0.053175 | -0.086641 | -0.096121 | 0.023942 | -0.040161 | -0.24231 | -122.1431 | -0.13526 | -0.087023 | -0.015142 | -122.4506 | 122.3567 | -0.048597 | 122.3384 | 122.3198 | -0.03693 | -0.082063 | -0.091543 | -0.11786 | -0.13068 | 122.2926 | 0.18969 | 0.30755 | -0.082445 | -0.010564 | 122.2796 | 122.2461 | 122.2366 | 122.3387 | 0.02852 | 122.1975 | 122.2457 | 122.3176 | 122.0905 | -122.446
1840.7031 | 122.5571 | -122.3328 | 0.022888 | -0.013049 | -0.061284 | 0.063962 | -0.012366 | -0.0085103 | 0.0069505 | -0.011751 | -0.0017945 | -0.0018716 | -0.0060825 | 0.023835 | -0.011595 | 0.005626 | 0.005985 | -0.012988 | -0.057754 | -0.086641 | -0.1007 | 0.019363 | -0.040161 | -0.24231 | -122.1476 | -0.13068 | -0.082444 | -0.015142 | -122.4598 | 122.3521 | -0.080642 | 122.3384 | 122.3198 | -0.032351 | -0.10953 | -0.12359 | -0.12701 | -0.15357 | 122.2926 | 0.18511 | 0.31213 | -0.10533 | -0.03803 | 122.275 | 122.2461 | 122.2321 | 122.3387 | -0.003525 | 122.2021 | 122.2503 | 122.3176 | 122.0905 | -122.4827
1842.4219 | 122.6212 | -122.3099 | -0.018311 | -0.005418 | -0.060856 | 0.063749 | -0.012366 | -0.0087239 | 0.0067369 | -0.011751 | -0.0013673 | -0.001658 | -0.0062963 | 0.023835 | -0.011168 | 0.014783 | 0.005985 | -0.008409 | -0.053175 | -0.082062 | -0.096121 | 0.019363 | -0.044739 | -0.25147 | -122.1385 | -0.13984 | -0.087023 | -0.005985 | -122.4552 | 122.3292 | -0.034864 | 122.3247 | 122.3015 | -0.027772 | -0.063751 | -0.07781 | -0.14532 | -0.12153 | 122.2651 | 0.17138 | 0.31671 | -0.068712 | 0.012326 | 122.2567 | 122.2278 | 122.2138 | 122.3159 | 0.037674 | 122.17 | 122.2229 | 122.3039 | 122.0584 | -122.4369
1844.125 | 122.4838 | -122.3602 | 0.027466 | -0.005418 | -0.061284 | 0.063962 | -0.012579 | -0.0087239 | 0.0071641 | -0.011751 | -0.0015809 | -0.0020852 | -0.0058689 | 0.024049 | -0.011809 | 0.001048 | -0.003172 | -0.017566 | -0.053175 | -0.095798 | -0.096121 | 0.019363 | -0.044739 | -0.25147 | -122.1431 | -0.13526 | -0.087023 | -0.015142 | -122.4644 | 122.3796 | -0.080641 | 122.3613 | 122.3427 | -0.036929 | -0.12326 | -0.12359 | -0.10413 | -0.16273 | 122.3155 | 0.21716 | 0.32128 | -0.11449 | -0.042608 | 122.3071 | 122.2644 | 122.2641 | 122.3571 | -0.008103 | 122.225 | 122.2732 | 122.3451 | 122.1088 | -122.4918
1845.8594 | 122.5296 | -122.3465 | 0.018311 | -0.005418 | -0.061497 | 0.063962 | -0.012579 | -0.0087239 | 0.0069505 | -0.011751 | -0.0015809 | -0.0018716 | -0.0060825 | 0.023835 | -0.012022 | 0.014783 | 0.005985 | -0.003831 | -0.053175 | -0.082062 | -0.096121 | 0.023942 | -0.035582 | -0.24689 | -122.1476 | -0.13526 | -0.082444 | -0.010564 | -122.4598 | 122.3704 | -0.071486 | 122.3613 | 122.3427 | -0.027773 | -0.10037 | -0.11443 | -0.11328 | -0.15357 | 122.3109 | 0.19885 | 0.31213 | -0.10076 | -0.028875 | 122.2933 | 122.2644 | 122.2504 | 122.3525 | 0.005631 | 122.2112 | 122.2641 | 122.3359 | 122.0996 | -122.4781
1847.5625 | 122.493 | -122.3373 | 0.036621 | -0.013049 | -0.06107 | 0.064176 | -0.012579 | -0.0082965 | 0.0067369 | -0.027012 | -0.0017945 | -0.0018716 | -0.0060825 | 0.023835 | -0.011595 | 0.014783 | 0.005985 | -0.012988 | -0.057754 | -0.077483 | -0.091543 | 0.019363 | -0.040161 | -0.24689 | -122.1431 | -0.13526 | -0.091601 | -0.015142 | -122.4552 | 122.3567 | -0.094375 | 122.3521 | 122.3244 | -0.032351 | -0.1141 | -0.12816 | -0.11786 | -0.17188 | 122.2972 | 0.19427 | 0.31213 | -0.12822 | -0.051763 | 122.2796 | 122.2599 | 122.2458 | 122.3433 | -0.017258 | 122.2021 | 122.2457 | 122.3222 | 122.0904 | -122.4918
1849.2812 | 122.6074 | -122.3053 | 0.004578 | -0.013049 | -0.061284 | 0.063749 | -0.012152 | -0.0085103 | 0.0069505 | -0.027012 | -0.0015809 | -0.0020852 | -0.0062963 | 0.023835 | -0.011809 | 0.005626 | 0.005985 | -0.012988 | -0.048597 | -0.086641 | -0.096121 | 0.019363 | -0.040161 | -0.24231 | -122.1476 | -0.13526 | -0.091601 | -0.015142 | -122.4598 | 122.3247 | -0.053175 | 122.3109 | 122.2923 | -0.032351 | -0.091219 | -0.1007 | -0.15448 | -0.13984 | 122.2651 | 0.15765 | 0.31213 | -0.096179 | -0.01972 | 122.2567 | 122.2187 | 122.2092 | 122.3113 | 0.014785 | 122.17 | 122.2137 | 122.2902 | 122.063 | -122.4644
1851 | 122.5708 | -122.3419 | -0.009155 | -0.013049 | -0.061711 | 0.063749 | -0.012366 | -0.0082965 | 0.0067369 | -0.019381 | -0.0017945 | -0.0018716 | -0.0062963 | 0.023835 | -0.011381 | 0.014783 | 0.001407 | -0.012988 | -0.053175 | -0.09122 | -0.091543 | 0.023942 | -0.044739 | -0.25147 | -122.1568 | -0.13984 | -0.091601 | -0.015142 | -122.4644 | 122.3659 | -0.04402 | 122.3567 | 122.3289 | -0.03693 | -0.082065 | -0.082388 | -0.12244 | -0.13068 | 122.2972 | 0.18511 | 0.30755 | -0.082446 | -0.005987 | 122.2887 | 122.2507 | 122.2504 | 122.3433 | 0.033097 | 122.2021 | 122.2503 | 122.3268 | 122.0904 | -122.4552
1852.6875 | 122.6395 | -122.3236 | -0.004578 | -0.005418 | -0.061284 | 0.063962 | -0.013007 | -0.0087239 | 0.0071641 | -0.027012 | -0.0020083 | -0.0014444 | -0.0058689 | 0.023622 | -0.011809 | 0.010204 | 0.005985 | -0.008409 | -0.057754 | -0.086641 | -0.086964 | 0.019363 | -0.044739 | -0.24689 | -122.1522 | -0.13526 | -0.087023 | -0.010564 | -122.4644 | 122.343 | -0.053176 | 122.3338 | 122.3152 | -0.027772 | -0.082063 | -0.082386 | -0.14075 | -0.13068 | 122.2789 | 0.17138 | 0.31213 | -0.082445 | -0.005986 | 122.2659 | 122.237 | 122.2366 | 122.3296 | 0.023941 | 122.1883 | 122.2366 | 122.313 | 122.0767 | -122.4598
1854.4062 | 122.58 | -122.3419 | 0.018311 | -0.005418 | -0.061284 | 0.063962 | -0.012366 | -0.0085103 | 0.0067369 | -0.011751 | -0.0015809 | -0.001658 | -0.0060825 | 0.023835 | -0.011809 | 0.005626 | 0.001407 | -0.012988 | -0.057754 | -0.09122 | -0.086964 | 0.019363 | -0.040161 | -0.25605 | -122.1568 | -0.14442 | -0.091601 | -0.015142 | -122.4735 | 122.3613 | -0.076065 | 122.3475 | 122.3289 | -0.032351 | -0.10953 | -0.10528 | -0.13159 | -0.16273 | 122.3018 | 0.18511 | 0.31671 | -0.10991 | -0.033453 | 122.2842 | 122.2507 | 122.255 | 122.3433 | 0.001052 | 122.1975 | 122.2503 | 122.3268 | 122.0859 | -122.4918
1856.0938 | 122.6028 | -122.3557 | 0.027466 | -0.02068 | -0.061497 | 0.063962 | -0.012366 | -0.0082965 | 0.0069505 | -0.011751 | -0.0017945 | -0.0018716 | -0.0060825 | 0.023835 | -0.011595 | 0.010204 | 0.001407 | -0.012988 | -0.048597 | -0.082062 | -0.091543 | 0.028521 | -0.044739 | -0.25147 | -122.1614 | -0.13068 | -0.087023 | -0.015142 | -122.4689 | 122.3842 | -0.076063 | 122.3659 | 122.3427 | -0.041509 | -0.10953 | -0.11901 | -0.11328 | -0.15815 | 122.3109 | 0.19427 | 0.30755 | -0.11449 | -0.042608 | 122.3071 | 122.2736 | 122.2641 | 122.3571 | 0.001055 | 122.225 | 122.2686 | 122.3405 | 122.1042 | -122.4964
1857.7969 | 122.5433 | -122.3648 | 0.027466 | -0.02068 | -0.06107 | 0.063962 | -0.012579 | -0.0085103 | 0.0067369 | -0.019381 | -0.0015809 | -0.0018716 | -0.0058689 | 0.023835 | -0.011595 | 0.010204 | 0.005985 | -0.008409 | -0.053175 | -0.086641 | -0.096121 | 0.019363 | -0.044739 | -0.24689 | -122.1568 | -0.13068 | -0.087023 | -0.015142 | -122.4689 | 122.3842 | -0.080641 | 122.375 | 122.3564 | -0.027772 | -0.11411 | -0.12359 | -0.10413 | -0.15815 | 122.3201 | 0.208 | 0.31213 | -0.11449 | -0.042608 | 122.3116 | 122.2782 | 122.2687 | 122.3708 | -0.008103 | 122.2341 | 122.2778 | 122.3497 | 122.1179 | -122.4964
1859.5 | 122.5113 | -122.3602 | 0.032043 | -0.013049 | -0.061284 | 0.063962 | -0.012366 | -0.0082965 | 0.0067369 | -0.019381 | -0.0015809 | -0.0018716 | -0.0060825 | 0.023622 | -0.011595 | 0.010204 | 0.005985 | -0.008409 | -0.057754 | -0.082062 | -0.096121 | 0.028521 | -0.044739 | -0.25147 | -122.1568 | -0.14442 | -0.091601 | -0.015142 | -122.4689 | 122.3888 | -0.089797 | 122.3704 | 122.3518 | -0.03693 | -0.1141 | -0.12816 | -0.10871 | -0.17646 | 122.3155 | 0.20342 | 0.31213 | -0.12364 | -0.047185 | 122.3025 | 122.2782 | 122.2641 | 122.3662 | -0.003522 | 122.2158 | 122.2686 | 122.3451 | 122.1088 | -122.501
1861.1875 | 122.6349 | -122.3236 | -0.004578 | -0.013049 | -0.061497 | 0.063962 | -0.012579 | -0.0082965 | 0.0063095 | -0.019381 | -0.0015809 | -0.0018716 | -0.0060825 | 0.023622 | -0.012022 | 0.014783 | 0.001407 | -0.012988 | -0.053175 | -0.082062 | -0.1007 | 0.023942 | -0.044739 | -0.25605 | -122.1568 | -0.13526 | -0.087023 | -0.005985 | -122.4781 | 122.3475 | -0.048597 | 122.3384 | 122.3106 | -0.03693 | -0.077484 | -0.096122 | -0.15448 | -0.13068 | 122.2789 | 0.1668 | 0.32129 | -0.082445 | -0.001407 | 122.2704 | 122.2415 | 122.2229 | 122.325 | 0.02852 | 122.1883 | 122.2366 | 122.3176 | 122.0676 | -122.4735
1862.9375 | 122.5891 | -122.3465 | 0 | -0.02068 | -0.061497 | 0.06439 | -0.012579 | -0.0082965 | 0.0067369 | -0.027012 | -0.0015809 | -0.001658 | -0.0056553 | 0.024049 | -0.011809 | 0.001048 | 0.005985 | -0.008409 | -0.048597 | -0.086641 | -0.096121 | 0.028521 | -0.044739 | -0.25147 | -122.166 | -0.13984 | -0.087023 | -0.015142 | -122.4689 | 122.375 | -0.048597 | 122.3475 | 122.3381 | -0.03693 | -0.086641 | -0.096121 | -0.12244 | -0.13984 | 122.3018 | 0.18053 | 0.30297 | -0.087023 | -0.015142 | 122.2979 | 122.2599 | 122.2504 | 122.3525 | 0.028521 | 122.2067 | 122.2595 | 122.3314 | 122.095 | -122.4689
1864.625 | 122.5845 | -122.3557 | 0.004578 | -0.013049 | -0.061925 | 0.063962 | -0.012366 | -0.0085103 | 0.0067369 | -0.011751 | -0.0017945 | -0.0018716 | -0.0056553 | 0.024049 | -0.011809 | 0.010204 | 0.005985 | -0.008409 | -0.057754 | -0.086641 | -0.091543 | 0.023942 | -0.044739 | -0.25605 | -122.1614 | -0.13526 | -0.087023 | -0.005985 | -122.4781 | 122.3796 | -0.062332 | 122.3659 | 122.3472 | -0.032351 | -0.091219 | -0.096121 | -0.12244 | -0.13984 | 122.3109 | 0.19427 | 0.31671 | -0.091601 | -0.010563 | 122.2979 | 122.269 | 122.2641 | 122.3616 | 0.019364 | 122.2204 | 122.2686 | 122.3497 | 122.0996 | -122.4827
1866.3125 | 122.5525 | -122.374 | 0.032043 | -0.005418 | -0.060856 | 0.064176 | -0.011938 | -0.0082965 | 0.0067369 | -0.0041205 | -0.0015809 | -0.001658 | -0.0062963 | 0.024049 | -0.011809 | 0.005626 | 0.005985 | -0.012988 | -0.053175 | -0.086641 | -0.091543 | 0.023942 | -0.040161 | -0.26063 | -122.166 | -0.13526 | -0.082444 | -0.019721 | -122.4735 | 122.3979 | -0.085218 | 122.3796 | 122.361 | -0.03693 | -0.11868 | -0.12359 | -0.099552 | -0.1673 | 122.3338 | 0.208 | 0.30755 | -0.11449 | -0.051764 | 122.3208 | 122.2873 | 122.2824 | 122.3799 | -0.008101 | 122.2387 | 122.2915 | 122.3542 | 122.1133 | -122.5056
1868.0156 | 122.6715 | -122.3419 | 0.004578 | -0.013049 | -0.061497 | 0.063962 | -0.012579 | -0.0082965 | 0.0067369 | -0.0041205 | -0.0017945 | -0.0020852 | -0.0062963 | 0.024049 | -0.012022 | 0.005626 | 0.005985 | -0.008409 | -0.048597 | -0.09122 | -0.091543 | 0.023942 | -0.044739 | -0.26063 | -122.166 | -0.13526 | -0.087023 | -0.015142 | -122.4827 | 122.3659 | -0.053175 | 122.3475 | 122.3335 | -0.032351 | -0.095798 | -0.096121 | -0.14075 | -0.13984 | 122.2972 | 0.17596 | 0.31671 | -0.091601 | -0.01972 | 122.2933 | 122.2507 | 122.2504 | 122.3479 | 0.019364 | 122.2067 | 122.2549 | 122.3268 | 122.0813 | -122.4872
1869.7656 | 122.6486 | -122.319 | -0.009155 | -0.02068 | -0.061497 | 0.064176 | -0.012366 | -0.0085103 | 0.0069505 | -0.019381 | -0.0015809 | -0.0018716 | -0.0060825 | 0.024049 | -0.012022 | 0.010204 | 0.001407 | -0.008409 | -0.053175 | -0.086641 | -0.091543 | 0.019363 | -0.044739 | -0.25605 | -122.166 | -0.13526 | -0.087023 | -0.019721 | -122.4781 | 122.3384 | -0.04402 | 122.3292 | 122.3106 | -0.027772 | -0.077486 | -0.082388 | -0.15906 | -0.1261 | 122.2743 | 0.15307 | 0.31213 | -0.077868 | -0.010566 | 122.2659 | 122.2324 | 122.2275 | 122.3204 | 0.028518 | 122.1838 | 122.232 | 122.2993 | 122.063 | -122.4689
1871.5312 | 122.6166 | -122.3557 | 0.022888 | -0.005418 | -0.061497 | 0.064176 | -0.012366 | -0.0085103 | 0.0069505 | -0.011751 | -0.0015809 | -0.001658 | -0.0062963 | 0.023835 | -0.011809 | 0.010204 | -0.003172 | -0.012988 | -0.053175 | -0.095798 | -0.086964 | 0.014784 | -0.040161 | -0.25605 | -122.1614 | -0.13526 | -0.082444 | -0.019721 | -122.4827 | 122.3704 | -0.076063 | 122.3659 | 122.3427 | -0.027772 | -0.11869 | -0.10985 | -0.12702 | -0.15815 | 122.3155 | 0.19427 | 0.32129 | -0.10533 | -0.042609 | 122.3025 | 122.2599 | 122.2687 | 122.3525 | -0.008104 | 122.2204 | 122.2732 | 122.3359 | 122.0996 | -122.5056
1873.25 | 122.6532 | -122.3511 | -0.013733 | -0.005418 | -0.061497 | 0.063962 | -0.012579 | -0.0087239 | 0.0069505 | -0.011751 | -0.0013673 | -0.001658 | -0.0062963 | 0.023835 | -0.011809 | 0.010204 | -0.012329 | -0.012988 | -0.053175 | -0.086641 | -0.086964 | 0.023942 | -0.049318 | -0.26063 | -122.1705 | -0.14442 | -0.09618 | -0.010564 | -122.4827 | 122.375 | -0.039442 | 122.3613 | 122.3381 | -0.03693 | -0.072908 | -0.073231 | -0.1316 | -0.13068 | 122.3018 | 0.18053 | 0.31213 | -0.082447 | 0.003169 | 122.2979 | 122.2644 | 122.2641 | 122.3387 | 0.037675 | 122.2067 | 122.2549 | 122.3405 | 122.0904 | -122.4689
1875 | 122.5571 | -122.3831 | 0.027466 | -0.013049 | -0.061497 | 0.063962 | -0.012579 | -0.0089375 | 0.0067369 | -0.0041205 | -0.0013673 | -0.0018716 | -0.0060825 | 0.023835 | -0.012022 | 0.010204 | 0.005985 | -0.003831 | -0.048597 | -0.086641 | -0.091543 | 0.023942 | -0.044739 | -0.26063 | -122.1705 | -0.13526 | -0.087023 | -0.010564 | -122.4918 | 122.4071 | -0.076063 | 122.3933 | 122.3793 | -0.027773 | -0.11411 | -0.11901 | -0.10871 | -0.16273 | 122.3384 | 0.21258 | 0.32129 | -0.11449 | -0.03803 | 122.3345 | 122.2965 | 122.2916 | 122.3891 | -0.003524 | 122.2479 | 122.2961 | 122.3726 | 122.1225 | -122.5193
1876.7031 | 122.4976 | -122.4106 | 0.022888 | 0.002213 | -0.061497 | 0.064176 | -0.012793 | -0.0085103 | 0.0069505 | -0.011751 | -0.0013673 | -0.001658 | -0.0058689 | 0.024049 | -0.012022 | 0.005626 | 0.010564 | -0.008409 | -0.048597 | -0.086641 | -0.091543 | 0.023942 | -0.040161 | -0.26521 | -122.1705 | -0.13984 | -0.082444 | -0.015142 | -122.4918 | 122.4345 | -0.071485 | 122.4162 | 122.4022 | -0.032351 | -0.10953 | -0.11443 | -0.081246 | -0.16273 | 122.3704 | 0.24004 | 0.32129 | -0.10533 | -0.03803 | 122.362 | 122.3239 | 122.319 | 122.4211 | 0.001054 | 122.2707 | 122.3281 | 122.3954 | 122.1454 | -122.5147
1878.4844 | 122.5983 | -122.3373 | 0.004578 | -0.013049 | -0.061711 | 0.064176 | -0.012579 | -0.0089375 | 0.0069505 | -0.0041205 | -0.0013673 | -0.001658 | -0.0060825 | 0.024263 | -0.012236 | 0.001048 | -0.003172 | -0.008409 | -0.048597 | -0.086641 | -0.096121 | 0.028521 | -0.049318 | -0.25605 | -122.1705 | -0.13984 | -0.077866 | -0.010564 | -122.4918 | 122.3659 | -0.053175 | 122.3384 | 122.3289 | -0.03693 | -0.091219 | -0.1007 | -0.15449 | -0.14442 | 122.288 | 0.1668 | 0.32129 | -0.082444 | -0.015142 | 122.2887 | 122.2507 | 122.2412 | 122.3342 | 0.023943 | 122.1975 | 122.2595 | 122.3268 | 122.0813 | -122.4964
1880.1875 | 122.612 | -122.374 | 0.004578 | -0.005418 | -0.061497 | 0.063962 | -0.012793 | -0.0085103 | 0.0065231 | -0.019381 | -0.0015809 | -0.001658 | -0.0060825 | 0.023835 | -0.012022 | 0.014783 | 0.005985 | -0.008409 | -0.044018 | -0.086641 | -0.086964 | 0.023942 | -0.049318 | -0.25147 | -122.1751 | -0.14442 | -0.082444 | -0.010564 | -122.4918 | 122.3979 | -0.048596 | 122.3887 | 122.3656 | -0.032351 | -0.091219 | -0.091542 | -0.11787 | -0.14899 | 122.3246 | 0.19884 | 0.31671 | -0.087022 | -0.015142 | 122.3299 | 122.2873 | 122.287 | 122.3799 | 0.019364 | 122.2295 | 122.2915 | 122.3634 | 122.1225 | -122.4964
1881.9219 | 122.6532 | -122.3373 | 0.009155 | -0.005418 | -0.061497 | 0.064176 | -0.012793 | -0.0085103 | 0.0067369 | -0.011751 | -0.0017945 | -0.0014444 | -0.0062963 | 0.024049 | -0.011595 | 0.014783 | 0.005985 | -0.003831 | -0.053175 | -0.086641 | -0.086964 | 0.023942 | -0.044739 | -0.25605 | -122.1705 | -0.13526 | -0.091601 | -0.015142 | -122.4918 | 122.3613 | -0.06233 | 122.3521 | 122.3335 | -0.027773 | -0.095796 | -0.096119 | -0.15449 | -0.14441 | 122.2926 | 0.1668 | 0.32129 | -0.10076 | -0.024297 | 122.2842 | 122.2507 | 122.2504 | 122.3433 | 0.014787 | 122.2021 | 122.2457 | 122.3222 | 122.0813 | -122.501
1883.625 | 122.6257 | -122.3602 | -0.004578 | -0.005418 | -0.061497 | 0.063962 | -0.012793 | -0.0085103 | 0.0069505 | -0.019381 | -0.0020083 | -0.0020852 | -0.0056553 | 0.024049 | -0.011595 | 0.010204 | 0.001407 | -0.008409 | -0.053175 | -0.086641 | -0.091543 | 0.019363 | -0.053897 | -0.26063 | -122.1705 | -0.13984 | -0.082444 | -0.015142 | -122.501 | 122.3796 | -0.048597 | 122.3704 | 122.3518 | -0.027772 | -0.082063 | -0.086965 | -0.14076 | -0.13526 | 122.3063 | 0.18969 | 0.33044 | -0.077866 | -0.010564 | 122.3071 | 122.2736 | 122.2687 | 122.3616 | 0.023941 | 122.2204 | 122.2778 | 122.3451 | 122.0996 | -122.4964
1885.3594 | 122.6074 | -122.3602 | 0.004578 | 0.002213 | -0.061497 | 0.063749 | -0.012579 | -0.0085103 | 0.0067369 | -0.027012 | -0.0015809 | -0.0025126 | -0.0062963 | 0.023835 | -0.012022 | 0.005626 | 0.001407 | -0.008409 | -0.048597 | -0.086641 | -0.096121 | 0.019363 | -0.044739 | -0.26978 | -122.1751 | -0.13526 | -0.082444 | -0.010564 | -122.501 | 122.3796 | -0.053175 | 122.3659 | 122.3518 | -0.027772 | -0.091219 | -0.1007 | -0.14076 | -0.13984 | 122.3155 | 0.18511 | 0.32586 | -0.087022 | -0.015142 | 122.3116 | 122.2736 | 122.2641 | 122.3616 | 0.014785 | 122.225 | 122.2778 | 122.3497 | 122.0904 | -122.5056
1887.0469 | 122.525 | -122.438 | 0.027466 | -0.005418 | -0.061711 | 0.064176 | -0.012793 | -0.0085103 | 0.0069505 | -0.027012 | -0.0015809 | -0.0018716 | -0.0060825 | 0.023835 | -0.011809 | 0.005626 | -0.003172 | -0.003831 | -0.057754 | -0.086641 | -0.096121 | 0.023942 | -0.044739 | -0.26978 | -122.1751 | -0.13526 | -0.087023 | -0.010564 | -122.501 | 122.462 | -0.08522 | 122.4437 | 122.4342 | -0.027773 | -0.11411 | -0.12359 | -0.062938 | -0.16273 | 122.3933 | 0.26293 | 0.32586 | -0.11449 | -0.03803 | 122.3803 | 122.3514 | 122.3419 | 122.4349 | -0.003524 | 122.3028 | 122.351 | 122.4275 | 122.1683 | -122.5285
1888.7188 | 122.5159 | -122.3785 | 0.022888 | 0.009844 | -0.061497 | 0.064176 | -0.012793 | -0.0085103 | 0.0067369 | -0.011751 | -0.0013673 | -0.0018716 | -0.0058689 | 0.024263 | -0.011809 | 0.014783 | 0.005985 | -0.012988 | -0.053175 | -0.077483 | -0.091543 | 0.023942 | -0.049318 | -0.26978 | -122.1797 | -0.13984 | -0.087023 | -0.010564 | -122.501 | 122.4025 | -0.076063 | 122.3933 | 122.3656 | -0.03693 | -0.10037 | -0.11443 | -0.12245 | -0.16273 | 122.3292 | 0.19884 | 0.32129 | -0.10991 | -0.033452 | 122.3254 | 122.3011 | 122.287 | 122.3845 | 0.001054 | 122.2387 | 122.2915 | 122.368 | 122.1088 | -122.5239
1890.4062 | 122.6486 | -122.3419 | 0 | -0.013049 | -0.061711 | 0.064176 | -0.012579 | -0.0085103 | 0.0065231 | -0.019381 | -0.0015809 | -0.0018716 | -0.0060825 | 0.024049 | -0.011809 | 0.005626 | -0.003172 | -0.012988 | -0.053175 | -0.086641 | -0.091543 | 0.028521 | -0.044739 | -0.26521 | -122.1889 | -0.13984 | -0.082444 | -0.010564 | -122.4964 | 122.3704 | -0.053175 | 122.3475 | 122.3289 | -0.041509 | -0.086641 | -0.091543 | -0.15449 | -0.13984 | 122.2972 | 0.15306 | 0.30755 | -0.082444 | -0.010564 | 122.2887 | 122.2553 | 122.2504 | 122.3387 | 0.028521 | 122.2021 | 122.2595 | 122.3314 | 122.0767 | -122.4964
1892.1094 | 122.5479 | -122.3923 | 0.027466 | -0.013049 | -0.061497 | 0.063749 | -0.012152 | -0.0085103 | 0.0067369 | -0.011751 | -0.0015809 | -0.0020852 | -0.0060825 | 0.024049 | -0.011595 | 0.014783 | -0.003172 | -0.008409 | -0.057754 | -0.095798 | -0.086964 | 0.028521 | -0.040161 | -0.26063 | -122.1843 | -0.13068 | -0.077866 | -0.005985 | -122.501 | 122.4208 | -0.08522 | 122.4071 | 122.3839 | -0.03693 | -0.12326 | -0.11443 | -0.10871 | -0.15815 | 122.3521 | 0.20799 | 0.31671 | -0.10533 | -0.033451 | 122.3345 | 122.2965 | 122.3053 | 122.3891 | 0.001055 | 122.2616 | 122.3144 | 122.3863 | 122.1316 | -122.5285
1893.8906 | 122.6624 | -122.3465 | 0.004578 | -0.02068 | -0.061497 | 0.064176 | -0.012579 | -0.0082965 | 0.0067369 | -0.0041205 | -0.0013673 | -0.001658 | -0.0062963 | 0.024263 | -0.011595 | 0.014783 | 0.005985 | -0.008409 | -0.053175 | -0.086641 | -0.091543 | 0.019363 | -0.049318 | -0.26978 | -122.1889 | -0.13984 | -0.077866 | 0.003172 | -122.4964 | 122.3659 | -0.057753 | 122.3613 | 122.3381 | -0.027772 | -0.091219 | -0.096121 | -0.14991 | -0.14442 | 122.2972 | 0.15764 | 0.30755 | -0.082444 | -0.001406 | 122.2933 | 122.2599 | 122.255 | 122.3525 | 0.014785 | 122.2067 | 122.2686 | 122.3497 | 122.0767 | -122.501
1895.5781 | 122.5296 | -122.406 | 0.036621 | -0.013049 | -0.061711 | 0.063962 | -0.012579 | -0.0085103 | 0.0065231 | -0.0041205 | -0.0017945 | -0.001658 | -0.0060825 | 0.024049 | -0.012022 | 0.014783 | -0.007751 | -0.008409 | -0.053175 | -0.082062 | -0.096121 | 0.019363 | -0.053897 | -0.26521 | -122.1797 | -0.13068 | -0.087023 | -0.010564 | -122.5101 | 122.4254 | -0.089796 | 122.4208 | 122.3976 | -0.027772 | -0.11868 | -0.13274 | -0.10414 | -0.1673 | 122.3521 | 0.22631 | 0.33044 | -0.12364 | -0.047185 | 122.3528 | 122.3239 | 122.3099 | 122.3983 | -0.017258 | 122.2753 | 122.319 | 122.3954 | 122.1408 | -122.5468
1897.2969 | 122.5113 | -122.4243 | 0.018311 | 0.002213 | -0.061711 | 0.063749 | -0.012579 | -0.0089375 | 0.0063095 | -0.0041205 | -0.0020083 | -0.0018716 | -0.0062963 | 0.024049 | -0.012236 | 0.010204 | 0.001407 | -0.012988 | -0.048597 | -0.086641 | -0.096121 | 0.028521 | -0.053897 | -0.26978 | -122.1889 | -0.13984 | -0.082444 | -0.015142 | -122.5056 | 122.4528 | -0.066908 | 122.4345 | 122.4113 | -0.041509 | -0.10495 | -0.11443 | -0.081249 | -0.15815 | 122.3704 | 0.23546 | 0.31671 | -0.10076 | -0.033453 | 122.3757 | 122.3377 | 122.3282 | 122.4257 | 0.01021 | 122.2845 | 122.3419 | 122.4092 | 122.1545 | -122.5239
1899 | 122.5662 | -122.3923 | 0.018311 | -0.028311 | -0.061497 | 0.063962 | -0.012579 | -0.0085103 | 0.0067369 | -0.019381 | -0.0017945 | -0.0018716 | -0.0060825 | 0.024049 | -0.011809 | 0.014783 | 0.001407 | -0.017566 | -0.044018 | -0.086641 | -0.091543 | 0.028521 | -0.053897 | -0.26521 | -122.1889 | -0.13984 | -0.082444 | -0.019721 | -122.5101 | 122.4208 | -0.062329 | 122.4071 | 122.3747 | -0.046087 | -0.10495 | -0.10985 | -0.11787 | -0.15815 | 122.3384 | 0.20342 | 0.32129 | -0.10076 | -0.038032 | 122.3483 | 122.3056 | 122.3007 | 122.3937 | 0.01021 | 122.2524 | 122.3098 | 122.3726 | 122.1271 | -122.5285
1900.6719 | 122.6669 | -122.3557 | 0.004578 | -0.005418 | -0.061711 | 0.063535 | -0.012793 | -0.0085103 | 0.0067369 | -0.019381 | -0.0015809 | -0.0018716 | -0.0062963 | 0.023835 | -0.011809 | 0.010204 | 0.010564 | -0.012988 | -0.053175 | -0.086641 | -0.086964 | 0.023942 | -0.049318 | -0.27436 | -122.1934 | -0.1261 | -0.082444 | -0.010564 | -122.5056 | 122.3796 | -0.057753 | 122.3659 | 122.3427 | -0.03693 | -0.091219 | -0.091542 | -0.14991 | -0.13068 | 122.3063 | 0.16222 | 0.31213 | -0.087022 | -0.015142 | 122.3025 | 122.269 | 122.2687 | 122.3662 | 0.019364 | 122.2295 | 122.2732 | 122.3451 | 122.0813 | -122.5101
1902.375 | 122.5296 | -122.406 | 0.009155 | -0.013049 | -0.061497 | 0.063321 | -0.012579 | -0.0087239 | 0.0067369 | -0.011751 | -0.0017945 | -0.0018716 | -0.0060825 | 0.024263 | -0.011809 | 0.010204 | 0.010564 | -0.008409 | -0.053175 | -0.086641 | -0.091543 | 0.023942 | -0.049318 | -0.26978 | -122.1889 | -0.13068 | -0.087023 | -0.015142 | -122.5101 | 122.4299 | -0.06233 | 122.4162 | 122.3976 | -0.032351 | -0.095796 | -0.1007 | -0.10414 | -0.13984 | 122.3567 | 0.21715 | 0.32129 | -0.096178 | -0.024297 | 122.3528 | 122.3194 | 122.3145 | 122.4166 | 0.014787 | 122.2753 | 122.319 | 122.3909 | 122.1362 | -122.5193
1904.0781 | 122.5845 | -122.374 | 0.004578 | 0.002213 | -0.061925 | 0.063962 | -0.012793 | -0.0089375 | 0.0067369 | -0.011751 | -0.0015809 | -0.001658 | -0.0060825 | 0.02469 | -0.012022 | 0.010204 | 0.001407 | -0.008409 | -0.048597 | -0.077483 | -0.086964 | 0.019363 | -0.049318 | -0.26521 | -122.1889 | -0.13526 | -0.091601 | -0.019721 | -122.5056 | 122.3933 | -0.053175 | 122.3842 | 122.3656 | -0.027772 | -0.082061 | -0.091542 | -0.1316 | -0.13984 | 122.3246 | 0.1851 | 0.31671 | -0.096179 | -0.024299 | 122.3254 | 122.2965 | 122.287 | 122.3754 | 0.014785 | 122.2387 | 122.2824 | 122.3542 | 122.1088 | -122.5101
1905.75 | 122.5433 | -122.4152 | 0.027466 | 0.009844 | -0.061497 | 0.063962 | -0.012579 | -0.0089375 | 0.0067369 | -0.019381 | -0.0015809 | -0.0018716 | -0.0060825 | 0.024476 | -0.011595 | 0.010204 | -0.003172 | -0.017566 | -0.053175 | -0.086641 | -0.091543 | 0.028521 | -0.044739 | -0.26978 | -122.1934 | -0.13526 | -0.091601 | -0.010564 | -122.5147 | 122.4437 | -0.080641 | 122.4254 | 122.3976 | -0.046087 | -0.11411 | -0.11901 | -0.099562 | -0.16273 | 122.3704 | 0.22172 | 0.32129 | -0.11907 | -0.03803 | 122.362 | 122.3285 | 122.3236 | 122.412 | 0.001055 | 122.2799 | 122.3236 | 122.4046 | 122.1454 | -122.5422
1907.4219 | 122.6486 | -122.374 | 0.009155 | 0.009844 | -0.061925 | 0.063749 | -0.012152 | -0.0087239 | 0.0067369 | -0.011751 | -0.0015809 | -0.001658 | -0.0060825 | 0.024263 | -0.012022 | 0.001048 | -0.003172 | -0.012988 | -0.053175 | -0.082062 | -0.086964 | 0.019363 | -0.049318 | -0.26521 | -122.1889 | -0.1261 | -0.082444 | -0.015142 | -122.5193 | 122.3933 | -0.06233 | 122.375 | 122.361 | -0.032351 | -0.091217 | -0.096119 | -0.14534 | -0.13526 | 122.3246 | 0.1851 | 0.33044 | -0.091599 | -0.024297 | 122.3208 | 122.2919 | 122.287 | 122.3708 | 0.010208 | 122.2479 | 122.2915 | 122.3588 | 122.1088 | -122.5285
1909.0938 | 122.5845 | -122.4289 | 0.013733 | 0.002213 | -0.061925 | 0.063962 | -0.012793 | -0.0082965 | 0.0067369 | -0.019381 | -0.0013673 | -0.001658 | -0.0058689 | 0.024049 | -0.011595 | 0.005626 | 0.001407 | -0.012988 | -0.053175 | -0.082062 | -0.082386 | 0.028521 | -0.049318 | -0.27436 | -122.1889 | -0.13068 | -0.082444 | -0.010564 | -122.5147 | 122.4574 | -0.066908 | 122.4345 | 122.4159 | -0.041509 | -0.095795 | -0.096119 | -0.085829 | -0.14441 | 122.3796 | 0.24004 | 0.32587 | -0.096177 | -0.024297 | 122.3757 | 122.3468 | 122.3465 | 122.4303 | 0.014788 | 122.2982 | 122.3465 | 122.4183 | 122.1545 | -122.5285
1910.7812 | 122.6532 | -122.3419 | -0.009155 | -0.013049 | -0.061711 | 0.063535 | -0.012793 | -0.0091513 | 0.0071641 | -0.019381 | -0.0013673 | -0.0014444 | -0.0058689 | 0.024049 | -0.011809 | 0.005626 | 0.001407 | -0.012988 | -0.044018 | -0.082062 | -0.086964 | 0.019363 | -0.049318 | -0.26521 | -122.198 | -0.13526 | -0.073287 | -0.015142 | -122.5193 | 122.3613 | -0.034863 | 122.3475 | 122.3289 | -0.032351 | -0.072907 | -0.077809 | -0.17738 | -0.1261 | 122.2926 | 0.1439 | 0.32129 | -0.064132 | -0.005987 | 122.2979 | 122.2599 | 122.255 | 122.3433 | 0.028518 | 122.2067 | 122.2686 | 122.3268 | 122.0767 | -122.5101
1912.4688 | 122.5433 | -122.4243 | 0.027466 | -0.005418 | -0.061925 | 0.063535 | -0.012579 | -0.0087239 | 0.0067369 | -0.011751 | -0.0017945 | -0.001658 | -0.0060825 | 0.024049 | -0.012236 | 0.001048 | -0.003172 | -0.017566 | -0.053175 | -0.082062 | -0.091543 | 0.023942 | -0.044739 | -0.27436 | -122.1934 | -0.13068 | -0.077866 | -0.015142 | -122.5239 | 122.4483 | -0.080641 | 122.4254 | 122.4068 | -0.041508 | -0.10953 | -0.11901 | -0.099565 | -0.15815 | 122.3796 | 0.23088 | 0.33044 | -0.10533 | -0.042608 | 122.3711 | 122.3423 | 122.3328 | 122.4211 | -0.003524 | 122.2936 | 122.3465 | 122.4092 | 122.15 | -122.5513
1914.1562 | 122.6074 | -122.3785 | -0.004578 | -0.005418 | -0.061497 | 0.063962 | -0.013007 | -0.0087239 | 0.0067369 | -0.019381 | -0.0017945 | -0.0018716 | -0.0060825 | 0.024049 | -0.011595 | 0.005626 | -0.007751 | -0.012988 | -0.053175 | -0.077483 | -0.082386 | 0.028521 | -0.049318 | -0.27894 | -122.2026 | -0.13068 | -0.077866 | -0.015142 | -122.5285 | 122.4071 | -0.048597 | 122.3842 | 122.3656 | -0.041509 | -0.072905 | -0.077808 | -0.14992 | -0.1261 | 122.3292 | 0.17595 | 0.32586 | -0.073288 | -0.010564 | 122.3254 | 122.3011 | 122.2962 | 122.3708 | 0.033099 | 122.2479 | 122.3007 | 122.3634 | 122.0996 | -122.5239
1915.9219 | 122.6349 | -122.3877 | -0.004578 | -0.005418 | -0.061497 | 0.063535 | -0.012579 | -0.0087239 | 0.0067369 | -0.019381 | -0.0015809 | -0.001658 | -0.0058689 | 0.024049 | -0.011595 | 0.005626 | 0.001407 | -0.012988 | -0.048597 | -0.086641 | -0.096121 | 0.019363 | -0.049318 | -0.27894 | -122.198 | -0.13068 | -0.082444 | -0.005985 | -122.5239 | 122.4071 | -0.044019 | 122.3933 | 122.3747 | -0.032351 | -0.082063 | -0.091543 | -0.13619 | -0.1261 | 122.3384 | 0.18968 | 0.32587 | -0.077866 | -0.001407 | 122.3391 | 122.3011 | 122.2916 | 122.3891 | 0.023941 | 122.257 | 122.3053 | 122.3817 | 122.1088 | -122.5193
1917.625 | 122.5571 | -122.4106 | 0.032043 | -0.013049 | -0.061497 | 0.063535 | -0.012793 | -0.0087239 | 0.0065231 | -0.011751 | -0.0017945 | -0.0018716 | -0.0062963 | 0.024049 | -0.011809 | 0.005626 | -0.003172 | -0.012988 | -0.053175 | -0.082062 | -0.082386 | 0.023942 | -0.044739 | -0.27894 | -122.198 | -0.13984 | -0.077866 | -0.005985 | -122.5285 | 122.4345 | -0.085218 | 122.4162 | 122.3976 | -0.03693 | -0.1141 | -0.11443 | -0.11788 | -0.17188 | 122.3658 | 0.21257 | 0.33044 | -0.10991 | -0.038028 | 122.3574 | 122.3285 | 122.3282 | 122.4074 | -0.008101 | 122.2707 | 122.3327 | 122.4046 | 122.1316 | -122.5605
1919.3438 | 122.5479 | -122.4106 | 0.022888 | -0.013049 | -0.061711 | 0.063535 | -0.012793 | -0.0087239 | 0.0065231 | -0.0041205 | -0.0020083 | -0.0018716 | -0.0058689 | 0.024263 | -0.011809 | 0.014783 | -0.003172 | -0.012988 | -0.053175 | -0.082062 | -0.086964 | 0.019363 | -0.049318 | -0.27436 | -122.198 | -0.14442 | -0.077866 | -0.005985 | -122.533 | 122.4299 | -0.076063 | 122.4254 | 122.3976 | -0.032351 | -0.10495 | -0.10985 | -0.12246 | -0.1673 | 122.3613 | 0.21257 | 0.33502 | -0.10075 | -0.028873 | 122.3574 | 122.3285 | 122.3236 | 122.4074 | -0.003525 | 122.2662 | 122.3327 | 122.4046 | 122.1362 | -122.5559
1921.0781 | 122.5937 | -122.4197 | 0.018311 | -0.013049 | -0.062138 | 0.063749 | -0.012579 | -0.0085103 | 0.0065231 | -0.011751 | -0.0017945 | -0.001658 | -0.0062963 | 0.024263 | -0.011809 | 0.010204 | 0.001407 | -0.012988 | -0.057754 | -0.082062 | -0.091543 | 0.023942 | -0.058476 | -0.27436 | -122.198 | -0.13526 | -0.091601 | -0.015142 | -122.5239 | 122.4437 | -0.076065 | 122.4299 | 122.4068 | -0.03693 | -0.10037 | -0.10985 | -0.10414 | -0.15357 | 122.3613 | 0.22172 | 0.32587 | -0.10991 | -0.033453 | 122.362 | 122.3377 | 122.3282 | 122.4211 | 0.005631 | 122.2845 | 122.3281 | 122.4046 | 122.1454 | -122.5422
1922.75 | 122.6578 | -122.3831 | 0.004578 | -0.005418 | -0.061925 | 0.063962 | -0.012793 | -0.0087239 | 0.0065231 | -0.019381 | -0.0017945 | -0.001658 | -0.0060825 | 0.024049 | -0.012022 | 0.010204 | -0.003172 | -0.017566 | -0.057754 | -0.082062 | -0.096121 | 0.023942 | -0.053897 | -0.27894 | -122.2072 | -0.1261 | -0.091601 | -0.015142 | -122.5239 | 122.4071 | -0.062332 | 122.3933 | 122.3656 | -0.041508 | -0.08664 | -0.1007 | -0.14076 | -0.13068 | 122.3292 | 0.17594 | 0.31671 | -0.096179 | -0.01972 | 122.3254 | 122.3011 | 122.287 | 122.3799 | 0.019364 | 122.257 | 122.2915 | 122.368 | 122.1042 | -122.5285
1924.4688 | 122.6028 | -122.3877 | -0.004578 | 0.002213 | -0.061497 | 0.063749 | -0.012366 | -0.0082965 | 0.0067369 | -0.0041205 | -0.0015809 | -0.0020852 | -0.0060825 | 0.024263 | -0.012022 | 0.010204 | -0.003172 | -0.012988 | -0.053175 | -0.082062 | -0.086964 | 0.019363 | -0.058476 | -0.27894 | -122.2026 | -0.1261 | -0.082444 | -0.015142 | -122.5285 | 122.4071 | -0.048597 | 122.3979 | 122.3747 | -0.032351 | -0.077484 | -0.082386 | -0.14076 | -0.12152 | 122.3292 | 0.1851 | 0.32586 | -0.077866 | -0.010564 | 122.3345 | 122.3056 | 122.3007 | 122.3845 | 0.023941 | 122.2616 | 122.3053 | 122.3726 | 122.1088 | -122.5239
1926.1719 | 122.6074 | -122.3877 | 0.045776 | 0.002213 | -0.061925 | 0.063749 | -0.012366 | -0.0082965 | 0.0067369 | -0.027012 | -0.0015809 | -0.0018716 | -0.0060825 | 0.02469 | -0.012236 | 0.014783 | -0.003172 | -0.026723 | -0.053175 | -0.086641 | -0.096121 | 0.028521 | -0.053897 | -0.27894 | -122.2026 | -0.13526 | -0.082444 | -0.015142 | -122.5285 | 122.4162 | -0.098951 | 122.4025 | 122.361 | -0.055244 | -0.13242 | -0.1419 | -0.14076 | -0.18104 | 122.3338 | 0.1851 | 0.32586 | -0.12822 | -0.060918 | 122.3345 | 122.3011 | 122.2916 | 122.3845 | -0.017255 | 122.2524 | 122.3053 | 122.3726 | 122.1088 | -122.5742
1927.9219 | 122.6028 | -122.4014 | 0.013733 | 0.002213 | -0.061925 | 0.063749 | -0.012579 | -0.0089375 | 0.0063095 | -0.0041205 | -0.0017945 | -0.001658 | -0.0060825 | 0.024263 | -0.011809 | 0.014783 | -0.003172 | -0.017566 | -0.048597 | -0.082062 | -0.086964 | 0.023942 | -0.044739 | -0.27894 | -122.198 | -0.13526 | -0.091601 | -0.010564 | -122.5285 | 122.4254 | -0.06233 | 122.4162 | 122.3839 | -0.041508 | -0.095795 | -0.1007 | -0.12703 | -0.14899 | 122.3567 | 0.20341 | 0.33044 | -0.10533 | -0.024297 | 122.3528 | 122.3194 | 122.3145 | 122.3983 | 0.010209 | 122.2662 | 122.3098 | 122.3909 | 122.1225 | -122.5422
1929.6094 | 122.5845 | -122.4152 | 0 | -0.013049 | -0.061925 | 0.063749 | -0.013007 | -0.0087239 | 0.0069505 | -0.0041205 | -0.0015809 | -0.0020852 | -0.0060825 | 0.024476 | -0.012022 | 0.010204 | -0.003172 | -0.017566 | -0.053175 | -0.086641 | -0.086964 | 0.023942 | -0.049318 | -0.27894 | -122.2163 | -0.13526 | -0.087023 | -0.015142 | -122.533 | 122.4391 | -0.053175 | 122.4254 | 122.3976 | -0.041508 | -0.086641 | -0.086964 | -0.11788 | -0.13526 | 122.3658 | 0.19883 | 0.31671 | -0.087023 | -0.015142 | 122.362 | 122.3285 | 122.3282 | 122.412 | 0.023942 | 122.2799 | 122.3281 | 122.4 | 122.1362 | -122.533
1931.2969 | 122.5479 | -122.438 | 0.018311 | -0.005418 | -0.062138 | 0.063749 | -0.012793 | -0.0085103 | 0.0065231 | -0.019381 | -0.0015809 | -0.0018716 | -0.0060825 | 0.024263 | -0.011595 | 0.005626 | -0.003172 | -0.012988 | -0.048597 | -0.082062 | -0.086964 | 0.019363 | -0.053897 | -0.28352 | -122.2026 | -0.13068 | -0.077866 | -0.015142 | -122.5376 | 122.4574 | -0.066908 | 122.4437 | 122.4251 | -0.032351 | -0.10037 | -0.10528 | -0.099568 | -0.14899 | 122.3842 | 0.23546 | 0.33502 | -0.096177 | -0.033453 | 122.3895 | 122.356 | 122.3511 | 122.4349 | 0.001052 | 122.3074 | 122.3602 | 122.4229 | 122.1545 | -122.5559
1933 | 122.5754 | -122.4289 | 0.018311 | -0.013049 | -0.062138 | 0.063749 | -0.012579 | -0.0085103 | 0.0067369 | -0.0041205 | -0.0017945 | -0.0018716 | -0.0060825 | 0.024476 | -0.011809 | 0.010204 | 0.001407 | -0.012988 | -0.048597 | -0.09122 | -0.096121 | 0.023942 | -0.049318 | -0.27894 | -122.2026 | -0.13068 | -0.087023 | -0.010564 | -122.533 | 122.4528 | -0.066908 | 122.4391 | 122.4159 | -0.03693 | -0.10953 | -0.11443 | -0.10414 | -0.14899 | 122.3796 | 0.2263 | 0.33044 | -0.10533 | -0.028875 | 122.3803 | 122.3377 | 122.3328 | 122.4303 | 0.005631 | 122.2982 | 122.3419 | 122.4183 | 122.15 | -122.5513
1934.6875 | 122.6212 | -122.3969 | -0.004578 | -0.005418 | -0.061925 | 0.063535 | -0.012579 | -0.0089375 | 0.0065231 | -0.011751 | -0.0015809 | -0.0014444 | -0.0058689 | 0.024263 | -0.012022 | 0.005626 | -0.003172 | -0.012988 | -0.048597 | -0.082062 | -0.086964 | 0.019363 | -0.058476 | -0.28352 | -122.2026 | -0.13068 | -0.082444 | -0.015142 | -122.5376 | 122.4162 | -0.044019 | 122.4025 | 122.3839 | -0.032351 | -0.077484 | -0.082386 | -0.14077 | -0.1261 | 122.3384 | 0.19426 | 0.33502 | -0.077866 | -0.010564 | 122.3483 | 122.3148 | 122.3099 | 122.3937 | 0.023941 | 122.2662 | 122.3144 | 122.3817 | 122.1133 | -122.533
1936.4062 | 122.5342 | -122.4152 | 0.036621 | 0.002213 | -0.061925 | 0.063321 | -0.013007 | -0.0085103 | 0.0063095 | -0.019381 | -0.0020083 | -0.0018716 | -0.0062963 | 0.024263 | -0.011809 | 0.010204 | 0.005985 | -0.012988 | -0.048597 | -0.086641 | -0.086964 | 0.028521 | -0.058476 | -0.27894 | -122.2072 | -0.13526 | -0.082444 | -0.010564 | -122.533 | 122.4437 | -0.085218 | 122.4254 | 122.4022 | -0.041509 | -0.12326 | -0.12359 | -0.11788 | -0.17188 | 122.3567 | 0.20799 | 0.32587 | -0.11907 | -0.047185 | 122.3666 | 122.3285 | 122.3282 | 122.4211 | -0.0081 | 122.2799 | 122.3327 | 122.4046 | 122.1362 | -122.5697
1938.1406 | 122.6486 | -122.4014 | 0.004578 | -0.013049 | -0.061925 | 0.063749 | -0.013007 | -0.0087239 | 0.0060959 | -0.027012 | -0.0017945 | -0.0018716 | -0.0058689 | 0.024476 | -0.012022 | 0.005626 | -0.003172 | -0.017566 | -0.044018 | -0.077483 | -0.086964 | 0.019363 | -0.053897 | -0.28352 | -122.2118 | -0.13068 | -0.087023 | -0.010564 | -122.5422 | 122.4208 | -0.048596 | 122.4071 | 122.3839 | -0.036929 | -0.082061 | -0.091542 | -0.14077 | -0.13526 | 122.3475 | 0.18968 | 0.33044 | -0.091601 | -0.015142 | 122.3574 | 122.3239 | 122.3145 | 122.3983 | 0.014785 | 122.2707 | 122.3144 | 122.3909 | 122.1179 | -122.5468
1939.8281 | 122.5754 | -122.438 | 0.027466 | -0.005418 | -0.062352 | 0.063535 | -0.012579 | -0.0085103 | 0.0063095 | -0.027012 | -0.0015809 | -0.0018716 | -0.0062963 | 0.024263 | -0.011809 | 0.005626 | 0.005985 | -0.012988 | -0.044018 | -0.086641 | -0.082386 | 0.014784 | -0.063054 | -0.28352 | -122.2209 | -0.13526 | -0.082444 | -0.005985 | -122.5422 | 122.4528 | -0.071484 | 122.4437 | 122.4251 | -0.027772 | -0.11411 | -0.10985 | -0.10415 | -0.16273 | 122.375 | 0.21714 | 0.32129 | -0.10991 | -0.033451 | 122.394 | 122.3514 | 122.3557 | 122.444 | -0.012682 | 122.3028 | 122.3556 | 122.4321 | 122.1545 | -122.5697
1941.5312 | 122.7127 | -122.3923 | 0 | -0.005418 | -0.062352 | 0.063535 | -0.012579 | -0.0087239 | 0.0065231 | -0.019381 | -0.0015809 | -0.0018716 | -0.0056553 | 0.024263 | -0.012022 | 0.014783 | -0.003172 | -0.008409 | -0.053175 | -0.077483 | -0.091543 | 0.023942 | -0.053897 | -0.28352 | -122.2072 | -0.13526 | -0.087023 | -0.010564 | -122.5422 | 122.4162 | -0.053175 | 122.4071 | 122.3839 | -0.032351 | -0.077483 | -0.091543 | -0.14992 | -0.13526 | 122.3384 | 0.1851 | 0.33502 | -0.087023 | -0.010564 | 122.3391 | 122.3148 | 122.3007 | 122.3891 | 0.023942 | 122.257 | 122.3053 | 122.3817 | 122.1088 | -122.5422
1943.2344 | 122.644 | -122.3923 | 0.022888 | 0.002213 | -0.062138 | 0.063749 | -0.012793 | -0.0087239 | 0.0067369 | -0.011751 | -0.0017945 | -0.0018716 | -0.0060825 | 0.024476 | -0.012022 | 0.014783 | 0.005985 | -0.017566 | -0.048597 | -0.082062 | -0.091543 | 0.019363 | -0.053897 | -0.28352 | -122.2209 | -0.13068 | -0.087023 | -0.010564 | -122.5468 | 122.4116 | -0.071485 | 122.4071 | 122.3747 | -0.036929 | -0.10495 | -0.11443 | -0.1545 | -0.15357 | 122.3384 | 0.17136 | 0.32587 | -0.10991 | -0.033452 | 122.3437 | 122.3102 | 122.3007 | 122.3983 | -0.003525 | 122.2616 | 122.3053 | 122.3817 | 122.1088 | -122.5697
1945.0156 | 122.6807 | -122.4152 | 0.004578 | -0.02068 | -0.062566 | 0.063749 | -0.013007 | -0.0087239 | 0.0065231 | -0.027012 | -0.0017945 | -0.0018716 | -0.0060825 | 0.024476 | -0.011809 | 0.001048 | -0.007751 | -0.008409 | -0.053175 | -0.082062 | -0.086964 | 0.023942 | -0.053897 | -0.29268 | -122.2118 | -0.13068 | -0.082444 | -0.010564 | -122.5514 | 122.4391 | -0.057753 | 122.4162 | 122.4068 | -0.032351 | -0.08664 | -0.091542 | -0.13619 | -0.13526 | 122.3613 | 0.20341 | 0.3396 | -0.087022 | -0.015142 | 122.362 | 122.3331 | 122.3282 | 122.4074 | 0.019364 | 122.2845 | 122.3327 | 122.4046 | 122.1225 | -122.5559
1946.6875 | 122.644 | -122.4014 | 0.022888 | -0.005418 | -0.062138 | 0.063535 | -0.012366 | -0.0087239 | 0.0067369 | -0.019381 | -0.0020083 | -0.0014444 | -0.0060825 | 0.024476 | -0.011809 | 0.005626 | 0.001407 | -0.017566 | -0.053175 | -0.086641 | -0.086964 | 0.023942 | -0.053897 | -0.2881 | -122.2255 | -0.13526 | -0.082444 | -0.010564 | -122.5514 | 122.4254 | -0.076063 | 122.4071 | 122.3839 | -0.041508 | -0.10953 | -0.10985 | -0.14993 | -0.15815 | 122.3475 | 0.17594 | 0.32587 | -0.10533 | -0.033452 | 122.3483 | 122.3148 | 122.3145 | 122.4028 | 0.001054 | 122.2662 | 122.319 | 122.3909 | 122.1133 | -122.5742
1948.4062 | 122.6852 | -122.3969 | 0.036621 | -0.005418 | -0.062352 | 0.063535 | -0.012793 | -0.0085103 | 0.0065231 | -0.0041205 | -0.0017945 | -0.0018716 | -0.0060825 | 0.024476 | -0.012022 | 0.005626 | 0.001407 | -0.008409 | -0.048597 | -0.077483 | -0.091543 | 0.019363 | -0.058476 | -0.2881 | -122.2118 | -0.13526 | -0.082444 | -0.010564 | -122.5514 | 122.4162 | -0.085218 | 122.4025 | 122.3884 | -0.027772 | -0.1141 | -0.12816 | -0.1545 | -0.17188 | 122.3384 | 0.1851 | 0.3396 | -0.11907 | -0.047185 | 122.3483 | 122.3194 | 122.3053 | 122.3983 | -0.017258 | 122.2616 | 122.3144 | 122.3863 | 122.1088 | -122.588
1950.0938 | 122.7036 | -122.3969 | 0.027466 | -0.013049 | -0.062352 | 0.063535 | -0.013007 | -0.0087239 | 0.0067369 | 0.00351 | -0.0015809 | -0.0018716 | -0.0060825 | 0.024263 | -0.012022 | 0.005626 | -0.003172 | -0.022144 | -0.048597 | -0.077483 | -0.096121 | 0.014784 | -0.058476 | -0.29268 | -122.2209 | -0.13068 | -0.073287 | -0.019721 | -122.5559 | 122.4116 | -0.076063 | 122.4025 | 122.3747 | -0.036928 | -0.10495 | -0.12359 | -0.15908 | -0.15815 | 122.3384 | 0.17594 | 0.33502 | -0.10075 | -0.047187 | 122.3483 | 122.3194 | 122.3007 | 122.3937 | -0.012682 | 122.2662 | 122.3236 | 122.3771 | 122.1042 | -122.5834
1951.7812 | 122.6532 | -122.406 | 0.013733 | -0.013049 | -0.062138 | 0.063535 | -0.012793 | -0.0087239 | 0.0065231 | -0.011751 | -0.0017945 | -0.0018716 | -0.0062963 | 0.02469 | -0.011809 | 0.010204 | -0.003172 | -0.022144 | -0.053175 | -0.082062 | -0.086964 | 0.019363 | -0.063054 | -0.29726 | -122.2163 | -0.13984 | -0.077866 | -0.010564 | -122.5468 | 122.4254 | -0.066908 | 122.4162 | 122.3839 | -0.041507 | -0.095795 | -0.1007 | -0.14077 | -0.15357 | 122.343 | 0.18968 | 0.33044 | -0.091599 | -0.024297 | 122.3528 | 122.3239 | 122.319 | 122.4028 | 0.00563 | 122.2662 | 122.3281 | 122.3954 | 122.1087 | -122.5605
1953.4688 | 122.5845 | -122.4243 | 0.013733 | -0.005418 | -0.062138 | 0.063108 | -0.012793 | -0.0085103 | 0.0063095 | -0.011751 | -0.0020083 | -0.0020852 | -0.0062963 | 0.024476 | -0.011809 | 0.014783 | -0.003172 | -0.012988 | -0.044018 | -0.082062 | -0.091543 | 0.019363 | -0.058476 | -0.29726 | -122.2209 | -0.13526 | -0.082444 | -0.015142 | -122.5514 | 122.4437 | -0.057751 | 122.4391 | 122.4113 | -0.032351 | -0.095795 | -0.10528 | -0.12704 | -0.14899 | 122.3658 | 0.20341 | 0.33044 | -0.096177 | -0.028875 | 122.3803 | 122.3423 | 122.3328 | 122.4211 | 0.00563 | 122.2891 | 122.3419 | 122.4092 | 122.1271 | -122.5651
1955.1719 | 122.644 | -122.4152 | 0.018311 | 0.002213 | -0.062138 | 0.063321 | -0.012793 | -0.0087239 | 0.0065231 | -0.011751 | -0.0015809 | -0.001658 | -0.0062963 | 0.02469 | -0.011809 | 0.010204 | 0.001407 | -0.022144 | -0.044018 | -0.095798 | -0.091543 | 0.014784 | -0.049318 | -0.29268 | -122.2209 | -0.13984 | -0.077866 | -0.005985 | -122.5422 | 122.4299 | -0.062329 | 122.4254 | 122.393 | -0.036928 | -0.11411 | -0.10985 | -0.12704 | -0.15815 | 122.3658 | 0.19425 | 0.32129 | -0.096177 | -0.024296 | 122.3711 | 122.3194 | 122.3236 | 122.4166 | -0.003527 | 122.2753 | 122.3373 | 122.4092 | 122.1225 | -122.5605
1956.8906 | 122.5616 | -122.4152 | 0.036621 | -0.013049 | -0.062352 | 0.063535 | -0.012793 | -0.0087239 | 0.0065231 | -0.011751 | -0.0015809 | -0.0018716 | -0.0062963 | 0.024476 | -0.012022 | 0.014783 | -0.003172 | -0.017566 | -0.057754 | -0.082062 | -0.086964 | 0.019363 | -0.058476 | -0.30184 | -122.2301 | -0.13984 | -0.077866 | -0.010564 | -122.5559 | 122.4345 | -0.094375 | 122.4299 | 122.3976 | -0.036929 | -0.11868 | -0.12359 | -0.14077 | -0.17646 | 122.3567 | 0.1851 | 0.32587 | -0.11449 | -0.047185 | 122.3574 | 122.3331 | 122.3282 | 122.412 | -0.017258 | 122.2753 | 122.3373 | 122.4046 | 122.1133 | -122.5926
1958.5625 | 122.6852 | -122.4014 | -0.009155 | -0.02068 | -0.062352 | 0.063321 | -0.012579 | -0.0089375 | 0.0063095 | -0.019381 | -0.0013673 | -0.0018716 | -0.0058689 | 0.024263 | -0.012022 | 0.001048 | -0.003172 | -0.012988 | -0.053175 | -0.082062 | -0.086964 | 0.014784 | -0.058476 | -0.29268 | -122.2301 | -0.1261 | -0.082444 | -0.010564 | -122.5605 | 122.4162 | -0.04402 | 122.4025 | 122.3884 | -0.027772 | -0.072907 | -0.077809 | -0.15908 | -0.11695 | 122.343 | 0.17136 | 0.33045 | -0.073289 | -0.001409 | 122.3483 | 122.3194 | 122.3145 | 122.3983 | 0.023939 | 122.2753 | 122.319 | 122.3909 | 122.1088 | -122.5514
1960.25 | 122.5616 | -122.4564 | 0.032043 | -0.005418 | -0.062566 | 0.063749 | -0.012579 | -0.0087239 | 0.0063095 | -0.011751 | -0.0015809 | -0.0014444 | -0.0062963 | 0.024476 | -0.011809 | 0.001048 | 0.001407 | -0.017566 | -0.048597 | -0.077483 | -0.091543 | 0.014784 | -0.058476 | -0.29726 | -122.2301 | -0.13068 | -0.082444 | -0.015142 | -122.5559 | 122.4711 | -0.08064 | 122.4574 | 122.4388 | -0.03235 | -0.10953 | -0.12359 | -0.099572 | -0.16272 | 122.3979 | 0.22629 | 0.32587 | -0.11449 | -0.047185 | 122.4078 | 122.3789 | 122.3648 | 122.4578 | -0.017259 | 122.3257 | 122.3739 | 122.4412 | 122.1591 | -122.588
1961.9219 | 122.5983 | -122.4564 | 0.036621 | -0.005418 | -0.062352 | 0.063108 | -0.012579 | -0.0087239 | 0.0063095 | -0.011751 | -0.0015809 | -0.0018716 | -0.0060825 | 0.024476 | -0.011809 | 0.005626 | 0.001407 | -0.012988 | -0.048597 | -0.072904 | -0.086964 | 0.019363 | -0.053897 | -0.30184 | -122.2346 | -0.13526 | -0.087023 | -0.010564 | -122.5559 | 122.4757 | -0.085218 | 122.462 | 122.4434 | -0.032351 | -0.10952 | -0.12359 | -0.099572 | -0.17188 | 122.4025 | 0.22172 | 0.32129 | -0.12364 | -0.047185 | 122.4078 | 122.3835 | 122.3694 | 122.4578 | -0.017258 | 122.3211 | 122.3693 | 122.4458 | 122.1545 | -122.5926
1963.6094 | 122.58 | -122.4335 | 0.032043 | -0.013049 | -0.062566 | 0.063535 | -0.012793 | -0.0080829 | 0.0060959 | -0.027012 | -0.0022219 | -0.0018716 | -0.0062963 | 0.024476 | -0.011809 | 0.010204 | -0.003172 | -0.017566 | -0.053175 | -0.077483 | -0.077807 | 0.023942 | -0.053897 | -0.30641 | -122.2255 | -0.13526 | -0.073287 | -0.010564 | -122.5651 | 122.4574 | -0.085218 | 122.4437 | 122.4159 | -0.041508 | -0.10953 | -0.10985 | -0.13162 | -0.1673 | 122.3796 | 0.20798 | 0.3396 | -0.10533 | -0.042607 | 122.3803 | 122.356 | 122.3557 | 122.4303 | -0.008101 | 122.2982 | 122.3602 | 122.4229 | 122.1271 | -122.5971
1965.2812 | 122.7127 | -122.3923 | -0.013733 | -0.02068 | -0.062352 | 0.063321 | -0.012793 | -0.0076555 | 0.0063095 | -0.011751 | -0.0017945 | -0.001658 | -0.0062963 | 0.02469 | -0.012022 | 0.014783 | 0.005985 | -0.017566 | -0.048597 | -0.082062 | -0.082386 | 0.023942 | -0.058476 | -0.29726 | -122.2301 | -0.13526 | -0.091601 | -0.005985 | -122.5697 | 122.4162 | -0.034864 | 122.4071 | 122.3747 | -0.041508 | -0.068329 | -0.068653 | -0.1774 | -0.12153 | 122.3338 | 0.16221 | 0.3396 | -0.077868 | 0.007748 | 122.3437 | 122.3102 | 122.3099 | 122.3983 | 0.037675 | 122.257 | 122.3007 | 122.3863 | 122.095 | -122.5559
1967.0156 | 122.6578 | -122.4335 | -0.004578 | -0.005418 | -0.062566 | 0.063108 | -0.012579 | -0.0080829 | 0.0063095 | -0.019381 | -0.0015809 | -0.0018716 | -0.0062963 | 0.024263 | -0.011809 | 0.005626 | 0.001407 | -0.017566 | -0.048597 | -0.077483 | -0.082386 | 0.014784 | -0.067633 | -0.30184 | -122.2346 | -0.13068 | -0.077866 | -0.015142 | -122.5605 | 122.4483 | -0.044019 | 122.4391 | 122.4159 | -0.03235 | -0.072905 | -0.077808 | -0.12704 | -0.1261 | 122.3658 | 0.19883 | 0.32587 | -0.073288 | -0.010564 | 122.3849 | 122.356 | 122.3511 | 122.4349 | 0.019362 | 122.3028 | 122.3556 | 122.4183 | 122.1316 | -122.5559
1968.7031 | 122.6303 | -122.4472 | 0.018311 | -0.013049 | -0.062566 | 0.063321 | -0.012579 | -0.0076555 | 0.0060959 | -0.011751 | -0.0013673 | -0.002299 | -0.0065099 | 0.024476 | -0.011595 | 0.014783 | -0.003172 | -0.022144 | -0.048597 | -0.086641 | -0.091543 | 0.019363 | -0.063054 | -0.30184 | -122.2301 | -0.13068 | -0.087023 | -0.005985 | -122.5651 | 122.4666 | -0.066908 | 122.462 | 122.4251 | -0.041507 | -0.10495 | -0.10985 | -0.11789 | -0.14899 | 122.3842 | 0.21714 | 0.33502 | -0.10533 | -0.024296 | 122.3986 | 122.3606 | 122.3557 | 122.444 | 0.001052 | 122.3165 | 122.3602 | 122.4412 | 122.1454 | -122.5834
1970.4062 | 122.699 | -122.3969 | -0.009155 | 0.002213 | -0.062566 | 0.063749 | -0.012579 | -0.0080829 | 0.0060959 | -0.019381 | -0.0015809 | -0.0018716 | -0.0060825 | 0.024263 | -0.012022 | 0.014783 | -0.007751 | -0.008409 | -0.048597 | -0.086641 | -0.082386 | 0.019363 | -0.058476 | -0.29726 | -122.2301 | -0.13984 | -0.082444 | -0.010564 | -122.5651 | 122.4162 | -0.039442 | 122.4116 | 122.3884 | -0.027772 | -0.077486 | -0.073231 | -0.16824 | -0.13068 | 122.3384 | 0.16679 | 0.33502 | -0.073289 | -0.001409 | 122.3483 | 122.3102 | 122.3145 | 122.3891 | 0.028518 | 122.257 | 122.3144 | 122.3863 | 122.0996 | -122.5559
1972.1094 | 122.5983 | -122.4564 | 0.013733 | -0.013049 | -0.062566 | 0.063321 | -0.012579 | -0.0080829 | 0.0063095 | -0.011751 | -0.0015809 | -0.0018716 | -0.0062963 | 0.02469 | -0.011809 | 0.010204 | 0.001407 | -0.008409 | -0.048597 | -0.082062 | -0.086964 | 0.019363 | -0.058476 | -0.30641 | -122.2346 | -0.13526 | -0.087023 | -0.010564 | -122.5697 | 122.4757 | -0.06233 | 122.4666 | 122.448 | -0.027772 | -0.095795 | -0.1007 | -0.11331 | -0.14899 | 122.3979 | 0.22172 | 0.33502 | -0.10076 | -0.024297 | 122.4078 | 122.3743 | 122.3694 | 122.4578 | 0.00563 | 122.3211 | 122.3693 | 122.4458 | 122.1499 | -122.5834
1973.7812 | 122.6624 | -122.4518 | 0.004578 | 0.002213 | -0.062779 | 0.063108 | -0.012366 | -0.0078693 | 0.0063095 | -0.011751 | -0.0013673 | -0.0018716 | -0.0062963 | 0.024476 | -0.012022 | 0.010204 | -0.003172 | -0.012988 | -0.053175 | -0.082062 | -0.086964 | 0.019363 | -0.053897 | -0.29726 | -122.2438 | -0.13984 | -0.077866 | -0.010564 | -122.5651 | 122.4711 | -0.057753 | 122.462 | 122.4388 | -0.032351 | -0.08664 | -0.091542 | -0.11331 | -0.14442 | 122.3979 | 0.20798 | 0.32129 | -0.082444 | -0.015142 | 122.3986 | 122.3697 | 122.3648 | 122.4486 | 0.014785 | 122.3119 | 122.3739 | 122.4412 | 122.1545 | -122.5697
1975.4688 | 122.5571 | -122.4335 | 0.022888 | 0.002213 | -0.062566 | 0.063535 | -0.012579 | -0.0080829 | 0.0060959 | -0.011751 | -0.0017945 | -0.0020852 | -0.0060825 | 0.024476 | -0.012236 | 0.014783 | 0.001407 | -0.022144 | -0.048597 | -0.082062 | -0.091543 | 0.019363 | -0.063054 | -0.31099 | -122.2346 | -0.13068 | -0.082444 | -0.010564 | -122.5651 | 122.4528 | -0.071485 | 122.4483 | 122.4113 | -0.041507 | -0.10495 | -0.11443 | -0.13162 | -0.15357 | 122.3704 | 0.19883 | 0.33044 | -0.10533 | -0.033452 | 122.3849 | 122.3514 | 122.3419 | 122.4349 | -0.003525 | 122.3028 | 122.351 | 122.4229 | 122.1225 | -122.588
1977.1562 | 122.6715 | -122.438 | 0.018311 | -0.005418 | -0.062352 | 0.063321 | -0.012366 | -0.0082965 | 0.0063095 | -0.011751 | -0.0015809 | -0.0020852 | -0.0058689 | 0.02469 | -0.012236 | 0.005626 | -0.003172 | -0.012988 | -0.048597 | -0.077483 | -0.082386 | 0.023942 | -0.058476 | -0.30641 | -122.2392 | -0.13526 | -0.077866 | -0.010564 | -122.5651 | 122.462 | -0.066908 | 122.4437 | 122.4251 | -0.03693 | -0.095794 | -0.1007 | -0.12704 | -0.15357 | 122.3796 | 0.19883 | 0.32587 | -0.096177 | -0.028875 | 122.3895 | 122.3606 | 122.3557 | 122.4349 | 0.005631 | 122.3028 | 122.3602 | 122.4275 | 122.1316 | -122.5834
1978.8594 | 122.5845 | -122.4701 | 0.009155 | -0.005418 | -0.062566 | 0.063321 | -0.012366 | -0.0080829 | 0.0063095 | -0.011751 | -0.0015809 | -0.0014444 | -0.0056553 | 0.02469 | -0.011595 | 0.014783 | 0.001407 | -0.008409 | -0.048597 | -0.082062 | -0.091543 | 0.014784 | -0.063054 | -0.31099 | -122.2392 | -0.13526 | -0.077866 | -0.005985 | -122.5742 | 122.4849 | -0.057752 | 122.4849 | 122.4617 | -0.023193 | -0.091217 | -0.1007 | -0.10415 | -0.14441 | 122.407 | 0.23087 | 0.33502 | -0.087021 | -0.01514 | 122.4215 | 122.388 | 122.3786 | 122.4715 | 0.005629 | 122.3348 | 122.3922 | 122.4641 | 122.1591 | -122.5834
1980.5469 | 122.6578 | -122.4472 | 0.004578 | -0.013049 | -0.062138 | 0.063321 | -0.012366 | -0.0080829 | 0.0063095 | -0.011751 | -0.0017945 | -0.0018716 | -0.0058689 | 0.024263 | -0.012236 | 0.010204 | 0.001407 | -0.017566 | -0.048597 | -0.082062 | -0.082386 | 0.023942 | -0.063054 | -0.30641 | -122.2392 | -0.1261 | -0.073287 | -0.010564 | -122.5742 | 122.4711 | -0.053175 | 122.4574 | 122.4296 | -0.041508 | -0.08664 | -0.086964 | -0.12704 | -0.13068 | 122.3842 | 0.20798 | 0.33502 | -0.077865 | -0.015142 | 122.3986 | 122.3651 | 122.3648 | 122.4486 | 0.019364 | 122.3211 | 122.3739 | 122.4366 | 122.1408 | -122.5788
1982.2188 | 122.731 | -122.406 | -0.004578 | -0.013049 | -0.062566 | 0.063321 | -0.012793 | -0.0080829 | 0.0060959 | -0.027012 | -0.0017945 | -0.001658 | -0.0062963 | 0.024476 | -0.012022 | 0.005626 | -0.003172 | -0.017566 | -0.048597 | -0.082062 | -0.077807 | 0.019363 | -0.067633 | -0.31099 | -122.2438 | -0.13984 | -0.077866 | -0.005985 | -122.5788 | 122.4254 | -0.044019 | 122.4116 | 122.3884 | -0.036929 | -0.077484 | -0.073229 | -0.17282 | -0.13526 | 122.3384 | 0.1622 | 0.33502 | -0.073288 | -0.001407 | 122.3574 | 122.3239 | 122.3282 | 122.4028 | 0.023941 | 122.2662 | 122.3281 | 122.4 | 122.095 | -122.5742
1983.8906 | 122.6257 | -122.4518 | 0.022888 | -0.005418 | -0.062779 | 0.063321 | -0.012793 | -0.0082965 | 0.0065231 | -0.0041205 | -0.0015809 | -0.0018716 | -0.0060825 | 0.024476 | -0.011809 | 0.010204 | -0.003172 | -0.026723 | -0.048597 | -0.077483 | -0.077807 | 0.014784 | -0.067633 | -0.31557 | -122.2392 | -0.13526 | -0.082444 | -0.001407 | -122.5788 | 122.4666 | -0.071485 | 122.462 | 122.4251 | -0.041507 | -0.10037 | -0.1007 | -0.12704 | -0.15815 | 122.3841 | 0.21256 | 0.3396 | -0.10533 | -0.024295 | 122.4032 | 122.3743 | 122.374 | 122.4486 | -0.008104 | 122.3165 | 122.3693 | 122.4504 | 122.1362 | -122.6017
1985.6094 | 122.6807 | -122.4014 | -0.004578 | -0.02068 | -0.062779 | 0.063321 | -0.012793 | -0.0078693 | 0.0065231 | -0.027012 | -0.0017945 | -0.0018716 | -0.0062963 | 0.024476 | -0.012022 | 0.014783 | 0.005985 | -0.017566 | -0.053175 | -0.082062 | -0.082386 | 0.014784 | -0.058476 | -0.30641 | -122.2484 | -0.13068 | -0.082444 | -0.010564 | -122.5788 | 122.4162 | -0.048597 | 122.4162 | 122.3839 | -0.03235 | -0.077484 | -0.077808 | -0.1774 | -0.1261 | 122.343 | 0.15305 | 0.33045 | -0.077866 | -0.005986 | 122.3483 | 122.3194 | 122.319 | 122.4074 | 0.019362 | 122.2707 | 122.319 | 122.3909 | 122.095 | -122.5742
1987.2969 | 122.7127 | -122.438 | -0.004578 | -0.02068 | -0.062779 | 0.063108 | -0.012793 | -0.0080829 | 0.0063095 | -0.011751 | -0.0017945 | -0.0018716 | -0.0062963 | 0.024476 | -0.012022 | 0.014783 | -0.003172 | -0.017566 | -0.044018 | -0.077483 | -0.086964 | 0.019363 | -0.063054 | -0.32015 | -122.2392 | -0.13068 | -0.087023 | -0.010564 | -122.5742 | 122.4574 | -0.03944 | 122.4528 | 122.4205 | -0.036929 | -0.072905 | -0.082386 | -0.1362 | -0.1261 | 122.375 | 0.19883 | 0.33502 | -0.082445 | -0.005986 | 122.394 | 122.3606 | 122.3511 | 122.4349 | 0.023941 | 122.3074 | 122.351 | 122.4275 | 122.1179 | -122.5697
1989 | 122.5708 | -122.4472 | 0.027466 | -0.013049 | -0.062566 | 0.063321 | -0.012579 | -0.0080829 | 0.0063095 | -0.011751 | -0.0015809 | -0.0020852 | -0.0058689 | 0.024476 | -0.012236 | 0.005626 | -0.003172 | -0.017566 | -0.044018 | -0.082062 | -0.086964 | 0.023942 | -0.067633 | -0.32015 | -122.2438 | -0.13526 | -0.091601 | -0.010564 | -122.5788 | 122.4711 | -0.071484 | 122.4528 | 122.4296 | -0.041508 | -0.10953 | -0.11443 | -0.13162 | -0.16273 | 122.3796 | 0.2034 | 0.33502 | -0.11907 | -0.03803 | 122.4032 | 122.3651 | 122.3602 | 122.444 | -0.003524 | 122.3119 | 122.3556 | 122.4366 | 122.1271 | -122.6063
1990.7188 | 122.5937 | -122.4747 | 0.032043 | -0.013049 | -0.062993 | 0.063108 | -0.012366 | -0.0076555 | 0.0063095 | -0.011751 | -0.0017945 | -0.0020852 | -0.0060825 | 0.024904 | -0.011809 | 0.005626 | -0.007751 | -0.022144 | -0.044018 | -0.082062 | -0.086964 | 0.014784 | -0.063054 | -0.32015 | -122.2484 | -0.13526 | -0.087023 | -0.010564 | -122.5788 | 122.4895 | -0.076061 | 122.4803 | 122.4525 | -0.036928 | -0.1141 | -0.11901 | -0.10416 | -0.1673 | 122.4116 | 0.22629 | 0.33045 | -0.11907 | -0.042607 | 122.4307 | 122.3926 | 122.3877 | 122.4669 | -0.017259 | 122.3394 | 122.3876 | 122.4641 | 122.1545 | -122.6109
1992.4062 | 122.6669 | -122.4426 | 0 | -0.013049 | -0.062566 | 0.062894 | -0.012579 | -0.0080829 | 0.0060959 | -0.011751 | -0.0017945 | -0.001658 | -0.0060825 | 0.024476 | -0.011809 | 0.010204 | -0.003172 | -0.012988 | -0.048597 | -0.072904 | -0.086964 | 0.019363 | -0.072212 | -0.31557 | -122.2484 | -0.13068 | -0.082444 | -0.010564 | -122.5788 | 122.462 | -0.048597 | 122.4528 | 122.4296 | -0.032351 | -0.072904 | -0.086964 | -0.1362 | -0.13068 | 122.3704 | 0.19425 | 0.33045 | -0.082444 | -0.010564 | 122.394 | 122.3697 | 122.3557 | 122.4395 | 0.019363 | 122.3119 | 122.3602 | 122.4321 | 122.1271 | -122.5788
1994.0781 | 122.644 | -122.4518 | 0.022888 | -0.005418 | -0.062779 | 0.062894 | -0.012579 | -0.0080829 | 0.0063095 | -0.0041205 | -0.0017945 | -0.001658 | -0.0062963 | 0.024904 | -0.012022 | 0.010204 | -0.003172 | -0.022144 | -0.044018 | -0.082062 | -0.086964 | 0.014784 | -0.072212 | -0.32473 | -122.2484 | -0.1261 | -0.082444 | -0.005985 | -122.5788 | 122.4666 | -0.066906 | 122.462 | 122.4296 | -0.036928 | -0.10495 | -0.10985 | -0.12704 | -0.14899 | 122.3796 | 0.2034 | 0.33045 | -0.10533 | -0.028873 | 122.4078 | 122.3697 | 122.3648 | 122.4486 | -0.008104 | 122.3257 | 122.3693 | 122.4458 | 122.1271 | -122.6017
1995.7656 | 122.7219 | -122.4289 | 0.004578 | -0.005418 | -0.062779 | 0.062894 | -0.012579 | -0.0080829 | 0.0065231 | -0.011751 | -0.0015809 | -0.0018716 | -0.0062963 | 0.02469 | -0.012022 | 0.005626 | -0.003172 | -0.012988 | -0.053175 | -0.082062 | -0.086964 | 0.019363 | -0.058476 | -0.32015 | -122.2438 | -0.13068 | -0.087023 | -0.005985 | -122.5788 | 122.4483 | -0.057753 | 122.4345 | 122.4159 | -0.032351 | -0.08664 | -0.091542 | -0.14993 | -0.13526 | 122.3704 | 0.18509 | 0.33502 | -0.091601 | -0.010563 | 122.3757 | 122.3468 | 122.3419 | 122.4257 | 0.014785 | 122.2982 | 122.3419 | 122.4229 | 122.1087 | -122.5834
1997.4531 | 122.6486 | -122.4701 | 0.018311 | 0.002213 | -0.062566 | 0.063321 | -0.012793 | -0.0078693 | 0.0063095 | -0.0041205 | -0.0015809 | -0.0018716 | -0.0060825 | 0.02469 | -0.012236 | 0.005626 | -0.003172 | -0.017566 | -0.048597 | -0.09122 | -0.082386 | 0.019363 | -0.067633 | -0.32931 | -122.2438 | -0.13068 | -0.082444 | -0.015142 | -122.5788 | 122.4895 | -0.066908 | 122.4757 | 122.4525 | -0.036929 | -0.10953 | -0.1007 | -0.10873 | -0.14899 | 122.4025 | 0.22629 | 0.33502 | -0.10076 | -0.033453 | 122.4215 | 122.3789 | 122.3877 | 122.4669 | 0.001052 | 122.3394 | 122.3876 | 122.455 | 122.1408 | -122.5971
1999.1406 | 122.7264 | -122.4335 | -0.018311 | -0.005418 | -0.062779 | 0.062894 | -0.012579 | -0.0078693 | 0.0060959 | -0.0041205 | -0.0020083 | -0.001658 | -0.0062963 | 0.024904 | -0.012236 | 0.014783 | -0.003172 | -0.012988 | -0.048597 | -0.086641 | -0.082386 | 0.019363 | -0.067633 | -0.31557 | -122.2438 | -0.13984 | -0.082444 | -0.015142 | -122.5834 | 122.4528 | -0.030286 | 122.4483 | 122.4205 | -0.032351 | -0.06833 | -0.064075 | -0.14993 | -0.12153 | 122.3658 | 0.18967 | 0.3396 | -0.064133 | 0.003169 | 122.3849 | 122.3468 | 122.3511 | 122.4303 | 0.037674 | 122.2936 | 122.351 | 122.4183 | 122.1179 | -122.5651
2000.8594 | 122.7448 | -122.4518 | 0 | 0.002213 | -0.062779 | 0.063321 | -0.012366 | -0.0076555 | 0.0060959 | -0.011751 | -0.0015809 | -0.001658 | -0.0060825 | 0.024904 | -0.011809 | 0.001048 | 0.001407 | -0.008409 | -0.048597 | -0.077483 | -0.082386 | 0.014784 | -0.063054 | -0.32015 | -122.2484 | -0.13984 | -0.087023 | -0.015142 | -122.5834 | 122.4666 | -0.048597 | 122.4528 | 122.4434 | -0.023193 | -0.077483 | -0.082386 | -0.13162 | -0.13984 | 122.3887 | 0.2034 | 0.33502 | -0.087023 | -0.015142 | 122.4032 | 122.3743 | 122.3694 | 122.4532 | 0.014784 | 122.3119 | 122.3648 | 122.4366 | 122.1316 | -122.5834
2002.5469 | 122.6349 | -122.4655 | 0.009155 | -0.005418 | -0.062779 | 0.063108 | -0.012579 | -0.0080829 | 0.0063095 | -0.027012 | -0.0013673 | -0.0020852 | -0.0058689 | 0.02469 | -0.012022 | 0.010204 | -0.003172 | -0.022144 | -0.048597 | -0.082062 | -0.086964 | 0.019363 | -0.063054 | -0.32473 | -122.2575 | -0.13068 | -0.077866 | -0.001407 | -122.5926 | 122.4849 | -0.057752 | 122.4757 | 122.4434 | -0.041507 | -0.091217 | -0.096119 | -0.12705 | -0.13984 | 122.4025 | 0.20798 | 0.33503 | -0.087021 | -0.010562 | 122.4169 | 122.3835 | 122.3786 | 122.4623 | 0.010208 | 122.3348 | 122.3876 | 122.4641 | 122.1408 | -122.6017
2004.2344 | 122.6761 | -122.4564 | 0.009155 | -0.013049 | -0.062779 | 0.063108 | -0.012152 | -0.0078693 | 0.0063095 | -0.019381 | -0.0017945 | -0.0018716 | -0.0065099 | 0.024904 | -0.012022 | 0.010204 | -0.003172 | -0.012988 | -0.053175 | -0.086641 | -0.086964 | 0.019363 | -0.072212 | -0.32473 | -122.2438 | -0.13068 | -0.077866 | -0.005985 | -122.5788 | 122.4757 | -0.06233 | 122.4666 | 122.4434 | -0.032351 | -0.095796 | -0.096119 | -0.12247 | -0.13984 | 122.3841 | 0.21256 | 0.33502 | -0.087021 | -0.01514 | 122.4032 | 122.3697 | 122.3694 | 122.4532 | 0.010208 | 122.3257 | 122.3785 | 122.4504 | 122.1316 | -122.588
2005.9844 | 122.7081 | -122.4243 | 0.009155 | -0.005418 | -0.062993 | 0.063108 | -0.012793 | -0.0082965 | 0.0060959 | -0.019381 | -0.0015809 | -0.001658 | -0.0062963 | 0.02469 | -0.012236 | 0.005626 | 0.001407 | -0.012988 | -0.048597 | -0.072904 | -0.077807 | 0.019363 | -0.067633 | -0.33389 | -122.2575 | -0.13068 | -0.087023 | -0.005985 | -122.5926 | 122.4437 | -0.057752 | 122.4299 | 122.4113 | -0.032351 | -0.082059 | -0.086962 | -0.16825 | -0.13984 | 122.3567 | 0.16678 | 0.33503 | -0.096178 | -0.01514 | 122.3757 | 122.3514 | 122.3465 | 122.4257 | 0.010208 | 122.2936 | 122.3373 | 122.4183 | 122.0904 | -122.6017
2007.6719 | 122.644 | -122.4747 | 0.036621 | -0.005418 | -0.062993 | 0.063321 | -0.012579 | -0.0078693 | 0.0063095 | -0.0041205 | -0.0020083 | -0.0018716 | -0.0062963 | 0.024904 | -0.012236 | 0.010204 | 0.005985 | -0.012988 | -0.048597 | -0.077483 | -0.086964 | 0.014784 | -0.067633 | -0.32931 | -122.2484 | -0.13526 | -0.082444 | -0.005985 | -122.588 | 122.4895 | -0.085218 | 122.4849 | 122.4617 | -0.027772 | -0.1141 | -0.12359 | -0.11331 | -0.17188 | 122.407 | 0.22629 | 0.3396 | -0.11907 | -0.042606 | 122.4261 | 122.3972 | 122.3877 | 122.4807 | -0.021837 | 122.3394 | 122.3922 | 122.4687 | 122.1454 | -122.6246
2009.375 | 122.6761 | -122.4426 | 0.004578 | -0.013049 | -0.062779 | 0.063321 | -0.012579 | -0.0080829 | 0.0058821 | -0.019381 | -0.0013673 | -0.0018716 | -0.0062963 | 0.025117 | -0.011809 | 0.010204 | -0.003172 | -0.017566 | -0.048597 | -0.072904 | -0.086964 | 0.028521 | -0.072212 | -0.32931 | -122.2575 | -0.13068 | -0.077866 | -0.010564 | -122.588 | 122.4711 | -0.053175 | 122.4528 | 122.4251 | -0.046087 | -0.077482 | -0.091542 | -0.14536 | -0.13526 | 122.3704 | 0.18509 | 0.33045 | -0.082444 | -0.015142 | 122.394 | 122.3697 | 122.3557 | 122.4395 | 0.023943 | 122.3119 | 122.3648 | 122.4321 | 122.1133 | -122.5926
2011.1094 | 122.6761 | -122.438 | 0.018311 | -0.02068 | -0.063207 | 0.062894 | -0.012793 | -0.0080829 | 0.0063095 | -0.0041205 | -0.0017945 | -0.001658 | -0.0060825 | 0.02469 | -0.011595 | 0.010204 | 0.001407 | -0.017566 | -0.048597 | -0.077483 | -0.082386 | 0.023942 | -0.072212 | -0.32015 | -122.2575 | -0.13068 | -0.087023 | -0.010564 | -122.588 | 122.462 | -0.066908 | 122.4483 | 122.4205 | -0.041508 | -0.095794 | -0.1007 | -0.14993 | -0.14899 | 122.3658 | 0.18051 | 0.33045 | -0.10533 | -0.028875 | 122.3895 | 122.3606 | 122.3557 | 122.4395 | 0.005631 | 122.3074 | 122.351 | 122.4275 | 122.1179 | -122.6063
2012.8125 | 122.5983 | -122.4838 | 0.022888 | -0.013049 | -0.062993 | 0.062894 | -0.012793 | -0.0080829 | 0.0063095 | -0.019381 | -0.0020083 | -0.001658 | -0.0065099 | 0.02469 | -0.012022 | 0.005626 | -0.003172 | -0.012988 | -0.053175 | -0.082062 | -0.086964 | 0.019363 | -0.072212 | -0.33389 | -122.2575 | -0.13526 | -0.087023 | -0.010564 | -122.5926 | 122.5032 | -0.076063 | 122.4895 | 122.4708 | -0.032351 | -0.10495 | -0.10985 | -0.10874 | -0.15815 | 122.4116 | 0.22629 | 0.33503 | -0.10991 | -0.033452 | 122.4307 | 122.4018 | 122.3969 | 122.4807 | -0.003525 | 122.3486 | 122.3968 | 122.4733 | 122.1499 | -122.6155
2014.5469 | 122.7264 | -122.4289 | -0.009155 | -0.013049 | -0.062779 | 0.062894 | -0.012579 | -0.0082965 | 0.0060959 | -0.011751 | -0.0017945 | -0.0018716 | -0.0058689 | 0.024904 | -0.012022 | 0.014783 | 0.001407 | -0.012988 | -0.048597 | -0.077483 | -0.082386 | 0.023942 | -0.063054 | -0.32931 | -122.2484 | -0.13068 | -0.082444 | -0.005985 | -122.588 | 122.4528 | -0.039442 | 122.4437 | 122.4159 | -0.03693 | -0.068328 | -0.073231 | -0.15909 | -0.12153 | 122.3658 | 0.18051 | 0.3396 | -0.073289 | 0.00317 | 122.3803 | 122.3514 | 122.3465 | 122.4303 | 0.033097 | 122.2982 | 122.3465 | 122.4229 | 122.0996 | -122.5788
2016.2344 | 122.7081 | -122.4426 | 0.009155 | -0.013049 | -0.062993 | 0.063108 | -0.012152 | -0.0076555 | 0.0060959 | -0.019381 | -0.0013673 | -0.0020852 | -0.0062963 | 0.02469 | -0.012022 | 0.010204 | 0.001407 | -0.012988 | -0.048597 | -0.077483 | -0.086964 | 0.028521 | -0.072212 | -0.33847 | -122.2575 | -0.13526 | -0.082444 | -0.010564 | -122.5926 | 122.4711 | -0.057752 | 122.4528 | 122.4296 | -0.041509 | -0.086638 | -0.096119 | -0.14994 | -0.14441 | 122.3704 | 0.18509 | 0.33503 | -0.091599 | -0.019719 | 122.394 | 122.3651 | 122.3557 | 122.444 | 0.019366 | 122.3074 | 122.3602 | 122.4321 | 122.1042 | -122.6017
2018 | 122.6074 | -122.4976 | 0.013733 | -0.013049 | -0.062993 | 0.06268 | -0.012366 | -0.0080829 | 0.0063095 | -0.019381 | -0.0015809 | -0.0014444 | -0.0062963 | 0.025117 | -0.012022 | 0.010204 | 0.001407 | -0.012988 | -0.044018 | -0.077483 | -0.077807 | 0.014784 | -0.072212 | -0.33389 | -122.253 | -0.13068 | -0.077866 | -0.015142 | -122.5971 | 122.5123 | -0.057751 | 122.5078 | 122.4846 | -0.027772 | -0.091216 | -0.09154 | -0.099583 | -0.14441 | 122.4253 | 0.2446 | 0.34418 | -0.091599 | -0.028875 | 122.4535 | 122.4201 | 122.4198 | 122.499 | 0.001051 | 122.3669 | 122.4197 | 122.4824 | 122.1637 | -122.6109
2019.6875 | 122.6532 | -122.4792 | 0.004578 | 0.002213 | -0.06342 | 0.06268 | -0.012793 | -0.0078693 | 0.0063095 | -0.019381 | -0.0020083 | -0.0014444 | -0.0062963 | 0.025117 | -0.012236 | 0.010204 | 0.001407 | -0.017566 | -0.044018 | -0.086641 | -0.082386 | 0.023942 | -0.081369 | -0.32931 | -122.2575 | -0.13984 | -0.077866 | -0.005985 | -122.6017 | 122.5032 | -0.048596 | 122.4895 | 122.4617 | -0.041508 | -0.091219 | -0.086964 | -0.12247 | -0.14442 | 122.3979 | 0.22171 | 0.34418 | -0.082444 | -0.010563 | 122.4352 | 122.3926 | 122.3969 | 122.4807 | 0.019364 | 122.3394 | 122.4014 | 122.4733 | 122.1499 | -122.6063
2021.3906 | 122.7219 | -122.4289 | -0.009155 | -0.005418 | -0.063207 | 0.063321 | -0.012366 | -0.0082965 | 0.0063095 | -0.019381 | -0.0013673 | -0.0020852 | -0.0065099 | 0.025117 | -0.012236 | 0.010204 | -0.003172 | -0.022144 | -0.048597 | -0.09122 | -0.073228 | 0.019363 | -0.072212 | -0.34304 | -122.2575 | -0.13068 | -0.087023 | -0.010564 | -122.5971 | 122.4483 | -0.039442 | 122.4391 | 122.4068 | -0.041507 | -0.082065 | -0.064073 | -0.16825 | -0.12153 | 122.3567 | 0.17136 | 0.3396 | -0.077868 | -0.001409 | 122.3803 | 122.3377 | 122.3557 | 122.4257 | 0.028518 | 122.2982 | 122.3419 | 122.4183 | 122.0858 | -122.588
2023.125 | 122.7402 | -122.4335 | 0.018311 | -0.02068 | -0.062993 | 0.063321 | -0.012579 | -0.0082965 | 0.0060959 | -0.011751 | -0.0017945 | -0.0020852 | -0.0065099 | 0.024904 | -0.012236 | 0.010204 | -0.007751 | -0.017566 | -0.048597 | -0.082062 | -0.082386 | 0.019363 | -0.072212 | -0.33389 | -122.2667 | -0.13526 | -0.082444 | -0.010564 | -122.6017 | 122.4528 | -0.066908 | 122.4437 | 122.4159 | -0.036929 | -0.10037 | -0.1007 | -0.16825 | -0.15357 | 122.3613 | 0.16678 | 0.33503 | -0.10076 | -0.028875 | 122.3849 | 122.3514 | 122.3511 | 122.4257 | 0.001052 | 122.2982 | 122.351 | 122.4229 | 122.0996 | -122.62
2024.8125 | 122.6074 | -122.4976 | 0.036621 | 0.002213 | -0.062779 | 0.062894 | -0.012152 | -0.0080829 | 0.0065231 | -0.011751 | -0.0015809 | -0.0020852 | -0.0062963 | 0.024476 | -0.012236 | 0.014783 | 0.001407 | -0.017566 | -0.053175 | -0.077483 | -0.082386 | 0.014784 | -0.072212 | -0.34304 | -122.253 | -0.13068 | -0.077866 | -0.001407 | -122.5971 | 122.5123 | -0.089796 | 122.5123 | 122.48 | -0.03235 | -0.1141 | -0.11901 | -0.099583 | -0.1673 | 122.4253 | 0.2446 | 0.34418 | -0.11449 | -0.038028 | 122.4444 | 122.4201 | 122.4152 | 122.499 | -0.021837 | 122.3669 | 122.4197 | 122.4962 | 122.1545 | -122.6338
2026.5156 | 122.6898 | -122.4518 | 0.013733 | -0.005418 | -0.062993 | 0.062894 | -0.012579 | -0.0078693 | 0.0063095 | -0.019381 | -0.0020083 | -0.0018716 | -0.0062963 | 0.02469 | -0.012236 | 0.005626 | -0.003172 | -0.012988 | -0.044018 | -0.077483 | -0.082386 | 0.019363 | -0.072212 | -0.34304 | -122.2667 | -0.13068 | -0.06413 | -0.010564 | -122.6017 | 122.4711 | -0.057751 | 122.4574 | 122.4388 | -0.032351 | -0.091216 | -0.096119 | -0.14994 | -0.14441 | 122.3796 | 0.18509 | 0.33503 | -0.077863 | -0.024297 | 122.4078 | 122.3743 | 122.3694 | 122.4486 | 0.00563 | 122.3211 | 122.3877 | 122.4412 | 122.1087 | -122.6155
2028.2188 | 122.7676 | -122.4609 | 0.004578 | -0.005418 | -0.063207 | 0.06268 | -0.012793 | -0.0082965 | 0.0058821 | -0.011751 | -0.0017945 | -0.0018716 | -0.0062963 | 0.025117 | -0.012022 | 0.005626 | 0.001407 | -0.022144 | -0.044018 | -0.082062 | -0.082386 | 0.019363 | -0.07679 | -0.33847 | -122.2713 | -0.1261 | -0.077866 | -0.010564 | -122.5971 | 122.4803 | -0.048596 | 122.4666 | 122.4388 | -0.041507 | -0.08664 | -0.086964 | -0.13621 | -0.13068 | 122.3841 | 0.18966 | 0.32587 | -0.082444 | -0.015142 | 122.4169 | 122.3789 | 122.3786 | 122.4623 | 0.014785 | 122.3348 | 122.3831 | 122.4504 | 122.1225 | -122.6017
2029.9531 | 122.7356 | -122.4472 | 0.004578 | -0.005418 | -0.06342 | 0.062467 | -0.012366 | -0.0080829 | 0.0065231 | -0.011751 | -0.0017945 | -0.001658 | -0.0067235 | 0.025117 | -0.012022 | 0.010204 | -0.007751 | -0.022144 | -0.048597 | -0.077483 | -0.082386 | 0.023942 | -0.072212 | -0.34304 | -122.2621 | -0.13068 | -0.077866 | -0.015142 | -122.5971 | 122.4711 | -0.053175 | 122.4574 | 122.4251 | -0.046086 | -0.082061 | -0.086964 | -0.14994 | -0.13526 | 122.375 | 0.18509 | 0.33503 | -0.082444 | -0.01972 | 122.3986 | 122.3697 | 122.3648 | 122.4395 | 0.019364 | 122.3165 | 122.3693 | 122.4321 | 122.1042 | -122.6017
2031.6406 | 122.7036 | -122.4838 | 0.036621 | -0.02068 | -0.063207 | 0.062894 | -0.012366 | -0.0082965 | 0.0060959 | -0.019381 | -0.0015809 | -0.0018716 | -0.0058689 | 0.024904 | -0.012022 | 0.005626 | -0.007751 | -0.017566 | -0.044018 | -0.077483 | -0.077807 | 0.019363 | -0.072212 | -0.34762 | -122.2621 | -0.13984 | -0.082444 | -0.010564 | -122.6017 | 122.5032 | -0.080639 | 122.4895 | 122.4663 | -0.036929 | -0.1141 | -0.11443 | -0.1179 | -0.17646 | 122.4116 | 0.22171 | 0.3396 | -0.11907 | -0.047185 | 122.4398 | 122.4063 | 122.406 | 122.4761 | -0.017258 | 122.344 | 122.4014 | 122.4733 | 122.1362 | -122.6383
2033.3594 | 122.6944 | -122.4335 | 0.022888 | -0.013049 | -0.063207 | 0.062894 | -0.012366 | -0.0080829 | 0.0063095 | -0.011751 | -0.0015809 | -0.001658 | -0.0060825 | 0.024904 | -0.012236 | 0.005626 | -0.003172 | -0.026723 | -0.044018 | -0.077483 | -0.082386 | 0.014784 | -0.081369 | -0.3522 | -122.2713 | -0.13068 | -0.073287 | -0.010564 | -122.6063 | 122.4483 | -0.066906 | 122.4391 | 122.4067 | -0.041507 | -0.10037 | -0.10527 | -0.17283 | -0.15357 | 122.3521 | 0.1622 | 0.33502 | -0.096175 | -0.033452 | 122.3895 | 122.356 | 122.3511 | 122.4303 | -0.008104 | 122.3028 | 122.3602 | 122.4229 | 122.0813 | -122.6292
2035.0469 | 122.644 | -122.4792 | 0.013733 | -0.013049 | -0.063207 | 0.063535 | -0.012366 | -0.0080829 | 0.0060959 | -0.011751 | -0.0017945 | -0.001658 | -0.0065099 | 0.025117 | -0.012022 | 0.014783 | 0.005985 | -0.017566 | -0.053175 | -0.077483 | -0.082386 | 0.023942 | -0.081369 | -0.34762 | -122.2621 | -0.13526 | -0.073287 | -0.005985 | -122.5971 | 122.5032 | -0.066908 | 122.494 | 122.4617 | -0.041508 | -0.091216 | -0.096119 | -0.11789 | -0.14899 | 122.3979 | 0.21713 | 0.33503 | -0.08702 | -0.019718 | 122.4261 | 122.4018 | 122.3969 | 122.4852 | 0.010209 | 122.344 | 122.406 | 122.4733 | 122.1316 | -122.6109
2036.7188 | 122.731 | -122.4472 | 0.004578 | -0.005418 | -0.06342 | 0.06268 | -0.012579 | -0.0080829 | 0.0060959 | -0.019381 | -0.0015809 | -0.0018716 | -0.0062963 | 0.025117 | -0.011809 | 0.005626 | 0.001407 | -0.026723 | -0.048597 | -0.077483 | -0.082386 | 0.014784 | -0.07679 | -0.34762 | -122.2667 | -0.13068 | -0.073287 | -0.001407 | -122.6063 | 122.462 | -0.053175 | 122.4528 | 122.4205 | -0.041507 | -0.082061 | -0.086964 | -0.15909 | -0.13526 | 122.3704 | 0.18051 | 0.3396 | -0.077865 | -0.005985 | 122.3986 | 122.3697 | 122.3648 | 122.4486 | 0.010206 | 122.3165 | 122.3739 | 122.4458 | 122.0996 | -122.6109
2038.4688 | 122.7585 | -122.4701 | 0.009155 | -0.013049 | -0.063207 | 0.062894 | -0.012366 | -0.0080829 | 0.0058821 | -0.0041205 | -0.0015809 | -0.0018716 | -0.0060825 | 0.025117 | -0.012022 | 0.010204 | 0.005985 | -0.017566 | -0.048597 | -0.077483 | -0.077807 | 0.019363 | -0.072212 | -0.3522 | -122.2713 | -0.1261 | -0.077866 | -0.010564 | -122.6063 | 122.4895 | -0.057752 | 122.4803 | 122.4525 | -0.036929 | -0.086638 | -0.086962 | -0.13621 | -0.13526 | 122.3979 | 0.19882 | 0.33502 | -0.087021 | -0.019719 | 122.4215 | 122.3926 | 122.3923 | 122.4761 | 0.010208 | 122.344 | 122.3922 | 122.4595 | 122.1179 | -122.6155
2040.25 | 122.7402 | -122.4564 | 0.013733 | 0.002213 | -0.063207 | 0.06268 | -0.012152 | -0.0080829 | 0.0063095 | -0.011751 | -0.0015809 | -0.0020852 | -0.0065099 | 0.025117 | -0.012022 | 0.014783 | -0.003172 | -0.026723 | -0.053175 | -0.072904 | -0.086964 | 0.019363 | -0.07679 | -0.35678 | -122.2713 | -0.13526 | -0.077866 | -0.010564 | -122.6017 | 122.4757 | -0.066908 | 122.4711 | 122.4296 | -0.046086 | -0.086637 | -0.1007 | -0.14536 | -0.14899 | 122.3796 | 0.18509 | 0.33045 | -0.091599 | -0.024297 | 122.4032 | 122.3835 | 122.3694 | 122.4532 | 0.00563 | 122.3211 | 122.3785 | 122.4458 | 122.0996 | -122.6155
2041.9531 | 122.6761 | -122.4838 | 0.022888 | -0.013049 | -0.062993 | 0.06268 | -0.012366 | -0.0078693 | 0.0063095 | -0.0041205 | -0.0015809 | -0.0018716 | -0.0060825 | 0.024904 | -0.012022 | 0.010204 | -0.007751 | -0.022144 | -0.053175 | -0.077483 | -0.086964 | 0.019363 | -0.07679 | -0.36136 | -122.2713 | -0.13526 | -0.073287 | -0.005985 | -122.6063 | 122.5032 | -0.076063 | 122.494 | 122.4617 | -0.041507 | -0.10037 | -0.10985 | -0.12247 | -0.15815 | 122.407 | 0.21255 | 0.33502 | -0.096175 | -0.028873 | 122.4307 | 122.4063 | 122.3969 | 122.4761 | -0.003525 | 122.3486 | 122.4105 | 122.4778 | 122.1225 | -122.6292
2043.7031 | 122.6166 | -122.5159 | 0.027466 | 0.002213 | -0.063207 | 0.06268 | -0.012579 | -0.0082965 | 0.0060959 | -0.019381 | -0.0020083 | -0.0020852 | -0.0062963 | 0.025117 | -0.012236 | 0.010204 | 0.005985 | -0.017566 | -0.03944 | -0.077483 | -0.073228 | 0.019363 | -0.07679 | -0.34762 | -122.2759 | -0.13526 | -0.073287 | -0.005985 | -122.6063 | 122.5352 | -0.066906 | 122.5261 | 122.4983 | -0.036929 | -0.10495 | -0.10069 | -0.09043 | -0.16273 | 122.4391 | 0.24002 | 0.33045 | -0.10075 | -0.033451 | 122.4764 | 122.4384 | 122.4426 | 122.5219 | -0.008103 | 122.3806 | 122.4426 | 122.5099 | 122.1682 | -122.6338
2045.4531 | 122.6944 | -122.4701 | -0.009155 | -0.005418 | -0.063207 | 0.062894 | -0.012366 | -0.0080829 | 0.0060959 | -0.011751 | -0.0017945 | -0.0018716 | -0.0062963 | 0.025331 | -0.012236 | 0.010204 | 0.005985 | -0.022144 | -0.03944 | -0.082062 | -0.082386 | 0.019363 | -0.07679 | -0.3522 | -122.2804 | -0.13068 | -0.082444 | -0.010564 | -122.6109 | 122.4895 | -0.030285 | 122.4803 | 122.4479 | -0.041507 | -0.072907 | -0.073231 | -0.14078 | -0.12153 | 122.3933 | 0.18966 | 0.33045 | -0.073289 | -0.001409 | 122.4307 | 122.388 | 122.3877 | 122.4761 | 0.028518 | 122.3394 | 122.3876 | 122.4595 | 122.1179 | -122.6017
2047.1406 | 122.7493 | -122.4655 | 0.013733 | -0.005418 | -0.063207 | 0.062467 | -0.012579 | -0.0080829 | 0.0060959 | -0.011751 | -0.0017945 | -0.0018716 | -0.0067235 | 0.025331 | -0.012236 | 0.005626 | 0.001407 | -0.017566 | -0.048597 | -0.082062 | -0.086964 | 0.019363 | -0.081369 | -0.35678 | -122.2759 | -0.13526 | -0.082444 | -0.005985 | -122.6155 | 122.4849 | -0.06233 | 122.4711 | 122.4479 | -0.036929 | -0.095795 | -0.1007 | -0.14994 | -0.14899 | 122.3841 | 0.18966 | 0.3396 | -0.096177 | -0.019718 | 122.4169 | 122.3835 | 122.3786 | 122.4669 | 0.00563 | 122.3303 | 122.3831 | 122.4595 | 122.1087 | -122.6292
2048.875 | 122.6212 | -122.5204 | 0.027466 | -0.013049 | -0.063207 | 0.062467 | -0.012579 | -0.0082965 | 0.0060959 | -0.011751 | -0.0015809 | -0.001658 | -0.0062963 | 0.024904 | -0.01245 | 0.014783 | 0.001407 | -0.017566 | -0.044018 | -0.077483 | -0.077807 | 0.019363 | -0.081369 | -0.35678 | -122.2759 | -0.13068 | -0.077866 | -0.001407 | -122.6109 | 122.5398 | -0.071484 | 122.5352 | 122.5029 | -0.036929 | -0.10495 | -0.10527 | -0.090431 | -0.15815 | 122.4391 | 0.24459 | 0.33503 | -0.10533 | -0.028873 | 122.4764 | 122.443 | 122.4426 | 122.5219 | -0.008103 | 122.3898 | 122.4426 | 122.519 | 122.1637 | -122.6383
2050.625 | 122.6578 | -122.4701 | 0.013733 | -0.013049 | -0.06342 | 0.062894 | -0.012366 | -0.0082965 | 0.0058821 | -0.011751 | -0.0017945 | -0.0018716 | -0.0060825 | 0.025331 | -0.011809 | 0.005626 | 0.005985 | -0.008409 | -0.044018 | -0.077483 | -0.073228 | 0.019363 | -0.07679 | -0.36136 | -122.2759 | -0.13526 | -0.073287 | -0.005985 | -122.62 | 122.4895 | -0.057751 | 122.4757 | 122.4617 | -0.027772 | -0.091216 | -0.086961 | -0.14994 | -0.14899 | 122.3933 | 0.19424 | 0.34418 | -0.08702 | -0.019718 | 122.4261 | 122.3926 | 122.3969 | 122.4761 | 0.00563 | 122.3348 | 122.3968 | 122.4641 | 122.1087 | -122.6338
2052.375 | 122.6166 | -122.525 | 0.032043 | 0.002213 | -0.063207 | 0.062894 | -0.012579 | -0.0080829 | 0.0058821 | -0.011751 | -0.0015809 | -0.001658 | -0.0062963 | 0.025331 | -0.012022 | 0.005626 | -0.003172 | -0.012988 | -0.048597 | -0.072904 | -0.077807 | 0.014784 | -0.090527 | -0.36136 | -122.2759 | -0.13526 | -0.073287 | -0.001407 | -122.62 | 122.5398 | -0.08064 | 122.5307 | 122.512 | -0.027772 | -0.10495 | -0.10985 | -0.095012 | -0.1673 | 122.4345 | 0.24917 | 0.34418 | -0.10533 | -0.03345 | 122.4764 | 122.4521 | 122.4472 | 122.5219 | -0.017259 | 122.3898 | 122.4517 | 122.5236 | 122.1637 | -122.6521
2054.0469 | 122.6166 | -122.5067 | 0.036621 | -0.013049 | -0.063207 | 0.06268 | -0.012579 | -0.0082965 | 0.0058821 | -0.011751 | -0.0015809 | -0.0018716 | -0.0058689 | 0.024904 | -0.012022 | 0.014783 | 0.010564 | -0.012988 | -0.048597 | -0.077483 | -0.082386 | 0.023942 | -0.07679 | -0.36136 | -122.2759 | -0.13068 | -0.077866 | -0.001407 | -122.6109 | 122.5307 | -0.085218 | 122.5215 | 122.4937 | -0.03693 | -0.1141 | -0.11901 | -0.10416 | -0.1673 | 122.4299 | 0.23086 | 0.33503 | -0.11449 | -0.038028 | 122.4581 | 122.4292 | 122.4243 | 122.5173 | -0.012679 | 122.376 | 122.4288 | 122.5053 | 122.1454 | -122.6475
2055.7812 | 122.6212 | -122.5113 | 0.041199 | 0.002213 | -0.063207 | 0.06268 | -0.012366 | -0.0082965 | 0.0058821 | -0.011751 | -0.0015809 | -0.0020852 | -0.0062963 | 0.025331 | -0.012236 | 0.005626 | 0.001407 | -0.017566 | -0.044018 | -0.082062 | -0.082386 | 0.019363 | -0.085948 | -0.36594 | -122.2804 | -0.13526 | -0.068708 | -0.010564 | -122.6155 | 122.5307 | -0.085217 | 122.5169 | 122.4937 | -0.036929 | -0.12326 | -0.12359 | -0.10417 | -0.17646 | 122.4253 | 0.23086 | 0.33503 | -0.10991 | -0.051763 | 122.4673 | 122.4292 | 122.4289 | 122.5127 | -0.021836 | 122.376 | 122.4426 | 122.5007 | 122.1454 | -122.6567
2057.5312 | 122.6852 | -122.4564 | 0.009155 | -0.013049 | -0.06342 | 0.062467 | -0.012579 | -0.0082965 | 0.0056685 | -0.0041205 | -0.0020083 | -0.001658 | -0.0060825 | 0.025331 | -0.012236 | 0.014783 | 0.001407 | -0.017566 | -0.053175 | -0.082062 | -0.082386 | 0.019363 | -0.072212 | -0.36594 | -122.285 | -0.13068 | -0.077866 | -0.005985 | -122.6109 | 122.4757 | -0.06233 | 122.4711 | 122.4388 | -0.036929 | -0.091217 | -0.091541 | -0.15452 | -0.13984 | 122.3841 | 0.17135 | 0.32587 | -0.087021 | -0.01514 | 122.4032 | 122.3743 | 122.374 | 122.4578 | 0.010208 | 122.3257 | 122.3785 | 122.4504 | 122.0904 | -122.62
2059.2188 | 122.6898 | -122.4701 | 0.027466 | -0.02068 | -0.063634 | 0.06268 | -0.012579 | -0.0082965 | 0.0058821 | -0.027012 | -0.0015809 | -0.0018716 | -0.0065099 | 0.024904 | -0.012022 | 0.010204 | 0.001407 | -0.022144 | -0.03944 | -0.072904 | -0.077807 | 0.019363 | -0.072212 | -0.37052 | -122.2942 | -0.13526 | -0.068708 | -0.005985 | -122.6155 | 122.4895 | -0.066906 | 122.4803 | 122.4479 | -0.041507 | -0.10037 | -0.10527 | -0.14536 | -0.16273 | 122.3979 | 0.17593 | 0.32129 | -0.096174 | -0.033451 | 122.4307 | 122.3972 | 122.3923 | 122.4715 | -0.008103 | 122.3348 | 122.4014 | 122.4641 | 122.0996 | -122.6429
2060.9688 | 122.612 | -122.5021 | 0.022888 | -0.013049 | -0.063634 | 0.062467 | -0.012579 | -0.0082965 | 0.0060959 | -0.019381 | -0.0013673 | -0.0018716 | -0.0062963 | 0.025331 | -0.012236 | 0.010204 | 0.005985 | -0.017566 | -0.048597 | -0.077483 | -0.073228 | 0.014784 | -0.081369 | -0.37052 | -122.285 | -0.13526 | -0.077866 | -0.015142 | -122.62 | 122.5169 | -0.071485 | 122.5123 | 122.4846 | -0.03235 | -0.10037 | -0.096116 | -0.1179 | -0.15815 | 122.4208 | 0.21712 | 0.33503 | -0.10075 | -0.03803 | 122.4535 | 122.4247 | 122.4289 | 122.5081 | -0.008104 | 122.3669 | 122.4243 | 122.487 | 122.1316 | -122.6429
2062.7188 | 122.644 | -122.5021 | 0.045776 | -0.02068 | -0.06342 | 0.06268 | -0.012366 | -0.0082965 | 0.0058821 | -0.0041205 | -0.0017945 | -0.0020852 | -0.0060825 | 0.025331 | -0.012022 | 0.010204 | -0.007751 | -0.008409 | -0.053175 | -0.077483 | -0.082386 | 0.019363 | -0.081369 | -0.36594 | -122.285 | -0.13526 | -0.082444 | -0.005985 | -122.6155 | 122.5215 | -0.098951 | 122.5123 | 122.4937 | -0.027772 | -0.12326 | -0.12816 | -0.11332 | -0.18104 | 122.4208 | 0.21712 | 0.33045 | -0.12822 | -0.051761 | 122.449 | 122.4247 | 122.4197 | 122.4944 | -0.026413 | 122.3669 | 122.4197 | 122.4962 | 122.1362 | -122.6612
2064.4688 | 122.6166 | -122.4976 | 0.036621 | -0.005418 | -0.063634 | 0.062467 | -0.012579 | -0.0082965 | 0.0060959 | -0.019381 | -0.0015809 | -0.001658 | -0.0062963 | 0.025117 | -0.012022 | 0.010204 | 0.005985 | -0.012988 | -0.048597 | -0.077483 | -0.073228 | 0.028521 | -0.085948 | -0.36594 | -122.285 | -0.13526 | -0.082444 | -0.005985 | -122.62 | 122.5261 | -0.085218 | 122.5078 | 122.4846 | -0.041509 | -0.1141 | -0.10985 | -0.12248 | -0.17188 | 122.4116 | 0.21255 | 0.33503 | -0.11907 | -0.042606 | 122.449 | 122.4201 | 122.4243 | 122.5035 | -0.0081 | 122.3623 | 122.4151 | 122.4916 | 122.1316 | -122.6567
2066.1406 | 122.7631 | -122.4609 | 0.009155 | -0.013049 | -0.063634 | 0.062467 | -0.012366 | -0.0080829 | 0.0060959 | -0.011751 | -0.0013673 | -0.001658 | -0.0065099 | 0.025117 | -0.012236 | 0.001048 | -0.003172 | -0.008409 | -0.048597 | -0.077483 | -0.077807 | 0.0331 | -0.085948 | -0.37052 | -122.2896 | -0.13526 | -0.068708 | -0.015142 | -122.6292 | 122.494 | -0.057752 | 122.462 | 122.4525 | -0.041509 | -0.086638 | -0.086962 | -0.16826 | -0.14441 | 122.375 | 0.17135 | 0.3396 | -0.077863 | -0.024297 | 122.4123 | 122.3835 | 122.3831 | 122.4578 | 0.023945 | 122.3257 | 122.3922 | 122.4458 | 122.0904 | -122.6383
2067.875 | 122.6395 | -122.5021 | 0.041199 | -0.013049 | -0.063634 | 0.06268 | -0.012152 | -0.0078693 | 0.0058821 | -0.011751 | -0.0017945 | -0.0018716 | -0.0058689 | 0.025331 | -0.012022 | 0.010204 | 0.005985 | -0.022144 | -0.057754 | -0.077483 | -0.077807 | 0.019363 | -0.085948 | -0.3751 | -122.2896 | -0.13526 | -0.082444 | -0.005985 | -122.6292 | 122.5215 | -0.098953 | 122.5123 | 122.48 | -0.041507 | -0.11868 | -0.11901 | -0.12706 | -0.17646 | 122.4162 | 0.21255 | 0.3396 | -0.12364 | -0.047184 | 122.4444 | 122.4247 | 122.4243 | 122.5081 | -0.021836 | 122.3669 | 122.4197 | 122.4962 | 122.127 | -122.6704
2069.625 | 122.6349 | -122.5159 | 0.032043 | 0.002213 | -0.063634 | 0.062253 | -0.012579 | -0.0082965 | 0.0058821 | -0.019381 | -0.0017945 | -0.0018716 | -0.0060825 | 0.025545 | -0.011809 | 0.014783 | 0.001407 | -0.017566 | -0.044018 | -0.082062 | -0.077807 | 0.019363 | -0.095105 | -0.37052 | -122.2896 | -0.13526 | -0.073287 | 0.003172 | -122.6246 | 122.5352 | -0.076061 | 122.5307 | 122.4983 | -0.036929 | -0.1141 | -0.10985 | -0.10875 | -0.1673 | 122.4208 | 0.22628 | 0.33503 | -0.10533 | -0.028871 | 122.4719 | 122.4338 | 122.4381 | 122.5173 | -0.01268 | 122.3806 | 122.4426 | 122.519 | 122.1454 | -122.6567
2071.3125 | 122.6761 | -122.4701 | 0.032043 | -0.02068 | -0.063848 | 0.062253 | -0.012366 | -0.0082965 | 0.0054549 | -0.011751 | -0.0015809 | -0.0018716 | -0.0060825 | 0.025331 | -0.012236 | 0.010204 | 0.005985 | -0.017566 | -0.044018 | -0.077483 | -0.073228 | 0.014784 | -0.085948 | -0.37967 | -122.2896 | -0.13984 | -0.082444 | -0.001407 | -122.6292 | 122.4849 | -0.076061 | 122.4803 | 122.4525 | -0.03235 | -0.10953 | -0.10527 | -0.1591 | -0.17188 | 122.3841 | 0.1805 | 0.3396 | -0.11449 | -0.03345 | 122.4261 | 122.3926 | 122.3969 | 122.4761 | -0.017259 | 122.3303 | 122.3876 | 122.4687 | 122.0904 | -122.6612
2073.125 | 122.7173 | -122.4472 | -0.013733 | -0.005418 | -0.06342 | 0.06268 | -0.012366 | -0.0080829 | 0.0058821 | -0.019381 | -0.0015809 | -0.0018716 | -0.0062963 | 0.025331 | -0.01245 | 0.010204 | 0.001407 | -0.012988 | -0.048597 | -0.082062 | -0.077807 | 0.023942 | -0.085948 | -0.3751 | -122.2896 | -0.13526 | -0.082444 | -0.010564 | -122.62 | 122.4711 | -0.034864 | 122.4574 | 122.4342 | -0.03693 | -0.068329 | -0.064074 | -0.17283 | -0.12153 | 122.3613 | 0.15762 | 0.33045 | -0.068711 | 0.003169 | 122.3986 | 122.3651 | 122.3694 | 122.4486 | 0.037675 | 122.3119 | 122.3648 | 122.4366 | 122.0721 | -122.6063
2074.8281 | 122.7859 | -122.4792 | 0.013733 | -0.013049 | -0.063634 | 0.062253 | -0.012579 | -0.0082965 | 0.0060959 | -0.019381 | -0.0017945 | -0.0018716 | -0.0062963 | 0.025331 | -0.012236 | 0.010204 | -0.003172 | -0.017566 | -0.048597 | -0.072904 | -0.077807 | 0.019363 | -0.090527 | -0.38883 | -122.2987 | -0.13068 | -0.082444 | -0.010564 | -122.6292 | 122.4986 | -0.06233 | 122.4895 | 122.4617 | -0.036929 | -0.086637 | -0.09154 | -0.14995 | -0.14441 | 122.3887 | 0.1805 | 0.33045 | -0.096177 | -0.024297 | 122.4307 | 122.4063 | 122.4014 | 122.4761 | 0.00563 | 122.3486 | 122.3968 | 122.4687 | 122.0904 | -122.6429
2076.5469 | 122.6486 | -122.5021 | 0.032043 | 0.002213 | -0.063634 | 0.062467 | -0.012366 | -0.0085103 | 0.0056685 | -0.019381 | -0.0013673 | -0.0020852 | -0.0062963 | 0.025331 | -0.012236 | 0.010204 | -0.003172 | -0.022144 | -0.044018 | -0.072904 | -0.077807 | 0.019363 | -0.099684 | -0.3751 | -122.2942 | -0.13068 | -0.077866 | -0.010564 | -122.6246 | 122.5215 | -0.076061 | 122.5123 | 122.48 | -0.041507 | -0.10495 | -0.10985 | -0.12248 | -0.16272 | 122.4025 | 0.20797 | 0.33045 | -0.10991 | -0.042607 | 122.4581 | 122.4292 | 122.4243 | 122.499 | -0.01268 | 122.3715 | 122.4243 | 122.4916 | 122.127 | -122.6567
2078.2344 | 122.7676 | -122.4518 | 0 | -0.005418 | -0.063634 | 0.062467 | -0.012793 | -0.0085103 | 0.0058821 | -0.0041205 | -0.0015809 | -0.0018716 | -0.0060825 | 0.025331 | -0.01245 | 0.010204 | 0.010564 | -0.017566 | -0.044018 | -0.068325 | -0.082386 | 0.019363 | -0.099684 | -0.38883 | -122.2896 | -0.13068 | -0.082444 | -0.010564 | -122.6384 | 122.4711 | -0.044018 | 122.462 | 122.4342 | -0.036929 | -0.068325 | -0.082386 | -0.18657 | -0.13068 | 122.3521 | 0.16219 | 0.34876 | -0.082444 | -0.010564 | 122.4078 | 122.3835 | 122.3694 | 122.4623 | 0.019363 | 122.3211 | 122.3693 | 122.4412 | 122.063 | -122.6384
2079.9062 | 122.7493 | -122.4564 | 0.013733 | -0.005418 | -0.063634 | 0.062253 | -0.012793 | -0.0082965 | 0.0060959 | -0.019381 | -0.0017945 | -0.0018716 | -0.0062963 | 0.025331 | -0.012236 | 0.014783 | 0.001407 | -0.017566 | -0.053175 | -0.082062 | -0.077807 | 0.023942 | -0.095105 | -0.38425 | -122.2942 | -0.13068 | -0.077866 | 0.003172 | -122.6338 | 122.4803 | -0.066908 | 122.4711 | 122.4388 | -0.041508 | -0.095795 | -0.09154 | -0.17741 | -0.14441 | 122.3613 | 0.16219 | 0.3396 | -0.091599 | -0.010561 | 122.4032 | 122.3743 | 122.3786 | 122.4578 | 0.010209 | 122.3257 | 122.3785 | 122.4595 | 122.0721 | -122.6475
2081.5938 | 122.6807 | -122.493 | 0 | -0.005418 | -0.064275 | 0.062467 | -0.012152 | -0.0080829 | 0.0056685 | -0.011751 | -0.0017945 | -0.0020852 | -0.0065099 | 0.025545 | -0.012022 | 0.014783 | -0.003172 | -0.017566 | -0.048597 | -0.082062 | -0.073228 | 0.014784 | -0.085948 | -0.38425 | -122.2942 | -0.13068 | -0.082444 | -0.005985 | -122.6338 | 122.5078 | -0.048597 | 122.5078 | 122.4754 | -0.03235 | -0.082062 | -0.073228 | -0.14079 | -0.13068 | 122.407 | 0.19881 | 0.3396 | -0.082444 | -0.005985 | 122.4444 | 122.4109 | 122.4198 | 122.4898 | 0.014784 | 122.3623 | 122.4105 | 122.487 | 122.1087 | -122.6338
2083.2812 | 122.7036 | -122.4838 | 0.018311 | 0.002213 | -0.064061 | 0.062467 | -0.012579 | -0.0082965 | 0.0058821 | -0.011751 | -0.0020083 | -0.0018716 | -0.0062963 | 0.025117 | -0.012236 | 0.005626 | 0.001407 | -0.012988 | -0.048597 | -0.077483 | -0.073228 | 0.019363 | -0.085948 | -0.38883 | -122.2987 | -0.1261 | -0.077866 | -0.005985 | -122.6338 | 122.5032 | -0.066908 | 122.4895 | 122.4708 | -0.032351 | -0.095794 | -0.091539 | -0.14995 | -0.14441 | 122.3979 | 0.18508 | 0.33502 | -0.096177 | -0.024296 | 122.4352 | 122.4063 | 122.4106 | 122.4852 | 0.001052 | 122.3577 | 122.406 | 122.4778 | 122.095 | -122.6521
2085 | 122.6807 | -122.4976 | 0.009155 | -0.005418 | -0.063848 | 0.062253 | -0.012579 | -0.0080829 | 0.0058821 | -0.027012 | -0.0015809 | -0.0018716 | -0.0062963 | 0.025545 | -0.012236 | 0.014783 | 0.001407 | -0.017566 | -0.048597 | -0.077483 | -0.073228 | 0.014784 | -0.090527 | -0.39341 | -122.2942 | -0.13526 | -0.082444 | -0.005985 | -122.6292 | 122.5123 | -0.057752 | 122.5123 | 122.48 | -0.03235 | -0.086638 | -0.082383 | -0.13163 | -0.14441 | 122.407 | 0.20339 | 0.33503 | -0.091599 | -0.01514 | 122.449 | 122.4201 | 122.4243 | 122.499 | 0.005629 | 122.3623 | 122.4151 | 122.4916 | 122.1041 | -122.6383
2086.7031 | 122.7768 | -122.4472 | -0.004578 | 0.002213 | -0.063848 | 0.062467 | -0.012579 | -0.0078693 | 0.0056685 | -0.019381 | -0.0017945 | -0.001658 | -0.0060825 | 0.025545 | -0.012022 | 0.010204 | 0.005985 | -0.022144 | -0.053175 | -0.077483 | -0.06865 | 0.023942 | -0.090527 | -0.38883 | -122.2942 | -0.13526 | -0.077866 | -0.010564 | -122.6384 | 122.4711 | -0.048597 | 122.4574 | 122.4251 | -0.046086 | -0.072905 | -0.064072 | -0.19115 | -0.13068 | 122.3567 | 0.15304 | 0.34418 | -0.073288 | -0.005986 | 122.394 | 122.3697 | 122.3786 | 122.4532 | 0.02852 | 122.3119 | 122.3693 | 122.4366 | 122.0584 | -122.6338
2088.4531 | 122.6807 | -122.5113 | 0.018311 | -0.005418 | -0.064061 | 0.062467 | -0.012366 | -0.0080829 | 0.0058821 | -0.0041205 | -0.0017945 | -0.001658 | -0.0065099 | 0.025758 | -0.01245 | 0.005626 | 0.001407 | -0.022144 | -0.044018 | -0.077483 | -0.077807 | 0.019363 | -0.099684 | -0.38883 | -122.2987 | -0.13068 | -0.077866 | -0.001407 | -122.6384 | 122.5307 | -0.062329 | 122.5169 | 122.4891 | -0.041507 | -0.095794 | -0.096118 | -0.12706 | -0.14899 | 122.4116 | 0.21254 | 0.3396 | -0.096177 | -0.019718 | 122.4673 | 122.4338 | 122.4335 | 122.5127 | 0.001052 | 122.3806 | 122.4334 | 122.5099 | 122.1225 | -122.6567
2090.1562 | 122.7493 | -122.4976 | -0.013733 | -0.013049 | -0.063848 | 0.062467 | -0.012793 | -0.0082965 | 0.0060959 | -0.019381 | -0.0017945 | -0.0020852 | -0.0065099 | 0.025545 | -0.01245 | 0.010204 | -0.007751 | -0.022144 | -0.048597 | -0.077483 | -0.073228 | 0.019363 | -0.081369 | -0.39799 | -122.2987 | -0.13526 | -0.077866 | -0.001407 | -122.6429 | 122.5169 | -0.034864 | 122.5078 | 122.4754 | -0.041507 | -0.06375 | -0.059495 | -0.14537 | -0.12153 | 122.4162 | 0.19881 | 0.34418 | -0.064133 | 0.012326 | 122.449 | 122.4201 | 122.4243 | 122.4898 | 0.033096 | 122.3623 | 122.4197 | 122.4962 | 122.0996 | -122.6292
2091.8594 | 122.7539 | -122.4792 | 0.022888 | -0.005418 | -0.064275 | 0.062467 | -0.012579 | -0.0080829 | 0.0058821 | -0.019381 | -0.0013673 | -0.0018716 | -0.0060825 | 0.025331 | -0.012022 | 0.014783 | -0.003172 | -0.017566 | -0.048597 | -0.082062 | -0.077807 | 0.014784 | -0.085948 | -0.38883 | -122.3033 | -0.1261 | -0.073287 | -0.005985 | -122.6338 | 122.494 | -0.071485 | 122.494 | 122.4617 | -0.03235 | -0.10495 | -0.1007 | -0.15452 | -0.14899 | 122.3933 | 0.17592 | 0.33045 | -0.096175 | -0.028873 | 122.4307 | 122.3972 | 122.4014 | 122.4761 | -0.008104 | 122.3531 | 122.406 | 122.4733 | 122.0904 | -122.6567
2093.5625 | 122.7859 | -122.4655 | 0.009155 | -0.013049 | -0.064061 | 0.062467 | -0.012579 | -0.0082965 | 0.0056685 | -0.019381 | -0.0013673 | -0.0018716 | -0.0065099 | 0.025545 | -0.012022 | 0.001048 | 0.001407 | -0.017566 | -0.044018 | -0.077483 | -0.082386 | 0.019363 | -0.095105 | -0.39341 | -122.2987 | -0.13068 | -0.082444 | -0.005985 | -122.6292 | 122.4849 | -0.053173 | 122.4666 | 122.4479 | -0.036929 | -0.086638 | -0.091541 | -0.16368 | -0.13984 | 122.3704 | 0.16677 | 0.33045 | -0.091599 | -0.01514 | 122.4215 | 122.388 | 122.3831 | 122.4669 | 0.010208 | 122.3348 | 122.3831 | 122.4595 | 122.0721 | -122.6383
2095.25 | 122.699 | -122.5113 | 0.032043 | 0.009844 | -0.064061 | 0.062467 | -0.012366 | -0.0080829 | 0.0054549 | -0.027012 | -0.0015809 | -0.0020852 | -0.0062963 | 0.025331 | -0.01245 | 0.010204 | 0.001407 | -0.012988 | -0.03944 | -0.077483 | -0.077807 | 0.019363 | -0.095105 | -0.40257 | -122.3033 | -0.1261 | -0.077866 | -0.005985 | -122.6384 | 122.5307 | -0.071483 | 122.5215 | 122.4983 | -0.032351 | -0.10953 | -0.10985 | -0.12706 | -0.15815 | 122.4162 | 0.20797 | 0.33503 | -0.10991 | -0.038028 | 122.4719 | 122.4338 | 122.4335 | 122.5127 | -0.01268 | 122.3852 | 122.4334 | 122.5053 | 122.1087 | -122.6704
2096.9375 | 122.7722 | -122.4655 | 0 | -0.005418 | -0.063848 | 0.062467 | -0.012579 | -0.0085103 | 0.0056685 | -0.027012 | -0.0017945 | -0.0020852 | -0.0062963 | 0.025545 | -0.012236 | 0.019361 | -0.003172 | -0.017566 | -0.03944 | -0.072904 | -0.073228 | 0.010206 | -0.095105 | -0.40257 | -122.3033 | -0.13068 | -0.077866 | -0.005985 | -122.6338 | 122.4757 | -0.03944 | 122.4849 | 122.4479 | -0.027772 | -0.072904 | -0.073228 | -0.16826 | -0.13068 | 122.3704 | 0.16219 | 0.33045 | -0.077866 | -0.005985 | 122.4261 | 122.3926 | 122.3923 | 122.4623 | 0.010206 | 122.3348 | 122.3876 | 122.4595 | 122.0629 | -122.6338
2098.625 | 122.7493 | -122.4609 | -0.009155 | -0.013049 | -0.064275 | 0.062253 | -0.012793 | -0.0078693 | 0.0058821 | -0.019381 | -0.0017945 | -0.0020852 | -0.0062963 | 0.025758 | -0.01245 | 0.014783 | 0.010564 | -0.022144 | -0.053175 | -0.063746 | -0.073228 | 0.019363 | -0.090527 | -0.40257 | -122.3033 | -0.13068 | -0.077866 | 0.003172 | -122.6429 | 122.4803 | -0.04402 | 122.4757 | 122.4388 | -0.041507 | -0.054591 | -0.064073 | -0.18199 | -0.12153 | 122.3704 | 0.15761 | 0.33961 | -0.068711 | 0.012327 | 122.4078 | 122.3972 | 122.3877 | 122.4715 | 0.028518 | 122.3303 | 122.3831 | 122.4641 | 122.0584 | -122.6338
2100.2969 | 122.7081 | -122.493 | 0.036621 | -0.005418 | -0.064061 | 0.062253 | -0.013007 | -0.0080829 | 0.0056685 | -0.011751 | -0.0015809 | -0.0018716 | -0.0062963 | 0.025331 | -0.011809 | 0.010204 | 0.005985 | -0.017566 | -0.053175 | -0.082062 | -0.077807 | 0.019363 | -0.090527 | -0.39799 | -122.3079 | -0.13526 | -0.073287 | -0.001407 | -122.6384 | 122.5123 | -0.089796 | 122.5032 | 122.4754 | -0.036929 | -0.11868 | -0.11443 | -0.14537 | -0.17188 | 122.4025 | 0.18508 | 0.33045 | -0.10991 | -0.038028 | 122.4398 | 122.4109 | 122.4152 | 122.499 | -0.017258 | 122.3577 | 122.4197 | 122.4916 | 122.095 | -122.675
2102.0156 | 122.7448 | -122.4884 | 0.004578 | -0.02068 | -0.064275 | 0.062253 | -0.012579 | -0.0082965 | 0.0060959 | -0.027012 | -0.00094006 | -0.0018716 | -0.0065099 | 0.025545 | -0.01245 | 0.010204 | 0.001407 | -0.017566 | -0.048597 | -0.072904 | -0.073228 | 0.019363 | -0.095105 | -0.40257 | -122.3079 | -0.13526 | -0.073287 | -0.005985 | -122.6429 | 122.5078 | -0.053175 | 122.4986 | 122.4708 | -0.036929 | -0.077482 | -0.077806 | -0.15453 | -0.13984 | 122.3933 | 0.1805 | 0.33503 | -0.077865 | -0.010563 | 122.4398 | 122.4155 | 122.4152 | 122.4898 | 0.014785 | 122.3531 | 122.4151 | 122.4824 | 122.0858 | -122.6475
2103.75 | 122.6715 | -122.5159 | 0.032043 | -0.02068 | -0.064489 | 0.062039 | -0.012793 | -0.0082965 | 0.0058821 | -0.019381 | 0.034097 | -0.0046492 | -0.0071509 | 0.025972 | 0.014471 | 0.010204 | 0.001407 | -0.017566 | -0.044018 | -0.077483 | -0.077807 | 0.010206 | -0.52092 | -1.0711 | -122.3079 | -9.1549 | -9.5006 | -9.3097 | -122.6384 | 122.5261 | -0.076061 | 122.5261 | 122.4983 | -0.027772 | -0.10953 | -0.10985 | -0.12248 | -9.1869 | 121.9949 | 0.20797 | 0.33045 | -9.5327 | -9.3417 | 122.4719 | 122.4384 | 122.4381 | 122.5173 | -0.021837 | 113.361 | 113.0152 | 113.2062 | 121.4448 | -122.6704
2105.4375 | 122.7448 | -122.4792 | 0.022888 | -0.005418 | -0.064061 | 0.062467 | -0.01322 | -0.0078693 | 0.0058821 | -0.011751 | 0.03431 | -0.0044356 | -0.0073645 | 0.026399 | 0.014471 | 0.005626 | 0.005985 | -0.012988 | -0.03944 | -0.077483 | -0.077807 | 0.010206 | -0.48887 | -1.0207 | -122.3033 | -9.1595 | -9.5006 | -9.3143 | -122.6384 | 122.4895 | -0.062328 | 122.4849 | 122.4663 | -0.023194 | -0.10037 | -0.1007 | -0.1591 | -9.1824 | 121.9904 | 0.17592 | 0.33503 | -9.5235 | -9.3372 | 122.4398 | 122.4018 | 122.4014 | 122.4852 | -0.012682 | 113.3198 | 112.9786 | 113.165 | 121.4586 | -122.6612
2107.1406 | 122.7631 | -122.4426 | 0.009155 | -0.028311 | -0.064275 | 0.062253 | -0.012366 | -0.0082965 | 0.0056685 | -0.011751 | 0.033883 | -0.0044356 | -0.0073645 | 0.026186 | 0.014684 | 0.010204 | 0.001407 | -0.017566 | -0.044018 | -0.068325 | -0.077807 | 0.014784 | -0.4614 | -0.98406 | -122.3033 | -9.1503 | -9.5006 | -9.3097 | -122.6475 | 122.4574 | -0.053173 | 122.4528 | 122.4251 | -0.03235 | -0.07748 | -0.086962 | -0.20488 | -9.1595 | 121.9812 | 0.1393 | 0.34418 | -9.5098 | -9.3189 | 122.3986 | 122.3743 | 122.3648 | 122.444 | 0.005629 | 113.2923 | 112.942 | 113.1329 | 121.4586 | -122.6567
2108.8906 | 122.6761 | -122.5388 | 0.032043 | -0.005418 | -0.064061 | 0.062253 | -0.012793 | -0.0082965 | 0.0058821 | -0.019381 | 0.034097 | -0.0046492 | -0.0067235 | 0.026399 | 0.014471 | 0.010204 | 0.005985 | -0.008409 | -0.044018 | -0.072904 | -0.077807 | 0.014784 | -0.44309 | -0.97491 | -122.3079 | -9.1549 | -9.5006 | -9.3189 | -122.6384 | 122.5535 | -0.076061 | 122.549 | 122.5303 | -0.023193 | -0.10495 | -0.10985 | -0.099594 | -9.1869 | 122.0957 | 0.23085 | 0.33045 | -9.5327 | -9.3509 | 122.4947 | 122.4659 | 122.4609 | 122.5447 | -0.017259 | 113.3839 | 113.0381 | 113.2199 | 121.5639 | -122.6704
2110.5625 | 122.7356 | -122.5113 | 0.004578 | -0.013049 | -0.064061 | 0.062253 | -0.012366 | -0.0085103 | 0.0054549 | -0.0041205 | 0.034524 | -0.0044356 | -0.0071509 | 0.025972 | 0.014684 | 0.014783 | 0.005985 | -0.017566 | -0.044018 | -0.072904 | -0.082386 | 0.019363 | -0.43851 | -0.97033 | -122.3125 | -9.1503 | -9.5098 | -9.3189 | -122.6384 | 122.5307 | -0.048596 | 122.5261 | 122.4937 | -0.036929 | -0.077482 | -0.086964 | -0.12706 | -9.1549 | 122.0728 | 0.19881 | 0.32587 | -9.5144 | -9.3234 | 122.4673 | 122.4384 | 122.4289 | 122.5173 | 0.014785 | 113.361 | 113.0015 | 113.1924 | 121.541 | -122.6429
2112.2812 | 122.7402 | -122.4976 | 0.022888 | -0.013049 | -0.064489 | 0.062253 | -0.012579 | -0.0085103 | 0.0058821 | -0.019381 | 0.03431 | -0.0048628 | -0.0069371 | 0.025972 | 0.014257 | 0.014783 | 0.005985 | -0.017566 | -0.03944 | -0.077483 | -0.077807 | 0.014784 | -0.43393 | -0.95659 | -122.3125 | -9.1641 | -9.5052 | -9.3143 | -122.6429 | 122.5123 | -0.062328 | 122.5123 | 122.48 | -0.03235 | -0.10037 | -0.1007 | -0.14537 | -9.1869 | 122.0636 | 0.18508 | 0.33045 | -9.5281 | -9.3372 | 122.4581 | 122.4201 | 122.4198 | 122.5035 | -0.008104 | 113.3335 | 112.9924 | 113.1833 | 121.541 | -122.6658
2113.9688 | 122.7036 | -122.5296 | 0.032043 | -0.013049 | -0.064275 | 0.062039 | -0.012579 | -0.0082965 | 0.0056685 | -0.011751 | 0.034097 | -0.0044356 | -0.0073645 | 0.026186 | 0.014471 | 0.010204 | 0.001407 | -0.017566 | -0.044018 | -0.072904 | -0.06865 | 0.028521 | -0.43851 | -0.96575 | -122.3079 | -9.1549 | -9.5006 | -9.3143 | -122.6475 | 122.5581 | -0.076061 | 122.5398 | 122.512 | -0.046087 | -0.10495 | -0.10069 | -0.11791 | -9.1869 | 122.0911 | 0.2217 | 0.33961 | -9.5327 | -9.3463 | 122.4856 | 122.4567 | 122.461 | 122.531 | -0.003522 | 113.3747 | 113.029 | 113.2153 | 121.5639 | -122.6796
2115.7031 | 122.7859 | -122.4747 | 0.018311 | -0.005418 | -0.064275 | 0.062253 | -0.012793 | -0.0080829 | 0.0056685 | -0.027012 | 0.034097 | -0.0046492 | -0.0073645 | 0.026399 | 0.014257 | 0.005626 | 0.001407 | -0.012988 | -0.044018 | -0.068325 | -0.073228 | 0.023942 | -0.42477 | -0.96117 | -122.3125 | -9.1503 | -9.5006 | -9.3189 | -122.6521 | 122.4986 | -0.062329 | 122.4803 | 122.4617 | -0.03693 | -0.086636 | -0.091539 | -0.17742 | -9.1686 | 122.0499 | 0.16219 | 0.33961 | -9.5189 | -9.3372 | 122.4307 | 122.4063 | 122.4014 | 122.4761 | 0.005631 | 113.3244 | 112.974 | 113.1558 | 121.5135 | -122.6704
2117.4062 | 122.7356 | -122.493 | 0.009155 | -0.013049 | -0.064702 | 0.062039 | -0.012579 | -0.0082965 | 0.0056685 | -0.019381 | 0.03431 | -0.0048628 | -0.0067235 | 0.026186 | 0.014471 | 0.014783 | 0.005985 | -0.017566 | -0.048597 | -0.072904 | -0.073228 | 0.014784 | -0.42019 | -0.96117 | -122.3125 | -9.1549 | -9.5006 | -9.3143 | -122.6475 | 122.5078 | -0.057752 | 122.5078 | 122.4754 | -0.03235 | -0.082059 | -0.082383 | -0.15453 | -9.164 | 122.0728 | 0.1805 | 0.33503 | -9.5098 | -9.3234 | 122.4444 | 122.4201 | 122.4198 | 122.499 | 0.005629 | 113.3381 | 112.9924 | 113.1787 | 121.5318 | -122.6567
2119.0938 | 122.7768 | -122.493 | -0.009155 | 0.002213 | -0.064275 | 0.062039 | -0.012579 | -0.0087239 | 0.0058821 | -0.0041205 | 0.03431 | -0.0046492 | -0.0071509 | 0.026186 | 0.014471 | 0.010204 | 0.005985 | -0.017566 | -0.048597 | -0.072904 | -0.073228 | 0.023942 | -0.42477 | -0.96117 | -122.3216 | -9.1595 | -9.5052 | -9.3189 | -122.6429 | 122.5169 | -0.039442 | 122.5032 | 122.4754 | -0.041508 | -0.063749 | -0.064073 | -0.14995 | -9.1503 | 122.0682 | 0.17134 | 0.32129 | -9.4961 | -9.3097 | 122.4444 | 122.4201 | 122.4198 | 122.499 | 0.033097 | 113.3335 | 112.9878 | 113.1741 | 121.5318 | -122.6338
2120.7812 | 122.7448 | -122.4976 | 0.018311 | -0.005418 | -0.064061 | 0.062253 | -0.012366 | -0.0085103 | 0.0054549 | -0.027012 | 0.03431 | -0.0046492 | -0.0069371 | 0.025972 | 0.014684 | 0.010204 | -0.007751 | -0.017566 | -0.044018 | -0.082062 | -0.077807 | 0.019363 | -0.42935 | -0.96575 | -122.3079 | -9.1503 | -9.5006 | -9.3189 | -122.6475 | 122.5169 | -0.062329 | 122.5078 | 122.48 | -0.036929 | -0.10037 | -0.096118 | -0.14995 | -9.1686 | 122.0682 | 0.18966 | 0.33961 | -9.5189 | -9.3372 | 122.4535 | 122.4155 | 122.4198 | 122.4898 | 0.001052 | 113.3472 | 112.9969 | 113.1787 | 121.5318 | -122.6658
2122.4688 | 122.7219 | -122.5113 | 0.004578 | -0.013049 | -0.064489 | 0.062039 | -0.012366 | -0.0087239 | 0.0054549 | -0.019381 | 0.03431 | -0.0044356 | -0.0073645 | 0.026186 | 0.014898 | 0.010204 | 0.001407 | -0.017566 | -0.044018 | -0.072904 | -0.073228 | 0.019363 | -0.42019 | -0.96575 | -122.3125 | -9.1595 | -9.5052 | -9.3234 | -122.6567 | 122.5307 | -0.048596 | 122.5215 | 122.4937 | -0.036929 | -0.077482 | -0.077806 | -0.14537 | -9.1641 | 122.0911 | 0.19881 | 0.34418 | -9.5098 | -9.328 | 122.4673 | 122.4384 | 122.4381 | 122.5127 | 0.014785 | 113.3518 | 113.0061 | 113.1879 | 121.5455 | -122.6612
2124.1406 | 122.699 | -122.5204 | 0.022888 | -0.005418 | -0.064275 | 0.062253 | -0.012793 | -0.0082965 | 0.0052411 | -0.027012 | 0.034097 | -0.0046492 | -0.0071509 | 0.025972 | 0.014043 | 0.010204 | 0.001407 | -0.012988 | -0.048597 | -0.072904 | -0.077807 | 0.019363 | -0.42477 | -0.97033 | -122.3125 | -9.1549 | -9.5006 | -9.3189 | -122.6475 | 122.5398 | -0.071485 | 122.5307 | 122.5075 | -0.032351 | -0.095792 | -0.1007 | -0.12706 | -9.1778 | 122.0957 | 0.20796 | 0.33503 | -9.5235 | -9.3418 | 122.4719 | 122.4475 | 122.4426 | 122.5219 | -0.003525 | 113.3656 | 113.0198 | 113.2016 | 121.5501 | -122.6704
2125.875 | 122.7264 | -122.5159 | 0.045776 | -0.005418 | -0.064061 | 0.062253 | -0.012793 | -0.0085103 | 0.0056685 | -0.019381 | 0.034097 | -0.0046492 | -0.0071509 | 0.026186 | 0.014684 | 0.014783 | 0.005985 | -0.017566 | -0.048597 | -0.082062 | -0.06865 | 0.014784 | -0.43393 | -0.97491 | -122.3125 | -9.1503 | -9.5098 | -9.3189 | -122.6475 | 122.5307 | -0.094373 | 122.5307 | 122.4983 | -0.03235 | -0.12784 | -0.11443 | -0.13164 | -9.1961 | 122.0819 | 0.20339 | 0.33503 | -9.5556 | -9.3646 | 122.4673 | 122.4338 | 122.4472 | 122.5219 | -0.030992 | 113.3656 | 113.0061 | 113.197 | 121.541 | -122.6933
2127.5625 | 122.7631 | -122.4976 | 0.013733 | -0.005418 | -0.064275 | 0.062253 | -0.012579 | -0.0087239 | 0.0054549 | -0.019381 | 0.034097 | -0.0048628 | -0.0073645 | 0.026613 | 0.014684 | 0.005626 | 0.001407 | -0.022144 | -0.044018 | -0.072904 | -0.077807 | 0.014784 | -0.42477 | -0.96117 | -122.3216 | -9.1503 | -9.5052 | -9.3143 | -122.6612 | 122.5123 | -0.057751 | 122.5032 | 122.4754 | -0.036928 | -0.086637 | -0.09154 | -0.16369 | -9.164 | 122.0728 | 0.17592 | 0.3396 | -9.5189 | -9.328 | 122.4535 | 122.4247 | 122.4198 | 122.499 | 0.001051 | 113.3472 | 112.9924 | 113.1833 | 121.5364 | -122.675
2129.25 | 122.6624 | -122.5342 | 0.041199 | -0.005418 | -0.064275 | 0.062253 | -0.012366 | -0.0085103 | 0.0058821 | -0.011751 | 0.033883 | -0.0044356 | -0.0073645 | 0.026186 | 0.014257 | 0.014783 | 0.001407 | -0.012988 | -0.053175 | -0.077483 | -0.073228 | 0.014784 | -0.42935 | -0.97491 | -122.3171 | -9.1549 | -9.5052 | -9.3097 | -122.6521 | 122.549 | -0.094374 | 122.549 | 122.5212 | -0.027772 | -0.11868 | -0.11443 | -0.11791 | -9.1961 | 122.1048 | 0.21712 | 0.33503 | -9.5464 | -9.3509 | 122.481 | 122.4567 | 122.461 | 122.5356 | -0.026415 | 113.3793 | 113.029 | 113.2245 | 121.5593 | -122.6933
2130.9844 | 122.7631 | -122.5113 | 0.004578 | -0.005418 | -0.064489 | 0.062253 | -0.012579 | -0.0082965 | 0.0056685 | -0.011751 | 0.033669 | -0.0044356 | -0.0069371 | 0.026186 | 0.014684 | 0.010204 | 0.001407 | -0.017566 | -0.03944 | -0.068325 | -0.077807 | 0.014784 | -0.42477 | -0.97949 | -122.3171 | -9.1549 | -9.5006 | -9.3143 | -122.6567 | 122.5261 | -0.044018 | 122.5215 | 122.4937 | -0.03235 | -0.072903 | -0.082385 | -0.14537 | -9.1595 | 122.0865 | 0.19423 | 0.3396 | -9.5052 | -9.3189 | 122.4719 | 122.443 | 122.4335 | 122.5127 | 0.010206 | 113.3564 | 113.0107 | 113.197 | 121.5318 | -122.6612
2132.6719 | 122.6532 | -122.5342 | 0.036621 | -0.013049 | -0.064275 | 0.062253 | -0.012793 | -0.0080829 | 0.0054549 | -0.0041205 | 0.034524 | -0.0042218 | -0.0075781 | 0.025972 | 0.014257 | 0.005626 | 0.001407 | -0.017566 | -0.048597 | -0.072904 | -0.077807 | 0.010206 | -0.42935 | -0.98406 | -122.3171 | -9.1595 | -9.5052 | -9.3189 | -122.6567 | 122.5444 | -0.085218 | 122.5398 | 122.5166 | -0.027772 | -0.10952 | -0.11443 | -0.12249 | -9.1961 | 122.1048 | 0.21712 | 0.3396 | -9.5418 | -9.3555 | 122.4856 | 122.4613 | 122.4564 | 122.5356 | -0.026415 | 113.3747 | 113.029 | 113.2153 | 121.5501 | -122.6933
2134.4062 | 122.7539 | -122.5113 | 0.018311 | -0.005418 | -0.064275 | 0.062039 | -0.012793 | -0.0082965 | 0.0052411 | -0.011751 | 0.034097 | -0.0046492 | -0.0071509 | 0.026399 | 0.014043 | 0.014783 | 0.005985 | -0.012988 | -0.048597 | -0.068325 | -0.077807 | 0.019363 | -0.43393 | -0.98864 | -122.3216 | -9.1549 | -9.5098 | -9.3097 | -122.6612 | 122.5307 | -0.066908 | 122.5261 | 122.4983 | -0.032351 | -0.086636 | -0.096118 | -0.14995 | -9.1732 | 122.0774 | 0.18965 | 0.3396 | -9.5281 | -9.328 | 122.4627 | 122.443 | 122.4335 | 122.5173 | 0.001052 | 113.3564 | 113.0015 | 113.2016 | 121.5226 | -122.6796
2136.1094 | 122.7814 | -122.5159 | -0.004578 | -0.005418 | -0.064275 | 0.062039 | -0.013007 | -0.0082965 | 0.0058821 | -0.027012 | 0.034097 | -0.0044356 | -0.0073645 | 0.026186 | 0.014043 | 0.014783 | 0.001407 | -0.022144 | -0.048597 | -0.077483 | -0.073228 | 0.010206 | -0.42935 | -0.98406 | -122.3171 | -9.1503 | -9.5006 | -9.3143 | -122.6612 | 122.5261 | -0.044019 | 122.5307 | 122.4937 | -0.03235 | -0.072905 | -0.06865 | -0.14538 | -9.1457 | 122.0865 | 0.19881 | 0.34418 | -9.4961 | -9.3097 | 122.4673 | 122.4384 | 122.4426 | 122.5173 | 0.014784 | 113.3656 | 113.0152 | 113.2016 | 121.5318 | -122.6567
2137.7969 | 122.7539 | -122.5067 | 0.013733 | -0.02068 | -0.064061 | 0.062253 | -0.012366 | -0.0082965 | 0.0054549 | -0.027012 | 0.033883 | -0.0044356 | -0.0073645 | 0.025972 | 0.014257 | 0.014783 | 0.005985 | -0.012988 | -0.044018 | -0.072904 | -0.073228 | 0.014784 | -0.43393 | -0.99322 | -122.3262 | -9.1595 | -9.5052 | -9.328 | -122.6658 | 122.5215 | -0.057751 | 122.5215 | 122.4937 | -0.027772 | -0.086637 | -0.086961 | -0.15911 | -9.1732 | 122.0728 | 0.1805 | 0.33961 | -9.5189 | -9.3418 | 122.4627 | 122.4338 | 122.4335 | 122.5127 | 0.001051 | 113.3472 | 113.0015 | 113.1787 | 121.5135 | -122.6796
2139.4844 | 122.7081 | -122.525 | 0.018311 | -0.013049 | -0.064275 | 0.062039 | -0.013007 | -0.0080829 | 0.0054549 | -0.019381 | 0.03431 | -0.0046492 | -0.0069371 | 0.025972 | 0.014471 | 0.010204 | 0.001407 | -0.012988 | -0.048597 | -0.077483 | -0.077807 | 0.023942 | -0.43393 | -0.9978 | -122.3171 | -9.1686 | -9.5052 | -9.3189 | -122.6567 | 122.549 | -0.066908 | 122.5352 | 122.512 | -0.03693 | -0.095794 | -0.096118 | -0.13164 | -9.1869 | 122.0911 | 0.20796 | 0.3396 | -9.5235 | -9.3372 | 122.4764 | 122.4475 | 122.4472 | 122.5264 | 0.005631 | 113.3564 | 113.0198 | 113.2062 | 121.5272 | -122.675
2141.1719 | 122.6761 | -122.5662 | 0.022888 | 0.002213 | -0.064702 | 0.062253 | -0.012793 | -0.0085103 | 0.0058821 | -0.019381 | 0.03431 | -0.0044356 | -0.0075781 | 0.026399 | 0.014471 | 0.014783 | -0.003172 | -0.022144 | -0.044018 | -0.068325 | -0.06865 | 0.019363 | -0.43851 | -1.0024 | -122.3171 | -9.1503 | -9.5006 | -9.3189 | -122.6612 | 122.5856 | -0.066906 | 122.581 | 122.5441 | -0.041507 | -0.091213 | -0.091538 | -0.095022 | -9.1732 | 122.1277 | 0.24916 | 0.34418 | -9.5235 | -9.3418 | 122.5222 | 122.4979 | 122.4976 | 122.5631 | -0.003525 | 113.4159 | 113.0656 | 113.2474 | 121.5638 | -122.6841
2142.8594 | 122.6761 | -122.5433 | 0.032043 | -0.005418 | -0.064489 | 0.062039 | -0.012793 | -0.0082965 | 0.0054549 | -0.019381 | 0.034524 | -0.0044356 | -0.0073645 | 0.026186 | 0.014471 | 0.014783 | -0.003172 | -0.022144 | -0.03944 | -0.072904 | -0.073228 | 0.023942 | -0.43851 | -0.9978 | -122.3262 | -9.1595 | -9.5006 | -9.3143 | -122.6567 | 122.5673 | -0.071483 | 122.5581 | 122.5212 | -0.046086 | -0.10495 | -0.10527 | -0.11333 | -9.1915 | 122.1048 | 0.21712 | 0.33045 | -9.5327 | -9.3463 | 122.5039 | 122.4704 | 122.4701 | 122.5402 | -0.008101 | 113.3839 | 113.0427 | 113.2291 | 121.5455 | -122.6887
2144.5469 | 122.7219 | -122.5296 | 0.018311 | -0.005418 | -0.064489 | 0.062039 | -0.012793 | -0.0082965 | 0.0052411 | -0.019381 | 0.034097 | -0.0046492 | -0.0071509 | 0.026186 | 0.014684 | 0.005626 | 0.001407 | -0.022144 | -0.044018 | -0.072904 | -0.073228 | 0.019363 | -0.43393 | -1.007 | -122.3216 | -9.1595 | -9.5052 | -9.3143 | -122.6658 | 122.549 | -0.062329 | 122.5352 | 122.5075 | -0.041507 | -0.091215 | -0.091539 | -0.13622 | -9.1778 | 122.0957 | 0.20796 | 0.34418 | -9.5235 | -9.3326 | 122.4856 | 122.4567 | 122.4564 | 122.531 | 0.001052 | 113.3701 | 113.0244 | 113.2153 | 121.5226 | -122.6841
2146.25 | 122.8043 | -122.4976 | 0.009155 | 0.009844 | -0.064061 | 0.062039 | -0.012579 | -0.0087239 | 0.0056685 | -0.019381 | 0.034097 | -0.0044356 | -0.0069371 | 0.026186 | 0.014257 | 0.019361 | -0.003172 | -0.017566 | -0.044018 | -0.072904 | -0.077807 | 0.019363 | -0.43851 | -1.007 | -122.3216 | -9.1549 | -9.5052 | -9.3097 | -122.6612 | 122.5169 | -0.053173 | 122.5169 | 122.48 | -0.036929 | -0.082059 | -0.086962 | -0.16369 | -9.164 | 122.059 | 0.17592 | 0.3396 | -9.5144 | -9.3189 | 122.4535 | 122.4247 | 122.4198 | 122.4944 | 0.010208 | 113.3427 | 112.9924 | 113.1879 | 121.4906 | -122.6704
2147.9844 | 122.6898 | -122.5433 | 0.036621 | -0.005418 | -0.064489 | 0.061826 | -0.012793 | -0.0082965 | 0.0054549 | -0.011751 | 0.034097 | -0.0048628 | -0.0071509 | 0.026399 | 0.014257 | 0.010204 | 0.001407 | -0.022144 | -0.048597 | -0.072904 | -0.073228 | 0.014784 | -0.43851 | -1.0115 | -122.3354 | -9.1549 | -9.5052 | -9.3097 | -122.6658 | 122.5581 | -0.085218 | 122.5535 | 122.5212 | -0.036928 | -0.10952 | -0.10985 | -0.12249 | -9.1915 | 122.1048 | 0.20796 | 0.33045 | -9.5418 | -9.3463 | 122.4947 | 122.4704 | 122.4701 | 122.5447 | -0.021837 | 113.3884 | 113.0381 | 113.2336 | 121.5318 | -122.7024
2149.6875 | 122.6898 | -122.5433 | 0.018311 | -0.005418 | -0.064489 | 0.061826 | -0.012579 | -0.0082965 | 0.0054549 | -0.0041205 | 0.034097 | -0.0046492 | -0.0071509 | 0.026186 | 0.014471 | 0.019361 | -0.003172 | -0.022144 | -0.048597 | -0.068325 | -0.073228 | 0.010206 | -0.43851 | -1.007 | -122.3262 | -9.1595 | -9.5006 | -9.3143 | -122.6704 | 122.5535 | -0.066908 | 122.5627 | 122.5212 | -0.03235 | -0.086636 | -0.091539 | -0.12707 | -9.1778 | 122.1048 | 0.21712 | 0.34418 | -9.5189 | -9.3326 | 122.4947 | 122.475 | 122.4701 | 122.5402 | -0.008105 | 113.3839 | 113.0427 | 113.2291 | 121.5364 | -122.6887
2151.375 | 122.699 | -122.5616 | 0.022888 | -0.005418 | -0.064489 | 0.062039 | -0.012793 | -0.0080829 | 0.0056685 | -0.0041205 | 0.034097 | -0.0048628 | -0.0069371 | 0.025972 | 0.014257 | 0.014783 | 0.005985 | -0.012988 | -0.044018 | -0.063746 | -0.077807 | 0.023942 | -0.45225 | -1.0161 | -122.3262 | -9.1595 | -9.5052 | -9.3143 | -122.6658 | 122.5856 | -0.066906 | 122.5764 | 122.5487 | -0.03693 | -0.086634 | -0.1007 | -0.10418 | -9.1824 | 122.1094 | 0.23543 | 0.33961 | -9.5281 | -9.3372 | 122.5176 | 122.4979 | 122.4838 | 122.5676 | 0.001054 | 113.4022 | 113.0564 | 113.2474 | 121.5455 | -122.6887
2153.0781 | 122.7676 | -122.5021 | 0.013733 | -0.005418 | -0.064702 | 0.061826 | -0.012793 | -0.0080829 | 0.0054549 | -0.019381 | 0.034097 | -0.0044356 | -0.0069371 | 0.026399 | 0.014471 | 0.014783 | -0.003172 | -0.026723 | -0.03944 | -0.072904 | -0.073228 | 0.019363 | -0.43851 | -1.0253 | -122.3216 | -9.1641 | -9.5006 | -9.3189 | -122.6612 | 122.5215 | -0.053173 | 122.5169 | 122.4754 | -0.046086 | -0.086637 | -0.086961 | -0.15911 | -9.1778 | 122.0636 | 0.1805 | 0.3396 | -9.5144 | -9.3326 | 122.4627 | 122.4292 | 122.4289 | 122.499 | 0.00563 | 113.3381 | 113.0015 | 113.1833 | 121.4769 | -122.675
2154.7656 | 122.7173 | -122.5433 | 0.032043 | 0.017475 | -0.064489 | 0.062039 | -0.013007 | -0.0082965 | 0.0054549 | -0.019381 | 0.034524 | -0.0046492 | -0.0071509 | 0.026186 | 0.014257 | 0.019361 | 0.001407 | -0.012988 | -0.044018 | -0.077483 | -0.073228 | 0.014784 | -0.44309 | -1.0161 | -122.3308 | -9.1549 | -9.5052 | -9.3143 | -122.6658 | 122.5581 | -0.076061 | 122.5627 | 122.5303 | -0.027772 | -0.10953 | -0.10527 | -0.12249 | -9.1869 | 122.1002 | 0.21254 | 0.33503 | -9.5373 | -9.3463 | 122.4993 | 122.4659 | 122.4701 | 122.5447 | -0.017259 | 113.3884 | 113.0381 | 113.2291 | 121.5272 | -122.6979
2156.4531 | 122.8043 | -122.5067 | 0.004578 | -0.005418 | -0.064702 | 0.062039 | -0.012793 | -0.0082965 | 0.0054549 | 0.00351 | 0.034097 | -0.0046492 | -0.0073645 | 0.026613 | 0.014898 | 0.010204 | -0.003172 | -0.017566 | -0.03944 | -0.068325 | -0.073228 | 0.014784 | -0.44767 | -1.0253 | -122.3308 | -9.1641 | -9.5006 | -9.3143 | -122.6704 | 122.5215 | -0.044018 | 122.5169 | 122.4891 | -0.03235 | -0.072903 | -0.077806 | -0.16369 | -9.1686 | 122.059 | 0.17592 | 0.3396 | -9.5052 | -9.3189 | 122.4673 | 122.4384 | 122.4335 | 122.5035 | 0.010206 | 113.3427 | 113.0061 | 113.1924 | 121.4814 | -122.675
2158.1406 | 122.7814 | -122.5159 | 0.009155 | -0.005418 | -0.064489 | 0.062253 | -0.012793 | -0.0080829 | 0.0054549 | -0.011751 | 0.034097 | -0.0048628 | -0.0073645 | 0.026399 | 0.014257 | 0.014783 | -0.003172 | -0.017566 | -0.048597 | -0.077483 | -0.06865 | 0.019363 | -0.44767 | -1.0299 | -122.3262 | -9.1503 | -9.5006 | -9.3051 | -122.6704 | 122.5352 | -0.057752 | 122.5307 | 122.4983 | -0.036929 | -0.086638 | -0.077805 | -0.15453 | -9.1595 | 122.0682 | 0.18965 | 0.34418 | -9.5098 | -9.3143 | 122.4673 | 122.4384 | 122.4472 | 122.5127 | 0.010208 | 113.3656 | 113.0152 | 113.2107 | 121.486 | -122.6796
2159.8438 | 122.8134 | -122.5296 | 0.004578 | -0.005418 | -0.064702 | 0.061826 | -0.012579 | -0.0085103 | 0.0052411 | -0.019381 | 0.034097 | -0.0040082 | -0.0069371 | 0.026399 | 0.014471 | 0.010204 | 0.005985 | -0.017566 | -0.048597 | -0.072904 | -0.077807 | 0.014784 | -0.44767 | -1.0344 | -122.3262 | -9.1595 | -9.5052 | -9.3097 | -122.6658 | 122.5444 | -0.053175 | 122.5398 | 122.512 | -0.03235 | -0.077482 | -0.082385 | -0.13622 | -9.1641 | 122.0819 | 0.20338 | 0.33961 | -9.5098 | -9.3143 | 122.481 | 122.4567 | 122.4518 | 122.5356 | 0.010206 | 113.3701 | 113.0244 | 113.2199 | 121.4952 | -122.6704
2161.5312 | 122.7493 | -122.5113 | 0.004578 | -0.013049 | -0.064916 | 0.061398 | -0.012579 | -0.0080829 | 0.0054549 | -0.027012 | 0.03431 | -0.0048628 | -0.0071509 | 0.026613 | 0.014257 | 0.010204 | 0.001407 | -0.022144 | -0.044018 | -0.063746 | -0.073228 | 0.019363 | -0.44767 | -1.0344 | -122.3354 | -9.1549 | -9.5006 | -9.3189 | -122.675 | 122.5307 | -0.048596 | 122.5215 | 122.4891 | -0.041507 | -0.068324 | -0.077806 | -0.16369 | -9.1595 | 122.0636 | 0.17592 | 0.33961 | -9.5052 | -9.3234 | 122.4673 | 122.4475 | 122.4381 | 122.5127 | 0.014785 | 113.3564 | 113.0107 | 113.1924 | 121.4769 | -122.6796
2163.2344 | 122.818 | -122.5021 | 0 | -0.02068 | -0.064275 | 0.061826 | -0.012579 | -0.0085103 | 0.0052411 | -0.019381 | 0.034097 | -0.0046492 | -0.0071509 | 0.026613 | 0.014471 | 0.010204 | -0.003172 | -0.022144 | -0.044018 | -0.068325 | -0.073228 | 0.019363 | -0.45225 | -1.039 | -122.3308 | -9.1549 | -9.4961 | -9.3051 | -122.6704 | 122.5215 | -0.044018 | 122.5123 | 122.48 | -0.041507 | -0.068325 | -0.073228 | -0.16827 | -9.1549 | 122.0499 | 0.17134 | 0.3396 | -9.4961 | -9.3051 | 122.4581 | 122.4338 | 122.4289 | 122.499 | 0.019363 | 113.3472 | 113.0061 | 113.197 | 121.4631 | -122.6704
2164.9531 | 122.6944 | -122.5296 | 0.022888 | -0.005418 | -0.064489 | 0.061826 | -0.012579 | -0.0082965 | 0.0054549 | -0.011751 | 0.03431 | -0.0046492 | -0.0069371 | 0.026399 | 0.014257 | 0.014783 | 0.010564 | -0.022144 | -0.03944 | -0.072904 | -0.073228 | 0.019363 | -0.45682 | -1.0436 | -122.3308 | -9.1503 | -9.5052 | -9.3143 | -122.6704 | 122.549 | -0.062328 | 122.5444 | 122.5075 | -0.041507 | -0.095792 | -0.096116 | -0.1408 | -9.1732 | 122.0728 | 0.1988 | 0.3396 | -9.5281 | -9.3372 | 122.4902 | 122.4567 | 122.4564 | 122.5402 | -0.003525 | 113.3793 | 113.0244 | 113.2153 | 121.486 | -122.6933
2166.6406 | 122.7264 | -122.525 | 0.032043 | -0.02068 | -0.064916 | 0.062039 | -0.012579 | -0.0082965 | 0.0058821 | -0.011751 | 0.03431 | -0.0042218 | -0.0071509 | 0.026613 | 0.014043 | 0.014783 | 0.005985 | -0.017566 | -0.048597 | -0.072904 | -0.073228 | 0.023942 | -0.45682 | -1.0436 | -122.3308 | -9.1595 | -9.5006 | -9.3189 | -122.6704 | 122.549 | -0.08064 | 122.5398 | 122.5075 | -0.041508 | -0.10495 | -0.10527 | -0.14538 | -9.1915 | 122.0682 | 0.19423 | 0.3396 | -9.5327 | -9.3509 | 122.4764 | 122.4521 | 122.4518 | 122.531 | -0.008101 | 113.3655 | 113.0244 | 113.2062 | 121.4814 | -122.7024
2168.3594 | 122.7951 | -122.4838 | -0.013733 | -0.013049 | -0.064702 | 0.061826 | -0.013007 | -0.0080829 | 0.0054549 | -0.027012 | 0.034097 | -0.0044356 | -0.0069371 | 0.026186 | 0.014257 | 0.019361 | 0.010564 | -0.017566 | -0.044018 | -0.077483 | -0.064071 | 0.023942 | -0.44767 | -1.0527 | -122.3354 | -9.1549 | -9.5006 | -9.3097 | -122.675 | 122.5078 | -0.030285 | 122.5032 | 122.4663 | -0.041508 | -0.06375 | -0.050338 | -0.19116 | -9.1412 | 122.0362 | 0.14845 | 0.33961 | -9.4869 | -9.296 | 122.4398 | 122.4063 | 122.4198 | 122.4944 | 0.037675 | 113.3289 | 112.9832 | 113.1741 | 121.4311 | -122.6612
2170.0625 | 122.7997 | -122.4884 | -0.009155 | -0.005418 | -0.064702 | 0.061826 | -0.012793 | -0.0080829 | 0.0054549 | -0.019381 | 0.03431 | -0.0044356 | -0.0069371 | 0.026399 | 0.014043 | 0.014783 | 0.005985 | -0.012988 | -0.044018 | -0.072904 | -0.06865 | 0.014784 | -0.46598 | -1.0482 | -122.3308 | -9.1595 | -9.5006 | -9.328 | -122.6796 | 122.5032 | -0.034863 | 122.5032 | 122.4754 | -0.027772 | -0.063749 | -0.059495 | -0.19116 | -9.1503 | 122.0224 | 0.15761 | 0.34876 | -9.4915 | -9.3189 | 122.4444 | 122.4155 | 122.4198 | 122.4944 | 0.023939 | 113.3289 | 112.9878 | 113.1604 | 121.4402 | -122.6704
2171.75 | 122.8134 | -122.5159 | 0.004578 | -0.028311 | -0.064489 | 0.061612 | -0.013007 | -0.0082965 | 0.0054549 | -0.011751 | 0.033883 | -0.0046492 | -0.0071509 | 0.026399 | 0.014043 | 0.010204 | 0.005985 | -0.012988 | -0.03944 | -0.072904 | -0.082386 | 0.023942 | -0.46598 | -1.0573 | -122.3354 | -9.1595 | -9.5006 | -9.3143 | -122.6841 | 122.5398 | -0.044018 | 122.5261 | 122.5029 | -0.03693 | -0.077482 | -0.086964 | -0.16827 | -9.1641 | 122.0499 | 0.18049 | 0.34876 | -9.5052 | -9.3189 | 122.4764 | 122.443 | 122.4335 | 122.5219 | 0.019364 | 113.3564 | 113.0152 | 113.2016 | 121.4585 | -122.6887
2173.4844 | 122.8134 | -122.5067 | -0.009155 | -0.013049 | -0.064702 | 0.062039 | -0.013007 | -0.0082965 | 0.0052411 | -0.019381 | 0.03431 | -0.0044356 | -0.0073645 | 0.026613 | 0.014257 | 0.014783 | 0.010564 | -0.026723 | -0.044018 | -0.077483 | -0.077807 | 0.019363 | -0.4614 | -1.0573 | -122.34 | -9.1549 | -9.5098 | -9.3143 | -122.6704 | 122.5261 | -0.034863 | 122.5215 | 122.48 | -0.046086 | -0.068328 | -0.068652 | -0.16369 | -9.1457 | 122.0453 | 0.16676 | 0.33045 | -9.5006 | -9.3051 | 122.4627 | 122.4292 | 122.4289 | 122.5173 | 0.028518 | 113.3518 | 112.9969 | 113.1924 | 121.4494 | -122.6612
2175.1719 | 122.7127 | -122.5571 | 0.041199 | -0.005418 | -0.064702 | 0.061612 | -0.013007 | -0.0082965 | 0.0054549 | -0.011751 | 0.034097 | -0.0042218 | -0.0071509 | 0.026186 | 0.014471 | 0.010204 | 0.005985 | -0.017566 | -0.03944 | -0.063746 | -0.06865 | 0.014784 | -0.4614 | -1.0665 | -122.3308 | -9.1549 | -9.5006 | -9.3097 | -122.675 | 122.5719 | -0.080639 | 122.5673 | 122.5395 | -0.03235 | -0.10494 | -0.10985 | -0.11791 | -9.1961 | 122.0957 | 0.22627 | 0.34418 | -9.5418 | -9.3509 | 122.5176 | 122.4933 | 122.4884 | 122.5631 | -0.026415 | 113.4022 | 113.0564 | 113.2474 | 121.4906 | -122.7162
2176.9219 | 122.731 | -122.5525 | 0.018311 | -0.005418 | -0.064916 | 0.062467 | -0.013007 | -0.0082965 | 0.0052411 | -0.0041205 | 0.034097 | -0.0046492 | -0.0071509 | 0.026613 | 0.014471 | 0.019361 | 0.001407 | -0.017566 | -0.044018 | -0.072904 | -0.073228 | 0.019363 | -0.4614 | -1.0665 | -122.3354 | -9.1549 | -9.5006 | -9.3189 | -122.6704 | 122.5719 | -0.062329 | 122.5719 | 122.5349 | -0.036929 | -0.091215 | -0.091539 | -0.11791 | -9.1732 | 122.0911 | 0.21711 | 0.33503 | -9.5189 | -9.3372 | 122.5085 | 122.4796 | 122.4793 | 122.5539 | 0.001052 | 113.3976 | 113.0519 | 113.2336 | 121.486 | -122.6887
2178.625 | 122.6624 | -122.5388 | 0.032043 | 0.009844 | -0.064916 | 0.061826 | -0.012793 | -0.0085103 | 0.0052411 | -0.019381 | 0.034097 | -0.0044356 | -0.0071509 | 0.026186 | 0.014684 | 0.019361 | -0.003172 | -0.017566 | -0.044018 | -0.068325 | -0.06865 | 0.014784 | -0.46598 | -1.0665 | -122.34 | -9.1549 | -9.5006 | -9.3143 | -122.6796 | 122.5535 | -0.076061 | 122.5581 | 122.5212 | -0.03235 | -0.10037 | -0.10069 | -0.1408 | -9.1869 | 122.0728 | 0.1988 | 0.3396 | -9.5327 | -9.3463 | 122.4947 | 122.4704 | 122.4701 | 122.5356 | -0.017259 | 113.3839 | 113.0381 | 113.2245 | 121.4723 | -122.7116
2180.3125 | 122.7448 | -122.5525 | 0.018311 | -0.005418 | -0.064916 | 0.062039 | -0.013007 | -0.0085103 | 0.0052411 | -0.019381 | 0.034097 | -0.0046492 | -0.0069371 | 0.026186 | 0.014257 | 0.014783 | 0.005985 | -0.017566 | -0.044018 | -0.068325 | -0.064071 | 0.023942 | -0.46598 | -1.0756 | -122.34 | -9.1549 | -9.4961 | -9.3143 | -122.6796 | 122.5764 | -0.062329 | 122.5673 | 122.5349 | -0.041508 | -0.086636 | -0.082382 | -0.12707 | -9.1732 | 122.0865 | 0.21254 | 0.3396 | -9.5144 | -9.3326 | 122.5085 | 122.4842 | 122.4884 | 122.5585 | 0.005631 | 113.3976 | 113.0564 | 113.2382 | 121.4769 | -122.6979
2182.0156 | 122.7814 | -122.525 | 0.004578 | -0.005418 | -0.064702 | 0.062253 | -0.012793 | -0.0087239 | 0.0056685 | -0.0041205 | 0.034097 | -0.0046492 | -0.0071509 | 0.026399 | 0.014257 | 0.014783 | 0.005985 | -0.022144 | -0.044018 | -0.072904 | -0.06865 | 0.010206 | -0.47972 | -1.0802 | -122.3445 | -9.1549 | -9.5052 | -9.3097 | -122.6841 | 122.5352 | -0.048596 | 122.5398 | 122.5029 | -0.03235 | -0.077482 | -0.073228 | -0.15911 | -9.1595 | 122.0453 | 0.18049 | 0.33961 | -9.5098 | -9.3143 | 122.481 | 122.4521 | 122.4564 | 122.531 | 0.005628 | 113.3701 | 113.0198 | 113.2153 | 121.4448 | -122.6887
2183.7188 | 122.7402 | -122.5388 | 0.013733 | -0.013049 | -0.064916 | 0.062039 | -0.012793 | -0.0082965 | 0.0050275 | -0.019381 | 0.03431 | -0.0042218 | -0.0073645 | 0.026827 | 0.014257 | 0.010204 | 0.005985 | -0.022144 | -0.03944 | -0.072904 | -0.06865 | 0.010206 | -0.47056 | -1.0848 | -122.34 | -9.1595 | -9.5052 | -9.3143 | -122.6796 | 122.549 | -0.053173 | 122.549 | 122.5166 | -0.03235 | -0.086637 | -0.082383 | -0.1408 | -9.1732 | 122.0682 | 0.1988 | 0.3396 | -9.5189 | -9.328 | 122.4993 | 122.4659 | 122.4701 | 122.5447 | -0.003527 | 113.3793 | 113.0335 | 113.2245 | 121.454 | -122.6933
2185.4531 | 122.7768 | -122.5159 | 0.004578 | -0.013049 | -0.064916 | 0.062467 | -0.012579 | -0.0085103 | 0.0052411 | -0.011751 | 0.033883 | -0.0046492 | -0.0073645 | 0.026613 | 0.014257 | 0.014783 | 0.005985 | -0.026723 | -0.044018 | -0.072904 | -0.073228 | 0.005627 | -0.47056 | -1.0848 | -122.34 | -9.1503 | -9.4961 | -9.3189 | -122.6887 | 122.5215 | -0.048596 | 122.5307 | 122.4891 | -0.03235 | -0.077482 | -0.077806 | -0.17285 | -9.1549 | 122.0453 | 0.17591 | 0.34876 | -9.5006 | -9.3234 | 122.4719 | 122.443 | 122.4426 | 122.5219 | 0.001049 | 113.3656 | 113.0198 | 113.197 | 121.4311 | -122.6933
2187.1719 | 122.7219 | -122.5571 | 0.018311 | -0.005418 | -0.064702 | 0.061612 | -0.012793 | -0.0082965 | 0.0052411 | -0.019381 | 0.033883 | -0.0042218 | -0.0073645 | 0.026399 | 0.01383 | 0.014783 | 0.001407 | -0.017566 | -0.044018 | -0.072904 | -0.077807 | 0.005627 | -0.47514 | -1.0848 | -122.34 | -9.1549 | -9.5006 | -9.3143 | -122.6796 | 122.5627 | -0.062329 | 122.5719 | 122.5395 | -0.023193 | -0.091215 | -0.096118 | -0.12249 | -9.1732 | 122.0819 | 0.21711 | 0.3396 | -9.5189 | -9.3326 | 122.5131 | 122.4842 | 122.4793 | 122.5585 | -0.012684 | 113.4022 | 113.0564 | 113.2428 | 121.4723 | -122.6979
2188.9375 | 122.7036 | -122.5525 | 0.036621 | -0.013049 | -0.064916 | 0.062253 | -0.013007 | -0.0085103 | 0.0052411 | -0.019381 | 0.03431 | -0.0046492 | -0.0069371 | 0.026399 | 0.014043 | 0.014783 | 0.010564 | -0.017566 | -0.034862 | -0.068325 | -0.073228 | 0.014784 | -0.47514 | -1.094 | -122.3445 | -9.1641 | -9.4961 | -9.3051 | -122.6841 | 122.5673 | -0.071483 | 122.5673 | 122.5349 | -0.03235 | -0.10495 | -0.10985 | -0.13165 | -9.2007 | 122.0774 | 0.20796 | 0.33961 | -9.5327 | -9.3417 | 122.5176 | 122.4842 | 122.4793 | 122.5631 | -0.021837 | 113.3884 | 113.0564 | 113.2474 | 121.4585 | -122.7208
2190.7031 | 122.8226 | -122.5021 | -0.004578 | -0.013049 | -0.06513 | 0.061612 | -0.012793 | -0.0085103 | 0.0050275 | -0.011751 | 0.03431 | -0.0044356 | -0.0069371 | 0.026613 | 0.014471 | 0.010204 | 0.001407 | -0.022144 | -0.048597 | -0.068325 | -0.06865 | 0.014784 | -0.47972 | -1.094 | -122.3308 | -9.1595 | -9.5006 | -9.3097 | -122.6796 | 122.5169 | -0.044019 | 122.5123 | 122.48 | -0.036928 | -0.063747 | -0.064072 | -0.17742 | -9.1549 | 122.0224 | 0.17134 | 0.34876 | -9.4961 | -9.3051 | 122.4535 | 122.4338 | 122.4335 | 122.5035 | 0.019362 | 113.3427 | 113.0015 | 113.1924 | 121.4082 | -122.675
2192.5 | 122.8317 | -122.525 | 0.004578 | -0.005418 | -0.06513 | 0.061826 | -0.013007 | -0.0085103 | 0.0050275 | -0.0041205 | 0.034097 | -0.0046492 | -0.0069371 | 0.026613 | 0.014043 | 0.014783 | 0.005985 | -0.017566 | -0.03944 | -0.068325 | -0.06865 | 0.019363 | -0.4843 | -1.0985 | -122.3354 | -9.1549 | -9.5006 | -9.3097 | -122.6887 | 122.5444 | -0.044018 | 122.5398 | 122.5075 | -0.036929 | -0.072903 | -0.073228 | -0.16369 | -9.1595 | 122.0407 | 0.18965 | 0.35334 | -9.5052 | -9.3143 | 122.4856 | 122.4567 | 122.4564 | 122.531 | 0.014785 | 113.3701 | 113.0244 | 113.2153 | 121.4265 | -122.6933
2194.2344 | 122.8043 | -122.5342 | 0.022888 | -0.013049 | -0.065343 | 0.061612 | -0.012793 | -0.0082965 | 0.0050275 | -0.011751 | 0.034097 | -0.0044356 | -0.0073645 | 0.026613 | 0.014257 | 0.010204 | 0.001407 | -0.017566 | -0.03944 | -0.072904 | -0.064071 | 0.010206 | -0.47972 | -1.0985 | -122.3445 | -9.1595 | -9.4961 | -9.3143 | -122.6796 | 122.5444 | -0.062328 | 122.5444 | 122.5166 | -0.027772 | -0.095792 | -0.086959 | -0.14538 | -9.1824 | 122.0545 | 0.18965 | 0.33503 | -9.5189 | -9.3372 | 122.4947 | 122.4613 | 122.4701 | 122.5356 | -0.012682 | 113.3747 | 113.0381 | 113.2199 | 121.4356 | -122.7024
2195.9688 | 122.8363 | -122.5342 | 0.009155 | -0.005418 | -0.064916 | 0.061612 | -0.012793 | -0.0085103 | 0.0050275 | -0.027012 | 0.034097 | -0.0044356 | -0.0067235 | 0.026613 | 0.014471 | 0.010204 | 0.005985 | -0.012988 | -0.03944 | -0.068325 | -0.06865 | 0.019363 | -0.4843 | -1.1031 | -122.3445 | -9.1549 | -9.5052 | -9.3051 | -122.6841 | 122.5535 | -0.048595 | 122.5444 | 122.5212 | -0.032351 | -0.07748 | -0.077805 | -0.14996 | -9.164 | 122.0499 | 0.18965 | 0.33961 | -9.5144 | -9.3143 | 122.4947 | 122.4659 | 122.4655 | 122.5402 | 0.010208 | 113.3793 | 113.029 | 113.2291 | 121.4311 | -122.6933
2197.6875 | 122.7814 | -122.5204 | -0.004578 | 0.002213 | -0.064916 | 0.061398 | -0.013007 | -0.0080829 | 0.0050275 | -0.027012 | 0.034097 | -0.0042218 | -0.0071509 | 0.026186 | 0.014257 | 0.014783 | 0.005985 | -0.012988 | -0.044018 | -0.072904 | -0.064071 | 0.019363 | -0.48887 | -1.0985 | -122.3308 | -9.1595 | -9.5006 | -9.3097 | -122.6841 | 122.5398 | -0.03944 | 122.5352 | 122.5075 | -0.032351 | -0.068326 | -0.059493 | -0.16369 | -9.1549 | 122.0316 | 0.18965 | 0.35334 | -9.4961 | -9.3051 | 122.4764 | 122.4475 | 122.4564 | 122.5264 | 0.023941 | 113.361 | 113.0198 | 113.2107 | 121.4219 | -122.6796
2199.375 | 122.6944 | -122.5708 | 0.013733 | 0.009844 | -0.064916 | 0.061826 | -0.012579 | -0.0085103 | 0.0050275 | -0.011751 | 0.034097 | -0.0044356 | -0.0073645 | 0.026399 | 0.014043 | 0.014783 | 0.005985 | -0.017566 | -0.03944 | -0.068325 | -0.06865 | 0.014784 | -0.48887 | -1.1077 | -122.3445 | -9.1595 | -9.5052 | -9.3189 | -122.6887 | 122.5856 | -0.053173 | 122.5856 | 122.5532 | -0.03235 | -0.082058 | -0.082383 | -0.11792 | -9.1732 | 122.0819 | 0.22627 | 0.34418 | -9.5189 | -9.3326 | 122.5314 | 122.5025 | 122.5022 | 122.5768 | 0.001051 | 113.4113 | 113.0656 | 113.2519 | 121.4631 | -122.7025
2201.0938 | 122.7127 | -122.5708 | 0.027466 | 0.002213 | -0.065557 | 0.061826 | -0.012579 | -0.0085103 | 0.0050275 | -0.011751 | 0.033883 | -0.0044356 | -0.0069371 | 0.026613 | 0.014043 | 0.014783 | 0.001407 | -0.012988 | -0.048597 | -0.068325 | -0.073228 | 0.019363 | -0.4843 | -1.1077 | -122.3445 | -9.1549 | -9.5052 | -9.3143 | -122.6933 | 122.5902 | -0.076063 | 122.5856 | 122.5578 | -0.032351 | -0.095791 | -0.10069 | -0.1225 | -9.1824 | 122.0865 | 0.22627 | 0.34876 | -9.5327 | -9.3418 | 122.5222 | 122.5025 | 122.4976 | 122.5722 | -0.008103 | 113.4159 | 113.0656 | 113.2565 | 121.4631 | -122.7208
2202.8125 | 122.7814 | -122.5296 | 0.018311 | -0.013049 | -0.065343 | 0.061398 | -0.012793 | -0.0085103 | 0.0054549 | -0.027012 | 0.034097 | -0.0044356 | -0.0075781 | 0.026399 | 0.014257 | 0.010204 | 0.010564 | -0.017566 | -0.03944 | -0.072904 | -0.06865 | 0.014784 | -0.4843 | -1.1123 | -122.3537 | -9.1503 | -9.5006 | -9.3143 | -122.6933 | 122.5444 | -0.057751 | 122.5398 | 122.512 | -0.03235 | -0.091215 | -0.086961 | -0.1637 | -9.1686 | 122.0453 | 0.17591 | 0.33961 | -9.5189 | -9.3326 | 122.4902 | 122.4567 | 122.461 | 122.5402 | -0.003527 | 113.3793 | 113.029 | 113.2153 | 121.4173 | -122.7116
2204.5312 | 122.8317 | -122.5113 | 0 | -0.013049 | -0.06513 | 0.061612 | -0.012579 | -0.0085103 | 0.0052411 | -0.019381 | 0.033883 | -0.0046492 | -0.0073645 | 0.026613 | 0.014684 | 0.019361 | 0.005985 | -0.017566 | -0.044018 | -0.072904 | -0.06865 | 0.014784 | -0.49345 | -1.1123 | -122.3445 | -9.1549 | -9.5006 | -9.3097 | -122.6979 | 122.5261 | -0.044018 | 122.5307 | 122.4937 | -0.03235 | -0.072904 | -0.06865 | -0.18658 | -9.1549 | 122.0178 | 0.16676 | 0.35334 | -9.5006 | -9.3097 | 122.4673 | 122.4384 | 122.4426 | 122.5173 | 0.014784 | 113.3564 | 113.0107 | 113.2016 | 121.399 | -122.6979
2206.2344 | 122.7539 | -122.5571 | 0.018311 | -0.013049 | -0.064916 | 0.062039 | -0.013007 | -0.0087239 | 0.0052411 | -0.019381 | 0.03431 | -0.0048628 | -0.0073645 | 0.02704 | 0.014257 | 0.014783 | 0.005985 | -0.017566 | -0.044018 | -0.072904 | -0.064071 | 0.010206 | -0.49803 | -1.1168 | -122.3491 | -9.1595 | -9.5006 | -9.3097 | -122.6887 | 122.5673 | -0.062329 | 122.5719 | 122.5395 | -0.027772 | -0.091215 | -0.082382 | -0.13165 | -9.1778 | 122.059 | 0.20795 | 0.3396 | -9.5189 | -9.328 | 122.5131 | 122.4842 | 122.493 | 122.5631 | -0.008105 | 113.3976 | 113.0564 | 113.2474 | 121.4402 | -122.707
2207.9844 | 122.7814 | -122.5433 | 0.027466 | -0.005418 | -0.065343 | 0.061826 | -0.012793 | -0.0087239 | 0.0050275 | -0.019381 | 0.034097 | -0.0044356 | -0.0071509 | 0.026613 | 0.014257 | 0.014783 | 0.005985 | -0.012988 | -0.044018 | -0.072904 | -0.06865 | 0.019363 | -0.49345 | -1.1214 | -122.3491 | -9.1595 | -9.4961 | -9.3097 | -122.6979 | 122.5627 | -0.071484 | 122.5581 | 122.5303 | -0.032351 | -0.10037 | -0.096116 | -0.15454 | -9.1869 | 122.0499 | 0.19422 | 0.34876 | -9.5235 | -9.3372 | 122.4993 | 122.4704 | 122.4747 | 122.5493 | -0.008103 | 113.3839 | 113.0473 | 113.2336 | 121.4219 | -122.7253
2209.6719 | 122.7814 | -122.5525 | 0.013733 | -0.013049 | -0.064916 | 0.061612 | -0.013007 | -0.0085103 | 0.0056685 | -0.011751 | 0.034097 | -0.0046492 | -0.0069371 | 0.026827 | 0.014043 | 0.010204 | 0.001407 | -0.012988 | -0.034862 | -0.063746 | -0.064071 | 0.014784 | -0.49803 | -1.1214 | -122.3491 | -9.1595 | -9.4961 | -9.3097 | -122.6979 | 122.5673 | -0.048595 | 122.5627 | 122.5395 | -0.027772 | -0.077479 | -0.077804 | -0.14539 | -9.1732 | 122.0545 | 0.20338 | 0.34876 | -9.5098 | -9.3234 | 122.5176 | 122.4887 | 122.4884 | 122.5539 | 0.001051 | 113.393 | 113.0564 | 113.2428 | 121.4311 | -122.7116
2211.375 | 122.7493 | -122.5616 | 0 | -0.013049 | -0.065343 | 0.061826 | -0.013007 | -0.0087239 | 0.0050275 | 0.00351 | 0.03431 | -0.0044356 | -0.0071509 | 0.026613 | 0.014043 | 0.005626 | 0.015142 | -0.017566 | -0.03944 | -0.072904 | -0.073228 | 0.014784 | -0.49345 | -1.126 | -122.3491 | -9.1549 | -9.4961 | -9.3097 | -122.6979 | 122.5764 | -0.03944 | 122.5673 | 122.5441 | -0.03235 | -0.072904 | -0.073228 | -0.13623 | -9.1549 | 122.0682 | 0.21253 | 0.34876 | -9.4961 | -9.3097 | 122.5222 | 122.4887 | 122.4884 | 122.5768 | 0.014784 | 113.4068 | 113.0656 | 113.2519 | 121.4356 | -122.6979
2213.1094 | 122.7173 | -122.5525 | 0.036621 | -0.013049 | -0.064916 | 0.061826 | -0.013007 | -0.0085103 | 0.0050275 | -0.0041205 | 0.03431 | -0.0046492 | -0.0073645 | 0.026613 | 0.014257 | 0.014783 | 0.005985 | -0.012988 | -0.03944 | -0.072904 | -0.073228 | 0.019363 | -0.49803 | -1.1214 | -122.3445 | -9.1549 | -9.5006 | -9.3097 | -122.707 | 122.5719 | -0.076061 | 122.5673 | 122.5395 | -0.032351 | -0.10952 | -0.10985 | -0.15454 | -9.1915 | 122.0545 | 0.20796 | 0.3625 | -9.5373 | -9.3463 | 122.5131 | 122.4796 | 122.4793 | 122.5585 | -0.017258 | 113.3976 | 113.0519 | 113.2428 | 121.4311 | -122.7437
2214.8125 | 122.7905 | -122.5616 | 0.004578 | -0.005418 | -0.065343 | 0.061826 | -0.012579 | -0.0082965 | 0.0052411 | -0.019381 | 0.034097 | -0.0044356 | -0.0073645 | 0.026399 | 0.01383 | 0.019361 | 0.005985 | -0.012988 | -0.03944 | -0.072904 | -0.073228 | 0.014784 | -0.50261 | -1.1306 | -122.3491 | -9.1549 | -9.5006 | -9.3143 | -122.6979 | 122.5764 | -0.044018 | 122.581 | 122.5487 | -0.027772 | -0.077482 | -0.077806 | -0.13623 | -9.1595 | 122.059 | 0.21253 | 0.34876 | -9.5052 | -9.3189 | 122.5222 | 122.4887 | 122.4884 | 122.5676 | 0.010206 | 113.4068 | 113.061 | 113.2474 | 121.4311 | -122.7025
2216.5156 | 122.7539 | -122.5525 | 0.022888 | 0.002213 | -0.065343 | 0.061398 | -0.013007 | -0.0085103 | 0.0052411 | -0.027012 | 0.03431 | -0.0048628 | -0.0071509 | 0.026613 | 0.01383 | 0.014783 | 0.005985 | -0.022144 | -0.034862 | -0.068325 | -0.073228 | 0.014784 | -0.50261 | -1.126 | -122.3491 | -9.1549 | -9.4961 | -9.3097 | -122.7025 | 122.5673 | -0.05775 | 122.5673 | 122.5303 | -0.036928 | -0.091213 | -0.096116 | -0.14996 | -9.1778 | 122.0499 | 0.20338 | 0.35334 | -9.5189 | -9.3326 | 122.5176 | 122.4842 | 122.4793 | 122.5585 | -0.008104 | 113.3976 | 113.0564 | 113.2428 | 121.4265 | -122.7253
2218.2031 | 122.7127 | -122.5708 | 0.032043 | -0.013049 | -0.06513 | 0.061612 | -0.012793 | -0.0087239 | 0.0052411 | -0.019381 | 0.034097 | -0.0048628 | -0.0073645 | 0.026613 | 0.01383 | 0.014783 | 0.010564 | -0.017566 | -0.048597 | -0.068325 | -0.064071 | 0.019363 | -0.50719 | -1.1352 | -122.3491 | -9.1549 | -9.5052 | -9.3051 | -122.6979 | 122.5902 | -0.08064 | 122.5856 | 122.5532 | -0.036929 | -0.10037 | -0.096114 | -0.12707 | -9.1869 | 122.0636 | 0.22169 | 0.34876 | -9.5373 | -9.3372 | 122.5222 | 122.5025 | 122.5067 | 122.5814 | -0.01268 | 113.4159 | 113.0656 | 113.2657 | 121.4356 | -122.7299
2219.9531 | 122.7081 | -122.5525 | 0.041199 | -0.013049 | -0.064916 | 0.061612 | -0.013007 | -0.0085103 | 0.0050275 | -0.019381 | 0.03431 | -0.0046492 | -0.0071509 | 0.026827 | 0.014043 | 0.010204 | 0.001407 | -0.017566 | -0.034862 | -0.072904 | -0.064071 | 0.010206 | -0.50261 | -1.126 | -122.3583 | -9.1595 | -9.5052 | -9.3143 | -122.6979 | 122.5627 | -0.076061 | 122.5627 | 122.5349 | -0.027772 | -0.1141 | -0.10527 | -0.14539 | -9.2007 | 122.0499 | 0.19422 | 0.33961 | -9.5464 | -9.3555 | 122.5176 | 122.4796 | 122.4884 | 122.5539 | -0.030993 | 113.393 | 113.0473 | 113.2382 | 121.4265 | -122.7391
2221.6562 | 122.8317 | -122.5204 | -0.004578 | -0.013049 | -0.064702 | 0.061398 | -0.012793 | -0.0082965 | 0.0050275 | -0.011751 | 0.034097 | -0.0046492 | -0.0073645 | 0.026399 | 0.014257 | 0.019361 | 0.005985 | -0.017566 | -0.044018 | -0.068325 | -0.064071 | 0.014784 | -0.51177 | -1.1397 | -122.3583 | -9.1503 | -9.4915 | -9.3143 | -122.6979 | 122.5352 | -0.03944 | 122.5398 | 122.5029 | -0.03235 | -0.063747 | -0.059493 | -0.17743 | -9.1457 | 122.0087 | 0.16218 | 0.33961 | -9.4869 | -9.3097 | 122.4764 | 122.4521 | 122.4564 | 122.5264 | 0.019362 | 113.3701 | 113.029 | 113.2062 | 121.3807 | -122.6933
2223.3438 | 122.8409 | -122.5113 | 0.009155 | -0.005418 | -0.06513 | 0.061612 | -0.01322 | -0.0087239 | 0.0050275 | -0.011751 | 0.03431 | -0.0046492 | -0.0073645 | 0.026613 | 0.014257 | 0.014783 | 0.001407 | -0.017566 | -0.044018 | -0.068325 | -0.077807 | 0.014784 | -0.52092 | -1.1397 | -122.3583 | -9.1549 | -9.4961 | -9.3189 | -122.6979 | 122.5261 | -0.053173 | 122.5261 | 122.4937 | -0.03235 | -0.07748 | -0.086962 | -0.18658 | -9.164 | 121.9904 | 0.15302 | 0.33961 | -9.5052 | -9.328 | 122.4673 | 122.443 | 122.4335 | 122.5127 | 0.005629 | 113.3564 | 113.0152 | 113.1924 | 121.3716 | -122.707
2225.0625 | 122.7585 | -122.5525 | 0.009155 | -0.005418 | -0.065557 | 0.061612 | -0.013007 | -0.0087239 | 0.0054549 | -0.019381 | 0.03431 | -0.0046492 | -0.0071509 | 0.026399 | 0.014043 | 0.014783 | 0.005985 | -0.012988 | -0.03944 | -0.063746 | -0.06865 | 0.010206 | -0.51635 | -1.1397 | -122.3537 | -9.1595 | -9.4961 | -9.3051 | -122.7116 | 122.5627 | -0.048595 | 122.5673 | 122.5395 | -0.023194 | -0.072901 | -0.077805 | -0.15912 | -9.1686 | 122.0361 | 0.1988 | 0.35792 | -9.5052 | -9.3143 | 122.5131 | 122.4887 | 122.4838 | 122.5585 | 0.001051 | 113.393 | 113.0564 | 113.2474 | 121.4128 | -122.7208
2226.7656 | 122.8043 | -122.5433 | -0.004578 | -0.005418 | -0.065343 | 0.061398 | -0.013007 | -0.0085103 | 0.0054549 | -0.011751 | 0.034524 | -0.0046492 | -0.0071509 | 0.026827 | 0.01383 | 0.019361 | 0.005985 | -0.017566 | -0.044018 | -0.068325 | -0.06865 | 0.014784 | -0.5255 | -1.1443 | -122.3537 | -9.1503 | -9.5006 | -9.3143 | -122.707 | 122.5581 | -0.03944 | 122.5627 | 122.5258 | -0.03235 | -0.063747 | -0.064072 | -0.1637 | -9.1457 | 122.0178 | 0.18964 | 0.35334 | -9.4961 | -9.3097 | 122.4993 | 122.475 | 122.4747 | 122.5493 | 0.019362 | 113.393 | 113.0427 | 113.2291 | 121.399 | -122.7025
2228.5156 | 122.7356 | -122.58 | 0.045776 | 0.002213 | -0.065343 | 0.061612 | -0.01322 | -0.0087239 | 0.0052411 | -0.019381 | 0.03431 | -0.0040082 | -0.0069371 | 0.026827 | 0.014043 | 0.014783 | 0.005985 | -0.017566 | -0.044018 | -0.068325 | -0.06865 | 0.014784 | -0.53008 | -1.1443 | -122.3583 | -9.1549 | -9.4961 | -9.3051 | -122.707 | 122.5947 | -0.089794 | 122.5947 | 122.5624 | -0.03235 | -0.1141 | -0.11443 | -0.12708 | -9.2007 | 122.0499 | 0.22169 | 0.34876 | -9.5418 | -9.3509 | 122.5359 | 122.5116 | 122.5113 | 122.5859 | -0.030992 | 113.4251 | 113.0839 | 113.2748 | 121.4356 | -122.7528
2230.2188 | 122.7905 | -122.5342 | -0.022888 | -0.005418 | -0.065557 | 0.061612 | -0.012793 | -0.0085103 | 0.0050275 | -0.019381 | 0.034097 | -0.0044356 | -0.0071509 | 0.026399 | 0.01383 | 0.014783 | 0.001407 | -0.017566 | -0.03944 | -0.068325 | -0.073228 | 0.014784 | -0.52092 | -1.1535 | -122.3537 | -9.1549 | -9.5006 | -9.3097 | -122.707 | 122.549 | -0.016552 | 122.549 | 122.5166 | -0.03235 | -0.045437 | -0.05034 | -0.17285 | -9.132 | 122.0133 | 0.18049 | 0.35334 | -9.4777 | -9.2868 | 122.4947 | 122.4659 | 122.461 | 122.5356 | 0.037672 | 113.3793 | 113.0336 | 113.2245 | 121.3807 | -122.6841
2231.9688 | 122.8592 | -122.5296 | 0.013733 | -0.005418 | -0.065343 | 0.061612 | -0.013007 | -0.0085103 | 0.0052411 | -0.011751 | 0.033883 | -0.0042218 | -0.0071509 | 0.026827 | 0.014257 | 0.019361 | -0.003172 | -0.012988 | -0.03944 | -0.068325 | -0.064071 | 0.014784 | -0.5255 | -1.1535 | -122.3628 | -9.1595 | -9.5006 | -9.3051 | -122.707 | 122.5444 | -0.053173 | 122.549 | 122.5166 | -0.027772 | -0.082058 | -0.077804 | -0.17743 | -9.1732 | 122.0041 | 0.16675 | 0.34418 | -9.5144 | -9.3189 | 122.4902 | 122.4613 | 122.4655 | 122.5264 | 0.001051 | 113.3701 | 113.029 | 113.2245 | 121.3761 | -122.7208
2233.7031 | 122.818 | -122.525 | 0.004578 | -0.005418 | -0.065343 | 0.061398 | -0.01322 | -0.0085103 | 0.0050275 | -0.019381 | 0.034097 | -0.0046492 | -0.0071509 | 0.026827 | 0.01383 | 0.005626 | -0.003172 | -0.012988 | -0.034862 | -0.072904 | -0.06865 | 0.019363 | -0.53008 | -1.1535 | -122.3537 | -9.1503 | -9.4961 | -9.3097 | -122.707 | 122.5444 | -0.03944 | 122.5307 | 122.512 | -0.032351 | -0.077482 | -0.073228 | -0.18201 | -9.1549 | 121.9949 | 0.17133 | 0.35334 | -9.5006 | -9.3143 | 122.4902 | 122.4521 | 122.4564 | 122.5219 | 0.014785 | 113.3747 | 113.029 | 113.2153 | 121.3715 | -122.7116
2235.5 | 122.85 | -122.525 | 0.004578 | 0.002213 | -0.065557 | 0.061185 | -0.013007 | -0.0082965 | 0.0052411 | -0.011751 | 0.033883 | -0.0046492 | -0.0071509 | 0.02704 | 0.014257 | 0.010204 | 0.001407 | -0.017566 | -0.044018 | -0.059167 | -0.077807 | 0.019363 | -0.53466 | -1.1626 | -122.3537 | -9.1503 | -9.4961 | -9.3097 | -122.7116 | 122.5444 | -0.048596 | 122.5352 | 122.5075 | -0.036929 | -0.063745 | -0.082385 | -0.18659 | -9.1549 | 121.9904 | 0.17133 | 0.35792 | -9.5006 | -9.3143 | 122.481 | 122.4659 | 122.4472 | 122.5264 | 0.014785 | 113.3747 | 113.029 | 113.2153 | 121.3624 | -122.7162
2237.2031 | 122.7081 | -122.6028 | 0.032043 | -0.005418 | -0.065557 | 0.061398 | -0.012793 | -0.0085103 | 0.0052411 | -0.019381 | 0.03431 | -0.0044356 | -0.0071509 | 0.026613 | 0.014043 | 0.019361 | 0.005985 | -0.012988 | -0.03944 | -0.068325 | -0.06865 | 0.014784 | -0.53924 | -1.1626 | -122.3583 | -9.1549 | -9.5006 | -9.3143 | -122.707 | 122.6176 | -0.071483 | 122.6222 | 122.5899 | -0.027772 | -0.10037 | -0.10069 | -0.10419 | -9.1869 | 122.0636 | 0.24457 | 0.34876 | -9.5327 | -9.3463 | 122.5634 | 122.5345 | 122.5342 | 122.6088 | -0.017259 | 113.4479 | 113.1022 | 113.2886 | 121.4402 | -122.7391
2238.9688 | 122.7539 | -122.5616 | 0.027466 | -0.013049 | -0.06513 | 0.061826 | -0.013007 | -0.0085103 | 0.0050275 | -0.011751 | 0.033883 | -0.0046492 | -0.0071509 | 0.026613 | 0.013616 | 0.014783 | 0.001407 | -0.012988 | -0.03944 | -0.072904 | -0.077807 | 0.019363 | -0.53466 | -1.1672 | -122.3583 | -9.1503 | -9.4961 | -9.3051 | -122.7116 | 122.581 | -0.066906 | 122.5764 | 122.5487 | -0.032351 | -0.10037 | -0.10527 | -0.14997 | -9.1778 | 122.027 | 0.20338 | 0.35334 | -9.5235 | -9.3326 | 122.5222 | 122.4887 | 122.4838 | 122.5631 | -0.008103 | 113.4113 | 113.0656 | 113.2565 | 121.3944 | -122.7391
2240.7031 | 122.8363 | -122.5433 | -0.004578 | -0.013049 | -0.065557 | 0.061612 | -0.012579 | -0.0087239 | 0.0054549 | -0.011751 | 0.034097 | -0.0046492 | -0.0071509 | 0.026613 | 0.014257 | 0.019361 | 0.001407 | -0.012988 | -0.044018 | -0.059167 | -0.06865 | 0.014784 | -0.53924 | -1.1672 | -122.3583 | -9.1549 | -9.4961 | -9.3143 | -122.7116 | 122.5581 | -0.03944 | 122.5627 | 122.5303 | -0.027772 | -0.054589 | -0.064072 | -0.16828 | -9.1503 | 122.0041 | 0.18506 | 0.35334 | -9.4915 | -9.3097 | 122.4993 | 122.4842 | 122.4747 | 122.5447 | 0.019362 | 113.3884 | 113.0473 | 113.2291 | 121.3761 | -122.707
2242.4062 | 122.7631 | -122.5754 | 0.032043 | -0.013049 | -0.065557 | 0.061398 | -0.013434 | -0.0087239 | 0.0050275 | -0.0041205 | 0.033883 | -0.0044356 | -0.0073645 | 0.026827 | 0.01383 | 0.010204 | -0.003172 | -0.012988 | -0.034862 | -0.072904 | -0.064071 | 0.019363 | -0.53466 | -1.1764 | -122.3674 | -9.1549 | -9.5006 | -9.3097 | -122.7116 | 122.5947 | -0.066905 | 122.5856 | 122.5624 | -0.032351 | -0.10495 | -0.096114 | -0.13623 | -9.1869 | 122.0407 | 0.20795 | 0.34418 | -9.5327 | -9.3417 | 122.5405 | 122.5025 | 122.5113 | 122.5722 | -0.01268 | 113.4205 | 113.0747 | 113.2657 | 121.399 | -122.7437
2244.1094 | 122.731 | -122.5754 | 0.018311 | 0.002213 | -0.065557 | 0.061826 | -0.013007 | -0.0085103 | 0.0050275 | -0.027012 | 0.034097 | -0.0042218 | -0.0075781 | 0.026827 | 0.014043 | 0.010204 | 0.001407 | -0.022144 | -0.044018 | -0.072904 | -0.06865 | 0.014784 | -0.53924 | -1.1809 | -122.3583 | -9.1549 | -9.4961 | -9.3143 | -122.7162 | 122.5902 | -0.062329 | 122.5856 | 122.5532 | -0.036928 | -0.091215 | -0.086961 | -0.14081 | -9.1732 | 122.0361 | 0.21711 | 0.35792 | -9.5144 | -9.3326 | 122.5314 | 122.5025 | 122.5067 | 122.5768 | -0.003527 | 113.4205 | 113.0793 | 113.2611 | 121.3944 | -122.7345
2245.8438 | 122.7081 | -122.6074 | 0.054932 | -0.013049 | -0.065343 | 0.061826 | -0.013007 | -0.0082965 | 0.0050275 | -0.0041205 | 0.034097 | -0.0040082 | -0.0071509 | 0.026613 | 0.014043 | 0.014783 | 0.001407 | -0.017566 | -0.03944 | -0.068325 | -0.059493 | 0.010206 | -0.5484 | -1.1809 | -122.3628 | -9.1503 | -9.4961 | -9.3097 | -122.7116 | 122.6176 | -0.094372 | 122.6222 | 122.5899 | -0.027772 | -0.12326 | -0.11442 | -0.10419 | -9.2052 | 122.059 | 0.24457 | 0.34876 | -9.551 | -9.3646 | 122.568 | 122.5391 | 122.5479 | 122.6088 | -0.044726 | 113.4571 | 113.1114 | 113.2977 | 121.4265 | -122.7665
2247.5469 | 122.8043 | -122.5388 | 0.004578 | -0.005418 | -0.065771 | 0.062039 | -0.012793 | -0.0085103 | 0.0050275 | -0.011751 | 0.03431 | -0.0040082 | -0.0069371 | 0.026613 | 0.01383 | 0.014783 | 0.005985 | -0.012988 | -0.044018 | -0.068325 | -0.064071 | 0.005627 | -0.5484 | -1.1947 | -122.3628 | -9.1595 | -9.4961 | -9.3005 | -122.7116 | 122.5444 | -0.048596 | 122.5535 | 122.5258 | -0.018615 | -0.072903 | -0.068649 | -0.17285 | -9.1641 | 121.9904 | 0.17591 | 0.34876 | -9.5006 | -9.3051 | 122.4947 | 122.4704 | 122.4747 | 122.5447 | 0.001049 | 113.3793 | 113.0427 | 113.2382 | 121.3441 | -122.7162
2249.25 | 122.7081 | -122.6074 | 0.032043 | -0.005418 | -0.065984 | 0.061826 | -0.013007 | -0.0085103 | 0.0052411 | -0.011751 | 0.033883 | -0.0046492 | -0.0073645 | 0.02704 | 0.01383 | 0.014783 | 0.005985 | -0.012988 | -0.044018 | -0.068325 | -0.064071 | 0.010206 | -0.5484 | -1.1901 | -122.3583 | -9.1549 | -9.5006 | -9.3005 | -122.7116 | 122.6176 | -0.076061 | 122.6222 | 122.5944 | -0.023194 | -0.10037 | -0.096114 | -0.10419 | -9.1869 | 122.059 | 0.24915 | 0.35334 | -9.5327 | -9.3326 | 122.5634 | 122.5391 | 122.5434 | 122.6134 | -0.021837 | 113.4525 | 113.1068 | 113.3069 | 121.4173 | -122.7437
2251 | 122.818 | -122.5571 | 0.009155 | -0.013049 | -0.065984 | 0.061398 | -0.01322 | -0.0087239 | 0.0050275 | -0.019381 | 0.03431 | -0.0042218 | -0.0071509 | 0.02704 | 0.014043 | 0.019361 | -0.003172 | -0.017566 | -0.03944 | -0.072904 | -0.06865 | 0.010206 | -0.55756 | -1.1947 | -122.3583 | -9.1549 | -9.5052 | -9.3097 | -122.7116 | 122.5673 | -0.048595 | 122.5764 | 122.5395 | -0.027772 | -0.082059 | -0.077805 | -0.15454 | -9.164 | 121.9995 | 0.1988 | 0.35334 | -9.5144 | -9.3189 | 122.5176 | 122.4842 | 122.4884 | 122.5539 | 0.001051 | 113.4022 | 113.0519 | 113.2474 | 121.3624 | -122.7208
2252.7188 | 122.85 | -122.58 | 0 | 0.002213 | -0.065557 | 0.061612 | -0.012793 | -0.0087239 | 0.0052411 | -0.011751 | 0.034097 | -0.0044356 | -0.0071509 | 0.026827 | 0.014257 | 0.010204 | 0.001407 | -0.017566 | -0.03944 | -0.063746 | -0.064071 | 0.010206 | -0.55756 | -1.1947 | -122.3628 | -9.1595 | -9.4961 | -9.3097 | -122.7162 | 122.5902 | -0.03944 | 122.5902 | 122.5624 | -0.027772 | -0.063746 | -0.064071 | -0.13623 | -9.1595 | 122.0224 | 0.21711 | 0.35334 | -9.4961 | -9.3097 | 122.5405 | 122.5162 | 122.5159 | 122.5814 | 0.010206 | 113.4205 | 113.0839 | 113.2703 | 121.3853 | -122.7162
2254.4219 | 122.8546 | -122.5296 | -0.013733 | -0.005418 | -0.065984 | 0.061826 | -0.01322 | -0.0087239 | 0.0050275 | -0.019381 | 0.03431 | -0.0044356 | -0.0071509 | 0.02704 | 0.01383 | 0.014783 | 0.001407 | -0.017566 | -0.03944 | -0.068325 | -0.06865 | 0.014784 | -0.55756 | -1.1993 | -122.3583 | -9.1503 | -9.4915 | -9.3143 | -122.7162 | 122.5444 | -0.025707 | 122.5444 | 122.512 | -0.03235 | -0.054592 | -0.054917 | -0.18659 | -9.1366 | 121.972 | 0.17133 | 0.35792 | -9.4777 | -9.3006 | 122.4902 | 122.4613 | 122.461 | 122.531 | 0.028517 | 113.3793 | 113.0381 | 113.2153 | 121.3303 | -122.7025
2256.1562 | 122.7997 | -122.5708 | -0.009155 | 0.002213 | -0.065771 | 0.061612 | -0.013434 | -0.0085103 | 0.0050275 | -0.011751 | 0.034097 | -0.0046492 | -0.0073645 | 0.02704 | 0.01383 | 0.010204 | -0.003172 | -0.017566 | -0.03944 | -0.063746 | -0.073228 | 0.005627 | -0.56671 | -1.2038 | -122.3628 | -9.1549 | -9.4915 | -9.3051 | -122.7208 | 122.5764 | -0.030285 | 122.581 | 122.5532 | -0.023193 | -0.054591 | -0.064073 | -0.14997 | -9.1457 | 122.0041 | 0.20795 | 0.35792 | -9.4823 | -9.296 | 122.5314 | 122.5071 | 122.4976 | 122.5676 | 0.014782 | 113.4159 | 113.0793 | 113.2657 | 121.367 | -122.7116
2257.9062 | 122.7951 | -122.5662 | 0 | -0.005418 | -0.065557 | 0.061398 | -0.013007 | -0.0087239 | 0.0050275 | -0.011751 | 0.034097 | -0.0044356 | -0.0071509 | 0.026827 | 0.01383 | 0.014783 | 0.001407 | -0.017566 | -0.044018 | -0.068325 | -0.064071 | 0.010206 | -0.56671 | -1.2038 | -122.3628 | -9.1503 | -9.4961 | -9.3097 | -122.7162 | 122.5764 | -0.044018 | 122.581 | 122.5487 | -0.027772 | -0.068325 | -0.064071 | -0.14997 | -9.1503 | 121.9995 | 0.20337 | 0.35334 | -9.4961 | -9.3097 | 122.5222 | 122.4979 | 122.5022 | 122.5676 | 0.010206 | 113.4159 | 113.0702 | 113.2565 | 121.3624 | -122.7162
2259.6406 | 122.7814 | -122.5754 | 0.009155 | -0.005418 | -0.065557 | 0.061398 | -0.013007 | -0.0087239 | 0.0050275 | -0.011751 | 0.033669 | -0.0044356 | -0.0071509 | 0.027254 | 0.01383 | 0.010204 | 0.005985 | -0.012988 | -0.044018 | -0.068325 | -0.06865 | 0.010206 | -0.56671 | -1.2084 | -122.3674 | -9.1549 | -9.4869 | -9.3051 | -122.7162 | 122.5856 | -0.053173 | 122.5856 | 122.5624 | -0.023194 | -0.07748 | -0.077805 | -0.14081 | -9.164 | 122.0087 | 0.20795 | 0.34876 | -9.496 | -9.3143 | 122.5314 | 122.5071 | 122.5067 | 122.5814 | 0.001051 | 113.4205 | 113.0885 | 113.2703 | 121.367 | -122.7253
2261.3438 | 122.8455 | -122.5525 | 0 | -0.013049 | -0.065557 | 0.061398 | -0.013434 | -0.0085103 | 0.0048139 | -0.011751 | 0.034097 | -0.0044356 | -0.0071509 | 0.026827 | 0.01383 | 0.014783 | 0.001407 | -0.017566 | -0.034862 | -0.072904 | -0.059493 | 0.014784 | -0.56671 | -1.213 | -122.372 | -9.1549 | -9.4961 | -9.3051 | -122.7162 | 122.5673 | -0.034862 | 122.5673 | 122.5349 | -0.03235 | -0.072904 | -0.059493 | -0.1637 | -9.1549 | 121.9858 | 0.18048 | 0.34418 | -9.4961 | -9.3051 | 122.5176 | 122.4796 | 122.493 | 122.5539 | 0.014784 | 113.3976 | 113.0564 | 113.2474 | 121.3395 | -122.7162
2263.0781 | 122.7814 | -122.5708 | 0.009155 | -0.013049 | -0.065771 | 0.061612 | -0.01322 | -0.0087239 | 0.0046001 | -0.011751 | 0.034097 | -0.0044356 | -0.0073645 | 0.02704 | 0.014043 | 0.010204 | 0.005985 | -0.012988 | -0.03944 | -0.059167 | -0.06865 | 0.019363 | -0.57129 | -1.2222 | -122.372 | -9.1457 | -9.4961 | -9.3097 | -122.7208 | 122.5902 | -0.048595 | 122.581 | 122.5578 | -0.032351 | -0.068322 | -0.077805 | -0.14997 | -9.1549 | 121.9995 | 0.1988 | 0.34876 | -9.5052 | -9.3189 | 122.5314 | 122.5116 | 122.5022 | 122.5768 | 0.010208 | 113.4251 | 113.0748 | 113.2611 | 121.3486 | -122.7299
2264.8281 | 122.7173 | -122.6074 | 0.032043 | -0.005418 | -0.065984 | 0.061826 | -0.012793 | -0.0082965 | 0.0048139 | -0.011751 | 0.033883 | -0.0044356 | -0.0071509 | 0.026613 | 0.013616 | 0.014783 | -0.003172 | -0.017566 | -0.044018 | -0.063746 | -0.073228 | 0.005627 | -0.57129 | -1.2176 | -122.372 | -9.1549 | -9.4915 | -9.3189 | -122.7253 | 122.613 | -0.076061 | 122.6222 | 122.5899 | -0.023193 | -0.095789 | -0.10527 | -0.11793 | -9.1869 | 122.0361 | 0.23542 | 0.35334 | -9.5235 | -9.3509 | 122.5634 | 122.5437 | 122.5342 | 122.6042 | -0.026416 | 113.4525 | 113.1159 | 113.2886 | 121.3898 | -122.7574
2266.5312 | 122.7905 | -122.5433 | 0.004578 | -0.02068 | -0.065771 | 0.061612 | -0.013007 | -0.0085103 | 0.0050275 | -0.027012 | 0.033883 | -0.0044356 | -0.0073645 | 0.026827 | 0.014043 | 0.010204 | 0.005985 | -0.022144 | -0.03944 | -0.063746 | -0.06865 | 0.014784 | -0.58045 | -1.2222 | -122.372 | -9.1549 | -9.5006 | -9.3097 | -122.7253 | 122.5581 | -0.044018 | 122.5535 | 122.5212 | -0.036928 | -0.068324 | -0.073228 | -0.18201 | -9.1595 | 121.9629 | 0.17133 | 0.35334 | -9.5052 | -9.3143 | 122.5039 | 122.4796 | 122.4747 | 122.5493 | 0.010206 | 113.3884 | 113.0427 | 113.2336 | 121.3212 | -122.7299
2268.2344 | 122.731 | -122.6074 | 0.050354 | 0.002213 | -0.065984 | 0.061612 | -0.013434 | -0.0087239 | 0.0050275 | -0.011751 | 0.033883 | -0.0044356 | -0.0071509 | 0.027254 | 0.01383 | 0.014783 | -0.003172 | -0.012988 | -0.03944 | -0.063746 | -0.06865 | 0.014784 | -0.57587 | -1.2267 | -122.3674 | -9.1549 | -9.5006 | -9.3097 | -122.7162 | 122.6222 | -0.089794 | 122.6222 | 122.5944 | -0.027772 | -0.1141 | -0.119 | -0.10877 | -9.2052 | 122.0316 | 0.23999 | 0.34876 | -9.551 | -9.3601 | 122.568 | 122.5437 | 122.5388 | 122.6042 | -0.03557 | 113.4525 | 113.1068 | 113.2977 | 121.3807 | -122.7665
2270 | 122.7219 | -122.6028 | 0.041199 | -0.005418 | -0.065557 | 0.061398 | -0.013007 | -0.0085103 | 0.0048139 | -0.011751 | 0.033669 | -0.0044356 | -0.0071509 | 0.02704 | 0.01383 | 0.014783 | 0.005985 | -0.017566 | -0.044018 | -0.072904 | -0.064071 | 0.010206 | -0.57587 | -1.2313 | -122.3674 | -9.1503 | -9.5006 | -9.3097 | -122.7253 | 122.6131 | -0.085217 | 122.6176 | 122.5853 | -0.027772 | -0.1141 | -0.10527 | -0.1225 | -9.1915 | 122.027 | 0.23542 | 0.35792 | -9.5418 | -9.3509 | 122.5588 | 122.5299 | 122.5388 | 122.6088 | -0.030993 | 113.4525 | 113.1022 | 113.2931 | 121.3715 | -122.7665
2271.7031 | 122.8683 | -122.5342 | 0 | -0.005418 | -0.065984 | 0.061612 | -0.013434 | -0.0082965 | 0.0052411 | -0.011751 | 0.033883 | -0.0044356 | -0.0075781 | 0.027254 | 0.014043 | 0.010204 | 0.001407 | -0.022144 | -0.03944 | -0.068325 | -0.06865 | 0.010206 | -0.58503 | -1.2359 | -122.372 | -9.1503 | -9.4961 | -9.3143 | -122.7162 | 122.5444 | -0.03944 | 122.5444 | 122.512 | -0.03235 | -0.068325 | -0.06865 | -0.18201 | -9.1503 | 121.9492 | 0.16217 | 0.34418 | -9.4961 | -9.3143 | 122.4947 | 122.4659 | 122.4655 | 122.5356 | 0.010206 | 113.3839 | 113.0381 | 113.2199 | 121.2983 | -122.7162
2273.4062 | 122.7356 | -122.5616 | 0.013733 | -0.013049 | -0.065984 | 0.061826 | -0.01322 | -0.0087239 | 0.0046001 | -0.011751 | 0.03431 | -0.0046492 | -0.0073645 | 0.02704 | 0.013402 | 0.014783 | 0.001407 | -0.017566 | -0.034862 | -0.068325 | -0.06865 | 0.019363 | -0.58503 | -1.2405 | -122.372 | -9.1457 | -9.5006 | -9.3005 | -122.7253 | 122.581 | -0.048595 | 122.5764 | 122.5441 | -0.036929 | -0.082058 | -0.082383 | -0.1637 | -9.1595 | 121.9766 | 0.18964 | 0.35334 | -9.5144 | -9.3143 | 122.5268 | 122.4933 | 122.493 | 122.5631 | 0.00563 | 113.4159 | 113.061 | 113.2611 | 121.3212 | -122.7391
2275.1094 | 122.731 | -122.58 | 0.054932 | -0.013049 | -0.065771 | 0.061612 | -0.013007 | -0.0087239 | 0.0050275 | -0.0041205 | 0.033669 | -0.0048628 | -0.0071509 | 0.02704 | 0.014043 | 0.010204 | 0.001407 | -0.022144 | -0.03944 | -0.068325 | -0.064071 | 0.010206 | -0.58045 | -1.2405 | -122.372 | -9.1503 | -9.4961 | -9.3097 | -122.7253 | 122.5902 | -0.094372 | 122.5902 | 122.5578 | -0.03235 | -0.12326 | -0.119 | -0.14539 | -9.2052 | 121.9995 | 0.20795 | 0.35334 | -9.551 | -9.3646 | 122.5405 | 122.5116 | 122.5159 | 122.5814 | -0.044726 | 113.4296 | 113.0839 | 113.2703 | 121.3395 | -122.7803
2276.8594 | 122.85 | -122.5754 | 0.009155 | 0.009844 | -0.065984 | 0.061185 | -0.01322 | -0.0089375 | 0.0048139 | -0.0041205 | 0.032388 | -0.00294 | -0.0069371 | 0.02704 | 0.014043 | 0.014783 | 0.001407 | -0.017566 | -0.044018 | -0.063746 | -0.064071 | 0.010206 | -0.58503 | -1.2405 | -122.3674 | -9.1457 | -9.4961 | -9.3097 | -122.7208 | 122.5856 | -0.053173 | 122.5902 | 122.5578 | -0.027772 | -0.072901 | -0.073226 | -0.14539 | -9.1549 | 121.9904 | 0.20795 | 0.35334 | -9.5052 | -9.3189 | 122.5314 | 122.5116 | 122.5113 | 122.5768 | 0.001051 | 113.4296 | 113.0793 | 113.2657 | 121.3349 | -122.7299
2278.5469 | 122.7264 | -122.6028 | 0.045776 | -0.005418 | -0.065557 | 0.061612 | -0.012793 | -0.0087239 | 0.0050275 | -0.027012 | 0.032388 | -0.0027262 | -0.0073645 | 0.027468 | 0.013616 | 0.014783 | 0.005985 | -0.017566 | -0.03944 | -0.059167 | -0.064071 | 0.014784 | -0.58503 | -1.2359 | -122.3766 | -9.1503 | -9.4961 | -9.3051 | -122.7253 | 122.6176 | -0.085216 | 122.6176 | 122.5853 | -0.03235 | -0.10494 | -0.10985 | -0.1225 | -9.1961 | 122.0178 | 0.22626 | 0.34876 | -9.5418 | -9.3509 | 122.5634 | 122.5437 | 122.5388 | 122.6088 | -0.030992 | 113.4525 | 113.1068 | 113.2977 | 121.367 | -122.7711
2280.2812 | 122.7722 | -122.5845 | 0.032043 | -0.005418 | -0.065984 | 0.061612 | -0.01322 | -0.0087239 | 0.0050275 | -0.019381 | 0.032815 | -0.00294 | -0.0071509 | 0.02704 | 0.01383 | 0.014783 | 0.001407 | -0.017566 | -0.03944 | -0.063746 | -0.06865 | 0.010206 | -0.58961 | -1.245 | -122.3674 | -9.1457 | -9.4961 | -9.3051 | -122.7253 | 122.5947 | -0.071483 | 122.5993 | 122.567 | -0.027772 | -0.095789 | -0.10069 | -0.14081 | -9.1778 | 121.9949 | 0.21711 | 0.35792 | -9.5281 | -9.3372 | 122.5451 | 122.5208 | 122.5159 | 122.5859 | -0.021837 | 113.4388 | 113.0885 | 113.2794 | 121.3395 | -122.7574
2282.0312 | 122.8409 | -122.5708 | -0.009155 | -0.005418 | -0.066412 | 0.061185 | -0.013434 | -0.0085103 | 0.0052411 | -0.0041205 | 0.032601 | -0.0031536 | -0.0073645 | 0.027254 | 0.01383 | 0.019361 | 0.001407 | -0.017566 | -0.034862 | -0.063746 | -0.064071 | 0.010206 | -0.59418 | -1.245 | -122.372 | -9.1503 | -9.4915 | -9.3097 | -122.7253 | 122.581 | -0.025707 | 122.5902 | 122.5532 | -0.027772 | -0.054591 | -0.054916 | -0.15455 | -9.1412 | 121.9766 | 0.1988 | 0.35334 | -9.4823 | -9.3005 | 122.5359 | 122.5071 | 122.5067 | 122.5722 | 0.019361 | 113.4205 | 113.0793 | 113.2611 | 121.3258 | -122.7162
2283.75 | 122.7402 | -122.6166 | 0.041199 | -0.005418 | -0.065984 | 0.061826 | -0.01322 | -0.0089375 | 0.0046001 | -0.0041205 | 0.032601 | -0.00294 | -0.0071509 | 0.027254 | 0.01383 | 0.019361 | 0.001407 | -0.017566 | -0.03944 | -0.063746 | -0.06865 | 0.010206 | -0.59418 | -1.2405 | -122.372 | -9.1549 | -9.4915 | -9.3051 | -122.7345 | 122.6268 | -0.080639 | 122.6359 | 122.599 | -0.027772 | -0.10494 | -0.10985 | -0.11793 | -9.1961 | 122.0224 | 0.24457 | 0.3625 | -9.5327 | -9.3463 | 122.5771 | 122.5528 | 122.5479 | 122.618 | -0.030993 | 113.4617 | 113.1251 | 113.3115 | 121.3761 | -122.7757
2285.4531 | 122.7997 | -122.5616 | 0.022888 | -0.013049 | -0.066412 | 0.061612 | -0.013434 | -0.0087239 | 0.0050275 | -0.027012 | 0.032388 | -0.00294 | -0.0071509 | 0.02704 | 0.01383 | 0.010204 | 0.001407 | -0.017566 | -0.03944 | -0.063746 | -0.06865 | 0.014784 | -0.58961 | -1.2496 | -122.372 | -9.1503 | -9.5052 | -9.3051 | -122.7299 | 122.5764 | -0.062328 | 122.5718 | 122.5441 | -0.03235 | -0.086634 | -0.091538 | -0.16828 | -9.1732 | 121.972 | 0.18964 | 0.35792 | -9.5281 | -9.328 | 122.5222 | 122.4979 | 122.493 | 122.5631 | -0.008104 | 113.4113 | 113.0564 | 113.2565 | 121.312 | -122.7528
2287.1562 | 122.7676 | -122.5937 | 0.032043 | 0.002213 | -0.066412 | 0.061612 | -0.012793 | -0.0087239 | 0.0048139 | -0.0041205 | 0.032601 | -0.00294 | -0.0071509 | 0.026827 | 0.01383 | 0.019361 | 0.001407 | -0.022144 | -0.044018 | -0.063746 | -0.06865 | 0.005627 | -0.60334 | -1.2496 | -122.3766 | -9.1503 | -9.4961 | -9.3097 | -122.7299 | 122.5993 | -0.076061 | 122.6131 | 122.5715 | -0.027771 | -0.095789 | -0.10069 | -0.13624 | -9.1824 | 121.9903 | 0.2171 | 0.35334 | -9.5281 | -9.3417 | 122.5497 | 122.5299 | 122.525 | 122.5951 | -0.026416 | 113.4434 | 113.0976 | 113.284 | 121.3441 | -122.762
2288.875 | 122.7264 | -122.5983 | 0.027466 | -0.005418 | -0.065984 | 0.061612 | -0.01322 | -0.0089375 | 0.0048139 | -0.019381 | 0.032601 | -0.0025126 | -0.0073645 | 0.02704 | 0.014043 | 0.019361 | 0.010564 | -0.017566 | -0.034862 | -0.068325 | -0.064071 | 0.010206 | -0.60334 | -1.2542 | -122.372 | -9.1549 | -9.4915 | -9.3005 | -122.7345 | 122.6085 | -0.062328 | 122.6176 | 122.5807 | -0.027772 | -0.095791 | -0.091537 | -0.13624 | -9.1824 | 121.9949 | 0.22626 | 0.3625 | -9.5189 | -9.328 | 122.5634 | 122.5299 | 122.5342 | 122.6088 | -0.01726 | 113.4434 | 113.1068 | 113.2977 | 121.3441 | -122.762
2290.5781 | 122.8226 | -122.5891 | 0.004578 | -0.013049 | -0.065984 | 0.061612 | -0.01322 | -0.0085103 | 0.0048139 | -0.011751 | 0.032815 | -0.00294 | -0.0071509 | 0.02704 | 0.013402 | 0.010204 | -0.003172 | -0.012988 | -0.034862 | -0.068325 | -0.064071 | 0.005627 | -5.6353 | -1.2634 | -122.3674 | -9.1503 | -9.4961 | -9.3051 | -122.7345 | 122.5947 | -0.03944 | 122.5993 | 122.5761 | -0.018615 | -0.072903 | -0.068649 | -0.14539 | -9.1549 | 116.9538 | 0.22168 | 0.36708 | -9.5006 | -9.3097 | 122.5542 | 122.5208 | 122.525 | 122.5859 | 0.001049 | 113.4388 | 113.0931 | 113.284 | 121.3257 | -122.7391
2292.2969 | 122.7036 | -122.6212 | 0.018311 | -0.013049 | -0.066625 | 0.061612 | -0.01322 | -0.0082965 | 0.0050275 | -0.019381 | 0.032601 | -0.00294 | -0.0073645 | 0.027254 | 0.01383 | 0.014783 | 0.001407 | -0.017566 | -0.034862 | -0.068325 | -0.06865 | 0.014784 | -118.1571 | -1.3824 | -122.372 | -9.1503 | -9.4915 | -9.3051 | -122.7299 | 122.6359 | -0.053173 | 122.6359 | 122.6036 | -0.03235 | -0.086636 | -0.086961 | -0.10877 | -9.1686 | 4.464 | 0.24915 | 0.35792 | -9.5098 | -9.3234 | 122.5863 | 122.5528 | 122.5525 | 122.6226 | -0.003527 | 113.4708 | 113.1297 | 113.316 | 121.2387 | -122.7482
2293.9844 | 122.8867 | -122.5662 | 0 | -0.013049 | -0.066412 | 0.061612 | -0.013007 | -0.0087239 | 0.0050275 | -0.011751 | 0.033029 | -0.0033672 | -0.0071509 | 0.027254 | 0.01383 | 0.010204 | -0.003172 | -0.022144 | -0.034862 | -0.068325 | -0.064071 | 0.014784 | -121.8888 | -1.3641 | -122.3766 | -9.1503 | -9.4915 | -9.3051 | -122.7345 | 122.581 | -0.034862 | 122.5764 | 122.5441 | -0.036928 | -0.068325 | -0.064071 | -0.16828 | -9.1503 | 0.67744 | 0.18964 | 0.35792 | -9.4915 | -9.3051 | 122.5314 | 122.4979 | 122.5022 | 122.5631 | 0.014784 | 113.4159 | 113.0748 | 113.2611 | 121.2021 | -122.7345
2295.7812 | 122.85 | -122.5525 | 0.013733 | 0.002213 | -0.066412 | 0.061398 | -0.01322 | -0.0087239 | 0.0048139 | -0.027012 | 0.032601 | -0.0033672 | -0.0077917 | 0.02704 | 0.01383 | 0.010204 | 0.005985 | -0.017566 | -0.03944 | -0.063746 | -0.059493 | 0.010206 | -122.6809 | -1.3549 | -122.3766 | -9.1412 | -9.4869 | -9.3005 | -122.7299 | 122.5627 | -0.053173 | 122.5627 | 122.5349 | -0.027772 | -0.077479 | -0.073226 | -0.17744 | -9.1549 | -0.12841 | 0.17591 | 0.35334 | -9.5006 | -9.3143 | 122.5131 | 122.4887 | 122.493 | 122.5585 | -0.003527 | 113.4113 | 113.0656 | 113.2519 | 121.1976 | -122.7437
2297.4844 | 122.8638 | -122.5708 | 0 | 0.002213 | -0.065984 | 0.061826 | -0.01322 | -0.0089375 | 0.0048139 | -0.011751 | 0.032601 | -0.0027262 | -0.0071509 | 0.027254 | 0.014043 | 0.010204 | 0.001407 | -0.017566 | -0.03944 | -0.068325 | -0.06865 | 0.010206 | -122.6901 | -1.3504 | -122.3766 | -9.1503 | -9.4961 | -9.3097 | -122.7345 | 122.581 | -0.03944 | 122.581 | 122.5532 | -0.027772 | -0.068325 | -0.06865 | -0.1637 | -9.1503 | -0.11926 | 0.19422 | 0.35792 | -9.4961 | -9.3097 | 122.5314 | 122.5025 | 122.5022 | 122.5722 | 0.010206 | 113.4205 | 113.0748 | 113.2611 | 121.2204 | -122.7345
2299.1875 | 122.8775 | -122.5525 | 0.013733 | -0.02068 | -0.065984 | 0.061826 | -0.013434 | -0.0089375 | 0.0050275 | -0.0041205 | 0.032601 | -0.0031536 | -0.0075781 | 0.027254 | 0.013616 | 0.010204 | 0.001407 | -0.017566 | -0.03944 | -0.077483 | -0.059493 | 0.014784 | -122.6946 | -1.3412 | -122.3766 | -9.1457 | -9.4915 | -9.3051 | -122.7345 | 122.5673 | -0.053173 | 122.5627 | 122.5349 | -0.03235 | -0.091216 | -0.073226 | -0.18202 | -9.1595 | -0.14215 | 0.17591 | 0.35792 | -9.5052 | -9.3189 | 122.5131 | 122.475 | 122.493 | 122.5539 | 0.001051 | 113.4068 | 113.061 | 113.2474 | 121.2113 | -122.7482
2300.875 | 122.7768 | -122.5891 | 0.027466 | 0.002213 | -0.065771 | 0.061612 | -0.013434 | -0.0087239 | 0.0043865 | -0.019381 | 0.032815 | -0.00294 | -0.0069371 | 0.027254 | 0.014043 | 0.010204 | -0.007751 | -0.012988 | -0.044018 | -0.059167 | -0.064071 | 0.010206 | -122.6901 | -1.3504 | -122.3812 | -9.1549 | -9.4961 | -9.3051 | -122.7299 | 122.5993 | -0.071484 | 122.5993 | 122.5761 | -0.023194 | -0.086633 | -0.091537 | -0.14082 | -9.1824 | -0.10095 | 0.20795 | 0.34876 | -9.5235 | -9.3326 | 122.5451 | 122.5299 | 122.525 | 122.5814 | -0.01726 | 113.4342 | 113.0931 | 113.284 | 121.2388 | -122.7574
2302.5781 | 122.8592 | -122.5845 | 0.013733 | 0.002213 | -0.066198 | 0.061185 | -0.013648 | -0.0085103 | 0.0043865 | -0.027012 | 0.033029 | -0.0031536 | -0.0075781 | 0.026827 | 0.014257 | 0.014783 | -0.003172 | -0.017566 | -0.034862 | -0.068325 | -0.059493 | 0.010206 | -122.6946 | -1.3504 | -122.6788 | -9.1457 | -9.4961 | -9.3097 | -122.7391 | 122.5947 | -0.048595 | 122.5993 | 122.567 | -0.027772 | -0.082058 | -0.073226 | -0.15455 | -9.1595 | -0.11011 | -0.094246 | 0.060305 | -9.5098 | -9.3234 | 122.5497 | 122.5162 | 122.525 | 122.5814 | -0.003527 | 113.4388 | 113.0885 | 113.2748 | 121.2342 | -122.7528
2304.2969 | 122.7264 | -122.6074 | 0.036621 | 0.002213 | -0.065984 | 0.061612 | -0.013007 | -0.0087239 | 0.0048139 | -0.011751 | 0.033029 | -0.0025126 | -0.0069371 | 0.026827 | 0.014257 | 0.014783 | 0.001407 | -0.012988 | -0.03944 | -0.068325 | -0.06865 | 0.019363 | -122.6901 | -1.3504 | -122.6834 | -9.1457 | -9.4961 | -9.3097 | -122.7391 | 122.6268 | -0.076061 | 122.6222 | 122.5944 | -0.032351 | -0.10495 | -0.10527 | -0.13166 | -9.1824 | -0.08264 | -0.075936 | 0.055727 | -9.5327 | -9.3463 | 122.568 | 122.5391 | 122.5388 | 122.6088 | -0.017258 | 113.4617 | 113.1114 | 113.2977 | 121.2571 | -122.7757
2306.0156 | 122.85 | -122.5616 | 0 | 0.002213 | -0.066412 | 0.061612 | -0.013434 | -0.0087239 | 0.0048139 | -0.019381 | 0.033029 | -0.0027262 | -0.0071509 | 0.02704 | 0.014043 | 0.005626 | 0.001407 | -0.012988 | -0.044018 | -0.068325 | -0.064071 | 0.010206 | -122.6992 | -1.3549 | -122.6879 | -9.1457 | -9.4915 | -9.3005 | -122.7345 | 122.5719 | -0.044018 | 122.5673 | 122.5487 | -0.023194 | -0.068325 | -0.064071 | -0.17286 | -9.1457 | -0.13757 | -0.12629 | 0.046569 | -9.4915 | -9.3005 | 122.5176 | 122.4933 | 122.4976 | 122.5631 | 0.010206 | 113.4159 | 113.0702 | 113.2611 | 121.2067 | -122.7345
2307.7188 | 122.7676 | -122.6028 | 0.022888 | 0.002213 | -0.066198 | 0.061612 | -0.013434 | -0.0082965 | 0.0046001 | -0.011751 | 0.032601 | -0.00294 | -0.0073645 | 0.026827 | 0.014257 | 0.005626 | -0.003172 | -0.017566 | -0.03944 | -0.072904 | -0.06865 | 0.014784 | -122.6992 | -1.3595 | -122.6925 | -9.1503 | -9.4915 | -9.3051 | -122.7391 | 122.6176 | -0.062328 | 122.6085 | 122.5853 | -0.03235 | -0.095792 | -0.091538 | -0.13624 | -9.1732 | -0.096375 | -0.089672 | 0.046569 | -9.5144 | -9.328 | 122.5634 | 122.5299 | 122.5342 | 122.5997 | -0.008104 | 113.4525 | 113.1114 | 113.2977 | 121.2433 | -122.762
2309.4531 | 122.7402 | -122.612 | 0.027466 | -0.013049 | -0.066198 | 0.061612 | -0.013434 | -0.0082965 | 0.0048139 | -0.0041205 | 0.033029 | -0.0025126 | -0.0073645 | 0.026613 | 0.014257 | 0.005626 | 0.005985 | -0.012988 | -0.044018 | -0.063746 | -0.064071 | 0.005627 | -122.6992 | -1.3641 | -122.6834 | -9.1412 | -9.4961 | -9.3097 | -122.7299 | 122.6176 | -0.071484 | 122.6176 | 122.599 | -0.018615 | -0.091212 | -0.091537 | -0.11793 | -9.1686 | -0.087219 | -0.071358 | 0.046569 | -9.5235 | -9.3372 | 122.568 | 122.5483 | 122.5479 | 122.618 | -0.021839 | 113.4708 | 113.1159 | 113.3023 | 121.2479 | -122.7574
2311.1719 | 122.8729 | -122.5708 | -0.009155 | -0.013049 | -0.066412 | 0.061826 | -0.01322 | -0.0087239 | 0.0048139 | -0.019381 | 0.032815 | -0.0027262 | -0.0071509 | 0.02704 | 0.014257 | 0.005626 | -0.007751 | -0.012988 | -0.044018 | -0.063746 | -0.059493 | 0.010206 | -122.7084 | -1.3778 | -122.6879 | -9.1503 | -9.4961 | -9.3097 | -122.7299 | 122.581 | -0.034863 | 122.5764 | 122.5578 | -0.023194 | -0.054591 | -0.050338 | -0.15913 | -9.1412 | -0.13757 | -0.11714 | 0.04199 | -9.4869 | -9.3005 | 122.5268 | 122.5071 | 122.5113 | 122.5631 | 0.019361 | 113.4205 | 113.0748 | 113.2611 | 121.193 | -122.7208
2312.9219 | 122.8134 | -122.5616 | -0.004578 | -0.02068 | -0.066412 | 0.061612 | -0.01322 | -0.0087239 | 0.0041729 | -0.019381 | 0.032601 | -0.0027262 | -0.0073645 | 0.02704 | 0.014043 | 0.014783 | 0.001407 | -0.008409 | -0.048597 | -0.063746 | -0.064071 | 0.014784 | -122.7038 | -1.3733 | -122.6879 | -9.1457 | -9.4823 | -9.3005 | -122.7437 | 122.5764 | -0.044019 | 122.5764 | 122.5532 | -0.023193 | -0.059168 | -0.059493 | -0.18202 | -9.1412 | -0.14215 | -0.12629 | 0.055727 | -9.4777 | -9.296 | 122.513 | 122.4979 | 122.4976 | 122.5631 | 0.019362 | 113.4159 | 113.0793 | 113.2611 | 121.1884 | -122.7391
2314.625 | 122.7631 | -122.5983 | 0.041199 | -0.005418 | -0.066412 | 0.061826 | -0.013434 | -0.0085103 | 0.0046001 | -0.011751 | 0.032815 | -0.0031536 | -0.0071509 | 0.026827 | 0.014043 | 0.010204 | 0.001407 | -0.008409 | -0.034862 | -0.063746 | -0.059493 | 0.005627 | -122.7038 | -1.3824 | -122.6971 | -9.1457 | -9.4869 | -9.3051 | -122.7345 | 122.6039 | -0.076061 | 122.6085 | 122.5899 | -0.014036 | -0.10494 | -0.10069 | -0.13624 | -9.1869 | -0.10553 | -0.098828 | 0.037411 | -9.5281 | -9.3463 | 122.5634 | 122.5345 | 122.5388 | 122.5997 | -0.035572 | 113.4525 | 113.1114 | 113.2931 | 121.2159 | -122.7757
2316.3438 | 122.8363 | -122.5937 | -0.013733 | -0.005418 | -0.066412 | 0.061612 | -0.013648 | -0.0082965 | 0.0048139 | -0.027012 | 0.032815 | -0.00294 | -0.0077917 | 0.02704 | 0.01383 | 0.014783 | -0.003172 | -0.012988 | -0.03944 | -0.068325 | -0.064071 | 0.010206 | -122.6992 | -1.387 | -122.6925 | -9.1549 | -9.4915 | -9.3005 | -122.7437 | 122.6039 | -0.025707 | 122.6085 | 122.5807 | -0.023194 | -0.054592 | -0.050338 | -0.14997 | -9.1412 | -0.10553 | -0.098827 | 0.051148 | -9.4777 | -9.2868 | 122.5542 | 122.5254 | 122.5296 | 122.5905 | 0.023939 | 113.4388 | 113.1022 | 113.2931 | 121.2067 | -122.7299
2318.0625 | 122.8317 | -122.5937 | 0.013733 | -0.005418 | -0.066625 | 0.062039 | -0.01322 | -0.0089375 | 0.0052411 | -0.019381 | 0.032601 | -0.0027262 | -0.0071509 | 0.027254 | 0.014257 | 0.010204 | 0.005985 | -0.012988 | -0.034862 | -0.063746 | -0.059493 | 0.014784 | -122.6992 | -1.3916 | -122.6971 | -9.1412 | -9.4961 | -9.3005 | -122.7482 | 122.6085 | -0.048595 | 122.6039 | 122.5807 | -0.027772 | -0.077479 | -0.073226 | -0.15455 | -9.1549 | -0.10553 | -0.10341 | 0.051148 | -9.5098 | -9.3143 | 122.5588 | 122.5299 | 122.5342 | 122.5997 | 0.001051 | 113.4525 | 113.0976 | 113.2931 | 121.2021 | -122.762
2319.75 | 122.8043 | -122.5754 | 0.022888 | -0.013049 | -0.066625 | 0.061826 | -0.013434 | -0.0087239 | 0.0048139 | -0.019381 | 0.032601 | -0.00294 | -0.0069371 | 0.02704 | 0.014043 | 0.010204 | 0.010564 | -0.008409 | -0.03944 | -0.072904 | -0.064071 | 0.014784 | -122.7084 | -1.3916 | -122.6925 | -9.1457 | -9.4869 | -9.3051 | -122.7437 | 122.5902 | -0.062328 | 122.5856 | 122.567 | -0.023193 | -0.095792 | -0.086959 | -0.16829 | -9.1686 | -0.133 | -0.11714 | 0.051148 | -9.5098 | -9.328 | 122.5359 | 122.5025 | 122.5113 | 122.5859 | -0.008104 | 113.4296 | 113.0885 | 113.2703 | 121.1838 | -122.7666
2321.4531 | 122.7768 | -122.5891 | 0.027466 | -0.02068 | -0.066198 | 0.061826 | -0.013434 | -0.0085103 | 0.0048139 | -0.0041205 | 0.032815 | -0.0025126 | -0.0073645 | 0.02704 | 0.01383 | 0.010204 | 0.001407 | -0.012988 | -0.034862 | -0.068325 | -0.064071 | 0.010206 | -122.7084 | -1.3961 | -122.6925 | -9.1503 | -9.4961 | -9.3005 | -122.7391 | 122.5993 | -0.062328 | 122.5993 | 122.5761 | -0.023194 | -0.095791 | -0.091537 | -0.14997 | -9.1778 | -0.11926 | -0.1034 | 0.046569 | -9.5235 | -9.328 | 122.5542 | 122.5208 | 122.525 | 122.5905 | -0.01726 | 113.4388 | 113.0931 | 113.2886 | 121.193 | -122.7666
2323.1719 | 122.8409 | -122.58 | 0.004578 | -0.005418 | -0.066625 | 0.061612 | -0.013434 | -0.0082965 | 0.0043865 | -0.027012 | 0.032815 | -0.0033672 | -0.0075781 | 0.02704 | 0.014043 | 0.014783 | 0.001407 | -0.008409 | -0.03944 | -0.063746 | -0.064071 | 0.005627 | -122.713 | -1.3961 | -122.6971 | -9.1457 | -9.4869 | -9.3051 | -122.7391 | 122.5856 | -0.044018 | 122.5947 | 122.5715 | -0.014036 | -0.068324 | -0.068649 | -0.15913 | -9.1503 | -0.133 | -0.11714 | 0.04199 | -9.4915 | -9.3097 | 122.5405 | 122.5162 | 122.5159 | 122.5814 | 0.001049 | 113.4342 | 113.0931 | 113.2748 | 121.1838 | -122.7437
2324.9375 | 122.7402 | -122.612 | 0.036621 | -0.005418 | -0.066412 | 0.061185 | -0.013434 | -0.0087239 | 0.0052411 | -0.011751 | 0.032388 | -0.0025126 | -0.0073645 | 0.027254 | 0.014257 | 0.005626 | 0.005985 | -0.012988 | -0.03944 | -0.063746 | -0.059493 | 0.014784 | -122.713 | -1.4099 | -122.6971 | -9.1412 | -9.4915 | -9.3005 | -122.7437 | 122.6268 | -0.076061 | 122.6176 | 122.599 | -0.027772 | -0.10037 | -0.096114 | -0.13166 | -9.1778 | -0.10095 | -0.085095 | 0.046569 | -9.5281 | -9.3372 | 122.5726 | 122.5483 | 122.5525 | 122.618 | -0.021837 | 113.4708 | 113.1205 | 113.3115 | 121.2021 | -122.7803
2326.625 | 122.8729 | -122.5525 | 0.009155 | -0.013049 | -0.066625 | 0.061612 | -0.013648 | -0.0085103 | 0.0048139 | -0.011751 | 0.032601 | -0.0027262 | -0.0071509 | 0.02704 | 0.01383 | 0.014783 | 0.005985 | -0.012988 | -0.044018 | -0.054588 | -0.054914 | 0.010206 | -122.7084 | -1.4099 | -122.6971 | -9.1457 | -9.4961 | -9.3051 | -122.7437 | 122.5627 | -0.053173 | 122.5673 | 122.5395 | -0.023194 | -0.063743 | -0.064069 | -0.19117 | -9.1549 | -0.15589 | -0.1446 | 0.046569 | -9.5052 | -9.3143 | 122.5085 | 122.4979 | 122.4976 | 122.5585 | 0.001051 | 113.4068 | 113.0564 | 113.2474 | 121.1426 | -122.7528
2328.3281 | 122.7402 | -122.5983 | 0.045776 | 0.002213 | -0.066412 | 0.061398 | -0.013434 | -0.0089375 | 0.0046001 | -0.019381 | 0.032601 | -0.0025126 | -0.0071509 | 0.02704 | 0.014043 | 0.014783 | 0.001407 | -0.012988 | -0.03944 | -0.068325 | -0.064071 | 0.010206 | -122.713 | 0.06904 | -122.6971 | -9.1412 | -9.4961 | -9.296 | -122.7391 | 122.6085 | -0.085216 | 122.6131 | 122.5853 | -0.023194 | -0.1141 | -0.10985 | -0.14082 | -9.1869 | -0.11469 | -0.098828 | 0.04199 | -9.5418 | -9.3417 | 122.5588 | 122.5299 | 122.5342 | 122.5997 | -0.03557 | 113.4571 | 113.1022 | 113.3023 | 122.6673 | -122.7849
2330.0312 | 122.8088 | -122.58 | 0.041199 | 0.002213 | -0.066625 | 0.061826 | -0.01322 | -0.0085103 | 0.0048139 | -0.011751 | 0.032601 | -0.0027262 | -0.0071509 | 0.027254 | 0.01383 | 0.010204 | 0.001407 | -0.008409 | -0.034862 | -0.072904 | -0.064071 | 0.019363 | -122.7175 | 0.073618 | -122.6971 | -9.1457 | -9.4915 | -9.3005 | -122.7437 | 122.5993 | -0.076061 | 122.5902 | 122.5715 | -0.027772 | -0.1141 | -0.10527 | -0.16371 | -9.1869 | -0.13758 | -0.11714 | 0.046569 | -9.5327 | -9.3417 | 122.5451 | 122.5071 | 122.5159 | 122.5814 | -0.021836 | 113.4342 | 113.0885 | 113.2794 | 122.6536 | -122.7849
2331.7344 | 122.7768 | -122.5937 | 0.018311 | -0.013049 | -0.066625 | 0.061612 | -0.01322 | -0.0087239 | 0.0048139 | -0.027012 | 0.032601 | -0.0027262 | -0.0071509 | 0.02704 | 0.014043 | 0.014783 | 0.005985 | -0.012988 | -0.03944 | -0.068325 | -0.054914 | 0.014784 | -122.7175 | 0.06904 | -122.6971 | -9.1412 | -9.4869 | -9.3051 | -122.7437 | 122.6085 | -0.057751 | 122.6085 | 122.5807 | -0.027772 | -0.086636 | -0.073225 | -0.14997 | -9.1595 | -0.12385 | -0.10341 | 0.046569 | -9.5052 | -9.3234 | 122.5542 | 122.5254 | 122.5388 | 122.5997 | -0.003527 | 113.4525 | 113.1068 | 113.2886 | 122.6627 | -122.762
2333.4375 | 122.8409 | -122.5754 | -0.009155 | -0.013049 | -0.066625 | 0.061612 | -0.013648 | -0.0087239 | 0.0043865 | -0.027012 | 0.032601 | -0.0027262 | -0.0077917 | 0.027254 | 0.014043 | 0.005626 | 0.001407 | -0.012988 | -0.03944 | -0.063746 | -0.064071 | 0.019363 | -122.713 | 0.073618 | -122.6925 | -9.1457 | -9.4869 | -9.3051 | -122.7482 | 122.5947 | -0.030285 | 122.581 | 122.5624 | -0.032351 | -0.054591 | -0.054916 | -0.17287 | -9.1366 | -0.13758 | -0.11714 | 0.055727 | -9.4777 | -9.296 | 122.5359 | 122.5116 | 122.5113 | 122.5768 | 0.028518 | 113.4296 | 113.0885 | 113.2703 | 122.649 | -122.7391
2335.1406 | 122.8729 | -122.5296 | -0.009155 | -0.013049 | -0.066625 | 0.061398 | -0.01322 | -0.0087239 | 0.0043865 | -0.011751 | 0.032601 | -0.0027262 | -0.0073645 | 0.026827 | 0.014043 | 0.023939 | 0.005985 | -0.017566 | -0.03944 | -0.059167 | -0.059493 | 0.014784 | -122.7175 | 0.06904 | -122.7017 | -9.1457 | -9.4823 | -9.3005 | -122.7528 | 122.5444 | -0.030285 | 122.5535 | 122.512 | -0.03235 | -0.050012 | -0.050338 | -0.22322 | -9.1366 | -0.18793 | -0.17207 | 0.051149 | -9.4732 | -9.2914 | 122.4902 | 122.4704 | 122.4701 | 122.5356 | 0.023939 | 113.3839 | 113.0473 | 113.2291 | 122.5986 | -122.7437
2336.9531 | 122.7356 | -122.612 | 0.018311 | 0.002213 | -0.066839 | 0.060971 | -0.013007 | -0.0087239 | 0.0046001 | -0.011751 | 0.032815 | -0.0027262 | -0.0073645 | 0.026827 | 0.014257 | 0.010204 | 0.005985 | -0.003831 | -0.034862 | -0.063746 | -0.054914 | 0.014784 | -122.7221 | 0.064461 | -122.6971 | -9.1457 | -9.4915 | -9.3051 | -122.7574 | 122.6268 | -0.053173 | 122.6222 | 122.6082 | -0.018615 | -0.082057 | -0.073225 | -0.1454 | -9.164 | -0.11011 | -0.085095 | 0.060305 | -9.5098 | -9.3234 | 122.5771 | 122.5483 | 122.5571 | 122.618 | -0.003527 | 113.4663 | 113.1205 | 113.3069 | 122.6765 | -122.7757
2338.6875 | 122.8409 | -122.5891 | 0.022888 | -0.013049 | -0.066412 | 0.061185 | -0.013434 | -0.0085103 | 0.0046001 | -0.011751 | 0.032601 | -0.0025126 | -0.0073645 | 0.02704 | 0.01383 | 0.005626 | -0.003172 | -0.008409 | -0.034862 | -0.063746 | -0.059493 | 0.010206 | -122.7221 | 0.064461 | -122.6925 | -9.1503 | -9.4961 | -9.3005 | -122.7437 | 122.5993 | -0.05775 | 122.5947 | 122.5807 | -0.018615 | -0.086634 | -0.082381 | -0.15455 | -9.1732 | -0.133 | -0.1034 | 0.051148 | -9.5189 | -9.3234 | 122.5542 | 122.5254 | 122.5296 | 122.5859 | -0.012682 | 113.4388 | 113.0931 | 113.2886 | 122.6536 | -122.7666
2340.4219 | 122.7814 | -122.5891 | 0.045776 | -0.013049 | -0.066412 | 0.061612 | -0.01322 | -0.0089375 | 0.0046001 | -0.027012 | 0.032388 | -0.0027262 | -0.0075781 | 0.02704 | 0.014043 | 0.014783 | 0.005985 | -0.017566 | -0.034862 | -0.063746 | -0.064071 | 0.014784 | -122.7267 | 0.073618 | -122.7017 | -9.1457 | -9.4869 | -9.3005 | -122.7482 | 122.6039 | -0.080638 | 122.6039 | 122.5715 | -0.03235 | -0.10952 | -0.10985 | -0.15913 | -9.1915 | -0.13758 | -0.11256 | 0.04657 | -9.5327 | -9.3463 | 122.5542 | 122.5254 | 122.525 | 122.5951 | -0.030992 | 113.4434 | 113.1022 | 113.2886 | 122.6627 | -122.794
2342.125 | 122.8363 | -122.5845 | -0.004578 | -0.02068 | -0.066839 | 0.061612 | -0.013434 | -0.0087239 | 0.0046001 | -0.0041205 | 0.032815 | -0.0027262 | -0.0073645 | 0.02704 | 0.01383 | 0.010204 | 0.010564 | -0.008409 | -0.034862 | -0.063746 | -0.064071 | 0.005627 | -122.7267 | 0.073618 | -122.7063 | -9.1412 | -9.4869 | -9.3005 | -122.7574 | 122.5902 | -0.030284 | 122.5947 | 122.5761 | -0.014036 | -0.059168 | -0.059493 | -0.17287 | -9.1366 | -0.14216 | -0.12172 | 0.051148 | -9.4823 | -9.296 | 122.5497 | 122.5208 | 122.5205 | 122.5951 | 0.010205 | 113.4434 | 113.0976 | 113.284 | 122.6582 | -122.7528
2343.9062 | 122.9004 | -122.5616 | 0.013733 | -0.005418 | -0.066839 | 0.061398 | -0.013007 | -0.0089375 | 0.0048139 | -0.011751 | 0.032815 | -0.0027262 | -0.0075781 | 0.02704 | 0.014043 | 0.010204 | 0.005985 | -0.012988 | -0.03944 | -0.059167 | -0.059493 | 0.010206 | -122.7175 | 0.073618 | -122.7063 | -9.1412 | -9.4961 | -9.296 | -122.7528 | 122.5719 | -0.053173 | 122.5718 | 122.5487 | -0.023194 | -0.0729 | -0.073226 | -0.19118 | -9.1549 | -0.15589 | -0.14461 | 0.04657 | -9.5098 | -9.3097 | 122.5222 | 122.5025 | 122.5022 | 122.5676 | -0.003527 | 113.4205 | 113.0656 | 113.2657 | 122.6353 | -122.7666
2345.625 | 122.8363 | -122.5891 | 0.004578 | 0.002213 | -0.066625 | 0.061185 | -0.013434 | -0.0087239 | 0.0046001 | -0.011751 | 0.032601 | -0.0027262 | -0.0075781 | 0.027254 | 0.01383 | 0.005626 | 0.005985 | -0.017566 | -0.034862 | -0.063746 | -0.064071 | 0.010206 | -122.713 | 0.059882 | -122.7017 | -9.1503 | -9.4915 | -9.2914 | -122.7574 | 122.5993 | -0.03944 | 122.5947 | 122.5715 | -0.027772 | -0.068324 | -0.068649 | -0.16829 | -9.1549 | -0.12384 | -0.11256 | 0.055727 | -9.4961 | -9.296 | 122.5542 | 122.5254 | 122.525 | 122.5951 | 0.005628 | 113.4388 | 113.0976 | 113.2977 | 122.649 | -122.762
2347.3594 | 122.8409 | -122.5891 | 0.009155 | -0.013049 | -0.066625 | 0.061185 | -0.013434 | -0.0085103 | 0.0046001 | -0.019381 | 0.032815 | -0.0027262 | -0.0075781 | 0.027468 | 0.01383 | 0.010204 | 0.001407 | -0.012988 | -0.044018 | -0.072904 | -0.050335 | 0.019363 | -122.7175 | 0.064461 | -122.6971 | -9.1412 | -9.4823 | -9.296 | -122.7574 | 122.6085 | -0.053173 | 122.5993 | 122.5761 | -0.032351 | -0.082059 | -0.05949 | -0.16829 | -9.1503 | -0.12842 | -0.10798 | 0.060305 | -9.4915 | -9.3051 | 122.5451 | 122.5162 | 122.5388 | 122.5905 | 0.010208 | 113.448 | 113.1068 | 113.2931 | 122.6536 | -122.7666
2349.0781 | 122.8317 | -122.58 | -0.004578 | -0.013049 | -0.066625 | 0.061612 | -0.013648 | -0.0085103 | 0.0046001 | -0.027012 | 0.032815 | -0.0027262 | -0.0075781 | 0.02704 | 0.014043 | 0.005626 | -0.003172 | -0.012988 | -0.03944 | -0.063746 | -0.059493 | 0.005627 | -122.7221 | 0.073618 | -122.7017 | -9.1457 | -9.4869 | -9.3005 | -122.7528 | 122.5856 | -0.034862 | 122.5856 | 122.567 | -0.018615 | -0.059168 | -0.054915 | -0.17287 | -9.1412 | -0.14216 | -0.12172 | 0.051149 | -9.4823 | -9.296 | 122.5405 | 122.5162 | 122.5205 | 122.5768 | 0.010205 | 113.4342 | 113.0931 | 113.2794 | 122.6536 | -122.7482
2350.7812 | 122.8455 | -122.58 | -0.004578 | -0.005418 | -0.066839 | 0.061398 | -0.013007 | -0.0089375 | 0.0043865 | -0.011751 | 0.032815 | -0.0027262 | -0.0071509 | 0.027254 | 0.013616 | 0.014783 | 0.005985 | -0.003831 | -0.030283 | -0.059167 | -0.059493 | 0.010206 | -122.7267 | 0.064461 | -122.7063 | -9.1457 | -9.4869 | -9.3005 | -122.7482 | 122.5902 | -0.025705 | 122.5947 | 122.5761 | -0.014037 | -0.054589 | -0.054915 | -0.16829 | -9.1412 | -0.14674 | -0.1263 | 0.041991 | -9.4823 | -9.296 | 122.5497 | 122.5208 | 122.5205 | 122.5859 | 0.014784 | 113.4342 | 113.0931 | 113.2794 | 122.6444 | -122.7437
2352.5625 | 122.8409 | -122.6074 | 0.013733 | -0.005418 | -0.066625 | 0.061612 | -0.01322 | -0.0089375 | 0.0041729 | -0.019381 | 0.032815 | -0.0027262 | -0.0073645 | 0.02704 | 0.014043 | 0.010204 | 0.005985 | -0.012988 | -0.030283 | -0.063746 | -0.054914 | 0.010206 | -122.7267 | 0.06904 | -122.6971 | -9.1503 | -9.4915 | -9.296 | -122.7482 | 122.6176 | -0.044016 | 122.6176 | 122.5944 | -0.023194 | -0.077479 | -0.068647 | -0.14082 | -9.164 | -0.11927 | -0.089673 | 0.051148 | -9.5052 | -9.3097 | 122.5771 | 122.5437 | 122.5525 | 122.6134 | -0.003527 | 113.4571 | 113.1159 | 113.3115 | 122.6765 | -122.762
2354.2812 | 122.7585 | -122.6074 | 0.032043 | -0.005418 | -0.066412 | 0.061185 | -0.013434 | -0.0085103 | 0.0048139 | -0.011751 | -0.028286 | 0.020776 | -0.0054417 | 0.027468 | 0.012334 | 0.010204 | 0.005985 | -0.022144 | -0.030283 | -0.063746 | -0.064071 | 0.014784 | -3.0392 | 0.06904 | -3.2614 | -0.31382 | -0.2839 | -0.19829 | -3.3831 | 122.6222 | -0.062326 | 122.6176 | 122.5853 | -0.036928 | -0.095789 | -0.096114 | 119.2244 | -0.34586 | 119.5682 | 119.346 | 0.12161 | -0.31595 | -0.23033 | 122.5771 | 122.5437 | 122.5434 | 122.6134 | -0.017259 | 122.2936 | 122.3235 | 122.4091 | 122.6765 | -3.4151
2356 | 122.8043 | -122.5983 | 0.018311 | -0.005418 | -0.066839 | 0.061398 | -0.01322 | -0.0087239 | 0.0043865 | -0.011751 | -0.028927 | 0.021417 | -0.0054417 | 0.027681 | 0.0074201 | 0.014783 | -0.003172 | -0.017566 | -0.030283 | -0.068325 | -0.064071 | 0.010206 | 0.037677 | 0.073618 | -0.079245 | -0.1261 | -0.077866 | -0.005985 | -0.1321 | 122.6085 | -0.048594 | 122.6131 | 122.5807 | -0.027772 | -0.086636 | -0.082382 | 122.4662 | -0.14441 | 122.6359 | 122.519 | 0.052852 | -0.096177 | -0.024296 | 122.568 | 122.5299 | 122.5342 | 122.5951 | -0.008105 | 122.4722 | 122.5204 | 122.5923 | 122.6719 | -0.15041
2357.6875 | 122.7905 | -122.6074 | 0.032043 | -0.02068 | -0.066839 | 0.060971 | -0.01322 | -0.0087239 | 0.0043865 | -0.019381 | -0.029354 | 0.021417 | -0.0058689 | 0.02704 | 0.0074201 | 0.014783 | 0.001407 | -0.017566 | -0.03944 | -0.068325 | -0.064071 | 0.014784 | 0.037677 | 0.06904 | -0.06093 | -0.13068 | -0.077866 | -0.010564 | -0.1321 | 122.6222 | -0.071483 | 122.6222 | 122.5899 | -0.03235 | -0.10037 | -0.096114 | 122.4753 | -0.16272 | 122.6451 | 122.5465 | 0.071167 | -0.10991 | -0.042607 | 122.568 | 122.5391 | 122.5434 | 122.6088 | -0.017259 | 122.4767 | 122.5296 | 122.5969 | 122.6765 | -0.16414
2359.375 | 122.7905 | -122.5754 | 0.013733 | -0.02068 | -0.066839 | 0.061398 | -0.01322 | -0.0087239 | 0.0046001 | -0.011751 | -0.029354 | 0.021844 | -0.0054417 | 0.027468 | 0.0074201 | 0.010204 | 0.001407 | -0.008409 | -0.044018 | -0.063746 | -0.054914 | 0.010206 | 0.042256 | 0.06904 | -0.056351 | -0.13526 | -0.073287 | -0.001407 | -0.12752 | 122.5856 | -0.057751 | 122.5856 | 122.567 | -0.018615 | -0.077479 | -0.068647 | 122.4479 | -0.14899 | 122.6176 | 122.519 | 0.071167 | -0.08702 | -0.01514 | 122.5314 | 122.5116 | 122.5205 | 122.5768 | -0.003527 | 122.4401 | 122.5021 | 122.574 | 122.6444 | -0.14125
2361.0781 | 122.8363 | -122.58 | 0.009155 | -0.013049 | -0.066412 | 0.061185 | -0.01322 | -0.0089375 | 0.0043865 | -0.027012 | -0.028286 | 0.021417 | -0.0052279 | 0.027468 | 0.0076339 | 0.010204 | 0.005985 | -0.012988 | -0.03944 | -0.059167 | -0.059493 | 0.014784 | 0.055992 | 0.073618 | -0.065509 | -0.11695 | -0.077866 | -0.001407 | -0.11836 | 122.5947 | -0.048595 | 122.5902 | 122.567 | -0.027772 | -0.068322 | -0.068648 | 122.4616 | -0.1261 | 122.6359 | 122.5144 | 0.052852 | -0.087021 | -0.010562 | 122.5405 | 122.5208 | 122.5205 | 122.5859 | 0.005629 | 122.463 | 122.5021 | 122.5785 | 122.6536 | -0.12752
2362.7656 | 122.8867 | -122.5616 | 0.018311 | -0.02068 | -0.066625 | 0.061185 | -0.013434 | -0.0087239 | 0.0043865 | -0.011751 | -0.028286 | 0.02099 | -0.0056553 | 0.027468 | 0.0080611 | 0.014783 | 0.001407 | 0.000747 | -0.034862 | -0.059167 | -0.064071 | 0.010206 | 0.051413 | 0.073618 | -0.051772 | -0.1261 | -0.073287 | -0.005985 | -0.10462 | 122.5719 | -0.053173 | 122.5764 | 122.5624 | -0.009459 | -0.077478 | -0.082382 | 122.457 | -0.14441 | 122.6131 | 122.5099 | 0.052852 | -0.091598 | -0.024296 | 122.5268 | 122.5025 | 122.4976 | 122.5631 | -0.008105 | 122.4355 | 122.4884 | 122.5557 | 122.6353 | -0.12293
2364.4531 | 122.8683 | -122.5525 | 0 | 0.002213 | -0.066625 | 0.061612 | -0.013648 | -0.0087239 | 0.0046001 | -0.0041205 | -0.027858 | 0.021203 | -0.0054417 | 0.027681 | 0.0074201 | 0.005626 | 0.001407 | -0.012988 | -0.034862 | -0.068325 | -0.064071 | 0.014784 | 0.051413 | 0.073618 | -0.06093 | -0.12152 | -0.068708 | -0.005985 | -0.10004 | 122.5673 | -0.034862 | 122.5581 | 122.5395 | -0.027772 | -0.068325 | -0.064071 | 122.4524 | -0.12152 | 122.6039 | 122.4916 | 0.039115 | -0.068708 | -0.005985 | 122.5176 | 122.4842 | 122.4884 | 122.5539 | 0.014784 | 122.431 | 122.4838 | 122.5465 | 122.6261 | -0.10004
2366.1562 | 122.7402 | -122.6212 | 0.027466 | -0.005418 | -0.066839 | 0.061612 | -0.013434 | -0.0089375 | 0.0046001 | -0.011751 | -0.028286 | 0.02099 | -0.0050143 | 0.027681 | 0.0074201 | 0.014783 | 0.001407 | -0.022144 | -0.034862 | -0.063746 | -0.059493 | 0.014784 | 0.051413 | 0.073618 | -0.051772 | -0.11695 | -0.077866 | -0.001407 | -0.10004 | 122.6359 | -0.062328 | 122.6359 | 122.599 | -0.036928 | -0.091212 | -0.086959 | 122.5211 | -0.14441 | 122.6726 | 122.5694 | 0.048273 | -0.10533 | -0.028873 | 122.5863 | 122.5574 | 122.5617 | 122.6226 | -0.012682 | 122.5042 | 122.5433 | 122.6197 | 122.6948 | -0.12751
2367.8906 | 122.8317 | -122.5845 | 0 | 0.002213 | -0.066625 | 0.061185 | -0.013434 | -0.0085103 | 0.0041729 | -0.0041205 | -0.027858 | 0.02099 | -0.0050143 | 0.027468 | 0.0072065 | 0.010204 | 0.001407 | -0.012988 | -0.034862 | -0.059167 | -0.054914 | 0.010206 | 0.051413 | 0.078197 | -0.047194 | -0.12152 | -0.06413 | -0.001407 | -0.10004 | 122.5947 | -0.034862 | 122.5947 | 122.5715 | -0.023194 | -0.059167 | -0.054914 | 122.4845 | -0.12152 | 122.6359 | 122.5373 | 0.052851 | -0.06413 | -0.001407 | 122.5497 | 122.5254 | 122.5296 | 122.5859 | 0.010206 | 122.463 | 122.5204 | 122.5831 | 122.6627 | -0.10004
2369.5938 | 122.8546 | -122.5983 | 0.009155 | 0.002213 | -0.066839 | 0.060757 | -0.01322 | -0.0087239 | 0.0041729 | -0.027012 | -0.028286 | 0.02099 | -0.0054417 | 0.027468 | 0.0076339 | 0.010204 | 0.005985 | -0.017566 | -0.034862 | -0.063746 | -0.064071 | 0.010206 | 0.055992 | 0.073618 | -0.051772 | -0.1261 | -0.073287 | 0.007751 | -0.1092 | 122.6085 | -0.044017 | 122.6085 | 122.5807 | -0.027772 | -0.072901 | -0.073226 | 122.4891 | -0.13526 | 122.6543 | 122.5465 | 0.057431 | -0.082442 | -0.001404 | 122.5634 | 122.5345 | 122.5342 | 122.6043 | 0.001051 | 122.4722 | 122.525 | 122.606 | 122.6719 | -0.11836
2371.2969 | 122.7631 | -122.5983 | 0.036621 | -0.013049 | -0.066839 | 0.061185 | -0.013434 | -0.0089375 | 0.0043865 | -0.019381 | -0.028286 | 0.021203 | -0.0052279 | 0.027681 | 0.0076339 | 0.010204 | 0.001407 | -0.008409 | -0.03944 | -0.063746 | -0.059493 | 0.005627 | 0.051413 | 0.078197 | -0.047194 | -0.1261 | -0.077866 | -0.005985 | -0.10004 | 122.6039 | -0.076061 | 122.6085 | 122.5899 | -0.014036 | -0.10037 | -0.096114 | 122.4982 | -0.16272 | 122.6497 | 122.5511 | 0.052851 | -0.11449 | -0.042606 | 122.5588 | 122.5345 | 122.5388 | 122.5997 | -0.030994 | 122.4722 | 122.5204 | 122.5923 | 122.6765 | -0.13667
2373.0156 | 122.7448 | -122.644 | 0.022888 | 0.002213 | -0.066839 | 0.061398 | -0.013434 | -0.0089375 | 0.0046001 | -0.011751 | -0.028499 | 0.021417 | -0.0052279 | 0.027468 | 0.0074201 | 0.014783 | 0.005985 | -0.012988 | -0.03944 | -0.063746 | -0.064071 | 0.010206 | 0.051413 | 0.073618 | -0.042615 | -0.1261 | -0.077866 | 0.003172 | -0.095467 | 122.6542 | -0.062328 | 122.6588 | 122.6311 | -0.023194 | -0.086634 | -0.086959 | 122.5486 | -0.14899 | 122.6955 | 122.6014 | 0.052852 | -0.10075 | -0.019716 | 122.6046 | 122.5803 | 122.58 | 122.65 | -0.012682 | 122.5179 | 122.5662 | 122.6472 | 122.7177 | -0.11835
2374.7031 | 122.7676 | -122.6257 | 0.018311 | 0.009844 | -0.066839 | 0.061185 | -0.01322 | -0.0089375 | 0.0041729 | -0.027012 | -0.028072 | 0.021417 | -0.0054417 | 0.027468 | 0.0074201 | 0.010204 | -0.003172 | -0.008409 | -0.034862 | -0.063746 | -0.059493 | 0.010206 | 0.051413 | 0.06904 | -0.056351 | -0.1261 | -0.077866 | -0.005985 | -0.090888 | 122.6359 | -0.053173 | 122.6359 | 122.6173 | -0.018615 | -0.082057 | -0.077804 | 122.5348 | -0.14441 | 122.6771 | 122.5694 | 0.034537 | -0.096177 | -0.024296 | 122.5909 | 122.562 | 122.5662 | 122.6226 | -0.008105 | 122.4996 | 122.5479 | 122.6197 | 122.6948 | -0.1092
2376.4062 | 122.8271 | -122.5983 | 0.013733 | -0.005418 | -0.066839 | 0.061398 | -0.013648 | -0.0087239 | 0.0041729 | -0.0041205 | -0.028072 | 0.02099 | -0.0054417 | 0.027468 | 0.0074201 | 0.010204 | 0.005985 | -0.003831 | -0.034862 | -0.063746 | -0.059493 | 0.001048 | 0.051413 | 0.06904 | -0.06093 | -0.1261 | -0.068708 | 0.003172 | -0.090888 | 122.5993 | -0.048595 | 122.6085 | 122.5944 | -0.004879 | -0.077479 | -0.073226 | 122.5074 | -0.13984 | 122.6497 | 122.5373 | 0.029958 | -0.082441 | -0.010561 | 122.5634 | 122.5345 | 122.5388 | 122.6043 | -0.012685 | 122.4722 | 122.5296 | 122.6014 | 122.6673 | -0.10462
2378.1094 | 122.7997 | -122.5891 | 0.045776 | -0.005418 | -0.066839 | 0.060971 | -0.013434 | -0.0087239 | 0.0043865 | -0.011751 | -0.028072 | 0.021417 | -0.0052279 | 0.027468 | 0.0076339 | 0.014783 | 0.001407 | -0.017566 | -0.03944 | -0.063746 | -0.059493 | 0.001048 | 0.055992 | 0.06904 | -0.056351 | -0.13068 | -0.073287 | -0.001407 | -0.10004 | 122.5902 | -0.085216 | 122.6039 | 122.5715 | -0.018614 | -0.10952 | -0.10527 | 122.4891 | -0.17646 | 122.6451 | 122.5328 | 0.043694 | -0.11906 | -0.047183 | 122.5497 | 122.5254 | 122.5296 | 122.5905 | -0.044728 | 122.4584 | 122.5158 | 122.5877 | 122.6582 | -0.14582
2379.8125 | 122.7814 | -122.612 | 0.013733 | -0.013049 | -0.066839 | 0.061398 | -0.013434 | -0.0087239 | 0.0043865 | -0.011751 | -0.027858 | 0.021417 | -0.0054417 | 0.027681 | 0.0074201 | 0.005626 | 0.005985 | -0.012988 | -0.030283 | -0.063746 | -0.064071 | 0.014784 | 0.051413 | 0.073618 | -0.042615 | -0.13068 | -0.073287 | 0.007751 | -0.090888 | 122.6268 | -0.044016 | 122.6176 | 122.599 | -0.027772 | -0.077479 | -0.077804 | 122.5211 | -0.14441 | 122.6634 | 122.5694 | 0.048273 | -0.08702 | -0.005982 | 122.5817 | 122.5483 | 122.5479 | 122.618 | 0.001051 | 122.4813 | 122.5387 | 122.6198 | 122.6856 | -0.10462
2381.5156 | 122.7905 | -122.5845 | 0.022888 | -0.013049 | -0.067053 | 0.061612 | -0.01322 | -0.0087239 | 0.0043865 | -0.0041205 | -0.028072 | 0.021203 | -0.0054417 | 0.027468 | 0.0076339 | 0.010204 | 0.005985 | -0.012988 | -0.030283 | -0.063746 | -0.054914 | 0.014784 | 0.051413 | 0.073618 | -0.051772 | -0.12152 | -0.06413 | 0.003172 | -0.095467 | 122.5993 | -0.053171 | 122.5947 | 122.5715 | -0.027772 | -0.086634 | -0.077802 | 122.4891 | -0.14441 | 122.6359 | 122.5328 | 0.043695 | -0.087018 | -0.019716 | 122.5543 | 122.5208 | 122.5296 | 122.5905 | -0.008104 | 122.463 | 122.5204 | 122.5877 | 122.6582 | -0.11835
2383.2188 | 122.7951 | -122.612 | 0.018311 | 0.002213 | -0.067053 | 0.061185 | -0.013434 | -0.0089375 | 0.0041729 | 0.00351 | -0.028286 | 0.021417 | -0.0054417 | 0.027681 | 0.0074201 | 0.014783 | -0.003172 | -0.012988 | -0.030283 | -0.063746 | -0.059493 | 0.001048 | 0.060571 | 0.078197 | -0.051772 | -0.1261 | -0.077866 | 0.003172 | -0.090888 | 122.613 | -0.048594 | 122.6268 | 122.599 | -0.014036 | -0.082057 | -0.077804 | 122.5211 | -0.14441 | 122.6726 | 122.5602 | 0.039116 | -0.096177 | -0.015139 | 122.5817 | 122.5483 | 122.5525 | 122.6088 | -0.017263 | 122.4859 | 122.5341 | 122.6152 | 122.6902 | -0.1092
2384.9688 | 122.7585 | -122.6349 | 0.027466 | -0.005418 | -0.066839 | 0.060757 | -0.013648 | -0.0091513 | 0.0043865 | -0.019381 | -0.028072 | 0.021203 | -0.0054417 | 0.027468 | 0.0074201 | 0.014783 | 0.001407 | -0.017566 | -0.030283 | -0.063746 | -0.059493 | 0.014784 | 0.060571 | 0.06904 | -0.056351 | -0.1261 | -0.082444 | 0.003172 | -0.086309 | 122.6497 | -0.057749 | 122.6497 | 122.6173 | -0.03235 | -0.091212 | -0.086959 | 122.5486 | -0.15357 | 122.6955 | 122.5785 | 0.029958 | -0.10991 | -0.024294 | 122.6046 | 122.5711 | 122.5754 | 122.6363 | -0.012682 | 122.5088 | 122.5524 | 122.6381 | 122.7039 | -0.11378
2386.6719 | 122.8043 | -122.5983 | 0.013733 | -0.013049 | -0.067266 | 0.060757 | -0.013434 | -0.0091513 | 0.0046001 | -0.0041205 | -0.028072 | 0.02099 | -0.0056553 | 0.027681 | 0.0076339 | 0.010204 | 0.010564 | -0.012988 | -0.03944 | -0.054588 | -0.059493 | 0.005627 | 0.051413 | 0.078197 | -0.042615 | -0.11695 | -0.068708 | 0.007751 | -0.090888 | 122.6039 | -0.053173 | 122.6085 | 122.5853 | -0.018615 | -0.068321 | -0.073226 | 122.5074 | -0.13068 | 122.6497 | 122.5557 | 0.048273 | -0.082441 | -0.005982 | 122.5588 | 122.5437 | 122.5388 | 122.6088 | -0.008106 | 122.4813 | 122.5296 | 122.606 | 122.6765 | -0.10462
2388.375 | 122.7539 | -122.6166 | 0.027466 | 0.002213 | -0.066839 | 0.060971 | -0.01322 | -0.0087239 | 0.0046001 | -0.034642 | -0.028072 | 0.021203 | -0.0054417 | 0.028109 | 0.0074201 | 0.010204 | 0.005985 | -0.017566 | -0.03944 | -0.059167 | -0.064071 | 0.010206 | 0.055992 | 0.073618 | -0.056351 | -0.1261 | -0.073287 | 0.003172 | -0.086309 | 122.6268 | -0.066906 | 122.6268 | 122.599 | -0.027772 | -0.086633 | -0.091537 | 122.5303 | -0.15357 | 122.6726 | 122.5602 | 0.029958 | -0.10075 | -0.024294 | 122.5771 | 122.5574 | 122.5525 | 122.6226 | -0.01726 | 122.4905 | 122.5433 | 122.6197 | 122.6902 | -0.11378
2390.0625 | 122.8043 | -122.6028 | 0.036621 | -0.005418 | -0.067053 | 0.060971 | -0.013434 | -0.0089375 | 0.0046001 | -0.019381 | -0.028072 | 0.021203 | -0.0054417 | 0.027681 | 0.0074201 | 0.010204 | 0.010564 | -0.017566 | -0.034862 | -0.059167 | -0.064071 | 0.010206 | 0.051413 | 0.073618 | -0.051772 | -0.1261 | -0.073287 | -0.001407 | -0.086309 | 122.6131 | -0.071483 | 122.613 | 122.5853 | -0.027772 | -0.095788 | -0.10069 | 122.5165 | -0.16272 | 122.6543 | 122.5511 | 0.034537 | -0.10991 | -0.038028 | 122.568 | 122.5437 | 122.5388 | 122.6134 | -0.026415 | 122.4767 | 122.5296 | 122.6014 | 122.6765 | -0.12293
2391.75 | 122.7722 | -122.6532 | 0.045776 | -0.013049 | -0.067053 | 0.060971 | -0.013434 | -0.0085103 | 0.0043865 | -0.011751 | -0.027645 | 0.021203 | -0.0054417 | 0.027681 | 0.0074201 | 0.010204 | 0.001407 | -0.008409 | -0.03944 | -0.059167 | -0.054914 | -0.003531 | 0.046835 | 0.078197 | -0.051772 | -0.13068 | -0.077866 | -0.001407 | -0.086309 | 122.6497 | -0.085216 | 122.6634 | 122.6448 | -0.004878 | -0.10494 | -0.10069 | 122.5669 | -0.17646 | 122.7 | 122.6014 | 0.034537 | -0.12364 | -0.047183 | 122.6138 | 122.594 | 122.5983 | 122.6546 | -0.049307 | 122.5225 | 122.5753 | 122.6518 | 122.7314 | -0.13209
2393.4375 | 122.7585 | -122.612 | 0.036621 | -0.013049 | -0.066839 | 0.061185 | -0.01322 | -0.0087239 | 0.0041729 | -0.011751 | -0.028072 | 0.021203 | -0.0054417 | 0.027468 | 0.0076339 | 0.014783 | 0.005985 | -0.012988 | -0.03944 | -0.063746 | -0.064071 | 0.019363 | 0.055992 | 0.06904 | -0.051772 | -0.1261 | -0.068708 | -0.001407 | -0.086309 | 122.6314 | -0.076061 | 122.6268 | 122.599 | -0.032351 | -0.10037 | -0.10069 | 122.5257 | -0.16272 | 122.668 | 122.5602 | 0.034537 | -0.10533 | -0.038028 | 122.5726 | 122.5483 | 122.5479 | 122.618 | -0.017258 | 122.4859 | 122.5433 | 122.6106 | 122.681 | -0.12293
2395.125 | 122.7585 | -122.612 | 0.054932 | -0.005418 | -0.067266 | 0.060757 | -0.01322 | -0.0085103 | 0.0043865 | -0.027012 | -0.028286 | 0.02099 | -0.0054417 | 0.027468 | 0.0078475 | 0.014783 | 0.005985 | -0.022144 | -0.034862 | -0.059167 | -0.054914 | 0.010206 | 0.06515 | 0.073618 | -0.051772 | -0.13526 | -0.068708 | -0.001407 | -0.086309 | 122.6222 | -0.089794 | 122.6268 | 122.5899 | -0.03235 | -0.1141 | -0.10985 | 122.5257 | -0.19019 | 122.6771 | 122.5602 | 0.034537 | -0.12364 | -0.056339 | 122.5771 | 122.5528 | 122.5571 | 122.618 | -0.044726 | 122.4767 | 122.5433 | 122.6106 | 122.6856 | -0.14124
2396.8125 | 122.7905 | -122.5937 | 0.032043 | -0.013049 | -0.067053 | 0.060757 | -0.013648 | -0.0087239 | 0.0039591 | -0.019381 | -0.028072 | 0.021203 | -0.0058689 | 0.027681 | 0.0076339 | 0.010204 | 0.001407 | -0.008409 | -0.03944 | -0.063746 | -0.050335 | 0.005627 | 0.051413 | 0.073618 | -0.056351 | -0.1261 | -0.073287 | 0.003172 | -0.08173 | 122.5993 | -0.071483 | 122.6039 | 122.5853 | -0.014036 | -0.095789 | -0.082378 | 122.512 | -0.15815 | 122.6451 | 122.5373 | 0.025379 | -0.10533 | -0.028871 | 122.5542 | 122.5299 | 122.5434 | 122.5951 | -0.026416 | 122.4676 | 122.5204 | 122.5969 | 122.6673 | -0.11377
2398.5 | 122.7722 | -122.5891 | 0.032043 | -0.005418 | -0.066839 | 0.060757 | -0.01322 | -0.0087239 | 0.0043865 | -0.019381 | -0.028072 | 0.020776 | -0.0054417 | 0.027681 | 0.0074201 | 0.014783 | -0.007751 | -0.012988 | -0.048597 | -0.063746 | -0.059493 | 0.001048 | 0.055992 | 0.078197 | -0.051772 | -0.13068 | -0.073287 | -0.001407 | -0.08173 | 122.5902 | -0.08064 | 122.6039 | 122.5761 | -0.014036 | -0.095789 | -0.091536 | 122.5074 | -0.16272 | 122.6451 | 122.5373 | 0.029958 | -0.10533 | -0.03345 | 122.5405 | 122.5254 | 122.5296 | 122.5814 | -0.030995 | 122.4584 | 122.5158 | 122.5877 | 122.6673 | -0.11377
2400.2188 | 122.8317 | -122.5845 | 0.009155 | -0.013049 | -0.067266 | 0.060544 | -0.013434 | -0.0089375 | 0.0046001 | -0.011751 | -0.028499 | 0.021417 | -0.0056553 | 0.027895 | 0.0074201 | 0.005626 | 0.005985 | -0.017566 | -0.03944 | -0.059167 | -0.054914 | 0.010206 | 0.051413 | 0.073618 | -0.047194 | -0.13526 | -0.068708 | 0.003172 | -0.086309 | 122.5947 | -0.048595 | 122.5902 | 122.567 | -0.027772 | -0.068322 | -0.064069 | 122.4982 | -0.14441 | 122.6359 | 122.5373 | 0.039115 | -0.077863 | -0.005983 | 122.5451 | 122.5254 | 122.5296 | 122.5905 | 0.001051 | 122.4493 | 122.5158 | 122.5877 | 122.6582 | -0.095464
2401.9531 | 122.7997 | -122.612 | 0.036621 | 0.002213 | -0.067053 | 0.060544 | -0.01322 | -0.0089375 | 0.0046001 | -0.0041205 | -0.028072 | 0.021417 | -0.0056553 | 0.027681 | 0.0076339 | 0.014783 | 0.005985 | -0.012988 | -0.03944 | -0.063746 | -0.045757 | 0.010206 | 0.051413 | 0.06904 | -0.051772 | -0.13068 | -0.068708 | 0.003172 | -0.086309 | 122.6222 | -0.076061 | 122.6268 | 122.599 | -0.023194 | -0.10037 | -0.082378 | 122.5257 | -0.1673 | 122.6634 | 122.5602 | 0.034537 | -0.10533 | -0.033449 | 122.5726 | 122.5483 | 122.5662 | 122.618 | -0.026415 | 122.4813 | 122.5433 | 122.6152 | 122.681 | -0.12293
2403.6562 | 122.7356 | -122.6303 | 0.041199 | -0.005418 | -0.066839 | 0.060544 | -0.013434 | -0.0085103 | 0.0043865 | -0.019381 | -0.027858 | 0.02099 | -0.0054417 | 0.027468 | 0.0076339 | 0.010204 | 0.005985 | -0.008409 | -0.034862 | -0.068325 | -0.054914 | 0.010206 | 0.051413 | 0.073618 | -0.047194 | -0.1261 | -0.06413 | -0.005985 | -0.077151 | 122.6405 | -0.076061 | 122.6405 | 122.6219 | -0.018615 | -0.10952 | -0.096113 | 122.5532 | -0.1673 | 122.6817 | 122.5831 | 0.029957 | -0.10533 | -0.047184 | 122.5954 | 122.562 | 122.5754 | 122.6363 | -0.030993 | 122.5042 | 122.5662 | 122.6243 | 122.7039 | -0.11835
2405.3438 | 122.8912 | -122.5708 | 0 | -0.013049 | -0.067266 | 0.060971 | -0.012793 | -0.0089375 | 0.0041729 | -0.019381 | -0.028072 | 0.021203 | -0.0052279 | 0.027681 | 0.0074201 | 0.005626 | -0.003172 | -0.017566 | -0.03944 | -0.063746 | -0.050335 | 0.014784 | 0.051413 | 0.073618 | -0.056351 | -0.1261 | -0.073287 | 0.003172 | -0.086309 | 122.5856 | -0.03944 | 122.5764 | 122.5532 | -0.03235 | -0.063746 | -0.050335 | 122.4845 | -0.1261 | 122.6222 | 122.5144 | 0.029958 | -0.073287 | 0.003172 | 122.5314 | 122.5071 | 122.5205 | 122.5676 | 0.014784 | 122.4447 | 122.4975 | 122.574 | 122.6444 | -0.086309
2407.0469 | 122.8958 | -122.5937 | -0.009155 | -0.005418 | -0.067266 | 0.060757 | -0.013434 | -0.0087239 | 0.0043865 | -0.011751 | -0.027645 | 0.021203 | -0.0054417 | 0.027895 | 0.0076339 | 0.010204 | 0.001407 | -0.012988 | -0.034862 | -0.063746 | -0.064071 | 0.010206 | 0.046835 | 0.06904 | -0.056351 | -0.1261 | -0.06413 | -0.005985 | -0.08173 | 122.6039 | -0.025707 | 122.6039 | 122.5807 | -0.023194 | -0.054591 | -0.054916 | 122.512 | -0.11695 | 122.6405 | 122.5373 | 0.025379 | -0.054975 | 0.00317 | 122.5588 | 122.5299 | 122.5296 | 122.5951 | 0.019361 | 122.4676 | 122.5296 | 122.5877 | 122.6627 | -0.072575
2408.7344 | 122.8958 | -122.58 | 0.009155 | -0.005418 | -0.067053 | 0.060757 | -0.01322 | -0.0089375 | 0.0041729 | -0.011751 | -0.028072 | 0.02099 | -0.0054417 | 0.027681 | 0.0076339 | 0.010204 | -0.007751 | -0.008409 | -0.034862 | -0.063746 | -0.050335 | 0.010206 | 0.055992 | 0.06904 | -0.056351 | -0.13068 | -0.068708 | -0.001407 | -0.077151 | 122.5902 | -0.044017 | 122.5902 | 122.5715 | -0.018615 | -0.072901 | -0.05949 | 122.5028 | -0.13984 | 122.6359 | 122.5236 | 0.0208 | -0.077863 | -0.010562 | 122.5451 | 122.5162 | 122.5296 | 122.5722 | 0.001051 | 122.4493 | 122.5112 | 122.5785 | 122.649 | -0.086306
2410.4375 | 122.7585 | -122.644 | 0.045776 | -0.005418 | -0.067266 | 0.060757 | -0.013434 | -0.0091513 | 0.0039591 | -0.0041205 | -0.027858 | 0.02099 | -0.0054417 | 0.028109 | 0.0074201 | 0.010204 | 0.005985 | -0.012988 | -0.034862 | -0.063746 | -0.059493 | 0.014784 | 0.051413 | 0.073618 | -0.051772 | -0.13068 | -0.077866 | -0.001407 | -0.077151 | 122.6588 | -0.080638 | 122.6542 | 122.6311 | -0.027772 | -0.10952 | -0.10527 | 122.5669 | -0.17646 | 122.6955 | 122.5923 | 0.025379 | -0.12364 | -0.047183 | 122.6092 | 122.5803 | 122.5845 | 122.65 | -0.030992 | 122.5134 | 122.5662 | 122.6426 | 122.7177 | -0.12293
2412.1406 | 122.8592 | -122.5754 | 0.004578 | -0.02068 | -0.067053 | 0.060971 | -0.013648 | -0.0085103 | 0.0041729 | -0.0041205 | -0.028072 | 0.020776 | -0.0056553 | 0.027895 | 0.0076339 | 0.014783 | 0.005985 | -0.022144 | -0.03944 | -0.059167 | -0.059493 | 0.005627 | 0.051413 | 0.06904 | -0.047194 | -0.13068 | -0.073287 | 0.003172 | -0.077151 | 122.581 | -0.044018 | 122.5902 | 122.5532 | -0.027771 | -0.063745 | -0.064071 | 122.4982 | -0.13526 | 122.6268 | 122.5282 | 0.029957 | -0.077865 | -0.001406 | 122.5359 | 122.5162 | 122.5159 | 122.5814 | 0.001049 | 122.4447 | 122.5021 | 122.5786 | 122.6444 | -0.081729
2413.8906 | 122.7493 | -122.6395 | 0.036621 | -0.005418 | -0.067266 | 0.061185 | -0.013434 | -0.0087239 | 0.0041729 | -0.019381 | -0.027858 | 0.021203 | -0.0054417 | 0.027681 | 0.0074201 | 0.010204 | 0.001407 | -0.012988 | -0.034862 | -0.059167 | -0.059493 | 0.010206 | 0.051413 | 0.06904 | -0.06093 | -0.13526 | -0.068708 | 0.007751 | -0.08173 | 122.6497 | -0.071483 | 122.6497 | 122.6265 | -0.023194 | -0.095788 | -0.096114 | 122.5577 | -0.17188 | 122.6909 | 122.5785 | 0.0208 | -0.10533 | -0.02887 | 122.6046 | 122.5803 | 122.58 | 122.6409 | -0.026415 | 122.5042 | 122.5708 | 122.6472 | 122.7085 | -0.11835
2415.5781 | 122.7493 | -122.6212 | 0.032043 | -0.013049 | -0.067053 | 0.060971 | -0.013648 | -0.0085103 | 0.0041729 | -0.019381 | -0.028072 | 0.02099 | -0.0056553 | 0.027681 | 0.0074201 | 0.019361 | 0.001407 | -0.017566 | -0.034862 | -0.068325 | -0.054914 | 0.014784 | 0.060571 | 0.073618 | -0.051772 | -0.13068 | -0.068708 | -0.005985 | -0.077151 | 122.6359 | -0.066905 | 122.6405 | 122.6036 | -0.03235 | -0.10037 | -0.086957 | 122.544 | -0.16272 | 122.6817 | 122.5694 | 0.025379 | -0.10075 | -0.038028 | 122.5863 | 122.5528 | 122.5662 | 122.6226 | -0.017259 | 122.4905 | 122.5524 | 122.6152 | 122.6948 | -0.10919
2417.2656 | 122.8958 | -122.5845 | -0.009155 | -0.02068 | -0.067266 | 0.060971 | -0.01322 | -0.0089375 | 0.0039591 | -0.027012 | -0.028072 | 0.02099 | -0.0056553 | 0.027468 | 0.0074201 | 0.010204 | 0.005985 | -0.017566 | -0.03944 | -0.063746 | -0.050335 | 0.005627 | 0.055992 | 0.073618 | -0.047194 | -0.1261 | -0.068708 | -0.001407 | -0.072572 | 122.5902 | -0.030285 | 122.5947 | 122.567 | -0.023193 | -0.054591 | -0.04118 | 122.512 | -0.11695 | 122.6405 | 122.5373 | 0.025378 | -0.059553 | 0.007748 | 122.5451 | 122.5208 | 122.5342 | 122.5905 | 0.014782 | 122.4584 | 122.5158 | 122.5831 | 122.6582 | -0.063417
2418.9844 | 122.8821 | -122.58 | -0.004578 | -0.013049 | -0.06748 | 0.060971 | -0.013434 | -0.0087239 | 0.0041729 | -0.011751 | -0.027858 | 0.02099 | -0.0052279 | 0.027681 | 0.0076339 | 0.014783 | 0.005985 | -0.008409 | -0.03944 | -0.059167 | -0.050335 | 0.010206 | 0.051413 | 0.06904 | -0.051772 | -0.1261 | -0.06413 | 0.003172 | -0.077151 | 122.5902 | -0.034862 | 122.5947 | 122.5715 | -0.018615 | -0.054589 | -0.045757 | 122.5028 | -0.12152 | 122.6314 | 122.5282 | 0.025379 | -0.059552 | 0.00775 | 122.5405 | 122.5208 | 122.5296 | 122.5859 | 0.014784 | 122.4539 | 122.5158 | 122.5831 | 122.649 | -0.072573
2420.6719 | 122.7631 | -122.6166 | 0.050354 | -0.005418 | -0.067266 | 0.060757 | -0.013434 | -0.0087239 | 0.0046001 | -0.0041205 | -0.028072 | 0.021203 | -0.0054417 | 0.027895 | 0.0076339 | 0.005626 | 0.001407 | -0.003831 | -0.034862 | -0.054588 | -0.050335 | 0.014784 | 0.051413 | 0.073618 | -0.051772 | -0.13068 | -0.068708 | 0.003172 | -0.08173 | 122.6314 | -0.085216 | 122.6222 | 122.6127 | -0.018615 | -0.10494 | -0.10069 | 122.5348 | -0.18104 | 122.668 | 122.5648 | 0.029958 | -0.11906 | -0.047182 | 122.5817 | 122.562 | 122.5662 | 122.618 | -0.03557 | 122.4859 | 122.5479 | 122.6197 | 122.6902 | -0.13208
2422.3906 | 122.8043 | -122.6028 | 0.032043 | 0.002213 | -0.06748 | 0.060971 | -0.013648 | -0.0091513 | 0.0043865 | -0.0041205 | -0.027858 | 0.02099 | -0.0056553 | 0.028109 | 0.0076339 | 0.014783 | 0.001407 | -0.012988 | -0.03944 | -0.054588 | -0.050335 | 0.001048 | 0.060571 | 0.073618 | -0.051772 | -0.13068 | -0.068708 | -0.001407 | -0.08173 | 122.6039 | -0.071483 | 122.6176 | 122.5899 | -0.014036 | -0.086631 | -0.082378 | 122.5211 | -0.16272 | 122.6634 | 122.5511 | 0.029958 | -0.10075 | -0.03345 | 122.5634 | 122.5483 | 122.5525 | 122.6043 | -0.030995 | 122.4722 | 122.5341 | 122.6014 | 122.6765 | -0.11377
2424.0781 | 122.8683 | -122.5845 | 0.009155 | -0.013049 | -0.06748 | 0.061185 | -0.013648 | -0.0087239 | 0.0037455 | -0.019381 | -0.027858 | 0.020776 | -0.0052279 | 0.027681 | 0.0074201 | 0.014783 | -0.007751 | -0.008409 | -0.03944 | -0.054588 | -0.064071 | 0.005627 | 0.055992 | 0.06904 | -0.051772 | -0.1261 | -0.077866 | -0.001407 | -0.077151 | 122.5902 | -0.048595 | 122.5993 | 122.5761 | -0.014036 | -0.063743 | -0.073226 | 122.5074 | -0.13526 | 122.6405 | 122.5328 | 0.025379 | -0.087021 | -0.010562 | 122.5451 | 122.5299 | 122.5205 | 122.5768 | -0.003528 | 122.4584 | 122.5067 | 122.5831 | 122.6536 | -0.086306
2425.7656 | 122.8683 | -122.5616 | 0.013733 | -0.013049 | -0.067266 | 0.061185 | -0.013434 | -0.0087239 | 0.0039591 | -0.019381 | -0.028072 | 0.02099 | -0.0054417 | 0.028109 | 0.0072065 | 0.010204 | 0.001407 | -0.017566 | -0.034862 | -0.063746 | -0.054914 | 0.010206 | 0.051413 | 0.078197 | -0.047194 | -0.1261 | -0.073287 | 0.003172 | -0.077151 | 122.5719 | -0.048595 | 122.5718 | 122.5441 | -0.027772 | -0.077479 | -0.068647 | 122.4845 | -0.13984 | 122.6131 | 122.5145 | 0.029957 | -0.08702 | -0.010561 | 122.5268 | 122.4979 | 122.5067 | 122.5631 | -0.003527 | 122.4355 | 122.4884 | 122.5648 | 122.6398 | -0.090884
2427.4688 | 122.7951 | -122.58 | 0.036621 | 0.009844 | -0.06748 | 0.060757 | -0.013862 | -0.0089375 | 0.0039591 | -0.011751 | -0.027858 | 0.021203 | -0.0056553 | 0.027681 | 0.0074201 | 0.014783 | 0.001407 | -0.012988 | -0.03944 | -0.054588 | -0.059493 | 0.005627 | 0.055992 | 0.073618 | -0.056351 | -0.1261 | -0.073287 | 0.007751 | -0.072572 | 122.5856 | -0.076061 | 122.5947 | 122.567 | -0.018615 | -0.091209 | -0.096114 | 122.5074 | -0.16272 | 122.6359 | 122.5236 | 0.016221 | -0.10991 | -0.02887 | 122.5405 | 122.5254 | 122.5205 | 122.5814 | -0.030994 | 122.4539 | 122.5067 | 122.5877 | 122.6536 | -0.10919
2429.1719 | 122.7264 | -122.6074 | 0.022888 | -0.013049 | -0.06748 | 0.061185 | -0.013648 | -0.0089375 | 0.0039591 | -0.019381 | -0.028072 | 0.021203 | -0.0054417 | 0.028322 | 0.0076339 | 0.010204 | -0.003172 | -0.017566 | -0.034862 | -0.059167 | -0.050335 | 0.010206 | 0.051413 | 0.078197 | -0.047194 | -0.12152 | -0.077866 | 0.003172 | -0.08173 | 122.6176 | -0.05775 | 122.6176 | 122.5899 | -0.027772 | -0.082055 | -0.073223 | 122.5257 | -0.14441 | 122.6588 | 122.5602 | 0.034536 | -0.10075 | -0.019716 | 122.5726 | 122.5483 | 122.5571 | 122.6042 | -0.012682 | 122.4859 | 122.5296 | 122.6106 | 122.6856 | -0.10462
2430.9219 | 122.7448 | -122.612 | 0.032043 | -0.013049 | -0.06748 | 0.061398 | -0.01322 | -0.0089375 | 0.0039591 | -0.011751 | -0.028072 | 0.02099 | -0.0054417 | 0.027681 | 0.0072065 | 0.014783 | 0.001407 | -0.008409 | -0.034862 | -0.063746 | -0.050335 | 0.001048 | 0.051413 | 0.082776 | -0.051772 | -0.1261 | -0.073287 | 0.003172 | -0.077151 | 122.613 | -0.066905 | 122.6268 | 122.6036 | -0.009457 | -0.095789 | -0.082378 | 122.5348 | -0.15815 | 122.6634 | 122.5602 | 0.025379 | -0.10533 | -0.028871 | 122.5771 | 122.5483 | 122.5617 | 122.6134 | -0.030995 | 122.4859 | 122.5387 | 122.6152 | 122.6948 | -0.10919
2432.6094 | 122.8226 | -122.6028 | 0.013733 | -0.013049 | -0.06748 | 0.061185 | -0.013434 | -0.0087239 | 0.0043865 | -0.034642 | -0.027858 | 0.021203 | -0.0056553 | 0.027895 | 0.0074201 | 0.019361 | 0.010564 | -0.017566 | -0.034862 | -0.063746 | -0.054914 | 0.010206 | 0.055992 | 0.078197 | -0.051772 | -0.1261 | -0.06413 | 0.007751 | -0.072572 | 122.6131 | -0.048595 | 122.6222 | 122.5853 | -0.027772 | -0.077479 | -0.068647 | 122.5303 | -0.13984 | 122.6588 | 122.5511 | 0.0208 | -0.077863 | -0.005982 | 122.568 | 122.5391 | 122.5479 | 122.6134 | -0.003527 | 122.4767 | 122.5387 | 122.6106 | 122.681 | -0.086305
2434.3281 | 122.8958 | -122.5708 | 0.004578 | -0.005418 | -0.06748 | 0.060971 | -0.013862 | -0.0089375 | 0.0041729 | -0.019381 | -0.028072 | 0.021417 | -0.0054417 | 0.028322 | 0.0074201 | 0.010204 | 0.001407 | -0.012988 | -0.034862 | -0.063746 | -0.054914 | 0.005627 | 0.051413 | 0.073618 | -0.056351 | -0.12152 | -0.059551 | 0.003172 | -0.067994 | 122.5764 | -0.03944 | 122.581 | 122.5578 | -0.018615 | -0.068324 | -0.059492 | 122.5028 | -0.1261 | 122.6222 | 122.5144 | 0.011643 | -0.064129 | -0.001406 | 122.5359 | 122.5071 | 122.5159 | 122.5722 | 0.001049 | 122.4493 | 122.5113 | 122.574 | 122.6444 | -0.072572
2436.0469 | 122.7493 | -122.612 | 0.050354 | -0.005418 | -0.06748 | 0.061185 | -0.01322 | -0.0089375 | 0.0041729 | -0.0041205 | -0.027858 | 0.021417 | -0.0052279 | 0.027681 | 0.0076339 | 0.005626 | 0.005985 | -0.008409 | -0.030283 | -0.063746 | -0.054914 | 0.010206 | 0.051413 | 0.073618 | -0.056351 | -0.11695 | -0.068708 | -0.001407 | -0.077151 | 122.6222 | -0.080637 | 122.6176 | 122.6036 | -0.018615 | -0.1141 | -0.10527 | 122.5348 | -0.1673 | 122.6634 | 122.5556 | 0.0208 | -0.11906 | -0.051761 | 122.5817 | 122.5483 | 122.5571 | 122.618 | -0.040148 | 122.4951 | 122.5433 | 122.6106 | 122.6856 | -0.12751
2437.7656 | 122.7676 | -122.6212 | 0.032043 | 0.002213 | -0.067694 | 0.060971 | -0.013862 | -0.0087239 | 0.0041729 | -0.011751 | -0.028072 | 0.02099 | -0.0054417 | 0.027895 | 0.0074201 | 0.005626 | 0.001407 | -0.008409 | -0.034862 | -0.059167 | -0.054914 | 0.010206 | 0.055992 | 0.073618 | -0.047194 | -0.12152 | -0.073287 | -0.001407 | -0.077151 | 122.6314 | -0.066905 | 122.6268 | 122.6127 | -0.018615 | -0.09121 | -0.086957 | 122.544 | -0.15357 | 122.6771 | 122.574 | 0.029957 | -0.10533 | -0.03345 | 122.5863 | 122.562 | 122.5662 | 122.6226 | -0.021837 | 122.4996 | 122.5479 | 122.6197 | 122.6948 | -0.10919
2439.4844 | 122.8592 | -122.5708 | 0.032043 | -0.005418 | -0.067694 | 0.060757 | -0.013862 | -0.0085103 | 0.0039591 | -0.011751 | -0.027858 | 0.021417 | -0.0056553 | 0.028322 | 0.0074201 | 0.005626 | -0.003172 | -0.012988 | -0.044018 | -0.054588 | -0.050335 | 0.010206 | 0.046835 | 0.082776 | -0.056351 | -0.13068 | -0.073287 | 0.003172 | -0.072572 | 122.581 | -0.076061 | 122.5764 | 122.5578 | -0.023194 | -0.086631 | -0.082378 | 122.4982 | -0.16272 | 122.6176 | 122.5144 | 0.016221 | -0.10533 | -0.028871 | 122.5268 | 122.5162 | 122.5205 | 122.5676 | -0.021837 | 122.4401 | 122.4975 | 122.574 | 122.6536 | -0.10461
2441.1719 | 122.7768 | -122.5845 | 0.027466 | -0.005418 | -0.067694 | 0.060757 | -0.013862 | -0.0089375 | 0.0039591 | -0.019381 | -0.027858 | 0.021417 | -0.0058689 | 0.028109 | 0.0069929 | 0.010204 | 0.005985 | -0.008409 | -0.030283 | -0.054588 | -0.045757 | 0.005627 | 0.046835 | 0.073618 | -0.051772 | -0.12152 | -0.06413 | 0.003172 | -0.067994 | 122.5902 | -0.057749 | 122.5947 | 122.5761 | -0.014036 | -0.082054 | -0.073223 | 122.5165 | -0.14899 | 122.6314 | 122.5328 | 0.016222 | -0.091596 | -0.024294 | 122.5543 | 122.5299 | 122.5388 | 122.5905 | -0.021839 | 122.463 | 122.5204 | 122.5877 | 122.6582 | -0.09546
2442.9219 | 122.7539 | -122.612 | 0.041199 | -0.005418 | -0.067907 | 0.06033 | -0.013648 | -0.0087239 | 0.0039591 | -0.0041205 | -0.027645 | 0.02099 | -0.0054417 | 0.028109 | 0.0069929 | 0.005626 | 0.001407 | -0.008409 | -0.03944 | -0.059167 | -0.050335 | 0.014784 | 0.055992 | 0.06904 | -0.051772 | -0.11237 | -0.06413 | 0.003172 | -0.072572 | 122.6268 | -0.080639 | 122.6176 | 122.6036 | -0.023193 | -0.10037 | -0.091534 | 122.5394 | -0.15357 | 122.668 | 122.5602 | 0.0208 | -0.10533 | -0.038027 | 122.5726 | 122.5528 | 122.5617 | 122.6134 | -0.026415 | 122.4996 | 122.5479 | 122.6152 | 122.681 | -0.11377
2444.6094 | 122.7814 | -122.5983 | 0.032043 | -0.013049 | -0.06748 | 0.06033 | -0.013648 | -0.0087239 | 0.0041729 | -0.0041205 | -0.028072 | 0.02099 | -0.0052279 | 0.028322 | 0.0074201 | 0.005626 | 0.001407 | -0.008409 | -0.030283 | -0.059167 | -0.050335 | 0.010206 | 0.055992 | 0.078197 | -0.051772 | -0.12152 | -0.059551 | -0.001407 | -0.072572 | 122.6085 | -0.062326 | 122.6039 | 122.5899 | -0.018615 | -0.09121 | -0.082378 | 122.5257 | -0.15357 | 122.6543 | 122.5465 | 0.0208 | -0.091594 | -0.03345 | 122.568 | 122.5391 | 122.5479 | 122.5997 | -0.021837 | 122.4767 | 122.5387 | 122.5969 | 122.6765 | -0.10461
2446.3281 | 122.8821 | -122.5479 | 0.013733 | -0.005418 | -0.067694 | 0.060757 | -0.013434 | -0.0089375 | 0.0041729 | -0.011751 | -0.028072 | 0.021203 | -0.0054417 | 0.027895 | 0.0072065 | 0.010204 | 0.001407 | -0.012988 | -0.034862 | -0.050009 | -0.045757 | 0.005627 | 0.051413 | 0.073618 | -0.051772 | -0.1261 | -0.059551 | 0.003172 | -0.072572 | 122.5535 | -0.048595 | 122.5581 | 122.5349 | -0.018615 | -0.063742 | -0.05949 | 122.4753 | -0.13984 | 122.5993 | 122.4961 | 0.0208 | -0.073284 | -0.010561 | 122.5131 | 122.4979 | 122.5022 | 122.5493 | -0.008106 | 122.4218 | 122.4884 | 122.5511 | 122.6215 | -0.086305
2448.0312 | 122.7676 | -122.5845 | 0.045776 | 0.002213 | -0.067907 | 0.060544 | -0.013434 | -0.0087239 | 0.0041729 | -0.011751 | -0.028072 | 0.02099 | -0.0056553 | 0.028322 | 0.0072065 | 0.010204 | 0.005985 | -0.003831 | -0.030283 | -0.063746 | -0.050335 | 0.014784 | 0.051413 | 0.078197 | -0.051772 | -0.1261 | -0.059551 | 0.003172 | -0.067994 | 122.5993 | -0.076059 | 122.5947 | 122.5807 | -0.018615 | -0.10952 | -0.096111 | 122.5165 | -0.17188 | 122.6359 | 122.5328 | 0.016222 | -0.10533 | -0.042604 | 122.5543 | 122.5208 | 122.5342 | 122.5905 | -0.030992 | 122.4584 | 122.525 | 122.5877 | 122.6627 | -0.11377
2449.7344 | 122.7631 | -122.6166 | 0.050354 | -0.005418 | -0.068121 | 0.060544 | -0.013434 | -0.0089375 | 0.0039591 | -0.027012 | -0.027858 | 0.02099 | -0.0056553 | 0.027895 | 0.0074201 | 0.014783 | 0.005985 | 0.000747 | -0.030283 | -0.059167 | -0.059493 | 0.010206 | 0.051413 | 0.06904 | -0.047194 | -0.1261 | -0.059551 | 0.003172 | -0.067994 | 122.6268 | -0.080637 | 122.6314 | 122.6173 | -0.009459 | -0.10952 | -0.10985 | 122.5486 | -0.17646 | 122.668 | 122.5694 | 0.0208 | -0.10991 | -0.047182 | 122.5863 | 122.5574 | 122.5571 | 122.6226 | -0.040148 | 122.4905 | 122.557 | 122.6197 | 122.6856 | -0.11835
2451.4219 | 122.7127 | -122.5983 | 0.045776 | -0.013049 | -0.067694 | 0.060971 | -0.013434 | -0.0089375 | 0.0039591 | -0.027012 | -0.027858 | 0.020776 | -0.0054417 | 0.028109 | 0.0072065 | 0.014783 | 0.001407 | -0.003831 | -0.034862 | -0.063746 | -0.054914 | 0.010206 | 0.055992 | 0.06904 | -0.047194 | -0.1261 | -0.06413 | 0.003172 | -0.063415 | 122.6085 | -0.080638 | 122.6131 | 122.5944 | -0.014037 | -0.10952 | -0.10069 | 122.5349 | -0.17188 | 122.6543 | 122.5511 | 0.016221 | -0.10991 | -0.042604 | 122.5634 | 122.5345 | 122.5434 | 122.5997 | -0.03557 | 122.4722 | 122.5341 | 122.6014 | 122.6673 | -0.10919
2453.125 | 122.8455 | -122.5708 | 0.022888 | -0.005418 | -0.067907 | 0.060757 | -0.013648 | -0.0089375 | 0.0039591 | -0.0041205 | -0.027858 | 0.021203 | -0.0056553 | 0.027895 | 0.0072065 | 0.010204 | 0.005985 | -0.008409 | -0.034862 | -0.054588 | -0.045757 | 0.010206 | 0.051413 | 0.064461 | -0.047194 | -0.12152 | -0.06413 | 0.003172 | -0.063415 | 122.581 | -0.05775 | 122.581 | 122.5624 | -0.018615 | -0.077476 | -0.068645 | 122.5074 | -0.14441 | 122.6222 | 122.5236 | 0.016221 | -0.087018 | -0.019716 | 122.5359 | 122.5162 | 122.525 | 122.5768 | -0.012682 | 122.4493 | 122.5067 | 122.574 | 122.6353 | -0.086303
2454.8281 | 122.7356 | -122.6166 | 0.045776 | -0.005418 | -0.06748 | 0.06033 | -0.013862 | -0.0089375 | 0.0041729 | -0.011751 | -0.028072 | 0.021203 | -0.0052279 | 0.028109 | 0.0072065 | 0.014783 | -0.003172 | -0.008409 | -0.030283 | -0.050009 | -0.054914 | 0.005627 | 0.060571 | 0.06904 | -0.047194 | -0.11695 | -0.068708 | 0.012329 | -0.058836 | 122.6222 | -0.076059 | 122.6314 | 122.6082 | -0.014036 | -0.095785 | -0.10069 | 122.5577 | -0.16272 | 122.6771 | 122.5694 | 0.011642 | -0.11448 | -0.033447 | 122.5863 | 122.5666 | 122.5617 | 122.6134 | -0.040149 | 122.4996 | 122.5479 | 122.6289 | 122.6856 | -0.10461
2456.5312 | 122.7768 | -122.6074 | 0.027466 | -0.013049 | -0.067907 | 0.060544 | -0.013648 | -0.0089375 | 0.0041729 | -0.011751 | -0.027858 | 0.02099 | -0.0052279 | 0.028109 | 0.0072065 | 0.019361 | 0.001407 | -0.008409 | -0.030283 | -0.054588 | -0.050335 | 0.001048 | 0.055992 | 0.073618 | -0.047194 | -0.1261 | -0.068708 | 0.012329 | -0.067994 | 122.6085 | -0.057749 | 122.6268 | 122.599 | -0.009457 | -0.082054 | -0.077801 | 122.5394 | -0.15357 | 122.6634 | 122.5602 | 0.0208 | -0.096174 | -0.015137 | 122.5771 | 122.5528 | 122.5571 | 122.6088 | -0.026418 | 122.4813 | 122.5387 | 122.6198 | 122.681 | -0.09546
2458.2344 | 122.7951 | -122.5891 | 0.041199 | -0.013049 | -0.06748 | 0.06033 | -0.013648 | -0.0089375 | 0.0037455 | -0.019381 | -0.027645 | 0.021417 | -0.0058689 | 0.028109 | 0.0069929 | 0.010204 | 0.005985 | -0.003831 | -0.044018 | -0.059167 | -0.045757 | 0.010206 | 0.055992 | 0.073618 | -0.06093 | -0.1261 | -0.059551 | 0.003172 | -0.063415 | 122.5993 | -0.085217 | 122.5993 | 122.5853 | -0.014037 | -0.10037 | -0.086956 | 122.5257 | -0.1673 | 122.6451 | 122.5282 | 0.002485 | -0.10075 | -0.038027 | 122.5451 | 122.5299 | 122.5434 | 122.5951 | -0.030993 | 122.463 | 122.5296 | 122.5923 | 122.6627 | -0.10461
2459.9844 | 122.7722 | -122.5983 | 0.050354 | -0.005418 | -0.067694 | 0.06033 | -0.013434 | -0.0087239 | 0.0041729 | -0.011751 | -0.027858 | 0.021203 | -0.0056553 | 0.027895 | 0.0072065 | 0.014783 | 0.005985 | -0.003831 | -0.030283 | -0.054588 | -0.054914 | 0.010206 | 0.055992 | 0.078197 | -0.047194 | -0.12152 | -0.059551 | 0.003172 | -0.067994 | 122.6085 | -0.080637 | 122.6131 | 122.5944 | -0.014037 | -0.10494 | -0.10527 | 122.5303 | -0.17188 | 122.6543 | 122.5511 | 0.0208 | -0.10991 | -0.047182 | 122.568 | 122.5437 | 122.5434 | 122.6043 | -0.040148 | 122.4767 | 122.5387 | 122.6014 | 122.6765 | -0.11835
2461.6875 | 122.8226 | -122.5433 | 0.009155 | -0.005418 | -0.067907 | 0.06033 | -0.013648 | -0.0087239 | 0.0039591 | -0.011751 | -0.027858 | 0.020776 | -0.0056553 | 0.027681 | 0.0074201 | 0.014783 | 0.010564 | -0.003831 | -0.030283 | -0.063746 | -0.050335 | 0.005627 | 0.055992 | 0.073618 | -0.051772 | -0.12152 | -0.059551 | 0.007751 | -0.067994 | 122.549 | -0.039438 | 122.5581 | 122.5395 | -0.009458 | -0.072901 | -0.05949 | 122.4753 | -0.13068 | 122.5993 | 122.4916 | 0.016222 | -0.068706 | -0.001404 | 122.5131 | 122.4796 | 122.493 | 122.5539 | -0.003528 | 122.4218 | 122.4838 | 122.5511 | 122.617 | -0.077149
2463.3906 | 122.8638 | -122.5571 | 0.027466 | 0.002213 | -0.068335 | 0.060544 | -0.013434 | -0.0091513 | 0.0037455 | -0.011751 | -0.027645 | 0.020776 | -0.0052279 | 0.027895 | 0.0069929 | 0.023939 | 0.005985 | -0.008409 | -0.025705 | -0.059167 | -0.045757 | 0.010206 | 0.051413 | 0.064461 | -0.047194 | -0.1261 | -0.06413 | 0.007751 | -0.072572 | 122.5673 | -0.053171 | 122.581 | 122.5487 | -0.018615 | -0.086633 | -0.073223 | 122.4845 | -0.15357 | 122.6085 | 122.5099 | 0.025378 | -0.091596 | -0.019715 | 122.5314 | 122.4979 | 122.5113 | 122.5631 | -0.01726 | 122.431 | 122.4929 | 122.5648 | 122.6215 | -0.10004
2465.0938 | 122.7448 | -122.5845 | 0.041199 | -0.005418 | -0.068121 | 0.060544 | -0.013434 | -0.0089375 | 0.0037455 | -0.0041205 | -0.027858 | 0.02099 | -0.0054417 | 0.027895 | 0.0072065 | 0.019361 | 0.005985 | -0.008409 | -0.034862 | -0.054588 | -0.054914 | 0.010206 | 0.055992 | 0.06904 | -0.051772 | -0.13526 | -0.06413 | 0.003172 | -0.067994 | 122.5947 | -0.076061 | 122.6039 | 122.5761 | -0.018615 | -0.095787 | -0.096113 | 122.5165 | -0.17646 | 122.6405 | 122.5328 | 0.016222 | -0.10533 | -0.038027 | 122.5497 | 122.5299 | 122.5296 | 122.5905 | -0.030993 | 122.4493 | 122.5204 | 122.5877 | 122.6536 | -0.10919
2466.7969 | 122.8546 | -122.5021 | 0.022888 | 0.002213 | -0.068121 | 0.06033 | -0.013434 | -0.0089375 | 0.0037455 | -0.019381 | -0.027858 | 0.02099 | -0.0058689 | 0.027895 | 0.0069929 | 0.014783 | 0.001407 | -0.003831 | -0.034862 | -0.054588 | -0.054914 | 0.019363 | 0.051413 | 0.06904 | -0.056351 | -0.12152 | -0.059551 | 0.007751 | -0.063415 | 122.5215 | -0.05775 | 122.5169 | 122.4983 | -0.023194 | -0.077476 | -0.077802 | 122.4387 | -0.14441 | 122.5535 | 122.4458 | 0.007064 | -0.082439 | -0.015137 | 122.4673 | 122.4475 | 122.4472 | 122.5035 | -0.003525 | 122.3806 | 122.4426 | 122.5099 | 122.5712 | -0.086303
2468.5781 | 122.7493 | -122.5708 | 0.054932 | -0.005418 | -0.068121 | 0.06033 | -0.013648 | -0.0087239 | 0.0039591 | -0.011751 | -0.028072 | 0.02099 | -0.0056553 | 0.028322 | 0.0074201 | 0.014783 | 0.010564 | -0.003831 | -0.030283 | -0.059167 | -0.045757 | 0.019363 | 0.055992 | 0.073618 | -0.051772 | -0.11695 | -0.059551 | -0.001407 | -0.063415 | 122.5902 | -0.085215 | 122.5856 | 122.567 | -0.023194 | -0.1141 | -0.10069 | 122.5074 | -0.17188 | 122.6268 | 122.519 | 0.011643 | -0.11448 | -0.056339 | 122.5405 | 122.5116 | 122.525 | 122.5814 | -0.035569 | 122.4539 | 122.5113 | 122.5694 | 122.6444 | -0.11835
2470.3594 | 122.7951 | -122.5433 | 0.027466 | -0.013049 | -0.068121 | 0.06033 | -0.01322 | -0.0089375 | 0.0041729 | -0.019381 | -0.027858 | 0.02099 | -0.0054417 | 0.028109 | 0.0072065 | 0.014783 | 0.001407 | 0.000747 | -0.034862 | -0.059167 | -0.050335 | 0.010206 | 0.055992 | 0.059882 | -0.047194 | -0.12152 | -0.068708 | 0.003172 | -0.067994 | 122.5535 | -0.062328 | 122.5581 | 122.5441 | -0.009459 | -0.086633 | -0.077801 | 122.4753 | -0.14899 | 122.5993 | 122.4961 | 0.0208 | -0.096174 | -0.024294 | 122.5085 | 122.4842 | 122.493 | 122.5447 | -0.01726 | 122.4218 | 122.4746 | 122.5465 | 122.6032 | -0.09546
2472.125 | 122.8043 | -122.5479 | 0.022888 | -0.005418 | -0.068121 | 0.06033 | -0.013434 | -0.0089375 | 0.0039591 | -0.027012 | -0.027858 | 0.02099 | -0.0054417 | 0.028109 | 0.0072065 | 0.014783 | 0.010564 | -0.003831 | -0.030283 | -0.059167 | -0.050335 | 0.010206 | 0.051413 | 0.064461 | -0.047194 | -0.13068 | -0.059551 | 0.007751 | -0.067994 | 122.5581 | -0.053171 | 122.5627 | 122.5441 | -0.014037 | -0.082055 | -0.073223 | 122.4799 | -0.15357 | 122.5993 | 122.5007 | 0.0208 | -0.082439 | -0.015137 | 122.5176 | 122.4887 | 122.4976 | 122.5585 | -0.012682 | 122.4172 | 122.4884 | 122.5557 | 122.6124 | -0.090882
2473.8281 | 122.7905 | -122.525 | 0.064087 | -0.005418 | -0.068335 | 0.060757 | -0.013648 | -0.0091513 | 0.0039591 | -0.011751 | -0.028072 | 0.02099 | -0.0054417 | 0.028322 | 0.0072065 | 0.014783 | 0.005985 | -0.008409 | -0.025705 | -0.059167 | -0.050335 | 0.019363 | 0.051413 | 0.073618 | -0.047194 | -0.11695 | -0.059551 | 0.003172 | -0.063415 | 122.5444 | -0.089792 | 122.5398 | 122.5166 | -0.027772 | -0.12325 | -0.11442 | 122.4616 | -0.18103 | 122.5764 | 122.4778 | 0.016221 | -0.12364 | -0.060915 | 122.4993 | 122.4659 | 122.4747 | 122.531 | -0.044724 | 122.4081 | 122.4655 | 122.5282 | 122.5986 | -0.1275
2475.5781 | 122.8134 | -122.5021 | 0.013733 | -0.013049 | -0.068121 | 0.060757 | -0.013434 | -0.0087239 | 0.0039591 | -0.019381 | -0.027858 | 0.02099 | -0.0056553 | 0.028109 | 0.0076339 | 0.014783 | 0.010564 | 0.000747 | -0.025705 | -0.050009 | -0.045757 | 0.014784 | 0.051413 | 0.078197 | -0.047194 | -0.1261 | -0.054973 | 0.003172 | -0.058836 | 122.5169 | -0.039438 | 122.5169 | 122.5029 | -0.014037 | -0.063742 | -0.05949 | 122.4433 | -0.13984 | 122.5535 | 122.4549 | 0.011642 | -0.068706 | -0.010561 | 122.4764 | 122.4521 | 122.4564 | 122.5127 | 0.001051 | 122.376 | 122.4472 | 122.5053 | 122.5803 | -0.072569
2477.2812 | 122.5937 | -122.4335 | 0.041199 | 0.002213 | -0.06919 | 0.061398 | -0.01322 | -0.0093649 | 0.0037455 | 0.00351 | -0.027645 | 0.020776 | -0.0056553 | 0.028322 | 0.0074201 | 0.023939 | 0.019721 | 0.009904 | -0.016548 | -0.040851 | -0.032021 | 0.023942 | 0.060571 | 0.082776 | -0.051772 | -0.1261 | -0.059551 | 0.012329 | -0.063415 | 122.4574 | -0.057747 | 122.4574 | 122.4434 | -0.014038 | -0.08205 | -0.07322 | 122.3701 | -0.1673 | 122.494 | 122.3817 | 0.011643 | -0.10075 | -0.02887 | 122.4169 | 122.3926 | 122.4015 | 122.4532 | -0.017257 | 122.3074 | 122.3739 | 122.4458 | 122.5162 | -0.10461
2479.0469 | 122.6578 | -122.4792 | 0.064087 | -0.013049 | -0.068121 | 0.060757 | -0.01322 | -0.0087239 | 0.0037455 | -0.011751 | -0.027858 | 0.020776 | -0.0056553 | 0.028536 | 0.0072065 | 0.019361 | 0.001407 | 0.005325 | -0.030283 | -0.04543 | -0.050335 | 0.010206 | 0.051413 | 0.078197 | -0.047194 | -0.11695 | -0.068708 | 0.003172 | -0.058836 | 122.4895 | -0.09437 | 122.4986 | 122.4846 | -0.004881 | -0.10952 | -0.11442 | 122.4204 | -0.18103 | 122.5307 | 122.4321 | 0.011642 | -0.13279 | -0.060915 | 122.449 | 122.4338 | 122.4289 | 122.4807 | -0.053881 | 122.3623 | 122.4105 | 122.4824 | 122.5574 | -0.12292
2480.75 | 122.7539 | -122.4472 | 0.018311 | -0.013049 | -0.068335 | 0.060544 | -0.013434 | -0.0091513 | 0.0039591 | -0.019381 | -0.028072 | 0.020562 | -0.0056553 | 0.028109 | 0.0072065 | 0.019361 | 0.005985 | 0.005325 | -0.034862 | -0.054588 | -0.050335 | 0.005627 | 0.046835 | 0.06904 | -0.051772 | -0.13068 | -0.068708 | -0.001407 | -0.072572 | 122.4528 | -0.053173 | 122.4666 | 122.4525 | -0.000302 | -0.072899 | -0.068646 | 122.3746 | -0.14899 | 122.494 | 122.3954 | 0.0208 | -0.087019 | -0.019718 | 122.4123 | 122.3926 | 122.3969 | 122.4532 | -0.012684 | 122.3165 | 122.3785 | 122.4458 | 122.5162 | -0.090883
2482.5156 | 122.8592 | -122.493 | 0.018311 | -0.013049 | -0.067907 | 0.06033 | -0.013648 | -0.0091513 | 0.0035319 | -0.019381 | -0.027858 | 0.02099 | -0.0058689 | 0.028322 | 0.0067793 | 0.019361 | -0.003172 | -0.003831 | -0.030283 | -0.054588 | -0.050335 | 0.005627 | 0.051413 | 0.082776 | -0.056351 | -0.1261 | -0.06413 | -0.001407 | -0.058836 | 122.4986 | -0.048594 | 122.5123 | 122.4891 | -0.009458 | -0.072899 | -0.068646 | 122.4341 | -0.14441 | 122.5444 | 122.4366 | 0.002485 | -0.082441 | -0.019718 | 122.4627 | 122.4384 | 122.4426 | 122.4898 | -0.012684 | 122.3669 | 122.4289 | 122.4916 | 122.5758 | -0.077147
2484.2656 | 122.7127 | -122.4655 | 0.050354 | -0.005418 | -0.068335 | 0.060544 | -0.013434 | -0.0089375 | 0.0037455 | -0.019381 | -0.027645 | 0.020776 | -0.0056553 | 0.028109 | 0.0069929 | 0.014783 | 0.005985 | 0.000747 | -0.030283 | -0.054588 | -0.050335 | 0.019363 | 0.055992 | 0.073618 | -0.047194 | -0.11695 | -0.059551 | 0.007751 | -0.058836 | 122.4849 | -0.080637 | 122.4803 | 122.4663 | -0.018616 | -0.10494 | -0.10069 | 122.4067 | -0.1673 | 122.5215 | 122.4183 | 0.011642 | -0.10991 | -0.042603 | 122.4352 | 122.4109 | 122.4152 | 122.4715 | -0.030991 | 122.3486 | 122.406 | 122.4733 | 122.5391 | -0.10919
2486.0156 | 122.6669 | -122.493 | 0.059509 | -0.005418 | -0.068121 | 0.060544 | -0.013648 | -0.0089375 | 0.0037455 | -0.011751 | -0.027645 | 0.020776 | -0.0054417 | 0.028536 | 0.0069929 | 0.019361 | 0.005985 | 0.000747 | -0.034862 | -0.054588 | -0.050335 | 0.010206 | 0.051413 | 0.06904 | -0.047194 | -0.12152 | -0.06413 | 0.007751 | -0.058836 | 122.5032 | -0.094371 | 122.5123 | 122.4937 | -0.009459 | -0.1141 | -0.10984 | 122.4341 | -0.18103 | 122.5444 | 122.4458 | 0.011642 | -0.12364 | -0.051758 | 122.4581 | 122.4384 | 122.4426 | 122.499 | -0.049303 | 122.3715 | 122.4289 | 122.5007 | 122.562 | -0.11835
2487.7188 | 122.6807 | -122.4838 | 0.050354 | 0.002213 | -0.068121 | 0.060971 | -0.013648 | -0.0087239 | 0.0039591 | -0.011751 | -0.027858 | 0.02099 | -0.0056553 | 0.028109 | 0.0069929 | 0.019361 | -0.003172 | 0.000747 | -0.025705 | -0.068325 | -0.041178 | 0.014784 | 0.055992 | 0.073618 | -0.056351 | -0.1261 | -0.068708 | 0.007751 | -0.058836 | 122.4986 | -0.076059 | 122.5032 | 122.4846 | -0.014037 | -0.11868 | -0.091532 | 122.425 | -0.17646 | 122.5398 | 122.4275 | 0.002485 | -0.11906 | -0.042603 | 122.4581 | 122.4155 | 122.4426 | 122.4807 | -0.03557 | 122.3577 | 122.4151 | 122.4916 | 122.5574 | -0.10919
2489.4844 | 122.5571 | -122.3831 | 0.11902 | 0.002213 | -0.068976 | 0.060971 | -0.01322 | -0.0091513 | 0.0039591 | -0.011751 | -0.027431 | 0.02099 | -0.0056553 | 0.028322 | 0.0072065 | 0.028518 | 0.019721 | 0.01906 | -0.016548 | -0.050009 | -0.041178 | 0.019363 | 0.060571 | 0.082776 | -0.038036 | -0.11695 | -0.06413 | 0.007751 | -0.054257 | 122.4025 | -0.13557 | 122.4116 | 122.4022 | -0.000303 | -0.16903 | -0.1602 | 122.3289 | -0.23596 | 122.4437 | 122.3451 | 0.016221 | -0.18315 | -0.11127 | 122.3666 | 122.3331 | 122.3419 | 122.4028 | -0.099656 | 122.2662 | 122.319 | 122.3909 | 122.4659 | -0.17328
2491.1875 | 122.3328 | -121.9574 | 0.31586 | 0.002213 | -0.070685 | 0.062253 | -0.012793 | -0.0091513 | 0.0035319 | -0.019381 | -0.027858 | 0.021203 | -0.0054417 | 0.028109 | 0.0069929 | 0.037675 | 0.033457 | 0.032795 | -0.002813 | -0.027115 | -0.018285 | 0.042258 | 0.06515 | 0.087354 | -0.038036 | -0.12152 | -0.050394 | 0.007751 | -0.049678 | 121.9997 | -0.31867 | 121.9951 | 121.9902 | -0.009463 | -0.34297 | -0.33414 | 121.9077 | -0.43738 | 122.0225 | 121.9194 | 0.011642 | -0.36625 | -0.30811 | 121.9546 | 121.9303 | 121.9391 | 121.9909 | -0.2736 | 121.8359 | 121.907 | 121.9651 | 122.0448 | -0.36553
2492.9531 | 122.5113 | -122.3007 | 0.004578 | 0.009844 | -0.068335 | 0.060116 | -0.013434 | -0.0091513 | 0.0035319 | -0.011751 | -0.027858 | 0.02099 | -0.0056553 | 0.028109 | 0.0074201 | 0.010204 | 0.001407 | -0.003831 | -0.030283 | -0.059167 | -0.054914 | 0.001048 | 0.055992 | 0.073618 | -0.056351 | -0.12152 | -0.06413 | 0.007751 | -0.063415 | 122.3018 | -0.034861 | 122.3109 | 122.2969 | -0.004879 | -0.063745 | -0.059492 | 122.2373 | -0.1261 | 122.3567 | 122.2444 | 0.007064 | -0.068708 | 0.003173 | 122.2704 | 122.2416 | 122.2458 | 122.3021 | -0.00353 | 122.1792 | 122.2366 | 122.3085 | 122.3743 | -0.067993
2494.7031 | 122.6303 | -122.374 | 0.022888 | -0.013049 | -0.068121 | 0.06033 | -0.013862 | -0.0085103 | 0.0035319 | -0.011751 | -0.027858 | 0.021203 | -0.0054417 | 0.028109 | 0.0072065 | 0.010204 | 0.010564 | 0.005325 | -0.034862 | -0.054588 | -0.045757 | 0.010206 | 0.051413 | 0.073618 | -0.047194 | -0.13068 | -0.059551 | 0.003172 | -0.063415 | 122.3842 | -0.05775 | 122.3842 | 122.3793 | -0.004881 | -0.077476 | -0.068645 | 122.3105 | -0.15357 | 122.4254 | 122.3268 | 0.016221 | -0.082439 | -0.019716 | 122.3391 | 122.3194 | 122.3282 | 122.3845 | -0.012682 | 122.2433 | 122.3144 | 122.3771 | 122.4476 | -0.086303
2496.4062 | 122.5891 | -122.438 | 0.041199 | -0.005418 | -0.067907 | 0.060544 | -0.013862 | -0.0089375 | 0.0039591 | -0.019381 | -0.027431 | 0.02099 | -0.0056553 | 0.028109 | 0.0072065 | 0.010204 | 0.001407 | 0.005325 | -0.030283 | -0.054588 | -0.045757 | 0.005627 | 0.051413 | 0.073618 | -0.056351 | -0.12152 | -0.068708 | 0.003172 | -0.058836 | 122.4437 | -0.071482 | 122.4483 | 122.4434 | -0.000302 | -0.095787 | -0.086956 | 122.3792 | -0.16272 | 122.4895 | 122.3817 | 0.002485 | -0.10991 | -0.038027 | 122.4078 | 122.3835 | 122.3923 | 122.4395 | -0.035572 | 122.3165 | 122.3693 | 122.4412 | 122.5117 | -0.10003

## Thermal Data
Fire Time | A Position - Middle | C Position - 3' | C Position - Middle | C Position - 7'
-0.0115 | 14.3882 | 10.184 | 11.0177 | 10.7294
0.9885 | 15.7546 | 10.3208 | 11.1248 | 10.9646
1.9885 | 17.1176 | 10.5821 | 11.4872 | 11.3413
2.9885 | 18.5299 | 11.1009 | 12.2135 | 12.3634
3.9885 | 22.1659 | 11.7054 | 12.6569 | 13.5147
4.9885 | 26.108 | 12.3431 | 13.7354 | 14.177
5.9885 | 30.7716 | 13.5371 | 14.5802 | 15.9515
6.9885 | 34.5481 | 14.2982 | 15.1424 | 17.0973
7.9885 | 38.3323 | 15.6583 | 16.7748 | 18.1374
8.9885 | 41.159 | 18.021 | 17.6755 | 19.259
9.9885 | 43.3338 | 19.2964 | 18.9951 | 20.7693
10.9885 | 47.4701 | 20.5155 | 20.4626 | 22.3277
11.9885 | 51.2885 | 22.0632 | 21.7587 | 23.5003
12.9885 | 54.5182 | 23.8556 | 23.3828 | 25.5834
13.9885 | 57.5085 | 25.3416 | 25.1678 | 27.3661
14.9885 | 61.2242 | 27.6511 | 27.0673 | 29.5144
15.9885 | 64.3916 | 29.8083 | 28.7288 | 31.7035
16.9885 | 68.0072 | 32.024 | 31.2379 | 34.1514
17.9885 | 71.5582 | 33.3064 | 33.3156 | 36.5188
18.9885 | 76.8949 | 35.5353 | 35.5103 | 39.5325
19.9885 | 80.9865 | 37.8854 | 37.7398 | 42.1869
20.9885 | 84.2908 | 41.3283 | 41.3718 | 44.7042
21.9885 | 87.957 | 43.9339 | 44.4337 | 46.9708
22.9885 | 89.8068 | 46.3714 | 46.9103 | 49.3935
23.9885 | 91.8901 | 47.8444 | 48.3753 | 51.1758
24.9885 | 92.7914 | 50.1467 | 50.9909 | 53.1569
25.9885 | 93.4893 | 51.8537 | 50.9125 | 55.999
26.9885 | 94.8782 | 53.0108 | 55.3552 | 57.7964
27.9885 | 97.0945 | 54.1795 | 54.9601 | 60.1405
28.9885 | 99.4971 | 55.8281 | 55.4046 | 61.434
29.9885 | 103.2254 | 57.4656 | 58.4652 | 63.3135
30.9885 | 106.629 | 59.0694 | 62.5808 | 64.616
31.9885 | 108.4187 | 60.8116 | 63.7904 | 66.7494
32.9885 | 111.3789 | 62.0121 | 62.8303 | 67.7897
33.9885 | 112.8953 | 64.2942 | 64.7674 | 69.0395
34.9885 | 114.8258 | 66.0651 | 67.9335 | 70.4023
35.9885 | 115.5648 | 67.6843 | 66.2629 | 72.1834
36.9885 | 115.5223 | 69.5644 | 68.5867 | 73.8715
37.9885 | 115.5914 | 71.2358 | 70.0945 | 75.4608
38.9885 | 115.5891 | 72.022 | 73.4755 | 77.5007
39.9885 | 116.0614 | 72.6651 | 72.1922 | 78.7279
40.9885 | 115.913 | 74.2955 | 71.9599 | 80.6737
41.9885 | 116.201 | 74.9553 | 74.6389 | 81.7953
42.9885 | 116.2362 | 75.9887 | 75.4001 | 83.7454
43.9885 | 115.8508 | 76.976 | 76.9021 | 84.8059
44.9885 | 116.8535 | 77.5995 | 79.7073 | 85.2163
45.9885 | 117.2071 | 78.957 | 84.1308 | 86.3596
46.9885 | 117.0441 | 80.4258 | 83.2153 | 88.22
47.9885 | 117.8264 | 81.5239 | 87.6948 | 89.2155
48.9885 | 118.13 | 82.8581 | 88.9504 | 90.1456
49.9885 | 119.8949 | 84.7556 | 90.2675 | 91.3262
50.9885 | 121.3921 | 85.9471 | 87.2859 | 92.5027
51.9885 | 122.5267 | 87.8626 | 92.6791 | 93.6736
52.9885 | 123.9934 | 89.3272 | 93.6927 | 95.5255
53.9885 | 124.7469 | 90.7166 | 94.8748 | 96.2869
54.9885 | 125.7384 | 91.5412 | 95.9466 | 97.1943
55.9885 | 127.7705 | 92.5495 | 97.4079 | 98.1131
56.9885 | 129.1996 | 93.4801 | 97.8858 | 99.0594
57.9885 | 132.4602 | 94.2102 | 99.125 | 100.168
58.9885 | 133.6144 | 95.9653 | 99.8547 | 100.9438
59.9885 | 136.0397 | 97.0212 | 100.5739 | 101.3444
60.9885 | 136.1493 | 97.2585 | 101.4601 | 101.7307
61.9885 | 135.8884 | 98.6709 | 102.5646 | 102.3507
62.9885 | 135.5148 | 100.0866 | 103.4215 | 102.8597
63.9885 | 136.5296 | 101.1129 | 104.1456 | 103.5843
64.9885 | 137.2046 | 101.4871 | 105.8819 | 104.6981
65.9885 | 138.1894 | 102.6842 | 106.8815 | 105.5483
66.9885 | 139.836 | 103.4088 | 107.714 | 106.0226
67.9885 | 140.5032 | 105.0492 | 108.865 | 107.0941
68.9885 | 140.2597 | 105.8484 | 109.4501 | 108.4074
69.9885 | 139.5907 | 106.108 | 109.8377 | 109.2149
70.9885 | 139.2297 | 106.4779 | 110.4655 | 110.0847
71.9885 | 139.4321 | 106.9761 | 111.3002 | 110.7364
72.9885 | 138.8572 | 108.2889 | 111.9792 | 111.2337
73.9885 | 140.8459 | 108.6731 | 112.392 | 111.7909
74.9885 | 142.9308 | 109.7969 | 113.201 | 112.2079
75.9885 | 143.8341 | 109.7995 | 113.8149 | 113.9412
76.9885 | 145.0962 | 110.527 | 114.6833 | 115.2498
77.9885 | 146.729 | 111.1803 | 115.2212 | 116.0226
78.9885 | 146.3405 | 111.9079 | 116.0762 | 117.0611
79.9885 | 146.5211 | 112.7225 | 116.5176 | 117.5365
80.9885 | 146.566 | 113.1946 | 117.0914 | 117.9918
81.9885 | 145.5591 | 114.5258 | 117.6743 | 118.8654
82.9885 | 146.8785 | 116.0447 | 118.4245 | 119.5129
83.9885 | 147.8977 | 116.7308 | 119.4087 | 120.3067
84.9885 | 148.5361 | 117.0763 | 120.1929 | 121.0538
85.9885 | 147.9591 | 117.9291 | 121.4962 | 121.8764
86.9885 | 150.7459 | 118.8798 | 121.9451 | 122.1789
87.9885 | 152.8113 | 119.904 | 122.4667 | 122.7097
88.9885 | 154.2124 | 119.7474 | 122.8691 | 123.2521
89.9885 | 153.3517 | 119.7909 | 123.1729 | 123.7288
90.9885 | 155.1736 | 121.072 | 123.6184 | 124.1538
91.9885 | 156.9091 | 121.46 | 124.1615 | 124.0998
92.9885 | 157.6626 | 122.3434 | 124.5784 | 124.1406
93.9885 | 159.2855 | 122.7037 | 124.7502 | 124.1714
94.9885 | 162.9172 | 122.3344 | 125.1237 | 124.9372
95.9885 | 165.2007 | 122.6839 | 125.276 | 125.8846
96.9885 | 165.8505 | 122.4226 | 125.3975 | 126.803
97.9885 | 166.452 | 122.6515 | 125.6374 | 127.1612
98.9885 | 168.0213 | 122.787 | 125.7156 | 127.2854
99.9885 | 170.5635 | 122.9593 | 125.8727 | 127.3789
100.9885 | 171.5883 | 122.9679 | 126.1816 | 127.6474
101.9885 | 174.543 | 123.0656 | 126.4185 | 128.3245
102.9885 | 177.8073 | 123.1774 | 126.5854 | 128.3271
103.9885 | 180.3553 | 123.1076 | 126.8224 | 128.3462
104.9885 | 180.0631 | 123.3761 | 127.01 | 128.6626
105.9885 | 183.0756 | 123.8424 | 127.3385 | 129.3584
106.9885 | 184.3864 | 124.4908 | 127.2211 | 129.8612
107.9885 | 185.9773 | 124.7143 | 127.4776 | 130.4122
108.9885 | 187.4808 | 125.05 | 127.54 | 130.9289
109.9885 | 187.7062 | 125.4105 | 128.414 | 131.3012
110.9885 | 186.3393 | 125.7535 | 128.5116 | 131.6993
111.9885 | 187.8176 | 125.9805 | 128.998 | 132.6911
112.9885 | 189.6016 | 126.6775 | 129.9879 | 133.5518
113.9885 | 188.9843 | 127.2509 | 130.1242 | 134.2376
114.9885 | 188.9462 | 127.491 | 130.5368 | 134.8273
115.9885 | 189.0166 | 127.9086 | 130.6405 | 135.4237
116.9885 | 189.1964 | 128.1963 | 130.3659 | 135.3087
117.9885 | 189.3628 | 128.3615 | 130.0075 | 135.3071
118.9885 | 188.2897 | 128.8448 | 130.0048 | 136.5358
119.9885 | 188.6473 | 128.9645 | 129.7537 | 136.7133
120.9885 | 187.4534 | 128.7893 | 130.0606 | 137.4149
121.9885 | 187.7154 | 128.5478 | 130.0744 | 138.0706
122.9885 | 186.061 | 128.3055 | 130.0844 | 138.6525
123.9885 | 186.9125 | 128.241 | 130.4059 | 138.6314
124.9885 | 187.0698 | 128.0193 | 130.9429 | 138.3606
125.9885 | 186.7987 | 128.3612 | 131.0375 | 138.3934
126.9885 | 186.2154 | 128.5594 | 131.3996 | 138.5449
127.9885 | 185.6278 | 128.6603 | 131.81 | 138.6511
128.9885 | 185.5246 | 129.6656 | 132.346 | 138.78
129.9885 | 185.778 | 130.2081 | 133.1054 | 139.2789
130.9885 | 186.3094 | 130.6202 | 133.3838 | 139.1419
131.9885 | 185.5223 | 130.3838 | 133.6002 | 138.7301
132.9885 | 185.4889 | 130.0657 | 133.7052 | 138.5225
133.9885 | 183.6962 | 130.3902 | 134.0899 | 138.3383
134.9885 | 183.8173 | 130.5329 | 133.9738 | 138.1524
135.9885 | 184.6762 | 131.5356 | 134.3099 | 137.9953
136.9885 | 184.4271 | 132.2567 | 134.8868 | 137.6281
137.9885 | 185.8831 | 132.4833 | 134.995 | 137.4538
138.9885 | 185.2684 | 132.7855 | 135.4246 | 137.3862
139.9885 | 184.9713 | 133.6274 | 135.6372 | 137.3185
140.9885 | 184.3508 | 134.0593 | 135.7988 | 137.7966
141.9885 | 185.8851 | 133.8966 | 136.0639 | 138.1658
142.9885 | 186.8055 | 134.5368 | 136.5057 | 138.5604
143.9885 | 188.1269 | 135.0641 | 136.6335 | 138.9107
144.9885 | 190.4662 | 135.695 | 137.1765 | 138.842
145.9885 | 192.1735 | 135.7656 | 137.2605 | 139.019
146.9885 | 192.7073 | 135.4342 | 137.4168 | 139.0956
147.9885 | 194.9527 | 135.2384 | 137.9457 | 139.363
148.9885 | 193.9874 | 135.4965 | 138.5659 | 139.8442
149.9885 | 193.0527 | 135.7324 | 139.1433 | 139.979
150.9885 | 192.9911 | 136.5484 | 139.3624 | 140.6416
151.9885 | 193.1708 | 136.5663 | 139.3891 | 140.9969
152.9885 | 193.7579 | 137.1955 | 139.8631 | 142.431
153.9885 | 192.3142 | 137.3579 | 140.1076 | 142.4274
154.9885 | 193.9109 | 137.6332 | 140.6965 | 142.9909
155.9885 | 194.0447 | 138.0448 | 141.1906 | 143.7164
156.9885 | 196.2558 | 138.6859 | 141.8787 | 143.5565
157.9885 | 195.1233 | 139.4525 | 142.4081 | 143.7739
158.9885 | 194.9533 | 139.9453 | 142.8324 | 144.0928
159.9885 | 195.9118 | 140.7335 | 143.1348 | 144.024
160.9885 | 196.9117 | 141.1777 | 143.1315 | 144.3541
161.9885 | 196.478 | 141.3035 | 143.2731 | 144.4561
162.9885 | 197.2395 | 140.9248 | 143.0092 | 144.3662
163.9885 | 197.7478 | 141.2508 | 143.0689 | 144.4306
164.9885 | 197.9015 | 141.9206 | 142.8162 | 144.5913
165.9885 | 198.3581 | 142.3716 | 142.9661 | 145.1149
166.9885 | 196.6221 | 142.6203 | 143.2926 | 145.1484
167.9885 | 199.7941 | 142.7552 | 143.7621 | 145.183
168.9885 | 200.2184 | 142.5447 | 144.0669 | 145.7518
169.9885 | 199.7774 | 143.2432 | 144.0125 | 145.9887
170.9885 | 198.2569 | 143.772 | 144.1368 | 145.935
171.9885 | 198.0992 | 143.7878 | 144.144 | 146.2656
172.9885 | 198.2838 | 143.3414 | 144.653 | 146.15
173.9885 | 197.6295 | 143.2545 | 145.2117 | 145.7668
174.9885 | 197.326 | 143.4351 | 145.0251 | 145.4318
175.9885 | 197.1084 | 144.2295 | 145.0126 | 145.3207
176.9885 | 198.1388 | 144.3382 | 145.0178 | 145.527
177.9885 | 197.76 | 143.935 | 144.9761 | 145.931
178.9885 | 198.3681 | 143.473 | 145.0073 | 146.1354
179.9885 | 199.1905 | 143.4019 | 145.0016 | 146.0161
180.9885 | 200.7158 | 142.9672 | 144.8454 | 146.0022
181.9885 | 201.5385 | 142.9383 | 144.7553 | 145.6835
182.9885 | 204.1945 | 143.3303 | 145.123 | 146.1641
183.9885 | 206.4704 | 143.3187 | 145.3726 | 146.6283
184.9885 | 206.9179 | 143.3803 | 145.5671 | 146.822
185.9885 | 206.4932 | 143.5349 | 145.7637 | 147.0496
186.9885 | 205.0975 | 143.6908 | 146.0063 | 147.0186
187.9885 | 204.372 | 143.5929 | 145.7011 | 147.2449
188.9885 | 203.4787 | 143.5292 | 145.7134 | 147.8302
189.9885 | 204.7392 | 143.9663 | 145.6978 | 148.0897
190.9885 | 204.076 | 144.2979 | 145.7477 | 147.8617
191.9885 | 203.5405 | 145.1621 | 145.7453 | 147.6589
192.9885 | 202.9251 | 145.0194 | 145.8066 | 147.4317
193.9885 | 201.0373 | 144.4103 | 145.778 | 147.5278
194.9885 | 201.3083 | 143.8968 | 145.9865 | 147.5771
195.9885 | 201.1045 | 144.277 | 146.1698 | 147.7079
196.9885 | 201.161 | 144.6936 | 146.4519 | 147.9581
197.9885 | 200.6071 | 144.9748 | 146.5931 | 148.3199
198.9885 | 200.754 | 144.9213 | 146.7374 | 148.918
199.9885 | 199.8958 | 144.7052 | 148.1972 | 149.1985
200.9885 | 200.6199 | 145.0195 | 148.5779 | 149.4698
201.9885 | 199.8635 | 145.8897 | 148.9113 | 150.4897
202.9885 | 200.2136 | 146.2323 | 149.121 | 150.56
203.9885 | 199.5064 | 147.4246 | 149.6237 | 150.6
204.9885 | 199.4877 | 148.2149 | 149.9788 | 151.3644
205.9885 | 200.961 | 148.4621 | 150.5822 | 151.5133
206.9885 | 199.9113 | 148.7871 | 151.2106 | 151.9178
207.9885 | 198.7314 | 148.935 | 151.78 | 153.0285
208.9885 | 198.8564 | 149.1711 | 151.8934 | 153.3792
209.9885 | 200.4735 | 149.6242 | 152.2593 | 153.8282
210.9885 | 198.1893 | 149.7349 | 152.4533 | 153.7217
211.9885 | 198.6324 | 149.7855 | 153.1406 | 154.2787
212.9885 | 199.2049 | 150.0816 | 153.3039 | 154.6416
213.9885 | 198.8643 | 150.4574 | 153.5435 | 154.8321
214.9885 | 199.5054 | 150.5338 | 153.8836 | 154.7701
215.9885 | 199.8685 | 150.6602 | 153.9957 | 154.8711
216.9885 | 198.2496 | 150.974 | 154.4624 | 154.7219
217.9885 | 196.8023 | 151.232 | 154.7326 | 154.3781
218.9885 | 195.0332 | 151.3744 | 154.8854 | 153.9653
219.9885 | 194.0942 | 151.5654 | 155.1179 | 153.8528
220.9885 | 194.6375 | 151.3738 | 155.538 | 154.5168
221.9885 | 195.4002 | 151.9121 | 156.4729 | 154.9342
222.9885 | 195.0433 | 152.149 | 156.4694 | 155.5007
223.9885 | 195.422 | 152.1763 | 156.6262 | 155.6191
224.9885 | 197.009 | 152.4747 | 156.8212 | 155.2772
225.9885 | 197.8017 | 152.5813 | 157.0323 | 155.0455
226.9885 | 198.8013 | 152.7534 | 157.2412 | 155.0148
227.9885 | 199.5276 | 153.4884 | 157.6961 | 154.9282
228.9885 | 201.5812 | 154.2229 | 158.039 | 154.9995
229.9885 | 201.2872 | 154.5232 | 158.3096 | 154.9928
230.9885 | 200.4261 | 154.349 | 158.4404 | 154.8346
231.9885 | 202.1301 | 154.8458 | 158.6017 | 155.0409
232.9885 | 204.1732 | 155.3038 | 158.6019 | 154.7738
233.9885 | 206.0655 | 155.1585 | 158.7386 | 154.5009
234.9885 | 206.5666 | 155.2765 | 158.7711 | 154.6392
235.9885 | 207.18 | 155.5741 | 158.9357 | 155.0076
236.9885 | 207.7724 | 155.8083 | 158.9094 | 155.3783
237.9885 | 208.3239 | 155.6366 | 158.9681 | 155.5158
238.9885 | 207.8839 | 155.6075 | 159.0599 | 155.5256
239.9885 | 208.5882 | 155.9159 | 159.4171 | 155.5778
240.9885 | 208.8175 | 155.6343 | 160.7119 | 156.3356
241.9885 | 207.959 | 155.4521 | 160.7327 | 156.1854
242.9885 | 208.5502 | 155.5361 | 160.6544 | 156.3371
243.9885 | 208.5841 | 155.4235 | 161.0616 | 156.7234
244.9885 | 209.6494 | 155.2313 | 161.5065 | 157.4167
245.9885 | 210.5123 | 154.9817 | 161.3695 | 157.7319
246.9885 | 212.419 | 154.8086 | 161.3465 | 157.8427
247.9885 | 212.4741 | 155.0992 | 161.2418 | 157.9646
248.9885 | 214.3084 | 155.1839 | 161.2451 | 158.0014
249.9885 | 215.6265 | 155.5977 | 161.0835 | 158.5003
250.9885 | 215.7589 | 155.9075 | 161.1458 | 158.382
251.9885 | 216.7861 | 156.5376 | 161.3432 | 158.6264
252.9885 | 218.7459 | 156.9595 | 161.4651 | 158.7739
253.9885 | 220.4027 | 157.0458 | 161.4307 | 158.8778
254.9885 | 220.3849 | 157.4645 | 161.624 | 159.0307
255.9885 | 221.0106 | 157.5105 | 162.3356 | 159.1209
256.9885 | 220.9764 | 158.0205 | 162.6641 | 159.0349
257.9885 | 220.4766 | 158.3768 | 162.7856 | 159.5265
258.9885 | 220.9648 | 159.1135 | 163.1035 | 159.9165
259.9885 | 221.2624 | 160.2321 | 163.7351 | 160.1803
260.9885 | 221.4856 | 160.2035 | 163.9916 | 160.2999
261.9885 | 222.7228 | 160.285 | 164.2576 | 160.7788
262.9885 | 220.5614 | 161.1742 | 164.3557 | 160.7058
263.9885 | 219.2652 | 161.3337 | 164.5552 | 160.6662
264.9885 | 220.3408 | 161.79 | 164.8639 | 160.8396
265.9885 | 220.115 | 162.6512 | 166.1407 | 161.4208
266.9885 | 220.1247 | 163.2008 | 166.4839 | 161.924
267.9885 | 221.2205 | 162.7395 | 166.8516 | 162.0725
268.9885 | 222.6563 | 162.6092 | 167.0662 | 162.2582
269.9885 | 223.3375 | 162.3221 | 167.294 | 162.7361
270.9885 | 226.3064 | 161.7233 | 167.4453 | 163.1377
271.9885 | 227.8108 | 161.8805 | 167.5932 | 163.5659
272.9885 | 230.0535 | 161.6126 | 167.7975 | 164.0966
273.9885 | 232.5899 | 161.5907 | 167.9498 | 164.2058
274.9885 | 232.895 | 161.8014 | 168.0945 | 164.3192
275.9885 | 232.2217 | 162.1733 | 168.0724 | 165.4139
276.9885 | 233.3686 | 162.1353 | 168.4396 | 165.1018
277.9885 | 231.7267 | 163.5471 | 168.7139 | 164.7424
278.9885 | 235.4472 | 163.7325 | 169.1414 | 164.8348
279.9885 | 236.4791 | 163.6997 | 169.621 | 165.0584
280.9885 | 237.2088 | 164.2662 | 169.7869 | 165.0354
281.9885 | 237.717 | 164.666 | 169.755 | 165.2802
282.9885 | 240.6201 | 164.8569 | 169.6773 | 165.5321
283.9885 | 239.1515 | 165.146 | 169.7775 | 165.6951
284.9885 | 243.3553 | 165.7689 | 169.9373 | 165.9597
285.9885 | 243.9762 | 165.9695 | 170.3142 | 166.3385
286.9885 | 246.974 | 165.9455 | 170.6176 | 166.4406
287.9885 | 249.4776 | 166.1909 | 171.0012 | 166.7222
288.9885 | 252.4071 | 166.5573 | 171.0901 | 167.1387
289.9885 | 253.6185 | 166.9647 | 171.6382 | 167.8426
290.9885 | 256.1404 | 167.0771 | 171.7183 | 168.0992
291.9885 | 256.1294 | 167.1666 | 171.8539 | 168.4305
292.9885 | 255.097 | 167.9768 | 172.1551 | 168.5581
293.9885 | 256.7574 | 169.4338 | 172.5093 | 168.9277
294.9885 | 256.6482 | 170.0156 | 172.5919 | 169.6932
295.9885 | 257.5153 | 171.0531 | 172.6464 | 170.0001
296.9885 | 273.7505 | 171.7747 | 173.034 | 170.5695
297.9885 | 288.6446 | 171.3436 | 173.4146 | 170.788
298.9885 | 297.6854 | 171.4478 | 173.8159 | 170.8545
299.9885 | 296.335 | 171.3462 | 174.0753 | 170.6303
300.9885 | 297.5058 | 171.8923 | 174.168 | 170.6697
301.9885 | 296.1728 | 172.1833 | 174.2467 | 170.7622
302.9885 | 295.8779 | 171.7563 | 174.6215 | 170.6717
303.9885 | 296.2883 | 172.0797 | 174.7848 | 170.5672
304.9885 | 297.1311 | 171.9301 | 175.0761 | 171.8692
305.9885 | 297.5145 | 171.7898 | 175.363 | 172.2148
306.9885 | 316.3197 | 171.5934 | 175.343 | 172.2454
307.9885 | 313.282 | 171.7588 | 175.5057 | 172.4691
308.9885 | 311.2478 | 172.0577 | 175.6047 | 172.4962
309.9885 | 311.3099 | 172.0635 | 175.5834 | 172.8738
310.9885 | 308.2628 | 171.6863 | 175.5302 | 173.3445
311.9885 | 309.416 | 171.5864 | 176.0389 | 173.8769
312.9885 | 308.3583 | 172.0832 | 176.3023 | 174.4469
313.9885 | 306.949 | 172.2996 | 176.7783 | 174.6169
314.9885 | 308.7163 | 172.9455 | 177.3246 | 174.9987
315.9885 | 308.8873 | 172.6227 | 177.6868 | 175.1728
316.9885 | 309.0887 | 172.6612 | 178.2535 | 175.7704
317.9885 | 310.7092 | 173.0344 | 178.4836 | 176.4892
318.9885 | 309.2369 | 173.7978 | 179.1472 | 176.836
319.9885 | 313.258 | 174.4409 | 179.2565 | 176.9568
320.9885 | 314.712 | 175.0079 | 179.4028 | 176.8972
321.9885 | 316.7881 | 175.4199 | 179.4409 | 176.9438
322.9885 | 318.0895 | 175.7656 | 179.5191 | 176.9767
323.9885 | 317.677 | 176.9257 | 179.7578 | 177.1046
324.9885 | 320.1649 | 177.0683 | 179.7945 | 177.4823
325.9885 | 323.9931 | 177.1268 | 179.9807 | 178.2011
326.9885 | 324.8942 | 177.258 | 180.2784 | 178.7001
327.9885 | 322.4458 | 177.4917 | 180.8043 | 179.2958
328.9885 | 322.5465 | 177.4557 | 182.3904 | 180.1611
329.9885 | 320.2062 | 177.8341 | 183.1138 | 180.799
330.9885 | 320.6593 | 178.3289 | 183.441 | 181.1921
331.9885 | 321.7497 | 178.8869 | 183.5839 | 181.8423
332.9885 | 324.3875 | 179.0302 | 183.8845 | 181.6415
333.9885 | 326.8393 | 179.6199 | 184.5911 | 181.5206
334.9885 | 332.0503 | 179.499 | 184.4754 | 181.6574
335.9885 | 334.634 | 179.4916 | 184.4536 | 181.671
336.9885 | 357.2708 | 180.1188 | 184.6786 | 181.9708
337.9885 | 369.5878 | 181.1164 | 184.6339 | 182.2646
338.9885 | 375.1844 | 181.7787 | 184.4446 | 182.2062
339.9885 | 411.6388 | 182.1236 | 184.5397 | 182.1364
340.9885 | 437.7987 | 182.6627 | 184.4428 | 182.1555
341.9885 | 452.2412 | 182.6879 | 184.9307 | 182.3297
342.9885 | 464.6511 | 182.9967 | 185.0944 | 182.5154
343.9885 | 483.9421 | 182.7134 | 185.0486 | 182.8513
344.9885 | 478.3682 | 182.5541 | 185.1439 | 182.8836
345.9885 | 473.3161 | 183.0016 | 185.47 | 182.5265
346.9885 | 470.5982 | 183.7041 | 185.2523 | 182.6642
347.9885 | 487.942 | 184.3299 | 185.7943 | 182.8117
348.9885 | 489.8593 | 185.0718 | 186.3405 | 183.0187
349.9885 | 484.0014 | 185.2589 | 186.0596 | 182.922
350.9885 | 477.1669 | 185.7954 | 186.0358 | 183.1696
351.9885 | 471.2899 | 186.3982 | 186.0591 | 183.4842
352.9885 | 464.3695 | 186.7446 | 186.3141 | 184.1428
353.9885 | 462.1087 | 187.5057 | 186.7408 | 184.3125
354.9885 | 454.8943 | 188.223 | 187.3229 | 185.1583
355.9885 | 450.9224 | 188.9636 | 187.8191 | 185.6547
356.9885 | 455.3707 | 189.9306 | 188.337 | 186.1325
357.9885 | 450.8933 | 190.1356 | 188.8916 | 186.871
358.9885 | 447.8558 | 190.2366 | 188.5167 | 187.3537
359.9885 | 442.3072 | 190.5646 | 189.4786 | 187.3908
360.9885 | 436.3271 | 190.6616 | 189.6813 | 187.6342
361.9885 | 434.2347 | 190.7586 | 189.8084 | 188.3059
362.9885 | 431.9915 | 191.5308 | 189.8137 | 188.7219
363.9885 | 428.5091 | 192.2679 | 190.1161 | 189.4143
364.9885 | 426.3772 | 191.7667 | 190.2567 | 189.5021
365.9885 | 427.9156 | 191.4843 | 190.3786 | 189.6976
366.9885 | 426.0717 | 192.3419 | 191.1863 | 189.6059
367.9885 | 422.3327 | 192.0543 | 191.5051 | 189.9444
368.9885 | 421.2784 | 191.798 | 191.8715 | 190.6552
369.9885 | 420.4016 | 192.3326 | 192.5619 | 191.2433
370.9885 | 421.2949 | 192.416 | 192.8531 | 191.5199
371.9885 | 419.7245 | 193.0848 | 192.8281 | 191.7545
372.9885 | 423.2063 | 193.5954 | 193.5286 | 191.709
373.9885 | 423.0247 | 193.7314 | 194.1952 | 192.0925
374.9885 | 424.4666 | 193.9947 | 195.146 | 191.8896
375.9885 | 425.7271 | 194.3433 | 194.9576 | 192.2066
376.9885 | 427.0939 | 194.5799 | 195.3933 | 191.897
377.9885 | 425.3134 | 194.0633 | 195.4982 | 191.8537
378.9885 | 425.8092 | 193.7506 | 195.2238 | 191.6733
379.9885 | 426.8008 | 193.8211 | 194.9524 | 191.7128
380.9885 | 426.953 | 193.9569 | 195.0992 | 192.2058
381.9885 | 426.547 | 193.9402 | 195.5667 | 192.7674
382.9885 | 427.3405 | 194.3606 | 195.7205 | 192.8612
383.9885 | 427.3091 | 195.1064 | 196.1695 | 192.7567
384.9885 | 427.9189 | 196.2804 | 196.7443 | 192.9002
385.9885 | 430.8602 | 196.8525 | 197.3057 | 193.2586
386.9885 | 433.9572 | 197.4626 | 197.926 | 193.6215
387.9885 | 435.6979 | 197.4203 | 198.4174 | 194.1684
388.9885 | 439.8072 | 196.9176 | 198.7498 | 194.3381
389.9885 | 446.606 | 197.3749 | 199.0992 | 193.7893
390.9885 | 449.1955 | 197.403 | 199.5298 | 194.2611
391.9885 | 451.7227 | 197.2145 | 199.8536 | 194.548
392.9885 | 455.8504 | 196.9034 | 200.1137 | 194.627
393.9885 | 461.2094 | 197.2826 | 200.5692 | 194.8959
394.9885 | 463.0455 | 197.6373 | 200.8071 | 195.387
395.9885 | 463.9579 | 197.5666 | 201.2463 | 195.7622
396.9885 | 464.6034 | 197.5764 | 201.6713 | 195.9503
397.9885 | 465.1399 | 197.5001 | 201.7798 | 196.0432
398.9885 | 472.1267 | 197.7329 | 201.7943 | 196.2379
399.9885 | 473.5135 | 197.6903 | 202.2189 | 196.7278
400.9885 | 474.4483 | 197.6068 | 202.4938 | 196.938
401.9885 | 478.5373 | 197.3446 | 202.799 | 197.2733
402.9885 | 482.3987 | 197.5208 | 202.7518 | 197.5837
403.9885 | 484.3836 | 197.7485 | 202.5308 | 197.7687
404.9885 | 484.343 | 197.4398 | 202.3742 | 197.7976
405.9885 | 484.6111 | 197.6451 | 201.9688 | 197.9561
406.9885 | 488.0014 | 197.8047 | 202.4941 | 198.8287
407.9885 | 493.2442 | 198.0377 | 202.6682 | 199.3303
408.9885 | 498.418 | 198.0422 | 202.918 | 200.296
409.9885 | 501.1432 | 198.3429 | 203.2859 | 200.8746
410.9885 | 511.4801 | 199.3491 | 203.1441 | 202.3616
411.9885 | 514.2493 | 199.5138 | 203.2685 | 203.4247
412.9885 | 522.0577 | 200.1041 | 202.9554 | 203.8423
413.9885 | 521.0423 | 199.8695 | 202.7954 | 204.8002
414.9885 | 522.0416 | 200.0496 | 203.0091 | 205.9031
415.9885 | 524.1771 | 199.7773 | 203.5461 | 207.0507
416.9885 | 530.422 | 199.8066 | 203.7915 | 208.4688
417.9885 | 544.0491 | 200.2034 | 205.0618 | 208.923
418.9885 | 568.0145 | 200.5619 | 204.6632 | 208.8657
419.9885 | 567.9243 | 201.2851 | 204.7144 | 209.5813
420.9885 | 565.5619 | 201.5934 | 205.4776 | 209.9787
421.9885 | 570.3543 | 201.9013 | 205.4574 | 210.4131
422.9885 | 570.4482 | 202.4373 | 205.7102 | 210.7927
423.9885 | 569.19 | 203.4363 | 205.8598 | 211.1755
424.9885 | 572.7513 | 203.8999 | 205.7548 | 211.8961
425.9885 | 572.9268 | 204.4709 | 206.8749 | 213.1441
426.9885 | 571.1283 | 204.6839 | 207.3392 | 212.9963
427.9885 | 588.4649 | 204.4059 | 206.9725 | 213.2802
428.9885 | 598.1019 | 203.7901 | 206.8056 | 213.0926
429.9885 | 597.9608 | 203.5403 | 206.6772 | 213.1446
430.9885 | 598.852 | 203.6508 | 206.6876 | 213.1799
431.9885 | 595.1874 | 203.3408 | 206.9923 | 212.9901
432.9885 | 601.4147 | 202.7545 | 206.8424 | 212.8587
433.9885 | 600.459 | 202.5254 | 206.9333 | 212.3867
434.9885 | 605.6903 | 202.5958 | 207.1592 | 212.4425
435.9885 | 603.1864 | 203.2561 | 207.3736 | 212.3233
436.9885 | 596.6018 | 203.4568 | 207.8144 | 212.2963
437.9885 | 593.9502 | 203.5336 | 208.1035 | 212.1513
438.9885 | 592.8664 | 202.995 | 208.4558 | 211.8599
439.9885 | 598.2846 | 203.1519 | 208.2396 | 211.5367
440.9885 | 606.7365 | 203.5739 | 207.9532 | 211.3657
441.9885 | 604.0945 | 203.4424 | 207.8521 | 211.1775
442.9885 | 601.2005 | 203.1601 | 207.7917 | 211.2208
443.9885 | 599.3189 | 203.853 | 208.0229 | 211.9454
444.9885 | 596.5668 | 203.6855 | 208.3071 | 212.6757
445.9885 | 595.651 | 203.1746 | 208.2318 | 213.0344
446.9885 | 599.0211 | 203.1578 | 208.0429 | 213.1307
447.9885 | 600.1927 | 203.2843 | 207.9957 | 213.3677
448.9885 | 609.5423 | 204.9865 | 207.6892 | 213.4829
449.9885 | 614.3616 | 205.4697 | 207.803 | 214.4021
450.9885 | 617.2313 | 205.3945 | 207.738 | 214.6589
451.9885 | 616.8323 | 204.9105 | 208.3831 | 215.256
452.9885 | 614.2087 | 204.7898 | 208.7864 | 215.1689
453.9885 | 612.7648 | 204.2252 | 209.2161 | 215.1614
454.9885 | 608.9928 | 204.1986 | 210.01 | 214.9614
455.9885 | 610.0138 | 204.0903 | 209.8793 | 215.2044
456.9885 | 611.1174 | 204.2291 | 209.5986 | 215.2155
457.9885 | 606.3233 | 204.8134 | 210.7917 | 215.4382
458.9885 | 607.6854 | 204.9343 | 210.3929 | 214.8585
459.9885 | 605.5196 | 205.439 | 210.3722 | 214.4259
460.9885 | 601.0222 | 204.7422 | 210.452 | 214.3179
461.9885 | 607.0907 | 204.7124 | 210.5643 | 214.0042
462.9885 | 604.6053 | 204.8683 | 210.7406 | 213.6533
463.9885 | 600.9029 | 204.1522 | 210.5451 | 213.7028
464.9885 | 612.0958 | 204.8593 | 210.3123 | 214.0322
465.9885 | 620.4011 | 205.4191 | 210.4775 | 214.4733
466.9885 | 616.3433 | 205.8462 | 211.1638 | 214.874
467.9885 | 617.5856 | 206.3324 | 211.5422 | 215.3686
468.9885 | 616.6502 | 206.4423 | 211.7958 | 215.6933
469.9885 | 618.0759 | 206.5505 | 212.2377 | 216.0318
470.9885 | 613.2188 | 206.4688 | 212.4712 | 215.9403
471.9885 | 609.9602 | 206.2038 | 212.5659 | 215.4507
472.9885 | 610.9795 | 206.0582 | 212.6802 | 215.2006
473.9885 | 609.0423 | 206.1711 | 212.6555 | 215.1985
474.9885 | 608.313 | 206.0543 | 212.661 | 214.8104
475.9885 | 620.0991 | 205.8851 | 212.5132 | 214.9325
476.9885 | 625.1409 | 206.2557 | 212.7245 | 215.0692
477.9885 | 617.8323 | 206.5755 | 212.9496 | 214.7897
478.9885 | 628.0686 | 206.5026 | 213.2865 | 214.8731
479.9885 | 623.6603 | 207.2024 | 213.5964 | 215.0816
480.9885 | 646.2055 | 207.1829 | 213.728 | 214.5458
481.9885 | 640.9986 | 207.3225 | 213.4523 | 214.8576
482.9885 | 636.9986 | 207.6142 | 213.6431 | 215.1527
483.9885 | 635.2547 | 207.9677 | 213.9089 | 215.52
484.9885 | 636.743 | 208.0873 | 214.0722 | 215.7552
485.9885 | 637.2707 | 207.1475 | 214.2997 | 216.0604
486.9885 | 639.4283 | 206.6973 | 214.27 | 215.8677
487.9885 | 637.6548 | 206.2489 | 214.1367 | 215.7007
488.9885 | 637.7137 | 206.0156 | 213.7384 | 215.3354
489.9885 | 632.4029 | 206.4746 | 213.5433 | 215.0372
490.9885 | 643.2575 | 205.9111 | 213.4997 | 214.5207
491.9885 | 643.3994 | 206.2024 | 213.6049 | 214.202
492.9885 | 641.1547 | 206.4608 | 213.4627 | 214.2638
493.9885 | 640.352 | 207.0134 | 213.5071 | 214.1934
494.9885 | 647.8073 | 207.1097 | 214.1022 | 214.4263
495.9885 | 639.4889 | 207.1555 | 214.2558 | 215.0863
496.9885 | 637.1863 | 206.9646 | 214.4263 | 214.3
497.9885 | 650.9503 | 206.3941 | 214.5031 | 214.2744
498.9885 | 663.6558 | 206.6411 | 214.596 | 213.8999
499.9885 | 659.472 | 207.1864 | 214.7847 | 214.2421
500.9885 | 654.3892 | 206.7397 | 215.3215 | 215.3462
501.9885 | 661.1328 | 206.909 | 215.2994 | 216.0378
502.9885 | 663.4594 | 207.3277 | 215.0928 | 216.8779
503.9885 | 657.7352 | 207.4791 | 215.0353 | 217.0304
504.9885 | 657.4878 | 207.382 | 214.7044 | 217.1529
505.9885 | 666.793 | 207.8758 | 214.6345 | 217.6177
506.9885 | 664.0782 | 207.8262 | 214.4489 | 217.3103
507.9885 | 662.5541 | 207.1129 | 214.6876 | 217.4582
508.9885 | 659.7093 | 206.6161 | 215.0366 | 217.5144
509.9885 | 670.5354 | 206.4608 | 215.028 | 217.8229
510.9885 | 673.8352 | 206.6659 | 215.0898 | 218.766
511.9885 | 679.1859 | 206.7846 | 214.596 | 219.1389
512.9885 | 677.5311 | 206.8143 | 214.4616 | 219.727
513.9885 | 685.5665 | 207.5474 | 215.9592 | 219.837
514.9885 | 683.8864 | 208.1281 | 215.6949 | 219.5995
515.9885 | 682.0257 | 208.2839 | 215.7716 | 219.8614
516.9885 | 681.0992 | 208.2705 | 215.7185 | 220.2767
517.9885 | 673.2499 | 207.7685 | 215.2976 | 220.8855
518.9885 | 672.6764 | 207.1369 | 214.8597 | 221.0228
519.9885 | 675.7019 | 207.0593 | 214.8095 | 220.3491
520.9885 | 688.3959 | 206.9323 | 214.6714 | 219.962
521.9885 | 679.5305 | 207.2437 | 214.7688 | 219.6826
522.9885 | 672.1633 | 207.627 | 214.7709 | 219.0993
523.9885 | 666.4124 | 207.6659 | 214.4327 | 218.6486
524.9885 | 671.3103 | 208.1266 | 214.7799 | 218.3425
525.9885 | 668.8302 | 208.5599 | 214.7565 | 217.928
526.9885 | 666.2017 | 209.0881 | 214.8407 | 218.0235
527.9885 | 674.6551 | 209.169 | 214.9832 | 218.1624
528.9885 | 673.0816 | 209.249 | 215.2323 | 217.8121
529.9885 | 676.1473 | 209.8104 | 215.4303 | 218.1148
530.9885 | 678.0224 | 209.9526 | 215.2976 | 217.9019
531.9885 | 685.3518 | 209.6984 | 215.5047 | 218.6743
532.9885 | 682.6359 | 209.5493 | 215.3521 | 218.8504
533.9885 | 678.8287 | 210.0865 | 215.2862 | 219.2547
534.9885 | 681.5759 | 210.8676 | 214.9266 | 218.9851
535.9885 | 685.6644 | 211.0135 | 214.8729 | 218.6821
536.9885 | 677.8567 | 212.2554 | 214.8149 | 218.3834
537.9885 | 674.6309 | 212.4813 | 214.8736 | 218.2368
538.9885 | 675.1244 | 212.0233 | 215.0254 | 218.6096
539.9885 | 679.7059 | 211.3531 | 215.1722 | 218.1706
540.9885 | 684.5948 | 211.2489 | 215.4885 | 217.7079
541.9885 | 685.0836 | 210.8247 | 216.029 | 217.5223
542.9885 | 682.2539 | 210.5397 | 216.2262 | 217.0477
543.9885 | 677.2515 | 210.9596 | 216.725 | 216.9964
544.9885 | 682.5617 | 211.2771 | 216.7665 | 216.5884
545.9885 | 679.6482 | 211.1768 | 216.8058 | 217.0276
546.9885 | 678.6506 | 210.93 | 216.7505 | 217.0312
547.9885 | 679.8376 | 210.7227 | 216.7013 | 216.9991
548.9885 | 675.1148 | 210.3626 | 216.6408 | 216.8102
549.9885 | 672.3733 | 210.0135 | 216.5978 | 216.6367
550.9885 | 675.0397 | 209.8704 | 216.659 | 216.9814
551.9885 | 677.4736 | 210.016 | 216.7161 | 217.498
552.9885 | 684.7072 | 209.9072 | 216.7353 | 217.3749
553.9885 | 700.4551 | 210.1096 | 218.0248 | 217.4594
554.9885 | 706.5814 | 210.1499 | 217.7371 | 217.9974
555.9885 | 712.0765 | 210.3252 | 217.9536 | 218.5616
556.9885 | 706.9956 | 210.3962 | 217.9713 | 218.4803
557.9885 | 706.0798 | 210.5894 | 218.2683 | 218.5114
558.9885 | 710.1323 | 210.9133 | 218.4064 | 218.9542
559.9885 | 711.0524 | 210.7134 | 218.5122 | 218.9232
560.9885 | 710.1204 | 210.8213 | 218.852 | 219.6576
561.9885 | 710.3923 | 211.2167 | 218.4184 | 220.1224
562.9885 | 717.6189 | 211.3967 | 218.0603 | 220.8471
563.9885 | 720.2036 | 212.0758 | 217.744 | 221.9134
564.9885 | 724.7057 | 212.7532 | 217.1416 | 222.255
565.9885 | 721.5384 | 213.7876 | 217.1036 | 222.4158
566.9885 | 729.0187 | 214.2464 | 216.6156 | 222.9423
567.9885 | 731.3171 | 214.7658 | 216.2241 | 222.9484
568.9885 | 726.8472 | 214.6369 | 215.929 | 223.3144
569.9885 | 723.4712 | 215.2406 | 215.8401 | 224.0451
570.9885 | 726.8459 | 215.2413 | 215.7306 | 223.5327
571.9885 | 734.8876 | 215.3122 | 216.1591 | 223.5832
572.9885 | 732.5859 | 215.8421 | 216.9254 | 223.1297
573.9885 | 731.2225 | 215.9258 | 217.3668 | 223.0028
574.9885 | 723.3362 | 216.2498 | 217.7371 | 223.8332
575.9885 | 722.8161 | 216.3935 | 217.6362 | 223.5428
576.9885 | 718.9425 | 216.3632 | 217.3578 | 223.8715
577.9885 | 716.4333 | 217.12 | 217.271 | 224.208
578.9885 | 718.389 | 216.4014 | 217.1166 | 224.2062
579.9885 | 716.8782 | 216.2992 | 216.9885 | 223.9904
580.9885 | 712.2076 | 216.4805 | 216.6021 | 223.5338
581.9885 | 713.8578 | 216.4488 | 216.5864 | 223.3221
582.9885 | 709.9184 | 217.0259 | 216.5493 | 223.3052
583.9885 | 715.7554 | 217.0718 | 216.8401 | 223.527
584.9885 | 720.7311 | 216.4852 | 216.7999 | 223.3861
585.9885 | 712.3169 | 216.2265 | 216.9366 | 223.0605
586.9885 | 726.7488 | 216.093 | 216.6132 | 222.6563
587.9885 | 731.8553 | 216.1036 | 216.5711 | 222.5831
588.9885 | 731.4721 | 216.5083 | 216.3447 | 223.0827
589.9885 | 737.0783 | 217.2108 | 217.076 | 223.1458
590.9885 | 739.1074 | 217.4467 | 217.7875 | 223.6345
591.9885 | 736.6705 | 217.9464 | 218.014 | 223.7233
592.9885 | 749.487 | 218.3487 | 218.1145 | 224.2149
593.9885 | 746.8532 | 218.4457 | 218.0588 | 224.6656
594.9885 | 743.6789 | 218.58 | 218.2422 | 224.9013
595.9885 | 744.9457 | 218.9207 | 218.4669 | 225.6061
596.9885 | 746.4908 | 219.4581 | 218.2882 | 225.4042
597.9885 | 746.1717 | 219.9312 | 217.7719 | 224.9233
598.9885 | 742.0362 | 220.3422 | 217.5953 | 224.9264
599.9885 | 744.315 | 220.6417 | 217.7811 | 224.9533
600.9885 | 752.0049 | 221.4062 | 218.5404 | 225.3375
601.9885 | 755.0186 | 221.5556 | 218.6693 | 226.0084
602.9885 | 752.3057 | 221.606 | 219.5847 | 225.8206
603.9885 | 754.8099 | 221.3273 | 220.096 | 226.6193
604.9885 | 753.1588 | 221.47 | 220.1688 | 226.4655
605.9885 | 751.5533 | 222.2502 | 220.1573 | 226.6557
606.9885 | 747.9974 | 221.9052 | 220.1983 | 226.9475
607.9885 | 745.7911 | 221.6827 | 220.1632 | 226.6994
608.9885 | 743.7778 | 222.0504 | 220.0766 | 226.1376
609.9885 | 745.2636 | 222.1931 | 220.4421 | 225.5816
610.9885 | 741.7714 | 222.2031 | 220.0154 | 226.1871
611.9885 | 743.1095 | 222.314 | 219.9992 | 226.2837
612.9885 | 750.9418 | 222.5818 | 220.9046 | 227.0528
613.9885 | 754.2176 | 223.4204 | 221.2509 | 227.3766
614.9885 | 756.6337 | 223.9918 | 221.371 | 227.1932
615.9885 | 761.2272 | 224.58 | 221.3517 | 227.2848
616.9885 | 763.5025 | 225.1182 | 221.728 | 227.1841
617.9885 | 763.1482 | 225.522 | 221.4482 | 227.512
618.9885 | 765.7298 | 225.4808 | 221.0135 | 227.4884
619.9885 | 759.2749 | 225.7966 | 221.501 | 227.3193
620.9885 | 767.1406 | 226.1763 | 221.5293 | 227.7128
621.9885 | 765.6877 | 226.1177 | 221.2382 | 227.729
622.9885 | 769.7077 | 226.5891 | 222.0163 | 227.4156
623.9885 | 765.6902 | 226.8279 | 221.9484 | 227.0922
624.9885 | 765.786 | 226.7469 | 221.3319 | 227.4399
625.9885 | 767.8038 | 227.2914 | 220.7186 | 227.2593
626.9885 | 763.3911 | 227.2974 | 220.7547 | 226.8124
627.9885 | 769.9086 | 227.7365 | 220.775 | 226.9212
628.9885 | 766.4001 | 227.9139 | 220.613 | 226.9832
629.9885 | 762.0699 | 227.6651 | 220.7039 | 226.8412
630.9885 | 760.3992 | 228.015 | 219.976 | 227.5965
631.9885 | 759.355 | 227.8327 | 219.9681 | 227.8662
632.9885 | 761.5663 | 227.9131 | 220.0463 | 227.7804
633.9885 | 765.8787 | 227.9079 | 219.8145 | 227.5989
634.9885 | 758.739 | 228.1015 | 219.6088 | 227.6441
635.9885 | 762.5095 | 228.4453 | 219.3211 | 227.4686
636.9885 | 762.8207 | 228.7549 | 219.1375 | 227.3335
637.9885 | 760.7643 | 229.0204 | 218.9281 | 227.1227
638.9885 | 765.5838 | 228.987 | 218.9277 | 227.0705
639.9885 | 763.0336 | 229.1851 | 219.1092 | 227.583
640.9885 | 764.2337 | 228.9989 | 219.4321 | 227.3654
641.9885 | 764.0004 | 229.2356 | 219.5616 | 227.4673
642.9885 | 759.8963 | 229.098 | 220.0239 | 227.76
643.9885 | 761.0452 | 229.1518 | 220.0236 | 228.1167
644.9885 | 758.7046 | 228.8499 | 220.145 | 228.0207
645.9885 | 760.8847 | 228.9341 | 220.4412 | 227.4037
646.9885 | 762.153 | 228.5029 | 220.7323 | 226.9416
647.9885 | 765.3099 | 228.3718 | 220.647 | 226.8559
648.9885 | 770.6496 | 228.3121 | 220.7998 | 226.9251
649.9885 | 769.064 | 228.1421 | 220.5459 | 227.3261
650.9885 | 770.0592 | 228.138 | 220.5726 | 227.1027
651.9885 | 766.6115 | 228.1078 | 220.6756 | 226.7552
652.9885 | 765.0851 | 228.262 | 220.8174 | 226.9976
653.9885 | 763.6438 | 228.2442 | 221.0709 | 226.5479
654.9885 | 759.6528 | 228.5138 | 221.1695 | 226.8007
655.9885 | 761.4436 | 228.4699 | 221.6513 | 226.762
656.9885 | 764.8529 | 228.2528 | 221.7294 | 226.5738
657.9885 | 763.5619 | 228.1125 | 221.6904 | 226.3305
658.9885 | 763.3463 | 228.4104 | 221.6732 | 226.0532
659.9885 | 763.9889 | 229.0859 | 221.6677 | 226.2732
660.9885 | 759.9972 | 229.3713 | 221.9061 | 226.501
661.9885 | 761.6689 | 229.3613 | 222.321 | 226.1183
662.9885 | 765.4326 | 229.6603 | 222.78 | 226.4316
663.9885 | 759.205 | 229.8241 | 223.018 | 226.5836
664.9885 | 754.4934 | 229.8794 | 223.171 | 226.5129
665.9885 | 751.6253 | 229.8306 | 223.4625 | 226.7217
666.9885 | 757.4106 | 229.748 | 223.592 | 226.6593
667.9885 | 761.359 | 229.6512 | 223.526 | 226.7431
668.9885 | 762.7943 | 230.0967 | 223.5185 | 226.2948
669.9885 | 763.7905 | 230.2984 | 223.3941 | 226.2475
670.9885 | 765.6189 | 230.6719 | 223.4268 | 226.7693
671.9885 | 763.8895 | 230.7978 | 223.3644 | 226.7301
672.9885 | 763.5756 | 230.4116 | 223.1165 | 226.5485
673.9885 | 761.3107 | 230.2244 | 223.1124 | 226.9417
674.9885 | 758.7471 | 230.19 | 221.9615 | 227.1837
675.9885 | 757.1821 | 230.1809 | 222.0261 | 227.1838
676.9885 | 760.3996 | 230.2506 | 221.7453 | 227.0541
677.9885 | 757.4291 | 230.1961 | 221.5403 | 227.1034
678.9885 | 755.3151 | 230.5205 | 221.551 | 227.26
679.9885 | 756.9573 | 230.3253 | 221.8271 | 227.1111
680.9885 | 753.9975 | 230.0371 | 221.669 | 227.3209
681.9885 | 753.2958 | 229.7835 | 221.7656 | 227.5073
682.9885 | 757.2733 | 229.2761 | 222.1552 | 227.8154
683.9885 | 757.8362 | 228.6876 | 222.1746 | 227.6304
684.9885 | 758.6325 | 228.9066 | 222.3662 | 227.3563
685.9885 | 763.1117 | 228.9806 | 222.5574 | 227.2435
686.9885 | 767.7241 | 228.9623 | 223.0789 | 227.0818
687.9885 | 764.0941 | 228.9018 | 223.3178 | 227.2052
688.9885 | 759.432 | 229.5927 | 223.6892 | 228.3564
689.9885 | 758.0003 | 229.6197 | 223.9155 | 228.8243
690.9885 | 757.7909 | 229.7525 | 224.2716 | 229.4921
691.9885 | 760.5334 | 229.2865 | 224.3369 | 229.3191
692.9885 | 758.2555 | 229.1994 | 224.3276 | 229.596
693.9885 | 760.8964 | 229.2723 | 224.595 | 229.623
694.9885 | 763.4936 | 229.4372 | 224.5399 | 229.9651
695.9885 | 760.0684 | 229.6697 | 224.8337 | 230.1816
696.9885 | 760.0873 | 229.7105 | 224.3989 | 231.1813
697.9885 | 762.1548 | 229.5008 | 224.2703 | 230.8678
698.9885 | 767.9086 | 229.5346 | 224.4655 | 230.8058
699.9885 | 764.6575 | 229.8563 | 225.0633 | 230.7563
700.9885 | 770.3512 | 230.285 | 225.3286 | 230.7431
701.9885 | 769.9999 | 230.8059 | 226.1485 | 230.9666
702.9885 | 768.4717 | 231.0951 | 225.8279 | 230.7959
703.9885 | 764.999 | 231.8463 | 225.9346 | 230.9365
704.9885 | 767.7181 | 231.8394 | 225.8851 | 230.6411
705.9885 | 766.8792 | 231.9463 | 226.194 | 230.4658
706.9885 | 762.2558 | 232.367 | 226.6236 | 231.125
707.9885 | 757.3661 | 232.5681 | 226.0349 | 231.2686
708.9885 | 758.6715 | 232.457 | 226.0713 | 231.6715
709.9885 | 762.4634 | 232.4586 | 226.0883 | 231.7422
710.9885 | 761.6611 | 232.7403 | 226.3319 | 231.7612
711.9885 | 762.3834 | 232.165 | 225.9658 | 231.2003
712.9885 | 759.8748 | 232.3528 | 226.039 | 230.8909
713.9885 | 761.2777 | 232.4806 | 226.1814 | 230.3437
714.9885 | 754.1353 | 232.5335 | 226.5805 | 230.2966
715.9885 | 759.4672 | 232.3481 | 226.5374 | 230.6537
716.9885 | 763.219 | 232.0601 | 226.4008 | 230.5099
717.9885 | 764.0915 | 232.1945 | 227.0988 | 230.2194
718.9885 | 762.2367 | 232.1521 | 227.1521 | 230.3963
719.9885 | 761.2742 | 232.1064 | 227.5952 | 230.4312
720.9885 | 758.0951 | 231.9299 | 227.4532 | 230.1313
721.9885 | 754.3862 | 231.9202 | 227.3328 | 230.1157
722.9885 | 752.2608 | 230.9992 | 227.4493 | 229.891
723.9885 | 752.5481 | 230.8533 | 227.3091 | 229.9828
724.9885 | 751.9818 | 230.6521 | 227.7819 | 230.4375
725.9885 | 750.1284 | 230.6897 | 228.35 | 230.5451
726.9885 | 754.1376 | 230.9994 | 228.7328 | 230.3344
727.9885 | 751.206 | 231.0534 | 228.6596 | 230.0004
728.9885 | 752.5171 | 230.7622 | 229.1932 | 230.1787
729.9885 | 756.3829 | 230.785 | 230.3706 | 230.2394
730.9885 | 757.6409 | 230.8599 | 230.5207 | 230.1386
731.9885 | 757.6369 | 230.9974 | 230.6365 | 230.5115
732.9885 | 755.2544 | 231.177 | 230.7568 | 230.5664
733.9885 | 755.1257 | 231.4191 | 231.4881 | 230.556
734.9885 | 748.9267 | 231.1884 | 231.3637 | 230.3005
735.9885 | 748.7335 | 230.9179 | 231.1906 | 230.2813
736.9885 | 749.9577 | 230.7876 | 231.3225 | 230.3626
737.9885 | 753.8119 | 230.2741 | 231.3026 | 230.4411
738.9885 | 758.0081 | 230.1531 | 231.2305 | 230.4931
739.9885 | 762.5926 | 230.0438 | 231.2846 | 230.3519
740.9885 | 768.2149 | 230.5661 | 231.2641 | 230.2637
741.9885 | 767.3654 | 230.8755 | 231.2849 | 230.2789
742.9885 | 768.7012 | 231.228 | 231.2604 | 230.0706
743.9885 | 773.0602 | 231.3347 | 231.1615 | 229.8151
744.9885 | 769.2655 | 231.5807 | 231.465 | 230.0076
745.9885 | 767.8003 | 231.4758 | 231.3772 | 230.1563
746.9885 | 764.5103 | 231.5194 | 230.8892 | 230.1652
747.9885 | 764.4528 | 231.3999 | 231.0922 | 230.2942
748.9885 | 763.7978 | 231.5995 | 231.2015 | 230.3603
749.9885 | 767.0217 | 232.0366 | 231.5027 | 230.3461
750.9885 | 768.6633 | 232.2126 | 231.6669 | 230.5592
751.9885 | 768.8376 | 232.2495 | 231.9462 | 230.7692
752.9885 | 776.4298 | 232.6795 | 232.2574 | 230.5926
753.9885 | 777.4295 | 232.7947 | 232.2772 | 230.8695
754.9885 | 779.872 | 233.6264 | 232.4631 | 230.8236
755.9885 | 786.4968 | 233.931 | 232.5982 | 231.039
756.9885 | 783.2838 | 234.8345 | 232.8058 | 231.348
757.9885 | 781.3122 | 235.5758 | 233.3959 | 232.1655
758.9885 | 786.9898 | 236.454 | 233.4407 | 232.1402
759.9885 | 787.6287 | 236.6969 | 233.6004 | 232.8484
760.9885 | 794.2772 | 237.6018 | 234.4046 | 233.5884
761.9885 | 795.3088 | 237.4648 | 234.0812 | 233.8523
762.9885 | 789.1884 | 237.8347 | 234.7506 | 234.4264
763.9885 | 794.8325 | 238.2382 | 234.8596 | 234.7191
764.9885 | 796.6879 | 238.4027 | 235.3223 | 234.8058
765.9885 | 794.8625 | 238.8516 | 235.5229 | 235.5989
766.9885 | 792.1087 | 239.2863 | 235.1707 | 235.4673
767.9885 | 794.5659 | 239.2733 | 234.9722 | 235.5843
768.9885 | 790.1561 | 239.4958 | 235.779 | 235.2738
769.9885 | 790.0413 | 239.4277 | 235.942 | 235.4737
770.9885 | 783.3439 | 239.3615 | 235.9405 | 235.2952
771.9885 | 782.6467 | 239.6947 | 235.5672 | 235.013
772.9885 | 782.9361 | 240.1072 | 235.5438 | 235.2551
773.9885 | 782.187 | 240.6776 | 235.5278 | 235.05
774.9885 | 782.1753 | 241.3661 | 236.8642 | 235.3661
775.9885 | 780.8604 | 241.872 | 237.1998 | 235.7393
776.9885 | 785.4553 | 241.7418 | 237.2922 | 235.8011
777.9885 | 783.5278 | 241.8894 | 236.5375 | 236.2585
778.9885 | 784.7133 | 242.4931 | 237.3129 | 236.269
779.9885 | 783.5833 | 242.9368 | 237.4092 | 236.5015
780.9885 | 784.5627 | 243.1253 | 237.5311 | 236.9974
781.9885 | 781.4623 | 243.0147 | 239.7122 | 237.1988
782.9885 | 779.8365 | 243.306 | 239.1335 | 237.3831
783.9885 | 778.8307 | 243.5892 | 239.2111 | 237.877
784.9885 | 779.3922 | 244.0538 | 239.5088 | 237.5782
785.9885 | 778.708 | 244.5623 | 239.3677 | 237.5334
786.9885 | 780.7096 | 245.097 | 239.9072 | 237.9926
787.9885 | 785.5487 | 245.7134 | 239.87 | 238.1183
788.9885 | 787.7156 | 246.1784 | 239.9395 | 238.4675
789.9885 | 787.4278 | 246.7185 | 239.5843 | 239.1206
790.9885 | 788.2229 | 247.2177 | 240.1881 | 238.6307
791.9885 | 785.3138 | 247.4451 | 241.0537 | 238.8713
792.9885 | 779.7343 | 247.5557 | 241.336 | 239.0283
793.9885 | 780.6656 | 247.7697 | 241.4314 | 239.2116
794.9885 | 782.3747 | 247.8486 | 242.0639 | 239.5897
795.9885 | 786.2042 | 248.3184 | 242.0884 | 239.8232
796.9885 | 785.6681 | 248.1546 | 241.8524 | 239.8381
797.9885 | 783.5127 | 248.4079 | 241.8175 | 239.8537
798.9885 | 783.7496 | 248.4597 | 241.8812 | 239.4237
799.9885 | 785.0486 | 248.5241 | 242.0222 | 239.4558
800.9885 | 785.7511 | 248.5437 | 243.1022 | 239.7
801.9885 | 789.4019 | 249.1236 | 243.2129 | 239.7435
802.9885 | 790.1217 | 249.4569 | 242.2425 | 239.9612
803.9885 | 793.5624 | 249.3181 | 241.682 | 240.1153
804.9885 | 797.4111 | 249.2828 | 241.5393 | 240.3336
805.9885 | 792.9312 | 249.3068 | 241.4365 | 240.6135
806.9885 | 791.9352 | 249.3022 | 241.4629 | 240.9115
807.9885 | 789.4098 | 249.5536 | 241.6784 | 241.3386
808.9885 | 791.5042 | 249.5055 | 241.3503 | 241.1386
809.9885 | 793.5957 | 249.5291 | 241.1998 | 240.7601
810.9885 | 791.664 | 249.7181 | 241.6967 | 240.8951
811.9885 | 790.5824 | 250.2743 | 241.2334 | 241.6612
812.9885 | 794.1797 | 250.2277 | 241.3163 | 241.762
813.9885 | 793.5603 | 250.5526 | 242.0613 | 241.3888
814.9885 | 792.6542 | 250.5414 | 242.3555 | 241.2056
815.9885 | 792.2829 | 250.8468 | 242.9562 | 241.3583
816.9885 | 793.4615 | 251.3583 | 242.523 | 241.7163
817.9885 | 791.1665 | 251.9235 | 242.4884 | 241.6346
818.9885 | 793.6675 | 252.3002 | 242.173 | 241.5763
819.9885 | 793.6902 | 252.3087 | 242.3376 | 241.3417
820.9885 | 792.3111 | 252.4571 | 242.9504 | 241.4446
821.9885 | 784.7873 | 252.5775 | 243.2717 | 241.4618
822.9885 | 788.303 | 252.9191 | 243.4966 | 241.4852
823.9885 | 787.4687 | 252.9292 | 243.2279 | 241.2295
824.9885 | 786.6346 | 253.124 | 243.3729 | 241.2205
825.9885 | 784.182 | 253.3165 | 243.7517 | 241.094
826.9885 | 787.2959 | 253.7726 | 244.0186 | 241.2836
827.9885 | 786.3492 | 253.8506 | 244.4077 | 241.9553
828.9885 | 790.8547 | 254.0028 | 243.9198 | 242.2406
829.9885 | 786.6788 | 254.2374 | 243.9374 | 242.5954
830.9885 | 788.761 | 254.4614 | 244.1493 | 242.496
831.9885 | 787.7522 | 254.5117 | 244.1527 | 243.054
832.9885 | 788.0356 | 254.2247 | 245.1706 | 243.8242
833.9885 | 789.6765 | 254.5876 | 246.0943 | 244.1761
834.9885 | 787.899 | 254.3814 | 245.8871 | 244.9829
835.9885 | 788.0868 | 254.3986 | 245.8391 | 245.6085
836.9885 | 790.5499 | 254.8573 | 246.0488 | 246.3986
837.9885 | 790.9193 | 255.0814 | 245.9465 | 246.4361
838.9885 | 792.6087 | 256.0631 | 247.8769 | 246.239
839.9885 | 795.4473 | 256.0447 | 247.39 | 245.6311
840.9885 | 793.09 | 256.0869 | 247.6568 | 245.5393
841.9885 | 790.704 | 256.4543 | 247.992 | 245.6065
842.9885 | 782.8745 | 256.4523 | 248.8851 | 245.8771
843.9885 | 780.867 | 256.7766 | 249.4522 | 245.5837
844.9885 | 782.8909 | 256.5519 | 249.7655 | 245.545
845.9885 | 784.6307 | 256.8917 | 250.6929 | 245.7879
846.9885 | 780.0483 | 257.4919 | 250.9513 | 245.5183
847.9885 | 781.066 | 257.4174 | 251.3855 | 245.9993
848.9885 | 782.1769 | 257.4488 | 251.9899 | 246.0085
849.9885 | 775.1821 | 257.7506 | 252.2547 | 246.2305
850.9885 | 778.0485 | 258.3619 | 252.1607 | 246.7768
851.9885 | 778.0511 | 258.3369 | 252.8501 | 246.7183
852.9885 | 780.4554 | 258.3356 | 253.7092 | 246.4706
853.9885 | 784.2688 | 259.0794 | 253.7896 | 246.6302
854.9885 | 786.7076 | 259.7815 | 254.6125 | 247.1106
855.9885 | 785.8629 | 259.779 | 254.4766 | 246.5126
856.9885 | 784.5486 | 260.5165 | 254.4465 | 246.5357
857.9885 | 786.935 | 259.9563 | 254.8234 | 246.8936
858.9885 | 786.6877 | 259.7823 | 254.8141 | 246.4975
859.9885 | 787.396 | 258.932 | 254.6399 | 246.1203
860.9885 | 788.3939 | 258.7405 | 255.0529 | 246.3194
861.9885 | 789.39 | 259.0535 | 254.1312 | 246.6784
862.9885 | 790.2896 | 259.0333 | 253.923 | 246.6714
863.9885 | 785.7639 | 259.1672 | 253.7498 | 246.2758
864.9885 | 789.3124 | 259.7522 | 254.3596 | 245.9383
865.9885 | 796.8974 | 260.5176 | 254.8913 | 245.4022
866.9885 | 797.9203 | 261.115 | 255.4918 | 245.8411
867.9885 | 794.0188 | 261.4026 | 256.0866 | 246.8368
868.9885 | 798.0867 | 262.1649 | 256.6484 | 247.2054
869.9885 | 794.1199 | 261.873 | 257.3198 | 247.485
870.9885 | 793.6686 | 262.1176 | 258.2901 | 248.0796
871.9885 | 793.523 | 262.3044 | 259.1654 | 248.5024
872.9885 | 790.8933 | 262.4627 | 259.6238 | 249.1037
873.9885 | 790.6407 | 261.8949 | 260.3046 | 249.7749
874.9885 | 795.9169 | 262.044 | 260.5154 | 249.861
875.9885 | 793.6801 | 262.4084 | 260.4846 | 250.0897
876.9885 | 795.2974 | 262.8412 | 260.4304 | 250.5422
877.9885 | 795.6322 | 262.7211 | 260.569 | 250.2712
878.9885 | 800.2947 | 262.8427 | 260.8366 | 250.3592
879.9885 | 797.4234 | 263.6896 | 261.6686 | 250.8405
880.9885 | 798.0723 | 264.4407 | 262.0042 | 251.1487
881.9885 | 798.6126 | 264.8456 | 262.3477 | 251.7174
882.9885 | 799.4919 | 265.2875 | 263.2243 | 252.7118
883.9885 | 802.3833 | 266.1889 | 262.9129 | 252.9151
884.9885 | 804.6129 | 266.6713 | 262.7568 | 252.5722
885.9885 | 802.0514 | 266.9086 | 263.6003 | 253.2956
886.9885 | 804.6415 | 266.9891 | 263.4431 | 253.5269
887.9885 | 804.4339 | 267.2024 | 263.3531 | 253.5513
888.9885 | 802.2179 | 267.5061 | 265.2788 | 254.0544
889.9885 | 804.0195 | 267.8668 | 265.2898 | 254.1383
890.9885 | 800.6774 | 268.1488 | 266.2518 | 254.2025
891.9885 | 796.7873 | 267.9096 | 265.5922 | 254.922
892.9885 | 795.6002 | 268.0433 | 264.9344 | 255.395
893.9885 | 796.786 | 267.8392 | 264.5545 | 255.7472
894.9885 | 796.8334 | 268.0204 | 265.0415 | 256.6203
895.9885 | 791.6953 | 267.9803 | 265.3776 | 256.7079
896.9885 | 790.1538 | 268.313 | 265.6492 | 256.5863
897.9885 | 791.2644 | 268.6495 | 265.9467 | 256.7466
898.9885 | 793.8265 | 269.2096 | 266.3216 | 256.8268
899.9885 | 789.1106 | 269.6578 | 266.1325 | 257.3498
900.9885 | 788.386 | 270.0142 | 266.1201 | 257.9537
901.9885 | 788.8598 | 270.3064 | 266.1054 | 257.6192
902.9885 | 785.5529 | 270.705 | 265.8177 | 257.7677
903.9885 | 780.8492 | 270.5775 | 266.3346 | 257.3737
904.9885 | 781.7414 | 271.1846 | 267.2666 | 257.1368
905.9885 | 785.3036 | 271.3884 | 267.639 | 257.3235
906.9885 | 786.3284 | 272.2594 | 268.8696 | 257.4852
908.0042 | 790.5951 | 272.6304 | 269.896 | 257.6816
908.9885 | 789.5554 | 273.0356 | 269.8522 | 257.5777
909.9885 | 790.482 | 273.0323 | 270.4258 | 257.4012
910.9885 | 792.8813 | 273.1203 | 269.9694 | 257.5798
911.9885 | 795.3312 | 273.474 | 269.8004 | 257.4866
912.9885 | 796.0476 | 273.758 | 269.4349 | 257.3152
913.9885 | 795.8598 | 274.5847 | 269.2093 | 257.7348
914.9885 | 795.9981 | 275.2991 | 269.3658 | 258.4328
915.9885 | 798.0502 | 275.0998 | 270.1813 | 258.3884
916.9885 | 797.5672 | 275.1515 | 270.5616 | 258.4695
917.9885 | 796.4069 | 275.6711 | 271.3306 | 259.0959
918.9885 | 793.9517 | 276.1107 | 272.2775 | 259.418
919.9885 | 798.6875 | 276.7661 | 272.4169 | 259.2007
920.9885 | 794.5387 | 276.8942 | 272.3489 | 259.9633
921.9885 | 789.9305 | 276.477 | 272.0422 | 260.2614
922.9885 | 788.9741 | 276.525 | 271.8893 | 260.5864
923.9885 | 793.6346 | 276.6987 | 271.8773 | 260.9141
924.9885 | 799.6527 | 277.3983 | 272.2905 | 261.4452
925.9885 | 798.5528 | 276.893 | 272.4534 | 261.5809
926.9885 | 800.0599 | 276.9925 | 272.5117 | 260.5419
927.9885 | 799.2114 | 276.7351 | 273.342 | 260.4559
928.9885 | 803.3241 | 277.5641 | 273.3024 | 260.984
929.9885 | 801.7027 | 277.7622 | 272.414 | 261.3566
930.9885 | 794.7164 | 278.254 | 272.0014 | 261.5144
931.9885 | 791.5594 | 278.2351 | 272.3119 | 262.0199
932.9885 | 790.5014 | 278.3767 | 272.791 | 262.1309
933.9885 | 791.3616 | 278.3711 | 273.2682 | 262.5192
934.9885 | 789.4918 | 278.5077 | 273.3844 | 262.3238
935.9885 | 796.5203 | 278.6639 | 273.4096 | 262.5707
936.9885 | 790.2163 | 279.1119 | 273.4868 | 262.9047
937.9885 | 788.9467 | 278.9444 | 273.3326 | 263.121
938.9885 | 789.3056 | 279.2407 | 273.3779 | 263.6297
939.9885 | 790.4787 | 279.4147 | 273.9757 | 264.1922
940.9885 | 790.632 | 279.6822 | 273.9711 | 264.2794
941.9885 | 789.5656 | 279.703 | 274.0646 | 264.6123
942.9885 | 795.3825 | 280.1892 | 274.4066 | 265.1746
943.9885 | 794.3345 | 280.1544 | 274.8707 | 266.0759
944.9885 | 796.414 | 280.1165 | 276.0015 | 266.4751
945.9885 | 793.5985 | 280.635 | 277.1161 | 266.0846
946.9885 | 798.3267 | 280.8473 | 277.1637 | 265.9661
947.9885 | 802.6776 | 281.0499 | 277.3785 | 266.0164
948.9885 | 804.5878 | 281.9756 | 278.4337 | 266.7734
949.9885 | 803.3237 | 282.4179 | 278.0712 | 267.4561
950.9885 | 803.731 | 283.2042 | 277.8993 | 267.1535
951.9885 | 799.1464 | 283.5548 | 278.272 | 267.249
952.9885 | 799.005 | 283.8456 | 278.2914 | 267.6261
953.9885 | 800.2022 | 284.0321 | 278.4134 | 268.0011
954.9885 | 800.9134 | 284.1004 | 279.3427 | 268.2525
955.9885 | 794.7431 | 283.9617 | 279.5816 | 268.8624
956.9885 | 792.998 | 283.698 | 279.5837 | 268.7378
957.9885 | 801.2934 | 283.826 | 279.4758 | 268.6955
958.9885 | 801.0701 | 284.1251 | 278.8071 | 268.7816
959.9885 | 802.652 | 284.5517 | 278.51 | 268.1447
960.9885 | 799.9063 | 284.617 | 278.3012 | 268.3118
961.9885 | 797.8236 | 284.5798 | 278.3628 | 267.761
962.9885 | 799.1681 | 285.2245 | 278.5226 | 267.2957
963.9885 | 799.6231 | 285.7179 | 278.6629 | 267.1979
964.9885 | 793.5652 | 286.0068 | 279.2444 | 267.91
965.9885 | 794.8453 | 285.5947 | 280.0895 | 268.7249
966.9885 | 800.5062 | 285.7936 | 280.9195 | 269.3877
967.9885 | 797.3235 | 285.2045 | 281.6007 | 269.7478
968.9885 | 799.2793 | 284.7931 | 281.6652 | 270.185
969.9885 | 798.4524 | 284.4179 | 281.5807 | 270.6857
970.9885 | 798.8358 | 284.5638 | 281.6941 | 271.3632
971.9885 | 800.2592 | 284.7197 | 282.0474 | 271.7678
972.9885 | 798.7787 | 285.097 | 282.9282 | 272.4244
973.9885 | 800.9947 | 285.3134 | 283.6837 | 273.2535
974.9885 | 802.9772 | 285.8961 | 283.8954 | 273.4003
975.9885 | 798.2782 | 285.7453 | 284.3219 | 273.8333
976.9885 | 798.9962 | 285.9001 | 285.0561 | 273.697
977.9885 | 794.1917 | 286.1239 | 285.2916 | 273.6291
978.9885 | 794.8901 | 286.2447 | 285.7391 | 274.0162
979.9885 | 793.5586 | 286.3815 | 286.0777 | 274.6294
980.9885 | 790.2161 | 286.0999 | 286.0576 | 275.3558
981.9885 | 785.4487 | 286.2921 | 286.4041 | 275.5983
982.9885 | 790.7291 | 286.2455 | 286.826 | 275.8246
983.9885 | 794.7903 | 286.3959 | 287.1717 | 276.1667
984.9885 | 789.971 | 286.7087 | 287.0917 | 276.0739
985.9885 | 796.644 | 286.7398 | 287.1662 | 276.1705
986.9885 | 800.0329 | 286.8835 | 287.3093 | 276.2929
987.9885 | 801.2294 | 287.118 | 288.7487 | 276.4697
988.9885 | 803.3698 | 287.4323 | 288.8987 | 276.2768
989.9885 | 806.0017 | 287.7722 | 289.1316 | 276.3593
990.9885 | 808.0249 | 288.1861 | 288.9231 | 276.9596
991.9885 | 807.7993 | 288.9998 | 289.382 | 277.7431
992.9885 | 803.6207 | 289.6424 | 289.8312 | 278.3511
993.9885 | 796.7812 | 290.0268 | 290.0247 | 278.6768
994.9885 | 800.3705 | 290.8817 | 290.0641 | 278.7379
995.9885 | 798.1161 | 291.5665 | 289.9529 | 278.6864
996.9885 | 796.9524 | 291.4498 | 289.8159 | 277.7891
997.9885 | 793.9292 | 291.546 | 289.9238 | 277.5233
998.9885 | 798.4196 | 292.4735 | 289.9092 | 277.4534
999.9885 | 797.7785 | 293.1993 | 289.7339 | 277.1153
1000.9885 | 795.6238 | 293.2016 | 290.08 | 277.6893
1001.9885 | 800.2954 | 293.7534 | 290.85 | 277.9985
1002.9885 | 800.0416 | 293.9897 | 291.2263 | 277.9578
1003.9885 | 799.7064 | 294.6925 | 291.2761 | 278.3278
1004.9885 | 794.9233 | 295.0445 | 291.9278 | 278.5694
1005.9885 | 795.1929 | 295.1338 | 292.6386 | 278.6124
1006.9885 | 792.856 | 295.15 | 292.8655 | 278.851
1007.9885 | 792.5917 | 295.312 | 293.4034 | 279.145
1008.9885 | 789.949 | 295.4349 | 292.5652 | 279.6649
1009.9885 | 789.0111 | 295.3963 | 292.423 | 279.4655
1010.9885 | 784.9992 | 295.3581 | 292.4189 | 280.3056
1011.9885 | 786.9427 | 296.1456 | 292.7028 | 280.3233
1012.9885 | 785.5154 | 295.4867 | 293.0017 | 280.3918
1013.9885 | 789.3249 | 295.5918 | 292.7473 | 280.6349
1014.9885 | 788.2436 | 295.9506 | 292.8402 | 280.495
1015.9885 | 787.9624 | 296.0392 | 292.1594 | 280.9827
1016.9885 | 784.0906 | 296.2231 | 291.2556 | 281.4898
1017.9885 | 784.5513 | 295.956 | 291.8791 | 281.5895
1018.9885 | 784.1964 | 296.301 | 292.2214 | 282.0082
1019.9885 | 782.5672 | 296.4192 | 292.4478 | 281.6691
1020.9885 | 778.2123 | 296.6284 | 292.632 | 281.7401
1021.9885 | 776.2498 | 297.2281 | 292.6649 | 281.6336
1022.9885 | 782.7625 | 296.9019 | 292.2084 | 281.6725
1023.9885 | 784.4018 | 297.5563 | 291.8958 | 281.2201
1024.9885 | 784.7236 | 297.7477 | 292.4059 | 281.273
1025.9885 | 788.8277 | 298.1991 | 293.58 | 281.9817
1026.9885 | 793.7454 | 298.5076 | 293.2704 | 281.3116
1027.9885 | 791.7489 | 298.5027 | 292.6673 | 280.8079
1028.9885 | 789.0108 | 298.8872 | 292.0559 | 280.4264
1029.9885 | 790.9945 | 299.0928 | 292.1515 | 279.581
1030.9885 | 788.8156 | 299.2123 | 292.0156 | 278.9466
1031.9885 | 787.1244 | 299.4176 | 291.1576 | 278.7448
1032.9885 | 787.2476 | 299.3111 | 290.5387 | 278.7249
1033.9885 | 780.6903 | 299.3886 | 291.4812 | 279.3615
1034.9885 | 782.6335 | 299.7528 | 291.8633 | 278.9855
1035.9885 | 785.9218 | 299.7769 | 292.8157 | 279.2734
1036.9885 | 786.7495 | 299.573 | 293.6334 | 280.0276
1037.9885 | 787.7737 | 299.6932 | 294.4923 | 280.2222
1038.9885 | 792.4807 | 299.5832 | 294.4641 | 280.3269
1039.9885 | 798.0038 | 299.5125 | 294.4293 | 280.7795
1040.9885 | 796.7652 | 299.1385 | 294.2224 | 280.953
1041.9885 | 793.7337 | 299.2957 | 293.9516 | 281.1168
1042.9885 | 790.8688 | 299.6971 | 293.551 | 281.1047
1043.9885 | 793.9622 | 299.9909 | 293.9078 | 280.7665
1044.9885 | 796.2022 | 299.5181 | 294.1877 | 281.0077
1045.9885 | 794.1747 | 299.6211 | 294.2415 | 280.7299
1046.9885 | 794.5296 | 299.8959 | 294.1696 | 280.8957
1047.9885 | 793.9765 | 299.5695 | 294.1188 | 281.1907
1048.9885 | 794.5341 | 299.5372 | 294.0163 | 281.3525
1049.9885 | 793.0633 | 299.8205 | 294.2249 | 281.539
1050.9885 | 794.4942 | 300.2846 | 294.7863 | 282.0877
1051.9885 | 791.5771 | 300.7452 | 294.925 | 282.1131
1052.9885 | 790.9133 | 301.6037 | 294.685 | 282.0912
1053.9885 | 787.0643 | 301.9114 | 295.5623 | 282.8058
1054.9885 | 790.4513 | 302.0296 | 295.9571 | 283.4684
1055.9885 | 784.807 | 302.1442 | 295.6693 | 283.7189
1056.9885 | 788.2913 | 302.1578 | 295.727 | 283.6731
1057.9885 | 789.8751 | 302.0764 | 295.8283 | 283.8232
1058.9885 | 789.7826 | 302.7679 | 295.9774 | 284.0695
1059.9885 | 791.4512 | 303.2003 | 296.0232 | 283.4656
1060.9885 | 786.3595 | 303.3368 | 296.1688 | 283.7546
1061.9885 | 783.5462 | 303.433 | 295.5568 | 283.0176
1062.9885 | 783.3304 | 303.9782 | 295.9679 | 282.8987
1063.9885 | 783.2138 | 304.6724 | 296.7589 | 282.8351
1064.9885 | 782.8613 | 305.2309 | 297.7583 | 282.5196
1065.9885 | 784.0057 | 305.5594 | 298.2227 | 283.0139
1066.9885 | 783.363 | 306.0455 | 298.4297 | 284.2155
1067.9885 | 790.4534 | 306.3413 | 299.0996 | 284.4883
1068.9885 | 791.0451 | 305.8449 | 299.3386 | 284.8805
1069.9885 | 788.9327 | 305.7845 | 299.2661 | 285.2473
1070.9885 | 787.5857 | 305.7098 | 299.4933 | 285.2527
1071.9885 | 789.9599 | 306.1641 | 299.7488 | 285.3449
1072.9885 | 789.9188 | 306.1055 | 299.9178 | 285.346
1073.9885 | 784.7006 | 306.1828 | 300.0682 | 285.4361
1074.9885 | 783.0567 | 306.2236 | 299.946 | 285.0307
1075.9885 | 775.4096 | 306.5042 | 299.8865 | 284.3722
1076.9885 | 770.9009 | 306.481 | 299.8133 | 284.1665
1077.9885 | 769.7317 | 306.4813 | 299.8439 | 284.8597
1078.9885 | 773.1715 | 306.2503 | 299.2774 | 284.7772
1079.9885 | 778.255 | 306.1303 | 300.0847 | 285.3527
1080.9885 | 779.8006 | 306.1261 | 300.2126 | 285.9257
1081.9885 | 778.9199 | 306.3518 | 300.8882 | 286.2237
1082.9885 | 775.4152 | 306.5194 | 301.1294 | 286.3571
1083.9885 | 778.9641 | 307.1499 | 300.8404 | 285.8125
1084.9885 | 786.5369 | 307.1008 | 300.9057 | 286.1144
1085.9885 | 790.7904 | 307.4013 | 301.6479 | 286.0514
1086.9885 | 793.7118 | 307.4175 | 301.873 | 286.1599
1087.9885 | 794.2662 | 307.6198 | 301.647 | 285.9157
1088.9885 | 799.7704 | 307.9226 | 302.5334 | 285.9599
1089.9885 | 798.0881 | 308.3613 | 302.8744 | 285.4469
1090.9885 | 796.5721 | 308.8322 | 303.2777 | 286.5067
1091.9885 | 796.5533 | 308.8216 | 303.6709 | 286.4773
1092.9885 | 791.5208 | 308.9016 | 302.9376 | 286.6508
1093.9885 | 791.404 | 308.7331 | 302.7516 | 286.9474
1094.9885 | 788.6645 | 309.0815 | 303.0337 | 287.0462
1095.9885 | 786.3165 | 309.4516 | 303.1967 | 288.5363
1096.9885 | 784.1554 | 309.3462 | 303.0328 | 288.494
1097.9885 | 784.0634 | 309.4533 | 303.1527 | 288.7262
1098.9885 | 787.5726 | 309.3071 | 303.1195 | 288.6945
1099.9885 | 785.973 | 309.4592 | 303.2356 | 289.0562
1100.9885 | 787.9867 | 309.8028 | 303.1579 | 289.0083
1101.9885 | 790.7353 | 309.6362 | 303.2739 | 288.4772
1102.9885 | 790.9434 | 309.6339 | 303.229 | 288.8263
1103.9885 | 782.8119 | 309.6797 | 303.118 | 288.6637
1104.9885 | 788.7604 | 309.526 | 303.4647 | 288.8454
1105.9885 | 788.6226 | 308.9744 | 303.3864 | 288.9037
1106.9885 | 788.8542 | 308.8509 | 303.5681 | 289.0911
1107.9885 | 789.9598 | 308.8183 | 303.3671 | 288.5477
1108.9885 | 787.0056 | 308.9524 | 303.1233 | 288.4097
1109.9885 | 794.7859 | 309.0114 | 303.9636 | 288.624
1110.9885 | 795.5022 | 308.5869 | 303.8342 | 288.2658
1111.9885 | 797.2306 | 308.7178 | 303.4364 | 288.2334
1112.9885 | 794.9034 | 309.4301 | 303.3849 | 288.122
1113.9885 | 790.4517 | 310.1703 | 302.8296 | 288.6212
1114.9885 | 796.3993 | 310.6113 | 302.6679 | 288.7792
1115.9885 | 792.4364 | 310.7409 | 302.4324 | 288.5552
1116.9885 | 796.1597 | 310.8186 | 302.4952 | 288.9454
1117.9885 | 794.8589 | 310.4696 | 302.516 | 289.0688
1118.9885 | 794.513 | 310.0483 | 302.6608 | 290.8459
1119.9885 | 790.7316 | 310.3025 | 303.0618 | 290.7876
1120.9885 | 794.215 | 310.8275 | 303.8989 | 291.4557
1121.9885 | 792.1515 | 310.5161 | 304.0814 | 291.3992
1122.9885 | 787.1052 | 310.4151 | 303.8607 | 291.7793
1123.9885 | 790.6316 | 310.5108 | 303.7714 | 291.9734
1124.9885 | 789.5872 | 310.9009 | 303.633 | 291.8249
1125.9885 | 791.6686 | 310.834 | 303.4528 | 291.2975
1126.9885 | 795.8214 | 310.7205 | 302.9983 | 291.0359
1127.9885 | 794.3934 | 310.9925 | 303.0483 | 291.4007
1128.9885 | 792.4837 | 310.8387 | 303.2078 | 291.6101
1129.9885 | 792.5437 | 311.2628 | 303.295 | 291.5077
1130.9885 | 794.6452 | 311.1354 | 303.7953 | 291.3957
1131.9885 | 791.4993 | 310.9414 | 303.7325 | 291.3052
1132.9885 | 794.137 | 310.4539 | 303.6723 | 291.0685
1133.9885 | 794.9066 | 310.7235 | 304.1046 | 291.2184
1134.9885 | 791.3378 | 310.5988 | 303.9946 | 291.3123
1135.9885 | 789.2651 | 310.5102 | 304.0251 | 291.1427
1136.9885 | 794.5394 | 310.5589 | 304.2689 | 291.0648
1137.9885 | 789.7179 | 310.4641 | 303.6336 | 291.0628
1138.9885 | 793.9452 | 310.748 | 303.6229 | 290.7191
1139.9885 | 794.0453 | 310.8573 | 303.6522 | 291.3166
1140.9885 | 790.3109 | 310.6381 | 303.1288 | 291.5936
1141.9885 | 787.3694 | 310.6526 | 303.0073 | 291.6495
1142.9885 | 788.7913 | 310.9421 | 303.7461 | 292.0661
1143.9885 | 792.1079 | 311.4024 | 303.0873 | 292.9625
1144.9885 | 795.4307 | 310.8992 | 303.3224 | 292.7752
1145.9885 | 792.9994 | 310.8311 | 303.5413 | 292.5492
1146.9885 | 794.3527 | 310.5719 | 303.662 | 292.427
1147.9885 | 794.388 | 310.2482 | 303.821 | 292.1085
1148.9885 | 794.8023 | 310.3503 | 303.9111 | 292.0248
1149.9885 | 794.4087 | 310.1498 | 303.6314 | 291.4219
1150.9885 | 790.4143 | 310.1235 | 304.2814 | 291.0568
1151.9885 | 793.1281 | 310.1272 | 304.5564 | 291.19
1152.9885 | 796.7641 | 310.2478 | 304.6278 | 291.03
1153.9885 | 792.814 | 310.6066 | 304.8131 | 292.025
1154.9885 | 794.7866 | 310.975 | 305.5566 | 291.5469
1155.9885 | 790.2434 | 310.8652 | 305.7148 | 291.5617
1156.9885 | 792.8001 | 310.9992 | 305.2641 | 292.0232
1157.9885 | 789.5143 | 310.8411 | 304.4964 | 292.0424
1158.9885 | 791.1655 | 311.3453 | 303.712 | 291.729
1159.9885 | 790.447 | 311.4246 | 303.7577 | 291.6618
1160.9885 | 787.8786 | 311.4111 | 304.0106 | 291.0928
1161.9885 | 787.6507 | 311.1653 | 304.541 | 290.8875
1162.9885 | 787.172 | 310.8115 | 304.3662 | 291.1101
1163.9885 | 790.4828 | 310.5948 | 304.513 | 291.6106
1164.9885 | 792.9515 | 311.0489 | 304.3557 | 291.0816
1165.9885 | 795.2394 | 311.3799 | 303.9376 | 291.0792
1166.9885 | 796.4093 | 311.2101 | 303.8607 | 291.0871
1167.9885 | 793.4462 | 311.1692 | 304.1142 | 290.9613
1168.9885 | 789.4999 | 311.9806 | 303.196 | 292
1169.9885 | 782.6032 | 312.0064 | 303.1477 | 291.7529
1170.9885 | 783.1524 | 312.0713 | 303.3395 | 292.6001
1171.9885 | 784.1633 | 312.1897 | 303.7696 | 293.2277
1172.9885 | 783.2947 | 312.1562 | 304.8218 | 292.6495
1173.9885 | 787.2871 | 312.0461 | 305.1871 | 292.2141
1174.9885 | 787.5638 | 312.2649 | 305.2901 | 292.1145
1175.9885 | 788.9064 | 312.1634 | 304.8483 | 292.1178
1176.9885 | 785.3038 | 311.9976 | 304.7527 | 292.0822
1177.9885 | 781.5396 | 312.281 | 305.0132 | 291.8622
1178.9885 | 780.9266 | 312.1022 | 305.2132 | 291.9515
1179.9885 | 781.0888 | 313.01 | 305.5868 | 291.8179
1180.9885 | 783.7115 | 312.8935 | 305.6879 | 292.1693
1181.9885 | 784.4166 | 312.7281 | 305.4738 | 292.412
1182.9885 | 781.6369 | 312.4813 | 305.3404 | 292.35
1183.9885 | 782.5597 | 312.3319 | 305.0704 | 292.3669
1184.9885 | 782.0015 | 312.1825 | 305.3639 | 292.3663
1185.9885 | 788.2049 | 312.1598 | 305.6394 | 292.1764
1186.9885 | 787.0768 | 312.1155 | 305.8307 | 292.8452
1187.9885 | 791.5965 | 312.4905 | 305.7501 | 293.1058
1188.9885 | 792.7199 | 312.5309 | 305.7787 | 292.7113
1189.9885 | 790.3557 | 312.6146 | 305.9279 | 292.5829
1190.9885 | 790.2073 | 312.7478 | 305.8802 | 292.6
1191.9885 | 789 | 312.6672 | 305.9542 | 292.8258
1192.9885 | 793.2772 | 312.7673 | 306.0012 | 292.7255
1193.9885 | 791.3306 | 312.94 | 306.1705 | 293.1946
1194.9885 | 793.7967 | 312.7854 | 305.7925 | 292.7605
1195.9885 | 790.5007 | 312.9367 | 305.9772 | 292.7481
1196.9885 | 788.3232 | 313.1158 | 305.8964 | 292.626
1197.9885 | 787.5689 | 313.4948 | 305.7605 | 292.2288
1198.9885 | 782.8204 | 313.2197 | 305.8083 | 292.0314
1199.9885 | 780.6751 | 313.4935 | 306.133 | 292.0208
1200.9885 | 779.4022 | 313.0503 | 305.9063 | 291.771
1201.9885 | 782.7323 | 312.9582 | 305.5856 | 291.7839
1202.9885 | 782.4325 | 312.7441 | 305.6106 | 292.3767
1203.9885 | 781.5136 | 312.7398 | 306.2841 | 292.7797
1204.9885 | 777.5609 | 313.5679 | 306.3147 | 293.1775
1205.9885 | 780.0726 | 313.2757 | 306.4251 | 292.9578
1206.9885 | 777.5486 | 313.2679 | 306.3769 | 292.9257
1207.9885 | 774.1079 | 313.2394 | 306.8846 | 292.9946
1208.9885 | 773.6076 | 312.8245 | 307.2701 | 292.6297
1209.9885 | 775.2398 | 312.6595 | 307.5404 | 292.2263
1210.9885 | 774.2722 | 312.8613 | 307.7707 | 292.6957
1211.9885 | 780.6072 | 313.1814 | 308.1385 | 292.8783
1212.9885 | 785.031 | 312.6674 | 307.7778 | 292.7497
1213.9885 | 786.4669 | 312.6158 | 307.2818 | 292.7706
1214.9885 | 787.7934 | 312.8852 | 306.9262 | 293.0862
1215.9885 | 787.6029 | 312.7761 | 307.0651 | 293.1136
1216.9885 | 782.3065 | 312.963 | 307.8311 | 293.6971
1217.9885 | 779.9224 | 312.7846 | 307.7923 | 293.7184
1218.9885 | 776.0131 | 312.9657 | 307.854 | 294.0659
1219.9885 | 770.7738 | 312.8814 | 308.057 | 294.0767
1220.9885 | 770.2566 | 313.0712 | 308.4944 | 294.2838
1221.9885 | 772.4873 | 313.5438 | 308.6056 | 294.2069
1222.9885 | 774.003 | 313.6662 | 309.2372 | 293.7524
1223.9885 | 777.2509 | 313.9089 | 308.8651 | 294.05
1224.9885 | 777.6227 | 313.7878 | 308.4805 | 293.9378
1225.9885 | 780.7984 | 313.3978 | 307.7981 | 293.6241
1226.9885 | 786.5697 | 313.4094 | 307.2344 | 293.3215
1227.9885 | 788.5903 | 313.1978 | 306.578 | 293.3426
1228.9885 | 779.333 | 313.0132 | 306.6686 | 293.3586
1229.9885 | 787.1735 | 313.1395 | 306.61 | 293.8506
1230.9885 | 788.6929 | 312.7931 | 306.449 | 293.7223
1231.9885 | 781.5404 | 312.7833 | 306.5496 | 293.4262
1232.9885 | 778.9339 | 312.7481 | 307.2487 | 293.4615
1233.9885 | 781.5844 | 312.6662 | 307.2211 | 293.4031
1234.9885 | 794.7932 | 312.8746 | 307.8655 | 293.8078
1235.9885 | 796.0737 | 313.2553 | 307.3267 | 293.3495
1236.9885 | 789.2951 | 313.295 | 306.7585 | 292.9567
1237.9885 | 784.3375 | 313.348 | 306.4489 | 292.477
1238.9885 | 781.7271 | 313.3967 | 306.5243 | 292.2323
1239.9885 | 783.3881 | 313.7084 | 306.0294 | 292.0756
1240.9885 | 790.1209 | 313.8157 | 306.1652 | 292.3855
1241.9885 | 792.313 | 313.5537 | 306.155 | 292.1919
1242.9885 | 799.1754 | 313.6504 | 306.3859 | 292.5222
1243.9885 | 793.4466 | 314.2451 | 306.721 | 292.651
1244.9885 | 797.2677 | 314.094 | 307.0569 | 293.148
1245.9885 | 788.0173 | 314.9073 | 307.1749 | 293.3291
1246.9885 | 781.4456 | 314.9009 | 307.3796 | 293.7185
1247.9885 | 782.6581 | 315.2457 | 307.8116 | 294.3011
1248.9885 | 785.8893 | 315.595 | 307.6969 | 294.0429
1249.9885 | 786.2495 | 315.4027 | 308.4377 | 294.4239
1250.9885 | 776.7319 | 315.8427 | 308.362 | 294.5469
1251.9885 | 775.1722 | 315.4396 | 308.3606 | 294.3413
1252.9885 | 772.632 | 315.2695 | 308.5555 | 294.2043
1253.9885 | 765.9322 | 315.3365 | 308.2408 | 294.3427
1254.9885 | 758.9429 | 315.0263 | 308.3135 | 294.342
1255.9885 | 767.5104 | 315.1114 | 308.3969 | 294.2821
1256.9885 | 765.3206 | 315.2645 | 308.4847 | 294.8494
1257.9885 | 772.6225 | 315.472 | 308.6675 | 295.3202
1258.9885 | 776.6298 | 315.7104 | 308.7943 | 295.7388
1259.9885 | 786.776 | 315.8627 | 308.728 | 295.9599
1260.9885 | 778.1535 | 316.2614 | 309.3477 | 296.2512
1261.9885 | 770.7245 | 316.4363 | 309.2735 | 296.0799
1262.9885 | 769.1041 | 316.1491 | 308.7172 | 296.07
1263.9885 | 771.5289 | 316.3525 | 308.3022 | 295.774
1264.9885 | 772.9257 | 316.1276 | 307.856 | 295.7746
1265.9885 | 773.3462 | 315.6166 | 307.4941 | 295.8472
1266.9885 | 772.1777 | 315.6249 | 307.0404 | 295.8589
1267.9885 | 772.1933 | 315.3985 | 306.7793 | 295.5642
1268.9885 | 775.8802 | 314.9464 | 306.8246 | 295.9126
1269.9885 | 769.777 | 314.4552 | 306.5705 | 295.9358
1270.9885 | 773.3864 | 314.7224 | 306.5432 | 295.9124
1271.9885 | 772.0628 | 314.7557 | 307.0547 | 295.563
1272.9885 | 767.601 | 314.6279 | 307.2849 | 295.9104
1273.9885 | 766.2949 | 315.3637 | 307.3345 | 295.7561
1274.9885 | 759.9462 | 315.2835 | 307.5062 | 295.9777
1275.9885 | 754.9078 | 315.4041 | 307.3273 | 296.0326
1276.9885 | 758.8463 | 315.616 | 307.0969 | 296.1589
1277.9885 | 763.2963 | 315.4035 | 306.8793 | 296.2665
1278.9885 | 770.2445 | 315.8226 | 307.2803 | 296.4535
1279.9885 | 768.6461 | 315.546 | 307.2391 | 296.6391
1280.9885 | 761.1063 | 315.4809 | 307.3297 | 296.6858
1281.9885 | 762.9417 | 315.1173 | 307.5616 | 296.9162
1282.9885 | 764.9278 | 315.0185 | 307.7575 | 296.2963
1283.9885 | 768.5585 | 315.0623 | 307.939 | 296.3352
1284.9885 | 771.9986 | 315.5463 | 307.4959 | 296.6842
1285.9885 | 767.0394 | 315.3163 | 307.9328 | 296.9979
1286.9885 | 769.9633 | 314.9872 | 307.8186 | 296.7738
1287.9885 | 771.291 | 314.8459 | 307.8812 | 296.6886
1288.9885 | 773.7247 | 314.9315 | 307.5175 | 296.6833
1289.9885 | 770.3456 | 315.06 | 307.5239 | 296.4656
1290.9885 | 773.6074 | 315.0901 | 307.2036 | 296.3284
1291.9885 | 777.7269 | 315.1205 | 306.7038 | 296.8155
1292.9885 | 777.3352 | 315.501 | 306.7521 | 296.4415
1293.9885 | 776.5142 | 315.6548 | 307.445 | 296.5538
1294.9885 | 778.4553 | 315.3196 | 308.2482 | 296.7106
1295.9885 | 779.4825 | 315.2405 | 308.4028 | 296.842
1296.9885 | 778.6375 | 315.1044 | 308.8988 | 296.3285
1297.9885 | 783.7352 | 315.3212 | 308.5942 | 296.93
1298.9885 | 775.4662 | 315.5397 | 308.2836 | 297.161
1299.9885 | 771.4536 | 315.3198 | 308.3835 | 296.7745
1300.9885 | 771.6214 | 315.1092 | 308.358 | 296.4154
1301.9885 | 770.0888 | 315.1867 | 308.2561 | 296.5437
1303.0042 | 771.1149 | 315.055 | 308.5772 | 296.9975
1303.9885 | 772.1434 | 315.5738 | 308.7059 | 296.9613
1304.9885 | 773.3504 | 315.6879 | 308.8804 | 297.1364
1305.9885 | 778.7557 | 315.4139 | 309.1344 | 296.8602
1306.9885 | 767.7488 | 315.1261 | 309.0322 | 296.6954
1307.9885 | 769.5331 | 315.7141 | 309.9042 | 297.3417
1308.9885 | 773.301 | 315.6374 | 309.2069 | 297.6581
1309.9885 | 773.3159 | 315.9377 | 309.2877 | 297.558
1310.9885 | 768.2609 | 315.9988 | 309.5661 | 297.772
1311.9885 | 775.1144 | 316.1743 | 309.1482 | 297.662
1312.9885 | 775.2691 | 316.3015 | 308.7568 | 297.463
1313.9885 | 782.106 | 316.3121 | 308.746 | 297.2051
1314.9885 | 782.421 | 316.5678 | 308.2802 | 297.3327
1315.9885 | 782.9029 | 316.5632 | 307.3816 | 297.3071
1316.9885 | 783.3344 | 316.739 | 307.0315 | 296.8654
1317.9885 | 779.371 | 317.3131 | 306.7894 | 296.8995
1318.9885 | 777.127 | 317.7399 | 307.1933 | 297.5598
1319.9885 | 777.6275 | 317.8089 | 307.2404 | 297.5166
1320.9885 | 776.5983 | 317.5117 | 307.2573 | 297.3742
1321.9885 | 770.1986 | 317.597 | 307.3812 | 297.4732
1322.9885 | 771.5401 | 317.7529 | 307.7874 | 297.6088
1323.9885 | 771.9811 | 317.7715 | 308.036 | 297.2078
1324.9885 | 763.2414 | 317.6917 | 308.3479 | 297.2597
1325.9885 | 766.0227 | 318.1111 | 308.4912 | 297.3671
1326.9885 | 757.6115 | 318.2146 | 308.2266 | 297.7771
1327.9885 | 766.0912 | 318.3653 | 308.709 | 297.8688
1328.9885 | 761.5078 | 318.465 | 309.3302 | 298.0755
1329.9885 | 760.8049 | 318.7297 | 309.2105 | 298.0869
1330.9885 | 758.4201 | 318.7583 | 309.2828 | 298.1127
1331.9885 | 763.7863 | 319.5065 | 309.6398 | 297.6698
1332.9885 | 756.365 | 319.4749 | 309.8802 | 297.5502
1333.9885 | 763.0945 | 319.7591 | 309.535 | 297.2977
1334.9885 | 762.1936 | 319.5896 | 310.0568 | 297.0215
1335.9885 | 757.9946 | 319.326 | 310.0258 | 296.5504
1336.9885 | 763.6876 | 319.2876 | 309.8101 | 296.6136
1337.9885 | 766.5516 | 318.9888 | 310.1636 | 297.2238
1338.9885 | 763.5267 | 319.4314 | 310.0842 | 297.6705
1339.9885 | 761.4218 | 319.8511 | 310.3198 | 297.8534
1340.9885 | 760.8298 | 320.0225 | 310.7354 | 297.7419
1341.9885 | 761.0808 | 319.8014 | 310.935 | 298.7898
1342.9885 | 762.1794 | 319.6064 | 310.9946 | 298.7725
1343.9885 | 762.5194 | 319.7437 | 310.8009 | 298.5577
1344.9885 | 760.0673 | 319.6811 | 310.657 | 298.1347
1345.9885 | 761.5317 | 319.8157 | 311.4359 | 299.1388
1346.9885 | 772.3882 | 319.7882 | 311.2123 | 299.3919
1347.9885 | 771.5129 | 320.2429 | 311.2307 | 299.7863
1348.9885 | 771.6188 | 320.0738 | 311.1243 | 299.4692
1349.9885 | 778.9703 | 319.973 | 310.9162 | 299.2212
1350.9885 | 774.5688 | 320.0125 | 310.3273 | 298.7236
1351.9885 | 782.6585 | 319.9646 | 310.3627 | 298.549
1352.9885 | 775.7807 | 320.1009 | 310.173 | 298.8125
1353.9885 | 777.1752 | 319.8307 | 310.1517 | 299.0906
1354.9885 | 775.6221 | 320.1462 | 310.3315 | 298.6514
1355.9885 | 775.9249 | 320.0579 | 310.4746 | 298.6551
1356.9885 | 772.8124 | 320.3234 | 310.6499 | 299.0757
1357.9885 | 774.7483 | 320.4686 | 310.9392 | 299.0678
1358.9885 | 774.8716 | 320.3233 | 310.6328 | 299.0248
1359.9885 | 771.7624 | 320.462 | 310.6313 | 298.814
1360.9885 | 773.043 | 320.4282 | 310.7416 | 298.8736
1361.9885 | 768.4217 | 320.762 | 310.1466 | 298.8383
1362.9885 | 764.237 | 320.5369 | 309.4052 | 298.4731
1363.9885 | 768.3595 | 320.2413 | 309.3232 | 298.4994
1364.9885 | 773.3311 | 320.3496 | 308.9399 | 298.2525
1365.9885 | 777.8078 | 320.3711 | 309.0863 | 297.8773
1366.9885 | 775.6515 | 320.4429 | 309.2652 | 297.7631
1367.9885 | 776.5386 | 320.6668 | 309.458 | 297.4447
1368.9885 | 772.0518 | 320.862 | 310.2347 | 297.3686
1369.9885 | 774.0447 | 320.2781 | 310.9115 | 297.5122
1370.9885 | 779.376 | 320.4494 | 311.3054 | 297.9853
1371.9885 | 777.9347 | 320.0847 | 311.0733 | 298.1699
1372.9885 | 774.3224 | 319.7328 | 310.9942 | 298.0946
1373.9885 | 771.3681 | 319.8916 | 311.4984 | 298.756
1374.9885 | 780.5347 | 319.6387 | 311.2181 | 298.4591
1375.9885 | 775.1862 | 319.7144 | 311.2084 | 298.9728
1376.9885 | 777.0086 | 319.6747 | 310.7306 | 299.5392
1377.9885 | 776.2864 | 320.0183 | 311.026 | 299.4454
1378.9885 | 777.7997 | 320.0737 | 311.4374 | 299.5999
1379.9885 | 767.0439 | 320.3492 | 312.0877 | 299.3808
1380.9885 | 761.1531 | 320.3287 | 312.2375 | 299.0352
1381.9885 | 763.4727 | 320.3235 | 312.2328 | 299.0175
1382.9885 | 766.2958 | 319.9674 | 311.7087 | 298.831
1383.9885 | 762.0035 | 319.8553 | 310.9418 | 298.4393
1384.9885 | 761.1906 | 319.5374 | 311.2116 | 298.1632
1385.9885 | 766.4306 | 319.8495 | 310.6615 | 297.802
1386.9885 | 765.0213 | 319.4421 | 310.4965 | 297.6299
1387.9885 | 770.5221 | 319.3571 | 309.7763 | 297.6385
1388.9885 | 776.5036 | 319.9685 | 309.6022 | 297.9238
1389.9885 | 776.3113 | 320.5243 | 309.3062 | 297.9289
1390.9885 | 779.4363 | 320.2013 | 308.7157 | 298.7234
1391.9885 | 778.1003 | 320.3884 | 308.6673 | 298.9708
1392.9885 | 771.762 | 319.989 | 308.7624 | 299.438
1393.9885 | 773.0882 | 320.028 | 309.0716 | 299.5271
1394.9885 | 771.1379 | 320.01 | 309.4854 | 299.2083
1395.9885 | 769.7219 | 319.7922 | 309.7193 | 299.2048
1396.9885 | 773.6017 | 319.5525 | 309.7145 | 299.0371
1397.9885 | 772.9226 | 319.3701 | 310.1162 | 298.909
1398.9885 | 770.6805 | 319.1206 | 310.2229 | 299.0092
1399.9885 | 770.3387 | 318.7188 | 310.3319 | 299.1172
1400.9885 | 766.06 | 318.3768 | 310.4337 | 298.6638
1401.9885 | 763.6196 | 318.2618 | 310.3614 | 298.5799
1402.9885 | 757.8446 | 318.2298 | 310.3435 | 298.3104
1403.9885 | 761.9666 | 318.5567 | 310.5396 | 298.2365
1404.9885 | 764.5817 | 318.5807 | 310.6568 | 298.2289
1405.9885 | 758.9464 | 318.6129 | 310.9346 | 298.285
1406.9885 | 759.9939 | 318.4555 | 311.2875 | 298.8492
1407.9885 | 757.833 | 318.3123 | 311.0293 | 298.9909
1408.9885 | 754.4596 | 318.7203 | 311.1379 | 299.5401
1409.9885 | 749.8473 | 318.3134 | 310.7783 | 299.3737
1410.9885 | 754.7141 | 318.0199 | 310.681 | 299.2096
1411.9885 | 756.2377 | 317.9523 | 310.378 | 299.1718
1412.9885 | 764.0889 | 317.9299 | 310.6065 | 299.6148
1413.9885 | 764.8625 | 318.3572 | 310.7295 | 299.5857
1414.9885 | 769.8441 | 319.1348 | 311.8623 | 300.2872
1415.9885 | 782.8108 | 320.1179 | 312.0106 | 301.9162
1416.9885 | 778.3743 | 320.8953 | 312.8868 | 302.6088
1417.9885 | 782.5018 | 320.9103 | 313.3295 | 303.3082
1418.9885 | 786.5446 | 321.3659 | 313.7714 | 303.6993
1419.9885 | 779.0412 | 321.7991 | 313.9694 | 303.6888
1421.0042 | 779.9061 | 322.111 | 314.609 | 303.9286
1421.9885 | 781.9738 | 322.8626 | 315.3415 | 304.1628
1422.9885 | 785.2803 | 322.8599 | 315.8373 | 304.6366
1423.9885 | 784.8558 | 322.933 | 316.3475 | 305.1962
1424.9885 | 784.4036 | 323.1274 | 316.7504 | 305.5175
1425.9885 | 780.1589 | 323.3639 | 317.2367 | 306.1406
1426.9885 | 781.3536 | 323.413 | 317.5807 | 306.9356
1427.9885 | 780.8877 | 324.3994 | 317.9812 | 307.6337
1428.9885 | 780.4449 | 324.7395 | 318.4935 | 308.1968
1429.9885 | 778.2863 | 325.4901 | 319.0567 | 308.9692
1430.9885 | 774.4778 | 325.7477 | 319.3932 | 309.4452
1431.9885 | 773.183 | 325.9435 | 319.4197 | 309.9903
1432.9885 | 773.1014 | 325.8047 | 319.6498 | 310.7384
1433.9885 | 779.0427 | 326.1025 | 320.1193 | 310.8471
1434.9885 | 772.6008 | 326.9151 | 320.5289 | 310.6947
1435.9885 | 770.6163 | 327.2115 | 320.7113 | 311.1473
1436.9885 | 775.1741 | 327.5583 | 321.2782 | 311.1822
1437.9885 | 779.0356 | 328.04 | 322.0343 | 311.7559
1438.9885 | 773.386 | 328.2667 | 322.5384 | 312.1055
1439.9885 | 768.3085 | 328.3504 | 323.7933 | 312.6193
1440.9885 | 766.5063 | 328.1384 | 323.8952 | 313.0466
1441.9885 | 766.7089 | 328.2477 | 323.6626 | 313.2292
1442.9885 | 764.1272 | 328.18 | 323.4031 | 313.2309
1443.9885 | 771.681 | 328.4392 | 323.0788 | 312.975
1444.9885 | 776.3421 | 328.3323 | 323.004 | 312.5715
1445.9885 | 771.9437 | 328.2902 | 322.9909 | 312.1592
1446.9885 | 782.2627 | 328.4525 | 323.165 | 311.949
1447.9885 | 781.1065 | 328.5295 | 323.4705 | 311.9874
1448.9885 | 788.3896 | 328.7977 | 323.5239 | 311.665
1449.9885 | 784.7875 | 329.055 | 324.2594 | 311.5094
1450.9885 | 779.7355 | 329.3547 | 324.7969 | 311.4891
1451.9885 | 781.8267 | 330.0636 | 325.4301 | 312.2065
1452.9885 | 788.4788 | 329.6551 | 325.4449 | 312.3218
1453.9885 | 792.9558 | 329.7044 | 325.0807 | 312.3893
1454.9885 | 796.437 | 329.1595 | 324.3464 | 312.0923
1455.9885 | 796.2071 | 329.8483 | 324.0937 | 311.6692
1456.9885 | 797.5362 | 330.2971 | 323.5859 | 311.2619
1457.9885 | 799.1984 | 330.3658 | 323.4157 | 311.2689
1458.9885 | 796.4154 | 331.0168 | 323.9167 | 311.047
1459.9885 | 797.9382 | 331.5293 | 324.0962 | 310.6031
1460.9885 | 794.4945 | 331.9351 | 324.4639 | 310.3757
1461.9885 | 794.1691 | 332.1563 | 325.0848 | 310.6185
1462.9885 | 798.4794 | 332.3264 | 325.0067 | 310.7083
1463.9885 | 798.6488 | 332.5028 | 325.2793 | 311.0337
1464.9885 | 795.5034 | 332.8761 | 325.7676 | 311.6935
1465.9885 | 797.1509 | 333.1086 | 325.9672 | 312.1222
1466.9885 | 793.1046 | 333.4799 | 325.8135 | 312.1207
1467.9885 | 793.1243 | 333.6404 | 326.0764 | 312.348
1468.9885 | 789.1036 | 333.9002 | 326.3911 | 312.5414
1469.9885 | 787.6847 | 333.7661 | 326.1832 | 312.9358
1470.9885 | 783.6142 | 334.3182 | 326.1949 | 312.9422
1471.9885 | 785.5278 | 334.6975 | 326.6078 | 313.0509
1472.9885 | 785.4216 | 334.8346 | 326.9337 | 313.2605
1473.9885 | 787.0407 | 335.2656 | 327.0496 | 313.8424
1474.9885 | 784.3665 | 335.5359 | 327.0392 | 314.3855
1475.9885 | 784.7118 | 335.5702 | 327.0165 | 314.3462
1476.9885 | 786.9281 | 335.3682 | 326.503 | 313.9021
1477.9885 | 790.1278 | 335.5302 | 326.5814 | 313.7662
1478.9885 | 791.7771 | 335.6601 | 326.6432 | 313.6054
1479.9885 | 788.8552 | 335.5099 | 325.9885 | 313.093
1480.9885 | 790.9855 | 335.3907 | 325.9191 | 312.7689
1481.9885 | 789.8911 | 335.7629 | 326.6774 | 314.0589
1482.9885 | 788.3245 | 336.2167 | 326.9727 | 314.0712
1483.9885 | 788.1494 | 336.1695 | 327.9543 | 314.5128
1484.9885 | 784.3192 | 336.634 | 328.3399 | 314.5146
1485.9885 | 783.1605 | 336.7279 | 328.3797 | 315.1188
1486.9885 | 780.2473 | 337.0903 | 328.4044 | 315.3906
1487.9885 | 781.6642 | 337.3079 | 328.4139 | 315.469
1488.9885 | 783.9902 | 337.8772 | 329.4805 | 315.7278
1489.9885 | 783.2448 | 338.0638 | 329.7244 | 315.9849
1490.9885 | 778.2732 | 338.0735 | 329.7362 | 316.3541
1491.9885 | 773.3736 | 338.5149 | 330.0714 | 316.9235
1492.9885 | 773.7984 | 338.8191 | 330.1204 | 316.8377
1493.9885 | 774.1392 | 338.8681 | 329.9319 | 317.2366
1494.9885 | 779.1726 | 338.6427 | 329.497 | 317.872
1495.9885 | 779.052 | 339.1306 | 329.1193 | 318.1012
1496.9885 | 780.4188 | 339.2834 | 328.9152 | 318.112
1497.9885 | 788.0281 | 339.6002 | 328.4978 | 317.7121
1498.9885 | 791.3327 | 340.1266 | 328.5954 | 317.3961
1499.9885 | 790.0078 | 341.1691 | 329.7369 | 317.7816
1500.9885 | 782.9587 | 341.8188 | 329.5685 | 317.4564
1501.9885 | 786.5681 | 342.2976 | 329.2582 | 317.0256
1502.9885 | 789.1816 | 342.0682 | 329.4378 | 316.9756
1503.9885 | 787.1204 | 341.9984 | 329.3101 | 316.7467
1504.9885 | 790.2087 | 341.5059 | 329.1157 | 316.795
1505.9885 | 791.3369 | 341.5141 | 329.5313 | 316.2896
1506.9885 | 790.1651 | 340.7858 | 329.8376 | 316.3772
1507.9885 | 795.6493 | 340.5591 | 329.8415 | 316.4185
1508.9885 | 794.5645 | 340.7051 | 329.975 | 316.0798
1509.9885 | 789.9375 | 341.8166 | 330.4002 | 316.2066
1510.9885 | 788.3806 | 341.9242 | 330.8039 | 316.5458
1511.9885 | 787.7919 | 342.3372 | 330.3862 | 316.737
1512.9885 | 785.6769 | 342.4548 | 331.0029 | 316.857
1513.9885 | 789.1998 | 342.3565 | 331.0923 | 316.7945
1514.9885 | 788.7904 | 342.4578 | 332.2909 | 317.2385
1515.9885 | 781.9195 | 342.6498 | 332.4918 | 317.458
1516.9885 | 788.2997 | 343.5094 | 333.3017 | 317.7105
1517.9885 | 788.1273 | 343.5311 | 333.1411 | 317.8482
1518.9885 | 781.3246 | 343.7892 | 332.9325 | 318.42
1519.9885 | 775.3578 | 343.3628 | 333.4602 | 318.7246
1520.9885 | 769.8439 | 342.9729 | 333.2621 | 319.3532
1521.9885 | 771.9778 | 342.7989 | 333.7101 | 319.4219
1522.9885 | 775.7597 | 342.8136 | 333.6315 | 319.3144
1523.9885 | 772.8776 | 343.559 | 333.7832 | 319.747
1524.9885 | 773.6463 | 343.75 | 333.2833 | 320.1618
1525.9885 | 767.671 | 344.1049 | 332.8255 | 320.1987
1526.9885 | 767.4824 | 343.9931 | 332.3207 | 320.3273
1527.9885 | 766.6526 | 344.2137 | 331.71 | 319.9553
1528.9885 | 767.6718 | 343.9424 | 331.5514 | 319.744
1529.9885 | 766.8943 | 344.2253 | 331.2901 | 319.6288
1530.9885 | 769.1919 | 344.2722 | 331.1566 | 319.6418
1531.9885 | 764.5646 | 344.1535 | 331.0064 | 319.7444
1532.9885 | 761.586 | 344.1944 | 331.1044 | 319.8292
1533.9885 | 760.5764 | 344.007 | 331.3988 | 320.0021
1534.9885 | 761.0546 | 344.0783 | 331.664 | 319.3477
1535.9885 | 760.7952 | 344.0295 | 332.299 | 318.9381
1536.9885 | 763.4741 | 344.0284 | 332.0281 | 319.2685
1537.9885 | 768.9769 | 343.8773 | 331.8169 | 319.409
1538.9885 | 768.4106 | 344.1678 | 332.0361 | 319.2742
1539.9885 | 764.9263 | 344.0383 | 332.0878 | 319.1988
1540.9885 | 766.2396 | 344.0492 | 331.9038 | 318.5833
1541.9885 | 761.7632 | 343.5745 | 331.7367 | 319.1784
1542.9885 | 763.3637 | 343.9224 | 331.9297 | 319.3275
1543.9885 | 760.8716 | 344.2678 | 332.5031 | 319.4827
1544.9885 | 759.0662 | 344.4567 | 333.2968 | 319.838
1545.9885 | 763.7984 | 344.7854 | 333.7701 | 319.854
1546.9885 | 773.6295 | 344.6687 | 334.3724 | 319.8911
1547.9885 | 774.3804 | 344.9903 | 334.8898 | 320.297
1548.9885 | 770.5526 | 344.7832 | 334.9879 | 320.9168
1549.9885 | 774.8203 | 344.6516 | 335.3896 | 321.1593
1550.9885 | 782.3453 | 344.7497 | 335.2507 | 322.3303
1551.9885 | 780.6214 | 345.0785 | 335.4107 | 322.6207
1552.9885 | 777.5037 | 345.8879 | 335.7296 | 322.1849
1553.9885 | 776.2322 | 346.7398 | 335.9442 | 321.9829
1554.9885 | 777.8375 | 347.2964 | 336.2915 | 322.3726
1555.9885 | 776.4796 | 347.9251 | 336.0064 | 323.1913
1556.9885 | 772.0611 | 348.0862 | 335.9213 | 323.7143
1557.9885 | 769.5694 | 348.6414 | 337.1307 | 323.5194
1558.9885 | 769.3091 | 349.3217 | 338.0891 | 324.1023
1559.9885 | 766.7024 | 348.9581 | 338.4806 | 324.0397
1560.9885 | 777.7651 | 349.0548 | 338.0492 | 323.6513
1561.9885 | 783.4627 | 349.1775 | 338.2948 | 323.4291
1562.9885 | 783.4618 | 349.747 | 338.3555 | 323.8232
1563.9885 | 777.7284 | 349.8096 | 338.9303 | 324.2083
1564.9885 | 782.4826 | 349.9984 | 338.8254 | 324.1848
1565.9885 | 781.7266 | 350.4263 | 339.2443 | 324.0605
1566.9885 | 783.3711 | 350.4946 | 340.1703 | 324.6576
1567.9885 | 782.9158 | 350.497 | 340.1754 | 324.9864
1568.9885 | 782.8067 | 351.0198 | 340.7997 | 325.4563
1569.9885 | 785.8213 | 351.1102 | 341.3244 | 325.7685
1570.9885 | 788.6883 | 351.461 | 341.1874 | 325.7519
1571.9885 | 785.2241 | 351.8644 | 340.941 | 325.9186
1572.9885 | 788.6734 | 351.5546 | 340.7324 | 325.7479
1573.9885 | 791.7612 | 351.3571 | 340.4837 | 325.8624
1574.9885 | 793.1321 | 351.7443 | 340.4831 | 325.3322
1575.9885 | 786.7246 | 351.5603 | 340.0311 | 325.5701
1576.9885 | 780.7449 | 351.6512 | 339.4346 | 325.0318
1577.9885 | 783.4611 | 351.3128 | 339.658 | 324.7948
1578.9885 | 786.6335 | 351.3914 | 339.78 | 325.4589
1579.9885 | 786.2418 | 351.6942 | 339.842 | 325.1907
1580.9885 | 795.812 | 352.059 | 339.8962 | 324.8727
1581.9885 | 796.1225 | 352.6957 | 340.3818 | 325.5182
1582.9885 | 789.3171 | 352.6137 | 341.1325 | 326.0409
1583.9885 | 783.8224 | 352.6211 | 341.1219 | 326.2849
1584.9885 | 777.7107 | 352.8426 | 341.287 | 326.926
1585.9885 | 774.696 | 352.8161 | 341.7543 | 327.393
1586.9885 | 774.9012 | 352.8695 | 342.4859 | 327.5545
1587.9885 | 769.247 | 352.9789 | 342.7849 | 327.6096
1588.9885 | 770.4215 | 353.2078 | 342.7357 | 328.3614
1589.9885 | 768.7898 | 353.129 | 342.0146 | 328.6126
1590.9885 | 769.4222 | 353.3575 | 342.4792 | 328.8602
1591.9885 | 770.67 | 353.0575 | 342.1715 | 328.7818
1592.9885 | 769.4516 | 353.3264 | 341.1265 | 329.3441
1593.9885 | 768.5558 | 352.9007 | 340.821 | 329.4836
1594.9885 | 766.4264 | 353.918 | 340.5221 | 329.0989
1595.9885 | 768.4662 | 353.9065 | 340.6522 | 329.0062
1596.9885 | 774.1695 | 354.2676 | 340.8563 | 329.5624
1597.9885 | 777.1863 | 354.2282 | 340.9031 | 330.1392
1598.9885 | 775.8826 | 354.0579 | 341.0656 | 329.7662
1599.9885 | 777.1408 | 354.4019 | 341.0244 | 329.9079
1600.9885 | 777.2508 | 354.4529 | 341.0493 | 330.243
1601.9885 | 782.6672 | 354.5873 | 341.1364 | 329.9822
1602.9885 | 779.1133 | 354.7755 | 340.9282 | 329.8246
1603.9885 | 777.6736 | 354.7226 | 341.0233 | 329.491
1604.9885 | 776.0712 | 355.0924 | 341.6005 | 329.565
1605.9885 | 778.0423 | 355.3547 | 341.9709 | 329.7545
1606.9885 | 776.2369 | 355.3751 | 342.8255 | 330.3542
1607.9885 | 764.2292 | 355.9126 | 342.5319 | 330.7202
1608.9885 | 761.4578 | 356.4562 | 342.6422 | 330.9723
1609.9885 | 764.3726 | 357.0171 | 342.3745 | 330.9164
1610.9885 | 770.3027 | 357.2597 | 343.0757 | 330.8788
1611.9885 | 771.3964 | 357.5683 | 343.6369 | 331.5642
1612.9885 | 769.526 | 357.6678 | 344.1325 | 332.0683
1613.9885 | 762.2497 | 357.603 | 344.3854 | 332.0549
1614.9885 | 759.2293 | 358.1095 | 345.7027 | 332.8106
1615.9885 | 764.2086 | 358.6508 | 345.6128 | 333.3791
1616.9885 | 770.0789 | 359.7075 | 345.4758 | 334.062
1617.9885 | 770.3012 | 360.0297 | 346.3193 | 334.0548
1618.9885 | 773.0045 | 360.0018 | 346.5733 | 334.9792
1619.9885 | 773.7869 | 360.7312 | 346.8543 | 335.3953
1620.9885 | 775.6665 | 361.6504 | 346.8724 | 335.5602
1621.9885 | 770.0234 | 361.7577 | 347.1705 | 335.8391
1622.9885 | 771.8017 | 362.2466 | 347.1556 | 336.2568
1623.9885 | 775.1881 | 362.8201 | 347.5288 | 336.503
1624.9885 | 770.4546 | 362.9727 | 348.2183 | 337.1312
1625.9885 | 777.0872 | 364.3537 | 349.7489 | 338.0416
1626.9885 | 779.7104 | 364.0159 | 349.9644 | 338.5424
1627.9885 | 774.6009 | 364.4653 | 350.1286 | 339.354
1628.9885 | 772.1861 | 364.8114 | 350.8494 | 339.8355
1629.9885 | 775.488 | 364.7729 | 351.1199 | 339.988
1630.9885 | 773.0664 | 364.621 | 350.8269 | 340.544
1631.9885 | 767.5562 | 364.5157 | 350.6654 | 339.8182
1632.9885 | 771.3773 | 364.5453 | 350.4811 | 340.3639
1633.9885 | 772.7812 | 364.7116 | 350.4318 | 339.7695
1634.9885 | 761.8569 | 365.0224 | 350.6196 | 339.6693
1635.9885 | 758.103 | 365.334 | 351.45 | 339.5941
1636.9885 | 760.8987 | 365.3467 | 351.8318 | 339.5623
1637.9885 | 756.2341 | 365.7142 | 352.0509 | 340.1062
1638.9885 | 756.9043 | 365.6281 | 352.7856 | 340.4975
1639.9885 | 761.0958 | 365.6743 | 352.9836 | 341.6794
1640.9885 | 762.9442 | 365.8979 | 353.2374 | 341.7947
1641.9885 | 764.9516 | 366.0557 | 353.353 | 341.7291
1642.9885 | 764.6605 | 366.1704 | 353.2401 | 342.3548
1643.9885 | 763.894 | 365.8692 | 353.3409 | 342.9727
1644.9885 | 767.1787 | 365.8629 | 353.2836 | 342.3035
1645.9885 | 770.9041 | 365.9884 | 353.2139 | 342.398
1646.9885 | 766.0857 | 366.5984 | 353.0256 | 341.7623
1647.9885 | 759.9255 | 366.964 | 352.4823 | 340.8625
1648.9885 | 760.8941 | 366.6254 | 352.22 | 341.1915
1649.9885 | 756.4715 | 366.7929 | 351.7197 | 341.1793
1650.9885 | 759.667 | 367.2144 | 352.1702 | 341.1806
1651.9885 | 759.2473 | 367.2202 | 352.2016 | 341.0883
1652.9885 | 759.1634 | 367.2982 | 352.0239 | 340.6648
1653.9885 | 759.4332 | 367.6277 | 352.1465 | 340.2711
1654.9885 | 754.0839 | 368.142 | 352.3569 | 340.0742
1655.9885 | 753.1906 | 367.8876 | 352.4388 | 340.3118
1656.9885 | 754.4722 | 368.6865 | 352.4928 | 340.2072
1657.9885 | 744.4189 | 369.5147 | 352.3842 | 339.9809
1658.9885 | 742.6483 | 369.8528 | 352.2264 | 340.1785
1659.9885 | 748.5341 | 370.3579 | 352.4782 | 339.9493
1660.9885 | 740.1621 | 370.5669 | 352.308 | 339.861
1661.9885 | 729.5302 | 371.3571 | 352.6614 | 339.9439
1662.9885 | 737.2123 | 371.3811 | 352.9498 | 340.6064
1663.9885 | 746.4882 | 371.2151 | 353.0826 | 341.0723
1664.9885 | 750.1587 | 371.4543 | 353.515 | 341.3783
1665.9885 | 750.8783 | 371.9192 | 353.7263 | 341.6244
1666.9885 | 751.7825 | 372.5866 | 353.9157 | 341.7901
1667.9885 | 754.5783 | 373.4635 | 354.5324 | 341.9727
1668.9885 | 758.6745 | 373.8321 | 355.5156 | 342.0965
1669.9885 | 763.3865 | 374.8031 | 356.1026 | 342.2233
1670.9885 | 769.8141 | 374.8756 | 356.2646 | 342.7155
1671.9885 | 769.5577 | 375.0499 | 356.4123 | 343.0464
1672.9885 | 770.2854 | 374.9922 | 356.1957 | 343.2582
1673.9885 | 778.5873 | 375.1885 | 356.8109 | 343.4373
1674.9885 | 774.6495 | 375.2046 | 357.1818 | 343.5011
1675.9885 | 779.5516 | 375.4989 | 357.5007 | 343.6647
1676.9885 | 773.1431 | 375.5607 | 358.0793 | 343.7777
1677.9885 | 760.0564 | 376.3938 | 358.0435 | 344.0319
1678.9885 | 756.6561 | 376.736 | 359.0411 | 345.0114
1679.9885 | 753.8636 | 376.5006 | 359.3284 | 344.797
1680.9885 | 751.0603 | 377.0925 | 359.8672 | 345.2965
1681.9885 | 748.3003 | 378.1066 | 360.1041 | 345.0665
1682.9885 | 750.0126 | 378.8648 | 360.529 | 344.8515
1683.9885 | 748.0406 | 379.4474 | 360.6895 | 344.2769
1684.9885 | 756.5129 | 379.7989 | 361.3353 | 344.1361
1685.9885 | 758.2151 | 380.0744 | 361.4184 | 344.8984
1686.9885 | 757.7217 | 380.4177 | 361.9771 | 345.5742
1687.9885 | 761.0382 | 380.8554 | 363.2222 | 346.5438
1688.9885 | 753.1904 | 380.9174 | 364.1033 | 347.3547
1689.9885 | 756.8124 | 381.038 | 364.3355 | 347.7766
1690.9885 | 758.5784 | 381.0157 | 364.3177 | 347.7207
1691.9885 | 762.0046 | 380.8949 | 364.2945 | 347.4731
1692.9885 | 761.2713 | 380.9396 | 364.1031 | 347.0335
1693.9885 | 759.2075 | 380.9503 | 363.9493 | 346.77
1694.9885 | 758.7951 | 381.0619 | 364.3163 | 346.8795
1695.9885 | 759.2273 | 380.905 | 364.1106 | 347.117
1696.9885 | 749.9369 | 380.6195 | 364.2029 | 347.6734
1697.9885 | 748.3815 | 380.2925 | 364.5848 | 348.9672
1698.9885 | 752.1065 | 380.0471 | 364.7135 | 349.087
1699.9885 | 758.1032 | 379.6431 | 364.5389 | 349.535
1700.9885 | 761.9149 | 379.8034 | 364.6431 | 349.4121
1701.9885 | 767.0595 | 380.0016 | 364.9323 | 349.3193
1702.9885 | 771.0756 | 380.3461 | 365.3677 | 349.448
1703.9885 | 771.2107 | 380.8758 | 365.5114 | 349.5032
1704.9885 | 768.6121 | 380.8962 | 365.4966 | 350.0338
1705.9885 | 776.1427 | 381.267 | 365.6291 | 350.1212
1706.9885 | 774.5759 | 381.478 | 365.569 | 349.9936
1707.9885 | 776.8475 | 381.9857 | 365.5075 | 350.22
1708.9885 | 786.3991 | 382.2934 | 365.5165 | 350.1274
1709.9885 | 787.4792 | 382.5138 | 365.5696 | 350.6791
1710.9885 | 786.1072 | 382.7476 | 365.7474 | 350.7665
1711.9885 | 785.0871 | 383.302 | 365.5193 | 350.6735
1712.9885 | 787.4125 | 383.7036 | 365.5261 | 350.7955
1713.9885 | 786.9674 | 383.8621 | 365.5408 | 351.3641
1714.9885 | 784.0583 | 383.7623 | 365.7425 | 351.9164
1715.9885 | 788.0537 | 383.9029 | 366.3636 | 352.0538
1716.9885 | 786.1349 | 384.5303 | 366.5452 | 352.1786
1717.9885 | 787.1183 | 384.703 | 366.3282 | 352.0735
1718.9885 | 787.072 | 385.2056 | 366.0865 | 351.8219
1719.9885 | 781.9955 | 385.3052 | 366.0027 | 351.7005
1720.9885 | 770.273 | 385.4136 | 365.9665 | 351.501
1721.9885 | 768.489 | 385.146 | 365.8222 | 352.3661
1722.9885 | 775.0852 | 385.7255 | 366.0352 | 351.853
1723.9885 | 781.8248 | 385.9826 | 366.4551 | 352.2187
1724.9885 | 779.2489 | 386.389 | 366.7262 | 352.3243
1725.9885 | 781.2828 | 386.4924 | 367.0326 | 352.5399
1726.9885 | 786.9887 | 386.8615 | 367.4639 | 352.6108
1727.9885 | 789.6929 | 386.7992 | 367.3058 | 353.1536
1728.9885 | 786.146 | 386.9177 | 367.4255 | 353.5591
1729.9885 | 785.8778 | 386.8611 | 367.0668 | 353.8147
1730.9885 | 785.1264 | 387.0222 | 366.9023 | 353.7161
1731.9885 | 773.7298 | 387.314 | 366.6229 | 353.6162
1732.9885 | 773.1273 | 387.2023 | 366.8748 | 353.6887
1733.9885 | 773.8399 | 387.3892 | 367.1335 | 353.3026
1734.9885 | 776.9511 | 387.4551 | 367.769 | 353.902
1735.9885 | 777.9443 | 388.2662 | 368.5832 | 353.853
1736.9885 | 781.8827 | 388.859 | 369.1279 | 353.7177
1737.9885 | 782.7209 | 389.4066 | 369.8084 | 353.8174
1738.9885 | 783.4074 | 389.6436 | 370.1943 | 354.4284
1739.9885 | 783.6565 | 389.758 | 370.5127 | 354.5991
1740.9885 | 783.6193 | 389.8414 | 370.676 | 355.2233
1741.9885 | 787.0928 | 390.1895 | 371.1246 | 354.962
1742.9885 | 792.8586 | 390.465 | 371.517 | 354.8533
1743.9885 | 795.5897 | 390.9074 | 371.6754 | 355.0634
1744.9885 | 800.6271 | 391.6383 | 371.3269 | 355.0691
1745.9885 | 792.1869 | 392.8897 | 371.3643 | 355.0295
1746.9885 | 783.8708 | 393.5139 | 371.6881 | 355.8828
1747.9885 | 786.172 | 394.3204 | 371.6187 | 355.8845
1748.9885 | 789.4953 | 394.4868 | 371.3067 | 356.361
1749.9885 | 792.7936 | 394.6925 | 371.2494 | 357.0137
1750.9885 | 789.9773 | 395.3589 | 371.8766 | 357.1978
1751.9885 | 790.2478 | 395.797 | 371.958 | 357.4325
1752.9885 | 789.6301 | 395.9857 | 372.6586 | 357.5448
1753.9885 | 797.6595 | 395.6332 | 373.3893 | 357.4026
1754.9885 | 798.9081 | 395.6065 | 373.9285 | 357.4092
1755.9885 | 797.5002 | 396.7218 | 374.2654 | 357.419
1756.9885 | 795.6444 | 397.2694 | 374.1147 | 358.2091
1757.9885 | 796.1303 | 397.2506 | 374.1596 | 358.1995
1758.9885 | 801.6096 | 397.1181 | 374.4249 | 358.5747
1759.9885 | 804.9638 | 397.0694 | 374.4589 | 358.3467
1760.9885 | 812.532 | 396.815 | 374.2501 | 358.2832
1761.9885 | 811.7902 | 398.2843 | 374.0334 | 357.9941
1762.9885 | 811.8617 | 398.8344 | 374.3988 | 357.6206
1763.9885 | 805.0989 | 399.4014 | 374.8335 | 357.8659
1764.9885 | 798.7489 | 400.0134 | 375.1405 | 358.0578
1765.9885 | 797.9711 | 400.1414 | 375.0146 | 358.1405
1766.9885 | 796.8385 | 399.9258 | 375.3228 | 358.1632
1767.9885 | 801.1384 | 400.3515 | 375.7485 | 358.5023
1768.9885 | 799.2963 | 401.1338 | 375.921 | 358.968
1769.9885 | 810.7655 | 401.2684 | 375.9192 | 359.0823
1770.9885 | 807.8533 | 401.2599 | 376.1583 | 359.4217
1771.9885 | 806.2148 | 401.3364 | 376.167 | 359.7372
1772.9885 | 802.5239 | 401.7275 | 376.381 | 360.0975
1773.9885 | 804.0305 | 401.8597 | 376.5917 | 360.3845
1774.9885 | 810.2621 | 402.4802 | 376.3864 | 360.8666
1775.9885 | 811.8756 | 403.056 | 376.2407 | 361.1963
1776.9885 | 814.1591 | 403.7832 | 376.3996 | 361.397
1777.9885 | 818.0328 | 404.4735 | 376.7102 | 361.428
1778.9885 | 814.4369 | 404.9395 | 377.4335 | 361.8029
1779.9885 | 812.607 | 405.0624 | 377.3726 | 361.928
1780.9885 | 815.3959 | 405.0204 | 377.6638 | 362.605
1781.9885 | 815.29 | 405.0058 | 377.8136 | 362.6102
1782.9885 | 813.3058 | 405.1352 | 378.2291 | 362.5015
1783.9885 | 806.5483 | 405.227 | 378.4859 | 362.2894
1784.9885 | 805.5424 | 404.5642 | 378.3383 | 362.471
1785.9885 | 802.2964 | 404.2282 | 378.5643 | 362.313
1786.9885 | 801.0814 | 403.7328 | 378.7297 | 362.1473
1787.9885 | 803.2005 | 403.4669 | 378.3533 | 362.0628
1788.9885 | 808.0713 | 403.7942 | 378.0925 | 362.4114
1789.9885 | 805.7196 | 403.5218 | 378.2203 | 362.4101
1790.9885 | 800.8023 | 403.161 | 378.6027 | 362.2415
1791.9885 | 800.5555 | 403.0558 | 378.7587 | 362.105
1792.9885 | 804.1216 | 402.8634 | 378.9731 | 362.4181
1793.9885 | 806.1391 | 402.4408 | 379.3849 | 362.5235
1794.9885 | 807.6266 | 401.9352 | 379.3935 | 362.9933
1795.9885 | 804.4924 | 401.391 | 379.0367 | 363.326
1796.9885 | 804.7778 | 401.1571 | 378.5862 | 363.5029
1797.9885 | 807.932 | 400.9171 | 378.1157 | 362.7364
1798.9885 | 806.7626 | 400.7409 | 377.5424 | 363.2433
1799.9885 | 801.8766 | 401.2864 | 377.2014 | 363.0319
1800.9885 | 796.8176 | 401.6029 | 378.2262 | 362.8581
1801.9885 | 792.8485 | 401.9969 | 379.29 | 362.6743
1802.9885 | 794.0254 | 402.2099 | 379.5702 | 362.89
1803.9885 | 793.2119 | 402.0262 | 379.615 | 362.4606
1804.9885 | 791.4068 | 402.6914 | 380.029 | 362.2998
1805.9885 | 791.1909 | 402.6694 | 379.7152 | 362.217
1806.9885 | 795.3682 | 402.8868 | 379.6823 | 362.4897
1807.9885 | 794.5753 | 402.8408 | 379.2483 | 362.8372
1808.9885 | 795.2826 | 402.8791 | 379.0494 | 362.9201
1809.9885 | 793.0103 | 402.9151 | 378.6327 | 363.0002
1810.9885 | 791.9073 | 403.4279 | 378.4164 | 363.641
1811.9885 | 792.5806 | 403.2676 | 379.2555 | 363.6706
1812.9885 | 790.3258 | 403.6399 | 379.6313 | 363.2722
1813.9885 | 791.7743 | 403.692 | 380.2472 | 363.8154
1814.9885 | 794.0679 | 404.0283 | 380.2827 | 363.7313
1815.9885 | 792.6277 | 403.8964 | 380.1598 | 363.9112
1816.9885 | 787.2375 | 403.6236 | 379.9471 | 363.7343
1817.9885 | 787.2847 | 403.4071 | 379.7317 | 364.0603
1818.9885 | 794.1163 | 403.6339 | 379.5307 | 364.3046
1819.9885 | 796.6574 | 404.378 | 380.8499 | 364.2925
1820.9885 | 790.676 | 405.2338 | 382.2062 | 364.006
1821.9885 | 787.358 | 405.6571 | 383.4435 | 364.3836
1822.9885 | 791.0536 | 405.5234 | 383.4927 | 364.7992
1823.9885 | 789.095 | 404.9382 | 383.9521 | 365.3157
1824.9885 | 788.8087 | 404.952 | 384.3314 | 365.8824
1825.9885 | 789.9225 | 404.7542 | 384.5863 | 366.2853
1826.9885 | 789.2939 | 404.9884 | 385.5656 | 366.4167
1827.9885 | 786.4486 | 405.8294 | 386.1102 | 366.677
1828.9885 | 772.0062 | 406.1105 | 386.7695 | 367.7711
1829.9885 | 762.993 | 406.2765 | 387.1412 | 367.6932
1830.9885 | 754.448 | 406.3593 | 387.8336 | 367.6926
1831.9885 | 750.3016 | 406.1131 | 388.2859 | 367.7833
1832.9885 | 757.4074 | 406.0072 | 388.5452 | 367.3721
1833.9885 | 760.1301 | 405.7706 | 388.5343 | 367.6376
1834.9885 | 760.5209 | 406.0291 | 388.4525 | 367.7033
1835.9885 | 755.7447 | 406.0159 | 388.4768 | 367.6246
1836.9885 | 764.9193 | 406.8331 | 388.1448 | 367.5704
1837.9885 | 769.2593 | 407.3771 | 387.818 | 367.824
1838.9885 | 772.736 | 407.5947 | 387.9692 | 368.2235
1839.9885 | 775.6683 | 407.9995 | 387.9979 | 368.5274
1840.9885 | 775.943 | 409.0896 | 388.2454 | 369.9091
1841.9885 | 778.6417 | 409.3199 | 389.2204 | 370.2604
1842.9885 | 788.3266 | 410.1565 | 389.959 | 370.4481
1843.9885 | 798.2152 | 411.2497 | 390.4254 | 370.6503
1844.9885 | 795.5936 | 411.2067 | 390.9253 | 370.6517
1845.9885 | 799.3596 | 411.3262 | 391.0672 | 371.1732
1846.9885 | 796.8851 | 411.5483 | 391.0098 | 371.2534
1847.9885 | 793.0247 | 411.9812 | 391.2603 | 371.5581
1848.9885 | 795.3428 | 411.7964 | 391.3249 | 371.5207
1849.9885 | 794.3758 | 412.0583 | 391.424 | 371.0491
1850.9885 | 799.6262 | 411.5411 | 391.2038 | 371.0696
1851.9885 | 799.0686 | 411.8849 | 390.9725 | 371.5505
1852.9885 | 798.2709 | 412.024 | 390.659 | 372.2625
1853.9885 | 794.5132 | 412.9425 | 391.0917 | 372.6009
1854.9885 | 792.3443 | 412.8616 | 391.5075 | 373.0925
1855.9885 | 793.8241 | 412.5028 | 391.8472 | 374.4517
1856.9885 | 789.207 | 412.0424 | 392.1144 | 375.2225
1857.9885 | 791.7037 | 411.3934 | 392.3992 | 375.6011
1858.9885 | 794.9028 | 410.7758 | 392.3871 | 375.3993
1859.9885 | 798.5844 | 410.6577 | 392.1369 | 375.0552
1860.9885 | 795.5793 | 411.0378 | 392.137 | 374.6126
1861.9885 | 795.6651 | 411.009 | 391.7756 | 374.2685
1862.9885 | 792.7789 | 411.1413 | 391.8959 | 374.393
1863.9885 | 787.4482 | 411.4568 | 392.1257 | 375.605
1864.9885 | 787.2079 | 411.2587 | 392.4703 | 376.6431
1865.9885 | 791.3795 | 411.497 | 392.0382 | 377.1342
1866.9885 | 788.5293 | 412.1084 | 391.9612 | 377.1347
1867.9885 | 788.3228 | 412.0276 | 391.6448 | 376.9024
1868.9885 | 790.9366 | 412.0734 | 391.6757 | 376.4043
1869.9885 | 793.1292 | 412.9645 | 391.596 | 376.2643
1870.9885 | 799.1937 | 412.9998 | 391.3441 | 376.1996
1871.9885 | 800.2994 | 413.2065 | 391.0598 | 375.9694
1872.9885 | 799.1993 | 413.251 | 390.9259 | 376.5597
1873.9885 | 801.2734 | 413.4827 | 391.0625 | 377.1455
1874.9885 | 800.6754 | 413.678 | 391.5017 | 377.601
1875.9885 | 802.3229 | 413.9618 | 392.4041 | 378.2512
1876.9885 | 794.2549 | 413.9453 | 392.9989 | 378.5471
1877.9885 | 791.6652 | 413.8554 | 393.122 | 378.8389
1878.9885 | 792.4064 | 413.8845 | 393.3075 | 378.9299
1879.9885 | 790.427 | 414.0589 | 393.65 | 378.9194
1880.9885 | 792.8928 | 413.8679 | 393.9641 | 378.5239
1881.9885 | 790.4044 | 413.9353 | 393.9435 | 378.0861
1882.9885 | 790.9688 | 414.0505 | 394.1455 | 377.8063
1883.9885 | 783.3031 | 414.0744 | 394.1423 | 378.0583
1884.9885 | 780.564 | 414.4331 | 394.9237 | 378.3147
1885.9885 | 779.6682 | 414.3906 | 395.1919 | 378.2161
1886.9885 | 778.8526 | 414.8883 | 394.9122 | 377.5725
1887.9885 | 783.9766 | 415.2349 | 394.7797 | 377.1705
1888.9885 | 784.6525 | 415.56 | 394.702 | 376.9752
1889.9885 | 782.4547 | 415.4636 | 394.3455 | 376.9337
1890.9885 | 785.6048 | 415.3934 | 394.6803 | 377.2582
1891.9885 | 786.9116 | 416.2469 | 395.1466 | 377.4662
1892.9885 | 780.013 | 417.3785 | 395.3558 | 377.8337
1893.9885 | 778.4698 | 417.2811 | 395.332 | 378.3913
1894.9885 | 774.3828 | 417.4559 | 395.3157 | 378.5076
1895.9885 | 772.7242 | 417.2181 | 395.5823 | 379.112
1896.9885 | 770.2305 | 417.2673 | 396.0613 | 379.6221
1897.9885 | 774.4937 | 417.4816 | 396.4674 | 380.9209
1898.9885 | 777.2175 | 417.1114 | 397.1407 | 381.8477
1899.9885 | 780.42 | 416.6217 | 397.5043 | 382.4716
1900.9885 | 782.9589 | 416.6358 | 397.6979 | 382.7405
1901.9885 | 778.78 | 416.6568 | 397.391 | 382.7372
1902.9885 | 775.2726 | 416.6199 | 397.671 | 383.2402
1903.9885 | 777.168 | 416.6083 | 398.2134 | 383.5289
1904.9885 | 772.4077 | 416.3141 | 398.081 | 383.732
1905.9885 | 776.2573 | 416.6057 | 397.9796 | 384.5101
1906.9885 | 781.1315 | 416.1753 | 398.0575 | 384.8705
1907.9885 | 783.9363 | 416.5438 | 397.9968 | 385.1731
1908.9885 | 785.8534 | 416.8243 | 397.578 | 386.0746
1909.9885 | 777.2605 | 417.5737 | 397.3563 | 386.6139
1910.9885 | 771.2586 | 417.8376 | 397.3905 | 386.758
1911.9885 | 771.7422 | 418.4652 | 397.9402 | 386.9415
1912.9885 | 771.6288 | 418.305 | 397.9668 | 387.0805
1913.9885 | 768.8142 | 417.8931 | 398.0951 | 386.9826
1914.9885 | 770.91 | 417.9212 | 397.9395 | 386.98
1915.9885 | 776.587 | 417.9119 | 397.8284 | 387.1615
1916.9885 | 775.4093 | 418.0161 | 398.051 | 387.1824
1917.9885 | 780.1005 | 417.8932 | 398.5788 | 387.7008
1918.9885 | 779.2071 | 417.6939 | 399.8498 | 388.3039
1919.9885 | 775.0157 | 417.7211 | 400.0041 | 388.8345
1920.9885 | 772.4356 | 418.0844 | 400.4003 | 389.2232
1921.9885 | 769.4367 | 417.8923 | 400.7672 | 389.9792
1922.9885 | 763.8053 | 418.1509 | 401.1745 | 390.3244
1923.9885 | 766.9475 | 418.447 | 401.4174 | 390.7833
1924.9885 | 758.2405 | 418.8069 | 401.778 | 391.0352
1925.9885 | 767.957 | 418.8566 | 401.6962 | 390.9826
1926.9885 | 769.724 | 418.977 | 401.6087 | 391.2298
1927.9885 | 770.6359 | 418.8843 | 402.6039 | 391.4382
1928.9885 | 769.8789 | 418.7938 | 402.6218 | 391.1866
1929.9885 | 771.6848 | 418.606 | 402.1184 | 390.918
1930.9885 | 769.9112 | 418.1363 | 401.6048 | 390.821
1931.9885 | 767.0864 | 419.2726 | 401.384 | 390.5156
1932.9885 | 770.3386 | 418.8701 | 400.9393 | 390.529
1933.9885 | 766.9753 | 420.8117 | 400.998 | 390.703
1934.9885 | 762.6022 | 421.5178 | 401.0955 | 390.3641
1935.9885 | 751.198 | 421.6102 | 401.2413 | 390.5607
1936.9885 | 751.9257 | 422.0376 | 401.8309 | 390.678
1937.9885 | 755.4273 | 422.05 | 402.2858 | 391.2867
1938.9885 | 742.2187 | 422.2279 | 403.0526 | 391.8116
1939.9885 | 738.4922 | 422.1249 | 403.8204 | 392.5037
1940.9885 | 733.222 | 422.4904 | 404.5319 | 392.9957
1941.9885 | 735.3162 | 422.6073 | 404.8128 | 393.3521
1942.9885 | 736.298 | 423.5057 | 404.8019 | 393.6195
1943.9885 | 733.4145 | 424.1671 | 404.7662 | 393.2877
1944.9885 | 727.8958 | 423.9969 | 404.9865 | 392.4828
1945.9885 | 723.4052 | 423.8775 | 405.1008 | 392.1808
1946.9885 | 726.2356 | 424.0262 | 405.182 | 392.3216
1947.9885 | 726.5461 | 424.4181 | 405.3924 | 392.6952
1948.9885 | 731.655 | 424.2929 | 405.1905 | 393.7062
1949.9885 | 732.957 | 424.2637 | 405.1632 | 393.9744
1950.9885 | 728.0323 | 424.7408 | 405.451 | 394.6195
1951.9885 | 726.5613 | 425.011 | 405.2049 | 394.4921
1952.9885 | 734.9342 | 424.872 | 405.3352 | 394.9591
1953.9885 | 743.5683 | 425.7317 | 405.8853 | 395.2457
1954.9885 | 743.0424 | 426.0846 | 406.1617 | 395.8779
1955.9885 | 747.1798 | 426.577 | 406.3561 | 396.2903
1956.9885 | 757.4748 | 426.7348 | 406.6541 | 396.8148
1957.9885 | 760.4145 | 427.0648 | 407.2891 | 396.2986
1958.9885 | 763.761 | 427.4653 | 407.4518 | 395.4705
1959.9885 | 748.1816 | 427.7201 | 407.3114 | 394.7729
1960.9885 | 744.3721 | 427.8685 | 407.4371 | 394.7465
1961.9885 | 741.7537 | 428.5319 | 407.7217 | 394.7092
1962.9885 | 741.8398 | 428.7102 | 407.4577 | 394.9421
1963.9885 | 730.993 | 429.3066 | 407.8156 | 395.4396
1964.9885 | 735.6566 | 429.3996 | 408.0283 | 395.8678
1965.9885 | 743.9856 | 429.5923 | 408.3159 | 396.5241
1966.9885 | 747.315 | 429.3536 | 408.7574 | 397.4816
1967.9885 | 752.97 | 429.4721 | 409.3858 | 397.9839
1968.9885 | 753.2159 | 429.1751 | 409.6797 | 398.3978
1969.9885 | 754.1219 | 428.7877 | 409.8513 | 398.7479
1970.9885 | 761.958 | 428.5115 | 409.7622 | 398.5409
1971.9885 | 754.9152 | 428.1987 | 409.4973 | 398.659
1972.9885 | 758.0289 | 427.9847 | 409.8872 | 398.6621
1973.9885 | 762.2021 | 427.9864 | 409.9318 | 399.2773
1974.9885 | 763.3469 | 427.926 | 409.9544 | 399.517
1975.9885 | 762.6458 | 428.2473 | 410.0977 | 399.6886
1976.9885 | 768.31 | 428.2626 | 410.4706 | 399.8372
1977.9885 | 772.7995 | 428.4886 | 410.6284 | 400.3266
1978.9885 | 773.7882 | 428.779 | 410.5941 | 401.1451
1979.9885 | 764.439 | 430.2421 | 410.6994 | 401.0545
1980.9885 | 758.9995 | 429.8649 | 410.5591 | 400.7039
1981.9885 | 763.0552 | 430.0847 | 410.6936 | 400.506
1982.9885 | 761.577 | 430.5862 | 410.81 | 400.6145
1983.9885 | 766.9352 | 431.0757 | 410.8234 | 400.5587
1984.9885 | 765.6227 | 431.1516 | 410.7423 | 399.8371
1985.9885 | 761.4459 | 431.1414 | 411.2497 | 399.7313
1986.9885 | 758.9606 | 431.2593 | 411.4608 | 399.2872
1987.9885 | 760.3764 | 431.66 | 411.4529 | 399.0414
1988.9885 | 758.946 | 431.3891 | 411.3592 | 398.9733
1989.9885 | 760.2977 | 431.1585 | 411.6528 | 399.0393
1990.9885 | 762.6373 | 431.3407 | 411.9998 | 399.6748
1991.9885 | 763.0716 | 431.2527 | 412.0019 | 400.0827
1992.9885 | 766.1643 | 431.7824 | 412.1344 | 400.66
1993.9885 | 767.3837 | 431.7345 | 412.0939 | 400.3812
1994.9885 | 760.4122 | 431.5478 | 412.1305 | 400.1469
1995.9885 | 767.8163 | 432.3185 | 412.1756 | 400.9033
1996.9885 | 767.9625 | 432.6299 | 412.3879 | 400.9968
1997.9885 | 773.0824 | 432.3918 | 412.2574 | 400.9148
1998.9885 | 768.774 | 433.2523 | 412.2215 | 400.8537
1999.9885 | 760.5081 | 434.2311 | 412.2998 | 401.0333
2000.9885 | 769.9928 | 434.8098 | 412.679 | 401.2524
2001.9885 | 773.8337 | 434.5345 | 413.1875 | 402.6871
2002.9885 | 781.0541 | 434.3172 | 413.5493 | 403.2379
2003.9885 | 785.4747 | 434.3295 | 413.946 | 404.1368
2004.9885 | 783.9308 | 434.5728 | 414.0757 | 405.2451
2005.9885 | 781.456 | 434.3582 | 413.9615 | 405.4814
2006.9885 | 779.4818 | 435.0878 | 414.4758 | 406.0479
2007.9885 | 775.4737 | 435.0814 | 414.7913 | 405.8557
2008.9885 | 769.4003 | 435.1391 | 414.8338 | 405.6031
2009.9885 | 765.9796 | 435.7386 | 414.53 | 405.4552
2010.9885 | 763.1204 | 436.2332 | 414.2162 | 405.2235
2011.9885 | 765.5859 | 436.3709 | 414.0964 | 404.7011
2012.9885 | 766.3931 | 436.1713 | 413.8205 | 404.5843
2013.9885 | 764.4066 | 436.335 | 413.8866 | 404.9588
2014.9885 | 762.365 | 436.116 | 414.1589 | 404.7738
2015.9885 | 759.9783 | 435.6312 | 414.3486 | 404.671
2016.9885 | 759.3702 | 435.4306 | 414.2315 | 405.3957
2017.9885 | 747.7261 | 435.043 | 413.9456 | 405.3523
2018.9885 | 747.3845 | 435.3237 | 414.143 | 405.7054
2019.9885 | 738.9145 | 435.825 | 414.6753 | 406.0136
2020.9885 | 741.962 | 436.5754 | 415.3158 | 406.2425
2021.9885 | 743.8505 | 438.3729 | 415.588 | 406.2106
2022.9885 | 739.3161 | 438.5547 | 415.7444 | 405.7892
2023.9885 | 740.9804 | 438.8544 | 416.1 | 405.6398
2024.9885 | 739.9123 | 438.1015 | 416.2173 | 405.7676
2025.9885 | 741.1887 | 438.1235 | 416.822 | 406.3411
2026.9885 | 745.1896 | 438.5418 | 417.1741 | 406.4325
2027.9885 | 749.7067 | 438.2526 | 416.9361 | 406.6668
2028.9885 | 755.8569 | 438.0762 | 416.9408 | 406.6306
2029.9885 | 762.4883 | 437.8744 | 417.0368 | 406.6065
2030.9885 | 764.4972 | 437.7165 | 418.2197 | 406.6391
2031.9885 | 764.4176 | 438.0968 | 418.2028 | 406.4475
2032.9885 | 755.648 | 438.0138 | 417.9989 | 406.3393
2033.9885 | 755.5935 | 438.6541 | 417.8193 | 406.9666
2034.9885 | 751.561 | 439.5068 | 417.7833 | 407.2766
2035.9885 | 747.995 | 439.947 | 418.1138 | 407.2436
2036.9885 | 748.9352 | 439.7026 | 418.3578 | 408.0714
2037.9885 | 750.3327 | 439.92 | 418.1456 | 408.6709
2038.9885 | 754.9837 | 439.8475 | 418.24 | 408.8932
2039.9885 | 752.2407 | 439.8217 | 418.4941 | 408.9537
2040.9885 | 761.7315 | 440.2308 | 418.6993 | 409.2563
2041.9885 | 765.3818 | 440.1483 | 418.802 | 409.4644
2042.9885 | 770.0453 | 440.4404 | 419.3754 | 410.0244
2043.9885 | 769.0985 | 440.425 | 419.3114 | 410.6586
2044.9885 | 767.3121 | 440.9419 | 419.5988 | 410.8269
2045.9885 | 757.9748 | 441.9481 | 420.1127 | 410.3905
2046.9885 | 752.7155 | 441.7872 | 420.2723 | 410.367
2047.9885 | 751.0305 | 441.8852 | 420.3455 | 410.573
2048.9885 | 751.1755 | 442.115 | 420.9979 | 410.9013
2049.9885 | 757.6552 | 442.1511 | 420.7378 | 411.2557
2050.9885 | 757.6665 | 442.5716 | 420.9646 | 411.7874
2051.9885 | 762.2521 | 443.2439 | 421.4818 | 412.0565
2052.9885 | 762.1395 | 443.6026 | 421.5311 | 412.3459
2053.9885 | 765.575 | 444.2095 | 421.7324 | 412.524
2054.9885 | 765.1227 | 444.7046 | 421.7515 | 413.1515
2055.9885 | 765.6126 | 444.062 | 421.4904 | 413.0791
2056.9885 | 763.0438 | 443.7435 | 421.3157 | 412.9539
2057.9885 | 753.7474 | 443.9334 | 420.9638 | 412.5036
2058.9885 | 756.4034 | 444.1173 | 420.8121 | 412.2036
2059.9885 | 764.7986 | 444.8015 | 421.0045 | 411.7575
2060.9885 | 766.3404 | 445.1796 | 421.0636 | 411.414
2061.9885 | 766.6584 | 446.2649 | 420.9748 | 411.0284
2062.9885 | 760.9393 | 447.1938 | 420.8387 | 410.7718
2063.9885 | 763.9129 | 447.4062 | 420.8008 | 410.954
2064.9885 | 764.8636 | 446.6328 | 421.6673 | 411.1208
2065.9885 | 761.9659 | 446.7499 | 422.2728 | 411.1985
2066.9885 | 758.6597 | 447.0701 | 422.96 | 411.4224
2067.9885 | 756.944 | 446.9481 | 423.3627 | 411.7027
2068.9885 | 759.3291 | 446.8902 | 424.4706 | 412.3617
2069.9885 | 754.2909 | 446.5381 | 424.8908 | 414.1989
2070.9885 | 751.1205 | 446.8025 | 425.3639 | 414.883
2071.9885 | 745.2866 | 447.2348 | 425.4654 | 415.2997
2072.9885 | 740.4863 | 447.7088 | 425.562 | 415.6699
2073.9885 | 739.6505 | 448.4313 | 425.8618 | 416.2983
2074.9885 | 741.2517 | 448.0408 | 425.6951 | 417.4767
2075.9885 | 744.1987 | 448.1461 | 426.3426 | 418.1165
2076.9885 | 745.6711 | 448.7375 | 426.6432 | 417.9932
2077.9885 | 744.6754 | 448.7087 | 427.176 | 417.6723
2078.9885 | 749.4563 | 449.3593 | 427.3739 | 418.4936
2079.9885 | 748.0307 | 449.4066 | 427.3895 | 418.5138
2080.9885 | 750.1497 | 449.1564 | 428.1471 | 419.036
2081.9885 | 746.7433 | 448.7914 | 428.0518 | 419.7467
2082.9885 | 744.0645 | 448.6636 | 427.999 | 420.5452
2083.9885 | 747.2138 | 448.7963 | 427.6761 | 421.004
2084.9885 | 736.2703 | 448.8605 | 427.4975 | 421.1682
2085.9885 | 734.4252 | 449.053 | 427.1795 | 420.6056
2086.9885 | 739.5227 | 449.7272 | 427.3735 | 420.3155
2087.9885 | 741.1209 | 449.5177 | 427.257 | 420.2081
2088.9885 | 748.7026 | 449.6702 | 427.257 | 420.2809
2089.9885 | 746.9854 | 450.3268 | 427.4322 | 420.5503
2090.9885 | 741.285 | 450.0609 | 427.6976 | 420.6223
2091.9885 | 738.7214 | 449.8723 | 427.5266 | 421.1631
2092.9885 | 737.0064 | 450.1767 | 428.4448 | 421.428
2093.9885 | 745.5689 | 450.6573 | 428.4452 | 421.8317
2094.9885 | 748.5454 | 451.6373 | 428.3475 | 421.7319
2095.9885 | 753.2621 | 452.7251 | 428.4126 | 422.1216
2096.9885 | 751.0723 | 452.8724 | 428.2844 | 422.3797
2097.9885 | 752.2015 | 453.3901 | 427.9819 | 422.3965
2098.9885 | 745.9061 | 453.1623 | 427.7279 | 422.7226
2099.9885 | 741.1887 | 453.0183 | 427.5238 | 422.3971
2100.9885 | 746.2144 | 452.9844 | 427.2205 | 421.6892
2101.9885 | 749.3396 | 452.7252 | 427.402 | 421.4366
2102.9885 | 745.3905 | 452.4482 | 427.4567 | 421.0451
2103.9885 | 752.1723 | 452.306 | 428.0417 | 420.9052
2104.9885 | 753.4842 | 452.3622 | 428.5765 | 421.0751
2105.9885 | 756.5779 | 452.1592 | 428.74 | 421.6726
2106.9885 | 757.7126 | 451.8296 | 428.957 | 422.1974
2107.9885 | 756.2518 | 452.1723 | 429.0655 | 423.1456
2108.9885 | 756.7647 | 451.9063 | 429.093 | 423.0817
2109.9885 | 754.958 | 452.3202 | 428.8387 | 423.118
2110.9885 | 753.3882 | 453.9036 | 428.9274 | 423.3523
2112.0042 | 752.0007 | 454.7933 | 429.3004 | 423.6884
2112.9885 | 747.0081 | 454.8242 | 429.5918 | 423.7047
2113.9885 | 741.3507 | 455.2963 | 429.8149 | 423.1789
2114.9885 | 737.8533 | 456.4556 | 429.8834 | 422.6412
2115.9885 | 737.1509 | 456.5954 | 429.7587 | 422.4132
2116.9885 | 739.2884 | 456.7121 | 429.4962 | 422.074
2117.9885 | 739.5073 | 457.5104 | 429.6629 | 421.8601
2118.9885 | 739.1331 | 457.9726 | 430.3519 | 421.8854
2119.9885 | 745.1813 | 458.2058 | 430.8572 | 421.8903
2120.9885 | 742.2451 | 457.5027 | 430.9156 | 422.0389
2121.9885 | 739.7858 | 457.6163 | 430.8562 | 422.0716
2122.9885 | 748.0875 | 457.3414 | 430.4443 | 422.0419
2123.9885 | 747.3895 | 457.5993 | 430.1499 | 422.382
2124.9885 | 731.9688 | 457.8357 | 430.1286 | 422.2491
2125.9885 | 738.7916 | 457.5018 | 429.6332 | 422.2171
2126.9885 | 741.0421 | 457.0388 | 429.4698 | 423.0463
2127.9885 | 730.9283 | 457.1928 | 429.5844 | 423.7784
2128.9885 | 736.7317 | 457.8934 | 429.7055 | 423.2914
2129.9885 | 741.5493 | 458.7443 | 429.5743 | 422.8655
2130.9885 | 740.2884 | 459.4225 | 429.8551 | 422.5955
2131.9885 | 731.9442 | 459.865 | 429.9353 | 422.4664
2132.9885 | 737.9378 | 460.7455 | 430.199 | 422.778
2133.9885 | 740.7915 | 461.9109 | 430.6901 | 423.1878
2134.9885 | 741.8718 | 462.345 | 431.2776 | 423.7072
2135.9885 | 739.6918 | 463.1559 | 432.4882 | 424.5359
2136.9885 | 750.9203 | 463.169 | 433.5038 | 424.9809
2137.9885 | 748.5539 | 462.674 | 434.2089 | 425.8539
2138.9885 | 748.1765 | 462.4667 | 434.5011 | 426.4338
2139.9885 | 750.8402 | 462.6826 | 434.699 | 427.1351
2140.9885 | 750.8216 | 462.7174 | 434.6321 | 427.2282
2141.9885 | 750.4817 | 462.8172 | 434.6924 | 427.7087
2142.9885 | 747.293 | 463.367 | 435.6442 | 427.9037
2143.9885 | 748.7341 | 464.1317 | 435.9802 | 428.837
2144.9885 | 753.2538 | 463.9355 | 436.6513 | 429.3535
2145.9885 | 755.461 | 464.0522 | 436.4989 | 429.3936
2146.9885 | 759.2321 | 464.5427 | 436.3785 | 429.3034
2147.9885 | 759.9633 | 464.4151 | 436.5854 | 429.5409
2148.9885 | 749.2223 | 463.6904 | 437.1448 | 430.2213
2149.9885 | 745.0932 | 464.4041 | 437.5625 | 430.6582
2150.9885 | 729.2267 | 464.1403 | 438.0631 | 430.8811
2151.9885 | 732.7048 | 463.456 | 438.3676 | 431.2008
2152.9885 | 737.1206 | 463.5204 | 438.5624 | 432.271
2153.9885 | 735.1029 | 463.5818 | 438.2988 | 432.414
2154.9885 | 740.4895 | 463.6379 | 437.9473 | 432.454
2155.9885 | 736.9954 | 463.3642 | 438.1348 | 432.0677
2156.9885 | 738.2878 | 463.1861 | 437.9887 | 432.3564
2157.9885 | 738.6293 | 463.5324 | 437.4102 | 432.2779
2158.9885 | 744.345 | 464.0013 | 437.0143 | 431.6373
2159.9885 | 748.6835 | 464.4278 | 436.8833 | 431.1989
2160.9885 | 755.1962 | 464.5693 | 436.6561 | 431.0943
2161.9885 | 761.8957 | 464.7472 | 436.4807 | 431.1255
2162.9885 | 769.0356 | 465.3377 | 436.3749 | 431.1158
2163.9885 | 774.5755 | 465.8605 | 436.3394 | 431.4348
2164.9885 | 771.0345 | 466.0963 | 436.5847 | 431.6128
2165.9885 | 771.5675 | 466.4653 | 436.8554 | 431.9298
2166.9885 | 778.8989 | 467.1375 | 437.0109 | 432.6697
2167.9885 | 783.8448 | 467.4694 | 436.9827 | 432.9334
2168.9885 | 781.3481 | 468.0538 | 437.0375 | 433.2997
2169.9885 | 771.1485 | 468.2269 | 437.1036 | 433.0308
2170.9885 | 767.0752 | 468.0536 | 437.2753 | 433.0645
2171.9885 | 770.0514 | 468.6245 | 437.2666 | 432.9281
2172.9885 | 769.3881 | 468.8722 | 437.3973 | 432.4835
2173.9885 | 773.8277 | 469.8181 | 437.5532 | 432.3038
2174.9885 | 759.7808 | 469.9914 | 437.7316 | 432.5357
2175.9885 | 762.4717 | 470.1052 | 438.3734 | 432.0611
2176.9885 | 766.5865 | 470.2474 | 438.6502 | 431.7335
2177.9885 | 765.1431 | 469.8762 | 438.8683 | 431.6867
2178.9885 | 761.9058 | 470.2869 | 438.8018 | 431.8356
2179.9885 | 755.7479 | 470.5857 | 438.7277 | 431.6892
2180.9885 | 743.4621 | 470.975 | 438.7417 | 431.5835
2181.9885 | 749.1029 | 471.4919 | 438.8137 | 431.4128
2182.9885 | 744.4952 | 471.6645 | 439.4833 | 431.1755
2183.9885 | 742.2156 | 472.0433 | 440.0725 | 431.2316
2184.9885 | 738.6423 | 472.1786 | 440.8044 | 431.0041
2185.9885 | 737.899 | 472.2235 | 441.1583 | 430.9317
2186.9885 | 734.2476 | 473.3949 | 441.3536 | 431.5138
2187.9885 | 740.8533 | 473.5024 | 441.6407 | 432.1261
2188.9885 | 750.6183 | 474.0892 | 441.7552 | 432.1651
2189.9885 | 747.7214 | 474.6722 | 441.6164 | 432.0466
2190.9885 | 744.3136 | 475.4582 | 441.6818 | 431.4467
2191.9885 | 747.9339 | 476.6883 | 442.3464 | 431.1481
2192.9885 | 754.0522 | 476.8216 | 442.9973 | 431.4023
2193.9885 | 759.374 | 476.7394 | 444.21 | 431.9859
2194.9885 | 762.2657 | 476.9129 | 445.1952 | 432.5188
2195.9885 | 760.9384 | 477.1137 | 445.6359 | 432.9629
2196.9885 | 767.9482 | 477.1418 | 445.4924 | 433.565
2197.9885 | 775.7735 | 477.4264 | 445.8217 | 434.416
2198.9885 | 781.2681 | 476.3725 | 446.4492 | 434.895
2199.9885 | 774.2395 | 476.6693 | 446.1446 | 435.6439
2200.9885 | 774.7789 | 476.2454 | 445.8576 | 435.6525
2201.9885 | 771.7487 | 476.2828 | 445.968 | 435.822
2202.9885 | 771.4726 | 477.2185 | 446.1329 | 435.9695
2203.9885 | 773.3101 | 476.742 | 446.1688 | 436.4992
2204.9885 | 779.0567 | 477.6713 | 446.3409 | 437.0024
2205.9885 | 773.7559 | 478.1434 | 446.5043 | 437.501
2206.9885 | 769.86 | 478.7038 | 447.1814 | 438.1119
2207.9885 | 770.4387 | 479.3224 | 447.4742 | 438.7191
2208.9885 | 770.8673 | 479.5443 | 447.7219 | 439.5917
2209.9885 | 768.875 | 480.5743 | 447.9415 | 440.3751
2210.9885 | 769.8046 | 480.8465 | 447.9307 | 440.7658
2211.9885 | 769.9544 | 480.4305 | 447.7924 | 441.4162
2212.9885 | 760.083 | 480.398 | 447.7352 | 441.2636
2213.9885 | 756.6029 | 480.5173 | 447.9965 | 441.5031
2214.9885 | 761.6757 | 480.3011 | 448.019 | 441.7895
2215.9885 | 761.0974 | 480.4331 | 448.0501 | 441.7489
2216.9885 | 762.4977 | 480.3084 | 448.3101 | 441.2547
2217.9885 | 763.8797 | 480.2257 | 447.9636 | 440.458
2218.9885 | 759.429 | 480.7527 | 447.6531 | 440.2211
2219.9885 | 756.5028 | 480.5377 | 447.2772 | 439.6132
2220.9885 | 768.495 | 480.7785 | 446.9253 | 439.0445
2221.9885 | 773.1745 | 480.55 | 446.884 | 438.454
2222.9885 | 778.2231 | 480.6386 | 447.0667 | 438.0675
2223.9885 | 778.2451 | 481.9393 | 447.2203 | 437.717
2224.9885 | 778.8508 | 482.8878 | 448.0215 | 437.9006
2225.9885 | 775.6271 | 483.5968 | 448.2871 | 438.7313
2226.9885 | 771.8857 | 484.3586 | 447.925 | 439.6518
2227.9885 | 773.9754 | 484.4141 | 447.762 | 439.9775
2228.9885 | 771.167 | 485.0531 | 447.5648 | 440.2083
2229.9885 | 760.884 | 484.4788 | 447.0866 | 440.3181
2230.9885 | 757.7159 | 484.4168 | 446.9799 | 439.8573
2231.9885 | 753.6564 | 484.5589 | 446.9312 | 439.6004
2232.9885 | 745.8324 | 484.7276 | 447.0168 | 439.7996
2233.9885 | 750.6371 | 483.9737 | 447.1865 | 439.6125
2234.9885 | 751.1813 | 483.5394 | 447.6996 | 440.3993
2235.9885 | 751.4408 | 483.0637 | 448.6736 | 441.927
2236.9885 | 753.5944 | 482.914 | 448.7454 | 441.9292
2237.9885 | 756.1955 | 483.0265 | 449.0683 | 441.9045
2238.9885 | 751.2817 | 483.0618 | 448.9485 | 441.5352
2239.9885 | 756.2312 | 483.238 | 448.7579 | 440.6687
2240.9885 | 756.1035 | 484.0992 | 448.5415 | 440.5513
2241.9885 | 757.2546 | 484.7526 | 448.9927 | 440.3415
2242.9885 | 751.2289 | 484.8533 | 449.7226 | 440.9189
2243.9885 | 748.9526 | 485.0774 | 450.5686 | 441.5223
2244.9885 | 753.0879 | 485.2565 | 451.4939 | 441.8914
2245.9885 | 757.5776 | 485.476 | 451.8688 | 442.2495
2246.9885 | 757.7165 | 486.244 | 452.1754 | 442.9757
2247.9885 | 758.9714 | 486.9914 | 453.3053 | 443.6087
2248.9885 | 769.1512 | 486.9933 | 453.591 | 444.1674
2249.9885 | 762.2137 | 487.8584 | 453.7769 | 444.1954
2250.9885 | 753.4916 | 487.8474 | 454.0321 | 444.2287
2251.9885 | 757.0186 | 488.3828 | 454.4651 | 444.425
2252.9885 | 754.5358 | 489.3045 | 455.7272 | 444.2766
2253.9885 | 758.1002 | 490.2614 | 456.1835 | 445.1259
2254.9885 | 754.7773 | 490.7772 | 456.4503 | 445.5374
2255.9885 | 754.6427 | 491.9024 | 457.1719 | 446.1842
2256.9885 | 753.156 | 492.0748 | 457.7507 | 446.2315
2257.9885 | 743.8422 | 491.973 | 458.1819 | 446.7043
2258.9885 | 741.6884 | 492.5725 | 458.1337 | 447.4147
2259.9885 | 741.0138 | 492.4414 | 457.8555 | 447.4175
2260.9885 | 742.1101 | 492.4697 | 458.2282 | 447.436
2261.9885 | 741.9103 | 493.5669 | 458.9084 | 447.2537
2262.9885 | 740.3921 | 493.0273 | 458.8331 | 448.9773
2263.9885 | 738.4653 | 493.0206 | 458.7525 | 448.4953
2264.9885 | 733.9744 | 492.8519 | 458.2083 | 449.3299
2265.9885 | 734.9938 | 493.5368 | 458.2946 | 449.0247
2266.9885 | 733.5466 | 493.7637 | 458.1685 | 448.6302
2267.9885 | 726.904 | 494.2245 | 458.2204 | 448.7425
2268.9885 | 723.1229 | 493.8154 | 458.2263 | 448.7221
2269.9885 | 725.0007 | 494.3561 | 458.6323 | 448.8211
2270.9885 | 727.5651 | 495.2986 | 459.3362 | 449.0367
2271.9885 | 736.0222 | 495.4047 | 460.075 | 449.9177
2272.9885 | 741.7113 | 495.9157 | 460.7221 | 450.3307
2273.9885 | 750.0261 | 495.3428 | 460.8481 | 450.5677
2274.9885 | 752.8415 | 495.6273 | 461.5217 | 451.4878
2275.9885 | 749.9197 | 496.7073 | 462.6852 | 451.358
2276.9885 | 748.6905 | 497.6853 | 464.5537 | 451.7587
2277.9885 | 749.3722 | 497.8053 | 464.599 | 451.722
2278.9885 | 754.9643 | 498.4212 | 465.2559 | 451.8236
2279.9885 | 751.5985 | 497.3864 | 464.8476 | 452.4289
2280.9885 | 742.2625 | 497.8364 | 464.8287 | 452.3743
2281.9885 | 739.399 | 497.2563 | 464.8548 | 452.3264
2282.9885 | 741.1533 | 497.1722 | 464.8975 | 452.2516
2283.9885 | 747.7666 | 497.6626 | 465.6654 | 451.815
2284.9885 | 756.7759 | 498.1693 | 465.9313 | 451.2999
2285.9885 | 762.6038 | 498.3386 | 465.6282 | 451.132
2286.9885 | 772.8852 | 498.4138 | 465.1894 | 450.992
2287.9885 | 767.3626 | 499.8183 | 464.7068 | 451.3128
2288.9885 | 768.1159 | 500.0193 | 465.4567 | 451.7032
2289.9885 | 779.3473 | 500.9218 | 466.1425 | 451.6692
2290.9885 | 788.3832 | 501.1433 | 465.8156 | 451.9583
2291.9885 | 789.3098 | 501.6407 | 466.0657 | 451.7509
2292.9885 | 790.2568 | 502.3932 | 467.1925 | 451.6989
2293.9885 | 790.9497 | 503.102 | 468.1869 | 452.2926
2294.9885 | 798.5498 | 503.096 | 468.4242 | 453.191
2295.9885 | 795.6394 | 503.6167 | 468.5655 | 453.4568
2296.9885 | 789.1209 | 503.5572 | 468.4292 | 453.6703
2297.9885 | 788.518 | 504.0481 | 468.7015 | 454.4877
2298.9885 | 786.1341 | 504.7271 | 469.335 | 454.4909
2299.9885 | 783.6362 | 505.5819 | 470.1467 | 454.8386
2300.9885 | 781.6549 | 505.3668 | 470.0711 | 454.851
2301.9885 | 774.4006 | 504.7187 | 469.6224 | 454.9474
2302.9885 | 774.4954 | 505.6797 | 470.1642 | 454.7365
2303.9885 | 773.6435 | 505.9259 | 470.338 | 455.1154
2304.9885 | 770.7671 | 505.5289 | 470.3321 | 456.0622
2305.9885 | 772.6204 | 505.5154 | 470.4731 | 456.5753
2306.9885 | 777.6685 | 506.4138 | 471.0135 | 456.6925
2307.9885 | 780.1673 | 506.0221 | 470.3302 | 457.2986
2308.9885 | 779.6829 | 506.3834 | 470.8086 | 457.4406
2309.9885 | 776.3653 | 506.737 | 470.978 | 456.8344
2310.9885 | 769.957 | 507.951 | 471.7714 | 457.2072
2311.9885 | 765.5121 | 507.9852 | 471.5204 | 457.6322
2312.9885 | 766.1584 | 507.572 | 471.7411 | 458.6545
2313.9885 | 761.9584 | 508.5613 | 472.2052 | 458.4747
2314.9885 | 755.5734 | 509.0919 | 471.8438 | 458.2411
2315.9885 | 746.6832 | 509.1404 | 471.7175 | 458.6995
2316.9885 | 750.7872 | 508.8471 | 471.9947 | 458.5055
2317.9885 | 751.1551 | 508.9237 | 472.0795 | 458.3382
2318.9885 | 750.0943 | 507.6148 | 471.155 | 458.859
2319.9885 | 747.5555 | 508.4678 | 471.4153 | 458.1057
2320.9885 | 752.6071 | 508.3822 | 471.0943 | 457.2183
2321.9885 | 748.5521 | 508.4793 | 470.599 | 456.9823
2322.9885 | 743.6738 | 510.122 | 471.5695 | 457.9988
2323.9885 | 741.7903 | 509.1481 | 471.5533 | 457.9539
2324.9885 | 745.0649 | 510.1556 | 472.5113 | 458.7062
2325.9885 | 743.7636 | 509.6488 | 471.8669 | 458.4407
2326.9885 | 739.7924 | 509.6078 | 471.7831 | 458.2238
2327.9885 | 749.1986 | 510.724 | 472.4147 | 458.0719
2328.9885 | 749.5233 | 510.17 | 471.4877 | 458.5026
2329.9885 | 748.727 | 511.9755 | 472.922 | 458.3965
2330.9885 | 738.8794 | 513.6883 | 474.4101 | 458.6816
2331.9885 | 732.4146 | 514.2097 | 474.8434 | 458.7021
2332.9885 | 733.8887 | 515.1702 | 476.8744 | 459.6814
2333.9885 | 730.18 | 513.5584 | 475.6474 | 459.3277
2334.9885 | 728.3355 | 512.8146 | 474.9849 | 458.7759
2335.9885 | 733.7532 | 513.7809 | 475.3466 | 458.5022
2336.9885 | 737.6266 | 512.9795 | 474.8856 | 458.8295
2337.9885 | 733.649 | 513.9723 | 475.997 | 459.2078
2338.9885 | 731.868 | 515.5805 | 476.6908 | 459.5188
2339.9885 | 729.8069 | 515.0344 | 476.0448 | 459.9384
2340.9885 | 733.5487 | 514.7434 | 475.4351 | 460.7898
2341.9885 | 736.2294 | 514.0944 | 474.8101 | 460.4517
2342.9885 | 734.538 | 515.3245 | 475.1645 | 460.4176
2343.9885 | 723.1671 | 516.6087 | 475.2884 | 460.0947
2344.9885 | 714.7836 | 516.1894 | 474.8459 | 460.225
2345.9885 | 719.322 | 515.6083 | 474.9552 | 460.4283
2346.9885 | 723.012 | 514.9539 | 474.5993 | 460.9174
2347.9885 | 724.8531 | 515.7525 | 475.092 | 460.5309
2348.9885 | 716.1789 | 516.6056 | 476.0834 | 460.9855
2349.9885 | 731.5502 | 517.8405 | 478.0187 | 461.1438
2350.9885 | 733.4973 | 518.1455 | 478.5207 | 461.8115
2351.9885 | 737.8029 | 517.3829 | 477.7592 | 462.3807
2352.9885 | 731.5305 | 518.1885 | 478.0513 | 462.4662
2353.9885 | 724.3689 | 519.6424 | 479.5342 | 462.9719
2354.9885 | 733.0349 | 519.8287 | 480.5652 | 463.928
2355.9885 | 738.8671 | 518.6668 | 480.1569 | 463.7704
2356.9885 | 740.2727 | 518.8843 | 480.3276 | 464.349
2357.9885 | 736.3651 | 519.6343 | 480.7091 | 465.1163
2358.9885 | 732.4161 | 518.0364 | 479.5267 | 465.333
2359.9885 | 742.4362 | 517.6885 | 478.9565 | 465.069
2360.9885 | 740.272 | 519.5482 | 480.3354 | 465.4146
2361.9885 | 731.6732 | 519.5244 | 480.1698 | 465.6362
2362.9885 | 717.2784 | 520.8683 | 481.6689 | 466.0372
2363.9885 | 706.9961 | 521.0148 | 482.0759 | 467.0412
2364.9885 | 711.2501 | 520.7073 | 482.4233 | 467.4043
2365.9885 | 714.1706 | 519.6915 | 481.6346 | 467.4351
2366.9885 | 716.0249 | 519.9514 | 481.4592 | 466.7662
2367.9885 | 724.9455 | 519.4079 | 481.1048 | 467.2424
2368.9885 | 731.033 | 520.0644 | 481.2121 | 467.5484
2369.9885 | 734.3515 | 518.8408 | 479.9416 | 467.126
2370.9885 | 735.9248 | 520.2264 | 481.0994 | 467.294
2371.9885 | 731.0427 | 521.2594 | 481.8348 | 468.3032
2372.9885 | 718.6485 | 522.2543 | 482.6214 | 468.7
2373.9885 | 713.1563 | 521.8128 | 482.8938 | 468.9366
2374.9885 | 713.6786 | 520.6927 | 482.0189 | 468.7556
2375.9885 | 721.1817 | 520.4065 | 481.8886 | 468.9025
2376.9885 | 730.4137 | 521.7574 | 482.8365 | 469.6328
2377.9885 | 736.6011 | 521.8611 | 482.832 | 469.5086
2378.9885 | 744.1389 | 521.7496 | 482.9978 | 469.8682
2379.9885 | 742.1689 | 523.8168 | 484.2585 | 469.9818
2380.9885 | 735.8992 | 524.2106 | 485.334 | 470.8738
2381.9885 | 732.3742 | 524.2647 | 485.5752 | 470.6912
2382.9885 | 732.341 | 523.3538 | 484.9499 | 470.25
2383.9885 | 744.8946 | 525.1548 | 486.6184 | 470.8138
2384.9885 | 745.9 | 524.0238 | 486.4888 | 471.1772
2385.9885 | 750.8036 | 524.0393 | 487.5143 | 471.3205
2386.9885 | 754.5914 | 523.8544 | 487.2136 | 470.8148
2387.9885 | 759.9884 | 524.2591 | 487.5081 | 470.5555
2388.9885 | 764.2608 | 523.356 | 486.8913 | 470.9317
2389.9885 | 766.6425 | 523.9192 | 487.6702 | 471.455
2390.9885 | 768.9578 | 524.185 | 487.6236 | 471.815
2391.9885 | 770.7665 | 523.4193 | 486.9096 | 471.1557
2392.9885 | 765.4614 | 523.774 | 486.6878 | 470.4531
2393.9885 | 759.8207 | 524.8461 | 486.8342 | 470.6381
2394.9885 | 753.0395 | 525.4344 | 486.926 | 471.3845
2395.9885 | 749.9658 | 526.3831 | 487.9715 | 471.9161
2396.9885 | 746.7841 | 525.9459 | 487.9078 | 471.6476
2397.9885 | 747.7635 | 525.4882 | 487.6764 | 472.0592
2398.9885 | 755.2699 | 524.2559 | 486.8407 | 471.7966
2399.9885 | 750.5748 | 524.6744 | 487.1858 | 471.4824
2400.9885 | 752.1188 | 524.6348 | 487.6222 | 470.6668
2401.9885 | 749.9367 | 525.2273 | 488.5944 | 471.753
2402.9885 | 757.0147 | 525.0635 | 489.0539 | 471.5986
2403.9885 | 753.8114 | 525.6495 | 489.6067 | 471.8392
2404.9885 | 761.3342 | 524.4785 | 489.039 | 472.5971
2405.9885 | 757.0358 | 525.0557 | 489.483 | 473.1759
2406.9885 | 750.7021 | 524.8992 | 489.5482 | 473.1193
2407.9885 | 751.7126 | 524.7059 | 489.632 | 473.391
2408.9885 | 743.9212 | 524.9131 | 489.3158 | 473.5039
2409.9885 | 739.2918 | 524.9087 | 490.2687 | 475.4725
2410.9885 | 737.7623 | 525.0975 | 490.9838 | 475.3561
2411.9885 | 740.1009 | 525.8904 | 491.2514 | 476.0091
2412.9885 | 750.5153 | 524.876 | 491.2645 | 475.581
2413.9885 | 751.2059 | 524.909 | 491.1716 | 475.0862
2414.9885 | 750.8653 | 525.459 | 491.9735 | 475.5378
2415.9885 | 744.588 | 526.0165 | 491.9845 | 475.3809
2416.9885 | 748.6335 | 524.6774 | 490.6279 | 476.0097
2417.9885 | 756.0079 | 526.3233 | 491.4991 | 476.3253
2418.9885 | 760.9745 | 526.998 | 491.7239 | 476.426
2419.9885 | 753.9263 | 526.5227 | 491.4288 | 476.0055
2420.9885 | 749.1809 | 527.2948 | 491.5212 | 475.9415
2421.9885 | 746.9417 | 526.8435 | 490.7849 | 475.9431
2422.9885 | 747.5811 | 525.5263 | 489.0496 | 475.119
2423.9885 | 741.3316 | 525.8198 | 489.1708 | 475.4382
2424.9885 | 746.0803 | 526.4456 | 490.1092 | 476.8598
2425.9885 | 750.6194 | 526.5347 | 490.1647 | 476.871
2426.9885 | 747.8822 | 526.3048 | 490.265 | 476.3609
2427.9885 | 753.1326 | 526.9509 | 490.5948 | 475.7447
2428.9885 | 749.9505 | 527.0482 | 490.3382 | 475.4418
2429.9885 | 743.3657 | 526.5824 | 489.8156 | 475.2829
2430.9885 | 742.9736 | 526.8503 | 489.356 | 475.3162
2431.9885 | 738.6211 | 527.6873 | 489.6161 | 475.2679
2432.9885 | 730.1574 | 527.697 | 490.254 | 476.2044
2433.9885 | 724.603 | 527.8014 | 490.5419 | 477.7908
2434.9885 | 737.2727 | 527.6901 | 491.2733 | 477.1938
2435.9885 | 733.0646 | 528.6349 | 492.2759 | 476.7906
2436.9885 | 727.9667 | 527.1679 | 491.5023 | 477.1265
2437.9885 | 733.8797 | 526.8836 | 490.8181 | 476.5024
2438.9885 | 735.331 | 526.6088 | 491.0788 | 476.7602
2439.9885 | 719.8511 | 526.4395 | 490.8211 | 476.9993
2440.9885 | 716.5927 | 527.0347 | 491.2017 | 477.1232
2441.9885 | 716.1816 | 527.2366 | 490.7776 | 476.7463
2442.9885 | 714.8791 | 526.7944 | 490.9199 | 476.5781
2443.9885 | 719.2527 | 526.6275 | 490.8506 | 476.3313
2444.9885 | 724.8152 | 527.4842 | 491.7758 | 475.9955
2445.9885 | 729.9417 | 529.1057 | 492.3989 | 476.1031
2446.9885 | 724.9739 | 528.2053 | 492.6016 | 477.4965
2447.9885 | 724.0158 | 529.0946 | 492.957 | 477.6628
2448.9885 | 720.0593 | 528.0795 | 492.7593 | 477.2976
2449.9885 | 722.2998 | 529.4429 | 493.8558 | 477.2813
2450.9885 | 712.9303 | 530.262 | 494.062 | 478.2102
2451.9885 | 707.789 | 529.5549 | 493.6369 | 477.5071
2452.9885 | 708.6847 | 528.492 | 492.3717 | 477.0323
2453.9885 | 714.5816 | 530.3127 | 493.1273 | 477.6905
2454.9885 | 719.197 | 528.1961 | 491.8099 | 477.99
2455.9885 | 720.7744 | 528.9624 | 492.0618 | 478.2597
2456.9885 | 724.8515 | 528.5469 | 492.2658 | 477.7998
2457.9885 | 725.4482 | 529.1851 | 492.6013 | 477.8635
2458.9885 | 731.3693 | 529.7145 | 493.0199 | 478.039
2459.9885 | 729.6641 | 528.934 | 492.433 | 477.6744
2460.9885 | 728.9757 | 529.0904 | 492.4774 | 477.8467
2461.9885 | 721.1508 | 532.295 | 493.7017 | 479.2829
2462.9885 | 730.0018 | 531.9524 | 493.6203 | 479.4727
2463.9885 | 735.7139 | 532.1951 | 494.0237 | 480.3436
2464.9885 | 735.2578 | 533.0581 | 495.0845 | 479.7171
2465.9885 | 728.0364 | 532.43 | 495.7763 | 479.6582
2466.9885 | 724.6175 | 530.3538 | 494.4048 | 479.4709
2467.9885 | 733.1246 | 529.4948 | 493.911 | 478.8973
2468.9885 | 738.5644 | 530.547 | 493.3949 | 479.4025
2469.9885 | 727.867 | 530.6082 | 493.7991 | 480.1459
2470.9885 | 719.2349 | 531.3682 | 493.7963 | 480.6007
2471.9885 | 717.0745 | 531.9863 | 493.2433 | 480.1847
2472.9885 | 719.3866 | 532.4835 | 493.9161 | 480.5846
2473.9885 | 728.5454 | 532.0793 | 493.7305 | 480.4711
2474.9885 | 730.6248 | 530.7406 | 492.4607 | 480.5873
2475.9885 | 720.3567 | 532.3073 | 493.4534 | 480.0161
2476.9885 | 719.9854 | 533.1913 | 493.3997 | 480.3039
2477.9885 | 720.4709 | 532.7474 | 493.4177 | 480.3576
2478.9885 | 720.4949 | 533.6705 | 493.7302 | 480.5931
2479.9885 | 716.5576 | 532.3379 | 493.0427 | 480.2188
2480.9885 | 714.0215 | 530.9696 | 492.6124 | 480.638
2481.9885 | 721.9208 | 531.6522 | 492.9552 | 480.5913
2482.9885 | 719.4375 | 531.6817 | 492.8192 | 480.7212
2483.9885 | 724.0665 | 530.5912 | 493.0185 | 481.8097
2484.9885 | 727.0665 | 530.2725 | 492.8606 | 481.6245
2485.9885 | 729.513 | 530.0961 | 492.8725 | 482.8963
2486.9885 | 727.9 | 530.1646 | 492.9097 | 482.9026
2487.9885 | 734.3163 | 530.7205 | 493.5012 | 482.8064
2488.9885 | 734.4868 | 531.4273 | 493.4009 | 483.2133
2489.9885 | 732.9456 | 529.8285 | 492.6538 | 483.2508
2490.9885 | 733.2705 | 528.3725 | 491.6862 | 482.739
2491.9885 | 736.3003 | 528.8552 | 492.1218 | 482.5382
2492.9885 | 736.8509 | 530.9245 | 492.7861 | 482.8124
2493.9885 | 734.782 | 532.2087 | 493.6898 | 482.6908
2494.9885 | 730.9177 | 531.3596 | 492.9437 | 482.7731
2495.9885 | 733.4597 | 530.1749 | 492.4526 | 482.585