## Test Conditions
DESIREE-FIRE Intermediate Scale Test Number 7 - Circuit Simulator Data Only
Test Date: | 2010-03-09
DCSim DAQ Start Time | 13:14
DCSim Time for Synchronization | 13:16
Heat Source Synchronization | 0:00 | hour:minutes:seconds
Heat Source DAQ Start Time | 13:15
Fire Time | 14:00
Offset | 0:46 | hour:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 2760 | seconds
Heat Source Offset | 0:45 | hour:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 2695 | seconds
Heat Source Stop Time | 14:40
Test Duration | 0:40 | hour:minutes:seconds
| 2400 | seconds
CT500 turns | 2 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 turns | 5 | 1 or 5
Pre-Test Baseline: | Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit number | Cable Type |  | Cable TC channel | Air TC Channel
MOV 1 | PE/PVC, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 1 represents the air temperature in the middle of the tray located in B Position. It is labeled as "B Position - Middle".
MOV 2 | PE/PVC, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 8, 9, and 10 represents the air temperature 3', 5', and 7' down the tray located in D Position. These are labeled as "D Position - 3'", "D Position - Middle", " D Position - 7'", respectively.
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | MOV-1_CT500 | MOV-1a_CT35_1_P | MOV-1a_CT35_2_N | MOV-1b_CT35_1_G | MOV-1b_CT35_2_R | MOV-1b_CT35_3_YO | MOV-1b_CT35_4_YC | MOV-2_CT500 | MOV-2a_CT35_1_P | MOV-2a_CT35_2_N | MOV-2b_CT35_1_G | MOV-2b_CT35_2_R | MOV-2b_CT35_3_YO | 2b_CT35_4_YC1 | MOV-1a_VT7_1_SP | MOV-1a_VTU_1_P | MOV-1a_VTU_2_N | MOV-1b_VT7_1_G | MOV-1b_VT7_2_R | MOV-1b_VT7_3_YO1 | MOV-1b_VT7_4_YC1 | MOV-2a_VT7_1_SP | MOV-2a_VTU_1_P | MOV-2a_VTU_2_N | MOV-2b_VT7_1_G | MOV-2b_VT7_2_R | 2b_VT7_3_YO1 | MOV-2b_VT7_4_YC1 | {MOV1} V(N) - V(Batt -) | {MOV1} V(P) - V(Batt +) | {MOV1} V(G) - V(Batt +) | {MOV1} V(R) - V(Batt -) | {MOV1} V(YC1) - V(Batt -) | {MOV1} V(YO1) - V(Batt -) | {MOV1} V(YC1) - V(N) | {MOV1} V(YO1) - V(N) | {MOV2} V(N) - V(Batt -) | {MOV2} V(P) - V(Batt +) | {MOV2} V(G) - V(Batt +) | {MOV2} V(R) - V(Batt -) | {MOV2} V(YC1) - V(Batt -) | {MOV2} V(YO1) - V(Batt -) | {MOV2} V(YC1) - V(N) | {MOV2} V(YO1) - V(N) | {MOV-1} V(R) - V(N) | {MOV-1} V(G) - V(N) | {MOV-2} V(R) - V(N) | {MOV-2} V(G) - V(N) | {MOV-1} V(P) - V(N) | {MOV-2} V(P) - V(N) | {MOV-1} V(P) - V(Batt -) | {MOV-2} V(P) - V(Batt -) | {MOV-1} V(N) - V(Batt +) | {MOV-2} V(N) - V(Batt +) | {MOV-1} V(G) - V(Batt -) | {MOV2} V(G) - V(Batt-) | {MOV1} V(SP) - V(Batt -) | {MOV2} V(SP) - V(Batt -)
-0.8125 | 121.9803 | -60.9421 | 60.9146 | -0.0036622 | 0.0020593 | 0.066736 | 0.066905 | -0.0023306 | -0.004251 | 0.0028347 | 0.013702 | 0.0045673 | 0.070545 | 0.062965 | -0.0062913 | 0.012403 | -0.0034159 | -0.091553 | 60.9787 | -61.0565 | 60.8505 | -60.704 | -61.0931 | -61.1206 | -0.054932 | 60.9146 | -61.0199 | 60.878 | -60.9375 | -60.9421 | -60.9192 | -0.11444 | 0.064087 | -0.064087 | 0.23804 | -0.17853 | -0.15106 | -0.064086 | -0.036621 | -0.077819 | 0 | -0.036621 | 0.004578 | 0.022889 | 0 | 0.10071 | 0.077819 | 0.35248 | 121.907 | 0.082397 | 121.8979 | 122.0352 | 121.9345 | 121.9208 | 121.8567 | -121.9711 | -121.9345 | 121.7926 | 121.8201 | 60.8505 | 60.8871
0.9375 | 122.0352 | -60.9192 | 60.9375 | -0.0036622 | 0.0050501 | 0.065668 | 0.062205 | -0.0059622 | -0.00083304 | -0.0010105 | -0.0015565 | 0.00072206 | 0.069263 | 0.061043 | -0.0052231 | 0.014325 | -0.0032021 | -0.022888 | 60.878 | -61.0016 | 60.9924 | -60.5942 | -61.0062 | -61.0565 | 0.054932 | 60.8414 | -60.9558 | 60.965 | -60.8276 | -60.8368 | -60.8414 | -0.082398 | -0.059509 | 0.054932 | 0.32501 | -0.13733 | -0.086976 | -0.054932 | -0.004578 | -0.036622 | -0.09613 | 0.027466 | 0.091552 | 0.077819 | 0.082397 | 0.11444 | 0.11902 | 0.40741 | 121.994 | 0.12817 | 121.9208 | 121.8796 | 121.7972 | 121.7972 | 121.7606 | -121.9391 | -121.8933 | 121.9116 | 121.8842 | 60.8963 | 60.9741
2.6094 | 122.0718 | -60.8917 | 60.9055 | 0.019226 | 0.0039819 | 0.068018 | 0.064128 | -0.0012624 | -0.002542 | 5.7688e-05 | 0.010651 | 0.0026447 | 0.067554 | 0.065315 | -0.0024461 | 0.016248 | 0.0021383 | -0.07782 | 60.9375 | -61.0474 | 60.9283 | -60.6445 | -61.0519 | -61.0931 | -0.032043 | 60.8093 | -60.965 | 60.9512 | -60.8551 | -60.8643 | -60.8368 | -0.15564 | 0.032043 | 0.022888 | 0.24719 | -0.20142 | -0.16022 | -0.045777 | -0.004578 | -0.073242 | -0.096131 | 0.045776 | 0.036621 | 0.054932 | 0.027466 | 0.12817 | 0.10071 | 0.40283 | 121.9757 | 0.10986 | 121.9162 | 121.9849 | 121.7743 | 121.8292 | 121.7011 | -121.9528 | -121.8704 | 121.8201 | 121.843 | 60.8139 | 60.8597
4.3438 | 121.9666 | -60.9375 | 60.9375 | -0.011291 | 0.0050501 | 0.066949 | 0.064982 | -0.0023306 | -0.0016876 | -0.0012241 | -0.0015565 | 0.0032855 | 0.069263 | 0.062965 | -0.0039413 | 0.013257 | -0.0010659 | -0.091553 | 60.9604 | -61.0382 | 60.8597 | -60.7178 | -61.1206 | -61.1481 | -0.073242 | 60.878 | -60.9695 | 60.878 | -60.9375 | -60.9421 | -60.9192 | -0.10071 | 0.022888 | -0.07782 | 0.21973 | -0.21057 | -0.1831 | -0.10986 | -0.082397 | -0.032043 | -0.059509 | -0.059509 | 0 | 0.018311 | -0.004578 | 0.050354 | 0.027465 | 0.32043 | 121.8979 | 0.032043 | 121.8475 | 121.9986 | 121.8475 | 121.8979 | 121.8155 | -121.9757 | -121.907 | 121.7972 | 121.8155 | 60.8459 | 60.8643
6.0938 | 122.1222 | -60.9146 | 60.8826 | -0.0036622 | 0.0041955 | 0.066949 | 0.065623 | -0.00062165 | -0.00083304 | 0.0015531 | -0.0046081 | 0.00072206 | 0.069049 | 0.06617 | -0.00073705 | 0.013471 | -0.0023477 | -0.050354 | 60.8551 | -61.0107 | 60.9421 | -60.6491 | -61.0794 | -61.0886 | 0.050354 | 60.8093 | -60.9924 | 60.9924 | -60.8185 | -60.8414 | -60.8185 | -0.09613 | -0.027465 | 0.05951 | 0.2655 | -0.17395 | -0.1648 | -0.07782 | -0.068665 | -0.07782 | -0.073242 | 0.10986 | 0.096131 | 0.096131 | 0.073242 | 0.17395 | 0.15106 | 0.36163 | 121.9528 | 0.17395 | 121.9849 | 121.8658 | 121.8018 | 121.7697 | 121.7239 | -121.8933 | -121.875 | 121.8567 | 121.907 | 60.8643 | 60.965
7.8281 | 121.9894 | -60.9695 | 60.9238 | -0.011291 | 0.0063317 | 0.064813 | 0.067546 | 0.0045054 | -0.0021148 | -0.0035739 | -0.0046081 | 0.0032855 | 0.068409 | 0.056557 | -0.0024461 | 0.013471 | 0.0012839 | -0.12817 | 60.9055 | -61.0931 | 60.8185 | -60.8093 | -61.203 | -61.2213 | -0.11444 | 60.8322 | -61.0336 | 60.8459 | -60.9787 | -60.9924 | -60.9283 | -0.1236 | -0.01831 | -0.10529 | 0.16022 | -0.25177 | -0.23346 | -0.12817 | -0.10986 | -0.064087 | -0.091553 | -0.07782 | -0.009156 | 0.041198 | -0.022889 | 0.10529 | 0.041198 | 0.28381 | 121.9116 | 0.054931 | 121.8796 | 121.9986 | 121.8658 | 121.875 | 121.8018 | -122.0169 | -121.9574 | 121.788 | 121.8155 | 60.8414 | 60.8551
9.5469 | 122.0993 | -60.878 | 60.9375 | -0.0036622 | 0.0063317 | 0.066949 | 0.062632 | -0.0029714 | -0.002542 | -0.0022921 | -0.0015565 | 0.0013629 | 0.067127 | 0.065529 | -0.0026597 | 0.016034 | 0.00085667 | -0.027466 | 60.8871 | -61.0153 | 61.0016 | -60.5621 | -60.9924 | -61.0245 | 0.073242 | 60.8231 | -60.9375 | 61.0107 | -60.7727 | -60.791 | -60.8047 | -0.13733 | -0.050354 | 0.064087 | 0.31586 | -0.14648 | -0.11444 | -0.009155 | 0.022888 | -0.059509 | -0.11444 | 0.073242 | 0.10529 | 0.073242 | 0.086975 | 0.13275 | 0.14648 | 0.45319 | 122.0169 | 0.16479 | 121.9482 | 121.9025 | 121.7606 | 121.7651 | 121.7011 | -121.9528 | -121.875 | 121.8796 | 121.8887 | 60.8505 | 60.9512
11.2188 | 122.0261 | -60.9421 | 60.91 | 0.049744 | 0.0061181 | 0.065454 | 0.066905 | 0.0042918 | -0.0033966 | -0.00058311 | 0.010651 | 0.0032855 | 0.068195 | 0.066811 | -0.0030869 | 0.014539 | -0.0023477 | -0.027466 | 60.9283 | -61.0931 | 60.8963 | -60.6903 | -61.1069 | -61.1343 | -0.027466 | 60.8414 | -61.0291 | 60.8917 | -60.9009 | -60.9192 | -60.9055 | -0.15106 | 0.018311 | -0.013733 | 0.25177 | -0.19226 | -0.16479 | -0.041198 | -0.013733 | -0.086975 | -0.068664 | -0.01831 | 0.041199 | 0.036621 | 0.022889 | 0.1236 | 0.10986 | 0.40283 | 121.9894 | 0.12817 | 121.9208 | 122.0215 | 121.8704 | 121.8704 | 121.7834 | -122.0032 | -121.9391 | 121.8384 | 121.8338 | 60.9146 | 60.9146
12.9531 | 122.0718 | -60.8917 | 60.9055 | 0.042114 | 0.0029139 | 0.06994 | 0.066477 | 0.0027964 | -0.0016876 | 0.0013395 | 0.010651 | 0.0024311 | 0.072681 | 0.063393 | 0.0018265 | 0.014112 | -0.00021153 | -0.050354 | 60.91 | -61.0199 | 60.9833 | -60.5942 | -61.0474 | -61.0703 | 0.050354 | 60.8139 | -60.965 | 60.9558 | -60.8459 | -60.8459 | -60.8368 | -0.12817 | 0.004577 | 0.077819 | 0.29755 | -0.17853 | -0.15564 | -0.050354 | -0.027466 | -0.073242 | -0.091553 | 0.050354 | 0.045777 | 0.054932 | 0.045777 | 0.12817 | 0.11902 | 0.42572 | 122.0032 | 0.11902 | 121.9208 | 121.9299 | 121.7789 | 121.8018 | 121.7056 | -121.9254 | -121.8704 | 121.875 | 121.8475 | 60.8414 | 60.9421
14.625 | 122.0856 | -60.9146 | 60.878 | 0.0039673 | 0.0059045 | 0.066095 | 0.067118 | 0.001301 | -0.001474 | 0.00048489 | -0.010712 | 0.0028583 | 0.067768 | 0.060829 | 0.00075835 | 0.015821 | -0.0019205 | -0.07782 | 60.8734 | -61.0474 | 60.9467 | -60.6445 | -61.0886 | -61.0886 | 0.009155 | 60.7773 | -60.9741 | 60.997 | -60.8322 | -60.8505 | -60.8139 | -0.13275 | -0.004578 | 0.068664 | 0.27008 | -0.17395 | -0.17395 | -0.041199 | -0.041199 | -0.059509 | -0.10071 | 0.11902 | 0.082398 | 0.10071 | 0.064087 | 0.16022 | 0.1236 | 0.40283 | 121.994 | 0.14191 | 121.9711 | 121.9208 | 121.7514 | 121.788 | 121.6919 | -121.9254 | -121.8521 | 121.8613 | 121.9116 | 60.8368 | 60.9238
16.375 | 122.1085 | -60.8826 | 60.9009 | -0.0036622 | 0.0024865 | 0.066736 | 0.065196 | 0.00023275 | -0.0023284 | -0.0012241 | -0.0046081 | 0.0015765 | 0.067127 | 0.062324 | -0.0050095 | 0.015821 | -0.0029885 | -0.050354 | 60.9238 | -61.0016 | 60.9879 | -60.5713 | -60.9695 | -61.0199 | 0.059509 | 60.8139 | -60.9421 | 61.0062 | -60.7819 | -60.7864 | -60.7819 | -0.11902 | 0.022888 | 0.086975 | 0.31128 | -0.13733 | -0.086975 | -0.01831 | 0.032044 | -0.05951 | -0.086975 | 0.10529 | 0.10071 | 0.10071 | 0.09613 | 0.16022 | 0.15564 | 0.4303 | 121.9894 | 0.16022 | 121.9482 | 121.9254 | 121.756 | 121.8063 | 121.6965 | -121.9025 | -121.843 | 121.8704 | 121.8887 | 60.8322 | 60.9421
18.1094 | 122.0856 | -60.9055 | 60.8734 | -0.0036622 | 0.0044091 | 0.065668 | 0.066264 | 0.00066015 | -0.0012604 | 0.00091209 | -0.0015565 | 0.0043537 | 0.066272 | 0.068947 | -0.0011643 | 0.016034 | -0.0027749 | -0.10529 | 60.9009 | -61.0565 | 60.9055 | -60.6812 | -61.1069 | -61.1252 | -0.018311 | 60.7819 | -60.9924 | 60.965 | -60.8551 | -60.8597 | -60.8231 | -0.15106 | 0.027466 | 0.032044 | 0.22431 | -0.21973 | -0.20142 | -0.068664 | -0.050354 | -0.086975 | -0.091553 | 0.091553 | 0.050354 | 0.082398 | 0.045777 | 0.16937 | 0.13275 | 0.37537 | 121.962 | 0.13733 | 121.9574 | 121.9574 | 121.7743 | 121.8063 | 121.6873 | -121.9299 | -121.8658 | 121.8109 | 121.8704 | 60.8002 | 60.8871
19.8438 | 121.9986 | -60.9375 | 60.9009 | 0.011597 | 0.0061181 | 0.066522 | 0.064982 | -0.00040805 | -0.0029694 | -0.0022921 | -0.0015565 | 0.0049945 | 0.069049 | 0.061256 | -0.0022325 | 0.014539 | -0.0038431 | -0.036621 | 60.9238 | -61.0657 | 60.8734 | -60.6995 | -61.116 | -61.1526 | -0.018311 | 60.8322 | -60.9879 | 60.8917 | -60.9421 | -60.9604 | -60.9238 | -0.12817 | 0.022888 | -0.027466 | 0.23804 | -0.21515 | -0.17853 | -0.086975 | -0.050354 | -0.050354 | -0.068665 | -0.009155 | -0.004578 | 0.013733 | -0.022888 | 0.064087 | 0.027466 | 0.36621 | 121.9391 | 0.045776 | 121.8796 | 121.9894 | 121.8201 | 121.8613 | 121.7697 | -121.9666 | -121.8887 | 121.8109 | 121.8292 | 60.9009 | 60.9192
21.5312 | 122.0627 | -60.9329 | 60.878 | -0.011291 | 0.0050501 | 0.065881 | 0.067332 | -0.00062165 | 2.1362e-05 | -0.0012241 | 0.0014953 | 0.0032855 | 0.068836 | 0.062752 | -0.0022325 | 0.013471 | 0.0017111 | -0.12817 | 60.8917 | -61.0977 | 60.8643 | -60.7224 | -61.1343 | -61.1526 | -0.050354 | 60.7864 | -60.9879 | 60.9512 | -60.8871 | -60.8826 | -60.8551 | -0.1648 | 0.013733 | -0.013733 | 0.21057 | -0.21973 | -0.20142 | -0.054932 | -0.036621 | -0.054932 | -0.091553 | 0.073242 | 0.045776 | 0.077819 | 0.050354 | 0.13275 | 0.10529 | 0.37537 | 121.962 | 0.10071 | 121.9391 | 121.9894 | 121.7743 | 121.8246 | 121.7194 | -121.9757 | -121.8658 | 121.7972 | 121.8842 | 60.8047 | 60.8826
23.2812 | 121.9986 | -60.9604 | 60.9192 | 0.011597 | 0.0065453 | 0.071008 | 0.06605 | 0.0015146 | 0.00044856 | -0.0027195 | 0.0014953 | 0.0028583 | 0.067554 | 0.058479 | -0.0028733 | 0.015821 | -0.0023477 | -0.036621 | 60.9375 | -61.0748 | 60.91 | -60.6857 | -61.0977 | -61.1252 | 0.004578 | 60.7956 | -61.0016 | 60.9009 | -60.9283 | -60.9375 | -60.9009 | -0.11444 | 0.018311 | -0.009155 | 0.27466 | -0.16479 | -0.13733 | -0.050354 | -0.022888 | -0.041199 | -0.1236 | -0.01831 | 0.032043 | 0.059509 | 0.022888 | 0.10071 | 0.064087 | 0.3891 | 121.9849 | 0.073242 | 121.9025 | 122.0123 | 121.7972 | 121.8979 | 121.756 | -121.994 | -121.9208 | 121.8704 | 121.8613 | 60.9238 | 60.965
25.0156 | 121.9528 | -60.965 | 60.878 | -0.0036622 | 0.0059045 | 0.066736 | 0.065409 | 0.0055734 | 2.1362e-05 | -0.0018649 | -0.0015565 | 0.0020039 | 0.070118 | 0.058693 | -0.0013779 | 0.015821 | -0.00021153 | -0.10529 | 60.9146 | -61.0748 | 60.8047 | -60.8002 | -61.2167 | -61.2213 | -0.14648 | 60.8231 | -61.0245 | 60.8139 | -61.0245 | -61.0153 | -60.9558 | -0.10986 | 0.036621 | -0.073242 | 0.16479 | -0.25635 | -0.25177 | -0.14648 | -0.14191 | -0.059509 | -0.054932 | -0.064087 | -0.059509 | 0.009155 | -0.050354 | 0.068664 | 0.009155 | 0.27466 | 121.8796 | 0 | 121.8384 | 121.9894 | 121.8475 | 121.8796 | 121.788 | -121.9528 | -121.9025 | 121.7697 | 121.7789 | 60.8597 | 60.8185
26.6875 | 121.9849 | -60.9375 | 60.8963 | -0.011291 | 0.0031275 | 0.065881 | 0.064768 | 0.0042918 | 0.0010896 | 0.0013395 | -0.0015565 | 0.0039265 | 0.069904 | 0.056129 | -0.0013779 | 0.01518 | 0.0010703 | -0.13733 | 60.9009 | -61.084 | 60.8093 | -60.7636 | -61.1938 | -61.1801 | -0.11902 | 60.8139 | -61.0016 | 60.8597 | -60.9604 | -60.9833 | -60.9192 | -0.14648 | 0.004578 | -0.086975 | 0.17395 | -0.24262 | -0.25635 | -0.096131 | -0.10986 | -0.064087 | -0.082397 | -0.036621 | -0.022888 | 0.018311 | -0.045776 | 0.082398 | 0.018311 | 0.32043 | 121.8933 | 0.041199 | 121.8613 | 121.9849 | 121.8155 | 121.8384 | 121.7514 | -121.9803 | -121.8979 | 121.7468 | 121.7972 | 60.8002 | 60.8185
28.4219 | 122.0398 | -60.8871 | 60.9238 | 0.019226 | 0.0039819 | 0.068445 | 0.063059 | -0.002117 | -0.0012604 | 5.7688e-05 | 0.0014953 | 0.0026447 | 0.068622 | 0.06852 | -0.0035141 | 0.013898 | 0.0014975 | -0.09613 | 60.9421 | -61.0291 | 60.9238 | -60.6445 | -61.0611 | -61.0703 | -0.054932 | 60.7956 | -60.9741 | 60.9421 | -60.8551 | -60.8551 | -60.8276 | -0.14191 | 0.018311 | 0 | 0.24262 | -0.1831 | -0.17395 | -0.041198 | -0.032043 | -0.086975 | -0.12817 | 0.018311 | 0.032043 | 0.059509 | 0.032043 | 0.14648 | 0.11902 | 0.38452 | 121.9528 | 0.11902 | 121.9162 | 121.9711 | 121.7697 | 121.8292 | 121.6827 | -121.9528 | -121.8979 | 121.8109 | 121.8292 | 60.791 | 60.8322
30.0938 | 121.962 | -60.9375 | 60.8826 | -0.011291 | 0.0052637 | 0.066522 | 0.067118 | 0.0010874 | -0.0010468 | -0.0010105 | -0.0046081 | 0.0026447 | 0.068195 | 0.063179 | -0.0011643 | 0.016462 | -0.0012795 | -0.13275 | 60.9055 | -61.0748 | 60.8093 | -60.7819 | -61.1938 | -61.1984 | -0.12817 | 60.8047 | -60.9924 | 60.8459 | -60.9879 | -60.997 | -60.9192 | -0.13733 | 0.022889 | -0.073242 | 0.15564 | -0.26093 | -0.25635 | -0.1236 | -0.11902 | -0.054932 | -0.077819 | -0.036621 | -0.050354 | 0.018311 | -0.059509 | 0.073243 | -0.004577 | 0.29297 | 121.8842 | 0.004578 | 121.8384 | 121.9803 | 121.7972 | 121.843 | 121.7422 | -121.9574 | -121.875 | 121.7468 | 121.7834 | 60.8047 | 60.8093
31.8594 | 121.9391 | -60.9375 | 60.9421 | 0.0039673 | 0.0056909 | 0.066309 | 0.06605 | -0.0042532 | -0.0033966 | -0.0018649 | -0.0015565 | 0.0026447 | 0.068622 | 0.057197 | -0.0056503 | 0.013898 | -0.0044839 | -0.07782 | 60.9192 | -61.0291 | 60.878 | -60.704 | -61.0886 | -61.1298 | -0.068665 | 60.8505 | -60.9879 | 60.8643 | -60.9283 | -60.9238 | -60.8963 | -0.091553 | -0.022889 | -0.064087 | 0.23346 | -0.19226 | -0.15106 | -0.10071 | -0.059509 | -0.050354 | -0.091553 | -0.07782 | 0.009155 | 0.041199 | 0.013733 | 0.091553 | 0.064087 | 0.32501 | 121.907 | 0.059509 | 121.8521 | 121.9482 | 121.8384 | 121.8567 | 121.788 | -121.9711 | -121.9299 | 121.8155 | 121.8018 | 60.8597 | 60.8688
33.5938 | 122.0581 | -60.878 | 60.9192 | -0.0036622 | 0.0037683 | 0.068658 | 0.064128 | -0.0010488 | -0.0029694 | -0.0027195 | -0.0046081 | 0.00072206 | 0.06969 | 0.061256 | -0.0039413 | 0.014112 | -0.0021341 | -0.10986 | 60.9009 | -61.0153 | 60.91 | -60.6354 | -61.0428 | -61.0611 | -0.018311 | 60.8139 | -60.9421 | 60.9787 | -60.8093 | -60.8002 | -60.7864 | -0.13733 | -0.01831 | -0.009155 | 0.24262 | -0.1831 | -0.16479 | -0.045776 | -0.027466 | -0.064087 | -0.10529 | 0.05951 | 0.068665 | 0.091553 | 0.07782 | 0.15564 | 0.14191 | 0.37994 | 121.9254 | 0.13275 | 121.9208 | 121.9162 | 121.756 | 121.7789 | 121.6919 | -121.9345 | -121.8613 | 121.788 | 121.8567 | 60.7681 | 60.8597
35.3281 | 121.9528 | -60.9467 | 60.8963 | -0.0036622 | 0.0039819 | 0.067377 | 0.067546 | -0.00019445 | -0.0021148 | 0.00091209 | -0.0015565 | 0.0047809 | 0.068409 | 0.060188 | -0.0026597 | 0.015394 | 2.068e-06 | -0.091553 | 60.9192 | -61.0886 | 60.8047 | -60.8047 | -61.1893 | -61.2259 | -0.15106 | 60.8002 | -61.0153 | 60.8322 | -60.9924 | -61.0153 | -60.9329 | -0.14191 | 0.022888 | -0.091552 | 0.14191 | -0.27924 | -0.24262 | -0.13733 | -0.10071 | -0.068665 | -0.09613 | -0.064087 | -0.045777 | 0.013733 | -0.068665 | 0.082398 | 0 | 0.28381 | 121.8933 | 0.022888 | 121.8475 | 122.0078 | 121.8155 | 121.8658 | 121.7468 | -121.9849 | -121.9116 | 121.7514 | 121.7789 | 60.8551 | 60.7956
37 | 122.0718 | -60.8917 | 60.8643 | 0.011597 | 0.0046227 | 0.067377 | 0.066477 | -0.00019445 | -0.00083304 | -0.0022921 | -0.0046081 | 0.0013629 | 0.06734 | 0.061897 | -0.0013779 | 0.016889 | 0.00042947 | -0.10071 | 60.8963 | -61.0428 | 60.9146 | -60.6674 | -61.0931 | -61.116 | -0.018311 | 60.7727 | -60.9741 | 60.965 | -60.8459 | -60.8597 | -60.8047 | -0.15106 | 0.032043 | 0.050354 | 0.22431 | -0.2243 | -0.20142 | -0.073242 | -0.050354 | -0.082397 | -0.091553 | 0.10071 | 0.045777 | 0.086975 | 0.032044 | 0.16937 | 0.11444 | 0.37537 | 121.9574 | 0.12817 | 121.9391 | 121.9391 | 121.7468 | 121.788 | 121.6644 | -121.907 | -121.8384 | 121.8063 | 121.8567 | 60.791 | 60.8734
38.75 | 122.0581 | -60.9055 | 60.878 | -0.0036622 | 0.0031275 | 0.068872 | 0.065409 | 0.0034372 | -0.00019224 | -0.00058311 | 0.013702 | 0.0017901 | 0.068836 | 0.063606 | -0.00073705 | 0.015821 | 0.0014975 | -0.064087 | 60.878 | -61.0611 | 60.9741 | -60.5667 | -61.0291 | -61.0428 | 0.041199 | 60.791 | -60.9741 | 60.9741 | -60.8231 | -60.8368 | -60.8185 | -0.15564 | 0 | 0.09613 | 0.33875 | -0.13733 | -0.1236 | 0.01831 | 0.032043 | -0.068664 | -0.086975 | 0.09613 | 0.082398 | 0.086976 | 0.068665 | 0.15564 | 0.13733 | 0.49439 | 122.0352 | 0.15106 | 121.9482 | 121.9391 | 121.7651 | 121.7834 | 121.6965 | -121.9391 | -121.8521 | 121.8796 | 121.8796 | 60.8414 | 60.9467
40.4844 | 122.0856 | -60.9055 | 60.8551 | 0.0039673 | 0.0050501 | 0.066309 | 0.064982 | -0.00040805 | -0.0027556 | -0.0010105 | -0.0076599 | 0.0017901 | 0.069477 | 0.061043 | -0.0015915 | 0.016034 | -0.00063873 | -0.10986 | 60.8963 | -61.0748 | 60.9009 | -60.6766 | -61.0886 | -61.1023 | 0.004578 | 60.791 | -61.0016 | 60.9604 | -60.8414 | -60.8688 | -60.8185 | -0.16937 | 0.041198 | 0.045776 | 0.22888 | -0.19684 | -0.18311 | -0.027466 | -0.013733 | -0.09613 | -0.064087 | 0.10529 | 0.064087 | 0.086976 | 0.036622 | 0.18311 | 0.13275 | 0.39825 | 121.9757 | 0.16022 | 121.962 | 121.9711 | 121.7926 | 121.8018 | 121.6965 | -121.9299 | -121.8567 | 121.8063 | 121.8658 | 60.7956 | 60.91
42.1562 | 121.9803 | -60.9421 | 60.8871 | 0.0039673 | 0.0052637 | 0.066309 | 0.066905 | 0.0025828 | -0.0027556 | 0.0019803 | 0.0045471 | 0.0011493 | 0.071827 | 0.059975 | -0.0050095 | 0.014966 | -0.0019205 | -0.041199 | 60.9055 | -61.0703 | 60.8871 | -60.6903 | -61.0977 | -61.1206 | -0.009155 | 60.7956 | -60.9833 | 60.878 | -60.9192 | -60.9421 | -60.8826 | -0.12817 | 0.018311 | 0 | 0.25177 | -0.17853 | -0.15564 | -0.050354 | -0.027466 | -0.041198 | -0.091553 | -0.009155 | 0.022889 | 0.05951 | 0 | 0.10071 | 0.041198 | 0.37994 | 121.9574 | 0.064087 | 121.8613 | 121.9757 | 121.7789 | 121.8475 | 121.7377 | -121.9574 | -121.8704 | 121.8292 | 121.8201 | 60.9009 | 60.9329
43.9062 | 121.9482 | -60.9329 | 60.9329 | -0.0036622 | 0.0069727 | 0.064813 | 0.066264 | 0.0017282 | 0.00023496 | 0.00048489 | 0.013702 | 0.0052081 | 0.070331 | 0.055061 | -0.0043687 | 0.014112 | -0.00063873 | -0.068665 | 60.9741 | -61.084 | 60.8643 | -60.7132 | -61.0794 | -61.1114 | -0.068665 | 60.8734 | -60.997 | 60.8505 | -60.9283 | -60.9375 | -60.8917 | -0.15106 | 0.041199 | -0.068664 | 0.21973 | -0.17853 | -0.14649 | -0.027466 | 0.004577 | -0.064087 | -0.059509 | -0.082397 | 0.004577 | 0.041198 | -0.004578 | 0.10528 | 0.059509 | 0.37079 | 121.9482 | 0.068664 | 121.8475 | 122.0581 | 121.8704 | 121.907 | 121.8063 | -122.0169 | -121.9299 | 121.7972 | 121.7834 | 60.8643 | 60.8643
45.6562 | 121.9391 | -60.9604 | 60.8917 | -0.0036622 | 0.0059045 | 0.067377 | 0.06605 | 0.0032236 | 0.0013032 | -0.00058311 | -0.0015565 | 0.0028583 | 0.071399 | 0.056343 | -0.0022325 | 0.01518 | -0.0032021 | -0.11444 | 60.9238 | -61.0931 | 60.8002 | -60.7819 | -61.1847 | -61.2076 | -0.13733 | 60.7819 | -61.0153 | 60.8414 | -60.9833 | -61.0062 | -60.9421 | -0.13275 | 0.032043 | -0.091553 | 0.17853 | -0.24719 | -0.2243 | -0.11444 | -0.091552 | -0.054932 | -0.10986 | -0.050354 | -0.022888 | 0.01831 | -0.045777 | 0.073242 | 0.009155 | 0.31128 | 121.8933 | 0.032044 | 121.8567 | 122.0169 | 121.7972 | 121.8842 | 121.7422 | -121.9849 | -121.907 | 121.7606 | 121.8018 | 60.8459 | 60.8231
47.4062 | 121.9666 | -60.9238 | 60.9238 | 0.049744 | 0.0067591 | 0.06759 | 0.064555 | 0.0021556 | -0.0019012 | -0.0029331 | 0.013702 | 0.0032855 | 0.071186 | 0.058693 | -0.0052231 | 0.013898 | -0.0019205 | -0.054932 | 60.9604 | -61.0474 | 60.8551 | -60.7086 | -61.0931 | -61.1252 | -0.059509 | 60.8459 | -60.997 | 60.8505 | -60.9009 | -60.9146 | -60.8688 | -0.1236 | 0.036621 | -0.068664 | 0.21515 | -0.20142 | -0.16937 | -0.07782 | -0.045777 | -0.073242 | -0.07782 | -0.073242 | 0.022888 | 0.054932 | 0.009155 | 0.12817 | 0.082397 | 0.33874 | 121.9025 | 0.09613 | 121.8475 | 122.0078 | 121.843 | 121.8842 | 121.7697 | -121.9711 | -121.9208 | 121.7789 | 121.7743 | 60.8688 | 60.8643
49.0781 | 121.9482 | -60.9283 | 60.9009 | 0.0039673 | 0.0018457 | 0.066522 | 0.067973 | 0.0015146 | -0.0016876 | -0.00058311 | 0.013702 | 0.0017901 | 0.06969 | 0.056343 | -0.0052231 | 0.013685 | -0.0042703 | -0.073242 | 60.965 | -61.0931 | 60.8643 | -60.6995 | -61.0886 | -61.0977 | -0.045776 | 60.8597 | -60.9924 | 60.8505 | -60.9283 | -60.9238 | -60.8826 | -0.16479 | 0.064087 | -0.036621 | 0.22888 | -0.16937 | -0.16022 | -0.004577 | 0.004578 | -0.064087 | -0.041199 | -0.050354 | 0 | 0.045777 | 0.004578 | 0.10986 | 0.068665 | 0.39368 | 121.9574 | 0.064087 | 121.843 | 122.0581 | 121.8521 | 121.8933 | 121.788 | -121.994 | -121.8933 | 121.7926 | 121.7789 | 60.8551 | 60.8826
50.8281 | 121.9849 | -60.9192 | 60.9055 | 0.011597 | 0.0052637 | 0.066949 | 0.062205 | -0.0033986 | -0.0012604 | -0.0022921 | 0.0014953 | 0.0013629 | 0.06969 | 0.064033 | -0.0041551 | 0.013898 | -0.0040567 | -0.022888 | 60.8917 | -60.997 | 60.9421 | -60.5942 | -60.9741 | -61.0428 | 0 | 60.8139 | -60.9512 | 60.91 | -60.8459 | -60.8414 | -60.8368 | -0.07782 | -0.013733 | 0.036621 | 0.32501 | -0.1236 | -0.054932 | -0.045777 | 0.022888 | -0.032044 | -0.091553 | 0.004577 | 0.073242 | 0.082397 | 0.077819 | 0.11444 | 0.10986 | 0.40283 | 121.9391 | 0.10529 | 121.8613 | 121.8887 | 121.7651 | 121.8109 | 121.7331 | -121.9025 | -121.8567 | 121.8613 | 121.8292 | 60.8963 | 60.9192
52.4844 | 122.0444 | -60.8871 | 60.9146 | 0.0039673 | 0.0041955 | 0.068445 | 0.06605 | -0.0012624 | -0.002542 | 0.00048489 | -0.0046081 | 0.0015765 | 0.067554 | 0.061897 | -0.00073705 | 0.014966 | -0.00021153 | -0.086975 | 60.9283 | -61.0291 | 60.8963 | -60.6445 | -61.0382 | -61.0703 | -0.041199 | 60.7956 | -60.9604 | 60.965 | -60.8139 | -60.8139 | -60.7956 | -0.14191 | 0.013733 | -0.018311 | 0.24262 | -0.1831 | -0.15106 | -0.041198 | -0.009155 | -0.073242 | -0.11902 | 0.050354 | 0.073242 | 0.091553 | 0.073242 | 0.1648 | 0.14648 | 0.38452 | 121.9254 | 0.14648 | 121.9254 | 121.9574 | 121.756 | 121.8155 | 121.6827 | -121.9437 | -121.875 | 121.7834 | 121.8521 | 60.8002 | 60.8459
54.2188 | 122.0718 | -60.8963 | 60.8688 | -0.0036622 | 0.0037683 | 0.067377 | 0.065623 | -0.00040805 | -0.0021148 | -0.00015591 | 0.010651 | 0.0024311 | 0.070545 | 0.072365 | -0.0024461 | 0.016889 | -0.0021341 | -0.054932 | 60.8871 | -61.0199 | 60.9329 | -60.6171 | -61.0611 | -61.0428 | 0.050354 | 60.7727 | -60.9604 | 60.9741 | -60.8139 | -60.8276 | -60.7956 | -0.1236 | 0.018311 | 0.064087 | 0.27924 | -0.14648 | -0.16479 | -0.022889 | -0.041199 | -0.064087 | -0.09613 | 0.10529 | 0.082397 | 0.10071 | 0.068664 | 0.1648 | 0.13275 | 0.40283 | 121.9528 | 0.14648 | 121.9345 | 121.907 | 121.7331 | 121.7834 | 121.669 | -121.8887 | -121.8292 | 121.8292 | 121.8704 | 60.8414 | 60.9467
55.8906 | 121.9757 | -60.9283 | 60.9329 | 0.042114 | 0.0041955 | 0.066309 | 0.065623 | 0.0021556 | -0.0019012 | -0.0018649 | 0.010651 | 0.0037127 | 0.069904 | 0.053993 | -0.0052231 | 0.014112 | -0.0012795 | -0.041199 | 60.9558 | -61.0611 | 60.8597 | -60.7132 | -61.0748 | -61.1023 | -0.036621 | 60.8551 | -60.9741 | 60.8688 | -60.91 | -60.9009 | -60.8597 | -0.13275 | 0.022889 | -0.073242 | 0.21515 | -0.17395 | -0.14648 | -0.041199 | -0.013733 | -0.045776 | -0.077819 | -0.064087 | 0.018311 | 0.068665 | 0.027466 | 0.11444 | 0.073242 | 0.3479 | 121.9208 | 0.064087 | 121.843 | 122.0169 | 121.8292 | 121.8842 | 121.7834 | -121.994 | -121.907 | 121.788 | 121.7972 | 60.8871 | 60.8917
57.625 | 122.0901 | -60.8688 | 60.8826 | 0.0039673 | 0.0035547 | 0.068018 | 0.064128 | -0.0012624 | -0.0021148 | -0.0033603 | -0.0046081 | 8.1264e-05 | 0.068195 | 0.068947 | -0.0047959 | 0.017316 | -0.0040567 | -0.068665 | 60.9329 | -61.0062 | 60.9604 | -60.5896 | -60.9787 | -60.9924 | 0.036621 | 60.8002 | -60.9467 | 60.997 | -60.7498 | -60.7681 | -60.7681 | -0.13733 | 0.050354 | 0.07782 | 0.27923 | -0.1236 | -0.10986 | 0.013733 | 0.027466 | -0.07782 | -0.082397 | 0.11444 | 0.11902 | 0.10071 | 0.10071 | 0.17853 | 0.17853 | 0.41657 | 121.9666 | 0.19684 | 121.9437 | 121.9391 | 121.7468 | 121.8018 | 121.669 | -121.8887 | -121.8292 | 121.8292 | 121.8658 | 60.8002 | 60.9055
59.2969 | 122.0261 | -60.8963 | 60.8597 | 0.057373 | 0.0041955 | 0.071222 | 0.067118 | -0.00083525 | -0.0010468 | 0.0017667 | 0.013702 | 0.0028583 | 0.071399 | 0.065102 | -0.0022325 | 0.016034 | 0.00021567 | -0.059509 | 60.8643 | -61.0153 | 60.9604 | -60.5942 | -61.0245 | -61.0291 | 0.022888 | 60.7956 | -60.9879 | 60.965 | -60.8276 | -60.8505 | -60.7956 | -0.11902 | 0.004578 | 0.10071 | 0.30212 | -0.13275 | -0.12817 | -0.013733 | -0.009155 | -0.091553 | -0.064087 | 0.10529 | 0.068664 | 0.10071 | 0.045776 | 0.19226 | 0.13733 | 0.42114 | 121.9757 | 0.16022 | 121.9528 | 121.8796 | 121.7834 | 121.7606 | 121.6919 | -121.875 | -121.8475 | 121.8567 | 121.8613 | 60.8368 | 60.9192
61.0469 | 122.0993 | -60.8643 | 60.9146 | -0.0036622 | 0.0039819 | 0.065668 | 0.0637 | -0.0019034 | -0.002542 | -0.00036951 | -0.0046081 | 0.0028583 | 0.068409 | 0.056984 | -0.0020187 | 0.01518 | -0.00021153 | -0.027466 | 60.8917 | -60.9924 | 60.9741 | -60.553 | -60.9833 | -60.9924 | 0.10986 | 60.7956 | -60.9238 | 61.0107 | -60.7269 | -60.7452 | -60.7544 | -0.12817 | -0.022888 | 0.059509 | 0.31128 | -0.12817 | -0.11902 | 0 | 0.009156 | -0.059509 | -0.11902 | 0.09613 | 0.13733 | 0.10986 | 0.11902 | 0.16937 | 0.17853 | 0.43945 | 121.9666 | 0.19684 | 121.9345 | 121.8842 | 121.7194 | 121.756 | 121.6599 | -121.907 | -121.8384 | 121.8384 | 121.875 | 60.8368 | 60.9741
62.7188 | 122.0123 | -60.8963 | 60.8597 | 0.026856 | 0.0061181 | 0.067377 | 0.068186 | 0.0032236 | 0.00023496 | -0.0018649 | 0.010651 | 0.0026447 | 0.069049 | 0.065315 | -0.00095065 | 0.016675 | -0.0044839 | -0.050354 | 60.91 | -61.0245 | 60.9558 | -60.5713 | -61.0291 | -61.0291 | 0.041199 | 60.8002 | -60.9741 | 60.9375 | -60.8459 | -60.8414 | -60.8139 | -0.12817 | 0.050354 | 0.096131 | 0.32501 | -0.13275 | -0.13275 | -0.004578 | -0.004578 | -0.07782 | -0.059509 | 0.07782 | 0.050354 | 0.082397 | 0.054931 | 0.16022 | 0.13275 | 0.45319 | 121.9803 | 0.12817 | 121.9116 | 121.9345 | 121.7743 | 121.8063 | 121.6965 | -121.8842 | -121.8338 | 121.8521 | 121.8338 | 60.8459 | 60.9375
64.4531 | 121.9345 | -60.9146 | 60.9467 | -0.0036622 | 0.0016321 | 0.066095 | 0.066905 | -0.0029714 | -0.0036102 | -0.0040011 | -0.0015565 | 0.0015765 | 0.068622 | 0.058693 | -0.0069321 | 0.012616 | -0.00085233 | -0.07782 | 60.9009 | -61.0245 | 60.8459 | -60.7086 | -61.0977 | -61.1252 | -0.059509 | 60.8231 | -60.965 | 60.8505 | -60.8871 | -60.9192 | -60.8734 | -0.10986 | -0.045776 | -0.10071 | 0.20599 | -0.21057 | -0.18311 | -0.10071 | -0.073242 | -0.050354 | -0.1236 | -0.09613 | 0.027466 | 0.041199 | -0.004577 | 0.091553 | 0.045777 | 0.31586 | 121.8704 | 0.07782 | 121.8155 | 121.9254 | 121.788 | 121.8155 | 121.7377 | -121.9711 | -121.9116 | 121.7606 | 121.7651 | 60.8368 | 60.8551
66.2031 | 121.9482 | -60.8917 | 60.91 | 0.057373 | 0.0061181 | 0.066095 | 0.067546 | 0.0051462 | -0.00019224 | 0.0021939 | 0.013702 | 0.0043537 | 0.070118 | 0.058266 | -0.0052231 | 0.014325 | 0.00064307 | -0.036621 | 60.9833 | -61.084 | 60.8597 | -60.6949 | -61.084 | -61.1023 | -0.064087 | 60.878 | -61.0062 | 60.8688 | -60.9146 | -60.9192 | -60.8643 | -0.19226 | 0.073242 | -0.050354 | 0.19684 | -0.21057 | -0.19226 | -0.018311 | 0 | -0.11444 | -0.032043 | -0.041199 | -0.022888 | 0.027466 | -0.027465 | 0.14191 | 0.086976 | 0.3891 | 121.9437 | 0.091553 | 121.875 | 122.0673 | 121.8842 | 121.875 | 121.7697 | -121.994 | -121.9162 | 121.7514 | 121.7606 | 60.8551 | 60.8276
67.9375 | 121.9208 | -60.9421 | 60.8826 | -0.011291 | 0.0065453 | 0.065881 | 0.066477 | -0.00019445 | -0.0021148 | -0.0029331 | -0.0015565 | 0.0043537 | 0.067981 | 0.066811 | -0.0022325 | 0.012403 | -0.0044839 | -0.11444 | 60.8917 | -61.0657 | 60.791 | -60.8093 | -61.2076 | -61.2167 | -0.13275 | 60.8093 | -60.997 | 60.8276 | -60.9879 | -60.9741 | -60.9055 | -0.1236 | 0.009156 | -0.091552 | 0.13275 | -0.27466 | -0.2655 | -0.15106 | -0.14191 | -0.054931 | -0.073242 | -0.054931 | -0.045776 | 0.036621 | -0.032043 | 0.091552 | 0.022888 | 0.25635 | 121.8567 | 0.009155 | 121.8246 | 121.9574 | 121.8063 | 121.8338 | 121.7514 | -121.9482 | -121.8796 | 121.7331 | 121.7697 | 60.8276 | 60.8093
69.6719 | 121.9711 | -60.8826 | 60.9283 | -0.011291 | 0.0056909 | 0.064813 | 0.066477 | -0.0042532 | -0.0027556 | 0.0013395 | -0.0015565 | 0.0020039 | 0.067981 | 0.061043 | -0.0033005 | 0.016462 | -0.0021341 | -0.036621 | 60.9055 | -61.0107 | 60.9375 | -60.6033 | -61.0062 | -61.0382 | -0.004578 | 60.8185 | -60.9604 | 60.8871 | -60.8551 | -60.8551 | -60.8459 | -0.12817 | -0.022888 | 0.009155 | 0.27923 | -0.15564 | -0.1236 | -0.027466 | 0.004577 | -0.07782 | -0.10986 | -0.041199 | 0.027465 | 0.036621 | 0.027465 | 0.11444 | 0.10529 | 0.40741 | 121.9482 | 0.10529 | 121.8475 | 121.9162 | 121.7789 | 121.788 | 121.701 | -121.9391 | -121.8887 | 121.8201 | 121.7697 | 60.8459 | 60.878
71.3438 | 121.9208 | -60.9604 | 60.8688 | -0.011291 | 0.0044091 | 0.066522 | 0.06605 | -0.00040805 | -0.0019012 | -0.0010105 | -0.0015565 | 0.0026447 | 0.06969 | 0.061897 | -0.0022325 | 0.01518 | -0.0014931 | -0.11444 | 60.9055 | -61.0565 | 60.8002 | -60.7819 | -61.1847 | -61.1893 | -0.11902 | 60.7819 | -60.9879 | 60.8322 | -60.965 | -60.9741 | -60.9055 | -0.096131 | 0.036622 | -0.068664 | 0.17853 | -0.22888 | -0.2243 | -0.13275 | -0.12817 | -0.027466 | -0.086975 | -0.036621 | -0.004578 | 0.054931 | -0.013733 | 0.082397 | 0.013733 | 0.27466 | 121.8567 | 0.022888 | 121.8201 | 121.962 | 121.7697 | 121.8658 | 121.7422 | -121.9254 | -121.8567 | 121.7606 | 121.7926 | 60.8459 | 60.8414
73.0781 | 121.9666 | -60.9283 | 60.8963 | 0.026856 | 0.0067591 | 0.066522 | 0.067118 | 0.0034372 | -0.0021148 | 0.00027129 | 0.019806 | 0.0030719 | 0.068409 | 0.062965 | -0.0033005 | 0.014753 | 0.00021567 | -0.073242 | 60.9375 | -61.0519 | 60.8643 | -60.7086 | -61.0703 | -61.1023 | -0.054932 | 60.8414 | -61.0107 | 60.878 | -60.9009 | -60.9055 | -60.8459 | -0.1236 | 0.041199 | -0.032043 | 0.21973 | -0.17395 | -0.14191 | -0.050354 | -0.01831 | -0.082397 | -0.054931 | -0.01831 | 0.027466 | 0.082398 | 0.022888 | 0.16479 | 0.10529 | 0.34332 | 121.9162 | 0.10986 | 121.8887 | 121.9894 | 121.8521 | 121.8658 | 121.7697 | -121.9482 | -121.907 | 121.7926 | 121.8063 | 60.8551 | 60.8734
74.75 | 121.9528 | -60.9009 | 60.9192 | -0.011291 | 0.0044091 | 0.066736 | 0.064128 | -0.0042532 | -0.0029694 | -0.0010105 | -0.0076599 | -0.00034614 | 0.066913 | 0.064888 | -0.0033005 | 0.014539 | -0.0036295 | -0.027466 | 60.9009 | -60.9924 | 60.9283 | -60.5988 | -61.0016 | -61.0565 | 0.004578 | 60.8139 | -60.9283 | 60.9009 | -60.8414 | -60.8597 | -60.8322 | -0.091553 | -0.01831 | 0.009156 | 0.30212 | -0.15564 | -0.10071 | -0.064087 | -0.009155 | -0.027466 | -0.10529 | -0.01831 | 0.059509 | 0.068665 | 0.041199 | 0.096131 | 0.068665 | 0.39368 | 121.9208 | 0.086975 | 121.8292 | 121.8933 | 121.7422 | 121.8018 | 121.7148 | -121.9116 | -121.8475 | 121.8292 | 121.8018 | 60.8734 | 60.9055
76.5 | 121.9254 | -60.91 | 60.9329 | 0.011597 | 0.0041955 | 0.067163 | 0.064555 | -0.00083525 | -0.0027556 | -0.00015591 | -0.0046081 | 0.0026447 | 0.069904 | 0.067024 | -0.0069321 | 0.012403 | -0.00042513 | -0.059509 | 60.9375 | -61.0107 | 60.8505 | -60.6903 | -61.084 | -61.0931 | -0.073242 | 60.8505 | -60.9512 | 60.8551 | -60.8917 | -60.9055 | -60.878 | -0.10071 | 0.004578 | -0.082397 | 0.21973 | -0.18311 | -0.17395 | -0.082398 | -0.073242 | -0.041199 | -0.082397 | -0.077819 | 0.01831 | 0.032043 | 0.004577 | 0.073242 | 0.045776 | 0.32043 | 121.8613 | 0.059509 | 121.8063 | 121.9482 | 121.8018 | 121.8475 | 121.7606 | -121.9437 | -121.8842 | 121.7606 | 121.7651 | 60.8505 | 60.8368
78.2344 | 121.994 | -60.878 | 60.9238 | 0.011597 | 0.0041955 | 0.067804 | 0.065196 | -0.0019034 | -0.0023284 | 0.0013395 | 0.0045471 | 0.0024311 | 0.068836 | 0.06147 | -0.0013779 | 0.01518 | 0.0012839 | -0.082397 | 60.9146 | -61.0382 | 60.9009 | -60.6354 | -61.0382 | -61.0474 | -0.032043 | 60.8047 | -60.9283 | 60.9375 | -60.8414 | -60.8231 | -60.8139 | -0.16022 | -0.009155 | -0.022888 | 0.24262 | -0.16937 | -0.16022 | -0.009155 | 0 | -0.050354 | -0.11902 | 0.013733 | 0.036621 | 0.064087 | 0.054932 | 0.11444 | 0.10529 | 0.40283 | 121.9391 | 0.086975 | 121.8658 | 121.9528 | 121.7331 | 121.7926 | 121.6827 | -121.962 | -121.8521 | 121.7789 | 121.8155 | 60.7956 | 60.8459
79.9531 | 121.9299 | -60.9146 | 60.9283 | 0.0039673 | 0.0050501 | 0.066736 | 0.064982 | -0.002117 | -0.0036102 | -0.0018649 | -0.0015565 | 0.0017901 | 0.068409 | 0.055489 | -0.0039413 | 0.014325 | -0.00042513 | -0.10071 | 60.91 | -61.0565 | 60.8414 | -60.7132 | -61.0886 | -61.1206 | -0.073242 | 60.8459 | -60.9467 | 60.8505 | -60.8917 | -60.91 | -60.8871 | -0.14191 | -0.018311 | -0.086975 | 0.20142 | -0.20599 | -0.17395 | -0.064086 | -0.032043 | -0.032043 | -0.082398 | -0.07782 | 0.022888 | 0.027466 | 0.004578 | 0.059509 | 0.036621 | 0.34332 | 121.8979 | 0.054931 | 121.7972 | 121.9666 | 121.7926 | 121.8246 | 121.7606 | -121.9849 | -121.875 | 121.756 | 121.7651 | 60.8139 | 60.8414
81.625 | 121.9299 | -60.9375 | 60.8643 | -0.0036622 | 0.0065453 | 0.065881 | 0.06605 | 0.0066416 | -0.0016876 | 0.00027129 | -0.0046081 | 0.0052081 | 0.06734 | 0.062111 | -0.0033005 | 0.015394 | -0.0010659 | -0.050354 | 60.8917 | -61.0565 | 60.8322 | -60.704 | -61.1343 | -61.1572 | -0.059509 | 60.7864 | -60.9879 | 60.8231 | -60.9375 | -60.9833 | -60.8871 | -0.11902 | 0.027466 | -0.032044 | 0.23346 | -0.21973 | -0.19684 | -0.10071 | -0.077819 | -0.050354 | -0.07782 | -0.041199 | 0 | 0.050354 | -0.045776 | 0.10071 | 0.004578 | 0.35248 | 121.8887 | 0.050354 | 121.8109 | 121.9482 | 121.7743 | 121.8292 | 121.7239 | -121.9208 | -121.8521 | 121.7697 | 121.7606 | 60.8871 | 60.878
83.3594 | 121.907 | -60.9421 | 60.8734 | -0.0036622 | 0.0067591 | 0.065668 | 0.067546 | -0.0033986 | -0.0021148 | 5.7688e-05 | -0.0046081 | 0.0043537 | 0.068622 | 0.052284 | -0.0018051 | 0.015821 | -0.0023477 | -0.073242 | 60.9009 | -61.0565 | 60.7956 | -60.7636 | -61.1755 | -61.1801 | -0.09613 | 60.7773 | -61.0016 | 60.8231 | -60.9467 | -60.965 | -60.8963 | -0.11444 | 0.027466 | -0.07782 | 0.17853 | -0.23804 | -0.23346 | -0.1236 | -0.11902 | -0.059509 | -0.09613 | -0.050354 | -0.004577 | 0.045777 | -0.022888 | 0.10529 | 0.036621 | 0.29297 | 121.8521 | 0.054932 | 121.8246 | 121.9574 | 121.7789 | 121.843 | 121.7194 | -121.9299 | -121.875 | 121.7377 | 121.7651 | 60.8688 | 60.8459
85.0938 | 122.0581 | -60.8734 | 60.8963 | -0.011291 | 0.0048365 | 0.064813 | 0.064555 | -0.0023306 | 2.1362e-05 | -0.0018649 | -0.0046081 | 0.0011493 | 0.069263 | 0.070442 | -0.0022325 | 0.016462 | -0.0061929 | -0.07782 | 60.91 | -60.9833 | 60.9558 | -60.5576 | -60.9741 | -60.9924 | 0.022888 | 60.8047 | -60.8917 | 60.9833 | -60.759 | -60.7544 | -60.7544 | -0.10986 | 0.013733 | 0.05951 | 0.31586 | -0.11902 | -0.10071 | -0.009156 | 0.009155 | -0.018311 | -0.091552 | 0.086975 | 0.11444 | 0.11902 | 0.11902 | 0.13733 | 0.13733 | 0.42572 | 121.9391 | 0.13275 | 121.875 | 121.8933 | 121.6965 | 121.7834 | 121.6782 | -121.8796 | -121.788 | 121.8292 | 121.8567 | 60.7956 | 60.8963
86.7812 | 121.9299 | -60.91 | 60.9146 | -0.011291 | 0.0041955 | 0.065241 | 0.064555 | -0.003185 | -0.0012604 | 5.7688e-05 | -0.0015565 | 0.0015765 | 0.067768 | 0.062538 | -0.0039413 | 0.014966 | -0.00021153 | -0.032043 | 60.91 | -60.997 | 60.8826 | -60.6445 | -61.0565 | -61.0703 | -0.018311 | 60.8185 | -60.9375 | 60.878 | -60.8734 | -60.8826 | -60.8734 | -0.086975 | -0.004578 | -0.032044 | 0.2655 | -0.16022 | -0.14648 | -0.073242 | -0.05951 | -0.027466 | -0.096131 | -0.036621 | 0.036621 | 0.036621 | 0.027466 | 0.064087 | 0.054932 | 0.35248 | 121.8796 | 0.064087 | 121.8155 | 121.907 | 121.756 | 121.8201 | 121.7285 | -121.9116 | -121.8521 | 121.7926 | 121.788 | 60.878 | 60.8917
88.5312 | 122.0169 | -60.9055 | 60.8322 | -0.011291 | 0.0029139 | 0.067163 | 0.066691 | -0.00062165 | -0.0016876 | -0.0022921 | -0.0046081 | 0.0034991 | 0.068409 | 0.066811 | 0.00033115 | 0.016248 | -0.0019205 | -0.11902 | 60.91 | -61.0519 | 60.8276 | -60.6949 | -61.1298 | -61.1298 | -0.054932 | 60.7773 | -60.9375 | 60.9146 | -60.8459 | -60.8597 | -60.8093 | -0.14648 | 0.07782 | -0.004577 | 0.21057 | -0.2243 | -0.2243 | -0.07782 | -0.07782 | -0.032043 | -0.054931 | 0.082398 | 0.05951 | 0.096131 | 0.045777 | 0.12817 | 0.07782 | 0.35706 | 121.8796 | 0.091553 | 121.8521 | 121.962 | 121.7148 | 121.8155 | 121.6827 | -121.8842 | -121.7697 | 121.7331 | 121.8201 | 60.7864 | 60.8505
90.2031 | 121.962 | -60.9283 | 60.8917 | 0.011597 | 0.0065453 | 0.066736 | 0.067546 | 0.00087375 | -0.002542 | -0.00036951 | -0.0015565 | 0.0022175 | 0.068409 | 0.052071 | -0.0028733 | 0.015394 | -0.0055521 | -0.041199 | 60.9146 | -61.0565 | 60.8734 | -60.6812 | -61.0794 | -61.1069 | -0.009155 | 60.7727 | -60.9787 | 60.8597 | -60.8871 | -60.91 | -60.8643 | -0.12817 | 0.022888 | -0.018311 | 0.24719 | -0.17853 | -0.15106 | -0.050354 | -0.022888 | -0.050354 | -0.11902 | -0.032044 | 0.041199 | 0.064087 | 0.018311 | 0.11444 | 0.068665 | 0.37537 | 121.9299 | 0.091553 | 121.8384 | 121.9711 | 121.7514 | 121.843 | 121.7011 | -121.9482 | -121.8704 | 121.8018 | 121.788 | 60.8871 | 60.9192
91.9062 | 121.8933 | -60.9558 | 60.878 | 0.0039673 | 0.0046227 | 0.069086 | 0.065409 | 0.00023275 | -0.00083304 | -0.0016513 | -0.0046081 | 0.0039265 | 0.06734 | 0.065102 | -0.0022325 | 0.016675 | 0.00085667 | -0.11902 | 60.8963 | -61.0565 | 60.7773 | -60.7636 | -61.1847 | -61.1847 | -0.13275 | 60.7956 | -60.997 | 60.8002 | -60.9741 | -60.9924 | -60.9238 | -0.10071 | 0.01831 | -0.10071 | 0.19226 | -0.22888 | -0.22888 | -0.12817 | -0.12817 | -0.041198 | -0.082398 | -0.07782 | -0.01831 | 0.032044 | -0.036621 | 0.073242 | 0.004577 | 0.29297 | 121.8338 | 0.022888 | 121.7972 | 121.9528 | 121.7926 | 121.8521 | 121.7514 | -121.9345 | -121.875 | 121.7331 | 121.756 | 60.8368 | 60.8231
93.6406 | 122.049 | -60.8414 | 60.8917 | -0.011291 | 0.00099112 | 0.068018 | 0.061991 | -0.002117 | -0.0019012 | -0.0031467 | -0.0015565 | -0.00077334 | 0.068622 | 0.064247 | -0.0041551 | 0.014966 | 0.0032065 | -0.064087 | 60.8917 | -60.965 | 60.9604 | -60.5621 | -60.9512 | -60.9879 | 0.054932 | 60.8002 | -60.9055 | 60.9787 | -60.7498 | -60.7544 | -60.7452 | -0.1236 | 0 | 0.068664 | 0.27924 | -0.14648 | -0.10986 | -0.022888 | 0.013733 | -0.064087 | -0.091553 | 0.086975 | 0.091553 | 0.096131 | 0.086975 | 0.16022 | 0.15106 | 0.40283 | 121.9254 | 0.15564 | 121.8842 | 121.8567 | 121.7056 | 121.7331 | 121.6415 | -121.8567 | -121.7972 | 121.8018 | 121.8201 | 60.7773 | 60.8963
95.3906 | 121.907 | -60.9512 | 60.878 | -0.0036622 | 0.0061181 | 0.068231 | 0.067759 | -0.0016898 | 0.00087596 | -0.0033603 | -0.0046081 | 0.0045673 | 0.069477 | 0.067665 | -0.0030869 | 0.017316 | -0.00063873 | -0.13733 | 60.9055 | -61.0657 | 60.7773 | -60.7864 | -61.1938 | -61.1755 | -0.11902 | 60.791 | -60.9741 | 60.8276 | -60.9558 | -60.9741 | -60.8826 | -0.11444 | 0.027466 | -0.10071 | 0.1648 | -0.2243 | -0.24262 | -0.10986 | -0.12817 | -0.022888 | -0.086975 | -0.050354 | -0.004578 | 0.068665 | -0.022888 | 0.091553 | 0 | 0.27924 | 121.843 | 0.01831 | 121.8018 | 121.9711 | 121.7651 | 121.8567 | 121.7422 | -121.9437 | -121.8521 | 121.7285 | 121.7789 | 60.8139 | 60.8322
97.0781 | 122.0078 | -60.8734 | 60.8734 | 0.034485 | 0.0046227 | 0.066522 | 0.064555 | 0.0027964 | -0.0019012 | 5.7688e-05 | 0.0075989 | 0.0026447 | 0.069477 | 0.058266 | -0.00052345 | 0.016889 | -0.0010659 | -0.059509 | 60.9055 | -61.0245 | 60.9375 | -60.5713 | -61.0153 | -61.0199 | 0.022888 | 60.7819 | -60.9558 | 60.9421 | -60.8047 | -60.8047 | -60.8002 | -0.15106 | 0.032044 | 0.064087 | 0.30212 | -0.14648 | -0.14191 | 0.004578 | 0.009155 | -0.082398 | -0.091553 | 0.068665 | 0.068664 | 0.073242 | 0.068664 | 0.15564 | 0.15106 | 0.45319 | 121.962 | 0.15106 | 121.8979 | 121.9299 | 121.7377 | 121.7789 | 121.6553 | -121.8979 | -121.8292 | 121.8109 | 121.8155 | 60.8139 | 60.8963
98.8281 | 121.9666 | -60.878 | 60.8734 | -0.011291 | 0.0046227 | 0.065027 | 0.064128 | -0.001476 | -0.0044646 | -0.00079691 | 0.0014953 | 0.00093566 | 0.069477 | 0.056557 | -0.0062913 | 0.017103 | 0.00021567 | -0.022888 | 60.8826 | -61.0016 | 60.9421 | -60.5713 | -60.9695 | -61.0062 | 0.032043 | 60.8047 | -60.9055 | 60.9192 | -60.8185 | -60.8368 | -60.7956 | -0.1236 | 0.009155 | 0.068665 | 0.3067 | -0.12817 | -0.091552 | -0.004578 | 0.032044 | -0.027466 | -0.068664 | 0.045776 | 0.05951 | 0.082398 | 0.041199 | 0.10986 | 0.068665 | 0.4303 | 121.9437 | 0.086976 | 121.8246 | 121.8842 | 121.7102 | 121.7606 | 121.6827 | -121.875 | -121.7789 | 121.8201 | 121.7972 | 60.8551 | 60.91
100.5469 | 121.9528 | -60.9146 | 60.8643 | -0.018921 | 0.0061181 | 0.067377 | 0.069041 | 0.0023692 | -0.0021148 | -0.0044285 | -0.0015565 | 0.0020039 | 0.069049 | 0.057838 | -0.00030965 | 0.015607 | -0.00042513 | -0.12817 | 60.9146 | -61.0611 | 60.7864 | -60.7452 | -61.1481 | -61.171 | -0.10529 | 60.8139 | -60.9787 | 60.8643 | -60.9238 | -60.9238 | -60.8505 | -0.14648 | 0.050354 | -0.07782 | 0.16937 | -0.25635 | -0.23346 | -0.10986 | -0.086975 | -0.064087 | -0.050354 | 0 | -0.009155 | 0.064087 | -0.009155 | 0.12817 | 0.054932 | 0.31586 | 121.8475 | 0.054932 | 121.843 | 121.9757 | 121.7926 | 121.8292 | 121.7285 | -121.9254 | -121.843 | 121.701 | 121.7789 | 60.7864 | 60.8093
102.2188 | 122.0398 | -60.8414 | 60.8597 | 0.0039673 | 0.0044091 | 0.067377 | 0.062632 | -0.0016898 | -0.0010468 | -0.00058311 | -0.0046081 | 0.00029486 | 0.068409 | 0.068092 | -0.0035141 | 0.01518 | -0.0010659 | -0.054932 | 60.9192 | -60.9467 | 60.9421 | -60.5621 | -60.9512 | -60.9741 | 0.064087 | 60.7773 | -60.9146 | 60.9787 | -60.7544 | -60.7452 | -60.7361 | -0.10529 | 0.059509 | 0.082398 | 0.27924 | -0.13275 | -0.10986 | -0.027466 | -0.004578 | -0.073242 | -0.082397 | 0.11902 | 0.086975 | 0.10529 | 0.096131 | 0.17853 | 0.16937 | 0.38452 | 121.8887 | 0.16022 | 121.8933 | 121.8658 | 121.6919 | 121.7606 | 121.6187 | -121.8063 | -121.7743 | 121.7834 | 121.8201 | 60.7864 | 60.9055
103.9531 | 122.0352 | -60.8368 | 60.878 | -0.011291 | 0.0061181 | 0.065454 | 0.064768 | -0.0051076 | -0.0021148 | 0.0021939 | -0.0046081 | 0.0017901 | 0.067554 | 0.061684 | -0.0033005 | 0.013044 | -0.0014931 | -0.022888 | 60.9055 | -60.9833 | 60.9741 | -60.5484 | -60.9558 | -60.9879 | 0.068665 | 60.7773 | -60.9238 | 60.965 | -60.7498 | -60.759 | -60.7544 | -0.14648 | 0.027466 | 0.09613 | 0.28839 | -0.15106 | -0.11902 | -0.004578 | 0.027465 | -0.086975 | -0.10071 | 0.086975 | 0.086975 | 0.082397 | 0.07782 | 0.16937 | 0.16479 | 0.43487 | 121.9574 | 0.17395 | 121.8887 | 121.8887 | 121.701 | 121.7422 | 121.6141 | -121.8613 | -121.8018 | 121.8109 | 121.8018 | 60.8139 | 60.9055
105.6875 | 121.9711 | -60.8643 | 60.8917 | 0.019226 | 0.0063317 | 0.066095 | 0.068186 | -0.00062165 | -0.00040584 | 0.00048489 | 0.0045471 | 0.0013629 | 0.068836 | 0.059975 | -0.0020187 | 0.015607 | -0.0014931 | -0.09613 | 60.9238 | -60.9787 | 60.9009 | -60.6079 | -61.0336 | -61.0428 | -0.036621 | 60.7956 | -60.91 | 60.91 | -60.8276 | -60.8276 | -60.791 | -0.11444 | 0.032043 | 0.009155 | 0.25635 | -0.17853 | -0.16937 | -0.064087 | -0.054931 | -0.045776 | -0.096131 | 0.01831 | 0.036621 | 0.073242 | 0.036621 | 0.11902 | 0.082397 | 0.37079 | 121.8796 | 0.082397 | 121.8201 | 121.9025 | 121.7056 | 121.788 | 121.6599 | -121.8704 | -121.8018 | 121.7651 | 121.7743 | 60.7681 | 60.8276
107.3594 | 121.9574 | -60.9055 | 60.8734 | 0.026856 | 0.0065453 | 0.066736 | 0.066477 | 0.00066015 | -0.0019012 | -0.0016513 | 0.0075989 | 0.0041401 | 0.0667 | 0.055916 | -0.0035141 | 0.014966 | -0.0029885 | -0.027466 | 60.8917 | -61.0748 | 60.8688 | -60.672 | -61.0794 | -61.0886 | 0.004578 | 60.8093 | -60.9695 | 60.878 | -60.8688 | -60.8826 | -60.8276 | -0.16937 | 0.018311 | -0.004578 | 0.23346 | -0.18311 | -0.17395 | -0.013733 | -0.004578 | -0.064086 | -0.064087 | 0.004578 | 0.036622 | 0.07782 | 0.022889 | 0.14191 | 0.086975 | 0.40283 | 121.9437 | 0.10071 | 121.8475 | 121.9666 | 121.7789 | 121.7972 | 121.7148 | -121.9482 | -121.843 | 121.7743 | 121.7834 | 60.878 | 60.91
109.0312 | 121.8933 | -60.8917 | 60.9146 | -0.0036622 | 0.0041955 | 0.065027 | 0.065196 | 0.0010874 | -0.0033966 | -0.0022921 | -0.0076599 | 0.0017901 | 0.068195 | 0.062538 | -0.0056503 | 0.012403 | -0.0017069 | -0.054932 | 60.9146 | -60.9924 | 60.8643 | -60.6445 | -61.0336 | -61.0703 | -0.059509 | 60.8276 | -60.9604 | 60.8551 | -60.8871 | -60.8963 | -60.8597 | -0.10071 | 0 | -0.050354 | 0.24719 | -0.17853 | -0.14191 | -0.077819 | -0.041198 | -0.068664 | -0.086975 | -0.059509 | 0.004578 | 0.032044 | -0.004577 | 0.10071 | 0.064087 | 0.3479 | 121.8567 | 0.073242 | 121.8155 | 121.907 | 121.788 | 121.8063 | 121.7194 | -121.907 | -121.875 | 121.756 | 121.7468 | 60.8368 | 60.8322
110.7812 | 122.0444 | -60.8322 | 60.8734 | -0.018921 | 0.0035547 | 0.067163 | 0.065196 | -0.0010488 | -0.0021148 | -0.0012241 | -0.0046081 | 0.00029486 | 0.068622 | 0.060188 | -0.0026597 | 0.013685 | -0.00021153 | -0.027466 | 60.8871 | -60.9695 | 60.9787 | -60.498 | -60.9421 | -60.965 | 0.073242 | 60.7681 | -60.8963 | 60.9833 | -60.7315 | -60.7269 | -60.7452 | -0.13733 | 0.013733 | 0.10529 | 0.33417 | -0.13275 | -0.10986 | 0.004577 | 0.027465 | -0.064087 | -0.10529 | 0.10986 | 0.10071 | 0.086975 | 0.10529 | 0.15106 | 0.16937 | 0.4715 | 121.9482 | 0.16479 | 121.8796 | 121.8567 | 121.6644 | 121.7194 | 121.6003 | -121.843 | -121.7697 | 121.8109 | 121.8155 | 60.8047 | 60.9055
112.5312 | 122.0078 | -60.8597 | 60.8871 | -0.011291 | 0.0037683 | 0.067163 | 0.064341 | -0.0023306 | -0.0033966 | -0.0025057 | -0.0046081 | 0.00050846 | 0.065845 | 0.055275 | -0.0033005 | 0.016675 | -0.0010659 | -0.018311 | 60.8963 | -60.9741 | 60.9604 | -60.5621 | -60.9604 | -60.997 | 0.054932 | 60.7681 | -60.8963 | 60.9604 | -60.759 | -60.7773 | -60.7498 | -0.11444 | 0.009155 | 0.073242 | 0.29755 | -0.13733 | -0.10071 | -0.022888 | 0.013733 | -0.036621 | -0.11902 | 0.073242 | 0.10071 | 0.10986 | 0.082397 | 0.14648 | 0.11902 | 0.41199 | 121.9345 | 0.13733 | 121.8567 | 121.8704 | 121.6644 | 121.756 | 121.6278 | -121.8613 | -121.7834 | 121.8201 | 121.8201 | 60.8414 | 60.9146
114.2031 | 122.0352 | -60.8459 | 60.8734 | -0.011291 | 0.0031275 | 0.06759 | 0.064555 | -0.0027578 | -0.0012604 | -0.0031467 | -0.0046081 | 0.0013629 | 0.066486 | 0.066383 | -0.0026597 | 0.016248 | -0.0017069 | -0.050354 | 60.9055 | -60.9787 | 60.9512 | -60.553 | -60.9375 | -60.9787 | 0.073242 | 60.7864 | -60.91 | 60.9787 | -60.7315 | -60.7636 | -60.7452 | -0.13275 | 0.032044 | 0.07782 | 0.29297 | -0.13275 | -0.091553 | 0 | 0.041199 | -0.064087 | -0.086975 | 0.10529 | 0.11444 | 0.10071 | 0.082397 | 0.1648 | 0.14648 | 0.42572 | 121.9299 | 0.17853 | 121.8887 | 121.8842 | 121.6965 | 121.7514 | 121.6324 | -121.8521 | -121.7834 | 121.7972 | 121.8246 | 60.7956 | 60.9192
115.9531 | 121.9711 | -60.8505 | 60.8643 | 0.019226 | 0.0039819 | 0.066309 | 0.066477 | 0.00087375 | -0.0016876 | -0.0010105 | 0.0014953 | 0.0017901 | 0.069049 | 0.05677 | -0.0026597 | 0.014753 | -0.0040567 | -0.091553 | 60.8917 | -60.9879 | 60.8917 | -60.6171 | -61.0336 | -61.0336 | -0.041199 | 60.8093 | -60.9238 | 60.9009 | -60.8139 | -60.8185 | -60.7864 | -0.13733 | 0.027466 | 0.027466 | 0.23346 | -0.18311 | -0.18311 | -0.045776 | -0.045776 | -0.073242 | -0.054932 | 0.036621 | 0.036621 | 0.064087 | 0.032044 | 0.13733 | 0.10529 | 0.37079 | 121.8796 | 0.10986 | 121.8246 | 121.8796 | 121.7331 | 121.7422 | 121.6599 | -121.8521 | -121.788 | 121.7422 | 121.7514 | 60.759 | 60.8093
117.7031 | 121.9025 | -60.9192 | 60.9009 | -0.011291 | 0.0041955 | 0.063532 | 0.064341 | -0.0029714 | -0.0019012 | -0.0018649 | 0.0014953 | 0.0041401 | 0.070972 | 0.059975 | -0.0058639 | 0.014539 | 0.0014975 | -0.086975 | 60.9421 | -61.0291 | 60.8276 | -60.6903 | -61.0703 | -61.1023 | -0.068665 | 60.8322 | -60.9467 | 60.8322 | -60.8963 | -60.9055 | -60.8643 | -0.10986 | 0.041199 | -0.073242 | 0.22888 | -0.18311 | -0.15106 | -0.073242 | -0.041198 | -0.027466 | -0.068665 | -0.068665 | 0.022888 | 0.054931 | 0.013732 | 0.082397 | 0.041198 | 0.33874 | 121.8567 | 0.050354 | 121.7789 | 121.9711 | 121.7789 | 121.8613 | 121.7514 | -121.9299 | -121.8475 | 121.7468 | 121.7514 | 60.8322 | 60.8505
119.375 | 121.907 | -60.8963 | 60.9146 | -0.0036622 | 0.0022729 | 0.065454 | 0.06605 | -0.003185 | -0.0040374 | -0.0035739 | -0.0015565 | 0.0049945 | 0.066059 | 0.071083 | -0.0054367 | 0.01283 | -0.0068337 | -0.036621 | 60.9283 | -60.9879 | 60.8826 | -60.6354 | -61.0199 | -61.0565 | -0.041199 | 60.8139 | -60.9238 | 60.8688 | -60.8643 | -60.8643 | -60.8368 | -0.091553 | 0.013733 | -0.032044 | 0.26093 | -0.16022 | -0.1236 | -0.068665 | -0.032043 | -0.027466 | -0.10071 | -0.045777 | 0.032043 | 0.059509 | 0.032043 | 0.086975 | 0.059509 | 0.35248 | 121.8704 | 0.059509 | 121.7926 | 121.9162 | 121.7377 | 121.8246 | 121.7102 | -121.9025 | -121.8384 | 121.7789 | 121.7651 | 60.8597 | 60.8551
121.1094 | 122.0215 | -60.8414 | 60.8963 | -0.0036622 | 0.0035547 | 0.066522 | 0.064982 | -0.0027578 | -0.0029694 | -0.0020785 | -0.0015565 | 0.00072206 | 0.069904 | 0.068306 | -0.0030869 | 0.017103 | -0.00021153 | -0.07782 | 60.8871 | -60.9879 | 60.9238 | -60.5667 | -60.9558 | -60.9879 | 0.032043 | 60.7956 | -60.9009 | 60.9604 | -60.7407 | -60.7407 | -60.7498 | -0.14648 | -0.009155 | 0.027466 | 0.27466 | -0.14648 | -0.11444 | 0 | 0.032043 | -0.059509 | -0.10071 | 0.064087 | 0.10071 | 0.091553 | 0.10071 | 0.15106 | 0.16022 | 0.42114 | 121.9116 | 0.16022 | 121.8613 | 121.875 | 121.6965 | 121.7285 | 121.637 | -121.8842 | -121.7972 | 121.7651 | 121.8018 | 60.7635 | 60.8734
122.8594 | 121.9391 | -60.91 | 60.8551 | 0.019226 | 0.0054773 | 0.067163 | 0.067759 | 0.0034372 | -0.002542 | 0.0024075 | 0.0075989 | 0.0047809 | 0.069477 | 0.060188 | -0.0022325 | 0.014966 | -0.00063873 | -0.032043 | 60.9055 | -61.0703 | 60.8505 | -60.6491 | -61.0657 | -61.0794 | 0 | 60.8002 | -60.9604 | 60.8734 | -60.8551 | -60.8826 | -60.8322 | -0.16022 | 0.050354 | -0.004578 | 0.26093 | -0.16937 | -0.15564 | -0.009156 | 0.004577 | -0.050354 | -0.054932 | 0.01831 | 0.054931 | 0.07782 | 0.027466 | 0.12817 | 0.07782 | 0.42114 | 121.9208 | 0.10529 | 121.8338 | 121.9757 | 121.7606 | 121.8155 | 121.7102 | -121.9254 | -121.8155 | 121.7606 | 121.7834 | 60.878 | 60.91
124.5312 | 121.8796 | -60.8871 | 60.91 | -0.011291 | 0.0059045 | 0.067163 | 0.064341 | 0.00066015 | -0.0029694 | -0.0029331 | -0.0015565 | 0.0028583 | 0.070545 | 0.056557 | -0.0058639 | 0.014966 | -0.00085233 | -0.09613 | 60.9329 | -61.0016 | 60.8185 | -60.6812 | -61.0703 | -61.0931 | -0.064087 | 60.8093 | -60.9512 | 60.8368 | -60.8826 | -60.8826 | -60.8414 | -0.11444 | 0.022888 | -0.091553 | 0.20599 | -0.20599 | -0.1831 | -0.091553 | -0.068664 | -0.064087 | -0.10071 | -0.073242 | 0.004578 | 0.045776 | 0.004578 | 0.10986 | 0.068665 | 0.32044 | 121.8201 | 0.068665 | 121.788 | 121.9345 | 121.7606 | 121.8201 | 121.6965 | -121.9116 | -121.8613 | 121.7056 | 121.7239 | 60.791 | 60.8231
126.2656 | 122.0123 | -60.8597 | 60.878 | 0.0039673 | 0.0061181 | 0.066736 | 0.065196 | 0.00087375 | -0.00083304 | -0.0025057 | 0.0014953 | 0.0037127 | 0.066059 | 0.064461 | -0.00052345 | 0.016675 | -0.0014931 | -0.091553 | 60.9192 | -60.9787 | 60.8917 | -60.6125 | -61.0062 | -61.0199 | -0.018311 | 60.7773 | -60.9238 | 60.9421 | -60.7819 | -60.7819 | -60.7498 | -0.11902 | 0.041198 | 0.013733 | 0.24719 | -0.16022 | -0.14649 | -0.041198 | -0.027466 | -0.064087 | -0.10071 | 0.064087 | 0.07782 | 0.10986 | 0.07782 | 0.17395 | 0.14191 | 0.36621 | 121.8704 | 0.14191 | 121.8658 | 121.8979 | 121.701 | 121.7789 | 121.637 | -121.8567 | -121.8018 | 121.7514 | 121.8018 | 60.7681 | 60.8414
127.9375 | 122.0352 | -60.8414 | 60.878 | -0.0036622 | 0.0024865 | 0.066309 | 0.062846 | -0.0012624 | -0.0012604 | -0.00036951 | -0.0076599 | 0.00072206 | 0.067554 | 0.058693 | -0.0020187 | 0.013685 | -0.00042513 | -0.050354 | 60.9009 | -60.9833 | 60.9512 | -60.5255 | -60.9238 | -60.9741 | 0.082397 | 60.7544 | -60.8963 | 60.9879 | -60.7132 | -60.7132 | -60.7315 | -0.14191 | 0.022888 | 0.073242 | 0.31586 | -0.13275 | -0.082397 | 0.009155 | 0.059509 | -0.054931 | -0.1236 | 0.10986 | 0.12817 | 0.10986 | 0.12817 | 0.16479 | 0.1831 | 0.45776 | 121.9345 | 0.1831 | 121.8842 | 121.8842 | 121.6507 | 121.7422 | 121.5958 | -121.8613 | -121.7743 | 121.7926 | 121.8292 | 60.791 | 60.9238
129.6719 | 122.0169 | -60.8322 | 60.8551 | -0.011291 | 0.0035547 | 0.066095 | 0.063487 | 1.915e-05 | -0.0029694 | -0.0020785 | -0.0046081 | 0.0032855 | 0.067768 | 0.063393 | -0.0037277 | 0.01753 | -0.0053385 | -0.027466 | 60.8871 | -60.9558 | 60.965 | -60.5026 | -60.91 | -60.9467 | 0.073242 | 60.8002 | -60.8734 | 60.9833 | -60.7178 | -60.7224 | -60.7361 | -0.1236 | 0.032043 | 0.10986 | 0.32959 | -0.11444 | -0.07782 | 0.009156 | 0.045777 | -0.041199 | -0.054932 | 0.12817 | 0.11444 | 0.09613 | 0.10986 | 0.13733 | 0.15106 | 0.45319 | 121.9208 | 0.15564 | 121.8567 | 121.843 | 121.6736 | 121.7194 | 121.6324 | -121.8109 | -121.7285 | 121.7972 | 121.8155 | 60.8047 | 60.9055
131.4062 | 122.0169 | -60.8551 | 60.8231 | -0.011291 | 0.0050501 | 0.065881 | 0.066477 | -0.0023306 | -0.00061944 | -0.0027195 | -0.0046081 | 0.0045673 | 0.069049 | 0.061684 | 0.00097195 | 0.017103 | -0.0012795 | -0.054932 | 60.8597 | -60.9604 | 60.9009 | -60.6079 | -61.0245 | -61.0565 | 0.032043 | 60.7361 | -60.965 | 60.9375 | -60.8002 | -60.8002 | -60.759 | -0.10529 | 0.036621 | 0.07782 | 0.24719 | -0.20142 | -0.16937 | -0.096131 | -0.064087 | -0.10986 | -0.086975 | 0.11444 | 0.054932 | 0.096131 | 0.054932 | 0.20599 | 0.16479 | 0.35248 | 121.8613 | 0.16479 | 121.9025 | 121.8201 | 121.701 | 121.7148 | 121.5912 | -121.7834 | -121.788 | 121.756 | 121.7926 | 60.8002 | 60.8871
133.1562 | 121.8887 | -60.9238 | 60.878 | 0.0039673 | 0.0059045 | 0.068018 | 0.066264 | -0.002117 | -0.0023284 | -0.0014377 | -0.0076599 | 0.0037127 | 0.068622 | 0.062965 | -0.0024461 | 0.016462 | 0.0014975 | -0.12817 | 60.9055 | -61.0519 | 60.7773 | -60.759 | -61.1664 | -61.1618 | -0.11902 | 60.791 | -60.9833 | 60.8185 | -60.9375 | -60.9512 | -60.8643 | -0.12817 | 0.027466 | -0.10071 | 0.16479 | -0.23804 | -0.24262 | -0.10986 | -0.11444 | -0.059509 | -0.086975 | -0.05951 | -0.013733 | 0.059509 | -0.027466 | 0.11902 | 0.032043 | 0.29297 | 121.8292 | 0.045776 | 121.8018 | 121.9574 | 121.7743 | 121.8292 | 121.7148 | -121.9299 | -121.8613 | 121.701 | 121.7422 | 60.7956 | 60.8047
134.9062 | 121.9025 | -60.9329 | 60.8414 | 0.0039673 | 0.0063317 | 0.068872 | 0.066905 | -0.0036124 | -0.0023284 | -0.0014377 | -0.0015565 | 0.0049945 | 0.069477 | 0.054634 | -0.0020187 | 0.014112 | -0.0021341 | -0.045776 | 60.9421 | -61.0382 | 60.8322 | -60.672 | -61.0977 | -61.1343 | -0.032043 | 60.7956 | -60.9787 | 60.8185 | -60.9375 | -60.9512 | -60.8734 | -0.10529 | 0.10071 | -0.009156 | 0.26093 | -0.20142 | -0.1648 | -0.09613 | -0.059509 | -0.045777 | -0.045777 | -0.022889 | -0.004578 | 0.059509 | -0.018311 | 0.10529 | 0.027466 | 0.36621 | 121.8704 | 0.041199 | 121.7972 | 121.9803 | 121.7743 | 121.875 | 121.7285 | -121.8796 | -121.8201 | 121.7651 | 121.7514 | 60.8871 | 60.9009
136.6562 | 121.9025 | -60.9055 | 60.9238 | -0.0036622 | 0.0035547 | 0.067377 | 0.067973 | 0.0034372 | -0.00083304 | 5.7688e-05 | 0.013702 | 0.0039265 | 0.070972 | 0.056343 | -0.0067185 | 0.012403 | -0.0017069 | -0.054932 | 60.997 | -61.0565 | 60.8368 | -60.6491 | -61.0565 | -61.0703 | -0.050354 | 60.8276 | -60.9924 | 60.8139 | -60.8734 | -60.8871 | -60.8459 | -0.15106 | 0.073242 | -0.086975 | 0.25635 | -0.16479 | -0.15106 | -0.013732 | 0 | -0.086975 | -0.09613 | -0.10986 | 0.032044 | 0.05951 | 0.018311 | 0.14648 | 0.10529 | 0.40741 | 121.8933 | 0.11902 | 121.8063 | 122.0535 | 121.8201 | 121.9025 | 121.7331 | -121.9803 | -121.9162 | 121.7422 | 121.7194 | 60.8505 | 60.8551
138.3906 | 121.9162 | -60.8643 | 60.8871 | -0.011291 | 0.0067591 | 0.065668 | 0.064341 | -0.003826 | -0.0027556 | -0.0012241 | -0.0076599 | 0.0030719 | 0.068622 | 0.067665 | -0.0060777 | 0.014112 | -0.0023477 | -0.032043 | 60.9238 | -60.9741 | 60.8826 | -60.5896 | -60.9879 | -61.0428 | -0.013733 | 60.7773 | -60.9283 | 60.8597 | -60.8505 | -60.8322 | -60.8322 | -0.10986 | 0.036621 | -0.004578 | 0.27466 | -0.17853 | -0.1236 | -0.068665 | -0.013733 | -0.064087 | -0.10986 | -0.027466 | 0.013733 | 0.032044 | 0.032044 | 0.096131 | 0.096131 | 0.38452 | 121.8567 | 0.07782 | 121.788 | 121.8979 | 121.7056 | 121.788 | 121.6415 | -121.8613 | -121.8155 | 121.7468 | 121.7239 | 60.8322 | 60.8505
140.0625 | 121.9986 | -60.8459 | 60.8368 | 0.034485 | 0.0069727 | 0.070154 | 0.066691 | 0.0017282 | -0.00040584 | -0.0018649 | 0.0075989 | 0.0022175 | 0.069263 | 0.063606 | -0.00052345 | 0.016034 | -0.0046975 | -0.054932 | 60.8826 | -61.0474 | 60.9375 | -60.5484 | -60.9879 | -61.0062 | 0.050354 | 60.7544 | -60.9375 | 60.9558 | -60.791 | -60.7956 | -60.759 | -0.20142 | 0.045776 | 0.10071 | 0.29755 | -0.16022 | -0.14191 | 0.041198 | 0.059509 | -0.091553 | -0.082397 | 0.11902 | 0.054931 | 0.086975 | 0.050354 | 0.17853 | 0.14191 | 0.49896 | 121.9849 | 0.14648 | 121.8933 | 121.9299 | 121.6919 | 121.7285 | 121.6003 | -121.8842 | -121.7743 | 121.7834 | 121.8018 | 60.791 | 60.8963
141.8125 | 121.9849 | -60.8871 | 60.8597 | 0.057373 | 0.0076135 | 0.066949 | 0.068614 | 0.0017282 | -0.00019224 | -0.00015591 | 0.010651 | 0.0026447 | 0.069904 | 0.065102 | 0.0011855 | 0.015607 | -0.0019205 | -0.027466 | 60.8917 | -61.0291 | 60.9238 | -60.5392 | -60.9879 | -61.0016 | 0.054932 | 60.7498 | -60.9329 | 60.9375 | -60.7773 | -60.8002 | -60.759 | -0.14191 | 0.032044 | 0.064087 | 0.3479 | -0.11444 | -0.10071 | 0.027466 | 0.041199 | -0.045776 | -0.10986 | 0.07782 | 0.10986 | 0.12817 | 0.086975 | 0.17395 | 0.13275 | 0.48981 | 121.9528 | 0.15564 | 121.8704 | 121.9208 | 121.6827 | 121.7789 | 121.637 | -121.8887 | -121.7926 | 121.8109 | 121.8246 | 60.8597 | 60.9421
143.5469 | 121.8979 | -60.9192 | 60.8688 | 0.011597 | 0.0065453 | 0.065454 | 0.066477 | 0.0019418 | -0.0023284 | -0.00058311 | 0.0014953 | 0.0022175 | 0.070118 | 0.067024 | -0.0043687 | 0.01518 | -0.0036295 | -0.036621 | 60.8963 | -61.0748 | 60.8414 | -60.6583 | -61.0657 | -61.0886 | -0.004578 | 60.791 | -60.9375 | 60.8368 | -60.8871 | -60.9009 | -60.8414 | -0.15564 | 0.027466 | -0.027465 | 0.26093 | -0.16937 | -0.14648 | -0.013733 | 0.009155 | -0.018311 | -0.077819 | -0.032043 | 0.032043 | 0.077819 | 0.01831 | 0.09613 | 0.036621 | 0.41656 | 121.9162 | 0.050354 | 121.7743 | 121.9711 | 121.7285 | 121.8155 | 121.7102 | -121.9437 | -121.8063 | 121.7606 | 121.756 | 60.8826 | 60.9146
145.2812 | 121.9986 | -60.8414 | 60.8917 | -0.011291 | 0.0039819 | 0.064813 | 0.061778 | -0.003826 | -0.0021148 | -0.0025057 | -0.0076599 | -0.00055974 | 0.0667 | 0.067665 | -0.0056503 | 0.01518 | 2.068e-06 | -0.022888 | 60.8917 | -60.9512 | 60.9375 | -60.5118 | -60.9329 | -60.965 | 0.07782 | 60.7819 | -60.8917 | 60.9695 | -60.7224 | -60.7178 | -60.7315 | -0.10986 | 0 | 0.045776 | 0.32959 | -0.1236 | -0.091552 | -0.013733 | 0.018311 | -0.050354 | -0.10986 | 0.077819 | 0.11902 | 0.10986 | 0.1236 | 0.16022 | 0.17395 | 0.43945 | 121.8887 | 0.16937 | 121.8613 | 121.843 | 121.6736 | 121.7331 | 121.6232 | -121.843 | -121.7834 | 121.7789 | 121.8109 | 60.8185 | 60.9192
146.9531 | 121.8842 | -60.9009 | 60.8826 | -0.011291 | 0.0061181 | 0.06759 | 0.066264 | -0.00083525 | -0.001474 | -0.0016513 | -0.0015565 | 0.0024311 | 0.070118 | 0.06382 | -0.0050095 | 0.013257 | -0.00021153 | -0.068665 | 60.9192 | -61.0016 | 60.8322 | -60.6583 | -61.0611 | -61.084 | -0.068665 | 60.8093 | -60.9375 | 60.8368 | -60.8734 | -60.8826 | -60.8551 | -0.10071 | 0.036621 | -0.050354 | 0.24262 | -0.1831 | -0.16022 | -0.082397 | -0.059509 | -0.036621 | -0.073242 | -0.045776 | 0.027466 | 0.045776 | 0.018311 | 0.082397 | 0.054932 | 0.34332 | 121.8338 | 0.064087 | 121.7743 | 121.9208 | 121.7468 | 121.8201 | 121.7102 | -121.8842 | -121.8201 | 121.7331 | 121.7377 | 60.8322 | 60.8322
148.6875 | 121.9208 | -60.8963 | 60.9055 | 0.049744 | 0.0063317 | 0.066522 | 0.065409 | 0.0017282 | -0.0033966 | -0.0010105 | 0.013702 | 0.0056355 | 0.068622 | 0.061043 | -0.0041551 | 0.014325 | -0.0017069 | -0.050354 | 60.9558 | -61.0428 | 60.8185 | -60.6995 | -61.0611 | -61.084 | -0.068665 | 60.8505 | -60.965 | 60.8368 | -60.8597 | -60.8734 | -60.8414 | -0.14648 | 0.050354 | -0.086976 | 0.19684 | -0.18768 | -0.16479 | -0.041198 | -0.01831 | -0.068665 | -0.054932 | -0.068665 | 0.036621 | 0.054931 | 0.022888 | 0.1236 | 0.091553 | 0.34332 | 121.8613 | 0.10529 | 121.8018 | 121.9986 | 121.8155 | 121.8521 | 121.7468 | -121.9482 | -121.8704 | 121.7148 | 121.7331 | 60.8459 | 60.8276
150.4219 | 121.9391 | -60.9283 | 60.8414 | 0.019226 | 0.0061181 | 0.069513 | 0.068186 | 1.915e-05 | -0.00083304 | 0.0039029 | 0.0014953 | 0.0045673 | 0.070972 | 0.057411 | -0.00095065 | 0.014753 | -0.0042703 | -0.036621 | 60.9146 | -61.0336 | 60.8414 | -60.6583 | -61.0565 | -61.0977 | 0.004578 | 60.7727 | -60.9695 | 60.8597 | -60.8688 | -60.8688 | -60.8322 | -0.10529 | 0.073242 | 0 | 0.27008 | -0.16937 | -0.12817 | -0.064087 | -0.022889 | -0.041198 | -0.068665 | 0.01831 | 0.05951 | 0.096131 | 0.05951 | 0.13733 | 0.10071 | 0.37537 | 121.875 | 0.10071 | 121.8292 | 121.9482 | 121.7422 | 121.843 | 121.7011 | -121.875 | -121.8109 | 121.7697 | 121.788 | 60.8917 | 60.9329
152.1094 | 122.0398 | -60.8368 | 60.8597 | -0.011291 | 0.0039819 | 0.067804 | 0.064982 | -0.0029714 | -0.0036102 | -0.0029331 | -0.0046081 | 0.0011493 | 0.069477 | 0.061256 | -0.0022325 | 0.015394 | 0.0025657 | -0.045776 | 60.8963 | -60.9741 | 60.9375 | -60.5255 | -60.9375 | -60.9604 | 0.068665 | 60.7361 | -60.8963 | 60.9695 | -60.704 | -60.704 | -60.7086 | -0.13733 | 0.036621 | 0.07782 | 0.31128 | -0.1236 | -0.10071 | 0.013733 | 0.036621 | -0.059509 | -0.1236 | 0.10986 | 0.13275 | 0.12817 | 0.13275 | 0.18768 | 0.19226 | 0.44861 | 121.9116 | 0.19226 | 121.8658 | 121.8704 | 121.6324 | 121.7331 | 121.5729 | -121.8338 | -121.756 | 121.7743 | 121.8063 | 60.791 | 60.9055
153.8594 | 121.9116 | -69.2276 | 52.4963 | -0.0036622 | 0.0056909 | 0.066309 | 0.066691 | 0.00023275 | -0.00040584 | -0.0010105 | -0.0046081 | 0.0030719 | 0.069904 | 0.058479 | -0.00030965 | 0.014753 | -0.0019205 | -0.13733 | 52.5238 | -69.3924 | 52.4094 | -69.0399 | -69.4656 | -69.4839 | -0.13275 | 52.4048 | -69.3283 | 52.478 | -69.2413 | -69.2551 | -69.1772 | -0.16479 | 0.027466 | -0.086975 | 0.18768 | -0.25635 | -0.23804 | -0.091553 | -0.073242 | -0.10071 | -0.091553 | -0.018311 | -0.013733 | 0.050354 | -0.027466 | 0.15106 | 0.073242 | 0.35248 | 121.8018 | 0.086975 | 121.8063 | 121.9162 | 121.7331 | 121.7514 | 121.6324 | -121.8887 | -121.8246 | 121.637 | 121.7056 | 69.0903 | 69.0948
155.5938 | 121.875 | -70.4224 | 51.3428 | -0.0036622 | 0.0050501 | 0.068445 | 0.067546 | 0.0027964 | -0.0027556 | -0.00079691 | -0.0015565 | 0.0039265 | 0.068195 | 0.063179 | -0.00030965 | 0.016462 | -0.0010659 | -0.13275 | 51.3474 | -70.5643 | 51.265 | -70.1797 | -70.6146 | -70.6284 | -0.15106 | 51.2695 | -70.4819 | 51.3062 | -70.3903 | -70.4269 | -70.3171 | -0.14191 | 0.004578 | -0.077819 | 0.24261 | -0.20599 | -0.19226 | -0.064087 | -0.050354 | -0.05951 | -0.073242 | -0.036621 | 0.032043 | 0.10529 | -0.004578 | 0.16479 | 0.054932 | 0.38452 | 121.8292 | 0.091553 | 121.788 | 121.9116 | 121.7514 | 121.7697 | 121.6919 | -121.907 | -121.8246 | 121.6873 | 121.7285 | 70.2896 | 70.2713
157.3594 | 122.0215 | -70.5139 | 51.1688 | 0.034485 | 0.0073999 | 0.070367 | 0.067118 | 0.0023692 | -0.0016876 | -0.0025057 | 0.0075989 | 0.0015765 | 0.070118 | 0.059975 | 0.00011755 | 0.015821 | -0.0036295 | -0.09613 | 51.1734 | -70.7062 | 51.2741 | -70.1294 | -70.6192 | -70.6512 | 0.013733 | 51.0773 | -70.6146 | 51.3016 | -70.3995 | -70.4086 | -70.3629 | -0.19226 | 0.004578 | 0.10529 | 0.38452 | -0.13733 | -0.10529 | 0.054932 | 0.086975 | -0.10071 | -0.091552 | 0.13275 | 0.11444 | 0.15106 | 0.10529 | 0.25177 | 0.20599 | 0.57678 | 121.9803 | 0.21515 | 121.9162 | 121.8796 | 121.6919 | 121.6873 | 121.5912 | -121.875 | -121.7834 | 121.788 | 121.8155 | 70.4178 | 70.5276
159.0312 | 121.8887 | -70.784 | 50.9811 | -0.0036622 | 0.0067591 | 0.065668 | 0.067332 | 0.00087375 | -0.00083304 | -0.0020785 | -0.0015565 | 0.0030719 | 0.068195 | 0.058693 | -0.0028733 | 0.016034 | 0.0017111 | -0.15564 | 51.0178 | -70.9167 | 50.9079 | -70.5414 | -70.9671 | -70.9854 | -0.13733 | 50.8942 | -70.8389 | 50.972 | -70.7245 | -70.7245 | -70.6558 | -0.13275 | 0.036621 | -0.073242 | 0.24262 | -0.20142 | -0.1831 | -0.068665 | -0.050354 | -0.054931 | -0.086975 | -0.009155 | 0.05951 | 0.12817 | 0.05951 | 0.1831 | 0.11444 | 0.37537 | 121.8246 | 0.11444 | 121.8109 | 121.9345 | 121.7331 | 121.8018 | 121.6782 | -121.8979 | -121.8201 | 121.6919 | 121.756 | 70.6284 | 70.6467
160.75 | 121.9757 | -60.8963 | 60.8368 | -0.011291 | 0.0046227 | 0.067804 | 0.064768 | 1.915e-05 | -0.002542 | 0.0011257 | -0.0015565 | -0.0012005 | 0.069263 | 0.06147 | -0.0024461 | 0.016462 | 0.0012839 | -0.091553 | 60.8505 | -60.9879 | 60.8597 | -60.5988 | -60.9924 | -61.0291 | 0.032043 | 60.7636 | -60.9055 | 60.91 | -60.759 | -60.7544 | -60.7407 | -0.091553 | 0.013733 | 0.022888 | 0.29755 | -0.13275 | -0.096131 | -0.041199 | -0.004578 | -0.009156 | -0.073242 | 0.073242 | 0.13733 | 0.15564 | 0.14191 | 0.16479 | 0.15106 | 0.3891 | 121.8475 | 0.14648 | 121.8155 | 121.8384 | 121.669 | 121.7468 | 121.6599 | -121.8246 | -121.7422 | 121.756 | 121.8063 | 60.8047 | 60.9283
162.4219 | 121.8567 | -60.9558 | 60.8368 | -0.0036622 | 0.0027001 | 0.065668 | 0.062846 | -0.00083525 | -0.0053192 | -0.0016513 | -0.0046081 | 0.0017901 | 0.06969 | 0.05677 | -0.0041551 | 0.012403 | 0.00042947 | -0.10529 | 60.8734 | -61.0336 | 60.759 | -60.7224 | -61.1069 | -61.1343 | -0.059509 | 60.7681 | -60.9879 | 60.7681 | -60.91 | -60.9146 | -60.8734 | -0.077819 | 0.036621 | -0.07782 | 0.23346 | -0.17853 | -0.15106 | -0.10071 | -0.073243 | -0.032043 | -0.068665 | -0.068665 | 0.045777 | 0.082398 | 0.041199 | 0.11444 | 0.073242 | 0.31128 | 121.7926 | 0.07782 | 121.756 | 121.907 | 121.756 | 121.8292 | 121.7239 | -121.8704 | -121.8246 | 121.7148 | 121.7239 | 60.8505 | 60.8963
164.0938 | 121.994 | -60.8871 | 60.8231 | -0.0036622 | 0.0037683 | 0.065027 | 0.064555 | 0.0038644 | -0.0040374 | -0.0031467 | -0.0046081 | 0.00093566 | 0.067768 | 0.067665 | -0.0026597 | 0.017103 | -0.0019205 | -0.054932 | 60.8551 | -61.0016 | 60.8826 | -60.5667 | -60.9924 | -60.997 | 0.082397 | 60.7407 | -60.9283 | 60.9146 | -60.7681 | -60.7681 | -60.7407 | -0.11444 | 0.032044 | 0.059509 | 0.32044 | -0.10986 | -0.10529 | 0.004578 | 0.009155 | -0.041199 | -0.082397 | 0.091553 | 0.11902 | 0.14648 | 0.11902 | 0.18768 | 0.16022 | 0.43488 | 121.8842 | 0.16022 | 121.843 | 121.8567 | 121.669 | 121.7422 | 121.6278 | -121.8246 | -121.7514 | 121.7697 | 121.8018 | 60.8322 | 60.9695
165.8281 | 121.8887 | -60.9558 | 60.8093 | -0.0036622 | 0.0061181 | 0.066309 | 0.066264 | 1.915e-05 | -0.0027556 | -0.0035739 | -0.0015565 | 0.0020039 | 0.067554 | 0.056343 | -0.0030869 | 0.014966 | -0.00085233 | -0.036621 | 60.8139 | -61.0886 | 60.791 | -60.6995 | -61.1023 | -61.1298 | 0 | 60.7224 | -60.9924 | 60.7956 | -60.9192 | -60.9375 | -60.878 | -0.13275 | 0.004578 | -0.01831 | 0.25635 | -0.17395 | -0.14648 | -0.041199 | -0.013733 | -0.036621 | -0.086975 | -0.013733 | 0.036622 | 0.07782 | 0.018311 | 0.11444 | 0.054932 | 0.3891 | 121.8796 | 0.073243 | 121.788 | 121.9025 | 121.7148 | 121.7697 | 121.6782 | -121.8979 | -121.8018 | 121.7468 | 121.7514 | 60.9192 | 60.9558
167.5 | 121.8658 | -60.9604 | 60.8002 | -0.0036622 | 0.0037683 | 0.066949 | 0.067118 | 0.0027964 | -0.0010468 | 0.00069849 | -0.0046081 | 0.0034991 | 0.069049 | 0.060829 | -0.0033005 | 0.016462 | -0.0025613 | -0.10529 | 60.8139 | -61.0977 | 60.7178 | -60.8002 | -61.2076 | -61.2076 | -0.12817 | 60.6995 | -61.0336 | 60.7315 | -61.0062 | -61.0107 | -60.9192 | -0.13733 | 0.013733 | -0.082398 | 0.16022 | -0.24719 | -0.24719 | -0.10986 | -0.10986 | -0.073242 | -0.10071 | -0.068665 | -0.045777 | 0.041199 | -0.050354 | 0.11444 | 0.022888 | 0.29755 | 121.8155 | 0.027465 | 121.7651 | 121.9116 | 121.7331 | 121.7743 | 121.6599 | -121.8979 | -121.8338 | 121.6782 | 121.6919 | 60.8551 | 60.8322
169.2344 | 121.8842 | -61.0062 | 60.7773 | 0.034485 | 0.0050501 | 0.067804 | 0.067118 | -0.00019445 | -0.0012604 | -0.0018649 | 0.0075989 | 0.0024311 | 0.070545 | 0.059761 | -0.0052231 | 0.012403 | -0.0010659 | -0.032043 | 60.8414 | -61.1526 | 60.7086 | -60.7864 | -61.1526 | -61.1755 | -0.054932 | 60.704 | -61.0611 | 60.7132 | -60.9833 | -60.9833 | -60.9238 | -0.14648 | 0.064087 | -0.068665 | 0.21973 | -0.16937 | -0.14648 | -0.022888 | 0 | -0.054931 | -0.073242 | -0.064087 | 0.022889 | 0.082398 | 0.022889 | 0.13733 | 0.07782 | 0.36621 | 121.8613 | 0.07782 | 121.7743 | 121.994 | 121.7651 | 121.8475 | 121.7102 | -121.9299 | -121.8384 | 121.7148 | 121.7194 | 60.9741 | 60.9512
170.9062 | 121.8658 | -60.9833 | 60.791 | -0.018921 | 0.0035547 | 0.066095 | 0.063914 | 0.0045054 | -0.0027556 | -0.0029331 | -0.0046081 | 0.0026447 | 0.070331 | 0.05677 | -0.0052231 | 0.015821 | -0.00042513 | -0.10529 | 60.8322 | -61.1069 | 60.6812 | -60.7819 | -61.1664 | -61.203 | -0.064087 | 60.6949 | -61.0291 | 60.7132 | -60.965 | -60.9787 | -60.9283 | -0.1236 | 0.041198 | -0.10986 | 0.20142 | -0.21973 | -0.18311 | -0.09613 | -0.059509 | -0.045777 | -0.096131 | -0.07782 | 0.01831 | 0.054931 | 0.004577 | 0.10071 | 0.050354 | 0.32501 | 121.788 | 0.064087 | 121.7422 | 121.9391 | 121.7239 | 121.8155 | 121.6782 | -121.8979 | -121.8201 | 121.6644 | 121.6965 | 60.878 | 60.9192
172.6406 | 121.8979 | -61.084 | 60.6766 | 0.026856 | 0.0061181 | 0.068445 | 0.06605 | -0.001476 | -0.0038238 | -0.0012241 | 0.013702 | 0.0047809 | 0.070118 | 0.062324 | -0.0020187 | 0.016462 | 0.00064307 | 0.022888 | 60.7315 | -61.2213 | 60.5896 | -60.8826 | -61.2442 | -61.2854 | 0.009155 | 60.585 | -61.1801 | 60.6262 | -61.0474 | -61.0703 | -61.0107 | -0.13733 | 0.054931 | -0.086975 | 0.20142 | -0.20142 | -0.16022 | -0.064087 | -0.022889 | -0.096131 | -0.091553 | -0.050354 | 0.036621 | 0.073242 | 0.013733 | 0.16937 | 0.10986 | 0.33875 | 121.8109 | 0.13275 | 121.8063 | 121.9528 | 121.7651 | 121.8155 | 121.669 | -121.8979 | -121.8567 | 121.6736 | 121.7102 | 61.1069 | 61.0931
174.375 | 121.8063 | -70.9488 | 50.8301 | -0.0036622 | 0.0054773 | 0.067804 | 0.065196 | 0.00066015 | -0.0016876 | -0.00079691 | 0.0014953 | 0.0020039 | 0.070118 | 0.061684 | -0.0033005 | 0.01753 | -0.0027749 | 2.4994 | 50.7339 | -71.1227 | 50.8667 | -70.4819 | -70.9396 | -70.9717 | 2.4078 | 50.9033 | -70.8664 | 50.8987 | -70.7245 | -70.7886 | -70.8069 | -0.17395 | -0.09613 | 0.036621 | 0.46692 | -0.022888 | 0.009156 | 0.15106 | 0.18311 | 0.082398 | 0.073242 | 0.068665 | 0.22431 | 0.14191 | 0.16022 | 0.059509 | 0.07782 | 0.64087 | 121.9894 | 0.14191 | 121.7651 | 121.8567 | 121.7697 | 121.6827 | 121.8521 | -121.9528 | -121.6965 | 121.8155 | 121.8475 | 73.4482 | 73.3566
176.0625 | 121.9528 | -70.3995 | 51.329 | -0.011291 | 0.0048365 | 0.066309 | 0.064128 | -0.0042532 | -0.001474 | -0.0025057 | -0.0076599 | -0.00013254 | 0.068622 | 0.064674 | -0.0041551 | 0.016248 | -0.00042513 | -0.082397 | 51.4023 | -70.4544 | 51.3565 | -70.0104 | -70.4773 | -70.5505 | -0.073242 | 51.123 | -70.5002 | 51.4252 | -70.1889 | -70.1843 | -70.1889 | -0.054932 | 0.073242 | 0.027465 | 0.3891 | -0.15106 | -0.07782 | -0.09613 | -0.022888 | -0.10071 | -0.20599 | 0.09613 | 0.21057 | 0.21057 | 0.21515 | 0.31128 | 0.31586 | 0.44403 | 121.8109 | 0.31128 | 121.9254 | 121.8567 | 121.6232 | 121.8018 | 121.5225 | -121.7834 | -121.8292 | 121.756 | 121.8246 | 70.3171 | 70.3262
177.8125 | 121.907 | -69.7861 | 52.034 | -0.0036622 | 0.0031275 | 0.067377 | 0.063487 | -0.001476 | -0.0023284 | -0.00058311 | 0.0014953 | 0.0015765 | 0.069049 | 0.05912 | -0.0047959 | 0.01518 | 0.0019247 | -0.041199 | 52.002 | -69.8456 | 52.0844 | -69.2871 | -69.7449 | -69.7952 | 0.09613 | 51.8875 | -69.7403 | 52.1072 | -69.5343 | -69.5297 | -69.5435 | -0.059509 | -0.032044 | 0.050354 | 0.49896 | -0.009155 | 0.041199 | 0.050354 | 0.10071 | 0.045777 | -0.14648 | 0.073242 | 0.25177 | 0.24262 | 0.25635 | 0.19684 | 0.21057 | 0.55847 | 121.9299 | 0.20599 | 121.8475 | 121.8475 | 121.6278 | 121.788 | 121.6736 | -121.8796 | -121.7743 | 121.8704 | 121.8933 | 69.7449 | 69.8822
179.5625 | 121.9482 | -71.4386 | 50.2533 | -0.018921 | 0.0035547 | 0.065241 | 0.065196 | -0.0036124 | -0.00061944 | 0.00091209 | -0.0015565 | 8.1264e-05 | 0.067554 | 0.066811 | -0.0011643 | 0.016034 | -0.00021153 | -0.082397 | 50.2899 | -71.5347 | 50.3494 | -71.0266 | -71.4661 | -71.4981 | 0.041199 | 50.1572 | -71.4798 | 50.3723 | -71.2418 | -71.2555 | -71.2326 | -0.09613 | 0.036621 | 0.09613 | 0.41199 | -0.059509 | -0.027465 | 0.036621 | 0.068665 | -0.041198 | -0.09613 | 0.11902 | 0.19684 | 0.20599 | 0.18311 | 0.24719 | 0.2243 | 0.50812 | 121.8842 | 0.23804 | 121.8521 | 121.8246 | 121.637 | 121.7285 | 121.5958 | -121.788 | -121.7331 | 121.788 | 121.8109 | 71.3562 | 71.4798
181.2344 | 121.8979 | -73.2422 | 48.4177 | 0.019226 | 0.0035547 | 0.067804 | 0.068614 | -0.00083525 | -0.00083304 | -0.0027195 | 0.0014953 | 0.0032855 | 0.069477 | 0.057625 | -0.0037277 | 0.019666 | -0.0032021 | -0.11444 | 48.436 | -73.4299 | 48.4543 | -72.9218 | -73.3841 | -73.4116 | -0.032043 | 48.3398 | -73.3475 | 48.4497 | -73.1552 | -73.1598 | -73.1277 | -0.18768 | 0.01831 | 0.036621 | 0.32043 | -0.16937 | -0.14191 | 0.018311 | 0.045777 | -0.10529 | -0.07782 | 0.032043 | 0.086975 | 0.11444 | 0.082397 | 0.21973 | 0.18768 | 0.50812 | 121.8842 | 0.19226 | 121.7972 | 121.8658 | 121.6873 | 121.6782 | 121.582 | -121.8475 | -121.7651 | 121.6965 | 121.6919 | 73.1277 | 73.2101
182.9844 | 121.8887 | -72.3358 | 49.4064 | 0.026856 | 0.0052637 | 0.067377 | 0.067546 | 0.0025828 | -0.0021148 | -0.0025057 | 0.0075989 | 0.0047809 | 0.070545 | 0.05912 | -0.0033005 | 0.015607 | -0.0036295 | 0.013733 | 49.4522 | -72.4731 | 49.4293 | -71.9833 | -72.4091 | -72.4548 | -0.018311 | 49.3515 | -72.3953 | 49.3881 | -72.226 | -72.258 | -72.1939 | -0.13733 | 0.045776 | 0.022888 | 0.35248 | -0.11902 | -0.073243 | 0.018311 | 0.064087 | -0.05951 | -0.054932 | -0.01831 | 0.10986 | 0.14191 | 0.077819 | 0.20142 | 0.13733 | 0.48981 | 121.9025 | 0.16937 | 121.7834 | 121.9254 | 121.7468 | 121.788 | 121.6873 | -121.8796 | -121.8018 | 121.7651 | 121.7239 | 72.3495 | 72.3175
184.7188 | 122.0078 | -109.5612 | 12.0758 | 0.011597 | 0.0039819 | 0.068018 | 0.067332 | -0.00062165 | 2.1362e-05 | -0.0027195 | 0.0014953 | 0.0034991 | 0.070118 | 0.067665 | -0.0043687 | 0.017957 | 0.0014975 | -0.27924 | 12.0712 | -109.8267 | 12.0483 | -109.0576 | -109.6527 | -109.7168 | -0.19684 | 11.9934 | -109.79 | 12.0712 | -109.346 | -109.3781 | -109.3369 | -0.2655 | -0.004578 | -0.027466 | 0.50354 | -0.15564 | -0.091553 | 0.10986 | 0.17395 | -0.22888 | -0.082398 | -0.004578 | 0.21515 | 0.2243 | 0.1831 | 0.45319 | 0.41199 | 0.76904 | 121.875 | 0.44403 | 121.8613 | 121.8979 | 121.7834 | 121.6324 | 121.5546 | -121.9025 | -121.8658 | 121.6095 | 121.6324 | 109.2819 | 109.3643
186.4062 | 122.0032 | -110.2295 | 11.4395 | 0.042114 | 0.0063317 | 0.072504 | 0.064982 | 0.0019418 | 0.0030122 | 0.0017667 | 0.010651 | 0.0028583 | 0.069477 | 0.062752 | 0.00054475 | 0.016675 | -0.0021341 | -0.17395 | 11.4578 | -110.4492 | 11.4944 | -109.5886 | -110.2386 | -110.2982 | -0.07782 | 11.4029 | -110.3851 | 11.4944 | -109.9091 | -109.9548 | -109.8999 | -0.21973 | 0.018311 | 0.054932 | 0.64087 | -0.068665 | -0.009155 | 0.15106 | 0.21057 | -0.15564 | -0.036621 | 0.054932 | 0.32043 | 0.32959 | 0.27466 | 0.48523 | 0.4303 | 0.8606 | 121.9437 | 0.47607 | 121.8796 | 121.907 | 121.788 | 121.6873 | 121.6324 | -121.8887 | -121.8246 | 121.7239 | 121.7239 | 110.0555 | 110.1517
188.1562 | 121.9162 | -110.4584 | 11.261 | 0.034485 | 0.0041955 | 0.068872 | 0.068614 | -0.00019445 | -0.0040374 | 5.7688e-05 | 0.010651 | 0.0028583 | 0.070758 | 0.060402 | -0.0050095 | 0.014325 | -0.00085233 | -0.18768 | 11.2839 | -110.7147 | 11.1786 | -109.9319 | -110.5133 | -110.6186 | -0.19226 | 11.2198 | -110.6598 | 11.2289 | -110.1929 | -110.2341 | -110.1883 | -0.25635 | 0.022889 | -0.082397 | 0.52643 | -0.16022 | -0.054932 | 0.096131 | 0.20142 | -0.20142 | -0.041198 | -0.032043 | 0.2655 | 0.27008 | 0.2243 | 0.4715 | 0.42572 | 0.78278 | 121.8933 | 0.46692 | 121.8887 | 121.9986 | 121.8796 | 121.7422 | 121.6782 | -121.9757 | -121.9208 | 121.637 | 121.6873 | 110.2707 | 110.2661
189.8906 | 121.9345 | -110.8337 | 10.9177 | 0.034485 | 0.0061181 | 0.065668 | 0.067118 | 0.00044655 | -0.0019012 | 0.00027129 | 0.010651 | 0.0032855 | 0.067981 | 0.062752 | -0.0035141 | 0.016462 | -0.00063873 | -0.14191 | 10.9543 | -111.0168 | 10.8673 | -110.2478 | -110.8429 | -110.9299 | -0.14191 | 10.8856 | -110.9985 | 10.8948 | -110.5041 | -110.5728 | -110.495 | -0.18311 | 0.036621 | -0.050354 | 0.58594 | -0.096131 | -0.009156 | 0.086975 | 0.17395 | -0.16479 | -0.032044 | -0.022889 | 0.32959 | 0.33875 | 0.26093 | 0.50354 | 0.42572 | 0.76904 | 121.8842 | 0.49439 | 121.8933 | 121.9711 | 121.8842 | 121.788 | 121.7194 | -121.9345 | -121.9162 | 121.7011 | 121.7285 | 110.6918 | 110.6918
191.5625 | 121.8658 | -111.0718 | 10.7071 | -0.018921 | 0.0069727 | 0.063959 | 0.065837 | 0.00023275 | -0.0023284 | -0.00058311 | -0.0046081 | 0.0015765 | 0.069477 | 0.062324 | -0.0060777 | 0.016034 | -0.0023477 | -0.23804 | 10.6613 | -111.2274 | 10.5789 | -110.4996 | -111.113 | -111.1954 | -0.22888 | 10.6476 | -111.1816 | 10.5972 | -110.7925 | -110.8017 | -110.8017 | -0.15564 | -0.045776 | -0.12817 | 0.5722 | -0.1236 | -0.041199 | 0.032043 | 0.11444 | -0.10986 | -0.059509 | -0.10986 | 0.27923 | 0.27008 | 0.27008 | 0.37994 | 0.37994 | 0.72784 | 121.8063 | 0.3891 | 121.7789 | 121.8887 | 121.8292 | 121.7331 | 121.7194 | -121.9345 | -121.8887 | 121.6507 | 121.669 | 110.8337 | 110.8429
193.3125 | 121.8521 | -111.4426 | 10.3455 | -0.0036622 | 0.00099112 | 0.064172 | 0.064555 | 0.00087375 | -0.002542 | -0.0031467 | -0.0015565 | 0.00093566 | 0.070118 | 0.05912 | -0.0052231 | 0.015607 | 0.00085667 | -0.27466 | 10.3363 | -111.5936 | 10.3638 | -110.8704 | -111.5295 | -111.5891 | -0.23346 | 10.2905 | -111.5524 | 10.199 | -111.1542 | -111.1908 | -111.1267 | -0.15106 | -0.009155 | 0.018311 | 0.5722 | -0.14648 | -0.086975 | 0.004578 | 0.064087 | -0.10986 | -0.054932 | -0.14648 | 0.28839 | 0.31586 | 0.25177 | 0.42572 | 0.36163 | 0.72327 | 121.9574 | 0.39825 | 121.7514 | 121.9299 | 121.843 | 121.7789 | 121.7331 | -121.9391 | -121.8979 | 121.8063 | 121.6415 | 111.1679 | 111.2091
195.0469 | 121.9574 | -111.0764 | 10.6064 | 0.049744 | 0.0050501 | 0.069086 | 0.064555 | -0.00062165 | 0.00023496 | 0.00048489 | 0.010651 | 0.00093566 | 0.070331 | 0.068306 | -0.00030965 | 0.016889 | -0.00021153 | -0.16022 | 10.6018 | -111.2686 | 10.6522 | -110.4263 | -111.058 | -111.1176 | -0.064087 | 10.5743 | -111.1954 | 10.6888 | -110.7651 | -110.8154 | -110.7056 | -0.19226 | -0.004577 | 0.045777 | 0.65002 | -0.041199 | 0.018311 | 0.15106 | 0.21057 | -0.11902 | -0.032043 | 0.082398 | 0.31128 | 0.37079 | 0.26093 | 0.48981 | 0.37994 | 0.84228 | 121.9208 | 0.4303 | 121.8842 | 121.8704 | 121.7697 | 121.6782 | 121.6507 | -121.875 | -121.8018 | 121.7285 | 121.7651 | 110.9161 | 111.0123
196.7188 | 121.8567 | -111.5112 | 10.2539 | -0.0036622 | 0.0029139 | 0.069086 | 0.066691 | -0.0016898 | -0.002542 | -0.0018649 | -0.0015565 | 0.0028583 | 0.069049 | 0.061897 | 0.00011755 | 0.016675 | 0.0019247 | -0.23346 | 10.2722 | -111.6531 | 10.1074 | -110.9711 | -111.6074 | -111.6531 | -0.23346 | 10.2081 | -111.6119 | 10.1807 | -111.2549 | -111.3098 | -111.2045 | -0.14191 | 0.018311 | -0.14648 | 0.54016 | -0.14191 | -0.096131 | 0 | 0.045776 | -0.10071 | -0.045776 | -0.073242 | 0.25635 | 0.3067 | 0.20142 | 0.40741 | 0.30212 | 0.68207 | 121.7606 | 0.35705 | 121.7926 | 121.9254 | 121.8201 | 121.7834 | 121.7194 | -121.907 | -121.8658 | 121.6187 | 121.6919 | 111.2778 | 111.2778
198.4531 | 121.8704 | -111.4151 | 10.3775 | -0.0036622 | 0.0039819 | 0.06759 | 0.06605 | 0.0023692 | -0.0027556 | -0.00079691 | -0.0015565 | 0.0020039 | 0.069904 | 0.05912 | -0.0035141 | 0.016462 | -0.0042703 | -0.21973 | 10.3409 | -111.5891 | 10.2127 | -110.8383 | -111.47 | -111.5295 | -0.20599 | 10.318 | -111.5112 | 10.2814 | -111.145 | -111.1954 | -111.0855 | -0.17395 | -0.036621 | -0.16479 | 0.57678 | -0.11444 | -0.054932 | 0.059509 | 0.11902 | -0.09613 | -0.059509 | -0.09613 | 0.27008 | 0.32959 | 0.21973 | 0.42572 | 0.31586 | 0.75073 | 121.8018 | 0.36621 | 121.7926 | 121.9299 | 121.8292 | 121.756 | 121.7331 | -121.9666 | -121.8887 | 121.6278 | 121.6965 | 111.1954 | 111.2091
200.1875 | 121.9528 | -111.8271 | 9.8969 | 0.042114 | 0.0035547 | 0.069086 | 0.0684 | 0.00023275 | 0.00066216 | -0.0012241 | 0.013702 | 0.0015765 | 0.073536 | 0.064888 | -0.00095065 | 0.01988 | 0.0014975 | -0.18768 | 9.8877 | -111.9827 | 9.9243 | -111.1679 | -111.7996 | -111.8546 | -0.10986 | 9.8557 | -111.9553 | 9.9197 | -111.4746 | -111.4883 | -111.4655 | -0.15564 | -0.009156 | 0.027465 | 0.65918 | -0.027466 | 0.027465 | 0.12817 | 0.1831 | -0.12817 | -0.041199 | 0.022888 | 0.35248 | 0.36163 | 0.33875 | 0.48981 | 0.46692 | 0.81482 | 121.907 | 0.48065 | 121.875 | 121.8704 | 121.8109 | 121.7148 | 121.6827 | -121.8796 | -121.8521 | 121.7514 | 121.7468 | 111.6394 | 111.7172
201.9219 | 121.8567 | -111.969 | 9.8328 | -0.0036622 | 0.0063317 | 0.064386 | 0.066691 | -0.003185 | -0.0029694 | -0.0012241 | 0.016754 | 0.0043537 | 0.071399 | 0.057838 | -0.0065049 | 0.014539 | 0.0010703 | -0.21973 | 9.8236 | -112.1658 | 9.668 | -111.2961 | -111.85 | -112.0697 | -0.17395 | 9.8007 | -112.0468 | 9.7 | -111.6943 | -111.5936 | -111.5799 | -0.19684 | -0.009156 | -0.16479 | 0.67291 | -0.10071 | 0.11902 | 0.096131 | 0.31586 | -0.07782 | -0.032044 | -0.13275 | 0.27466 | 0.3891 | 0.37537 | 0.46692 | 0.45319 | 0.86975 | 121.8338 | 0.35248 | 121.7468 | 121.9894 | 121.8475 | 121.7926 | 121.7697 | -121.9986 | -121.8796 | 121.637 | 121.669 | 111.7493 | 111.795
203.5938 | 121.7606 | -67.2272 | 54.6341 | -0.0036622 | 0.0059045 | 0.065454 | 0.064555 | -0.001476 | -0.001474 | -0.00036951 | -0.0015565 | 0.0028583 | 0.068409 | 0.057411 | -0.0033005 | 0.015607 | 0.0021383 | -0.091553 | 54.6341 | -67.2455 | 54.4922 | -66.9205 | -67.3462 | -67.3782 | -0.086975 | 54.5013 | -67.1677 | 54.5563 | -67.1082 | -67.1265 | -67.0166 | -0.01831 | 0 | -0.14191 | 0.3067 | -0.15106 | -0.11902 | -0.13275 | -0.10071 | 0.059509 | -0.13275 | -0.07782 | 0.11902 | 0.21057 | 0.10071 | 0.15106 | 0.041199 | 0.32501 | 121.7377 | 0.05951 | 121.7239 | 121.8796 | 121.669 | 121.8613 | 121.7285 | -121.8796 | -121.8018 | 121.7194 | 121.7834 | 67.1356 | 67.1402
205.3281 | 121.8109 | -67.7353 | 54.0665 | 0.026856 | 0.0080407 | 0.067377 | 0.06605 | 0.00087375 | -0.00061944 | -0.0016513 | 0.013702 | 0.0026447 | 0.070118 | 0.059547 | -0.0069321 | 0.016034 | -0.0017069 | -0.045776 | 54.1077 | -67.8543 | 53.9978 | -67.4286 | -67.8314 | -67.8589 | -0.045776 | 53.9932 | -67.7902 | 54.0024 | -67.6163 | -67.6346 | -67.5522 | -0.11902 | 0.041199 | -0.068664 | 0.3067 | -0.1236 | -0.09613 | -0.004578 | 0.022888 | -0.054931 | -0.073242 | -0.064087 | 0.11902 | 0.18311 | 0.10071 | 0.23804 | 0.15564 | 0.42572 | 121.8521 | 0.17395 | 121.7926 | 121.962 | 121.7834 | 121.843 | 121.7285 | -121.9208 | -121.8567 | 121.7331 | 121.7377 | 67.6895 | 67.6895
207 | 121.7834 | -65.4602 | 56.3416 | -0.011291 | 0.0033411 | 0.066309 | 0.06605 | 0.00066015 | -0.0027556 | 5.7688e-05 | -0.0046081 | 0.0032855 | 0.068836 | 0.053566 | -0.0077867 | 0.015394 | 0.0021383 | -0.26093 | 56.3232 | -65.5655 | 56.2363 | -65.1535 | -65.5792 | -65.5884 | -0.21057 | 56.25 | -65.4648 | 56.2271 | -65.3549 | -65.3732 | -65.3366 | -0.10529 | -0.018311 | -0.10529 | 0.3067 | -0.12817 | -0.11902 | -0.022888 | -0.013733 | -0.004578 | -0.091553 | -0.11444 | 0.10529 | 0.1236 | 0.086975 | 0.12817 | 0.091553 | 0.41199 | 121.8018 | 0.10986 | 121.6919 | 121.8887 | 121.7148 | 121.7834 | 121.7102 | -121.907 | -121.8063 | 121.6965 | 121.6873 | 65.1993 | 65.2496
208.7344 | 121.8887 | -61.1252 | 60.5804 | 0.019226 | 0.0027001 | 0.066522 | 0.0637 | -0.0010488 | -0.00061944 | -0.00079691 | 0.0014953 | 0.00093566 | 0.069049 | 0.067024 | -0.0015915 | 0.016889 | -0.0014931 | -0.073242 | 60.6262 | -61.2488 | 60.5713 | -60.8505 | -61.2579 | -61.2762 | -0.013733 | 60.4889 | -61.1664 | 60.585 | -61.0245 | -61.0519 | -61.0062 | -0.1236 | 0.045777 | -0.009155 | 0.27466 | -0.15106 | -0.13275 | -0.027466 | -0.009156 | -0.041199 | -0.091552 | 0.004578 | 0.10071 | 0.11902 | 0.073242 | 0.16022 | 0.11444 | 0.39825 | 121.8201 | 0.14191 | 121.7514 | 121.875 | 121.6553 | 121.7514 | 121.6141 | -121.8292 | -121.7468 | 121.6965 | 121.7102 | 61.0519 | 61.1114
210.4219 | 121.8704 | -61.0977 | 60.5896 | 0.042114 | 0.0063317 | 0.071008 | 0.065196 | -0.0012624 | -0.0019012 | -0.00058311 | 0.0045471 | 0.00093566 | 0.070758 | 0.062538 | -0.0026597 | 0.017316 | -0.0014931 | -0.054932 | 60.6079 | -61.2808 | 60.5988 | -60.8231 | -61.2625 | -61.2717 | 0.018311 | 60.4797 | -61.203 | 60.5896 | -61.0474 | -61.0519 | -61.0153 | -0.18311 | 0.01831 | 0.009155 | 0.27466 | -0.17395 | -0.16479 | 0.009156 | 0.018311 | -0.10529 | -0.10986 | 0 | 0.050354 | 0.082397 | 0.045776 | 0.18768 | 0.15106 | 0.45776 | 121.8796 | 0.15564 | 121.7926 | 121.8887 | 121.6827 | 121.7056 | 121.5775 | -121.8704 | -121.7926 | 121.6965 | 121.6873 | 61.0428 | 61.116
212.1562 | 121.875 | -61.084 | 60.6171 | 0.019226 | 0.0048365 | 0.066949 | 0.065409 | 0.00066015 | -0.0027556 | -0.0010105 | 0.0045471 | 0.0032855 | 0.070331 | 0.062324 | -0.0037277 | 0.016889 | -0.0029885 | -0.068665 | 60.5988 | -61.2488 | 60.5896 | -60.8414 | -61.2717 | -61.2808 | -0.009155 | 60.4797 | -61.1572 | 60.585 | -61.0428 | -61.0703 | -61.0245 | -0.16479 | -0.01831 | -0.027465 | 0.24261 | -0.19684 | -0.18768 | -0.032044 | -0.022888 | -0.073243 | -0.13733 | -0.032043 | 0.041198 | 0.059509 | 0.013733 | 0.13275 | 0.086976 | 0.40741 | 121.8384 | 0.11444 | 121.7422 | 121.8475 | 121.637 | 121.6827 | 121.5637 | -121.8658 | -121.7743 | 121.6736 | 121.669 | 61.0153 | 61.0748
213.9062 | 121.8613 | -61.1526 | 60.5759 | 0.026856 | 0.0061181 | 0.065668 | 0.068186 | 1.915e-05 | 0.00044856 | -0.0044285 | 0.016754 | 0.0047809 | 0.067768 | 0.055061 | -0.0047959 | 0.015607 | -0.0032021 | -0.018311 | 60.6171 | -61.3174 | 60.5392 | -60.9146 | -61.3129 | -61.3358 | -0.013733 | 60.5118 | -61.2259 | 60.5118 | -61.1252 | -61.1389 | -61.0748 | -0.1648 | 0.041198 | -0.036621 | 0.23804 | -0.18311 | -0.16022 | -0.01831 | 0.004578 | -0.073242 | -0.064087 | -0.064087 | 0.027466 | 0.07782 | 0.013733 | 0.15106 | 0.086975 | 0.40283 | 121.8567 | 0.10071 | 121.7377 | 121.9345 | 121.7377 | 121.7697 | 121.6644 | -121.8933 | -121.8018 | 121.6919 | 121.6644 | 61.1343 | 61.1389
215.5938 | 121.8155 | -61.1801 | 60.553 | 0.0039673 | 0.0091089 | 0.065881 | 0.066905 | 0.0042918 | -0.001474 | -0.0022921 | 0.0014953 | 0.0043537 | 0.068409 | 0.060402 | -0.00052345 | 0.016034 | -0.00042513 | -0.045776 | 60.5759 | -61.3266 | 60.4797 | -60.9787 | -61.4136 | -61.4273 | -0.082397 | 60.4294 | -61.2442 | 60.466 | -61.2122 | -61.235 | -61.1206 | -0.14648 | 0.022888 | -0.073243 | 0.20142 | -0.24719 | -0.23346 | -0.10071 | -0.086975 | -0.064087 | -0.1236 | -0.086976 | -0.032043 | 0.05951 | -0.054931 | 0.1236 | 0.009156 | 0.3479 | 121.8063 | 0.032044 | 121.7102 | 121.9025 | 121.6736 | 121.756 | 121.6095 | -121.8796 | -121.7972 | 121.6599 | 121.6461 | 61.1343 | 61.0977
217.3281 | 121.9391 | -61.1114 | 60.5392 | -0.011291 | 0.0020593 | 0.066095 | 0.062846 | 0.00301 | -0.00040584 | -0.0012241 | 0.0014953 | 0.0015765 | 0.069049 | 0.056984 | -0.0022325 | 0.017957 | 0.0034201 | -0.036621 | 60.553 | -61.2717 | 60.6079 | -60.7819 | -61.2076 | -61.2488 | 0.10986 | 60.4477 | -61.1847 | 60.6171 | -60.997 | -61.0016 | -60.997 | -0.16022 | 0.013733 | 0.068664 | 0.32959 | -0.13733 | -0.096131 | 0.022888 | 0.064086 | -0.073242 | -0.091553 | 0.077819 | 0.11444 | 0.11444 | 0.10986 | 0.18768 | 0.1831 | 0.48981 | 121.8796 | 0.18768 | 121.8018 | 121.8246 | 121.6324 | 121.6644 | 121.5591 | -121.8109 | -121.7239 | 121.7194 | 121.7285 | 61.0748 | 61.2213
219 | 121.8567 | -61.203 | 60.5576 | 0.049744 | 0.0041955 | 0.067377 | 0.065623 | 0.00023275 | 0.0023712 | -0.00058311 | 0.010651 | 0.0043537 | 0.070758 | 0.061684 | -0.0043687 | 0.016462 | -0.00085233 | -0.041199 | 60.5942 | -61.3174 | 60.4752 | -60.9604 | -61.3586 | -61.3815 | -0.041199 | 60.4889 | -61.3083 | 60.4797 | -61.1618 | -61.1618 | -61.1114 | -0.11444 | 0.036621 | -0.082397 | 0.24262 | -0.17853 | -0.15564 | -0.064087 | -0.041199 | -0.10529 | -0.068664 | -0.07782 | 0.041199 | 0.091553 | 0.041199 | 0.19684 | 0.14649 | 0.35706 | 121.7926 | 0.14649 | 121.788 | 121.9116 | 121.7972 | 121.7972 | 121.6919 | -121.875 | -121.8658 | 121.6782 | 121.6827 | 61.1618 | 61.1618
220.7344 | 121.9711 | -61.171 | 60.4477 | -0.0036622 | 0.0039819 | 0.066309 | 0.064982 | 1.915e-05 | -0.001474 | -0.0037875 | -0.0046081 | 0.0020039 | 0.068195 | 0.062324 | 0.0013991 | 0.01753 | -0.0019205 | -0.086975 | 60.5255 | -61.3358 | 60.4797 | -60.9375 | -61.3586 | -61.377 | 0.004578 | 60.3745 | -61.2625 | 60.5484 | -61.116 | -61.1069 | -61.0474 | -0.16479 | 0.07782 | 0.032043 | 0.23346 | -0.20599 | -0.18768 | -0.041199 | -0.022889 | -0.091553 | -0.073242 | 0.10071 | 0.054931 | 0.1236 | 0.064086 | 0.21515 | 0.15564 | 0.39825 | 121.8155 | 0.14648 | 121.8109 | 121.8613 | 121.637 | 121.6965 | 121.5454 | -121.7834 | -121.7102 | 121.6507 | 121.7194 | 61.084 | 61.1755
222.4844 | 121.8613 | -61.2076 | 60.4523 | -0.0036622 | 0.0037683 | 0.066095 | 0.067759 | -0.00062165 | -0.00019224 | -0.0025057 | -0.0015565 | 0.0052081 | 0.068409 | 0.058479 | -0.00052345 | 0.016889 | 0.0010703 | -0.14191 | 60.5392 | -61.377 | 60.3973 | -61.0336 | -61.4594 | -61.4731 | -0.09613 | 60.4019 | -61.3083 | 60.4614 | -61.2122 | -61.2167 | -61.1435 | -0.16937 | 0.086975 | -0.054932 | 0.17395 | -0.2655 | -0.25177 | -0.09613 | -0.082398 | -0.10071 | -0.050354 | 0.009155 | -0.004577 | 0.064087 | -0.009155 | 0.1648 | 0.091553 | 0.34332 | 121.7743 | 0.096131 | 121.7697 | 121.9162 | 121.7102 | 121.7468 | 121.6095 | -121.8292 | -121.7606 | 121.6049 | 121.669 | 61.0657 | 61.1115
224.2188 | 121.8521 | -61.2579 | 60.4752 | 0.011597 | 0.0048365 | 0.065241 | 0.0637 | 0.0017282 | -0.0012604 | -0.0020785 | -0.0046081 | 0.0022175 | 0.069904 | 0.070015 | -0.0037277 | 0.018171 | -0.00021153 | -0.14191 | 60.5255 | -61.3861 | 60.3561 | -61.0703 | -61.4914 | -61.4914 | -0.10529 | 60.4019 | -61.3037 | 60.434 | -61.2671 | -61.2396 | -61.1755 | -0.12817 | 0.050354 | -0.11902 | 0.18768 | -0.23346 | -0.23346 | -0.10529 | -0.10529 | -0.045776 | -0.073242 | -0.041199 | -0.009155 | 0.082398 | 0.018311 | 0.12817 | 0.064087 | 0.31586 | 121.7422 | 0.036621 | 121.7377 | 121.9116 | 121.7056 | 121.7834 | 121.6599 | -121.8613 | -121.7789 | 121.6141 | 121.6919 | 61.116 | 61.1526
225.9062 | 121.8658 | -61.5234 | 60.1685 | 0.019226 | 0.0056909 | 0.068018 | 0.064555 | 0.001301 | -0.00019224 | -0.00058311 | 0.0075989 | 0.0052081 | 0.070118 | 0.066597 | -0.0041551 | 0.01753 | -0.0066201 | 0.004578 | 60.2463 | -61.7203 | 60.1639 | -61.2534 | -61.6974 | -61.7111 | 0.050354 | 60.1135 | -61.5921 | 60.173 | -61.5005 | -61.5051 | -61.441 | -0.19684 | 0.07782 | -0.004578 | 0.27008 | -0.18768 | -0.17395 | 0.009155 | 0.022888 | -0.068665 | -0.054932 | 0.004578 | 0.022888 | 0.082397 | 0.01831 | 0.15106 | 0.086975 | 0.46692 | 121.8842 | 0.091553 | 121.7651 | 121.9666 | 121.7056 | 121.7697 | 121.637 | -121.8887 | -121.7606 | 121.6873 | 121.6965 | 61.528 | 61.5738
227.6562 | 121.8292 | -61.8896 | 59.8434 | -0.0036622 | 0.0061181 | 0.067804 | 0.064128 | 0.00087375 | 2.1362e-05 | 0.0011257 | 0.016754 | 0.0047809 | 0.071399 | 0.059334 | -0.0056503 | 0.014325 | 0.0010703 | -0.091553 | 59.8892 | -62.0407 | 59.761 | -61.647 | -62.0407 | -62.0956 | -0.045776 | 59.7656 | -61.9949 | 59.7382 | -61.8896 | -61.8942 | -61.8347 | -0.15106 | 0.045776 | -0.082398 | 0.24261 | -0.20599 | -0.15106 | -0.054932 | 0 | -0.10529 | -0.07782 | -0.10529 | 0 | 0.054931 | -0.004578 | 0.16022 | 0.10071 | 0.39368 | 121.8018 | 0.10529 | 121.7331 | 121.9299 | 121.7606 | 121.7789 | 121.6553 | -121.8842 | -121.8384 | 121.6507 | 121.6278 | 61.7981 | 61.8439
229.4062 | 121.907 | -61.6608 | 60.0082 | -0.0036622 | 0.0061181 | 0.067377 | 0.061564 | -0.004894 | -0.0023284 | -0.00036951 | -0.0015565 | 0.0030719 | 0.067981 | 0.064033 | -0.0056503 | 0.015821 | -0.0053385 | -0.018311 | 59.9991 | -61.8301 | 60.0082 | -61.3724 | -61.8118 | -61.8393 | 0.041199 | 59.8755 | -61.7661 | 60.0494 | -61.5829 | -61.6058 | -61.5829 | -0.16937 | -0.009156 | 0 | 0.28839 | -0.17853 | -0.15106 | -0.009155 | 0.01831 | -0.10529 | -0.13275 | 0.041198 | 0.07782 | 0.07782 | 0.054932 | 0.18311 | 0.16022 | 0.45776 | 121.8384 | 0.18311 | 121.8155 | 121.8292 | 121.6415 | 121.6599 | 121.5363 | -121.8384 | -121.7743 | 121.669 | 121.7102 | 61.6425 | 61.702
231.1406 | 121.9482 | -61.4365 | 60.2234 | 0.0039673 | 0.0020593 | 0.067377 | 0.062632 | -0.0010488 | -0.00061944 | 0.00027129 | -0.0046081 | 0.00072206 | 0.068622 | 0.064461 | -0.00095065 | 0.01753 | -0.0014931 | -0.036621 | 60.2463 | -61.6013 | 60.2554 | -61.1252 | -61.5555 | -61.615 | 0.09613 | 60.1135 | -61.5097 | 60.3149 | -61.3266 | -61.3174 | -61.3266 | -0.16479 | 0.022888 | 0.032043 | 0.31128 | -0.17853 | -0.11902 | -0.013733 | 0.045776 | -0.073243 | -0.10986 | 0.091552 | 0.10986 | 0.10986 | 0.11902 | 0.18311 | 0.19226 | 0.47607 | 121.8567 | 0.18311 | 121.8246 | 121.8475 | 121.6232 | 121.6827 | 121.55 | -121.8246 | -121.7331 | 121.6919 | 121.7514 | 61.3998 | 61.5326
232.875 | 121.8338 | -61.9858 | 59.761 | 0.0039673 | 0.0022729 | 0.065241 | 0.067973 | -0.0027578 | -0.0023284 | -0.0031467 | 0.019806 | 0.0054217 | 0.072895 | 0.062965 | -0.0060777 | 0.014753 | -0.00042513 | -0.11444 | 59.7885 | -62.114 | 59.6741 | -61.7523 | -62.1277 | -62.1414 | -0.036621 | 59.7336 | -62.0453 | 59.6786 | -61.972 | -61.9629 | -61.9034 | -0.12817 | 0.027466 | -0.086975 | 0.23346 | -0.15564 | -0.14191 | -0.027465 | -0.013733 | -0.059509 | -0.027465 | -0.082397 | 0.013733 | 0.082398 | 0.022888 | 0.14191 | 0.082397 | 0.36163 | 121.788 | 0.073242 | 121.7239 | 121.9025 | 121.7789 | 121.7743 | 121.7194 | -121.875 | -121.8063 | 121.6599 | 121.6644 | 61.8713 | 61.9492
234.6094 | 121.8613 | -62.1872 | 59.5505 | 0.042114 | 0.0039819 | 0.06759 | 0.067546 | 0.001301 | -0.0038238 | -0.0037875 | 0.013702 | 0.0026447 | 0.070758 | 0.056129 | -0.0030869 | 0.016889 | 0.0010703 | -0.073242 | 59.5871 | -62.3474 | 59.4635 | -61.972 | -62.3657 | -62.3749 | -0.059509 | 59.4772 | -62.2925 | 59.4681 | -62.1735 | -62.1689 | -62.1185 | -0.16022 | 0.036621 | -0.086975 | 0.21515 | -0.18768 | -0.17853 | -0.027466 | -0.018311 | -0.10528 | -0.073242 | -0.082397 | 0.013733 | 0.068665 | 0.018311 | 0.17395 | 0.1236 | 0.37537 | 121.8109 | 0.11902 | 121.7606 | 121.9345 | 121.7697 | 121.7743 | 121.6644 | -121.8979 | -121.843 | 121.6507 | 121.6553 | 62.114 | 62.1277
236.3438 | 121.8796 | -64.6408 | 57.0786 | 0.026856 | 0.0069727 | 0.065881 | 0.066264 | 0.006428 | -0.0021148 | 0.00091209 | 0.0075989 | 0.0034991 | 0.068409 | 0.063179 | -0.0043687 | 0.016889 | -0.0023477 | -0.068665 | 57.1472 | -64.7873 | 57.0648 | -64.3524 | -64.7827 | -64.7964 | -0.073242 | 57.0145 | -64.7232 | 57.0465 | -64.5767 | -64.5905 | -64.5447 | -0.14648 | 0.068665 | -0.013733 | 0.28839 | -0.15564 | -0.14191 | -0.009156 | 0.004577 | -0.082398 | -0.064087 | -0.032043 | 0.064087 | 0.09613 | 0.050354 | 0.17853 | 0.13275 | 0.43487 | 121.8521 | 0.14648 | 121.7697 | 121.9345 | 121.7377 | 121.788 | 121.6553 | -121.8658 | -121.8018 | 121.7056 | 121.6873 | 64.5721 | 64.5676
238.0156 | 121.9299 | -65.2771 | 56.3324 | -0.011291 | 0.0048365 | 0.067163 | 0.065409 | -0.0012624 | -0.0023284 | -0.0022921 | 0.0014953 | 0.0030719 | 0.069049 | 0.067451 | 0.00033115 | 0.018812 | 0.0017111 | -0.27924 | 56.4239 | -65.4556 | 56.2912 | -65.0803 | -65.538 | -65.5655 | -0.17395 | 56.2637 | -65.3961 | 56.4194 | -65.2176 | -65.2496 | -65.1764 | -0.17853 | 0.091553 | -0.041198 | 0.19684 | -0.28839 | -0.26093 | -0.10986 | -0.082398 | -0.11902 | -0.068664 | 0.086976 | 0.05951 | 0.10071 | 0.027466 | 0.21973 | 0.14648 | 0.37537 | 121.7468 | 0.17853 | 121.8155 | 121.8796 | 121.6599 | 121.7011 | 121.5408 | -121.788 | -121.7285 | 121.5683 | 121.6965 | 64.9979 | 65.1031
239.75 | 121.8887 | -65.0299 | 56.6666 | 0.019226 | 0.0052637 | 0.066736 | 0.068614 | -0.0023306 | -0.0027556 | -0.00079691 | 0.0045471 | 0.0043537 | 0.069904 | 0.063606 | -0.0041551 | 0.016675 | -0.0029885 | 0.10529 | 56.7261 | -65.1947 | 56.6391 | -64.7461 | -65.1947 | -65.1993 | 0.17853 | 56.6025 | -65.0848 | 56.6711 | -64.9475 | -64.9612 | -64.9246 | -0.1648 | 0.059509 | -0.027466 | 0.28381 | -0.16937 | -0.1648 | -0.004578 | 0 | -0.054932 | -0.064087 | 0.004578 | 0.082397 | 0.10528 | 0.068664 | 0.16022 | 0.1236 | 0.44861 | 121.8338 | 0.13733 | 121.756 | 121.9208 | 121.6873 | 121.756 | 121.6324 | -121.8613 | -121.7514 | 121.669 | 121.701 | 65.1352 | 65.2084
241.4688 | 121.8887 | -65.6616 | 56.0211 | 0.019226 | 0.0059045 | 0.068231 | 0.066905 | 0.0010874 | -0.0023284 | -0.0010105 | 0.0045471 | 0.0015765 | 0.068195 | 0.059547 | -0.00095065 | 0.017743 | 2.068e-06 | -0.29755 | 56.0806 | -65.7944 | 56.0394 | -65.3549 | -65.7852 | -65.7852 | -0.14648 | 55.9662 | -65.6799 | 56.0761 | -65.5746 | -65.5746 | -65.5334 | -0.13275 | 0.059509 | 0.018311 | 0.3067 | -0.1236 | -0.1236 | 0.009156 | 0.009156 | -0.018311 | -0.054931 | 0.054932 | 0.086975 | 0.12817 | 0.086975 | 0.14648 | 0.10529 | 0.43945 | 121.8338 | 0.10529 | 121.756 | 121.875 | 121.6461 | 121.7422 | 121.6278 | -121.8155 | -121.701 | 121.701 | 121.7377 | 65.3641 | 65.5151
243.1562 | 121.8979 | -65.0482 | 56.6071 | 0.011597 | 0.0039819 | 0.068658 | 0.065196 | -0.0012624 | -0.00040584 | 0.00048489 | 0.0045471 | 0.0015765 | 0.070331 | 0.062752 | -0.0030869 | 0.017103 | 0.0021383 | -0.11444 | 56.6345 | -65.213 | 56.5979 | -64.7736 | -65.2176 | -65.2222 | -0.050354 | 56.5109 | -65.1443 | 56.6437 | -65.0116 | -64.9979 | -64.9429 | -0.16479 | 0.027465 | -0.009156 | 0.27466 | -0.17395 | -0.16937 | -0.009155 | -0.004577 | -0.09613 | -0.096131 | 0.036621 | 0.036621 | 0.10529 | 0.050354 | 0.20142 | 0.14648 | 0.43945 | 121.8109 | 0.13275 | 121.788 | 121.8475 | 121.6553 | 121.6827 | 121.5591 | -121.8201 | -121.7514 | 121.6461 | 121.6919 | 64.9338 | 64.9979
244.8906 | 121.9666 | -64.801 | 56.8176 | 0.0039673 | 0.0037683 | 0.065027 | 0.064341 | 0.00023275 | -0.0029694 | 0.0017667 | 0.0014953 | 0.0017901 | 0.068622 | 0.064247 | -0.0035141 | 0.016889 | 2.068e-06 | -0.032043 | 56.7215 | -65.0894 | 56.7856 | -64.5447 | -64.9567 | -65.0024 | 0.15564 | 56.6666 | -64.9155 | 56.9183 | -64.682 | -64.7095 | -64.6774 | -0.28839 | -0.09613 | -0.032044 | 0.25635 | -0.20142 | -0.15564 | 0.086976 | 0.13275 | -0.11444 | -0.15106 | 0.10071 | 0.11902 | 0.1236 | 0.091552 | 0.23804 | 0.20599 | 0.54474 | 121.875 | 0.23346 | 121.8338 | 121.8109 | 121.582 | 121.5225 | 121.4676 | -121.907 | -121.7331 | 121.5866 | 121.7194 | 64.769 | 64.9567
246.5625 | 121.9116 | -65.5014 | 56.1401 | 0.011597 | 0.0056909 | 0.065881 | 0.064128 | 0.00044655 | -0.0016876 | 5.7688e-05 | 0.0075989 | 0.0017901 | 0.069904 | 0.058906 | -0.0022325 | 0.016248 | 2.068e-06 | -0.16479 | 56.1356 | -65.7257 | 56.1447 | -65.2039 | -65.6662 | -65.7028 | -0.073242 | 56.044 | -65.6158 | 56.1996 | -65.4053 | -65.4236 | -65.3824 | -0.2243 | -0.004578 | 0.004577 | 0.29755 | -0.20142 | -0.1648 | 0.022888 | 0.059509 | -0.11444 | -0.096131 | 0.059509 | 0.096131 | 0.11902 | 0.07782 | 0.23346 | 0.19226 | 0.52185 | 121.8704 | 0.21057 | 121.8155 | 121.8613 | 121.6599 | 121.637 | 121.5454 | -121.8658 | -121.756 | 121.6461 | 121.701 | 65.3366 | 65.4282
248.3125 | 121.9025 | -65.1581 | 56.5063 | 0.026856 | 0.0024865 | 0.067163 | 0.065196 | 0.0017282 | 0.00044856 | -0.00015591 | 0.0045471 | 0.0022175 | 0.06969 | 0.067238 | -0.0013779 | 0.016675 | -0.00021153 | -0.082397 | 56.4743 | -65.3915 | 56.4743 | -64.8972 | -65.3229 | -65.3412 | 0.050354 | 56.4239 | -65.2634 | 56.5338 | -65.1031 | -65.0986 | -65.0391 | -0.23346 | -0.032044 | -0.032044 | 0.26093 | -0.18311 | -0.16479 | 0.050354 | 0.068665 | -0.10529 | -0.082398 | 0.027465 | 0.054932 | 0.11902 | 0.059509 | 0.22431 | 0.16479 | 0.49439 | 121.8658 | 0.16022 | 121.7972 | 121.8658 | 121.6873 | 121.6324 | 121.582 | -121.8979 | -121.7697 | 121.6324 | 121.6919 | 65.0757 | 65.2084
249.9844 | 121.9025 | -65.4144 | 56.282 | 0.026856 | 0.0067591 | 0.069727 | 0.066905 | -0.0012624 | -0.0010468 | -0.0010105 | 0.013702 | 0.0052081 | 0.070331 | 0.065956 | -0.0028733 | 0.015394 | 0.00064307 | -0.11444 | 56.2454 | -65.6342 | 56.2683 | -65.0986 | -65.5518 | -65.5563 | 0.004578 | 56.1676 | -65.4831 | 56.3049 | -65.3412 | -65.3229 | -65.2725 | -0.21973 | -0.036621 | -0.013732 | 0.31586 | -0.14191 | -0.13733 | 0.07782 | 0.082397 | -0.068664 | -0.11444 | 0.022889 | 0.073242 | 0.14191 | 0.091553 | 0.21057 | 0.16022 | 0.53558 | 121.9025 | 0.14191 | 121.788 | 121.8796 | 121.6507 | 121.6599 | 121.582 | -121.9162 | -121.7651 | 121.6827 | 121.7194 | 65.3 | 65.419
251.7188 | 121.9574 | -65.2496 | 56.3599 | -0.011291 | 0.0052637 | 0.068018 | 0.066905 | -0.0010488 | -0.0010468 | -0.0014377 | -0.0076599 | 0.0047809 | 0.069049 | 0.061684 | 0.0028945 | 0.018171 | -0.0066201 | -0.13733 | 56.4697 | -65.3961 | 56.4423 | -64.9612 | -65.4236 | -65.4099 | -0.064087 | 56.3187 | -65.3 | 56.4835 | -65.181 | -65.1855 | -65.126 | -0.14648 | 0.10986 | 0.082398 | 0.28839 | -0.16022 | -0.17395 | -0.013733 | -0.027466 | -0.050354 | -0.041198 | 0.1236 | 0.068665 | 0.1236 | 0.064087 | 0.17395 | 0.11444 | 0.43488 | 121.8384 | 0.11902 | 121.7834 | 121.8658 | 121.6187 | 121.7194 | 121.5683 | -121.756 | -121.6599 | 121.6919 | 121.7331 | 65.1123 | 65.1855
253.3906 | 121.8887 | -65.062 | 56.5842 | 0.019226 | 0.0061181 | 0.066309 | 0.067332 | -0.00040805 | 2.1362e-05 | 0.00091209 | 0.0075989 | 0.0026447 | 0.068409 | 0.063393 | -0.0028733 | 0.016889 | 0.00085667 | -0.11902 | 56.6483 | -65.1718 | 56.6574 | -64.7141 | -65.1581 | -65.1764 | -0.050354 | 56.543 | -65.1169 | 56.662 | -64.9887 | -64.9933 | -64.9338 | -0.10986 | 0.064087 | 0.073243 | 0.3479 | -0.11444 | -0.09613 | -0.004578 | 0.013733 | -0.054931 | -0.041198 | 0.07782 | 0.073243 | 0.12817 | 0.068665 | 0.1831 | 0.1236 | 0.45776 | 121.8292 | 0.12817 | 121.7789 | 121.8201 | 121.6599 | 121.7102 | 121.6049 | -121.756 | -121.701 | 121.7194 | 121.7239 | 64.9429 | 65.0116
255.0625 | 121.9482 | -64.9658 | 56.6757 | 0.049744 | 0.0061181 | 0.066736 | 0.066905 | 0.0010874 | -0.00040584 | 5.7688e-05 | 0.013702 | 0.0011493 | 0.070758 | 0.061043 | -0.0013779 | 0.017743 | -0.0032021 | -0.027466 | 56.7032 | -65.1535 | 56.7627 | -64.595 | -65.0894 | -65.094 | 0.10071 | 56.6116 | -65.0482 | 56.7902 | -64.8605 | -64.8697 | -64.8239 | -0.18768 | 0.027466 | 0.086975 | 0.37079 | -0.12817 | -0.1236 | 0.059509 | 0.064086 | -0.082398 | -0.064087 | 0.11444 | 0.10528 | 0.14191 | 0.09613 | 0.2243 | 0.17853 | 0.55847 | 121.9162 | 0.18768 | 121.8384 | 121.8567 | 121.6599 | 121.669 | 121.5775 | -121.8292 | -121.7239 | 121.7285 | 121.756 | 64.9384 | 65.0665
256.7969 | 121.8292 | -65.0665 | 56.6299 | 0.011597 | 0.0059045 | 0.068445 | 0.066905 | 0.00023275 | -0.001474 | -0.0044285 | -0.0046081 | 0.0028583 | 0.071827 | 0.062324 | -0.0020187 | 0.015821 | 2.068e-06 | -0.16937 | 56.7123 | -65.2222 | 56.5521 | -64.7964 | -65.2771 | -65.2771 | -0.16937 | 56.5567 | -65.1398 | 56.5796 | -65.062 | -65.0894 | -64.9979 | -0.15564 | 0.082397 | -0.07782 | 0.27008 | -0.21057 | -0.21057 | -0.054932 | -0.054932 | -0.073243 | -0.073242 | -0.050354 | 0.004577 | 0.068664 | -0.022889 | 0.14191 | 0.050354 | 0.42572 | 121.7743 | 0.07782 | 121.7194 | 121.9345 | 121.6965 | 121.7789 | 121.6232 | -121.8521 | -121.7697 | 121.6187 | 121.6461 | 64.8972 | 64.8972
258.5312 | 121.7972 | -64.1693 | 57.5134 | -0.0036622 | 0.0054773 | 0.066736 | 0.067759 | 0.00301 | -0.0019012 | -0.0010105 | -0.0015565 | 0.0028583 | 0.069904 | 0.063179 | -0.0045823 | 0.01753 | -0.0040567 | -0.11444 | 57.5729 | -64.3204 | 57.4539 | -63.9221 | -64.3936 | -64.3982 | -0.10986 | 57.4677 | -64.2334 | 57.4722 | -64.1739 | -64.1968 | -64.1006 | -0.15106 | 0.059509 | -0.05951 | 0.24719 | -0.22888 | -0.2243 | -0.077819 | -0.073242 | -0.064086 | -0.045777 | -0.041199 | -0.004577 | 0.068665 | -0.027465 | 0.13275 | 0.036621 | 0.39825 | 121.7743 | 0.059509 | 121.7056 | 121.8933 | 121.701 | 121.7422 | 121.637 | -121.8338 | -121.7468 | 121.6232 | 121.6415 | 64.0549 | 64.0594
260.2656 | 121.907 | -63.8855 | 57.7606 | 0.034485 | 0.0050501 | 0.069086 | 0.067118 | 0.0015146 | 2.1362e-05 | 0.0015531 | 0.013702 | -0.00013254 | 0.06969 | 0.061043 | -0.0035141 | 0.018812 | -0.0021341 | -0.17395 | 57.7972 | -64.0869 | 57.7377 | -63.6108 | -64.1006 | -64.1052 | -0.082397 | 57.6141 | -64.0549 | 57.7972 | -63.8077 | -63.7985 | -63.739 | -0.20142 | 0.036621 | -0.022888 | 0.27466 | -0.21973 | -0.21515 | -0.018311 | -0.013733 | -0.16937 | -0.14648 | 0.036621 | 0.07782 | 0.14648 | 0.086975 | 0.31586 | 0.25635 | 0.47607 | 121.8246 | 0.24719 | 121.8521 | 121.8842 | 121.669 | 121.6827 | 121.4996 | -121.8475 | -121.8155 | 121.6232 | 121.6827 | 63.7115 | 63.8031
262 | 121.4676 | -28.775 | 93.0588 | 0.0039673 | 0.0063317 | 0.063104 | 0.065837 | -0.0019034 | -0.00083304 | -0.0033603 | -0.0046081 | 0.0041401 | 0.0667 | 0.062324 | -0.0037277 | 0.014753 | -0.0042703 | 0.050354 | 93.0817 | -28.8528 | 92.8574 | -28.7567 | -29.0497 | -29.0497 | 0.064087 | 92.9169 | -28.7796 | 92.8665 | -28.862 | -28.8986 | -28.8025 | -0.07782 | 0.022888 | -0.20142 | 0.01831 | -0.27466 | -0.27466 | -0.19684 | -0.19684 | -0.004578 | -0.14191 | -0.19226 | -0.086976 | -0.027466 | -0.1236 | -0.022888 | -0.11902 | 0.09613 | 121.7102 | -0.082398 | 121.6461 | 121.9345 | 121.6965 | 121.8567 | 121.6919 | -121.9116 | -121.8384 | 121.6324 | 121.6415 | 28.8254 | 28.8391
263.7344 | 121.9528 | -63.5651 | 57.962 | 0.042114 | 0.0084681 | 0.069727 | 0.064768 | -0.0023306 | 0.0015168 | 0.00048489 | 0.0075989 | 0.0022175 | 0.070972 | 0.060188 | -0.0035141 | 0.016889 | -0.00021153 | -0.67291 | 58.1131 | -63.7436 | 58.0582 | -63.2812 | -63.7802 | -63.8168 | -0.54474 | 57.9071 | -63.7482 | 58.0399 | -63.6017 | -63.5834 | -63.533 | -0.17853 | 0.15106 | 0.096131 | 0.28381 | -0.25177 | -0.21515 | -0.073242 | -0.036621 | -0.18311 | -0.054932 | 0.07782 | -0.036622 | 0.032043 | -0.018311 | 0.21515 | 0.16479 | 0.46234 | 121.8018 | 0.14648 | 121.788 | 121.8567 | 121.6553 | 121.6782 | 121.4722 | -121.7056 | -121.7102 | 121.6232 | 121.6049 | 62.8922 | 63.0203
265.4062 | 122.0261 | -47.9462 | 73.732 | -0.011291 | 0.0050501 | 0.067804 | 0.064128 | 0.00066015 | -0.00040584 | -0.00079691 | -0.0015565 | 0.00050846 | 0.070331 | 0.063393 | -0.0084275 | 0.01753 | -0.0012795 | 0.15106 | 74.057 | -47.7951 | 73.2788 | -47.7585 | -47.6852 | -47.2458 | -0.58594 | 73.7091 | -47.9004 | 73.7686 | -47.5754 | -47.7631 | -47.8226 | 0.15106 | 0.32501 | -0.45319 | 0.18768 | 0.70038 | 0.26093 | 0.54932 | 0.10986 | 0.045776 | -0.022889 | 0.036621 | 0.37079 | 0.1236 | 0.18311 | 0.07782 | 0.13733 | 0.036621 | 121.0739 | 0.32501 | 121.669 | 121.8521 | 121.6095 | 122.0032 | 121.6553 | -121.5271 | -121.6324 | 121.225 | 121.7148 | 48.0972 | 47.3602
267.1406 | 121.7148 | -27.4521 | 94.3542 | -0.0036622 | 0.0063317 | 0.067804 | 0.067546 | 0.0053598 | -0.0016876 | -0.0014377 | 0.0014953 | 0.0030719 | 0.068409 | 0.067879 | -0.0030869 | 0.014539 | -0.0023477 | -0.09613 | 94.4321 | -27.5162 | 94.1895 | -27.4338 | -27.6947 | -27.7084 | -0.073242 | 94.2627 | -27.4292 | 94.1574 | -27.5894 | -27.6306 | -27.5253 | -0.064087 | 0.07782 | -0.16479 | 0.01831 | -0.25635 | -0.24262 | -0.19226 | -0.17853 | 0.022888 | -0.091553 | -0.19684 | -0.13733 | -0.073243 | -0.17853 | -0.096131 | -0.20142 | 0.082397 | 121.7056 | -0.16022 | 121.5866 | 121.9482 | 121.6919 | 121.8842 | 121.7148 | -121.8704 | -121.7834 | 121.6415 | 121.6095 | 27.356 | 27.3788
268.8906 | 121.7926 | -27.0813 | 94.6838 | 0.011597 | 0.0067591 | 0.065027 | 0.066905 | 1.915e-05 | -0.004251 | -0.0027195 | -0.0046081 | 0.0056355 | 0.070545 | 0.063393 | -0.0035141 | 0.015607 | -0.0040567 | 0.041199 | 94.7388 | -27.2003 | 94.5419 | -27.0447 | -27.3239 | -27.3331 | 0.13275 | 94.5831 | -27.1042 | 94.5648 | -27.15 | -27.2186 | -27.1408 | -0.11902 | 0.054932 | -0.14191 | 0.036621 | -0.25177 | -0.24261 | -0.13275 | -0.1236 | -0.022888 | -0.10071 | -0.11902 | -0.068664 | -0.059509 | -0.13733 | -0.036621 | -0.11444 | 0.15564 | 121.7422 | -0.045776 | 121.669 | 121.9391 | 121.6873 | 121.8201 | 121.6644 | -121.8842 | -121.788 | 121.6232 | 121.6461 | 27.1225 | 27.2141
270.5781 | 121.8933 | -26.6647 | 95.0226 | -0.011291 | 0.0061181 | 0.068445 | 0.064555 | -0.00040805 | -0.0046782 | -0.0016513 | 0.019806 | 0.0043537 | 0.070118 | 0.06382 | -0.00095065 | 0.01753 | 0.00021567 | -0.082397 | 95.0958 | -26.7609 | 95.0134 | -26.5549 | -26.8387 | -26.8662 | 0.064087 | 94.899 | -26.7654 | 94.9951 | -26.7242 | -26.7563 | -26.7242 | -0.09613 | 0.073242 | -0.009155 | 0.10986 | -0.20142 | -0.17395 | -0.10529 | -0.07782 | -0.10071 | -0.1236 | -0.027466 | -0.059509 | -0.059509 | -0.091553 | 0.041199 | 0.009155 | 0.20599 | 121.7743 | 0.041199 | 121.7606 | 121.8567 | 121.6644 | 121.7606 | 121.5637 | -121.7834 | -121.788 | 121.6782 | 121.6599 | 26.5823 | 26.7288
272.3125 | 121.7697 | -26.564 | 95.2148 | -0.0036622 | 0.0067591 | 0.067163 | 0.064341 | 0.0019418 | -0.001474 | 5.7688e-05 | 0.0014953 | 0.0047809 | 0.067127 | 0.06617 | -0.0041551 | 0.01518 | 0.00021567 | -0.013733 | 95.2423 | -26.6968 | 95.0226 | -26.5503 | -26.8433 | -26.8478 | 0.059509 | 95.0912 | -26.5915 | 95.0409 | -26.7014 | -26.738 | -26.6602 | -0.13275 | 0.027466 | -0.19226 | 0.013733 | -0.28381 | -0.27924 | -0.15106 | -0.14648 | -0.027466 | -0.1236 | -0.17395 | -0.13733 | -0.09613 | -0.17395 | -0.068664 | -0.14648 | 0.14648 | 121.7194 | -0.10986 | 121.6324 | 121.9391 | 121.6827 | 121.8063 | 121.6553 | -121.9116 | -121.8063 | 121.5866 | 121.6049 | 26.5503 | 26.6235
274.0469 | 121.8658 | -26.619 | 95.1187 | -0.011291 | 0.0046227 | 0.0646 | 0.0637 | -0.003826 | -0.0016876 | -0.0025057 | 0.0014953 | 0.00072206 | 0.06969 | 0.064888 | -0.0056503 | 0.015394 | -0.0019205 | 0.041199 | 95.1828 | -26.6785 | 95.05 | -26.4862 | -26.77 | -26.7929 | 0.13733 | 94.9997 | -26.6647 | 95.0317 | -26.6418 | -26.6922 | -26.6647 | -0.059509 | 0.064087 | -0.068664 | 0.13275 | -0.17395 | -0.15106 | -0.11444 | -0.091553 | -0.045776 | -0.11902 | -0.086975 | -0.022888 | -0.045776 | -0.073242 | 0 | -0.027466 | 0.19226 | 121.7285 | 0.022888 | 121.6965 | 121.8613 | 121.6644 | 121.8018 | 121.6187 | -121.7972 | -121.7834 | 121.669 | 121.6507 | 26.6602 | 26.7563
275.7812 | 121.8246 | -26.683 | 95.0455 | 0.034485 | 0.0061181 | 0.065881 | 0.06605 | -0.00019445 | -0.0010468 | 0.00069849 | 0.0045471 | 0.0049945 | 0.070331 | 0.062965 | -0.0018051 | 0.014112 | -0.0019205 | -0.036621 | 95.1279 | -26.8295 | 94.9356 | -26.564 | -26.8982 | -26.9165 | 0.082397 | 94.9814 | -26.7197 | 94.9402 | -26.7654 | -26.8066 | -26.7471 | -0.14649 | 0.082398 | -0.10986 | 0.11902 | -0.23346 | -0.21515 | -0.086975 | -0.068664 | -0.036622 | -0.064087 | -0.10529 | -0.082398 | -0.064087 | -0.1236 | -0.027465 | -0.086975 | 0.2655 | 121.7651 | -0.045776 | 121.6599 | 121.9574 | 121.7011 | 121.8109 | 121.6644 | -121.875 | -121.7651 | 121.6187 | 121.6232 | 26.6464 | 26.7654
277.4531 | 121.8109 | -26.5091 | 95.2286 | 0.019226 | 0.0071863 | 0.065881 | 0.066264 | 0.0010874 | -0.0027556 | -0.0022921 | 0.0045471 | 0.0034991 | 0.070331 | 0.069801 | -0.00030965 | 0.014753 | -0.0010659 | -0.022888 | 95.3247 | -26.6373 | 95.1004 | -26.239 | -26.7426 | -26.7563 | 0.091553 | 95.1233 | -26.5549 | 95.1004 | -26.6006 | -26.6327 | -26.5594 | -0.12817 | 0.09613 | -0.12817 | 0.27008 | -0.24719 | -0.23346 | -0.11902 | -0.10529 | -0.045777 | -0.10529 | -0.12817 | -0.091553 | -0.050354 | -0.1236 | -0.004577 | -0.077819 | 0.39825 | 121.7377 | -0.045776 | 121.6553 | 121.962 | 121.6782 | 121.8338 | 121.6324 | -121.8658 | -121.7834 | 121.6095 | 121.6095 | 26.4862 | 26.6006
279.125 | 121.907 | -26.6876 | 94.9768 | -0.0036622 | 0.0052637 | 0.065454 | 0.064341 | 0.00023275 | -0.001474 | -0.0018649 | 0.0014953 | 0.0032855 | 0.06734 | 0.064247 | -0.00073705 | 0.016675 | -0.0040567 | -0.036621 | 95.1508 | -26.7197 | 94.9585 | -26.5411 | -26.8982 | -26.9119 | 0.10071 | 94.8807 | -26.7242 | 95.0134 | -26.7105 | -26.7609 | -26.6785 | -0.032044 | 0.17395 | -0.018311 | 0.14648 | -0.2243 | -0.21057 | -0.19226 | -0.17853 | -0.036621 | -0.096131 | 0.036621 | -0.022888 | 0.009155 | -0.073242 | 0.045776 | -0.036621 | 0.17853 | 121.6782 | 0.013733 | 121.7377 | 121.8704 | 121.6049 | 121.8384 | 121.5683 | -121.6965 | -121.701 | 121.6461 | 121.7011 | 26.651 | 26.7883
280.8594 | 121.8704 | -27.1912 | 94.4962 | 0.026856 | 0.0061181 | 0.067163 | 0.065623 | -0.0051076 | -0.00061944 | -0.0014377 | 0.0014953 | 0.00093566 | 0.071827 | 0.074928 | -0.0050095 | 0.015607 | -0.0027749 | 0.036621 | 95.2423 | -26.6098 | 95.0684 | -25.9918 | -26.7105 | -26.7014 | 0.16479 | 95.0729 | -26.6052 | 94.5602 | -27.3239 | -27.3331 | -27.3193 | 0.58136 | 0.74616 | 0.5722 | 1.1993 | 0.48981 | 0.48065 | -0.091553 | -0.10071 | 0.58594 | 0.57678 | 0.064087 | -0.13275 | -0.12817 | -0.14191 | -0.71411 | -0.72784 | 0.61798 | 121.6782 | -0.71869 | 121.1655 | 121.8521 | 121.6782 | 122.4335 | 122.2641 | -121.106 | -121.1014 | 122.2595 | 121.7514 | 27.2278 | 27.356
282.5938 | 121.8109 | -26.8341 | 94.9356 | -0.0036622 | 0.0069727 | 0.066949 | 0.066905 | -0.0019034 | -0.00019224 | -0.0040011 | 0.0014953 | 0.0056355 | 0.070545 | 0.061897 | -0.0043687 | 0.017103 | -0.0034159 | -0.050354 | 95.0134 | -26.9623 | 94.5694 | -26.7151 | -27.1957 | -27.1408 | -0.059509 | 94.7021 | -26.9669 | 94.8166 | -26.9302 | -26.9806 | -26.8707 | -0.12817 | 0.07782 | -0.36621 | 0.11902 | -0.3067 | -0.36163 | -0.17853 | -0.23346 | -0.13275 | -0.23346 | -0.11902 | -0.096131 | -0.036622 | -0.14649 | 0.09613 | -0.013733 | 0.24719 | 121.5317 | 0.036621 | 121.7834 | 121.9757 | 121.669 | 121.8475 | 121.5363 | -121.8979 | -121.9025 | 121.4035 | 121.6507 | 26.7838 | 26.7746
284.3281 | 121.7651 | -26.9348 | 94.7983 | -0.011291 | 0.0048365 | 0.065027 | 0.065409 | 0.00301 | -0.0012604 | -0.00036951 | -0.0076599 | 0.0043537 | 0.070545 | 0.064674 | -0.0080003 | 0.014112 | -0.0025613 | -0.004578 | 94.931 | -27.0081 | 94.6335 | -26.5686 | -27.182 | -27.1866 | 0.073242 | 94.7067 | -26.9669 | 94.6243 | -27.0676 | -27.095 | -27.0218 | -0.073243 | 0.13275 | -0.16479 | 0.36621 | -0.25177 | -0.24719 | -0.17853 | -0.17395 | -0.032044 | -0.091553 | -0.17395 | -0.13275 | -0.086976 | -0.16022 | -0.054932 | -0.12817 | 0.43945 | 121.6415 | -0.10071 | 121.5912 | 121.9391 | 121.6736 | 121.8658 | 121.6415 | -121.8063 | -121.7651 | 121.5683 | 121.5591 | 26.9302 | 27.0081
286.0625 | 121.7926 | -26.8295 | 94.9722 | 0.034485 | 0.0069727 | 0.065454 | 0.066905 | 0.0021556 | -0.0016876 | 0.0024075 | 0.019806 | 0.0039265 | 0.068195 | 0.057197 | -0.0024461 | 0.015607 | -0.0012795 | -0.059509 | 95.0546 | -26.9257 | 94.7937 | -26.2619 | -27.0172 | -27.0264 | 0.036621 | 94.9173 | -26.8478 | 94.8029 | -26.9073 | -26.9257 | -26.8662 | -0.09613 | 0.082397 | -0.17853 | 0.56763 | -0.19684 | -0.18768 | -0.10071 | -0.091553 | -0.01831 | -0.054932 | -0.16937 | -0.07782 | -0.036621 | -0.09613 | -0.018311 | -0.07782 | 0.66376 | 121.7194 | -0.05951 | 121.6507 | 121.9803 | 121.7651 | 121.8842 | 121.7468 | -121.8979 | -121.8201 | 121.6232 | 121.6324 | 26.77 | 26.8662
287.7969 | 121.7514 | -26.6098 | 95.1462 | 0.0039673 | 0.0039819 | 0.065027 | 0.066264 | 0.00044655 | -0.0029694 | 0.00048489 | 0.019806 | 0.0045673 | 0.070331 | 0.064461 | -0.0065049 | 0.01753 | -0.00063873 | -0.11902 | 95.2377 | -26.7105 | 94.9402 | -25.9644 | -26.8433 | -26.8616 | -0.004578 | 95.0684 | -26.6739 | 94.9631 | -26.7471 | -26.7746 | -26.7105 | -0.10071 | 0.091553 | -0.20599 | 0.64545 | -0.25177 | -0.23346 | -0.15106 | -0.13275 | -0.064087 | -0.07782 | -0.1831 | -0.13733 | -0.10071 | -0.1648 | -0.036621 | -0.10071 | 0.74615 | 121.6507 | -0.073242 | 121.637 | 121.9482 | 121.7422 | 121.8475 | 121.6782 | -121.8567 | -121.8201 | 121.55 | 121.5729 | 26.4908 | 26.6052
289.5312 | 121.7606 | -26.7105 | 95.0821 | -0.0036622 | 0.0050501 | 0.065454 | 0.065409 | -0.0010488 | -0.0023284 | 0.00048489 | -0.0015565 | 0.0024311 | 0.069904 | 0.055916 | -0.0035141 | 0.014325 | -0.0046975 | -0.10529 | 95.1324 | -26.7838 | 94.8669 | -25.9918 | -26.9257 | -26.9348 | -0.018311 | 94.9768 | -26.7288 | 94.8715 | -26.8158 | -26.8478 | -26.7838 | -0.073242 | 0.050354 | -0.21515 | 0.71869 | -0.2243 | -0.21515 | -0.15106 | -0.14191 | -0.018311 | -0.10529 | -0.21057 | -0.10529 | -0.073242 | -0.13733 | -0.054931 | -0.11902 | 0.79193 | 121.6507 | -0.086975 | 121.6003 | 121.9162 | 121.7056 | 121.843 | 121.6873 | -121.8658 | -121.8109 | 121.5775 | 121.582 | 26.6052 | 26.6922
291.2031 | 121.8063 | -26.6602 | 95.0638 | -0.0036622 | 0.0046227 | 0.066949 | 0.064128 | -0.00019445 | -0.002542 | -0.0014377 | -0.0015565 | 0.0017901 | 0.069049 | 0.058693 | -0.0043687 | 0.016034 | -0.0038431 | -0.032043 | 95.0867 | -26.77 | 94.9127 | -26.2802 | -26.8707 | -26.889 | 0.10986 | 94.8944 | -26.7151 | 94.9265 | -26.7426 | -26.7838 | -26.7288 | -0.10986 | 0.022888 | -0.15106 | 0.37994 | -0.22888 | -0.21057 | -0.11902 | -0.10071 | -0.054932 | -0.16937 | -0.13733 | -0.082398 | -0.068665 | -0.1236 | -0.013733 | -0.068664 | 0.48981 | 121.6827 | -0.027466 | 121.6415 | 121.8567 | 121.6095 | 121.7468 | 121.5546 | -121.8338 | -121.7789 | 121.5729 | 121.5866 | 26.6281 | 26.77
292.9375 | 121.8842 | -26.4038 | 95.3064 | 0.042114 | 0.0063317 | 0.067804 | 0.065196 | 0.00301 | -0.001474 | 0.00091209 | 0.010651 | 0.0039265 | 0.071186 | 0.066383 | -0.00030965 | 0.017743 | 0.00064307 | -0.54474 | 95.1599 | -26.7059 | 94.7708 | -25.3098 | -27.0584 | -27.1774 | -0.55389 | 94.6152 | -27.0218 | 95.1004 | -26.5182 | -26.4908 | -26.358 | -0.30212 | -0.14648 | -0.53558 | 1.0941 | -0.77362 | -0.6546 | -0.4715 | -0.35248 | -0.61798 | -0.69122 | -0.20599 | -0.11444 | 0.045777 | -0.086975 | 0.66376 | 0.53101 | 1.3962 | 121.4767 | 0.50354 | 122.1222 | 121.8658 | 121.637 | 121.5637 | 121.019 | -122.0123 | -122.3282 | 121.1746 | 121.5042 | 25.8591 | 25.8499
294.6094 | 121.8979 | -21.373 | 100.2914 | -0.02655 | 0.0061181 | 0.071008 | 0.064555 | -0.003185 | -0.0036102 | -0.0025057 | -0.0046081 | 0.0022175 | 0.069477 | 0.061043 | -0.0041551 | 0.016248 | 0.0017111 | -0.032043 | 100.3876 | -21.524 | 100.2274 | -8.6334 | -21.5378 | -21.5378 | 0.21057 | 100.209 | -21.4005 | 100.296 | -21.3776 | -21.4325 | -21.3959 | -0.15106 | 0.09613 | -0.064087 | 12.7396 | -0.16479 | -0.16479 | -0.013733 | -0.013733 | -0.027466 | -0.082398 | 0.004578 | -0.004577 | -0.022888 | -0.059509 | 0.004578 | -0.032043 | 12.8906 | 121.7514 | 0.022889 | 121.6965 | 121.9116 | 121.6095 | 121.7606 | 121.582 | -121.8155 | -121.6919 | 121.6003 | 121.669 | 21.3409 | 21.5836
296.3438 | 121.8842 | -20.9381 | 100.7492 | 0.034485 | 0.0095361 | 0.076349 | 0.066691 | 0.0042918 | 0.0021576 | -0.00079691 | 0.013702 | 0.0026447 | 0.071186 | 0.062111 | 0.00033115 | 0.016675 | -0.0046975 | 0.10529 | 100.8682 | -21.0617 | 100.6622 | -6.8756 | -21.1395 | -21.1487 | 0.1831 | 100.5615 | -21.0617 | 100.7675 | -20.9244 | -21.0068 | -20.961 | -0.1236 | 0.11902 | -0.086976 | 14.0625 | -0.21057 | -0.20142 | -0.086975 | -0.077819 | -0.1236 | -0.18768 | 0.01831 | 0.013733 | -0.022889 | -0.068665 | 0.10071 | 0.054932 | 14.1861 | 121.7239 | 0.13733 | 121.8292 | 121.9299 | 121.6232 | 121.8063 | 121.4996 | -121.8109 | -121.8109 | 121.6003 | 121.7056 | 21.0434 | 21.1212
298.0156 | 89.4928 | -0.15106 | 69.1818 | 0.11078 | 0.072341 | 0.13296 | -0.013204 | 0.0085642 | 0.064749 | 0.055813 | 0.04422 | 0.02892 | 0.022052 | 0.015755 | 0.044978 | 0.03761 | 0.0329 | 0.082397 | 70.903 | -7.37 | 70.1797 | 0.07782 | 0.07782 | 0.073242 | 0.082397 | 69.4565 | -0.14648 | 68.9804 | 0.064087 | 0.082397 | 0.082397 | -7.2189 | 1.7212 | 0.99792 | 0.22888 | 0.2243 | 0.22888 | 7.4432 | 7.4478 | 0.004578 | 0.27466 | -0.20142 | 0.21515 | 0.23346 | 0.23346 | 0.22888 | 0.22888 | 7.4478 | 77.5497 | 0.21057 | 69.1269 | 78.273 | 69.603 | 71.0541 | 69.6075 | -76.5518 | -69.3283 | 70.3308 | 69.1315 | 0.23346 | 0.23346
299.7656 | 121.9162 | -20.2515 | 97.9935 | 0.026856 | -0.0066993 | 0.071863 | -0.01534 | 0.0094186 | 0.064749 | 0.055172 | 0.041168 | 0.028493 | 0.022693 | 0.016182 | 0.044551 | 0.037824 | 0.032686 | 0.073242 | 96.2402 | -20.6085 | 83.1024 | 0.045776 | -1.8539 | -0.83771 | 0.07782 | 72.6425 | -10.8856 | 78.5431 | -6.0333 | -0.81024 | 0.11444 | -0.35706 | -1.7532 | -14.8911 | 20.2972 | 19.4138 | 18.3975 | 19.7708 | 18.7546 | 9.3658 | -25.351 | -19.4504 | 14.2181 | 20.3659 | 19.4412 | 11.0001 | 10.0754 | 20.6543 | 103.7109 | 4.8523 | 89.4287 | 116.8488 | 83.5281 | 116.4917 | 92.894 | -118.602 | -108.8791 | 103.3539 | 98.7946 | 20.3247 | 20.3293
301.5 | 121.9711 | -118.2312 | 3.3875 | 0.0039673 | -7.6884e-05 | 0.1289 | 0.066691 | 0.001301 | -0.004251 | -0.0012241 | -0.0046081 | 0.0022175 | 0.069263 | 0.060402 | -0.0041551 | 0.016248 | -0.0023477 | -0.33875 | 3.3875 | -118.4601 | 3.3096 | -5.7953 | -117.7917 | -117.897 | -0.25177 | 3.3417 | -118.4509 | 3.3325 | -117.6956 | -117.5903 | -117.5217 | -0.22888 | 0 | -0.07782 | 112.4359 | 0.33417 | 0.43945 | 0.56305 | 0.66833 | -0.21973 | -0.045776 | -0.054931 | 0.53558 | 0.70953 | 0.64087 | 0.92926 | 0.8606 | 112.6648 | 121.7697 | 0.75531 | 121.7834 | 121.8475 | 121.7926 | 121.6187 | 121.5729 | -121.8475 | -121.8384 | 121.5408 | 121.5637 | 117.8925 | 117.9794
303.2344 | 121.9116 | -119.6594 | 1.9913 | -0.0036622 | 0.0059045 | 0.13146 | 0.069041 | 0.00066015 | 0.00044856 | 0.00027129 | 0.0045471 | 0.0067035 | 0.068195 | 0.06382 | -0.00052345 | 0.020948 | 0.0010703 | -0.3891 | 2.0142 | -119.8425 | 1.8036 | -5.4153 | -117.984 | -118.8812 | -0.32959 | 2.0004 | -119.8196 | 1.9226 | -119.2154 | -119.0186 | -118.8721 | -0.1831 | 0.022888 | -0.18768 | 114.2441 | 0.7782 | 1.6754 | 0.9613 | 1.8585 | -0.16022 | 0.009155 | -0.068665 | 0.44403 | 0.78735 | 0.64087 | 0.94757 | 0.80109 | 114.4272 | 121.6461 | 0.60425 | 121.7422 | 121.8567 | 121.8201 | 121.6736 | 121.6599 | -121.8338 | -121.8109 | 121.463 | 121.582 | 119.2703 | 119.3298
304.9688 | 121.9116 | -119.6777 | 2.0279 | 0.011597 | 0.0048365 | 0.13125 | 0.0684 | -0.0042532 | -0.0012604 | -0.0035739 | -0.096161 | -0.016368 | 0.068409 | 0.060402 | -0.0033005 | 0.013044 | -0.0093973 | -0.27924 | 2.0462 | -119.8837 | 1.8723 | -5.4337 | -101.9394 | -104.2969 | -0.16479 | 1.9913 | -119.7968 | 1.9455 | -119.0826 | -119.5267 | -108.6868 | -0.20599 | 0.018311 | -0.15564 | 114.2441 | 15.3809 | 17.7383 | 15.5869 | 17.9443 | -0.11902 | -0.036621 | -0.082397 | 0.59509 | 10.9909 | 0.15106 | 11.1099 | 0.27008 | 114.4501 | 121.756 | 0.71411 | 121.7422 | 121.9299 | 121.788 | 121.7239 | 121.669 | -121.9116 | -121.8246 | 121.55 | 121.6232 | 119.3985 | 119.5129
306.6406 | 121.8109 | -119.7372 | 1.9958 | -0.0036622 | 0.0044091 | 0.13339 | 0.067973 | -0.0019034 | -0.0027556 | -0.00079691 | -0.029022 | 0.0015765 | 0.069263 | 0.062324 | -0.0022325 | 0.017743 | 0.00021567 | -0.37537 | 1.9958 | -119.8746 | 1.767 | -5.3879 | -116.5009 | -116.0934 | -0.3067 | 1.9638 | -119.838 | 1.8585 | -119.4351 | -119.1696 | -118.9178 | -0.13733 | 0 | -0.22888 | 114.3494 | 3.6438 | 3.2364 | 3.7811 | 3.3737 | -0.10071 | -0.032044 | -0.13733 | 0.30212 | 0.8194 | 0.56763 | 0.92011 | 0.66833 | 114.4867 | 121.6415 | 0.40283 | 121.6965 | 121.8704 | 121.8018 | 121.7331 | 121.7011 | -121.8704 | -121.8338 | 121.5042 | 121.5958 | 119.3619 | 119.4305
308.375 | 121.8063 | -119.7693 | 1.9409 | 0.0039673 | 0.0061181 | 0.12997 | 0.067973 | 0.00044655 | -0.0027556 | 5.7688e-05 | 0.0075989 | 0.0034991 | 0.068622 | 0.061897 | -0.0015915 | 0.017957 | -0.00063873 | -0.35706 | 1.9547 | -119.9112 | 1.7075 | -5.4382 | -119.838 | -120.0302 | -0.29297 | 1.918 | -119.8791 | 1.8036 | -119.4809 | -119.3298 | -119.014 | -0.14191 | 0.013733 | -0.23346 | 114.3311 | -0.26093 | -0.068665 | -0.11902 | 0.073242 | -0.10986 | -0.022888 | -0.13733 | 0.28839 | 0.75531 | 0.43945 | 0.86517 | 0.54932 | 114.473 | 121.6187 | 0.39825 | 121.6827 | 121.8658 | 121.7972 | 121.7239 | 121.6873 | -121.8521 | -121.8201 | 121.4767 | 121.5729 | 119.4122 | 119.4763
310.0469 | 121.8796 | -119.8242 | 1.8539 | 0.042114 | 0.0054773 | 0.13317 | 0.065623 | 0.0042918 | -0.00083304 | 0.00091209 | 0.013702 | 0.0015765 | 0.069904 | 0.069588 | -0.0020187 | 0.019452 | 0.0012839 | -0.28839 | 1.8723 | -119.9524 | 1.7944 | -5.1178 | -119.6823 | -119.6548 | -0.13275 | 1.8494 | -119.9066 | 1.8356 | -119.4168 | -119.4626 | -119.3893 | -0.12817 | 0.01831 | -0.059509 | 114.7064 | 0.16937 | 0.14191 | 0.29755 | 0.27008 | -0.082397 | -0.004578 | -0.018311 | 0.40741 | 0.43488 | 0.36163 | 0.51727 | 0.44403 | 114.8346 | 121.7468 | 0.48981 | 121.7422 | 121.8246 | 121.756 | 121.6965 | 121.6736 | -121.8063 | -121.7606 | 121.6187 | 121.6599 | 119.5358 | 119.6915
311.7812 | 121.8704 | -119.8608 | 1.8173 | 0.042114 | 0.0071863 | 0.13339 | 0.067546 | 0.0017282 | -0.0010468 | 0.00048489 | 0.025909 | 0.0013629 | 0.069263 | 0.061684 | -0.0024461 | 0.018812 | 0.0047019 | -0.28839 | 1.8402 | -119.9753 | 1.7624 | -4.6875 | -119.7784 | -119.7601 | -0.12817 | 1.7944 | -119.9295 | 1.7899 | -119.4534 | -119.4946 | -119.4214 | -0.11444 | 0.022888 | -0.054932 | 115.1733 | 0.10071 | 0.082398 | 0.21515 | 0.19684 | -0.068664 | -0.022888 | -0.027466 | 0.40741 | 0.43945 | 0.36621 | 0.50812 | 0.43487 | 115.2878 | 121.7377 | 0.47607 | 121.7194 | 121.8155 | 121.7239 | 121.701 | 121.6553 | -121.7926 | -121.7468 | 121.6232 | 121.6507 | 119.5724 | 119.7327
313.5156 | 121.7651 | -119.7556 | 1.9913 | 0.0039673 | 0.0046227 | 0.13253 | 0.070109 | 0.00087375 | -0.0019012 | -0.0016513 | -0.0015565 | 0.0034991 | 0.068195 | 0.065956 | -0.0011643 | 0.017743 | 0.0012839 | -0.32501 | 1.9913 | -119.8334 | 1.7624 | -4.8889 | -119.3527 | -119.4443 | -0.26093 | 1.9684 | -119.783 | 1.8448 | -119.4122 | -119.458 | -119.101 | -0.07782 | 0 | -0.22888 | 114.8666 | 0.31128 | 0.40283 | 0.3891 | 0.48065 | -0.027466 | -0.022888 | -0.14648 | 0.34332 | 0.6546 | 0.29755 | 0.68207 | 0.32501 | 114.9445 | 121.5958 | 0.37079 | 121.6278 | 121.8246 | 121.7514 | 121.7468 | 121.7239 | -121.8246 | -121.7743 | 121.5179 | 121.6003 | 119.4305 | 119.4946
315.2031 | 121.843 | -119.3893 | 2.2659 | 0.026856 | 0.0018457 | 0.13146 | 0.065837 | -0.0016898 | -0.0012604 | 5.7688e-05 | 0.013702 | 0.0028583 | 0.071186 | 0.05912 | -0.0041551 | 0.01988 | 0.0012839 | -0.32501 | 2.2659 | -119.5312 | 2.1423 | -4.8386 | -119.3436 | -119.4168 | -0.19684 | 2.2476 | -119.4855 | 2.2064 | -118.9911 | -119.0369 | -118.9682 | -0.14191 | 0 | -0.1236 | 114.5508 | -0.027466 | 0.045776 | 0.11444 | 0.18768 | -0.096131 | -0.01831 | -0.059509 | 0.39825 | 0.42114 | 0.35248 | 0.51727 | 0.44861 | 114.6927 | 121.6736 | 0.49438 | 121.6919 | 121.7972 | 121.7331 | 121.6553 | 121.637 | -121.7972 | -121.7514 | 121.5317 | 121.5958 | 119.0643 | 119.1925
316.9531 | 121.756 | -119.1834 | 2.5406 | 0.011597 | 0.0078271 | 0.13082 | 0.067546 | 0.0023692 | -0.0029694 | 0.0017667 | 0.0014953 | 0.00093566 | 0.068195 | 0.065742 | -0.0022325 | 0.01753 | -0.0017069 | -0.27466 | 2.4994 | -119.3069 | 2.3666 | -4.1977 | -118.8446 | -118.7943 | -0.18768 | 2.4673 | -119.2245 | 2.3804 | -118.8263 | -118.9087 | -118.6066 | -0.1236 | -0.041198 | -0.17395 | 114.9857 | 0.3891 | 0.33875 | 0.5127 | 0.46234 | -0.041198 | -0.073242 | -0.16022 | 0.35706 | 0.57678 | 0.27466 | 0.61798 | 0.31586 | 115.1093 | 121.6736 | 0.39825 | 121.6049 | 121.8063 | 121.6919 | 121.6827 | 121.6507 | -121.8475 | -121.7651 | 121.55 | 121.5637 | 118.9087 | 118.9957
318.625 | 121.7468 | -118.8766 | 2.8381 | 0.0039673 | 0.0059045 | 0.13104 | 0.067759 | 0.0017282 | -0.0021148 | -0.0037875 | 0.0014953 | 0.00072206 | 0.068622 | 0.060829 | -0.0033005 | 0.018171 | -0.0012795 | -0.27924 | 2.7924 | -119.0048 | 2.6138 | -4.6463 | -118.7439 | -118.6478 | -0.20599 | 2.829 | -118.9316 | 2.6779 | -118.5562 | -118.6066 | -118.483 | -0.12817 | -0.045777 | -0.2243 | 114.2303 | 0.22888 | 0.13275 | 0.35706 | 0.26093 | -0.054932 | -0.009156 | -0.16022 | 0.32044 | 0.39368 | 0.27008 | 0.44861 | 0.32501 | 114.3585 | 121.6187 | 0.37537 | 121.6095 | 121.7972 | 121.7606 | 121.669 | 121.7056 | -121.843 | -121.7697 | 121.4905 | 121.5546 | 118.5974 | 118.6707
320.3594 | 121.8155 | -119.4351 | 2.2247 | 0.011597 | 0.0031275 | 0.12933 | 0.065196 | 0.00087375 | -0.0036102 | -0.0037875 | -0.0015565 | -0.00034614 | 0.070118 | 0.068947 | -0.0018051 | 0.01753 | 0.0014975 | -0.35706 | 2.2018 | -119.6045 | 2.0599 | -4.4952 | -119.4626 | -119.3848 | -0.1831 | 2.179 | -119.545 | 2.1835 | -119.0323 | -119.0872 | -118.9636 | -0.16937 | -0.022888 | -0.16479 | 114.9399 | 0.050354 | -0.027465 | 0.21973 | 0.14191 | -0.10986 | -0.045776 | -0.041198 | 0.40283 | 0.4715 | 0.3479 | 0.58136 | 0.45776 | 115.1093 | 121.6644 | 0.5127 | 121.7285 | 121.8063 | 121.7239 | 121.637 | 121.6141 | -121.8292 | -121.7697 | 121.4951 | 121.6187 | 119.0781 | 119.252
322.0312 | 121.8658 | -119.5679 | 2.0462 | 0.042114 | 0.0054773 | 0.13403 | 0.066264 | 1.915e-05 | -0.00061944 | 0.00069849 | 0.019806 | 0.0017901 | 0.06969 | 0.062965 | -9.605e-05 | 0.019452 | -0.00021153 | -0.3067 | 2.0782 | -119.696 | 2.0416 | -4.1702 | -119.4763 | -119.5358 | -0.091553 | 2.0462 | -119.7006 | 2.037 | -119.133 | -119.1971 | -119.1055 | -0.12817 | 0.032043 | -0.004578 | 115.3976 | 0.032043 | 0.091553 | 0.16022 | 0.21973 | -0.13275 | 0 | -0.009156 | 0.43487 | 0.46234 | 0.37079 | 0.59509 | 0.50354 | 115.5258 | 121.7377 | 0.56763 | 121.7377 | 121.7743 | 121.7468 | 121.6461 | 121.6141 | -121.7422 | -121.7468 | 121.6095 | 121.6049 | 119.2612 | 119.4763
323.75 | 121.5591 | -118.4921 | 3.0212 | -0.0036622 | 0.0097497 | 0.010553 | -0.0016685 | -0.0027578 | -0.0046782 | 0.00048489 | 0.022858 | 0.0024311 | 0.070331 | 0.060829 | -0.0084275 | 0.016248 | -0.0032021 | 0.1236 | 2.9755 | 0.20142 | 2.8198 | 0.26093 | 0.34332 | 0.35248 | -0.24261 | 2.9984 | -118.5699 | 2.8244 | -118.1213 | -118.1534 | -118.0618 | 118.6935 | -0.045776 | -0.20142 | 118.7531 | 118.8446 | 118.8354 | 0.15106 | 0.14191 | -0.07782 | -0.022888 | -0.19684 | 0.37079 | 0.4303 | 0.33875 | 0.50812 | 0.41657 | 0.059509 | 2.6184 | 0.44861 | 121.3943 | 2.774 | 121.5683 | 121.4676 | 121.4905 | -2.8198 | -121.5912 | 121.3119 | 121.3165 | 118.6157 | 118.2495
325.4844 | 121.3486 | -118.602 | 3.1128 | 0.0039673 | 0.0039819 | 0.013544 | -0.00017307 | 0.0010874 | -0.004251 | 0.0024075 | 0.022858 | 0.0047809 | 0.069904 | 0.055702 | -0.0058639 | 0.015394 | 0.0010703 | -0.059509 | 3.1082 | 0.059509 | 2.9022 | 0.10071 | 0.19226 | 0.21057 | -0.20142 | 3.067 | -118.7073 | 2.8976 | -118.2358 | -118.309 | -118.1992 | 118.6615 | -0.004578 | -0.21057 | 118.7027 | 118.8126 | 118.7943 | 0.15106 | 0.13275 | -0.10528 | -0.045776 | -0.21515 | 0.36621 | 0.40283 | 0.29297 | 0.50812 | 0.39825 | 0.041199 | 2.8427 | 0.4715 | 121.6049 | 3.0487 | 121.7743 | 121.7102 | 121.669 | -3.0533 | -121.8201 | 121.5042 | 121.4996 | 118.5425 | 118.4006
327.2188 | 121.8338 | -118.6569 | 2.9846 | -0.011291 | 0.0039819 | 0.015253 | -0.0016685 | -0.0019034 | -0.0029694 | -0.00036951 | 0.0014953 | 0.0015765 | 0.068195 | 0.064461 | -0.00095065 | 0.016034 | 0.00085667 | -0.09613 | 2.9434 | 0.11444 | 2.8702 | 0.18768 | 0.25635 | 0.25635 | -0.14191 | 2.9068 | -118.7714 | 2.9205 | -118.2358 | -118.2861 | -118.222 | 118.7714 | -0.041199 | -0.11444 | 118.8446 | 118.9133 | 118.9133 | 0.14191 | 0.14191 | -0.11444 | -0.07782 | -0.064087 | 0.42114 | 0.43487 | 0.37079 | 0.54932 | 0.48523 | 0.073242 | 2.7557 | 0.53558 | 121.6919 | 2.829 | 121.6782 | 121.6003 | 121.5637 | -2.8702 | -121.756 | 121.5271 | 121.5775 | 118.5608 | 118.515
328.9531 | 121.8384 | -118.8309 | 2.7878 | -0.0036622 | 0.0050501 | 0.013757 | 0.00025413 | -0.0025442 | -0.0027556 | -0.0022921 | 0.0075989 | 0.0022175 | 0.069477 | 0.075355 | 0.00097195 | 0.016675 | -0.0025613 | -0.082397 | 2.7512 | 0.33417 | 2.7328 | 0.19684 | 0.45319 | 0.45319 | -0.10986 | 2.742 | -118.9224 | 2.774 | -118.4189 | -118.4738 | -118.364 | 119.165 | -0.036621 | -0.054932 | 119.0277 | 119.2841 | 119.2841 | 0.11902 | 0.11902 | -0.091552 | -0.045777 | -0.013733 | 0.41199 | 0.46692 | 0.35706 | 0.55847 | 0.44861 | -0.13733 | 2.3987 | 0.50354 | 121.6965 | 2.417 | 121.6644 | 121.582 | 121.5729 | -2.4536 | -121.7102 | 121.5637 | 121.6049 | 118.7485 | 118.721
330.7188 | 121.7789 | -118.808 | 2.8748 | 0.019226 | 0.0056909 | 0.014825 | 0.0017495 | 0.0034372 | -0.0010468 | -0.0010105 | 0.0075989 | 0.0026447 | 0.070118 | 0.064247 | -0.0054367 | 0.017316 | -0.0036295 | -0.013733 | 2.8702 | 0.091553 | 2.7603 | 0.14648 | 0.24261 | 0.23346 | -0.086975 | 2.8519 | -118.8995 | 2.7786 | -118.4143 | -118.4692 | -118.3868 | 118.8995 | -0.004578 | -0.11444 | 118.9545 | 119.0414 | 119.0506 | 0.14191 | 0.15106 | -0.091553 | -0.022888 | -0.096131 | 0.39368 | 0.42114 | 0.33874 | 0.51269 | 0.4303 | 0.054931 | 2.6688 | 0.48523 | 121.6782 | 2.7786 | 121.7514 | 121.6782 | 121.6599 | -2.7832 | -121.7743 | 121.5683 | 121.5866 | 118.7942 | 118.721
332.3906 | 121.7056 | -119.1055 | 2.5681 | -0.0036622 | 0.0073999 | 0.015894 | 0.0036721 | -0.003826 | -0.002542 | -0.0016513 | 0.0045471 | 0.0039265 | 0.068622 | 0.062538 | -0.0024461 | 0.015821 | 0.0034201 | -0.10071 | 2.5589 | 0.13275 | 2.3621 | 0.045776 | 0.16479 | 0.1831 | -0.25177 | 2.5497 | -119.2108 | 2.3849 | -118.8171 | -118.8858 | -118.7439 | 119.2383 | -0.009155 | -0.20599 | 119.1513 | 119.2886 | 119.2703 | 0.050354 | 0.032044 | -0.10528 | -0.01831 | -0.1831 | 0.28839 | 0.36163 | 0.21973 | 0.46692 | 0.32501 | -0.086975 | 2.2293 | 0.39368 | 121.5958 | 2.4261 | 121.7606 | 121.6644 | 121.6553 | -2.4353 | -121.7789 | 121.4676 | 121.4905 | 119.0048 | 118.8538
334.0625 | 121.6965 | -118.721 | 2.9709 | 0.0039673 | 0.0061181 | 0.01568 | 0.0017495 | 0.0066416 | -0.0019012 | -0.0012241 | 0.0014953 | 0.00072206 | 0.068836 | 0.060188 | -0.0024461 | 0.014753 | 0.00085667 | -0.09613 | 2.9663 | 0.10986 | 2.7924 | 0.059509 | 0.14648 | 0.16022 | -0.26093 | 2.9526 | -118.7943 | 2.8061 | -118.4097 | -118.4692 | -118.3365 | 118.8309 | -0.004577 | -0.17853 | 118.7805 | 118.8812 | 118.8675 | 0.050354 | 0.036621 | -0.073242 | -0.01831 | -0.1648 | 0.31128 | 0.38452 | 0.25177 | 0.45776 | 0.32501 | -0.050354 | 2.6825 | 0.38452 | 121.6003 | 2.8564 | 121.7468 | 121.6873 | 121.6736 | -2.861 | -121.7651 | 121.5134 | 121.5271 | 118.6249 | 118.4601
335.7969 | 121.7285 | -119.1879 | 2.5269 | -0.0036622 | 0.0059045 | 0.016321 | 0.0017495 | -0.0012624 | -0.00061944 | 0.00027129 | 0.0014953 | 0.0011493 | 0.068195 | 0.06147 | -0.00052345 | 0.018598 | -0.00021153 | -0.12817 | 2.5085 | 0.10071 | 2.3071 | 0.027466 | 0.10986 | 0.13275 | -0.27008 | 2.4673 | -119.2841 | 2.3621 | -118.895 | -118.9316 | -118.8126 | 119.2886 | -0.01831 | -0.21973 | 119.2154 | 119.3207 | 119.2978 | 0.032043 | 0.009155 | -0.096131 | -0.059509 | -0.16479 | 0.29297 | 0.37537 | 0.25635 | 0.4715 | 0.35248 | -0.073242 | 2.2064 | 0.3891 | 121.6461 | 2.4078 | 121.7514 | 121.6965 | 121.6553 | -2.4261 | -121.8109 | 121.4951 | 121.55 | 119.0598 | 118.9178
337.5312 | 121.7377 | -119.3298 | 2.4033 | 0.042114 | 0.0073999 | 0.013544 | 0.0017495 | 0.0015146 | -0.0016876 | -0.00015591 | 0.022858 | 0.0015765 | 0.073108 | 0.056557 | -0.0060777 | 0.016034 | -0.0027749 | -0.073242 | 2.4216 | 0.10071 | 2.1927 | 0.10071 | 0.21057 | 0.23346 | -0.1831 | 2.3758 | -119.4489 | 2.211 | -118.9682 | -119.0094 | -118.9224 | 119.4305 | 0.018311 | -0.21057 | 119.4305 | 119.5633 | 119.5404 | 0.13275 | 0.10986 | -0.11902 | -0.027466 | -0.19226 | 0.36163 | 0.40741 | 0.32044 | 0.52643 | 0.43945 | 0 | 2.092 | 0.48065 | 121.6599 | 2.3209 | 121.8246 | 121.7514 | 121.7056 | -2.3026 | -121.8521 | 121.5225 | 121.5408 | 119.2566 | 119.1467
339.2656 | 121.8155 | -118.8171 | 2.8107 | 0.026856 | 0.0022729 | 0.014612 | -0.0010275 | 0.00023275 | -0.00083304 | -0.0033603 | 0.010651 | 0.00050846 | 0.070118 | 0.062324 | -0.0028733 | 0.019452 | -0.00021153 | -0.12817 | 2.7924 | 0.10986 | 2.6962 | 0.15106 | 0.20599 | 0.21515 | -0.19226 | 2.774 | -118.927 | 2.742 | -118.4555 | -118.4967 | -118.4006 | 118.927 | -0.018311 | -0.11444 | 118.9682 | 119.0323 | 119.0231 | 0.10529 | 0.096131 | -0.10986 | -0.036621 | -0.068665 | 0.36163 | 0.41656 | 0.32044 | 0.52643 | 0.4303 | 0.041199 | 2.5864 | 0.4715 | 121.669 | 2.6825 | 121.701 | 121.6095 | 121.5912 | -2.7008 | -121.7377 | 121.5134 | 121.5591 | 118.689 | 118.6249
341 | 121.8338 | -119.2612 | 2.3621 | -0.0036622 | 0.0046227 | 0.014612 | -0.0016685 | -0.00040805 | -0.004251 | -0.00079691 | 0.0014953 | 0.00029486 | 0.067554 | 0.064247 | -0.0037277 | 0.017957 | 0.00042947 | -0.054932 | 2.33 | 0.17853 | 2.33 | 0.22888 | 0.32044 | 0.3067 | -0.086975 | 2.3026 | -119.3848 | 2.33 | -118.84 | -118.895 | -118.8263 | 119.4397 | -0.032044 | -0.032044 | 119.4901 | 119.5679 | 119.5816 | 0.12817 | 0.14191 | -0.1236 | -0.05951 | -0.032044 | 0.42114 | 0.43487 | 0.36621 | 0.55847 | 0.48981 | 0.050354 | 2.1515 | 0.54474 | 121.7148 | 2.1515 | 121.6873 | 121.5912 | 121.5637 | -2.1835 | -121.7468 | 121.5912 | 121.5912 | 119.2062 | 119.1742
342.6719 | 121.7514 | -119.3436 | 2.3438 | 0.011597 | 0.0073999 | 0.015894 | 0.0032449 | -0.00062165 | -0.00061944 | -0.0022921 | 0.0075989 | 0.0037127 | 0.068195 | 0.06147 | -0.0015915 | 0.014966 | 0.0010703 | -0.054932 | 2.3483 | 0.10071 | 2.1927 | 0.13275 | 0.18768 | 0.17853 | -0.16022 | 2.3254 | -119.4305 | 2.1973 | -119.0094 | -119.0552 | -118.9545 | 119.4443 | 0.004578 | -0.15106 | 119.4763 | 119.5221 | 119.5312 | 0.07782 | 0.086975 | -0.086975 | -0.018311 | -0.14648 | 0.33417 | 0.3891 | 0.28839 | 0.47607 | 0.37537 | 0.032043 | 2.092 | 0.42114 | 121.6278 | 2.2476 | 121.756 | 121.6919 | 121.669 | -2.243 | -121.7743 | 121.5363 | 121.5408 | 119.2886 | 119.1833
344.4062 | 121.7422 | -119.252 | 2.449 | 0.0039673 | 0.0031275 | 0.013116 | -0.00038667 | 0.0019418 | -0.0027556 | 0.0013395 | 0.0014953 | 0.0032855 | 0.067768 | 0.064247 | -0.0033005 | 0.017743 | -0.0012795 | -0.13275 | 2.4216 | 0.11444 | 2.2202 | 0.050354 | 0.15564 | 0.19684 | -0.25635 | 2.4078 | -119.3436 | 2.2705 | -118.9407 | -118.9865 | -118.8446 | 119.3665 | -0.027466 | -0.22888 | 119.3024 | 119.4489 | 119.4077 | 0.082397 | 0.041199 | -0.091553 | -0.041199 | -0.17853 | 0.31128 | 0.40741 | 0.2655 | 0.49896 | 0.35706 | -0.064087 | 2.1057 | 0.40283 | 121.6141 | 2.3071 | 121.7514 | 121.6736 | 121.6599 | -2.3346 | -121.7926 | 121.4722 | 121.5225 | 119.1193 | 118.9957
346.1562 | 121.7331 | -119.1055 | 2.5955 | -0.0036622 | 0.0073999 | 0.014398 | 0.0011087 | -0.0029714 | -0.002542 | -0.00058311 | -0.0015565 | 0.0013629 | 0.069477 | 0.059761 | 0.0011855 | 0.016675 | -0.0019205 | -0.13275 | 2.6001 | 0.15564 | 2.3621 | 0.027466 | 0.16937 | 0.19226 | -0.25177 | 2.5452 | -119.2062 | 2.417 | -118.8034 | -118.8446 | -118.6981 | 119.2612 | 0.004578 | -0.23346 | 119.133 | 119.2978 | 119.2749 | 0.036621 | 0.013733 | -0.10071 | -0.050354 | -0.17853 | 0.30212 | 0.40741 | 0.26093 | 0.50812 | 0.36163 | -0.12817 | 2.2064 | 0.40283 | 121.6232 | 2.4445 | 121.7514 | 121.7056 | 121.6507 | -2.4399 | -121.8018 | 121.4676 | 121.5225 | 118.9728 | 118.8538
347.8906 | 121.7834 | -119.133 | 2.5772 | 0.034485 | 0.0069727 | 0.015894 | 0.0019631 | 0.0025828 | -0.0010468 | 0.0017667 | 0.0045471 | 0.0034991 | 0.069904 | 0.065315 | -0.0030869 | 0.018598 | -0.00063873 | -0.032043 | 2.5543 | 0.09613 | 2.4399 | 0.15564 | 0.21515 | 0.23346 | -0.11444 | 2.5269 | -119.2383 | 2.4445 | -118.7393 | -118.8034 | -118.689 | 119.2291 | -0.022888 | -0.13733 | 119.2886 | 119.3665 | 119.3481 | 0.13733 | 0.11902 | -0.10528 | -0.050354 | -0.13275 | 0.39368 | 0.44403 | 0.32959 | 0.54932 | 0.43488 | 0.05951 | 2.3438 | 0.49896 | 121.6827 | 2.4582 | 121.7651 | 121.6873 | 121.6599 | -2.4811 | -121.8155 | 121.5729 | 121.5775 | 119.101 | 119.0186
349.5625 | 121.8475 | -119.2062 | 2.4078 | -0.0036622 | 0.0048365 | 0.015039 | 0.00089513 | -0.00040805 | -0.004251 | -0.00058311 | -0.0015565 | 0.0015765 | 0.068836 | 0.062965 | -0.00052345 | 0.01988 | -0.00063873 | -0.14648 | 2.417 | 0.13733 | 2.3026 | 0.14648 | 0.21973 | 0.23346 | -0.16479 | 2.3758 | -119.3069 | 2.3941 | -118.808 | -118.8766 | -118.7622 | 119.3436 | 0.009155 | -0.10529 | 119.3527 | 119.4397 | 119.426 | 0.09613 | 0.082398 | -0.10071 | -0.032044 | -0.013733 | 0.39826 | 0.44403 | 0.32959 | 0.54474 | 0.4303 | 0.009155 | 2.1652 | 0.49896 | 121.701 | 2.2797 | 121.6827 | 121.6232 | 121.582 | -2.2705 | -121.7148 | 121.5088 | 121.6003 | 119.0598 | 119.0414
351.2969 | 121.8658 | -119.2062 | 2.4445 | 0.011597 | 0.0065453 | 0.01333 | -0.00017307 | 0.0010874 | -0.0038238 | -0.0046421 | 0.0014953 | -0.0016277 | 0.06734 | 0.066597 | -0.0022325 | 0.020521 | -0.0049111 | -0.11902 | 2.4261 | 0.14648 | 2.3163 | 0.16937 | 0.25635 | 0.27924 | -0.1236 | 2.3758 | -119.3207 | 2.417 | -118.808 | -118.8446 | -118.7347 | 119.3527 | -0.018311 | -0.12817 | 119.3756 | 119.4855 | 119.4626 | 0.13275 | 0.10986 | -0.11444 | -0.068665 | -0.027466 | 0.39826 | 0.4715 | 0.36163 | 0.58594 | 0.47607 | 0.022889 | 2.1698 | 0.5127 | 121.7377 | 2.2797 | 121.6965 | 121.6324 | 121.582 | -2.298 | -121.7651 | 121.5225 | 121.6232 | 119.0872 | 119.0826
353.0469 | 121.7422 | -119.0964 | 2.5772 | 0.011597 | 0.0063317 | 0.014612 | 0.00025413 | 0.0042918 | -0.0021148 | -0.00058311 | 0.0045471 | 0.0024311 | 0.070118 | 0.056129 | -0.0020187 | 0.016675 | -0.00063873 | -0.086975 | 2.5314 | 0.12817 | 2.3987 | 0.1236 | 0.18768 | 0.20142 | -0.16022 | 2.5177 | -119.2154 | 2.417 | -118.7943 | -118.8538 | -118.7256 | 119.2245 | -0.045776 | -0.17853 | 119.22 | 119.2978 | 119.2841 | 0.073242 | 0.059509 | -0.11902 | -0.059509 | -0.16022 | 0.30212 | 0.37079 | 0.24262 | 0.48981 | 0.36163 | -0.004578 | 2.2705 | 0.42114 | 121.6324 | 2.4033 | 121.7331 | 121.6278 | 121.6141 | -2.449 | -121.7926 | 121.4951 | 121.5134 | 119.0094 | 118.9362
354.7188 | 121.7331 | -118.7485 | 2.9663 | 0.0039673 | 0.0052637 | 0.016962 | -0.00017307 | 0.00023275 | -0.00019224 | 5.7688e-05 | -0.0015565 | 0.0043537 | 0.068622 | 0.054634 | -0.0047959 | 0.016248 | -0.00042513 | -0.064087 | 2.9343 | 0.34332 | 2.7786 | 0.11444 | 0.38452 | 0.41199 | -0.20142 | 2.916 | -118.8263 | 2.8015 | -118.4189 | -118.4647 | -118.3365 | 119.0918 | -0.032044 | -0.18768 | 118.8629 | 119.1605 | 119.133 | 0.068664 | 0.041198 | -0.07782 | -0.050354 | -0.16479 | 0.32959 | 0.41199 | 0.28381 | 0.48981 | 0.36163 | -0.22888 | 2.4353 | 0.40741 | 121.6278 | 2.5909 | 121.7422 | 121.6827 | 121.6644 | -2.623 | -121.7926 | 121.5271 | 121.55 | 118.6844 | 118.5471
356.4688 | 121.756 | -118.9362 | 2.774 | 0.019226 | 0.0063317 | 0.015039 | 0.00025413 | 0.0025828 | -0.0023284 | -0.00058311 | 0.0014953 | 0.0030719 | 0.072681 | 0.069588 | -0.0024461 | 0.017316 | 0.0027793 | -0.07782 | 2.7466 | 1.2543 | 2.6184 | 0.21057 | 1.3458 | 1.3504 | -0.13733 | 2.7145 | -119.014 | 2.6321 | -118.5837 | -118.6386 | -118.5059 | 120.1904 | -0.027466 | -0.15564 | 119.1467 | 120.2866 | 120.282 | 0.096131 | 0.091553 | -0.07782 | -0.059509 | -0.14191 | 0.35248 | 0.4303 | 0.29755 | 0.50812 | 0.37537 | -1.0437 | 1.3641 | 0.4303 | 121.6461 | 1.4923 | 121.7285 | 121.6827 | 121.6507 | -1.5198 | -121.788 | 121.5546 | 121.5683 | 118.8583 | 118.7988
358.1562 | 121.7377 | -118.6981 | 2.9846 | 0.0039673 | 0.0059045 | 0.014398 | -0.0016685 | -0.00019445 | -0.001474 | -0.0014377 | -0.0015565 | 0.0011493 | 0.071186 | 0.060402 | -0.0018051 | 0.01753 | 0.0012839 | -0.14648 | 2.98 | 1.355 | 2.7786 | 0.12817 | 1.4053 | 1.4145 | -0.25635 | 2.9297 | -118.8126 | 2.8244 | -118.3777 | -118.4372 | -118.2953 | 120.0531 | -0.004577 | -0.20599 | 118.8263 | 120.1126 | 120.1035 | 0.05951 | 0.050354 | -0.11444 | -0.054932 | -0.16022 | 0.32043 | 0.40283 | 0.26093 | 0.51727 | 0.37537 | -1.2268 | 1.4236 | 0.43488 | 121.637 | 1.6251 | 121.7422 | 121.6782 | 121.6278 | -1.6296 | -121.7972 | 121.4767 | 121.5225 | 118.5516 | 118.4418
359.9062 | 121.8475 | -118.5104 | 3.067 | 0.0039673 | 0.0037683 | 0.014612 | -0.0025229 | -0.0029714 | -0.001474 | -0.0014377 | 0.0014953 | 0.0020039 | 0.069904 | 0.069801 | -0.0026597 | 0.017103 | -0.00042513 | -0.13733 | 3.0533 | 1.4374 | 3.0029 | 0.23804 | 1.5656 | 1.5884 | -0.16022 | 3.0487 | -118.6386 | 3.0396 | -118.1442 | -118.1763 | -118.0939 | 119.9478 | -0.013733 | -0.064087 | 118.7485 | 120.0989 | 120.076 | 0.15106 | 0.12817 | -0.12817 | -0.018311 | -0.027466 | 0.36621 | 0.41656 | 0.33417 | 0.54474 | 0.46234 | -1.1993 | 1.5656 | 0.49438 | 121.6782 | 1.6159 | 121.6873 | 121.5637 | 121.5591 | -1.6296 | -121.7056 | 121.5134 | 121.55 | 118.3731 | 118.3502
361.5781 | 121.8567 | -118.5883 | 3.0167 | -0.0036622 | 0.0063317 | 0.014825 | -0.0014547 | -0.00019445 | 0.00023496 | -0.0027195 | 0.019806 | 0.0024311 | 0.071186 | 0.065315 | -0.00030965 | 0.018598 | -0.0021341 | -0.07782 | 2.9846 | 1.4236 | 3.0029 | 0.32501 | 1.5701 | 1.5839 | -0.082397 | 2.98 | -118.6981 | 3.0258 | -118.1808 | -118.2266 | -118.1442 | 120.0119 | -0.032044 | -0.013733 | 118.9133 | 120.1721 | 120.1584 | 0.16022 | 0.14648 | -0.10986 | -0.036621 | 0.009155 | 0.40741 | 0.44403 | 0.36163 | 0.55389 | 0.4715 | -1.0986 | 1.5793 | 0.51727 | 121.7239 | 1.561 | 121.6782 | 121.5729 | 121.5683 | -1.593 | -121.7148 | 121.5912 | 121.6141 | 118.5104 | 118.5059
363.25 | 121.8155 | -118.0115 | 3.5843 | 0.011597 | 0.0065453 | 0.016321 | 4.0528e-05 | 0.0017282 | -0.0029694 | -0.0027195 | 0.0045471 | 0.0024311 | 0.069263 | 0.056984 | -0.0035141 | 0.01753 | 0.00042947 | -0.13275 | 3.5477 | 1.6342 | 3.3554 | 0.14648 | 1.6663 | 1.7075 | -0.24719 | 3.5248 | -118.1946 | 3.4103 | -117.8284 | -117.8558 | -117.7139 | 119.6457 | -0.036622 | -0.22888 | 118.158 | 119.7189 | 119.6777 | 0.073242 | 0.032044 | -0.1831 | -0.05951 | -0.17395 | 0.18311 | 0.29755 | 0.15564 | 0.48065 | 0.33875 | -1.4877 | 1.7212 | 0.36621 | 121.6049 | 1.9135 | 121.7194 | 121.5591 | 121.5363 | -1.9501 | -121.7789 | 121.3669 | 121.4218 | 117.8787 | 117.7643
364.9844 | 121.8063 | -119.3619 | 2.2888 | -0.0036622 | 0.0046227 | 0.015466 | 0.0028177 | 0.0010874 | -0.00061944 | -0.0022921 | -0.0046081 | 0.0039265 | 0.06734 | 0.063179 | -0.0037277 | 0.017957 | -0.0012795 | -0.10529 | 2.3254 | 1.0162 | 2.0645 | 0.10529 | 0.9613 | 0.99792 | -0.37079 | 2.179 | -119.5862 | 2.1744 | -119.0781 | -119.133 | -118.9911 | 120.3781 | 0.036621 | -0.2243 | 119.4672 | 120.3598 | 120.3232 | -0.01831 | -0.054931 | -0.2243 | -0.10986 | -0.11444 | 0.28381 | 0.37079 | 0.22888 | 0.59509 | 0.45319 | -0.91095 | 1.0483 | 0.50812 | 121.7606 | 1.3092 | 121.7651 | 121.6873 | 121.5408 | -1.2726 | -121.875 | 121.4264 | 121.5363 | 119.2566 | 118.9911
366.7188 | 121.9025 | -119.6045 | 2.0325 | -0.011291 | 0.0022729 | 0.013757 | -0.0023093 | 0.0027964 | -0.0055328 | -0.0022921 | -0.0015565 | 0.0022175 | 0.066486 | 0.066383 | -0.0069321 | 0.018598 | -0.0019205 | -0.022888 | 1.9913 | 0.92468 | 1.9958 | 0.27466 | 1.0849 | 1.0757 | -0.09613 | 1.9913 | -119.7052 | 2.005 | -119.22 | -119.2429 | -119.1513 | 120.5292 | -0.041199 | -0.036621 | 119.8791 | 120.6802 | 120.6894 | 0.15106 | 0.16022 | -0.10071 | -0.041199 | -0.027466 | 0.38452 | 0.45319 | 0.36163 | 0.55389 | 0.46234 | -0.65003 | 1.0712 | 0.48523 | 121.7102 | 1.0666 | 121.6965 | 121.5958 | 121.5958 | -1.1078 | -121.7377 | 121.6003 | 121.6095 | 119.5816 | 119.5084
368.3906 | 121.9116 | -120.1996 | 1.4603 | 0.0039673 | 0.0027001 | 0.016962 | -0.0033775 | -0.00062165 | -0.0046782 | -0.0029331 | -0.0015565 | 0.00093566 | 0.068836 | 0.067238 | -0.00095065 | 0.018598 | -0.00021153 | -0.054932 | 1.4191 | 0.64545 | 1.4328 | 0.28839 | 0.82855 | 0.81024 | -0.073242 | 1.4191 | -120.2728 | 1.4511 | -119.7556 | -119.7876 | -119.7372 | 120.845 | -0.041199 | -0.027466 | 120.488 | 121.0098 | 121.0281 | 0.1648 | 0.1831 | -0.073242 | -0.041199 | -0.009155 | 0.44403 | 0.46234 | 0.41199 | 0.53558 | 0.48523 | -0.35706 | 0.78735 | 0.51727 | 121.7239 | 0.77362 | 121.6919 | 121.6187 | 121.6187 | -0.81482 | -121.7331 | 121.6324 | 121.6507 | 120.1447 | 120.1263
370.0625 | 121.8613 | -120.3644 | 1.3229 | -0.0036622 | 0.0041955 | 0.015894 | -0.0035911 | 0.00044655 | -0.0046782 | 0.0017667 | -0.0015565 | 0.00050846 | 0.06734 | 0.060615 | -0.0052231 | 0.014539 | -0.0023477 | -0.027466 | 1.2863 | 0.56305 | 1.2451 | 0.23346 | 0.70038 | 0.69122 | -0.09613 | 1.2726 | -120.4468 | 1.2634 | -119.9387 | -119.9799 | -119.8929 | 120.9274 | -0.036621 | -0.07782 | 120.5978 | 121.0556 | 121.0648 | 0.12817 | 0.13733 | -0.082397 | -0.050354 | -0.059509 | 0.42572 | 0.4715 | 0.38452 | 0.55389 | 0.46692 | -0.32959 | 0.68207 | 0.50812 | 121.7102 | 0.72327 | 121.7194 | 121.6507 | 121.637 | -0.75989 | -121.7697 | 121.6095 | 121.6278 | 120.3369 | 120.2682
371.7969 | 121.8796 | -120.1263 | 1.5656 | 0.042114 | 0.021926 | 0.015466 | -0.00060027 | -0.00019445 | 0.00044856 | 0.0011257 | 0.013702 | 0.0013629 | 0.069049 | 0.064033 | -0.00095065 | 0.016675 | -0.00021153 | -0.032043 | 1.4969 | 1.3046 | 1.4923 | 1.5976 | 1.4511 | 1.474 | -0.086975 | 1.4923 | -120.2133 | 1.5518 | -119.7144 | -119.7556 | -119.664 | 121.431 | -0.068665 | -0.073242 | 121.7239 | 121.6003 | 121.5775 | 0.16937 | 0.14648 | -0.086975 | -0.073242 | -0.013733 | 0.41199 | 0.46234 | 0.37079 | 0.54932 | 0.45776 | 0.29297 | 0.18768 | 0.49896 | 121.7651 | 0.19226 | 121.7056 | 121.6232 | 121.6187 | -0.26093 | -121.7789 | 121.6187 | 121.6782 | 120.0943 | 120.0394
373.4688 | 121.9345 | -120.1309 | 1.5427 | 0.011597 | 0.020858 | 0.01568 | -0.0023093 | -0.002117 | -0.0044646 | -0.00079691 | 0.0045471 | -0.0020551 | 0.067981 | 0.070015 | -0.0033005 | 0.017743 | -0.0021341 | -0.054932 | 1.5198 | 1.3367 | 1.506 | 1.6434 | 1.4923 | 1.5015 | -0.068665 | 1.4786 | -120.2179 | 1.5472 | -119.6732 | -119.7144 | -119.6228 | 121.4676 | -0.022889 | -0.036622 | 121.7743 | 121.6324 | 121.6232 | 0.1648 | 0.15564 | -0.086976 | -0.064087 | 0.004577 | 0.45776 | 0.50812 | 0.41657 | 0.59509 | 0.50354 | 0.3067 | 0.16937 | 0.54474 | 121.7651 | 0.18311 | 121.6965 | 121.6507 | 121.6095 | -0.20599 | -121.7606 | 121.637 | 121.6782 | 120.076 | 120.0623
375.2031 | 121.9254 | -120.0485 | 1.6525 | -0.018921 | 0.024063 | 0.014825 | -0.0023093 | -0.003185 | -0.0038238 | -0.00015591 | -0.0015565 | 0.0022175 | 0.06734 | 0.064461 | -0.0039413 | 0.017316 | 0.0012839 | -0.027466 | 1.6022 | 1.4328 | 1.5793 | 1.7532 | 1.5884 | 1.6113 | -0.041199 | 1.6022 | -120.0989 | 1.6113 | -119.5679 | -119.6365 | -119.5404 | 121.4813 | -0.050354 | -0.073242 | 121.8018 | 121.6599 | 121.637 | 0.17853 | 0.15564 | -0.050354 | -0.050354 | -0.041199 | 0.48065 | 0.50812 | 0.41199 | 0.55847 | 0.46234 | 0.32044 | 0.14648 | 0.53101 | 121.7102 | 0.16937 | 121.701 | 121.6507 | 121.6507 | -0.21973 | -121.7514 | 121.6278 | 121.6599 | 120.0211 | 120.0073
376.9375 | 121.9116 | -120.5566 | 1.1124 | 0.0039673 | 0.019576 | 0.016534 | 0.0015359 | 0.0072824 | 0.00066216 | 0.0015531 | 0.016754 | 0.0028583 | 0.068409 | 0.064674 | 0.00033115 | 0.019025 | 0.00085667 | 0 | 1.1169 | 0.90637 | 1.0941 | 1.2131 | 1.0666 | 1.0849 | -0.07782 | 1.0849 | -120.6802 | 1.1169 | -120.1309 | -120.1996 | -120.1035 | 121.463 | 0.004577 | -0.018311 | 121.7697 | 121.6415 | 121.6232 | 0.17853 | 0.16022 | -0.1236 | -0.027466 | 0.004577 | 0.42572 | 0.45319 | 0.35706 | 0.57678 | 0.48065 | 0.3067 | 0.18768 | 0.54932 | 121.7972 | 0.21057 | 121.7651 | 121.6736 | 121.6415 | -0.20599 | -121.7926 | 121.6507 | 121.6736 | 120.5566 | 120.4788
378.6719 | 121.8018 | -120.2911 | 1.4191 | 0.011597 | 0.021713 | 0.013757 | -0.00017307 | 0.0036508 | -0.0016876 | -0.00058311 | -0.0015565 | 0.0041401 | 0.071186 | 0.064247 | -0.0022325 | 0.016248 | 0.0021383 | -0.09613 | 1.4236 | 1.1627 | 1.2268 | 1.3367 | 1.1856 | 1.2177 | -0.24261 | 1.4053 | -120.3873 | 1.2955 | -119.9661 | -120.0256 | -119.8654 | 121.4539 | 0.004578 | -0.19226 | 121.6278 | 121.5088 | 121.4767 | 0.054931 | 0.022888 | -0.09613 | -0.013733 | -0.1236 | 0.32501 | 0.42572 | 0.2655 | 0.52185 | 0.36163 | 0.17395 | 0.064087 | 0.42114 | 121.6827 | 0.26093 | 121.7926 | 121.7148 | 121.6965 | -0.25635 | -121.8063 | 121.5179 | 121.5866 | 120.195 | 120.0485
380.3594 | 121.9345 | -120.4697 | 1.2451 | 0.019226 | 0.01744 | 0.012476 | -0.0025229 | -0.00040805 | -0.0016876 | -0.0020785 | -0.0015565 | 0.0013629 | 0.069477 | 0.061684 | -0.0039413 | 0.016675 | -0.00021153 | -0.16022 | 1.2039 | 1.0391 | 1.1993 | 1.3367 | 1.2085 | 1.2177 | -0.18768 | 1.1765 | -120.5292 | 1.2131 | -119.9844 | -120.0211 | -119.9661 | 121.5088 | -0.041199 | -0.045776 | 121.8063 | 121.6873 | 121.6782 | 0.17853 | 0.16937 | -0.059509 | -0.068664 | -0.032043 | 0.48523 | 0.50354 | 0.44861 | 0.56305 | 0.50812 | 0.29755 | 0.16022 | 0.54474 | 121.7422 | 0.16479 | 121.7056 | 121.6736 | 121.6461 | -0.20599 | -121.7743 | 121.669 | 121.6827 | 120.3094 | 120.282
382.0938 | 121.8521 | -120.2637 | 1.4648 | -0.0036622 | 0.023422 | 0.016107 | 4.0528e-05 | 0.0025828 | -0.0012604 | -0.0010105 | 0.0014953 | 0.0015765 | 0.06969 | 0.065742 | -0.0015915 | 0.017316 | -0.0053385 | -0.10529 | 1.4648 | 1.2314 | 1.3092 | 1.4053 | 1.2589 | 1.3092 | -0.21973 | 1.4328 | -120.3461 | 1.3733 | -119.87 | -119.9295 | -119.8059 | 121.4951 | 0 | -0.15564 | 121.669 | 121.5729 | 121.5225 | 0.07782 | 0.027466 | -0.082397 | -0.032044 | -0.091553 | 0.39368 | 0.45776 | 0.33417 | 0.54016 | 0.41657 | 0.17395 | 0.07782 | 0.47607 | 121.7194 | 0.23346 | 121.7789 | 121.7285 | 121.6965 | -0.23346 | -121.8109 | 121.5729 | 121.637 | 120.1584 | 120.0439
383.8438 | 121.7743 | -120.314 | 1.4557 | -0.0036622 | 0.023208 | 0.013757 | -0.0014547 | 0.001301 | -0.0040374 | -0.0018649 | 0.0014953 | 0.0022175 | 0.067981 | 0.062111 | -0.0069321 | 0.016675 | 0.0014975 | -0.050354 | 1.4145 | 1.2177 | 1.268 | 1.3962 | 1.2909 | 1.3 | -0.20599 | 1.4191 | -120.3827 | 1.2817 | -119.9387 | -119.9844 | -119.8791 | 121.5317 | -0.041198 | -0.18768 | 121.7102 | 121.6141 | 121.6049 | 0.082398 | 0.073243 | -0.068664 | -0.036621 | -0.17395 | 0.37537 | 0.43488 | 0.32959 | 0.50354 | 0.39825 | 0.17853 | 0.050354 | 0.44403 | 121.6644 | 0.19684 | 121.8018 | 121.7285 | 121.7331 | -0.23804 | -121.8384 | 121.582 | 121.5958 | 120.2637 | 120.108
385.5312 | 121.875 | -120.3278 | 1.3504 | 0.034485 | 0.022567 | 0.016962 | -0.00038667 | 0.0023692 | -0.00019224 | -0.00079691 | 0.016754 | 0.0013629 | 0.069904 | 0.072365 | -0.0035141 | 0.018812 | -0.0019205 | -0.059509 | 1.3596 | 1.1581 | 1.3367 | 1.4511 | 1.3138 | 1.3412 | -0.10986 | 1.3458 | -120.4239 | 1.3412 | -119.9066 | -119.9661 | -119.8608 | 121.4859 | 0.009155 | -0.013733 | 121.7789 | 121.669 | 121.6415 | 0.18311 | 0.15564 | -0.09613 | -0.004578 | -0.009155 | 0.42114 | 0.46692 | 0.36163 | 0.56305 | 0.45776 | 0.29297 | 0.17853 | 0.51727 | 121.7651 | 0.20142 | 121.7697 | 121.6873 | 121.6736 | -0.19226 | -121.7743 | 121.6644 | 121.669 | 120.2682 | 120.2179
387.2656 | 121.8567 | -120.0577 | 1.6571 | 0.034485 | 0.025985 | 0.016962 | 0.00046793 | 1.915e-05 | -0.00061944 | -0.00036951 | 0.0075989 | 0.0022175 | 0.070972 | 0.06617 | -0.0026597 | 0.017957 | -0.0021341 | -0.068665 | 1.6296 | 1.4511 | 1.5564 | 1.6754 | 1.5564 | 1.5747 | -0.19684 | 1.6022 | -120.1584 | 1.5884 | -119.6732 | -119.696 | -119.5953 | 121.5088 | -0.027465 | -0.10071 | 121.7331 | 121.6324 | 121.6141 | 0.1236 | 0.10528 | -0.10071 | -0.054931 | -0.068664 | 0.38452 | 0.46234 | 0.36163 | 0.56305 | 0.46234 | 0.2243 | 0.10528 | 0.48523 | 121.7468 | 0.17853 | 121.7606 | 121.6873 | 121.6599 | -0.20599 | -121.8155 | 121.6141 | 121.6461 | 119.989 | 119.8608
389 | 121.7468 | -120.1492 | 1.6022 | 0.0039673 | 0.02684 | 0.014185 | 0.00046793 | 0.0017282 | -0.00040584 | 0.0011257 | 0.0014953 | 0.0030719 | 0.068409 | 0.058052 | -0.00073705 | 0.017743 | -0.0017069 | -0.032043 | 1.5518 | 1.3092 | 1.387 | 1.474 | 1.3596 | 1.3824 | -0.25177 | 1.5656 | -120.2545 | 1.4145 | -119.8563 | -119.8975 | -119.7464 | 121.4584 | -0.050354 | -0.21515 | 121.6232 | 121.5317 | 121.5088 | 0.073242 | 0.050354 | -0.10529 | -0.036621 | -0.18768 | 0.29297 | 0.40283 | 0.25177 | 0.50812 | 0.35706 | 0.1648 | 0.07782 | 0.39826 | 121.669 | 0.24262 | 121.8201 | 121.701 | 121.7148 | -0.29297 | -121.8567 | 121.5363 | 121.5637 | 120.1172 | 119.8975
390.75 | 121.7606 | -120.1813 | 1.5472 | 0.0039673 | 0.023849 | 0.014612 | 0.00025413 | -0.002117 | -0.0019012 | -0.0016513 | 0.0014953 | 0.0028583 | 0.070545 | 0.060402 | -0.0015915 | 0.018598 | 0.00021567 | 0.018311 | 1.5335 | 1.3138 | 1.3596 | 1.4648 | 1.3367 | 1.3641 | -0.21515 | 1.5198 | -120.2682 | 1.3733 | -119.8791 | -119.9203 | -119.783 | 121.4951 | -0.013733 | -0.18768 | 121.6461 | 121.5454 | 121.5179 | 0.050354 | 0.022888 | -0.086976 | -0.027466 | -0.17395 | 0.30212 | 0.39825 | 0.26093 | 0.48523 | 0.3479 | 0.15106 | 0.045776 | 0.3891 | 121.6415 | 0.21973 | 121.788 | 121.7148 | 121.701 | -0.23346 | -121.8155 | 121.5408 | 121.5546 | 120.1996 | 119.9661
392.4375 | 121.8246 | -120.1035 | 1.6205 | 0.042114 | 0.025131 | 0.016321 | -0.00017307 | -0.0010488 | -0.0010468 | 0.00027129 | 0.010651 | 0.0041401 | 0.069049 | 0.052711 | -0.0043687 | 0.017743 | -0.0027749 | 0.068665 | 1.6205 | 1.3504 | 1.4603 | 1.561 | 1.4786 | 1.4694 | -0.14191 | 1.6022 | -120.2133 | 1.4969 | -119.7052 | -119.7556 | -119.6503 | 121.4539 | 0 | -0.16022 | 121.6644 | 121.5729 | 121.582 | 0.11902 | 0.12817 | -0.10986 | -0.01831 | -0.1236 | 0.39825 | 0.45319 | 0.3479 | 0.56305 | 0.45776 | 0.21057 | 0.10986 | 0.50812 | 121.7102 | 0.27008 | 121.8155 | 121.7239 | 121.7056 | -0.27008 | -121.8338 | 121.5637 | 121.6003 | 120.1721 | 119.9615
394.1875 | 121.9025 | -120.0943 | 1.6113 | 0.0039673 | 0.023208 | 0.01333 | -0.0031637 | 0.00301 | -0.0033966 | -0.0018649 | 0.0014953 | 0.00029486 | 0.067768 | 0.062538 | -0.0054367 | 0.017743 | -0.0023477 | 0.036621 | 1.5564 | 1.4099 | 1.5427 | 1.6983 | 1.5656 | 1.5518 | -0.068665 | 1.5518 | -120.1904 | 1.5747 | -119.6411 | -119.6915 | -119.6136 | 121.5042 | -0.054932 | -0.068664 | 121.7926 | 121.6461 | 121.6599 | 0.14191 | 0.15564 | -0.096131 | -0.059509 | -0.036621 | 0.45319 | 0.48065 | 0.40283 | 0.57678 | 0.49896 | 0.28839 | 0.13275 | 0.54932 | 121.7651 | 0.14648 | 121.7422 | 121.6507 | 121.6461 | -0.20142 | -121.8018 | 121.637 | 121.669 | 120.1309 | 120.0256
395.9531 | 121.7789 | -120.1172 | 1.6388 | 0.0039673 | 0.02449 | 0.012262 | -0.0010275 | -0.00062165 | -0.0016876 | -0.00036951 | -0.0015565 | 0.00072206 | 0.068836 | 0.061684 | -0.0052231 | 0.017957 | 0.0021383 | -0.013733 | 1.6159 | 1.3779 | 1.4191 | 1.5335 | 1.4648 | 1.4832 | -0.16479 | 1.6296 | -120.2499 | 1.4511 | -119.783 | -119.8242 | -119.7052 | 121.4951 | -0.022888 | -0.21973 | 121.6507 | 121.6003 | 121.582 | 0.10529 | 0.086975 | -0.13275 | -0.009155 | -0.18768 | 0.33417 | 0.41199 | 0.29297 | 0.54474 | 0.42572 | 0.15564 | 0.041198 | 0.46692 | 121.701 | 0.23804 | 121.8796 | 121.7331 | 121.7468 | -0.26093 | -121.8887 | 121.5363 | 121.5683 | 120.1035 | 119.9524
397.6406 | 121.8338 | -120.1218 | 1.5701 | 0.026856 | 0.027694 | 0.015039 | -0.0010275 | -0.0027578 | -0.0027556 | -0.00036951 | 0.010651 | 0.0041401 | 0.070118 | 0.06147 | -0.0022325 | 0.018812 | -0.0021341 | 0.11444 | 1.5884 | 1.3367 | 1.4557 | 1.5701 | 1.4786 | 1.4832 | -0.1236 | 1.5701 | -120.2545 | 1.474 | -119.7464 | -119.8059 | -119.6732 | 121.4584 | 0.018311 | -0.11444 | 121.6919 | 121.6049 | 121.6003 | 0.14648 | 0.14191 | -0.13275 | 0 | -0.09613 | 0.37537 | 0.44861 | 0.31586 | 0.58136 | 0.44861 | 0.23346 | 0.11902 | 0.50812 | 121.7285 | 0.25177 | 121.8246 | 121.7102 | 121.6919 | -0.23346 | -121.8246 | 121.5775 | 121.5958 | 120.2362 | 119.9982
399.375 | 121.9025 | -120.3918 | 1.2955 | 0.042114 | 0.027053 | 0.017816 | -0.00038667 | 0.0021556 | -0.00040584 | -0.00015591 | 0.016754 | 0.0011493 | 0.071186 | 0.069801 | -0.00030965 | 0.016889 | 0.00021567 | 0.045776 | 1.3046 | 1.1124 | 1.2634 | 1.4053 | 1.2817 | 1.2817 | -0.086975 | 1.2634 | -120.5017 | 1.2772 | -119.9661 | -120.0165 | -119.9112 | 121.5042 | 0.009155 | -0.032043 | 121.7972 | 121.6736 | 121.6736 | 0.16937 | 0.16937 | -0.10986 | -0.032043 | -0.01831 | 0.42572 | 0.48065 | 0.37537 | 0.59052 | 0.48523 | 0.29297 | 0.15106 | 0.53558 | 121.7789 | 0.19226 | 121.7651 | 121.6965 | 121.6553 | -0.18311 | -121.7972 | 121.6553 | 121.669 | 120.4376 | 120.3049
401.0469 | 121.8475 | -120.1813 | 1.5106 | 0.011597 | 0.020858 | 0.013971 | -0.0014547 | -0.0033986 | 0.00023496 | -0.0027195 | 0.0075989 | 0.00093566 | 0.070758 | 0.064888 | -0.0045823 | 0.017103 | -0.0053385 | 0.13275 | 1.4832 | 1.2955 | 1.3824 | 1.5106 | 1.4053 | 1.4236 | -0.20142 | 1.4648 | -120.3094 | 1.4099 | -119.8334 | -119.8654 | -119.751 | 121.4767 | -0.027466 | -0.12817 | 121.6919 | 121.6049 | 121.5866 | 0.12817 | 0.10986 | -0.12817 | -0.045776 | -0.10071 | 0.3479 | 0.4303 | 0.31586 | 0.55847 | 0.44403 | 0.21515 | 0.086975 | 0.47607 | 121.7194 | 0.18768 | 121.7743 | 121.6644 | 121.6461 | -0.21515 | -121.8201 | 121.5637 | 121.5912 | 120.314 | 119.9799
402.7969 | 121.8704 | -120.4742 | 1.2085 | 0.034485 | 0.025344 | 0.017389 | 0.00046793 | -0.0012624 | -0.0012604 | -0.00036951 | 0.013702 | 0.0034991 | 0.070331 | 0.059547 | -0.0050095 | 0.017316 | -0.0014931 | 0.17395 | 1.2131 | 1.0529 | 1.1856 | 1.3092 | 1.1581 | 1.1902 | -0.14648 | 1.1673 | -120.5795 | 1.149 | -120.0943 | -120.1309 | -120.0165 | 121.5271 | 0.004578 | -0.022888 | 121.7834 | 121.6644 | 121.6324 | 0.13733 | 0.10529 | -0.10529 | -0.041199 | -0.059509 | 0.37994 | 0.45776 | 0.34332 | 0.56305 | 0.44861 | 0.25635 | 0.13275 | 0.48523 | 121.7285 | 0.16022 | 121.7468 | 121.6873 | 121.6415 | -0.15564 | -121.788 | 121.6599 | 121.6232 | 120.6482 | 120.3278
404.5312 | 121.7834 | -120.5017 | 1.2589 | 0.0039673 | 0.017868 | 0.015253 | 0.0026041 | 0.001301 | -0.0021148 | -0.0027195 | -0.0015565 | 0.0045673 | 0.067768 | 0.063393 | -0.0030869 | 0.01753 | -0.0025613 | 0.14648 | 1.236 | 0.99792 | 1.03 | 1.0895 | 0.98877 | 1.0345 | -0.22888 | 1.2039 | -120.607 | 1.0849 | -120.2087 | -120.2499 | -120.0714 | 121.4996 | -0.022888 | -0.22888 | 121.5912 | 121.5363 | 121.4905 | 0.036621 | -0.009155 | -0.10529 | -0.054932 | -0.17395 | 0.29297 | 0.4303 | 0.25177 | 0.53558 | 0.35706 | 0.091553 | 0.032043 | 0.39825 | 121.6919 | 0.23804 | 121.8109 | 121.7377 | 121.7056 | -0.26093 | -121.8658 | 121.5317 | 121.5866 | 120.6482 | 120.2728
406.2812 | 121.8567 | -120.0302 | 1.6708 | -0.0036622 | 0.0035547 | 0.014398 | 0.00068153 | 0.0038644 | -0.0021148 | 0.0013395 | 0.0045471 | 0.0034991 | 0.070331 | 0.063179 | -0.0013779 | 0.016675 | -0.0040567 | 0.11444 | 1.68 | 0.027466 | 1.5427 | 0.18768 | 0.09613 | 0.09613 | -0.21973 | 1.6571 | -120.0943 | 1.593 | -119.6548 | -119.6457 | -119.5267 | 120.0577 | 0.009156 | -0.12817 | 120.2179 | 120.1263 | 120.1263 | 0.068664 | 0.068664 | -0.064087 | -0.013733 | -0.077819 | 0.37537 | 0.50354 | 0.38452 | 0.56763 | 0.44861 | 0.16022 | 1.5152 | 0.43945 | 121.6873 | 1.6525 | 121.7514 | 121.7102 | 121.6873 | -1.6434 | -121.7651 | 121.5729 | 121.6232 | 120.1447 | 119.8105
408.0156 | 121.8155 | -120.52 | 1.2222 | 0.019226 | 0.019363 | 0.016534 | 0.0011087 | 0.00087375 | -0.0040374 | -0.0020785 | 0.0075989 | 0.0022175 | 0.068622 | 0.059547 | -0.0024461 | 0.015821 | -0.0025613 | 0.19226 | 1.1765 | 0.99792 | 1.0849 | 1.2085 | 1.0895 | 1.1032 | -0.14191 | 1.181 | -120.6253 | 1.0895 | -120.163 | -120.2271 | -120.0714 | 121.5179 | -0.045776 | -0.13733 | 121.7285 | 121.6232 | 121.6095 | 0.10529 | 0.091553 | -0.10528 | -0.041199 | -0.13275 | 0.35706 | 0.44861 | 0.29297 | 0.55389 | 0.39825 | 0.21057 | 0.086975 | 0.46234 | 121.7148 | 0.17853 | 121.8063 | 121.6965 | 121.7011 | -0.2243 | -121.8475 | 121.6049 | 121.6095 | 120.7123 | 120.3781
409.75 | 121.8292 | -120.5475 | 1.236 | 0.034485 | 0.01979 | 0.015039 | -0.00081387 | 0.0045054 | -0.0016876 | -0.0012241 | 0.019806 | 0.0032855 | 0.070545 | 0.058479 | -0.0030869 | 0.017103 | -0.0017069 | 0.1236 | 1.2543 | 0.9613 | 1.0574 | 1.1673 | 1.0941 | 1.1078 | -0.17853 | 1.2222 | -120.639 | 1.0712 | -120.1309 | -120.1904 | -120.0577 | 121.5088 | 0.01831 | -0.17853 | 121.7148 | 121.6553 | 121.6415 | 0.14648 | 0.13275 | -0.091553 | -0.013733 | -0.1648 | 0.41656 | 0.48981 | 0.35705 | 0.58136 | 0.44861 | 0.20599 | 0.09613 | 0.50812 | 121.7102 | 0.29297 | 121.8613 | 121.8018 | 121.7697 | -0.27466 | -121.875 | 121.6049 | 121.6187 | 120.6711 | 120.369
411.4219 | 121.8063 | -120.4697 | 1.3138 | 0.019226 | 0.018936 | 0.014612 | 0.00025413 | 0.00066015 | -0.0033966 | -0.0010105 | 0.0045471 | 0.0034991 | 0.069477 | 0.059761 | -0.0020187 | 0.016034 | 0.0012839 | 0.21973 | 1.2497 | 1.0712 | 1.1536 | 1.268 | 1.1581 | 1.1719 | -0.15106 | 1.2634 | -120.5612 | 1.1627 | -120.0897 | -120.1401 | -120.0027 | 121.5408 | -0.064087 | -0.16022 | 121.7377 | 121.6415 | 121.6278 | 0.10071 | 0.086975 | -0.091552 | -0.050354 | -0.15106 | 0.37994 | 0.46692 | 0.32959 | 0.55847 | 0.42114 | 0.19684 | 0.082397 | 0.4715 | 121.7239 | 0.17853 | 121.8246 | 121.7194 | 121.7331 | -0.24262 | -121.875 | 121.6232 | 121.6324 | 120.6894 | 120.3186
413.1719 | 121.7834 | -120.4742 | 1.3046 | 0.049744 | 0.01979 | 0.014185 | 4.0528e-05 | 0.0045054 | -0.0021148 | -0.0012241 | 0.013702 | 0.0028583 | 0.07204 | 0.063393 | -0.0043687 | 0.016248 | -0.00042513 | 0.19684 | 1.3275 | 1.0666 | 1.1261 | 1.2405 | 1.1902 | 1.181 | -0.19684 | 1.3092 | -120.5795 | 1.149 | -120.1172 | -120.1447 | -120.0302 | 121.5408 | 0.022889 | -0.17853 | 121.7148 | 121.6553 | 121.6644 | 0.11444 | 0.1236 | -0.10529 | 0.004578 | -0.15564 | 0.35706 | 0.44403 | 0.32959 | 0.54932 | 0.43488 | 0.17395 | 0.05951 | 0.46234 | 121.7285 | 0.26093 | 121.8887 | 121.8018 | 121.7834 | -0.23804 | -121.8842 | 121.6003 | 121.6232 | 120.6711 | 120.2774
414.9219 | 121.9025 | -120.5383 | 1.1627 | 0.0039673 | 0.015945 | 0.013116 | -0.0050863 | 0.0034372 | -0.00019224 | -0.0012241 | -0.0015565 | 0.00050846 | 0.068409 | 0.06916 | -0.0035141 | 0.016248 | -0.0021341 | 0.09613 | 1.1124 | 0.98419 | 1.1261 | 1.2909 | 1.1627 | 1.1261 | -0.086975 | 1.1078 | -120.6436 | 1.1215 | -120.1172 | -120.1355 | -120.0348 | 121.5225 | -0.050354 | -0.036621 | 121.8292 | 121.6644 | 121.701 | 0.14191 | 0.17853 | -0.10529 | -0.054932 | -0.041199 | 0.42114 | 0.50354 | 0.40283 | 0.60883 | 0.50812 | 0.3067 | 0.14191 | 0.52643 | 121.7651 | 0.12817 | 121.7514 | 121.6507 | 121.6461 | -0.17853 | -121.8063 | 121.6644 | 121.6599 | 120.6345 | 120.4514
416.6094 | 121.7514 | -120.6482 | 1.1261 | 0.0039673 | 0.018081 | 0.016107 | 0.00068153 | 0.00087375 | -0.002542 | -0.0020785 | 0.0014953 | 0.0024311 | 0.069049 | 0.056984 | -0.0013779 | 0.018384 | 0.00021567 | 0.050354 | 1.1078 | 0.88348 | 0.9201 | 0.98877 | 0.91553 | 0.9201 | -0.28381 | 1.0757 | -120.7443 | 0.94757 | -120.3598 | -120.3781 | -120.2271 | 121.5317 | -0.018311 | -0.20599 | 121.637 | 121.5683 | 121.5637 | 0.036621 | 0.032043 | -0.096131 | -0.050354 | -0.17853 | 0.28839 | 0.42114 | 0.27008 | 0.51727 | 0.36621 | 0.10529 | 0.036621 | 0.38452 | 121.6919 | 0.2243 | 121.8201 | 121.756 | 121.7239 | -0.24261 | -121.8704 | 121.5683 | 121.5958 | 120.6985 | 120.3644
418.3438 | 121.8384 | -120.5566 | 1.181 | -0.0036622 | 0.021285 | 0.013544 | -0.0042319 | -0.0042532 | -0.0021148 | 0.00027129 | 0.0075989 | -0.00034614 | 0.0667 | 0.063179 | -0.0024461 | 0.016248 | 0.0040611 | 0.082397 | 1.1398 | 0.99335 | 1.1078 | 1.2314 | 1.1307 | 1.1261 | -0.1236 | 1.1307 | -120.6024 | 1.0803 | -120.1584 | -120.1996 | -120.076 | 121.55 | -0.041198 | -0.073242 | 121.788 | 121.6827 | 121.6873 | 0.13275 | 0.13733 | -0.045776 | -0.050354 | -0.10071 | 0.39826 | 0.48065 | 0.35706 | 0.52643 | 0.40283 | 0.23804 | 0.11444 | 0.44403 | 121.6827 | 0.14648 | 121.7331 | 121.6965 | 121.6873 | -0.18768 | -121.7834 | 121.6644 | 121.637 | 120.639 | 120.433
420.0781 | 121.8155 | -120.6299 | 1.1536 | 0.0039673 | 0.019363 | 0.013116 | -0.0010275 | -0.0023306 | -0.0016876 | 5.7688e-05 | 0.0014953 | 0.0032855 | 0.068836 | 0.059547 | -0.0039413 | 0.015394 | -0.0019205 | 0.050354 | 1.1032 | 0.95215 | 1.0071 | 1.1215 | 1.0437 | 1.03 | -0.17853 | 1.0941 | -120.7031 | 0.97504 | -120.2499 | -120.2682 | -120.163 | 121.582 | -0.050354 | -0.14648 | 121.7514 | 121.6599 | 121.6736 | 0.07782 | 0.091553 | -0.073242 | -0.059509 | -0.17853 | 0.37994 | 0.46692 | 0.36163 | 0.54016 | 0.43488 | 0.16937 | 0.054932 | 0.45319 | 121.6782 | 0.15106 | 121.7972 | 121.7331 | 121.7239 | -0.20142 | -121.8567 | 121.637 | 121.6049 | 120.6802 | 120.4514
421.75 | 121.8109 | -120.4605 | 1.3092 | 0.011597 | 0.020217 | 0.014185 | -0.0012411 | -0.0016898 | -0.0016876 | 5.7688e-05 | 0.0014953 | 0.0039265 | 0.069477 | 0.062538 | 0.00011755 | 0.016462 | -0.00063873 | 0.09613 | 1.2817 | 1.0895 | 1.1719 | 1.2863 | 1.181 | 1.1719 | -0.14648 | 1.2589 | -120.5292 | 1.1948 | -120.0623 | -120.1263 | -119.9707 | 121.55 | -0.027466 | -0.13733 | 121.7468 | 121.6324 | 121.6415 | 0.082397 | 0.091552 | -0.068665 | -0.050354 | -0.11444 | 0.39825 | 0.48981 | 0.33417 | 0.55847 | 0.40283 | 0.19684 | 0.082397 | 0.46692 | 121.7239 | 0.19226 | 121.788 | 121.7422 | 121.7194 | -0.21973 | -121.8384 | 121.6324 | 121.6553 | 120.5566 | 120.314
423.4844 | 121.9025 | -120.4788 | 1.2268 | 0.0039673 | 0.018295 | 0.01568 | -0.0038047 | 0.0019418 | -0.0021148 | -0.0014377 | 0.0014953 | -0.00013254 | 0.069049 | 0.068947 | -0.0037277 | 0.01753 | 0.0027793 | 0 | 1.2085 | 1.0437 | 1.1124 | 1.236 | 1.149 | 1.1581 | -0.19226 | 1.181 | -120.575 | 1.1581 | -120.0623 | -120.1035 | -119.9844 | 121.5225 | -0.018311 | -0.11444 | 121.7148 | 121.637 | 121.6278 | 0.11444 | 0.10529 | -0.09613 | -0.045777 | -0.068665 | 0.41656 | 0.49438 | 0.37537 | 0.59051 | 0.4715 | 0.19226 | 0.068665 | 0.51269 | 121.7331 | 0.1648 | 121.756 | 121.6873 | 121.6599 | -0.18311 | -121.8018 | 121.5912 | 121.637 | 120.4788 | 120.2866
425.2188 | 121.9208 | -120.4239 | 1.2589 | 0.0039673 | 0.018722 | 0.014185 | -0.0048727 | -0.0016898 | -0.0012604 | 5.7688e-05 | 0.022858 | 0.0032855 | 0.073108 | 0.065742 | 0.00033115 | 0.016675 | -0.0023477 | 0.086975 | 1.236 | 1.1078 | 1.2543 | 1.3824 | 1.2405 | 1.2543 | -0.07782 | 1.2589 | -120.5338 | 1.2772 | -119.989 | -120.0302 | -119.9112 | 121.5317 | -0.022888 | -0.004578 | 121.8063 | 121.6782 | 121.6644 | 0.14648 | 0.13275 | -0.10986 | 0 | 0.018311 | 0.43488 | 0.5127 | 0.39368 | 0.62256 | 0.50354 | 0.27466 | 0.14648 | 0.54474 | 121.8109 | 0.12817 | 121.7926 | 121.6599 | 121.6827 | -0.15106 | -121.7926 | 121.6782 | 121.7011 | 120.5109 | 120.3461
426.8906 | 121.788 | -120.5566 | 1.2314 | -0.0036622 | 0.018722 | 0.017175 | -0.00060027 | -0.0010488 | -0.0023284 | -0.0022921 | 0.0014953 | 0.0024311 | 0.070758 | 0.061684 | -0.0045823 | 0.016248 | -0.00063873 | 0.07782 | 1.1902 | 1.0071 | 1.0574 | 1.181 | 1.0849 | 1.0986 | -0.1831 | 1.181 | -120.6024 | 1.0529 | -120.1859 | -120.2087 | -120.1035 | 121.5637 | -0.041198 | -0.17395 | 121.7377 | 121.6553 | 121.6415 | 0.091553 | 0.07782 | -0.045776 | -0.050354 | -0.17853 | 0.37079 | 0.45319 | 0.3479 | 0.49896 | 0.39368 | 0.17395 | 0.050354 | 0.41657 | 121.6553 | 0.18311 | 121.7834 | 121.7468 | 121.7377 | -0.2243 | -121.8338 | 121.6141 | 121.6095 | 120.6345 | 120.3735
428.625 | 121.8704 | -120.5933 | 1.1581 | 0.011597 | 0.014663 | 0.015253 | 0.00068153 | -0.0019034 | -0.0027556 | -0.0042147 | 0.0045471 | 0.00072206 | 0.068195 | 0.065315 | -0.0020187 | 0.01753 | -0.0019205 | -0.004578 | 1.1444 | 0.97046 | 1.0437 | 1.1581 | 1.0712 | 1.0757 | -0.19226 | 1.1215 | -120.6436 | 1.0574 | -120.1721 | -120.2087 | -120.0851 | 121.5637 | -0.013733 | -0.11444 | 121.7514 | 121.669 | 121.6644 | 0.10529 | 0.10071 | -0.050354 | -0.036621 | -0.10071 | 0.42114 | 0.50812 | 0.38452 | 0.55847 | 0.43488 | 0.18768 | 0.073242 | 0.4715 | 121.701 | 0.17395 | 121.7651 | 121.7377 | 121.7148 | -0.18768 | -121.8018 | 121.637 | 121.6507 | 120.5887 | 120.401
430.3594 | 121.7789 | -120.5658 | 1.1627 | 0.0039673 | 0.018936 | 0.013116 | 0.00068153 | 0.00301 | -0.0040374 | 0.00069849 | 0.0014953 | 0.0026447 | 0.068836 | 0.060188 | -0.0013779 | 0.019452 | -0.0046975 | 0.073242 | 1.1398 | 0.94757 | 0.97961 | 1.1032 | 0.97504 | 1.0025 | -0.19684 | 1.1398 | -120.6757 | 1.0208 | -120.2591 | -120.314 | -120.1447 | 121.5134 | -0.022888 | -0.18311 | 121.669 | 121.5683 | 121.5408 | 0.054931 | 0.027466 | -0.10986 | -0.022888 | -0.14191 | 0.3067 | 0.42114 | 0.25177 | 0.53101 | 0.36163 | 0.15564 | 0.032043 | 0.41656 | 121.6965 | 0.19226 | 121.8155 | 121.7056 | 121.7056 | -0.21515 | -121.8384 | 121.5454 | 121.5866 | 120.639 | 120.369
432.1094 | 121.7468 | -120.6299 | 1.1307 | 0.0039673 | 0.017013 | 0.016107 | -0.00081387 | 0.0021556 | -0.0023284 | -0.0020785 | 0.0014953 | 0.0024311 | 0.069263 | 0.058693 | -0.0024461 | 0.01753 | -0.0036295 | -0.11902 | 1.1169 | 0.90637 | 0.91095 | 0.99335 | 0.90637 | 0.93384 | -0.4715 | 1.0895 | -120.7306 | 0.97046 | -120.3369 | -120.3735 | -120.2087 | 121.5363 | -0.013733 | -0.21973 | 121.6232 | 121.5637 | 121.5363 | 0.027466 | 0 | -0.10071 | -0.041198 | -0.16022 | 0.29297 | 0.42114 | 0.25635 | 0.52185 | 0.35706 | 0.086975 | 0.004578 | 0.39368 | 121.7011 | 0.21057 | 121.8201 | 121.7468 | 121.7194 | -0.2243 | -121.8613 | 121.5408 | 121.6003 | 120.5109 | 120.1584
433.8438 | 121.8292 | -119.9066 | 1.8402 | 0.026856 | 0.025131 | 0.013757 | -0.00017307 | 0.0038644 | -0.0027556 | 0.0024075 | 0.0045471 | 0.0032855 | 0.070118 | 0.061897 | -0.0030869 | 0.018384 | 0.00042947 | 0.19684 | 1.8311 | 1.6113 | 1.7075 | 1.8311 | 1.712 | 1.7441 | -0.082397 | 1.8127 | -119.9844 | 1.7441 | -119.5221 | -119.5496 | -119.426 | 121.5179 | -0.009155 | -0.13275 | 121.7377 | 121.6507 | 121.6187 | 0.13275 | 0.10071 | -0.07782 | -0.027466 | -0.09613 | 0.38452 | 0.48065 | 0.35706 | 0.55847 | 0.43488 | 0.21973 | 0.09613 | 0.46234 | 121.7285 | 0.21973 | 121.7972 | 121.7377 | 121.7194 | -0.22888 | -121.8246 | 121.6141 | 121.6507 | 120.1035 | 119.8242
435.5156 | 121.8842 | -121.0007 | 0.71411 | -0.0036622 | 0.013809 | 0.013757 | -0.0020957 | -0.0025442 | -0.0036102 | -0.0035739 | 0.0045471 | 0.00029486 | 0.069477 | 0.065315 | -0.0067185 | 0.016034 | 0.0019247 | 0.059509 | 0.67291 | 0.54932 | 0.65002 | 0.78735 | 0.6958 | 0.67749 | -0.086975 | 0.66834 | -121.1014 | 0.66834 | -120.5521 | -120.5978 | -120.5017 | 121.55 | -0.041198 | -0.064087 | 121.788 | 121.6782 | 121.6965 | 0.12817 | 0.14648 | -0.10071 | -0.045776 | -0.045776 | 0.44861 | 0.49896 | 0.40283 | 0.59967 | 0.50354 | 0.23804 | 0.10071 | 0.54932 | 121.7697 | 0.1236 | 121.7697 | 121.6736 | 121.669 | -0.1648 | -121.8155 | 121.6507 | 121.669 | 121.0602 | 120.9137
437.25 | 121.8704 | -120.8084 | 0.90637 | 0.049744 | 0.015731 | 0.014825 | 0.00025413 | 0.001301 | -0.0016876 | -0.0022921 | 0.0075989 | 0.00072206 | 0.069477 | 0.065529 | -0.0018051 | 0.018384 | 0.0012839 | 0.036621 | 0.88806 | 0.70496 | 0.82855 | 0.95215 | 0.82855 | 0.85602 | -0.16479 | 0.85602 | -120.9137 | 0.84228 | -120.4422 | -120.4697 | -120.3323 | 121.5134 | -0.01831 | -0.07782 | 121.7606 | 121.6644 | 121.637 | 0.15106 | 0.1236 | -0.10528 | -0.050354 | -0.064087 | 0.36621 | 0.47608 | 0.33875 | 0.58136 | 0.44403 | 0.24719 | 0.1236 | 0.4715 | 121.756 | 0.18311 | 121.7697 | 121.6965 | 121.6644 | -0.20142 | -121.8201 | 121.637 | 121.6507 | 120.845 | 120.6436
438.9844 | 121.7972 | -121.2479 | 0.49896 | 0.011597 | 0.016586 | 0.014398 | -0.00081387 | -0.0023306 | -0.0016876 | -0.0016513 | -0.0015565 | 0.0049945 | 0.068622 | 0.062324 | -0.0022325 | 0.01753 | -0.0014931 | 0.09613 | 0.48523 | 0.28839 | 0.3479 | 0.47607 | 0.35706 | 0.38452 | -0.15564 | 0.46234 | -121.344 | 0.37994 | -120.8954 | -120.9412 | -120.7947 | 121.5363 | -0.013733 | -0.15106 | 121.7239 | 121.6324 | 121.6049 | 0.09613 | 0.068665 | -0.09613 | -0.036621 | -0.11902 | 0.35248 | 0.45319 | 0.3067 | 0.54932 | 0.40283 | 0.18768 | 0.059509 | 0.44861 | 121.7239 | 0.19684 | 121.8063 | 121.7331 | 121.7102 | -0.21057 | -121.843 | 121.5958 | 121.6278 | 121.344 | 121.0922
440.7188 | 121.9162 | -121.2067 | 0.48065 | 0.0039673 | 0.013168 | 0.01568 | -0.0023093 | 0.0010874 | 2.1362e-05 | -0.00058311 | -0.0015565 | 0.00093566 | 0.070118 | 0.064033 | 0.0011855 | 0.020948 | -0.00063873 | 0.1236 | 0.45319 | 0.33417 | 0.43945 | 0.54932 | 0.4303 | 0.4303 | -0.1236 | 0.43945 | -121.2936 | 0.49439 | -120.7901 | -120.8359 | -120.6848 | 121.5408 | -0.027466 | -0.041199 | 121.756 | 121.637 | 121.637 | 0.096131 | 0.096131 | -0.086975 | -0.041199 | 0.013733 | 0.41657 | 0.52185 | 0.37079 | 0.60883 | 0.45776 | 0.21515 | 0.10529 | 0.50354 | 121.788 | 0.11902 | 121.7331 | 121.6599 | 121.6461 | -0.14649 | -121.7743 | 121.6461 | 121.701 | 121.3303 | 121.0831
442.3906 | 121.7789 | -121.4172 | 0.36163 | 0.0039673 | 0.0121 | 0.013544 | 0.0011087 | 0.0021556 | -0.0010468 | 0.00048489 | 0.0045471 | 0.0022175 | 0.071399 | 0.05912 | -0.0028733 | 0.01753 | -0.0025613 | 0.032043 | 0.34332 | 0.14648 | 0.16022 | 0.26093 | 0.16022 | 0.19226 | -0.25635 | 0.3479 | -121.4676 | 0.20599 | -121.0693 | -121.1243 | -120.932 | 121.5637 | -0.01831 | -0.20142 | 121.6782 | 121.6095 | 121.5775 | 0.045777 | 0.013733 | -0.050354 | -0.013733 | -0.15564 | 0.3479 | 0.48523 | 0.29297 | 0.53558 | 0.34332 | 0.11444 | 0.013733 | 0.39825 | 121.6736 | 0.19684 | 121.8155 | 121.7606 | 121.7651 | -0.21515 | -121.8292 | 121.5775 | 121.6232 | 121.4493 | 121.1609
444.0781 | 121.788 | -121.4218 | 0.37537 | 0.0039673 | 0.016586 | 0.012903 | 0.0015359 | 0.00066015 | -0.00040584 | -0.0016513 | -0.0015565 | 0.00050846 | 0.067554 | 0.059547 | -0.0039413 | 0.018812 | -0.0034159 | 0.064087 | 0.35706 | 0.15106 | 0.14191 | 0.24261 | 0.16022 | 0.20142 | -0.24719 | 0.32501 | -121.5042 | 0.21057 | -121.0785 | -121.1197 | -120.9366 | 121.5729 | -0.01831 | -0.23346 | 121.6644 | 121.6232 | 121.582 | 0.050354 | 0.009155 | -0.082397 | -0.050354 | -0.16479 | 0.34332 | 0.48523 | 0.30212 | 0.56763 | 0.38452 | 0.091553 | -0.009155 | 0.42572 | 121.7148 | 0.20599 | 121.8292 | 121.7789 | 121.7468 | -0.2243 | -121.8796 | 121.5637 | 121.6324 | 121.4859 | 121.1746
445.8281 | 121.8246 | -121.1838 | 0.55847 | 0.026856 | 0.024917 | 0.013971 | -0.0020957 | 0.00066015 | -0.00061944 | 0.00091209 | 0.010651 | 0.0045673 | 0.073536 | 0.064674 | -0.0037277 | 0.018384 | -0.00042513 | 0.20142 | 0.58136 | 0.32501 | 0.41657 | 0.54474 | 0.44861 | 0.4715 | -0.16022 | 0.55847 | -121.2662 | 0.45319 | -120.7993 | -120.8405 | -120.6848 | 121.5088 | 0.022888 | -0.14191 | 121.7285 | 121.6553 | 121.6324 | 0.14648 | 0.1236 | -0.082397 | 0 | -0.10529 | 0.38452 | 0.49896 | 0.34332 | 0.58136 | 0.42572 | 0.21973 | 0.091553 | 0.46692 | 121.7194 | 0.25635 | 121.8246 | 121.7651 | 121.7422 | -0.23346 | -121.8246 | 121.6003 | 121.637 | 121.3852 | 121.0236
447.5625 | 121.6003 | -121.3989 | 0.17853 | -0.018921 | 0.062728 | 0.012476 | -0.0016685 | -0.0040396 | -0.0027556 | -0.0025057 | 0.0045471 | 0.0011493 | 0.072681 | 0.062538 | -0.0082139 | 0.015821 | 0.00064307 | -0.082397 | 0.14191 | -0.054932 | -0.054932 | 0.09613 | 0.013733 | 0.013733 | -0.24261 | 0.14191 | -121.4767 | -0.009155 | -121.0693 | -121.0922 | -120.9503 | 121.344 | -0.036621 | -0.23346 | 121.4951 | 121.4127 | 121.4127 | 0.068665 | 0.068665 | -0.07782 | -0.036621 | -0.18768 | 0.32959 | 0.44861 | 0.3067 | 0.52643 | 0.38452 | 0.15106 | 0 | 0.40741 | 121.4676 | 0.19684 | 121.6187 | 121.5408 | 121.5408 | -0.23346 | -121.6553 | 121.344 | 121.3898 | 121.3165 | 121.1563
449.2344 | 121.788 | -121.5866 | 0.16479 | 0.0039673 | 0.069992 | 0.016534 | -0.0027365 | -0.0012624 | -0.003183 | -0.0022921 | -0.0015565 | 0.0026447 | 0.065418 | 0.064674 | -0.0052231 | 0.017103 | -0.0042703 | -0.032043 | 0.1236 | -0.022888 | 0.004578 | 0.13275 | 0.050354 | 0.064087 | -0.19684 | 0.11902 | -121.6507 | 0 | -121.2067 | -121.2433 | -121.1105 | 121.5637 | -0.041199 | -0.16022 | 121.7194 | 121.6507 | 121.637 | 0.086975 | 0.073242 | -0.064087 | -0.045776 | -0.16479 | 0.37994 | 0.47607 | 0.34332 | 0.54016 | 0.40741 | 0.15564 | 0.027466 | 0.44403 | 121.6507 | 0.14648 | 121.7697 | 121.7102 | 121.7056 | -0.18768 | -121.8155 | 121.5912 | 121.5866 | 121.5546 | 121.3898
450.9844 | 121.7697 | -121.5866 | 0.16937 | -0.011291 | 0.067428 | 0.012476 | -0.00038667 | -0.001476 | -0.002542 | -0.0014377 | 0.0075989 | 0.0041401 | 0.068195 | 0.064033 | -0.0020187 | 0.016034 | -0.00021153 | -0.032043 | 0.15106 | -0.059509 | -0.032043 | 0.082397 | -0.022888 | 0.004578 | -0.25635 | 0.15564 | -121.6553 | -0.004578 | -121.2524 | -121.2936 | -121.1288 | 121.5271 | -0.018311 | -0.20142 | 121.669 | 121.5912 | 121.5637 | 0.064087 | 0.036621 | -0.068664 | -0.013733 | -0.17395 | 0.33417 | 0.45776 | 0.29297 | 0.52643 | 0.36163 | 0.14191 | 0.027466 | 0.40283 | 121.6507 | 0.21057 | 121.8109 | 121.7377 | 121.7422 | -0.22888 | -121.8246 | 121.5546 | 121.582 | 121.5546 | 121.3303
452.6719 | 121.8613 | -121.55 | 0.14648 | 0.019226 | 0.066574 | 0.013971 | -0.0012411 | 0.00066015 | -0.00061944 | -0.00079691 | 0.0075989 | 0.0011493 | 0.068622 | 0.067024 | -0.00030965 | 0.018812 | 0.0012839 | -0.018311 | 0.13275 | -0.013733 | 0.050354 | 0.15564 | 0.07782 | 0.082397 | -0.20142 | 0.13733 | -121.6278 | 0.082397 | -121.1609 | -121.2021 | -121.0556 | 121.5363 | -0.013733 | -0.09613 | 121.7056 | 121.6324 | 121.6278 | 0.09613 | 0.091553 | -0.07782 | -0.009155 | -0.064087 | 0.3891 | 0.49438 | 0.3479 | 0.5722 | 0.42572 | 0.16937 | 0.064087 | 0.46692 | 121.7102 | 0.14648 | 121.7651 | 121.6827 | 121.6873 | -0.16022 | -121.7743 | 121.6003 | 121.6324 | 121.5317 | 121.3486
454.4062 | 121.7972 | -121.5866 | 0.1831 | 0.011597 | 0.069992 | 0.015894 | -0.0012411 | 0.0042918 | -0.002542 | -0.0014377 | 0.0045471 | 0.0032855 | 0.071186 | 0.06617 | -0.00073705 | 0.01753 | 0.0014975 | 0.013733 | 0.14648 | -0.036621 | 0.022888 | 0.15106 | 0.045776 | 0.050354 | -0.14191 | 0.13733 | -121.6324 | 0.059509 | -121.2067 | -121.257 | -121.0876 | 121.55 | -0.036621 | -0.16022 | 121.7377 | 121.637 | 121.6324 | 0.086975 | 0.082397 | -0.045776 | -0.045776 | -0.1236 | 0.37994 | 0.49896 | 0.32959 | 0.54474 | 0.37537 | 0.18768 | 0.059509 | 0.42572 | 121.6919 | 0.18311 | 121.7697 | 121.7331 | 121.7239 | -0.21973 | -121.8155 | 121.6095 | 121.6461 | 121.6003 | 121.4447
456.1562 | 121.7606 | -121.5866 | 0.19226 | 0.0039673 | 0.067001 | 0.011835 | 4.0528e-05 | 0.0015146 | -0.0010468 | -0.0020785 | -0.0015565 | 0.0032855 | 0.070331 | 0.060188 | -0.00073705 | 0.017103 | -0.0051247 | -0.045776 | 0.15106 | -0.041199 | -0.064087 | 0.050354 | -0.041199 | -0.022888 | -0.25635 | 0.15106 | -121.6553 | 0.018311 | -121.2753 | -121.2936 | -121.1105 | 121.5454 | -0.041199 | -0.25635 | 121.637 | 121.5637 | 121.5454 | 0.018311 | 0 | -0.068664 | -0.041199 | -0.17395 | 0.31128 | 0.47607 | 0.29297 | 0.54474 | 0.36163 | 0.091553 | -0.022888 | 0.37994 | 121.6736 | 0.19226 | 121.8063 | 121.7377 | 121.7377 | -0.23346 | -121.8475 | 121.5225 | 121.6049 | 121.5408 | 121.3303
457.9062 | 121.8338 | -121.5729 | 0.16479 | 0.0039673 | 0.071487 | 0.014185 | 0.00089513 | 0.00301 | -0.00083304 | -0.00036951 | 0.0045471 | 0.0015765 | 0.069263 | 0.055702 | -0.0047959 | 0.016889 | -0.0014931 | 0.022888 | 0.16479 | -0.050354 | 0.022888 | 0.1831 | 0.07782 | 0.07782 | -0.10986 | 0.15106 | -121.637 | 0.073242 | -121.1792 | -121.2204 | -121.0602 | 121.5225 | 0 | -0.14191 | 121.756 | 121.6507 | 121.6507 | 0.12817 | 0.12817 | -0.064087 | -0.013733 | -0.091553 | 0.39368 | 0.51269 | 0.35248 | 0.57678 | 0.41656 | 0.23346 | 0.073242 | 0.45776 | 121.7102 | 0.21515 | 121.788 | 121.7377 | 121.7239 | -0.21515 | -121.8018 | 121.5958 | 121.6461 | 121.5958 | 121.463
459.5938 | 121.7789 | -121.5866 | 0.17395 | 0.0039673 | 0.066787 | 0.015039 | 0.00025413 | 0.0019418 | 0.00066216 | 0.00091209 | -0.0015565 | 0.0030719 | 0.06969 | 0.062965 | -0.0018051 | 0.01753 | -0.00042513 | -0.022888 | 0.15564 | -0.027466 | -0.022888 | 0.091553 | -0.004578 | 0.009155 | -0.21973 | 0.13733 | -121.6553 | 0.004578 | -121.2387 | -121.3028 | -121.1288 | 121.5591 | -0.01831 | -0.19684 | 121.6782 | 121.5958 | 121.582 | 0.036621 | 0.022888 | -0.068664 | -0.036621 | -0.16937 | 0.3479 | 0.45776 | 0.28381 | 0.52643 | 0.35248 | 0.11902 | 0.004578 | 0.41656 | 121.6599 | 0.18311 | 121.7926 | 121.7422 | 121.7239 | -0.20142 | -121.8292 | 121.5637 | 121.5912 | 121.5637 | 121.3669
461.3438 | 121.843 | -121.5729 | 0.16479 | -0.0036622 | 0.066574 | 0.014825 | -0.00060027 | -0.00083525 | -0.0010468 | -0.0018649 | -0.0015565 | 0.0020039 | 0.070331 | 0.062752 | -0.00073705 | 0.021802 | -0.00021153 | -0.059509 | 0.13733 | -0.050354 | -0.036621 | 0.09613 | -0.022888 | 0.018311 | -0.21515 | 0.11902 | -121.6415 | 0.064087 | -121.1929 | -121.2433 | -121.0693 | 121.5225 | -0.027466 | -0.20142 | 121.669 | 121.5912 | 121.55 | 0.068665 | 0.027466 | -0.068665 | -0.045776 | -0.10071 | 0.37994 | 0.50354 | 0.32959 | 0.5722 | 0.39826 | 0.14648 | 0.013733 | 0.44861 | 121.7056 | 0.18768 | 121.7606 | 121.7102 | 121.6919 | -0.21515 | -121.8063 | 121.5363 | 121.637 | 121.5134 | 121.3577
463.0156 | 121.9116 | -121.5408 | 0.13733 | -0.011291 | 0.069137 | 0.015894 | 0.0017495 | 0.0038644 | -0.0012604 | 0.0019803 | 0.013702 | 0.0020039 | 0.071827 | 0.070869 | 0.0016129 | 0.018812 | -0.0036295 | 0.050354 | 0.14191 | -0.022888 | 0.12817 | 0.26093 | 0.13733 | 0.14191 | -0.07782 | 0.1236 | -121.6507 | 0.15106 | -121.1105 | -121.1655 | -121.019 | 121.5179 | 0.004578 | -0.009155 | 121.8018 | 121.6827 | 121.6782 | 0.16479 | 0.16022 | -0.10986 | -0.013733 | 0.013733 | 0.4303 | 0.52185 | 0.37537 | 0.63171 | 0.48523 | 0.28381 | 0.15106 | 0.54016 | 121.8018 | 0.16479 | 121.7743 | 121.6827 | 121.6644 | -0.16022 | -121.788 | 121.669 | 121.6919 | 121.5912 | 121.463
464.75 | 121.7743 | -121.5729 | 0.18768 | 0.0039673 | 0.06871 | 0.014185 | -0.0020957 | 0.0015146 | -0.001474 | -0.0040011 | -0.0015565 | 0.0026447 | 0.069904 | 0.065102 | -0.0013779 | 0.017316 | 2.068e-06 | -0.027466 | 0.12817 | -0.045776 | -0.022888 | 0.11902 | 0.004578 | 0.009155 | -0.19684 | 0.13733 | -121.637 | 0.013733 | -121.2433 | -121.3074 | -121.1243 | 121.5271 | -0.059509 | -0.21057 | 121.6919 | 121.582 | 121.5775 | 0.054931 | 0.050354 | -0.064087 | -0.050354 | -0.17395 | 0.32959 | 0.44861 | 0.2655 | 0.51269 | 0.32959 | 0.16479 | 0.022888 | 0.39368 | 121.6507 | 0.17395 | 121.7743 | 121.701 | 121.7102 | -0.23346 | -121.8246 | 121.55 | 121.5866 | 121.5454 | 121.376
466.4844 | 121.8521 | -121.6187 | 0.16022 | -0.011291 | 0.042434 | 0.012689 | -0.019185 | -0.0016898 | -0.002542 | -0.00036951 | 0.0014953 | 0.0026447 | 0.071186 | 0.062965 | -0.00073705 | 0.020307 | -0.00085233 | -0.022888 | 0.14648 | -0.045776 | 0.027466 | 0.16479 | 0.041199 | 0.082397 | -0.15106 | 0.082397 | -121.6324 | 0.11444 | -121.1426 | -121.1792 | -121.0144 | 121.5729 | -0.013733 | -0.13275 | 121.7834 | 121.701 | 121.6599 | 0.12817 | 0.086975 | -0.013733 | -0.07782 | -0.045776 | 0.47607 | 0.60425 | 0.43945 | 0.61798 | 0.45319 | 0.21057 | 0.073242 | 0.48981 | 121.7468 | 0.19226 | 121.7148 | 121.7651 | 121.701 | -0.20599 | -121.7926 | 121.6461 | 121.7331 | 121.5958 | 121.4676
468.1719 | 121.875 | -121.5637 | 0.13275 | -0.0036622 | 0.042007 | 0.012476 | -0.017263 | -0.002117 | -0.001474 | -0.0010105 | 0.0014953 | 0.00029486 | 0.068195 | 0.064247 | 0.00033115 | 0.017103 | 0.00064307 | 0.022888 | 0.1236 | -0.027466 | 0.059509 | 0.18768 | 0.082397 | 0.09613 | -0.12817 | 0.082397 | -121.6232 | 0.12817 | -121.1243 | -121.17 | -121.019 | 121.5363 | -0.009155 | -0.073242 | 121.7514 | 121.6599 | 121.6461 | 0.1236 | 0.10986 | -0.059509 | -0.050354 | -0.004577 | 0.43945 | 0.54474 | 0.39368 | 0.60425 | 0.45319 | 0.21515 | 0.086975 | 0.49896 | 121.7514 | 0.15106 | 121.7056 | 121.6873 | 121.6461 | -0.16022 | -121.756 | 121.6232 | 121.6919 | 121.5866 | 121.4355
469.8906 | 121.8658 | -121.5683 | 0.15106 | -0.0036622 | 0.042861 | 0.013971 | -0.018331 | -0.0012624 | -0.0023284 | -0.0018649 | -0.0015565 | 0.00093566 | 0.069263 | 0.060402 | -0.0073593 | 0.016248 | -0.0042703 | 0.022888 | 0.10071 | -0.022888 | 0.073242 | 0.23804 | 0.1236 | 0.13275 | -0.10071 | 0.10986 | -121.6278 | 0.082397 | -121.1426 | -121.1792 | -121.051 | 121.5454 | -0.050354 | -0.07782 | 121.8063 | 121.701 | 121.6919 | 0.15564 | 0.14648 | -0.05951 | -0.041199 | -0.068665 | 0.42572 | 0.51727 | 0.3891 | 0.57678 | 0.44861 | 0.26093 | 0.09613 | 0.48523 | 121.7102 | 0.1236 | 121.7377 | 121.669 | 121.6782 | -0.17395 | -121.7789 | 121.6415 | 121.6507 | 121.5912 | 121.4676
471.5781 | 121.7606 | -121.6095 | 0.16937 | -0.0036622 | 0.044998 | 0.012903 | -0.01534 | 0.00301 | -0.0016876 | -0.0020785 | -0.0046081 | 0.0047809 | 0.070972 | 0.055702 | -0.0015915 | 0.018171 | -0.0025613 | -0.045776 | 0.13733 | -0.041199 | -0.036621 | 0.07782 | -0.032043 | -0.004578 | -0.23804 | 0.13275 | -121.6553 | -0.009155 | -121.2845 | -121.3165 | -121.1334 | 121.5683 | -0.032044 | -0.20599 | 121.6873 | 121.6049 | 121.5775 | 0.036621 | 0.009156 | -0.045776 | -0.036622 | -0.17853 | 0.32501 | 0.47607 | 0.29297 | 0.52185 | 0.33874 | 0.11902 | 0.004578 | 0.37079 | 121.6461 | 0.17853 | 121.788 | 121.7468 | 121.7422 | -0.21057 | -121.8246 | 121.5729 | 121.6003 | 121.5637 | 121.3715
473.25 | 121.8018 | -121.6049 | 0.17395 | 0.019226 | 0.044357 | 0.015253 | -0.017049 | 0.0017282 | -0.0033966 | -0.0010105 | 0.0014953 | 0.0034991 | 0.070118 | 0.05912 | -0.0047959 | 0.017743 | -0.00085233 | -0.013733 | 0.13733 | -0.032043 | 0.009155 | 0.15106 | 0.027466 | 0.032043 | -0.14191 | 0.11444 | -121.6599 | 0.045776 | -121.2387 | -121.2936 | -121.1151 | 121.5729 | -0.036621 | -0.16479 | 121.756 | 121.637 | 121.6324 | 0.064086 | 0.059509 | -0.054932 | -0.059509 | -0.12817 | 0.36621 | 0.48981 | 0.31128 | 0.54474 | 0.36621 | 0.18311 | 0.041198 | 0.42114 | 121.7056 | 0.16937 | 121.7743 | 121.7422 | 121.7194 | -0.20599 | -121.8338 | 121.6141 | 121.6507 | 121.5912 | 121.463
474.9844 | 121.8521 | -121.5729 | 0.15106 | 0.019226 | 0.042221 | 0.014612 | -0.018545 | 0.0017282 | 0.0015168 | -0.0022921 | 0.0014953 | -0.00013254 | 0.071399 | 0.068306 | -0.00073705 | 0.017957 | 0.0021383 | -0.022888 | 0.11444 | -0.050354 | 0.018311 | 0.19226 | 0.050354 | 0.054932 | -0.20142 | 0.10071 | -121.6919 | 0.054932 | -121.2021 | -121.225 | -121.0739 | 121.5225 | -0.036621 | -0.13275 | 121.7651 | 121.6278 | 121.6232 | 0.10529 | 0.10071 | -0.11902 | -0.050354 | -0.09613 | 0.37079 | 0.49896 | 0.3479 | 0.61798 | 0.46692 | 0.24261 | 0.068665 | 0.48981 | 121.7468 | 0.16479 | 121.7926 | 121.6873 | 121.6736 | -0.20142 | -121.843 | 121.5912 | 121.6278 | 121.55 | 121.3715
476.6562 | 121.8567 | -121.5775 | 0.16937 | 0.0039673 | 0.041152 | 0.013971 | -0.018545 | 0.0015146 | -0.002542 | -0.00079691 | -0.0015565 | 0.00050846 | 0.068409 | 0.063393 | -0.0067185 | 0.018384 | 0.0025657 | 0.009155 | 0.10986 | -0.032043 | 0.082397 | 0.21973 | 0.11444 | 0.09613 | -0.09613 | 0.10986 | -121.6599 | 0.068665 | -121.17 | -121.1929 | -121.0693 | 121.5454 | -0.05951 | -0.086976 | 121.7972 | 121.6736 | 121.6919 | 0.12817 | 0.14648 | -0.082397 | -0.05951 | -0.10071 | 0.40741 | 0.50812 | 0.38452 | 0.59051 | 0.46692 | 0.25177 | 0.11444 | 0.48981 | 121.7285 | 0.14191 | 121.7697 | 121.6873 | 121.6873 | -0.20142 | -121.8292 | 121.6599 | 121.6461 | 121.5866 | 121.4813
478.3906 | 121.7972 | -121.6003 | 0.1831 | 0.057373 | 0.043502 | 0.013544 | -0.016195 | 0.0032236 | -0.0010468 | -0.0012241 | 0.016754 | 0.0028583 | 0.070118 | 0.058693 | -0.0060777 | 0.017103 | -0.00063873 | -0.022888 | 0.17395 | -0.1236 | -0.027466 | 0.10071 | -0.004578 | 0.022888 | -0.20142 | 0.16022 | -121.7377 | -0.013733 | -121.2753 | -121.2845 | -121.138 | 121.4767 | -0.009155 | -0.21057 | 121.701 | 121.6232 | 121.5958 | 0.14648 | 0.11902 | -0.13733 | -0.022888 | -0.19684 | 0.32501 | 0.46234 | 0.31586 | 0.59967 | 0.45319 | 0.2243 | 0.09613 | 0.46234 | 121.7239 | 0.29755 | 121.8979 | 121.7743 | 121.7606 | -0.3067 | -121.9208 | 121.5729 | 121.5866 | 121.5775 | 121.3989
480.125 | 121.8201 | -121.6095 | 0.17853 | -0.0036622 | 0.042861 | 0.013544 | -0.018117 | -0.0010488 | -0.00083304 | -0.0010105 | -0.0015565 | 0.00093566 | 0.068836 | 0.062538 | -0.0047959 | 0.018812 | 0.0010703 | -0.009155 | 0.13275 | -0.045776 | 0.022888 | 0.16937 | 0.032043 | 0.054932 | -0.17853 | 0.11902 | -121.6644 | 0.004578 | -121.2433 | -121.2753 | -121.138 | 121.5637 | -0.045777 | -0.15564 | 121.7789 | 121.6644 | 121.6415 | 0.10071 | 0.077819 | -0.054932 | -0.059509 | -0.17395 | 0.36621 | 0.4715 | 0.33417 | 0.52643 | 0.3891 | 0.21515 | 0.068664 | 0.42114 | 121.669 | 0.17853 | 121.7834 | 121.7422 | 121.7285 | -0.2243 | -121.843 | 121.6324 | 121.6141 | 121.6003 | 121.431
481.875 | 121.7926 | -121.6095 | 0.16937 | -0.0036622 | 0.044143 | 0.01333 | -0.016836 | 0.0017282 | -0.00083304 | 0.0013395 | -0.0046081 | 0.0017901 | 0.07204 | 0.056557 | -0.0011643 | 0.017743 | -0.00063873 | -0.045776 | 0.14648 | -0.086975 | -0.054932 | 0.054932 | -0.068665 | -0.041199 | -0.2655 | 0.1236 | -121.7056 | -0.004578 | -121.2982 | -121.3257 | -121.138 | 121.5225 | -0.022889 | -0.22431 | 121.6644 | 121.5683 | 121.5408 | 0.045776 | 0.01831 | -0.09613 | -0.045777 | -0.17395 | 0.31128 | 0.4715 | 0.28381 | 0.56763 | 0.37994 | 0.14191 | 0.032043 | 0.40741 | 121.701 | 0.23346 | 121.8292 | 121.756 | 121.7331 | -0.25635 | -121.875 | 121.5546 | 121.6049 | 121.5637 | 121.344
483.5625 | 121.9299 | -121.5546 | 0.14648 | 0.0039673 | 0.043502 | 0.013757 | -0.015767 | 0.00044655 | 0.00066216 | 5.7688e-05 | -0.0046081 | -0.00013254 | 0.070331 | 0.06617 | -0.00052345 | 0.019452 | 0.00021567 | 0.036621 | 0.11444 | -0.036621 | 0.068665 | 0.21515 | 0.073242 | 0.068665 | -0.12817 | 0.07782 | -121.6461 | 0.14191 | -121.1563 | -121.1838 | -121.0281 | 121.5179 | -0.032043 | -0.077819 | 121.7697 | 121.6232 | 121.6278 | 0.10529 | 0.10986 | -0.091553 | -0.068664 | -0.004577 | 0.39825 | 0.52643 | 0.37079 | 0.61798 | 0.46234 | 0.25177 | 0.10529 | 0.48981 | 121.788 | 0.15106 | 121.7239 | 121.669 | 121.6324 | -0.18311 | -121.7926 | 121.6232 | 121.6965 | 121.5912 | 121.4264
485.2969 | 121.843 | -121.6003 | 0.16479 | 0.034485 | 0.041366 | 0.016321 | -0.015981 | 0.00087375 | -0.0029694 | 0.00048489 | 0.016754 | 0.0041401 | 0.071613 | 0.058052 | -0.0043687 | 0.016675 | -0.0019205 | -0.032043 | 0.16022 | -0.10529 | -0.013733 | 0.10529 | 0.022888 | 0 | -0.1831 | 0.16937 | -121.7239 | 0.013733 | -121.2341 | -121.2799 | -121.1105 | 121.4951 | -0.004578 | -0.17853 | 121.7056 | 121.6003 | 121.6232 | 0.10529 | 0.12817 | -0.1236 | 0.004578 | -0.15106 | 0.36621 | 0.48981 | 0.32044 | 0.6134 | 0.44403 | 0.21057 | 0.091553 | 0.48981 | 121.7377 | 0.2655 | 121.8933 | 121.7606 | 121.7697 | -0.27008 | -121.8887 | 121.5866 | 121.6141 | 121.5683 | 121.4172
487.0312 | 121.8018 | -121.6187 | 0.15564 | 0.0039673 | 0.04393 | 0.01568 | -0.015127 | -0.0012624 | -0.00040584 | -0.0037875 | -0.0015565 | 0.0043537 | 0.069477 | 0.054207 | -0.00030965 | 0.017316 | -0.0012795 | -0.054932 | 0.15106 | -0.073242 | -0.054932 | 0.064087 | -0.059509 | -0.036621 | -0.27466 | 0.13275 | -121.6782 | 0.004578 | -121.3028 | -121.344 | -121.1288 | 121.5454 | -0.004578 | -0.21057 | 121.6827 | 121.582 | 121.5591 | 0.036621 | 0.013733 | -0.05951 | -0.022889 | -0.15106 | 0.31586 | 0.48981 | 0.27466 | 0.54932 | 0.33417 | 0.13733 | 0.01831 | 0.37537 | 121.6827 | 0.2243 | 121.8109 | 121.7697 | 121.7514 | -0.22888 | -121.8338 | 121.5637 | 121.6232 | 121.5637 | 121.344
488.7031 | 121.9254 | -121.5683 | 0.14191 | -0.0036622 | 0.042007 | 0.014398 | -0.016622 | 0.00301 | -0.00061944 | 0.00048489 | -0.0015565 | 0.0030719 | 0.070972 | 0.059975 | -0.0015915 | 0.020734 | -0.0019205 | -0.013733 | 0.1236 | -0.050354 | 0.036621 | 0.16022 | 0.032043 | 0.054932 | -0.14191 | 0.10071 | -121.669 | 0.1236 | -121.17 | -121.2112 | -121.0327 | 121.5179 | -0.018311 | -0.10529 | 121.7285 | 121.6232 | 121.6003 | 0.10529 | 0.082397 | -0.10071 | -0.041199 | -0.018311 | 0.39825 | 0.53558 | 0.35706 | 0.63629 | 0.45776 | 0.21057 | 0.086975 | 0.49896 | 121.7926 | 0.17395 | 121.7697 | 121.6919 | 121.669 | -0.19226 | -121.8109 | 121.6049 | 121.6919 | 121.5546 | 121.4264
490.4375 | 121.9299 | -121.582 | 0.15564 | -0.0036622 | 0.043289 | 0.016321 | -0.015981 | 0.0025828 | 2.1362e-05 | -0.0027195 | 0.013702 | 0.0037127 | 0.070972 | 0.065315 | -0.0011643 | 0.018812 | 0.0021383 | 0.064087 | 0.11902 | -0.073242 | 0.11902 | 0.2655 | 0.10071 | 0.10986 | -0.09613 | 0.1236 | -121.6827 | 0.13733 | -121.1609 | -121.1975 | -121.0373 | 121.5088 | -0.036621 | -0.036621 | 121.8475 | 121.6919 | 121.6827 | 0.18311 | 0.17395 | -0.10071 | -0.032044 | -0.018311 | 0.42114 | 0.54474 | 0.38452 | 0.64545 | 0.48523 | 0.33874 | 0.19226 | 0.52185 | 121.8201 | 0.19226 | 121.8063 | 121.701 | 121.7056 | -0.22888 | -121.8384 | 121.701 | 121.7194 | 121.6461 | 121.4859
492.1094 | 121.8063 | -121.6187 | 0.20142 | -0.0036622 | 0.040939 | 0.013971 | -0.017476 | 0.00044655 | -0.0012604 | 0.0013395 | -0.0015565 | 0.0011493 | 0.073536 | 0.063179 | -0.0060777 | 0.018812 | -0.0012795 | 0 | 0.13275 | -0.064087 | 0.032043 | 0.17395 | 0.059509 | 0.041199 | -0.1831 | 0.13275 | -121.6782 | 0 | -121.2296 | -121.2753 | -121.1472 | 121.5546 | -0.068665 | -0.16937 | 121.7926 | 121.6599 | 121.6782 | 0.10529 | 0.1236 | -0.05951 | -0.068665 | -0.20142 | 0.3891 | 0.4715 | 0.34332 | 0.53101 | 0.40283 | 0.23804 | 0.09613 | 0.44861 | 121.6782 | 0.19684 | 121.8109 | 121.7514 | 121.7514 | -0.2655 | -121.8796 | 121.6507 | 121.6187 | 121.6187 | 121.4355
493.8438 | 121.8292 | -121.6187 | 0.16937 | 0.011597 | 0.043289 | 0.013116 | -0.017049 | 0.0025828 | -0.0016876 | -0.0020785 | 0.0045471 | 0.0037127 | 0.071399 | 0.061256 | -0.0024461 | 0.018384 | -0.00021153 | -0.032043 | 0.14648 | -0.050354 | -0.045776 | 0.073242 | -0.041199 | -0.032043 | -0.24719 | 0.14191 | -121.701 | 0.018311 | -121.2936 | -121.3165 | -121.1151 | 121.5683 | -0.022889 | -0.21515 | 121.6919 | 121.5866 | 121.5775 | 0.018311 | 0.009155 | -0.082398 | -0.027466 | -0.15106 | 0.32501 | 0.50354 | 0.30212 | 0.58594 | 0.38452 | 0.1236 | 0.004578 | 0.40741 | 121.7194 | 0.19684 | 121.843 | 121.7651 | 121.7606 | -0.21973 | -121.8704 | 121.5729 | 121.637 | 121.5866 | 121.3715
495.5938 | 121.8384 | -121.6324 | 0.15106 | 0.042114 | 0.041793 | 0.013971 | -0.014486 | 0.0040782 | -0.0021148 | 0.0015531 | 0.013702 | 0.0039265 | 0.070972 | 0.062538 | -0.0054367 | 0.015607 | 0.0012839 | -0.041199 | 0.17853 | -0.10529 | -0.009155 | 0.10071 | -0.004578 | 0.018311 | -0.20142 | 0.15106 | -121.7194 | 0.004578 | -121.2662 | -121.3028 | -121.1288 | 121.5271 | 0.027466 | -0.16022 | 121.7331 | 121.6507 | 121.6278 | 0.1236 | 0.10071 | -0.086975 | 0 | -0.14648 | 0.36621 | 0.50354 | 0.32959 | 0.59051 | 0.41656 | 0.20599 | 0.096131 | 0.45319 | 121.7239 | 0.28381 | 121.8704 | 121.8109 | 121.7834 | -0.25635 | -121.8704 | 121.6232 | 121.637 | 121.5912 | 121.431
497.2812 | 121.9391 | -121.582 | 0.14648 | -0.011291 | 0.04457 | 0.012689 | -0.016622 | 0.00044655 | -0.0023284 | 5.7688e-05 | -0.0015565 | 0.0020039 | 0.069049 | 0.064888 | -0.00052345 | 0.019239 | -0.0019205 | 0.027466 | 0.11444 | -0.036621 | 0.07782 | 0.21057 | 0.07782 | 0.073242 | -0.12817 | 0.073242 | -121.6599 | 0.14648 | -121.1609 | -121.1975 | -121.0281 | 121.5454 | -0.032043 | -0.068664 | 121.7926 | 121.6553 | 121.6599 | 0.10986 | 0.11444 | -0.07782 | -0.073242 | 0 | 0.42114 | 0.55389 | 0.38452 | 0.63171 | 0.46234 | 0.24719 | 0.11444 | 0.49896 | 121.8063 | 0.15106 | 121.7331 | 121.6965 | 121.6553 | -0.18311 | -121.8063 | 121.6599 | 121.7285 | 121.6095 | 121.4539
499.0156 | 121.8201 | -121.6049 | 0.17395 | 0.0039673 | 0.042861 | 0.014825 | -0.017049 | 0.0027964 | -0.0012604 | -0.00079691 | -0.0015565 | 0.0032855 | 0.068195 | 0.057411 | -0.0011643 | 0.019666 | -0.00063873 | -0.059509 | 0.15106 | -0.073242 | -0.059509 | 0.050354 | -0.059509 | -0.032043 | -0.25635 | 0.14648 | -121.7056 | 0.004578 | -121.3028 | -121.3348 | -121.1288 | 121.5317 | -0.022888 | -0.23346 | 121.6553 | 121.5729 | 121.5454 | 0.041199 | 0.013733 | -0.10071 | -0.027466 | -0.16937 | 0.30212 | 0.47607 | 0.27008 | 0.57678 | 0.37079 | 0.1236 | 0.013733 | 0.40283 | 121.7102 | 0.2243 | 121.8521 | 121.756 | 121.7514 | -0.24719 | -121.8796 | 121.5454 | 121.6095 | 121.5454 | 121.3486
500.7656 | 121.9437 | -121.582 | 0.13733 | 0.042114 | 0.044143 | 0.015253 | -0.017263 | 0.00087375 | -0.0016876 | -0.00015591 | 0.010651 | 0.0024311 | 0.071186 | 0.067451 | 0.00054475 | 0.019452 | 0.00042947 | 0.041199 | 0.1236 | -0.059509 | 0.14191 | 0.27008 | 0.10986 | 0.11902 | -0.11444 | 0.11444 | -121.6965 | 0.11902 | -121.1655 | -121.1975 | -121.0419 | 121.5225 | -0.013733 | 0.004578 | 121.8521 | 121.701 | 121.6919 | 0.17853 | 0.16937 | -0.11444 | -0.022888 | -0.01831 | 0.41657 | 0.54016 | 0.38452 | 0.6546 | 0.49896 | 0.32959 | 0.20142 | 0.53101 | 121.8155 | 0.1831 | 121.8109 | 121.7056 | 121.6965 | -0.19684 | -121.8338 | 121.7239 | 121.701 | 121.6232 | 121.4676
502.4531 | 121.9391 | -121.5683 | 0.14191 | 0.0039673 | 0.040512 | 0.014398 | -0.018545 | 0.0015146 | -0.0023284 | 0.0015531 | -0.0076599 | 0.00093566 | 0.069477 | 0.062538 | -0.0058639 | 0.018171 | -0.0017069 | 0.022888 | 0.10529 | -0.027466 | 0.09613 | 0.27008 | 0.1236 | 0.10986 | -0.07782 | 0.10071 | -121.6644 | 0.11902 | -121.1334 | -121.1609 | -121.0419 | 121.5408 | -0.036621 | -0.045777 | 121.8384 | 121.6782 | 121.6919 | 0.13733 | 0.15106 | -0.096131 | -0.041199 | -0.022888 | 0.43488 | 0.52643 | 0.40741 | 0.62256 | 0.50354 | 0.29755 | 0.1236 | 0.53101 | 121.7834 | 0.13275 | 121.7651 | 121.6736 | 121.669 | -0.16937 | -121.8063 | 121.6644 | 121.6873 | 121.5912 | 121.4905
504.1875 | 121.8658 | -121.5912 | 0.16022 | 0.0039673 | 0.043075 | 0.014185 | -0.015767 | -0.0016898 | -0.0023284 | -0.0027195 | -0.0015565 | 0.0017901 | 0.068836 | 0.057411 | -0.0024461 | 0.019452 | 0.0023521 | -0.041199 | 0.15564 | -0.059509 | -0.041199 | 0.07782 | -0.045776 | -0.027466 | -0.23804 | 0.13275 | -121.7102 | 0.036621 | -121.2662 | -121.3074 | -121.1105 | 121.5317 | -0.004577 | -0.20142 | 121.669 | 121.5637 | 121.5454 | 0.032043 | 0.013733 | -0.11902 | -0.027466 | -0.1236 | 0.32501 | 0.48065 | 0.28381 | 0.59967 | 0.40283 | 0.13733 | 0.01831 | 0.44403 | 121.7468 | 0.21515 | 121.843 | 121.7468 | 121.7239 | -0.21973 | -121.8704 | 121.55 | 121.6278 | 121.55 | 121.3531
505.9375 | 121.8658 | -121.582 | 0.15564 | 0.019226 | 0.042861 | 0.013757 | -0.014913 | 0.00044655 | -0.0023284 | 5.7688e-05 | 0.0014953 | 0.0034991 | 0.067554 | 0.058693 | -0.0035141 | 0.017743 | -0.0023477 | 0.004578 | 0.16022 | -0.086975 | 0.022888 | 0.16479 | 0.032043 | 0.036621 | -0.1236 | 0.1236 | -121.6873 | 0.059509 | -121.225 | -121.2845 | -121.0968 | 121.4951 | 0.004577 | -0.13275 | 121.7468 | 121.6187 | 121.6141 | 0.1236 | 0.11902 | -0.10529 | -0.032044 | -0.096131 | 0.35706 | 0.48523 | 0.29755 | 0.59051 | 0.40283 | 0.25177 | 0.10986 | 0.46234 | 121.7468 | 0.24719 | 121.8109 | 121.7422 | 121.7056 | -0.24261 | -121.843 | 121.6049 | 121.6415 | 121.5866 | 121.4584
507.6094 | 121.9666 | -121.5729 | 0.14191 | -0.011291 | 0.040939 | 0.01333 | -0.018758 | -0.0036124 | -0.0016876 | -0.0042147 | -0.0046081 | 8.1264e-05 | 0.066059 | 0.064247 | -0.0050095 | 0.018384 | -0.00042513 | 0.013733 | 0.11444 | -0.045776 | 0.082397 | 0.25635 | 0.10529 | 0.11444 | -0.073242 | 0.10529 | -121.6507 | 0.13275 | -121.1334 | -121.1517 | -121.0419 | 121.5271 | -0.027466 | -0.05951 | 121.8292 | 121.6873 | 121.6782 | 0.16022 | 0.15106 | -0.07782 | -0.036621 | -0.009156 | 0.43945 | 0.53101 | 0.42114 | 0.60883 | 0.49896 | 0.30212 | 0.12817 | 0.51727 | 121.7834 | 0.16022 | 121.756 | 121.6873 | 121.6782 | -0.18768 | -121.7926 | 121.6553 | 121.7056 | 121.5866 | 121.4996
509.3438 | 121.9299 | -121.5958 | 0.12817 | 0.049744 | 0.045639 | 0.016107 | -0.014058 | 0.0027964 | 2.1362e-05 | -0.00015591 | 0.016754 | 0.0030719 | 0.071186 | 0.073219 | 0.00054475 | 0.01753 | -0.0038431 | 0.045776 | 0.12817 | -0.054932 | 0.11902 | 0.25177 | 0.091553 | 0.11444 | -0.10071 | 0.10529 | -121.6965 | 0.10986 | -121.1746 | -121.2204 | -121.0419 | 121.5408 | 0 | -0.009155 | 121.8475 | 121.7102 | 121.6873 | 0.16937 | 0.14649 | -0.10071 | -0.022888 | -0.018311 | 0.42114 | 0.55389 | 0.37537 | 0.6546 | 0.47607 | 0.3067 | 0.17395 | 0.52185 | 121.8063 | 0.18311 | 121.8018 | 121.7239 | 121.7011 | -0.18311 | -121.8246 | 121.7148 | 121.7056 | 121.6415 | 121.4951
511.0781 | 121.9162 | -121.6095 | 0.16479 | 0.042114 | 0.044998 | 0.015039 | -0.017263 | 0.0036508 | -0.00040584 | -0.0027195 | 0.0045471 | 0.0017901 | 0.071186 | 0.067238 | -0.0030869 | 0.02223 | -0.0034159 | -0.004578 | 0.13733 | -0.032043 | 0.045776 | 0.20599 | 0.082397 | 0.10529 | -0.17395 | 0.13275 | -121.7148 | 0.068665 | -121.225 | -121.2479 | -121.0831 | 121.5775 | -0.027466 | -0.11902 | 121.8155 | 121.7148 | 121.6919 | 0.13733 | 0.11444 | -0.10529 | -0.032044 | -0.09613 | 0.38452 | 0.52643 | 0.36163 | 0.63171 | 0.46692 | 0.23804 | 0.077819 | 0.48981 | 121.7834 | 0.16937 | 121.8475 | 121.7468 | 121.7422 | -0.19684 | -121.8796 | 121.6553 | 121.6782 | 121.6049 | 121.4355
512.8281 | 121.7972 | -121.6141 | 0.16022 | -0.0036622 | 0.043502 | 0.014398 | -0.016195 | 0.0010874 | -0.0027556 | -0.00058311 | -0.0015565 | 0.0030719 | 0.070758 | 0.05912 | -0.0015915 | 0.016034 | -0.0019205 | -0.054932 | 0.14191 | -0.082397 | -0.045776 | 0.032043 | -0.064087 | -0.050354 | -0.27924 | 0.13733 | -121.7102 | 0.004578 | -121.3303 | -121.376 | -121.1655 | 121.5317 | -0.01831 | -0.20599 | 121.6461 | 121.5637 | 121.55 | 0.032043 | 0.01831 | -0.09613 | -0.022888 | -0.15564 | 0.28381 | 0.44861 | 0.23804 | 0.54474 | 0.33417 | 0.11444 | 0.036621 | 0.37994 | 121.7148 | 0.2243 | 121.8475 | 121.756 | 121.7514 | -0.24261 | -121.8704 | 121.5683 | 121.6187 | 121.5591 | 121.3348
514.5156 | 121.875 | -121.6049 | 0.15106 | 0.026856 | 0.044357 | 0.014185 | -0.015554 | 0.0027964 | -0.0016876 | -0.0025057 | 0.0075989 | 0.0013629 | 0.069904 | 0.060188 | -0.0028733 | 0.018171 | 0.00021567 | 0.032043 | 0.14191 | -0.068665 | 0.036621 | 0.17395 | 0.032043 | 0.059509 | -0.11902 | 0.13733 | -121.7239 | 0.059509 | -121.2296 | -121.2753 | -121.1014 | 121.5363 | -0.009155 | -0.11444 | 121.7789 | 121.6644 | 121.637 | 0.12817 | 0.10071 | -0.11902 | -0.013733 | -0.091553 | 0.37537 | 0.50354 | 0.32959 | 0.62256 | 0.44861 | 0.24261 | 0.10529 | 0.49439 | 121.7834 | 0.21057 | 121.8613 | 121.7468 | 121.7422 | -0.21973 | -121.875 | 121.6415 | 121.6644 | 121.637 | 121.4859
516.25 | 121.8658 | -121.6141 | 0.16022 | 0.026856 | 0.044784 | 0.014398 | -0.016836 | 0.00023275 | -0.0027556 | -0.00036951 | 0.010651 | 0.0030719 | 0.070118 | 0.062965 | -0.0047959 | 0.017957 | -0.00042513 | -0.004578 | 0.14648 | -0.050354 | 0.018311 | 0.16479 | 0.068665 | 0.064087 | -0.13275 | 0.16479 | -121.7102 | 0.059509 | -121.2341 | -121.2708 | -121.106 | 121.5637 | -0.013733 | -0.14191 | 121.7789 | 121.6782 | 121.6827 | 0.11444 | 0.11902 | -0.09613 | 0.004578 | -0.10071 | 0.37994 | 0.50812 | 0.34332 | 0.60425 | 0.43945 | 0.21515 | 0.068665 | 0.47607 | 121.7697 | 0.19684 | 121.875 | 121.7606 | 121.7789 | -0.21057 | -121.8704 | 121.6324 | 121.6736 | 121.6095 | 121.4813
518 | 121.8933 | -121.6095 | 0.14191 | 0.011597 | 0.042007 | 0.015466 | -0.017263 | -0.00062165 | -0.0040374 | -0.0020785 | 0.0045471 | 0.0028583 | 0.069904 | 0.062111 | -0.0022325 | 0.018384 | 0.0014975 | -0.013733 | 0.13733 | -0.027466 | 0.036621 | 0.1831 | 0.064087 | 0.10071 | -0.19684 | 0.11444 | -121.7102 | 0.073242 | -121.2158 | -121.2387 | -121.0876 | 121.582 | -0.004578 | -0.10529 | 121.7926 | 121.7102 | 121.6736 | 0.12817 | 0.091553 | -0.10071 | -0.027466 | -0.068665 | 0.39368 | 0.52185 | 0.37079 | 0.62256 | 0.4715 | 0.21057 | 0.064087 | 0.49439 | 121.7834 | 0.16479 | 121.8246 | 121.7468 | 121.7239 | -0.16937 | -121.8521 | 121.6461 | 121.6827 | 121.5958 | 121.4127
519.6719 | 121.907 | -121.6003 | 0.14648 | 0.034485 | 0.044998 | 0.015253 | -0.014272 | 0.0040782 | -0.0019012 | -0.00058311 | 0.013702 | 0.0026447 | 0.07204 | 0.059547 | -0.0018051 | 0.017957 | -0.00063873 | 0.064087 | 0.11444 | -0.027466 | 0.10529 | 0.26093 | 0.12817 | 0.13275 | -0.10529 | 0.11444 | -121.7056 | 0.11444 | -121.1838 | -121.2158 | -121.0648 | 121.5729 | -0.032043 | -0.041198 | 121.8613 | 121.7331 | 121.7285 | 0.16022 | 0.15564 | -0.10529 | -0.032043 | -0.032043 | 0.41656 | 0.53558 | 0.38452 | 0.64087 | 0.48981 | 0.28839 | 0.13275 | 0.52185 | 121.8201 | 0.14191 | 121.8201 | 121.7148 | 121.7148 | -0.17395 | -121.8521 | 121.7056 | 121.7148 | 121.6644 | 121.4951
521.4062 | 121.9482 | -121.5591 | 0.12817 | -0.0036622 | 0.045211 | 0.015253 | -0.014058 | 0.0023692 | -0.00019224 | 0.0015531 | 0.010651 | 0.0034991 | 0.071186 | 0.065102 | -0.0011643 | 0.019452 | 2.068e-06 | 0.050354 | 0.10986 | 0 | 0.091553 | 0.23346 | 0.09613 | 0.10529 | -0.07782 | 0.14191 | -121.701 | 0.14648 | -121.1655 | -121.2021 | -121.0373 | 121.5591 | -0.018311 | -0.036621 | 121.7926 | 121.6644 | 121.6553 | 0.10529 | 0.09613 | -0.14191 | 0.013733 | 0.01831 | 0.39368 | 0.52185 | 0.35706 | 0.66376 | 0.49896 | 0.23346 | 0.091553 | 0.53558 | 121.8475 | 0.10986 | 121.843 | 121.669 | 121.7011 | -0.12817 | -121.8292 | 121.6507 | 121.7056 | 121.6095 | 121.4813
523.1562 | 121.9574 | -121.5683 | 0.13733 | -0.0036622 | 0.042861 | 0.011835 | -0.02004 | 1.915e-05 | -0.0044646 | -0.0033603 | -0.0015565 | 8.1264e-05 | 0.068195 | 0.063606 | -0.0041551 | 0.018598 | 0.0014975 | 0.022888 | 0.10071 | 0 | 0.07782 | 0.23346 | 0.13275 | 0.14648 | -0.086975 | 0.07782 | -121.6919 | 0.1236 | -121.1243 | -121.1609 | -121.019 | 121.5683 | -0.036621 | -0.059509 | 121.8018 | 121.7148 | 121.701 | 0.14648 | 0.13275 | -0.1236 | -0.059509 | -0.013733 | 0.44403 | 0.54932 | 0.40741 | 0.67291 | 0.53101 | 0.23346 | 0.07782 | 0.56763 | 121.8155 | 0.10071 | 121.7697 | 121.669 | 121.6461 | -0.13733 | -121.8292 | 121.6461 | 121.6919 | 121.5912 | 121.4813
524.8906 | 121.8933 | -121.6049 | 0.15564 | 0.042114 | 0.046279 | 0.016321 | -0.017263 | 0.0072824 | -0.0021148 | -0.0010105 | 0.010651 | 0.0024311 | 0.070545 | 0.071724 | -0.0026597 | 0.017743 | 0.0014975 | 0.027466 | 0.11902 | -0.032043 | 0.07782 | 0.21057 | 0.086975 | 0.11444 | -0.16479 | 0.1236 | -121.701 | 0.073242 | -121.2158 | -121.2296 | -121.0922 | 121.5729 | -0.036621 | -0.07782 | 121.8155 | 121.7194 | 121.6919 | 0.14648 | 0.11902 | -0.096131 | -0.032044 | -0.082398 | 0.3891 | 0.51269 | 0.37537 | 0.60883 | 0.4715 | 0.24261 | 0.10986 | 0.48523 | 121.7743 | 0.15106 | 121.8246 | 121.7239 | 121.7285 | -0.18768 | -121.8567 | 121.6827 | 121.6782 | 121.6324 | 121.4401
526.5625 | 121.9345 | -121.5454 | 0.12817 | 0.042114 | 0.045852 | 0.018671 | -0.014913 | 0.0042918 | 2.1362e-05 | -0.00079691 | 0.019806 | 0.0039265 | 0.06969 | 0.058052 | -0.0020187 | 0.019239 | -0.0017069 | 0.064087 | 0.13275 | -0.009155 | 0.14191 | 0.27008 | 0.13275 | 0.13733 | -0.10071 | 0.11902 | -121.7148 | 0.1236 | -121.1609 | -121.1975 | -121.0373 | 121.5363 | 0.004577 | 0.013733 | 121.8155 | 121.6827 | 121.6782 | 0.14648 | 0.14191 | -0.16937 | -0.009155 | -0.004578 | 0.38452 | 0.50812 | 0.3479 | 0.67749 | 0.51727 | 0.27924 | 0.15106 | 0.55389 | 121.8384 | 0.14191 | 121.8338 | 121.6782 | 121.6644 | -0.13733 | -121.843 | 121.6873 | 121.669 | 121.6095 | 121.4447
528.3125 | 121.8201 | -121.6324 | 0.1831 | -0.0036622 | 0.045425 | 0.01098 | -0.015554 | 0.0019418 | -0.0033966 | 0.00027129 | 0.0045471 | 0.0058491 | 0.069049 | 0.062965 | -0.0056503 | 0.016248 | -0.0036295 | -0.045776 | 0.16937 | -0.054932 | -0.036621 | 0.10529 | 0.018311 | 0.032043 | -0.18768 | 0.16479 | -121.7697 | -0.018311 | -121.2799 | -121.312 | -121.1472 | 121.5775 | -0.013732 | -0.21973 | 121.7377 | 121.6644 | 121.6507 | 0.086975 | 0.073243 | -0.13733 | -0.01831 | -0.20142 | 0.35248 | 0.48523 | 0.32043 | 0.62256 | 0.45776 | 0.16022 | 0.018311 | 0.48981 | 121.7514 | 0.22431 | 121.9345 | 121.8018 | 121.7972 | -0.23804 | -121.9528 | 121.5958 | 121.6141 | 121.5866 | 121.4447
529.9844 | 121.8475 | -121.6415 | 0.16937 | 0.042114 | 0.046707 | 0.014612 | -0.014699 | -0.00062165 | -0.00019224 | -0.0025057 | 0.010651 | 0.0043537 | 0.069904 | 0.057625 | -0.0058639 | 0.01753 | -0.0034159 | -0.018311 | 0.1831 | -0.07782 | -0.004578 | 0.10986 | 0.013733 | 0.045776 | -0.20142 | 0.16479 | -121.7377 | 0.009155 | -121.2341 | -121.2982 | -121.1151 | 121.5637 | 0.013732 | -0.17395 | 121.7514 | 121.6873 | 121.6553 | 0.1236 | 0.091553 | -0.09613 | -0.004578 | -0.16022 | 0.40741 | 0.52643 | 0.34332 | 0.62256 | 0.43945 | 0.18768 | 0.073242 | 0.50354 | 121.7468 | 0.26092 | 121.9025 | 121.8246 | 121.8063 | -0.24719 | -121.907 | 121.637 | 121.6507 | 121.6232 | 121.4401
531.7188 | 121.8201 | -121.6415 | 0.1831 | 0.0039673 | 0.043716 | 0.011835 | -0.014913 | -0.0033986 | -0.001474 | -0.0018649 | 0.019806 | 0.0043537 | 0.070118 | 0.068947 | -0.0043687 | 0.016889 | -0.0034159 | -0.068665 | 0.15564 | -0.07782 | -0.009155 | 0.1236 | 0.041199 | 0.041199 | -0.19684 | 0.17853 | -121.756 | 0 | -121.2845 | -121.312 | -121.1426 | 121.5637 | -0.027465 | -0.19226 | 121.7651 | 121.6827 | 121.6827 | 0.11902 | 0.11902 | -0.11444 | -0.004577 | -0.1831 | 0.35706 | 0.49896 | 0.32959 | 0.6134 | 0.44403 | 0.20142 | 0.068665 | 0.4715 | 121.756 | 0.23346 | 121.9345 | 121.7972 | 121.8201 | -0.26092 | -121.9391 | 121.6324 | 121.6415 | 121.5729 | 121.4447
533.4531 | 121.8201 | -121.6324 | 0.17853 | -0.011291 | 0.043716 | 0.01333 | -0.015981 | -0.0029714 | -0.0029694 | -0.00079691 | 0.0014953 | 0.0034991 | 0.069263 | 0.064247 | -0.0052231 | 0.015821 | -0.0055521 | -0.054932 | 0.16479 | -0.022888 | -0.041199 | 0.11444 | 0.009155 | 0.027466 | -0.23346 | 0.14191 | -121.7194 | -0.004578 | -121.2616 | -121.3211 | -121.1472 | 121.6095 | -0.013733 | -0.21973 | 121.7468 | 121.6599 | 121.6415 | 0.050354 | 0.032043 | -0.086975 | -0.036621 | -0.18311 | 0.37079 | 0.48523 | 0.31128 | 0.5722 | 0.39825 | 0.13733 | -0.018311 | 0.45776 | 121.7148 | 0.18768 | 121.8613 | 121.7972 | 121.7743 | -0.20142 | -121.8979 | 121.5912 | 121.6278 | 121.5775 | 121.3989
535.125 | 121.8155 | -121.6232 | 0.1831 | -0.02655 | 0.062301 | 0.013971 | 0.017344 | -0.0044668 | -0.0029694 | -0.0014377 | -0.0076599 | 0.0015765 | 0.016498 | -0.0058213 | -0.0071457 | 0.01518 | -0.0025613 | -0.059509 | 0.14648 | -0.041199 | -0.036621 | 0.09613 | 0.018311 | 0.027466 | 0.004578 | 0.16479 | -0.082397 | 0.032043 | 0.07782 | 0.018311 | 0.13733 | 121.582 | -0.036621 | -0.21973 | 121.7194 | 121.6507 | 121.6415 | 0.068665 | 0.05951 | 121.5408 | -0.01831 | -0.15106 | 121.7011 | 121.7606 | 121.6415 | 0.21973 | 0.10071 | 0.13733 | 0.004578 | 0.16022 | 0.11444 | 0.18768 | 0.24719 | 121.7697 | 121.788 | -0.2243 | -0.2655 | 121.5866 | 121.6553 | 121.5637 | 121.6278
536.875 | 121.8246 | -121.6187 | 0.18768 | -0.0036622 | 0.061447 | 0.014185 | 0.018199 | 1.915e-05 | -0.0036102 | -0.0018649 | -0.0046081 | 0.0030719 | 0.018421 | -0.0015487 | -0.0035141 | 0.016248 | 0.0029929 | 0 | 0.13275 | -0.036621 | 0.027466 | 0.16479 | 0.036621 | 0.064087 | 0.036621 | 0.13733 | -0.064087 | 0.068665 | 0.09613 | 0.022888 | 0.14648 | 121.582 | -0.054932 | -0.16022 | 121.7834 | 121.6827 | 121.6553 | 0.10071 | 0.073242 | 121.5546 | -0.050354 | -0.11902 | 121.7148 | 121.7651 | 121.6415 | 0.21057 | 0.086975 | 0.20142 | 0.064087 | 0.16022 | 0.13275 | 0.16937 | 0.20142 | 121.7514 | 121.756 | -0.2243 | -0.25177 | 121.6461 | 121.6873 | 121.6187 | 121.6553
538.5469 | 121.8201 | -121.6278 | 0.19684 | -0.0036622 | 0.061019 | 0.010767 | 0.016917 | -0.0010488 | -0.002542 | 0.00069849 | 0.0014953 | 0.0017901 | 0.018634 | -0.0088119 | -0.0056503 | 0.015394 | -0.0017069 | -0.054932 | 0.14648 | -0.045776 | -0.041199 | 0.10986 | 0.027466 | 0.027466 | -0.059509 | 0.15106 | -0.082397 | 0.009155 | 0.073242 | -0.004578 | 0.1236 | 121.582 | -0.050354 | -0.23804 | 121.7377 | 121.6553 | 121.6553 | 0.073242 | 0.073242 | 121.5454 | -0.045776 | -0.18768 | 121.701 | 121.7514 | 121.6232 | 0.20599 | 0.077819 | 0.15564 | 0.004577 | 0.15564 | 0.091552 | 0.19226 | 0.23346 | 121.7743 | 121.7789 | -0.24261 | -0.27924 | 121.5866 | 121.637 | 121.5729 | 121.5683
540.2812 | 121.9528 | -121.6003 | 0.13275 | 0.0039673 | 0.062301 | 0.014825 | 0.018839 | -0.0036124 | -0.0038238 | -0.0022921 | -0.0015565 | 0.0020039 | 0.017566 | -0.00026713 | -0.00052345 | 0.018812 | -0.0042703 | -0.004578 | 0.14191 | -0.018311 | 0.073242 | 0.2243 | 0.11902 | 0.13275 | 0.045776 | 0.10071 | -0.054932 | 0.15106 | 0.21515 | 0.15564 | 0.23804 | 121.582 | 0.009156 | -0.059509 | 121.8246 | 121.7331 | 121.7194 | 0.15106 | 0.13733 | 121.5454 | -0.032043 | 0.018311 | 121.8155 | 121.8384 | 121.756 | 0.29297 | 0.21057 | 0.24261 | 0.091553 | 0.27008 | 0.20599 | 0.16022 | 0.15564 | 121.7422 | 121.701 | -0.15106 | -0.18768 | 121.6736 | 121.7514 | 121.5958 | 121.6461
542.0312 | 121.9391 | -121.5958 | 0.15106 | -0.0036622 | 0.063796 | 0.013544 | 0.018199 | -0.0010488 | -0.004892 | -0.0029331 | -0.0046081 | -0.00013254 | 0.019916 | -0.0028305 | -0.0015915 | 0.017743 | 0.00085667 | -0.009155 | 0.1236 | -0.004578 | 0.041199 | 0.19684 | 0.10529 | 0.12817 | -0.013733 | 0.1236 | -0.054932 | 0.12817 | 0.17853 | 0.13275 | 0.2243 | 121.5912 | -0.027466 | -0.10986 | 121.7926 | 121.7239 | 121.7011 | 0.13275 | 0.10986 | 121.5408 | -0.027466 | -0.022888 | 121.7743 | 121.8201 | 121.7285 | 0.27924 | 0.18768 | 0.20142 | 0.045777 | 0.23346 | 0.18311 | 0.12817 | 0.17853 | 121.7194 | 121.7194 | -0.15564 | -0.20599 | 121.637 | 121.7239 | 121.5866 | 121.582
543.7656 | 121.8475 | -121.637 | 0.19684 | -0.018921 | 0.065933 | 0.012689 | 0.013072 | -0.00062165 | -0.0057464 | -0.00015591 | -0.0046081 | 0.00029486 | 0.019275 | -0.0088119 | -0.0043687 | 0.014112 | -0.0057657 | -0.045776 | 0.16022 | -0.018311 | -0.045776 | 0.07782 | -0.004578 | 0.027466 | -0.082397 | 0.15564 | -0.086975 | 0.036621 | 0.073242 | 0.018311 | 0.13275 | 121.6187 | -0.036621 | -0.24261 | 121.7148 | 121.6644 | 121.6324 | 0.045777 | 0.013733 | 121.55 | -0.041198 | -0.16022 | 121.7102 | 121.7697 | 121.6553 | 0.21973 | 0.10529 | 0.096131 | -0.027465 | 0.16022 | 0.1236 | 0.17853 | 0.24261 | 121.7972 | 121.7926 | -0.21515 | -0.28381 | 121.5912 | 121.6736 | 121.5912 | 121.5546
545.4375 | 121.8384 | -121.637 | 0.17853 | -0.0036622 | 0.068923 | 0.014825 | 0.010295 | 0.00066015 | -0.0027556 | -0.0044285 | 0.0075989 | 0.0032855 | 0.019062 | -0.0013351 | -0.00073705 | 0.019452 | -0.00063873 | -0.013733 | 0.12817 | -0.041199 | 0.013733 | 0.13733 | 0.036621 | 0.032043 | -0.041199 | 0.14191 | -0.07782 | 0.059509 | 0.064087 | -0.004578 | 0.13733 | 121.5958 | -0.050354 | -0.16479 | 121.7743 | 121.669 | 121.6736 | 0.073242 | 0.07782 | 121.5591 | -0.036621 | -0.11902 | 121.701 | 121.7743 | 121.6324 | 0.21515 | 0.073242 | 0.17853 | 0.054932 | 0.14191 | 0.13733 | 0.16937 | 0.21973 | 121.7651 | 121.7789 | -0.21973 | -0.25635 | 121.6507 | 121.6965 | 121.6232 | 121.5958
547.1719 | 121.8201 | -121.637 | 0.17395 | -0.011291 | 0.070205 | 0.016962 | 0.01179 | 0.0021556 | -0.00040584 | -0.0042147 | 0.0014953 | 0.0022175 | 0.019703 | -0.0036849 | -9.605e-05 | 0.018171 | -0.00021153 | -0.032043 | 0.16022 | -0.045776 | -0.054932 | 0.050354 | -0.041199 | -0.009155 | -0.16022 | 0.16022 | -0.073242 | 0.032043 | 0.036621 | -0.018311 | 0.13275 | 121.5912 | -0.013733 | -0.22888 | 121.6873 | 121.6278 | 121.5958 | 0.036621 | 0.004577 | 121.5637 | -0.013733 | -0.14191 | 121.6736 | 121.7697 | 121.6187 | 0.20599 | 0.054931 | 0.09613 | -0.009156 | 0.10986 | 0.10529 | 0.20599 | 0.23346 | 121.7972 | 121.7972 | -0.21973 | -0.24719 | 121.582 | 121.669 | 121.6049 | 121.4767
548.9219 | 121.8338 | -121.6553 | 0.17853 | -0.0036622 | 0.068496 | 0.013544 | 0.0079447 | 0.0042918 | -0.004892 | -0.00079691 | 0.0045471 | 0.00093566 | 0.019062 | -0.0077439 | -0.0033005 | 0.017957 | 0.0023521 | -0.059509 | 0.14648 | -0.054932 | -0.018311 | 0.11444 | 0.013733 | 0.022888 | -0.10529 | 0.16937 | -0.068665 | 0.004578 | 0.068665 | 0 | 0.11902 | 121.6003 | -0.032044 | -0.19684 | 121.7697 | 121.6782 | 121.669 | 0.07782 | 0.068665 | 121.5866 | -0.009155 | -0.17395 | 121.7239 | 121.7743 | 121.6553 | 0.18768 | 0.068665 | 0.16937 | 0.036621 | 0.13733 | 0.073243 | 0.20142 | 0.23804 | 121.8018 | 121.8246 | -0.23346 | -0.24719 | 121.637 | 121.6599 | 121.5958 | 121.55
550.5938 | 121.8338 | -121.6461 | 0.19226 | -0.011291 | 0.068283 | 0.01333 | 0.01414 | 0.0017282 | -0.003183 | -0.0020785 | -0.0015565 | 0.0017901 | 0.019275 | -0.00090793 | 0.0011855 | 0.016675 | -0.0023477 | -0.041199 | 0.15564 | -0.041199 | -0.032043 | 0.073242 | -0.027466 | -0.004578 | -0.15106 | 0.15106 | -0.082397 | 0.013733 | 0.041199 | -0.036621 | 0.12817 | 121.6049 | -0.036621 | -0.2243 | 121.7194 | 121.6415 | 121.6187 | 0.036621 | 0.013733 | 121.5637 | -0.041199 | -0.17853 | 121.6873 | 121.7743 | 121.6095 | 0.21057 | 0.045776 | 0.11444 | 0.009156 | 0.1236 | 0.09613 | 0.19684 | 0.23346 | 121.8018 | 121.7972 | -0.23346 | -0.27466 | 121.6141 | 121.6599 | 121.6049 | 121.4951
552.3281 | 121.9757 | -121.6232 | 0.13275 | -0.011291 | 0.066787 | 0.01333 | 0.0098673 | 0.0010874 | -0.002542 | -0.00079691 | 0.0014953 | 8.1264e-05 | 0.019916 | -0.0045395 | -0.00052345 | 0.020521 | 0.00042947 | 0.022888 | 0.091553 | -0.013733 | 0.082397 | 0.21515 | 0.082397 | 0.10529 | -0.027466 | 0.11902 | -0.022888 | 0.15564 | 0.20142 | 0.11444 | 0.23346 | 121.6095 | -0.041198 | -0.050354 | 121.8384 | 121.7285 | 121.7056 | 0.11902 | 0.09613 | 121.6003 | -0.013732 | 0.022889 | 121.8246 | 121.8567 | 121.7377 | 0.25635 | 0.13733 | 0.22888 | 0.09613 | 0.2243 | 0.17853 | 0.10529 | 0.14191 | 121.7148 | 121.7422 | -0.14648 | -0.15564 | 121.7056 | 121.7789 | 121.6461 | 121.5958
554.0625 | 121.8384 | -121.6324 | 0.16022 | -0.0036622 | 0.06871 | 0.012903 | 0.010508 | 0.00087375 | -0.0036102 | -0.0020785 | 0.0045471 | 0.0024311 | 0.022266 | -0.0026169 | -0.0024461 | 0.016462 | -0.0034159 | 0 | 0.13275 | -0.027466 | 0.009155 | 0.15106 | 0.032043 | 0.036621 | -0.064087 | 0.14648 | -0.054932 | 0.059509 | 0.10529 | 0.022888 | 0.14648 | 121.6049 | -0.027466 | -0.15106 | 121.7834 | 121.669 | 121.6644 | 0.064087 | 0.059509 | 121.5775 | -0.013733 | -0.10071 | 121.7377 | 121.7789 | 121.6553 | 0.20142 | 0.07782 | 0.17853 | 0.036621 | 0.16022 | 0.11444 | 0.16022 | 0.20142 | 121.7651 | 121.7789 | -0.18768 | -0.21515 | 121.6415 | 121.6919 | 121.6324 | 121.5683
555.8125 | 121.9437 | -121.6232 | 0.16479 | -0.018921 | 0.068496 | 0.013116 | 0.010081 | 1.915e-05 | -0.0021148 | -0.0033603 | 0.0014953 | 0.0017901 | 0.021198 | -0.010094 | -0.00095065 | 0.020948 | -0.0040567 | -0.045776 | 0.16937 | -0.032043 | -0.013733 | 0.13733 | 0 | 0.045776 | -0.11444 | 0.1236 | -0.073242 | 0.11444 | 0.13733 | 0.07782 | 0.20142 | 121.5912 | 0.004578 | -0.17853 | 121.7606 | 121.669 | 121.6232 | 0.077819 | 0.032043 | 121.55 | -0.041199 | -0.050354 | 121.7606 | 121.8246 | 121.7011 | 0.27466 | 0.15106 | 0.16937 | 0.01831 | 0.21057 | 0.18768 | 0.20142 | 0.19684 | 121.7926 | 121.7468 | -0.19684 | -0.23804 | 121.6095 | 121.7377 | 121.5775 | 121.5088
557.4844 | 121.8567 | -121.6232 | 0.19226 | -0.0036622 | 0.068923 | 0.017175 | 0.010935 | 0.00087375 | -0.0051056 | 0.00091209 | -0.0015565 | 0.0032855 | 0.019275 | -0.0079575 | -0.0028733 | 0.017316 | -0.0036295 | -0.036621 | 0.15106 | -0.027466 | -0.032043 | 0.10071 | -0.018311 | -0.013733 | -0.16022 | 0.16479 | -0.068665 | 0.027466 | 0.045776 | -0.027466 | 0.12817 | 121.5958 | -0.041199 | -0.2243 | 121.7239 | 121.6095 | 121.6049 | 0.013733 | 0.009155 | 121.5546 | -0.027466 | -0.16479 | 121.669 | 121.7514 | 121.5958 | 0.19684 | 0.041199 | 0.12817 | -0.004577 | 0.11444 | 0.096131 | 0.17853 | 0.23346 | 121.7743 | 121.788 | -0.21973 | -0.26093 | 121.5912 | 121.6507 | 121.5866 | 121.463
559.2188 | 121.8796 | -121.6599 | 0.1831 | -0.02655 | 0.067428 | 0.011621 | 0.0096537 | -0.002117 | -0.0029694 | -0.0029331 | -0.0046081 | 0.0017901 | 0.017566 | -0.0049667 | -0.0043687 | 0.016034 | -0.0027749 | -0.054932 | 0.14648 | -0.036621 | -0.050354 | 0.082397 | 0.009155 | 0.022888 | -0.16479 | 0.11902 | -0.068665 | 0.013733 | 0.073242 | 0.018311 | 0.15106 | 121.6232 | -0.036621 | -0.23346 | 121.7422 | 121.6827 | 121.669 | 0.059509 | 0.045776 | 121.5912 | -0.064086 | -0.16937 | 121.7331 | 121.8109 | 121.6782 | 0.21973 | 0.086976 | 0.11902 | -0.013733 | 0.14191 | 0.082398 | 0.18311 | 0.18768 | 121.8063 | 121.7789 | -0.21973 | -0.25177 | 121.6095 | 121.6736 | 121.6049 | 121.4951
560.9688 | 121.8979 | -121.6415 | 0.17395 | -0.018921 | 0.069564 | 0.014185 | 0.0092263 | 1.915e-05 | -0.001474 | -0.00079691 | -0.0046081 | 0.0039265 | 0.017994 | -0.0085983 | -0.0043687 | 0.016675 | -0.0014931 | 0.004578 | 0.14648 | -0.032043 | 0.018311 | 0.16022 | 0.045776 | 0.045776 | -0.07782 | 0.13733 | -0.064087 | 0.09613 | 0.13275 | 0.064087 | 0.1831 | 121.6095 | -0.027466 | -0.15564 | 121.8018 | 121.6873 | 121.6873 | 0.077819 | 0.077819 | 121.5775 | -0.036621 | -0.07782 | 121.7743 | 121.8246 | 121.7056 | 0.24719 | 0.12817 | 0.19226 | 0.050354 | 0.19684 | 0.16022 | 0.17853 | 0.20142 | 121.788 | 121.7789 | -0.20599 | -0.23804 | 121.6599 | 121.7377 | 121.6461 | 121.5637
562.6406 | 121.994 | -121.6141 | 0.15106 | -0.0036622 | 0.061874 | 0.014398 | 0.010081 | -0.00040805 | -0.0016876 | -0.0042147 | -0.0015565 | -0.00034614 | 0.018848 | -0.0011215 | -0.0015915 | 0.017957 | 0.00042947 | 0.004578 | 0.1236 | 0.004578 | 0.07782 | 0.25177 | 0.15106 | 0.16479 | -0.022888 | 0.10986 | -0.050354 | 0.15564 | 0.22888 | 0.16937 | 0.24719 | 121.6187 | -0.027466 | -0.073242 | 121.8658 | 121.7789 | 121.7651 | 0.16022 | 0.14648 | 121.5637 | -0.041199 | 0.004578 | 121.843 | 121.8613 | 121.7834 | 0.29755 | 0.21973 | 0.24719 | 0.073242 | 0.27924 | 0.20599 | 0.11902 | 0.16022 | 121.7377 | 121.7239 | -0.14648 | -0.20142 | 121.6919 | 121.7697 | 121.6187 | 121.5912
564.3906 | 121.9345 | -121.6278 | 0.15106 | -0.02655 | 0.068283 | 0.013971 | 0.0075173 | 0.00044655 | -0.0016876 | -0.0025057 | -0.0046081 | -0.0012005 | 0.019489 | -0.0047531 | -9.605e-05 | 0.019666 | 0.0044883 | -0.018311 | 0.091553 | -0.004578 | 0.032043 | 0.20599 | 0.068665 | 0.086975 | -0.11444 | 0.10071 | -0.036621 | 0.10529 | 0.1236 | 0.086975 | 0.19226 | 121.6232 | -0.059509 | -0.11902 | 121.8338 | 121.7148 | 121.6965 | 0.091553 | 0.073243 | 121.5912 | -0.050354 | -0.045776 | 121.7514 | 121.8201 | 121.7148 | 0.22888 | 0.1236 | 0.21057 | 0.036621 | 0.16022 | 0.14191 | 0.096131 | 0.13733 | 121.7194 | 121.7285 | -0.15564 | -0.18768 | 121.6599 | 121.7331 | 121.6095 | 121.5134
566.0625 | 121.9391 | -121.6187 | 0.14648 | -0.011291 | 0.069137 | 0.014398 | 0.0083719 | -0.0023306 | -0.0023284 | -0.0025057 | -0.0076599 | 0.00072206 | 0.019062 | -0.0019759 | -0.00052345 | 0.018384 | -0.0019205 | -0.022888 | 0.10529 | -0.004578 | 0.041199 | 0.20142 | 0.064087 | 0.091553 | -0.15564 | 0.1236 | -0.054932 | 0.091553 | 0.1236 | 0.09613 | 0.19226 | 121.6141 | -0.041198 | -0.10529 | 121.8201 | 121.7102 | 121.6827 | 0.096131 | 0.068665 | 121.5637 | -0.022888 | -0.054931 | 121.7422 | 121.8109 | 121.7148 | 0.24719 | 0.15106 | 0.20599 | 0.045777 | 0.17853 | 0.14649 | 0.10986 | 0.17853 | 121.7239 | 121.7422 | -0.15106 | -0.20142 | 121.6599 | 121.7102 | 121.5958 | 121.463
567.8125 | 121.9528 | -121.5958 | 0.15564 | -0.0036622 | 0.065933 | 0.013544 | 0.014781 | 1.915e-05 | -0.0010468 | -0.00058311 | -0.0015565 | 0.0026447 | 0.018848 | -0.0024033 | -0.00052345 | 0.016248 | 2.068e-06 | -0.027466 | 0.14191 | -0.041199 | 0.013733 | 0.13733 | 0.036621 | 0.041199 | -0.15564 | 0.11902 | -0.041199 | 0.10986 | 0.15564 | 0.091553 | 0.22888 | 121.5546 | -0.013733 | -0.14191 | 121.7331 | 121.637 | 121.6324 | 0.082398 | 0.07782 | 121.5546 | -0.036621 | -0.045777 | 121.7514 | 121.8246 | 121.6873 | 0.27008 | 0.13275 | 0.17853 | 0.054932 | 0.19684 | 0.15106 | 0.18311 | 0.16022 | 121.7377 | 121.7148 | -0.19684 | -0.19684 | 121.6095 | 121.7056 | 121.5683 | 121.4401
569.4844 | 121.8475 | -121.6873 | 0.16937 | -0.011291 | 0.070846 | 0.01333 | 0.012431 | 0.0010874 | -0.0027556 | 0.0013395 | 0.0014953 | 8.1264e-05 | 0.020771 | -0.0090255 | -0.0011643 | 0.017743 | 0.00042947 | -0.032043 | 0.16479 | -0.041199 | -0.022888 | 0.086975 | -0.036621 | -0.018311 | -0.25177 | 0.16479 | -0.073242 | 0.022888 | 0.041199 | -0.036621 | 0.12817 | 121.6461 | -0.004578 | -0.19226 | 121.7743 | 121.669 | 121.6507 | 0.022888 | 0.004578 | 121.6141 | -0.004578 | -0.14649 | 121.7285 | 121.8155 | 121.6507 | 0.20142 | 0.036621 | 0.12817 | 0.018311 | 0.11444 | 0.09613 | 0.20599 | 0.23804 | 121.8521 | 121.8521 | -0.21057 | -0.24261 | 121.6644 | 121.7102 | 121.6553 | 121.4355
571.2188 | 121.8979 | -121.6507 | 0.16937 | -0.011291 | 0.064437 | 0.013544 | 0.015208 | -0.0012624 | -0.0027556 | -0.0022921 | -0.0046081 | 8.1264e-05 | 0.019916 | -0.0015487 | -0.0037277 | 0.017316 | -0.0057657 | 0 | 0.14648 | -0.022888 | 0.036621 | 0.16022 | 0.045776 | 0.068665 | -0.13275 | 0.12817 | -0.050354 | 0.068665 | 0.10986 | 0.045776 | 0.16022 | 121.6278 | -0.022889 | -0.13275 | 121.8109 | 121.7194 | 121.6965 | 0.091553 | 0.068664 | 121.6003 | -0.041199 | -0.10071 | 121.7606 | 121.8109 | 121.6965 | 0.21057 | 0.09613 | 0.1831 | 0.059509 | 0.16022 | 0.11902 | 0.16937 | 0.17853 | 121.7972 | 121.7789 | -0.19226 | -0.21973 | 121.6873 | 121.7194 | 121.6507 | 121.5179
572.9844 | 121.9666 | -121.6232 | 0.14191 | -0.0036622 | 0.062942 | 0.013544 | 0.017344 | 1.915e-05 | -0.0016876 | -0.0016513 | -0.0015565 | 0.0017901 | 0.017566 | -0.00069433 | -0.0013779 | 0.019452 | -0.0023477 | -0.036621 | 0.14191 | -0.022888 | 0.036621 | 0.15564 | 0.027466 | 0.054932 | -0.1831 | 0.11444 | -0.050354 | 0.1236 | 0.15564 | 0.10071 | 0.20599 | 121.6003 | 0 | -0.10529 | 121.7789 | 121.6782 | 121.6507 | 0.07782 | 0.050354 | 121.5729 | -0.027466 | -0.018311 | 121.7789 | 121.8292 | 121.7239 | 0.25635 | 0.15106 | 0.17853 | 0.059509 | 0.20599 | 0.17395 | 0.16479 | 0.16479 | 121.7651 | 121.7377 | -0.16479 | -0.19226 | 121.6599 | 121.7468 | 121.5866 | 121.4401
574.6562 | 121.9849 | -121.6141 | 0.15106 | -0.0036622 | 0.062515 | 0.012689 | 0.016917 | 0.0023692 | -0.004251 | -0.00036951 | -0.0015565 | 0.0013629 | 0.019489 | -0.0026169 | -0.00095065 | 0.018171 | 0.0021383 | -0.013733 | 0.13275 | -0.009155 | 0.041199 | 0.17853 | 0.054932 | 0.091553 | -0.15564 | 0.10071 | -0.036621 | 0.13275 | 0.16937 | 0.11902 | 0.22888 | 121.6049 | -0.018311 | -0.10986 | 121.7926 | 121.7056 | 121.669 | 0.10071 | 0.064087 | 121.5775 | -0.050354 | -0.018311 | 121.7834 | 121.843 | 121.7331 | 0.2655 | 0.15564 | 0.18768 | 0.050354 | 0.20599 | 0.16937 | 0.14191 | 0.13733 | 121.7468 | 121.7148 | -0.16022 | -0.18768 | 121.6553 | 121.7468 | 121.6003 | 121.4584
576.3906 | 121.9208 | -121.6507 | 0.16937 | -0.0036622 | 0.062515 | 0.012262 | 0.015635 | -0.0025442 | -0.0010468 | -0.0016513 | -0.0076599 | 0.0030719 | 0.018634 | -0.0088119 | -0.0054367 | 0.019452 | 2.068e-06 | -0.013733 | 0.14648 | -0.027466 | 0 | 0.15106 | 0.041199 | 0.045776 | -0.18768 | 0.13275 | -0.036621 | 0.054932 | 0.13733 | 0.059509 | 0.19226 | 121.6232 | -0.022889 | -0.16937 | 121.8018 | 121.6965 | 121.6919 | 0.073242 | 0.068665 | 121.6141 | -0.036622 | -0.11444 | 121.788 | 121.843 | 121.7102 | 0.22888 | 0.09613 | 0.17853 | 0.027466 | 0.17395 | 0.091553 | 0.17395 | 0.16937 | 121.7972 | 121.7834 | -0.19684 | -0.20599 | 121.6507 | 121.7056 | 121.637 | 121.463
578.125 | 122.0032 | -121.6141 | 0.16479 | -0.011291 | 0.063156 | 0.012689 | 0.015208 | -0.0010488 | -0.00061944 | -0.0020785 | -0.0076599 | 0.00029486 | 0.018848 | -0.0049667 | -0.00095065 | 0.018171 | 0.0027793 | 0.027466 | 0.09613 | 0.022888 | 0.082397 | 0.22888 | 0.086975 | 0.10529 | -0.15106 | 0.086975 | -0.004578 | 0.14191 | 0.20599 | 0.12817 | 0.23804 | 121.637 | -0.068665 | -0.082398 | 121.843 | 121.7194 | 121.701 | 0.082398 | 0.064087 | 121.6095 | -0.07782 | -0.022888 | 121.8201 | 121.8521 | 121.7422 | 0.24261 | 0.13275 | 0.20599 | 0.059509 | 0.21057 | 0.14649 | 0.073242 | 0.091553 | 121.7102 | 121.701 | -0.14191 | -0.16937 | 121.6965 | 121.756 | 121.6415 | 121.463
579.8594 | 121.994 | -121.6324 | 0.14191 | -0.0036622 | 0.062087 | 0.013757 | 0.016917 | 0.00087375 | -0.00040584 | 0.00069849 | -0.010712 | 0.0022175 | 0.019916 | -0.0015487 | -0.0041551 | 0.01753 | 0.0012839 | -0.004578 | 0.10986 | -0.013733 | 0.045776 | 0.20142 | 0.09613 | 0.11902 | -0.15106 | 0.11902 | -0.022888 | 0.12817 | 0.21515 | 0.15106 | 0.24261 | 121.6187 | -0.032044 | -0.096131 | 121.8338 | 121.7514 | 121.7285 | 0.13275 | 0.10986 | 121.6095 | -0.022888 | -0.013733 | 121.8475 | 121.875 | 121.7834 | 0.2655 | 0.17395 | 0.21515 | 0.059509 | 0.23804 | 0.15106 | 0.1236 | 0.14191 | 121.7422 | 121.7514 | -0.15564 | -0.16479 | 121.6782 | 121.7606 | 121.6278 | 121.4813
581.5938 | 121.9574 | -121.6187 | 0.16022 | 0.0039673 | 0.062942 | 0.014398 | 0.018199 | 0.0027964 | 2.1362e-05 | 5.7688e-05 | -0.0046081 | 0.0028583 | 0.017994 | -0.0034713 | -0.0030869 | 0.015394 | 0.00085667 | -0.022888 | 0.14648 | -0.045776 | 0 | 0.11902 | -0.004578 | 0.041199 | -0.24261 | 0.13275 | -0.027466 | 0.091553 | 0.14191 | 0.086975 | 0.21515 | 121.5729 | -0.013733 | -0.16022 | 121.7377 | 121.6599 | 121.6141 | 0.086975 | 0.041198 | 121.5912 | -0.027466 | -0.068664 | 121.7606 | 121.8338 | 121.7056 | 0.24261 | 0.11444 | 0.16479 | 0.045776 | 0.16937 | 0.11902 | 0.19226 | 0.16022 | 121.7651 | 121.7514 | -0.20599 | -0.18768 | 121.6187 | 121.7102 | 121.5958 | 121.376
583.2812 | 121.9849 | -121.6049 | 0.14191 | 0.0039673 | 0.062301 | 0.016534 | 0.017344 | -0.0019034 | -0.002542 | -0.0016513 | -0.0015565 | 0.0022175 | 0.017353 | -0.0041123 | 0.00011755 | 0.019239 | 0.00064307 | 0.022888 | 0.11444 | -0.018311 | 0.091553 | 0.21973 | 0.086975 | 0.10986 | -0.14648 | 0.11444 | -0.004578 | 0.14648 | 0.21057 | 0.14648 | 0.25177 | 121.5866 | -0.027466 | -0.050354 | 121.8246 | 121.7148 | 121.6919 | 0.12817 | 0.10529 | 121.6003 | -0.027466 | 0.004577 | 121.8155 | 121.8567 | 121.7514 | 0.25635 | 0.15106 | 0.23804 | 0.10986 | 0.21515 | 0.15106 | 0.13275 | 0.11902 | 121.7194 | 121.7194 | -0.16022 | -0.14649 | 121.6965 | 121.7514 | 121.6278 | 121.4584
585.0312 | 121.9208 | -121.6599 | 0.17395 | -0.018921 | 0.062515 | 0.013757 | 0.017771 | 0.0010874 | -0.0012604 | -0.0018649 | -0.0015565 | 0.0022175 | 0.02013 | -0.0064621 | -0.0047959 | 0.016462 | -0.0023477 | 0 | 0.14191 | -0.022888 | 0.027466 | 0.16479 | 0.059509 | 0.064087 | -0.082397 | 0.14191 | -0.036621 | 0.07782 | 0.1236 | 0.068665 | 0.17853 | 121.637 | -0.032043 | -0.14648 | 121.8246 | 121.7239 | 121.7194 | 0.086975 | 0.082397 | 121.6232 | -0.032043 | -0.09613 | 121.7834 | 121.8384 | 121.7285 | 0.21515 | 0.10529 | 0.18768 | 0.050354 | 0.16022 | 0.11444 | 0.16479 | 0.17853 | 121.8018 | 121.8018 | -0.19684 | -0.21057 | 121.6873 | 121.7377 | 121.6599 | 121.5775
586.7031 | 121.9116 | -121.6644 | 0.17853 | -0.018921 | 0.062301 | 0.014398 | 0.01649 | 0.00087375 | -0.0019012 | 0.00027129 | -0.0015565 | 0.00093566 | 0.018634 | -0.0079575 | -0.0028733 | 0.017103 | -0.0019205 | -0.004578 | 0.15106 | -0.009155 | 0.041199 | 0.16937 | 0.064087 | 0.07782 | -0.21515 | 0.14191 | -0.032043 | 0.082397 | 0.1236 | 0.036621 | 0.17395 | 121.6553 | -0.027466 | -0.13733 | 121.8338 | 121.7422 | 121.7285 | 0.086975 | 0.073242 | 121.6324 | -0.036621 | -0.096131 | 121.788 | 121.8384 | 121.701 | 0.20599 | 0.068664 | 0.17853 | 0.050354 | 0.15564 | 0.11444 | 0.16022 | 0.17395 | 121.8155 | 121.8063 | -0.18768 | -0.21057 | 121.7056 | 121.7468 | 121.6599 | 121.4493
588.4375 | 121.9162 | -121.6461 | 0.17853 | 0.0039673 | 0.063369 | 0.013971 | 0.015849 | 0.00066015 | -0.0033966 | -0.0020785 | -0.0046081 | 0.0032855 | 0.016925 | -0.0058213 | -0.0035141 | 0.015821 | -0.0034159 | -0.022888 | 0.13733 | -0.022888 | 0.027466 | 0.16937 | 0.054932 | 0.064087 | -0.11444 | 0.12817 | -0.045776 | 0.082397 | 0.14191 | 0.068665 | 0.17853 | 121.6232 | -0.041199 | -0.15106 | 121.8155 | 121.7102 | 121.701 | 0.086975 | 0.07782 | 121.6003 | -0.050354 | -0.096131 | 121.788 | 121.8246 | 121.7148 | 0.2243 | 0.11444 | 0.19226 | 0.050354 | 0.18768 | 0.12817 | 0.16022 | 0.17395 | 121.7834 | 121.7743 | -0.20142 | -0.2243 | 121.6736 | 121.7285 | 121.6232 | 121.5317
590.1719 | 121.9757 | -121.6232 | 0.16022 | -0.011291 | 0.059951 | 0.01568 | 0.01414 | -0.003826 | -0.0010468 | -0.0044285 | -0.0015565 | -0.0012005 | 0.019275 | 0.0018693 | -0.0030869 | 0.018598 | -0.0021341 | -0.027466 | 0.1236 | -0.018311 | 0.036621 | 0.18768 | 0.082397 | 0.10071 | -0.11444 | 0.10986 | -0.050354 | 0.10529 | 0.19226 | 0.13733 | 0.2243 | 121.6049 | -0.036621 | -0.1236 | 121.8109 | 121.7239 | 121.7056 | 0.11902 | 0.10071 | 121.5729 | -0.050354 | -0.054931 | 121.8155 | 121.8475 | 121.7606 | 0.27466 | 0.18768 | 0.20599 | 0.054932 | 0.24261 | 0.15564 | 0.14191 | 0.16022 | 121.7468 | 121.7331 | -0.17853 | -0.21057 | 121.6599 | 121.7285 | 121.5958 | 121.5088
591.9219 | 121.8796 | -121.6736 | 0.19684 | -0.0036622 | 0.062728 | 0.011835 | 0.014781 | -0.00019445 | -0.003183 | -0.0012241 | -0.0046081 | 0.0020039 | 0.015857 | -0.0045395 | -0.0071457 | 0.016034 | -0.0025613 | -0.009155 | 0.11902 | -0.009155 | 0.022888 | 0.16937 | 0.082397 | 0.073242 | -0.16022 | 0.14191 | -0.054932 | 0.027466 | 0.10071 | 0.036621 | 0.13733 | 121.6644 | -0.077819 | -0.17395 | 121.843 | 121.7468 | 121.756 | 0.082397 | 0.091552 | 121.6187 | -0.054931 | -0.16937 | 121.7743 | 121.8109 | 121.7102 | 0.19226 | 0.091553 | 0.17853 | 0.032043 | 0.15564 | 0.082398 | 0.12817 | 0.19684 | 121.7926 | 121.8155 | -0.20599 | -0.25177 | 121.6965 | 121.7011 | 121.6644 | 121.5134
593.6094 | 121.875 | -121.6782 | 0.17853 | -0.0036622 | 0.062515 | 0.013757 | 0.017771 | 0.00087375 | -0.002542 | 0.0030483 | 0.0014953 | 0.0032855 | 0.022266 | -0.0068893 | -9.605e-05 | 0.016889 | -0.00021153 | -0.045776 | 0.15564 | -0.050354 | -0.050354 | 0.07782 | -0.027466 | 0 | -0.20599 | 0.15106 | -0.064087 | 0.027466 | 0.050354 | -0.009155 | 0.13275 | 121.6278 | -0.022888 | -0.22888 | 121.756 | 121.6782 | 121.6507 | 0.050354 | 0.022888 | 121.6141 | -0.027466 | -0.15106 | 121.7285 | 121.8109 | 121.669 | 0.19684 | 0.054932 | 0.12817 | 0 | 0.11444 | 0.091553 | 0.20599 | 0.21515 | 121.8338 | 121.8292 | -0.22888 | -0.24261 | 121.6278 | 121.7056 | 121.6324 | 121.4722
595.3438 | 121.8704 | -121.6782 | 0.18768 | -0.0036622 | 0.062301 | 0.014185 | 0.017985 | 0.0021556 | -0.0019012 | -0.00036951 | 0.0014953 | 0.0039265 | 0.018421 | -0.0047531 | -0.0054367 | 0.014325 | -0.0025613 | 0.013733 | 0.15106 | -0.036621 | 0.009155 | 0.15106 | 0.041199 | 0.059509 | -0.13275 | 0.16022 | -0.064087 | 0.054932 | 0.09613 | -0.004578 | 0.13733 | 121.6415 | -0.036621 | -0.17853 | 121.8292 | 121.7377 | 121.7194 | 0.09613 | 0.07782 | 121.6141 | -0.027466 | -0.13275 | 121.7743 | 121.8155 | 121.6736 | 0.20142 | 0.059509 | 0.18768 | 0.045776 | 0.16022 | 0.11902 | 0.18768 | 0.2243 | 121.8292 | 121.8384 | -0.2243 | -0.25177 | 121.6873 | 121.7331 | 121.6919 | 121.5454
597.0938 | 121.9299 | -121.6461 | 0.1831 | -0.018921 | 0.062942 | 0.014398 | 0.016703 | -0.00040805 | -0.0029694 | -0.0014377 | -0.0015565 | 0.0039265 | 0.017566 | -0.0015487 | -0.0020187 | 0.017103 | -0.0019205 | 0.009155 | 0.14648 | -0.013733 | 0.022888 | 0.15564 | 0.041199 | 0.059509 | -0.1236 | 0.12817 | -0.041199 | 0.082397 | 0.11902 | 0.050354 | 0.16937 | 121.6324 | -0.036621 | -0.16022 | 121.8018 | 121.7056 | 121.6873 | 0.073242 | 0.054932 | 121.6049 | -0.054931 | -0.10071 | 121.7651 | 121.8155 | 121.6965 | 0.21057 | 0.091553 | 0.16937 | 0.036621 | 0.16022 | 0.1236 | 0.16022 | 0.16937 | 121.7926 | 121.7743 | -0.19684 | -0.2243 | 121.669 | 121.7285 | 121.6553 | 121.5225
598.7812 | 121.8887 | -121.6461 | 0.1831 | -0.0036622 | 0.06401 | 0.014185 | 0.016276 | 0.0019418 | -0.0038238 | 0.00069849 | -0.0015565 | 0.0020039 | 0.019062 | -0.010307 | -0.0022325 | 0.018812 | -0.0019205 | -0.036621 | 0.16479 | -0.027466 | -0.045776 | 0.073242 | -0.032043 | 0 | -0.21515 | 0.15106 | -0.068665 | 0.022888 | 0.045776 | -0.013733 | 0.14191 | 121.6187 | -0.01831 | -0.22888 | 121.7194 | 121.6461 | 121.6141 | 0.027466 | -0.004577 | 121.5775 | -0.032043 | -0.16022 | 121.6919 | 121.788 | 121.6324 | 0.21057 | 0.054932 | 0.10071 | -0.01831 | 0.11444 | 0.091553 | 0.19226 | 0.21973 | 121.8109 | 121.7972 | -0.21057 | -0.25177 | 121.6003 | 121.669 | 121.6095 | 121.431
600.5156 | 121.9254 | -121.6873 | 0.17853 | -0.018921 | 0.06166 | 0.011621 | 0.015849 | -0.0044668 | -0.0040374 | 0.00048489 | -0.0046081 | 0.0020039 | 0.017566 | -0.0092391 | -0.0045823 | 0.016889 | -0.00063873 | -0.009155 | 0.14648 | -0.032043 | 0 | 0.14648 | 0.054932 | 0.050354 | -0.12817 | 0.15106 | -0.045776 | 0.073242 | 0.13733 | 0.064087 | 0.17853 | 121.6553 | -0.032044 | -0.17853 | 121.8338 | 121.7377 | 121.7422 | 0.082397 | 0.086975 | 121.6415 | -0.027466 | -0.10529 | 121.8246 | 121.8658 | 121.7514 | 0.2243 | 0.10986 | 0.17853 | 0.032043 | 0.18311 | 0.11902 | 0.17853 | 0.19684 | 121.8338 | 121.8384 | -0.21057 | -0.2243 | 121.6873 | 121.7606 | 121.6782 | 121.5591
602.25 | 121.962 | -121.6278 | 0.15106 | -0.02655 | 0.058242 | 0.014612 | 0.013499 | 0.0036508 | -0.00019224 | -0.0050693 | -0.0046081 | 8.1264e-05 | 0.018207 | -0.0024033 | -0.0013779 | 0.01988 | -0.0029885 | 0.009155 | 0.10986 | 0.013733 | 0.073242 | 0.22888 | 0.086975 | 0.10986 | -0.050354 | 0.11444 | -0.009155 | 0.13733 | 0.19226 | 0.11902 | 0.21515 | 121.6415 | -0.041199 | -0.07782 | 121.8567 | 121.7377 | 121.7148 | 0.09613 | 0.073242 | 121.6187 | -0.036621 | -0.013733 | 121.8201 | 121.843 | 121.7468 | 0.2243 | 0.12817 | 0.21515 | 0.059509 | 0.20142 | 0.14648 | 0.09613 | 0.1236 | 121.7377 | 121.7422 | -0.13733 | -0.16022 | 121.701 | 121.7651 | 121.637 | 121.5775
604 | 121.875 | -121.669 | 0.20142 | -0.011291 | 0.062515 | 0.016107 | 0.01649 | 0.0032236 | -0.00083304 | -0.00058311 | -0.0046081 | 0.0030719 | 0.019275 | -0.0015487 | -0.0056503 | 0.018598 | -0.0014931 | -0.013733 | 0.16022 | -0.036621 | -0.009155 | 0.11444 | -0.013733 | 0.027466 | -0.16937 | 0.13733 | -0.041199 | 0.013733 | 0.059509 | -0.009155 | 0.12817 | 121.6324 | -0.041199 | -0.21057 | 121.7834 | 121.6965 | 121.6553 | 0.064087 | 0.022888 | 121.6278 | -0.064087 | -0.18768 | 121.7285 | 121.7972 | 121.6599 | 0.16937 | 0.032044 | 0.15106 | 0.027466 | 0.10071 | 0.054932 | 0.19684 | 0.17853 | 121.8292 | 121.8063 | -0.23804 | -0.24262 | 121.6599 | 121.6827 | 121.6553 | 121.4996
605.6875 | 122.0169 | -121.6278 | 0.15106 | -0.0036622 | 0.060165 | 0.014398 | 0.017344 | 0.00044655 | -0.003183 | -0.0020785 | 0.0014953 | 0.0013629 | 0.018207 | 0.0020829 | -0.00073705 | 0.018598 | -0.0019205 | 0.009155 | 0.11444 | -0.004578 | 0.07782 | 0.20142 | 0.091553 | 0.11444 | -0.059509 | 0.11444 | -0.027466 | 0.15564 | 0.19684 | 0.13733 | 0.26093 | 121.6232 | -0.036621 | -0.073242 | 121.8292 | 121.7422 | 121.7194 | 0.11902 | 0.096131 | 121.6003 | -0.036621 | 0.004578 | 121.8246 | 121.8887 | 121.7651 | 0.28839 | 0.16479 | 0.20599 | 0.082398 | 0.2243 | 0.18311 | 0.11902 | 0.14191 | 121.7422 | 121.7422 | -0.15564 | -0.17853 | 121.7056 | 121.7834 | 121.637 | 121.5683
607.4219 | 122.0123 | -121.6187 | 0.14191 | -0.0036622 | 0.063156 | 0.014185 | 0.016703 | 0.00087375 | -0.0023284 | -0.0027195 | -0.0046081 | 0.0028583 | 0.016925 | -0.0032577 | 0.0011855 | 0.018384 | 0.00085667 | 0.041199 | 0.11444 | 0.009155 | 0.09613 | 0.23346 | 0.091553 | 0.11902 | -0.027466 | 0.086975 | -0.013733 | 0.16022 | 0.19226 | 0.14191 | 0.25177 | 121.6278 | -0.027466 | -0.045777 | 121.8521 | 121.7377 | 121.7102 | 0.10986 | 0.082398 | 121.6049 | -0.054932 | 0.01831 | 121.8109 | 121.8704 | 121.7606 | 0.2655 | 0.15564 | 0.2243 | 0.086975 | 0.20599 | 0.17395 | 0.10529 | 0.10071 | 121.7331 | 121.7056 | -0.13275 | -0.15564 | 121.7148 | 121.7789 | 121.6599 | 121.5912
609.1094 | 122.0078 | -121.6232 | 0.15106 | -0.0036622 | 0.060806 | 0.011408 | 0.015422 | -0.00019445 | -0.0033966 | -0.0016513 | -0.0015565 | 0.00093566 | 0.01778 | 0.0027237 | -0.0022325 | 0.019239 | 0.0017111 | 0.032043 | 0.11444 | 0.004578 | 0.086975 | 0.27008 | 0.13733 | 0.15564 | -0.004578 | 0.09613 | -0.032043 | 0.15564 | 0.23346 | 0.16479 | 0.25177 | 121.6278 | -0.036621 | -0.064087 | 121.8933 | 121.7789 | 121.7606 | 0.15106 | 0.13275 | 121.5912 | -0.054932 | 0.004578 | 121.8567 | 121.875 | 121.788 | 0.28381 | 0.19684 | 0.2655 | 0.082397 | 0.2655 | 0.18768 | 0.10986 | 0.12817 | 121.7377 | 121.7194 | -0.14648 | -0.18311 | 121.7102 | 121.7789 | 121.6553 | 121.6187
610.8438 | 121.9757 | -121.6461 | 0.15564 | -0.018921 | 0.061019 | 0.013544 | 0.015422 | 0.00044655 | -0.0029694 | -0.0046421 | 0.0014953 | -0.00013254 | 0.017566 | -0.0019759 | -0.0054367 | 0.017743 | 0.00064307 | -0.009155 | 0.12817 | 0.013733 | 0.018311 | 0.17853 | 0.068665 | 0.10071 | -0.11902 | 0.12817 | -0.032043 | 0.11902 | 0.15564 | 0.1236 | 0.21057 | 121.6599 | -0.027466 | -0.13733 | 121.8246 | 121.7468 | 121.7148 | 0.086975 | 0.054932 | 121.6141 | -0.027466 | -0.036621 | 121.8018 | 121.8567 | 121.7697 | 0.24261 | 0.15564 | 0.16479 | 0.004578 | 0.18768 | 0.15106 | 0.11444 | 0.16022 | 121.7743 | 121.7743 | -0.14191 | -0.18768 | 121.6644 | 121.7651 | 121.637 | 121.5271
612.5781 | 121.9574 | -121.6415 | 0.16937 | -0.011291 | 0.060165 | 0.013544 | 0.013285 | -0.0040396 | -0.0040374 | -0.0052829 | -0.0076599 | 0.0013629 | 0.017994 | 0.0027237 | -0.0060777 | 0.017103 | 0.0021383 | -0.009155 | 0.11902 | 0 | 0.018311 | 0.14191 | 0.050354 | 0.086975 | -0.10071 | 0.11902 | -0.027466 | 0.10071 | 0.16022 | 0.1236 | 0.21057 | 121.6415 | -0.050354 | -0.15106 | 121.7834 | 121.7285 | 121.6919 | 0.086975 | 0.050354 | 121.6141 | -0.050354 | -0.068665 | 121.8018 | 121.8521 | 121.7651 | 0.23804 | 0.15106 | 0.14191 | 0.018311 | 0.18768 | 0.12817 | 0.11902 | 0.14649 | 121.7606 | 121.7606 | -0.16937 | -0.19684 | 121.6599 | 121.7422 | 121.6324 | 121.5408
614.25 | 121.8842 | -121.669 | 0.18768 | -0.0036622 | 0.063796 | 0.01333 | 0.017558 | 0.0049326 | -0.0023284 | -0.0025057 | -0.0076599 | 0.0015765 | 0.020771 | -0.0066757 | -0.0033005 | 0.017957 | -0.0049111 | -0.013733 | 0.16479 | -0.013733 | -0.013733 | 0.11902 | -0.013733 | 0 | -0.17395 | 0.17395 | -0.032043 | 0.018311 | 0.068665 | 0 | 0.15106 | 121.6553 | -0.022888 | -0.20142 | 121.788 | 121.669 | 121.6553 | 0.013733 | 0 | 121.637 | -0.013733 | -0.16937 | 121.7377 | 121.8201 | 121.669 | 0.18311 | 0.032043 | 0.13275 | 0 | 0.10071 | 0.050354 | 0.17853 | 0.20599 | 121.8338 | 121.843 | -0.20142 | -0.21973 | 121.6553 | 121.6873 | 121.6553 | 121.4951
615.9844 | 121.8979 | -121.6553 | 0.1831 | 0.0039673 | 0.063156 | 0.013116 | 0.016062 | 0.0010874 | -0.00083304 | -0.0040011 | 0.0014953 | 0.0041401 | 0.018848 | -0.0034713 | 0.00011755 | 0.016675 | -0.00063873 | -0.036621 | 0.17395 | -0.036621 | -0.041199 | 0.082397 | -0.022888 | 0.018311 | -0.16937 | 0.16479 | -0.054932 | 0.045776 | 0.07782 | 0.013733 | 0.17395 | 121.6187 | -0.009155 | -0.2243 | 121.7377 | 121.6736 | 121.6324 | 0.054932 | 0.013733 | 121.6003 | -0.01831 | -0.13733 | 121.7331 | 121.8292 | 121.669 | 0.22888 | 0.068665 | 0.11902 | -0.004578 | 0.13275 | 0.10071 | 0.21057 | 0.21973 | 121.8292 | 121.8201 | -0.21973 | -0.23804 | 121.6141 | 121.701 | 121.6187 | 121.4859
617.7344 | 121.8933 | -121.701 | 0.18768 | -0.0036622 | 0.059738 | 0.012476 | 0.016703 | 0.0017282 | -0.0036102 | -0.0025057 | -0.0015565 | 0.0017901 | 0.020343 | -0.0047531 | -0.0033005 | 0.016034 | 0.00064307 | -0.036621 | 0.16022 | -0.032043 | -0.032043 | 0.086975 | -0.022888 | 0.013733 | -0.18768 | 0.16022 | -0.041199 | 0.050354 | 0.091553 | 0.013733 | 0.16022 | 121.669 | -0.027466 | -0.21973 | 121.788 | 121.7148 | 121.6782 | 0.045776 | 0.009155 | 121.6599 | -0.027466 | -0.13733 | 121.7926 | 121.8613 | 121.7148 | 0.20142 | 0.054932 | 0.11902 | 0 | 0.13275 | 0.091553 | 0.19226 | 0.20142 | 121.8613 | 121.8613 | -0.21973 | -0.22888 | 121.669 | 121.7514 | 121.6644 | 121.5134
619.4844 | 122.0032 | -121.6141 | 0.14648 | -0.0036622 | 0.060379 | 0.014398 | 0.013926 | 0.001301 | -0.0027556 | -0.00015591 | 0.0014953 | 0.00093566 | 0.017566 | -0.0017623 | -0.00030965 | 0.018384 | 0.0032065 | -0.004578 | 0.13275 | 0 | 0.050354 | 0.18768 | 0.054932 | 0.09613 | -0.09613 | 0.11902 | -0.013733 | 0.15106 | 0.20142 | 0.11902 | 0.25177 | 121.6141 | -0.013733 | -0.09613 | 121.8018 | 121.7102 | 121.669 | 0.09613 | 0.054932 | 121.6003 | -0.027465 | 0.004578 | 121.8155 | 121.8658 | 121.7331 | 0.2655 | 0.13275 | 0.18768 | 0.050354 | 0.21515 | 0.16479 | 0.13275 | 0.13275 | 121.7468 | 121.7331 | -0.14648 | -0.16022 | 121.6644 | 121.7651 | 121.6095 | 121.5179
621.1562 | 122.0123 | -121.6049 | 0.13733 | -0.018921 | 0.061233 | 0.015039 | 0.014994 | 0.00066015 | -0.001474 | -0.0012241 | -0.010712 | 0.00050846 | 0.018421 | 0.0031509 | -0.0041551 | 0.021161 | -0.0027749 | 0.041199 | 0.09613 | 0.013733 | 0.086975 | 0.23804 | 0.07782 | 0.11444 | 0.14191 | 0.082397 | -0.004578 | 0.16479 | 0.20599 | 0.14648 | 0.25177 | 121.6187 | -0.041199 | -0.050354 | 121.843 | 121.7194 | 121.6827 | 0.10071 | 0.064087 | 121.6003 | -0.054932 | 0.027466 | 121.8109 | 121.8567 | 121.7514 | 0.25635 | 0.15106 | 0.2243 | 0.073242 | 0.21057 | 0.16937 | 0.082397 | 0.086975 | 121.701 | 121.6873 | -0.1236 | -0.14191 | 121.6919 | 121.7697 | 121.6461 | 121.7468
622.9062 | 121.9711 | -121.6507 | 0.16479 | -0.0036622 | 0.061019 | 0.015894 | 0.014353 | 0.0023692 | -0.003183 | -0.0020785 | -0.0015565 | -0.00098694 | 0.019062 | -0.0092391 | -0.0054367 | 0.017957 | -0.0012795 | 0.045776 | 0.10529 | 0.009155 | 0.091553 | 0.24719 | 0.14191 | 0.14648 | 0.11902 | 0.12817 | -0.009155 | 0.11444 | 0.19226 | 0.13275 | 0.20142 | 121.6599 | -0.059509 | -0.073242 | 121.8979 | 121.7972 | 121.7926 | 0.13733 | 0.13275 | 121.6415 | -0.036621 | -0.050354 | 121.843 | 121.8521 | 121.7834 | 0.21057 | 0.14191 | 0.23804 | 0.082398 | 0.20142 | 0.1236 | 0.096131 | 0.13733 | 121.756 | 121.7789 | -0.15564 | -0.17395 | 121.7422 | 121.7651 | 121.6965 | 121.7697
624.5781 | 121.962 | -121.6644 | 0.16022 | -0.011291 | 0.060592 | 0.014185 | 0.013926 | 0.0025828 | -0.0027556 | -0.0025057 | -0.0046081 | 0.0020039 | 0.019062 | -0.0053939 | -0.0041551 | 0.01753 | -0.0042703 | -0.009155 | 0.13733 | 0.009155 | 0.022888 | 0.16479 | 0.054932 | 0.073242 | 0.050354 | 0.13275 | -0.022888 | 0.086975 | 0.16479 | 0.10071 | 0.21515 | 121.6736 | -0.022888 | -0.13733 | 121.8292 | 121.7377 | 121.7194 | 0.064087 | 0.045777 | 121.6415 | -0.027466 | -0.073242 | 121.8292 | 121.8796 | 121.7651 | 0.23804 | 0.1236 | 0.15564 | 0.013733 | 0.18768 | 0.10986 | 0.12817 | 0.15564 | 121.8018 | 121.7972 | -0.15106 | -0.1831 | 121.6873 | 121.7514 | 121.6553 | 121.7148
626.3125 | 121.9391 | -121.6461 | 0.17853 | -0.018921 | 0.061233 | 0.014185 | 0.016917 | 0.0034372 | -0.0046782 | -0.0031467 | -0.010712 | 0.0045673 | 0.019062 | 0.0029373 | -0.0039413 | 0.017743 | -0.00063873 | 0.013733 | 0.14648 | -0.013733 | 0.036621 | 0.16479 | 0.045776 | 0.054932 | 0.064087 | 0.14648 | -0.041199 | 0.07782 | 0.14191 | 0.059509 | 0.19226 | 121.6324 | -0.032044 | -0.14191 | 121.8109 | 121.701 | 121.6919 | 0.068665 | 0.059509 | 121.6049 | -0.032044 | -0.10071 | 121.788 | 121.8384 | 121.7056 | 0.23346 | 0.10071 | 0.17853 | 0.050354 | 0.18311 | 0.11902 | 0.16022 | 0.18768 | 121.7926 | 121.7926 | -0.19226 | -0.21973 | 121.6827 | 121.7239 | 121.6599 | 121.7102
628 | 122.0123 | -121.6232 | 0.15564 | -0.018921 | 0.059524 | 0.016962 | 0.014781 | 0.0038644 | -0.0040374 | -0.0020785 | -0.0046081 | -0.00013254 | 0.019062 | -0.00069433 | -0.00052345 | 0.018812 | -0.00021153 | 0.022888 | 0.10529 | 0.027466 | 0.11444 | 0.23804 | 0.082397 | 0.11444 | 0.14648 | 0.10529 | 0.004578 | 0.16937 | 0.23804 | 0.15106 | 0.25635 | 121.6507 | -0.050354 | -0.041199 | 121.8613 | 121.7377 | 121.7056 | 0.086975 | 0.054931 | 121.6278 | -0.050354 | 0.013733 | 121.8613 | 121.8796 | 121.7743 | 0.25177 | 0.14648 | 0.21057 | 0.086975 | 0.23346 | 0.16479 | 0.07782 | 0.10071 | 121.7285 | 121.7285 | -0.12817 | -0.15106 | 121.7377 | 121.7926 | 121.6461 | 121.7697
629.7344 | 122.0078 | -121.6278 | 0.15106 | -0.0036622 | 0.058456 | 0.014398 | 0.015635 | -0.0010488 | -0.00083304 | -0.0014377 | -0.0015565 | 0.0024311 | 0.019275 | 0.0020829 | -0.0018051 | 0.018598 | -0.0010659 | -0.013733 | 0.15564 | -0.032043 | 0.036621 | 0.15564 | 0.036621 | 0.07782 | 0.082397 | 0.1236 | -0.009155 | 0.13275 | 0.18768 | 0.10986 | 0.24261 | 121.5958 | 0.004578 | -0.11444 | 121.7834 | 121.7056 | 121.6644 | 0.10986 | 0.068664 | 121.6187 | -0.027466 | -0.018311 | 121.8155 | 121.8704 | 121.7377 | 0.25177 | 0.11902 | 0.18768 | 0.068664 | 0.19684 | 0.14191 | 0.18768 | 0.13275 | 121.7834 | 121.7514 | -0.18311 | -0.16022 | 121.6644 | 121.7606 | 121.6141 | 121.7102
631.4062 | 122.0032 | -121.6278 | 0.14648 | 0.0039673 | 0.058242 | 0.013757 | 0.013713 | -0.00019445 | -0.0023284 | -0.0018649 | -0.0046081 | 0.0017901 | 0.018634 | 0.0025101 | -9.605e-05 | 0.018384 | -0.0023477 | -0.013733 | 0.13275 | -0.009155 | 0.036621 | 0.17853 | 0.041199 | 0.091553 | 0.10986 | 0.1236 | 0 | 0.14648 | 0.1831 | 0.11444 | 0.25635 | 121.6187 | -0.013733 | -0.10986 | 121.8063 | 121.7194 | 121.669 | 0.10071 | 0.050354 | 121.6278 | -0.022888 | 0 | 121.8109 | 121.8842 | 121.7422 | 0.25635 | 0.11444 | 0.18768 | 0.045776 | 0.1831 | 0.14648 | 0.14191 | 0.1236 | 121.7606 | 121.7514 | -0.15564 | -0.14648 | 121.6644 | 121.7743 | 121.6141 | 121.7377
633.0938 | 122.0215 | -121.637 | 0.16022 | -0.0036622 | 0.059951 | 0.015466 | 0.015422 | 1.915e-05 | -0.0012604 | -0.0016513 | 0.0014953 | -0.00013254 | 0.017353 | -0.0047531 | 0.00054475 | 0.018384 | -0.00063873 | 0.050354 | 0.12817 | 0.013733 | 0.10529 | 0.22888 | 0.086975 | 0.10529 | 0.14648 | 0.10986 | 0.004578 | 0.16479 | 0.21973 | 0.15106 | 0.25177 | 121.6507 | -0.032043 | -0.054931 | 121.8658 | 121.7422 | 121.7239 | 0.091553 | 0.073242 | 121.6415 | -0.050354 | 0.004578 | 121.8567 | 121.8887 | 121.788 | 0.24719 | 0.14648 | 0.21515 | 0.091553 | 0.21515 | 0.16022 | 0.11444 | 0.10529 | 121.7651 | 121.7468 | -0.14648 | -0.15564 | 121.7422 | 121.8018 | 121.6873 | 121.7834
634.8438 | 121.9528 | -121.6507 | 0.16022 | -0.0036622 | 0.059524 | 0.016107 | 0.015635 | 0.0025828 | -0.001474 | -0.0033603 | 0.0014953 | 0.0030719 | 0.018848 | -0.0041123 | -0.0022325 | 0.019452 | -0.0010659 | -0.022888 | 0.15106 | -0.027466 | -0.009155 | 0.10529 | -0.004578 | 0.022888 | 0.036621 | 0.11902 | -0.027466 | 0.091553 | 0.13275 | 0.073242 | 0.21515 | 121.6232 | -0.009155 | -0.16937 | 121.756 | 121.6736 | 121.6461 | 0.050354 | 0.022888 | 121.6232 | -0.041198 | -0.068664 | 121.7834 | 121.8658 | 121.7239 | 0.24261 | 0.10071 | 0.13275 | 0.018311 | 0.16022 | 0.11902 | 0.17853 | 0.14649 | 121.8018 | 121.7697 | -0.18768 | -0.18768 | 121.6415 | 121.7422 | 121.6278 | 121.6873
636.5156 | 121.9528 | -121.6736 | 0.16937 | 0.0039673 | 0.057174 | 0.01098 | 0.01414 | 0.0023692 | -0.002542 | -0.0020785 | -0.0015565 | 0.0034991 | 0.019489 | -0.0068893 | -0.0011643 | 0.018384 | 0.00064307 | -0.013733 | 0.14648 | -0.041199 | -0.009155 | 0.1236 | -0.013733 | 0.041199 | 0.022888 | 0.14648 | -0.009155 | 0.10986 | 0.16022 | 0.068665 | 0.21057 | 121.6324 | -0.022889 | -0.17853 | 121.7972 | 121.7148 | 121.6599 | 0.082398 | 0.027466 | 121.6644 | -0.022889 | -0.05951 | 121.8338 | 121.8842 | 121.7422 | 0.21973 | 0.07782 | 0.16479 | 0.032044 | 0.16937 | 0.11902 | 0.18768 | 0.15564 | 121.8201 | 121.8201 | -0.21057 | -0.17853 | 121.6644 | 121.7834 | 121.6599 | 121.6965
638.2656 | 122.0352 | -121.6415 | 0.13275 | -0.011291 | 0.056961 | 0.013544 | 0.01179 | -0.0010488 | -0.0021148 | -0.0012241 | -0.0076599 | -0.00034614 | 0.020771 | -0.0034713 | -0.00095065 | 0.017957 | -0.0010659 | 0.045776 | 0.10529 | 0.027466 | 0.086975 | 0.2243 | 0.082397 | 0.11902 | 0.13733 | 0.10071 | 0.022888 | 0.14648 | 0.23346 | 0.16479 | 0.24261 | 121.669 | -0.027465 | -0.045776 | 121.8658 | 121.7606 | 121.7239 | 0.091553 | 0.054931 | 121.6644 | -0.032043 | 0.013733 | 121.875 | 121.8842 | 121.8063 | 0.21973 | 0.14191 | 0.19684 | 0.059509 | 0.21057 | 0.1236 | 0.07782 | 0.07782 | 121.7468 | 121.7422 | -0.10529 | -0.10986 | 121.7285 | 121.788 | 121.6873 | 121.7789
640 | 121.8887 | -121.7285 | 0.19684 | -0.011291 | 0.057601 | 0.014398 | 0.013499 | 0.00066015 | -0.0044646 | -0.0016513 | -0.0015565 | 0.0030719 | 0.019916 | -0.012016 | -0.0094955 | 0.012616 | -0.0014931 | -0.064087 | 0.16479 | -0.041199 | -0.032043 | 0.10986 | 0.018311 | 0.036621 | -0.032043 | 0.16022 | -0.041199 | -0.009155 | 0.086975 | 0.022888 | 0.15106 | 121.6873 | -0.032043 | -0.22888 | 121.8384 | 121.7651 | 121.7468 | 0.07782 | 0.05951 | 121.6873 | -0.036621 | -0.20599 | 121.8155 | 121.8796 | 121.7514 | 0.19226 | 0.064087 | 0.15106 | 0.009156 | 0.12817 | 0.032044 | 0.20599 | 0.20142 | 121.8933 | 121.8887 | -0.23804 | -0.23804 | 121.6965 | 121.7194 | 121.6644 | 121.6965
641.6562 | 122.0169 | -121.6599 | 0.12817 | -0.018921 | 0.056961 | 0.015039 | 0.01179 | -0.0025442 | -0.0016876 | -0.0033603 | -0.0046081 | 8.1264e-05 | 0.019703 | -0.0064621 | -0.0033005 | 0.016034 | -0.0012795 | 0 | 0.1236 | -0.013733 | 0.073242 | 0.21973 | 0.11902 | 0.14191 | 0.11444 | 0.11444 | -0.013733 | 0.13275 | 0.2243 | 0.17853 | 0.2655 | 121.6461 | -0.004578 | -0.054932 | 121.8796 | 121.8018 | 121.7789 | 0.15564 | 0.13275 | 121.6461 | -0.013733 | 0.004577 | 121.8842 | 121.9254 | 121.8384 | 0.27924 | 0.19226 | 0.23346 | 0.086975 | 0.23804 | 0.14648 | 0.13733 | 0.12817 | 121.7834 | 121.7743 | -0.14191 | -0.14191 | 121.7331 | 121.7926 | 121.6599 | 121.7743
643.4062 | 122.0215 | -121.6736 | 0.14191 | -0.0036622 | 0.056106 | 0.012903 | 0.012217 | -0.002117 | -0.004892 | -0.0050693 | -0.0046081 | 0.00093566 | 0.016498 | -0.0011215 | -0.0056503 | 0.018171 | 2.068e-06 | 0.022888 | 0.11444 | -0.009155 | 0.10986 | 0.2655 | 0.14648 | 0.14648 | 0.14191 | 0.091553 | 0.009155 | 0.13275 | 0.24261 | 0.16937 | 0.25177 | 121.6644 | -0.027466 | -0.032044 | 121.9391 | 121.8201 | 121.8201 | 0.15564 | 0.15564 | 121.6827 | -0.050354 | -0.009156 | 121.9162 | 121.9254 | 121.843 | 0.24261 | 0.16022 | 0.27466 | 0.11902 | 0.23346 | 0.1236 | 0.1236 | 0.082398 | 121.788 | 121.7651 | -0.15106 | -0.13275 | 121.7834 | 121.8063 | 121.6965 | 121.8155
645.0781 | 122.0261 | -121.6599 | 0.15106 | 0.0039673 | 0.057174 | 0.013544 | 0.010935 | 0.0010874 | -0.0044646 | -0.0035739 | 0.0014953 | 0.0032855 | 0.018421 | -0.0015487 | -0.0033005 | 0.014966 | 0.0012839 | 0.013733 | 0.10071 | 0.018311 | 0.10986 | 0.25177 | 0.14648 | 0.13733 | 0.14191 | 0.10071 | 0.004578 | 0.15106 | 0.24719 | 0.16479 | 0.25635 | 121.6782 | -0.050354 | -0.041199 | 121.9116 | 121.7972 | 121.8063 | 0.11902 | 0.12817 | 121.6644 | -0.050354 | 0 | 121.907 | 121.9162 | 121.8246 | 0.25177 | 0.16022 | 0.23346 | 0.091552 | 0.24261 | 0.14648 | 0.082397 | 0.09613 | 121.7606 | 121.7606 | -0.13275 | -0.14648 | 121.7697 | 121.8109 | 121.6736 | 121.8018
646.8125 | 122.0215 | -121.6873 | 0.13733 | -0.0036622 | 0.05397 | 0.014398 | 0.013072 | -0.0053214 | -0.0055328 | -0.0010105 | 0.0014953 | -0.00034614 | 0.017994 | -0.00090793 | -0.0028733 | 0.015394 | -0.0025613 | -0.027466 | 0.10529 | -0.032043 | 0.054932 | 0.20599 | 0.086975 | 0.10986 | 0.10071 | 0.082397 | -0.027466 | 0.10986 | 0.18768 | 0.14191 | 0.2243 | 121.6553 | -0.032043 | -0.082397 | 121.8933 | 121.7972 | 121.7743 | 0.14191 | 0.11902 | 121.6599 | -0.054932 | -0.027466 | 121.875 | 121.9116 | 121.8292 | 0.25177 | 0.16937 | 0.23804 | 0.086975 | 0.21515 | 0.13733 | 0.13733 | 0.10986 | 121.7926 | 121.7697 | -0.16937 | -0.16479 | 121.7422 | 121.7972 | 121.6599 | 121.788
648.5469 | 121.9025 | -121.7239 | 0.16022 | -0.0036622 | 0.054397 | 0.013971 | 0.010935 | -0.0025442 | -0.001474 | -0.0027195 | -0.0015565 | 0.0028583 | 0.017566 | -0.0011215 | -0.0047959 | 0.016462 | -0.0044839 | -0.018311 | 0.10529 | -0.045776 | 0.013733 | 0.13733 | 0.032043 | 0.050354 | -0.009155 | 0.11902 | -0.059509 | -0.004578 | 0.082397 | 0.018311 | 0.1236 | 121.6782 | -0.054931 | -0.14648 | 121.8613 | 121.7743 | 121.756 | 0.09613 | 0.077819 | 121.6644 | -0.041198 | -0.16479 | 121.8063 | 121.8475 | 121.7422 | 0.1831 | 0.07782 | 0.18311 | 0.059509 | 0.14191 | 0.054931 | 0.15106 | 0.17853 | 121.8292 | 121.843 | -0.20599 | -0.21973 | 121.7377 | 121.7194 | 121.7056 | 121.7148
650.2188 | 121.9803 | -121.7056 | 0.13275 | -0.0036622 | 0.054183 | 0.014612 | 0.0085855 | -0.0025442 | -0.0033966 | -0.00079691 | -0.0015565 | -0.00034614 | 0.016925 | -0.0049667 | -0.0050095 | 0.017316 | 0.00064307 | 0.009155 | 0.07782 | -0.018311 | 0.09613 | 0.21057 | 0.10071 | 0.10529 | 0.073242 | 0.091553 | -0.041199 | 0.073242 | 0.17395 | 0.11902 | 0.21057 | 121.6873 | -0.054931 | -0.036621 | 121.9162 | 121.8109 | 121.8063 | 0.1236 | 0.11902 | 121.6644 | -0.041198 | -0.059509 | 121.8796 | 121.9162 | 121.8246 | 0.25177 | 0.16022 | 0.22888 | 0.11444 | 0.21515 | 0.11444 | 0.096131 | 0.13275 | 121.7834 | 121.7972 | -0.15106 | -0.17395 | 121.8018 | 121.7789 | 121.7148 | 121.7789
651.9688 | 122.0078 | -121.6873 | 0.10071 | 0.0039673 | 0.054824 | 0.013971 | 0.011363 | -0.00040805 | -0.0016876 | -0.0027195 | -0.0015565 | 0.0015765 | 0.018207 | -0.00048073 | -0.00030965 | 0.020307 | -0.00085233 | 0.013733 | 0.091553 | -0.027466 | 0.082397 | 0.19226 | 0.064087 | 0.09613 | 0.11444 | 0.082397 | -0.018311 | 0.12817 | 0.1831 | 0.12817 | 0.22888 | 121.6599 | -0.009155 | -0.018311 | 121.8796 | 121.7834 | 121.7514 | 0.1236 | 0.091553 | 121.669 | -0.018311 | 0.027466 | 121.8704 | 121.9162 | 121.8155 | 0.24719 | 0.14649 | 0.21973 | 0.10986 | 0.20142 | 0.14649 | 0.11902 | 0.10071 | 121.7789 | 121.7697 | -0.12817 | -0.11902 | 121.7697 | 121.8155 | 121.701 | 121.8018
653.7188 | 121.9986 | -121.7102 | 0.14191 | -0.011291 | 0.056106 | 0.012689 | 0.011149 | -0.0044668 | -0.0038238 | -0.0027195 | -0.0015565 | 0.00093566 | 0.019275 | -0.0024033 | -0.0028733 | 0.017316 | 0.0023521 | -0.050354 | 0.082397 | -0.036621 | 0.009155 | 0.15106 | 0.027466 | 0.064087 | 0.022888 | 0.09613 | -0.050354 | 0.082397 | 0.15564 | 0.10071 | 0.19684 | 121.6736 | -0.05951 | -0.13275 | 121.8613 | 121.7743 | 121.7377 | 0.10071 | 0.064087 | 121.6599 | -0.045777 | -0.05951 | 121.8658 | 121.907 | 121.8109 | 0.24719 | 0.15106 | 0.18768 | 0.045776 | 0.20599 | 0.13275 | 0.11902 | 0.14648 | 121.7926 | 121.8063 | -0.17853 | -0.19226 | 121.7194 | 121.7926 | 121.6599 | 121.7331
655.4062 | 122.0078 | -121.6873 | 0.13275 | -0.011291 | 0.054397 | 0.012476 | 0.0077309 | 0.0032236 | -0.004892 | -0.0016513 | -0.0046081 | 0.0020039 | 0.018421 | -0.00090793 | -0.0041551 | 0.018598 | 0.0012839 | -0.045776 | 0.10071 | -0.041199 | 0.022888 | 0.15106 | 0.050354 | 0.068665 | 0.041199 | 0.10071 | -0.045776 | 0.073242 | 0.17853 | 0.12817 | 0.20599 | 121.6461 | -0.032043 | -0.10986 | 121.8384 | 121.756 | 121.7377 | 0.10986 | 0.091553 | 121.6415 | -0.032043 | -0.059509 | 121.8658 | 121.8933 | 121.8155 | 0.25177 | 0.17395 | 0.19226 | 0.064087 | 0.2243 | 0.11902 | 0.14191 | 0.14648 | 121.788 | 121.788 | -0.17395 | -0.17853 | 121.7102 | 121.7606 | 121.6415 | 121.7285
657.1406 | 121.9986 | -121.6919 | 0.1236 | -0.0036622 | 0.055252 | 0.01568 | 0.011576 | 0.00301 | -0.0021148 | -0.0035739 | -0.0015565 | 0.0047809 | 0.020343 | 0.00058747 | -0.00095065 | 0.018384 | -0.0012795 | -0.054932 | 0.10529 | -0.045776 | -0.004578 | 0.11902 | -0.004578 | 0.027466 | 0.041199 | 0.091553 | -0.045776 | 0.091553 | 0.15564 | 0.10071 | 0.21057 | 121.6461 | -0.01831 | -0.12817 | 121.8109 | 121.7194 | 121.6873 | 0.073242 | 0.041198 | 121.6461 | -0.032043 | -0.032043 | 121.8475 | 121.9025 | 121.7926 | 0.25635 | 0.14648 | 0.16479 | 0.041198 | 0.20142 | 0.13733 | 0.15106 | 0.13733 | 121.7972 | 121.7834 | -0.16937 | -0.16937 | 121.6873 | 121.7834 | 121.637 | 121.7331
658.8906 | 121.9894 | -121.6965 | 0.13733 | -0.011291 | 0.055679 | 0.013544 | 0.011149 | 0.00087375 | -0.0036102 | -0.0025057 | -0.0015565 | -0.00055974 | 0.019062 | -0.0013351 | -0.0043687 | 0.018812 | -0.0019205 | 0.004578 | 0.07782 | -0.022888 | 0.068665 | 0.20599 | 0.10529 | 0.11902 | 0.082397 | 0.07782 | -0.036621 | 0.091553 | 0.18768 | 0.14191 | 0.19684 | 121.6736 | -0.059509 | -0.068664 | 121.9025 | 121.8155 | 121.8018 | 0.14191 | 0.12817 | 121.6599 | -0.059509 | -0.045776 | 121.8842 | 121.8933 | 121.8384 | 0.23346 | 0.17853 | 0.22888 | 0.091553 | 0.2243 | 0.12817 | 0.10071 | 0.11444 | 121.7743 | 121.7743 | -0.16022 | -0.17395 | 121.7651 | 121.788 | 121.701 | 121.7789
660.5625 | 121.9894 | -121.6919 | 0.13733 | -0.0036622 | 0.05397 | 0.01333 | 0.010722 | 0.0017282 | -0.003183 | -0.0033603 | 0.0014953 | 0.0013629 | 0.016712 | -0.0088119 | -0.0045823 | 0.01753 | -0.0010659 | 0.013733 | 0.082397 | -0.041199 | 0.059509 | 0.21515 | 0.09613 | 0.10071 | 0.068665 | 0.086975 | -0.022888 | 0.07782 | 0.19226 | 0.10071 | 0.20142 | 121.6507 | -0.054932 | -0.07782 | 121.907 | 121.7926 | 121.788 | 0.14191 | 0.13733 | 121.669 | -0.050354 | -0.059509 | 121.8842 | 121.8933 | 121.7926 | 0.2243 | 0.1236 | 0.25635 | 0.10071 | 0.21515 | 0.10071 | 0.1236 | 0.10986 | 121.7743 | 121.7789 | -0.17853 | -0.16022 | 121.7514 | 121.7697 | 121.7056 | 121.7606
662.2969 | 121.9894 | -121.7148 | 0.13275 | -0.02655 | 0.053756 | 0.013971 | 0.012004 | -0.002117 | -0.002542 | -0.0037875 | -0.010712 | 0.0017901 | 0.016712 | -0.0071029 | -0.0028733 | 0.018384 | -0.0019205 | -0.050354 | 0.086975 | -0.027466 | 0 | 0.13275 | 0.032043 | 0.045776 | 0.009155 | 0.086975 | -0.022888 | 0.059509 | 0.14191 | 0.073242 | 0.18768 | 121.6873 | -0.045776 | -0.13275 | 121.8475 | 121.7606 | 121.7468 | 0.073242 | 0.059509 | 121.6919 | -0.045776 | -0.073242 | 121.8567 | 121.9025 | 121.788 | 0.21057 | 0.09613 | 0.16022 | 0.027466 | 0.16479 | 0.082397 | 0.11444 | 0.10986 | 121.8018 | 121.8018 | -0.16022 | -0.15564 | 121.7148 | 121.7743 | 121.6644 | 121.7239
664.0312 | 121.907 | -121.7514 | 0.15106 | -0.011291 | 0.054611 | 0.010767 | 0.011363 | -0.0023306 | -0.0023284 | -0.0040011 | -0.0015565 | 0.0030719 | 0.017353 | -0.013084 | -0.0069321 | 0.015394 | -0.0051247 | -0.032043 | 0.10071 | -0.050354 | -0.018311 | 0.11902 | 0.036621 | 0.022888 | -0.027466 | 0.11444 | -0.059509 | -0.004578 | 0.086975 | 0.027466 | 0.11444 | 121.701 | -0.050354 | -0.16937 | 121.8704 | 121.7743 | 121.788 | 0.073242 | 0.086975 | 121.6919 | -0.036621 | -0.15564 | 121.8384 | 121.8658 | 121.7789 | 0.17395 | 0.086975 | 0.16937 | 0.032043 | 0.14648 | 0.054931 | 0.15106 | 0.17395 | 121.8521 | 121.8658 | -0.20142 | -0.21057 | 121.7331 | 121.7468 | 121.7194 | 121.7239
665.7812 | 121.8933 | -121.7377 | 0.16022 | 0.0039673 | 0.055252 | 0.016107 | 0.013926 | -0.0010488 | -0.002542 | -0.0025057 | -0.0046081 | 0.0037127 | 0.017994 | -0.0060349 | -0.0035141 | 0.016462 | 0.0027793 | -0.064087 | 0.13733 | -0.054932 | -0.068665 | 0.050354 | -0.059509 | -0.027466 | -0.064087 | 0.1236 | -0.073242 | -0.004578 | 0.045776 | -0.018311 | 0.12817 | 121.6827 | -0.022888 | -0.22888 | 121.788 | 121.7102 | 121.6782 | 0.027466 | -0.004577 | 121.6644 | -0.036621 | -0.16479 | 121.7834 | 121.8658 | 121.7194 | 0.20142 | 0.054931 | 0.10529 | -0.013733 | 0.11902 | 0.068664 | 0.19226 | 0.19684 | 121.875 | 121.8613 | -0.21515 | -0.23346 | 121.669 | 121.7331 | 121.6736 | 121.6736
667.5156 | 121.8842 | -121.7239 | 0.15564 | -0.0036622 | 0.05632 | 0.012903 | 0.01414 | -0.0023306 | -0.0027556 | 0.00048489 | 0.0014953 | 0.0032855 | 0.018848 | -0.0066757 | -0.0020187 | 0.017743 | -0.0055521 | -0.045776 | 0.10529 | -0.050354 | -0.045776 | 0.082397 | -0.036621 | -0.013733 | -0.054932 | 0.12817 | -0.050354 | -0.004578 | 0.041199 | -0.041199 | 0.11444 | 121.6736 | -0.050354 | -0.20142 | 121.8063 | 121.7102 | 121.6873 | 0.036621 | 0.013733 | 121.6736 | -0.027466 | -0.16022 | 121.7651 | 121.8384 | 121.6827 | 0.16479 | 0.009155 | 0.13275 | 0.004578 | 0.091553 | 0.045776 | 0.15564 | 0.17853 | 121.8292 | 121.8521 | -0.20599 | -0.20599 | 121.6782 | 121.7194 | 121.6782 | 121.669
669.1875 | 121.9849 | -121.6919 | 0.09613 | -0.018921 | 0.053543 | 0.013971 | 0.010722 | 0.0040782 | -0.0019012 | -0.0027195 | -0.0046081 | 0.00050846 | 0.021198 | 0.0018693 | -9.605e-05 | 0.021161 | -0.0040567 | -0.022888 | 0.07782 | 0.004578 | 0.041199 | 0.21057 | 0.050354 | 0.068665 | 0.10529 | 0.068665 | -0.041199 | 0.11444 | 0.17395 | 0.11444 | 0.20142 | 121.6965 | -0.01831 | -0.054931 | 121.9025 | 121.7606 | 121.7422 | 0.064087 | 0.045776 | 121.6507 | -0.027465 | 0.018311 | 121.8658 | 121.8933 | 121.8063 | 0.24262 | 0.15564 | 0.20599 | 0.036621 | 0.21515 | 0.15564 | 0.073242 | 0.10986 | 121.7697 | 121.7606 | -0.091552 | -0.13733 | 121.7331 | 121.8063 | 121.669 | 121.7972
670.9375 | 121.8979 | -121.7422 | 0.15106 | -0.0036622 | 0.054611 | 0.015039 | 0.011363 | -0.00019445 | -0.0023284 | -0.00015591 | -0.0046081 | 0.0060627 | 0.021412 | 0.00016027 | -0.0015915 | 0.019666 | -0.0046975 | -0.068665 | 0.11902 | -0.059509 | -0.07782 | 0.045776 | -0.050354 | -0.027466 | -0.050354 | 0.11444 | -0.086975 | 0.013733 | 0.050354 | -0.013733 | 0.12817 | 121.6827 | -0.032043 | -0.22888 | 121.788 | 121.7148 | 121.6919 | 0.032043 | 0.009155 | 121.6553 | -0.036621 | -0.13733 | 121.7926 | 121.8704 | 121.7285 | 0.21515 | 0.073242 | 0.10528 | -0.018311 | 0.13733 | 0.10071 | 0.17853 | 0.20142 | 121.8613 | 121.8567 | -0.21057 | -0.23804 | 121.6644 | 121.756 | 121.6736 | 121.6919
672.6094 | 121.9345 | -121.7285 | 0.13733 | 0.0039673 | 0.057388 | 0.011835 | 0.013926 | 0.0023692 | -0.0019012 | -0.0040011 | -0.0015565 | 0.0017901 | 0.02013 | -0.010094 | -0.0020187 | 0.018812 | -0.0032021 | -0.032043 | 0.10071 | -0.045776 | -0.009155 | 0.12817 | 0.018311 | 0.022888 | 0.013733 | 0.11902 | -0.054932 | 0.027466 | 0.09613 | 0.022888 | 0.16479 | 121.6827 | -0.036621 | -0.14648 | 121.8567 | 121.7514 | 121.7468 | 0.068664 | 0.064087 | 121.6736 | -0.01831 | -0.10986 | 121.8246 | 121.8933 | 121.7514 | 0.21973 | 0.07782 | 0.17395 | 0.036621 | 0.15106 | 0.082398 | 0.14648 | 0.17395 | 121.8292 | 121.8475 | -0.18311 | -0.19226 | 121.7194 | 121.756 | 121.6965 | 121.7422
674.3594 | 121.9528 | -121.7239 | 0.12817 | -0.011291 | 0.055252 | 0.013116 | 0.012858 | 0.0042918 | -0.001474 | -0.00015591 | -0.0076599 | 0.0045673 | 0.01778 | -0.0092391 | -0.0028733 | 0.016034 | -0.00042513 | -0.027466 | 0.13275 | -0.054932 | -0.022888 | 0.12817 | 0.018311 | 0.032043 | 0 | 0.10986 | -0.050354 | 0.041199 | 0.11902 | 0.045776 | 0.16937 | 121.669 | 0.004577 | -0.15106 | 121.8521 | 121.756 | 121.7422 | 0.086975 | 0.073243 | 121.6736 | -0.018311 | -0.086975 | 121.843 | 121.8933 | 121.7697 | 0.21973 | 0.09613 | 0.18311 | 0.032044 | 0.16937 | 0.091553 | 0.18768 | 0.16022 | 121.8567 | 121.8338 | -0.18311 | -0.17853 | 121.7011 | 121.7651 | 121.6965 | 121.7239
676.1094 | 121.9391 | -121.7194 | 0.15564 | -0.03418 | 0.053115 | 0.013116 | 0.0098673 | -0.003185 | -0.0033966 | 5.7688e-05 | -0.0076599 | 0.0037127 | 0.019916 | -0.0017623 | -0.0045823 | 0.01753 | -0.0017069 | -0.073242 | 0.11444 | -0.036621 | -0.045776 | 0.086975 | 0.009155 | 0.009155 | -0.018311 | 0.11902 | -0.032043 | 0.036621 | 0.10529 | 0.045776 | 0.16479 | 121.6827 | -0.041199 | -0.20142 | 121.8063 | 121.7285 | 121.7285 | 0.045776 | 0.045776 | 121.6873 | -0.036621 | -0.11902 | 121.8246 | 121.8842 | 121.7651 | 0.19684 | 0.077819 | 0.1236 | -0.009155 | 0.13733 | 0.068664 | 0.15106 | 0.15106 | 121.8338 | 121.8384 | -0.19226 | -0.18768 | 121.6736 | 121.756 | 121.6461 | 121.701
677.8594 | 121.994 | -121.7148 | 0.1236 | -0.0036622 | 0.052902 | 0.014825 | 0.0098673 | 0.00066015 | -0.002542 | -0.00036951 | 0.0014953 | 0.0022175 | 0.021412 | -0.0081711 | 0.00033115 | 0.019025 | -0.0040567 | -0.068665 | 0.11902 | -0.050354 | -0.045776 | 0.10529 | -0.032043 | 0 | -0.009155 | 0.10529 | -0.036621 | 0.07782 | 0.14191 | 0.07782 | 0.19684 | 121.6644 | -0.004577 | -0.16937 | 121.8201 | 121.7148 | 121.6827 | 0.050354 | 0.018311 | 121.6782 | -0.01831 | -0.045776 | 121.8567 | 121.9116 | 121.7926 | 0.23346 | 0.11444 | 0.15564 | 0.004578 | 0.17853 | 0.11444 | 0.16937 | 0.14191 | 121.8338 | 121.8201 | -0.17395 | -0.16022 | 121.669 | 121.7926 | 121.6461 | 121.7056
679.5938 | 121.9894 | -121.7194 | 0.12817 | -0.018921 | 0.054611 | 0.01333 | 0.010295 | 0.0015146 | -0.001474 | -0.00079691 | -0.010712 | 0.0011493 | 0.018207 | 0.00016027 | -0.0033005 | 0.018384 | -0.0038431 | -0.045776 | 0.09613 | -0.032043 | -0.022888 | 0.14191 | 0.036621 | 0.041199 | -0.004578 | 0.073242 | -0.032043 | 0.064087 | 0.14648 | 0.091553 | 0.19226 | 121.6873 | -0.032044 | -0.15106 | 121.8613 | 121.7606 | 121.756 | 0.073242 | 0.068664 | 121.6873 | -0.054932 | -0.064087 | 121.8658 | 121.9116 | 121.8109 | 0.2243 | 0.1236 | 0.17395 | 0.009155 | 0.17853 | 0.09613 | 0.12817 | 0.10529 | 121.8155 | 121.7926 | -0.16022 | -0.16022 | 121.6965 | 121.7834 | 121.6736 | 121.7148
681.2656 | 122.0261 | -121.6736 | 0.12817 | 0.0039673 | 0.055465 | 0.015466 | 0.0098673 | 0.0040782 | -0.0019012 | -0.0042147 | -0.0076599 | 0.0030719 | 0.018421 | -0.0028305 | -9.605e-05 | 0.018598 | 0.00021567 | 0.013733 | 0.054932 | -0.018311 | 0.050354 | 0.19226 | 0.050354 | 0.082397 | 0.091553 | 0.082397 | -0.009155 | 0.1236 | 0.20599 | 0.12817 | 0.2243 | 121.6553 | -0.073242 | -0.07782 | 121.8658 | 121.756 | 121.7239 | 0.10071 | 0.068665 | 121.6644 | -0.045777 | -0.004578 | 121.8796 | 121.8979 | 121.8018 | 0.23346 | 0.13733 | 0.21057 | 0.068665 | 0.21515 | 0.13275 | 0.073243 | 0.091552 | 121.7285 | 121.756 | -0.14649 | -0.13733 | 121.7239 | 121.7972 | 121.6873 | 121.7651
683 | 121.9254 | -121.6965 | 0.16479 | 0.0039673 | 0.058242 | 0.014825 | 0.013285 | -0.00062165 | 2.1362e-05 | -0.0016513 | -0.0015565 | 0.0030719 | 0.018848 | -0.010521 | -0.0028733 | 0.016248 | 0.00021567 | -0.009155 | 0.13733 | -0.050354 | -0.004578 | 0.12817 | 0.022888 | 0.018311 | -0.022888 | 0.11902 | -0.045776 | 0.041199 | 0.086975 | 0.013733 | 0.13275 | 121.6461 | -0.027466 | -0.16937 | 121.8246 | 121.7148 | 121.7194 | 0.068665 | 0.073242 | 121.6507 | -0.045776 | -0.1236 | 121.7834 | 121.8292 | 121.7102 | 0.17853 | 0.059509 | 0.17853 | 0.045776 | 0.13275 | 0.086975 | 0.18768 | 0.16479 | 121.8338 | 121.8155 | -0.21515 | -0.21057 | 121.6919 | 121.7377 | 121.6873 | 121.6736
684.75 | 121.9482 | -121.7285 | 0.13733 | -0.0036622 | 0.056533 | 0.013757 | 0.011576 | 0.00044655 | -0.0033966 | -0.0033603 | -0.0046081 | 0.0037127 | 0.019916 | -0.0045395 | -0.0033005 | 0.017957 | -0.00021153 | -0.07782 | 0.12817 | -0.073242 | -0.073242 | 0.064087 | -0.050354 | -0.018311 | -0.10529 | 0.10986 | -0.073242 | 0.018311 | 0.073242 | 0 | 0.13733 | 121.6553 | -0.009155 | -0.21057 | 121.7926 | 121.7102 | 121.6782 | 0.054931 | 0.022888 | 121.6553 | -0.027466 | -0.11902 | 121.8018 | 121.8658 | 121.7285 | 0.21057 | 0.073242 | 0.13733 | 0 | 0.14648 | 0.091553 | 0.20142 | 0.18311 | 121.8567 | 121.8384 | -0.21057 | -0.21057 | 121.6553 | 121.7468 | 121.6507 | 121.6232
686.4219 | 122.0261 | -121.6965 | 0.11444 | -0.0036622 | 0.055679 | 0.015253 | 0.012217 | 0.0055734 | -0.0029694 | -0.0014377 | -0.0046081 | 0.0020039 | 0.019703 | -0.0036849 | -0.0013779 | 0.019452 | -0.0032021 | -0.032043 | 0.11902 | -0.050354 | 0.009155 | 0.16022 | 0.036621 | 0.059509 | 0.068665 | 0.11444 | -0.036621 | 0.11444 | 0.1831 | 0.10529 | 0.23804 | 121.6461 | 0.004578 | -0.10529 | 121.8567 | 121.756 | 121.7331 | 0.10986 | 0.086975 | 121.6599 | 0 | 0 | 121.8796 | 121.9345 | 121.8018 | 0.27466 | 0.14191 | 0.21057 | 0.059509 | 0.21973 | 0.15106 | 0.16937 | 0.15106 | 121.8155 | 121.8109 | -0.16479 | -0.15106 | 121.7056 | 121.8109 | 121.6644 | 121.7651
688.1562 | 122.0123 | -121.7102 | 0.11444 | -0.02655 | 0.05397 | 0.01333 | 0.0087991 | 0.0027964 | -0.0012604 | -0.0020785 | -0.010712 | 0.0022175 | 0.02013 | -0.0013351 | -0.00052345 | 0.019452 | 0.00085667 | -0.009155 | 0.073242 | 0 | 0.059509 | 0.21057 | 0.064087 | 0.082397 | 0.10071 | 0.073242 | -0.022888 | 0.1236 | 0.1831 | 0.11444 | 0.22888 | 121.7102 | -0.041199 | -0.054932 | 121.9208 | 121.7926 | 121.7743 | 0.082397 | 0.064087 | 121.6873 | -0.041199 | 0.009155 | 121.8933 | 121.9391 | 121.8246 | 0.25177 | 0.13733 | 0.21057 | 0.059509 | 0.20599 | 0.14648 | 0.073242 | 0.09613 | 121.7834 | 121.7834 | -0.11444 | -0.13733 | 121.7697 | 121.8338 | 121.701 | 121.8109
689.9062 | 122.0078 | -121.7285 | 0.11902 | -0.018921 | 0.053329 | 0.013544 | 0.010722 | 0.0021556 | -0.004892 | -0.0042147 | -0.0015565 | -0.00077334 | 0.018421 | 0.0037919 | -0.0028733 | 0.017103 | -0.0010659 | -0.064087 | 0.091553 | -0.050354 | 0 | 0.16022 | 0.054932 | 0.07782 | 0.032043 | 0.091553 | -0.045776 | 0.064087 | 0.15564 | 0.10071 | 0.20599 | 121.6782 | -0.027466 | -0.11902 | 121.8887 | 121.8063 | 121.7834 | 0.12817 | 0.10529 | 121.6827 | -0.027466 | -0.054932 | 121.8842 | 121.9345 | 121.8292 | 0.25177 | 0.14648 | 0.21057 | 0.050354 | 0.20142 | 0.10986 | 0.14191 | 0.13733 | 121.8201 | 121.8201 | -0.16937 | -0.16479 | 121.7285 | 121.7926 | 121.6644 | 121.7606
691.5781 | 122.0261 | -121.6965 | 0.1236 | -0.011291 | 0.053115 | 0.014612 | 0.0073037 | -0.00083525 | -0.0057464 | -0.0025057 | -0.0015565 | 0.00050846 | 0.019275 | -0.0047531 | -0.0045823 | 0.017957 | -0.0053385 | -0.045776 | 0.10071 | -0.032043 | 0.004578 | 0.16479 | 0.050354 | 0.07782 | 0.059509 | 0.086975 | -0.045776 | 0.07782 | 0.17853 | 0.11444 | 0.2243 | 121.6644 | -0.022888 | -0.11902 | 121.8613 | 121.7743 | 121.7468 | 0.10986 | 0.082397 | 121.6507 | -0.036621 | -0.045776 | 121.875 | 121.9208 | 121.8109 | 0.27008 | 0.16022 | 0.19684 | 0.036621 | 0.2243 | 0.1236 | 0.13275 | 0.13275 | 121.7972 | 121.7834 | -0.15564 | -0.16937 | 121.701 | 121.7743 | 121.6507 | 121.756
693.3281 | 121.9711 | -121.7331 | 0.14191 | -0.018921 | 0.055679 | 0.011408 | 0.0098673 | -0.0012624 | -0.0012604 | -0.00036951 | -0.0046081 | 0.0049945 | 0.017139 | -0.0058213 | -0.0035141 | 0.016889 | -0.0012795 | -0.018311 | 0.12817 | -0.045776 | 0.013733 | 0.13275 | 0.022888 | 0.036621 | 0.022888 | 0.13275 | -0.050354 | 0.054932 | 0.11902 | 0.050354 | 0.1831 | 121.6873 | -0.013733 | -0.12817 | 121.8658 | 121.7697 | 121.756 | 0.082397 | 0.068664 | 121.6827 | -0.009156 | -0.086975 | 121.8521 | 121.9162 | 121.7834 | 0.23346 | 0.10071 | 0.17853 | 0.059509 | 0.16937 | 0.10529 | 0.17395 | 0.18311 | 121.8613 | 121.8658 | -0.18768 | -0.19226 | 121.7468 | 121.788 | 121.7148 | 121.756
695.0156 | 121.9254 | -121.7514 | 0.17395 | 0.0039673 | 0.05632 | 0.013116 | 0.012644 | 0.0019418 | -0.0010468 | -0.0014377 | 0.0014953 | 0.0043537 | 0.02013 | -0.0021897 | -0.0024461 | 0.016462 | -0.00063873 | -0.018311 | 0.11444 | -0.050354 | -0.018311 | 0.1236 | 0 | 0.004578 | -0.013733 | 0.11444 | -0.027466 | 0.022888 | 0.068665 | -0.009155 | 0.1236 | 121.701 | -0.059509 | -0.19226 | 121.875 | 121.756 | 121.7514 | 0.054932 | 0.050354 | 121.7239 | -0.059509 | -0.15106 | 121.8201 | 121.875 | 121.7422 | 0.15106 | 0.018311 | 0.17395 | 0.032043 | 0.096131 | 0.050354 | 0.16479 | 0.14191 | 121.8658 | 121.8658 | -0.2243 | -0.20142 | 121.7331 | 121.7743 | 121.7331 | 121.7377
696.75 | 121.9254 | -121.7514 | 0.15106 | -0.03418 | 0.054183 | 0.012048 | 0.010508 | -0.0025442 | -0.004892 | -0.0025057 | -0.013763 | 0.0034991 | 0.017353 | -0.0077439 | -0.0071457 | 0.016675 | -0.0019205 | -0.09613 | 0.1236 | -0.041199 | -0.086975 | 0.050354 | -0.045776 | -0.004578 | -0.091553 | 0.11444 | -0.068665 | -0.027466 | 0.064087 | -0.009155 | 0.13275 | 121.7102 | -0.027466 | -0.23804 | 121.8018 | 121.7468 | 121.7056 | 0.036621 | -0.004577 | 121.6827 | -0.036621 | -0.17853 | 121.8155 | 121.8842 | 121.7422 | 0.20142 | 0.05951 | 0.091553 | -0.045776 | 0.13275 | 0.041199 | 0.16479 | 0.18311 | 121.875 | 121.8658 | -0.19226 | -0.21973 | 121.6644 | 121.7239 | 121.6553 | 121.6599
698.5 | 121.9666 | -121.7239 | 0.13275 | -0.0036622 | 0.054183 | 0.015039 | 0.0096537 | 0.00301 | -0.0029694 | -0.00079691 | -0.0015565 | 0.00029486 | 0.019489 | 0.00058747 | -0.00095065 | 0.016889 | 0.0010703 | -0.082397 | 0.14648 | -0.064087 | -0.054932 | 0.064087 | -0.050354 | -0.004578 | -0.09613 | 0.11902 | -0.054932 | 0.045776 | 0.091553 | 0.027466 | 0.15564 | 121.6599 | 0.013733 | -0.18768 | 121.788 | 121.7194 | 121.6736 | 0.059509 | 0.013733 | 121.669 | -0.013732 | -0.086975 | 121.8155 | 121.8796 | 121.7514 | 0.21057 | 0.082398 | 0.12817 | 0.009155 | 0.14649 | 0.10071 | 0.21057 | 0.17395 | 121.8704 | 121.843 | -0.19684 | -0.18768 | 121.669 | 121.7697 | 121.6415 | 121.6278
700.2344 | 121.994 | -121.6827 | 0.13275 | -0.011291 | 0.054824 | 0.014185 | 0.0083719 | -0.0023306 | -0.004251 | -0.0040011 | -0.0076599 | 0.0013629 | 0.018634 | -0.0021897 | -0.0015915 | 0.017957 | -0.00085233 | -0.045776 | 0.07782 | -0.022888 | 0 | 0.17395 | 0.041199 | 0.073242 | -0.059509 | 0.086975 | -0.041199 | 0.07782 | 0.14648 | 0.091553 | 0.17853 | 121.6599 | -0.054931 | -0.13275 | 121.8567 | 121.756 | 121.7239 | 0.09613 | 0.064087 | 121.6415 | -0.045776 | -0.054931 | 121.8292 | 121.8613 | 121.7743 | 0.21973 | 0.13275 | 0.19684 | 0.022888 | 0.18768 | 0.11902 | 0.10071 | 0.12817 | 121.7606 | 121.7697 | -0.15564 | -0.17395 | 121.6827 | 121.7606 | 121.637 | 121.6232
701.9219 | 121.9849 | -121.7148 | 0.15106 | -0.0036622 | 0.056747 | 0.013971 | 0.0087991 | 1.915e-05 | -0.0016876 | -0.0025057 | -0.0046081 | 0.00093566 | 0.015644 | -0.0060349 | -0.0043687 | 0.017743 | -0.0038431 | 0 | 0.09613 | -0.027466 | 0.064087 | 0.20142 | 0.10986 | 0.10986 | 0.018311 | 0.09613 | -0.027466 | 0.068665 | 0.16022 | 0.086975 | 0.17395 | 121.6873 | -0.054932 | -0.086975 | 121.9162 | 121.8246 | 121.8246 | 0.13733 | 0.13733 | 121.6873 | -0.054932 | -0.082397 | 121.875 | 121.8887 | 121.8018 | 0.20142 | 0.11444 | 0.22888 | 0.091553 | 0.18768 | 0.096131 | 0.1236 | 0.1236 | 121.8109 | 121.8109 | -0.17853 | -0.17853 | 121.7789 | 121.7834 | 121.7148 | 121.7331
703.6719 | 121.9345 | -121.7285 | 0.16937 | -0.02655 | 0.053543 | 0.012689 | 0.010081 | -0.00019445 | -0.003183 | -0.0018649 | -0.0076599 | 0.0022175 | 0.015857 | -0.0066757 | -0.00073705 | 0.01753 | -0.0032021 | -0.064087 | 0.10986 | -0.059509 | -0.041199 | 0.07782 | 0 | 0.013733 | -0.045776 | 0.13275 | -0.054932 | 0.022888 | 0.10986 | 0.045776 | 0.16022 | 121.669 | -0.05951 | -0.21057 | 121.8063 | 121.7422 | 121.7285 | 0.073242 | 0.059509 | 121.6736 | -0.036622 | -0.14649 | 121.8384 | 121.8887 | 121.7743 | 0.21515 | 0.10071 | 0.13733 | 0.01831 | 0.16479 | 0.07782 | 0.16937 | 0.18768 | 121.8384 | 121.8613 | -0.22888 | -0.22431 | 121.6873 | 121.7514 | 121.6644 | 121.6827
705.4219 | 121.907 | -121.7422 | 0.17853 | -0.0036622 | 0.057174 | 0.01568 | 0.011576 | -0.00083525 | -0.002542 | -0.0010105 | -0.0076599 | 0.0030719 | 0.018207 | -0.0079575 | -0.00030965 | 0.016675 | 0.0019247 | -0.07782 | 0.13275 | -0.073242 | -0.091553 | 0.022888 | -0.07782 | -0.013733 | -0.12817 | 0.10529 | -0.068665 | 0 | 0.032043 | -0.036621 | 0.13733 | 121.669 | -0.045777 | -0.27008 | 121.7651 | 121.7285 | 121.6644 | 0.059509 | -0.004578 | 121.6736 | -0.073242 | -0.17853 | 121.7743 | 121.8796 | 121.7056 | 0.20599 | 0.032044 | 0.09613 | -0.018311 | 0.10071 | 0.068665 | 0.20599 | 0.17395 | 121.875 | 121.8475 | -0.25177 | -0.24719 | 121.6507 | 121.7422 | 121.6644 | 121.6141
707.1406 | 122.0352 | -121.7102 | 0.10071 | -0.0036622 | 0.053115 | 0.015039 | 0.0083719 | 0.0019418 | -0.0019012 | -0.0014377 | -0.0015565 | -0.0033367 | 0.01778 | -0.0036849 | -0.0045823 | 0.016889 | -0.00042513 | -0.013733 | 0.07782 | -0.027466 | 0.054932 | 0.21973 | 0.10529 | 0.10986 | 0.050354 | 0.07782 | -0.041199 | 0.13275 | 0.21973 | 0.16479 | 0.23346 | 121.6827 | -0.022888 | -0.045776 | 121.9299 | 121.8201 | 121.8155 | 0.13733 | 0.13275 | 121.669 | -0.022888 | 0.032043 | 121.9299 | 121.9437 | 121.875 | 0.27466 | 0.20599 | 0.24719 | 0.082398 | 0.26093 | 0.17395 | 0.10529 | 0.11902 | 121.788 | 121.788 | -0.12817 | -0.14191 | 121.7651 | 121.843 | 121.6965 | 121.7606
708.875 | 121.994 | -121.7102 | 0.13275 | -0.011291 | 0.056106 | 0.014612 | 0.0096537 | -0.003185 | -0.0029694 | -0.00036951 | -0.0046081 | 0.00050846 | 0.018848 | 0.0044327 | -0.0020187 | 0.018384 | -0.0051247 | -0.050354 | 0.091553 | -0.013733 | 0.004578 | 0.13275 | 0.036621 | 0.064087 | -0.064087 | 0.10071 | -0.041199 | 0.073242 | 0.13275 | 0.086975 | 0.19684 | 121.6965 | -0.041198 | -0.12817 | 121.843 | 121.7743 | 121.7468 | 0.07782 | 0.050354 | 121.669 | -0.032043 | -0.059509 | 121.843 | 121.907 | 121.7972 | 0.23804 | 0.12817 | 0.14648 | 0.018311 | 0.17395 | 0.11444 | 0.10529 | 0.14191 | 121.8018 | 121.8109 | -0.14648 | -0.17395 | 121.7148 | 121.7834 | 121.6599 | 121.6461
710.5469 | 121.9116 | -121.7331 | 0.15564 | -0.0036622 | 0.05632 | 0.012903 | 0.010508 | 0.0025828 | -0.00040584 | -0.0018649 | -0.0015565 | 0.0030719 | 0.018634 | -0.0066757 | -0.0015915 | 0.018598 | -0.0023477 | -0.050354 | 0.12817 | -0.073242 | -0.054932 | 0.064087 | -0.041199 | -0.022888 | -0.09613 | 0.11444 | -0.068665 | 0.013733 | 0.050354 | -0.013733 | 0.13733 | 121.6599 | -0.027466 | -0.21057 | 121.7972 | 121.7102 | 121.6919 | 0.050354 | 0.032043 | 121.6644 | -0.041199 | -0.14191 | 121.7834 | 121.8704 | 121.7194 | 0.20599 | 0.054932 | 0.13733 | 0.01831 | 0.11902 | 0.082398 | 0.20142 | 0.18311 | 121.8613 | 121.8475 | -0.22888 | -0.22431 | 121.6782 | 121.7468 | 121.6827 | 121.637
712.2812 | 121.9208 | -121.756 | 0.16937 | -0.0036622 | 0.054397 | 0.016962 | 0.0094399 | -0.0025442 | -0.0012604 | -0.00058311 | -0.0015565 | 0.0024311 | 0.017139 | -0.0021897 | -0.0037277 | 0.017103 | 0.00085667 | -0.050354 | 0.11444 | -0.041199 | -0.045776 | 0.09613 | 0.009155 | 0.022888 | -0.059509 | 0.13733 | -0.054932 | -0.018311 | 0.073242 | 0.018311 | 0.12817 | 121.7148 | -0.054932 | -0.21515 | 121.8521 | 121.7789 | 121.7651 | 0.064087 | 0.050354 | 121.701 | -0.032044 | -0.18768 | 121.8292 | 121.8842 | 121.7743 | 0.18311 | 0.073243 | 0.13733 | -0.004577 | 0.12817 | 0.036621 | 0.15564 | 0.19226 | 121.8704 | 121.8933 | -0.21057 | -0.22431 | 121.7102 | 121.7377 | 121.7056 | 121.6965
714 | 122.0306 | -121.6919 | 0.12817 | -0.011291 | 0.05397 | 0.014825 | 0.0098673 | -0.0010488 | -0.0038238 | 5.7688e-05 | -0.0015565 | -0.00034614 | 0.021625 | -0.00048073 | 0.00054475 | 0.018598 | -0.0027749 | -0.004578 | 0.07782 | 0.004578 | 0.064087 | 0.21973 | 0.07782 | 0.091553 | 0.027466 | 0.068665 | -0.013733 | 0.14191 | 0.18768 | 0.11444 | 0.22888 | 121.6965 | -0.050354 | -0.064087 | 121.9116 | 121.7834 | 121.7697 | 0.086975 | 0.073242 | 121.6782 | -0.059509 | 0.013733 | 121.8796 | 121.9208 | 121.8063 | 0.24261 | 0.12817 | 0.21515 | 0.059509 | 0.20142 | 0.15564 | 0.073242 | 0.082398 | 121.7697 | 121.7606 | -0.1236 | -0.14191 | 121.756 | 121.8338 | 121.6873 | 121.7194
715.6875 | 121.9666 | -121.7422 | 0.16937 | -0.03418 | 0.055038 | 0.014612 | 0.010508 | 0.00087375 | -0.002542 | -0.0035739 | -0.0076599 | 0.0022175 | 0.019489 | -0.0071029 | -0.0024461 | 0.015607 | -0.0053385 | -0.059509 | 0.11444 | -0.041199 | -0.068665 | 0.07782 | -0.009155 | -0.009155 | -0.050354 | 0.12817 | -0.054932 | 0.032043 | 0.10529 | 0.032043 | 0.16479 | 121.701 | -0.054932 | -0.23804 | 121.8201 | 121.7331 | 121.7331 | 0.032044 | 0.032044 | 121.6873 | -0.041199 | -0.13733 | 121.8475 | 121.907 | 121.7743 | 0.21973 | 0.086975 | 0.11902 | -0.027466 | 0.16022 | 0.086975 | 0.15564 | 0.18311 | 121.8567 | 121.8704 | -0.21057 | -0.22431 | 121.6736 | 121.7743 | 121.6827 | 121.6919
717.4375 | 122.0444 | -121.6965 | 0.13275 | 0.011597 | 0.053329 | 0.013544 | 0.0087991 | -0.0010488 | -0.0033966 | -0.0040011 | -0.0076599 | 0.00093566 | 0.018207 | 0.0010147 | -0.0035141 | 0.017957 | -0.00063873 | 0.004578 | 0.082397 | -0.013733 | 0.068665 | 0.25635 | 0.11444 | 0.13275 | 0.064087 | 0.091553 | -0.018311 | 0.11902 | 0.21973 | 0.16479 | 0.23346 | 121.6827 | -0.050354 | -0.064086 | 121.9528 | 121.8292 | 121.8109 | 0.14648 | 0.12817 | 121.6782 | -0.041198 | -0.013732 | 121.9162 | 121.9299 | 121.8613 | 0.25177 | 0.18311 | 0.27008 | 0.082398 | 0.23804 | 0.13733 | 0.09613 | 0.10986 | 121.7789 | 121.788 | -0.14648 | -0.15106 | 121.7651 | 121.8155 | 121.701 | 121.7606
719.1875 | 121.907 | -121.7331 | 0.16937 | -0.02655 | 0.056106 | 0.013116 | 0.013072 | 0.0015146 | -0.00083304 | -0.0022921 | -0.0015565 | 0.0037127 | 0.018848 | -0.0053939 | -0.0056503 | 0.015821 | 2.068e-06 | -0.068665 | 0.13275 | -0.059509 | -0.045776 | 0.07782 | -0.004578 | 0.013733 | -0.086975 | 0.12817 | -0.068665 | 0 | 0.07782 | 0.022888 | 0.1236 | 121.6736 | -0.036622 | -0.21515 | 121.8109 | 121.7468 | 121.7285 | 0.073242 | 0.054931 | 121.6644 | -0.041199 | -0.16937 | 121.8109 | 121.8567 | 121.756 | 0.19226 | 0.091553 | 0.13733 | 0.013733 | 0.14649 | 0.068665 | 0.19226 | 0.19684 | 121.8658 | 121.8613 | -0.22888 | -0.23804 | 121.6873 | 121.7331 | 121.6644 | 121.6461
720.9375 | 122.0215 | -121.6782 | 0.12817 | 0.0039673 | 0.05397 | 0.013971 | 0.0085855 | -0.001476 | -0.001474 | -0.0020785 | -0.0046081 | 0.0017901 | 0.017566 | -0.0028305 | -0.0043687 | 0.017103 | -0.0023477 | 0.022888 | 0.086975 | -0.018311 | 0.086975 | 0.22888 | 0.1236 | 0.11902 | 0.068665 | 0.10529 | -0.027466 | 0.11444 | 0.20599 | 0.13275 | 0.23346 | 121.6599 | -0.041199 | -0.041199 | 121.907 | 121.7972 | 121.8018 | 0.13733 | 0.14191 | 121.6507 | -0.022888 | -0.013733 | 121.8842 | 121.9116 | 121.8109 | 0.26093 | 0.16022 | 0.24719 | 0.10529 | 0.23346 | 0.14191 | 0.10529 | 0.13275 | 121.7651 | 121.7834 | -0.14649 | -0.15564 | 121.7651 | 121.7926 | 121.701 | 121.7468
722.6094 | 122.0398 | -121.6782 | 0.11902 | 0.0039673 | 0.055465 | 0.011835 | 0.011576 | -0.00040805 | -0.00083304 | -0.0027195 | 0.0014953 | 0.0026447 | 0.018207 | 0.0012283 | -0.0030869 | 0.016889 | -0.00042513 | 0.013733 | 0.10071 | -0.004578 | 0.091553 | 0.24261 | 0.11902 | 0.1236 | 0.068665 | 0.086975 | -0.036621 | 0.13275 | 0.2243 | 0.16022 | 0.23346 | 121.6736 | -0.018311 | -0.027466 | 121.9208 | 121.8018 | 121.7972 | 0.12817 | 0.1236 | 121.6415 | -0.032044 | 0.013732 | 121.9025 | 121.9116 | 121.8384 | 0.27008 | 0.19684 | 0.24719 | 0.096131 | 0.26093 | 0.16937 | 0.10529 | 0.1236 | 121.7789 | 121.7651 | -0.1236 | -0.15564 | 121.7697 | 121.8109 | 121.6919 | 121.7468
724.3438 | 122.0215 | -121.7331 | 0.13733 | -0.018921 | 0.054397 | 0.01333 | 0.0096537 | 0.0017282 | -0.003183 | -0.0037875 | -0.0076599 | 0.0020039 | 0.015644 | -5.3326e-05 | 0.00011755 | 0.020307 | 0.0036337 | -0.018311 | 0.068665 | -0.009155 | 0.032043 | 0.1831 | 0.050354 | 0.059509 | -0.022888 | 0.07782 | -0.004578 | 0.073242 | 0.16479 | 0.09613 | 0.19226 | 121.7239 | -0.068664 | -0.10529 | 121.9162 | 121.7926 | 121.7834 | 0.068664 | 0.059509 | 121.7285 | -0.059509 | -0.064087 | 121.8979 | 121.9254 | 121.8292 | 0.19684 | 0.10071 | 0.19226 | 0.041198 | 0.16937 | 0.07782 | 0.07782 | 0.082398 | 121.8018 | 121.8109 | -0.14648 | -0.14191 | 121.7651 | 121.8063 | 121.7148 | 121.7102
726.0938 | 122.0169 | -121.6873 | 0.1236 | -0.011291 | 0.053756 | 0.015466 | 0.010081 | -0.004894 | -0.0012604 | -0.0029331 | -0.0076599 | 0.0013629 | 0.018848 | 0.00037387 | -0.00030965 | 0.019025 | 0.00021567 | 0.004578 | 0.073242 | 0 | 0.07782 | 0.21057 | 0.064087 | 0.082397 | 0.018311 | 0.059509 | -0.009155 | 0.1236 | 0.17395 | 0.10071 | 0.21515 | 121.6873 | -0.050354 | -0.045776 | 121.8979 | 121.7697 | 121.7514 | 0.082397 | 0.064087 | 121.6782 | -0.064087 | 0 | 121.8613 | 121.9025 | 121.788 | 0.2243 | 0.10986 | 0.21057 | 0.07782 | 0.1831 | 0.13275 | 0.073242 | 0.068664 | 121.7606 | 121.7468 | -0.1236 | -0.13275 | 121.7651 | 121.8109 | 121.6919 | 121.7056
727.8438 | 121.9894 | -121.701 | 0.14648 | -0.011291 | 0.056533 | 0.013971 | 0.0098673 | 1.915e-05 | -0.0055328 | 0.0017667 | -0.0015565 | 0.0022175 | 0.017994 | -0.0071029 | -0.0052231 | 0.018171 | 0.00042947 | 0.013733 | 0.086975 | -0.032043 | 0.068665 | 0.21973 | 0.10986 | 0.10071 | 0.059509 | 0.082397 | -0.018311 | 0.073242 | 0.19226 | 0.11902 | 0.19226 | 121.669 | -0.059509 | -0.077819 | 121.9208 | 121.8018 | 121.8109 | 0.13275 | 0.14191 | 121.6827 | -0.064087 | -0.073242 | 121.8933 | 121.8933 | 121.8201 | 0.21057 | 0.13733 | 0.25177 | 0.10071 | 0.21057 | 0.091553 | 0.11902 | 0.10071 | 121.788 | 121.7834 | -0.17853 | -0.16479 | 121.7697 | 121.7743 | 121.7148 | 121.7606
729.5156 | 121.9025 | -121.7331 | 0.16022 | -0.011291 | 0.057601 | 0.010767 | 0.012004 | -0.00062165 | -0.003183 | 0.0011257 | -0.0015565 | 0.0030719 | 0.019703 | -0.011803 | -0.0052231 | 0.01753 | -0.0021341 | -0.036621 | 0.1236 | -0.045776 | -0.054932 | 0.050354 | -0.045776 | -0.027466 | -0.10529 | 0.1236 | -0.059509 | -0.004578 | 0.036621 | -0.018311 | 0.13733 | 121.6873 | -0.036621 | -0.21515 | 121.7834 | 121.7056 | 121.6873 | 0.01831 | 0 | 121.6736 | -0.036621 | -0.16479 | 121.7697 | 121.8704 | 121.7148 | 0.19684 | 0.041198 | 0.09613 | -0.009156 | 0.09613 | 0.054931 | 0.16937 | 0.1831 | 121.8567 | 121.8567 | -0.20599 | -0.21973 | 121.6782 | 121.7285 | 121.6965 | 121.6278
731.25 | 121.9299 | -121.7377 | 0.15106 | -0.041809 | 0.052902 | 0.012262 | 0.010081 | -0.001476 | -0.004251 | -0.0050693 | -0.013763 | 0.0026447 | 0.019703 | -0.011803 | -0.0065049 | 0.020734 | -0.0010659 | -0.091553 | 0.1236 | -0.064087 | -0.054932 | 0.068665 | -0.013733 | -0.013733 | -0.082397 | 0.13275 | -0.050354 | 0 | 0.068665 | 0.009155 | 0.13275 | 121.6736 | -0.027466 | -0.20599 | 121.8063 | 121.7239 | 121.7239 | 0.050354 | 0.050354 | 121.6873 | -0.018311 | -0.15106 | 121.8063 | 121.8704 | 121.7468 | 0.18311 | 0.059509 | 0.13275 | 0.009155 | 0.11902 | 0.050354 | 0.18768 | 0.18311 | 121.8613 | 121.8704 | -0.21515 | -0.20142 | 121.6827 | 121.7377 | 121.6461 | 121.6553
733.0156 | 121.9391 | -121.7606 | 0.13733 | -0.018921 | 0.054183 | 0.014185 | 0.012431 | -0.0016898 | -0.00019224 | 0.0017667 | -0.0076599 | 0.0032855 | 0.018848 | -0.0088119 | -0.0050095 | 0.018812 | -0.0023477 | -0.086975 | 0.12817 | -0.054932 | -0.059509 | 0.054932 | -0.022888 | -0.004578 | -0.07782 | 0.12817 | -0.036621 | 0.009155 | 0.064087 | 0.036621 | 0.14648 | 121.7056 | -0.009155 | -0.19684 | 121.8155 | 121.756 | 121.7377 | 0.050354 | 0.032044 | 121.7239 | -0.009155 | -0.12817 | 121.8246 | 121.907 | 121.7972 | 0.18311 | 0.073242 | 0.10986 | -0.004577 | 0.10071 | 0.045776 | 0.18311 | 0.1648 | 121.8887 | 121.8887 | -0.19226 | -0.17395 | 121.701 | 121.7697 | 121.6736 | 121.6827
734.7031 | 121.9162 | -121.7651 | 0.16022 | -0.011291 | 0.056106 | 0.013544 | 0.010722 | 0.0040782 | -0.0023284 | -0.0033603 | -0.0046081 | 0.0024311 | 0.017566 | 0.0014419 | -0.0020187 | 0.018812 | 0.0023521 | -0.068665 | 0.13733 | -0.054932 | -0.082397 | 0.036621 | -0.059509 | -0.032043 | -0.11902 | 0.13275 | -0.064087 | 0.009155 | 0.032043 | -0.018311 | 0.13275 | 121.7102 | -0.022888 | -0.24261 | 121.8018 | 121.7331 | 121.7056 | 0.022889 | -0.004577 | 121.701 | -0.027466 | -0.15106 | 121.7972 | 121.8979 | 121.7468 | 0.19684 | 0.045776 | 0.091553 | -0.027465 | 0.09613 | 0.073242 | 0.19226 | 0.19684 | 121.9025 | 121.8979 | -0.21515 | -0.2243 | 121.6827 | 121.7743 | 121.6965 | 121.6461
736.4531 | 121.9208 | -121.7606 | 0.16479 | -0.0036622 | 0.055252 | 0.01333 | 0.010081 | -0.0023306 | -0.004251 | -0.0020785 | -0.010712 | 0.00050846 | 0.018207 | -0.0043259 | -0.0062913 | 0.017743 | 0.00085667 | -0.082397 | 0.13275 | -0.073242 | -0.07782 | 0.068665 | -0.018311 | -0.004578 | -0.10071 | 0.13275 | -0.050354 | -0.013733 | 0.059509 | 0.018311 | 0.11444 | 121.6873 | -0.032044 | -0.24261 | 121.8292 | 121.756 | 121.7422 | 0.068664 | 0.054931 | 121.7102 | -0.032044 | -0.17853 | 121.8201 | 121.875 | 121.7789 | 0.16479 | 0.068665 | 0.14191 | -0.004578 | 0.10986 | 0.036621 | 0.20599 | 0.18311 | 121.8933 | 121.8933 | -0.23804 | -0.21515 | 121.6827 | 121.7468 | 121.6782 | 121.6599
738.2031 | 121.9208 | -121.7468 | 0.16022 | -0.011291 | 0.055892 | 0.012048 | 0.012004 | -0.0019034 | -0.0040374 | -0.0029331 | -0.0015565 | 0.0039265 | 0.019062 | -0.0015487 | -0.0050095 | 0.017743 | -0.0038431 | -0.086975 | 0.13275 | -0.050354 | -0.068665 | 0.068665 | 0 | 0.018311 | -0.068665 | 0.1236 | -0.050354 | -0.004578 | 0.059509 | 0.004578 | 0.11902 | 121.6965 | -0.027466 | -0.22888 | 121.8155 | 121.7651 | 121.7468 | 0.068665 | 0.050354 | 121.6965 | -0.036621 | -0.16479 | 121.8063 | 121.8658 | 121.7514 | 0.16937 | 0.054932 | 0.11902 | -0.018311 | 0.10986 | 0.045776 | 0.18311 | 0.17395 | 121.8796 | 121.8704 | -0.21057 | -0.21057 | 121.6782 | 121.7422 | 121.6599 | 121.6782
739.9531 | 121.962 | -121.7468 | 0.15106 | -0.041809 | 0.054397 | 0.014612 | 0.010508 | 0.00066015 | -0.003183 | -0.0010105 | -0.0076599 | 0.0041401 | 0.017566 | -0.0058213 | -0.0033005 | 0.019239 | -0.0010659 | -0.041199 | 0.13275 | -0.032043 | -0.050354 | 0.086975 | 0.004578 | 0.013733 | -0.013733 | 0.11902 | -0.032043 | 0.045776 | 0.11444 | 0.045776 | 0.17395 | 121.7148 | -0.018311 | -0.20142 | 121.8338 | 121.7606 | 121.7514 | 0.045776 | 0.036621 | 121.7148 | -0.032043 | -0.10529 | 121.8613 | 121.9208 | 121.7926 | 0.20599 | 0.077819 | 0.11902 | -0.018311 | 0.14648 | 0.077819 | 0.16479 | 0.15106 | 121.8796 | 121.8658 | -0.18311 | -0.18311 | 121.6965 | 121.7926 | 121.7056 | 121.7331
741.625 | 121.9254 | -121.7468 | 0.15106 | -0.011291 | 0.054824 | 0.010553 | 0.010722 | -0.0019034 | -0.0040374 | -0.0027195 | -0.0076599 | 0.00093566 | 0.01778 | -0.0053939 | -0.0045823 | 0.01753 | 0.0017111 | -0.086975 | 0.11444 | -0.045776 | -0.086975 | 0.064087 | -0.022888 | 0 | -0.07782 | 0.11902 | -0.050354 | 0 | 0.086975 | 0.018311 | 0.14191 | 121.701 | -0.036621 | -0.23804 | 121.8109 | 121.7468 | 121.7239 | 0.045776 | 0.022888 | 121.6965 | -0.032043 | -0.15106 | 121.8338 | 121.8887 | 121.7651 | 0.19226 | 0.068665 | 0.10986 | -0.041199 | 0.13733 | 0.050354 | 0.16022 | 0.16937 | 121.8613 | 121.8658 | -0.19684 | -0.20142 | 121.6599 | 121.7468 | 121.6599 | 121.669
743.3594 | 121.9894 | -121.7239 | 0.14191 | -0.02655 | 0.056106 | 0.016534 | 0.0094399 | -0.00019445 | -0.0023284 | -0.00015591 | -0.0046081 | 0.0028583 | 0.018848 | -0.0068893 | -0.00073705 | 0.015821 | -0.0034159 | -0.041199 | 0.1236 | -0.045776 | -0.009155 | 0.12817 | 0.018311 | 0.018311 | 0.009155 | 0.11902 | -0.041199 | 0.054932 | 0.12817 | 0.054932 | 0.17853 | 121.6782 | -0.018311 | -0.15106 | 121.8521 | 121.7422 | 121.7422 | 0.064087 | 0.064087 | 121.6827 | -0.022888 | -0.086975 | 121.8521 | 121.9025 | 121.7789 | 0.21973 | 0.096131 | 0.17395 | 0.036621 | 0.16937 | 0.096131 | 0.16937 | 0.16022 | 121.8475 | 121.843 | -0.18768 | -0.18311 | 121.7148 | 121.7789 | 121.6827 | 121.7331
745.0938 | 121.9528 | -121.7468 | 0.16022 | -0.011291 | 0.052902 | 0.012476 | 0.011576 | -0.0033986 | -0.0040374 | -0.0059237 | -0.0076599 | 0.0013629 | 0.019703 | -0.010307 | -0.0030869 | 0.019239 | 0.00064307 | -0.073242 | 0.10986 | -0.050354 | -0.064087 | 0.064087 | -0.004578 | 0.004578 | -0.059509 | 0.10986 | -0.050354 | 0.041199 | 0.082397 | 0.050354 | 0.15564 | 121.6965 | -0.050354 | -0.2243 | 121.8109 | 121.7514 | 121.7422 | 0.054932 | 0.045776 | 121.6965 | -0.050354 | -0.11902 | 121.8292 | 121.9025 | 121.7972 | 0.20599 | 0.10071 | 0.11444 | -0.013733 | 0.13275 | 0.091553 | 0.16022 | 0.16022 | 121.8567 | 121.8567 | -0.21057 | -0.21057 | 121.6827 | 121.788 | 121.6736 | 121.6873
746.8281 | 122.0673 | -121.7056 | 0.12817 | 0.0039673 | 0.054611 | 0.013971 | 0.0085855 | 0.00044655 | -0.004251 | -0.0022921 | 0.0014953 | 8.1264e-05 | 0.01778 | -0.0049667 | -0.0020187 | 0.018171 | -0.0049111 | -0.022888 | 0.09613 | -0.027466 | 0.032043 | 0.20142 | 0.091553 | 0.11444 | 0.036621 | 0.09613 | -0.027466 | 0.1236 | 0.20142 | 0.14648 | 0.25177 | 121.6782 | -0.032044 | -0.096131 | 121.907 | 121.8201 | 121.7972 | 0.14191 | 0.11902 | 121.6782 | -0.032044 | -0.004578 | 121.907 | 121.9574 | 121.8521 | 0.27924 | 0.17395 | 0.22888 | 0.059509 | 0.22888 | 0.15106 | 0.1236 | 0.1236 | 121.8018 | 121.8018 | -0.15564 | -0.15564 | 121.7377 | 121.8292 | 121.6827 | 121.7422
748.5156 | 121.9894 | -121.7239 | 0.12817 | 0.0039673 | 0.056747 | 0.014612 | 0.012858 | -0.0019034 | -0.0019012 | -0.0031467 | 0.0014953 | 0.0034991 | 0.019916 | -0.0083847 | 0.00033115 | 0.019239 | -0.0046975 | -0.059509 | 0.1236 | -0.045776 | -0.050354 | 0.10071 | -0.018311 | 0.009155 | -0.064087 | 0.11444 | -0.036621 | 0.073242 | 0.1236 | 0.059509 | 0.18768 | 121.6782 | -0.004578 | -0.17853 | 121.8246 | 121.7331 | 121.7056 | 0.054931 | 0.027465 | 121.6873 | -0.013733 | -0.054932 | 121.8475 | 121.9116 | 121.7834 | 0.2243 | 0.09613 | 0.14648 | -0.004578 | 0.16022 | 0.10986 | 0.16937 | 0.15106 | 121.8475 | 121.8384 | -0.17395 | -0.1648 | 121.6736 | 121.7972 | 121.6644 | 121.6599
750.25 | 121.9803 | -121.7285 | 0.15106 | -0.011291 | 0.052261 | 0.012262 | 0.013713 | -0.00019445 | -0.0027556 | -0.0037875 | -0.0046081 | 0.0017901 | 0.019062 | -0.0051803 | -0.0033005 | 0.01753 | 2.068e-06 | -0.013733 | 0.12817 | -0.050354 | 0 | 0.13275 | 0.018311 | 0.032043 | 0.022888 | 0.10529 | -0.022888 | 0.064087 | 0.15106 | 0.07782 | 0.17853 | 121.6782 | -0.022888 | -0.15106 | 121.8613 | 121.7606 | 121.7468 | 0.082397 | 0.068665 | 121.7056 | -0.045776 | -0.086975 | 121.8796 | 121.907 | 121.8063 | 0.20142 | 0.10071 | 0.18311 | 0.050354 | 0.17395 | 0.086975 | 0.17853 | 0.12817 | 121.8567 | 121.8338 | -0.20142 | -0.17395 | 121.7285 | 121.7926 | 121.7148 | 121.7514
751.9375 | 121.9528 | -121.7514 | 0.15106 | -0.02655 | 0.054824 | 0.013971 | 0.010935 | -0.0025442 | -0.0038238 | -0.0042147 | -0.0046081 | 0.0015765 | 0.019489 | -0.0041123 | -0.0039413 | 0.017103 | 0.00042947 | -0.082397 | 0.1236 | -0.059509 | -0.07782 | 0.064087 | -0.013733 | 0.004578 | -0.073242 | 0.11444 | -0.045776 | 0.009155 | 0.091553 | 0.027466 | 0.14191 | 121.6919 | -0.027466 | -0.22888 | 121.8155 | 121.756 | 121.7377 | 0.064087 | 0.045776 | 121.7056 | -0.036621 | -0.14191 | 121.843 | 121.8933 | 121.7789 | 0.18768 | 0.073242 | 0.1236 | -0.018311 | 0.13733 | 0.054931 | 0.1831 | 0.16022 | 121.875 | 121.8658 | -0.21057 | -0.19684 | 121.6736 | 121.7606 | 121.669 | 121.6782
753.6719 | 121.962 | -121.7422 | 0.15106 | -0.02655 | 0.053329 | 0.012689 | 0.010508 | -0.0016898 | -0.0051056 | -0.0031467 | -0.010712 | 0.0020039 | 0.017353 | -0.010094 | -0.0024461 | 0.018171 | 0.0010703 | -0.082397 | 0.12817 | -0.059509 | -0.073242 | 0.068665 | 0 | 0.009155 | -0.054932 | 0.10529 | -0.041199 | 0.022888 | 0.10529 | 0.027466 | 0.16479 | 121.6827 | -0.022888 | -0.2243 | 121.8109 | 121.7514 | 121.7422 | 0.068664 | 0.059509 | 121.701 | -0.045776 | -0.12817 | 121.8475 | 121.907 | 121.7697 | 0.20599 | 0.068665 | 0.12817 | -0.013733 | 0.14649 | 0.064087 | 0.18768 | 0.14649 | 121.8704 | 121.8475 | -0.21057 | -0.19226 | 121.669 | 121.7651 | 121.6599 | 121.6873
755.4219 | 121.9162 | -121.7743 | 0.16937 | -0.011291 | 0.055252 | 0.011835 | 0.013285 | -0.0010488 | -0.0019012 | -0.0022921 | -0.0046081 | 0.0037127 | 0.019489 | -0.01458 | -0.0045823 | 0.016034 | -0.0025613 | -0.091553 | 0.12817 | -0.068665 | -0.068665 | 0.064087 | -0.004578 | 0.022888 | -0.07782 | 0.1236 | -0.045776 | -0.013733 | 0.059509 | 0.009155 | 0.13275 | 121.7056 | -0.041199 | -0.23804 | 121.8384 | 121.7972 | 121.7697 | 0.091553 | 0.064087 | 121.7285 | -0.045777 | -0.18311 | 121.8338 | 121.907 | 121.7834 | 0.17853 | 0.054931 | 0.13275 | 0 | 0.10528 | 0.032043 | 0.19684 | 0.16937 | 121.9025 | 121.8979 | -0.23804 | -0.21515 | 121.7056 | 121.7606 | 121.6827 | 121.6965
757.1562 | 122.0398 | -121.7331 | 0.1236 | -0.018921 | 0.055252 | 0.013544 | 0.0087991 | -0.002117 | -0.002542 | -0.0012241 | -0.0046081 | 0.00093566 | 0.018421 | -0.0013351 | -0.0030869 | 0.017957 | -0.00021153 | -0.050354 | 0.073242 | -0.022888 | -0.009155 | 0.13733 | 0.036621 | 0.064087 | -0.050354 | 0.082397 | -0.032043 | 0.068665 | 0.13733 | 0.073242 | 0.20142 | 121.7102 | -0.050354 | -0.13275 | 121.8704 | 121.7972 | 121.7697 | 0.086975 | 0.059509 | 121.701 | -0.041199 | -0.054931 | 121.8704 | 121.9345 | 121.8063 | 0.23346 | 0.10529 | 0.16022 | 0.013733 | 0.16937 | 0.10071 | 0.09613 | 0.11444 | 121.8063 | 121.8155 | -0.14648 | -0.15564 | 121.7239 | 121.8018 | 121.6827 | 121.6827
758.8906 | 122.0078 | -121.7194 | 0.15106 | -0.0036622 | 0.056533 | 0.014612 | 0.0098673 | -0.0012624 | 2.1362e-05 | 0.00027129 | -0.0015565 | 8.1264e-05 | 0.015857 | -0.0021897 | -0.0030869 | 0.016675 | -0.0017069 | 0.013733 | 0.068665 | -0.022888 | 0.054932 | 0.20599 | 0.10071 | 0.10529 | 0.050354 | 0.091553 | -0.036621 | 0.059509 | 0.16022 | 0.10071 | 0.17853 | 121.6965 | -0.082397 | -0.09613 | 121.9254 | 121.8246 | 121.8201 | 0.12817 | 0.1236 | 121.6827 | -0.059509 | -0.091553 | 121.8796 | 121.8979 | 121.8201 | 0.21515 | 0.13733 | 0.22888 | 0.07782 | 0.19684 | 0.09613 | 0.091553 | 0.12817 | 121.788 | 121.8109 | -0.17395 | -0.18768 | 121.7743 | 121.7789 | 121.7331 | 121.7697
760.5625 | 121.9574 | -121.7606 | 0.14648 | -0.0036622 | 0.053756 | 0.014398 | 0.012004 | -0.0010488 | -0.00019224 | 0.00027129 | -0.0015565 | 0.0032855 | 0.02248 | 0.00016027 | -0.00073705 | 0.019452 | 0.0012839 | -0.054932 | 0.13275 | -0.054932 | -0.068665 | 0.059509 | -0.050354 | -0.027466 | -0.022888 | 0.12817 | -0.054932 | 0.036621 | 0.073242 | 0.009155 | 0.14648 | 121.7056 | -0.013733 | -0.21515 | 121.8201 | 121.7331 | 121.7102 | 0.027466 | 0.004578 | 121.7056 | -0.01831 | -0.10986 | 121.8338 | 121.907 | 121.7697 | 0.20142 | 0.064087 | 0.11444 | -0.013733 | 0.12817 | 0.091553 | 0.18768 | 0.18311 | 121.8933 | 121.8887 | -0.20142 | -0.20142 | 121.6919 | 121.7972 | 121.7056 | 121.7377
762.2969 | 122.0078 | -121.7148 | 0.14648 | -0.011291 | 0.052261 | 0.014612 | 0.010295 | -0.0025442 | -0.0040374 | -0.0033603 | -0.0046081 | 0.0015765 | 0.020343 | -0.0047531 | -0.0024461 | 0.019452 | -0.0010659 | -0.059509 | 0.086975 | -0.018311 | -0.013733 | 0.15106 | 0.050354 | 0.068665 | 0.022888 | 0.10529 | -0.036621 | 0.082397 | 0.16479 | 0.11444 | 0.21057 | 121.6965 | -0.059509 | -0.16022 | 121.8658 | 121.7834 | 121.7651 | 0.086976 | 0.068665 | 121.6782 | -0.041198 | -0.064087 | 121.8796 | 121.9254 | 121.8292 | 0.24719 | 0.15106 | 0.16937 | 0.004578 | 0.20142 | 0.11902 | 0.10529 | 0.14191 | 121.8018 | 121.8201 | -0.16479 | -0.18311 | 121.701 | 121.7972 | 121.6553 | 121.7377
763.9688 | 122.0718 | -121.7102 | 0.13733 | 0.0039673 | 0.053543 | 0.012689 | 0.0090127 | -0.004894 | -0.0033966 | -0.00058311 | -0.0046081 | 0.0013629 | 0.017139 | -0.0073165 | -0.0028733 | 0.018384 | -0.00021153 | 0.018311 | 0.082397 | -0.027466 | 0.09613 | 0.24719 | 0.14191 | 0.14191 | 0.12817 | 0.09613 | -0.013733 | 0.1236 | 0.21057 | 0.16479 | 0.24261 | 121.6827 | -0.054932 | -0.041199 | 121.9574 | 121.8521 | 121.8521 | 0.16937 | 0.16937 | 121.6965 | -0.041199 | -0.013733 | 121.9208 | 121.9528 | 121.875 | 0.25635 | 0.17853 | 0.27466 | 0.1236 | 0.2243 | 0.13733 | 0.10986 | 0.10986 | 121.7926 | 121.8063 | -0.16479 | -0.15106 | 121.8063 | 121.8338 | 121.7285 | 121.8384
765.7188 | 121.9391 | -121.7606 | 0.16022 | -0.02655 | 0.054397 | 0.012903 | 0.0098673 | -0.0040396 | -0.0023284 | -0.0042147 | -0.0046081 | 0.0022175 | 0.019916 | -0.0098801 | -0.0052231 | 0.017743 | -0.0012795 | -0.07782 | 0.10986 | -0.036621 | -0.073242 | 0.045776 | -0.018311 | 0 | -0.068665 | 0.1236 | -0.050354 | -0.009155 | 0.059509 | 0.022888 | 0.12817 | 121.7239 | -0.050354 | -0.23346 | 121.8063 | 121.7606 | 121.7422 | 0.036621 | 0.01831 | 121.7102 | -0.036621 | -0.16937 | 121.8201 | 121.8887 | 121.7834 | 0.17853 | 0.073242 | 0.082397 | -0.036621 | 0.10986 | 0.041199 | 0.14648 | 0.17395 | 121.8704 | 121.8842 | -0.19684 | -0.21057 | 121.6873 | 121.7514 | 121.6827 | 121.6919
767.4531 | 122.0215 | -121.7239 | 0.14191 | -0.0036622 | 0.053543 | 0.012689 | 0.0081583 | -0.0019034 | -0.002542 | -0.00058311 | -0.0046081 | 0.00050846 | 0.019703 | -0.0028305 | -0.0018051 | 0.01753 | -0.0019205 | -0.032043 | 0.086975 | -0.022888 | -0.013733 | 0.13733 | 0.032043 | 0.050354 | 0.022888 | 0.07782 | -0.022888 | 0.059509 | 0.14648 | 0.082397 | 0.19684 | 121.7011 | -0.054932 | -0.15564 | 121.8613 | 121.7743 | 121.756 | 0.073242 | 0.054931 | 121.7011 | -0.064087 | -0.082398 | 121.8704 | 121.9208 | 121.8063 | 0.21973 | 0.10528 | 0.16022 | 0.009155 | 0.16937 | 0.082397 | 0.10986 | 0.10071 | 121.8109 | 121.8018 | -0.16479 | -0.16479 | 121.7102 | 121.7834 | 121.6919 | 121.7468
769.1875 | 122.0398 | -121.7056 | 0.10529 | 0.0039673 | 0.054611 | 0.013544 | 0.011363 | 0.00044655 | -0.002542 | -0.00079691 | 0.0014953 | 0.0032855 | 0.018634 | -0.0056075 | -0.00052345 | 0.019025 | 0.0012839 | 0 | 0.10529 | -0.032043 | 0.041199 | 0.15106 | 0.036621 | 0.091553 | 0.07782 | 0.07782 | -0.027466 | 0.13275 | 0.16479 | 0.10986 | 0.25177 | 121.6736 | 0 | -0.064087 | 121.8567 | 121.7972 | 121.7422 | 0.1236 | 0.068664 | 121.6782 | -0.027466 | 0.027465 | 121.8704 | 121.9574 | 121.8155 | 0.27924 | 0.13733 | 0.18311 | 0.073242 | 0.19226 | 0.16022 | 0.13733 | 0.10529 | 121.8109 | 121.7834 | -0.13733 | -0.13275 | 121.7468 | 121.8384 | 121.7056 | 121.7834
770.9375 | 122.0352 | -121.701 | 0.12817 | -0.018921 | 0.056747 | 0.012689 | 0.0098673 | 0.0019418 | -0.0012604 | -0.00036951 | -0.0076599 | 0.0020039 | 0.020343 | -0.0038987 | -0.00030965 | 0.018812 | -0.0059793 | 0 | 0.073242 | 0.009155 | 0.064087 | 0.20599 | 0.059509 | 0.082397 | 0.10986 | 0.068665 | 0 | 0.11444 | 0.17853 | 0.10529 | 0.22888 | 121.7102 | -0.054932 | -0.064087 | 121.907 | 121.7834 | 121.7606 | 0.073242 | 0.050354 | 121.701 | -0.059509 | -0.013733 | 121.8796 | 121.9299 | 121.8063 | 0.22888 | 0.10529 | 0.19684 | 0.054932 | 0.17853 | 0.11444 | 0.064087 | 0.068665 | 121.7743 | 121.7697 | -0.11902 | -0.12817 | 121.7651 | 121.8155 | 121.701 | 121.8109
772.6094 | 121.9254 | -121.7697 | 0.16937 | -0.0036622 | 0.055679 | 0.014825 | 0.012431 | -0.0010488 | -0.00083304 | -0.00036951 | 0.0014953 | 0.0032855 | 0.019275 | -0.0036849 | -0.00095065 | 0.01753 | -0.0032021 | -0.068665 | 0.13733 | -0.073242 | -0.073242 | 0.036621 | -0.064087 | -0.036621 | -0.054932 | 0.11444 | -0.064087 | 0 | 0.032043 | -0.027466 | 0.12817 | 121.6965 | -0.032044 | -0.24261 | 121.8063 | 121.7331 | 121.7056 | 0.036621 | 0.009155 | 121.7056 | -0.054932 | -0.16937 | 121.8018 | 121.8979 | 121.7422 | 0.19226 | 0.036621 | 0.10986 | 0 | 0.09613 | 0.064087 | 0.21057 | 0.17853 | 121.907 | 121.8842 | -0.24261 | -0.23346 | 121.6965 | 121.7697 | 121.701 | 121.7148
774.3438 | 121.9757 | -121.7514 | 0.14648 | 0.0039673 | 0.056106 | 0.015466 | 0.012858 | -0.001476 | -0.0019012 | -0.0031467 | -0.0076599 | 0.0028583 | 0.018421 | -0.011162 | -0.0030869 | 0.018384 | -0.0010659 | -0.022888 | 0.1236 | -0.054932 | -0.004578 | 0.13733 | 0.004578 | 0.041199 | 0.032043 | 0.1236 | -0.045776 | 0.064087 | 0.12817 | 0.054932 | 0.1831 | 121.6965 | -0.022888 | -0.15106 | 121.8887 | 121.7926 | 121.756 | 0.096131 | 0.05951 | 121.7056 | -0.022888 | -0.082397 | 121.8796 | 121.9345 | 121.8063 | 0.22888 | 0.10071 | 0.19226 | 0.050354 | 0.17395 | 0.10986 | 0.17853 | 0.16937 | 121.875 | 121.875 | -0.20142 | -0.19226 | 121.7468 | 121.8155 | 121.7285 | 121.7834
776.0938 | 122.1085 | -121.7239 | 0.12817 | -0.011291 | 0.051406 | 0.012689 | 0.0090127 | 0.0010874 | -0.0027556 | -0.0031467 | -0.0015565 | -0.00034614 | 0.017353 | 0.0059281 | -0.0013779 | 0.019452 | -0.0012795 | -0.004578 | 0.086975 | -0.027466 | 0.068665 | 0.23346 | 0.10986 | 0.13275 | 0.14191 | 0.082397 | -0.022888 | 0.11444 | 0.2243 | 0.17853 | 0.24261 | 121.6965 | -0.041199 | -0.059509 | 121.9574 | 121.8567 | 121.8338 | 0.16022 | 0.13733 | 121.7011 | -0.045777 | -0.013733 | 121.9482 | 121.9666 | 121.9025 | 0.2655 | 0.20142 | 0.26093 | 0.096131 | 0.24719 | 0.13733 | 0.11444 | 0.10528 | 121.8109 | 121.8063 | -0.15564 | -0.15106 | 121.7926 | 121.8384 | 121.7194 | 121.8658
777.8281 | 122.0169 | -121.7239 | 0.09613 | -0.02655 | 0.05397 | 0.014612 | 0.010081 | -0.002117 | -0.0016876 | -0.0012241 | -0.0046081 | -0.00055974 | 0.017353 | -0.0038987 | -0.0035141 | 0.019025 | -0.00042513 | -0.013733 | 0.086975 | 0.004578 | 0.041199 | 0.18768 | 0.032043 | 0.059509 | 0.082397 | 0.068665 | -0.013733 | 0.09613 | 0.15564 | 0.10071 | 0.21515 | 121.7285 | -0.009155 | -0.054931 | 121.9116 | 121.7834 | 121.756 | 0.054931 | 0.027465 | 121.7102 | -0.027465 | 0 | 121.8796 | 121.9391 | 121.8246 | 0.22888 | 0.11444 | 0.1831 | 0.036621 | 0.16937 | 0.10986 | 0.082397 | 0.082398 | 121.8109 | 121.7926 | -0.091552 | -0.10986 | 121.7651 | 121.8201 | 121.7102 | 121.8063
779.5156 | 122.0398 | -121.7285 | 0.12817 | -0.0036622 | 0.054397 | 0.014825 | 0.0075173 | -0.00062165 | -0.0019012 | -0.00036951 | -0.0015565 | 0.00029486 | 0.019489 | 0.0010147 | -0.0054367 | 0.017743 | -0.0032021 | -0.022888 | 0.10071 | -0.018311 | 0.018311 | 0.16022 | 0.064087 | 0.086975 | 0.050354 | 0.09613 | -0.036621 | 0.10071 | 0.19226 | 0.13275 | 0.22888 | 121.7102 | -0.027466 | -0.10986 | 121.8887 | 121.8155 | 121.7926 | 0.10529 | 0.082398 | 121.6919 | -0.032044 | -0.027466 | 121.9208 | 121.9574 | 121.8613 | 0.2655 | 0.16937 | 0.17853 | 0.036622 | 0.22888 | 0.13733 | 0.11902 | 0.13275 | 121.8292 | 121.8246 | -0.14649 | -0.1648 | 121.7468 | 121.8292 | 121.7056 | 121.7789
781.2656 | 121.9299 | -121.7377 | 0.14648 | 0.0039673 | 0.054611 | 0.014825 | 0.013499 | 0.0010874 | -0.00083304 | -0.0029331 | -0.0046081 | 0.0045673 | 0.020984 | -0.0038987 | -0.0033005 | 0.018384 | 0.0012839 | -0.018311 | 0.12817 | -0.059509 | -0.009155 | 0.11444 | -0.004578 | -0.004578 | -0.004578 | 0.11902 | -0.054932 | 0.018311 | 0.073242 | -0.013733 | 0.13275 | 121.6782 | -0.01831 | -0.15564 | 121.8521 | 121.7331 | 121.7331 | 0.054931 | 0.054931 | 121.6827 | -0.027465 | -0.12817 | 121.8109 | 121.8704 | 121.7239 | 0.18768 | 0.041199 | 0.17395 | 0.050354 | 0.12817 | 0.073243 | 0.18768 | 0.17395 | 121.8658 | 121.8567 | -0.20599 | -0.20142 | 121.7285 | 121.756 | 121.7194 | 121.7331
783 | 121.9574 | -121.7514 | 0.16022 | -0.018921 | 0.055252 | 0.014398 | 0.010935 | 0.00023275 | -0.0023284 | -0.0022921 | -0.0046081 | 0.0032855 | 0.019062 | -0.0085983 | -0.0043687 | 0.014966 | -0.0029885 | -0.022888 | 0.13733 | -0.054932 | 0.009155 | 0.13275 | 0.018311 | 0.018311 | 0.022888 | 0.10986 | -0.045776 | 0.036621 | 0.11444 | 0.036621 | 0.15564 | 121.6965 | -0.022888 | -0.15106 | 121.8842 | 121.7697 | 121.7697 | 0.073243 | 0.073243 | 121.7056 | -0.050354 | -0.1236 | 121.8658 | 121.907 | 121.788 | 0.20142 | 0.082397 | 0.18768 | 0.064087 | 0.16022 | 0.082397 | 0.19226 | 0.15564 | 121.8887 | 121.8613 | -0.21515 | -0.20599 | 121.7606 | 121.788 | 121.7285 | 121.7743
784.6719 | 121.9528 | -121.756 | 0.16022 | -0.0036622 | 0.053756 | 0.01333 | 0.010935 | -0.0010488 | -0.0036102 | -0.0052829 | -0.0015565 | 0.00093566 | 0.018207 | -0.0075301 | -0.0047959 | 0.018598 | -0.0019205 | -0.022888 | 0.10071 | -0.032043 | 0.018311 | 0.15564 | 0.059509 | 0.064087 | 0 | 0.11902 | -0.041199 | 0.009155 | 0.11444 | 0.032043 | 0.13733 | 121.7239 | -0.059509 | -0.14191 | 121.9116 | 121.8201 | 121.8155 | 0.09613 | 0.091552 | 121.7148 | -0.041198 | -0.15106 | 121.8704 | 121.8933 | 121.788 | 0.17853 | 0.073242 | 0.18768 | 0.050354 | 0.15564 | 0.050354 | 0.13275 | 0.16022 | 121.8567 | 121.875 | -0.19226 | -0.20142 | 121.7743 | 121.7651 | 121.7331 | 121.756
786.4219 | 121.9757 | -121.7422 | 0.14648 | -0.018921 | 0.05632 | 0.015253 | 0.012217 | 0.00301 | -0.003183 | 0.00027129 | -0.010712 | 0.0030719 | 0.018634 | -0.017998 | -0.0024461 | 0.016889 | -0.00063873 | -0.045776 | 0.11902 | -0.041199 | -0.032043 | 0.086975 | 0.004578 | 0.027466 | -0.004578 | 0.11902 | -0.041199 | 0.050354 | 0.13733 | 0.050354 | 0.15564 | 121.701 | -0.027465 | -0.17853 | 121.8292 | 121.7697 | 121.7468 | 0.068665 | 0.045777 | 121.701 | -0.027465 | -0.09613 | 121.8796 | 121.8979 | 121.7926 | 0.19684 | 0.091553 | 0.12817 | 0.009156 | 0.17853 | 0.091553 | 0.16022 | 0.16022 | 121.8613 | 121.8613 | -0.18768 | -0.18768 | 121.7102 | 121.7926 | 121.6965 | 121.7377
788.1719 | 121.9391 | -121.6827 | 0.14191 | -0.011291 | 0.078109 | 0.011835 | 0.035716 | 0.0021556 | -0.0023284 | -0.0018649 | -0.0046081 | 0.0034991 | 0.018634 | -0.0077439 | -0.0013779 | 0.016675 | -0.0038431 | -0.032043 | 0.091553 | -0.050354 | -0.004578 | 0.1236 | 0 | 0.032043 | 0.009155 | 0.10071 | -0.045776 | 0.059509 | 0.11902 | 0.059509 | 0.16937 | 121.6324 | -0.050354 | -0.14649 | 121.8063 | 121.7148 | 121.6827 | 0.082397 | 0.050354 | 121.637 | -0.041199 | -0.082398 | 121.8018 | 121.8521 | 121.7422 | 0.21515 | 0.10528 | 0.17395 | 0.045776 | 0.16479 | 0.10528 | 0.14191 | 0.14648 | 121.7743 | 121.7834 | -0.19226 | -0.18768 | 121.6782 | 121.7422 | 121.6507 | 121.6919
789.9219 | 122.0215 | -121.6461 | 0.11444 | -0.011291 | 0.078109 | 0.014398 | 0.033152 | 0.0015146 | -0.0016876 | -0.0014377 | -0.0015565 | 0.0039265 | 0.019275 | -0.0011215 | -0.0020187 | 0.019239 | -0.0040567 | 0 | 0.073242 | -0.018311 | 0.045776 | 0.1831 | 0.059509 | 0.073242 | 0.10071 | 0.073242 | -0.036621 | 0.13275 | 0.1831 | 0.11902 | 0.2243 | 121.6278 | -0.041199 | -0.068665 | 121.8292 | 121.7194 | 121.7056 | 0.091553 | 0.07782 | 121.6095 | -0.041199 | 0.01831 | 121.8292 | 121.8704 | 121.7651 | 0.26093 | 0.15564 | 0.20142 | 0.064087 | 0.21973 | 0.16937 | 0.091553 | 0.10986 | 121.7194 | 121.7194 | -0.13275 | -0.15106 | 121.6919 | 121.7789 | 121.6461 | 121.7468
791.5938 | 121.9162 | -121.7194 | 0.16022 | -0.03418 | 0.0764 | 0.011835 | 0.034861 | -0.0016898 | -0.0027556 | -0.0010105 | -0.010712 | 0.0022175 | 0.019916 | -0.0073165 | -0.0045823 | 0.017957 | 0.0019247 | -0.091553 | 0.10986 | -0.064087 | -0.10529 | 0.036621 | -0.050354 | -0.022888 | -0.086975 | 0.1236 | -0.064087 | 0 | 0.068665 | 0 | 0.1236 | 121.6553 | -0.050354 | -0.2655 | 121.756 | 121.6965 | 121.669 | 0.041199 | 0.013733 | 121.6553 | -0.036621 | -0.16022 | 121.788 | 121.843 | 121.7194 | 0.18768 | 0.064087 | 0.10071 | -0.041199 | 0.13275 | 0.064087 | 0.17395 | 0.18768 | 121.8292 | 121.843 | -0.2243 | -0.2243 | 121.6141 | 121.7194 | 121.6278 | 121.6324
793.3281 | 121.9025 | -121.7285 | 0.13733 | -0.0036622 | 0.078964 | 0.014398 | 0.035502 | 0.0032236 | -0.001474 | 0.0011257 | -0.0046081 | 0.0041401 | 0.019916 | -0.0058213 | -0.0018051 | 0.019239 | -0.00021153 | -0.07782 | 0.1236 | -0.054932 | -0.09613 | 0.045776 | -0.050354 | -0.036621 | -0.07782 | 0.09613 | -0.068665 | 0.009155 | 0.032043 | -0.022888 | 0.10986 | 121.6736 | -0.013733 | -0.23346 | 121.7743 | 121.6919 | 121.6782 | 0.018311 | 0.004578 | 121.6599 | -0.041199 | -0.12817 | 121.7606 | 121.8384 | 121.7056 | 0.17853 | 0.045777 | 0.10071 | -0.041198 | 0.10071 | 0.07782 | 0.17853 | 0.16479 | 121.8521 | 121.8246 | -0.19226 | -0.20599 | 121.6324 | 121.7377 | 121.6507 | 121.6507
795 | 121.907 | -121.7514 | 0.13733 | -0.0036622 | 0.077468 | 0.016534 | 0.034861 | 0.005787 | -0.0040374 | -0.0010105 | 0.0014953 | 0.0041401 | 0.021625 | -0.010735 | -0.0015915 | 0.018171 | -0.00063873 | -0.050354 | 0.10529 | -0.054932 | -0.054932 | 0.086975 | -0.045776 | -0.027466 | -0.041199 | 0.11902 | -0.064087 | 0 | 0.050354 | -0.009155 | 0.11444 | 121.6965 | -0.032043 | -0.19226 | 121.8384 | 121.7239 | 121.7056 | 0.027466 | 0.009156 | 121.6873 | -0.01831 | -0.13733 | 121.8018 | 121.8658 | 121.7422 | 0.17853 | 0.054932 | 0.14191 | 0 | 0.11444 | 0.064087 | 0.16022 | 0.18311 | 121.8567 | 121.8704 | -0.19226 | -0.20142 | 121.6965 | 121.7514 | 121.701 | 121.7102
796.7344 | 122.0261 | -121.7148 | 0.11444 | -0.018921 | 0.076827 | 0.014825 | 0.032939 | -0.001476 | -0.0023284 | -0.0027195 | -0.013763 | 0.0017901 | 0.017994 | -0.0056075 | 0.00075835 | 0.017743 | -0.0023477 | 0.004578 | 0.059509 | -0.009155 | 0.041199 | 0.20142 | 0.059509 | 0.091553 | 0.091553 | 0.064087 | -0.022888 | 0.10986 | 0.18768 | 0.1236 | 0.2243 | 121.7056 | -0.054932 | -0.073242 | 121.9162 | 121.8063 | 121.7743 | 0.10071 | 0.068664 | 121.6919 | -0.050354 | -0.004578 | 121.9025 | 121.9391 | 121.8384 | 0.24719 | 0.14648 | 0.21057 | 0.050354 | 0.21057 | 0.13275 | 0.068664 | 0.086975 | 121.7743 | 121.7789 | -0.1236 | -0.13733 | 121.756 | 121.8246 | 121.7194 | 121.8063
798.4688 | 121.994 | -121.7239 | 0.11444 | 0.011597 | 0.075759 | 0.014825 | 0.033793 | -0.001476 | -0.0012604 | -0.0014377 | -0.0046081 | 0.0047809 | 0.01778 | -0.0038987 | -0.0013779 | 0.018384 | -0.0040567 | -0.073242 | 0.10071 | -0.073242 | -0.054932 | 0.082397 | -0.036621 | 0.004578 | 0.009155 | 0.09613 | -0.045776 | 0.07782 | 0.13275 | 0.073242 | 0.17395 | 121.6507 | -0.013733 | -0.16937 | 121.8063 | 121.7285 | 121.6873 | 0.07782 | 0.036621 | 121.6782 | -0.018311 | -0.036621 | 121.8567 | 121.8979 | 121.7972 | 0.21973 | 0.11902 | 0.15564 | 0.01831 | 0.17853 | 0.1236 | 0.17395 | 0.14191 | 121.8246 | 121.8201 | -0.18768 | -0.16022 | 121.669 | 121.8018 | 121.6507 | 121.7331
800.2031 | 122.0352 | -121.6873 | 0.10529 | 0.0039673 | 0.076187 | 0.014612 | 0.032511 | 0.0049326 | -0.0027556 | -0.0018649 | -0.0076599 | 0.0028583 | 0.016925 | -0.0066757 | -9.605e-05 | 0.020521 | -0.00063873 | 0.013733 | 0.086975 | -0.027466 | 0.054932 | 0.18768 | 0.064087 | 0.068665 | 0.073242 | 0.054932 | -0.022888 | 0.12817 | 0.19684 | 0.10986 | 0.23804 | 121.6599 | -0.018311 | -0.050354 | 121.875 | 121.756 | 121.7514 | 0.096131 | 0.091553 | 121.6644 | -0.050354 | 0.022888 | 121.8842 | 121.9254 | 121.7972 | 0.26093 | 0.13275 | 0.21515 | 0.082398 | 0.21973 | 0.15106 | 0.11444 | 0.07782 | 121.7743 | 121.7422 | -0.13275 | -0.12817 | 121.7422 | 121.8155 | 121.701 | 121.7606
801.9375 | 121.9482 | -121.7606 | 0.13275 | -0.018921 | 0.076614 | 0.012262 | 0.033793 | 0.0010874 | -0.0044646 | 0.00069849 | -0.0046081 | 0.0054217 | 0.016712 | -0.0032577 | -0.0060777 | 0.016889 | -0.0032021 | -0.091553 | 0.10986 | -0.054932 | -0.07782 | 0.041199 | -0.018311 | -0.018311 | -0.082397 | 0.091553 | -0.054932 | -0.009155 | 0.064087 | 0 | 0.1236 | 121.7056 | -0.022888 | -0.21057 | 121.8018 | 121.7422 | 121.7422 | 0.036621 | 0.036621 | 121.7056 | -0.041198 | -0.14191 | 121.8246 | 121.8842 | 121.7606 | 0.17853 | 0.054932 | 0.096131 | -0.022888 | 0.11902 | 0.045777 | 0.16479 | 0.14649 | 121.8704 | 121.8521 | -0.18768 | -0.18768 | 121.6827 | 121.7514 | 121.669 | 121.6782
803.625 | 121.9528 | -121.7422 | 0.12817 | -0.011291 | 0.076187 | 0.013544 | 0.032939 | -0.0012624 | -0.0036102 | -0.0010105 | -0.0046081 | 0.0045673 | 0.018848 | -0.00090793 | -0.0043687 | 0.019666 | 0.0023521 | -0.041199 | 0.09613 | -0.050354 | -0.032043 | 0.11444 | 0.009155 | 0.032043 | 0 | 0.10529 | -0.045776 | 0.041199 | 0.12817 | 0.054932 | 0.16937 | 121.6919 | -0.032044 | -0.16022 | 121.8567 | 121.7743 | 121.7514 | 0.082397 | 0.059509 | 121.6965 | -0.022888 | -0.086975 | 121.8704 | 121.9116 | 121.7972 | 0.21515 | 0.10071 | 0.16479 | 0.018311 | 0.17395 | 0.086975 | 0.14648 | 0.15106 | 121.8384 | 121.8475 | -0.17853 | -0.17395 | 121.7102 | 121.7834 | 121.701 | 121.7422
805.375 | 121.9711 | -121.7422 | 0.13733 | -0.02655 | 0.078109 | 0.015466 | 0.033793 | 0.0060008 | -0.0036102 | -0.0033603 | -0.0076599 | 0.0030719 | 0.019062 | -5.3326e-05 | -0.0047959 | 0.017103 | -0.00063873 | -0.036621 | 0.11444 | -0.050354 | -0.027466 | 0.12817 | 0.013733 | 0.027466 | 0.022888 | 0.10529 | -0.027466 | 0.054932 | 0.10529 | 0.064087 | 0.15564 | 121.6919 | -0.022888 | -0.16479 | 121.8704 | 121.7697 | 121.756 | 0.07782 | 0.064087 | 121.7148 | -0.032043 | -0.082397 | 121.8475 | 121.8979 | 121.8063 | 0.18311 | 0.091553 | 0.17853 | 0.022888 | 0.13275 | 0.082398 | 0.16479 | 0.13275 | 121.8567 | 121.8475 | -0.18768 | -0.16479 | 121.7148 | 121.7972 | 121.7056 | 121.7651
807.1094 | 121.9208 | -121.756 | 0.14191 | -0.011291 | 0.076827 | 0.014398 | 0.031657 | -0.0068166 | -0.0019012 | -0.0025057 | -0.010712 | 0.0026447 | 0.018421 | -0.0034713 | -0.0039413 | 0.017316 | 0.0032065 | -0.036621 | 0.10071 | -0.050354 | -0.009155 | 0.11902 | 0.050354 | 0.041199 | -0.013733 | 0.10529 | -0.064087 | 0 | 0.09613 | 0.018311 | 0.11902 | 121.7056 | -0.041199 | -0.15106 | 121.875 | 121.7972 | 121.8063 | 0.091553 | 0.10071 | 121.6919 | -0.036621 | -0.14191 | 121.8521 | 121.875 | 121.7743 | 0.18311 | 0.082398 | 0.16937 | 0.041199 | 0.16022 | 0.064087 | 0.15106 | 0.16937 | 121.8567 | 121.8613 | -0.19226 | -0.20599 | 121.7468 | 121.756 | 121.7194 | 121.7422
808.8438 | 121.9162 | -121.7834 | 0.13733 | -0.011291 | 0.075973 | 0.017389 | 0.032084 | -0.001476 | -0.003183 | -0.0014377 | -0.0015565 | 0.0026447 | 0.018421 | -0.00090793 | -0.0047959 | 0.01753 | -0.0017069 | -0.041199 | 0.091553 | -0.036621 | -0.018311 | 0.11444 | 0.009155 | 0.027466 | -0.032043 | 0.11444 | -0.054932 | -0.018311 | 0.086975 | 0.004578 | 0.11902 | 121.7468 | -0.045776 | -0.15564 | 121.8979 | 121.8109 | 121.7926 | 0.064087 | 0.045776 | 121.7285 | -0.022888 | -0.15564 | 121.8704 | 121.9025 | 121.788 | 0.17395 | 0.05951 | 0.15106 | 0.01831 | 0.14191 | 0.036621 | 0.12817 | 0.16937 | 121.875 | 121.8979 | -0.17395 | -0.19226 | 121.7651 | 121.7651 | 121.7422 | 121.7514
810.5312 | 122.0398 | -121.7239 | 0.1236 | -0.0036622 | 0.07405 | 0.01333 | 0.032084 | -0.003185 | -0.0033966 | -0.0061373 | -0.0015565 | 0.0030719 | 0.018421 | 0.00080107 | -0.0018051 | 0.017103 | -0.0053385 | -0.050354 | 0.086975 | -0.018311 | 0 | 0.16479 | 0.068665 | 0.091553 | 0.054932 | 0.07782 | -0.027466 | 0.09613 | 0.19226 | 0.12817 | 0.21515 | 121.7056 | -0.036621 | -0.1236 | 121.8887 | 121.8155 | 121.7926 | 0.10986 | 0.086976 | 121.6965 | -0.045776 | -0.027466 | 121.9162 | 121.9391 | 121.8521 | 0.24261 | 0.15564 | 0.18311 | 0.018311 | 0.21973 | 0.1236 | 0.10529 | 0.10529 | 121.8109 | 121.8018 | -0.14191 | -0.15106 | 121.7239 | 121.8201 | 121.6736 | 121.7789
812.2656 | 121.9025 | -121.756 | 0.15564 | 0.011597 | 0.07875 | 0.016321 | 0.034007 | -0.002117 | -0.0010468 | -0.0014377 | -0.0015565 | 0.0049945 | 0.018634 | -0.0053939 | -0.0028733 | 0.016248 | 0.0014975 | -0.054932 | 0.10986 | -0.036621 | -0.068665 | 0.050354 | -0.054932 | -0.022888 | -0.041199 | 0.11902 | -0.059509 | 0 | 0.041199 | -0.032043 | 0.10986 | 121.7194 | -0.045777 | -0.22431 | 121.8063 | 121.7331 | 121.701 | 0.013733 | -0.018311 | 121.6965 | -0.036621 | -0.15564 | 121.7972 | 121.8658 | 121.7239 | 0.16937 | 0.027466 | 0.086975 | -0.032044 | 0.10071 | 0.059509 | 0.14648 | 0.17853 | 121.8658 | 121.875 | -0.19226 | -0.21515 | 121.6873 | 121.756 | 121.701 | 121.7148
813.9375 | 122.0398 | -121.7056 | 0.11444 | -0.0036622 | 0.0764 | 0.015894 | 0.032084 | -0.0019034 | -0.0027556 | -0.0027195 | -0.0015565 | 0.0013629 | 0.018421 | -0.0024033 | 0.0018265 | 0.020734 | -0.0014931 | 0.009155 | 0.073242 | -0.018311 | 0.054932 | 0.20599 | 0.054932 | 0.07782 | 0.091553 | 0.054932 | 0 | 0.1236 | 0.19684 | 0.11902 | 0.23346 | 121.6873 | -0.041199 | -0.059509 | 121.9116 | 121.7834 | 121.7606 | 0.096131 | 0.073243 | 121.7056 | -0.059509 | 0.009155 | 121.9025 | 121.9391 | 121.8246 | 0.23346 | 0.11902 | 0.22431 | 0.073243 | 0.19684 | 0.1236 | 0.091553 | 0.054932 | 121.7789 | 121.7606 | -0.13275 | -0.11444 | 121.7606 | 121.8292 | 121.7148 | 121.7972
815.6719 | 122.0123 | -121.7285 | 0.13275 | -0.018921 | 0.073837 | 0.014398 | 0.031443 | -0.002117 | -0.0029694 | -0.0027195 | -0.0046081 | 0.0015765 | 0.019489 | 0.0057145 | -0.0030869 | 0.01988 | 0.00085667 | -0.054932 | 0.10071 | -0.027466 | -0.009155 | 0.12817 | 0.018311 | 0.045776 | -0.013733 | 0.086975 | -0.059509 | 0.054932 | 0.13275 | 0.09613 | 0.16937 | 121.701 | -0.032043 | -0.14191 | 121.8567 | 121.7743 | 121.7468 | 0.073242 | 0.045777 | 121.669 | -0.045776 | -0.077819 | 121.8613 | 121.8979 | 121.8246 | 0.22888 | 0.15564 | 0.15564 | 0.018311 | 0.19226 | 0.11444 | 0.12817 | 0.14648 | 121.8292 | 121.8155 | -0.16022 | -0.19226 | 121.7194 | 121.7834 | 121.6736 | 121.7148
817.4062 | 121.9757 | -121.756 | 0.13733 | -0.011291 | 0.078323 | 0.012476 | 0.034861 | 0.00044655 | -0.004251 | -0.0046421 | -0.0015565 | 0.0058491 | 0.016712 | -0.0043259 | -0.0030869 | 0.020307 | 2.068e-06 | -0.013733 | 0.10986 | -0.045776 | 0 | 0.11444 | 0.018311 | 0.018311 | 0.032043 | 0.10529 | -0.041199 | 0.050354 | 0.12817 | 0.045776 | 0.16937 | 121.7102 | -0.027466 | -0.13733 | 121.8704 | 121.7743 | 121.7743 | 0.064087 | 0.064087 | 121.7148 | -0.032043 | -0.086975 | 121.8842 | 121.9254 | 121.8018 | 0.21057 | 0.086975 | 0.16022 | 0.045776 | 0.16937 | 0.091553 | 0.15564 | 0.14649 | 121.8658 | 121.8613 | -0.18311 | -0.17853 | 121.756 | 121.8063 | 121.7422 | 121.788
819.0938 | 121.9574 | -121.7606 | 0.11902 | -0.041809 | 0.077041 | 0.013116 | 0.034648 | 0.0034372 | -0.004251 | -0.0012241 | -0.0015565 | 0.0067035 | 0.01778 | -0.0064621 | -0.0015915 | 0.018384 | 0.00021567 | -0.059509 | 0.10529 | -0.054932 | -0.036621 | 0.086975 | 0.004578 | 0.004578 | -0.009155 | 0.11444 | -0.041199 | 0.045776 | 0.11902 | 0.041199 | 0.16479 | 121.7056 | -0.013733 | -0.15564 | 121.8475 | 121.7651 | 121.7651 | 0.05951 | 0.05951 | 121.7194 | -0.004578 | -0.073243 | 121.8796 | 121.9254 | 121.8018 | 0.20599 | 0.082398 | 0.14191 | 0.018311 | 0.16022 | 0.086975 | 0.16022 | 0.15564 | 121.8658 | 121.875 | -0.17395 | -0.16022 | 121.7239 | 121.8063 | 121.701 | 121.7514
820.8438 | 121.9116 | -121.8063 | 0.14648 | -0.018921 | 0.074905 | 0.013544 | 0.03123 | 0.00044655 | -0.0046782 | -0.0063511 | -0.0076599 | 0.0043537 | 0.019275 | -0.0075301 | -0.0073593 | 0.018384 | -0.0019205 | -0.09613 | 0.11444 | -0.068665 | -0.086975 | 0.050354 | -0.032043 | -0.013733 | -0.091553 | 0.091553 | -0.054932 | -0.018311 | 0.064087 | 0 | 0.12817 | 121.7377 | -0.032043 | -0.23346 | 121.8567 | 121.7926 | 121.7743 | 0.054932 | 0.036622 | 121.7514 | -0.054931 | -0.16479 | 121.8704 | 121.9345 | 121.8063 | 0.18311 | 0.054932 | 0.11902 | -0.01831 | 0.11902 | 0.036621 | 0.18311 | 0.14649 | 121.9208 | 121.8979 | -0.21515 | -0.20142 | 121.7194 | 121.788 | 121.7102 | 121.7148
822.5781 | 122.0032 | -121.7102 | 0.14648 | -0.0036622 | 0.073837 | 0.012903 | 0.031871 | 0.0021556 | -0.003183 | -0.0010105 | -0.0076599 | 0.0039265 | 0.016925 | 0.0018693 | -0.0024461 | 0.017743 | -0.0051247 | -0.050354 | 0.082397 | -0.022888 | -0.004578 | 0.13275 | 0.004578 | 0.064087 | 0.009155 | 0.09613 | -0.050354 | 0.041199 | 0.1236 | 0.073242 | 0.16937 | 121.6873 | -0.064087 | -0.15106 | 121.843 | 121.7743 | 121.7148 | 0.086975 | 0.027466 | 121.6599 | -0.050354 | -0.10529 | 121.8338 | 121.8796 | 121.7834 | 0.21973 | 0.1236 | 0.15564 | 0.01831 | 0.17395 | 0.091553 | 0.10528 | 0.14648 | 121.7926 | 121.8063 | -0.16937 | -0.19684 | 121.7056 | 121.7514 | 121.6599 | 121.7194
824.25 | 122.0398 | -121.7331 | 0.12817 | -0.011291 | 0.07405 | 0.011835 | 0.030375 | -0.0029714 | -0.0044646 | -0.0016513 | -0.0076599 | 0.0030719 | 0.015644 | 0.00037387 | -0.0018051 | 0.018171 | -0.0029885 | -0.036621 | 0.073242 | -0.041199 | -0.004578 | 0.14648 | 0.041199 | 0.064087 | 0.050354 | 0.09613 | -0.045776 | 0.082397 | 0.17395 | 0.10071 | 0.20142 | 121.6919 | -0.054932 | -0.13275 | 121.8796 | 121.7972 | 121.7743 | 0.10529 | 0.082398 | 121.6873 | -0.032044 | -0.045777 | 121.907 | 121.9345 | 121.8338 | 0.24719 | 0.14648 | 0.18768 | 0.036621 | 0.21973 | 0.12817 | 0.11444 | 0.14191 | 121.8063 | 121.8292 | -0.16937 | -0.17395 | 121.7285 | 121.8155 | 121.6965 | 121.7834
826 | 122.049 | -121.7194 | 0.10071 | -0.0036622 | 0.077896 | 0.014612 | 0.032939 | 0.0025828 | -0.0021148 | -0.00079691 | -0.0015565 | 0.0043537 | 0.018848 | -0.0032577 | -9.605e-05 | 0.018812 | -0.0014931 | -0.045776 | 0.10071 | -0.064087 | -0.004578 | 0.11902 | -0.004578 | 0.050354 | 0.064087 | 0.082397 | -0.027466 | 0.11444 | 0.15564 | 0.091553 | 0.23804 | 121.6553 | 0 | -0.10529 | 121.8384 | 121.7697 | 121.7148 | 0.11444 | 0.059509 | 121.6919 | -0.018311 | 0.013733 | 121.875 | 121.9574 | 121.8109 | 0.2655 | 0.11902 | 0.18311 | 0.059509 | 0.18311 | 0.14191 | 0.1648 | 0.10986 | 121.8201 | 121.8018 | -0.1648 | -0.12817 | 121.7148 | 121.8338 | 121.6736 | 121.7834
827.6719 | 122.0123 | -121.7331 | 0.13733 | -0.0036622 | 0.076827 | 0.014398 | 0.033579 | 0.001301 | -0.0033966 | -0.0025057 | -0.0046081 | 0.0030719 | 0.019489 | -0.0043259 | -0.0011643 | 0.019452 | -0.0014931 | -0.068665 | 0.10071 | -0.054932 | -0.032043 | 0.091553 | -0.036621 | 0.004578 | 0.022888 | 0.09613 | -0.054932 | 0.091553 | 0.14191 | 0.086975 | 0.21515 | 121.6782 | -0.036621 | -0.16937 | 121.8246 | 121.7377 | 121.6965 | 0.05951 | 0.018311 | 121.6782 | -0.041199 | -0.045776 | 121.875 | 121.9482 | 121.8201 | 0.27008 | 0.14191 | 0.14649 | 0.022889 | 0.19684 | 0.14649 | 0.15564 | 0.15106 | 121.8338 | 121.8292 | -0.19226 | -0.19226 | 121.701 | 121.8246 | 121.6644 | 121.756
829.4062 | 121.9711 | -121.7834 | 0.14648 | -0.011291 | 0.077041 | 0.014612 | 0.032939 | -0.0046804 | -0.0038238 | -0.0018649 | -0.0076599 | 0.0039265 | 0.01778 | -0.012657 | -0.0065049 | 0.017957 | 0.0027793 | -0.059509 | 0.10986 | -0.041199 | -0.054932 | 0.054932 | -0.009155 | 0.004578 | -0.032043 | 0.10986 | -0.068665 | 0.027466 | 0.10986 | 0.022888 | 0.15106 | 121.7422 | -0.036621 | -0.20142 | 121.8384 | 121.788 | 121.7743 | 0.045777 | 0.032044 | 121.7148 | -0.036621 | -0.11902 | 121.8933 | 121.9345 | 121.8063 | 0.21973 | 0.091553 | 0.096131 | -0.013733 | 0.17853 | 0.096131 | 0.15106 | 0.17853 | 121.8933 | 121.8933 | -0.18768 | -0.21515 | 121.7285 | 121.8109 | 121.7239 | 121.7514
831.0938 | 122.0261 | -121.7102 | 0.10986 | -0.02655 | 0.0764 | 0.015253 | 0.031016 | -0.0023306 | -0.00083304 | -0.0020785 | -0.0046081 | 0.0026447 | 0.017139 | 0.0040055 | 0.00011755 | 0.01988 | 0.00064307 | -0.004578 | 0.032043 | 0 | 0.041199 | 0.20599 | 0.050354 | 0.073242 | 0.091553 | 0.064087 | -0.018311 | 0.10529 | 0.16479 | 0.10071 | 0.19684 | 121.7102 | -0.07782 | -0.068664 | 121.9162 | 121.7834 | 121.7606 | 0.073242 | 0.050354 | 121.6919 | -0.045776 | -0.004577 | 121.875 | 121.907 | 121.8109 | 0.21515 | 0.11902 | 0.20599 | 0.041199 | 0.18311 | 0.1236 | 0.032043 | 0.082398 | 121.7422 | 121.7743 | -0.10986 | -0.12817 | 121.7514 | 121.8155 | 121.7056 | 121.8018
832.8281 | 121.9986 | -121.756 | 0.13733 | -0.02655 | 0.076614 | 0.015466 | 0.033793 | -0.00019445 | 2.1362e-05 | -0.0031467 | -0.0046081 | 0.0034991 | 0.019489 | -0.0098801 | -0.0026597 | 0.016889 | -0.0027749 | -0.022888 | 0.091553 | -0.059509 | 0 | 0.11902 | 0.022888 | 0.022888 | 0.036621 | 0.10529 | -0.032043 | 0.036621 | 0.11902 | 0.050354 | 0.17395 | 121.6965 | -0.045776 | -0.13733 | 121.875 | 121.7789 | 121.7789 | 0.082397 | 0.082397 | 121.7239 | -0.032043 | -0.10071 | 121.875 | 121.9299 | 121.8063 | 0.20599 | 0.082397 | 0.17853 | 0.059509 | 0.15106 | 0.068664 | 0.15106 | 0.13733 | 121.8475 | 121.8613 | -0.19684 | -0.16937 | 121.756 | 121.7926 | 121.7331 | 121.7926
834.5156 | 121.9437 | -121.7697 | 0.14648 | 0.0039673 | 0.076827 | 0.015039 | 0.035288 | 0.0021556 | 0.00044856 | -0.0025057 | 0.0014953 | 0.0037127 | 0.018421 | -0.0056075 | -0.0011643 | 0.020734 | -0.0032021 | -0.082397 | 0.11444 | -0.059509 | -0.07782 | 0.036621 | -0.091553 | -0.027466 | -0.07782 | 0.12817 | -0.064087 | -0.009155 | 0.041199 | -0.018311 | 0.11902 | 121.7102 | -0.032043 | -0.2243 | 121.8063 | 121.7422 | 121.6782 | 0.032043 | -0.032044 | 121.7056 | -0.01831 | -0.15564 | 121.8109 | 121.8887 | 121.7514 | 0.18311 | 0.045776 | 0.09613 | -0.018311 | 0.10529 | 0.054932 | 0.17395 | 0.19226 | 121.8842 | 121.8979 | -0.20599 | -0.21057 | 121.6919 | 121.7606 | 121.6873 | 121.6919
836.2656 | 122.0398 | -121.7056 | 0.10529 | -0.0036622 | 0.075546 | 0.01568 | 0.032298 | -0.0010488 | -0.0019012 | -0.0029331 | 0.0014953 | 0.00072206 | 0.018848 | 0.00058747 | -0.00052345 | 0.018598 | -0.0017069 | 0.004578 | 0.086975 | -0.022888 | 0.041199 | 0.19226 | 0.050354 | 0.082397 | 0.082397 | 0.068665 | -0.036621 | 0.12817 | 0.19226 | 0.11444 | 0.23346 | 121.6827 | -0.018311 | -0.064087 | 121.8979 | 121.788 | 121.756 | 0.10528 | 0.073242 | 121.669 | -0.036621 | 0.022888 | 121.8979 | 121.9391 | 121.8201 | 0.27008 | 0.15106 | 0.21515 | 0.064087 | 0.22888 | 0.1648 | 0.10986 | 0.10529 | 121.7926 | 121.7743 | -0.12817 | -0.14191 | 121.7468 | 121.8338 | 121.7102 | 121.788
838 | 121.9254 | -121.7606 | 0.13733 | -0.0036622 | 0.075332 | 0.014185 | 0.031871 | -0.00040805 | 0.00023496 | -0.0014377 | -0.0015565 | 0.0043537 | 0.019916 | -0.0032577 | -0.0043687 | 0.019666 | 0.0012839 | -0.050354 | 0.10986 | -0.059509 | -0.036621 | 0.091553 | -0.032043 | -0.036621 | -0.027466 | 0.10986 | -0.050354 | -0.004578 | 0.054932 | -0.022888 | 0.11444 | 121.701 | -0.027466 | -0.17395 | 121.8521 | 121.7239 | 121.7285 | 0.022888 | 0.027466 | 121.7102 | -0.027466 | -0.14191 | 121.8155 | 121.875 | 121.7377 | 0.16479 | 0.027466 | 0.15106 | 0.022888 | 0.10529 | 0.045776 | 0.16937 | 0.16022 | 121.8704 | 121.8704 | -0.19684 | -0.18768 | 121.7239 | 121.756 | 121.7102 | 121.7331
839.6719 | 122.0261 | -121.7377 | 0.13275 | -0.011291 | 0.075973 | 0.013757 | 0.031871 | 0.0010874 | -0.0038238 | -0.0010105 | 0.0014953 | 0.0020039 | 0.01778 | -0.0077439 | -0.0045823 | 0.01753 | -0.00063873 | -0.013733 | 0.086975 | -0.032043 | 0.045776 | 0.19684 | 0.09613 | 0.091553 | 0.07782 | 0.07782 | -0.045776 | 0.073242 | 0.19226 | 0.11444 | 0.19226 | 121.7056 | -0.045776 | -0.086975 | 121.9345 | 121.8292 | 121.8338 | 0.1236 | 0.12817 | 121.6919 | -0.054931 | -0.059509 | 121.9299 | 121.9299 | 121.8521 | 0.23804 | 0.16022 | 0.22888 | 0.077819 | 0.23804 | 0.11902 | 0.11902 | 0.1236 | 121.8246 | 121.8155 | -0.16479 | -0.17853 | 121.7834 | 121.8109 | 121.7239 | 121.8155
841.4219 | 121.9345 | -121.7972 | 0.15106 | -0.011291 | 0.075332 | 0.014612 | 0.034434 | 0.00044655 | -0.003183 | -0.0027195 | -0.0046081 | 0.0041401 | 0.019275 | -0.0077439 | -0.00052345 | 0.018812 | -0.0019205 | -0.07782 | 0.10986 | -0.064087 | -0.091553 | 0.027466 | -0.073242 | -0.045776 | -0.07782 | 0.11444 | -0.07782 | -0.018311 | 0.027466 | -0.032043 | 0.11444 | 121.7331 | -0.041199 | -0.24261 | 121.8246 | 121.7514 | 121.7239 | 0.018311 | -0.009155 | 121.7194 | -0.036621 | -0.16937 | 121.8246 | 121.9116 | 121.7651 | 0.19226 | 0.045777 | 0.091553 | -0.027466 | 0.10529 | 0.059509 | 0.17395 | 0.19226 | 121.907 | 121.9116 | -0.21515 | -0.22888 | 121.7056 | 121.7789 | 121.7194 | 121.7194
843.1094 | 122.0078 | -121.7102 | 0.1236 | -0.011291 | 0.076614 | 0.014185 | 0.032725 | -0.0016898 | -0.0023284 | -0.0025057 | -0.010712 | 0.0015765 | 0.016712 | -5.3326e-05 | 0.00033115 | 0.017103 | -0.00042513 | -0.027466 | 0.064087 | 0 | 0.022888 | 0.17853 | 0.050354 | 0.059509 | 0.07782 | 0.07782 | -0.022888 | 0.10071 | 0.16937 | 0.10986 | 0.19684 | 121.7102 | -0.059509 | -0.10071 | 121.8887 | 121.7697 | 121.7606 | 0.059509 | 0.050354 | 121.6873 | -0.045776 | -0.022888 | 121.8796 | 121.907 | 121.8201 | 0.21973 | 0.13275 | 0.17853 | 0.022888 | 0.19226 | 0.1236 | 0.064087 | 0.10071 | 121.7743 | 121.788 | -0.1236 | -0.14648 | 121.7331 | 121.8109 | 121.6827 | 121.788
844.8438 | 122.0123 | -121.7514 | 0.11902 | 0.0039673 | 0.0764 | 0.013971 | 0.031443 | -0.004894 | -0.0019012 | 0.00048489 | -0.0046081 | 0.0028583 | 0.018634 | -0.0026169 | -0.0039413 | 0.017103 | -0.0010659 | -0.018311 | 0.07782 | -0.036621 | 0.050354 | 0.19226 | 0.10071 | 0.10071 | 0.068665 | 0.073242 | -0.032043 | 0.059509 | 0.16937 | 0.10986 | 0.1831 | 121.7148 | -0.041199 | -0.068665 | 121.9437 | 121.8521 | 121.8521 | 0.13733 | 0.13733 | 121.7194 | -0.045777 | -0.05951 | 121.9208 | 121.9345 | 121.8613 | 0.21515 | 0.14191 | 0.22888 | 0.086975 | 0.20142 | 0.091552 | 0.11444 | 0.10529 | 121.8292 | 121.8246 | -0.15564 | -0.15106 | 121.8018 | 121.8109 | 121.7331 | 121.8201
846.5312 | 121.994 | -121.7651 | 0.13275 | -0.018921 | 0.077468 | 0.014825 | 0.031657 | -0.00019445 | -0.0023284 | -0.0016513 | -0.0046081 | 0.0032855 | 0.018421 | -0.0090255 | -0.0035141 | 0.019239 | -0.0051247 | -0.050354 | 0.10529 | -0.050354 | -0.032043 | 0.10986 | 0.013733 | 0.036621 | 0.013733 | 0.10529 | -0.050354 | 0.041199 | 0.11444 | 0.045776 | 0.17853 | 121.7148 | -0.027465 | -0.16479 | 121.875 | 121.8018 | 121.7789 | 0.086975 | 0.064087 | 121.7148 | -0.027465 | -0.091552 | 121.8796 | 121.9437 | 121.8109 | 0.22888 | 0.09613 | 0.16022 | 0.018311 | 0.16479 | 0.091553 | 0.15564 | 0.15564 | 121.8704 | 121.8704 | -0.18311 | -0.18311 | 121.7331 | 121.8063 | 121.7148 | 121.7789
848.2812 | 121.9894 | -121.7743 | 0.14191 | -0.011291 | 0.075973 | 0.014185 | 0.032939 | -0.0023306 | -0.0033966 | -0.0018649 | -0.0015565 | 0.0054217 | 0.018421 | -0.0066757 | -0.0013779 | 0.018812 | -0.0044839 | -0.045776 | 0.10071 | -0.050354 | -0.027466 | 0.11444 | -0.004578 | 0.009155 | 0.018311 | 0.09613 | -0.036621 | 0.045776 | 0.11444 | 0.036621 | 0.17395 | 121.7239 | -0.041199 | -0.16937 | 121.8887 | 121.7834 | 121.7697 | 0.059509 | 0.045776 | 121.7377 | -0.045777 | -0.096131 | 121.8887 | 121.9482 | 121.8109 | 0.21057 | 0.073242 | 0.16479 | 0.022888 | 0.15106 | 0.082397 | 0.15106 | 0.13275 | 121.875 | 121.8704 | -0.19226 | -0.17853 | 121.7468 | 121.8201 | 121.7285 | 121.7926
850.0156 | 122.0123 | -121.7422 | 0.12817 | 0.0039673 | 0.075973 | 0.014398 | 0.029521 | -0.00062165 | -0.003183 | -0.00015591 | -0.0015565 | 0.0028583 | 0.017566 | -0.0030441 | -0.0050095 | 0.017743 | -0.00085233 | -0.009155 | 0.073242 | -0.036621 | 0.045776 | 0.1831 | 0.091553 | 0.091553 | 0.064087 | 0.09613 | -0.054932 | 0.050354 | 0.15106 | 0.086975 | 0.17853 | 121.7056 | -0.054932 | -0.082398 | 121.9254 | 121.8338 | 121.8338 | 0.12817 | 0.12817 | 121.6873 | -0.032044 | -0.07782 | 121.8933 | 121.9208 | 121.8292 | 0.23346 | 0.14191 | 0.21973 | 0.082397 | 0.20599 | 0.10529 | 0.10986 | 0.15106 | 121.8155 | 121.8384 | -0.1648 | -0.18311 | 121.788 | 121.7926 | 121.7331 | 121.8063
851.7031 | 122.0673 | -121.7239 | 0.10071 | -0.02655 | 0.07341 | 0.015253 | 0.031657 | -0.0029714 | -0.0016876 | -0.00058311 | -0.0076599 | 0.0020039 | 0.018421 | 0.0044327 | -0.00030965 | 0.018171 | -0.0012795 | -0.009155 | 0.064087 | -0.009155 | 0.041199 | 0.18768 | 0.059509 | 0.073242 | 0.11902 | 0.064087 | -0.009155 | 0.11902 | 0.19226 | 0.10986 | 0.20599 | 121.7148 | -0.036621 | -0.059509 | 121.9116 | 121.7972 | 121.7834 | 0.082397 | 0.068664 | 121.7148 | -0.036621 | 0.018311 | 121.9162 | 121.9299 | 121.8338 | 0.21515 | 0.11902 | 0.19684 | 0.050354 | 0.20142 | 0.12817 | 0.073242 | 0.073242 | 121.788 | 121.788 | -0.10986 | -0.10986 | 121.7651 | 121.843 | 121.7148 | 121.843
853.4375 | 122.0215 | -121.7422 | 0.12817 | -0.0036622 | 0.074905 | 0.015039 | 0.032939 | -0.0036124 | -0.0036102 | -0.0042147 | 0.0014953 | 0.0032855 | 0.019916 | -0.0030441 | -0.00073705 | 0.018812 | -0.0027749 | -0.082397 | 0.10071 | -0.059509 | -0.054932 | 0.086975 | -0.059509 | -0.004578 | 0.022888 | 0.10071 | -0.041199 | 0.073242 | 0.11902 | 0.050354 | 0.18768 | 121.6827 | -0.027466 | -0.18311 | 121.8292 | 121.7377 | 121.6827 | 0.054931 | 0 | 121.701 | -0.027466 | -0.054932 | 121.8613 | 121.9299 | 121.7926 | 0.22888 | 0.091553 | 0.14648 | 0.004577 | 0.16022 | 0.11444 | 0.16022 | 0.14191 | 121.843 | 121.843 | -0.18768 | -0.16937 | 121.6873 | 121.8155 | 121.6599 | 121.7651
855.1094 | 122.0718 | -121.7148 | 0.1236 | -0.0036622 | 0.073196 | 0.014398 | 0.031871 | 0.001301 | -0.0016876 | -0.0012241 | -0.0015565 | 0.0011493 | 0.018421 | 0.0097733 | 0.0016129 | 0.020307 | -0.00063873 | 0 | 0.09613 | -0.032043 | 0.036621 | 0.17853 | 0.054932 | 0.07782 | 0.091553 | 0.073242 | 0 | 0.12817 | 0.18768 | 0.10986 | 0.24719 | 121.6827 | -0.027466 | -0.086975 | 121.8933 | 121.7926 | 121.7697 | 0.10986 | 0.086975 | 121.7148 | -0.050354 | 0.004578 | 121.9025 | 121.962 | 121.8246 | 0.24719 | 0.10986 | 0.21057 | 0.068664 | 0.18768 | 0.12817 | 0.12817 | 0.073242 | 121.8109 | 121.788 | -0.15564 | -0.1236 | 121.7514 | 121.843 | 121.7148 | 121.8063
856.8594 | 122.0673 | -121.7422 | 0.11444 | 0.0039673 | 0.076827 | 0.013971 | 0.032511 | 0.00044655 | -0.0036102 | -0.0022921 | -0.0015565 | 0.0032855 | 0.016712 | -0.0030441 | -0.0043687 | 0.017743 | -0.0032021 | -0.022888 | 0.073242 | -0.022888 | 0.054932 | 0.21057 | 0.10071 | 0.091553 | 0.10986 | 0.086975 | -0.041199 | 0.10529 | 0.20599 | 0.13733 | 0.21515 | 121.7194 | -0.041199 | -0.059509 | 121.9528 | 121.8338 | 121.843 | 0.11444 | 0.1236 | 121.701 | -0.027466 | -0.009155 | 121.9482 | 121.9574 | 121.8796 | 0.25635 | 0.17853 | 0.23346 | 0.07782 | 0.24719 | 0.14649 | 0.09613 | 0.12817 | 121.8155 | 121.8292 | -0.13733 | -0.15564 | 121.7972 | 121.8475 | 121.7194 | 121.8521
858.6094 | 121.8979 | -121.7743 | 0.15106 | -0.0036622 | 0.076827 | 0.015039 | 0.035716 | 1.915e-05 | -0.004251 | -0.0025057 | -0.0015565 | 0.0041401 | 0.019275 | -0.0098801 | -0.0030869 | 0.018384 | -0.0040567 | -0.064087 | 0.1236 | -0.050354 | -0.082397 | 0.027466 | -0.07782 | -0.027466 | -0.07782 | 0.1236 | -0.068665 | 0.004578 | 0.045776 | -0.032043 | 0.11444 | 121.7239 | -0.027466 | -0.23346 | 121.8018 | 121.7468 | 121.6965 | 0.022888 | -0.027466 | 121.7056 | -0.027466 | -0.14648 | 121.8201 | 121.8887 | 121.7422 | 0.18311 | 0.036622 | 0.07782 | -0.032043 | 0.11444 | 0.073243 | 0.17395 | 0.19226 | 121.8979 | 121.8979 | -0.20142 | -0.21973 | 121.6919 | 121.7789 | 121.7102 | 121.6965
860.3438 | 121.9345 | -121.7834 | 0.16022 | -0.011291 | 0.074691 | 0.013757 | 0.032511 | -0.001476 | -0.0051056 | -0.0012241 | -0.0015565 | 0.0026447 | 0.019703 | -0.0075301 | -0.0045823 | 0.014753 | 2.068e-06 | -0.068665 | 0.10529 | -0.064087 | -0.054932 | 0.07782 | -0.018311 | 0.004578 | -0.059509 | 0.12817 | -0.054932 | -0.032043 | 0.068665 | 0.009155 | 0.10529 | 121.7194 | -0.054931 | -0.21515 | 121.8613 | 121.788 | 121.7651 | 0.068665 | 0.045776 | 121.7285 | -0.032043 | -0.19226 | 121.8521 | 121.8887 | 121.7926 | 0.16022 | 0.064087 | 0.14191 | 0.009155 | 0.1236 | 0.022889 | 0.16937 | 0.18311 | 121.8887 | 121.9116 | -0.2243 | -0.21515 | 121.7285 | 121.7514 | 121.7148 | 121.7239
862.0938 | 122.081 | -121.7377 | 0.13275 | -0.011291 | 0.073837 | 0.013757 | 0.029948 | -0.001476 | -0.0027556 | -0.0010105 | -0.0046081 | 0.0024311 | 0.016285 | 0.00016027 | -0.0026597 | 0.017743 | -0.0017069 | -0.032043 | 0.068665 | -0.027466 | 0.032043 | 0.1831 | 0.10529 | 0.10529 | 0.082397 | 0.082397 | -0.054932 | 0.11902 | 0.20142 | 0.16022 | 0.22888 | 121.7102 | -0.064086 | -0.10071 | 121.9208 | 121.843 | 121.843 | 0.13275 | 0.13275 | 121.6827 | -0.050354 | -0.013732 | 121.9391 | 121.9666 | 121.8979 | 0.28381 | 0.21515 | 0.21057 | 0.059509 | 0.25635 | 0.17395 | 0.096131 | 0.13733 | 121.8063 | 121.8201 | -0.16022 | -0.18768 | 121.7697 | 121.8567 | 121.7056 | 121.8201
863.8438 | 121.9345 | -121.7834 | 0.14648 | -0.011291 | 0.075759 | 0.015466 | 0.032298 | 0.0010874 | -0.0033966 | -0.0012241 | -0.0046081 | 0.0039265 | 0.018634 | 0.00037387 | -0.0045823 | 0.016034 | 0.0034201 | -0.073242 | 0.09613 | -0.054932 | -0.050354 | 0.07782 | -0.013733 | 0.009155 | -0.041199 | 0.11902 | -0.086975 | -0.022888 | 0.054932 | 0.004578 | 0.10529 | 121.7285 | -0.050354 | -0.19684 | 121.8613 | 121.7926 | 121.7697 | 0.064087 | 0.041199 | 121.6965 | -0.027465 | -0.16937 | 121.8384 | 121.8887 | 121.788 | 0.19226 | 0.091553 | 0.13275 | 0.004578 | 0.14191 | 0.064087 | 0.15106 | 0.20599 | 121.8796 | 121.9025 | -0.20142 | -0.23346 | 121.7331 | 121.7606 | 121.7102 | 121.7422
865.5312 | 122.0581 | -121.7377 | 0.11444 | -0.011291 | 0.07341 | 0.014185 | 0.030589 | -0.0040396 | -0.0016876 | -0.0027195 | 0.0014953 | 0.0030719 | 0.018421 | -0.0013351 | -0.0033005 | 0.019025 | -0.00063873 | -0.013733 | 0.082397 | -0.027466 | 0.068665 | 0.21973 | 0.091553 | 0.1236 | 0.11902 | 0.073242 | -0.032043 | 0.11444 | 0.20599 | 0.13275 | 0.21973 | 121.7102 | -0.032044 | -0.045776 | 121.9574 | 121.8613 | 121.8292 | 0.15106 | 0.11902 | 121.7056 | -0.041199 | 0 | 121.9437 | 121.9574 | 121.8704 | 0.25177 | 0.16479 | 0.24719 | 0.096131 | 0.23804 | 0.14648 | 0.10986 | 0.10529 | 121.8201 | 121.8109 | -0.14191 | -0.14648 | 121.8063 | 121.8521 | 121.7239 | 121.8567
867.2656 | 122.0261 | -121.7331 | 0.11444 | -0.0036622 | 0.074264 | 0.01568 | 0.033152 | -0.0012624 | -0.0016876 | -0.0042147 | -0.0046081 | 0.0022175 | 0.018848 | 0.00016027 | -0.00052345 | 0.016675 | -0.0025613 | -0.045776 | 0.086975 | -0.027466 | -0.018311 | 0.11902 | 0.009155 | 0.022888 | 0.013733 | 0.07782 | -0.041199 | 0.054932 | 0.14648 | 0.07782 | 0.1831 | 121.7056 | -0.027466 | -0.13275 | 121.8521 | 121.756 | 121.7422 | 0.050354 | 0.036621 | 121.6919 | -0.036621 | -0.059509 | 121.8796 | 121.9162 | 121.8109 | 0.2243 | 0.11902 | 0.14649 | 0.009155 | 0.18768 | 0.096131 | 0.11444 | 0.11902 | 121.8201 | 121.8109 | -0.14191 | -0.15564 | 121.7148 | 121.788 | 121.6873 | 121.7468
869 | 121.994 | -121.7789 | 0.1236 | 0.0039673 | 0.075973 | 0.014185 | 0.034434 | -0.00019445 | -0.0046782 | -0.0014377 | -0.0015565 | 0.0049945 | 0.020343 | -0.0075301 | -0.00030965 | 0.018384 | -0.00063873 | -0.073242 | 0.13275 | -0.064087 | -0.045776 | 0.054932 | -0.064087 | -0.018311 | -0.013733 | 0.11444 | -0.059509 | 0.059509 | 0.086975 | 0.036621 | 0.16937 | 121.7148 | 0.009155 | -0.16937 | 121.8338 | 121.7606 | 121.7148 | 0.045776 | 0 | 121.7194 | -0.009155 | -0.064087 | 121.8658 | 121.9482 | 121.8155 | 0.22888 | 0.09613 | 0.11902 | 0.018311 | 0.14648 | 0.11902 | 0.19684 | 0.17395 | 121.9116 | 121.8933 | -0.18768 | -0.1831 | 121.7331 | 121.8384 | 121.7056 | 121.7651
870.75 | 122.0123 | -121.7514 | 0.13733 | -0.018921 | 0.074905 | 0.014398 | 0.031657 | 0.00044655 | -0.0023284 | -0.0037875 | -0.0046081 | 0.0022175 | 0.01778 | -0.0017623 | -0.00095065 | 0.018384 | 0.0010703 | -0.064087 | 0.064087 | -0.027466 | -0.009155 | 0.1236 | 0.013733 | 0.059509 | 0.018311 | 0.07782 | -0.064087 | 0.050354 | 0.11444 | 0.07782 | 0.16937 | 121.7239 | -0.073242 | -0.14648 | 121.875 | 121.8109 | 121.7651 | 0.086975 | 0.041199 | 121.6873 | -0.059509 | -0.086975 | 121.8658 | 121.9208 | 121.8292 | 0.23346 | 0.14191 | 0.15106 | 0.018311 | 0.17853 | 0.11444 | 0.091553 | 0.14191 | 121.8155 | 121.8292 | -0.16479 | -0.20142 | 121.7422 | 121.8018 | 121.6873 | 121.7697
872.4219 | 121.9208 | -121.7972 | 0.14191 | -0.011291 | 0.075759 | 0.010767 | 0.031871 | -0.0016898 | -0.0038238 | -0.0033603 | -0.0046081 | 0.0049945 | 0.019062 | -0.0030441 | -0.0060777 | 0.014966 | -0.00042513 | -0.091553 | 0.11902 | -0.07782 | -0.07782 | 0.054932 | -0.018311 | -0.013733 | -0.07782 | 0.10071 | -0.050354 | -0.027466 | 0.064087 | -0.009155 | 0.10986 | 121.7194 | -0.022888 | -0.21973 | 121.8521 | 121.7834 | 121.7789 | 0.064087 | 0.059509 | 121.7468 | -0.041199 | -0.16937 | 121.8613 | 121.907 | 121.788 | 0.16022 | 0.041199 | 0.13275 | 0 | 0.11444 | 0.022888 | 0.19684 | 0.15106 | 121.9162 | 121.8979 | -0.21973 | -0.19226 | 121.7194 | 121.7697 | 121.7056 | 121.7194
874.1562 | 121.9757 | -121.788 | 0.16479 | -0.02655 | 0.075546 | 0.012476 | 0.030589 | 0.00044655 | -0.003183 | -0.0035739 | -0.010712 | 0.0037127 | 0.018848 | -0.0034713 | -0.0024461 | 0.016248 | -0.00085233 | -0.086975 | 0.09613 | -0.068665 | -0.068665 | 0.059509 | -0.036621 | -0.013733 | -0.07782 | 0.11444 | -0.073242 | -0.013733 | 0.07782 | 0.009155 | 0.14191 | 121.7194 | -0.068665 | -0.23346 | 121.8475 | 121.7743 | 121.7514 | 0.054932 | 0.032044 | 121.7148 | -0.050354 | -0.17853 | 121.8658 | 121.9299 | 121.7972 | 0.21515 | 0.082397 | 0.12817 | 0 | 0.15106 | 0.059509 | 0.16479 | 0.18768 | 121.8842 | 121.9025 | -0.23346 | -0.23804 | 121.7194 | 121.7743 | 121.7011 | 121.7102
875.9062 | 121.9574 | -121.8018 | 0.15564 | -0.011291 | 0.072128 | 0.01333 | 0.031016 | -0.00040805 | -0.004251 | -0.0025057 | -0.013763 | 0.0030719 | 0.017353 | -0.0043259 | -0.0041551 | 0.017957 | -0.0029885 | -0.09613 | 0.1236 | -0.064087 | -0.082397 | 0.036621 | -0.045776 | -0.027466 | -0.073242 | 0.11444 | -0.054932 | -0.013733 | 0.073242 | 0.004578 | 0.10529 | 121.7377 | -0.032044 | -0.23804 | 121.8384 | 121.7743 | 121.756 | 0.036621 | 0.018311 | 121.7468 | -0.041199 | -0.16937 | 121.875 | 121.907 | 121.8063 | 0.16022 | 0.05951 | 0.10071 | -0.01831 | 0.12817 | 0.041199 | 0.18768 | 0.16937 | 121.9254 | 121.9162 | -0.21973 | -0.21057 | 121.7194 | 121.788 | 121.7056 | 121.7285
877.6562 | 121.9391 | -121.788 | 0.14191 | -0.0036622 | 0.076187 | 0.016107 | 0.03422 | 0.001301 | -0.0027556 | -0.00079691 | -0.0015565 | 0.0056355 | 0.020343 | -0.0073165 | -0.0020187 | 0.018598 | -0.0046975 | -0.064087 | 0.10071 | -0.059509 | -0.086975 | 0.036621 | -0.068665 | -0.027466 | -0.054932 | 0.11444 | -0.073242 | 0.004578 | 0.054932 | -0.027466 | 0.11444 | 121.7285 | -0.041199 | -0.22888 | 121.8246 | 121.7606 | 121.7194 | 0.032043 | -0.009156 | 121.7148 | -0.027466 | -0.13733 | 121.843 | 121.9025 | 121.7606 | 0.18768 | 0.045776 | 0.09613 | -0.027466 | 0.12817 | 0.07782 | 0.16022 | 0.18768 | 121.8887 | 121.9025 | -0.20142 | -0.21515 | 121.7011 | 121.7926 | 121.7239 | 121.7331
879.3281 | 121.9437 | -121.7606 | 0.12817 | -0.0036622 | 0.077896 | 0.015894 | 0.032939 | 0.0042918 | -0.0038238 | -0.0018649 | 0.0014953 | 0.0045673 | 0.017994 | -0.0060349 | -0.00073705 | 0.018384 | 0.0012839 | -0.073242 | 0.11444 | -0.07782 | -0.082397 | 0.022888 | -0.073242 | -0.032043 | -0.064087 | 0.11902 | -0.068665 | 0.004578 | 0.045776 | -0.027466 | 0.1236 | 121.6827 | -0.013733 | -0.21057 | 121.7834 | 121.7285 | 121.6873 | 0.045777 | 0.004578 | 121.6919 | -0.009155 | -0.1236 | 121.8063 | 121.8842 | 121.7331 | 0.19226 | 0.041199 | 0.10071 | -0.004577 | 0.11444 | 0.073243 | 0.19226 | 0.18768 | 121.875 | 121.8796 | -0.20599 | -0.19684 | 121.6782 | 121.7651 | 121.6873 | 121.6965
881 | 121.9849 | -121.756 | 0.13733 | -0.011291 | 0.076187 | 0.014398 | 0.032511 | 0.00066015 | -0.003183 | 0.00091209 | -0.0076599 | 0.0030719 | 0.02013 | -0.00069433 | -0.0022325 | 0.018384 | -0.0051247 | -0.032043 | 0.09613 | -0.064087 | 0 | 0.11902 | 0.018311 | 0.018311 | 0.027466 | 0.10529 | -0.045776 | 0.068665 | 0.11902 | 0.059509 | 0.16937 | 121.6919 | -0.041199 | -0.13733 | 121.875 | 121.7743 | 121.7743 | 0.082398 | 0.082398 | 121.7102 | -0.032043 | -0.068664 | 121.875 | 121.9254 | 121.8155 | 0.21515 | 0.10528 | 0.18311 | 0.064087 | 0.16479 | 0.11444 | 0.16022 | 0.15106 | 121.8521 | 121.8613 | -0.20142 | -0.18311 | 121.756 | 121.8246 | 121.7239 | 121.7834
882.75 | 122.0306 | -121.7148 | 0.10986 | -0.0036622 | 0.075332 | 0.01333 | 0.032725 | -0.0016898 | -0.0019012 | -0.0022921 | -0.0046081 | 0.0039265 | 0.019703 | -0.0060349 | -0.0035141 | 0.020521 | 0.0014975 | -0.073242 | 0.10529 | -0.064087 | -0.045776 | 0.09613 | -0.036621 | 0 | 0.009155 | 0.091553 | -0.050354 | 0.082397 | 0.14191 | 0.073242 | 0.20142 | 121.6507 | -0.004577 | -0.15564 | 121.8109 | 121.7148 | 121.6782 | 0.064087 | 0.027466 | 121.6644 | -0.01831 | -0.027466 | 121.8567 | 121.9162 | 121.788 | 0.25177 | 0.1236 | 0.16022 | 0.018311 | 0.19226 | 0.13275 | 0.16937 | 0.14191 | 121.8201 | 121.8063 | -0.17395 | -0.16022 | 121.669 | 121.7972 | 121.6415 | 121.7239
884.4844 | 121.9437 | -121.8018 | 0.14191 | -0.0036622 | 0.074691 | 0.014825 | 0.032511 | -0.00040805 | -0.0012604 | -0.0033603 | -0.0046081 | 0.00093566 | 0.021412 | -0.0085983 | -0.0050095 | 0.01753 | -0.0019205 | -0.07782 | 0.10986 | -0.068665 | -0.064087 | 0.07782 | -0.027466 | -0.018311 | -0.054932 | 0.1236 | -0.054932 | -0.018311 | 0.082397 | 0.018311 | 0.09613 | 121.7331 | -0.032044 | -0.20599 | 121.8796 | 121.7834 | 121.7743 | 0.050354 | 0.041199 | 121.7468 | -0.018311 | -0.16022 | 121.8842 | 121.8979 | 121.8201 | 0.15106 | 0.073243 | 0.14649 | 0.004578 | 0.13733 | 0.036621 | 0.17853 | 0.17853 | 121.9116 | 121.9254 | -0.21057 | -0.19684 | 121.7377 | 121.7834 | 121.7239 | 121.7468
886.1562 | 122.0078 | -121.7743 | 0.12817 | -0.018921 | 0.074264 | 0.013757 | 0.032939 | -0.0012624 | -0.004251 | -0.0010105 | -0.0076599 | 0.0022175 | 0.018421 | -0.0051803 | -0.00052345 | 0.01753 | -0.0029885 | -0.027466 | 0.11902 | -0.054932 | -0.022888 | 0.12817 | 0.013733 | 0.032043 | 0 | 0.09613 | -0.050354 | 0.054932 | 0.12817 | 0.041199 | 0.16479 | 121.7194 | -0.009155 | -0.15106 | 121.9025 | 121.8063 | 121.788 | 0.086975 | 0.068665 | 121.7239 | -0.032044 | -0.073242 | 121.9025 | 121.9391 | 121.8155 | 0.21515 | 0.091553 | 0.18311 | 0.032044 | 0.17853 | 0.10529 | 0.17395 | 0.14648 | 121.8933 | 121.8704 | -0.18311 | -0.17853 | 121.7514 | 121.8292 | 121.7468 | 121.7743
887.9062 | 122.0535 | -121.7377 | 0.11902 | -0.0036622 | 0.075332 | 0.01568 | 0.032298 | 0.00087375 | -0.0023284 | -0.0025057 | -0.0076599 | 0.0013629 | 0.019062 | -0.0034713 | 0.00033115 | 0.018384 | 0.00021567 | -0.059509 | 0.10071 | -0.036621 | 0 | 0.13733 | 0.013733 | 0.054932 | 0.054932 | 0.07782 | -0.050354 | 0.1236 | 0.17395 | 0.09613 | 0.22888 | 121.7011 | -0.018311 | -0.11902 | 121.875 | 121.7926 | 121.7514 | 0.091553 | 0.050354 | 121.6873 | -0.041199 | 0.004577 | 121.9116 | 121.9666 | 121.8338 | 0.27924 | 0.14648 | 0.17395 | 0.036621 | 0.2243 | 0.17395 | 0.13733 | 0.12817 | 121.8384 | 121.8155 | -0.15564 | -0.16937 | 121.7377 | 121.8613 | 121.6782 | 121.7926
889.5938 | 122.0627 | -121.7422 | 0.11902 | -0.02655 | 0.075332 | 0.015039 | 0.032725 | 0.0021556 | -0.0016876 | 0.0015531 | -0.0076599 | 0.00072206 | 0.019916 | -0.00026713 | -0.0018051 | 0.018384 | -0.0040567 | -0.004578 | 0.064087 | -0.018311 | 0.041199 | 0.19684 | 0.050354 | 0.07782 | 0.086975 | 0.050354 | -0.027466 | 0.1236 | 0.17395 | 0.11902 | 0.21973 | 121.7239 | -0.054932 | -0.07782 | 121.9391 | 121.8201 | 121.7926 | 0.096131 | 0.068665 | 121.7148 | -0.068665 | 0.004577 | 121.9162 | 121.962 | 121.8613 | 0.24719 | 0.14649 | 0.21515 | 0.05951 | 0.20142 | 0.15106 | 0.082398 | 0.07782 | 121.8063 | 121.7926 | -0.13733 | -0.14649 | 121.7834 | 121.8658 | 121.7377 | 121.8292
891.3438 | 122.0901 | -121.7331 | 0.1236 | -0.018921 | 0.073623 | 0.012262 | 0.032084 | 0.0025828 | -0.00083304 | -0.00079691 | -0.0015565 | 0.0017901 | 0.018207 | 0.0016555 | -0.0039413 | 0.019025 | -0.0019205 | -0.009155 | 0.059509 | -0.045776 | 0.068665 | 0.23346 | 0.10986 | 0.11444 | 0.10986 | 0.07782 | -0.027466 | 0.10529 | 0.21057 | 0.15564 | 0.21973 | 121.6873 | -0.064087 | -0.054931 | 121.9666 | 121.8475 | 121.843 | 0.16022 | 0.15564 | 121.7056 | -0.045776 | -0.01831 | 121.9437 | 121.9528 | 121.8887 | 0.24719 | 0.18311 | 0.27924 | 0.11444 | 0.23804 | 0.13275 | 0.10528 | 0.10529 | 121.7926 | 121.8109 | -0.16937 | -0.15106 | 121.8018 | 121.8384 | 121.7239 | 121.843
893.0938 | 122.0215 | -121.7377 | 0.13275 | -0.03418 | 0.07341 | 0.014825 | 0.032084 | -0.00062165 | -0.0044646 | -0.0031467 | -0.0076599 | 0.0043537 | 0.016712 | -0.0056075 | -0.0030869 | 0.018171 | 0.0017111 | -0.059509 | 0.091553 | -0.036621 | -0.036621 | 0.11902 | 0.022888 | 0.032043 | 0.009155 | 0.07782 | -0.032043 | 0.059509 | 0.13275 | 0.064087 | 0.16937 | 121.7011 | -0.041198 | -0.16937 | 121.8567 | 121.7697 | 121.7606 | 0.068664 | 0.059509 | 121.7056 | -0.054931 | -0.073242 | 121.8704 | 121.907 | 121.8018 | 0.20142 | 0.09613 | 0.15564 | 0 | 0.16479 | 0.091552 | 0.12817 | 0.10986 | 121.8292 | 121.8155 | -0.16937 | -0.16479 | 121.7011 | 121.7972 | 121.6782 | 121.7468
894.8281 | 122.0856 | -121.7102 | 0.11902 | -0.02655 | 0.075332 | 0.014185 | 0.029307 | 0.0027964 | -0.0027556 | -0.0048557 | -0.010712 | 0.0028583 | 0.017353 | -0.0083847 | 0.00054475 | 0.01988 | 0.00064307 | 0 | 0.059509 | -0.009155 | 0.045776 | 0.20599 | 0.050354 | 0.07782 | 0.11444 | 0.050354 | -0.018311 | 0.10986 | 0.18768 | 0.10529 | 0.2243 | 121.701 | -0.05951 | -0.073243 | 121.9162 | 121.788 | 121.7606 | 0.086975 | 0.059509 | 121.6919 | -0.068665 | -0.009156 | 121.8979 | 121.9345 | 121.8155 | 0.24261 | 0.1236 | 0.21515 | 0.054931 | 0.20599 | 0.12817 | 0.068664 | 0.068665 | 121.7697 | 121.7606 | -0.12817 | -0.13733 | 121.756 | 121.8201 | 121.7102 | 121.8246
896.5156 | 122.0535 | -121.756 | 0.10529 | -0.011291 | 0.072341 | 0.014398 | 0.028666 | -0.00083525 | -0.0027556 | -0.0022921 | 0.0014953 | 0.0024311 | 0.01778 | -0.0017623 | -0.0035141 | 0.015821 | 0.00085667 | 0.004578 | 0.07782 | -0.041199 | 0.068665 | 0.20599 | 0.10986 | 0.10986 | 0.086975 | 0.059509 | -0.036621 | 0.086975 | 0.17853 | 0.1236 | 0.21515 | 121.7148 | -0.027466 | -0.036621 | 121.962 | 121.8658 | 121.8658 | 0.15106 | 0.15106 | 121.7194 | -0.045777 | -0.018311 | 121.9345 | 121.9711 | 121.8796 | 0.25177 | 0.16022 | 0.24719 | 0.10986 | 0.21515 | 0.1236 | 0.11902 | 0.09613 | 121.8338 | 121.8155 | -0.14649 | -0.14191 | 121.8246 | 121.843 | 121.7606 | 121.843
898.25 | 121.9803 | -121.7743 | 0.16937 | -0.0036622 | 0.075759 | 0.014825 | 0.032298 | -0.00083525 | -0.0033966 | 0.00091209 | -0.0046081 | 0.0032855 | 0.018848 | -0.0096665 | -0.0045823 | 0.016889 | 0.00021567 | -0.009155 | 0.086975 | -0.036621 | 0.013733 | 0.17853 | 0.064087 | 0.073242 | 0.041199 | 0.09613 | -0.045776 | 0.022888 | 0.10986 | 0.054932 | 0.15106 | 121.7377 | -0.082398 | -0.15564 | 121.9528 | 121.8475 | 121.8384 | 0.10986 | 0.10071 | 121.7285 | -0.073243 | -0.14649 | 121.8842 | 121.9254 | 121.8292 | 0.19684 | 0.10071 | 0.21515 | 0.050354 | 0.15564 | 0.068664 | 0.1236 | 0.14191 | 121.8613 | 121.8704 | -0.20599 | -0.21515 | 121.788 | 121.7972 | 121.7651 | 121.8155
900 | 122.0032 | -121.7926 | 0.14648 | -0.0036622 | 0.076614 | 0.015039 | 0.032084 | 0.00023275 | -0.0078826 | -0.0022921 | -0.0046081 | 0.0024311 | 0.019916 | -0.0053939 | -0.0045823 | 0.018384 | -0.0044839 | -0.009155 | 0.09613 | -0.036621 | 0.027466 | 0.17395 | 0.07782 | 0.07782 | 0.027466 | 0.086975 | -0.045776 | 0.018311 | 0.11902 | 0.041199 | 0.14191 | 121.756 | -0.050354 | -0.11902 | 121.9666 | 121.8704 | 121.8704 | 0.11444 | 0.11444 | 121.7468 | -0.059509 | -0.12817 | 121.9116 | 121.9345 | 121.8338 | 0.18768 | 0.086975 | 0.21057 | 0.064087 | 0.16479 | 0.064087 | 0.13275 | 0.13275 | 121.8887 | 121.8796 | -0.18311 | -0.19226 | 121.8201 | 121.8109 | 121.7834 | 121.8201
901.6719 | 121.9254 | -121.7972 | 0.13275 | 0.0039673 | 0.07341 | 0.015039 | 0.03422 | 0.0036508 | -0.0019012 | 0.0013395 | -0.0015565 | 0.0054217 | 0.019916 | -0.0041123 | 0.00033115 | 0.016889 | 0.00085667 | -0.059509 | 0.10529 | -0.059509 | -0.082397 | 0.036621 | -0.086975 | -0.050354 | -0.082397 | 0.1236 | -0.059509 | -0.018311 | 0.045776 | -0.041199 | 0.10986 | 121.7377 | -0.027465 | -0.21515 | 121.8338 | 121.7468 | 121.7102 | 0.009155 | -0.027466 | 121.7377 | -0.009155 | -0.15106 | 121.843 | 121.907 | 121.756 | 0.16937 | 0.01831 | 0.09613 | -0.022888 | 0.10528 | 0.041198 | 0.16479 | 0.1831 | 121.9025 | 121.9208 | -0.19226 | -0.19226 | 121.7148 | 121.7789 | 121.7377 | 121.7148
903.4062 | 121.9849 | -121.7606 | 0.15106 | -0.0036622 | 0.073837 | 0.012048 | 0.03422 | 0.00066015 | -0.0027556 | -0.0018649 | -0.0046081 | 0.0052081 | 0.019916 | -0.0098801 | 0.00033115 | 0.018384 | -0.0019205 | -0.032043 | 0.10071 | -0.059509 | -0.022888 | 0.11444 | -0.004578 | 0.013733 | 0.018311 | 0.10529 | -0.045776 | 0.045776 | 0.12817 | 0.059509 | 0.1831 | 121.701 | -0.050354 | -0.17395 | 121.875 | 121.7743 | 121.756 | 0.073242 | 0.054931 | 121.7148 | -0.045776 | -0.10529 | 121.8887 | 121.9437 | 121.8201 | 0.22888 | 0.10528 | 0.17395 | 0.036621 | 0.17395 | 0.091552 | 0.16022 | 0.15106 | 121.8613 | 121.8658 | -0.21057 | -0.19684 | 121.7377 | 121.8063 | 121.7285 | 121.7789
905.1406 | 122.0352 | -121.7194 | 0.10071 | -0.0036622 | 0.075759 | 0.014612 | 0.030589 | -0.003185 | -0.002542 | -0.0033603 | -0.0046081 | -0.00013254 | 0.018207 | -0.0083847 | -0.0018051 | 0.018812 | -0.0029885 | -0.036621 | 0.064087 | -0.009155 | 0.022888 | 0.1831 | 0.027466 | 0.07782 | 0.036621 | 0.07782 | -0.018311 | 0.086975 | 0.15564 | 0.086975 | 0.19226 | 121.7102 | -0.036621 | -0.07782 | 121.9025 | 121.7972 | 121.7468 | 0.086975 | 0.036621 | 121.701 | -0.022888 | -0.013733 | 121.875 | 121.9116 | 121.8063 | 0.21057 | 0.10529 | 0.19226 | 0.032043 | 0.17395 | 0.10529 | 0.073242 | 0.096131 | 121.7834 | 121.7972 | -0.10986 | -0.11902 | 121.7422 | 121.8063 | 121.6827 | 121.756
906.8281 | 122.0718 | -121.756 | 0.11902 | -0.0036622 | 0.074478 | 0.01333 | 0.03123 | 0.0010874 | -0.0021148 | -0.0025057 | -0.0046081 | 0.0030719 | 0.01778 | -0.00069433 | -0.0045823 | 0.019452 | -0.00063873 | -0.009155 | 0.064087 | -0.027466 | 0.064087 | 0.23346 | 0.11444 | 0.10986 | 0.09613 | 0.082397 | -0.032043 | 0.11444 | 0.21057 | 0.1236 | 0.21057 | 121.7285 | -0.054932 | -0.054932 | 121.9894 | 121.8658 | 121.8704 | 0.13733 | 0.14191 | 121.7239 | -0.036622 | -0.004578 | 121.9666 | 121.9666 | 121.8796 | 0.24261 | 0.15564 | 0.26093 | 0.091553 | 0.24261 | 0.14648 | 0.091553 | 0.11444 | 121.8201 | 121.8384 | -0.14649 | -0.15106 | 121.8201 | 121.8704 | 121.7468 | 121.8521
908.5625 | 122.049 | -121.7651 | 0.11444 | -0.02655 | 0.072128 | 0.014612 | 0.030162 | -0.0023306 | -0.003183 | 0.0019803 | -0.0046081 | 0.0041401 | 0.018207 | -0.0015487 | -0.0033005 | 0.018598 | 0.0014975 | -0.068665 | 0.091553 | -0.022888 | -0.013733 | 0.13275 | 0.004578 | 0.041199 | -0.004578 | 0.07782 | -0.059509 | 0.059509 | 0.14191 | 0.07782 | 0.17853 | 121.7422 | -0.022888 | -0.12817 | 121.8979 | 121.8063 | 121.7697 | 0.064087 | 0.027466 | 121.7056 | -0.036621 | -0.054932 | 121.907 | 121.9437 | 121.843 | 0.23804 | 0.13733 | 0.15564 | 0.009155 | 0.20142 | 0.11902 | 0.11444 | 0.13733 | 121.8567 | 121.843 | -0.13733 | -0.17395 | 121.7514 | 121.8246 | 121.6965 | 121.7606
910.2969 | 122.0581 | -121.756 | 0.1236 | -0.011291 | 0.073623 | 0.013544 | 0.029307 | -0.0010488 | -0.0027556 | -0.0020785 | -0.0046081 | 0.0034991 | 0.016498 | 0.00037387 | -0.0033005 | 0.019452 | -0.0012795 | -0.050354 | 0.073242 | -0.022888 | -0.009155 | 0.12817 | 0.027466 | 0.059509 | 0.018311 | 0.086975 | -0.036621 | 0.064087 | 0.15564 | 0.091553 | 0.18768 | 121.7331 | -0.050354 | -0.13275 | 121.8842 | 121.8155 | 121.7834 | 0.082397 | 0.050354 | 121.7194 | -0.036621 | -0.059509 | 121.9116 | 121.9437 | 121.8475 | 0.2243 | 0.12817 | 0.15106 | 0.013733 | 0.19226 | 0.10071 | 0.09613 | 0.1236 | 121.8292 | 121.843 | -0.14648 | -0.16022 | 121.7468 | 121.8201 | 121.7056 | 121.7743
911.9844 | 122.0032 | -121.7926 | 0.13733 | -0.018921 | 0.073196 | 0.013971 | 0.032511 | -0.0012624 | -0.0038238 | 5.7688e-05 | -0.013763 | 0.0067035 | 0.016925 | -0.010521 | -0.0026597 | 0.018812 | -0.0014931 | -0.009155 | 0.11444 | -0.068665 | -0.013733 | 0.11444 | 0.004578 | 0.018311 | 0.027466 | 0.10529 | -0.045776 | 0.041199 | 0.11902 | 0.045776 | 0.16479 | 121.7239 | -0.022888 | -0.15106 | 121.907 | 121.8109 | 121.7972 | 0.086976 | 0.073243 | 121.7468 | -0.032043 | -0.09613 | 121.9116 | 121.9574 | 121.8384 | 0.21057 | 0.091552 | 0.18311 | 0.054932 | 0.16479 | 0.086975 | 0.18311 | 0.15106 | 121.907 | 121.8979 | -0.20599 | -0.18311 | 121.7789 | 121.8338 | 121.7834 | 121.8201
913.7188 | 122.0947 | -121.7285 | 0.11902 | -0.0036622 | 0.072769 | 0.012903 | 0.030375 | -0.001476 | -0.0033966 | -0.0020785 | -0.0015565 | 0.00072206 | 0.019703 | 0.0050735 | -0.0045823 | 0.018812 | -0.0021341 | -0.004578 | 0.082397 | -0.032043 | 0.073242 | 0.23804 | 0.09613 | 0.11444 | 0.14648 | 0.073242 | -0.013733 | 0.11444 | 0.21515 | 0.16022 | 0.21973 | 121.6965 | -0.036622 | -0.045777 | 121.9666 | 121.843 | 121.8246 | 0.14648 | 0.12817 | 121.7148 | -0.045777 | -0.004578 | 121.9437 | 121.9482 | 121.8887 | 0.23346 | 0.17395 | 0.27008 | 0.10529 | 0.22888 | 0.12817 | 0.11444 | 0.086975 | 121.8109 | 121.8018 | -0.15106 | -0.13275 | 121.8018 | 121.843 | 121.7239 | 121.875
915.3906 | 121.9666 | -121.7743 | 0.13733 | -0.0036622 | 0.078536 | 0.013757 | 0.033152 | -0.002117 | -0.004251 | -0.0018649 | -0.0046081 | 0.0037127 | 0.018421 | -0.0026169 | -0.0015915 | 0.016889 | -0.0072611 | -0.022888 | 0.10071 | -0.054932 | -0.013733 | 0.10529 | 0.004578 | 0.004578 | 0.004578 | 0.1236 | -0.054932 | 0.032043 | 0.09613 | 0 | 0.14648 | 121.7194 | -0.036621 | -0.15106 | 121.8796 | 121.7789 | 121.7789 | 0.05951 | 0.05951 | 121.7194 | -0.013733 | -0.10529 | 121.8704 | 121.9208 | 121.7743 | 0.20142 | 0.054932 | 0.16022 | 0.041199 | 0.15106 | 0.086975 | 0.15564 | 0.17853 | 121.875 | 121.8979 | -0.19226 | -0.19226 | 121.7606 | 121.8063 | 121.7514 | 121.7789
917.1406 | 121.9437 | -121.7926 | 0.15106 | -0.0036622 | 0.076187 | 0.014185 | 0.034007 | 0.0021556 | -0.0021148 | -0.00079691 | 0.0014953 | 0.0045673 | 0.019703 | -0.0090255 | -0.0011643 | 0.020093 | -0.0019205 | -0.07782 | 0.13733 | -0.054932 | -0.082397 | 0.004578 | -0.07782 | -0.054932 | -0.09613 | 0.11444 | -0.073242 | -0.004578 | 0.041199 | -0.022888 | 0.10986 | 121.7377 | -0.013733 | -0.23346 | 121.7972 | 121.7377 | 121.7148 | 0 | -0.022888 | 121.7194 | -0.036621 | -0.15564 | 121.8338 | 121.9025 | 121.7697 | 0.18311 | 0.050354 | 0.05951 | -0.027465 | 0.11444 | 0.068664 | 0.19226 | 0.18768 | 121.9299 | 121.907 | -0.20599 | -0.2243 | 121.7102 | 121.788 | 121.7148 | 121.6965
918.875 | 122.0535 | -121.7422 | 0.12817 | -0.011291 | 0.075759 | 0.016321 | 0.033793 | 0.00087375 | -0.0010468 | -0.0048557 | -0.0015565 | 0.0039265 | 0.021412 | -0.0079575 | 0.0011855 | 0.017743 | 0.00042947 | -0.068665 | 0.11444 | -0.054932 | -0.032043 | 0.10529 | -0.032043 | 0.027466 | 0.022888 | 0.086975 | -0.045776 | 0.09613 | 0.15564 | 0.073242 | 0.21515 | 121.6873 | -0.013733 | -0.16022 | 121.8475 | 121.7697 | 121.7102 | 0.082398 | 0.022889 | 121.6965 | -0.041199 | -0.032044 | 121.8979 | 121.9574 | 121.8155 | 0.26093 | 0.11902 | 0.16022 | 0.022889 | 0.20142 | 0.14191 | 0.16937 | 0.13275 | 121.8567 | 121.8292 | -0.18311 | -0.17395 | 121.7102 | 121.8384 | 121.6736 | 121.7651
920.625 | 122.0718 | -121.7514 | 0.11444 | -0.0036622 | 0.072555 | 0.015894 | 0.032084 | -0.00062165 | -0.002542 | -0.00058311 | -0.013763 | 0.0028583 | 0.018421 | 0.00037387 | -0.00095065 | 0.018384 | -0.0010659 | 0.004578 | 0.07782 | -0.022888 | 0.050354 | 0.18768 | 0.032043 | 0.064087 | 0.086975 | 0.082397 | -0.009155 | 0.13275 | 0.19226 | 0.14191 | 0.22888 | 121.7285 | -0.036621 | -0.064087 | 121.9391 | 121.8155 | 121.7834 | 0.086975 | 0.054931 | 121.7422 | -0.032044 | 0.01831 | 121.9437 | 121.9803 | 121.8933 | 0.23804 | 0.15106 | 0.21057 | 0.073242 | 0.20142 | 0.14191 | 0.10071 | 0.091552 | 121.8292 | 121.8338 | -0.13733 | -0.1236 | 121.8018 | 121.8842 | 121.756 | 121.8384
922.3125 | 122.0947 | -121.7514 | 0.09613 | -0.0036622 | 0.076614 | 0.014185 | 0.03123 | 0.001301 | -0.0029694 | -0.0010105 | -0.0046081 | 0.0022175 | 0.020343 | -0.0024033 | -0.0020187 | 0.017957 | 0.00064307 | -0.041199 | 0.091553 | -0.022888 | 0.027466 | 0.16022 | 0.068665 | 0.091553 | 0.07782 | 0.091553 | -0.036621 | 0.091553 | 0.19226 | 0.13733 | 0.22888 | 121.7285 | -0.004577 | -0.068664 | 121.9116 | 121.843 | 121.8201 | 0.11444 | 0.091553 | 121.7148 | -0.004577 | -0.004577 | 121.9437 | 121.9803 | 121.8887 | 0.2655 | 0.17395 | 0.1831 | 0.050354 | 0.22888 | 0.12817 | 0.11444 | 0.12817 | 121.843 | 121.843 | -0.11902 | -0.13275 | 121.7789 | 121.843 | 121.7102 | 121.8292
923.9844 | 122.0261 | -121.7468 | 0.13275 | 0.0039673 | 0.075332 | 0.013971 | 0.030802 | -0.0046804 | -0.001474 | -0.0027195 | 0.0014953 | 0.0043537 | 0.018421 | -0.0036849 | -0.0028733 | 0.017103 | -0.0029885 | -0.009155 | 0.068665 | -0.032043 | 0.050354 | 0.19226 | 0.09613 | 0.086975 | 0.059509 | 0.07782 | -0.041199 | 0.054932 | 0.16022 | 0.091553 | 0.17853 | 121.7148 | -0.064086 | -0.082397 | 121.9391 | 121.8338 | 121.843 | 0.11902 | 0.12817 | 121.7056 | -0.054931 | -0.077819 | 121.907 | 121.9254 | 121.8384 | 0.21973 | 0.13275 | 0.2243 | 0.082397 | 0.20142 | 0.096131 | 0.10071 | 0.11902 | 121.8155 | 121.8246 | -0.16479 | -0.17395 | 121.7972 | 121.8018 | 121.7377 | 121.8063
925.7344 | 122.0993 | -121.7606 | 0.12817 | -0.011291 | 0.075332 | 0.014398 | 0.029948 | 1.915e-05 | -0.0046782 | -0.0018649 | 0.0014953 | 0.0032855 | 0.016498 | -0.0015487 | -0.0045823 | 0.019239 | -0.0023477 | -0.013733 | 0.07782 | -0.045776 | 0.073242 | 0.23346 | 0.10986 | 0.1236 | 0.14191 | 0.082397 | -0.032043 | 0.10529 | 0.21515 | 0.14648 | 0.21973 | 121.7148 | -0.050354 | -0.054932 | 121.994 | 121.8842 | 121.8704 | 0.16937 | 0.15564 | 121.7285 | -0.045777 | -0.022888 | 121.9757 | 121.9803 | 121.907 | 0.25177 | 0.17853 | 0.27924 | 0.11902 | 0.24719 | 0.13733 | 0.1236 | 0.11444 | 121.8384 | 121.843 | -0.17395 | -0.16022 | 121.8338 | 121.8658 | 121.7468 | 121.9025
927.4688 | 122.0398 | -121.7514 | 0.11444 | -0.018921 | 0.074691 | 0.015253 | 0.031871 | -0.0010488 | -0.0029694 | 0.0024075 | -0.010712 | 0.0015765 | 0.01543 | 0.00080107 | -0.0037277 | 0.019666 | -0.0061929 | -0.064087 | 0.086975 | -0.032043 | -0.004578 | 0.10986 | 0.013733 | 0.041199 | 0.009155 | 0.082397 | -0.045776 | 0.054932 | 0.12817 | 0.073242 | 0.1831 | 121.7194 | -0.027466 | -0.11902 | 121.8613 | 121.7926 | 121.7651 | 0.073242 | 0.045776 | 121.7056 | -0.032044 | -0.059509 | 121.8796 | 121.9345 | 121.8246 | 0.22888 | 0.11902 | 0.14191 | 0.027465 | 0.17395 | 0.10071 | 0.11902 | 0.12817 | 121.8384 | 121.8338 | -0.14648 | -0.16022 | 121.7468 | 121.8063 | 121.6873 | 121.7606
929.2031 | 121.962 | -121.7697 | 0.15564 | -0.018921 | 0.077896 | 0.013544 | 0.034648 | 0.005787 | -0.0038238 | -0.00079691 | -0.0046081 | 0.0043537 | 0.018634 | -0.0098801 | -0.0015915 | 0.018598 | -0.0034159 | -0.041199 | 0.10071 | -0.059509 | -0.032043 | 0.10986 | -0.013733 | 0 | -0.004578 | 0.11902 | -0.050354 | 0.018311 | 0.082397 | -0.018311 | 0.12817 | 121.7102 | -0.054932 | -0.18768 | 121.8796 | 121.7697 | 121.756 | 0.059509 | 0.045776 | 121.7194 | -0.036621 | -0.13733 | 121.8521 | 121.8979 | 121.7514 | 0.17853 | 0.032043 | 0.16937 | 0.027466 | 0.13275 | 0.068665 | 0.16022 | 0.16937 | 121.8704 | 121.8887 | -0.21515 | -0.20599 | 121.7377 | 121.788 | 121.7285 | 121.7651
930.9531 | 122.0352 | -121.756 | 0.11444 | -0.011291 | 0.074264 | 0.014612 | 0.032511 | -0.0042532 | -0.0021148 | -0.00079691 | -0.0046081 | 0.0020039 | 0.021625 | -0.0030441 | -0.0020187 | 0.019025 | -0.0010659 | -0.041199 | 0.036621 | 0.004578 | 0.027466 | 0.17395 | 0.018311 | 0.059509 | 0.059509 | 0.07782 | -0.022888 | 0.086975 | 0.15106 | 0.07782 | 0.16937 | 121.7606 | -0.07782 | -0.086975 | 121.9299 | 121.8155 | 121.7743 | 0.054931 | 0.013733 | 121.7331 | -0.036621 | -0.027466 | 121.907 | 121.9254 | 121.8338 | 0.19226 | 0.10071 | 0.16937 | 0.022888 | 0.17395 | 0.10986 | 0.032043 | 0.10071 | 121.7926 | 121.8338 | -0.10986 | -0.13733 | 121.7834 | 121.843 | 121.7148 | 121.8155
932.7031 | 121.9986 | -121.7834 | 0.13275 | -0.018921 | 0.076187 | 0.013544 | 0.031657 | 0.0042918 | -0.0033966 | -0.0020785 | -0.010712 | 0.0052081 | 0.017994 | -0.0064621 | -0.0054367 | 0.016462 | -0.0036295 | -0.07782 | 0.11444 | -0.059509 | -0.064087 | 0.054932 | -0.009155 | -0.013733 | -0.041199 | 0.10071 | -0.068665 | 0.022888 | 0.10529 | 0.036621 | 0.15106 | 121.7239 | -0.01831 | -0.19684 | 121.8384 | 121.7697 | 121.7743 | 0.045776 | 0.050354 | 121.7148 | -0.032043 | -0.10986 | 121.8887 | 121.9345 | 121.8201 | 0.21973 | 0.10529 | 0.11444 | -0.004578 | 0.17395 | 0.091553 | 0.17395 | 0.16937 | 121.8979 | 121.8842 | -0.19226 | -0.20142 | 121.7194 | 121.8063 | 121.7056 | 121.7422
934.4531 | 122.0627 | -121.7514 | 0.13275 | 0.011597 | 0.076187 | 0.011621 | 0.031871 | 0.00023275 | -0.0012604 | 5.7688e-05 | -0.0015565 | 0.00093566 | 0.020771 | -0.0034713 | -0.0052231 | 0.018812 | -0.00021153 | -0.032043 | 0.07782 | -0.032043 | 0.059509 | 0.20142 | 0.09613 | 0.10986 | 0.086975 | 0.10071 | -0.032043 | 0.091553 | 0.20142 | 0.1236 | 0.19684 | 121.7194 | -0.054931 | -0.073242 | 121.9528 | 121.8613 | 121.8475 | 0.14191 | 0.12817 | 121.7194 | -0.032043 | -0.041198 | 121.9528 | 121.9482 | 121.875 | 0.22888 | 0.15564 | 0.23346 | 0.091552 | 0.23346 | 0.1236 | 0.10986 | 0.13275 | 121.8292 | 121.8521 | -0.16479 | -0.16479 | 121.8109 | 121.843 | 121.7194 | 121.8384
936.125 | 121.962 | -121.7834 | 0.16479 | -0.018921 | 0.074905 | 0.012903 | 0.031657 | -0.0029714 | -0.0057464 | -0.0029331 | -0.0015565 | 0.0032855 | 0.017994 | -0.0043259 | -0.0060777 | 0.016462 | -0.0040567 | -0.09613 | 0.10071 | -0.068665 | -0.059509 | 0.073242 | -0.013733 | -0.013733 | -0.086975 | 0.13275 | -0.064087 | -0.027466 | 0.054932 | 0 | 0.09613 | 121.7148 | -0.064087 | -0.2243 | 121.8567 | 121.7697 | 121.7697 | 0.054932 | 0.054932 | 121.7194 | -0.032044 | -0.19226 | 121.8384 | 121.8796 | 121.7834 | 0.16022 | 0.064087 | 0.14191 | 0.009156 | 0.11902 | 0.036621 | 0.16937 | 0.19684 | 121.8842 | 121.9162 | -0.23346 | -0.22888 | 121.7239 | 121.756 | 121.6873 | 121.6965
937.875 | 121.9528 | -121.7972 | 0.14648 | -0.0036622 | 0.076187 | 0.017175 | 0.035075 | -0.00062165 | -0.0046782 | 0.00027129 | -0.0046081 | 0.0041401 | 0.019703 | -0.0060349 | 0.00033115 | 0.018812 | -0.0027749 | -0.07782 | 0.10986 | -0.054932 | -0.09613 | 0.032043 | -0.07782 | -0.027466 | -0.045776 | 0.10529 | -0.07782 | -0.004578 | 0.050354 | -0.009155 | 0.1236 | 121.7422 | -0.036621 | -0.24261 | 121.8292 | 121.7697 | 121.7194 | 0.027466 | -0.022888 | 121.7194 | -0.041198 | -0.15106 | 121.8475 | 121.9208 | 121.788 | 0.20142 | 0.068665 | 0.086975 | -0.041198 | 0.12817 | 0.073242 | 0.16479 | 0.18311 | 121.907 | 121.9025 | -0.20142 | -0.2243 | 121.701 | 121.7926 | 121.7194 | 121.7514
939.5469 | 121.9711 | -121.8063 | 0.15106 | -0.0036622 | 0.075759 | 0.014398 | 0.032084 | 0.0034372 | -0.004251 | -0.0016513 | -0.0076599 | 0.0037127 | 0.019062 | -0.0043259 | -0.0033005 | 0.017743 | -0.0034159 | -0.073242 | 0.12817 | -0.059509 | -0.091553 | 0.041199 | -0.068665 | -0.032043 | -0.073242 | 0.10986 | -0.064087 | 0 | 0.045776 | -0.032043 | 0.12817 | 121.7468 | -0.022888 | -0.24261 | 121.8475 | 121.7743 | 121.7377 | 0.027466 | -0.009156 | 121.7422 | -0.041199 | -0.15106 | 121.8521 | 121.9345 | 121.7743 | 0.19226 | 0.032044 | 0.10071 | -0.032044 | 0.10986 | 0.064087 | 0.18768 | 0.17395 | 121.9345 | 121.9162 | -0.21057 | -0.21515 | 121.7148 | 121.8063 | 121.7331 | 121.7331
941.2969 | 122.0901 | -121.7468 | 0.12817 | -0.0036622 | 0.074691 | 0.016321 | 0.032298 | 0.0032236 | -0.00083304 | -0.0022921 | -0.010712 | 0.0028583 | 0.019489 | 0.0044327 | -9.605e-05 | 0.018812 | -0.0025613 | 0.022888 | 0.073242 | -0.018311 | 0.045776 | 0.18768 | 0.027466 | 0.073242 | 0.09613 | 0.068665 | -0.018311 | 0.11902 | 0.19684 | 0.1236 | 0.23804 | 121.7285 | -0.054932 | -0.082398 | 121.9345 | 121.8201 | 121.7743 | 0.091553 | 0.045777 | 121.7285 | -0.059509 | -0.009155 | 121.9437 | 121.9849 | 121.8704 | 0.25635 | 0.14191 | 0.20599 | 0.064087 | 0.21515 | 0.13733 | 0.091553 | 0.086976 | 121.8201 | 121.8155 | -0.14649 | -0.14649 | 121.7926 | 121.8658 | 121.7697 | 121.843
943.0469 | 122.0306 | -121.7697 | 0.1236 | -0.018921 | 0.076187 | 0.016107 | 0.031443 | -0.0019034 | -0.0044646 | -0.0035739 | -0.0076599 | 0.0032855 | 0.016498 | -0.0013351 | -0.0030869 | 0.019025 | 0.00021567 | -0.073242 | 0.073242 | -0.041199 | -0.022888 | 0.1236 | 0.018311 | 0.050354 | 0.013733 | 0.073242 | -0.022888 | 0.050354 | 0.10986 | 0.064087 | 0.17395 | 121.7285 | -0.050354 | -0.14648 | 121.8933 | 121.8201 | 121.788 | 0.091553 | 0.05951 | 121.7468 | -0.050354 | -0.073242 | 121.8796 | 121.9437 | 121.8338 | 0.19684 | 0.086975 | 0.16479 | 0.018311 | 0.13275 | 0.073242 | 0.11444 | 0.09613 | 121.843 | 121.843 | -0.16479 | -0.14648 | 121.7468 | 121.8201 | 121.6965 | 121.7834
944.7344 | 122.0627 | -121.7239 | 0.11444 | -0.0036622 | 0.073837 | 0.012689 | 0.030589 | 0.001301 | -0.0040374 | -0.00058311 | -0.0015565 | 0.0017901 | 0.01778 | -5.3326e-05 | -0.0026597 | 0.019025 | -0.00021153 | -0.036621 | 0.064087 | -0.050354 | 0.009155 | 0.15564 | 0.059509 | 0.073242 | 0.064087 | 0.07782 | -0.032043 | 0.10071 | 0.18768 | 0.13733 | 0.21057 | 121.6736 | -0.050354 | -0.10529 | 121.8796 | 121.7972 | 121.7834 | 0.1236 | 0.10986 | 121.6919 | -0.036621 | -0.013733 | 121.9116 | 121.9345 | 121.8613 | 0.24261 | 0.16937 | 0.20599 | 0.059509 | 0.21973 | 0.13275 | 0.11444 | 0.10986 | 121.788 | 121.8018 | -0.16479 | -0.14648 | 121.7331 | 121.8246 | 121.6873 | 121.788
946.4844 | 122.0627 | -121.7468 | 0.11902 | -0.011291 | 0.072555 | 0.014612 | 0.031657 | 0.0045054 | -0.0046782 | -0.00058311 | -0.0046081 | 0.0026447 | 0.01778 | 0.0050735 | -0.0026597 | 0.017743 | -0.0044839 | -0.050354 | 0.091553 | -0.041199 | -0.009155 | 0.13733 | 0.036621 | 0.064087 | 0.041199 | 0.091553 | -0.027466 | 0.086975 | 0.17853 | 0.11902 | 0.21973 | 121.7056 | -0.027466 | -0.12817 | 121.8842 | 121.8109 | 121.7834 | 0.10529 | 0.07782 | 121.7194 | -0.027466 | -0.032044 | 121.9254 | 121.9666 | 121.8658 | 0.24719 | 0.14649 | 0.17853 | 0.032044 | 0.20599 | 0.11444 | 0.13275 | 0.11902 | 121.8384 | 121.8384 | -0.16022 | -0.14649 | 121.7377 | 121.8338 | 121.6965 | 121.788
948.2344 | 121.9757 | -121.7972 | 0.13733 | -0.0036622 | 0.075759 | 0.014185 | 0.033152 | 0.0017282 | -0.0023284 | -0.00058311 | -0.0015565 | 0.0030719 | 0.016498 | -0.0062485 | -0.0047959 | 0.016675 | -0.0046975 | -0.022888 | 0.09613 | -0.045776 | -0.013733 | 0.13733 | 0.036621 | 0.032043 | 0 | 0.10529 | -0.050354 | 0 | 0.086975 | 0.022888 | 0.1236 | 121.7514 | -0.041199 | -0.15106 | 121.9345 | 121.8292 | 121.8338 | 0.077819 | 0.082397 | 121.7468 | -0.032043 | -0.13733 | 121.8842 | 121.9208 | 121.8201 | 0.17395 | 0.073242 | 0.18311 | 0.032043 | 0.13733 | 0.050354 | 0.14191 | 0.15564 | 121.8933 | 121.9025 | -0.18311 | -0.18768 | 121.7834 | 121.7972 | 121.7743 | 121.7972
949.9688 | 122.0581 | -121.7422 | 0.10529 | -0.018921 | 0.076187 | 0.016534 | 0.032084 | 0.0017282 | -0.0027556 | -0.0020785 | -0.013763 | 0.0011493 | 0.019703 | 0.0037919 | 0.00054475 | 0.019025 | 0.0029929 | -0.013733 | 0.050354 | -0.013733 | 0.050354 | 0.19684 | 0.041199 | 0.07782 | 0.09613 | 0.064087 | -0.018311 | 0.10986 | 0.19684 | 0.10529 | 0.21057 | 121.7285 | -0.054932 | -0.054932 | 121.9391 | 121.8201 | 121.7834 | 0.091553 | 0.054932 | 121.7239 | -0.041199 | 0.004577 | 121.9391 | 121.9528 | 121.8475 | 0.22888 | 0.1236 | 0.21057 | 0.064087 | 0.21515 | 0.12817 | 0.064087 | 0.082398 | 121.7926 | 121.8063 | -0.11902 | -0.1236 | 121.7926 | 121.8521 | 121.7285 | 121.8384
951.6406 | 121.9849 | -121.7834 | 0.14191 | -0.011291 | 0.0764 | 0.016534 | 0.034861 | -0.00040805 | -0.0036102 | -0.0025057 | -0.0046081 | 0.0045673 | 0.020984 | -0.0062485 | -0.0018051 | 0.017316 | -0.0055521 | -0.07782 | 0.13275 | -0.064087 | -0.082397 | 0.050354 | -0.073242 | -0.036621 | -0.041199 | 0.10529 | -0.059509 | 0.013733 | 0.073242 | -0.004578 | 0.14648 | 121.7194 | -0.009156 | -0.2243 | 121.8338 | 121.7468 | 121.7102 | 0.027466 | -0.009155 | 121.7239 | -0.036621 | -0.12817 | 121.8567 | 121.9299 | 121.7789 | 0.20599 | 0.054931 | 0.11444 | -0.01831 | 0.13275 | 0.073242 | 0.19684 | 0.16479 | 121.9162 | 121.8887 | -0.20599 | -0.20142 | 121.701 | 121.7972 | 121.7056 | 121.7422
953.4062 | 122.0306 | -121.7789 | 0.12817 | -0.011291 | 0.075332 | 0.014612 | 0.031016 | -0.00040805 | -0.003183 | -0.0027195 | -0.0076599 | 0.0011493 | 0.020343 | -0.0024033 | -0.0062913 | 0.018812 | 0.0040611 | -0.018311 | 0.082397 | -0.036621 | 0.064087 | 0.19684 | 0.10071 | 0.086975 | 0.064087 | 0.064087 | -0.050354 | 0.059509 | 0.16022 | 0.091553 | 0.16022 | 121.7422 | -0.045777 | -0.064087 | 121.9757 | 121.8658 | 121.8796 | 0.1236 | 0.13733 | 121.7285 | -0.064087 | -0.068665 | 121.9391 | 121.9391 | 121.8704 | 0.21057 | 0.14191 | 0.23346 | 0.10071 | 0.21057 | 0.10986 | 0.11902 | 0.11444 | 121.8613 | 121.843 | -0.1648 | -0.17853 | 121.843 | 121.8384 | 121.7606 | 121.843
955.0781 | 122.0215 | -121.7377 | 0.1236 | -0.018921 | 0.074478 | 0.013757 | 0.03123 | 0.00066015 | -0.0044646 | -0.0046421 | -0.013763 | 0.0015765 | 0.019062 | 0.0046463 | -0.0011643 | 0.016034 | 0.00064307 | -0.054932 | 0.07782 | -0.022888 | 0 | 0.14191 | 0.018311 | 0.045776 | 0.032043 | 0.07782 | -0.022888 | 0.054932 | 0.14191 | 0.059509 | 0.18768 | 121.7148 | -0.045776 | -0.1236 | 121.8796 | 121.7834 | 121.756 | 0.068664 | 0.041199 | 121.7148 | -0.045776 | -0.068664 | 121.8796 | 121.9254 | 121.7972 | 0.21057 | 0.082397 | 0.16479 | 0.022888 | 0.16479 | 0.07782 | 0.10071 | 0.10071 | 121.8155 | 121.8155 | -0.14648 | -0.14648 | 121.7377 | 121.7926 | 121.6827 | 121.7697
956.8281 | 121.9803 | -121.8155 | 0.14191 | -0.0036622 | 0.076614 | 0.01803 | 0.033152 | -0.00040805 | -0.0029694 | -0.0027195 | -0.010712 | 0.0049945 | 0.019703 | -0.0058213 | -0.00073705 | 0.018812 | -0.0017069 | -0.068665 | 0.11902 | -0.068665 | -0.073242 | 0.050354 | -0.064087 | -0.032043 | -0.045776 | 0.10986 | -0.073242 | 0.004578 | 0.054932 | -0.027466 | 0.11902 | 121.7468 | -0.022888 | -0.21515 | 121.8658 | 121.7834 | 121.7514 | 0.036622 | 0.004578 | 121.7422 | -0.032044 | -0.13733 | 121.8704 | 121.9345 | 121.788 | 0.19226 | 0.045776 | 0.11902 | -0.004577 | 0.12817 | 0.07782 | 0.18768 | 0.18311 | 121.9345 | 121.9254 | -0.21057 | -0.21515 | 121.7422 | 121.8201 | 121.7468 | 121.7697
958.5938 | 122.0032 | -121.7697 | 0.13275 | -0.02655 | 0.076187 | 0.013544 | 0.032939 | 0.00066015 | -0.003183 | -0.0029331 | -0.0076599 | 0.0034991 | 0.017353 | -0.0096665 | -0.0011643 | 0.017957 | -0.0019205 | -0.032043 | 0.11444 | -0.059509 | -0.013733 | 0.1236 | 0.009155 | 0.018311 | 0.036621 | 0.09613 | -0.054932 | 0.041199 | 0.11444 | 0.027466 | 0.16022 | 121.7102 | -0.01831 | -0.14648 | 121.8933 | 121.788 | 121.7789 | 0.07782 | 0.068664 | 121.7148 | -0.036621 | -0.091552 | 121.8842 | 121.9299 | 121.7972 | 0.21515 | 0.082398 | 0.1831 | 0.045776 | 0.16937 | 0.096131 | 0.17395 | 0.15106 | 121.8842 | 121.8658 | -0.19226 | -0.18768 | 121.756 | 121.8109 | 121.7377 | 121.8063
960.2656 | 121.9528 | -121.8063 | 0.14648 | -0.011291 | 0.0764 | 0.012689 | 0.03422 | -0.003185 | -0.0010468 | -0.00079691 | -0.0046081 | 0.0049945 | 0.020557 | -0.0024033 | -0.0015915 | 0.019666 | -0.0012795 | -0.059509 | 0.10986 | -0.073242 | -0.041199 | 0.073242 | -0.059509 | -0.022888 | -0.059509 | 0.10986 | -0.041199 | -0.009155 | 0.059509 | -0.027466 | 0.091553 | 121.7331 | -0.036621 | -0.18768 | 121.8796 | 121.7834 | 121.7468 | 0.050354 | 0.013733 | 121.7651 | -0.036621 | -0.15564 | 121.8658 | 121.8979 | 121.7789 | 0.13275 | 0.013733 | 0.14648 | 0.032043 | 0.10071 | 0.032044 | 0.18311 | 0.15106 | 121.9162 | 121.9162 | -0.21973 | -0.18768 | 121.7651 | 121.7972 | 121.7468 | 121.7468
962 | 122.0261 | -121.788 | 0.12817 | -0.02655 | 0.071914 | 0.013757 | 0.032084 | 1.915e-05 | -0.002542 | -0.0012241 | -0.0076599 | 0.0020039 | 0.019062 | -0.00026713 | -0.0018051 | 0.019239 | -0.0034159 | -0.07782 | 0.082397 | -0.032043 | -0.009155 | 0.1236 | 0.009155 | 0.054932 | 0.018311 | 0.082397 | -0.032043 | 0.045776 | 0.14191 | 0.068665 | 0.17395 | 121.756 | -0.045777 | -0.13733 | 121.9116 | 121.843 | 121.7972 | 0.086975 | 0.041198 | 121.756 | -0.045777 | -0.082398 | 121.9299 | 121.962 | 121.8567 | 0.20599 | 0.10071 | 0.15564 | 0.022888 | 0.17395 | 0.077819 | 0.11444 | 0.11444 | 121.8704 | 121.8704 | -0.16022 | -0.16022 | 121.7789 | 121.8338 | 121.7102 | 121.8063
963.7031 | 121.9574 | -121.8109 | 0.16937 | -0.011291 | 0.077255 | 0.013544 | 0.030162 | -0.00083525 | -0.0036102 | -0.0027195 | -0.0046081 | 0.0017901 | 0.01778 | -0.0049667 | -0.0060777 | 0.016034 | 0.0042747 | -0.11444 | 0.11902 | -0.059509 | -0.09613 | 0.054932 | -0.027466 | -0.009155 | -0.10071 | 0.10529 | -0.054932 | -0.032043 | 0.054932 | 0 | 0.10986 | 121.7514 | -0.050354 | -0.2655 | 121.8658 | 121.8018 | 121.7834 | 0.050354 | 0.032043 | 121.756 | -0.064087 | -0.20142 | 121.8658 | 121.9208 | 121.8109 | 0.16479 | 0.054932 | 0.11444 | -0.036621 | 0.10986 | 0.022889 | 0.17853 | 0.16022 | 121.9299 | 121.9162 | -0.22888 | -0.22431 | 121.7148 | 121.7789 | 121.6965 | 121.7102
965.4375 | 122.0444 | -121.7743 | 0.1236 | -0.018921 | 0.074264 | 0.013544 | 0.029093 | -0.001476 | -0.0012604 | -0.0035739 | -0.0046081 | 0.0017901 | 0.018634 | 0.00037387 | 0.00011755 | 0.019025 | -0.00042513 | -0.054932 | 0.073242 | -0.036621 | -0.027466 | 0.1236 | 0.018311 | 0.036621 | -0.004578 | 0.07782 | -0.050354 | 0.050354 | 0.15106 | 0.082397 | 0.17395 | 121.7377 | -0.050354 | -0.15106 | 121.8979 | 121.8109 | 121.7926 | 0.073242 | 0.054932 | 121.7239 | -0.045776 | -0.073242 | 121.9254 | 121.9482 | 121.8567 | 0.2243 | 0.13275 | 0.16022 | 0.009155 | 0.20142 | 0.10071 | 0.10986 | 0.12817 | 121.8475 | 121.8521 | -0.16022 | -0.17395 | 121.7468 | 121.8246 | 121.7194 | 121.7697
967.1094 | 121.9849 | -121.8063 | 0.15106 | -0.0036622 | 0.07405 | 0.013757 | 0.029307 | 0.00087375 | -0.0044646 | 0.00069849 | -0.0015565 | 0.0045673 | 0.020771 | -0.0088119 | -0.0056503 | 0.017316 | -0.0032021 | -0.018311 | 0.086975 | -0.050354 | 0 | 0.1236 | 0.041199 | 0.054932 | -0.009155 | 0.091553 | -0.054932 | 0.013733 | 0.10071 | 0.027466 | 0.1236 | 121.756 | -0.064087 | -0.15106 | 121.9299 | 121.8613 | 121.8475 | 0.10529 | 0.091553 | 121.7514 | -0.059509 | -0.13733 | 121.907 | 121.9299 | 121.8338 | 0.17853 | 0.082398 | 0.17395 | 0.050354 | 0.15564 | 0.068665 | 0.13733 | 0.14649 | 121.8933 | 121.8979 | -0.20142 | -0.20599 | 121.8063 | 121.8201 | 121.788 | 121.7972
968.8438 | 121.9345 | -121.7743 | 0.13733 | -0.011291 | 0.075973 | 0.016534 | 0.032939 | -0.002117 | -0.0040374 | -0.00058311 | -0.0046081 | 0.0060627 | 0.020557 | -0.010094 | 0.00054475 | 0.018171 | -0.0019205 | -0.064087 | 0.086975 | -0.054932 | -0.054932 | 0.059509 | -0.059509 | -0.032043 | -0.07782 | 0.11902 | -0.054932 | -0.009155 | 0.032043 | -0.032043 | 0.10986 | 121.7194 | -0.050354 | -0.19226 | 121.8338 | 121.7422 | 121.7148 | 0.022889 | -0.004577 | 121.7194 | -0.01831 | -0.14648 | 121.8063 | 121.8842 | 121.7422 | 0.16479 | 0.022889 | 0.11444 | 0 | 0.086975 | 0.045777 | 0.14191 | 0.17395 | 121.8613 | 121.8933 | -0.19226 | -0.19226 | 121.7194 | 121.7651 | 121.7102 | 121.6965
970.5781 | 122.0444 | -121.7651 | 0.1236 | -0.0036622 | 0.074905 | 0.014185 | 0.029734 | 0.0017282 | -0.0036102 | -0.0014377 | 0.0014953 | 0.0026447 | 0.021198 | -0.0024033 | -0.0045823 | 0.016462 | -0.0029885 | 0 | 0.068665 | -0.032043 | 0.064087 | 0.21057 | 0.10529 | 0.091553 | 0.082397 | 0.064087 | -0.032043 | 0.09613 | 0.19226 | 0.13733 | 0.19684 | 121.7331 | -0.054931 | -0.059509 | 121.9757 | 121.8567 | 121.8704 | 0.1236 | 0.13733 | 121.7331 | -0.059509 | -0.027466 | 121.9574 | 121.962 | 121.9025 | 0.22888 | 0.16937 | 0.24261 | 0.09613 | 0.2243 | 0.12817 | 0.10071 | 0.09613 | 121.8338 | 121.8292 | -0.15564 | -0.15564 | 121.8292 | 121.8613 | 121.7651 | 121.8475
972.3125 | 121.9894 | -121.7789 | 0.12817 | -0.018921 | 0.076187 | 0.013757 | 0.032298 | 0.0010874 | -0.002542 | -0.0025057 | -0.0015565 | 0.0037127 | 0.020557 | -0.0024033 | -0.0024461 | 0.017316 | -0.0044839 | -0.036621 | 0.10071 | -0.050354 | -0.013733 | 0.10986 | -0.004578 | 0.022888 | 0.004578 | 0.10986 | -0.036621 | 0.032043 | 0.10071 | 0.013733 | 0.13733 | 121.7285 | -0.027466 | -0.14191 | 121.8887 | 121.8018 | 121.7743 | 0.073242 | 0.045776 | 121.7422 | -0.018311 | -0.096131 | 121.8796 | 121.9162 | 121.7926 | 0.17395 | 0.050354 | 0.16022 | 0.036621 | 0.13733 | 0.068664 | 0.15106 | 0.14648 | 121.8796 | 121.8887 | -0.17853 | -0.1648 | 121.7651 | 121.8109 | 121.7422 | 121.7834
973.9844 | 121.9894 | -121.7834 | 0.16937 | -0.018921 | 0.075759 | 0.014185 | 0.029521 | -0.003185 | -0.0057464 | -0.0054965 | -0.0076599 | 0.0034991 | 0.019916 | -0.0058213 | -0.0028733 | 0.019239 | -0.0055521 | -0.086975 | 0.11902 | -0.059509 | -0.068665 | 0.041199 | -0.022888 | -0.022888 | -0.07782 | 0.10986 | -0.045776 | -0.004578 | 0.07782 | 0.013733 | 0.11902 | 121.7239 | -0.050354 | -0.23804 | 121.8246 | 121.7606 | 121.7606 | 0.036621 | 0.036621 | 121.7377 | -0.05951 | -0.17395 | 121.8613 | 121.9025 | 121.7972 | 0.16479 | 0.059509 | 0.10071 | -0.009156 | 0.1236 | 0.041198 | 0.17853 | 0.15564 | 121.9025 | 121.8933 | -0.22888 | -0.21515 | 121.7148 | 121.7789 | 121.6965 | 121.7056
975.7188 | 122.0581 | -121.7789 | 0.1236 | -0.011291 | 0.07405 | 0.015253 | 0.031016 | -0.0010488 | -0.0040374 | -0.00015591 | -0.0076599 | 0.0020039 | 0.01778 | -0.0045395 | -0.0022325 | 0.018598 | 0.0025657 | -0.050354 | 0.086975 | -0.036621 | -0.013733 | 0.13733 | 0.041199 | 0.068665 | 0.036621 | 0.07782 | -0.032043 | 0.07782 | 0.16022 | 0.10986 | 0.19684 | 121.7422 | -0.036621 | -0.13733 | 121.9162 | 121.8475 | 121.8201 | 0.10529 | 0.07782 | 121.7468 | -0.045776 | -0.045776 | 121.9391 | 121.9757 | 121.8887 | 0.22888 | 0.14191 | 0.17395 | 0.022888 | 0.19226 | 0.10986 | 0.1236 | 0.10986 | 121.8658 | 121.8567 | -0.16022 | -0.15564 | 121.7651 | 121.8567 | 121.7285 | 121.8155
977.4688 | 122.0993 | -121.7697 | 0.10986 | -0.0036622 | 0.074905 | 0.014612 | 0.031657 | 0.00023275 | -0.00596 | -0.00036951 | -0.0076599 | 0.0015765 | 0.017353 | -0.0024033 | -0.0024461 | 0.016675 | -0.0014931 | -0.004578 | 0.073242 | -0.018311 | 0.068665 | 0.24261 | 0.11902 | 0.12817 | 0.14191 | 0.068665 | -0.013733 | 0.10529 | 0.21973 | 0.14648 | 0.2243 | 121.7514 | -0.036621 | -0.041198 | 122.0123 | 121.8979 | 121.8887 | 0.14649 | 0.13733 | 121.756 | -0.041198 | -0.004577 | 121.9894 | 121.994 | 121.9162 | 0.23804 | 0.16022 | 0.26093 | 0.086976 | 0.23346 | 0.11902 | 0.091553 | 0.082398 | 121.843 | 121.8384 | -0.12817 | -0.1236 | 121.8384 | 121.875 | 121.7651 | 121.9116
979.1406 | 121.9986 | -121.8063 | 0.1236 | -0.0036622 | 0.075546 | 0.016748 | 0.031657 | 0.0017282 | -0.0036102 | -0.0012241 | -0.0046081 | 0.0037127 | 0.017139 | -0.0026169 | -0.0030869 | 0.016889 | -0.0040567 | -0.013733 | 0.086975 | -0.036621 | 0.036621 | 0.16479 | 0.068665 | 0.082397 | 0.022888 | 0.091553 | -0.054932 | 0.027466 | 0.13275 | 0.045776 | 0.14191 | 121.7697 | -0.036621 | -0.086975 | 121.9711 | 121.8887 | 121.875 | 0.11902 | 0.10529 | 121.7514 | -0.032043 | -0.09613 | 121.9391 | 121.9482 | 121.8521 | 0.19684 | 0.10071 | 0.20142 | 0.073242 | 0.18768 | 0.082398 | 0.1236 | 0.14649 | 121.8933 | 121.8979 | -0.16022 | -0.17853 | 121.843 | 121.8338 | 121.7926 | 121.8292
980.8906 | 122.0078 | -121.788 | 0.13733 | -0.018921 | 0.076187 | 0.013116 | 0.032725 | 0.0010874 | -0.0051056 | -0.0012241 | -0.0076599 | 0.0041401 | 0.018634 | -0.0090255 | -0.0033005 | 0.01753 | -0.0027749 | -0.027466 | 0.10529 | -0.045776 | -0.018311 | 0.10529 | 0.009155 | 0.009155 | 0.018311 | 0.091553 | -0.050354 | 0.041199 | 0.14191 | 0.041199 | 0.14648 | 121.7422 | -0.032043 | -0.15564 | 121.8933 | 121.7972 | 121.7972 | 0.054931 | 0.054931 | 121.7377 | -0.045776 | -0.09613 | 121.9299 | 121.9345 | 121.8292 | 0.19684 | 0.091553 | 0.15106 | 0.027465 | 0.19226 | 0.091553 | 0.15106 | 0.14191 | 121.8933 | 121.8796 | -0.18311 | -0.18768 | 121.7697 | 121.8292 | 121.7606 | 121.8063
982.5781 | 122.0673 | -121.7514 | 0.10986 | -0.018921 | 0.073837 | 0.015039 | 0.031443 | -0.00040805 | -0.0010468 | -0.0022921 | -0.0046081 | 0.0026447 | 0.018634 | -0.0066757 | -0.00030965 | 0.019452 | -0.00042513 | -0.032043 | 0.059509 | 0.004578 | 0.032043 | 0.20599 | 0.036621 | 0.07782 | 0.07782 | 0.064087 | -0.009155 | 0.11444 | 0.17853 | 0.10529 | 0.21057 | 121.756 | -0.050354 | -0.07782 | 121.9574 | 121.8292 | 121.788 | 0.073242 | 0.032043 | 121.7422 | -0.045776 | 0.004578 | 121.9299 | 121.962 | 121.8567 | 0.21973 | 0.11444 | 0.20142 | 0.027465 | 0.18768 | 0.1236 | 0.054931 | 0.073242 | 121.8109 | 121.8155 | -0.10529 | -0.11902 | 121.7834 | 121.8658 | 121.7194 | 121.8292
984.3125 | 122.0032 | -121.7697 | 0.14191 | -0.02655 | 0.074691 | 0.013757 | 0.031443 | 0.00301 | -0.0033966 | -0.00058311 | -0.010712 | 0.0045673 | 0.018421 | -0.010307 | -0.0026597 | 0.01753 | -0.0019205 | -0.045776 | 0.091553 | -0.059509 | -0.027466 | 0.11444 | 0.013733 | 0.013733 | 0.004578 | 0.11902 | -0.050354 | 0.045776 | 0.11902 | 0.045776 | 0.16937 | 121.7102 | -0.050354 | -0.16937 | 121.8842 | 121.7834 | 121.7834 | 0.073242 | 0.073242 | 121.7194 | -0.022888 | -0.096131 | 121.8887 | 121.9391 | 121.8155 | 0.21973 | 0.09613 | 0.17395 | 0.032043 | 0.16937 | 0.09613 | 0.15106 | 0.16937 | 121.8613 | 121.8887 | -0.20142 | -0.19226 | 121.7422 | 121.8155 | 121.7239 | 121.7743
985.9844 | 122.0078 | -121.7926 | 0.12817 | -0.018921 | 0.074264 | 0.013116 | 0.029734 | -0.00040805 | -0.0038238 | 0.0011257 | -0.0046081 | 0.0043537 | 0.018421 | -0.0073165 | -0.0020187 | 0.017957 | 0.0012839 | -0.050354 | 0.09613 | -0.059509 | -0.041199 | 0.10071 | 0.013733 | 0.027466 | -0.027466 | 0.09613 | -0.059509 | 0.045776 | 0.1236 | 0.050354 | 0.15564 | 121.7331 | -0.032044 | -0.16937 | 121.8933 | 121.8201 | 121.8063 | 0.086975 | 0.073242 | 121.7331 | -0.032044 | -0.082398 | 121.9162 | 121.9482 | 121.843 | 0.21515 | 0.10986 | 0.16022 | 0.01831 | 0.1831 | 0.10528 | 0.15564 | 0.15564 | 121.8887 | 121.8887 | -0.18768 | -0.18768 | 121.7514 | 121.8384 | 121.7422 | 121.7651
987.7188 | 122.081 | -121.7468 | 0.10529 | 0.0039673 | 0.07341 | 0.015253 | 0.032511 | -0.0027578 | -0.002542 | -0.0025057 | -0.0015565 | 0.0024311 | 0.016498 | -0.0049667 | 0.0033217 | 0.020521 | -0.0040567 | -0.004578 | 0.086975 | -0.032043 | 0.036621 | 0.16937 | 0.054932 | 0.068665 | 0.082397 | 0.059509 | -0.032043 | 0.12817 | 0.18768 | 0.1236 | 0.22888 | 121.7148 | -0.018311 | -0.068665 | 121.9162 | 121.8155 | 121.8018 | 0.10071 | 0.086975 | 121.7148 | -0.045777 | 0.022888 | 121.9345 | 121.9757 | 121.8704 | 0.26093 | 0.15564 | 0.20142 | 0.068664 | 0.21973 | 0.16022 | 0.11902 | 0.091552 | 121.8338 | 121.8063 | -0.13733 | -0.13733 | 121.7834 | 121.875 | 121.7422 | 121.8292
989.3906 | 122.0444 | -121.7697 | 0.10986 | -0.0036622 | 0.073837 | 0.013757 | 0.028025 | -0.00019445 | -0.0036102 | -0.0014377 | -0.0076599 | 0.00072206 | 0.020984 | 0.0014419 | -0.00073705 | 0.020307 | -0.00085233 | -0.054932 | 0.086975 | -0.027466 | -0.027466 | 0.12817 | 0.022888 | 0.041199 | 0.009155 | 0.068665 | -0.036621 | 0.073242 | 0.14648 | 0.082397 | 0.18768 | 121.7422 | -0.022888 | -0.13733 | 121.8979 | 121.8109 | 121.7926 | 0.068665 | 0.050354 | 121.7331 | -0.041198 | -0.036621 | 121.9162 | 121.9574 | 121.8521 | 0.2243 | 0.11902 | 0.15564 | 0 | 0.18311 | 0.10986 | 0.11444 | 0.10529 | 121.8567 | 121.8384 | -0.13733 | -0.14648 | 121.7422 | 121.843 | 121.7148 | 121.7789
991.0625 | 122.0947 | -121.7743 | 0.1236 | -0.018921 | 0.073196 | 0.014398 | 0.031016 | -0.0010488 | -0.0010468 | -0.0010105 | -0.0015565 | 0.0011493 | 0.017566 | -0.0013351 | -0.0054367 | 0.017743 | -0.00085233 | -0.009155 | 0.082397 | -0.013733 | 0.045776 | 0.2243 | 0.10986 | 0.10071 | 0.10529 | 0.059509 | -0.032043 | 0.10986 | 0.2243 | 0.15106 | 0.21973 | 121.7606 | -0.041199 | -0.07782 | 121.9986 | 121.875 | 121.8842 | 0.11444 | 0.1236 | 121.7422 | -0.064087 | -0.013733 | 121.9986 | 121.994 | 121.9254 | 0.25177 | 0.18311 | 0.23804 | 0.059509 | 0.25635 | 0.14191 | 0.09613 | 0.091552 | 121.8567 | 121.8338 | -0.13733 | -0.15564 | 121.8201 | 121.8842 | 121.7651 | 121.8796
992.8125 | 122.0078 | -121.756 | 0.13733 | -0.018921 | 0.074691 | 0.013544 | 0.034434 | 0.001301 | -0.0027556 | 0.00091209 | -0.0046081 | 0.0037127 | 0.019489 | -0.0047531 | -0.0030869 | 0.016462 | 0.0012839 | -0.036621 | 0.11902 | -0.054932 | -0.050354 | 0.07782 | 0 | 0.009155 | -0.004578 | 0.11902 | -0.054932 | 0.036621 | 0.11902 | 0.045776 | 0.15564 | 121.701 | -0.01831 | -0.18768 | 121.8338 | 121.7651 | 121.756 | 0.064087 | 0.054932 | 121.701 | -0.01831 | -0.10071 | 121.875 | 121.9116 | 121.8018 | 0.21057 | 0.10071 | 0.13275 | 0.004578 | 0.17395 | 0.091553 | 0.17395 | 0.17395 | 121.875 | 121.875 | -0.19226 | -0.19226 | 121.7056 | 121.7926 | 121.7194 | 121.7514
994.5469 | 122.0215 | -121.7743 | 0.11902 | 0.0039673 | 0.073837 | 0.014398 | 0.033793 | -0.00083525 | -0.001474 | -0.0022921 | -0.0015565 | 0.0022175 | 0.019275 | -0.0019759 | -0.00095065 | 0.01753 | -0.00063873 | -0.07782 | 0.11444 | -0.091553 | -0.073242 | 0.059509 | -0.059509 | -0.018311 | -0.013733 | 0.10986 | -0.068665 | 0.054932 | 0.10071 | 0.036621 | 0.16022 | 121.6827 | -0.004578 | -0.19226 | 121.8338 | 121.756 | 121.7148 | 0.073242 | 0.032044 | 121.7056 | -0.009156 | -0.064087 | 121.875 | 121.9345 | 121.8109 | 0.22888 | 0.10529 | 0.15106 | 0.018311 | 0.16937 | 0.1236 | 0.20599 | 0.17853 | 121.8887 | 121.8842 | -0.21057 | -0.18768 | 121.7011 | 121.8292 | 121.6965 | 121.7606
996.2969 | 122.0123 | -121.7972 | 0.13275 | -0.0036622 | 0.075332 | 0.014185 | 0.032725 | 0.0025828 | -0.00061944 | -0.0029331 | -0.0046081 | 0.0047809 | 0.019062 | -0.0049667 | -0.0015915 | 0.018171 | -0.0046975 | -0.041199 | 0.10529 | -0.045776 | -0.018311 | 0.13275 | 0.022888 | 0.032043 | 0.032043 | 0.086975 | -0.045776 | 0.059509 | 0.11902 | 0.032043 | 0.14648 | 121.7514 | -0.027465 | -0.15106 | 121.9299 | 121.8292 | 121.8201 | 0.077819 | 0.068664 | 121.7514 | -0.045776 | -0.073242 | 121.9162 | 121.9437 | 121.8292 | 0.19226 | 0.077819 | 0.17853 | 0.027465 | 0.16479 | 0.10528 | 0.15106 | 0.13275 | 121.9025 | 121.8842 | -0.17853 | -0.17853 | 121.7789 | 121.8567 | 121.756 | 121.8292
998.0312 | 122.0078 | -121.7926 | 0.13733 | -0.018921 | 0.073837 | 0.014185 | 0.032298 | 0.0019418 | -0.0038238 | 5.7688e-05 | -0.0015565 | 0.0047809 | 0.019275 | 0.0014419 | -0.0011643 | 0.019452 | 0.0025657 | -0.027466 | 0.10986 | -0.054932 | -0.009155 | 0.11444 | 0.027466 | 0.018311 | 0.013733 | 0.11444 | -0.050354 | 0.050354 | 0.11444 | 0.022888 | 0.15106 | 121.7377 | -0.027466 | -0.14648 | 121.907 | 121.8109 | 121.8201 | 0.073243 | 0.082398 | 121.7422 | -0.022888 | -0.086975 | 121.907 | 121.9437 | 121.8155 | 0.20142 | 0.073242 | 0.16937 | 0.045777 | 0.16479 | 0.10071 | 0.16479 | 0.16479 | 121.9025 | 121.907 | -0.19226 | -0.18768 | 121.7834 | 121.843 | 121.7651 | 121.8063
999.7812 | 122.0123 | -121.7834 | 0.1236 | 0.0039673 | 0.0764 | 0.014185 | 0.031657 | 0.0010874 | 0.00023496 | -0.0022921 | -0.0015565 | 0.0037127 | 0.020557 | -0.0056075 | 0.00097195 | 0.01988 | -0.0025613 | -0.082397 | 0.1236 | -0.082397 | -0.07782 | 0.054932 | -0.054932 | -0.022888 | -0.032043 | 0.09613 | -0.050354 | 0.036621 | 0.086975 | 0.022888 | 0.14191 | 121.701 | 0 | -0.20142 | 121.8384 | 121.7606 | 121.7285 | 0.059509 | 0.027465 | 121.7331 | -0.027466 | -0.086975 | 121.8704 | 121.9254 | 121.8063 | 0.19226 | 0.073242 | 0.13733 | 0.004577 | 0.13733 | 0.086975 | 0.20599 | 0.14648 | 121.907 | 121.8796 | -0.20599 | -0.17395 | 121.7056 | 121.8201 | 121.701 | 121.7514
1001.5312 | 122.049 | -121.7743 | 0.13275 | -0.0036622 | 0.073623 | 0.016107 | 0.029521 | 0.0036508 | -0.0029694 | 0.00027129 | -0.0015565 | 0.0043537 | 0.019916 | -0.00048073 | -0.0011643 | 0.018171 | 0.0019247 | -0.082397 | 0.11444 | -0.064087 | -0.045776 | 0.073242 | -0.036621 | -0.004578 | 0.009155 | 0.091553 | -0.041199 | 0.07782 | 0.13275 | 0.054932 | 0.19684 | 121.7102 | -0.01831 | -0.17853 | 121.8475 | 121.7697 | 121.7377 | 0.059509 | 0.027466 | 121.7331 | -0.041198 | -0.054931 | 121.907 | 121.9711 | 121.8292 | 0.23804 | 0.096131 | 0.13733 | 0.018311 | 0.17395 | 0.11902 | 0.17853 | 0.13275 | 121.8887 | 121.8658 | -0.19684 | -0.17395 | 121.7285 | 121.8521 | 121.6919 | 121.7834
1003.2188 | 122.0078 | -121.8109 | 0.13733 | -0.018921 | 0.07341 | 0.014398 | 0.031016 | -0.00062165 | -0.0046782 | -0.0010105 | -0.0076599 | 0.0034991 | 0.019062 | -0.0034713 | -0.0039413 | 0.019239 | 0.0017111 | -0.045776 | 0.10071 | -0.059509 | -0.036621 | 0.11444 | 0.004578 | 0.018311 | 0.018311 | 0.09613 | -0.036621 | 0.045776 | 0.11444 | 0.041199 | 0.15564 | 121.7514 | -0.036621 | -0.17395 | 121.9254 | 121.8292 | 121.8155 | 0.07782 | 0.064087 | 121.7743 | -0.041199 | -0.091553 | 121.9254 | 121.9666 | 121.8521 | 0.19226 | 0.07782 | 0.17395 | 0.022888 | 0.15106 | 0.082397 | 0.16022 | 0.13275 | 121.9116 | 121.907 | -0.19684 | -0.17395 | 121.7743 | 121.8567 | 121.7651 | 121.8292
1004.9531 | 122.0535 | -121.7926 | 0.11444 | -0.018921 | 0.071487 | 0.014398 | 0.028025 | 0.00066015 | -0.0040374 | -0.00079691 | -0.0046081 | 0.0022175 | 0.019275 | 0.0010147 | -0.0015915 | 0.017743 | 0.0034201 | -0.073242 | 0.086975 | -0.032043 | -0.022888 | 0.12817 | 0.032043 | 0.054932 | 0.004578 | 0.068665 | -0.022888 | 0.064087 | 0.13275 | 0.068665 | 0.1831 | 121.7606 | -0.027466 | -0.13733 | 121.9208 | 121.8475 | 121.8246 | 0.086975 | 0.064086 | 121.7697 | -0.045776 | -0.050354 | 121.9254 | 121.9757 | 121.8613 | 0.20599 | 0.091553 | 0.16022 | 0.009155 | 0.15564 | 0.086975 | 0.11902 | 0.091553 | 121.8796 | 121.8613 | -0.14648 | -0.13733 | 121.7697 | 121.8567 | 121.7194 | 121.7972
1006.625 | 122.081 | -121.7514 | 0.1236 | -0.011291 | 0.075546 | 0.013544 | 0.029521 | 0.00066015 | -0.00040584 | -0.0022921 | -0.0046081 | 0.0022175 | 0.017994 | -0.0011215 | -0.0022325 | 0.018171 | -0.0019205 | -0.059509 | 0.091553 | -0.041199 | 0 | 0.14648 | 0.054932 | 0.073242 | 0.036621 | 0.07782 | -0.050354 | 0.091553 | 0.16479 | 0.11902 | 0.21057 | 121.7102 | -0.032043 | -0.1236 | 121.8979 | 121.8246 | 121.8063 | 0.11444 | 0.096131 | 121.701 | -0.045776 | -0.032043 | 121.9162 | 121.962 | 121.8704 | 0.26093 | 0.16937 | 0.18768 | 0.041199 | 0.21515 | 0.14191 | 0.13275 | 0.12817 | 121.843 | 121.8292 | -0.16479 | -0.17395 | 121.7514 | 121.843 | 121.6919 | 121.788
1008.3125 | 122.1222 | -121.756 | 0.11902 | -0.018921 | 0.074905 | 0.013544 | 0.029521 | 0.0017282 | -0.0033966 | -0.0029331 | -0.0046081 | 0.00072206 | 0.022052 | -0.0015487 | -0.0037277 | 0.017957 | 0.0010703 | -0.013733 | 0.082397 | -0.036621 | 0.059509 | 0.22888 | 0.11902 | 0.12817 | 0.13733 | 0.082397 | -0.013733 | 0.12817 | 0.22888 | 0.14648 | 0.22888 | 121.7194 | -0.036622 | -0.05951 | 121.9849 | 121.8842 | 121.875 | 0.1648 | 0.15564 | 121.7422 | -0.036622 | 0.009155 | 121.9849 | 121.9849 | 121.9025 | 0.24261 | 0.16022 | 0.2655 | 0.09613 | 0.24261 | 0.14191 | 0.11902 | 0.09613 | 121.8384 | 121.8384 | -0.15564 | -0.13275 | 121.8155 | 121.8842 | 121.7422 | 121.8933
1010.0469 | 122.0673 | -121.7422 | 0.10529 | -0.011291 | 0.07405 | 0.013116 | 0.031016 | -0.00040805 | -0.0019012 | -0.0010105 | -0.010712 | 0.0026447 | 0.018421 | -0.0015487 | -0.0013779 | 0.017743 | -0.0021341 | -0.018311 | 0.059509 | -0.009155 | 0.036621 | 0.1831 | 0.059509 | 0.07782 | 0.09613 | 0.068665 | -0.009155 | 0.10529 | 0.16022 | 0.10529 | 0.21057 | 121.7331 | -0.045777 | -0.068665 | 121.9254 | 121.8201 | 121.8018 | 0.086975 | 0.068664 | 121.7331 | -0.036621 | 0 | 121.9025 | 121.9528 | 121.8475 | 0.21973 | 0.11444 | 0.19226 | 0.045776 | 0.16937 | 0.11444 | 0.068664 | 0.07782 | 121.8018 | 121.8109 | -0.11444 | -0.11444 | 121.7789 | 121.8475 | 121.7239 | 121.8384
1011.7812 | 122.0673 | -121.7743 | 0.11444 | -0.02655 | 0.07341 | 0.013544 | 0.031443 | -0.002117 | -0.0021148 | -0.0052829 | -0.0046081 | 0.0026447 | 0.018207 | 0.0014419 | -0.0035141 | 0.01753 | -0.0032021 | -0.054932 | 0.082397 | -0.027466 | -0.018311 | 0.1236 | 0.022888 | 0.041199 | 0 | 0.09613 | -0.032043 | 0.054932 | 0.14191 | 0.091553 | 0.17853 | 121.7468 | -0.032044 | -0.13275 | 121.8979 | 121.8155 | 121.7972 | 0.068665 | 0.050354 | 121.7422 | -0.018311 | -0.059509 | 121.9162 | 121.9528 | 121.8658 | 0.21057 | 0.1236 | 0.15106 | 0.009155 | 0.17395 | 0.086975 | 0.10986 | 0.12817 | 121.8567 | 121.8704 | -0.14191 | -0.14648 | 121.756 | 121.8292 | 121.7194 | 121.7743
1013.4688 | 122.0306 | -121.7743 | 0.11902 | -0.0036622 | 0.074691 | 0.012903 | 0.031443 | 0.001301 | -0.00061944 | -0.0025057 | -0.0046081 | 0.0054217 | 0.018634 | -0.0017623 | 0.00011755 | 0.017957 | -0.0036295 | -0.073242 | 0.09613 | -0.07782 | -0.064087 | 0.07782 | -0.054932 | -0.022888 | -0.004578 | 0.10986 | -0.068665 | 0.041199 | 0.11444 | 0.041199 | 0.16479 | 121.6965 | -0.022889 | -0.18311 | 121.8521 | 121.7514 | 121.7194 | 0.054932 | 0.022888 | 121.7056 | -0.009156 | -0.07782 | 121.8887 | 121.9391 | 121.8155 | 0.23346 | 0.10986 | 0.15564 | 0.013733 | 0.18311 | 0.10986 | 0.17395 | 0.17853 | 121.8704 | 121.8842 | -0.19684 | -0.18768 | 121.7102 | 121.8155 | 121.7011 | 121.7697
1015.2031 | 121.994 | -121.7743 | 0.14648 | -0.011291 | 0.074478 | 0.015466 | 0.031016 | -0.0012624 | -0.0033966 | -0.0037875 | 0.0014953 | 0.0024311 | 0.019275 | -0.011162 | -0.0026597 | 0.016889 | -0.0012795 | -0.018311 | 0.091553 | -0.050354 | 0.013733 | 0.16479 | 0.054932 | 0.068665 | 0.013733 | 0.09613 | -0.036621 | 0.013733 | 0.10071 | 0.036621 | 0.10986 | 121.7239 | -0.054931 | -0.13275 | 121.9391 | 121.843 | 121.8292 | 0.11902 | 0.10529 | 121.7377 | -0.050354 | -0.13275 | 121.875 | 121.8842 | 121.8109 | 0.14648 | 0.073242 | 0.21515 | 0.064087 | 0.13733 | 0.050354 | 0.14191 | 0.13275 | 121.8658 | 121.8704 | -0.19684 | -0.18311 | 121.788 | 121.788 | 121.756 | 121.788
1016.9375 | 122.0673 | -121.7789 | 0.1236 | -0.03418 | 0.075118 | 0.013971 | 0.029521 | -0.0019034 | -0.0012604 | -0.0027195 | -0.0046081 | 0.0011493 | 0.017353 | 0.0035783 | -0.0015915 | 0.018171 | -0.0023477 | -0.073242 | 0.082397 | -0.022888 | -0.018311 | 0.13275 | 0.032043 | 0.059509 | 0.027466 | 0.07782 | -0.041199 | 0.068665 | 0.15106 | 0.10529 | 0.18768 | 121.756 | -0.041199 | -0.14191 | 121.9116 | 121.8384 | 121.8109 | 0.082397 | 0.054931 | 121.7377 | -0.045776 | -0.054931 | 121.9299 | 121.9666 | 121.8842 | 0.22888 | 0.14649 | 0.15564 | 0.004577 | 0.19226 | 0.10986 | 0.10528 | 0.11902 | 121.8613 | 121.8567 | -0.14648 | -0.16479 | 121.7606 | 121.8475 | 121.7056 | 121.8063
1018.6875 | 122.0078 | -121.7697 | 0.13275 | 0.0039673 | 0.0764 | 0.013116 | 0.033793 | -0.0016898 | -0.0016876 | -0.00079691 | -0.0046081 | 0.0022175 | 0.019703 | -0.0032577 | -0.0024461 | 0.019025 | 0.0010703 | -0.032043 | 0.10071 | -0.059509 | 0 | 0.13733 | 0.022888 | 0.032043 | 0.036621 | 0.091553 | -0.032043 | 0.050354 | 0.1236 | 0.027466 | 0.15564 | 121.7102 | -0.032043 | -0.13275 | 121.907 | 121.8018 | 121.7926 | 0.091552 | 0.082397 | 121.7377 | -0.041198 | -0.082397 | 121.8933 | 121.9254 | 121.7972 | 0.18768 | 0.059509 | 0.19684 | 0.059509 | 0.15564 | 0.082397 | 0.16022 | 0.1236 | 121.8704 | 121.8613 | -0.19226 | -0.16479 | 121.7697 | 121.8201 | 121.7377 | 121.8063
1020.4375 | 122.0444 | -121.788 | 0.12817 | -0.011291 | 0.076187 | 0.013757 | 0.029093 | 1.915e-05 | -0.0036102 | -0.0022921 | -0.0046081 | 0.0030719 | 0.017139 | -0.0051803 | -0.0020187 | 0.018598 | -0.0036295 | -0.059509 | 0.07782 | -0.041199 | -0.018311 | 0.13733 | 0.018311 | 0.041199 | -0.013733 | 0.07782 | -0.041199 | 0.041199 | 0.12817 | 0.068665 | 0.16937 | 121.7468 | -0.050354 | -0.14649 | 121.9254 | 121.8292 | 121.8063 | 0.082398 | 0.05951 | 121.7468 | -0.050354 | -0.086975 | 121.9162 | 121.9574 | 121.8567 | 0.21057 | 0.10986 | 0.17853 | 0.022888 | 0.16937 | 0.082398 | 0.11902 | 0.11902 | 121.8658 | 121.8658 | -0.16937 | -0.16937 | 121.7697 | 121.8292 | 121.7285 | 121.7743
1022.125 | 122.0764 | -121.7606 | 0.11902 | -0.018921 | 0.074905 | 0.012476 | 0.029093 | -0.0051076 | -0.002542 | -0.0025057 | -0.0046081 | 0.0020039 | 0.02013 | -0.0019759 | -0.00073705 | 0.018384 | -0.00063873 | -0.041199 | 0.09613 | -0.036621 | 0.009155 | 0.15106 | 0.073242 | 0.068665 | 0.050354 | 0.082397 | -0.036621 | 0.091553 | 0.16479 | 0.11444 | 0.21057 | 121.7239 | -0.022889 | -0.10986 | 121.9116 | 121.8292 | 121.8338 | 0.10529 | 0.10986 | 121.7239 | -0.036622 | -0.027466 | 121.9254 | 121.9711 | 121.875 | 0.24719 | 0.15106 | 0.18768 | 0.045776 | 0.20142 | 0.12817 | 0.13275 | 0.11902 | 121.8567 | 121.843 | -0.15564 | -0.15564 | 121.7697 | 121.8521 | 121.7194 | 121.8109
1023.875 | 121.9711 | -121.8201 | 0.16022 | -0.0036622 | 0.076614 | 0.017175 | 0.032084 | 0.0040782 | 0.00023496 | -0.0025057 | -0.0015565 | 0.0064899 | 0.019489 | -0.00026713 | -0.00052345 | 0.017103 | -0.0034159 | -0.082397 | 0.10986 | -0.07782 | -0.073242 | 0.018311 | -0.073242 | -0.032043 | -0.068665 | 0.1236 | -0.073242 | 0 | 0.041199 | -0.036621 | 0.1236 | 121.7422 | -0.050354 | -0.23346 | 121.8384 | 121.788 | 121.7468 | 0.045777 | 0.004578 | 121.7468 | -0.036621 | -0.16022 | 121.8613 | 121.9437 | 121.7834 | 0.19684 | 0.036621 | 0.096131 | 0.004578 | 0.11444 | 0.073242 | 0.18768 | 0.19684 | 121.9299 | 121.9437 | -0.23804 | -0.23346 | 121.7468 | 121.8201 | 121.7377 | 121.7514
1025.5469 | 122.0856 | -121.7743 | 0.09613 | -0.018921 | 0.075332 | 0.013544 | 0.031016 | 0.0027964 | -0.0027556 | -0.0044285 | -0.013763 | 0.00029486 | 0.018207 | -0.0068893 | 0.0013991 | 0.020093 | 0.0017111 | -0.013733 | 0.07782 | -0.018311 | 0.045776 | 0.20599 | 0.054932 | 0.064087 | 0.10071 | 0.068665 | -0.013733 | 0.12817 | 0.1831 | 0.10071 | 0.21515 | 121.756 | -0.01831 | -0.050354 | 121.9803 | 121.8384 | 121.8292 | 0.082398 | 0.073243 | 121.7606 | -0.027465 | 0.032044 | 121.9574 | 121.9894 | 121.875 | 0.22888 | 0.11444 | 0.22431 | 0.064087 | 0.19684 | 0.14191 | 0.096131 | 0.082398 | 121.8521 | 121.843 | -0.11444 | -0.10986 | 121.8201 | 121.9025 | 121.7606 | 121.875
1027.2812 | 121.9849 | -121.8109 | 0.15564 | 0.0039673 | 0.078109 | 0.016534 | 0.032298 | 0.0023692 | -0.002542 | -0.00079691 | -0.0046081 | 0.0037127 | 0.018634 | -0.0030441 | -0.0018051 | 0.018598 | 2.068e-06 | -0.073242 | 0.12817 | -0.059509 | -0.082397 | 0.041199 | -0.073242 | -0.032043 | -0.064087 | 0.11444 | -0.054932 | -0.009155 | 0.054932 | -0.018311 | 0.1236 | 121.7514 | -0.027466 | -0.23804 | 121.8521 | 121.7789 | 121.7377 | 0.027466 | -0.013733 | 121.756 | -0.041199 | -0.16479 | 121.8658 | 121.9345 | 121.7926 | 0.17853 | 0.036621 | 0.10071 | -0.022888 | 0.10986 | 0.045777 | 0.18768 | 0.16937 | 121.9391 | 121.9254 | -0.21515 | -0.21057 | 121.7285 | 121.8018 | 121.7377 | 121.7468
1028.9531 | 122.0947 | -121.7834 | 0.13733 | 0.0039673 | 0.075546 | 0.015039 | 0.029521 | -0.0027578 | -0.00061944 | -0.0020785 | -0.0015565 | 0.0015765 | 0.019703 | 0.0046463 | -0.0030869 | 0.020093 | -0.0017069 | -0.009155 | 0.068665 | -0.032043 | 0.082397 | 0.23804 | 0.10529 | 0.10071 | 0.10986 | 0.073242 | -0.027466 | 0.086975 | 0.2243 | 0.14191 | 0.20142 | 121.7514 | -0.068664 | -0.054932 | 122.0215 | 121.8842 | 121.8887 | 0.13275 | 0.13733 | 121.756 | -0.064087 | -0.050354 | 122.0078 | 121.9849 | 121.9254 | 0.22888 | 0.16937 | 0.27008 | 0.11444 | 0.25177 | 0.11444 | 0.10071 | 0.10071 | 121.8521 | 121.8567 | -0.16937 | -0.16479 | 121.8658 | 121.8704 | 121.7743 | 121.8933
1030.6875 | 122.0764 | -121.7697 | 0.10071 | -0.0036622 | 0.07341 | 0.014825 | 0.031016 | -0.0012624 | -0.001474 | -0.00079691 | -0.0076599 | 0.0026447 | 0.020557 | -0.00090793 | 0.0011855 | 0.019666 | 0.0036337 | -0.022888 | 0.059509 | -0.022888 | 0.050354 | 0.19684 | 0.059509 | 0.068665 | 0.10986 | 0.064087 | -0.004578 | 0.10986 | 0.19226 | 0.11444 | 0.20142 | 121.7468 | -0.041199 | -0.050354 | 121.9666 | 121.8384 | 121.8292 | 0.091553 | 0.082397 | 121.7651 | -0.036621 | 0.009155 | 121.962 | 121.9711 | 121.8842 | 0.20599 | 0.11902 | 0.21973 | 0.073242 | 0.19684 | 0.11444 | 0.082397 | 0.068665 | 121.8292 | 121.8338 | -0.1236 | -0.10529 | 121.8201 | 121.8796 | 121.7468 | 121.8796
1032.4219 | 122.0169 | -121.7834 | 0.13275 | -0.02655 | 0.077041 | 0.01333 | 0.031657 | 0.00023275 | -0.002542 | -0.0018649 | -0.0076599 | 0.0028583 | 0.019275 | -0.011589 | -0.00095065 | 0.016248 | -0.0023477 | -0.050354 | 0.10071 | -0.059509 | -0.018311 | 0.10071 | 0.009155 | 0 | -0.022888 | 0.09613 | -0.045776 | 0.032043 | 0.11902 | 0.036621 | 0.15564 | 121.7239 | -0.032043 | -0.15106 | 121.8842 | 121.7834 | 121.7926 | 0.059509 | 0.068664 | 121.7377 | -0.036621 | -0.10071 | 121.9025 | 121.9391 | 121.8201 | 0.20142 | 0.082397 | 0.16022 | 0.041198 | 0.16479 | 0.077819 | 0.16022 | 0.14191 | 121.8842 | 121.8796 | -0.19226 | -0.17853 | 121.7651 | 121.8155 | 121.7331 | 121.7606
1034.1562 | 122.0123 | -121.7926 | 0.13275 | -0.02655 | 0.072982 | 0.01333 | 0.033793 | 0.0015146 | -0.0044646 | -0.0046421 | -0.0046081 | 0.0052081 | 0.018634 | -0.0066757 | -0.0030869 | 0.016675 | -0.0038431 | -0.064087 | 0.11444 | -0.059509 | -0.032043 | 0.10529 | 0.004578 | 0.009155 | 0 | 0.086975 | -0.045776 | 0.050354 | 0.11444 | 0.032043 | 0.16937 | 121.7331 | -0.01831 | -0.16479 | 121.8979 | 121.8018 | 121.7972 | 0.068664 | 0.064087 | 121.7468 | -0.045776 | -0.082397 | 121.907 | 121.962 | 121.8246 | 0.21515 | 0.077819 | 0.16479 | 0.027466 | 0.16022 | 0.09613 | 0.17395 | 0.13275 | 121.907 | 121.8796 | -0.19226 | -0.17853 | 121.7606 | 121.843 | 121.7285 | 121.7926
1035.9062 | 122.0306 | -121.7926 | 0.14191 | -0.011291 | 0.07405 | 0.012689 | 0.032725 | 1.915e-05 | -0.0027556 | -0.0020785 | -0.0015565 | 0.0039265 | 0.018421 | -0.0017623 | -0.0022325 | 0.017103 | -0.0059793 | -0.054932 | 0.10529 | -0.050354 | -0.027466 | 0.1236 | 0 | 0.013733 | 0.009155 | 0.10071 | -0.036621 | 0.045776 | 0.1236 | 0.050354 | 0.16022 | 121.7422 | -0.036621 | -0.16937 | 121.9162 | 121.8063 | 121.7926 | 0.064087 | 0.050354 | 121.756 | -0.041199 | -0.096131 | 121.9162 | 121.9528 | 121.843 | 0.19684 | 0.086975 | 0.17395 | 0.022888 | 0.16022 | 0.082397 | 0.15564 | 0.13733 | 121.8979 | 121.8933 | -0.19226 | -0.17853 | 121.7651 | 121.8384 | 121.7377 | 121.8018
1037.5781 | 122.0123 | -121.8109 | 0.14648 | -0.018921 | 0.07405 | 0.012689 | 0.031871 | 0.00087375 | -0.0019012 | 0.00027129 | -0.010712 | 0.0026447 | 0.019275 | -0.0094529 | -0.0035141 | 0.018812 | -0.0019205 | -0.086975 | 0.10529 | -0.059509 | -0.09613 | 0.054932 | -0.032043 | -0.004578 | -0.082397 | 0.09613 | -0.054932 | -0.004578 | 0.091553 | 0.022888 | 0.12817 | 121.7514 | -0.041198 | -0.24261 | 121.8658 | 121.8063 | 121.7789 | 0.054931 | 0.027466 | 121.756 | -0.050354 | -0.15106 | 121.9025 | 121.9391 | 121.8338 | 0.18311 | 0.07782 | 0.11444 | -0.036621 | 0.14649 | 0.050354 | 0.16479 | 0.15106 | 121.9162 | 121.907 | -0.20599 | -0.20142 | 121.7148 | 121.8063 | 121.7239 | 121.7285
1039.3125 | 121.962 | -121.7789 | 0.13275 | -0.0036622 | 0.076187 | 0.014398 | 0.033152 | 0.001301 | -0.0033966 | -0.00058311 | -0.0015565 | 0.0043537 | 0.02013 | -0.0062485 | -0.0011643 | 0.017957 | -0.0055521 | -0.045776 | 0.10529 | -0.054932 | -0.045776 | 0.09613 | -0.036621 | -0.022888 | -0.050354 | 0.1236 | -0.059509 | 0.009155 | 0.068665 | -0.022888 | 0.11444 | 121.7239 | -0.027465 | -0.17853 | 121.875 | 121.756 | 121.7422 | 0.032044 | 0.018311 | 121.7194 | -0.009155 | -0.1236 | 121.8475 | 121.8933 | 121.756 | 0.17395 | 0.036621 | 0.15106 | 0.009156 | 0.12817 | 0.068664 | 0.16022 | 0.1831 | 121.8842 | 121.9025 | -0.18768 | -0.19226 | 121.7331 | 121.788 | 121.7331 | 121.7285
1040.9844 | 121.962 | -121.8155 | 0.14191 | -0.0036622 | 0.075546 | 0.015466 | 0.031443 | 0.0021556 | -0.002542 | 5.7688e-05 | -0.0015565 | 0.0039265 | 0.020984 | -0.0064621 | -0.0013779 | 0.019025 | -0.0010659 | -0.086975 | 0.10986 | -0.050354 | -0.091553 | 0.022888 | -0.059509 | -0.032043 | -0.091553 | 0.10071 | -0.054932 | -0.004578 | 0.050354 | -0.036621 | 0.11444 | 121.7651 | -0.032044 | -0.23346 | 121.8384 | 121.7834 | 121.756 | 0.018311 | -0.009155 | 121.7606 | -0.041199 | -0.14649 | 121.8658 | 121.9299 | 121.7789 | 0.16937 | 0.018311 | 0.073242 | -0.041199 | 0.10529 | 0.050354 | 0.16022 | 0.15564 | 121.9254 | 121.9162 | -0.19226 | -0.19684 | 121.7239 | 121.8109 | 121.7285 | 121.7239
1042.7188 | 121.9894 | -121.8018 | 0.15106 | -0.03418 | 0.075973 | 0.012262 | 0.030589 | -0.0023306 | -0.0036102 | -0.0027195 | -0.0076599 | 0.0043537 | 0.019275 | -0.0015487 | -0.0058639 | 0.019239 | -0.0025613 | -0.07782 | 0.086975 | -0.068665 | -0.068665 | 0.045776 | -0.022888 | -0.013733 | -0.064087 | 0.10986 | -0.041199 | 0.009155 | 0.10071 | 0.018311 | 0.15564 | 121.7331 | -0.064087 | -0.21973 | 121.8475 | 121.788 | 121.7789 | 0.054932 | 0.045777 | 121.7606 | -0.041199 | -0.14191 | 121.9025 | 121.9574 | 121.8201 | 0.19684 | 0.05951 | 0.11444 | 0 | 0.14191 | 0.050354 | 0.15564 | 0.15106 | 121.8887 | 121.9116 | -0.21973 | -0.19226 | 121.7331 | 121.8109 | 121.7239 | 121.7377
1044.4688 | 122.0078 | -121.8018 | 0.15106 | -0.018921 | 0.072555 | 0.012903 | 0.030589 | -0.00062165 | -0.0023284 | -0.0012241 | -0.0046081 | 0.0030719 | 0.019489 | -0.0051803 | -0.0037277 | 0.017957 | -0.0032021 | -0.07782 | 0.10071 | -0.059509 | -0.064087 | 0.073242 | 0.009155 | 0.013733 | -0.036621 | 0.10071 | -0.036621 | 0.032043 | 0.1236 | 0.032043 | 0.15106 | 121.7422 | -0.050354 | -0.21515 | 121.875 | 121.8155 | 121.8109 | 0.073242 | 0.068664 | 121.7651 | -0.050354 | -0.11902 | 121.9254 | 121.9528 | 121.8338 | 0.18768 | 0.068664 | 0.13275 | -0.004578 | 0.16022 | 0.068664 | 0.16022 | 0.13733 | 121.9025 | 121.9025 | -0.21057 | -0.18768 | 121.7377 | 121.8338 | 121.7239 | 121.7651
1046.2188 | 122.0169 | -121.7972 | 0.1236 | -0.018921 | 0.075759 | 0.014825 | 0.032939 | -0.00083525 | -0.003183 | -0.00058311 | -0.0015565 | 0.0043537 | 0.01778 | -0.0024033 | -0.0013779 | 0.018812 | -0.0034159 | -0.041199 | 0.10529 | -0.050354 | -0.022888 | 0.1236 | 0.027466 | 0.022888 | 0.013733 | 0.10986 | -0.027466 | 0.050354 | 0.1236 | 0.045776 | 0.16022 | 121.7468 | -0.01831 | -0.14648 | 121.9208 | 121.8201 | 121.8246 | 0.073242 | 0.07782 | 121.7697 | -0.013733 | -0.073242 | 121.9208 | 121.9574 | 121.843 | 0.18768 | 0.073242 | 0.17395 | 0.027466 | 0.15106 | 0.07782 | 0.15564 | 0.13733 | 121.9025 | 121.907 | -0.17395 | -0.15106 | 121.7743 | 121.8475 | 121.756 | 121.8109
1047.9688 | 122.0993 | -121.7789 | 0.12817 | -0.0036622 | 0.073837 | 0.014612 | 0.029948 | -0.002117 | -0.0040374 | -0.0029331 | -0.0015565 | 0.0017901 | 0.019275 | -0.0045395 | -0.0026597 | 0.017957 | 0.00064307 | -0.027466 | 0.068665 | -0.018311 | 0.045776 | 0.21973 | 0.11902 | 0.11444 | 0.091553 | 0.073242 | -0.018311 | 0.11902 | 0.21973 | 0.15564 | 0.2243 | 121.7606 | -0.059509 | -0.082398 | 121.9986 | 121.8933 | 121.8979 | 0.13275 | 0.13733 | 121.7606 | -0.054932 | -0.009155 | 121.9986 | 122.0032 | 121.9345 | 0.24261 | 0.17395 | 0.23804 | 0.064087 | 0.23804 | 0.13733 | 0.086976 | 0.091553 | 121.8475 | 121.8521 | -0.14649 | -0.14649 | 121.8246 | 121.8979 | 121.7514 | 121.8704
1049.6562 | 121.9711 | -121.788 | 0.14648 | -0.011291 | 0.075118 | 0.014185 | 0.033152 | 1.915e-05 | -0.00040584 | -0.0020785 | -0.0046081 | 0.0043537 | 0.021412 | -0.0043259 | -0.00073705 | 0.01753 | -0.0044839 | -0.09613 | 0.10529 | -0.082397 | -0.082397 | 0.018311 | -0.07782 | -0.045776 | -0.073242 | 0.09613 | -0.050354 | 0 | 0.045776 | -0.027466 | 0.10986 | 121.7056 | -0.041198 | -0.22888 | 121.8063 | 121.7422 | 121.7102 | 0.036621 | 0.004577 | 121.7377 | -0.050354 | -0.14648 | 121.8338 | 121.8979 | 121.7606 | 0.16022 | 0.022888 | 0.10071 | 0 | 0.09613 | 0.050354 | 0.18768 | 0.14648 | 121.8933 | 121.8842 | -0.22888 | -0.19684 | 121.7056 | 121.788 | 121.6919 | 121.7148
1051.4062 | 121.9803 | -121.8018 | 0.13275 | -0.0036622 | 0.075546 | 0.017389 | 0.03422 | 0.00023275 | -0.002542 | 0.00027129 | -0.0046081 | 0.0032855 | 0.018634 | -0.0073165 | -0.0018051 | 0.020307 | -0.0032021 | -0.036621 | 0.10986 | -0.059509 | -0.045776 | 0.086975 | -0.036621 | -0.027466 | -0.032043 | 0.10529 | -0.036621 | 0.018311 | 0.086975 | 0.013733 | 0.1236 | 121.7422 | -0.022888 | -0.17853 | 121.8887 | 121.7743 | 121.7651 | 0.032043 | 0.022888 | 121.7651 | -0.027465 | -0.11444 | 121.8887 | 121.9254 | 121.8155 | 0.16022 | 0.050354 | 0.14648 | 0.013733 | 0.1236 | 0.054932 | 0.16937 | 0.14191 | 121.9116 | 121.907 | -0.19226 | -0.16937 | 121.756 | 121.8201 | 121.7651 | 121.7697
1053.1562 | 121.9711 | -121.8292 | 0.14648 | 0.0039673 | 0.075118 | 0.014612 | 0.033793 | 0.0021556 | -0.00083304 | 0.0011257 | -0.0015565 | 0.0026447 | 0.019489 | -0.0034713 | -0.00052345 | 0.020734 | -0.0029885 | -0.09613 | 0.11444 | -0.064087 | -0.091553 | 0.032043 | -0.068665 | -0.036621 | -0.091553 | 0.10986 | -0.073242 | -0.013733 | 0.041199 | -0.032043 | 0.11444 | 121.7651 | -0.032043 | -0.23804 | 121.8613 | 121.7926 | 121.7606 | 0.027466 | -0.004578 | 121.756 | -0.036621 | -0.16022 | 121.8704 | 121.9437 | 121.7972 | 0.18768 | 0.041199 | 0.09613 | -0.027466 | 0.11444 | 0.059509 | 0.17853 | 0.18311 | 121.9437 | 121.9391 | -0.21057 | -0.21973 | 121.7377 | 121.8155 | 121.7331 | 121.7377
1054.9062 | 122.0535 | -121.7606 | 0.1236 | -0.011291 | 0.074264 | 0.014398 | 0.030375 | -0.0036124 | -0.0036102 | -0.0033603 | -0.0076599 | 0.0034991 | 0.018848 | -0.0026169 | -0.0022325 | 0.018812 | 0.0036337 | -0.013733 | 0.064087 | -0.018311 | 0 | 0.20599 | 0.050354 | 0.068665 | 0.068665 | 0.064087 | -0.018311 | 0.091553 | 0.16022 | 0.091553 | 0.20599 | 121.7422 | -0.059509 | -0.1236 | 121.9666 | 121.8292 | 121.8109 | 0.086976 | 0.068665 | 121.7422 | -0.059509 | -0.032043 | 121.9208 | 121.9666 | 121.8521 | 0.22431 | 0.10986 | 0.22431 | 0.018311 | 0.17853 | 0.10986 | 0.082398 | 0.082398 | 121.8246 | 121.8246 | -0.14191 | -0.14191 | 121.7606 | 121.8521 | 121.7468 | 121.8292
1056.6406 | 122.0032 | -121.8201 | 0.13275 | -0.011291 | 0.077041 | 0.016107 | 0.034434 | 0.0034372 | -0.0016876 | -0.0040011 | -0.0015565 | 0.0032855 | 0.020557 | -0.0051803 | -0.0037277 | 0.01988 | -0.0025613 | -0.082397 | 0.1236 | -0.068665 | -0.07782 | 0.032043 | -0.073242 | -0.036621 | -0.059509 | 0.10986 | -0.059509 | 0.013733 | 0.054932 | -0.018311 | 0.12817 | 121.7514 | -0.009155 | -0.21057 | 121.8521 | 121.7834 | 121.7468 | 0.032044 | -0.004577 | 121.7606 | -0.022888 | -0.11902 | 121.875 | 121.9482 | 121.8018 | 0.18768 | 0.041198 | 0.10071 | -0.009155 | 0.11444 | 0.073242 | 0.19226 | 0.16937 | 121.9437 | 121.9299 | -0.20142 | -0.19226 | 121.7422 | 121.8338 | 121.7377 | 121.7606
1058.3438 | 121.9986 | -121.8063 | 0.14648 | -0.011291 | 0.075973 | 0.013757 | 0.03123 | 0.00087375 | -0.0027556 | -0.0025057 | -0.0046081 | 0.0047809 | 0.019916 | -0.0073165 | -0.0041551 | 0.019025 | -0.0040567 | -0.036621 | 0.10529 | -0.054932 | -0.013733 | 0.10529 | 0.004578 | 0.009155 | 0.009155 | 0.10071 | -0.050354 | 0.013733 | 0.086975 | 0.004578 | 0.14191 | 121.7514 | -0.041198 | -0.16022 | 121.9116 | 121.8155 | 121.8109 | 0.064087 | 0.05951 | 121.756 | -0.045776 | -0.13275 | 121.8933 | 121.9482 | 121.8109 | 0.19226 | 0.054932 | 0.16022 | 0.041199 | 0.13733 | 0.064087 | 0.16022 | 0.15106 | 121.9116 | 121.907 | -0.20142 | -0.19684 | 121.7926 | 121.8201 | 121.7697 | 121.8155
1060.0781 | 122.0993 | -121.7606 | 0.10986 | -0.011291 | 0.075546 | 0.01568 | 0.031443 | 0.0032236 | -0.0027556 | 0.00069849 | -0.0046081 | 0.0034991 | 0.018634 | -0.0058213 | 0.00011755 | 0.01988 | -0.00063873 | -0.018311 | 0.068665 | -0.022888 | 0.027466 | 0.17853 | 0.054932 | 0.073242 | 0.082397 | 0.07782 | -0.018311 | 0.13733 | 0.17853 | 0.1236 | 0.22888 | 121.7377 | -0.041198 | -0.082397 | 121.9391 | 121.8338 | 121.8155 | 0.09613 | 0.07782 | 121.7422 | -0.032043 | 0.027466 | 121.9391 | 121.9894 | 121.8842 | 0.24719 | 0.14191 | 0.20142 | 0.050354 | 0.19684 | 0.15564 | 0.091553 | 0.096131 | 121.8292 | 121.8384 | -0.13275 | -0.12817 | 121.788 | 121.8979 | 121.7422 | 121.843
1061.8281 | 122.0673 | -121.7468 | 0.11902 | -0.018921 | 0.073196 | 0.013971 | 0.028239 | 0.0019418 | -0.0021148 | -0.00079691 | -0.010712 | 0.0015765 | 0.02013 | 0.00037387 | -0.0024461 | 0.018812 | -0.0023477 | -0.009155 | 0.054932 | -0.013733 | 0.027466 | 0.1831 | 0.045776 | 0.07782 | 0.091553 | 0.064087 | -0.022888 | 0.10071 | 0.16022 | 0.10529 | 0.20142 | 121.7331 | -0.064087 | -0.091553 | 121.9299 | 121.8246 | 121.7926 | 0.091553 | 0.059509 | 121.7239 | -0.054932 | -0.018311 | 121.907 | 121.9482 | 121.8521 | 0.2243 | 0.12817 | 0.19684 | 0.041199 | 0.1831 | 0.1236 | 0.068665 | 0.086975 | 121.8018 | 121.8109 | -0.13275 | -0.14191 | 121.7743 | 121.8475 | 121.7377 | 121.8384
1063.5156 | 121.9666 | -121.8063 | 0.13733 | -0.011291 | 0.076827 | 0.016962 | 0.032511 | -0.00083525 | -0.0023284 | -0.00079691 | -0.0046081 | 0.0028583 | 0.020771 | -0.0047531 | -0.0039413 | 0.019452 | -0.0010659 | -0.07782 | 0.10071 | -0.059509 | -0.091553 | 0.022888 | -0.068665 | -0.027466 | -0.041199 | 0.1236 | -0.07782 | -0.013733 | 0.036621 | -0.022888 | 0.13733 | 121.7468 | -0.036621 | -0.22888 | 121.8292 | 121.7789 | 121.7377 | 0.032043 | -0.009156 | 121.7285 | -0.013733 | -0.15106 | 121.843 | 121.9437 | 121.7834 | 0.21515 | 0.054932 | 0.082397 | -0.032044 | 0.11444 | 0.064087 | 0.16022 | 0.20142 | 121.907 | 121.9299 | -0.19684 | -0.21515 | 121.7148 | 121.7926 | 121.7285 | 121.7651
1065.25 | 122.1176 | -121.756 | 0.10986 | 0.0039673 | 0.072982 | 0.013544 | 0.029521 | 0.00023275 | -0.0023284 | -0.0027195 | -0.0046081 | 0.0032855 | 0.018634 | 0.0012283 | -0.0035141 | 0.019239 | -0.0010659 | -0.018311 | 0.082397 | -0.045776 | 0.050354 | 0.21515 | 0.10071 | 0.12817 | 0.11902 | 0.059509 | -0.027466 | 0.13275 | 0.21515 | 0.16479 | 0.23346 | 121.7102 | -0.027466 | -0.059509 | 121.9711 | 121.8842 | 121.8567 | 0.17395 | 0.14648 | 121.7285 | -0.050354 | 0.022888 | 121.9711 | 121.9894 | 121.9208 | 0.26093 | 0.19226 | 0.26093 | 0.09613 | 0.24261 | 0.16022 | 0.12817 | 0.086975 | 121.8384 | 121.8155 | -0.15564 | -0.13733 | 121.8063 | 121.8887 | 121.7377 | 121.875
1066.9844 | 121.9803 | -121.788 | 0.14191 | 0.0039673 | 0.077255 | 0.014825 | 0.031657 | 0.00087375 | -0.00061944 | -0.0016513 | -0.0046081 | 0.0034991 | 0.019916 | -0.0041123 | -0.0024461 | 0.019239 | -0.0032021 | -0.082397 | 0.13275 | -0.068665 | -0.086975 | 0.022888 | -0.07782 | -0.045776 | -0.082397 | 0.09613 | -0.054932 | 0 | 0.018311 | -0.036621 | 0.11902 | 121.7194 | -0.009156 | -0.22888 | 121.8109 | 121.7422 | 121.7102 | 0.022889 | -0.009155 | 121.7331 | -0.045777 | -0.14191 | 121.8063 | 121.907 | 121.7514 | 0.17395 | 0.018311 | 0.091553 | -0.01831 | 0.073243 | 0.054932 | 0.20142 | 0.15106 | 121.9208 | 121.8842 | -0.21057 | -0.19684 | 121.7011 | 121.788 | 121.7056 | 121.7056
1068.6719 | 121.9894 | -121.8246 | 0.13733 | -0.0036622 | 0.074905 | 0.013116 | 0.032298 | -0.0012624 | -0.0010468 | -0.0016513 | -0.010712 | 0.0034991 | 0.017994 | -0.0041123 | -0.0052231 | 0.015821 | -0.00042513 | -0.09613 | 0.10986 | -0.064087 | -0.086975 | 0.045776 | -0.032043 | -0.027466 | -0.086975 | 0.11902 | -0.045776 | -0.032043 | 0.059509 | -0.009155 | 0.09613 | 121.7606 | -0.027466 | -0.2243 | 121.8704 | 121.7972 | 121.7926 | 0.036621 | 0.032044 | 121.7789 | -0.01831 | -0.16937 | 121.8842 | 121.9208 | 121.8155 | 0.14191 | 0.036621 | 0.10986 | -0.022888 | 0.10528 | 0.013733 | 0.17395 | 0.16479 | 121.9345 | 121.9437 | -0.20142 | -0.18311 | 121.7377 | 121.7926 | 121.7285 | 121.7377
1070.4219 | 122.0444 | -121.8063 | 0.1236 | -0.018921 | 0.072769 | 0.014825 | 0.029521 | -0.0027578 | -0.0033966 | 0.00091209 | -0.0046081 | 0.0017901 | 0.019275 | -0.0047531 | -0.0028733 | 0.01753 | -0.0025613 | -0.064087 | 0.09613 | -0.059509 | -0.059509 | 0.082397 | 0.009155 | 0.009155 | -0.018311 | 0.091553 | -0.045776 | 0.041199 | 0.11444 | 0.050354 | 0.14191 | 121.7468 | -0.027466 | -0.1831 | 121.8887 | 121.8155 | 121.8155 | 0.068664 | 0.068664 | 121.7606 | -0.032043 | -0.082397 | 121.9208 | 121.9482 | 121.8567 | 0.18768 | 0.09613 | 0.14191 | 0 | 0.16022 | 0.086975 | 0.15564 | 0.13733 | 121.9025 | 121.8979 | -0.1831 | -0.16937 | 121.7468 | 121.8475 | 121.7422 | 121.788
1072.1562 | 122.0764 | -121.7972 | 0.12817 | -0.011291 | 0.075118 | 0.013116 | 0.027812 | -0.0027578 | -0.0033966 | -0.0025057 | 0.0014953 | 0.0020039 | 0.017566 | -0.0092391 | -0.0039413 | 0.017957 | -0.00085233 | -0.009155 | 0.059509 | -0.036621 | 0.045776 | 0.21057 | 0.10071 | 0.10986 | 0.082397 | 0.073242 | -0.032043 | 0.086975 | 0.20142 | 0.12817 | 0.19684 | 121.7606 | -0.068665 | -0.082398 | 122.0078 | 121.907 | 121.8979 | 0.14648 | 0.13733 | 121.7651 | -0.054932 | -0.041199 | 121.9986 | 121.994 | 121.9254 | 0.22888 | 0.16022 | 0.24719 | 0.082397 | 0.23346 | 0.11902 | 0.09613 | 0.10529 | 121.8567 | 121.8704 | -0.1648 | -0.16022 | 121.843 | 121.8842 | 121.788 | 121.8796
1073.9219 | 122.0718 | -121.7651 | 0.10986 | -0.018921 | 0.073837 | 0.013971 | 0.029948 | 0.001301 | -0.0016876 | -0.0035739 | -0.0076599 | -0.00034614 | 0.018421 | -0.0088119 | -0.00095065 | 0.016675 | -0.0023477 | -0.032043 | 0.059509 | 0 | 0.041199 | 0.19226 | 0.032043 | 0.073242 | 0.082397 | 0.050354 | -0.013733 | 0.09613 | 0.15564 | 0.10986 | 0.17853 | 121.7651 | -0.050354 | -0.068664 | 121.9574 | 121.8384 | 121.7972 | 0.073242 | 0.032043 | 121.7514 | -0.059509 | -0.013733 | 121.9208 | 121.9437 | 121.875 | 0.19226 | 0.1236 | 0.19226 | 0.041199 | 0.16937 | 0.10986 | 0.059509 | 0.064087 | 121.8246 | 121.8155 | -0.10986 | -0.1236 | 121.8063 | 121.8613 | 121.7331 | 121.8475
1075.6562 | 122.0993 | -121.7651 | 0.11902 | -0.02655 | 0.074478 | 0.015894 | 0.030802 | 0.0010874 | -0.0036102 | -0.0050693 | -0.0076599 | 0.0030719 | 0.017566 | -0.0036849 | 0.00011755 | 0.017957 | -0.0027749 | 0 | 0.054932 | -0.013733 | 0.050354 | 0.1831 | 0.064087 | 0.07782 | 0.10071 | 0.054932 | 0 | 0.11902 | 0.18768 | 0.1236 | 0.21515 | 121.7514 | -0.064087 | -0.068665 | 121.9482 | 121.843 | 121.8292 | 0.091553 | 0.07782 | 121.7651 | -0.064087 | 0 | 121.9528 | 121.9803 | 121.8887 | 0.21515 | 0.1236 | 0.19684 | 0.064087 | 0.18768 | 0.11902 | 0.068665 | 0.054932 | 121.8201 | 121.8201 | -0.13275 | -0.11902 | 121.8155 | 121.8842 | 121.7651 | 121.8658
1077.3281 | 122.0764 | -121.7606 | 0.10529 | -0.018921 | 0.072982 | 0.014185 | 0.029734 | -0.00040805 | -0.003183 | -0.0020785 | 0.0014953 | 0.0026447 | 0.018634 | -0.0053939 | -0.0018051 | 0.017316 | -0.0017069 | -0.064087 | 0.07782 | -0.036621 | -0.009155 | 0.13733 | 0.032043 | 0.050354 | 0.045776 | 0.07782 | -0.041199 | 0.068665 | 0.16022 | 0.091553 | 0.19684 | 121.7239 | -0.027466 | -0.11444 | 121.8979 | 121.8109 | 121.7926 | 0.086975 | 0.068664 | 121.7194 | -0.027466 | -0.036621 | 121.9208 | 121.9574 | 121.8521 | 0.23804 | 0.13275 | 0.17395 | 0.027466 | 0.20142 | 0.10986 | 0.11444 | 0.11902 | 121.8384 | 121.8384 | -0.14191 | -0.14649 | 121.7514 | 121.8292 | 121.6965 | 121.8063
1079.0625 | 121.9849 | -121.8292 | 0.15106 | -0.011291 | 0.073623 | 0.013544 | 0.031871 | -0.0036124 | -0.003183 | -0.0027195 | -0.0015565 | 0.0034991 | 0.021625 | -0.0058213 | -0.0035141 | 0.016889 | -0.0012795 | -0.064087 | 0.10529 | -0.050354 | -0.064087 | 0.064087 | -0.009155 | 0.004578 | -0.036621 | 0.1236 | -0.068665 | -0.027466 | 0.068665 | 0.009155 | 0.09613 | 121.7789 | -0.045776 | -0.21515 | 121.8933 | 121.8338 | 121.8201 | 0.054932 | 0.041199 | 121.7606 | -0.027466 | -0.17853 | 121.8979 | 121.9254 | 121.8384 | 0.16479 | 0.07782 | 0.11444 | -0.013733 | 0.13733 | 0.041199 | 0.15564 | 0.19226 | 121.9345 | 121.9528 | -0.20142 | -0.21973 | 121.7651 | 121.8018 | 121.7651 | 121.7926
1080.7969 | 122.0993 | -121.7468 | 0.1236 | 0.0039673 | 0.072555 | 0.013544 | 0.02888 | -0.002117 | -0.0021148 | 0.00048489 | -0.0046081 | 0.0034991 | 0.018634 | -0.0015487 | -0.0037277 | 0.018812 | 0.0010703 | -0.022888 | 0.07782 | -0.036621 | 0.059509 | 0.21515 | 0.10529 | 0.11444 | 0.082397 | 0.068665 | -0.022888 | 0.10071 | 0.19684 | 0.14648 | 0.21057 | 121.7102 | -0.045776 | -0.064087 | 121.962 | 121.8613 | 121.8521 | 0.15106 | 0.14191 | 121.7239 | -0.054931 | -0.022888 | 121.9437 | 121.9574 | 121.8933 | 0.23346 | 0.16937 | 0.25177 | 0.09613 | 0.21973 | 0.1236 | 0.11444 | 0.091553 | 121.8246 | 121.8155 | -0.16022 | -0.14648 | 121.8063 | 121.8475 | 121.7239 | 121.8292
1082.4688 | 122.113 | -121.7926 | 0.12817 | -0.011291 | 0.07341 | 0.013757 | 0.028666 | -0.0044668 | -0.0036102 | -0.0037875 | -0.0046081 | 0.0015765 | 0.019062 | -5.3326e-05 | -0.0020187 | 0.01753 | 2.068e-06 | -0.050354 | 0.073242 | -0.027466 | 0.032043 | 0.17395 | 0.07782 | 0.10529 | 0.059509 | 0.073242 | -0.027466 | 0.086975 | 0.21057 | 0.13733 | 0.21973 | 121.7651 | -0.054932 | -0.096131 | 121.9666 | 121.8979 | 121.8704 | 0.13275 | 0.10529 | 121.7651 | -0.054932 | -0.041199 | 122.0032 | 122.0123 | 121.9299 | 0.24719 | 0.16479 | 0.20142 | 0.059509 | 0.23804 | 0.11444 | 0.10071 | 0.10071 | 121.8658 | 121.8658 | -0.15564 | -0.15564 | 121.8246 | 121.8796 | 121.7422 | 121.8521
1084.2188 | 121.994 | -121.8292 | 0.14648 | -0.0036622 | 0.074478 | 0.013757 | 0.032298 | 0.0010874 | -0.0021148 | -0.0033603 | 0.0014953 | 0.0049945 | 0.020343 | -0.011162 | -0.00030965 | 0.019666 | -0.00085233 | -0.059509 | 0.10986 | -0.073242 | -0.09613 | 0.022888 | -0.082397 | -0.027466 | -0.059509 | 0.11444 | -0.059509 | 0 | 0.045776 | -0.032043 | 0.10986 | 121.756 | -0.036621 | -0.24261 | 121.8521 | 121.8018 | 121.7468 | 0.045776 | -0.009155 | 121.7697 | -0.032043 | -0.14648 | 121.875 | 121.9391 | 121.7972 | 0.16937 | 0.027466 | 0.09613 | -0.022888 | 0.10528 | 0.059509 | 0.18311 | 0.17395 | 121.9391 | 121.9437 | -0.21973 | -0.20599 | 121.7331 | 121.8292 | 121.7697 | 121.7697
1085.9531 | 121.9757 | -121.7926 | 0.13733 | -0.0036622 | 0.072982 | 0.013116 | 0.031443 | -0.00083525 | -0.0036102 | -0.0016513 | -0.0046081 | 0.0049945 | 0.019062 | -0.0088119 | -0.0020187 | 0.017743 | -0.0023477 | -0.054932 | 0.10071 | -0.073242 | -0.041199 | 0.07782 | -0.032043 | -0.013733 | -0.041199 | 0.10529 | -0.054932 | -0.009155 | 0.059509 | -0.027466 | 0.09613 | 121.7194 | -0.036621 | -0.17853 | 121.8704 | 121.7789 | 121.7606 | 0.059509 | 0.041199 | 121.7377 | -0.032043 | -0.14648 | 121.8521 | 121.8887 | 121.7651 | 0.15106 | 0.027466 | 0.15106 | 0.032043 | 0.11444 | 0.045777 | 0.17395 | 0.16022 | 121.8933 | 121.8979 | -0.21057 | -0.19226 | 121.7514 | 121.7834 | 121.7377 | 121.7514
1087.625 | 122.0352 | -121.8063 | 0.13733 | -0.02655 | 0.073196 | 0.013544 | 0.029948 | -0.0010488 | -0.0038238 | -0.0035739 | -0.0076599 | 0.0041401 | 0.017994 | -0.0071029 | -0.00095065 | 0.017957 | -0.0049111 | -0.045776 | 0.10986 | -0.041199 | -0.022888 | 0.09613 | 0.009155 | 0.022888 | -0.009155 | 0.091553 | -0.041199 | 0.027466 | 0.1236 | 0.032043 | 0.16937 | 121.7651 | -0.027466 | -0.16022 | 121.9025 | 121.8292 | 121.8155 | 0.064087 | 0.050354 | 121.7651 | -0.045776 | -0.10986 | 121.9299 | 121.9757 | 121.8384 | 0.21057 | 0.073242 | 0.13733 | 0.018311 | 0.16479 | 0.068665 | 0.15106 | 0.13275 | 121.9162 | 121.8979 | -0.17853 | -0.17853 | 121.7834 | 121.8338 | 121.7606 | 121.7972
1089.375 | 122.0993 | -121.7926 | 0.10071 | -0.011291 | 0.073196 | 0.014825 | 0.028239 | 0.00087375 | -0.0012604 | -0.0027195 | -0.0046081 | 0.00050846 | 0.019916 | -0.0045395 | -0.0022325 | 0.019025 | -0.0012795 | -0.059509 | 0.068665 | -0.032043 | 0.009155 | 0.14648 | 0.059509 | 0.068665 | 0.054932 | 0.073242 | -0.050354 | 0.07782 | 0.19684 | 0.11902 | 0.20599 | 121.7606 | -0.032043 | -0.091553 | 121.9391 | 121.8613 | 121.8521 | 0.10071 | 0.091552 | 121.7422 | -0.027466 | -0.022888 | 121.9894 | 121.9986 | 121.9116 | 0.25635 | 0.16937 | 0.17853 | 0.041198 | 0.24719 | 0.12817 | 0.10071 | 0.1236 | 121.8613 | 121.8658 | -0.13275 | -0.15106 | 121.8018 | 121.8704 | 121.7331 | 121.8475
1091.1094 | 122.0444 | -121.8155 | 0.13275 | -0.018921 | 0.071914 | 0.011408 | 0.028025 | 0.001301 | -0.002542 | -0.0040011 | -0.0046081 | 0.00093566 | 0.019703 | -0.010521 | -0.0020187 | 0.018598 | 0.00064307 | -0.059509 | 0.082397 | -0.032043 | 0 | 0.1236 | 0.027466 | 0.032043 | 0.013733 | 0.068665 | -0.041199 | 0.045776 | 0.12817 | 0.059509 | 0.16937 | 121.7834 | -0.050354 | -0.13275 | 121.9391 | 121.8475 | 121.843 | 0.064086 | 0.059509 | 121.7743 | -0.064086 | -0.086975 | 121.9437 | 121.9849 | 121.875 | 0.21057 | 0.10071 | 0.15564 | 0.032043 | 0.16937 | 0.086975 | 0.11444 | 0.10986 | 121.8979 | 121.8842 | -0.16479 | -0.17395 | 121.8155 | 121.8613 | 121.756 | 121.8292
1092.8594 | 122.0718 | -121.8109 | 0.11902 | -0.011291 | 0.071487 | 0.013544 | 0.027812 | -0.0029714 | -0.0021148 | -0.0029331 | -0.0015565 | 0.00050846 | 0.019275 | -0.0066757 | -0.0015915 | 0.020521 | 0.0023521 | -0.059509 | 0.091553 | -0.022888 | -0.022888 | 0.11444 | 0.004578 | 0.036621 | 0 | 0.082397 | -0.041199 | 0.041199 | 0.14191 | 0.064087 | 0.17395 | 121.788 | -0.027466 | -0.14191 | 121.9254 | 121.8475 | 121.8155 | 0.059509 | 0.027466 | 121.7697 | -0.036622 | -0.07782 | 121.9528 | 121.9849 | 121.875 | 0.21515 | 0.10529 | 0.13733 | 0 | 0.18311 | 0.082398 | 0.11444 | 0.1236 | 121.9025 | 121.8933 | -0.14191 | -0.16022 | 121.788 | 121.8521 | 121.7514 | 121.8109
1094.5469 | 121.9894 | -121.8155 | 0.11444 | -0.018921 | 0.075332 | 0.01568 | 0.030589 | 0.0053598 | -0.003183 | 5.7688e-05 | -0.0046081 | 0.0060627 | 0.018634 | -0.010094 | -0.0024461 | 0.017316 | -0.0032021 | -0.036621 | 0.10071 | -0.059509 | -0.009155 | 0.11444 | -0.004578 | 0.022888 | 0.013733 | 0.10071 | -0.045776 | 0.045776 | 0.12817 | 0.041199 | 0.15564 | 121.756 | -0.013733 | -0.1236 | 121.9299 | 121.8384 | 121.8109 | 0.082397 | 0.054931 | 121.7697 | -0.013733 | -0.068665 | 121.9437 | 121.9711 | 121.8567 | 0.20142 | 0.086975 | 0.17395 | 0.050354 | 0.17395 | 0.091552 | 0.16022 | 0.14648 | 121.9162 | 121.9162 | -0.17395 | -0.16022 | 121.8063 | 121.8613 | 121.7789 | 121.8292
1096.2812 | 122.0123 | -121.8292 | 0.1236 | 0.0039673 | 0.071701 | 0.014398 | 0.030162 | -0.0010488 | -0.0023284 | -0.00015591 | -0.0046081 | 0.0024311 | 0.019916 | -0.0085983 | -0.0041551 | 0.018384 | -0.0038431 | -0.032043 | 0.068665 | -0.041199 | 0.022888 | 0.16479 | 0.073242 | 0.073242 | 0.032043 | 0.09613 | -0.041199 | 0.032043 | 0.14191 | 0.054932 | 0.15106 | 121.788 | -0.054931 | -0.10071 | 121.994 | 121.9025 | 121.9025 | 0.11444 | 0.11444 | 121.788 | -0.027466 | -0.091553 | 121.9711 | 121.9803 | 121.8842 | 0.19226 | 0.096131 | 0.20599 | 0.064087 | 0.18311 | 0.073242 | 0.10986 | 0.13733 | 121.8979 | 121.9254 | -0.16479 | -0.16479 | 121.8521 | 121.8613 | 121.7972 | 121.8613
1098.0156 | 122.081 | -121.8201 | 0.11902 | -0.0036622 | 0.073623 | 0.013116 | 0.026957 | -0.0010488 | -0.003183 | -0.0020785 | -0.0046081 | 0.0015765 | 0.019275 | 0.0020829 | -0.0033005 | 0.017743 | -0.0021341 | -0.027466 | 0.073242 | -0.027466 | 0.054932 | 0.19226 | 0.09613 | 0.10529 | 0.086975 | 0.068665 | -0.032043 | 0.10529 | 0.19226 | 0.1236 | 0.21515 | 121.7926 | -0.045777 | -0.064087 | 122.0123 | 121.9254 | 121.9162 | 0.13275 | 0.1236 | 121.788 | -0.050354 | -0.013733 | 122.0123 | 122.0352 | 121.9437 | 0.24719 | 0.15564 | 0.21973 | 0.082398 | 0.2243 | 0.13733 | 0.10071 | 0.10071 | 121.8933 | 121.8887 | -0.14649 | -0.15106 | 121.875 | 121.9254 | 121.7926 | 121.907
1099.75 | 121.9711 | -121.8384 | 0.15106 | -0.011291 | 0.072341 | 0.013757 | 0.028453 | -0.0019034 | -0.0023284 | 0.0017667 | -0.0076599 | 0.0017901 | 0.019062 | -0.0038987 | -0.0050095 | 0.017957 | -0.0049111 | -0.10071 | 0.1236 | -0.07782 | -0.086975 | 0.059509 | -0.036621 | -0.018311 | -0.091553 | 0.10529 | -0.054932 | -0.041199 | 0.054932 | 0.004578 | 0.09613 | 121.7606 | -0.027466 | -0.23804 | 121.8979 | 121.8201 | 121.8018 | 0.059509 | 0.041199 | 121.7834 | -0.045776 | -0.19226 | 121.8933 | 121.9345 | 121.843 | 0.15106 | 0.05951 | 0.13733 | -0.009155 | 0.10986 | 0.013733 | 0.20142 | 0.16022 | 121.962 | 121.9437 | -0.22888 | -0.20599 | 121.7514 | 121.7972 | 121.7377 | 121.7468
1101.5 | 121.7239 | -121.5134 | 0.13733 | 0.0039673 | 0.071273 | 0.014612 | 0.032084 | 0.0021556 | -0.004892 | 0.00069849 | -0.0046081 | 0.0034991 | 0.016712 | -0.0081711 | 0.00097195 | 0.017957 | -0.0023477 | -0.082397 | 0.10986 | -0.073242 | -0.073242 | 0.050354 | -0.073242 | -0.032043 | -0.045776 | 0.091553 | -0.068665 | 0.036621 | 0.082397 | 0.004578 | 0.14648 | 121.4401 | -0.027466 | -0.21057 | 121.5637 | 121.4813 | 121.4401 | 0.041199 | 0 | 121.4447 | -0.045776 | -0.10071 | 121.5958 | 121.6599 | 121.5179 | 0.21515 | 0.073243 | 0.1236 | 0 | 0.15106 | 0.10529 | 0.18311 | 0.16022 | 121.6232 | 121.6049 | -0.21057 | -0.20599 | 121.4401 | 121.55 | 121.431 | 121.4676
1103.1719 | 121.9208 | -121.5912 | 0.09613 | -0.0036622 | 0.073837 | 0.01568 | 0.030162 | -0.00040805 | -0.0029694 | -0.0012241 | -0.0076599 | 0.0020039 | 0.019062 | -0.010735 | 0.00054475 | 0.019239 | 0.0023521 | -0.036621 | 0.082397 | -0.054932 | 0.013733 | 0.16022 | 0.027466 | 0.064087 | 0.073242 | 0.064087 | -0.027466 | 0.11444 | 0.19226 | 0.10986 | 0.21515 | 121.5363 | -0.013733 | -0.082397 | 121.7514 | 121.6553 | 121.6187 | 0.11902 | 0.082398 | 121.5637 | -0.032043 | 0.018311 | 121.7834 | 121.8063 | 121.7011 | 0.24261 | 0.13733 | 0.21515 | 0.068665 | 0.21973 | 0.14191 | 0.13733 | 0.091553 | 121.6736 | 121.6553 | -0.15106 | -0.1236 | 121.6049 | 121.7056 | 121.5546 | 121.6644
1104.9375 | 121.8842 | -121.6827 | 0.13733 | -0.011291 | 0.07405 | 0.014398 | 0.029521 | 0.00044655 | -0.001474 | 0.0015531 | -0.0015565 | 0.0047809 | 0.018421 | -0.012657 | -9.605e-05 | 0.020307 | -0.0038431 | -0.032043 | 0.082397 | -0.059509 | -0.036621 | 0.11902 | -0.004578 | 0.018311 | 0 | 0.086975 | -0.041199 | 0.050354 | 0.11444 | 0.045776 | 0.15564 | 121.6232 | -0.054932 | -0.17395 | 121.8018 | 121.701 | 121.6782 | 0.07782 | 0.054931 | 121.6415 | -0.050354 | -0.086975 | 121.7972 | 121.8384 | 121.7285 | 0.19684 | 0.086975 | 0.17853 | 0.022888 | 0.15564 | 0.091553 | 0.14191 | 0.12817 | 121.7651 | 121.7697 | -0.19684 | -0.17853 | 121.6461 | 121.7331 | 121.6507 | 121.6827
1106.6719 | 121.8475 | -121.7102 | 0.13275 | 0.011597 | 0.077255 | 0.014612 | 0.032725 | 0.00044655 | 0.00087596 | -0.0020785 | 0.0014953 | 0.0032855 | 0.019489 | -0.0066757 | -0.0011643 | 0.01753 | 0.00085667 | -0.054932 | 0.11444 | -0.054932 | -0.054932 | 0.068665 | -0.045776 | -0.022888 | -0.054932 | 0.09613 | -0.045776 | 0 | 0.059509 | -0.013733 | 0.09613 | 121.6553 | -0.01831 | -0.18768 | 121.7789 | 121.6873 | 121.6644 | 0.032044 | 0.009156 | 121.6644 | -0.036621 | -0.13275 | 121.7697 | 121.8063 | 121.6965 | 0.14191 | 0.032043 | 0.1236 | 0 | 0.10528 | 0.045776 | 0.16937 | 0.14191 | 121.8246 | 121.8063 | -0.18768 | -0.17853 | 121.6553 | 121.7102 | 121.6553 | 121.6553
1108.3438 | 121.8704 | -121.6736 | 0.13733 | -0.0036622 | 0.074691 | 0.014825 | 0.031016 | 1.915e-05 | -0.00019224 | 0.00048489 | -0.0046081 | 0.0047809 | 0.019489 | -0.0051803 | -0.0018051 | 0.018598 | -0.0012795 | -0.041199 | 0.091553 | -0.041199 | -0.045776 | 0.10529 | -0.027466 | -0.009155 | -0.013733 | 0.091553 | -0.054932 | 0.013733 | 0.091553 | -0.009155 | 0.12817 | 121.6324 | -0.045776 | -0.18311 | 121.7789 | 121.6644 | 121.6461 | 0.032044 | 0.013733 | 121.6187 | -0.045776 | -0.1236 | 121.7651 | 121.8018 | 121.6644 | 0.18311 | 0.045777 | 0.14649 | -0.004577 | 0.14649 | 0.068665 | 0.13275 | 0.14649 | 121.7651 | 121.7651 | -0.17853 | -0.19226 | 121.6278 | 121.6873 | 121.6324 | 121.6599
1110.0938 | 121.9437 | -121.6736 | 0.13275 | -0.0036622 | 0.074905 | 0.014825 | 0.029307 | -0.0029714 | -0.0040374 | -0.0027195 | -0.0046081 | 0.0017901 | 0.019275 | -0.0026169 | -0.0018051 | 0.017743 | -0.0010659 | -0.059509 | 0.086975 | -0.022888 | -0.036621 | 0.11902 | 0.004578 | 0.032043 | -0.009155 | 0.073242 | -0.027466 | 0.041199 | 0.13275 | 0.064087 | 0.16022 | 121.6507 | -0.045776 | -0.16937 | 121.7926 | 121.7056 | 121.6782 | 0.054931 | 0.027466 | 121.6461 | -0.059509 | -0.091552 | 121.8063 | 121.8338 | 121.7377 | 0.18768 | 0.091553 | 0.14191 | -0.013733 | 0.16022 | 0.068665 | 0.10986 | 0.10071 | 121.7606 | 121.7468 | -0.15564 | -0.16022 | 121.637 | 121.7148 | 121.6141 | 121.6644
1111.8281 | 122.0169 | -121.6507 | 0.09613 | 0.0039673 | 0.07405 | 0.014185 | 0.029948 | -0.00062165 | -0.0033966 | -0.0022921 | -0.0076599 | 0.0015765 | 0.019062 | 0.0048599 | -0.0043687 | 0.018598 | -0.0012795 | -0.009155 | 0.07782 | -0.018311 | 0.059509 | 0.24261 | 0.11444 | 0.10529 | 0.11902 | 0.059509 | -0.036621 | 0.10529 | 0.23346 | 0.15106 | 0.21515 | 121.6324 | -0.01831 | -0.036621 | 121.8933 | 121.756 | 121.7651 | 0.1236 | 0.13275 | 121.6141 | -0.036621 | 0.009156 | 121.8842 | 121.8658 | 121.8018 | 0.25177 | 0.18768 | 0.26093 | 0.07782 | 0.27008 | 0.14191 | 0.096131 | 0.09613 | 121.7285 | 121.7102 | -0.11444 | -0.13275 | 121.7102 | 121.756 | 121.6415 | 121.7697
1113.5156 | 121.875 | -121.7102 | 0.13733 | -0.011291 | 0.076187 | 0.015039 | 0.033366 | -0.0019034 | -0.0019012 | -0.0048557 | -0.0015565 | 0.0026447 | 0.02013 | -0.0030441 | 0.00075835 | 0.020734 | -0.0010659 | -0.086975 | 0.10986 | -0.082397 | -0.07782 | 0.027466 | -0.082397 | -0.036621 | -0.068665 | 0.1236 | -0.068665 | -0.013733 | 0.041199 | -0.045776 | 0.10071 | 121.6278 | -0.027466 | -0.21515 | 121.7377 | 121.6736 | 121.6278 | 0.045776 | 0 | 121.6415 | -0.013733 | -0.15106 | 121.7514 | 121.8109 | 121.6644 | 0.16937 | 0.022889 | 0.10986 | 0.004577 | 0.10986 | 0.054932 | 0.19226 | 0.19226 | 121.8201 | 121.8338 | -0.21973 | -0.20599 | 121.6324 | 121.6965 | 121.6232 | 121.6415
1115.2656 | 122.0261 | -121.6553 | 0.10986 | 0.0039673 | 0.073196 | 0.015253 | 0.03123 | 0.0010874 | -0.0029694 | -0.0014377 | -0.0015565 | 0.0024311 | 0.02013 | -0.0028305 | -0.0030869 | 0.017957 | 0.00021567 | -0.022888 | 0.07782 | -0.041199 | 0.041199 | 0.20599 | 0.091553 | 0.10071 | 0.11902 | 0.059509 | -0.022888 | 0.11444 | 0.2243 | 0.16479 | 0.21973 | 121.6141 | -0.032043 | -0.068664 | 121.8613 | 121.756 | 121.7468 | 0.14191 | 0.13275 | 121.6324 | -0.050354 | 0.004578 | 121.8796 | 121.875 | 121.8201 | 0.24261 | 0.18768 | 0.24719 | 0.082398 | 0.24719 | 0.13733 | 0.11902 | 0.082397 | 121.7331 | 121.7148 | -0.15106 | -0.13275 | 121.6965 | 121.7697 | 121.6324 | 121.7743
1117 | 121.9482 | -121.6827 | 0.11902 | -0.011291 | 0.074264 | 0.01333 | 0.032298 | -0.002117 | -0.0016876 | -0.0025057 | -0.0046081 | 0.0032855 | 0.019275 | -0.0011215 | -0.00052345 | 0.018812 | 0.00064307 | -0.073242 | 0.10071 | -0.073242 | -0.050354 | 0.050354 | -0.054932 | -0.022888 | -0.009155 | 0.091553 | -0.050354 | 0.054932 | 0.10986 | 0.036621 | 0.16937 | 121.6095 | -0.018311 | -0.16937 | 121.7331 | 121.6599 | 121.6278 | 0.050354 | 0.01831 | 121.6324 | -0.027466 | -0.064087 | 121.7926 | 121.8521 | 121.7194 | 0.21973 | 0.086975 | 0.1236 | 0.022888 | 0.16022 | 0.10529 | 0.17395 | 0.14191 | 121.7834 | 121.7743 | -0.19226 | -0.16937 | 121.6324 | 121.7377 | 121.6095 | 121.6736
1118.6875 | 122.0215 | -121.6553 | 0.11444 | -0.011291 | 0.07106 | 0.014185 | 0.030589 | -0.0016898 | -0.001474 | -0.0010105 | 0.0014953 | 0.0022175 | 0.018207 | -0.0079575 | -0.0030869 | 0.017743 | -0.0019205 | -0.036621 | 0.091553 | -0.036621 | 0.004578 | 0.16479 | 0.064087 | 0.082397 | 0.064087 | 0.073242 | -0.041199 | 0.086975 | 0.1831 | 0.13275 | 0.22888 | 121.6187 | -0.022888 | -0.10986 | 121.8201 | 121.7377 | 121.7194 | 0.11902 | 0.10071 | 121.6141 | -0.041199 | -0.027466 | 121.8384 | 121.8842 | 121.788 | 0.27008 | 0.17395 | 0.20142 | 0.041199 | 0.2243 | 0.12817 | 0.12817 | 0.11444 | 121.7468 | 121.7285 | -0.15106 | -0.15564 | 121.6599 | 121.7422 | 121.6187 | 121.7194
1120.4531 | 121.9208 | -121.6919 | 0.12817 | 0.0039673 | 0.075759 | 0.014185 | 0.033152 | 0.00087375 | -0.0021148 | -0.0048557 | -0.0015565 | 0.0024311 | 0.020557 | -0.0032577 | -0.0018051 | 0.017103 | -0.00063873 | -0.07782 | 0.11902 | -0.073242 | -0.07782 | 0.050354 | -0.059509 | -0.027466 | -0.022888 | 0.11444 | -0.050354 | 0.050354 | 0.07782 | 0 | 0.14191 | 121.6187 | -0.009155 | -0.20599 | 121.7422 | 121.6644 | 121.6324 | 0.045776 | 0.013733 | 121.6415 | -0.013733 | -0.07782 | 121.7697 | 121.8338 | 121.6919 | 0.19226 | 0.050354 | 0.1236 | -0.004578 | 0.12817 | 0.10071 | 0.19226 | 0.16479 | 121.8109 | 121.8063 | -0.20142 | -0.17853 | 121.6141 | 121.7422 | 121.6141 | 121.669
1122.125 | 121.9528 | -121.7056 | 0.11902 | -0.018921 | 0.075973 | 0.01333 | 0.033579 | -0.00062165 | -0.0040374 | -0.0016513 | -0.0076599 | 0.0026447 | 0.02013 | -0.0098801 | -0.0011643 | 0.017743 | -0.0036295 | -0.059509 | 0.07782 | -0.059509 | -0.027466 | 0.11444 | -0.009155 | 0.004578 | 0.018311 | 0.10071 | -0.054932 | 0.041199 | 0.10986 | 0.045776 | 0.15564 | 121.6461 | -0.041199 | -0.14649 | 121.8201 | 121.7102 | 121.6965 | 0.064087 | 0.050354 | 121.6507 | -0.018311 | -0.07782 | 121.8155 | 121.8613 | 121.7514 | 0.21057 | 0.10071 | 0.17395 | 0.032043 | 0.16479 | 0.096131 | 0.13733 | 0.15564 | 121.7834 | 121.8063 | -0.17853 | -0.17395 | 121.6782 | 121.7468 | 121.6461 | 121.7239
1123.875 | 121.9757 | -121.7056 | 0.10986 | -0.018921 | 0.074264 | 0.015894 | 0.031657 | -0.0010488 | 0.00023496 | -0.00015591 | -0.010712 | -0.0014141 | 0.020343 | -0.0079575 | -0.0024461 | 0.018384 | -0.0044839 | -0.059509 | 0.073242 | -0.045776 | -0.013733 | 0.1236 | 0.013733 | 0.032043 | 0 | 0.073242 | -0.022888 | 0.041199 | 0.14191 | 0.073242 | 0.16937 | 121.6599 | -0.036621 | -0.1236 | 121.8292 | 121.7377 | 121.7194 | 0.077819 | 0.059509 | 121.6827 | -0.036621 | -0.068664 | 121.8475 | 121.875 | 121.7789 | 0.19226 | 0.09613 | 0.16937 | 0.032043 | 0.16479 | 0.064087 | 0.11902 | 0.09613 | 121.7789 | 121.7789 | -0.15564 | -0.13275 | 121.6919 | 121.7468 | 121.6461 | 121.7056
1125.625 | 121.9666 | -121.6965 | 0.11902 | -0.0036622 | 0.074905 | 0.01333 | 0.032939 | 0.00066015 | -0.00019224 | 0.0013395 | -0.0046081 | 0.0028583 | 0.017566 | -0.0090255 | 0.0011855 | 0.018171 | -0.0059793 | -0.086975 | 0.10071 | -0.073242 | -0.059509 | 0.073242 | -0.050354 | -0.022888 | -0.004578 | 0.09613 | -0.064087 | 0.064087 | 0.09613 | 0.027466 | 0.16479 | 121.6232 | -0.018311 | -0.17853 | 121.7697 | 121.6736 | 121.6461 | 0.050354 | 0.022888 | 121.6324 | -0.022889 | -0.054932 | 121.7926 | 121.8613 | 121.7239 | 0.22888 | 0.091553 | 0.14648 | 0.013733 | 0.16022 | 0.12817 | 0.17395 | 0.16022 | 121.7972 | 121.7926 | -0.19226 | -0.18311 | 121.637 | 121.7606 | 121.6095 | 121.6919
1127.2969 | 121.8933 | -121.7377 | 0.13275 | -0.011291 | 0.075973 | 0.012476 | 0.032939 | -0.0010488 | -0.001474 | -0.0018649 | -0.0046081 | 0.0013629 | 0.021198 | -0.0077439 | 0.00033115 | 0.019025 | -0.0027749 | -0.082397 | 0.10529 | -0.082397 | -0.091553 | 0.027466 | -0.082397 | -0.041199 | -0.068665 | 0.11902 | -0.068665 | -0.022888 | 0.018311 | -0.045776 | 0.10529 | 121.6553 | -0.027465 | -0.2243 | 121.7651 | 121.6965 | 121.6553 | 0.041198 | 0 | 121.669 | -0.013732 | -0.15564 | 121.756 | 121.843 | 121.6919 | 0.17395 | 0.022889 | 0.10986 | -0.009156 | 0.086976 | 0.045777 | 0.18768 | 0.18768 | 121.843 | 121.8567 | -0.21515 | -0.20142 | 121.6461 | 121.7148 | 121.6553 | 121.669
1129.0469 | 121.9162 | -121.7331 | 0.14191 | 0.011597 | 0.073837 | 0.014185 | 0.033579 | 0.0025828 | -0.0033966 | -0.0010105 | -0.0015565 | 0.0047809 | 0.017139 | -0.0083847 | -0.0039413 | 0.018171 | -0.0029885 | -0.050354 | 0.086975 | -0.064087 | -0.036621 | 0.10529 | -0.009155 | 0 | 0.004578 | 0.086975 | -0.050354 | 0.022888 | 0.086975 | 0 | 0.09613 | 121.669 | -0.054932 | -0.17853 | 121.8384 | 121.7331 | 121.7239 | 0.064087 | 0.054932 | 121.6827 | -0.054932 | -0.11902 | 121.8201 | 121.8292 | 121.7331 | 0.14648 | 0.050354 | 0.16937 | 0.027466 | 0.13733 | 0.073242 | 0.15106 | 0.13733 | 121.8201 | 121.8201 | -0.20599 | -0.19226 | 121.6965 | 121.756 | 121.6827 | 121.7377
1130.7969 | 122.0169 | -121.6919 | 0.11902 | -0.0036622 | 0.073623 | 0.016321 | 0.029307 | 0.0025828 | -0.0033966 | -0.0031467 | -0.0076599 | 0.0020039 | 0.018634 | -0.0053939 | -0.0033005 | 0.01988 | 0.0019247 | -0.022888 | 0.054932 | -0.036621 | 0.045776 | 0.21057 | 0.09613 | 0.10986 | 0.086975 | 0.07782 | -0.032043 | 0.09613 | 0.21515 | 0.14648 | 0.20599 | 121.6553 | -0.064087 | -0.073243 | 121.9025 | 121.8018 | 121.788 | 0.14648 | 0.13275 | 121.6599 | -0.041199 | -0.022889 | 121.907 | 121.8979 | 121.8384 | 0.23804 | 0.17853 | 0.24719 | 0.082397 | 0.24719 | 0.12817 | 0.091553 | 0.10986 | 121.7468 | 121.7697 | -0.15564 | -0.15106 | 121.7377 | 121.788 | 121.669 | 121.7789
1132.5312 | 121.9574 | -121.7239 | 0.1236 | -0.02655 | 0.07405 | 0.014398 | 0.030802 | -0.00083525 | -0.003183 | -0.00079691 | -0.0046081 | 0.0030719 | 0.019062 | -0.0028305 | -0.0026597 | 0.018384 | 0.00021567 | -0.041199 | 0.086975 | -0.059509 | -0.013733 | 0.13275 | 0.009155 | 0.018311 | 0.004578 | 0.09613 | -0.050354 | 0.032043 | 0.11902 | 0.054932 | 0.16937 | 121.6644 | -0.036621 | -0.13733 | 121.8567 | 121.7422 | 121.7331 | 0.07782 | 0.068664 | 121.6736 | -0.027466 | -0.091553 | 121.843 | 121.8933 | 121.7789 | 0.21973 | 0.10529 | 0.19226 | 0.045776 | 0.16937 | 0.082397 | 0.14648 | 0.14648 | 121.8109 | 121.8201 | -0.1831 | -0.17395 | 121.7102 | 121.756 | 121.6827 | 121.7285
1134.2031 | 122.0352 | -121.6919 | 0.10529 | -0.011291 | 0.074905 | 0.014185 | 0.029521 | 0.0032236 | -0.0019012 | -0.00058311 | -0.0015565 | 0.0020039 | 0.019703 | 0.0012283 | 0.00033115 | 0.017103 | -0.0029885 | -0.032043 | 0.082397 | -0.032043 | 0.036621 | 0.18768 | 0.059509 | 0.068665 | 0.082397 | 0.064087 | -0.036621 | 0.12817 | 0.19684 | 0.11444 | 0.23804 | 121.6599 | -0.022889 | -0.068665 | 121.8796 | 121.7606 | 121.7514 | 0.10071 | 0.091552 | 121.6553 | -0.041199 | 0.022888 | 121.8887 | 121.9299 | 121.8063 | 0.27466 | 0.15106 | 0.21973 | 0.068664 | 0.23346 | 0.1648 | 0.11444 | 0.10071 | 121.7743 | 121.756 | -0.13733 | -0.14191 | 121.7285 | 121.8201 | 121.6599 | 121.7743
1135.9531 | 121.9116 | -121.7377 | 0.14191 | -0.0036622 | 0.073623 | 0.013116 | 0.031016 | 0.0027964 | -0.0053192 | -0.0054965 | -0.0015565 | 0.0030719 | 0.02013 | -0.0075301 | -0.0047959 | 0.016462 | -0.00021153 | -0.068665 | 0.10529 | -0.054932 | -0.064087 | 0.091553 | 0.013733 | 0.004578 | -0.041199 | 0.086975 | -0.054932 | -0.018311 | 0.068665 | 0.009155 | 0.09613 | 121.6827 | -0.036621 | -0.20599 | 121.8292 | 121.7422 | 121.7514 | 0.05951 | 0.068665 | 121.6827 | -0.054932 | -0.16022 | 121.8063 | 121.8338 | 121.7468 | 0.15106 | 0.064087 | 0.14649 | -0.009155 | 0.1236 | 0.036621 | 0.16022 | 0.14191 | 121.843 | 121.8246 | -0.19684 | -0.19684 | 121.6736 | 121.7194 | 121.669 | 121.6965
1137.7031 | 122.0123 | -121.7194 | 0.11902 | -0.02655 | 0.075759 | 0.015466 | 0.030162 | -0.00083525 | 2.1362e-05 | -0.0040011 | -0.010712 | 0.0017901 | 0.019275 | 0.0040055 | 0.0020401 | 0.019452 | 0.00085667 | -0.013733 | 0.045776 | -0.018311 | 0.027466 | 0.18768 | 0.064087 | 0.064087 | 0.09613 | 0.045776 | -0.009155 | 0.10986 | 0.1831 | 0.10986 | 0.20599 | 121.701 | -0.073243 | -0.091553 | 121.907 | 121.7834 | 121.7834 | 0.082398 | 0.082398 | 121.7102 | -0.073243 | -0.009156 | 121.9025 | 121.9254 | 121.8292 | 0.21515 | 0.11902 | 0.20599 | 0.045777 | 0.19226 | 0.11902 | 0.064087 | 0.054931 | 121.7651 | 121.7651 | -0.13733 | -0.12817 | 121.7468 | 121.8292 | 121.7056 | 121.8155
1139.3906 | 122.0032 | -121.7056 | 0.1236 | -0.0036622 | 0.074905 | 0.015253 | 0.029948 | -0.0010488 | -0.0033966 | -0.0025057 | -0.0015565 | 0.0026447 | 0.018848 | 0.00016027 | -0.0039413 | 0.019452 | -0.0027749 | -0.004578 | 0.082397 | -0.036621 | 0.050354 | 0.20142 | 0.091553 | 0.10071 | 0.10986 | 0.073242 | -0.022888 | 0.10071 | 0.20142 | 0.11444 | 0.19684 | 121.669 | -0.041199 | -0.073242 | 121.907 | 121.8063 | 121.7972 | 0.13733 | 0.12817 | 121.6827 | -0.050354 | -0.022888 | 121.907 | 121.9025 | 121.8201 | 0.21973 | 0.13733 | 0.23804 | 0.086975 | 0.2243 | 0.1236 | 0.11902 | 0.09613 | 121.788 | 121.7789 | -0.16022 | -0.14648 | 121.756 | 121.8063 | 121.701 | 121.8155
1141.0625 | 121.9437 | -121.7285 | 0.13275 | -0.018921 | 0.075118 | 0.015039 | 0.032725 | -0.0036124 | -0.0051056 | 5.7688e-05 | -0.010712 | 0.0020039 | 0.018848 | -0.0028305 | -0.0043687 | 0.014966 | 0.00021567 | -0.082397 | 0.10986 | -0.064087 | -0.07782 | 0.045776 | -0.027466 | -0.022888 | -0.07782 | 0.11444 | -0.045776 | 0.009155 | 0.10071 | 0.013733 | 0.14191 | 121.6644 | -0.022888 | -0.21057 | 121.7743 | 121.7056 | 121.701 | 0.041199 | 0.036621 | 121.6827 | -0.01831 | -0.1236 | 121.8292 | 121.8704 | 121.7422 | 0.18768 | 0.059509 | 0.10986 | -0.013733 | 0.14648 | 0.054931 | 0.17395 | 0.16022 | 121.8384 | 121.843 | -0.19684 | -0.17853 | 121.6507 | 121.7377 | 121.6461 | 121.6507
1142.8125 | 122.0032 | -121.7285 | 0.1236 | 0.0039673 | 0.075118 | 0.014825 | 0.031443 | 0.0034372 | -0.0027556 | -0.0018649 | -0.0046081 | 0.0041401 | 0.018207 | -0.00048073 | -9.605e-05 | 0.019452 | -0.00042513 | -0.068665 | 0.10529 | -0.073242 | -0.050354 | 0.082397 | -0.041199 | -0.009155 | 0.009155 | 0.086975 | -0.045776 | 0.068665 | 0.13733 | 0.064087 | 0.18768 | 121.6553 | -0.01831 | -0.17395 | 121.8109 | 121.7194 | 121.6873 | 0.064087 | 0.032043 | 121.6827 | -0.036621 | -0.054931 | 121.8658 | 121.9162 | 121.7926 | 0.23346 | 0.10986 | 0.15564 | 0.022888 | 0.18311 | 0.11444 | 0.17853 | 0.13275 | 121.8338 | 121.8155 | -0.19684 | -0.16937 | 121.6782 | 121.7972 | 121.6599 | 121.7377
1144.5625 | 121.9574 | -121.7514 | 0.1236 | -0.0036622 | 0.074905 | 0.014612 | 0.032084 | -0.006603 | -0.0021148 | -0.0035739 | -0.0076599 | 0.0024311 | 0.019703 | -0.0056075 | -0.0033005 | 0.017957 | -0.0072611 | -0.018311 | 0.11902 | -0.059509 | -0.022888 | 0.10986 | 0.009155 | 0.013733 | 0.013733 | 0.09613 | -0.054932 | 0.059509 | 0.11444 | 0.045776 | 0.16937 | 121.6919 | -0.004577 | -0.14648 | 121.8613 | 121.7651 | 121.7606 | 0.073242 | 0.068664 | 121.6965 | -0.027466 | -0.064087 | 121.8658 | 121.9208 | 121.7972 | 0.22431 | 0.10071 | 0.16937 | 0.036621 | 0.16937 | 0.11444 | 0.17853 | 0.15106 | 121.8704 | 121.8475 | -0.1831 | -0.17853 | 121.7285 | 121.8109 | 121.7331 | 121.7651
1146.25 | 121.9894 | -121.7194 | 0.10529 | -0.018921 | 0.074691 | 0.014398 | 0.028239 | -0.0029714 | -0.0029694 | -0.0025057 | -0.0076599 | 0.0017901 | 0.020557 | -0.0079575 | 0.00033115 | 0.016675 | 2.068e-06 | -0.073242 | 0.082397 | -0.027466 | -0.022888 | 0.10986 | 0.027466 | 0.041199 | 0.004578 | 0.082397 | -0.041199 | 0.050354 | 0.11902 | 0.054932 | 0.17395 | 121.6919 | -0.022889 | -0.12817 | 121.8292 | 121.7606 | 121.7468 | 0.068665 | 0.054932 | 121.6782 | -0.022889 | -0.054932 | 121.8384 | 121.8933 | 121.7743 | 0.21515 | 0.096131 | 0.13733 | 0.004578 | 0.16022 | 0.091553 | 0.10986 | 0.1236 | 121.8018 | 121.8018 | -0.13275 | -0.14649 | 121.6965 | 121.7697 | 121.6461 | 121.7239
1147.9844 | 121.907 | -121.7514 | 0.15564 | -0.011291 | 0.075973 | 0.01568 | 0.03123 | 0.0042918 | -0.0033966 | -0.0029331 | 0.0014953 | 0.0039265 | 0.017994 | -0.0038987 | 0.00011755 | 0.01988 | -0.0021341 | -0.073242 | 0.10071 | -0.054932 | -0.082397 | 0.059509 | -0.059509 | -0.013733 | -0.045776 | 0.11444 | -0.045776 | 0.004578 | 0.045776 | -0.036621 | 0.11902 | 121.6965 | -0.054932 | -0.23804 | 121.8109 | 121.7377 | 121.6919 | 0.041199 | -0.004577 | 121.7056 | -0.041199 | -0.15106 | 121.7972 | 121.8704 | 121.7148 | 0.16479 | 0.009155 | 0.11444 | -0.027465 | 0.091552 | 0.050354 | 0.15564 | 0.16022 | 121.8521 | 121.8658 | -0.21057 | -0.20142 | 121.669 | 121.756 | 121.6782 | 121.7056
1149.7344 | 122.049 | -121.7056 | 0.10986 | -0.0036622 | 0.072555 | 0.016321 | 0.030162 | -0.0033986 | -0.0038238 | -0.00015591 | -0.0015565 | 0.0017901 | 0.017994 | -0.00026713 | -0.0030869 | 0.019666 | 0.0010703 | -0.009155 | 0.068665 | -0.041199 | 0.045776 | 0.23346 | 0.11444 | 0.091553 | 0.09613 | 0.091553 | -0.032043 | 0.11444 | 0.21515 | 0.14191 | 0.20599 | 121.6644 | -0.041198 | -0.064087 | 121.9391 | 121.7972 | 121.8201 | 0.13275 | 0.15564 | 121.6736 | -0.01831 | 0.004578 | 121.9208 | 121.9116 | 121.8475 | 0.23804 | 0.17395 | 0.27466 | 0.086975 | 0.24719 | 0.14648 | 0.10986 | 0.1236 | 121.7743 | 121.7972 | -0.15106 | -0.14191 | 121.7514 | 121.8201 | 121.6965 | 121.8018
1151.4219 | 122.0673 | -121.6965 | 0.10529 | -0.011291 | 0.074264 | 0.012048 | 0.029093 | -0.0044668 | -0.0029694 | 0.0017667 | -0.0076599 | 0.00050846 | 0.018634 | -0.0024033 | -0.00030965 | 0.014753 | -0.0014931 | -0.032043 | 0.059509 | -0.045776 | 0.045776 | 0.21057 | 0.09613 | 0.13733 | 0.11444 | 0.064087 | -0.050354 | 0.11444 | 0.21973 | 0.15564 | 0.23804 | 121.6507 | -0.045777 | -0.05951 | 121.907 | 121.8338 | 121.7926 | 0.18311 | 0.14191 | 121.6461 | -0.041199 | 0.009155 | 121.9162 | 121.9345 | 121.8521 | 0.28839 | 0.20599 | 0.25635 | 0.091552 | 0.27008 | 0.16479 | 0.10528 | 0.11444 | 121.756 | 121.7606 | -0.15106 | -0.15564 | 121.7422 | 121.8109 | 121.6644 | 121.8109
1153.0938 | 121.9208 | -121.7651 | 0.15106 | 0.0039673 | 0.074478 | 0.015039 | 0.028666 | -0.0012624 | -0.0023284 | -0.0027195 | 0.0014953 | 0.0039265 | 0.019916 | -0.0030441 | -0.0069321 | 0.01753 | 0.0010703 | -0.073242 | 0.091553 | -0.073242 | -0.045776 | 0.07782 | 0 | 0.004578 | -0.050354 | 0.10529 | -0.068665 | -0.018311 | 0.073242 | 0.004578 | 0.09613 | 121.6919 | -0.059509 | -0.19684 | 121.843 | 121.7697 | 121.7651 | 0.07782 | 0.073242 | 121.6965 | -0.045776 | -0.16937 | 121.8384 | 121.8613 | 121.7697 | 0.16479 | 0.073243 | 0.15106 | 0.027466 | 0.14191 | 0.050354 | 0.16479 | 0.17395 | 121.8567 | 121.8704 | -0.2243 | -0.21973 | 121.7194 | 121.7468 | 121.6919 | 121.7148
1154.8438 | 122.0261 | -121.7102 | 0.10986 | -0.018921 | 0.075332 | 0.014185 | 0.030802 | -0.001476 | -0.0012604 | -0.00036951 | -0.0076599 | 0.0045673 | 0.017353 | -0.0075301 | -0.0022325 | 0.019025 | -0.00021153 | -0.022888 | 0.059509 | -0.032043 | 0.050354 | 0.21057 | 0.086975 | 0.10071 | 0.082397 | 0.073242 | -0.032043 | 0.09613 | 0.18768 | 0.11444 | 0.20599 | 121.6782 | -0.050354 | -0.059509 | 121.9208 | 121.8109 | 121.7972 | 0.13275 | 0.11902 | 121.6782 | -0.036621 | -0.013733 | 121.8979 | 121.9162 | 121.8246 | 0.23804 | 0.14648 | 0.24261 | 0.082397 | 0.21973 | 0.12817 | 0.091552 | 0.10529 | 121.7697 | 121.7834 | -0.14191 | -0.14191 | 121.7606 | 121.8063 | 121.6873 | 121.7926
1156.5938 | 121.9025 | -121.7743 | 0.12817 | -0.018921 | 0.074905 | 0.012048 | 0.030375 | -0.00062165 | -0.00596 | -0.0018649 | -0.013763 | 0.0032855 | 0.018421 | -0.0075301 | -0.0041551 | 0.017103 | -0.00063873 | -0.10529 | 0.091553 | -0.073242 | -0.086975 | 0.032043 | -0.045776 | -0.018311 | -0.091553 | 0.10529 | -0.050354 | 0 | 0.064087 | -0.009155 | 0.11902 | 121.7011 | -0.036621 | -0.21515 | 121.8063 | 121.756 | 121.7285 | 0.054931 | 0.027466 | 121.7239 | -0.022888 | -0.12817 | 121.8384 | 121.8933 | 121.7651 | 0.16937 | 0.041199 | 0.10529 | -0.013733 | 0.11444 | 0.050354 | 0.16479 | 0.15564 | 121.8658 | 121.8796 | -0.20142 | -0.17853 | 121.6873 | 121.7743 | 121.669 | 121.6827
1158.2656 | 121.8887 | -121.7422 | 0.14648 | -0.011291 | 0.076827 | 0.014825 | 0.031871 | -0.0025442 | -0.003183 | -0.0020785 | -0.0046081 | 0.0049945 | 0.019062 | -0.0047531 | -0.0022325 | 0.018171 | -0.0040567 | -0.073242 | 0.11444 | -0.068665 | -0.082397 | 0.045776 | -0.082397 | -0.036621 | -0.082397 | 0.10529 | -0.059509 | -0.009155 | 0.027466 | -0.027466 | 0.10071 | 121.6736 | -0.032043 | -0.22888 | 121.788 | 121.7056 | 121.6599 | 0.032044 | -0.013732 | 121.6827 | -0.041198 | -0.15564 | 121.7697 | 121.843 | 121.7148 | 0.16022 | 0.032043 | 0.11444 | -0.013732 | 0.086975 | 0.050354 | 0.18311 | 0.16479 | 121.8567 | 121.8475 | -0.21515 | -0.20599 | 121.6599 | 121.7331 | 121.669 | 121.6599
1159.9375 | 122.0078 | -121.7056 | 0.10529 | -0.018921 | 0.07341 | 0.015894 | 0.030375 | 0.00023275 | -0.002542 | -0.0046421 | -0.0015565 | 0.0017901 | 0.019062 | -0.0049667 | -0.00073705 | 0.020307 | -0.00063873 | -0.068665 | 0.064087 | -0.027466 | -0.013733 | 0.11902 | 0.013733 | 0.041199 | 0 | 0.059509 | -0.022888 | 0.045776 | 0.12817 | 0.068665 | 0.16479 | 121.6782 | -0.041199 | -0.11902 | 121.8246 | 121.7468 | 121.7194 | 0.068665 | 0.041199 | 121.6827 | -0.045777 | -0.05951 | 121.8338 | 121.8704 | 121.7743 | 0.18768 | 0.091553 | 0.14649 | 0.013733 | 0.15106 | 0.068664 | 0.091553 | 0.082397 | 121.7697 | 121.7651 | -0.13275 | -0.12817 | 121.6919 | 121.7514 | 121.637 | 121.7056
1161.625 | 121.9299 | -121.7514 | 0.15106 | -0.0036622 | 0.075973 | 0.013757 | 0.031016 | -0.002117 | -0.00596 | 0.00027129 | -0.0015565 | 0.0041401 | 0.018848 | -0.0038987 | -0.0033005 | 0.016462 | -0.0049111 | -0.050354 | 0.086975 | -0.068665 | -0.041199 | 0.091553 | 0 | 0.009155 | -0.027466 | 0.10529 | -0.059509 | -0.018311 | 0.086975 | 0.009155 | 0.09613 | 121.6827 | -0.064087 | -0.19226 | 121.843 | 121.7606 | 121.7514 | 0.07782 | 0.068665 | 121.6919 | -0.045776 | -0.16937 | 121.8384 | 121.8475 | 121.7606 | 0.15564 | 0.068664 | 0.16022 | 0.027466 | 0.14648 | 0.041198 | 0.15564 | 0.16479 | 121.8384 | 121.8567 | -0.21973 | -0.21057 | 121.7102 | 121.7331 | 121.701 | 121.7239
1164.7656 | 121.9894 | -121.7194 | 0.12817 | -0.02655 | 0.074478 | 0.014185 | 0.030589 | -0.0016898 | -0.001474 | -0.0031467 | -0.0046081 | 0.0013629 | 0.01778 | -0.0077439 | -0.0011643 | 0.018384 | 0.0025657 | -0.068665 | 0.073242 | -0.022888 | -0.041199 | 0.12817 | 0.004578 | 0.045776 | 0.018311 | 0.059509 | -0.032043 | 0.045776 | 0.14648 | 0.07782 | 0.16479 | 121.6965 | -0.054932 | -0.16937 | 121.8475 | 121.7651 | 121.7239 | 0.068664 | 0.027466 | 121.6873 | -0.068665 | -0.082398 | 121.8658 | 121.8842 | 121.7972 | 0.19684 | 0.10986 | 0.15106 | -0.018311 | 0.17853 | 0.077819 | 0.09613 | 0.091552 | 121.7926 | 121.7789 | -0.15106 | -0.16022 | 121.6782 | 121.7651 | 121.6507 | 121.7377
1168.5 | 121.9162 | -121.756 | 0.13275 | -0.0036622 | 0.075973 | 0.015039 | 0.03422 | -0.0023306 | -0.001474 | -0.0014377 | 0.0014953 | 0.0039265 | 0.019275 | -0.0024033 | -0.0013779 | 0.021161 | -0.0019205 | -0.086975 | 0.091553 | -0.073242 | -0.086975 | 0.022888 | -0.07782 | -0.041199 | -0.068665 | 0.10986 | -0.054932 | -0.013733 | 0.045776 | -0.013733 | 0.11902 | 121.6827 | -0.041198 | -0.21973 | 121.7789 | 121.7148 | 121.6782 | 0.032043 | -0.004578 | 121.701 | -0.022888 | -0.14648 | 121.8018 | 121.875 | 121.7422 | 0.17395 | 0.041199 | 0.09613 | -0.013733 | 0.10071 | 0.041199 | 0.16479 | 0.16479 | 121.8475 | 121.8658 | -0.20599 | -0.18768 | 121.669 | 121.7422 | 121.669 | 121.6873
1173.7812 | 122.0627 | -121.7239 | 0.10986 | -0.0036622 | 0.073837 | 0.015466 | 0.030802 | -0.002117 | -0.0033966 | 5.7688e-05 | -0.0046081 | 0.0024311 | 0.019489 | 0.0018693 | -0.0035141 | 0.019239 | 0.0027793 | -0.032043 | 0.082397 | -0.032043 | 0.036621 | 0.19226 | 0.07782 | 0.10071 | 0.091553 | 0.082397 | -0.027466 | 0.11902 | 0.22888 | 0.16022 | 0.22888 | 121.6919 | -0.027466 | -0.073242 | 121.9162 | 121.8246 | 121.8018 | 0.13275 | 0.10986 | 121.6965 | -0.027466 | 0.009156 | 121.9528 | 121.9528 | 121.8842 | 0.25635 | 0.18768 | 0.2243 | 0.068664 | 0.25635 | 0.14649 | 0.11444 | 0.10986 | 121.8063 | 121.8063 | -0.14191 | -0.13733 | 121.7606 | 121.843 | 121.6919 | 121.8155
1176.4062 | 121.962 | -121.7468 | 0.13733 | 0.0039673 | 0.08345 | 0.012689 | 0.040415 | -0.00083525 | -0.0027556 | -0.0031467 | -0.0015565 | 0.0056355 | 0.020343 | -0.0079575 | -0.00073705 | 0.016675 | -0.0021341 | -0.027466 | 0.11902 | -0.054932 | 0 | 0.1236 | 0.009155 | 0.018311 | 0.032043 | 0.10986 | -0.022888 | 0.068665 | 0.09613 | 0.036621 | 0.14648 | 121.6919 | -0.01831 | -0.13733 | 121.8704 | 121.7651 | 121.756 | 0.073243 | 0.064087 | 121.7239 | -0.027466 | -0.068664 | 121.843 | 121.8933 | 121.7834 | 0.16937 | 0.059509 | 0.17853 | 0.054932 | 0.11902 | 0.091553 | 0.17395 | 0.13275 | 121.8658 | 121.8567 | -0.19226 | -0.16022 | 121.7468 | 121.8155 | 121.7194 | 121.7789
1178.0938 | 121.9391 | -121.7422 | 0.14191 | -0.011291 | 0.084945 | 0.013971 | 0.039561 | 0.0038644 | -0.0023284 | -0.0012241 | -0.0015565 | 0.0043537 | 0.019916 | -0.0060349 | -0.0011643 | 0.019239 | -0.0021341 | -0.082397 | 0.10986 | -0.064087 | -0.09613 | 0.045776 | -0.068665 | -0.041199 | -0.050354 | 0.10529 | -0.059509 | 0 | 0.041199 | -0.022888 | 0.1236 | 121.6782 | -0.032044 | -0.23804 | 121.788 | 121.701 | 121.6736 | 0.022888 | -0.004578 | 121.6827 | -0.036621 | -0.14191 | 121.7834 | 121.8658 | 121.7194 | 0.1831 | 0.036621 | 0.10986 | -0.032043 | 0.10071 | 0.059509 | 0.17395 | 0.16479 | 121.8521 | 121.8475 | -0.20599 | -0.20142 | 121.6461 | 121.7422 | 121.6599 | 121.6919
1179.8438 | 121.9391 | -121.7789 | 0.14648 | 0.0039673 | 0.073196 | 0.014398 | 0.031871 | -0.0025442 | -0.0033966 | -0.0014377 | -0.0046081 | 0.0017901 | 0.020343 | -0.0015487 | -0.0077867 | 0.018812 | 0.00021567 | -0.032043 | 0.07782 | -0.059509 | -0.018311 | 0.14191 | 0.032043 | 0.041199 | 0 | 0.10071 | -0.045776 | 0.009155 | 0.10071 | 0.018311 | 0.11902 | 121.7194 | -0.068664 | -0.16479 | 121.9208 | 121.8201 | 121.8109 | 0.10071 | 0.091552 | 121.7331 | -0.045776 | -0.13733 | 121.8796 | 121.8979 | 121.7972 | 0.16479 | 0.064087 | 0.20142 | 0.041198 | 0.14648 | 0.054931 | 0.13733 | 0.14648 | 121.8567 | 121.8796 | -0.20599 | -0.19226 | 121.7606 | 121.788 | 121.7468 | 121.7789
1181.5781 | 121.9345 | -121.7285 | 0.14648 | 0.0039673 | 0.075546 | 0.016748 | 0.032939 | -0.00083525 | -0.001474 | -0.0016513 | -0.0015565 | 0.0049945 | 0.019489 | -0.0077439 | 0.00033115 | 0.017957 | -0.0019205 | -0.041199 | 0.09613 | -0.045776 | -0.022888 | 0.10986 | -0.009155 | -0.004578 | 0.009155 | 0.10986 | -0.064087 | 0.022888 | 0.07782 | -0.009155 | 0.14191 | 121.6827 | -0.050354 | -0.16937 | 121.8384 | 121.7239 | 121.7194 | 0.041198 | 0.036621 | 121.6644 | -0.036621 | -0.1236 | 121.8063 | 121.8704 | 121.7194 | 0.20599 | 0.054932 | 0.15564 | 0.022888 | 0.14191 | 0.086975 | 0.14191 | 0.17395 | 121.8246 | 121.8384 | -0.19226 | -0.21057 | 121.7056 | 121.7514 | 121.6873 | 121.7377
1183.2812 | 121.962 | -121.7377 | 0.11902 | 0.0039673 | 0.073623 | 0.014185 | 0.032084 | 0.0017282 | -0.0019012 | -0.0025057 | -0.0046081 | 0.0034991 | 0.021625 | -0.0079575 | -0.00073705 | 0.019239 | -0.0029885 | -0.032043 | 0.10071 | -0.050354 | -0.022888 | 0.11902 | 0.004578 | 0.022888 | 0.018311 | 0.09613 | -0.032043 | 0.050354 | 0.13275 | 0.041199 | 0.16479 | 121.6873 | -0.018311 | -0.14191 | 121.8567 | 121.7606 | 121.7422 | 0.073242 | 0.054932 | 121.7056 | -0.022889 | -0.068665 | 121.8704 | 121.9025 | 121.7789 | 0.19684 | 0.073242 | 0.16937 | 0.027466 | 0.16479 | 0.082397 | 0.15106 | 0.12817 | 121.8384 | 121.8338 | -0.16937 | -0.15106 | 121.7148 | 121.788 | 121.7056 | 121.756
1185.0156 | 121.9116 | -121.7834 | 0.14191 | -0.02655 | 0.073623 | 0.01333 | 0.03123 | -0.0029714 | -0.002542 | -0.00058311 | -0.0076599 | 0.0024311 | 0.020557 | -0.01223 | -0.0022325 | 0.017103 | -0.00042513 | -0.12817 | 0.10071 | -0.050354 | -0.10986 | 0.045776 | -0.050354 | -0.022888 | -0.10071 | 0.10529 | -0.050354 | -0.022888 | 0.059509 | -0.004578 | 0.09613 | 121.7331 | -0.041199 | -0.25177 | 121.8292 | 121.7606 | 121.7331 | 0.027466 | 0 | 121.7331 | -0.036621 | -0.16479 | 121.843 | 121.8796 | 121.7789 | 0.14648 | 0.045776 | 0.09613 | -0.059509 | 0.10986 | 0.027466 | 0.15106 | 0.15564 | 121.8842 | 121.8887 | -0.19226 | -0.19226 | 121.6736 | 121.7606 | 121.6553 | 121.6827
1186.6875 | 122.0078 | -121.7285 | 0.1236 | -0.011291 | 0.073196 | 0.013544 | 0.030802 | -0.00083525 | -0.0023284 | -0.00079691 | -0.016815 | 0.00029486 | 0.018207 | -0.0011215 | -9.605e-05 | 0.018812 | -0.00085233 | -0.086975 | 0.073242 | -0.027466 | -0.027466 | 0.12817 | 0.004578 | 0.050354 | 0.013733 | 0.073242 | -0.054932 | 0.068665 | 0.13275 | 0.073242 | 0.16479 | 121.701 | -0.050354 | -0.15106 | 121.8567 | 121.7789 | 121.7331 | 0.07782 | 0.032044 | 121.6736 | -0.050354 | -0.054931 | 121.8613 | 121.8933 | 121.8018 | 0.21973 | 0.12817 | 0.15564 | 0 | 0.18768 | 0.1236 | 0.10071 | 0.12817 | 121.8018 | 121.8018 | -0.15106 | -0.17853 | 121.701 | 121.7972 | 121.6415 | 121.7422
1188.4219 | 122.049 | -121.701 | 0.10529 | 0.0039673 | 0.083663 | 0.014825 | 0.038706 | 0.0010874 | -0.0027556 | -0.0014377 | -0.010712 | 0.0032855 | 0.018421 | 0.0035783 | 0.00054475 | 0.021161 | 0.0010703 | 0.009155 | 0.073242 | -0.022888 | 0.036621 | 0.16479 | 0.050354 | 0.068665 | 0.086975 | 0.059509 | -0.013733 | 0.14191 | 0.20142 | 0.12817 | 0.23346 | 121.6782 | -0.032044 | -0.068665 | 121.8658 | 121.7697 | 121.7514 | 0.091553 | 0.073242 | 121.6873 | -0.045777 | 0.036621 | 121.9025 | 121.9345 | 121.8292 | 0.24719 | 0.14191 | 0.18768 | 0.059509 | 0.21515 | 0.15564 | 0.09613 | 0.073242 | 121.7743 | 121.7606 | -0.12817 | -0.11902 | 121.7377 | 121.843 | 121.7102 | 121.788
1190.0938 | 122.0169 | -121.701 | 0.12817 | -0.02655 | 0.083023 | 0.014612 | 0.036357 | 0.001301 | -0.002542 | -0.0018649 | -0.0076599 | 0.0011493 | 0.020984 | -0.0045395 | -0.00073705 | 0.019239 | 0.00021567 | -0.013733 | 0.064087 | -0.022888 | 0.032043 | 0.19684 | 0.059509 | 0.07782 | 0.10071 | 0.059509 | -0.009155 | 0.10071 | 0.18768 | 0.11444 | 0.21515 | 121.6782 | -0.064087 | -0.096131 | 121.8979 | 121.7789 | 121.7606 | 0.10071 | 0.082397 | 121.6919 | -0.068665 | -0.027466 | 121.8887 | 121.9162 | 121.8155 | 0.2243 | 0.1236 | 0.21973 | 0.054931 | 0.19684 | 0.10986 | 0.086975 | 0.068664 | 121.7651 | 121.7606 | -0.15106 | -0.13733 | 121.7331 | 121.8018 | 121.6873 | 121.8018
1191.8438 | 121.9666 | -121.7606 | 0.14648 | -0.018921 | 0.084732 | 0.012903 | 0.039775 | -0.002117 | -0.004892 | -0.0016513 | -0.0015565 | 0.0026447 | 0.01778 | -0.0094529 | -0.00052345 | 0.019452 | -0.0014931 | -0.050354 | 0.1236 | -0.050354 | -0.027466 | 0.09613 | 0.004578 | 0.013733 | 0.022888 | 0.10071 | -0.022888 | 0.050354 | 0.12817 | 0.050354 | 0.16937 | 121.7102 | -0.022888 | -0.17395 | 121.8567 | 121.7743 | 121.7651 | 0.064087 | 0.054932 | 121.7377 | -0.045776 | -0.09613 | 121.8887 | 121.9299 | 121.8109 | 0.19226 | 0.073242 | 0.14648 | 0.022888 | 0.15106 | 0.073242 | 0.17395 | 0.1236 | 121.8842 | 121.8613 | -0.19684 | -0.16937 | 121.7331 | 121.8109 | 121.7102 | 121.7834
1193.5781 | 121.9345 | -121.756 | 0.16022 | -0.011291 | 0.083236 | 0.012903 | 0.035716 | -0.00083525 | -0.0019012 | -0.0020785 | -0.0015565 | 0.0043537 | 0.019489 | -0.0041123 | -0.0069321 | 0.019239 | -0.0019205 | -0.091553 | 0.10529 | -0.064087 | -0.059509 | 0.068665 | -0.036621 | 0 | -0.059509 | 0.13733 | -0.059509 | -0.018311 | 0.068665 | 0.013733 | 0.10529 | 121.6919 | -0.054931 | -0.21973 | 121.8246 | 121.756 | 121.7194 | 0.064087 | 0.027466 | 121.6965 | -0.022888 | -0.17853 | 121.8246 | 121.8613 | 121.7697 | 0.16479 | 0.073242 | 0.13275 | 0.004578 | 0.12817 | 0.041198 | 0.16937 | 0.19684 | 121.8613 | 121.8933 | -0.2243 | -0.21973 | 121.6965 | 121.7377 | 121.6644 | 121.6965
1195.25 | 121.9391 | -121.7743 | 0.15564 | -0.0036622 | 0.083236 | 0.011835 | 0.037852 | -0.0012624 | -0.003183 | -0.0022921 | -0.010712 | 0.0020039 | 0.017994 | -0.0066757 | -0.0039413 | 0.019452 | -0.0012795 | -0.10986 | 0.11444 | -0.050354 | -0.10529 | 0.045776 | -0.022888 | -0.022888 | -0.082397 | 0.11444 | -0.050354 | -0.009155 | 0.068665 | 0 | 0.11444 | 121.7239 | -0.041199 | -0.26093 | 121.8201 | 121.7514 | 121.7514 | 0.027466 | 0.027466 | 121.7239 | -0.041199 | -0.16479 | 121.843 | 121.8887 | 121.7743 | 0.16479 | 0.050354 | 0.09613 | -0.054932 | 0.11902 | 0.041199 | 0.16479 | 0.16479 | 121.8887 | 121.8887 | -0.20599 | -0.20599 | 121.669 | 121.7651 | 121.6644 | 121.6919
1197 | 121.9803 | -121.7285 | 0.13275 | -0.0036622 | 0.084091 | 0.014825 | 0.039988 | 0.0010874 | -0.004251 | -0.0020785 | -0.0015565 | 0.0060627 | 0.017139 | -0.0051803 | -0.00030965 | 0.017103 | -0.0010659 | -0.036621 | 0.10529 | -0.059509 | -0.027466 | 0.11902 | 0.013733 | 0.022888 | 0.018311 | 0.10529 | -0.027466 | 0.068665 | 0.1236 | 0.064087 | 0.16022 | 121.669 | -0.027465 | -0.16022 | 121.8475 | 121.7514 | 121.7422 | 0.082397 | 0.073242 | 121.701 | -0.027465 | -0.064086 | 121.8521 | 121.8887 | 121.7926 | 0.18768 | 0.091553 | 0.17853 | 0.032043 | 0.15106 | 0.096131 | 0.16479 | 0.13275 | 121.8338 | 121.8338 | -0.19226 | -0.16022 | 121.701 | 121.7972 | 121.6919 | 121.7468
1198.7344 | 121.9666 | -121.7651 | 0.12817 | -0.011291 | 0.074478 | 0.013757 | 0.029307 | 1.915e-05 | -0.0044646 | -0.00079691 | -0.0046081 | 0.0045673 | 0.019062 | -0.0079575 | -0.0022325 | 0.016462 | 2.068e-06 | -0.041199 | 0.073242 | -0.050354 | 0.018311 | 0.16022 | 0.07782 | 0.073242 | 0.004578 | 0.068665 | -0.050354 | 0.027466 | 0.11444 | 0.054932 | 0.15564 | 121.7148 | -0.054932 | -0.10986 | 121.9254 | 121.8384 | 121.843 | 0.1236 | 0.12817 | 121.7148 | -0.059509 | -0.10071 | 121.8796 | 121.9208 | 121.8201 | 0.20599 | 0.10529 | 0.21057 | 0.068665 | 0.16479 | 0.07782 | 0.1236 | 0.11902 | 121.8384 | 121.8338 | -0.17853 | -0.17853 | 121.7834 | 121.7926 | 121.7239 | 121.7697
1200.4844 | 121.9162 | -121.7789 | 0.1236 | -0.0036622 | 0.075118 | 0.01333 | 0.033579 | 0.00066015 | -0.0010468 | 0.00027129 | 0.0075989 | 0.0039265 | 0.019916 | -0.0068893 | -0.00073705 | 0.015607 | -0.0021341 | -0.086975 | 0.11902 | -0.064087 | -0.10071 | 0.004578 | -0.091553 | -0.064087 | -0.07782 | 0.1236 | -0.073242 | 0.004578 | 0.032043 | -0.041199 | 0.10529 | 121.7148 | -0.004577 | -0.2243 | 121.7834 | 121.7148 | 121.6873 | 0 | -0.027466 | 121.7056 | 0 | -0.11902 | 121.8109 | 121.8842 | 121.7377 | 0.17853 | 0.032043 | 0.068665 | -0.036621 | 0.10529 | 0.07782 | 0.18311 | 0.19684 | 121.8979 | 121.9025 | -0.18768 | -0.19684 | 121.6782 | 121.7834 | 121.6919 | 121.701
1202.1562 | 122.0078 | -121.7102 | 0.13275 | -0.0036622 | 0.074478 | 0.01568 | 0.02888 | -0.0016898 | -0.004251 | -0.0044285 | -0.0076599 | -0.00098694 | 0.019275 | 0.0025101 | -0.0022325 | 0.019666 | 0.0036337 | -0.064087 | 0.086975 | -0.032043 | -0.036621 | 0.10529 | 0.009155 | 0.050354 | 0.013733 | 0.07782 | -0.036621 | 0.050354 | 0.13733 | 0.07782 | 0.16022 | 121.6782 | -0.045776 | -0.16937 | 121.8155 | 121.7606 | 121.7194 | 0.082397 | 0.041198 | 121.6736 | -0.054931 | -0.082397 | 121.8475 | 121.8704 | 121.788 | 0.19684 | 0.11444 | 0.13733 | -0.004578 | 0.17395 | 0.086975 | 0.11902 | 0.11444 | 121.7972 | 121.788 | -0.16479 | -0.16937 | 121.6736 | 121.7606 | 121.6461 | 121.7239
1203.8906 | 121.9574 | -121.7377 | 0.13275 | -0.0036622 | 0.076614 | 0.015039 | 0.032725 | 0.0045054 | -0.0010468 | -0.0012241 | -0.0046081 | 0.0034991 | 0.02013 | -0.0043259 | -0.0022325 | 0.017743 | -0.0021341 | -0.027466 | 0.091553 | -0.041199 | -0.027466 | 0.12817 | 0 | 0.009155 | 0.032043 | 0.11444 | -0.036621 | 0.041199 | 0.09613 | 0.018311 | 0.15564 | 121.6965 | -0.041198 | -0.16022 | 121.8658 | 121.7468 | 121.7377 | 0.050354 | 0.041199 | 121.7011 | -0.01831 | -0.091552 | 121.8338 | 121.8933 | 121.756 | 0.19226 | 0.054932 | 0.16937 | 0.013733 | 0.13275 | 0.07782 | 0.13275 | 0.15106 | 121.8292 | 121.8521 | -0.17395 | -0.16937 | 121.7102 | 121.7789 | 121.7102 | 121.7697
1205.625 | 122.0535 | -121.7331 | 0.11444 | -0.0036622 | 0.072555 | 0.016107 | 0.030375 | 0.0025828 | -0.0051056 | -0.0020785 | 0.0014953 | 0.00072206 | 0.017994 | -0.00069433 | -0.0035141 | 0.018812 | -0.0012795 | -0.013733 | 0.082397 | -0.041199 | 0.064087 | 0.23346 | 0.11902 | 0.1236 | 0.1236 | 0.059509 | -0.022888 | 0.10986 | 0.22888 | 0.15564 | 0.21057 | 121.6919 | -0.032044 | -0.050354 | 121.9666 | 121.8567 | 121.8521 | 0.16479 | 0.16022 | 121.7102 | -0.054932 | -0.004578 | 121.962 | 121.9437 | 121.8887 | 0.23346 | 0.17853 | 0.27466 | 0.10529 | 0.25177 | 0.13275 | 0.1236 | 0.082397 | 121.8155 | 121.7926 | -0.15564 | -0.13733 | 121.7972 | 121.843 | 121.7194 | 121.8567
1207.375 | 122.0032 | -121.7285 | 0.10529 | -0.011291 | 0.073196 | 0.012476 | 0.030162 | -0.00083525 | -0.0044646 | -0.00079691 | -0.0076599 | 0.0022175 | 0.017566 | 0.0031509 | 0.00097195 | 0.01988 | 2.068e-06 | -0.036621 | 0.059509 | 0 | 0.004578 | 0.18768 | 0.022888 | 0.059509 | 0.059509 | 0.041199 | -0.004578 | 0.07782 | 0.15106 | 0.086975 | 0.1831 | 121.7285 | -0.045777 | -0.10071 | 121.9162 | 121.788 | 121.7514 | 0.059509 | 0.022888 | 121.7239 | -0.064087 | -0.027466 | 121.8796 | 121.9116 | 121.8155 | 0.18768 | 0.091553 | 0.18768 | 0.004578 | 0.15564 | 0.082398 | 0.059509 | 0.045777 | 121.788 | 121.7697 | -0.10529 | -0.10986 | 121.7331 | 121.8063 | 121.6919 | 121.788
1209.0625 | 122.0215 | -121.7377 | 0.13275 | -0.011291 | 0.074478 | 0.013757 | 0.03123 | -0.00019445 | -0.0044646 | -0.0016513 | -0.0076599 | 0.0022175 | 0.020984 | 0.0040055 | -0.00030965 | 0.019025 | -0.0012795 | -0.059509 | 0.086975 | -0.032043 | -0.013733 | 0.10986 | 0.004578 | 0.032043 | 0.004578 | 0.10071 | -0.045776 | 0.050354 | 0.12817 | 0.07782 | 0.17853 | 121.7056 | -0.045776 | -0.14648 | 121.8475 | 121.7697 | 121.7422 | 0.064086 | 0.036621 | 121.6919 | -0.032043 | -0.082397 | 121.8658 | 121.9162 | 121.8155 | 0.2243 | 0.1236 | 0.14191 | 0.01831 | 0.17395 | 0.09613 | 0.11902 | 0.14648 | 121.8246 | 121.8384 | -0.16479 | -0.17853 | 121.7239 | 121.788 | 121.6782 | 121.7422
1210.7969 | 122.0078 | -121.7102 | 0.1236 | -0.0036622 | 0.075332 | 0.015253 | 0.034648 | -0.0010488 | -0.0029694 | 5.7688e-05 | 0.0014953 | 0.0032855 | 0.019916 | -0.0081711 | 0.00054475 | 0.019452 | -0.0042703 | -0.068665 | 0.09613 | -0.07782 | -0.050354 | 0.068665 | -0.050354 | -0.018311 | 0 | 0.091553 | -0.050354 | 0.064087 | 0.12817 | 0.045776 | 0.18768 | 121.6324 | -0.027466 | -0.17395 | 121.7789 | 121.6919 | 121.6599 | 0.059509 | 0.027466 | 121.6599 | -0.032043 | -0.059509 | 121.8384 | 121.8979 | 121.756 | 0.23804 | 0.09613 | 0.14649 | 0.027466 | 0.17853 | 0.11444 | 0.17395 | 0.14191 | 121.8063 | 121.8018 | -0.20142 | -0.17395 | 121.6599 | 121.7743 | 121.6415 | 121.7102
1212.5469 | 122.0398 | -121.7102 | 0.11902 | -0.041809 | 0.073837 | 0.016534 | 0.029093 | 0.00087375 | -0.0010468 | 0.00027129 | -0.0076599 | 0.0022175 | 0.017994 | -5.3326e-05 | 0.00033115 | 0.020307 | -0.0025613 | -0.004578 | 0.064087 | 0.004578 | 0.032043 | 0.19684 | 0.050354 | 0.064087 | 0.10071 | 0.045776 | 0 | 0.10529 | 0.17853 | 0.10986 | 0.21515 | 121.7148 | -0.054932 | -0.086976 | 121.907 | 121.7743 | 121.7606 | 0.059509 | 0.045776 | 121.7102 | -0.073243 | -0.013733 | 121.8887 | 121.9254 | 121.8201 | 0.21515 | 0.10986 | 0.19226 | 0.027465 | 0.17853 | 0.10529 | 0.059509 | 0.045776 | 121.7743 | 121.756 | -0.11444 | -0.11902 | 121.7422 | 121.8155 | 121.7056 | 121.8109
1214.2188 | 122.049 | -121.6919 | 0.082397 | 0.011597 | 0.075546 | 0.01568 | 0.032298 | -0.0012624 | -0.002542 | -0.0016513 | -0.0015565 | 0.0028583 | 0.018421 | -0.0041123 | 0.0016129 | 0.019452 | -0.0029885 | 0.013733 | 0.064087 | -0.027466 | 0.045776 | 0.18768 | 0.068665 | 0.064087 | 0.082397 | 0.036621 | -0.004578 | 0.12817 | 0.19684 | 0.10986 | 0.21515 | 121.6644 | -0.01831 | -0.036621 | 121.8796 | 121.756 | 121.7606 | 0.091553 | 0.096131 | 121.6873 | -0.045776 | 0.045777 | 121.8887 | 121.907 | 121.8018 | 0.21973 | 0.11444 | 0.21515 | 0.073242 | 0.20142 | 0.13275 | 0.091553 | 0.041199 | 121.756 | 121.7285 | -0.10986 | -0.086975 | 121.7377 | 121.8201 | 121.7056 | 121.7743
1215.9531 | 121.9208 | -121.8018 | 0.15564 | -0.011291 | 0.075546 | 0.015894 | 0.029948 | -0.0012624 | -0.0033966 | -0.0025057 | -0.0015565 | 0.0054217 | 0.020984 | -0.0088119 | -0.0062913 | 0.018171 | -0.0017069 | -0.041199 | 0.09613 | -0.073242 | -0.032043 | 0.086975 | 0.004578 | 0.009155 | -0.045776 | 0.11902 | -0.073242 | -0.013733 | 0.07782 | 0.009155 | 0.10986 | 121.7285 | -0.05951 | -0.18768 | 121.8887 | 121.8109 | 121.8063 | 0.082397 | 0.07782 | 121.7285 | -0.036621 | -0.16937 | 121.8796 | 121.9116 | 121.8109 | 0.18311 | 0.082397 | 0.16022 | 0.041199 | 0.15106 | 0.059509 | 0.16937 | 0.19226 | 121.8979 | 121.9208 | -0.22888 | -0.22888 | 121.7697 | 121.788 | 121.7606 | 121.756
1217.6406 | 122.0581 | -121.7651 | 0.10986 | 0.0039673 | 0.074691 | 0.012262 | 0.027812 | 0.0023692 | -0.0038238 | -0.0016513 | -0.0015565 | 0.0032855 | 0.019703 | -0.0062485 | -0.0018051 | 0.017316 | 0.00021567 | -0.032043 | 0.073242 | -0.022888 | 0.041199 | 0.17853 | 0.086975 | 0.10529 | 0.082397 | 0.059509 | -0.045776 | 0.10529 | 0.19684 | 0.1236 | 0.2243 | 121.7422 | -0.036621 | -0.068664 | 121.9437 | 121.8704 | 121.8521 | 0.12817 | 0.10986 | 121.7194 | -0.050354 | -0.004577 | 121.962 | 121.9894 | 121.8887 | 0.27008 | 0.16937 | 0.20142 | 0.064087 | 0.24261 | 0.15106 | 0.09613 | 0.10528 | 121.8384 | 121.8246 | -0.13275 | -0.15564 | 121.8063 | 121.8704 | 121.7331 | 121.8475
1219.375 | 122.0581 | -121.6919 | 0.11902 | -0.011291 | 0.075546 | 0.015894 | 0.032511 | 0.0040782 | -0.0044646 | -0.0016513 | -0.0015565 | 0.0037127 | 0.017566 | 0.0025101 | 0.0031081 | 0.02223 | -0.0023477 | -0.009155 | 0.082397 | -0.022888 | 0.032043 | 0.15564 | 0.041199 | 0.068665 | 0.082397 | 0.086975 | -0.036621 | 0.12817 | 0.19226 | 0.10071 | 0.23346 | 121.669 | -0.036622 | -0.086976 | 121.8475 | 121.7606 | 121.7331 | 0.091553 | 0.064087 | 121.6553 | -0.032044 | 0.009155 | 121.8842 | 121.9254 | 121.7926 | 0.27008 | 0.13733 | 0.17853 | 0.054931 | 0.22888 | 0.1648 | 0.10528 | 0.1236 | 121.7743 | 121.7789 | -0.14191 | -0.15564 | 121.7239 | 121.8201 | 121.6827 | 121.7743
1221.125 | 122.0673 | -121.7285 | 0.09613 | -0.03418 | 0.07405 | 0.016321 | 0.030162 | -0.0010488 | -0.0019012 | -0.0029331 | -0.0076599 | 0.0041401 | 0.018634 | 0.0040055 | 0.00011755 | 0.019452 | 0.0017111 | -0.018311 | 0.050354 | -0.009155 | 0.045776 | 0.19226 | 0.041199 | 0.068665 | 0.09613 | 0.064087 | -0.032043 | 0.11444 | 0.18768 | 0.11902 | 0.21515 | 121.7194 | -0.045776 | -0.050354 | 121.9208 | 121.7972 | 121.7697 | 0.07782 | 0.050354 | 121.6965 | -0.032043 | 0.018311 | 121.9162 | 121.9437 | 121.8475 | 0.24719 | 0.15106 | 0.20142 | 0.054931 | 0.21973 | 0.14648 | 0.059509 | 0.09613 | 121.7789 | 121.7926 | -0.10528 | -0.12817 | 121.7743 | 121.843 | 121.7102 | 121.8246
1222.8906 | 121.9254 | -121.7789 | 0.14191 | 0.0039673 | 0.077896 | 0.014398 | 0.030802 | 0.001301 | -0.0038238 | 0.0015531 | 0.0014953 | 0.0056355 | 0.018848 | -0.0088119 | -0.0020187 | 0.016248 | -0.0032021 | -0.059509 | 0.10529 | -0.07782 | -0.050354 | 0.068665 | -0.068665 | -0.036621 | -0.041199 | 0.10071 | -0.059509 | -0.013733 | 0.041199 | -0.041199 | 0.10071 | 121.701 | -0.036621 | -0.19226 | 121.8475 | 121.7422 | 121.7102 | 0.041199 | 0.009155 | 121.7194 | -0.041199 | -0.15564 | 121.8201 | 121.8796 | 121.7377 | 0.16022 | 0.01831 | 0.14649 | 0.027466 | 0.10071 | 0.045776 | 0.18311 | 0.16022 | 121.8842 | 121.8796 | -0.21973 | -0.20142 | 121.7285 | 121.7651 | 121.7194 | 121.7377
1224.5625 | 121.9025 | -121.7697 | 0.14648 | -0.0036622 | 0.076187 | 0.014185 | 0.032725 | 0.0042918 | -0.0019012 | 0.00091209 | -0.0046081 | 0.0043537 | 0.019916 | 0.00080107 | -0.0015915 | 0.018598 | -0.0032021 | -0.091553 | 0.10986 | -0.068665 | -0.086975 | 0.036621 | -0.082397 | -0.054932 | -0.091553 | 0.11902 | -0.068665 | -0.027466 | 0.027466 | -0.059509 | 0.09613 | 121.701 | -0.036621 | -0.23346 | 121.8063 | 121.7148 | 121.6873 | 0.013733 | -0.013732 | 121.701 | -0.027465 | -0.17395 | 121.7972 | 121.8658 | 121.7102 | 0.16479 | 0.009156 | 0.10529 | -0.01831 | 0.096131 | 0.041199 | 0.17853 | 0.18768 | 121.8796 | 121.8887 | -0.21515 | -0.21515 | 121.6827 | 121.7422 | 121.6782 | 121.6782
1226.2969 | 121.9894 | -121.7285 | 0.11444 | -0.011291 | 0.072982 | 0.01568 | 0.030375 | -0.0012624 | -0.0036102 | -0.0014377 | -0.0076599 | 0.0026447 | 0.019062 | -0.0026169 | -0.0026597 | 0.021589 | -0.0019205 | -0.064087 | 0.082397 | -0.022888 | -0.022888 | 0.12817 | 0.027466 | 0.036621 | 0.009155 | 0.091553 | -0.022888 | 0.054932 | 0.13275 | 0.068665 | 0.16479 | 121.7056 | -0.032044 | -0.13733 | 121.8567 | 121.7651 | 121.756 | 0.059509 | 0.050354 | 121.7056 | -0.022888 | -0.059509 | 121.8613 | 121.8933 | 121.7972 | 0.18768 | 0.091553 | 0.15106 | 0 | 0.15564 | 0.07782 | 0.10528 | 0.11444 | 121.8109 | 121.8201 | -0.13733 | -0.13733 | 121.7056 | 121.7834 | 121.6644 | 121.7377
1228.0312 | 121.994 | -121.7468 | 0.1236 | -0.018921 | 0.076614 | 0.015466 | 0.030589 | -0.0023306 | -0.0019012 | -0.0018649 | -0.0046081 | 0.0026447 | 0.018207 | -0.0013351 | -0.00095065 | 0.019239 | -0.0014931 | -0.045776 | 0.07782 | -0.022888 | 0.004578 | 0.16022 | 0.018311 | 0.045776 | 0.032043 | 0.073242 | -0.022888 | 0.059509 | 0.11902 | 0.073242 | 0.17853 | 121.7239 | -0.045776 | -0.11902 | 121.907 | 121.7926 | 121.7651 | 0.068664 | 0.041199 | 121.7239 | -0.050354 | -0.064087 | 121.8658 | 121.9254 | 121.8201 | 0.20142 | 0.09613 | 0.1831 | 0.027466 | 0.14191 | 0.082397 | 0.10071 | 0.09613 | 121.8246 | 121.8201 | -0.14648 | -0.14648 | 121.7514 | 121.8063 | 121.701 | 121.7789
1229.7031 | 122.0398 | -121.7422 | 0.10529 | -0.011291 | 0.074905 | 0.015039 | 0.030375 | -0.001476 | -0.002542 | -0.0016513 | -0.0015565 | -0.00013254 | 0.019275 | -0.0032577 | -0.0026597 | 0.01753 | -0.0021341 | 0 | 0.073242 | -0.018311 | 0.054932 | 0.19684 | 0.10986 | 0.10071 | 0.10529 | 0.073242 | -0.022888 | 0.091553 | 0.20599 | 0.1236 | 0.19684 | 121.7239 | -0.032044 | -0.050354 | 121.9391 | 121.843 | 121.8521 | 0.11902 | 0.12817 | 121.7194 | -0.032044 | -0.013733 | 121.9482 | 121.9391 | 121.8658 | 0.21973 | 0.14648 | 0.21515 | 0.073243 | 0.22888 | 0.11444 | 0.091553 | 0.09613 | 121.8155 | 121.8155 | -0.1236 | -0.12817 | 121.7972 | 121.8338 | 121.7422 | 121.8475
1231.4531 | 121.9711 | -121.7514 | 0.1236 | 0.0039673 | 0.073837 | 0.014185 | 0.031871 | 0.0038644 | -0.0023284 | -0.0025057 | -0.0046081 | 0.0047809 | 0.020984 | -0.0021897 | -0.0026597 | 0.01753 | -0.00021153 | -0.045776 | 0.10071 | -0.045776 | -0.018311 | 0.1236 | 0.004578 | 0.027466 | 0.022888 | 0.09613 | -0.050354 | 0.036621 | 0.1236 | 0.041199 | 0.16022 | 121.7056 | -0.022888 | -0.14191 | 121.875 | 121.7789 | 121.756 | 0.073242 | 0.050354 | 121.701 | -0.027466 | -0.086975 | 121.875 | 121.9116 | 121.7926 | 0.21057 | 0.091553 | 0.16937 | 0.027465 | 0.17395 | 0.086975 | 0.14648 | 0.14648 | 121.8521 | 121.8475 | -0.16937 | -0.17395 | 121.7331 | 121.788 | 121.7056 | 121.7743
1233.1406 | 122.0123 | -121.7606 | 0.1236 | 0.0039673 | 0.071914 | 0.014185 | 0.02653 | -0.00040805 | -0.00083304 | -0.00036951 | -0.0015565 | 0.0017901 | 0.018421 | 0.0012283 | -0.0043687 | 0.017957 | 0.0029929 | -0.013733 | 0.064087 | -0.022888 | 0.041199 | 0.1831 | 0.091553 | 0.091553 | 0.068665 | 0.091553 | -0.041199 | 0.059509 | 0.16479 | 0.073242 | 0.16479 | 121.7377 | -0.059509 | -0.082397 | 121.9437 | 121.8521 | 121.8521 | 0.11444 | 0.11444 | 121.7194 | -0.032043 | -0.064087 | 121.9254 | 121.9254 | 121.8338 | 0.20599 | 0.11444 | 0.20599 | 0.064087 | 0.20599 | 0.10071 | 0.086975 | 0.13275 | 121.8246 | 121.8521 | -0.14648 | -0.16479 | 121.8018 | 121.8201 | 121.7468 | 121.8292
1234.875 | 121.9803 | -121.7468 | 0.15106 | -0.02655 | 0.07405 | 0.01568 | 0.034434 | -0.0027578 | -0.0010468 | -0.0027195 | -0.0076599 | 0.0056355 | 0.017994 | -0.0045395 | -0.00095065 | 0.016889 | -0.0019205 | -0.045776 | 0.10986 | -0.045776 | -0.022888 | 0.1236 | 0.009155 | 0.022888 | 0.009155 | 0.091553 | -0.050354 | 0.059509 | 0.13275 | 0.045776 | 0.16022 | 121.701 | -0.041199 | -0.17395 | 121.8704 | 121.7697 | 121.756 | 0.068664 | 0.054931 | 121.6965 | -0.059509 | -0.091553 | 121.8796 | 121.907 | 121.7926 | 0.21057 | 0.09613 | 0.16937 | 0.022888 | 0.18311 | 0.10986 | 0.15564 | 0.14191 | 121.8567 | 121.8384 | -0.19684 | -0.20142 | 121.7239 | 121.8063 | 121.701 | 121.756
1236.5469 | 121.962 | -121.7331 | 0.13275 | -0.0036622 | 0.075973 | 0.013757 | 0.031016 | 0.00301 | -0.001474 | -0.0014377 | -0.0046081 | 0.0037127 | 0.016498 | -0.0077439 | -0.0011643 | 0.017957 | -0.0027749 | -0.045776 | 0.09613 | -0.059509 | -0.036621 | 0.11902 | 0.004578 | 0.013733 | 0.013733 | 0.10986 | -0.045776 | 0.041199 | 0.11444 | 0.045776 | 0.15106 | 121.6736 | -0.036621 | -0.16937 | 121.8521 | 121.7468 | 121.7377 | 0.073242 | 0.064087 | 121.6873 | -0.022888 | -0.091552 | 121.8475 | 121.8842 | 121.7789 | 0.19684 | 0.091552 | 0.17853 | 0.022888 | 0.16022 | 0.086975 | 0.15564 | 0.15564 | 121.8292 | 121.843 | -0.19226 | -0.17853 | 121.6965 | 121.7743 | 121.6873 | 121.7468
1238.2969 | 121.9711 | -121.7377 | 0.12817 | -0.0036622 | 0.075118 | 0.01568 | 0.032084 | -0.003826 | -0.0036102 | -0.0031467 | -0.0015565 | 0.0026447 | 0.018634 | -0.0079575 | 0.00054475 | 0.020307 | 0.0010703 | -0.07782 | 0.09613 | -0.064087 | -0.07782 | 0.050354 | -0.068665 | -0.022888 | -0.013733 | 0.10071 | -0.041199 | 0.041199 | 0.11444 | 0.027466 | 0.15564 | 121.6736 | -0.032044 | -0.20599 | 121.788 | 121.7148 | 121.669 | 0.041199 | -0.004578 | 121.6965 | -0.027466 | -0.086975 | 121.8521 | 121.8933 | 121.7651 | 0.19684 | 0.068665 | 0.11444 | -0.013733 | 0.15564 | 0.082398 | 0.16022 | 0.14191 | 121.8338 | 121.8384 | -0.19226 | -0.16937 | 121.6599 | 121.7789 | 121.6599 | 121.7239
1239.9688 | 122.0123 | -121.7056 | 0.10986 | -0.03418 | 0.074264 | 0.015253 | 0.030802 | 0.00023275 | -0.002542 | -0.0035739 | -0.0076599 | 0.0024311 | 0.017994 | 0.0016555 | -0.00052345 | 0.019452 | -0.0044839 | -0.050354 | 0.064087 | -0.027466 | -0.009155 | 0.17395 | 0.027466 | 0.050354 | 0.068665 | 0.073242 | -0.032043 | 0.07782 | 0.14191 | 0.059509 | 0.16937 | 121.6782 | -0.045776 | -0.11902 | 121.8796 | 121.756 | 121.7331 | 0.07782 | 0.054932 | 121.6736 | -0.036621 | -0.032043 | 121.8475 | 121.875 | 121.7651 | 0.20142 | 0.091552 | 0.20142 | 0.018311 | 0.17395 | 0.10986 | 0.091553 | 0.10529 | 121.7697 | 121.7789 | -0.13733 | -0.14191 | 121.6965 | 121.7834 | 121.6553 | 121.7743
1241.7031 | 121.9711 | -121.7651 | 0.13733 | -0.02655 | 0.075118 | 0.013544 | 0.031657 | 0.0015146 | -0.004251 | -0.0018649 | -0.010712 | 0.0028583 | 0.020343 | -0.0075301 | -0.0018051 | 0.017957 | -0.00021153 | -0.064087 | 0.10071 | -0.068665 | -0.064087 | 0.07782 | -0.009155 | 0.004578 | -0.022888 | 0.09613 | -0.064087 | 0.027466 | 0.11444 | 0.022888 | 0.14648 | 121.6965 | -0.036621 | -0.20142 | 121.843 | 121.7697 | 121.756 | 0.073243 | 0.05951 | 121.701 | -0.041199 | -0.10986 | 121.8796 | 121.9116 | 121.788 | 0.21057 | 0.086975 | 0.14649 | 0.004578 | 0.17853 | 0.091553 | 0.16937 | 0.16022 | 121.8658 | 121.8613 | -0.20599 | -0.20142 | 121.701 | 121.7926 | 121.701 | 121.7422
1243.3906 | 122.0169 | -121.7148 | 0.10071 | -0.011291 | 0.074478 | 0.014185 | 0.031657 | 0.001301 | -0.0036102 | -0.0027195 | -0.0046081 | 0.0034991 | 0.01778 | 0.00080107 | -0.00030965 | 0.018812 | -0.0014931 | -0.064087 | 0.10529 | -0.064087 | -0.045776 | 0.086975 | -0.032043 | 0.013733 | 0.013733 | 0.07782 | -0.027466 | 0.086975 | 0.14648 | 0.068665 | 0.19684 | 121.6507 | 0.004578 | -0.14648 | 121.8018 | 121.7285 | 121.6827 | 0.07782 | 0.032044 | 121.6873 | -0.022888 | -0.013733 | 121.8613 | 121.9116 | 121.7834 | 0.2243 | 0.096131 | 0.15106 | 0.018311 | 0.17395 | 0.11444 | 0.16937 | 0.10529 | 121.8201 | 121.7926 | -0.1648 | -0.12817 | 121.669 | 121.8018 | 121.6507 | 121.7285
1245.125 | 121.962 | -121.7422 | 0.12817 | -0.0036622 | 0.075118 | 0.017389 | 0.033579 | 1.915e-05 | 0.00023496 | 5.7688e-05 | -0.0015565 | 0.0032855 | 0.019916 | -0.011162 | -0.0028733 | 0.019239 | -0.0032021 | -0.086975 | 0.10529 | -0.064087 | -0.073242 | 0.054932 | -0.068665 | -0.027466 | -0.036621 | 0.10529 | -0.059509 | 0.036621 | 0.086975 | 0.018311 | 0.14648 | 121.6782 | -0.022888 | -0.20142 | 121.7972 | 121.7148 | 121.6736 | 0.036621 | -0.004578 | 121.6827 | -0.022888 | -0.091553 | 121.8292 | 121.8887 | 121.7606 | 0.20599 | 0.07782 | 0.11902 | -0.009155 | 0.14648 | 0.09613 | 0.16937 | 0.16479 | 121.8475 | 121.8475 | -0.19226 | -0.18768 | 121.669 | 121.7789 | 121.6553 | 121.7056
1246.875 | 122.081 | -121.7148 | 0.10529 | -0.0036622 | 0.074264 | 0.01568 | 0.029093 | -0.0036124 | -0.0029694 | 0.0011257 | -0.0015565 | 0.0032855 | 0.019489 | 0.0014419 | -0.0050095 | 0.018171 | -0.0027749 | -0.013733 | 0.064087 | -0.022888 | 0.064087 | 0.23804 | 0.10986 | 0.11444 | 0.13275 | 0.09613 | -0.036621 | 0.10071 | 0.21057 | 0.13733 | 0.20599 | 121.6919 | -0.041199 | -0.041199 | 121.9528 | 121.8292 | 121.8246 | 0.13733 | 0.13275 | 121.6782 | -0.009156 | -0.004578 | 121.9254 | 121.9208 | 121.8521 | 0.24262 | 0.17395 | 0.26093 | 0.086975 | 0.24719 | 0.13733 | 0.086975 | 0.13275 | 121.7789 | 121.8109 | -0.12817 | -0.14191 | 121.7789 | 121.8155 | 121.701 | 121.8475
1248.5625 | 122.0123 | -121.7468 | 0.1236 | -0.018921 | 0.072128 | 0.015253 | 0.029521 | -0.0016898 | -0.0038238 | -0.0018649 | -0.0046081 | 0.0020039 | 0.017566 | -5.3326e-05 | -0.0045823 | 0.018598 | -0.00063873 | -0.018311 | 0.064087 | -0.036621 | 0.050354 | 0.20142 | 0.091553 | 0.082397 | 0.064087 | 0.068665 | -0.027466 | 0.064087 | 0.16479 | 0.10071 | 0.18768 | 121.7102 | -0.059509 | -0.073242 | 121.9482 | 121.8292 | 121.8384 | 0.11902 | 0.12817 | 121.7194 | -0.054931 | -0.059509 | 121.9116 | 121.9345 | 121.8475 | 0.21515 | 0.12817 | 0.23804 | 0.086975 | 0.19226 | 0.091553 | 0.10071 | 0.096131 | 121.8109 | 121.8155 | -0.16022 | -0.15106 | 121.7972 | 121.8109 | 121.7285 | 121.8109
1250.2969 | 122.0398 | -121.7056 | 0.10986 | -0.011291 | 0.073837 | 0.01568 | 0.02888 | -0.003826 | -0.0019012 | -0.0014377 | -0.0076599 | 0.0022175 | 0.018421 | -0.0036849 | 0.0013991 | 0.016889 | 0.0017111 | -0.018311 | 0.059509 | -0.013733 | 0.032043 | 0.17853 | 0.041199 | 0.073242 | 0.09613 | 0.064087 | 0 | 0.09613 | 0.16937 | 0.10986 | 0.21515 | 121.6919 | -0.050354 | -0.07782 | 121.8842 | 121.7789 | 121.7468 | 0.086975 | 0.054932 | 121.7056 | -0.045776 | -0.013733 | 121.875 | 121.9208 | 121.8155 | 0.21515 | 0.10986 | 0.19226 | 0.045776 | 0.16937 | 0.09613 | 0.073242 | 0.064087 | 121.7651 | 121.7697 | -0.1236 | -0.10986 | 121.7377 | 121.8018 | 121.6873 | 121.8018
1252.0312 | 122.081 | -121.7331 | 0.11444 | -0.011291 | 0.073837 | 0.013757 | 0.029948 | -0.0027578 | -0.0023284 | 0.00048489 | 0.0014953 | 0.0020039 | 0.018207 | 0.0046463 | -0.0028733 | 0.018171 | -0.0014931 | -0.027466 | 0.073242 | -0.027466 | 0.054932 | 0.23804 | 0.11444 | 0.10071 | 0.10986 | 0.073242 | -0.009155 | 0.09613 | 0.2243 | 0.14648 | 0.21057 | 121.7056 | -0.041199 | -0.059509 | 121.9711 | 121.8338 | 121.8475 | 0.12817 | 0.14191 | 121.7239 | -0.041199 | -0.018311 | 121.9574 | 121.9437 | 121.8796 | 0.21973 | 0.15564 | 0.2655 | 0.082398 | 0.23346 | 0.10528 | 0.10071 | 0.082397 | 121.8063 | 121.8063 | -0.14191 | -0.1236 | 121.788 | 121.8292 | 121.7056 | 121.843
1253.7656 | 122.0535 | -121.7285 | 0.10071 | -0.02655 | 0.07405 | 0.015253 | 0.032511 | -0.0010488 | -0.0021148 | -0.0022921 | -0.0076599 | 0.0024311 | 0.017139 | -0.0073165 | -0.00073705 | 0.018384 | -0.00021153 | -0.022888 | 0.068665 | -0.032043 | 0.036621 | 0.20599 | 0.082397 | 0.11444 | 0.11902 | 0.059509 | -0.018311 | 0.11444 | 0.21515 | 0.14648 | 0.2243 | 121.6965 | -0.032043 | -0.064087 | 121.9345 | 121.843 | 121.8109 | 0.14648 | 0.11444 | 121.7102 | -0.041199 | 0.013733 | 121.9437 | 121.9528 | 121.875 | 0.24261 | 0.16479 | 0.23804 | 0.068664 | 0.23346 | 0.13275 | 0.10071 | 0.07782 | 121.7972 | 121.788 | -0.13275 | -0.11902 | 121.7651 | 121.843 | 121.7056 | 121.8475
1255.4375 | 121.962 | -121.756 | 0.12817 | -0.011291 | 0.073837 | 0.013757 | 0.031871 | -0.00040805 | -0.0044646 | -0.00079691 | -0.010712 | 0.0049945 | 0.019703 | 0.0014419 | -0.0020187 | 0.019452 | -0.00042513 | -0.07782 | 0.10529 | -0.054932 | -0.064087 | 0.045776 | -0.032043 | -0.022888 | -0.050354 | 0.09613 | -0.068665 | 0.009155 | 0.09613 | -0.004578 | 0.13275 | 121.701 | -0.022888 | -0.19226 | 121.8018 | 121.7331 | 121.7239 | 0.032044 | 0.022889 | 121.6873 | -0.032044 | -0.11902 | 121.8521 | 121.8887 | 121.7514 | 0.20142 | 0.064087 | 0.10071 | -0.009155 | 0.16479 | 0.07782 | 0.16022 | 0.16479 | 121.8613 | 121.8521 | -0.18311 | -0.19684 | 121.6919 | 121.7651 | 121.6782 | 121.7056
1257.1094 | 122.0352 | -121.7285 | 0.10986 | -0.0036622 | 0.070846 | 0.013544 | 0.031871 | 0.0021556 | -0.00061944 | -0.0029331 | -0.0015565 | 0.0045673 | 0.018848 | -0.0036849 | 0.00033115 | 0.018812 | 0.00085667 | -0.086975 | 0.09613 | -0.050354 | -0.054932 | 0.086975 | -0.032043 | 0.009155 | 0.022888 | 0.073242 | -0.041199 | 0.091553 | 0.14648 | 0.073242 | 0.21515 | 121.6782 | -0.013733 | -0.16479 | 121.8155 | 121.7377 | 121.6965 | 0.059509 | 0.018311 | 121.6873 | -0.036621 | -0.01831 | 121.875 | 121.9437 | 121.8018 | 0.25635 | 0.11444 | 0.13733 | -0.004578 | 0.18768 | 0.13275 | 0.14648 | 0.11444 | 121.8246 | 121.8018 | -0.16022 | -0.15106 | 121.6736 | 121.8201 | 121.6415 | 121.7514
1258.8438 | 121.9528 | -121.7514 | 0.13733 | 0.0039673 | 0.076827 | 0.013116 | 0.033366 | -0.0029714 | 2.1362e-05 | -0.0016513 | -0.0046081 | 0.0041401 | 0.019275 | -0.0043259 | -0.0033005 | 0.018384 | -0.00085233 | -0.07782 | 0.10071 | -0.068665 | -0.091553 | 0.045776 | -0.064087 | -0.027466 | -0.050354 | 0.10529 | -0.054932 | 0.013733 | 0.064087 | -0.009155 | 0.12817 | 121.6827 | -0.036621 | -0.22888 | 121.7972 | 121.7239 | 121.6873 | 0.041199 | 0.004578 | 121.6965 | -0.032043 | -0.1236 | 121.8155 | 121.8796 | 121.7422 | 0.18311 | 0.045777 | 0.11444 | -0.022888 | 0.11902 | 0.068665 | 0.16937 | 0.16022 | 121.8521 | 121.8567 | -0.20599 | -0.19226 | 121.6599 | 121.7651 | 121.6736 | 121.701
1260.5781 | 121.907 | -121.7514 | 0.13733 | -0.0036622 | 0.075973 | 0.015894 | 0.032298 | -0.003826 | -0.0023284 | -0.0025057 | -0.0015565 | 0.0049945 | 0.019062 | -0.0060349 | -0.0015915 | 0.018812 | -0.0076883 | -0.086975 | 0.10071 | -0.064087 | -0.082397 | 0.022888 | -0.082397 | -0.041199 | -0.10071 | 0.10529 | -0.059509 | -0.013733 | 0.041199 | -0.045776 | 0.10529 | 121.6873 | -0.036621 | -0.21973 | 121.7743 | 121.7102 | 121.669 | 0.022888 | -0.01831 | 121.6919 | -0.032043 | -0.15106 | 121.7926 | 121.8567 | 121.7056 | 0.16479 | 0.013733 | 0.086975 | -0.01831 | 0.10071 | 0.045776 | 0.1648 | 0.16479 | 121.8521 | 121.8567 | -0.20142 | -0.19684 | 121.669 | 121.7377 | 121.6644 | 121.6507
1262.3125 | 122.0169 | -121.7606 | 0.12817 | -0.0036622 | 0.074478 | 0.014398 | 0.032298 | 0.00044655 | -0.0019012 | -0.00015591 | -0.0015565 | 0.0028583 | 0.018848 | -0.0058213 | 0.00054475 | 0.017957 | -0.0014931 | -0.086975 | 0.10071 | -0.059509 | -0.073242 | 0.073242 | -0.059509 | 0 | -0.004578 | 0.09613 | -0.045776 | 0.059509 | 0.13275 | 0.050354 | 0.17853 | 121.701 | -0.027466 | -0.20142 | 121.8338 | 121.7606 | 121.701 | 0.059509 | 0 | 121.7148 | -0.032044 | -0.068665 | 121.8933 | 121.9391 | 121.8109 | 0.2243 | 0.09613 | 0.13275 | -0.013733 | 0.17853 | 0.10528 | 0.16022 | 0.14191 | 121.8613 | 121.8567 | -0.18768 | -0.17395 | 121.6873 | 121.8201 | 121.6736 | 121.756
1263.9844 | 122.049 | -121.7468 | 0.11902 | -0.0036622 | 0.072341 | 0.013544 | 0.029948 | 0.001301 | -0.0036102 | -0.0037875 | -0.0015565 | 0.0024311 | 0.019062 | -0.00069433 | -0.0020187 | 0.01988 | 0.0036337 | -0.068665 | 0.082397 | -0.045776 | -0.013733 | 0.14648 | 0.032043 | 0.050354 | 0.027466 | 0.073242 | -0.041199 | 0.082397 | 0.16022 | 0.10529 | 0.1831 | 121.701 | -0.036622 | -0.13275 | 121.8933 | 121.7972 | 121.7789 | 0.09613 | 0.077819 | 121.7056 | -0.045777 | -0.036622 | 121.907 | 121.9299 | 121.8521 | 0.2243 | 0.14649 | 0.19226 | 0.032043 | 0.20142 | 0.1236 | 0.12817 | 0.11444 | 121.8292 | 121.8201 | -0.16479 | -0.16022 | 121.7331 | 121.8292 | 121.6782 | 121.7743
1265.7188 | 122.0123 | -121.7422 | 0.10071 | -0.03418 | 0.07405 | 0.016107 | 0.030162 | 0.0034372 | -0.0019012 | -0.0050693 | -0.0076599 | 0.0017901 | 0.018421 | -0.0053939 | -0.0045823 | 0.019025 | 0.0061973 | -0.050354 | 0.064087 | -0.009155 | -0.009155 | 0.14191 | 0.022888 | 0.054932 | 0.009155 | 0.068665 | -0.041199 | 0.064087 | 0.13733 | 0.07782 | 0.17395 | 121.7331 | -0.036621 | -0.10986 | 121.8842 | 121.7972 | 121.7651 | 0.064087 | 0.032043 | 121.701 | -0.032043 | -0.036621 | 121.8796 | 121.9162 | 121.8201 | 0.21515 | 0.11902 | 0.15106 | 0 | 0.17853 | 0.10529 | 0.073242 | 0.10986 | 121.8063 | 121.8109 | -0.10986 | -0.14191 | 121.7331 | 121.8063 | 121.6919 | 121.7514
1267.4531 | 122.0535 | -121.7285 | 0.10529 | -0.018921 | 0.074691 | 0.014612 | 0.030802 | -0.00040805 | -0.0027556 | 0.0011257 | -0.0046081 | 0.0017901 | 0.019489 | -0.0013351 | -0.0028733 | 0.019239 | 0.00042947 | -0.045776 | 0.073242 | -0.041199 | 0.022888 | 0.17853 | 0.07782 | 0.091553 | 0.059509 | 0.073242 | -0.018311 | 0.10529 | 0.20142 | 0.13733 | 0.21515 | 121.6873 | -0.032044 | -0.082398 | 121.907 | 121.8201 | 121.8063 | 0.13275 | 0.11902 | 121.7102 | -0.032044 | 0 | 121.9299 | 121.9437 | 121.8658 | 0.23346 | 0.15564 | 0.21973 | 0.064087 | 0.21973 | 0.1236 | 0.11444 | 0.091553 | 121.8018 | 121.8018 | -0.14649 | -0.1236 | 121.7514 | 121.8338 | 121.6827 | 121.788
1269.1875 | 122.0078 | -121.7331 | 0.12817 | -0.011291 | 0.074264 | 0.01333 | 0.030162 | -0.0029714 | -0.0038238 | -0.0014377 | -0.0015565 | 0.0024311 | 0.017353 | -0.00048073 | -0.0033005 | 0.017316 | -0.0036295 | -0.004578 | 0.059509 | -0.027466 | 0.050354 | 0.19226 | 0.10071 | 0.09613 | 0.073242 | 0.086975 | -0.018311 | 0.073242 | 0.19226 | 0.11902 | 0.19684 | 121.7056 | -0.068665 | -0.07782 | 121.9254 | 121.8292 | 121.8338 | 0.1236 | 0.12817 | 121.7148 | -0.041199 | -0.054932 | 121.9254 | 121.9299 | 121.8521 | 0.21515 | 0.13733 | 0.21973 | 0.07782 | 0.21057 | 0.091553 | 0.086975 | 0.10529 | 121.7926 | 121.8201 | -0.15564 | -0.14649 | 121.7834 | 121.8063 | 121.7285 | 121.8063
1270.9531 | 121.9666 | -121.7697 | 0.1236 | -0.018921 | 0.074478 | 0.013544 | 0.032939 | 0.001301 | -0.0044646 | 0.00091209 | -0.010712 | 0.0037127 | 0.017566 | -0.010948 | -0.0026597 | 0.017316 | -0.0034159 | -0.086975 | 0.10986 | -0.059509 | -0.068665 | 0.032043 | -0.032043 | -0.009155 | -0.082397 | 0.10071 | -0.036621 | 0.004578 | 0.082397 | 0 | 0.13275 | 121.7102 | -0.013733 | -0.19226 | 121.8018 | 121.7606 | 121.7377 | 0.050354 | 0.027466 | 121.7331 | -0.022888 | -0.11902 | 121.8521 | 121.9025 | 121.7697 | 0.16937 | 0.036621 | 0.091552 | -0.009156 | 0.11902 | 0.041199 | 0.16937 | 0.13733 | 121.8796 | 121.8704 | -0.1831 | -0.16022 | 121.701 | 121.7743 | 121.6827 | 121.6873
1272.6406 | 122.0306 | -121.7285 | 0.11902 | -0.02655 | 0.075118 | 0.014612 | 0.029307 | 0.0038644 | -0.0033966 | -0.0016513 | -0.010712 | 0.0028583 | 0.019489 | 0.00058747 | -0.00073705 | 0.018171 | -0.0017069 | -0.022888 | 0.041199 | -0.004578 | 0.045776 | 0.19684 | 0.045776 | 0.064087 | 0.082397 | 0.064087 | 0 | 0.10529 | 0.17853 | 0.10071 | 0.21515 | 121.7239 | -0.07782 | -0.073243 | 121.9254 | 121.7926 | 121.7743 | 0.068665 | 0.050354 | 121.7285 | -0.054932 | -0.013733 | 121.907 | 121.9437 | 121.8292 | 0.21515 | 0.10071 | 0.20142 | 0.050354 | 0.17853 | 0.10529 | 0.045777 | 0.064087 | 121.7697 | 121.7926 | -0.1236 | -0.11902 | 121.7743 | 121.8338 | 121.7056 | 121.8109
1274.3906 | 122.0627 | -121.7148 | 0.10986 | -0.0036622 | 0.074691 | 0.014398 | 0.030802 | -0.0029714 | -0.0033966 | -0.0012241 | -0.0015565 | 0.0022175 | 0.019062 | -0.0015487 | -0.0043687 | 0.017957 | -0.0014931 | -0.022888 | 0.064087 | -0.027466 | 0.054932 | 0.23346 | 0.11444 | 0.11444 | 0.11444 | 0.054932 | -0.036621 | 0.10529 | 0.21973 | 0.16937 | 0.2243 | 121.6873 | -0.045776 | -0.054931 | 121.9482 | 121.8292 | 121.8292 | 0.14191 | 0.14191 | 121.6782 | -0.054931 | -0.004577 | 121.9345 | 121.9391 | 121.8842 | 0.26093 | 0.20599 | 0.26093 | 0.082398 | 0.25635 | 0.14191 | 0.091553 | 0.091553 | 121.7789 | 121.7697 | -0.13733 | -0.14648 | 121.7697 | 121.8201 | 121.6919 | 121.8292
1276.0625 | 121.9986 | -121.7194 | 0.11902 | -0.011291 | 0.075759 | 0.013971 | 0.032298 | 0.00023275 | -0.003183 | -0.0022921 | -0.0046081 | 0.0030719 | 0.019275 | -0.0028305 | -0.0022325 | 0.018384 | 0.0023521 | 0.004578 | 0.059509 | -0.036621 | 0.059509 | 0.20142 | 0.091553 | 0.091553 | 0.068665 | 0.073242 | -0.032043 | 0.086975 | 0.19226 | 0.11444 | 0.19684 | 121.6827 | -0.05951 | -0.05951 | 121.9208 | 121.8109 | 121.8109 | 0.12817 | 0.12817 | 121.6873 | -0.045777 | -0.032044 | 121.9116 | 121.9162 | 121.8338 | 0.22888 | 0.14648 | 0.23804 | 0.09613 | 0.2243 | 0.11902 | 0.09613 | 0.10529 | 121.7789 | 121.7926 | -0.15564 | -0.15106 | 121.7789 | 121.8063 | 121.7239 | 121.788
1277.8125 | 122.0261 | -121.7194 | 0.11444 | -0.0036622 | 0.075546 | 0.014612 | 0.031443 | -0.0016898 | -0.0040374 | -0.0014377 | -0.0015565 | 0.0028583 | 0.019275 | 0.00037387 | -0.0039413 | 0.020521 | -0.0027749 | -0.054932 | 0.068665 | -0.045776 | 0.018311 | 0.16937 | 0.054932 | 0.091553 | 0.059509 | 0.07782 | -0.027466 | 0.086975 | 0.18768 | 0.1236 | 0.23346 | 121.6736 | -0.045776 | -0.09613 | 121.8887 | 121.8109 | 121.7743 | 0.13733 | 0.10071 | 121.6919 | -0.036621 | -0.027466 | 121.907 | 121.9528 | 121.843 | 0.26093 | 0.15106 | 0.21515 | 0.064087 | 0.21515 | 0.11444 | 0.11444 | 0.10529 | 121.788 | 121.7972 | -0.16022 | -0.14191 | 121.7377 | 121.8063 | 121.6644 | 121.7789
1279.5625 | 121.994 | -121.7239 | 0.09613 | -0.02655 | 0.075546 | 0.015466 | 0.033366 | -0.0029714 | -0.0016876 | -0.0025057 | -0.0046081 | 0.0015765 | 0.019703 | -0.0038987 | 0.00097195 | 0.018384 | -0.0032021 | -0.041199 | 0.045776 | -0.013733 | 0 | 0.16022 | 0.018311 | 0.041199 | 0.068665 | 0.07782 | -0.013733 | 0.073242 | 0.15106 | 0.073242 | 0.16937 | 121.7102 | -0.050354 | -0.09613 | 121.8842 | 121.7651 | 121.7422 | 0.054932 | 0.032044 | 121.7102 | -0.01831 | -0.022888 | 121.875 | 121.8933 | 121.7972 | 0.18311 | 0.086975 | 0.17395 | 0.013733 | 0.16479 | 0.086975 | 0.059509 | 0.091553 | 121.7697 | 121.8018 | -0.10986 | -0.10986 | 121.7239 | 121.7972 | 121.6827 | 121.7926
1281.2969 | 121.9803 | -121.7285 | 0.1236 | -0.011291 | 0.076614 | 0.017175 | 0.034648 | 0.0053598 | -0.0051056 | -0.00015591 | -0.010712 | 0.0037127 | 0.020343 | -0.012871 | -0.0015915 | 0.016034 | -0.00063873 | -0.022888 | 0.091553 | -0.041199 | -0.032043 | 0.10529 | 0.004578 | 0.018311 | 0.032043 | 0.11444 | -0.041199 | 0.045776 | 0.11902 | 0.032043 | 0.15106 | 121.6873 | -0.032043 | -0.15564 | 121.8338 | 121.7468 | 121.7331 | 0.05951 | 0.045777 | 121.6873 | -0.009155 | -0.07782 | 121.8475 | 121.8796 | 121.7606 | 0.19226 | 0.073242 | 0.14649 | 0.009156 | 0.16022 | 0.086975 | 0.13275 | 0.15564 | 121.8201 | 121.843 | -0.16479 | -0.16479 | 121.6965 | 121.7743 | 121.7056 | 121.7606
1282.9844 | 121.8933 | -121.7285 | 0.13733 | -0.0036622 | 0.077468 | 0.016534 | 0.033579 | 0.0015146 | -0.00083304 | 0.0034757 | -0.0046081 | 0.0056355 | 0.021412 | -0.0098801 | -0.0022325 | 0.017103 | 0.0021383 | -0.050354 | 0.10529 | -0.050354 | -0.041199 | 0.07782 | -0.032043 | -0.018311 | -0.036621 | 0.10986 | -0.036621 | 0 | 0.059509 | -0.022888 | 0.10071 | 121.6782 | -0.032043 | -0.17853 | 121.8063 | 121.7102 | 121.6965 | 0.032043 | 0.018311 | 121.6919 | -0.027466 | -0.13733 | 121.788 | 121.8292 | 121.7056 | 0.13733 | 0.013733 | 0.12817 | 0.009155 | 0.09613 | 0.036621 | 0.15564 | 0.14648 | 121.8338 | 121.8384 | -0.18768 | -0.17395 | 121.6873 | 121.7285 | 121.6782 | 121.6919
1284.7344 | 121.8155 | -120.8679 | 0.79651 | 0.0039673 | 0.96358 | 0.014825 | 0.70414 | -0.00083525 | -0.002542 | 0.00091209 | -0.0046081 | 0.012685 | 0.016712 | 0.0078507 | -0.0022325 | 0.018812 | -0.0021341 | 0.27008 | 0.56763 | 0.3067 | 0.69122 | 0.58594 | 0.39825 | 0.40283 | 0.66376 | 0.70038 | 0.5722 | 1.1124 | 0.94757 | 0.71869 | 0.81024 | 121.1746 | -0.22888 | -0.10529 | 121.4539 | 121.2708 | 121.2662 | 0.09613 | 0.091552 | 121.4401 | -0.096131 | 0.31586 | 121.8155 | 121.6782 | 121.5866 | 0.23804 | 0.14648 | 0.27924 | 0.38452 | 0.37537 | 0.54016 | 0.26093 | 0.12817 | 121.4355 | 121.5683 | -0.48981 | -0.2243 | 121.5591 | 121.9803 | 121.138 | 121.5317
1286.4844 | 121.4813 | -9.1187 | 112.5916 | 0.011597 | 0.068496 | 0.013971 | 0.022257 | 0.00087375 | -0.0019012 | -0.0027195 | 0.0045471 | 0.025075 | 0.017994 | 0.013832 | -0.0030869 | 0.017743 | -0.0049111 | -0.12817 | 0.032043 | -0.14191 | -0.1236 | -0.004578 | -0.073242 | -0.07782 | -0.10986 | 0.027466 | -0.13275 | -0.059509 | 0.036621 | -0.045776 | 0.073242 | 8.9767 | -112.5595 | -112.7151 | 9.1141 | 9.0408 | 9.0454 | 0.064087 | 0.068665 | 8.9859 | -112.5641 | -112.6511 | 9.1553 | 9.1919 | 9.0729 | 0.20599 | 0.086975 | 0.13733 | 0.018311 | 0.16937 | 0.073242 | 0.17395 | 0.16022 | 9.1507 | 9.1461 | -112.7335 | -112.7243 | 8.9951 | 9.0591 | 8.9905 | 9.0088
1288.2344 | 121.6873 | -8.7753 | 112.9669 | 0.0039673 | 0.066574 | 0.012689 | 0.023753 | -0.002117 | -0.003183 | -0.0029331 | -0.0015565 | 0.026784 | 0.021839 | 0.010841 | -0.00095065 | 0.020093 | -0.0055521 | -0.10071 | 0.041199 | -0.14191 | -0.086975 | 0.032043 | -0.050354 | -0.054932 | -0.045776 | 0.041199 | -0.1236 | -0.041199 | 0.059509 | -0.022888 | 0.09613 | 8.6334 | -112.9257 | -113.0539 | 8.8074 | 8.7204 | 8.725 | 0.086975 | 0.091553 | 8.6517 | -112.9257 | -113.0081 | 8.8348 | 8.8715 | 8.7524 | 0.21973 | 0.10071 | 0.17395 | 0.054932 | 0.1831 | 0.082397 | 0.18311 | 0.16479 | 8.8165 | 8.8165 | -113.1088 | -113.0905 | 8.6884 | 8.7341 | 8.6746 | 8.7296
1289.9219 | 121.7194 | -9.2148 | 112.5229 | -0.0036622 | 0.066787 | 0.015466 | 0.020976 | 0.0010874 | -0.0027556 | -0.0035739 | -0.0015565 | 0.025289 | 0.019489 | 0.018745 | -0.0015915 | 0.019239 | -0.0032021 | -0.09613 | 0.036621 | -0.13275 | -0.086975 | 0.045776 | -0.059509 | -0.050354 | -0.059509 | 0.027466 | -0.11902 | -0.032043 | 0.068665 | -0.022888 | 0.082397 | 9.082 | -112.4863 | -112.6099 | 9.2606 | 9.1644 | 9.1553 | 0.082397 | 0.073242 | 9.0958 | -112.4954 | -112.5549 | 9.2834 | 9.2972 | 9.1919 | 0.20142 | 0.096131 | 0.17853 | 0.045776 | 0.18768 | 0.086976 | 0.16937 | 0.14649 | 9.2514 | 9.2422 | -112.6556 | -112.6419 | 9.1278 | 9.1827 | 9.1187 | 9.1553
1291.6719 | 121.6919 | -8.8806 | 112.8845 | -0.0036622 | 0.06636 | 0.016321 | 0.022044 | 0.0027964 | -0.00061944 | -0.0022921 | 0.0014953 | 0.026998 | 0.019916 | 0.020454 | 0.00011755 | 0.016462 | -0.0014931 | -0.14191 | 0.045776 | -0.14191 | -0.16937 | -0.054932 | -0.14191 | -0.12817 | -0.19226 | 0.050354 | -0.1236 | -0.091553 | -0.013733 | -0.09613 | 0.036621 | 8.7387 | -112.8387 | -113.0539 | 8.8257 | 8.7524 | 8.7387 | 0.013733 | 0 | 8.757 | -112.8342 | -112.9761 | 8.8669 | 8.9172 | 8.7845 | 0.16022 | 0.027466 | 0.086975 | -0.027466 | 0.10986 | 0.032043 | 0.18768 | 0.17395 | 8.9264 | 8.931 | -113.0264 | -113.0081 | 8.7112 | 8.7891 | 8.7387 | 8.6884
1293.4219 | 121.8796 | -8.6472 | 113.0859 | -0.0036622 | 0.065933 | 0.015466 | 0.020121 | -0.0036124 | -0.0033966 | -0.0027195 | -0.0046081 | 0.022298 | 0.02013 | 0.015114 | -0.0011643 | 0.018384 | -0.0023477 | -0.10071 | -0.004578 | -0.091553 | -0.013733 | 0.17395 | 0.032043 | 0.050354 | 0.050354 | -0.013733 | -0.091553 | 0.013733 | 0.16479 | 0.091553 | 0.14648 | 8.5556 | -113.0905 | -113.0997 | 8.8211 | 8.6975 | 8.6792 | 0.14191 | 0.1236 | 8.5556 | -113.0997 | -113.0722 | 8.812 | 8.7936 | 8.7387 | 0.23804 | 0.18311 | 0.2655 | 0.07782 | 0.25635 | 0.10529 | 0.086975 | 0.07782 | 8.6426 | 8.6334 | -113.1775 | -113.1775 | 8.6334 | 8.6609 | 8.5464 | 8.6975
1295.1562 | 121.7972 | -9.2514 | 112.4771 | -0.0036622 | 0.068283 | 0.01568 | 0.022257 | 0.00044655 | -0.002542 | -0.0031467 | -0.0046081 | 0.024648 | 0.020343 | 0.014473 | -0.00030965 | 0.020521 | -0.0021341 | -0.10529 | 0.045776 | -0.11902 | -0.082397 | 0.064087 | -0.059509 | -0.045776 | -0.032043 | 0.013733 | -0.11444 | -0.045776 | 0.045776 | -0.036621 | 0.091553 | 9.1324 | -112.4313 | -112.5595 | 9.3155 | 9.2056 | 9.1919 | 0.073243 | 0.05951 | 9.137 | -112.4634 | -112.5229 | 9.2972 | 9.343 | 9.2148 | 0.20599 | 0.07782 | 0.18311 | 0.036622 | 0.16022 | 0.068665 | 0.16479 | 0.12817 | 9.2972 | 9.2651 | -112.5961 | -112.5916 | 9.169 | 9.2056 | 9.1461 | 9.2194
1296.9062 | 121.8155 | -9.3063 | 112.4634 | -0.011291 | 0.067642 | 0.014398 | 0.025035 | -0.00083525 | -0.0033966 | -0.0037875 | -0.0015565 | 0.025929 | 0.019489 | 0.017036 | -0.0018051 | 0.018384 | -0.00063873 | -0.10529 | 0.036621 | -0.12817 | -0.091553 | 0.073242 | -0.050354 | -0.050354 | -0.068665 | 0.018311 | -0.10071 | -0.041199 | 0.064087 | -0.009155 | 0.10071 | 9.1782 | -112.4268 | -112.5549 | 9.3796 | 9.256 | 9.256 | 0.07782 | 0.07782 | 9.2056 | -112.4451 | -112.5046 | 9.3704 | 9.407 | 9.2972 | 0.20142 | 0.091553 | 0.20142 | 0.036621 | 0.1648 | 0.059509 | 0.1648 | 0.11902 | 9.343 | 9.3246 | -112.5916 | -112.5641 | 9.2148 | 9.2651 | 9.201 | 9.2377
1298.5938 | 121.8384 | -8.8486 | 112.9028 | 0.0039673 | 0.066146 | 0.016748 | 0.019053 | -0.0012624 | 0.00066216 | -0.00036951 | -0.0076599 | 0.024007 | 0.018848 | 0.023231 | -0.00073705 | 0.01753 | -0.0017069 | -0.13733 | 0.013733 | -0.10071 | -0.10071 | 0.050354 | -0.041199 | -0.032043 | -0.07782 | 0.013733 | -0.10986 | -0.050354 | 0.059509 | 0.004578 | 0.10529 | 8.7479 | -112.8891 | -113.0035 | 8.8989 | 8.8165 | 8.8074 | 0.068665 | 0.059509 | 8.7387 | -112.8891 | -112.9532 | 8.9081 | 8.9539 | 8.8532 | 0.21515 | 0.11444 | 0.15106 | 0 | 0.16937 | 0.059509 | 0.11444 | 0.1236 | 8.8623 | 8.8623 | -113.0035 | -113.0127 | 8.7479 | 8.7982 | 8.7112 | 8.7708
1300.3438 | 121.8246 | -8.3817 | 113.4064 | 0.0039673 | 0.065505 | 0.012476 | 0.023326 | -0.00083525 | -0.0019012 | -0.0031467 | 0.0014953 | 0.026998 | 0.019489 | 0.0095597 | -0.0013779 | 0.016675 | -0.0023477 | -0.12817 | 0.064087 | -0.15106 | -0.10529 | 0.027466 | -0.054932 | -0.059509 | -0.086975 | 0.050354 | -0.13733 | -0.059509 | 0.036621 | -0.018311 | 0.091553 | 8.2306 | -113.3423 | -113.5117 | 8.4091 | 8.3221 | 8.3267 | 0.091553 | 0.09613 | 8.2443 | -113.356 | -113.4659 | 8.4183 | 8.4732 | 8.3633 | 0.22888 | 0.11902 | 0.17853 | 0.045776 | 0.17395 | 0.07782 | 0.21515 | 0.18768 | 8.4457 | 8.432 | -113.5574 | -113.5437 | 8.2764 | 8.3221 | 8.2535 | 8.2947
1302.0625 | 121.7743 | -8.8989 | 112.9211 | -0.0036622 | 0.066787 | 0.014825 | 0.021617 | 0.0032236 | -0.00019224 | -0.0016513 | -0.0046081 | 0.024007 | 0.019916 | 0.017677 | 0.00054475 | 0.020734 | -0.0042703 | -0.15106 | 0.045776 | -0.14191 | -0.15564 | -0.032043 | -0.14191 | -0.11902 | -0.16937 | 0.041199 | -0.11902 | -0.10529 | -0.041199 | -0.12817 | 0.032043 | 8.757 | -112.8754 | -113.0768 | 8.8669 | 8.7799 | 8.757 | 0.022888 | 0 | 8.7799 | -112.8799 | -113.0264 | 8.8577 | 8.931 | 8.7708 | 0.15106 | -0.009155 | 0.10986 | -0.013733 | 0.07782 | 0.013733 | 0.18768 | 0.16022 | 8.9447 | 8.9401 | -113.0631 | -113.0402 | 8.7433 | 8.7936 | 8.7479 | 8.7296
1303.7656 | 121.9162 | -8.1116 | 113.6261 | -0.0036622 | 0.063156 | 0.017389 | 0.021189 | -0.003826 | -0.0021148 | 0.00048489 | 0.0045471 | 0.023793 | 0.018848 | 0.01255 | 0.00011755 | 0.021589 | 0.00064307 | -0.13733 | 0.018311 | -0.13733 | -0.082397 | 0.045776 | -0.068665 | -0.045776 | -0.032043 | 0.013733 | -0.10529 | 0.041199 | 0.09613 | 0.018311 | 0.15564 | 7.9742 | -113.6078 | -113.7085 | 8.1573 | 8.0658 | 8.0429 | 0.091553 | 0.068664 | 8.0063 | -113.6124 | -113.5849 | 8.2077 | 8.2672 | 8.1299 | 0.26093 | 0.1236 | 0.18311 | 0.054932 | 0.20142 | 0.14649 | 0.15564 | 0.11902 | 8.1299 | 8.1253 | -113.7634 | -113.7314 | 8.0292 | 8.1528 | 7.9742 | 8.0795
1305.4531 | 121.9574 | -8.4457 | 113.2874 | 0.0039673 | 0.065078 | 0.013544 | 0.017771 | -0.00083525 | -0.0010468 | -0.0022921 | -0.0046081 | 0.024007 | 0.019062 | 0.012764 | -0.0020187 | 0.020734 | 0.00085667 | -0.10071 | 0 | -0.10986 | -0.045776 | 0.11444 | 0.013733 | 0.036621 | 0.009155 | 0 | -0.09613 | 0.018311 | 0.14191 | 0.082397 | 0.16022 | 8.3359 | -113.2874 | -113.3331 | 8.5602 | 8.4824 | 8.4595 | 0.14648 | 0.1236 | 8.3496 | -113.2874 | -113.269 | 8.5876 | 8.606 | 8.5281 | 0.25635 | 0.17853 | 0.2243 | 0.064087 | 0.23804 | 0.11444 | 0.10986 | 0.09613 | 8.4457 | 8.4457 | -113.3972 | -113.3835 | 8.4 | 8.4641 | 8.345 | 8.4549
1307.1562 | 121.907 | -8.8852 | 112.8616 | -0.0036622 | 0.064224 | 0.017603 | 0.022898 | 0.0019418 | -0.0016876 | -0.00058311 | 0.0014953 | 0.023366 | 0.020557 | 0.018532 | -0.00030965 | 0.017957 | -0.0014931 | -0.10986 | 0.013733 | -0.09613 | -0.086975 | 0.054932 | -0.045776 | -0.022888 | -0.068665 | 0 | -0.10529 | -0.045776 | 0.064087 | 0.009155 | 0.10529 | 8.7891 | -112.8479 | -112.9486 | 8.9401 | 8.8623 | 8.8394 | 0.073242 | 0.050354 | 8.7799 | -112.8616 | -112.9074 | 8.9493 | 8.9905 | 8.8943 | 0.21057 | 0.11444 | 0.15106 | 0.009155 | 0.16937 | 0.05951 | 0.10986 | 0.10529 | 8.8989 | 8.8852 | -112.9578 | -112.9669 | 8.7982 | 8.8394 | 8.7753 | 8.8165
1308.8438 | 121.9345 | -8.2855 | 113.4842 | -0.011291 | 0.063156 | 0.014398 | 0.021403 | 1.915e-05 | -0.0029694 | -0.0014377 | 0.0014953 | 0.024007 | 0.017994 | 0.019386 | -0.0022325 | 0.017743 | -0.0034159 | -0.1236 | 0.009155 | -0.10986 | -0.073242 | 0.082397 | -0.004578 | -0.009155 | -0.022888 | 0.018311 | -0.10071 | 0.009155 | 0.10529 | 0.059509 | 0.13275 | 8.1757 | -113.475 | -113.5574 | 8.3679 | 8.2764 | 8.2809 | 0.10071 | 0.10529 | 8.1848 | -113.4659 | -113.475 | 8.3908 | 8.4183 | 8.345 | 0.23346 | 0.16022 | 0.19226 | 0.036621 | 0.20599 | 0.10986 | 0.11902 | 0.11902 | 8.2947 | 8.3038 | -113.5941 | -113.5849 | 8.2123 | 8.2947 | 8.1619 | 8.2626
1310.5469 | 121.9666 | -8.931 | 112.8204 | -0.018921 | 0.066787 | 0.015466 | 0.021403 | -0.0016898 | -0.0029694 | -0.0012241 | -0.0015565 | 0.02358 | 0.022266 | 0.013191 | -0.00052345 | 0.020521 | -0.0032021 | -0.07782 | 0.004578 | -0.10529 | -0.036621 | 0.091553 | -0.009155 | 0 | 0.027466 | 0.009155 | -0.10529 | 0.036621 | 0.10986 | 0.041199 | 0.16022 | 8.8257 | -112.8159 | -112.8571 | 9.0225 | 8.931 | 8.9218 | 0.10529 | 0.096131 | 8.8257 | -112.8113 | -112.7838 | 9.0408 | 9.0912 | 8.9722 | 0.2655 | 0.14649 | 0.19684 | 0.068665 | 0.21515 | 0.14191 | 0.10986 | 0.11444 | 8.9355 | 8.9401 | -112.9257 | -112.9257 | 8.8943 | 8.9676 | 8.8531 | 8.9584
1312.2344 | 121.8658 | -8.6197 | 113.1821 | -0.0036622 | 0.067001 | 0.014185 | 0.021403 | -0.00019445 | -0.0029694 | -0.00058311 | -0.0076599 | 0.025075 | 0.019062 | 0.017891 | -0.0015915 | 0.018812 | -0.0019205 | -0.10071 | 0.032043 | -0.13275 | -0.082397 | 0.050354 | -0.059509 | -0.041199 | -0.045776 | 0.032043 | -0.10529 | -0.032043 | 0.050354 | -0.036621 | 0.091553 | 8.4869 | -113.15 | -113.2645 | 8.67 | 8.5785 | 8.5602 | 0.091552 | 0.073242 | 8.5144 | -113.15 | -113.2141 | 8.67 | 8.7112 | 8.5831 | 0.19684 | 0.068665 | 0.18311 | 0.050354 | 0.15564 | 0.073243 | 0.16479 | 0.13733 | 8.6517 | 8.6517 | -113.3148 | -113.2874 | 8.5373 | 8.5876 | 8.519 | 8.5739
1313.9375 | 121.8704 | -8.9539 | 112.8708 | 0.0039673 | 0.066574 | 0.015253 | 0.019908 | 0.0017282 | -0.001474 | -0.00036951 | -0.0076599 | 0.026357 | 0.018207 | 0.0149 | -0.00073705 | 0.01988 | 0.0010703 | -0.11444 | 0.041199 | -0.13733 | -0.11902 | -0.009155 | -0.073242 | -0.068665 | -0.11902 | 0.050354 | -0.11902 | -0.054932 | 0.018311 | -0.036621 | 0.07782 | 8.8165 | -112.8296 | -112.9898 | 8.9447 | 8.8852 | 8.8806 | 0.068664 | 0.064087 | 8.8348 | -112.8204 | -112.9257 | 8.9722 | 9.0317 | 8.9172 | 0.19684 | 0.082398 | 0.12817 | 0.01831 | 0.13733 | 0.064087 | 0.17853 | 0.16937 | 8.9951 | 9.0042 | -113.0081 | -112.9898 | 8.8348 | 8.8989 | 8.8394 | 8.8348
1315.6094 | 121.8658 | -8.9722 | 112.8662 | 0.0039673 | 0.065505 | 0.014825 | 0.022471 | -0.0010488 | -0.00061944 | -0.0022921 | -0.0046081 | 0.024434 | 0.021412 | 0.016823 | -0.0020187 | 0.017316 | -0.00063873 | -0.1236 | 0.041199 | -0.11902 | -0.1236 | 0.013733 | -0.068665 | -0.054932 | -0.10071 | 0.041199 | -0.13275 | -0.050354 | 0.041199 | -0.036621 | 0.07782 | 8.8531 | -112.825 | -112.9898 | 8.9859 | 8.9172 | 8.9035 | 0.064087 | 0.050354 | 8.8394 | -112.825 | -112.9166 | 9.0134 | 9.05 | 8.9355 | 0.21057 | 0.09613 | 0.13275 | -0.004577 | 0.17395 | 0.082397 | 0.16022 | 0.17395 | 9.0134 | 9.0134 | -112.9852 | -112.999 | 8.8486 | 8.9218 | 8.8486 | 8.8715
1317.2812 | 121.907 | -8.5281 | 113.2507 | -0.011291 | 0.064865 | 0.017816 | 0.022685 | -0.0025442 | 0.00023496 | -0.00058311 | -0.0015565 | 0.026784 | 0.017566 | 0.015114 | -0.00052345 | 0.020734 | 0.00021567 | -0.15106 | 0.027466 | -0.14191 | -0.13275 | -0.009155 | -0.12817 | -0.082397 | -0.10986 | 0.022888 | -0.1236 | -0.032043 | 0.027466 | -0.050354 | 0.091553 | 8.3862 | -113.2233 | -113.3835 | 8.519 | 8.4457 | 8.4 | 0.05951 | 0.013733 | 8.4045 | -113.2278 | -113.2828 | 8.5556 | 8.6197 | 8.4778 | 0.21515 | 0.073242 | 0.13275 | 0.009156 | 0.15106 | 0.091553 | 0.16937 | 0.14648 | 8.5556 | 8.551 | -113.3926 | -113.3743 | 8.3954 | 8.4961 | 8.3771 | 8.4183
1318.9688 | 121.9711 | -8.725 | 113.0493 | 0.0039673 | 0.06401 | 0.015039 | 0.020976 | -0.00019445 | -0.0012604 | -0.0014377 | -0.0046081 | 0.022939 | 0.019062 | 0.016395 | -0.0026597 | 0.020521 | -0.00063873 | -0.11444 | 0.022888 | -0.12817 | -0.068665 | 0.091553 | -0.013733 | 0.004578 | -0.004578 | 0 | -0.10986 | 0.022888 | 0.10986 | 0.068665 | 0.14648 | 8.5968 | -113.0264 | -113.118 | 8.8165 | 8.7296 | 8.7112 | 0.13275 | 0.11444 | 8.6151 | -113.0493 | -113.0264 | 8.8348 | 8.8715 | 8.7936 | 0.25635 | 0.17853 | 0.21973 | 0.059509 | 0.21973 | 0.13275 | 0.15106 | 0.10986 | 8.7479 | 8.725 | -113.1775 | -113.1592 | 8.6563 | 8.7479 | 8.6105 | 8.7204
1320.6406 | 121.9666 | -9.05 | 112.7563 | -0.011291 | 0.062728 | 0.01568 | 0.022471 | -0.0027578 | -0.0010468 | -0.00079691 | 0.0014953 | 0.024434 | 0.016071 | 0.016395 | -0.0015915 | 0.019025 | -0.00085233 | -0.11444 | 0.009155 | -0.11902 | -0.059509 | 0.091553 | 0.009155 | 0.036621 | -0.009155 | 0.004578 | -0.10529 | 0.022888 | 0.11444 | 0.068665 | 0.15564 | 8.931 | -112.7472 | -112.8159 | 9.1415 | 9.0866 | 9.0591 | 0.15564 | 0.12817 | 8.9447 | -112.7518 | -112.7335 | 9.1644 | 9.2056 | 9.1187 | 0.26093 | 0.17395 | 0.21057 | 0.05951 | 0.21973 | 0.12817 | 0.12817 | 0.10986 | 9.0591 | 9.0546 | -112.8754 | -112.8616 | 8.9905 | 9.0729 | 8.9355 | 9.0408
1322.3281 | 121.9803 | -8.6929 | 113.0676 | 0.011597 | 0.066146 | 0.015039 | 0.020976 | -0.0044668 | -0.00083304 | 0.00069849 | -0.0046081 | 0.024434 | 0.020343 | 0.017036 | 0.00054475 | 0.021375 | -0.00021153 | -0.059509 | 0 | -0.10529 | -0.004578 | 0.1236 | -0.013733 | 0.018311 | 0.045776 | 0 | -0.10071 | 0.045776 | 0.11444 | 0.045776 | 0.14648 | 8.5876 | -113.0676 | -113.0722 | 8.8165 | 8.7112 | 8.6792 | 0.1236 | 0.091553 | 8.5922 | -113.0676 | -113.0219 | 8.8074 | 8.8394 | 8.7387 | 0.24719 | 0.14648 | 0.22888 | 0.10071 | 0.21515 | 0.14648 | 0.10529 | 0.10071 | 8.6929 | 8.6929 | -113.1729 | -113.1683 | 8.6884 | 8.7387 | 8.6334 | 8.7387
1324 | 121.962 | -8.6746 | 113.0722 | -0.0036622 | 0.065078 | 0.01568 | 0.023539 | -0.0012624 | -0.00083304 | -0.0014377 | -0.0015565 | 0.023793 | 0.018207 | 0.019386 | 0.0013991 | 0.020521 | 0.00021567 | -0.041199 | -0.009155 | -0.11444 | -0.004578 | 0.11902 | -0.013733 | 0.013733 | 0.050354 | -0.009155 | -0.10529 | 0.050354 | 0.11902 | 0.032043 | 0.15106 | 8.5602 | -113.0814 | -113.0768 | 8.7936 | 8.6884 | 8.6609 | 0.12817 | 0.10071 | 8.5693 | -113.0814 | -113.0219 | 8.7936 | 8.8257 | 8.7067 | 0.25635 | 0.13733 | 0.23346 | 0.10986 | 0.22431 | 0.15564 | 0.10529 | 0.096131 | 8.6655 | 8.6655 | -113.1866 | -113.1775 | 8.67 | 8.725 | 8.6334 | 8.725
1325.6875 | 121.9162 | -8.7341 | 113.0402 | 0.019226 | 0.065292 | 0.016321 | 0.022257 | -0.0012624 | -0.00083304 | -0.00015591 | -0.0046081 | 0.024648 | 0.018421 | 0.018532 | -0.00030965 | 0.022443 | 0.0023521 | -0.07782 | -0.004578 | -0.09613 | -0.036621 | 0.11444 | -0.027466 | -0.018311 | 0.004578 | 0.004578 | -0.11902 | 0 | 0.082397 | 0.004578 | 0.10529 | 8.638 | -113.0447 | -113.0768 | 8.8486 | 8.7158 | 8.7067 | 0.077819 | 0.068664 | 8.6151 | -113.0356 | -113.0402 | 8.8165 | 8.8394 | 8.7387 | 0.22431 | 0.1236 | 0.21057 | 0.059509 | 0.20142 | 0.11902 | 0.091552 | 0.1236 | 8.7296 | 8.7387 | -113.1363 | -113.1592 | 8.6975 | 8.7341 | 8.6563 | 8.7387
1327.4062 | 121.9299 | -14.6896 | 107.1259 | -0.011291 | 0.06636 | 0.014185 | 0.02418 | 0.00087375 | -0.0010468 | -0.0025057 | -0.0046081 | 0.022725 | 0.019916 | 0.018745 | -0.0018051 | 0.018384 | 0.0014975 | -0.11902 | 0.013733 | -0.086975 | -0.068665 | 0.059509 | -0.050354 | -0.022888 | -0.054932 | 0.027466 | -0.11444 | -0.027466 | 0.073242 | -0.018311 | 0.091553 | 14.6027 | -107.1121 | -107.1945 | 14.7491 | 14.6667 | 14.6393 | 0.064087 | 0.036621 | 14.5752 | -107.0984 | -107.1533 | 14.7629 | 14.7812 | 14.6713 | 0.20599 | 0.09613 | 0.14648 | 0.01831 | 0.18768 | 0.086975 | 0.10071 | 0.14191 | 14.7034 | 14.7171 | -107.2128 | -107.2403 | 14.621 | 14.6622 | 14.5706 | 14.6347
1329.0938 | 121.8567 | -12.4008 | 109.4604 | -0.0036622 | 0.068069 | 0.016321 | 0.023112 | 0.005787 | -0.003183 | -0.0027195 | -0.0076599 | 0.02657 | 0.02013 | 0.016182 | 0.00054475 | 0.017103 | -0.0040567 | -0.09613 | 0.027466 | -0.11902 | -0.10071 | 0.018311 | -0.10071 | -0.082397 | -0.09613 | 0.036621 | -0.12817 | -0.064087 | -0.009155 | -0.10071 | 0.036621 | 12.2818 | -109.433 | -109.5612 | 12.4191 | 12.3184 | 12.3001 | 0.036622 | 0.018311 | 12.2726 | -109.4238 | -109.5245 | 12.3917 | 12.4374 | 12.3001 | 0.1648 | 0.027466 | 0.13733 | 0.018311 | 0.11902 | 0.064087 | 0.14649 | 0.1648 | 12.4283 | 12.4374 | -109.5795 | -109.5886 | 12.3001 | 12.3367 | 12.3047 | 12.3047
1330.8594 | 121.843 | -11.3068 | 110.5362 | -0.011291 | 0.065292 | 0.014825 | 0.023539 | 0.001301 | -0.00019224 | -0.0012241 | -0.0046081 | 0.026143 | 0.02013 | 0.017891 | -9.605e-05 | 0.01753 | -0.0014931 | -0.14648 | 0.022888 | -0.13733 | -0.15564 | -0.027466 | -0.14648 | -0.10071 | -0.12817 | 0.050354 | -0.12817 | -0.07782 | -0.004578 | -0.09613 | 0.054932 | 11.1694 | -110.5133 | -110.6918 | 11.2793 | 11.2061 | 11.1603 | 0.036621 | -0.009155 | 11.1786 | -110.4858 | -110.614 | 11.3022 | 11.3617 | 11.2106 | 0.18311 | 0.032044 | 0.10986 | -0.018311 | 0.1236 | 0.050354 | 0.16022 | 0.17853 | 11.3297 | 11.3571 | -110.6735 | -110.6644 | 11.1511 | 11.2289 | 11.1603 | 11.1786
1332.5938 | 121.8384 | -11.5036 | 110.3806 | -0.0036622 | 0.066146 | 0.015894 | 0.024394 | 0.0010874 | -0.0040374 | 0.00069849 | -0.0015565 | 0.026357 | 0.020343 | 0.0099869 | -0.0015915 | 0.019452 | -0.0012795 | -0.15106 | 0.050354 | -0.13275 | -0.15564 | -0.032043 | -0.14191 | -0.10071 | -0.14648 | 0.041199 | -0.14648 | -0.086975 | -0.027466 | -0.09613 | 0.032043 | 11.3708 | -110.3302 | -110.5362 | 11.4716 | 11.4029 | 11.3617 | 0.032043 | -0.009156 | 11.3571 | -110.3394 | -110.4675 | 11.4761 | 11.5356 | 11.4075 | 0.17853 | 0.050354 | 0.10071 | -0.022889 | 0.11902 | 0.059509 | 0.18311 | 0.18768 | 11.554 | 11.5448 | -110.5133 | -110.527 | 11.348 | 11.4166 | 11.3525 | 11.3571
1334.2812 | 121.9254 | -11.2015 | 110.5728 | -0.011291 | 0.064437 | 0.014612 | 0.020121 | 1.915e-05 | -0.0040374 | -0.0022921 | -0.0046081 | 0.024861 | 0.018421 | 0.021522 | -0.0030869 | 0.018812 | 0.0029929 | -0.14191 | -0.004578 | -0.09613 | -0.082397 | 0.045776 | -0.045776 | -0.036621 | -0.064087 | 0.018311 | -0.10986 | -0.041199 | 0.07782 | -0.009155 | 0.09613 | 11.1053 | -110.5774 | -110.6552 | 11.2473 | 11.1649 | 11.1557 | 0.059509 | 0.050354 | 11.0916 | -110.5545 | -110.614 | 11.2793 | 11.2976 | 11.1923 | 0.20599 | 0.10071 | 0.14191 | 0.013733 | 0.18768 | 0.068664 | 0.091552 | 0.12817 | 11.1969 | 11.2198 | -110.6689 | -110.6827 | 11.1191 | 11.1603 | 11.0596 | 11.1374
1336.0312 | 121.8521 | -11.1786 | 110.6873 | 0.0039673 | 0.064224 | 0.012903 | 0.021189 | -0.00062165 | -0.0033966 | -0.0014377 | -0.0015565 | 0.025502 | 0.022266 | 0.015541 | -0.0022325 | 0.017743 | -0.0021341 | -0.16479 | 0.050354 | -0.14191 | -0.16022 | -0.022888 | -0.086975 | -0.086975 | -0.13733 | 0.050354 | -0.14648 | -0.09613 | 0 | -0.07782 | 0.041199 | 11.0367 | -110.6369 | -110.8475 | 11.1557 | 11.0916 | 11.0916 | 0.054932 | 0.054932 | 11.0321 | -110.6369 | -110.7834 | 11.1786 | 11.2198 | 11.1008 | 0.18768 | 0.068664 | 0.11902 | -0.01831 | 0.14648 | 0.050354 | 0.19226 | 0.19684 | 11.2289 | 11.2289 | -110.8292 | -110.8337 | 11.0184 | 11.0825 | 11.0138 | 11.0413
1337.7812 | 121.9757 | -11.3388 | 110.4538 | -0.011291 | 0.062942 | 0.013116 | 0.020548 | -0.003826 | -0.003183 | 5.7688e-05 | -0.0015565 | 0.021871 | 0.017353 | 0.018959 | -0.0028733 | 0.01753 | 0.0032065 | -0.11444 | 0.013733 | -0.11902 | -0.091553 | 0.068665 | -0.018311 | 0 | -0.050354 | 0 | -0.09613 | -0.032043 | 0.10986 | 0.045776 | 0.13733 | 11.2198 | -110.4401 | -110.5453 | 11.4075 | 11.3388 | 11.3205 | 0.11902 | 0.10071 | 11.2427 | -110.4538 | -110.4858 | 11.4487 | 11.4761 | 11.3846 | 0.23346 | 0.14191 | 0.18768 | 0.027466 | 0.20599 | 0.064087 | 0.13275 | 0.09613 | 11.3525 | 11.3388 | -110.5728 | -110.5499 | 11.2473 | 11.3068 | 11.2244 | 11.2885
1339.5312 | 121.8384 | -11.2473 | 110.582 | -0.011291 | 0.066146 | 0.01333 | 0.020121 | -0.0033986 | -0.0033966 | -0.0027195 | 0.0045471 | 0.023793 | 0.019489 | 0.016182 | -0.0028733 | 0.017316 | -0.0025613 | -0.15564 | 0.045776 | -0.12817 | -0.14648 | -0.018311 | -0.086975 | -0.07782 | -0.16022 | 0.032043 | -0.13733 | -0.10071 | -0.013733 | -0.091553 | 0.032043 | 11.1191 | -110.5362 | -110.7285 | 11.2289 | 11.1694 | 11.1603 | 0.050354 | 0.041199 | 11.1099 | -110.5499 | -110.6827 | 11.2335 | 11.2793 | 11.1557 | 0.16937 | 0.045776 | 0.10986 | -0.01831 | 0.1236 | 0.036621 | 0.17395 | 0.16937 | 11.293 | 11.2793 | -110.7101 | -110.7193 | 11.1008 | 11.1465 | 11.0916 | 11.087
1341.2188 | 121.8796 | -11.1832 | 110.6598 | -0.011291 | 0.064651 | 0.014398 | 0.021617 | -0.0044668 | -0.007669 | -0.0020785 | -0.0015565 | 0.024648 | 0.01778 | 0.0093461 | -0.0022325 | 0.016889 | -0.00042513 | -0.15564 | 0.059509 | -0.13733 | -0.15106 | -0.027466 | -0.09613 | -0.082397 | -0.14191 | 0.054932 | -0.13275 | -0.07782 | 0 | -0.059509 | 0.041199 | 11.0458 | -110.6003 | -110.8109 | 11.1557 | 11.1008 | 11.087 | 0.054932 | 0.041199 | 11.0504 | -110.6049 | -110.7376 | 11.1832 | 11.2244 | 11.1237 | 0.17395 | 0.073242 | 0.10986 | -0.013733 | 0.13275 | 0.054931 | 0.19684 | 0.18768 | 11.2427 | 11.2381 | -110.7971 | -110.7925 | 11.0321 | 11.1053 | 11.0275 | 11.0413
1342.9531 | 121.9666 | -9.6359 | 112.1384 | 0.0039673 | 0.063583 | 0.01568 | 0.023753 | -0.00019445 | -0.0038238 | -0.0014377 | 0.0014953 | 0.025289 | 0.016712 | 0.016823 | -0.00052345 | 0.020521 | -0.00085233 | -0.10071 | 0.009155 | -0.11902 | -0.073242 | 0.064087 | -0.041199 | -0.022888 | -0.009155 | 0.013733 | -0.11444 | 0.018311 | 0.11444 | 0.032043 | 0.15106 | 9.5169 | -112.1292 | -112.2116 | 9.7 | 9.613 | 9.5947 | 0.096131 | 0.07782 | 9.5215 | -112.1246 | -112.1201 | 9.7504 | 9.787 | 9.668 | 0.2655 | 0.14648 | 0.18311 | 0.045777 | 0.22888 | 0.13275 | 0.12817 | 0.12817 | 9.6451 | 9.6497 | -112.2574 | -112.2528 | 9.5627 | 9.6542 | 9.5352 | 9.6268
1344.7031 | 121.8658 | -9.4711 | 112.3856 | -0.0036622 | 0.065933 | 0.016534 | 0.023326 | 0.00066015 | -0.0016876 | -0.0018649 | -0.0015565 | 0.023366 | 0.019489 | 0.011269 | -0.0018051 | 0.018384 | -0.0027749 | -0.10986 | 0.027466 | -0.11902 | -0.10071 | 0.041199 | -0.059509 | -0.054932 | -0.045776 | 0.036621 | -0.1236 | -0.054932 | 0.022888 | -0.082397 | 0.068665 | 9.3521 | -112.3581 | -112.4863 | 9.5123 | 9.4162 | 9.4116 | 0.064087 | 0.05951 | 9.3475 | -112.3489 | -112.4405 | 9.494 | 9.5398 | 9.3887 | 0.19226 | 0.041199 | 0.16022 | 0.018311 | 0.14648 | 0.068664 | 0.14649 | 0.16022 | 9.4986 | 9.5078 | -112.5046 | -112.5092 | 9.3704 | 9.4162 | 9.3613 | 9.4254
1346.4531 | 121.8658 | -9.8923 | 111.9781 | -0.0036622 | 0.064651 | 0.017175 | 0.020121 | 0.00066015 | -0.0019012 | -0.0025057 | 0.0014953 | 0.026784 | 0.018207 | 0.0089187 | -0.0022325 | 0.018812 | -0.0019205 | -0.13733 | 0.045776 | -0.15564 | -0.14648 | 0 | -0.07782 | -0.073242 | -0.11444 | 0.054932 | -0.14191 | -0.059509 | 0.045776 | -0.041199 | 0.068665 | 9.7366 | -111.9324 | -112.1246 | 9.8923 | 9.819 | 9.8145 | 0.082398 | 0.07782 | 9.7504 | -111.9232 | -112.0377 | 9.938 | 9.9609 | 9.8511 | 0.21057 | 0.10071 | 0.15564 | 0.009156 | 0.18768 | 0.082398 | 0.20142 | 0.19684 | 9.938 | 9.9472 | -112.1338 | -112.1201 | 9.7458 | 9.8328 | 9.7549 | 9.7778
1348.1406 | 117.5903 | -7.814 | 109.8175 | -0.011291 | 0.06636 | 0.015039 | 0.022471 | -0.00083525 | -0.003183 | 0.00048489 | -0.0015565 | 0.024648 | 0.019489 | 0.0099869 | -0.0020187 | 0.019666 | -0.00063873 | -0.10986 | 0.036621 | -0.11444 | -0.10529 | 0.036621 | -0.059509 | -0.054932 | -0.059509 | 0.022888 | -0.11902 | -0.041199 | 0.045776 | -0.027466 | 0.086975 | 7.6996 | -109.7809 | -109.9228 | 7.8506 | 7.7591 | 7.7545 | 0.059509 | 0.054932 | 7.695 | -109.7946 | -109.8587 | 7.8598 | 7.901 | 7.7866 | 0.20599 | 0.091553 | 0.15106 | 0.009155 | 0.16479 | 0.07782 | 0.15106 | 0.14191 | 7.8506 | 7.8369 | -109.9319 | -109.9365 | 7.7087 | 7.7728 | 7.7042 | 7.7545
1349.875 | 116.9998 | -9.7595 | 107.2861 | -0.011291 | 0.065078 | 0.01333 | 0.020976 | -0.0012624 | -0.0040374 | 0.00027129 | -0.0015565 | 0.024861 | 0.018634 | 0.011482 | -0.0035141 | 0.019025 | 0.0027793 | -0.16937 | 0.050354 | -0.11444 | -0.15564 | 0 | -0.086975 | -0.086975 | -0.15564 | 0.045776 | -0.14191 | -0.11902 | 0.004578 | -0.068665 | 0.022888 | 9.6451 | -107.2357 | -107.4417 | 9.7595 | 9.6725 | 9.6725 | 0.027466 | 0.027466 | 9.6176 | -107.2403 | -107.4051 | 9.7641 | 9.7824 | 9.6909 | 0.16479 | 0.073242 | 0.11444 | -0.041199 | 0.14649 | 0.022888 | 0.16479 | 0.18768 | 9.8099 | 9.8053 | -107.4005 | -107.428 | 9.6039 | 9.6405 | 9.5901 | 9.6039
1351.5469 | 116.7206 | -9.5673 | 107.0206 | 0.0039673 | 0.065933 | 0.016107 | 0.022471 | 0.00087375 | -0.0016876 | 0.0011257 | 0.0014953 | 0.022725 | 0.022266 | 0.0087051 | 0.00075835 | 0.020093 | -0.00042513 | -0.16022 | 0.045776 | -0.13733 | -0.10986 | 0.022888 | -0.091553 | -0.073242 | -0.068665 | 0.027466 | -0.10529 | 0 | 0.086975 | 0.013733 | 0.1236 | 9.4299 | -106.9748 | -107.1304 | 9.5901 | 9.494 | 9.4757 | 0.064087 | 0.045776 | 9.462 | -106.9931 | -107.0206 | 9.6542 | 9.6909 | 9.581 | 0.22888 | 0.11902 | 0.16022 | 0.027466 | 0.19226 | 0.10529 | 0.18311 | 0.13275 | 9.613 | 9.5947 | -107.1579 | -107.1259 | 9.4574 | 9.5673 | 9.407 | 9.4986
1353.2812 | 116.4322 | -9.0866 | 107.1487 | -0.011291 | 0.064651 | 0.015039 | 0.020121 | 0.00087375 | -0.001474 | -0.0020785 | 0.0014953 | 0.022725 | 0.019703 | 0.021095 | -0.0015915 | 0.017957 | -0.0019205 | -0.086975 | 0.009155 | -0.086975 | -0.036621 | 0.16022 | 0.032043 | 0.045776 | 0.036621 | 0.004578 | -0.10071 | 0.018311 | 0.16022 | 0.07782 | 0.15106 | 8.9996 | -107.1396 | -107.1854 | 9.2468 | 9.1324 | 9.1187 | 0.13275 | 0.11902 | 8.9859 | -107.1442 | -107.1304 | 9.2468 | 9.2377 | 9.1644 | 0.25177 | 0.17853 | 0.24719 | 0.050354 | 0.26093 | 0.11902 | 0.09613 | 0.10529 | 9.0958 | 9.0912 | -107.2357 | -107.2495 | 9.05 | 9.1049 | 8.9996 | 9.1232
1354.9531 | 116.0568 | -9.1461 | 106.9199 | -0.0036622 | 0.06636 | 0.013116 | 0.020121 | -0.0012624 | -0.0027556 | -0.0031467 | -0.0015565 | 0.024434 | 0.017139 | 0.014686 | -0.0028733 | 0.017957 | 0.0012839 | -0.13275 | 0.041199 | -0.14191 | -0.12817 | 0.004578 | -0.07782 | -0.064087 | -0.11444 | 0.045776 | -0.14191 | -0.11444 | 0.004578 | -0.068665 | 0.022888 | 9.0042 | -106.8787 | -107.048 | 9.1507 | 9.082 | 9.0683 | 0.07782 | 0.064087 | 9.0042 | -106.8741 | -107.0343 | 9.1507 | 9.169 | 9.0775 | 0.16479 | 0.073242 | 0.14649 | 0.013733 | 0.14649 | 0.027466 | 0.18311 | 0.18768 | 9.1873 | 9.1919 | -107.0618 | -107.0618 | 9.0179 | 9.0317 | 9.0134 | 9.0317
1356.6875 | 115.9012 | -9.137 | 106.6315 | -0.0036622 | 0.065078 | 0.016962 | 0.02183 | 0.00023275 | -0.0021148 | -0.0016513 | 0.0014953 | 0.022512 | 0.020771 | 0.019173 | -0.0026597 | 0.018171 | -0.0029885 | -0.09613 | -0.004578 | -0.10071 | -0.050354 | 0.09613 | -0.027466 | -0.013733 | -0.009155 | 0.009155 | -0.10071 | -0.013733 | 0.07782 | 0.013733 | 0.09613 | 9.0363 | -106.636 | -106.6818 | 9.2331 | 9.1232 | 9.1095 | 0.086975 | 0.073242 | 9.0363 | -106.6223 | -106.6452 | 9.2148 | 9.2331 | 9.1507 | 0.19684 | 0.11444 | 0.19684 | 0.050354 | 0.17853 | 0.086975 | 0.09613 | 0.10986 | 9.1324 | 9.1461 | -106.7322 | -106.7322 | 9.0866 | 9.1232 | 9.0408 | 9.1278
1358.375 | 115.6998 | -89.6942 | 25.795 | -0.0036622 | 0.067642 | 0.01568 | 0.025035 | 0.004719 | -0.0010468 | -0.0027195 | -0.0046081 | 0.027211 | 0.017566 | 0.0061417 | -9.605e-05 | 0.019452 | -0.0025613 | -0.064087 | 0.082397 | -0.082397 | -0.050354 | 0.086975 | -0.032043 | -0.013733 | -0.018311 | 0.086975 | -0.064087 | 0 | 0.059509 | -0.004578 | 0.10071 | 89.6118 | -25.7126 | -25.8453 | 89.7812 | 89.6805 | 89.6622 | 0.068664 | 0.050354 | 89.6301 | -25.708 | -25.795 | 89.7537 | 89.7949 | 89.6896 | 0.1648 | 0.059509 | 0.16937 | 0.032043 | 0.1236 | 0.064087 | 0.16479 | 0.15106 | 89.7766 | 89.7812 | -25.8774 | -25.8591 | 89.6439 | 89.6942 | 89.6301 | 89.6759
1360.0469 | 115.6952 | -89.5706 | 25.7172 | -0.0036622 | 0.066787 | 0.01803 | 0.023112 | 0.001301 | -0.00040584 | -0.0014377 | 0.0014953 | 0.022939 | 0.018421 | 0.020241 | 0.0041763 | 0.018598 | -0.0029885 | -0.027466 | 0.054932 | -0.045776 | 0.022888 | 0.15106 | 0.032043 | 0.045776 | 0.059509 | 0.036621 | -0.050354 | 0.09613 | 0.15106 | 0.091553 | 0.21973 | 89.5248 | -25.6622 | -25.6943 | 89.7217 | 89.6164 | 89.6027 | 0.091552 | 0.077819 | 89.5203 | -25.6805 | -25.621 | 89.7217 | 89.7903 | 89.6622 | 0.27008 | 0.14191 | 0.19684 | 0.068664 | 0.20142 | 0.14648 | 0.10071 | 0.086975 | 89.6255 | 89.6072 | -25.7629 | -25.7675 | 89.5935 | 89.6667 | 89.5432 | 89.6301
1361.7812 | 115.5487 | -89.5569 | 25.6897 | -0.0036622 | 0.065292 | 0.015894 | 0.021189 | 1.915e-05 | -0.004251 | -0.0016513 | -0.0046081 | 0.024007 | 0.017994 | 0.015968 | -0.0022325 | 0.019239 | -0.00085233 | -0.022888 | 0.050354 | -0.068665 | 0.022888 | 0.18768 | 0.059509 | 0.07782 | 0.050354 | 0.059509 | -0.050354 | 0.054932 | 0.15106 | 0.09613 | 0.18768 | 89.4882 | -25.6393 | -25.6668 | 89.7446 | 89.6347 | 89.6164 | 0.14649 | 0.12817 | 89.5065 | -25.6302 | -25.6348 | 89.7079 | 89.7446 | 89.653 | 0.23804 | 0.14648 | 0.25635 | 0.091553 | 0.20142 | 0.10529 | 0.11902 | 0.10986 | 89.6072 | 89.6164 | -25.7584 | -25.7401 | 89.5798 | 89.6118 | 89.534 | 89.6072
1363.4688 | 115.3473 | -89.4974 | 25.7034 | -0.018921 | 0.067428 | 0.015466 | 0.022471 | -0.0025442 | -0.00083304 | -0.00079691 | -0.0015565 | 0.025502 | 0.019916 | 0.013832 | 0.00075835 | 0.019452 | -0.0051247 | -0.10529 | 0.086975 | -0.091553 | -0.10986 | -0.004578 | -0.10529 | -0.054932 | -0.091553 | 0.082397 | -0.086975 | -0.027466 | 0 | -0.045776 | 0.082397 | 89.4058 | -25.6165 | -25.8133 | 89.4928 | 89.4424 | 89.3921 | 0.036621 | -0.013733 | 89.4104 | -25.621 | -25.7309 | 89.4974 | 89.5798 | 89.4516 | 0.16937 | 0.041199 | 0.086975 | -0.01831 | 0.086975 | 0.059509 | 0.17853 | 0.16937 | 89.5844 | 89.5798 | -25.795 | -25.7904 | 89.3875 | 89.4699 | 89.3921 | 89.4058
1365.2188 | 115.2237 | -89.4608 | 25.6668 | -0.011291 | 0.067214 | 0.015466 | 0.024607 | 0.0010874 | -0.00061944 | -0.0029331 | -0.0046081 | 0.022725 | 0.017994 | 0.0099869 | -0.0018051 | 0.01753 | -0.0034159 | -0.10529 | 0.091553 | -0.11444 | -0.11444 | -0.013733 | -0.091553 | -0.07782 | -0.10986 | 0.086975 | -0.082397 | -0.036621 | 0.009155 | -0.054932 | 0.09613 | 89.3463 | -25.5753 | -25.7812 | 89.447 | 89.3829 | 89.3692 | 0.036621 | 0.022888 | 89.3784 | -25.5798 | -25.7034 | 89.4699 | 89.5569 | 89.4058 | 0.17853 | 0.027465 | 0.10071 | 0 | 0.091552 | 0.045776 | 0.20599 | 0.16937 | 89.5523 | 89.5477 | -25.7812 | -25.7492 | 89.3463 | 89.4241 | 89.3555 | 89.3509
1366.9531 | 115.1733 | -89.4012 | 25.6348 | -0.011291 | 0.06871 | 0.013757 | 0.022471 | 0.0021556 | -0.0040374 | -0.0014377 | 0.0014953 | 0.024861 | 0.019062 | 0.015541 | -0.00052345 | 0.017743 | -0.0079019 | -0.073242 | 0.091553 | -0.073242 | -0.059509 | 0.07782 | -0.045776 | -0.022888 | -0.041199 | 0.091553 | -0.086975 | -0.013733 | 0.027466 | -0.050354 | 0.10529 | 89.328 | -25.5432 | -25.6943 | 89.4791 | 89.3784 | 89.3555 | 0.050354 | 0.027466 | 89.3143 | -25.5432 | -25.6485 | 89.4287 | 89.5065 | 89.3509 | 0.19226 | 0.036621 | 0.15106 | 0.013733 | 0.11444 | 0.073242 | 0.16479 | 0.17853 | 89.4928 | 89.4928 | -25.708 | -25.7217 | 89.3417 | 89.3875 | 89.328 | 89.36
1368.6406 | 115.2145 | -89.3143 | 25.6073 | -0.011291 | 0.065078 | 0.012903 | 0.01948 | -0.0036124 | -0.0016876 | -0.0016513 | -0.0015565 | 0.021657 | 0.019703 | 0.015968 | -0.0047959 | 0.017957 | -0.0010659 | -0.036621 | 0.032043 | -0.068665 | 0.032043 | 0.17395 | 0.073242 | 0.073242 | 0.059509 | 0.036621 | -0.045776 | 0.064087 | 0.16937 | 0.10071 | 0.16479 | 89.2456 | -25.5753 | -25.5753 | 89.4882 | 89.3875 | 89.3875 | 0.14191 | 0.14191 | 89.2685 | -25.5707 | -25.5432 | 89.4836 | 89.4791 | 89.415 | 0.21057 | 0.14648 | 0.24261 | 0.10071 | 0.21515 | 0.10986 | 0.10071 | 0.082397 | 89.3463 | 89.3509 | -25.676 | -25.6531 | 89.3463 | 89.3784 | 89.2776 | 89.3738
1370.3906 | 115.1047 | -89.3417 | 25.6256 | 0.0039673 | 0.066787 | 0.015253 | 0.023112 | 0.00023275 | -0.002542 | -0.0035739 | 0.0014953 | 0.024861 | 0.018634 | 0.020668 | -0.00030965 | 0.01753 | -0.00042513 | -0.054932 | 0.091553 | -0.091553 | -0.068665 | 0.059509 | -0.013733 | -0.009155 | -0.018311 | 0.10529 | -0.059509 | 0.018311 | 0.091553 | -0.004578 | 0.11902 | 89.2502 | -25.5341 | -25.6943 | 89.4012 | 89.3326 | 89.328 | 0.082398 | 0.07782 | 89.2822 | -25.5203 | -25.6073 | 89.4333 | 89.4608 | 89.3372 | 0.17853 | 0.054931 | 0.15106 | 0.022888 | 0.15106 | 0.07782 | 0.18311 | 0.16479 | 89.4333 | 89.447 | -25.7172 | -25.6851 | 89.2731 | 89.36 | 89.2868 | 89.3234
1372.125 | 115.0269 | -89.2868 | 25.589 | -0.011291 | 0.068069 | 0.01568 | 0.022898 | -0.00083525 | -0.004251 | 0.0015531 | -0.0046081 | 0.025502 | 0.021412 | 0.017464 | -0.00095065 | 0.017316 | -0.0019205 | -0.059509 | 0.09613 | -0.059509 | -0.064087 | 0.082397 | -0.027466 | -0.013733 | -0.018311 | 0.073242 | -0.068665 | 0.004578 | 0.059509 | -0.018311 | 0.09613 | 89.2273 | -25.4929 | -25.6531 | 89.3692 | 89.2731 | 89.2593 | 0.045776 | 0.032043 | 89.2181 | -25.5157 | -25.5844 | 89.3463 | 89.3829 | 89.2685 | 0.16479 | 0.050354 | 0.14191 | -0.004578 | 0.12817 | 0.073243 | 0.15564 | 0.14191 | 89.3829 | 89.36 | -25.6485 | -25.6577 | 89.2227 | 89.2914 | 89.2273 | 89.2685
1373.875 | 115.0772 | -89.2685 | 25.5569 | -0.011291 | 0.065292 | 0.014825 | 0.019053 | -0.001476 | -0.0040374 | -0.0029331 | -0.0015565 | 0.021657 | 0.019489 | 0.0149 | -0.0020187 | 0.019239 | -0.0017069 | -0.032043 | 0.054932 | -0.045776 | 0.022888 | 0.1831 | 0.073242 | 0.064087 | 0.050354 | 0.068665 | -0.059509 | 0.068665 | 0.15564 | 0.10529 | 0.16479 | 89.2227 | -25.502 | -25.5341 | 89.4516 | 89.3326 | 89.3417 | 0.10986 | 0.11902 | 89.209 | -25.4883 | -25.4883 | 89.4241 | 89.4333 | 89.3738 | 0.2243 | 0.16479 | 0.22888 | 0.068664 | 0.21515 | 0.12817 | 0.10071 | 0.12817 | 89.3234 | 89.3372 | -25.6027 | -25.6165 | 89.2914 | 89.3372 | 89.2365 | 89.3188
1375.5625 | 114.9673 | -89.2593 | 25.5341 | -0.0036622 | 0.067855 | 0.016748 | 0.021403 | -0.002117 | -0.0021148 | -0.0027195 | -0.0046081 | 0.025502 | 0.018848 | 0.012123 | 0.0013991 | 0.019666 | -0.0051247 | -0.054932 | 0.07782 | -0.059509 | -0.054932 | 0.07782 | -0.032043 | -0.022888 | -0.036621 | 0.09613 | -0.07782 | -0.004578 | 0.027466 | -0.032043 | 0.09613 | 89.1998 | -25.4562 | -25.589 | 89.3372 | 89.2365 | 89.2273 | 0.036621 | 0.027466 | 89.1815 | -25.4379 | -25.5386 | 89.2868 | 89.3555 | 89.2273 | 0.17395 | 0.045777 | 0.13733 | 0.004577 | 0.10529 | 0.073242 | 0.13733 | 0.17395 | 89.3372 | 89.3555 | -25.5936 | -25.6119 | 89.2044 | 89.2548 | 89.2044 | 89.2227
1377.3125 | 114.9765 | -89.2731 | 25.5753 | -0.011291 | 0.064865 | 0.015253 | 0.020548 | 0.00044655 | -0.00061944 | -0.0044285 | -0.0046081 | 0.021443 | 0.01778 | 0.015327 | -0.0065049 | 0.016034 | -0.0036295 | -0.050354 | 0.050354 | -0.045776 | -0.013733 | 0.12817 | 0.036621 | 0.054932 | -0.009155 | 0.068665 | -0.059509 | -0.004578 | 0.073242 | 0.009155 | 0.1236 | 89.2273 | -25.5249 | -25.589 | 89.4012 | 89.328 | 89.3097 | 0.10071 | 0.082397 | 89.2136 | -25.5066 | -25.5798 | 89.3463 | 89.3967 | 89.2822 | 0.1831 | 0.068664 | 0.17395 | 0.032043 | 0.13275 | 0.054931 | 0.09613 | 0.12817 | 89.3234 | 89.3417 | -25.621 | -25.6348 | 89.2593 | 89.2685 | 89.2227 | 89.2639
1379.0625 | 115.004 | -89.2365 | 25.5203 | -0.0036622 | 0.065505 | 0.016534 | 0.020335 | -0.0019034 | -0.0027556 | -0.00015591 | 0.0014953 | 0.022939 | 0.01778 | 0.023445 | -0.00052345 | 0.018598 | -0.0017069 | -0.073242 | 0.045776 | -0.059509 | -0.018311 | 0.13275 | -0.004578 | 0.022888 | -0.004578 | 0.045776 | -0.073242 | 0.045776 | 0.10529 | 0.027466 | 0.14191 | 89.1769 | -25.4745 | -25.5386 | 89.3692 | 89.2593 | 89.2319 | 0.082397 | 0.054931 | 89.1632 | -25.4745 | -25.4745 | 89.3417 | 89.3784 | 89.2639 | 0.21515 | 0.10071 | 0.19226 | 0.041198 | 0.17853 | 0.11902 | 0.10528 | 0.11902 | 89.2822 | 89.2822 | -25.5798 | -25.5936 | 89.2181 | 89.2822 | 89.1632 | 89.2319
1380.75 | 114.8895 | -89.2502 | 25.5524 | 0.011597 | 0.066574 | 0.017175 | 0.025248 | 0.00066015 | -0.0027556 | 0.00091209 | -0.0076599 | 0.025289 | 0.02013 | 0.0078507 | -0.0022325 | 0.019025 | -0.0014931 | -0.091553 | 0.091553 | -0.082397 | -0.09613 | 0.032043 | -0.082397 | -0.064087 | -0.07782 | 0.073242 | -0.07782 | -0.032043 | 0.013733 | -0.064087 | 0.086975 | 89.1678 | -25.4608 | -25.6485 | 89.2822 | 89.1861 | 89.1678 | 0.01831 | 0 | 89.1724 | -25.4791 | -25.5844 | 89.2639 | 89.3372 | 89.1861 | 0.16479 | 0.013733 | 0.11444 | -0.013733 | 0.091553 | 0.045777 | 0.17395 | 0.15106 | 89.3417 | 89.3234 | -25.6348 | -25.6302 | 89.1541 | 89.2181 | 89.1586 | 89.1724
1382.4844 | 114.949 | -89.2456 | 25.5249 | -0.0036622 | 0.06401 | 0.016534 | 0.021617 | -0.0019034 | -0.0010468 | -0.00058311 | -0.0015565 | 0.024648 | 0.019275 | 0.011482 | -0.00095065 | 0.017957 | -0.0034159 | -0.064087 | 0.091553 | -0.07782 | -0.050354 | 0.10071 | -0.009155 | -0.013733 | -0.004578 | 0.068665 | -0.073242 | 0.022888 | 0.10071 | 0.013733 | 0.13275 | 89.1678 | -25.4333 | -25.5753 | 89.3463 | 89.2319 | 89.2364 | 0.064087 | 0.068665 | 89.1724 | -25.4562 | -25.502 | 89.3463 | 89.3784 | 89.2593 | 0.20599 | 0.086975 | 0.17853 | 0.027466 | 0.17395 | 0.09613 | 0.16937 | 0.14191 | 89.3372 | 89.3143 | -25.6027 | -25.5981 | 89.1953 | 89.2685 | 89.1815 | 89.241
1384.1719 | 114.9902 | -89.2227 | 25.502 | -0.0036622 | 0.064437 | 0.016962 | 0.021617 | -0.0027578 | -0.00040584 | -0.0014377 | 0.0014953 | 0.023366 | 0.019916 | 0.018104 | -0.0011643 | 0.01753 | -0.0040567 | -0.050354 | 0.045776 | -0.041199 | -0.013733 | 0.16022 | -0.004578 | 0.045776 | 0.050354 | 0.036621 | -0.045776 | 0.050354 | 0.11902 | 0.045776 | 0.15564 | 89.1815 | -25.4562 | -25.5157 | 89.3829 | 89.2685 | 89.2181 | 0.086975 | 0.036621 | 89.1769 | -25.4654 | -25.4517 | 89.3417 | 89.3784 | 89.2685 | 0.20142 | 0.091552 | 0.20142 | 0.027466 | 0.16479 | 0.09613 | 0.086975 | 0.082397 | 89.2685 | 89.2593 | -25.5432 | -25.5478 | 89.209 | 89.2731 | 89.1724 | 89.2731
1385.9375 | 115.004 | -89.2639 | 25.5249 | -0.0036622 | 0.063156 | 0.014612 | 0.020548 | -0.0025442 | -0.0021148 | -0.0018649 | 0.0014953 | 0.023152 | 0.019703 | 0.016823 | -0.0013779 | 0.018812 | -0.0014931 | -0.073242 | 0.068665 | -0.064087 | -0.041199 | 0.091553 | -0.018311 | 0.018311 | -0.022888 | 0.045776 | -0.068665 | 0.013733 | 0.10986 | 0.045776 | 0.14191 | 89.1998 | -25.4562 | -25.5661 | 89.3555 | 89.2822 | 89.2456 | 0.082398 | 0.045776 | 89.1953 | -25.4791 | -25.5112 | 89.3738 | 89.4058 | 89.3097 | 0.21057 | 0.11444 | 0.15564 | 0.022888 | 0.17853 | 0.082398 | 0.13275 | 0.11444 | 89.3326 | 89.3097 | -25.589 | -25.5936 | 89.2227 | 89.2776 | 89.1907 | 89.241
1387.6875 | 118.0756 | -117.6453 | 0.32044 | -0.0036622 | 0.06636 | 0.016107 | 0.024821 | 0.0019418 | -0.0012604 | -0.0033603 | -0.0015565 | 0.024007 | 0.019916 | 0.0089187 | -0.00030965 | 0.01988 | -0.00042513 | -0.073242 | 0.10529 | -0.073242 | -0.064087 | 0.054932 | -0.064087 | -0.045776 | -0.045776 | 0.10529 | -0.064087 | -0.027466 | 0.041199 | -0.050354 | 0.10529 | 117.572 | -0.21515 | -0.38452 | 117.7002 | 117.5995 | 117.5812 | 0.027466 | 0.009155 | 117.5812 | -0.21515 | -0.3479 | 117.6865 | 117.7506 | 117.5949 | 0.16937 | 0.013733 | 0.12817 | 0.009155 | 0.10529 | 0.036621 | 0.17853 | 0.16937 | 117.7506 | 117.7506 | -0.39368 | -0.38452 | 117.5812 | 117.6178 | 117.572 | 117.5995
1389.3594 | 118.5196 | -117.9565 | 0.27008 | -0.011291 | 0.065078 | 0.015253 | 0.020335 | 1.915e-05 | -0.00061944 | -0.0022921 | -0.0076599 | 0.02358 | 0.021198 | 0.018532 | -0.0024461 | 0.019452 | 0.0034201 | -0.041199 | 0.054932 | -0.032043 | 0.018311 | 0.1831 | 0.07782 | 0.09613 | 0.091553 | 0.068665 | -0.041199 | 0.091553 | 0.20142 | 0.11902 | 0.20599 | 117.9245 | -0.21515 | -0.25177 | 118.1396 | 118.0527 | 118.0344 | 0.12817 | 0.10986 | 117.9153 | -0.20142 | -0.17853 | 118.158 | 118.1625 | 118.0756 | 0.24719 | 0.16022 | 0.21515 | 0.050354 | 0.24262 | 0.13275 | 0.086975 | 0.10986 | 118.0115 | 118.0252 | -0.30212 | -0.31128 | 117.9749 | 118.0481 | 117.9153 | 118.0481
1391.0312 | 118.5425 | -118.2083 | 0.3067 | 0.0039673 | 0.064865 | 0.01333 | 0.02183 | 0.00044655 | -0.0027556 | -0.00036951 | 0.0014953 | 0.025929 | 0.020557 | 0.018104 | -0.0030869 | 0.016248 | -0.0012795 | -0.091553 | 0.10986 | -0.09613 | -0.09613 | 0.041199 | -0.041199 | -0.027466 | -0.07782 | 0.10529 | -0.073242 | -0.022888 | 0.045776 | -0.022888 | 0.10529 | 118.1122 | -0.19684 | -0.40283 | 118.2495 | 118.1808 | 118.1671 | 0.068664 | 0.054931 | 118.1351 | -0.20142 | -0.32959 | 118.2541 | 118.3136 | 118.1854 | 0.17853 | 0.050354 | 0.13733 | 0 | 0.11902 | 0.050354 | 0.20599 | 0.17853 | 118.3182 | 118.3136 | -0.40283 | -0.37994 | 118.1122 | 118.1854 | 118.1168 | 118.1305
1392.7656 | 118.689 | -118.2495 | 0.32501 | -0.011291 | 0.06636 | 0.016962 | 0.02183 | 0.001301 | -0.0023284 | -0.0018649 | 0.0014953 | 0.024861 | 0.020557 | 0.013405 | -9.605e-05 | 0.018171 | 0.00021567 | -0.032043 | 0.10071 | -0.073242 | -0.013733 | 0.11444 | 0.013733 | 0.027466 | 0.027466 | 0.09613 | -0.050354 | 0.050354 | 0.091553 | 0.013733 | 0.14648 | 118.1763 | -0.2243 | -0.33875 | 118.364 | 118.277 | 118.2632 | 0.10071 | 0.086975 | 118.1992 | -0.22888 | -0.27466 | 118.3411 | 118.396 | 118.2632 | 0.19684 | 0.064087 | 0.18768 | 0.059509 | 0.14191 | 0.10071 | 0.17395 | 0.14648 | 118.3502 | 118.3456 | -0.39825 | -0.37537 | 118.2358 | 118.2999 | 118.2175 | 118.277
1394.5156 | 118.8263 | -118.3228 | 0.3479 | 0.011597 | 0.065719 | 0.014398 | 0.020121 | -0.0012624 | -0.003183 | -0.00079691 | -0.0046081 | 0.02358 | 0.019703 | 0.017464 | 0.00054475 | 0.020307 | -0.00021153 | -0.068665 | 0.09613 | -0.082397 | -0.064087 | 0.068665 | -0.054932 | -0.004578 | 0 | 0.068665 | -0.054932 | 0.059509 | 0.11444 | 0.032043 | 0.15564 | 118.2404 | -0.25177 | -0.41199 | 118.3914 | 118.3182 | 118.2678 | 0.077819 | 0.027465 | 118.2678 | -0.27924 | -0.28839 | 118.4372 | 118.4784 | 118.3548 | 0.21057 | 0.086975 | 0.15106 | 0.01831 | 0.16937 | 0.11444 | 0.17853 | 0.1236 | 118.4189 | 118.3914 | -0.4303 | -0.40283 | 118.2587 | 118.3823 | 118.2541 | 118.3228
1396.1875 | 118.8538 | -118.5242 | 0.27466 | -0.0036622 | 0.067428 | 0.014398 | 0.022898 | -0.00040805 | -0.003183 | -0.0033603 | -0.0015565 | 0.025289 | 0.018848 | 0.015541 | -0.00095065 | 0.018812 | -0.0014931 | -0.086975 | 0.10071 | -0.09613 | -0.10071 | 0.032043 | -0.07782 | -0.045776 | -0.054932 | 0.09613 | -0.059509 | -0.004578 | 0.027466 | -0.027466 | 0.10986 | 118.428 | -0.17395 | -0.37537 | 118.5562 | 118.4784 | 118.4463 | 0.050354 | 0.01831 | 118.4647 | -0.17853 | -0.27924 | 118.5516 | 118.634 | 118.4967 | 0.16937 | 0.032043 | 0.12817 | -0.004578 | 0.086975 | 0.054931 | 0.19684 | 0.15564 | 118.6249 | 118.6203 | -0.37079 | -0.33417 | 118.4235 | 118.5196 | 118.4372 | 118.4692
1397.9375 | 119.0369 | -118.5791 | 0.24719 | -0.011291 | 0.064224 | 0.013757 | 0.020121 | -0.00019445 | -0.004892 | -0.0018649 | -0.0046081 | 0.019948 | 0.015644 | 0.0076371 | -0.0024461 | 0.017957 | -0.0010659 | -0.059509 | 0.050354 | -0.036621 | -0.027466 | 0.13275 | 0.022888 | 0.054932 | 0.022888 | 0.054932 | -0.050354 | 0.073242 | 0.15106 | 0.10071 | 0.1831 | 118.5425 | -0.19684 | -0.27466 | 118.7119 | 118.634 | 118.602 | 0.091553 | 0.059509 | 118.5287 | -0.19226 | -0.17395 | 118.7302 | 118.7622 | 118.6798 | 0.23346 | 0.15106 | 0.16937 | 0.009155 | 0.20142 | 0.1236 | 0.086975 | 0.10529 | 118.6295 | 118.634 | -0.28381 | -0.29755 | 118.5516 | 118.6523 | 118.5196 | 118.602
1399.6875 | 119.0231 | -118.7119 | 0.27466 | 0.0039673 | 0.067214 | 0.014185 | 0.023753 | -0.0029714 | -0.0016876 | -0.0020785 | 0.0014953 | 0.025716 | 0.016712 | 0.0102 | -0.0033005 | 0.019452 | -0.0014931 | -0.041199 | 0.082397 | -0.073242 | -0.041199 | 0.09613 | -0.027466 | -0.013733 | -0.032043 | 0.091553 | -0.045776 | 0.009155 | 0.059509 | -0.032043 | 0.11444 | 118.6386 | -0.19226 | -0.31586 | 118.808 | 118.6981 | 118.6844 | 0.059509 | 0.045776 | 118.6661 | -0.18311 | -0.2655 | 118.7714 | 118.8263 | 118.6798 | 0.16022 | 0.013733 | 0.16937 | 0.032043 | 0.10528 | 0.054931 | 0.15564 | 0.13733 | 118.7943 | 118.8034 | -0.3479 | -0.32043 | 118.6707 | 118.721 | 118.6707 | 118.6798
1401.4219 | 119.0964 | -118.7668 | 0.27466 | 0.0039673 | 0.065292 | 0.012689 | 0.02183 | -0.0029714 | -0.0038238 | -0.0029331 | -0.0046081 | 0.024434 | 0.020557 | 0.01725 | -0.0056503 | 0.017743 | -0.0012795 | -0.082397 | 0.10529 | -0.09613 | -0.086975 | 0.059509 | -0.036621 | -0.036621 | -0.086975 | 0.09613 | -0.068665 | -0.022888 | 0.068665 | -0.009155 | 0.10986 | 118.6707 | -0.16937 | -0.36163 | 118.8263 | 118.7302 | 118.7302 | 0.059509 | 0.059509 | 118.6981 | -0.17853 | -0.29755 | 118.8354 | 118.8766 | 118.7576 | 0.17853 | 0.05951 | 0.15564 | 0.009155 | 0.13733 | 0.045777 | 0.20142 | 0.16479 | 118.8721 | 118.8629 | -0.37079 | -0.34332 | 118.6798 | 118.7439 | 118.6844 | 118.6798
1403.1094 | 119.1925 | -118.8538 | 0.29755 | -0.0036622 | 0.064651 | 0.012048 | 0.020762 | -0.0012624 | -0.0027556 | -0.0022921 | -0.0015565 | 0.023152 | 0.01778 | 0.021522 | -0.0054367 | 0.018812 | -0.00021153 | -0.073242 | 0.082397 | -0.068665 | -0.054932 | 0.10071 | -0.004578 | -0.009155 | -0.07782 | 0.091553 | -0.073242 | -0.009155 | 0.068665 | 0.009155 | 0.082397 | 118.7851 | -0.21515 | -0.35248 | 118.9545 | 118.8446 | 118.8492 | 0.05951 | 0.064087 | 118.7805 | -0.20599 | -0.3067 | 118.9224 | 118.9362 | 118.8629 | 0.15564 | 0.082397 | 0.16937 | 0.013733 | 0.14191 | 0.064087 | 0.15106 | 0.16479 | 118.9362 | 118.9453 | -0.36621 | -0.37079 | 118.7988 | 118.8446 | 118.7805 | 118.7759
1404.8594 | 119.3253 | -118.9041 | 0.27008 | -0.0036622 | 0.064437 | 0.015253 | 0.02183 | -0.002117 | -0.0046782 | -0.0027195 | -0.0015565 | 0.021016 | 0.021198 | 0.021095 | -0.00030965 | 0.019452 | -0.00042513 | -0.054932 | 0.073242 | -0.032043 | -0.018311 | 0.11444 | 0 | 0.036621 | 0.018311 | 0.064087 | -0.045776 | 0.041199 | 0.10529 | 0.064087 | 0.14648 | 118.8721 | -0.19684 | -0.28839 | 119.0186 | 118.9407 | 118.9041 | 0.068664 | 0.032043 | 118.8583 | -0.20599 | -0.22888 | 119.0094 | 119.0506 | 118.9682 | 0.19226 | 0.10986 | 0.14648 | 0.013732 | 0.15106 | 0.086975 | 0.10529 | 0.10986 | 118.9774 | 118.9682 | -0.30212 | -0.31586 | 118.8858 | 118.9453 | 118.8492 | 118.9224
1406.5938 | 119.4397 | -118.9728 | 0.2655 | -0.0036622 | 0.064224 | 0.015466 | 0.021617 | -0.0040396 | -0.0010468 | -0.0022921 | -0.0015565 | 0.022084 | 0.018207 | 0.025154 | 0.00097195 | 0.020093 | -0.0021341 | -0.050354 | 0.068665 | -0.027466 | -0.004578 | 0.14191 | 0.045776 | 0.07782 | 0.059509 | 0.064087 | -0.045776 | 0.10071 | 0.17395 | 0.12817 | 0.20142 | 118.9453 | -0.19684 | -0.27008 | 119.1147 | 119.0506 | 119.0186 | 0.10529 | 0.073242 | 118.927 | -0.20142 | -0.16479 | 119.1467 | 119.1742 | 119.101 | 0.24719 | 0.17395 | 0.16937 | 0.022888 | 0.21973 | 0.14648 | 0.096131 | 0.10986 | 119.0414 | 119.0369 | -0.29297 | -0.31128 | 118.9682 | 119.0735 | 118.9224 | 119.0323
1408.2656 | 119.4214 | -118.9865 | 0.31128 | 0.0039673 | 0.065933 | 0.01568 | 0.024821 | -0.0010488 | -0.0010468 | -0.00079691 | 0.0014953 | 0.024434 | 0.018207 | 0.013832 | -0.0037277 | 0.020307 | -0.00021153 | -0.064087 | 0.09613 | -0.091553 | -0.054932 | 0.068665 | -0.009155 | 0.004578 | -0.004578 | 0.10986 | -0.068665 | 0.041199 | 0.10986 | 0.032043 | 0.13275 | 118.895 | -0.21515 | -0.36621 | 119.0552 | 118.9911 | 118.9774 | 0.096131 | 0.082398 | 118.9178 | -0.20142 | -0.27008 | 119.0964 | 119.1193 | 119.0186 | 0.20142 | 0.10071 | 0.16022 | 0.036621 | 0.17853 | 0.10986 | 0.18768 | 0.17853 | 119.0826 | 119.0964 | -0.40283 | -0.37994 | 118.9316 | 119.0277 | 118.9224 | 118.9819
1410.0156 | 119.5541 | -119.0552 | 0.29755 | -0.011291 | 0.066146 | 0.01333 | 0.020335 | -0.0023306 | -0.0029694 | -0.0012241 | -0.0015565 | 0.024434 | 0.019275 | 0.022591 | -9.605e-05 | 0.018598 | 0.0012839 | -0.059509 | 0.064087 | -0.059509 | -0.027466 | 0.10529 | 0.018311 | 0.032043 | 0.018311 | 0.068665 | -0.050354 | 0.064087 | 0.16022 | 0.09613 | 0.17395 | 118.9957 | -0.23346 | -0.32501 | 119.1605 | 119.0872 | 119.0735 | 0.091552 | 0.07782 | 119.0048 | -0.22888 | -0.23346 | 119.2154 | 119.2291 | 119.1513 | 0.2243 | 0.14648 | 0.16479 | 0.032043 | 0.21057 | 0.11444 | 0.1236 | 0.11902 | 119.1193 | 119.1238 | -0.35705 | -0.3479 | 119.0277 | 119.1193 | 118.9957 | 119.0735
1411.75 | 119.4946 | -119.1422 | 0.32501 | 0.0039673 | 0.06871 | 0.015894 | 0.023112 | 0.001301 | -0.0027556 | -0.00058311 | 0.0014953 | 0.022512 | 0.02013 | 0.015755 | 0.00097195 | 0.018171 | -0.0034159 | -0.07782 | 0.10529 | -0.082397 | -0.09613 | -0.004578 | -0.10071 | -0.059509 | -0.073242 | 0.09613 | -0.068665 | -0.013733 | 0.009155 | -0.050354 | 0.091553 | 119.0598 | -0.21973 | -0.42114 | 119.1376 | 119.0826 | 119.0414 | 0.022888 | -0.018311 | 119.0735 | -0.22888 | -0.33875 | 119.1513 | 119.2337 | 119.0918 | 0.16022 | 0.018311 | 0.077819 | -0.013733 | 0.07782 | 0.054932 | 0.18768 | 0.16479 | 119.2474 | 119.2383 | -0.40741 | -0.39368 | 119.046 | 119.1284 | 119.0643 | 119.0689
1413.4219 | 119.6548 | -119.1742 | 0.31128 | -0.0036622 | 0.063369 | 0.014612 | 0.020335 | 0.00044655 | -0.00019224 | -0.00015591 | -0.0015565 | 0.022939 | 0.019062 | 0.023018 | -0.0018051 | 0.019025 | 0.00021567 | -0.07782 | 0.059509 | -0.054932 | -0.036621 | 0.10986 | -0.004578 | 0.036621 | -0.004578 | 0.082397 | -0.054932 | 0.045776 | 0.13275 | 0.059509 | 0.15106 | 119.1193 | -0.25177 | -0.3479 | 119.2841 | 119.2108 | 119.1696 | 0.091553 | 0.050354 | 119.1193 | -0.22888 | -0.2655 | 119.3069 | 119.3253 | 119.2337 | 0.20599 | 0.11444 | 0.16479 | 0.018311 | 0.18768 | 0.10071 | 0.11444 | 0.13733 | 119.2337 | 119.2566 | -0.36621 | -0.36621 | 119.1376 | 119.22 | 119.0964 | 119.1696
1415.1719 | 119.7876 | -119.252 | 0.27924 | 0.0039673 | 0.062728 | 0.015039 | 0.022257 | -0.0033986 | -0.0040374 | 5.7688e-05 | -0.0046081 | 0.023152 | 0.019703 | 0.01725 | -0.0013779 | 0.018812 | -0.0049111 | -0.018311 | 0.045776 | -0.041199 | 0.032043 | 0.18768 | 0.07782 | 0.086975 | 0.1236 | 0.068665 | -0.022888 | 0.11444 | 0.21515 | 0.15106 | 0.21057 | 119.2108 | -0.23346 | -0.24719 | 119.4397 | 119.339 | 119.3298 | 0.12817 | 0.11902 | 119.2291 | -0.21057 | -0.16479 | 119.4672 | 119.4626 | 119.4031 | 0.23346 | 0.17395 | 0.22888 | 0.073242 | 0.23804 | 0.13733 | 0.086975 | 0.091553 | 119.2978 | 119.3207 | -0.32043 | -0.30212 | 119.2841 | 119.3665 | 119.2337 | 119.3756
1416.9219 | 119.8059 | -119.2474 | 0.28839 | -0.0036622 | 0.06636 | 0.015894 | 0.023112 | -0.00062165 | -0.0036102 | -0.00079691 | -0.0015565 | 0.024007 | 0.018634 | 0.013405 | 0.00097195 | 0.019025 | -0.0014931 | -0.022888 | 0.086975 | -0.050354 | 0.013733 | 0.15564 | 0.041199 | 0.073242 | 0.073242 | 0.045776 | -0.036621 | 0.11444 | 0.17395 | 0.10529 | 0.2243 | 119.1971 | -0.20142 | -0.27466 | 119.4031 | 119.3207 | 119.2886 | 0.1236 | 0.091553 | 119.2108 | -0.24262 | -0.17395 | 119.4214 | 119.4717 | 119.3527 | 0.26093 | 0.14191 | 0.20599 | 0.064087 | 0.21057 | 0.15106 | 0.13733 | 0.082397 | 119.3344 | 119.2932 | -0.33875 | -0.32501 | 119.2612 | 119.3619 | 119.2245 | 119.3207
1418.6562 | 119.8471 | -119.3344 | 0.3067 | 0.0039673 | 0.067855 | 0.017175 | 0.020762 | 0.0017282 | -0.002542 | 0.00048489 | -0.0015565 | 0.022512 | 0.020343 | 0.02195 | -0.00052345 | 0.020521 | -0.0029885 | 0.009155 | 0.073242 | -0.041199 | 0.036621 | 0.17853 | 0.045776 | 0.059509 | 0.11444 | 0.073242 | -0.032043 | 0.10071 | 0.16937 | 0.086975 | 0.20142 | 119.2932 | -0.23346 | -0.27008 | 119.5129 | 119.3939 | 119.3802 | 0.10071 | 0.086975 | 119.3024 | -0.23346 | -0.20599 | 119.5038 | 119.5358 | 119.4214 | 0.23346 | 0.11902 | 0.21973 | 0.07782 | 0.20142 | 0.13275 | 0.11444 | 0.10529 | 119.4077 | 119.4077 | -0.3479 | -0.33874 | 119.371 | 119.4351 | 119.3436 | 119.4489
1420.4062 | 119.8242 | -119.426 | 0.32959 | -0.011291 | 0.067001 | 0.012048 | 0.025462 | -0.002117 | -0.0029694 | -0.0029331 | -0.0015565 | 0.026143 | 0.020771 | 0.0091325 | -9.605e-05 | 0.01753 | -0.0025613 | -0.086975 | 0.082397 | -0.073242 | -0.10529 | 0.027466 | -0.086975 | -0.059509 | -0.050354 | 0.10071 | -0.059509 | -0.004578 | 0.018311 | -0.041199 | 0.10071 | 119.3527 | -0.24719 | -0.43488 | 119.4534 | 119.3665 | 119.339 | 0.013733 | -0.013733 | 119.3665 | -0.22888 | -0.33417 | 119.4443 | 119.5267 | 119.3848 | 0.16022 | 0.01831 | 0.10071 | -0.032044 | 0.07782 | 0.054931 | 0.15564 | 0.16022 | 119.5084 | 119.5267 | -0.40283 | -0.3891 | 119.3207 | 119.4214 | 119.339 | 119.3756
1422.0781 | 119.8425 | -119.4855 | 0.34332 | -0.0036622 | 0.066787 | 0.015894 | 0.021403 | 0.0010874 | -0.0019012 | -0.0044285 | -0.0015565 | 0.024434 | 0.018634 | 0.014259 | -0.0011643 | 0.017316 | -0.0014931 | -0.091553 | 0.11902 | -0.068665 | -0.09613 | 0.009155 | -0.086975 | -0.059509 | -0.086975 | 0.10986 | -0.068665 | -0.013733 | 0.013733 | -0.054932 | 0.091553 | 119.4168 | -0.2243 | -0.43945 | 119.4946 | 119.426 | 119.3985 | 0.009156 | -0.01831 | 119.4168 | -0.23346 | -0.35706 | 119.4992 | 119.577 | 119.4305 | 0.16022 | 0.013733 | 0.07782 | -0.027465 | 0.082398 | 0.054932 | 0.18768 | 0.17853 | 119.6045 | 119.5953 | -0.41199 | -0.41199 | 119.3893 | 119.4717 | 119.3939 | 119.3985
1423.8281 | 119.9707 | -119.5038 | 0.35248 | 0.0039673 | 0.066787 | 0.016107 | 0.023112 | 0.0017282 | -0.00040584 | -0.0010105 | -0.0015565 | 0.024434 | 0.019062 | 0.019386 | -0.0018051 | 0.019025 | -0.0017069 | -0.054932 | 0.09613 | -0.064087 | -0.032043 | 0.11444 | 0 | 0.004578 | 0 | 0.10986 | -0.059509 | 0.036621 | 0.11902 | 0.022888 | 0.13733 | 119.4397 | -0.25635 | -0.38452 | 119.6182 | 119.5084 | 119.5038 | 0.068665 | 0.064087 | 119.4443 | -0.24262 | -0.31586 | 119.6228 | 119.6411 | 119.5267 | 0.19684 | 0.082397 | 0.17853 | 0.032044 | 0.17853 | 0.09613 | 0.16022 | 0.16937 | 119.5999 | 119.6136 | -0.41657 | -0.41199 | 119.4717 | 119.5404 | 119.4489 | 119.5038
1425.5781 | 119.9203 | -119.6182 | 0.30212 | -0.011291 | 0.067642 | 0.016321 | 0.022257 | 0.00066015 | -0.002542 | -0.0046421 | -0.0015565 | 0.023366 | 0.019916 | 0.015114 | -0.0024461 | 0.020521 | -0.0012795 | -0.091553 | 0.10986 | -0.07782 | -0.10529 | 0 | -0.091553 | -0.068665 | -0.10986 | 0.091553 | -0.091553 | -0.013733 | 0.018311 | -0.059509 | 0.09613 | 119.5404 | -0.19226 | -0.40741 | 119.6182 | 119.5496 | 119.5267 | 0.009155 | -0.013733 | 119.5267 | -0.21057 | -0.31586 | 119.6365 | 119.7144 | 119.5587 | 0.18768 | 0.032044 | 0.07782 | -0.027466 | 0.10986 | 0.07782 | 0.18768 | 0.18311 | 119.7281 | 119.7098 | -0.37994 | -0.39368 | 119.5129 | 119.6045 | 119.5267 | 119.5084
1427.3281 | 120.0485 | -119.664 | 0.29297 | -0.011291 | 0.068923 | 0.014185 | 0.022257 | -0.00040805 | -0.0010468 | -0.00079691 | -0.0015565 | 0.023793 | 0.018634 | 0.015327 | -0.00073705 | 0.017316 | -0.0025613 | -0.036621 | 0.086975 | -0.068665 | -0.036621 | 0.1236 | -0.009155 | 0.004578 | 0.009155 | 0.082397 | -0.082397 | 0.054932 | 0.10986 | 0.036621 | 0.14648 | 119.5953 | -0.20599 | -0.32959 | 119.7876 | 119.6686 | 119.6548 | 0.073243 | 0.05951 | 119.5816 | -0.21057 | -0.23804 | 119.7739 | 119.8105 | 119.7006 | 0.22888 | 0.11902 | 0.19226 | 0.032044 | 0.19226 | 0.13733 | 0.15564 | 0.16479 | 119.751 | 119.7464 | -0.36163 | -0.37537 | 119.6274 | 119.7189 | 119.6274 | 119.6732
1429.0781 | 120.0806 | -119.7372 | 0.31586 | -0.018921 | 0.068069 | 0.016107 | 0.020762 | 0.00066015 | -0.00083304 | 0.00048489 | 0.0014953 | 0.025929 | 0.017994 | 0.013618 | -0.0024461 | 0.01988 | -0.00085233 | -0.036621 | 0.086975 | -0.064087 | -0.050354 | 0.09613 | -0.022888 | 0.009155 | -0.013733 | 0.10071 | -0.064087 | 0.027466 | 0.068665 | -0.013733 | 0.11902 | 119.6732 | -0.22888 | -0.36621 | 119.8334 | 119.7464 | 119.7144 | 0.073242 | 0.041199 | 119.6732 | -0.21515 | -0.28839 | 119.8059 | 119.8563 | 119.7235 | 0.18311 | 0.050354 | 0.16022 | 0.013733 | 0.13275 | 0.091553 | 0.15106 | 0.1648 | 119.8242 | 119.838 | -0.37994 | -0.37994 | 119.6869 | 119.7647 | 119.7006 | 119.7235
1430.8281 | 120.2545 | -119.7189 | 0.27924 | 0.011597 | 0.065505 | 0.016321 | 0.018626 | -0.003185 | -0.0021148 | 5.7688e-05 | 0.0045471 | 0.022725 | 0.017994 | 0.02195 | -0.00030965 | 0.020948 | 2.068e-06 | -0.009155 | 0.059509 | -0.045776 | 0.027466 | 0.1831 | 0.036621 | 0.064087 | 0.086975 | 0.068665 | -0.041199 | 0.10986 | 0.1831 | 0.10986 | 0.21057 | 119.6732 | -0.21973 | -0.25177 | 119.902 | 119.783 | 119.7556 | 0.10986 | 0.082397 | 119.6777 | -0.21057 | -0.16937 | 119.902 | 119.9295 | 119.8288 | 0.25177 | 0.15106 | 0.22888 | 0.073242 | 0.2243 | 0.15106 | 0.10528 | 0.10986 | 119.7784 | 119.7876 | -0.32501 | -0.32043 | 119.7464 | 119.8288 | 119.7098 | 119.8059
1432.5156 | 120.2774 | -119.7556 | 0.28839 | -0.0036622 | 0.065505 | 0.018671 | 0.022685 | 0.00301 | -0.002542 | -0.0018649 | 0.0014953 | 0.024648 | 0.019062 | 0.013832 | -0.00052345 | 0.020734 | -0.0038431 | -0.013733 | 0.050354 | -0.032043 | 0.022888 | 0.18768 | 0.054932 | 0.059509 | 0.086975 | 0.059509 | -0.036621 | 0.10071 | 0.18768 | 0.09613 | 0.19684 | 119.7235 | -0.23804 | -0.2655 | 119.9432 | 119.8151 | 119.8105 | 0.091552 | 0.086975 | 119.7189 | -0.22888 | -0.18768 | 119.9432 | 119.9524 | 119.8517 | 0.23346 | 0.13275 | 0.21973 | 0.054931 | 0.2243 | 0.13733 | 0.082397 | 0.09613 | 119.8059 | 119.8151 | -0.32043 | -0.32501 | 119.7784 | 119.8563 | 119.7418 | 119.8425
1434.2656 | 120.3323 | -119.783 | 0.27924 | -0.0036622 | 0.06401 | 0.015253 | 0.021403 | 1.915e-05 | -0.0040374 | -0.0020785 | 0.0014953 | 0.021871 | 0.01778 | 0.015968 | -0.0020187 | 0.020093 | -0.0010659 | -0.054932 | 0.036621 | -0.064087 | 0.009155 | 0.1831 | 0.064087 | 0.10071 | 0.082397 | 0.064087 | -0.050354 | 0.091553 | 0.20142 | 0.12817 | 0.20599 | 119.7189 | -0.24261 | -0.27008 | 119.9661 | 119.8837 | 119.8471 | 0.1648 | 0.12817 | 119.7327 | -0.21515 | -0.18768 | 119.9844 | 119.989 | 119.9112 | 0.25635 | 0.17853 | 0.24719 | 0.073242 | 0.25177 | 0.14191 | 0.10071 | 0.11444 | 119.8196 | 119.8471 | -0.34332 | -0.32959 | 119.7922 | 119.8746 | 119.7281 | 119.8654
1436.0156 | 120.2545 | -119.8975 | 0.30212 | 0.0039673 | 0.064865 | 0.012048 | 0.020548 | 0.00023275 | -0.002542 | -0.0035739 | -0.0076599 | 0.025075 | 0.01778 | 0.0067825 | -0.0062913 | 0.016248 | -0.0017069 | -0.10529 | 0.10986 | -0.091553 | -0.10529 | 0.041199 | -0.050354 | -0.018311 | -0.07782 | 0.10529 | -0.07782 | -0.036621 | 0.050354 | -0.022888 | 0.091553 | 119.8059 | -0.19226 | -0.40741 | 119.9387 | 119.8792 | 119.8471 | 0.073242 | 0.041199 | 119.8196 | -0.19684 | -0.33875 | 119.9478 | 119.989 | 119.8746 | 0.16937 | 0.054932 | 0.13275 | -0.013733 | 0.12817 | 0.041199 | 0.20142 | 0.18311 | 120.0073 | 120.0027 | -0.39368 | -0.37994 | 119.7922 | 119.8608 | 119.7922 | 119.8196
1437.6875 | 120.3049 | -119.9158 | 0.31586 | -0.011291 | 0.065933 | 0.015039 | 0.022044 | -0.0023306 | -0.0029694 | -0.0016513 | -0.0015565 | 0.025502 | 0.019703 | 0.011696 | -0.0022325 | 0.015821 | -0.0032021 | -0.073242 | 0.10529 | -0.091553 | -0.091553 | 0.045776 | -0.032043 | -0.004578 | -0.073242 | 0.10071 | -0.086975 | -0.009155 | 0.073242 | 0 | 0.12817 | 119.8242 | -0.21057 | -0.40741 | 119.9615 | 119.9112 | 119.8837 | 0.086975 | 0.05951 | 119.8288 | -0.21515 | -0.32501 | 119.989 | 120.0439 | 119.9158 | 0.21515 | 0.086975 | 0.13733 | 0 | 0.16022 | 0.07782 | 0.19684 | 0.18768 | 120.0211 | 120.0165 | -0.40741 | -0.40283 | 119.8242 | 119.9066 | 119.8425 | 119.8425
1439.4375 | 120.4239 | -119.9112 | 0.29297 | 0.0039673 | 0.06636 | 0.014612 | 0.02183 | 0.001301 | -0.001474 | 0.00027129 | -0.0076599 | 0.021443 | 0.019916 | 0.016395 | 0.0024673 | 0.018812 | -0.00085233 | -0.036621 | 0.07782 | -0.054932 | 0.018311 | 0.16479 | 0.027466 | 0.041199 | 0.059509 | 0.050354 | -0.032043 | 0.10529 | 0.16479 | 0.091553 | 0.2243 | 119.8563 | -0.21515 | -0.27466 | 120.076 | 119.9524 | 119.9387 | 0.096131 | 0.082398 | 119.8792 | -0.24261 | -0.18768 | 120.076 | 120.1355 | 120.0027 | 0.25635 | 0.1236 | 0.21973 | 0.073243 | 0.19684 | 0.13733 | 0.13275 | 0.082397 | 119.989 | 119.9615 | -0.3479 | -0.32501 | 119.9295 | 120.0165 | 119.8746 | 119.9707
1441.1094 | 120.4285 | -119.957 | 0.31128 | -0.0036622 | 0.065933 | 0.015039 | 0.020548 | 0.0023692 | -0.002542 | -0.0022921 | 0.0014953 | 0.022298 | 0.020984 | 0.018959 | -0.0026597 | 0.020093 | -0.0025613 | -0.064087 | 0.064087 | -0.041199 | -0.018311 | 0.15564 | 0.009155 | 0.050354 | 0.027466 | 0.064087 | -0.054932 | 0.050354 | 0.1236 | 0.041199 | 0.15564 | 119.9158 | -0.24719 | -0.32959 | 120.1126 | 120.0073 | 119.9661 | 0.091553 | 0.050354 | 119.902 | -0.24719 | -0.26092 | 120.0806 | 120.1126 | 119.9982 | 0.21057 | 0.096131 | 0.19684 | 0.022888 | 0.17853 | 0.10529 | 0.10529 | 0.11902 | 120.0211 | 120.0211 | -0.35248 | -0.36621 | 119.9387 | 120.0073 | 119.8929 | 119.9844
1442.8594 | 120.4514 | -120.0348 | 0.33417 | -0.011291 | 0.067855 | 0.015894 | 0.022685 | -0.0023306 | -0.004251 | -0.00015591 | -0.0015565 | 0.022725 | 0.020771 | 0.012123 | -0.0045823 | 0.019452 | -0.00085233 | -0.07782 | 0.091553 | -0.10986 | -0.073242 | 0.054932 | -0.022888 | 0 | -0.022888 | 0.10529 | -0.073242 | 0.018311 | 0.086975 | 0.022888 | 0.13733 | 119.9249 | -0.24261 | -0.40741 | 120.0897 | 120.0348 | 120.0119 | 0.10986 | 0.086975 | 119.9615 | -0.22888 | -0.31586 | 120.1218 | 120.1721 | 120.0577 | 0.21057 | 0.09613 | 0.16479 | 0.036621 | 0.16022 | 0.091553 | 0.20142 | 0.17853 | 120.1263 | 120.1401 | -0.44403 | -0.40741 | 119.9615 | 120.0531 | 119.957 | 120.0119
1444.5469 | 120.5154 | -120.0485 | 0.30212 | 0.0039673 | 0.063583 | 0.013971 | 0.020976 | -0.00083525 | -0.0021148 | -0.0031467 | -0.0015565 | 0.021871 | 0.022052 | 0.015114 | -0.0026597 | 0.01753 | 0.0032065 | -0.07782 | 0.050354 | -0.041199 | -0.032043 | 0.13733 | 0 | 0.036621 | 0.004578 | 0.059509 | -0.036621 | 0.064087 | 0.1236 | 0.054932 | 0.15106 | 120.0073 | -0.25177 | -0.33417 | 120.1859 | 120.0851 | 120.0485 | 0.07782 | 0.041199 | 120.0119 | -0.24261 | -0.23804 | 120.1721 | 120.1996 | 120.1035 | 0.18768 | 0.091553 | 0.17853 | 0.009156 | 0.16022 | 0.10071 | 0.091553 | 0.09613 | 120.0989 | 120.108 | -0.34332 | -0.33875 | 120.0165 | 120.1126 | 119.9707 | 120.0531
1446.2969 | 120.5887 | -120.0623 | 0.29755 | -0.0036622 | 0.06636 | 0.016321 | 0.022898 | 0.00044655 | -0.001474 | -0.0037875 | -0.0015565 | 0.02358 | 0.017139 | 0.017464 | 0.00075835 | 0.01988 | -0.0029885 | -0.004578 | 0.041199 | -0.036621 | 0.036621 | 0.17853 | 0.032043 | 0.064087 | 0.091553 | 0.064087 | -0.036621 | 0.10986 | 0.18768 | 0.10071 | 0.21973 | 120.0256 | -0.25635 | -0.26092 | 120.2408 | 120.1263 | 120.0943 | 0.10071 | 0.068664 | 120.0256 | -0.23346 | -0.18768 | 120.2499 | 120.282 | 120.163 | 0.25635 | 0.13733 | 0.21515 | 0.073242 | 0.2243 | 0.14648 | 0.07782 | 0.10071 | 120.1035 | 120.1263 | -0.33417 | -0.33417 | 120.0989 | 120.1721 | 120.0577 | 120.1538
1447.9844 | 120.5154 | -120.1492 | 0.32044 | -0.0036622 | 0.064224 | 0.016107 | 0.020335 | -0.0010488 | -0.0029694 | -0.0010105 | -0.0076599 | 0.023793 | 0.019916 | 0.014686 | -0.0058639 | 0.016248 | -0.0023477 | -0.036621 | 0.064087 | -0.059509 | -0.009155 | 0.13275 | 0.032043 | 0.050354 | 0 | 0.082397 | -0.045776 | -0.004578 | 0.086975 | 0.032043 | 0.10071 | 120.0897 | -0.25635 | -0.32959 | 120.282 | 120.1996 | 120.1813 | 0.10986 | 0.091552 | 120.1035 | -0.23804 | -0.32501 | 120.2362 | 120.2499 | 120.1813 | 0.14648 | 0.077819 | 0.19226 | 0.050354 | 0.13275 | 0.041198 | 0.1236 | 0.12817 | 120.2133 | 120.2316 | -0.37994 | -0.36621 | 120.1401 | 120.1447 | 120.1126 | 120.1492
1449.7344 | 120.6299 | -120.1538 | 0.32044 | -0.011291 | 0.062301 | 0.015253 | 0.020548 | -0.0033986 | -0.0019012 | -0.0029331 | 0.0014953 | 0.024434 | 0.021412 | 0.018532 | 0.00011755 | 0.018171 | -0.00085233 | -0.073242 | 0.07782 | -0.050354 | -0.032043 | 0.1236 | 0 | 0.032043 | -0.004578 | 0.059509 | -0.068665 | 0.036621 | 0.1236 | 0.07782 | 0.17395 | 120.1035 | -0.24262 | -0.35248 | 120.2774 | 120.1859 | 120.1538 | 0.082397 | 0.050354 | 120.0851 | -0.26093 | -0.28381 | 120.2774 | 120.3278 | 120.2316 | 0.24261 | 0.14649 | 0.17395 | 0.018311 | 0.19226 | 0.10529 | 0.12817 | 0.12817 | 120.2316 | 120.2133 | -0.37079 | -0.3891 | 120.1218 | 120.1904 | 120.0806 | 120.1492
1451.4062 | 120.5658 | -120.2316 | 0.32501 | -0.011291 | 0.065719 | 0.012048 | 0.021617 | -0.0051076 | -0.0036102 | -0.0035739 | -0.0046081 | 0.025075 | 0.016925 | 0.012978 | -0.0054367 | 0.016675 | -0.00042513 | -0.10529 | 0.09613 | -0.091553 | -0.086975 | 0.036621 | -0.045776 | -0.022888 | -0.073242 | 0.09613 | -0.091553 | -0.041199 | 0.041199 | -0.022888 | 0.09613 | 120.1401 | -0.22888 | -0.41199 | 120.2682 | 120.2087 | 120.1859 | 0.068665 | 0.045777 | 120.1401 | -0.22888 | -0.36621 | 120.2728 | 120.3278 | 120.2087 | 0.18768 | 0.068665 | 0.12817 | 0.004578 | 0.13275 | 0.050354 | 0.18768 | 0.18768 | 120.3278 | 120.3278 | -0.41657 | -0.41657 | 120.1447 | 120.1904 | 120.1263 | 120.1584
1453.0938 | 120.7031 | -120.2179 | 0.27924 | 0.011597 | 0.066574 | 0.017175 | 0.021403 | 0.0010874 | -0.00040584 | -0.0014377 | -0.0015565 | 0.023152 | 0.018634 | 0.020027 | 0.0028945 | 0.019666 | -0.00021153 | -0.027466 | 0.054932 | -0.018311 | 0.027466 | 0.17395 | 0.036621 | 0.07782 | 0.082397 | 0.064087 | -0.045776 | 0.10071 | 0.15106 | 0.086975 | 0.18768 | 120.1996 | -0.2243 | -0.25177 | 120.3918 | 120.2957 | 120.2545 | 0.096131 | 0.054932 | 120.1721 | -0.21515 | -0.17853 | 120.369 | 120.4056 | 120.3049 | 0.23346 | 0.13275 | 0.19226 | 0.045777 | 0.19684 | 0.14648 | 0.073243 | 0.10986 | 120.2728 | 120.282 | -0.29755 | -0.32501 | 120.2454 | 120.3186 | 120.1904 | 120.3003
1454.8281 | 120.6207 | -120.2316 | 0.31586 | 0.0039673 | 0.067214 | 0.012476 | 0.022471 | 0.00066015 | -0.004251 | -0.0027195 | -0.0076599 | 0.025929 | 0.020771 | 0.013618 | -0.00073705 | 0.019452 | -0.0023477 | -0.10529 | 0.09613 | -0.09613 | -0.091553 | 0.004578 | -0.086975 | -0.045776 | -0.082397 | 0.091553 | -0.07782 | -0.009155 | 0.032043 | -0.054932 | 0.09613 | 120.1355 | -0.21973 | -0.40741 | 120.2362 | 120.1859 | 120.1447 | 0.050354 | 0.009155 | 120.1538 | -0.2243 | -0.32501 | 120.2637 | 120.3278 | 120.1767 | 0.17395 | 0.022888 | 0.10071 | 0.004577 | 0.10986 | 0.068665 | 0.19226 | 0.16937 | 120.3278 | 120.3232 | -0.41199 | -0.39368 | 120.1401 | 120.2225 | 120.1263 | 120.1492
1456.5 | 120.7169 | -120.2637 | 0.3067 | -0.0036622 | 0.065292 | 0.014185 | 0.022044 | -0.0019034 | -0.0021148 | -0.0014377 | -0.0015565 | 0.022512 | 0.017994 | 0.020454 | -0.00073705 | 0.019452 | -0.0021341 | -0.045776 | 0.050354 | -0.054932 | -0.004578 | 0.16022 | -0.004578 | 0.045776 | 0.041199 | 0.054932 | -0.064087 | 0.041199 | 0.11902 | 0.054932 | 0.14648 | 120.2087 | -0.25635 | -0.31128 | 120.4239 | 120.3094 | 120.2591 | 0.10071 | 0.050354 | 120.1996 | -0.25177 | -0.2655 | 120.3827 | 120.4102 | 120.3186 | 0.21057 | 0.11902 | 0.21515 | 0.050354 | 0.18311 | 0.10529 | 0.10529 | 0.11902 | 120.314 | 120.3186 | -0.36163 | -0.37079 | 120.2591 | 120.3049 | 120.2179 | 120.3049
1458.25 | 120.6528 | -120.314 | 0.33875 | -0.011291 | 0.068496 | 0.017175 | 0.023112 | 0.0019418 | -0.003183 | -0.0018649 | -0.0076599 | 0.024007 | 0.016498 | 0.018104 | -0.0030869 | 0.019239 | -0.0023477 | -0.082397 | 0.086975 | -0.07782 | -0.09613 | 0.004578 | -0.09613 | -0.07782 | -0.10529 | 0.10529 | -0.059509 | -0.022888 | 0.013733 | -0.054932 | 0.10986 | 120.2362 | -0.25177 | -0.43488 | 120.3186 | 120.2362 | 120.2179 | 0 | -0.01831 | 120.2545 | -0.23346 | -0.36163 | 120.3278 | 120.4239 | 120.2591 | 0.16937 | 0.004577 | 0.082398 | -0.01831 | 0.073242 | 0.036621 | 0.16479 | 0.16479 | 120.401 | 120.4193 | -0.41657 | -0.39825 | 120.2179 | 120.2911 | 120.2316 | 120.2087
1459.9844 | 120.7031 | -120.369 | 0.31586 | -0.0036622 | 0.066787 | 0.016962 | 0.025462 | -0.00040805 | -0.0036102 | -0.0020785 | 0.0014953 | 0.02657 | 0.017566 | 0.014686 | 0.00033115 | 0.018812 | 0.00042947 | -0.10986 | 0.091553 | -0.091553 | -0.086975 | 0 | -0.09613 | -0.050354 | -0.091553 | 0.10986 | -0.086975 | -0.018311 | 0.009155 | -0.059509 | 0.10529 | 120.2774 | -0.2243 | -0.40283 | 120.369 | 120.3186 | 120.2728 | 0.041199 | -0.004577 | 120.282 | -0.20599 | -0.33417 | 120.3781 | 120.4742 | 120.3094 | 0.19226 | 0.027466 | 0.091553 | 0.004578 | 0.09613 | 0.068664 | 0.18311 | 0.19684 | 120.4605 | 120.4788 | -0.40741 | -0.40283 | 120.282 | 120.3506 | 120.2591 | 120.2774
1461.6562 | 120.8588 | -120.3369 | 0.3067 | -0.0036622 | 0.067214 | 0.015039 | 0.023539 | 1.915e-05 | -0.0040374 | 5.7688e-05 | -0.0015565 | 0.025502 | 0.017566 | 0.015541 | 0.0018265 | 0.01988 | 0.0017111 | -0.004578 | 0.059509 | -0.054932 | 0.009155 | 0.16479 | 0.036621 | 0.045776 | 0.07782 | 0.07782 | -0.027466 | 0.11902 | 0.17395 | 0.091553 | 0.21057 | 120.282 | -0.24719 | -0.29755 | 120.5017 | 120.3827 | 120.3735 | 0.10071 | 0.091553 | 120.3094 | -0.22888 | -0.18768 | 120.5109 | 120.5475 | 120.4285 | 0.23804 | 0.11902 | 0.21973 | 0.064087 | 0.20142 | 0.14649 | 0.11444 | 0.10529 | 120.3964 | 120.4147 | -0.36163 | -0.33417 | 120.3461 | 120.4559 | 120.3323 | 120.4147
1463.4062 | 120.813 | -120.3644 | 0.34332 | -0.018921 | 0.065292 | 0.014612 | 0.023966 | 0.0015146 | -0.00061944 | -0.00079691 | 0.0014953 | 0.024221 | 0.022052 | 0.018532 | -0.0024461 | 0.017957 | -0.0019205 | -0.032043 | 0.10529 | -0.064087 | -0.036621 | 0.091553 | -0.009155 | 0.004578 | 0.032043 | 0.091553 | -0.064087 | 0.022888 | 0.11444 | 0.027466 | 0.14191 | 120.3003 | -0.23804 | -0.37994 | 120.4559 | 120.369 | 120.3552 | 0.068665 | 0.054932 | 120.3003 | -0.25177 | -0.32043 | 120.4788 | 120.5063 | 120.3918 | 0.20599 | 0.091553 | 0.15564 | 0.027466 | 0.17853 | 0.086975 | 0.16937 | 0.15564 | 120.4697 | 120.4559 | -0.40741 | -0.40741 | 120.3278 | 120.3873 | 120.3323 | 120.3964
1465.0938 | 120.8862 | -120.3873 | 0.28381 | -0.0036622 | 0.06401 | 0.016962 | 0.020548 | -0.00019445 | -0.0019012 | 0.00069849 | 0.0014953 | 0.023366 | 0.018421 | 0.014686 | -0.0018051 | 0.020521 | 0.0023521 | -0.068665 | 0.073242 | -0.054932 | -0.027466 | 0.12817 | 0.032043 | 0.041199 | 0.018311 | 0.068665 | -0.064087 | 0.059509 | 0.15564 | 0.086975 | 0.19226 | 120.3323 | -0.21057 | -0.31128 | 120.5154 | 120.4285 | 120.4193 | 0.096131 | 0.086975 | 120.3232 | -0.21515 | -0.2243 | 120.5429 | 120.5795 | 120.4742 | 0.25635 | 0.15106 | 0.18311 | 0.027466 | 0.21973 | 0.1236 | 0.12817 | 0.13275 | 120.4605 | 120.4559 | -0.33874 | -0.3479 | 120.3598 | 120.4468 | 120.3186 | 120.4056
1466.8438 | 120.8176 | -120.4514 | 0.32501 | -0.018921 | 0.065078 | 0.01333 | 0.022257 | -0.00083525 | -0.0046782 | -0.0027195 | 0.0045471 | 0.025502 | 0.020343 | 0.014686 | -0.0039413 | 0.018171 | -0.0042703 | -0.10071 | 0.10071 | -0.07782 | -0.10986 | 0.036621 | -0.041199 | -0.036621 | -0.07782 | 0.10529 | -0.07782 | -0.013733 | 0.050354 | -0.018311 | 0.10529 | 120.3735 | -0.2243 | -0.43488 | 120.488 | 120.4147 | 120.4102 | 0.041199 | 0.036621 | 120.3735 | -0.21973 | -0.33875 | 120.5017 | 120.5566 | 120.433 | 0.18311 | 0.059509 | 0.11444 | -0.032043 | 0.12817 | 0.064087 | 0.17853 | 0.18311 | 120.5521 | 120.5566 | -0.40283 | -0.40283 | 120.3415 | 120.4376 | 120.3506 | 120.3735
1468.5781 | 120.8313 | -120.4651 | 0.32501 | -0.0036622 | 0.067428 | 0.017389 | 0.02418 | -0.0010488 | -0.0012604 | 0.0017667 | -0.0046081 | 0.024648 | 0.019489 | 0.015114 | -0.0035141 | 0.017743 | -0.0017069 | -0.082397 | 0.10071 | -0.082397 | -0.10986 | 0.022888 | -0.086975 | -0.050354 | -0.082397 | 0.10071 | -0.082397 | -0.004578 | 0.032043 | -0.064087 | 0.091553 | 120.3827 | -0.2243 | -0.43488 | 120.488 | 120.4147 | 120.3781 | 0.032043 | -0.004578 | 120.3827 | -0.2243 | -0.32959 | 120.4971 | 120.5566 | 120.401 | 0.17395 | 0.01831 | 0.10528 | -0.027466 | 0.11444 | 0.077819 | 0.18311 | 0.18311 | 120.5658 | 120.5658 | -0.40741 | -0.40741 | 120.3552 | 120.4605 | 120.3827 | 120.3827
1470.2656 | 120.9412 | -120.4559 | 0.32501 | -0.0036622 | 0.064224 | 0.016107 | 0.022898 | -0.0016898 | -0.0036102 | 0.00027129 | -0.0015565 | 0.023366 | 0.017353 | 0.016395 | -0.0020187 | 0.019666 | -0.00042513 | -0.059509 | 0.073242 | -0.045776 | -0.022888 | 0.14191 | 0 | 0.036621 | 0.018311 | 0.050354 | -0.054932 | 0.045776 | 0.1236 | 0.050354 | 0.16937 | 120.4102 | -0.25177 | -0.3479 | 120.5978 | 120.4926 | 120.4559 | 0.082397 | 0.045776 | 120.401 | -0.27466 | -0.27924 | 120.5795 | 120.6253 | 120.5063 | 0.22431 | 0.10529 | 0.18768 | 0.022888 | 0.17853 | 0.10071 | 0.11902 | 0.10529 | 120.5292 | 120.5063 | -0.37079 | -0.37994 | 120.433 | 120.5017 | 120.3964 | 120.4742
1472 | 120.9915 | -120.4697 | 0.28839 | -0.011291 | 0.066574 | 0.018243 | 0.022257 | 0.00023275 | -0.002542 | -0.0014377 | -0.0015565 | 0.023793 | 0.018634 | 0.02195 | 0.0011855 | 0.020521 | -0.0023477 | -0.045776 | 0.059509 | -0.059509 | 0.009155 | 0.12817 | 0.013733 | 0.050354 | 0.068665 | 0.068665 | -0.045776 | 0.10529 | 0.16937 | 0.082397 | 0.21973 | 120.4102 | -0.22888 | -0.27924 | 120.5978 | 120.52 | 120.4834 | 0.10986 | 0.073242 | 120.4239 | -0.21973 | -0.18311 | 120.639 | 120.6894 | 120.5521 | 0.2655 | 0.12817 | 0.18768 | 0.068664 | 0.21515 | 0.15106 | 0.11902 | 0.11444 | 120.5292 | 120.5383 | -0.3479 | -0.33417 | 120.4788 | 120.575 | 120.4239 | 120.5383
1473.7344 | 121.0007 | -120.52 | 0.30212 | -0.0036622 | 0.064651 | 0.01568 | 0.020121 | -0.0025442 | -0.001474 | -0.0016513 | -0.0015565 | 0.024861 | 0.018421 | 0.014046 | -0.0022325 | 0.019239 | -0.0014931 | -0.054932 | 0.059509 | -0.064087 | -0.013733 | 0.12817 | 0.022888 | 0.050354 | 0.027466 | 0.082397 | -0.059509 | 0.064087 | 0.15106 | 0.10986 | 0.19684 | 120.4559 | -0.24261 | -0.31586 | 120.6482 | 120.5704 | 120.5429 | 0.11444 | 0.086975 | 120.4605 | -0.21973 | -0.23804 | 120.6711 | 120.7169 | 120.6299 | 0.25635 | 0.16937 | 0.19226 | 0.050354 | 0.21057 | 0.1236 | 0.1236 | 0.14191 | 120.5795 | 120.6024 | -0.36621 | -0.36163 | 120.5063 | 120.5841 | 120.4651 | 120.5475
1475.4844 | 121.019 | -120.5475 | 0.32044 | -0.018921 | 0.065505 | 0.014398 | 0.02183 | -0.0036124 | -0.0021148 | -0.00015591 | -0.0046081 | 0.021871 | 0.018421 | 0.017891 | -0.0018051 | 0.019452 | -0.0014931 | -0.07782 | 0.054932 | -0.064087 | -0.032043 | 0.11444 | -0.004578 | 0.027466 | 0.004578 | 0.082397 | -0.054932 | 0.045776 | 0.13733 | 0.073242 | 0.16479 | 120.4834 | -0.2655 | -0.35248 | 120.6619 | 120.575 | 120.5429 | 0.091553 | 0.059509 | 120.4926 | -0.23804 | -0.27466 | 120.6848 | 120.7123 | 120.6207 | 0.21973 | 0.12817 | 0.17853 | 0.032044 | 0.19226 | 0.10071 | 0.11902 | 0.13733 | 120.6024 | 120.6299 | -0.38452 | -0.37537 | 120.5154 | 120.5933 | 120.4697 | 120.5521
1477.1562 | 120.9457 | -120.5658 | 0.3479 | -0.018921 | 0.066574 | 0.014612 | 0.020548 | 0.0010874 | -0.0036102 | 0.00091209 | -0.0046081 | 0.024648 | 0.017566 | 0.0099869 | -0.0056503 | 0.016889 | 0.00042947 | -0.041199 | 0.064087 | -0.064087 | -0.032043 | 0.10986 | 0.004578 | 0.032043 | -0.018311 | 0.09613 | -0.064087 | -0.013733 | 0.07782 | -0.004578 | 0.10529 | 120.5017 | -0.28381 | -0.37994 | 120.6757 | 120.5978 | 120.5704 | 0.09613 | 0.068665 | 120.5017 | -0.25177 | -0.36163 | 120.6436 | 120.6711 | 120.5612 | 0.16937 | 0.059509 | 0.17395 | 0.032044 | 0.14191 | 0.050354 | 0.12817 | 0.16022 | 120.6299 | 120.6619 | -0.41199 | -0.41199 | 120.5338 | 120.5521 | 120.5246 | 120.5475
1478.9062 | 120.9686 | -120.6162 | 0.33875 | -0.0036622 | 0.068069 | 0.017389 | 0.023753 | 0.0019418 | -0.0019012 | -0.0020785 | 0.0014953 | 0.027425 | 0.021198 | 0.015114 | -0.00052345 | 0.018171 | -0.0029885 | -0.041199 | 0.091553 | -0.054932 | -0.041199 | 0.091553 | -0.032043 | -0.018311 | -0.009155 | 0.09613 | -0.064087 | 0.009155 | 0.082397 | -0.018311 | 0.11902 | 120.5612 | -0.24719 | -0.37994 | 120.7077 | 120.5978 | 120.5841 | 0.036621 | 0.022889 | 120.5521 | -0.24262 | -0.32959 | 120.6985 | 120.7352 | 120.5978 | 0.18311 | 0.045776 | 0.14649 | 0.013733 | 0.14648 | 0.073242 | 0.14649 | 0.16022 | 120.7077 | 120.7123 | -0.39368 | -0.40283 | 120.575 | 120.6253 | 120.575 | 120.607
1480.6719 | 120.9732 | -120.6345 | 0.33417 | -0.0036622 | 0.065292 | 0.01333 | 0.022257 | 0.0015146 | -0.0057464 | -0.0029331 | -0.0046081 | 0.025289 | 0.019489 | 0.014046 | -0.0047959 | 0.018171 | -0.0021341 | -0.10986 | 0.10071 | -0.073242 | -0.07782 | 0.059509 | -0.018311 | -0.004578 | -0.073242 | 0.09613 | -0.073242 | -0.041199 | 0.050354 | -0.018311 | 0.082397 | 120.5612 | -0.23346 | -0.41199 | 120.694 | 120.6299 | 120.6161 | 0.068664 | 0.054931 | 120.5612 | -0.23804 | -0.37537 | 120.6848 | 120.7169 | 120.6161 | 0.15564 | 0.054931 | 0.13275 | -0.004578 | 0.1236 | 0.032043 | 0.17395 | 0.16937 | 120.7352 | 120.7306 | -0.40741 | -0.40741 | 120.5566 | 120.5933 | 120.5246 | 120.5612
1482.3438 | 121.019 | -120.639 | 0.33875 | -0.0036622 | 0.068496 | 0.016321 | 0.02418 | 0.00087375 | -0.002542 | -0.00058311 | -0.0046081 | 0.025716 | 0.019916 | 0.011055 | -0.0013779 | 0.019452 | -0.0014931 | -0.041199 | 0.086975 | -0.068665 | -0.041199 | 0.10529 | -0.036621 | -0.009155 | -0.018311 | 0.10529 | -0.064087 | 0 | 0.086975 | -0.022888 | 0.10529 | 120.5704 | -0.25177 | -0.37994 | 120.7443 | 120.6299 | 120.6024 | 0.05951 | 0.032044 | 120.575 | -0.23346 | -0.33875 | 120.726 | 120.7443 | 120.6162 | 0.16937 | 0.041199 | 0.17395 | 0.027466 | 0.15106 | 0.064087 | 0.15564 | 0.16937 | 120.726 | 120.7443 | -0.40741 | -0.40283 | 120.5978 | 120.639 | 120.5978 | 120.6207
1484.0156 | 121.1243 | -120.6024 | 0.29755 | -0.0036622 | 0.064651 | 0.016107 | 0.022471 | -0.0025442 | -0.0019012 | -0.0035739 | -0.0015565 | 0.022084 | 0.020343 | 0.013618 | -0.00095065 | 0.020307 | 0.00064307 | -0.032043 | 0.045776 | -0.036621 | 0.009155 | 0.17853 | 0.018311 | 0.068665 | 0.059509 | 0.054932 | -0.059509 | 0.073242 | 0.14648 | 0.082397 | 0.16937 | 120.5658 | -0.25177 | -0.28839 | 120.7809 | 120.6711 | 120.6207 | 0.10529 | 0.054932 | 120.5429 | -0.24261 | -0.2243 | 120.7489 | 120.7718 | 120.6848 | 0.22888 | 0.14191 | 0.21515 | 0.045776 | 0.20599 | 0.13275 | 0.082397 | 0.11444 | 120.6482 | 120.6573 | -0.33417 | -0.35705 | 120.6116 | 120.6757 | 120.5704 | 120.6619
1485.7656 | 121.1746 | -120.6299 | 0.31128 | 0.0039673 | 0.064224 | 0.015039 | 0.020976 | -0.004894 | -0.004892 | -0.0040011 | -0.0015565 | 0.021443 | 0.019916 | 0.024727 | -0.00073705 | 0.019239 | -0.0046975 | -0.050354 | 0.054932 | -0.054932 | -0.009155 | 0.17395 | 0.050354 | 0.073242 | 0.045776 | 0.054932 | -0.050354 | 0.09613 | 0.19684 | 0.1236 | 0.19684 | 120.575 | -0.25635 | -0.32043 | 120.8038 | 120.7031 | 120.6802 | 0.12817 | 0.10529 | 120.5795 | -0.25635 | -0.21515 | 120.8267 | 120.8267 | 120.7535 | 0.24719 | 0.17395 | 0.22888 | 0.045777 | 0.24719 | 0.14648 | 0.10986 | 0.10529 | 120.6848 | 120.6848 | -0.36621 | -0.36163 | 120.6207 | 120.726 | 120.5795 | 120.6757
1487.5 | 121.1746 | -120.6619 | 0.30212 | -0.0036622 | 0.066146 | 0.014612 | 0.020335 | 0.0015146 | -0.0019012 | 0.00027129 | 0.0014953 | 0.025075 | 0.01778 | 0.017036 | 0.0031081 | 0.020948 | -0.0046975 | 0.004578 | 0.064087 | -0.045776 | 0.013733 | 0.16479 | 0.022888 | 0.059509 | 0.086975 | 0.059509 | -0.032043 | 0.10529 | 0.17853 | 0.091553 | 0.2243 | 120.6161 | -0.23804 | -0.28839 | 120.8267 | 120.7214 | 120.6848 | 0.10528 | 0.068664 | 120.6299 | -0.24261 | -0.19684 | 120.8405 | 120.8862 | 120.7535 | 0.25635 | 0.1236 | 0.21057 | 0.059509 | 0.21057 | 0.13733 | 0.10986 | 0.091552 | 120.726 | 120.7214 | -0.3479 | -0.33417 | 120.6757 | 120.7672 | 120.6665 | 120.7489
1489.2344 | 121.0922 | -120.7214 | 0.34332 | 0.011597 | 0.065719 | 0.014612 | 0.022257 | -0.0029714 | -0.0033966 | -0.0020785 | -0.0015565 | 0.024434 | 0.020771 | 0.012123 | -0.0043687 | 0.017743 | -0.0014931 | -0.10529 | 0.10071 | -0.09613 | -0.09613 | 0.041199 | -0.054932 | -0.032043 | -0.073242 | 0.09613 | -0.073242 | -0.009155 | 0.059509 | -0.018311 | 0.09613 | 120.6253 | -0.24261 | -0.43945 | 120.7626 | 120.6894 | 120.6665 | 0.064087 | 0.041198 | 120.6482 | -0.24719 | -0.35248 | 120.7809 | 120.8176 | 120.7031 | 0.16937 | 0.054931 | 0.13733 | 0 | 0.13275 | 0.064087 | 0.19684 | 0.16937 | 120.8221 | 120.8176 | -0.43945 | -0.41656 | 120.6253 | 120.7123 | 120.6161 | 120.6482
1490.9844 | 121.2021 | -120.6802 | 0.3067 | -0.0036622 | 0.066146 | 0.017175 | 0.022685 | 0.00087375 | -0.0036102 | -0.0035739 | -0.0076599 | 0.02358 | 0.018634 | 0.0196 | 0.0011855 | 0.019666 | -0.0049111 | -0.059509 | 0.07782 | -0.07782 | -0.018311 | 0.11902 | 0 | 0.036621 | 0.068665 | 0.091553 | -0.050354 | 0.10529 | 0.16022 | 0.091553 | 0.21057 | 120.6024 | -0.22888 | -0.32501 | 120.7993 | 120.7169 | 120.6802 | 0.11444 | 0.07782 | 120.6299 | -0.21515 | -0.20142 | 120.8405 | 120.8908 | 120.7718 | 0.26093 | 0.14191 | 0.19684 | 0.059509 | 0.21057 | 0.15564 | 0.15564 | 0.14191 | 120.7581 | 120.7718 | -0.38452 | -0.35706 | 120.6619 | 120.7855 | 120.6207 | 120.7489
1492.6562 | 121.2387 | -120.6985 | 0.29755 | -0.0036622 | 0.066146 | 0.013757 | 0.021617 | -0.0027578 | -0.004251 | -0.0010105 | -0.0046081 | 0.02123 | 0.017994 | 0.016609 | -0.0035141 | 0.020307 | -0.00021153 | -0.018311 | 0.064087 | -0.059509 | 0.041199 | 0.21057 | 0.086975 | 0.091553 | 0.09613 | 0.054932 | -0.032043 | 0.09613 | 0.21515 | 0.13275 | 0.20142 | 120.639 | -0.23346 | -0.25635 | 120.9091 | 120.7901 | 120.7855 | 0.15106 | 0.14648 | 120.6665 | -0.24261 | -0.20142 | 120.9137 | 120.9 | 120.8313 | 0.23346 | 0.16479 | 0.27008 | 0.10071 | 0.24719 | 0.12817 | 0.1236 | 0.086975 | 120.7626 | 120.7535 | -0.35705 | -0.32959 | 120.7397 | 120.7947 | 120.6802 | 120.7947
1494.3906 | 121.2204 | -120.7306 | 0.32959 | -0.018921 | 0.064437 | 0.01568 | 0.020335 | 0.0017282 | -0.0019012 | -0.0031467 | -0.0046081 | 0.023793 | 0.019062 | 0.010414 | -0.0020187 | 0.020521 | -0.0034159 | -0.059509 | 0.059509 | -0.064087 | -0.036621 | 0.10071 | 0.004578 | 0.027466 | 0 | 0.068665 | -0.036621 | 0.032043 | 0.13275 | 0.050354 | 0.17853 | 120.6665 | -0.27008 | -0.36621 | 120.8313 | 120.7581 | 120.7352 | 0.091553 | 0.068665 | 120.694 | -0.26092 | -0.29755 | 120.8633 | 120.9091 | 120.7809 | 0.21515 | 0.086975 | 0.1648 | 0.027466 | 0.16937 | 0.068664 | 0.1236 | 0.10529 | 120.7901 | 120.7993 | -0.39368 | -0.36621 | 120.694 | 120.7626 | 120.6711 | 120.7306
1496.125 | 121.2158 | -120.7764 | 0.31128 | -0.011291 | 0.067428 | 0.014825 | 0.022898 | -0.0023306 | 0.00023496 | -0.00079691 | 0.0014953 | 0.023793 | 0.019062 | 0.018318 | -0.0018051 | 0.01753 | -0.00021153 | -0.018311 | 0.050354 | -0.054932 | 0.022888 | 0.17853 | 0.073242 | 0.073242 | 0.045776 | 0.082397 | -0.045776 | 0.045776 | 0.13733 | 0.059509 | 0.15564 | 120.7214 | -0.26092 | -0.28839 | 120.9549 | 120.8496 | 120.8496 | 0.12817 | 0.12817 | 120.7306 | -0.22888 | -0.2655 | 120.9137 | 120.932 | 120.8359 | 0.20142 | 0.10528 | 0.23346 | 0.07782 | 0.18311 | 0.091552 | 0.10529 | 0.12817 | 120.8267 | 120.8588 | -0.36621 | -0.35705 | 120.7993 | 120.8221 | 120.7581 | 120.8221
1497.7969 | 121.2799 | -120.7718 | 0.27924 | -0.011291 | 0.064865 | 0.01803 | 0.024607 | -0.001476 | -0.0012604 | -0.0014377 | -0.0015565 | 0.022939 | 0.019275 | 0.020027 | 0.0028945 | 0.017957 | 0.0010703 | -0.004578 | 0.045776 | -0.013733 | 0.032043 | 0.17853 | 0.050354 | 0.068665 | 0.10071 | 0.064087 | -0.041199 | 0.10986 | 0.17395 | 0.09613 | 0.21515 | 120.7581 | -0.23346 | -0.24719 | 120.9503 | 120.8405 | 120.8221 | 0.082398 | 0.064087 | 120.7306 | -0.21515 | -0.16937 | 120.9457 | 120.9869 | 120.8679 | 0.25635 | 0.13733 | 0.19226 | 0.045776 | 0.21515 | 0.15106 | 0.059509 | 0.10529 | 120.8176 | 120.8359 | -0.29297 | -0.32043 | 120.8038 | 120.8817 | 120.7672 | 120.8725
1499.5312 | 121.3074 | -120.8084 | 0.2655 | -0.0036622 | 0.066574 | 0.015253 | 0.023112 | 0.0015146 | -0.003183 | -0.0033603 | -0.0015565 | 0.024434 | 0.018848 | 0.011696 | 0.0018265 | 0.019452 | -0.00063873 | -0.004578 | 0.045776 | -0.032043 | 0.036621 | 0.16937 | 0.036621 | 0.068665 | 0.10071 | 0.059509 | -0.036621 | 0.12817 | 0.17853 | 0.10529 | 0.20599 | 120.7764 | -0.21973 | -0.22888 | 120.9778 | 120.8771 | 120.845 | 0.10071 | 0.068664 | 120.7718 | -0.20599 | -0.13733 | 120.9869 | 121.0144 | 120.9137 | 0.24262 | 0.14191 | 0.20142 | 0.068664 | 0.21515 | 0.1648 | 0.077819 | 0.09613 | 120.8542 | 120.8679 | -0.29755 | -0.30212 | 120.845 | 120.9366 | 120.8038 | 120.9091
1501.2188 | 121.2845 | -120.7993 | 0.28381 | -0.0036622 | 0.065078 | 0.014398 | 0.022898 | 0.0010874 | -0.001474 | 0.00048489 | -0.0076599 | 0.024007 | 0.017566 | 0.018745 | 0.0024673 | 0.019666 | -0.0023477 | -0.091553 | 0.086975 | -0.064087 | -0.054932 | 0.054932 | -0.054932 | -0.013733 | -0.009155 | 0.082397 | -0.054932 | 0.059509 | 0.12817 | 0.050354 | 0.17853 | 120.7352 | -0.19684 | -0.33874 | 120.8542 | 120.7855 | 120.7443 | 0.050354 | 0.009155 | 120.7443 | -0.20142 | -0.2243 | 120.9274 | 120.9778 | 120.8496 | 0.23346 | 0.10529 | 0.11902 | 0.009155 | 0.18311 | 0.11444 | 0.15106 | 0.13733 | 120.8862 | 120.8817 | -0.3479 | -0.33874 | 120.7443 | 120.8588 | 120.7077 | 120.7901
1502.9531 | 121.2524 | -120.8725 | 0.28381 | -0.0036622 | 0.066574 | 0.015466 | 0.023112 | -0.001476 | -0.003183 | -0.00036951 | -0.0015565 | 0.025929 | 0.019703 | 0.012764 | -0.0030869 | 0.018598 | -0.0044839 | -0.054932 | 0.082397 | -0.086975 | -0.013733 | 0.11902 | 0 | 0.013733 | 0.013733 | 0.073242 | -0.036621 | 0.036621 | 0.091553 | 0.013733 | 0.14191 | 120.7855 | -0.20142 | -0.29755 | 120.9915 | 120.8862 | 120.8725 | 0.10071 | 0.086975 | 120.8359 | -0.21057 | -0.24719 | 120.9641 | 121.0144 | 120.8862 | 0.17853 | 0.050354 | 0.20599 | 0.073242 | 0.12817 | 0.073242 | 0.16937 | 0.10986 | 120.9549 | 120.9457 | -0.37079 | -0.32043 | 120.8588 | 120.9091 | 120.8176 | 120.8862
1504.625 | 121.2067 | -120.9091 | 0.29755 | -0.011291 | 0.066787 | 0.015466 | 0.023966 | 0.0025828 | -0.0040374 | 0.0011257 | -0.0015565 | 0.024648 | 0.017994 | 0.012123 | -0.00073705 | 0.01988 | -0.0076883 | -0.091553 | 0.091553 | -0.082397 | -0.091553 | 0.041199 | -0.07782 | -0.050354 | -0.082397 | 0.09613 | -0.068665 | -0.032043 | 0.032043 | -0.050354 | 0.07782 | 120.8267 | -0.20599 | -0.3891 | 120.9503 | 120.8588 | 120.8313 | 0.032043 | 0.004577 | 120.8405 | -0.20142 | -0.32959 | 120.9412 | 120.9869 | 120.8588 | 0.14649 | 0.018311 | 0.1236 | -0.009156 | 0.10071 | 0.036622 | 0.17395 | 0.16479 | 121.0007 | 121.0052 | -0.37994 | -0.36621 | 120.8176 | 120.8771 | 120.8176 | 120.8267
1506.375 | 121.2341 | -120.8908 | 0.31586 | -0.011291 | 0.064651 | 0.01333 | 0.02183 | -0.0010488 | -0.0046782 | -0.0027195 | 0.0014953 | 0.025502 | 0.020557 | 0.010628 | -0.0026597 | 0.018384 | 0.0023521 | -0.10986 | 0.10529 | -0.082397 | -0.11902 | 0.045776 | -0.050354 | -0.032043 | -0.086975 | 0.10071 | -0.073242 | -0.032043 | 0.064087 | -0.013733 | 0.10071 | 120.8084 | -0.21057 | -0.43488 | 120.9366 | 120.8588 | 120.8405 | 0.050354 | 0.032043 | 120.8176 | -0.21515 | -0.3479 | 120.9549 | 120.9915 | 120.8771 | 0.17395 | 0.059509 | 0.12817 | -0.036622 | 0.13733 | 0.041199 | 0.18768 | 0.17395 | 120.9961 | 120.9915 | -0.39825 | -0.3891 | 120.7718 | 120.8588 | 120.7809 | 120.8038
1508.1094 | 121.2708 | -120.9274 | 0.27924 | 0.0039673 | 0.063796 | 0.016962 | 0.021189 | 0.00066015 | -0.0023284 | 0.00091209 | -0.0015565 | 0.024648 | 0.02013 | 0.020454 | 0.00097195 | 0.017743 | 0.00085667 | -0.091553 | 0.09613 | -0.082397 | -0.091553 | 0.022888 | -0.09613 | -0.041199 | -0.068665 | 0.09613 | -0.059509 | -0.004578 | 0.032043 | -0.036621 | 0.10071 | 120.845 | -0.18311 | -0.37079 | 120.9503 | 120.8862 | 120.8313 | 0.041198 | -0.013733 | 120.8679 | -0.18311 | -0.28381 | 120.9595 | 121.0281 | 120.8908 | 0.16022 | 0.022888 | 0.10528 | -0.009156 | 0.091552 | 0.054931 | 0.17853 | 0.15564 | 121.0236 | 121.0236 | -0.36163 | -0.33874 | 120.8359 | 120.9229 | 120.8359 | 120.8588
1509.8594 | 121.3531 | -120.9183 | 0.29297 | -0.0036622 | 0.065078 | 0.015253 | 0.02183 | 0.0017282 | -0.003183 | -0.00015591 | -0.0046081 | 0.022939 | 0.018848 | 0.0097733 | -0.00030965 | 0.019452 | -0.0027749 | -0.091553 | 0.091553 | -0.064087 | -0.068665 | 0.07782 | -0.041199 | -0.004578 | 0.013733 | 0.09613 | -0.050354 | 0.07782 | 0.14191 | 0.041199 | 0.17395 | 120.8542 | -0.20142 | -0.36163 | 120.9961 | 120.9137 | 120.8771 | 0.059509 | 0.022888 | 120.8679 | -0.19684 | -0.21515 | 121.0602 | 121.0922 | 120.9595 | 0.2243 | 0.091553 | 0.14191 | -0.004578 | 0.19226 | 0.12817 | 0.15564 | 0.14648 | 121.0098 | 121.0144 | -0.35706 | -0.34332 | 120.8496 | 120.9961 | 120.8267 | 120.932
1511.5469 | 121.2891 | -120.9869 | 0.3067 | -0.0036622 | 0.064651 | 0.016748 | 0.02183 | 0.00044655 | -0.0023284 | 0.0015531 | -0.0046081 | 0.024861 | 0.016498 | 0.011269 | -0.0058639 | 0.018384 | 0.0010703 | -0.054932 | 0.059509 | -0.036621 | -0.036621 | 0.1236 | 0.013733 | 0.022888 | -0.027466 | 0.082397 | -0.064087 | -0.022888 | 0.07782 | 0.013733 | 0.10071 | 120.9503 | -0.24719 | -0.34332 | 121.1105 | 121.0098 | 121.0007 | 0.059509 | 0.050354 | 120.9229 | -0.2243 | -0.32959 | 121.0648 | 121.0876 | 121.0007 | 0.1648 | 0.07782 | 0.16022 | 0 | 0.14191 | 0.041199 | 0.09613 | 0.14648 | 121.0464 | 121.0693 | -0.34332 | -0.37079 | 120.9503 | 120.9641 | 120.932 | 120.9595
1513.2969 | 121.4218 | -120.9229 | 0.27008 | -0.011291 | 0.066574 | 0.017175 | 0.022471 | 1.915e-05 | -0.003183 | 0.0015531 | 0.0045471 | 0.024434 | 0.016925 | 0.016609 | 0.0022537 | 0.019666 | -0.0036295 | 0 | 0.041199 | -0.032043 | 0.027466 | 0.1831 | 0.032043 | 0.068665 | 0.086975 | 0.050354 | -0.041199 | 0.10986 | 0.17853 | 0.10529 | 0.21973 | 120.8908 | -0.22888 | -0.24262 | 121.106 | 120.9915 | 120.9549 | 0.10071 | 0.064086 | 120.8817 | -0.21973 | -0.16022 | 121.1014 | 121.1426 | 121.0281 | 0.26093 | 0.14649 | 0.21515 | 0.059509 | 0.21973 | 0.15106 | 0.073242 | 0.091553 | 120.9641 | 120.9732 | -0.30212 | -0.31128 | 120.9503 | 121.0327 | 120.9229 | 121.0098
1514.9688 | 121.4447 | -120.9503 | 0.25635 | -0.0036622 | 0.063369 | 0.015466 | 0.021189 | -0.003826 | -0.002542 | -0.0033603 | 0.0014953 | 0.023366 | 0.020771 | 0.020027 | -0.0022325 | 0.017743 | 0.00042947 | -0.045776 | 0.059509 | -0.045776 | 0.009155 | 0.16479 | 0.059509 | 0.082397 | 0.064087 | 0.064087 | -0.068665 | 0.082397 | 0.1831 | 0.1236 | 0.19684 | 120.9045 | -0.19684 | -0.24719 | 121.1151 | 121.0327 | 121.0098 | 0.12817 | 0.10528 | 120.8817 | -0.19226 | -0.17395 | 121.1334 | 121.1472 | 121.0739 | 0.2655 | 0.19226 | 0.21057 | 0.054931 | 0.25177 | 0.15106 | 0.10528 | 0.13275 | 121.0098 | 121.0144 | -0.30212 | -0.32501 | 120.9595 | 121.0327 | 120.9045 | 121.0144
1516.7188 | 121.3715 | -120.9778 | 0.27008 | -0.011291 | 0.066574 | 0.013971 | 0.019908 | -0.0023306 | -0.00061944 | 0.00027129 | -0.0046081 | 0.024007 | 0.018634 | 0.014046 | -0.0022325 | 0.01988 | -0.0029885 | -0.032043 | 0.068665 | -0.050354 | 0.022888 | 0.16479 | 0.059509 | 0.050354 | 0.032043 | 0.07782 | -0.045776 | 0.027466 | 0.12817 | 0.050354 | 0.15106 | 120.9274 | -0.20142 | -0.24719 | 121.1426 | 121.0281 | 121.0373 | 0.10071 | 0.10986 | 120.932 | -0.19226 | -0.24262 | 121.106 | 121.1288 | 121.0281 | 0.19684 | 0.09613 | 0.21515 | 0.073242 | 0.17395 | 0.073242 | 0.11902 | 0.1236 | 121.0464 | 121.0556 | -0.32044 | -0.31586 | 121.0007 | 121.0052 | 120.9457 | 121.0098
1518.4531 | 121.4264 | -120.9686 | 0.28381 | 0.0039673 | 0.064224 | 0.015039 | 0.020762 | 0.00301 | -0.00083304 | -0.0018649 | -0.0046081 | 0.022725 | 0.017566 | 0.021736 | -0.0024461 | 0.020307 | 0.00042947 | -0.082397 | 0.064087 | -0.07782 | -0.041199 | 0.10071 | -0.004578 | 0.022888 | -0.009155 | 0.086975 | -0.059509 | 0.041199 | 0.13733 | 0.07782 | 0.16022 | 120.8908 | -0.21973 | -0.32501 | 121.0693 | 120.9915 | 120.9641 | 0.10071 | 0.073242 | 120.9091 | -0.19684 | -0.24261 | 121.106 | 121.1288 | 121.0464 | 0.21973 | 0.13733 | 0.17853 | 0.036621 | 0.19684 | 0.10071 | 0.14191 | 0.14648 | 121.0327 | 121.0556 | -0.36163 | -0.34332 | 120.9274 | 121.0098 | 120.8862 | 120.9595
1520.125 | 121.344 | -121.2158 | 0.14191 | -0.02655 | 0.064865 | 0.016107 | 0.022685 | -0.0019034 | -0.0038238 | -0.0029331 | -0.0015565 | 0.025289 | 0.019703 | 0.0097733 | -0.0052231 | 0.017743 | -0.0014931 | -0.10071 | 0.09613 | -0.082397 | -0.11444 | 0.036621 | -0.041199 | -0.027466 | -0.064087 | 0.10529 | -0.068665 | -0.045776 | 0.054932 | -0.027466 | 0.07782 | 121.1334 | -0.045777 | -0.25635 | 121.2524 | 121.1884 | 121.1746 | 0.054931 | 0.041198 | 121.1472 | -0.036621 | -0.18768 | 121.2708 | 121.2936 | 121.1884 | 0.14649 | 0.041199 | 0.11902 | -0.032044 | 0.1236 | 0.022889 | 0.17853 | 0.17395 | 121.3119 | 121.3211 | -0.2243 | -0.21057 | 121.1014 | 121.17 | 121.1151 | 121.1517
1521.875 | 121.4355 | -121.1563 | 0.10986 | 0.0039673 | 0.06636 | 0.017816 | 0.022685 | 0.00066015 | -0.0023284 | -0.0022921 | -0.0015565 | 0.022512 | 0.019703 | 0.013405 | 0.00054475 | 0.018171 | -0.0012795 | -0.054932 | 0.050354 | -0.050354 | -0.022888 | 0.1236 | -0.018311 | 0.032043 | 0.013733 | 0.068665 | -0.059509 | 0.041199 | 0.10986 | 0.041199 | 0.15564 | 121.106 | -0.059509 | -0.13275 | 121.2799 | 121.1884 | 121.138 | 0.082397 | 0.032043 | 121.0968 | -0.041198 | -0.068664 | 121.2662 | 121.312 | 121.1975 | 0.21515 | 0.10071 | 0.17395 | 0.027466 | 0.16937 | 0.10071 | 0.10071 | 0.12817 | 121.2067 | 121.225 | -0.16022 | -0.16937 | 121.1334 | 121.1975 | 121.1014 | 121.17
1523.625 | 121.3898 | -121.2296 | 0.14191 | -0.0036622 | 0.06636 | 0.013971 | 0.022898 | -0.0023306 | -0.0023284 | -0.0012241 | -0.0015565 | 0.026143 | 0.019703 | 0.015327 | 0.00097195 | 0.020307 | -0.0044839 | -0.082397 | 0.10529 | -0.082397 | -0.10529 | 0.036621 | -0.086975 | -0.050354 | -0.045776 | 0.09613 | -0.068665 | -0.004578 | 0.036621 | -0.041199 | 0.11444 | 121.1472 | -0.036621 | -0.24719 | 121.2662 | 121.1792 | 121.1426 | 0.032043 | -0.004578 | 121.1609 | -0.045777 | -0.14649 | 121.2662 | 121.344 | 121.1884 | 0.18311 | 0.027466 | 0.11902 | -0.022889 | 0.10529 | 0.064087 | 0.18768 | 0.16479 | 121.3348 | 121.3257 | -0.2243 | -0.21057 | 121.1243 | 121.225 | 121.1472 | 121.1838
1525.375 | 121.4264 | -121.2158 | 0.13733 | 0.0039673 | 0.067001 | 0.013971 | 0.023539 | -0.00083525 | -0.0038238 | -0.0016513 | -0.0046081 | 0.024007 | 0.019275 | 0.0069961 | -0.0037277 | 0.019452 | -0.00085233 | -0.086975 | 0.10986 | -0.07782 | -0.09613 | 0.054932 | -0.045776 | -0.027466 | -0.07782 | 0.091553 | -0.082397 | -0.022888 | 0.073242 | -0.004578 | 0.10071 | 121.138 | -0.027466 | -0.23346 | 121.2708 | 121.1884 | 121.17 | 0.050354 | 0.032044 | 121.1334 | -0.045776 | -0.16022 | 121.2891 | 121.3165 | 121.2112 | 0.18311 | 0.077819 | 0.13275 | -0.01831 | 0.15564 | 0.059509 | 0.18768 | 0.17395 | 121.3257 | 121.3074 | -0.21515 | -0.21973 | 121.1197 | 121.1929 | 121.1288 | 121.138
1527.0469 | 121.4035 | -121.2479 | 0.13275 | -0.011291 | 0.063796 | 0.012903 | 0.022044 | -0.0057486 | -0.004251 | -0.0020785 | -0.0015565 | 0.024861 | 0.020557 | 0.013618 | -0.0037277 | 0.017103 | -0.0019205 | -0.10529 | 0.091553 | -0.10071 | -0.11444 | 0.041199 | -0.041199 | -0.036621 | -0.073242 | 0.10071 | -0.091553 | -0.036621 | 0.045776 | -0.013733 | 0.10529 | 121.1472 | -0.041198 | -0.24719 | 121.2891 | 121.2112 | 121.2067 | 0.064087 | 0.059509 | 121.1563 | -0.032043 | -0.16937 | 121.2936 | 121.3532 | 121.2341 | 0.19684 | 0.07782 | 0.14191 | -0.013733 | 0.13733 | 0.054932 | 0.19226 | 0.19226 | 121.3394 | 121.3486 | -0.23346 | -0.2243 | 121.1334 | 121.2112 | 121.1426 | 121.1746
1528.7969 | 121.4172 | -121.2387 | 0.14648 | -0.011291 | 0.064437 | 0.013544 | 0.022685 | -0.0016898 | -0.0036102 | -0.0022921 | -0.0015565 | 0.025075 | 0.019703 | 0.011482 | -0.0041551 | 0.017316 | 0.00042947 | -0.11444 | 0.086975 | -0.10071 | -0.10986 | 0.041199 | -0.032043 | -0.032043 | -0.082397 | 0.09613 | -0.086975 | -0.018311 | 0.041199 | -0.027466 | 0.10986 | 121.138 | -0.059509 | -0.25635 | 121.2799 | 121.2067 | 121.2067 | 0.068665 | 0.068665 | 121.1517 | -0.050354 | -0.16479 | 121.2799 | 121.3486 | 121.2112 | 0.19684 | 0.059509 | 0.14191 | -0.009155 | 0.12817 | 0.068664 | 0.18768 | 0.1831 | 121.3257 | 121.3348 | -0.24719 | -0.23346 | 121.1288 | 121.2204 | 121.1243 | 121.1563
1530.5625 | 121.5042 | -121.2662 | 0.10071 | 0.0039673 | 0.062515 | 0.014185 | 0.020121 | 0.0019418 | -0.0046782 | 0.0011257 | -0.0015565 | 0.024221 | 0.017353 | 0.019813 | 0.0033217 | 0.019239 | -0.0014931 | -0.082397 | 0.054932 | -0.045776 | -0.022888 | 0.10529 | -0.013733 | 0.027466 | -0.032043 | 0.054932 | -0.045776 | 0.036621 | 0.12817 | 0.064087 | 0.15564 | 121.2204 | -0.045776 | -0.1236 | 121.3715 | 121.2936 | 121.2524 | 0.073242 | 0.032043 | 121.2204 | -0.045776 | -0.064087 | 121.3943 | 121.4218 | 121.3303 | 0.20142 | 0.10986 | 0.15106 | 0.022888 | 0.17395 | 0.082397 | 0.10071 | 0.10071 | 121.3211 | 121.3211 | -0.14648 | -0.14648 | 121.2433 | 121.3028 | 121.1838 | 121.2341
1532.25 | 121.5042 | -121.2616 | 0.10071 | -0.018921 | 0.066146 | 0.014185 | 0.021403 | -0.00019445 | -0.0027556 | -0.0033603 | -0.0046081 | 0.024648 | 0.017566 | 0.014046 | -0.0026597 | 0.015821 | -0.0044839 | -0.022888 | 0.050354 | -0.045776 | 0.032043 | 0.16937 | 0.073242 | 0.073242 | 0.068665 | 0.059509 | -0.045776 | 0.041199 | 0.16022 | 0.09613 | 0.17395 | 121.2158 | -0.050354 | -0.068665 | 121.431 | 121.3348 | 121.3348 | 0.11902 | 0.11902 | 121.2158 | -0.041199 | -0.059509 | 121.4218 | 121.4355 | 121.3577 | 0.21973 | 0.14191 | 0.21515 | 0.077819 | 0.20599 | 0.086975 | 0.09613 | 0.10528 | 121.312 | 121.3211 | -0.14648 | -0.14648 | 121.2936 | 121.3028 | 121.2387 | 121.3303
1534 | 121.4447 | -121.2753 | 0.13733 | -0.011291 | 0.063796 | 0.014825 | 0.02418 | -0.003826 | -0.0027556 | -0.0022921 | -0.0015565 | 0.024221 | 0.020557 | 0.011055 | -0.0020187 | 0.018171 | 0.00085667 | -0.068665 | 0.064087 | -0.082397 | -0.068665 | 0.073242 | -0.032043 | -0.009155 | -0.054932 | 0.086975 | -0.068665 | -0.022888 | 0.059509 | -0.013733 | 0.086975 | 121.1929 | -0.073242 | -0.20599 | 121.3486 | 121.2662 | 121.2433 | 0.073242 | 0.050354 | 121.2067 | -0.050354 | -0.16022 | 121.3348 | 121.3623 | 121.2616 | 0.15564 | 0.054932 | 0.15564 | 0.013732 | 0.12817 | 0.045777 | 0.14648 | 0.15564 | 121.3394 | 121.3623 | -0.21973 | -0.20599 | 121.2067 | 121.2524 | 121.2067 | 121.2204
1535.6875 | 121.4584 | -121.2936 | 0.11444 | -0.011291 | 0.065078 | 0.014185 | 0.022898 | -0.003826 | -0.0038238 | 0.00027129 | -0.0046081 | 0.022725 | 0.018421 | 0.012978 | -0.00073705 | 0.018384 | -0.0044839 | -0.059509 | 0.054932 | -0.050354 | -0.036621 | 0.10986 | 0.004578 | 0.009155 | -0.032043 | 0.07782 | -0.059509 | -0.013733 | 0.082397 | -0.004578 | 0.091553 | 121.2433 | -0.059509 | -0.15106 | 121.4035 | 121.3028 | 121.2982 | 0.059509 | 0.054932 | 121.2341 | -0.036621 | -0.12817 | 121.376 | 121.3852 | 121.2891 | 0.15106 | 0.054931 | 0.16022 | 0.013733 | 0.14191 | 0.045776 | 0.10529 | 0.13733 | 121.3486 | 121.3715 | -0.16479 | -0.17395 | 121.257 | 121.2799 | 121.2341 | 121.2616
1537.4219 | 121.5363 | -121.2845 | 0.10529 | 0.0039673 | 0.064865 | 0.017389 | 0.021617 | -0.0023306 | -0.002542 | -0.0031467 | -0.0046081 | 0.024861 | 0.016498 | 0.017891 | -0.0015915 | 0.018171 | -0.0017069 | -0.045776 | 0.041199 | -0.041199 | 0.018311 | 0.16937 | 0.022888 | 0.059509 | 0.086975 | 0.050354 | -0.045776 | 0.068665 | 0.15106 | 0.073242 | 0.16479 | 121.2433 | -0.064087 | -0.086975 | 121.4539 | 121.344 | 121.3074 | 0.10071 | 0.064087 | 121.2387 | -0.054932 | -0.036621 | 121.4355 | 121.4493 | 121.3577 | 0.21057 | 0.11902 | 0.21057 | 0.05951 | 0.19684 | 0.11444 | 0.082398 | 0.09613 | 121.3257 | 121.3348 | -0.14649 | -0.15106 | 121.3028 | 121.3531 | 121.2387 | 121.3715
1539.1719 | 121.4539 | -121.3165 | 0.13275 | -0.0036622 | 0.066787 | 0.016748 | 0.023112 | 0.00301 | -0.0021148 | -0.0020785 | -0.0076599 | 0.026143 | 0.019062 | 0.012978 | 0.00033115 | 0.018384 | 0.00021567 | -0.082397 | 0.09613 | -0.07782 | -0.082397 | 0 | -0.082397 | -0.068665 | -0.09613 | 0.10071 | -0.082397 | -0.036621 | 0.022888 | -0.064087 | 0.082397 | 121.2387 | -0.036621 | -0.21515 | 121.3165 | 121.2479 | 121.2341 | 0.009155 | -0.004577 | 121.2341 | -0.032043 | -0.16937 | 121.3394 | 121.3989 | 121.2524 | 0.16479 | 0.01831 | 0.07782 | -0.004577 | 0.10528 | 0.045776 | 0.17395 | 0.18311 | 121.4127 | 121.4172 | -0.21057 | -0.21515 | 121.2341 | 121.2799 | 121.2341 | 121.2204
1540.9375 | 121.5729 | -121.2708 | 0.082397 | -0.0036622 | 0.062728 | 0.016321 | 0.022471 | -0.0051076 | -0.0029694 | -0.0020785 | -0.0015565 | 0.023152 | 0.018848 | 0.013618 | 0.0018265 | 0.019452 | -0.00063873 | -0.036621 | 0.050354 | -0.027466 | 0.036621 | 0.1831 | 0.032043 | 0.059509 | 0.086975 | 0.068665 | -0.041199 | 0.10071 | 0.16022 | 0.091553 | 0.17853 | 121.2433 | -0.032043 | -0.045776 | 121.4539 | 121.3303 | 121.3028 | 0.086975 | 0.059509 | 121.2296 | -0.013732 | 0.018311 | 121.431 | 121.4493 | 121.3623 | 0.21973 | 0.13275 | 0.21057 | 0.064087 | 0.20142 | 0.14191 | 0.07782 | 0.10986 | 121.3211 | 121.3394 | -0.10986 | -0.1236 | 121.3074 | 121.3715 | 121.2341 | 121.3577
1542.625 | 121.637 | -121.2845 | 0.10986 | -0.011291 | 0.065933 | 0.014185 | 0.020121 | 0.0010874 | -0.0012604 | -0.0029331 | 0.0014953 | 0.020803 | 0.017566 | 0.020027 | -0.0022325 | 0.020521 | -0.0040567 | -0.013733 | 0.054932 | -0.041199 | 0.027466 | 0.19684 | 0.073242 | 0.091553 | 0.11444 | 0.045776 | -0.032043 | 0.11902 | 0.2243 | 0.13275 | 0.20599 | 121.2433 | -0.054931 | -0.082397 | 121.4813 | 121.376 | 121.3577 | 0.13275 | 0.11444 | 121.2524 | -0.064087 | 0.009156 | 121.5088 | 121.4905 | 121.4172 | 0.23804 | 0.16479 | 0.23804 | 0.068665 | 0.25635 | 0.15106 | 0.096131 | 0.077819 | 121.3394 | 121.3303 | -0.15106 | -0.14191 | 121.312 | 121.4035 | 121.2708 | 121.3989
1544.375 | 121.6324 | -121.3028 | 0.086975 | -0.011291 | 0.065719 | 0.016107 | 0.022471 | -0.0023306 | -0.00061944 | -0.0010105 | -0.0046081 | 0.025502 | 0.018848 | 0.013832 | 0.0024673 | 0.019666 | 0.00021567 | 0.018311 | 0.064087 | -0.045776 | 0.027466 | 0.17395 | 0.032043 | 0.045776 | 0.091553 | 0.064087 | -0.045776 | 0.10986 | 0.16937 | 0.10986 | 0.21515 | 121.257 | -0.022888 | -0.059509 | 121.4767 | 121.3486 | 121.3348 | 0.091552 | 0.077819 | 121.257 | -0.022888 | 0.022888 | 121.4722 | 121.5179 | 121.4127 | 0.26093 | 0.15564 | 0.21973 | 0.073242 | 0.21515 | 0.15564 | 0.10986 | 0.10986 | 121.3669 | 121.3669 | -0.13275 | -0.13275 | 121.3303 | 121.4127 | 121.3211 | 121.3943
1546.0469 | 121.6553 | -121.3074 | 0.09613 | -0.0036622 | 0.063369 | 0.015039 | 0.020976 | -0.0027578 | -0.0051056 | -0.0018649 | -0.0015565 | 0.022084 | 0.018848 | 0.015968 | -0.0035141 | 0.021161 | 0.0010703 | -0.027466 | 0.050354 | -0.050354 | 0.054932 | 0.2243 | 0.10529 | 0.11444 | 0.10071 | 0.064087 | -0.036621 | 0.09613 | 0.21057 | 0.12817 | 0.20142 | 121.257 | -0.045776 | -0.041198 | 121.5317 | 121.4218 | 121.4127 | 0.16479 | 0.15564 | 121.2708 | -0.032043 | 0 | 121.5179 | 121.5088 | 121.4355 | 0.23804 | 0.1648 | 0.27466 | 0.10529 | 0.24719 | 0.13275 | 0.10071 | 0.10071 | 121.3577 | 121.3715 | -0.14648 | -0.13275 | 121.3623 | 121.4035 | 121.2799 | 121.4081
1547.7969 | 121.5271 | -121.3531 | 0.1236 | -0.011291 | 0.065933 | 0.012903 | 0.021189 | 0.00044655 | -0.0027556 | -0.00058311 | -0.0015565 | 0.023793 | 0.019703 | 0.012123 | -0.0045823 | 0.016462 | -0.0034159 | -0.041199 | 0.073242 | -0.059509 | -0.022888 | 0.10986 | 0.004578 | 0.009155 | -0.018311 | 0.082397 | -0.068665 | -0.013733 | 0.073242 | -0.004578 | 0.09613 | 121.2936 | -0.050354 | -0.14648 | 121.463 | 121.3623 | 121.3577 | 0.068664 | 0.064087 | 121.2845 | -0.041199 | -0.13733 | 121.4264 | 121.4493 | 121.3486 | 0.16479 | 0.064087 | 0.16937 | 0.036621 | 0.14191 | 0.054932 | 0.13275 | 0.15106 | 121.4264 | 121.4355 | -0.1831 | -0.19226 | 121.3303 | 121.3394 | 121.3119 | 121.3348
1549.5312 | 121.6278 | -121.3486 | 0.11444 | -0.011291 | 0.064865 | 0.015253 | 0.022685 | 0.0027964 | -0.0040374 | -0.0022921 | -0.0015565 | 0.023793 | 0.018207 | 0.018532 | -0.0020187 | 0.020307 | 0.00021567 | -0.068665 | 0.07782 | -0.050354 | -0.036621 | 0.091553 | 0.004578 | 0.032043 | -0.009155 | 0.054932 | -0.045776 | 0.036621 | 0.1236 | 0.064087 | 0.17395 | 121.2982 | -0.036621 | -0.15106 | 121.4401 | 121.3806 | 121.3531 | 0.082397 | 0.054932 | 121.3028 | -0.059509 | -0.07782 | 121.4722 | 121.5225 | 121.4127 | 0.21973 | 0.10986 | 0.14191 | 0.013733 | 0.16937 | 0.082397 | 0.12817 | 0.10071 | 121.4264 | 121.4035 | -0.16479 | -0.16022 | 121.312 | 121.3852 | 121.2799 | 121.3394
1551.2656 | 121.6141 | -121.3669 | 0.11444 | -0.011291 | 0.063369 | 0.016321 | 0.020335 | 0.00066015 | -0.0036102 | -0.0014377 | -0.0046081 | 0.02123 | 0.018634 | 0.014473 | -0.00052345 | 0.018598 | -0.0027749 | -0.009155 | 0.050354 | -0.050354 | 0.032043 | 0.17853 | 0.068665 | 0.073242 | 0.045776 | 0.064087 | -0.036621 | 0.027466 | 0.13275 | 0.054932 | 0.16022 | 121.3165 | -0.064087 | -0.082398 | 121.5454 | 121.4401 | 121.4355 | 0.1236 | 0.11902 | 121.3303 | -0.050354 | -0.086975 | 121.4996 | 121.5271 | 121.4218 | 0.19684 | 0.091553 | 0.22888 | 0.082397 | 0.16937 | 0.064087 | 0.10071 | 0.10071 | 121.4172 | 121.431 | -0.16479 | -0.15106 | 121.3989 | 121.3943 | 121.3577 | 121.4127
1552.9375 | 121.5408 | -121.4127 | 0.14191 | -0.0036622 | 0.067855 | 0.016107 | 0.024607 | -0.0010488 | -0.0019012 | -0.0018649 | -0.0015565 | 0.026143 | 0.021198 | 0.0067825 | 0.00075835 | 0.017103 | -0.0027749 | -0.082397 | 0.10529 | -0.073242 | -0.09613 | 0.009155 | -0.082397 | -0.073242 | -0.091553 | 0.09613 | -0.082397 | -0.032043 | 0.004578 | -0.073242 | 0.07782 | 121.3394 | -0.036621 | -0.23804 | 121.4218 | 121.3394 | 121.3303 | 0 | -0.009155 | 121.3303 | -0.045777 | -0.17395 | 121.4172 | 121.4905 | 121.3394 | 0.16022 | 0.009155 | 0.082397 | -0.022888 | 0.086975 | 0.050354 | 0.17853 | 0.17853 | 121.5179 | 121.5088 | -0.21515 | -0.2243 | 121.3165 | 121.3806 | 121.3303 | 121.3211
1554.6719 | 121.5729 | -121.3943 | 0.14191 | -0.018921 | 0.068069 | 0.015466 | 0.023966 | 0.00044655 | -0.0036102 | -0.00079691 | 0.0014953 | 0.025929 | 0.02013 | 0.01255 | 0.00075835 | 0.020734 | -0.00021153 | -0.07782 | 0.10529 | -0.073242 | -0.082397 | 0.041199 | -0.082397 | -0.054932 | -0.10071 | 0.086975 | -0.073242 | -0.027466 | 0.018311 | -0.050354 | 0.086975 | 121.3211 | -0.036621 | -0.2243 | 121.4355 | 121.3394 | 121.312 | 0.01831 | -0.009155 | 121.3211 | -0.054932 | -0.16937 | 121.4127 | 121.4813 | 121.344 | 0.16022 | 0.022888 | 0.11444 | -0.009155 | 0.091553 | 0.045776 | 0.17853 | 0.16022 | 121.4996 | 121.4813 | -0.21515 | -0.21515 | 121.312 | 121.3669 | 121.3165 | 121.2936
1556.4219 | 121.6644 | -121.3943 | 0.09613 | -0.0036622 | 0.065078 | 0.017816 | 0.022685 | 0.00044655 | -0.004251 | -0.0016513 | -0.0015565 | 0.021871 | 0.019275 | 0.019813 | 0.00097195 | 0.020307 | -0.00063873 | -0.032043 | 0.064087 | -0.041199 | 0.009155 | 0.1831 | 0.032043 | 0.059509 | 0.07782 | 0.050354 | -0.045776 | 0.086975 | 0.15564 | 0.082397 | 0.17395 | 121.3531 | -0.032043 | -0.086975 | 121.5775 | 121.4539 | 121.4264 | 0.10071 | 0.073242 | 121.3486 | -0.045776 | -0.009155 | 121.55 | 121.5683 | 121.4767 | 0.21973 | 0.12817 | 0.2243 | 0.050354 | 0.20142 | 0.13275 | 0.10529 | 0.09613 | 121.4584 | 121.4447 | -0.13733 | -0.14191 | 121.4035 | 121.4813 | 121.3623 | 121.4722
1558.1719 | 121.582 | -121.4355 | 0.13275 | -0.0036622 | 0.063369 | 0.012689 | 0.021403 | -0.0057486 | -0.0023284 | -0.0018649 | -0.0015565 | 0.021871 | 0.018421 | 0.0076371 | -0.0041551 | 0.016034 | 2.068e-06 | -0.10071 | 0.09613 | -0.082397 | -0.082397 | 0.059509 | -0.041199 | -0.018311 | -0.082397 | 0.086975 | -0.068665 | -0.045776 | 0.054932 | -0.022888 | 0.082397 | 121.3531 | -0.036621 | -0.21515 | 121.4951 | 121.4172 | 121.3943 | 0.064086 | 0.041198 | 121.3669 | -0.045776 | -0.17853 | 121.4905 | 121.5179 | 121.4127 | 0.15106 | 0.045777 | 0.14191 | 0 | 0.1236 | 0.022889 | 0.17853 | 0.15564 | 121.5317 | 121.5225 | -0.21515 | -0.20142 | 121.3531 | 121.3898 | 121.3348 | 121.3531
1559.9062 | 121.6461 | -121.4264 | 0.12817 | -0.0036622 | 0.065505 | 0.014398 | 0.024607 | -0.0027578 | -0.0038238 | -0.00058311 | 0.0045471 | 0.025929 | 0.018848 | 0.01725 | -0.0013779 | 0.016034 | -0.00063873 | -0.10071 | 0.10529 | -0.082397 | -0.086975 | 0.045776 | -0.041199 | -0.013733 | -0.068665 | 0.10529 | -0.086975 | 0 | 0.091553 | 0 | 0.12817 | 121.344 | -0.022888 | -0.21515 | 121.4722 | 121.4127 | 121.3852 | 0.068664 | 0.041198 | 121.3394 | -0.022888 | -0.12817 | 121.5179 | 121.5546 | 121.4264 | 0.21515 | 0.086975 | 0.12817 | -0.004578 | 0.17853 | 0.086975 | 0.18768 | 0.19226 | 121.5317 | 121.5317 | -0.21057 | -0.21515 | 121.3394 | 121.4264 | 121.3257 | 121.3577
1561.5781 | 121.6965 | -121.4081 | 0.11444 | -0.018921 | 0.062515 | 0.014825 | 0.022471 | -0.003185 | -0.003183 | -0.00058311 | -0.0015565 | 0.021443 | 0.019062 | 0.012978 | -0.0015915 | 0.019239 | -0.00042513 | -0.07782 | 0.068665 | -0.059509 | -0.032043 | 0.11444 | 0.018311 | 0.036621 | 0.004578 | 0.068665 | -0.073242 | 0.064087 | 0.15106 | 0.07782 | 0.16479 | 121.3486 | -0.045776 | -0.14648 | 121.5225 | 121.4447 | 121.4264 | 0.09613 | 0.07782 | 121.3348 | -0.045776 | -0.050354 | 121.5591 | 121.5729 | 121.4859 | 0.23804 | 0.15106 | 0.17395 | 0.027466 | 0.2243 | 0.13733 | 0.12817 | 0.14191 | 121.4767 | 121.4767 | -0.17395 | -0.18768 | 121.376 | 121.4722 | 121.3303 | 121.4127
1563.3438 | 121.6095 | -121.4493 | 0.15106 | -0.011291 | 0.064865 | 0.015253 | 0.021617 | -0.00062165 | -0.002542 | 0.0021939 | -0.0046081 | 0.024861 | 0.019275 | 0.015541 | -0.0050095 | 0.018171 | 0.00021567 | -0.07782 | 0.091553 | -0.068665 | -0.07782 | 0.064087 | -0.027466 | -0.004578 | -0.054932 | 0.091553 | -0.073242 | -0.022888 | 0.064087 | -0.022888 | 0.082397 | 121.3806 | -0.059509 | -0.22888 | 121.5134 | 121.4447 | 121.4218 | 0.064087 | 0.041199 | 121.376 | -0.059509 | -0.17395 | 121.5134 | 121.5317 | 121.4264 | 0.15564 | 0.050354 | 0.13275 | -0.009155 | 0.13733 | 0.050354 | 0.16022 | 0.16479 | 121.5408 | 121.5408 | -0.21973 | -0.2243 | 121.3715 | 121.4264 | 121.3715 | 121.3943
1565.0312 | 121.6141 | -121.4676 | 0.12817 | -0.0036622 | 0.06636 | 0.015466 | 0.023326 | -0.003185 | -0.001474 | 0.00048489 | -0.0015565 | 0.026784 | 0.019275 | 0.012764 | -0.00073705 | 0.016462 | -0.0025613 | -0.086975 | 0.10529 | -0.086975 | -0.11444 | -0.004578 | -0.10986 | -0.07782 | -0.10071 | 0.10986 | -0.068665 | -0.018311 | 0.027466 | -0.064087 | 0.09613 | 121.3806 | -0.022888 | -0.24262 | 121.463 | 121.3898 | 121.3577 | 0.009155 | -0.022888 | 121.3989 | -0.018311 | -0.14649 | 121.4951 | 121.5637 | 121.4035 | 0.16479 | 0.004578 | 0.082397 | -0.027466 | 0.096131 | 0.050354 | 0.19226 | 0.17853 | 121.5729 | 121.5775 | -0.21515 | -0.19684 | 121.3531 | 121.4493 | 121.3806 | 121.3669
1566.7812 | 121.7056 | -121.4447 | 0.11902 | -0.0036622 | 0.065933 | 0.014185 | 0.022257 | -0.0016898 | -0.0023284 | -0.0042147 | 0.0014953 | 0.022298 | 0.019703 | 0.022804 | -0.0020187 | 0.018171 | -0.0057657 | -0.027466 | 0.032043 | -0.054932 | 0.027466 | 0.17853 | 0.068665 | 0.073242 | 0.041199 | 0.054932 | -0.050354 | 0.050354 | 0.16479 | 0.073242 | 0.15564 | 121.3898 | -0.086976 | -0.091553 | 121.6232 | 121.5179 | 121.5134 | 0.12817 | 0.1236 | 121.3943 | -0.064087 | -0.068665 | 121.6095 | 121.6003 | 121.5179 | 0.20599 | 0.1236 | 0.23346 | 0.082398 | 0.21515 | 0.10071 | 0.086975 | 0.10529 | 121.4767 | 121.4996 | -0.17395 | -0.16937 | 121.4722 | 121.4951 | 121.4172 | 121.4859
1568.5156 | 121.6736 | -121.4676 | 0.13275 | -0.011291 | 0.063796 | 0.014185 | 0.022471 | -0.00083525 | -0.0046782 | -0.0037875 | -0.0015565 | 0.025075 | 0.017566 | 0.013832 | -0.0018051 | 0.017103 | -0.00063873 | -0.059509 | 0.073242 | -0.082397 | -0.036621 | 0.10529 | 0.004578 | 0.013733 | 0 | 0.10071 | -0.07782 | 0.036621 | 0.1236 | 0.032043 | 0.14191 | 121.3852 | -0.059509 | -0.16937 | 121.5729 | 121.4813 | 121.4722 | 0.09613 | 0.086975 | 121.3898 | -0.032043 | -0.09613 | 121.5912 | 121.6095 | 121.4996 | 0.21973 | 0.10986 | 0.18768 | 0.045776 | 0.20142 | 0.11444 | 0.15564 | 0.17853 | 121.5408 | 121.5683 | -0.21515 | -0.21057 | 121.431 | 121.5042 | 121.4081 | 121.4676
1570.25 | 121.7194 | -121.4676 | 0.10071 | 0.011597 | 0.065078 | 0.017389 | 0.020976 | -0.0016898 | -0.0021148 | 0.00048489 | -0.0015565 | 0.024007 | 0.02013 | 0.019386 | 0.0016129 | 0.018598 | -0.0023477 | -0.041199 | 0.041199 | -0.050354 | 0.004578 | 0.15564 | 0.018311 | 0.050354 | 0.041199 | 0.064087 | -0.064087 | 0.068665 | 0.14191 | 0.073242 | 0.16022 | 121.4172 | -0.059509 | -0.09613 | 121.6232 | 121.5179 | 121.4859 | 0.10071 | 0.068665 | 121.4035 | -0.036621 | -0.032043 | 121.6095 | 121.6278 | 121.5408 | 0.2243 | 0.13733 | 0.20599 | 0.054932 | 0.20599 | 0.13275 | 0.091553 | 0.12817 | 121.5088 | 121.5317 | -0.15106 | -0.1648 | 121.4722 | 121.5363 | 121.4264 | 121.5088
1571.9375 | 121.6599 | -121.4767 | 0.11444 | -0.011291 | 0.066787 | 0.015894 | 0.022257 | -0.0036124 | 2.1362e-05 | -0.0025057 | -0.0015565 | 0.024221 | 0.020343 | 0.0074235 | -0.00073705 | 0.020734 | -0.0023477 | -0.054932 | 0.068665 | -0.073242 | -0.036621 | 0.082397 | -0.032043 | -0.027466 | -0.022888 | 0.082397 | -0.064087 | 0 | 0.064087 | -0.018311 | 0.11444 | 121.4035 | -0.045776 | -0.15106 | 121.5591 | 121.4493 | 121.4447 | 0.045776 | 0.041199 | 121.4127 | -0.032044 | -0.11444 | 121.5408 | 121.5912 | 121.4584 | 0.17853 | 0.045776 | 0.15564 | 0.036621 | 0.12817 | 0.064087 | 0.14191 | 0.14648 | 121.5454 | 121.5591 | -0.18768 | -0.17853 | 121.4401 | 121.4767 | 121.4218 | 121.4539
1573.6719 | 121.788 | -121.4813 | 0.13733 | -0.0036622 | 0.067428 | 0.013757 | 0.023112 | 0.0025828 | -0.0023284 | -0.0022921 | -0.0076599 | 0.023366 | 0.019489 | 0.019173 | -0.0020187 | 0.017743 | -0.0046975 | -0.050354 | 0.09613 | -0.054932 | -0.032043 | 0.11902 | -0.018311 | -0.004578 | -0.013733 | 0.086975 | -0.07782 | 0.009155 | 0.086975 | -0.004578 | 0.12817 | 121.4264 | -0.041199 | -0.16937 | 121.6003 | 121.4767 | 121.463 | 0.050354 | 0.036621 | 121.4035 | -0.050354 | -0.12817 | 121.5683 | 121.6095 | 121.4767 | 0.20599 | 0.073242 | 0.17395 | 0.022889 | 0.16479 | 0.086975 | 0.15106 | 0.16479 | 121.5775 | 121.5683 | -0.19226 | -0.21515 | 121.4493 | 121.4905 | 121.431 | 121.4676
1575.4062 | 121.7972 | -121.4447 | 0.086975 | -0.0036622 | 0.064224 | 0.017175 | 0.020976 | -0.00040805 | 0.00066216 | -0.0025057 | -0.0015565 | 0.025075 | 0.01778 | 0.017677 | 0.0018265 | 0.021802 | -0.00042513 | -0.004578 | 0.054932 | -0.041199 | 0.027466 | 0.17395 | 0.018311 | 0.054932 | 0.068665 | 0.059509 | -0.041199 | 0.1236 | 0.19226 | 0.10071 | 0.21057 | 121.4035 | -0.032043 | -0.059509 | 121.6187 | 121.4996 | 121.463 | 0.096131 | 0.05951 | 121.4035 | -0.027466 | 0.036621 | 121.637 | 121.6553 | 121.5454 | 0.25177 | 0.14191 | 0.21515 | 0.068665 | 0.23346 | 0.16479 | 0.096131 | 0.10071 | 121.4996 | 121.5042 | -0.12817 | -0.12817 | 121.4722 | 121.5683 | 121.4401 | 121.5134
1577.0938 | 121.7331 | -121.4996 | 0.11902 | -0.0036622 | 0.067642 | 0.015253 | 0.02418 | 0.0010874 | -0.0038238 | -0.0025057 | -0.0046081 | 0.024221 | 0.019062 | 0.011909 | -0.0013779 | 0.018598 | -0.0042703 | -0.041199 | 0.09613 | -0.09613 | -0.041199 | 0.10986 | -0.013733 | -0.004578 | -0.004578 | 0.082397 | -0.045776 | 0.027466 | 0.10986 | 0.018311 | 0.14648 | 121.4035 | -0.022889 | -0.16022 | 121.6095 | 121.4951 | 121.4859 | 0.091552 | 0.082397 | 121.4539 | -0.036622 | -0.091553 | 121.6095 | 121.6461 | 121.5179 | 0.19226 | 0.064087 | 0.20599 | 0.054931 | 0.15564 | 0.073242 | 0.19226 | 0.12817 | 121.5958 | 121.582 | -0.21515 | -0.16479 | 121.4584 | 121.5271 | 121.4584 | 121.4951
1578.8438 | 121.6919 | -121.5179 | 0.11444 | -0.011291 | 0.065505 | 0.01568 | 0.023539 | 1.915e-05 | -0.0010468 | -0.0014377 | -0.0046081 | 0.026784 | 0.019489 | 0.0076371 | -0.0018051 | 0.016675 | -0.0023477 | -0.050354 | 0.086975 | -0.082397 | -0.027466 | 0.10986 | -0.009155 | 0.009155 | 0.004578 | 0.086975 | -0.064087 | 0.036621 | 0.10986 | 0.013733 | 0.12817 | 121.4355 | -0.027466 | -0.14191 | 121.6278 | 121.5271 | 121.5088 | 0.091552 | 0.073242 | 121.4539 | -0.027466 | -0.07782 | 121.6278 | 121.6461 | 121.5317 | 0.19226 | 0.07782 | 0.19226 | 0.054931 | 0.17395 | 0.10071 | 0.16937 | 0.15106 | 121.6049 | 121.6049 | -0.19684 | -0.17853 | 121.4905 | 121.5546 | 121.4676 | 121.5225
1580.5938 | 121.7331 | -121.5271 | 0.11902 | -0.011291 | 0.068923 | 0.016748 | 0.023326 | -0.0029714 | -0.0038238 | -0.0010105 | -0.0046081 | 0.024434 | 0.018848 | 0.0149 | 0.00011755 | 0.017957 | -0.00085233 | -0.045776 | 0.086975 | -0.073242 | -0.027466 | 0.12817 | 0.004578 | 0.009155 | 0 | 0.091553 | -0.064087 | 0.027466 | 0.10071 | 0.022888 | 0.14648 | 121.4539 | -0.032044 | -0.14649 | 121.6553 | 121.5363 | 121.5317 | 0.082397 | 0.07782 | 121.463 | -0.027466 | -0.091553 | 121.6278 | 121.6736 | 121.55 | 0.21057 | 0.086975 | 0.20142 | 0.045776 | 0.1648 | 0.091553 | 0.16022 | 0.15564 | 121.6141 | 121.6187 | -0.19226 | -0.18311 | 121.4996 | 121.5546 | 121.4813 | 121.5271
1582.3438 | 121.7926 | -121.5134 | 0.11444 | -0.0036622 | 0.06401 | 0.017389 | 0.022685 | -0.00040805 | -0.003183 | 0.00027129 | -0.0046081 | 0.022939 | 0.019275 | 0.014046 | 0.00097195 | 0.018598 | 0.00064307 | -0.082397 | 0.086975 | -0.054932 | -0.054932 | 0.09613 | -0.027466 | 0 | 0.018311 | 0.086975 | -0.054932 | 0.082397 | 0.13275 | 0.050354 | 0.16937 | 121.4584 | -0.027466 | -0.16937 | 121.6095 | 121.5134 | 121.4859 | 0.054932 | 0.027466 | 121.4584 | -0.027466 | -0.032044 | 121.6461 | 121.6827 | 121.5637 | 0.22431 | 0.10529 | 0.15106 | 0 | 0.18768 | 0.13733 | 0.14191 | 0.14191 | 121.6003 | 121.6003 | -0.16937 | -0.16937 | 121.4584 | 121.5958 | 121.431 | 121.5317
1584.0938 | 121.7834 | -121.4996 | 0.10529 | -0.018921 | 0.06636 | 0.015894 | 0.021403 | -0.00083525 | -0.0010468 | -0.00036951 | -0.0015565 | 0.022084 | 0.020343 | 0.016823 | -0.0018051 | 0.01988 | -0.0019205 | -0.07782 | 0.050354 | -0.059509 | -0.036621 | 0.13733 | -0.009155 | 0.036621 | -0.009155 | 0.07782 | -0.032043 | 0.045776 | 0.11902 | 0.036621 | 0.16479 | 121.4401 | -0.054932 | -0.14191 | 121.637 | 121.5363 | 121.4905 | 0.09613 | 0.050354 | 121.4676 | -0.027466 | -0.05951 | 121.6187 | 121.6644 | 121.5363 | 0.19684 | 0.068664 | 0.19684 | 0.022888 | 0.15106 | 0.077819 | 0.10986 | 0.10986 | 121.55 | 121.5775 | -0.16479 | -0.13733 | 121.463 | 121.5454 | 121.4218 | 121.4905
1585.8594 | 121.7239 | -121.5546 | 0.13275 | -0.0036622 | 0.065719 | 0.015039 | 0.020335 | -0.00083525 | -0.0040374 | -0.0010105 | -0.0015565 | 0.025289 | 0.019275 | 0.012978 | -0.0054367 | 0.018598 | -0.0040567 | -0.10071 | 0.091553 | -0.086975 | -0.10529 | 0.050354 | -0.041199 | -0.013733 | -0.07782 | 0.091553 | -0.091553 | -0.050354 | 0.045776 | -0.036621 | 0.09613 | 121.4676 | -0.041198 | -0.23804 | 121.6049 | 121.5408 | 121.5134 | 0.073242 | 0.045776 | 121.463 | -0.041198 | -0.18311 | 121.6003 | 121.6507 | 121.5179 | 0.18768 | 0.054932 | 0.13733 | -0.018311 | 0.13733 | 0.041199 | 0.17853 | 0.18311 | 121.6461 | 121.6461 | -0.21973 | -0.2243 | 121.4493 | 121.5042 | 121.4539 | 121.4767
1587.5469 | 121.7514 | -121.5363 | 0.11444 | -0.0036622 | 0.067214 | 0.016534 | 0.022685 | 0.0015146 | -0.0021148 | -0.0037875 | -0.0015565 | 0.02358 | 0.020771 | 0.020241 | 0.00011755 | 0.017316 | -0.0027749 | -0.09613 | 0.09613 | -0.086975 | -0.091553 | 0.032043 | -0.086975 | -0.036621 | -0.050354 | 0.10529 | -0.064087 | 0.004578 | 0.054932 | -0.022888 | 0.11902 | 121.4493 | -0.018311 | -0.20599 | 121.5683 | 121.4996 | 121.4493 | 0.050354 | 0 | 121.4722 | -0.009155 | -0.10986 | 121.5912 | 121.6553 | 121.5134 | 0.18311 | 0.041199 | 0.11902 | -0.004578 | 0.11902 | 0.068665 | 0.1831 | 0.16937 | 121.6324 | 121.6415 | -0.20142 | -0.17853 | 121.4447 | 121.5408 | 121.4401 | 121.4859
1589.2969 | 121.8155 | -121.5271 | 0.10529 | -0.011291 | 0.066787 | 0.018671 | 0.021617 | -0.0029714 | -0.0012604 | -0.0018649 | 0.0014953 | 0.024007 | 0.020557 | 0.01255 | 0.0028945 | 0.018812 | -0.00063873 | -0.022888 | 0.054932 | -0.032043 | 0.036621 | 0.19226 | 0.050354 | 0.073242 | 0.091553 | 0.059509 | -0.036621 | 0.10071 | 0.1831 | 0.09613 | 0.20142 | 121.4951 | -0.050354 | -0.068665 | 121.7194 | 121.6003 | 121.5775 | 0.10529 | 0.082397 | 121.4905 | -0.045777 | -0.004578 | 121.7102 | 121.7285 | 121.6232 | 0.23804 | 0.13275 | 0.2243 | 0.068664 | 0.21973 | 0.13733 | 0.086975 | 0.09613 | 121.582 | 121.5866 | -0.13733 | -0.14191 | 121.5637 | 121.6278 | 121.5042 | 121.6187
1591.0469 | 121.8246 | -121.5363 | 0.13275 | 0.0039673 | 0.06636 | 0.018884 | 0.021189 | 0.0032236 | -0.003183 | -0.0022921 | -0.0015565 | 0.023366 | 0.021412 | 0.016395 | -9.605e-05 | 0.019239 | 2.068e-06 | -0.032043 | 0.054932 | -0.027466 | 0.022888 | 0.17853 | 0.022888 | 0.059509 | 0.091553 | 0.045776 | -0.027466 | 0.059509 | 0.14648 | 0.068665 | 0.16022 | 121.5088 | -0.077819 | -0.10986 | 121.7148 | 121.5958 | 121.5591 | 0.086975 | 0.050354 | 121.5088 | -0.086975 | -0.073242 | 121.6827 | 121.6965 | 121.6049 | 0.18768 | 0.096131 | 0.20599 | 0.050354 | 0.17395 | 0.086975 | 0.082398 | 0.073242 | 121.5912 | 121.582 | -0.16022 | -0.16022 | 121.5591 | 121.5958 | 121.5042 | 121.6278
1592.7344 | 121.7148 | -121.5683 | 0.13733 | -0.0036622 | 0.067001 | 0.01568 | 0.023753 | -0.0012624 | -0.0012604 | -0.00079691 | -0.0046081 | 0.024434 | 0.02013 | 0.012123 | 0.00033115 | 0.018598 | -0.0046975 | -0.068665 | 0.086975 | -0.091553 | -0.10986 | -0.009155 | -0.10986 | -0.07782 | -0.10529 | 0.09613 | -0.059509 | -0.027466 | 0.018311 | -0.050354 | 0.10071 | 121.4767 | -0.050354 | -0.24719 | 121.5591 | 121.4905 | 121.4584 | 0.013733 | -0.01831 | 121.5088 | -0.041199 | -0.16479 | 121.5866 | 121.669 | 121.5179 | 0.16022 | 0.009155 | 0.082398 | -0.01831 | 0.07782 | 0.032043 | 0.17853 | 0.15564 | 121.6553 | 121.6644 | -0.22888 | -0.19684 | 121.4584 | 121.5408 | 121.4996 | 121.463
1594.4688 | 121.8521 | -121.5317 | 0.10529 | 0.0039673 | 0.064865 | 0.014185 | 0.023753 | 0.0051462 | 2.1362e-05 | -0.00058311 | -0.0046081 | 0.024221 | 0.020557 | 0.024513 | 0.0018265 | 0.019452 | -0.00042513 | -0.059509 | 0.082397 | -0.059509 | -0.032043 | 0.10986 | -0.045776 | 0.013733 | 0.027466 | 0.073242 | -0.032043 | 0.091553 | 0.15564 | 0.059509 | 0.20142 | 121.4722 | -0.022889 | -0.13733 | 121.6415 | 121.5454 | 121.4859 | 0.073242 | 0.013733 | 121.4996 | -0.032044 | -0.013733 | 121.6873 | 121.7331 | 121.5912 | 0.23346 | 0.091552 | 0.16937 | 0.027466 | 0.18768 | 0.1236 | 0.14191 | 0.10529 | 121.6141 | 121.6049 | -0.16479 | -0.13733 | 121.4996 | 121.6232 | 121.4722 | 121.5591
1596.2344 | 121.843 | -121.5317 | 0.10071 | -0.0036622 | 0.067855 | 0.016107 | 0.019053 | 0.0040782 | -0.0012604 | -0.00079691 | 0.0014953 | 0.02358 | 0.020343 | 0.015114 | -0.00052345 | 0.019666 | 0.0017111 | -0.027466 | 0.045776 | -0.027466 | 0.027466 | 0.1831 | 0.022888 | 0.064087 | 0.086975 | 0.054932 | -0.054932 | 0.086975 | 0.17395 | 0.086975 | 0.1831 | 121.5042 | -0.054932 | -0.073242 | 121.7148 | 121.5958 | 121.5546 | 0.091553 | 0.050354 | 121.4767 | -0.045776 | -0.013733 | 121.7056 | 121.7148 | 121.6187 | 0.23804 | 0.14191 | 0.21057 | 0.054932 | 0.22888 | 0.14191 | 0.073242 | 0.10986 | 121.5775 | 121.5866 | -0.12817 | -0.15564 | 121.5591 | 121.6187 | 121.5042 | 121.6187
1597.9375 | 121.8338 | -121.5775 | 0.13275 | -0.0036622 | 0.065933 | 0.016321 | 0.020762 | 0.0040782 | -0.0023284 | 0.00027129 | 0.0014953 | 0.021443 | 0.019275 | 0.020882 | -0.0039413 | 0.018598 | -0.0012795 | -0.032043 | 0.054932 | -0.045776 | 0.018311 | 0.19226 | 0.064087 | 0.064087 | 0.059509 | 0.054932 | -0.054932 | 0.032043 | 0.14191 | 0.068665 | 0.15106 | 121.5317 | -0.077819 | -0.11444 | 121.7697 | 121.6415 | 121.6415 | 0.10986 | 0.10986 | 121.5225 | -0.077819 | -0.10071 | 121.7194 | 121.7285 | 121.6461 | 0.20599 | 0.1236 | 0.23804 | 0.064087 | 0.19684 | 0.086975 | 0.10071 | 0.10986 | 121.6324 | 121.6324 | -0.17853 | -0.18768 | 121.5958 | 121.6095 | 121.5454 | 121.637
1599.6875 | 121.7651 | -121.6278 | 0.12817 | -0.011291 | 0.065505 | 0.013971 | 0.022044 | -0.0016898 | -0.002542 | -0.0025057 | -0.0046081 | 0.026357 | 0.019489 | 0.017036 | -0.0033005 | 0.016675 | 0.0021383 | -0.11444 | 0.10529 | -0.10071 | -0.09613 | 0.032043 | -0.041199 | -0.027466 | -0.068665 | 0.11444 | -0.086975 | -0.041199 | 0.041199 | -0.022888 | 0.09613 | 121.5271 | -0.022888 | -0.2243 | 121.6599 | 121.6003 | 121.5866 | 0.073242 | 0.059509 | 121.5408 | -0.013733 | -0.16937 | 121.669 | 121.7239 | 121.6049 | 0.1831 | 0.064087 | 0.13275 | 0.004578 | 0.12817 | 0.045776 | 0.20599 | 0.20142 | 121.7331 | 121.7422 | -0.22888 | -0.21515 | 121.5317 | 121.5866 | 121.5134 | 121.5591
1601.375 | 121.8887 | -121.5729 | 0.10071 | -0.0036622 | 0.065933 | 0.017175 | 0.020762 | -0.0025442 | -0.0010468 | 0.00048489 | -0.0015565 | 0.02358 | 0.019062 | 0.017677 | -0.0020187 | 0.01988 | -0.0014931 | -0.073242 | 0.07782 | -0.054932 | -0.022888 | 0.1236 | 0.018311 | 0.054932 | 0.032043 | 0.086975 | -0.059509 | 0.073242 | 0.16479 | 0.091553 | 0.20142 | 121.5179 | -0.022888 | -0.1236 | 121.6965 | 121.6278 | 121.5912 | 0.10986 | 0.073243 | 121.5134 | -0.013733 | -0.027466 | 121.7377 | 121.7743 | 121.6644 | 0.26093 | 0.15106 | 0.17853 | 0.032044 | 0.2243 | 0.13275 | 0.13275 | 0.14648 | 121.6507 | 121.6599 | -0.15564 | -0.16022 | 121.55 | 121.6461 | 121.4996 | 121.6049
1603.1094 | 121.9116 | -121.5775 | 0.10071 | 0.0039673 | 0.066146 | 0.016534 | 0.020762 | -0.0046804 | -0.0044646 | 0.00027129 | -0.0015565 | 0.023366 | 0.019062 | 0.017677 | -0.00073705 | 0.019452 | -0.0027749 | -0.054932 | 0.054932 | -0.032043 | 0 | 0.15564 | 0.059509 | 0.086975 | 0.045776 | 0.059509 | -0.036621 | 0.07782 | 0.1831 | 0.10529 | 0.19684 | 121.5454 | -0.045776 | -0.10071 | 121.7331 | 121.6644 | 121.637 | 0.11902 | 0.091552 | 121.5408 | -0.041199 | -0.022888 | 121.7606 | 121.7743 | 121.6827 | 0.23346 | 0.14191 | 0.18768 | 0.032043 | 0.21973 | 0.11444 | 0.086975 | 0.09613 | 121.6324 | 121.637 | -0.13275 | -0.13733 | 121.5775 | 121.6553 | 121.5225 | 121.6232
1604.8594 | 121.8475 | -121.6141 | 0.11444 | -0.0036622 | 0.064865 | 0.014398 | 0.021403 | -0.0061758 | -0.0027556 | 5.7688e-05 | 0.0045471 | 0.024861 | 0.021198 | 0.012764 | -0.0047959 | 0.018171 | -0.0042703 | -0.018311 | 0.036621 | -0.032043 | 0.018311 | 0.16937 | 0.064087 | 0.068665 | 0.036621 | 0.073242 | -0.050354 | 0.041199 | 0.13275 | 0.059509 | 0.14191 | 121.582 | -0.07782 | -0.09613 | 121.7834 | 121.6827 | 121.6782 | 0.10071 | 0.09613 | 121.5637 | -0.041199 | -0.073242 | 121.7468 | 121.756 | 121.6736 | 0.19226 | 0.10986 | 0.20142 | 0.050354 | 0.18311 | 0.091553 | 0.068664 | 0.1236 | 121.6507 | 121.6873 | -0.14648 | -0.16479 | 121.6324 | 121.6553 | 121.5958 | 121.6507
1606.6094 | 121.8292 | -121.5958 | 0.12817 | 0.0039673 | 0.065078 | 0.014825 | 0.022471 | 0.0017282 | -0.0019012 | -0.0022921 | -0.0015565 | 0.025075 | 0.019062 | 0.012978 | 0.00054475 | 0.017103 | -0.00063873 | -0.032043 | 0.086975 | -0.064087 | -0.018311 | 0.10071 | -0.018311 | 0.022888 | 0.009155 | 0.10529 | -0.073242 | 0.027466 | 0.086975 | 0.013733 | 0.1236 | 121.5317 | -0.041199 | -0.14649 | 121.6965 | 121.6187 | 121.5775 | 0.086975 | 0.045776 | 121.5225 | -0.022888 | -0.10071 | 121.6827 | 121.7194 | 121.6095 | 0.19684 | 0.086975 | 0.1648 | 0.045776 | 0.16022 | 0.10071 | 0.15106 | 0.17853 | 121.6827 | 121.7011 | -0.19226 | -0.20142 | 121.5775 | 121.6232 | 121.5637 | 121.6049
1608.3125 | 121.843 | -121.6278 | 0.1236 | -0.0036622 | 0.066787 | 0.013971 | 0.02183 | 0.0021556 | -0.0021148 | -0.0035739 | 0.0014953 | 0.025289 | 0.020343 | 0.017891 | 0.00054475 | 0.017743 | -0.0010659 | -0.041199 | 0.082397 | -0.064087 | -0.018311 | 0.11444 | 0 | 0.022888 | 0.018311 | 0.11902 | -0.059509 | 0.036621 | 0.11902 | 0.022888 | 0.14648 | 121.5637 | -0.041199 | -0.14191 | 121.7422 | 121.6507 | 121.6278 | 0.086975 | 0.064087 | 121.5683 | -0.004577 | -0.086975 | 121.7468 | 121.7743 | 121.6507 | 0.20599 | 0.082397 | 0.17853 | 0.045776 | 0.17853 | 0.09613 | 0.14648 | 0.17853 | 121.7102 | 121.7468 | -0.18768 | -0.1831 | 121.6095 | 121.6644 | 121.5866 | 121.6461
1610.0469 | 121.8109 | -121.6599 | 0.13733 | -0.0036622 | 0.067428 | 0.014398 | 0.021617 | -0.0046804 | -0.003183 | -0.0025057 | -0.0046081 | 0.024648 | 0.019062 | 0.015114 | -0.0039413 | 0.015821 | 2.068e-06 | -0.10071 | 0.086975 | -0.09613 | -0.10529 | 0.045776 | -0.045776 | -0.022888 | -0.07782 | 0.10071 | -0.086975 | -0.036621 | 0.050354 | -0.013733 | 0.10071 | 121.5637 | -0.050354 | -0.24262 | 121.7056 | 121.637 | 121.6141 | 0.073242 | 0.050354 | 121.5729 | -0.036621 | -0.17395 | 121.7102 | 121.7606 | 121.6461 | 0.18768 | 0.073242 | 0.14191 | -0.009156 | 0.13733 | 0.050354 | 0.1831 | 0.18768 | 121.7468 | 121.7606 | -0.23346 | -0.2243 | 121.5546 | 121.6232 | 121.5591 | 121.582
1611.7344 | 121.9025 | -121.6278 | 0.07782 | -0.0036622 | 0.062515 | 0.015039 | 0.020976 | -0.00062165 | -0.0016876 | 0.0011257 | 0.0014953 | 0.023152 | 0.019703 | 0.013405 | 0.0026809 | 0.019452 | 0.0012839 | -0.059509 | 0.059509 | -0.041199 | -0.013733 | 0.16479 | 0.013733 | 0.045776 | 0.032043 | 0.054932 | -0.036621 | 0.068665 | 0.1236 | 0.054932 | 0.16022 | 121.5866 | -0.018311 | -0.091553 | 121.7926 | 121.6736 | 121.6415 | 0.086975 | 0.054932 | 121.5912 | -0.022888 | -0.009155 | 121.7514 | 121.788 | 121.6827 | 0.19684 | 0.091553 | 0.20599 | 0.027466 | 0.16022 | 0.10529 | 0.10071 | 0.091553 | 121.6873 | 121.6827 | -0.11902 | -0.11444 | 121.6141 | 121.6965 | 121.5683 | 121.6599
1613.4844 | 121.9482 | -121.582 | 0.10529 | -0.011291 | 0.063369 | 0.015039 | 0.022471 | -0.0029714 | -0.0040374 | -0.0035739 | 0.0014953 | 0.020375 | 0.01778 | 0.023018 | -0.0030869 | 0.018812 | -0.0036295 | -0.045776 | 0.050354 | -0.054932 | 0.018311 | 0.16937 | 0.068665 | 0.086975 | 0.068665 | 0.054932 | -0.045776 | 0.091553 | 0.21515 | 0.11902 | 0.20142 | 121.5271 | -0.054932 | -0.086975 | 121.7514 | 121.669 | 121.6507 | 0.14191 | 0.1236 | 121.5363 | -0.050354 | -0.013733 | 121.7972 | 121.7834 | 121.701 | 0.24719 | 0.16479 | 0.22431 | 0.073243 | 0.26093 | 0.13733 | 0.10529 | 0.10071 | 121.6324 | 121.637 | -0.16022 | -0.15106 | 121.6003 | 121.6736 | 121.5363 | 121.6507
1615.1719 | 121.9437 | -121.6187 | 0.10986 | -0.0036622 | 0.063796 | 0.013544 | 0.019053 | -0.0042532 | -0.0033966 | -0.0010105 | 0.0014953 | 0.022939 | 0.017566 | 0.015327 | -0.0026597 | 0.020307 | -0.0017069 | -0.050354 | 0.073242 | -0.041199 | -0.009155 | 0.15106 | 0.022888 | 0.050354 | 0.054932 | 0.064087 | -0.054932 | 0.064087 | 0.17395 | 0.09613 | 0.20142 | 121.5775 | -0.036621 | -0.11902 | 121.7697 | 121.669 | 121.6415 | 0.091553 | 0.064087 | 121.5637 | -0.045776 | -0.045776 | 121.7926 | 121.8201 | 121.7148 | 0.25635 | 0.15106 | 0.19226 | 0.032044 | 0.22888 | 0.11902 | 0.11444 | 0.11902 | 121.6919 | 121.6827 | -0.15106 | -0.16479 | 121.6095 | 121.6827 | 121.5683 | 121.6736
1616.9219 | 121.9574 | -121.6049 | 0.082397 | -0.0036622 | 0.064651 | 0.015894 | 0.024607 | 0.00023275 | -0.003183 | -0.0020785 | -0.0046081 | 0.025289 | 0.019062 | 0.02195 | 0.0024673 | 0.019025 | 0.0012839 | 0.004578 | 0.054932 | -0.041199 | 0.032043 | 0.16479 | 0.041199 | 0.050354 | 0.082397 | 0.054932 | -0.045776 | 0.1236 | 0.17853 | 0.082397 | 0.20142 | 121.5637 | -0.027465 | -0.050354 | 121.7697 | 121.6553 | 121.6461 | 0.091553 | 0.082398 | 121.5591 | -0.027465 | 0.041199 | 121.7834 | 121.8063 | 121.6873 | 0.24719 | 0.12817 | 0.20599 | 0.073242 | 0.2243 | 0.16937 | 0.096131 | 0.10071 | 121.6599 | 121.6599 | -0.1236 | -0.12817 | 121.637 | 121.7285 | 121.6095 | 121.6873
1618.6562 | 121.9666 | -121.6324 | 0.082397 | -0.0036622 | 0.06636 | 0.015039 | 0.022685 | -0.00019445 | -0.0027556 | 0.0011257 | -0.0015565 | 0.025075 | 0.019916 | 0.026222 | 0.00011755 | 0.018384 | -0.00021153 | -0.054932 | 0.07782 | -0.059509 | 0.004578 | 0.14191 | -0.013733 | 0.027466 | 0.059509 | 0.064087 | -0.041199 | 0.10071 | 0.16022 | 0.07782 | 0.21057 | 121.5729 | -0.004577 | -0.077819 | 121.7743 | 121.6599 | 121.6187 | 0.086975 | 0.045776 | 121.5912 | -0.01831 | 0.018311 | 121.7926 | 121.843 | 121.7102 | 0.25177 | 0.11902 | 0.20142 | 0.064087 | 0.20142 | 0.14191 | 0.13733 | 0.10529 | 121.7102 | 121.6965 | -0.14191 | -0.1236 | 121.637 | 121.7331 | 121.5775 | 121.6919
1620.3281 | 121.9437 | -121.669 | 0.10071 | 0.011597 | 0.063583 | 0.016962 | 0.021403 | -0.0046804 | -0.0016876 | -0.0016513 | -0.0046081 | 0.022939 | 0.017994 | 0.015114 | -0.00073705 | 0.019666 | -0.0012795 | -0.082397 | 0.059509 | -0.050354 | -0.036621 | 0.10071 | -0.004578 | 0.022888 | 0.013733 | 0.082397 | -0.059509 | 0.045776 | 0.14191 | 0.068665 | 0.15564 | 121.6187 | -0.041199 | -0.13733 | 121.7697 | 121.6919 | 121.6644 | 0.073242 | 0.045776 | 121.6095 | -0.018311 | -0.054932 | 121.8109 | 121.8246 | 121.7377 | 0.21515 | 0.12817 | 0.15106 | 0.013733 | 0.20142 | 0.10528 | 0.10986 | 0.14191 | 121.7285 | 121.7514 | -0.15106 | -0.16022 | 121.6324 | 121.7148 | 121.5866 | 121.6827
1622.0781 | 121.9757 | -121.6415 | 0.068665 | -0.0036622 | 0.066146 | 0.016962 | 0.024821 | 0.0025828 | -0.001474 | -0.0012241 | -0.0015565 | 0.025502 | 0.019489 | 0.020027 | 0.00011755 | 0.01988 | -0.0051247 | -0.045776 | 0.059509 | -0.041199 | 0.018311 | 0.14648 | 0.027466 | 0.054932 | 0.07782 | 0.059509 | -0.032043 | 0.09613 | 0.15564 | 0.091553 | 0.2243 | 121.6003 | -0.009156 | -0.050354 | 121.788 | 121.6965 | 121.669 | 0.096131 | 0.068665 | 121.6095 | -0.009156 | 0.027465 | 121.7972 | 121.8658 | 121.7331 | 0.25635 | 0.1236 | 0.18768 | 0.05951 | 0.18768 | 0.12817 | 0.10071 | 0.091552 | 121.7011 | 121.7011 | -0.10986 | -0.10071 | 121.6599 | 121.7377 | 121.5958 | 121.7194
1623.7656 | 121.9711 | -121.6232 | 0.082397 | -0.0036622 | 0.065719 | 0.014612 | 0.021189 | 0.0023692 | -0.0021148 | -0.0025057 | -0.0015565 | 0.024861 | 0.017566 | 0.0149 | 0.0024673 | 0.020948 | 0.0010703 | -0.004578 | 0.059509 | -0.032043 | 0.041199 | 0.17395 | 0.013733 | 0.059509 | 0.09613 | 0.054932 | -0.050354 | 0.10529 | 0.16937 | 0.10071 | 0.21515 | 121.5912 | -0.022888 | -0.041198 | 121.7972 | 121.6827 | 121.637 | 0.091552 | 0.045776 | 121.5729 | -0.027465 | 0.022889 | 121.7926 | 121.8384 | 121.7239 | 0.2655 | 0.15106 | 0.20599 | 0.073242 | 0.21973 | 0.15564 | 0.091552 | 0.10529 | 121.6827 | 121.6782 | -0.11444 | -0.13275 | 121.6644 | 121.7285 | 121.6187 | 121.7194
1625.5156 | 121.9162 | -121.6827 | 0.11444 | -0.011291 | 0.063369 | 0.015253 | 0.022257 | -0.0042532 | -0.002542 | -0.0037875 | -0.0015565 | 0.025289 | 0.019489 | 0.015327 | 0.0011855 | 0.020521 | 0.00021567 | -0.086975 | 0.07782 | -0.086975 | -0.086975 | 0.041199 | -0.082397 | -0.041199 | -0.032043 | 0.10071 | -0.073242 | 0.032043 | 0.07782 | 0 | 0.14191 | 121.5958 | -0.036621 | -0.20142 | 121.7239 | 121.6415 | 121.6003 | 0.045776 | 0.004578 | 121.6095 | -0.013733 | -0.082398 | 121.7606 | 121.8246 | 121.6827 | 0.21515 | 0.073242 | 0.12817 | 0 | 0.15106 | 0.10529 | 0.16479 | 0.17395 | 121.7606 | 121.7834 | -0.20142 | -0.18768 | 121.5958 | 121.7148 | 121.5958 | 121.6507
1627.25 | 121.875 | -121.7102 | 0.11444 | 0.0039673 | 0.066787 | 0.016748 | 0.022898 | -0.00062165 | -0.0012604 | 0.0013395 | -0.0015565 | 0.026784 | 0.019275 | 0.015755 | -0.0022325 | 0.021375 | 2.068e-06 | -0.091553 | 0.082397 | -0.073242 | -0.09613 | 0.022888 | -0.086975 | -0.045776 | -0.064087 | 0.10071 | -0.07782 | -0.018311 | 0.045776 | -0.041199 | 0.086975 | 121.637 | -0.032044 | -0.21057 | 121.7331 | 121.6644 | 121.6232 | 0.027466 | -0.013733 | 121.6324 | -0.013733 | -0.13275 | 121.756 | 121.7972 | 121.669 | 0.16479 | 0.036621 | 0.09613 | -0.022888 | 0.1236 | 0.059509 | 0.15564 | 0.17853 | 121.7926 | 121.8109 | -0.18768 | -0.19226 | 121.6141 | 121.6919 | 121.6187 | 121.6461
1629 | 121.994 | -121.6507 | 0.086975 | 0.0039673 | 0.065292 | 0.016748 | 0.020976 | 0.00087375 | -0.0023284 | -0.0016513 | -0.0015565 | 0.023152 | 0.020343 | 0.017891 | 0.0022537 | 0.020521 | -0.0046975 | -0.036621 | 0.082397 | -0.036621 | 0.022888 | 0.15106 | 0.018311 | 0.045776 | 0.054932 | 0.059509 | -0.022888 | 0.11444 | 0.16479 | 0.10529 | 0.21515 | 121.6141 | -0.004578 | -0.064087 | 121.8018 | 121.6965 | 121.669 | 0.082397 | 0.054932 | 121.6278 | -0.027466 | 0.027466 | 121.8155 | 121.8658 | 121.756 | 0.23804 | 0.12817 | 0.18768 | 0.059509 | 0.18768 | 0.13733 | 0.11902 | 0.082397 | 121.7331 | 121.7102 | -0.1236 | -0.10986 | 121.6736 | 121.7651 | 121.6141 | 121.7056
1630.75 | 122.0078 | -121.6644 | 0.10529 | -0.0036622 | 0.064865 | 0.013116 | 0.01948 | 0.00044655 | -0.0023284 | -0.0010105 | -0.0046081 | 0.023366 | 0.018207 | 0.020882 | -0.0018051 | 0.018598 | -0.0012795 | -0.054932 | 0.068665 | -0.045776 | 0 | 0.16022 | 0.045776 | 0.073242 | 0.041199 | 0.073242 | -0.054932 | 0.082397 | 0.17853 | 0.11444 | 0.21057 | 121.6187 | -0.036621 | -0.10529 | 121.8246 | 121.7377 | 121.7102 | 0.11902 | 0.091552 | 121.6095 | -0.032044 | -0.022889 | 121.843 | 121.875 | 121.7789 | 0.2655 | 0.16937 | 0.20599 | 0.045776 | 0.23346 | 0.13733 | 0.11444 | 0.12817 | 121.7331 | 121.7377 | -0.15106 | -0.16022 | 121.6644 | 121.7468 | 121.6095 | 121.7056
1632.4375 | 122.0123 | -121.6736 | 0.10071 | 0.0039673 | 0.067855 | 0.017603 | 0.02418 | -0.0029714 | -0.001474 | -0.0027195 | -0.0015565 | 0.024861 | 0.018207 | 0.013191 | 0.00033115 | 0.018384 | -0.0010659 | -0.004578 | 0.027466 | -0.041199 | 0.032043 | 0.1831 | 0.045776 | 0.064087 | 0.10529 | 0.050354 | -0.032043 | 0.10529 | 0.16937 | 0.086975 | 0.21057 | 121.6324 | -0.073242 | -0.068665 | 121.8567 | 121.7377 | 121.7194 | 0.10529 | 0.086975 | 121.6415 | -0.050354 | 0.004578 | 121.843 | 121.8842 | 121.7606 | 0.24261 | 0.11902 | 0.2243 | 0.073242 | 0.20142 | 0.13733 | 0.068665 | 0.082397 | 121.7011 | 121.7239 | -0.14191 | -0.13275 | 121.7056 | 121.7789 | 121.669 | 121.7789
1634.1875 | 121.9025 | -121.7285 | 0.10986 | 0.0039673 | 0.064437 | 0.017175 | 0.023326 | -0.0016898 | -0.0012604 | 0.0015531 | -0.0015565 | 0.025075 | 0.019275 | 0.014259 | -0.00052345 | 0.017743 | -0.0025613 | -0.086975 | 0.09613 | -0.09613 | -0.086975 | 0.041199 | -0.082397 | -0.032043 | -0.059509 | 0.091553 | -0.07782 | 0 | 0.041199 | -0.036621 | 0.11902 | 121.6324 | -0.013733 | -0.19684 | 121.7697 | 121.6965 | 121.6461 | 0.064087 | 0.013733 | 121.6507 | -0.01831 | -0.10986 | 121.7697 | 121.8475 | 121.6919 | 0.19684 | 0.041199 | 0.13733 | 0.009155 | 0.11902 | 0.07782 | 0.19226 | 0.16937 | 121.8246 | 121.8201 | -0.20599 | -0.18768 | 121.6415 | 121.7285 | 121.6415 | 121.669
1635.875 | 121.8933 | -121.7377 | 0.13733 | -0.011291 | 0.068069 | 0.016107 | 0.021189 | -0.0019034 | -0.0016876 | -0.0031467 | -0.0015565 | 0.022939 | 0.018848 | 0.0093461 | -0.0054367 | 0.016675 | 0.0017111 | -0.11444 | 0.091553 | -0.073242 | -0.10071 | 0.050354 | -0.059509 | -0.018311 | -0.082397 | 0.12817 | -0.09613 | -0.059509 | 0.054932 | -0.022888 | 0.073242 | 121.6644 | -0.045776 | -0.23804 | 121.788 | 121.7194 | 121.6782 | 0.054931 | 0.013733 | 121.6415 | -0.009155 | -0.19684 | 121.7926 | 121.8109 | 121.7148 | 0.16937 | 0.073242 | 0.1236 | -0.027466 | 0.15106 | 0.036621 | 0.16479 | 0.2243 | 121.8292 | 121.8658 | -0.21057 | -0.23346 | 121.637 | 121.6782 | 121.6232 | 121.6553
1637.625 | 121.9345 | -121.7285 | 0.1236 | 0.0039673 | 0.067001 | 0.01568 | 0.024394 | 0.0027964 | -0.0023284 | -0.0022921 | -0.0046081 | 0.025716 | 0.021198 | 0.01725 | -0.0033005 | 0.016889 | 0.00085667 | -0.041199 | 0.07782 | -0.059509 | -0.032043 | 0.11444 | -0.036621 | -0.013733 | -0.004578 | 0.091553 | -0.054932 | 0.018311 | 0.07782 | -0.013733 | 0.11444 | 121.669 | -0.045776 | -0.15564 | 121.843 | 121.7148 | 121.6919 | 0.045776 | 0.022888 | 121.6736 | -0.032043 | -0.10528 | 121.8063 | 121.843 | 121.7148 | 0.16937 | 0.041199 | 0.17395 | 0.027466 | 0.13275 | 0.073243 | 0.13733 | 0.14649 | 121.8063 | 121.8201 | -0.1831 | -0.17853 | 121.6965 | 121.7468 | 121.6873 | 121.7239
1639.375 | 122.0215 | -121.6873 | 0.09613 | -0.011291 | 0.06871 | 0.017175 | 0.022471 | 0.00023275 | -0.0046782 | -0.00079691 | -0.0015565 | 0.024221 | 0.018634 | 0.014473 | 0.0033217 | 0.019452 | -0.0044839 | -0.032043 | 0.050354 | -0.045776 | 0.013733 | 0.14648 | 0.022888 | 0.054932 | 0.082397 | 0.064087 | -0.050354 | 0.11444 | 0.16937 | 0.10529 | 0.21057 | 121.6415 | -0.045776 | -0.082397 | 121.8338 | 121.7422 | 121.7102 | 0.10071 | 0.068664 | 121.637 | -0.032043 | 0.018311 | 121.8567 | 121.8979 | 121.7926 | 0.26093 | 0.15564 | 0.19226 | 0.059509 | 0.21973 | 0.16479 | 0.09613 | 0.11444 | 121.7377 | 121.7514 | -0.14191 | -0.14648 | 121.701 | 121.8018 | 121.6553 | 121.7697
1641.0469 | 122.0352 | -121.6965 | 0.086975 | -0.0036622 | 0.06636 | 0.017175 | 0.023539 | 0.0034372 | 0.00023496 | -0.0016513 | -0.0015565 | 0.023366 | 0.017994 | 0.014473 | 0.0013991 | 0.021589 | -0.0032021 | 0 | 0.064087 | -0.027466 | 0.027466 | 0.16937 | 0.045776 | 0.068665 | 0.10529 | 0.045776 | -0.036621 | 0.1236 | 0.19226 | 0.07782 | 0.21973 | 121.669 | -0.022888 | -0.059509 | 121.8658 | 121.7651 | 121.7422 | 0.096131 | 0.073242 | 121.6599 | -0.041199 | 0.036621 | 121.8887 | 121.9162 | 121.7743 | 0.25635 | 0.11444 | 0.19684 | 0.054932 | 0.22888 | 0.16022 | 0.091553 | 0.082397 | 121.7606 | 121.7422 | -0.11444 | -0.1236 | 121.7239 | 121.8201 | 121.6965 | 121.8018
1642.7969 | 121.9574 | -121.7285 | 0.13275 | -0.0036622 | 0.065719 | 0.014398 | 0.019694 | 0.00023275 | -0.0038238 | -0.0014377 | -0.0046081 | 0.025289 | 0.018634 | 0.0078507 | -0.0037277 | 0.017316 | -0.00042513 | -0.059509 | 0.091553 | -0.07782 | -0.036621 | 0.10071 | -0.013733 | 0 | 0 | 0.10529 | -0.073242 | 0.013733 | 0.10529 | 0.018311 | 0.14648 | 121.6507 | -0.041198 | -0.16937 | 121.8292 | 121.7285 | 121.7148 | 0.07782 | 0.064087 | 121.6553 | -0.027465 | -0.11902 | 121.8338 | 121.875 | 121.7468 | 0.21973 | 0.091553 | 0.17853 | 0.041199 | 0.17853 | 0.086975 | 0.16937 | 0.17853 | 121.8201 | 121.8338 | -0.21057 | -0.20599 | 121.6919 | 121.7422 | 121.669 | 121.7285
1644.5312 | 121.9254 | -121.7194 | 0.14191 | -0.0036622 | 0.066787 | 0.015039 | 0.022257 | -0.001476 | -0.0016876 | -0.0016513 | -0.0015565 | 0.024007 | 0.019275 | 0.016395 | -0.0018051 | 0.017103 | -0.0044839 | -0.059509 | 0.10529 | -0.073242 | -0.050354 | 0.10071 | -0.032043 | 0.004578 | -0.027466 | 0.082397 | -0.059509 | 0.013733 | 0.086975 | -0.018311 | 0.1236 | 121.6461 | -0.036621 | -0.19226 | 121.8201 | 121.7239 | 121.6873 | 0.07782 | 0.041199 | 121.6599 | -0.05951 | -0.12817 | 121.8063 | 121.843 | 121.701 | 0.1831 | 0.041198 | 0.17395 | 0.022888 | 0.14648 | 0.073242 | 0.17853 | 0.14191 | 121.8246 | 121.8018 | -0.21515 | -0.20142 | 121.669 | 121.7331 | 121.6599 | 121.6919
1646.2031 | 122.049 | -121.7148 | 0.10529 | -0.0036622 | 0.067428 | 0.019739 | 0.021403 | -0.00040805 | 0.00044856 | -0.0040011 | -0.0015565 | 0.022512 | 0.019703 | 0.014259 | -0.0015915 | 0.019666 | 0.00064307 | -0.013733 | 0.045776 | -0.045776 | 0.027466 | 0.20142 | 0.041199 | 0.054932 | 0.10529 | 0.045776 | -0.018311 | 0.091553 | 0.17853 | 0.091553 | 0.19226 | 121.669 | -0.05951 | -0.07782 | 121.9162 | 121.7697 | 121.756 | 0.10071 | 0.086975 | 121.6965 | -0.05951 | -0.013733 | 121.8933 | 121.907 | 121.8063 | 0.21057 | 0.10986 | 0.24719 | 0.073242 | 0.19684 | 0.10986 | 0.091552 | 0.064087 | 121.7606 | 121.7606 | -0.15106 | -0.1236 | 121.7422 | 121.8063 | 121.701 | 121.8201
1647.9531 | 121.962 | -121.7468 | 0.1236 | -0.011291 | 0.065078 | 0.013757 | 0.022685 | 0.0017282 | -0.003183 | -0.0022921 | -0.0046081 | 0.024221 | 0.019703 | 0.0055009 | -0.0024461 | 0.017743 | -0.0023477 | -0.068665 | 0.091553 | -0.073242 | -0.068665 | 0.073242 | -0.027466 | -0.013733 | -0.018311 | 0.10986 | -0.073242 | 0.009155 | 0.10071 | 0.027466 | 0.14191 | 121.6736 | -0.032043 | -0.19226 | 121.8201 | 121.7331 | 121.7194 | 0.059509 | 0.045776 | 121.6736 | -0.013733 | -0.11444 | 121.8475 | 121.8887 | 121.7743 | 0.21515 | 0.10071 | 0.14648 | 0.004577 | 0.17395 | 0.082397 | 0.16479 | 0.18311 | 121.8384 | 121.8567 | -0.19684 | -0.19684 | 121.6782 | 121.756 | 121.6782 | 121.7285
1649.6875 | 121.9666 | -121.7743 | 0.11902 | 0.011597 | 0.066787 | 0.013757 | 0.022898 | -0.00040805 | -0.0027556 | 5.7688e-05 | 0.0014953 | 0.025502 | 0.020771 | 0.017677 | 0.00011755 | 0.018171 | -0.0053385 | -0.09613 | 0.091553 | -0.082397 | -0.10529 | 0.036621 | -0.091553 | -0.050354 | -0.064087 | 0.091553 | -0.073242 | 0.004578 | 0.045776 | -0.027466 | 0.10071 | 121.6919 | -0.027466 | -0.22431 | 121.8109 | 121.7239 | 121.6827 | 0.032043 | -0.009156 | 121.7011 | -0.027466 | -0.11444 | 121.8201 | 121.875 | 121.7468 | 0.17395 | 0.045776 | 0.11902 | -0.022889 | 0.11902 | 0.07782 | 0.17395 | 0.16479 | 121.8658 | 121.8658 | -0.20142 | -0.19226 | 121.669 | 121.7789 | 121.6782 | 121.7102
1651.3594 | 121.9528 | -121.7697 | 0.11444 | -0.0036622 | 0.063796 | 0.013971 | 0.020548 | -0.00062165 | -0.0046782 | -0.0029331 | -0.0015565 | 0.022298 | 0.019916 | 0.021095 | -0.0045823 | 0.017316 | -0.00085233 | -0.041199 | 0.068665 | -0.050354 | -0.032043 | 0.10529 | 0.022888 | 0.022888 | -0.022888 | 0.09613 | -0.068665 | -0.032043 | 0.07782 | 0.004578 | 0.10071 | 121.7194 | -0.045776 | -0.14648 | 121.875 | 121.7926 | 121.7926 | 0.073242 | 0.073242 | 121.701 | -0.018311 | -0.14648 | 121.8475 | 121.8704 | 121.7743 | 0.16937 | 0.073243 | 0.15564 | 0.018311 | 0.14649 | 0.036622 | 0.11902 | 0.16479 | 121.8384 | 121.8658 | -0.16479 | -0.18311 | 121.7377 | 121.7377 | 121.7285 | 121.7468
1653.1094 | 122.081 | -121.7239 | 0.091553 | -0.011291 | 0.06636 | 0.019312 | 0.021617 | 0.0015146 | -0.0021148 | -0.0037875 | 0.0014953 | 0.023152 | 0.021412 | 0.0099869 | 0.0011855 | 0.017316 | -0.0040567 | -0.018311 | 0.018311 | -0.022888 | 0.041199 | 0.19226 | 0.045776 | 0.064087 | 0.091553 | 0.041199 | -0.032043 | 0.10529 | 0.17395 | 0.086975 | 0.18768 | 121.7011 | -0.073242 | -0.050354 | 121.9162 | 121.788 | 121.7697 | 0.086975 | 0.068664 | 121.6919 | -0.050354 | 0.013733 | 121.8979 | 121.9116 | 121.8109 | 0.21973 | 0.11902 | 0.21515 | 0.064087 | 0.20599 | 0.13733 | 0.041199 | 0.073242 | 121.7422 | 121.7651 | -0.11444 | -0.1236 | 121.7651 | 121.8292 | 121.7056 | 121.8155
1654.8438 | 122.0215 | -121.756 | 0.10071 | 0.0039673 | 0.064224 | 0.01568 | 0.019908 | -0.001476 | -0.0033966 | 5.7688e-05 | -0.0046081 | 0.022939 | 0.018421 | 0.013191 | -0.0035141 | 0.018384 | -0.0046975 | -0.068665 | 0.068665 | -0.059509 | -0.045776 | 0.11444 | -0.004578 | 0.027466 | -0.013733 | 0.07782 | -0.050354 | 0.041199 | 0.1236 | 0.064087 | 0.15106 | 121.6965 | -0.032043 | -0.14648 | 121.8704 | 121.7834 | 121.7514 | 0.086975 | 0.054931 | 121.7056 | -0.022888 | -0.059509 | 121.8796 | 121.907 | 121.8201 | 0.20142 | 0.11444 | 0.17395 | 0.013733 | 0.17395 | 0.091553 | 0.12817 | 0.12817 | 121.8246 | 121.8338 | -0.16022 | -0.15106 | 121.7102 | 121.7972 | 121.6873 | 121.7422
1656.5781 | 122.0306 | -121.7697 | 0.1236 | -0.0036622 | 0.065719 | 0.014825 | 0.022898 | 0.00023275 | -0.0038238 | -0.0010105 | -0.0015565 | 0.021871 | 0.018634 | 0.022591 | -0.00052345 | 0.018598 | -0.00063873 | -0.073242 | 0.050354 | -0.064087 | -0.032043 | 0.11902 | -0.013733 | 0.045776 | 0 | 0.059509 | -0.045776 | 0.045776 | 0.10986 | 0.045776 | 0.15106 | 121.7056 | -0.073242 | -0.15564 | 121.8887 | 121.8155 | 121.756 | 0.10986 | 0.050354 | 121.7239 | -0.064087 | -0.07782 | 121.8796 | 121.9208 | 121.8155 | 0.19684 | 0.091552 | 0.18311 | 0.032044 | 0.15564 | 0.091552 | 0.11444 | 0.10528 | 121.8201 | 121.8292 | -0.18768 | -0.16937 | 121.7377 | 121.8155 | 121.6965 | 121.7697
1658.25 | 121.9437 | -121.8018 | 0.1236 | 0.0039673 | 0.068069 | 0.015466 | 0.023753 | -0.0010488 | -0.001474 | -0.0022921 | -0.0076599 | 0.023793 | 0.02013 | 0.0093461 | 0.0026809 | 0.020521 | -0.0079019 | -0.09613 | 0.086975 | -0.082397 | -0.10986 | 0.013733 | -0.086975 | -0.041199 | -0.086975 | 0.10529 | -0.064087 | -0.018311 | 0.013733 | -0.059509 | 0.10071 | 121.7194 | -0.036621 | -0.23346 | 121.8155 | 121.7606 | 121.7148 | 0.041198 | -0.004578 | 121.7377 | -0.01831 | -0.14191 | 121.8155 | 121.9025 | 121.7422 | 0.1648 | 0.004578 | 0.09613 | -0.027466 | 0.07782 | 0.045776 | 0.16937 | 0.16937 | 121.8887 | 121.907 | -0.20599 | -0.18768 | 121.6919 | 121.7834 | 121.7056 | 121.7148
1659.9844 | 121.9849 | -121.8109 | 0.13733 | -0.011291 | 0.065078 | 0.016107 | 0.022471 | 0.0019418 | 0.00044856 | -0.0022921 | -0.0015565 | 0.024221 | 0.020343 | 0.016609 | -0.00095065 | 0.018384 | -0.0046975 | -0.082397 | 0.10071 | -0.086975 | -0.09613 | 0.027466 | -0.091553 | -0.045776 | -0.09613 | 0.086975 | -0.09613 | -0.032043 | 0.022888 | -0.054932 | 0.10071 | 121.7239 | -0.036621 | -0.23346 | 121.8384 | 121.7651 | 121.7194 | 0.041199 | -0.004578 | 121.7148 | -0.050354 | -0.16937 | 121.8338 | 121.9116 | 121.756 | 0.19684 | 0.041198 | 0.11444 | -0.009155 | 0.11902 | 0.064087 | 0.18768 | 0.1831 | 121.9116 | 121.8979 | -0.2243 | -0.23346 | 121.7148 | 121.7789 | 121.7285 | 121.7148
1661.7188 | 122.0856 | -121.7514 | 0.10529 | -0.011291 | 0.065292 | 0.016748 | 0.022471 | -0.00040805 | -0.0027556 | -0.0014377 | -0.0015565 | 0.024221 | 0.021839 | 0.020241 | 0.0031081 | 0.018171 | -0.00085233 | -0.064087 | 0.07782 | -0.059509 | -0.041199 | 0.10986 | -0.018311 | 0.022888 | 0.032043 | 0.073242 | -0.041199 | 0.082397 | 0.14648 | 0.073242 | 0.19684 | 121.6919 | -0.027466 | -0.14649 | 121.8613 | 121.7743 | 121.7331 | 0.082397 | 0.041198 | 121.7102 | -0.032044 | -0.022889 | 121.8979 | 121.9482 | 121.8246 | 0.23804 | 0.11444 | 0.16937 | 0.01831 | 0.18768 | 0.1236 | 0.13733 | 0.11444 | 121.8292 | 121.8246 | -0.16479 | -0.14649 | 121.7102 | 121.8338 | 121.6873 | 121.7834
1663.4844 | 122.0627 | -121.7789 | 0.073242 | -0.0036622 | 0.066146 | 0.016321 | 0.022898 | 0.0010874 | 0.00023496 | -0.0010105 | -0.0046081 | 0.023793 | 0.02013 | 0.020027 | -0.0020187 | 0.019025 | 0.0017111 | -0.041199 | 0.045776 | -0.041199 | 0.022888 | 0.17853 | 0.032043 | 0.050354 | 0.086975 | 0.045776 | -0.045776 | 0.07782 | 0.13733 | 0.073242 | 0.16937 | 121.7377 | -0.027466 | -0.050354 | 121.9574 | 121.8292 | 121.8109 | 0.091553 | 0.073242 | 121.7331 | -0.027466 | 0.004578 | 121.9162 | 121.9482 | 121.8521 | 0.21515 | 0.11902 | 0.21973 | 0.064087 | 0.18311 | 0.1236 | 0.086975 | 0.091552 | 121.8246 | 121.8246 | -0.11444 | -0.11902 | 121.8018 | 121.8567 | 121.7377 | 121.8658
1665.1562 | 122.0947 | -121.7789 | 0.11444 | 0.0039673 | 0.062728 | 0.01568 | 0.020335 | -0.0051076 | -0.002542 | -0.0016513 | -0.0046081 | 0.021657 | 0.017139 | 0.018104 | -0.0020187 | 0.017957 | 0.0021383 | -0.054932 | 0.059509 | -0.050354 | 0.018311 | 0.16479 | 0.059509 | 0.082397 | 0.068665 | 0.050354 | -0.045776 | 0.091553 | 0.19226 | 0.11902 | 0.21057 | 121.7285 | -0.054932 | -0.09613 | 121.9437 | 121.8613 | 121.8384 | 0.13275 | 0.10986 | 121.7331 | -0.064087 | -0.022888 | 121.9711 | 121.9894 | 121.8979 | 0.25635 | 0.16479 | 0.21515 | 0.068665 | 0.23804 | 0.13733 | 0.10986 | 0.09613 | 121.8384 | 121.8292 | -0.16479 | -0.16022 | 121.7972 | 121.8704 | 121.7239 | 121.8475
1666.9062 | 122.0856 | -121.7697 | 0.11444 | 0.0039673 | 0.065292 | 0.015253 | 0.019908 | -0.0025442 | -0.0029694 | -0.0035739 | -0.0015565 | 0.023152 | 0.017994 | 0.019173 | -0.0035141 | 0.017316 | -0.0027749 | -0.027466 | 0.054932 | -0.045776 | 0.036621 | 0.20142 | 0.086975 | 0.091553 | 0.082397 | 0.064087 | -0.022888 | 0.082397 | 0.18768 | 0.11444 | 0.1831 | 121.7239 | -0.059509 | -0.07782 | 121.9711 | 121.8613 | 121.8567 | 0.13733 | 0.13275 | 121.7468 | -0.050354 | -0.032044 | 121.9574 | 121.9528 | 121.8842 | 0.20599 | 0.13733 | 0.24719 | 0.082397 | 0.21057 | 0.10528 | 0.10071 | 0.086975 | 121.8246 | 121.8338 | -0.16022 | -0.13733 | 121.8063 | 121.8521 | 121.7422 | 121.8521
1668.5938 | 121.994 | -121.8246 | 0.14648 | 0.0039673 | 0.06871 | 0.013757 | 0.025675 | -0.00040805 | -0.004251 | -0.0029331 | -0.0046081 | 0.024861 | 0.02013 | 0.016823 | 0.00075835 | 0.017316 | -0.0044839 | -0.068665 | 0.091553 | -0.086975 | -0.086975 | 0.032043 | -0.10529 | -0.041199 | -0.082397 | 0.09613 | -0.07782 | -0.013733 | 0.041199 | -0.045776 | 0.10071 | 121.7377 | -0.054931 | -0.23346 | 121.8567 | 121.7834 | 121.7194 | 0.045776 | -0.018311 | 121.7468 | -0.050354 | -0.16022 | 121.8658 | 121.9254 | 121.7789 | 0.17853 | 0.032044 | 0.11902 | 0 | 0.11902 | 0.064087 | 0.17853 | 0.17395 | 121.9162 | 121.9208 | -0.23346 | -0.2243 | 121.7377 | 121.8109 | 121.756 | 121.7422
1670.3438 | 122.1222 | -121.8018 | 0.11902 | -0.011291 | 0.063369 | 0.014185 | 0.022685 | -0.0044668 | -0.0033966 | -0.0018649 | 0.0045471 | 0.022298 | 0.019703 | 0.013405 | -0.0030869 | 0.017957 | 0.0012839 | -0.041199 | 0.064087 | -0.050354 | 0.009155 | 0.16022 | 0.045776 | 0.07782 | 0.07782 | 0.064087 | -0.045776 | 0.073242 | 0.18768 | 0.11902 | 0.19684 | 121.7514 | -0.054932 | -0.10986 | 121.962 | 121.8796 | 121.8475 | 0.12817 | 0.09613 | 121.756 | -0.054932 | -0.045777 | 121.9894 | 121.9986 | 121.9208 | 0.24261 | 0.16479 | 0.21057 | 0.059509 | 0.23346 | 0.11902 | 0.11444 | 0.10986 | 121.8658 | 121.8658 | -0.16937 | -0.16479 | 121.8109 | 121.875 | 121.7606 | 121.8796
1672.0156 | 122.0078 | -121.8246 | 0.11902 | -0.011291 | 0.065292 | 0.013971 | 0.02183 | 0.0040782 | -0.0023284 | -0.00036951 | 0.0014953 | 0.024648 | 0.019703 | 0.015968 | -0.0043687 | 0.015394 | -0.0019205 | -0.045776 | 0.059509 | -0.064087 | -0.032043 | 0.11444 | -0.004578 | 0.013733 | -0.045776 | 0.09613 | -0.050354 | -0.045776 | 0.068665 | -0.004578 | 0.091553 | 121.7606 | -0.05951 | -0.15106 | 121.9391 | 121.8384 | 121.8201 | 0.07782 | 0.059509 | 121.7743 | -0.022889 | -0.16479 | 121.8933 | 121.9162 | 121.8201 | 0.14191 | 0.045776 | 0.17853 | 0.032044 | 0.11902 | 0.004578 | 0.1236 | 0.14648 | 121.8842 | 121.9208 | -0.18311 | -0.16937 | 121.7926 | 121.7789 | 121.7789 | 121.7789
1673.75 | 122.0352 | -121.8109 | 0.11902 | 0.011597 | 0.067642 | 0.014825 | 0.022471 | -0.001476 | -0.0021148 | -0.00058311 | -0.0046081 | 0.025929 | 0.020771 | 0.012337 | -0.00095065 | 0.016889 | -0.0023477 | -0.036621 | 0.086975 | -0.073242 | -0.027466 | 0.10986 | -0.009155 | 0 | -0.004578 | 0.10071 | -0.059509 | 0.032043 | 0.10529 | 0.022888 | 0.14191 | 121.7377 | -0.032044 | -0.14649 | 121.9208 | 121.8109 | 121.8018 | 0.073242 | 0.064087 | 121.7514 | -0.018311 | -0.086976 | 121.9162 | 121.9528 | 121.8338 | 0.20142 | 0.082397 | 0.18311 | 0.045776 | 0.16479 | 0.091552 | 0.16022 | 0.16022 | 121.8979 | 121.9116 | -0.19226 | -0.17853 | 121.7834 | 121.843 | 121.7743 | 121.8063
1675.5 | 122.0352 | -121.7789 | 0.10986 | -0.0036622 | 0.066787 | 0.015039 | 0.023539 | 0.0019418 | -0.0027556 | -0.0020785 | 0.0014953 | 0.025929 | 0.017994 | 0.017891 | -0.0026597 | 0.019666 | 0.00085667 | -0.050354 | 0.086975 | -0.082397 | -0.041199 | 0.086975 | -0.013733 | 0.013733 | 0 | 0.091553 | -0.086975 | 0.036621 | 0.10071 | 0.022888 | 0.14191 | 121.6965 | -0.022888 | -0.15106 | 121.8658 | 121.7926 | 121.7651 | 0.09613 | 0.068664 | 121.6919 | -0.01831 | -0.073242 | 121.8796 | 121.9208 | 121.8018 | 0.22888 | 0.10986 | 0.16937 | 0.041198 | 0.18768 | 0.1236 | 0.16937 | 0.17853 | 121.8658 | 121.8704 | -0.19226 | -0.19684 | 121.7377 | 121.8155 | 121.7285 | 121.7789
1677.2188 | 122.113 | -121.7926 | 0.10986 | -0.011291 | 0.065933 | 0.015253 | 0.021189 | -0.004894 | -0.0023284 | 0.00048489 | 0.0014953 | 0.022725 | 0.02013 | 0.018318 | -0.00030965 | 0.01753 | -0.0012795 | -0.059509 | 0.068665 | -0.041199 | -0.013733 | 0.1236 | 0.013733 | 0.064087 | 0.041199 | 0.054932 | -0.050354 | 0.082397 | 0.18768 | 0.1236 | 0.18768 | 121.7514 | -0.041198 | -0.1236 | 121.9162 | 121.8567 | 121.8063 | 0.10529 | 0.054932 | 121.7422 | -0.054931 | -0.027466 | 121.9803 | 121.9803 | 121.9162 | 0.23804 | 0.17395 | 0.16479 | 0.027466 | 0.23804 | 0.13275 | 0.10986 | 0.10529 | 121.8613 | 121.8475 | -0.15106 | -0.16022 | 121.7789 | 121.875 | 121.7331 | 121.8338
1678.9062 | 122.1039 | -121.7697 | 0.16479 | -0.018921 | 0.065933 | 0.014185 | 0.020976 | -0.0044668 | -0.001474 | 5.7688e-05 | -0.0046081 | 0.021657 | 0.019703 | 0.016395 | -0.0030869 | 0.019452 | -0.0044839 | -0.054932 | 0.059509 | -0.050354 | -0.004578 | 0.1831 | 0.064087 | 0.07782 | 0.073242 | 0.059509 | -0.050354 | 0.091553 | 0.19226 | 0.13733 | 0.19684 | 121.7194 | -0.10529 | -0.16937 | 121.9528 | 121.8475 | 121.8338 | 0.12817 | 0.11444 | 121.7194 | -0.10529 | -0.073242 | 121.962 | 121.9666 | 121.907 | 0.24719 | 0.18768 | 0.23346 | 0.045776 | 0.24261 | 0.14191 | 0.10986 | 0.10986 | 121.8292 | 121.8292 | -0.21515 | -0.21515 | 121.7651 | 121.8613 | 121.7148 | 121.843
1680.6562 | 122.1359 | -121.8475 | 0.09613 | 0.0039673 | 0.063369 | 0.012689 | 0.020762 | 0.00023275 | -0.0023284 | -0.00036951 | 0.0014953 | 0.023152 | 0.017353 | 0.019173 | -0.00073705 | 0.017743 | -0.0051247 | -0.036621 | 0.050354 | -0.045776 | 0.036621 | 0.21515 | 0.082397 | 0.10071 | 0.11902 | 0.064087 | -0.059509 | 0.1236 | 0.21973 | 0.14191 | 0.20142 | 121.8018 | -0.045776 | -0.059509 | 122.0627 | 121.9482 | 121.9299 | 0.14648 | 0.12817 | 121.788 | -0.032043 | 0.027466 | 122.0673 | 122.0489 | 121.9894 | 0.26093 | 0.20142 | 0.26093 | 0.082397 | 0.27924 | 0.1831 | 0.09613 | 0.1236 | 121.8979 | 121.9116 | -0.14191 | -0.15564 | 121.8842 | 121.9711 | 121.8109 | 121.9666
1682.3906 | 122.1222 | -121.8292 | 0.10986 | -0.0036622 | 0.062942 | 0.014825 | 0.020976 | -0.0042532 | -0.0019012 | -0.00079691 | -0.0076599 | 0.022939 | 0.018634 | 0.016182 | 0.0011855 | 0.017103 | -0.0036295 | -0.054932 | 0.050354 | -0.054932 | 0.009155 | 0.14648 | 0.041199 | 0.07782 | 0.054932 | 0.059509 | -0.054932 | 0.07782 | 0.1831 | 0.11444 | 0.20142 | 121.7743 | -0.059509 | -0.10071 | 121.9757 | 121.907 | 121.8704 | 0.13275 | 0.096131 | 121.7743 | -0.050354 | -0.032043 | 122.0123 | 122.0306 | 121.9437 | 0.25635 | 0.16937 | 0.20142 | 0.064087 | 0.23804 | 0.13275 | 0.10529 | 0.11444 | 121.8796 | 121.8887 | -0.16479 | -0.16479 | 121.8384 | 121.907 | 121.7743 | 121.8842
1684.0781 | 122.1313 | -121.8338 | 0.10986 | -0.0036622 | 0.064865 | 0.015466 | 0.021189 | -0.0019034 | -0.0033966 | 0.00069849 | -0.0046081 | 0.024434 | 0.017353 | 0.017891 | -0.0022325 | 0.019239 | -0.0036295 | -0.013733 | 0.059509 | -0.054932 | 0.054932 | 0.20599 | 0.07782 | 0.09613 | 0.10529 | 0.054932 | -0.032043 | 0.082397 | 0.21057 | 0.12817 | 0.19226 | 121.7789 | -0.050354 | -0.054931 | 122.0398 | 121.9299 | 121.9116 | 0.15106 | 0.13275 | 121.8018 | -0.054931 | -0.027466 | 122.0444 | 122.0261 | 121.962 | 0.2243 | 0.16022 | 0.26093 | 0.10986 | 0.24261 | 0.11444 | 0.11444 | 0.086975 | 121.8933 | 121.8887 | -0.16479 | -0.14191 | 121.8887 | 121.9162 | 121.8201 | 121.9391
1685.75 | 122.0215 | -121.8521 | 0.14191 | -0.0036622 | 0.06636 | 0.014612 | 0.023966 | 0.0040782 | -0.0036102 | -0.0010105 | -0.0015565 | 0.025289 | 0.019703 | 0.016182 | 0.00054475 | 0.017103 | -0.00042513 | -0.082397 | 0.086975 | -0.07782 | -0.10986 | 0.018311 | -0.091553 | -0.068665 | -0.068665 | 0.082397 | -0.059509 | -0.018311 | 0.027466 | -0.054932 | 0.10071 | 121.7743 | -0.054932 | -0.25177 | 121.8704 | 121.7834 | 121.7606 | 0.009155 | -0.013733 | 121.7926 | -0.05951 | -0.16022 | 121.8796 | 121.9528 | 121.7972 | 0.16022 | 0.004577 | 0.096131 | -0.032043 | 0.086975 | 0.041198 | 0.16479 | 0.14191 | 121.9391 | 121.9345 | -0.21973 | -0.20142 | 121.7422 | 121.8338 | 121.7697 | 121.7834
1687.4844 | 122.1405 | -121.8338 | 0.10529 | -0.0036622 | 0.066787 | 0.01568 | 0.020548 | -0.0036124 | -0.0021148 | -0.0031467 | -0.0046081 | 0.022298 | 0.019703 | 0.015114 | -0.0022325 | 0.018598 | 0.00042947 | -0.064087 | 0.059509 | -0.059509 | -0.013733 | 0.14648 | 0.027466 | 0.064087 | 0.041199 | 0.064087 | -0.050354 | 0.073242 | 0.17853 | 0.10529 | 0.20142 | 121.7743 | -0.045777 | -0.11902 | 121.9803 | 121.8979 | 121.8613 | 0.1236 | 0.086975 | 121.7834 | -0.041199 | -0.032044 | 122.0123 | 122.0352 | 121.9391 | 0.25177 | 0.15564 | 0.20599 | 0.045776 | 0.22888 | 0.1236 | 0.11902 | 0.11444 | 121.8933 | 121.8979 | -0.16479 | -0.15564 | 121.8201 | 121.907 | 121.7697 | 121.875
1689.1719 | 122.0398 | -121.8567 | 0.14648 | -0.011291 | 0.06636 | 0.014612 | 0.023112 | -0.001476 | -0.0019012 | -0.00079691 | 0.0045471 | 0.025929 | 0.020771 | 0.020454 | -0.0018051 | 0.019025 | -0.0053385 | -0.073242 | 0.10071 | -0.091553 | -0.086975 | 0.036621 | -0.050354 | -0.032043 | -0.07782 | 0.1236 | -0.07782 | -0.022888 | 0.064087 | -0.013733 | 0.10986 | 121.7651 | -0.045776 | -0.23346 | 121.8933 | 121.8246 | 121.8063 | 0.05951 | 0.041199 | 121.7789 | -0.022888 | -0.16937 | 121.9208 | 121.9666 | 121.843 | 0.18768 | 0.064087 | 0.12817 | 0.004578 | 0.14191 | 0.054932 | 0.19226 | 0.20142 | 121.9574 | 121.9803 | -0.23804 | -0.2243 | 121.7697 | 121.8338 | 121.7834 | 121.7789
1690.9375 | 122.0764 | -121.8567 | 0.1236 | -0.0036622 | 0.067001 | 0.014825 | 0.023539 | -0.00019445 | -0.004251 | -0.0025057 | 0.0014953 | 0.026784 | 0.017139 | 0.022804 | -0.0018051 | 0.017103 | -0.00063873 | -0.064087 | 0.09613 | -0.082397 | -0.027466 | 0.11444 | -0.018311 | 0.018311 | 0.022888 | 0.10986 | -0.059509 | 0.045776 | 0.11444 | 0.027466 | 0.13733 | 121.7743 | -0.027466 | -0.15106 | 121.9711 | 121.875 | 121.8384 | 0.10071 | 0.064086 | 121.7972 | -0.013733 | -0.07782 | 121.9711 | 121.994 | 121.8842 | 0.19684 | 0.086975 | 0.19684 | 0.054931 | 0.17395 | 0.10528 | 0.17853 | 0.16937 | 121.9528 | 121.9666 | -0.20599 | -0.1831 | 121.8292 | 121.9025 | 121.7926 | 121.8796
1692.6875 | 122.1313 | -121.7834 | 0.14191 | -0.0036622 | 0.064651 | 0.016107 | 0.02183 | -0.0012624 | -0.0033966 | 5.7688e-05 | 0.0045471 | 0.023793 | 0.019275 | 0.018532 | 0.00054475 | 0.01988 | -0.0038431 | -0.032043 | 0.045776 | -0.041199 | 0.018311 | 0.18768 | 0.018311 | 0.064087 | 0.07782 | 0.073242 | -0.032043 | 0.091553 | 0.17395 | 0.082397 | 0.18768 | 121.7422 | -0.096131 | -0.1236 | 121.9711 | 121.8475 | 121.8018 | 0.10529 | 0.05951 | 121.7514 | -0.068665 | -0.050354 | 121.9574 | 121.9711 | 121.8658 | 0.21973 | 0.11444 | 0.22888 | 0.05951 | 0.20599 | 0.1236 | 0.086975 | 0.10529 | 121.8292 | 121.8567 | -0.18311 | -0.17395 | 121.8018 | 121.875 | 121.7514 | 121.8613
1694.4219 | 122.113 | -121.843 | 0.13733 | -0.011291 | 0.065719 | 0.01568 | 0.022685 | 0.0015146 | -0.0016876 | -0.0029331 | -0.0015565 | 0.024007 | 0.019275 | 0.0196 | 0.00075835 | 0.019666 | -0.0012795 | -0.041199 | 0.054932 | -0.059509 | -0.013733 | 0.16022 | 0.013733 | 0.032043 | 0.045776 | 0.054932 | -0.041199 | 0.050354 | 0.12817 | 0.054932 | 0.16479 | 121.7834 | -0.082397 | -0.15106 | 122.0032 | 121.875 | 121.8567 | 0.091552 | 0.073242 | 121.8018 | -0.082397 | -0.086975 | 121.9711 | 122.0078 | 121.8979 | 0.20599 | 0.096131 | 0.21973 | 0.045776 | 0.16937 | 0.091553 | 0.11444 | 0.096131 | 121.8979 | 121.8979 | -0.19684 | -0.17853 | 121.8292 | 121.8933 | 121.8018 | 121.8887
1696.0938 | 122.049 | -121.8201 | 0.22888 | -0.0036622 | 0.065933 | 0.014398 | 0.019908 | -0.001476 | -0.0033966 | -0.0018649 | -0.0046081 | 0.024648 | 0.02013 | 0.014473 | -0.0043687 | 0.017743 | -0.00021153 | -0.10071 | 0.091553 | -0.07782 | -0.082397 | 0.041199 | -0.032043 | -0.022888 | -0.082397 | 0.10071 | -0.073242 | -0.032043 | 0.059509 | -0.009155 | 0.091553 | 121.7422 | -0.13733 | -0.31128 | 121.8613 | 121.7972 | 121.788 | 0.054932 | 0.045777 | 121.7468 | -0.12817 | -0.26093 | 121.8796 | 121.9116 | 121.8109 | 0.16479 | 0.064087 | 0.11902 | -0.004577 | 0.13275 | 0.041199 | 0.16937 | 0.17395 | 121.9116 | 121.9208 | -0.3067 | -0.30212 | 121.7377 | 121.788 | 121.7194 | 121.7377
1697.8438 | 122.113 | -121.875 | 0.13275 | -0.011291 | 0.06636 | 0.014825 | 0.022257 | 1.915e-05 | -0.0021148 | -0.00058311 | 0.0045471 | 0.023793 | 0.019916 | 0.022591 | -0.0015915 | 0.018171 | 2.068e-06 | -0.073242 | 0.054932 | -0.045776 | -0.036621 | 0.10986 | -0.009155 | 0.027466 | -0.013733 | 0.07782 | -0.045776 | 0.041199 | 0.13275 | 0.041199 | 0.17395 | 121.8292 | -0.077819 | -0.16937 | 121.9849 | 121.9025 | 121.8658 | 0.073242 | 0.036621 | 121.8292 | -0.054931 | -0.091552 | 122.0078 | 122.049 | 121.9162 | 0.21973 | 0.086975 | 0.15564 | 0.009155 | 0.17853 | 0.086975 | 0.10071 | 0.1236 | 121.9299 | 121.9528 | -0.17853 | -0.17853 | 121.8384 | 121.9162 | 121.8018 | 121.8613
1699.5156 | 122.0306 | -121.8842 | 0.14191 | -0.011291 | 0.06401 | 0.013544 | 0.022044 | -0.0033986 | -0.003183 | -0.0044285 | -0.0076599 | 0.024861 | 0.020343 | 0.012978 | -0.0030869 | 0.017316 | -0.00042513 | -0.11444 | 0.09613 | -0.086975 | -0.091553 | 0.050354 | -0.036621 | -0.022888 | -0.082397 | 0.10986 | -0.091553 | -0.050354 | 0.045776 | -0.022888 | 0.086975 | 121.7972 | -0.045777 | -0.23346 | 121.9345 | 121.8613 | 121.8475 | 0.064087 | 0.050354 | 121.7926 | -0.032044 | -0.19226 | 121.9299 | 121.9711 | 121.8613 | 0.17853 | 0.068665 | 0.13733 | -0.004578 | 0.13733 | 0.041199 | 0.1831 | 0.20142 | 121.9803 | 121.994 | -0.22888 | -0.23346 | 121.7926 | 121.8338 | 121.7697 | 121.8018
1701.25 | 122.0261 | -121.8887 | 0.14648 | -0.0036622 | 0.06636 | 0.015039 | 0.023966 | 0.0017282 | -0.0023284 | -0.0018649 | -0.0046081 | 0.024434 | 0.019489 | 0.0091325 | -0.00030965 | 0.017957 | -0.00021153 | -0.086975 | 0.10071 | -0.091553 | -0.10071 | 0.013733 | -0.10071 | -0.068665 | -0.10071 | 0.09613 | -0.064087 | -0.027466 | 0.018311 | -0.086975 | 0.10071 | 121.7972 | -0.045776 | -0.24719 | 121.9025 | 121.8201 | 121.788 | 0.022888 | -0.009155 | 121.8246 | -0.050354 | -0.17395 | 121.907 | 121.9894 | 121.8018 | 0.1648 | -0.022888 | 0.10529 | -0.009155 | 0.082398 | 0.036621 | 0.19226 | 0.16022 | 121.9894 | 121.9849 | -0.23804 | -0.21057 | 121.788 | 121.8613 | 121.8018 | 121.788
1703 | 122.0627 | -121.8887 | 0.13275 | -0.0036622 | 0.067001 | 0.015894 | 0.025035 | -0.0027578 | -0.00083304 | -0.00036951 | -0.0076599 | 0.025075 | 0.018848 | 0.013832 | -0.0018051 | 0.017316 | -0.0038431 | -0.054932 | 0.082397 | -0.073242 | -0.050354 | 0.09613 | -0.036621 | -0.018311 | -0.018311 | 0.086975 | -0.059509 | 0.004578 | 0.073242 | -0.027466 | 0.11902 | 121.8155 | -0.050354 | -0.18311 | 121.9849 | 121.8704 | 121.8521 | 0.054931 | 0.036621 | 121.8292 | -0.045776 | -0.12817 | 121.962 | 122.0078 | 121.8613 | 0.17853 | 0.032043 | 0.16937 | 0.022888 | 0.13275 | 0.064087 | 0.15564 | 0.14648 | 121.9711 | 121.9757 | -0.20599 | -0.19226 | 121.8384 | 121.8933 | 121.8338 | 121.8704
1704.6719 | 122.1405 | -121.8704 | 0.11902 | -0.0036622 | 0.065078 | 0.01568 | 0.022471 | 1.915e-05 | -0.00083304 | -0.0037875 | 0.0014953 | 0.022298 | 0.021412 | 0.020241 | -0.0026597 | 0.018812 | -0.0021341 | -0.045776 | 0.050354 | -0.045776 | -0.004578 | 0.16479 | 0.004578 | 0.045776 | 0.036621 | 0.059509 | -0.041199 | 0.050354 | 0.14648 | 0.059509 | 0.15564 | 121.8246 | -0.068665 | -0.1236 | 122.0352 | 121.9162 | 121.875 | 0.091552 | 0.050354 | 121.8292 | -0.05951 | -0.068665 | 122.0169 | 122.0261 | 121.9299 | 0.19684 | 0.10071 | 0.21057 | 0.041198 | 0.18768 | 0.091553 | 0.09613 | 0.10071 | 121.9208 | 121.9299 | -0.16479 | -0.16022 | 121.8658 | 121.9208 | 121.8246 | 121.907
1706.4219 | 122.2 | -121.8658 | 0.1236 | -0.0036622 | 0.065719 | 0.015894 | 0.022471 | 1.915e-05 | -0.0010468 | -0.0012241 | -0.0046081 | 0.022939 | 0.017994 | 0.024513 | 0.0016129 | 0.018812 | -0.0017069 | -0.009155 | 0.050354 | -0.054932 | 0.027466 | 0.17853 | 0.022888 | 0.050354 | 0.073242 | 0.054932 | -0.027466 | 0.11444 | 0.17853 | 0.086975 | 0.2243 | 121.8109 | -0.073242 | -0.09613 | 122.0444 | 121.9162 | 121.8887 | 0.10529 | 0.07782 | 121.8384 | -0.068664 | -0.009155 | 122.0444 | 122.0901 | 121.9528 | 0.25177 | 0.11444 | 0.23346 | 0.082398 | 0.20599 | 0.14191 | 0.10529 | 0.082398 | 121.9162 | 121.9208 | -0.17853 | -0.15106 | 121.8933 | 121.9803 | 121.8567 | 121.9391
1708.1094 | 122.0947 | -121.8842 | 0.13733 | -0.011291 | 0.067214 | 0.015039 | 0.023112 | 0.00066015 | -0.0012604 | 0.00048489 | 0.0014953 | 0.024007 | 0.019703 | 0.010628 | -0.0043687 | 0.017743 | 0.0027793 | -0.018311 | 0.07782 | -0.064087 | -0.041199 | 0.11902 | -0.022888 | 0.022888 | 0.022888 | 0.068665 | -0.045776 | 0.027466 | 0.10071 | 0.004578 | 0.13275 | 121.8201 | -0.059509 | -0.17853 | 122.0032 | 121.907 | 121.8613 | 0.086975 | 0.041199 | 121.8384 | -0.068664 | -0.10986 | 121.9849 | 122.0169 | 121.8887 | 0.17853 | 0.050354 | 0.18311 | 0.022888 | 0.14648 | 0.073242 | 0.14191 | 0.11444 | 121.962 | 121.9528 | -0.20142 | -0.18311 | 121.843 | 121.9116 | 121.8658 | 121.907
1709.8594 | 122.1771 | -121.8475 | 0.11902 | -0.0036622 | 0.066146 | 0.017389 | 0.020548 | -0.0016898 | -0.0036102 | -0.0010105 | 0.0045471 | 0.022512 | 0.019703 | 0.0149 | 0.0018265 | 0.020307 | -0.0066201 | -0.009155 | 0.054932 | -0.018311 | 0.022888 | 0.16022 | 0.036621 | 0.068665 | 0.09613 | 0.07782 | -0.027466 | 0.11444 | 0.1831 | 0.10071 | 0.20142 | 121.8292 | -0.064087 | -0.096131 | 122.0078 | 121.9162 | 121.8842 | 0.086976 | 0.054932 | 121.8201 | -0.041199 | -0.004578 | 122.0306 | 122.0489 | 121.9482 | 0.22888 | 0.12817 | 0.17853 | 0.041199 | 0.21057 | 0.14191 | 0.073243 | 0.10529 | 121.9025 | 121.9254 | -0.13733 | -0.14649 | 121.8704 | 121.962 | 121.8384 | 121.9437
1711.5469 | 122.0581 | -121.9025 | 0.14648 | -0.011291 | 0.065292 | 0.012903 | 0.02183 | -0.00019445 | -0.0040374 | 0.0015531 | -0.0015565 | 0.025075 | 0.021625 | 0.0059281 | -0.0073593 | 0.014753 | -0.00063873 | -0.11902 | 0.09613 | -0.07782 | -0.091553 | 0.045776 | -0.045776 | -0.004578 | -0.064087 | 0.10071 | -0.073242 | -0.036621 | 0.059509 | -0.022888 | 0.082397 | 121.8246 | -0.050354 | -0.23804 | 121.9482 | 121.8979 | 121.8567 | 0.073242 | 0.032044 | 121.8292 | -0.045776 | -0.18311 | 121.962 | 121.9849 | 121.8796 | 0.15564 | 0.050354 | 0.1236 | -0.013733 | 0.13275 | 0.036621 | 0.17395 | 0.17395 | 121.9986 | 122.0032 | -0.2243 | -0.21973 | 121.8109 | 121.8658 | 121.7834 | 121.8384
1713.2969 | 122.1268 | -121.7972 | 0.10986 | -0.0036622 | 0.066574 | 0.015253 | 0.023326 | -0.001476 | -0.00061944 | -0.0020785 | 0.0014953 | 0.023152 | 0.019275 | 0.018745 | 0.0020401 | 0.019025 | -0.00085233 | -0.009155 | 0.045776 | -0.068665 | 0.027466 | 0.16022 | 0.022888 | 0.064087 | 0.068665 | 0.045776 | -0.036621 | 0.11444 | 0.1831 | 0.091553 | 0.21515 | 121.7285 | -0.064087 | -0.082397 | 121.9574 | 121.8613 | 121.8201 | 0.13275 | 0.091553 | 121.7606 | -0.064087 | 0.004578 | 121.9803 | 122.0123 | 121.8887 | 0.25177 | 0.12817 | 0.22888 | 0.096131 | 0.21973 | 0.15106 | 0.11444 | 0.082397 | 121.843 | 121.843 | -0.17853 | -0.14648 | 121.8246 | 121.9116 | 121.788 | 121.8658
1715.0469 | 122.1268 | -121.7926 | 0.11902 | -0.0036622 | 0.062087 | 0.014612 | 0.023326 | -0.0012624 | -0.00596 | -0.0052829 | 0.0014953 | 0.022084 | 0.020343 | 0.013191 | -0.0011643 | 0.019239 | -0.0025613 | -0.068665 | 0.068665 | -0.050354 | -0.027466 | 0.12817 | 0.027466 | 0.050354 | 0.027466 | 0.064087 | -0.050354 | 0.064087 | 0.17395 | 0.09613 | 0.19226 | 121.7422 | -0.050354 | -0.14649 | 121.9208 | 121.843 | 121.8201 | 0.10071 | 0.07782 | 121.7422 | -0.054932 | -0.054932 | 121.9666 | 121.9849 | 121.8887 | 0.24261 | 0.14648 | 0.17853 | 0.022888 | 0.2243 | 0.11444 | 0.11902 | 0.11444 | 121.8613 | 121.8567 | -0.16937 | -0.16937 | 121.7651 | 121.8567 | 121.7239 | 121.8201
1716.7344 | 122.0718 | -121.8384 | 0.14191 | -0.02655 | 0.065933 | 0.014825 | 0.022257 | -0.00083525 | -0.0036102 | -0.0022921 | -0.0015565 | 0.02358 | 0.01778 | 0.018959 | -0.0037277 | 0.016248 | -0.0038431 | -0.013733 | 0.022888 | -0.041199 | 0.027466 | 0.16479 | 0.073242 | 0.064087 | 0.041199 | 0.07782 | -0.054932 | 0.041199 | 0.15106 | 0.07782 | 0.15106 | 121.7972 | -0.11902 | -0.11444 | 122.0032 | 121.9025 | 121.9116 | 0.10529 | 0.11444 | 121.7834 | -0.064087 | -0.10071 | 121.9894 | 121.9894 | 121.9162 | 0.20599 | 0.13275 | 0.20599 | 0.068665 | 0.20599 | 0.096131 | 0.064087 | 0.13275 | 121.8613 | 121.9162 | -0.18311 | -0.19684 | 121.8658 | 121.8796 | 121.8246 | 121.8796
1718.5 | 122.0947 | -121.8109 | 0.11444 | 0.0039673 | 0.06401 | 0.015253 | 0.020335 | -0.0040396 | -0.004892 | -0.0035739 | -0.0076599 | 0.022298 | 0.020343 | 0.02494 | -0.00052345 | 0.018598 | -0.00021153 | -0.068665 | 0.045776 | -0.064087 | -0.009155 | 0.15106 | 0.059509 | 0.068665 | 0.054932 | 0.064087 | -0.045776 | 0.091553 | 0.1831 | 0.11444 | 0.19684 | 121.7468 | -0.068665 | -0.1236 | 121.962 | 121.8796 | 121.8704 | 0.13275 | 0.1236 | 121.7651 | -0.050354 | -0.022888 | 121.994 | 122.0078 | 121.9254 | 0.24261 | 0.16022 | 0.21515 | 0.054932 | 0.22888 | 0.13733 | 0.10986 | 0.10986 | 121.8567 | 121.875 | -0.17853 | -0.16022 | 121.8018 | 121.9025 | 121.7422 | 121.8658
1720.2344 | 122.1085 | -121.788 | 0.12817 | -0.0036622 | 0.064865 | 0.01333 | 0.020976 | -0.0019034 | -0.0040374 | -0.0037875 | 0.0014953 | 0.023366 | 0.018421 | 0.019813 | -0.00095065 | 0.018598 | -0.00021153 | -0.027466 | 0.054932 | -0.004578 | 0.041199 | 0.20599 | 0.086975 | 0.10529 | 0.11902 | 0.045776 | -0.027466 | 0.091553 | 0.20142 | 0.1236 | 0.20142 | 121.7834 | -0.073242 | -0.086975 | 121.994 | 121.8933 | 121.875 | 0.10986 | 0.091553 | 121.7606 | -0.082398 | -0.036621 | 121.9894 | 121.9894 | 121.9116 | 0.22888 | 0.15106 | 0.21057 | 0.045777 | 0.22888 | 0.11902 | 0.05951 | 0.073242 | 121.843 | 121.8338 | -0.13275 | -0.15564 | 121.8292 | 121.8796 | 121.7606 | 121.907
1721.9219 | 122.0306 | -121.7972 | 0.13733 | -0.0036622 | 0.067214 | 0.015039 | 0.022257 | -0.001476 | -0.0023284 | -0.0022921 | 0.0045471 | 0.025716 | 0.016712 | 0.014259 | 0.00033115 | 0.019239 | -0.0042703 | -0.032043 | 0.07782 | -0.064087 | -0.041199 | 0.10986 | 0 | 0.013733 | 0 | 0.086975 | -0.059509 | 0.022888 | 0.11902 | 0.027466 | 0.13733 | 121.7331 | -0.059509 | -0.17853 | 121.907 | 121.8109 | 121.7972 | 0.07782 | 0.064087 | 121.7377 | -0.050354 | -0.11444 | 121.9162 | 121.9345 | 121.8246 | 0.19684 | 0.086975 | 0.17395 | 0.022888 | 0.17853 | 0.082397 | 0.14191 | 0.14648 | 121.875 | 121.8842 | -0.20142 | -0.19684 | 121.756 | 121.8201 | 121.7651 | 121.7972
1723.6719 | 121.9345 | -121.8109 | 0.16479 | -0.011291 | 0.068923 | 0.017603 | 0.026316 | 0.0034372 | -0.0027556 | 0.0015531 | -0.0015565 | 0.026784 | 0.018207 | 0.014473 | -0.0013779 | 0.016248 | -0.0038431 | -0.082397 | 0.082397 | -0.073242 | -0.091553 | 0.041199 | -0.091553 | -0.050354 | -0.086975 | 0.10529 | -0.064087 | -0.032043 | 0.041199 | -0.073242 | 0.091553 | 121.7377 | -0.082398 | -0.25635 | 121.8521 | 121.7606 | 121.7194 | 0.022888 | -0.018311 | 121.7468 | -0.059509 | -0.19684 | 121.8521 | 121.9025 | 121.7377 | 0.15564 | -0.009155 | 0.11444 | -0.018311 | 0.10529 | 0.032044 | 0.15564 | 0.16937 | 121.8933 | 121.9162 | -0.23804 | -0.22888 | 121.7194 | 121.7789 | 121.7285 | 121.7239
1725.4219 | 122.0718 | -121.6461 | 0.2243 | -0.011291 | 0.063583 | 0.015894 | 0.02183 | -0.002117 | -0.0038238 | 5.7688e-05 | -0.0076599 | 0.023793 | 0.018207 | 0.018532 | -0.0026597 | 0.017103 | -0.00085233 | -0.018311 | 0.050354 | -0.050354 | 0.036621 | 0.21057 | 0.064087 | 0.086975 | 0.082397 | 0.059509 | -0.032043 | 0.09613 | 0.19684 | 0.13275 | 0.19684 | 121.5958 | -0.17395 | -0.18768 | 121.8567 | 121.7331 | 121.7102 | 0.13733 | 0.11444 | 121.6141 | -0.16479 | -0.12817 | 121.843 | 121.843 | 121.7789 | 0.22888 | 0.16479 | 0.26093 | 0.086975 | 0.22888 | 0.12817 | 0.10071 | 0.091552 | 121.6965 | 121.7056 | -0.27466 | -0.25635 | 121.6827 | 121.7422 | 121.6278 | 121.7285
1727.0938 | 121.9711 | -121.8475 | 0.14191 | -0.011291 | 0.066146 | 0.015039 | 0.024394 | -0.0023306 | -0.0036102 | -0.0016513 | 0.0014953 | 0.02123 | 0.019916 | 0.017036 | -0.0037277 | 0.016248 | -0.0027749 | -0.1236 | 0.10071 | -0.082397 | -0.10071 | 0.041199 | -0.064087 | -0.022888 | -0.068665 | 0.11902 | -0.073242 | -0.041199 | 0.054932 | -0.027466 | 0.073242 | 121.7651 | -0.041199 | -0.24262 | 121.8887 | 121.8246 | 121.7834 | 0.059509 | 0.01831 | 121.7743 | -0.022888 | -0.18311 | 121.9025 | 121.9208 | 121.8201 | 0.14648 | 0.045776 | 0.1236 | -0.018311 | 0.12817 | 0.032043 | 0.18311 | 0.19226 | 121.9482 | 121.9666 | -0.2243 | -0.21515 | 121.7468 | 121.8063 | 121.7239 | 121.7789
1728.8438 | 121.9757 | -121.8567 | 0.15564 | -0.0036622 | 0.065292 | 0.012476 | 0.022471 | 0.0015146 | -0.0023284 | -0.00058311 | -0.0015565 | 0.024861 | 0.019489 | 0.017036 | -0.0024461 | 0.01753 | -0.0014931 | -0.064087 | 0.059509 | -0.059509 | -0.064087 | 0.086975 | -0.022888 | 0.004578 | -0.045776 | 0.10071 | -0.064087 | -0.027466 | 0.073242 | -0.004578 | 0.09613 | 121.7972 | -0.096131 | -0.21973 | 121.9437 | 121.8613 | 121.8338 | 0.064087 | 0.036621 | 121.7926 | -0.054932 | -0.18311 | 121.9299 | 121.9528 | 121.8521 | 0.16022 | 0.059509 | 0.14648 | -0.004578 | 0.13733 | 0.036621 | 0.11902 | 0.1648 | 121.9162 | 121.9574 | -0.21515 | -0.21973 | 121.7926 | 121.8292 | 121.7926 | 121.8109
1730.5938 | 122.0581 | -121.7972 | 0.12817 | 0.0039673 | 0.064865 | 0.014398 | 0.020976 | -0.0033986 | -0.0038238 | -0.0014377 | -0.0015565 | 0.023152 | 0.02013 | 0.0196 | 0.00054475 | 0.019452 | 2.068e-06 | -0.07782 | 0.059509 | -0.064087 | -0.054932 | 0.10071 | -0.013733 | 0.027466 | -0.018311 | 0.073242 | -0.059509 | 0.059509 | 0.13275 | 0.054932 | 0.16022 | 121.7331 | -0.068665 | -0.18311 | 121.8979 | 121.8246 | 121.7834 | 0.091553 | 0.050354 | 121.7377 | -0.054932 | -0.068665 | 121.9299 | 121.9574 | 121.8521 | 0.21973 | 0.11444 | 0.1648 | 0.009155 | 0.19226 | 0.11902 | 0.1236 | 0.13275 | 121.8567 | 121.8704 | -0.19226 | -0.18768 | 121.7422 | 121.8567 | 121.7194 | 121.7789
1732.2812 | 121.962 | -121.8246 | 0.16022 | -0.018921 | 0.067001 | 0.015039 | 0.020548 | -0.00019445 | -0.0033966 | -0.0014377 | -0.0046081 | 0.023793 | 0.018207 | 0.014686 | -0.0045823 | 0.017743 | -0.0038431 | -0.091553 | 0.07782 | -0.054932 | -0.091553 | 0.050354 | -0.036621 | -0.027466 | -0.068665 | 0.09613 | -0.059509 | -0.045776 | 0.050354 | -0.022888 | 0.073242 | 121.7697 | -0.082397 | -0.25177 | 121.875 | 121.7972 | 121.788 | 0.027466 | 0.018311 | 121.7651 | -0.064087 | -0.20599 | 121.875 | 121.8979 | 121.8018 | 0.13275 | 0.036621 | 0.10529 | -0.036621 | 0.10986 | 0.013733 | 0.13275 | 0.15564 | 121.9025 | 121.9208 | -0.21515 | -0.21973 | 121.7331 | 121.7789 | 121.7331 | 121.756
1734.0312 | 121.9986 | -121.7834 | 0.18768 | -0.0036622 | 0.063796 | 0.015253 | 0.022471 | -0.00040805 | -0.002542 | -0.0014377 | -0.0046081 | 0.025289 | 0.021198 | 0.014259 | 0.00054475 | 0.018171 | -0.0057657 | -0.09613 | 0.09613 | -0.07782 | -0.09613 | 0.054932 | -0.045776 | -0.027466 | -0.073242 | 0.10529 | -0.082397 | -0.027466 | 0.059509 | -0.018311 | 0.10986 | 121.7056 | -0.091553 | -0.28381 | 121.8384 | 121.756 | 121.7377 | 0.050354 | 0.032044 | 121.701 | -0.082397 | -0.21515 | 121.843 | 121.8933 | 121.7651 | 0.19226 | 0.064086 | 0.13275 | -0.01831 | 0.14191 | 0.054931 | 0.17395 | 0.18768 | 121.8796 | 121.8887 | -0.2655 | -0.27008 | 121.6873 | 121.756 | 121.6873 | 121.7102
1735.7812 | 122.0581 | -121.7972 | 0.10529 | -0.0036622 | 0.063156 | 0.016534 | 0.021617 | 0.0010874 | -0.001474 | 0.0015531 | 0.0014953 | 0.021871 | 0.02013 | 0.019813 | 0.00033115 | 0.018812 | -0.0038431 | -0.064087 | 0.050354 | -0.050354 | -0.036621 | 0.11444 | 0 | 0.027466 | -0.004578 | 0.050354 | -0.050354 | 0.045776 | 0.11902 | 0.064087 | 0.15106 | 121.7468 | -0.054932 | -0.14191 | 121.9116 | 121.8246 | 121.7972 | 0.07782 | 0.050354 | 121.7468 | -0.054932 | -0.05951 | 121.9162 | 121.9482 | 121.8613 | 0.20142 | 0.11444 | 0.16479 | 0.013733 | 0.16937 | 0.09613 | 0.10071 | 0.10071 | 121.8475 | 121.8475 | -0.15564 | -0.15564 | 121.7606 | 121.843 | 121.7331 | 121.7926
1737.4531 | 121.9437 | -121.8292 | 0.16937 | 0.011597 | 0.065505 | 0.012476 | 0.024821 | -0.0023306 | -0.0055328 | -0.0029331 | -0.0076599 | 0.024434 | 0.01778 | 0.01255 | -0.0024461 | 0.017957 | -0.0010659 | -0.11444 | 0.09613 | -0.09613 | -0.10071 | 0.045776 | -0.054932 | -0.036621 | -0.073242 | 0.086975 | -0.068665 | -0.036621 | 0.059509 | -0.018311 | 0.10071 | 121.7331 | -0.073243 | -0.27008 | 121.875 | 121.7926 | 121.7743 | 0.059509 | 0.041198 | 121.7606 | -0.082398 | -0.20599 | 121.8887 | 121.9299 | 121.8109 | 0.16937 | 0.050354 | 0.14191 | -0.004578 | 0.12817 | 0.032044 | 0.19226 | 0.15564 | 121.9254 | 121.9162 | -0.2655 | -0.23804 | 121.7285 | 121.7926 | 121.7148 | 121.756
1739.2031 | 122.0947 | -121.7606 | 0.11902 | -0.011291 | 0.064865 | 0.015253 | 0.022044 | 1.915e-05 | -0.003183 | -0.0040011 | 0.0014953 | 0.023152 | 0.017994 | 0.014259 | 0.0022537 | 0.020521 | -0.0012795 | -0.045776 | 0.07782 | -0.045776 | 0.009155 | 0.12817 | 0.018311 | 0.045776 | 0.07782 | 0.064087 | -0.050354 | 0.10529 | 0.16479 | 0.07782 | 0.20142 | 121.7148 | -0.041199 | -0.10986 | 121.8887 | 121.8063 | 121.7789 | 0.091552 | 0.064087 | 121.7102 | -0.054932 | -0.013733 | 121.9254 | 121.962 | 121.8384 | 0.25177 | 0.12817 | 0.17395 | 0.054931 | 0.21515 | 0.15564 | 0.1236 | 0.11444 | 121.8384 | 121.8246 | -0.16479 | -0.16937 | 121.7697 | 121.8658 | 121.7148 | 121.8384
1740.8906 | 121.9757 | -121.8292 | 0.13275 | -0.0036622 | 0.066146 | 0.016107 | 0.02418 | -0.0016898 | -0.0055328 | -0.0012241 | -0.0046081 | 0.024221 | 0.022266 | 0.019386 | -0.00052345 | 0.020093 | -0.0012795 | -0.10071 | 0.10071 | -0.068665 | -0.09613 | 0.004578 | -0.10071 | -0.059509 | -0.091553 | 0.09613 | -0.073242 | -0.022888 | 0.027466 | -0.059509 | 0.10071 | 121.7606 | -0.032043 | -0.22888 | 121.8338 | 121.7697 | 121.7285 | 0.009156 | -0.032043 | 121.756 | -0.036621 | -0.15564 | 121.8567 | 121.9299 | 121.7697 | 0.17395 | 0.013733 | 0.073243 | -0.027465 | 0.10071 | 0.050354 | 0.16937 | 0.16937 | 121.9299 | 121.9254 | -0.20142 | -0.20599 | 121.7331 | 121.8063 | 121.7285 | 121.7377
1742.6406 | 121.9803 | -121.7743 | 0.12817 | -0.0036622 | 0.066146 | 0.016748 | 0.022685 | -0.00019445 | -0.00019224 | -0.0025057 | -0.0015565 | 0.023366 | 0.019489 | 0.014686 | 0.0013991 | 0.020093 | -0.0042703 | -0.027466 | 0.050354 | -0.018311 | 0.009155 | 0.1831 | 0.027466 | 0.050354 | 0.073242 | 0.07782 | -0.032043 | 0.086975 | 0.14648 | 0.086975 | 0.17853 | 121.756 | -0.07782 | -0.11902 | 121.9574 | 121.8246 | 121.8018 | 0.068665 | 0.045777 | 121.7422 | -0.050354 | -0.041199 | 121.9208 | 121.9528 | 121.8613 | 0.21057 | 0.11902 | 0.20142 | 0.027466 | 0.17853 | 0.11902 | 0.068665 | 0.10986 | 121.8246 | 121.8521 | -0.14649 | -0.16022 | 121.7834 | 121.8613 | 121.7468 | 121.8475
1744.3906 | 122.0901 | -121.7834 | 0.10071 | -0.018921 | 0.064651 | 0.014825 | 0.021189 | -0.002117 | -0.0040374 | -0.0027195 | -0.0046081 | 0.020803 | 0.01778 | 0.018959 | -0.0030869 | 0.020734 | -0.0044839 | -0.022888 | 0.036621 | -0.045776 | 0.041199 | 0.23804 | 0.10529 | 0.09613 | 0.09613 | 0.064087 | -0.045776 | 0.091553 | 0.21973 | 0.1236 | 0.18768 | 121.7377 | -0.064087 | -0.059509 | 122.0215 | 121.8796 | 121.8887 | 0.14191 | 0.15106 | 121.7377 | -0.036621 | -0.009155 | 122.0032 | 121.9711 | 121.907 | 0.23346 | 0.16937 | 0.28381 | 0.086975 | 0.2655 | 0.13733 | 0.082397 | 0.10986 | 121.8201 | 121.8475 | -0.14648 | -0.14648 | 121.8246 | 121.875 | 121.7606 | 121.8796
1746.1406 | 121.9803 | -121.788 | 0.14648 | -0.0036622 | 0.063156 | 0.013544 | 0.022044 | -0.00083525 | -0.0021148 | 5.7688e-05 | 0.0014953 | 0.025289 | 0.018634 | 0.0093461 | -0.0026597 | 0.018171 | 0.0019247 | -0.09613 | 0.091553 | -0.07782 | -0.10529 | 0.041199 | -0.054932 | -0.036621 | -0.073242 | 0.086975 | -0.068665 | -0.032043 | 0.073242 | -0.027466 | 0.10071 | 121.7102 | -0.054931 | -0.25177 | 121.8292 | 121.7514 | 121.7331 | 0.041199 | 0.022888 | 121.7194 | -0.059509 | -0.17853 | 121.8613 | 121.8887 | 121.7606 | 0.16937 | 0.041199 | 0.11902 | -0.027466 | 0.14191 | 0.036622 | 0.16937 | 0.15564 | 121.8796 | 121.875 | -0.2243 | -0.21515 | 121.6827 | 121.756 | 121.6919 | 121.7148
1747.875 | 121.962 | -121.8018 | 0.14648 | -0.018921 | 0.066787 | 0.016321 | 0.021617 | -0.0010488 | -0.0019012 | -0.0044285 | -0.0015565 | 0.024648 | 0.019703 | 0.0149 | 0.00054475 | 0.020521 | 0.00064307 | -0.09613 | 0.091553 | -0.073242 | -0.091553 | 0.013733 | -0.10986 | -0.068665 | -0.09613 | 0.086975 | -0.082397 | -0.022888 | 0.036621 | -0.064087 | 0.09613 | 121.7285 | -0.054931 | -0.23804 | 121.8155 | 121.7331 | 121.6919 | 0.004577 | -0.036621 | 121.7194 | -0.059509 | -0.16937 | 121.8384 | 121.8979 | 121.7377 | 0.17853 | 0.01831 | 0.086975 | -0.018311 | 0.11902 | 0.059509 | 0.16479 | 0.16937 | 121.8933 | 121.8887 | -0.21973 | -0.22888 | 121.7102 | 121.7789 | 121.7056 | 121.7056
1749.5469 | 122.0627 | -121.5363 | 0.32501 | -0.011291 | 0.065505 | 0.015894 | 0.01948 | -0.00083525 | -0.0040374 | -0.0029331 | 0.0014953 | 0.022512 | 0.016285 | 0.016395 | -0.0015915 | 0.018598 | 0.0019247 | -0.013733 | 0.059509 | -0.050354 | 0.036621 | 0.1831 | 0.064087 | 0.073242 | 0.068665 | 0.068665 | -0.027466 | 0.086975 | 0.19226 | 0.10529 | 0.19226 | 121.4859 | -0.2655 | -0.28839 | 121.7194 | 121.6095 | 121.6003 | 0.1236 | 0.11444 | 121.5088 | -0.25635 | -0.23804 | 121.7285 | 121.7285 | 121.6415 | 0.21973 | 0.13275 | 0.23346 | 0.086975 | 0.21973 | 0.11444 | 0.10986 | 0.096131 | 121.5958 | 121.6049 | -0.37537 | -0.35248 | 121.5729 | 121.6232 | 121.5225 | 121.6049
1751.2344 | 122.0169 | -121.7789 | 0.14191 | -0.0036622 | 0.067428 | 0.014398 | 0.022257 | -0.0019034 | -0.001474 | -0.00058311 | -0.0015565 | 0.024861 | 0.018848 | 0.015114 | 0.00033115 | 0.017957 | -0.0040567 | -0.045776 | 0.086975 | -0.068665 | -0.022888 | 0.09613 | -0.022888 | 0 | 0.018311 | 0.09613 | -0.068665 | 0.032043 | 0.10986 | 0.041199 | 0.14648 | 121.7102 | -0.054932 | -0.16479 | 121.875 | 121.7789 | 121.756 | 0.068665 | 0.045777 | 121.7102 | -0.045777 | -0.10986 | 121.8887 | 121.9254 | 121.8201 | 0.21515 | 0.10986 | 0.16479 | 0.045777 | 0.17853 | 0.10071 | 0.15564 | 0.16479 | 121.8658 | 121.875 | -0.21057 | -0.21057 | 121.756 | 121.8109 | 121.7331 | 121.7972
1752.9844 | 122.0169 | -121.7651 | 0.13275 | -0.0036622 | 0.06636 | 0.01568 | 0.023326 | -0.00040805 | -0.0029694 | -0.0016513 | -0.0076599 | 0.023793 | 0.018634 | 0.018745 | -0.00095065 | 0.018812 | 2.068e-06 | -0.045776 | 0.091553 | -0.082397 | -0.027466 | 0.11444 | -0.009155 | 0.004578 | -0.004578 | 0.10071 | -0.073242 | 0.036621 | 0.10986 | 0.032043 | 0.13275 | 121.6827 | -0.041198 | -0.16022 | 121.8796 | 121.7697 | 121.756 | 0.086975 | 0.073242 | 121.6919 | -0.032043 | -0.09613 | 121.875 | 121.8979 | 121.7972 | 0.20599 | 0.10529 | 0.19684 | 0.054931 | 0.18311 | 0.10986 | 0.17395 | 0.17395 | 121.8567 | 121.8658 | -0.21515 | -0.20599 | 121.7377 | 121.8018 | 121.7194 | 121.7606
1754.6719 | 122.0764 | -121.7697 | 0.13275 | 0.0039673 | 0.064865 | 0.01568 | 0.02183 | 0.0027964 | -0.0040374 | -0.0020785 | -0.0076599 | 0.022084 | 0.021198 | 0.020668 | 0.0024673 | 0.020307 | -0.0014931 | -0.022888 | 0.032043 | -0.032043 | 0.027466 | 0.20142 | 0.032043 | 0.054932 | 0.086975 | 0.045776 | -0.032043 | 0.086975 | 0.17395 | 0.091553 | 0.19684 | 121.7377 | -0.10071 | -0.10529 | 121.9711 | 121.8246 | 121.8018 | 0.086975 | 0.064086 | 121.7377 | -0.086975 | -0.045776 | 121.9437 | 121.9666 | 121.8613 | 0.22888 | 0.1236 | 0.23346 | 0.059509 | 0.20599 | 0.11902 | 0.064086 | 0.077819 | 121.8018 | 121.8155 | -0.16479 | -0.16479 | 121.7972 | 121.8567 | 121.7468 | 121.8567
1756.4219 | 122.049 | -121.7606 | 0.10529 | -0.0036622 | 0.063583 | 0.014612 | 0.020976 | 0.0034372 | -0.0027556 | -0.0040011 | 0.0045471 | 0.022725 | 0.02013 | 0.016182 | -0.00052345 | 0.019239 | 0.00021567 | -0.050354 | 0.036621 | -0.036621 | -0.004578 | 0.15106 | 0.013733 | 0.041199 | 0.054932 | 0.045776 | -0.045776 | 0.050354 | 0.11444 | 0.059509 | 0.15564 | 121.7239 | -0.068665 | -0.10986 | 121.9116 | 121.8018 | 121.7743 | 0.07782 | 0.050354 | 121.7148 | -0.05951 | -0.054932 | 121.875 | 121.9162 | 121.8201 | 0.20142 | 0.10528 | 0.18768 | 0.032043 | 0.16022 | 0.09613 | 0.073242 | 0.091552 | 121.7972 | 121.8063 | -0.14191 | -0.15106 | 121.756 | 121.8109 | 121.7102 | 121.8155
1758.1719 | 121.994 | -121.8063 | 0.14191 | 0.0039673 | 0.065719 | 0.014398 | 0.022685 | -0.0010488 | -0.0023284 | 0.00027129 | -0.0076599 | 0.024648 | 0.019489 | 0.010628 | -0.0039413 | 0.017103 | 0.00042947 | -0.09613 | 0.09613 | -0.091553 | -0.09613 | 0.032043 | -0.064087 | -0.022888 | -0.068665 | 0.09613 | -0.086975 | -0.027466 | 0.064087 | -0.018311 | 0.10986 | 121.7148 | -0.045777 | -0.23804 | 121.8384 | 121.7834 | 121.7422 | 0.068665 | 0.027466 | 121.7194 | -0.045777 | -0.16937 | 121.8704 | 121.9162 | 121.788 | 0.19684 | 0.068664 | 0.1236 | -0.004577 | 0.15106 | 0.059509 | 0.18768 | 0.1831 | 121.9025 | 121.9025 | -0.23346 | -0.22888 | 121.7102 | 121.7789 | 121.7102 | 121.7377
1759.8438 | 122.0764 | -121.7651 | 0.11444 | -0.011291 | 0.064865 | 0.01568 | 0.021403 | -0.00083525 | -0.001474 | 0.00069849 | 0.0014953 | 0.022939 | 0.019275 | 0.011696 | 0.00011755 | 0.019666 | 0.0019247 | -0.018311 | 0.036621 | -0.018311 | 0.027466 | 0.19226 | 0.036621 | 0.064087 | 0.091553 | 0.064087 | -0.032043 | 0.091553 | 0.16937 | 0.086975 | 0.20599 | 121.7468 | -0.07782 | -0.086975 | 121.9574 | 121.8292 | 121.8018 | 0.082398 | 0.054932 | 121.7331 | -0.050354 | -0.022888 | 121.9345 | 121.9711 | 121.8521 | 0.23804 | 0.11902 | 0.21057 | 0.045777 | 0.20142 | 0.1236 | 0.054932 | 0.09613 | 121.8018 | 121.8292 | -0.13275 | -0.14648 | 121.7926 | 121.8567 | 121.7468 | 121.8567
1761.5938 | 122.1039 | -121.8704 | 0.10529 | -0.018921 | 0.063796 | 0.014398 | 0.020976 | -0.005535 | -0.00083304 | -0.0018649 | 0.0014953 | 0.022725 | 0.021412 | 0.01255 | -0.0033005 | 0.015821 | -0.0017069 | -0.027466 | 0.036621 | -0.036621 | 0.036621 | 0.17853 | 0.054932 | 0.082397 | 0.054932 | 0.041199 | -0.036621 | 0.041199 | 0.16022 | 0.082397 | 0.16937 | 121.8338 | -0.068665 | -0.068665 | 122.049 | 121.9528 | 121.9254 | 0.11902 | 0.091553 | 121.8338 | -0.064087 | -0.064087 | 122.0306 | 122.0398 | 121.9528 | 0.20599 | 0.11902 | 0.21515 | 0.073242 | 0.19684 | 0.07782 | 0.073242 | 0.07782 | 121.907 | 121.9116 | -0.14191 | -0.14191 | 121.907 | 121.9116 | 121.843 | 121.9254
1763.3438 | 122.081 | -121.8979 | 0.10071 | -0.0036622 | 0.066146 | 0.015894 | 0.025462 | 0.0025828 | -0.0023284 | -0.00036951 | -0.0046081 | 0.024861 | 0.02013 | 0.020668 | 0.0016129 | 0.017743 | -0.0014931 | -0.091553 | 0.091553 | -0.07782 | -0.09613 | 0.045776 | -0.086975 | -0.041199 | -0.045776 | 0.082397 | -0.073242 | 0.013733 | 0.082397 | -0.009155 | 0.12817 | 121.8201 | -0.009155 | -0.19684 | 121.9437 | 121.8567 | 121.8109 | 0.036621 | -0.009155 | 121.8246 | -0.018311 | -0.086975 | 121.9803 | 122.0261 | 121.8887 | 0.20142 | 0.064087 | 0.1236 | -0.01831 | 0.15564 | 0.086975 | 0.16937 | 0.15564 | 121.9894 | 121.9803 | -0.17853 | -0.17395 | 121.8018 | 121.9116 | 121.8063 | 121.8521
1765.0312 | 122.0581 | -121.8887 | 0.1236 | -0.011291 | 0.066787 | 0.018243 | 0.022685 | 0.0015146 | -0.0046782 | -0.00015591 | -0.0046081 | 0.025075 | 0.019275 | 0.011482 | 0.00011755 | 0.019025 | -0.0029885 | -0.054932 | 0.073242 | -0.07782 | -0.027466 | 0.091553 | -0.027466 | -0.018311 | -0.018311 | 0.082397 | -0.059509 | -0.004578 | 0.07782 | -0.032043 | 0.11444 | 121.8109 | -0.050354 | -0.15106 | 121.9803 | 121.8704 | 121.8613 | 0.059509 | 0.050354 | 121.8292 | -0.041199 | -0.12817 | 121.9666 | 122.0032 | 121.8567 | 0.17395 | 0.027466 | 0.16937 | 0.050354 | 0.13733 | 0.054931 | 0.15106 | 0.14191 | 121.962 | 121.9711 | -0.20142 | -0.1831 | 121.8613 | 121.8842 | 121.8338 | 121.8704
1766.7812 | 122.1634 | -121.8704 | 0.10071 | -0.0036622 | 0.068496 | 0.01803 | 0.022898 | -0.00040805 | -0.0010468 | 0.0015531 | 0.0014953 | 0.023366 | 0.02013 | 0.013405 | 0.00011755 | 0.019239 | -0.00063873 | -0.022888 | 0.036621 | -0.041199 | 0.022888 | 0.17853 | 0.041199 | 0.064087 | 0.091553 | 0.059509 | -0.032043 | 0.086975 | 0.16937 | 0.073242 | 0.19226 | 121.8292 | -0.064087 | -0.07782 | 122.049 | 121.9345 | 121.9116 | 0.10529 | 0.082398 | 121.8384 | -0.041199 | -0.013733 | 122.0398 | 122.0627 | 121.9437 | 0.2243 | 0.10529 | 0.21973 | 0.064087 | 0.20142 | 0.11902 | 0.07782 | 0.091552 | 121.907 | 121.9299 | -0.14191 | -0.13275 | 121.8933 | 121.9574 | 121.8475 | 121.962
1768.5156 | 122.0901 | -121.9299 | 0.13733 | 0.0039673 | 0.06636 | 0.014398 | 0.02183 | 0.0017282 | -0.0023284 | -0.00015591 | -0.0015565 | 0.024648 | 0.019275 | 0.0093461 | -0.0028733 | 0.017743 | -0.0012795 | -0.09613 | 0.091553 | -0.1236 | -0.10529 | 0.027466 | -0.054932 | -0.032043 | -0.073242 | 0.091553 | -0.073242 | -0.032043 | 0.054932 | -0.009155 | 0.10071 | 121.8063 | -0.045776 | -0.24262 | 121.9574 | 121.8979 | 121.875 | 0.091553 | 0.068664 | 121.8567 | -0.045776 | -0.16937 | 121.9849 | 122.0306 | 121.9208 | 0.17395 | 0.064087 | 0.15106 | 0.01831 | 0.12817 | 0.041199 | 0.21515 | 0.16479 | 122.0215 | 122.0215 | -0.26093 | -0.21057 | 121.8246 | 121.8979 | 121.8338 | 121.8567
1770.1875 | 122.1268 | -121.8979 | 0.10071 | 0.0039673 | 0.067001 | 0.016534 | 0.022257 | -0.001476 | -0.001474 | -0.0025057 | 0.0014953 | 0.023366 | 0.019062 | 0.019813 | -0.00095065 | 0.016248 | -0.0042703 | -0.050354 | 0.082397 | -0.07782 | -0.032043 | 0.10986 | -0.004578 | 0 | 0.013733 | 0.068665 | -0.073242 | 0.032043 | 0.10071 | 0.013733 | 0.14648 | 121.8201 | -0.018311 | -0.13275 | 122.0078 | 121.8979 | 121.8933 | 0.07782 | 0.073242 | 121.8246 | -0.032043 | -0.068665 | 121.9986 | 122.0444 | 121.9116 | 0.21973 | 0.086975 | 0.18768 | 0.045777 | 0.17395 | 0.10529 | 0.16022 | 0.14191 | 121.9803 | 121.9666 | -0.17853 | -0.17395 | 121.8658 | 121.9299 | 121.8475 | 121.9116
1771.9219 | 122.1222 | -121.9254 | 0.10529 | -0.0036622 | 0.067642 | 0.015466 | 0.021403 | 1.915e-05 | -0.0019012 | 0.0024075 | -0.0046081 | 0.02358 | 0.020984 | 0.0091325 | -0.0011643 | 0.01753 | -0.00042513 | -0.054932 | 0.068665 | -0.07782 | -0.050354 | 0.10071 | -0.018311 | 0 | -0.013733 | 0.09613 | -0.054932 | 0.018311 | 0.082397 | -0.009155 | 0.1236 | 121.8475 | -0.036621 | -0.15564 | 122.0261 | 121.9254 | 121.907 | 0.07782 | 0.059509 | 121.8704 | -0.009156 | -0.086975 | 122.0078 | 122.049 | 121.9162 | 0.17853 | 0.045777 | 0.17853 | 0.027466 | 0.13733 | 0.073243 | 0.14649 | 0.15106 | 121.994 | 122.0215 | -0.18311 | -0.16022 | 121.875 | 121.9437 | 121.8704 | 121.9116
1773.6094 | 122.0993 | -121.9391 | 0.11444 | -0.018921 | 0.065933 | 0.016748 | 0.022257 | 0.0045054 | -0.0019012 | -0.0016513 | -0.0015565 | 0.023793 | 0.018421 | 0.01255 | -0.00030965 | 0.017957 | -0.0061929 | -0.091553 | 0.082397 | -0.073242 | -0.1236 | 0.009155 | -0.10071 | -0.073242 | -0.086975 | 0.091553 | -0.086975 | -0.018311 | 0.022888 | -0.045776 | 0.09613 | 121.8658 | -0.032044 | -0.23804 | 121.9482 | 121.8658 | 121.8384 | 0 | -0.027466 | 121.8521 | -0.022888 | -0.13275 | 121.962 | 122.0352 | 121.8933 | 0.1831 | 0.041199 | 0.082397 | -0.050354 | 0.10986 | 0.068664 | 0.15564 | 0.17853 | 122.0215 | 122.0306 | -0.18768 | -0.20142 | 121.8155 | 121.9208 | 121.8475 | 121.8521
1775.3438 | 122.1725 | -121.9162 | 0.10071 | -0.018921 | 0.067428 | 0.017389 | 0.023539 | -0.0027578 | -0.002542 | -0.0033603 | -0.0046081 | 0.021871 | 0.020557 | 0.016609 | 0.00033115 | 0.020093 | 0.0010703 | -0.050354 | 0.068665 | -0.064087 | -0.022888 | 0.14648 | -0.009155 | 0.041199 | 0.022888 | 0.041199 | -0.064087 | 0.045776 | 0.12817 | 0.059509 | 0.16479 | 121.8521 | -0.032043 | -0.1236 | 122.0627 | 121.9574 | 121.907 | 0.10529 | 0.054932 | 121.8521 | -0.059509 | -0.054932 | 122.0444 | 122.081 | 121.9757 | 0.22888 | 0.1236 | 0.21057 | 0.041199 | 0.19226 | 0.10986 | 0.13275 | 0.10529 | 121.9849 | 121.9574 | -0.1648 | -0.1648 | 121.8933 | 121.962 | 121.8658 | 121.9391
1777.0781 | 122.1863 | -121.9162 | 0.086975 | -0.011291 | 0.063583 | 0.016962 | 0.022044 | 0.0010874 | 0.00087596 | -0.0057101 | -0.0015565 | 0.02358 | 0.022052 | 0.018104 | 0.00033115 | 0.021161 | -0.0014931 | -0.032043 | 0.045776 | -0.036621 | 0 | 0.17395 | 0.013733 | 0.054932 | 0.059509 | 0.059509 | -0.050354 | 0.073242 | 0.15106 | 0.064087 | 0.17853 | 121.8796 | -0.041199 | -0.086975 | 122.0901 | 121.9711 | 121.9299 | 0.091553 | 0.050354 | 121.8658 | -0.027466 | -0.013733 | 122.0673 | 122.0947 | 121.9803 | 0.22888 | 0.11444 | 0.21057 | 0.036621 | 0.20142 | 0.1236 | 0.082397 | 0.10986 | 121.962 | 121.9757 | -0.1236 | -0.13733 | 121.9162 | 121.9894 | 121.8842 | 121.9757
1778.7656 | 122.1634 | -121.9437 | 0.11444 | -0.0036622 | 0.065505 | 0.015466 | 0.019908 | -0.0016898 | -0.00083304 | -0.0018649 | 0.0014953 | 0.024648 | 0.02013 | 0.01725 | -0.0030869 | 0.019666 | -0.0034159 | -0.073242 | 0.091553 | -0.09613 | -0.091553 | 0.045776 | -0.036621 | -0.022888 | -0.050354 | 0.10071 | -0.068665 | -0.013733 | 0.082397 | 0.004578 | 0.13275 | 121.8475 | -0.022888 | -0.20599 | 121.9894 | 121.9208 | 121.907 | 0.073242 | 0.059509 | 121.875 | -0.013733 | -0.12817 | 122.0261 | 122.0764 | 121.9482 | 0.20142 | 0.073243 | 0.14191 | 0.004577 | 0.15106 | 0.054932 | 0.18768 | 0.16937 | 122.0352 | 122.0444 | -0.21057 | -0.18311 | 121.8521 | 121.9299 | 121.8704 | 121.8933
1780.5156 | 122.2366 | -121.9025 | 0.10071 | -0.0036622 | 0.062942 | 0.013971 | 0.020762 | -0.0012624 | -0.0027556 | -0.0010105 | -0.0015565 | 0.019948 | 0.020771 | 0.014259 | -0.0039413 | 0.018598 | -0.0012795 | -0.036621 | 0.068665 | -0.036621 | 0.032043 | 0.21515 | 0.091553 | 0.086975 | 0.082397 | 0.059509 | -0.041199 | 0.091553 | 0.21057 | 0.11444 | 0.19684 | 121.8658 | -0.032043 | -0.068665 | 122.1176 | 121.9894 | 121.994 | 0.1236 | 0.12817 | 121.8613 | -0.041199 | -0.009155 | 122.113 | 122.0993 | 122.0169 | 0.23804 | 0.15564 | 0.25177 | 0.068664 | 0.25177 | 0.13275 | 0.10529 | 0.10071 | 121.9711 | 121.962 | -0.13733 | -0.14191 | 121.9345 | 121.994 | 121.8658 | 121.9849
1782.25 | 122.287 | -121.9345 | 0.07782 | -0.011291 | 0.063156 | 0.015466 | 0.019694 | -0.003185 | -0.002542 | -0.0027195 | -0.0046081 | 0.02358 | 0.018207 | 0.022377 | -0.0033005 | 0.018171 | -0.0021341 | -0.018311 | 0.045776 | -0.054932 | 0.041199 | 0.20599 | 0.07782 | 0.091553 | 0.11902 | 0.050354 | -0.041199 | 0.082397 | 0.19684 | 0.12817 | 0.19684 | 121.8796 | -0.032044 | -0.036621 | 122.1405 | 122.0261 | 122.0123 | 0.14649 | 0.13275 | 121.8933 | -0.027466 | 0.004577 | 122.1313 | 122.1313 | 122.0627 | 0.23804 | 0.16937 | 0.26093 | 0.096131 | 0.23804 | 0.1236 | 0.10071 | 0.091553 | 121.9803 | 121.9849 | -0.13275 | -0.11902 | 121.9757 | 122.0169 | 121.9162 | 122.0535
1783.9219 | 122.2412 | -121.9025 | 0.082397 | -0.0036622 | 0.067214 | 0.01568 | 0.024607 | -0.0019034 | -0.0036102 | 0.00027129 | -0.0015565 | 0.024007 | 0.016285 | 0.020668 | 0.0020401 | 0.019452 | -0.0027749 | -0.036621 | 0.054932 | -0.064087 | 0.018311 | 0.15564 | 0.018311 | 0.054932 | 0.064087 | 0.045776 | -0.036621 | 0.09613 | 0.16479 | 0.068665 | 0.21515 | 121.8384 | -0.027465 | -0.064086 | 122.0581 | 121.9574 | 121.9208 | 0.11902 | 0.082398 | 121.8658 | -0.036621 | 0.013733 | 122.0673 | 122.1176 | 121.9711 | 0.25177 | 0.10529 | 0.21973 | 0.082398 | 0.20142 | 0.13275 | 0.11902 | 0.082397 | 121.9574 | 121.9482 | -0.14648 | -0.11902 | 121.9208 | 121.9986 | 121.8658 | 121.9666
1785.6719 | 122.2229 | -121.9254 | 0.09613 | -0.0036622 | 0.065078 | 0.015466 | 0.022685 | 0.0019418 | -0.0023284 | -0.0014377 | 0.0045471 | 0.02358 | 0.019275 | 0.012978 | -0.00030965 | 0.019666 | -0.0025613 | -0.041199 | 0.059509 | -0.041199 | 0.022888 | 0.17395 | 0.013733 | 0.050354 | 0.054932 | 0.068665 | -0.050354 | 0.054932 | 0.14191 | 0.050354 | 0.17853 | 121.8842 | -0.036621 | -0.073242 | 122.0993 | 121.9757 | 121.9391 | 0.091553 | 0.054932 | 121.875 | -0.027465 | -0.041198 | 122.0673 | 122.1039 | 121.9757 | 0.22888 | 0.10071 | 0.21515 | 0.064087 | 0.19226 | 0.10529 | 0.10071 | 0.11902 | 121.9849 | 121.994 | -0.13733 | -0.14648 | 121.9482 | 121.9803 | 121.8842 | 121.9803
1787.4219 | 122.1542 | -122.0032 | 0.11444 | -0.0036622 | 0.06636 | 0.014398 | 0.021403 | -0.00019445 | -0.0019012 | -0.0029331 | -0.0015565 | 0.027852 | 0.019275 | 0.0074235 | -9.605e-05 | 0.019239 | -0.0040567 | -0.050354 | 0.07782 | -0.073242 | -0.032043 | 0.091553 | -0.027466 | -0.013733 | -0.004578 | 0.09613 | -0.07782 | 0.018311 | 0.068665 | -0.022888 | 0.11444 | 121.9299 | -0.036621 | -0.14648 | 122.0947 | 121.9894 | 121.9757 | 0.059509 | 0.045776 | 121.9254 | -0.018311 | -0.09613 | 122.0718 | 122.1176 | 121.9803 | 0.19226 | 0.054932 | 0.16479 | 0.041199 | 0.14649 | 0.096131 | 0.15106 | 0.17395 | 122.081 | 122.0993 | -0.18768 | -0.19226 | 121.9711 | 122.0215 | 121.9528 | 121.9986
1789.1094 | 122.2092 | -121.9528 | 0.11444 | -0.011291 | 0.064651 | 0.014185 | 0.020548 | 1.915e-05 | -0.004251 | -0.0016513 | -0.0015565 | 0.022725 | 0.018421 | 0.018532 | -0.0011643 | 0.01988 | -0.0044839 | -0.07782 | 0.068665 | -0.050354 | -0.032043 | 0.11902 | 0 | 0.027466 | -0.018311 | 0.073242 | -0.054932 | 0.013733 | 0.11902 | 0.032043 | 0.13733 | 121.9025 | -0.045776 | -0.14648 | 122.0718 | 121.9803 | 121.9528 | 0.07782 | 0.050354 | 121.8979 | -0.041199 | -0.10071 | 122.0718 | 122.0901 | 121.9849 | 0.19226 | 0.086975 | 0.16937 | 0.018311 | 0.17395 | 0.068665 | 0.11902 | 0.12817 | 122.0215 | 122.0261 | -0.16479 | -0.16937 | 121.9208 | 121.9666 | 121.875 | 121.9345
1790.875 | 122.1817 | -121.962 | 0.1236 | -0.0036622 | 0.067428 | 0.015466 | 0.021403 | -0.00062165 | -0.0027556 | -0.00036951 | -0.0046081 | 0.023366 | 0.017566 | 0.0025101 | -0.0011643 | 0.017103 | -0.0027749 | -0.054932 | 0.086975 | -0.064087 | -0.036621 | 0.09613 | -0.013733 | -0.009155 | 0.004578 | 0.07782 | -0.064087 | 0.004578 | 0.086975 | -0.004578 | 0.13275 | 121.8979 | -0.036621 | -0.16022 | 122.0581 | 121.9528 | 121.9482 | 0.054932 | 0.050354 | 121.8979 | -0.045776 | -0.11902 | 122.0489 | 122.0947 | 121.9574 | 0.19684 | 0.059509 | 0.16022 | 0.027466 | 0.15106 | 0.068665 | 0.15106 | 0.14191 | 122.0489 | 122.0398 | -0.18768 | -0.18768 | 121.9254 | 121.9666 | 121.907 | 121.9666
1792.6094 | 122.2366 | -121.962 | 0.086975 | 0.011597 | 0.06636 | 0.017816 | 0.02183 | -0.001476 | -0.0027556 | -0.0012241 | -0.0046081 | 0.02358 | 0.020771 | 0.022591 | -0.0013779 | 0.019025 | 0.00021567 | -0.064087 | 0.068665 | -0.045776 | -0.036621 | 0.10986 | -0.013733 | 0.036621 | -0.009155 | 0.064087 | -0.054932 | 0.027466 | 0.11444 | 0.036621 | 0.13733 | 121.9162 | -0.01831 | -0.1236 | 122.0718 | 121.9986 | 121.9482 | 0.082397 | 0.032043 | 121.907 | -0.022888 | -0.059509 | 122.0764 | 122.0993 | 121.9986 | 0.19226 | 0.091553 | 0.15564 | 0.009155 | 0.16937 | 0.082398 | 0.11444 | 0.11902 | 122.0306 | 122.0261 | -0.13275 | -0.14191 | 121.9254 | 121.9894 | 121.8979 | 121.9528
1794.2969 | 122.1863 | -121.9894 | 0.10529 | -0.0036622 | 0.066574 | 0.015466 | 0.023539 | 0.0010874 | -0.003183 | 0.0013395 | 0.0014953 | 0.025716 | 0.020771 | 0.0102 | -0.0026597 | 0.016462 | -0.0012795 | -0.054932 | 0.082397 | -0.07782 | -0.054932 | 0.086975 | -0.036621 | -0.018311 | -0.004578 | 0.09613 | -0.064087 | -0.004578 | 0.064087 | -0.027466 | 0.10986 | 121.9116 | -0.022889 | -0.16022 | 122.0764 | 121.9711 | 121.9528 | 0.059509 | 0.041199 | 121.9254 | -0.009156 | -0.10986 | 122.0535 | 122.0993 | 121.962 | 0.17395 | 0.036621 | 0.16479 | 0.022888 | 0.12817 | 0.059509 | 0.16022 | 0.16022 | 122.0718 | 122.0856 | -0.18311 | -0.16937 | 121.9345 | 121.9849 | 121.9345 | 121.9849
1796.0469 | 122.1542 | -121.9803 | 0.13275 | -0.018921 | 0.066574 | 0.015894 | 0.023112 | 0.0015146 | -0.0027556 | -0.0029331 | -0.0046081 | 0.027211 | 0.019062 | 0.017464 | -9.605e-05 | 0.017957 | -0.0025613 | -0.10986 | 0.086975 | -0.086975 | -0.091553 | 0.009155 | -0.10071 | -0.059509 | -0.09613 | 0.09613 | -0.073242 | -0.027466 | 0.009155 | -0.068665 | 0.086975 | 121.8933 | -0.045776 | -0.2243 | 121.9894 | 121.9208 | 121.8796 | 0.027466 | -0.013733 | 121.907 | -0.036621 | -0.16022 | 121.9894 | 122.0673 | 121.9116 | 0.16022 | 0.004577 | 0.09613 | -0.004578 | 0.082397 | 0.045776 | 0.17395 | 0.16937 | 122.0673 | 122.0764 | -0.21973 | -0.20599 | 121.8887 | 121.9528 | 121.8704 | 121.8842
1797.7344 | 122.2916 | -121.962 | 0.086975 | -0.011291 | 0.065933 | 0.017389 | 0.020762 | -0.001476 | -0.00083304 | -0.0020785 | -0.0046081 | 0.021871 | 0.021839 | 0.014686 | 0.0026809 | 0.019239 | -0.0014931 | -0.027466 | 0.045776 | -0.022888 | 0.013733 | 0.17853 | 0.004578 | 0.054932 | 0.07782 | 0.041199 | -0.036621 | 0.091553 | 0.16937 | 0.091553 | 0.20142 | 121.9391 | -0.041199 | -0.073242 | 122.1405 | 122.0169 | 121.9666 | 0.07782 | 0.027466 | 121.9254 | -0.045776 | 0.004578 | 122.1313 | 122.1634 | 122.0535 | 0.23804 | 0.12817 | 0.20142 | 0.036621 | 0.20599 | 0.12817 | 0.068664 | 0.07782 | 122.0078 | 122.0032 | -0.10986 | -0.1236 | 121.9757 | 122.0535 | 121.9345 | 122.0398
1799.4844 | 122.1634 | -121.9757 | 0.1236 | -0.018921 | 0.067428 | 0.016107 | 0.023112 | -0.002117 | -0.0023284 | 0.0017667 | -0.0046081 | 0.023152 | 0.019275 | 0.0091325 | -0.00095065 | 0.020307 | -0.0027749 | -0.068665 | 0.07782 | -0.082397 | -0.073242 | 0.059509 | -0.073242 | -0.045776 | -0.054932 | 0.091553 | -0.059509 | -0.018311 | 0.050354 | -0.032043 | 0.082397 | 121.8933 | -0.045776 | -0.19684 | 122.0352 | 121.9299 | 121.9025 | 0.036621 | 0.009155 | 121.9162 | -0.032043 | -0.14191 | 122.0261 | 122.0581 | 121.9437 | 0.14191 | 0.027466 | 0.14191 | 0.009155 | 0.10986 | 0.041198 | 0.16022 | 0.15106 | 122.0535 | 122.0673 | -0.20599 | -0.1831 | 121.9025 | 121.9574 | 121.907 | 121.9208
1801.1562 | 122.3007 | -121.9574 | 0.07782 | -0.011291 | 0.06636 | 0.013971 | 0.021189 | -0.00083525 | -0.00061944 | 0.00027129 | -0.0015565 | 0.021016 | 0.021839 | 0.020668 | 0.0022537 | 0.020307 | 0.0010703 | -0.018311 | 0.041199 | -0.050354 | 0.036621 | 0.18768 | 0.036621 | 0.054932 | 0.086975 | 0.068665 | -0.045776 | 0.10529 | 0.1831 | 0.086975 | 0.19226 | 121.907 | -0.036621 | -0.041199 | 122.1451 | 122.0123 | 121.994 | 0.10529 | 0.086975 | 121.9116 | -0.009155 | 0.027466 | 122.1405 | 122.1497 | 122.0444 | 0.23804 | 0.13275 | 0.23804 | 0.086975 | 0.22888 | 0.15106 | 0.091553 | 0.11444 | 121.9986 | 122.0261 | -0.12817 | -0.1236 | 121.994 | 122.0627 | 121.9391 | 122.0444
1802.9062 | 122.3099 | -121.9666 | 0.10071 | -0.011291 | 0.062728 | 0.014825 | 0.020335 | -0.0012624 | -0.0023284 | -0.0022921 | -0.0015565 | 0.022084 | 0.020771 | 0.018745 | -0.0024461 | 0.019025 | -0.0017069 | -0.032043 | 0.036621 | -0.041199 | 0.032043 | 0.2243 | 0.082397 | 0.09613 | 0.09613 | 0.045776 | -0.022888 | 0.082397 | 0.20142 | 0.13275 | 0.21057 | 121.9254 | -0.064087 | -0.068665 | 122.1909 | 122.0627 | 122.049 | 0.13733 | 0.1236 | 121.9437 | -0.054932 | -0.018311 | 122.168 | 122.1771 | 122.0993 | 0.23346 | 0.15564 | 0.2655 | 0.073242 | 0.2243 | 0.10528 | 0.07782 | 0.068664 | 122.0032 | 122.0123 | -0.14191 | -0.1236 | 121.9986 | 122.049 | 121.9345 | 122.0627
1804.5938 | 122.1863 | -121.9849 | 0.1236 | 0.0039673 | 0.065078 | 0.015894 | 0.022471 | 0.0027964 | -0.0027556 | -0.0020785 | -0.0046081 | 0.025716 | 0.021625 | 0.0196 | -0.0015915 | 0.017743 | -0.00063873 | -0.045776 | 0.07782 | -0.082397 | -0.050354 | 0.091553 | -0.036621 | -0.022888 | -0.022888 | 0.091553 | -0.054932 | 0.013733 | 0.064087 | -0.027466 | 0.11444 | 121.9025 | -0.045776 | -0.17395 | 122.0764 | 121.962 | 121.9482 | 0.059509 | 0.045776 | 121.9299 | -0.032043 | -0.10986 | 122.049 | 122.0993 | 121.9574 | 0.16937 | 0.027466 | 0.17395 | 0.032043 | 0.11902 | 0.068665 | 0.16022 | 0.14649 | 122.0627 | 122.0764 | -0.20599 | -0.17853 | 121.9345 | 121.9986 | 121.9391 | 121.962
1806.3438 | 122.1451 | -122.0261 | 0.12817 | 0.0039673 | 0.064865 | 0.01568 | 0.021617 | -0.0010488 | -0.004251 | 0.00069849 | -0.0015565 | 0.02657 | 0.017994 | 0.0089187 | 0.0013991 | 0.019025 | -0.00021153 | -0.091553 | 0.068665 | -0.059509 | -0.11902 | 0.013733 | -0.11444 | -0.064087 | -0.11444 | 0.10529 | -0.082397 | -0.054932 | 0.013733 | -0.082397 | 0.068665 | 121.9666 | -0.059509 | -0.24719 | 122.0398 | 121.962 | 121.9116 | -0.004578 | -0.054932 | 121.9437 | -0.022888 | -0.18311 | 122.0398 | 122.0947 | 121.9437 | 0.15106 | 0 | 0.073242 | -0.05951 | 0.09613 | 0.027465 | 0.12817 | 0.18768 | 122.0947 | 122.1313 | -0.18768 | -0.21057 | 121.907 | 121.9711 | 121.9345 | 121.9116
1808.0938 | 122.168 | -122.0261 | 0.11444 | -0.011291 | 0.065933 | 0.015466 | 0.021617 | 0.00066015 | -0.0012604 | -0.0014377 | 0.0014953 | 0.022725 | 0.020771 | 0.018959 | -0.00095065 | 0.017743 | -0.0055521 | -0.091553 | 0.082397 | -0.086975 | -0.10986 | -0.004578 | -0.10529 | -0.068665 | -0.13275 | 0.091553 | -0.07782 | -0.032043 | 0.018311 | -0.045776 | 0.10071 | 121.9391 | -0.032044 | -0.2243 | 122.0215 | 121.9574 | 121.9208 | 0.01831 | -0.018311 | 121.9482 | -0.022888 | -0.14648 | 122.0444 | 122.1268 | 121.9803 | 0.17853 | 0.032044 | 0.082397 | -0.022888 | 0.096131 | 0.045777 | 0.16937 | 0.16937 | 122.1085 | 122.1176 | -0.20142 | -0.19226 | 121.9162 | 121.994 | 121.9345 | 121.8933
1809.8438 | 122.2824 | -122.0078 | 0.10071 | -0.011291 | 0.065505 | 0.015253 | 0.020121 | 1.915e-05 | -0.003183 | -0.0014377 | -0.0076599 | 0.021871 | 0.017994 | 0.021736 | -0.0013779 | 0.018171 | -0.0019205 | -0.027466 | 0.050354 | -0.050354 | 0.013733 | 0.1831 | 0.07782 | 0.086975 | 0.041199 | 0.054932 | -0.036621 | 0.059509 | 0.17853 | 0.082397 | 0.18768 | 121.9574 | -0.050354 | -0.086975 | 122.1909 | 122.0947 | 122.0856 | 0.13733 | 0.12817 | 121.9711 | -0.045776 | -0.041199 | 122.1863 | 122.1954 | 122.0901 | 0.2243 | 0.11902 | 0.23346 | 0.064087 | 0.21515 | 0.09613 | 0.10071 | 0.091553 | 122.0581 | 122.0627 | -0.15106 | -0.13733 | 122.0215 | 122.0673 | 121.9803 | 122.049
1811.5781 | 122.1909 | -122.0718 | 0.11444 | -0.0036622 | 0.067214 | 0.012476 | 0.020548 | -0.0029714 | -0.0046782 | -0.00058311 | -0.0076599 | 0.024007 | 0.018848 | 0.013191 | -0.0035141 | 0.015821 | -0.00085233 | -0.11902 | 0.086975 | -0.07782 | -0.11444 | 0.041199 | -0.050354 | -0.018311 | -0.10529 | 0.10071 | -0.086975 | -0.050354 | 0.032043 | -0.018311 | 0.082397 | 121.994 | -0.027466 | -0.22888 | 122.113 | 122.0535 | 122.0215 | 0.059509 | 0.027466 | 121.9849 | -0.013733 | -0.16479 | 122.1039 | 122.1542 | 122.0535 | 0.16937 | 0.068664 | 0.11902 | -0.036621 | 0.11902 | 0.036621 | 0.16479 | 0.18768 | 122.1588 | 122.1725 | -0.19226 | -0.20142 | 121.9574 | 122.0215 | 121.9528 | 121.9666
1813.2656 | 122.319 | -121.9849 | 0.07782 | -0.0036622 | 0.066146 | 0.01803 | 0.023326 | 0.00044655 | -0.0027556 | -0.00079691 | -0.0015565 | 0.02358 | 0.019916 | 0.017464 | 0.0022537 | 0.019666 | -0.0036295 | -0.050354 | 0.073242 | -0.050354 | -0.004578 | 0.15564 | 0.004578 | 0.036621 | 0.054932 | 0.068665 | -0.045776 | 0.11444 | 0.16937 | 0.073242 | 0.21515 | 121.9345 | -0.004578 | -0.082398 | 122.1405 | 122.0215 | 121.9894 | 0.086975 | 0.054932 | 121.9391 | -0.009155 | 0.036621 | 122.1542 | 122.2 | 122.0581 | 0.26093 | 0.11902 | 0.20599 | 0.045776 | 0.21515 | 0.16022 | 0.1236 | 0.11444 | 122.0581 | 122.0535 | -0.12817 | -0.1236 | 121.9803 | 122.0993 | 121.9345 | 122.0398
1815.0156 | 122.3145 | -121.9757 | 0.10071 | -0.011291 | 0.06636 | 0.017816 | 0.021189 | 0.0032236 | -0.00083304 | -0.00015591 | 0.0045471 | 0.02358 | 0.019703 | 0.014046 | 0.0013991 | 0.020307 | 0.0012839 | -0.018311 | 0.050354 | -0.041199 | 0.022888 | 0.19684 | 0.032043 | 0.059509 | 0.082397 | 0.054932 | -0.041199 | 0.09613 | 0.16937 | 0.09613 | 0.20142 | 121.9345 | -0.050354 | -0.07782 | 122.1725 | 122.0352 | 122.0078 | 0.10071 | 0.073242 | 121.9345 | -0.045776 | -0.004578 | 122.1451 | 122.1771 | 122.0718 | 0.24262 | 0.13733 | 0.23804 | 0.064087 | 0.21057 | 0.13733 | 0.091553 | 0.096131 | 122.0261 | 122.0306 | -0.14191 | -0.14191 | 121.9986 | 122.0718 | 121.9574 | 122.0581
1816.7031 | 122.287 | -122.0352 | 0.086975 | -0.0036622 | 0.063583 | 0.015466 | 0.022257 | 1.915e-05 | -0.0033966 | -0.0016513 | -0.0015565 | 0.022512 | 0.020557 | 0.016823 | -0.00073705 | 0.017743 | 2.068e-06 | -0.068665 | 0.045776 | -0.054932 | -0.050354 | 0.11444 | -0.018311 | 0.018311 | 0 | 0.073242 | -0.068665 | 0.050354 | 0.13275 | 0.068665 | 0.16937 | 121.9803 | -0.041199 | -0.13733 | 122.1497 | 122.0535 | 122.0169 | 0.073243 | 0.036621 | 121.9666 | -0.013733 | -0.036621 | 122.168 | 122.2046 | 122.1039 | 0.23804 | 0.13733 | 0.16937 | 0.004578 | 0.20142 | 0.11902 | 0.10071 | 0.14191 | 122.081 | 122.1085 | -0.14191 | -0.15564 | 121.9849 | 122.0856 | 121.9666 | 122.0352
1818.4531 | 122.2137 | -122.049 | 0.10986 | -0.011291 | 0.065505 | 0.015253 | 0.023539 | 1.915e-05 | -0.0012604 | -0.0020785 | -0.0076599 | 0.026998 | 0.019489 | 0.0074235 | 0.0011855 | 0.018598 | 0.0017111 | -0.07782 | 0.09613 | -0.07782 | -0.10986 | 0 | -0.10071 | -0.054932 | -0.068665 | 0.10986 | -0.082397 | -0.018311 | 0.009155 | -0.054932 | 0.091553 | 121.9711 | -0.013733 | -0.21973 | 122.049 | 121.994 | 121.9482 | 0.022888 | -0.022888 | 121.9666 | 0 | -0.12817 | 122.0581 | 122.1405 | 121.994 | 0.17395 | 0.027465 | 0.07782 | -0.032043 | 0.091552 | 0.064086 | 0.17395 | 0.19226 | 122.1451 | 122.1588 | -0.18768 | -0.19226 | 121.9391 | 122.0306 | 121.9711 | 121.9803
1820.1406 | 122.2229 | -122.0673 | 0.12817 | -0.0036622 | 0.067001 | 0.016534 | 0.01948 | 0.00023275 | -0.0029694 | 0.0013395 | -0.0046081 | 0.022084 | 0.019916 | 0.01725 | -0.0058639 | 0.018384 | 0.0012839 | -0.036621 | 0.045776 | -0.064087 | -0.032043 | 0.1236 | 0.013733 | 0.032043 | -0.022888 | 0.07782 | -0.059509 | -0.013733 | 0.073242 | -0.004578 | 0.10529 | 122.0032 | -0.082398 | -0.16022 | 122.1909 | 122.0993 | 122.081 | 0.09613 | 0.07782 | 122.0078 | -0.050354 | -0.14191 | 122.1405 | 122.1725 | 122.0627 | 0.16479 | 0.054931 | 0.18768 | 0.032044 | 0.13275 | 0.045776 | 0.10986 | 0.13733 | 122.113 | 122.1451 | -0.19226 | -0.18768 | 122.0352 | 122.0535 | 122.0306 | 122.0444
1821.8906 | 122.3328 | -122.0032 | 0.082397 | 0.0039673 | 0.066787 | 0.017175 | 0.024394 | -0.0016898 | -0.0027556 | -0.0031467 | -0.0015565 | 0.023366 | 0.019489 | 0.0149 | 0.00011755 | 0.018384 | -0.0038431 | -0.022888 | 0.036621 | -0.054932 | 0.032043 | 0.17853 | 0.022888 | 0.073242 | 0.086975 | 0.059509 | -0.041199 | 0.086975 | 0.17853 | 0.086975 | 0.20599 | 121.9482 | -0.045776 | -0.050354 | 122.1817 | 122.0764 | 122.0261 | 0.12817 | 0.07782 | 121.962 | -0.022888 | 0.004578 | 122.1817 | 122.2092 | 122.0901 | 0.24719 | 0.12817 | 0.23346 | 0.086975 | 0.21973 | 0.12817 | 0.091553 | 0.10071 | 122.0398 | 122.0627 | -0.13733 | -0.1236 | 122.0352 | 122.0901 | 121.9803 | 122.0901
1823.6406 | 122.2137 | -122.0947 | 0.11902 | -0.0036622 | 0.067214 | 0.013971 | 0.024394 | -0.0040396 | -0.0023284 | -0.0020785 | 0.0075989 | 0.026998 | 0.020343 | 0.016823 | -0.0033005 | 0.016889 | -0.0046975 | -0.11902 | 0.11444 | -0.091553 | -0.11444 | 0.027466 | -0.050354 | -0.032043 | -0.086975 | 0.091553 | -0.10071 | -0.054932 | 0.032043 | -0.054932 | 0.091553 | 122.0032 | -0.004578 | -0.23346 | 122.1222 | 122.0627 | 122.0444 | 0.05951 | 0.041199 | 121.994 | -0.027466 | -0.17395 | 122.1268 | 122.1863 | 122.0398 | 0.19226 | 0.045776 | 0.11902 | -0.022888 | 0.13275 | 0.045776 | 0.20599 | 0.19226 | 122.2092 | 122.1863 | -0.21057 | -0.21973 | 121.9803 | 122.0398 | 121.9757 | 122.0078
1825.3906 | 122.2961 | -122.0352 | 0.09613 | -0.011291 | 0.065933 | 0.018457 | 0.021403 | 0.00023275 | -0.0019012 | -0.00058311 | 0.0045471 | 0.022512 | 0.018634 | 0.019813 | -0.0022325 | 0.01753 | -0.0049111 | -0.064087 | 0.054932 | -0.032043 | -0.018311 | 0.13275 | -0.009155 | 0.027466 | 0.013733 | 0.064087 | -0.054932 | 0.050354 | 0.11902 | 0.041199 | 0.14191 | 122.0032 | -0.041198 | -0.11444 | 122.168 | 122.0627 | 122.0261 | 0.059509 | 0.022888 | 121.9803 | -0.032043 | -0.045776 | 122.1542 | 122.1771 | 122.0764 | 0.19684 | 0.096131 | 0.16479 | 0.013732 | 0.17395 | 0.10529 | 0.086975 | 0.11902 | 122.0901 | 122.0993 | -0.12817 | -0.15106 | 122.0169 | 122.0856 | 121.9711 | 122.049
1827.125 | 122.2824 | -122.0627 | 0.10986 | -0.0036622 | 0.064865 | 0.014398 | 0.021617 | 0.0017282 | -0.0021148 | -0.0033603 | 0.0014953 | 0.022939 | 0.018421 | 0.0196 | -0.0030869 | 0.019452 | -0.0021341 | -0.018311 | 0.045776 | -0.050354 | 0.013733 | 0.16479 | 0.045776 | 0.059509 | 0.027466 | 0.054932 | -0.064087 | 0.022888 | 0.1236 | 0.032043 | 0.13733 | 122.0123 | -0.064087 | -0.09613 | 122.2275 | 122.1222 | 122.1085 | 0.10986 | 0.09613 | 121.9986 | -0.054931 | -0.086975 | 122.1863 | 122.2 | 122.0947 | 0.20142 | 0.09613 | 0.21515 | 0.064087 | 0.18768 | 0.086975 | 0.09613 | 0.11902 | 122.1085 | 122.1176 | -0.16022 | -0.17395 | 122.0764 | 122.0856 | 122.0444 | 122.0901
1828.8594 | 122.2458 | -122.0764 | 0.10986 | -0.011291 | 0.067642 | 0.018243 | 0.021617 | 0.0017282 | -0.0044646 | 0.0013395 | 0.0014953 | 0.026784 | 0.020343 | 0.011269 | -0.0020187 | 0.018598 | -0.0061929 | -0.054932 | 0.07782 | -0.07782 | -0.045776 | 0.09613 | -0.036621 | 0.004578 | -0.013733 | 0.082397 | -0.07782 | 0.009155 | 0.073242 | -0.009155 | 0.1236 | 121.9986 | -0.032043 | -0.15564 | 122.1725 | 122.081 | 122.0398 | 0.082398 | 0.041199 | 121.9986 | -0.027466 | -0.10071 | 122.1497 | 122.2 | 122.0673 | 0.20142 | 0.068665 | 0.17395 | 0.032044 | 0.15106 | 0.086975 | 0.15564 | 0.16022 | 122.1542 | 122.1588 | -0.18768 | -0.18768 | 122.0306 | 122.0856 | 122.0215 | 122.0627
1830.5469 | 122.2458 | -122.0718 | 0.10529 | -0.0036622 | 0.065933 | 0.01568 | 0.022471 | 0.00044655 | -0.003183 | -0.00036951 | -0.0046081 | 0.02358 | 0.020343 | 0.016823 | 0.00075835 | 0.017743 | -0.0010659 | -0.041199 | 0.073242 | -0.082397 | -0.045776 | 0.10986 | -0.036621 | -0.013733 | -0.004578 | 0.082397 | -0.054932 | 0.018311 | 0.082397 | -0.009155 | 0.10986 | 121.9894 | -0.032044 | -0.15106 | 122.1817 | 122.0581 | 122.0352 | 0.068664 | 0.045776 | 122.0169 | -0.022889 | -0.086975 | 122.1542 | 122.1817 | 122.0627 | 0.16479 | 0.045777 | 0.19226 | 0.036621 | 0.13733 | 0.073243 | 0.15564 | 0.13733 | 122.1451 | 122.1542 | -0.18768 | -0.16022 | 122.0261 | 122.0901 | 122.0306 | 122.0673
1832.2812 | 122.2641 | -122.0856 | 0.10529 | -0.011291 | 0.065933 | 0.016107 | 0.020335 | -0.003826 | -0.002542 | -0.0020785 | -0.0076599 | 0.024221 | 0.019703 | 0.011909 | -0.0045823 | 0.018384 | -0.0021341 | -0.036621 | 0.041199 | -0.050354 | -0.009155 | 0.15106 | 0.022888 | 0.045776 | -0.004578 | 0.073242 | -0.068665 | -0.009155 | 0.10986 | 0.013733 | 0.13275 | 122.0352 | -0.064087 | -0.11444 | 122.2366 | 122.1313 | 122.1085 | 0.09613 | 0.073242 | 122.0169 | -0.032044 | -0.11444 | 122.1954 | 122.2183 | 122.0993 | 0.20142 | 0.082398 | 0.20142 | 0.041199 | 0.17853 | 0.05951 | 0.091553 | 0.14191 | 122.1268 | 122.1588 | -0.15564 | -0.17395 | 122.0764 | 122.0764 | 122.049 | 122.081
1834.0312 | 122.2961 | -122.0581 | 0.10986 | 0.0039673 | 0.064651 | 0.014398 | 0.023539 | 0.00023275 | -0.0019012 | -0.0012241 | -0.0015565 | 0.022725 | 0.020771 | 0.015968 | -0.00095065 | 0.019025 | -0.0038431 | -0.050354 | 0.073242 | -0.068665 | -0.027466 | 0.09613 | -0.027466 | 0.009155 | 0.018311 | 0.082397 | -0.073242 | 0.022888 | 0.11444 | 0.022888 | 0.13733 | 121.9894 | -0.036621 | -0.13733 | 122.1542 | 122.0673 | 122.0306 | 0.07782 | 0.041199 | 121.9849 | -0.027466 | -0.086975 | 122.1725 | 122.1954 | 122.081 | 0.21057 | 0.09613 | 0.16479 | 0.041199 | 0.18768 | 0.09613 | 0.14191 | 0.15564 | 122.1313 | 122.1405 | -0.17853 | -0.18311 | 122.0306 | 122.081 | 122.0078 | 122.0764
1835.7188 | 122.2321 | -122.0993 | 0.15106 | -0.0036622 | 0.065078 | 0.016107 | 0.019908 | -0.0027578 | -0.0016876 | -0.0029331 | -0.0015565 | 0.023793 | 0.019703 | 0.012337 | -0.0039413 | 0.017743 | -0.00042513 | -0.11444 | 0.07782 | -0.07782 | -0.11902 | 0.036621 | -0.059509 | -0.022888 | -0.07782 | 0.082397 | -0.09613 | -0.064087 | 0.050354 | -0.032043 | 0.082397 | 122.0215 | -0.073242 | -0.27008 | 122.1359 | 122.0764 | 122.0398 | 0.054932 | 0.018311 | 122.0032 | -0.068665 | -0.21515 | 122.1497 | 122.1817 | 122.0673 | 0.17853 | 0.064087 | 0.11444 | -0.041199 | 0.14648 | 0.032043 | 0.15564 | 0.17853 | 122.1771 | 122.1817 | -0.22888 | -0.24719 | 121.9803 | 122.0352 | 121.9849 | 122.0215
1837.4688 | 122.2458 | -122.0993 | 0.1236 | 0.0039673 | 0.064651 | 0.016107 | 0.022257 | -0.00019445 | -0.0040374 | 0.00069849 | -0.0015565 | 0.024434 | 0.02013 | 0.010628 | -0.0033005 | 0.015821 | -0.0055521 | -0.10986 | 0.082397 | -0.09613 | -0.11444 | 0.041199 | -0.050354 | -0.022888 | -0.086975 | 0.10986 | -0.082397 | -0.050354 | 0.050354 | -0.036621 | 0.091553 | 122.0032 | -0.041199 | -0.23804 | 122.1405 | 122.0764 | 122.049 | 0.073242 | 0.045776 | 122.0169 | -0.013733 | -0.17395 | 122.1497 | 122.1909 | 122.0627 | 0.17395 | 0.045776 | 0.13733 | -0.018311 | 0.13275 | 0.032043 | 0.17853 | 0.19226 | 122.1817 | 122.2092 | -0.21973 | -0.20599 | 121.9849 | 122.049 | 121.9894 | 122.0123
1839.1562 | 122.2412 | -122.0947 | 0.13275 | -0.0036622 | 0.066574 | 0.018457 | 0.023753 | 0.0021556 | -0.0040374 | -0.0020785 | -0.0015565 | 0.024434 | 0.017994 | 0.014473 | -0.00030965 | 0.017316 | -0.0012795 | -0.064087 | 0.082397 | -0.07782 | -0.10986 | 0.004578 | -0.10071 | -0.073242 | -0.10986 | 0.11444 | -0.082397 | -0.045776 | 0.027466 | -0.073242 | 0.068665 | 122.0169 | -0.050354 | -0.24261 | 122.0993 | 122.0215 | 121.994 | 0.004578 | -0.022888 | 122.0123 | -0.01831 | -0.17853 | 122.1222 | 122.1634 | 122.0215 | 0.15106 | 0.009155 | 0.082398 | -0.032043 | 0.10986 | 0.036621 | 0.16022 | 0.19684 | 122.1771 | 122.2092 | -0.21057 | -0.21515 | 121.9849 | 122.049 | 122.0306 | 121.9849
1840.9219 | 122.3465 | -122.0718 | 0.086975 | -0.011291 | 0.06401 | 0.01568 | 0.021617 | -0.0033986 | -0.0010468 | -0.0022921 | -0.0076599 | 0.024221 | 0.019916 | 0.014259 | -0.00052345 | 0.017957 | -0.0040567 | -0.082397 | 0.059509 | -0.059509 | -0.045776 | 0.10529 | -0.018311 | 0.027466 | 0.004578 | 0.073242 | -0.064087 | 0.050354 | 0.14191 | 0.068665 | 0.16022 | 122.0123 | -0.027466 | -0.13275 | 122.1771 | 122.0993 | 122.0535 | 0.086975 | 0.041198 | 122.0078 | -0.013733 | -0.036621 | 122.2137 | 122.2321 | 122.1405 | 0.2243 | 0.13275 | 0.16479 | 0.013733 | 0.20599 | 0.11444 | 0.11902 | 0.13733 | 122.1313 | 122.1451 | -0.14648 | -0.15106 | 122.0261 | 122.1222 | 121.9894 | 122.0764
1842.6562 | 122.3099 | -122.0993 | 0.10986 | -0.018921 | 0.065719 | 0.016962 | 0.025035 | -0.0010488 | -0.0021148 | -0.0018649 | -0.0015565 | 0.024648 | 0.02013 | 0.012978 | -0.00095065 | 0.017743 | -0.0027749 | -0.041199 | 0.07782 | -0.073242 | -0.036621 | 0.09613 | -0.018311 | -0.009155 | 0.009155 | 0.086975 | -0.054932 | 0.036621 | 0.10529 | 0.018311 | 0.15564 | 122.0261 | -0.032043 | -0.14648 | 122.1954 | 122.0901 | 122.081 | 0.064087 | 0.054931 | 122.0444 | -0.022888 | -0.073242 | 122.2046 | 122.2549 | 122.1176 | 0.21057 | 0.073243 | 0.16937 | 0.036621 | 0.16022 | 0.091553 | 0.15106 | 0.14191 | 122.1771 | 122.1863 | -0.18311 | -0.16479 | 122.0627 | 122.1359 | 122.0581 | 122.1085
1844.4062 | 122.374 | -122.081 | 0.086975 | -0.0036622 | 0.063796 | 0.013971 | 0.020976 | -0.0019034 | -0.0023284 | -0.00079691 | -0.0046081 | 0.022084 | 0.017994 | 0.015755 | 0.0018265 | 0.019666 | -0.0036295 | -0.059509 | 0.054932 | -0.054932 | -0.018311 | 0.14648 | 0.027466 | 0.059509 | 0.036621 | 0.050354 | -0.050354 | 0.082397 | 0.17853 | 0.10071 | 0.20599 | 122.0261 | -0.032043 | -0.10529 | 122.2275 | 122.1405 | 122.1085 | 0.11444 | 0.082398 | 122.0306 | -0.036621 | -0.004578 | 122.2595 | 122.287 | 122.1817 | 0.25635 | 0.15106 | 0.20142 | 0.036621 | 0.22888 | 0.13275 | 0.10986 | 0.10071 | 122.1359 | 122.1313 | -0.14191 | -0.13733 | 122.0627 | 122.1634 | 122.0215 | 122.1176
1846.0781 | 122.2321 | -122.1085 | 0.13275 | -0.011291 | 0.067001 | 0.015466 | 0.023326 | 0.00023275 | -0.0033966 | -0.0016513 | -0.0046081 | 0.025502 | 0.019703 | 0.0031509 | -0.00073705 | 0.019239 | -0.0021341 | -0.086975 | 0.07782 | -0.07782 | -0.10529 | 0.004578 | -0.11444 | -0.073242 | -0.10529 | 0.086975 | -0.07782 | -0.050354 | 0 | -0.064087 | 0.082397 | 122.0306 | -0.054931 | -0.23804 | 122.113 | 122.0352 | 121.994 | 0.004578 | -0.036621 | 122.0306 | -0.045776 | -0.18311 | 122.1085 | 122.1909 | 122.0444 | 0.16022 | 0.013733 | 0.082398 | -0.027466 | 0.07782 | 0.027466 | 0.15564 | 0.16479 | 122.1863 | 122.1954 | -0.21057 | -0.21057 | 122.0032 | 122.0581 | 122.0215 | 122.0032
1847.8125 | 122.2687 | -122.1085 | 0.11902 | -0.0036622 | 0.065078 | 0.018884 | 0.022257 | -0.001476 | -0.0046782 | 0.00091209 | -0.0015565 | 0.025289 | 0.021839 | 0.021736 | 0.0013991 | 0.019025 | -0.0021341 | -0.10071 | 0.082397 | -0.086975 | -0.11444 | -0.004578 | -0.10986 | -0.050354 | -0.082397 | 0.10071 | -0.086975 | -0.018311 | 0.018311 | -0.059509 | 0.091553 | 122.0215 | -0.036622 | -0.23346 | 122.1039 | 122.0581 | 121.9986 | 0.036621 | -0.022888 | 122.0215 | -0.018311 | -0.13733 | 122.1268 | 122.2 | 122.0489 | 0.17853 | 0.027466 | 0.082397 | -0.027466 | 0.10529 | 0.068664 | 0.16937 | 0.18768 | 122.1909 | 122.2092 | -0.20599 | -0.20599 | 121.994 | 122.0901 | 122.0078 | 122.0261
1849.5625 | 122.3785 | -122.0627 | 0.09613 | -0.011291 | 0.065078 | 0.013971 | 0.018626 | -0.0010488 | -0.0012604 | -0.00036951 | -0.0046081 | 0.022939 | 0.019275 | 0.011909 | -0.0030869 | 0.016462 | -0.0044839 | -0.036621 | 0.036621 | -0.045776 | 0.032043 | 0.19226 | 0.073242 | 0.082397 | 0.073242 | 0.045776 | -0.045776 | 0.082397 | 0.19226 | 0.12817 | 0.1831 | 122.0169 | -0.059509 | -0.064087 | 122.2549 | 122.1451 | 122.1359 | 0.12817 | 0.11902 | 122.0169 | -0.050354 | -0.013733 | 122.2549 | 122.2458 | 122.1909 | 0.22888 | 0.17395 | 0.23804 | 0.077819 | 0.23804 | 0.12817 | 0.082397 | 0.091552 | 122.0993 | 122.1085 | -0.14191 | -0.14191 | 122.0947 | 122.1451 | 122.0261 | 122.1359
1851.25 | 122.2824 | -122.113 | 0.09613 | -0.0036622 | 0.065933 | 0.01568 | 0.021189 | -0.003826 | -0.0023284 | -0.0018649 | -0.0015565 | 0.023152 | 0.019916 | 0.011909 | -0.0035141 | 0.016675 | 0.0038473 | -0.059509 | 0.054932 | -0.059509 | -0.059509 | 0.082397 | -0.009155 | 0.009155 | -0.036621 | 0.09613 | -0.07782 | -0.013733 | 0.068665 | 0 | 0.082397 | 122.0535 | -0.041198 | -0.15564 | 122.1954 | 122.1222 | 122.1039 | 0.068664 | 0.050354 | 122.0352 | 0 | -0.10986 | 122.1817 | 122.1954 | 122.113 | 0.16022 | 0.07782 | 0.14191 | 0 | 0.14649 | 0.064087 | 0.11444 | 0.17395 | 122.168 | 122.2092 | -0.15564 | -0.17395 | 122.0535 | 122.0993 | 122.0535 | 122.0764
1852.9844 | 122.2687 | -122.1039 | 0.11444 | 0.0039673 | 0.067855 | 0.013544 | 0.024607 | 1.915e-05 | -0.003183 | -0.0016513 | -0.0046081 | 0.024007 | 0.019916 | 0.010628 | -0.0039413 | 0.017316 | -0.0012795 | -0.10071 | 0.10071 | -0.091553 | -0.1236 | 0.027466 | -0.045776 | -0.022888 | -0.086975 | 0.091553 | -0.064087 | -0.032043 | 0.054932 | -0.036621 | 0.091553 | 122.0123 | -0.013733 | -0.23804 | 122.1313 | 122.081 | 122.0581 | 0.068665 | 0.045777 | 122.0398 | -0.022888 | -0.14648 | 122.1588 | 122.1954 | 122.0673 | 0.15564 | 0.027466 | 0.11902 | -0.032043 | 0.11902 | 0.032044 | 0.19226 | 0.15564 | 122.2046 | 122.1954 | -0.20599 | -0.17853 | 121.9803 | 122.0718 | 122.0032 | 122.0169
1854.7344 | 122.3602 | -122.0764 | 0.10529 | -0.0036622 | 0.065292 | 0.018457 | 0.020976 | 0.001301 | -0.0012604 | 0.00048489 | 0.0014953 | 0.023366 | 0.018848 | 0.0196 | 0.0016129 | 0.019025 | 2.068e-06 | -0.050354 | 0.045776 | -0.036621 | -0.004578 | 0.14648 | -0.004578 | 0.032043 | 0.036621 | 0.050354 | -0.036621 | 0.054932 | 0.11902 | 0.050354 | 0.16479 | 122.0398 | -0.05951 | -0.10986 | 122.2229 | 122.1085 | 122.0718 | 0.068664 | 0.032043 | 122.0398 | -0.054932 | -0.050354 | 122.1954 | 122.2412 | 122.1268 | 0.20142 | 0.086975 | 0.18311 | 0.032043 | 0.15564 | 0.091553 | 0.082397 | 0.086975 | 122.1222 | 122.1268 | -0.14191 | -0.14191 | 122.0718 | 122.1313 | 122.0261 | 122.113
1856.4688 | 122.3694 | -122.1313 | 0.10529 | -0.018921 | 0.063796 | 0.017389 | 0.023753 | -0.0012624 | -0.0012604 | -0.0037875 | 0.0014953 | 0.023793 | 0.02013 | 0.012123 | -0.0015915 | 0.020307 | -0.00021153 | -0.059509 | 0.050354 | -0.054932 | -0.041199 | 0.10529 | -0.027466 | 0.013733 | 0 | 0.068665 | -0.054932 | 0.045776 | 0.12817 | 0.059509 | 0.16479 | 122.0764 | -0.054932 | -0.14649 | 122.2366 | 122.1451 | 122.1039 | 0.068665 | 0.027466 | 122.0764 | -0.036621 | -0.05951 | 122.2595 | 122.2961 | 122.1909 | 0.21973 | 0.11444 | 0.16022 | 0.013733 | 0.18311 | 0.10071 | 0.10529 | 0.1236 | 122.1817 | 122.2 | -0.16022 | -0.16022 | 122.0901 | 122.1771 | 122.0718 | 122.1313
1858.1406 | 122.3328 | -122.1176 | 0.11444 | -0.0036622 | 0.064865 | 0.015039 | 0.023753 | 0.0015146 | -0.0016876 | 0.00091209 | -0.0046081 | 0.025716 | 0.019275 | 0.015755 | -0.0011643 | 0.017743 | 0.0014975 | -0.032043 | 0.086975 | -0.086975 | -0.054932 | 0.068665 | -0.032043 | 0 | -0.009155 | 0.091553 | -0.068665 | 0.009155 | 0.10071 | 0.009155 | 0.14191 | 122.0306 | -0.027466 | -0.16937 | 122.1863 | 122.1176 | 122.0856 | 0.086975 | 0.054932 | 122.049 | -0.022888 | -0.10529 | 122.2183 | 122.2595 | 122.1268 | 0.21057 | 0.07782 | 0.15564 | 0.032043 | 0.16937 | 0.07782 | 0.17395 | 0.16022 | 122.2046 | 122.2092 | -0.20142 | -0.18311 | 122.0627 | 122.1268 | 122.0856 | 122.1085
1859.8906 | 122.3831 | -122.0947 | 0.10529 | 0.0039673 | 0.065505 | 0.01568 | 0.02183 | -0.005535 | -0.0044646 | 0.0011257 | -0.0015565 | 0.022939 | 0.020557 | 0.015968 | -0.0022325 | 0.018812 | -0.0036295 | -0.068665 | 0.050354 | -0.068665 | -0.045776 | 0.11902 | 0.022888 | 0.032043 | -0.013733 | 0.050354 | -0.059509 | 0.036621 | 0.14648 | 0.073242 | 0.16022 | 122.0261 | -0.054932 | -0.15106 | 122.2137 | 122.1268 | 122.1176 | 0.10071 | 0.091553 | 122.0352 | -0.054932 | -0.068665 | 122.2412 | 122.2549 | 122.168 | 0.21973 | 0.13275 | 0.18768 | 0.022889 | 0.20599 | 0.09613 | 0.11902 | 0.10986 | 122.1451 | 122.1451 | -0.17395 | -0.16479 | 122.049 | 122.1313 | 122.0261 | 122.081
1861.6406 | 122.3145 | -122.1359 | 0.10529 | 0.011597 | 0.066146 | 0.013544 | 0.022898 | -0.0036124 | -0.0010468 | 5.7688e-05 | -0.0015565 | 0.024007 | 0.019703 | 0.013618 | -0.00095065 | 0.017743 | 0.00042947 | -0.073242 | 0.086975 | -0.082397 | -0.086975 | 0.032043 | -0.036621 | -0.009155 | -0.050354 | 0.082397 | -0.059509 | 0.004578 | 0.082397 | -0.013733 | 0.12817 | 122.0535 | -0.018311 | -0.19226 | 122.168 | 122.1268 | 122.0993 | 0.073242 | 0.045776 | 122.0764 | -0.022889 | -0.10071 | 122.2183 | 122.2641 | 122.1222 | 0.18768 | 0.045776 | 0.11444 | -0.004578 | 0.14191 | 0.064087 | 0.16937 | 0.14191 | 122.2229 | 122.2183 | -0.18768 | -0.16479 | 122.049 | 122.1405 | 122.0627 | 122.0856
1863.3281 | 122.4152 | -122.0901 | 0.10071 | -0.011291 | 0.062728 | 0.015894 | 0.020762 | -0.002117 | -0.001474 | -0.00079691 | 0.0045471 | 0.024007 | 0.019062 | 0.018532 | -0.0030869 | 0.020521 | 0.0019247 | -0.082397 | 0.059509 | -0.054932 | -0.022888 | 0.11444 | 0.009155 | 0.027466 | -0.009155 | 0.073242 | -0.054932 | 0.045776 | 0.14191 | 0.073242 | 0.16022 | 122.0352 | -0.041199 | -0.1236 | 122.2046 | 122.1176 | 122.0993 | 0.082398 | 0.064087 | 122.0352 | -0.027466 | -0.054932 | 122.2321 | 122.2504 | 122.1634 | 0.21515 | 0.12817 | 0.16937 | 0.032044 | 0.19684 | 0.10071 | 0.11444 | 0.12817 | 122.1497 | 122.1634 | -0.15564 | -0.15564 | 122.0673 | 122.1359 | 122.0078 | 122.081
1865.0781 | 122.4014 | -122.1039 | 0.07782 | -0.011291 | 0.066574 | 0.013971 | 0.020976 | -0.00062165 | -0.004251 | -0.0029331 | -0.0015565 | 0.02358 | 0.020343 | 0.020241 | -0.0026597 | 0.016034 | 0.00064307 | -0.027466 | 0.050354 | -0.032043 | 0.022888 | 0.19684 | 0.064087 | 0.082397 | 0.073242 | 0.050354 | -0.050354 | 0.068665 | 0.17395 | 0.11444 | 0.1831 | 122.0718 | -0.027466 | -0.054932 | 122.3007 | 122.1863 | 122.168 | 0.11444 | 0.09613 | 122.0535 | -0.027466 | -0.009155 | 122.2778 | 122.287 | 122.2183 | 0.23346 | 0.16479 | 0.22888 | 0.054931 | 0.2243 | 0.11902 | 0.082397 | 0.10071 | 122.1542 | 122.1542 | -0.10986 | -0.12817 | 122.1268 | 122.1725 | 122.0764 | 122.1771
1866.8281 | 122.3557 | -122.1268 | 0.10986 | -0.0036622 | 0.066574 | 0.014825 | 0.023539 | 0.0015146 | -0.0029694 | -0.0035739 | -0.0015565 | 0.024648 | 0.01778 | 0.019386 | 0.00033115 | 0.016675 | -0.00085233 | -0.050354 | 0.073242 | -0.07782 | -0.045776 | 0.091553 | -0.022888 | -0.004578 | -0.022888 | 0.086975 | -0.064087 | 0.022888 | 0.10529 | 0.018311 | 0.12817 | 122.0489 | -0.036621 | -0.15564 | 122.2183 | 122.1222 | 122.1039 | 0.073242 | 0.054932 | 122.0627 | -0.022888 | -0.086975 | 122.2321 | 122.2549 | 122.1451 | 0.19226 | 0.082398 | 0.16937 | 0.032044 | 0.16937 | 0.086975 | 0.15106 | 0.15106 | 122.2 | 122.2137 | -0.18768 | -0.17395 | 122.081 | 122.1497 | 122.0764 | 122.1039
1868.5 | 122.4014 | -122.0901 | 0.11902 | 0.0039673 | 0.063796 | 0.01568 | 0.020121 | -0.0010488 | -0.0016876 | -0.00058311 | -0.0015565 | 0.020803 | 0.018207 | 0.020241 | -9.605e-05 | 0.017743 | 0.00085667 | -0.086975 | 0.059509 | -0.050354 | -0.018311 | 0.11902 | 0.009155 | 0.041199 | 0.004578 | 0.054932 | -0.059509 | 0.054932 | 0.15106 | 0.091553 | 0.17395 | 122.0398 | -0.05951 | -0.13733 | 122.2092 | 122.1313 | 122.0993 | 0.091553 | 0.059509 | 122.0306 | -0.064087 | -0.064087 | 122.2412 | 122.2641 | 122.1817 | 0.23346 | 0.15106 | 0.16937 | 0.032043 | 0.21057 | 0.11444 | 0.10986 | 0.11444 | 122.1497 | 122.1451 | -0.16937 | -0.17853 | 122.0718 | 122.1451 | 122.0032 | 122.0947
1870.25 | 122.2916 | -122.1588 | 0.13733 | -0.011291 | 0.064437 | 0.014825 | 0.021403 | -0.00019445 | -0.0016876 | -0.0014377 | -0.0015565 | 0.025075 | 0.019489 | 0.010841 | -0.0035141 | 0.017316 | -0.0042703 | -0.1236 | 0.073242 | -0.091553 | -0.10071 | 0.050354 | -0.064087 | -0.018311 | -0.086975 | 0.10986 | -0.07782 | -0.054932 | 0.032043 | -0.041199 | 0.082397 | 122.0673 | -0.064087 | -0.23804 | 122.2092 | 122.1405 | 122.0947 | 0.073242 | 0.027466 | 122.081 | -0.027466 | -0.19226 | 122.1909 | 122.2412 | 122.1176 | 0.16022 | 0.036621 | 0.14191 | -0.009155 | 0.10986 | 0.022888 | 0.16479 | 0.18768 | 122.2321 | 122.2687 | -0.22888 | -0.21515 | 122.0581 | 122.1039 | 122.0352 | 122.0718
1871.9844 | 122.3099 | -122.1588 | 0.11902 | -0.011291 | 0.06636 | 0.016107 | 0.022471 | 0.0023692 | -0.0061736 | -0.00079691 | -0.0046081 | 0.024861 | 0.021625 | 0.019173 | -0.0052231 | 0.017103 | -0.0051247 | -0.041199 | 0.059509 | -0.050354 | -0.022888 | 0.13275 | 0.004578 | 0.027466 | 0 | 0.082397 | -0.064087 | 0.004578 | 0.086975 | 0.022888 | 0.10529 | 122.1085 | -0.05951 | -0.14191 | 122.2916 | 122.1863 | 122.1634 | 0.07782 | 0.054932 | 122.0947 | -0.036622 | -0.11444 | 122.2458 | 122.2641 | 122.1817 | 0.16937 | 0.086975 | 0.18311 | 0.027466 | 0.15106 | 0.068665 | 0.10986 | 0.14648 | 122.2183 | 122.2412 | -0.16937 | -0.18311 | 122.1359 | 122.1634 | 122.1176 | 122.1588
1873.7344 | 122.3877 | -122.1222 | 0.11444 | 0.0039673 | 0.065505 | 0.016748 | 0.018839 | -0.002117 | -0.0023284 | -0.00036951 | -0.0046081 | 0.02358 | 0.018207 | 0.013832 | -9.605e-05 | 0.020948 | -0.0021341 | -0.082397 | 0.059509 | -0.050354 | -0.027466 | 0.10529 | -0.013733 | 0.018311 | -0.013733 | 0.054932 | -0.068665 | 0.027466 | 0.10529 | 0.036621 | 0.15564 | 122.0718 | -0.054932 | -0.14191 | 122.2275 | 122.1405 | 122.1085 | 0.068665 | 0.036621 | 122.0535 | -0.059509 | -0.086975 | 122.2275 | 122.2778 | 122.1588 | 0.22431 | 0.10529 | 0.15564 | 0.022888 | 0.17395 | 0.096131 | 0.10986 | 0.1236 | 122.1817 | 122.1771 | -0.16479 | -0.18311 | 122.0947 | 122.1497 | 122.0398 | 122.1085
1875.4219 | 122.4335 | -122.1222 | 0.091553 | -0.0036622 | 0.062301 | 0.016748 | 0.020762 | -0.00083525 | -0.0027556 | -0.0025057 | -0.0046081 | 0.022512 | 0.02013 | 0.020668 | -0.00073705 | 0.019239 | 0.00085667 | -0.07782 | 0.045776 | -0.059509 | -0.013733 | 0.13733 | 0.027466 | 0.050354 | 0.027466 | 0.059509 | -0.050354 | 0.068665 | 0.16022 | 0.10986 | 0.19684 | 122.0627 | -0.045777 | -0.10529 | 122.2595 | 122.1725 | 122.1497 | 0.10986 | 0.086975 | 122.0718 | -0.032044 | -0.022888 | 122.2824 | 122.319 | 122.2321 | 0.24719 | 0.16022 | 0.19684 | 0.045776 | 0.21057 | 0.11902 | 0.10528 | 0.10986 | 122.168 | 122.1817 | -0.15106 | -0.14191 | 122.1085 | 122.1909 | 122.0444 | 122.1497
1877.1562 | 122.4472 | -122.1222 | 0.091553 | -0.011291 | 0.062515 | 0.013757 | 0.020548 | -0.004894 | -0.004251 | -0.0037875 | 0.0014953 | 0.022939 | 0.019703 | 0.017036 | -0.0028733 | 0.017743 | -0.0012795 | -0.018311 | 0.050354 | -0.050354 | 0.036621 | 0.21515 | 0.059509 | 0.11444 | 0.12817 | 0.050354 | -0.045776 | 0.07782 | 0.20599 | 0.11444 | 0.18768 | 122.0718 | -0.041199 | -0.054932 | 122.3373 | 122.2366 | 122.1817 | 0.16479 | 0.10986 | 122.0764 | -0.041199 | -0.013733 | 122.3282 | 122.3099 | 122.2366 | 0.23346 | 0.16022 | 0.2655 | 0.086975 | 0.25177 | 0.1236 | 0.10071 | 0.09613 | 122.1725 | 122.1725 | -0.14191 | -0.13733 | 122.1588 | 122.2 | 122.1039 | 122.2504
1878.9062 | 122.3053 | -122.1542 | 0.14191 | -0.011291 | 0.068069 | 0.014825 | 0.02653 | 0.001301 | 0.00044856 | -0.0010105 | -0.0015565 | 0.02657 | 0.02013 | 0.014686 | -0.00030965 | 0.019452 | -0.00063873 | -0.059509 | 0.07782 | -0.068665 | -0.073242 | 0.050354 | -0.086975 | -0.054932 | -0.054932 | 0.10529 | -0.059509 | -0.027466 | 0.041199 | -0.050354 | 0.09613 | 122.0856 | -0.064087 | -0.21515 | 122.2046 | 122.0993 | 122.0673 | 0.013733 | -0.01831 | 122.0947 | -0.036621 | -0.16937 | 122.1954 | 122.2504 | 122.1039 | 0.15564 | 0.009155 | 0.11902 | -0.004577 | 0.10071 | 0.032043 | 0.14649 | 0.16479 | 122.2321 | 122.2595 | -0.21057 | -0.20142 | 122.081 | 122.1268 | 122.0947 | 122.0993
1880.5938 | 122.3145 | -122.168 | 0.10986 | -0.0036622 | 0.064651 | 0.014185 | 0.02183 | 1.915e-05 | -0.0033966 | -0.00079691 | -0.0015565 | 0.023366 | 0.019916 | 0.014046 | -0.0037277 | 0.016034 | 0.00042947 | -0.082397 | 0.064087 | -0.091553 | -0.086975 | 0.045776 | -0.050354 | -0.004578 | -0.082397 | 0.091553 | -0.073242 | -0.036621 | 0.045776 | -0.018311 | 0.073242 | 122.0764 | -0.045776 | -0.19684 | 122.2137 | 122.1634 | 122.1176 | 0.086975 | 0.041199 | 122.0947 | -0.01831 | -0.14648 | 122.2137 | 122.2412 | 122.1497 | 0.14648 | 0.054931 | 0.13733 | 0.004578 | 0.11902 | 0.036621 | 0.15564 | 0.16479 | 122.2321 | 122.2595 | -0.20142 | -0.18311 | 122.081 | 122.1313 | 122.0856 | 122.0856
1882.3281 | 122.4106 | -122.1497 | 0.10071 | -0.0036622 | 0.06401 | 0.017389 | 0.022044 | 0.00066015 | -0.0027556 | 0.00069849 | -0.0046081 | 0.022084 | 0.018421 | 0.018959 | 0.00033115 | 0.018384 | -0.0014931 | -0.073242 | 0.041199 | -0.050354 | -0.045776 | 0.10529 | -0.013733 | 0.022888 | -0.009155 | 0.054932 | -0.068665 | 0.032043 | 0.12817 | 0.054932 | 0.16022 | 122.0993 | -0.059509 | -0.14648 | 122.2549 | 122.1725 | 122.1359 | 0.073242 | 0.036621 | 122.081 | -0.045776 | -0.068665 | 122.2778 | 122.3099 | 122.2046 | 0.22888 | 0.1236 | 0.15564 | 0.004578 | 0.19684 | 0.10071 | 0.091553 | 0.1236 | 122.1909 | 122.2046 | -0.15106 | -0.16937 | 122.1039 | 122.1817 | 122.0764 | 122.1405
1884.0781 | 122.3877 | -122.1176 | 0.09613 | -0.011291 | 0.06636 | 0.015894 | 0.020762 | 0.00044655 | -0.001474 | -0.0010105 | 0.0014953 | 0.024221 | 0.018634 | 0.011909 | 0.00054475 | 0.019666 | -0.0012795 | -0.073242 | 0.054932 | -0.050354 | -0.036621 | 0.10071 | -0.018311 | 0.013733 | -0.009155 | 0.059509 | -0.064087 | 0.032043 | 0.11444 | 0.036621 | 0.15106 | 122.0673 | -0.041198 | -0.13275 | 122.2183 | 122.1313 | 122.0993 | 0.064087 | 0.032043 | 122.0535 | -0.036621 | -0.064087 | 122.2321 | 122.2687 | 122.1542 | 0.21515 | 0.10071 | 0.15106 | 0.013733 | 0.17853 | 0.09613 | 0.10529 | 0.1236 | 122.1725 | 122.1771 | -0.14648 | -0.16022 | 122.081 | 122.1497 | 122.0444 | 122.1085
1885.8594 | 122.4609 | -122.1039 | 0.10071 | -0.011291 | 0.067428 | 0.018243 | 0.022898 | -0.00040805 | -0.0012604 | 0.0015531 | -0.0015565 | 0.025075 | 0.018207 | 0.019386 | 0.0020401 | 0.018598 | -0.0040567 | 0.004578 | 0.050354 | -0.036621 | 0.041199 | 0.18768 | 0.027466 | 0.059509 | 0.082397 | 0.045776 | -0.041199 | 0.10986 | 0.16937 | 0.091553 | 0.19684 | 122.0673 | -0.050354 | -0.059509 | 122.2916 | 122.1634 | 122.1313 | 0.09613 | 0.064087 | 122.0627 | -0.054932 | 0.009155 | 122.2733 | 122.3007 | 122.1954 | 0.23804 | 0.13275 | 0.2243 | 0.07782 | 0.21057 | 0.15106 | 0.086975 | 0.086975 | 122.1542 | 122.1497 | -0.13733 | -0.14191 | 122.1451 | 122.2137 | 122.1085 | 122.1863
1887.5469 | 122.3969 | -122.1588 | 0.091553 | -0.0036622 | 0.067214 | 0.014185 | 0.02183 | 0.0015146 | -0.002542 | 0.00069849 | -0.0046081 | 0.024007 | 0.022052 | 0.013191 | -0.00052345 | 0.017316 | -0.0017069 | -0.064087 | 0.050354 | -0.068665 | -0.022888 | 0.10529 | -0.027466 | 0.032043 | -0.009155 | 0.07782 | -0.059509 | 0.045776 | 0.10986 | 0.045776 | 0.14191 | 122.0901 | -0.041199 | -0.11444 | 122.2641 | 122.1909 | 122.1313 | 0.10071 | 0.041199 | 122.0993 | -0.013733 | -0.045777 | 122.2687 | 122.3007 | 122.2046 | 0.20142 | 0.10528 | 0.17395 | 0.045777 | 0.16937 | 0.10528 | 0.11902 | 0.13733 | 122.2092 | 122.2366 | -0.16022 | -0.15106 | 122.1359 | 122.2046 | 122.0947 | 122.1497
1889.2969 | 122.4518 | -122.1405 | 0.07782 | -0.011291 | 0.068069 | 0.017816 | 0.019908 | 0.0010874 | -0.0029694 | -0.0018649 | -0.0015565 | 0.023152 | 0.018207 | 0.021309 | 0.0028945 | 0.020093 | -0.0017069 | 0 | 0.027466 | -0.041199 | 0.036621 | 0.15106 | 0.022888 | 0.059509 | 0.09613 | 0.045776 | -0.050354 | 0.10529 | 0.1831 | 0.086975 | 0.19684 | 122.0993 | -0.050354 | -0.041199 | 122.2916 | 122.2 | 122.1634 | 0.10071 | 0.064087 | 122.0901 | -0.032044 | 0.027466 | 122.3236 | 122.3373 | 122.2275 | 0.24719 | 0.13733 | 0.19226 | 0.07782 | 0.23346 | 0.15564 | 0.068665 | 0.09613 | 122.168 | 122.1863 | -0.11902 | -0.12817 | 122.1771 | 122.2458 | 122.1405 | 122.2366
1891.0469 | 122.3419 | -122.168 | 0.10986 | -0.0036622 | 0.067001 | 0.016748 | 0.02418 | -0.00083525 | -0.00040584 | -0.00036951 | -0.0046081 | 0.02657 | 0.020343 | 0.011909 | 0.00011755 | 0.018171 | -0.0025613 | -0.068665 | 0.073242 | -0.059509 | -0.059509 | 0.082397 | -0.054932 | -0.045776 | -0.041199 | 0.091553 | -0.068665 | -0.009155 | 0.032043 | -0.036621 | 0.086975 | 122.1085 | -0.036621 | -0.16937 | 122.2504 | 122.1222 | 122.113 | 0.013733 | 0.004577 | 122.0993 | -0.01831 | -0.11902 | 122.2 | 122.2549 | 122.1313 | 0.15564 | 0.032044 | 0.14191 | 0 | 0.10071 | 0.05951 | 0.13275 | 0.16022 | 122.2412 | 122.2595 | -0.16937 | -0.17853 | 122.1085 | 122.1588 | 122.0993 | 122.1268
1892.7188 | 122.4243 | -122.1542 | 0.10986 | -0.011291 | 0.06636 | 0.017816 | 0.022898 | -0.0012624 | -0.0027556 | -0.0016513 | -0.0046081 | 0.025289 | 0.021839 | 0.019386 | -9.605e-05 | 0.01988 | -0.0014931 | -0.09613 | 0.073242 | -0.086975 | -0.068665 | 0.059509 | -0.073242 | -0.022888 | -0.022888 | 0.082397 | -0.050354 | 0.045776 | 0.10071 | 0.032043 | 0.16937 | 122.0673 | -0.036621 | -0.17853 | 122.2137 | 122.1313 | 122.081 | 0.064087 | 0.013733 | 122.1039 | -0.027466 | -0.064087 | 122.2549 | 122.3236 | 122.1863 | 0.21973 | 0.082397 | 0.14648 | 0.01831 | 0.15106 | 0.09613 | 0.16022 | 0.13275 | 122.2275 | 122.2366 | -0.19684 | -0.16022 | 122.0856 | 122.2 | 122.0581 | 122.1313
1894.4531 | 122.4609 | -122.1634 | 0.091553 | -0.011291 | 0.063583 | 0.016962 | 0.020335 | -0.0016898 | -0.0038238 | -0.0037875 | 0.0014953 | 0.021016 | 0.019703 | 0.020882 | -0.0026597 | 0.017957 | -0.00021153 | -0.032043 | 0.041199 | -0.036621 | 0.041199 | 0.20599 | 0.064087 | 0.07782 | 0.07782 | 0.041199 | -0.036621 | 0.082397 | 0.20142 | 0.11444 | 0.19684 | 122.1268 | -0.050354 | -0.050354 | 122.3694 | 122.2412 | 122.2275 | 0.11444 | 0.10071 | 122.1268 | -0.050354 | -0.009156 | 122.3648 | 122.3602 | 122.2778 | 0.23346 | 0.15106 | 0.24262 | 0.07782 | 0.23804 | 0.11902 | 0.07782 | 0.07782 | 122.2046 | 122.2046 | -0.12817 | -0.12817 | 122.2046 | 122.2458 | 122.1313 | 122.2412
1896.1406 | 122.4792 | -122.1542 | 0.09613 | -0.0036622 | 0.063583 | 0.016321 | 0.019267 | -0.00083525 | -0.0038238 | -0.0022921 | 0.0014953 | 0.023366 | 0.018421 | 0.020241 | -0.0033005 | 0.017957 | -0.00085233 | -0.022888 | 0.050354 | -0.041199 | 0.059509 | 0.2243 | 0.082397 | 0.10071 | 0.091553 | 0.059509 | -0.054932 | 0.091553 | 0.20142 | 0.12817 | 0.1831 | 122.113 | -0.045776 | -0.036621 | 122.3785 | 122.2549 | 122.2366 | 0.14191 | 0.1236 | 122.0993 | -0.036621 | -0.004577 | 122.3557 | 122.3373 | 122.2824 | 0.23804 | 0.18311 | 0.2655 | 0.10071 | 0.25635 | 0.14649 | 0.091553 | 0.11444 | 122.2046 | 122.2137 | -0.13733 | -0.15106 | 122.2137 | 122.2458 | 122.1313 | 122.2458
1897.875 | 122.4518 | -122.1085 | 0.091553 | 0.0039673 | 0.067428 | 0.016107 | 0.022044 | 0.00023275 | -0.0029694 | -0.0059237 | -0.0046081 | 0.024221 | 0.020984 | 0.030922 | 0.0022537 | 0.019666 | -0.0010659 | -0.013733 | 0.041199 | -0.018311 | 0.032043 | 0.19226 | 0.018311 | 0.068665 | 0.086975 | 0.036621 | -0.045776 | 0.091553 | 0.16937 | 0.082397 | 0.19684 | 122.0901 | -0.050354 | -0.05951 | 122.3007 | 122.1771 | 122.1268 | 0.086976 | 0.036622 | 122.0627 | -0.054932 | 0 | 122.2778 | 122.3053 | 122.1909 | 0.24261 | 0.12817 | 0.21057 | 0.050354 | 0.21515 | 0.13733 | 0.05951 | 0.082397 | 122.1497 | 122.1451 | -0.10986 | -0.13733 | 122.1405 | 122.2 | 122.0947 | 122.1954
1899.5625 | 122.4335 | -122.1313 | 0.086975 | 0.0039673 | 0.065719 | 0.015253 | 0.022471 | 0.0017282 | -0.00040584 | 5.7688e-05 | -0.0046081 | 0.024648 | 0.021412 | 0.018318 | -0.00073705 | 0.019666 | 0.0032065 | -0.022888 | 0.050354 | -0.050354 | 0.036621 | 0.20142 | 0.013733 | 0.059509 | 0.09613 | 0.059509 | -0.045776 | 0.091553 | 0.14648 | 0.07782 | 0.19226 | 122.081 | -0.036621 | -0.050354 | 122.3328 | 122.1909 | 122.1451 | 0.10986 | 0.064087 | 122.0856 | -0.027466 | 0.004578 | 122.2778 | 122.3236 | 122.2092 | 0.23804 | 0.1236 | 0.25177 | 0.086975 | 0.19226 | 0.13733 | 0.10071 | 0.10528 | 122.1817 | 122.1909 | -0.13733 | -0.13275 | 122.168 | 122.2229 | 122.1085 | 122.2275
1901.25 | 122.3328 | -122.1909 | 0.12817 | -0.011291 | 0.067214 | 0.016962 | 0.023112 | -0.001476 | -0.0016876 | 0.00027129 | -0.0015565 | 0.026143 | 0.019062 | 0.012123 | -0.00095065 | 0.019452 | -0.0051247 | -0.082397 | 0.082397 | -0.050354 | -0.082397 | 0.050354 | -0.09613 | -0.045776 | -0.09613 | 0.091553 | -0.068665 | -0.036621 | 0.018311 | -0.064087 | 0.086975 | 122.1405 | -0.045777 | -0.21057 | 122.2412 | 122.1451 | 122.0947 | 0.004578 | -0.045776 | 122.1222 | -0.036621 | -0.1648 | 122.2092 | 122.2778 | 122.1268 | 0.15564 | 0.004578 | 0.10071 | -0.032043 | 0.086976 | 0.032044 | 0.13275 | 0.16022 | 122.2733 | 122.2824 | -0.17853 | -0.19684 | 122.1085 | 122.1542 | 122.1085 | 122.0947
1902.9844 | 122.3648 | -122.1771 | 0.10529 | -0.011291 | 0.065719 | 0.014612 | 0.022685 | 0.001301 | -0.0027556 | -0.00015591 | -0.0015565 | 0.025289 | 0.019275 | 0.011055 | -0.00095065 | 0.01753 | -0.00042513 | -0.054932 | 0.068665 | -0.059509 | -0.050354 | 0.10071 | -0.027466 | -0.018311 | -0.018311 | 0.082397 | -0.059509 | 0.004578 | 0.068665 | -0.018311 | 0.11902 | 122.1176 | -0.036621 | -0.15564 | 122.2778 | 122.1588 | 122.1497 | 0.041198 | 0.032043 | 122.1176 | -0.022889 | -0.10071 | 122.2458 | 122.2961 | 122.1588 | 0.17853 | 0.041198 | 0.16022 | 0.009155 | 0.12817 | 0.064087 | 0.12817 | 0.14191 | 122.2458 | 122.2595 | -0.16479 | -0.16479 | 122.1268 | 122.1817 | 122.1222 | 122.1588
1904.7188 | 122.4152 | -122.1863 | 0.086975 | -0.0036622 | 0.064651 | 0.016107 | 0.023753 | -0.0016898 | -0.00083304 | -0.0033603 | -0.0046081 | 0.022084 | 0.019275 | 0.016395 | -0.0022325 | 0.019239 | -0.0036295 | -0.091553 | 0.054932 | -0.041199 | -0.036621 | 0.11444 | -0.018311 | 0.022888 | -0.027466 | 0.059509 | -0.054932 | 0.027466 | 0.11444 | 0.036621 | 0.15564 | 122.1451 | -0.032043 | -0.1236 | 122.3007 | 122.2092 | 122.168 | 0.064087 | 0.022888 | 122.1313 | -0.027466 | -0.059509 | 122.3007 | 122.3419 | 122.2229 | 0.21057 | 0.091553 | 0.15564 | 0.004578 | 0.16937 | 0.082398 | 0.096131 | 0.11444 | 122.2412 | 122.2458 | -0.12817 | -0.14191 | 122.1497 | 122.2137 | 122.0947 | 122.1588
1906.4688 | 122.3831 | -122.2092 | 0.11444 | -0.0036622 | 0.066146 | 0.015253 | 0.020976 | -0.0019034 | -0.0021148 | 0.0011257 | -0.0015565 | 0.022939 | 0.021198 | 0.017464 | -0.0058639 | 0.017743 | -0.0023477 | -0.041199 | 0.045776 | -0.041199 | 0 | 0.15106 | 0.036621 | 0.064087 | 0 | 0.073242 | -0.050354 | 0.004578 | 0.10986 | 0.013733 | 0.10986 | 122.168 | -0.068665 | -0.11444 | 122.3602 | 122.2733 | 122.2458 | 0.10529 | 0.07782 | 122.1588 | -0.041199 | -0.10986 | 122.319 | 122.319 | 122.2229 | 0.16022 | 0.064087 | 0.19226 | 0.041199 | 0.16022 | 0.054932 | 0.086975 | 0.1236 | 122.2549 | 122.2824 | -0.15564 | -0.16479 | 122.2092 | 122.2137 | 122.168 | 122.2092
1908.1562 | 122.3877 | -122.1817 | 0.10529 | -0.0036622 | 0.067642 | 0.016321 | 0.023966 | 0.0034372 | -0.0027556 | 0.0011257 | -0.0076599 | 0.02657 | 0.020557 | 0.012978 | -0.0013779 | 0.018598 | -0.0042703 | -0.045776 | 0.059509 | -0.068665 | -0.022888 | 0.10529 | -0.018311 | 0.009155 | 0.013733 | 0.07782 | -0.064087 | 0.041199 | 0.091553 | 0.027466 | 0.13733 | 122.113 | -0.045777 | -0.12817 | 122.287 | 122.1909 | 122.1634 | 0.07782 | 0.050354 | 122.1176 | -0.027466 | -0.064087 | 122.2733 | 122.319 | 122.2092 | 0.20142 | 0.091553 | 0.17395 | 0.045777 | 0.15564 | 0.10529 | 0.12817 | 0.14191 | 122.2412 | 122.2595 | -0.17395 | -0.16937 | 122.1588 | 122.2229 | 122.1359 | 122.1954
1909.9062 | 122.4243 | -122.1863 | 0.13275 | -0.0036622 | 0.065292 | 0.013116 | 0.020335 | -0.003826 | -0.0021148 | 0.0013395 | -0.0046081 | 0.02123 | 0.020343 | 0.015114 | -0.0022325 | 0.016248 | 0.0012839 | -0.022888 | 0.027466 | -0.041199 | 0.004578 | 0.16022 | 0.054932 | 0.068665 | 0.041199 | 0.054932 | -0.050354 | 0.032043 | 0.12817 | 0.045776 | 0.14191 | 122.1451 | -0.10529 | -0.12817 | 122.3465 | 122.2549 | 122.2412 | 0.10986 | 0.096131 | 122.1359 | -0.077819 | -0.10071 | 122.3145 | 122.3282 | 122.2321 | 0.19226 | 0.09613 | 0.20142 | 0.045777 | 0.17853 | 0.082397 | 0.068665 | 0.10529 | 122.2137 | 122.2412 | -0.17395 | -0.18311 | 122.1909 | 122.2183 | 122.1634 | 122.2275
1911.6562 | 122.4792 | -122.1634 | 0.059509 | 0.011597 | 0.06636 | 0.01568 | 0.022044 | -0.0010488 | -0.002542 | -0.0014377 | 0.0045471 | 0.025075 | 0.019062 | 0.019386 | 0.0016129 | 0.019025 | 0.0032065 | -0.009155 | 0.032043 | -0.045776 | 0.032043 | 0.18768 | 0.045776 | 0.054932 | 0.091553 | 0.036621 | -0.036621 | 0.10986 | 0.18768 | 0.091553 | 0.18768 | 122.1176 | -0.027466 | -0.027466 | 122.3511 | 122.2183 | 122.2092 | 0.10071 | 0.091552 | 122.1268 | -0.022888 | 0.050354 | 122.3511 | 122.3511 | 122.2549 | 0.2243 | 0.12817 | 0.23346 | 0.077819 | 0.2243 | 0.14648 | 0.077819 | 0.073242 | 122.1954 | 122.2 | -0.10528 | -0.09613 | 122.1954 | 122.2733 | 122.1542 | 122.2549
1913.3438 | 122.3465 | -122.2 | 0.11902 | -0.011291 | 0.066787 | 0.017603 | 0.025035 | 0.0010874 | -0.0019012 | -0.00058311 | -0.0046081 | 0.025289 | 0.021412 | 0.015755 | -0.00030965 | 0.018171 | -0.0040567 | -0.07782 | 0.082397 | -0.073242 | -0.082397 | 0.036621 | -0.091553 | -0.054932 | -0.068665 | 0.10071 | -0.073242 | -0.032043 | 0.022888 | -0.059509 | 0.073242 | 122.1268 | -0.036622 | -0.20142 | 122.2366 | 122.1451 | 122.1085 | 0.01831 | -0.018311 | 122.1268 | -0.018311 | -0.15106 | 122.2229 | 122.2733 | 122.1405 | 0.14648 | 0.013733 | 0.10986 | -0.009155 | 0.09613 | 0.041199 | 0.15564 | 0.17395 | 122.2824 | 122.3007 | -0.19226 | -0.19226 | 122.1176 | 122.168 | 122.1222 | 122.1313
1915.0312 | 122.4106 | -122.1909 | 0.10986 | -0.011291 | 0.065292 | 0.016962 | 0.021189 | 0.0023692 | -0.002542 | -0.0035739 | -0.0015565 | 0.023793 | 0.021198 | 0.020454 | -0.00073705 | 0.019239 | -0.00063873 | -0.10986 | 0.10529 | -0.086975 | -0.10071 | 0.045776 | -0.082397 | -0.036621 | -0.054932 | 0.091553 | -0.064087 | 0.032043 | 0.068665 | -0.013733 | 0.13275 | 122.1039 | -0.004577 | -0.21057 | 122.2366 | 122.1542 | 122.1085 | 0.050354 | 0.004578 | 122.1268 | -0.01831 | -0.07782 | 122.2595 | 122.3236 | 122.1771 | 0.19684 | 0.050354 | 0.13275 | -0.013733 | 0.13275 | 0.09613 | 0.19226 | 0.15564 | 122.2961 | 122.2824 | -0.19684 | -0.17395 | 122.0901 | 122.2229 | 122.081 | 122.1359
1916.7812 | 122.4701 | -122.1725 | 0.10986 | -0.018921 | 0.065933 | 0.01568 | 0.021617 | -0.002117 | -0.0012604 | 0.0015531 | -0.0015565 | 0.025289 | 0.018848 | 0.018532 | 0.00097195 | 0.018812 | 0.00021567 | -0.086975 | 0.09613 | -0.064087 | -0.045776 | 0.09613 | -0.041199 | 0.004578 | 0.022888 | 0.050354 | -0.045776 | 0.10071 | 0.1236 | 0.064087 | 0.1831 | 122.1085 | -0.013733 | -0.15564 | 122.2687 | 122.1771 | 122.1313 | 0.068665 | 0.022888 | 122.1268 | -0.059509 | -0.009155 | 122.2961 | 122.3557 | 122.2366 | 0.22888 | 0.10986 | 0.16022 | 0.018311 | 0.16937 | 0.14648 | 0.16022 | 0.09613 | 122.2687 | 122.2229 | -0.17395 | -0.15564 | 122.1268 | 122.2733 | 122.0856 | 122.1954
1918.5312 | 122.4976 | -122.1909 | 0.073242 | -0.011291 | 0.06401 | 0.014398 | 0.022257 | -0.0023306 | -0.0036102 | 0.00069849 | -0.0015565 | 0.022084 | 0.021198 | 0.0196 | -0.0037277 | 0.019239 | 0.00042947 | -0.050354 | 0.045776 | -0.045776 | 0.018311 | 0.17853 | 0.064087 | 0.086975 | 0.10071 | 0.050354 | -0.054932 | 0.091553 | 0.18768 | 0.14191 | 0.21057 | 122.1451 | -0.027466 | -0.054931 | 122.3694 | 122.2778 | 122.2549 | 0.13275 | 0.10986 | 122.1359 | -0.022888 | 0.018311 | 122.3785 | 122.4014 | 122.3328 | 0.2655 | 0.19684 | 0.2243 | 0.064087 | 0.24261 | 0.14649 | 0.091552 | 0.10529 | 122.2366 | 122.2412 | -0.11902 | -0.12817 | 122.2092 | 122.2824 | 122.1405 | 122.2916
1920.2188 | 122.374 | -122.2229 | 0.1236 | -0.011291 | 0.067642 | 0.014398 | 0.023753 | -0.0029714 | -0.0040374 | 0.0013395 | -0.0015565 | 0.024434 | 0.018634 | 0.01725 | -0.00095065 | 0.017957 | -0.0040567 | -0.10071 | 0.082397 | -0.086975 | -0.1236 | 0.013733 | -0.10071 | -0.050354 | -0.082397 | 0.09613 | -0.086975 | -0.018311 | 0.045776 | -0.059509 | 0.10071 | 122.1359 | -0.041199 | -0.24719 | 122.2366 | 122.1725 | 122.1222 | 0.036621 | -0.013733 | 122.1359 | -0.027466 | -0.14191 | 122.2687 | 122.3236 | 122.1634 | 0.18768 | 0.027466 | 0.10071 | -0.036621 | 0.13275 | 0.068664 | 0.16937 | 0.1831 | 122.3053 | 122.319 | -0.21057 | -0.21057 | 122.0993 | 122.2046 | 122.1222 | 122.1405
1921.9531 | 122.4518 | -122.1954 | 0.10529 | 0.0039673 | 0.065505 | 0.014825 | 0.020121 | -0.002117 | -0.0029694 | -0.00015591 | 0.0014953 | 0.022512 | 0.019489 | 0.017036 | -0.0024461 | 0.016889 | -0.00042513 | -0.064087 | 0.050354 | -0.045776 | -0.022888 | 0.13275 | -0.009155 | 0.032043 | 0.004578 | 0.050354 | -0.054932 | 0.036621 | 0.1236 | 0.041199 | 0.15106 | 122.1497 | -0.054932 | -0.12817 | 122.3282 | 122.2275 | 122.1863 | 0.077819 | 0.036621 | 122.1405 | -0.054932 | -0.068665 | 122.319 | 122.3465 | 122.2366 | 0.20599 | 0.096131 | 0.17853 | 0.022888 | 0.17853 | 0.091553 | 0.09613 | 0.10529 | 122.2458 | 122.2458 | -0.15106 | -0.16022 | 122.1725 | 122.2321 | 122.1313 | 122.2
1923.625 | 122.3785 | -122.2137 | 0.1236 | -0.011291 | 0.062942 | 0.014825 | 0.021403 | 0.00087375 | -0.0021148 | -0.00015591 | -0.0015565 | 0.024434 | 0.020557 | 0.018318 | -0.0030869 | 0.017103 | -0.0014931 | -0.09613 | 0.082397 | -0.073242 | -0.10986 | 0.050354 | -0.045776 | -0.022888 | -0.07782 | 0.07782 | -0.082397 | -0.054932 | 0.050354 | -0.027466 | 0.082397 | 122.1405 | -0.041199 | -0.23346 | 122.2641 | 122.1909 | 122.168 | 0.050354 | 0.027466 | 122.1313 | -0.045776 | -0.17853 | 122.2641 | 122.2961 | 122.1863 | 0.16479 | 0.054931 | 0.1236 | -0.036621 | 0.13275 | 0.027465 | 0.15564 | 0.16022 | 122.2961 | 122.2916 | -0.19684 | -0.20599 | 122.1039 | 122.1588 | 122.1176 | 122.1359
1925.3594 | 122.3694 | -122.2275 | 0.12817 | -0.011291 | 0.066787 | 0.01568 | 0.022898 | 0.001301 | -0.00040584 | -0.0012241 | -0.0015565 | 0.024434 | 0.020343 | 0.0089187 | 0.00033115 | 0.018171 | -0.0014931 | -0.091553 | 0.09613 | -0.086975 | -0.10529 | 0 | -0.11902 | -0.064087 | -0.082397 | 0.10986 | -0.068665 | -0.022888 | 0.009155 | -0.054932 | 0.091553 | 122.1405 | -0.032044 | -0.23346 | 122.2275 | 122.1634 | 122.1085 | 0.022888 | -0.032044 | 122.1588 | -0.018311 | -0.15106 | 122.2366 | 122.319 | 122.1725 | 0.16022 | 0.013733 | 0.086975 | -0.018311 | 0.07782 | 0.045777 | 0.1831 | 0.17853 | 122.3236 | 122.3373 | -0.21515 | -0.19684 | 122.1222 | 122.2046 | 122.1359 | 122.1451
1927.0469 | 122.4472 | -122.1863 | 0.10529 | -0.011291 | 0.066787 | 0.014612 | 0.021403 | -0.0010488 | -0.002542 | -0.00036951 | -0.0015565 | 0.022725 | 0.018634 | 0.014473 | -0.00052345 | 0.017103 | -0.0014931 | -0.082397 | 0.059509 | -0.045776 | -0.032043 | 0.10529 | -0.004578 | 0.036621 | -0.009155 | 0.041199 | -0.059509 | 0.027466 | 0.11444 | 0.045776 | 0.13733 | 122.1405 | -0.045777 | -0.13733 | 122.2916 | 122.2229 | 122.1817 | 0.082397 | 0.041198 | 122.1268 | -0.064087 | -0.07782 | 122.3007 | 122.3236 | 122.2321 | 0.19684 | 0.10528 | 0.15106 | 0.013733 | 0.17395 | 0.086975 | 0.10528 | 0.10071 | 122.2458 | 122.2275 | -0.15106 | -0.16479 | 122.1542 | 122.2137 | 122.1039 | 122.1771
1928.7969 | 122.4518 | -122.1909 | 0.10071 | -0.011291 | 0.063796 | 0.015466 | 0.021403 | 0.00044655 | -0.002542 | -0.0012241 | 0.0014953 | 0.021016 | 0.018848 | 0.02195 | 0.0013991 | 0.01753 | -0.0055521 | -0.073242 | 0.050354 | -0.054932 | -0.022888 | 0.11902 | -0.027466 | 0.050354 | 0 | 0.059509 | -0.059509 | 0.041199 | 0.11444 | 0.041199 | 0.13275 | 122.1359 | -0.050354 | -0.1236 | 122.3099 | 122.2412 | 122.1634 | 0.10529 | 0.027466 | 122.1313 | -0.041199 | -0.059509 | 122.3053 | 122.3236 | 122.2321 | 0.19226 | 0.10071 | 0.17395 | 0.032044 | 0.17395 | 0.10071 | 0.10529 | 0.11902 | 122.2412 | 122.2504 | -0.15564 | -0.16022 | 122.168 | 122.2321 | 122.1176 | 122.1909
1930.5469 | 122.4243 | -122.2275 | 0.1236 | 0.0039673 | 0.063583 | 0.016748 | 0.022685 | -0.0019034 | -0.003183 | 0.00069849 | 0.0045471 | 0.025716 | 0.016285 | 0.015541 | -0.0043687 | 0.016248 | -0.0010659 | -0.045776 | 0.082397 | -0.07782 | -0.036621 | 0.086975 | -0.018311 | 0 | 0.013733 | 0.073242 | -0.064087 | 0.036621 | 0.10071 | 0.009155 | 0.14191 | 122.1497 | -0.041199 | -0.16022 | 122.3145 | 122.2275 | 122.2092 | 0.07782 | 0.059509 | 122.1634 | -0.050354 | -0.086975 | 122.3282 | 122.3694 | 122.2366 | 0.20599 | 0.073242 | 0.16479 | 0.041199 | 0.1648 | 0.10071 | 0.16022 | 0.13733 | 122.3099 | 122.3007 | -0.20142 | -0.18768 | 122.1909 | 122.2641 | 122.1817 | 122.2412
1932.2812 | 122.4518 | -122.2275 | 0.10071 | -0.0036622 | 0.065078 | 0.015466 | 0.020121 | -0.00040805 | -0.0036102 | -0.00058311 | -0.0015565 | 0.022298 | 0.020343 | 0.015327 | -0.0011643 | 0.016889 | -0.0023477 | -0.022888 | 0.050354 | -0.050354 | -0.004578 | 0.15564 | 0.050354 | 0.073242 | 0.032043 | 0.059509 | -0.050354 | 0.022888 | 0.13275 | 0.054932 | 0.14191 | 122.1771 | -0.050354 | -0.10529 | 122.3831 | 122.3007 | 122.2778 | 0.1236 | 0.10071 | 122.1771 | -0.041199 | -0.07782 | 122.3602 | 122.3694 | 122.2824 | 0.19226 | 0.10529 | 0.20599 | 0.045776 | 0.18311 | 0.073242 | 0.10071 | 0.10986 | 122.2778 | 122.287 | -0.15106 | -0.15106 | 122.2229 | 122.2504 | 122.2046 | 122.2595
1934.0156 | 122.493 | -122.2046 | 0.086975 | 0.0039673 | 0.065292 | 0.016107 | 0.022257 | 0.00301 | -0.0027556 | -0.0016513 | -0.0046081 | 0.022725 | 0.018848 | 0.019386 | -0.00095065 | 0.01753 | -0.0021341 | -0.07782 | 0.064087 | -0.041199 | -0.032043 | 0.10529 | 0 | 0.022888 | 0.004578 | 0.059509 | -0.059509 | 0.036621 | 0.14191 | 0.082397 | 0.17395 | 122.1634 | -0.022888 | -0.11902 | 122.3099 | 122.2275 | 122.2046 | 0.064087 | 0.041199 | 122.1451 | -0.027466 | -0.050354 | 122.3465 | 122.3785 | 122.287 | 0.23346 | 0.14191 | 0.14649 | 0.009156 | 0.20142 | 0.09613 | 0.10529 | 0.11902 | 122.2687 | 122.2641 | -0.12817 | -0.14648 | 122.1725 | 122.2412 | 122.1268 | 122.2092
1935.7812 | 122.3969 | -122.2366 | 0.10529 | 0.011597 | 0.066146 | 0.013971 | 0.022685 | 0.0010874 | -0.00019224 | -0.0037875 | -0.0046081 | 0.025075 | 0.018421 | 0.012123 | -0.0028733 | 0.016675 | -0.0034159 | -0.091553 | 0.091553 | -0.10071 | -0.10071 | 0.027466 | -0.073242 | -0.027466 | -0.086975 | 0.09613 | -0.082397 | -0.032043 | 0.045776 | -0.022888 | 0.09613 | 122.1359 | -0.013733 | -0.20599 | 122.2641 | 122.2092 | 122.1634 | 0.073242 | 0.027466 | 122.1542 | -0.009156 | -0.13733 | 122.2824 | 122.3328 | 122.2137 | 0.17853 | 0.059509 | 0.12817 | 0 | 0.12817 | 0.050354 | 0.19226 | 0.17853 | 122.3282 | 122.3328 | -0.20599 | -0.18768 | 122.1359 | 122.2046 | 122.1451 | 122.1497
1937.4531 | 122.5113 | -122.1863 | 0.073242 | -0.0036622 | 0.065719 | 0.016107 | 0.023753 | -0.002117 | -0.0051056 | -0.0050693 | -0.0015565 | 0.025075 | 0.020557 | 0.020882 | 0.0037491 | 0.017957 | -0.0021341 | -0.050354 | 0.064087 | -0.064087 | -0.013733 | 0.15564 | 0.004578 | 0.036621 | 0.045776 | 0.050354 | -0.041199 | 0.10071 | 0.14648 | 0.07782 | 0.21057 | 122.1222 | -0.009155 | -0.086975 | 122.3419 | 122.2229 | 122.1909 | 0.10071 | 0.068665 | 122.1451 | -0.022888 | 0.027466 | 122.3328 | 122.3969 | 122.2641 | 0.25177 | 0.11902 | 0.21973 | 0.050354 | 0.18768 | 0.14191 | 0.12817 | 0.091553 | 122.2504 | 122.2366 | -0.13733 | -0.11444 | 122.1725 | 122.287 | 122.1359 | 122.2321
1939.1875 | 122.4701 | -122.2229 | 0.082397 | -0.011291 | 0.065292 | 0.01803 | 0.023539 | -0.00083525 | -0.0016876 | -0.0033603 | 0.0014953 | 0.023366 | 0.019489 | 0.023659 | 0.00097195 | 0.019452 | -0.0023477 | -0.027466 | 0.041199 | -0.059509 | 0 | 0.16937 | 0 | 0.036621 | 0.045776 | 0.059509 | -0.032043 | 0.045776 | 0.1236 | 0.041199 | 0.16022 | 122.1634 | -0.041198 | -0.082397 | 122.3923 | 122.2595 | 122.2229 | 0.09613 | 0.059509 | 122.1909 | -0.022888 | -0.036621 | 122.3465 | 122.3831 | 122.2641 | 0.19226 | 0.073242 | 0.22888 | 0.059509 | 0.15564 | 0.077819 | 0.10071 | 0.091552 | 122.2641 | 122.2824 | -0.14191 | -0.11444 | 122.2229 | 122.2687 | 122.1954 | 122.2687
1940.9531 | 122.4106 | -122.2275 | 0.11902 | 0.0039673 | 0.068496 | 0.016962 | 0.023539 | 0.0027964 | -0.0010468 | 5.7688e-05 | -0.0015565 | 0.025075 | 0.020557 | 0.0099869 | 0.00011755 | 0.01753 | -0.00021153 | -0.045776 | 0.073242 | -0.059509 | -0.054932 | 0.086975 | -0.036621 | -0.009155 | -0.013733 | 0.068665 | -0.082397 | 0.004578 | 0.054932 | -0.045776 | 0.091553 | 122.168 | -0.045777 | -0.17395 | 122.3145 | 122.2183 | 122.1909 | 0.050354 | 0.022888 | 122.1451 | -0.050354 | -0.11444 | 122.2824 | 122.319 | 122.1817 | 0.17395 | 0.036621 | 0.14648 | 0.004577 | 0.13733 | 0.086975 | 0.13275 | 0.15106 | 122.3007 | 122.2961 | -0.17853 | -0.20142 | 122.1725 | 122.2321 | 122.1817 | 122.2137
1942.625 | 122.5204 | -122.1771 | 0.07782 | 0.0039673 | 0.065505 | 0.018457 | 0.020976 | -0.0010488 | -0.0012604 | -0.0018649 | -0.0046081 | 0.02358 | 0.019916 | 0.015755 | 0.0020401 | 0.018812 | -0.0042703 | -0.009155 | 0.041199 | -0.036621 | 0.018311 | 0.1831 | 0.018311 | 0.073242 | 0.091553 | 0.045776 | -0.027466 | 0.10529 | 0.17853 | 0.086975 | 0.19684 | 122.1405 | -0.036621 | -0.059509 | 122.3602 | 122.2504 | 122.1954 | 0.10986 | 0.054932 | 122.1497 | -0.032044 | 0.027466 | 122.3557 | 122.374 | 122.2641 | 0.2243 | 0.11444 | 0.21973 | 0.054932 | 0.20599 | 0.13275 | 0.07782 | 0.073242 | 122.2183 | 122.2229 | -0.11444 | -0.10529 | 122.1954 | 122.2824 | 122.168 | 122.2687
1944.2969 | 122.5159 | -122.2321 | 0.10071 | -0.011291 | 0.066574 | 0.015039 | 0.022471 | -0.003826 | 0.00023496 | -0.0054965 | -0.0015565 | 0.020162 | 0.019275 | 0.023445 | -0.0011643 | 0.019025 | 0.0012839 | -0.07782 | 0.059509 | -0.059509 | -0.036621 | 0.1236 | 0.027466 | 0.054932 | 0.041199 | 0.064087 | -0.045776 | 0.059509 | 0.17395 | 0.11444 | 0.21057 | 122.1725 | -0.041199 | -0.13733 | 122.3557 | 122.287 | 122.2595 | 0.11444 | 0.086975 | 122.1863 | -0.036621 | -0.041199 | 122.406 | 122.4426 | 122.3465 | 0.25635 | 0.16022 | 0.1831 | 0.022888 | 0.21973 | 0.10528 | 0.11902 | 0.10986 | 122.2916 | 122.2961 | -0.16022 | -0.14648 | 122.1954 | 122.2916 | 122.1542 | 122.2733
1946.0469 | 122.3969 | -122.2458 | 0.10986 | -0.0036622 | 0.065719 | 0.016748 | 0.023753 | -0.00062165 | -0.0023284 | 0.00048489 | -0.0015565 | 0.025929 | 0.020771 | 0.013405 | -0.0015915 | 0.016462 | -0.0029885 | -0.045776 | 0.068665 | -0.07782 | -0.041199 | 0.082397 | -0.064087 | -0.027466 | -0.027466 | 0.091553 | -0.068665 | 0 | 0.050354 | -0.045776 | 0.10529 | 122.168 | -0.041198 | -0.15106 | 122.3282 | 122.2183 | 122.1817 | 0.050354 | 0.013733 | 122.1771 | -0.01831 | -0.10986 | 122.2961 | 122.3511 | 122.2 | 0.17395 | 0.022889 | 0.16022 | 0.036621 | 0.11902 | 0.068665 | 0.14649 | 0.16022 | 122.3145 | 122.3373 | -0.18768 | -0.17853 | 122.2046 | 122.2458 | 122.2 | 122.2183
1947.7344 | 122.493 | -122.2137 | 0.086975 | -0.0036622 | 0.06401 | 0.015894 | 0.021189 | -0.0025442 | -0.0036102 | 0.0013395 | -0.0046081 | 0.023152 | 0.019703 | 0.016823 | -0.00073705 | 0.018812 | -0.0021341 | -0.068665 | 0.059509 | -0.054932 | -0.045776 | 0.10986 | -0.009155 | 0.022888 | 0.004578 | 0.064087 | -0.050354 | 0.036621 | 0.11444 | 0.036621 | 0.15106 | 122.1588 | -0.027466 | -0.13275 | 122.3236 | 122.2366 | 122.2046 | 0.07782 | 0.045777 | 122.1634 | -0.022888 | -0.050354 | 122.3282 | 122.3648 | 122.2504 | 0.20142 | 0.086975 | 0.16479 | 0.009156 | 0.16479 | 0.086975 | 0.11444 | 0.11444 | 122.2733 | 122.2778 | -0.14191 | -0.13733 | 122.168 | 122.2504 | 122.1451 | 122.2183
1949.4688 | 122.3877 | -122.2778 | 0.13275 | -0.0036622 | 0.067001 | 0.015039 | 0.023753 | -0.00062165 | -0.0023284 | -0.0016513 | 0.0045471 | 0.024861 | 0.018421 | 0.015327 | 0.00033115 | 0.019452 | -0.0044839 | -0.091553 | 0.07782 | -0.068665 | -0.091553 | 0.018311 | -0.10986 | -0.059509 | -0.10986 | 0.086975 | -0.068665 | -0.032043 | 0.013733 | -0.086975 | 0.07782 | 122.2092 | -0.054931 | -0.2243 | 122.2961 | 122.2183 | 122.168 | 0.009156 | -0.041198 | 122.2092 | -0.045776 | -0.16479 | 122.2916 | 122.3557 | 122.1909 | 0.14649 | -0.01831 | 0.086976 | -0.022888 | 0.082398 | 0.036622 | 0.14649 | 0.15564 | 122.3557 | 122.3648 | -0.20142 | -0.20142 | 122.1863 | 122.2458 | 122.1863 | 122.168
1951.1562 | 122.4289 | -122.2687 | 0.11444 | 0.011597 | 0.067855 | 0.016107 | 0.024607 | 0.00087375 | -0.0029694 | -0.0031467 | -0.0046081 | 0.025075 | 0.019062 | 0.018745 | -0.0013779 | 0.018171 | -0.00021153 | -0.045776 | 0.07782 | -0.059509 | -0.059509 | 0.091553 | -0.041199 | -0.018311 | -0.013733 | 0.09613 | -0.073242 | 0 | 0.054932 | -0.022888 | 0.10986 | 122.2092 | -0.036621 | -0.17395 | 122.3602 | 122.2504 | 122.2275 | 0.041198 | 0.01831 | 122.1954 | -0.018311 | -0.11444 | 122.3236 | 122.3785 | 122.2458 | 0.18311 | 0.050354 | 0.15106 | 0 | 0.12817 | 0.073242 | 0.13733 | 0.16937 | 122.3465 | 122.3648 | -0.17395 | -0.18768 | 122.2092 | 122.2687 | 122.2229 | 122.2549
1952.9062 | 122.5388 | -122.2229 | 0.091553 | -0.011291 | 0.06401 | 0.014612 | 0.019908 | -0.0019034 | -0.0033966 | -0.0022921 | -0.0015565 | 0.022512 | 0.021198 | 0.018745 | -0.0033005 | 0.018171 | -0.0025613 | -0.059509 | 0.054932 | -0.064087 | 0.013733 | 0.19226 | 0.068665 | 0.082397 | 0.10071 | 0.050354 | -0.059509 | 0.10071 | 0.21057 | 0.14191 | 0.21973 | 122.1588 | -0.036621 | -0.07782 | 122.4152 | 122.3053 | 122.2916 | 0.14648 | 0.13275 | 122.1634 | -0.041199 | 0.009155 | 122.4335 | 122.4426 | 122.3648 | 0.27924 | 0.20142 | 0.25635 | 0.07782 | 0.27008 | 0.16022 | 0.11902 | 0.10986 | 122.2778 | 122.2733 | -0.15564 | -0.15106 | 122.2366 | 122.3236 | 122.1634 | 122.3236
1954.6562 | 122.5204 | -122.2 | 0.10529 | -0.0036622 | 0.065292 | 0.016107 | 0.023112 | -0.0012624 | -0.003183 | -0.0035739 | -0.0046081 | 0.022939 | 0.019062 | 0.019173 | 0.0024673 | 0.019025 | 0.00064307 | -0.068665 | 0.064087 | -0.064087 | -0.032043 | 0.11444 | -0.022888 | 0.022888 | 0.036621 | 0.045776 | -0.050354 | 0.10529 | 0.14191 | 0.073242 | 0.19684 | 122.1359 | -0.041199 | -0.13733 | 122.3145 | 122.2229 | 122.1771 | 0.086975 | 0.041199 | 122.1497 | -0.05951 | 0 | 122.3419 | 122.3969 | 122.2733 | 0.24719 | 0.1236 | 0.17853 | 0.032044 | 0.19226 | 0.15564 | 0.12817 | 0.09613 | 122.2641 | 122.2458 | -0.16937 | -0.15564 | 122.168 | 122.3053 | 122.1313 | 122.2366
1956.3438 | 122.4564 | -122.2504 | 0.13275 | -0.011291 | 0.065719 | 0.016748 | 0.023539 | -0.00083525 | -0.0040374 | -0.0014377 | -0.0046081 | 0.025502 | 0.021412 | 0.013405 | 0.00011755 | 0.01753 | 0.00021567 | -0.045776 | 0.068665 | -0.068665 | -0.027466 | 0.1236 | -0.018311 | -0.004578 | -0.004578 | 0.07782 | -0.07782 | 0.027466 | 0.091553 | 0.013733 | 0.13275 | 122.1817 | -0.064086 | -0.16022 | 122.374 | 122.2458 | 122.2321 | 0.064087 | 0.050354 | 122.1725 | -0.054931 | -0.10529 | 122.3419 | 122.3831 | 122.2641 | 0.21057 | 0.091553 | 0.19226 | 0.041199 | 0.16937 | 0.10529 | 0.13733 | 0.15564 | 122.319 | 122.3282 | -0.20142 | -0.21057 | 122.2229 | 122.2778 | 122.2046 | 122.2458
1958.0938 | 122.4152 | -122.2778 | 0.11902 | -0.018921 | 0.064651 | 0.013971 | 0.021617 | -0.0012624 | -0.004251 | -0.00036951 | -0.0046081 | 0.024434 | 0.020771 | 0.016182 | -0.0050095 | 0.01753 | -0.0019205 | -0.086975 | 0.073242 | -0.082397 | -0.09613 | 0.073242 | -0.041199 | -0.032043 | -0.082397 | 0.091553 | -0.082397 | -0.036621 | 0.059509 | -0.013733 | 0.068665 | 122.1954 | -0.045777 | -0.21515 | 122.3511 | 122.2458 | 122.2366 | 0.050354 | 0.041198 | 122.1954 | -0.027466 | -0.15564 | 122.3373 | 122.3465 | 122.2641 | 0.15106 | 0.068664 | 0.15564 | -0.013733 | 0.14191 | 0.045776 | 0.15564 | 0.17395 | 122.3511 | 122.3694 | -0.20142 | -0.20142 | 122.1817 | 122.2412 | 122.1909 | 122.1954
1959.8438 | 122.5388 | -122.2504 | 0.073242 | -0.011291 | 0.06636 | 0.017389 | 0.023539 | -0.0012624 | -0.0010468 | 5.7688e-05 | -0.0015565 | 0.022084 | 0.019062 | 0.018959 | 0.0026809 | 0.018812 | -0.0040567 | -0.027466 | 0.054932 | -0.036621 | 0.036621 | 0.17853 | 0.022888 | 0.050354 | 0.086975 | 0.045776 | -0.022888 | 0.10071 | 0.17853 | 0.09613 | 0.19226 | 122.2137 | -0.01831 | -0.036621 | 122.4289 | 122.3007 | 122.2733 | 0.086975 | 0.059509 | 122.2275 | -0.027466 | 0.027466 | 122.4289 | 122.4426 | 122.3465 | 0.21515 | 0.11902 | 0.21515 | 0.073242 | 0.20142 | 0.1236 | 0.091553 | 0.068664 | 122.3053 | 122.2961 | -0.10986 | -0.09613 | 122.287 | 122.3511 | 122.2229 | 122.3373
1961.5312 | 122.4609 | -122.2458 | 0.09613 | -0.018921 | 0.065078 | 0.016107 | 0.022685 | -0.00062165 | -0.0012604 | -0.0018649 | -0.0015565 | 0.022298 | 0.022693 | 0.0084915 | 0.00011755 | 0.019452 | -0.00063873 | -0.050354 | 0.091553 | -0.064087 | -0.050354 | 0.10071 | -0.013733 | 0.009155 | -0.004578 | 0.086975 | -0.059509 | 0.032043 | 0.11444 | 0.018311 | 0.14191 | 122.1817 | -0.004577 | -0.14648 | 122.3465 | 122.2549 | 122.2321 | 0.073242 | 0.050354 | 122.1863 | -0.009155 | -0.064087 | 122.3602 | 122.3877 | 122.2641 | 0.20142 | 0.07782 | 0.1648 | 0.013733 | 0.17395 | 0.091552 | 0.15564 | 0.14648 | 122.3373 | 122.3328 | -0.16022 | -0.15564 | 122.1954 | 122.2778 | 122.1954 | 122.2412
1963.2812 | 122.4701 | -122.2549 | 0.10529 | 0.0039673 | 0.067001 | 0.016962 | 0.023326 | -0.00062165 | -0.0019012 | -0.00015591 | -0.0015565 | 0.025716 | 0.019916 | 0.015541 | -0.0011643 | 0.01753 | 0.0029929 | -0.068665 | 0.07782 | -0.086975 | -0.073242 | 0.086975 | -0.027466 | 0 | -0.027466 | 0.07782 | -0.050354 | 0.022888 | 0.091553 | 0.004578 | 0.13275 | 122.168 | -0.027466 | -0.17853 | 122.3419 | 122.2549 | 122.2275 | 0.086975 | 0.059509 | 122.2046 | -0.027466 | -0.082398 | 122.3465 | 122.3877 | 122.2595 | 0.18311 | 0.054932 | 0.17395 | 0.013733 | 0.14191 | 0.073242 | 0.16479 | 0.12817 | 122.3328 | 122.3328 | -0.19226 | -0.15564 | 122.1817 | 122.2778 | 122.1863 | 122.2275
1965.0312 | 122.4747 | -122.2641 | 0.091553 | -0.02655 | 0.068283 | 0.013757 | 0.022471 | -0.0016898 | -0.0040374 | -0.0025057 | 0.0014953 | 0.024648 | 0.020343 | 0.0048599 | -0.0013779 | 0.01753 | -0.0019205 | -0.050354 | 0.073242 | -0.068665 | -0.027466 | 0.10529 | -0.022888 | 0.004578 | 0 | 0.086975 | -0.059509 | 0.022888 | 0.11902 | 0.018311 | 0.1236 | 122.1954 | -0.018311 | -0.11902 | 122.3694 | 122.2687 | 122.2412 | 0.073243 | 0.045777 | 122.2046 | -0.004578 | -0.068665 | 122.3831 | 122.3877 | 122.2824 | 0.1831 | 0.07782 | 0.17395 | 0.041199 | 0.17853 | 0.082397 | 0.14191 | 0.14648 | 122.3373 | 122.3511 | -0.16022 | -0.15106 | 122.2366 | 122.287 | 122.2137 | 122.2641
1966.7188 | 122.4609 | -122.2916 | 0.1236 | -0.011291 | 0.064437 | 0.013757 | 0.023966 | -0.0036124 | -0.0046782 | 5.7688e-05 | 0.0014953 | 0.024648 | 0.018421 | 0.011696 | -0.0024461 | 0.01753 | -0.0044839 | -0.086975 | 0.09613 | -0.10071 | -0.10071 | 0.018311 | -0.050354 | -0.018311 | -0.086975 | 0.10071 | -0.086975 | -0.032043 | 0.07782 | -0.009155 | 0.10071 | 122.1909 | -0.027466 | -0.2243 | 122.3099 | 122.2733 | 122.2412 | 0.082397 | 0.050354 | 122.2046 | -0.022888 | -0.15564 | 122.3694 | 122.3923 | 122.2824 | 0.18768 | 0.07782 | 0.11902 | 0 | 0.16479 | 0.054932 | 0.19684 | 0.18768 | 122.3877 | 122.3923 | -0.2243 | -0.21057 | 122.1909 | 122.2595 | 122.2046 | 122.2046
1968.4688 | 122.5479 | -122.2046 | 0.09613 | 0.011597 | 0.067428 | 0.016962 | 0.020976 | 0.0017282 | 0.0013032 | -0.00015591 | 0.0014953 | 0.021871 | 0.018848 | 0.017677 | 0.0016129 | 0.021802 | -0.0023477 | -0.022888 | 0.032043 | -0.018311 | 0.018311 | 0.17395 | 0.036621 | 0.050354 | 0.07782 | 0.054932 | -0.032043 | 0.082397 | 0.16937 | 0.091553 | 0.20142 | 122.1863 | -0.064087 | -0.077819 | 122.3785 | 122.2549 | 122.2412 | 0.068665 | 0.054932 | 122.1725 | -0.041198 | -0.013733 | 122.374 | 122.406 | 122.2961 | 0.23346 | 0.1236 | 0.19226 | 0.036622 | 0.20142 | 0.11444 | 0.050354 | 0.086975 | 122.2366 | 122.2595 | -0.11444 | -0.12817 | 122.2229 | 122.287 | 122.1817 | 122.2824
1970.1562 | 122.5433 | -122.2412 | 0.082397 | -0.011291 | 0.063369 | 0.014185 | 0.021189 | -0.0051076 | -0.0029694 | -0.00079691 | -0.0015565 | 0.019094 | 0.019489 | 0.021522 | -0.0022325 | 0.018171 | -0.0034159 | -0.032043 | 0.036621 | -0.045776 | 0.036621 | 0.21515 | 0.082397 | 0.091553 | 0.068665 | 0.059509 | -0.036621 | 0.091553 | 0.21057 | 0.1236 | 0.18768 | 122.1954 | -0.045776 | -0.045776 | 122.4564 | 122.3328 | 122.3236 | 0.13733 | 0.12817 | 122.2046 | -0.022888 | 0.009156 | 122.4518 | 122.4289 | 122.3648 | 0.2243 | 0.16022 | 0.26093 | 0.082397 | 0.24719 | 0.12817 | 0.082397 | 0.09613 | 122.2778 | 122.3007 | -0.12817 | -0.11902 | 122.2778 | 122.3328 | 122.2092 | 122.3099
1971.9062 | 122.4152 | -122.2778 | 0.13275 | -0.011291 | 0.064437 | 0.015253 | 0.02418 | 0.00066015 | -0.0010468 | -0.0037875 | -0.0076599 | 0.024861 | 0.017566 | 0.011696 | -9.605e-05 | 0.017957 | -0.0012795 | -0.10071 | 0.091553 | -0.086975 | -0.10986 | 0 | -0.10986 | -0.068665 | -0.10071 | 0.091553 | -0.082397 | -0.041199 | 0.022888 | -0.059509 | 0.086975 | 122.1909 | -0.041198 | -0.24261 | 122.2778 | 122.2092 | 122.168 | 0.01831 | -0.022888 | 122.1954 | -0.041198 | -0.17395 | 122.3007 | 122.3648 | 122.2183 | 0.16937 | 0.022888 | 0.086975 | -0.022888 | 0.10528 | 0.041198 | 0.17853 | 0.17395 | 122.3694 | 122.3694 | -0.21973 | -0.21515 | 122.168 | 122.2366 | 122.1771 | 122.1771
1973.6562 | 122.5662 | -122.2641 | 0.09613 | 0.0039673 | 0.066787 | 0.017816 | 0.023112 | -0.0012624 | -0.0019012 | -0.0025057 | -0.0015565 | 0.022725 | 0.019916 | 0.016609 | 0.0013991 | 0.018171 | -0.0023477 | -0.022888 | 0.041199 | -0.041199 | 0.045776 | 0.19684 | 0.027466 | 0.064087 | 0.086975 | 0.050354 | -0.036621 | 0.10071 | 0.17395 | 0.086975 | 0.19684 | 122.2229 | -0.054931 | -0.050354 | 122.4609 | 122.3282 | 122.2916 | 0.10529 | 0.068665 | 122.2275 | -0.045776 | 0.004578 | 122.438 | 122.4609 | 122.3511 | 0.23346 | 0.1236 | 0.23804 | 0.086975 | 0.21057 | 0.13733 | 0.082398 | 0.086975 | 122.3053 | 122.3145 | -0.13733 | -0.13275 | 122.3099 | 122.3648 | 122.2412 | 122.3511
1975.4062 | 122.4335 | -122.2961 | 0.11902 | 0.0039673 | 0.065933 | 0.015039 | 0.025035 | 0.00023275 | -0.0019012 | -0.0016513 | -0.0015565 | 0.028066 | 0.02013 | 0.013832 | -0.00052345 | 0.01753 | 2.068e-06 | -0.082397 | 0.073242 | -0.068665 | -0.082397 | 0.041199 | -0.091553 | -0.045776 | -0.059509 | 0.073242 | -0.07782 | -0.018311 | 0.036621 | -0.082397 | 0.091553 | 122.2275 | -0.045777 | -0.20142 | 122.3373 | 122.2504 | 122.2046 | 0.022889 | -0.022888 | 122.2183 | -0.045777 | -0.13733 | 122.3328 | 122.3877 | 122.2137 | 0.16937 | -0.004577 | 0.10986 | -0.013732 | 0.11444 | 0.059509 | 0.14191 | 0.15106 | 122.3694 | 122.3694 | -0.18768 | -0.19684 | 122.2137 | 122.2778 | 122.2137 | 122.2366
1977.0938 | 122.5708 | -122.2366 | 0.086975 | -0.0036622 | 0.06401 | 0.01333 | 0.022471 | 0.00066015 | -0.003183 | -0.0014377 | -0.0046081 | 0.023366 | 0.019275 | 0.019173 | -0.0028733 | 0.018812 | -0.0014931 | -0.068665 | 0.050354 | -0.054932 | 0.004578 | 0.16022 | 0.041199 | 0.086975 | 0.07782 | 0.050354 | -0.050354 | 0.086975 | 0.18768 | 0.11902 | 0.21515 | 122.1817 | -0.036621 | -0.082397 | 122.3969 | 122.3236 | 122.2778 | 0.14191 | 0.096131 | 122.1863 | -0.036621 | 0 | 122.4243 | 122.4518 | 122.3557 | 0.2655 | 0.16937 | 0.21515 | 0.05951 | 0.23804 | 0.13733 | 0.10529 | 0.10071 | 122.287 | 122.287 | -0.14191 | -0.13733 | 122.2412 | 122.3236 | 122.168 | 122.3145
1978.8281 | 122.525 | -122.2595 | 0.10529 | -0.0036622 | 0.064651 | 0.015894 | 0.020976 | 0.0015146 | -0.0046782 | -0.00079691 | -0.0015565 | 0.022939 | 0.021625 | 0.017464 | -0.0011643 | 0.015394 | -0.00085233 | -0.07782 | 0.064087 | -0.050354 | -0.054932 | 0.13275 | -0.013733 | 0.013733 | -0.018311 | 0.059509 | -0.045776 | 0.022888 | 0.10986 | 0.036621 | 0.15564 | 122.2092 | -0.041199 | -0.16022 | 122.3923 | 122.2733 | 122.2458 | 0.064087 | 0.036621 | 122.2137 | -0.045777 | -0.082398 | 122.3694 | 122.4152 | 122.2961 | 0.20142 | 0.082397 | 0.18311 | -0.004578 | 0.15564 | 0.068664 | 0.11444 | 0.10528 | 122.3236 | 122.319 | -0.15564 | -0.15106 | 122.2046 | 122.2824 | 122.1817 | 122.2412
1980.5781 | 122.493 | -122.2824 | 0.11902 | 0.0039673 | 0.069564 | 0.015253 | 0.022471 | 0.00044655 | -0.0029694 | 0.00048489 | -0.0046081 | 0.025289 | 0.018207 | 0.012337 | -0.00052345 | 0.016248 | -0.0040567 | -0.041199 | 0.086975 | -0.059509 | -0.045776 | 0.10986 | -0.018311 | 0.009155 | 0.022888 | 0.073242 | -0.073242 | 0.041199 | 0.10529 | 0.018311 | 0.16022 | 122.2229 | -0.032044 | -0.16479 | 122.3923 | 122.2916 | 122.2641 | 0.068664 | 0.041198 | 122.2092 | -0.045777 | -0.07782 | 122.3877 | 122.4426 | 122.3007 | 0.23346 | 0.091553 | 0.16937 | 0.013733 | 0.17853 | 0.11444 | 0.14648 | 0.14648 | 122.3694 | 122.3557 | -0.17853 | -0.19226 | 122.2366 | 122.3236 | 122.2412 | 122.3053
1982.2656 | 122.5388 | -122.2641 | 0.07782 | 0.0039673 | 0.066574 | 0.016962 | 0.022471 | 0.0025828 | -0.003183 | -0.00058311 | -0.0046081 | 0.021871 | 0.017353 | 0.018104 | 0.00011755 | 0.016462 | 0.0017111 | -0.054932 | 0.045776 | -0.041199 | 0.013733 | 0.18768 | 0.022888 | 0.064087 | 0.068665 | 0.045776 | -0.036621 | 0.050354 | 0.1236 | 0.050354 | 0.15106 | 122.2229 | -0.032044 | -0.064087 | 122.4518 | 122.3282 | 122.287 | 0.10529 | 0.064087 | 122.2275 | -0.032044 | -0.027466 | 122.3877 | 122.4152 | 122.3145 | 0.18768 | 0.086975 | 0.22888 | 0.054932 | 0.16022 | 0.086975 | 0.086975 | 0.082397 | 122.3099 | 122.3099 | -0.11902 | -0.11444 | 122.2778 | 122.3145 | 122.2092 | 122.3328
1984 | 122.5525 | -122.2641 | 0.10071 | -0.0036622 | 0.062728 | 0.015039 | 0.020762 | -0.00040805 | -0.0019012 | -0.0020785 | -0.0015565 | 0.022512 | 0.019062 | 0.017464 | -0.00052345 | 0.018171 | 2.068e-06 | -0.064087 | 0.045776 | -0.050354 | -0.027466 | 0.1236 | 0.009155 | 0.022888 | 0.022888 | 0.054932 | -0.059509 | 0.045776 | 0.15564 | 0.082397 | 0.1831 | 122.2137 | -0.054932 | -0.12817 | 122.3877 | 122.287 | 122.2733 | 0.073242 | 0.059509 | 122.2046 | -0.045776 | -0.054932 | 122.4197 | 122.4472 | 122.3465 | 0.24261 | 0.14191 | 0.17395 | 0.022888 | 0.21515 | 0.10528 | 0.09613 | 0.11444 | 122.3099 | 122.319 | -0.15106 | -0.16022 | 122.2366 | 122.3099 | 122.2 | 122.287
1985.6719 | 122.4472 | -122.2778 | 0.10986 | -0.011291 | 0.066787 | 0.015039 | 0.023966 | -0.00062165 | -0.002542 | -0.0057101 | -0.0015565 | 0.024648 | 0.020343 | 0.014686 | 0.00054475 | 0.016675 | -0.0023477 | -0.086975 | 0.086975 | -0.073242 | -0.11902 | -0.009155 | -0.11902 | -0.091553 | -0.082397 | 0.09613 | -0.082397 | -0.018311 | 0.022888 | -0.073242 | 0.10529 | 122.2046 | -0.022888 | -0.22888 | 122.2687 | 122.1863 | 122.1588 | -0.018311 | -0.045777 | 122.1954 | -0.013733 | -0.12817 | 122.3007 | 122.3831 | 122.2046 | 0.18768 | 0.009155 | 0.064087 | -0.045777 | 0.10528 | 0.064086 | 0.16022 | 0.17853 | 122.3648 | 122.374 | -0.18311 | -0.19226 | 122.1588 | 122.2595 | 122.1909 | 122.1954
1987.4219 | 122.5296 | -122.2641 | 0.09613 | 0.0039673 | 0.065078 | 0.016962 | 0.022257 | -0.0023306 | -0.0010468 | 0.0013395 | 0.0014953 | 0.024007 | 0.019275 | 0.020454 | -0.00095065 | 0.018598 | 2.068e-06 | -0.027466 | 0.054932 | -0.027466 | 0 | 0.1831 | 0.004578 | 0.054932 | 0.073242 | 0.064087 | -0.050354 | 0.068665 | 0.13733 | 0.064087 | 0.15106 | 122.2366 | -0.041198 | -0.09613 | 122.4472 | 122.319 | 122.2687 | 0.082398 | 0.032044 | 122.2137 | -0.032043 | -0.027465 | 122.4014 | 122.4152 | 122.3282 | 0.20142 | 0.11444 | 0.21057 | 0.027466 | 0.18768 | 0.11902 | 0.082398 | 0.11444 | 122.319 | 122.3282 | -0.1236 | -0.14648 | 122.2641 | 122.3328 | 122.2366 | 122.3373
1989.1094 | 122.5479 | -122.3099 | 0.10529 | -0.011291 | 0.066574 | 0.014398 | 0.019267 | -0.00062165 | -0.0029694 | -0.0025057 | -0.0015565 | 0.024221 | 0.019916 | 0.016823 | -0.0026597 | 0.018812 | -0.0025613 | -0.013733 | 0.041199 | -0.041199 | 0.027466 | 0.17853 | 0.059509 | 0.068665 | 0.045776 | 0.068665 | -0.045776 | 0.054932 | 0.16479 | 0.086975 | 0.16479 | 122.2687 | -0.064087 | -0.07782 | 122.4884 | 122.3785 | 122.3694 | 0.10986 | 0.10071 | 122.2641 | -0.036621 | -0.050354 | 122.4747 | 122.4747 | 122.3969 | 0.21057 | 0.13275 | 0.21973 | 0.068665 | 0.21057 | 0.10071 | 0.082398 | 0.11444 | 122.3511 | 122.3785 | -0.14649 | -0.15106 | 122.3373 | 122.3648 | 122.2961 | 122.3557
1990.8594 | 122.5388 | -122.2549 | 0.082397 | -0.0036622 | 0.066787 | 0.017603 | 0.021617 | 0.00044655 | -0.0016876 | 0.0019803 | -0.0015565 | 0.024648 | 0.022052 | 0.018532 | 0.0018265 | 0.018598 | -0.0034159 | -0.022888 | 0.013733 | -0.032043 | 0.022888 | 0.17853 | 0.018311 | 0.068665 | 0.091553 | 0.050354 | -0.041199 | 0.07782 | 0.15564 | 0.064087 | 0.16937 | 122.2229 | -0.068664 | -0.059509 | 122.4335 | 122.3236 | 122.2733 | 0.10071 | 0.050354 | 122.2137 | -0.032043 | -0.004577 | 122.4106 | 122.4243 | 122.319 | 0.21057 | 0.10529 | 0.21057 | 0.054931 | 0.19684 | 0.11902 | 0.045776 | 0.091553 | 122.2687 | 122.3053 | -0.11444 | -0.1236 | 122.2778 | 122.3328 | 122.2321 | 122.3465
1992.6094 | 122.5891 | -122.2687 | 0.068665 | -0.011291 | 0.064651 | 0.014825 | 0.021189 | -0.00083525 | -0.0021148 | -0.0014377 | 0.0014953 | 0.021443 | 0.019489 | 0.021095 | -0.0011643 | 0.018812 | -0.0029885 | -0.032043 | 0.059509 | -0.050354 | 0.013733 | 0.17853 | 0.045776 | 0.082397 | 0.09613 | 0.059509 | -0.059509 | 0.10986 | 0.1831 | 0.11444 | 0.18768 | 122.2183 | -0.009156 | -0.054932 | 122.4472 | 122.3511 | 122.3145 | 0.13275 | 0.09613 | 122.2092 | -0.009156 | 0.041198 | 122.4518 | 122.4564 | 122.3831 | 0.24719 | 0.17395 | 0.22888 | 0.064087 | 0.24261 | 0.16937 | 0.10986 | 0.11902 | 122.3282 | 122.3282 | -0.11902 | -0.12817 | 122.2824 | 122.3785 | 122.2366 | 122.3648
1994.375 | 122.5891 | -122.2778 | 0.086975 | 0.011597 | 0.063796 | 0.017175 | 0.020121 | 0.0032236 | -0.002542 | -0.0018649 | -0.0046081 | 0.023152 | 0.019489 | 0.0149 | 0.0039627 | 0.020521 | -0.0032021 | -0.004578 | 0.045776 | -0.041199 | 0.027466 | 0.17395 | 0.041199 | 0.054932 | 0.086975 | 0.045776 | -0.059509 | 0.091553 | 0.16479 | 0.07782 | 0.20599 | 122.2366 | -0.041199 | -0.059509 | 122.4518 | 122.3328 | 122.319 | 0.096131 | 0.082398 | 122.2183 | -0.041199 | 0.004578 | 122.4426 | 122.4838 | 122.3557 | 0.2655 | 0.13733 | 0.21515 | 0.068665 | 0.2243 | 0.15106 | 0.086975 | 0.10528 | 122.3236 | 122.3236 | -0.12817 | -0.14648 | 122.3053 | 122.3694 | 122.2733 | 122.3648
1996.0625 | 122.5342 | -122.2961 | 0.1236 | -0.011291 | 0.06636 | 0.016534 | 0.022471 | -0.0025442 | -0.0033966 | -0.0022921 | -0.0076599 | 0.023793 | 0.018634 | 0.0243 | -0.0037277 | 0.016462 | -0.0036295 | -0.027466 | 0.032043 | -0.036621 | 0.027466 | 0.16937 | 0.050354 | 0.068665 | 0.036621 | 0.059509 | -0.022888 | 0.041199 | 0.12817 | 0.068665 | 0.16022 | 122.2595 | -0.091553 | -0.09613 | 122.4655 | 122.3648 | 122.3465 | 0.10529 | 0.086975 | 122.2733 | -0.064087 | -0.082397 | 122.4243 | 122.4564 | 122.3648 | 0.1831 | 0.091553 | 0.20599 | 0.064087 | 0.15106 | 0.064087 | 0.068664 | 0.082397 | 122.3282 | 122.3557 | -0.16022 | -0.14648 | 122.3236 | 122.3373 | 122.2687 | 122.3328
1997.8125 | 122.4838 | -122.287 | 0.10529 | 0.0039673 | 0.067001 | 0.014612 | 0.023539 | -0.0010488 | -0.0040374 | -0.0010105 | -0.0015565 | 0.02358 | 0.018421 | 0.019173 | -0.0037277 | 0.015394 | -0.0042703 | -0.036621 | 0.059509 | -0.050354 | -0.022888 | 0.11444 | -0.009155 | 0.018311 | -0.022888 | 0.082397 | -0.059509 | -0.018311 | 0.068665 | 0.004578 | 0.091553 | 122.2366 | -0.045777 | -0.12817 | 122.4014 | 122.3053 | 122.2778 | 0.068665 | 0.041199 | 122.2275 | -0.022889 | -0.1236 | 122.3557 | 122.3785 | 122.2916 | 0.15106 | 0.064087 | 0.16479 | 0.027466 | 0.12817 | 0.041198 | 0.10986 | 0.14191 | 122.3465 | 122.3694 | -0.15564 | -0.16479 | 122.2641 | 122.2687 | 122.2504 | 122.2641
1999.5625 | 122.4655 | -122.3007 | 0.1236 | 0.0039673 | 0.067214 | 0.019098 | 0.023326 | -0.0010488 | -0.0021148 | 0.00069849 | -0.0015565 | 0.025289 | 0.021198 | 0.015327 | 0.0016129 | 0.016034 | 2.068e-06 | -0.09613 | 0.086975 | -0.082397 | -0.09613 | -0.004578 | -0.11902 | -0.073242 | -0.14648 | 0.091553 | -0.082397 | -0.027466 | 0.009155 | -0.073242 | 0.09613 | 122.2183 | -0.036621 | -0.21973 | 122.2961 | 122.2275 | 122.1817 | 0.009155 | -0.036622 | 122.2183 | -0.032043 | -0.15106 | 122.3099 | 122.3969 | 122.2275 | 0.17853 | 0.009155 | 0.077819 | -0.013733 | 0.091552 | 0.054931 | 0.16937 | 0.17395 | 122.3877 | 122.3923 | -0.20599 | -0.20599 | 122.2046 | 122.2733 | 122.2046 | 122.1542
2001.2344 | 122.5708 | -122.2733 | 0.07782 | -0.0036622 | 0.063583 | 0.016321 | 0.019908 | -0.0025442 | -0.003183 | -0.0037875 | -0.0046081 | 0.021443 | 0.018421 | 0.023018 | -0.0033005 | 0.017957 | -0.0042703 | -0.07782 | 0.050354 | -0.054932 | -0.022888 | 0.1236 | 0 | 0.045776 | 0.009155 | 0.068665 | -0.059509 | 0.050354 | 0.15106 | 0.09613 | 0.17853 | 122.2183 | -0.027466 | -0.10071 | 122.3969 | 122.319 | 122.2733 | 0.10071 | 0.054932 | 122.2137 | -0.009155 | -0.027466 | 122.4243 | 122.4518 | 122.3694 | 0.23804 | 0.15564 | 0.17853 | 0.032044 | 0.21057 | 0.10986 | 0.10529 | 0.12817 | 122.3236 | 122.3419 | -0.13275 | -0.13733 | 122.2504 | 122.3236 | 122.1954 | 122.2824
2002.9688 | 122.4701 | -122.3373 | 0.12817 | -0.018921 | 0.064651 | 0.013544 | 0.021189 | -0.0059622 | -0.0038238 | -0.0018649 | 0.0014953 | 0.024648 | 0.01778 | 0.012337 | -0.0015915 | 0.016462 | -0.0057657 | -0.10529 | 0.09613 | -0.082397 | -0.10986 | 0.050354 | -0.064087 | -0.041199 | -0.09613 | 0.11444 | -0.091553 | -0.036621 | 0.054932 | -0.027466 | 0.082397 | 122.2549 | -0.032044 | -0.23804 | 122.3877 | 122.2961 | 122.2733 | 0.041198 | 0.01831 | 122.2458 | -0.013733 | -0.1648 | 122.3923 | 122.4197 | 122.3099 | 0.17395 | 0.064087 | 0.13275 | -0.027466 | 0.14649 | 0.054932 | 0.17853 | 0.20599 | 122.4335 | 122.4518 | -0.21057 | -0.21973 | 122.2275 | 122.3007 | 122.2321 | 122.2412
2004.7031 | 122.4976 | -122.2916 | 0.11444 | -0.011291 | 0.065719 | 0.012689 | 0.024821 | -0.0012624 | -0.0021148 | 0.00048489 | -0.0015565 | 0.026143 | 0.02013 | 0.015327 | 0.00097195 | 0.015394 | -0.0032021 | -0.07782 | 0.068665 | -0.086975 | -0.064087 | 0.064087 | -0.032043 | -0.004578 | -0.027466 | 0.09613 | -0.068665 | 0.009155 | 0.09613 | 0 | 0.12817 | 122.2046 | -0.045776 | -0.17853 | 122.3557 | 122.287 | 122.2595 | 0.082397 | 0.054932 | 122.2229 | -0.018311 | -0.10529 | 122.3877 | 122.4197 | 122.2916 | 0.19684 | 0.068665 | 0.15106 | 0.022888 | 0.16479 | 0.07782 | 0.15564 | 0.16479 | 122.3602 | 122.3877 | -0.20142 | -0.18311 | 122.2275 | 122.3007 | 122.2137 | 122.2641
2006.4531 | 122.6212 | -122.2824 | 0.07782 | -0.011291 | 0.062515 | 0.016534 | 0.020762 | -0.0023306 | -0.0021148 | -0.0010105 | -0.0046081 | 0.022084 | 0.019062 | 0.0243 | -0.0013779 | 0.016675 | -0.0010659 | -0.045776 | 0.032043 | -0.050354 | 0.009155 | 0.18768 | 0.054932 | 0.07782 | 0.073242 | 0.041199 | -0.045776 | 0.10071 | 0.21057 | 0.11902 | 0.19684 | 122.2321 | -0.045777 | -0.068665 | 122.4701 | 122.3602 | 122.3373 | 0.12817 | 0.10529 | 122.2366 | -0.036621 | 0.022888 | 122.493 | 122.4792 | 122.4014 | 0.24261 | 0.16479 | 0.23804 | 0.059509 | 0.25635 | 0.14648 | 0.082397 | 0.086975 | 122.3145 | 122.3236 | -0.12817 | -0.1236 | 122.2916 | 122.3831 | 122.2366 | 122.3557
2008.125 | 122.5296 | -122.3053 | 0.11444 | -0.0036622 | 0.064865 | 0.015039 | 0.023326 | -0.00062165 | -0.0023284 | -0.0022921 | 0.0014953 | 0.024861 | 0.019275 | 0.017891 | 0.00097195 | 0.018812 | -0.0032021 | -0.064087 | 0.068665 | -0.09613 | -0.050354 | 0.086975 | -0.032043 | 0.004578 | -0.004578 | 0.07782 | -0.07782 | 0.027466 | 0.09613 | 0.018311 | 0.13733 | 122.2092 | -0.045776 | -0.16479 | 122.3923 | 122.3099 | 122.2733 | 0.10071 | 0.064087 | 122.2275 | -0.036621 | -0.086975 | 122.4014 | 122.4426 | 122.3236 | 0.21515 | 0.096131 | 0.1831 | 0.045776 | 0.17395 | 0.10529 | 0.16479 | 0.15564 | 122.374 | 122.3831 | -0.21057 | -0.19226 | 122.2549 | 122.3328 | 122.2412 | 122.3007
2009.875 | 122.5571 | -122.2961 | 0.086975 | -0.0036622 | 0.067001 | 0.017603 | 0.022685 | -0.00083525 | -0.0016876 | -0.00058311 | -0.0015565 | 0.022725 | 0.020557 | 0.014259 | -0.0011643 | 0.019452 | -0.0046975 | -0.036621 | 0.045776 | -0.045776 | 0.018311 | 0.16937 | 0.009155 | 0.064087 | 0.064087 | 0.050354 | -0.059509 | 0.082397 | 0.13733 | 0.064087 | 0.16479 | 122.2504 | -0.041199 | -0.068664 | 122.4655 | 122.3602 | 122.3053 | 0.10986 | 0.054931 | 122.2366 | -0.036621 | -0.004578 | 122.4335 | 122.4609 | 122.3602 | 0.2243 | 0.1236 | 0.21515 | 0.064087 | 0.19684 | 0.14191 | 0.091552 | 0.10986 | 122.3419 | 122.3465 | -0.13275 | -0.14648 | 122.3145 | 122.3785 | 122.2595 | 122.3602
2011.5625 | 122.4564 | -122.3236 | 0.11444 | -0.011291 | 0.066146 | 0.016321 | 0.023966 | 0.00301 | -0.0012604 | -0.0010105 | -0.0015565 | 0.024007 | 0.020343 | 0.010628 | -0.00030965 | 0.018812 | -0.0044839 | -0.086975 | 0.064087 | -0.082397 | -0.10986 | 0.004578 | -0.10986 | -0.07782 | -0.11902 | 0.091553 | -0.073242 | -0.032043 | 0.018311 | -0.054932 | 0.091553 | 122.2412 | -0.050354 | -0.2243 | 122.3282 | 122.2458 | 122.2137 | 0.004577 | -0.027466 | 122.2504 | -0.022888 | -0.14648 | 122.3419 | 122.4152 | 122.2687 | 0.16479 | 0.01831 | 0.086975 | -0.027466 | 0.091553 | 0.041199 | 0.14648 | 0.16479 | 122.3877 | 122.4152 | -0.19684 | -0.18768 | 122.2137 | 122.2916 | 122.2366 | 122.2046
2013.2344 | 122.5983 | -122.2733 | 0.07782 | 0.0039673 | 0.065292 | 0.015894 | 0.021617 | -0.0063894 | -0.0012604 | -0.0016513 | -0.0046081 | 0.022512 | 0.019275 | 0.0087051 | -0.0018051 | 0.018812 | -0.00042513 | -0.036621 | 0.032043 | -0.041199 | 0.032043 | 0.19226 | 0.059509 | 0.07782 | 0.050354 | 0.068665 | -0.050354 | 0.068665 | 0.16479 | 0.10071 | 0.17853 | 122.2321 | -0.045777 | -0.045777 | 122.4655 | 122.3511 | 122.3328 | 0.11902 | 0.10071 | 122.2229 | -0.009155 | -0.009155 | 122.438 | 122.4518 | 122.374 | 0.22888 | 0.15106 | 0.23346 | 0.073242 | 0.21515 | 0.11902 | 0.073242 | 0.11902 | 122.3053 | 122.3419 | -0.11902 | -0.12817 | 122.3053 | 122.3419 | 122.2366 | 122.3236
2014.9688 | 122.6028 | -122.2916 | 0.082397 | -0.011291 | 0.061233 | 0.013971 | 0.022257 | 1.915e-05 | -0.004251 | -0.00058311 | -0.0015565 | 0.022512 | 0.017994 | 0.011055 | -9.605e-05 | 0.016675 | -0.0059793 | -0.041199 | 0.064087 | -0.041199 | 0 | 0.17395 | 0.059509 | 0.091553 | 0.07782 | 0.041199 | -0.045776 | 0.091553 | 0.18768 | 0.11902 | 0.20599 | 122.2504 | -0.01831 | -0.082397 | 122.4655 | 122.3831 | 122.3511 | 0.13275 | 0.10071 | 122.2458 | -0.041198 | 0.009156 | 122.4792 | 122.4976 | 122.4106 | 0.25177 | 0.16479 | 0.21515 | 0.041199 | 0.23346 | 0.13733 | 0.10529 | 0.086975 | 122.3557 | 122.3328 | -0.1236 | -0.12817 | 122.2916 | 122.3831 | 122.2504 | 122.3694
2016.6562 | 122.4655 | -122.3282 | 0.1236 | -0.0036622 | 0.067428 | 0.017389 | 0.023112 | 0.0021556 | -0.004892 | -0.00079691 | -0.0046081 | 0.026357 | 0.019489 | 0.013405 | -0.00095065 | 0.016889 | 0.0014975 | -0.091553 | 0.091553 | -0.09613 | -0.11444 | -0.027466 | -0.10986 | -0.082397 | -0.09613 | 0.091553 | -0.082397 | -0.018311 | 0.013733 | -0.054932 | 0.10071 | 122.2321 | -0.032043 | -0.23804 | 122.3007 | 122.2458 | 122.2183 | 0.013733 | -0.013733 | 122.2458 | -0.032043 | -0.14191 | 122.3419 | 122.4289 | 122.2733 | 0.18311 | 0.027465 | 0.068664 | -0.018311 | 0.09613 | 0.064086 | 0.18768 | 0.17395 | 122.4197 | 122.4197 | -0.21973 | -0.20599 | 122.2137 | 122.3099 | 122.2366 | 122.2321
2018.4062 | 122.6028 | -122.3145 | 0.091553 | -0.011291 | 0.066146 | 0.01568 | 0.020335 | -0.0012624 | -0.0016876 | -0.00058311 | -0.0015565 | 0.021443 | 0.02013 | 0.013405 | -0.0011643 | 0.018171 | 0.0012839 | -0.036621 | 0.054932 | -0.050354 | 0.032043 | 0.19684 | 0.064087 | 0.086975 | 0.068665 | 0.059509 | -0.054932 | 0.091553 | 0.19226 | 0.1236 | 0.19226 | 122.2641 | -0.036621 | -0.05951 | 122.5113 | 122.4014 | 122.3785 | 0.13733 | 0.11444 | 122.2595 | -0.032044 | 0 | 122.5067 | 122.5067 | 122.438 | 0.24719 | 0.17853 | 0.24719 | 0.082397 | 0.24719 | 0.14649 | 0.10529 | 0.11444 | 122.3694 | 122.374 | -0.14191 | -0.14649 | 122.3465 | 122.406 | 122.2778 | 122.3831
2020.1406 | 122.6166 | -122.3145 | 0.091553 | -0.0036622 | 0.063796 | 0.017389 | 0.020335 | -0.002117 | -0.0038238 | -0.00015591 | -0.0046081 | 0.023793 | 0.02013 | 0.020668 | -0.00052345 | 0.020734 | -0.0019205 | -0.073242 | 0.059509 | -0.045776 | -0.004578 | 0.15106 | 0.022888 | 0.050354 | 0.036621 | 0.059509 | -0.064087 | 0.064087 | 0.16022 | 0.10071 | 0.19684 | 122.2687 | -0.032044 | -0.096131 | 122.4655 | 122.3648 | 122.3373 | 0.09613 | 0.068664 | 122.2504 | -0.032044 | -0.027466 | 122.4747 | 122.5113 | 122.4152 | 0.26093 | 0.1648 | 0.19684 | 0.041198 | 0.2243 | 0.12817 | 0.10528 | 0.1236 | 122.374 | 122.374 | -0.13733 | -0.15564 | 122.3099 | 122.3785 | 122.2412 | 122.3511
2021.8906 | 122.4838 | -122.3328 | 0.11444 | -0.018921 | 0.065292 | 0.015466 | 0.023539 | -0.002117 | -0.00083304 | -0.0012241 | -0.0015565 | 0.025289 | 0.018848 | 0.021736 | 0.00033115 | 0.018812 | -0.00021153 | -0.091553 | 0.086975 | -0.091553 | -0.10986 | 0.004578 | -0.086975 | -0.059509 | -0.064087 | 0.086975 | -0.073242 | -0.027466 | 0.027466 | -0.054932 | 0.10071 | 122.2412 | -0.027466 | -0.2243 | 122.3373 | 122.2733 | 122.2458 | 0.032044 | 0.004578 | 122.2595 | -0.027466 | -0.14191 | 122.3602 | 122.4335 | 122.2778 | 0.17395 | 0.01831 | 0.096131 | -0.01831 | 0.10071 | 0.045776 | 0.17853 | 0.16022 | 122.4197 | 122.4197 | -0.20599 | -0.18768 | 122.2229 | 122.3053 | 122.2412 | 122.2687
2023.5781 | 122.5296 | -122.3328 | 0.11444 | -0.011291 | 0.06636 | 0.014398 | 0.022044 | -0.001476 | -0.0027556 | -0.0031467 | -0.0015565 | 0.022298 | 0.018848 | 0.015968 | -0.0018051 | 0.016675 | -0.0040567 | -0.082397 | 0.091553 | -0.082397 | -0.091553 | 0.022888 | -0.050354 | -0.013733 | -0.059509 | 0.082397 | -0.073242 | -0.018311 | 0.073242 | -0.022888 | 0.11444 | 122.2504 | -0.022888 | -0.20599 | 122.3557 | 122.319 | 122.2824 | 0.068664 | 0.032043 | 122.2595 | -0.032044 | -0.13275 | 122.406 | 122.4472 | 122.3099 | 0.18768 | 0.050354 | 0.10528 | -0.009156 | 0.14648 | 0.054931 | 0.17395 | 0.15564 | 122.4243 | 122.4152 | -0.19684 | -0.18768 | 122.2412 | 122.3145 | 122.2504 | 122.2733
2025.3125 | 122.525 | -122.3328 | 0.10986 | 0.0039673 | 0.064865 | 0.015466 | 0.02183 | -0.0019034 | -0.002542 | -0.0014377 | -0.0015565 | 0.024648 | 0.019703 | 0.014473 | -0.0024461 | 0.018598 | -0.0017069 | -0.09613 | 0.07782 | -0.07782 | -0.10071 | 0.045776 | -0.068665 | -0.032043 | -0.050354 | 0.091553 | -0.082397 | -0.013733 | 0.07782 | -0.004578 | 0.11444 | 122.2549 | -0.032043 | -0.21057 | 122.3785 | 122.3007 | 122.2641 | 0.045777 | 0.009155 | 122.2504 | -0.01831 | -0.1236 | 122.4106 | 122.4472 | 122.3282 | 0.19684 | 0.077819 | 0.1236 | -0.022888 | 0.16022 | 0.068664 | 0.15564 | 0.17395 | 122.4106 | 122.4243 | -0.18768 | -0.19226 | 122.2321 | 122.319 | 122.2366 | 122.2824
2027.0469 | 122.5845 | -122.3053 | 0.09613 | -0.0036622 | 0.066146 | 0.015894 | 0.023539 | 0.0019418 | -0.00019224 | -0.00015591 | -0.0076599 | 0.025075 | 0.018421 | 0.015755 | 0.0020401 | 0.01753 | 2.068e-06 | -0.086975 | 0.064087 | -0.082397 | -0.050354 | 0.09613 | -0.045776 | 0.009155 | 0.004578 | 0.07782 | -0.045776 | 0.07782 | 0.14191 | 0.054932 | 0.19226 | 122.2229 | -0.032043 | -0.14648 | 122.4014 | 122.3145 | 122.2595 | 0.091552 | 0.036621 | 122.2595 | -0.01831 | -0.01831 | 122.4472 | 122.4976 | 122.3602 | 0.23804 | 0.10071 | 0.17853 | 0.032043 | 0.18768 | 0.1236 | 0.14648 | 0.1236 | 122.3694 | 122.3831 | -0.17853 | -0.14191 | 122.2549 | 122.3831 | 122.2183 | 122.3099
2028.7969 | 122.5433 | -122.3282 | 0.09613 | 0.0039673 | 0.06871 | 0.017175 | 0.023966 | 0.0049326 | -0.0023284 | 0.00048489 | 0.0014953 | 0.02358 | 0.019916 | 0.018104 | 0.0026809 | 0.019452 | -0.00085233 | -0.086975 | 0.073242 | -0.073242 | -0.10986 | 0.022888 | -0.10071 | -0.059509 | -0.050354 | 0.082397 | -0.091553 | 0.022888 | 0.064087 | -0.018311 | 0.13275 | 122.2549 | -0.022888 | -0.20599 | 122.3511 | 122.2687 | 122.2275 | 0.013733 | -0.027466 | 122.2366 | -0.013733 | -0.073242 | 122.3923 | 122.4609 | 122.3099 | 0.2243 | 0.073242 | 0.09613 | -0.036621 | 0.15564 | 0.11444 | 0.14648 | 0.17395 | 122.4014 | 122.4106 | -0.16937 | -0.18768 | 122.2183 | 122.3511 | 122.2412 | 122.2778
2030.4688 | 122.5983 | -122.3145 | 0.086975 | 0.011597 | 0.06636 | 0.016321 | 0.021189 | 0.00023275 | -0.00083304 | -0.0033603 | -0.0015565 | 0.02358 | 0.019062 | 0.016609 | 0.0016129 | 0.020093 | 0.00085667 | -0.022888 | 0.032043 | -0.041199 | 0.036621 | 0.18768 | 0.027466 | 0.059509 | 0.09613 | 0.068665 | -0.050354 | 0.064087 | 0.16479 | 0.07782 | 0.19226 | 122.2733 | -0.054932 | -0.050354 | 122.5021 | 122.374 | 122.3419 | 0.10071 | 0.068665 | 122.2641 | -0.01831 | -0.022888 | 122.4792 | 122.5067 | 122.3923 | 0.24261 | 0.12817 | 0.22888 | 0.07782 | 0.21515 | 0.11444 | 0.073242 | 0.11902 | 122.3465 | 122.3831 | -0.12817 | -0.13733 | 122.3511 | 122.3785 | 122.2916 | 122.4106
2032.2031 | 122.5662 | -122.3236 | 0.10071 | -0.011291 | 0.064224 | 0.015466 | 0.019267 | -0.0040396 | -0.0029694 | -0.0012241 | -0.0015565 | 0.021657 | 0.01778 | 0.018532 | 0.0020401 | 0.017743 | 0.0017111 | -0.073242 | 0.064087 | -0.032043 | -0.027466 | 0.1236 | 0 | 0.027466 | 0 | 0.068665 | -0.054932 | 0.036621 | 0.10529 | 0.045776 | 0.14648 | 122.2916 | -0.036621 | -0.12817 | 122.4472 | 122.3511 | 122.3236 | 0.059509 | 0.032043 | 122.2687 | -0.032043 | -0.064087 | 122.4289 | 122.4701 | 122.3694 | 0.20142 | 0.10071 | 0.15564 | 0.004577 | 0.16022 | 0.091553 | 0.09613 | 0.1236 | 122.3877 | 122.3923 | -0.13275 | -0.15564 | 122.2961 | 122.3602 | 122.2504 | 122.3236
2033.9531 | 122.5754 | -122.319 | 0.09613 | 0.0039673 | 0.063583 | 0.014825 | 0.020335 | 1.915e-05 | -0.0023284 | -0.0018649 | -0.0076599 | 0.024648 | 0.019703 | 0.014046 | -0.0018051 | 0.019452 | -0.0036295 | -0.068665 | 0.064087 | -0.054932 | -0.045776 | 0.11444 | -0.013733 | 0.018311 | -0.009155 | 0.054932 | -0.073242 | 0.013733 | 0.10071 | 0.036621 | 0.15106 | 122.2641 | -0.032043 | -0.14191 | 122.4335 | 122.3373 | 122.3053 | 0.073243 | 0.041199 | 122.2458 | -0.041198 | -0.082397 | 122.4197 | 122.4701 | 122.3557 | 0.2243 | 0.10986 | 0.16937 | 0.009156 | 0.17395 | 0.086975 | 0.11902 | 0.12817 | 122.3831 | 122.374 | -0.15106 | -0.16937 | 122.2733 | 122.3328 | 122.2504 | 122.3099
2035.625 | 122.5021 | -122.3511 | 0.13733 | -0.0036622 | 0.064651 | 0.016107 | 0.021403 | -0.002117 | -0.001474 | -0.0010105 | -0.0046081 | 0.024648 | 0.019062 | 0.011482 | -0.0033005 | 0.016462 | 0.0019247 | -0.07782 | 0.064087 | -0.07782 | -0.068665 | 0.07782 | -0.041199 | -0.009155 | -0.068665 | 0.086975 | -0.082397 | -0.036621 | 0.050354 | -0.013733 | 0.082397 | 122.2733 | -0.073242 | -0.20599 | 122.4289 | 122.3419 | 122.3099 | 0.068665 | 0.036621 | 122.2687 | -0.050354 | -0.17395 | 122.4014 | 122.4335 | 122.3373 | 0.16479 | 0.068664 | 0.15564 | 0.009155 | 0.13275 | 0.045776 | 0.14191 | 0.16937 | 122.4152 | 122.438 | -0.21515 | -0.21973 | 122.2824 | 122.3145 | 122.2733 | 122.2824
2037.3906 | 122.5754 | -122.3145 | 0.091553 | -0.0036622 | 0.062942 | 0.018457 | 0.022471 | -0.00019445 | -0.00061944 | -0.0014377 | -0.0015565 | 0.023152 | 0.018421 | 0.01725 | 0.0020401 | 0.017957 | 0.00064307 | -0.059509 | 0.054932 | -0.054932 | -0.032043 | 0.10529 | -0.013733 | 0.027466 | -0.004578 | 0.059509 | -0.050354 | 0.018311 | 0.11444 | 0.032043 | 0.14191 | 122.2595 | -0.036621 | -0.1236 | 122.4197 | 122.3419 | 122.3007 | 0.082398 | 0.041199 | 122.2641 | -0.032044 | -0.073242 | 122.4289 | 122.4564 | 122.3465 | 0.19226 | 0.082397 | 0.16022 | 0.022889 | 0.16479 | 0.068665 | 0.10986 | 0.10986 | 122.3694 | 122.374 | -0.14649 | -0.14191 | 122.2824 | 122.3328 | 122.2549 | 122.3099
2039.0625 | 122.5067 | -122.374 | 0.11902 | -0.011291 | 0.064865 | 0.015039 | 0.021189 | -0.002117 | -0.004892 | 0.0021939 | -0.0015565 | 0.024434 | 0.018207 | 0.011055 | -0.0043687 | 0.016889 | -0.0046975 | -0.11444 | 0.09613 | -0.091553 | -0.09613 | 0.054932 | -0.045776 | -0.013733 | -0.082397 | 0.10529 | -0.073242 | -0.050354 | 0.022888 | -0.041199 | 0.082397 | 122.2824 | -0.022889 | -0.21515 | 122.4289 | 122.3602 | 122.3282 | 0.07782 | 0.045777 | 122.3007 | -0.013733 | -0.16937 | 122.3969 | 122.4564 | 122.3328 | 0.15564 | 0.032043 | 0.14649 | -0.004577 | 0.09613 | 0.022888 | 0.18768 | 0.17853 | 122.4701 | 122.4792 | -0.21057 | -0.19226 | 122.2778 | 122.3236 | 122.2595 | 122.2916
2040.7969 | 122.5571 | -122.3602 | 0.13275 | 0.0039673 | 0.065719 | 0.014612 | 0.024394 | -0.0012624 | -0.0033966 | -0.00058311 | -0.0015565 | 0.025716 | 0.020771 | 0.015755 | -0.0020187 | 0.016675 | -0.0042703 | -0.073242 | 0.073242 | -0.10529 | -0.082397 | 0.041199 | -0.036621 | -0.022888 | -0.07782 | 0.10529 | -0.07782 | -0.004578 | 0.082397 | -0.009155 | 0.11444 | 122.2549 | -0.059509 | -0.21515 | 122.4014 | 122.3373 | 122.3236 | 0.082398 | 0.068665 | 122.2824 | -0.027465 | -0.13733 | 122.4426 | 122.4747 | 122.3511 | 0.19226 | 0.068665 | 0.14649 | 0.022889 | 0.16022 | 0.073242 | 0.17853 | 0.18311 | 122.4335 | 122.4655 | -0.23804 | -0.21057 | 122.2778 | 122.3557 | 122.287 | 122.2824
2042.5 | 122.5845 | -122.3373 | 0.091553 | 0.011597 | 0.063583 | 0.017816 | 0.022685 | -0.0042532 | -0.003183 | 0.00069849 | -0.0046081 | 0.022084 | 0.020557 | 0.021736 | 0.0022537 | 0.019025 | -0.0017069 | -0.036621 | 0.032043 | -0.041199 | 0.009155 | 0.16937 | 0.009155 | 0.064087 | 0.032043 | 0.050354 | -0.059509 | 0.054932 | 0.11902 | 0.054932 | 0.16479 | 122.2961 | -0.05951 | -0.082398 | 122.5067 | 122.4014 | 122.3465 | 0.10529 | 0.050354 | 122.2778 | -0.041199 | -0.036621 | 122.4564 | 122.5021 | 122.3923 | 0.2243 | 0.11444 | 0.21057 | 0.050354 | 0.17853 | 0.11444 | 0.073242 | 0.10986 | 122.3694 | 122.3877 | -0.13275 | -0.15106 | 122.3465 | 122.3923 | 122.3007 | 122.3694
2044.25 | 122.6395 | -122.3282 | 0.09613 | -0.011291 | 0.064865 | 0.014398 | 0.019908 | -0.0033986 | -0.0019012 | -0.0046421 | -0.0015565 | 0.024007 | 0.016712 | 0.020454 | -0.0015915 | 0.018598 | 0.0012839 | -0.022888 | 0.045776 | -0.045776 | 0.045776 | 0.20599 | 0.059509 | 0.082397 | 0.07782 | 0.041199 | -0.045776 | 0.091553 | 0.19226 | 0.10986 | 0.18768 | 122.2824 | -0.050354 | -0.050354 | 122.5342 | 122.4106 | 122.3877 | 0.12817 | 0.10528 | 122.2824 | -0.054931 | -0.004577 | 122.5204 | 122.5159 | 122.438 | 0.23346 | 0.15564 | 0.25177 | 0.091552 | 0.23804 | 0.13733 | 0.091552 | 0.086975 | 122.374 | 122.3694 | -0.14191 | -0.14191 | 122.374 | 122.4197 | 122.3053 | 122.406
2046 | 122.5204 | -122.374 | 0.11444 | 0.0039673 | 0.064224 | 0.01568 | 0.020335 | 0.00087375 | -0.0029694 | -0.0010105 | -0.0015565 | 0.026143 | 0.019275 | 0.013191 | -0.0033005 | 0.015607 | -0.00085233 | -0.10071 | 0.10529 | -0.10529 | -0.10529 | 0.032043 | -0.054932 | -0.027466 | -0.07782 | 0.09613 | -0.091553 | -0.022888 | 0.045776 | -0.013733 | 0.10529 | 122.2687 | -0.009155 | -0.21973 | 122.406 | 122.3465 | 122.319 | 0.07782 | 0.050354 | 122.2824 | -0.018311 | -0.13733 | 122.4197 | 122.4792 | 122.3602 | 0.19684 | 0.07782 | 0.13733 | 0 | 0.13733 | 0.068665 | 0.21057 | 0.18768 | 122.4792 | 122.4701 | -0.21973 | -0.20599 | 122.2687 | 122.3511 | 122.2733 | 122.2961
2047.6719 | 122.5891 | -122.3557 | 0.09613 | -0.0036622 | 0.065933 | 0.016962 | 0.020335 | -0.0053214 | -0.0021148 | 0.0015531 | 0.0045471 | 0.022298 | 0.018207 | 0.022377 | 0.0018265 | 0.017743 | -0.0027749 | -0.068665 | 0.045776 | -0.041199 | -0.041199 | 0.11902 | -0.013733 | 0.022888 | 0 | 0.07782 | -0.054932 | 0.041199 | 0.12817 | 0.050354 | 0.15106 | 122.3145 | -0.050354 | -0.13733 | 122.4747 | 122.3785 | 122.3419 | 0.064087 | 0.027466 | 122.3007 | -0.01831 | -0.054931 | 122.4838 | 122.5067 | 122.406 | 0.20599 | 0.10529 | 0.16022 | 0 | 0.18311 | 0.096131 | 0.086975 | 0.13275 | 122.4014 | 122.4335 | -0.13733 | -0.15106 | 122.3145 | 122.3969 | 122.287 | 122.3557
2049.4219 | 122.5891 | -122.3419 | 0.10071 | -0.011291 | 0.066787 | 0.013757 | 0.022898 | -0.0051076 | -0.0038238 | -0.0014377 | 0.0045471 | 0.023793 | 0.01778 | 0.017677 | -0.00052345 | 0.019025 | -0.0038431 | -0.004578 | 0.036621 | -0.050354 | 0.022888 | 0.16022 | 0.054932 | 0.073242 | 0.050354 | 0.073242 | -0.045776 | 0.050354 | 0.15564 | 0.068665 | 0.14191 | 122.2916 | -0.064087 | -0.07782 | 122.5021 | 122.4152 | 122.3969 | 0.1236 | 0.10529 | 122.2961 | -0.027466 | -0.050354 | 122.4976 | 122.4838 | 122.4106 | 0.18768 | 0.11444 | 0.21057 | 0.073242 | 0.20142 | 0.09613 | 0.086975 | 0.11902 | 122.3785 | 122.4152 | -0.15106 | -0.14648 | 122.3648 | 122.3923 | 122.3373 | 122.3923
2051.1562 | 122.5159 | -122.3877 | 0.13733 | -0.011291 | 0.066146 | 0.014398 | 0.022898 | 0.001301 | -0.0023284 | -0.0018649 | -0.0015565 | 0.025716 | 0.019916 | 0.011269 | -0.0026597 | 0.018171 | -0.0014931 | -0.086975 | 0.059509 | -0.086975 | -0.082397 | 0.073242 | -0.050354 | -0.018311 | -0.064087 | 0.10529 | -0.082397 | -0.045776 | 0.036621 | -0.022888 | 0.07782 | 122.3007 | -0.07782 | -0.21973 | 122.4609 | 122.3694 | 122.3373 | 0.068664 | 0.036621 | 122.3053 | -0.032043 | -0.18311 | 122.4243 | 122.4655 | 122.3648 | 0.16022 | 0.059509 | 0.16022 | 0.004578 | 0.11902 | 0.036621 | 0.14648 | 0.18768 | 122.4472 | 122.493 | -0.2243 | -0.21973 | 122.3053 | 122.3419 | 122.3007 | 122.3236
2052.9062 | 122.6212 | -122.3373 | 0.082397 | 0.0039673 | 0.063369 | 0.016321 | 0.022685 | 0.0010874 | -0.0010468 | -0.0012241 | -0.0046081 | 0.023366 | 0.020771 | 0.0069961 | 0.00033115 | 0.019239 | -0.0042703 | -0.073242 | 0.059509 | -0.068665 | -0.041199 | 0.10529 | -0.004578 | 0.022888 | -0.004578 | 0.068665 | -0.054932 | 0.045776 | 0.12817 | 0.059509 | 0.17395 | 122.2687 | -0.022888 | -0.1236 | 122.4426 | 122.3602 | 122.3328 | 0.091553 | 0.064087 | 122.2824 | -0.013732 | -0.036621 | 122.4655 | 122.5113 | 122.3969 | 0.22888 | 0.11444 | 0.17395 | 0.027466 | 0.18311 | 0.10071 | 0.12817 | 0.1236 | 122.3969 | 122.406 | -0.15106 | -0.13733 | 122.2961 | 122.3831 | 122.2641 | 122.3328
2054.5781 | 122.5662 | -122.3557 | 0.1236 | 0.0039673 | 0.065505 | 0.013757 | 0.022257 | -0.0027578 | -0.004251 | 0.0026211 | -0.0076599 | 0.025502 | 0.019703 | 0.013405 | 0.0018265 | 0.015821 | -0.00085233 | -0.059509 | 0.073242 | -0.07782 | -0.050354 | 0.059509 | -0.018311 | -0.013733 | -0.032043 | 0.10529 | -0.064087 | 0.013733 | 0.10529 | 0.013733 | 0.13733 | 122.2778 | -0.050354 | -0.17395 | 122.4152 | 122.3419 | 122.3373 | 0.064087 | 0.059509 | 122.2916 | -0.01831 | -0.10986 | 122.4609 | 122.493 | 122.3694 | 0.20142 | 0.07782 | 0.13733 | 0.027466 | 0.16937 | 0.07782 | 0.15106 | 0.16937 | 122.4289 | 122.4609 | -0.20142 | -0.18768 | 122.3053 | 122.3694 | 122.2961 | 122.3236
2056.3281 | 122.6349 | -122.3099 | 0.07782 | -0.011291 | 0.068283 | 0.018457 | 0.021617 | -0.0010488 | -0.0046782 | -0.0020785 | 0.0014953 | 0.025502 | 0.019062 | 0.0149 | 0.0037491 | 0.01988 | 0.0010703 | 0 | 0.036621 | -0.036621 | 0.027466 | 0.17853 | 0.027466 | 0.050354 | 0.091553 | 0.036621 | -0.036621 | 0.11902 | 0.19226 | 0.10529 | 0.20142 | 122.2733 | -0.041199 | -0.050354 | 122.4884 | 122.3602 | 122.3373 | 0.086975 | 0.064087 | 122.2733 | -0.041199 | 0.041199 | 122.5021 | 122.5113 | 122.4152 | 0.23804 | 0.14191 | 0.21515 | 0.064087 | 0.22888 | 0.15564 | 0.073242 | 0.073242 | 122.3465 | 122.3465 | -0.11444 | -0.11444 | 122.3373 | 122.4289 | 122.3099 | 122.4014
2058.0781 | 122.6486 | -122.3419 | 0.086975 | 0.0039673 | 0.064865 | 0.014825 | 0.02183 | -0.00062165 | -0.004892 | -0.0010105 | -0.0015565 | 0.02358 | 0.020557 | 0.017677 | -0.0018051 | 0.018598 | 0.00021567 | -0.022888 | 0.045776 | -0.041199 | 0.041199 | 0.21973 | 0.082397 | 0.09613 | 0.091553 | 0.059509 | -0.036621 | 0.086975 | 0.21057 | 0.1236 | 0.19226 | 122.3007 | -0.041199 | -0.045776 | 122.5616 | 122.438 | 122.4243 | 0.13733 | 0.1236 | 122.3053 | -0.027466 | 0 | 122.5525 | 122.5342 | 122.4655 | 0.22888 | 0.16022 | 0.26093 | 0.082398 | 0.24719 | 0.1236 | 0.086975 | 0.09613 | 122.3877 | 122.4014 | -0.12817 | -0.1236 | 122.3831 | 122.4289 | 122.319 | 122.4335
2059.8281 | 122.5159 | -122.3465 | 0.10529 | 0.011597 | 0.06636 | 0.017175 | 0.022471 | -0.00040805 | -0.0033966 | -0.0014377 | 0.0014953 | 0.026143 | 0.020984 | 0.015968 | 0.0016129 | 0.017957 | -0.0025613 | -0.091553 | 0.07782 | -0.068665 | -0.09613 | -0.004578 | -0.11902 | -0.07782 | -0.10529 | 0.10071 | -0.068665 | -0.018311 | 0.022888 | -0.059509 | 0.09613 | 122.2778 | -0.027466 | -0.20142 | 122.3419 | 122.2687 | 122.2275 | -0.009155 | -0.050354 | 122.2778 | -0.004578 | -0.1236 | 122.3694 | 122.4426 | 122.287 | 0.16479 | 0.009156 | 0.064087 | -0.027465 | 0.091553 | 0.050354 | 0.14649 | 0.16937 | 122.4243 | 122.4472 | -0.17395 | -0.17395 | 122.2504 | 122.3282 | 122.2549 | 122.2412
2061.5156 | 122.5708 | -122.3557 | 0.1236 | -0.018921 | 0.064437 | 0.016534 | 0.02183 | -0.00019445 | -0.002542 | -0.0020785 | -0.0046081 | 0.022512 | 0.019703 | 0.015755 | -0.0028733 | 0.018598 | -0.0042703 | -0.041199 | 0.050354 | -0.041199 | 0.004578 | 0.15106 | 0.036621 | 0.054932 | 0.018311 | 0.07782 | -0.054932 | 0.004578 | 0.10529 | 0.027466 | 0.1236 | 122.3145 | -0.073242 | -0.11902 | 122.5067 | 122.4106 | 122.3923 | 0.096131 | 0.07782 | 122.3007 | -0.045776 | -0.11902 | 122.4609 | 122.4792 | 122.3831 | 0.17853 | 0.082398 | 0.19226 | 0.045777 | 0.16022 | 0.05951 | 0.091553 | 0.13275 | 122.406 | 122.4335 | -0.16479 | -0.17853 | 122.3602 | 122.3602 | 122.3145 | 122.374
2063.2656 | 122.5616 | -122.3602 | 0.11444 | -0.018921 | 0.067642 | 0.016748 | 0.022257 | -0.0029714 | -0.0019012 | 0.00069849 | -0.0015565 | 0.027638 | 0.019916 | 0.015968 | 0.0016129 | 0.019452 | -0.0046975 | -0.10529 | 0.091553 | -0.091553 | -0.09613 | 0.032043 | -0.10986 | -0.050354 | -0.064087 | 0.082397 | -0.07782 | 0.009155 | 0.041199 | -0.045776 | 0.10986 | 122.2687 | -0.022888 | -0.21057 | 122.3923 | 122.3099 | 122.2504 | 0.041199 | -0.01831 | 122.2824 | -0.032044 | -0.10529 | 122.4014 | 122.4701 | 122.3145 | 0.18768 | 0.032044 | 0.1236 | -0.004577 | 0.11902 | 0.086975 | 0.18311 | 0.16022 | 122.4518 | 122.4426 | -0.20599 | -0.19226 | 122.2641 | 122.3694 | 122.2549 | 122.2961
2065.0156 | 122.5983 | -122.3511 | 0.09613 | -0.011291 | 0.063796 | 0.016962 | 0.022898 | 0.00087375 | -0.002542 | -0.0042147 | -0.0015565 | 0.02358 | 0.02013 | 0.013405 | -0.0011643 | 0.018171 | 0.00021567 | -0.036621 | 0.041199 | -0.045776 | -0.013733 | 0.16937 | -0.009155 | 0.036621 | 0.045776 | 0.045776 | -0.064087 | 0.054932 | 0.13275 | 0.054932 | 0.15106 | 122.3053 | -0.054931 | -0.10986 | 122.5204 | 122.3877 | 122.3419 | 0.082397 | 0.036621 | 122.287 | -0.050354 | -0.041198 | 122.4838 | 122.5021 | 122.406 | 0.21515 | 0.11902 | 0.21515 | 0.032043 | 0.19684 | 0.11902 | 0.086975 | 0.10986 | 122.3923 | 122.3969 | -0.14191 | -0.16022 | 122.3373 | 122.406 | 122.3145 | 122.3969
2066.7031 | 122.6395 | -122.3465 | 0.091553 | 0.0039673 | 0.065933 | 0.01568 | 0.021617 | -0.00040805 | -0.00019224 | -0.00036951 | -0.0015565 | 0.025289 | 0.019489 | 0.012764 | 0.00054475 | 0.017743 | -0.0038431 | -0.064087 | 0.082397 | -0.073242 | -0.036621 | 0.10529 | -0.050354 | 0.009155 | 0.036621 | 0.073242 | -0.054932 | 0.082397 | 0.15564 | 0.059509 | 0.20599 | 122.2733 | -0.009156 | -0.12817 | 122.4518 | 122.3557 | 122.2961 | 0.082397 | 0.022888 | 122.2916 | -0.018311 | -0.009156 | 122.5021 | 122.5525 | 122.406 | 0.26093 | 0.11444 | 0.17853 | 0.036621 | 0.21057 | 0.13733 | 0.15564 | 0.12817 | 122.4289 | 122.4197 | -0.16479 | -0.14649 | 122.3099 | 122.4289 | 122.2824 | 122.3831
2068.4531 | 122.5021 | -122.3877 | 0.10071 | -0.0036622 | 0.066787 | 0.016748 | 0.023539 | -0.00040805 | -0.0010468 | 0.00027129 | 0.0014953 | 0.02657 | 0.02013 | 0.017677 | 0.00011755 | 0.018812 | 0.00021567 | -0.091553 | 0.086975 | -0.10529 | -0.10986 | -0.013733 | -0.10986 | -0.073242 | -0.10986 | 0.091553 | -0.064087 | -0.032043 | 0.027466 | -0.059509 | 0.09613 | 122.2824 | -0.013733 | -0.21057 | 122.374 | 122.3145 | 122.2778 | 0.032044 | -0.004577 | 122.3236 | -0.009155 | -0.13275 | 122.4152 | 122.4838 | 122.3282 | 0.16022 | 0.004578 | 0.091553 | -0.004577 | 0.091553 | 0.032044 | 0.19226 | 0.15564 | 122.4747 | 122.4792 | -0.20599 | -0.1648 | 122.2778 | 122.3557 | 122.2961 | 122.2778
2070.125 | 122.644 | -122.3511 | 0.086975 | -0.0036622 | 0.067855 | 0.01803 | 0.021403 | 0.0034372 | -0.0010468 | -0.00058311 | 0.0014953 | 0.023366 | 0.018634 | 0.018104 | 0.0028945 | 0.019666 | -0.0014931 | -0.013733 | 0.041199 | -0.041199 | 0.032043 | 0.19226 | 0.022888 | 0.068665 | 0.086975 | 0.036621 | -0.032043 | 0.09613 | 0.1831 | 0.09613 | 0.19226 | 122.3099 | -0.045776 | -0.054932 | 122.5433 | 122.4197 | 122.374 | 0.10986 | 0.064087 | 122.319 | -0.050354 | 0.009155 | 122.5342 | 122.5433 | 122.4472 | 0.2243 | 0.12817 | 0.23346 | 0.073242 | 0.21515 | 0.12817 | 0.082398 | 0.068664 | 122.3923 | 122.3877 | -0.12817 | -0.11902 | 122.3831 | 122.4472 | 122.3373 | 122.438
2071.8594 | 122.612 | -122.3557 | 0.10071 | -0.0036622 | 0.065933 | 0.014825 | 0.018839 | -0.0036124 | -0.0038238 | -0.0014377 | -0.0015565 | 0.023366 | 0.019062 | 0.0102 | -0.0026597 | 0.016675 | 0.00085667 | -0.013733 | 0.045776 | -0.032043 | 0 | 0.17853 | 0.059509 | 0.07782 | 0.045776 | 0.07782 | -0.041199 | 0.022888 | 0.14191 | 0.059509 | 0.14191 | 122.3236 | -0.054932 | -0.10071 | 122.5342 | 122.4335 | 122.4152 | 0.10986 | 0.091552 | 122.3145 | -0.022888 | -0.07782 | 122.4976 | 122.4976 | 122.4152 | 0.18311 | 0.10071 | 0.21057 | 0.032043 | 0.18311 | 0.064087 | 0.077819 | 0.11902 | 122.4014 | 122.4335 | -0.13275 | -0.14191 | 122.3557 | 122.3785 | 122.3419 | 122.4014
2073.6094 | 122.612 | -122.3557 | 0.10529 | 0.0039673 | 0.064651 | 0.014825 | 0.020762 | -0.0023306 | -0.0012604 | 0.00069849 | -0.0015565 | 0.022939 | 0.017994 | 0.025154 | 0.00011755 | 0.019025 | -0.0061929 | -0.082397 | 0.054932 | -0.036621 | -0.027466 | 0.1236 | 0.004578 | 0.036621 | 0.009155 | 0.054932 | -0.064087 | 0.032043 | 0.11902 | 0.027466 | 0.14648 | 122.319 | -0.050354 | -0.13275 | 122.4792 | 122.3923 | 122.3602 | 0.073242 | 0.041199 | 122.2916 | -0.050354 | -0.073243 | 122.4747 | 122.5021 | 122.3831 | 0.21057 | 0.091553 | 0.16022 | 0.009155 | 0.18311 | 0.09613 | 0.091553 | 0.11902 | 122.4106 | 122.4106 | -0.14191 | -0.16937 | 122.3282 | 122.3877 | 122.2733 | 122.3648
2075.3438 | 122.5571 | -122.3831 | 0.09613 | -0.011291 | 0.063583 | 0.015466 | 0.023112 | -0.002117 | -0.0040374 | 0.0015531 | -0.0015565 | 0.02358 | 0.022266 | 0.013405 | -0.0033005 | 0.018598 | 0.00021567 | -0.050354 | 0.054932 | -0.07782 | -0.041199 | 0.10529 | 0.004578 | 0.009155 | -0.022888 | 0.073242 | -0.07782 | -0.004578 | 0.073242 | -0.004578 | 0.10529 | 122.3053 | -0.041198 | -0.13733 | 122.4884 | 122.3923 | 122.3877 | 0.086975 | 0.082398 | 122.3053 | -0.022888 | -0.10071 | 122.4564 | 122.4884 | 122.3785 | 0.18311 | 0.073242 | 0.18311 | 0.036621 | 0.15106 | 0.073242 | 0.13275 | 0.15106 | 122.438 | 122.4564 | -0.17395 | -0.17395 | 122.3419 | 122.3785 | 122.3328 | 122.3602
2077.0938 | 122.6669 | -122.3602 | 0.082397 | -0.018921 | 0.062087 | 0.013971 | 0.020548 | -0.0027578 | -0.0019012 | -0.00036951 | 0.0014953 | 0.023366 | 0.018848 | 0.015968 | -0.00052345 | 0.016248 | -0.0032021 | -0.032043 | 0.036621 | -0.059509 | 0.027466 | 0.20142 | 0.07782 | 0.082397 | 0.07782 | 0.054932 | -0.045776 | 0.082397 | 0.1831 | 0.1236 | 0.1831 | 122.3007 | -0.045776 | -0.054931 | 122.5616 | 122.4426 | 122.438 | 0.14191 | 0.13733 | 122.3145 | -0.027465 | 0 | 122.5433 | 122.5433 | 122.4838 | 0.22888 | 0.16937 | 0.26093 | 0.086975 | 0.22888 | 0.12817 | 0.09613 | 0.10071 | 122.3969 | 122.4152 | -0.14191 | -0.12817 | 122.3877 | 122.4426 | 122.3282 | 122.438
2078.7812 | 122.6028 | -122.3694 | 0.11444 | -0.011291 | 0.064865 | 0.015466 | 0.020976 | -0.005535 | -0.0019012 | -0.0020785 | -0.0076599 | 0.024221 | 0.018848 | 0.015327 | -0.00095065 | 0.016462 | 0.00042947 | -0.022888 | 0.054932 | -0.041199 | 0.009155 | 0.16479 | 0.045776 | 0.059509 | 0.050354 | 0.064087 | -0.036621 | 0.036621 | 0.13733 | 0.059509 | 0.16022 | 122.3282 | -0.059509 | -0.10529 | 122.5342 | 122.4289 | 122.4152 | 0.10071 | 0.086975 | 122.3328 | -0.050354 | -0.07782 | 122.5067 | 122.5296 | 122.4289 | 0.19684 | 0.09613 | 0.20599 | 0.050354 | 0.17395 | 0.073242 | 0.096131 | 0.10071 | 122.4243 | 122.4335 | -0.15564 | -0.15106 | 122.3785 | 122.406 | 122.3465 | 122.4197
2080.5312 | 122.6852 | -122.374 | 0.073242 | -0.011291 | 0.066146 | 0.016321 | 0.022044 | -0.0027578 | -0.0033966 | -0.0029331 | 0.0014953 | 0.023793 | 0.018207 | 0.017891 | -0.0026597 | 0.019025 | -0.0014931 | -0.032043 | 0.032043 | -0.045776 | 0.050354 | 0.21515 | 0.086975 | 0.09613 | 0.10529 | 0.059509 | -0.050354 | 0.086975 | 0.19684 | 0.10071 | 0.19684 | 122.3282 | -0.041199 | -0.022888 | 122.5891 | 122.4701 | 122.4609 | 0.14191 | 0.13275 | 122.3236 | -0.013733 | 0.013733 | 122.5708 | 122.5708 | 122.4747 | 0.24719 | 0.15106 | 0.26093 | 0.09613 | 0.24719 | 0.13733 | 0.077819 | 0.10986 | 122.406 | 122.4335 | -0.11902 | -0.1236 | 122.4243 | 122.4609 | 122.3419 | 122.4792
2082.2656 | 122.612 | -122.374 | 0.10071 | -0.011291 | 0.066574 | 0.014185 | 0.021189 | -0.0019034 | -0.0012604 | -0.0046421 | -0.0076599 | 0.024007 | 0.019489 | 0.019173 | -0.0013779 | 0.016462 | 0.0025657 | -0.059509 | 0.059509 | -0.036621 | -0.036621 | 0.10986 | -0.004578 | 0.009155 | -0.013733 | 0.059509 | -0.050354 | 0.045776 | 0.10529 | 0.032043 | 0.13733 | 122.3373 | -0.041199 | -0.13733 | 122.4838 | 122.3831 | 122.3694 | 0.045776 | 0.032043 | 122.3236 | -0.041199 | -0.054932 | 122.4792 | 122.5113 | 122.406 | 0.18768 | 0.082397 | 0.14648 | 0 | 0.15564 | 0.09613 | 0.09613 | 0.10986 | 122.4335 | 122.4335 | -0.13733 | -0.15106 | 122.3373 | 122.4197 | 122.3145 | 122.3602
2083.9375 | 122.6395 | -122.3511 | 0.086975 | -0.011291 | 0.065505 | 0.016107 | 0.024394 | -0.0010488 | -0.0027556 | -0.0022921 | -0.0015565 | 0.022725 | 0.020343 | 0.016823 | 0.0031081 | 0.016462 | -0.0017069 | -0.086975 | 0.073242 | -0.068665 | -0.045776 | 0.073242 | -0.041199 | -0.004578 | 0.004578 | 0.068665 | -0.068665 | 0.082397 | 0.13275 | 0.045776 | 0.17395 | 122.2824 | -0.013733 | -0.13275 | 122.4243 | 122.3465 | 122.3099 | 0.064087 | 0.027466 | 122.2824 | -0.01831 | -0.004578 | 122.4838 | 122.525 | 122.3969 | 0.24261 | 0.11444 | 0.14191 | 0.022889 | 0.20142 | 0.15106 | 0.14191 | 0.13733 | 122.4243 | 122.4197 | -0.15564 | -0.15564 | 122.3053 | 122.4335 | 122.2641 | 122.3557
2085.6875 | 122.5479 | -122.3969 | 0.1236 | -0.0036622 | 0.067428 | 0.016321 | 0.021617 | 0.0036508 | -0.0016876 | -0.0014377 | 0.0014953 | 0.025716 | 0.019489 | 0.015968 | 0.00033115 | 0.01753 | -0.0053385 | -0.09613 | 0.09613 | -0.09613 | -0.11444 | 0.004578 | -0.10529 | -0.059509 | -0.09613 | 0.086975 | -0.07782 | -0.032043 | 0.032043 | -0.064087 | 0.09613 | 122.3007 | -0.027466 | -0.23804 | 122.4014 | 122.3373 | 122.2916 | 0.036621 | -0.009156 | 122.319 | -0.036621 | -0.15564 | 122.4289 | 122.493 | 122.3328 | 0.17395 | 0.013733 | 0.10071 | -0.018311 | 0.10986 | 0.045777 | 0.19226 | 0.16479 | 122.493 | 122.4838 | -0.21973 | -0.20142 | 122.2824 | 122.3648 | 122.3007 | 122.3007
2087.4531 | 122.5708 | -122.3923 | 0.1236 | 0.0039673 | 0.065078 | 0.015466 | 0.02183 | 0.00023275 | 0.00023496 | -0.00079691 | -0.0046081 | 0.025075 | 0.021625 | 0.016395 | -0.0026597 | 0.016889 | 0.0014975 | -0.082397 | 0.11444 | -0.07782 | -0.086975 | 0.036621 | -0.050354 | -0.032043 | -0.082397 | 0.10529 | -0.082397 | -0.032043 | 0.073242 | -0.013733 | 0.11902 | 122.3145 | -0.009155 | -0.21057 | 122.4289 | 122.3602 | 122.3419 | 0.045777 | 0.027466 | 122.3099 | -0.01831 | -0.15564 | 122.4655 | 122.5113 | 122.3785 | 0.20142 | 0.068664 | 0.11444 | -0.009155 | 0.15564 | 0.050354 | 0.19226 | 0.18768 | 122.5067 | 122.4976 | -0.20142 | -0.20599 | 122.3053 | 122.3602 | 122.3099 | 122.3099
2089.125 | 122.5433 | -122.4197 | 0.13275 | -0.0036622 | 0.067001 | 0.016534 | 0.026103 | -0.00083525 | -0.0012604 | -0.0020785 | 0.0014953 | 0.025502 | 0.020771 | 0.015114 | -0.0018051 | 0.020093 | -0.0012795 | -0.10529 | 0.09613 | -0.10071 | -0.11444 | 0.009155 | -0.11444 | -0.050354 | -0.10529 | 0.10986 | -0.068665 | -0.018311 | 0.027466 | -0.059509 | 0.10071 | 122.319 | -0.036621 | -0.24719 | 122.4289 | 122.3694 | 122.3053 | 0.050354 | -0.013733 | 122.3511 | -0.022888 | -0.15106 | 122.4472 | 122.5204 | 122.3602 | 0.16937 | 0.009156 | 0.10986 | -0.013733 | 0.096131 | 0.050354 | 0.19684 | 0.17853 | 122.5159 | 122.5296 | -0.23346 | -0.20142 | 122.3053 | 122.4014 | 122.3145 | 122.3145
2090.875 | 122.612 | -122.3877 | 0.09613 | -0.0036622 | 0.065078 | 0.017816 | 0.020976 | -0.0019034 | -0.004251 | 0.00027129 | -0.0015565 | 0.025075 | 0.019489 | 0.020027 | -0.0020187 | 0.020521 | -0.00042513 | -0.07782 | 0.064087 | -0.054932 | -0.045776 | 0.11902 | -0.004578 | 0.027466 | -0.013733 | 0.054932 | -0.054932 | 0.041199 | 0.10986 | 0.050354 | 0.15564 | 122.3328 | -0.032043 | -0.14191 | 122.5067 | 122.4152 | 122.3831 | 0.082398 | 0.050354 | 122.3328 | -0.041198 | -0.054931 | 122.4976 | 122.5433 | 122.438 | 0.21057 | 0.10529 | 0.17395 | 0.009156 | 0.16479 | 0.096131 | 0.11902 | 0.10986 | 122.4518 | 122.4426 | -0.15106 | -0.15106 | 122.3419 | 122.4289 | 122.3099 | 122.374
2092.625 | 122.5937 | -122.3602 | 0.10986 | -0.011291 | 0.066574 | 0.016534 | 0.025675 | 0.0015146 | -0.0029694 | 0.00048489 | -0.0015565 | 0.025716 | 0.020984 | 0.0095597 | -0.0018051 | 0.019666 | -0.00063873 | -0.050354 | 0.059509 | -0.07782 | -0.050354 | 0.09613 | -0.036621 | 0.004578 | 0.013733 | 0.09613 | -0.059509 | 0.022888 | 0.10071 | 0.027466 | 0.12817 | 122.2824 | -0.050354 | -0.16022 | 122.4564 | 122.3648 | 122.3236 | 0.082398 | 0.041199 | 122.3007 | -0.013733 | -0.086975 | 122.4609 | 122.4884 | 122.3877 | 0.18768 | 0.086975 | 0.17395 | 0.027466 | 0.16022 | 0.082397 | 0.13733 | 0.15564 | 122.4197 | 122.4564 | -0.18768 | -0.16937 | 122.3099 | 122.3831 | 122.3099 | 122.374
2094.3594 | 122.5433 | -122.3877 | 0.13275 | -0.0036622 | 0.070419 | 0.016107 | 0.023539 | -0.0029714 | -0.00083304 | 0.0013395 | -0.0046081 | 0.025502 | 0.019916 | 0.01255 | 0.00097195 | 0.018171 | -0.0012795 | -0.068665 | 0.064087 | -0.073242 | -0.082397 | 0.050354 | -0.082397 | -0.050354 | -0.059509 | 0.082397 | -0.073242 | -0.036621 | 0.036621 | -0.054932 | 0.091553 | 122.3145 | -0.068664 | -0.21515 | 122.438 | 122.3373 | 122.3053 | 0.022888 | -0.009155 | 122.3145 | -0.050354 | -0.16937 | 122.4243 | 122.4792 | 122.3328 | 0.16479 | 0.01831 | 0.1236 | -0.009155 | 0.10986 | 0.036621 | 0.13733 | 0.15564 | 122.4518 | 122.4701 | -0.20599 | -0.20599 | 122.3053 | 122.3511 | 122.319 | 122.3282
2096.0938 | 122.6578 | -122.3694 | 0.07782 | -0.011291 | 0.065933 | 0.016534 | 0.022471 | 0.001301 | -0.0019012 | 0.00027129 | -0.0046081 | 0.023793 | 0.022266 | 0.015755 | 0.0031081 | 0.017316 | -0.0014931 | -0.10529 | 0.082397 | -0.073242 | -0.054932 | 0.082397 | -0.050354 | -0.009155 | 0.018311 | 0.068665 | -0.059509 | 0.068665 | 0.13733 | 0.059509 | 0.17853 | 122.2961 | 0.004577 | -0.13275 | 122.4518 | 122.3602 | 122.319 | 0.064087 | 0.022888 | 122.3099 | -0.009155 | -0.009155 | 122.5067 | 122.5479 | 122.4289 | 0.23804 | 0.11902 | 0.15564 | 0.01831 | 0.19684 | 0.12817 | 0.15564 | 0.12817 | 122.4518 | 122.438 | -0.15106 | -0.13733 | 122.3145 | 122.438 | 122.2641 | 122.3877
2097.8594 | 122.6761 | -122.3694 | 0.086975 | 0.011597 | 0.065719 | 0.016321 | 0.021189 | 0.00023275 | 0.00066216 | 0.0019803 | 0.0014953 | 0.023366 | 0.019703 | 0.020241 | 0.0016129 | 0.019452 | -0.0023477 | 0.004578 | 0.054932 | -0.050354 | 0.018311 | 0.19226 | 0.022888 | 0.050354 | 0.091553 | 0.045776 | -0.036621 | 0.11444 | 0.16937 | 0.082397 | 0.20142 | 122.319 | -0.032043 | -0.068664 | 122.5616 | 122.4197 | 122.3923 | 0.10071 | 0.073242 | 122.3328 | -0.041199 | 0.027466 | 122.5388 | 122.5708 | 122.4518 | 0.23804 | 0.11902 | 0.24261 | 0.068665 | 0.20599 | 0.15106 | 0.10529 | 0.082397 | 122.4243 | 122.4152 | -0.13733 | -0.1236 | 122.3877 | 122.4838 | 122.374 | 122.4609
2099.5469 | 122.6624 | -122.406 | 0.086975 | -0.0036622 | 0.064224 | 0.014185 | 0.019053 | -0.00019445 | -0.0046782 | 0.00069849 | -0.0046081 | 0.024434 | 0.019275 | 0.020668 | -0.0033005 | 0.018171 | -0.0017069 | -0.022888 | 0.045776 | -0.036621 | 0.018311 | 0.17853 | 0.068665 | 0.07782 | 0.064087 | 0.064087 | -0.054932 | 0.054932 | 0.16937 | 0.091553 | 0.15564 | 122.3694 | -0.041199 | -0.068664 | 122.5845 | 122.4838 | 122.4747 | 0.11444 | 0.10529 | 122.3511 | -0.022888 | -0.032043 | 122.5754 | 122.5616 | 122.4976 | 0.21057 | 0.14649 | 0.21515 | 0.054932 | 0.22431 | 0.10986 | 0.082397 | 0.11902 | 122.4518 | 122.4701 | -0.1236 | -0.14191 | 122.4243 | 122.4609 | 122.3831 | 122.4701
2101.2969 | 122.5662 | -122.406 | 0.11444 | -0.011291 | 0.065719 | 0.014398 | 0.025035 | -0.0016898 | 0.00044856 | -0.00015591 | -0.0046081 | 0.024434 | 0.019275 | 0.011055 | 0.00097195 | 0.017957 | 0.00021567 | -0.09613 | 0.091553 | -0.082397 | -0.10529 | 0.018311 | -0.10986 | -0.036621 | -0.086975 | 0.07782 | -0.086975 | -0.022888 | 0.036621 | -0.041199 | 0.10529 | 122.3236 | -0.022888 | -0.21973 | 122.4243 | 122.3694 | 122.2961 | 0.045776 | -0.027466 | 122.319 | -0.036621 | -0.13733 | 122.4426 | 122.5113 | 122.3648 | 0.19226 | 0.045776 | 0.10071 | -0.022889 | 0.1236 | 0.064087 | 0.17395 | 0.16479 | 122.4976 | 122.4838 | -0.19684 | -0.20142 | 122.3007 | 122.3831 | 122.3099 | 122.319
2103.0312 | 122.6486 | -122.374 | 0.086975 | -0.018921 | 0.06401 | 0.015039 | 0.020335 | -0.0012624 | -0.0021148 | -0.0037875 | -0.0046081 | 0.023366 | 0.019062 | 0.014259 | 0.00033115 | 0.01988 | 0.0010703 | -0.086975 | 0.041199 | -0.064087 | -0.050354 | 0.10986 | 0.004578 | 0.018311 | -0.018311 | 0.059509 | -0.064087 | 0.027466 | 0.11444 | 0.032043 | 0.14648 | 122.3099 | -0.045776 | -0.13733 | 122.4838 | 122.3923 | 122.3785 | 0.082398 | 0.068665 | 122.3099 | -0.027466 | -0.059509 | 122.4884 | 122.5204 | 122.406 | 0.21057 | 0.09613 | 0.17395 | 0.013733 | 0.17853 | 0.091553 | 0.10529 | 0.1236 | 122.4152 | 122.4335 | -0.15106 | -0.15106 | 122.3236 | 122.4014 | 122.287 | 122.3557
2104.7031 | 122.6532 | -122.3511 | 0.10071 | -0.0036622 | 0.062942 | 0.014612 | 0.020548 | -0.0019034 | -0.0010468 | -0.0010105 | -0.0015565 | 0.021871 | 0.01778 | 0.020454 | -0.0035141 | 0.017957 | 0.00064307 | -0.027466 | 0.041199 | -0.045776 | 0.018311 | 0.18768 | 0.054932 | 0.073242 | 0.059509 | 0.07782 | -0.059509 | 0.045776 | 0.16022 | 0.07782 | 0.16479 | 122.3053 | -0.059509 | -0.082397 | 122.5388 | 122.4243 | 122.406 | 0.11902 | 0.10071 | 122.2916 | -0.022888 | -0.054932 | 122.5113 | 122.5159 | 122.4289 | 0.2243 | 0.13733 | 0.23346 | 0.064087 | 0.21973 | 0.10528 | 0.086975 | 0.13733 | 122.3923 | 122.4289 | -0.14648 | -0.16022 | 122.3694 | 122.3969 | 122.3236 | 122.4106
2106.4531 | 122.612 | -122.4243 | 0.1236 | 0.0039673 | 0.067642 | 0.01568 | 0.022471 | -0.001476 | -0.0033966 | 5.7688e-05 | -0.0046081 | 0.027211 | 0.020343 | 0.015541 | -0.00052345 | 0.014325 | -0.0023477 | -0.082397 | 0.09613 | -0.091553 | -0.064087 | 0.054932 | -0.041199 | -0.022888 | -0.036621 | 0.082397 | -0.082397 | 0.004578 | 0.09613 | 0 | 0.13275 | 122.3328 | -0.027466 | -0.18768 | 122.4792 | 122.4014 | 122.3831 | 0.068665 | 0.050354 | 122.3419 | -0.041199 | -0.11902 | 122.5204 | 122.5571 | 122.4243 | 0.21515 | 0.082397 | 0.14649 | 0.027466 | 0.17853 | 0.086975 | 0.18768 | 0.16479 | 122.5204 | 122.5067 | -0.21515 | -0.20599 | 122.3602 | 122.4289 | 122.3419 | 122.3877
2108.2031 | 122.644 | -122.3694 | 0.10529 | 0.0039673 | 0.067001 | 0.019312 | 0.02183 | -0.0046804 | -0.00083304 | -0.0016513 | -0.0015565 | 0.024221 | 0.019703 | 0.014046 | 0.0011855 | 0.01753 | -0.0014931 | -0.045776 | 0.036621 | -0.045776 | -0.004578 | 0.17395 | 0.004578 | 0.045776 | 0.036621 | 0.054932 | -0.059509 | 0.054932 | 0.12817 | 0.050354 | 0.16479 | 122.3236 | -0.068665 | -0.10986 | 122.5433 | 122.4152 | 122.374 | 0.091552 | 0.050354 | 122.3099 | -0.050354 | -0.050354 | 122.4976 | 122.5342 | 122.4197 | 0.2243 | 0.10986 | 0.21973 | 0.041198 | 0.18768 | 0.11444 | 0.082397 | 0.11444 | 122.406 | 122.4243 | -0.15106 | -0.16479 | 122.3648 | 122.4243 | 122.3236 | 122.406
2109.8906 | 122.7173 | -122.3831 | 0.086975 | -0.011291 | 0.063796 | 0.016321 | 0.018626 | -0.00040805 | -0.00061944 | -0.0025057 | 0.0014953 | 0.022084 | 0.018207 | 0.018318 | -0.00030965 | 0.019666 | -0.0012795 | -0.018311 | 0.059509 | -0.045776 | 0.027466 | 0.19684 | 0.073242 | 0.091553 | 0.10986 | 0.050354 | -0.045776 | 0.10071 | 0.19684 | 0.13275 | 0.20142 | 122.3373 | -0.027466 | -0.059509 | 122.58 | 122.4747 | 122.4564 | 0.13733 | 0.11902 | 122.3373 | -0.036621 | 0.013733 | 122.58 | 122.5845 | 122.5159 | 0.24719 | 0.17853 | 0.24261 | 0.073242 | 0.24261 | 0.14648 | 0.10528 | 0.09613 | 122.4426 | 122.4335 | -0.13275 | -0.13275 | 122.4106 | 122.4838 | 122.3648 | 122.493
2111.625 | 122.6898 | -122.3557 | 0.086975 | -0.0036622 | 0.066146 | 0.018884 | 0.020121 | -0.0033986 | -0.0036102 | -0.0040011 | -0.0015565 | 0.024007 | 0.018421 | 0.011696 | -0.0033005 | 0.01753 | 2.068e-06 | -0.013733 | 0.050354 | -0.036621 | 0.036621 | 0.18768 | 0.073242 | 0.07782 | 0.082397 | 0.036621 | -0.054932 | 0.073242 | 0.17853 | 0.10529 | 0.18768 | 122.319 | -0.036621 | -0.050354 | 122.5433 | 122.4335 | 122.4289 | 0.11444 | 0.10986 | 122.3007 | -0.050354 | -0.013733 | 122.5342 | 122.5433 | 122.4609 | 0.24261 | 0.16022 | 0.2243 | 0.073242 | 0.23346 | 0.12817 | 0.086975 | 0.091553 | 122.406 | 122.3923 | -0.1236 | -0.14191 | 122.3923 | 122.4289 | 122.3419 | 122.438
2113.375 | 122.7081 | -122.3694 | 0.07782 | 0.0039673 | 0.06636 | 0.016534 | 0.019908 | 0.00066015 | 0.00066216 | 0.0013395 | 0.0014953 | 0.024861 | 0.019489 | 0.017464 | 0.0011855 | 0.018171 | 0.00085667 | -0.004578 | 0.036621 | -0.054932 | 0.045776 | 0.16937 | 0.027466 | 0.050354 | 0.091553 | 0.059509 | -0.045776 | 0.10071 | 0.17395 | 0.091553 | 0.19684 | 122.3145 | -0.041199 | -0.032044 | 122.5388 | 122.4197 | 122.3969 | 0.10529 | 0.082398 | 122.3236 | -0.018311 | 0.022888 | 122.5433 | 122.5662 | 122.4609 | 0.24261 | 0.13733 | 0.22431 | 0.10071 | 0.21973 | 0.14648 | 0.091553 | 0.10528 | 122.406 | 122.4289 | -0.13275 | -0.1236 | 122.4152 | 122.4701 | 122.3648 | 122.4609
2115.0625 | 122.6532 | -122.3831 | 0.09613 | -0.0036622 | 0.065292 | 0.016962 | 0.021617 | -0.0036124 | -0.0021148 | -0.0031467 | -0.0046081 | 0.024221 | 0.020771 | 0.0087051 | -0.00073705 | 0.018171 | 2.068e-06 | -0.068665 | 0.045776 | -0.041199 | -0.041199 | 0.1236 | -0.018311 | 0.032043 | 0.009155 | 0.073242 | -0.068665 | 0.036621 | 0.11444 | 0.027466 | 0.15106 | 122.3419 | -0.050354 | -0.13733 | 122.5067 | 122.4152 | 122.3648 | 0.073242 | 0.022888 | 122.3145 | -0.022888 | -0.059509 | 122.4976 | 122.5342 | 122.4106 | 0.21973 | 0.096131 | 0.16479 | 0 | 0.18311 | 0.10529 | 0.086975 | 0.14191 | 122.4289 | 122.4564 | -0.13733 | -0.16479 | 122.3419 | 122.4197 | 122.3145 | 122.3923
2116.8125 | 122.5571 | -122.4106 | 0.11902 | -0.011291 | 0.066146 | 0.016962 | 0.025248 | -0.0023306 | -0.0019012 | 0.00091209 | -0.0015565 | 0.025502 | 0.021412 | 0.011909 | -0.00030965 | 0.017743 | -0.0021341 | -0.073242 | 0.082397 | -0.07782 | -0.086975 | 0.032043 | -0.09613 | -0.064087 | -0.086975 | 0.10071 | -0.082397 | -0.022888 | 0.027466 | -0.059509 | 0.082397 | 122.3328 | -0.036622 | -0.20599 | 122.4426 | 122.3465 | 122.3145 | 0.013733 | -0.01831 | 122.3282 | -0.018311 | -0.14191 | 122.438 | 122.493 | 122.3511 | 0.16479 | 0.022888 | 0.10986 | -0.009155 | 0.10986 | 0.059509 | 0.16022 | 0.18311 | 122.493 | 122.5113 | -0.19684 | -0.20142 | 122.3236 | 122.3877 | 122.3373 | 122.3236
2118.5625 | 122.612 | -122.4243 | 0.12817 | -0.011291 | 0.065719 | 0.016534 | 0.023966 | -0.002117 | -0.0044646 | -0.0044285 | -0.0046081 | 0.024007 | 0.021625 | 0.017677 | -0.0022325 | 0.018384 | 0.00042947 | -0.10071 | 0.086975 | -0.073242 | -0.10529 | 0.022888 | -0.036621 | -0.018311 | -0.082397 | 0.09613 | -0.073242 | -0.036621 | 0.073242 | -0.013733 | 0.10986 | 122.3511 | -0.041199 | -0.23346 | 122.4472 | 122.406 | 122.3877 | 0.054931 | 0.036621 | 122.3511 | -0.032044 | -0.1648 | 122.4976 | 122.5342 | 122.4106 | 0.18311 | 0.059509 | 0.09613 | -0.032044 | 0.14648 | 0.036621 | 0.16022 | 0.16937 | 122.5113 | 122.5204 | -0.20142 | -0.20142 | 122.319 | 122.3877 | 122.3236 | 122.3419
2120.2969 | 122.5983 | -122.4197 | 0.09613 | -0.011291 | 0.068069 | 0.015253 | 0.023112 | -0.0010488 | -0.0012604 | 5.7688e-05 | -0.0046081 | 0.024221 | 0.020984 | 0.016609 | 0.00097195 | 0.018171 | -0.0036295 | -0.045776 | 0.059509 | -0.068665 | -0.045776 | 0.10529 | -0.045776 | -0.013733 | -0.009155 | 0.082397 | -0.073242 | 0.004578 | 0.091553 | -0.009155 | 0.1236 | 122.3511 | -0.036621 | -0.14191 | 122.525 | 122.406 | 122.374 | 0.054932 | 0.022889 | 122.3465 | -0.013733 | -0.091552 | 122.5113 | 122.5433 | 122.4106 | 0.19684 | 0.064087 | 0.17395 | 0.022889 | 0.16479 | 0.07782 | 0.12817 | 0.15564 | 122.4792 | 122.5021 | -0.16479 | -0.16937 | 122.374 | 122.4243 | 122.374 | 122.4106
2122.0312 | 122.6624 | -122.406 | 0.086975 | -0.0036622 | 0.064224 | 0.016962 | 0.021403 | -0.0016898 | -0.0027556 | -0.0014377 | 0.0014953 | 0.022084 | 0.018421 | 0.020882 | 0.00054475 | 0.020734 | 0.0017111 | -0.068665 | 0.050354 | -0.041199 | -0.036621 | 0.10986 | -0.013733 | 0.018311 | 0.009155 | 0.054932 | -0.050354 | 0.050354 | 0.11902 | 0.041199 | 0.14648 | 122.3648 | -0.036621 | -0.1236 | 122.5159 | 122.4243 | 122.3923 | 0.05951 | 0.027466 | 122.3557 | -0.032043 | -0.036621 | 122.525 | 122.5525 | 122.4472 | 0.19684 | 0.091553 | 0.15106 | 0.004578 | 0.16937 | 0.10071 | 0.091553 | 0.10529 | 122.4564 | 122.4609 | -0.12817 | -0.13733 | 122.3694 | 122.4564 | 122.3373 | 122.4152
2123.7188 | 122.6624 | -122.3923 | 0.086975 | 0.0039673 | 0.065078 | 0.016534 | 0.023112 | 0.0032236 | -0.003183 | -0.00015591 | -0.0046081 | 0.026357 | 0.018634 | 0.01725 | 0.0016129 | 0.017743 | 0.0025657 | -0.09613 | 0.073242 | -0.073242 | -0.086975 | 0.064087 | -0.073242 | -0.036621 | -0.013733 | 0.068665 | -0.073242 | 0.036621 | 0.1236 | 0.036621 | 0.16479 | 122.319 | -0.013733 | -0.17395 | 122.4564 | 122.3557 | 122.319 | 0.036621 | 0 | 122.319 | -0.01831 | -0.050354 | 122.5159 | 122.5571 | 122.4289 | 0.23804 | 0.10986 | 0.13733 | -0.013733 | 0.19684 | 0.10986 | 0.14648 | 0.14191 | 122.4655 | 122.4609 | -0.16022 | -0.16022 | 122.3053 | 122.4289 | 122.2961 | 122.3785
2125.4531 | 122.7081 | -122.3831 | 0.091553 | -0.0036622 | 0.067001 | 0.014185 | 0.020762 | -0.00062165 | -0.0036102 | 5.7688e-05 | -0.0015565 | 0.022512 | 0.018421 | 0.017464 | -0.0022325 | 0.01753 | 0.0025657 | -0.036621 | 0.045776 | -0.054932 | 0.032043 | 0.21057 | 0.059509 | 0.082397 | 0.091553 | 0.036621 | -0.036621 | 0.07782 | 0.20142 | 0.1236 | 0.18768 | 122.3282 | -0.045777 | -0.05951 | 122.5937 | 122.4655 | 122.4426 | 0.13733 | 0.11444 | 122.3465 | -0.054932 | -0.013733 | 122.5845 | 122.5708 | 122.5067 | 0.2243 | 0.16022 | 0.2655 | 0.086975 | 0.23804 | 0.11444 | 0.10071 | 0.073242 | 122.4289 | 122.4197 | -0.14649 | -0.12817 | 122.4152 | 122.4609 | 122.3465 | 122.4747
2127.1875 | 122.5662 | -122.4518 | 0.12817 | -0.0036622 | 0.065719 | 0.016107 | 0.02183 | -0.0025442 | -0.0036102 | 0.0011257 | 0.0014953 | 0.02358 | 0.018634 | 0.016395 | -0.0062913 | 0.014966 | -0.00063873 | -0.11444 | 0.09613 | -0.086975 | -0.10071 | 0.036621 | -0.064087 | -0.022888 | -0.068665 | 0.10529 | -0.082397 | -0.036621 | 0.045776 | -0.050354 | 0.086975 | 122.3648 | -0.032044 | -0.22888 | 122.4884 | 122.4289 | 122.3877 | 0.064087 | 0.022888 | 122.3694 | -0.022888 | -0.1648 | 122.4976 | 122.5388 | 122.4014 | 0.16937 | 0.032043 | 0.1236 | -0.013733 | 0.12817 | 0.045776 | 0.1831 | 0.18768 | 122.5479 | 122.5571 | -0.21515 | -0.21057 | 122.3511 | 122.4152 | 122.3373 | 122.3831
2128.875 | 122.5937 | -122.4472 | 0.11444 | 0.0039673 | 0.066146 | 0.016107 | 0.020121 | 0.0023692 | -0.0040374 | -0.0031467 | -0.0015565 | 0.024861 | 0.019275 | 0.017677 | -0.0041551 | 0.015394 | -0.0029885 | -0.054932 | 0.059509 | -0.068665 | -0.07782 | 0.091553 | -0.027466 | -0.018311 | -0.059509 | 0.07782 | -0.068665 | -0.027466 | 0.064087 | -0.013733 | 0.082397 | 122.3785 | -0.054932 | -0.19226 | 122.5388 | 122.4289 | 122.4197 | 0.050354 | 0.041199 | 122.3785 | -0.036621 | -0.14191 | 122.5113 | 122.5296 | 122.4335 | 0.15106 | 0.054932 | 0.16022 | -0.009155 | 0.13275 | 0.041199 | 0.12817 | 0.14649 | 122.5067 | 122.525 | -0.18311 | -0.18311 | 122.3694 | 122.4197 | 122.3923 | 122.3877
2130.6094 | 122.6212 | -122.4197 | 0.10071 | -0.011291 | 0.06401 | 0.014398 | 0.022257 | -0.0019034 | -0.0040374 | -0.00036951 | -0.0015565 | 0.025929 | 0.018207 | 0.013405 | 0.0020401 | 0.016462 | -0.0017069 | -0.054932 | 0.082397 | -0.082397 | -0.032043 | 0.10529 | -0.018311 | 0.009155 | -0.004578 | 0.09613 | -0.064087 | 0.032043 | 0.10071 | 0.013733 | 0.13275 | 122.3373 | -0.018311 | -0.13275 | 122.525 | 122.4289 | 122.4014 | 0.091552 | 0.064086 | 122.3557 | -0.004578 | -0.068665 | 122.5204 | 122.5525 | 122.4335 | 0.19684 | 0.07782 | 0.18768 | 0.050354 | 0.1648 | 0.09613 | 0.16479 | 0.16022 | 122.5021 | 122.5159 | -0.18311 | -0.1648 | 122.3877 | 122.4518 | 122.3648 | 122.4152
2132.3594 | 122.5845 | -122.4472 | 0.11902 | -0.011291 | 0.065505 | 0.015894 | 0.022898 | -0.002117 | -0.0016876 | -0.0025057 | -0.0046081 | 0.024221 | 0.020343 | 0.02195 | -0.0033005 | 0.017103 | 0.00042947 | -0.073242 | 0.059509 | -0.054932 | -0.073242 | 0.054932 | -0.018311 | -0.018311 | -0.073242 | 0.082397 | -0.086975 | -0.027466 | 0.068665 | -0.018311 | 0.091553 | 122.3923 | -0.05951 | -0.19226 | 122.5021 | 122.4289 | 122.4289 | 0.036621 | 0.036621 | 122.3602 | -0.036622 | -0.14649 | 122.5159 | 122.5388 | 122.4289 | 0.17853 | 0.068664 | 0.10986 | -0.01831 | 0.15564 | 0.059509 | 0.11444 | 0.16937 | 122.5067 | 122.5296 | -0.17395 | -0.20599 | 122.374 | 122.4197 | 122.374 | 122.374
2134.0469 | 122.7127 | -122.3923 | 0.091553 | -0.0036622 | 0.064651 | 0.013971 | 0.020335 | -0.0042532 | -0.001474 | -0.0018649 | 0.0014953 | 0.023366 | 0.019703 | 0.013405 | -0.00073705 | 0.016462 | -0.0021341 | -0.054932 | 0.054932 | -0.041199 | 0.004578 | 0.17395 | 0.041199 | 0.07782 | 0.054932 | 0.045776 | -0.045776 | 0.091553 | 0.21057 | 0.11902 | 0.21515 | 122.3511 | -0.036621 | -0.086975 | 122.5662 | 122.4701 | 122.4335 | 0.11902 | 0.082398 | 122.3465 | -0.045777 | 0 | 122.6028 | 122.6074 | 122.5113 | 0.26093 | 0.16479 | 0.21515 | 0.045777 | 0.25635 | 0.13733 | 0.096131 | 0.091552 | 122.4472 | 122.438 | -0.13275 | -0.13733 | 122.3969 | 122.4838 | 122.3373 | 122.4472
2135.7969 | 122.6395 | -122.4289 | 0.10071 | -0.011291 | 0.067001 | 0.017175 | 0.024394 | 0.0042918 | -0.0021148 | -0.0010105 | -0.0046081 | 0.024861 | 0.019489 | 0.015541 | 0.00033115 | 0.018598 | -0.0051247 | -0.032043 | 0.082397 | -0.086975 | -0.045776 | 0.10529 | -0.018311 | 0.004578 | 0.027466 | 0.07782 | -0.073242 | 0.032043 | 0.10986 | 0.004578 | 0.14191 | 122.3419 | -0.018311 | -0.14648 | 122.5342 | 122.4335 | 122.4106 | 0.091553 | 0.068664 | 122.3557 | -0.022888 | -0.068665 | 122.5388 | 122.5708 | 122.4335 | 0.21515 | 0.07782 | 0.19226 | 0.041199 | 0.18311 | 0.10529 | 0.16937 | 0.15106 | 122.5113 | 122.5067 | -0.18768 | -0.17395 | 122.3831 | 122.4609 | 122.3969 | 122.4564
2137.5312 | 122.7219 | -122.4197 | 0.086975 | -0.0036622 | 0.06401 | 0.018671 | 0.022898 | -0.0019034 | -0.0012604 | 0.0017667 | -0.0046081 | 0.024434 | 0.01778 | 0.019813 | 0.0033217 | 0.020093 | -0.0021341 | -0.036621 | 0.054932 | -0.045776 | -0.013733 | 0.13733 | -0.009155 | 0.050354 | 0.059509 | 0.054932 | -0.022888 | 0.11444 | 0.16479 | 0.09613 | 0.21973 | 122.374 | -0.032043 | -0.10071 | 122.5571 | 122.4701 | 122.4106 | 0.09613 | 0.036621 | 122.3969 | -0.032043 | 0.027466 | 122.5845 | 122.6395 | 122.5159 | 0.24261 | 0.11902 | 0.18311 | 0.032043 | 0.18768 | 0.13733 | 0.10071 | 0.07782 | 122.4747 | 122.4747 | -0.13275 | -0.10986 | 122.406 | 122.5342 | 122.3831 | 122.4792
2139.2812 | 122.6761 | -122.4014 | 0.064087 | -0.0036622 | 0.066574 | 0.017175 | 0.022044 | 0.001301 | -0.001474 | -0.00079691 | -0.0076599 | 0.024648 | 0.017353 | 0.016182 | 0.00075835 | 0.020307 | -0.0029885 | -0.018311 | 0.041199 | -0.022888 | 0.027466 | 0.17853 | 0.036621 | 0.059509 | 0.07782 | 0.054932 | -0.041199 | 0.091553 | 0.15564 | 0.082397 | 0.19684 | 122.3785 | -0.022888 | -0.036621 | 122.58 | 122.4609 | 122.438 | 0.082397 | 0.059509 | 122.3602 | -0.009155 | 0.027466 | 122.5571 | 122.5983 | 122.4838 | 0.23804 | 0.1236 | 0.20142 | 0.050354 | 0.19684 | 0.13275 | 0.064087 | 0.096131 | 122.4426 | 122.4564 | -0.086975 | -0.10529 | 122.4289 | 122.493 | 122.3831 | 122.4792
2141.0312 | 122.6852 | -122.3831 | 0.07782 | -0.0036622 | 0.063796 | 0.014825 | 0.02418 | 0.0032236 | -0.0019012 | 0.0015531 | 0.0014953 | 0.025075 | 0.017353 | 0.022804 | -0.0024461 | 0.019666 | -0.00042513 | -0.041199 | 0.041199 | -0.032043 | 0.022888 | 0.17395 | 0.009155 | 0.041199 | 0.064087 | 0.054932 | -0.045776 | 0.064087 | 0.14648 | 0.064087 | 0.16937 | 122.3511 | -0.036621 | -0.054932 | 122.5571 | 122.4243 | 122.3923 | 0.073242 | 0.041198 | 122.3373 | -0.022888 | -0.013733 | 122.5296 | 122.5525 | 122.4472 | 0.21515 | 0.10986 | 0.20599 | 0.054931 | 0.19226 | 0.10986 | 0.073242 | 0.10071 | 122.4243 | 122.438 | -0.10986 | -0.1236 | 122.406 | 122.4472 | 122.3419 | 122.4472
2142.7656 | 122.7036 | -122.3923 | 0.082397 | -0.011291 | 0.066787 | 0.01803 | 0.022471 | -0.001476 | -0.00061944 | 0.00027129 | -0.0046081 | 0.024221 | 0.018848 | 0.019386 | -0.00030965 | 0.018384 | -0.0053385 | -0.018311 | 0.032043 | -0.045776 | 0.027466 | 0.1831 | 0.027466 | 0.059509 | 0.10986 | 0.050354 | -0.050354 | 0.09613 | 0.17395 | 0.091553 | 0.19684 | 122.3465 | -0.050354 | -0.054931 | 122.5754 | 122.4518 | 122.4197 | 0.10528 | 0.073242 | 122.3419 | -0.032043 | 0.013733 | 122.5662 | 122.5891 | 122.4838 | 0.24719 | 0.14191 | 0.22888 | 0.073242 | 0.2243 | 0.14648 | 0.077819 | 0.10071 | 122.4243 | 122.4426 | -0.12817 | -0.13275 | 122.4197 | 122.4884 | 122.374 | 122.5021
2144.4531 | 122.5983 | -122.4335 | 0.11902 | -0.018921 | 0.066146 | 0.013544 | 0.022471 | -0.0010488 | -0.0019012 | -0.00058311 | 0.0014953 | 0.025502 | 0.018848 | 0.0080643 | -0.0037277 | 0.015607 | -0.0021341 | -0.10071 | 0.09613 | -0.07782 | -0.10071 | 0.036621 | -0.054932 | -0.013733 | -0.073242 | 0.10071 | -0.091553 | -0.036621 | 0.036621 | -0.022888 | 0.10071 | 122.3557 | -0.022889 | -0.21973 | 122.4701 | 122.4197 | 122.3785 | 0.064087 | 0.022888 | 122.3419 | -0.018311 | -0.15564 | 122.4701 | 122.5342 | 122.4106 | 0.19226 | 0.068665 | 0.11444 | -0.022888 | 0.12817 | 0.054932 | 0.17395 | 0.19226 | 122.5296 | 122.5342 | -0.19684 | -0.21057 | 122.3328 | 122.3969 | 122.3328 | 122.3602
2146.2031 | 122.6669 | -122.4335 | 0.09613 | -0.0036622 | 0.06401 | 0.016962 | 0.020762 | 0.0019418 | -0.0021148 | 0.0015531 | 0.0045471 | 0.023152 | 0.019062 | 0.019173 | -0.00052345 | 0.017316 | 0.0021383 | -0.068665 | 0.045776 | -0.064087 | -0.045776 | 0.11444 | -0.022888 | 0.022888 | 0 | 0.064087 | -0.054932 | 0.045776 | 0.10986 | 0.054932 | 0.14648 | 122.3694 | -0.050354 | -0.14191 | 122.5479 | 122.4564 | 122.4106 | 0.086975 | 0.041199 | 122.3785 | -0.032043 | -0.050354 | 122.5433 | 122.58 | 122.4884 | 0.20142 | 0.10986 | 0.17853 | 0.018311 | 0.16479 | 0.10071 | 0.10986 | 0.11902 | 122.4792 | 122.4976 | -0.16022 | -0.15106 | 122.3877 | 122.4792 | 122.3648 | 122.4335
2147.9531 | 122.6578 | -122.4335 | 0.1236 | -0.0036622 | 0.066146 | 0.015039 | 0.021189 | -0.0025442 | -0.0033966 | -0.00036951 | -0.0015565 | 0.023152 | 0.018848 | 0.011909 | -0.0028733 | 0.016889 | 2.068e-06 | -0.027466 | 0.050354 | -0.050354 | 0.018311 | 0.15564 | 0.050354 | 0.068665 | 0.036621 | 0.045776 | -0.036621 | 0.022888 | 0.13275 | 0.059509 | 0.15106 | 122.3831 | -0.073242 | -0.10528 | 122.5891 | 122.5021 | 122.4838 | 0.11902 | 0.10071 | 122.3969 | -0.07782 | -0.10071 | 122.5662 | 122.5845 | 122.493 | 0.18768 | 0.09613 | 0.20599 | 0.068665 | 0.16937 | 0.059509 | 0.10071 | 0.082397 | 122.4838 | 122.4792 | -0.17395 | -0.16022 | 122.4518 | 122.4564 | 122.406 | 122.4701
2149.6406 | 122.7264 | -122.4106 | 0.086975 | -0.0036622 | 0.067642 | 0.016321 | 0.021403 | 0.001301 | -0.001474 | -0.0025057 | -0.0015565 | 0.025929 | 0.018207 | 0.021736 | 0.0013991 | 0.018384 | -0.0010659 | -0.045776 | 0.059509 | -0.054932 | -0.018311 | 0.12817 | -0.004578 | 0.036621 | 0.041199 | 0.045776 | -0.050354 | 0.09613 | 0.16479 | 0.068665 | 0.20599 | 122.3557 | -0.027466 | -0.10529 | 122.5388 | 122.4472 | 122.406 | 0.091553 | 0.050354 | 122.3602 | -0.041199 | 0.009155 | 122.5754 | 122.6166 | 122.4792 | 0.25635 | 0.11902 | 0.18311 | 0.036621 | 0.21515 | 0.14648 | 0.11444 | 0.09613 | 122.4701 | 122.4564 | -0.14191 | -0.13733 | 122.3923 | 122.5067 | 122.3648 | 122.4518
2151.3906 | 122.7081 | -122.4243 | 0.10071 | -0.0036622 | 0.066787 | 0.017175 | 0.021617 | -0.0016898 | -0.004892 | 0.00048489 | 0.0045471 | 0.023793 | 0.02013 | 0.015327 | -0.0022325 | 0.017316 | -0.0027749 | -0.032043 | 0.041199 | -0.059509 | 0.027466 | 0.21057 | 0.054932 | 0.07782 | 0.064087 | 0.068665 | -0.032043 | 0.07782 | 0.16937 | 0.10071 | 0.19226 | 122.3648 | -0.059509 | -0.073242 | 122.6349 | 122.5021 | 122.4792 | 0.13733 | 0.11444 | 122.3923 | -0.032043 | -0.022888 | 122.5937 | 122.6166 | 122.525 | 0.2243 | 0.13275 | 0.27008 | 0.086975 | 0.20142 | 0.10986 | 0.10071 | 0.10071 | 122.4655 | 122.493 | -0.16022 | -0.13275 | 122.4518 | 122.5021 | 122.3923 | 122.4884
2153.0625 | 122.644 | -122.4243 | 0.10986 | -0.0036622 | 0.066787 | 0.018671 | 0.025675 | 0.00087375 | -0.004251 | -0.0029331 | -0.0046081 | 0.025289 | 0.017994 | 0.0087051 | -0.0022325 | 0.014753 | -0.0034159 | -0.041199 | 0.073242 | -0.073242 | -0.045776 | 0.10071 | -0.022888 | 0.013733 | 0.009155 | 0.082397 | -0.064087 | 0.027466 | 0.10529 | 0.022888 | 0.14648 | 122.3511 | -0.036621 | -0.15564 | 122.525 | 122.438 | 122.4014 | 0.086975 | 0.050354 | 122.3602 | -0.027466 | -0.082397 | 122.5296 | 122.5708 | 122.4472 | 0.21057 | 0.086975 | 0.17395 | 0.027466 | 0.16937 | 0.091553 | 0.14648 | 0.14648 | 122.4976 | 122.5067 | -0.18311 | -0.17395 | 122.3785 | 122.4518 | 122.3831 | 122.4335
2154.8125 | 122.6898 | -122.4197 | 0.09613 | -0.011291 | 0.064437 | 0.017389 | 0.022044 | 0.0017282 | -0.0038238 | -0.0035739 | -0.0015565 | 0.023793 | 0.020557 | 0.02195 | 0.00075835 | 0.018812 | -0.0014931 | -0.073242 | 0.054932 | -0.059509 | -0.045776 | 0.10529 | -0.004578 | 0.018311 | -0.009155 | 0.073242 | -0.054932 | 0.032043 | 0.10986 | 0.050354 | 0.15564 | 122.3602 | -0.041198 | -0.14191 | 122.525 | 122.4381 | 122.4152 | 0.07782 | 0.054931 | 122.3648 | -0.022888 | -0.064087 | 122.5296 | 122.5754 | 122.4701 | 0.21057 | 0.10529 | 0.16479 | 0.013733 | 0.16479 | 0.086975 | 0.11444 | 0.12817 | 122.4747 | 122.493 | -0.15564 | -0.15106 | 122.374 | 122.4518 | 122.3465 | 122.4106
2156.5625 | 122.7173 | -122.406 | 0.064087 | -0.011291 | 0.067214 | 0.019525 | 0.020762 | -0.0023306 | -0.0019012 | 0.00048489 | -0.0015565 | 0.022725 | 0.019703 | 0.016395 | 0.0011855 | 0.017957 | -0.0036295 | -0.050354 | 0.068665 | -0.064087 | -0.013733 | 0.1236 | -0.018311 | 0.036621 | 0.045776 | 0.050354 | -0.050354 | 0.09613 | 0.15564 | 0.082397 | 0.19226 | 122.3419 | 0.004578 | -0.07782 | 122.5296 | 122.4426 | 122.3877 | 0.10071 | 0.045776 | 122.3557 | -0.013733 | 0.032043 | 122.5616 | 122.5983 | 122.4884 | 0.24261 | 0.13275 | 0.18768 | 0.050354 | 0.20599 | 0.14648 | 0.13275 | 0.10071 | 122.4747 | 122.4564 | -0.12817 | -0.11444 | 122.3923 | 122.5021 | 122.3557 | 122.4518
2158.25 | 122.5983 | -122.4655 | 0.10529 | -0.011291 | 0.067001 | 0.017175 | 0.023112 | -0.00019445 | -0.0021148 | 0.00027129 | 0.0014953 | 0.027211 | 0.021198 | 0.011482 | -0.00073705 | 0.018598 | 0.0012839 | -0.10529 | 0.082397 | -0.082397 | -0.10529 | 0.013733 | -0.11444 | -0.073242 | -0.086975 | 0.10071 | -0.068665 | -0.013733 | 0.022888 | -0.064087 | 0.091553 | 122.3831 | -0.022889 | -0.21057 | 122.4792 | 122.3923 | 122.3511 | 0.009155 | -0.032044 | 122.3969 | -0.004578 | -0.11902 | 122.4884 | 122.5571 | 122.4014 | 0.16022 | 0.004578 | 0.09613 | -0.022889 | 0.091553 | 0.054932 | 0.16479 | 0.16937 | 122.5479 | 122.5662 | -0.18768 | -0.17395 | 122.3602 | 122.4518 | 122.3602 | 122.3785
2160 | 122.644 | -122.4655 | 0.10986 | -0.011291 | 0.067001 | 0.014825 | 0.021617 | -0.0053214 | -0.00061944 | -0.0022921 | -0.0046081 | 0.025075 | 0.021839 | 0.014046 | -0.0033005 | 0.016248 | 2.068e-06 | -0.091553 | 0.09613 | -0.082397 | -0.10071 | 0.045776 | -0.045776 | -0.041199 | -0.07782 | 0.11902 | -0.086975 | -0.032043 | 0.07782 | -0.018311 | 0.10529 | 122.3831 | -0.013733 | -0.21057 | 122.5113 | 122.4243 | 122.4197 | 0.041198 | 0.036621 | 122.3785 | 0.009156 | -0.14191 | 122.5433 | 122.5708 | 122.4472 | 0.19226 | 0.068664 | 0.12817 | -0.018311 | 0.16479 | 0.054932 | 0.17853 | 0.20599 | 122.5616 | 122.5845 | -0.19226 | -0.19684 | 122.3648 | 122.4335 | 122.374 | 122.3877
2161.6719 | 122.731 | -122.4152 | 0.07782 | -0.011291 | 0.066787 | 0.01568 | 0.020976 | -0.0016898 | -0.001474 | -0.00058311 | -0.0046081 | 0.024007 | 0.020343 | 0.013405 | 0.0024673 | 0.017103 | -0.00063873 | -0.032043 | 0.050354 | -0.054932 | -0.013733 | 0.14648 | -0.009155 | 0.050354 | 0.045776 | 0.059509 | -0.045776 | 0.10986 | 0.1831 | 0.086975 | 0.20599 | 122.3602 | -0.027466 | -0.091553 | 122.5616 | 122.4655 | 122.406 | 0.10529 | 0.045777 | 122.3694 | -0.018311 | 0.032043 | 122.5983 | 122.6212 | 122.5021 | 0.25177 | 0.13275 | 0.20142 | 0.041199 | 0.22888 | 0.15564 | 0.10529 | 0.10528 | 122.4655 | 122.4747 | -0.13275 | -0.1236 | 122.4014 | 122.525 | 122.3831 | 122.4609
2163.4219 | 122.6852 | -122.4335 | 0.09613 | -0.011291 | 0.06636 | 0.016748 | 0.020976 | -0.0042532 | 0.0017304 | -0.0029331 | -0.0076599 | 0.022084 | 0.019703 | 0.015755 | -0.0011643 | 0.019025 | -0.0025613 | -0.07782 | 0.050354 | -0.054932 | -0.045776 | 0.11444 | -0.022888 | 0.022888 | -0.009155 | 0.054932 | -0.054932 | 0.032043 | 0.13275 | 0.036621 | 0.15106 | 122.3785 | -0.045776 | -0.14191 | 122.5479 | 122.4564 | 122.4106 | 0.07782 | 0.032044 | 122.3785 | -0.041198 | -0.064087 | 122.5662 | 122.5845 | 122.4701 | 0.20599 | 0.091553 | 0.16937 | 0.009156 | 0.18768 | 0.086975 | 0.10529 | 0.10986 | 122.4838 | 122.4884 | -0.15106 | -0.15106 | 122.3877 | 122.4655 | 122.3557 | 122.4243
2165.0938 | 122.699 | -122.4197 | 0.10529 | -0.011291 | 0.064651 | 0.01568 | 0.020976 | 0.001301 | -0.0023284 | -0.0031467 | 0.0014953 | 0.022725 | 0.019275 | 0.022591 | -0.00052345 | 0.017103 | 2.068e-06 | -0.018311 | 0.041199 | -0.032043 | 0.027466 | 0.16937 | 0.059509 | 0.073242 | 0.059509 | 0.064087 | -0.054932 | 0.050354 | 0.16479 | 0.091553 | 0.16479 | 122.3877 | -0.064087 | -0.07782 | 122.5891 | 122.493 | 122.4792 | 0.10529 | 0.091552 | 122.3648 | -0.041199 | -0.054932 | 122.5845 | 122.5845 | 122.5113 | 0.21973 | 0.14649 | 0.20142 | 0.059509 | 0.21973 | 0.10529 | 0.073242 | 0.11902 | 122.4609 | 122.4838 | -0.13733 | -0.16022 | 122.4472 | 122.4701 | 122.4014 | 122.4792
2166.8281 | 122.6944 | -122.4472 | 0.10986 | -0.018921 | 0.064437 | 0.015466 | 0.022044 | -0.0025442 | -0.00596 | -0.00015591 | 0.0014953 | 0.022512 | 0.019275 | 0.012764 | -0.00073705 | 0.016675 | -0.0014931 | -0.013733 | 0.032043 | -0.045776 | 0.022888 | 0.16479 | 0.054932 | 0.068665 | 0.054932 | 0.050354 | -0.045776 | 0.050354 | 0.17395 | 0.07782 | 0.15564 | 122.4014 | -0.07782 | -0.086975 | 122.612 | 122.5159 | 122.5021 | 0.11444 | 0.10071 | 122.4014 | -0.059509 | -0.059509 | 122.6212 | 122.6028 | 122.525 | 0.20142 | 0.1236 | 0.21057 | 0.068664 | 0.21973 | 0.09613 | 0.077819 | 0.09613 | 122.4792 | 122.4976 | -0.15564 | -0.15564 | 122.4701 | 122.4976 | 122.4335 | 122.5021
2168.5938 | 122.6257 | -122.4564 | 0.10071 | 0.0039673 | 0.066574 | 0.016321 | 0.024394 | 0.00301 | -0.001474 | -0.00015591 | -0.0015565 | 0.023793 | 0.020984 | 0.016609 | 0.00011755 | 0.016675 | -0.00021153 | -0.091553 | 0.091553 | -0.073242 | -0.09613 | 0.013733 | -0.10071 | -0.064087 | -0.07782 | 0.082397 | -0.082397 | -0.009155 | 0.041199 | -0.045776 | 0.10071 | 122.3831 | -0.009155 | -0.19684 | 122.4701 | 122.3923 | 122.3557 | 0.009155 | -0.027466 | 122.374 | -0.018311 | -0.10986 | 122.4976 | 122.5571 | 122.4106 | 0.18311 | 0.036621 | 0.086975 | -0.022888 | 0.1236 | 0.073242 | 0.16479 | 0.16479 | 122.5479 | 122.5388 | -0.17395 | -0.18311 | 122.3602 | 122.4472 | 122.3648 | 122.3785
2170.2812 | 122.7585 | -122.4289 | 0.10071 | -0.0036622 | 0.063369 | 0.015253 | 0.019694 | -0.0027578 | -0.003183 | -0.0037875 | -0.0015565 | 0.023366 | 0.021839 | 0.012978 | -0.00030965 | 0.020307 | -0.0023477 | -0.041199 | 0.041199 | -0.036621 | 0.027466 | 0.19226 | 0.082397 | 0.09613 | 0.11444 | 0.050354 | -0.032043 | 0.10986 | 0.20599 | 0.13733 | 0.21973 | 122.3923 | -0.059509 | -0.073242 | 122.6212 | 122.525 | 122.5113 | 0.13275 | 0.11902 | 122.3969 | -0.050354 | 0.009155 | 122.6349 | 122.6486 | 122.5662 | 0.25177 | 0.16937 | 0.22888 | 0.064087 | 0.23804 | 0.14191 | 0.07782 | 0.082397 | 122.4701 | 122.4792 | -0.13733 | -0.13275 | 122.4564 | 122.5388 | 122.3877 | 122.5433
2172.0156 | 122.6257 | -122.4609 | 0.10071 | -0.011291 | 0.06636 | 0.014398 | 0.020762 | 0.00044655 | -0.0044646 | 0.00027129 | -0.0015565 | 0.022084 | 0.018848 | 0.019173 | -0.0045823 | 0.016462 | -0.0025613 | -0.027466 | 0.045776 | -0.059509 | -0.009155 | 0.1236 | 0.041199 | 0.036621 | 0 | 0.073242 | -0.068665 | 0.004578 | 0.07782 | 0.013733 | 0.11444 | 122.4014 | -0.054932 | -0.10986 | 122.5845 | 122.4976 | 122.5021 | 0.09613 | 0.10071 | 122.3923 | -0.027466 | -0.09613 | 122.5388 | 122.5754 | 122.4747 | 0.18311 | 0.082398 | 0.1831 | 0.050354 | 0.14649 | 0.073243 | 0.10528 | 0.14191 | 122.5067 | 122.5342 | -0.16022 | -0.16937 | 122.4518 | 122.4655 | 122.4335 | 122.4609
2173.7031 | 122.7356 | -122.4197 | 0.082397 | -0.0036622 | 0.062515 | 0.014825 | 0.020548 | -0.0051076 | -0.0021148 | -0.00058311 | -0.0015565 | 0.023793 | 0.017994 | 0.017677 | -0.00052345 | 0.01753 | 0.0051291 | -0.086975 | 0.050354 | -0.059509 | -0.027466 | 0.12817 | 0.027466 | 0.032043 | 0.009155 | 0.054932 | -0.068665 | 0.068665 | 0.15564 | 0.10071 | 0.18768 | 122.3602 | -0.032043 | -0.10986 | 122.5479 | 122.4518 | 122.4472 | 0.091552 | 0.086975 | 122.3511 | -0.027465 | -0.013732 | 122.5754 | 122.6074 | 122.5204 | 0.25635 | 0.16937 | 0.18768 | 0.032043 | 0.22431 | 0.13733 | 0.10986 | 0.1236 | 122.4701 | 122.4747 | -0.14191 | -0.15106 | 122.3923 | 122.4884 | 122.3328 | 122.4289
2175.4375 | 122.699 | -122.4518 | 0.091553 | 0.011597 | 0.064224 | 0.016748 | 0.022471 | -0.0010488 | -0.0029694 | 5.7688e-05 | -0.0015565 | 0.023152 | 0.02013 | 0.014686 | 0.00097195 | 0.017957 | 0.00064307 | -0.054932 | 0.059509 | -0.059509 | -0.027466 | 0.1236 | -0.018311 | 0.018311 | 0.009155 | 0.059509 | -0.059509 | 0.036621 | 0.1236 | 0.036621 | 0.15564 | 122.3923 | -0.032044 | -0.11902 | 122.5754 | 122.4701 | 122.4335 | 0.07782 | 0.041198 | 122.3923 | -0.032044 | -0.054932 | 122.5754 | 122.6074 | 122.4884 | 0.21515 | 0.09613 | 0.1831 | 0.032043 | 0.1831 | 0.09613 | 0.11902 | 0.11902 | 122.5113 | 122.5113 | -0.15106 | -0.15106 | 122.4243 | 122.4884 | 122.3969 | 122.4609
2177.1094 | 122.731 | -122.4243 | 0.10071 | -0.0036622 | 0.067001 | 0.016962 | 0.018199 | -0.0019034 | -0.0044646 | -0.0014377 | -0.0015565 | 0.022725 | 0.019062 | 0.014473 | -0.0033005 | 0.01518 | 0.0021383 | -0.018311 | 0.027466 | -0.045776 | 0.036621 | 0.19684 | 0.068665 | 0.086975 | 0.068665 | 0.045776 | -0.032043 | 0.082397 | 0.19226 | 0.09613 | 0.19684 | 122.3785 | -0.073242 | -0.064087 | 122.6212 | 122.5113 | 122.493 | 0.13275 | 0.11444 | 122.3923 | -0.054932 | -0.018311 | 122.6166 | 122.6212 | 122.5204 | 0.22888 | 0.12817 | 0.24261 | 0.082397 | 0.2243 | 0.11444 | 0.073242 | 0.077819 | 122.4518 | 122.4701 | -0.14648 | -0.13275 | 122.4609 | 122.5067 | 122.406 | 122.493
2178.875 | 122.7539 | -122.4243 | 0.091553 | -0.018921 | 0.061874 | 0.014612 | 0.021189 | -0.004894 | -0.003183 | -0.0027195 | -0.0046081 | 0.022725 | 0.019703 | 0.013618 | -0.0013779 | 0.018171 | -0.00063873 | -0.018311 | 0.050354 | -0.050354 | 0.050354 | 0.22888 | 0.091553 | 0.091553 | 0.086975 | 0.050354 | -0.036621 | 0.086975 | 0.19226 | 0.10529 | 0.18768 | 122.374 | -0.041199 | -0.041199 | 122.6532 | 122.5159 | 122.5159 | 0.14191 | 0.14191 | 122.3877 | -0.041199 | -0.004578 | 122.6166 | 122.612 | 122.5296 | 0.2243 | 0.14191 | 0.27924 | 0.10071 | 0.22888 | 0.1236 | 0.10071 | 0.086975 | 122.4747 | 122.4747 | -0.14191 | -0.12817 | 122.4747 | 122.5113 | 122.406 | 122.5113
2180.5625 | 122.6257 | -122.493 | 0.091553 | -0.011291 | 0.066146 | 0.015039 | 0.024607 | 0.0025828 | -0.00083304 | 0.00027129 | -0.0046081 | 0.024648 | 0.018848 | 0.013405 | 0.0026809 | 0.016675 | -0.0042703 | -0.086975 | 0.073242 | -0.082397 | -0.09613 | 0.009155 | -0.10071 | -0.068665 | -0.09613 | 0.082397 | -0.073242 | -0.022888 | 0.009155 | -0.059509 | 0.086975 | 122.4106 | -0.018311 | -0.18768 | 122.5021 | 122.4243 | 122.3923 | 0.013732 | -0.018311 | 122.4197 | -0.009156 | -0.11444 | 122.5021 | 122.58 | 122.4335 | 0.16022 | 0.013733 | 0.091552 | -0.013733 | 0.082397 | 0.050354 | 0.15564 | 0.15564 | 122.5662 | 122.5754 | -0.17395 | -0.16479 | 122.3969 | 122.4701 | 122.406 | 122.3969
2182.3125 | 122.7493 | -122.4106 | 0.073242 | -0.0036622 | 0.065078 | 0.017603 | 0.022685 | 0.00044655 | -0.0023284 | 5.7688e-05 | -0.0046081 | 0.025716 | 0.019916 | 0.02195 | 0.0020401 | 0.018171 | -0.00063873 | -0.009155 | 0.018311 | -0.018311 | 0.032043 | 0.17395 | 0.018311 | 0.041199 | 0.07782 | 0.064087 | -0.045776 | 0.11444 | 0.17395 | 0.07782 | 0.19226 | 122.3923 | -0.054931 | -0.041199 | 122.5845 | 122.4518 | 122.4289 | 0.05951 | 0.036622 | 122.3648 | -0.009155 | 0.041199 | 122.5845 | 122.6028 | 122.4884 | 0.23804 | 0.1236 | 0.19226 | 0.050354 | 0.21973 | 0.16022 | 0.036622 | 0.10986 | 122.4289 | 122.4747 | -0.091553 | -0.11902 | 122.4426 | 122.525 | 122.4014 | 122.4884
2184.0156 | 122.7448 | -122.438 | 0.09613 | -0.0036622 | 0.06401 | 0.01803 | 0.02183 | 0.00066015 | -0.0023284 | -0.0010105 | 0.0014953 | 0.024434 | 0.018421 | 0.017891 | 0.0022537 | 0.020093 | -0.0032021 | -0.013733 | 0.050354 | -0.022888 | 0.027466 | 0.16937 | 0.009155 | 0.068665 | 0.073242 | 0.064087 | -0.045776 | 0.11902 | 0.17395 | 0.07782 | 0.21057 | 122.4152 | -0.045776 | -0.068664 | 122.6074 | 122.5067 | 122.4472 | 0.091553 | 0.032043 | 122.3923 | -0.032043 | 0.022889 | 122.612 | 122.6486 | 122.5159 | 0.25635 | 0.1236 | 0.19226 | 0.050354 | 0.21973 | 0.16479 | 0.073242 | 0.10986 | 122.4884 | 122.5021 | -0.11902 | -0.14191 | 122.4655 | 122.5571 | 122.4243 | 122.5113
2185.7656 | 122.7356 | -122.4472 | 0.082397 | -0.0036622 | 0.067214 | 0.018243 | 0.022044 | 0.001301 | -0.0029694 | -0.0010105 | 0.0014953 | 0.022298 | 0.020984 | 0.020454 | 0.00011755 | 0.019452 | -0.0019205 | -0.013733 | 0.032043 | -0.036621 | 0.032043 | 0.19226 | 0.032043 | 0.064087 | 0.091553 | 0.045776 | -0.032043 | 0.091553 | 0.16937 | 0.064087 | 0.17853 | 122.4106 | -0.050354 | -0.050354 | 122.6395 | 122.5113 | 122.4792 | 0.10071 | 0.068664 | 122.4152 | -0.036621 | 0.009156 | 122.6166 | 122.6257 | 122.5113 | 0.21057 | 0.09613 | 0.22888 | 0.068664 | 0.20142 | 0.1236 | 0.068664 | 0.077819 | 122.4792 | 122.493 | -0.11902 | -0.11444 | 122.4792 | 122.5388 | 122.4335 | 122.5388
2187.5 | 122.612 | -122.4472 | 0.10986 | -0.0036622 | 0.067001 | 0.017816 | 0.024394 | -0.00062165 | -0.001474 | -0.00015591 | 0.0045471 | 0.025502 | 0.018634 | 0.012764 | -0.00095065 | 0.018598 | -0.00063873 | -0.073242 | 0.082397 | -0.068665 | -0.086975 | 0.036621 | -0.082397 | -0.059509 | -0.09613 | 0.091553 | -0.073242 | -0.032043 | 0.018311 | -0.068665 | 0.086975 | 122.3785 | -0.027466 | -0.19684 | 122.4838 | 122.3877 | 122.3648 | 0.009156 | -0.013732 | 122.374 | -0.01831 | -0.14191 | 122.4655 | 122.5342 | 122.3785 | 0.16022 | 0.004577 | 0.10529 | -0.01831 | 0.091553 | 0.041199 | 0.15106 | 0.16479 | 122.5296 | 122.5388 | -0.17853 | -0.18311 | 122.3602 | 122.4152 | 122.374 | 122.3511
2189.2344 | 122.7036 | -122.4564 | 0.07782 | -0.0036622 | 0.065292 | 0.014612 | 0.022685 | -0.00062165 | -0.0038238 | 0.00091209 | -0.0015565 | 0.027425 | 0.018848 | 0.016395 | 0.0020401 | 0.019239 | -0.0019205 | -0.09613 | 0.07782 | -0.068665 | -0.07782 | 0.059509 | -0.068665 | -0.013733 | -0.022888 | 0.068665 | -0.032043 | 0.064087 | 0.13275 | 0.036621 | 0.17853 | 122.3877 | 0 | -0.15564 | 122.5159 | 122.4426 | 122.3877 | 0.054932 | 0 | 122.4243 | -0.009155 | -0.013733 | 122.5891 | 122.6349 | 122.493 | 0.21057 | 0.068664 | 0.12817 | -0.009155 | 0.16479 | 0.09613 | 0.14649 | 0.10071 | 122.5342 | 122.525 | -0.14649 | -0.10986 | 122.3785 | 122.5204 | 122.3602 | 122.4335
2190.9375 | 122.7814 | -122.4289 | 0.09613 | 0.0039673 | 0.06401 | 0.014612 | 0.022257 | -0.0046804 | -0.0040374 | -0.0012241 | -0.0015565 | 0.02358 | 0.021839 | 0.022163 | -0.0060777 | 0.017316 | -0.0010659 | -0.032043 | 0.050354 | -0.036621 | 0.013733 | 0.19684 | 0.059509 | 0.091553 | 0.086975 | 0.032043 | -0.054932 | 0.086975 | 0.20142 | 0.11902 | 0.19226 | 122.3923 | -0.045776 | -0.082397 | 122.6257 | 122.5204 | 122.4884 | 0.12817 | 0.09613 | 122.374 | -0.064087 | -0.009155 | 122.6303 | 122.6212 | 122.5479 | 0.24719 | 0.17395 | 0.23346 | 0.050354 | 0.25635 | 0.14191 | 0.086975 | 0.086975 | 122.4792 | 122.4609 | -0.13275 | -0.15106 | 122.4426 | 122.5159 | 122.3969 | 122.5159
2192.6875 | 122.6166 | -122.4838 | 0.13275 | 0.0039673 | 0.068283 | 0.016321 | 0.023326 | 0.0010874 | -0.0027556 | -0.00079691 | -0.0046081 | 0.025075 | 0.020343 | 0.016823 | -0.0056503 | 0.016034 | -0.00085233 | -0.11902 | 0.09613 | -0.086975 | -0.10529 | 0.041199 | -0.036621 | -0.018311 | -0.086975 | 0.09613 | -0.068665 | -0.059509 | 0.032043 | -0.027466 | 0.086975 | 122.3969 | -0.036621 | -0.23804 | 122.525 | 122.4655 | 122.4472 | 0.068664 | 0.050354 | 122.4152 | -0.036621 | -0.19226 | 122.5159 | 122.5708 | 122.4564 | 0.15564 | 0.041199 | 0.12817 | -0.018311 | 0.10071 | 0.009156 | 0.1831 | 0.16479 | 122.58 | 122.58 | -0.21973 | -0.20142 | 122.3785 | 122.4243 | 122.3648 | 122.3969
2194.3906 | 122.6669 | -122.4609 | 0.10529 | -0.011291 | 0.065933 | 0.015039 | 0.024821 | 0.0015146 | -0.0036102 | -0.0025057 | -0.0015565 | 0.025289 | 0.019275 | 0.015968 | -0.00073705 | 0.016462 | -0.0044839 | -0.054932 | 0.086975 | -0.082397 | -0.041199 | 0.086975 | -0.018311 | -0.004578 | -0.013733 | 0.082397 | -0.054932 | 0.018311 | 0.09613 | 0.022888 | 0.13275 | 122.3785 | -0.018311 | -0.14649 | 122.5479 | 122.4564 | 122.4426 | 0.077819 | 0.064086 | 122.406 | -0.022889 | -0.086975 | 122.5571 | 122.5937 | 122.4838 | 0.18768 | 0.07782 | 0.16937 | 0.041198 | 0.15106 | 0.073243 | 0.16937 | 0.13733 | 122.5479 | 122.5433 | -0.18768 | -0.16022 | 122.4197 | 122.4792 | 122.406 | 122.4472
2196.1562 | 122.6486 | -122.4701 | 0.10986 | -0.0036622 | 0.068923 | 0.014612 | 0.022044 | 0.0010874 | -0.0010468 | -0.0012241 | -0.0046081 | 0.026357 | 0.019703 | 0.010628 | 0.00011755 | 0.017957 | -0.00085233 | -0.032043 | 0.086975 | -0.068665 | -0.036621 | 0.10986 | -0.018311 | 0.004578 | -0.018311 | 0.07782 | -0.064087 | 0.022888 | 0.086975 | -0.004578 | 0.1236 | 122.4014 | -0.022888 | -0.14648 | 122.58 | 122.4747 | 122.4518 | 0.073243 | 0.050354 | 122.406 | -0.032043 | -0.086975 | 122.5571 | 122.5937 | 122.4655 | 0.18768 | 0.059509 | 0.17853 | 0.032044 | 0.15106 | 0.086975 | 0.15564 | 0.14191 | 122.5571 | 122.5479 | -0.17853 | -0.17395 | 122.4335 | 122.493 | 122.4381 | 122.4518
2197.9062 | 122.6715 | -122.4747 | 0.10529 | -0.011291 | 0.06871 | 0.016107 | 0.023539 | -0.0010488 | -0.0016876 | 0.0015531 | -0.0015565 | 0.023366 | 0.019489 | 0.011055 | -9.605e-05 | 0.018598 | -0.0055521 | -0.059509 | 0.068665 | -0.073242 | -0.041199 | 0.10986 | -0.022888 | -0.013733 | -0.022888 | 0.09613 | -0.068665 | 0.022888 | 0.10071 | 0.004578 | 0.12817 | 122.4014 | -0.036621 | -0.14649 | 122.5845 | 122.4609 | 122.4518 | 0.059509 | 0.050354 | 122.406 | -0.009156 | -0.082398 | 122.5754 | 122.6028 | 122.4792 | 0.19684 | 0.073243 | 0.18311 | 0.032043 | 0.16937 | 0.091553 | 0.14191 | 0.16479 | 122.5433 | 122.5708 | -0.17853 | -0.17395 | 122.4335 | 122.4976 | 122.4152 | 122.4518
2199.6094 | 122.6669 | -122.4701 | 0.12817 | -0.011291 | 0.066574 | 0.014825 | 0.02183 | -0.003185 | -0.0053192 | -0.0016513 | -0.0015565 | 0.02358 | 0.02248 | 0.012123 | -0.0030869 | 0.016675 | 2.068e-06 | -0.086975 | 0.07782 | -0.082397 | -0.10529 | 0.022888 | -0.064087 | -0.018311 | -0.082397 | 0.10071 | -0.091553 | -0.018311 | 0.082397 | -0.027466 | 0.13275 | 122.3877 | -0.050354 | -0.23346 | 122.493 | 122.4518 | 122.406 | 0.064086 | 0.01831 | 122.3785 | -0.027466 | -0.14649 | 122.5525 | 122.6028 | 122.4426 | 0.2243 | 0.064087 | 0.10528 | -0.022889 | 0.17395 | 0.073242 | 0.16022 | 0.19226 | 122.5479 | 122.5708 | -0.21057 | -0.21973 | 122.3648 | 122.4518 | 122.3831 | 122.3877
2201.2969 | 122.7173 | -122.4564 | 0.10071 | 0.0039673 | 0.065505 | 0.017816 | 0.022257 | 0.001301 | -0.0016876 | 0.0013395 | -0.0015565 | 0.022512 | 0.02013 | 0.015327 | 0.00011755 | 0.01753 | -0.0040567 | -0.050354 | 0.027466 | -0.041199 | 0 | 0.17395 | 0.022888 | 0.059509 | 0.068665 | 0.050354 | -0.041199 | 0.050354 | 0.15106 | 0.059509 | 0.16479 | 122.4152 | -0.073242 | -0.10071 | 122.6303 | 122.5159 | 122.4792 | 0.10071 | 0.064087 | 122.4152 | -0.050354 | -0.050354 | 122.6074 | 122.6212 | 122.5159 | 0.20599 | 0.10071 | 0.21515 | 0.041199 | 0.19226 | 0.091553 | 0.068665 | 0.091553 | 122.4838 | 122.5067 | -0.14191 | -0.14191 | 122.4564 | 122.5067 | 122.406 | 122.525
2203.0469 | 122.7219 | -122.4884 | 0.10986 | -0.0036622 | 0.063369 | 0.016962 | 0.020121 | -0.00062165 | -0.0029694 | -0.0031467 | -0.0046081 | 0.021871 | 0.016071 | 0.018318 | -0.00095065 | 0.017316 | -0.0014931 | -0.073242 | 0.054932 | -0.059509 | -0.050354 | 0.091553 | -0.013733 | 0.009155 | -0.013733 | 0.059509 | -0.059509 | 0.032043 | 0.10986 | 0.064087 | 0.15106 | 122.4289 | -0.054931 | -0.16022 | 122.58 | 122.4976 | 122.4747 | 0.068664 | 0.045776 | 122.4289 | -0.050354 | -0.07782 | 122.5983 | 122.6395 | 122.5525 | 0.21057 | 0.1236 | 0.15106 | 0.009155 | 0.16937 | 0.091552 | 0.11444 | 0.11902 | 122.5433 | 122.5479 | -0.16937 | -0.16937 | 122.438 | 122.5204 | 122.4152 | 122.4747
2204.7344 | 122.6807 | -122.4564 | 0.10071 | -0.011291 | 0.066146 | 0.016107 | 0.022685 | -0.0040396 | -0.0036102 | -0.0016513 | -0.0046081 | 0.023793 | 0.020557 | 0.0093461 | 0.0016129 | 0.016889 | -0.0014931 | -0.10986 | 0.073242 | -0.082397 | -0.091553 | 0.022888 | -0.086975 | -0.032043 | -0.036621 | 0.068665 | -0.054932 | 0.045776 | 0.07782 | 0.004578 | 0.13733 | 122.374 | -0.027466 | -0.19226 | 122.4792 | 122.4243 | 122.3694 | 0.050354 | -0.004578 | 122.4014 | -0.032043 | -0.054932 | 122.5342 | 122.5937 | 122.4609 | 0.19226 | 0.05951 | 0.10528 | -0.009156 | 0.13275 | 0.10071 | 0.15564 | 0.1236 | 122.5296 | 122.525 | -0.18311 | -0.15564 | 122.3648 | 122.5021 | 122.3465 | 122.4197
2206.4844 | 122.7722 | -122.4335 | 0.082397 | 0.011597 | 0.065292 | 0.015253 | 0.020121 | -0.0057486 | -0.0023284 | -0.0018649 | -0.0076599 | 0.022725 | 0.018421 | 0.027077 | -9.605e-05 | 0.017743 | -0.0021341 | -0.032043 | 0.045776 | -0.045776 | 0.036621 | 0.21973 | 0.07782 | 0.11444 | 0.11902 | 0.045776 | -0.050354 | 0.091553 | 0.18768 | 0.12817 | 0.19226 | 122.3877 | -0.036621 | -0.045776 | 122.6532 | 122.5479 | 122.5113 | 0.16022 | 0.1236 | 122.3831 | -0.036621 | 0.009156 | 122.6212 | 122.6257 | 122.5616 | 0.24261 | 0.17853 | 0.2655 | 0.082397 | 0.23804 | 0.14191 | 0.091552 | 0.09613 | 122.4792 | 122.4792 | -0.12817 | -0.13275 | 122.4701 | 122.525 | 122.4014 | 122.5525
2208.1719 | 122.644 | -122.4792 | 0.10986 | -0.011291 | 0.06636 | 0.015253 | 0.022685 | -0.0012624 | -0.002542 | -0.0046421 | 0.0014953 | 0.024007 | 0.019275 | 0.011482 | -0.0028733 | 0.017316 | -0.0040567 | -0.11902 | 0.09613 | -0.086975 | -0.10986 | 0.032043 | -0.059509 | -0.041199 | -0.091553 | 0.11902 | -0.07782 | -0.032043 | 0.032043 | -0.036621 | 0.082397 | 122.3923 | -0.013733 | -0.21973 | 122.5113 | 122.438 | 122.4197 | 0.045776 | 0.027466 | 122.4014 | 0.009156 | -0.14191 | 122.5113 | 122.5616 | 122.4426 | 0.16022 | 0.041199 | 0.11902 | -0.022888 | 0.10986 | 0.045777 | 0.1831 | 0.19684 | 122.5754 | 122.5983 | -0.19684 | -0.18768 | 122.3694 | 122.4472 | 122.3602 | 122.3877
2209.9219 | 122.6761 | -122.4838 | 0.091553 | -0.011291 | 0.064865 | 0.015466 | 0.022471 | 0.001301 | -0.002542 | 0.00069849 | 0.0014953 | 0.024007 | 0.02013 | 0.011909 | 0.00011755 | 0.017743 | 0.00042947 | -0.10071 | 0.082397 | -0.086975 | -0.10529 | 0.036621 | -0.09613 | -0.050354 | -0.050354 | 0.10071 | -0.07782 | 0.013733 | 0.068665 | -0.018311 | 0.1236 | 122.3969 | -0.009156 | -0.19684 | 122.5204 | 122.4335 | 122.3877 | 0.036621 | -0.009155 | 122.406 | 0.009155 | -0.07782 | 122.5525 | 122.6074 | 122.4655 | 0.20142 | 0.059509 | 0.1236 | -0.018311 | 0.14649 | 0.091553 | 0.16937 | 0.17853 | 122.5662 | 122.5845 | -0.17853 | -0.16937 | 122.3785 | 122.4976 | 122.3831 | 122.4335
2211.6562 | 122.7264 | -122.4747 | 0.086975 | -0.0036622 | 0.06636 | 0.015894 | 0.02183 | 0.0015146 | -0.0027556 | -0.00079691 | 0.0014953 | 0.024221 | 0.021412 | 0.021522 | -9.605e-05 | 0.019025 | -0.0029885 | -0.041199 | 0.027466 | -0.045776 | -0.009155 | 0.17395 | 0 | 0.032043 | 0.041199 | 0.07782 | -0.054932 | 0.045776 | 0.13275 | 0.054932 | 0.17395 | 122.4289 | -0.059509 | -0.09613 | 122.6486 | 122.5067 | 122.4747 | 0.077819 | 0.045776 | 122.4197 | -0.009155 | -0.041199 | 122.6074 | 122.6486 | 122.5296 | 0.22888 | 0.10986 | 0.21973 | 0.036621 | 0.18768 | 0.10071 | 0.073242 | 0.13275 | 122.5021 | 122.5525 | -0.13275 | -0.14191 | 122.4655 | 122.5204 | 122.4335 | 122.5159
2213.4062 | 122.6898 | -122.4655 | 0.10071 | -0.011291 | 0.06636 | 0.016107 | 0.025035 | -0.0023306 | -0.001474 | -0.00015591 | -0.0046081 | 0.024648 | 0.020984 | 0.013405 | 0.00011755 | 0.016675 | -0.0023477 | -0.045776 | 0.068665 | -0.07782 | -0.032043 | 0.10071 | -0.009155 | 0.009155 | 0.009155 | 0.10071 | -0.059509 | 0.041199 | 0.091553 | 0.013733 | 0.14648 | 122.3877 | -0.032043 | -0.13275 | 122.5662 | 122.4747 | 122.4564 | 0.086975 | 0.068665 | 122.406 | 0 | -0.059509 | 122.5571 | 122.612 | 122.4792 | 0.20599 | 0.073242 | 0.17853 | 0.045777 | 0.15106 | 0.10071 | 0.14649 | 0.16022 | 122.5342 | 122.5662 | -0.17853 | -0.16022 | 122.4335 | 122.5067 | 122.4197 | 122.4747
2215.0938 | 122.7493 | -122.493 | 0.064087 | -0.011291 | 0.063583 | 0.015253 | 0.022044 | -0.0046804 | -0.0027556 | 0.00027129 | 0.0014953 | 0.021657 | 0.019916 | 0.017891 | -0.0015915 | 0.018384 | 0.00021567 | -0.068665 | 0.045776 | -0.064087 | -0.041199 | 0.12817 | 0.004578 | 0.050354 | 0.004578 | 0.054932 | -0.064087 | 0.059509 | 0.15564 | 0.07782 | 0.17395 | 122.4289 | -0.018311 | -0.10529 | 122.6212 | 122.5433 | 122.4976 | 0.11444 | 0.068665 | 122.4289 | -0.009155 | -0.004578 | 122.6486 | 122.6669 | 122.5708 | 0.23804 | 0.14191 | 0.19226 | 0.022888 | 0.21973 | 0.1236 | 0.10986 | 0.11902 | 122.5388 | 122.5479 | -0.12817 | -0.12817 | 122.4518 | 122.5525 | 122.4243 | 122.4976
2216.8281 | 122.7264 | -122.4564 | 0.10071 | 0.011597 | 0.065078 | 0.016534 | 0.021403 | -0.0016898 | -0.0021148 | 0.00048489 | -0.0046081 | 0.022725 | 0.020771 | 0.026649 | -0.00030965 | 0.01988 | -0.0010659 | -0.064087 | 0.036621 | -0.059509 | -0.036621 | 0.10529 | -0.009155 | 0.036621 | 0 | 0.054932 | -0.073242 | 0.032043 | 0.1236 | 0.041199 | 0.14648 | 122.3969 | -0.064087 | -0.13733 | 122.5616 | 122.493 | 122.4472 | 0.09613 | 0.050354 | 122.3831 | -0.045776 | -0.068665 | 122.58 | 122.6028 | 122.4976 | 0.21973 | 0.11444 | 0.16479 | 0.022888 | 0.19684 | 0.10529 | 0.09613 | 0.12817 | 122.493 | 122.5113 | -0.16022 | -0.17395 | 122.4197 | 122.4884 | 122.3923 | 122.4564
2218.5 | 122.6486 | -122.4701 | 0.11902 | -0.011291 | 0.067214 | 0.014825 | 0.024394 | 0.0032236 | -0.00083304 | 0.00048489 | -0.0046081 | 0.024221 | 0.020771 | 0.019813 | 0.0024673 | 0.016462 | -0.0036295 | -0.10529 | 0.07782 | -0.086975 | -0.10986 | 0 | -0.10986 | -0.064087 | -0.086975 | 0.086975 | -0.073242 | -0.027466 | 0.022888 | -0.064087 | 0.09613 | 122.3831 | -0.041199 | -0.22888 | 122.4701 | 122.406 | 122.3602 | 0.022888 | -0.022888 | 122.3969 | -0.032044 | -0.14649 | 122.493 | 122.5662 | 122.406 | 0.16937 | 0.009155 | 0.086975 | -0.022888 | 0.09613 | 0.045776 | 0.16479 | 0.16022 | 122.5479 | 122.5571 | -0.20599 | -0.19226 | 122.3602 | 122.4426 | 122.3648 | 122.3831
2220.1875 | 122.6303 | -122.4976 | 0.12817 | -0.0036622 | 0.067001 | 0.01803 | 0.024607 | 0.0019418 | -0.0033966 | -0.0025057 | -0.0046081 | 0.024861 | 0.018848 | 0.010628 | -0.00095065 | 0.016675 | -0.0025613 | -0.09613 | 0.068665 | -0.082397 | -0.11444 | 0.004578 | -0.10071 | -0.064087 | -0.10986 | 0.10071 | -0.07782 | -0.041199 | 0.004578 | -0.091553 | 0.064087 | 122.4152 | -0.059509 | -0.24262 | 122.5021 | 122.4335 | 122.3969 | 0.01831 | -0.018311 | 122.4197 | -0.027466 | -0.16937 | 122.5021 | 122.5616 | 122.406 | 0.14191 | -0.013733 | 0.086975 | -0.032044 | 0.082398 | 0.036621 | 0.15106 | 0.17853 | 122.5662 | 122.5983 | -0.21057 | -0.20599 | 122.3831 | 122.4564 | 122.4014 | 122.3877
2221.9219 | 122.6944 | -122.5067 | 0.13275 | -0.011291 | 0.064651 | 0.015039 | 0.02183 | -0.0027578 | -0.0010468 | -0.0012241 | 0.0045471 | 0.024861 | 0.015857 | 0.015968 | -0.0030869 | 0.017743 | 0.0012839 | -0.068665 | 0.07782 | -0.082397 | -0.086975 | 0.054932 | -0.032043 | -0.013733 | -0.064087 | 0.086975 | -0.091553 | 0.009155 | 0.082397 | 0 | 0.1236 | 122.4243 | -0.054931 | -0.21973 | 122.5616 | 122.493 | 122.4747 | 0.068664 | 0.050354 | 122.4152 | -0.045776 | -0.1236 | 122.5891 | 122.6303 | 122.5067 | 0.21515 | 0.091553 | 0.13733 | -0.004578 | 0.17395 | 0.10071 | 0.16022 | 0.17853 | 122.5845 | 122.5937 | -0.21515 | -0.2243 | 122.4197 | 122.5159 | 122.438 | 122.4426
2223.6875 | 122.7676 | -122.4701 | 0.086975 | -0.0036622 | 0.065292 | 0.015253 | 0.020762 | 0.00066015 | -0.001474 | 5.7688e-05 | -0.0046081 | 0.022298 | 0.017994 | 0.022804 | -0.00095065 | 0.016248 | -0.0038431 | -0.036621 | 0.013733 | -0.032043 | 0.022888 | 0.21057 | 0.068665 | 0.09613 | 0.073242 | 0.059509 | -0.036621 | 0.086975 | 0.18768 | 0.11902 | 0.20142 | 122.4381 | -0.073242 | -0.064087 | 122.6807 | 122.5662 | 122.5388 | 0.12817 | 0.10071 | 122.4335 | -0.027466 | 0 | 122.6578 | 122.6715 | 122.5891 | 0.23804 | 0.15564 | 0.24261 | 0.054931 | 0.2243 | 0.1236 | 0.045776 | 0.09613 | 122.4838 | 122.5296 | -0.11902 | -0.1236 | 122.493 | 122.5571 | 122.4335 | 122.5433
2225.375 | 122.8043 | -122.4701 | 0.091553 | 0.0039673 | 0.064651 | 0.014825 | 0.019908 | -0.003185 | -0.002542 | -0.00036951 | -0.0046081 | 0.021871 | 0.017994 | 0.023231 | -0.0018051 | 0.017103 | -0.0027749 | -0.032043 | 0.041199 | -0.022888 | 0.027466 | 0.21057 | 0.082397 | 0.10071 | 0.10529 | 0.050354 | -0.041199 | 0.082397 | 0.1831 | 0.11902 | 0.17853 | 122.4472 | -0.050354 | -0.064087 | 122.6807 | 122.5708 | 122.5525 | 0.1236 | 0.10528 | 122.4289 | -0.041199 | -0.009156 | 122.6532 | 122.6486 | 122.5891 | 0.21973 | 0.16022 | 0.23346 | 0.050354 | 0.2243 | 0.1236 | 0.064087 | 0.091553 | 122.5113 | 122.5204 | -0.11444 | -0.13275 | 122.4976 | 122.5525 | 122.4381 | 122.5754
2227.1094 | 122.7951 | -122.4426 | 0.082397 | -0.018921 | 0.062515 | 0.013757 | 0.022685 | -0.0012624 | -0.0021148 | 0.0013395 | -0.0046081 | 0.020375 | 0.020343 | 0.02494 | -0.0018051 | 0.017316 | -0.0017069 | -0.032043 | 0.032043 | -0.036621 | 0.027466 | 0.21973 | 0.073242 | 0.10071 | 0.10986 | 0.041199 | -0.041199 | 0.09613 | 0.20599 | 0.11444 | 0.19226 | 122.406 | -0.050354 | -0.054931 | 122.6624 | 122.5433 | 122.5159 | 0.13733 | 0.10986 | 122.4014 | -0.041198 | 0.013733 | 122.6486 | 122.6349 | 122.5571 | 0.23346 | 0.15564 | 0.25635 | 0.064087 | 0.24719 | 0.13733 | 0.068664 | 0.082398 | 122.4747 | 122.4838 | -0.11902 | -0.1236 | 122.4701 | 122.5388 | 122.4106 | 122.5525
2228.875 | 122.7722 | -122.438 | 0.082397 | 0.011597 | 0.064865 | 0.016962 | 0.022471 | 0.0021556 | -0.001474 | -0.0035739 | -0.0015565 | 0.023152 | 0.016925 | 0.015755 | 0.0041763 | 0.019666 | -0.00042513 | -0.022888 | 0.073242 | -0.059509 | 0 | 0.13733 | -0.004578 | 0.045776 | 0.07782 | 0.054932 | -0.045776 | 0.10529 | 0.17395 | 0.082397 | 0.21515 | 122.3785 | -0.009155 | -0.082397 | 122.5754 | 122.4838 | 122.4335 | 0.10528 | 0.054931 | 122.3923 | -0.027465 | 0.022889 | 122.612 | 122.6532 | 122.5204 | 0.26093 | 0.12817 | 0.19684 | 0.059509 | 0.21973 | 0.15106 | 0.13275 | 0.10071 | 122.5113 | 122.493 | -0.14191 | -0.12817 | 122.438 | 122.5433 | 122.4152 | 122.5159
2230.5625 | 122.7814 | -122.4609 | 0.086975 | -0.011291 | 0.066787 | 0.017816 | 0.023539 | -0.0033986 | -0.0021148 | -0.0010105 | -0.0015565 | 0.025075 | 0.018207 | 0.023872 | 0.0028945 | 0.020307 | -0.0019205 | -0.013733 | 0.027466 | -0.027466 | 0.036621 | 0.16479 | 0.027466 | 0.054932 | 0.082397 | 0.050354 | -0.022888 | 0.10529 | 0.17853 | 0.091553 | 0.21973 | 122.4335 | -0.059509 | -0.050354 | 122.6257 | 122.5159 | 122.4884 | 0.082398 | 0.054932 | 122.438 | -0.036621 | 0.018311 | 122.6395 | 122.6807 | 122.5525 | 0.24261 | 0.11444 | 0.19226 | 0.064087 | 0.20142 | 0.12817 | 0.054932 | 0.073242 | 122.4884 | 122.5113 | -0.11444 | -0.10986 | 122.4976 | 122.5662 | 122.4472 | 122.5433
2232.3125 | 122.644 | -122.4976 | 0.1236 | -0.011291 | 0.067855 | 0.017816 | 0.023112 | -0.001476 | -0.0029694 | 0.0017667 | -0.0015565 | 0.025929 | 0.018848 | 0.0089187 | 0.0013991 | 0.018171 | -0.0040567 | -0.10071 | 0.082397 | -0.073242 | -0.1236 | -0.004578 | -0.10529 | -0.064087 | -0.082397 | 0.09613 | -0.07782 | -0.013733 | 0.018311 | -0.064087 | 0.09613 | 122.4243 | -0.041199 | -0.24719 | 122.493 | 122.4335 | 122.3923 | 0.009155 | -0.032044 | 122.4197 | -0.027466 | -0.13733 | 122.5159 | 122.5937 | 122.4335 | 0.17395 | 0.013733 | 0.068664 | -0.050354 | 0.096131 | 0.064087 | 0.15564 | 0.17395 | 122.58 | 122.5937 | -0.19684 | -0.20142 | 122.374 | 122.4838 | 122.3969 | 122.4152
2234 | 122.6624 | -122.5021 | 0.12817 | -0.0036622 | 0.064865 | 0.014398 | 0.022257 | -0.0061758 | -0.0012604 | 0.00027129 | 0.0045471 | 0.024434 | 0.018634 | 0.014473 | -0.0043687 | 0.016462 | -0.0038431 | -0.11444 | 0.086975 | -0.09613 | -0.091553 | 0.036621 | -0.050354 | -0.022888 | -0.073242 | 0.086975 | -0.091553 | -0.050354 | 0.054932 | -0.027466 | 0.082397 | 122.406 | -0.041199 | -0.21973 | 122.5388 | 122.4792 | 122.4518 | 0.073242 | 0.045776 | 122.4106 | -0.041199 | -0.17853 | 122.5571 | 122.5845 | 122.4747 | 0.17395 | 0.064087 | 0.13275 | 0.004577 | 0.14649 | 0.041199 | 0.1831 | 0.17853 | 122.5891 | 122.5891 | -0.2243 | -0.21973 | 122.4106 | 122.4518 | 122.3877 | 122.4289
2235.75 | 122.7127 | -122.4701 | 0.10529 | 0.0039673 | 0.065719 | 0.01568 | 0.02418 | 0.0032236 | -0.001474 | -0.0010105 | 0.0014953 | 0.025075 | 0.019489 | 0.02195 | 0.0022537 | 0.020093 | -0.0040567 | -0.09613 | 0.07782 | -0.082397 | -0.10071 | 0.041199 | -0.086975 | -0.045776 | -0.041199 | 0.073242 | -0.073242 | 0.018311 | 0.073242 | 0.004578 | 0.14191 | 122.3877 | -0.027466 | -0.20599 | 122.5113 | 122.4243 | 122.3831 | 0.036621 | -0.004578 | 122.3969 | -0.032044 | -0.086975 | 122.5433 | 122.612 | 122.4747 | 0.21515 | 0.07782 | 0.1236 | -0.018311 | 0.14648 | 0.091553 | 0.16022 | 0.14648 | 122.5479 | 122.5433 | -0.18768 | -0.17853 | 122.3694 | 122.4884 | 122.374 | 122.4289
2237.4375 | 122.7402 | -122.4838 | 0.091553 | -0.0036622 | 0.064224 | 0.017175 | 0.022257 | 0.0017282 | -0.0012604 | -0.0012241 | -0.0046081 | 0.023152 | 0.019703 | 0.020027 | -0.0026597 | 0.018598 | -0.0010659 | -0.07782 | 0.068665 | -0.027466 | -0.045776 | 0.10071 | -0.013733 | 0.018311 | -0.004578 | 0.064087 | -0.064087 | 0.022888 | 0.11444 | 0.050354 | 0.14648 | 122.4564 | -0.022888 | -0.13733 | 122.5845 | 122.5021 | 122.4701 | 0.045777 | 0.013733 | 122.4197 | -0.027466 | -0.068665 | 122.5983 | 122.6303 | 122.5342 | 0.21057 | 0.11444 | 0.12817 | -0.01831 | 0.17853 | 0.086975 | 0.096131 | 0.12817 | 122.5525 | 122.5479 | -0.11902 | -0.15564 | 122.438 | 122.5067 | 122.406 | 122.4792
2239.1875 | 122.7905 | -122.4609 | 0.073242 | 0.0039673 | 0.065719 | 0.01568 | 0.020335 | -0.002117 | -0.0029694 | -0.0018649 | -0.0046081 | 0.021443 | 0.018634 | 0.020668 | -0.0030869 | 0.017957 | -0.0032021 | -0.032043 | 0.041199 | -0.032043 | 0.032043 | 0.21057 | 0.073242 | 0.091553 | 0.086975 | 0.045776 | -0.036621 | 0.082397 | 0.19684 | 0.11444 | 0.1831 | 122.4289 | -0.032043 | -0.041199 | 122.6715 | 122.5525 | 122.5342 | 0.1236 | 0.10529 | 122.4243 | -0.027466 | 0.009155 | 122.6578 | 122.644 | 122.5754 | 0.21973 | 0.15106 | 0.24261 | 0.064086 | 0.23346 | 0.11902 | 0.073242 | 0.082397 | 122.5021 | 122.5067 | -0.10529 | -0.10986 | 122.493 | 122.5433 | 122.4289 | 122.5479
2240.9531 | 122.6761 | -122.5296 | 0.11444 | -0.011291 | 0.06871 | 0.017603 | 0.02183 | -0.0010488 | -0.0033966 | -0.00079691 | -0.0046081 | 0.025929 | 0.021839 | 0.012978 | -0.0033005 | 0.016034 | -0.00021153 | -0.091553 | 0.082397 | -0.086975 | -0.10071 | 0.050354 | -0.050354 | -0.022888 | -0.068665 | 0.10986 | -0.07782 | -0.041199 | 0.054932 | -0.036621 | 0.082397 | 122.4426 | -0.032044 | -0.21515 | 122.58 | 122.5067 | 122.4792 | 0.064087 | 0.036621 | 122.4518 | -0.004578 | -0.15564 | 122.5845 | 122.612 | 122.493 | 0.16022 | 0.041199 | 0.13733 | -0.013733 | 0.13275 | 0.036621 | 0.16937 | 0.18768 | 122.612 | 122.6395 | -0.20142 | -0.19226 | 122.4289 | 122.4884 | 122.438 | 122.4609
2242.7031 | 122.644 | -122.525 | 0.11444 | -0.0036622 | 0.06636 | 0.015466 | 0.024394 | 0.0019418 | -0.0021148 | -0.00079691 | -0.0046081 | 0.026357 | 0.019916 | 0.015755 | 0.00011755 | 0.016675 | -0.0029885 | -0.09613 | 0.09613 | -0.091553 | -0.12817 | -0.013733 | -0.11444 | -0.073242 | -0.11444 | 0.073242 | -0.082397 | -0.018311 | 0.022888 | -0.073242 | 0.091553 | 122.4335 | -0.018311 | -0.24262 | 122.5113 | 122.4518 | 122.4106 | 0.018311 | -0.022888 | 122.4426 | -0.041199 | -0.13275 | 122.5479 | 122.6166 | 122.4518 | 0.17395 | 0.009155 | 0.07782 | -0.036621 | 0.10528 | 0.064086 | 0.18768 | 0.15564 | 122.6212 | 122.5983 | -0.20599 | -0.19684 | 122.3969 | 122.5067 | 122.4289 | 122.4106
2244.375 | 122.731 | -122.493 | 0.11444 | -0.011291 | 0.065292 | 0.016107 | 0.020976 | -0.00062165 | -0.0046782 | -0.0016513 | -0.0015565 | 0.022939 | 0.018207 | 0.013618 | -0.0026597 | 0.017743 | 0.0025657 | -0.027466 | 0.050354 | -0.041199 | 0.004578 | 0.17853 | 0.059509 | 0.064087 | 0.036621 | 0.059509 | -0.064087 | 0.036621 | 0.14191 | 0.050354 | 0.15564 | 122.4518 | -0.064087 | -0.10986 | 122.6715 | 122.5571 | 122.5525 | 0.10529 | 0.10071 | 122.4289 | -0.054932 | -0.07782 | 122.6349 | 122.6486 | 122.5433 | 0.21973 | 0.11444 | 0.21973 | 0.045777 | 0.20599 | 0.10071 | 0.091553 | 0.1236 | 122.5433 | 122.5525 | -0.15564 | -0.17853 | 122.4976 | 122.5296 | 122.4655 | 122.5296
2246.125 | 122.6532 | -122.525 | 0.11902 | 0.0039673 | 0.066574 | 0.016534 | 0.023539 | -0.0023306 | -0.00040584 | 0.0011257 | -0.0015565 | 0.025075 | 0.018421 | 0.021522 | 0.00054475 | 0.019239 | -0.0029885 | -0.09613 | 0.082397 | -0.086975 | -0.11444 | -0.022888 | -0.11902 | -0.082397 | -0.07782 | 0.10986 | -0.064087 | -0.018311 | 0.009155 | -0.068665 | 0.091553 | 122.438 | -0.036622 | -0.23346 | 122.5021 | 122.4426 | 122.406 | 0.004578 | -0.032044 | 122.4609 | -0.009156 | -0.13733 | 122.5342 | 122.6166 | 122.4564 | 0.15564 | -0.004578 | 0.064087 | -0.027466 | 0.073242 | 0.045776 | 0.16937 | 0.17395 | 122.6074 | 122.6349 | -0.20599 | -0.18311 | 122.4106 | 122.5067 | 122.4289 | 122.4472
2247.875 | 122.7585 | -122.4884 | 0.09613 | 0.0039673 | 0.06636 | 0.016534 | 0.020548 | -0.00083525 | -0.0012604 | -0.0010105 | -0.0046081 | 0.022725 | 0.019703 | 0.015114 | -0.00052345 | 0.018171 | 0.00021567 | -0.07782 | 0.059509 | -0.050354 | -0.045776 | 0.10986 | -0.013733 | 0.050354 | 0.004578 | 0.064087 | -0.064087 | 0.036621 | 0.13275 | 0.064087 | 0.16479 | 122.438 | -0.036621 | -0.14191 | 122.5983 | 122.5388 | 122.4747 | 0.10071 | 0.036621 | 122.4243 | -0.032043 | -0.059509 | 122.6212 | 122.6532 | 122.5525 | 0.22888 | 0.12817 | 0.16022 | 0.004578 | 0.19684 | 0.10071 | 0.10986 | 0.12817 | 122.5479 | 122.5525 | -0.14648 | -0.16022 | 122.4426 | 122.525 | 122.4106 | 122.493
2249.625 | 122.6624 | -122.4838 | 0.10529 | 0.0039673 | 0.066574 | 0.016962 | 0.021617 | 1.915e-05 | -0.0029694 | -0.00058311 | -0.0015565 | 0.025502 | 0.018421 | 0.016182 | 0.00011755 | 0.017957 | 0.00042947 | -0.054932 | 0.073242 | -0.064087 | -0.059509 | 0.07782 | -0.045776 | 0 | -0.013733 | 0.086975 | -0.064087 | 0 | 0.073242 | -0.036621 | 0.11444 | 122.4197 | -0.032044 | -0.16479 | 122.5616 | 122.4838 | 122.438 | 0.064087 | 0.018311 | 122.4197 | -0.018311 | -0.10529 | 122.5571 | 122.5983 | 122.4472 | 0.17853 | 0.027466 | 0.14191 | 0.004578 | 0.13733 | 0.064087 | 0.13733 | 0.15106 | 122.5571 | 122.5708 | -0.16937 | -0.16937 | 122.4243 | 122.4838 | 122.4289 | 122.4701
2251.3125 | 122.7997 | -122.4792 | 0.07782 | -0.011291 | 0.065933 | 0.016748 | 0.023112 | -0.0033986 | -0.0023284 | -0.0014377 | -0.0015565 | 0.022084 | 0.022052 | 0.017464 | 0.0018265 | 0.020093 | -0.00085233 | -0.027466 | 0.045776 | -0.050354 | 0.022888 | 0.16937 | 0.027466 | 0.054932 | 0.07782 | 0.059509 | -0.050354 | 0.11444 | 0.1831 | 0.091553 | 0.21057 | 122.4289 | -0.032044 | -0.054932 | 122.6486 | 122.5342 | 122.5067 | 0.10529 | 0.07782 | 122.4289 | -0.018311 | 0.036621 | 122.6624 | 122.6898 | 122.5708 | 0.26093 | 0.14191 | 0.21973 | 0.073242 | 0.23346 | 0.16479 | 0.09613 | 0.10986 | 122.525 | 122.5388 | -0.12817 | -0.12817 | 122.5021 | 122.5937 | 122.4518 | 122.5571
2253.0625 | 122.7997 | -122.4655 | 0.086975 | 0.0039673 | 0.065933 | 0.017389 | 0.023112 | 0.0015146 | -0.00061944 | 0.0028347 | -0.0046081 | 0.024434 | 0.019916 | 0.014686 | 0.0022537 | 0.018812 | -0.0038431 | -0.041199 | 0.064087 | -0.045776 | 0 | 0.15564 | 0.013733 | 0.054932 | 0.064087 | 0.059509 | -0.036621 | 0.10529 | 0.16479 | 0.086975 | 0.20142 | 122.4197 | -0.022888 | -0.086975 | 122.6212 | 122.5204 | 122.4792 | 0.10071 | 0.059509 | 122.4289 | -0.027466 | 0.018311 | 122.6303 | 122.6669 | 122.5525 | 0.23804 | 0.1236 | 0.20142 | 0.045776 | 0.20142 | 0.14191 | 0.10986 | 0.09613 | 122.5296 | 122.525 | -0.13275 | -0.1236 | 122.4655 | 122.5708 | 122.4243 | 122.5296
2254.8281 | 122.7219 | -122.4976 | 0.11444 | -0.011291 | 0.065719 | 0.017389 | 0.024394 | -0.0012624 | -0.0019012 | 0.00069849 | -0.0015565 | 0.027211 | 0.022052 | 0.011696 | -0.0015915 | 0.018598 | -0.0025613 | -0.054932 | 0.064087 | -0.064087 | -0.041199 | 0.1236 | -0.018311 | 0 | 0.009155 | 0.091553 | -0.068665 | 0.032043 | 0.10529 | 0.027466 | 0.13275 | 122.4335 | -0.050354 | -0.15564 | 122.6212 | 122.4976 | 122.4792 | 0.064087 | 0.045776 | 122.4289 | -0.022888 | -0.082398 | 122.6028 | 122.6303 | 122.525 | 0.20142 | 0.096131 | 0.18768 | 0.022888 | 0.17395 | 0.10071 | 0.12817 | 0.16022 | 122.5616 | 122.5891 | -0.17853 | -0.18311 | 122.4564 | 122.5296 | 122.4426 | 122.5067
2256.5156 | 122.7448 | -122.493 | 0.10071 | 0.0039673 | 0.063369 | 0.016534 | 0.020335 | -0.0023306 | -0.003183 | -0.00036951 | -0.0015565 | 0.020589 | 0.020771 | 0.015541 | -0.0035141 | 0.019239 | -0.00042513 | -0.086975 | 0.041199 | -0.054932 | -0.050354 | 0.10986 | -0.018311 | 0.018311 | -0.018311 | 0.059509 | -0.064087 | 0.018311 | 0.11902 | 0.027466 | 0.15564 | 122.438 | -0.059509 | -0.15106 | 122.6028 | 122.5113 | 122.4747 | 0.073243 | 0.036621 | 122.4289 | -0.041199 | -0.082397 | 122.612 | 122.6486 | 122.5204 | 0.21973 | 0.091553 | 0.16479 | 0.004578 | 0.18311 | 0.082398 | 0.096131 | 0.1236 | 122.5342 | 122.5525 | -0.15564 | -0.1648 | 122.4426 | 122.5113 | 122.406 | 122.4747
2258.2656 | 122.6761 | -122.5296 | 0.1236 | -0.011291 | 0.068069 | 0.016107 | 0.022685 | 0.001301 | -0.0021148 | -0.00058311 | -0.0046081 | 0.027638 | 0.019703 | 0.014046 | 0.00075835 | 0.020093 | -0.0023477 | -0.082397 | 0.07782 | -0.082397 | -0.10986 | 0.004578 | -0.10986 | -0.054932 | -0.082397 | 0.091553 | -0.073242 | -0.009155 | 0.027466 | -0.064087 | 0.10071 | 122.4472 | -0.045776 | -0.23346 | 122.5342 | 122.4747 | 122.4197 | 0.027465 | -0.027466 | 122.4564 | -0.032043 | -0.13275 | 122.5571 | 122.6303 | 122.4655 | 0.17395 | 0.009155 | 0.086975 | -0.027466 | 0.10071 | 0.064087 | 0.16022 | 0.16479 | 122.6074 | 122.6212 | -0.20599 | -0.19684 | 122.4197 | 122.5204 | 122.4472 | 122.4472
2260.0156 | 122.6669 | -122.5204 | 0.12817 | -0.0036622 | 0.067428 | 0.015253 | 0.02183 | 0.0027964 | -0.00083304 | 0.0024075 | -0.0015565 | 0.024434 | 0.018634 | 0.010841 | -0.0020187 | 0.01753 | -0.0036295 | -0.086975 | 0.082397 | -0.07782 | -0.10986 | 0.036621 | -0.10529 | -0.054932 | -0.10529 | 0.086975 | -0.086975 | -0.050354 | 0.009155 | -0.068665 | 0.09613 | 122.4426 | -0.045777 | -0.23804 | 122.5571 | 122.4655 | 122.4152 | 0.022888 | -0.027466 | 122.4335 | -0.041199 | -0.17853 | 122.5296 | 122.6166 | 122.4518 | 0.1831 | 0.01831 | 0.11444 | -0.032043 | 0.09613 | 0.036621 | 0.16022 | 0.17395 | 122.6028 | 122.6074 | -0.20599 | -0.21515 | 122.4106 | 122.4701 | 122.4335 | 122.4152
2261.7031 | 122.7768 | -122.4884 | 0.10529 | -0.011291 | 0.063369 | 0.01568 | 0.021403 | -0.0029714 | -0.0019012 | -0.0020785 | -0.0046081 | 0.022512 | 0.019062 | 0.016182 | -9.605e-05 | 0.016675 | -0.0053385 | -0.091553 | 0.064087 | -0.054932 | -0.018311 | 0.13275 | 0.013733 | 0.045776 | 0.022888 | 0.059509 | -0.050354 | 0.07782 | 0.16022 | 0.07782 | 0.1831 | 122.4335 | -0.041199 | -0.1236 | 122.6212 | 122.5342 | 122.5021 | 0.10071 | 0.068665 | 122.438 | -0.045777 | -0.027466 | 122.6486 | 122.6715 | 122.5662 | 0.23346 | 0.12817 | 0.18768 | 0.036621 | 0.21057 | 0.12817 | 0.11902 | 0.10986 | 122.5525 | 122.5479 | -0.16022 | -0.15564 | 122.4701 | 122.5662 | 122.3969 | 122.5113
2263.4531 | 122.8134 | -122.4976 | 0.082397 | -0.0036622 | 0.06636 | 0.015894 | 0.018412 | -0.006603 | -0.0029694 | -0.0020785 | -0.0015565 | 0.022084 | 0.018207 | 0.023445 | -0.0018051 | 0.018171 | -0.0034159 | -0.050354 | 0.032043 | -0.059509 | 0.022888 | 0.17395 | 0.050354 | 0.082397 | 0.086975 | 0.064087 | -0.036621 | 0.10986 | 0.21057 | 0.12817 | 0.21515 | 122.438 | -0.050354 | -0.059509 | 122.6715 | 122.58 | 122.5479 | 0.14191 | 0.10986 | 122.4609 | -0.01831 | 0.027466 | 122.7081 | 122.7127 | 122.6257 | 0.25177 | 0.1648 | 0.23346 | 0.082397 | 0.24719 | 0.14648 | 0.091552 | 0.10071 | 122.5296 | 122.5616 | -0.14191 | -0.11902 | 122.5204 | 122.6074 | 122.4472 | 122.5845
2265.1406 | 122.7722 | -122.4701 | 0.091553 | -0.0036622 | 0.066146 | 0.017603 | 0.023326 | -0.0010488 | -0.00061944 | -0.00015591 | 0.0014953 | 0.022512 | 0.018848 | 0.011269 | 0.0020401 | 0.01988 | 0.00085667 | -0.022888 | 0.050354 | -0.041199 | 0.013733 | 0.18768 | 0.018311 | 0.073242 | 0.091553 | 0.041199 | -0.041199 | 0.082397 | 0.15564 | 0.07782 | 0.1831 | 122.4289 | -0.041199 | -0.07782 | 122.6578 | 122.5433 | 122.4884 | 0.11444 | 0.05951 | 122.4289 | -0.050354 | -0.009156 | 122.6257 | 122.6532 | 122.5479 | 0.2243 | 0.11902 | 0.22888 | 0.054932 | 0.19684 | 0.1236 | 0.091553 | 0.082398 | 122.5204 | 122.5113 | -0.13275 | -0.13275 | 122.4838 | 122.5525 | 122.4472 | 122.5616
2266.875 | 122.7951 | -122.4838 | 0.091553 | -0.0036622 | 0.069351 | 0.018884 | 0.023326 | -0.002117 | -0.0010468 | -0.0010105 | -0.0015565 | 0.02358 | 0.020557 | 0.019813 | -9.605e-05 | 0.019239 | -0.00042513 | -0.018311 | 0.041199 | -0.032043 | 0.032043 | 0.17395 | 0.018311 | 0.059509 | 0.082397 | 0.068665 | -0.054932 | 0.10071 | 0.16479 | 0.10529 | 0.1831 | 122.4518 | -0.050354 | -0.05951 | 122.6578 | 122.5433 | 122.5021 | 0.091552 | 0.050354 | 122.4289 | -0.022888 | 0.009155 | 122.6486 | 122.6669 | 122.5891 | 0.23804 | 0.16022 | 0.20599 | 0.064086 | 0.21973 | 0.15564 | 0.073242 | 0.1236 | 122.525 | 122.5525 | -0.1236 | -0.14649 | 122.5159 | 122.5845 | 122.4655 | 122.5662
2268.6094 | 122.7951 | -122.4884 | 0.068665 | -0.018921 | 0.064437 | 0.015894 | 0.020548 | -0.00083525 | -0.0044646 | -0.0020785 | 0.0045471 | 0.023152 | 0.019916 | 0.015968 | -0.0028733 | 0.019025 | -0.00063873 | -0.041199 | 0.032043 | -0.041199 | 0.022888 | 0.20599 | 0.068665 | 0.082397 | 0.082397 | 0.068665 | -0.041199 | 0.07782 | 0.20142 | 0.09613 | 0.19226 | 122.4472 | -0.036622 | -0.045777 | 122.6944 | 122.5708 | 122.5571 | 0.1236 | 0.10986 | 122.4472 | 0 | 0.009155 | 122.6898 | 122.6807 | 122.5845 | 0.23346 | 0.13733 | 0.24719 | 0.064087 | 0.24262 | 0.11902 | 0.073242 | 0.10986 | 122.5204 | 122.5571 | -0.10986 | -0.10986 | 122.5113 | 122.5662 | 122.4472 | 122.5708
2270.3594 | 122.7219 | -122.5204 | 0.10071 | -0.0036622 | 0.067855 | 0.016107 | 0.021617 | -0.005535 | -0.001474 | -0.0016513 | -0.0015565 | 0.024861 | 0.017994 | 0.014046 | -0.00095065 | 0.015607 | -0.0021341 | -0.045776 | 0.064087 | -0.073242 | -0.059509 | 0.09613 | -0.032043 | 0 | 0.004578 | 0.091553 | -0.064087 | 0.027466 | 0.10071 | 0.009155 | 0.14191 | 122.4472 | -0.036621 | -0.16022 | 122.6166 | 122.5204 | 122.4884 | 0.073242 | 0.041199 | 122.4564 | -0.009155 | -0.073242 | 122.6212 | 122.6624 | 122.5296 | 0.20599 | 0.073242 | 0.16937 | 0.013733 | 0.1648 | 0.091553 | 0.13733 | 0.15564 | 122.5845 | 122.612 | -0.17395 | -0.1648 | 122.4609 | 122.5479 | 122.4747 | 122.525
2272.1094 | 122.6761 | -122.5204 | 0.1236 | 0.0039673 | 0.064865 | 0.017816 | 0.023966 | -0.00019445 | -0.0016876 | -0.0022921 | -0.0076599 | 0.024221 | 0.020343 | 0.014046 | -9.605e-05 | 0.016675 | -0.00063873 | -0.086975 | 0.082397 | -0.07782 | -0.10986 | 0 | -0.12817 | -0.064087 | -0.09613 | 0.07782 | -0.073242 | -0.032043 | 0.022888 | -0.068665 | 0.09613 | 122.4426 | -0.041199 | -0.23346 | 122.5204 | 122.4564 | 122.3923 | 0.013733 | -0.050354 | 122.4472 | -0.045776 | -0.15564 | 122.5433 | 122.6166 | 122.4518 | 0.16937 | 0.004577 | 0.07782 | -0.032043 | 0.09613 | 0.041199 | 0.16022 | 0.15106 | 122.6028 | 122.5983 | -0.20142 | -0.19684 | 122.4106 | 122.4884 | 122.4335 | 122.4243
2273.875 | 122.8134 | -122.4838 | 0.091553 | -0.018921 | 0.064224 | 0.016321 | 0.02183 | -0.00019445 | -0.0029694 | -0.00079691 | -0.010712 | 0.02123 | 0.01778 | 0.01725 | -0.0015915 | 0.019666 | 0.00064307 | -0.07782 | 0.050354 | -0.036621 | -0.018311 | 0.13733 | 0.018311 | 0.045776 | 0.022888 | 0.054932 | -0.068665 | 0.059509 | 0.15564 | 0.10071 | 0.20142 | 122.4472 | -0.041199 | -0.10986 | 122.6212 | 122.5296 | 122.5021 | 0.082397 | 0.054932 | 122.4152 | -0.036621 | -0.032044 | 122.6395 | 122.6852 | 122.5845 | 0.27008 | 0.16937 | 0.17395 | 0.01831 | 0.22431 | 0.12817 | 0.086975 | 0.1236 | 122.5342 | 122.5388 | -0.12817 | -0.16022 | 122.4655 | 122.5433 | 122.406 | 122.5067
2275.5625 | 122.7264 | -122.5159 | 0.10071 | -0.011291 | 0.06636 | 0.017175 | 0.019908 | -0.00062165 | -0.004251 | -0.0025057 | -0.0076599 | 0.023152 | 0.019275 | 0.015968 | -0.0030869 | 0.018598 | -0.0040567 | -0.027466 | 0.045776 | -0.045776 | -0.004578 | 0.16479 | 0.045776 | 0.059509 | 0.018311 | 0.068665 | -0.059509 | 0.022888 | 0.11444 | 0.036621 | 0.12817 | 122.4701 | -0.054932 | -0.10529 | 122.6807 | 122.5754 | 122.5616 | 0.10528 | 0.091552 | 122.4564 | -0.032043 | -0.07782 | 122.6303 | 122.644 | 122.5525 | 0.18768 | 0.09613 | 0.21057 | 0.041198 | 0.17395 | 0.082397 | 0.091552 | 0.12817 | 122.5616 | 122.5845 | -0.14648 | -0.16022 | 122.5113 | 122.5388 | 122.4884 | 122.5342
2277.2969 | 122.7173 | -122.5479 | 0.086975 | -0.011291 | 0.064224 | 0.015253 | 0.020335 | -0.001476 | -0.00083304 | 0.00091209 | -0.0046081 | 0.023152 | 0.019275 | 0.011696 | -0.0020187 | 0.017743 | 0.0036337 | -0.041199 | 0.036621 | -0.050354 | 0 | 0.16022 | 0.045776 | 0.050354 | 0.022888 | 0.064087 | -0.059509 | 0.013733 | 0.10529 | 0.027466 | 0.1236 | 122.4976 | -0.050354 | -0.086975 | 122.7081 | 122.5983 | 122.5937 | 0.10071 | 0.09613 | 122.4884 | -0.022888 | -0.073242 | 122.6532 | 122.6715 | 122.5754 | 0.1831 | 0.086975 | 0.21057 | 0.050354 | 0.16479 | 0.073242 | 0.086975 | 0.1236 | 122.5845 | 122.612 | -0.13733 | -0.14648 | 122.5479 | 122.5616 | 122.5067 | 122.5708
2279.0625 | 122.7081 | -122.5342 | 0.10986 | -0.011291 | 0.066787 | 0.016321 | 0.025248 | 0.00087375 | -0.0016876 | -0.0027195 | -0.0015565 | 0.025502 | 0.018848 | 0.0082779 | 0.00075835 | 0.017743 | -0.0027749 | -0.041199 | 0.073242 | -0.073242 | -0.022888 | 0.10986 | -0.018311 | 0 | -0.004578 | 0.07782 | -0.064087 | 0.022888 | 0.086975 | -0.013733 | 0.1236 | 122.4609 | -0.036621 | -0.13275 | 122.644 | 122.5342 | 122.5159 | 0.073242 | 0.054931 | 122.4701 | -0.032043 | -0.086975 | 122.6212 | 122.6578 | 122.5204 | 0.18768 | 0.050354 | 0.18311 | 0.050354 | 0.15106 | 0.086975 | 0.14648 | 0.14191 | 122.6074 | 122.612 | -0.18311 | -0.17395 | 122.5113 | 122.5571 | 122.493 | 122.5296
2280.75 | 122.7173 | -122.525 | 0.11444 | 0.0039673 | 0.064865 | 0.016321 | 0.024821 | -0.00040805 | -0.0019012 | -0.0029331 | -0.0015565 | 0.025289 | 0.019275 | 0.0061417 | 0.0011855 | 0.017103 | -0.0025613 | -0.045776 | 0.073242 | -0.082397 | -0.050354 | 0.10071 | -0.018311 | -0.009155 | 0.013733 | 0.09613 | -0.07782 | 0.022888 | 0.10986 | 0.018311 | 0.15106 | 122.4426 | -0.041199 | -0.16479 | 122.6257 | 122.5159 | 122.5067 | 0.073242 | 0.064086 | 122.4472 | -0.018311 | -0.091553 | 122.6349 | 122.6761 | 122.5433 | 0.22888 | 0.096131 | 0.18311 | 0.032043 | 0.18768 | 0.10071 | 0.15564 | 0.17395 | 122.5983 | 122.6212 | -0.19684 | -0.19226 | 122.4747 | 122.5479 | 122.4792 | 122.5388
2282.4844 | 122.731 | -122.5388 | 0.10986 | 0.0039673 | 0.065292 | 0.015253 | 0.022898 | -0.0016898 | -0.0036102 | -0.0025057 | -0.010712 | 0.02358 | 0.019062 | 0.015114 | 0.00011755 | 0.016034 | -0.00021153 | -0.091553 | 0.086975 | -0.10529 | -0.09613 | 0.041199 | -0.036621 | -0.018311 | -0.073242 | 0.10986 | -0.073242 | 0.004578 | 0.07782 | 0 | 0.13275 | 122.4335 | -0.022888 | -0.20599 | 122.58 | 122.5204 | 122.5021 | 0.086975 | 0.068665 | 122.4655 | 0 | -0.10529 | 122.6166 | 122.6715 | 122.5388 | 0.20599 | 0.073242 | 0.14649 | 0.009156 | 0.15106 | 0.07782 | 0.19226 | 0.18311 | 122.6257 | 122.6486 | -0.21515 | -0.18311 | 122.4426 | 122.5433 | 122.4472 | 122.4655
2284.2031 | 122.6669 | -122.5525 | 0.10529 | -0.011291 | 0.065719 | 0.018243 | 0.023112 | -0.00019445 | 2.1362e-05 | -0.00036951 | -0.0046081 | 0.024221 | 0.02013 | 0.0052871 | 0.00097195 | 0.017957 | -0.00021153 | -0.07782 | 0.07782 | -0.064087 | -0.10529 | 0.045776 | -0.09613 | -0.054932 | -0.086975 | 0.09613 | -0.082397 | -0.027466 | 0.027466 | -0.073242 | 0.086975 | 122.4884 | -0.027466 | -0.21057 | 122.5983 | 122.4976 | 122.4564 | 0.009155 | -0.032043 | 122.4701 | -0.009156 | -0.13275 | 122.58 | 122.6395 | 122.4792 | 0.16937 | 0.009155 | 0.10986 | -0.041199 | 0.10986 | 0.054931 | 0.14191 | 0.17853 | 122.6303 | 122.6486 | -0.16937 | -0.18768 | 122.4472 | 122.525 | 122.4747 | 122.4655
2285.9219 | 122.7676 | -122.5021 | 0.091553 | -0.0036622 | 0.064224 | 0.014398 | 0.020976 | -0.0023306 | -0.0046782 | -0.0010105 | -0.0015565 | 0.022298 | 0.017994 | 0.015968 | 0.00054475 | 0.017103 | -0.00021153 | -0.09613 | 0.032043 | -0.045776 | -0.045776 | 0.10529 | -0.018311 | 0.032043 | -0.032043 | 0.068665 | -0.050354 | 0.027466 | 0.13275 | 0.036621 | 0.15106 | 122.4564 | -0.05951 | -0.13733 | 122.6074 | 122.5342 | 122.4838 | 0.077819 | 0.027465 | 122.4518 | -0.022888 | -0.064087 | 122.6349 | 122.6532 | 122.5388 | 0.20142 | 0.086975 | 0.15106 | 0 | 0.18311 | 0.07782 | 0.077819 | 0.11902 | 122.5342 | 122.5708 | -0.13733 | -0.14191 | 122.4564 | 122.5296 | 122.406 | 122.4701
2287.6719 | 122.7859 | -122.4976 | 0.086975 | 0.011597 | 0.065719 | 0.017175 | 0.022257 | -0.00019445 | -0.0010468 | -0.0010105 | -0.0015565 | 0.023793 | 0.018634 | 0.023872 | 0.0011855 | 0.017103 | 0.0047019 | -0.032043 | 0.041199 | -0.018311 | 0.004578 | 0.17395 | 0.018311 | 0.068665 | 0.073242 | 0.059509 | -0.041199 | 0.059509 | 0.15106 | 0.068665 | 0.17853 | 122.4792 | -0.045776 | -0.082397 | 122.6715 | 122.5662 | 122.5159 | 0.086976 | 0.036622 | 122.4564 | -0.027466 | -0.027466 | 122.6486 | 122.6761 | 122.5662 | 0.21973 | 0.10986 | 0.19226 | 0.022889 | 0.19226 | 0.10071 | 0.05951 | 0.10071 | 122.5388 | 122.5571 | -0.10529 | -0.12817 | 122.5021 | 122.5571 | 122.4655 | 122.5708
2289.4219 | 122.7676 | -122.5021 | 0.10529 | 0.0039673 | 0.065505 | 0.015894 | 0.022257 | -0.00040805 | -0.0029694 | 0.00091209 | 0.0045471 | 0.022084 | 0.019275 | 0.019173 | 0.0022537 | 0.019666 | -0.0034159 | -0.054932 | 0.041199 | -0.045776 | -0.018311 | 0.14191 | -0.004578 | 0.027466 | 0.041199 | 0.054932 | -0.050354 | 0.050354 | 0.12817 | 0.050354 | 0.15106 | 122.4564 | -0.064087 | -0.1236 | 122.644 | 122.5296 | 122.4976 | 0.073242 | 0.041198 | 122.4518 | -0.050354 | -0.054932 | 122.6303 | 122.6532 | 122.5525 | 0.20142 | 0.10071 | 0.18768 | 0.027465 | 0.17853 | 0.10071 | 0.086975 | 0.10529 | 122.5433 | 122.5571 | -0.15106 | -0.15564 | 122.4838 | 122.5525 | 122.4472 | 122.5433
2291.125 | 122.6944 | -122.5525 | 0.13275 | -0.011291 | 0.065719 | 0.013971 | 0.022257 | 0.00023275 | -0.0027556 | -0.0033603 | -0.0046081 | 0.025075 | 0.018848 | 0.014473 | -0.0033005 | 0.016248 | -0.00042513 | -0.11444 | 0.086975 | -0.086975 | -0.11902 | 0.041199 | -0.064087 | -0.027466 | -0.07782 | 0.09613 | -0.07782 | -0.059509 | 0.050354 | -0.041199 | 0.086975 | 122.4655 | -0.045776 | -0.25177 | 122.5937 | 122.525 | 122.4884 | 0.059509 | 0.022888 | 122.4747 | -0.036621 | -0.19226 | 122.6028 | 122.6395 | 122.5113 | 0.16479 | 0.036621 | 0.12817 | -0.032044 | 0.12817 | 0.018311 | 0.17395 | 0.17395 | 122.6395 | 122.6486 | -0.21973 | -0.21057 | 122.4335 | 122.493 | 122.438 | 122.4747
2292.875 | 122.699 | -122.5021 | 0.11444 | -0.011291 | 0.064865 | 0.016962 | 0.024394 | -0.002117 | -0.0038238 | -0.0035739 | 0.0014953 | 0.026143 | 0.019275 | 0.017677 | 0.0028945 | 0.018171 | 0.0021383 | -0.10529 | 0.086975 | -0.07782 | -0.10071 | 0.036621 | -0.10986 | -0.059509 | -0.064087 | 0.086975 | -0.050354 | -0.009155 | 0.045776 | -0.041199 | 0.10071 | 122.4243 | -0.027466 | -0.21515 | 122.5388 | 122.4426 | 122.3923 | 0.018311 | -0.032043 | 122.4518 | -0.027466 | -0.1236 | 122.5479 | 122.6028 | 122.4609 | 0.15106 | 0.009155 | 0.11444 | -0.022888 | 0.09613 | 0.041199 | 0.16479 | 0.13733 | 122.5891 | 122.5891 | -0.19226 | -0.16479 | 122.4014 | 122.493 | 122.3968 | 122.438
2294.5469 | 122.8546 | -122.4792 | 0.068665 | 0.0039673 | 0.064224 | 0.015253 | 0.020121 | -0.0019034 | -0.0023284 | -0.0010105 | -0.0076599 | 0.024007 | 0.020984 | 0.021095 | -0.0011643 | 0.019452 | -0.00042513 | -0.027466 | 0.032043 | -0.036621 | 0.036621 | 0.20142 | 0.073242 | 0.086975 | 0.11444 | 0.064087 | -0.032043 | 0.091553 | 0.20599 | 0.11902 | 0.19226 | 122.4426 | -0.036622 | -0.032044 | 122.6807 | 122.5662 | 122.5525 | 0.1236 | 0.10986 | 122.4472 | -0.004578 | 0.022888 | 122.6852 | 122.6715 | 122.5983 | 0.2243 | 0.15106 | 0.23804 | 0.073242 | 0.23804 | 0.1236 | 0.068664 | 0.09613 | 122.5113 | 122.5433 | -0.10529 | -0.10071 | 122.5159 | 122.5708 | 122.4518 | 122.5937
2296.2969 | 122.699 | -122.5479 | 0.13275 | -0.011291 | 0.062728 | 0.014398 | 0.022685 | 0.0015146 | -0.002542 | -0.0022921 | -0.0046081 | 0.024221 | 0.017566 | 0.01255 | -0.0022325 | 0.01753 | -0.0014931 | -0.09613 | 0.068665 | -0.082397 | -0.07782 | 0.068665 | -0.050354 | -0.013733 | -0.064087 | 0.091553 | -0.073242 | -0.022888 | 0.059509 | -0.032043 | 0.086975 | 122.4655 | -0.064086 | -0.21057 | 122.6166 | 122.5342 | 122.4976 | 0.068664 | 0.032043 | 122.4747 | -0.041198 | -0.15564 | 122.6074 | 122.6349 | 122.5159 | 0.16022 | 0.041199 | 0.15106 | 0.004577 | 0.13275 | 0.050354 | 0.15106 | 0.16479 | 122.6166 | 122.6395 | -0.21515 | -0.20599 | 122.4701 | 122.525 | 122.4518 | 122.4838
2297.9688 | 122.6898 | -122.5616 | 0.11902 | -0.011291 | 0.066146 | 0.015039 | 0.024394 | 0.0015146 | -0.0012604 | -0.0018649 | -0.0015565 | 0.024434 | 0.018634 | 0.013191 | 0.0016129 | 0.015821 | -0.0021341 | -0.082397 | 0.07782 | -0.073242 | -0.09613 | 0.013733 | -0.09613 | -0.064087 | -0.10071 | 0.086975 | -0.054932 | -0.032043 | 0.027466 | -0.064087 | 0.086975 | 122.4884 | -0.041199 | -0.21515 | 122.5754 | 122.4976 | 122.4655 | 0.009155 | -0.022888 | 122.5067 | -0.032044 | -0.15106 | 122.5891 | 122.6486 | 122.4976 | 0.14191 | -0.009155 | 0.086975 | -0.022888 | 0.082398 | 0.022889 | 0.15106 | 0.14191 | 122.6395 | 122.6486 | -0.19226 | -0.17395 | 122.4655 | 122.5296 | 122.4792 | 122.4609
2299.7188 | 122.7264 | -122.5388 | 0.091553 | -0.0036622 | 0.06636 | 0.01568 | 0.022685 | 0.00044655 | -0.00019224 | -0.0010105 | -0.0046081 | 0.024434 | 0.021625 | 0.01255 | 0.0024673 | 0.019452 | -0.0014931 | -0.10071 | 0.09613 | -0.07782 | -0.10071 | 0.022888 | -0.091553 | -0.054932 | -0.068665 | 0.07782 | -0.068665 | 0.018311 | 0.064087 | -0.036621 | 0.10986 | 122.4609 | 0.004577 | -0.19226 | 122.5616 | 122.4838 | 122.4472 | 0.022888 | -0.013733 | 122.4701 | -0.013733 | -0.073242 | 122.6028 | 122.6486 | 122.5021 | 0.17853 | 0.032044 | 0.10071 | -0.022888 | 0.13275 | 0.086976 | 0.17395 | 0.14649 | 122.6349 | 122.6166 | -0.16937 | -0.16022 | 122.438 | 122.5571 | 122.438 | 122.4701
2301.4062 | 122.731 | -122.5296 | 0.10071 | -0.011291 | 0.065719 | 0.015466 | 0.022898 | -0.002117 | -0.0019012 | 0.00048489 | -0.0015565 | 0.02358 | 0.022052 | 0.011696 | 0.00011755 | 0.01753 | -0.0019205 | -0.054932 | 0.068665 | -0.068665 | -0.036621 | 0.091553 | -0.013733 | 0 | -0.013733 | 0.073242 | -0.07782 | 0.032043 | 0.10986 | 0.009155 | 0.14191 | 122.4609 | -0.032043 | -0.13733 | 122.6212 | 122.5296 | 122.5159 | 0.068665 | 0.054932 | 122.4518 | -0.027466 | -0.068665 | 122.6395 | 122.6715 | 122.5388 | 0.21973 | 0.086975 | 0.16022 | 0.032044 | 0.18768 | 0.10986 | 0.13733 | 0.15106 | 122.5983 | 122.6028 | -0.16937 | -0.17853 | 122.493 | 122.5616 | 122.4747 | 122.5159
2303.1406 | 122.6852 | -122.5662 | 0.11444 | -0.0036622 | 0.065933 | 0.014612 | 0.020335 | -0.0025442 | -0.0029694 | 5.7688e-05 | -0.0015565 | 0.024007 | 0.019275 | 0.012337 | -0.0058639 | 0.017957 | 0.0012839 | -0.11902 | 0.091553 | -0.086975 | -0.11902 | 0.045776 | -0.054932 | -0.036621 | -0.091553 | 0.11444 | -0.082397 | -0.036621 | 0.036621 | -0.022888 | 0.09613 | 122.4792 | -0.022888 | -0.23346 | 122.612 | 122.5296 | 122.5113 | 0.050354 | 0.032043 | 122.4838 | 0 | -0.15106 | 122.6028 | 122.6624 | 122.5433 | 0.17853 | 0.059509 | 0.13275 | -0.032044 | 0.11902 | 0.045776 | 0.17853 | 0.19684 | 122.6578 | 122.6807 | -0.20142 | -0.19684 | 122.4472 | 122.5296 | 122.4472 | 122.4747
2304.8906 | 122.7768 | -122.525 | 0.10529 | -0.0036622 | 0.065933 | 0.018457 | 0.022685 | -0.0025442 | -0.001474 | 0.00027129 | -0.0046081 | 0.025502 | 0.020557 | 0.014473 | 0.00075835 | 0.01988 | -0.0032021 | -0.10986 | 0.07782 | -0.068665 | -0.091553 | 0.050354 | -0.073242 | -0.036621 | -0.022888 | 0.068665 | -0.064087 | 0.045776 | 0.11902 | 0.018311 | 0.15564 | 122.4564 | -0.027466 | -0.19684 | 122.5754 | 122.4884 | 122.4518 | 0.032044 | -0.004577 | 122.4609 | -0.036621 | -0.05951 | 122.644 | 122.6807 | 122.5433 | 0.21973 | 0.082398 | 0.11902 | -0.022888 | 0.18311 | 0.10986 | 0.14649 | 0.13275 | 122.6028 | 122.5937 | -0.17395 | -0.16937 | 122.4335 | 122.5708 | 122.4152 | 122.5021
2306.5781 | 122.6898 | -122.5433 | 0.1236 | -0.0036622 | 0.067855 | 0.017389 | 0.022898 | -0.0016898 | -0.003183 | -0.00079691 | 0.0014953 | 0.022725 | 0.017994 | 0.011055 | 0.00011755 | 0.019025 | 0.0014975 | -0.10529 | 0.073242 | -0.086975 | -0.11444 | -0.004578 | -0.10529 | -0.059509 | -0.13275 | 0.10071 | -0.068665 | -0.027466 | 0.022888 | -0.068665 | 0.091553 | 122.4564 | -0.050354 | -0.23804 | 122.5388 | 122.4838 | 122.438 | 0.027466 | -0.018311 | 122.4747 | -0.022888 | -0.15106 | 122.5662 | 122.6349 | 122.4747 | 0.16022 | 0 | 0.082397 | -0.027466 | 0.091553 | 0.041199 | 0.16022 | 0.16937 | 122.6166 | 122.644 | -0.21057 | -0.19226 | 122.4289 | 122.5159 | 122.438 | 122.4106
2308.3281 | 122.7493 | -122.5342 | 0.10529 | -0.011291 | 0.067214 | 0.016534 | 0.021189 | 0.001301 | -0.002542 | 0.0019803 | -0.0015565 | 0.024221 | 0.021412 | 0.0102 | -0.00030965 | 0.017743 | -0.0019205 | -0.07782 | 0.07782 | -0.073242 | -0.041199 | 0.11444 | -0.022888 | 0.004578 | 0.004578 | 0.091553 | -0.059509 | 0.022888 | 0.10529 | 0 | 0.12817 | 122.4609 | -0.027466 | -0.14649 | 122.6486 | 122.5388 | 122.5113 | 0.07782 | 0.050354 | 122.4747 | -0.013733 | -0.082398 | 122.6395 | 122.6624 | 122.5342 | 0.18768 | 0.059509 | 0.18768 | 0.032043 | 0.16479 | 0.082397 | 0.15106 | 0.15106 | 122.612 | 122.6257 | -0.17853 | -0.16479 | 122.493 | 122.5571 | 122.4564 | 122.5388
2310.0781 | 122.7814 | -122.5204 | 0.073242 | -0.018921 | 0.065719 | 0.016962 | 0.022471 | 0.0062144 | 0.00044856 | -0.0016513 | -0.0076599 | 0.021443 | 0.019916 | 0.015968 | 0.00033115 | 0.018598 | -0.0014931 | -0.050354 | 0.050354 | -0.036621 | -0.009155 | 0.16022 | 0.013733 | 0.050354 | 0.054932 | 0.045776 | -0.041199 | 0.073242 | 0.15106 | 0.064087 | 0.16937 | 122.4838 | -0.022888 | -0.082397 | 122.6807 | 122.5708 | 122.5342 | 0.086975 | 0.050354 | 122.4792 | -0.027466 | 0 | 122.6715 | 122.6898 | 122.5845 | 0.21057 | 0.10529 | 0.19684 | 0.027466 | 0.19226 | 0.11444 | 0.086975 | 0.086975 | 122.5708 | 122.5662 | -0.10986 | -0.11444 | 122.5113 | 122.5937 | 122.4701 | 122.5754
2311.8281 | 122.7859 | -122.5113 | 0.086975 | -0.0036622 | 0.06636 | 0.016534 | 0.023326 | -0.0027578 | 0.00044856 | -0.0020785 | -0.0015565 | 0.023152 | 0.019916 | 0.014473 | 0.0041763 | 0.017957 | -0.0025613 | -0.091553 | 0.091553 | -0.064087 | -0.068665 | 0.064087 | -0.07782 | -0.018311 | -0.004578 | 0.068665 | -0.059509 | 0.059509 | 0.11902 | 0.050354 | 0.17395 | 122.4472 | 0.004578 | -0.15564 | 122.5754 | 122.493 | 122.4335 | 0.045776 | -0.013733 | 122.4518 | -0.01831 | -0.027466 | 122.6303 | 122.6852 | 122.5616 | 0.23346 | 0.10986 | 0.12817 | -0.004578 | 0.17853 | 0.11902 | 0.15564 | 0.12817 | 122.6028 | 122.58 | -0.15106 | -0.14648 | 122.4426 | 122.5708 | 122.4197 | 122.5067
2313.5938 | 122.7402 | -122.5479 | 0.11444 | -0.0036622 | 0.067001 | 0.015466 | 0.022044 | -0.0012624 | 0.00044856 | -0.00058311 | 0.0014953 | 0.025716 | 0.018634 | 0.014259 | -0.0015915 | 0.019025 | -0.0034159 | -0.041199 | 0.091553 | -0.07782 | -0.050354 | 0.11902 | -0.018311 | -0.004578 | 0.009155 | 0.086975 | -0.059509 | 0.022888 | 0.082397 | -0.009155 | 0.12817 | 122.4701 | -0.022888 | -0.16479 | 122.6669 | 122.5433 | 122.5296 | 0.073242 | 0.059509 | 122.4884 | -0.027466 | -0.091553 | 122.6303 | 122.6761 | 122.5388 | 0.18768 | 0.050354 | 0.19684 | 0.027466 | 0.14191 | 0.082397 | 0.16937 | 0.14648 | 122.6395 | 122.6349 | -0.19226 | -0.17395 | 122.4976 | 122.5708 | 122.5067 | 122.5571
2315.2812 | 122.8409 | -122.525 | 0.086975 | -0.0036622 | 0.063583 | 0.01568 | 0.021189 | -0.004894 | -0.0012604 | -0.0025057 | 0.0014953 | 0.022298 | 0.019275 | 0.021095 | -0.0039413 | 0.016462 | -0.0023477 | -0.032043 | 0.036621 | -0.050354 | 0.041199 | 0.21973 | 0.086975 | 0.082397 | 0.09613 | 0.041199 | -0.027466 | 0.086975 | 0.19684 | 0.1236 | 0.19684 | 122.4747 | -0.050354 | -0.045776 | 122.7448 | 122.6074 | 122.612 | 0.13275 | 0.13733 | 122.4976 | -0.045776 | 0 | 122.7219 | 122.7219 | 122.6486 | 0.2243 | 0.15106 | 0.27008 | 0.091553 | 0.2243 | 0.11444 | 0.086975 | 0.068665 | 122.5616 | 122.5662 | -0.13733 | -0.11444 | 122.5662 | 122.612 | 122.493 | 122.6212
2317.0312 | 122.7219 | -122.5662 | 0.10529 | -0.0036622 | 0.067855 | 0.016748 | 0.022471 | 1.915e-05 | 0.00044856 | -0.0037875 | 0.0014953 | 0.024648 | 0.020343 | 0.012123 | 0.00075835 | 0.018384 | 0.0021383 | -0.086975 | 0.073242 | -0.073242 | -0.11444 | 0 | -0.10986 | -0.064087 | -0.086975 | 0.11902 | -0.07782 | -0.018311 | 0.036621 | -0.050354 | 0.10071 | 122.493 | -0.032044 | -0.21973 | 122.5662 | 122.5021 | 122.4564 | 0.009155 | -0.036621 | 122.4884 | 0.013733 | -0.1236 | 122.6028 | 122.6669 | 122.5159 | 0.17853 | 0.027466 | 0.073242 | -0.041199 | 0.11444 | 0.059509 | 0.14648 | 0.19684 | 122.6395 | 122.6852 | -0.17853 | -0.18311 | 122.4518 | 122.5479 | 122.4792 | 122.4792
2318.7812 | 122.7448 | -122.5388 | 0.10529 | 0.0039673 | 0.065505 | 0.013757 | 0.022898 | 0.0023692 | -0.0023284 | -0.0010105 | 0.0014953 | 0.024861 | 0.019703 | 0.019813 | -0.0015915 | 0.018171 | 0.00085667 | -0.068665 | 0.09613 | -0.082397 | -0.073242 | 0.064087 | -0.018311 | -0.013733 | -0.027466 | 0.082397 | -0.068665 | 0.013733 | 0.10071 | -0.004578 | 0.13275 | 122.4564 | -0.009156 | -0.17853 | 122.6028 | 122.525 | 122.5204 | 0.068664 | 0.064086 | 122.4701 | -0.022889 | -0.091553 | 122.6395 | 122.6715 | 122.5342 | 0.20142 | 0.064087 | 0.14648 | 0.009155 | 0.16937 | 0.082398 | 0.17853 | 0.15106 | 122.6349 | 122.6212 | -0.18768 | -0.17395 | 122.4655 | 122.5525 | 122.4701 | 122.5113
2320.4688 | 122.699 | -122.5433 | 0.12817 | 0.0039673 | 0.067642 | 0.01568 | 0.021403 | 0.0042918 | -0.002542 | -0.00058311 | 0.0014953 | 0.024434 | 0.019703 | 0.011482 | 0.00033115 | 0.018598 | -0.0032021 | -0.07782 | 0.07782 | -0.073242 | -0.091553 | 0.054932 | -0.07782 | -0.054932 | -0.068665 | 0.091553 | -0.068665 | -0.018311 | 0.041199 | -0.059509 | 0.07782 | 122.4701 | -0.050354 | -0.21973 | 122.5983 | 122.4884 | 122.4655 | 0.01831 | -0.004578 | 122.4747 | -0.036621 | -0.14649 | 122.5845 | 122.6212 | 122.4838 | 0.14649 | 0.009156 | 0.12817 | -0.018311 | 0.10986 | 0.050354 | 0.15106 | 0.16022 | 122.6212 | 122.6349 | -0.20142 | -0.19684 | 122.4518 | 122.525 | 122.4655 | 122.4747
2322.2031 | 122.7585 | -122.5388 | 0.10986 | 0.0039673 | 0.068069 | 0.016748 | 0.023753 | 0.0027964 | -0.0019012 | 0.0013395 | -0.0046081 | 0.022725 | 0.020984 | 0.011909 | 0.0013991 | 0.018171 | -0.0040567 | -0.10529 | 0.073242 | -0.07782 | -0.11444 | 0.022888 | -0.10071 | -0.050354 | -0.054932 | 0.086975 | -0.068665 | 0.018311 | 0.073242 | -0.009155 | 0.14191 | 122.4609 | -0.036621 | -0.2243 | 122.5616 | 122.4884 | 122.438 | 0.027466 | -0.022888 | 122.4701 | -0.022888 | -0.091552 | 122.612 | 122.6807 | 122.5296 | 0.21057 | 0.05951 | 0.10071 | -0.036621 | 0.14191 | 0.086976 | 0.15106 | 0.15564 | 122.612 | 122.6257 | -0.18768 | -0.17853 | 122.4243 | 122.5571 | 122.4335 | 122.4838
2323.9531 | 122.7951 | -122.5204 | 0.09613 | -0.0036622 | 0.064865 | 0.017389 | 0.019053 | 1.915e-05 | -0.0016876 | -0.0018649 | -0.0015565 | 0.022725 | 0.019275 | 0.018104 | 0.00075835 | 0.017103 | -0.0027749 | -0.027466 | 0.032043 | -0.045776 | 0.004578 | 0.17395 | 0.022888 | 0.054932 | 0.086975 | 0.050354 | -0.041199 | 0.07782 | 0.13733 | 0.068665 | 0.18768 | 122.4747 | -0.064087 | -0.091552 | 122.6944 | 122.5754 | 122.5433 | 0.10071 | 0.068664 | 122.4792 | -0.045776 | -0.01831 | 122.6578 | 122.7081 | 122.5891 | 0.22888 | 0.10986 | 0.21973 | 0.050354 | 0.17853 | 0.11902 | 0.077819 | 0.091553 | 122.5525 | 122.5708 | -0.14191 | -0.13733 | 122.525 | 122.5983 | 122.493 | 122.6074
2325.7188 | 122.8363 | -122.4976 | 0.09613 | -0.011291 | 0.064224 | 0.016534 | 0.02183 | 0.00044655 | -0.0010468 | 0.0011257 | -0.0015565 | 0.023152 | 0.020343 | 0.018745 | 0.00075835 | 0.01988 | -0.0023477 | -0.004578 | 0.045776 | -0.032043 | 0.027466 | 0.16479 | 0.022888 | 0.050354 | 0.10071 | 0.041199 | -0.032043 | 0.09613 | 0.16937 | 0.082397 | 0.20142 | 122.4655 | -0.050354 | -0.068664 | 122.6624 | 122.5479 | 122.5204 | 0.082397 | 0.054931 | 122.4655 | -0.054931 | 0 | 122.6669 | 122.699 | 122.58 | 0.23346 | 0.11444 | 0.19684 | 0.059509 | 0.20142 | 0.12817 | 0.077819 | 0.073242 | 122.5433 | 122.5388 | -0.12817 | -0.12817 | 122.525 | 122.5937 | 122.493 | 122.5983
2327.3906 | 122.8455 | -122.5067 | 0.10986 | -0.011291 | 0.064651 | 0.016321 | 0.018839 | -0.0016898 | -0.00083304 | 0.00027129 | -0.0046081 | 0.022725 | 0.018848 | 0.013191 | -0.0030869 | 0.017103 | -0.0014931 | -0.018311 | 0.045776 | -0.050354 | 0.027466 | 0.21057 | 0.064087 | 0.07782 | 0.11444 | 0.07782 | -0.045776 | 0.07782 | 0.21515 | 0.11444 | 0.19684 | 122.4564 | -0.064087 | -0.082397 | 122.7173 | 122.5845 | 122.5708 | 0.12817 | 0.11444 | 122.4609 | -0.032043 | -0.032043 | 122.7219 | 122.7036 | 122.6212 | 0.24261 | 0.16022 | 0.26093 | 0.07782 | 0.26093 | 0.1236 | 0.09613 | 0.1236 | 122.5525 | 122.5845 | -0.16022 | -0.15564 | 122.5342 | 122.5845 | 122.4884 | 122.6212
2329.0781 | 122.8226 | -122.5113 | 0.082397 | -0.011291 | 0.066787 | 0.014185 | 0.022257 | -0.0029714 | -0.0029694 | -0.0014377 | -0.0015565 | 0.02657 | 0.017994 | 0.010841 | 0.0022537 | 0.017957 | -0.0025613 | -0.054932 | 0.054932 | -0.059509 | 0 | 0.13733 | 0.004578 | 0.036621 | 0.064087 | 0.054932 | -0.032043 | 0.086975 | 0.16479 | 0.073242 | 0.19684 | 122.4518 | -0.027465 | -0.082397 | 122.6486 | 122.5479 | 122.5159 | 0.09613 | 0.064087 | 122.4792 | -0.027465 | 0.004578 | 122.6761 | 122.7081 | 122.5845 | 0.22888 | 0.10529 | 0.19684 | 0.059509 | 0.19684 | 0.11902 | 0.11444 | 0.086975 | 122.5662 | 122.5662 | -0.14191 | -0.11444 | 122.5113 | 122.5983 | 122.4564 | 122.5754
2330.8438 | 122.7722 | -122.5433 | 0.082397 | -0.0036622 | 0.067001 | 0.015894 | 0.023112 | 0.0034372 | -0.00061944 | -0.00079691 | -0.0015565 | 0.024861 | 0.019916 | 0.014259 | -0.00030965 | 0.018171 | -0.0027749 | -0.09613 | 0.068665 | -0.086975 | -0.10529 | 0.027466 | -0.10071 | -0.041199 | -0.045776 | 0.091553 | -0.068665 | 0.027466 | 0.073242 | -0.013733 | 0.13733 | 122.4564 | -0.013732 | -0.18768 | 122.5708 | 122.5021 | 122.4426 | 0.045776 | -0.013733 | 122.4747 | 0.009156 | -0.054931 | 122.6166 | 122.6807 | 122.5296 | 0.20599 | 0.054932 | 0.11444 | -0.018311 | 0.14191 | 0.096131 | 0.15564 | 0.16022 | 122.612 | 122.6349 | -0.16937 | -0.15106 | 122.438 | 122.5708 | 122.4472 | 122.4976
2332.5938 | 122.731 | -122.5571 | 0.11444 | -0.0036622 | 0.065719 | 0.016534 | 0.021617 | -0.0012624 | 0.00044856 | 0.0026211 | -0.0015565 | 0.025716 | 0.021412 | 0.014686 | 0.0016129 | 0.01753 | 0.00021567 | -0.10986 | 0.07782 | -0.086975 | -0.1236 | 0.022888 | -0.09613 | -0.050354 | -0.07782 | 0.086975 | -0.064087 | -0.022888 | 0.032043 | -0.036621 | 0.09613 | 122.4701 | -0.036621 | -0.23804 | 122.58 | 122.5067 | 122.4609 | 0.036621 | -0.009155 | 122.493 | -0.027466 | -0.13733 | 122.5891 | 122.6532 | 122.5204 | 0.16022 | 0.027466 | 0.10986 | -0.036621 | 0.09613 | 0.041199 | 0.16479 | 0.15106 | 122.6349 | 122.644 | -0.20142 | -0.17853 | 122.4335 | 122.5342 | 122.4472 | 122.4792
2334.3438 | 122.7356 | -122.5479 | 0.091553 | 0.011597 | 0.067001 | 0.016534 | 0.023112 | 0.0010874 | -0.0027556 | -0.0025057 | -0.0046081 | 0.025716 | 0.018421 | 0.013405 | 0.00075835 | 0.01753 | 0.00042947 | -0.091553 | 0.07782 | -0.082397 | -0.10529 | 0.022888 | -0.10071 | -0.068665 | -0.082397 | 0.09613 | -0.068665 | -0.027466 | 0.018311 | -0.073242 | 0.086975 | 122.4655 | -0.013733 | -0.19684 | 122.5708 | 122.4792 | 122.4472 | 0.013732 | -0.018311 | 122.4792 | 0.004577 | -0.11902 | 122.5662 | 122.6349 | 122.4747 | 0.15564 | -0.004577 | 0.10528 | -0.022889 | 0.086976 | 0.041199 | 0.16022 | 0.16479 | 122.6257 | 122.644 | -0.17395 | -0.16022 | 122.4426 | 122.5204 | 122.4564 | 122.4655
2336.1094 | 122.7448 | -122.5388 | 0.1236 | 0.0039673 | 0.065933 | 0.015039 | 0.020335 | 0.00066015 | -0.0019012 | -0.0044285 | -0.0015565 | 0.024648 | 0.020984 | 0.010414 | -0.0018051 | 0.018171 | -0.0053385 | -0.091553 | 0.082397 | -0.10071 | -0.10529 | 0.041199 | -0.073242 | -0.013733 | -0.07782 | 0.09613 | -0.082397 | -0.036621 | 0.054932 | -0.022888 | 0.10529 | 122.438 | -0.041199 | -0.22888 | 122.58 | 122.525 | 122.4655 | 0.086975 | 0.027466 | 122.4564 | -0.027466 | -0.16022 | 122.5937 | 122.644 | 122.5159 | 0.18768 | 0.059509 | 0.14191 | -0.004578 | 0.13733 | 0.045776 | 0.18311 | 0.17853 | 122.6212 | 122.6349 | -0.2243 | -0.20599 | 122.4335 | 122.5021 | 122.4472 | 122.4609
2337.7969 | 122.7356 | -122.5708 | 0.10529 | -0.011291 | 0.068283 | 0.015466 | 0.023326 | -0.00040805 | -0.0029694 | -0.0029331 | -0.0046081 | 0.024861 | 0.019916 | 0.010414 | -0.00095065 | 0.017743 | 0.00021567 | -0.10529 | 0.086975 | -0.082397 | -0.1236 | 0.032043 | -0.09613 | -0.050354 | -0.07782 | 0.091553 | -0.059509 | -0.013733 | 0.045776 | -0.041199 | 0.11444 | 122.4884 | -0.018311 | -0.22888 | 122.6028 | 122.5204 | 122.4747 | 0.032043 | -0.013733 | 122.5113 | -0.013733 | -0.11902 | 122.6166 | 122.6852 | 122.5296 | 0.17395 | 0.01831 | 0.11444 | -0.041199 | 0.10528 | 0.045776 | 0.16937 | 0.15106 | 122.6578 | 122.6624 | -0.18768 | -0.16479 | 122.4472 | 122.5571 | 122.4655 | 122.493
2339.5469 | 122.85 | -122.5388 | 0.082397 | -0.0036622 | 0.062515 | 0.01568 | 0.018839 | -0.00019445 | -0.0027556 | -0.0042147 | -0.0046081 | 0.02123 | 0.017139 | 0.019386 | -0.00095065 | 0.017316 | 0.0023521 | -0.07782 | 0.064087 | -0.059509 | -0.009155 | 0.15106 | 0.041199 | 0.073242 | 0.050354 | 0.041199 | -0.050354 | 0.086975 | 0.1831 | 0.10071 | 0.17395 | 122.4792 | -0.01831 | -0.091552 | 122.6898 | 122.612 | 122.58 | 0.13275 | 0.10071 | 122.4884 | -0.041198 | 0.004578 | 122.7219 | 122.7127 | 122.6395 | 0.2243 | 0.15106 | 0.21057 | 0.050354 | 0.23346 | 0.13733 | 0.1236 | 0.091553 | 122.6028 | 122.58 | -0.14191 | -0.13275 | 122.5296 | 122.6257 | 122.4609 | 122.5891
2341.2969 | 122.7448 | -122.5616 | 0.086975 | -0.011291 | 0.065292 | 0.015466 | 0.023112 | 0.004719 | -0.004892 | -0.00079691 | 0.0014953 | 0.024221 | 0.019489 | 0.010628 | -0.00095065 | 0.018384 | -0.0049111 | -0.09613 | 0.082397 | -0.07782 | -0.12817 | 0.013733 | -0.10071 | -0.045776 | -0.068665 | 0.091553 | -0.073242 | -0.009155 | 0.041199 | -0.041199 | 0.09613 | 122.4838 | -0.004578 | -0.21515 | 122.5754 | 122.5159 | 122.4609 | 0.032044 | -0.022888 | 122.4884 | 0.004578 | -0.09613 | 122.6028 | 122.6578 | 122.5204 | 0.16937 | 0.032043 | 0.091553 | -0.050354 | 0.11444 | 0.064087 | 0.16022 | 0.16479 | 122.644 | 122.6532 | -0.16479 | -0.16022 | 122.4335 | 122.5525 | 122.4655 | 122.493
2343.0469 | 122.7814 | -122.5571 | 0.1236 | 0.0039673 | 0.066787 | 0.014825 | 0.021617 | -0.0012624 | -0.0029694 | -0.0020785 | 0.0014953 | 0.024221 | 0.016925 | 0.013405 | -0.0024461 | 0.017316 | -0.0021341 | -0.068665 | 0.082397 | -0.068665 | -0.027466 | 0.10071 | -0.018311 | 0.004578 | -0.018311 | 0.086975 | -0.073242 | 0.041199 | 0.10529 | 0.018311 | 0.13733 | 122.4884 | -0.041199 | -0.15106 | 122.6578 | 122.5616 | 122.5388 | 0.073243 | 0.050354 | 122.4838 | -0.036621 | -0.082397 | 122.6624 | 122.6944 | 122.5754 | 0.21057 | 0.091553 | 0.16937 | 0.041199 | 0.17853 | 0.11444 | 0.15106 | 0.16022 | 122.6395 | 122.644 | -0.19226 | -0.19684 | 122.5296 | 122.5983 | 122.4884 | 122.5388
2344.7344 | 122.8455 | -122.5113 | 0.082397 | -0.011291 | 0.064865 | 0.017816 | 0.022471 | 0.0010874 | 2.1362e-05 | 0.0011257 | -0.0015565 | 0.024861 | 0.020557 | 0.023872 | 0.0043899 | 0.016675 | -0.00063873 | -0.013733 | 0.041199 | -0.036621 | 0.027466 | 0.1831 | 0.013733 | 0.059509 | 0.086975 | 0.068665 | -0.036621 | 0.091553 | 0.1831 | 0.09613 | 0.19226 | 122.4747 | -0.041198 | -0.054931 | 122.6944 | 122.5708 | 122.525 | 0.09613 | 0.050354 | 122.4747 | -0.013732 | 0.009156 | 122.6944 | 122.7036 | 122.6074 | 0.22888 | 0.13275 | 0.21973 | 0.064087 | 0.21973 | 0.12817 | 0.07782 | 0.10529 | 122.5525 | 122.58 | -0.11902 | -0.11902 | 122.5388 | 122.6028 | 122.4976 | 122.5983
2346.5 | 122.7127 | -122.5891 | 0.11902 | 0.0039673 | 0.066146 | 0.014398 | 0.019267 | -0.002117 | -0.00596 | -0.0035739 | -0.0015565 | 0.025075 | 0.018421 | 0.0102 | -0.0056503 | 0.01518 | -0.0017069 | -0.10986 | 0.045776 | -0.086975 | -0.10986 | 0.045776 | -0.068665 | -0.036621 | -0.073242 | 0.091553 | -0.07782 | -0.041199 | 0.045776 | -0.027466 | 0.086975 | 122.5021 | -0.073243 | -0.22888 | 122.6349 | 122.5525 | 122.5204 | 0.050354 | 0.01831 | 122.5113 | -0.027466 | -0.16022 | 122.6349 | 122.6761 | 122.5616 | 0.16479 | 0.050354 | 0.13275 | -0.022888 | 0.1236 | 0.036621 | 0.13275 | 0.16937 | 122.6349 | 122.6807 | -0.20599 | -0.19684 | 122.4792 | 122.5479 | 122.4792 | 122.5159
2348.1719 | 122.7173 | -122.58 | 0.10529 | 0.0039673 | 0.066574 | 0.016321 | 0.022685 | -0.00083525 | -0.001474 | -0.00015591 | 0.0045471 | 0.024221 | 0.019489 | 0.013191 | -0.00073705 | 0.019025 | -0.0021341 | -0.086975 | 0.064087 | -0.091553 | -0.091553 | 0.027466 | -0.10071 | -0.073242 | -0.10529 | 0.07782 | -0.082397 | -0.036621 | 0.018311 | -0.068665 | 0.091553 | 122.4884 | -0.041199 | -0.19684 | 122.6074 | 122.5067 | 122.4792 | 0.018311 | -0.009155 | 122.4976 | -0.027466 | -0.14191 | 122.5983 | 122.6715 | 122.5113 | 0.17395 | 0.013732 | 0.11902 | 0 | 0.10071 | 0.045776 | 0.15564 | 0.16022 | 122.644 | 122.6578 | -0.19684 | -0.18768 | 122.4884 | 122.5433 | 122.493 | 122.4747
2349.9062 | 122.8592 | -122.5021 | 0.064087 | -0.0036622 | 0.065719 | 0.017389 | 0.01948 | 0.0025828 | -0.0016876 | -0.0012241 | -0.0046081 | 0.02358 | 0.02013 | 0.019173 | 0.0039627 | 0.019025 | -0.0021341 | -0.032043 | 0.054932 | -0.041199 | -0.004578 | 0.16022 | 0.018311 | 0.045776 | 0.073242 | 0.059509 | -0.041199 | 0.09613 | 0.17395 | 0.091553 | 0.20142 | 122.4609 | -0.009155 | -0.068665 | 122.6624 | 122.5479 | 122.5204 | 0.086975 | 0.05951 | 122.4609 | -0.004578 | 0.032043 | 122.6761 | 122.7036 | 122.5937 | 0.24262 | 0.13275 | 0.20142 | 0.036621 | 0.21515 | 0.13733 | 0.096131 | 0.10071 | 122.5571 | 122.5616 | -0.10529 | -0.10529 | 122.4976 | 122.5983 | 122.4701 | 122.5754
2351.5938 | 122.818 | -122.525 | 0.082397 | -0.0036622 | 0.068283 | 0.016534 | 0.022898 | 0.0010874 | -0.0012604 | -0.0020785 | 0.0014953 | 0.024221 | 0.019916 | 0.018959 | 0.00054475 | 0.019025 | -0.0017069 | -0.036621 | 0.045776 | -0.027466 | 0 | 0.17853 | 0.013733 | 0.045776 | 0.073242 | 0.050354 | -0.041199 | 0.064087 | 0.16022 | 0.059509 | 0.17853 | 122.4976 | -0.036621 | -0.082397 | 122.7036 | 122.5708 | 122.5388 | 0.073242 | 0.041199 | 122.4838 | -0.032043 | -0.01831 | 122.6852 | 122.7036 | 122.5845 | 0.21973 | 0.10071 | 0.20599 | 0.027466 | 0.20142 | 0.10529 | 0.073242 | 0.091553 | 122.5708 | 122.5754 | -0.10986 | -0.1236 | 122.525 | 122.5891 | 122.4884 | 122.5983
2353.3281 | 122.8592 | -122.5479 | 0.054932 | -0.018921 | 0.063583 | 0.014825 | 0.018839 | -0.001476 | -0.0010468 | 0.00069849 | -0.0046081 | 0.022725 | 0.019703 | 0.016182 | -0.0045823 | 0.018171 | 0.00042947 | -0.032043 | 0.050354 | -0.045776 | 0.018311 | 0.1831 | 0.054932 | 0.10071 | 0.10071 | 0.041199 | -0.064087 | 0.09613 | 0.20599 | 0.11444 | 0.19684 | 122.5021 | -0.004578 | -0.036621 | 122.731 | 122.6486 | 122.6028 | 0.14648 | 0.10071 | 122.4838 | -0.013733 | 0.041198 | 122.7539 | 122.7448 | 122.6624 | 0.26093 | 0.17853 | 0.22888 | 0.064087 | 0.27008 | 0.16022 | 0.09613 | 0.10529 | 122.5983 | 122.5891 | -0.10071 | -0.11902 | 122.5662 | 122.644 | 122.5159 | 122.6486
2355.0625 | 122.7448 | -122.5616 | 0.11902 | -0.0036622 | 0.064865 | 0.015253 | 0.022257 | -0.0036124 | -0.001474 | -0.0033603 | -0.0015565 | 0.023152 | 0.018848 | 0.014473 | -0.0050095 | 0.015607 | -0.0046975 | -0.041199 | 0.045776 | -0.045776 | -0.009155 | 0.1236 | 0.022888 | 0.027466 | 0.004578 | 0.059509 | -0.054932 | 0.004578 | 0.091553 | 0 | 0.11444 | 122.5159 | -0.073243 | -0.12817 | 122.6852 | 122.5891 | 122.5845 | 0.073242 | 0.068664 | 122.5067 | -0.05951 | -0.11444 | 122.6532 | 122.6761 | 122.5616 | 0.16937 | 0.054932 | 0.16937 | 0.036621 | 0.14649 | 0.05951 | 0.091552 | 0.11444 | 122.6074 | 122.6212 | -0.16479 | -0.17395 | 122.5525 | 122.5662 | 122.5204 | 122.5662
2356.8125 | 122.8271 | -122.5479 | 0.073242 | -0.011291 | 0.06401 | 0.017389 | 0.023966 | -0.001476 | -0.0044646 | -0.00079691 | -0.0076599 | 0.025075 | 0.020343 | 0.016395 | 0.0028945 | 0.019666 | -0.00063873 | -0.054932 | 0.064087 | -0.064087 | -0.009155 | 0.14191 | -0.004578 | 0.032043 | 0.07782 | 0.054932 | -0.050354 | 0.09613 | 0.15564 | 0.064087 | 0.21973 | 122.4838 | -0.009155 | -0.082397 | 122.6898 | 122.58 | 122.5433 | 0.09613 | 0.059509 | 122.4976 | -0.01831 | 0.022888 | 122.7036 | 122.7676 | 122.612 | 0.27008 | 0.11444 | 0.20599 | 0.054932 | 0.20599 | 0.14648 | 0.12817 | 0.10529 | 122.612 | 122.6028 | -0.13733 | -0.1236 | 122.5388 | 122.644 | 122.493 | 122.6257
2358.5 | 122.8043 | -122.5433 | 0.09613 | -0.011291 | 0.063583 | 0.016748 | 0.019908 | 0.0015146 | -0.002542 | -0.0012241 | 0.0014953 | 0.025075 | 0.019062 | 0.016395 | -0.00030965 | 0.017103 | -0.0034159 | -0.050354 | 0.036621 | -0.054932 | -0.022888 | 0.15106 | -0.004578 | 0.027466 | 0.041199 | 0.068665 | -0.054932 | 0.036621 | 0.1236 | 0.045776 | 0.14648 | 122.4884 | -0.059509 | -0.11902 | 122.6944 | 122.5708 | 122.5388 | 0.082398 | 0.050354 | 122.4884 | -0.027465 | -0.059509 | 122.6669 | 122.6898 | 122.5891 | 0.20142 | 0.10071 | 0.20599 | 0.032044 | 0.17853 | 0.091553 | 0.091553 | 0.1236 | 122.58 | 122.612 | -0.15106 | -0.15106 | 122.5204 | 122.58 | 122.493 | 122.5845
2360.25 | 122.7402 | -122.5571 | 0.11444 | -0.011291 | 0.065292 | 0.017603 | 0.022257 | 0.0023692 | -0.0021148 | 5.7688e-05 | -0.0015565 | 0.025075 | 0.018421 | 0.018745 | 0.0018265 | 0.018812 | -0.0021341 | -0.086975 | 0.086975 | -0.07782 | -0.10986 | 0.027466 | -0.11902 | -0.054932 | -0.068665 | 0.09613 | -0.064087 | -0.022888 | 0.032043 | -0.045776 | 0.091553 | 122.4792 | -0.027466 | -0.2243 | 122.5845 | 122.5021 | 122.438 | 0.022888 | -0.041199 | 122.493 | -0.018311 | -0.13733 | 122.5891 | 122.6486 | 122.5113 | 0.15564 | 0.018311 | 0.10529 | -0.032043 | 0.09613 | 0.041199 | 0.16479 | 0.16022 | 122.644 | 122.6532 | -0.19226 | -0.17853 | 122.4472 | 122.5342 | 122.4701 | 122.4884
2362 | 122.7814 | -122.5525 | 0.10529 | -0.011291 | 0.064865 | 0.016534 | 0.023539 | 0.0017282 | -0.0010468 | 0.00027129 | -0.0015565 | 0.026784 | 0.020557 | 0.019386 | -0.0022325 | 0.015394 | -0.0023477 | -0.064087 | 0.068665 | -0.07782 | -0.027466 | 0.10529 | -0.018311 | 0.009155 | 0.018311 | 0.082397 | -0.091553 | 0.022888 | 0.10986 | 0.004578 | 0.13275 | 122.4747 | -0.036621 | -0.13275 | 122.6578 | 122.5616 | 122.5342 | 0.086975 | 0.059509 | 122.4609 | -0.022889 | -0.082398 | 122.6624 | 122.6852 | 122.5571 | 0.2243 | 0.096131 | 0.18311 | 0.050354 | 0.20142 | 0.11444 | 0.14649 | 0.17395 | 122.6212 | 122.6349 | -0.18311 | -0.19684 | 122.525 | 122.5754 | 122.4884 | 122.5708
2363.75 | 122.7356 | -122.5891 | 0.11444 | -0.011291 | 0.067642 | 0.017389 | 0.023753 | -0.00040805 | -0.0027556 | 0.0019803 | -0.0015565 | 0.025716 | 0.020343 | 0.020027 | -0.0018051 | 0.017957 | 0.0019247 | -0.064087 | 0.068665 | -0.07782 | -0.07782 | 0.059509 | -0.068665 | -0.050354 | -0.064087 | 0.09613 | -0.045776 | -0.022888 | 0.027466 | -0.050354 | 0.073242 | 122.5113 | -0.045776 | -0.19226 | 122.6486 | 122.5388 | 122.5204 | 0.027466 | 0.009155 | 122.5433 | -0.018311 | -0.13733 | 122.6166 | 122.6624 | 122.5388 | 0.11902 | -0.004578 | 0.13733 | 0 | 0.073242 | 0.022888 | 0.14649 | 0.14191 | 122.6578 | 122.6852 | -0.19226 | -0.16022 | 122.5113 | 122.5662 | 122.525 | 122.525
2365.4219 | 122.8134 | -122.5342 | 0.086975 | 0.011597 | 0.066146 | 0.017816 | 0.020762 | 1.915e-05 | -0.00019224 | 0.0011257 | -0.0015565 | 0.022084 | 0.019489 | 0.017464 | 0.00054475 | 0.019452 | -0.0040567 | -0.032043 | 0.027466 | -0.045776 | 0.013733 | 0.18768 | 0.018311 | 0.050354 | 0.082397 | 0.045776 | -0.036621 | 0.082397 | 0.16479 | 0.082397 | 0.16937 | 122.4884 | -0.059509 | -0.073242 | 122.7219 | 122.5845 | 122.5525 | 0.09613 | 0.064087 | 122.4976 | -0.041199 | -0.004578 | 122.699 | 122.7036 | 122.6166 | 0.20599 | 0.11902 | 0.23346 | 0.059509 | 0.20142 | 0.11902 | 0.073242 | 0.082397 | 122.5616 | 122.58 | -0.13275 | -0.1236 | 122.5479 | 122.6166 | 122.5021 | 122.6166
2367.1719 | 122.7402 | -122.5845 | 0.1236 | -0.0036622 | 0.067855 | 0.014825 | 0.020762 | -0.0033986 | -0.0029694 | 5.7688e-05 | 0.0014953 | 0.025502 | 0.018421 | 0.015114 | -0.0058639 | 0.017103 | 0.00085667 | -0.11444 | 0.068665 | -0.091553 | -0.10529 | 0.054932 | -0.050354 | -0.027466 | -0.073242 | 0.10529 | -0.086975 | -0.045776 | 0.054932 | -0.032043 | 0.07782 | 122.493 | -0.054931 | -0.22888 | 122.6395 | 122.5571 | 122.5342 | 0.064087 | 0.041199 | 122.4976 | -0.01831 | -0.16937 | 122.6395 | 122.6624 | 122.5525 | 0.16479 | 0.054932 | 0.14649 | -0.013733 | 0.14191 | 0.041199 | 0.16022 | 0.19226 | 122.6532 | 122.6898 | -0.21515 | -0.21057 | 122.4792 | 122.5388 | 122.4701 | 122.5113
2368.8594 | 122.8638 | -122.5616 | 0.09613 | -0.018921 | 0.064224 | 0.017175 | 0.019694 | -0.003826 | -0.003183 | 0.00069849 | -0.0015565 | 0.020375 | 0.017139 | 0.020668 | -0.0028733 | 0.016034 | -0.0051247 | -0.041199 | 0.045776 | -0.041199 | 0.027466 | 0.21057 | 0.082397 | 0.091553 | 0.091553 | 0.059509 | -0.045776 | 0.091553 | 0.19226 | 0.11444 | 0.20142 | 122.5204 | -0.050354 | -0.068664 | 122.7722 | 122.6532 | 122.644 | 0.13275 | 0.1236 | 122.5159 | -0.036621 | -0.004577 | 122.7539 | 122.7631 | 122.6761 | 0.24719 | 0.16022 | 0.25177 | 0.068665 | 0.23804 | 0.13733 | 0.086975 | 0.10528 | 122.6074 | 122.6212 | -0.13733 | -0.14191 | 122.5891 | 122.6532 | 122.5204 | 122.6532
2370.6094 | 122.731 | -122.5571 | 0.10529 | -0.0036622 | 0.065078 | 0.015894 | 0.023539 | -0.0010488 | 2.1362e-05 | -0.0016513 | -0.0015565 | 0.024648 | 0.02013 | 0.019813 | 0.0031081 | 0.017957 | -0.0029885 | -0.11902 | 0.09613 | -0.086975 | -0.13733 | -0.027466 | -0.10986 | -0.059509 | -0.10071 | 0.086975 | -0.073242 | -0.027466 | 0.022888 | -0.073242 | 0.09613 | 122.4701 | -0.009156 | -0.24262 | 122.5296 | 122.4976 | 122.4472 | 0.027466 | -0.022888 | 122.4838 | -0.018311 | -0.13275 | 122.58 | 122.6532 | 122.4838 | 0.16937 | 0 | 0.059509 | -0.050354 | 0.09613 | 0.045776 | 0.1831 | 0.16022 | 122.6532 | 122.644 | -0.19226 | -0.17853 | 122.4197 | 122.5296 | 122.438 | 122.4564
2372.2969 | 122.7768 | -122.5708 | 0.11444 | -0.0036622 | 0.065505 | 0.01568 | 0.023112 | -0.0027578 | -0.00061944 | 0.00048489 | -0.0015565 | 0.023152 | 0.017994 | 0.011696 | -0.0011643 | 0.018812 | -0.00021153 | -0.073242 | 0.07782 | -0.07782 | -0.054932 | 0.064087 | -0.022888 | -0.009155 | -0.022888 | 0.10071 | -0.073242 | 0.022888 | 0.10529 | -0.009155 | 0.1236 | 122.493 | -0.036621 | -0.16937 | 122.6349 | 122.5616 | 122.5479 | 0.068665 | 0.054932 | 122.4976 | -0.013733 | -0.091553 | 122.6761 | 122.6944 | 122.5616 | 0.19684 | 0.064087 | 0.14191 | 0.022888 | 0.17853 | 0.09613 | 0.15564 | 0.17395 | 122.6486 | 122.6715 | -0.19226 | -0.18768 | 122.5159 | 122.5937 | 122.4976 | 122.5479
2373.9688 | 122.7448 | -122.5845 | 0.1236 | -0.0036622 | 0.067642 | 0.013971 | 0.02418 | -0.00040805 | -0.001474 | -0.0022921 | -0.0046081 | 0.024648 | 0.019916 | 0.020241 | 0.0018265 | 0.019666 | -0.00021153 | -0.11902 | 0.10986 | -0.059509 | -0.11444 | 0.013733 | -0.11444 | -0.073242 | -0.082397 | 0.086975 | -0.07782 | -0.018311 | 0.027466 | -0.054932 | 0.086975 | 122.525 | -0.013733 | -0.23804 | 122.5983 | 122.5113 | 122.4701 | -0.013733 | -0.054932 | 122.5067 | -0.036621 | -0.14191 | 122.612 | 122.6715 | 122.5296 | 0.16479 | 0.022888 | 0.073242 | -0.054932 | 0.10529 | 0.059509 | 0.16937 | 0.16479 | 122.6944 | 122.6715 | -0.1831 | -0.20142 | 122.4701 | 122.5662 | 122.4655 | 122.5021
2375.6562 | 122.8683 | -122.5342 | 0.082397 | -0.011291 | 0.065078 | 0.016107 | 0.021189 | -0.00040805 | -0.0019012 | 0.0013395 | 0.0014953 | 0.02358 | 0.018421 | 0.020454 | 0.0024673 | 0.018812 | -0.00085233 | -0.032043 | 0.027466 | -0.050354 | 0.018311 | 0.17853 | 0.022888 | 0.045776 | 0.082397 | 0.054932 | -0.036621 | 0.10071 | 0.18768 | 0.09613 | 0.20142 | 122.4838 | -0.054931 | -0.064086 | 122.7127 | 122.58 | 122.5571 | 0.09613 | 0.073242 | 122.4976 | -0.027465 | 0.018311 | 122.7219 | 122.7356 | 122.6303 | 0.23804 | 0.13275 | 0.22888 | 0.068665 | 0.2243 | 0.13733 | 0.07782 | 0.091553 | 122.5616 | 122.5891 | -0.13275 | -0.11902 | 122.5525 | 122.6349 | 122.5021 | 122.6166
2377.3906 | 122.8546 | -122.5433 | 0.091553 | -0.0036622 | 0.066787 | 0.015466 | 0.020121 | -0.003185 | -0.003183 | 0.0013395 | -0.0046081 | 0.022298 | 0.019703 | 0.020454 | -0.0026597 | 0.017103 | 2.068e-06 | -0.041199 | 0.027466 | -0.059509 | 0.036621 | 0.20142 | 0.068665 | 0.086975 | 0.086975 | 0.045776 | -0.050354 | 0.091553 | 0.20142 | 0.11902 | 0.19226 | 122.4838 | -0.064087 | -0.054932 | 122.7448 | 122.6303 | 122.612 | 0.14648 | 0.12817 | 122.493 | -0.045777 | 0 | 122.7448 | 122.7356 | 122.6624 | 0.24261 | 0.16937 | 0.26093 | 0.09613 | 0.25177 | 0.14191 | 0.086975 | 0.09613 | 122.5708 | 122.5891 | -0.15106 | -0.14191 | 122.58 | 122.6349 | 122.5021 | 122.6303
2379.0781 | 122.7219 | -122.5845 | 0.1236 | -0.0036622 | 0.067642 | 0.014825 | 0.025675 | -0.00083525 | -0.0016876 | 0.0032621 | -0.0046081 | 0.025929 | 0.018207 | 0.013832 | 0.0011855 | 0.016034 | -0.0036295 | -0.086975 | 0.086975 | -0.07782 | -0.10986 | 0.004578 | -0.10529 | -0.068665 | -0.11444 | 0.086975 | -0.07782 | -0.036621 | 0.004578 | -0.082397 | 0.07782 | 122.5067 | -0.036621 | -0.23346 | 122.5891 | 122.5159 | 122.4792 | 0.009155 | -0.027466 | 122.5067 | -0.036621 | -0.16022 | 122.5891 | 122.6624 | 122.5021 | 0.15564 | -0.004577 | 0.082398 | -0.032043 | 0.082398 | 0.041199 | 0.16479 | 0.16479 | 122.6715 | 122.6715 | -0.20142 | -0.20142 | 122.4747 | 122.5479 | 122.4976 | 122.4701
2380.8281 | 122.8271 | -122.5616 | 0.07782 | -0.0036622 | 0.065292 | 0.015466 | 0.021189 | -0.003185 | -0.0021148 | -0.00015591 | -0.0046081 | 0.023366 | 0.018421 | 0.015327 | -0.00073705 | 0.017743 | 0.0012839 | -0.036621 | 0.045776 | -0.041199 | 0.018311 | 0.1831 | 0.004578 | 0.059509 | 0.064087 | 0.041199 | -0.064087 | 0.073242 | 0.15106 | 0.064087 | 0.16479 | 122.5204 | -0.032044 | -0.059509 | 122.7448 | 122.6212 | 122.5662 | 0.10071 | 0.045777 | 122.4976 | -0.036621 | -0.004578 | 122.7127 | 122.7264 | 122.6257 | 0.22888 | 0.12817 | 0.2243 | 0.05951 | 0.21515 | 0.13733 | 0.086975 | 0.10529 | 122.6074 | 122.6028 | -0.11902 | -0.14191 | 122.58 | 122.6349 | 122.525 | 122.6257
2382.5781 | 122.7493 | -122.58 | 0.13275 | -0.018921 | 0.068069 | 0.014825 | 0.02183 | -0.00040805 | -0.0023284 | 0.0011257 | -0.0046081 | 0.024221 | 0.018207 | 0.015327 | -0.0067185 | 0.017103 | -0.00063873 | -0.064087 | 0.041199 | -0.059509 | -0.068665 | 0.068665 | -0.041199 | -0.004578 | -0.050354 | 0.10071 | -0.07782 | -0.032043 | 0.050354 | -0.022888 | 0.086975 | 122.5204 | -0.091552 | -0.20142 | 122.6486 | 122.5754 | 122.5388 | 0.054931 | 0.01831 | 122.5021 | -0.032043 | -0.16479 | 122.6303 | 122.6669 | 122.5571 | 0.16479 | 0.054932 | 0.12817 | -0.009156 | 0.12817 | 0.045777 | 0.10071 | 0.17853 | 122.6212 | 122.6807 | -0.19226 | -0.21057 | 122.5113 | 122.5479 | 122.5159 | 122.5296
2384.3281 | 122.8683 | -122.5433 | 0.086975 | -0.018921 | 0.065719 | 0.016748 | 0.023539 | 0.00044655 | -0.0019012 | 0.0013395 | -0.0046081 | 0.024221 | 0.019275 | 0.021522 | 0.0035355 | 0.020307 | -0.0025613 | -0.041199 | 0.068665 | -0.050354 | 0.004578 | 0.14191 | 0.009155 | 0.050354 | 0.07782 | 0.050354 | -0.045776 | 0.10529 | 0.16479 | 0.073242 | 0.2243 | 122.493 | -0.01831 | -0.082397 | 122.6852 | 122.5937 | 122.5525 | 0.10071 | 0.059509 | 122.4976 | -0.036621 | 0.018311 | 122.7081 | 122.7676 | 122.6166 | 0.27008 | 0.11902 | 0.19226 | 0.054932 | 0.21057 | 0.15106 | 0.11902 | 0.09613 | 122.612 | 122.5937 | -0.13733 | -0.13275 | 122.5479 | 122.6486 | 122.5021 | 122.6212
2386.0781 | 122.8134 | -122.5845 | 0.09613 | -0.011291 | 0.067428 | 0.015894 | 0.020976 | -0.0059622 | -0.0027556 | -0.00079691 | -0.0015565 | 0.021657 | 0.016712 | 0.0067825 | -9.605e-05 | 0.017103 | -0.00085233 | -0.032043 | 0.022888 | -0.032043 | 0.013733 | 0.17395 | 0.050354 | 0.07782 | 0.036621 | 0.068665 | -0.054932 | 0.041199 | 0.15106 | 0.059509 | 0.15106 | 122.5525 | -0.073242 | -0.082397 | 122.7585 | 122.6624 | 122.6349 | 0.10986 | 0.082397 | 122.5296 | -0.027465 | -0.054931 | 122.7356 | 122.7356 | 122.644 | 0.20599 | 0.11444 | 0.20599 | 0.045776 | 0.20599 | 0.096131 | 0.054931 | 0.1236 | 122.6074 | 122.6532 | -0.12817 | -0.15106 | 122.5983 | 122.6257 | 122.5525 | 122.6212
2387.8125 | 122.7402 | -122.6074 | 0.11902 | -0.011291 | 0.06401 | 0.014825 | 0.021189 | -0.00062165 | -0.0040374 | -0.0016513 | -0.0015565 | 0.024434 | 0.017566 | 0.022377 | -0.0037277 | 0.016889 | -0.0021341 | -0.10071 | 0.091553 | -0.09613 | -0.10529 | 0.013733 | -0.054932 | -0.036621 | -0.10529 | 0.073242 | -0.09613 | -0.036621 | 0.041199 | -0.041199 | 0.091553 | 122.5113 | -0.027466 | -0.22431 | 122.6212 | 122.5708 | 122.5525 | 0.059509 | 0.041198 | 122.5113 | -0.045777 | -0.15564 | 122.6486 | 122.699 | 122.5662 | 0.18768 | 0.054931 | 0.10986 | -0.009156 | 0.13733 | 0.059509 | 0.18768 | 0.16937 | 122.699 | 122.6807 | -0.21515 | -0.21515 | 122.5021 | 122.5708 | 122.5067 | 122.5021
2389.4844 | 122.7448 | -122.5937 | 0.091553 | -0.018921 | 0.065078 | 0.016748 | 0.025035 | -0.0053214 | -0.0023284 | -0.0018649 | 0.0014953 | 0.023793 | 0.017566 | 0.011055 | -0.0018051 | 0.017743 | 0.0036337 | -0.10529 | 0.082397 | -0.07782 | -0.11902 | 0.018311 | -0.09613 | -0.041199 | -0.07782 | 0.091553 | -0.086975 | -0.004578 | 0.054932 | -0.041199 | 0.091553 | 122.5159 | -0.009156 | -0.21057 | 122.612 | 122.5525 | 122.4976 | 0.036621 | -0.01831 | 122.5067 | 0 | -0.096131 | 122.6486 | 122.6852 | 122.5525 | 0.17853 | 0.045776 | 0.096131 | -0.041199 | 0.14191 | 0.082397 | 0.16022 | 0.17853 | 122.6761 | 122.6852 | -0.16937 | -0.17853 | 122.4747 | 122.5891 | 122.4884 | 122.5159
2391.2344 | 122.8683 | -122.5388 | 0.086975 | -0.0036622 | 0.064224 | 0.014612 | 0.02183 | -0.0012624 | -0.0010468 | 0.0017667 | -0.0046081 | 0.023366 | 0.019916 | 0.012764 | 0.0031081 | 0.019239 | -0.00021153 | -0.054932 | 0.045776 | -0.064087 | -0.013733 | 0.1236 | -0.036621 | 0.036621 | 0.064087 | 0.059509 | -0.041199 | 0.10529 | 0.17395 | 0.068665 | 0.19226 | 122.4747 | -0.041199 | -0.10071 | 122.6624 | 122.5754 | 122.5021 | 0.10071 | 0.027466 | 122.4976 | -0.027466 | 0.018311 | 122.7127 | 122.731 | 122.6074 | 0.23346 | 0.10986 | 0.18768 | 0.050354 | 0.21515 | 0.14649 | 0.10986 | 0.10071 | 122.5845 | 122.5983 | -0.15106 | -0.12817 | 122.525 | 122.644 | 122.4838 | 122.6028
2392.9219 | 122.7356 | -122.5845 | 0.11444 | -0.011291 | 0.066574 | 0.015466 | 0.022898 | -0.00083525 | -0.002542 | -0.00036951 | -0.0015565 | 0.026143 | 0.022693 | 0.014473 | -0.00095065 | 0.018171 | -0.0019205 | -0.09613 | 0.09613 | -0.082397 | -0.10986 | 0.004578 | -0.11902 | -0.068665 | -0.082397 | 0.091553 | -0.064087 | -0.027466 | 0.027466 | -0.045776 | 0.10529 | 122.5021 | -0.018311 | -0.2243 | 122.5891 | 122.5159 | 122.4655 | 0.013732 | -0.036622 | 122.5204 | -0.022888 | -0.14191 | 122.612 | 122.6898 | 122.5388 | 0.16937 | 0.018311 | 0.086975 | -0.027466 | 0.091553 | 0.036621 | 0.17853 | 0.15564 | 122.6807 | 122.6761 | -0.19684 | -0.17853 | 122.4747 | 122.5571 | 122.4884 | 122.5021
2394.6719 | 122.8821 | -122.5525 | 0.086975 | -0.0036622 | 0.063796 | 0.014612 | 0.019908 | -0.003185 | -0.0040374 | -0.0012241 | -0.0046081 | 0.021443 | 0.019489 | 0.027931 | -0.0028733 | 0.018812 | -0.0027749 | -0.041199 | 0.041199 | -0.045776 | 0.013733 | 0.20142 | 0.073242 | 0.09613 | 0.10529 | 0.068665 | -0.022888 | 0.10071 | 0.2243 | 0.15106 | 0.21515 | 122.5067 | -0.045776 | -0.073242 | 122.7539 | 122.6486 | 122.6257 | 0.14191 | 0.11902 | 122.5296 | -0.01831 | 0.013733 | 122.7768 | 122.7676 | 122.7036 | 0.23804 | 0.17395 | 0.24719 | 0.059509 | 0.24719 | 0.1236 | 0.086975 | 0.091553 | 122.5937 | 122.6212 | -0.13275 | -0.10986 | 122.5662 | 122.6532 | 122.5113 | 122.6578
2396.4375 | 122.8729 | -122.5571 | 0.07782 | -0.0036622 | 0.063583 | 0.014825 | 0.02183 | -0.0016898 | -0.00061944 | -0.00015591 | -0.0015565 | 0.022084 | 0.020984 | 0.019173 | 0.0022537 | 0.020093 | 0.0038473 | -0.013733 | 0.036621 | -0.045776 | 0.032043 | 0.17395 | 0.041199 | 0.068665 | 0.082397 | 0.036621 | -0.036621 | 0.091553 | 0.16937 | 0.07782 | 0.19684 | 122.5113 | -0.041199 | -0.045777 | 122.731 | 122.6257 | 122.5983 | 0.11444 | 0.086975 | 122.5204 | -0.041199 | 0.013733 | 122.7264 | 122.7539 | 122.6349 | 0.23346 | 0.11444 | 0.21973 | 0.077819 | 0.20599 | 0.12817 | 0.082397 | 0.073242 | 122.5937 | 122.5937 | -0.1236 | -0.11444 | 122.5891 | 122.6486 | 122.5433 | 122.6395
2398.1094 | 122.8729 | -122.5479 | 0.11444 | -0.011291 | 0.062728 | 0.018243 | 0.020548 | -0.0010488 | -0.003183 | -0.0012241 | -0.0046081 | 0.022939 | 0.020343 | 0.020454 | -0.0015915 | 0.016034 | -0.00021153 | -0.064087 | 0.041199 | -0.036621 | -0.009155 | 0.14191 | 0.050354 | 0.050354 | 0.059509 | 0.054932 | -0.050354 | 0.082397 | 0.1831 | 0.10529 | 0.19226 | 122.5113 | -0.073242 | -0.1236 | 122.6898 | 122.5983 | 122.5983 | 0.086975 | 0.086975 | 122.4976 | -0.059509 | -0.032044 | 122.731 | 122.7402 | 122.6532 | 0.24261 | 0.15564 | 0.17853 | 0.027466 | 0.23346 | 0.13275 | 0.07782 | 0.10529 | 122.5891 | 122.6028 | -0.15106 | -0.16479 | 122.5388 | 122.6303 | 122.4838 | 122.6074
2399.8594 | 122.8958 | -122.5479 | 0.073242 | 0.0039673 | 0.062515 | 0.015466 | 0.020762 | -0.0036124 | 0.00023496 | -0.00058311 | -0.0046081 | 0.023152 | 0.019062 | 0.024727 | -0.00073705 | 0.017103 | -0.0046975 | -0.018311 | 0.041199 | -0.036621 | 0.032043 | 0.21057 | 0.054932 | 0.082397 | 0.10529 | 0.050354 | -0.041199 | 0.086975 | 0.19684 | 0.1236 | 0.18768 | 122.5113 | -0.032043 | -0.041199 | 122.7585 | 122.6303 | 122.6028 | 0.11902 | 0.091553 | 122.5067 | -0.022888 | 0.013733 | 122.7448 | 122.7356 | 122.6715 | 0.22888 | 0.16479 | 0.24719 | 0.068664 | 0.23804 | 0.12817 | 0.07782 | 0.091553 | 122.5891 | 122.5983 | -0.10986 | -0.11444 | 122.58 | 122.6349 | 122.5296 | 122.6532
2401.5625 | 122.8317 | -122.5754 | 0.07782 | -0.0036622 | 0.064865 | 0.016962 | 0.019908 | -0.0025442 | -0.0033966 | -0.0029331 | 0.0014953 | 0.024861 | 0.020557 | 0.01725 | 0.00033115 | 0.015394 | -0.0038431 | -0.036621 | 0.045776 | -0.041199 | 0.004578 | 0.14191 | -0.004578 | 0.032043 | 0.032043 | 0.07782 | -0.045776 | 0.054932 | 0.11444 | 0.050354 | 0.16022 | 122.5342 | -0.032044 | -0.073242 | 122.7173 | 122.6074 | 122.5708 | 0.073242 | 0.036621 | 122.5296 | 0 | -0.022888 | 122.6898 | 122.7356 | 122.6257 | 0.20599 | 0.09613 | 0.18311 | 0.045777 | 0.16022 | 0.10071 | 0.086975 | 0.1236 | 122.6212 | 122.6532 | -0.11902 | -0.1236 | 122.58 | 122.6303 | 122.5388 | 122.6074

## Thermal Data
Fire Time | B Position - Tray - Middle | D Position - 3' | D Position - Middle | D Position - 7'
-0.6521 | 8.3904 | 8.7226 | 8.9391 | 9.1304
0.3479 | 8.4021 | 8.7223 | 8.9368 | 9.1227
1.3479 | 8.3969 | 8.7281 | 8.9402 | 9.1225
2.3479 | 8.396 | 8.7265 | 8.9472 | 9.1288
3.3479 | 8.3933 | 8.7247 | 8.9364 | 9.1283
4.3479 | 8.3849 | 8.7228 | 8.9467 | 9.1309
5.3479 | 8.377 | 8.7287 | 8.9466 | 9.1313
6.3479 | 8.3778 | 8.7159 | 8.9431 | 9.1419
7.3479 | 8.3751 | 8.7214 | 8.9591 | 9.1373
8.3479 | 8.3643 | 8.7182 | 8.9509 | 9.1418
9.3479 | 8.3657 | 8.735 | 9.0033 | 9.138
10.3479 | 8.3853 | 8.8056 | 9.3678 | 9.1769
11.3479 | 8.4461 | 8.8167 | 10.1256 | 9.1933
12.3479 | 8.9291 | 8.8896 | 10.7955 | 9.4277
13.3479 | 9.6074 | 9.6256 | 12.2755 | 10.0204
14.3479 | 10.8227 | 11.1179 | 14.9358 | 11.1338
15.3479 | 12.3648 | 12.9705 | 17.6633 | 11.6566
16.3479 | 14.326 | 15.9452 | 21.4652 | 12.4693
17.3479 | 16.3186 | 18.7013 | 25.8345 | 13.6754
18.3479 | 18.6458 | 21.3915 | 31.1198 | 15.2184
19.3479 | 21.1644 | 24.7169 | 35.6621 | 16.4091
20.3479 | 23.6847 | 28.602 | 40.2139 | 17.8927
21.3479 | 26.3148 | 31.4608 | 45.3636 | 19.4871
22.3479 | 29.8526 | 35.3153 | 49.8693 | 22.5897
23.3479 | 33.7732 | 37.9095 | 56.8248 | 24.9875
24.3479 | 36.9402 | 41.1215 | 61.1181 | 26.654
25.3479 | 39.4387 | 44.0889 | 66.0871 | 29.465
26.3479 | 42.3454 | 46.4959 | 71.7811 | 32.0977
27.3479 | 44.9516 | 49.1573 | 76.2848 | 33.87
28.3635 | 48.1349 | 52.1088 | 82.1126 | 37.683
29.3479 | 50.4804 | 54.9021 | 85.1065 | 40.2315
30.3479 | 52.5706 | 57.981 | 88.7704 | 42.9183
31.3479 | 55.6334 | 61.249 | 93.6723 | 46.0203
32.3479 | 58.4649 | 63.3538 | 98.0333 | 50.5142
33.3479 | 61.4369 | 67.0195 | 101.7869 | 53.9619
34.3479 | 64.1266 | 69.0416 | 107.0979 | 56.6008
35.3479 | 66.4786 | 73.0635 | 111.9718 | 58.8709
36.3479 | 68.8715 | 76.4136 | 114.3823 | 61.9838
37.3479 | 70.7295 | 80.1321 | 116.4689 | 65.016
38.3479 | 72.4062 | 81.6728 | 119.7646 | 67.8479
39.3479 | 74.8624 | 83.1728 | 122.2224 | 70.5556
40.3479 | 77.0016 | 84.9189 | 124.8157 | 72.3135
41.3479 | 79.2881 | 87.1484 | 127.2985 | 74.4399
42.3479 | 82.4389 | 89.1051 | 129.3108 | 77.238
43.3479 | 84.6468 | 92.7118 | 130.6121 | 80.5044
44.3479 | 85.9249 | 94.6574 | 132.1059 | 82.9248
45.3479 | 87.8505 | 96.2465 | 132.8888 | 85.3105
46.3479 | 88.599 | 98.0403 | 134.1165 | 88.8757
47.3479 | 89.5101 | 98.6193 | 136.5777 | 90.9358
48.3479 | 91.0657 | 99.8119 | 137.6981 | 93.1927
49.3479 | 92.7904 | 100.6305 | 139.7043 | 96.2432
50.3479 | 95.1632 | 101.8538 | 142.2219 | 98.6324
51.3479 | 97.7746 | 103.4459 | 143.2724 | 100.2478
52.3479 | 98.2368 | 103.9747 | 144.5491 | 102.7187
53.3479 | 98.1179 | 104.9835 | 146.3396 | 105.1657
54.3479 | 97.8816 | 105.6452 | 147.5398 | 106.5805
55.3635 | 98.4408 | 105.9526 | 148.5046 | 108.0742
56.3479 | 99.3506 | 107.6457 | 149.6477 | 109.4381
57.3479 | 100.5354 | 109.3352 | 151.7362 | 110.5242
58.3479 | 101.3682 | 111.1894 | 153.8676 | 112.3351
59.3479 | 102.2335 | 113.7384 | 154.6317 | 114.4619
60.3479 | 103.5718 | 116.6468 | 155.6816 | 115.7475
61.3479 | 104.4736 | 119.8053 | 156.9683 | 117.1797
62.3479 | 104.9255 | 121.425 | 158.4194 | 119.4354
63.3479 | 105.9802 | 123.6866 | 159.8112 | 120.7854
64.3479 | 107.0373 | 126.3207 | 160.8386 | 122.7156
65.3479 | 107.5496 | 128.9539 | 162.2039 | 123.9187
66.3479 | 107.7194 | 130.0008 | 163.4423 | 125.4131
67.3479 | 108.0523 | 131.0526 | 164.456 | 126.355
68.3479 | 108.8248 | 131.83 | 164.469 | 127.2466
69.3479 | 108.6351 | 133.4563 | 164.8365 | 128.1043
70.3479 | 108.6658 | 134.4525 | 166.0062 | 129.1022
71.3479 | 109.7081 | 134.616 | 167.494 | 130.1829
72.3479 | 110.3827 | 134.559 | 167.8232 | 131.5561
73.3479 | 110.8645 | 134.3585 | 166.8863 | 131.8026
74.3479 | 111.3022 | 134.3843 | 167.2491 | 132.3367
75.3479 | 111.8404 | 134.663 | 167.967 | 132.4935
76.3479 | 112.1188 | 135.1286 | 167.9419 | 132.9796
77.3479 | 112.4657 | 135.2904 | 167.1524 | 133.7348
78.3479 | 113.1567 | 136.2712 | 167.389 | 134.7921
79.3479 | 113.4907 | 136.4738 | 168.1451 | 135.7726
80.3479 | 114.7779 | 136.8341 | 168.4328 | 136.7967
81.3479 | 115.3008 | 136.7278 | 168.7336 | 137.7923
82.3479 | 115.4408 | 136.8249 | 168.5174 | 138.1884
83.3479 | 115.7439 | 136.5669 | 168.6751 | 138.9324
84.3479 | 115.7304 | 137.1731 | 169.6073 | 140.1688
85.3479 | 116.213 | 137.5295 | 168.7527 | 140.493
86.3479 | 116.8047 | 137.445 | 167.8261 | 141.2247
87.3479 | 116.6779 | 137.5194 | 166.8316 | 141.9395
88.3479 | 116.993 | 137.8127 | 165.723 | 141.8682
89.3479 | 117.8312 | 138.0481 | 165.3183 | 142.8423
90.3479 | 118.5693 | 139.1142 | 166.0071 | 143.2404
91.3479 | 119.3214 | 139.6624 | 166.1055 | 143.6051
92.3479 | 120.2318 | 140.0061 | 166.4634 | 145.5674
93.3479 | 121.0007 | 139.7809 | 167.6406 | 145.9994
94.3479 | 121.8555 | 139.7144 | 167.0327 | 147.6564
95.3479 | 122.9333 | 139.6099 | 166.2426 | 148.4702
96.3479 | 124.7083 | 139.3024 | 165.716 | 148.9304
97.3479 | 124.7308 | 139.4059 | 165.6803 | 149.8226
98.3479 | 125.2608 | 139.5043 | 166.2373 | 150.6795
99.3479 | 125.7435 | 139.3313 | 166.4777 | 152.051
100.3479 | 126.7639 | 139.0033 | 166.196 | 153.0321
101.3479 | 126.7956 | 138.8393 | 166.0558 | 153.8671
102.3479 | 127.1621 | 138.6934 | 166.859 | 155.2063
103.3479 | 126.9261 | 138.9057 | 167.7154 | 156.3842
104.3479 | 126.8985 | 139.1839 | 167.5743 | 157.1762
105.3479 | 127.3453 | 139.0078 | 168.5746 | 157.7732
106.3479 | 129.062 | 140.0965 | 169.3239 | 158.7353
107.3479 | 130.0972 | 140.3515 | 170.3351 | 160.3964
108.3479 | 130.3784 | 140.8524 | 171.3593 | 160.9092
109.3479 | 130.98 | 141.2878 | 172.4878 | 161.1332
110.3479 | 131.952 | 141.5629 | 174.1133 | 161.5756
111.3479 | 132.5672 | 141.4854 | 175.1104 | 161.5117
112.3479 | 133.787 | 141.9609 | 175.8999 | 162.2069
113.3479 | 134.6032 | 141.5767 | 176.1124 | 162.4563
114.3479 | 135.3948 | 141.9451 | 177.1473 | 162.7495
115.3479 | 136.7007 | 143.798 | 179.8261 | 163.6402
116.3479 | 138.0252 | 144.5353 | 181.7759 | 164.0637
117.3479 | 139.821 | 146.4075 | 182.8628 | 165.1952
118.3479 | 140.816 | 146.2616 | 183.8242 | 165.3308
119.3479 | 142.4394 | 146.6573 | 184.0302 | 165.8568
120.3479 | 144.049 | 148.163 | 184.9292 | 166.5644
121.3479 | 146.1309 | 149.0475 | 186.2124 | 167.278
122.3479 | 146.9483 | 149.878 | 186.7774 | 167.7688
123.3479 | 148.5615 | 150.2125 | 187.0667 | 168.8107
124.3479 | 149.6361 | 150.5083 | 187.5204 | 169.0978
125.3479 | 150.4394 | 150.5193 | 187.16 | 169.8762
126.3479 | 150.4858 | 151.1727 | 188.4868 | 170.2154
127.3479 | 152.6285 | 150.8693 | 187.7761 | 171.1633
128.3479 | 153.037 | 151.1251 | 188.5501 | 170.5116
129.3479 | 153.6362 | 151.4198 | 187.1017 | 172.343
130.3479 | 153.4294 | 151.5345 | 186.8438 | 174.0333
131.3479 | 152.695 | 151.7222 | 187.2208 | 175.7962
132.3479 | 153.7779 | 151.6481 | 187.8773 | 177.0193
133.3479 | 153.7577 | 151.9734 | 188.4942 | 177.9299
134.3479 | 153.6122 | 151.9671 | 188.2603 | 178.1149
135.3479 | 153.61 | 152.5876 | 189.705 | 178.6601
136.3479 | 154.2429 | 152.6716 | 191.1539 | 179.3745
137.3479 | 154.5788 | 153.5089 | 191.9667 | 179.6908
138.3479 | 154.8838 | 153.5178 | 192.9221 | 181.7078
139.3479 | 156.302 | 153.2328 | 192.5441 | 182.1631
140.3479 | 157.1158 | 152.7173 | 193.3484 | 183.2284
141.3479 | 157.2778 | 152.5808 | 194.9709 | 184.4299
142.3479 | 157.4464 | 152.2404 | 193.9012 | 183.6215
143.3479 | 157.3545 | 151.8782 | 193.8503 | 183.5916
144.3479 | 158.5225 | 151.4596 | 193.399 | 183.2769
145.3479 | 159.3801 | 151.7598 | 194.3163 | 183.0771
146.3479 | 160.7795 | 152.0663 | 196.4921 | 182.7023
147.3479 | 161.7383 | 153.61 | 197.7916 | 182.4215
148.3479 | 162.6771 | 154.4318 | 198.978 | 182.9248
149.3479 | 163.2378 | 154.693 | 199.0486 | 182.4632
150.3479 | 165.1912 | 155.309 | 198.9485 | 182.9571
151.3479 | 166.983 | 155.7713 | 199.7988 | 182.8983
152.3479 | 167.3069 | 156.2359 | 201.4818 | 184.3492
153.3479 | 168.0293 | 157.0189 | 202.5758 | 185.0311
154.3479 | 169.1712 | 157.1672 | 202.4136 | 186.1167
155.3479 | 170.3095 | 156.9276 | 202.3295 | 186.2659
156.3479 | 171.8454 | 156.7651 | 201.8391 | 187.4606
157.3479 | 172.7131 | 156.5073 | 201.1097 | 189.2217
158.3479 | 173.4344 | 156.1803 | 200.4409 | 190.2869
159.3479 | 174.0763 | 156.8026 | 201.024 | 190.9673
160.3479 | 174.8393 | 157.4391 | 201.8369 | 192.4305
161.3479 | 175.8856 | 157.8387 | 202.2779 | 191.7081
162.3479 | 177.1162 | 157.5158 | 202.3421 | 192.6645
163.3479 | 177.7338 | 157.1784 | 202.3877 | 192.1069
164.3479 | 178.4697 | 157.4975 | 201.6871 | 193.4614
165.3479 | 179.1161 | 158.1076 | 201.5318 | 194.253
166.3479 | 179.5153 | 158.1016 | 200.8388 | 195.5481
167.3479 | 180.0256 | 158.2218 | 200.5867 | 195.1583
168.3479 | 180.9529 | 157.8369 | 200.0011 | 195.4199
169.3479 | 181.5956 | 157.677 | 200.173 | 195.2936
170.3479 | 182.1013 | 157.7509 | 199.5164 | 194.767
171.3479 | 182.3472 | 157.8244 | 199.3896 | 194.8959
172.3479 | 181.7558 | 158.2402 | 199.2665 | 194.8901
173.3479 | 181.8952 | 157.9671 | 199.9392 | 195.2387
174.3479 | 182.3779 | 157.8977 | 200.9832 | 194.7116
175.3479 | 182.1615 | 157.8065 | 200.6448 | 193.6457
176.3479 | 182.2208 | 157.4012 | 200.8381 | 192.5413
177.3479 | 183.5417 | 157.2119 | 201.1702 | 192.8206
178.3479 | 185.606 | 157.5819 | 202.3467 | 192.8496
179.3479 | 185.8259 | 157.4408 | 201.5243 | 193.0459
180.3479 | 186.2903 | 157.2109 | 201.803 | 192.9411
181.3479 | 188.1918 | 156.9567 | 202.2049 | 194.4982
182.3479 | 189.6627 | 157.2417 | 201.7919 | 194.8077
183.3479 | 189.4396 | 157.0645 | 202.222 | 194.3431
184.3479 | 189.6267 | 157.658 | 202.3878 | 193.8114
185.3479 | 190.1211 | 158.0952 | 203.9823 | 193.5983
186.3479 | 190.4714 | 158.4589 | 205.5938 | 193.6313
187.3479 | 191.584 | 159.1133 | 206.5751 | 194.2403
188.3479 | 192.1406 | 159.793 | 207.7249 | 194.3761
189.3479 | 192.1342 | 160.2997 | 207.6643 | 195.1094
190.3479 | 193.3956 | 161.204 | 207.4329 | 196.4245
191.3479 | 195.5643 | 162.008 | 207.3296 | 197.5991
192.3479 | 195.783 | 162.5836 | 208.1516 | 197.5586
193.3479 | 195.8521 | 163.5961 | 209.2692 | 197.2522
194.3479 | 196.1531 | 163.9007 | 210.5903 | 196.8699
195.3479 | 196.1505 | 165.486 | 213.8387 | 197.0144
196.3479 | 196.0919 | 166.6153 | 214.8957 | 196.8865
197.3479 | 196.8357 | 167.0404 | 213.9312 | 197.4273
198.3479 | 197.5958 | 167.9166 | 213.7337 | 198.0883
199.3479 | 197.8587 | 168.7263 | 214.1414 | 198.5532
200.3479 | 199.5127 | 169.2348 | 213.5065 | 198.8787
201.3479 | 199.6157 | 168.8678 | 212.3324 | 200.1974
202.3479 | 199.906 | 168.3566 | 213.2903 | 200.6144
203.3479 | 200.042 | 168.5906 | 212.0504 | 201.6042
204.3479 | 201.3649 | 169.0434 | 212.8292 | 202.5589
205.3479 | 200.2951 | 169.4412 | 213.7125 | 202.9676
206.3479 | 200.4394 | 169.3467 | 213.7142 | 203.4314
207.3479 | 200.4319 | 169.217 | 214.2501 | 203.5344
208.3479 | 200.4188 | 169.8121 | 214.0582 | 203.8521
209.3479 | 200.6215 | 170.6716 | 214.3099 | 204.7941
210.3479 | 201.6712 | 170.8915 | 215.0883 | 205.7181
211.3479 | 201.707 | 171.3537 | 215.3895 | 206.1766
212.3479 | 201.8096 | 171.9282 | 215.4358 | 206.3801
213.3479 | 203.0288 | 171.6605 | 215.9165 | 206.1135
214.3479 | 203.0568 | 171.7992 | 216.1702 | 205.5547
215.3479 | 203.168 | 172.8746 | 216.5805 | 205.9219
216.3479 | 202.6881 | 172.79 | 217.1683 | 206.5572
217.3479 | 202.6696 | 173.3431 | 217.3126 | 206.1234
218.3479 | 203.4837 | 173.5486 | 217.5292 | 207.4268
219.3479 | 203.5503 | 173.9384 | 217.7448 | 207.6269
220.3479 | 203.7578 | 173.5075 | 216.5876 | 209.0169
221.3479 | 205.2413 | 173.2056 | 217.0029 | 211.6851
222.3479 | 205.0533 | 173.1771 | 218.0622 | 212.2486
223.3479 | 205.8632 | 173.1161 | 217.8468 | 213.6861
224.3479 | 207.2644 | 173.1047 | 218.0953 | 213.6053
225.3479 | 208.3656 | 174.0247 | 219.1606 | 213.6734
226.3479 | 209.5396 | 174.5317 | 219.0059 | 214.203
227.3479 | 210.4417 | 175.1198 | 221.0144 | 214.081
228.3479 | 211.5906 | 175.3542 | 221.5289 | 213.7005
229.3479 | 213.0545 | 176.3786 | 222.6032 | 214.4489
230.3479 | 214.6668 | 177.1959 | 222.8491 | 215.4508
231.3479 | 215.2847 | 176.5632 | 225.3559 | 215.9041
232.3479 | 216.0035 | 176.7223 | 226.2728 | 216.9702
233.3479 | 217.8758 | 177.8801 | 227.8729 | 217.8766
234.3479 | 218.6342 | 178.355 | 229.7113 | 219.6432
235.3479 | 219.0066 | 179.1173 | 230.2028 | 220.177
236.3479 | 219.944 | 179.6454 | 230.9997 | 220.9313
237.3479 | 221.2406 | 179.9763 | 231.5552 | 221.908
238.3479 | 223.268 | 180.2733 | 232.3659 | 222.9476
239.3479 | 223.2569 | 180.3464 | 232.6439 | 224.1592
240.3479 | 224.3563 | 180.0727 | 232.922 | 225.3354
241.3479 | 224.5159 | 179.9788 | 233.0249 | 227.5
242.3479 | 225.1345 | 179.8192 | 233.3825 | 228.5113
243.3479 | 225.9037 | 180.4116 | 233.7147 | 227.7509
244.3479 | 226.3594 | 181.4143 | 234.3488 | 228.7649
245.3479 | 227.521 | 181.5636 | 234.3473 | 229.6005
246.3479 | 227.511 | 182.2246 | 235.1323 | 229.7394
247.3479 | 227.7084 | 182.1019 | 235.5228 | 230.8644
248.3479 | 228.4085 | 182.1929 | 235.9406 | 230.438
249.3479 | 229.0878 | 182.478 | 237.4305 | 232.8633
250.3479 | 229.0734 | 182.9965 | 237.4693 | 232.5117
251.3479 | 229.1686 | 183.0463 | 238.2579 | 232.4721
252.3479 | 229.1522 | 184.0332 | 238.9521 | 233.336
253.3479 | 228.8014 | 184.2128 | 238.8229 | 236.2831
254.3479 | 228.2795 | 183.6466 | 238.9683 | 236.7215
255.3479 | 227.8958 | 184.2251 | 238.3597 | 236.2334
256.3479 | 228.4505 | 184.4452 | 238.5434 | 237.6316
257.3479 | 228.0843 | 185.5941 | 238.6304 | 238.1686
258.3479 | 228.1989 | 185.6576 | 238.9278 | 238.583
259.3479 | 227.7178 | 186.4817 | 239.5676 | 239.1586
260.3479 | 228.5193 | 186.2003 | 240.8805 | 239.1029
261.3479 | 228.4907 | 186.4425 | 241.9298 | 241.3513
262.3479 | 229.7335 | 188.6556 | 244.3272 | 241.8022
263.3479 | 230.1462 | 188.8781 | 244.6204 | 241.8732
264.3479 | 230.4207 | 189.9312 | 245.0933 | 242.6932
265.3479 | 230.4039 | 190.2767 | 245.3448 | 242.9005
266.3479 | 231.2598 | 191.8988 | 246.438 | 245.5208
267.3479 | 232.5599 | 191.7219 | 246.2611 | 245.4339
268.3479 | 233.4154 | 191.8446 | 246.2735 | 245.1372
269.3479 | 233.4041 | 191.8289 | 246.8294 | 245.7139
270.3479 | 233.549 | 191.5156 | 248.2588 | 246.2554
271.3479 | 235.6409 | 195.0934 | 248.8436 | 239.7669
272.3479 | 233.2171 | 191.8783 | 247.8768 | 246.9871
273.3479 | 233.7941 | 192.9537 | 248.4937 | 247.0124
274.3479 | 233.8447 | 193.2411 | 250.1631 | 246.6604
275.3479 | 234.3364 | 193.7448 | 250.1362 | 247.4756
276.3479 | 234.0205 | 193.904 | 251.1123 | 247.9281
277.3479 | 234.1931 | 194.1254 | 251.4556 | 248.0009
278.3479 | 234.4322 | 193.6602 | 250.564 | 249.3495
279.3479 | 234.6592 | 193.3885 | 250.0825 | 248.6639
280.3479 | 235.7368 | 193.2679 | 251.8791 | 248.8151
281.3479 | 236.9497 | 193.4572 | 252.6952 | 248.5123
282.3479 | 237.166 | 195.0215 | 253.9792 | 247.9477
283.3479 | 237.7291 | 195.3265 | 254.4307 | 247.349
284.3479 | 237.9742 | 195.2522 | 253.9764 | 247.3789
285.3479 | 238.1425 | 195.2039 | 253.9151 | 247.0866
286.3479 | 238.8506 | 195.8042 | 254.9207 | 246.0614
287.3479 | 240.9435 | 196.3916 | 256.4481 | 245.6099
288.3479 | 241.8373 | 197.0881 | 257.7852 | 245.6943
289.3479 | 242.2076 | 197.5294 | 259.4495 | 245.4802
290.3479 | 242.632 | 199.3611 | 262.7592 | 246.104
291.3479 | 243.284 | 200.3141 | 264.1192 | 246.5766
292.3479 | 243.1716 | 200.2901 | 263.5014 | 247.4392
293.3479 | 243.1076 | 200.2958 | 262.8304 | 248.1738
294.3479 | 243.1492 | 199.9473 | 262.4232 | 249.3043
295.3479 | 244.0475 | 199.6608 | 262.3886 | 248.9798
296.3479 | 245.2345 | 200.4255 | 263.2605 | 249.1293
297.3479 | 245.6448 | 202.5962 | 264.1339 | 250.1522
298.3479 | 245.8387 | 203.0444 | 265.3614 | 250.6728
299.3479 | 245.7718 | 203.5302 | 265.7898 | 252.0311
300.3479 | 245.7369 | 203.3695 | 264.9433 | 253.7833
301.3479 | 245.9801 | 203.3753 | 265.4226 | 254.2368
302.3479 | 246.052 | 203.7057 | 264.2363 | 255.3294
303.3479 | 247.1432 | 203.6162 | 264.0876 | 255.0803
304.3479 | 247.7042 | 204.4587 | 265.9639 | 255.1046
305.3479 | 248.099 | 205.597 | 267.9737 | 255.4617
306.3479 | 248.6199 | 206.6869 | 268.4945 | 256.3787
307.3479 | 248.1669 | 206.937 | 269.1598 | 256.8192
308.3479 | 247.5447 | 206.7863 | 269.2264 | 257.6421
309.3479 | 247.3237 | 206.99 | 268.7643 | 258.4871
310.3479 | 247.747 | 208.2942 | 268.5789 | 259.6565
311.3479 | 248.0328 | 208.551 | 269.2956 | 260.3193
312.3479 | 247.8417 | 209.1747 | 270.142 | 262.0873
313.3479 | 248.2153 | 210.0268 | 270.4454 | 262.5127
314.3479 | 248.2514 | 210.9794 | 270.6517 | 263.2197
315.3479 | 248.5326 | 211.4042 | 270.3683 | 263.9209
316.3479 | 248.6007 | 211.4204 | 272.5238 | 265.0239
317.3479 | 249.046 | 212.5303 | 273.5319 | 265.8442
318.3479 | 249.9203 | 213.4981 | 274.5919 | 265.3723
319.3479 | 250.3767 | 213.4509 | 274.7559 | 265.5697
320.3479 | 251.0888 | 213.9068 | 276.2546 | 265.1246
321.3479 | 251.7598 | 215.1961 | 277.2086 | 264.4626
322.3479 | 252.3893 | 216.288 | 278.7781 | 264.6939
323.3479 | 253.567 | 218.017 | 281.122 | 265.0814
324.3479 | 255.6393 | 218.3343 | 283.6002 | 265.4953
325.3479 | 256.1306 | 219.0909 | 284.8217 | 267.0139
326.3479 | 257.4465 | 220.6773 | 288.0042 | 267.8117
327.3479 | 258.1237 | 221.3824 | 289.5353 | 267.81
328.3479 | 258.6555 | 223.1208 | 291.0963 | 268.1381
329.3479 | 260.4345 | 223.4596 | 291.7298 | 268.4054
330.3479 | 261.3586 | 223.072 | 292.3004 | 267.9247
331.3479 | 261.9287 | 223.4117 | 292.3792 | 268.3895
332.3479 | 262.56 | 224.0186 | 291.5656 | 269.4739
333.3479 | 263.9828 | 224.9044 | 292.0478 | 269.0004
334.3479 | 263.9911 | 224.4392 | 291.3454 | 270.2657
335.3479 | 264.6728 | 224.7078 | 290.5231 | 271.0717
336.3479 | 266.7163 | 224.6245 | 291.4331 | 271.4822
337.3479 | 267.6594 | 224.265 | 292.4939 | 271.8048
338.3479 | 268.0595 | 224.741 | 293.5505 | 272.6659
339.3479 | 268.486 | 224.2409 | 293.5632 | 273.2346
340.3479 | 269.5685 | 224.4143 | 294.8739 | 273.3445
341.3479 | 269.9152 | 224.4008 | 294.8986 | 273.7469
342.3479 | 270.4286 | 224.2486 | 295.1423 | 273.6973
343.3479 | 270.8633 | 223.6009 | 295.1331 | 272.6058
344.3479 | 272.4968 | 223.7557 | 293.7843 | 272.1199
345.3479 | 273.7278 | 223.7676 | 293.782 | 271.1602
346.3479 | 274.8409 | 224.2634 | 293.6383 | 270.6293
347.3479 | 275.9831 | 224.7482 | 295.446 | 271.4041
348.3479 | 276.554 | 225.5847 | 296.4158 | 272.9905
349.3479 | 276.7443 | 226.8816 | 296.084 | 273.5397
350.3479 | 277.8177 | 228.0931 | 299.1888 | 274.0245
351.3479 | 278.8232 | 228.6909 | 299.4883 | 275.565
352.3479 | 279.5793 | 228.8475 | 298.6738 | 275.641
353.3479 | 280.1992 | 228.999 | 299.3672 | 275.1038
354.3479 | 281.2541 | 228.959 | 298.6113 | 275.7084
355.3479 | 282.9019 | 228.7639 | 299.2111 | 276.7082
356.3479 | 283.4504 | 228.7905 | 299.7171 | 278.3401
357.3479 | 284.712 | 228.4732 | 299.8469 | 280.7942
358.3479 | 285.9121 | 229.0606 | 301.0253 | 282.4579
359.3479 | 286.4414 | 229.6131 | 299.8325 | 282.3141
360.3479 | 287.4336 | 229.3317 | 299.7123 | 281.8736
361.3479 | 287.3318 | 230.0516 | 300.8124 | 281.1263
362.3479 | 287.1173 | 231.089 | 301.5987 | 280.9972
363.3479 | 286.5124 | 231.5637 | 302.9818 | 280.8344
364.3479 | 287.3589 | 232.7666 | 304.0607 | 280.8587
365.3479 | 287.8327 | 232.3296 | 305.1453 | 281.3943
366.3479 | 288.5248 | 233.3042 | 306.4291 | 281.2272
367.3479 | 289.829 | 233.7261 | 306.941 | 280.7077
368.3479 | 290.4164 | 235.3877 | 307.5972 | 281.9134
369.3479 | 291.3718 | 235.901 | 308.4597 | 282.1476
370.3479 | 292.2545 | 236.9514 | 308.1669 | 282.2372
371.3479 | 292.2524 | 237.3945 | 308.3383 | 281.4344
372.3479 | 292.0216 | 237.7943 | 309.9212 | 281.5142
373.3479 | 292.1179 | 238.72 | 310.9969 | 279.9848
374.3479 | 292.8291 | 243.0175 | 311.0735 | 280.2069
375.3479 | 294.4936 | 244.4231 | 315.2026 | 280.0475
376.3479 | 295.5532 | 246.2886 | 317.1537 | 280.426
377.3479 | 295.9637 | 245.5345 | 318.8249 | 281.1647
378.3479 | 298.1726 | 245.9137 | 318.4998 | 281.7129
379.3479 | 299.6035 | 245.2442 | 319.0919 | 282.1797
380.3479 | 300.9447 | 245.4125 | 318.4085 | 282.237
381.3479 | 300.987 | 244.7761 | 318.7847 | 281.5821
382.3479 | 301.7668 | 245.6972 | 318.4971 | 281.9354
383.3479 | 301.6884 | 247.4153 | 320.0255 | 282.777
384.3479 | 301.8204 | 249.2144 | 322.1132 | 282.6958
385.3479 | 302.3059 | 249.7026 | 322.8424 | 282.3267
386.3479 | 304.3093 | 250.3817 | 325.7852 | 283.6334
387.3479 | 305.9677 | 249.9266 | 325.9347 | 283.3466
388.3479 | 306.0212 | 249.464 | 329.1666 | 283.0408
389.3479 | 306.0346 | 249.8116 | 330.1538 | 283.7563
390.3479 | 307.624 | 250.0685 | 329.4597 | 284.5256
391.3479 | 309.8251 | 250.4405 | 329.2956 | 285.9041
392.3479 | 309.8785 | 249.9986 | 329.8138 | 286.492
393.3479 | 310.1814 | 249.2988 | 329.7365 | 286.269
394.3479 | 311.1837 | 249.6972 | 331.6639 | 287.5608
395.3479 | 312.6003 | 249.8314 | 332.8052 | 288.1247
396.3479 | 312.4006 | 250.09 | 335.3682 | 288.2563
397.3479 | 313.7211 | 249.8566 | 335.7221 | 290.2073
398.3479 | 313.5002 | 251.3917 | 337.6197 | 289.8713
399.3479 | 314.5513 | 251.9418 | 338.7129 | 289.6502
400.3479 | 315.2567 | 252.198 | 339.4525 | 289.7856
401.3479 | 315.5379 | 252.5376 | 340.2605 | 290.6898
402.3479 | 316.1815 | 252.375 | 339.3748 | 291.4648
403.3479 | 316.6808 | 251.9914 | 342.661 | 292.0122
404.3479 | 318.5467 | 252.8086 | 345.3418 | 291.3777
405.3479 | 320.1945 | 254.038 | 349.4902 | 292.1861
406.3479 | 322.9845 | 253.8951 | 353.8368 | 292.7704
407.3479 | 323.2717 | 253.8146 | 352.8113 | 294.8443
408.3479 | 324.4928 | 254.1966 | 352.6615 | 296.0135
409.3479 | 324.4962 | 255.002 | 361.7826 | 296.4583
410.3479 | 325.7612 | 255.7304 | 366.4485 | 297.2773
411.3479 | 325.9494 | 256.0143 | 363.947 | 298.115
412.3479 | 325.8152 | 256.6161 | 360.1146 | 299.3023
413.3479 | 327.1113 | 255.7431 | 356.7563 | 303.8799
414.3479 | 329.8578 | 255.5099 | 357.5135 | 305.5458
415.3479 | 330.813 | 255.2071 | 359.6212 | 307.8777
416.3479 | 332.2059 | 254.5275 | 356.3761 | 308.9459
417.3479 | 331.6307 | 255.1129 | 355.5748 | 309.2381
418.3479 | 332.08 | 254.9661 | 356.4979 | 309.8256
419.3479 | 332.0292 | 255.1611 | 357.0494 | 309.2793
420.3479 | 331.888 | 256.2094 | 357.9493 | 308.2871
421.3479 | 333.2941 | 257.705 | 366.1226 | 307.3204
422.3479 | 333.8167 | 257.5386 | 363.455 | 307.7173
423.3479 | 334.0887 | 257.5569 | 362.8193 | 308.475
424.3479 | 333.1303 | 257.7709 | 360.6149 | 307.6459
425.3479 | 333.962 | 258.4819 | 359.8905 | 308.6065
426.3479 | 334.9342 | 258.7896 | 360.4433 | 309.4338
427.3479 | 335.1017 | 259.2153 | 360.4516 | 311.3252
428.3479 | 336.1166 | 260.0777 | 360.9264 | 311.0789
429.3479 | 338.0613 | 260.5491 | 363.0799 | 310.6723
430.3479 | 337.9581 | 260.8896 | 363.6374 | 309.7038
431.3479 | 336.6204 | 261.6003 | 362.5666 | 308.8577
432.3479 | 338.012 | 260.9119 | 362.5597 | 308.7223
433.3479 | 339.6185 | 260.8274 | 365.8255 | 310.2546
434.3479 | 340.1058 | 261.896 | 368.064 | 310.8571
435.3479 | 340.5892 | 263.0539 | 369.0251 | 311.448
436.3479 | 342.4342 | 262.7694 | 371.611 | 312.4811
437.3479 | 343.1739 | 262.6003 | 376.8464 | 311.6088
438.3479 | 343.8075 | 264.698 | 377.4823 | 313.0713
439.3479 | 344.8652 | 267.1488 | 378.6588 | 312.0569
440.3479 | 345.9075 | 268.651 | 376.7817 | 313.4958
441.3479 | 345.5728 | 269.3604 | 374.6997 | 313.6429
442.3479 | 347.3905 | 270.6368 | 375.6939 | 312.4261
443.3479 | 348.0501 | 270.9869 | 375.198 | 312.0125
444.3479 | 348.1703 | 270.5714 | 375.5576 | 312.0537
445.3479 | 349.6959 | 271.1165 | 379.4833 | 313.3071
446.3479 | 351.1896 | 272.8574 | 387.1369 | 314.5482
447.3479 | 353.4064 | 273.6433 | 396.6055 | 315.3136
448.3479 | 355.9329 | 274.0968 | 406.9608 | 317.2308
449.3479 | 359.4575 | 274.3485 | 412.5415 | 319.01
450.3479 | 360.2809 | 275.8139 | 418.3042 | 320.3622
451.3479 | 366.5834 | 276.1672 | 420.9163 | 323.3026
452.3479 | 369.3534 | 277.6845 | 424.0973 | 322.7998
453.3479 | 371.4124 | 277.5198 | 432.0934 | 328.8968
454.3479 | 374.8196 | 277.2798 | 434.3509 | 329.2754
455.3479 | 376.0484 | 277.7561 | 439.8517 | 330.9761
456.3479 | 377.5816 | 279.0661 | 438.7399 | 333.9856
457.3479 | 379.5049 | 279.361 | 443.2214 | 335.4155
458.3479 | 381.5798 | 279.9941 | 446.5465 | 336.6495
459.3479 | 381.3921 | 279.8738 | 447.4749 | 334.5769
460.3479 | 380.4085 | 281.4137 | 443.7621 | 332.3831
461.3479 | 379.1836 | 283.4746 | 440.349 | 329.4763
462.3479 | 378.7603 | 286.1269 | 437.344 | 328.7686
463.3479 | 376.2026 | 286.028 | 430.8099 | 328.1674
464.3479 | 377.2893 | 285.3341 | 427.3715 | 327.6945
465.3479 | 379.2365 | 285.4421 | 424.9872 | 329.5207
466.3479 | 380.4155 | 285.0387 | 427.4035 | 331.5486
467.3479 | 380.7092 | 284.061 | 424.5618 | 332.8435
468.3479 | 382.7402 | 283.1563 | 424.5943 | 335.7756
469.3479 | 385.2602 | 283.1948 | 427.8091 | 334.3845
470.3479 | 383.8621 | 284.7249 | 430.9316 | 335.9045
471.3479 | 383.8564 | 285.4111 | 432.6555 | 335.4713
472.3479 | 385.0003 | 285.0329 | 442.2822 | 337.2263
473.3479 | 384.0765 | 286.5775 | 446.362 | 338.111
474.3479 | 385.7901 | 287.172 | 448.8334 | 339.5177
475.3479 | 387.7429 | 287.0907 | 447.6634 | 338.7877
476.3479 | 388.3096 | 287.6197 | 446.8277 | 338.0469
477.3479 | 388.0439 | 287.9931 | 440.7981 | 339.2378
478.3479 | 387.9706 | 287.5468 | 436.1187 | 340.9947
479.3479 | 388.9232 | 286.1819 | 434.0949 | 342.2684
480.3479 | 391.0239 | 286.8715 | 431.5091 | 344.6597
481.3479 | 393.8748 | 285.6869 | 431.8782 | 343.6404
482.3479 | 395.8517 | 285.1956 | 434.3456 | 344.6798
483.3479 | 396.2512 | 284.2637 | 433.2451 | 345.3306
484.3479 | 397.9713 | 283.7191 | 436.9658 | 346.1896
485.3479 | 400.7888 | 282.976 | 441.9703 | 348.1104
486.3479 | 407.189 | 281.9468 | 444.2995 | 349.1159
487.3479 | 409.474 | 282.2939 | 449.1899 | 352.3844
488.3479 | 410.5956 | 282.0024 | 458.0403 | 351.572
489.3479 | 412.0051 | 282.3102 | 462.6571 | 352.5893
490.3479 | 413.4642 | 283.1091 | 466.3813 | 353.3082
491.3479 | 414.1738 | 284.3054 | 466.2996 | 354.0455
492.3479 | 413.8066 | 284.0907 | 465.23 | 351.0349
493.3479 | 412.8115 | 284.5356 | 458.6134 | 349.0739
494.3479 | 411.64 | 284.7037 | 450.9197 | 347.9211
495.3479 | 410.3884 | 283.7339 | 446.0854 | 346.8493
496.3479 | 413.3966 | 283.3545 | 444.7035 | 345.1051
497.3479 | 413.769 | 284.7391 | 446.615 | 343.4892
498.3479 | 416.6059 | 284.2096 | 448.8387 | 344.142
499.3479 | 418.9881 | 284.7165 | 451.2986 | 343.3025
500.3479 | 422.8094 | 284.1324 | 453.0598 | 344.5655
501.3479 | 423.1332 | 283.4259 | 461.4945 | 342.7255
502.3479 | 422.5535 | 282.5757 | 466.0105 | 341.4773
503.3479 | 420.6578 | 283.6392 | 463.9283 | 339.5567
504.3479 | 419.3131 | 284.7026 | 471.2514 | 339.7237
505.3479 | 420.8872 | 284.2893 | 472.1391 | 339.9237
506.3479 | 419.4664 | 283.9459 | 474.401 | 341.2723
507.3479 | 420.6935 | 284.4361 | 466.7045 | 340.7526
508.3479 | 422.3922 | 284.7921 | 467.5705 | 340.7595
509.3479 | 423.3346 | 285.6596 | 466.5045 | 339.7942
510.3479 | 426.0441 | 287.0477 | 468.8791 | 338.7459
511.3479 | 428.556 | 287.4617 | 475.2016 | 340.3205
512.3479 | 430.2569 | 289.1349 | 471.1489 | 340.3596
513.3479 | 429.8337 | 288.4204 | 468.4642 | 341.9676
514.3479 | 430.749 | 288.7688 | 464.6441 | 342.1217
515.3479 | 429.878 | 288.5264 | 461.0916 | 344.6499
516.3479 | 431.7081 | 288.1112 | 461.2983 | 344.5876
517.3479 | 435.1057 | 289.1956 | 460.443 | 345.4901
518.3479 | 437.982 | 288.2803 | 461.3896 | 347.0741
519.3479 | 440.3674 | 288.8857 | 469.1374 | 344.9217
520.3479 | 444.5127 | 289.3071 | 467.0116 | 344.8
521.3479 | 448.2023 | 289.5523 | 469.9554 | 346.1982
522.3479 | 449.2613 | 289.1148 | 471.3022 | 345.0216
523.3479 | 450.2997 | 288.5824 | 478.276 | 345.1113
524.3479 | 450.8634 | 288.204 | 491.6939 | 343.9308
525.3479 | 453.7866 | 289.402 | 493.4751 | 344.093
526.3479 | 454.6824 | 290.7876 | 502.6495 | 344.6776
527.3479 | 456.0249 | 291.2965 | 515.433 | 346.6993
528.3479 | 459.6272 | 292.3096 | 515.6192 | 346.8965
529.3479 | 462.1281 | 292.8103 | 523.6727 | 347.1114
530.3479 | 466.3331 | 293.7396 | 529.5978 | 349.3388
531.3479 | 466.2807 | 295.1994 | 525.2462 | 350.3058
532.3479 | 466.8297 | 295.8338 | 527.2008 | 350.2097
533.3479 | 466.1314 | 296.865 | 527.5124 | 350.4822
534.3479 | 467.8709 | 299.8342 | 531.279 | 351.4774
535.3479 | 469.1376 | 300.1756 | 532.532 | 350.6619
536.3479 | 469.2804 | 302.5804 | 537.8056 | 351.9817
537.3479 | 471.4884 | 303.9287 | 540.7348 | 353.431
538.3479 | 472.8345 | 304.1208 | 536.9051 | 353.6534
539.3479 | 475.3937 | 305.3229 | 542.735 | 355.1475
540.3479 | 476.6855 | 306.6292 | 547.8165 | 355.4807
541.3479 | 478.1346 | 307.0451 | 546.7366 | 356.1591
542.3479 | 481.139 | 308.4345 | 546.3862 | 357.9608
543.3479 | 485.0111 | 309.7823 | 541.5546 | 357.7336
544.3479 | 488.0601 | 309.6439 | 542.8529 | 357.5384
545.3479 | 490.9295 | 309.6008 | 540.3419 | 356.7922
546.3479 | 492.0051 | 308.634 | 544.7939 | 357.6043
547.3479 | 492.9978 | 308.6866 | 544.3488 | 358.3158
548.3479 | 492.2966 | 309.4133 | 541.1254 | 359.4827
549.3479 | 492.6853 | 310.7142 | 544.398 | 358.0449
550.3479 | 496.9736 | 313.6497 | 546.5919 | 357.7835
551.3479 | 500.0279 | 312.6526 | 545.7551 | 357.7576
552.3479 | 505.0114 | 314.9066 | 548.3709 | 355.9974
553.3479 | 506.1362 | 315.797 | 546.0338 | 357.0722
554.3479 | 506.3946 | 314.7908 | 548.2167 | 361.7638
555.3479 | 508.4861 | 314.8428 | 543.8431 | 364.9665
556.3479 | 506.7279 | 313.7278 | 549.7579 | 366.0244
557.3479 | 504.5249 | 314.5208 | 551.3584 | 366.1205
558.3479 | 505.0091 | 316.0213 | 552.5637 | 366.9174
559.3479 | 505.137 | 318.3627 | 553.0536 | 366.2177
560.3479 | 507.5186 | 321.0501 | 555.7746 | 366.4267
561.3479 | 509.9789 | 323.7567 | 560.0455 | 368.0545
562.3479 | 513.0416 | 325.9923 | 559.4582 | 368.8242
563.3479 | 512.1123 | 327.2804 | 558.7818 | 368.7824
564.3479 | 517.5903 | 327.1527 | 564.5085 | 371.0291
565.3479 | 520.9566 | 327.927 | 563.3468 | 373.9823
566.3635 | 524.9275 | 328.7772 | 560.0487 | 378.6222
567.3479 | 526.4341 | 329.6922 | 564.8487 | 383.4688
568.3479 | 527.9341 | 331.8001 | 569.3561 | 387.0861
569.3479 | 528.645 | 332.5218 | 565.5646 | 387.4646
570.3479 | 529.6552 | 335.6647 | 567.6756 | 388.4215
571.3479 | 530.2614 | 337.0934 | 571.5693 | 389.2101
572.3479 | 529.2457 | 338.8257 | 580.3464 | 395.9938
573.3479 | 530.5596 | 338.2916 | 583.9599 | 395.4405
574.3479 | 531.3184 | 339.5886 | 580.8529 | 399.5458
575.3479 | 531.8158 | 340.5468 | 587.3069 | 399.58
576.3479 | 531.0564 | 340.0973 | 584.1498 | 398.7285
577.3479 | 528.5577 | 339.0487 | 583.0658 | 403.3994
578.3479 | 529.1813 | 337.0961 | 584.2486 | 404.1423
579.3479 | 528.4069 | 341.6011 | 583.2806 | 404.4372
580.3479 | 530.4562 | 341.2646 | 587.22 | 403.2984
581.3479 | 532.1389 | 342.7294 | 587.6856 | 405.9461
582.3479 | 530.2704 | 344.3914 | 584.0798 | 404.9968
583.3479 | 530.6221 | 343.2991 | 584.8847 | 402.3497
584.3479 | 533.7981 | 346.9251 | 587.7371 | 401.2344
585.3479 | 536.0674 | 347.0262 | 588.3357 | 399.1285
586.3479 | 537.5574 | 348.2395 | 592.9066 | 396.7895
587.3479 | 540.2139 | 347.7395 | 597.6727 | 398.8429
588.3479 | 542.3608 | 347.419 | 598.4445 | 396.8312
589.3479 | 544.3909 | 349.7716 | 601.2519 | 395.374
590.3479 | 546.3358 | 350.4331 | 601.2562 | 394.2255
591.3479 | 549.3063 | 353.325 | 599.3257 | 392.0251
592.3479 | 550.7356 | 354.0848 | 598.925 | 392.3254
593.3479 | 553.1997 | 355.6588 | 601.4059 | 394.9463
594.3479 | 556.511 | 355.1756 | 603.1734 | 395.9215
595.3479 | 558.1507 | 355.8788 | 601.3678 | 395.656
596.3635 | 560.6536 | 356.5266 | 599.9106 | 395.4184
597.3479 | 560.9631 | 363.2296 | 602.2829 | 393.4463
598.3479 | 560.7041 | 365.9104 | 601.2081 | 392.2743
599.3479 | 560.9803 | 369.1467 | 595.7325 | 391.8996
600.3479 | 561.8036 | 369.1541 | 596.6804 | 391.5034
601.3479 | 560.6721 | 369.6307 | 594.8481 | 391.0846
602.3479 | 557.6992 | 369.9933 | 599.1016 | 394.3084
603.3479 | 556.5728 | 370.0032 | 597.2567 | 392.9723
604.3479 | 555.4974 | 369.2862 | 595.168 | 395.5956
605.3479 | 557.9367 | 370.3134 | 601.9694 | 395.1232
606.3479 | 557.6763 | 370.8203 | 599.2543 | 398.2785
607.3479 | 558.3413 | 371.8164 | 603.462 | 398.0296
608.3479 | 558.4499 | 370.4298 | 598.9815 | 396.8014
609.3479 | 557.0139 | 368.9974 | 598.3274 | 395.6203
610.3479 | 556.6512 | 372.6724 | 598.7044 | 398.3405
611.3479 | 555.0775 | 371.0994 | 599.2035 | 399.8835
612.3479 | 558.0492 | 370.0399 | 602.0528 | 400.2473
613.3479 | 556.8158 | 368.537 | 599.1731 | 398.5337
614.3479 | 557.0881 | 370.6999 | 601.6773 | 399.2553
615.3479 | 557.0233 | 377.0665 | 605.2033 | 398.1672
616.3479 | 559.3339 | 376.8722 | 606.8632 | 397.6733
617.3479 | 562.6688 | 377.2198 | 608.619 | 398.4548
618.3479 | 563.0908 | 375.5379 | 610.1154 | 401.0655
619.3479 | 563.0581 | 374.1618 | 612.3174 | 403.317
620.3479 | 562.5614 | 374.8841 | 609.2851 | 404.2093
621.3479 | 562.5138 | 376.8329 | 611.6504 | 403.5022
622.3479 | 559.8306 | 377.463 | 612.7889 | 402.8373
623.3479 | 557.1503 | 379.6637 | 611.3048 | 404.6122
624.3479 | 558.5409 | 380.2503 | 605.077 | 403.375
625.3479 | 559.7056 | 383.4795 | 605.0627 | 401.538
626.3479 | 560.9403 | 385.8447 | 605.7752 | 400.9474
627.3479 | 560.613 | 386.268 | 607.9325 | 401.3757
628.3479 | 557.171 | 384.9385 | 606.6395 | 400.1776
629.3479 | 556.9074 | 386.3581 | 613.6442 | 401.1667
630.3479 | 559.327 | 384.861 | 618.1006 | 399.9819
631.3479 | 557.6976 | 385.7275 | 623.1423 | 399.1972
632.3479 | 557.3061 | 388.7197 | 619.4591 | 398.0461
633.3479 | 554.7504 | 388.9152 | 624.0496 | 397.2548
634.3479 | 555.3609 | 389.5371 | 625.5584 | 397.2221
635.3479 | 557.329 | 392.4683 | 628.7942 | 395.6946
636.3479 | 565.9799 | 394.3932 | 624.7093 | 394.6351
637.3479 | 567.1282 | 394.3905 | 617.8712 | 394.435
638.3479 | 565.2402 | 395.184 | 616.4526 | 393.8304
639.3479 | 563.0145 | 396.1181 | 614.9149 | 398.3097
640.3479 | 562.6739 | 394.2998 | 618.5246 | 398.8065
641.3479 | 562.9361 | 393.8548 | 612.9908 | 399.1184
642.3479 | 562.339 | 391.4846 | 611.0955 | 398.026
643.3479 | 565.3794 | 390.1136 | 612.6322 | 398.277
644.3479 | 566.2209 | 388.0243 | 614.8175 | 403.2309
645.3479 | 567.0696 | 387.794 | 614.0108 | 406.6521
646.3479 | 566.7779 | 385.6008 | 614.067 | 404.849
647.3479 | 565.0339 | 385.3334 | 610.0373 | 402.4625
648.3479 | 564.3585 | 386.8103 | 615.9973 | 401.03
649.3479 | 567.6624 | 387.4127 | 616.5288 | 400.3301
650.3479 | 567.6137 | 388.3225 | 617.6478 | 400.3727
651.3479 | 568.7386 | 389.1816 | 615.9475 | 400.4676
652.3479 | 568.6172 | 387.6886 | 616.8771 | 400.3026
653.3479 | 571.8127 | 389.6189 | 613.7775 | 398.7474
654.3479 | 572.7396 | 392.2603 | 611.6076 | 396.7823
655.3479 | 573.2028 | 390.6853 | 608.4749 | 396.1594
656.3479 | 571.8052 | 392.2935 | 611.6338 | 396.149
657.3479 | 573.3395 | 393.9335 | 612.4554 | 395.2837
658.3479 | 574.1179 | 398.0033 | 612.5403 | 395.3452
659.3479 | 580.7061 | 398.8439 | 616.206 | 393.5856
660.3479 | 584.8799 | 397.9543 | 614.4449 | 392.6114
661.3479 | 587.1401 | 398.5695 | 613.7358 | 391.0705
662.3479 | 588.5901 | 398.909 | 612.0038 | 390.5341
663.3479 | 592.4247 | 398.0208 | 613.2062 | 390.6106
664.3479 | 600.5961 | 396.5412 | 611.7355 | 393.3594
665.3479 | 597.0586 | 395.6113 | 605.3917 | 392.3947
666.3479 | 590.8216 | 393.514 | 608.6772 | 397.242
667.3479 | 594.2098 | 395.4842 | 616.314 | 396.4272
668.3479 | 592.8803 | 394.54 | 613.348 | 395.4114
669.3479 | 591.1431 | 393.0701 | 612.5309 | 394.7867
670.3479 | 587.7631 | 392.4264 | 618.3931 | 395.0455
671.3479 | 589.6293 | 394.1666 | 616.573 | 395.9469
672.3479 | 585.5784 | 393.1714 | 615.9435 | 396.1623
673.3479 | 589.9478 | 390.8388 | 615.2022 | 396.3009
674.3479 | 590.0538 | 391.6707 | 611.5808 | 394.7524
675.3479 | 591.638 | 393.8453 | 605.6708 | 394.6807
676.3479 | 591.9106 | 393.3443 | 602.7904 | 393.7778
677.3479 | 598.5443 | 393.0216 | 600.1168 | 391.8836
678.3479 | 593.9778 | 391.5573 | 609.276 | 392.6784
679.3479 | 589.4526 | 390.134 | 619.698 | 392.723
680.3479 | 588.8133 | 388.4557 | 620.8322 | 392.8238
681.3479 | 588.5755 | 385.7298 | 616.0132 | 393.7356
682.3479 | 583.6108 | 385.8009 | 621.9857 | 393.5989
683.3479 | 582.0723 | 383.8998 | 628.8195 | 393.6951
684.3479 | 578.3887 | 381.9582 | 627.6326 | 391.8172
685.3479 | 578.5731 | 385.6322 | 627.1085 | 392.3386
686.3479 | 578.191 | 387.314 | 629.1025 | 391.4611
687.3479 | 581.2815 | 389.4423 | 630.6846 | 389.9472
688.3479 | 581.1325 | 389.4295 | 630.2955 | 388.5036
689.3479 | 577.4166 | 389.4782 | 635.8263 | 389.2244
690.3479 | 573.5468 | 388.1984 | 637.2405 | 388.9748
691.3479 | 572.773 | 387.0567 | 627.3114 | 388.9072
692.3479 | 572.1386 | 385.9503 | 621.8344 | 392.356
693.3479 | 568.016 | 383.5253 | 627.1747 | 392.5366
694.3479 | 564.9733 | 383.4975 | 622.244 | 392.057
695.3479 | 562.9457 | 386.1319 | 629.4344 | 390.4949
696.3479 | 559.6542 | 390.3928 | 628.0703 | 391.1029
697.3479 | 557.852 | 393.1689 | 626.7709 | 391.5361
698.3479 | 558.8795 | 391.587 | 629.8594 | 390.6085
699.3479 | 560.4497 | 392.2226 | 628.7223 | 390.0863
700.3479 | 568.8969 | 392.7455 | 622.8834 | 388.6885
701.3479 | 569.6332 | 394.2934 | 619.851 | 389.4507
702.3479 | 566.6347 | 397.1668 | 623.6504 | 390.1159
703.3479 | 563.2801 | 397.4805 | 629.3646 | 390.6375
704.3479 | 561.4899 | 396.593 | 628.7423 | 390.5895
705.3479 | 560.7585 | 399.6001 | 626.2963 | 390.5294
706.3479 | 582.5758 | 400.8683 | 625.4579 | 390.4929
707.3479 | 591.7602 | 403.4927 | 620.3831 | 389.8352
708.3479 | 587.7289 | 403.0279 | 623.2124 | 389.0408
709.3479 | 583.7249 | 402.5401 | 623.0767 | 390.5497
710.3479 | 579.6342 | 401.4428 | 628.5032 | 391.2556
711.3479 | 574.6606 | 398.4828 | 630.622 | 390.9777
712.3479 | 574.9306 | 396.5342 | 633.4594 | 391.9572
713.3479 | 572.2487 | 396.364 | 632.3577 | 391.6207
714.3479 | 570.0928 | 394.2391 | 632.6892 | 389.7309
715.3479 | 568.6645 | 398.6565 | 630.4158 | 390.5573
716.3479 | 566.3764 | 399.9003 | 628.1685 | 390.4238
717.3479 | 566.0185 | 398.3177 | 636.3457 | 391.7412
718.3479 | 568.9324 | 398.621 | 637.0385 | 391.4071
719.3479 | 570.5288 | 397.2688 | 628.0165 | 390.6843
720.3479 | 576.9252 | 399.2981 | 622.3387 | 392.093
721.3479 | 577.2675 | 402.8111 | 617.611 | 391.4499
722.3479 | 580.1606 | 403.8231 | 611.2992 | 390.354
723.3479 | 579.462 | 405.0712 | 605.872 | 391.3539
724.3479 | 577.0121 | 407.3 | 604.6414 | 390.0995
725.3479 | 575.1652 | 413.0669 | 602.7885 | 389.2201
726.3479 | 580.0571 | 414.0304 | 601.3868 | 388.0897
727.3479 | 577.6556 | 412.4579 | 593.3826 | 387.8267
728.3479 | 577.7459 | 411.9061 | 602.5481 | 388.0376
729.3479 | 575.9108 | 413.5991 | 606.608 | 389.1193
730.3479 | 573.7848 | 413.7434 | 608.1458 | 388.3868
731.3479 | 572.6728 | 414.2819 | 611.5557 | 388.8283
732.3479 | 571.0286 | 414.3551 | 610.9198 | 389.9246
733.3479 | 568.1838 | 413.7605 | 613.0012 | 391.6458
734.3479 | 566.3089 | 412.6408 | 629.298 | 395.527
735.3479 | 566.4306 | 409.6731 | 631.6304 | 397.3226
736.3479 | 566.2747 | 407.9564 | 630.109 | 397.9841
737.3479 | 567.3678 | 410.2728 | 631.8397 | 397.2871
738.3479 | 567.4438 | 408.9681 | 624.8289 | 396.4441
739.3479 | 566.0612 | 409.7069 | 627.074 | 396.3728
740.3479 | 565.8716 | 415.5153 | 622.3517 | 395.6153
741.3479 | 564.1811 | 414.9769 | 620.8093 | 395.6064
742.3479 | 565.7201 | 416.7071 | 623.4863 | 401.4619
743.3479 | 565.5804 | 417.4918 | 623.1731 | 399.6321
744.3479 | 564.1072 | 418.0818 | 616.9847 | 398.4031
745.3479 | 564.5755 | 417.1509 | 615.4936 | 400.1506
746.3479 | 564.2311 | 415.7894 | 616.6982 | 399.4765
747.3479 | 562.2907 | 413.8894 | 622.4594 | 399.2963
748.3479 | 560.5652 | 415.4611 | 629.0987 | 400.1612
749.3479 | 561.8167 | 414.9232 | 631.4199 | 400.4512
750.3479 | 559.5229 | 414.2808 | 633.2665 | 400.0303
751.3479 | 559.3459 | 412.83 | 629.9 | 397.731
752.3479 | 560.6425 | 412.8868 | 628.7034 | 397.001
753.3479 | 560.5342 | 412.9814 | 629.0964 | 396.2652
754.3479 | 572.5284 | 412.6757 | 627.1338 | 396.9666
755.3479 | 574.3829 | 416.3482 | 621.8612 | 398.7929
756.3479 | 573.8339 | 415.3992 | 618.44 | 399.5705
757.3479 | 573.5791 | 415.6963 | 618.5616 | 400.441
758.3479 | 571.5321 | 416.3332 | 634.1796 | 400.5245
759.3479 | 569.3649 | 417.4677 | 636.8188 | 399.8531
760.3479 | 566.0085 | 415.7649 | 637.0424 | 399.3473
761.3479 | 560.3113 | 413.6138 | 644.7025 | 397.6397
762.3479 | 557.2339 | 412.1753 | 649.1093 | 395.851
763.3479 | 557.6712 | 412.5258 | 656.4976 | 396.0174
764.3479 | 555.6879 | 412.481 | 657.7434 | 396.5188
765.3479 | 553.6685 | 411.773 | 653.1807 | 398.715
766.3479 | 550.9805 | 412.6624 | 647.8486 | 400.4665
767.3479 | 549.1279 | 411.5404 | 654.8634 | 399.7056
768.3479 | 548.9544 | 412.0683 | 657.9214 | 399.3502
769.3479 | 551.3951 | 415.4575 | 656.091 | 398.4892
770.3479 | 551.8822 | 414.9971 | 653.5101 | 400.8117
771.3479 | 553.0629 | 416.885 | 656.325 | 399.399
772.3479 | 552.8592 | 417.8839 | 652.2158 | 400.1601
773.3479 | 551.8246 | 417.7147 | 652.1523 | 399.1419
774.3479 | 551.6981 | 419.0999 | 657.2949 | 399.7412
775.3479 | 552.7847 | 419.1176 | 662.9876 | 399.0867
776.3479 | 555.4795 | 418.9949 | 659.6067 | 398.7087
777.3479 | 558.4208 | 419.0909 | 658.8225 | 399.6712
778.3479 | 559.9763 | 419.4544 | 656.5824 | 399.4523
779.3479 | 560.693 | 421.0192 | 663.0434 | 400.7399
780.3479 | 557.9635 | 419.3072 | 659.0613 | 399.8568
781.3479 | 555.4737 | 416.1973 | 669.1445 | 401.5071
782.3479 | 555.0447 | 416.1673 | 667.5261 | 400.6682
783.3479 | 551.0013 | 414.6587 | 666.5488 | 401.4935
784.3479 | 548.8095 | 416.1772 | 663.739 | 402.0214
785.3479 | 550.147 | 415.2141 | 669.1706 | 403.1277
786.3479 | 551.1632 | 414.0071 | 674.189 | 403.0058
787.3479 | 551.6522 | 415.8966 | 669.9045 | 402.6894
788.3479 | 551.0504 | 420.1982 | 666.859 | 405.2247
789.3479 | 554.087 | 420.3772 | 659.348 | 404.8755
790.3479 | 556.6815 | 420.1978 | 659.9887 | 404.4771
791.3479 | 558.5434 | 421.5454 | 657.6201 | 403.4674
792.3479 | 558.5389 | 420.815 | 661.8726 | 402.8104
793.3479 | 558.6511 | 421.9063 | 660.3898 | 402.7501
794.3479 | 560.6974 | 421.1027 | 661.2212 | 404.1703
795.3479 | 563.2615 | 422.8804 | 663.8378 | 404.0567
796.3479 | 567.2207 | 424.7598 | 667.2563 | 403.0614
797.3479 | 568.182 | 432.1073 | 661.6652 | 402.7298
798.3479 | 568.0036 | 431.7213 | 673.8907 | 401.5731
799.3479 | 574.7509 | 431.6406 | 667.2229 | 400.5261
800.3479 | 581.0564 | 432.2153 | 669.3306 | 399.5991
801.3479 | 583.1679 | 433.7369 | 668.1192 | 402.8796
802.3479 | 584.1964 | 433.6391 | 670.2919 | 404.3832
803.3479 | 582.2181 | 434.1206 | 663.1772 | 404.3819
804.3479 | 580.4211 | 435.3786 | 662.5837 | 405.61
805.3479 | 579.1605 | 432.5128 | 655.6552 | 404.5544
806.3479 | 578.4618 | 431.9269 | 653.0362 | 404.667
807.3479 | 578.7925 | 430.502 | 655.0695 | 405.0139
808.3479 | 580.4406 | 430.1224 | 655.1469 | 404.5727
809.3479 | 583.1074 | 429.428 | 653.1816 | 403.6656
810.3479 | 581.7471 | 432.3478 | 655.6026 | 408.0144
811.3479 | 582.3358 | 431.3753 | 660.5131 | 409.5231
812.3479 | 582.7682 | 432.0271 | 665.3217 | 407.7857
813.3479 | 583.2853 | 432.6072 | 663.7465 | 407.2647
814.3479 | 583.9884 | 433.2748 | 662.0827 | 407.3913
815.3479 | 584.2222 | 431.7961 | 656.5134 | 406.7248
816.3479 | 585.8048 | 432.7556 | 664.1741 | 405.7633
817.3479 | 586.102 | 432.6503 | 663.6536 | 405.3007
818.3479 | 584.2545 | 432.8347 | 663.9133 | 403.6635
819.3479 | 582.6116 | 430.4605 | 668.1357 | 404.3116
820.3479 | 582.4347 | 429.8426 | 664.8536 | 403.9368
821.3479 | 581.6848 | 429.4823 | 662.3142 | 404.1869
822.3479 | 582.4205 | 428.5595 | 661.9327 | 405.5383
823.3479 | 584.6778 | 426.4741 | 666.0211 | 405.3449
824.3479 | 586.9352 | 425.4627 | 662.3227 | 408.2081
825.3479 | 587.0077 | 423.8862 | 662.4919 | 410.451
826.3479 | 588.6664 | 423.2038 | 664.6382 | 415.7207
827.3479 | 589.6368 | 421.3074 | 659.335 | 417.4984
828.3479 | 591.0155 | 418.782 | 654.0568 | 419.264
829.3479 | 592.4499 | 420.9102 | 659.6681 | 418.2671
830.3479 | 592.6459 | 419.752 | 660.0305 | 419.3905
831.3479 | 593.3691 | 422.8017 | 655.9813 | 418.5145
832.3479 | 592.3151 | 423.7262 | 655.5508 | 417.9833
833.3479 | 590.6868 | 427.0522 | 660.8569 | 419.6396
834.3479 | 593.6246 | 426.4895 | 661.6325 | 419.1074
835.3479 | 595.9219 | 426.5132 | 656.3046 | 419.9018
836.3479 | 595.5698 | 426.689 | 651.0455 | 418.0144
837.3479 | 594.9905 | 426.9958 | 651.3149 | 418.0502
838.3479 | 596.2447 | 431.0232 | 645.37 | 418.4756
839.3479 | 596.5122 | 433.9044 | 642.3977 | 416.7485
840.3479 | 596.2703 | 434.9283 | 641.626 | 418.7491
841.3479 | 596.0321 | 435.738 | 640.4609 | 417.6844
842.3479 | 594.2565 | 435.3235 | 638.2096 | 417.5842
843.3479 | 591.4649 | 433.481 | 643.6377 | 417.6829
844.3479 | 588.0663 | 434.3779 | 641.996 | 417.4462
845.3479 | 583.3562 | 435.4836 | 647.2867 | 415.3043
846.3479 | 580.5618 | 438.3984 | 644.165 | 411.9333
847.3479 | 583.6052 | 443.2141 | 655.0694 | 412.4119
848.3479 | 581.7786 | 445.2553 | 654.6307 | 412.6976
849.3479 | 581.138 | 447.0868 | 653.4953 | 413.0722
850.3479 | 579.8011 | 448.3125 | 656.8596 | 410.0657
851.3479 | 577.7005 | 448.0093 | 665.0174 | 408.8517
852.3479 | 577.0568 | 445.5934 | 664.2121 | 408.5957
853.3479 | 576.972 | 446.6789 | 662.8364 | 411.8745
854.3479 | 577.6527 | 444.5495 | 656.4705 | 411.845
855.3479 | 577.8043 | 445.6199 | 653.7195 | 410.5234
856.3479 | 579.9836 | 443.5393 | 651.6911 | 418.0164
857.3479 | 581.3735 | 441.7745 | 654.4866 | 416.2952
858.3479 | 579.1902 | 442.0823 | 650.2787 | 416.171
859.3479 | 577.9848 | 441.0797 | 655.8132 | 416.593
860.3479 | 579.9051 | 441.3791 | 655.0171 | 416.2914
861.3479 | 583.2968 | 438.9141 | 658.2651 | 417.5247
862.3479 | 585.3158 | 440.1995 | 658.7948 | 414.7659
863.3479 | 583.9055 | 440.8503 | 658.6312 | 413.7225
864.3479 | 583.9418 | 439.7175 | 671.4394 | 412.517
865.3479 | 586.5984 | 439.0047 | 665.0229 | 411.1816
866.3479 | 588.8621 | 438.4202 | 650.6754 | 408.7904
867.3479 | 590.43 | 440.2801 | 647.1496 | 407.5996
868.3479 | 591.3277 | 439.5114 | 643.1982 | 406.5312
869.3479 | 593.4573 | 444.6482 | 652.352 | 406.0683
870.3479 | 592.8929 | 443.339 | 653.7212 | 405.3427
871.3479 | 593.3169 | 444.5096 | 650.0854 | 405.5143
872.3479 | 593.3777 | 446.3632 | 653.0935 | 404.9655
873.3479 | 594.1681 | 444.9842 | 646.505 | 404.6959
874.3479 | 593.0319 | 445.2605 | 642.5433 | 403.7802
875.3635 | 594.0224 | 444.555 | 646.6236 | 404.8996
876.3479 | 593.7014 | 444.3205 | 645.7269 | 404.5501
877.3479 | 594.9565 | 441.657 | 643.8564 | 403.7909
878.3479 | 596.0914 | 439.8285 | 638.3578 | 403.984
879.3479 | 596.5975 | 441.504 | 631.0101 | 403.346
880.3479 | 598.8453 | 443.0792 | 638.4586 | 404.4724
881.3479 | 602.8439 | 443.5926 | 634.5535 | 403.4664
882.3479 | 604.5817 | 443.0976 | 638.3973 | 403.1515
883.3479 | 603.1893 | 447.6266 | 639.1107 | 402.4531
884.3479 | 601.2361 | 447.1898 | 646.3825 | 402.2924
885.3479 | 601.2452 | 446.3191 | 644.4101 | 403.8045
886.3479 | 604.3258 | 444.7283 | 647.1519 | 402.2931
887.3479 | 605.4049 | 444.9098 | 642.2227 | 402.0106
888.3479 | 604.5656 | 448.1207 | 652.1635 | 402.3271
889.3479 | 604.2487 | 451.224 | 657.8524 | 402.4335
890.3479 | 606.7706 | 449.697 | 652.3786 | 403.4404
891.3479 | 607.3218 | 448.8594 | 655.6802 | 403.392
892.3479 | 606.267 | 447.4492 | 661.4413 | 403.9259
893.3479 | 601.9232 | 448.2614 | 653.7768 | 403.6377
894.3479 | 600.5958 | 444.6442 | 659.7373 | 402.4355
895.3479 | 600.3495 | 442.6745 | 661.475 | 401.6558
896.3479 | 599.5947 | 442.3083 | 670.5191 | 406.0905
897.3479 | 601.5888 | 442.3371 | 670.7915 | 406.1971
898.3479 | 604.037 | 443.4445 | 666.286 | 409.7328
899.3479 | 606.2745 | 442.8906 | 662.1221 | 411.7607
900.3479 | 604.4671 | 444.028 | 660.1495 | 410.8506
901.3479 | 605.1157 | 443.3993 | 658.0671 | 413.1613
902.3479 | 604.663 | 443.7398 | 659.8373 | 410.6673
903.3479 | 601.691 | 443.2769 | 653.6064 | 409.0406
904.3479 | 601.1704 | 445.9414 | 646.3697 | 408.7496
905.3479 | 600.2454 | 445.6978 | 643.0304 | 408.3814
906.3479 | 596.9334 | 450.5186 | 645.7615 | 407.0255
907.3479 | 592.3202 | 450.7024 | 637.5609 | 405.2773
908.3479 | 586.916 | 452.0599 | 633.993 | 403.6437
909.3479 | 581.3051 | 450.7041 | 644.0667 | 402.7377
910.3479 | 577.4967 | 450.5865 | 647.5406 | 402.3181
911.3479 | 580.6976 | 449.5712 | 648.5613 | 401.5045
912.3479 | 582.5818 | 447.8106 | 650.5127 | 400.378
913.3479 | 582.4648 | 448.1316 | 652.1141 | 401.592
914.3479 | 581.7833 | 445.7067 | 659.1909 | 405.3622
915.3479 | 579.0748 | 443.6469 | 652.8492 | 404.7839
916.3479 | 579.9976 | 449.4369 | 660.0925 | 405.2913
917.3479 | 579.3509 | 452.4561 | 664.7125 | 404.4534
918.3479 | 578.721 | 453.666 | 678.3307 | 407.0938
919.3479 | 578.29 | 453.8284 | 672.9971 | 406.3255
920.3479 | 580.1058 | 453.9132 | 673.9898 | 407.9871
921.3479 | 581.4049 | 455.7068 | 669.585 | 407.1441
922.3479 | 584.0221 | 459.4999 | 671.3404 | 406.4902
923.3479 | 584.9179 | 458.8006 | 670.7373 | 407.1249
924.3479 | 593.4226 | 457.1456 | 669.7705 | 406.966
925.3479 | 597.6253 | 459.028 | 669.7964 | 407.4362
926.3479 | 599.1412 | 461.5146 | 668.8109 | 406.068
927.3479 | 600.6108 | 461.8978 | 666.0673 | 406.817
928.3479 | 601.7601 | 458.34 | 669.0538 | 410.2493
929.3479 | 603.1132 | 455.9279 | 665.2962 | 411.1069
930.3479 | 601.2727 | 456.0299 | 666.5193 | 411.2276
931.3479 | 598.822 | 458.4454 | 663.3531 | 410.9942
932.3479 | 599.6375 | 460.8606 | 669.3306 | 411.2295
933.3479 | 602.0613 | 462.0079 | 668.0654 | 410.5448
934.3479 | 604.2415 | 460.5658 | 661.5619 | 414.916
935.3479 | 602.9262 | 458.3571 | 662.2482 | 416.4959
936.3479 | 602.0218 | 457.8059 | 659.9933 | 419.8227
937.3479 | 602.2886 | 456.5556 | 665.3047 | 419.9137
938.3479 | 600.6386 | 459.1881 | 660.0946 | 419.0111
939.3479 | 598.0989 | 466.3223 | 664.2533 | 420.2131
940.3479 | 598.1315 | 467.9917 | 671.3564 | 419.7972
941.3479 | 595.0059 | 466.8872 | 662.9854 | 421.0562
942.3479 | 592.2649 | 466.7989 | 653.8214 | 420.7796
943.3479 | 589.0554 | 467.9181 | 650.6586 | 419.7362
944.3479 | 588.1203 | 468.7334 | 664.4422 | 420.0625
945.3479 | 587.6006 | 467.8368 | 672.1879 | 418.9042
946.3479 | 586.5889 | 466.3251 | 675.5135 | 421.9658
947.3479 | 587.1067 | 465.9859 | 675.6626 | 422.7843
948.3479 | 590.357 | 464.3784 | 677.7159 | 423.8093
949.3479 | 590.7878 | 464.3193 | 678.5421 | 422.9691
950.3479 | 593.267 | 464.0394 | 679.0978 | 421.1797
951.3479 | 600.6249 | 467.721 | 692.1937 | 420.9642
952.3479 | 601.2138 | 465.966 | 690.8765 | 422.7515
953.3479 | 600.1611 | 468.381 | 692.6586 | 423.0561
954.3479 | 599.1763 | 470.6989 | 689.0099 | 422.999
955.3479 | 606.5654 | 473.3635 | 690.6648 | 422.8217
956.3479 | 604.7294 | 473.7079 | 685.9333 | 422.8476
957.3479 | 603.1246 | 475.9389 | 686.7913 | 424.0889
958.3479 | 604.5266 | 480.98 | 696.7306 | 424.125
959.3479 | 608.8242 | 481.9076 | 701.5113 | 426.3132
960.3479 | 609.0798 | 485.9883 | 705.63 | 427.8448
961.3479 | 609.154 | 485.6834 | 710.8018 | 428.57
962.3479 | 606.0029 | 484.7456 | 705.6658 | 427.6425
963.3479 | 602.1319 | 489.9908 | 697.5187 | 428.7519
964.3479 | 598.7249 | 495.1446 | 695.5757 | 427.6033
965.3479 | 594.6656 | 495.3472 | 692.2259 | 426.0412
966.3479 | 591.819 | 494.7773 | 688.6777 | 424.5474
967.3479 | 591.0897 | 492.3345 | 694.7768 | 424.2371
968.3479 | 591.988 | 492.2812 | 694.1706 | 423.6735
969.3479 | 589.5479 | 488.143 | 700.6323 | 422.8273
970.3479 | 587.8027 | 487.1625 | 701.7185 | 421.8883
971.3479 | 585.9353 | 487.081 | 698.2886 | 419.6284
972.3479 | 584.664 | 487.4646 | 699.1895 | 418.9997
973.3479 | 582.9742 | 489.3796 | 695.1403 | 419.4772
974.3479 | 580.5214 | 486.6602 | 691.1355 | 417.8062
975.3479 | 577.1695 | 490.3325 | 702.1211 | 416.6047
976.3479 | 579.7781 | 493.0937 | 710.9624 | 418.9986
977.3479 | 583.0942 | 497.936 | 718.3715 | 417.8972
978.3479 | 585.6967 | 496.7838 | 707.4845 | 417.9861
979.3479 | 589.3943 | 496.7357 | 704.8056 | 419.8742
980.3479 | 588.9156 | 495.4219 | 694.6032 | 420.3905
981.3479 | 587.7789 | 497.9507 | 697.1166 | 419.3958
982.3479 | 586.4271 | 500.2957 | 697.6349 | 419.397
983.3479 | 583.6432 | 499.6908 | 698.7481 | 419.0359
984.3479 | 582.1017 | 503.2446 | 698.6048 | 421.6521
985.3479 | 582.0921 | 504.9166 | 685.9058 | 422.3001
986.3479 | 585.3133 | 503.3261 | 697.0911 | 425.5585
987.3479 | 586.8273 | 503.0311 | 692.2941 | 426.2149
988.3479 | 587.785 | 505.3676 | 701.7955 | 429.5196
989.3479 | 586.5132 | 505.1956 | 701.0702 | 431.5794
990.3479 | 585.6011 | 505.3345 | 682.7997 | 430.9826
991.3479 | 587.654 | 508.4303 | 681.0497 | 433.0817
992.3479 | 589.9365 | 512.8162 | 691.3804 | 434.0717
993.3479 | 591.0597 | 517.4255 | 698.3638 | 435.5932
994.3479 | 590.8393 | 519.5189 | 690.3273 | 436.6784
995.3479 | 589.2596 | 518.1521 | 696.2506 | 435.3398
996.3479 | 590.639 | 516.256 | 695.5665 | 434.3569
997.3479 | 589.6936 | 522.5917 | 689.2742 | 434.1235
998.3479 | 588.1408 | 519.1411 | 697.3507 | 432.242
999.3479 | 592.338 | 516.5788 | 698.7615 | 432.4317
1000.3479 | 599.569 | 515.59 | 709.3654 | 433.4027
1001.3479 | 603.3155 | 511.7585 | 705.0277 | 432.4393
1002.3479 | 601.9568 | 511.8875 | 697.0364 | 429.8438
1003.3479 | 599.3721 | 511.5287 | 698.403 | 428.7594
1004.3479 | 597.3121 | 508.8502 | 700.7474 | 427.4544
1005.3479 | 593.3941 | 505.5822 | 705.802 | 425.3949
1006.3479 | 589.3734 | 505.8057 | 704.955 | 424.8335
1007.3479 | 584.0792 | 503.2021 | 707.5373 | 424.187
1008.3479 | 592.0253 | 502.9181 | 713.3802 | 423.5946
1009.3479 | 593.8547 | 500.6223 | 718.94 | 423.1686
1010.3479 | 594.2891 | 500.0181 | 724.0175 | 422.6726
1011.3479 | 596.9853 | 501.0855 | 722.4857 | 422.4201
1012.3479 | 601.1955 | 503.5622 | 722.6925 | 423.075
1013.3479 | 602.0361 | 503.3443 | 716.4585 | 423.1348
1014.3479 | 599.4972 | 503.7195 | 716.4749 | 421.7207
1015.3479 | 597.2111 | 502.7183 | 715.9431 | 422.1046
1016.3479 | 595.5133 | 504.1194 | 705.6658 | 421.8207
1017.3479 | 592.7773 | 509.1483 | 707.8189 | 423.83
1018.3479 | 589.5184 | 511.1659 | 719.1964 | 423.1097
1019.3479 | 586.5803 | 511.9627 | 713.5721 | 422.7298
1020.3479 | 589.0751 | 516.9491 | 721.752 | 423.7313
1021.3479 | 595.974 | 520.0494 | 719.6348 | 422.9362
1022.3479 | 600.1471 | 521.2489 | 713.447 | 423.0515
1023.3479 | 599.5623 | 526.3606 | 721.3791 | 423.3693
1024.3479 | 600.1305 | 528.0363 | 710.8905 | 423.9929
1025.3479 | 602.9271 | 531.7981 | 721.1178 | 424.6832
1026.3479 | 600.7895 | 534.986 | 722.7533 | 427.0315
1027.3479 | 598.6717 | 541.2829 | 720.6355 | 427.5639
1028.3479 | 597.124 | 540.7384 | 714.0092 | 426.9497
1029.3479 | 595.3435 | 542.6012 | 712.6981 | 427.6803
1030.3479 | 595.5679 | 543.6563 | 706.256 | 426.4552
1031.3479 | 594.3357 | 538.06 | 702.6114 | 425.5935
1032.3479 | 597.1626 | 537 | 702.9776 | 424.3224
1033.3479 | 594.6194 | 537.5242 | 704.0032 | 423.4942
1034.3479 | 591.3719 | 538.035 | 705.0096 | 422.4333
1035.3479 | 587.7904 | 535.6955 | 712.0569 | 421.9219
1036.3479 | 592.0949 | 535.076 | 708.9413 | 421.5434
1037.3479 | 593.2311 | 536.6006 | 715.6393 | 422.6133
1038.3479 | 597.0977 | 536.6576 | 711.7163 | 423.5072
1039.3479 | 596.851 | 538.1438 | 719.4956 | 425.5066
1040.3479 | 597.6804 | 539.2655 | 721.5323 | 428.8982
1041.3479 | 597.8073 | 539.3799 | 718.9549 | 429.2176
1042.3479 | 594.6392 | 539.4134 | 721.0141 | 429.0028
1043.3479 | 589.0707 | 543.4528 | 720.1746 | 428.5812
1044.3479 | 587.1009 | 546.5597 | 714.1839 | 431.1104
1045.3479 | 584.4857 | 550.4567 | 713.4278 | 429.1064
1046.3479 | 581.6363 | 554.0221 | 707.6218 | 429.7003
1047.3479 | 577.9017 | 557.0984 | 705.7996 | 429.03
1048.3479 | 578.7364 | 559.7943 | 709.0931 | 430.4371
1049.3479 | 577.8439 | 562.8731 | 702.2501 | 430.1553
1050.3479 | 575.2194 | 565.1336 | 705.5543 | 430.6258
1051.3479 | 574.2506 | 560.913 | 709.5008 | 430.5604
1052.3479 | 573.6021 | 562.4689 | 700.8827 | 431.9879
1053.3479 | 572.8644 | 561.5347 | 708.6376 | 434.0604
1054.3479 | 571.585 | 565.8219 | 700.3507 | 434.0716
1055.3479 | 567.3187 | 567.7621 | 695.9405 | 432.3563
1056.3479 | 565.7939 | 565.8353 | 696.4519 | 431.5556
1057.3479 | 565.1417 | 569.394 | 697.3224 | 430.9432
1058.3479 | 562.4062 | 572.7906 | 694.9623 | 429.5691
1059.3479 | 561.5966 | 574.5736 | 691.4194 | 429.4541
1060.3479 | 561.0475 | 575.1417 | 683.7278 | 429.8296
1061.3479 | 561.1034 | 571.6147 | 682.614 | 430.3646
1062.3479 | 560.1727 | 568.2018 | 679.9829 | 430.5787
1063.3479 | 559.1164 | 568.5045 | 684.8315 | 430.6523
1064.3479 | 557.8809 | 568.1848 | 686.2401 | 430.1663
1065.3479 | 557.3762 | 566.9883 | 681.0838 | 429.3493
1066.3479 | 558.8457 | 569.3289 | 677.1044 | 430.182
1067.3479 | 558.9497 | 570.8544 | 681.7209 | 430.4748
1068.3479 | 559.3105 | 573.7024 | 682.2862 | 431.2421
1069.3479 | 559.3094 | 575.1922 | 669.833 | 430.4851
1070.3479 | 558.842 | 577.9232 | 667.6203 | 429.9246
1071.3479 | 558.6924 | 584.9041 | 670.901 | 429.0836
1072.3479 | 560.6613 | 588.6029 | 682.5207 | 429.8898
1073.3479 | 562.7502 | 592.157 | 685.1942 | 431.2764
1074.3479 | 563.9295 | 597.5249 | 684.0279 | 430.677
1075.3479 | 576.686 | 589.361 | 688.5519 | 430.3072
1076.3479 | 578.1555 | 590.7421 | 684.0253 | 430.3425
1077.3479 | 576.7308 | 594.0336 | 679.1007 | 429.3871
1078.3479 | 575.8486 | 591.2 | 678.0317 | 429.8152
1079.3479 | 581.3411 | 588.7166 | 676.6045 | 431.9172
1080.3479 | 582.757 | 590.972 | 689.5966 | 433.0679
1081.3479 | 582.2627 | 591.8245 | 685.6585 | 433.6777
1082.3479 | 580.2389 | 590.6111 | 681.6224 | 432.6803
1083.3479 | 581.3934 | 590.2408 | 687.7535 | 433.1484
1084.3479 | 582.2003 | 588.6547 | 684.9154 | 433.4715
1085.3479 | 585.4211 | 585.7536 | 676.9535 | 432.9424
1086.3479 | 588.2671 | 578.1748 | 677.4074 | 431.5327
1087.3479 | 587.3857 | 575.1833 | 679.9934 | 430.2198
1088.3479 | 592.098 | 571.0987 | 673.2879 | 429.6831
1089.3479 | 596.9211 | 567.838 | 670.7857 | 430.3732
1090.3479 | 601.1194 | 569.2467 | 673.9546 | 430.1798
1091.3479 | 602.3574 | 573.9239 | 673.1032 | 430.4754
1092.3479 | 600.1226 | 581.4067 | 666.0173 | 429.8421
1093.3479 | 599.177 | 584.0086 | 675.4586 | 429.5905
1094.3479 | 606.2487 | 582.8331 | 682.1118 | 429.9395
1095.3479 | 607.4058 | 586.2045 | 677.9695 | 429.4296
1096.3479 | 607.7133 | 591.1682 | 681.4728 | 429.304
1097.3479 | 610.7477 | 589.6895 | 680.8215 | 428.4273
1098.3479 | 613.0466 | 588.8143 | 690.1919 | 428.3384
1099.3479 | 615.6109 | 585.7355 | 696.4756 | 430.1192
1100.3479 | 613.6746 | 585.1644 | 696.8214 | 431.4875
1101.3479 | 612.1243 | 583.9487 | 696.497 | 432.2459
1102.3479 | 610.1997 | 583.0507 | 698.0648 | 434.3785
1103.3479 | 606.1938 | 581.651 | 710.3399 | 433.5157
1104.3479 | 605.2891 | 583.152 | 714.2205 | 433.585
1105.3479 | 599.9836 | 583.3386 | 707.7553 | 433.7798
1106.3479 | 600.3761 | 584.3404 | 718.1738 | 433.8925
1107.3479 | 604.0823 | 586.7018 | 721.6909 | 434.0313
1108.3479 | 610.7944 | 588.2715 | 721.5529 | 434.167
1109.3479 | 612.682 | 589.168 | 720.8235 | 434.8796
1110.3479 | 613.8114 | 590.1566 | 719.4637 | 435.4436
1111.3479 | 612.8824 | 593.934 | 717.0044 | 434.9683
1112.3479 | 619.9263 | 591.5671 | 712.6207 | 435.3714
1113.3479 | 619.8522 | 589.8947 | 709.6861 | 435.4627
1114.3479 | 615.8833 | 590.6004 | 705.8115 | 435.3776
1115.3479 | 610.5997 | 597.4252 | 698.1367 | 436.444
1116.3479 | 607.9879 | 594.3606 | 699.5494 | 437.3147
1117.3479 | 606.7491 | 593.0475 | 702.967 | 436.64
1118.3479 | 603.3335 | 594.3661 | 718.4636 | 437.5855
1119.3479 | 600.7129 | 594.6197 | 711.2321 | 437.8586
1120.3479 | 595.8556 | 597.3222 | 704.2352 | 438.9489
1121.3479 | 592.547 | 598.8656 | 706.855 | 440.1821
1122.3479 | 600.9009 | 601.0833 | 714.0868 | 439.8712
1123.3479 | 602.8083 | 600.0438 | 715.1355 | 441.4835
1124.3479 | 600.7577 | 598.3285 | 702.12 | 440.9198
1125.3479 | 599.5846 | 603.4907 | 703.7136 | 440.1197
1126.3479 | 607.1096 | 606.2268 | 707.1056 | 440.4396
1127.3479 | 610.0304 | 602.8914 | 710.2458 | 441.2661
1128.3479 | 608.433 | 606.2766 | 707.5035 | 440.7099
1129.3479 | 611.2743 | 604.946 | 704.6357 | 441.3877
1130.3479 | 613.9906 | 606.2451 | 702.171 | 441.9894
1131.3479 | 615.4086 | 609.259 | 690.72 | 441.5114
1132.3479 | 614.1776 | 609.738 | 689.3676 | 441.4626
1133.3479 | 612.9132 | 618.0057 | 696.0805 | 442.0281
1134.3479 | 610.6156 | 626.2987 | 683.7549 | 442.9269
1135.3479 | 606.3204 | 626.0812 | 673.0922 | 443.6142
1136.3479 | 605.8243 | 621.4766 | 688.0302 | 445.3142
1137.3479 | 603.7069 | 624.9289 | 686.2696 | 448.062
1138.3479 | 601.9196 | 630.9167 | 685.6655 | 448.4374
1139.3479 | 600.9897 | 632.745 | 691.6385 | 449.2227
1140.3479 | 608.1761 | 631.0587 | 684.2449 | 449.2712
1141.3479 | 613.3447 | 633.5772 | 691.2059 | 452.5876
1142.3479 | 616.6549 | 634.8446 | 693.3415 | 453.8475
1143.3479 | 622.1798 | 631.33 | 686.1898 | 456.7474
1144.3479 | 622.2676 | 637.7446 | 694.0466 | 458.1133
1145.3479 | 622.3396 | 637.5373 | 686.3021 | 457.0637
1146.3479 | 625.8435 | 632.4312 | 690.9189 | 456.462
1147.3479 | 624.853 | 636.739 | 691.6064 | 456.1834
1148.3479 | 620.5559 | 637.4381 | 684.0217 | 456.6016
1149.3479 | 623.8411 | 638.8865 | 689.9799 | 456.5673
1150.3479 | 624.134 | 645.8405 | 681.7606 | 457.6338
1151.3479 | 622.2327 | 641.87 | 686.1616 | 457.0951
1152.3479 | 619.7492 | 646.6917 | 679.0222 | 459.6644
1153.3479 | 616.8168 | 646.5194 | 677.5189 | 461.4722
1154.3479 | 618.1525 | 643.5618 | 692.4553 | 461.2003
1155.3479 | 622.2114 | 645.4036 | 692.1469 | 460.9223
1156.3479 | 621.2183 | 641.7423 | 685.3307 | 460.2666
1157.3479 | 618.1922 | 639.3997 | 686.6286 | 459.6723
1158.3479 | 623.291 | 640.9359 | 697.8022 | 460.0197
1159.3479 | 629.3911 | 637.5026 | 698.6994 | 462.1265
1160.3479 | 636.1761 | 634.9276 | 694.7046 | 464.3098
1161.3479 | 637.4432 | 641.7568 | 695.8916 | 466.8418
1162.3479 | 636.7985 | 644.1298 | 697.3975 | 467.4853
1163.3479 | 638.19 | 644.5437 | 700.1235 | 467.8534
1164.3479 | 638.8531 | 645.9626 | 701.3372 | 468.3856
1165.3479 | 638.8472 | 651.5309 | 701.6031 | 471.449
1166.3479 | 643.494 | 647.9004 | 694.8695 | 470.8427
1167.3479 | 653.7777 | 648.4986 | 698.2246 | 473.0066
1168.3479 | 653.3064 | 646.1708 | 695.4706 | 474.3214
1169.3479 | 661.8779 | 646.2734 | 693.501 | 474.3268
1170.3479 | 656.2656 | 649.2042 | 685.803 | 474.9411
1171.3479 | 656.9678 | 648.9886 | 680.6924 | 475.0979
1172.3479 | 652.0746 | 644.9162 | 681.1444 | 475.9112
1173.3479 | 652.9878 | 647.0284 | 681.7315 | 474.5647
1174.3479 | 655.5519 | 648.8033 | 670.0457 | 472.7806
1175.3479 | 652.5362 | 644.475 | 669.8448 | 471.6983
1176.3479 | 651.1751 | 644.2398 | 677.0086 | 470.8001
1177.3479 | 652.9491 | 644.5514 | 677.4925 | 470.4866
1178.3479 | 652.7836 | 651.7232 | 676.493 | 472.783
1179.3479 | 651.4213 | 648.5813 | 676.9215 | 470.2724
1180.3479 | 647.7035 | 646.1074 | 674.0747 | 470.2481
1181.3479 | 649.9602 | 648.5061 | 687.5277 | 468.2503
1182.3479 | 651.4885 | 648.9168 | 687.2261 | 469.3881
1183.3479 | 656.7196 | 646.917 | 682.5854 | 470.5589
1184.3479 | 660.451 | 649.6875 | 675.9314 | 470.9344
1185.3479 | 659.3939 | 651.8799 | 682.0152 | 473.3066
1186.3479 | 656.0193 | 660.1393 | 676.1919 | 471.9007
1187.3479 | 661.0909 | 658.44 | 682.3108 | 470.9712
1188.3479 | 661.5894 | 656.554 | 685.2563 | 472.2359
1189.3479 | 669.93 | 650.2029 | 676.0313 | 472.3695
1190.3479 | 673.0548 | 646.8561 | 680.3974 | 471.501
1191.3479 | 673.2645 | 643.4 | 682.8891 | 471.5999
1192.3479 | 673.6523 | 643.2942 | 694.0147 | 470.9381
1193.3479 | 672.3203 | 640.0717 | 696.3985 | 469.7874
1194.3479 | 669.0393 | 641.2557 | 687.5675 | 469.6696
1195.3479 | 666.835 | 645.3878 | 693.815 | 469.4345
1196.3479 | 662.6406 | 645.9182 | 682.0796 | 469.3937
1197.3479 | 663.6003 | 648.9901 | 673.6519 | 470.7504
1198.3479 | 659.9035 | 650.3846 | 669.1219 | 469.9412
1199.3479 | 651.2255 | 652.112 | 678.1018 | 467.5362
1200.3479 | 656.3215 | 650.204 | 684.3347 | 466.4242
1201.3479 | 654.5802 | 648.5753 | 682.8852 | 466.0978
1202.3479 | 655.321 | 646.832 | 674.2959 | 465.4466
1203.3479 | 655.8771 | 645.744 | 674.9558 | 467.6485
1204.3479 | 660.7702 | 648.6823 | 674.5761 | 471.5867
1205.3479 | 661.9262 | 648.6436 | 671.1805 | 472.8183
1206.3479 | 665.8481 | 649.3599 | 676.8313 | 473.3452
1207.3479 | 671.5465 | 651.9453 | 672.227 | 472.8372
1208.3479 | 674.009 | 649.3149 | 661.5013 | 475.4578
1209.3479 | 672.6031 | 653.2436 | 668.9213 | 476.5214
1210.3479 | 670.9169 | 651.5785 | 673.6939 | 478.0904
1211.3479 | 668.8609 | 656.5912 | 665.3732 | 479.629
1212.3479 | 670.5619 | 659.6288 | 661.9069 | 482.6436
1213.3479 | 669.7946 | 664.7414 | 667.9854 | 484.0778
1214.3479 | 666.9374 | 671.2471 | 660.6261 | 484.9769
1215.3479 | 665.2733 | 674.663 | 654.9753 | 483.2486
1216.3479 | 665.2159 | 674.2797 | 654.8259 | 482.8359
1217.3479 | 665.6968 | 682.091 | 657.0848 | 481.2994
1218.3479 | 665.8011 | 681.8833 | 659.4384 | 479.4225
1219.3479 | 665.7991 | 674.5565 | 671.9828 | 479.843
1220.3479 | 666.6081 | 675.2665 | 669.8726 | 479.0763
1221.3479 | 667.3328 | 674.742 | 668.5893 | 480.0782
1222.3479 | 667.3726 | 679.0124 | 665.246 | 477.98
1223.3479 | 668.9031 | 671.8469 | 670.5271 | 479.9445
1224.3479 | 670.7135 | 670.4598 | 675.7597 | 477.2578
1225.3479 | 674.1969 | 668.9694 | 679.0438 | 477.7639
1226.3479 | 675.002 | 667.5752 | 684.8986 | 478.8563
1227.3479 | 678.6253 | 665.9831 | 683.1136 | 480.1465
1228.3479 | 678.5845 | 660.3896 | 685.0272 | 479.1208
1229.3479 | 678.1774 | 668.7515 | 680.3438 | 478.2185
1230.3479 | 677.7321 | 674.1368 | 678.8013 | 477.5294
1231.3479 | 681.8045 | 668.8213 | 677.0611 | 476.5437
1232.3479 | 684.3178 | 661.9043 | 668.7883 | 477.2241
1233.3479 | 685.1958 | 652.0935 | 672.424 | 477.2719
1234.3479 | 684.7959 | 650.4606 | 682.4516 | 478.0317
1235.3479 | 686.5239 | 657.6076 | 690.7333 | 478.2622
1236.3479 | 684.4206 | 659.1158 | 683.5929 | 479.4488
1237.3479 | 679.503 | 663.9537 | 691.172 | 480.4646
1238.3479 | 676.632 | 663.8807 | 686.0869 | 480.1139
1239.3479 | 675.8472 | 663.6944 | 683.9844 | 485.1732
1240.3479 | 674.2961 | 668.1926 | 687.7918 | 483.638
1241.3479 | 673.5385 | 677.8606 | 678.1644 | 483.5398
1242.3479 | 675.1303 | 676.167 | 669.652 | 483.6474
1243.3479 | 677.5945 | 675.3791 | 665.6295 | 487.8434
1244.3479 | 678.6362 | 677.3425 | 676.2212 | 489.0812
1245.3479 | 676.5808 | 681.7626 | 671.2775 | 488.0883
1246.3479 | 676.1496 | 682.7445 | 664.4021 | 488.727
1247.3479 | 678.1155 | 674.2945 | 665.2744 | 487.6618
1248.3479 | 677.477 | 679.6836 | 659.4512 | 489.8369
1249.3479 | 680.01 | 673.0688 | 658.6015 | 488.8599
1250.3479 | 678.5706 | 675.2017 | 652.1552 | 487.4811
1251.3479 | 678.0409 | 671.2373 | 641.7531 | 486.1695
1252.3479 | 680.1378 | 672.5076 | 635.1192 | 486.7757
1253.3479 | 679.0719 | 666.4193 | 647.614 | 486.1476
1254.3479 | 678.0583 | 668.8427 | 646.9825 | 485.8429
1255.3479 | 676.9616 | 674.6568 | 640.5198 | 483.6135
1256.3479 | 676.2252 | 675.6246 | 637.7847 | 480.5733
1257.3479 | 678.6061 | 677.836 | 633.5004 | 483.0449
1258.3479 | 676.1931 | 672.4733 | 628.8653 | 482.9594
1259.3479 | 679.9837 | 671.1038 | 631.8654 | 483.3702
1260.3479 | 678.4259 | 678.0435 | 628.4472 | 483.3019
1261.3479 | 677.6626 | 688.3945 | 635.4917 | 481.8181
1262.3479 | 680.0856 | 683.3571 | 645.4056 | 484.8905
1263.3479 | 676.8708 | 678.538 | 638.1803 | 483.2569
1264.3479 | 674.0561 | 687.7158 | 630.2144 | 482.76
1265.3479 | 677.1447 | 692.5487 | 629.0797 | 481.7121
1266.3479 | 676.3738 | 692.9056 | 623.5611 | 483.3321
1267.3479 | 674.2848 | 694.5424 | 621.2092 | 483.4236
1268.3479 | 672.8043 | 701.3881 | 624.2674 | 483.3721
1269.3479 | 674.5462 | 698.9958 | 621.1257 | 484.6588
1270.3479 | 670.3767 | 694.7746 | 614.5724 | 484.3912
1271.3479 | 671.5991 | 688.9775 | 623.5178 | 486.7347
1272.3479 | 670.6447 | 689.2642 | 629.0898 | 484.9634
1273.3479 | 670.3259 | 693.9257 | 642.6037 | 486.6894
1274.3479 | 671.8865 | 699.2141 | 644.0776 | 489.7931
1275.3479 | 671.7496 | 697.7513 | 654.0434 | 489.6326
1276.3479 | 671.4609 | 698.4864 | 650.6638 | 488.907
1277.3479 | 671.7497 | 697.9662 | 642.4647 | 488.0871
1278.3479 | 672.3764 | 700.9858 | 643.0511 | 487.6055
1279.3479 | 672.9518 | 697.3459 | 646.4799 | 486.6471
1280.3479 | 672.9085 | 700.2555 | 648.3144 | 488.1121
1281.3479 | 676.3068 | 699.4346 | 659.7873 | 488.3477
1282.3479 | 676.9153 | 700.7155 | 668.3122 | 488.5103
1283.3479 | 677.3572 | 697.9565 | 670.0838 | 490.6842
1284.3479 | 677.0833 | 697.7694 | 685.0792 | 491.6053
1285.3479 | 677.6837 | 697.2974 | 688.1361 | 489.7454
1286.3479 | 683.9162 | 689.3966 | 688.2235 | 492.0057
1287.3479 | 684.5896 | 686.9618 | 689.9264 | 491.1043
1288.3479 | 687.0086 | 690.5692 | 695.268 | 491.1944
1289.3479 | 687.7764 | 700.5807 | 687.9692 | 490.5234
1290.3479 | 686.2536 | 700.62 | 688.0004 | 492.1637
1291.3479 | 685.9269 | 700.7497 | 684.3294 | 493.4055
1292.3479 | 685.1132 | 694.5947 | 685.249 | 496.1207
1293.3479 | 684.2893 | 687.4768 | 682.2536 | 493.3921
1294.3479 | 684.1486 | 689.0752 | 686.4081 | 493.0623
1295.3479 | 682.3864 | 689.7442 | 688.4017 | 491.6181
1296.3479 | 682.5759 | 686.7169 | 685.6267 | 490.406
1297.3479 | 682.5747 | 683.9438 | 688.3434 | 490.5108
1298.3479 | 681.3035 | 692.1939 | 691.0613 | 490.647
1299.3479 | 680.8214 | 693.8472 | 682.883 | 493.4166
1300.3479 | 683.0804 | 690.2682 | 670.7435 | 495.2393
1301.3479 | 684.171 | 691.2278 | 673.5439 | 495.5504
1302.3479 | 685.1985 | 694.9082 | 661.5113 | 495.8841
1303.3479 | 684.1811 | 686.1918 | 650.5003 | 496.4046
1304.3479 | 689.8632 | 684.6863 | 643.4042 | 496.4878
1305.3479 | 687.0698 | 677.5458 | 638.9626 | 498.8378
1306.3479 | 685.4865 | 683.3932 | 632.6367 | 499.1866
1307.3479 | 684.5842 | 677.6665 | 623.7288 | 497.057
1308.3479 | 683.0364 | 669.9686 | 617.273 | 495.1072
1309.3479 | 682.6045 | 679.1426 | 622.2406 | 497.4895
1310.3479 | 680.2422 | 685.9143 | 628.078 | 500.9411
1311.3479 | 678.1424 | 687.8856 | 633.1171 | 501.4872
1312.3479 | 676.2608 | 698.712 | 630.9641 | 502.0652
1313.3479 | 678.7091 | 708.9117 | 626.44 | 499.9152
1314.3479 | 679.2495 | 707.0777 | 622.3128 | 499.7609
1315.3479 | 680.419 | 711.8165 | 622.1432 | 498.4182
1316.3479 | 680.4168 | 718.0113 | 620.893 | 500.86
1317.3479 | 679.9544 | 720.1471 | 618.4717 | 501.0168
1318.3479 | 679.4086 | 712.7395 | 611.5569 | 502.933
1319.3479 | 677.2625 | 712.8274 | 604.6145 | 513.8425
1320.3479 | 674.7873 | 711.3421 | 612.5014 | 514.9805
1321.3479 | 674.6996 | 723.069 | 617.4719 | 515.2813
1322.3479 | 674.4954 | 727.3288 | 622.6283 | 514.298
1323.3479 | 672.6423 | 727.4856 | 629.4973 | 515.5057
1324.3479 | 671.8286 | 727.1333 | 625.7943 | 519.9185
1325.3479 | 669.8489 | 722.3384 | 621.5164 | 520.83
1326.3479 | 668.0774 | 714.8308 | 616.3673 | 518.4045
1327.3479 | 669.1569 | 719.7156 | 611.2713 | 518.4295
1328.3479 | 669.3365 | 716.8335 | 607.9008 | 519.1348
1329.3479 | 669.7963 | 708.8797 | 606.6015 | 516.5363
1330.3479 | 668.6005 | 719.216 | 607.8964 | 518.1976
1331.3479 | 667.0505 | 720.9513 | 612.8655 | 523.3548
1332.3479 | 666.333 | 728.9485 | 611.6344 | 524.3084
1333.3479 | 667.0634 | 731.6285 | 609.6974 | 521.495
1334.3479 | 668.5296 | 735.9917 | 613.3684 | 519.386
1335.3479 | 668.7986 | 731.7179 | 618.6578 | 515.9403
1336.3479 | 668.6721 | 723.7348 | 620.9212 | 513.0225
1337.3479 | 666.5048 | 729.6627 | 629.4729 | 514.1267
1338.3479 | 666.1015 | 740.4916 | 629.6772 | 512.7856
1339.3479 | 670.4181 | 738.9679 | 629.1072 | 511.1297
1340.3479 | 671.4665 | 727.8973 | 643.6365 | 512.4386
1341.3479 | 670.9627 | 731.7133 | 649.609 | 512.1055
1342.3479 | 673.8034 | 732.7257 | 649.5991 | 510.6196
1343.3479 | 673.003 | 734.7749 | 654.2377 | 512.216
1344.3479 | 673.9807 | 727.0084 | 650.5315 | 510.4607
1345.3479 | 674.2917 | 730.2576 | 651.0704 | 510.4367
1346.3479 | 675.7677 | 730.6996 | 640.4869 | 509.4502
1347.3479 | 675.103 | 719.1187 | 634.5374 | 511.1659
1348.3479 | 678.0343 | 713.0639 | 629.4666 | 509.7075
1349.3479 | 677.8738 | 714.7009 | 636.8519 | 508.7984
1350.3479 | 685.9735 | 715.8237 | 632.1632 | 506.8798
1351.3479 | 684.466 | 713.2718 | 624.3871 | 505.346
1352.3479 | 684.3715 | 710.4126 | 630.0279 | 503.5931
1353.3479 | 687.8961 | 713.4822 | 639.2518 | 505.5569
1354.3479 | 689.9307 | 715.7077 | 633.6569 | 506.0675
1355.3479 | 687.9172 | 720.3027 | 626.6698 | 505.6327
1356.3479 | 692.7668 | 719.1691 | 618.4513 | 507.6472
1357.3479 | 689.5028 | 718.2986 | 612.0931 | 509.6471
1358.3479 | 684.8133 | 730.6373 | 611.727 | 507.4275
1359.3479 | 684.6353 | 733.4748 | 622.6638 | 505.3188
1360.3479 | 681.4694 | 732.3924 | 628.3994 | 505.3632
1361.3479 | 679.0956 | 732.9107 | 621.7013 | 504.528
1362.3479 | 678.5698 | 729.2654 | 615.2436 | 503.4978
1363.3479 | 675.6051 | 741.0612 | 612.4115 | 504.8605
1364.3479 | 673.0023 | 740.9705 | 606.5185 | 508.6148
1365.3479 | 670.045 | 744.0398 | 603.1607 | 508.5218
1366.3479 | 668.7018 | 745.6981 | 615.7924 | 508.6376
1367.3479 | 671.1859 | 749.8692 | 628.0821 | 509.2638
1368.3479 | 671.385 | 747.4202 | 644.2936 | 509.7674
1369.3479 | 670.977 | 744.826 | 637.3266 | 510.2602
1370.3479 | 671.7262 | 735.2244 | 629.6754 | 514.4854
1371.3479 | 671.2784 | 734.2575 | 639.6754 | 513.6006
1372.3479 | 673.7068 | 737.9175 | 648.4429 | 514.9426
1373.3479 | 673.9909 | 738.4559 | 656.848 | 514.5246
1374.3479 | 674.6767 | 742.7162 | 664.2651 | 513.3416
1375.3479 | 674.7041 | 745.1815 | 666.8699 | 512.8142
1376.3479 | 675.6512 | 742.9171 | 674.0867 | 511.2949
1377.3479 | 676.2421 | 743.1088 | 677.3185 | 512.2743
1378.3479 | 676.4135 | 746.953 | 685.6872 | 511.9931
1379.3479 | 675.8311 | 746.5366 | 693.2426 | 511.0007
1380.3479 | 675.3606 | 743.6044 | 694.2753 | 511.514
1381.3479 | 676.0969 | 739.4131 | 697.6097 | 511.5839
1382.3479 | 677.9375 | 745.7873 | 697.9851 | 516.5879
1383.3479 | 678.1507 | 739.9322 | 695.9112 | 516.6744
1384.3479 | 678.5556 | 738.9245 | 701.5963 | 520.1644
1385.3479 | 678.5489 | 737.075 | 689.3465 | 519.2118
1386.3479 | 680.039 | 738.4778 | 676.5076 | 520.5075
1387.3479 | 679.955 | 736.3421 | 666.1222 | 522.738
1388.3479 | 678.3382 | 740.3952 | 657.2165 | 524.7468
1389.3479 | 677.1169 | 737.4641 | 666.4176 | 522.3259
1390.3479 | 677.7911 | 747.1617 | 670.071 | 520.1065
1391.3479 | 681.768 | 747.2827 | 664.4365 | 520.4449
1392.3479 | 679.337 | 749.1089 | 669.2446 | 522.1351
1393.3479 | 679.994 | 755.4091 | 678.8539 | 524.4362
1394.3479 | 679.3028 | 747.6783 | 685.6647 | 524.1997
1395.3479 | 679.0592 | 754.3503 | 692.5826 | 522.5483
1396.3479 | 679.7325 | 756.0487 | 690.5984 | 520.444
1397.3479 | 680.2472 | 754.6873 | 695.2456 | 520.4586
1398.3479 | 679.6794 | 748.8502 | 697.7565 | 518.9101
1399.3479 | 678.6894 | 751.7333 | 708.8043 | 517.9421
1400.3479 | 680.302 | 757.462 | 704.5169 | 514.3141
1401.3479 | 683.4022 | 749.5499 | 701.3049 | 513.7768
1402.3479 | 687.0227 | 750.7895 | 704.4515 | 512.6829
1403.3479 | 686.3143 | 745.6313 | 709.7811 | 513.5
1404.3479 | 686.1178 | 732.8338 | 720.674 | 515.2947
1405.3479 | 683.9989 | 738.3016 | 712.0041 | 514.7901
1406.3479 | 682.6944 | 740.3089 | 715.2771 | 516.8416
1407.3479 | 680.1648 | 747.1941 | 718.825 | 514.9675
1408.3479 | 679.1458 | 758.3952 | 723.4056 | 517.9074
1409.3479 | 677.9616 | 762.4003 | 717.3714 | 517.9253
1410.3479 | 681.9279 | 762.916 | 724.2777 | 519.5047
1411.3479 | 678.1464 | 762.7124 | 722.313 | 519.7526
1412.3479 | 676.3583 | 760.6463 | 711.0046 | 522.644
1413.3479 | 679.4545 | 754.0676 | 715.0055 | 524.9405
1414.3479 | 677.5139 | 757.677 | 710.2412 | 523.4341
1415.3479 | 673.7962 | 768.1027 | 720.5556 | 525.4312
1416.3479 | 669.7892 | 761.5021 | 709.0637 | 524.3745
1417.3479 | 665.8295 | 762.3765 | 716.8336 | 523.5041
1418.3479 | 666.7161 | 764.2337 | 726.0737 | 523.3988
1419.3479 | 666.1484 | 761.7763 | 736.9084 | 523.0335
1420.3479 | 665.2251 | 766.2371 | 724.9079 | 524.6079
1421.3479 | 665.4236 | 770.6396 | 720.3815 | 533.5104
1422.3479 | 665.0036 | 776.7997 | 723.4605 | 538.7431
1423.3479 | 665.3576 | 776.2145 | 724.3255 | 542.0632
1424.3479 | 664.1854 | 783.0404 | 723.49 | 549.6065
1425.3479 | 662.1794 | 778.0059 | 722.5303 | 546.7798
1426.3479 | 661.6316 | 775.7301 | 717.0075 | 543.5596
1427.3479 | 660.0008 | 772.8249 | 716.761 | 540.3275
1428.3479 | 655.9917 | 770.3032 | 714.4261 | 541.0065
1429.3479 | 652.1718 | 770.899 | 710.356 | 541.0949
1430.3479 | 652.2612 | 766.5185 | 707.9329 | 538.9678
1431.3479 | 653.3459 | 762.6289 | 708.9942 | 537.5198
1432.3479 | 652.7015 | 759.0394 | 707.5162 | 536.9716
1433.3479 | 652.8743 | 761.1091 | 701.9452 | 537.9598
1434.3479 | 652.7737 | 753.2491 | 697.274 | 540.1995
1435.3479 | 654.0942 | 754.2922 | 689.8212 | 537.6098
1436.3479 | 654.058 | 748.3936 | 685.614 | 535.5856
1437.3479 | 654.2296 | 752.1832 | 689.0933 | 533.3751
1438.3479 | 653.5916 | 754.8192 | 691.8401 | 535.0479
1439.3479 | 654.2987 | 746.8658 | 682.6513 | 534.7293
1440.3479 | 653.2859 | 748.7813 | 680.9319 | 534.1909
1441.3479 | 653.2847 | 748.8243 | 678.8138 | 538.1934
1442.3479 | 655.7047 | 749.1108 | 673.5616 | 535.361
1443.3479 | 654.6672 | 754.1015 | 669.7006 | 534.2354
1444.3479 | 654.1918 | 751.716 | 667.195 | 534.7586
1445.3479 | 655.5968 | 752.1055 | 672.3428 | 533.9481
1446.3479 | 655.7456 | 753.2862 | 675.0959 | 531.7092
1447.3479 | 654.5534 | 743.481 | 675.1348 | 529.2748
1448.3479 | 652.2071 | 741.0511 | 669.9211 | 527.0576
1449.3479 | 653.0219 | 739.0079 | 674.6396 | 534.8318
1450.3479 | 653.0485 | 744.1916 | 671.3296 | 538.9216
1451.3479 | 651.6564 | 744.1358 | 661.9011 | 535.8852
1452.3479 | 652.7966 | 747.5649 | 667.6889 | 535.996
1453.3479 | 656.7122 | 751.7933 | 679.8488 | 534.7273
1454.3479 | 656.6533 | 754.6494 | 674.8582 | 532.5323
1455.3479 | 657.8239 | 760.5814 | 673.6821 | 530.7473
1456.3479 | 657.6535 | 748.1058 | 679.3389 | 528.4775
1457.3479 | 658.2647 | 741.469 | 680.6945 | 526.6302
1458.3479 | 658.5406 | 734.0821 | 677.0918 | 529.5277
1459.3479 | 656.74 | 733.0268 | 680.6957 | 528.8104
1460.3479 | 652.6049 | 731.6796 | 683.8805 | 527.2052
1461.3479 | 651.3925 | 730.4831 | 672.4101 | 525.3422
1462.3479 | 651.2058 | 727.0752 | 676.2968 | 523.2785
1463.3479 | 652.1674 | 728.1938 | 675.9843 | 522.1632
1464.3479 | 653.7005 | 730.3888 | 686.6372 | 524.9382
1465.3479 | 651.9573 | 738.2525 | 682.2131 | 526.0163
1466.3479 | 649.4703 | 735.3634 | 672.6154 | 528.8802
1467.3479 | 647.9105 | 736.6589 | 666.5912 | 527.1089
1468.3479 | 645.8728 | 744.6399 | 663.5413 | 526.778
1469.3479 | 645.2997 | 747.0735 | 653.5359 | 523.5328
1470.3479 | 644.8431 | 745.0565 | 647.1381 | 524.491
1471.3479 | 648.6846 | 752.6492 | 641.8924 | 525.2342
1472.3479 | 647.5671 | 747.6387 | 647.8446 | 523.119
1473.3479 | 646.5904 | 738.2408 | 636.0623 | 521.2635
1474.3479 | 644.9093 | 738.4875 | 633.43 | 521.507
1475.3479 | 643.0298 | 740.8614 | 631.157 | 522.304
1476.3479 | 642.1928 | 748.0939 | 630.864 | 525.1489
1477.3479 | 642.8731 | 744.988 | 631.6025 | 524.5858
1478.3479 | 643.7601 | 750.7642 | 641.9333 | 523.6717
1479.3479 | 645.3129 | 749.1029 | 648.2182 | 524.2657
1480.3479 | 645.9501 | 748.6698 | 643.4072 | 527.3164
1481.3479 | 646.999 | 750.1181 | 644.5578 | 526.8434
1482.3479 | 645.6918 | 752.4072 | 642.2511 | 525.6216
1483.3479 | 645.2012 | 743.959 | 637.5374 | 530.5002
1484.3479 | 643.3664 | 754.1064 | 633.0237 | 529.3911
1485.3479 | 643.5005 | 749.0757 | 635.505 | 530.6487
1486.3479 | 646.1535 | 749.8915 | 633.2257 | 531.6663
1487.3479 | 643.9868 | 752.9481 | 635.1549 | 530.6951
1488.3479 | 643.2183 | 756.196 | 630.7964 | 529.4741
1489.3479 | 643.9664 | 757.0418 | 631.4679 | 530.845
1490.3479 | 646.4108 | 759.557 | 630.4008 | 529.4101
1491.3479 | 645.6747 | 758.3915 | 631.2153 | 527.0123
1492.3479 | 646.5808 | 760.7569 | 624.8088 | 526.864
1493.3479 | 646.4435 | 758.1247 | 626.8031 | 527.3435
1494.3479 | 643.3758 | 754.0099 | 619.832 | 526.9992
1495.3479 | 641.1501 | 746.9647 | 614.7821 | 526.1611
1496.3479 | 641.9103 | 753.0537 | 608.4181 | 525.8803
1497.3479 | 640.8005 | 754.4366 | 602.6519 | 527.1539
1498.3479 | 642.4047 | 763.3561 | 601.9884 | 527.3927
1499.3479 | 641.8994 | 761.0156 | 602.7081 | 528.5437
1500.3479 | 642.1865 | 771.1737 | 599.9385 | 531.2699
1501.3479 | 641.6613 | 769.68 | 599.9754 | 531.3621
1502.3479 | 640.2013 | 774.8142 | 598.4322 | 529.9932
1503.3479 | 641.2808 | 774.989 | 601.1105 | 536.5315
1504.3479 | 641.7207 | 775.1921 | 603.4183 | 532.7003
1505.3479 | 641.4179 | 768.0751 | 602.9364 | 530.545
1506.3479 | 642.7275 | 773.6968 | 598.8892 | 531.2112
1507.3479 | 647.5029 | 771.6418 | 594.826 | 530.3675
1508.3479 | 645.67 | 780.9921 | 592.1815 | 530.3635
1509.3479 | 645.4054 | 781.6513 | 593.5706 | 529.6066
1510.3479 | 645.5986 | 776.3751 | 594.94 | 527.6328
1511.3479 | 646.7222 | 779.3894 | 593.1466 | 526.1843
1512.3479 | 645.2876 | 778.2671 | 597.7345 | 525.1177
1513.3479 | 643.9946 | 779.7622 | 597.1606 | 523.6536
1514.3479 | 641.7218 | 777.0955 | 601.6607 | 523.6119
1515.3479 | 641.9757 | 780.5721 | 599.7117 | 524.2841
1516.3479 | 646.2991 | 777.4616 | 596.9245 | 526.0607
1517.3479 | 647.8482 | 777.2902 | 596.1552 | 526.4759
1518.3479 | 647.1156 | 777.8519 | 593.2009 | 527.9001
1519.3479 | 648.9048 | 768.3887 | 589.0563 | 528.2354
1520.3479 | 650.0735 | 755.684 | 585.2763 | 527.4723
1521.3479 | 648.4002 | 761.2758 | 585.1765 | 528.1753
1522.3479 | 648.5048 | 757.9418 | 588.1754 | 531.7921
1523.3479 | 647.7932 | 762.8747 | 585.5606 | 529.2328
1524.3479 | 647.2537 | 760.5311 | 583.4605 | 528.3606
1525.3479 | 646.5313 | 760.5585 | 583.3529 | 525.8711
1526.3479 | 645.603 | 756.7519 | 583.1714 | 527.9493
1527.3479 | 645.3722 | 754.076 | 581.8121 | 528.5035
1528.3479 | 645.0402 | 752.5588 | 580.97 | 527.875
1529.3479 | 645.5088 | 752.3569 | 584.1559 | 529.1985
1530.3479 | 650.6446 | 748.9055 | 585.6155 | 529.7542
1531.3479 | 651.9096 | 749.9655 | 587.8864 | 529.7302
1532.3479 | 651.9956 | 756.0672 | 595.6114 | 529.9863
1533.3479 | 654.6334 | 751.1049 | 591.798 | 530.1654
1534.3479 | 654.9289 | 748.5908 | 589.5774 | 538.849
1535.3479 | 654.6169 | 748.0464 | 586.6218 | 539.7287
1536.3479 | 654.9794 | 749.2233 | 588.1155 | 537.8097
1537.3479 | 654.8173 | 752.3165 | 587.0604 | 535.829
1538.3479 | 654.373 | 752.4787 | 585.4118 | 534.654
1539.3479 | 654.5921 | 745.8204 | 584.0921 | 532.3356
1540.3479 | 655.4568 | 745.6885 | 582.7277 | 530.9813
1541.3479 | 654.3622 | 744.6262 | 582.5614 | 527.7886
1542.3479 | 653.2787 | 750.311 | 581.8501 | 528.4967
1543.3479 | 655.7269 | 748.0942 | 580.2971 | 527.9623
1544.3479 | 652.4887 | 737.3237 | 576.0789 | 527.935
1545.3479 | 648.1618 | 734.0683 | 573.856 | 529.2937
1546.3479 | 645.6175 | 738.9732 | 573.2292 | 527.2152
1547.3479 | 645.2473 | 744.0211 | 573.1749 | 528.7717
1548.3479 | 645.0444 | 746.9246 | 571.6875 | 526.1691
1549.3479 | 645.334 | 751.9116 | 571.0437 | 525.3082
1550.3479 | 642.9815 | 753.7425 | 570.4715 | 525.5294
1551.3479 | 641.311 | 753.9484 | 568.625 | 524.5905
1552.3479 | 641.8343 | 750.3836 | 567.3598 | 525.6299
1553.3479 | 641.698 | 749.382 | 566.7078 | 527.5201
1554.3479 | 641.7278 | 749.3979 | 565.718 | 529.2299
1555.3479 | 642.8802 | 749.1351 | 565.8926 | 528.9625
1556.3479 | 642.877 | 754.4976 | 565.6311 | 533.6771
1557.3479 | 643.4625 | 749.5121 | 565.3923 | 534.0431
1558.3479 | 645.0101 | 746.8683 | 564.1858 | 533.8265
1559.3479 | 647.6579 | 746.1194 | 564.093 | 535.27
1560.3479 | 650.0019 | 753.4546 | 564.5382 | 535.2511
1561.3479 | 650.3606 | 752.0492 | 564.9782 | 536.4669
1562.3479 | 650.084 | 754.8369 | 566.3127 | 535.3267
1563.3479 | 649.2134 | 754.2038 | 565.7919 | 533.8356
1564.3479 | 649.7694 | 752.9953 | 565.0942 | 533.2401
1565.3479 | 650.4291 | 749.561 | 565.409 | 534.1366
1566.3479 | 649.3027 | 757.859 | 567.7316 | 532.5374
1567.3479 | 647.3062 | 757.0013 | 566.846 | 533.6921
1568.3479 | 646.6674 | 754.0656 | 565.556 | 532.8599
1569.3479 | 646.9672 | 751.6325 | 564.5055 | 530.7127
1570.3479 | 646.7746 | 755.2873 | 564.3372 | 532.765
1571.3479 | 645.5807 | 757.3933 | 565.153 | 532.8321
1572.3479 | 644.7155 | 766.1936 | 564.423 | 534.5073
1573.3479 | 645.4713 | 764.4879 | 565.4027 | 532.549
1574.3479 | 645.5982 | 764.8049 | 564.4734 | 531.2537
1575.3479 | 647.4967 | 754.6236 | 564.5359 | 537.3419
1576.3479 | 648.3016 | 756.6186 | 567.9012 | 541.5346
1577.3479 | 649.9977 | 742.5883 | 567.6396 | 541.5145
1578.3479 | 649.4033 | 738.5484 | 566.6295 | 540.5875
1579.3479 | 648.662 | 746.4221 | 566.3938 | 536.9864
1580.3479 | 649.43 | 747.9923 | 566.0854 | 536.7155
1581.3479 | 648.8833 | 757.3169 | 566.2736 | 540.2897
1582.3479 | 649.0613 | 754.8573 | 566.0354 | 541.8269
1583.3479 | 648.4023 | 755.1886 | 565.8129 | 541.1984
1584.3479 | 647.101 | 751.3824 | 565.0345 | 540.3237
1585.3479 | 645.6886 | 745.3997 | 563.1877 | 537.2396
1586.3479 | 643.7572 | 737.3795 | 560.782 | 539.4673
1587.3479 | 641.9281 | 723.334 | 559.9247 | 542.7169
1588.3479 | 642.3024 | 744.3024 | 559.4085 | 540.1508
1589.3479 | 646.3189 | 733.9576 | 559.1305 | 539.1687
1590.3479 | 644.3299 | 745.2202 | 560.4803 | 537.3863
1591.3479 | 642.1983 | 746.8061 | 559.9294 | 536.7484
1592.3479 | 641.0964 | 759.0341 | 559.7829 | 535.3973
1593.3479 | 639.7554 | 758.5217 | 559.9478 | 534.2218
1594.3479 | 639.3261 | 748.356 | 559.9286 | 536.6141
1595.3479 | 640.9785 | 738.2222 | 557.2663 | 534.5809
1596.3479 | 641.2087 | 742.0768 | 557.1576 | 533.8509
1597.3479 | 642.266 | 741.5356 | 556.6542 | 533.3162
1598.3479 | 641.1756 | 745.5115 | 557.7922 | 531.9494
1599.3479 | 640.524 | 743.0026 | 558.3023 | 530.9981
1600.3479 | 645.2713 | 735.0461 | 559.3243 | 530.6175
1601.3479 | 645.7473 | 730.4215 | 561.2703 | 532.8898
1602.3479 | 645.1757 | 734.6462 | 564.0534 | 530.7389
1603.3479 | 644.883 | 731.8981 | 563.5615 | 529.7116
1604.3479 | 644.0775 | 726.0546 | 562.6322 | 528.8555
1605.3479 | 645.4735 | 735.8399 | 561.7871 | 527.6653
1606.3479 | 645.4833 | 736.5505 | 561.8713 | 526.5661
1607.3479 | 644.2823 | 743.7868 | 561.8521 | 524.2264
1608.3479 | 641.8757 | 742.1831 | 560.4289 | 524.186
1609.3479 | 644.05 | 735.9052 | 559.9171 | 521.8173
1610.3479 | 644.1948 | 728.6595 | 560.3532 | 521.0669
1611.3479 | 643.1357 | 722.3465 | 559.469 | 522.3387
1612.3479 | 642.7403 | 724.1448 | 559.4784 | 522.4997
1613.3479 | 640.0636 | 734.2864 | 560.4965 | 524.8142
1614.3479 | 639.0599 | 742.416 | 559.1789 | 523.3445
1615.3479 | 639.4227 | 749.5582 | 560.0224 | 521.638
1616.3479 | 638.8992 | 753.0097 | 562.1595 | 521.9291
1617.3635 | 641.145 | 748.2989 | 564.8015 | 523.2754
1618.3479 | 640.2653 | 750.2151 | 562.1257 | 523.5455
1619.3479 | 641.3369 | 749.8318 | 560.7195 | 522.7508
1620.3479 | 641.4218 | 760.1782 | 560.9117 | 523.9084
1621.3479 | 642.0395 | 746.2916 | 560.131 | 524.4558
1622.3479 | 642.4868 | 745.0754 | 559.1221 | 522.6736
1623.3479 | 643.6444 | 745.4813 | 559.2657 | 523.5467
1624.3479 | 645.9615 | 756.1795 | 559.7096 | 522.0845
1625.3479 | 648.3784 | 744.3558 | 560.9754 | 526.1472
1626.3479 | 650.3131 | 741.3151 | 561.7078 | 525.716
1627.3479 | 649.7974 | 731.7703 | 560.4711 | 526.5878
1628.3479 | 646.0361 | 717.1888 | 560.2165 | 525.0571
1629.3479 | 644.1746 | 714.7503 | 560.3521 | 522.9464
1630.3479 | 643.9845 | 720.8904 | 559.7126 | 522.3052
1631.3479 | 644.7171 | 707.8176 | 559.7279 | 520.7961
1632.3479 | 644.2498 | 702.8347 | 559.6987 | 524.2202
1633.3479 | 642.6232 | 715.298 | 559.025 | 523.1396
1634.3479 | 640.9476 | 726.1309 | 558.3954 | 521.0081
1635.3479 | 639.3946 | 728.0848 | 558.235 | 520.0669
1636.3479 | 637.1597 | 729.485 | 558.8802 | 519.0109
1637.3479 | 634.6435 | 728.6339 | 557.6281 | 518.8374
1638.3479 | 634.0296 | 730.9079 | 556.8233 | 519.9792
1639.3479 | 633.7681 | 735.7156 | 557.4507 | 521.0357
1640.3479 | 628.7837 | 741.1731 | 556.6305 | 520.7388
1641.3479 | 625.665 | 738.9354 | 555.395 | 521.3059
1642.3479 | 625.3653 | 740.3081 | 555.4138 | 519.7032
1643.3479 | 624.3269 | 739.8716 | 555.221 | 518.613
1644.3479 | 624.4814 | 732.1562 | 555.2586 | 519.1368
1645.3479 | 624.5031 | 741.9808 | 554.0307 | 521.3626
1646.3479 | 625.4583 | 739.1902 | 553.7337 | 521.5078
1647.3635 | 624.3764 | 736.4309 | 553.0837 | 522.7744
1648.3479 | 624.2051 | 732.3629 | 552.7999 | 521.7874
1649.3479 | 625.3845 | 727.7843 | 552.6467 | 522.9409
1650.3479 | 626.5896 | 733.5521 | 552.3609 | 526.9202
1651.3479 | 627.5761 | 739.7019 | 554.4507 | 528.6309
1652.3479 | 627.3702 | 738.3623 | 555.3862 | 528.3828
1653.3479 | 625.1487 | 744.2398 | 554.085 | 526.714
1654.3479 | 625.5377 | 749.1731 | 554.091 | 525.8351
1655.3479 | 627.2241 | 737.6388 | 556.102 | 526.9876
1656.3479 | 629.0366 | 745.1288 | 556.5546 | 525.8439
1657.3479 | 628.8418 | 743.081 | 556.5624 | 525.2073
1658.3479 | 627.6912 | 743.7516 | 556.7548 | 524.3626
1659.3479 | 628.3283 | 731.4038 | 556.6027 | 522.4963
1660.3479 | 626.8572 | 727.9185 | 556.7445 | 521.7949
1661.3479 | 628.0386 | 732.0233 | 556.3064 | 520.3958
1662.3479 | 631.8026 | 723.9542 | 556.8288 | 523.0985
1663.3479 | 633.8896 | 715.0548 | 556.602 | 522.3753
1664.3479 | 632.65 | 698.6734 | 556.4539 | 522.5669
1665.3479 | 631.701 | 695.7122 | 557.099 | 522.558
1666.3479 | 632.1397 | 695.2049 | 558.1171 | 520.6449
1667.3479 | 632.5902 | 704.2844 | 556.5321 | 519.4058
1668.3479 | 631.587 | 700.3493 | 555.1007 | 520.9929
1669.3479 | 629.4841 | 689.4074 | 552.1352 | 523.6022
1670.3479 | 624.107 | 692.0602 | 550.98 | 527.4928
1671.3479 | 622.2952 | 700.8293 | 551.2026 | 526.7351
1672.3479 | 622.32 | 698.1456 | 551.1265 | 526.1222
1673.3479 | 621.7445 | 689.9345 | 551.3242 | 523.3826
1674.3479 | 621.7478 | 685.6274 | 551.068 | 522.8013
1675.3479 | 622.0985 | 687.6431 | 551.1764 | 521.5969
1676.3479 | 622.8845 | 691.2406 | 550.901 | 519.2037
1677.3479 | 621.6737 | 685.7321 | 549.8394 | 519.0096
1678.3479 | 620.6568 | 693.3904 | 548.0514 | 519.7429
1679.3479 | 617.9116 | 684.7592 | 546.468 | 518.9596
1680.3479 | 618.9241 | 683.7188 | 544.8679 | 519.6381
1681.3479 | 616.9014 | 674.8471 | 543.4239 | 519.4694
1682.3479 | 616.167 | 677.4093 | 542.8519 | 520.1815
1683.3479 | 618.4643 | 677.5882 | 544.0243 | 519.5096
1684.3479 | 618.6493 | 678.7527 | 545.8831 | 518.3439
1685.3479 | 616.8676 | 680.4555 | 546.3021 | 518.4245
1686.3479 | 616.9137 | 685.7526 | 547.9301 | 516.9325
1687.3479 | 617.009 | 685.064 | 547.7556 | 516.5988
1688.3479 | 617.2468 | 681.048 | 547.7124 | 517.0437
1689.3479 | 618.1848 | 678.0663 | 547.5337 | 517.3316
1690.3479 | 620.4179 | 670.5572 | 547.7751 | 516.5029
1691.3479 | 621.5072 | 671.9029 | 548.6561 | 517.4407
1692.3479 | 623.6487 | 667.2136 | 548.9771 | 517.9995
1693.3479 | 624.3757 | 674.4058 | 549.6253 | 516.1463
1694.3479 | 625.437 | 678.399 | 548.791 | 514.3149
1695.3479 | 625.3469 | 672.1956 | 548.9929 | 516.0908
1696.3479 | 624.7644 | 678.5923 | 549.3656 | 513.7837
1697.3479 | 625.7478 | 676.1575 | 548.3958 | 512.6801
1698.3479 | 628.0193 | 671.693 | 549.3665 | 519.3448
1699.3479 | 626.6717 | 668.8065 | 548.682 | 523.4151
1700.3479 | 627.4219 | 682.4997 | 549.9493 | 522.3976
1701.3479 | 627.8472 | 689.9282 | 549.1597 | 521.2712
1702.3479 | 626.1655 | 703.2718 | 548.6426 | 518.6988
1703.3479 | 626.218 | 702.2745 | 548.9929 | 517.4341
1704.3479 | 627.0159 | 703.05 | 549.4956 | 518.0962
1705.3479 | 626.8293 | 694.5077 | 548.2741 | 518.5121
1706.3479 | 628.8114 | 685.0544 | 546.7968 | 518.9479
1707.3479 | 628.7598 | 686.9855 | 545.6877 | 519.3563
1708.3479 | 625.3656 | 682.3292 | 544.1155 | 519.3238
1709.3479 | 625.3707 | 676.8395 | 541.7294 | 517.6277
1710.3479 | 624.2573 | 692.9493 | 539.6483 | 517.1588
1711.3479 | 625.4128 | 692.5586 | 539.5035 | 515.2687
1712.3479 | 625.8307 | 684.7662 | 539.0776 | 513.3223
1713.3479 | 626.5589 | 680.3579 | 538.6649 | 513.2728
1714.3479 | 626.2003 | 669.7611 | 538.7435 | 514.3753
1715.3479 | 625.8683 | 671.8035 | 540.3953 | 515.469
1716.3479 | 624.9219 | 675.4329 | 540.5672 | 515.2272
1717.3479 | 624.5311 | 665.016 | 538.7085 | 512.9601
1718.3479 | 622.9289 | 657.6716 | 538.9343 | 512.9349
1719.3479 | 622.0623 | 667.5117 | 539.9993 | 511.1447
1720.3479 | 621.3987 | 681.4565 | 541.096 | 512.3153
1721.3479 | 621.9244 | 686.2297 | 542.5421 | 512.3886
1722.3479 | 621.9419 | 685.1606 | 542.9093 | 510.7022
1723.3479 | 619.0924 | 690.8842 | 543.8316 | 507.9816
1724.3479 | 616.7325 | 699.8935 | 543.8448 | 507.8019
1725.3479 | 616.7259 | 706.0756 | 542.9825 | 505.2394
1726.3479 | 615.9746 | 708.3799 | 543.7075 | 505.0956
1727.3479 | 613.3162 | 718.0149 | 543.5977 | 503.5866
1728.3479 | 612.6666 | 718.5714 | 542.4324 | 502.2983
1729.3479 | 613.3861 | 710.1402 | 541.4062 | 504.6284
1730.3479 | 615.156 | 698.9179 | 541.9081 | 503.3598
1731.3479 | 615.9415 | 686.9736 | 541.851 | 504.7583
1732.3479 | 617.1698 | 681.5148 | 542.0332 | 504.9514
1733.3479 | 618.7949 | 682.5917 | 542.6399 | 505.7144
1734.3479 | 618.5994 | 676.0931 | 542.0968 | 506.8526
1735.3479 | 619.3458 | 677.8213 | 542.9038 | 508.3859
1736.3479 | 619.3949 | 672.7861 | 543.9017 | 509.2543
1737.3479 | 620.2557 | 672.1973 | 544.7304 | 510.9381
1738.3479 | 622.536 | 673.5255 | 545.3947 | 511.6177
1739.3479 | 623.4018 | 667.2697 | 543.3187 | 510.8749
1740.3479 | 620.9457 | 662.3504 | 539.8132 | 511.7755
1741.3479 | 620.169 | 660.1571 | 538.5338 | 513.5804
1742.3479 | 620.1308 | 659.653 | 538.0693 | 515.4258
1743.3479 | 618.0383 | 659.856 | 538.9682 | 514.8378
1744.3479 | 618.4514 | 671.0102 | 539.8105 | 513.3785
1745.3479 | 618.7597 | 668.5579 | 540.7774 | 511.2633
1746.3479 | 615.8528 | 662.0571 | 540.2644 | 513.7179
1747.3479 | 615.6506 | 655.144 | 539.6373 | 511.7487
1748.3479 | 615.7237 | 647.8814 | 539.8068 | 511.7557
1749.3479 | 615.6014 | 640.8146 | 538.773 | 512.1896
1750.3479 | 614.9005 | 635.2241 | 538.1646 | 512.6107
1751.3479 | 613.1758 | 632.5108 | 537.5983 | 510.6412
1752.3479 | 613.6678 | 628.2324 | 536.287 | 510.3573
1753.3479 | 614.1676 | 629.9231 | 537.0503 | 514.187
1754.3479 | 614.7628 | 625.9861 | 537.0139 | 512.3018
1755.3479 | 615.2936 | 629.4737 | 539.1437 | 512.2008
1756.3479 | 612.8481 | 633.3278 | 539.6778 | 510.6893
1757.3479 | 611.4366 | 641.2507 | 539.2378 | 510.232
1758.3479 | 610.1732 | 645.5537 | 538.8374 | 508.625
1759.3479 | 606.6706 | 652.7382 | 538.2569 | 506.6846
1760.3479 | 608.9766 | 655.1208 | 539.7847 | 506.9115
1761.3479 | 609.5885 | 659.9697 | 539.9791 | 505.7517
1762.3479 | 610.8818 | 662.7309 | 540.0498 | 503.6949
1763.3479 | 612.0429 | 654.8111 | 540.2376 | 503.8351
1764.3479 | 613.5429 | 658.709 | 540.3836 | 502.466
1765.3479 | 613.0547 | 655.5252 | 539.6963 | 501.5692
1766.3479 | 613.5046 | 649.8911 | 540.5813 | 500.729
1767.3479 | 612.6512 | 645.5263 | 541.198 | 500.1899
1768.3479 | 611.0688 | 646.3883 | 541.7648 | 501.7584
1769.3479 | 611.4245 | 642.3889 | 541.7222 | 500.4339
1770.3479 | 613.3103 | 648.0924 | 542.5911 | 500.5335
1771.3479 | 614.1374 | 651.3292 | 543.5553 | 502.0294
1772.3479 | 613.5406 | 644.0642 | 543.3156 | 502.9154
1773.3479 | 616.0186 | 647.5819 | 540.9256 | 503.8182
1774.3479 | 617.7563 | 648.0338 | 541.2673 | 507.5973
1775.3479 | 617.4512 | 645.386 | 540.4811 | 505.896
1776.3479 | 618.8421 | 644.896 | 541.0258 | 505.6289
1777.3479 | 618.7663 | 639.158 | 540.5377 | 505.1059
1778.3479 | 619.8153 | 643.5013 | 540.7193 | 504.9424
1779.3479 | 618.2821 | 641.434 | 542.5704 | 503.287
1780.3479 | 618.9911 | 639.4673 | 542.4247 | 505.256
1781.3479 | 621.1978 | 638.2792 | 541.4632 | 504.1892
1782.3479 | 621.114 | 643.6431 | 540.9181 | 504.4506
1783.3479 | 621.7725 | 640.4309 | 540.376 | 506.2659
1784.3479 | 622.5477 | 635.9351 | 540.3988 | 505.9047
1785.3479 | 621.6551 | 631.2246 | 540.5062 | 505.1802
1786.3479 | 621.645 | 626.3282 | 540.0612 | 507.3653
1787.3479 | 621.2523 | 623.0914 | 539.7961 | 506.7402
1788.3479 | 619.8771 | 625.5185 | 540.4925 | 508.5266
1789.3479 | 618.7615 | 623.0392 | 540.2012 | 509.2527
1790.3479 | 619.6299 | 620.9504 | 541.0396 | 509.2922
1791.3479 | 620.5396 | 619.8889 | 541.1198 | 509.3105
1792.3479 | 621.7715 | 617.4349 | 541.971 | 507.4373
1793.3479 | 620.3185 | 618.8356 | 541.3941 | 505.9606
1794.3479 | 619.1484 | 613.7666 | 540.7681 | 505.5394
1795.3479 | 619.7609 | 613.4712 | 539.7901 | 503.7947
1796.3479 | 618.7347 | 616.6016 | 540.5276 | 501.7826
1797.3635 | 619.055 | 618.8608 | 542.2922 | 500.8502
1798.3479 | 619.9696 | 622.65 | 543.0668 | 499.3346
1799.3479 | 619.9146 | 620.0719 | 542.612 | 498.7441
1800.3479 | 614.947 | 618.552 | 542.2289 | 496.4402
1801.3479 | 613.846 | 617.1259 | 542.8767 | 495.0614
1802.3479 | 614.3242 | 617.8668 | 543.2151 | 493.989
1803.3479 | 615.7336 | 613.9931 | 542.7604 | 493.9075
1804.3479 | 615.8079 | 618.4229 | 543.5958 | 493.7308
1805.3479 | 618.0296 | 616.8565 | 543.3449 | 492.6263
1806.3479 | 618.89 | 617.6267 | 541.8358 | 491.343
1807.3479 | 618.6262 | 618.0387 | 541.4759 | 491.7316
1808.3479 | 619.8514 | 614.3568 | 541.0727 | 491.2843
1809.3479 | 621.0304 | 614.9778 | 540.5168 | 490.7141
1810.3479 | 618.8492 | 613.4045 | 540.9525 | 489.7729
1811.3479 | 619.1512 | 611.5509 | 539.783 | 487.8642
1812.3479 | 617.7876 | 609.8939 | 540.5589 | 486.5985
1813.3479 | 614.6374 | 608.9764 | 541.5759 | 486.1754
1814.3479 | 615.8475 | 610.0101 | 541.3757 | 486.3199
1815.3479 | 617.4746 | 607.6451 | 540.9356 | 485.401
1816.3479 | 618.4161 | 611.4635 | 541.3532 | 484.3248
1817.3479 | 619.2212 | 610.9589 | 541.7283 | 484.204
1818.3479 | 617.3724 | 609.6703 | 540.4465 | 484.4419
1819.3479 | 616.3869 | 609.202 | 539.1763 | 484.3557
1820.3479 | 615.4932 | 622.2294 | 540.1577 | 485.2256
1821.3479 | 616.4429 | 627.9848 | 538.47 | 487.208
1822.3479 | 619.159 | 636.1585 | 538.215 | 491.2251
1823.3479 | 618.6873 | 634.4608 | 538.2659 | 492.6804
1824.3479 | 619.2341 | 631.481 | 539.772 | 493.0179
1825.3479 | 618.9514 | 628.6581 | 538.1935 | 497.0945
1826.3479 | 618.2401 | 628.6004 | 539.6195 | 496.3044
1827.3479 | 619.2687 | 623.8217 | 540.2902 | 495.0991
1828.3479 | 620.3601 | 622.5962 | 539.7215 | 494.8676
1829.3479 | 621.0714 | 625.5623 | 538.9694 | 493.4343
1830.3479 | 620.413 | 624.4175 | 537.8257 | 492.4621
1831.3479 | 619.6992 | 619.1965 | 538.4963 | 492.7666
1832.3479 | 621.1981 | 618.0165 | 537.6176 | 497.5631
1833.3479 | 622.3034 | 621.5234 | 539.45 | 497.7684
1834.3479 | 624.1095 | 624 | 538.3953 | 496.6591
1835.3479 | 621.2424 | 627.6411 | 536.2874 | 499.6388
1836.3479 | 620.7941 | 624.7986 | 536.0147 | 499.2511
1837.3479 | 619.2532 | 619.7833 | 536.5932 | 498.5161
1838.3479 | 618.7427 | 613.1954 | 536.5868 | 498.2994
1839.3479 | 620.1138 | 613.1246 | 536.6126 | 498.409
1840.3479 | 620.0056 | 611.3236 | 535.3268 | 498.1977
1841.3479 | 620.7182 | 608.7072 | 535.0864 | 498.8872
1842.3479 | 620.4693 | 611.431 | 535.0878 | 496.8091
1843.3479 | 622.0586 | 607.7759 | 535.4951 | 495.5119
1844.3479 | 622.0671 | 606.3569 | 534.2433 | 496.0632
1845.3479 | 622.0184 | 602.961 | 532.9991 | 496.6303
1846.3479 | 621.2769 | 601.4352 | 533.1602 | 495.4351
1847.3479 | 621.0633 | 602.509 | 534.409 | 496.9856
1848.3479 | 619.8492 | 621.5657 | 529.784 | 496.8848
1849.3479 | 618.6577 | 629.4141 | 528.2821 | 496.5058
1850.3479 | 620.788 | 633.0609 | 525.9493 | 494.5147
1851.3479 | 619.6687 | 638.7687 | 526.3916 | 492.8576
1852.3479 | 619.4566 | 641.8965 | 527.1312 | 492.6004
1853.3479 | 619.8177 | 635.6747 | 528.3813 | 492.7734
1854.3479 | 618.5653 | 631.4105 | 530.2893 | 491.2603
1855.3479 | 616.937 | 626.533 | 531.683 | 491.4844
1856.3479 | 618.118 | 622.9445 | 530.6745 | 491.7693
1857.3479 | 618.6571 | 618.1386 | 532.9656 | 491.0553
1858.3479 | 615.2601 | 625.3866 | 533.0123 | 490.0552
1859.3479 | 615.3705 | 623.6104 | 534.0063 | 489.6575
1860.3479 | 617.065 | 621.956 | 532.8446 | 489.9445
1861.3479 | 618.9468 | 616.8284 | 534.6072 | 490.3906
1862.3479 | 620.7383 | 610.6525 | 536.3392 | 490.0934
1863.3479 | 621.2283 | 615.2527 | 536.6108 | 489.822
1864.3479 | 622.7535 | 611.0821 | 535.7211 | 489.2892
1865.3479 | 623.7618 | 607.0477 | 536.2839 | 489.251
1866.3479 | 623.5787 | 613.9438 | 537.4582 | 489.5676
1867.3479 | 625.6741 | 616.1146 | 535.5239 | 488.8489
1868.3479 | 625.9702 | 627.9038 | 533.8471 | 488.2588
1869.3479 | 627.2985 | 625.4419 | 532.4682 | 488.0698
1870.3479 | 627.5546 | 626.0963 | 534.1167 | 490.4344
1871.3479 | 626.2993 | 632.3616 | 534.599 | 489.7775
1872.3479 | 623.9872 | 638.2436 | 535.238 | 489.4004
1873.3479 | 624.9899 | 643.582 | 533.3714 | 489.0872
1874.3479 | 626.0592 | 650.7753 | 530.3176 | 487.4391
1875.3479 | 625.2357 | 667.0401 | 529.3909 | 489.9496
1876.3479 | 625.2993 | 661.64 | 529.4822 | 489.4448
1877.3479 | 624.1256 | 652.2028 | 530.9107 | 493.2938
1878.3479 | 626.0317 | 648.3496 | 532.0134 | 492.1833
1879.3479 | 625.6811 | 668.2466 | 532.7588 | 493.0867
1880.3479 | 623.7307 | 664.9598 | 532.6916 | 491.5282
1881.3479 | 623.6677 | 658.3212 | 531.1433 | 490.6098
1882.3479 | 623.9394 | 652.8709 | 529.2903 | 491.2851
1883.3479 | 624.2265 | 661.6257 | 529.4982 | 491.0817
1884.3479 | 623.8651 | 666.9024 | 529.4452 | 490.3702
1885.3479 | 620.6214 | 661.1666 | 529.1228 | 488.7674
1886.3479 | 619.8955 | 655.9032 | 527.9213 | 488.021
1887.3479 | 617.8822 | 652.3339 | 530.1182 | 486.6946
1888.3479 | 617.3146 | 662.7215 | 533.8677 | 486.0489
1889.3479 | 619.3276 | 661.7988 | 534.9801 | 485.9496
1890.3479 | 618.9232 | 659.9922 | 534.9718 | 485.2964
1891.3479 | 619.5726 | 661.2641 | 537.7597 | 484.9354
1892.3479 | 619.5397 | 656.8392 | 539.1838 | 484.9386
1893.3479 | 616.8727 | 662.5713 | 539.5499 | 483.5736
1894.3479 | 615.8394 | 656.2915 | 541.5057 | 482.8687
1895.3479 | 617.5233 | 650.0098 | 542.1768 | 483.0237
1896.3479 | 619.8542 | 642.7952 | 542.0309 | 481.9254
1897.3479 | 621.9717 | 636.095 | 541.8525 | 480.8019
1898.3479 | 622.5767 | 640.7397 | 542.2478 | 480.9977
1899.3479 | 623.3577 | 634.5514 | 541.6185 | 479.5681
1900.3479 | 623.4974 | 641.6194 | 539.379 | 478.4752
1901.3479 | 625.8456 | 659.8475 | 538.1492 | 477.5526
1902.3479 | 626.3274 | 649.8319 | 538.6566 | 477.0266
1903.3479 | 625.0001 | 643.7364 | 538.7112 | 475.8489
1904.3479 | 622.9729 | 636.2874 | 538.1408 | 474.173
1905.3479 | 620.7956 | 632.8165 | 538.8852 | 473.281
1906.3479 | 619.5735 | 633.3633 | 539.0869 | 473.0388
1907.3479 | 622.1923 | 634.6226 | 539.8585 | 473.1719
1908.3479 | 621.0299 | 637.911 | 538.7835 | 472.823
1909.3479 | 623.6998 | 630.3924 | 538.2463 | 472.5109
1910.3479 | 623.5039 | 635.0904 | 538.1789 | 471.5193
1911.3479 | 622.1737 | 631.6224 | 537.4326 | 470.9568
1912.3479 | 621.277 | 626.5055 | 537.0231 | 470.934
1913.3479 | 618.2032 | 619.1656 | 535.7569 | 471.1014
1914.3479 | 614.9396 | 622.6937 | 533.6043 | 470.6789
1915.3479 | 614.5963 | 627.4052 | 533.6872 | 470.0275
1916.3479 | 613.8242 | 630.9806 | 530.9582 | 469.0594
1917.3479 | 616.3673 | 630.9871 | 532.6866 | 468.4144
1918.3479 | 615.4319 | 633.4931 | 533.302 | 468.0684
1919.3479 | 619.4637 | 629.8828 | 534.8601 | 468.085
1920.3479 | 620.2835 | 628.6977 | 534.3789 | 468.1787
1921.3479 | 620.3218 | 633.8386 | 532.5888 | 467.6149
1922.3479 | 622.7197 | 638.5308 | 530.3328 | 467.492
1923.3479 | 624.2063 | 641.2198 | 530.2976 | 467.6304
1924.3479 | 625.3707 | 646.1704 | 531.7965 | 467.7861
1925.3479 | 625.3293 | 651.7599 | 533.6487 | 468.6566
1926.3479 | 625.5767 | 645.8318 | 534.4149 | 472.1468
1927.3479 | 625.4419 | 637.0165 | 535.5078 | 472.7371
1928.3479 | 623.5968 | 633.2762 | 535.4792 | 474.0707
1929.3479 | 623.5967 | 630.216 | 536.5504 | 473.7523
1930.3479 | 621.0344 | 626.2259 | 535.6193 | 472.5548
1931.3479 | 622.8289 | 621.4285 | 535.1204 | 473.4496
1932.3479 | 622.7661 | 616.9482 | 535.5051 | 472.7381
1933.3479 | 623.4138 | 615.2669 | 535.5927 | 472.7871
1934.3479 | 624.3393 | 612.6736 | 537.5436 | 471.5463
1935.3479 | 624.0383 | 609.6865 | 537.0215 | 471.5252
1936.3479 | 626.9727 | 614.4149 | 535.9696 | 471.9475
1937.3479 | 626.8415 | 620.1055 | 535.0995 | 472.6141
1938.3479 | 627.5734 | 620.2958 | 534.7128 | 473.4556
1939.3479 | 626.8867 | 633.9809 | 531.7069 | 473.0487
1940.3479 | 626.5728 | 651.5166 | 531.069 | 472.4355
1941.3479 | 626.3237 | 651.8182 | 531.9726 | 472.1558
1942.3479 | 625.3852 | 655.03 | 532.7832 | 474.0134
1943.3479 | 625.2182 | 652.8822 | 532.6115 | 473.6985
1944.3479 | 625.0522 | 657.2292 | 532.0415 | 472.9199
1945.3479 | 622.232 | 654.8001 | 533.1864 | 474.3458
1946.3479 | 621.3362 | 647.6264 | 534.1121 | 474.2677
1947.3479 | 621.838 | 644.8709 | 536.1252 | 474.0636
1948.3479 | 622.9398 | 644.0638 | 536.0744 | 472.5055
1949.3479 | 620.1892 | 647.4328 | 537.6693 | 472.559
1950.3479 | 622.6092 | 642.2788 | 536.0885 | 471.2786
1951.3479 | 619.8361 | 637.5833 | 536.5136 | 471.4194
1952.3479 | 622.3611 | 643.0832 | 537.2337 | 471.2434
1953.3479 | 622.608 | 641.7601 | 536.3999 | 470.9908
1954.3479 | 622.4008 | 647.65 | 537.2417 | 471.3614
1955.3479 | 622.0251 | 648.9798 | 538.1028 | 471.4204
1956.3479 | 621.2928 | 645.9123 | 539.2471 | 470.1796
1957.3479 | 622.3059 | 640.5681 | 538.0483 | 471.3845
1958.3479 | 624.5567 | 637.8164 | 538.219 | 473.4388
1959.3479 | 624.198 | 634.5912 | 537.8117 | 471.6391
1960.3479 | 625.4188 | 634.5572 | 538.3823 | 471.0848
1961.3479 | 626.6442 | 636.1324 | 539.4015 | 470.338
1962.3479 | 626.328 | 635.2803 | 540.7444 | 470.3187
1963.3479 | 626.5171 | 629.5282 | 541.5491 | 473.8712
1964.3479 | 627.5525 | 622.4063 | 540.6398 | 473.6999
1965.3479 | 628.2826 | 626.8805 | 539.5094 | 472.3208
1966.3479 | 629.21 | 629.9383 | 540.8336 | 474.4866
1967.3479 | 629.3561 | 625.8038 | 539.4882 | 474.4715
1968.3479 | 629.6136 | 623.3461 | 539.1438 | 472.912
1969.3479 | 631.8786 | 622.3351 | 537.804 | 473.0229
1970.3479 | 632.6912 | 633.0797 | 538.5563 | 473.8587
1971.3479 | 632.0464 | 635.7074 | 536.507 | 472.8284
1972.3479 | 629.096 | 642.3577 | 535.1623 | 472.6539
1973.3479 | 630.9464 | 634.1271 | 535.7093 | 474.4097
1974.3479 | 630.8825 | 632.0811 | 537.7656 | 474.8957
1975.3479 | 630.6638 | 631.8882 | 537.1228 | 473.9992
1976.3479 | 630.6869 | 626.1522 | 539.0691 | 475.2645
1977.3479 | 630.424 | 629.1547 | 539.7685 | 474.9968
1978.3479 | 628.8326 | 625.7426 | 539.1732 | 475.403
1979.3479 | 626.8439 | 626.0599 | 540.3077 | 474.5556
1980.3479 | 627.3896 | 626.1652 | 540.5558 | 475.375
1981.3479 | 625.6876 | 622.4291 | 541.3959 | 474.5494
1982.3479 | 624.3915 | 617.2679 | 540.6514 | 474.3591
1983.3479 | 623.3233 | 612.5498 | 539.3796 | 473.5596
1984.3479 | 624.0956 | 610.5267 | 539.9534 | 473.2058
1985.3479 | 625.5543 | 622.0498 | 538.4639 | 472.9117
1986.3479 | 626.0547 | 616.8935 | 540.3074 | 473.4153
1987.3479 | 627.3362 | 618.6902 | 540.6166 | 472.4056
1988.3479 | 628.802 | 621.2845 | 538.6968 | 473.0433
1989.3479 | 628.9978 | 624.2193 | 539.0927 | 473.8073
1990.3479 | 627.6309 | 622.1433 | 540.037 | 473.9733
1991.3479 | 628.4186 | 622.9391 | 540.8517 | 473.7833
1992.3479 | 628.406 | 616.8387 | 539.6913 | 473.7016
1993.3479 | 629.5126 | 610.7949 | 539.3067 | 472.5542
1994.3479 | 630.3979 | 604.9307 | 539.2796 | 471.7114
1995.3479 | 630.6141 | 602.8481 | 538.8617 | 471.7345
1996.3479 | 632.0822 | 598.5811 | 538.5801 | 472.4861
1997.3479 | 632.3518 | 595.1869 | 538.5093 | 471.4497
1998.3479 | 632.9937 | 593.2906 | 537.5386 | 470.4474
1999.3479 | 631.2018 | 590.6373 | 537.1357 | 471.159
2000.3479 | 633.3756 | 588.219 | 539.765 | 471.762
2001.3479 | 632.5394 | 583.8855 | 541.58 | 472.1924
2002.3479 | 633.6559 | 581.573 | 540.8427 | 472.2957
2003.3479 | 633.2752 | 579.928 | 539.4709 | 471.0321
2004.3479 | 633.1549 | 579.4957 | 539.9895 | 475.7301
2005.3479 | 633.1058 | 577.3798 | 540.0161 | 476.2982
2006.3479 | 634.8914 | 575.2055 | 540.8918 | 475.5537
2007.3479 | 635.5823 | 572.1324 | 540.6963 | 474.1505
2008.3479 | 635.178 | 569.0541 | 540.4812 | 473.445
2009.3479 | 636.4034 | 567.3916 | 541.22 | 472.986
2010.3479 | 634.725 | 567.1323 | 541.3489 | 473.5149
2011.3479 | 633.1442 | 565.5132 | 540.463 | 473.2132
2012.3479 | 634.2192 | 564.2031 | 541.2665 | 472.3328
2013.3479 | 633.3333 | 564.8629 | 542.632 | 473.0312
2014.3479 | 633.9569 | 563.3948 | 543.6167 | 473.1536
2015.3479 | 632.9106 | 563.2828 | 544.9096 | 472.9027
2016.3479 | 635.3963 | 563.4641 | 543.9403 | 471.4819
2017.3479 | 634.7165 | 561.9411 | 543.8286 | 471.2455
2018.3479 | 635.5203 | 561.122 | 543.5284 | 470.5933
2019.3479 | 636.9794 | 559.5179 | 545.0296 | 471.1552
2020.3479 | 637.5902 | 558.4387 | 545.7084 | 470.6007
2021.3479 | 636.5652 | 557.3921 | 544.0859 | 470.6186
2022.3479 | 635.3033 | 556.0263 | 543.4589 | 470.1979
2023.3479 | 629.7898 | 556.218 | 543.5989 | 471.0805
2024.3479 | 630.5058 | 556.2663 | 542.3384 | 471.8716
2025.3479 | 630.9974 | 555.2099 | 541.5784 | 471.6161
2026.3479 | 632.2056 | 554.9378 | 543.0043 | 471.7879
2027.3479 | 633.5553 | 554.1336 | 542.912 | 470.6293
2028.3479 | 633.5846 | 553.7543 | 541.7798 | 471.1025
2029.3479 | 634.9231 | 552.7853 | 541.2725 | 470.5554
2030.3479 | 636.1933 | 552.8274 | 541.1598 | 471.2177
2031.3479 | 635.6745 | 553.1414 | 541.6305 | 472.2511
2032.3479 | 634.7194 | 551.4698 | 540.7027 | 471.59
2033.3479 | 634.8005 | 551.9592 | 540.7721 | 471.432
2034.3479 | 635.0471 | 551.0335 | 541.4355 | 473.907
2035.3479 | 634.7297 | 550.3026 | 541.3525 | 473.3739
2036.3479 | 631.8417 | 548.8292 | 539.6296 | 472.3988
2037.3479 | 631.9071 | 549.2932 | 538.921 | 472.7352
2038.3479 | 630.9277 | 548.7276 | 539.5214 | 472.6338
2039.3479 | 631.467 | 548.097 | 538.2722 | 471.8509
2040.3479 | 629.7794 | 546.131 | 539.3589 | 470.3605
2041.3479 | 631.1513 | 545.1653 | 539.8098 | 469.6113
2042.3479 | 632.4515 | 545.1491 | 538.3591 | 469.69
2043.3479 | 633.1302 | 546.1848 | 539.8062 | 468.8937
2044.3479 | 634.2693 | 544.8982 | 540.0234 | 469.5389
2045.3479 | 633.6121 | 543.8207 | 541.2111 | 469.1882
2046.3479 | 631.217 | 543.5744 | 540.4491 | 468.9771
2047.3479 | 630.0136 | 543.0917 | 539.9595 | 467.7867
2048.3479 | 631.875 | 542.4204 | 539.3646 | 467.0628
2049.3479 | 633.6816 | 544.4877 | 540.2794 | 466.0302
2050.3479 | 634.3503 | 544.1073 | 538.7723 | 465.8002
2051.3479 | 634.5612 | 543.793 | 539.2067 | 465.4228
2052.3479 | 631.92 | 541.9015 | 536.5752 | 465.6446
2053.3479 | 630.8286 | 542.2904 | 536.2451 | 467.2145
2054.3479 | 630.4324 | 543.1211 | 537.4201 | 466.5762
2055.3479 | 630.3971 | 543.4754 | 535.2232 | 466.5207
2056.3479 | 630.2682 | 543.6103 | 535.4801 | 466.0229
2057.3479 | 630.1779 | 542.803 | 533.0012 | 464.8661
2058.3479 | 631.7178 | 540.7605 | 533.9921 | 464.4702
2059.3479 | 631.5953 | 539.8439 | 535.188 | 464.3657
2060.3479 | 631.3906 | 538.7468 | 534.0398 | 465.1839
2061.3479 | 631.1781 | 536.6437 | 533.5784 | 467.756
2062.3479 | 628.9548 | 535.7054 | 535.9547 | 467.0007
2063.3479 | 628.608 | 533.8233 | 535.5742 | 467.8821
2064.3479 | 628.0634 | 533.0095 | 535.4557 | 467.5054
2065.3479 | 626.3828 | 533.3043 | 535.1732 | 466.9899
2066.3479 | 619.5501 | 534.4157 | 534.7132 | 465.9939
2067.3479 | 616.4896 | 536.8203 | 532.0347 | 465.0052
2068.3479 | 616.397 | 537.4314 | 532.2916 | 464.1007
2069.3479 | 618.622 | 537.3625 | 533.108 | 463.7752
2070.3479 | 615.9395 | 537.2012 | 534.8977 | 463.5514
2071.3479 | 619.5179 | 536.9016 | 533.4479 | 463.4804
2072.3479 | 622.6634 | 538.0161 | 532.1252 | 463.162
2073.3479 | 624.3004 | 538.594 | 533.4197 | 463.2539
2074.3479 | 624.6304 | 538.047 | 532.1151 | 462.8033
2075.3479 | 624.1234 | 538.4356 | 532.1737 | 462.3088
2076.3479 | 624.9476 | 537.6257 | 532.236 | 462.2717
2077.3479 | 625.4264 | 537.0609 | 531.8368 | 461.5458
2078.3479 | 627.1056 | 536.7032 | 533.001 | 461.4341
2079.3479 | 626.3521 | 536.4823 | 532.6856 | 460.959
2080.3479 | 627.5358 | 535.7509 | 531.8106 | 461.1855
2081.3479 | 627.695 | 535.7383 | 530.4795 | 461.7657
2082.3479 | 626.6271 | 535.5772 | 532.0178 | 461.4909
2083.3479 | 626.9821 | 535.3252 | 531.6568 | 462.1836
2084.3479 | 626.2015 | 534.8915 | 530.4894 | 464.0645
2085.3479 | 627.3395 | 533.8675 | 532.0848 | 463.4883
2086.3479 | 627.8923 | 533.7066 | 530.8408 | 463.6405
2087.3479 | 628.2298 | 533.5993 | 530.6273 | 464.1344
2088.3479 | 630.1414 | 533.7627 | 532.4045 | 465.2542
2089.3479 | 629.3037 | 534.4038 | 530.9506 | 464.5108
2090.3479 | 629.987 | 535.0024 | 533.3098 | 463.5748
2091.3479 | 630.2526 | 535.5241 | 534.3328 | 463.1769
2092.3479 | 629.4971 | 534.6888 | 535.9067 | 462.4792
2093.3479 | 626.9553 | 534.1091 | 536.2452 | 461.5088
2094.3479 | 628.905 | 533.6777 | 537.1002 | 460.6051
2095.3479 | 630.0549 | 534.1184 | 537.1769 | 459.9672
2096.3479 | 628.4865 | 534.4894 | 538.3699 | 459.8409
2097.3635 | 626.893 | 533.4745 | 537.8304 | 459.7951
2098.3479 | 627.5003 | 533.2564 | 540.3003 | 459.3767
2099.3479 | 624.2778 | 532.2048 | 542.2568 | 458.728
2100.3479 | 625.3688 | 530.5533 | 541.0526 | 458.3777
2101.3479 | 625.0366 | 529.4568 | 539.9171 | 459.6652
2102.3479 | 625.2205 | 527.8832 | 538.5447 | 458.449
2103.3479 | 621.8098 | 527.7466 | 538.113 | 457.6073
2104.3479 | 621.6089 | 528.7117 | 538.0044 | 457.9021
2105.3479 | 620.2441 | 528.7415 | 538.2766 | 457.7716
2106.3479 | 620.1497 | 528.4229 | 539.183 | 457.5231
2107.3479 | 621.3599 | 527.2465 | 539.3509 | 457.5204
2108.3479 | 621.0481 | 526.6808 | 536.043 | 456.0443
2109.3479 | 622.3658 | 527.0005 | 536.7388 | 455.6245
2110.3479 | 621.7323 | 526.9146 | 537.192 | 455.9908
2111.3479 | 621.91 | 526.9099 | 536.7832 | 457.3671
2112.3479 | 623.4852 | 527.4227 | 536.0811 | 456.6498
2113.3479 | 623.9006 | 527.6643 | 536.3984 | 456.4811
2114.3479 | 626.4326 | 526.1663 | 536.048 | 456.5401
2115.3479 | 627.2908 | 525.6006 | 535.8299 | 456.5773
2116.3479 | 627.2099 | 525.6782 | 534.9672 | 456.7338
2117.3479 | 626.811 | 525.6598 | 535.6052 | 457.0614
2118.3479 | 626.1559 | 525.7977 | 535.7449 | 456.9059
2119.3479 | 626.6567 | 525.2861 | 536.1241 | 456.5927
2120.3479 | 626.5188 | 525.7741 | 537.0012 | 457.2896
2121.3479 | 627.9656 | 525.7264 | 536.8532 | 456.5353
2122.3479 | 628.4843 | 524.9803 | 536.0018 | 455.7173
2123.3479 | 627.6254 | 524.7048 | 534.0004 | 455.3627
2124.3479 | 626.9358 | 523.7978 | 532.7467 | 455.353
2125.3479 | 626.1384 | 523.6615 | 532.5589 | 455.3371
2126.3479 | 624.7006 | 525.0047 | 532.3118 | 455.124
2127.3479 | 622.6319 | 526.2658 | 533.9238 | 455.1697
2128.3479 | 623.4945 | 526.875 | 534.097 | 454.801
2129.3479 | 623.6768 | 527.0279 | 533.4621 | 454.3055
2130.3479 | 622.7955 | 527.1847 | 533.3623 | 455.7547
2131.3479 | 625.7657 | 527.2481 | 536.5994 | 457.3458
2132.3479 | 627.7078 | 528.9249 | 536.9143 | 458.4462
2133.3479 | 628.9126 | 530.2673 | 537.9612 | 458.4213
2134.3479 | 631.4002 | 529.9458 | 540.9837 | 458.9428
2135.3479 | 632.2149 | 531.3 | 543.3435 | 459.2044
2136.3479 | 634.6321 | 532.5014 | 544.1329 | 458.9888
2137.3479 | 636.047 | 533.0067 | 546.7801 | 459.9344
2138.3479 | 639.5274 | 534.6946 | 547.7034 | 460.8081
2139.3479 | 640.8666 | 535.5909 | 550.2437 | 461.1426
2140.3479 | 642.2911 | 537.4109 | 554.1695 | 461.0086
2141.3479 | 642.7422 | 538.2833 | 557.0293 | 461.8076
2142.3479 | 643.5856 | 538.5252 | 556.3255 | 461.8647
2143.3479 | 641.6653 | 539.6291 | 556.8316 | 462.0417
2144.3479 | 642.4414 | 540.8914 | 557.2537 | 461.9709
2145.3479 | 641.7228 | 541.7791 | 557.7367 | 461.925
2146.3479 | 640.8125 | 542.1476 | 559.3251 | 462.8069
2147.3479 | 640.4426 | 541.9423 | 562.4008 | 465.4153
2148.3479 | 640.8272 | 541.7206 | 560.5711 | 464.7217
2149.3479 | 640.5258 | 543.1132 | 563.1369 | 465.1214
2150.3479 | 640.5345 | 545.1124 | 562.5118 | 465.1671
2151.3479 | 640.5551 | 545.8396 | 563.2454 | 466.6693
2152.3479 | 641.3992 | 545.253 | 562.7281 | 467.4351
2153.3479 | 641.8131 | 545.9932 | 564.5237 | 468.0871
2154.3479 | 643.1106 | 544.1695 | 565.2408 | 468.0122
2155.3479 | 644.3491 | 544.5773 | 564.9807 | 467.3653
2156.3479 | 645.8404 | 543.4389 | 564.5646 | 466.4678
2157.3479 | 643.3545 | 543.6011 | 566.5806 | 465.9394
2158.3479 | 643.5889 | 542.9832 | 566.1147 | 465.8419
2159.3479 | 642.6535 | 542.7648 | 565.5283 | 464.8885
2160.3479 | 643.8546 | 543.2975 | 566.0979 | 464.977
2161.3479 | 645.5304 | 543.579 | 566.9142 | 465.2959
2162.3479 | 644.738 | 543.3627 | 567.9885 | 464.5043
2163.3479 | 642.389 | 545.0527 | 569.1555 | 464.4957
2164.3479 | 643.3112 | 544.7333 | 568.9417 | 464.2452
2165.3479 | 643.2521 | 543.6856 | 568.8056 | 464.9829
2166.3479 | 644.82 | 543.3485 | 568.1145 | 465.2066
2167.3479 | 644.9061 | 542.6872 | 569.0898 | 464.9383
2168.3479 | 646.4255 | 542.7877 | 571.1033 | 464.8066
2169.3479 | 647.4482 | 542.1395 | 571.7756 | 465.1409
2170.3479 | 645.6683 | 541.3076 | 571.9314 | 464.7088
2171.3479 | 645.2518 | 541.2469 | 571.7681 | 464.7669
2172.3479 | 644.8938 | 540.6654 | 569.4487 | 465.0727
2173.3479 | 643.9048 | 539.3814 | 567.336 | 465.9633
2174.3479 | 644.8195 | 538.2072 | 566.3833 | 467.0586
2175.3479 | 641.6449 | 536.4931 | 565.8132 | 469.8758
2176.3479 | 642.4949 | 535.4328 | 569.0507 | 470.9723
2177.3479 | 641.2401 | 534.2711 | 569.063 | 471.4734
2178.3479 | 639.4945 | 534.2382 | 569.4297 | 474.3219
2179.3479 | 638.5995 | 532.6649 | 568.0146 | 474.694
2180.3479 | 636.2997 | 530.5942 | 567.0471 | 473.906
2181.3479 | 635.5894 | 530.074 | 567.8881 | 473.3358
2182.3479 | 636.6868 | 529.812 | 566.4579 | 472.5125
2183.3479 | 637.4386 | 529.6237 | 565.5232 | 471.733
2184.3479 | 638.5343 | 529.383 | 565.8103 | 471.2476
2185.3479 | 639.3476 | 529.155 | 565.5695 | 470.9516
2186.3479 | 638.5786 | 529.0552 | 566.1218 | 469.8811
2187.3479 | 638.6719 | 529.6633 | 563.8081 | 468.2519
2188.3479 | 638.1967 | 530.3776 | 563.5236 | 467.7831
2189.3479 | 639.9541 | 530.2185 | 563.2496 | 467.3586
2190.3479 | 641.8596 | 531.1867 | 563.0345 | 466.4518
2191.3479 | 640.0329 | 532.7782 | 561.4523 | 465.8667
2192.3479 | 641.6853 | 532.7635 | 558.7232 | 465.8308
2193.3479 | 641.4909 | 532.2441 | 559.0016 | 465.6585
2194.3479 | 641.9316 | 532.0208 | 561.0643 | 465.1397
2195.3479 | 642.4826 | 533.1593 | 562.5412 | 464.5436
2196.3479 | 640.421 | 534.312 | 563.8674 | 464.3354
2197.3479 | 639.3391 | 535.0685 | 565.1765 | 464.3141
2198.3635 | 641.6782 | 535.3207 | 567.0823 | 464.1694
2199.3479 | 640.899 | 535.5423 | 566.2195 | 464.6763
2200.3479 | 642.8719 | 535.9568 | 563.5497 | 463.5662
2201.3479 | 641.9789 | 536.9258 | 563.141 | 462.8354
2202.3479 | 644.7622 | 538.193 | 561.2382 | 463.1665
2203.3479 | 644.7649 | 539.0939 | 561.1023 | 462.6947
2204.3479 | 645.5915 | 539.462 | 561.9408 | 463.9197
2205.3479 | 643.5072 | 538.5054 | 561.8086 | 463.4681
2206.3479 | 643.9662 | 539.475 | 562.362 | 462.1518
2207.3479 | 644.4413 | 538.9102 | 561.6394 | 463.3586
2208.3479 | 643.4199 | 538.2064 | 560.28 | 462.6432
2209.3479 | 644.644 | 538.4975 | 560.6936 | 462.027
2210.3479 | 644.9499 | 537.8021 | 560.5077 | 464.0535
2211.3479 | 645.0487 | 536.7551 | 562.2902 | 464.8294
2212.3479 | 643.0472 | 535.7657 | 564.1303 | 466.0709
2213.3479 | 643.3874 | 535.1973 | 564.1181 | 465.55
2214.3479 | 643.2313 | 534.5612 | 564.7147 | 464.8741
2215.3479 | 640.5777 | 535.4337 | 565.6267 | 463.9938
2216.3479 | 641.7877 | 535.8202 | 564.7389 | 463.2743
2217.3479 | 641.9229 | 535.541 | 563.3608 | 463.5026
2218.3479 | 641.3144 | 536.367 | 563.5379 | 462.4834
2219.3479 | 641.9269 | 537.1586 | 564.9434 | 461.8078
2220.3479 | 638.753 | 537.6314 | 565.2082 | 461.3886
2221.3479 | 636.1933 | 539.4852 | 566.0455 | 460.5763
2222.3479 | 639.2059 | 540.1993 | 566.5615 | 460.5565
2223.3479 | 641.2722 | 540.2483 | 567.9116 | 460.5008
2224.3479 | 640.0437 | 541.2365 | 567.9082 | 459.7867
2225.3479 | 639.1511 | 542.0881 | 567.8779 | 459.0387
2226.3479 | 633.9296 | 542.4259 | 568.401 | 459.3427
2227.3479 | 632.7018 | 544.1215 | 568.6945 | 458.5025
2228.3479 | 632.3979 | 545.219 | 566.4193 | 457.5845
2229.3479 | 634.6931 | 544.3884 | 564.3442 | 456.9067
2230.3479 | 635.5865 | 543.6999 | 561.5669 | 456.5383
2231.3479 | 637.6984 | 541.802 | 559.642 | 456.8857
2232.3479 | 636.2459 | 540.7826 | 559.3117 | 456.3631
2233.3479 | 638.9551 | 540.0591 | 559.4974 | 456.0067
2234.3479 | 640.3934 | 539.2563 | 559.234 | 455.9875
2235.3479 | 639.8429 | 538.9609 | 561.4133 | 458.2193
2236.3479 | 637.8443 | 539.6799 | 562.8197 | 458.7837
2237.3479 | 634.8416 | 540.0153 | 562.1946 | 457.6692
2238.3479 | 634.8402 | 540.2204 | 563.233 | 457.712
2239.3479 | 635.7632 | 540.4183 | 564.1484 | 457.3552
2240.3479 | 634.4702 | 541.5581 | 564.7306 | 457.1853
2241.3479 | 634.2642 | 542.4546 | 564.0893 | 456.2727
2242.3479 | 635.7608 | 543.0566 | 563.0962 | 456.2584
2243.3479 | 634.5125 | 542.2687 | 564.1452 | 457.7134
2244.3479 | 634.7965 | 541.8832 | 564.0856 | 457.4675
2245.3479 | 634.2793 | 541.7146 | 563.8618 | 457.5963
2246.3479 | 633.4708 | 540.8808 | 562.7188 | 457.781
2247.3479 | 632.7216 | 540.9587 | 562.2464 | 458.2859
2248.3479 | 629.8351 | 541.6224 | 563.9708 | 458.5386
2249.3479 | 629.9512 | 542.263 | 563.2135 | 457.6853
2250.3479 | 632.4951 | 541.6568 | 562.3909 | 456.8619
2251.3479 | 635.0883 | 540.7886 | 560.0216 | 456.4041
2252.3479 | 636.4822 | 540.0463 | 562.0692 | 457.0133
2253.3479 | 637.8897 | 539.9952 | 561.2039 | 455.9008
2254.3479 | 637.408 | 541.0684 | 560.0593 | 455.575
2255.3479 | 639.1898 | 541.5167 | 560.6857 | 455.2383
2256.3479 | 636.775 | 542.7054 | 559.6623 | 455.219
2257.3479 | 636.998 | 542.8553 | 560.6137 | 455.0493
2258.3479 | 634.9814 | 543.3323 | 564.1246 | 456.0962
2259.3479 | 636.7963 | 544.5079 | 563.7857 | 455.8068
2260.3479 | 639.0427 | 544.4575 | 564.991 | 456.7695
2261.3479 | 640.7342 | 543.8106 | 566.0711 | 458.4431
2262.3479 | 642.3569 | 542.1585 | 566.3163 | 458.7999
2263.3479 | 640.4208 | 542.363 | 568.3339 | 458.7697
2264.3479 | 640.6162 | 542.2652 | 568.4906 | 458.2662
2265.3479 | 639.7767 | 542.5818 | 568.3412 | 458.4403
2266.3479 | 643.5934 | 542.4672 | 569.8169 | 458.9269
2267.3479 | 644.6585 | 543.539 | 568.0054 | 459.5087
2268.3479 | 644.0615 | 543.8273 | 567.4979 | 458.6936
2269.3479 | 644.6013 | 545.3296 | 568.4906 | 458.5071
2270.3479 | 645.5837 | 546.1518 | 571.8969 | 458.7746
2271.3479 | 646.2107 | 546.6436 | 571.1194 | 458.729
2272.3479 | 647.3657 | 546.8022 | 570.1081 | 458.694
2273.3479 | 645.9723 | 546.2111 | 569.2442 | 458.871
2274.3479 | 646.0198 | 545.056 | 568.0028 | 460.9855
2275.3479 | 646.8057 | 543.7218 | 568.3746 | 460.9797
2276.3479 | 645.2387 | 543.1993 | 568.7895 | 461.1492
2277.3479 | 644.6495 | 543.1888 | 568.55 | 460.6769
2278.3479 | 646.0681 | 543.5836 | 568.2186 | 460.3056
2279.3479 | 645.4747 | 543.7705 | 567.8395 | 460.8136
2280.3479 | 647.976 | 544.1625 | 564.4589 | 459.775
2281.3479 | 651.6488 | 545.069 | 564.8208 | 460.1089
2282.3479 | 651.9686 | 546.946 | 566.6861 | 459.7549
2283.3479 | 654.4149 | 547.5518 | 568.3086 | 460.0922
2284.3479 | 656.2599 | 547.7097 | 568.4042 | 460.9853
2285.3479 | 657.9366 | 548.138 | 569.3877 | 460.4071
2286.3479 | 658.9817 | 547.3065 | 569.7854 | 460.8557
2287.3479 | 657.0391 | 547.4165 | 568.6729 | 460.3726
2288.3479 | 657.7453 | 546.914 | 567.4056 | 460.8283
2289.3479 | 656.79 | 546.0609 | 568.7773 | 460.6081
2290.3479 | 654.931 | 545.6677 | 570.7133 | 461.1722
2291.3479 | 654.2487 | 545.0212 | 571.9746 | 464.3903
2292.3479 | 652.0066 | 544.5836 | 570.5217 | 466.4749
2293.3479 | 649.9624 | 544.3136 | 571.9031 | 467.3443
2294.3479 | 647.468 | 543.3273 | 571.0473 | 467.2607
2295.3479 | 647.4895 | 542.512 | 569.7543 | 468.7905
2296.3479 | 647.8745 | 541.0593 | 568.5624 | 469.4018
2297.3479 | 648.1755 | 539.5852 | 569.5475 | 470.2149
2298.3479 | 648.5087 | 538.6358 | 569.5471 | 469.4465
2299.3479 | 650.1413 | 539.823 | 569.7528 | 470.0568
2300.3479 | 650.7851 | 540.2478 | 568.4391 | 471.5615
2301.3479 | 650.0814 | 539.2392 | 569.0506 | 474.2283
2302.3479 | 649.4227 | 538.1556 | 568.0848 | 472.9392
2303.3479 | 649.5544 | 538.1236 | 566.7455 | 471.3417
2304.3479 | 649.1597 | 538.1467 | 567.2964 | 470.3163
2305.3479 | 648.2931 | 537.6477 | 567.5085 | 469.2663
2306.3479 | 646.9138 | 537.3054 | 567.8566 | 469.5107
2307.3479 | 647.5489 | 538.0718 | 568.4895 | 468.9908
2308.3479 | 648.5253 | 539.4471 | 568.4719 | 468.2059
2309.3479 | 649.0616 | 540.6772 | 568.8404 | 467.8906
2310.3479 | 648.3805 | 540.673 | 569.2103 | 468.6794
2311.3479 | 649.1898 | 539.8899 | 571.1203 | 468.7392
2312.3479 | 650.9335 | 540.8674 | 571.0027 | 468.1283
2313.3479 | 651.3927 | 540.7374 | 570.6447 | 468.2748
2314.3479 | 652.4307 | 540.6853 | 571.5079 | 467.4145
2315.3479 | 650.2852 | 542.4227 | 572.9489 | 466.3729
2316.3479 | 651.8888 | 543.9996 | 571.1352 | 465.1856
2317.3479 | 652.0915 | 544.7534 | 569.023 | 464.7435
2318.3479 | 652.6489 | 544.6924 | 568.9707 | 464.4087
2319.3479 | 651.0401 | 543.3197 | 571.3679 | 464.1595
2320.3479 | 652.3019 | 542.9258 | 571.5936 | 463.4479
2321.3479 | 648.7869 | 544.0023 | 571.0537 | 462.6893
2322.3479 | 647.3393 | 544.8621 | 570.1793 | 461.4619
2323.3479 | 649.9941 | 545.474 | 565.2591 | 460.6117
2324.3479 | 652.9565 | 547.3377 | 565.9304 | 460.3293
2325.3479 | 652.3853 | 548.5731 | 565.3244 | 459.8356
2326.3479 | 653.6896 | 549.3297 | 565.1204 | 459.2687
2327.3479 | 653.7492 | 549.7368 | 566.0205 | 458.9421
2328.3479 | 653.2166 | 550.0133 | 566.8806 | 460.179
2329.3479 | 652.4443 | 549.0479 | 568.2847 | 461.6067
2330.3479 | 650.5219 | 547.3733 | 569.4538 | 463.6419
2331.3479 | 651.9623 | 545.9882 | 568.6768 | 465.8158
2332.3479 | 650.1334 | 544.8838 | 569.2979 | 466.2726
2333.3479 | 649.2755 | 545.0371 | 569.1631 | 465.4485
2334.3479 | 648.0255 | 545.1149 | 569.28 | 466.677
2335.3479 | 648.9529 | 544.3818 | 569.1407 | 467.4341
2336.3479 | 647.0824 | 543.9943 | 569.8967 | 467.7319
2337.3479 | 644.3106 | 543.7441 | 570.8719 | 468.8835
2338.3479 | 644.57 | 543.3472 | 570.6308 | 468.4616
2339.3479 | 642.8805 | 543.7993 | 569.4259 | 467.729
2340.3479 | 641.9413 | 544.8407 | 568.9009 | 467.5664
2341.3479 | 642.0839 | 544.2909 | 570.6445 | 468.7007
2342.3479 | 644.4787 | 542.7567 | 570.8144 | 469.3831
2343.3479 | 645.4338 | 542.2156 | 571.575 | 469.4765
2344.3479 | 645.8988 | 542.312 | 571.9903 | 469.7277
2345.3479 | 642.6486 | 541.6728 | 572.7907 | 470.9577
2346.3479 | 642.7336 | 540.5597 | 572.2168 | 471.5779
2347.3479 | 642.7334 | 540.5387 | 571.42 | 470.7636
2348.3479 | 642.6326 | 540.4028 | 571.9723 | 473.4917
2349.3479 | 642.174 | 540.0463 | 572.4542 | 474.9811
2350.3479 | 642.413 | 538.8835 | 572.7975 | 477.6909
2351.3479 | 642.6359 | 536.7513 | 571.7962 | 477.6492
2352.3479 | 642.9021 | 535.5078 | 571.8531 | 479.1471
2353.3479 | 641.8513 | 535.0856 | 571.618 | 481.5405
2354.3479 | 641.3574 | 534.3077 | 571.1716 | 480.5527
2355.3479 | 642.4802 | 534.3213 | 571.7365 | 480.1873
2356.3479 | 641.0925 | 534.221 | 569.8615 | 478.1496
2357.3479 | 642.4525 | 535.404 | 567.4641 | 476.6185
2358.3479 | 641.9813 | 536.9454 | 568.1555 | 475.3138
2359.3479 | 640.9422 | 537.0288 | 568.5703 | 474.5937
2360.3479 | 638.0061 | 537.05 | 568.5165 | 473.676
2361.3479 | 638.1009 | 537.4584 | 568.3064 | 472.3111
2362.3479 | 637.8888 | 537.4818 | 567.2122 | 470.8117
2363.3479 | 636.483 | 537.512 | 565.3408 | 469.6864
2364.3479 | 637.1772 | 536.8108 | 565.7696 | 469.955
2365.3479 | 637.7666 | 537.3911 | 566.5052 | 469.1072
2366.3479 | 637.1088 | 537.7026 | 564.4071 | 467.9011
2367.3479 | 634.8454 | 538.0807 | 562.3012 | 466.5752
2368.3479 | 634.0343 | 537.588 | 560.6406 | 465.3742
2369.3479 | 637.1658 | 538.0787 | 560.8505 | 464.9127
2370.3479 | 637.6082 | 539.1555 | 560.0885 | 463.5545
2371.3479 | 639.2046 | 540.0836 | 557.3124 | 462.7636
2372.3479 | 639.7101 | 540.1959 | 558.1436 | 462.6037
2373.3479 | 641.7296 | 539.1578 | 560.6616 | 462.6389
2374.3479 | 641.108 | 538.9052 | 562.4215 | 463.2337
2375.3479 | 641.8273 | 537.9771 | 560.9396 | 463.7277
2376.3479 | 642.7445 | 537.5885 | 561.8058 | 464.3149
2377.3479 | 643.1094 | 537.277 | 561.7472 | 464.2329
2378.3635 | 644.207 | 536.7988 | 561.303 | 463.9632
2379.3479 | 645.5585 | 538.0889 | 560.3762 | 462.766
2380.3479 | 640.5725 | 540.3942 | 561.4145 | 463.2138
2381.3479 | 642.6231 | 542.2293 | 565.0538 | 462.5182
2382.3479 | 643.1834 | 541.5432 | 566.1001 | 462.2044
2383.3479 | 644.8078 | 542.1168 | 567.6245 | 462.1032
2384.3479 | 645.3417 | 541.9933 | 566.2842 | 464.2496
2385.3479 | 645.134 | 541.0565 | 569.0827 | 466.3294
2386.3479 | 645.9885 | 540.4597 | 568.3546 | 467.1046
2387.3479 | 646.642 | 540.9641 | 569.0315 | 467.6878
2388.3479 | 649.2196 | 540.9607 | 569.6337 | 467.7416
2389.3479 | 648.6308 | 541.8923 | 570.1485 | 467.3394
2390.3479 | 647.6123 | 542.4249 | 568.6534 | 466.9228
2391.3479 | 646.6611 | 543.2328 | 567.5859 | 465.9539
2392.3479 | 646.3556 | 544.4463 | 566.8835 | 465.0679
2393.3479 | 646.7422 | 545.6081 | 566.7564 | 464.5001
2394.3479 | 647.6438 | 546.3025 | 566.3553 | 463.7331
2395.3479 | 648.9016 | 545.8319 | 565.3549 | 462.575
2396.3479 | 648.3806 | 546.9765 | 566.2847 | 461.4278
2397.3479 | 649.5046 | 546.5073 | 565.3149 | 460.4949
2398.3479 | 651.8038 | 546.7026 | 566.0282 | 460.0586
2399.3479 | 652.8072 | 546.4213 | 565.0673 | 461.8111
2400.3479 | 650.5914 | 544.7421 | 564.0988 | 461.4068