## Test Conditions
DESIREE-FIRE Intermediate Scale Test 7 - Circuit Simulator Data Only
Test Date: | 2010-03-09
DCSim DAQ Start Time | 13:14
DCSim Time for Synchronization | 13:16
Heat Source Synchronization | 0:00 | hour:minutes:seconds
Heat Source DAQ Start Time | 13:15
Fire Time | 14:00
Offset | 0:46 | hour:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 2760 | seconds
Heat Source Offset | 0:45 | hour:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 2695 | seconds
Heat Source Stop Time | 14:40
Test Duration | 0:40 | hour:minutes:seconds
| 2400 | seconds
CT500 turns | 2 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 turns | 5 | 1 or 5
Pre-Test Baseline: | Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
SOV 1 | PE/PVC, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 1 represents the air temperature in the middle of the tray located in B Position. It is labeled as "B Position - Middle".
SOV 2 | PE/PVC, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 8, 9, and 10 represents the air temperature 3', 5', and 7' down the tray located in D Position. These are labeled as "D Position - 3'", "D Position - Middle", " D Position - 7'", respectively.
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | SOV-1_CT500 | SOV-1_CT35_1_P | SOV-1_CT35_2_S1 | SOV-1_CT35_3_G | SOV-1_CT35_4_S2 | SOV-1_CT35_5_N | SOV-2_CT500 | SOV-2_CT35_1_P | SOV-2_CT35_2_S1 | SOV-2_CT35_3_G | SOV-2_CT35_4_S2 | SOV-2_CT35_5_N | SOV-1_VT7_1_R | SOV-1_VT7_2_SP | SOV-1_VT7_3_S | SOV-1_VTU_1_P | SOV-1_VTU_2_S1 | SOV-1_VTU_3_G | SOV-1_VTU_4_N | SOV-2_VT7_1_R | SOV-2_VT7_2_SP | SOV-2_VT7_3_S | SOV-2_VTU_1_P | SOV-2_VTU_2_S1 | SOV-2_VTU_3_G | SOV-2_VTU_4_N | {SOV1} V(N) - V(Batt -) | {SOV1} V(P) - V(Batt +) | {SOV1} V(R) - V(Batt -) | {SOV1} V(S) - V(Batt -) | {SOV1} V(S) - V(N) | {SOV1} V(S1) - V(Batt +) | {SOV1} V(G) - V(Batt +) | {SOV2} V(N) - V(Batt -) | {SOV2} V(P) - V(Batt +) | {SOV2} V(R) - V(Batt -) | {SOV2} V(S) - V(Batt -) | {SOV2} V(S) - V(N) | {SOV2} V(S1) - V(Batt +) | {SOV2} V(G) - V(Batt +) | {SOV1} V(P) - V(Batt -) | {SOV1} V(S1) - V(Batt -) | {SOV1} V(G) - V(Batt -) | {SOV1} V(SP) - V(Batt -) | {SOV1} V(N) - V(Batt +) | {SOV2} V(P) - V(Batt -) | {SOV2} V(S1) - V(Batt -) | {SOV1} V(G) - V(Batt -) | {SOV2} V(SP) - V(Batt -) | {SOV2} V(N) - V(Batt +)
-0.8125 | 121.9803 | -60.9421 | 60.9146 | 1.4211e-13 | -0.018925 | -0.00049144 | 0.06474 | -0.0074183 | 0.062003 | -0.22533 | -0.0012156 | -0.00033976 | 0.063028 | 0.020906 | 0.061812 | -60.8045 | -0.003172 | -60.9224 | 60.8943 | 60.6803 | 60.7901 | -60.9673 | -60.8775 | 0.014095 | -60.9532 | 60.7313 | 60.845 | 60.6651 | -61.1494 | -0.025255 | -0.020288 | 0.13756 | 0.019646 | 0.044901 | -0.23434 | -0.12448 | -0.20734 | -0.18336 | 0.064599 | -0.011114 | 0.19622 | -0.069592 | -0.24954 | 121.8364 | 121.6223 | 121.7322 | 60.9389 | -121.8819 | 121.6733 | 121.7871 | 121.6072 | 60.9562 | -122.064
0.9375 | 122.0352 | -60.9192 | 60.9375 | 1.4211e-13 | -0.018498 | -0.00049144 | 0.064953 | -0.0072047 | 0.062217 | -0.23296 | -0.001002 | -0.00033976 | 0.063028 | 0.020478 | 0.061812 | -60.7999 | -0.003172 | -60.9224 | 60.8943 | 60.6757 | 60.781 | -60.9673 | -60.8821 | 0.014095 | -60.9486 | 60.7313 | 60.845 | 60.6697 | -61.1448 | -0.048144 | -0.043176 | 0.11925 | -0.003243 | 0.044901 | -0.26181 | -0.15652 | -0.22565 | -0.20625 | 0.037132 | -0.029424 | 0.19622 | -0.09248 | -0.26785 | 121.8135 | 121.5949 | 121.7002 | 60.916 | -121.9048 | 121.6504 | 121.7642 | 121.5888 | 60.9333 | -122.0823
2.6094 | 122.0718 | -60.8917 | 60.9055 | 1.4211e-13 | -0.018711 | -0.00070504 | 0.064312 | -0.0078457 | 0.061789 | -0.24059 | -0.00078837 | -0.00055336 | 0.062815 | 0.020478 | 0.061598 | -60.8045 | -0.007751 | -60.9133 | 60.8989 | 60.6894 | 60.7856 | -60.9673 | -60.8866 | 0.018674 | -60.9486 | 60.7267 | 60.8404 | 60.6605 | -61.154 | -0.075609 | -0.006555 | 0.087202 | -0.021551 | 0.054058 | -0.21603 | -0.1199 | -0.26227 | -0.17878 | 0.005088 | -0.056889 | 0.20538 | -0.065016 | -0.24496 | 121.7906 | 121.5811 | 121.6773 | 60.884 | -121.8728 | 121.6184 | 121.7322 | 121.5522 | 60.9104 | -122.0595
4.3438 | 121.9666 | -60.9375 | 60.9375 | 1.4211e-13 | -0.018711 | -0.00027784 | 0.064312 | -0.0072047 | 0.062003 | -0.23296 | -0.001002 | -0.00055336 | 0.062815 | 0.020906 | 0.061598 | -60.8045 | 0.001407 | -60.9179 | 60.8989 | 60.6848 | 60.7901 | -60.9673 | -60.8866 | 0.009516 | -60.9486 | 60.7313 | 60.8404 | 60.6697 | -61.1494 | -0.029833 | -0.038598 | 0.13298 | 0.019646 | 0.049479 | -0.25265 | -0.14737 | -0.21191 | -0.20625 | 0.050864 | -0.011113 | 0.2008 | -0.097059 | -0.26785 | 121.8364 | 121.6223 | 121.7276 | 60.9389 | -121.9048 | 121.6688 | 121.7779 | 121.6072 | 60.947 | -122.0869
6.0938 | 122.1222 | -60.9146 | 60.8826 | 1.4211e-13 | -0.018711 | -0.00049144 | 0.064526 | -0.0072047 | 0.062217 | -0.24059 | -0.00057477 | -0.00012596 | 0.062387 | 0.020906 | 0.061385 | -60.7999 | -0.007751 | -60.9133 | 60.8943 | 60.6757 | 60.781 | -60.9719 | -60.8683 | 0.014095 | -60.944 | 60.7313 | 60.845 | 60.6559 | -61.1494 | -0.0573 | 0.011756 | 0.11467 | 0.001337 | 0.058637 | -0.20688 | -0.10159 | -0.2348 | -0.15131 | 0.046291 | -0.029423 | 0.20538 | -0.037548 | -0.22665 | 121.8089 | 121.5903 | 121.6956 | 60.9069 | -121.8545 | 121.6459 | 121.7596 | 121.5705 | 60.9287 | -122.032
7.8281 | 121.9894 | -60.9695 | 60.9238 | 1.4211e-13 | -0.018284 | -6.4044e-05 | 0.06474 | -0.0069911 | 0.062217 | -0.22533 | -0.001002 | -0.00033976 | 0.062815 | 0.021333 | 0.061598 | -60.7999 | 0.001407 | -60.9133 | 60.8943 | 60.6757 | 60.7856 | -60.9582 | -60.8775 | 0.004938 | -60.9532 | 60.7358 | 60.8404 | 60.6605 | -61.154 | 0.011368 | -0.029443 | 0.1696 | 0.056268 | 0.0449 | -0.24808 | -0.13821 | -0.18445 | -0.18793 | 0.092064 | 0.016351 | 0.2008 | -0.083326 | -0.26327 | 121.8639 | 121.6452 | 121.7551 | 60.971 | -121.8819 | 121.7054 | 121.81 | 121.63 | 60.9745 | -122.0778
9.5469 | 122.0993 | -60.878 | 60.9375 | 1.4211e-13 | -0.018711 | -0.00027784 | 0.064526 | -0.0072047 | 0.062003 | -0.22533 | -0.00078837 | -0.00033976 | 0.063028 | 0.021119 | 0.061385 | -60.7999 | 0.005985 | -60.9087 | 60.8943 | 60.6803 | 60.7947 | -60.9673 | -60.8866 | 0.009516 | -60.944 | 60.7267 | 60.8496 | 60.6651 | -61.1494 | -0.089342 | -0.043176 | 0.078048 | -0.030706 | 0.058636 | -0.25723 | -0.14279 | -0.27142 | -0.21082 | -0.008645 | -0.066044 | 0.20538 | -0.087902 | -0.27242 | 121.7723 | 121.5583 | 121.6727 | 60.884 | -121.9048 | 121.6047 | 121.7276 | 121.5431 | 60.8875 | -122.0869
11.2188 | 122.0261 | -60.9421 | 60.91 | 1.4211e-13 | -0.019139 | -0.00049144 | 0.064526 | -0.0074183 | 0.062217 | -0.24059 | -0.001002 | -0.00055336 | 0.063028 | 0.020906 | 0.061598 | -60.8045 | 0.005985 | -60.9087 | 60.8943 | 60.6757 | 60.7856 | -60.9582 | -60.8775 | 0.009516 | -60.9486 | 60.7267 | 60.8404 | 60.6513 | -61.1494 | -0.016097 | -0.01571 | 0.13756 | 0.033381 | 0.049478 | -0.23435 | -0.12448 | -0.20734 | -0.18336 | 0.064599 | -0.006535 | 0.2008 | -0.069593 | -0.25869 | 121.8364 | 121.6178 | 121.7276 | 60.9481 | -121.8682 | 121.6688 | 121.7825 | 121.5934 | 60.9516 | -122.0594
12.9531 | 122.0718 | -60.8917 | 60.9055 | 1.4211e-13 | -0.018711 | -0.00027784 | 0.064526 | -0.0074183 | 0.062217 | -0.21007 | -0.00078837 | -0.00012596 | 0.063028 | 0.021333 | 0.061598 | -60.7954 | -0.003172 | -60.9041 | 60.8989 | 60.6757 | 60.781 | -60.9673 | -60.8775 | 0.009516 | -60.9486 | 60.7267 | 60.845 | 60.6651 | -61.1494 | -0.075609 | -0.006555 | 0.096359 | -0.012395 | 0.063214 | -0.22977 | -0.12448 | -0.25769 | -0.17878 | 0.014245 | -0.056889 | 0.2008 | -0.060437 | -0.24038 | 121.7906 | 121.5674 | 121.6727 | 60.8886 | -121.8728 | 121.6184 | 121.7367 | 121.5568 | 60.9012 | -122.0549
14.625 | 122.0856 | -60.9146 | 60.878 | 1.4211e-13 | -0.018925 | -0.00049144 | 0.064526 | -0.0074183 | 0.062003 | -0.24059 | -0.001002 | -0.00098076 | 0.062815 | 0.021119 | 0.061598 | -60.7999 | -0.003172 | -60.9041 | 60.8943 | 60.6757 | 60.7856 | -60.9582 | -60.8775 | 0.004938 | -60.9486 | 60.7267 | 60.845 | 60.6559 | -61.1448 | -0.043563 | 0.016333 | 0.11467 | 0.010493 | 0.054056 | -0.2023 | -0.092435 | -0.23022 | -0.15131 | 0.037133 | -0.034001 | 0.19622 | -0.032971 | -0.22207 | 121.8089 | 121.5903 | 121.7002 | 60.9114 | -121.8362 | 121.6413 | 121.7596 | 121.5705 | 60.9196 | -122.0228
16.375 | 122.1085 | -60.8826 | 60.9009 | 1.4211e-13 | -0.018498 | -0.00070504 | 0.064526 | -0.0072047 | 0.062217 | -0.2177 | -0.0012156 | -0.00055336 | 0.062601 | 0.020906 | 0.061598 | -60.7954 | -0.003172 | -60.9041 | 60.8943 | 60.6803 | 60.781 | -60.9628 | -60.8729 | 0.000359 | -60.9486 | 60.7267 | 60.845 | 60.6651 | -61.1494 | -0.080186 | -0.006555 | 0.087203 | -0.021551 | 0.058635 | -0.22061 | -0.1199 | -0.26685 | -0.1742 | 0.009668 | -0.066045 | 0.2008 | -0.055859 | -0.2358 | 121.7769 | 121.5628 | 121.6635 | 60.8794 | -121.8636 | 121.6092 | 121.7276 | 121.5476 | 60.8829 | -122.0503
18.1094 | 122.0856 | -60.9055 | 60.8734 | 1.4211e-13 | -0.018498 | -0.00027784 | 0.06474 | -0.0074183 | 0.062217 | -0.23296 | -0.001002 | -0.00012596 | 0.062815 | 0.021119 | 0.061171 | -60.7954 | 0.005985 | -60.9133 | 60.8943 | 60.6711 | 60.7856 | -60.9582 | -60.8821 | 0.014095 | -60.9395 | 60.7221 | 60.8359 | 60.6605 | -61.1494 | -0.052718 | 0.020911 | 0.11009 | -0.007818 | 0.0449 | -0.2023 | -0.087857 | -0.24396 | -0.15131 | 0.0234 | -0.033999 | 0.20996 | -0.037551 | -0.21292 | 121.7998 | 121.5766 | 121.691 | 60.9114 | -121.8316 | 121.6276 | 121.7413 | 121.566 | 60.9196 | -122.0228
19.8438 | 121.9986 | -60.9375 | 60.9009 | 1.4211e-13 | -0.018711 | -6.4044e-05 | 0.06474 | -0.0076321 | 0.06243 | -0.22533 | -0.001002 | -0.00076696 | 0.062601 | 0.021119 | 0.061812 | -60.7862 | -0.007751 | -60.9087 | 60.8806 | 60.6757 | 60.781 | -60.9582 | -60.8729 | 0.014095 | -60.944 | 60.7267 | 60.8359 | 60.6513 | -61.1403 | -0.020675 | -0.02029 | 0.15129 | 0.028803 | 0.049478 | -0.22519 | -0.1199 | -0.20276 | -0.1742 | 0.0646 | -0.006535 | 0.19622 | -0.065017 | -0.24954 | 121.8181 | 121.6132 | 121.7185 | 60.9297 | -121.8591 | 121.6642 | 121.7734 | 121.5888 | 60.9516 | -122.0411
21.5312 | 122.0627 | -60.9329 | 60.878 | 1.4211e-13 | -0.019139 | -0.00049144 | 0.064526 | -0.0072047 | 0.062217 | -0.23296 | -0.00057477 | -0.00055336 | 0.062815 | 0.021119 | 0.061171 | -60.7908 | 0.001407 | -60.9041 | 60.8897 | 60.6757 | 60.7764 | -60.9628 | -60.8821 | 0.014095 | -60.9395 | 60.7175 | 60.8542 | 60.6559 | -61.1403 | -0.029832 | 0.011755 | 0.14214 | 0.028803 | 0.058635 | -0.2023 | -0.10159 | -0.20734 | -0.16047 | 0.050865 | -0.006534 | 0.2008 | -0.023814 | -0.22207 | 121.8227 | 121.6086 | 121.7093 | 60.9343 | -121.8407 | 121.6504 | 121.7871 | 121.5888 | 60.947 | -122.0182
23.2812 | 121.9986 | -60.9604 | 60.9192 | 1.4211e-13 | -0.018498 | -0.00027784 | 0.064526 | -0.0074183 | 0.062217 | -0.22533 | -0.00078837 | -0.00098076 | 0.062815 | 0.021119 | 0.061171 | -60.7908 | 0.001407 | -60.9041 | 60.8852 | 60.6757 | 60.7718 | -60.9536 | -60.8821 | 0.014095 | -60.9349 | 60.7267 | 60.8359 | 60.6513 | -61.154 | 0.006792 | -0.034022 | 0.1696 | 0.056269 | 0.049477 | -0.2435 | -0.14737 | -0.19361 | -0.19251 | 0.078331 | 0.025511 | 0.21912 | -0.083327 | -0.26785 | 121.8456 | 121.6361 | 121.7322 | 60.9618 | -121.8728 | 121.6871 | 121.7963 | 121.6117 | 60.9745 | -122.0732
25.0156 | 121.9528 | -60.965 | 60.878 | 1.4211e-13 | -0.018711 | -6.4044e-05 | 0.064526 | -0.0078457 | 0.062003 | -0.22533 | -0.001002 | -0.00055336 | 0.062815 | 0.021333 | 0.061385 | -60.7862 | -0.003172 | -60.9087 | 60.8897 | 60.6711 | 60.7764 | -60.9628 | -60.8729 | 0.014095 | -60.944 | 60.7175 | 60.845 | 60.6559 | -61.1448 | 0.002212 | 0.011755 | 0.17876 | 0.056269 | 0.054057 | -0.20688 | -0.10159 | -0.17987 | -0.16047 | 0.092066 | 0.020931 | 0.2008 | -0.032971 | -0.22207 | 121.8547 | 121.6361 | 121.7414 | 60.9618 | -121.8407 | 121.6825 | 121.81 | 121.6209 | 60.9791 | -122.0228
26.6875 | 121.9849 | -60.9375 | 60.8963 | 1.4211e-13 | -0.018925 | -0.00070504 | 0.064526 | -0.0074183 | 0.062003 | -0.24059 | -0.001002 | -0.00033976 | 0.063028 | 0.021119 | 0.061598 | -60.7908 | 0.001407 | -60.9041 | 60.8897 | 60.6711 | 60.7718 | -60.9582 | -60.8775 | 0.009516 | -60.9486 | 60.7175 | 60.8359 | 60.6513 | -61.1448 | -0.020675 | -0.006555 | 0.14671 | 0.033381 | 0.054056 | -0.22519 | -0.12448 | -0.20734 | -0.17878 | 0.060021 | -0.011113 | 0.19622 | -0.060439 | -0.24496 | 121.8272 | 121.6086 | 121.7093 | 60.9389 | -121.8545 | 121.655 | 121.7734 | 121.5888 | 60.947 | -122.0411
28.4219 | 122.0398 | -60.8871 | 60.9238 | 1.4211e-13 | -0.018925 | -0.00027784 | 0.064526 | -0.0076321 | 0.06243 | -0.23296 | -0.00078837 | 8.7636e-05 | 0.062601 | 0.021333 | 0.061385 | -60.7862 | 0.005985 | -60.8995 | 60.8852 | 60.6757 | 60.7764 | -60.9536 | -60.8729 | 0.009516 | -60.9486 | 60.7221 | 60.8404 | 60.6651 | -61.1403 | -0.06645 | -0.0386 | 0.10094 | -0.012395 | 0.054055 | -0.24808 | -0.14737 | -0.25311 | -0.20167 | 0.014246 | -0.061467 | 0.19164 | -0.083326 | -0.25869 | 121.7723 | 121.5628 | 121.6635 | 60.8931 | -121.8774 | 121.6092 | 121.7276 | 121.5522 | 60.8967 | -122.064
30.0938 | 121.962 | -60.9375 | 60.8826 | 1.4211e-13 | -0.019139 | -0.00027784 | 0.064312 | -0.0078457 | 0.062003 | -0.22533 | -0.001002 | -0.00055336 | 0.063028 | 0.021333 | 0.061171 | -60.7816 | 0.001407 | -60.8995 | 60.8897 | 60.6711 | 60.7718 | -60.9536 | -60.8729 | 0.009516 | -60.9486 | 60.7267 | 60.845 | 60.6559 | -61.1403 | -0.016096 | 0.007178 | 0.15587 | 0.037959 | 0.054055 | -0.21146 | -0.11075 | -0.20276 | -0.15589 | 0.0646 | -0.011113 | 0.19164 | -0.037548 | -0.22665 | 121.8272 | 121.6086 | 121.7093 | 60.9389 | -121.8362 | 121.6642 | 121.7825 | 121.5934 | 60.947 | -122.0228
31.8594 | 121.9391 | -60.9375 | 60.9421 | 1.4211e-13 | -0.018925 | -0.00049144 | 0.064312 | -0.0076321 | 0.062003 | -0.2177 | -0.00057477 | -0.00033976 | 0.062601 | 0.021333 | 0.061598 | -60.7908 | 0.001407 | -60.8995 | 60.8852 | 60.6711 | 60.7764 | -60.9628 | -60.8729 | 0.004938 | -60.9486 | 60.7221 | 60.8313 | 60.6559 | -61.1357 | -0.025254 | -0.056911 | 0.14671 | 0.037959 | 0.063213 | -0.27097 | -0.16568 | -0.19818 | -0.21998 | 0.0646 | -0.011113 | 0.18707 | -0.11079 | -0.28616 | 121.8227 | 121.6086 | 121.7139 | 60.9389 | -121.9048 | 121.6596 | 121.7688 | 121.5934 | 60.9424 | -122.0778
33.5938 | 122.0581 | -60.878 | 60.9192 | 1.4211e-13 | -0.018925 | -0.00049144 | 0.06474 | -0.0074183 | 0.062217 | -0.22533 | -0.00078837 | -0.00055336 | 0.063028 | 0.021333 | 0.061598 | -60.7908 | 0.001407 | -60.895 | 60.8897 | 60.6711 | 60.781 | -60.9582 | -60.8683 | 0.009516 | -60.944 | 60.7221 | 60.8313 | 60.6559 | -61.1448 | -0.080184 | -0.029443 | 0.087205 | -0.016971 | 0.063213 | -0.24808 | -0.13821 | -0.26684 | -0.19709 | 0.00967 | -0.066044 | 0.2008 | -0.087905 | -0.26327 | 121.7677 | 121.5491 | 121.659 | 60.8794 | -121.8774 | 121.6001 | 121.7093 | 121.5339 | 60.8875 | -122.064
35.3281 | 121.9528 | -60.9467 | 60.8963 | 1.4211e-13 | -0.019139 | -0.00027784 | 0.064312 | -0.0076321 | 0.061789 | -0.23296 | -0.00078837 | -0.00055336 | 0.062601 | 0.021547 | 0.061385 | -60.7908 | 0.001407 | -60.9041 | 60.8806 | 60.6665 | 60.781 | -60.9582 | -60.8729 | 0.009516 | -60.9349 | 60.7175 | 60.8404 | 60.6513 | -61.1448 | -0.01152 | -0.015712 | 0.15587 | 0.042536 | 0.054056 | -0.22977 | -0.11532 | -0.19818 | -0.17878 | 0.073755 | 0.011778 | 0.20996 | -0.05586 | -0.24496 | 121.8272 | 121.6132 | 121.7276 | 60.9481 | -121.8545 | 121.6642 | 121.7871 | 121.598 | 60.9562 | -122.0411
37 | 122.0718 | -60.8917 | 60.8643 | 1.4211e-13 | -0.019139 | -0.00027784 | 0.06474 | -0.0072047 | 0.06243 | -0.2177 | -0.001002 | -0.00033976 | 0.062815 | 0.021333 | 0.061812 | -60.7908 | -0.003172 | -60.9041 | 60.8852 | 60.662 | 60.7764 | -60.9536 | -60.8683 | 0.014095 | -60.9303 | 60.7267 | 60.8404 | 60.6559 | -61.1448 | -0.061872 | 0.020909 | 0.10094 | -0.012395 | 0.049477 | -0.20231 | -0.087859 | -0.25311 | -0.13758 | 0.023403 | -0.038575 | 0.21454 | -0.023817 | -0.20834 | 121.7769 | 121.5537 | 121.6681 | 60.8886 | -121.8179 | 121.6184 | 121.7322 | 121.5476 | 60.9058 | -122.0091
38.75 | 122.0581 | -60.9055 | 60.878 | 1.4211e-13 | -0.019139 | -0.00070504 | 0.064526 | -0.0074183 | 0.061789 | -0.23296 | -0.00078837 | -0.00033976 | 0.062601 | 0.02176 | 0.061598 | -60.7816 | 0.001407 | -60.895 | 60.8806 | 60.6757 | 60.7764 | -60.9536 | -60.8637 | 0.009516 | -60.944 | 60.7267 | 60.8313 | 60.6559 | -61.1448 | -0.048139 | 0.002598 | 0.12383 | 0.010495 | 0.058634 | -0.2023 | -0.10159 | -0.23938 | -0.15131 | 0.041715 | -0.038578 | 0.2008 | -0.046707 | -0.22207 | 121.786 | 121.5811 | 121.6819 | 60.9069 | -121.8316 | 121.6321 | 121.7367 | 121.5614 | 60.915 | -122.0228
40.4844 | 122.0856 | -60.9055 | 60.8551 | 1.4211e-13 | -0.019139 | -0.00070504 | 0.064526 | -0.0074183 | 0.062217 | -0.23296 | -0.001002 | -0.00033976 | 0.062174 | 0.02176 | 0.061812 | -60.7862 | 0.001407 | -60.8904 | 60.8852 | 60.6665 | 60.7718 | -60.9536 | -60.8729 | 0.014095 | -60.9395 | 60.7221 | 60.8313 | 60.6513 | -61.1448 | -0.048139 | 0.030064 | 0.11925 | 0.015073 | 0.063212 | -0.18857 | -0.083282 | -0.23938 | -0.133 | 0.032557 | -0.033999 | 0.20538 | -0.023819 | -0.20376 | 121.7906 | 121.572 | 121.6773 | 60.9069 | -121.8087 | 121.6276 | 121.7367 | 121.5568 | 60.9196 | -121.9999
42.1562 | 121.9803 | -60.9421 | 60.8871 | 1.4211e-13 | -0.018711 | -0.00049144 | 0.064312 | -0.0078457 | 0.062003 | -0.23296 | -0.001002 | -0.00076696 | 0.062601 | 0.021547 | 0.061385 | -60.7816 | -0.003172 | -60.8995 | 60.8897 | 60.662 | 60.781 | -60.9536 | -60.8637 | 0.009516 | -60.9395 | 60.7129 | 60.8359 | 60.6468 | -61.1494 | -0.011518 | 0.0026 | 0.16045 | 0.042537 | 0.054055 | -0.22519 | -0.10617 | -0.20734 | -0.17421 | 0.078336 | 0.002622 | 0.20996 | -0.051284 | -0.24038 | 121.8318 | 121.604 | 121.7231 | 60.9389 | -121.8407 | 121.655 | 121.7779 | 121.5888 | 60.9516 | -122.0366
43.9062 | 121.9482 | -60.9329 | 60.9329 | 1.4211e-13 | -0.018925 | -0.00027784 | 0.064312 | -0.0074183 | 0.062644 | -0.22533 | -0.001002 | -0.00012596 | 0.062815 | 0.021333 | 0.061598 | -60.7816 | -0.003172 | -60.9041 | 60.8714 | 60.6711 | 60.7764 | -60.9582 | -60.8592 | 0.014095 | -60.9303 | 60.7129 | 60.8313 | 60.6468 | -61.1448 | -0.025253 | -0.06149 | 0.15129 | 0.028803 | 0.054056 | -0.26181 | -0.15652 | -0.21191 | -0.21998 | 0.073758 | 0.002623 | 0.21454 | -0.10164 | -0.28616 | 121.8044 | 121.604 | 121.7093 | 60.9297 | -121.8911 | 121.6459 | 121.7642 | 121.5797 | 60.947 | -122.0778
45.6562 | 121.9391 | -60.9604 | 60.8917 | 1.4211e-13 | -0.019352 | -0.00027784 | 0.064312 | -0.0076321 | 0.061789 | -0.22533 | -0.00078837 | -0.00055336 | 0.063028 | 0.021547 | 0.061598 | -60.7908 | 0.005985 | -60.8904 | 60.8806 | 60.662 | 60.7718 | -60.9628 | -60.8683 | 0.004938 | -60.9211 | 60.7175 | 60.8359 | 60.6513 | -61.1357 | -0.002366 | -0.011135 | 0.1696 | 0.070004 | 0.07237 | -0.22977 | -0.1199 | -0.17529 | -0.1742 | 0.092067 | 0.039247 | 0.21454 | -0.055862 | -0.24038 | 121.841 | 121.6223 | 121.7322 | 60.9664 | -121.8545 | 121.6779 | 121.7963 | 121.6117 | 60.9653 | -122.0274
47.4062 | 121.9666 | -60.9238 | 60.9238 | 1.4211e-13 | -0.019352 | -0.00049144 | 0.06474 | -0.0080593 | 0.062003 | -0.22533 | -0.001002 | -0.00012596 | 0.063028 | 0.021547 | 0.061385 | -60.7816 | 0.001407 | -60.895 | 60.8806 | 60.781 | 60.781 | -60.9582 | -60.8546 | 0.018674 | -60.9303 | 60.7221 | 60.8404 | 60.7338 | -61.1357 | -0.034408 | -0.043178 | 0.14214 | 0.028805 | 0.063213 | -0.14276 | -0.14279 | -0.21191 | -0.20167 | 0.069182 | -0.006532 | 0.20538 | -0.083326 | -0.19001 | 121.8044 | 121.7048 | 121.7047 | 60.9252 | -121.8819 | 121.6459 | 121.7642 | 121.6575 | 60.9424 | -122.0594
49.0781 | 121.9482 | -60.9283 | 60.9009 | 1.4211e-13 | -0.019139 | -6.4044e-05 | 0.064526 | -0.0078457 | 0.061789 | -0.23296 | -0.0012156 | -0.00012596 | 0.062815 | 0.021547 | 0.061385 | -60.7816 | 0.010564 | -60.895 | 60.8897 | 60.662 | 60.781 | -60.9582 | -60.8683 | 0.009516 | -60.9303 | 60.7084 | 60.8359 | 60.6559 | -61.1448 | -0.02983 | -0.011133 | 0.14672 | 0.033383 | 0.063213 | -0.23893 | -0.1199 | -0.21649 | -0.19252 | 0.060024 | -0.001954 | 0.21454 | -0.065017 | -0.24496 | 121.8181 | 121.5903 | 121.7093 | 60.9389 | -121.8591 | 121.6367 | 121.7642 | 121.5843 | 60.9379 | -122.0457
50.8281 | 121.9849 | -60.9192 | 60.9055 | 1.4211e-13 | -0.019352 | -0.00027784 | 0.064526 | -0.0078457 | 0.062217 | -0.23296 | -0.001002 | -0.00055336 | 0.062601 | 0.021974 | 0.060957 | -60.7725 | 0.010564 | -60.895 | 60.8852 | 60.6711 | 60.7764 | -60.949 | -60.8683 | 0.014095 | -60.9395 | 60.7175 | 60.8313 | 60.6605 | -61.1448 | -0.029828 | -0.02029 | 0.14672 | 0.024227 | 0.054055 | -0.23435 | -0.12906 | -0.22565 | -0.18794 | 0.050868 | -0.020267 | 0.20538 | -0.074173 | -0.24496 | 121.8044 | 121.5903 | 121.6956 | 60.9298 | -121.8545 | 121.6367 | 121.7505 | 121.5797 | 60.9333 | -122.0503
52.4844 | 122.0444 | -60.8871 | 60.9146 | 1.4211e-13 | -0.018711 | -0.00070504 | 0.064526 | -0.0078457 | 0.062217 | -0.23296 | -0.00078837 | -0.00012596 | 0.062387 | 0.021974 | 0.061812 | -60.7816 | 0.001407 | -60.895 | 60.8806 | 60.6665 | 60.7764 | -60.9536 | -60.8592 | 0.014095 | -60.9303 | 60.7038 | 60.8359 | 60.6468 | -61.1448 | -0.06645 | -0.034023 | 0.10552 | -0.007816 | 0.058634 | -0.24808 | -0.13821 | -0.25769 | -0.21083 | 0.027982 | -0.043153 | 0.21454 | -0.07875 | -0.26785 | 121.7677 | 121.5537 | 121.6635 | 60.8886 | -121.8682 | 121.5909 | 121.723 | 121.5339 | 60.9012 | -122.0594
54.2188 | 122.0718 | -60.8963 | 60.8688 | 1.4211e-13 | -0.019139 | -0.00049144 | 0.064526 | -0.0078457 | 0.062217 | -0.24059 | -0.00057477 | -0.00012596 | 0.062174 | 0.021974 | 0.061171 | -60.7771 | -0.007751 | -60.895 | 60.876 | 60.6574 | 60.7718 | -60.949 | -60.8546 | 0.014095 | -60.9303 | 60.7129 | 60.8404 | 60.6468 | -61.1403 | -0.052716 | 0.007175 | 0.11925 | 0.001339 | 0.054055 | -0.21146 | -0.097014 | -0.24396 | -0.15589 | 0.041716 | -0.033998 | 0.20996 | -0.028394 | -0.22207 | 121.7723 | 121.5537 | 121.6681 | 60.8886 | -121.8179 | 121.6092 | 121.7367 | 121.5431 | 60.9104 | -122.0091
55.8906 | 121.9757 | -60.9283 | 60.9329 | 1.4211e-13 | -0.019139 | -0.00049144 | 0.064526 | -0.0072047 | 0.062217 | -0.23296 | -0.001002 | -0.00055336 | 0.062601 | 0.02176 | 0.061598 | -60.7771 | 0.005985 | -60.8904 | 60.8806 | 60.662 | 60.7718 | -60.9536 | -60.8592 | 0.009516 | -60.9257 | 60.7129 | 60.8404 | 60.6559 | -61.1448 | -0.025251 | -0.052333 | 0.15129 | 0.037961 | 0.063212 | -0.27097 | -0.1611 | -0.21649 | -0.21998 | 0.069181 | 0.002625 | 0.21912 | -0.092481 | -0.277 | 121.8089 | 121.5903 | 121.7002 | 60.9343 | -121.8865 | 121.6413 | 121.7688 | 121.5843 | 60.9379 | -122.0778
57.625 | 122.0901 | -60.8688 | 60.8826 | 1.4211e-13 | -0.019139 | -0.00070504 | 0.064526 | -0.0078457 | 0.062003 | -0.22533 | -0.00078837 | -0.00055336 | 0.062815 | 0.021974 | 0.061385 | -60.7771 | -0.003172 | -60.895 | 60.876 | 60.662 | 60.7764 | -60.9444 | -60.8546 | 0.009516 | -60.9349 | 60.7129 | 60.8313 | 60.6513 | -61.1494 | -0.075603 | -0.006558 | 0.091784 | -0.026127 | 0.049476 | -0.22062 | -0.10617 | -0.28058 | -0.16963 | 0.01425 | -0.066042 | 0.21454 | -0.051284 | -0.23123 | 121.7448 | 121.5308 | 121.6452 | 60.8657 | -121.827 | 121.5818 | 121.7001 | 121.5202 | 60.8784 | -122.032
59.2969 | 122.0261 | -60.8963 | 60.8597 | 1.4211e-13 | -0.019352 | -0.00027784 | 0.06474 | -0.0076321 | 0.061789 | -0.22533 | -0.001002 | -0.00033976 | 0.062815 | 0.022188 | 0.061385 | -60.7771 | 0.001407 | -60.8858 | 60.8714 | 60.6665 | 60.7764 | -60.949 | -60.8637 | 0.009516 | -60.9257 | 60.7084 | 60.8313 | 60.6468 | -61.1448 | -0.052716 | 0.011752 | 0.11925 | 0.010495 | 0.063211 | -0.19315 | -0.083281 | -0.24853 | -0.15132 | 0.032559 | -0.029419 | 0.21912 | -0.028396 | -0.21292 | 121.7677 | 121.5628 | 121.6727 | 60.8977 | -121.8087 | 121.6047 | 121.7276 | 121.5431 | 60.9058 | -122.0045
61.0469 | 122.0993 | -60.8643 | 60.9146 | 1.4211e-13 | -0.019566 | -0.00027784 | 0.064526 | -0.0074183 | 0.061789 | -0.22533 | -0.001002 | -0.00055336 | 0.062815 | 0.021974 | 0.061385 | -60.7725 | -0.003172 | -60.8904 | 60.876 | 60.6711 | 60.7718 | -60.9536 | -60.8592 | 0.009516 | -60.9349 | 60.7084 | 60.8359 | 60.6559 | -61.1448 | -0.089338 | -0.038602 | 0.091785 | -0.026126 | 0.063212 | -0.2435 | -0.14279 | -0.28058 | -0.20625 | 0.005094 | -0.070619 | 0.20996 | -0.07875 | -0.25869 | 121.7403 | 121.5354 | 121.6361 | 60.8611 | -121.8682 | 121.5726 | 121.7001 | 121.5202 | 60.8738 | -122.0594
62.7188 | 122.0123 | -60.8963 | 60.8597 | 1.4211e-13 | -0.019352 | -0.00070504 | 0.064312 | -0.0076321 | 0.062003 | -0.23296 | -0.00078837 | -0.00012596 | 0.062815 | 0.021974 | 0.061171 | -60.7725 | 0.005985 | -60.8904 | 60.8714 | 60.6665 | 60.7627 | -60.9444 | -60.8637 | 0.009516 | -60.9303 | 60.7129 | 60.8267 | 60.6422 | -61.1357 | -0.048137 | 0.011752 | 0.12383 | 0.005917 | 0.054054 | -0.19315 | -0.097017 | -0.23938 | -0.14674 | 0.032559 | -0.033998 | 0.20538 | -0.032975 | -0.2175 | 121.7677 | 121.5628 | 121.659 | 60.9023 | -121.8041 | 121.6092 | 121.723 | 121.5385 | 60.9058 | -121.9954
64.4531 | 121.9345 | -60.9146 | 60.9467 | 1.4211e-13 | -0.01978 | -0.00070504 | 0.064312 | -0.0076321 | 0.062217 | -0.23296 | -0.0012156 | -0.00033976 | 0.062815 | 0.02176 | 0.061171 | -60.7771 | -0.003172 | -60.8904 | 60.876 | 60.6711 | 60.7718 | -60.949 | -60.8592 | 0.014095 | -60.9303 | 60.7084 | 60.8404 | 60.6468 | -61.1448 | -0.034405 | -0.070645 | 0.13756 | 0.024228 | 0.058633 | -0.27555 | -0.17483 | -0.23022 | -0.23829 | 0.055448 | -0.015687 | 0.21454 | -0.10621 | -0.29989 | 121.7906 | 121.5857 | 121.6864 | 60.9114 | -121.8957 | 121.623 | 121.7551 | 121.5614 | 60.9287 | -122.0915
66.2031 | 121.9482 | -60.8917 | 60.91 | 1.4211e-13 | -0.01978 | -0.00049144 | 0.064526 | -0.0074183 | 0.062003 | -0.2177 | -0.0012156 | -0.00076696 | 0.062815 | 0.021974 | 0.061171 | -60.7816 | 0.001407 | -60.8904 | 60.876 | 60.6665 | 60.7764 | -60.9444 | -60.8546 | 0.014095 | -60.9303 | 60.7129 | 60.8359 | 60.6513 | -61.1403 | -0.052714 | -0.034024 | 0.11009 | 0.00134 | 0.054054 | -0.2435 | -0.13364 | -0.24853 | -0.19709 | 0.037139 | -0.038575 | 0.20996 | -0.074172 | -0.25869 | 121.7677 | 121.5583 | 121.6681 | 60.8931 | -121.8545 | 121.6047 | 121.7276 | 121.5431 | 60.9058 | -122.0503
67.9375 | 121.9208 | -60.9421 | 60.8826 | 1.4211e-13 | -0.01978 | -0.00027784 | 0.064099 | -0.0076321 | 0.062003 | -0.24059 | -0.00078837 | 8.7636e-05 | 0.063028 | 0.021974 | 0.061385 | -60.7679 | 0.001407 | -60.8904 | 60.8714 | 60.6574 | 60.7718 | -60.9399 | -60.85 | 0.014095 | -60.9303 | 60.7084 | 60.8359 | 60.6468 | -61.1311 | 0.002219 | -0.011136 | 0.17418 | 0.051694 | 0.049475 | -0.2252 | -0.11075 | -0.18902 | -0.17421 | 0.092072 | 0.011779 | 0.2008 | -0.046706 | -0.23581 | 121.8135 | 121.5995 | 121.7139 | 60.9435 | -121.8224 | 121.6504 | 121.7779 | 121.5888 | 60.9562 | -122.0137
69.6719 | 121.9711 | -60.8826 | 60.9283 | 1.4211e-13 | -0.019566 | -0.00027784 | 0.064312 | -0.0074183 | 0.06243 | -0.23296 | -0.001002 | -0.00055336 | 0.062601 | 0.021974 | 0.061385 | -60.7725 | -0.003172 | -60.8858 | 60.8714 | 60.6574 | 60.7718 | -60.949 | -60.8637 | 0.009516 | -60.9303 | 60.7175 | 60.8313 | 60.6513 | -61.1448 | -0.066449 | -0.056913 | 0.1101 | -0.003238 | 0.063211 | -0.27097 | -0.15652 | -0.26227 | -0.21082 | 0.018826 | -0.047731 | 0.21454 | -0.097061 | -0.277 | 121.754 | 121.5399 | 121.6544 | 60.8794 | -121.8774 | 121.6001 | 121.7139 | 121.5339 | 60.8921 | -122.0732
71.3438 | 121.9208 | -60.9604 | 60.8688 | 1.4211e-13 | -0.019566 | -0.00049144 | 0.064312 | -0.0076321 | 0.061576 | -0.22533 | -0.001002 | -0.00055336 | 0.062815 | 0.02176 | 0.061812 | -60.7679 | 0.001407 | -60.8858 | 60.8669 | 60.6574 | 60.7627 | -60.9399 | -60.85 | 0.009516 | -60.9303 | 60.7084 | 60.8404 | 60.6376 | -61.1357 | 0.020529 | -0.001981 | 0.19249 | 0.074582 | 0.054053 | -0.21146 | -0.10617 | -0.17529 | -0.16047 | 0.11038 | 0.030089 | 0.20538 | -0.028394 | -0.23123 | 121.8272 | 121.6178 | 121.7231 | 60.9618 | -121.8087 | 121.6688 | 121.8008 | 121.598 | 60.9699 | -122.0045
73.0781 | 121.9666 | -60.9283 | 60.8963 | 1.4211e-13 | -0.01978 | -0.00070504 | 0.06474 | -0.0078457 | 0.06243 | -0.24822 | -0.0012156 | -0.00033976 | 0.062387 | 0.021974 | 0.061385 | -60.7771 | -0.003172 | -60.8858 | 60.8806 | 60.6665 | 60.7718 | -60.9399 | -60.8546 | 0.009516 | -60.9211 | 60.7084 | 60.8313 | 60.6376 | -61.1357 | -0.011514 | -0.015712 | 0.15129 | 0.042539 | 0.054053 | -0.22977 | -0.12448 | -0.20733 | -0.18794 | 0.07376 | 0.007204 | 0.21454 | -0.065017 | -0.2587 | 121.8089 | 121.5949 | 121.7002 | 60.9252 | -121.8362 | 121.6367 | 121.7596 | 121.566 | 60.9379 | -122.032
74.75 | 121.9528 | -60.9009 | 60.9192 | 1.4211e-13 | -0.019566 | -0.00049144 | 0.06474 | -0.0078457 | 0.062003 | -0.22533 | -0.0012156 | 8.7636e-05 | 0.062601 | 0.022188 | 0.061385 | -60.7771 | 0.010564 | -60.8858 | 60.8669 | 60.6574 | 60.7718 | -60.949 | -60.8546 | 0.014095 | -60.9303 | 60.7084 | 60.8313 | 60.6422 | -61.1357 | -0.048138 | -0.052335 | 0.12383 | 0.015073 | 0.063211 | -0.26182 | -0.14737 | -0.2348 | -0.21083 | 0.046294 | -0.02942 | 0.20538 | -0.087905 | -0.27701 | 121.7677 | 121.5583 | 121.6727 | 60.9114 | -121.8682 | 121.6092 | 121.7322 | 121.5431 | 60.915 | -122.0549
76.5 | 121.9254 | -60.91 | 60.9329 | 1.4211e-13 | -0.019566 | -0.00049144 | 0.06474 | -0.0078457 | 0.062003 | -0.22533 | -0.001002 | -0.00033976 | 0.062387 | 0.021974 | 0.061385 | -60.7679 | -0.003172 | -60.8858 | 60.876 | 60.662 | 60.7764 | -60.9353 | -60.8592 | 0.014095 | -60.9257 | 60.7038 | 60.8313 | 60.6422 | -61.1403 | -0.025246 | -0.056912 | 0.14214 | 0.024228 | 0.049474 | -0.27097 | -0.15652 | -0.23022 | -0.22914 | 0.05087 | -0.015686 | 0.21454 | -0.10164 | -0.29074 | 121.786 | 121.572 | 121.6864 | 60.9069 | -121.8682 | 121.6138 | 121.7413 | 121.5522 | 60.9241 | -122.0732
78.2344 | 121.994 | -60.878 | 60.9238 | 1.4211e-13 | -0.019566 | -0.00049144 | 0.064526 | -0.0076321 | 0.062003 | -0.24059 | -0.0012156 | -0.00033976 | 0.062815 | 0.022188 | 0.061385 | -60.7725 | -0.003172 | -60.8904 | 60.8714 | 60.662 | 60.7672 | -60.9444 | -60.8546 | 0.009516 | -60.9303 | 60.7038 | 60.8313 | 60.6513 | -61.1403 | -0.066447 | -0.052335 | 0.10552 | -0.012393 | 0.054054 | -0.26182 | -0.15652 | -0.26227 | -0.21998 | 0.023406 | -0.052308 | 0.20996 | -0.092483 | -0.27243 | 121.7494 | 121.5399 | 121.6452 | 60.8748 | -121.8682 | 121.5818 | 121.7093 | 121.5293 | 60.8875 | -122.064
79.9531 | 121.9299 | -60.9146 | 60.9283 | 1.4211e-13 | -0.01978 | -0.00049144 | 0.06474 | -0.0078457 | 0.062003 | -0.24059 | -0.0012156 | -0.00033976 | 0.062601 | 0.022401 | 0.061385 | -60.7679 | 0.001407 | -60.8904 | 60.876 | 60.6665 | 60.7718 | -60.9353 | -60.8592 | 0.014095 | -60.9257 | 60.7038 | 60.8313 | 60.6376 | -61.1403 | -0.020668 | -0.052335 | 0.14672 | 0.024228 | 0.044896 | -0.26181 | -0.15652 | -0.22565 | -0.22456 | 0.055448 | -0.011108 | 0.21454 | -0.097061 | -0.29074 | 121.7906 | 121.5811 | 121.6864 | 60.916 | -121.8636 | 121.6184 | 121.7459 | 121.5522 | 60.9287 | -122.0686
81.625 | 121.9299 | -60.9375 | 60.8643 | 1.4211e-13 | -0.019566 | -0.00027784 | 0.064099 | -0.0078457 | 0.062217 | -0.22533 | -0.0012156 | -0.00055336 | 0.062815 | 0.022401 | 0.061598 | -60.7725 | -0.003172 | -60.8904 | 60.8669 | 60.6528 | 60.7718 | -60.9444 | -60.85 | 0.004938 | -60.9166 | 60.7084 | 60.8313 | 60.6376 | -61.1403 | -0.006938 | 0.002596 | 0.16503 | 0.047116 | 0.054054 | -0.21146 | -0.092437 | -0.20276 | -0.1559 | 0.087494 | 0.020938 | 0.22369 | -0.032974 | -0.22665 | 121.8044 | 121.5903 | 121.7093 | 60.9343 | -121.8087 | 121.6459 | 121.7688 | 121.5751 | 60.9424 | -122.0045
83.3594 | 121.907 | -60.9421 | 60.8734 | 1.4211e-13 | -0.019566 | -0.00049144 | 0.064526 | -0.0076321 | 0.062003 | -0.23296 | -0.00078837 | -0.00012596 | 0.062387 | 0.022188 | 0.061385 | -60.7725 | -0.003172 | -60.8812 | 60.8669 | 60.6574 | 60.7718 | -60.949 | -60.85 | 0.009516 | -60.9257 | 60.7084 | 60.8267 | 60.6239 | -61.1357 | -0.006939 | -0.006559 | 0.16961 | 0.060851 | 0.06779 | -0.21604 | -0.10159 | -0.1936 | -0.16505 | 0.092072 | 0.016358 | 0.20996 | -0.046708 | -0.24954 | 121.8089 | 121.5995 | 121.7139 | 60.9389 | -121.8224 | 121.6504 | 121.7688 | 121.5659 | 60.9516 | -122.0091
85.0938 | 122.0581 | -60.8734 | 60.8963 | 1.4211e-13 | -0.01978 | -0.00049144 | 0.064312 | -0.0076321 | 0.06243 | -0.23296 | -0.001002 | -0.00033976 | 0.062601 | 0.022188 | 0.061171 | -60.7679 | 0.001407 | -60.8858 | 60.8577 | 60.6665 | 60.7672 | -60.9353 | -60.8454 | 0.009516 | -60.9211 | 60.6946 | 60.8267 | 60.6376 | -61.1448 | -0.061867 | -0.038604 | 0.10552 | -0.012393 | 0.049474 | -0.22977 | -0.12906 | -0.27142 | -0.20167 | 0.027985 | -0.047728 | 0.22369 | -0.069596 | -0.2587 | 121.7311 | 121.5399 | 121.6407 | 60.8748 | -121.8316 | 121.568 | 121.7001 | 121.511 | 60.8829 | -122.0411
86.7812 | 121.9299 | -60.91 | 60.9146 | 1.4211e-13 | -0.01978 | -0.00049144 | 0.064312 | -0.0078457 | 0.061789 | -0.23296 | -0.0014292 | -0.00033976 | 0.062601 | 0.022401 | 0.061171 | -60.7633 | 0.001407 | -60.8858 | 60.8714 | 60.6528 | 60.7672 | -60.9399 | -60.85 | 0.014095 | -60.9211 | 60.7038 | 60.8221 | 60.6376 | -61.1357 | -0.029825 | -0.04318 | 0.14672 | 0.024228 | 0.054053 | -0.26182 | -0.14737 | -0.22565 | -0.21083 | 0.060028 | -0.011107 | 0.21454 | -0.092485 | -0.27701 | 121.7815 | 121.5628 | 121.6773 | 60.9114 | -121.8545 | 121.6138 | 121.7322 | 121.5476 | 60.9241 | -122.0503
88.5312 | 122.0169 | -60.9055 | 60.8322 | 1.4211e-13 | -0.01978 | -0.00027784 | 0.064312 | -0.0076321 | 0.06243 | -0.23296 | -0.00078837 | -0.00076696 | 0.062601 | 0.022401 | 0.061598 | -60.7633 | -0.003172 | -60.8812 | 60.8623 | 60.6574 | 60.7718 | -60.9399 | -60.85 | 0.014095 | -60.9211 | 60.7038 | 60.8267 | 60.633 | -61.1311 | -0.034402 | 0.030061 | 0.14214 | 0.02423 | 0.058632 | -0.17484 | -0.060393 | -0.22564 | -0.12843 | 0.055451 | -0.015684 | 0.20996 | -0.005509 | -0.19919 | 121.7677 | 121.5628 | 121.6773 | 60.9023 | -121.7721 | 121.6092 | 121.7322 | 121.5385 | 60.9196 | -121.9633
90.2031 | 121.962 | -60.9283 | 60.8917 | 1.4211e-13 | -0.019566 | -0.00049144 | 0.064526 | -0.0078457 | 0.062003 | -0.23296 | -0.00078837 | -0.00033976 | 0.062815 | 0.022401 | 0.061385 | -60.7633 | -0.007751 | -60.8858 | 60.8669 | 60.6848 | 60.7718 | -60.9353 | -60.85 | 0.014095 | -60.9166 | 60.7084 | 60.8221 | 60.6376 | -61.1357 | -0.006935 | -0.02487 | 0.16503 | 0.042539 | 0.049474 | -0.20688 | -0.1199 | -0.20733 | -0.18336 | 0.078339 | 0.011783 | 0.21912 | -0.069597 | -0.25412 | 121.7952 | 121.6132 | 121.7002 | 60.9206 | -121.827 | 121.6367 | 121.7505 | 121.566 | 60.9424 | -122.0274
91.9062 | 121.8933 | -60.9558 | 60.878 | 1.4211e-13 | -0.01978 | -0.00027784 | 0.064312 | -0.0076321 | 0.062003 | -0.24059 | -0.001002 | -0.00033976 | 0.062815 | 0.022401 | 0.061171 | -60.7633 | 0.001407 | -60.8858 | 60.8714 | 60.6528 | 60.7718 | -60.9399 | -60.85 | 0.009516 | -60.9211 | 60.7038 | 60.8267 | 60.6284 | -61.1357 | 0.015952 | -0.006559 | 0.19249 | 0.070005 | 0.054053 | -0.2252 | -0.10617 | -0.17987 | -0.17421 | 0.1058 | 0.03467 | 0.21454 | -0.051286 | -0.24954 | 121.8272 | 121.6086 | 121.7276 | 60.9572 | -121.8178 | 121.6596 | 121.7825 | 121.5843 | 60.9653 | -122.0137
93.6406 | 122.049 | -60.8414 | 60.8917 | 1.4211e-13 | -0.01978 | -0.00049144 | 0.064526 | -0.0078457 | 0.062217 | -0.22533 | -0.0012156 | -0.00033976 | 0.062601 | 0.022188 | 0.061171 | -60.7587 | -0.003172 | -60.8858 | 60.8669 | 60.6574 | 60.7718 | -60.9307 | -60.85 | 0.009516 | -60.9211 | 60.7084 | 60.8313 | 60.6376 | -61.1357 | -0.089331 | -0.02487 | 0.082632 | -0.044436 | 0.044895 | -0.23435 | -0.1199 | -0.29431 | -0.18336 | -0.008636 | -0.079771 | 0.21454 | -0.06044 | -0.25412 | 121.7082 | 121.4987 | 121.6132 | 60.8382 | -121.8224 | 121.5497 | 121.6727 | 121.479 | 60.8509 | -122.0274
95.3906 | 121.907 | -60.9512 | 60.878 | 1.4211e-13 | -0.01978 | -0.00027784 | 0.06474 | -0.0076321 | 0.062217 | -0.23296 | -0.0012156 | -0.00033976 | 0.062387 | 0.022188 | 0.061385 | -60.7633 | -0.007751 | -60.8766 | 60.8669 | 60.6482 | 60.7718 | -60.9399 | -60.85 | 0.014095 | -60.9166 | 60.6992 | 60.8313 | 60.633 | -61.1219 | 0.011374 | -0.011137 | 0.18792 | 0.074584 | 0.06321 | -0.22978 | -0.10617 | -0.17071 | -0.17879 | 0.10123 | 0.034671 | 0.20538 | -0.046707 | -0.24496 | 121.8181 | 121.5994 | 121.7231 | 60.9435 | -121.8178 | 121.6504 | 121.7825 | 121.5843 | 60.9653 | -121.9999
97.0781 | 122.0078 | -60.8734 | 60.8734 | 1.4211e-13 | -0.019993 | -0.00027784 | 0.064312 | -0.0078457 | 0.061789 | -0.23296 | -0.00078837 | -0.00055336 | 0.062387 | 0.022401 | 0.061598 | -60.7679 | 0.001407 | -60.8858 | 60.8714 | 60.662 | 60.7718 | -60.9353 | -60.8454 | 0.014095 | -60.9166 | 60.7038 | 60.8267 | 60.6376 | -61.1357 | -0.061867 | -0.001981 | 0.10552 | -0.012393 | 0.049474 | -0.21146 | -0.10159 | -0.26227 | -0.16963 | 0.027985 | -0.043149 | 0.21912 | -0.046708 | -0.23581 | 121.7448 | 121.5354 | 121.6452 | 60.8748 | -121.8087 | 121.5772 | 121.7001 | 121.511 | 60.8875 | -122.0091
98.8281 | 121.9666 | -60.878 | 60.8734 | 1.4211e-13 | -0.01978 | -0.00091884 | 0.064526 | -0.0080593 | 0.062003 | -0.23296 | -0.001002 | -0.00033976 | 0.062387 | 0.022401 | 0.061385 | -60.7633 | -0.003172 | -60.8858 | 60.8714 | 60.6528 | 60.7627 | -60.9353 | -60.8454 | 0.009516 | -60.9211 | 60.7038 | 60.8221 | 60.6468 | -61.1311 | -0.057289 | -0.001981 | 0.11467 | -0.007815 | 0.049474 | -0.22062 | -0.11075 | -0.25311 | -0.16963 | 0.032563 | -0.04315 | 0.20996 | -0.051286 | -0.22665 | 121.7494 | 121.5308 | 121.6407 | 60.8748 | -121.8087 | 121.5818 | 121.7001 | 121.5248 | 60.8875 | -122.0045
100.5469 | 121.9528 | -60.9146 | 60.8643 | 1.4211e-13 | -0.019566 | -0.00049144 | 0.06474 | -0.0078457 | 0.062003 | -0.22533 | -0.0012156 | -0.00055336 | 0.062815 | 0.022401 | 0.061171 | -60.7587 | -0.003172 | -60.8812 | 60.8623 | 60.6665 | 60.7581 | -60.9307 | -60.8408 | 0.014095 | -60.9257 | 60.7084 | 60.8359 | 60.6376 | -61.1311 | -0.016089 | -0.001983 | 0.15587 | 0.033385 | 0.049474 | -0.19773 | -0.10617 | -0.21649 | -0.1559 | 0.073763 | -0.011108 | 0.20538 | -0.028396 | -0.22665 | 121.7769 | 121.5811 | 121.6727 | 60.9114 | -121.795 | 121.623 | 121.7505 | 121.5522 | 60.9287 | -121.9954
102.2188 | 122.0398 | -60.8414 | 60.8597 | 1.4211e-13 | -0.01978 | -0.00049144 | 0.064526 | -0.0076321 | 0.062003 | -0.22533 | -0.0012156 | -0.00012596 | 0.062387 | 0.022615 | 0.061171 | -60.7587 | 0.001407 | -60.8812 | 60.8714 | 60.6665 | 60.7627 | -60.9399 | -60.8408 | 0.014095 | -60.9166 | 60.7038 | 60.8221 | 60.6422 | -61.1311 | -0.098489 | 0.011752 | 0.082632 | -0.039857 | 0.058632 | -0.19315 | -0.097017 | -0.28973 | -0.1559 | 0.000521 | -0.075192 | 0.21454 | -0.037553 | -0.2175 | 121.7128 | 121.5079 | 121.604 | 60.8428 | -121.7995 | 121.5452 | 121.6635 | 121.4836 | 60.8555 | -121.9908
103.9531 | 122.0352 | -60.8368 | 60.878 | 1.4211e-13 | -0.01978 | -0.00049144 | 0.06474 | -0.0080593 | 0.062217 | -0.24059 | -0.0012156 | -0.00012596 | 0.062815 | 0.022188 | 0.061812 | -60.7633 | 0.005985 | -60.8858 | 60.8714 | 60.694 | 60.7627 | -60.9353 | -60.8408 | 0.018674 | -60.9166 | 60.7084 | 60.8313 | 60.633 | -61.1311 | -0.098488 | -0.006559 | 0.073476 | -0.049014 | 0.049474 | -0.18399 | -0.11533 | -0.29431 | -0.16963 | -0.004057 | -0.07977 | 0.21454 | -0.046707 | -0.24496 | 121.7082 | 121.5308 | 121.5995 | 60.8428 | -121.8133 | 121.5452 | 121.6681 | 121.4698 | 60.8555 | -122.0091
105.6875 | 121.9711 | -60.8643 | 60.8917 | 1.4211e-13 | -0.01978 | -0.00049144 | 0.064526 | -0.0080593 | 0.06243 | -0.22533 | -0.0012156 | -0.00033976 | 0.062387 | 0.022615 | 0.061385 | -60.7633 | -0.003172 | -60.8812 | 60.8714 | 60.6665 | 60.7581 | -60.9307 | -60.8363 | 0.014095 | -60.912 | 60.6992 | 60.8313 | 60.633 | -61.1265 | -0.066443 | -0.020292 | 0.10094 | -0.016969 | 0.049474 | -0.22519 | -0.13364 | -0.26226 | -0.19252 | 0.027988 | -0.047726 | 0.21454 | -0.06044 | -0.2587 | 121.7357 | 121.5308 | 121.6223 | 60.8611 | -121.8224 | 121.5635 | 121.6955 | 121.4973 | 60.8784 | -122.0182
107.3594 | 121.9574 | -60.9055 | 60.8734 | 1.4211e-13 | -0.01978 | -0.00049144 | 0.06474 | -0.0076321 | 0.062003 | -0.22533 | -0.001002 | -0.00033976 | 0.062601 | 0.022615 | 0.061385 | -60.7587 | -0.003172 | -60.8721 | 60.8623 | 60.6803 | 60.7718 | -60.9307 | -60.8408 | 0.009516 | -60.912 | 60.6946 | 60.8267 | 60.6284 | -61.1311 | -0.025244 | -0.011138 | 0.14672 | 0.033386 | 0.05863 | -0.19315 | -0.10159 | -0.22564 | -0.17879 | 0.064608 | -0.006527 | 0.21912 | -0.046708 | -0.24497 | 121.7677 | 121.5857 | 121.6773 | 60.9023 | -121.8041 | 121.6001 | 121.7322 | 121.5339 | 60.915 | -122.0045
109.0312 | 121.8933 | -60.8917 | 60.9146 | 1.4211e-13 | -0.019993 | -0.00049144 | 0.064526 | -0.0082731 | 0.062217 | -0.23296 | -0.00078837 | -0.00012596 | 0.063028 | 0.022188 | 0.061171 | -60.7633 | 0.001407 | -60.8812 | 60.8623 | 60.6528 | 60.7718 | -60.9399 | -60.85 | 0.014095 | -60.9028 | 60.7038 | 60.8175 | 60.6422 | -61.1311 | -0.048135 | -0.052337 | 0.12841 | 0.010497 | 0.058632 | -0.26182 | -0.14279 | -0.23938 | -0.21083 | 0.041718 | -0.011102 | 0.22827 | -0.097064 | -0.27243 | 121.754 | 121.5445 | 121.6635 | 60.8931 | -121.8545 | 121.5955 | 121.7093 | 121.5339 | 60.9058 | -122.0457
110.7812 | 122.0444 | -60.8322 | 60.8734 | 1.4211e-13 | -0.019993 | -0.00027784 | 0.06474 | -0.0078457 | 0.062003 | -0.23296 | -0.001002 | -0.00033976 | 0.062601 | 0.022829 | 0.061171 | -60.7587 | -0.003172 | -60.8812 | 60.8577 | 60.6711 | 60.7718 | -60.9353 | -60.8408 | 0.014095 | -60.912 | 60.7038 | 60.8221 | 60.6284 | -61.1311 | -0.10307 | -0.015716 | 0.073476 | -0.049013 | 0.054053 | -0.2023 | -0.10159 | -0.29889 | -0.16963 | -0.008635 | -0.07977 | 0.21912 | -0.051286 | -0.24497 | 121.6899 | 121.5033 | 121.604 | 60.829 | -121.8087 | 121.536 | 121.6543 | 121.4607 | 60.8463 | -122.0045
112.5312 | 122.0078 | -60.8597 | 60.8871 | 1.4211e-13 | -0.019993 | -0.00049144 | 0.064099 | -0.0080593 | 0.062003 | -0.22533 | -0.001002 | -0.00076696 | 0.062815 | 0.022401 | 0.061171 | -60.7587 | 0.005985 | -60.8812 | 60.8714 | 60.6803 | 60.7627 | -60.9307 | -60.8408 | 0.018674 | -60.9028 | 60.6946 | 60.8267 | 60.6376 | -61.1219 | -0.071021 | -0.015714 | 0.10094 | -0.021547 | 0.049474 | -0.20688 | -0.12448 | -0.26226 | -0.19252 | 0.018831 | -0.043146 | 0.21912 | -0.060441 | -0.24954 | 121.7311 | 121.5399 | 121.6223 | 60.8657 | -121.8178 | 121.5543 | 121.6864 | 121.4973 | 60.8784 | -122.0091
114.2031 | 122.0352 | -60.8459 | 60.8734 | 1.4211e-13 | -0.019993 | -0.00070504 | 0.06474 | -0.0082731 | 0.062217 | -0.22533 | -0.001002 | -0.00033976 | 0.062815 | 0.022615 | 0.061171 | -60.7587 | -0.003172 | -60.8766 | 60.8669 | 60.6665 | 60.7672 | -60.9353 | -60.8408 | 0.009516 | -60.912 | 60.6992 | 60.8175 | 60.633 | -61.1311 | -0.089333 | -0.006559 | 0.087209 | -0.030702 | 0.058631 | -0.20688 | -0.10617 | -0.28515 | -0.17421 | 0.005098 | -0.066037 | 0.21912 | -0.055865 | -0.24039 | 121.7128 | 121.5125 | 121.6132 | 60.8428 | -121.8087 | 121.5452 | 121.6635 | 121.479 | 60.8555 | -122.0045
115.9531 | 121.9711 | -60.8505 | 60.8643 | 1.4211e-13 | -0.01978 | -0.00049144 | 0.064312 | -0.0078457 | 0.062003 | -0.23296 | -0.00078837 | -0.00076696 | 0.062815 | 0.022615 | 0.061598 | -60.7542 | -0.003172 | -60.8766 | 60.8577 | 60.6848 | 60.7627 | -60.9399 | -60.8363 | 0.000359 | -60.912 | 60.6992 | 60.8221 | 60.6376 | -61.1219 | -0.089334 | -0.006561 | 0.096366 | -0.026124 | 0.06321 | -0.17941 | -0.10159 | -0.27142 | -0.16505 | 0.014255 | -0.061459 | 0.20996 | -0.042131 | -0.22665 | 121.7082 | 121.5354 | 121.6132 | 60.8474 | -121.8041 | 121.5497 | 121.6727 | 121.4881 | 60.8509 | -121.9862
117.7031 | 121.9025 | -60.9192 | 60.9009 | 1.4211e-13 | -0.020207 | -0.00049144 | 0.064526 | -0.0080593 | 0.06243 | -0.23296 | -0.0012156 | -0.00033976 | 0.062815 | 0.022829 | 0.061171 | -60.7542 | -0.003172 | -60.8766 | 60.8623 | 60.6757 | 60.7672 | -60.9307 | -60.85 | 0.009516 | -60.912 | 60.6946 | 60.8267 | 60.6284 | -61.1219 | -0.011512 | -0.038604 | 0.16503 | 0.04254 | 0.054052 | -0.22519 | -0.13364 | -0.20275 | -0.20625 | 0.069183 | 0.007205 | 0.20996 | -0.074174 | -0.27243 | 121.7815 | 121.5949 | 121.6864 | 60.916 | -121.8316 | 121.6138 | 121.7459 | 121.5476 | 60.9287 | -122.0228
119.375 | 121.907 | -60.8963 | 60.9146 | 1.4211e-13 | -0.01978 | -0.00070504 | 0.064312 | -0.0078457 | 0.062217 | -0.22533 | -0.001002 | -0.00033976 | 0.062601 | 0.022615 | 0.061385 | -60.7587 | -0.003172 | -60.8721 | 60.8577 | 60.6711 | 60.7627 | -60.9353 | -60.8408 | 0.014095 | -60.9074 | 60.69 | 60.8221 | 60.6284 | -61.1219 | -0.038979 | -0.056915 | 0.13756 | 0.02423 | 0.063209 | -0.2435 | -0.15195 | -0.22564 | -0.22456 | 0.055452 | -0.011104 | 0.21454 | -0.092485 | -0.28616 | 121.754 | 121.5674 | 121.659 | 60.8931 | -121.8499 | 121.5864 | 121.7184 | 121.5247 | 60.9104 | -122.0366
121.1094 | 122.0215 | -60.8414 | 60.8963 | 1.4211e-13 | -0.020207 | -0.00070504 | 0.064526 | -0.0078457 | 0.062217 | -0.23296 | -0.0012156 | -0.00076696 | 0.062601 | 0.022829 | 0.061171 | -60.7542 | 0.001407 | -60.8721 | 60.8577 | 60.6757 | 60.7581 | -60.9353 | -60.8363 | 0.009516 | -60.912 | 60.6946 | 60.8313 | 60.6239 | -61.1219 | -0.09391 | -0.038604 | 0.087211 | -0.030701 | 0.063209 | -0.22061 | -0.13822 | -0.28057 | -0.20167 | 0.0051 | -0.070614 | 0.20996 | -0.065017 | -0.27243 | 121.6991 | 121.5171 | 121.5995 | 60.8428 | -121.8316 | 121.536 | 121.6727 | 121.4652 | 60.8509 | -122.0182
122.8594 | 121.9391 | -60.91 | 60.8551 | 1.4211e-13 | -0.019993 | -0.00070504 | 0.064526 | -0.0082731 | 0.062003 | -0.2177 | -0.0012156 | -0.00012596 | 0.062387 | 0.022188 | 0.061171 | -60.7587 | 0.001407 | -60.8721 | 60.8669 | 60.6848 | 60.7627 | -60.9307 | -60.8363 | 0.014095 | -60.912 | 60.6946 | 60.8267 | 60.6284 | -61.1219 | -0.020667 | 0.011751 | 0.1513 | 0.037963 | 0.05863 | -0.17026 | -0.09244 | -0.21191 | -0.16048 | 0.073764 | -0.00195 | 0.20996 | -0.028398 | -0.22666 | 121.7769 | 121.5949 | 121.6727 | 60.9114 | -121.7858 | 121.6047 | 121.7367 | 121.5385 | 60.9241 | -121.977
124.5312 | 121.8796 | -60.8871 | 60.91 | 1.4211e-13 | -0.01978 | -0.00091884 | 0.064312 | -0.0084867 | 0.062003 | -0.24059 | -0.0012156 | -0.00033976 | 0.062601 | 0.022829 | 0.061598 | -60.745 | -0.007751 | -60.8766 | 60.8531 | 60.6848 | 60.7672 | -60.9261 | -60.8408 | 0.014095 | -60.9028 | 60.6946 | 60.8267 | 60.6239 | -61.1219 | -0.038976 | -0.056916 | 0.14214 | 0.010497 | 0.049473 | -0.22519 | -0.14279 | -0.2348 | -0.21541 | 0.046297 | -0.01568 | 0.21912 | -0.083329 | -0.28617 | 121.7403 | 121.572 | 121.6544 | 60.8794 | -121.8362 | 121.5818 | 121.7139 | 121.511 | 60.9012 | -122.032
126.2656 | 122.0123 | -60.8597 | 60.878 | 1.4211e-13 | -0.01978 | -0.00070504 | 0.064312 | -0.0082731 | 0.062217 | -0.23296 | -0.0012156 | -0.00012596 | 0.062815 | 0.022829 | 0.060957 | -60.7587 | 0.001407 | -60.8812 | 60.8577 | 60.6848 | 60.7672 | -60.9399 | -60.8271 | 0.009516 | -60.9074 | 60.6946 | 60.8175 | 60.6284 | -61.1311 | -0.080179 | -0.020294 | 0.10094 | -0.021547 | 0.058632 | -0.19315 | -0.11075 | -0.27142 | -0.18336 | 0.032567 | -0.047725 | 0.2237 | -0.060443 | -0.24954 | 121.7174 | 121.5445 | 121.6269 | 60.8611 | -121.8178 | 121.5543 | 121.6772 | 121.4881 | 60.8692 | -122.0091
127.9375 | 122.0352 | -60.8414 | 60.878 | 1.4211e-13 | -0.020207 | -0.00049144 | 0.064526 | -0.0080593 | 0.062003 | -0.23296 | -0.0012156 | -0.00055336 | 0.062601 | 0.022829 | 0.060957 | -60.7587 | -0.003172 | -60.8812 | 60.8577 | 60.662 | 60.7627 | -60.9261 | -60.8408 | 0.014095 | -60.9028 | 60.6855 | 60.8221 | 60.6239 | -61.1265 | -0.084752 | -0.020294 | 0.082632 | -0.039857 | 0.044895 | -0.21604 | -0.11533 | -0.28515 | -0.19252 | 0.000521 | -0.061456 | 0.22369 | -0.055864 | -0.25412 | 121.6991 | 121.5033 | 121.604 | 60.8382 | -121.8041 | 121.5268 | 121.6635 | 121.4652 | 60.8555 | -122.0045
129.6719 | 122.0169 | -60.8322 | 60.8551 | 1.4211e-13 | -0.019993 | -0.00049144 | 0.06474 | -0.0080593 | 0.062217 | -0.23296 | -0.001002 | -0.00033976 | 0.063028 | 0.022615 | 0.061171 | -60.7542 | -0.007751 | -60.8721 | 60.8623 | 60.6482 | 60.7627 | -60.9261 | -60.8363 | 0.009516 | -60.9028 | 60.69 | 60.8221 | 60.6284 | -61.1219 | -0.093908 | 0.007172 | 0.078055 | -0.039857 | 0.054051 | -0.20689 | -0.09244 | -0.28973 | -0.16505 | -0.004056 | -0.070612 | 0.21912 | -0.032976 | -0.22666 | 121.6945 | 121.4804 | 121.5949 | 60.8245 | -121.7812 | 121.5223 | 121.6543 | 121.4607 | 60.8417 | -121.977
131.4062 | 122.0169 | -60.8551 | 60.8231 | 1.4211e-13 | -0.019993 | -0.00049144 | 0.064312 | -0.0080593 | 0.062003 | -0.24059 | -0.001002 | -0.00055336 | 0.062387 | 0.022615 | 0.061385 | -60.7587 | -0.007751 | -60.8721 | 60.8531 | 60.6528 | 60.7581 | -60.9307 | -60.8317 | 0.004938 | -60.9028 | 60.69 | 60.8175 | 60.633 | -61.1265 | -0.075598 | 0.030059 | 0.096365 | -0.016968 | 0.05863 | -0.17027 | -0.064974 | -0.27142 | -0.13301 | 0.023411 | -0.047723 | 0.22369 | -0.005511 | -0.19003 | 121.7082 | 121.5079 | 121.6132 | 60.8474 | -121.7538 | 121.5452 | 121.6727 | 121.4881 | 60.86 | -121.9496
133.1562 | 121.8887 | -60.9238 | 60.878 | 1.4211e-13 | -0.020207 | -0.00070504 | 0.06474 | -0.0082731 | 0.062003 | -0.23296 | -0.0012156 | -0.00055336 | 0.062815 | 0.023042 | 0.061171 | -60.7587 | -0.012329 | -60.8812 | 60.8623 | 60.6436 | 60.7581 | -60.9215 | -60.8317 | 0.014095 | -60.9028 | 60.69 | 60.8175 | 60.6193 | -61.1219 | 0.002224 | -0.015716 | 0.16503 | 0.04254 | 0.040316 | -0.23436 | -0.11991 | -0.19817 | -0.18794 | 0.092075 | 0.020941 | 0.21912 | -0.060443 | -0.2587 | 121.786 | 121.5674 | 121.6819 | 60.9114 | -121.7995 | 121.6138 | 121.7413 | 121.5431 | 60.9379 | -121.9999
134.9062 | 121.9025 | -60.9329 | 60.8414 | 1.4211e-13 | -0.020635 | -0.00049144 | 0.064526 | -0.0080593 | 0.062003 | -0.23296 | -0.00078837 | -0.00033976 | 0.062387 | 0.022829 | 0.061385 | -60.7496 | -0.003172 | -60.8721 | 60.8485 | 60.6757 | 60.7627 | -60.9215 | -60.8317 | 0.014095 | -60.8982 | 60.69 | 60.8175 | 60.6239 | -61.1265 | 0.011379 | 0.00717 | 0.18334 | 0.060851 | 0.049472 | -0.16568 | -0.078707 | -0.1936 | -0.15132 | 0.10123 | 0.034674 | 0.22827 | -0.023822 | -0.2175 | 121.7815 | 121.6086 | 121.6956 | 60.9297 | -121.7629 | 121.623 | 121.7505 | 121.5568 | 60.947 | -121.9679
136.6562 | 121.9025 | -60.9055 | 60.9238 | 1.4211e-13 | -0.020207 | -0.00049144 | 0.064526 | -0.0080593 | 0.062003 | -0.23296 | -0.0012156 | -0.00033976 | 0.062387 | 0.022829 | 0.060957 | -60.7542 | 0.001407 | -60.8721 | 60.8531 | 60.6757 | 60.7627 | -60.9261 | -60.8317 | 0.018674 | -60.9028 | 60.6855 | 60.8175 | 60.6239 | -61.1174 | -0.020665 | -0.070649 | 0.1513 | 0.033386 | 0.054051 | -0.24808 | -0.1611 | -0.21191 | -0.2383 | 0.073765 | 0.002631 | 0.21454 | -0.10622 | -0.2999 | 121.7586 | 121.5811 | 121.6681 | 60.9069 | -121.8499 | 121.5909 | 121.723 | 121.5293 | 60.9241 | -122.0411
138.3906 | 121.9162 | -60.8643 | 60.8871 | 1.4211e-13 | -0.020421 | -0.00049144 | 0.064526 | -0.0078457 | 0.062217 | -0.22533 | -0.0012156 | -0.00055336 | 0.062601 | 0.023042 | 0.060957 | -60.745 | -0.007751 | -60.8721 | 60.8485 | 60.662 | 60.7627 | -60.9261 | -60.8363 | 0.014095 | -60.9074 | 60.69 | 60.8221 | 60.6193 | -61.1265 | -0.061864 | -0.038606 | 0.11926 | -0.007813 | 0.054051 | -0.22519 | -0.12448 | -0.26226 | -0.1971 | 0.027988 | -0.043147 | 0.21912 | -0.065019 | -0.26786 | 121.7128 | 121.5262 | 121.6269 | 60.8565 | -121.8133 | 121.5543 | 121.6864 | 121.4835 | 60.8784 | -122.0137
140.0625 | 121.9986 | -60.8459 | 60.8368 | 1.4211e-13 | -0.020207 | -0.00027784 | 0.064526 | -0.0080593 | 0.061789 | -0.2177 | -0.00078837 | -0.00055336 | 0.062387 | 0.022829 | 0.060957 | -60.7496 | -0.007751 | -60.8766 | 60.8531 | 60.6986 | 60.7581 | -60.9215 | -60.8363 | 0.009516 | -60.9028 | 60.6855 | 60.8175 | 60.6147 | -61.1174 | -0.075596 | 0.016326 | 0.096366 | -0.030702 | 0.044894 | -0.13821 | -0.078707 | -0.27142 | -0.15132 | 0.009677 | -0.056879 | 0.21454 | -0.019244 | -0.22208 | 121.6991 | 121.5445 | 121.604 | 60.8382 | -121.7583 | 121.5314 | 121.6635 | 121.4607 | 60.8555 | -121.9542
141.8125 | 121.9849 | -60.8871 | 60.8597 | 1.4211e-13 | -0.020421 | -0.00027784 | 0.064312 | -0.0078457 | 0.062217 | -0.23296 | -0.0012156 | -0.00033976 | 0.062601 | 0.023042 | 0.060957 | -60.7496 | -0.007751 | -60.8721 | 60.8531 | 60.6986 | 60.7627 | -60.9215 | -60.8317 | 0.004938 | -60.8982 | 60.69 | 60.813 | 60.6239 | -61.1174 | -0.034397 | -0.006562 | 0.13757 | 0.015075 | 0.049472 | -0.1611 | -0.097017 | -0.23022 | -0.16963 | 0.055454 | -0.011102 | 0.21911 | -0.046711 | -0.23581 | 121.7403 | 121.5857 | 121.6498 | 60.8794 | -121.7812 | 121.5772 | 121.7001 | 121.511 | 60.8921 | -121.977
143.5469 | 121.8979 | -60.9192 | 60.8688 | 1.4211e-13 | -0.020421 | -0.00049144 | 0.06474 | -0.0082731 | 0.061789 | -0.23296 | -0.0012156 | -0.00033976 | 0.062815 | 0.022829 | 0.060957 | -60.745 | -0.003172 | -60.8721 | 60.8577 | 60.7123 | 60.7535 | -60.9261 | -60.8271 | 0.004938 | -60.9074 | 60.6946 | 60.813 | 60.6101 | -61.1265 | -0.006933 | -0.011138 | 0.17419 | 0.047118 | 0.054051 | -0.15652 | -0.11533 | -0.20733 | -0.17421 | 0.092076 | 0.011784 | 0.21912 | -0.055866 | -0.2587 | 121.7769 | 121.6315 | 121.6727 | 60.916 | -121.795 | 121.6138 | 121.7322 | 121.5293 | 60.9241 | -121.9954
145.2812 | 121.9986 | -60.8414 | 60.8917 | 1.4211e-13 | -0.020421 | -0.00049144 | 0.064526 | -0.0080593 | 0.062217 | -0.23296 | -0.001002 | -0.00055336 | 0.062387 | 0.023042 | 0.061171 | -60.7496 | -0.003172 | -60.8766 | 60.8531 | 60.6803 | 60.7489 | -60.9307 | -60.8271 | 0.014095 | -60.9028 | 60.6855 | 60.8175 | 60.6193 | -61.1265 | -0.089331 | -0.038606 | 0.091789 | -0.035279 | 0.054052 | -0.21146 | -0.1428 | -0.28515 | -0.20625 | 0.014257 | -0.061456 | 0.22369 | -0.074176 | -0.27243 | 121.6945 | 121.5216 | 121.5903 | 60.8382 | -121.8224 | 121.5268 | 121.6589 | 121.4607 | 60.8555 | -122.0182
146.9531 | 121.8842 | -60.9009 | 60.8826 | 1.4211e-13 | -0.020635 | -0.00027784 | 0.064526 | -0.0080593 | 0.062217 | -0.22533 | -0.0014292 | -0.00055336 | 0.062174 | 0.022829 | 0.061171 | -60.7542 | -0.003172 | -60.8812 | 60.8485 | 60.6574 | 60.7581 | -60.9353 | -60.8317 | 0.009516 | -60.9074 | 60.69 | 60.813 | 60.6147 | -61.1265 | -0.034401 | -0.034028 | 0.14672 | 0.019652 | 0.054053 | -0.2252 | -0.12448 | -0.22564 | -0.19252 | 0.069187 | -0.006526 | 0.21912 | -0.069599 | -0.26786 | 121.7494 | 121.5583 | 121.659 | 60.8977 | -121.8178 | 121.5909 | 121.7138 | 121.5156 | 60.9104 | -122.0091
148.6875 | 121.9208 | -60.8963 | 60.9055 | 1.4211e-13 | -0.020421 | -0.00070504 | 0.064526 | -0.0080593 | 0.06243 | -0.21007 | -0.001002 | -0.00012596 | 0.062387 | 0.023256 | 0.061171 | -60.7542 | -0.012329 | -60.8766 | 60.844 | 60.6665 | 60.7535 | -60.9307 | -60.8317 | 0.014095 | -60.8982 | 60.6855 | 60.8084 | 60.6147 | -61.1265 | -0.0344 | -0.061495 | 0.14214 | 0.019652 | 0.054052 | -0.23893 | -0.15195 | -0.23022 | -0.21999 | 0.064609 | -0.001947 | 0.22827 | -0.097066 | -0.29075 | 121.7403 | 121.5628 | 121.6498 | 60.884 | -121.8362 | 121.5818 | 121.7047 | 121.511 | 60.9104 | -122.032
150.4219 | 121.9391 | -60.9283 | 60.8414 | 1.4211e-13 | -0.019993 | -0.00027784 | 0.064312 | -0.0082731 | 0.062217 | -0.22533 | -0.001002 | -0.00076696 | 0.062387 | 0.023256 | 0.060957 | -60.7542 | -0.003172 | -60.8766 | 60.844 | 60.7215 | 60.7489 | -60.9261 | -60.8271 | 0.004938 | -60.9028 | 60.6809 | 60.8038 | 60.6056 | -61.1311 | 0.002223 | 0.002592 | 0.17419 | 0.051696 | 0.049473 | -0.11989 | -0.092442 | -0.20276 | -0.16048 | 0.10123 | 0.025519 | 0.22827 | -0.037558 | -0.23581 | 121.7723 | 121.6498 | 121.6773 | 60.9252 | -121.7675 | 121.6092 | 121.7322 | 121.5339 | 60.9333 | -121.9725
152.1094 | 122.0398 | -60.8368 | 60.8597 | 1.4211e-13 | -0.020421 | -6.4044e-05 | 0.064099 | -0.0078457 | 0.06243 | -0.23296 | -0.0012156 | -0.00012596 | 0.062387 | 0.023256 | 0.061171 | -60.7587 | -0.003172 | -60.8812 | 60.844 | 60.7169 | 60.7535 | -60.9261 | -60.8363 | 0.014095 | -60.9074 | 60.6809 | 60.8084 | 60.6101 | -61.1265 | -0.08933 | -0.015718 | 0.078054 | -0.044435 | 0.044895 | -0.14278 | -0.10617 | -0.28973 | -0.17879 | 0.000522 | -0.070613 | 0.21912 | -0.051289 | -0.24955 | 121.6808 | 121.5537 | 121.5903 | 60.8336 | -121.7858 | 121.5177 | 121.6452 | 121.4469 | 60.8509 | -121.9862
153.8594 | 121.9116 | -69.2276 | 52.4963 | 1.4211e-13 | -0.020421 | -0.00027784 | 0.064526 | -0.0080593 | 0.062217 | -0.23296 | -0.0012156 | -0.00033976 | 0.062387 | 0.022829 | 0.060744 | -68.8487 | -0.044379 | -68.9894 | 52.6761 | 52.6168 | 52.6723 | -69.0903 | -68.9543 | -0.036271 | -69.0071 | 52.5312 | 52.6402 | 52.4465 | -69.286 | 0.13725 | 0.17978 | 0.37885 | 0.23824 | 0.10098 | 0.12044 | 0.17593 | -0.058373 | 0.034832 | 0.27328 | 0.22046 | 0.27883 | 0.14383 | -0.049853 | 121.9037 | 121.8444 | 121.8999 | 69.1832 | -121.5867 | 121.7588 | 121.8678 | 121.6741 | 69.1913 | -121.7823
155.5938 | 121.875 | -70.4224 | 51.3428 | 1.4211e-13 | -0.020635 | -0.00049144 | 0.064099 | -0.0082731 | 0.062217 | -0.22533 | -0.0014292 | -0.00055336 | 0.062174 | 0.023042 | 0.061171 | -70.1948 | -0.026065 | -70.3445 | 51.3118 | 51.1195 | 51.2483 | -70.432 | -70.2913 | -0.022535 | -70.3533 | 51.1805 | 51.2849 | 51.1004 | -70.6596 | -0.009607 | -0.031015 | 0.22757 | 0.07783 | 0.087437 | -0.2233 | -0.094446 | -0.23725 | -0.16226 | 0.13106 | 0.06908 | 0.30633 | -0.057876 | -0.2424 | 121.7341 | 121.5418 | 121.6707 | 70.3963 | -121.7747 | 121.6029 | 121.7073 | 121.5227 | 70.3998 | -122.0024
157.3594 | 122.0215 | -70.5139 | 51.1688 | 1.4211e-13 | -0.020635 | -0.00070504 | 0.064312 | -0.0080593 | 0.062217 | -0.23296 | -0.001002 | -0.00055336 | 0.062387 | 0.02347 | 0.060957 | -70.355 | -0.026065 | -70.5185 | 51.1469 | 50.9501 | 51.0881 | -70.6151 | -70.4607 | -0.008798 | -70.5135 | 51.0065 | 51.1246 | 50.931 | -70.8199 | -0.10121 | -0.021887 | 0.15888 | -0.004592 | 0.096619 | -0.21877 | -0.080747 | -0.30596 | -0.16229 | 0.053198 | 0.000378 | 0.30634 | -0.044177 | -0.23786 | 121.6609 | 121.464 | 121.602 | 70.4879 | -121.784 | 121.5204 | 121.6386 | 121.4449 | 70.5051 | -121.9887
159.0312 | 121.8887 | -70.784 | 50.9811 | 1.4211e-13 | -0.020848 | -0.00027784 | 0.063885 | -0.0078457 | 0.062217 | -0.23296 | -0.0012156 | -0.00033976 | 0.062601 | 0.022829 | 0.060744 | -70.584 | -0.030644 | -70.7383 | 50.918 | 50.7119 | 50.8683 | -70.8303 | -70.6851 | -0.017956 | -70.7471 | 50.7776 | 50.8957 | 50.702 | -71.0534 | -0.046339 | -0.063123 | 0.20004 | 0.045732 | 0.092071 | -0.26919 | -0.11284 | -0.2694 | -0.20353 | 0.098922 | 0.036944 | 0.30634 | -0.085424 | -0.2791 | 121.702 | 121.4959 | 121.6523 | 70.7534 | -121.8115 | 121.5616 | 121.6797 | 121.486 | 70.766 | -122.0345
160.75 | 121.9757 | -60.8963 | 60.8368 | 1.4211e-13 | -0.020635 | -0.00027784 | 0.064526 | -0.0080593 | 0.061789 | -0.22533 | -0.001002 | -0.00055336 | 0.062387 | 0.023256 | 0.060744 | -60.7816 | 0.010564 | -60.8995 | 60.8073 | 60.6803 | 60.7169 | -60.949 | -60.8637 | 0.023253 | -60.9395 | 60.6488 | 60.7855 | 60.5827 | -61.1494 | -0.052716 | -0.029457 | 0.11467 | -0.00324 | 0.049476 | -0.15653 | -0.11992 | -0.25311 | -0.18795 | 0.032559 | -0.043155 | 0.20996 | -0.051294 | -0.25413 | 121.7036 | 121.5766 | 121.6132 | 60.9069 | -121.7858 | 121.5451 | 121.6818 | 121.479 | 60.9196 | -121.9862
162.4219 | 121.8567 | -60.9558 | 60.8368 | 1.4211e-13 | -0.020421 | -0.00049144 | 0.064099 | -0.0080593 | 0.061789 | -0.22533 | -0.0014292 | -0.00033976 | 0.062601 | 0.023042 | 0.060957 | -60.7862 | -0.003172 | -60.9087 | 60.8073 | 60.6253 | 60.7077 | -60.9582 | -60.8683 | 0.009516 | -60.9349 | 60.6443 | 60.7763 | 60.5689 | -61.1494 | -0.002364 | -0.029457 | 0.1696 | 0.047114 | 0.049478 | -0.21147 | -0.12907 | -0.1936 | -0.19253 | 0.08749 | 0.020934 | 0.21454 | -0.060451 | -0.26787 | 121.7631 | 121.5811 | 121.6635 | 60.9526 | -121.795 | 121.6001 | 121.7322 | 121.5247 | 60.9653 | -121.9862
164.0938 | 121.994 | -60.8871 | 60.8231 | 1.4211e-13 | -0.020848 | -0.00070504 | 0.064526 | -0.0082731 | 0.062003 | -0.24059 | -0.001002 | -0.00033976 | 0.062387 | 0.022829 | 0.060744 | -60.7771 | 0.001407 | -60.9133 | 60.8028 | 60.6116 | 60.7077 | -60.9628 | -60.8683 | 0.009516 | -60.9349 | 60.6397 | 60.7672 | 60.5781 | -61.1632 | -0.075608 | -0.020303 | 0.1101 | -0.026129 | 0.049479 | -0.21148 | -0.11534 | -0.276 | -0.18337 | 0.018825 | -0.047731 | 0.22827 | -0.055876 | -0.24498 | 121.6899 | 121.4987 | 121.5949 | 60.8886 | -121.7858 | 121.5268 | 121.6543 | 121.4652 | 60.8967 | -121.9862
165.8281 | 121.8887 | -60.9558 | 60.8093 | 1.4211e-13 | -0.020635 | -0.00049144 | 0.064099 | -0.0084867 | 0.061789 | -0.23296 | -0.0012156 | -0.00033976 | 0.062601 | 0.02347 | 0.060957 | -60.7954 | 0.001407 | -60.9179 | 60.7982 | 60.6391 | 60.7031 | -60.9673 | -60.8821 | 0.018674 | -60.9395 | 60.6305 | 60.758 | 60.5552 | -61.1632 | -0.011522 | -0.011148 | 0.16045 | 0.037957 | 0.049479 | -0.17027 | -0.10618 | -0.20734 | -0.1788 | 0.073754 | 0.016355 | 0.22369 | -0.0513 | -0.25414 | 121.754 | 121.5949 | 121.659 | 60.9572 | -121.7767 | 121.5863 | 121.7138 | 121.511 | 60.9745 | -121.9725
167.5 | 121.8658 | -60.9604 | 60.8002 | 1.4211e-13 | -0.020421 | -0.00049144 | 0.064526 | -0.0082731 | 0.062003 | -0.22533 | -0.00078837 | -0.00033976 | 0.062601 | 0.02347 | 0.060744 | -60.7954 | 0.010564 | -60.9224 | 60.7799 | 60.6391 | 60.6894 | -60.9856 | -60.8821 | 0.014095 | -60.9624 | 60.6122 | 60.7443 | 60.546 | -61.1815 | -0.02526 | -0.020307 | 0.16502 | 0.037956 | 0.063216 | -0.16111 | -0.11077 | -0.22108 | -0.18796 | 0.078331 | -0.001962 | 0.21912 | -0.055881 | -0.25414 | 121.7403 | 121.5994 | 121.6498 | 60.971 | -121.7858 | 121.5726 | 121.7047 | 121.5064 | 60.9745 | -121.9816
169.2344 | 121.8842 | -61.0062 | 60.7773 | 1.4211e-13 | -0.020421 | -0.00027784 | 0.06474 | -0.0080593 | 0.062217 | -0.22533 | -0.001002 | -0.00012596 | 0.062387 | 0.02347 | 0.060744 | -60.8274 | -0.003172 | -60.9682 | 60.7524 | 60.5887 | 60.6619 | -61.0177 | -60.9187 | 0.009516 | -60.9761 | 60.5893 | 60.7168 | 60.5231 | -61.2089 | -0.011536 | -0.024889 | 0.17875 | 0.03795 | 0.049486 | -0.18859 | -0.11535 | -0.20277 | -0.18796 | 0.087478 | 0.030079 | 0.23285 | -0.060464 | -0.25414 | 121.7586 | 121.5949 | 121.6681 | 61.003 | -121.795 | 121.5955 | 121.723 | 121.5293 | 61.0157 | -121.9862
170.9062 | 121.8658 | -60.9833 | 60.791 | 1.4211e-13 | -0.020848 | -0.00049144 | 0.064312 | -0.0084867 | 0.062217 | -0.23296 | -0.0012156 | -0.00033976 | 0.062601 | 0.023256 | 0.060957 | -60.8503 | -0.007751 | -60.9728 | 60.7341 | 60.5704 | 60.6436 | -61.0314 | -60.937 | 0.014095 | -61.0036 | 60.5619 | 60.6985 | 60.4957 | -61.2318 | -0.048162 | -0.056936 | 0.13297 | 0.010483 | 0.058645 | -0.22064 | -0.1474 | -0.24856 | -0.22917 | 0.046274 | -0.020282 | 0.22828 | -0.092512 | -0.29535 | 121.7174 | 121.5536 | 121.6269 | 60.9755 | -121.8225 | 121.5451 | 121.6818 | 121.4789 | 60.9974 | -122.0229
172.6406 | 121.8979 | -61.084 | 60.6766 | 1.4211e-13 | -0.020421 | -0.00049144 | 0.064099 | -0.0082731 | 0.062003 | -0.23296 | -0.0014292 | -0.00012596 | 0.062174 | 0.02347 | 0.061171 | -62.3566 | 0.0243 | -62.4882 | 59.2461 | 59.1097 | 59.1602 | -62.5059 | -62.4205 | 0.046146 | -62.4596 | 59.0967 | 59.2196 | 59.058 | -62.6925 | -1.4219 | -1.4305 | -1.2726 | -1.4042 | 0.017647 | -1.5669 | -1.5164 | -1.6085 | -1.5798 | -1.3365 | -1.3756 | 0.23289 | -1.457 | -1.6186 | 120.3301 | 120.1937 | 120.2441 | 61.1083 | -123.1824 | 120.1807 | 120.3036 | 120.142 | 61.1301 | -123.3691
174.375 | 121.8063 | -70.9488 | 50.8301 | 1.4211e-13 | -0.020635 | -0.00070504 | 0.064099 | -0.0078457 | 0.062644 | -0.22533 | -0.001643 | -0.00098076 | 0.062174 | 0.023256 | 0.060744 | -94.4648 | 0.11587 | -94.6048 | 26.7441 | 26.5581 | 26.8306 | -94.9567 | -94.65 | 0.19267 | -94.6662 | 26.5665 | 26.7482 | 26.5636 | -95.0601 | -24.0079 | -24.0859 | -23.516 | -23.6561 | 0.35185 | -24.272 | -23.9994 | -24.1113 | -24.2636 | -23.7013 | -23.7174 | 0.3939 | -24.0819 | -24.2664 | 97.6929 | 97.5069 | 97.7794 | 71.0647 | -145.7868 | 97.5153 | 97.697 | 97.5124 | 71.1415 | -145.8902
176.0625 | 121.9528 | -70.3995 | 51.329 | 1.4211e-13 | -0.020848 | -0.00049144 | 0.064312 | -0.0078457 | 0.061789 | -0.23296 | -0.0012156 | -0.00055336 | 0.062387 | 0.02347 | 0.060957 | -70.4191 | 0.001407 | -70.5643 | 51.1057 | 50.9455 | 51.056 | -70.6518 | -70.5248 | 0.018674 | -70.5456 | 50.9745 | 51.0926 | 50.9676 | -70.8474 | -0.25228 | -0.22331 | -0.019661 | -0.16482 | 0.087467 | -0.38357 | -0.27301 | -0.44788 | -0.35456 | -0.12535 | -0.14611 | 0.30176 | -0.23644 | -0.36144 | 121.5052 | 121.3449 | 121.4555 | 70.4009 | -121.9808 | 121.374 | 121.4921 | 121.3671 | 70.4181 | -122.1764
177.8125 | 121.907 | -69.7861 | 52.034 | 1.4211e-13 | -0.020848 | -0.00049144 | 0.064099 | -0.0082731 | 0.062217 | -0.24059 | -0.0012156 | -0.00055336 | 0.062387 | 0.02347 | 0.060744 | -71.1151 | 0.10214 | -71.3792 | 50.3182 | 50.2541 | 50.2227 | -71.3478 | -71.1658 | 0.10567 | -71.2049 | 50.2877 | 50.3325 | 50.3129 | -71.5479 | -1.5617 | -1.7157 | -1.329 | -1.5932 | -0.03147 | -1.7799 | -1.8113 | -1.7618 | -1.7463 | -1.3798 | -1.4189 | 0.34298 | -1.7014 | -1.7211 | 120.1043 | 120.0401 | 120.0088 | 69.8882 | -123.3818 | 120.0738 | 120.1186 | 120.0989 | 69.8917 | -123.5819
179.5625 | 121.9482 | -71.4386 | 50.2533 | 1.4211e-13 | -0.020635 | -0.0013462 | 0.064312 | -0.0087003 | 0.062217 | -0.22533 | -0.0012156 | -0.00033976 | 0.062174 | 0.02347 | 0.060744 | -71.1013 | -0.021486 | -71.2144 | 50.4281 | 50.2312 | 50.3738 | -71.3203 | -71.207 | -0.00422 | -71.2187 | 50.2923 | 50.4104 | 50.2121 | -71.5342 | 0.11832 | 0.17483 | 0.33728 | 0.22419 | 0.10587 | -0.022135 | 0.12052 | -0.095573 | 0.03899 | 0.23155 | 0.21994 | 0.31551 | 0.15709 | -0.041169 | 121.8667 | 121.6698 | 121.8124 | 71.4171 | -121.5736 | 121.7309 | 121.849 | 121.6507 | 71.4344 | -121.7875
181.2344 | 121.8979 | -73.2422 | 48.4177 | 1.4211e-13 | -0.020848 | -0.00027784 | 0.064526 | -0.0084867 | 0.062003 | -0.24059 | -0.0012156 | -0.00055336 | 0.062387 | 0.023256 | 0.060957 | -73.1158 | -0.035222 | -73.2838 | 48.3495 | 48.1615 | 48.2997 | -73.3854 | -73.2217 | -0.013377 | -73.2791 | 48.2182 | 48.3363 | 48.1426 | -73.613 | -0.14319 | -0.068123 | 0.12638 | -0.041602 | 0.10159 | -0.25618 | -0.11796 | -0.37077 | -0.19944 | 0.020507 | -0.036892 | 0.33388 | -0.081387 | -0.27507 | 121.5917 | 121.4037 | 121.5419 | 73.207 | -121.803 | 121.4604 | 121.5785 | 121.3848 | 73.2288 | -122.0306
182.9844 | 121.8887 | -72.3358 | 49.4064 | 1.4211e-13 | -0.020635 | -0.00049144 | 0.064526 | -0.0084867 | 0.062217 | -0.22533 | -0.0014292 | -0.00033976 | 0.062601 | 0.023684 | 0.060957 | -72.4153 | -0.007751 | -72.5833 | 49.05 | 48.8666 | 49.0048 | -72.6848 | -72.5257 | 0.018674 | -72.5694 | 48.9233 | 49.0414 | 48.8706 | -72.8987 | -0.34899 | -0.3564 | -0.079498 | -0.2475 | 0.10149 | -0.53979 | -0.40162 | -0.56285 | -0.48312 | -0.1899 | -0.23356 | 0.32928 | -0.36505 | -0.53584 | 121.3859 | 121.2025 | 121.3406 | 72.3281 | -122.0912 | 121.2591 | 121.3772 | 121.2064 | 72.3545 | -122.3051
184.7188 | 122.0078 | -109.5612 | 12.0758 | 1.4211e-13 | -0.021489 | -0.00091884 | 0.063885 | -0.0080593 | 0.062217 | -0.23296 | -0.001643 | -0.00076696 | 0.06196 | 0.023684 | 0.061385 | -109.1248 | -0.14053 | -109.4476 | 12.0841 | 12.0933 | 12.1974 | -109.7466 | -109.3477 | -0.12327 | -109.3868 | 12.0344 | 12.1058 | 12.1273 | -109.9413 | -0.18546 | 0.008325 | 0.43633 | 0.11353 | 0.29899 | 0.017493 | 0.12162 | -0.38013 | -0.041426 | 0.21346 | 0.17437 | 0.55451 | 0.02999 | 0.051506 | 121.6453 | 121.6545 | 121.7586 | 109.4206 | -121.8224 | 121.5955 | 121.667 | 121.6885 | 109.4379 | -122.0171
186.4062 | 122.0032 | -110.2295 | 11.4395 | 1.4211e-13 | -0.021062 | -0.00091884 | 0.063885 | -0.0080593 | 0.062644 | -0.23296 | -0.0014292 | -0.00098076 | 0.061533 | 0.023684 | 0.061171 | -109.8619 | -0.12222 | -110.1985 | 11.3333 | 11.3515 | 11.4557 | -110.406 | -110.0757 | -0.10953 | -110.124 | 11.2881 | 11.3595 | 11.2528 | -110.6785 | -0.17649 | -0.10624 | 0.36754 | 0.031027 | 0.20752 | -0.088001 | 0.016179 | -0.44899 | -0.15143 | 0.15378 | 0.10553 | 0.55452 | -0.08003 | -0.18672 | 121.5628 | 121.581 | 121.6852 | 110.1073 | -121.8455 | 121.5176 | 121.589 | 121.4823 | 110.12 | -122.118
188.1562 | 121.9162 | -110.4584 | 11.261 | 1.4211e-13 | -0.021489 | -0.0011324 | 0.064312 | -0.0082731 | 0.06243 | -0.23296 | -0.001643 | -0.00076696 | 0.06196 | 0.023684 | 0.061171 | -109.8757 | -0.12222 | -110.2076 | 11.3241 | 11.1684 | 11.4511 | -110.4197 | -110.094 | -0.10037 | -110.1331 | 11.2835 | 11.3549 | 11.1612 | -110.706 | 0.038656 | 0.063133 | 0.58269 | 0.25075 | 0.2121 | -0.09263 | 0.19013 | -0.24758 | 0.022521 | 0.36434 | 0.32526 | 0.57284 | 0.093919 | -0.09976 | 121.7825 | 121.6267 | 121.9095 | 110.3362 | -121.6807 | 121.7419 | 121.8133 | 121.6196 | 110.358 | -121.9669
189.8906 | 121.9345 | -110.8337 | 10.9177 | 1.4211e-13 | -0.021062 | -0.00091884 | 0.063885 | -0.0084867 | 0.062858 | -0.23296 | -0.001643 | -0.00098076 | 0.062174 | 0.023256 | 0.061385 | -110.3473 | -0.10848 | -110.6792 | 10.8388 | 10.6876 | 10.9658 | -110.8959 | -110.5611 | -0.10037 | -110.6093 | 10.8119 | 10.8696 | 10.6896 | -111.1776 | -0.062186 | -0.078855 | 0.48648 | 0.15456 | 0.21674 | -0.2301 | 0.048118 | -0.34383 | -0.10574 | 0.27268 | 0.22444 | 0.56827 | -0.048091 | -0.22803 | 121.6725 | 121.5213 | 121.7995 | 110.7253 | -121.8136 | 121.6457 | 121.7033 | 121.5234 | 110.7334 | -122.0952
191.5625 | 121.8658 | -111.0718 | 10.7071 | 1.4211e-13 | -0.021276 | -0.0011324 | 0.064099 | -0.0082731 | 0.062217 | -0.22533 | -0.0012156 | -0.00076696 | 0.06196 | 0.024111 | 0.061598 | -110.5899 | -0.10848 | -110.9356 | 10.6007 | 10.4586 | 10.7277 | -111.1478 | -110.8129 | -0.091215 | -110.8566 | 10.5555 | 10.6315 | 10.447 | -111.4248 | -0.07599 | -0.10636 | 0.48187 | 0.13621 | 0.2122 | -0.24847 | 0.020603 | -0.35305 | -0.15156 | 0.25889 | 0.21523 | 0.56828 | -0.075606 | -0.26013 | 121.6725 | 121.5304 | 121.7995 | 110.9633 | -121.8549 | 121.6273 | 121.7033 | 121.5187 | 110.9806 | -122.1319
193.3125 | 121.8521 | -111.4426 | 10.3455 | 1.4211e-13 | -0.021276 | -0.00070504 | 0.063885 | -0.0082731 | 0.06243 | -0.23296 | -0.001643 | -0.00076696 | 0.06196 | 0.023684 | 0.061385 | -110.8875 | -0.11306 | -111.2286 | 10.3031 | 10.1564 | 10.4255 | -111.4546 | -111.1105 | -0.082058 | -111.1542 | 10.2671 | 10.3293 | 10.1448 | -111.7225 | -0.011989 | -0.042321 | 0.55506 | 0.21399 | 0.22598 | -0.18905 | 0.080048 | -0.27989 | -0.078378 | 0.33206 | 0.2884 | 0.56828 | -0.016161 | -0.20068 | 121.7457 | 121.599 | 121.8681 | 111.3295 | -121.8 | 121.7096 | 121.7719 | 121.5873 | 111.3605 | -122.0679
195.0469 | 121.9574 | -111.0764 | 10.6064 | 1.4211e-13 | -0.020848 | -0.00070504 | 0.063885 | -0.0082731 | 0.062644 | -0.24059 | -0.001643 | -0.0011944 | 0.062174 | 0.024111 | 0.061385 | -110.6998 | -0.10848 | -111.0409 | 10.4863 | 10.3396 | 10.6132 | -111.2439 | -110.9274 | -0.086637 | -110.9573 | 10.4456 | 10.5216 | 10.3371 | -111.5256 | -0.16757 | -0.12011 | 0.37656 | 0.035486 | 0.20306 | -0.26681 | 0.006846 | -0.44921 | -0.16074 | 0.149 | 0.11907 | 0.56828 | -0.084785 | -0.26931 | 121.5626 | 121.4159 | 121.6896 | 110.9679 | -121.8503 | 121.522 | 121.598 | 121.4134 | 110.9897 | -122.1319
196.7188 | 121.8567 | -111.5112 | 10.2539 | 1.4211e-13 | -0.021489 | -0.00070504 | 0.063885 | -0.0080593 | 0.062644 | -0.24822 | -0.0012156 | -0.00076696 | 0.062174 | 0.023684 | 0.061385 | -110.9058 | -0.10848 | -111.2469 | 10.2802 | 10.1244 | 10.4072 | -111.4637 | -111.1334 | -0.095794 | -111.1816 | 10.235 | 10.311 | 10.1219 | -111.7362 | 0.047518 | 0.02634 | 0.60541 | 0.26434 | 0.21682 | -0.12955 | 0.15329 | -0.22496 | -0.018874 | 0.37783 | 0.32959 | 0.55455 | 0.057078 | -0.13202 | 121.7915 | 121.6356 | 121.9184 | 111.4027 | -121.7176 | 121.7463 | 121.8222 | 121.6331 | 111.4154 | -121.9901
198.4531 | 121.8704 | -111.4151 | 10.3775 | 1.4211e-13 | -0.021276 | -0.0013462 | 0.063671 | -0.0082731 | 0.062644 | -0.22533 | -0.001643 | -0.00055336 | 0.061746 | 0.023897 | 0.061385 | -110.8417 | -0.1039 | -111.1874 | 10.3352 | 10.1839 | 10.4072 | -111.4042 | -111.0693 | -0.086637 | -111.1084 | 10.2946 | 10.3659 | 10.1814 | -111.6767 | 0.010914 | -0.042315 | 0.57338 | 0.22773 | 0.21681 | -0.19361 | 0.029691 | -0.26156 | -0.08295 | 0.3458 | 0.30672 | 0.56828 | -0.011575 | -0.1961 | 121.7503 | 121.599 | 121.8223 | 111.3112 | -121.7817 | 121.7097 | 121.781 | 121.5965 | 111.3285 | -122.0542
200.1875 | 121.9528 | -111.8271 | 9.8969 | 1.4211e-13 | -0.021276 | -0.0011324 | 0.063885 | -0.0080593 | 0.062217 | -0.24059 | -0.001643 | -0.00076696 | 0.062387 | 0.023897 | 0.061385 | -111.2126 | -0.11764 | -111.5491 | 9.9689 | 9.8176 | 10.0455 | -111.7751 | -111.431 | -0.095794 | -111.4793 | 9.9237 | 10.0042 | 9.806 | -112.043 | 0.052008 | 0.072065 | 0.61452 | 0.27803 | 0.22602 | -0.079278 | 0.14863 | -0.21588 | 0.026843 | 0.39607 | 0.34783 | 0.56371 | 0.10737 | -0.090891 | 121.796 | 121.6447 | 121.8726 | 111.7095 | -121.6719 | 121.7508 | 121.8313 | 121.633 | 111.7313 | -121.9398
201.9219 | 121.8567 | -111.969 | 9.8328 | 1.4211e-13 | -0.021276 | -0.0011324 | 0.063885 | -0.0084867 | 0.062644 | -0.23296 | -0.001643 | -0.00098076 | 0.062174 | 0.02347 | 0.061385 | -111.4644 | -0.1039 | -111.81 | 9.7034 | 9.5566 | 9.7891 | -112.0407 | -111.692 | -0.086637 | -111.7402 | 9.6719 | 9.7432 | 9.5496 | -112.3085 | -0.071663 | -0.12939 | 0.50461 | 0.15897 | 0.23064 | -0.27619 | -0.043683 | -0.33955 | -0.16089 | 0.27699 | 0.22875 | 0.5683 | -0.089527 | -0.28321 | 121.6724 | 121.5256 | 121.7581 | 111.8651 | -121.8734 | 121.6409 | 121.7122 | 121.5186 | 111.8824 | -122.1413
203.5938 | 121.7606 | -67.2272 | 54.6341 | 1.4211e-13 | -0.021276 | -0.00049144 | 0.064099 | -0.0084867 | 0.062003 | -0.23296 | -0.0012156 | -0.00055336 | 0.062387 | 0.023897 | 0.060744 | -67.988 | 0.10214 | -68.1836 | 53.514 | 53.3631 | 53.4186 | -68.1837 | -68.0615 | 0.11483 | -68.0777 | 53.4102 | 53.4964 | 53.3759 | -68.3839 | -0.95655 | -1.1201 | -0.76084 | -0.95641 | 0.000133 | -1.2709 | -1.2155 | -1.1568 | -1.2239 | -0.8343 | -0.85049 | 0.30628 | -1.1377 | -1.2582 | 120.7411 | 120.5903 | 120.6458 | 67.3293 | -122.8178 | 120.6374 | 120.7235 | 120.6031 | 67.342 | -123.018
205.3281 | 121.8109 | -67.7353 | 54.0665 | 1.4211e-13 | -0.021062 | -0.00027784 | 0.064099 | -0.0080593 | 0.062217 | -0.2177 | -0.0014292 | -0.00033976 | 0.06196 | 0.023256 | 0.060957 | -67.5256 | 0.0243 | -67.6342 | 54.013 | 53.8165 | 53.9451 | -67.7167 | -67.6219 | 0.03241 | -67.6381 | 53.8635 | 53.9909 | 53.7972 | -67.9306 | 0.018624 | -0.05346 | 0.2097 | 0.1011 | 0.082476 | -0.25001 | -0.12134 | -0.19535 | -0.20296 | 0.11337 | 0.097182 | 0.29253 | -0.075615 | -0.26929 | 121.7483 | 121.5517 | 121.6804 | 67.7596 | -121.7831 | 121.5988 | 121.7261 | 121.5325 | 67.7677 | -121.9971
207 | 121.7834 | -65.4602 | 56.3416 | 1.4211e-13 | -0.021062 | -0.00049144 | 0.064312 | -0.0087003 | 0.061576 | -0.2177 | -0.0012156 | -0.00055336 | 0.062174 | 0.023897 | 0.060957 | -65.8591 | 0.10671 | -66.0089 | 55.6338 | 55.4832 | 55.5614 | -66.1186 | -65.9415 | 0.10567 | -65.9989 | 55.5072 | 55.6208 | 55.4272 | -66.2823 | -0.65842 | -0.7078 | -0.39886 | -0.5487 | 0.10972 | -0.85836 | -0.78018 | -0.82206 | -0.83436 | -0.48133 | -0.53872 | 0.28334 | -0.72072 | -0.9144 | 121.094 | 120.9434 | 121.0216 | 65.5669 | -122.4602 | 120.9674 | 121.081 | 120.8874 | 65.5659 | -122.6238
208.7344 | 121.8887 | -61.1252 | 60.5804 | 1.4211e-13 | -0.020848 | -0.00027784 | 0.064526 | -0.0082731 | 0.061576 | -0.23296 | -0.001002 | -0.00076696 | 0.062174 | 0.023897 | 0.060744 | -60.9922 | 0.019721 | -61.1239 | 60.5601 | 60.4559 | 60.4651 | -61.178 | -61.0835 | 0.036989 | -61.1455 | 60.397 | 60.5154 | 60.3354 | -61.3875 | -0.05278 | -0.020342 | 0.13295 | 0.001307 | 0.054087 | -0.12454 | -0.11539 | -0.26233 | -0.18342 | 0.041662 | -0.020315 | 0.24201 | -0.065084 | -0.24503 | 121.6853 | 121.5811 | 121.5902 | 61.1449 | -121.7584 | 121.5222 | 121.6405 | 121.4606 | 61.1622 | -121.968
210.4219 | 121.8704 | -61.0977 | 60.5896 | 1.4211e-13 | -0.020848 | -0.00070504 | 0.064526 | -0.0082731 | 0.062003 | -0.22533 | -0.0014292 | -0.00033976 | 0.062174 | 0.023897 | 0.06053 | -61.006 | 0.019721 | -61.1285 | 60.5509 | 60.4467 | 60.4605 | -61.1825 | -61.0789 | 0.023253 | -61.1547 | 60.3833 | 60.5154 | 60.3308 | -61.4012 | -0.084825 | -0.038655 | 0.091746 | -0.030738 | 0.054087 | -0.14286 | -0.12912 | -0.30353 | -0.20631 | 0.018775 | -0.056938 | 0.24659 | -0.07424 | -0.25876 | 121.6487 | 121.5445 | 121.5582 | 61.1174 | -121.7721 | 121.481 | 121.6131 | 121.4286 | 61.121 | -121.9908
212.1562 | 121.875 | -61.084 | 60.6171 | 1.4211e-13 | -0.021276 | -0.00027784 | 0.064312 | -0.0087003 | 0.061789 | -0.23296 | -0.001002 | -0.00055336 | 0.062174 | 0.023897 | 0.060744 | -61.0014 | 0.005985 | -61.1285 | 60.5464 | 60.401 | 60.4467 | -61.1825 | -61.0835 | 0.023253 | -61.1501 | 60.3833 | 60.5199 | 60.3217 | -61.3921 | -0.098558 | -0.070699 | 0.082592 | -0.044471 | 0.054087 | -0.21611 | -0.17032 | -0.30811 | -0.23377 | 0.000463 | -0.066093 | 0.24201 | -0.097126 | -0.29538 | 121.6303 | 121.4849 | 121.5307 | 61.09 | -121.7996 | 121.4673 | 121.6039 | 121.4057 | 61.1072 | -122.0092
213.9062 | 121.8613 | -61.1526 | 60.5759 | 1.4211e-13 | -0.020848 | -0.00070504 | 0.064099 | -0.0082731 | 0.062003 | -0.23296 | -0.0012156 | -0.00055336 | 0.062387 | 0.023897 | 0.060957 | -61.0151 | 0.015142 | -61.1376 | 60.5372 | 60.4284 | 60.4513 | -61.1917 | -61.0973 | 0.018674 | -61.1638 | 60.3741 | 60.5108 | 60.3034 | -61.3967 | -0.039051 | -0.038657 | 0.13752 | 0.015038 | 0.054089 | -0.14744 | -0.12455 | -0.24402 | -0.20173 | 0.055392 | -0.011164 | 0.23286 | -0.065085 | -0.2725 | 121.6899 | 121.5811 | 121.604 | 61.1678 | -121.7676 | 121.5268 | 121.6634 | 121.456 | 61.1713 | -121.9725
215.5938 | 121.8155 | -61.1801 | 60.553 | 1.4211e-13 | -0.021062 | -0.00049144 | 0.064312 | -0.0084867 | 0.062003 | -0.22533 | -0.001002 | -0.00055336 | 0.062174 | 0.023897 | 0.06053 | -61.0243 | 0.010564 | -61.1513 | 60.5235 | 60.3689 | 60.4238 | -61.21 | -61.1064 | 0.018674 | -61.1867 | 60.3558 | 60.4879 | 60.2896 | -61.4196 | -0.029901 | -0.029504 | 0.15583 | 0.028769 | 0.05867 | -0.18408 | -0.12913 | -0.23945 | -0.19716 | 0.073701 | -0.006591 | 0.23286 | -0.06509 | -0.26335 | 121.7036 | 121.549 | 121.604 | 61.1907 | -121.763 | 121.5359 | 121.668 | 121.4697 | 61.1988 | -121.9725
217.3281 | 121.9391 | -61.1114 | 60.5392 | 1.4211e-13 | -0.020848 | -0.00049144 | 0.064312 | -0.0082731 | 0.061789 | -0.24059 | -0.0012156 | -0.00033976 | 0.062387 | 0.02347 | 0.06053 | -61.0426 | 0.010564 | -61.1697 | 60.5097 | 60.3781 | 60.4193 | -61.2238 | -61.1156 | 0.014095 | -61.1913 | 60.3467 | 60.4787 | 60.2805 | -61.4241 | -0.1123 | -0.029507 | 0.068852 | -0.058209 | 0.054093 | -0.16119 | -0.11998 | -0.31269 | -0.19258 | -0.004122 | -0.079835 | 0.23286 | -0.060515 | -0.25877 | 121.6212 | 121.4895 | 121.5307 | 61.122 | -121.763 | 121.4581 | 121.5902 | 121.3919 | 61.1255 | -121.9634
219 | 121.8567 | -61.203 | 60.5576 | 1.4211e-13 | -0.020635 | -0.00070504 | 0.064099 | -0.0082731 | 0.062003 | -0.24822 | -0.001002 | -0.00033976 | 0.062387 | 0.023897 | 0.060957 | -61.0518 | 0.010564 | -61.1742 | 60.5052 | 60.3826 | 60.4147 | -61.2283 | -61.1202 | 0.027831 | -61.1913 | 60.3421 | 60.4742 | 60.2759 | -61.4287 | -0.025328 | -0.052395 | 0.15125 | 0.028766 | 0.054094 | -0.17492 | -0.14287 | -0.22572 | -0.21547 | 0.082853 | 0.011718 | 0.23744 | -0.083403 | -0.28166 | 121.7082 | 121.5856 | 121.6177 | 61.2136 | -121.7859 | 121.5451 | 121.6772 | 121.4789 | 61.2308 | -121.9863
220.7344 | 121.9711 | -61.171 | 60.4477 | 1.4211e-13 | -0.021062 | -0.00070504 | 0.063885 | -0.0087003 | 0.061789 | -0.22533 | -0.001002 | -0.00076696 | 0.062387 | 0.023897 | 0.060744 | -61.0563 | 0.005985 | -61.1834 | 60.4914 | 60.3872 | 60.401 | -61.2283 | -61.1339 | 0.018674 | -61.2096 | 60.3329 | 60.4558 | 60.2576 | -61.4425 | -0.057372 | 0.043733 | 0.11463 | -0.012435 | 0.044937 | -0.060477 | -0.046739 | -0.2715 | -0.11477 | 0.037073 | -0.038641 | 0.23286 | 0.008145 | -0.19011 | 121.6624 | 121.5582 | 121.5719 | 61.1769 | -121.676 | 121.5039 | 121.6268 | 121.4285 | 61.1896 | -121.8902
222.4844 | 121.8613 | -61.2076 | 60.4523 | 1.4211e-13 | -0.021062 | -0.00049144 | 0.064099 | -0.0087003 | 0.062003 | -0.22533 | -0.00078837 | -0.00076696 | 0.062174 | 0.023897 | 0.060744 | -61.0609 | 0.005985 | -61.188 | 60.4823 | 60.3689 | 60.3964 | -61.2558 | -61.1476 | 0.009516 | -61.2188 | 60.31 | 60.4467 | 60.2484 | -61.4562 | -0.048224 | 0.029998 | 0.14667 | 0.019609 | 0.067833 | -0.083371 | -0.055896 | -0.24862 | -0.14224 | 0.059959 | -0.011176 | 0.23744 | -0.00559 | -0.20385 | 121.6899 | 121.5765 | 121.604 | 61.2136 | -121.7081 | 121.5176 | 121.6543 | 121.456 | 61.2171 | -121.9085
224.2188 | 121.8521 | -61.2579 | 60.4752 | 1.4211e-13 | -0.021062 | -0.00049144 | 0.064312 | -0.0084867 | 0.061789 | -0.23296 | -0.001002 | -0.00033976 | 0.062174 | 0.024111 | 0.060744 | -61.0838 | 0.005985 | -61.2017 | 60.464 | 60.3414 | 60.3826 | -61.2604 | -61.1705 | 0.014095 | -61.2325 | 60.3055 | 60.4329 | 60.2347 | -61.4699 | -0.002449 | -0.011203 | 0.17413 | 0.056228 | 0.058677 | -0.13373 | -0.09252 | -0.212 | -0.1697 | 0.087419 | 0.025442 | 0.23744 | -0.042214 | -0.24047 | 121.7219 | 121.5994 | 121.6406 | 61.2639 | -121.7355 | 121.5634 | 121.6909 | 121.4926 | 61.272 | -121.9451
225.9062 | 121.8658 | -61.5234 | 60.1685 | 1.4211e-13 | -0.020848 | -0.00027784 | 0.064312 | -0.0084867 | 0.062217 | -0.22533 | -0.0012156 | -0.00033976 | 0.06196 | 0.024325 | 0.06053 | -61.5828 | 0.005985 | -61.7099 | 59.9558 | 59.8194 | 59.8698 | -61.7686 | -61.6696 | 0.023253 | -61.727 | 59.7972 | 59.9247 | 59.7494 | -61.969 | -0.24521 | -0.2127 | -0.059411 | -0.18646 | 0.058748 | -0.34903 | -0.29862 | -0.44559 | -0.37121 | -0.14616 | -0.20356 | 0.24203 | -0.24374 | -0.4191 | 121.4792 | 121.3429 | 121.3933 | 61.5294 | -121.9371 | 121.3207 | 121.4482 | 121.2728 | 61.5467 | -122.1375
227.6562 | 121.8292 | -61.8896 | 59.8434 | 1.4211e-13 | -0.021062 | -0.00049144 | 0.063885 | -0.0084867 | 0.061789 | -0.22533 | -0.0012156 | -0.00033976 | 0.062387 | 0.023897 | 0.06053 | -61.6561 | -0.003172 | -61.7877 | 59.8825 | 59.7736 | 59.7874 | -61.8419 | -61.7474 | 0.004938 | -61.8094 | 59.7331 | 59.8515 | 59.6578 | -62.0514 | 0.047741 | 0.039055 | 0.23355 | 0.10192 | 0.05418 | -0.069805 | -0.056024 | -0.16179 | -0.1103 | 0.14222 | 0.080237 | 0.24203 | 0.008018 | -0.18566 | 121.7721 | 121.6633 | 121.6771 | 61.8865 | -121.6854 | 121.6228 | 121.7411 | 121.5474 | 61.8946 | -121.8949
229.4062 | 121.907 | -61.6608 | 60.0082 | 1.4211e-13 | -0.021062 | -0.00070504 | 0.064526 | -0.0087003 | 0.061789 | -0.22533 | -0.0012156 | -0.00055336 | 0.062387 | 0.023897 | 0.06053 | -61.56 | 0.001407 | -61.6824 | 59.9878 | 59.8698 | 59.8973 | -61.7458 | -61.6421 | 0.014095 | -61.7133 | 59.8247 | 59.9476 | 59.7722 | -61.9507 | -0.084983 | -0.020437 | 0.10081 | -0.02166 | 0.063323 | -0.13844 | -0.11093 | -0.28994 | -0.18353 | 0.018644 | -0.052491 | 0.23745 | -0.060627 | -0.23599 | 121.6486 | 121.5306 | 121.5581 | 61.6622 | -121.754 | 121.4855 | 121.6084 | 121.433 | 61.6749 | -121.9589
231.1406 | 121.9482 | -61.4365 | 60.2234 | 1.4211e-13 | -0.020848 | -0.00049144 | 0.064312 | -0.0089141 | 0.061789 | -0.21007 | -0.0012156 | -0.00055336 | 0.062387 | 0.023897 | 0.060957 | -61.3814 | 0.001407 | -61.5039 | 60.1664 | 60.0621 | 60.0713 | -61.5626 | -61.459 | 0.009516 | -61.5255 | 59.9987 | 60.1353 | 59.9508 | -61.7584 | -0.12613 | -0.057029 | 0.055063 | -0.067412 | 0.058719 | -0.16128 | -0.15209 | -0.32194 | -0.22469 | -0.022513 | -0.089069 | 0.23287 | -0.088053 | -0.27257 | 121.6028 | 121.4986 | 121.5078 | 61.4379 | -121.786 | 121.4352 | 121.5718 | 121.3873 | 61.446 | -121.9818
232.875 | 121.8338 | -61.9858 | 59.761 | 1.4211e-13 | -0.021062 | -0.00049144 | 0.06474 | -0.0087003 | 0.062003 | -0.23296 | -0.0014292 | -0.00012596 | 0.062601 | 0.024111 | 0.060316 | -61.8118 | -0.003172 | -61.9434 | 59.7268 | 59.5813 | 59.6409 | -62.0067 | -61.8985 | 0.014095 | -61.9651 | 59.5592 | 59.6958 | 59.493 | -62.2071 | -0.020969 | -0.034212 | 0.17401 | 0.04239 | 0.063359 | -0.17972 | -0.12014 | -0.22134 | -0.20189 | 0.087248 | 0.020692 | 0.24204 | -0.065257 | -0.26809 | 121.7126 | 121.5671 | 121.6267 | 61.9826 | -121.7678 | 121.5449 | 121.6816 | 121.4787 | 61.9999 | -121.9682
234.6094 | 121.8613 | -62.1872 | 59.5505 | 1.4211e-13 | -0.021276 | -0.00070504 | 0.064526 | -0.0084867 | 0.062003 | -0.23296 | -0.0012156 | -0.00055336 | 0.062387 | 0.023897 | 0.06053 | -61.9216 | -0.007751 | -62.0395 | 59.617 | 59.5126 | 59.5402 | -62.1166 | -62.0038 | 0.004938 | -62.075 | 59.4584 | 59.5859 | 59.3876 | -62.3216 | 0.070552 | 0.066478 | 0.26555 | 0.14766 | 0.077111 | -0.037835 | -0.0103 | -0.1344 | -0.092042 | 0.18335 | 0.11222 | 0.24662 | 0.035428 | -0.16283 | 121.8041 | 121.6998 | 121.7274 | 62.1794 | -121.6671 | 121.6456 | 121.7731 | 121.5748 | 62.1921 | -121.8721
236.3438 | 121.8796 | -64.6408 | 57.0786 | 1.4211e-13 | -0.021276 | -0.00027784 | 0.064312 | -0.0089141 | 0.062217 | -0.24059 | -0.0014292 | -0.00033976 | 0.062174 | 0.024111 | 0.060744 | -64.3894 | -0.007751 | -64.521 | 57.1172 | 56.9622 | 57.0494 | -64.5984 | -64.4718 | -0.00422 | -64.5429 | 56.9723 | 57.0906 | 56.8832 | -64.8125 | 0.042388 | 0.038602 | 0.25141 | 0.11985 | 0.07746 | -0.11637 | -0.029135 | -0.17166 | -0.10624 | 0.16904 | 0.097907 | 0.26957 | 0.012013 | -0.1954 | 121.758 | 121.603 | 121.6902 | 64.6331 | -121.677 | 121.6131 | 121.7314 | 121.524 | 64.6366 | -121.891
238.0156 | 121.9299 | -65.2771 | 56.3324 | 1.4211e-13 | -0.021276 | -0.00049144 | 0.064312 | -0.0084867 | 0.061789 | -0.22533 | -0.0012156 | -0.00055336 | 0.062387 | 0.024325 | 0.060744 | -64.9434 | -0.016908 | -65.0749 | 56.5677 | 56.399 | 56.4908 | -65.1479 | -65.0304 | -0.00422 | -65.0969 | 56.4183 | 56.5411 | 56.3337 | -65.3665 | 0.12921 | 0.23535 | 0.33372 | 0.20217 | 0.072959 | 0.066576 | 0.15843 | -0.089406 | 0.085916 | 0.24673 | 0.18018 | 0.26958 | 0.20874 | 0.001322 | 121.8448 | 121.6761 | 121.7679 | 65.2602 | -121.4803 | 121.6954 | 121.8182 | 121.6108 | 65.2729 | -121.6989
239.75 | 121.8887 | -65.0299 | 56.6666 | 1.4211e-13 | -0.021276 | -6.4044e-05 | 0.064099 | -0.0087003 | 0.061789 | -0.23296 | -0.0012156 | -0.00033976 | 0.062387 | 0.023897 | 0.060103 | -64.8106 | -0.016908 | -64.9422 | 56.6914 | 56.5592 | 56.6236 | -65.0243 | -64.9022 | -0.008798 | -64.9687 | 56.5419 | 56.6648 | 56.4665 | -65.2383 | 0.005647 | 0.024799 | 0.2193 | 0.087745 | 0.082098 | -0.10733 | -0.042958 | -0.20839 | -0.12463 | 0.12774 | 0.061186 | 0.26958 | -0.00181 | -0.20007 | 121.7213 | 121.5891 | 121.6535 | 65.013 | -121.6908 | 121.5718 | 121.6947 | 121.4964 | 65.0211 | -121.9049
241.4688 | 121.8887 | -65.6616 | 56.0211 | 1.4211e-13 | -0.021276 | -0.00049144 | 0.063885 | -0.0087003 | 0.061789 | -0.22533 | -0.0012156 | -0.00055336 | 0.062174 | 0.024111 | 0.060316 | -64.3802 | -0.044379 | -64.521 | 57.1263 | 57.0034 | 57.0448 | -64.603 | -64.4718 | -0.036271 | -64.5475 | 56.9677 | 57.0906 | 56.9518 | -64.8033 | 1.0586 | 1.1052 | 1.2814 | 1.1407 | 0.082039 | 0.98227 | 1.0237 | 0.85831 | 0.94661 | 1.1899 | 1.1141 | 0.25583 | 1.0694 | 0.93071 | 122.7879 | 122.665 | 122.7065 | 65.6172 | -120.6241 | 122.6294 | 122.7522 | 122.6135 | 65.6253 | -120.8244
243.1562 | 121.8979 | -65.0482 | 56.6071 | 1.4211e-13 | -0.020848 | -0.00070504 | 0.064312 | -0.0089141 | 0.062003 | -0.23296 | -0.0014292 | -0.00055336 | 0.062174 | 0.024325 | 0.06053 | -64.774 | -0.012329 | -64.9101 | 56.7326 | 56.573 | 56.6602 | -64.9968 | -64.8701 | 0.004938 | -64.9367 | 56.5831 | 56.7014 | 56.5031 | -65.2017 | 0.051432 | 0.12551 | 0.27423 | 0.1381 | 0.086672 | -0.034084 | 0.053179 | -0.15345 | -0.023917 | 0.1781 | 0.11155 | 0.265 | 0.094328 | -0.10393 | 121.7808 | 121.6212 | 121.7085 | 65.0359 | -121.6038 | 121.6314 | 121.7496 | 121.5513 | 65.0532 | -121.8087
244.8906 | 121.9666 | -64.801 | 56.8176 | 1.4211e-13 | -0.020848 | -0.00049144 | 0.063671 | -0.0084867 | 0.062003 | -0.22533 | -0.0012156 | -0.00055336 | 0.062387 | 0.024111 | 0.060957 | -64.4443 | -0.016908 | -64.5805 | 57.0668 | 56.9118 | 56.9945 | -64.6579 | -64.5313 | 0.000359 | -64.5978 | 56.9082 | 57.031 | 56.8236 | -64.8674 | 0.14308 | 0.24916 | 0.35668 | 0.22055 | 0.077468 | 0.094185 | 0.17685 | -0.06639 | 0.090585 | 0.26974 | 0.20318 | 0.26957 | 0.21342 | 0.006002 | 121.8678 | 121.7128 | 121.7955 | 64.7841 | -121.4756 | 121.7092 | 121.8321 | 121.6247 | 64.8014 | -121.685
246.5625 | 121.9116 | -65.5014 | 56.1401 | 1.4211e-13 | -0.021062 | -0.00070504 | 0.064099 | -0.0087003 | 0.062003 | -0.23296 | -0.00078837 | -0.00055336 | 0.062174 | 0.024325 | 0.060744 | -65.2456 | -0.016908 | -65.3908 | 56.261 | 56.1197 | 56.1886 | -65.4547 | -65.328 | -0.008798 | -65.4037 | 56.107 | 56.2252 | 56.0361 | -65.6687 | 0.046725 | 0.12086 | 0.25585 | 0.11057 | 0.063845 | -0.020479 | 0.048502 | -0.1673 | -0.033162 | 0.17342 | 0.097706 | 0.26501 | 0.085073 | -0.10403 | 121.7624 | 121.6211 | 121.69 | 65.4845 | -121.5948 | 121.6084 | 121.7266 | 121.5375 | 65.4926 | -121.8088
248.3125 | 121.9025 | -65.1581 | 56.5063 | 1.4211e-13 | -0.021276 | -0.00049144 | 0.064526 | -0.0087003 | 0.062003 | -0.23296 | -0.001002 | -0.00055336 | 0.062174 | 0.024111 | 0.060744 | -65.1082 | -0.003172 | -65.2581 | 56.3755 | 56.2387 | 56.3123 | -65.331 | -65.2044 | 0.004938 | -65.2618 | 56.2352 | 56.358 | 56.1643 | -65.5497 | -0.17297 | -0.13089 | 0.049875 | -0.099983 | 0.072984 | -0.26764 | -0.19409 | -0.39158 | -0.27117 | -0.046278 | -0.10368 | 0.2879 | -0.14836 | -0.34204 | 121.5335 | 121.3968 | 121.4703 | 65.1549 | -121.8374 | 121.3933 | 121.5161 | 121.3224 | 65.163 | -122.056
249.9844 | 121.9025 | -65.4144 | 56.282 | 1.4211e-13 | -0.021489 | -0.00070504 | 0.064099 | -0.0087003 | 0.061789 | -0.22533 | -0.0014292 | -0.00033976 | 0.062387 | 0.024325 | 0.06053 | -65.2135 | -0.003172 | -65.3496 | 56.2793 | 56.1471 | 56.2024 | -65.4272 | -65.3051 | -0.008798 | -65.3716 | 56.139 | 56.2527 | 56.0636 | -65.6504 | -0.012776 | -0.002734 | 0.20092 | 0.0648 | 0.077576 | -0.13491 | -0.079668 | -0.23596 | -0.14302 | 0.10934 | 0.042782 | 0.27875 | -0.029362 | -0.21846 | 121.6937 | 121.5616 | 121.6168 | 65.4113 | -121.7092 | 121.5535 | 121.6671 | 121.478 | 65.4056 | -121.9324
251.7188 | 121.9574 | -65.2496 | 56.3599 | 1.4211e-13 | -0.021276 | -0.00070504 | 0.063885 | -0.0087003 | 0.062003 | -0.23296 | -0.00078837 | -0.00033976 | 0.06196 | 0.024111 | 0.060744 | -64.9342 | -0.007751 | -65.0749 | 56.5632 | 56.4356 | 56.4862 | -65.1525 | -65.0212 | 0.004938 | -65.0832 | 56.4183 | 56.5366 | 56.3566 | -65.3573 | 0.097164 | 0.20331 | 0.31541 | 0.1747 | 0.077538 | 0.075741 | 0.12639 | -0.10771 | 0.05845 | 0.22842 | 0.16645 | 0.27416 | 0.17669 | -0.003251 | 121.8128 | 121.6852 | 121.7359 | 65.2419 | -121.5123 | 121.6679 | 121.7862 | 121.6062 | 65.2546 | -121.7172
253.3906 | 121.8887 | -65.062 | 56.5842 | 1.4211e-13 | -0.021489 | -0.00049144 | 0.064526 | -0.0087003 | 0.061789 | -0.23296 | -0.0014292 | -0.00055336 | 0.062601 | 0.024111 | 0.060957 | -64.8381 | -0.003172 | -64.9834 | 56.6547 | 56.5226 | 56.5778 | -65.0517 | -64.9296 | 0.000359 | -65.0054 | 56.5007 | 56.6281 | 56.4299 | -65.2703 | 0.010218 | 0.07057 | 0.22387 | 0.078584 | 0.068366 | -0.061563 | -0.006346 | -0.2084 | -0.083441 | 0.13231 | 0.056601 | 0.265 | 0.04396 | -0.1543 | 121.7167 | 121.5846 | 121.6398 | 65.0588 | -121.6359 | 121.5627 | 121.6901 | 121.4918 | 65.0623 | -121.8545
255.0625 | 121.9482 | -64.9658 | 56.6757 | 1.4211e-13 | -0.021489 | -0.00070504 | 0.064099 | -0.0087003 | 0.061576 | -0.22533 | -0.0014292 | -0.00055336 | 0.062387 | 0.023897 | 0.060744 | -64.9113 | -0.007751 | -65.0475 | 56.5723 | 56.4356 | 56.5046 | -65.1296 | -65.0075 | 0.004938 | -65.0649 | 56.4275 | 56.5549 | 56.3566 | -65.3482 | -0.16376 | -0.10339 | 0.054484 | -0.081643 | 0.082112 | -0.24012 | -0.17116 | -0.38237 | -0.24825 | -0.041655 | -0.099054 | 0.28332 | -0.12085 | -0.31911 | 121.5381 | 121.4014 | 121.4704 | 64.9581 | -121.8053 | 121.3933 | 121.5207 | 121.3224 | 64.9708 | -122.0239
256.7969 | 121.8292 | -65.0665 | 56.6299 | 1.4211e-13 | -0.021276 | -0.00070504 | 0.064312 | -0.0089141 | 0.061789 | -0.23296 | -0.001643 | -0.00055336 | 0.062174 | 0.024111 | 0.060316 | -64.7419 | -0.012329 | -64.8781 | 56.7463 | 56.6096 | 56.6786 | -64.9556 | -64.8381 | -0.00422 | -64.9 | 56.5969 | 56.7243 | 56.526 | -65.1696 | 0.11095 | 0.11636 | 0.32459 | 0.18846 | 0.07751 | -0.020341 | 0.048606 | -0.10309 | -0.03307 | 0.22846 | 0.16649 | 0.26958 | 0.094333 | -0.10392 | 121.8128 | 121.6761 | 121.7451 | 65.0542 | -121.5855 | 121.6634 | 121.7908 | 121.5925 | 65.0623 | -121.7996
258.5312 | 121.7972 | -64.1693 | 57.5134 | 1.4211e-13 | -0.021489 | -0.00091884 | 0.064099 | -0.0089141 | 0.061789 | -0.23296 | -0.0014292 | -0.00076696 | 0.062174 | 0.024111 | 0.060744 | -64.0506 | -0.007751 | -64.1867 | 57.4468 | 57.2964 | 57.3699 | -64.255 | -64.1467 | 0.014095 | -64.2041 | 57.302 | 57.4202 | 57.2265 | -64.4691 | -0.085688 | -0.06663 | 0.11871 | -0.017434 | 0.068254 | -0.21699 | -0.14351 | -0.29975 | -0.21147 | 0.022635 | -0.034764 | 0.26498 | -0.093203 | -0.28688 | 121.6161 | 121.4658 | 121.5392 | 64.1616 | -121.7684 | 121.4713 | 121.5895 | 121.3959 | 64.1834 | -121.9825
260.2656 | 121.907 | -63.8855 | 57.7606 | 1.4211e-13 | -0.021062 | -0.00091884 | 0.064526 | -0.0089141 | 0.061789 | -0.23296 | -0.0014292 | -0.00076696 | 0.062387 | 0.024752 | 0.060957 | -63.6614 | 0.005985 | -63.793 | 57.8497 | 57.6857 | 57.7637 | -63.8612 | -63.7438 | 0.009516 | -63.8195 | 57.682 | 57.814 | 57.6157 | -64.0844 | 0.024285 | 0.089076 | 0.22406 | 0.092484 | 0.068199 | -0.07497 | 0.003059 | -0.19894 | -0.078643 | 0.14175 | 0.066033 | 0.26497 | 0.053365 | -0.14489 | 121.7352 | 121.5711 | 121.6492 | 63.8915 | -121.6218 | 121.5675 | 121.6995 | 121.5012 | 63.895 | -121.8451
262 | 121.4676 | -28.775 | 93.0588 | 1.4211e-13 | -0.021276 | -0.00049144 | 0.064526 | 0.0088201 | 0.061148 | -0.23296 | -0.00078837 | -0.00012596 | 0.062387 | 0.024111 | 0.060316 | -29.232 | 0.19371 | -6.2257 | 92.5356 | 92.4168 | 92.3138 | -29.153 | -29.2478 | 0.18351 | -29.3372 | 92.2359 | 92.4603 | 92.2529 | -29.2351 | -0.37794 | -0.52322 | -0.45694 | 22.5493 | 22.9273 | -0.64198 | -0.74496 | -0.46004 | -0.8229 | -0.47273 | -0.56218 | -0.10214 | -0.59851 | -0.80592 | 121.3106 | 121.1918 | 121.0888 | 28.9687 | -122.2117 | 121.0109 | 121.2353 | 121.0279 | 28.9585 | -122.2938
263.7344 | 121.9528 | -63.5651 | 57.962 | 1.4211e-13 | -0.021276 | -0.00070504 | 0.063671 | -0.0084867 | 0.061789 | -0.23296 | -0.0014292 | -0.00033976 | 0.062174 | 0.024538 | 0.060957 | -62.6725 | 0.010564 | -62.6988 | 58.8295 | 58.8075 | 58.8213 | -62.95 | -62.7593 | 0.004938 | -62.8305 | 58.6892 | 58.8121 | 58.8428 | -63.0817 | 0.61506 | 0.86744 | 0.89256 | 0.86626 | 0.2512 | 0.84545 | 0.8593 | 0.48339 | 0.72721 | 0.80574 | 0.7346 | 0.25121 | 0.85008 | 0.88076 | 122.3945 | 122.3726 | 122.3864 | 63.5756 | -120.912 | 122.2543 | 122.3772 | 122.4079 | 63.57 | -121.0437
265.4062 | 122.0261 | -47.9462 | 73.732 | 1.4211e-13 | -0.020848 | -0.00027784 | 0.064312 | -0.0012221 | 0.061789 | -0.24059 | -0.001002 | -0.00055336 | 0.062387 | 0.024538 | 0.060744 | -48.0125 | 0.10214 | -38.3011 | 73.6314 | 73.5425 | 73.482 | -47.5923 | -48.0479 | 0.10109 | -48.1053 | 73.4641 | 73.5918 | 73.4852 | -48.2143 | 0.35387 | -0.1006 | -0.066339 | 9.645 | 9.2911 | -0.18953 | -0.24997 | -0.26809 | -0.26794 | -0.10177 | -0.15916 | 0.10892 | -0.14015 | -0.24683 | 121.5776 | 121.4886 | 121.4282 | 48.0483 | -121.3243 | 121.4102 | 121.538 | 121.4313 | 48.0473 | -121.9463
267.1406 | 121.7148 | -27.4521 | 94.3542 | 1.4211e-13 | -0.021489 | -0.00049144 | 0.064526 | 0.0094611 | 0.061362 | -0.22533 | -0.00078837 | -0.00033976 | 0.062174 | 0.024538 | 0.060316 | -27.4555 | 0.13419 | -3.7122 | 94.3898 | 94.2438 | 94.2002 | -27.3901 | -27.4849 | 0.12398 | -27.5744 | 94.0673 | 94.3192 | 93.8828 | -27.4631 | 0.062008 | 0.035562 | -0.003457 | 23.7398 | 23.6778 | -0.11046 | -0.15405 | -0.01097 | -0.28697 | -0.032861 | -0.12231 | -0.11134 | -0.035065 | -0.47141 | 121.8419 | 121.6959 | 121.6523 | 27.5863 | -121.7443 | 121.5194 | 121.7713 | 121.3349 | 27.5761 | -121.8173
268.8906 | 121.7926 | -27.0813 | 94.6838 | 1.4211e-13 | -0.021276 | -0.00027784 | 0.064099 | 0.0092473 | 0.061148 | -0.23296 | -0.001002 | 8.7636e-05 | 0.062387 | 0.024325 | 0.060103 | -27.1671 | 0.11129 | -3.3322 | 94.6508 | 94.5048 | 94.4429 | -27.1382 | -27.2056 | 0.11483 | -27.3409 | 94.3237 | 94.5664 | 94.24 | -27.2204 | -0.056939 | -0.03306 | -0.085807 | 23.7491 | 23.806 | -0.17905 | -0.24097 | -0.13908 | -0.36016 | -0.12435 | -0.25958 | -0.1205 | -0.11741 | -0.44387 | 121.7321 | 121.5861 | 121.5242 | 27.1926 | -121.8221 | 121.405 | 121.6477 | 121.3213 | 27.1961 | -121.9042
270.5781 | 121.8933 | -26.6647 | 95.0226 | 1.4211e-13 | -0.021062 | -0.00027784 | 0.064099 | 0.0092473 | 0.061362 | -0.2177 | -0.0012156 | -0.00012596 | 0.062387 | 0.024752 | 0.06053 | -26.6085 | 0.097557 | -2.8698 | 95.1956 | 95.0497 | 94.9969 | -26.5842 | -26.6516 | 0.10567 | -26.7823 | 94.8731 | 95.1204 | 94.7848 | -26.6663 | 0.080546 | 0.17302 | 0.056191 | 23.7949 | 23.7144 | 0.027092 | -0.025709 | -0.001609 | -0.14949 | 0.013112 | -0.11755 | -0.11594 | 0.097855 | -0.23776 | 121.8603 | 121.7144 | 121.6616 | 26.7623 | -121.6068 | 121.5378 | 121.7852 | 121.4496 | 26.7704 | -121.6889
272.3125 | 121.7697 | -26.564 | 95.2148 | 1.4211e-13 | -0.021276 | -0.00027784 | 0.064312 | 0.0094611 | 0.061576 | -0.23296 | -0.0012156 | -0.00012596 | 0.062174 | 0.024538 | 0.060103 | -26.5857 | 0.10214 | -2.6775 | 95.2231 | 95.0863 | 95.0198 | -26.5567 | -26.6242 | 0.10109 | -26.7594 | 94.9006 | 95.1616 | 94.8031 | -26.6434 | 0.007311 | 0.008232 | -0.021625 | 23.8865 | 23.8792 | -0.12854 | -0.19508 | -0.079423 | -0.31428 | -0.060124 | -0.19536 | -0.11594 | -0.053199 | -0.41171 | 121.7871 | 121.6503 | 121.5838 | 26.6662 | -121.7716 | 121.4646 | 121.7257 | 121.3672 | 26.6651 | -121.8583
274.0469 | 121.8658 | -26.619 | 95.1187 | 1.4211e-13 | -0.021489 | -0.00027784 | 0.064526 | 0.0094611 | 0.061148 | -0.23296 | -0.0012156 | -0.00033976 | 0.062601 | 0.024538 | 0.060316 | -26.7322 | 0.10214 | -2.8195 | 95.0766 | 94.9444 | 94.8687 | -26.7078 | -26.7752 | 0.10109 | -26.9013 | 94.7495 | 95.006 | 94.7619 | -26.7991 | -0.088861 | -0.042145 | -0.1132 | 23.7995 | 23.8883 | -0.17435 | -0.25004 | -0.18017 | -0.36924 | -0.15629 | -0.28237 | -0.1022 | -0.11274 | -0.35678 | 121.6955 | 121.5633 | 121.4876 | 26.7211 | -121.8265 | 121.3684 | 121.6249 | 121.3809 | 26.72 | -121.9178
275.7812 | 121.8246 | -26.683 | 95.0455 | 1.4211e-13 | -0.021062 | -0.00027784 | 0.064312 | 0.0094611 | 0.061362 | -0.23296 | -0.0012156 | -0.00012596 | 0.062387 | 0.024325 | 0.06053 | -26.6589 | 0.092979 | -2.3937 | 95.1452 | 95.0039 | 94.9557 | -26.6391 | -26.6974 | 0.096512 | -26.8326 | 94.8273 | 95.0838 | 94.7986 | -26.7167 | 0.043909 | 0.099773 | 0.024139 | 24.2893 | 24.2454 | -0.041586 | -0.089804 | -0.033666 | -0.21816 | -0.014366 | -0.1496 | -0.11594 | 0.038338 | -0.24691 | 121.8283 | 121.6869 | 121.6387 | 26.776 | -121.6846 | 121.5104 | 121.7669 | 121.4816 | 26.7796 | -121.7622
277.4531 | 121.8109 | -26.5091 | 95.2286 | 1.4211e-13 | -0.021276 | -0.00027784 | 0.064526 | 0.0094611 | 0.061362 | -0.23296 | -0.001002 | -0.00033976 | 0.062387 | 0.024538 | 0.060103 | -26.5261 | 0.0884 | -2.3342 | 95.2826 | 95.1458 | 95.0793 | -26.4972 | -26.56 | 0.096512 | -26.6953 | 94.9647 | 95.2257 | 94.62 | -26.5793 | 0.011905 | 0.054018 | -0.017038 | 24.1749 | 24.163 | -0.082745 | -0.14929 | -0.070251 | -0.26391 | -0.050954 | -0.18619 | -0.11594 | -0.002831 | -0.60858 | 121.7917 | 121.6549 | 121.5884 | 26.5975 | -121.7258 | 121.4738 | 121.7348 | 121.1291 | 26.6056 | -121.8079
279.125 | 121.907 | -26.6876 | 94.9768 | 1.4211e-13 | -0.021062 | -6.4044e-05 | 0.064099 | 0.0096747 | 0.061362 | -0.23296 | -0.001002 | -0.00055336 | 0.062815 | 0.024538 | 0.060103 | -26.7367 | 0.097557 | -2.3296 | 95.0674 | 94.926 | 94.8778 | -26.7078 | -26.7752 | 0.087354 | -26.9013 | 94.7495 | 95.006 | 94.7116 | -26.7946 | -0.020197 | 0.090604 | -0.049116 | 24.358 | 24.3782 | -0.050763 | -0.098976 | -0.10693 | -0.22733 | -0.087626 | -0.2137 | -0.10678 | 0.029166 | -0.26524 | 121.755 | 121.6137 | 121.5655 | 26.7852 | -121.6846 | 121.4371 | 121.6936 | 121.3992 | 26.775 | -121.7714
280.8594 | 121.8704 | -27.1912 | 94.4962 | 1.4211e-13 | -0.021276 | -0.00027784 | 0.064312 | 0.0094611 | 0.061362 | -0.22533 | -0.001002 | -0.00012596 | 0.062601 | 0.024538 | 0.059889 | -26.7138 | 0.092979 | -2.4532 | 95.0949 | 94.9535 | 94.9053 | -26.6987 | -26.7478 | 0.091933 | -26.8876 | 94.7724 | 95.0243 | 94.6566 | -26.7762 | 0.4925 | 0.59873 | 0.47732 | 24.738 | 24.2455 | 0.45736 | 0.40915 | 0.41493 | 0.27621 | 0.44339 | 0.30357 | -0.11136 | 0.52813 | 0.16047 | 122.286 | 122.1447 | 122.0965 | 27.2841 | -121.1948 | 121.9635 | 122.2154 | 121.8478 | 27.2831 | -121.2724
282.5938 | 121.8109 | -26.8341 | 94.9356 | 1.4211e-13 | -0.021489 | -0.00027784 | 0.064526 | 0.0098883 | 0.061362 | -0.23296 | -0.00078837 | -0.00012596 | 0.062601 | 0.024538 | 0.060103 | -26.9061 | 0.11129 | -2.3616 | 94.9438 | 94.7978 | 94.7496 | -26.8543 | -26.9401 | 0.11025 | -27.0295 | 94.6167 | 94.8732 | 94.5834 | -26.9777 | -0.020239 | 0.008186 | -0.072032 | 24.4725 | 24.4927 | -0.13777 | -0.18598 | -0.1436 | -0.31891 | -0.10598 | -0.19543 | -0.051829 | -0.062415 | -0.35224 | 121.7779 | 121.6319 | 121.5837 | 26.9454 | -121.79 | 121.4508 | 121.7073 | 121.4175 | 26.9444 | -121.9133
284.3281 | 121.7651 | -26.9348 | 94.7983 | 1.4211e-13 | -0.021489 | -6.4044e-05 | 0.064526 | 0.0094611 | 0.061148 | -0.22533 | -0.00078837 | -0.00012596 | 0.062601 | 0.024325 | 0.06053 | -26.984 | 0.0884 | -2.6913 | 94.8248 | 94.6834 | 94.626 | -26.9642 | -27.0271 | 0.082776 | -27.1532 | 94.5022 | 94.745 | 94.6063 | -27.1105 | -0.029425 | 0.026477 | -0.049157 | 24.2435 | 24.273 | -0.11492 | -0.17227 | -0.17567 | -0.29604 | -0.092263 | -0.21834 | -0.042668 | -0.053286 | -0.19202 | 121.7596 | 121.6182 | 121.5608 | 27.0232 | -121.7625 | 121.437 | 121.6798 | 121.5411 | 27.0176 | -121.9088
286.0625 | 121.7926 | -26.8295 | 94.9722 | 1.4211e-13 | -0.021276 | 0.00014956 | 0.064526 | 0.0096747 | 0.061362 | -0.24059 | -0.001002 | -0.00012596 | 0.062815 | 0.024325 | 0.060316 | -26.9382 | 0.11587 | -2.5494 | 94.9117 | 94.7704 | 94.7267 | -26.8681 | -26.9721 | 0.10109 | -27.0616 | 94.6487 | 94.8457 | 94.4826 | -27.0235 | -0.038553 | -0.060483 | -0.10866 | 24.2802 | 24.3187 | -0.20187 | -0.24549 | -0.19396 | -0.32348 | -0.1426 | -0.23205 | -0.038092 | -0.12651 | -0.48959 | 121.7413 | 121.5999 | 121.5563 | 26.9454 | -121.8403 | 121.4783 | 121.6753 | 121.3122 | 26.9306 | -121.9957
287.7969 | 121.7514 | -26.6098 | 95.1462 | 1.4211e-13 | -0.021489 | -6.4044e-05 | 0.064526 | 0.0098883 | 0.061148 | -0.22533 | -0.00078837 | -0.00033976 | 0.062387 | 0.024325 | 0.060103 | -26.6589 | 0.097557 | -2.2106 | 95.1452 | 95.0039 | 94.9465 | -26.63 | -26.6974 | 0.091933 | -26.8189 | 94.8914 | 95.0792 | 94.6795 | -26.7854 | -0.020175 | -0.000935 | -0.049103 | 24.3992 | 24.4194 | -0.14229 | -0.19967 | -0.17559 | -0.25477 | -0.087608 | -0.20911 | -0.033518 | -0.066948 | -0.46666 | 121.755 | 121.6137 | 121.5563 | 26.7074 | -121.7762 | 121.5012 | 121.689 | 121.2893 | 26.7017 | -121.9316
289.5312 | 121.7606 | -26.7105 | 95.0821 | 1.4211e-13 | -0.021489 | 0.00014956 | 0.064312 | 0.0094611 | 0.061576 | -0.24059 | -0.0012156 | 8.7636e-05 | 0.062601 | 0.024538 | 0.060316 | -26.7047 | 0.0884 | -2.206 | 95.0995 | 94.9581 | 94.9053 | -26.6758 | -26.7524 | 0.091933 | -26.8784 | 94.841 | 95.0289 | 94.6429 | -26.8266 | 0.034743 | 0.017368 | 0.005821 | 24.5045 | 24.4698 | -0.124 | -0.17679 | -0.11609 | -0.24105 | -0.041844 | -0.16792 | -0.051832 | -0.053226 | -0.43921 | 121.81 | 121.6686 | 121.6158 | 26.7989 | -121.7579 | 121.5516 | 121.7394 | 121.3534 | 26.8024 | -121.9087
291.2031 | 121.8063 | -26.6602 | 95.0638 | 1.4211e-13 | -0.021703 | -0.00027784 | 0.064526 | 0.0094611 | 0.061362 | -0.23296 | -0.001002 | -0.00033976 | 0.062601 | 0.024966 | 0.060316 | -26.7551 | 0.097557 | -2.1282 | 95.0445 | 94.894 | 94.8504 | -26.7353 | -26.7844 | 0.10109 | -26.9196 | 94.7861 | 94.9785 | 94.6612 | -26.877 | -0.075137 | -0.019263 | -0.094895 | 24.532 | 24.6071 | -0.16979 | -0.21342 | -0.21681 | -0.27768 | -0.12425 | -0.25949 | -0.042674 | -0.085281 | -0.40258 | 121.7047 | 121.5541 | 121.5105 | 26.7577 | -121.7991 | 121.4463 | 121.6387 | 121.3214 | 26.7612 | -121.9408
292.9375 | 121.8842 | -26.4038 | 95.3064 | 1.4211e-13 | -0.021917 | -0.00027784 | 0.064312 | 0.0096747 | 0.061576 | -0.24059 | -0.001002 | -0.00012596 | 0.062387 | 0.024538 | 0.060316 | -26.6772 | 0.11129 | -2.0183 | 95.1178 | 94.981 | 94.9236 | -26.6575 | -26.7111 | 0.1194 | -26.8464 | 94.8639 | 95.0563 | 94.7802 | -26.7946 | -0.25364 | -0.18862 | -0.27341 | 24.3855 | 24.6392 | -0.32541 | -0.38278 | -0.39074 | -0.44246 | -0.30734 | -0.44257 | -0.051832 | -0.25006 | -0.52615 | 121.5216 | 121.3848 | 121.3274 | 26.5151 | -121.9638 | 121.2677 | 121.4601 | 121.1841 | 26.5232 | -122.1009
294.6094 | 121.8979 | -21.373 | 100.2914 | 1.4211e-13 | -0.021703 | -0.00027784 | 0.064312 | 0.0060423 | 0.061148 | -0.23296 | -0.001002 | -0.00033976 | 0.062174 | 0.024966 | 0.060316 | -21.5952 | 0.11587 | -1.7207 | 100.2089 | 100.0499 | 99.983 | -21.5794 | -21.6379 | 0.11483 | -21.7732 | 99.9323 | 100.134 | 99.7114 | -21.7212 | -0.20644 | -0.082502 | -0.22222 | 19.6523 | 19.8587 | -0.24158 | -0.30847 | -0.34823 | -0.35911 | -0.26495 | -0.40019 | -0.051952 | -0.15744 | -0.58004 | 121.5819 | 121.4228 | 121.356 | 21.4889 | -121.8709 | 121.3053 | 121.507 | 121.0844 | 21.4878 | -122.0127
296.3438 | 121.8842 | -20.9381 | 100.7492 | 1.4211e-13 | -0.021489 | 0.00014956 | 0.064526 | 0.0056151 | 0.061148 | -0.23296 | -0.001002 | -0.00012596 | 0.062174 | 0.024538 | 0.060103 | -21.1145 | 0.10671 | -1.6841 | 100.6942 | 100.5444 | 100.4775 | -21.0941 | -21.1434 | 0.11025 | -21.297 | 100.4268 | 100.6239 | 100.3753 | -21.2313 | -0.15595 | -0.054957 | -0.17637 | 19.2541 | 19.41 | -0.20482 | -0.27174 | -0.29318 | -0.3224 | -0.20532 | -0.35888 | -0.065699 | -0.12529 | -0.37391 | 121.6324 | 121.4825 | 121.4156 | 21.0448 | -121.8433 | 121.3649 | 121.562 | 121.3134 | 21.0484 | -121.9805
298.0156 | 89.4928 | -0.15106 | 69.1818 | 1.4211e-13 | -0.021489 | 0.0035684 | 0.064099 | 0.0079653 | 0.061576 | -0.23296 | -0.00078837 | -0.00012596 | 0.062387 | 0.024538 | 0.060103 | -22.1492 | 0.2166 | -0.70889 | 99.6641 | 99.5782 | 99.3969 | -22.1335 | -22.1416 | 0.22929 | -22.2677 | 99.3783 | 99.5251 | 99.6839 | -22.1883 | -21.9824 | 30.4823 | -21.9981 | -0.55782 | 21.4246 | 30.3964 | 30.2151 | -22.0372 | 30.1965 | -21.9905 | -22.1166 | -0.079414 | 30.3432 | 30.5021 | 99.8152 | 99.7293 | 99.548 | 0.36766 | -91.3153 | 99.5294 | 99.6761 | 99.835 | 0.38036 | -91.3701
299.7656 | 121.9162 | -20.2515 | 97.9935 | 1.4211e-13 | -0.021917 | 0.001859 | 0.064312 | 0.0060423 | 0.061148 | -0.23296 | -0.001002 | 8.7636e-05 | 0.062601 | 0.024752 | 0.060103 | -20.2446 | 0.15708 | -0.79129 | 101.6145 | 101.5197 | 101.4481 | -20.192 | -20.2689 | 0.17435 | -20.3812 | 101.3196 | 101.5305 | 101.5474 | -20.2606 | 0.059455 | 3.621 | 0.006881 | 19.4602 | 19.4007 | 3.5262 | 3.4547 | -0.009112 | 3.3261 | -0.017436 | -0.12978 | -0.12067 | 3.537 | 3.554 | 121.866 | 121.7712 | 121.6996 | 20.4085 | -118.1855 | 121.5711 | 121.7819 | 121.7989 | 20.4258 | -118.254
301.5 | 121.9711 | -118.2312 | 3.3875 | 1.4211e-13 | -0.022771 | 0.0025 | 0.063244 | 0.078688 | 0.062644 | -0.23296 | -0.0018566 | -0.001408 | 0.061746 | 0.024966 | 0.062239 | -117.6132 | -0.22295 | -1.8809 | 3.5225 | 3.4941 | 3.6446 | -118.2955 | -117.8778 | -0.224 | -117.9123 | 3.4497 | 3.5163 | 3.5195 | -118.5174 | -0.064267 | 0.1351 | 0.61804 | 116.3503 | 116.4145 | 0.10663 | 0.25715 | -0.28621 | 0.062251 | 0.35336 | 0.31886 | 0.60507 | 0.12889 | 0.13209 | 121.7537 | 121.7253 | 121.8758 | 118.0083 | -121.6829 | 121.6809 | 121.7475 | 121.7507 | 118.0072 | -121.9049
303.2344 | 121.9116 | -119.6594 | 1.9913 | 1.4211e-13 | -0.022344 | 0.10229 | 0.063458 | 0.07997 | 0.062217 | -0.23296 | -0.0018566 | -0.00098076 | 0.061746 | 0.024966 | 0.062453 | -119.0462 | -0.18632 | -1.739 | 2.0712 | 2.038 | 2.1886 | -119.747 | -119.3156 | -0.16905 | -119.3592 | 2.0075 | 2.0741 | 2.0819 | -119.9689 | -0.087563 | 0.079925 | 0.61323 | 117.9204 | 118.008 | 0.046708 | 0.19733 | -0.30948 | 0.016204 | 0.34387 | 0.30021 | 0.60969 | 0.082806 | 0.090586 | 121.7306 | 121.6974 | 121.848 | 119.4731 | -121.7383 | 121.6669 | 121.7335 | 121.7413 | 119.4904 | -121.9602
304.9688 | 121.9116 | -119.6777 | 2.0279 | 1.4211e-13 | -0.022558 | 0.1243 | 0.063458 | 0.079756 | 0.061789 | -0.23296 | -0.001643 | -0.00098076 | 0.061533 | 0.025179 | 0.061385 | -119.0828 | -0.17716 | -1.652 | 1.9705 | 1.9785 | 2.1291 | -119.7928 | -119.3522 | -0.14158 | -119.3958 | 1.9525 | 2.0237 | 2.0406 | -120.0193 | -0.11504 | -0.057421 | 0.59491 | 118.0257 | 118.1408 | -0.049439 | 0.10119 | -0.34153 | -0.075359 | 0.32555 | 0.28189 | 0.62342 | -0.00418 | 0.012757 | 121.6482 | 121.6562 | 121.8068 | 119.5006 | -121.8207 | 121.6303 | 121.7014 | 121.7184 | 119.5362 | -122.0472
306.6406 | 121.8109 | -119.7372 | 1.9958 | 1.4211e-13 | -0.022344 | 0.077928 | 0.063244 | 0.079542 | 0.061789 | -0.23296 | -0.001643 | -0.0011944 | 0.061533 | 0.025179 | 0.060957 | -119.0141 | -0.18632 | -1.652 | 2.0391 | 2.0655 | 2.2115 | -119.7104 | -119.2881 | -0.12784 | -119.3317 | 2.0258 | 2.0924 | 2.1002 | -119.9414 | 0.026888 | 0.043298 | 0.7231 | 118.0852 | 118.0583 | 0.069604 | 0.21564 | -0.20418 | 0.02994 | 0.44916 | 0.4055 | 0.60968 | 0.096542 | 0.10432 | 121.7764 | 121.8027 | 121.9487 | 119.5509 | -121.7062 | 121.763 | 121.8296 | 121.8374 | 119.6094 | -121.9373
308.375 | 121.8063 | -119.7693 | 1.9409 | 1.4211e-13 | -0.02213 | 0.11404 | 0.063244 | 0.079542 | 0.061789 | -0.23296 | -0.0014292 | -0.00076696 | 0.061533 | 0.025607 | 0.061171 | -119.1698 | -0.17716 | -1.5925 | 1.8743 | 1.9006 | 2.0375 | -119.866 | -119.4346 | -0.10953 | -119.4783 | 1.861 | 1.9321 | 1.9445 | -120.1017 | -0.096752 | -0.066592 | 0.59948 | 118.1768 | 118.2735 | -0.040305 | 0.096589 | -0.3324 | -0.079954 | 0.33469 | 0.29103 | 0.62342 | -0.008777 | 0.003582 | 121.6436 | 121.6699 | 121.8068 | 119.5921 | -121.807 | 121.6303 | 121.7014 | 121.7138 | 119.6598 | -122.0426
310.0469 | 121.8796 | -119.8242 | 1.8539 | 1.4211e-13 | -0.022344 | 0.10934 | 0.063458 | 0.079542 | 0.062003 | -0.22533 | -0.001643 | -0.00076696 | 0.061319 | 0.025179 | 0.061598 | -119.2019 | -0.18632 | -1.5513 | 1.8377 | 1.864 | 2.0009 | -119.8248 | -119.4712 | -0.11411 | -119.524 | 1.8243 | 1.8909 | 1.6881 | -120.1429 | -0.00061 | -0.016244 | 0.62236 | 118.2729 | 118.2735 | 0.010038 | 0.14694 | -0.31868 | -0.029607 | 0.35299 | 0.30017 | 0.61885 | 0.036991 | -0.16584 | 121.6619 | 121.6882 | 121.8251 | 119.6379 | -121.6788 | 121.6486 | 121.7152 | 121.5123 | 119.7101 | -121.9968
311.7812 | 121.8704 | -119.8608 | 1.8173 | 1.4211e-13 | -0.022558 | 0.12878 | 0.063244 | 0.079756 | 0.062217 | -0.23296 | -0.0014292 | -0.00076696 | 0.061319 | 0.025393 | 0.061171 | -119.2751 | -0.18632 | -1.5513 | 1.7507 | 1.6442 | 1.923 | -119.8981 | -119.5491 | -0.10495 | -119.6019 | 1.7419 | 1.8177 | 1.624 | -120.2162 | -0.037251 | -0.066612 | 0.58573 | 118.3096 | 118.3468 | -0.17313 | 0.10572 | -0.35532 | -0.075399 | 0.31177 | 0.25895 | 0.61427 | 0.000354 | -0.19333 | 121.6115 | 121.505 | 121.7839 | 119.6745 | -121.7154 | 121.6028 | 121.6785 | 121.4848 | 119.7559 | -122.0335
313.5156 | 121.7651 | -119.7556 | 1.9913 | 1.4211e-13 | -0.022558 | 0.12857 | 0.06303 | 0.079115 | 0.062217 | -0.22533 | -0.001643 | -0.00055336 | 0.061533 | 0.024966 | 0.061385 | -119.1332 | -0.1909 | -1.7482 | 1.8881 | 1.7404 | 2.0558 | -119.747 | -119.4117 | -0.10495 | -119.4416 | 1.8839 | 1.9459 | 1.7614 | -120.0742 | 0.008567 | -0.10321 | 0.62237 | 118.0074 | 117.9988 | -0.25092 | 0.06455 | -0.31866 | -0.10742 | 0.34385 | 0.31392 | 0.63258 | -0.045395 | -0.22992 | 121.6436 | 121.4959 | 121.8114 | 119.5647 | -121.7383 | 121.6394 | 121.7014 | 121.5169 | 119.6506 | -122.0655
315.2031 | 121.843 | -119.3893 | 2.2659 | 1.4211e-13 | -0.022344 | 0.15849 | 0.063244 | 0.078901 | 0.06243 | -0.22533 | -0.0018566 | -0.00098076 | 0.061746 | 0.024966 | 0.061385 | -118.8356 | -0.1909 | -1.5284 | 2.1811 | 2.0334 | 2.3397 | -119.4631 | -119.1049 | -0.095794 | -119.1578 | 2.1769 | 2.2435 | 2.0452 | -119.7766 | -0.073751 | -0.084852 | 0.55375 | 117.8609 | 117.9347 | -0.23253 | 0.073765 | -0.38725 | -0.08905 | 0.28441 | 0.23159 | 0.61884 | -0.022444 | -0.2207 | 121.5704 | 121.4227 | 121.729 | 119.1984 | -121.729 | 121.5662 | 121.6328 | 121.4346 | 119.2935 | -122.0425
316.9531 | 121.756 | -119.1834 | 2.5406 | 1.4211e-13 | -0.022558 | 0.16468 | 0.063458 | 0.078474 | 0.062217 | -0.22533 | -0.001643 | -0.00076696 | 0.061746 | 0.025179 | 0.061171 | -118.5792 | -0.18174 | -2.0503 | 2.4329 | 2.2852 | 2.5869 | -119.1929 | -118.8577 | -0.095794 | -118.8876 | 2.4287 | 2.4953 | 2.2971 | -119.5156 | -0.009587 | -0.1077 | 0.60415 | 117.133 | 117.1426 | -0.25535 | 0.046352 | -0.33225 | -0.11189 | 0.32567 | 0.29574 | 0.62799 | -0.045279 | -0.24354 | 121.6162 | 121.4686 | 121.7703 | 119.0016 | -121.7335 | 121.612 | 121.6787 | 121.4804 | 119.0876 | -122.0562
318.625 | 121.7468 | -118.8766 | 2.8381 | 1.4211e-13 | -0.022771 | 0.10592 | 0.063244 | 0.078047 | 0.06243 | -0.22533 | -0.0018566 | -0.00098076 | 0.061319 | 0.025607 | 0.061171 | -118.4418 | -0.1909 | -1.6886 | 2.5657 | 2.4272 | 2.7335 | -119.0601 | -118.7203 | -0.086637 | -118.764 | 2.5569 | 2.6235 | 2.4298 | -119.3828 | -0.1835 | -0.27247 | 0.4348 | 117.188 | 117.3715 | -0.41095 | -0.10468 | -0.50616 | -0.28124 | 0.15633 | 0.11267 | 0.61883 | -0.21462 | -0.4083 | 121.4423 | 121.3038 | 121.6101 | 118.6858 | -121.8983 | 121.4335 | 121.5002 | 121.3065 | 118.79 | -122.2209
320.3594 | 121.8155 | -119.4351 | 2.2247 | 1.4211e-13 | -0.022344 | 0.06639 | 0.063244 | 0.078474 | 0.062003 | -0.24059 | -0.001643 | -0.00076696 | 0.061533 | 0.025179 | 0.061171 | -118.8768 | -0.19547 | -1.7985 | 2.1307 | 1.9922 | 2.3031 | -119.5089 | -119.1599 | -0.095794 | -119.199 | 2.1219 | 2.1931 | 1.9949 | -119.8224 | -0.073763 | -0.094015 | 0.55833 | 117.6366 | 117.7104 | -0.23254 | 0.078335 | -0.38726 | -0.10279 | 0.27524 | 0.23616 | 0.62342 | -0.03161 | -0.22987 | 121.5658 | 121.4273 | 121.7382 | 119.2396 | -121.7336 | 121.5571 | 121.6282 | 121.43 | 119.3393 | -122.0471
322.0312 | 121.8658 | -119.5679 | 2.0462 | 1.4211e-13 | -0.022771 | 0.056988 | 0.062817 | 0.078474 | 0.06243 | -0.23296 | -0.0018566 | -0.00098076 | 0.061319 | 0.025179 | 0.061385 | -118.9226 | -0.18632 | -1.6429 | 2.0804 | 1.951 | 2.1978 | -119.5455 | -119.2011 | -0.10037 | -119.2356 | 2.067 | 2.1473 | 1.9491 | -119.8727 | 0.022357 | 0.03415 | 0.64529 | 117.925 | 117.9027 | -0.095223 | 0.15156 | -0.30488 | 0.020792 | 0.36679 | 0.33228 | 0.63716 | 0.10113 | -0.097126 | 121.6482 | 121.5189 | 121.7656 | 119.3816 | -121.5917 | 121.6349 | 121.7152 | 121.5169 | 119.4675 | -121.919
323.75 | 121.5591 | -118.4921 | 3.0212 | 1.4211e-13 | -0.022344 | 1.5119 | 0.062817 | 0.075696 | 0.061789 | -0.22533 | -0.0018566 | -0.00076696 | 0.061746 | 0.025393 | 0.061171 | -114.9714 | -0.021486 | -1.6062 | 5.07 | 4.996 | 5.1647 | -115.6031 | -115.2084 | 0.050725 | -115.2567 | 5.7252 | 5.7507 | 5.6669 | -115.8983 | 2.8891 | 2.0488 | 3.5207 | 116.8859 | 113.9968 | 1.9747 | 2.1435 | 2.5938 | 2.704 | 3.2837 | 3.2354 | 0.64164 | 2.7295 | 2.6457 | 123.5622 | 123.4881 | 123.6568 | 118.4706 | -118.6243 | 124.2173 | 124.2428 | 124.159 | 118.5429 | -118.9196
325.4844 | 121.3486 | -118.602 | 3.1128 | 1.4211e-13 | -0.02384 | 0.13156 | 0.06303 | 0.077406 | 0.062217 | -0.22533 | -0.001643 | -0.00098076 | 0.061533 | 0.025393 | 0.061171 | -117.9886 | -0.14969 | -1.6795 | 2.996 | 3.0316 | 3.1638 | -118.6893 | -118.267 | -0.091215 | -118.3107 | 2.9964 | 3.0585 | 3.08 | -118.9295 | -0.087265 | -0.11676 | 0.6134 | 116.9225 | 117.0098 | -0.081186 | 0.051051 | -0.32752 | -0.11636 | 0.33496 | 0.2913 | 0.61882 | -0.054316 | -0.0328 | 121.598 | 121.6336 | 121.7658 | 118.4523 | -121.802 | 121.5984 | 121.6605 | 121.682 | 118.5108 | -122.0423
327.2188 | 121.8338 | -118.6569 | 2.9846 | 1.4211e-13 | -0.024481 | 0.13156 | 0.063458 | 0.077833 | 0.062217 | -0.22533 | -0.0018566 | -0.00098076 | 0.061533 | 0.024966 | 0.060957 | -118.0481 | -0.15884 | -1.5925 | 2.964 | 2.9996 | 3.1226 | -118.6526 | -118.3082 | -0.086637 | -118.3519 | 2.9506 | 3.0218 | 3.0296 | -118.9799 | 0.004297 | -0.020637 | 0.60882 | 117.0644 | 117.0601 | 0.014936 | 0.13802 | -0.32296 | -0.033973 | 0.34869 | 0.30502 | 0.62798 | 0.037229 | 0.045009 | 121.6209 | 121.6565 | 121.7796 | 118.4981 | -121.6372 | 121.6076 | 121.6788 | 121.6865 | 118.5703 | -121.9645
328.9531 | 121.8384 | -118.8309 | 2.7878 | 1.4211e-13 | -0.024267 | 0.13242 | 0.063244 | 0.077833 | 0.062217 | -0.24059 | -0.0018566 | -0.0011944 | 0.061319 | 0.025179 | 0.061171 | -118.2541 | -0.15427 | -1.5467 | 2.7488 | 2.7706 | 2.8479 | -118.8861 | -118.5326 | -0.086637 | -118.5717 | 2.7309 | 2.8067 | 2.6084 | -119.1997 | -0.055277 | -0.038983 | 0.57674 | 117.2842 | 117.3394 | -0.017173 | 0.060139 | -0.36879 | -0.056903 | 0.29828 | 0.2592 | 0.62798 | 0.018873 | -0.17938 | 121.5797 | 121.6015 | 121.6788 | 118.6766 | -121.6739 | 121.5618 | 121.6375 | 121.4393 | 118.7442 | -121.9874
330.7188 | 121.7789 | -118.808 | 2.8748 | 1.4211e-13 | -0.024267 | 0.13199 | 0.063244 | 0.077192 | 0.061576 | -0.22533 | -0.001643 | -0.00098076 | 0.061746 | 0.025179 | 0.061385 | -118.1946 | -0.13595 | -1.8123 | 2.8083 | 2.6653 | 2.9212 | -118.822 | -118.4685 | -0.091215 | -118.5076 | 2.8041 | 2.8662 | 2.6725 | -119.131 | -0.014061 | -0.066439 | 0.61337 | 116.9957 | 117.0098 | -0.20946 | 0.046422 | -0.32299 | -0.070622 | 0.33949 | 0.30041 | 0.6234 | -0.00858 | -0.20226 | 121.6163 | 121.4733 | 121.7292 | 118.672 | -121.6968 | 121.6121 | 121.6742 | 121.4805 | 118.7168 | -122.0057
332.3906 | 121.7056 | -119.1055 | 2.5681 | 1.4211e-13 | -0.02384 | 0.13263 | 0.063244 | 0.077406 | 0.062217 | -0.23296 | -0.0018566 | -0.00098076 | 0.061533 | 0.025393 | 0.060744 | -118.5288 | -0.13595 | -1.7985 | 2.4695 | 2.3356 | 2.5869 | -119.1517 | -118.8027 | -0.082058 | -118.8464 | 2.4653 | 2.5319 | 2.3383 | -119.4835 | -0.046197 | -0.098538 | 0.57669 | 117.307 | 117.3532 | -0.23244 | 0.018886 | -0.37802 | -0.10273 | 0.30279 | 0.25913 | 0.63715 | -0.036116 | -0.2298 | 121.575 | 121.4411 | 121.6925 | 118.9696 | -121.7198 | 121.5709 | 121.6375 | 121.4438 | 119.0235 | -122.0516
334.0625 | 121.6965 | -118.721 | 2.9709 | 1.4211e-13 | -0.024053 | 0.13178 | 0.063458 | 0.077192 | 0.062003 | -0.24822 | -0.001643 | -0.00098076 | 0.061746 | 0.025393 | 0.060744 | -118.071 | -0.14053 | -1.7665 | 2.9365 | 2.7935 | 3.0356 | -118.703 | -118.3586 | -0.082058 | -118.3931 | 2.9232 | 2.9898 | 2.7961 | -119.0165 | 0.018016 | -0.034374 | 0.65001 | 116.9545 | 116.9365 | -0.17738 | 0.064757 | -0.2955 | -0.047711 | 0.36241 | 0.3279 | 0.6234 | 0.018912 | -0.17477 | 121.6575 | 121.5145 | 121.7567 | 118.5805 | -121.6739 | 121.6442 | 121.7108 | 121.5171 | 118.6389 | -121.9874
335.7969 | 121.7285 | -119.1879 | 2.5269 | 1.4211e-13 | -0.02384 | 0.13263 | 0.063244 | 0.077619 | 0.061576 | -0.23296 | -0.001643 | -0.00055336 | 0.061746 | 0.025393 | 0.060957 | -118.6112 | -0.12679 | -1.6841 | 2.4008 | 2.2532 | 2.5045 | -119.2433 | -118.8943 | -0.082058 | -118.9334 | 2.3921 | 2.4541 | 2.265 | -119.5614 | -0.055378 | -0.12601 | 0.57668 | 117.5039 | 117.5592 | -0.27366 | -0.02233 | -0.37346 | -0.13478 | 0.29362 | 0.25453 | 0.62799 | -0.072753 | -0.26185 | 121.5888 | 121.4411 | 121.6925 | 119.0611 | -121.7702 | 121.58 | 121.642 | 121.4529 | 119.1059 | -122.0882
337.5312 | 121.7377 | -119.3298 | 2.4033 | 1.4211e-13 | -0.024053 | 0.13284 | 0.063458 | 0.077406 | 0.062217 | -0.24059 | -0.0018566 | -0.00098076 | 0.061319 | 0.025393 | 0.061171 | -118.6982 | -0.13137 | -1.8397 | 2.2955 | 2.1616 | 2.413 | -119.344 | -118.995 | -0.086637 | -119.0295 | 2.2959 | 2.358 | 2.1643 | -119.6621 | -0.014208 | -0.10772 | 0.6316 | 117.4901 | 117.5043 | -0.24165 | 0.009694 | -0.33229 | -0.10734 | 0.33479 | 0.30029 | 0.63257 | -0.045308 | -0.23899 | 121.6254 | 121.4914 | 121.7428 | 119.1985 | -121.7473 | 121.6258 | 121.6878 | 121.4941 | 119.2432 | -122.0654
339.2656 | 121.8155 | -118.8171 | 2.8107 | 1.4211e-13 | -0.024481 | 0.13135 | 0.06303 | 0.076765 | 0.062217 | -0.22533 | -0.001643 | -0.0011944 | 0.061746 | 0.025393 | 0.060957 | -118.1855 | -0.12679 | -1.8626 | 2.8221 | 2.6882 | 2.9258 | -118.8175 | -118.4593 | -0.086637 | -118.5076 | 2.8087 | 2.8845 | 2.6908 | -119.1356 | -0.000326 | 0.011383 | 0.63168 | 116.9545 | 116.9549 | -0.12248 | 0.11509 | -0.31842 | -0.001956 | 0.3578 | 0.30956 | 0.62798 | 0.073821 | -0.11986 | 121.6392 | 121.5053 | 121.7429 | 118.6903 | -121.6281 | 121.6259 | 121.7016 | 121.508 | 118.7305 | -121.9462
341 | 121.8338 | -119.2612 | 2.3621 | 1.4211e-13 | -0.02384 | 0.13284 | 0.063458 | 0.077192 | 0.061576 | -0.24059 | -0.0018566 | -0.00055336 | 0.061533 | 0.025393 | 0.060957 | -118.6799 | -0.14511 | -1.7298 | 2.3276 | 2.1845 | 2.4267 | -119.3257 | -118.9721 | -0.086637 | -119.0021 | 2.3234 | 2.3808 | 2.1872 | -119.6392 | -0.064557 | -0.034475 | 0.58125 | 117.5313 | 117.5959 | -0.17756 | 0.064628 | -0.37806 | -0.038669 | 0.28902 | 0.25909 | 0.63715 | 0.018783 | -0.1749 | 121.5888 | 121.4457 | 121.6879 | 119.1161 | -121.6878 | 121.5846 | 121.642 | 121.4483 | 119.1745 | -122.0013
342.6719 | 121.7514 | -119.3436 | 2.3438 | 1.4211e-13 | -0.024267 | 0.13263 | 0.063244 | 0.077406 | 0.061789 | -0.23296 | -0.0020702 | -0.0011944 | 0.061746 | 0.025607 | 0.06053 | -118.7257 | -0.14969 | -1.7115 | 2.2635 | 2.1204 | 2.3763 | -119.3761 | -119.0179 | -0.086637 | -119.057 | 2.2547 | 2.3305 | 2.1368 | -119.6896 | -0.032527 | -0.080261 | 0.61786 | 117.632 | 117.6646 | -0.22335 | 0.032574 | -0.34603 | -0.089035 | 0.32563 | 0.28655 | 0.63257 | -0.013271 | -0.20695 | 121.6071 | 121.464 | 121.7199 | 119.1939 | -121.7198 | 121.5983 | 121.674 | 121.4804 | 119.2569 | -122.0333
344.4062 | 121.7422 | -119.252 | 2.449 | 1.4211e-13 | -0.024053 | 0.13113 | 0.063458 | 0.076551 | 0.062217 | -0.24059 | -0.0018566 | -0.00098076 | 0.061319 | 0.025607 | 0.060957 | -118.6296 | -0.14511 | -2.1739 | 2.3642 | 2.2257 | 2.4771 | -119.2708 | -118.9172 | -0.077479 | -118.9563 | 2.3646 | 2.4266 | 2.2284 | -119.6026 | -0.018765 | -0.084822 | 0.62245 | 117.0781 | 117.0968 | -0.22332 | 0.028017 | -0.35058 | -0.084437 | 0.33481 | 0.29573 | 0.64631 | -0.022406 | -0.22066 | 121.6162 | 121.4777 | 121.7291 | 119.1069 | -121.7198 | 121.6166 | 121.6786 | 121.4804 | 119.1745 | -122.0516
346.1562 | 121.7331 | -119.1055 | 2.5955 | 1.4211e-13 | -0.024053 | 0.13135 | 0.062817 | 0.076978 | 0.062003 | -0.24059 | -0.0018566 | -0.001408 | 0.061746 | 0.025393 | 0.060744 | -118.4922 | -0.12222 | -1.6154 | 2.5107 | 2.3722 | 2.619 | -119.1288 | -118.7753 | -0.082058 | -118.8143 | 2.5111 | 2.5777 | 2.3795 | -119.4561 | -0.023302 | -0.084798 | 0.61332 | 117.4901 | 117.5134 | -0.22328 | 0.02347 | -0.35054 | -0.08441 | 0.33026 | 0.29118 | 0.64172 | -0.017796 | -0.21605 | 121.6163 | 121.4778 | 121.7245 | 118.9833 | -121.7244 | 121.6166 | 121.6833 | 121.485 | 119.0235 | -122.0516
347.8906 | 121.7834 | -119.133 | 2.5772 | 1.4211e-13 | -0.024267 | 0.13135 | 0.06303 | 0.077619 | 0.06243 | -0.22533 | -0.001643 | -0.0011944 | 0.061533 | 0.025179 | 0.060744 | -118.5655 | -0.12222 | -1.6062 | 2.4375 | 2.2898 | 2.5503 | -119.2021 | -118.8485 | -0.086637 | -118.8968 | 2.4241 | 2.4953 | 2.2971 | -119.5293 | -0.069099 | -0.13974 | 0.56753 | 117.5268 | 117.5959 | -0.28739 | -0.026898 | -0.39634 | -0.15309 | 0.28447 | 0.23623 | 0.63257 | -0.0819 | -0.28016 | 121.5705 | 121.4228 | 121.6833 | 119.0108 | -121.7793 | 121.5571 | 121.6283 | 121.43 | 119.0464 | -122.1065
349.5625 | 121.8475 | -119.2062 | 2.4078 | 1.4211e-13 | -0.024053 | 0.13113 | 0.063244 | 0.076765 | 0.062003 | -0.22533 | -0.0018566 | -0.00098076 | 0.061533 | 0.025179 | 0.06053 | -118.6158 | -0.12222 | -1.6612 | 2.3734 | 2.2257 | 2.4816 | -119.2754 | -118.9218 | -0.082058 | -118.9654 | 2.3646 | 2.4312 | 2.2421 | -119.598 | -0.06912 | -0.034467 | 0.59041 | 117.5451 | 117.6142 | -0.18212 | 0.073795 | -0.39178 | -0.043238 | 0.28445 | 0.24079 | 0.63257 | 0.023372 | -0.16573 | 121.5796 | 121.432 | 121.6879 | 119.084 | -121.6832 | 121.5708 | 121.6374 | 121.4483 | 119.1242 | -122.0059
351.2969 | 121.8658 | -119.2062 | 2.4445 | 1.4211e-13 | -0.024267 | 0.13135 | 0.063244 | 0.076765 | 0.062003 | -0.23296 | -0.001643 | -0.00098076 | 0.061746 | 0.025607 | 0.060957 | -118.657 | -0.11306 | -1.5467 | 2.3276 | 2.1891 | 2.4358 | -119.3166 | -118.9584 | -0.077479 | -119.0021 | 2.3234 | 2.3992 | 2.1963 | -119.6392 | -0.11033 | -0.11687 | 0.54921 | 117.6595 | 117.7699 | -0.25537 | -0.008612 | -0.43299 | -0.12107 | 0.24783 | 0.20416 | 0.63715 | -0.0453 | -0.24813 | 121.5338 | 121.3953 | 121.6421 | 119.0932 | -121.761 | 121.5296 | 121.6054 | 121.4026 | 119.1288 | -122.0837
353.0469 | 121.7422 | -119.0964 | 2.5772 | 1.4211e-13 | -0.024053 | 0.13071 | 0.06303 | 0.076124 | 0.062217 | -0.2177 | -0.0020702 | -0.00076696 | 0.061319 | 0.02582 | 0.060744 | -118.4831 | -0.11764 | -2.2518 | 2.5061 | 2.3677 | 2.6144 | -119.138 | -118.7844 | -0.082058 | -118.8281 | 2.4882 | 2.564 | 2.3703 | -119.4607 | -0.041615 | -0.071065 | 0.61332 | 116.8446 | 116.8862 | -0.20955 | 0.037202 | -0.36428 | -0.088991 | 0.31195 | 0.26829 | 0.63257 | -0.013221 | -0.2069 | 121.6025 | 121.464 | 121.7108 | 118.9787 | -121.7152 | 121.5846 | 121.6604 | 121.4667 | 119.0143 | -122.0379
354.7188 | 121.7331 | -118.7485 | 2.9663 | 1.4211e-13 | -0.024053 | 0.12921 | 0.063458 | 0.075696 | 0.062003 | -0.23296 | -0.0014292 | -0.0011944 | 0.061533 | 0.025607 | 0.060744 | -118.1671 | -0.12222 | -2.6043 | 2.8266 | 2.6836 | 2.9258 | -118.8175 | -118.4548 | -0.082058 | -118.503 | 2.8179 | 2.8753 | 2.6908 | -119.1401 | -0.068991 | -0.13968 | 0.58133 | 116.1442 | 116.2132 | -0.2827 | -0.040553 | -0.39166 | -0.14844 | 0.29372 | 0.24548 | 0.63714 | -0.090976 | -0.2755 | 121.5751 | 121.4321 | 121.6742 | 118.6263 | -121.7838 | 121.5663 | 121.6238 | 121.4393 | 118.6664 | -122.1064
356.4688 | 121.756 | -118.9362 | 2.774 | 1.4211e-13 | -0.024267 | 0.13071 | 0.063244 | 0.075696 | 0.062003 | -0.23296 | -0.0022838 | -0.0011944 | 0.061533 | 0.025607 | 0.060744 | -118.2999 | -0.12222 | -2.5219 | 2.6755 | 2.5462 | 2.793 | -118.9548 | -118.5967 | -0.086637 | -118.6404 | 2.6805 | 2.7426 | 2.5535 | -119.2775 | -0.018676 | -0.098504 | 0.63624 | 116.4143 | 116.4329 | -0.22781 | 0.018929 | -0.34134 | -0.093533 | 0.33946 | 0.2958 | 0.63714 | -0.031494 | -0.22059 | 121.6117 | 121.4824 | 121.7291 | 118.8139 | -121.7289 | 121.6167 | 121.6787 | 121.4896 | 118.8495 | -122.0515
358.1562 | 121.7377 | -118.6981 | 2.9846 | 1.4211e-13 | -0.024053 | 0.12985 | 0.06303 | 0.075483 | 0.062217 | -0.24059 | -0.001002 | -0.00098076 | 0.061319 | 0.025393 | 0.060957 | -118.103 | -0.13137 | -2.6043 | 2.8862 | 2.7431 | 2.9899 | -118.7488 | -118.4044 | -0.077479 | -118.4435 | 2.8865 | 2.9532 | 2.7549 | -119.0806 | -0.050661 | -0.098469 | 0.59507 | 116.0938 | 116.1445 | -0.24148 | 0.005238 | -0.38249 | -0.098072 | 0.29373 | 0.25465 | 0.63714 | -0.03145 | -0.22971 | 121.5843 | 121.4413 | 121.688 | 118.5667 | -121.7334 | 121.5847 | 121.6513 | 121.453 | 118.6206 | -122.0652
359.9062 | 121.8475 | -118.5104 | 3.067 | 1.4211e-13 | -0.02384 | 0.12964 | 0.06303 | 0.075055 | 0.062217 | -0.24822 | -0.0018566 | -0.0011944 | 0.061533 | 0.025607 | 0.060744 | -117.9657 | -0.12222 | -2.5677 | 3.0052 | 2.8713 | 3.1089 | -118.6297 | -118.2762 | -0.086637 | -118.3198 | 2.9964 | 3.0722 | 2.874 | -118.9616 | -0.11929 | -0.061829 | 0.54474 | 115.9428 | 116.0621 | -0.19567 | 0.041883 | -0.45112 | -0.070586 | 0.23425 | 0.19059 | 0.64171 | 0.005196 | -0.19306 | 121.5156 | 121.3818 | 121.6193 | 118.3882 | -121.6967 | 121.5069 | 121.5827 | 121.3844 | 118.4238 | -122.0286
361.5781 | 121.8567 | -118.5883 | 3.0167 | 1.4211e-13 | -0.024053 | 0.12964 | 0.06303 | 0.075269 | 0.062003 | -0.24059 | -0.001643 | -0.00098076 | 0.061319 | 0.025607 | 0.061171 | -117.9657 | -0.14053 | -2.1602 | 3.0006 | 2.8576 | 3.1043 | -118.6343 | -118.2853 | -0.077479 | -118.329 | 2.9919 | 3.0631 | 2.8694 | -118.9616 | -0.046051 | -0.016054 | 0.62256 | 116.4281 | 116.4741 | -0.15905 | 0.087659 | -0.3733 | -0.024811 | 0.30291 | 0.25925 | 0.63256 | 0.046393 | -0.14729 | 121.5889 | 121.4459 | 121.6926 | 118.4477 | -121.651 | 121.5801 | 121.6513 | 121.4576 | 118.5108 | -121.9782
363.25 | 121.8155 | -118.0115 | 3.5843 | 1.4211e-13 | -0.024694 | 0.01703 | -0.0029979 | -0.0093413 | 0.020552 | -0.24059 | -0.0018566 | -0.00076696 | 0.061746 | 0.025607 | 0.06053 | 0.055988 | 0.038035 | 0.028217 | 0.15743 | 0.11941 | 0.26559 | -0.15006 | -117.9831 | -0.0729 | -118.0085 | 3.3032 | 3.3744 | 3.3822 | -118.6502 | 117.8614 | -3.4269 | 118.0675 | 118.0397 | 0.17827 | -3.4649 | -3.3187 | -0.63873 | -0.2811 | 0.028327 | 0.002979 | 0.64171 | -0.20989 | -0.20211 | 118.1689 | 118.1309 | 118.2771 | 118.0495 | -3.7343 | 121.3147 | 121.3859 | 121.3937 | 117.9386 | -122.2345
364.9844 | 121.8063 | -119.3619 | 2.2888 | 1.4211e-13 | -0.024053 | 0.016817 | -0.0032117 | -0.0093413 | 0.020125 | -0.2177 | -0.0018566 | -0.00098076 | 0.061746 | 0.025607 | 0.060744 | 0.074302 | 0.019721 | 0.032795 | 0.11622 | 0.11941 | 0.26101 | 0.069732 | -118.702 | -0.10495 | -118.7411 | 2.6027 | 2.6647 | 2.6725 | -119.3782 | 119.4316 | -2.1726 | 119.4362 | 119.3947 | -0.036937 | -2.1694 | -2.0278 | -0.016356 | 0.31386 | 0.65987 | 0.62079 | 0.63714 | 0.3759 | 0.38368 | 119.4781 | 119.4813 | 119.6229 | 119.3816 | -2.2191 | 121.9646 | 122.0266 | 122.0344 | 119.2569 | -121.6671
366.7188 | 121.9025 | -119.6045 | 2.0325 | 1.4211e-13 | -0.024053 | 0.016817 | -0.0032117 | -0.0093413 | 0.020339 | -0.22533 | -0.0014292 | -0.0011944 | 0.061746 | 0.025393 | 0.061171 | 0.10177 | 0.019721 | 0.037373 | 0.11622 | 0.12399 | 0.26101 | 0.092626 | -119.3751 | -0.091215 | -119.4233 | 1.9205 | 1.9871 | 1.7934 | -120.0696 | 119.6971 | -1.9162 | 119.7063 | 119.6419 | -0.055253 | -1.9085 | -1.7715 | -0.46514 | -0.11199 | 0.22942 | 0.18117 | 0.64632 | -0.045387 | -0.23907 | 119.7207 | 119.7285 | 119.8655 | 119.6242 | -1.9398 | 121.525 | 121.5916 | 121.3979 | 119.5133 | -122.1021
368.3906 | 121.9116 | -120.1996 | 1.4603 | 1.4211e-13 | -0.024694 | 0.016603 | -0.0034253 | -0.0093413 | 0.020125 | -0.24059 | -0.0018566 | -0.0011944 | 0.061319 | 0.025607 | 0.061171 | 0.092615 | 0.001407 | 0.037373 | 0.11622 | 0.050727 | 0.25185 | 0.088047 | -119.7872 | -0.086637 | -119.8262 | 1.5038 | 1.5842 | 1.3859 | -120.4817 | 120.2876 | -1.344 | 120.2922 | 120.237 | -0.050674 | -1.4095 | -1.2084 | -0.28214 | 0.043576 | 0.41242 | 0.37334 | 0.65548 | 0.1239 | -0.074356 | 120.3158 | 120.2503 | 120.4514 | 120.201 | -1.3722 | 121.7034 | 121.7838 | 121.5855 | 120.1129 | -121.942
370.0625 | 121.8613 | -120.3644 | 1.3229 | 1.4211e-13 | -0.024481 | 0.016603 | -0.0034253 | -0.0095551 | 0.020552 | -0.22533 | -0.0018566 | -0.00098076 | 0.061746 | 0.02582 | 0.06053 | 0.10177 | -0.007751 | 0.037373 | 0.11165 | 0.046148 | 0.26101 | 0.10178 | -120.0024 | -0.082058 | -120.0414 | 1.3207 | 1.3827 | 1.1936 | -120.6786 | 120.4662 | -1.2113 | 120.4662 | 120.4018 | -0.064411 | -1.2768 | -1.0619 | -0.31424 | -0.002235 | 0.36202 | 0.32294 | 0.63717 | 0.059772 | -0.12933 | 120.476 | 120.4105 | 120.6254 | 120.3566 | -1.2212 | 121.6851 | 121.7471 | 121.558 | 120.2823 | -122.0016
371.7969 | 121.8796 | -120.1263 | 1.5656 | 1.4211e-13 | -0.024481 | 0.016817 | -0.0032117 | -0.0097687 | 0.020125 | -0.23296 | -0.0018566 | -0.00098076 | 0.061746 | 0.025607 | 0.060744 | 0.097194 | 0.001407 | 0.037373 | 0.11622 | 0.046148 | 0.26559 | 0.097205 | -119.7093 | -0.095794 | -119.7484 | 1.6 | 1.6803 | 1.4775 | -120.3947 | 120.2235 | -1.4493 | 120.2235 | 120.1637 | -0.059832 | -1.5194 | -1.3 | -0.26839 | 0.034438 | 0.41702 | 0.37794 | 0.64633 | 0.11477 | -0.08807 | 120.2426 | 120.1725 | 120.3919 | 120.1278 | -1.4683 | 121.7263 | 121.8067 | 121.6038 | 120.0305 | -121.9603
373.4688 | 121.9345 | -120.1309 | 1.5427 | 1.4211e-13 | -0.024694 | 0.016817 | -0.0036391 | -0.0093413 | 0.021407 | -0.24059 | -0.0020702 | -0.00098076 | 0.061319 | 0.02582 | 0.06053 | 0.10177 | 0.015142 | 0.041952 | 0.10707 | 0.046148 | 0.25643 | 0.097205 | -119.8375 | -0.086637 | -119.872 | 1.4809 | 1.5475 | 1.3539 | -120.5184 | 120.2281 | -1.4356 | 120.2327 | 120.1729 | -0.055253 | -1.4965 | -1.2862 | -0.38744 | -0.061715 | 0.2934 | 0.25889 | 0.64633 | 0.004874 | -0.1888 | 120.238 | 120.1771 | 120.3874 | 120.1461 | -1.4455 | 121.6119 | 121.6785 | 121.4848 | 120.0443 | -122.061
375.2031 | 121.9254 | -120.0485 | 1.6525 | 1.4211e-13 | -0.024481 | 0.016817 | -0.0034253 | -0.0097687 | 0.021193 | -0.23296 | -0.0018566 | -0.00076696 | 0.061746 | 0.025607 | 0.060957 | 0.097194 | 0.019721 | 0.032795 | 0.11622 | 0.050727 | 0.22896 | 0.10178 | -119.7414 | -0.082058 | -119.7667 | 1.5817 | 1.6391 | 1.4546 | -120.4268 | 120.1503 | -1.5363 | 120.1457 | 120.0813 | -0.068989 | -1.6018 | -1.4236 | -0.37826 | -0.070851 | 0.30715 | 0.2818 | 0.66006 | -0.013417 | -0.19794 | 120.1647 | 120.0992 | 120.2775 | 120.0682 | -1.5507 | 121.6302 | 121.6876 | 121.5031 | 119.9665 | -122.0793
376.9375 | 121.9116 | -120.5566 | 1.1124 | 1.4211e-13 | -0.024694 | 0.016603 | -0.0034253 | -0.0095551 | 0.021193 | -0.24059 | -0.0020702 | -0.00076696 | 0.061319 | 0.02582 | 0.060744 | 0.092615 | 0.0243 | 0.041952 | 0.1208 | 0.046148 | 0.2198 | 0.097205 | -120.2725 | -0.082058 | -120.3162 | 1.0506 | 1.1126 | 0.93263 | -120.9579 | 120.6538 | -0.99156 | 120.6493 | 120.5986 | -0.055253 | -1.0662 | -0.89256 | -0.40128 | -0.061795 | 0.28414 | 0.24048 | 0.64176 | 0.000205 | -0.17974 | 120.6774 | 120.6028 | 120.7764 | 120.5809 | -1.0152 | 121.6072 | 121.6692 | 121.4893 | 120.4746 | -122.0703
378.6719 | 121.8018 | -120.2911 | 1.4191 | 1.4211e-13 | -0.024481 | 0.016817 | -0.0032117 | -0.0097687 | 0.021193 | -0.23296 | -0.001643 | -0.00076696 | 0.061746 | 0.02582 | 0.060744 | 0.097194 | 0.0243 | 0.037373 | 0.11165 | 0.050727 | 0.2198 | 0.10178 | -120.0619 | -0.0729 | -120.1055 | 1.2612 | 1.3369 | 1.1387 | -120.7565 | 120.3929 | -1.3074 | 120.3883 | 120.3285 | -0.064411 | -1.3683 | -1.1993 | -0.46532 | -0.15789 | 0.22926 | 0.18559 | 0.65091 | -0.082144 | -0.2804 | 120.4028 | 120.3419 | 120.5109 | 120.3154 | -1.3173 | 121.5523 | 121.6281 | 121.4298 | 120.2182 | -122.1755
380.3594 | 121.9345 | -120.4697 | 1.2451 | 1.4211e-13 | -0.025122 | 0.01703 | -0.0034253 | -0.0097687 | 0.021407 | -0.23296 | -0.001643 | -0.00098076 | 0.061746 | 0.025607 | 0.060744 | 0.10177 | 0.0243 | 0.041952 | 0.10707 | 0.046148 | 0.22438 | 0.10636 | -120.1306 | -0.082058 | -120.1742 | 1.1971 | 1.2682 | 1.0746 | -120.8251 | 120.576 | -1.138 | 120.5714 | 120.5116 | -0.064411 | -1.199 | -1.0207 | -0.35547 | -0.048035 | 0.3391 | 0.29544 | 0.65091 | 0.023127 | -0.17055 | 120.5767 | 120.5158 | 120.694 | 120.494 | -1.1388 | 121.6667 | 121.7379 | 121.5442 | 120.3876 | -122.0703
382.0938 | 121.8521 | -120.2637 | 1.4648 | 1.4211e-13 | -0.024694 | 0.016817 | -0.0034253 | -0.0095551 | 0.021193 | -0.23296 | -0.001643 | -0.00076696 | 0.061319 | 0.025607 | 0.060744 | 0.097194 | 0.019721 | 0.028217 | 0.1208 | 0.046148 | 0.22438 | 0.11094 | -119.8925 | -0.082058 | -119.927 | 1.4443 | 1.5201 | 1.3127 | -120.5687 | 120.3746 | -1.344 | 120.3609 | 120.2919 | -0.082725 | -1.4187 | -1.2405 | -0.30505 | -0.020523 | 0.3712 | 0.3367 | 0.64175 | 0.055223 | -0.15219 | 120.3845 | 120.3098 | 120.4881 | 120.2834 | -1.3539 | 121.708 | 121.7837 | 121.5763 | 120.1816 | -122.0336
383.8438 | 121.7743 | -120.314 | 1.4557 | 1.4211e-13 | -0.024481 | 0.01703 | -0.0034253 | -0.0097687 | 0.021193 | -0.23296 | -0.001643 | -0.00098076 | 0.061319 | 0.025607 | 0.060744 | 0.10177 | 0.019721 | 0.032795 | 0.11622 | 0.046148 | 0.22438 | 0.11094 | -119.9749 | -0.082058 | -120.0231 | 1.3436 | 1.4193 | 1.2302 | -120.6649 | 120.425 | -1.3395 | 120.4158 | 120.3468 | -0.078147 | -1.4095 | -1.2313 | -0.35085 | -0.11209 | 0.33914 | 0.2909 | 0.64175 | -0.036351 | -0.22545 | 120.4303 | 120.3602 | 120.5384 | 120.3337 | -1.3447 | 121.6576 | 121.7334 | 121.5443 | 120.232 | -122.1206
385.5312 | 121.875 | -120.3278 | 1.3504 | 1.4211e-13 | -0.025122 | 0.01703 | -0.0034253 | -0.0095551 | 0.021193 | -0.23296 | -0.0018566 | -0.00076696 | 0.061105 | 0.026034 | 0.06053 | 0.092615 | 0.019721 | 0.032795 | 0.11622 | 0.046148 | 0.2198 | 0.11094 | -119.952 | -0.091215 | -119.9865 | 1.3802 | 1.4514 | 1.2486 | -120.6466 | 120.4387 | -1.2342 | 120.4204 | 120.3606 | -0.078147 | -1.3043 | -1.1306 | -0.31881 | 0.029819 | 0.37577 | 0.34126 | 0.66007 | 0.10098 | -0.10185 | 120.444 | 120.3739 | 120.5476 | 120.3475 | -1.2395 | 121.708 | 121.7791 | 121.5763 | 120.2365 | -121.997
387.2656 | 121.8567 | -120.0577 | 1.6571 | 1.4211e-13 | -0.024694 | 0.016603 | -0.0038527 | -0.0097687 | 0.02098 | -0.23296 | -0.0018566 | -0.0011944 | 0.061533 | 0.02582 | 0.06053 | 0.10177 | 0.028878 | 0.028217 | 0.11165 | 0.046148 | 0.22438 | 0.12468 | -119.7597 | -0.082058 | -119.8079 | 1.5588 | 1.63 | 1.4409 | -120.4497 | 120.1824 | -1.5455 | 120.1594 | 120.0859 | -0.096462 | -1.611 | -1.4327 | -0.392 | -0.098321 | 0.29799 | 0.24975 | 0.64175 | -0.027151 | -0.21625 | 120.1693 | 120.1038 | 120.2821 | 120.0866 | -1.5324 | 121.6165 | 121.6876 | 121.4985 | 119.9756 | -122.1068
389 | 121.7468 | -120.1492 | 1.6022 | 1.4211e-13 | -0.024481 | 0.016175 | -0.0036391 | -0.0091277 | 0.02098 | -0.23296 | -0.0020702 | -0.00098076 | 0.061533 | 0.02582 | 0.060744 | 0.092615 | 0.019721 | 0.032795 | 0.1208 | 0.046148 | 0.2198 | 0.11094 | -119.8329 | -0.091215 | -119.8766 | 1.4947 | 1.5521 | 1.363 | -120.5229 | 120.2602 | -1.4814 | 120.2418 | 120.182 | -0.078147 | -1.556 | -1.3824 | -0.37371 | -0.10749 | 0.31628 | 0.27262 | 0.64633 | -0.050056 | -0.23916 | 120.27 | 120.1954 | 120.369 | 120.169 | -1.4912 | 121.6439 | 121.7013 | 121.5122 | 120.058 | -122.1251
390.75 | 121.7606 | -120.1813 | 1.5472 | 1.4211e-13 | -0.024694 | 0.016603 | -0.0034253 | -0.0097687 | 0.02098 | -0.24059 | -0.0018566 | -0.0011944 | 0.061319 | 0.026248 | 0.06053 | 0.10635 | 0.019721 | 0.028217 | 0.11165 | 0.032411 | 0.22438 | 0.11552 | -119.8833 | -0.086637 | -119.9224 | 1.4535 | 1.5109 | 1.3172 | -120.5779 | 120.2968 | -1.4356 | 120.2876 | 120.2095 | -0.087304 | -1.5148 | -1.3229 | -0.39661 | -0.093763 | 0.29796 | 0.25888 | 0.65549 | -0.036331 | -0.23001 | 120.2929 | 120.2137 | 120.4057 | 120.201 | -1.4317 | 121.6348 | 121.6922 | 121.4985 | 120.0946 | -122.1251
392.4375 | 121.8246 | -120.1035 | 1.6205 | 1.4211e-13 | -0.024908 | 0.015962 | -0.0036391 | -0.0095551 | 0.020766 | -0.23296 | -0.0018566 | -0.00098076 | 0.061746 | 0.025393 | 0.060744 | 0.10177 | 0.028878 | 0.037373 | 0.10707 | 0.046148 | 0.22438 | 0.11094 | -119.7917 | -0.091215 | -119.8308 | 1.5405 | 1.6025 | 1.4042 | -120.4909 | 120.2144 | -1.5134 | 120.2052 | 120.1408 | -0.073569 | -1.5743 | -1.3961 | -0.38743 | -0.080013 | 0.31172 | 0.27263 | 0.66006 | -0.018001 | -0.21626 | 120.2105 | 120.1496 | 120.3278 | 120.1323 | -1.5095 | 121.6439 | 121.7059 | 121.5077 | 120.0122 | -122.1114
394.1875 | 121.9025 | -120.0943 | 1.6113 | 1.4211e-13 | -0.024481 | 0.016175 | -0.0036391 | -0.0095551 | 0.02098 | -0.24059 | -0.0018566 | -0.00098076 | 0.061533 | 0.025607 | 0.060957 | 0.097194 | 0.0243 | 0.032795 | 0.11622 | 0.050727 | 0.22438 | 0.11094 | -119.7688 | -0.082058 | -119.8125 | 1.5542 | 1.63 | 1.4409 | -120.4588 | 120.2052 | -1.4951 | 120.1915 | 120.1271 | -0.078147 | -1.5606 | -1.3869 | -0.36453 | -0.057123 | 0.32545 | 0.28179 | 0.64633 | 0.018625 | -0.17048 | 120.2105 | 120.145 | 120.3187 | 120.1186 | -1.5004 | 121.6485 | 121.7243 | 121.5352 | 120.0122 | -122.0702
395.9531 | 121.7789 | -120.1172 | 1.6388 | 1.4211e-13 | -0.024694 | 0.015962 | -0.0032117 | -0.0099823 | 0.02098 | -0.2177 | -0.0022838 | -0.00055336 | 0.061105 | 0.02582 | 0.06053 | 0.097194 | 0.015142 | 0.032795 | 0.10707 | 0.050727 | 0.22896 | 0.10636 | -119.7826 | -0.091215 | -119.8217 | 1.545 | 1.6116 | 1.4317 | -120.4726 | 120.2236 | -1.5317 | 120.2144 | 120.15 | -0.073568 | -1.5881 | -1.4098 | -0.35538 | -0.093746 | 0.33461 | 0.29552 | 0.65091 | -0.027155 | -0.2071 | 120.2243 | 120.1679 | 120.3461 | 120.1323 | -1.5324 | 121.6622 | 121.7288 | 121.5489 | 120.026 | -122.1114
397.6406 | 121.8338 | -120.1218 | 1.5701 | 1.4211e-13 | -0.024694 | 0.016389 | -0.0036391 | -0.0099823 | 0.02098 | -0.24059 | -0.0020702 | -0.00098076 | 0.061105 | 0.02582 | 0.060744 | 0.097194 | 0.019721 | 0.032795 | 0.11165 | 0.03699 | 0.2198 | 0.11552 | -119.8009 | -0.082058 | -119.8491 | 1.5176 | 1.5979 | 1.3996 | -120.5046 | 120.2373 | -1.4585 | 120.219 | 120.1546 | -0.082726 | -1.5331 | -1.3503 | -0.38286 | -0.052552 | 0.32087 | 0.27263 | 0.65548 | 0.027774 | -0.17048 | 120.2334 | 120.1588 | 120.3416 | 120.1415 | -1.4546 | 121.6393 | 121.7197 | 121.5214 | 120.0397 | -122.0748
399.375 | 121.9025 | -120.3918 | 1.2955 | 1.4211e-13 | -0.024908 | 0.016175 | -0.0029979 | -0.0097687 | 0.02098 | -0.22533 | -0.0020702 | -0.00098076 | 0.061319 | 0.026034 | 0.060744 | 0.097194 | 0.019721 | 0.032795 | 0.10249 | 0.032411 | 0.22438 | 0.11094 | -120.1214 | -0.082058 | -120.1605 | 1.22 | 1.2911 | 1.0929 | -120.816 | 120.5028 | -1.193 | 120.489 | 120.4246 | -0.078147 | -1.2631 | -1.0711 | -0.42414 | -0.075496 | 0.27044 | 0.23136 | 0.65549 | -0.004334 | -0.20259 | 120.4943 | 120.4243 | 120.6162 | 120.4116 | -1.1845 | 121.6118 | 121.683 | 121.4847 | 120.3098 | -122.1115
401.0469 | 121.8475 | -120.1813 | 1.5106 | 1.4211e-13 | -0.024481 | 0.016389 | -0.0032117 | -0.0097687 | 0.021407 | -0.24059 | -0.0018566 | -0.0011944 | 0.061319 | 0.02582 | 0.06053 | 0.097194 | 0.028878 | 0.037373 | 0.11622 | 0.046148 | 0.2198 | 0.10178 | -119.9245 | -0.082058 | -119.9636 | 1.4168 | 1.4834 | 1.2898 | -120.6145 | 120.2831 | -1.3944 | 120.2785 | 120.2186 | -0.064411 | -1.4645 | -1.2908 | -0.43324 | -0.09377 | 0.25675 | 0.21767 | 0.65091 | -0.027182 | -0.22086 | 120.2975 | 120.2274 | 120.4011 | 120.2102 | -1.4088 | 121.5981 | 121.6647 | 121.471 | 120.0992 | -122.1251
402.7969 | 121.8704 | -120.4742 | 1.2085 | 1.4211e-13 | -0.024694 | 0.016175 | -0.0034253 | -0.0095551 | 0.021193 | -0.24059 | -0.0020702 | -0.00098076 | 0.061105 | 0.02582 | 0.06053 | 0.10177 | 0.0243 | 0.028217 | 0.10707 | 0.041569 | 0.21522 | 0.10636 | -120.1855 | -0.082058 | -120.2292 | 1.1513 | 1.2133 | 1.0196 | -120.8847 | 120.5806 | -1.1014 | 120.576 | 120.5025 | -0.078146 | -1.1669 | -0.99327 | -0.41042 | -0.057199 | 0.28874 | 0.24507 | 0.65549 | 0.004804 | -0.18887 | 120.5813 | 120.5158 | 120.6895 | 120.4985 | -1.1021 | 121.6255 | 121.6875 | 121.4939 | 120.3922 | -122.0932
404.5312 | 121.7834 | -120.5017 | 1.2589 | 1.4211e-13 | -0.024694 | 0.015962 | -0.0034253 | -0.0097687 | 0.02098 | -0.23296 | -0.0018566 | -0.00098076 | 0.061319 | 0.026034 | 0.060957 | 0.10635 | -0.003172 | 0.032795 | 0.10249 | 0.027833 | 0.2198 | 0.1201 | -119.865 | -0.10037 | -119.9132 | 1.4672 | 1.5384 | 1.3355 | -120.5641 | 120.6218 | -1.1564 | 120.6081 | 120.5345 | -0.087305 | -1.231 | -1.039 | -0.062438 | 0.20836 | 0.63671 | 0.58847 | 0.65091 | 0.27953 | 0.076695 | 120.6042 | 120.5295 | 120.7215 | 120.4985 | -1.1387 | 121.9689 | 122.0401 | 121.8373 | 120.4013 | -121.823
406.2812 | 121.8567 | -120.0302 | 1.6708 | 1.4211e-13 | -0.024694 | 0.015962 | -0.0034253 | -0.0099823 | 0.02098 | -0.23296 | -0.001643 | -0.00076696 | 0.061319 | 0.02582 | 0.060316 | 0.10177 | -0.003172 | 0.023639 | 0.10249 | 0.046148 | 0.2198 | 0.11552 | -119.6223 | -0.086637 | -119.666 | 1.7145 | 1.7902 | 1.5919 | -120.3077 | 120.1457 | -1.5683 | 120.132 | 120.0539 | -0.091882 | -1.6247 | -1.451 | -0.27752 | 0.043615 | 0.40789 | 0.36422 | 0.64174 | 0.11937 | -0.07889 | 120.1327 | 120.0764 | 120.25 | 120.027 | -1.5553 | 121.7447 | 121.8204 | 121.6222 | 119.9436 | -121.9786
408.0156 | 121.8155 | -120.52 | 1.2222 | 1.4211e-13 | -0.024908 | 0.016603 | -0.0034253 | -0.0097687 | 0.020766 | -0.23296 | -0.001643 | -0.00098076 | 0.061533 | 0.026034 | 0.060316 | 0.10635 | 0.015142 | 0.037373 | 0.11622 | 0.03699 | 0.2198 | 0.11552 | -120.1901 | -0.082058 | -120.2292 | 1.1513 | 1.2133 | 1.0196 | -120.8892 | 120.6355 | -1.106 | 120.6264 | 120.5574 | -0.078148 | -1.1852 | -1.0024 | -0.36922 | -0.070932 | 0.32993 | 0.29085 | 0.66007 | -0.008929 | -0.20261 | 120.6362 | 120.557 | 120.7398 | 120.5352 | -1.1067 | 121.6713 | 121.7333 | 121.5396 | 120.438 | -122.1115
409.75 | 121.8292 | -120.5475 | 1.236 | 1.4211e-13 | -0.024481 | 0.016175 | -0.0034253 | -0.0099823 | 0.020766 | -0.23296 | -0.0022838 | -0.00098076 | 0.06196 | 0.02582 | 0.060316 | 0.10177 | 0.0243 | 0.032795 | 0.11165 | 0.041569 | 0.22438 | 0.11552 | -120.2084 | -0.077479 | -120.2521 | 1.1284 | 1.1996 | 1.0013 | -120.9121 | 120.663 | -1.1243 | 120.6493 | 120.5803 | -0.082726 | -1.1944 | -1.0116 | -0.36465 | -0.10756 | 0.33908 | 0.29542 | 0.66007 | -0.036397 | -0.23466 | 120.6591 | 120.5891 | 120.7719 | 120.5718 | -1.1204 | 121.6759 | 121.7471 | 121.5488 | 120.47 | -122.1481
411.4219 | 121.8063 | -120.4697 | 1.3138 | 1.4211e-13 | -0.024908 | 0.015962 | -0.0034253 | -0.0095551 | 0.02098 | -0.24059 | -0.0018566 | -0.0011944 | 0.061319 | 0.026248 | 0.060744 | 0.097194 | 0.028878 | 0.037373 | 0.11165 | 0.046148 | 0.22438 | 0.11552 | -120.158 | -0.082058 | -120.2017 | 1.1833 | 1.2545 | 1.0563 | -120.8572 | 120.5852 | -1.2021 | 120.5669 | 120.507 | -0.078148 | -1.2676 | -1.0894 | -0.38752 | -0.13044 | 0.31163 | 0.26797 | 0.65549 | -0.059274 | -0.25753 | 120.5813 | 120.5158 | 120.694 | 120.4985 | -1.1983 | 121.653 | 121.7242 | 121.5259 | 120.3876 | -122.171
413.1719 | 121.7834 | -120.4742 | 1.3046 | 1.4211e-13 | -0.024908 | 0.015962 | -0.0034253 | -0.0097687 | 0.02098 | -0.23296 | -0.0018566 | -0.0011944 | 0.061533 | 0.02582 | 0.060744 | 0.10635 | 0.019721 | 0.032795 | 0.1208 | 0.032411 | 0.22438 | 0.11094 | -120.0939 | -0.082058 | -120.1422 | 1.2337 | 1.314 | 1.1066 | -120.7977 | 120.5852 | -1.1838 | 120.5806 | 120.507 | -0.078147 | -1.2722 | -1.0802 | -0.32342 | -0.070916 | 0.38031 | 0.33207 | 0.65549 | 0.009404 | -0.19801 | 120.595 | 120.5067 | 120.6986 | 120.494 | -1.1937 | 121.708 | 121.7883 | 121.5809 | 120.3922 | -122.1023
414.9219 | 121.9025 | -120.5383 | 1.1627 | 1.4211e-13 | -0.024694 | 0.016175 | -0.0034253 | -0.0099823 | 0.02098 | -0.23296 | -0.0018566 | -0.00098076 | 0.061105 | 0.026034 | 0.06053 | 0.10177 | 0.028878 | 0.032795 | 0.1208 | 0.046148 | 0.22438 | 0.11094 | -120.2405 | -0.082058 | -120.2841 | 1.0964 | 1.1584 | 0.96926 | -120.9488 | 120.6493 | -1.0419 | 120.6401 | 120.5711 | -0.078147 | -1.1166 | -0.93834 | -0.41044 | -0.066365 | 0.29788 | 0.25422 | 0.66465 | -0.004363 | -0.19346 | 120.6591 | 120.5845 | 120.7627 | 120.5672 | -1.0518 | 121.6347 | 121.6967 | 121.5076 | 120.4563 | -122.1115
416.6094 | 121.7514 | -120.6482 | 1.1261 | 1.4211e-13 | -0.024694 | 0.016175 | -0.0036391 | -0.0097687 | 0.021193 | -0.24059 | -0.0018566 | -0.00098076 | 0.061319 | 0.026034 | 0.060744 | 0.10635 | 0.028878 | 0.037373 | 0.11165 | 0.041569 | 0.22438 | 0.11552 | -120.2405 | -0.086637 | -120.2795 | 1.1009 | 1.1721 | 0.98299 | -120.9396 | 120.7637 | -1.0145 | 120.7545 | 120.6856 | -0.078148 | -1.0845 | -0.90172 | -0.29142 | -0.025165 | 0.40774 | 0.36866 | 0.66007 | 0.045994 | -0.14311 | 120.7598 | 120.6898 | 120.8726 | 120.6771 | -1.0106 | 121.7491 | 121.8203 | 121.6312 | 120.5616 | -122.0657
418.3438 | 121.8384 | -120.5566 | 1.181 | 1.4211e-13 | -0.025335 | 0.016175 | -0.0034253 | -0.0097687 | 0.020766 | -0.24059 | -0.0022838 | -0.00076696 | 0.061533 | 0.026248 | 0.06053 | 0.10177 | 0.028878 | 0.041952 | 0.10707 | 0.018675 | 0.22438 | 0.11552 | -120.2679 | -0.077479 | -120.307 | 1.0689 | 1.1492 | 0.95552 | -120.9717 | 120.6722 | -1.074 | 120.6584 | 120.5986 | -0.073569 | -1.1624 | -0.95665 | -0.41502 | -0.11215 | 0.28872 | 0.24963 | 0.66465 | -0.03183 | -0.22551 | 120.6637 | 120.5753 | 120.781 | 120.5855 | -1.0655 | 121.6255 | 121.7058 | 121.5122 | 120.4792 | -122.1527
420.0781 | 121.8155 | -120.6299 | 1.1536 | 1.4211e-13 | -0.025335 | 0.016175 | -0.0036391 | -0.0097687 | 0.020766 | -0.23296 | -0.0020702 | -0.00098076 | 0.061105 | 0.026034 | 0.060744 | 0.11093 | 0.0243 | 0.032795 | 0.1208 | 0.046148 | 0.22896 | 0.11552 | -120.2771 | -0.077479 | -120.3253 | 1.0643 | 1.14 | 0.94179 | -120.9717 | 120.7454 | -1.0328 | 120.7408 | 120.6627 | -0.082726 | -1.1074 | -0.92461 | -0.34178 | -0.089258 | 0.3528 | 0.30456 | 0.64634 | -0.013521 | -0.21178 | 120.7507 | 120.676 | 120.8588 | 120.6542 | -1.038 | 121.6942 | 121.7699 | 121.5717 | 120.5524 | -122.1252
421.75 | 121.8109 | -120.4605 | 1.3092 | 1.4211e-13 | -0.024908 | 0.016175 | -0.0036391 | -0.0093413 | 0.021193 | -0.23296 | -0.001643 | -0.00098076 | 0.061105 | 0.026461 | 0.060316 | 0.10177 | 0.028878 | 0.028217 | 0.11622 | 0.032411 | 0.21522 | 0.10636 | -120.126 | -0.077479 | -120.1605 | 1.22 | 1.2957 | 1.0975 | -120.8114 | 120.5669 | -1.193 | 120.5623 | 120.4887 | -0.078146 | -1.2768 | -1.094 | -0.35089 | -0.089229 | 0.33453 | 0.30002 | 0.65091 | -0.013489 | -0.21175 | 120.5767 | 120.4929 | 120.6757 | 120.4894 | -1.2028 | 121.6805 | 121.7562 | 121.558 | 120.383 | -122.1206
423.4844 | 121.9025 | -120.4788 | 1.2268 | 1.4211e-13 | -0.025122 | 0.016175 | -0.0032117 | -0.0099823 | 0.020766 | -0.22533 | -0.0018566 | -0.00098076 | 0.061533 | 0.026034 | 0.060316 | 0.10177 | 0.015142 | 0.028217 | 0.1208 | 0.03699 | 0.2198 | 0.11552 | -120.1947 | -0.082058 | -120.2292 | 1.1605 | 1.2316 | 1.0288 | -120.8755 | 120.5943 | -1.106 | 120.5806 | 120.507 | -0.087304 | -1.1898 | -1.007 | -0.39669 | -0.066353 | 0.28416 | 0.24965 | 0.64634 | 0.004808 | -0.19803 | 120.5996 | 120.5158 | 120.6986 | 120.494 | -1.1113 | 121.6393 | 121.7104 | 121.5076 | 120.3968 | -122.1023
425.2188 | 121.9208 | -120.4239 | 1.2589 | 1.4211e-13 | -0.024694 | 0.016175 | -0.0034253 | -0.0095551 | 0.020766 | -0.22533 | -0.0022838 | -0.00098076 | 0.061533 | 0.026248 | 0.060316 | 0.10635 | 0.028878 | 0.028217 | 0.10707 | 0.046148 | 0.22438 | 0.11094 | -120.1306 | -0.082058 | -120.1742 | 1.2108 | 1.2866 | 1.0883 | -120.8297 | 120.5348 | -1.1518 | 120.5302 | 120.4521 | -0.082725 | -1.2127 | -1.0345 | -0.40583 | -0.048032 | 0.29333 | 0.24966 | 0.65549 | 0.027708 | -0.17055 | 120.531 | 120.47 | 120.6483 | 120.4528 | -1.1479 | 121.6347 | 121.7104 | 121.5122 | 120.3418 | -122.0886
426.8906 | 121.788 | -120.5566 | 1.2314 | 1.4211e-13 | -0.024694 | 0.016175 | -0.0034253 | -0.0097687 | 0.020766 | -0.24059 | -0.0018566 | -0.00098076 | 0.061533 | 0.026461 | 0.06053 | 0.10177 | 0.0243 | 0.032795 | 0.11165 | 0.050727 | 0.22896 | 0.11552 | -120.1901 | -0.082058 | -120.2337 | 1.1605 | 1.2316 | 1.0242 | -120.8847 | 120.6722 | -1.1197 | 120.6584 | 120.5894 | -0.082726 | -1.1807 | -1.0024 | -0.32802 | -0.07093 | 0.36656 | 0.32289 | 0.65091 | 0.000231 | -0.20718 | 120.6683 | 120.6074 | 120.7856 | 120.5809 | -1.1159 | 121.7171 | 121.7883 | 121.5808 | 120.4746 | -122.116
428.625 | 121.8704 | -120.5933 | 1.1581 | 1.4211e-13 | -0.024908 | 0.015962 | -0.0034253 | -0.0097687 | 0.021193 | -0.24059 | -0.0020702 | -0.00098076 | 0.061319 | 0.026248 | 0.06053 | 0.10635 | 0.0243 | 0.028217 | 0.11165 | 0.041569 | 0.2198 | 0.11094 | -120.3503 | -0.0729 | -120.3986 | 0.99105 | 1.0576 | 0.85937 | -121.0495 | 120.7042 | -1.0465 | 120.6996 | 120.6215 | -0.082725 | -1.1166 | -0.93834 | -0.45624 | -0.16709 | 0.24292 | 0.19468 | 0.65092 | -0.10051 | -0.29877 | 120.7049 | 120.6348 | 120.8131 | 120.6176 | -1.0472 | 121.5843 | 121.6509 | 121.4526 | 120.5204 | -122.2076
430.3594 | 121.7789 | -120.5658 | 1.1627 | 1.4211e-13 | -0.025335 | 0.016389 | -0.0034253 | -0.0099823 | 0.02098 | -0.23296 | -0.0018566 | -0.00098076 | 0.061319 | 0.026461 | 0.060744 | 0.10635 | 0.028878 | 0.032795 | 0.1208 | 0.041569 | 0.22438 | 0.1201 | -120.2405 | -0.082058 | -120.2887 | 1.0964 | 1.1675 | 0.98299 | -120.935 | 120.6859 | -1.0419 | 120.6721 | 120.5986 | -0.087305 | -1.1212 | -0.93834 | -0.36923 | -0.066365 | 0.32534 | 0.2771 | 0.64634 | 0.004794 | -0.17973 | 120.6866 | 120.6074 | 120.7902 | 120.5947 | -1.0426 | 121.6622 | 121.7333 | 121.5488 | 120.4837 | -122.0978
432.1094 | 121.7468 | -120.6299 | 1.1307 | 1.4211e-13 | -0.024908 | 0.015962 | -0.0032117 | -0.0099823 | 0.02098 | -0.23296 | -0.0018566 | -0.00098076 | 0.061319 | 0.026034 | 0.06053 | 0.10635 | 0.0243 | 0.028217 | 0.10707 | 0.027833 | 0.22438 | 0.11094 | -119.7185 | -0.077479 | -119.7713 | 1.6091 | 1.6849 | 1.4821 | -120.4222 | 120.7408 | -1.0236 | 120.7362 | 120.6581 | -0.082725 | -1.1028 | -0.9063 | 0.20768 | 0.47847 | 0.9114 | 0.85858 | 0.6509 | 0.55422 | 0.35139 | 120.737 | 120.6577 | 120.8543 | 120.6542 | -1.0197 | 122.239 | 122.3148 | 122.1119 | 120.5524 | -121.5529
433.8438 | 121.8292 | -119.9066 | 1.8402 | 1.4211e-13 | -0.025122 | 0.015748 | -0.0034253 | -0.010196 | 0.021193 | -0.23296 | -0.0018566 | -0.00076696 | 0.061533 | 0.026248 | 0.060744 | 0.10635 | 0.028878 | 0.032795 | 0.11165 | 0.027833 | 0.22438 | 0.10636 | -119.6315 | -0.0729 | -119.6889 | 1.7007 | 1.7765 | 1.5828 | -120.3306 | 120.013 | -1.7286 | 120.013 | 119.9394 | -0.073568 | -1.8124 | -1.6158 | -0.42401 | -0.13949 | 0.27513 | 0.21773 | 0.64175 | -0.063742 | -0.25742 | 120.0183 | 119.9344 | 120.131 | 119.9355 | -1.7338 | 121.6073 | 121.6831 | 121.4894 | 119.8337 | -122.1708
435.5156 | 121.8842 | -121.0007 | 0.71411 | 1.4211e-13 | -0.025335 | 0.015962 | -0.0034253 | -0.0097687 | 0.020766 | -0.24059 | -0.0018566 | -0.00098076 | 0.061319 | 0.026675 | 0.060744 | 0.11093 | 0.028878 | 0.028217 | 0.11622 | 0.046148 | 0.22438 | 0.12468 | -120.7029 | -0.082058 | -120.7328 | 0.64766 | 0.72339 | 0.52055 | -121.3975 | 121.1253 | -0.59789 | 121.1116 | 121.0289 | -0.096462 | -0.66796 | -0.48973 | -0.39682 | -0.066448 | 0.29777 | 0.26784 | 0.66466 | 0.009279 | -0.19356 | 121.1169 | 121.0468 | 121.2251 | 121.0295 | -0.58943 | 121.6483 | 121.7241 | 121.5212 | 120.9186 | -122.1116
437.25 | 121.8704 | -120.8084 | 0.90637 | 1.4211e-13 | -0.025122 | 0.015962 | -0.0032117 | -0.0097687 | 0.020552 | -0.22533 | -0.0020702 | -0.00098076 | 0.061105 | 0.026034 | 0.060103 | 0.10177 | 0.0243 | 0.028217 | 0.10249 | 0.050727 | 0.2198 | 0.11094 | -120.5106 | -0.086637 | -120.5451 | 0.84912 | 0.91111 | 0.71743 | -121.2006 | 120.9194 | -0.80388 | 120.9102 | 120.8366 | -0.082725 | -0.85564 | -0.68657 | -0.39219 | -0.057255 | 0.29781 | 0.26331 | 0.6555 | 0.004741 | -0.18894 | 120.9109 | 120.8591 | 121.0282 | 120.8327 | -0.79543 | 121.6575 | 121.7195 | 121.5258 | 120.7218 | -122.107
438.9844 | 121.7972 | -121.2479 | 0.49896 | 1.4211e-13 | -0.024908 | 0.016175 | -0.0034253 | -0.0097687 | 0.021193 | -0.23296 | -0.001643 | -0.00098076 | 0.061533 | 0.026248 | 0.06053 | 0.10177 | 0.033457 | 0.037373 | 0.11622 | 0.046148 | 0.22896 | 0.11094 | -120.9227 | -0.091215 | -120.9572 | 0.43247 | 0.50362 | 0.30078 | -121.6219 | 121.3588 | -0.38274 | 121.3496 | 121.2852 | -0.073569 | -0.45281 | -0.27 | -0.37399 | -0.066488 | 0.32518 | 0.29068 | 0.66467 | 0.004655 | -0.19818 | 121.3641 | 121.294 | 121.4768 | 121.2813 | -0.38802 | 121.6803 | 121.7515 | 121.5486 | 121.1566 | -122.1208
440.7188 | 121.9162 | -121.2067 | 0.48065 | 1.4211e-13 | -0.025122 | 0.016175 | -0.0032117 | -0.0099823 | 0.020766 | -0.23296 | -0.001643 | -0.00098076 | 0.061533 | 0.026675 | 0.060744 | 0.11093 | 0.028878 | 0.032795 | 0.10707 | 0.03699 | 0.22438 | 0.1201 | -120.9089 | -0.086637 | -120.9526 | 0.4279 | 0.49904 | 0.30536 | -121.6127 | 121.3268 | -0.37358 | 121.3176 | 121.2395 | -0.087305 | -0.44366 | -0.25627 | -0.40603 | -0.052757 | 0.29772 | 0.25406 | 0.66009 | 0.018386 | -0.17529 | 121.3137 | 121.2437 | 121.431 | 121.2355 | -0.36055 | 121.6346 | 121.7057 | 121.512 | 121.12 | -122.0933
442.3906 | 121.7789 | -121.4172 | 0.36163 | 1.4211e-13 | -0.025122 | 0.015748 | -0.0032117 | -0.0097687 | 0.02098 | -0.23296 | -0.0020702 | -0.0011944 | 0.061319 | 0.026675 | 0.060103 | 0.10177 | 0.033457 | 0.032795 | 0.11622 | 0.023254 | 0.22438 | 0.092626 | -121.06 | -0.082058 | -121.1037 | 0.29512 | 0.36168 | 0.19547 | -121.7684 | 121.5099 | -0.24541 | 121.519 | 121.45 | -0.059831 | -0.33838 | -0.13725 | -0.35114 | -0.066514 | 0.3572 | 0.31353 | 0.66467 | 4.7e-05 | -0.16616 | 121.5335 | 121.4405 | 121.6416 | 121.4507 | -0.26901 | 121.7124 | 121.7789 | 121.6127 | 121.3352 | -122.13
444.0781 | 121.788 | -121.4218 | 0.37537 | 1.4211e-13 | -0.025122 | 0.015748 | -0.0032117 | -0.0099823 | 0.021407 | -0.23296 | -0.001643 | -0.0011944 | 0.061533 | 0.026248 | 0.060316 | 0.10177 | 0.033457 | 0.023639 | 0.10249 | 0.046148 | 0.22438 | 0.083468 | -121.0738 | -0.091215 | -121.1174 | 0.26765 | 0.33421 | 0.18174 | -121.7821 | 121.5053 | -0.27288 | 121.5236 | 121.4455 | -0.059829 | -0.32922 | -0.15098 | -0.3603 | -0.10772 | 0.34804 | 0.30437 | 0.66467 | -0.041157 | -0.19363 | 121.5243 | 121.468 | 121.6462 | 121.4553 | -0.2919 | 121.6895 | 121.756 | 121.6036 | 121.3306 | -122.1575
445.8281 | 121.8246 | -121.1838 | 0.55847 | 1.4211e-13 | -0.025335 | 0.015962 | -0.0034253 | -0.010196 | 0.021407 | -0.24059 | -0.0022838 | -0.00076696 | 0.060892 | 0.026248 | 0.06053 | 0.097194 | 0.028878 | 0.032795 | 0.10707 | 0.041569 | 0.22438 | 0.042258 | -120.9776 | -0.077479 | -121.0213 | 0.37295 | 0.4441 | 0.26415 | -121.6722 | 121.226 | -0.4514 | 121.281 | 121.2166 | -0.009463 | -0.5169 | -0.33409 | -0.48844 | -0.18552 | 0.20615 | 0.16249 | 0.65093 | -0.11438 | -0.29432 | 121.2908 | 121.2253 | 121.4082 | 121.2127 | -0.51621 | 121.5567 | 121.6279 | 121.4479 | 121.1063 | -122.2307
447.5625 | 121.6003 | -121.3989 | 0.17853 | 1.4211e-13 | -0.025335 | 0.015748 | -0.0036391 | -0.01041 | 0.020766 | -0.23296 | -0.0018566 | -0.00098076 | 0.061319 | 0.026248 | 0.060316 | 0.10635 | 0.028878 | 0.037373 | 0.11622 | 0.041569 | 0.22438 | 0.092626 | -118.2396 | -0.20568 | -118.2878 | 2.7858 | 2.8479 | 2.7824 | -118.9524 | 121.4916 | -0.062303 | 121.5053 | 121.4363 | -0.055253 | -0.13696 | 0.045853 | 2.4465 | 2.6073 | 3.1594 | 3.1111 | 0.66461 | 2.6693 | 2.6039 | 121.5152 | 121.4405 | 121.6233 | 121.4278 | -0.085902 | 124.1847 | 124.2468 | 124.1813 | 121.1932 | -119.1309
449.2344 | 121.788 | -121.5866 | 0.16479 | 1.4211e-13 | -0.025335 | 0.015748 | -0.0034253 | -0.0099823 | 0.020766 | -0.23296 | -0.0018566 | -0.0011944 | 0.061105 | 0.026675 | 0.060316 | 0.097194 | 0.0243 | 0.023639 | 0.10707 | 0.041569 | 0.2198 | 0.11552 | -121.234 | -0.091215 | -121.2777 | 0.093665 | 0.16022 | 0.168 | -121.9424 | 121.7021 | -0.057727 | 121.6838 | 121.6102 | -0.091882 | -0.12323 | 0.055007 | -0.35576 | -0.07113 | 0.35258 | 0.30891 | 0.66468 | -0.004573 | 0.003207 | 121.6937 | 121.6282 | 121.8064 | 121.6109 | -0.049274 | 121.6803 | 121.7468 | 121.7546 | 121.4954 | -122.1072
450.9844 | 121.7697 | -121.5866 | 0.16937 | 1.4211e-13 | -0.025122 | 0.015962 | -0.0032117 | -0.0097687 | 0.02098 | -0.23296 | -0.0020702 | -0.00098076 | 0.061319 | 0.026675 | 0.060316 | 0.10177 | 0.019721 | 0.01906 | 0.10707 | 0.004938 | 0.22438 | 0.1201 | -121.2432 | -0.086637 | -121.2823 | 0.089087 | 0.16022 | 0.17716 | -121.9424 | 121.7067 | -0.062305 | 121.6884 | 121.6057 | -0.10104 | -0.16443 | 0.055008 | -0.35576 | -0.080286 | 0.34342 | 0.30434 | 0.6601 | -0.009151 | 0.007786 | 121.6937 | 121.5915 | 121.811 | 121.6063 | -0.049273 | 121.6757 | 121.7468 | 121.7638 | 121.5 | -122.1117
452.6719 | 121.8613 | -121.55 | 0.14648 | 1.4211e-13 | -0.025335 | 0.015748 | -0.0034253 | -0.0099823 | 0.020766 | -0.21007 | -0.0018566 | -0.00098076 | 0.061319 | 0.026461 | 0.06053 | 0.10177 | 0.015142 | 0.023639 | 0.11165 | 0.03699 | 0.2198 | 0.11094 | -121.2478 | -0.086637 | -121.2869 | 0.084508 | 0.1648 | -0.13419 | -121.947 | 121.6609 | -0.034837 | 121.6518 | 121.5736 | -0.087303 | -0.10949 | 0.073318 | -0.39696 | -0.061976 | 0.30222 | 0.26314 | 0.6601 | 0.018316 | -0.28067 | 121.6616 | 121.587 | 121.7698 | 121.5651 | -0.035542 | 121.6345 | 121.7148 | 121.4158 | 121.4634 | -122.0934
454.4062 | 121.7972 | -121.5866 | 0.1831 | 1.4211e-13 | -0.025335 | 0.015748 | -0.0029979 | -0.0097687 | 0.020552 | -0.22533 | -0.0020702 | -0.00076696 | 0.061105 | 0.026675 | 0.060316 | 0.10177 | 0.019721 | 0.023639 | 0.10707 | 0.014096 | 0.22438 | 0.10636 | -121.234 | -0.086637 | -121.2914 | 0.098244 | 0.1648 | -0.13876 | -121.9515 | 121.693 | -0.076037 | 121.6884 | 121.6102 | -0.082724 | -0.16901 | 0.041276 | -0.36492 | -0.084861 | 0.35258 | 0.29518 | 0.6601 | -0.018305 | -0.32187 | 121.6937 | 121.6007 | 121.811 | 121.6063 | -0.076742 | 121.6849 | 121.7514 | 121.4478 | 121.5 | -122.1346
456.1562 | 121.7606 | -121.5866 | 0.19226 | 1.4211e-13 | -0.025122 | 0.016175 | -0.0034253 | -0.0099823 | 0.020766 | -0.23296 | -0.0018566 | -0.00098076 | 0.061105 | 0.026461 | 0.06053 | 0.11093 | 0.019721 | 0.01906 | 0.11165 | 0.027833 | 0.22438 | 0.11552 | -121.2386 | -0.091215 | -121.2914 | 0.093665 | 0.16022 | -0.13419 | -121.9561 | 121.7021 | -0.080614 | 121.6975 | 121.6057 | -0.096461 | -0.16443 | 0.03212 | -0.3695 | -0.098596 | 0.348 | 0.29518 | 0.66468 | -0.032039 | -0.32645 | 121.6983 | 121.6144 | 121.811 | 121.6063 | -0.07674 | 121.6803 | 121.7468 | 121.4524 | 121.4954 | -122.1484
457.9062 | 121.8338 | -121.5729 | 0.16479 | 1.4211e-13 | -0.024908 | 0.016389 | -0.0036391 | -0.010196 | 0.020766 | -0.22533 | -0.0018566 | -0.00076696 | 0.061319 | 0.026675 | 0.060103 | 0.10177 | 0.015142 | 0.028217 | 0.097912 | 0.032411 | 0.2198 | 0.10636 | -121.2478 | -0.095794 | -121.2777 | 0.098244 | 0.15564 | -0.13876 | -121.9607 | 121.6792 | -0.066883 | 121.6746 | 121.6011 | -0.078146 | -0.13238 | 0.055007 | -0.38781 | -0.066551 | 0.32511 | 0.29518 | 0.68299 | -0.009152 | -0.30356 | 121.6708 | 121.6053 | 121.7927 | 121.588 | -0.058432 | 121.6711 | 121.7285 | 121.4341 | 121.4771 | -122.1255
459.5938 | 121.7789 | -121.5866 | 0.17395 | 1.4211e-13 | -0.025122 | 0.015962 | -0.0032117 | -0.0099823 | 0.020339 | -0.23296 | -0.0022838 | -0.00098076 | 0.061319 | 0.026461 | 0.06053 | 0.097194 | 0.010564 | 0.023639 | 0.10249 | 0.023254 | 0.22438 | 0.11552 | -121.2523 | -0.086637 | -121.2914 | 0.098244 | 0.15564 | -0.13876 | -121.9607 | 121.7021 | -0.07146 | 121.6838 | 121.6102 | -0.091882 | -0.1507 | 0.050431 | -0.37408 | -0.075706 | 0.33426 | 0.29518 | 0.66925 | -0.018307 | -0.31271 | 121.6891 | 121.6099 | 121.811 | 121.5972 | -0.058429 | 121.6849 | 121.7423 | 121.4478 | 121.5 | -122.1346
461.3438 | 121.843 | -121.5729 | 0.16479 | 1.4211e-13 | -0.025122 | 0.016175 | -0.0032117 | -0.0099823 | 0.020766 | -0.22533 | -0.0018566 | -0.0011944 | 0.061319 | 0.026461 | 0.06053 | 0.097194 | 0.019721 | 0.014482 | 0.11165 | 0.023254 | 0.2198 | 0.1201 | -121.2478 | -0.086637 | -121.296 | 0.098244 | 0.1648 | -0.13419 | -121.9561 | 121.693 | -0.053148 | 121.6701 | 121.5874 | -0.10562 | -0.14154 | 0.055007 | -0.38323 | -0.066551 | 0.32511 | 0.27687 | 0.6601 | 5e-06 | -0.29898 | 121.6845 | 121.5961 | 121.7927 | 121.5926 | -0.044695 | 121.6711 | 121.7377 | 121.4387 | 121.4862 | -122.1209
463.0156 | 121.9116 | -121.5408 | 0.13733 | 1.4211e-13 | -0.025335 | 0.016175 | -0.0034253 | -0.010196 | 0.020552 | -0.23296 | -0.0018566 | -0.00055336 | 0.061319 | 0.026461 | 0.060316 | 0.10635 | 0.015142 | 0.023639 | 0.10707 | 0.046148 | 0.21522 | 0.11552 | -121.2569 | -0.095794 | -121.296 | 0.093665 | 0.15107 | -0.13876 | -121.9607 | 121.6564 | -0.030261 | 121.6472 | 121.5645 | -0.091882 | -0.091181 | 0.077895 | -0.41985 | -0.043664 | 0.28391 | 0.24482 | 0.66468 | 0.013736 | -0.27609 | 121.6479 | 121.587 | 121.7561 | 121.556 | -0.021808 | 121.6345 | 121.6919 | 121.4021 | 121.445 | -122.098
464.75 | 121.7743 | -121.5729 | 0.18768 | 1.4211e-13 | -0.025335 | 0.015748 | -0.0029979 | -0.010196 | 0.02098 | -0.22533 | -0.0022838 | -0.00098076 | 0.061319 | 0.026675 | 0.060103 | 0.11093 | 0.019721 | 0.023639 | 0.11165 | 0.041569 | 0.21522 | 0.11094 | -121.2523 | -0.086637 | -121.3052 | 0.089087 | 0.16022 | -0.14334 | -121.9607 | 121.6838 | -0.076036 | 121.6838 | 121.5965 | -0.087303 | -0.14611 | 0.027541 | -0.38781 | -0.098596 | 0.32053 | 0.26771 | 0.65552 | -0.027461 | -0.33103 | 121.6845 | 121.6144 | 121.7881 | 121.5926 | -0.076741 | 121.662 | 121.7331 | 121.4295 | 121.4862 | -122.1484
466.4844 | 121.8521 | -121.6187 | 0.16022 | 1.4211e-13 | -0.025335 | 0.015962 | -0.0032117 | -0.010196 | 0.020766 | -0.22533 | -0.0018566 | -0.0011944 | -0.0036299 | 0.026889 | 0.011604 | 0.10635 | 0.0243 | 0.023639 | 0.097912 | 0.009517 | 0.2198 | 0.11094 | 0.019362 | 0.1194 | -0.070087 | 0.098244 | 0.15564 | 0.18174 | -0.20078 | 121.7296 | -0.062305 | 121.725 | 121.6423 | -0.087303 | -0.1507 | 0.059585 | 121.4179 | -0.061973 | 121.638 | 121.5486 | 0.13069 | -0.004574 | 0.021521 | 121.7166 | 121.6282 | 121.8385 | 121.643 | -0.049275 | 121.7169 | 121.7743 | 121.8004 | 121.7381 | -0.361
468.1719 | 121.875 | -121.5637 | 0.13275 | 1.4211e-13 | -0.025549 | 0.015962 | -0.0036391 | -0.0097687 | 0.02098 | -0.22533 | -0.001643 | -0.0011944 | -0.0029889 | 0.026889 | 0.011604 | 0.10177 | 0.015142 | 0.028217 | 0.10249 | 0.027833 | 0.22438 | 0.11094 | 0.097201 | 0.091933 | 0.01233 | 0.084508 | 0.1648 | 0.168 | -0.08173 | 121.6747 | -0.030261 | 121.6655 | 121.5919 | -0.082725 | -0.10492 | 0.09163 | 121.482 | -0.048243 | 121.6609 | 121.5761 | 0.09406 | 0.032049 | 0.035251 | 121.6662 | 121.5916 | 121.7881 | 121.5789 | -0.021809 | 121.6482 | 121.7285 | 121.7317 | 121.6557 | -0.21448
469.8906 | 121.8658 | -121.5683 | 0.15106 | 1.4211e-13 | -0.025122 | 0.016175 | -0.0034253 | -0.010196 | 0.02098 | -0.24059 | -0.0018566 | -0.0011944 | -0.0038435 | 0.026889 | 0.011604 | 0.10635 | 0.015142 | 0.028217 | 0.10249 | 0.032411 | 0.21522 | 0.11094 | 0.10636 | 0.06904 | 0.01233 | 0.089087 | 0.16022 | 0.168 | -0.067994 | 121.6792 | -0.048572 | 121.6746 | 121.5965 | -0.082725 | -0.11865 | 0.064162 | 121.5003 | -0.061975 | 121.6747 | 121.5806 | 0.080324 | 0.00916 | 0.01694 | 121.6708 | 121.6007 | 121.7835 | 121.5834 | -0.04012 | 121.6574 | 121.7285 | 121.7363 | 121.6373 | -0.21906
471.5781 | 121.7606 | -121.6095 | 0.16937 | 1.4211e-13 | -0.025549 | 0.015962 | -0.0034253 | -0.0099823 | 0.020552 | -0.23296 | -0.0020702 | -0.001408 | -0.0034163 | 0.026889 | 0.011604 | 0.10177 | 0.019721 | 0.028217 | 0.10707 | 0.032411 | 0.21064 | 0.10636 | 0.10636 | 0.036989 | 0.026066 | 0.093665 | 0.16938 | -0.13876 | -0.054257 | 121.7159 | -0.062305 | 121.7113 | 121.6377 | -0.078146 | -0.13696 | 0.041272 | 121.5552 | -0.075708 | 121.7159 | 121.6356 | 0.080323 | 6e-06 | -0.30814 | 121.7166 | 121.6419 | 121.8201 | 121.6292 | -0.06301 | 121.7032 | 121.7789 | 121.4707 | 121.6465 | -0.22363
473.25 | 121.8018 | -121.6049 | 0.17395 | 1.4211e-13 | -0.025549 | 0.016175 | -0.0034253 | -0.0099823 | 0.020552 | -0.2177 | -0.001643 | -0.0011944 | -0.0036299 | 0.026889 | 0.011604 | 0.092615 | 0.0243 | 0.028217 | 0.10707 | 0.027833 | 0.21522 | 0.11552 | 0.11094 | 0.036989 | 0.021487 | 0.098244 | 0.16938 | -0.14334 | -0.058836 | 121.7204 | -0.066882 | 121.6975 | 121.6331 | -0.087304 | -0.14612 | 0.041274 | 121.5461 | -0.075706 | 121.7159 | 121.6264 | 0.080323 | -0.004571 | -0.31729 | 121.712 | 121.6328 | 121.8201 | 121.6292 | -0.058429 | 121.7032 | 121.7743 | 121.4616 | 121.6419 | -0.23279
474.9844 | 121.8521 | -121.5729 | 0.15106 | 1.4211e-13 | -0.025549 | 0.015962 | -0.0036391 | -0.010196 | 0.020766 | -0.23296 | -0.0018566 | -0.00098076 | -0.0034163 | 0.026889 | 0.011176 | 0.097194 | 0.015142 | 0.028217 | 0.10249 | 0.023254 | 0.22438 | 0.11552 | 0.11094 | 0.023253 | 0.021487 | 0.093665 | 0.1648 | -0.13876 | -0.0451 | 121.6884 | -0.048572 | 121.6701 | 121.6011 | -0.087304 | -0.12781 | 0.073319 | 121.5278 | -0.057397 | 121.6838 | 121.5944 | 0.066587 | 0.013738 | -0.28983 | 121.6754 | 121.5961 | 121.7973 | 121.588 | -0.035541 | 121.6665 | 121.7377 | 121.4341 | 121.5961 | -0.19616
476.6562 | 121.8567 | -121.5775 | 0.16937 | 1.4211e-13 | -0.025976 | 0.015748 | -0.0036391 | -0.010196 | 0.02098 | -0.24822 | -0.0020702 | -0.00076696 | -0.0034163 | 0.027102 | 0.011604 | 0.097194 | 0.019721 | 0.032795 | 0.10707 | 0.018675 | 0.22438 | 0.11094 | 0.11094 | 0.018674 | 0.021487 | 0.098244 | 0.1648 | -0.13876 | -0.0451 | 121.6884 | -0.062305 | 121.6746 | 121.6102 | -0.078147 | -0.1507 | 0.055008 | 121.5324 | -0.071129 | 121.6884 | 121.5989 | 0.066587 | -0.004573 | -0.30814 | 121.6845 | 121.5961 | 121.8018 | 121.5972 | -0.058431 | 121.6757 | 121.7423 | 121.4387 | 121.5961 | -0.21447
478.3906 | 121.7972 | -121.6003 | 0.1831 | 1.4211e-13 | -0.025549 | 0.015962 | -0.0034253 | -0.010623 | 0.020766 | -0.23296 | -0.0020702 | -0.00076696 | -0.0036299 | 0.027102 | 0.011176 | 0.10177 | 0.0243 | 0.037373 | 0.10249 | 0.041569 | 0.21522 | 0.1201 | 0.10636 | 0.018674 | 0.021487 | 0.098244 | 0.16938 | -0.13419 | -0.026784 | 121.7204 | -0.080615 | 121.7021 | 121.6377 | -0.082727 | -0.14154 | 0.032119 | 121.5736 | -0.084861 | 121.7067 | 121.6218 | 0.048271 | -0.013726 | -0.31729 | 121.7028 | 121.6419 | 121.8156 | 121.6246 | -0.063005 | 121.6986 | 121.7697 | 121.4662 | 121.619 | -0.20989
480.125 | 121.8201 | -121.6095 | 0.17853 | 1.4211e-13 | -0.025122 | 0.015534 | -0.0034253 | -0.01041 | 0.02098 | -0.24059 | -0.0020702 | -0.00098076 | -0.0034163 | 0.026889 | 0.01139 | 0.097194 | 0.0243 | 0.032795 | 0.11165 | 0.018675 | 0.2198 | 0.11552 | 0.11094 | 0.018674 | 0.016908 | 0.093665 | 0.15564 | -0.12503 | -0.049678 | 121.725 | -0.066881 | 121.7067 | 121.6423 | -0.082726 | -0.15985 | 0.041274 | 121.5598 | -0.084863 | 121.7204 | 121.6264 | 0.066586 | -0.022885 | -0.30356 | 121.7211 | 121.6282 | 121.8293 | 121.6338 | -0.063007 | 121.7032 | 121.7651 | 121.4845 | 121.6282 | -0.22821
481.875 | 121.7926 | -121.6095 | 0.16937 | 1.4211e-13 | -0.025335 | 0.015534 | -0.0034253 | -0.010196 | 0.020766 | -0.22533 | -0.001643 | -0.00076696 | -0.0036299 | 0.027102 | 0.01139 | 0.083459 | 0.0243 | 0.032795 | 0.10707 | 0.027833 | 0.21522 | 0.1201 | 0.10636 | 0.023253 | 0.021487 | 0.093665 | 0.16938 | -0.14334 | -0.0451 | 121.7296 | -0.062305 | 121.693 | 121.6423 | -0.087305 | -0.14154 | 0.045851 | 121.5644 | -0.075708 | 121.7159 | 121.631 | 0.066587 | 6e-06 | -0.31272 | 121.7166 | 121.6373 | 121.8247 | 121.6338 | -0.049273 | 121.7032 | 121.7789 | 121.4662 | 121.6328 | -0.21447
483.5625 | 121.9299 | -121.5546 | 0.14648 | 1.4211e-13 | -0.025763 | 0.016175 | -0.0032117 | -0.010196 | 0.020766 | -0.23296 | -0.0020702 | -0.00098076 | -0.0032025 | 0.027102 | 0.01139 | 0.083459 | 0.019721 | 0.028217 | 0.10707 | 0.027833 | 0.2198 | 0.11552 | 0.11552 | 0.014095 | 0.021487 | 0.089087 | 0.16022 | -0.13419 | -0.040521 | 121.6701 | -0.039416 | 121.638 | 121.5828 | -0.087304 | -0.11865 | 0.073318 | 121.514 | -0.057397 | 121.6701 | 121.5761 | 0.062008 | 0.013738 | -0.28067 | 121.6616 | 121.5824 | 121.7744 | 121.5743 | -0.030963 | 121.6437 | 121.7148 | 121.4204 | 121.5687 | -0.18701
485.2969 | 121.843 | -121.6003 | 0.16479 | 1.4211e-13 | -0.025335 | 0.015748 | -0.0034253 | -0.01041 | 0.020339 | -0.24059 | -0.0020702 | -0.00098076 | -0.0036299 | 0.026675 | 0.011604 | 0.083459 | 0.019721 | 0.032795 | 0.10249 | 0.032411 | 0.2198 | 0.11094 | 0.11552 | 0.023253 | 0.021487 | 0.093665 | 0.16022 | -0.13419 | -0.035942 | 121.7113 | -0.062305 | 121.6838 | 121.6331 | -0.078147 | -0.13238 | 0.055007 | 121.5644 | -0.07113 | 121.7159 | 121.6218 | 0.057429 | -0.004573 | -0.29898 | 121.7028 | 121.6328 | 121.8201 | 121.6201 | -0.053853 | 121.694 | 121.7606 | 121.4662 | 121.6236 | -0.20074
487.0312 | 121.8018 | -121.6187 | 0.15564 | 1.4211e-13 | -0.025549 | 0.016175 | -0.0032117 | -0.01041 | 0.020766 | -0.22533 | -0.0014292 | -0.0011944 | -0.0036299 | 0.026889 | 0.011176 | 0.074302 | 0.019721 | 0.032795 | 0.10249 | 0.027833 | 0.21522 | 0.11094 | 0.11094 | 0.018674 | 0.026066 | 0.089087 | 0.16022 | -0.14334 | -0.031363 | 121.7296 | -0.05315 | 121.693 | 121.6514 | -0.078147 | -0.12781 | 0.059584 | 121.5873 | -0.066553 | 121.7296 | 121.6447 | 0.057429 | 0.004582 | -0.29898 | 121.7211 | 121.6465 | 121.8339 | 121.6384 | -0.044698 | 121.7077 | 121.7789 | 121.4753 | 121.6373 | -0.187
488.7031 | 121.9254 | -121.5683 | 0.14191 | 1.4211e-13 | -0.025763 | 0.015748 | -0.0034253 | -0.010196 | 0.020766 | -0.23296 | -0.0018566 | -0.0011944 | -0.0032025 | 0.027316 | 0.01139 | 0.083459 | 0.019721 | 0.032795 | 0.10249 | 0.03699 | 0.22438 | 0.11552 | 0.097201 | 0.014095 | 0.039802 | 0.098244 | 0.1648 | -0.13419 | -0.035942 | 121.6838 | -0.039417 | 121.6518 | 121.6011 | -0.082726 | -0.10492 | 0.082474 | 121.5324 | -0.043663 | 121.6655 | 121.6081 | 0.075744 | 0.022893 | -0.27609 | 121.6708 | 121.6053 | 121.7927 | 121.588 | -0.026386 | 121.6665 | 121.7331 | 121.4341 | 121.5824 | -0.17785
490.4375 | 121.9299 | -121.582 | 0.15564 | 1.4211e-13 | -0.025549 | 0.015534 | -0.0034253 | -0.010196 | 0.020552 | -0.22533 | -0.0018566 | -0.00098076 | -0.0034163 | 0.027102 | 0.01139 | 0.074302 | 0.019721 | 0.037373 | 0.10249 | 0.050727 | 0.22438 | 0.11552 | 0.097201 | 0.009516 | 0.030644 | 0.10282 | 0.16938 | -0.12503 | -0.035942 | 121.6976 | -0.05315 | 121.6563 | 121.6194 | -0.078148 | -0.10491 | 0.068741 | 121.5461 | -0.052818 | 121.6792 | 121.6127 | 0.066586 | 0.013739 | -0.28067 | 121.6845 | 121.6328 | 121.8064 | 121.6018 | -0.040119 | 121.6849 | 121.7514 | 121.457 | 121.5915 | -0.19158
492.1094 | 121.8063 | -121.6187 | 0.20142 | 1.4211e-13 | -0.025335 | 0.015534 | -0.0034253 | -0.010623 | 0.02098 | -0.24059 | -0.0018566 | -0.00098076 | -0.0034163 | 0.027102 | 0.011604 | 0.07888 | 0.019721 | 0.041952 | 0.11165 | 0.000359 | 0.22438 | 0.11094 | 0.10636 | 0.009516 | 0.030644 | 0.093665 | 0.1648 | -0.13419 | -0.022205 | 121.7296 | -0.089769 | 121.6975 | 121.6606 | -0.06899 | -0.20106 | 0.022965 | 121.5964 | -0.10775 | 121.725 | 121.6493 | 0.052849 | -0.036616 | -0.3356 | 121.7303 | 121.619 | 121.843 | 121.6384 | -0.090474 | 121.7123 | 121.7835 | 121.4845 | 121.6282 | -0.22362
493.8438 | 121.8292 | -121.6187 | 0.16937 | 1.4211e-13 | -0.025549 | 0.015962 | -0.0036391 | -0.01041 | 0.020339 | -0.22533 | -0.0022838 | -0.00098076 | -0.0036299 | 0.026675 | 0.01139 | 0.074302 | 0.015142 | 0.032795 | 0.10249 | 0.046148 | 0.21522 | 0.11552 | 0.10636 | 0.000359 | 0.030644 | 0.098244 | 0.1648 | -0.13876 | -0.031363 | 121.7342 | -0.066883 | 121.693 | 121.6514 | -0.082726 | -0.12323 | 0.045851 | 121.5873 | -0.071129 | 121.725 | 121.6493 | 0.062007 | -0.004573 | -0.30814 | 121.7211 | 121.6648 | 121.8339 | 121.6338 | -0.053852 | 121.7169 | 121.7835 | 121.4799 | 121.619 | -0.20074
495.5938 | 121.8384 | -121.6324 | 0.15106 | 1.4211e-13 | -0.025549 | 0.015962 | -0.0036391 | -0.01041 | 0.020766 | -0.23296 | -0.0018566 | -0.00098076 | -0.0034163 | 0.027102 | 0.011176 | 0.074302 | 0.0243 | 0.032795 | 0.10249 | 0.03699 | 0.21522 | 0.11552 | 0.10178 | 0.000359 | 0.035223 | 0.098244 | 0.17396 | -0.13876 | -0.031363 | 121.7479 | -0.048572 | 121.7067 | 121.6652 | -0.082726 | -0.11407 | 0.064162 | 121.601 | -0.052818 | 121.7342 | 121.6676 | 0.066586 | 0.022896 | -0.28983 | 121.7349 | 121.6694 | 121.8476 | 121.6567 | -0.035541 | 121.7306 | 121.8063 | 121.4936 | 121.6327 | -0.18243
497.2812 | 121.9391 | -121.582 | 0.14648 | 1.4211e-13 | -0.025763 | 0.015962 | -0.0034253 | -0.010196 | 0.02098 | -0.23296 | -0.0020702 | -0.00076696 | -0.0034163 | 0.026889 | 0.011176 | 0.083459 | 0.019721 | 0.037373 | 0.10707 | 0.023254 | 0.21522 | 0.1201 | 0.097201 | 0.004938 | 0.039802 | 0.093665 | 0.17396 | -0.13419 | -0.026784 | 121.7021 | -0.039416 | 121.6655 | 121.6194 | -0.082727 | -0.12323 | 0.06874 | 121.5552 | -0.052819 | 121.6792 | 121.6218 | 0.066586 | 0.027474 | -0.28067 | 121.6891 | 121.6053 | 121.7973 | 121.6018 | -0.026384 | 121.6757 | 121.756 | 121.4478 | 121.587 | -0.17327
499.0156 | 121.8201 | -121.6049 | 0.17395 | 1.4211e-13 | -0.025549 | 0.015748 | -0.0032117 | -0.01041 | 0.020552 | -0.23296 | -0.0020702 | -0.00098076 | -0.0036299 | 0.026889 | 0.011176 | 0.07888 | 0.015142 | 0.037373 | 0.11622 | 0.009517 | 0.22438 | 0.11552 | 0.097201 | 0.000359 | 0.030644 | 0.093665 | 0.1648 | -0.13876 | -0.026784 | 121.7204 | -0.057725 | 121.6838 | 121.6423 | -0.078148 | -0.16443 | 0.050431 | 121.5781 | -0.080285 | 121.7021 | 121.6356 | 0.057428 | -0.00915 | -0.31271 | 121.7211 | 121.6144 | 121.8293 | 121.6201 | -0.058429 | 121.6986 | 121.7697 | 121.4662 | 121.6053 | -0.20073
500.7656 | 121.9437 | -121.582 | 0.13733 | 1.4211e-13 | -0.025549 | 0.015748 | -0.0029979 | -0.010196 | 0.021193 | -0.24822 | -0.0020702 | -0.0011944 | -0.0032025 | 0.026889 | 0.01139 | 0.083459 | 0.019721 | 0.032795 | 0.097912 | 0.03699 | 0.2198 | 0.11552 | 0.10178 | 0.000359 | 0.035223 | 0.098244 | 0.1648 | -0.13419 | -0.026784 | 121.6976 | -0.039417 | 121.6655 | 121.6148 | -0.082726 | -0.10034 | 0.082473 | 121.5552 | -0.039085 | 121.6838 | 121.6173 | 0.062007 | 0.027471 | -0.27152 | 121.6799 | 121.619 | 121.8018 | 121.6018 | -0.021808 | 121.6803 | 121.7468 | 121.4478 | 121.5824 | -0.16411
502.4531 | 121.9391 | -121.5683 | 0.14191 | 1.4211e-13 | -0.025763 | 0.015748 | -0.0036391 | -0.010196 | 0.020552 | -0.23296 | -0.0018566 | -0.00098076 | -0.0036299 | 0.026889 | 0.01139 | 0.07888 | 0.0243 | 0.037373 | 0.10249 | 0.018675 | 0.21522 | 0.11552 | 0.10636 | 0.004938 | 0.035223 | 0.10282 | 0.16938 | -0.14334 | -0.026784 | 121.6838 | -0.039417 | 121.6472 | 121.6057 | -0.078148 | -0.12323 | 0.073317 | 121.5415 | -0.039085 | 121.6747 | 121.6035 | 0.062007 | 0.027472 | -0.28525 | 121.6708 | 121.587 | 121.7835 | 121.5926 | -0.026386 | 121.6711 | 121.7377 | 121.425 | 121.5732 | -0.16869
504.1875 | 121.8658 | -121.5912 | 0.16022 | 1.4211e-13 | -0.025763 | 0.015748 | -0.0034253 | -0.01041 | 0.020552 | -0.23296 | -0.0020702 | -0.001408 | -0.0036299 | 0.027102 | 0.01139 | 0.083459 | 0.0243 | 0.028217 | 0.11165 | 0.018675 | 0.2198 | 0.1201 | 0.097201 | 0.004938 | 0.030644 | 0.098244 | 0.17396 | -0.13876 | -0.022205 | 121.7113 | -0.04857 | 121.6746 | 121.6194 | -0.091883 | -0.14154 | 0.059585 | 121.569 | -0.061973 | 121.6884 | 121.6218 | 0.052849 | 0.013741 | -0.29898 | 121.7028 | 121.6099 | 121.811 | 121.6155 | -0.040117 | 121.6894 | 121.7651 | 121.4524 | 121.5961 | -0.18242
505.9375 | 121.8658 | -121.582 | 0.15564 | 1.4211e-13 | -0.025335 | 0.015748 | -0.0034253 | -0.010196 | 0.020766 | -0.22533 | -0.0020702 | -0.00098076 | -0.0032025 | 0.027102 | 0.01139 | 0.07888 | 0.0243 | 0.037373 | 0.10249 | 0.023254 | 0.21064 | 0.11094 | 0.097201 | 0.000359 | 0.030644 | 0.098244 | 0.16938 | -0.14334 | -0.022205 | 121.693 | -0.05315 | 121.6609 | 121.6194 | -0.073569 | -0.13239 | 0.055005 | 121.5598 | -0.057396 | 121.6792 | 121.6127 | 0.052849 | 0.013739 | -0.29898 | 121.6845 | 121.6053 | 121.7927 | 121.6063 | -0.044698 | 121.6803 | 121.7514 | 121.4387 | 121.5824 | -0.17785
507.6094 | 121.9666 | -121.5729 | 0.14191 | 1.4211e-13 | -0.025549 | 0.015748 | -0.0036391 | -0.010623 | 0.020552 | -0.23296 | -0.0020702 | -0.00076696 | -0.0029889 | 0.02753 | 0.011817 | 0.083459 | 0.028878 | 0.032795 | 0.10707 | 0.018675 | 0.2198 | 0.11094 | 0.097201 | 0.004938 | 0.026066 | 0.093665 | 0.17396 | -0.14334 | -0.022205 | 121.6838 | -0.034839 | 121.6563 | 121.6057 | -0.078147 | -0.12323 | 0.077895 | 121.5507 | -0.048242 | 121.6701 | 121.5989 | 0.048271 | 0.032051 | -0.28525 | 121.6799 | 121.5916 | 121.7927 | 121.6018 | -0.030965 | 121.6665 | 121.7468 | 121.4295 | 121.5778 | -0.16411
509.3438 | 121.9299 | -121.5958 | 0.12817 | 1.4211e-13 | -0.025763 | 0.015534 | -0.0034253 | -0.01041 | 0.021193 | -0.23296 | -0.0018566 | -0.0011944 | -0.0036299 | 0.027316 | 0.01139 | 0.083459 | 0.0243 | 0.041952 | 0.10249 | 0.009517 | 0.22438 | 0.11552 | 0.097201 | 0.000359 | 0.026066 | 0.093665 | 0.15564 | -0.13419 | -0.026784 | 121.7113 | -0.025684 | 121.6792 | 121.6377 | -0.073569 | -0.11866 | 0.096207 | 121.569 | -0.034509 | 121.693 | 121.6218 | 0.05285 | 0.027469 | -0.26236 | 121.6983 | 121.6053 | 121.8201 | 121.6201 | -0.012653 | 121.6894 | 121.7514 | 121.4616 | 121.5961 | -0.15496
511.0781 | 121.9162 | -121.6095 | 0.16479 | 1.4211e-13 | -0.025122 | 0.015748 | -0.0032117 | -0.01041 | 0.020766 | -0.22533 | -0.0020702 | -0.00098076 | -0.0034163 | 0.027316 | 0.011817 | 0.083459 | 0.028878 | 0.037373 | 0.10707 | 0.004938 | 0.21522 | 0.11552 | 0.092622 | 0.004938 | 0.030644 | 0.093665 | 0.1648 | -0.13876 | -0.026784 | 121.725 | -0.057727 | 121.693 | 121.6469 | -0.078148 | -0.15986 | 0.050429 | 121.5827 | -0.07113 | 121.7021 | 121.6401 | 0.057428 | 5e-06 | -0.30356 | 121.7166 | 121.6144 | 121.8247 | 121.6384 | -0.049274 | 121.7032 | 121.7743 | 121.4707 | 121.6144 | -0.19158
512.8281 | 121.7972 | -121.6141 | 0.16022 | 1.4211e-13 | -0.025763 | 0.015748 | -0.0032117 | -0.010196 | 0.020766 | -0.24059 | -0.0020702 | -0.00076696 | -0.0036299 | 0.027102 | 0.01139 | 0.07888 | 0.028878 | 0.032795 | 0.10249 | 0.041569 | 0.2198 | 0.12468 | 0.097201 | 0.000359 | 0.026066 | 0.089087 | 0.1648 | -0.13876 | -0.026784 | 121.7388 | -0.057727 | 121.693 | 121.6469 | -0.091884 | -0.11865 | 0.059585 | 121.5873 | -0.07113 | 121.7113 | 121.6401 | 0.05285 | 0.004583 | -0.29898 | 121.7166 | 121.6556 | 121.8339 | 121.643 | -0.035538 | 121.7032 | 121.7789 | 121.4753 | 121.6144 | -0.187
514.5156 | 121.875 | -121.6049 | 0.15106 | 1.4211e-13 | -0.025549 | 0.015534 | -0.0029979 | -0.010196 | 0.020766 | -0.24822 | -0.0018566 | -0.00098076 | -0.0036299 | 0.02753 | 0.011176 | 0.07888 | 0.019721 | 0.041952 | 0.10707 | 0.041569 | 0.2198 | 0.11094 | 0.097201 | 0.000359 | 0.035223 | 0.093665 | 0.16938 | -0.13876 | -0.017627 | 121.7159 | -0.043994 | 121.6838 | 121.6469 | -0.06899 | -0.10949 | 0.06874 | 121.5873 | -0.057397 | 121.7021 | 121.6401 | 0.05285 | 0.018317 | -0.28983 | 121.712 | 121.6465 | 121.8247 | 121.6246 | -0.04012 | 121.6986 | 121.7743 | 121.4662 | 121.6053 | -0.16869
516.25 | 121.8658 | -121.6141 | 0.16022 | 1.4211e-13 | -0.025549 | 0.015962 | -0.0034253 | -0.01041 | 0.02098 | -0.24059 | -0.0020702 | -0.0011944 | -0.0032025 | 0.02753 | 0.011176 | 0.083459 | 0.015142 | 0.037373 | 0.11622 | 0.004938 | 0.2198 | 0.11552 | 0.074307 | -0.013377 | 0.003172 | 0.098244 | 0.16938 | -0.14334 | -0.040521 | 121.7296 | -0.043992 | 121.6975 | 121.6514 | -0.078148 | -0.15528 | 0.059585 | 121.5736 | -0.061973 | 121.6884 | 121.6172 | 0.043693 | 0.009162 | -0.30356 | 121.7303 | 121.619 | 121.8339 | 121.6292 | -0.044696 | 121.7123 | 121.7835 | 121.4707 | 121.6007 | -0.20074
518 | 121.8933 | -121.6095 | 0.14191 | 1.4211e-13 | -0.025763 | 0.015962 | -0.0036391 | -0.010623 | 0.020552 | -0.23296 | -0.0018566 | -0.00076696 | -0.0034163 | 0.02753 | 0.01139 | 0.07888 | 0.015142 | 0.037373 | 0.10707 | 0.041569 | 0.2198 | 0.1201 | 0.083464 | -0.008798 | 0.003172 | 0.098244 | 0.1648 | -0.13419 | -0.035942 | 121.7296 | -0.034839 | 121.6884 | 121.6469 | -0.082727 | -0.10034 | 0.077895 | 121.5736 | -0.043663 | 121.693 | 121.6127 | 0.039114 | 0.022893 | -0.27609 | 121.7166 | 121.6511 | 121.8293 | 121.6246 | -0.021807 | 121.7077 | 121.7743 | 121.4753 | 121.6007 | -0.17785
519.6719 | 121.907 | -121.6003 | 0.14648 | 1.4211e-13 | -0.025976 | 0.015962 | -0.0029979 | -0.010196 | 0.020552 | -0.23296 | -0.001643 | -0.00076696 | -0.0038435 | 0.02753 | 0.01139 | 0.083459 | 0.019721 | 0.032795 | 0.097912 | 0.041569 | 0.2198 | 0.11552 | 0.083464 | -0.008798 | 0.01233 | 0.098244 | 0.1648 | -0.12961 | -0.031363 | 121.7159 | -0.048572 | 121.6838 | 121.6331 | -0.082726 | -0.10492 | 0.073318 | 121.569 | -0.04824 | 121.6838 | 121.6127 | 0.043693 | 0.018316 | -0.27609 | 121.6983 | 121.6419 | 121.8201 | 121.6201 | -0.030963 | 121.6986 | 121.7651 | 121.4707 | 121.5915 | -0.17785
521.4062 | 121.9482 | -121.5591 | 0.12817 | 1.4211e-13 | -0.025976 | 0.015962 | -0.0034253 | -0.01041 | 0.020766 | -0.22533 | -0.001643 | -0.0011944 | -0.0034163 | 0.027316 | 0.01139 | 0.07888 | 0.015142 | 0.037373 | 0.10249 | 0.018675 | 0.2198 | 0.11094 | 0.078886 | -0.00422 | 0.007751 | 0.10282 | 0.1648 | -0.13419 | -0.040521 | 121.6701 | -0.025684 | 121.638 | 121.5965 | -0.073569 | -0.1095 | 0.091628 | 121.5186 | -0.025352 | 121.638 | 121.5669 | 0.048272 | 0.036626 | -0.26236 | 121.6616 | 121.5778 | 121.7789 | 121.5743 | -0.017232 | 121.662 | 121.7239 | 121.425 | 121.5549 | -0.1687
523.1562 | 121.9574 | -121.5683 | 0.13733 | 1.4211e-13 | -0.025976 | 0.015962 | -0.0029979 | -0.01041 | 0.020552 | -0.23296 | -0.0020702 | -0.00076696 | -0.0034163 | 0.027316 | 0.011176 | 0.07888 | 0.019721 | 0.032795 | 0.10707 | 0.018675 | 0.22438 | 0.11552 | 0.074307 | -0.008798 | 0.01233 | 0.10282 | 0.1648 | -0.12961 | -0.040521 | 121.6838 | -0.030261 | 121.6472 | 121.6011 | -0.082726 | -0.11865 | 0.087052 | 121.5278 | -0.034507 | 121.6426 | 121.5806 | 0.052851 | 0.027471 | -0.26694 | 121.6754 | 121.587 | 121.7927 | 121.588 | -0.021808 | 121.6711 | 121.7331 | 121.4387 | 121.5595 | -0.17785
524.8906 | 121.8933 | -121.6049 | 0.15564 | 1.4211e-13 | -0.025976 | 0.015321 | -0.0034253 | -0.010623 | 0.020766 | -0.23296 | -0.001643 | -0.0011944 | -0.0034163 | 0.027102 | 0.011176 | 0.088037 | 0.0243 | 0.032795 | 0.10707 | 0.027833 | 0.2198 | 0.11094 | 0.074307 | -0.008798 | 0.007751 | 0.10282 | 0.17854 | -0.12503 | -0.040521 | 121.7159 | -0.048572 | 121.693 | 121.6377 | -0.078147 | -0.12781 | 0.064162 | 121.5644 | -0.052818 | 121.6792 | 121.6127 | 0.048272 | 0.022896 | -0.28067 | 121.712 | 121.6328 | 121.8247 | 121.6292 | -0.044698 | 121.7077 | 121.7835 | 121.4799 | 121.5961 | -0.19616
526.5625 | 121.9345 | -121.5454 | 0.12817 | 1.4211e-13 | -0.025763 | 0.015748 | -0.0032117 | -0.010196 | 0.020552 | -0.23296 | -0.0018566 | -0.00098076 | -0.0034163 | 0.027102 | 0.011176 | 0.07888 | 0.0243 | 0.032795 | 0.10707 | 0.027833 | 0.2198 | 0.1201 | 0.074307 | 0.000359 | 0.003172 | 0.1074 | 0.16938 | -0.13876 | -0.026784 | 121.6655 | -0.021106 | 121.6243 | 121.5782 | -0.087305 | -0.10034 | 0.091628 | 121.5186 | -0.020773 | 121.6197 | 121.5486 | 0.029956 | 0.041205 | -0.26694 | 121.6525 | 121.5732 | 121.7652 | 121.5697 | -0.008074 | 121.6528 | 121.7148 | 121.4066 | 121.5458 | -0.15496
528.3125 | 121.8201 | -121.6324 | 0.1831 | 1.4211e-13 | -0.02619 | 0.015748 | -0.0034253 | -0.010196 | 0.020339 | -0.23296 | -0.0018566 | -0.00076696 | -0.0032025 | 0.02753 | 0.010963 | 0.088037 | 0.019721 | 0.037373 | 0.10707 | 0.032411 | 0.22438 | 0.11094 | 0.078886 | 0.000359 | 0.003172 | 0.098244 | 0.17396 | -0.13419 | -0.035942 | 121.7433 | -0.076037 | 121.7204 | 121.6698 | -0.073569 | -0.15069 | 0.041276 | 121.5964 | -0.084861 | 121.7113 | 121.6356 | 0.039114 | -0.009147 | -0.31729 | 121.7395 | 121.6648 | 121.8568 | 121.6521 | -0.072163 | 121.7306 | 121.8063 | 121.4982 | 121.6327 | -0.21905
529.9844 | 121.8475 | -121.6415 | 0.16937 | 1.4211e-13 | -0.025976 | 0.015748 | -0.0034253 | -0.01041 | 0.020339 | -0.23296 | -0.0020702 | -0.00076696 | -0.0036299 | 0.027316 | 0.01139 | 0.074302 | 0.0243 | 0.037373 | 0.10707 | 0.018675 | 0.22438 | 0.11094 | 0.078886 | -0.00422 | 0.01233 | 0.098244 | 0.17854 | -0.12503 | -0.040521 | 121.7525 | -0.062305 | 121.7158 | 121.6789 | -0.073569 | -0.1507 | 0.055008 | 121.601 | -0.071129 | 121.7204 | 121.6539 | 0.052851 | 0.009163 | -0.2944 | 121.7486 | 121.6602 | 121.8659 | 121.6658 | -0.058431 | 121.7398 | 121.8201 | 121.5165 | 121.6373 | -0.20989
531.7188 | 121.8201 | -121.6415 | 0.1831 | 1.4211e-13 | -0.025763 | 0.015534 | -0.0036391 | -0.01041 | 0.020766 | -0.23296 | -0.0020702 | -0.0011944 | -0.0032025 | 0.027316 | 0.010963 | 0.083459 | 0.019721 | 0.028217 | 0.10707 | 0.004938 | 0.22438 | 0.12468 | 0.088043 | -0.008798 | 0.01233 | 0.098244 | 0.17396 | -0.12961 | -0.022205 | 121.7662 | -0.076037 | 121.725 | 121.6698 | -0.096462 | -0.17817 | 0.041276 | 121.6193 | -0.084861 | 121.7296 | 121.6539 | 0.034535 | -0.009147 | -0.31271 | 121.7486 | 121.6465 | 121.8659 | 121.6613 | -0.058426 | 121.7398 | 121.8155 | 121.5119 | 121.6327 | -0.20531
533.4531 | 121.8201 | -121.6324 | 0.17853 | 1.4211e-13 | -0.025976 | 0.015962 | -0.0036391 | -0.010623 | 0.020766 | -0.23296 | -0.001643 | -0.00076696 | -0.0034163 | 0.02753 | 0.011176 | 0.083459 | 0.028878 | 0.032795 | 0.11622 | 0.046148 | 0.22438 | 0.11552 | 0.11094 | 0.004938 | 0.044381 | 0.1074 | 0.16938 | -0.13419 | -0.022205 | 121.7479 | -0.062303 | 121.7158 | 121.6652 | -0.082726 | -0.13238 | 0.045853 | 121.6102 | -0.071127 | 121.7433 | 121.6768 | 0.066586 | -0.009149 | -0.31271 | 121.7486 | 121.6785 | 121.8568 | 121.6613 | -0.063007 | 121.7398 | 121.8018 | 121.4982 | 121.6373 | -0.20073
535.125 | 121.8155 | -121.6232 | 0.1831 | 1.4211e-13 | -0.02619 | 0.015748 | -0.0034253 | -0.01041 | 0.02098 | -0.23296 | -0.0018566 | -0.00055336 | -0.0032025 | 0.02753 | 0.011176 | 0.083459 | 0.0243 | 0.04653 | 0.10707 | 0.023254 | 0.22896 | 0.11094 | 0.097201 | 0.000359 | 0.003172 | 0.10282 | 0.17396 | 0.18632 | -0.1321 | 121.7342 | -0.076037 | 121.7067 | 121.6698 | -0.064412 | -0.15985 | 0.045854 | 121.4911 | -0.080283 | 121.7204 | 121.6264 | 0.13527 | -0.009147 | 0.003211 | 121.7303 | 121.6465 | 121.8522 | 121.6475 | -0.072163 | 121.7261 | 121.7972 | 121.8095 | 121.6236 | -0.3152
536.875 | 121.8246 | -121.6187 | 0.18768 | 1.4211e-13 | -0.02619 | 0.015748 | -0.0038527 | -0.01041 | 0.020766 | -0.23296 | -0.0018566 | -0.0011944 | -0.0036299 | 0.02753 | 0.01139 | 0.07888 | 0.0243 | 0.037373 | 0.10707 | 0.046148 | 0.22438 | 0.11094 | 0.10178 | -0.00422 | 0.016908 | 0.10282 | 0.17396 | 0.1909 | -0.1321 | 121.7296 | -0.080615 | 121.6975 | 121.656 | -0.073569 | -0.14153 | 0.036698 | 121.4866 | -0.084861 | 121.7204 | 121.6356 | 0.149 | -0.013725 | 0.003212 | 121.7257 | 121.6648 | 121.843 | 121.643 | -0.076741 | 121.7215 | 121.7926 | 121.8095 | 121.6144 | -0.31978
538.5469 | 121.8201 | -121.6278 | 0.19684 | 1.4211e-13 | -0.026404 | 0.015321 | -0.0032117 | -0.010196 | 0.020339 | -0.24059 | -0.0018566 | -0.00098076 | -0.0034163 | 0.02753 | 0.010963 | 0.07888 | 0.019721 | 0.037373 | 0.10249 | 0.03699 | 0.21522 | 0.10636 | 0.10178 | 0.000359 | 0.003172 | 0.1074 | 0.17396 | -0.11587 | -0.13668 | 121.7342 | -0.094348 | 121.7067 | 121.6652 | -0.06899 | -0.15985 | 0.018386 | 121.4911 | -0.089437 | 121.7296 | 121.631 | 0.13985 | -0.02288 | -0.31271 | 121.7303 | 121.6648 | 121.843 | 121.6475 | -0.090475 | 121.7352 | 121.8018 | 121.5119 | 121.6282 | -0.33351
540.2812 | 121.9528 | -121.6003 | 0.13275 | 1.4211e-13 | -0.02619 | 0.015321 | -0.0032117 | -0.010196 | 0.020552 | -0.24059 | -0.001643 | -0.00098076 | -0.0032025 | 0.027316 | 0.01139 | 0.083459 | 0.0243 | 0.037373 | 0.10707 | 0.023254 | 0.22438 | 0.11552 | 0.10178 | -0.008798 | 0.003172 | 0.1074 | 0.17396 | -0.11587 | -0.1321 | 121.7159 | -0.025683 | 121.6838 | 121.6377 | -0.078148 | -0.1095 | 0.09163 | 121.4682 | -0.02535 | 121.7021 | 121.6035 | 0.13527 | 0.041207 | -0.24862 | 121.7074 | 121.6236 | 121.8247 | 121.6246 | -0.01723 | 121.7077 | 121.7743 | 121.4845 | 121.5915 | -0.26485
542.0312 | 121.9391 | -121.5958 | 0.15106 | 1.4211e-13 | -0.026404 | 0.015534 | -0.0036391 | -0.010623 | 0.020766 | -0.23296 | -0.0020702 | -0.0011944 | -0.0034163 | 0.02753 | 0.01139 | 0.083459 | 0.019721 | 0.037373 | 0.11165 | 0.041569 | 0.22438 | 0.11094 | 0.097201 | -0.00422 | 0.01233 | 0.1074 | 0.17396 | -0.12045 | -0.13668 | 121.7067 | -0.039415 | 121.6792 | 121.6331 | -0.073569 | -0.10949 | 0.073319 | 121.4591 | -0.043661 | 121.693 | 121.6081 | 0.14901 | 0.022896 | -0.27151 | 121.7074 | 121.6373 | 121.8201 | 121.6155 | -0.04012 | 121.7032 | 121.7697 | 121.4753 | 121.5915 | -0.28774
543.7656 | 121.8475 | -121.637 | 0.19684 | 1.4211e-13 | -0.026404 | 0.015748 | -0.0034253 | -0.01041 | 0.020766 | -0.23296 | -0.0018566 | -0.0011944 | -0.0034163 | 0.027102 | 0.010963 | 0.088037 | 0.033457 | 0.032795 | 0.11622 | 0.014096 | 0.22896 | 0.11552 | 0.10178 | -0.008798 | 0.01233 | 0.10282 | 0.17854 | -0.12045 | -0.13668 | 121.7525 | -0.080613 | 121.725 | 121.6698 | -0.082726 | -0.18274 | 0.032121 | 121.5003 | -0.094016 | 121.7387 | 121.6493 | 0.14901 | -0.018302 | -0.31729 | 121.7532 | 121.6511 | 121.8659 | 121.6704 | -0.081317 | 121.7398 | 121.8155 | 121.5165 | 121.6282 | -0.33351
545.4375 | 121.8384 | -121.637 | 0.17853 | 1.4211e-13 | -0.02619 | 0.015534 | -0.0034253 | -0.01041 | 0.020766 | -0.23296 | -0.001643 | -0.0011944 | -0.0038435 | 0.02753 | 0.011176 | 0.074302 | 0.0243 | 0.032795 | 0.11165 | 0.041569 | 0.22896 | 0.11552 | 0.10178 | -0.00422 | 0.007751 | 0.1074 | 0.17854 | -0.0884 | -0.12294 | 121.7525 | -0.066881 | 121.7113 | 121.6698 | -0.082726 | -0.13696 | 0.050431 | 121.514 | -0.071127 | 121.7387 | 121.6447 | 0.13069 | 8e-06 | -0.26693 | 121.7486 | 121.6785 | 121.8659 | 121.6613 | -0.063007 | 121.7444 | 121.8155 | 121.5486 | 121.6327 | -0.30147
547.1719 | 121.8201 | -121.637 | 0.17395 | 1.4211e-13 | -0.02619 | 0.015748 | -0.0038527 | -0.010837 | 0.02098 | -0.24059 | -0.0022838 | -0.0011944 | -0.0034163 | 0.027316 | 0.01139 | 0.083459 | 0.019721 | 0.037373 | 0.10249 | 0.03699 | 0.2198 | 0.11094 | 0.097201 | -0.008798 | 0.003172 | 0.11198 | 0.17396 | -0.083821 | -0.13668 | 121.7479 | -0.07146 | 121.7204 | 121.6743 | -0.073569 | -0.13696 | 0.045852 | 121.5003 | -0.061971 | 121.7342 | 121.6401 | 0.13985 | 8e-06 | -0.25777 | 121.7395 | 121.674 | 121.8568 | 121.6567 | -0.063008 | 121.7489 | 121.8109 | 121.5531 | 121.6282 | -0.31063
548.9219 | 121.8338 | -121.6553 | 0.17853 | 1.4211e-13 | -0.026617 | 0.015321 | -0.0034253 | -0.01041 | 0.020766 | -0.23296 | -0.0020702 | -0.00076696 | -0.0036299 | 0.027743 | 0.01139 | 0.088037 | 0.019721 | 0.037373 | 0.10249 | 0.046148 | 0.22896 | 0.11552 | 0.092622 | -0.008798 | 0.007751 | 0.098244 | 0.16938 | -0.10671 | -0.1321 | 121.7708 | -0.076038 | 121.7433 | 121.6926 | -0.078148 | -0.13238 | 0.050431 | 121.5232 | -0.080284 | 121.7479 | 121.663 | 0.13985 | -0.009149 | -0.28524 | 121.7578 | 121.7014 | 121.8842 | 121.675 | -0.063007 | 121.7535 | 121.8247 | 121.5486 | 121.6465 | -0.31062
550.5938 | 121.8338 | -121.6461 | 0.19226 | 1.4211e-13 | -0.02619 | 0.015534 | -0.0032117 | -0.010196 | 0.020766 | -0.22533 | -0.0018566 | -0.00098076 | -0.0034163 | 0.027743 | 0.010963 | 0.083459 | 0.019721 | 0.028217 | 0.10249 | 0.041569 | 0.22438 | 0.1201 | 0.097201 | -0.008798 | -0.001407 | 0.098244 | 0.17396 | -0.10671 | -0.1321 | 121.7662 | -0.089771 | 121.7296 | 121.6743 | -0.091883 | -0.15069 | 0.03212 | 121.514 | -0.094017 | 121.7433 | 121.6447 | 0.13069 | -0.018303 | -0.29897 | 121.7486 | 121.6877 | 121.8705 | 121.6658 | -0.072161 | 121.7444 | 121.8201 | 121.5394 | 121.6373 | -0.32436
552.3281 | 121.9757 | -121.6232 | 0.13275 | 1.4211e-13 | -0.02619 | 0.015321 | -0.0032117 | -0.010623 | 0.020552 | -0.22533 | -0.0018566 | -0.00076696 | -0.0038435 | 0.02753 | 0.011176 | 0.083459 | 0.0243 | 0.032795 | 0.10707 | 0.041569 | 0.22438 | 0.10636 | 0.092622 | -0.008798 | 0.007751 | 0.1074 | 0.17854 | -0.079243 | -0.1321 | 121.7296 | -0.025683 | 121.7067 | 121.656 | -0.073568 | -0.091182 | 0.09163 | 121.4911 | -0.02535 | 121.7159 | 121.631 | 0.13985 | 0.045785 | -0.21199 | 121.7303 | 121.6648 | 121.8476 | 121.6475 | -0.026388 | 121.7306 | 121.8018 | 121.544 | 121.6144 | -0.26485
554.0625 | 121.8384 | -121.6324 | 0.16022 | 1.4211e-13 | -0.025976 | 0.015748 | -0.0029979 | -0.01041 | 0.020766 | -0.23296 | -0.0020702 | -0.00098076 | -0.0036299 | 0.02753 | 0.010963 | 0.083459 | 0.028878 | 0.037373 | 0.10707 | 0.03699 | 0.23354 | 0.11552 | 0.092622 | -0.008798 | 0.007751 | 0.1074 | 0.17396 | -0.10214 | -0.1321 | 121.7479 | -0.053149 | 121.7158 | 121.6698 | -0.078148 | -0.12323 | 0.073321 | 121.5003 | -0.052816 | 121.725 | 121.6401 | 0.13985 | 0.013741 | -0.26235 | 121.7395 | 121.6694 | 121.8659 | 121.6613 | -0.044696 | 121.7398 | 121.8063 | 121.5302 | 121.6236 | -0.29231
555.8125 | 121.9437 | -121.6232 | 0.16479 | 1.4211e-13 | -0.026404 | 0.015748 | -0.0032117 | -0.01041 | 0.020766 | -0.23296 | -0.0018566 | -0.00098076 | -0.0034163 | 0.02753 | 0.011176 | 0.07888 | 0.015142 | 0.032795 | 0.11165 | 0.03699 | 0.2198 | 0.1201 | 0.097201 | -0.008798 | 0.003172 | 0.098244 | 0.17854 | -0.070086 | -0.1321 | 121.7433 | -0.053148 | 121.7021 | 121.656 | -0.087305 | -0.12781 | 0.055007 | 121.4911 | -0.066551 | 121.7204 | 121.6264 | 0.13527 | 0.013741 | -0.23488 | 121.7349 | 121.6602 | 121.843 | 121.6384 | -0.044695 | 121.7215 | 121.8018 | 121.5531 | 121.6144 | -0.29689
557.4844 | 121.8567 | -121.6232 | 0.19226 | 1.4211e-13 | -0.02619 | 0.015748 | -0.0034253 | -0.010196 | 0.020766 | -0.23296 | -0.0018566 | -0.00076696 | -0.0036299 | 0.027743 | 0.010963 | 0.07888 | 0.0243 | 0.037373 | 0.10707 | 0.027833 | 0.2198 | 0.11552 | 0.092622 | -0.008798 | 0.016908 | 0.10282 | 0.16938 | -0.12045 | -0.1321 | 121.7388 | -0.085193 | 121.7021 | 121.6606 | -0.078148 | -0.16443 | 0.027541 | 121.4911 | -0.089439 | 121.7159 | 121.6401 | 0.149 | -0.022882 | -0.31271 | 121.7303 | 121.6511 | 121.843 | 121.6475 | -0.07674 | 121.7261 | 121.7926 | 121.5028 | 121.6144 | -0.32436
559.2188 | 121.8796 | -121.6599 | 0.1831 | 1.4211e-13 | -0.02619 | 0.015748 | -0.0032117 | -0.01041 | 0.020766 | -0.23296 | -0.0018566 | -0.00076696 | -0.0038435 | 0.027743 | 0.011176 | 0.088037 | 0.028878 | 0.04653 | 0.11165 | 0.032411 | 0.22896 | 0.11094 | 0.078886 | -0.00422 | 0.003172 | 0.11198 | 0.18311 | -0.097557 | -0.1321 | 121.7708 | -0.071458 | 121.7479 | 121.7064 | -0.064412 | -0.15069 | 0.045854 | 121.5278 | -0.071126 | 121.7387 | 121.663 | 0.13527 | 1e-05 | -0.28066 | 121.7715 | 121.6923 | 121.8888 | 121.6887 | -0.072163 | 121.7718 | 121.843 | 121.5623 | 121.6556 | -0.3152
560.9688 | 121.8979 | -121.6415 | 0.17395 | 1.4211e-13 | -0.026404 | 0.015748 | -0.0034253 | -0.010623 | 0.020552 | -0.24059 | -0.0018566 | -0.00055336 | -0.0036299 | 0.02753 | 0.011604 | 0.07888 | 0.028878 | 0.041952 | 0.11165 | 0.03699 | 0.21522 | 0.11552 | 0.078886 | -0.013377 | 0.007751 | 0.10282 | 0.17396 | -0.074664 | -0.1321 | 121.7571 | -0.062303 | 121.7204 | 121.6835 | -0.073569 | -0.13696 | 0.041274 | 121.5094 | -0.071128 | 121.7204 | 121.6493 | 0.13985 | 8e-06 | -0.24861 | 121.7532 | 121.6785 | 121.8568 | 121.6704 | -0.058429 | 121.7444 | 121.8155 | 121.5669 | 121.6282 | -0.30605
562.6406 | 121.994 | -121.6141 | 0.15106 | 1.4211e-13 | -0.026617 | 0.015748 | -0.0038527 | -0.01041 | 0.02098 | -0.24059 | -0.001643 | -0.00076696 | -0.0038435 | 0.02753 | 0.01139 | 0.088037 | 0.0243 | 0.041952 | 0.11165 | 0.046148 | 0.22896 | 0.11552 | 0.083464 | -0.017956 | 0.01233 | 0.098244 | 0.17854 | -0.097557 | -0.12752 | 121.7296 | -0.039415 | 121.7021 | 121.656 | -0.073569 | -0.10491 | 0.077897 | 121.4866 | -0.052818 | 121.6975 | 121.6264 | 0.13985 | 0.027474 | -0.24862 | 121.7257 | 121.6602 | 121.843 | 121.6384 | -0.035541 | 121.7123 | 121.7926 | 121.5165 | 121.5961 | -0.27858
564.3906 | 121.9345 | -121.6278 | 0.15106 | 1.4211e-13 | -0.026404 | 0.015962 | -0.0036391 | -0.010837 | 0.020766 | -0.23296 | -0.0020702 | -0.00076696 | -0.0036299 | 0.027743 | 0.011176 | 0.083459 | 0.028878 | 0.037373 | 0.10249 | 0.041569 | 0.22438 | 0.11094 | 0.074307 | -0.008798 | 0.003172 | 0.1074 | 0.17854 | -0.11129 | -0.11836 | 121.7387 | -0.048572 | 121.7113 | 121.6652 | -0.073569 | -0.10949 | 0.073319 | 121.5094 | -0.043661 | 121.7021 | 121.631 | 0.12153 | 0.027474 | -0.26236 | 121.7303 | 121.6694 | 121.8522 | 121.6567 | -0.04012 | 121.7352 | 121.8063 | 121.5165 | 121.619 | -0.26942
566.0625 | 121.9391 | -121.6187 | 0.14648 | 1.4211e-13 | -0.026404 | 0.015534 | -0.0032117 | -0.010196 | 0.020766 | -0.23296 | -0.0020702 | -0.00098076 | -0.0036299 | 0.027743 | 0.01139 | 0.07888 | 0.019721 | 0.041952 | 0.10707 | 0.046148 | 0.21522 | 0.11094 | 0.083464 | -0.008798 | 0.003172 | 0.1074 | 0.17854 | -0.070086 | -0.12752 | 121.7296 | -0.039416 | 121.6975 | 121.6606 | -0.06899 | -0.10034 | 0.06874 | 121.4911 | -0.039083 | 121.7021 | 121.6218 | 0.13069 | 0.032052 | -0.21657 | 121.7257 | 121.6648 | 121.8339 | 121.6384 | -0.035542 | 121.7261 | 121.7972 | 121.5486 | 121.6099 | -0.274
567.8125 | 121.9528 | -121.5958 | 0.15564 | 1.4211e-13 | -0.025976 | 0.015321 | -0.0029979 | -0.010623 | 0.02098 | -0.24822 | -0.0020702 | -0.00098076 | -0.0034163 | 0.027743 | 0.011176 | 0.083459 | 0.028878 | 0.041952 | 0.10707 | 0.046148 | 0.22438 | 0.1201 | 0.074307 | -0.008798 | 0.007751 | 0.1074 | 0.16938 | -0.074664 | -0.11836 | 121.7159 | -0.048572 | 121.6792 | 121.6377 | -0.078148 | -0.10949 | 0.068741 | 121.4774 | -0.048239 | 121.6701 | 121.6035 | 0.12611 | 0.013739 | -0.2303 | 121.7028 | 121.6419 | 121.8201 | 121.6246 | -0.03554 | 121.7032 | 121.7651 | 121.5211 | 121.587 | -0.274
569.4844 | 121.8475 | -121.6873 | 0.16937 | 1.4211e-13 | -0.02619 | 0.015534 | -0.0034253 | -0.01041 | 0.020552 | -0.23296 | -0.0020702 | -0.00055336 | -0.0034163 | 0.027743 | 0.010963 | 0.07888 | 0.028878 | 0.032795 | 0.11622 | 0.046148 | 0.21522 | 0.1201 | 0.083464 | -0.008798 | 0.007751 | 0.10282 | 0.17396 | -0.097557 | -0.1321 | 121.8074 | -0.053148 | 121.7662 | 121.7201 | -0.087305 | -0.12323 | 0.045851 | 121.5552 | -0.066551 | 121.7708 | 121.6951 | 0.13985 | 0.004585 | -0.26693 | 121.8035 | 121.7335 | 121.9025 | 121.7162 | -0.049273 | 121.7901 | 121.8613 | 121.5898 | 121.6785 | -0.30147
571.2188 | 121.8979 | -121.6507 | 0.16937 | 1.4211e-13 | -0.026617 | 0.015321 | -0.0034253 | -0.010623 | 0.020766 | -0.24059 | -0.0022838 | -0.00076696 | -0.0034163 | 0.028598 | 0.01139 | 0.083459 | 0.028878 | 0.041952 | 0.10707 | 0.03699 | 0.22438 | 0.11094 | 0.083464 | -0.00422 | 0.007751 | 0.1074 | 0.16938 | -0.047193 | -0.14125 | 121.7616 | -0.062305 | 121.7342 | 121.6926 | -0.06899 | -0.13238 | 0.055008 | 121.5094 | -0.061972 | 121.7342 | 121.6584 | 0.14901 | 6e-06 | -0.21657 | 121.7578 | 121.6877 | 121.8751 | 121.6796 | -0.058431 | 121.7581 | 121.8201 | 121.6035 | 121.6465 | -0.31063
572.9844 | 121.9666 | -121.6232 | 0.14191 | 1.4211e-13 | -0.026404 | 0.015534 | -0.0032117 | -0.010623 | 0.020552 | -0.24059 | -0.0020702 | -0.00098076 | -0.0038435 | 0.02753 | 0.01139 | 0.074302 | 0.028878 | 0.04653 | 0.10707 | 0.03699 | 0.22438 | 0.10636 | 0.069728 | -0.013377 | 0.007751 | 0.098244 | 0.16938 | -0.10671 | -0.12752 | 121.7296 | -0.034839 | 121.6975 | 121.6698 | -0.059833 | -0.10492 | 0.082474 | 121.4957 | -0.043663 | 121.693 | 121.631 | 0.13527 | 0.027472 | -0.24862 | 121.7303 | 121.6602 | 121.8476 | 121.6521 | -0.035544 | 121.7215 | 121.7926 | 121.5165 | 121.6099 | -0.26943
574.6562 | 121.9849 | -121.6141 | 0.15106 | 1.4211e-13 | -0.026404 | 0.015748 | -0.0036391 | -0.010196 | 0.020766 | -0.23296 | -0.001643 | -0.00098076 | -0.0036299 | 0.02753 | 0.010963 | 0.07888 | 0.0243 | 0.055687 | 0.11165 | 0.03699 | 0.22438 | 0.11094 | 0.074307 | -0.008798 | 0.007751 | 0.1074 | 0.16938 | -0.065507 | -0.12752 | 121.725 | -0.039415 | 121.693 | 121.6698 | -0.055255 | -0.11407 | 0.073319 | 121.4866 | -0.043661 | 121.6884 | 121.6218 | 0.13527 | 0.018317 | -0.21657 | 121.7257 | 121.6511 | 121.8385 | 121.6384 | -0.04012 | 121.7215 | 121.7835 | 121.5486 | 121.6053 | -0.27858
576.3906 | 121.9208 | -121.6507 | 0.16937 | 1.4211e-13 | -0.026831 | 0.015534 | -0.0029979 | -0.010623 | 0.020766 | -0.23296 | -0.0018566 | -0.00076696 | -0.0034163 | 0.028171 | 0.010963 | 0.07888 | 0.0243 | 0.051108 | 0.11165 | 0.03699 | 0.2198 | 0.11552 | 0.078886 | -0.00422 | 0.003172 | 0.10282 | 0.17854 | -0.092979 | -0.12294 | 121.7662 | -0.057726 | 121.7296 | 121.7018 | -0.064413 | -0.13238 | 0.050429 | 121.5278 | -0.066551 | 121.7296 | 121.6539 | 0.12611 | 0.009163 | -0.26235 | 121.7623 | 121.6877 | 121.8705 | 121.675 | -0.053852 | 121.7535 | 121.8292 | 121.5577 | 121.6465 | -0.29231
578.125 | 122.0032 | -121.6141 | 0.16479 | 1.4211e-13 | -0.026617 | 0.015962 | -0.0034253 | -0.01041 | 0.020552 | -0.23296 | -0.001643 | -0.00076696 | -0.0038435 | 0.027743 | 0.010749 | 0.083459 | 0.0243 | 0.04653 | 0.11165 | 0.041569 | 0.2198 | 0.10636 | 0.074307 | -0.00422 | 0.01233 | 0.1074 | 0.16938 | -0.047193 | -0.12752 | 121.7204 | -0.053148 | 121.6975 | 121.6606 | -0.059833 | -0.12323 | 0.055007 | 121.4866 | -0.057394 | 121.6884 | 121.6264 | 0.13985 | 0.004584 | -0.21199 | 121.7257 | 121.6556 | 121.8339 | 121.6384 | -0.058432 | 121.7215 | 121.7835 | 121.5669 | 121.6099 | -0.29231
579.8594 | 121.994 | -121.6324 | 0.14191 | 1.4211e-13 | -0.026404 | 0.015748 | -0.0029979 | -0.010623 | 0.020766 | -0.22533 | -0.0018566 | -0.00098076 | -0.0038435 | 0.027957 | 0.010749 | 0.083459 | 0.0243 | 0.04653 | 0.11165 | 0.041569 | 0.2198 | 0.11552 | 0.074307 | -0.008798 | 0.007751 | 0.1074 | 0.17396 | -0.033457 | -0.12752 | 121.7479 | -0.03026 | 121.7158 | 121.6789 | -0.068991 | -0.10034 | 0.077895 | 121.5049 | -0.034506 | 121.7067 | 121.6401 | 0.13527 | 0.032051 | -0.17536 | 121.744 | 121.674 | 121.8522 | 121.6567 | -0.026386 | 121.7398 | 121.8063 | 121.5989 | 121.6236 | -0.26943
581.5938 | 121.9574 | -121.6187 | 0.16022 | 1.4211e-13 | -0.026404 | 0.015321 | -0.0032117 | -0.01041 | 0.020766 | -0.24059 | -0.0018566 | -0.00098076 | -0.0038435 | 0.027957 | 0.011176 | 0.07888 | 0.019721 | 0.051108 | 0.11622 | 0.03699 | 0.2198 | 0.11552 | 0.078886 | -0.008798 | 0.01233 | 0.098244 | 0.16938 | -0.005985 | -0.12294 | 121.7342 | -0.043992 | 121.6975 | 121.6698 | -0.064413 | -0.12323 | 0.059585 | 121.4957 | -0.061973 | 121.6975 | 121.631 | 0.13527 | 0.009162 | -0.1662 | 121.7349 | 121.6556 | 121.8385 | 121.6384 | -0.044696 | 121.7169 | 121.788 | 121.6127 | 121.6099 | -0.28316
583.2812 | 121.9849 | -121.6049 | 0.14191 | 1.4211e-13 | -0.026831 | 0.015321 | -0.0032117 | -0.01041 | 0.020552 | -0.24059 | -0.0018566 | -0.00098076 | -0.0034163 | 0.027957 | 0.010963 | 0.07888 | 0.033457 | 0.051108 | 0.11165 | 0.041569 | 0.2198 | 0.1201 | 0.074307 | -0.013377 | 0.01233 | 0.10282 | 0.17854 | -0.0884 | -0.12752 | 121.725 | -0.03026 | 121.6838 | 121.656 | -0.068992 | -0.10034 | 0.077895 | 121.4774 | -0.039085 | 121.6792 | 121.6172 | 0.13985 | 0.036629 | -0.23031 | 121.7166 | 121.6465 | 121.8247 | 121.6384 | -0.021807 | 121.7077 | 121.7835 | 121.5165 | 121.5915 | -0.26943
585.0312 | 121.9208 | -121.6599 | 0.17395 | 1.4211e-13 | -0.025763 | 0.015748 | -0.0034253 | -0.011051 | 0.020339 | -0.23296 | -0.0018566 | -0.00076696 | -0.0036299 | 0.028171 | 0.011176 | 0.088037 | 0.019721 | 0.055687 | 0.11165 | 0.041569 | 0.21522 | 0.1201 | 0.078886 | -0.008798 | 0.007751 | 0.11198 | 0.18311 | -0.033457 | -0.1321 | 121.78 | -0.062303 | 121.7479 | 121.7155 | -0.064413 | -0.13238 | 0.041274 | 121.5278 | -0.061971 | 121.7387 | 121.6676 | 0.13985 | 0.009165 | -0.20741 | 121.7715 | 121.7014 | 121.8751 | 121.6796 | -0.05385 | 121.7718 | 121.843 | 121.6264 | 121.6511 | -0.30605
586.7031 | 121.9116 | -121.6644 | 0.17853 | 1.4211e-13 | -0.026617 | 0.015748 | -0.0029979 | -0.01041 | 0.020552 | -0.22533 | -0.0018566 | -0.001408 | -0.0036299 | 0.027957 | 0.010963 | 0.083459 | 0.0243 | 0.04653 | 0.11165 | 0.041569 | 0.22438 | 0.11094 | 0.088043 | -0.008798 | 0.003172 | 0.10282 | 0.17854 | -0.042614 | -0.12752 | 121.7754 | -0.066881 | 121.7479 | 121.711 | -0.064412 | -0.13696 | 0.045853 | 121.5369 | -0.075706 | 121.7525 | 121.6676 | 0.13069 | 8e-06 | -0.22114 | 121.7761 | 121.706 | 121.8888 | 121.6887 | -0.067586 | 121.7673 | 121.843 | 121.6218 | 121.6556 | -0.30605
588.4375 | 121.9162 | -121.6461 | 0.17853 | 1.4211e-13 | -0.026831 | 0.015321 | -0.0034253 | -0.010837 | 0.020766 | -0.23296 | -0.001643 | -0.0011944 | -0.0034163 | 0.028171 | 0.010963 | 0.083459 | 0.028878 | 0.041952 | 0.11165 | 0.03699 | 0.22438 | 0.10636 | 0.078886 | -0.013377 | 0.01233 | 0.11656 | 0.16938 | -0.079243 | -0.12294 | 121.7525 | -0.066881 | 121.7296 | 121.6881 | -0.064411 | -0.14154 | 0.045853 | 121.5232 | -0.061971 | 121.725 | 121.6584 | 0.13527 | -0.009149 | -0.25777 | 121.7578 | 121.6831 | 121.8705 | 121.675 | -0.072165 | 121.7627 | 121.8155 | 121.5669 | 121.6327 | -0.30147
590.1719 | 121.9757 | -121.6232 | 0.16022 | 1.4211e-13 | -0.026617 | 0.015321 | -0.0036391 | -0.01041 | 0.020766 | -0.24059 | -0.0020702 | -0.00098076 | -0.0038435 | 0.028171 | 0.01139 | 0.088037 | 0.028878 | 0.055687 | 0.10707 | 0.041569 | 0.22896 | 0.11552 | 0.083464 | -0.008798 | 0.01233 | 0.10282 | 0.17396 | -0.019721 | -0.1321 | 121.7388 | -0.053149 | 121.7113 | 121.6789 | -0.059834 | -0.11865 | 0.068742 | 121.4911 | -0.057395 | 121.7067 | 121.6356 | 0.14443 | 0.013741 | -0.17994 | 121.7303 | 121.6648 | 121.8522 | 121.6521 | -0.044696 | 121.7261 | 121.7972 | 121.6035 | 121.6144 | -0.29231
591.9219 | 121.8796 | -121.6736 | 0.19684 | 1.4211e-13 | -0.026617 | 0.015321 | -0.0034253 | -0.01041 | 0.020552 | -0.24059 | -0.001643 | -0.0011944 | -0.0038435 | 0.028171 | 0.01139 | 0.083459 | 0.0243 | 0.060265 | 0.10249 | 0.03699 | 0.22438 | 0.1201 | 0.083464 | -0.008798 | 0.01233 | 0.1074 | 0.17854 | 0.007751 | -0.12752 | 121.7937 | -0.094348 | 121.757 | 121.7338 | -0.059835 | -0.15985 | 0.027543 | 121.5461 | -0.089437 | 121.757 | 121.6859 | 0.13985 | -0.018302 | -0.18909 | 121.7761 | 121.7106 | 121.898 | 121.6979 | -0.076738 | 121.781 | 121.8521 | 121.6813 | 121.6648 | -0.32436
593.6094 | 121.875 | -121.6782 | 0.17853 | 1.4211e-13 | -0.026404 | 0.015321 | -0.0032117 | -0.010623 | 0.020766 | -0.23296 | -0.0020702 | -0.0011944 | -0.0034163 | 0.028171 | 0.011176 | 0.088037 | 0.0243 | 0.051108 | 0.10707 | 0.046148 | 0.22438 | 0.12468 | 0.083464 | -0.008798 | 0.007751 | 0.11198 | 0.17854 | -0.038035 | -0.12752 | 121.8028 | -0.07146 | 121.7662 | 121.7293 | -0.073571 | -0.13238 | 0.045853 | 121.5506 | -0.066549 | 121.7616 | 121.6859 | 0.13527 | 8e-06 | -0.21656 | 121.7852 | 121.7243 | 121.9025 | 121.7025 | -0.053849 | 121.7901 | 121.8567 | 121.6401 | 121.6694 | -0.30605
595.3438 | 121.8704 | -121.6782 | 0.18768 | 1.4211e-13 | -0.026831 | 0.015107 | -0.0034253 | -0.01041 | 0.020552 | -0.22533 | -0.001643 | -0.00098076 | -0.0036299 | 0.027957 | 0.010963 | 0.088037 | 0.0243 | 0.051108 | 0.11165 | 0.041569 | 0.22438 | 0.11552 | 0.074307 | -0.013377 | 0.003172 | 0.10282 | 0.18311 | -0.092979 | -0.1321 | 121.7937 | -0.076036 | 121.7662 | 121.7293 | -0.064413 | -0.14611 | 0.036698 | 121.5461 | -0.084861 | 121.7525 | 121.6813 | 0.13527 | -0.004568 | -0.28066 | 121.7898 | 121.7197 | 121.9025 | 121.7025 | -0.072162 | 121.781 | 121.8613 | 121.5852 | 121.6648 | -0.31978
597.0938 | 121.9299 | -121.6461 | 0.1831 | 1.4211e-13 | -0.026831 | 0.015321 | -0.0034253 | -0.01041 | 0.020766 | -0.22533 | -0.0020702 | -0.00076696 | -0.0038435 | 0.028171 | 0.011176 | 0.083459 | 0.019721 | 0.055687 | 0.11165 | 0.046148 | 0.22438 | 0.1201 | 0.074307 | -0.013377 | 0.01233 | 0.11198 | 0.17396 | -0.097557 | -0.12752 | 121.7662 | -0.071458 | 121.7296 | 121.7018 | -0.064413 | -0.13696 | 0.041276 | 121.5186 | -0.071126 | 121.7204 | 121.6584 | 0.13985 | -0.009147 | -0.28066 | 121.7578 | 121.6923 | 121.8705 | 121.6658 | -0.063005 | 121.7581 | 121.8201 | 121.5486 | 121.6327 | -0.31062
598.7812 | 121.8887 | -121.6461 | 0.1831 | 1.4211e-13 | -0.026404 | 0.015748 | -0.0034253 | -0.010623 | 0.020552 | -0.24059 | -0.0020702 | -0.0011944 | -0.0036299 | 0.028171 | 0.010535 | 0.074302 | 0.0243 | 0.041952 | 0.10249 | 0.041569 | 0.22896 | 0.11552 | 0.083464 | -0.013377 | 0.01233 | 0.10282 | 0.17854 | -0.051771 | -0.12752 | 121.7616 | -0.080615 | 121.7204 | 121.6881 | -0.073569 | -0.14154 | 0.045854 | 121.5186 | -0.080283 | 121.7296 | 121.6584 | 0.13985 | -0.004569 | -0.23488 | 121.7486 | 121.6877 | 121.8751 | 121.6704 | -0.067584 | 121.7489 | 121.8247 | 121.5943 | 121.6327 | -0.31062
600.5156 | 121.9254 | -121.6873 | 0.17853 | 1.4211e-13 | -0.027258 | 0.015321 | -0.0032117 | -0.010837 | 0.020552 | -0.23296 | -0.0018566 | -0.00098076 | -0.0038435 | 0.028171 | 0.011176 | 0.083459 | 0.0243 | 0.051108 | 0.10707 | 0.046148 | 0.2198 | 0.11552 | 0.088043 | -0.00422 | 0.003172 | 0.1074 | 0.17396 | -0.005985 | -0.12752 | 121.8028 | -0.07146 | 121.7708 | 121.7384 | -0.064413 | -0.13238 | 0.041274 | 121.5598 | -0.071127 | 121.7754 | 121.6905 | 0.13069 | -0.00457 | -0.18451 | 121.7944 | 121.7335 | 121.9071 | 121.7116 | -0.063007 | 121.7947 | 121.8613 | 121.6813 | 121.6831 | -0.30605
602.25 | 121.962 | -121.6278 | 0.15106 | 1.4211e-13 | -0.026617 | 0.015534 | -0.0034253 | -0.010837 | 0.020339 | -0.24059 | -0.0018566 | -0.0011944 | -0.0034163 | 0.028171 | 0.010749 | 0.088037 | 0.019721 | 0.055687 | 0.10249 | 0.041569 | 0.22438 | 0.11552 | 0.078886 | -0.008798 | 0.007751 | 0.10282 | 0.17854 | -0.083821 | -0.12294 | 121.7433 | -0.048572 | 121.7158 | 121.6835 | -0.059834 | -0.10949 | 0.073319 | 121.5049 | -0.04824 | 121.7067 | 121.6356 | 0.13069 | 0.027474 | -0.23488 | 121.7303 | 121.6694 | 121.8522 | 121.6475 | -0.035541 | 121.7306 | 121.8063 | 121.544 | 121.619 | -0.274
604 | 121.875 | -121.669 | 0.20142 | 1.4211e-13 | -0.026617 | 0.015321 | -0.0029979 | -0.01041 | 0.020339 | -0.23296 | -0.0018566 | -0.00076696 | -0.0036299 | 0.027957 | 0.010963 | 0.07888 | 0.028878 | 0.051108 | 0.10707 | 0.032411 | 0.2198 | 0.11552 | 0.078886 | -0.00422 | 0.007751 | 0.11656 | 0.17854 | -0.092979 | -0.12752 | 121.7845 | -0.094348 | 121.7479 | 121.7201 | -0.064413 | -0.16901 | 0.018386 | 121.5415 | -0.084859 | 121.7479 | 121.6768 | 0.13527 | -0.02288 | -0.2944 | 121.7761 | 121.7014 | 121.8888 | 121.6979 | -0.085895 | 121.7856 | 121.8475 | 121.576 | 121.6648 | -0.32893
605.6875 | 122.0169 | -121.6278 | 0.15106 | 1.4211e-13 | -0.027045 | 0.015321 | -0.0034253 | -0.010623 | 0.020766 | -0.22533 | -0.0018566 | -0.0011944 | -0.0036299 | 0.027957 | 0.011176 | 0.083459 | 0.019721 | 0.04653 | 0.11622 | 0.018675 | 0.22438 | 0.11552 | 0.083464 | -0.00422 | 0.016908 | 0.11656 | 0.18311 | -0.074664 | -0.12752 | 121.7433 | -0.034837 | 121.7113 | 121.6743 | -0.068991 | -0.13239 | 0.073319 | 121.5003 | -0.034505 | 121.7113 | 121.6447 | 0.14443 | 0.032053 | -0.22573 | 121.744 | 121.6465 | 121.8522 | 121.6475 | -0.035541 | 121.7444 | 121.8109 | 121.5531 | 121.6236 | -0.27858
607.4219 | 122.0123 | -121.6187 | 0.14191 | 1.4211e-13 | -0.026831 | 0.015321 | -0.0034253 | -0.011051 | 0.020766 | -0.24059 | -0.0018566 | -0.00098076 | -0.0038435 | 0.028171 | 0.010963 | 0.088037 | 0.0243 | 0.055687 | 0.11165 | 0.046148 | 0.22438 | 0.11552 | 0.078886 | -0.008798 | 0.01233 | 0.1074 | 0.17854 | -0.001407 | -0.12294 | 121.7342 | -0.03026 | 121.7067 | 121.6743 | -0.059834 | -0.095759 | 0.082474 | 121.4957 | -0.034506 | 121.6975 | 121.631 | 0.13527 | 0.036629 | -0.14331 | 121.7303 | 121.6648 | 121.843 | 121.643 | -0.026386 | 121.7261 | 121.7972 | 121.6172 | 121.6099 | -0.26485
609.1094 | 122.0078 | -121.6232 | 0.15106 | 1.4211e-13 | -0.026617 | 0.015321 | -0.0034253 | -0.010623 | 0.020339 | -0.24059 | -0.0020702 | -0.00098076 | -0.0034163 | 0.028384 | 0.011176 | 0.083459 | 0.019721 | 0.051108 | 0.10249 | 0.046148 | 0.22438 | 0.11094 | 0.083464 | 0.000359 | 0.007751 | 0.11198 | 0.18311 | -0.010564 | -0.11836 | 121.7342 | -0.048572 | 121.7067 | 121.6743 | -0.059834 | -0.10491 | 0.073319 | 121.5049 | -0.039083 | 121.7067 | 121.631 | 0.12611 | 0.032053 | -0.16163 | 121.7257 | 121.6694 | 121.8476 | 121.643 | -0.04012 | 121.7352 | 121.8063 | 121.6127 | 121.6236 | -0.26942
610.8438 | 121.9757 | -121.6461 | 0.15564 | 1.4211e-13 | -0.027045 | 0.015321 | -0.0032117 | -0.010623 | 0.020339 | -0.23296 | -0.0018566 | -0.00098076 | -0.0034163 | 0.028171 | 0.010963 | 0.07888 | 0.028878 | 0.04653 | 0.10707 | 0.03699 | 0.22438 | 0.11094 | 0.078886 | 0.000359 | 0.01233 | 0.11198 | 0.18311 | 0.007751 | -0.11836 | 121.7571 | -0.048572 | 121.725 | 121.6926 | -0.064412 | -0.11865 | 0.068741 | 121.5278 | -0.043661 | 121.725 | 121.6584 | 0.13069 | 0.027475 | -0.14789 | 121.7532 | 121.6831 | 121.8705 | 121.675 | -0.044698 | 121.7581 | 121.8292 | 121.6539 | 121.6465 | -0.274
612.5781 | 121.9574 | -121.6415 | 0.16937 | 1.4211e-13 | -0.026831 | 0.015321 | -0.0034253 | -0.010623 | 0.020552 | -0.24059 | -0.001643 | -0.00098076 | -0.0034163 | 0.028171 | 0.010963 | 0.083459 | 0.0243 | 0.051108 | 0.11165 | 0.041569 | 0.22896 | 0.1201 | 0.088043 | -0.00422 | 0.003172 | 0.1074 | 0.18769 | 0.007751 | -0.12752 | 121.7616 | -0.057726 | 121.725 | 121.6926 | -0.068992 | -0.1278 | 0.059586 | 121.514 | -0.061972 | 121.7296 | 121.6447 | 0.13069 | 0.01832 | -0.16162 | 121.7532 | 121.6831 | 121.8705 | 121.6658 | -0.049273 | 121.7489 | 121.8292 | 121.6493 | 121.6373 | -0.29689
614.25 | 121.8842 | -121.669 | 0.18768 | 1.4211e-13 | -0.026831 | 0.015748 | -0.0032117 | -0.010623 | 0.020339 | -0.22533 | -0.001643 | -0.00098076 | -0.0040571 | 0.028384 | 0.011176 | 0.083459 | 0.0243 | 0.051108 | 0.10249 | 0.046148 | 0.22896 | 0.1201 | 0.088043 | -0.00422 | 0.007751 | 0.12571 | 0.17854 | 0.035222 | -0.12752 | 121.7891 | -0.085193 | 121.7525 | 121.7201 | -0.068992 | -0.14153 | 0.041276 | 121.5415 | -0.061969 | 121.757 | 121.6768 | 0.13527 | -0.009147 | -0.15246 | 121.7715 | 121.7152 | 121.898 | 121.6933 | -0.067583 | 121.7947 | 121.8475 | 121.7042 | 121.6648 | -0.3152
615.9844 | 121.8979 | -121.6553 | 0.1831 | 1.4211e-13 | -0.026831 | 0.015107 | -0.0032117 | -0.010623 | 0.02098 | -0.22533 | -0.0020702 | -0.0011944 | -0.0038435 | 0.028384 | 0.011604 | 0.092615 | 0.0243 | 0.051108 | 0.11165 | 0.041569 | 0.2198 | 0.11552 | 0.078886 | -0.00422 | 0.007751 | 0.12114 | 0.18311 | 0.007751 | -0.12752 | 121.7708 | -0.071458 | 121.7479 | 121.7064 | -0.064413 | -0.14154 | 0.036697 | 121.5278 | -0.061969 | 121.7342 | 121.663 | 0.13527 | 1e-05 | -0.17535 | 121.7669 | 121.6968 | 121.8751 | 121.6796 | -0.067584 | 121.7764 | 121.8384 | 121.663 | 121.6511 | -0.31062
617.7344 | 121.8933 | -121.701 | 0.18768 | 1.4211e-13 | -0.027045 | 0.015321 | -0.0032117 | -0.01041 | 0.020552 | -0.24059 | -0.0018566 | -0.00098076 | -0.0036299 | 0.028171 | 0.011604 | 0.083459 | 0.0243 | 0.04653 | 0.10707 | 0.046148 | 0.2198 | 0.1201 | 0.083464 | -0.00422 | 0.016908 | 0.12571 | 0.18311 | -0.028878 | -0.1321 | 121.8211 | -0.080615 | 121.7845 | 121.7476 | -0.07357 | -0.14153 | 0.032119 | 121.569 | -0.061969 | 121.7845 | 121.718 | 0.149 | -0.004568 | -0.21656 | 121.8081 | 121.7472 | 121.9209 | 121.7253 | -0.067583 | 121.8268 | 121.8842 | 121.6722 | 121.6968 | -0.31978
619.4844 | 122.0032 | -121.6141 | 0.14648 | 1.4211e-13 | -0.026831 | 0.015321 | -0.0034253 | -0.010837 | 0.020552 | -0.2177 | -0.0022838 | -0.0011944 | -0.0036299 | 0.028812 | 0.01139 | 0.07888 | 0.0243 | 0.041952 | 0.10249 | 0.023254 | 0.22438 | 0.11094 | 0.074307 | -0.00422 | 0.01233 | 0.11198 | 0.17854 | -0.015142 | -0.12294 | 121.725 | -0.043994 | 121.693 | 121.656 | -0.06899 | -0.12323 | 0.077897 | 121.4911 | -0.034505 | 121.6884 | 121.6264 | 0.13527 | 0.032052 | -0.16163 | 121.7166 | 121.6373 | 121.8385 | 121.6384 | -0.035542 | 121.7261 | 121.7926 | 121.5989 | 121.6099 | -0.26942
621.1562 | 122.0123 | -121.6049 | 0.13733 | 1.4211e-13 | -0.027045 | 0.015321 | -0.0032117 | -0.010623 | 0.020339 | -0.22533 | -0.0018566 | -0.00076696 | -0.0038435 | 0.028384 | 0.011817 | 0.07888 | 0.0243 | 0.051108 | 0.10707 | 0.046148 | 0.22438 | 0.11552 | 0.083464 | 0.004938 | 0.003172 | 0.11198 | 0.18769 | -0.028878 | -0.12294 | 121.7204 | -0.030261 | 121.6838 | 121.656 | -0.064413 | -0.091181 | 0.087052 | 121.482 | -0.02535 | 121.6884 | 121.6081 | 0.12611 | 0.050364 | -0.16621 | 121.712 | 121.6511 | 121.8293 | 121.6292 | -0.021808 | 121.7169 | 121.7926 | 121.576 | 121.6099 | -0.26027
622.9062 | 121.9711 | -121.6507 | 0.16479 | 1.4211e-13 | -0.026831 | 0.015107 | -0.0036391 | -0.010837 | 0.020339 | -0.23296 | -0.0018566 | -0.0011944 | -0.0038435 | 0.028171 | 0.01139 | 0.069723 | 0.033457 | 0.04653 | 0.10707 | 0.03699 | 0.22896 | 0.11094 | 0.078886 | 0.000359 | 0.01233 | 0.11656 | 0.18769 | 0.026065 | -0.12294 | 121.7616 | -0.057727 | 121.7204 | 121.6972 | -0.064412 | -0.12781 | 0.064164 | 121.5278 | -0.048238 | 121.7296 | 121.663 | 0.13527 | 0.022898 | -0.13873 | 121.7578 | 121.6877 | 121.8797 | 121.6842 | -0.053853 | 121.7673 | 121.8384 | 121.6768 | 121.6511 | -0.28773
624.5781 | 121.962 | -121.6644 | 0.16022 | 1.4211e-13 | -0.027258 | 0.015107 | -0.0036391 | -0.010623 | 0.020766 | -0.22533 | -0.0020702 | -0.00055336 | -0.0040571 | 0.028384 | 0.011176 | 0.083459 | 0.0243 | 0.04653 | 0.11165 | 0.041569 | 0.22438 | 0.1201 | 0.078886 | 0.000359 | 0.007751 | 0.11656 | 0.18311 | -0.001407 | -0.11836 | 121.7845 | -0.04857 | 121.7479 | 121.711 | -0.07357 | -0.11865 | 0.064164 | 121.5461 | -0.04366 | 121.7433 | 121.6722 | 0.12611 | 0.022898 | -0.16162 | 121.7761 | 121.706 | 121.8888 | 121.6887 | -0.040117 | 121.781 | 121.8475 | 121.663 | 121.6648 | -0.27858
626.3125 | 121.9391 | -121.6461 | 0.17853 | 1.4211e-13 | -0.026831 | 0.014893 | -0.0034253 | -0.01041 | 0.020766 | -0.23296 | -0.0020702 | -0.0011944 | -0.0038435 | 0.028384 | 0.011604 | 0.083459 | 0.028878 | 0.051108 | 0.11622 | 0.041569 | 0.22896 | 0.11552 | 0.078886 | -0.00422 | 0.021487 | 0.11198 | 0.18311 | 0.016908 | -0.12752 | 121.7616 | -0.062303 | 121.7296 | 121.6972 | -0.064413 | -0.13696 | 0.050431 | 121.5186 | -0.066549 | 121.725 | 121.6676 | 0.149 | 0.004587 | -0.16162 | 121.7623 | 121.6877 | 121.8751 | 121.675 | -0.063007 | 121.7581 | 121.8292 | 121.663 | 121.6419 | -0.30605
628 | 122.0123 | -121.6232 | 0.15564 | 1.4211e-13 | -0.027045 | 0.015534 | -0.0032117 | -0.010623 | 0.020552 | -0.23296 | -0.0018566 | -0.0011944 | -0.0036299 | 0.028171 | 0.01139 | 0.07888 | 0.0243 | 0.051108 | 0.10707 | 0.046148 | 0.22438 | 0.11552 | 0.088043 | 0.004938 | 0.007751 | 0.11656 | 0.18769 | 0.035222 | -0.12752 | 121.7388 | -0.048572 | 121.7021 | 121.6743 | -0.064413 | -0.10949 | 0.068741 | 121.4957 | -0.039083 | 121.7113 | 121.631 | 0.13527 | 0.032053 | -0.12042 | 121.7303 | 121.6694 | 121.8476 | 121.6475 | -0.040119 | 121.7398 | 121.8109 | 121.6585 | 121.6282 | -0.28316
629.7344 | 122.0078 | -121.6278 | 0.15106 | 1.4211e-13 | -0.027045 | 0.015321 | -0.0032117 | -0.010623 | 0.020552 | -0.23296 | -0.0018566 | -0.00076696 | -0.0034163 | 0.028384 | 0.01139 | 0.07888 | 0.0243 | 0.041952 | 0.11165 | 0.03699 | 0.2198 | 0.11094 | 0.078886 | 0.000359 | 0.016908 | 0.11198 | 0.18311 | -0.028878 | -0.12752 | 121.7387 | -0.039415 | 121.7067 | 121.6698 | -0.06899 | -0.11407 | 0.06874 | 121.5003 | -0.039083 | 121.7067 | 121.6447 | 0.14443 | 0.032053 | -0.17994 | 121.7395 | 121.6648 | 121.8476 | 121.6521 | -0.04012 | 121.7398 | 121.8109 | 121.5989 | 121.6282 | -0.27858
631.4062 | 122.0032 | -121.6278 | 0.14648 | 1.4211e-13 | -0.026831 | 0.015534 | -0.0034253 | -0.010623 | 0.020339 | -0.24059 | -0.0018566 | -0.00076696 | -0.0038435 | 0.028384 | 0.011604 | 0.07888 | 0.0243 | 0.04653 | 0.10707 | 0.03699 | 0.22438 | 0.11094 | 0.078886 | 0.000359 | 0.016908 | 0.11656 | 0.18311 | -0.028878 | -0.12294 | 121.7387 | -0.039416 | 121.7067 | 121.6743 | -0.064412 | -0.10949 | 0.077897 | 121.5049 | -0.029927 | 121.7067 | 121.6447 | 0.13985 | 0.036631 | -0.17536 | 121.7349 | 121.6648 | 121.8522 | 121.6521 | -0.035542 | 121.7444 | 121.8109 | 121.5989 | 121.6282 | -0.26942
633.0938 | 122.0215 | -121.637 | 0.16022 | 1.4211e-13 | -0.027045 | 0.015321 | -0.0036391 | -0.010837 | 0.020339 | -0.24059 | -0.0020702 | -0.00076696 | -0.0036299 | 0.028171 | 0.01139 | 0.074302 | 0.0243 | 0.051108 | 0.10707 | 0.050727 | 0.2198 | 0.11552 | 0.088043 | 0.004938 | 0.01233 | 0.12571 | 0.18769 | -0.070086 | -0.12752 | 121.7525 | -0.053149 | 121.7113 | 121.6881 | -0.064413 | -0.10949 | 0.059585 | 121.5094 | -0.034503 | 121.725 | 121.6493 | 0.13985 | 0.027476 | -0.2303 | 121.744 | 121.6877 | 121.8568 | 121.6613 | -0.044696 | 121.7627 | 121.8247 | 121.5669 | 121.6419 | -0.28773
634.8438 | 121.9528 | -121.6507 | 0.16022 | 1.4211e-13 | -0.026831 | 0.015107 | -0.0032117 | -0.01041 | 0.020339 | -0.23296 | -0.0018566 | -0.00098076 | -0.0038435 | 0.028384 | 0.011604 | 0.088037 | 0.015142 | 0.037373 | 0.10249 | 0.046148 | 0.2198 | 0.11552 | 0.083464 | 0.000359 | 0.01233 | 0.11198 | 0.18769 | 0.021486 | -0.12752 | 121.7662 | -0.057727 | 121.7387 | 121.6881 | -0.078148 | -0.11407 | 0.059585 | 121.5232 | -0.048238 | 121.7342 | 121.663 | 0.13985 | 0.027476 | -0.13873 | 121.7532 | 121.6968 | 121.8705 | 121.6658 | -0.044696 | 121.7627 | 121.8384 | 121.6722 | 121.6511 | -0.28773
636.5156 | 121.9528 | -121.6736 | 0.16937 | 1.4211e-13 | -0.026831 | 0.015321 | -0.0036391 | -0.010623 | 0.020552 | -0.23296 | -0.0020702 | -0.00098076 | -0.0040571 | 0.028384 | 0.01139 | 0.083459 | 0.015142 | 0.051108 | 0.11165 | 0.041569 | 0.2198 | 0.11094 | 0.083464 | 0.000359 | 0.007751 | 0.11656 | 0.18769 | 0.012329 | -0.11836 | 121.7845 | -0.057726 | 121.757 | 121.7247 | -0.059834 | -0.1278 | 0.050429 | 121.5552 | -0.052816 | 121.757 | 121.6813 | 0.12611 | 0.01832 | -0.15704 | 121.7852 | 121.7152 | 121.8934 | 121.6887 | -0.058431 | 121.7901 | 121.8613 | 121.6859 | 121.6739 | -0.28773
638.2656 | 122.0352 | -121.6415 | 0.13275 | 1.4211e-13 | -0.026831 | 0.015321 | -0.0034253 | -0.010623 | 0.020125 | -0.24059 | -0.0018566 | -0.00076696 | -0.0036299 | 0.028598 | 0.011604 | 0.083459 | 0.019721 | 0.032795 | 0.10249 | 0.023254 | 0.22896 | 0.11552 | 0.078886 | 0.000359 | 0.007751 | 0.1074 | 0.18769 | -0.038035 | -0.12294 | 121.7571 | -0.030261 | 121.725 | 121.6743 | -0.082726 | -0.1095 | 0.096208 | 121.5186 | -0.02535 | 121.7204 | 121.6493 | 0.13069 | 0.054942 | -0.17079 | 121.744 | 121.6648 | 121.8705 | 121.6613 | -0.01723 | 121.7489 | 121.8292 | 121.6035 | 121.6419 | -0.25569
640 | 121.8887 | -121.7285 | 0.19684 | 1.4211e-13 | -0.026831 | 0.015107 | -0.0034253 | -0.010623 | 0.020339 | -0.22533 | -0.0018566 | -0.00098076 | -0.0036299 | 0.028384 | 0.011176 | 0.083459 | 0.0243 | 0.051108 | 0.10707 | 0.03699 | 0.22438 | 0.11552 | 0.092622 | 0.004938 | 0.021487 | 0.11656 | 0.17854 | -0.001407 | -0.12294 | 121.844 | -0.08977 | 121.812 | 121.7796 | -0.064413 | -0.15985 | 0.027543 | 121.6056 | -0.080281 | 121.8211 | 121.75 | 0.14443 | -0.018302 | -0.19825 | 121.8356 | 121.7655 | 121.9529 | 121.7528 | -0.081317 | 121.8451 | 121.9071 | 121.7271 | 121.7335 | -0.31978
641.6562 | 122.0169 | -121.6599 | 0.12817 | 1.4211e-13 | -0.027045 | 0.015321 | -0.0036391 | -0.010623 | 0.020339 | -0.22533 | -0.0018566 | -0.0011944 | -0.0036299 | 0.028598 | 0.011604 | 0.07888 | 0.019721 | 0.04653 | 0.10707 | 0.046148 | 0.22896 | 0.11552 | 0.074307 | -0.00422 | 0.007751 | 0.1074 | 0.17854 | -0.038035 | -0.12294 | 121.7754 | -0.021106 | 121.7387 | 121.7064 | -0.068991 | -0.082026 | 0.10078 | 121.5369 | -0.020773 | 121.7342 | 121.6676 | 0.13069 | 0.050362 | -0.16621 | 121.7669 | 121.706 | 121.8888 | 121.6796 | -0.012653 | 121.7673 | 121.8384 | 121.6218 | 121.6556 | -0.25111
643.4062 | 122.0215 | -121.6736 | 0.14191 | 1.4211e-13 | -0.027045 | 0.015534 | -0.0032117 | -0.011264 | 0.020339 | -0.24822 | 0.0024162 | -0.00076696 | -0.0038435 | 0.028598 | 0.011817 | 0.07888 | 0.019721 | 0.04653 | 0.10707 | 0.03699 | 0.2198 | 0.11552 | 0.083464 | -0.00422 | 0.01233 | 0.098244 | 0.16938 | -0.065507 | -0.12294 | 121.7891 | -0.034839 | 121.7525 | 121.7201 | -0.068991 | -0.10492 | 0.077895 | 121.5506 | -0.043663 | 121.757 | 121.6859 | 0.13527 | 0.027472 | -0.20741 | 121.7807 | 121.7106 | 121.8934 | 121.6933 | -0.026386 | 121.7718 | 121.843 | 121.6081 | 121.6694 | -0.26485
645.0781 | 122.0261 | -121.6599 | 0.15106 | 1.4211e-13 | -0.027045 | 0.015321 | -0.0032117 | -0.010623 | 0.020552 | -0.2177 | -0.0014292 | -0.00098076 | -0.0040571 | 0.029025 | 0.010963 | 0.083459 | 0.0243 | 0.051108 | 0.10707 | 0.041569 | 0.23354 | 0.11094 | 0.078886 | 0.009516 | 0.016908 | 0.10282 | 0.16938 | -0.051771 | -0.12752 | 121.7708 | -0.043994 | 121.7433 | 121.711 | -0.059834 | -0.10949 | 0.082476 | 121.5323 | -0.04824 | 121.7387 | 121.6768 | 0.14443 | 0.018317 | -0.20283 | 121.7669 | 121.7014 | 121.8934 | 121.6842 | -0.04012 | 121.7627 | 121.8292 | 121.6081 | 121.6694 | -0.27858
646.8125 | 122.0215 | -121.6873 | 0.13733 | 1.4211e-13 | -0.027258 | 0.015321 | -0.0034253 | -0.010623 | 0.020339 | -0.23296 | 0.0034844 | -0.00076696 | -0.0038435 | 0.028598 | 0.01139 | 0.083459 | 0.028878 | 0.051108 | 0.11165 | 0.018675 | 0.22438 | 0.10636 | 0.078886 | 0.004938 | 0.007751 | 0.093665 | 0.1648 | -0.12503 | -0.12294 | 121.7937 | -0.025682 | 121.7708 | 121.7384 | -0.055255 | -0.11865 | 0.087052 | 121.5644 | -0.043664 | 121.7662 | 121.6951 | 0.13069 | 0.027471 | -0.26236 | 121.799 | 121.706 | 121.9117 | 121.7162 | -0.030966 | 121.781 | 121.8521 | 121.5623 | 121.6923 | -0.26027
648.5469 | 121.9025 | -121.7239 | 0.16022 | 1.4211e-13 | -0.027045 | 0.015107 | -0.0034253 | -0.010837 | 0.020125 | -0.2177 | 0.017157 | -0.00098076 | -0.0036299 | 0.028598 | 0.01139 | 0.074302 | 0.0243 | 0.04653 | 0.10249 | 0.03699 | 0.22896 | 0.11552 | 0.078886 | 0.000359 | 0.007751 | 0.07993 | 0.14191 | -0.14792 | -0.12294 | 121.8395 | -0.057727 | 121.7982 | 121.7705 | -0.068991 | -0.12323 | 0.068742 | 121.601 | -0.080287 | 121.8028 | 121.7317 | 0.13069 | -0.01831 | -0.30814 | 121.8264 | 121.7609 | 121.9529 | 121.7482 | -0.044696 | 121.8039 | 121.8658 | 121.576 | 121.7243 | -0.28316
650.2188 | 121.9803 | -121.7056 | 0.13275 | 1.4211e-13 | -0.026831 | 0.015107 | -0.0032117 | -0.010837 | 0.020339 | -0.23296 | 0.01673 | -0.00098076 | -0.0038435 | 0.028812 | 0.011176 | 0.088037 | 0.015142 | 0.051108 | 0.10249 | 0.032411 | 0.21522 | 0.11552 | 0.074307 | 0.004938 | 0.003172 | 0.075351 | 0.14191 | -0.14334 | -0.12752 | 121.8211 | -0.030261 | 121.7937 | 121.7567 | -0.064413 | -0.10034 | 0.082473 | 121.5781 | -0.0574 | 121.7799 | 121.7088 | 0.13069 | 0.009156 | -0.27609 | 121.8081 | 121.738 | 121.9209 | 121.7208 | -0.01723 | 121.781 | 121.8475 | 121.5623 | 121.7106 | -0.26027
651.9688 | 122.0078 | -121.6873 | 0.10071 | 1.4211e-13 | -0.026831 | 0.015107 | -0.0029979 | -0.010837 | 0.020125 | -0.2177 | 0.01673 | -0.00076696 | -0.0036299 | 0.028812 | 0.01139 | 0.083459 | 0.019721 | 0.04653 | 0.10707 | 0.03699 | 0.22438 | 0.11552 | 0.074307 | 0.000359 | 0.007751 | 0.07993 | 0.14649 | -0.14334 | -0.12752 | 121.8028 | 0.00636 | 121.7708 | 121.7338 | -0.068991 | -0.063718 | 0.12367 | 121.5598 | -0.020778 | 121.7616 | 121.6951 | 0.13527 | 0.045778 | -0.24405 | 121.7944 | 121.7243 | 121.9117 | 121.707 | 0.014813 | 121.7672 | 121.8338 | 121.544 | 121.6877 | -0.22823
653.7188 | 121.9986 | -121.7102 | 0.14191 | 1.4211e-13 | -0.027258 | 0.015321 | -0.0034253 | -0.010623 | 0.020125 | -0.24059 | 0.016303 | -0.0011944 | -0.0036299 | 0.028384 | 0.011604 | 0.083459 | 0.033457 | 0.055687 | 0.10249 | 0.03699 | 0.2198 | 0.1201 | 0.078886 | 0.004938 | 0.016908 | 0.084508 | 0.14649 | -0.13876 | -0.11836 | 121.8303 | -0.039417 | 121.7937 | 121.7659 | -0.064413 | -0.10492 | 0.077895 | 121.5918 | -0.057399 | 121.7891 | 121.7271 | 0.13527 | 0.004579 | -0.28067 | 121.8127 | 121.7472 | 121.93 | 121.7437 | -0.021807 | 121.7947 | 121.8567 | 121.5714 | 121.7151 | -0.26027
655.4062 | 122.0078 | -121.6873 | 0.13275 | 1.4211e-13 | -0.027258 | 0.015107 | -0.0034253 | -0.010623 | 0.020125 | -0.23296 | 0.015662 | -0.00098076 | -0.0036299 | 0.028812 | 0.011604 | 0.083459 | 0.028878 | 0.04653 | 0.10707 | 0.046148 | 0.23354 | 0.11094 | 0.078886 | 0.004938 | 0.01233 | 0.075351 | 0.14649 | -0.13419 | -0.12294 | 121.7983 | -0.025683 | 121.7708 | 121.7338 | -0.064412 | -0.086603 | 0.10079 | 121.5644 | -0.0574 | 121.7662 | 121.6996 | 0.13527 | 0.013735 | -0.26694 | 121.7944 | 121.7335 | 121.9209 | 121.7162 | -0.021809 | 121.7627 | 121.8338 | 121.5531 | 121.6923 | -0.25569
657.1406 | 121.9986 | -121.6919 | 0.1236 | 1.4211e-13 | -0.027045 | 0.015107 | -0.0036391 | -0.011051 | 0.020125 | -0.23296 | 0.01438 | -0.00098076 | -0.0036299 | 0.028812 | 0.011604 | 0.083459 | 0.028878 | 0.051108 | 0.11165 | 0.050727 | 0.22896 | 0.11552 | 0.083464 | 0.000359 | 0.01233 | 0.075351 | 0.14191 | -0.14792 | -0.12294 | 121.8074 | -0.011949 | 121.7754 | 121.743 | -0.064413 | -0.072869 | 0.10536 | 121.569 | -0.048245 | 121.7754 | 121.7042 | 0.13527 | 0.018311 | -0.27152 | 121.8035 | 121.7426 | 121.9209 | 121.7208 | -0.008075 | 121.7672 | 121.8338 | 121.544 | 121.6923 | -0.24654
658.8906 | 121.9894 | -121.6965 | 0.13733 | 1.4211e-13 | -0.027472 | 0.015107 | -0.0029979 | -0.010837 | 0.020125 | -0.23296 | 0.015448 | -0.00098076 | -0.0038435 | 0.028812 | 0.010963 | 0.07888 | 0.019721 | 0.041952 | 0.11165 | 0.018675 | 0.22438 | 0.1201 | 0.078886 | 0.004938 | 0.01233 | 0.07993 | 0.14649 | -0.12503 | -0.11836 | 121.8166 | -0.025682 | 121.7754 | 121.7384 | -0.078148 | -0.11865 | 0.087052 | 121.5781 | -0.057399 | 121.7754 | 121.7088 | 0.13069 | 0.009157 | -0.26236 | 121.8081 | 121.7151 | 121.9209 | 121.7162 | -0.017229 | 121.7764 | 121.843 | 121.5714 | 121.7014 | -0.25569
660.5625 | 121.9894 | -121.6919 | 0.13733 | 1.4211e-13 | -0.027045 | 0.015321 | -0.0034253 | -0.011051 | 0.020766 | -0.22533 | 0.015234 | -0.001408 | -0.0036299 | 0.028812 | 0.01139 | 0.07888 | 0.033457 | 0.041952 | 0.11165 | 0.046148 | 0.22896 | 0.11094 | 0.078886 | -0.00422 | 0.01233 | 0.07993 | 0.14649 | -0.13876 | -0.11378 | 121.8028 | -0.025682 | 121.7708 | 121.7338 | -0.06899 | -0.091181 | 0.09163 | 121.5781 | -0.057399 | 121.7708 | 121.7042 | 0.12611 | 0.009157 | -0.27609 | 121.8035 | 121.738 | 121.9209 | 121.7254 | -0.026387 | 121.7718 | 121.8384 | 121.5531 | 121.6877 | -0.25111
662.2969 | 121.9894 | -121.7148 | 0.13275 | 1.4211e-13 | -0.027045 | 0.015107 | -0.0034253 | -0.010837 | 0.020339 | -0.24822 | 0.015234 | -0.00076696 | -0.0036299 | 0.028598 | 0.01139 | 0.083459 | 0.0243 | 0.037373 | 0.10249 | 0.046148 | 0.23354 | 0.1201 | 0.088043 | -0.013377 | 0.003172 | 0.075351 | 0.15107 | -0.14792 | -0.1321 | 121.8349 | -0.030261 | 121.7982 | 121.7522 | -0.082727 | -0.086603 | 0.10079 | 121.5827 | -0.0574 | 121.8028 | 121.718 | 0.13527 | 0.018314 | -0.28067 | 121.8173 | 121.7609 | 121.9483 | 121.7391 | -0.012651 | 121.7901 | 121.8658 | 121.5669 | 121.7014 | -0.26485
664.0312 | 121.907 | -121.7514 | 0.15106 | 1.4211e-13 | -0.027258 | 0.015534 | -0.0034253 | -0.010623 | 0.020339 | -0.24059 | 0.016089 | -0.00098076 | -0.0036299 | 0.028598 | 0.010963 | 0.083459 | 0.0243 | 0.04653 | 0.11165 | 0.032411 | 0.22438 | 0.1201 | 0.083464 | -0.008798 | 0.016908 | 0.075351 | 0.14191 | -0.13876 | -0.11378 | 121.8715 | -0.039415 | 121.8349 | 121.7979 | -0.07357 | -0.11865 | 0.073319 | 121.6376 | -0.075711 | 121.8349 | 121.7683 | 0.13069 | -0.009155 | -0.28983 | 121.8631 | 121.7838 | 121.9758 | 121.7757 | -0.030962 | 121.8268 | 121.8933 | 121.6126 | 121.7426 | -0.26484
665.7812 | 121.8933 | -121.7377 | 0.16022 | 1.4211e-13 | -0.027258 | 0.015107 | -0.0036391 | -0.010623 | 0.020125 | -0.23296 | 0.016516 | -0.00076696 | -0.0038435 | 0.029025 | 0.01139 | 0.083459 | 0.028878 | 0.032795 | 0.11165 | 0.03699 | 0.23354 | 0.11552 | 0.078886 | -0.008798 | 0.007751 | 0.07993 | 0.15107 | -0.14334 | -0.12752 | 121.8532 | -0.04857 | 121.8211 | 121.7705 | -0.082726 | -0.12323 | 0.073321 | 121.6102 | -0.080287 | 121.8166 | 121.7454 | 0.13527 | -0.009152 | -0.30356 | 121.8493 | 121.7747 | 121.9712 | 121.7665 | -0.044696 | 121.8176 | 121.8887 | 121.5943 | 121.7289 | -0.28773
667.5156 | 121.8842 | -121.7239 | 0.15564 | 1.4211e-13 | -0.027472 | 0.014893 | -0.0032117 | -0.010837 | 0.020552 | -0.24059 | 0.016303 | -0.0011944 | -0.0036299 | 0.029239 | 0.011604 | 0.083459 | 0.033457 | 0.041952 | 0.11165 | 0.027833 | 0.22896 | 0.1201 | 0.078886 | -0.017956 | 0.003172 | 0.075351 | 0.14649 | -0.14792 | -0.12752 | 121.844 | -0.043993 | 121.8074 | 121.7659 | -0.078148 | -0.12781 | 0.073319 | 121.5964 | -0.080289 | 121.8028 | 121.7271 | 0.13069 | -0.009154 | -0.30356 | 121.8356 | 121.7518 | 121.9529 | 121.7574 | -0.03554 | 121.7993 | 121.8704 | 121.576 | 121.706 | -0.28316
669.1875 | 121.9849 | -121.6919 | 0.09613 | 1.4211e-13 | -0.027258 | 0.015107 | -0.0032117 | -0.011264 | 0.020125 | -0.23296 | 0.016516 | -0.0011944 | -0.0036299 | 0.029025 | 0.01139 | 0.083459 | 0.0243 | 0.037373 | 0.11165 | 0.032411 | 0.23812 | 0.11094 | 0.083464 | -0.017956 | 0.007751 | 0.084508 | 0.13733 | -0.14334 | -0.12752 | 121.8028 | 0.015517 | 121.7754 | 121.7293 | -0.073569 | -0.063719 | 0.14199 | 121.5644 | -0.011622 | 121.7754 | 121.6996 | 0.13527 | 0.041199 | -0.23947 | 121.8035 | 121.7243 | 121.93 | 121.7162 | 0.014812 | 121.7764 | 121.8292 | 121.5486 | 121.6739 | -0.22365
670.9375 | 121.8979 | -121.7422 | 0.15106 | 1.4211e-13 | -0.027258 | 0.015107 | -0.0036391 | -0.011051 | 0.020339 | -0.24059 | 0.015875 | -0.00098076 | -0.0038435 | 0.029025 | 0.01139 | 0.083459 | 0.019721 | 0.028217 | 0.10249 | 0.018675 | 0.21522 | 0.11552 | 0.083464 | -0.017956 | 0.007751 | 0.07993 | 0.14649 | -0.14334 | -0.12294 | 121.8578 | -0.048572 | 121.8257 | 121.7705 | -0.087304 | -0.13239 | 0.064162 | 121.6193 | -0.071132 | 121.8257 | 121.75 | 0.13069 | -0.004576 | -0.29441 | 121.8447 | 121.7609 | 121.9575 | 121.762 | -0.035541 | 121.8222 | 121.8887 | 121.5989 | 121.7243 | -0.274
672.6094 | 121.9345 | -121.7285 | 0.13733 | 1.4211e-13 | -0.027472 | 0.015107 | -0.0034253 | -0.010623 | 0.020125 | -0.24059 | 0.016303 | -0.00076696 | -0.0038435 | 0.028598 | 0.011176 | 0.088037 | 0.028878 | 0.032795 | 0.1208 | 0.041569 | 0.23354 | 0.12468 | 0.083464 | -0.022535 | 0.007751 | 0.075351 | 0.14191 | -0.14792 | -0.11836 | 121.8532 | -0.016525 | 121.8166 | 121.7613 | -0.091884 | -0.09576 | 0.096209 | 121.6102 | -0.061978 | 121.812 | 121.7363 | 0.12611 | 0.004578 | -0.28525 | 121.8493 | 121.7701 | 121.9621 | 121.7574 | -0.01265 | 121.8039 | 121.8704 | 121.5806 | 121.706 | -0.25569
674.3594 | 121.9528 | -121.7239 | 0.12817 | 1.4211e-13 | -0.027258 | 0.015107 | -0.0032117 | -0.010837 | 0.020125 | -0.23296 | 0.016089 | -0.00098076 | -0.0038435 | 0.029239 | 0.01139 | 0.07888 | 0.019721 | 0.032795 | 0.10707 | 0.03699 | 0.22438 | 0.11094 | 0.083464 | -0.013377 | 0.016908 | 0.084508 | 0.14191 | -0.13419 | -0.11836 | 121.8349 | -0.021106 | 121.8028 | 121.7567 | -0.078147 | -0.091184 | 0.096207 | 121.6056 | -0.043666 | 121.8074 | 121.7408 | 0.13527 | 0.013733 | -0.26236 | 121.831 | 121.7609 | 121.9483 | 121.7437 | -0.017232 | 121.8084 | 121.8658 | 121.5898 | 121.7106 | -0.24654
676.1094 | 121.9391 | -121.7194 | 0.15564 | 1.4211e-13 | -0.027258 | 0.015107 | -0.0034253 | -0.010837 | 0.020339 | -0.23296 | 0.015662 | -0.0011944 | -0.0038435 | 0.029025 | 0.01139 | 0.088037 | 0.028878 | 0.032795 | 0.10707 | 0.041569 | 0.22438 | 0.11552 | 0.074307 | -0.017956 | 0.01233 | 0.070773 | 0.14649 | -0.13876 | -0.12752 | 121.8349 | -0.048572 | 121.8074 | 121.7522 | -0.082726 | -0.11407 | 0.068741 | 121.5918 | -0.084867 | 121.7937 | 121.7317 | 0.13985 | -0.009154 | -0.29441 | 121.8264 | 121.7609 | 121.9437 | 121.7482 | -0.040119 | 121.7901 | 121.8658 | 121.5806 | 121.7014 | -0.28316
677.8594 | 121.994 | -121.7148 | 0.1236 | 1.4211e-13 | -0.027258 | 0.015321 | -0.0032117 | -0.010837 | 0.019911 | -0.23296 | 0.016303 | -0.0011944 | -0.0038435 | 0.029025 | 0.01139 | 0.07888 | 0.0243 | 0.037373 | 0.11165 | 0.03699 | 0.23354 | 0.12468 | 0.083464 | -0.008798 | 0.016908 | 0.084508 | 0.14191 | -0.13419 | -0.12752 | 121.8395 | -0.011949 | 121.7937 | 121.7522 | -0.087306 | -0.086606 | 0.10994 | 121.5873 | -0.039088 | 121.7982 | 121.7317 | 0.14443 | 0.018311 | -0.25778 | 121.8264 | 121.7518 | 121.9483 | 121.7391 | 0.001083 | 121.7993 | 121.8567 | 121.5806 | 121.706 | -0.25111
679.5938 | 121.9894 | -121.7194 | 0.12817 | 1.4211e-13 | -0.027472 | 0.014893 | -0.0034253 | -0.011051 | 0.020339 | -0.23296 | 0.015662 | -0.00098076 | -0.0038435 | 0.028812 | 0.011176 | 0.07888 | 0.028878 | 0.032795 | 0.11165 | 0.018675 | 0.22438 | 0.1201 | 0.078886 | -0.013377 | 0.01233 | 0.075351 | 0.13733 | -0.14792 | -0.12294 | 121.8395 | -0.016527 | 121.7982 | 121.7522 | -0.087305 | -0.1095 | 0.096207 | 121.5964 | -0.052823 | 121.7982 | 121.7317 | 0.13527 | 0.009155 | -0.2761 | 121.831 | 121.738 | 121.9437 | 121.7482 | -0.008074 | 121.7947 | 121.8567 | 121.5714 | 121.706 | -0.25111
681.2656 | 122.0261 | -121.6736 | 0.12817 | 1.4211e-13 | -0.027686 | 0.015107 | -0.0034253 | -0.010837 | 0.020339 | -0.23296 | 0.015234 | -0.00098076 | -0.0036299 | 0.028812 | 0.01139 | 0.083459 | 0.0243 | 0.032795 | 0.10707 | 0.009517 | 0.22896 | 0.1201 | 0.078886 | -0.008798 | 0.01233 | 0.07993 | 0.14649 | -0.13876 | -0.12752 | 121.7937 | -0.021106 | 121.757 | 121.7064 | -0.087305 | -0.11866 | 0.10078 | 121.5461 | -0.048244 | 121.7525 | 121.6859 | 0.13985 | 0.018312 | -0.26694 | 121.7807 | 121.6831 | 121.9025 | 121.6979 | -0.008074 | 121.7535 | 121.8201 | 121.5348 | 121.6648 | -0.25569
683 | 121.9254 | -121.6965 | 0.16479 | 1.4211e-13 | -0.027472 | 0.015107 | -0.0034253 | -0.011051 | 0.019911 | -0.23296 | -0.0018566 | -0.00098076 | -0.0040571 | 0.028812 | 0.01139 | 0.07888 | 0.028878 | 0.028217 | 0.11165 | 0.041569 | 0.22438 | 0.11552 | 0.078886 | -0.013377 | 0.007751 | 0.098244 | 0.1648 | -0.12961 | -0.12294 | 121.812 | -0.053148 | 121.7754 | 121.7247 | -0.087304 | -0.12323 | 0.059586 | 121.5735 | -0.066551 | 121.7754 | 121.7042 | 0.13069 | 5e-06 | -0.2944 | 121.8081 | 121.738 | 121.9209 | 121.7254 | -0.049274 | 121.7947 | 121.8613 | 121.5669 | 121.6831 | -0.28773
684.75 | 121.9482 | -121.7285 | 0.13733 | 1.4211e-13 | -0.027472 | 0.015321 | -0.0034253 | -0.010837 | 0.020125 | -0.24059 | 0.01203 | -0.00098076 | -0.0036299 | 0.029025 | 0.01139 | 0.083459 | 0.0243 | 0.023639 | 0.11165 | 0.041569 | 0.22438 | 0.11552 | 0.078886 | -0.013377 | 0.007751 | 0.084508 | 0.15564 | -0.14334 | -0.12294 | 121.844 | -0.025682 | 121.812 | 121.7522 | -0.091882 | -0.09576 | 0.087052 | 121.6056 | -0.052821 | 121.8074 | 121.7363 | 0.13069 | 0.018314 | -0.28067 | 121.8402 | 121.7701 | 121.9529 | 121.7528 | -0.021808 | 121.813 | 121.8842 | 121.5852 | 121.7151 | -0.26027
686.4219 | 122.0261 | -121.6965 | 0.11444 | 1.4211e-13 | -0.027686 | 0.015107 | -0.0034253 | -0.010623 | 0.020125 | -0.24059 | 0.015021 | -0.0011944 | -0.0036299 | 0.029453 | 0.011176 | 0.083459 | 0.0243 | 0.041952 | 0.10249 | 0.041569 | 0.23354 | 0.11094 | 0.083464 | -0.013377 | 0.01233 | 0.07993 | 0.15107 | -0.13876 | -0.12294 | 121.8074 | -0.011951 | 121.7799 | 121.7384 | -0.06899 | -0.072872 | 0.1191 | 121.5735 | -0.034511 | 121.7799 | 121.7088 | 0.13527 | 0.036624 | -0.25321 | 121.799 | 121.738 | 121.93 | 121.7208 | -0.003499 | 121.7764 | 121.8475 | 121.5577 | 121.6831 | -0.23738
688.1562 | 122.0123 | -121.7102 | 0.11444 | 1.4211e-13 | -0.027258 | 0.014893 | -0.0032117 | -0.011051 | 0.019911 | -0.23296 | 0.014594 | -0.0011944 | -0.0038435 | 0.029239 | 0.011176 | 0.083459 | 0.028878 | 0.032795 | 0.10707 | 0.03699 | 0.23354 | 0.1201 | 0.074307 | -0.008798 | 0.01233 | 0.070773 | 0.15107 | -0.14334 | -0.12752 | 121.8303 | -0.007373 | 121.7937 | 121.743 | -0.087305 | -0.077451 | 0.1191 | 121.5827 | -0.043668 | 121.7845 | 121.7225 | 0.13985 | 0.036624 | -0.25778 | 121.8173 | 121.7472 | 121.9437 | 121.7391 | 0.005659 | 121.781 | 121.8613 | 121.5669 | 121.7014 | -0.24196
689.9062 | 122.0078 | -121.7285 | 0.11902 | 1.4211e-13 | -0.027899 | 0.015107 | -0.0032117 | -0.010837 | 0.020125 | -0.23296 | 0.014807 | -0.00076696 | -0.0038435 | 0.029025 | 0.01139 | 0.088037 | 0.0243 | 0.023639 | 0.10707 | 0.03699 | 0.22896 | 0.11094 | 0.088043 | -0.008798 | 0.016908 | 0.07993 | 0.15107 | -0.13419 | -0.12294 | 121.8395 | -0.011951 | 121.8166 | 121.7522 | -0.087303 | -0.082029 | 0.10994 | 121.6056 | -0.039089 | 121.8166 | 121.7454 | 0.13985 | 0.032046 | -0.25321 | 121.8356 | 121.7655 | 121.9575 | 121.7528 | -0.008077 | 121.8084 | 121.8796 | 121.5943 | 121.7197 | -0.24196
691.5781 | 122.0261 | -121.6965 | 0.1236 | 1.4211e-13 | -0.027472 | 0.015321 | -0.0038527 | -0.010837 | 0.020339 | -0.23296 | 0.014807 | -0.00076696 | -0.0038435 | 0.029453 | 0.011176 | 0.074302 | 0.019721 | 0.028217 | 0.10707 | 0.046148 | 0.22896 | 0.1201 | 0.078886 | -0.008798 | 0.01233 | 0.07993 | 0.15107 | -0.13419 | -0.12294 | 121.8166 | -0.016528 | 121.7708 | 121.7247 | -0.091883 | -0.077448 | 0.10536 | 121.5735 | -0.043666 | 121.7754 | 121.7088 | 0.13527 | 0.027469 | -0.25778 | 121.8035 | 121.7426 | 121.9254 | 121.7162 | -0.003496 | 121.7764 | 121.8475 | 121.5623 | 121.6877 | -0.24654
693.3281 | 121.9711 | -121.7331 | 0.14191 | 1.4211e-13 | -0.027472 | 0.014893 | -0.0034253 | -0.010623 | 0.020339 | -0.23296 | -0.0020702 | -0.0011944 | -0.0036299 | 0.028812 | 0.01139 | 0.083459 | 0.028878 | 0.023639 | 0.11165 | 0.046148 | 0.22896 | 0.12468 | 0.088043 | -0.00422 | 0.007751 | 0.093665 | 0.16022 | -0.13419 | -0.12294 | 121.8578 | -0.03026 | 121.8166 | 121.7567 | -0.10104 | -0.095759 | 0.087052 | 121.6102 | -0.048242 | 121.8211 | 121.7408 | 0.13069 | 0.018315 | -0.27609 | 121.8447 | 121.7792 | 121.9621 | 121.762 | -0.017228 | 121.8268 | 121.8933 | 121.5989 | 121.7289 | -0.26485
695.0156 | 121.9254 | -121.7514 | 0.17395 | 1.4211e-13 | -0.027686 | 0.015107 | -0.0036391 | -0.010837 | 0.019911 | -0.22533 | -0.0018566 | -0.00098076 | -0.0038435 | 0.028812 | 0.010963 | 0.07888 | 0.0243 | 0.023639 | 0.10707 | 0.03699 | 0.22438 | 0.11552 | 0.083464 | -0.013377 | 0.01233 | 0.093665 | 0.1648 | -0.12961 | -0.12294 | 121.8669 | -0.066882 | 121.8303 | 121.775 | -0.091882 | -0.13696 | 0.050431 | 121.6285 | -0.080285 | 121.8349 | 121.7637 | 0.13527 | -0.00915 | -0.30356 | 121.8585 | 121.7884 | 121.9758 | 121.7757 | -0.058429 | 121.8451 | 121.9162 | 121.6218 | 121.738 | -0.29689
696.75 | 121.9254 | -121.7514 | 0.15106 | 1.4211e-13 | -0.026831 | 0.015321 | -0.0036391 | -0.011264 | 0.019911 | -0.24059 | 0.014594 | -0.00076696 | -0.0042707 | 0.029025 | 0.011176 | 0.083459 | 0.0243 | 0.028217 | 0.10249 | 0.050727 | 0.22896 | 0.11094 | 0.074307 | -0.013377 | 0.016908 | 0.07993 | 0.15107 | -0.14792 | -0.12752 | 121.8623 | -0.048572 | 121.8349 | 121.7796 | -0.082725 | -0.10034 | 0.077897 | 121.6239 | -0.071132 | 121.8257 | 121.7683 | 0.14443 | 3e-06 | -0.29898 | 121.8539 | 121.8021 | 121.9804 | 121.7757 | -0.04012 | 121.8313 | 121.9025 | 121.6035 | 121.738 | -0.27858
698.5 | 121.9666 | -121.7239 | 0.13275 | 1.4211e-13 | -0.027472 | 0.014893 | -0.0032117 | -0.011264 | 0.020125 | -0.22533 | 0.013953 | -0.00076696 | -0.0038435 | 0.029239 | 0.01139 | 0.07888 | 0.0243 | 0.032795 | 0.11622 | 0.018675 | 0.22438 | 0.11552 | 0.078886 | -0.008798 | 0.016908 | 0.075351 | 0.14649 | -0.1525 | -0.12294 | 121.8395 | -0.016526 | 121.8028 | 121.7567 | -0.082726 | -0.11408 | 0.09163 | 121.601 | -0.0574 | 121.8028 | 121.7408 | 0.13985 | 0.013735 | -0.28525 | 121.8402 | 121.7426 | 121.9483 | 121.7482 | -0.01723 | 121.7993 | 121.8704 | 121.5714 | 121.7151 | -0.25569
700.2344 | 121.994 | -121.6827 | 0.13275 | 1.4211e-13 | -0.027472 | 0.015107 | -0.0032117 | -0.010837 | 0.020339 | -0.2177 | -0.0020702 | -0.00098076 | -0.0038435 | 0.029239 | 0.01139 | 0.07888 | 0.0243 | 0.023639 | 0.11165 | 0.050727 | 0.22438 | 0.12468 | 0.092622 | -0.013377 | 0.026066 | 0.089087 | 0.16022 | -0.13876 | -0.11378 | 121.8074 | -0.021104 | 121.7616 | 121.7064 | -0.10104 | -0.082024 | 0.09163 | 121.569 | -0.043664 | 121.7754 | 121.7088 | 0.13985 | 0.027471 | -0.27152 | 121.7944 | 121.7335 | 121.9071 | 121.707 | -0.008072 | 121.7718 | 121.843 | 121.544 | 121.6694 | -0.24653
701.9219 | 121.9849 | -121.7148 | 0.15106 | 1.4211e-13 | -0.027686 | 0.01468 | -0.0034253 | -0.011051 | 0.020339 | -0.23296 | 0.001348 | -0.00098076 | -0.0044845 | 0.029025 | 0.01139 | 0.07888 | 0.028878 | 0.028217 | 0.1208 | 0.046148 | 0.22896 | 0.11552 | 0.092622 | -0.017956 | 0.021487 | 0.089087 | 0.14649 | -0.12045 | -0.11378 | 121.8303 | -0.030258 | 121.7937 | 121.743 | -0.087304 | -0.10491 | 0.077897 | 121.601 | -0.061975 | 121.8074 | 121.7363 | 0.13527 | -0.004576 | -0.27151 | 121.8356 | 121.7609 | 121.9437 | 121.7437 | -0.035541 | 121.8039 | 121.8613 | 121.5943 | 121.6968 | -0.26484
703.6719 | 121.9345 | -121.7285 | 0.16937 | 1.4211e-13 | -0.027472 | 0.015107 | -0.0032117 | -0.010837 | 0.019911 | -0.22533 | 0.0039116 | -0.00098076 | -0.0038435 | 0.029025 | 0.010749 | 0.074302 | 0.0243 | 0.028217 | 0.10707 | 0.046148 | 0.22896 | 0.11552 | 0.088043 | -0.00422 | 0.026066 | 0.084508 | 0.15564 | -0.14334 | -0.11836 | 121.844 | -0.062305 | 121.8028 | 121.7567 | -0.087304 | -0.12323 | 0.059586 | 121.6102 | -0.084865 | 121.8166 | 121.7546 | 0.14443 | -0.01373 | -0.31272 | 121.8356 | 121.7747 | 121.9575 | 121.7528 | -0.053852 | 121.813 | 121.8842 | 121.5852 | 121.7243 | -0.28773
705.4219 | 121.907 | -121.7422 | 0.17853 | 1.4211e-13 | -0.027258 | 0.014893 | -0.0034253 | -0.011051 | 0.020125 | -0.23296 | 0.011603 | -0.00055336 | -0.0036299 | 0.029453 | 0.011176 | 0.07888 | 0.0243 | 0.032795 | 0.10249 | 0.046148 | 0.22438 | 0.11552 | 0.078886 | -0.00422 | 0.007751 | 0.089087 | 0.15107 | -0.13876 | -0.12294 | 121.8578 | -0.076038 | 121.8211 | 121.775 | -0.082726 | -0.13238 | 0.045853 | 121.6193 | -0.089441 | 121.8211 | 121.75 | 0.13069 | -0.027463 | -0.31729 | 121.8447 | 121.7884 | 121.9666 | 121.7665 | -0.063007 | 121.8313 | 121.8933 | 121.6035 | 121.738 | -0.30147
707.1406 | 122.0352 | -121.7102 | 0.10071 | 1.4211e-13 | -0.027472 | 0.015534 | -0.0032117 | -0.011264 | 0.020339 | -0.23296 | 0.0098936 | -0.001408 | -0.0038435 | 0.029453 | 0.011176 | 0.088037 | 0.028878 | 0.028217 | 0.11622 | 0.050727 | 0.22896 | 0.1201 | 0.088043 | -0.013377 | 0.021487 | 0.084508 | 0.15107 | -0.13876 | -0.12294 | 121.8303 | 0.015517 | 121.7982 | 121.7384 | -0.091883 | -0.049981 | 0.12825 | 121.5873 | -0.0162 | 121.7982 | 121.7317 | 0.14443 | 0.050357 | -0.23947 | 121.8264 | 121.7609 | 121.9392 | 121.7391 | 0.019392 | 121.7947 | 121.8613 | 121.5714 | 121.6968 | -0.22365
708.875 | 121.994 | -121.7102 | 0.13275 | 1.4211e-13 | -0.027899 | 0.015107 | -0.0029979 | -0.011051 | 0.019484 | -0.24822 | -0.0024974 | -0.00076696 | -0.0040571 | 0.029453 | 0.011176 | 0.083459 | 0.033457 | 0.01906 | 0.10707 | 0.023254 | 0.22896 | 0.11094 | 0.083464 | -0.008798 | 0.007751 | 0.089087 | 0.16022 | -0.13876 | -0.11836 | 121.8211 | -0.025683 | 121.7937 | 121.7293 | -0.091882 | -0.1095 | 0.096208 | 121.5918 | -0.043664 | 121.7937 | 121.718 | 0.12611 | 0.027471 | -0.27152 | 121.8173 | 121.7335 | 121.9392 | 121.7437 | -0.021809 | 121.7993 | 121.8704 | 121.5714 | 121.7014 | -0.25111
710.5469 | 121.9116 | -121.7331 | 0.15564 | 1.4211e-13 | -0.027899 | 0.015321 | -0.0034253 | -0.011051 | 0.019911 | -0.22533 | -0.0022838 | -0.0011944 | -0.0038435 | 0.029239 | 0.01139 | 0.074302 | 0.0243 | 0.028217 | 0.10707 | 0.055306 | 0.23354 | 0.1201 | 0.078886 | -0.00422 | 0.01233 | 0.084508 | 0.14649 | -0.13876 | -0.11836 | 121.8532 | -0.048572 | 121.8074 | 121.7613 | -0.091883 | -0.10033 | 0.077898 | 121.6147 | -0.071132 | 121.812 | 121.7454 | 0.13069 | -0.009154 | -0.29441 | 121.8402 | 121.7884 | 121.9666 | 121.7574 | -0.03554 | 121.8176 | 121.8796 | 121.5943 | 121.7289 | -0.274
712.2812 | 121.9208 | -121.756 | 0.16937 | 1.4211e-13 | -0.027472 | 0.015321 | -0.0034253 | -0.011051 | 0.019698 | -0.24059 | -0.0020702 | -0.00098076 | -0.0038435 | 0.029453 | 0.01139 | 0.083459 | 0.033457 | 0.023639 | 0.10707 | 0.041569 | 0.23354 | 0.1201 | 0.083464 | -0.00422 | 0.016908 | 0.089087 | 0.16022 | -0.14334 | -0.11836 | 121.8761 | -0.062305 | 121.8394 | 121.7796 | -0.096461 | -0.1278 | 0.064165 | 121.6376 | -0.080286 | 121.8394 | 121.7729 | 0.13527 | -0.009151 | -0.31272 | 121.863 | 121.7976 | 121.9895 | 121.7894 | -0.049273 | 121.8451 | 121.9162 | 121.6126 | 121.7518 | -0.28773
714 | 122.0306 | -121.6919 | 0.12817 | 1.4211e-13 | -0.027472 | 0.014893 | -0.0036391 | -0.011264 | 0.019911 | -0.22533 | -0.0020702 | -0.00098076 | -0.0036299 | 0.029666 | 0.010963 | 0.088037 | 0.028878 | 0.01906 | 0.10707 | 0.041569 | 0.2198 | 0.11552 | 0.078886 | -0.013377 | 0.007751 | 0.07993 | 0.15107 | -0.13419 | -0.11836 | 121.8074 | -0.021106 | 121.7799 | 121.711 | -0.096461 | -0.086605 | 0.091628 | 121.5735 | -0.048244 | 121.7708 | 121.6996 | 0.12611 | 0.022891 | -0.26236 | 121.799 | 121.7335 | 121.9117 | 121.7208 | -0.012653 | 121.7718 | 121.843 | 121.5577 | 121.6785 | -0.24654
715.6875 | 121.9666 | -121.7422 | 0.16937 | 1.4211e-13 | -0.027472 | 0.01468 | -0.0034253 | -0.011051 | 0.019911 | -0.23296 | -0.0020702 | -0.001408 | -0.0036299 | 0.029453 | 0.011176 | 0.083459 | 0.033457 | 0.023639 | 0.11165 | 0.046148 | 0.22438 | 0.11552 | 0.078886 | -0.008798 | 0.003172 | 0.084508 | 0.15107 | -0.11129 | -0.12294 | 121.8578 | -0.057726 | 121.8257 | 121.7659 | -0.091882 | -0.12323 | 0.055008 | 121.6193 | -0.084865 | 121.8211 | 121.7454 | 0.12611 | -0.018308 | -0.28067 | 121.8539 | 121.7884 | 121.9666 | 121.7757 | -0.053852 | 121.8268 | 121.8933 | 121.631 | 121.7335 | -0.29231
717.4375 | 122.0444 | -121.6965 | 0.13275 | 1.4211e-13 | -0.027686 | 0.015321 | -0.0036391 | -0.011051 | 0.019911 | -0.24059 | -0.0024974 | -0.0011944 | -0.0038435 | 0.029453 | 0.01139 | 0.074302 | 0.019721 | 0.028217 | 0.11622 | 0.050727 | 0.23354 | 0.11094 | 0.069728 | 0.000359 | 0.01233 | 0.089087 | 0.15564 | -0.13876 | -0.12294 | 121.8074 | -0.016526 | 121.7708 | 121.7247 | -0.082725 | -0.082024 | 0.10079 | 121.5735 | -0.043664 | 121.7662 | 121.7088 | 0.13527 | 0.022892 | -0.27152 | 121.8127 | 121.7472 | 121.93 | 121.7162 | -0.021809 | 121.7856 | 121.8521 | 121.5577 | 121.6968 | -0.25569
719.1875 | 121.907 | -121.7331 | 0.16937 | 1.4211e-13 | -0.027472 | 0.014893 | -0.0032117 | -0.011051 | 0.019911 | -0.24059 | -0.0022838 | -0.00098076 | -0.0036299 | 0.029453 | 0.011176 | 0.083459 | 0.0243 | 0.028217 | 0.11165 | 0.041569 | 0.23354 | 0.11094 | 0.069728 | -0.008798 | 0.01233 | 0.089087 | 0.1648 | -0.14334 | -0.12294 | 121.844 | -0.057726 | 121.8166 | 121.7613 | -0.082725 | -0.1278 | 0.064165 | 121.6102 | -0.080286 | 121.8028 | 121.7454 | 0.13527 | -0.004573 | -0.31272 | 121.8447 | 121.7747 | 121.9666 | 121.7574 | -0.058431 | 121.8222 | 121.8979 | 121.5897 | 121.7243 | -0.29231
720.9375 | 122.0215 | -121.6782 | 0.12817 | 1.4211e-13 | -0.027686 | 0.01468 | -0.0036391 | -0.011264 | 0.019698 | -0.24059 | -0.0020702 | -0.00098076 | -0.0038435 | 0.029453 | 0.011176 | 0.074302 | 0.0243 | 0.032795 | 0.10707 | 0.055306 | 0.23354 | 0.11552 | 0.083464 | -0.013377 | 0.007751 | 0.07993 | 0.15564 | -0.10671 | -0.13668 | 121.7937 | -0.021106 | 121.7525 | 121.711 | -0.082726 | -0.072868 | 0.10536 | 121.5415 | -0.048244 | 121.7616 | 121.6859 | 0.14443 | 0.027469 | -0.23489 | 121.7852 | 121.7335 | 121.9117 | 121.7025 | -0.012653 | 121.7581 | 121.8338 | 121.5714 | 121.6648 | -0.26485
722.6094 | 122.0398 | -121.6782 | 0.11902 | 1.4211e-13 | -0.027472 | 0.015107 | -0.0036391 | -0.010837 | 0.019911 | -0.23296 | -0.0020702 | -0.00055336 | -0.0036299 | 0.029453 | 0.011176 | 0.083459 | 0.028878 | 0.023639 | 0.1208 | 0.03699 | 0.23354 | 0.11552 | 0.088043 | -0.008798 | 0.01233 | 0.089087 | 0.16022 | -0.13419 | -0.12752 | 121.7937 | 0.001785 | 121.7616 | 121.7018 | -0.091882 | -0.082029 | 0.11452 | 121.5506 | -0.029932 | 121.7662 | 121.6905 | 0.13985 | 0.041203 | -0.25321 | 121.799 | 121.7152 | 121.9117 | 121.707 | -0.003498 | 121.7672 | 121.8384 | 121.544 | 121.6694 | -0.24654
724.3438 | 122.0215 | -121.7331 | 0.13733 | 1.4211e-13 | -0.027686 | 0.015321 | -0.0032117 | -0.011051 | 0.020125 | -0.23296 | -0.0022838 | -0.00098076 | -0.0038435 | 0.029453 | 0.011176 | 0.083459 | 0.0243 | 0.028217 | 0.10707 | 0.050727 | 0.23812 | 0.11094 | 0.088043 | 0.000359 | 0.021487 | 0.084508 | 0.16022 | -0.12961 | -0.11378 | 121.844 | -0.030261 | 121.8166 | 121.7613 | -0.082725 | -0.086602 | 0.10079 | 121.6193 | -0.052821 | 121.8211 | 121.7546 | 0.13527 | 0.022893 | -0.26694 | 121.8402 | 121.7838 | 121.9712 | 121.7574 | -0.026387 | 121.8176 | 121.8933 | 121.6035 | 121.7335 | -0.25111
726.0938 | 122.0169 | -121.6873 | 0.1236 | 1.4211e-13 | -0.027686 | 0.01468 | -0.0034253 | -0.011051 | 0.020125 | -0.23296 | -0.0020702 | -0.00098076 | -0.0038435 | 0.029239 | 0.011176 | 0.07888 | 0.0243 | 0.028217 | 0.11622 | 0.059885 | 0.23354 | 0.1201 | 0.083464 | -0.008798 | 0.01233 | 0.089087 | 0.16022 | -0.12961 | -0.12294 | 121.8074 | -0.007371 | 121.7662 | 121.7155 | -0.091883 | -0.063711 | 0.10994 | 121.5644 | -0.034509 | 121.7708 | 121.6996 | 0.13527 | 0.036626 | -0.2532 | 121.8035 | 121.7472 | 121.9209 | 121.7116 | -0.003496 | 121.7764 | 121.8475 | 121.5577 | 121.6785 | -0.24654
727.8438 | 121.9894 | -121.701 | 0.14648 | 1.4211e-13 | -0.027686 | 0.015107 | -0.0032117 | -0.010837 | 0.019698 | -0.22533 | -0.0022838 | -0.0011944 | -0.0036299 | 0.029666 | 0.010963 | 0.083459 | 0.033457 | 0.023639 | 0.11165 | 0.055306 | 0.23354 | 0.11094 | 0.078886 | -0.008798 | 0.01233 | 0.089087 | 0.16022 | -0.12503 | -0.11836 | 121.812 | -0.034837 | 121.7845 | 121.7247 | -0.087303 | -0.091178 | 0.087054 | 121.5827 | -0.057397 | 121.7799 | 121.7134 | 0.13069 | 0.013738 | -0.27151 | 121.8127 | 121.7564 | 121.9346 | 121.7345 | -0.035542 | 121.7901 | 121.8613 | 121.576 | 121.6923 | -0.26484
729.5156 | 121.9025 | -121.7331 | 0.16022 | 1.4211e-13 | -0.028113 | 0.014893 | -0.0036391 | -0.011051 | 0.019911 | -0.23296 | -0.0018566 | -0.0011944 | -0.0038435 | 0.029666 | 0.011176 | 0.083459 | 0.0243 | 0.028217 | 0.11165 | 0.050727 | 0.22896 | 0.11552 | 0.088043 | 0.004938 | 0.016908 | 0.084508 | 0.15107 | -0.13876 | -0.11378 | 121.8486 | -0.04857 | 121.8166 | 121.7613 | -0.087304 | -0.10949 | 0.068742 | 121.6193 | -0.075709 | 121.8211 | 121.75 | 0.13069 | -0.009152 | -0.29898 | 121.8447 | 121.7838 | 121.9621 | 121.7574 | -0.044696 | 121.8176 | 121.8842 | 121.5943 | 121.738 | -0.274
731.25 | 121.9299 | -121.7377 | 0.15106 | 1.4211e-13 | -0.027899 | 0.014893 | -0.0032117 | -0.011478 | 0.019911 | -0.23296 | -0.0022838 | -0.0011944 | -0.0040571 | 0.029453 | 0.010535 | 0.074302 | 0.033457 | 0.023639 | 0.11165 | 0.046148 | 0.22896 | 0.1201 | 0.097201 | 0.004938 | 0.026066 | 0.084508 | 0.16022 | -0.13876 | -0.1092 | 121.8578 | -0.039415 | 121.812 | 121.7613 | -0.096461 | -0.10491 | 0.077897 | 121.6285 | -0.066554 | 121.8349 | 121.7637 | 0.13527 | 0.00916 | -0.28983 | 121.8493 | 121.7838 | 121.9666 | 121.7711 | -0.030962 | 121.8222 | 121.8979 | 121.5989 | 121.7426 | -0.26026
733.0156 | 121.9391 | -121.7606 | 0.13733 | 1.4211e-13 | -0.028113 | 0.015107 | -0.0036391 | -0.011051 | 0.020125 | -0.23296 | -0.0022838 | -0.0011944 | -0.0034163 | 0.029666 | 0.011176 | 0.088037 | 0.028878 | 0.032795 | 0.11622 | 0.041569 | 0.23812 | 0.1201 | 0.097201 | 0.009516 | 0.021487 | 0.084508 | 0.1648 | -0.12961 | -0.11378 | 121.8807 | -0.021104 | 121.8486 | 121.7934 | -0.087305 | -0.09576 | 0.10079 | 121.6468 | -0.052821 | 121.8578 | 121.782 | 0.13527 | 0.027471 | -0.26694 | 121.8768 | 121.8021 | 121.9987 | 121.7894 | -0.017229 | 121.8451 | 121.9254 | 121.631 | 121.7701 | -0.25111
734.7031 | 121.9162 | -121.7651 | 0.16022 | 1.4211e-13 | -0.027899 | 0.014893 | -0.0032117 | -0.011051 | 0.020125 | -0.22533 | -0.0018566 | -0.00076696 | -0.0038435 | 0.029666 | 0.011604 | 0.074302 | 0.028878 | 0.028217 | 0.10249 | 0.041569 | 0.23354 | 0.1201 | 0.088043 | 0.004938 | 0.026066 | 0.093665 | 0.15564 | -0.12961 | -0.11378 | 121.8852 | -0.057727 | 121.8394 | 121.7934 | -0.091883 | -0.11865 | 0.073321 | 121.6514 | -0.066552 | 121.8532 | 121.7912 | 0.13985 | -0.004574 | -0.28982 | 121.8676 | 121.8067 | 121.9987 | 121.794 | -0.040117 | 121.8588 | 121.9208 | 121.6355 | 121.7701 | -0.274
736.4531 | 121.9208 | -121.7606 | 0.16479 | 1.4211e-13 | -0.027899 | 0.015107 | -0.0036391 | -0.010837 | 0.019911 | -0.24059 | -0.0022838 | -0.00076696 | -0.0038435 | 0.030094 | 0.010749 | 0.074302 | 0.028878 | 0.028217 | 0.11622 | 0.03699 | 0.22896 | 0.11094 | 0.083464 | 0.018674 | 0.016908 | 0.093665 | 0.15107 | -0.13876 | -0.1092 | 121.8715 | -0.04857 | 121.8349 | 121.7888 | -0.082725 | -0.12781 | 0.064164 | 121.6514 | -0.07113 | 121.844 | 121.7775 | 0.12611 | -0.01373 | -0.30356 | 121.8768 | 121.7975 | 121.9895 | 121.7894 | -0.053853 | 121.8542 | 121.9116 | 121.6218 | 121.7792 | -0.274
738.2031 | 121.9208 | -121.7468 | 0.16022 | 1.4211e-13 | -0.027899 | 0.015107 | -0.0036391 | -0.010837 | 0.020125 | -0.22533 | -0.0024974 | -0.00098076 | -0.0040571 | 0.029239 | 0.010535 | 0.088037 | 0.033457 | 0.028217 | 0.11622 | 0.03699 | 0.23812 | 0.1201 | 0.097201 | 0.004938 | 0.021487 | 0.093665 | 0.1648 | -0.13419 | -0.1092 | 121.8669 | -0.043992 | 121.8349 | 121.775 | -0.091883 | -0.12323 | 0.0779 | 121.6376 | -0.066552 | 121.844 | 121.7683 | 0.13069 | 0.004583 | -0.2944 | 121.8631 | 121.7838 | 121.9849 | 121.7803 | -0.040117 | 121.8405 | 121.9116 | 121.6126 | 121.7518 | -0.26942
739.9531 | 121.962 | -121.7468 | 0.15106 | 1.4211e-13 | -0.028113 | 0.015107 | -0.0034253 | -0.011051 | 0.019911 | -0.24822 | -0.0020702 | -0.00076696 | -0.0038435 | 0.029666 | 0.010749 | 0.088037 | 0.033457 | 0.032795 | 0.10707 | 0.041569 | 0.22896 | 0.10178 | 0.083464 | 0.009516 | 0.021487 | 0.089087 | 0.16022 | -0.12961 | -0.1092 | 121.8486 | -0.043994 | 121.8349 | 121.7796 | -0.068989 | -0.10949 | 0.077897 | 121.6376 | -0.061975 | 121.8303 | 121.7683 | 0.13069 | 0.00916 | -0.28067 | 121.8539 | 121.7884 | 121.9758 | 121.7803 | -0.049278 | 121.8359 | 121.907 | 121.6172 | 121.7563 | -0.26026
741.625 | 121.9254 | -121.7468 | 0.15106 | 1.4211e-13 | -0.027472 | 0.014893 | -0.0032117 | -0.011051 | 0.019698 | -0.23296 | -0.0020702 | -0.0011944 | -0.0040571 | 0.029666 | 0.010963 | 0.083459 | 0.033457 | 0.032795 | 0.11165 | 0.046148 | 0.24269 | 0.1201 | 0.083464 | 0.018674 | 0.016908 | 0.089087 | 0.1648 | -0.13419 | -0.11378 | 121.8669 | -0.039415 | 121.8303 | 121.7796 | -0.087305 | -0.10491 | 0.091633 | 121.633 | -0.061975 | 121.8303 | 121.7637 | 0.13069 | 0.013738 | -0.28525 | 121.8585 | 121.793 | 121.9895 | 121.7803 | -0.030962 | 121.8359 | 121.9116 | 121.6126 | 121.7655 | -0.26484
743.3594 | 121.9894 | -121.7239 | 0.14191 | 1.4211e-13 | -0.028113 | 0.014893 | -0.0034253 | -0.011051 | 0.019911 | -0.24059 | -0.0020702 | -0.0011944 | -0.0036299 | 0.029666 | 0.010749 | 0.07888 | 0.028878 | 0.028217 | 0.11165 | 0.055306 | 0.23812 | 0.11552 | 0.088043 | 0.018674 | 0.026066 | 0.084508 | 0.16022 | -0.11587 | -0.11378 | 121.8395 | -0.03026 | 121.8028 | 121.7522 | -0.087304 | -0.086601 | 0.09621 | 121.6102 | -0.057399 | 121.812 | 121.75 | 0.13985 | 0.018315 | -0.25778 | 121.8356 | 121.7792 | 121.9621 | 121.7528 | -0.026386 | 121.8084 | 121.8842 | 121.6081 | 121.7426 | -0.25569
745.0938 | 121.9528 | -121.7468 | 0.16022 | 1.4211e-13 | -0.028113 | 0.014893 | -0.0034253 | -0.011051 | 0.019911 | -0.24059 | -0.0022838 | -0.00098076 | -0.0038435 | 0.02988 | 0.011176 | 0.07888 | 0.033457 | 0.028217 | 0.11622 | 0.050727 | 0.24269 | 0.11552 | 0.092622 | 0.009516 | 0.026066 | 0.089087 | 0.1648 | -0.13419 | -0.11378 | 121.8623 | -0.043992 | 121.8257 | 121.775 | -0.087304 | -0.10949 | 0.082478 | 121.633 | -0.07113 | 121.8394 | 121.7729 | 0.13985 | 0.004583 | -0.2944 | 121.8631 | 121.7976 | 121.9895 | 121.7803 | -0.044696 | 121.8359 | 121.9116 | 121.6126 | 121.7563 | -0.274
746.8281 | 122.0673 | -121.7056 | 0.12817 | 1.4211e-13 | -0.027899 | 0.015107 | -0.0034253 | -0.011051 | 0.020125 | -0.22533 | -0.0022838 | -0.00098076 | -0.0038435 | 0.02988 | 0.010963 | 0.088037 | 0.033457 | 0.037373 | 0.10707 | 0.050727 | 0.23354 | 0.11094 | 0.092622 | 0.009516 | 0.021487 | 0.084508 | 0.16022 | -0.092979 | -0.11378 | 121.8166 | -0.021106 | 121.7937 | 121.743 | -0.073569 | -0.077447 | 0.10536 | 121.5918 | -0.043666 | 121.7982 | 121.7271 | 0.13527 | 0.032048 | -0.22115 | 121.8127 | 121.7564 | 121.9392 | 121.7391 | -0.017232 | 121.7901 | 121.8658 | 121.6126 | 121.7151 | -0.24196
748.5156 | 121.9894 | -121.7239 | 0.12817 | 1.4211e-13 | -0.028113 | 0.014252 | -0.0032117 | -0.011051 | 0.019484 | -0.23296 | -0.0018566 | -0.00098076 | -0.0038435 | 0.030094 | 0.011176 | 0.07888 | 0.028878 | 0.023639 | 0.11165 | 0.046148 | 0.23354 | 0.10178 | 0.092622 | 0.009516 | 0.026066 | 0.084508 | 0.15107 | -0.13876 | -0.1092 | 121.8257 | -0.016527 | 121.8028 | 121.7476 | -0.078145 | -0.082026 | 0.10536 | 121.6147 | -0.043666 | 121.8166 | 121.75 | 0.13527 | 0.022891 | -0.26694 | 121.8356 | 121.7701 | 121.9575 | 121.7528 | -0.02639 | 121.8084 | 121.875 | 121.5852 | 121.7335 | -0.23738
750.25 | 121.9803 | -121.7285 | 0.15106 | 1.4211e-13 | -0.027686 | 0.014893 | -0.0034253 | -0.010837 | 0.019698 | -0.24059 | -0.0020702 | -0.0011944 | -0.0038435 | 0.029666 | 0.011176 | 0.088037 | 0.033457 | 0.023639 | 0.11622 | 0.046148 | 0.23354 | 0.097205 | 0.092622 | 0.004938 | 0.021487 | 0.089087 | 0.16938 | -0.10214 | -0.11836 | 121.8257 | -0.034837 | 121.8166 | 121.7522 | -0.073566 | -0.10491 | 0.082476 | 121.6102 | -0.061975 | 121.8211 | 121.75 | 0.13985 | 0.018317 | -0.2532 | 121.8447 | 121.7747 | 121.9621 | 121.762 | -0.053857 | 121.8176 | 121.8979 | 121.6264 | 121.7335 | -0.26942
751.9375 | 121.9528 | -121.7514 | 0.15106 | 1.4211e-13 | -0.027899 | 0.014893 | -0.0032117 | -0.011051 | 0.019911 | -0.22533 | -0.0020702 | -0.00098076 | -0.0042707 | 0.02988 | 0.010749 | 0.083459 | 0.033457 | 0.01906 | 0.12538 | 0.041569 | 0.23354 | 0.046837 | 0.088043 | 0.000359 | 0.026066 | 0.089087 | 0.1648 | -0.13419 | -0.10462 | 121.7982 | -0.02568 | 121.8349 | 121.7705 | -0.027777 | -0.10949 | 0.082476 | 121.6468 | -0.061975 | 121.8394 | 121.7775 | 0.13069 | 0.013738 | -0.28525 | 121.8768 | 121.793 | 121.9849 | 121.7849 | -0.10423 | 121.8405 | 121.9162 | 121.6172 | 121.7518 | -0.25569
753.6719 | 121.962 | -121.7422 | 0.15106 | 1.4211e-13 | -0.028113 | 0.014893 | -0.0036391 | -0.011051 | 0.019911 | -0.24059 | -0.0018566 | -0.001408 | -0.0036299 | 0.02988 | 0.010749 | 0.07888 | 0.019721 | 0.023639 | 0.11165 | 0.041569 | 0.23354 | 0.10178 | 0.092622 | 0.000359 | 0.021487 | 0.089087 | 0.16938 | -0.12961 | -0.11378 | 121.844 | -0.039415 | 121.8211 | 121.7659 | -0.078145 | -0.10949 | 0.082476 | 121.6285 | -0.061975 | 121.8349 | 121.7637 | 0.13527 | 0.018317 | -0.28067 | 121.8539 | 121.7838 | 121.9758 | 121.762 | -0.049278 | 121.8313 | 121.9116 | 121.6126 | 121.7426 | -0.26484
755.4219 | 121.9162 | -121.7743 | 0.16937 | 1.4211e-13 | -0.027899 | 0.015107 | -0.0029979 | -0.011051 | 0.019698 | -0.23296 | -0.0022838 | -0.00076696 | -0.0036299 | 0.029666 | 0.011176 | 0.083459 | 0.033457 | 0.032795 | 0.11622 | 0.046148 | 0.23354 | 0.042258 | 0.097201 | 0.000359 | 0.035223 | 0.07993 | 0.15107 | -0.13419 | -0.1092 | 121.8166 | -0.053148 | 121.8578 | 121.8071 | -0.009463 | -0.12323 | 0.064165 | 121.6651 | -0.089443 | 121.8715 | 121.8095 | 0.14443 | -0.018308 | -0.30356 | 121.8905 | 121.8204 | 122.0078 | 121.8077 | -0.12712 | 121.8542 | 121.9254 | 121.6401 | 121.7747 | -0.27858
757.1562 | 122.0398 | -121.7331 | 0.1236 | 1.4211e-13 | -0.027899 | 0.015107 | -0.0034253 | -0.011264 | 0.019698 | -0.22533 | -0.0022838 | -0.00033976 | -0.0038435 | 0.02988 | 0.010963 | 0.083459 | 0.028878 | 0.023639 | 0.1208 | 0.046148 | 0.23354 | 0.046837 | 0.092622 | -0.013377 | 0.021487 | 0.084508 | 0.1648 | -0.11587 | -0.1092 | 121.7799 | -0.002792 | 121.8166 | 121.7567 | -0.023198 | -0.077448 | 0.10994 | 121.6239 | -0.039088 | 121.8257 | 121.7546 | 0.13069 | 0.041204 | -0.23947 | 121.8539 | 121.7792 | 121.9666 | 121.762 | -0.076759 | 121.8176 | 121.8979 | 121.6172 | 121.7197 | -0.2328
758.8906 | 122.0078 | -121.7194 | 0.15106 | 1.4211e-13 | -0.028113 | 0.014893 | -0.0029979 | -0.011478 | 0.019698 | -0.24059 | -0.0022838 | -0.00098076 | -0.0036299 | 0.029666 | 0.010963 | 0.088037 | 0.033457 | 0.032795 | 0.10707 | 0.055306 | 0.23354 | 0.11094 | 0.097201 | -0.00422 | 0.030644 | 0.084508 | 0.16022 | -0.13419 | -0.1092 | 121.8303 | -0.043994 | 121.8074 | 121.7522 | -0.078147 | -0.095756 | 0.082476 | 121.6102 | -0.066554 | 121.8166 | 121.75 | 0.13985 | 0.00916 | -0.28525 | 121.8264 | 121.7747 | 121.9529 | 121.7528 | -0.04012 | 121.8039 | 121.8796 | 121.5852 | 121.7151 | -0.26026
760.5625 | 121.9574 | -121.7606 | 0.14648 | 1.4211e-13 | -0.027899 | 0.014893 | -0.0034253 | -0.011051 | 0.019698 | -0.2177 | -0.0020702 | -0.00098076 | -0.0036299 | 0.029666 | 0.010749 | 0.074302 | 0.033457 | 0.028217 | 0.11165 | 0.055306 | 0.23812 | 0.10178 | 0.092622 | 0.018674 | 0.021487 | 0.084508 | 0.15564 | -0.10671 | -0.1092 | 121.8623 | -0.034837 | 121.8349 | 121.7888 | -0.073567 | -0.091178 | 0.091633 | 121.6514 | -0.061976 | 121.8532 | 121.782 | 0.13069 | 0.009159 | -0.2532 | 121.8722 | 121.8159 | 121.9987 | 121.794 | -0.0447 | 121.8451 | 121.9162 | 121.6538 | 121.7792 | -0.25569
762.2969 | 122.0078 | -121.7148 | 0.14648 | 1.4211e-13 | -0.027899 | 0.014893 | -0.0034253 | -0.011051 | 0.019911 | -0.23296 | -0.0022838 | -0.00076696 | -0.0036299 | 0.029666 | 0.010749 | 0.07888 | 0.028878 | 0.023639 | 0.11165 | 0.050727 | 0.22896 | 0.11094 | 0.092622 | 0.018674 | 0.030644 | 0.093665 | 0.15564 | -0.13419 | -0.1092 | 121.8257 | -0.034837 | 121.7937 | 121.7384 | -0.087303 | -0.095757 | 0.082475 | 121.6056 | -0.052819 | 121.8074 | 121.7454 | 0.13985 | 0.009159 | -0.28067 | 121.8264 | 121.7655 | 121.9437 | 121.7437 | -0.035542 | 121.8084 | 121.8704 | 121.5806 | 121.7335 | -0.25569
763.9688 | 122.0718 | -121.7102 | 0.13733 | 1.4211e-13 | -0.028327 | 0.014893 | -0.0034253 | -0.011051 | 0.019698 | -0.23296 | -0.0018566 | -0.00076696 | -0.0036299 | 0.029666 | 0.01139 | 0.088037 | 0.033457 | 0.032795 | 0.1208 | 0.055306 | 0.22896 | 0.11094 | 0.092622 | 0.027831 | 0.021487 | 0.089087 | 0.16022 | -0.13419 | -0.11836 | 121.8211 | -0.016525 | 121.7982 | 121.743 | -0.078147 | -0.082023 | 0.09163 | 121.5918 | -0.048242 | 121.8028 | 121.7317 | 0.13985 | 0.022893 | -0.27152 | 121.831 | 121.7655 | 121.9392 | 121.7437 | -0.026387 | 121.7993 | 121.8704 | 121.576 | 121.738 | -0.25569
765.7188 | 121.9391 | -121.7606 | 0.16022 | 1.4211e-13 | -0.027899 | 0.015107 | -0.0032117 | -0.011478 | 0.019698 | -0.23296 | -0.0022838 | -0.00055336 | -0.0038435 | 0.02988 | 0.011176 | 0.083459 | 0.028878 | 0.032795 | 0.10707 | 0.055306 | 0.23354 | 0.088047 | 0.092622 | 0.027831 | 0.026066 | 0.089087 | 0.1648 | -0.13419 | -0.1092 | 121.8486 | -0.053149 | 121.844 | 121.7934 | -0.055252 | -0.10491 | 0.073321 | 121.6514 | -0.07113 | 121.8532 | 121.7866 | 0.13527 | 0.004583 | -0.2944 | 121.8676 | 121.8159 | 121.9941 | 121.7894 | -0.07217 | 121.8496 | 121.9254 | 121.6264 | 121.7884 | -0.26942
767.4531 | 122.0215 | -121.7239 | 0.14191 | 1.4211e-13 | -0.027899 | 0.014893 | -0.0034253 | -0.011051 | 0.019911 | -0.24822 | -0.001643 | -0.001408 | -0.0038435 | 0.02988 | 0.011176 | 0.088037 | 0.0243 | 0.023639 | 0.11165 | 0.050727 | 0.23812 | 0.11552 | 0.092622 | 0.023253 | 0.021487 | 0.084508 | 0.1648 | -0.13876 | -0.11378 | 121.8395 | -0.03026 | 121.812 | 121.7476 | -0.091882 | -0.09118 | 0.09621 | 121.6102 | -0.057399 | 121.8166 | 121.7454 | 0.13527 | 0.022893 | -0.28067 | 121.8356 | 121.7747 | 121.9621 | 121.7482 | -0.026386 | 121.8084 | 121.8887 | 121.5852 | 121.7472 | -0.25569
769.1875 | 122.0398 | -121.7056 | 0.10529 | 1.4211e-13 | -0.027899 | 0.014893 | -0.0032117 | -0.011051 | 0.019911 | -0.23296 | -0.0018566 | -0.00098076 | -0.0036299 | 0.030521 | 0.010963 | 0.07888 | 0.028878 | 0.037373 | 0.11165 | 0.050727 | 0.23354 | 0.11552 | 0.097201 | 0.009516 | 0.016908 | 0.07993 | 0.15564 | -0.13419 | -0.1092 | 121.8211 | 0.006361 | 121.7845 | 121.743 | -0.078148 | -0.054559 | 0.12825 | 121.5964 | -0.025356 | 121.8028 | 121.7225 | 0.12611 | 0.050357 | -0.23947 | 121.8173 | 121.7564 | 121.9392 | 121.7345 | 0.010235 | 121.7856 | 121.8613 | 121.5714 | 121.7151 | -0.21449
770.9375 | 122.0352 | -121.701 | 0.12817 | 1.4211e-13 | -0.028113 | 0.014893 | -0.0034253 | -0.011051 | 0.019911 | -0.22533 | -0.0018566 | -0.0011944 | -0.0036299 | 0.02988 | 0.010963 | 0.07888 | 0.028878 | 0.028217 | 0.11165 | 0.050727 | 0.23354 | 0.1201 | 0.092622 | 0.000359 | 0.021487 | 0.084508 | 0.16022 | -0.13419 | -0.11378 | 121.8211 | -0.016527 | 121.7799 | 121.7293 | -0.091883 | -0.077447 | 0.10536 | 121.5873 | -0.043666 | 121.7937 | 121.7225 | 0.13527 | 0.032048 | -0.26236 | 121.8127 | 121.7518 | 121.9346 | 121.7299 | -0.008074 | 121.7856 | 121.8613 | 121.5669 | 121.7014 | -0.24196
772.6094 | 121.9254 | -121.7697 | 0.16937 | 1.4211e-13 | -0.028113 | 0.01468 | -0.0034253 | -0.011051 | 0.019911 | -0.24059 | -0.0020702 | -0.00098076 | -0.0036299 | 0.02988 | 0.010749 | 0.088037 | 0.028878 | 0.028217 | 0.11165 | 0.050727 | 0.23354 | 0.11552 | 0.088043 | -0.00422 | 0.026066 | 0.089087 | 0.1648 | -0.14334 | -0.11378 | 121.8852 | -0.057726 | 121.8578 | 121.7979 | -0.087304 | -0.11865 | 0.064165 | 121.6559 | -0.080286 | 121.8578 | 121.7958 | 0.13985 | -0.004573 | -0.31272 | 121.8814 | 121.8204 | 122.0033 | 121.7986 | -0.053852 | 121.8588 | 121.9345 | 121.6264 | 121.7655 | -0.28315
774.3438 | 121.9757 | -121.7514 | 0.14648 | 1.4211e-13 | -0.028327 | 0.01468 | -0.0034253 | -0.011264 | 0.019698 | -0.23296 | -0.0018566 | -0.00098076 | -0.0040571 | 0.030094 | 0.011176 | 0.074302 | 0.0243 | 0.028217 | 0.11165 | 0.050727 | 0.23354 | 0.11094 | 0.088043 | -0.00422 | 0.030644 | 0.084508 | 0.15564 | -0.13876 | -0.10462 | 121.8623 | -0.034837 | 121.8257 | 121.7796 | -0.082725 | -0.095757 | 0.087054 | 121.6468 | -0.061976 | 121.8394 | 121.782 | 0.13527 | 0.009159 | -0.28525 | 121.8631 | 121.8021 | 121.9849 | 121.7757 | -0.035542 | 121.8359 | 121.907 | 121.6126 | 121.7472 | -0.25111
776.0938 | 122.1085 | -121.7239 | 0.12817 | 1.4211e-13 | -0.028113 | 0.015107 | -0.0036391 | -0.011478 | 0.019911 | -0.23296 | -0.0018566 | -0.00098076 | -0.0036299 | 0.029666 | 0.011176 | 0.07888 | 0.033457 | 0.023639 | 0.10707 | 0.050727 | 0.23812 | 0.083468 | 0.092622 | -0.013377 | 0.030644 | 0.089087 | 0.15107 | -0.12503 | -0.10462 | 121.8074 | -0.021106 | 121.8028 | 121.7476 | -0.059829 | -0.077447 | 0.10994 | 121.6193 | -0.039087 | 121.8166 | 121.7546 | 0.13527 | 0.022891 | -0.2532 | 121.831 | 121.7747 | 121.9621 | 121.7574 | -0.044706 | 121.813 | 121.875 | 121.5989 | 121.7106 | -0.2328
777.8281 | 122.0169 | -121.7239 | 0.09613 | 1.4211e-13 | -0.028327 | 0.014466 | -0.0036391 | -0.011264 | 0.019698 | -0.24059 | -0.0018566 | -0.00076696 | -0.0036299 | 0.029666 | 0.010963 | 0.083459 | 0.028878 | 0.023639 | 0.11622 | 0.046148 | 0.23354 | 0.028521 | 0.088043 | -0.013377 | 0.026066 | 0.089087 | 0.1648 | -0.12961 | -0.10462 | 121.7525 | 0.020095 | 121.8074 | 121.7476 | -0.004882 | -0.049982 | 0.13741 | 121.6193 | -0.007043 | 121.812 | 121.75 | 0.13069 | 0.06867 | -0.22574 | 121.8402 | 121.7701 | 121.9575 | 121.7528 | -0.067609 | 121.813 | 121.8887 | 121.5943 | 121.7106 | -0.20075
779.5156 | 122.0398 | -121.7285 | 0.12817 | 1.4211e-13 | -0.028327 | 0.014893 | -0.0034253 | -0.010623 | 0.019698 | -0.22533 | -0.0018566 | -0.00098076 | -0.0042707 | 0.030307 | 0.010963 | 0.074302 | 0.033457 | 0.032795 | 0.11165 | 0.059885 | 0.23812 | 0.11094 | 0.088043 | -0.022535 | 0.026066 | 0.089087 | 0.1648 | -0.13419 | -0.11378 | 121.8395 | -0.016527 | 121.8028 | 121.7613 | -0.078147 | -0.068289 | 0.10994 | 121.6147 | -0.039087 | 121.8166 | 121.7546 | 0.13985 | 0.036626 | -0.26236 | 121.8402 | 121.7884 | 121.9666 | 121.762 | -0.017232 | 121.8176 | 121.8933 | 121.5943 | 121.706 | -0.24196
781.2656 | 121.9299 | -121.7377 | 0.14648 | 1.4211e-13 | -0.028327 | 0.01468 | -0.0036391 | -0.011264 | 0.019911 | -0.22533 | -0.001643 | -0.00098076 | -0.0036299 | 0.02988 | 0.011604 | 0.088037 | 0.028878 | 0.023639 | 0.11165 | 0.046148 | 0.23354 | 0.10636 | 0.092622 | -0.008798 | 0.026066 | 0.084508 | 0.15564 | -0.13419 | -0.1092 | 121.844 | -0.034837 | 121.8257 | 121.7613 | -0.082724 | -0.10034 | 0.087054 | 121.6285 | -0.061976 | 121.8303 | 121.7637 | 0.13527 | 0.009159 | -0.28067 | 121.8493 | 121.7838 | 121.9712 | 121.7665 | -0.040121 | 121.8222 | 121.8933 | 121.6035 | 121.7289 | -0.25569
783 | 121.9574 | -121.7514 | 0.16022 | 1.4211e-13 | -0.028113 | 0.014466 | -0.0034253 | -0.011051 | 0.019698 | -0.24059 | -0.0022838 | -0.00098076 | -0.0036299 | 0.02988 | 0.011176 | 0.083459 | 0.028878 | 0.028217 | 0.11165 | 0.046148 | 0.23354 | 0.11094 | 0.083464 | -0.022535 | 0.021487 | 0.07993 | 0.15564 | -0.13419 | -0.11378 | 121.8623 | -0.04857 | 121.8349 | 121.7796 | -0.082725 | -0.11407 | 0.073321 | 121.6376 | -0.080287 | 121.8349 | 121.7729 | 0.13527 | -0.004574 | -0.2944 | 121.8631 | 121.7976 | 121.9849 | 121.7803 | -0.049275 | 121.8313 | 121.907 | 121.6172 | 121.7289 | -0.274
784.6719 | 121.9528 | -121.756 | 0.16022 | 1.4211e-13 | -0.028327 | 0.01468 | -0.0036391 | -0.011264 | 0.019484 | -0.23296 | -0.0022838 | -0.00076696 | -0.0040571 | 0.030307 | 0.01139 | 0.083459 | 0.028878 | 0.023639 | 0.1208 | 0.050727 | 0.23812 | 0.11094 | 0.097201 | -0.013377 | 0.021487 | 0.084508 | 0.16022 | -0.13419 | -0.11378 | 121.8669 | -0.039413 | 121.8394 | 121.7796 | -0.087303 | -0.10949 | 0.0779 | 121.6422 | -0.075709 | 121.8532 | 121.7775 | 0.13527 | 5e-06 | -0.2944 | 121.8768 | 121.8067 | 121.9941 | 121.7849 | -0.049275 | 121.8405 | 121.9162 | 121.6218 | 121.7426 | -0.274
786.4219 | 121.9757 | -121.7422 | 0.14648 | 1.4211e-13 | -0.028327 | 0.01468 | -0.0032117 | -0.011051 | 0.019911 | -0.24059 | -0.0020702 | -0.0011944 | -0.0040571 | 0.030094 | 0.010749 | 0.092615 | 0.038035 | 0.028217 | 0.11165 | 0.046148 | 0.23812 | 0.092626 | 0.10178 | -0.017956 | 0.035223 | 0.093665 | 0.1648 | -0.13876 | -0.10462 | 121.8349 | -0.034837 | 121.8349 | 121.7705 | -0.064409 | -0.10034 | 0.091633 | 121.6376 | -0.052819 | 121.844 | 121.7775 | 0.13985 | 0.018316 | -0.28525 | 121.8539 | 121.7884 | 121.9804 | 121.7803 | -0.053858 | 121.8359 | 121.907 | 121.6035 | 121.7243 | -0.25111
788.1719 | 121.9391 | -121.6827 | 0.14191 | 1.4211e-13 | -0.028327 | 0.01468 | -0.0034253 | -0.011264 | 0.019698 | -0.22533 | -0.0018566 | -0.00098076 | -0.0036299 | 0.030094 | 0.011176 | 0.074302 | 0.0243 | 0.023639 | 0.11165 | 0.046148 | 0.23354 | 0.1201 | 0.097201 | -0.022535 | 0.01233 | 0.075351 | 0.15107 | 0.15884 | -0.12752 | 121.8028 | -0.03026 | 121.757 | 121.7064 | -0.096461 | -0.095759 | 0.091631 | 121.5552 | -0.066556 | 121.7799 | 121.6951 | 0.13985 | 0.009158 | 0.016938 | 121.7944 | 121.7289 | 121.9163 | 121.707 | -0.021807 | 121.7581 | 121.8338 | 121.8416 | 121.6602 | -0.26943
789.9219 | 122.0215 | -121.6461 | 0.11444 | 1.4211e-13 | -0.028327 | 0.014466 | -0.0034253 | -0.011051 | 0.019911 | -0.22533 | -0.0018566 | -0.00076696 | -0.0040571 | 0.030307 | 0.010963 | 0.083459 | 0.0243 | 0.01906 | 0.11165 | 0.046148 | 0.23812 | 0.1201 | 0.10178 | -0.027113 | 0.016908 | 0.07993 | 0.14649 | -0.14334 | -0.12752 | 121.7662 | -0.002794 | 121.7296 | 121.6652 | -0.10104 | -0.068293 | 0.12368 | 121.5186 | -0.034511 | 121.7479 | 121.663 | 0.14443 | 0.032045 | -0.25778 | 121.7578 | 121.6923 | 121.8842 | 121.6704 | 0.005659 | 121.726 | 121.7926 | 121.5028 | 121.619 | -0.24196
791.5938 | 121.9162 | -121.7194 | 0.16022 | 1.4211e-13 | -0.027899 | 0.01468 | -0.0034253 | -0.011478 | 0.019698 | -0.23296 | -0.0018566 | -0.00098076 | -0.0038435 | 0.02988 | 0.010963 | 0.069723 | 0.019721 | 0.032795 | 0.11622 | 0.032411 | 0.23812 | 0.11094 | 0.088043 | -0.031692 | 0.007751 | 0.07993 | 0.14649 | -0.13876 | -0.12294 | 121.8303 | -0.043992 | 121.7891 | 121.7522 | -0.078147 | -0.12781 | 0.0779 | 121.5964 | -0.080287 | 121.8074 | 121.7271 | 0.13069 | -0.013731 | -0.29898 | 121.8356 | 121.7518 | 121.9575 | 121.7391 | -0.049275 | 121.7993 | 121.8658 | 121.5806 | 121.6877 | -0.28316
793.3281 | 121.9025 | -121.7285 | 0.13733 | 1.4211e-13 | -0.028113 | 0.014893 | -0.0034253 | -0.011051 | 0.019484 | -0.23296 | -0.0020702 | -0.00076696 | -0.0038435 | 0.030307 | 0.010963 | 0.083459 | 0.033457 | 0.023639 | 0.10707 | 0.050727 | 0.23354 | 0.1201 | 0.097201 | -0.031692 | 0.007751 | 0.075351 | 0.14649 | -0.13876 | -0.11836 | 121.8486 | -0.030261 | 121.812 | 121.7522 | -0.096461 | -0.086602 | 0.096209 | 121.6102 | -0.061978 | 121.8257 | 121.7363 | 0.12611 | 0.009157 | -0.27609 | 121.8356 | 121.7792 | 121.9621 | 121.762 | -0.017229 | 121.8039 | 121.875 | 121.5898 | 121.6968 | -0.25569
795 | 121.907 | -121.7514 | 0.13733 | 1.4211e-13 | -0.027899 | 0.01468 | -0.0038527 | -0.011051 | 0.019911 | -0.23296 | -0.0020702 | -0.00098076 | -0.0040571 | 0.030094 | 0.01139 | 0.074302 | 0.0243 | 0.014482 | 0.11165 | 0.046148 | 0.24269 | 0.1201 | 0.092622 | -0.036271 | 0.021487 | 0.070773 | 0.14191 | -0.14334 | -0.12752 | 121.8715 | -0.025682 | 121.8257 | 121.7659 | -0.10562 | -0.091181 | 0.10537 | 121.6239 | -0.066556 | 121.844 | 121.7729 | 0.149 | 0.004578 | -0.28067 | 121.8631 | 121.7976 | 121.9941 | 121.7757 | -0.017229 | 121.8222 | 121.8933 | 121.6081 | 121.7151 | -0.26485
796.7344 | 122.0261 | -121.7148 | 0.11444 | 1.4211e-13 | -0.028327 | 0.01468 | -0.0036391 | -0.011264 | 0.019911 | -0.24822 | -0.0027112 | -0.00055336 | -0.0040571 | 0.030094 | 0.010963 | 0.074302 | 0.028878 | 0.014482 | 0.11165 | 0.041569 | 0.22896 | 0.11552 | 0.097201 | -0.027113 | 0.007751 | 0.075351 | 0.14649 | -0.13419 | -0.11836 | 121.8303 | -0.002794 | 121.7891 | 121.7293 | -0.10104 | -0.072872 | 0.11452 | 121.5964 | -0.03909 | 121.812 | 121.7225 | 0.12611 | 0.032045 | -0.24863 | 121.8264 | 121.7564 | 121.9437 | 121.7437 | 0.00108 | 121.7901 | 121.8613 | 121.5806 | 121.6877 | -0.2328
798.4688 | 121.994 | -121.7239 | 0.11444 | 1.4211e-13 | -0.028327 | 0.01468 | -0.0034253 | -0.011051 | 0.019698 | -0.23296 | -0.0018566 | -0.00076696 | -0.0042707 | 0.030094 | 0.010749 | 0.07888 | 0.028878 | 0.032795 | 0.10707 | 0.041569 | 0.23354 | 0.11094 | 0.097201 | -0.027113 | 0.016908 | 0.07993 | 0.14649 | -0.10671 | -0.12294 | 121.8349 | -0.007373 | 121.8028 | 121.7567 | -0.078147 | -0.072872 | 0.1191 | 121.601 | -0.034511 | 121.8211 | 121.7408 | 0.13985 | 0.032045 | -0.22115 | 121.831 | 121.7655 | 121.9575 | 121.7528 | -0.003499 | 121.8039 | 121.8704 | 121.6172 | 121.6968 | -0.23738
800.2031 | 122.0352 | -121.6873 | 0.10529 | 1.4211e-13 | -0.028327 | 0.01468 | -0.0034253 | -0.011692 | 0.019911 | -0.22533 | -0.0022838 | -0.00098076 | -0.0036299 | 0.030307 | 0.010963 | 0.074302 | 0.019721 | 0.01906 | 0.10707 | 0.046148 | 0.22896 | 0.11094 | 0.097201 | -0.031692 | 0.01233 | 0.07993 | 0.14649 | -0.13876 | -0.11378 | 121.7983 | 0.001782 | 121.7616 | 121.7064 | -0.091882 | -0.059138 | 0.12367 | 121.5735 | -0.025356 | 121.7845 | 121.6996 | 0.12611 | 0.0412 | -0.24405 | 121.7944 | 121.7335 | 121.9163 | 121.707 | 0.005656 | 121.7672 | 121.8338 | 121.5486 | 121.6556 | -0.21907
801.9375 | 121.9482 | -121.7606 | 0.13275 | 1.4211e-13 | -0.028327 | 0.01468 | -0.0034253 | -0.011051 | 0.019698 | -0.23296 | -0.0020702 | -0.0011944 | -0.0040571 | 0.030307 | 0.010749 | 0.07888 | 0.028878 | 0.032795 | 0.11165 | 0.050727 | 0.23812 | 0.1201 | 0.10178 | -0.008798 | 0.016908 | 0.07993 | 0.15564 | -0.13419 | -0.12294 | 121.8807 | -0.021104 | 121.8394 | 121.7934 | -0.087305 | -0.082024 | 0.10537 | 121.6376 | -0.052821 | 121.8623 | 121.7775 | 0.13985 | 0.022892 | -0.26694 | 121.8722 | 121.8113 | 121.9987 | 121.7894 | -0.012651 | 121.8405 | 121.9162 | 121.6264 | 121.7518 | -0.25569
803.625 | 121.9528 | -121.7422 | 0.12817 | 1.4211e-13 | -0.027899 | 0.01468 | -0.0038527 | -0.011478 | 0.019484 | -0.23296 | -0.0020702 | -0.0011944 | -0.0036299 | 0.030307 | 0.010963 | 0.088037 | 0.028878 | 0.028217 | 0.11165 | 0.046148 | 0.24269 | 0.1201 | 0.097201 | 0.027831 | 0.01233 | 0.075351 | 0.15107 | -0.14792 | -0.11378 | 121.8623 | -0.016527 | 121.8303 | 121.7705 | -0.091883 | -0.082026 | 0.11452 | 121.6285 | -0.052823 | 121.8394 | 121.7546 | 0.12611 | 0.022891 | -0.2761 | 121.8539 | 121.7884 | 121.9849 | 121.7711 | -0.008074 | 121.8176 | 121.8933 | 121.5943 | 121.7701 | -0.24196
805.375 | 121.9711 | -121.7422 | 0.13733 | 1.4211e-13 | -0.02854 | 0.014893 | -0.0038527 | -0.011264 | 0.019698 | -0.24059 | -0.0022838 | -0.00076696 | -0.0036299 | 0.030521 | 0.01139 | 0.07888 | 0.028878 | 0.01906 | 0.11622 | 0.046148 | 0.23354 | 0.1201 | 0.088043 | 0.03241 | 0.016908 | 0.07993 | 0.15564 | -0.13876 | -0.12752 | 121.8623 | -0.021104 | 121.8211 | 121.7613 | -0.10104 | -0.091181 | 0.096209 | 121.6147 | -0.057399 | 121.8303 | 121.7592 | 0.14443 | 0.018314 | -0.27609 | 121.8585 | 121.7884 | 121.9758 | 121.7711 | -0.017229 | 121.8222 | 121.8979 | 121.6035 | 121.7747 | -0.26485
807.1094 | 121.9208 | -121.756 | 0.14191 | 1.4211e-13 | -0.028113 | 0.01468 | -0.0036391 | -0.011051 | 0.019484 | -0.24059 | -0.0020702 | -0.00098076 | -0.0038435 | 0.030094 | 0.011176 | 0.092615 | 0.0243 | 0.032795 | 0.11165 | 0.046148 | 0.23354 | 0.11552 | 0.10636 | 0.03241 | 0.007751 | 0.075351 | 0.14191 | -0.13876 | -0.12752 | 121.8715 | -0.03026 | 121.8486 | 121.7888 | -0.082726 | -0.095759 | 0.091631 | 121.6285 | -0.066556 | 121.8623 | 121.7637 | 0.13527 | 0 | -0.28067 | 121.8676 | 121.8021 | 121.9895 | 121.7803 | -0.026386 | 121.8313 | 121.8979 | 121.6172 | 121.7884 | -0.26943
808.8438 | 121.9162 | -121.7834 | 0.13733 | 1.4211e-13 | -0.028327 | 0.014893 | -0.0032117 | -0.011051 | 0.019911 | -0.24059 | -0.0020702 | -0.00076696 | -0.0040571 | 0.030521 | 0.011176 | 0.083459 | 0.028878 | 0.023639 | 0.11165 | 0.050727 | 0.23354 | 0.1201 | 0.10178 | 0.027831 | 0.007751 | 0.07993 | 0.14649 | -0.13876 | -0.12752 | 121.9035 | -0.025682 | 121.8669 | 121.8071 | -0.096461 | -0.086602 | 0.096209 | 121.6559 | -0.057399 | 121.8852 | 121.7912 | 0.13527 | 0.009157 | -0.27609 | 121.8951 | 121.8342 | 122.017 | 121.8123 | -0.017229 | 121.8634 | 121.9299 | 121.6447 | 121.8113 | -0.26485
810.5312 | 122.0398 | -121.7239 | 0.1236 | 1.4211e-13 | -0.028113 | 0.014466 | -0.0034253 | -0.011478 | 0.019484 | -0.23296 | -0.0020702 | -0.0011944 | -0.0040571 | 0.030307 | 0.011176 | 0.07888 | 0.033457 | 0.014482 | 0.11622 | 0.041569 | 0.23354 | 0.1201 | 0.097201 | 0.036989 | 0.016908 | 0.070773 | 0.15107 | -0.14334 | -0.12294 | 121.844 | -0.007371 | 121.8028 | 121.7384 | -0.10562 | -0.082027 | 0.10994 | 121.601 | -0.052823 | 121.8211 | 121.7408 | 0.13985 | 0.027469 | -0.26694 | 121.8402 | 121.7655 | 121.9575 | 121.7574 | -0.003496 | 121.7947 | 121.875 | 121.5806 | 121.7609 | -0.24654
812.2656 | 121.9025 | -121.756 | 0.15564 | 1.4211e-13 | -0.028327 | 0.014893 | -0.0038527 | -0.011051 | 0.019484 | -0.23296 | -0.0024974 | -0.0011944 | -0.0034163 | 0.030735 | 0.010535 | 0.07888 | 0.019721 | 0.01906 | 0.11165 | 0.046148 | 0.22896 | 0.1201 | 0.097201 | 0.027831 | 0.016908 | 0.07993 | 0.15107 | -0.13876 | -0.11836 | 121.8761 | -0.043993 | 121.8349 | 121.775 | -0.10104 | -0.10949 | 0.073319 | 121.6376 | -0.07571 | 121.8532 | 121.7729 | 0.13527 | -0.004575 | -0.29441 | 121.8676 | 121.8021 | 121.9849 | 121.7757 | -0.03554 | 121.8359 | 121.907 | 121.6172 | 121.7838 | -0.274
813.9375 | 122.0398 | -121.7056 | 0.11444 | 1.4211e-13 | -0.02854 | 0.014466 | -0.0034253 | -0.011264 | 0.019698 | -0.24059 | -0.0018566 | -0.00076696 | -0.0036299 | 0.030735 | 0.011176 | 0.07888 | 0.0243 | 0.009904 | 0.11165 | 0.046148 | 0.23354 | 0.11552 | 0.097201 | 0.023253 | 0.007751 | 0.070773 | 0.15107 | -0.14334 | -0.12752 | 121.8211 | -0.002794 | 121.7845 | 121.7155 | -0.10562 | -0.068293 | 0.1191 | 121.5781 | -0.043668 | 121.8028 | 121.7134 | 0.13527 | 0.036624 | -0.25778 | 121.8173 | 121.7518 | 121.9392 | 121.7299 | 0.00108 | 121.7764 | 121.8567 | 121.5623 | 121.7289 | -0.24196
815.6719 | 122.0123 | -121.7285 | 0.13275 | 1.4211e-13 | -0.028113 | 0.014252 | -0.0034253 | -0.011264 | 0.019484 | -0.24059 | -0.0020702 | -0.001408 | -0.0040571 | 0.030094 | 0.010749 | 0.088037 | 0.0243 | 0.014482 | 0.11165 | 0.046148 | 0.23812 | 0.1201 | 0.097201 | 0.03241 | 0.016908 | 0.07993 | 0.14649 | -0.13419 | -0.11836 | 121.8486 | -0.021104 | 121.8166 | 121.743 | -0.10562 | -0.086603 | 0.10537 | 121.6102 | -0.052821 | 121.8257 | 121.7454 | 0.13527 | 0.013735 | -0.26694 | 121.8402 | 121.7747 | 121.9666 | 121.7528 | -0.012651 | 121.8084 | 121.875 | 121.5943 | 121.7609 | -0.25111
817.4062 | 121.9757 | -121.756 | 0.13733 | 1.4211e-13 | -0.02854 | 0.015107 | -0.0036391 | -0.011264 | 0.019698 | -0.23296 | -0.0020702 | -0.0011944 | -0.0038435 | 0.030521 | 0.010749 | 0.083459 | 0.028878 | 0.01906 | 0.10249 | 0.050727 | 0.23354 | 0.1201 | 0.097201 | 0.03241 | 0.01233 | 0.07993 | 0.14649 | -0.13419 | -0.12294 | 121.8761 | -0.034839 | 121.8394 | 121.775 | -0.10104 | -0.086602 | 0.096209 | 121.633 | -0.057399 | 121.8532 | 121.7683 | 0.13527 | 0.009157 | -0.27152 | 121.8585 | 121.8067 | 121.9895 | 121.7849 | -0.017229 | 121.8359 | 121.9025 | 121.6218 | 121.7884 | -0.26027
819.0938 | 121.9574 | -121.7606 | 0.11902 | 1.4211e-13 | -0.02854 | 0.01468 | -0.0034253 | -0.011264 | 0.019698 | -0.24059 | -0.0020702 | -0.00055336 | -0.0042707 | 0.030521 | 0.011176 | 0.07888 | 0.0243 | 0.009904 | 0.11165 | 0.050727 | 0.22896 | 0.11552 | 0.074307 | 0.027831 | 0.01233 | 0.075351 | 0.14649 | -0.13419 | -0.12294 | 121.8761 | -0.007372 | 121.8394 | 121.7705 | -0.10562 | -0.068292 | 0.10994 | 121.6376 | -0.043668 | 121.8349 | 121.7729 | 0.13527 | 0.027467 | -0.25321 | 121.8722 | 121.8113 | 121.9895 | 121.7849 | -0.003498 | 121.8359 | 121.907 | 121.6264 | 121.7884 | -0.24196
820.8438 | 121.9116 | -121.8063 | 0.14648 | 1.4211e-13 | -0.02854 | 0.014893 | -0.0036391 | -0.011264 | 0.019698 | -0.2177 | -0.0020702 | -0.00098076 | -0.0038435 | 0.030521 | 0.011176 | 0.083459 | 0.033457 | 0.009904 | 0.11165 | 0.055306 | 0.24727 | 0.11552 | 0.083464 | 0.027831 | 0.016908 | 0.075351 | 0.14191 | -0.13419 | -0.11836 | 121.9219 | -0.034837 | 121.8898 | 121.8162 | -0.10562 | -0.091178 | 0.10079 | 121.688 | -0.071133 | 121.8898 | 121.8232 | 0.13527 | -0.004577 | -0.28067 | 121.918 | 121.8616 | 122.0536 | 121.8398 | -0.030963 | 121.8817 | 121.9482 | 121.6721 | 121.8342 | -0.26484
822.5781 | 122.0032 | -121.7102 | 0.14648 | 1.4211e-13 | -0.028327 | 0.01468 | -0.0036391 | -0.011478 | 0.019698 | -0.23296 | -0.0020702 | -0.0011944 | -0.0038435 | 0.030307 | 0.010749 | 0.07888 | 0.019721 | 0.014482 | 0.11622 | 0.050727 | 0.23812 | 0.11094 | 0.083464 | 0.018674 | 0.01233 | 0.07993 | 0.15107 | -0.13876 | -0.12294 | 121.8211 | -0.030259 | 121.7891 | 121.7247 | -0.09646 | -0.095757 | 0.091633 | 121.5873 | -0.066554 | 121.7937 | 121.7225 | 0.13527 | 0.004581 | -0.28525 | 121.8264 | 121.7609 | 121.9483 | 121.7299 | -0.035542 | 121.7901 | 121.8613 | 121.5714 | 121.7289 | -0.26942
824.25 | 122.0398 | -121.7331 | 0.12817 | 1.4211e-13 | -0.028327 | 0.01468 | -0.0036391 | -0.011051 | 0.019484 | -0.24059 | -0.0018566 | -0.0011944 | -0.0038435 | 0.030307 | 0.011176 | 0.07888 | 0.0243 | 0.023639 | 0.10707 | 0.041569 | 0.23812 | 0.11552 | 0.083464 | 0.036989 | 0.01233 | 0.075351 | 0.15107 | -0.14334 | -0.11836 | 121.8486 | -0.021106 | 121.812 | 121.7567 | -0.091882 | -0.086605 | 0.10994 | 121.6147 | -0.052823 | 121.8166 | 121.7454 | 0.13069 | 0.022891 | -0.27152 | 121.8402 | 121.7747 | 121.9712 | 121.7574 | -0.012653 | 121.8084 | 121.8842 | 121.5897 | 121.7701 | -0.24654
826 | 122.049 | -121.7194 | 0.10071 | 1.4211e-13 | -0.02854 | 0.014893 | -0.0034253 | -0.011692 | 0.019484 | -0.23296 | -0.0018566 | -0.00098076 | -0.0038435 | 0.030735 | 0.010963 | 0.07888 | 0.028878 | 0.014482 | 0.11165 | 0.050727 | 0.23354 | 0.12468 | 0.083464 | 0.03241 | 0.016908 | 0.075351 | 0.14649 | -0.14334 | -0.12752 | 121.844 | 0.010939 | 121.7982 | 121.7338 | -0.1102 | -0.049981 | 0.13283 | 121.5918 | -0.025357 | 121.8028 | 121.7363 | 0.14443 | 0.045778 | -0.24405 | 121.831 | 121.7701 | 121.9529 | 121.7482 | 0.023971 | 121.7947 | 121.8658 | 121.576 | 121.7518 | -0.22823
827.6719 | 122.0123 | -121.7331 | 0.13733 | 1.4211e-13 | -0.02854 | 0.01468 | -0.0040665 | -0.011264 | 0.019698 | -0.24822 | -0.0020702 | -0.00098076 | -0.0036299 | 0.030735 | 0.010963 | 0.07888 | 0.0243 | 0.014482 | 0.10707 | 0.046148 | 0.24269 | 0.11094 | 0.074307 | 0.036989 | 0.007751 | 0.07993 | 0.15107 | -0.14334 | -0.12294 | 121.844 | -0.030261 | 121.812 | 121.7476 | -0.09646 | -0.091181 | 0.10537 | 121.6102 | -0.057399 | 121.8074 | 121.7408 | 0.13069 | 0.013736 | -0.28067 | 121.8402 | 121.7792 | 121.9758 | 121.7574 | -0.026387 | 121.813 | 121.8842 | 121.5897 | 121.7701 | -0.26027
829.4062 | 121.9711 | -121.7834 | 0.14648 | 1.4211e-13 | -0.028754 | 0.014466 | -0.0034253 | -0.011051 | 0.019698 | -0.24059 | -0.0018566 | -0.00098076 | -0.0036299 | 0.030735 | 0.011176 | 0.088037 | 0.0243 | 0.014482 | 0.11165 | 0.046148 | 0.22438 | 0.11094 | 0.078886 | 0.027831 | 0.01233 | 0.075351 | 0.14649 | -0.13876 | -0.12294 | 121.8944 | -0.034837 | 121.8715 | 121.7979 | -0.09646 | -0.10034 | 0.077897 | 121.6605 | -0.071133 | 121.8623 | 121.7958 | 0.13527 | 2e-06 | -0.28525 | 121.8951 | 121.8296 | 122.0078 | 121.8077 | -0.035542 | 121.8588 | 121.9299 | 121.6447 | 121.8113 | -0.26942
831.0938 | 122.0261 | -121.7102 | 0.10986 | 1.4211e-13 | -0.02854 | 0.01468 | -0.0038527 | -0.011264 | 0.019698 | -0.23296 | -0.0020702 | -0.00098076 | -0.0042707 | 0.030521 | 0.01139 | 0.07888 | 0.028878 | 0.01906 | 0.11622 | 0.050727 | 0.23812 | 0.11094 | 0.078886 | 0.027831 | 0.01233 | 0.07993 | 0.15564 | -0.11129 | -0.12752 | 121.8211 | 0.006362 | 121.7891 | 121.7293 | -0.091882 | -0.059136 | 0.12825 | 121.5827 | -0.029933 | 121.7891 | 121.7225 | 0.13985 | 0.04578 | -0.22116 | 121.8264 | 121.7609 | 121.9483 | 121.7391 | 0.001079 | 121.7901 | 121.8658 | 121.5989 | 121.738 | -0.23738
832.8281 | 121.9986 | -121.756 | 0.13733 | 1.4211e-13 | -0.028327 | 0.01468 | -0.0034253 | -0.011478 | 0.019911 | -0.24059 | -0.0022838 | -0.00098076 | -0.0036299 | 0.030521 | 0.011176 | 0.083459 | 0.028878 | 0.014482 | 0.11165 | 0.046148 | 0.23812 | 0.11552 | 0.083464 | 0.027831 | 0.01233 | 0.075351 | 0.14191 | -0.13419 | -0.12294 | 121.8715 | -0.025682 | 121.8394 | 121.7705 | -0.10104 | -0.091181 | 0.10079 | 121.633 | -0.061978 | 121.8394 | 121.7683 | 0.13527 | 0.004578 | -0.27152 | 121.8676 | 121.8021 | 121.9941 | 121.7849 | -0.021808 | 121.8313 | 121.8979 | 121.6218 | 121.7838 | -0.26027
834.5156 | 121.9437 | -121.7697 | 0.14648 | 1.4211e-13 | -0.02854 | 0.014893 | -0.0034253 | -0.011051 | 0.019911 | -0.23296 | -0.0020702 | -0.0011944 | -0.0038435 | 0.030521 | 0.011176 | 0.07888 | 0.0243 | 0.014482 | 0.11165 | 0.050727 | 0.23354 | 0.12468 | 0.083464 | 0.027831 | 0.016908 | 0.07993 | 0.15107 | -0.14792 | -0.1321 | 121.8944 | -0.034837 | 121.8486 | 121.7842 | -0.1102 | -0.095757 | 0.087054 | 121.6376 | -0.066554 | 121.8532 | 121.7866 | 0.149 | 0.004581 | -0.29441 | 121.8814 | 121.8204 | 122.0033 | 121.794 | -0.021805 | 121.8496 | 121.9208 | 121.6218 | 121.7975 | -0.27858
836.2656 | 122.0398 | -121.7056 | 0.10529 | 1.4211e-13 | -0.028754 | 0.014893 | -0.0036391 | -0.011051 | 0.019911 | -0.22533 | -0.0024974 | -0.00076696 | -0.0042707 | 0.030521 | 0.010749 | 0.07888 | 0.019721 | 0.01906 | 0.10707 | 0.041569 | 0.23812 | 0.11094 | 0.078886 | 0.023253 | 0.016908 | 0.07993 | 0.14191 | -0.13876 | -0.12752 | 121.8166 | 0.001782 | 121.7845 | 121.7247 | -0.091882 | -0.063717 | 0.13283 | 121.5781 | -0.025356 | 121.7845 | 121.7225 | 0.14443 | 0.036621 | -0.24405 | 121.8127 | 121.7472 | 121.9437 | 121.7253 | 0.005656 | 121.7856 | 121.8475 | 121.5669 | 121.7289 | -0.2328
838 | 121.9254 | -121.7606 | 0.13733 | 1.4211e-13 | -0.02854 | 0.014466 | -0.0036391 | -0.011051 | 0.019698 | -0.23296 | -0.0022838 | -0.001408 | -0.0040571 | 0.030948 | 0.011176 | 0.074302 | 0.028878 | 0.009904 | 0.11165 | 0.046148 | 0.23812 | 0.11552 | 0.083464 | 0.027831 | 0.016908 | 0.07993 | 0.14649 | -0.13876 | -0.12294 | 121.8761 | -0.025682 | 121.8349 | 121.7705 | -0.10562 | -0.091181 | 0.10079 | 121.6376 | -0.057399 | 121.844 | 121.7775 | 0.13985 | 0.009157 | -0.27609 | 121.8722 | 121.8067 | 121.9987 | 121.7894 | -0.021808 | 121.8405 | 121.907 | 121.6218 | 121.7884 | -0.26027
839.6719 | 122.0261 | -121.7377 | 0.13275 | 1.4211e-13 | -0.028754 | 0.014466 | -0.0036391 | -0.011692 | 0.019698 | -0.22533 | -0.0020702 | -0.00098076 | -0.0038435 | 0.030735 | 0.010963 | 0.074302 | 0.028878 | 0.009904 | 0.11622 | 0.046148 | 0.23354 | 0.1201 | 0.083464 | 0.027831 | 0.01233 | 0.07993 | 0.15564 | -0.14334 | -0.12752 | 121.8578 | -0.016526 | 121.812 | 121.7476 | -0.1102 | -0.086603 | 0.10079 | 121.6102 | -0.052821 | 121.8211 | 121.75 | 0.13985 | 0.022892 | -0.27609 | 121.8539 | 121.7838 | 121.9712 | 121.7665 | -0.012651 | 121.8176 | 121.8933 | 121.5943 | 121.7655 | -0.26027
841.4219 | 121.9345 | -121.7972 | 0.15106 | 1.4211e-13 | -0.028113 | 0.014893 | -0.0036391 | -0.011692 | 0.019698 | -0.23296 | -0.0018566 | -0.001408 | -0.0038435 | 0.030735 | 0.010963 | 0.07888 | 0.019721 | 0.01906 | 0.10249 | 0.050727 | 0.23354 | 0.10636 | 0.078886 | 0.023253 | 0.01233 | 0.075351 | 0.14649 | -0.13876 | -0.11836 | 121.9035 | -0.048572 | 121.8761 | 121.8162 | -0.087303 | -0.10034 | 0.082476 | 121.6788 | -0.075711 | 121.8761 | 121.8095 | 0.13069 | -0.004576 | -0.28983 | 121.8997 | 121.8479 | 122.0307 | 121.8169 | -0.044699 | 121.8725 | 121.9437 | 121.6584 | 121.8204 | -0.26942
843.1094 | 122.0078 | -121.7102 | 0.1236 | 1.4211e-13 | -0.028754 | 0.014893 | -0.0034253 | -0.011264 | 0.019698 | -0.24059 | -0.0022838 | -0.0011944 | -0.0040571 | 0.030735 | 0.010749 | 0.083459 | 0.019721 | 0.009904 | 0.10707 | 0.050727 | 0.23812 | 0.11552 | 0.083464 | 0.027831 | 0.01233 | 0.075351 | 0.15564 | -0.14334 | -0.12752 | 121.8257 | -0.016528 | 121.7937 | 121.7201 | -0.10562 | -0.072869 | 0.11452 | 121.5827 | -0.048245 | 121.7937 | 121.7225 | 0.13985 | 0.032047 | -0.26694 | 121.8173 | 121.7609 | 121.9483 | 121.7299 | -0.008075 | 121.7856 | 121.8658 | 121.5669 | 121.738 | -0.25111
844.8438 | 122.0123 | -121.7514 | 0.11902 | 1.4211e-13 | -0.02854 | 0.01468 | -0.0034253 | -0.011478 | 0.019698 | -0.23296 | -0.0020702 | -0.00076696 | -0.0040571 | 0.030521 | 0.011604 | 0.07888 | 0.0243 | 0.009904 | 0.11165 | 0.050727 | 0.23354 | 0.11552 | 0.088043 | 0.036989 | 0.016908 | 0.070773 | 0.15107 | -0.13876 | -0.11836 | 121.8669 | -0.007372 | 121.8303 | 121.7613 | -0.10562 | -0.068292 | 0.11452 | 121.633 | -0.048246 | 121.8394 | 121.7683 | 0.13527 | 0.032046 | -0.25778 | 121.8631 | 121.8021 | 121.9849 | 121.7757 | -0.003498 | 121.8222 | 121.9025 | 121.6126 | 121.7884 | -0.23738
846.5312 | 121.994 | -121.7651 | 0.13275 | 1.4211e-13 | -0.02854 | 0.014466 | -0.0036391 | -0.011264 | 0.019484 | -0.23296 | -0.0020702 | -0.0011944 | -0.0038435 | 0.030948 | 0.010963 | 0.07888 | 0.0243 | 0.014482 | 0.11165 | 0.050727 | 0.23812 | 0.11552 | 0.088043 | 0.041567 | 0.007751 | 0.075351 | 0.15564 | -0.13876 | -0.12294 | 121.8807 | -0.021104 | 121.844 | 121.7796 | -0.10104 | -0.082024 | 0.10537 | 121.6422 | -0.0574 | 121.8532 | 121.7729 | 0.13069 | 0.022892 | -0.27152 | 121.8768 | 121.8159 | 122.0033 | 121.7894 | -0.01723 | 121.8405 | 121.9208 | 121.6264 | 121.8067 | -0.25569
848.2812 | 121.9894 | -121.7743 | 0.14191 | 1.4211e-13 | -0.028754 | 0.01468 | -0.0034253 | -0.011264 | 0.01927 | -0.24059 | -0.0022838 | -0.0011944 | -0.0038435 | 0.030948 | 0.010963 | 0.083459 | 0.0243 | 0.009904 | 0.11165 | 0.050727 | 0.23812 | 0.1201 | 0.083464 | 0.027831 | 0.021487 | 0.07993 | 0.15564 | -0.13876 | -0.12752 | 121.8944 | -0.03026 | 121.8578 | 121.7842 | -0.1102 | -0.09118 | 0.09621 | 121.6468 | -0.061977 | 121.8578 | 121.7958 | 0.149 | 0.013736 | -0.28067 | 121.8859 | 121.825 | 122.0124 | 121.7986 | -0.021807 | 121.8542 | 121.9299 | 121.6355 | 121.8021 | -0.26943
850.0156 | 122.0123 | -121.7422 | 0.12817 | 1.4211e-13 | -0.02854 | 0.014252 | -0.0034253 | -0.011692 | 0.019484 | -0.22533 | -0.0022838 | -0.00098076 | -0.0038435 | 0.030735 | 0.011176 | 0.07888 | 0.028878 | 0.014482 | 0.11622 | 0.050727 | 0.22896 | 0.11552 | 0.078886 | 0.018674 | 0.007751 | 0.075351 | 0.14649 | -0.13876 | -0.12294 | 121.8578 | -0.011949 | 121.8211 | 121.7567 | -0.10104 | -0.077447 | 0.10078 | 121.6193 | -0.052823 | 121.8211 | 121.75 | 0.13069 | 0.018312 | -0.26694 | 121.8585 | 121.793 | 121.9712 | 121.7711 | -0.012653 | 121.8176 | 121.8887 | 121.6035 | 121.7609 | -0.25111
851.7031 | 122.0673 | -121.7239 | 0.10071 | 1.4211e-13 | -0.02854 | 0.01468 | -0.0036391 | -0.011264 | 0.019484 | -0.24059 | -0.001643 | -0.0011944 | -0.0038435 | 0.030948 | 0.010963 | 0.07888 | 0.028878 | 0.009904 | 0.11622 | 0.032411 | 0.23812 | 0.11094 | 0.088043 | 0.023253 | 0.007751 | 0.07993 | 0.15107 | -0.14334 | -0.12294 | 121.8349 | 0.015517 | 121.8028 | 121.7338 | -0.10104 | -0.068297 | 0.13741 | 121.601 | -0.020778 | 121.812 | 121.7317 | 0.13069 | 0.050357 | -0.24405 | 121.8402 | 121.7563 | 121.9621 | 121.7528 | 0.010234 | 121.8039 | 121.875 | 121.5806 | 121.7472 | -0.22365
853.4375 | 122.0215 | -121.7422 | 0.12817 | 1.4211e-13 | -0.02854 | 0.014252 | -0.0034253 | -0.011692 | 0.01927 | -0.23296 | -0.0018566 | -0.00076696 | -0.0038435 | 0.030307 | 0.01139 | 0.083459 | 0.0243 | 0.009904 | 0.11165 | 0.055306 | 0.23354 | 0.1201 | 0.078886 | 0.023253 | 0.016908 | 0.075351 | 0.15564 | -0.13419 | -0.12294 | 121.8623 | -0.016527 | 121.8257 | 121.7522 | -0.1102 | -0.072868 | 0.10536 | 121.6193 | -0.052823 | 121.8211 | 121.7592 | 0.13985 | 0.027469 | -0.26236 | 121.8539 | 121.7976 | 121.9758 | 121.7665 | -0.008074 | 121.8176 | 121.8979 | 121.6081 | 121.7655 | -0.25111
855.1094 | 122.0718 | -121.7148 | 0.1236 | 1.4211e-13 | -0.028754 | 0.01468 | -0.0034253 | -0.011478 | 0.019698 | -0.24822 | -0.0022838 | -0.0011944 | -0.0040571 | 0.030948 | 0.010963 | 0.074302 | 0.019721 | 0.014482 | 0.11165 | 0.03699 | 0.23812 | 0.1201 | 0.074307 | 0.023253 | 0.01233 | 0.07993 | 0.16022 | -0.12961 | -0.12294 | 121.8349 | -0.011949 | 121.7891 | 121.7293 | -0.10562 | -0.086606 | 0.11452 | 121.5918 | -0.043666 | 121.7891 | 121.7271 | 0.13527 | 0.036626 | -0.2532 | 121.8264 | 121.7518 | 121.9529 | 121.7345 | -0.003496 | 121.7947 | 121.875 | 121.5852 | 121.738 | -0.24654
856.8594 | 122.0673 | -121.7422 | 0.11444 | 1.4211e-13 | -0.02854 | 0.014466 | -0.0036391 | -0.011264 | 0.019698 | -0.23296 | -0.0020702 | -0.00098076 | -0.0038435 | 0.030735 | 0.011176 | 0.074302 | 0.028878 | 0.005325 | 0.11622 | 0.059885 | 0.24269 | 0.1201 | 0.083464 | 0.046146 | 0.007751 | 0.07993 | 0.15107 | -0.13876 | -0.1321 | 121.8623 | 0.001784 | 121.8166 | 121.7476 | -0.11478 | -0.054556 | 0.12825 | 121.6102 | -0.034511 | 121.8257 | 121.75 | 0.13985 | 0.036624 | -0.25321 | 121.8585 | 121.8021 | 121.9849 | 121.7711 | 0.005659 | 121.8222 | 121.8933 | 121.6035 | 121.7884 | -0.24654
858.6094 | 121.8979 | -121.7743 | 0.15106 | 1.4211e-13 | -0.028754 | 0.01468 | -0.0036391 | -0.011478 | 0.019484 | -0.24059 | -0.0022838 | -0.00098076 | -0.0042707 | 0.030521 | 0.010749 | 0.07888 | 0.019721 | 0.014482 | 0.10249 | 0.046148 | 0.24269 | 0.12468 | 0.069728 | 0.03241 | 0.016908 | 0.07993 | 0.15564 | -0.14792 | -0.12752 | 121.899 | -0.048572 | 121.8532 | 121.7888 | -0.1102 | -0.10491 | 0.091633 | 121.6468 | -0.071132 | 121.844 | 121.7912 | 0.14443 | 0.004581 | -0.29898 | 121.8768 | 121.8204 | 122.017 | 121.794 | -0.026383 | 121.8542 | 121.9299 | 121.6264 | 121.8067 | -0.27858
860.3438 | 121.9345 | -121.7834 | 0.16022 | 1.4211e-13 | -0.02854 | 0.01468 | -0.0038527 | -0.011478 | 0.019698 | -0.23296 | -0.0022838 | -0.0011944 | -0.0040571 | 0.030735 | 0.010963 | 0.083459 | 0.0243 | 0.009904 | 0.11165 | 0.046148 | 0.24727 | 0.11552 | 0.074307 | 0.036989 | 0.01233 | 0.075351 | 0.15564 | -0.14334 | -0.1321 | 121.899 | -0.04857 | 121.8669 | 121.7934 | -0.10562 | -0.11407 | 0.087057 | 121.6513 | -0.084866 | 121.8578 | 121.7958 | 0.14443 | -0.004574 | -0.30356 | 121.8951 | 121.8296 | 122.0307 | 121.8077 | -0.044696 | 121.8588 | 121.9391 | 121.6401 | 121.8204 | -0.29231
862.0938 | 122.081 | -121.7377 | 0.13275 | 1.4211e-13 | -0.028754 | 0.014466 | -0.0036391 | -0.011478 | 0.019698 | -0.24059 | -0.0022838 | -0.00098076 | -0.0038435 | 0.030948 | 0.010749 | 0.074302 | 0.028878 | 0.005325 | 0.11165 | 0.046148 | 0.23812 | 0.1201 | 0.078886 | 0.041567 | 0.01233 | 0.070773 | 0.15564 | -0.13876 | -0.12294 | 121.8578 | -0.021104 | 121.812 | 121.743 | -0.11478 | -0.086603 | 0.10537 | 121.6147 | -0.061978 | 121.8166 | 121.75 | 0.13527 | 0.022892 | -0.27152 | 121.8493 | 121.7838 | 121.9758 | 121.7665 | -0.012651 | 121.8084 | 121.8933 | 121.5989 | 121.7792 | -0.25569
863.8438 | 121.9345 | -121.7834 | 0.14648 | 1.4211e-13 | -0.028754 | 0.015107 | -0.0036391 | -0.011692 | 0.019698 | -0.24822 | -0.0018566 | -0.00076696 | -0.0038435 | 0.030521 | 0.010963 | 0.083459 | 0.019721 | 0.014482 | 0.11165 | 0.046148 | 0.23812 | 0.11094 | 0.083464 | 0.036989 | 0.007751 | 0.075351 | 0.15564 | -0.13419 | -0.12752 | 121.8944 | -0.034837 | 121.8669 | 121.7979 | -0.09646 | -0.10034 | 0.091633 | 121.6559 | -0.071133 | 121.8669 | 121.7912 | 0.13527 | 0.009159 | -0.28067 | 121.8951 | 121.8296 | 122.0216 | 121.8032 | -0.035542 | 121.8588 | 121.9391 | 121.6493 | 121.8204 | -0.274
865.5312 | 122.0581 | -121.7377 | 0.11444 | 1.4211e-13 | -0.028754 | 0.01468 | -0.0034253 | -0.011478 | 0.01927 | -0.22533 | -0.0022838 | -0.0011944 | -0.0038435 | 0.030735 | 0.01139 | 0.07888 | 0.0243 | 0.014482 | 0.11165 | 0.050727 | 0.23812 | 0.1201 | 0.088043 | 0.041567 | 0.016908 | 0.07993 | 0.15564 | -0.13419 | -0.1321 | 121.8578 | -0.002794 | 121.8166 | 121.7522 | -0.10562 | -0.063714 | 0.12368 | 121.6056 | -0.034511 | 121.8257 | 121.7546 | 0.149 | 0.041202 | -0.24863 | 121.8493 | 121.7884 | 121.9758 | 121.762 | 0.005659 | 121.8176 | 121.8933 | 121.6035 | 121.7792 | -0.24654
867.2656 | 122.0261 | -121.7331 | 0.11444 | 1.4211e-13 | -0.02854 | 0.01468 | -0.0034253 | -0.011264 | 0.019484 | -0.24059 | -0.0022838 | -0.001408 | -0.0040571 | 0.031162 | 0.011176 | 0.088037 | 0.019721 | 0.009904 | 0.11622 | 0.041569 | 0.23812 | 0.1201 | 0.074307 | 0.041567 | 0.01233 | 0.084508 | 0.16022 | -0.14334 | -0.12294 | 121.8532 | 0.001784 | 121.8211 | 121.743 | -0.1102 | -0.072872 | 0.12368 | 121.6102 | -0.029933 | 121.8074 | 121.7454 | 0.13527 | 0.045781 | -0.25778 | 121.8493 | 121.7747 | 121.9712 | 121.7528 | 0.005659 | 121.8176 | 121.8933 | 121.5897 | 121.7747 | -0.23738
869 | 121.994 | -121.7789 | 0.1236 | 1.4211e-13 | -0.02854 | 0.014252 | -0.0038527 | -0.011692 | 0.019484 | -0.23296 | -0.0020702 | -0.001408 | -0.0036299 | 0.030948 | 0.010963 | 0.083459 | 0.010564 | 0.014482 | 0.11622 | 0.055306 | 0.23812 | 0.1201 | 0.078886 | 0.03241 | 0.01233 | 0.07993 | 0.16022 | -0.13876 | -0.12294 | 121.899 | -0.007371 | 121.8623 | 121.7934 | -0.10562 | -0.06829 | 0.11452 | 121.6559 | -0.043666 | 121.8578 | 121.7912 | 0.13527 | 0.036626 | -0.26236 | 121.8951 | 121.8342 | 122.017 | 121.7894 | -0.003496 | 121.8588 | 121.9391 | 121.6401 | 121.8113 | -0.24654
870.75 | 122.0123 | -121.7514 | 0.13733 | 1.4211e-13 | -0.028754 | 0.014893 | -0.0038527 | -0.011264 | 0.019484 | -0.23296 | -0.0020702 | -0.0011944 | -0.0042707 | 0.030948 | 0.010749 | 0.083459 | 0.0243 | 0.009904 | 0.1208 | 0.046148 | 0.23812 | 0.11552 | 0.083464 | 0.041567 | 0.01233 | 0.07993 | 0.15564 | -0.11129 | -0.12294 | 121.8669 | -0.016525 | 121.8349 | 121.7613 | -0.10562 | -0.091181 | 0.10079 | 121.6285 | -0.057399 | 121.8349 | 121.7637 | 0.13527 | 0.018314 | -0.24862 | 121.8722 | 121.7976 | 121.9895 | 121.7757 | -0.021808 | 121.8313 | 121.907 | 121.6401 | 121.793 | -0.26027
872.4219 | 121.9208 | -121.7972 | 0.14191 | 1.4211e-13 | -0.028327 | 0.01468 | -0.0034253 | -0.011692 | 0.019484 | -0.22533 | -0.0020702 | -0.0011944 | -0.0038435 | 0.030521 | 0.010749 | 0.07888 | 0.0243 | 0.005325 | 0.11622 | 0.046148 | 0.23812 | 0.1201 | 0.088043 | 0.041567 | 0.016908 | 0.075351 | 0.1648 | -0.13419 | -0.12294 | 121.9173 | -0.025682 | 121.8761 | 121.8025 | -0.11478 | -0.095759 | 0.09621 | 121.6742 | -0.066556 | 121.8852 | 121.8141 | 0.13985 | 0.022893 | -0.27609 | 121.9134 | 121.8433 | 122.0353 | 121.8215 | -0.021807 | 121.8725 | 121.962 | 121.663 | 121.8387 | -0.26485
874.1562 | 121.9757 | -121.788 | 0.16479 | 1.4211e-13 | -0.028754 | 0.014466 | -0.0036391 | -0.011692 | 0.019484 | -0.24059 | -0.0020702 | -0.00098076 | -0.0040571 | 0.030948 | 0.010749 | 0.083459 | 0.0243 | 0.009904 | 0.11165 | 0.055306 | 0.23354 | 0.11552 | 0.083464 | 0.041567 | 0.01233 | 0.07993 | 0.15564 | -0.14334 | -0.12294 | 121.9035 | -0.053148 | 121.8715 | 121.7979 | -0.10562 | -0.10949 | 0.068743 | 121.6651 | -0.084865 | 121.8715 | 121.8004 | 0.13527 | -0.009152 | -0.30814 | 121.8997 | 121.8433 | 122.0216 | 121.8123 | -0.049274 | 121.868 | 121.9437 | 121.6447 | 121.8296 | -0.28773
875.9062 | 121.9574 | -121.8018 | 0.15564 | 1.4211e-13 | -0.028754 | 0.014466 | -0.0038527 | -0.011692 | 0.019484 | -0.23296 | -0.0022838 | -0.0011944 | -0.0040571 | 0.030948 | 0.010963 | 0.07888 | 0.019721 | 0.023639 | 0.11622 | 0.046148 | 0.23812 | 0.11552 | 0.083464 | 0.036989 | 0.021487 | 0.075351 | 0.15107 | -0.13876 | -0.12752 | 121.9173 | -0.039415 | 121.8806 | 121.8254 | -0.091882 | -0.10949 | 0.082477 | 121.6742 | -0.080289 | 121.8852 | 121.8232 | 0.149 | -0.004575 | -0.29441 | 121.918 | 121.8479 | 122.0399 | 121.8215 | -0.040119 | 121.8771 | 121.9528 | 121.663 | 121.8387 | -0.28316
877.6562 | 121.9391 | -121.788 | 0.14191 | 1.4211e-13 | -0.028754 | 0.014466 | -0.0034253 | -0.011478 | 0.019484 | -0.24059 | -0.0022838 | -0.00076696 | -0.0040571 | 0.030948 | 0.010963 | 0.07888 | 0.019721 | 0.014482 | 0.10707 | 0.041569 | 0.23354 | 0.1201 | 0.083464 | 0.036989 | 0.016908 | 0.07993 | 0.15564 | -0.13876 | -0.12294 | 121.9081 | -0.034839 | 121.8669 | 121.8025 | -0.10562 | -0.10034 | 0.091631 | 121.6651 | -0.061977 | 121.8715 | 121.8049 | 0.13985 | 0.013736 | -0.28067 | 121.8951 | 121.8296 | 122.0216 | 121.8077 | -0.021807 | 121.868 | 121.9437 | 121.6493 | 121.825 | -0.26485
879.3281 | 121.9437 | -121.7606 | 0.12817 | 1.4211e-13 | -0.02854 | 0.01468 | -0.0036391 | -0.011692 | 0.019911 | -0.24822 | -0.0022838 | -0.0011944 | -0.0040571 | 0.030948 | 0.011604 | 0.083459 | 0.015142 | 0.005325 | 0.11165 | 0.041569 | 0.23354 | 0.11552 | 0.074307 | 0.041567 | 0.016908 | 0.084508 | 0.15564 | -0.10214 | -0.12752 | 121.8761 | -0.016527 | 121.844 | 121.7659 | -0.1102 | -0.086605 | 0.10536 | 121.633 | -0.043666 | 121.8349 | 121.7775 | 0.14443 | 0.027469 | -0.23031 | 121.8722 | 121.8021 | 121.9941 | 121.7757 | -0.012653 | 121.8451 | 121.9162 | 121.6584 | 121.8021 | -0.25569
881 | 121.9849 | -121.756 | 0.13733 | 1.4211e-13 | -0.028968 | 0.01468 | -0.0036391 | -0.011905 | 0.01927 | -0.24059 | -0.0020702 | -0.00076696 | -0.0040571 | 0.030948 | 0.010963 | 0.074302 | 0.015142 | 0.005325 | 0.11622 | 0.046148 | 0.23812 | 0.11552 | 0.088043 | 0.041567 | 0.016908 | 0.084508 | 0.15107 | -0.13876 | -0.11836 | 121.8715 | -0.021104 | 121.8303 | 121.7613 | -0.1102 | -0.091181 | 0.10079 | 121.6376 | -0.052821 | 121.844 | 121.7729 | 0.13527 | 0.013736 | -0.27609 | 121.8722 | 121.8021 | 121.9941 | 121.7711 | -0.021808 | 121.8405 | 121.907 | 121.6172 | 121.7975 | -0.25569
882.75 | 122.0306 | -121.7148 | 0.10986 | 1.4211e-13 | -0.028754 | 0.01468 | -0.0036391 | -0.011692 | 0.019484 | -0.23296 | -0.0020702 | -0.001408 | -0.0038435 | 0.030735 | 0.010963 | 0.07888 | 0.019721 | 0.009904 | 0.10707 | 0.050727 | 0.24269 | 0.11552 | 0.078886 | 0.046146 | 0.01233 | 0.070773 | 0.15107 | -0.13419 | -0.12294 | 121.8303 | -0.002795 | 121.7937 | 121.7247 | -0.10562 | -0.059136 | 0.13283 | 121.5918 | -0.03909 | 121.7937 | 121.7271 | 0.13527 | 0.041202 | -0.24405 | 121.8219 | 121.7655 | 121.9575 | 121.7345 | 0.005658 | 121.7856 | 121.8658 | 121.5806 | 121.7609 | -0.2328
884.4844 | 121.9437 | -121.8018 | 0.14191 | 1.4211e-13 | -0.028968 | 0.014466 | -0.0038527 | -0.011692 | 0.01927 | -0.2177 | -0.0022838 | -0.00098076 | -0.0038435 | 0.030948 | 0.010963 | 0.07888 | 0.015142 | 0.014482 | 0.11165 | 0.046148 | 0.23354 | 0.1201 | 0.083464 | 0.041567 | 0.003172 | 0.070773 | 0.14649 | -0.13876 | -0.11836 | 121.9219 | -0.03026 | 121.8806 | 121.8162 | -0.10562 | -0.095759 | 0.091631 | 121.6834 | -0.071134 | 121.8852 | 121.8049 | 0.12153 | 0.004579 | -0.28067 | 121.9134 | 121.8479 | 122.0353 | 121.8169 | -0.021807 | 121.8725 | 121.9482 | 121.663 | 121.8433 | -0.26027
886.1562 | 122.0078 | -121.7743 | 0.12817 | 1.4211e-13 | -0.028754 | 0.01468 | -0.0032117 | -0.011478 | 0.019484 | -0.22533 | -0.0020702 | -0.00098076 | -0.0040571 | 0.030735 | 0.011176 | 0.07888 | 0.019721 | 0.009904 | 0.11622 | 0.041569 | 0.23354 | 0.10636 | 0.083464 | 0.041567 | 0.01233 | 0.07993 | 0.14649 | -0.13419 | -0.12294 | 121.8807 | -0.011949 | 121.8532 | 121.7842 | -0.096459 | -0.086605 | 0.10536 | 121.6514 | -0.048244 | 121.8578 | 121.7866 | 0.13527 | 0.018312 | -0.26236 | 121.8905 | 121.8159 | 122.0078 | 121.794 | -0.021811 | 121.8542 | 121.9208 | 121.6401 | 121.8159 | -0.25111
887.9062 | 122.0535 | -121.7377 | 0.11902 | 1.4211e-13 | -0.028754 | 0.014466 | -0.0036391 | -0.011478 | 0.01927 | -0.24059 | -0.0022838 | -0.001408 | -0.0038435 | 0.030735 | 0.010749 | 0.07888 | 0.019721 | 0.009904 | 0.11165 | 0.041569 | 0.23812 | 0.1201 | 0.088043 | 0.041567 | 0.016908 | 0.07993 | 0.15107 | -0.14334 | -0.12294 | 121.8578 | -0.007372 | 121.8166 | 121.7476 | -0.1102 | -0.07745 | 0.1191 | 121.6147 | -0.039089 | 121.8257 | 121.7546 | 0.13985 | 0.032046 | -0.26236 | 121.8493 | 121.7792 | 121.9758 | 121.7574 | 0.001081 | 121.8176 | 121.8887 | 121.5943 | 121.7792 | -0.24196
889.5938 | 122.0627 | -121.7422 | 0.11902 | 1.4211e-13 | -0.028968 | 0.01468 | -0.0036391 | -0.011478 | 0.019484 | -0.24822 | -0.0020702 | -0.0011944 | -0.0036299 | 0.031162 | 0.011176 | 0.069723 | 0.0243 | 0.014482 | 0.11165 | 0.050727 | 0.23354 | 0.11094 | 0.069728 | 0.041567 | 0.01233 | 0.07993 | 0.15107 | -0.13419 | -0.11836 | 121.8532 | -0.007372 | 121.812 | 121.7567 | -0.09646 | -0.068292 | 0.11452 | 121.6239 | -0.039089 | 121.812 | 121.7546 | 0.13069 | 0.032046 | -0.25321 | 121.8539 | 121.793 | 121.9758 | 121.7665 | -0.008077 | 121.8222 | 121.8933 | 121.6081 | 121.7838 | -0.23738
891.3438 | 122.0901 | -121.7331 | 0.1236 | 1.4211e-13 | -0.028968 | 0.014466 | -0.0042801 | -0.011905 | 0.019484 | -0.24059 | -0.0022838 | -0.00076696 | -0.0042707 | 0.030948 | 0.011176 | 0.083459 | 0.019721 | 0.01906 | 0.11622 | 0.050727 | 0.24269 | 0.11552 | 0.083464 | 0.046146 | 0.021487 | 0.07993 | 0.16022 | -0.13876 | -0.11836 | 121.8486 | -0.007371 | 121.8166 | 121.7522 | -0.096461 | -0.072869 | 0.1191 | 121.6147 | -0.043666 | 121.8166 | 121.7546 | 0.13985 | 0.036626 | -0.26236 | 121.8493 | 121.7838 | 121.9758 | 121.7528 | -0.008075 | 121.813 | 121.8933 | 121.5943 | 121.7792 | -0.24196
893.0938 | 122.0215 | -121.7377 | 0.13275 | 1.4211e-13 | -0.028754 | 0.01468 | -0.0036391 | -0.011478 | 0.019484 | -0.24822 | -0.0022838 | -0.0011944 | -0.0040571 | 0.030948 | 0.010963 | 0.083459 | 0.0243 | 0.01906 | 0.11622 | 0.046148 | 0.24269 | 0.1201 | 0.074307 | 0.046146 | 0.01233 | 0.075351 | 0.16022 | -0.13876 | -0.12294 | 121.8578 | -0.016526 | 121.8211 | 121.7567 | -0.10104 | -0.086603 | 0.10994 | 121.6147 | -0.0574 | 121.812 | 121.75 | 0.13527 | 0.027471 | -0.27152 | 121.8539 | 121.7838 | 121.9804 | 121.762 | -0.012651 | 121.813 | 121.8979 | 121.5989 | 121.7838 | -0.25569
894.8281 | 122.0856 | -121.7102 | 0.11902 | 1.4211e-13 | -0.028754 | 0.014466 | -0.0036391 | -0.011692 | 0.019484 | -0.23296 | -0.0020702 | -0.00098076 | -0.0040571 | 0.031162 | 0.010322 | 0.069723 | 0.015142 | 0.014482 | 0.11622 | 0.041569 | 0.23354 | 0.1201 | 0.088043 | 0.036989 | 0.016908 | 0.075351 | 0.16022 | -0.12961 | -0.12294 | 121.8303 | -0.002794 | 121.7799 | 121.7247 | -0.10562 | -0.07745 | 0.11452 | 121.5873 | -0.043668 | 121.7982 | 121.7271 | 0.13985 | 0.041203 | -0.24863 | 121.8264 | 121.7518 | 121.9437 | 121.7253 | 0.001081 | 121.7856 | 121.8704 | 121.5806 | 121.7472 | -0.24196
896.5156 | 122.0535 | -121.756 | 0.10529 | 1.4211e-13 | -0.028968 | 0.01468 | -0.0038527 | -0.011478 | 0.01927 | -0.23296 | -0.0022838 | -0.00098076 | -0.0038435 | 0.031162 | 0.010963 | 0.083459 | 0.0243 | 0.009904 | 0.11622 | 0.046148 | 0.22896 | 0.11552 | 0.092622 | 0.041567 | 0.01233 | 0.075351 | 0.15564 | -0.13876 | -0.12294 | 121.8715 | 0.010939 | 121.8394 | 121.7659 | -0.10562 | -0.059138 | 0.12367 | 121.633 | -0.029935 | 121.8486 | 121.7683 | 0.13527 | 0.050357 | -0.24405 | 121.8722 | 121.8021 | 121.9849 | 121.7803 | 0.010235 | 121.8313 | 121.9116 | 121.6172 | 121.7975 | -0.22823
898.25 | 121.9803 | -121.7743 | 0.16937 | 1.4211e-13 | -0.028968 | 0.014252 | -0.0034253 | -0.011264 | 0.019911 | -0.23296 | -0.0024974 | -0.0011944 | -0.0042707 | 0.031376 | 0.010963 | 0.074302 | 0.019721 | 0.014482 | 0.11622 | 0.050727 | 0.25185 | 0.1201 | 0.074307 | 0.046146 | 0.01233 | 0.084508 | 0.16022 | -0.12961 | -0.12294 | 121.8944 | -0.053148 | 121.8486 | 121.7888 | -0.10562 | -0.11865 | 0.082479 | 121.6514 | -0.084865 | 121.8486 | 121.7866 | 0.13527 | -0.009151 | -0.29898 | 121.8905 | 121.825 | 122.0261 | 121.794 | -0.049273 | 121.8588 | 121.9345 | 121.6447 | 121.8204 | -0.29231
900 | 122.0032 | -121.7926 | 0.14648 | 1.4211e-13 | -0.028968 | 0.014893 | -0.0034253 | -0.011264 | 0.019484 | -0.2177 | -0.0020702 | -0.00098076 | -0.0038435 | 0.030948 | 0.010963 | 0.083459 | 0.0243 | 0.014482 | 0.11165 | 0.046148 | 0.23354 | 0.1201 | 0.083464 | 0.041567 | 0.01233 | 0.075351 | 0.15564 | -0.14334 | -0.12294 | 121.9127 | -0.034837 | 121.8761 | 121.8071 | -0.10562 | -0.10034 | 0.087054 | 121.6697 | -0.071133 | 121.8761 | 121.8049 | 0.13527 | 0.009159 | -0.28983 | 121.9043 | 121.8388 | 122.0261 | 121.8169 | -0.026384 | 121.868 | 121.9482 | 121.6493 | 121.8342 | -0.26942
901.6719 | 121.9254 | -121.7972 | 0.13275 | 1.4211e-13 | -0.028968 | 0.01468 | -0.0036391 | -0.011051 | 0.01927 | -0.24822 | -0.0024974 | -0.00098076 | -0.0038435 | 0.030735 | 0.010963 | 0.083459 | 0.019721 | 0.014482 | 0.11165 | 0.046148 | 0.24727 | 0.11552 | 0.083464 | 0.036989 | 0.01233 | 0.084508 | 0.15107 | -0.13419 | -0.12294 | 121.9127 | -0.021104 | 121.8806 | 121.8117 | -0.10104 | -0.086603 | 0.11452 | 121.6742 | -0.048243 | 121.8806 | 121.8095 | 0.13527 | 0.018314 | -0.26694 | 121.9088 | 121.8433 | 122.0445 | 121.8169 | -0.01723 | 121.8817 | 121.9482 | 121.663 | 121.8342 | -0.25569
903.4062 | 121.9849 | -121.7606 | 0.15106 | 1.4211e-13 | -0.029181 | 0.014466 | -0.0034253 | -0.011478 | 0.01927 | -0.23296 | -0.0022838 | -0.0011944 | -0.0036299 | 0.030948 | 0.010749 | 0.07888 | 0.019721 | 0.01906 | 0.1208 | 0.055306 | 0.24727 | 0.11552 | 0.078886 | 0.036989 | 0.016908 | 0.089087 | 0.15107 | -0.13419 | -0.12294 | 121.8761 | -0.030258 | 121.8394 | 121.7796 | -0.096461 | -0.095756 | 0.096212 | 121.6376 | -0.061975 | 121.8394 | 121.7775 | 0.13985 | 3e-06 | -0.28525 | 121.8814 | 121.8159 | 122.0078 | 121.7803 | -0.035541 | 121.8496 | 121.9116 | 121.6264 | 121.7975 | -0.274
905.1406 | 122.0352 | -121.7194 | 0.10071 | 1.4211e-13 | -0.028754 | 0.014893 | -0.0036391 | -0.011692 | 0.019484 | -0.23296 | -0.0020702 | -0.0011944 | -0.0040571 | 0.030948 | 0.010535 | 0.074302 | 0.015142 | 0.01906 | 0.11622 | 0.041569 | 0.23354 | 0.11552 | 0.078886 | 0.046146 | 0.007751 | 0.075351 | 0.15564 | -0.13419 | -0.12294 | 121.8349 | 0.015517 | 121.7937 | 121.7384 | -0.096461 | -0.059139 | 0.13283 | 121.5964 | -0.025357 | 121.7982 | 121.7271 | 0.13069 | 0.054935 | -0.23489 | 121.8356 | 121.7609 | 121.9529 | 121.7345 | 0.014813 | 121.7947 | 121.875 | 121.5852 | 121.7655 | -0.22365
906.8281 | 122.0718 | -121.756 | 0.11902 | 1.4211e-13 | -0.029181 | 0.01468 | -0.0034253 | -0.011478 | 0.019484 | -0.23296 | -0.0022838 | -0.00076696 | -0.0040571 | 0.031162 | 0.010963 | 0.083459 | 0.019721 | 0.009904 | 0.11622 | 0.055306 | 0.24269 | 0.11552 | 0.083464 | 0.046146 | 0.01233 | 0.07993 | 0.14649 | -0.13419 | -0.12294 | 121.8715 | -0.002794 | 121.8394 | 121.7659 | -0.10562 | -0.063713 | 0.12368 | 121.633 | -0.039089 | 121.8394 | 121.7683 | 0.13527 | 0.027467 | -0.25321 | 121.8722 | 121.8113 | 121.9987 | 121.7757 | -0.003498 | 121.8359 | 121.9025 | 121.6218 | 121.8021 | -0.24196
908.5625 | 122.049 | -121.7651 | 0.11444 | 1.4211e-13 | -0.028968 | 0.014466 | -0.0038527 | -0.011478 | 0.019057 | -0.22533 | -0.0020702 | -0.0011944 | -0.0044845 | 0.030948 | 0.010963 | 0.07888 | 0.0243 | 0.023639 | 0.097912 | 0.055306 | 0.23812 | 0.11552 | 0.074307 | 0.041567 | 0.01233 | 0.075351 | 0.14649 | -0.14792 | -0.12294 | 121.8807 | -0.016529 | 121.844 | 121.7888 | -0.091882 | -0.059135 | 0.12368 | 121.6422 | -0.03909 | 121.8394 | 121.7775 | 0.13527 | 0.032045 | -0.26236 | 121.863 | 121.8204 | 122.0033 | 121.7894 | 0.00108 | 121.8405 | 121.9116 | 121.6172 | 121.8067 | -0.23738
910.2969 | 122.0581 | -121.756 | 0.1236 | 1.4211e-13 | -0.028968 | 0.01468 | -0.0034253 | -0.011692 | 0.019057 | -0.22533 | -0.0022838 | -0.00098076 | -0.0042707 | 0.030948 | 0.010963 | 0.083459 | 0.019721 | 0.01906 | 0.10707 | 0.03699 | 0.24269 | 0.11552 | 0.092622 | 0.03241 | 0.016908 | 0.075351 | 0.15564 | -0.13876 | -0.11836 | 121.8715 | -0.016528 | 121.8394 | 121.775 | -0.096461 | -0.086606 | 0.1191 | 121.6376 | -0.048245 | 121.8486 | 121.7729 | 0.13527 | 0.032047 | -0.26236 | 121.863 | 121.793 | 121.9987 | 121.7757 | -0.008075 | 121.8313 | 121.9116 | 121.6172 | 121.7884 | -0.24196
911.9844 | 122.0032 | -121.7926 | 0.13733 | 1.4211e-13 | -0.029181 | 0.014466 | -0.0038527 | -0.011905 | 0.019484 | -0.23296 | -0.0022838 | -0.0011944 | -0.0038435 | 0.031376 | 0.010749 | 0.07888 | 0.015142 | 0.01906 | 0.11165 | 0.050727 | 0.24269 | 0.11552 | 0.088043 | 0.03241 | 0.01233 | 0.07993 | 0.15564 | -0.13419 | -0.12752 | 121.9081 | -0.025682 | 121.8715 | 121.8117 | -0.096461 | -0.086602 | 0.10537 | 121.6651 | -0.057399 | 121.8806 | 121.8049 | 0.13985 | 0.018314 | -0.27152 | 121.9043 | 121.8433 | 122.0353 | 121.8077 | -0.021808 | 121.8725 | 121.9482 | 121.6584 | 121.825 | -0.26485
913.7188 | 122.0947 | -121.7285 | 0.11902 | 1.4211e-13 | -0.028968 | 0.01468 | -0.0036391 | -0.011905 | 0.01927 | -0.24059 | -0.0022838 | -0.00098076 | -0.0042707 | 0.031162 | 0.010749 | 0.083459 | 0.019721 | 0.014482 | 0.11622 | 0.050727 | 0.24269 | 0.11552 | 0.083464 | 0.03241 | 0.01233 | 0.075351 | 0.15107 | -0.13876 | -0.12752 | 121.844 | -0.002794 | 121.812 | 121.743 | -0.10104 | -0.068292 | 0.12368 | 121.601 | -0.043668 | 121.812 | 121.7408 | 0.13985 | 0.032046 | -0.25778 | 121.8447 | 121.7792 | 121.9712 | 121.7482 | -0.003498 | 121.8039 | 121.8796 | 121.5898 | 121.7609 | -0.24654
915.3906 | 121.9666 | -121.7743 | 0.13733 | 1.4211e-13 | -0.029181 | 0.014466 | -0.0034253 | -0.011905 | 0.019484 | -0.23296 | -0.001643 | -0.00098076 | -0.0038435 | 0.030735 | 0.010749 | 0.07888 | 0.019721 | 0.01906 | 0.1208 | 0.046148 | 0.23354 | 0.1201 | 0.078886 | 0.041567 | 0.016908 | 0.075351 | 0.15564 | -0.13419 | -0.12294 | 121.8944 | -0.016525 | 121.8532 | 121.7934 | -0.10104 | -0.091181 | 0.096209 | 121.6514 | -0.061978 | 121.8532 | 121.7912 | 0.13985 | 0.018314 | -0.27152 | 121.8951 | 121.8204 | 122.0078 | 121.794 | -0.017229 | 121.8496 | 121.9299 | 121.6401 | 121.8159 | -0.26027
917.1406 | 121.9437 | -121.7926 | 0.15106 | 1.4211e-13 | -0.029181 | 0.014252 | -0.0034253 | -0.011692 | 0.019698 | -0.24822 | -0.0020702 | -0.001408 | -0.0040571 | 0.031376 | 0.010963 | 0.083459 | 0.0243 | 0.014482 | 0.11165 | 0.050727 | 0.23812 | 0.11094 | 0.074307 | 0.036989 | 0.016908 | 0.07993 | 0.15564 | -0.13876 | -0.12294 | 121.9035 | -0.039415 | 121.8761 | 121.8071 | -0.09646 | -0.10034 | 0.087055 | 121.6697 | -0.071132 | 121.8669 | 121.8095 | 0.13985 | 0.004581 | -0.28983 | 121.9043 | 121.8433 | 122.0307 | 121.8169 | -0.04012 | 121.8725 | 121.9482 | 121.6538 | 121.8296 | -0.274
918.875 | 122.0535 | -121.7422 | 0.12817 | 1.4211e-13 | -0.028968 | 0.014252 | -0.0036391 | -0.011905 | 0.01927 | -0.23296 | -0.0024974 | -0.00098076 | -0.0038435 | 0.031162 | 0.010535 | 0.074302 | 0.019721 | 0.01906 | 0.11165 | 0.050727 | 0.24269 | 0.12468 | 0.074307 | 0.036989 | 0.016908 | 0.089087 | 0.15564 | -0.13419 | -0.12752 | 121.8669 | -0.016527 | 121.8166 | 121.7613 | -0.10562 | -0.077447 | 0.11452 | 121.6147 | -0.039087 | 121.8166 | 121.7592 | 0.14443 | 0.027469 | -0.26236 | 121.8539 | 121.793 | 121.9849 | 121.762 | -0.003495 | 121.8313 | 121.8979 | 121.6081 | 121.7792 | -0.25569
920.625 | 122.0718 | -121.7514 | 0.11444 | 1.4211e-13 | -0.028968 | 0.01468 | -0.0034253 | -0.011692 | 0.01927 | -0.2177 | -0.0018566 | -0.00098076 | -0.0038435 | 0.031803 | 0.010963 | 0.074302 | 0.0243 | 0.009904 | 0.1208 | 0.050727 | 0.24269 | 0.11552 | 0.083464 | 0.041567 | 0.01233 | 0.075351 | 0.16022 | -0.13419 | -0.12294 | 121.8669 | 0.006363 | 121.8257 | 121.7613 | -0.10562 | -0.063714 | 0.12825 | 121.6285 | -0.03909 | 121.8349 | 121.7637 | 0.13527 | 0.045781 | -0.24863 | 121.8722 | 121.8021 | 121.9941 | 121.7757 | 0.00108 | 121.8268 | 121.9116 | 121.6172 | 121.793 | -0.23738
922.3125 | 122.0947 | -121.7514 | 0.09613 | 1.4211e-13 | -0.029181 | 0.014466 | -0.0038527 | -0.011478 | 0.01927 | -0.23296 | -0.0018566 | -0.00076696 | -0.0040571 | 0.031162 | 0.010749 | 0.074302 | 0.028878 | 0.014482 | 0.11622 | 0.055306 | 0.23812 | 0.1201 | 0.083464 | 0.03241 | 0.01233 | 0.084508 | 0.15107 | -0.13419 | -0.12294 | 121.8715 | 0.020095 | 121.8257 | 121.7659 | -0.10562 | -0.040824 | 0.14199 | 121.6285 | -0.011622 | 121.8349 | 121.7637 | 0.13527 | 0.054935 | -0.23032 | 121.8676 | 121.8067 | 121.9895 | 121.7803 | 0.02397 | 121.8359 | 121.9025 | 121.6172 | 121.7838 | -0.21907
923.9844 | 122.0261 | -121.7468 | 0.13275 | 1.4211e-13 | -0.028968 | 0.01468 | -0.0036391 | -0.011478 | 0.019484 | -0.24059 | -0.0022838 | -0.0011944 | -0.0040571 | 0.030948 | 0.010749 | 0.083459 | 0.019721 | 0.014482 | 0.11165 | 0.050727 | 0.23812 | 0.11552 | 0.083464 | 0.036989 | 0.007751 | 0.07993 | 0.1648 | -0.12961 | -0.12294 | 121.8623 | -0.021104 | 121.8303 | 121.7613 | -0.10104 | -0.082024 | 0.10537 | 121.6239 | -0.052821 | 121.8303 | 121.7546 | 0.13069 | 0.032049 | -0.26236 | 121.8585 | 121.7976 | 121.9849 | 121.7665 | -0.01723 | 121.8268 | 121.9116 | 121.6172 | 121.7838 | -0.25569
925.7344 | 122.0993 | -121.7606 | 0.12817 | 1.4211e-13 | -0.029181 | 0.01468 | -0.0036391 | -0.011478 | 0.019484 | -0.22533 | -0.0020702 | -0.0011944 | -0.0040571 | 0.031162 | 0.010749 | 0.07888 | 0.0243 | 0.023639 | 0.11165 | 0.050727 | 0.24727 | 0.11094 | 0.074307 | 0.046146 | 0.021487 | 0.07993 | 0.14649 | -0.13876 | -0.12294 | 121.8715 | -0.016527 | 121.8394 | 121.7842 | -0.087303 | -0.077447 | 0.1191 | 121.6376 | -0.048244 | 121.8349 | 121.782 | 0.14443 | 0.018312 | -0.26694 | 121.8722 | 121.8113 | 122.0078 | 121.7849 | -0.017232 | 121.8405 | 121.907 | 121.6218 | 121.8067 | -0.25111
927.4688 | 122.0398 | -121.7514 | 0.11444 | 1.4211e-13 | -0.029181 | 0.01468 | -0.0036391 | -0.012119 | 0.01927 | -0.22533 | -0.0018566 | -0.0011944 | -0.0038435 | 0.031376 | 0.011176 | 0.07888 | 0.015142 | 0.023639 | 0.11622 | 0.050727 | 0.24727 | 0.11552 | 0.088043 | 0.041567 | 0.016908 | 0.07993 | 0.15564 | -0.13419 | -0.12752 | 121.8669 | 0.001784 | 121.8303 | 121.775 | -0.091882 | -0.063714 | 0.13283 | 121.6239 | -0.034511 | 121.8394 | 121.7683 | 0.14443 | 0.041202 | -0.24863 | 121.8676 | 121.8021 | 121.9987 | 121.7665 | 0.00108 | 121.8313 | 121.907 | 121.6172 | 121.793 | -0.24196
929.2031 | 121.962 | -121.7697 | 0.15564 | 1.4211e-13 | -0.028968 | 0.014893 | -0.0038527 | -0.011692 | 0.019698 | -0.24059 | -0.0020702 | -0.00098076 | -0.0042707 | 0.031589 | 0.010749 | 0.07888 | 0.015142 | 0.023639 | 0.11622 | 0.046148 | 0.24269 | 0.11552 | 0.078886 | 0.036989 | 0.01233 | 0.07993 | 0.16022 | -0.13419 | -0.1321 | 121.8852 | -0.039415 | 121.8486 | 121.7934 | -0.091882 | -0.10949 | 0.087055 | 121.6376 | -0.07571 | 121.8486 | 121.782 | 0.14443 | 0.004582 | -0.28983 | 121.8859 | 121.8159 | 122.0124 | 121.7849 | -0.040119 | 121.8496 | 121.9299 | 121.6355 | 121.8067 | -0.28774
930.9531 | 122.0352 | -121.756 | 0.11444 | 1.4211e-13 | -0.029181 | 0.014893 | -0.0036391 | -0.011478 | 0.019484 | -0.24059 | -0.0022838 | -0.0011944 | -0.0040571 | 0.031376 | 0.010749 | 0.07888 | 0.019721 | 0.01906 | 0.11622 | 0.050727 | 0.24727 | 0.1201 | 0.078886 | 0.036989 | 0.01233 | 0.07993 | 0.15564 | -0.13419 | -0.12294 | 121.8761 | 0.001784 | 121.8349 | 121.775 | -0.10104 | -0.063714 | 0.13283 | 121.633 | -0.034511 | 121.8349 | 121.7683 | 0.13527 | 0.041202 | -0.24863 | 121.8722 | 121.8067 | 122.0033 | 121.7757 | 0.005659 | 121.8359 | 121.9116 | 121.6218 | 121.793 | -0.23738
932.7031 | 121.9986 | -121.7834 | 0.13275 | 1.4211e-13 | -0.029181 | 0.014252 | -0.0038527 | -0.011478 | 0.01927 | -0.23296 | -0.0020702 | -0.0011944 | -0.0038435 | 0.031376 | 0.010963 | 0.074302 | 0.019721 | 0.014482 | 0.10707 | 0.050727 | 0.24269 | 0.11552 | 0.083464 | 0.041567 | 0.016908 | 0.07993 | 0.16022 | -0.12503 | -0.12752 | 121.899 | -0.025683 | 121.8577 | 121.7979 | -0.10104 | -0.082024 | 0.10994 | 121.6559 | -0.052821 | 121.8669 | 121.8004 | 0.14443 | 0.027471 | -0.25778 | 121.8905 | 121.8342 | 122.0261 | 121.8032 | -0.01723 | 121.8634 | 121.9437 | 121.6584 | 121.825 | -0.26027
934.4531 | 122.0627 | -121.7514 | 0.13275 | 1.4211e-13 | -0.029181 | 0.01468 | -0.0036391 | -0.011478 | 0.019698 | -0.22533 | -0.0024974 | -0.00098076 | -0.0038435 | 0.031162 | 0.010749 | 0.07888 | 0.019721 | 0.01906 | 0.11622 | 0.055306 | 0.24727 | 0.1201 | 0.083464 | 0.036989 | 0.021487 | 0.07993 | 0.16022 | -0.14334 | -0.12294 | 121.8715 | -0.016526 | 121.8303 | 121.7705 | -0.10104 | -0.077445 | 0.11452 | 121.6285 | -0.052821 | 121.8349 | 121.7729 | 0.14443 | 0.027471 | -0.27609 | 121.8676 | 121.8067 | 121.9987 | 121.7711 | -0.012651 | 121.8313 | 121.9116 | 121.6081 | 121.7884 | -0.25569
936.125 | 121.962 | -121.7834 | 0.16479 | 1.4211e-13 | -0.029395 | 0.014252 | -0.0036391 | -0.011905 | 0.019057 | -0.24059 | -0.0020702 | -0.0011944 | -0.0036299 | 0.031162 | 0.010963 | 0.074302 | 0.0243 | 0.023639 | 0.11165 | 0.050727 | 0.24269 | 0.12468 | 0.083464 | 0.041567 | 0.01233 | 0.084508 | 0.15564 | -0.13419 | -0.12752 | 121.9081 | -0.053148 | 121.8577 | 121.8071 | -0.10104 | -0.11407 | 0.0779 | 121.6559 | -0.080287 | 121.8669 | 121.7958 | 0.13985 | -0.009152 | -0.29898 | 121.8951 | 121.8342 | 122.0261 | 121.8077 | -0.040116 | 121.868 | 121.9391 | 121.6493 | 121.825 | -0.29231
937.875 | 121.9528 | -121.7972 | 0.14648 | 1.4211e-13 | -0.028968 | 0.014252 | -0.0036391 | -0.011905 | 0.019484 | -0.22533 | -0.0020702 | -0.00076696 | -0.0038435 | 0.030948 | 0.010749 | 0.069723 | 0.0243 | 0.01906 | 0.11622 | 0.055306 | 0.24269 | 0.11552 | 0.078886 | 0.041567 | 0.016908 | 0.07993 | 0.1648 | -0.13419 | -0.12752 | 121.9127 | -0.030259 | 121.8669 | 121.8162 | -0.096461 | -0.091178 | 0.096211 | 121.6697 | -0.066554 | 121.8761 | 121.8141 | 0.14443 | 0.018316 | -0.28067 | 121.9134 | 121.8525 | 122.0399 | 121.8215 | -0.030963 | 121.8771 | 121.962 | 121.663 | 121.8387 | -0.274
939.5469 | 121.9711 | -121.8063 | 0.15106 | 1.4211e-13 | -0.029181 | 0.014466 | -0.0034253 | -0.011478 | 0.019484 | -0.24059 | -0.0018566 | -0.001408 | -0.0040571 | 0.031589 | 0.010963 | 0.07888 | 0.019721 | 0.023639 | 0.11622 | 0.059885 | 0.24269 | 0.11094 | 0.083464 | 0.036989 | 0.01233 | 0.075351 | 0.15564 | -0.13876 | -0.12294 | 121.9173 | -0.034837 | 121.8852 | 121.83 | -0.087303 | -0.091177 | 0.091633 | 121.6834 | -0.075711 | 121.8898 | 121.8187 | 0.13527 | 0.004581 | -0.28983 | 121.9226 | 121.8662 | 122.049 | 121.8261 | -0.04012 | 121.8817 | 121.962 | 121.6676 | 121.8433 | -0.274
941.2969 | 122.0901 | -121.7468 | 0.12817 | 1.4211e-13 | -0.028968 | 0.014466 | -0.0038527 | -0.012119 | 0.019484 | -0.24822 | -0.0020702 | -0.00098076 | -0.0042707 | 0.031162 | 0.010749 | 0.07888 | 0.028878 | 0.023639 | 0.10707 | 0.050727 | 0.24269 | 0.12468 | 0.078886 | 0.03241 | 0.007751 | 0.07993 | 0.15564 | -0.13876 | -0.12294 | 121.8715 | -0.021106 | 121.8257 | 121.7705 | -0.10104 | -0.077447 | 0.11452 | 121.6239 | -0.048244 | 121.8257 | 121.7546 | 0.13069 | 0.027469 | -0.26694 | 121.8539 | 121.7976 | 121.9895 | 121.7757 | -0.003495 | 121.8268 | 121.9025 | 121.6081 | 121.7792 | -0.25111
943.0469 | 122.0306 | -121.7697 | 0.1236 | 1.4211e-13 | -0.029395 | 0.01468 | -0.0040665 | -0.011478 | 0.019484 | -0.24059 | -0.0020702 | -0.00076696 | -0.0042707 | 0.031589 | 0.010535 | 0.074302 | 0.0243 | 0.023639 | 0.11622 | 0.055306 | 0.24269 | 0.1201 | 0.083464 | 0.046146 | 0.01233 | 0.07993 | 0.15564 | -0.097557 | -0.12752 | 121.8898 | -0.007371 | 121.844 | 121.7934 | -0.096461 | -0.06829 | 0.1191 | 121.6422 | -0.043666 | 121.8532 | 121.782 | 0.13985 | 0.032047 | -0.22115 | 121.8859 | 121.825 | 122.0124 | 121.794 | -0.003496 | 121.8496 | 121.9254 | 121.6722 | 121.8159 | -0.25111
944.7344 | 122.0627 | -121.7239 | 0.11444 | 1.4211e-13 | -0.029181 | 0.014252 | -0.0034253 | -0.011478 | 0.01927 | -0.24059 | -0.0020702 | -0.00076696 | -0.0040571 | 0.031376 | 0.010963 | 0.07888 | 0.019721 | 0.028217 | 0.11165 | 0.055306 | 0.24727 | 0.11094 | 0.078886 | 0.036989 | 0.026066 | 0.084508 | 0.15564 | -0.13419 | -0.12294 | 121.8349 | -0.002794 | 121.8028 | 121.7522 | -0.082725 | -0.059135 | 0.13283 | 121.601 | -0.029933 | 121.8028 | 121.75 | 0.149 | 0.041202 | -0.24863 | 121.8356 | 121.7792 | 121.9712 | 121.7437 | -0.003499 | 121.8084 | 121.8796 | 121.5898 | 121.7609 | -0.23738
946.4844 | 122.0627 | -121.7468 | 0.11902 | 1.4211e-13 | -0.029181 | 0.01468 | -0.0036391 | -0.011692 | 0.019698 | -0.24059 | -0.0020702 | -0.0011944 | -0.0042707 | 0.031589 | 0.010963 | 0.07888 | 0.019721 | 0.023639 | 0.11165 | 0.055306 | 0.24269 | 0.11552 | 0.074307 | 0.041567 | 0.016908 | 0.075351 | 0.15564 | -0.092979 | -0.12752 | 121.8623 | -0.007372 | 121.8257 | 121.7705 | -0.091882 | -0.063713 | 0.12368 | 121.6193 | -0.043668 | 121.8211 | 121.7637 | 0.14443 | 0.036624 | -0.212 | 121.8585 | 121.8021 | 121.9895 | 121.7665 | -0.003498 | 121.8222 | 121.9025 | 121.6538 | 121.7884 | -0.24654
948.2344 | 121.9757 | -121.7972 | 0.13733 | 1.4211e-13 | -0.029181 | 0.014252 | -0.0038527 | -0.011905 | 0.019698 | -0.23296 | -0.0020702 | -0.0011944 | -0.0038435 | 0.031376 | 0.010963 | 0.074302 | 0.0243 | 0.023639 | 0.11622 | 0.059885 | 0.24727 | 0.11094 | 0.083464 | 0.036989 | 0.007751 | 0.07993 | 0.15107 | -0.13419 | -0.1321 | 121.9081 | -0.021104 | 121.8715 | 121.8208 | -0.087303 | -0.077444 | 0.10994 | 121.6651 | -0.057399 | 121.8806 | 121.8049 | 0.13985 | 0.013736 | -0.27152 | 121.9134 | 121.8571 | 122.0445 | 121.8215 | -0.026387 | 121.8771 | 121.9482 | 121.663 | 121.8342 | -0.26943
949.9688 | 122.0581 | -121.7422 | 0.10529 | 1.4211e-13 | -0.028754 | 0.014466 | -0.0034253 | -0.011905 | 0.01927 | -0.23296 | -0.0022838 | -0.0011944 | -0.0040571 | 0.031589 | 0.010963 | 0.07888 | 0.0243 | 0.01906 | 0.11165 | 0.055306 | 0.23812 | 0.1201 | 0.083464 | 0.046146 | 0.01233 | 0.07993 | 0.15107 | -0.13876 | -0.11836 | 121.8623 | 0.006361 | 121.8211 | 121.7613 | -0.10104 | -0.04998 | 0.13283 | 121.6239 | -0.025356 | 121.8257 | 121.7546 | 0.13069 | 0.045779 | -0.24405 | 121.8539 | 121.7976 | 121.9804 | 121.7665 | 0.014814 | 121.8222 | 121.8933 | 121.6035 | 121.7884 | -0.22365
951.6406 | 121.9849 | -121.7834 | 0.14191 | 1.4211e-13 | -0.028754 | 0.014252 | -0.0038527 | -0.011692 | 0.019484 | -0.24059 | -0.0020702 | -0.00076696 | -0.0040571 | 0.031589 | 0.010963 | 0.074302 | 0.015142 | 0.01906 | 0.1208 | 0.050727 | 0.24269 | 0.11094 | 0.078886 | 0.046146 | 0.01233 | 0.075351 | 0.15564 | -0.12961 | -0.12294 | 121.8944 | -0.021103 | 121.8577 | 121.8025 | -0.091882 | -0.09118 | 0.10079 | 121.6605 | -0.066556 | 121.8623 | 121.7958 | 0.13527 | 0.013736 | -0.27151 | 121.9043 | 121.8342 | 122.0261 | 121.7986 | -0.030965 | 121.8588 | 121.9391 | 121.6538 | 121.8296 | -0.26485
953.4062 | 122.0306 | -121.7789 | 0.12817 | 1.4211e-13 | -0.029181 | 0.01468 | -0.0036391 | -0.011905 | 0.019698 | -0.23296 | -0.0024974 | -0.00098076 | -0.0040571 | 0.031589 | 0.010749 | 0.074302 | 0.019721 | 0.028217 | 0.11622 | 0.046148 | 0.24727 | 0.11552 | 0.078886 | 0.050725 | 0.016908 | 0.07993 | 0.16022 | -0.13876 | -0.12752 | 121.8944 | -0.011949 | 121.8532 | 121.8071 | -0.087304 | -0.082026 | 0.1191 | 121.6514 | -0.048244 | 121.8578 | 121.7958 | 0.14443 | 0.032048 | -0.26694 | 121.8951 | 121.825 | 122.0261 | 121.7986 | -0.012653 | 121.8588 | 121.9391 | 121.6401 | 121.8296 | -0.25569
955.0781 | 122.0215 | -121.7377 | 0.1236 | 1.4211e-13 | -0.028968 | 0.01468 | -0.0038527 | -0.011692 | 0.019698 | -0.22533 | -0.0018566 | -0.00098076 | -0.0038435 | 0.031589 | 0.010749 | 0.083459 | 0.0243 | 0.023639 | 0.1208 | 0.046148 | 0.24727 | 0.11552 | 0.078886 | 0.050725 | 0.021487 | 0.07993 | 0.15564 | -0.13876 | -0.12752 | 121.8532 | -0.002792 | 121.8211 | 121.7613 | -0.091882 | -0.077448 | 0.12368 | 121.6102 | -0.043666 | 121.8166 | 121.7592 | 0.149 | 0.032047 | -0.26236 | 121.8585 | 121.7838 | 121.9849 | 121.762 | -0.008075 | 121.8176 | 121.8933 | 121.5989 | 121.7884 | -0.25111
956.8281 | 121.9803 | -121.8155 | 0.14191 | 1.4211e-13 | -0.029181 | 0.014466 | -0.0034253 | -0.011692 | 0.01927 | -0.24059 | -0.0020702 | -0.00098076 | -0.0038435 | 0.031803 | 0.010535 | 0.07888 | 0.0243 | 0.023639 | 0.11622 | 0.046148 | 0.25185 | 0.1201 | 0.074307 | 0.036989 | 0.016908 | 0.089087 | 0.16022 | -0.14334 | -0.11836 | 121.9356 | -0.025682 | 121.8944 | 121.8391 | -0.096461 | -0.095759 | 0.10995 | 121.6971 | -0.05282 | 121.8898 | 121.8324 | 0.13527 | 0.018315 | -0.28525 | 121.9317 | 121.8616 | 122.0673 | 121.8398 | -0.021807 | 121.9046 | 121.9757 | 121.6721 | 121.8525 | -0.26027
958.5938 | 122.0032 | -121.7697 | 0.13275 | 1.4211e-13 | -0.028968 | 0.014466 | -0.0038527 | -0.011692 | 0.019484 | -0.23296 | -0.0022838 | -0.00098076 | -0.0038435 | 0.031589 | 0.010963 | 0.07888 | 0.0243 | 0.028217 | 0.11165 | 0.055306 | 0.23812 | 0.1201 | 0.074307 | 0.046146 | 0.01233 | 0.07993 | 0.15107 | -0.13419 | -0.12294 | 121.8898 | -0.021104 | 121.8486 | 121.7979 | -0.091883 | -0.077445 | 0.10537 | 121.6468 | -0.052821 | 121.844 | 121.782 | 0.13527 | 0.018314 | -0.26694 | 121.8814 | 121.825 | 122.0078 | 121.794 | -0.012651 | 121.8496 | 121.9208 | 121.6355 | 121.8159 | -0.25569
960.2656 | 121.9528 | -121.8063 | 0.14648 | 1.4211e-13 | -0.029181 | 0.01468 | -0.0036391 | -0.011905 | 0.019484 | -0.2177 | -0.0022838 | -0.00076696 | -0.0038435 | 0.031376 | 0.010749 | 0.083459 | 0.019721 | 0.028217 | 0.11622 | 0.050727 | 0.24727 | 0.1201 | 0.092622 | 0.046146 | 0.01233 | 0.07993 | 0.15564 | -0.12961 | -0.12752 | 121.9264 | -0.030259 | 121.8898 | 121.8346 | -0.091883 | -0.095757 | 0.10079 | 121.6788 | -0.066554 | 121.899 | 121.8187 | 0.13985 | 0.009159 | -0.27609 | 121.9226 | 121.8571 | 122.0536 | 121.8261 | -0.026384 | 121.8863 | 121.962 | 121.6767 | 121.8525 | -0.274
962 | 122.0261 | -121.788 | 0.12817 | 1.4211e-13 | -0.028968 | 0.01468 | -0.0032117 | -0.011905 | 0.019484 | -0.22533 | -0.0022838 | -0.001408 | -0.0040571 | 0.031589 | 0.010749 | 0.074302 | 0.015142 | 0.028217 | 0.10707 | 0.064464 | 0.23812 | 0.1201 | 0.074307 | 0.050725 | 0.01233 | 0.07993 | 0.15107 | -0.12503 | -0.11836 | 121.9081 | -0.021106 | 121.8623 | 121.8162 | -0.091883 | -0.06371 | 0.10994 | 121.6697 | -0.048244 | 121.8623 | 121.8004 | 0.13069 | 0.022891 | -0.2532 | 121.8951 | 121.8525 | 122.0261 | 121.8032 | -0.008074 | 121.868 | 121.9391 | 121.663 | 121.8388 | -0.24654
963.7031 | 121.9574 | -121.8109 | 0.16937 | 1.4211e-13 | -0.029181 | 0.01468 | -0.0038527 | -0.011905 | 0.01927 | -0.22533 | -0.0020702 | -0.00076696 | -0.0040571 | 0.031589 | 0.010749 | 0.07888 | 0.019721 | 0.023639 | 0.1208 | 0.055306 | 0.24269 | 0.1201 | 0.074307 | 0.046146 | 0.016908 | 0.07993 | 0.15107 | -0.13876 | -0.12294 | 121.931 | -0.048569 | 121.8898 | 121.8346 | -0.096461 | -0.11407 | 0.073322 | 121.688 | -0.089443 | 121.8852 | 121.8278 | 0.13985 | -0.018308 | -0.30814 | 121.9317 | 121.8662 | 122.0536 | 121.8306 | -0.049273 | 121.8908 | 121.962 | 121.6721 | 121.8571 | -0.29231
965.4375 | 122.0444 | -121.7743 | 0.1236 | 1.4211e-13 | -0.028968 | 0.01468 | -0.0036391 | -0.011905 | 0.019698 | -0.24059 | -0.0020702 | -0.0011944 | -0.0038435 | 0.032017 | 0.010535 | 0.083459 | 0.0243 | 0.028217 | 0.11165 | 0.046148 | 0.24269 | 0.1201 | 0.083464 | 0.041567 | 0.016908 | 0.07993 | 0.16022 | -0.13876 | -0.12294 | 121.8944 | -0.011949 | 121.8578 | 121.8025 | -0.091883 | -0.077448 | 0.1191 | 121.6514 | -0.043666 | 121.8578 | 121.7912 | 0.13985 | 0.036626 | -0.26236 | 121.8859 | 121.8204 | 122.017 | 121.7986 | -0.003496 | 121.8542 | 121.9345 | 121.6355 | 121.8159 | -0.24654
967.1094 | 121.9849 | -121.8063 | 0.15106 | 1.4211e-13 | -0.028968 | 0.014466 | -0.0036391 | -0.012119 | 0.019698 | -0.23296 | -0.0022838 | -0.0011944 | -0.0038435 | 0.031376 | 0.010535 | 0.088037 | 0.0243 | 0.028217 | 0.11622 | 0.055306 | 0.24727 | 0.11094 | 0.083464 | 0.041567 | 0.01233 | 0.07993 | 0.15564 | -0.13876 | -0.12294 | 121.9173 | -0.034837 | 121.8944 | 121.8346 | -0.082725 | -0.095756 | 0.096212 | 121.6834 | -0.071132 | 121.8898 | 121.8187 | 0.13527 | 0.004581 | -0.28983 | 121.9226 | 121.8616 | 122.0536 | 121.8306 | -0.04012 | 121.8863 | 121.962 | 121.6676 | 121.8479 | -0.274
968.8438 | 121.9345 | -121.7743 | 0.13733 | 1.4211e-13 | -0.028754 | 0.014466 | -0.0034253 | -0.011692 | 0.01927 | -0.23296 | -0.001643 | -0.0011944 | -0.0038435 | 0.031589 | 0.010535 | 0.074302 | 0.019721 | 0.032795 | 0.11165 | 0.050727 | 0.24727 | 0.1201 | 0.078886 | 0.046146 | 0.007751 | 0.07993 | 0.15564 | -0.13419 | -0.12752 | 121.8944 | -0.025682 | 121.8486 | 121.8071 | -0.087305 | -0.086602 | 0.10994 | 121.6468 | -0.057399 | 121.8532 | 121.782 | 0.13527 | 0.018314 | -0.27152 | 121.8859 | 121.825 | 122.0216 | 121.794 | -0.017229 | 121.8542 | 121.9299 | 121.6401 | 121.8204 | -0.26485
970.5781 | 122.0444 | -121.7651 | 0.1236 | 1.4211e-13 | -0.028968 | 0.014466 | -0.0036391 | -0.011905 | 0.019484 | -0.24059 | -0.0022838 | -0.00098076 | -0.0040571 | 0.031376 | 0.010535 | 0.083459 | 0.0243 | 0.028217 | 0.11622 | 0.032411 | 0.24727 | 0.11552 | 0.083464 | 0.055303 | 0.016908 | 0.070773 | 0.16022 | -0.13876 | -0.12752 | 121.8807 | -0.007371 | 121.8486 | 121.7934 | -0.087304 | -0.091185 | 0.12368 | 121.6376 | -0.052823 | 121.8486 | 121.782 | 0.14443 | 0.036626 | -0.26236 | 121.8814 | 121.7975 | 122.0124 | 121.7894 | -0.008075 | 121.8359 | 121.9254 | 121.6264 | 121.8204 | -0.25111
972.3125 | 121.9894 | -121.7789 | 0.12817 | 1.4211e-13 | -0.029181 | 0.014466 | -0.0032117 | -0.011692 | 0.019484 | -0.24822 | -0.0022838 | -0.00098076 | -0.0038435 | 0.032017 | 0.010963 | 0.083459 | 0.033457 | 0.028217 | 0.10707 | 0.050727 | 0.24727 | 0.12468 | 0.078886 | 0.046146 | 0.01233 | 0.084508 | 0.15564 | -0.14334 | -0.12294 | 121.9035 | -0.021106 | 121.8623 | 121.8071 | -0.096462 | -0.077447 | 0.1191 | 121.6559 | -0.043666 | 121.8578 | 121.7912 | 0.13527 | 0.027469 | -0.27152 | 121.8859 | 121.8296 | 122.0261 | 121.8123 | -0.003495 | 121.8634 | 121.9345 | 121.6355 | 121.825 | -0.25111
973.9844 | 121.9894 | -121.7834 | 0.16937 | 1.4211e-13 | -0.028968 | 0.014466 | -0.0036391 | -0.011905 | 0.01927 | -0.24059 | -0.0018566 | -0.0011944 | -0.0038435 | 0.031803 | 0.010749 | 0.088037 | 0.028878 | 0.028217 | 0.11165 | 0.050727 | 0.24269 | 0.1201 | 0.083464 | 0.046146 | 0.016908 | 0.07993 | 0.15107 | -0.13419 | -0.1321 | 121.9035 | -0.057726 | 121.8715 | 121.8117 | -0.091883 | -0.11865 | 0.073322 | 121.6513 | -0.089443 | 121.8669 | 121.8004 | 0.149 | -0.018308 | -0.30356 | 121.8951 | 121.8342 | 122.0261 | 121.8123 | -0.049273 | 121.8634 | 121.9345 | 121.6493 | 121.8296 | -0.30147
975.7188 | 122.0581 | -121.7789 | 0.1236 | 1.4211e-13 | -0.028968 | 0.014466 | -0.0036391 | -0.011905 | 0.019484 | -0.22533 | -0.0022838 | -0.0011944 | -0.0038435 | 0.031589 | 0.010535 | 0.074302 | 0.0243 | 0.01906 | 0.11165 | 0.055306 | 0.24269 | 0.11094 | 0.083464 | 0.046146 | 0.007751 | 0.075351 | 0.15564 | -0.13419 | -0.12752 | 121.8898 | -0.011949 | 121.8532 | 121.7979 | -0.091882 | -0.06829 | 0.1191 | 121.6514 | -0.048245 | 121.8623 | 121.7866 | 0.13527 | 0.032047 | -0.25778 | 121.8905 | 121.8342 | 122.0216 | 121.8032 | -0.012654 | 121.8542 | 121.9345 | 121.6447 | 121.825 | -0.25111
977.4688 | 122.0993 | -121.7697 | 0.10986 | 1.4211e-13 | -0.029181 | 0.014466 | -0.0036391 | -0.011905 | 0.01927 | -0.22533 | -0.0020702 | -0.00098076 | -0.0042707 | 0.031803 | 0.010535 | 0.07888 | 0.019721 | 0.028217 | 0.11165 | 0.041569 | 0.24727 | 0.11552 | 0.078886 | 0.046146 | 0.01233 | 0.075351 | 0.15107 | -0.13876 | -0.12752 | 121.8852 | 0.001784 | 121.8486 | 121.7979 | -0.087304 | -0.068294 | 0.13741 | 121.6422 | -0.034512 | 121.8486 | 121.782 | 0.13985 | 0.041202 | -0.24863 | 121.8814 | 121.8113 | 122.017 | 121.7894 | 0.005658 | 121.8451 | 121.9208 | 121.6309 | 121.8159 | -0.23738
979.1406 | 121.9986 | -121.8063 | 0.1236 | 1.4211e-13 | -0.029395 | 0.014466 | -0.0036391 | -0.011905 | 0.019057 | -0.23296 | -0.0020702 | -0.00098076 | -0.0038435 | 0.031589 | 0.010322 | 0.074302 | 0.0243 | 0.023639 | 0.11622 | 0.055306 | 0.24727 | 0.1201 | 0.078886 | 0.050725 | 0.021487 | 0.075351 | 0.15107 | -0.13419 | -0.12752 | 121.9264 | -0.007371 | 121.8806 | 121.83 | -0.096461 | -0.06829 | 0.12368 | 121.6788 | -0.048245 | 121.8852 | 121.8278 | 0.149 | 0.027469 | -0.25778 | 121.9226 | 121.8616 | 122.0536 | 121.8306 | -0.003496 | 121.8817 | 121.9574 | 121.6721 | 121.8571 | -0.25111
980.8906 | 122.0078 | -121.788 | 0.13733 | 1.4211e-13 | -0.029181 | 0.014466 | -0.0036391 | -0.011905 | 0.019484 | -0.23296 | -0.0022838 | -0.00098076 | -0.0038435 | 0.031589 | 0.010322 | 0.07888 | 0.0243 | 0.032795 | 0.11165 | 0.046148 | 0.24269 | 0.1201 | 0.078886 | 0.041567 | 0.021487 | 0.075351 | 0.15564 | -0.13876 | -0.12294 | 121.9081 | -0.025682 | 121.8669 | 121.8208 | -0.087305 | -0.091181 | 0.10537 | 121.6651 | -0.061978 | 121.8669 | 121.8095 | 0.14443 | 0.018314 | -0.27609 | 121.8997 | 121.8342 | 122.0307 | 121.8123 | -0.017229 | 121.8634 | 121.9437 | 121.6493 | 121.8296 | -0.26027
982.5781 | 122.0673 | -121.7514 | 0.10986 | 1.4211e-13 | -0.029395 | 0.01468 | -0.0036391 | -0.011905 | 0.01927 | -0.23296 | -0.0020702 | -0.001408 | -0.0040571 | 0.031803 | 0.010963 | 0.069723 | 0.019721 | 0.028217 | 0.11622 | 0.055306 | 0.24269 | 0.11094 | 0.078886 | 0.046146 | 0.01233 | 0.07993 | 0.1648 | -0.13419 | -0.11836 | 121.8623 | 0.006362 | 121.8211 | 121.7796 | -0.082725 | -0.054557 | 0.13283 | 121.633 | -0.029933 | 121.8303 | 121.7637 | 0.13069 | 0.054937 | -0.24405 | 121.8676 | 121.8067 | 121.9941 | 121.7711 | 0.001079 | 121.8313 | 121.9162 | 121.6172 | 121.7975 | -0.22822
984.3125 | 122.0032 | -121.7697 | 0.14191 | 1.4211e-13 | -0.029181 | 0.01468 | -0.0038527 | -0.011692 | 0.01927 | -0.24059 | -0.0018566 | -0.00076696 | -0.0040571 | 0.031803 | 0.010535 | 0.07888 | 0.019721 | 0.01906 | 0.11165 | 0.046148 | 0.24269 | 0.1201 | 0.078886 | 0.036989 | 0.01233 | 0.075351 | 0.15564 | -0.13876 | -0.12752 | 121.8898 | -0.03026 | 121.8486 | 121.7888 | -0.10104 | -0.095759 | 0.10079 | 121.6422 | -0.066556 | 121.8486 | 121.782 | 0.13985 | 0.013736 | -0.28067 | 121.8814 | 121.8159 | 122.0124 | 121.7894 | -0.021807 | 121.8451 | 121.9254 | 121.6309 | 121.8067 | -0.26943
985.9844 | 122.0078 | -121.7926 | 0.12817 | 1.4211e-13 | -0.028968 | 0.014252 | -0.0034253 | -0.011905 | 0.019484 | -0.24059 | -0.0020702 | -0.00098076 | -0.0038435 | 0.031803 | 0.010535 | 0.083459 | 0.0243 | 0.028217 | 0.11165 | 0.050727 | 0.25185 | 0.1201 | 0.083464 | 0.046146 | 0.016908 | 0.084508 | 0.1648 | -0.12961 | -0.11836 | 121.9127 | -0.016527 | 121.8761 | 121.8208 | -0.091883 | -0.077447 | 0.12368 | 121.6742 | -0.043666 | 121.8761 | 121.8095 | 0.13527 | 0.036626 | -0.25778 | 121.9043 | 121.8433 | 122.0445 | 121.8169 | -0.008074 | 121.8771 | 121.9574 | 121.663 | 121.8387 | -0.24654
987.7188 | 122.081 | -121.7468 | 0.10529 | 1.4211e-13 | -0.029395 | 0.014252 | -0.0034253 | -0.012119 | 0.019484 | -0.24059 | -0.0020702 | -0.0011944 | -0.0040571 | 0.031589 | 0.010535 | 0.083459 | 0.0243 | 0.023639 | 0.10707 | 0.046148 | 0.24727 | 0.11552 | 0.083464 | 0.041567 | 0.007751 | 0.089087 | 0.16022 | -0.13876 | -0.12752 | 121.8623 | 0.001782 | 121.8303 | 121.7705 | -0.091882 | -0.059138 | 0.14199 | 121.6193 | -0.016199 | 121.8303 | 121.7546 | 0.13527 | 0.054936 | -0.24405 | 121.8539 | 121.793 | 121.9941 | 121.7711 | 0.010235 | 121.8359 | 121.907 | 121.6081 | 121.7884 | -0.2328
989.3906 | 122.0444 | -121.7697 | 0.10986 | 1.4211e-13 | -0.029181 | 0.014466 | -0.0036391 | -0.011692 | 0.019484 | -0.23296 | -0.0022838 | -0.00076696 | -0.0042707 | 0.031376 | 0.010749 | 0.07888 | 0.0243 | 0.023639 | 0.1208 | 0.059885 | 0.24269 | 0.11094 | 0.074307 | 0.046146 | 0.016908 | 0.084508 | 0.15564 | -0.13876 | -0.12752 | 121.8807 | 0.010941 | 121.8486 | 121.7934 | -0.087303 | -0.049978 | 0.13283 | 121.6422 | -0.025355 | 121.844 | 121.7866 | 0.14443 | 0.04578 | -0.24863 | 121.8905 | 121.8296 | 122.0124 | 121.794 | 0.001079 | 121.8542 | 121.9254 | 121.6309 | 121.8159 | -0.23738
991.0625 | 122.0947 | -121.7743 | 0.1236 | 1.4211e-13 | -0.029395 | 0.014252 | -0.0036391 | -0.011692 | 0.01927 | -0.24822 | -0.0020702 | -0.0011944 | -0.0038435 | 0.031803 | 0.010322 | 0.083459 | 0.019721 | 0.023639 | 0.11622 | 0.055306 | 0.24727 | 0.12468 | 0.083464 | 0.036989 | 0.016908 | 0.07993 | 0.15107 | -0.13876 | -0.11836 | 121.899 | -0.007371 | 121.8578 | 121.7979 | -0.10104 | -0.06829 | 0.12368 | 121.6559 | -0.043666 | 121.8578 | 121.7912 | 0.13527 | 0.027469 | -0.26236 | 121.8905 | 121.8296 | 122.0216 | 121.794 | 0.001083 | 121.8542 | 121.9254 | 121.6355 | 121.8113 | -0.24196
992.8125 | 122.0078 | -121.756 | 0.13733 | 1.4211e-13 | -0.029395 | 0.014252 | -0.0032117 | -0.011692 | 0.01927 | -0.24059 | -0.0022838 | -0.00098076 | -0.0038435 | 0.031589 | 0.010322 | 0.07888 | 0.0243 | 0.023639 | 0.1208 | 0.050727 | 0.24269 | 0.11094 | 0.083464 | 0.046146 | 0.01233 | 0.084508 | 0.15564 | -0.13876 | -0.12752 | 121.8669 | -0.016525 | 121.8349 | 121.7796 | -0.087303 | -0.086602 | 0.10537 | 121.6285 | -0.052821 | 121.8394 | 121.7683 | 0.13985 | 0.018314 | -0.27609 | 121.8768 | 121.8067 | 121.9987 | 121.7803 | -0.026387 | 121.8405 | 121.9116 | 121.6172 | 121.8021 | -0.26485
994.5469 | 122.0215 | -121.7743 | 0.11902 | 1.4211e-13 | -0.029609 | 0.014466 | -0.0036391 | -0.012119 | 0.019484 | -0.24059 | -0.0020702 | -0.0011944 | -0.0044845 | 0.031803 | 0.010535 | 0.07888 | 0.028878 | 0.01906 | 0.1208 | 0.050727 | 0.23812 | 0.11552 | 0.074307 | 0.046146 | 0.01233 | 0.07993 | 0.16022 | -0.12961 | -0.12752 | 121.8898 | 0.001785 | 121.8532 | 121.7934 | -0.096461 | -0.068292 | 0.1191 | 121.6468 | -0.039089 | 121.8486 | 121.7866 | 0.13985 | 0.041203 | -0.24863 | 121.8951 | 121.825 | 122.0124 | 121.8032 | -0.003498 | 121.8542 | 121.9345 | 121.6447 | 121.8204 | -0.24654
996.2969 | 122.0123 | -121.7972 | 0.13275 | 1.4211e-13 | -0.029609 | 0.01468 | -0.0036391 | -0.012119 | 0.019484 | -0.23296 | -0.0018566 | -0.00098076 | -0.0040571 | 0.031803 | 0.010963 | 0.074302 | 0.015142 | 0.023639 | 0.11622 | 0.059885 | 0.24269 | 0.1201 | 0.074307 | 0.041567 | 0.01233 | 0.07993 | 0.16022 | -0.13419 | -0.12294 | 121.9173 | -0.016526 | 121.8715 | 121.8208 | -0.096461 | -0.072866 | 0.10994 | 121.6742 | -0.052821 | 121.8715 | 121.8095 | 0.13527 | 0.027471 | -0.26694 | 121.9134 | 121.8571 | 122.0399 | 121.8123 | -0.012651 | 121.8771 | 121.9574 | 121.663 | 121.8387 | -0.25569
998.0312 | 122.0078 | -121.7926 | 0.13733 | 1.4211e-13 | -0.029181 | 0.014466 | -0.0036391 | -0.011692 | 0.01927 | -0.2177 | -0.0018566 | -0.0011944 | -0.0038435 | 0.031589 | 0.010535 | 0.07888 | 0.010564 | 0.023639 | 0.10707 | 0.050727 | 0.24269 | 0.11552 | 0.078886 | 0.046146 | 0.016908 | 0.084508 | 0.15107 | -0.13876 | -0.12294 | 121.9081 | -0.030261 | 121.8715 | 121.8162 | -0.091882 | -0.086602 | 0.10537 | 121.6697 | -0.052821 | 121.8715 | 121.8095 | 0.13985 | 0.013736 | -0.27609 | 121.8997 | 121.8433 | 122.0353 | 121.8032 | -0.021808 | 121.8771 | 121.9437 | 121.6538 | 121.8387 | -0.26027
999.7812 | 122.0123 | -121.7834 | 0.1236 | 1.4211e-13 | -0.028754 | 0.014252 | -0.0036391 | -0.011905 | 0.01927 | -0.23296 | -0.0020702 | -0.0011944 | -0.0040571 | 0.031803 | 0.010749 | 0.083459 | 0.0243 | 0.023639 | 0.11622 | 0.050727 | 0.23812 | 0.11552 | 0.074307 | 0.036989 | 0.01233 | 0.07993 | 0.14649 | -0.14334 | -0.12752 | 121.899 | -0.007371 | 121.8669 | 121.8071 | -0.091882 | -0.072869 | 0.11452 | 121.6559 | -0.043666 | 121.8578 | 121.7958 | 0.13985 | 0.02289 | -0.26694 | 121.8997 | 121.8342 | 122.0216 | 121.8077 | -0.008075 | 121.8634 | 121.9299 | 121.6401 | 121.8204 | -0.25111
1001.5312 | 122.049 | -121.7743 | 0.13275 | 1.4211e-13 | -0.029395 | 0.01468 | -0.0036391 | -0.011905 | 0.019484 | -0.24059 | -0.0020702 | -0.00076696 | -0.0042707 | 0.031803 | 0.010322 | 0.07888 | 0.019721 | 0.01906 | 0.11622 | 0.055306 | 0.24269 | 0.11094 | 0.078886 | 0.041567 | 0.01233 | 0.07993 | 0.16022 | -0.13876 | -0.1321 | 121.8852 | -0.016526 | 121.8532 | 121.7934 | -0.091882 | -0.077445 | 0.10994 | 121.6422 | -0.052821 | 121.8532 | 121.7866 | 0.14443 | 0.027471 | -0.27152 | 121.8905 | 121.8296 | 122.017 | 121.794 | -0.021809 | 121.8542 | 121.9345 | 121.6355 | 121.8159 | -0.26485
1003.2188 | 122.0078 | -121.8109 | 0.13733 | 1.4211e-13 | -0.029395 | 0.014252 | -0.0038527 | -0.011905 | 0.019057 | -0.23296 | -0.001643 | -0.0011944 | -0.0038435 | 0.031803 | 0.010749 | 0.083459 | 0.0243 | 0.023639 | 0.11165 | 0.055306 | 0.23812 | 0.1201 | 0.074307 | 0.046146 | 0.01233 | 0.075351 | 0.16022 | -0.12961 | -0.12752 | 121.931 | -0.025682 | 121.8944 | 121.8346 | -0.096461 | -0.082023 | 0.10079 | 121.6834 | -0.061978 | 121.8852 | 121.8232 | 0.13985 | 0.022893 | -0.26694 | 121.9226 | 121.8662 | 122.049 | 121.8352 | -0.017229 | 121.8863 | 121.9711 | 121.6813 | 121.8571 | -0.26485
1004.9531 | 122.0535 | -121.7926 | 0.11444 | 1.4211e-13 | -0.028968 | 0.014252 | -0.0036391 | -0.011905 | 0.019698 | -0.23296 | -0.0020702 | -0.00076696 | -0.0042707 | 0.031803 | 0.010535 | 0.074302 | 0.019721 | 0.01906 | 0.1208 | 0.050727 | 0.24269 | 0.11094 | 0.083464 | 0.046146 | 0.007751 | 0.084508 | 0.15564 | -0.13419 | -0.12752 | 121.9035 | 0.006363 | 121.8669 | 121.8117 | -0.091882 | -0.063714 | 0.12825 | 121.6651 | -0.029933 | 121.8761 | 121.8004 | 0.13527 | 0.041202 | -0.24863 | 121.9134 | 121.8433 | 122.0353 | 121.8123 | -0.003499 | 121.8771 | 121.9482 | 121.6584 | 121.8387 | -0.24196
1006.625 | 122.081 | -121.7514 | 0.1236 | 1.4211e-13 | -0.029609 | 0.01468 | -0.0036391 | -0.011692 | 0.019057 | -0.23296 | -0.0018566 | -0.00055336 | -0.0040571 | 0.032017 | 0.010322 | 0.07888 | 0.010564 | 0.01906 | 0.11622 | 0.055306 | 0.24269 | 0.1201 | 0.078886 | 0.041567 | 0.016908 | 0.07993 | 0.1648 | -0.13876 | -0.12294 | 121.8715 | -0.007371 | 121.8303 | 121.7705 | -0.10104 | -0.06829 | 0.1191 | 121.6285 | -0.043666 | 121.8303 | 121.7683 | 0.13985 | 0.041204 | -0.26236 | 121.8676 | 121.8067 | 121.9941 | 121.762 | -0.003496 | 121.8313 | 121.9162 | 121.6126 | 121.793 | -0.24654
1008.3125 | 122.1222 | -121.756 | 0.11902 | 1.4211e-13 | -0.029395 | 0.014466 | -0.0038527 | -0.012119 | 0.01927 | -0.24822 | -0.0018566 | -0.00098076 | -0.0042707 | 0.032017 | 0.010749 | 0.074302 | 0.0243 | 0.023639 | 0.1208 | 0.050727 | 0.24727 | 0.1201 | 0.074307 | 0.041567 | 0.016908 | 0.075351 | 0.15564 | -0.14334 | -0.11836 | 121.8761 | 0.001785 | 121.8303 | 121.7796 | -0.096461 | -0.068292 | 0.12826 | 121.6376 | -0.043668 | 121.8303 | 121.7729 | 0.13527 | 0.036624 | -0.26236 | 121.8768 | 121.8067 | 122.0033 | 121.7803 | 0.001081 | 121.8313 | 121.9116 | 121.6126 | 121.7975 | -0.23738
1010.0469 | 122.0673 | -121.7422 | 0.10529 | 1.4211e-13 | -0.029395 | 0.014252 | -0.0036391 | -0.011905 | 0.01927 | -0.23296 | -0.0018566 | -0.0011944 | -0.0040571 | 0.032017 | 0.010535 | 0.07888 | 0.019721 | 0.023639 | 0.11622 | 0.050727 | 0.24727 | 0.11552 | 0.078886 | 0.041567 | 0.016908 | 0.07993 | 0.1648 | -0.13876 | -0.12752 | 121.8578 | 0.010939 | 121.8211 | 121.7659 | -0.091882 | -0.054559 | 0.14199 | 121.6147 | -0.025356 | 121.8211 | 121.7592 | 0.14443 | 0.059514 | -0.24405 | 121.8585 | 121.793 | 121.9895 | 121.762 | 0.010235 | 121.8222 | 121.907 | 121.6035 | 121.7838 | -0.2328
1011.7812 | 122.0673 | -121.7743 | 0.11444 | 1.4211e-13 | -0.029181 | 0.014466 | -0.0034253 | -0.011905 | 0.01927 | -0.22533 | -0.0022838 | -0.001408 | -0.0040571 | 0.031803 | 0.010108 | 0.07888 | 0.019721 | 0.009904 | 0.11165 | 0.055306 | 0.24269 | 0.1201 | 0.074307 | 0.041567 | 0.01233 | 0.07993 | 0.1648 | -0.12961 | -0.12294 | 121.8944 | -0.002794 | 121.8532 | 121.7842 | -0.1102 | -0.059135 | 0.12825 | 121.6514 | -0.034511 | 121.8486 | 121.7866 | 0.13527 | 0.050359 | -0.24405 | 121.8859 | 121.8296 | 122.017 | 121.794 | 0.005659 | 121.8542 | 121.9391 | 121.6447 | 121.8159 | -0.23738
1013.4688 | 122.0306 | -121.7743 | 0.11902 | 1.4211e-13 | -0.029395 | 0.014039 | -0.0036391 | -0.011905 | 0.019484 | -0.22533 | -0.0020702 | -0.00098076 | -0.0040571 | 0.032017 | 0.010535 | 0.074302 | 0.0243 | 0.023639 | 0.11622 | 0.050727 | 0.24269 | 0.10636 | 0.078886 | 0.041567 | 0.016908 | 0.075351 | 0.16938 | -0.12961 | -0.12752 | 121.8807 | -0.002794 | 121.8486 | 121.7979 | -0.082724 | -0.068292 | 0.12368 | 121.6468 | -0.043668 | 121.8532 | 121.7912 | 0.14443 | 0.05036 | -0.24863 | 121.8905 | 121.825 | 122.017 | 121.7986 | -0.012656 | 121.8496 | 121.9437 | 121.6447 | 121.8159 | -0.24654
1015.2031 | 121.994 | -121.7743 | 0.14648 | 1.4211e-13 | -0.029609 | 0.014252 | -0.0036391 | -0.012119 | 0.01927 | -0.24059 | -0.0022838 | -0.0011944 | -0.0038435 | 0.032017 | 0.010535 | 0.074302 | 0.005985 | 0.023639 | 0.12538 | 0.055306 | 0.24269 | 0.11552 | 0.074307 | 0.046146 | 0.016908 | 0.07993 | 0.16022 | -0.13419 | -0.12294 | 121.8898 | -0.021102 | 121.8486 | 121.7979 | -0.091882 | -0.091178 | 0.096211 | 121.6514 | -0.066554 | 121.8486 | 121.7912 | 0.13985 | 0.013738 | -0.28067 | 121.8997 | 121.8296 | 122.017 | 121.7803 | -0.030963 | 121.8542 | 121.9345 | 121.6401 | 121.8204 | -0.26942
1016.9375 | 122.0673 | -121.7789 | 0.1236 | 1.4211e-13 | -0.029395 | 0.01468 | -0.0036391 | -0.011905 | 0.019057 | -0.24059 | -0.0020702 | -0.00098076 | -0.0042707 | 0.032017 | 0.010535 | 0.07888 | 0.019721 | 0.023639 | 0.11165 | 0.050727 | 0.24269 | 0.11552 | 0.078886 | 0.046146 | 0.01233 | 0.07993 | 0.15564 | -0.13419 | -0.12752 | 121.8944 | -0.011949 | 121.8577 | 121.8025 | -0.091882 | -0.072869 | 0.1191 | 121.6514 | -0.043666 | 121.8578 | 121.7912 | 0.13985 | 0.032047 | -0.25778 | 121.8905 | 121.8296 | 122.0216 | 121.7986 | -0.008075 | 121.8588 | 121.9345 | 121.6447 | 121.825 | -0.25111
1018.6875 | 122.0078 | -121.7697 | 0.13275 | 1.4211e-13 | -0.029181 | 0.014466 | -0.0036391 | -0.011905 | 0.01927 | -0.24822 | -0.0020702 | -0.001408 | -0.0034163 | 0.031803 | 0.010322 | 0.07888 | 0.019721 | 0.01906 | 0.11622 | 0.055306 | 0.24727 | 0.1201 | 0.083464 | 0.046146 | 0.007751 | 0.07993 | 0.16022 | -0.13876 | -0.12752 | 121.8898 | -0.016526 | 121.8486 | 121.7888 | -0.10104 | -0.077445 | 0.11452 | 121.6422 | -0.052821 | 121.8532 | 121.7775 | 0.13527 | 0.027471 | -0.27152 | 121.8859 | 121.825 | 122.017 | 121.7894 | -0.012651 | 121.8496 | 121.9299 | 121.6309 | 121.8159 | -0.26027
1020.4375 | 122.0444 | -121.788 | 0.12817 | 1.4211e-13 | -0.029181 | 0.014039 | -0.0036391 | -0.012333 | 0.019057 | -0.23296 | -0.0022838 | -0.0011944 | -0.0042707 | 0.031803 | 0.010535 | 0.074302 | 0.019721 | 0.023639 | 0.11165 | 0.041569 | 0.24269 | 0.11552 | 0.069728 | 0.036989 | 0.016908 | 0.07993 | 0.16022 | -0.13876 | -0.12752 | 121.9035 | -0.016527 | 121.8623 | 121.8117 | -0.091882 | -0.086605 | 0.11452 | 121.6605 | -0.048244 | 121.8578 | 121.8049 | 0.14443 | 0.032048 | -0.26694 | 121.8997 | 121.8296 | 122.0307 | 121.8077 | -0.012653 | 121.868 | 121.9482 | 121.6493 | 121.825 | -0.25569
1022.125 | 122.0764 | -121.7606 | 0.11902 | 1.4211e-13 | -0.029181 | 0.014039 | -0.0040665 | -0.011692 | 0.01927 | -0.23296 | -0.0022838 | -0.0011944 | -0.0040571 | 0.032017 | 0.010749 | 0.083459 | 0.019721 | 0.01906 | 0.11622 | 0.059885 | 0.24269 | 0.11552 | 0.074307 | 0.046146 | 0.016908 | 0.07993 | 0.16022 | -0.11587 | -0.12752 | 121.8761 | -0.002794 | 121.844 | 121.7796 | -0.096461 | -0.059134 | 0.12368 | 121.633 | -0.039089 | 121.8349 | 121.7775 | 0.14443 | 0.041203 | -0.23489 | 121.8768 | 121.8204 | 122.0033 | 121.7803 | -0.003498 | 121.8405 | 121.9208 | 121.6447 | 121.8067 | -0.24654
1023.875 | 121.9711 | -121.8201 | 0.16022 | 1.4211e-13 | -0.029181 | 0.014252 | -0.0036391 | -0.011905 | 0.01927 | -0.23296 | -0.0018566 | -0.0011944 | -0.0038435 | 0.032017 | 0.010322 | 0.07888 | 0.0243 | 0.023639 | 0.11622 | 0.055306 | 0.24727 | 0.12468 | 0.074307 | 0.046146 | 0.007751 | 0.089087 | 0.16022 | -0.13419 | -0.12752 | 121.9447 | -0.043992 | 121.8989 | 121.8437 | -0.10104 | -0.10491 | 0.087057 | 121.6926 | -0.07113 | 121.8944 | 121.8278 | 0.13527 | 5e-06 | -0.2944 | 121.9363 | 121.8754 | 122.0673 | 121.8444 | -0.035538 | 121.9092 | 121.9803 | 121.6859 | 121.8662 | -0.28773
1025.5469 | 122.0856 | -121.7743 | 0.09613 | 1.4211e-13 | -0.028968 | 0.014039 | -0.0034253 | -0.012119 | 0.019057 | -0.22533 | -0.0022838 | -0.0011944 | -0.0042707 | 0.032017 | 0.010749 | 0.074302 | 0.019721 | 0.023639 | 0.11165 | 0.055306 | 0.24269 | 0.12468 | 0.078886 | 0.036989 | 0.016908 | 0.07993 | 0.16022 | -0.13876 | -0.1321 | 121.899 | 0.015517 | 121.8486 | 121.7979 | -0.10104 | -0.040824 | 0.14657 | 121.6422 | -0.0162 | 121.8532 | 121.7912 | 0.149 | 0.064092 | -0.23489 | 121.8859 | 121.8296 | 122.017 | 121.794 | 0.028549 | 121.8542 | 121.9345 | 121.6355 | 121.8113 | -0.22823
1027.2812 | 121.9849 | -121.8109 | 0.15564 | 1.4211e-13 | -0.029181 | 0.013825 | -0.0036391 | -0.011905 | 0.019057 | -0.23296 | -0.0022838 | -0.0011944 | -0.0040571 | 0.032017 | 0.010322 | 0.074302 | 0.015142 | 0.028217 | 0.11622 | 0.046148 | 0.24727 | 0.11552 | 0.078886 | 0.046146 | 0.01233 | 0.075351 | 0.15564 | -0.14334 | -0.12752 | 121.9264 | -0.039415 | 121.8852 | 121.8391 | -0.087304 | -0.10949 | 0.091634 | 121.6834 | -0.080289 | 121.8898 | 121.8232 | 0.13985 | 3e-06 | -0.29898 | 121.9271 | 121.8571 | 122.0582 | 121.8261 | -0.040119 | 121.8863 | 121.9666 | 121.6676 | 121.8571 | -0.28316
1028.9531 | 122.0947 | -121.7834 | 0.13733 | 1.4211e-13 | -0.029395 | 0.014252 | -0.0034253 | -0.012119 | 0.019484 | -0.23296 | -0.0018566 | -0.00076696 | -0.0040571 | 0.031803 | 0.010108 | 0.069723 | 0.0243 | 0.028217 | 0.1208 | 0.059885 | 0.24269 | 0.1201 | 0.078886 | 0.046146 | 0.01233 | 0.07993 | 0.16022 | -0.13876 | -0.12294 | 121.9035 | -0.016525 | 121.8532 | 121.8117 | -0.091883 | -0.077444 | 0.10537 | 121.6605 | -0.057399 | 121.8623 | 121.7958 | 0.13527 | 0.022893 | -0.27609 | 121.9043 | 121.8433 | 122.0261 | 121.8077 | -0.017229 | 121.8634 | 121.9437 | 121.6447 | 121.8296 | -0.26027
1030.6875 | 122.0764 | -121.7697 | 0.10071 | 1.4211e-13 | -0.029395 | 0.014466 | -0.0038527 | -0.012119 | 0.019057 | -0.22533 | -0.0020702 | -0.0011944 | -0.0038435 | 0.03223 | 0.010108 | 0.074302 | 0.019721 | 0.01906 | 0.1208 | 0.055306 | 0.25185 | 0.11552 | 0.074307 | 0.041567 | 0.007751 | 0.07993 | 0.16022 | -0.12961 | -0.12294 | 121.8852 | 0.020096 | 121.844 | 121.7888 | -0.096461 | -0.045402 | 0.15114 | 121.6468 | -0.020778 | 121.844 | 121.7775 | 0.13069 | 0.059514 | -0.23031 | 121.8905 | 121.825 | 122.0216 | 121.7894 | 0.014813 | 121.8496 | 121.9299 | 121.6401 | 121.8113 | -0.22365
1032.4219 | 122.0169 | -121.7834 | 0.13275 | 1.4211e-13 | -0.029181 | 0.014252 | -0.0038527 | -0.011905 | 0.01927 | -0.22533 | -0.0022838 | -0.00076696 | -0.0040571 | 0.031803 | 0.010322 | 0.07888 | 0.0243 | 0.023639 | 0.11165 | 0.055306 | 0.24727 | 0.1201 | 0.078886 | 0.050725 | 0.016908 | 0.075351 | 0.15564 | -0.12961 | -0.12294 | 121.9035 | -0.021104 | 121.8623 | 121.8071 | -0.096461 | -0.077445 | 0.11452 | 121.6605 | -0.0574 | 121.8623 | 121.8004 | 0.13985 | 0.022892 | -0.26236 | 121.8951 | 121.8388 | 122.0307 | 121.8077 | -0.012651 | 121.8588 | 121.9391 | 121.6538 | 121.8342 | -0.25569
1034.1562 | 122.0123 | -121.7926 | 0.13275 | 1.4211e-13 | -0.029609 | 0.014466 | -0.0038527 | -0.012333 | 0.01927 | -0.23296 | -0.0022838 | -0.00098076 | -0.0038435 | 0.032017 | 0.010322 | 0.07888 | 0.015142 | 0.037373 | 0.1208 | 0.055306 | 0.24269 | 0.1201 | 0.078886 | 0.046146 | 0.016908 | 0.075351 | 0.15564 | -0.13419 | -0.1321 | 121.9127 | -0.011947 | 121.8715 | 121.83 | -0.082727 | -0.077445 | 0.10994 | 121.6605 | -0.0574 | 121.8715 | 121.8095 | 0.149 | 0.022892 | -0.26694 | 121.9134 | 121.8479 | 122.0353 | 121.8077 | -0.012651 | 121.868 | 121.9482 | 121.6584 | 121.8387 | -0.26485
1035.9062 | 122.0306 | -121.7926 | 0.14191 | 1.4211e-13 | -0.029609 | 0.014252 | -0.0032117 | -0.011905 | 0.01927 | -0.23296 | -0.001643 | -0.00098076 | -0.0038435 | 0.031803 | 0.010535 | 0.07888 | 0.019721 | 0.023639 | 0.10249 | 0.055306 | 0.24727 | 0.11552 | 0.078886 | 0.041567 | 0.01233 | 0.084508 | 0.16022 | -0.12961 | -0.1321 | 121.9081 | -0.039417 | 121.8715 | 121.8162 | -0.091882 | -0.086601 | 0.10537 | 121.6605 | -0.057399 | 121.8715 | 121.8049 | 0.14443 | 0.018315 | -0.27151 | 121.8951 | 121.8479 | 122.0399 | 121.8123 | -0.026386 | 121.8771 | 121.9528 | 121.663 | 121.8342 | -0.274
1037.5781 | 122.0123 | -121.8109 | 0.14648 | 1.4211e-13 | -0.029395 | 0.014252 | -0.0034253 | -0.011905 | 0.019057 | -0.23296 | -0.0020702 | -0.001408 | -0.0040571 | 0.03223 | 0.010749 | 0.074302 | 0.015142 | 0.032795 | 0.11165 | 0.059885 | 0.25185 | 0.12468 | 0.078886 | 0.046146 | 0.021487 | 0.07993 | 0.15564 | -0.12961 | -0.12294 | 121.9356 | -0.034837 | 121.8852 | 121.8437 | -0.091884 | -0.086599 | 0.10537 | 121.688 | -0.066554 | 121.8898 | 121.8324 | 0.14443 | 0.009159 | -0.27609 | 121.9226 | 121.8708 | 122.0628 | 121.8261 | -0.021805 | 121.8908 | 121.9666 | 121.6813 | 121.8571 | -0.26942
1039.3125 | 121.962 | -121.7789 | 0.13275 | 1.4211e-13 | -0.029395 | 0.01468 | -0.0034253 | -0.011478 | 0.019057 | -0.22533 | -0.0020702 | -0.00098076 | -0.0038435 | 0.03223 | 0.010322 | 0.07888 | 0.019721 | 0.023639 | 0.10707 | 0.050727 | 0.24269 | 0.11552 | 0.074307 | 0.046146 | 0.007751 | 0.07993 | 0.1648 | -0.12503 | -0.1321 | 121.8944 | -0.025683 | 121.8577 | 121.8025 | -0.091882 | -0.082024 | 0.10994 | 121.6468 | -0.052821 | 121.8532 | 121.7866 | 0.13985 | 0.032049 | -0.25778 | 121.8859 | 121.8296 | 122.0216 | 121.7986 | -0.01723 | 121.8588 | 121.9437 | 121.6538 | 121.825 | -0.26485
1040.9844 | 121.962 | -121.8155 | 0.14191 | 1.4211e-13 | -0.029181 | 0.014252 | -0.0036391 | -0.011905 | 0.019484 | -0.23296 | -0.0020702 | -0.00098076 | -0.0040571 | 0.03223 | 0.010535 | 0.07888 | 0.005985 | 0.032795 | 0.10707 | 0.046148 | 0.24727 | 0.11552 | 0.083464 | 0.036989 | 0.01233 | 0.075351 | 0.16022 | -0.12961 | -0.1321 | 121.931 | -0.034839 | 121.8944 | 121.8483 | -0.082726 | -0.095759 | 0.10537 | 121.6834 | -0.066556 | 121.899 | 121.8278 | 0.14443 | 0.018315 | -0.27151 | 121.9226 | 121.8616 | 122.0628 | 121.8215 | -0.026386 | 121.8908 | 121.9757 | 121.6859 | 121.8525 | -0.274
1042.7188 | 121.9894 | -121.8018 | 0.15106 | 1.4211e-13 | -0.029395 | 0.014466 | -0.0036391 | -0.011905 | 0.01927 | -0.22533 | -0.0020702 | -0.0011944 | -0.0040571 | 0.032017 | 0.010749 | 0.07888 | 0.019721 | 0.037373 | 0.11622 | 0.055306 | 0.25185 | 0.11094 | 0.078886 | 0.046146 | 0.016908 | 0.084508 | 0.1648 | -0.13419 | -0.12752 | 121.9127 | -0.034837 | 121.8806 | 121.8391 | -0.073569 | -0.095756 | 0.10079 | 121.6742 | -0.066554 | 121.8806 | 121.8187 | 0.14443 | 0.013738 | -0.28525 | 121.918 | 121.8571 | 122.0536 | 121.8215 | -0.04012 | 121.8863 | 121.9666 | 121.6676 | 121.8479 | -0.27858
1044.4688 | 122.0078 | -121.8018 | 0.15106 | 1.4211e-13 | -0.029609 | 0.014252 | -0.0036391 | -0.012119 | 0.01927 | -0.24822 | -0.0020702 | -0.0011944 | -0.0042707 | 0.032017 | 0.010749 | 0.074302 | 0.019721 | 0.028217 | 0.11165 | 0.046148 | 0.24727 | 0.11094 | 0.078886 | 0.046146 | 0.007751 | 0.07993 | 0.16022 | -0.12961 | -0.12294 | 121.9127 | -0.039415 | 121.8761 | 121.83 | -0.082725 | -0.10491 | 0.096212 | 121.6788 | -0.071132 | 121.8806 | 121.8095 | 0.13069 | 0.00916 | -0.28067 | 121.9134 | 121.8479 | 122.049 | 121.8215 | -0.04012 | 121.8817 | 121.962 | 121.6722 | 121.8479 | -0.274
1046.2188 | 122.0169 | -121.7972 | 0.1236 | 1.4211e-13 | -0.029181 | 0.014252 | -0.0040665 | -0.012119 | 0.01927 | -0.23296 | -0.0020702 | -0.00098076 | -0.0042707 | 0.032017 | 0.010535 | 0.083459 | 0.019721 | 0.028217 | 0.1208 | 0.055306 | 0.24727 | 0.11552 | 0.074307 | 0.041567 | 0.021487 | 0.084508 | 0.1648 | -0.12961 | -0.12294 | 121.9127 | -0.002792 | 121.8806 | 121.8254 | -0.087304 | -0.06829 | 0.12368 | 121.6742 | -0.039088 | 121.8715 | 121.8187 | 0.14443 | 0.041204 | -0.2532 | 121.918 | 121.8525 | 122.0445 | 121.8169 | -0.008075 | 121.8817 | 121.962 | 121.6676 | 121.8387 | -0.24654
1047.9688 | 122.0993 | -121.7789 | 0.12817 | 1.4211e-13 | -0.029395 | 0.014466 | -0.0038527 | -0.012119 | 0.01927 | -0.23296 | -0.0020702 | -0.00076696 | -0.0042707 | 0.032017 | 0.010535 | 0.07888 | 0.0243 | 0.028217 | 0.1208 | 0.055306 | 0.24269 | 0.11552 | 0.088043 | 0.046146 | 0.01233 | 0.07993 | 0.15564 | -0.13876 | -0.12752 | 121.8944 | -0.00737 | 121.8577 | 121.8071 | -0.087304 | -0.072868 | 0.11452 | 121.6514 | -0.048244 | 121.8669 | 121.7912 | 0.13985 | 0.027469 | -0.26694 | 121.8997 | 121.8342 | 122.0216 | 121.8032 | -0.012653 | 121.8588 | 121.9345 | 121.6401 | 121.825 | -0.25569
1049.6562 | 121.9711 | -121.788 | 0.14648 | 1.4211e-13 | -0.029395 | 0.014252 | -0.0036391 | -0.012119 | 0.01927 | -0.23296 | -0.0022838 | -0.00098076 | -0.0040571 | 0.032017 | 0.010535 | 0.074302 | 0.0243 | 0.028217 | 0.11622 | 0.055306 | 0.24727 | 0.11094 | 0.078886 | 0.041567 | 0.01233 | 0.07993 | 0.15107 | -0.13419 | -0.12294 | 121.899 | -0.030259 | 121.8623 | 121.8162 | -0.082725 | -0.091178 | 0.10079 | 121.6651 | -0.066554 | 121.8669 | 121.8004 | 0.13527 | 0.004581 | -0.28067 | 121.9043 | 121.8433 | 122.0353 | 121.8123 | -0.035542 | 121.868 | 121.9391 | 121.6538 | 121.8296 | -0.26942
1051.4062 | 121.9803 | -121.8018 | 0.13275 | 1.4211e-13 | -0.029181 | 0.014252 | -0.0038527 | -0.012119 | 0.019057 | -0.23296 | -0.0018566 | -0.0011944 | -0.0038435 | 0.03223 | 0.010749 | 0.083459 | 0.0243 | 0.028217 | 0.10707 | 0.059885 | 0.24269 | 0.11552 | 0.074307 | 0.050725 | 0.01233 | 0.07993 | 0.15564 | -0.12503 | -0.12752 | 121.9173 | -0.025683 | 121.8852 | 121.83 | -0.087304 | -0.072866 | 0.10994 | 121.6742 | -0.052821 | 121.8761 | 121.8141 | 0.13985 | 0.022892 | -0.25778 | 121.9088 | 121.8616 | 122.0445 | 121.8261 | -0.01723 | 121.8817 | 121.9574 | 121.6767 | 121.8525 | -0.26027
1053.1562 | 121.9711 | -121.8292 | 0.14648 | 1.4211e-13 | -0.029395 | 0.014466 | -0.0036391 | -0.011692 | 0.01927 | -0.24059 | -0.0020702 | -0.00076696 | -0.0036299 | 0.03223 | 0.010749 | 0.065145 | 0.0243 | 0.032795 | 0.11622 | 0.055306 | 0.24727 | 0.11552 | 0.078886 | 0.050725 | 0.007751 | 0.07993 | 0.16938 | -0.097557 | -0.12752 | 121.9447 | -0.030259 | 121.8944 | 121.862 | -0.082726 | -0.091178 | 0.10079 | 121.7017 | -0.066554 | 121.9081 | 121.837 | 0.13527 | 0.022895 | -0.24404 | 121.9454 | 121.8845 | 122.0765 | 121.8535 | -0.030963 | 121.9092 | 121.9986 | 121.7317 | 121.8799 | -0.274
1054.9062 | 122.0535 | -121.7606 | 0.1236 | 1.4211e-13 | -0.029181 | 0.014039 | -0.0038527 | -0.011905 | 0.01927 | -0.23296 | -0.0018566 | -0.0011944 | -0.0038435 | 0.032017 | 0.010535 | 0.07888 | 0.0243 | 0.032795 | 0.11165 | 0.055306 | 0.24269 | 0.1201 | 0.078886 | 0.046146 | 0.016908 | 0.07993 | 0.1648 | -0.14334 | -0.12294 | 121.8807 | -0.011949 | 121.8394 | 121.7934 | -0.087305 | -0.06829 | 0.1191 | 121.6376 | -0.043666 | 121.8394 | 121.7775 | 0.13985 | 0.041204 | -0.26694 | 121.8722 | 121.8159 | 122.0033 | 121.7849 | -0.003496 | 121.8405 | 121.9254 | 121.6172 | 121.8067 | -0.24654
1056.6406 | 122.0032 | -121.8201 | 0.13275 | 1.4211e-13 | -0.028968 | 0.014252 | -0.0038527 | -0.011905 | 0.019484 | -0.25585 | -0.0020702 | -0.0011944 | -0.0040571 | 0.03223 | 0.010535 | 0.083459 | 0.019721 | 0.028217 | 0.11165 | 0.050727 | 0.24727 | 0.12468 | 0.074307 | 0.041567 | 0.007751 | 0.075351 | 0.16022 | -0.13419 | -0.12752 | 121.9447 | -0.021104 | 121.9035 | 121.8483 | -0.096462 | -0.082024 | 0.11452 | 121.6926 | -0.0574 | 121.8944 | 121.8278 | 0.13527 | 0.027471 | -0.26694 | 121.9317 | 121.8708 | 122.0673 | 121.8398 | -0.008072 | 121.8954 | 121.9803 | 121.6859 | 121.8616 | -0.26027
1058.3438 | 121.9986 | -121.8063 | 0.14648 | 1.4211e-13 | -0.028968 | 0.014039 | -0.0034253 | -0.012119 | 0.019484 | -0.23296 | -0.0022838 | -0.0011944 | -0.0040571 | 0.032017 | 0.010749 | 0.074302 | 0.0243 | 0.037373 | 0.1208 | 0.050727 | 0.24727 | 0.11094 | 0.078886 | 0.055303 | 0.021487 | 0.084508 | 0.15564 | -0.12961 | -0.12752 | 121.9173 | -0.02568 | 121.8806 | 121.8437 | -0.073569 | -0.095757 | 0.10079 | 121.6788 | -0.061976 | 121.8852 | 121.8278 | 0.149 | 0.009159 | -0.27609 | 121.9271 | 121.8571 | 122.0536 | 121.8306 | -0.035542 | 121.8908 | 121.962 | 121.6767 | 121.8616 | -0.274
1060.0781 | 122.0993 | -121.7606 | 0.10986 | 1.4211e-13 | -0.029181 | 0.01468 | -0.0034253 | -0.012333 | 0.01927 | -0.22533 | -0.0020702 | -0.00098076 | -0.0042707 | 0.032444 | 0.010963 | 0.07888 | 0.019721 | 0.032795 | 0.11165 | 0.055306 | 0.24269 | 0.12468 | 0.078886 | 0.046146 | 0.007751 | 0.07993 | 0.16022 | -0.0884 | -0.12752 | 121.8852 | 0.001784 | 121.8394 | 121.7934 | -0.091884 | -0.054557 | 0.13283 | 121.633 | -0.029933 | 121.8394 | 121.7683 | 0.13527 | 0.050359 | -0.19826 | 121.8722 | 121.8159 | 122.0033 | 121.7803 | 0.014816 | 121.8405 | 121.9208 | 121.6722 | 121.8067 | -0.23738
1061.8281 | 122.0673 | -121.7468 | 0.11902 | 1.4211e-13 | -0.029181 | 0.014252 | -0.0036391 | -0.012119 | 0.019057 | -0.22533 | -0.0020702 | -0.00098076 | -0.0038435 | 0.031803 | 0.010535 | 0.074302 | 0.0243 | 0.023639 | 0.11165 | 0.055306 | 0.24727 | 0.11552 | 0.092622 | 0.036989 | 0.016908 | 0.075351 | 0.16022 | -0.12961 | -0.1321 | 121.8623 | -0.007372 | 121.8211 | 121.7705 | -0.091882 | -0.063713 | 0.12826 | 121.6147 | -0.043668 | 121.8394 | 121.7637 | 0.149 | 0.041203 | -0.24863 | 121.8585 | 121.8021 | 121.9941 | 121.7711 | -0.003498 | 121.8222 | 121.907 | 121.6172 | 121.7838 | -0.25112
1063.5156 | 121.9666 | -121.8063 | 0.13733 | 1.4211e-13 | -0.029395 | 0.01468 | -0.0036391 | -0.011905 | 0.019057 | -0.24822 | -0.0024974 | -0.0011944 | -0.0042707 | 0.03223 | 0.010108 | 0.074302 | 0.019721 | 0.032795 | 0.11165 | 0.041569 | 0.25185 | 0.11552 | 0.074307 | 0.046146 | 0.01233 | 0.075351 | 0.15564 | -0.13876 | -0.1321 | 121.9219 | -0.025682 | 121.8806 | 121.8391 | -0.082726 | -0.09576 | 0.11452 | 121.6742 | -0.061978 | 121.8806 | 121.8187 | 0.14443 | 0.018314 | -0.27609 | 121.918 | 121.8479 | 122.0582 | 121.8261 | -0.021808 | 121.8817 | 121.962 | 121.6676 | 121.8525 | -0.26943
1065.25 | 122.1176 | -121.756 | 0.10986 | 1.4211e-13 | -0.029609 | 0.014252 | -0.0038527 | -0.012333 | 0.01927 | -0.24059 | -0.0012156 | -0.00012596 | -0.0029889 | 0.032017 | 0.010535 | 0.074302 | 0.0243 | 0.032795 | 0.11622 | 0.050727 | 0.24269 | 0.11094 | 0.083464 | 0.036989 | 0.021487 | 0.07993 | 0.1648 | -0.13876 | -0.1321 | 121.8669 | 0.006362 | 121.8303 | 121.7888 | -0.078147 | -0.059136 | 0.13283 | 121.6239 | -0.029933 | 121.8394 | 121.7775 | 0.15358 | 0.054937 | -0.24863 | 121.8722 | 121.8067 | 121.9987 | 121.7803 | 0.001079 | 121.8359 | 121.9208 | 121.6172 | 121.793 | -0.24196
1066.9844 | 121.9803 | -121.788 | 0.14191 | 1.4211e-13 | -0.029609 | 0.014252 | -0.0036391 | -0.011905 | 0.01927 | -0.23296 | -0.0022838 | -0.0011944 | -0.0040571 | 0.03223 | 0.010322 | 0.07888 | 0.033457 | 0.028217 | 0.11622 | 0.050727 | 0.24727 | 0.11552 | 0.078886 | 0.041567 | 0.01233 | 0.075351 | 0.15564 | -0.12503 | -0.12294 | 121.9035 | -0.025682 | 121.8669 | 121.8162 | -0.087304 | -0.09118 | 0.10537 | 121.6651 | -0.066556 | 121.8669 | 121.8004 | 0.13527 | 0.013736 | -0.26694 | 121.9043 | 121.8388 | 122.0353 | 121.8215 | -0.026386 | 121.8634 | 121.9437 | 121.663 | 121.8296 | -0.26485
1068.6719 | 121.9894 | -121.8246 | 0.13733 | 1.4211e-13 | -0.029395 | 0.014466 | -0.0038527 | -0.011905 | 0.019057 | -0.22533 | -0.0022838 | -0.0011944 | -0.0044845 | 0.03223 | 0.010108 | 0.074302 | 0.0243 | 0.023639 | 0.11165 | 0.050727 | 0.24727 | 0.1201 | 0.083464 | 0.046146 | 0.016908 | 0.07993 | 0.15564 | -0.13876 | -0.12752 | 121.9447 | -0.025682 | 121.8989 | 121.8483 | -0.096461 | -0.086602 | 0.10994 | 121.6971 | -0.057399 | 121.9081 | 121.8416 | 0.14443 | 0.018314 | -0.27609 | 121.9363 | 121.8754 | 122.0719 | 121.8489 | -0.017229 | 121.9046 | 121.9803 | 121.6859 | 121.8708 | -0.26485
1070.4219 | 122.0444 | -121.8063 | 0.1236 | 1.4211e-13 | -0.028968 | 0.014252 | -0.0038527 | -0.011905 | 0.01927 | -0.2177 | 0.00070703 | 0.0015832 | -0.0014933 | 0.032444 | 0.010749 | 0.07888 | 0.019721 | 0.032795 | 0.1208 | 0.046148 | 0.25185 | 0.1201 | 0.074307 | 0.041567 | 0.007751 | 0.075351 | 0.16022 | -0.13419 | -0.13668 | 121.9264 | -0.002792 | 121.8852 | 121.8391 | -0.087305 | -0.077448 | 0.12826 | 121.6697 | -0.048245 | 121.8806 | 121.8141 | 0.14443 | 0.036626 | -0.25778 | 121.9271 | 121.8525 | 122.0582 | 121.8261 | -0.003496 | 121.8817 | 121.9666 | 121.6721 | 121.8479 | -0.26027
1072.1562 | 122.0764 | -121.7972 | 0.12817 | 1.4211e-13 | -0.028968 | 0.014039 | -0.0034253 | -0.012119 | 0.019057 | -0.24059 | 0.00049343 | 0.0020104 | -0.0010661 | 0.032444 | 0.010535 | 0.07888 | 0.0243 | 0.032795 | 0.11165 | 0.041569 | 0.24727 | 0.11552 | 0.069728 | 0.046146 | 0.021487 | 0.084508 | 0.1648 | -0.12503 | -0.12752 | 121.9127 | -0.016527 | 121.8761 | 121.83 | -0.082726 | -0.086605 | 0.1191 | 121.6697 | -0.043666 | 121.8669 | 121.8187 | 0.149 | 0.036626 | -0.2532 | 121.9088 | 121.8387 | 122.0445 | 121.8215 | -0.012653 | 121.8817 | 121.962 | 121.6722 | 121.8433 | -0.25569
1073.9219 | 122.0718 | -121.7651 | 0.10986 | 1.4211e-13 | -0.029395 | 0.014252 | -0.0038527 | -0.011692 | 0.018843 | -0.24059 | 0.0015616 | 0.0024378 | -0.00042513 | 0.03223 | 0.010535 | 0.07888 | 0.028878 | 0.032795 | 0.1208 | 0.050727 | 0.25185 | 0.10178 | 0.069728 | 0.046146 | 0.003172 | 0.075351 | 0.15564 | -0.13876 | -0.12752 | 121.8669 | 0.010941 | 121.844 | 121.7979 | -0.068989 | -0.059136 | 0.14199 | 121.6376 | -0.034512 | 121.8349 | 121.7683 | 0.13069 | 0.04578 | -0.24863 | 121.8859 | 121.8159 | 122.017 | 121.794 | -0.008079 | 121.8405 | 121.9208 | 121.6264 | 121.8113 | -0.23738
1075.6562 | 122.0993 | -121.7651 | 0.11902 | 1.4211e-13 | -0.029609 | 0.014252 | -0.0034253 | -0.011905 | 0.01927 | -0.24059 | 0.0017752 | 0.0026514 | -0.00021153 | 0.03223 | 0.010535 | 0.069723 | 0.019721 | 0.028217 | 0.1208 | 0.055306 | 0.24727 | 0.1201 | 0.078886 | 0.041567 | 0.007751 | 0.075351 | 0.16022 | -0.13419 | -0.12752 | 121.8852 | 0.001785 | 121.8349 | 121.7934 | -0.091883 | -0.063713 | 0.12826 | 121.6376 | -0.043668 | 121.844 | 121.7729 | 0.13527 | 0.041203 | -0.25321 | 121.8859 | 121.8204 | 122.0124 | 121.7849 | 0.001081 | 121.8405 | 121.9254 | 121.631 | 121.8067 | -0.24654
1077.3281 | 122.0764 | -121.7606 | 0.10529 | 1.4211e-13 | -0.029609 | 0.014252 | -0.0036391 | -0.011692 | 0.019484 | -0.24059 | 0.0015616 | 0.0024378 | -0.00042513 | 0.032017 | 0.0098942 | 0.074302 | 0.0243 | 0.032795 | 0.1208 | 0.055306 | 0.24269 | 0.11552 | 0.078886 | 0.03241 | 0.01233 | 0.07993 | 0.15564 | -0.13419 | -0.1321 | 121.8761 | 0.015518 | 121.8349 | 121.7934 | -0.082726 | -0.04998 | 0.13741 | 121.6285 | -0.025356 | 121.8394 | 121.7729 | 0.14443 | 0.050357 | -0.23947 | 121.8814 | 121.8159 | 122.0033 | 121.7849 | 0.010235 | 121.8405 | 121.9162 | 121.6264 | 121.793 | -0.23738
1079.0625 | 121.9849 | -121.8292 | 0.15106 | 1.4211e-13 | -0.029181 | 0.014039 | -0.0040665 | -0.012119 | 0.019698 | -0.22533 | 0.0017752 | 0.0024378 | -0.00042513 | 0.03223 | 0.010322 | 0.074302 | 0.028878 | 0.032795 | 0.11165 | 0.046148 | 0.24269 | 0.11552 | 0.074307 | 0.050725 | 0.007751 | 0.084508 | 0.15564 | -0.14334 | -0.12752 | 121.9447 | -0.039415 | 121.9035 | 121.862 | -0.082726 | -0.10491 | 0.091633 | 121.7017 | -0.066554 | 121.9035 | 121.837 | 0.13527 | 0.004581 | -0.29441 | 121.9409 | 121.8754 | 122.0719 | 121.8581 | -0.035541 | 121.9137 | 121.9849 | 121.6859 | 121.8799 | -0.27858
1080.7969 | 122.0993 | -121.7468 | 0.1236 | 1.4211e-13 | -0.029822 | 0.014466 | -0.0038527 | -0.011905 | 0.019057 | -0.24822 | 0.0015616 | 0.0026514 | -0.00021153 | 0.03223 | 0.010322 | 0.069723 | 0.033457 | 0.028217 | 0.11165 | 0.059885 | 0.25643 | 0.11552 | 0.078886 | 0.041567 | 0.003172 | 0.075351 | 0.15564 | -0.12961 | -0.12752 | 121.8623 | -0.011949 | 121.8165 | 121.775 | -0.087304 | -0.063711 | 0.13284 | 121.6193 | -0.048245 | 121.8257 | 121.75 | 0.13069 | 0.032047 | -0.2532 | 121.8585 | 121.8067 | 122.0033 | 121.7803 | -0.008075 | 121.8222 | 121.9025 | 121.6172 | 121.7884 | -0.25111
1082.4688 | 122.113 | -121.7926 | 0.12817 | 1.4211e-13 | -0.029609 | 0.01468 | -0.0038527 | -0.012333 | 0.019698 | -0.24822 | 0.00092083 | 0.0024378 | -0.00042513 | 0.032444 | 0.010322 | 0.069723 | 0.033457 | 0.032795 | 0.11165 | 0.055306 | 0.24269 | 0.11552 | 0.074307 | 0.041567 | 0.01233 | 0.07993 | 0.15107 | -0.13876 | -0.12752 | 121.9081 | -0.016527 | 121.8623 | 121.8254 | -0.082726 | -0.072868 | 0.11452 | 121.6651 | -0.048244 | 121.8669 | 121.8049 | 0.13985 | 0.022891 | -0.26694 | 121.9043 | 121.8479 | 122.0353 | 121.8261 | -0.012653 | 121.8725 | 121.9437 | 121.6538 | 121.8342 | -0.25569
1084.2188 | 121.994 | -121.8292 | 0.14648 | 1.4211e-13 | -0.029395 | 0.014252 | -0.0034253 | -0.011905 | 0.019484 | -0.23296 | 0.0017752 | 0.0030788 | 0.00021587 | 0.032444 | 0.010322 | 0.07888 | 0.033457 | 0.028217 | 0.1208 | 0.050727 | 0.25185 | 0.11094 | 0.078886 | 0.041567 | 0.01233 | 0.07993 | 0.15564 | -0.12961 | -0.14125 | 121.9402 | -0.02568 | 121.9081 | 121.8574 | -0.082725 | -0.095757 | 0.10537 | 121.688 | -0.066554 | 121.9081 | 121.8416 | 0.15358 | 0.009159 | -0.27609 | 121.95 | 121.88 | 122.0811 | 121.8627 | -0.035542 | 121.9092 | 121.9849 | 121.6996 | 121.8708 | -0.28774
1085.9531 | 121.9757 | -121.7926 | 0.13733 | 1.4211e-13 | -0.029822 | 0.01468 | -0.0038527 | -0.011905 | 0.01927 | -0.24059 | 0.0017752 | 0.0032924 | 2.074e-06 | 0.032017 | 0.010322 | 0.07888 | 0.028878 | 0.023639 | 0.1208 | 0.055306 | 0.25185 | 0.11552 | 0.074307 | 0.036989 | 0.007751 | 0.07993 | 0.16022 | -0.13876 | -0.12752 | 121.9081 | -0.016525 | 121.8715 | 121.8162 | -0.091882 | -0.082023 | 0.11452 | 121.6651 | -0.057399 | 121.8669 | 121.8004 | 0.13527 | 0.022893 | -0.27609 | 121.9134 | 121.8479 | 122.0445 | 121.8215 | -0.021808 | 121.8725 | 121.9528 | 121.6538 | 121.8296 | -0.26485
1087.625 | 122.0352 | -121.8063 | 0.13733 | 1.4211e-13 | -0.029609 | 0.014466 | -0.0036391 | -0.011692 | 0.019057 | -0.24059 | 0.0017752 | 0.0035062 | 2.074e-06 | 0.032017 | 0.010322 | 0.074302 | 0.028878 | 0.028217 | 0.10707 | 0.050727 | 0.25185 | 0.11552 | 0.078886 | 0.041567 | 0.007751 | 0.075351 | 0.15564 | -0.13876 | -0.1321 | 121.9219 | -0.030261 | 121.8806 | 121.8346 | -0.087304 | -0.086602 | 0.11452 | 121.6742 | -0.061978 | 121.8852 | 121.8141 | 0.13985 | 0.018314 | -0.27609 | 121.9134 | 121.8571 | 122.0582 | 121.8352 | -0.021808 | 121.8817 | 121.962 | 121.6676 | 121.8479 | -0.26943
1089.375 | 122.0993 | -121.7926 | 0.10071 | 1.4211e-13 | -0.029395 | 0.014252 | -0.0038527 | -0.012333 | 0.019484 | -0.23296 | 0.0017752 | 0.0028652 | 2.074e-06 | 0.032444 | 0.010322 | 0.069723 | 0.033457 | 0.028217 | 0.11622 | 0.055306 | 0.24727 | 0.11552 | 0.074307 | 0.046146 | -0.001407 | 0.07993 | 0.15564 | -0.13419 | -0.1321 | 121.9081 | 0.015517 | 121.8623 | 121.8208 | -0.087304 | -0.045402 | 0.14657 | 121.6605 | -0.020778 | 121.8669 | 121.7912 | 0.13069 | 0.054935 | -0.23489 | 121.9088 | 121.8479 | 122.0399 | 121.8261 | 0.014813 | 121.8725 | 121.9482 | 121.6584 | 121.8387 | -0.2328
1091.1094 | 122.0444 | -121.8155 | 0.13275 | 1.4211e-13 | -0.029395 | 0.014252 | -0.0034253 | -0.011905 | 0.01927 | -0.24059 | 0.0015616 | 0.0026514 | 2.074e-06 | 0.032444 | 0.010322 | 0.074302 | 0.028878 | 0.028217 | 0.1208 | 0.055306 | 0.25185 | 0.1201 | 0.078886 | 0.041567 | 0.01233 | 0.075351 | 0.15564 | -0.13419 | -0.12752 | 121.9356 | -0.011947 | 121.8898 | 121.8437 | -0.091883 | -0.077445 | 0.1191 | 121.688 | -0.0574 | 121.8944 | 121.8278 | 0.13985 | 0.022892 | -0.26694 | 121.9363 | 121.8708 | 122.0673 | 121.8444 | -0.012651 | 121.8908 | 121.9711 | 121.6813 | 121.8571 | -0.26027
1092.8594 | 122.0718 | -121.8109 | 0.11902 | 1.4211e-13 | -0.029395 | 0.014466 | -0.0036391 | -0.012119 | 0.01927 | -0.22533 | 0.0015616 | 0.0024378 | -0.00042513 | 0.032444 | 0.010322 | 0.069723 | 0.033457 | 0.01906 | 0.12538 | 0.050727 | 0.25185 | 0.10178 | 0.069728 | 0.036989 | 0.007751 | 0.075351 | 0.16022 | -0.13419 | -0.12752 | 121.9127 | 0.006363 | 121.8806 | 121.83 | -0.082724 | -0.068292 | 0.13283 | 121.6834 | -0.043668 | 121.8806 | 121.8187 | 0.13527 | 0.041203 | -0.25321 | 121.9363 | 121.8616 | 122.0628 | 121.8444 | -0.017235 | 121.8863 | 121.9711 | 121.6767 | 121.8479 | -0.24654
1094.5469 | 121.9894 | -121.8155 | 0.11444 | 1.4211e-13 | -0.029395 | 0.014252 | -0.0036391 | -0.011905 | 0.01927 | -0.23296 | 0.0015616 | 0.0030788 | -0.00021153 | 0.03223 | 0.010322 | 0.07888 | 0.028878 | 0.023639 | 0.11622 | 0.046148 | 0.24727 | 0.065153 | 0.074307 | 0.041567 | 0.007751 | 0.07993 | 0.15564 | -0.12961 | -0.14125 | 121.8806 | 0.001784 | 121.8944 | 121.8391 | -0.041514 | -0.068293 | 0.13283 | 121.6742 | -0.034511 | 121.8898 | 121.8232 | 0.14901 | 0.041202 | -0.24405 | 121.9317 | 121.8616 | 122.0628 | 121.8444 | -0.049288 | 121.8954 | 121.9711 | 121.6859 | 121.8571 | -0.2557
1096.2812 | 122.0123 | -121.8292 | 0.1236 | 1.4211e-13 | -0.029395 | 0.014466 | -0.0038527 | -0.011905 | 0.01927 | -0.22533 | 0.001348 | 0.0026514 | -0.00063873 | 0.032444 | 0.010108 | 0.07888 | 0.0243 | 0.023639 | 0.11165 | 0.050727 | 0.24727 | 0.11094 | 0.074307 | 0.041567 | 0.003172 | 0.07993 | 0.15107 | -0.13419 | -0.12752 | 121.9402 | -0.011949 | 121.9081 | 121.8529 | -0.087303 | -0.072869 | 0.12368 | 121.7017 | -0.043666 | 121.9035 | 121.8324 | 0.13069 | 0.027469 | -0.25778 | 121.9409 | 121.88 | 122.0765 | 121.8535 | -0.012654 | 121.9092 | 121.9803 | 121.695 | 121.8708 | -0.25111
1098.0156 | 122.081 | -121.8201 | 0.11902 | 1.4211e-13 | -0.029609 | 0.014252 | -0.0038527 | -0.011905 | 0.019057 | -0.24059 | 0.001348 | 0.0024378 | -0.00021153 | 0.03223 | 0.010108 | 0.07888 | 0.028878 | 0.023639 | 0.11165 | 0.055306 | 0.24727 | 0.1201 | 0.078886 | 0.036989 | -0.001407 | 0.075351 | 0.14649 | -0.12961 | -0.13668 | 121.9402 | -0.007372 | 121.8989 | 121.8437 | -0.096461 | -0.063713 | 0.12826 | 121.6834 | -0.043668 | 121.899 | 121.8187 | 0.13527 | 0.027467 | -0.24863 | 121.9317 | 121.8754 | 122.0673 | 121.8489 | 0.001081 | 121.8954 | 121.9666 | 121.6905 | 121.8571 | -0.2557
1099.75 | 121.9711 | -121.8384 | 0.15106 | 1.4211e-13 | -0.029609 | 0.014252 | -0.0036391 | -0.012333 | 0.019057 | -0.24059 | 0.001348 | 0.0028652 | -0.00042513 | 0.03223 | 0.010322 | 0.07888 | 0.019721 | 0.028217 | 0.11165 | 0.050727 | 0.25643 | 0.11552 | 0.069728 | 0.041567 | 0.007751 | 0.070773 | 0.15564 | -0.13419 | -0.13668 | 121.9539 | -0.039415 | 121.9173 | 121.8666 | -0.087304 | -0.10034 | 0.10537 | 121.7017 | -0.080289 | 121.9081 | 121.8461 | 0.14443 | 0.004581 | -0.28525 | 121.95 | 121.8891 | 122.0948 | 121.8581 | -0.035541 | 121.9092 | 121.994 | 121.7042 | 121.8799 | -0.28774
1101.5 | 121.7239 | -121.5134 | 0.13733 | 1.4211e-13 | -0.029609 | 0.014252 | -0.0036391 | -0.012119 | 0.019484 | -0.23296 | 0.0011344 | 0.0024378 | -0.00021153 | 0.032658 | 0.010535 | 0.07888 | 0.0243 | 0.028217 | 0.11622 | 0.055306 | 0.25185 | 0.11552 | 0.06515 | 0.03241 | 0.007751 | 0.075351 | 0.16022 | -0.13876 | -0.12752 | 121.6289 | -0.021104 | 121.5922 | 121.5416 | -0.087304 | -0.082023 | 0.11452 | 121.3858 | -0.061978 | 121.5785 | 121.5211 | 0.13527 | 0.022893 | -0.27609 | 121.6296 | 121.5687 | 121.7652 | 121.5377 | -0.021808 | 121.5887 | 121.6736 | 121.3746 | 121.5458 | -0.26485
1103.1719 | 121.9208 | -121.5912 | 0.09613 | 1.4211e-13 | -0.029395 | 0.014466 | -0.0034253 | -0.011905 | 0.018843 | -0.24059 | 0.0011344 | 0.0022242 | -0.00063873 | 0.032444 | 0.010322 | 0.074302 | 0.0243 | 0.023639 | 0.11165 | 0.050727 | 0.25185 | 0.11094 | 0.074307 | 0.036989 | 0.01233 | 0.07993 | 0.16022 | -0.13876 | -0.13668 | 121.7021 | 0.015517 | 121.6655 | 121.6148 | -0.087303 | -0.045403 | 0.15572 | 121.4545 | -0.0162 | 121.6655 | 121.6035 | 0.14901 | 0.064092 | -0.23489 | 121.7028 | 121.6419 | 121.843 | 121.6155 | 0.014812 | 121.6711 | 121.7514 | 121.4524 | 121.6282 | -0.23281
1104.9375 | 121.8842 | -121.6827 | 0.13733 | 1.4211e-13 | -0.029395 | 0.014252 | -0.0036391 | -0.012119 | 0.019057 | -0.23296 | 0.00092083 | 0.0017968 | -0.0014933 | 0.032444 | 0.010535 | 0.074302 | 0.0243 | 0.023639 | 0.11165 | 0.055306 | 0.24727 | 0.11552 | 0.069728 | 0.041567 | 0.01233 | 0.07993 | 0.15564 | -0.12503 | -0.12752 | 121.7983 | -0.025682 | 121.757 | 121.7064 | -0.091882 | -0.082023 | 0.10994 | 121.5552 | -0.057399 | 121.7525 | 121.6951 | 0.13985 | 0.018314 | -0.26236 | 121.7944 | 121.738 | 121.93 | 121.707 | -0.021808 | 121.7627 | 121.8384 | 121.5577 | 121.7243 | -0.26485
1106.6719 | 121.8475 | -121.7102 | 0.13275 | 1.4211e-13 | -0.029395 | 0.014466 | -0.0038527 | -0.011905 | 0.019057 | -0.24059 | -0.00078837 | 8.7636e-05 | -0.0032025 | 0.03223 | 0.010108 | 0.074302 | 0.028878 | 0.028217 | 0.11165 | 0.055306 | 0.24727 | 0.11094 | 0.078886 | 0.046146 | -0.001407 | 0.07993 | 0.15107 | -0.13876 | -0.1321 | 121.8211 | -0.021104 | 121.7845 | 121.7384 | -0.082725 | -0.077445 | 0.11452 | 121.5781 | -0.052821 | 121.7891 | 121.7088 | 0.13069 | 0.018314 | -0.27152 | 121.8219 | 121.7655 | 121.9575 | 121.7391 | -0.021809 | 121.7901 | 121.8613 | 121.5714 | 121.7564 | -0.26485
1108.3438 | 121.8704 | -121.6736 | 0.13733 | 1.4211e-13 | -0.029609 | 0.01468 | -0.0036391 | -0.012119 | 0.01927 | -0.22533 | -0.00057477 | 0.00051484 | -0.0023479 | 0.032017 | 0.010322 | 0.07888 | 0.0243 | 0.028217 | 0.11622 | 0.046148 | 0.24727 | 0.1201 | 0.074307 | 0.046146 | 0.007751 | 0.07993 | 0.16022 | -0.13876 | -0.1321 | 121.7937 | -0.021104 | 121.7525 | 121.7018 | -0.091883 | -0.091181 | 0.10994 | 121.5415 | -0.057399 | 121.7479 | 121.6813 | 0.13985 | 0.022893 | -0.27609 | 121.7898 | 121.7197 | 121.9209 | 121.6979 | -0.017229 | 121.7535 | 121.8338 | 121.5348 | 121.7197 | -0.26943
1110.0938 | 121.9437 | -121.6736 | 0.13275 | 1.4211e-13 | -0.029395 | 0.014466 | -0.0036391 | -0.011905 | 0.01927 | -0.23296 | -0.0014292 | -0.00055336 | -0.0034163 | 0.032444 | 0.0098942 | 0.074302 | 0.0243 | 0.032795 | 0.11165 | 0.055306 | 0.24269 | 0.11552 | 0.078886 | 0.046146 | 0.01233 | 0.075351 | 0.15107 | -0.13419 | -0.13668 | 121.7891 | -0.021104 | 121.7479 | 121.7064 | -0.082726 | -0.077445 | 0.10994 | 121.5369 | -0.0574 | 121.7525 | 121.6859 | 0.14901 | 0.018314 | -0.26694 | 121.7852 | 121.7289 | 121.9163 | 121.6979 | -0.01723 | 121.7489 | 121.8246 | 121.5394 | 121.7197 | -0.26943
1111.8281 | 122.0169 | -121.6507 | 0.09613 | 1.4211e-13 | -0.029609 | 0.014252 | -0.0038527 | -0.012119 | 0.019057 | -0.22533 | -0.0014292 | -0.00033976 | -0.0034163 | 0.032658 | 0.010322 | 0.074302 | 0.015142 | 0.028217 | 0.11165 | 0.055306 | 0.25185 | 0.11552 | 0.074307 | 0.036989 | 0.007751 | 0.07993 | 0.1648 | -0.13419 | -0.12752 | 121.7662 | 0.015517 | 121.725 | 121.6789 | -0.087304 | -0.040824 | 0.15572 | 121.5232 | -0.0162 | 121.725 | 121.6584 | 0.13527 | 0.06867 | -0.23032 | 121.7623 | 121.706 | 121.9025 | 121.6658 | 0.019391 | 121.7306 | 121.8155 | 121.5165 | 121.6877 | -0.22365
1113.5156 | 121.875 | -121.7102 | 0.13733 | 1.4211e-13 | -0.029609 | 0.013825 | -0.0040665 | -0.011905 | 0.019057 | -0.24059 | -0.001643 | -0.00033976 | -0.0034163 | 0.032658 | 0.010535 | 0.074302 | 0.019721 | 0.023639 | 0.11165 | 0.055306 | 0.24727 | 0.11094 | 0.069728 | 0.03241 | 0.007751 | 0.075351 | 0.16022 | -0.13419 | -0.1321 | 121.8211 | -0.025682 | 121.7845 | 121.7338 | -0.087303 | -0.082023 | 0.10994 | 121.5781 | -0.061978 | 121.7799 | 121.718 | 0.13985 | 0.022893 | -0.27152 | 121.8219 | 121.7655 | 121.9575 | 121.7299 | -0.026387 | 121.7856 | 121.8704 | 121.576 | 121.7426 | -0.26943
1115.2656 | 122.0261 | -121.6553 | 0.10986 | 1.4211e-13 | -0.029395 | 0.014252 | -0.0036391 | -0.011905 | 0.01927 | -0.24822 | -0.0014292 | -0.00076696 | -0.0038435 | 0.032871 | 0.010322 | 0.069723 | 0.028878 | 0.028217 | 0.11165 | 0.055306 | 0.24727 | 0.12468 | 0.074307 | 0.041567 | 0.01233 | 0.075351 | 0.16022 | -0.13876 | -0.1321 | 121.78 | 0.001784 | 121.725 | 121.6835 | -0.096462 | -0.054557 | 0.13741 | 121.5232 | -0.034512 | 121.7296 | 121.6676 | 0.14443 | 0.050359 | -0.24863 | 121.7669 | 121.7106 | 121.9025 | 121.6842 | 0.014816 | 121.7306 | 121.8155 | 121.5165 | 121.6968 | -0.24196
1117 | 121.9482 | -121.6827 | 0.11902 | 1.4211e-13 | -0.029822 | 0.014252 | -0.0038527 | -0.012333 | 0.019484 | -0.23296 | -0.0018566 | -0.00076696 | -0.0036299 | 0.032017 | 0.010322 | 0.07888 | 0.019721 | 0.023639 | 0.11622 | 0.059885 | 0.25643 | 0.11552 | 0.074307 | 0.041567 | 0.007751 | 0.075351 | 0.16022 | -0.13419 | -0.12752 | 121.7983 | -0.002794 | 121.7616 | 121.7064 | -0.091882 | -0.059134 | 0.13741 | 121.5552 | -0.043668 | 121.757 | 121.6905 | 0.13527 | 0.041203 | -0.25321 | 121.799 | 121.7426 | 121.9392 | 121.7025 | -0.003498 | 121.7581 | 121.843 | 121.5486 | 121.7243 | -0.24654
1118.6875 | 122.0215 | -121.6553 | 0.11444 | 1.4211e-13 | -0.029609 | 0.014252 | -0.0036391 | -0.012119 | 0.019057 | -0.22533 | -0.001643 | -0.00076696 | -0.0038435 | 0.033085 | 0.010322 | 0.07888 | 0.019721 | 0.028217 | 0.10707 | 0.059885 | 0.23812 | 0.11552 | 0.074307 | 0.036989 | 0.01233 | 0.084508 | 0.16022 | -0.11587 | -0.12752 | 121.7708 | -0.007373 | 121.7342 | 121.6835 | -0.087304 | -0.054556 | 0.12368 | 121.5278 | -0.029933 | 121.7296 | 121.6676 | 0.13985 | 0.045781 | -0.23031 | 121.7623 | 121.7152 | 121.8934 | 121.675 | 0.00108 | 121.7398 | 121.8155 | 121.5394 | 121.6923 | -0.24196
1120.4531 | 121.9208 | -121.6919 | 0.12817 | 1.4211e-13 | -0.029609 | 0.014039 | -0.0036391 | -0.012119 | 0.019057 | -0.23296 | -0.0018566 | -0.00098076 | -0.0040571 | 0.032658 | 0.010535 | 0.07888 | 0.0243 | 0.023639 | 0.11165 | 0.046148 | 0.24727 | 0.10636 | 0.069728 | 0.041567 | 0.01233 | 0.084508 | 0.16022 | -0.10214 | -0.1321 | 121.7983 | -0.016527 | 121.7708 | 121.7155 | -0.082724 | -0.082026 | 0.1191 | 121.5598 | -0.043666 | 121.7616 | 121.7042 | 0.14443 | 0.032048 | -0.23031 | 121.8035 | 121.738 | 121.9392 | 121.7162 | -0.021811 | 121.7764 | 121.8521 | 121.5898 | 121.7335 | -0.26027
1122.125 | 121.9528 | -121.7056 | 0.11902 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0034253 | -0.012119 | 0.01927 | -0.24059 | -0.0018566 | -0.00055336 | -0.0038435 | 0.032444 | 0.010108 | 0.069723 | 0.019721 | 0.028217 | 0.11622 | 0.055306 | 0.24727 | 0.11094 | 0.074307 | 0.041567 | 0.007751 | 0.075351 | 0.16022 | -0.13419 | -0.1321 | 121.8166 | -0.002794 | 121.7754 | 121.7338 | -0.082725 | -0.063713 | 0.12826 | 121.5735 | -0.043668 | 121.7799 | 121.7134 | 0.13985 | 0.041203 | -0.25321 | 121.8219 | 121.7609 | 121.9529 | 121.7253 | -0.008077 | 121.781 | 121.8658 | 121.5714 | 121.7472 | -0.25112
1123.875 | 121.9757 | -121.7056 | 0.10986 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0038527 | -0.012333 | 0.01927 | -0.24059 | -0.0018566 | -0.00033976 | -0.0036299 | 0.03223 | 0.010322 | 0.069723 | 0.028878 | 0.028217 | 0.11622 | 0.055306 | 0.24269 | 0.11094 | 0.074307 | 0.041567 | 0.01233 | 0.07993 | 0.15107 | -0.13419 | -0.1321 | 121.8166 | 0.006362 | 121.7754 | 121.7338 | -0.082725 | -0.054557 | 0.13283 | 121.5735 | -0.029933 | 121.7799 | 121.718 | 0.14443 | 0.041202 | -0.24405 | 121.8219 | 121.7609 | 121.9483 | 121.7345 | 0.001079 | 121.7856 | 121.8567 | 121.5714 | 121.7472 | -0.24196
1125.625 | 121.9666 | -121.6965 | 0.11902 | 1.4211e-13 | -0.029609 | 0.014039 | -0.0034253 | -0.012546 | 0.01927 | -0.23296 | -0.0018566 | -0.0016216 | -0.0044845 | 0.032658 | 0.010322 | 0.074302 | 0.0243 | 0.01906 | 0.1208 | 0.055306 | 0.25185 | 0.11094 | 0.074307 | 0.036989 | 0.003172 | 0.070773 | 0.15107 | -0.10671 | -0.12752 | 121.8074 | 0.001785 | 121.7708 | 121.7155 | -0.091882 | -0.063713 | 0.13283 | 121.569 | -0.048246 | 121.7708 | 121.6996 | 0.13069 | 0.032046 | -0.22573 | 121.8173 | 121.7518 | 121.9483 | 121.7208 | -0.008077 | 121.7672 | 121.8475 | 121.5898 | 121.7335 | -0.24654
1127.2969 | 121.8933 | -121.7377 | 0.13275 | 1.4211e-13 | -0.029609 | 0.014466 | -0.0038527 | -0.012119 | 0.019057 | -0.23296 | -0.0018566 | -0.00098076 | -0.0038435 | 0.032658 | 0.010535 | 0.07888 | 0.0243 | 0.028217 | 0.1208 | 0.046148 | 0.24269 | 0.11552 | 0.078886 | 0.046146 | 0.01233 | 0.075351 | 0.15564 | -0.12503 | -0.12752 | 121.8532 | -0.011947 | 121.8166 | 121.7659 | -0.087304 | -0.086603 | 0.10994 | 121.6102 | -0.0574 | 121.8166 | 121.75 | 0.13985 | 0.022892 | -0.25778 | 121.8585 | 121.7838 | 121.9804 | 121.762 | -0.01723 | 121.813 | 121.8933 | 121.6126 | 121.7838 | -0.26027
1129.0469 | 121.9162 | -121.7331 | 0.14191 | 1.4211e-13 | -0.029822 | 0.014466 | -0.0038527 | -0.012546 | 0.019057 | -0.23296 | -0.001643 | -0.00033976 | -0.0034163 | 0.03223 | 0.010108 | 0.065145 | 0.028878 | 0.028217 | 0.10707 | 0.050727 | 0.24269 | 0.1201 | 0.074307 | 0.041567 | 0.003172 | 0.07993 | 0.15564 | -0.12961 | -0.12752 | 121.8532 | -0.034839 | 121.7982 | 121.7613 | -0.091883 | -0.09118 | 0.10079 | 121.6056 | -0.061977 | 121.8074 | 121.7363 | 0.13069 | 0.013736 | -0.27151 | 121.8402 | 121.7838 | 121.9758 | 121.762 | -0.021807 | 121.813 | 121.8887 | 121.6035 | 121.7747 | -0.26943
1130.7969 | 122.0169 | -121.6919 | 0.11902 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0036391 | -0.012333 | 0.01927 | -0.23296 | -0.001002 | -0.00076696 | -0.0036299 | 0.032658 | 0.010108 | 0.074302 | 0.019721 | 0.023639 | 0.1208 | 0.055306 | 0.24727 | 0.11094 | 0.074307 | 0.050725 | 0.01233 | 0.075351 | 0.15564 | -0.12961 | -0.1321 | 121.8028 | 0.001785 | 121.7662 | 121.7155 | -0.087303 | -0.063713 | 0.12826 | 121.5598 | -0.043668 | 121.7662 | 121.7042 | 0.14443 | 0.036624 | -0.24863 | 121.8127 | 121.7472 | 121.9392 | 121.7116 | -0.008077 | 121.7672 | 121.8475 | 121.5623 | 121.7426 | -0.25112
1132.5312 | 121.9574 | -121.7239 | 0.1236 | 1.4211e-13 | -0.029609 | 0.014252 | -0.0034253 | -0.012119 | 0.019057 | -0.22533 | -0.0014292 | -0.00033976 | -0.0034163 | 0.03223 | 0.0098942 | 0.074302 | 0.0243 | 0.028217 | 0.11165 | 0.055306 | 0.25185 | 0.1201 | 0.083464 | 0.036989 | 0.007751 | 0.07993 | 0.15107 | -0.12503 | -0.1321 | 121.844 | -0.011949 | 121.7982 | 121.7522 | -0.091883 | -0.06829 | 0.12826 | 121.5918 | -0.043666 | 121.8074 | 121.7317 | 0.13985 | 0.027469 | -0.24862 | 121.8356 | 121.7792 | 121.9758 | 121.7482 | -0.003496 | 121.8039 | 121.875 | 121.5989 | 121.7609 | -0.25569
1134.2031 | 122.0352 | -121.6919 | 0.10529 | 1.4211e-13 | -0.030036 | 0.014039 | -0.0036391 | -0.012119 | 0.018843 | -0.22533 | -0.0014292 | -0.00012596 | -0.0032025 | 0.032444 | 0.010322 | 0.074302 | 0.019721 | 0.023639 | 0.11622 | 0.03699 | 0.25185 | 0.1201 | 0.078886 | 0.041567 | 0.007751 | 0.07993 | 0.15107 | -0.12961 | -0.12752 | 121.812 | 0.010939 | 121.7662 | 121.7155 | -0.096461 | -0.068296 | 0.14657 | 121.5644 | -0.025356 | 121.7708 | 121.6996 | 0.13527 | 0.045779 | -0.23489 | 121.8081 | 121.7289 | 121.9437 | 121.7116 | 0.014814 | 121.7718 | 121.843 | 121.5623 | 121.7335 | -0.2328
1135.9531 | 121.9116 | -121.7377 | 0.14191 | 1.4211e-13 | -0.029609 | 0.014039 | -0.0034253 | -0.012333 | 0.018843 | -0.23296 | -0.0012156 | -0.00012596 | -0.0034163 | 0.032871 | 0.010322 | 0.07888 | 0.0243 | 0.01906 | 0.1208 | 0.050727 | 0.25185 | 0.11094 | 0.069728 | 0.036989 | 0.01233 | 0.07993 | 0.16022 | -0.13419 | -0.13668 | 121.8486 | -0.021103 | 121.8166 | 121.7567 | -0.091882 | -0.09118 | 0.10995 | 121.601 | -0.061977 | 121.8074 | 121.75 | 0.14901 | 0.018315 | -0.27609 | 121.8585 | 121.7884 | 121.9895 | 121.762 | -0.030965 | 121.8176 | 121.8979 | 121.6035 | 121.7747 | -0.27858
1137.7031 | 122.0123 | -121.7194 | 0.11902 | 1.4211e-13 | -0.029609 | 0.013825 | -0.0038527 | -0.012119 | 0.019057 | -0.22533 | -0.0014292 | -0.00055336 | -0.0029889 | 0.032658 | 0.010322 | 0.074302 | 0.019721 | 0.023639 | 0.11622 | 0.050727 | 0.25185 | 0.12468 | 0.074307 | 0.036989 | 0.01233 | 0.075351 | 0.15107 | -0.11129 | -0.12752 | 121.844 | -0.002794 | 121.7937 | 121.743 | -0.10104 | -0.068292 | 0.13283 | 121.5918 | -0.043668 | 121.7937 | 121.7317 | 0.13985 | 0.032046 | -0.23031 | 121.8356 | 121.7701 | 121.9712 | 121.7391 | 0.00566 | 121.7947 | 121.8704 | 121.6081 | 121.7563 | -0.24654
1139.3906 | 122.0032 | -121.7056 | 0.1236 | 1.4211e-13 | -0.029609 | 0.014039 | -0.0036391 | -0.012333 | 0.019057 | -0.24059 | -0.001002 | -0.00033976 | -0.0032025 | 0.032871 | 0.0098942 | 0.07888 | 0.015142 | 0.028217 | 0.1208 | 0.055306 | 0.25185 | 0.11094 | 0.083464 | 0.041567 | 0.003172 | 0.084508 | 0.15107 | -0.13419 | -0.1321 | 121.8166 | -0.002792 | 121.7845 | 121.7338 | -0.082725 | -0.06829 | 0.12826 | 121.5735 | -0.039088 | 121.7891 | 121.7088 | 0.13527 | 0.027469 | -0.25778 | 121.8264 | 121.7609 | 121.9575 | 121.7208 | -0.012654 | 121.7901 | 121.8567 | 121.5714 | 121.7472 | -0.25569
1141.0625 | 121.9437 | -121.7285 | 0.13275 | 1.4211e-13 | -0.029609 | 0.014039 | -0.0036391 | -0.011905 | 0.018843 | -0.24822 | -0.0012156 | 8.7636e-05 | -0.0032025 | 0.032871 | 0.010535 | 0.07888 | 0.028878 | 0.023639 | 0.11622 | 0.050727 | 0.25643 | 0.11094 | 0.074307 | 0.041567 | 0.01233 | 0.070773 | 0.15107 | -0.11587 | -0.1321 | 121.8395 | -0.016526 | 121.8074 | 121.7522 | -0.087303 | -0.082024 | 0.12368 | 121.5964 | -0.061978 | 121.8028 | 121.7408 | 0.14443 | 0.018314 | -0.24862 | 121.8447 | 121.7792 | 121.9849 | 121.7574 | -0.021809 | 121.7993 | 121.8796 | 121.6126 | 121.7701 | -0.26485
1142.8125 | 122.0032 | -121.7285 | 0.1236 | 1.4211e-13 | -0.029609 | 0.014039 | -0.0036391 | -0.012119 | 0.01927 | -0.24059 | -0.0014292 | 8.7636e-05 | -0.0032025 | 0.032444 | 0.010535 | 0.074302 | 0.019721 | 0.01906 | 0.10707 | 0.059885 | 0.25185 | 0.12468 | 0.06515 | 0.036989 | 0.003172 | 0.075351 | 0.15564 | -0.092979 | -0.12752 | 121.8532 | -0.016528 | 121.8028 | 121.7476 | -0.10562 | -0.063711 | 0.12826 | 121.601 | -0.048245 | 121.7937 | 121.7317 | 0.13069 | 0.032047 | -0.21658 | 121.8356 | 121.7884 | 121.9804 | 121.7482 | 0.001083 | 121.8039 | 121.8842 | 121.6355 | 121.7655 | -0.25111
1144.5625 | 121.9574 | -121.7514 | 0.1236 | 1.4211e-13 | -0.029609 | 0.014039 | -0.0036391 | -0.012333 | 0.019057 | -0.24822 | -0.0012156 | -0.00076696 | -0.0034163 | 0.032658 | 0.010108 | 0.069723 | 0.0243 | 0.028217 | 0.11622 | 0.050727 | 0.25185 | 0.11552 | 0.078886 | 0.036989 | 0.01233 | 0.084508 | 0.1648 | -0.12961 | -0.12752 | 121.8669 | -0.007371 | 121.8211 | 121.7796 | -0.087304 | -0.072869 | 0.12826 | 121.6239 | -0.039088 | 121.8303 | 121.7637 | 0.13985 | 0.041204 | -0.2532 | 121.8676 | 121.8021 | 122.0033 | 121.7757 | -0.008075 | 121.8359 | 121.9162 | 121.6218 | 121.7884 | -0.25111
1146.25 | 121.9894 | -121.7194 | 0.10529 | 1.4211e-13 | -0.029609 | 0.014039 | -0.0038527 | -0.011692 | 0.01927 | -0.24059 | -0.001643 | -0.00012596 | -0.0032025 | 0.032658 | 0.010322 | 0.069723 | 0.028878 | 0.028217 | 0.11622 | 0.059885 | 0.25643 | 0.1201 | 0.078886 | 0.041567 | 0.01233 | 0.07993 | 0.15564 | -0.11587 | -0.1321 | 121.8395 | 0.010939 | 121.7891 | 121.7476 | -0.091883 | -0.045401 | 0.15115 | 121.5873 | -0.025356 | 121.7982 | 121.7317 | 0.14443 | 0.050357 | -0.22116 | 121.8356 | 121.7792 | 121.9758 | 121.7482 | 0.014814 | 121.7993 | 121.875 | 121.6035 | 121.7609 | -0.23738
1147.9844 | 121.907 | -121.7514 | 0.15564 | 1.4211e-13 | -0.029609 | 0.014039 | -0.0038527 | -0.012119 | 0.018843 | -0.22533 | -0.001643 | -0.00033976 | -0.0034163 | 0.032658 | 0.010322 | 0.074302 | 0.0243 | 0.01906 | 0.11165 | 0.050727 | 0.25185 | 0.11094 | 0.078886 | 0.041567 | 0.021487 | 0.075351 | 0.15107 | -0.12503 | -0.1321 | 121.8623 | -0.043993 | 121.8257 | 121.7705 | -0.091882 | -0.10491 | 0.096212 | 121.6193 | -0.080289 | 121.8303 | 121.7729 | 0.15358 | -0.004575 | -0.28067 | 121.8631 | 121.8021 | 122.0033 | 121.7757 | -0.044698 | 121.8268 | 121.9025 | 121.6264 | 121.793 | -0.28774
1149.7344 | 122.049 | -121.7056 | 0.10986 | 1.4211e-13 | -0.029609 | 0.014252 | -0.0036391 | -0.012333 | 0.018843 | -0.23296 | -0.0018566 | -0.00033976 | -0.0034163 | 0.032658 | 0.010322 | 0.07888 | 0.019721 | 0.023639 | 0.11165 | 0.046148 | 0.25185 | 0.1201 | 0.074307 | 0.03241 | 0.007751 | 0.07993 | 0.16022 | -0.12961 | -0.1321 | 121.8257 | 0.001784 | 121.7845 | 121.7293 | -0.096461 | -0.063715 | 0.14199 | 121.5735 | -0.029933 | 121.7799 | 121.7134 | 0.13985 | 0.050359 | -0.23947 | 121.8173 | 121.7518 | 121.9575 | 121.7253 | 0.010237 | 121.7856 | 121.8658 | 121.576 | 121.738 | -0.24196
1151.4219 | 122.0673 | -121.6965 | 0.10529 | 1.4211e-13 | -0.029609 | 0.013825 | -0.0036391 | -0.012546 | 0.019057 | -0.22533 | -0.0020702 | -0.00055336 | -0.0040571 | 0.032658 | 0.010322 | 0.07888 | 0.019721 | 0.01906 | 0.11165 | 0.055306 | 0.24727 | 0.1201 | 0.078886 | 0.041567 | 0.007751 | 0.084508 | 0.1648 | -0.13419 | -0.1321 | 121.8166 | 0.006361 | 121.7754 | 121.7155 | -0.10104 | -0.04998 | 0.14199 | 121.5644 | -0.020778 | 121.7754 | 121.7042 | 0.13985 | 0.059514 | -0.23947 | 121.8081 | 121.7518 | 121.9437 | 121.7162 | 0.014814 | 121.781 | 121.8613 | 121.5623 | 121.738 | -0.23738
1153.0938 | 121.9208 | -121.7651 | 0.15106 | 1.4211e-13 | -0.029609 | 0.014039 | -0.0036391 | -0.012546 | 0.019057 | -0.22533 | -0.0014292 | -0.00033976 | -0.0034163 | 0.032658 | 0.010108 | 0.07888 | 0.0243 | 0.032795 | 0.11622 | 0.055306 | 0.25643 | 0.10178 | 0.083464 | 0.036989 | 0.01233 | 0.07993 | 0.15564 | -0.13419 | -0.13668 | 121.8669 | -0.034837 | 121.844 | 121.7979 | -0.068989 | -0.095756 | 0.10537 | 121.6285 | -0.071132 | 121.8486 | 121.7775 | 0.14901 | 0.004581 | -0.28525 | 121.8814 | 121.8204 | 122.0216 | 121.7894 | -0.049278 | 121.8451 | 121.9208 | 121.631 | 121.8021 | -0.28774
1154.8438 | 122.0261 | -121.7102 | 0.10986 | 1.4211e-13 | -0.029822 | 0.014466 | -0.0038527 | -0.012333 | 0.019057 | -0.24059 | -0.0018566 | -0.00033976 | -0.0036299 | 0.032871 | 0.010322 | 0.069723 | 0.019721 | 0.028217 | 0.11622 | 0.059885 | 0.25185 | 0.11552 | 0.074307 | 0.036989 | 0.016908 | 0.07993 | 0.15107 | -0.12961 | -0.12294 | 121.8257 | 0.006362 | 121.7799 | 121.7384 | -0.087304 | -0.049978 | 0.14199 | 121.5873 | -0.029933 | 121.7845 | 121.7271 | 0.13985 | 0.041202 | -0.23947 | 121.8264 | 121.7701 | 121.9621 | 121.7299 | 0.005658 | 121.7901 | 121.8613 | 121.5806 | 121.7472 | -0.2328
1156.5938 | 121.9025 | -121.7743 | 0.12817 | 1.4211e-13 | -0.029822 | 0.014466 | -0.0036391 | -0.012546 | 0.019484 | -0.22533 | -0.001643 | -0.00012596 | -0.0038435 | 0.032444 | 0.010322 | 0.07888 | 0.0243 | 0.028217 | 0.1208 | 0.059885 | 0.25185 | 0.10636 | 0.074307 | 0.050725 | 0.007751 | 0.07993 | 0.1648 | -0.12045 | -0.14125 | 121.8807 | -0.00737 | 121.8532 | 121.8025 | -0.078146 | -0.068289 | 0.12368 | 121.633 | -0.048244 | 121.8486 | 121.782 | 0.14901 | 0.036626 | -0.24862 | 121.8951 | 121.8342 | 122.0261 | 121.7986 | -0.021811 | 121.8542 | 121.9391 | 121.6538 | 121.825 | -0.26943
1158.2656 | 121.8887 | -121.7422 | 0.14648 | 1.4211e-13 | -0.029609 | 0.014252 | -0.0036391 | -0.012119 | 0.019057 | -0.23296 | -0.0014292 | -0.00012596 | -0.0034163 | 0.032658 | 0.010108 | 0.074302 | 0.0243 | 0.028217 | 0.11165 | 0.055306 | 0.24727 | 0.11552 | 0.069728 | 0.046146 | 0.003172 | 0.075351 | 0.15107 | -0.12045 | -0.1321 | 121.8578 | -0.034837 | 121.8166 | 121.7705 | -0.087304 | -0.091178 | 0.10079 | 121.6102 | -0.071133 | 121.812 | 121.7454 | 0.13527 | 0.004581 | -0.26693 | 121.8539 | 121.7976 | 121.9895 | 121.7665 | -0.030963 | 121.8176 | 121.8933 | 121.6218 | 121.7884 | -0.27858
1159.9375 | 122.0078 | -121.7056 | 0.10529 | 1.4211e-13 | -0.029822 | 0.013825 | -0.0034253 | -0.012333 | 0.019057 | -0.23296 | -0.0012156 | -0.00055336 | -0.0036299 | 0.033085 | 0.010535 | 0.069723 | 0.0243 | 0.023639 | 0.11622 | 0.059885 | 0.25643 | 0.11094 | 0.078886 | 0.041567 | 0.01233 | 0.075351 | 0.14649 | -0.13419 | -0.1321 | 121.8166 | 0.010939 | 121.7754 | 121.7293 | -0.087303 | -0.045401 | 0.15115 | 121.5735 | -0.029935 | 121.7845 | 121.718 | 0.14443 | 0.0412 | -0.23947 | 121.8219 | 121.7655 | 121.9621 | 121.7299 | 0.005656 | 121.781 | 121.8521 | 121.5714 | 121.7472 | -0.23738
1161.625 | 121.9299 | -121.7514 | 0.15106 | 1.4211e-13 | -0.029822 | 0.014252 | -0.0036391 | -0.012333 | 0.019057 | -0.23296 | -0.0012156 | -0.00076696 | -0.0034163 | 0.032658 | 0.010108 | 0.074302 | 0.0243 | 0.01906 | 0.11165 | 0.059885 | 0.25185 | 0.11552 | 0.074307 | 0.046146 | 0.007751 | 0.084508 | 0.16022 | -0.11587 | -0.1321 | 121.8669 | -0.039415 | 121.8257 | 121.7705 | -0.096461 | -0.091177 | 0.10079 | 121.6193 | -0.066554 | 121.8257 | 121.7592 | 0.13985 | 0.00916 | -0.26693 | 121.8631 | 121.8113 | 122.0033 | 121.7757 | -0.035541 | 121.8359 | 121.9116 | 121.6355 | 121.7975 | -0.28316
1164.7656 | 121.9894 | -121.7194 | 0.12817 | 1.4211e-13 | -0.029822 | 0.014252 | -0.0038527 | -0.012119 | 0.01927 | -0.22533 | -0.001643 | -0.00055336 | -0.0034163 | 0.032871 | 0.010322 | 0.069723 | 0.015142 | 0.023639 | 0.1208 | 0.059885 | 0.25185 | 0.1201 | 0.074307 | 0.03241 | 0.01233 | 0.089087 | 0.16022 | -0.13419 | -0.1321 | 121.8395 | -0.00737 | 121.7891 | 121.743 | -0.096461 | -0.068289 | 0.12368 | 121.5873 | -0.039087 | 121.7937 | 121.7317 | 0.14443 | 0.032048 | -0.26236 | 121.8402 | 121.7792 | 121.9712 | 121.7345 | -0.008074 | 121.8084 | 121.8796 | 121.5852 | 121.7518 | -0.26027
1168.5 | 121.9162 | -121.756 | 0.13275 | 1.4211e-13 | -0.029609 | 0.013825 | -0.0038527 | -0.012119 | 0.019057 | -0.22533 | -0.001643 | -0.00076696 | -0.0036299 | 0.032871 | 0.010108 | 0.074302 | 0.0243 | 0.01906 | 0.11622 | 0.055306 | 0.25185 | 0.1201 | 0.069728 | 0.036989 | 0.007751 | 0.093665 | 0.16022 | -0.13419 | -0.12752 | 121.8761 | -0.016526 | 121.8303 | 121.775 | -0.10104 | -0.077445 | 0.1191 | 121.6285 | -0.039086 | 121.8257 | 121.7637 | 0.13527 | 0.027471 | -0.26694 | 121.8722 | 121.8113 | 122.0078 | 121.7803 | -0.012651 | 121.8496 | 121.9162 | 121.6218 | 121.793 | -0.26027
1173.7812 | 122.0627 | -121.7239 | 0.10986 | 1.4211e-13 | -0.029609 | 0.014252 | -0.0038527 | -0.012333 | 0.018629 | -0.24822 | -0.001643 | -0.0011944 | -0.0040571 | 0.033085 | 0.010322 | 0.074302 | 0.033457 | 0.023639 | 0.11165 | 0.050727 | 0.25185 | 0.11094 | 0.074307 | 0.041567 | 0.01233 | 0.089087 | 0.15107 | -0.12961 | -0.13668 | 121.8349 | 0.001784 | 121.7982 | 121.7476 | -0.087303 | -0.059136 | 0.14199 | 121.5873 | -0.020776 | 121.7982 | 121.7363 | 0.14901 | 0.041202 | -0.23947 | 121.8356 | 121.7747 | 121.9758 | 121.7574 | 0.001079 | 121.813 | 121.875 | 121.5943 | 121.7655 | -0.24654
1176.4062 | 121.962 | -121.7468 | 0.13733 | 1.4211e-13 | -0.029181 | 0.014039 | -0.0038527 | -0.012119 | 0.019057 | -0.23296 | -0.001643 | -0.00076696 | -0.0034163 | 0.032871 | 0.0098942 | 0.069723 | 0.0243 | 0.023639 | 0.11165 | 0.055306 | 0.25643 | 0.11094 | 0.078886 | 0.046146 | 0.016908 | 0.10282 | 0.1648 | -0.12045 | -0.12752 | 121.8578 | -0.025682 | 121.8165 | 121.7705 | -0.087303 | -0.082023 | 0.1191 | 121.6193 | -0.034507 | 121.8257 | 121.7637 | 0.14443 | 0.027471 | -0.25778 | 121.8585 | 121.8021 | 122.0033 | 121.7711 | -0.026387 | 121.8496 | 121.9116 | 121.6264 | 121.793 | -0.26485
1178.0938 | 121.9391 | -121.7422 | 0.14191 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0036391 | -0.011905 | 0.019057 | -0.23296 | -0.0014292 | -0.0011944 | -0.0034163 | 0.032871 | 0.010108 | 0.074302 | 0.0243 | 0.028217 | 0.11622 | 0.055306 | 0.25185 | 0.10636 | 0.083464 | 0.041567 | 0.021487 | 0.098244 | 0.1648 | -0.070086 | -0.12752 | 121.8486 | -0.025682 | 121.8166 | 121.7705 | -0.078146 | -0.086601 | 0.10995 | 121.6147 | -0.043663 | 121.8257 | 121.7637 | 0.149 | 0.022893 | -0.21199 | 121.8585 | 121.7976 | 121.9941 | 121.7665 | -0.035544 | 121.8405 | 121.907 | 121.6722 | 121.7838 | -0.26943
1179.8438 | 121.9391 | -121.7789 | 0.14648 | 1.4211e-13 | -0.029822 | 0.014252 | -0.0036391 | -0.012119 | 0.019057 | -0.22533 | -0.0020702 | -0.00098076 | -0.0042707 | 0.033085 | 0.010535 | 0.07888 | 0.0243 | 0.032795 | 0.1208 | 0.059885 | 0.25185 | 0.11094 | 0.074307 | 0.036989 | 0.007751 | 0.089087 | 0.15107 | -0.10671 | -0.1321 | 121.8898 | -0.02568 | 121.8577 | 121.8117 | -0.078147 | -0.086599 | 0.10537 | 121.6468 | -0.057397 | 121.8532 | 121.7866 | 0.13985 | 0.004581 | -0.2532 | 121.8997 | 121.8388 | 122.0307 | 121.8032 | -0.035542 | 121.868 | 121.9299 | 121.6722 | 121.8159 | -0.27858
1181.5781 | 121.9345 | -121.7285 | 0.14648 | 1.4211e-13 | -0.029609 | 0.01468 | -0.0038527 | -0.012119 | 0.01927 | -0.23296 | -0.001643 | -0.00076696 | -0.0040571 | 0.032871 | 0.010322 | 0.074302 | 0.028878 | 0.023639 | 0.1208 | 0.064464 | 0.25185 | 0.11094 | 0.069728 | 0.046146 | 0.007751 | 0.098244 | 0.16022 | -0.11587 | -0.1321 | 121.8395 | -0.02568 | 121.8028 | 121.7522 | -0.087303 | -0.08202 | 0.10537 | 121.5964 | -0.04824 | 121.7982 | 121.7363 | 0.13985 | 0.013738 | -0.26236 | 121.8493 | 121.793 | 121.9804 | 121.7574 | -0.035542 | 121.8268 | 121.8887 | 121.6126 | 121.7747 | -0.27858
1183.2812 | 121.962 | -121.7377 | 0.11902 | 1.4211e-13 | -0.029822 | 0.014252 | -0.0034253 | -0.012546 | 0.01927 | -0.22533 | -0.0020702 | -0.00098076 | -0.0038435 | 0.032871 | 0.010322 | 0.069723 | 0.0243 | 0.028217 | 0.1208 | 0.055306 | 0.25185 | 0.11094 | 0.074307 | 0.036989 | 0.01233 | 0.089087 | 0.15564 | -0.13419 | -0.1321 | 121.8486 | 0.001785 | 121.8074 | 121.7659 | -0.082725 | -0.063713 | 0.13283 | 121.6056 | -0.029932 | 121.812 | 121.75 | 0.14443 | 0.036624 | -0.25321 | 121.8585 | 121.793 | 121.9895 | 121.762 | -0.008077 | 121.8268 | 121.8933 | 121.6035 | 121.7747 | -0.25112
1185.0156 | 121.9116 | -121.7834 | 0.14191 | 1.4211e-13 | -0.029822 | 0.014252 | -0.0038527 | -0.01276 | 0.019057 | -0.23296 | -0.0018566 | -0.00098076 | -0.0040571 | 0.033085 | 0.010535 | 0.07888 | 0.033457 | 0.028217 | 0.1208 | 0.055306 | 0.25643 | 0.11094 | 0.074307 | 0.041567 | 0.003172 | 0.089087 | 0.16022 | -0.083821 | -0.12752 | 121.8944 | -0.021103 | 121.8623 | 121.8117 | -0.082725 | -0.086601 | 0.11452 | 121.6559 | -0.05282 | 121.8578 | 121.7866 | 0.13069 | 0.018315 | -0.22573 | 121.9043 | 121.8388 | 122.0399 | 121.8169 | -0.030965 | 121.8725 | 121.9437 | 121.6996 | 121.825 | -0.26943
1186.6875 | 122.0078 | -121.7285 | 0.1236 | 1.4211e-13 | -0.030036 | 0.014252 | -0.0036391 | -0.012333 | 0.019057 | -0.24059 | -0.0018566 | -0.0011944 | -0.0042707 | 0.032871 | 0.010322 | 0.065145 | 0.0243 | 0.028217 | 0.11622 | 0.059885 | 0.25643 | 0.092626 | 0.078886 | 0.041567 | 0.007751 | 0.084508 | 0.15564 | -0.12045 | -0.12752 | 121.8211 | -0.007371 | 121.7937 | 121.7567 | -0.064409 | -0.063711 | 0.13284 | 121.601 | -0.039088 | 121.8074 | 121.7363 | 0.13527 | 0.032047 | -0.24405 | 121.8447 | 121.7884 | 121.9849 | 121.7528 | -0.03097 | 121.813 | 121.8842 | 121.6081 | 121.7701 | -0.25111
1188.4219 | 122.049 | -121.701 | 0.10529 | 1.4211e-13 | -0.030036 | 0.014252 | -0.0038527 | -0.012119 | 0.019057 | -0.23296 | -0.00078837 | 0.00072864 | -0.0032025 | 0.032871 | 0.010322 | 0.074302 | 0.0243 | 0.023639 | 0.1208 | 0.059885 | 0.25185 | 0.10636 | 0.078886 | 0.041567 | 0.016908 | 0.098244 | 0.16022 | -0.0884 | -0.12752 | 121.8074 | 0.015518 | 121.7754 | 121.7247 | -0.082724 | -0.045401 | 0.14657 | 121.5735 | -0.007042 | 121.7799 | 121.718 | 0.14443 | 0.054936 | -0.19369 | 121.8219 | 121.7609 | 121.9529 | 121.7253 | 0.001077 | 121.7993 | 121.8613 | 121.6127 | 121.7426 | -0.2328
1190.0938 | 122.0169 | -121.701 | 0.12817 | 1.4211e-13 | -0.029609 | 0.014039 | -0.0038527 | -0.012333 | 0.019057 | -0.23296 | -0.001643 | -0.00033976 | -0.0036299 | 0.032658 | 0.010322 | 0.07888 | 0.028878 | 0.023639 | 0.11165 | 0.059885 | 0.25185 | 0.11552 | 0.083464 | 0.041567 | 0.01233 | 0.089087 | 0.1648 | -0.05635 | -0.12294 | 121.8166 | -0.016527 | 121.7799 | 121.7247 | -0.091882 | -0.068289 | 0.12368 | 121.5781 | -0.039087 | 121.7845 | 121.7134 | 0.13527 | 0.036626 | -0.18452 | 121.8127 | 121.7609 | 121.9529 | 121.7299 | -0.012653 | 121.7901 | 121.8658 | 121.6447 | 121.7426 | -0.25111
1191.8438 | 121.9666 | -121.7606 | 0.14648 | 1.4211e-13 | -0.029609 | 0.014252 | -0.0038527 | -0.012333 | 0.019057 | -0.24059 | -0.0012156 | -0.00055336 | -0.0032025 | 0.032658 | 0.010322 | 0.074302 | 0.019721 | 0.023639 | 0.11622 | 0.059885 | 0.25643 | 0.11094 | 0.078886 | 0.041567 | 0.01233 | 0.093665 | 0.16022 | -0.051771 | -0.12294 | 121.8715 | -0.030259 | 121.8349 | 121.7842 | -0.087303 | -0.086599 | 0.10995 | 121.6376 | -0.052819 | 121.8394 | 121.7729 | 0.13527 | 0.013738 | -0.19826 | 121.8768 | 121.8204 | 122.017 | 121.7803 | -0.035542 | 121.8542 | 121.9208 | 121.7088 | 121.8021 | -0.26942
1193.5781 | 121.9345 | -121.756 | 0.16022 | 1.4211e-13 | -0.029822 | 0.014252 | -0.0034253 | -0.012119 | 0.019057 | -0.23296 | -0.0020702 | -0.00098076 | -0.0042707 | 0.032871 | 0.010322 | 0.074302 | 0.033457 | 0.028217 | 0.11165 | 0.064464 | 0.26101 | 0.10636 | 0.088043 | 0.041567 | 0.01233 | 0.098244 | 0.17396 | -0.001407 | -0.12752 | 121.8623 | -0.04857 | 121.8303 | 121.7842 | -0.078146 | -0.095753 | 0.10079 | 121.6285 | -0.061973 | 121.844 | 121.7683 | 0.13985 | 0.013741 | -0.16162 | 121.8676 | 121.8204 | 122.017 | 121.7894 | -0.053854 | 121.8542 | 121.9299 | 121.7546 | 121.7975 | -0.28773
1195.25 | 121.9391 | -121.7743 | 0.15564 | 1.4211e-13 | -0.029822 | 0.014466 | -0.0034253 | -0.012119 | 0.01927 | -0.23296 | -0.00078837 | 0.00030124 | -0.0032025 | 0.032871 | 0.010108 | 0.074302 | 0.028878 | 0.028217 | 0.11622 | 0.055306 | 0.25185 | 0.092626 | 0.083464 | 0.041567 | 0.016908 | 0.093665 | 0.16938 | -0.033457 | -0.12294 | 121.8669 | -0.039415 | 121.8486 | 121.8025 | -0.064409 | -0.10033 | 0.096212 | 121.6514 | -0.061975 | 121.8578 | 121.7912 | 0.13985 | 0.013739 | -0.1891 | 121.8905 | 121.8296 | 122.0261 | 121.8032 | -0.063014 | 121.868 | 121.9437 | 121.7408 | 121.8159 | -0.27858
1197 | 121.9803 | -121.7285 | 0.13275 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0034253 | -0.012333 | 0.018843 | -0.2177 | -0.001002 | 0.00030124 | -0.0029889 | 0.032871 | 0.010535 | 0.074302 | 0.028878 | 0.023639 | 0.11622 | 0.055306 | 0.25643 | 0.10636 | 0.083464 | 0.046146 | 0.01233 | 0.098244 | 0.1648 | -0.079243 | -0.12752 | 121.8349 | -0.016526 | 121.8028 | 121.7522 | -0.082724 | -0.077445 | 0.12368 | 121.601 | -0.034507 | 121.812 | 121.7408 | 0.13985 | 0.032049 | -0.21199 | 121.8447 | 121.7838 | 121.9849 | 121.7574 | -0.026388 | 121.8268 | 121.8933 | 121.6493 | 121.7747 | -0.26027
1198.7344 | 121.9666 | -121.7651 | 0.12817 | 1.4211e-13 | -0.029822 | 0.013825 | -0.0034253 | -0.012333 | 0.018843 | -0.24822 | -0.0014292 | -0.00055336 | -0.0034163 | 0.033085 | 0.010322 | 0.07888 | 0.0243 | 0.028217 | 0.11165 | 0.050727 | 0.26101 | 0.097205 | 0.069728 | 0.041567 | 0.016908 | 0.093665 | 0.15564 | -0.10671 | -0.1321 | 121.8623 | -0.016527 | 121.844 | 121.7934 | -0.068988 | -0.077447 | 0.13284 | 121.633 | -0.034509 | 121.8349 | 121.782 | 0.149 | 0.027469 | -0.23489 | 121.8768 | 121.8159 | 122.0261 | 121.7894 | -0.030969 | 121.8588 | 121.9208 | 121.6584 | 121.8067 | -0.26027
1200.4844 | 121.9162 | -121.7789 | 0.1236 | 1.4211e-13 | -0.029609 | 0.014252 | -0.0038527 | -0.012333 | 0.019057 | -0.24059 | -0.0018566 | -0.00076696 | -0.0036299 | 0.032658 | 0.010322 | 0.07888 | 0.0243 | 0.028217 | 0.1208 | 0.055306 | 0.25185 | 0.11094 | 0.078886 | 0.036989 | 0.003172 | 0.093665 | 0.15564 | -0.097557 | -0.14125 | 121.8898 | -0.002792 | 121.8577 | 121.8071 | -0.082725 | -0.06829 | 0.12826 | 121.6376 | -0.029931 | 121.8578 | 121.782 | 0.14443 | 0.032047 | -0.22115 | 121.8997 | 121.8342 | 122.0307 | 121.8032 | -0.012654 | 121.8725 | 121.9345 | 121.6813 | 121.8159 | -0.26485
1202.1562 | 122.0078 | -121.7102 | 0.13275 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0036391 | -0.012333 | 0.019057 | -0.23296 | -0.0018566 | -0.00098076 | -0.0040571 | 0.032871 | 0.010749 | 0.069723 | 0.028878 | 0.028217 | 0.11622 | 0.050727 | 0.26101 | 0.083468 | 0.078886 | 0.03241 | 0.01233 | 0.089087 | 0.16022 | -0.070086 | -0.1321 | 121.7937 | -0.016526 | 121.7799 | 121.7384 | -0.055251 | -0.082024 | 0.12826 | 121.5781 | -0.043664 | 121.7891 | 121.7225 | 0.14443 | 0.027471 | -0.20284 | 121.8264 | 121.7609 | 121.9712 | 121.7391 | -0.049283 | 121.7993 | 121.8704 | 121.6401 | 121.7426 | -0.26485
1203.8906 | 121.9574 | -121.7377 | 0.13275 | 1.4211e-13 | -0.029609 | 0.014466 | -0.0036391 | -0.012119 | 0.019057 | -0.23296 | -0.0012156 | -0.00033976 | -0.0038435 | 0.033299 | 0.010322 | 0.065145 | 0.028878 | 0.01906 | 0.11622 | 0.059885 | 0.25185 | 0.10636 | 0.078886 | 0.036989 | 0.01233 | 0.084508 | 0.15564 | -0.12045 | -0.14125 | 121.844 | -0.016526 | 121.8028 | 121.7567 | -0.087303 | -0.072866 | 0.1191 | 121.5964 | -0.048243 | 121.8166 | 121.75 | 0.15358 | 0.022892 | -0.2532 | 121.8539 | 121.7976 | 121.9895 | 121.7665 | -0.026388 | 121.8222 | 121.8933 | 121.6172 | 121.7747 | -0.27401
1205.625 | 122.0535 | -121.7331 | 0.11444 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0032117 | -0.012546 | 0.018843 | -0.23296 | -0.0020702 | -0.00055336 | -0.0036299 | 0.033085 | 0.010535 | 0.074302 | 0.028878 | 0.032795 | 0.1208 | 0.059885 | 0.25643 | 0.097205 | 0.074307 | 0.03241 | 0.003172 | 0.093665 | 0.16022 | -0.10214 | -0.12752 | 121.8303 | 0.006363 | 121.8074 | 121.7659 | -0.06441 | -0.054556 | 0.14199 | 121.6056 | -0.020776 | 121.8074 | 121.7363 | 0.13069 | 0.045781 | -0.21658 | 121.8539 | 121.793 | 121.9895 | 121.762 | -0.017236 | 121.8268 | 121.8933 | 121.631 | 121.7655 | -0.24196
1207.375 | 122.0032 | -121.7285 | 0.10529 | 1.4211e-13 | -0.029822 | 0.01468 | -0.0034253 | -0.011905 | 0.018843 | -0.23296 | -0.001643 | -0.00055336 | -0.0038435 | 0.033299 | 0.010108 | 0.069723 | 0.028878 | 0.023639 | 0.11622 | 0.059885 | 0.25185 | 0.11552 | 0.074307 | 0.03241 | -0.001407 | 0.089087 | 0.15564 | -0.083821 | -0.1321 | 121.844 | 0.010939 | 121.7982 | 121.7522 | -0.091882 | -0.045401 | 0.14657 | 121.5964 | -0.016199 | 121.8028 | 121.7271 | 0.13069 | 0.050357 | -0.18911 | 121.8447 | 121.7884 | 121.9804 | 121.7574 | 0.010235 | 121.8176 | 121.8842 | 121.6447 | 121.7609 | -0.23738
1209.0625 | 122.0215 | -121.7377 | 0.13275 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0036391 | -0.012119 | 0.019057 | -0.23296 | -0.0018566 | -0.00055336 | -0.0038435 | 0.033085 | 0.010535 | 0.07888 | 0.0243 | 0.028217 | 0.1208 | 0.055306 | 0.25185 | 0.11094 | 0.074307 | 0.036989 | 0.003172 | 0.089087 | 0.16022 | -0.074664 | -0.12752 | 121.8486 | -0.011947 | 121.8166 | 121.7659 | -0.082725 | -0.077445 | 0.1191 | 121.6102 | -0.043664 | 121.812 | 121.7408 | 0.13069 | 0.027471 | -0.20742 | 121.8585 | 121.793 | 121.9895 | 121.762 | -0.021809 | 121.8268 | 121.8979 | 121.663 | 121.7747 | -0.26027
1210.7969 | 122.0078 | -121.7102 | 0.1236 | 1.4211e-13 | -0.029609 | 0.014252 | -0.0036391 | -0.012119 | 0.018843 | -0.24059 | -0.001643 | -0.00076696 | -0.0038435 | 0.032871 | 0.0098942 | 0.074302 | 0.0243 | 0.032795 | 0.11622 | 0.059885 | 0.25643 | 0.097205 | 0.078886 | 0.041567 | 0.007751 | 0.089087 | 0.16022 | -0.038035 | -0.13668 | 121.8074 | -0.007371 | 121.7845 | 121.743 | -0.06441 | -0.063711 | 0.13284 | 121.5735 | -0.034509 | 121.7891 | 121.718 | 0.14443 | 0.036626 | -0.16163 | 121.8264 | 121.7701 | 121.9666 | 121.7345 | -0.026391 | 121.7993 | 121.8704 | 121.6722 | 121.7518 | -0.26027
1212.5469 | 122.0398 | -121.7102 | 0.11902 | 1.4211e-13 | -0.029609 | 0.014252 | -0.0036391 | -0.012119 | 0.018843 | -0.23296 | -0.0014292 | -0.00033976 | -0.0038435 | 0.033512 | 0.010108 | 0.069723 | 0.0243 | 0.032795 | 0.11622 | 0.055306 | 0.25643 | 0.088047 | 0.083464 | 0.041567 | 0.01233 | 0.093665 | 0.15107 | -0.079243 | -0.1321 | 121.7983 | -0.002794 | 121.7799 | 121.743 | -0.055252 | -0.063713 | 0.13741 | 121.5781 | -0.025354 | 121.7937 | 121.7225 | 0.14443 | 0.032046 | -0.19826 | 121.8264 | 121.7655 | 121.9666 | 121.7345 | -0.030972 | 121.8039 | 121.8613 | 121.631 | 121.7518 | -0.25112
1214.2188 | 122.049 | -121.6919 | 0.082397 | 1.4211e-13 | -0.029609 | 0.014252 | -0.0036391 | -0.01276 | 0.018843 | -0.23296 | -0.001643 | -0.00055336 | -0.0038435 | 0.032871 | 0.010535 | 0.065145 | 0.0243 | 0.028217 | 0.1208 | 0.055306 | 0.25643 | 0.11094 | 0.074307 | 0.036989 | 0.007751 | 0.084508 | 0.16022 | -0.10214 | -0.1321 | 121.8028 | 0.038407 | 121.757 | 121.7201 | -0.082725 | -0.027091 | 0.17403 | 121.5598 | 0.002111 | 121.7662 | 121.6996 | 0.13985 | 0.077825 | -0.18453 | 121.8127 | 121.7472 | 121.9483 | 121.7162 | 0.028545 | 121.7764 | 121.8521 | 121.5898 | 121.7289 | -0.21449
1215.9531 | 121.9208 | -121.8018 | 0.15564 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0040665 | -0.012333 | 0.018843 | -0.23296 | -0.0018566 | -0.00055336 | -0.0038435 | 0.032871 | 0.0098942 | 0.069723 | 0.033457 | 0.028217 | 0.1208 | 0.059885 | 0.25643 | 0.078889 | 0.083464 | 0.03241 | 0.01233 | 0.089087 | 0.1648 | -0.065507 | -0.1321 | 121.8806 | -0.034836 | 121.8715 | 121.83 | -0.050672 | -0.095755 | 0.10079 | 121.6697 | -0.066553 | 121.8852 | 121.8141 | 0.14443 | 0.00916 | -0.22115 | 121.9226 | 121.8616 | 122.0582 | 121.8352 | -0.076751 | 121.8908 | 121.9666 | 121.7363 | 121.8342 | -0.28774
1217.6406 | 122.0581 | -121.7651 | 0.10986 | 1.4211e-13 | -0.030036 | 0.014039 | -0.0040665 | -0.012546 | 0.019057 | -0.23296 | -0.0014292 | -0.00076696 | -0.0038435 | 0.033085 | 0.010322 | 0.07888 | 0.0243 | 0.028217 | 0.1208 | 0.055306 | 0.25643 | 0.10178 | 0.06515 | 0.041567 | 0.01233 | 0.089087 | 0.16022 | -0.074664 | -0.1321 | 121.8669 | 0.010941 | 121.844 | 121.7934 | -0.073567 | -0.054557 | 0.14657 | 121.633 | -0.020776 | 121.8303 | 121.7775 | 0.14443 | 0.050359 | -0.18453 | 121.8859 | 121.8204 | 122.0216 | 121.7894 | -0.008079 | 121.8542 | 121.9254 | 121.6905 | 121.8067 | -0.24196
1219.375 | 122.0581 | -121.6919 | 0.11902 | 1.4211e-13 | -0.029822 | 0.014466 | -0.0036391 | -0.012546 | 0.019057 | -0.22533 | -0.0018566 | -0.00098076 | -0.0036299 | 0.033726 | 0.010108 | 0.074302 | 0.0243 | 0.032795 | 0.11622 | 0.059885 | 0.27017 | 0.10178 | 0.069728 | 0.036989 | 0.016908 | 0.089087 | 0.16022 | -0.097557 | -0.12752 | 121.7937 | -0.002794 | 121.7662 | 121.7247 | -0.068989 | -0.059134 | 0.15115 | 121.5644 | -0.029932 | 121.7616 | 121.7088 | 0.14443 | 0.041203 | -0.21658 | 121.8081 | 121.7518 | 121.9621 | 121.7162 | -0.017235 | 121.781 | 121.8521 | 121.5943 | 121.7289 | -0.24654
1221.125 | 122.0673 | -121.7285 | 0.09613 | 1.4211e-13 | -0.029609 | 0.014252 | -0.0036391 | -0.012546 | 0.019057 | -0.2177 | -0.0012156 | -0.00055336 | -0.0034163 | 0.032871 | 0.010108 | 0.074302 | 0.028878 | 0.023639 | 0.11165 | 0.059885 | 0.25185 | 0.11094 | 0.069728 | 0.036989 | 0.007751 | 0.093665 | 0.15564 | -0.0884 | -0.12752 | 121.8395 | 0.015517 | 121.8028 | 121.7522 | -0.087303 | -0.036245 | 0.15572 | 121.601 | -0.002465 | 121.7982 | 121.7363 | 0.13527 | 0.059513 | -0.18453 | 121.8402 | 121.7884 | 121.9804 | 121.7574 | 0.014812 | 121.8222 | 121.8842 | 121.6401 | 121.7655 | -0.22365
1222.8906 | 121.9254 | -121.7789 | 0.14191 | 1.4211e-13 | -0.03025 | 0.014039 | -0.0040665 | -0.012546 | 0.018629 | -0.23296 | -0.001002 | -0.00033976 | -0.0034163 | 0.032658 | 0.010108 | 0.069723 | 0.028878 | 0.023639 | 0.11622 | 0.059885 | 0.25185 | 0.10636 | 0.078886 | 0.036989 | 0.01233 | 0.089087 | 0.16022 | -0.0884 | -0.1321 | 121.8852 | -0.025682 | 121.8486 | 121.8025 | -0.082724 | -0.082022 | 0.10995 | 121.6468 | -0.05282 | 121.8578 | 121.7912 | 0.14443 | 0.018315 | -0.23031 | 121.8951 | 121.8388 | 122.0307 | 121.8077 | -0.035544 | 121.868 | 121.9391 | 121.6905 | 121.8159 | -0.274
1224.5625 | 121.9025 | -121.7697 | 0.14648 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0034253 | -0.012333 | 0.018843 | -0.22533 | -0.0014292 | -0.00012596 | -0.0034163 | 0.033085 | 0.010108 | 0.074302 | 0.028878 | 0.028217 | 0.10707 | 0.050727 | 0.24727 | 0.097205 | 0.074307 | 0.041567 | 0.003172 | 0.093665 | 0.16022 | -0.10214 | -0.13668 | 121.8669 | -0.039416 | 121.844 | 121.7979 | -0.068988 | -0.095757 | 0.10079 | 121.633 | -0.052819 | 121.844 | 121.7729 | 0.13985 | 0.013738 | -0.24862 | 121.8768 | 121.8204 | 122.017 | 121.7986 | -0.049279 | 121.8634 | 121.9299 | 121.6676 | 121.8113 | -0.28316
1226.2969 | 121.9894 | -121.7285 | 0.11444 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0038527 | -0.012119 | 0.018843 | -0.23296 | -0.0014292 | -0.00055336 | -0.0034163 | 0.033299 | 0.010322 | 0.074302 | 0.019721 | 0.023639 | 0.11622 | 0.059885 | 0.25643 | 0.097205 | 0.074307 | 0.046146 | 0.01233 | 0.093665 | 0.15107 | -0.12045 | -0.13668 | 121.8257 | 0.001784 | 121.8028 | 121.7522 | -0.073566 | -0.054556 | 0.14199 | 121.5918 | -0.020776 | 121.8028 | 121.7408 | 0.14901 | 0.036624 | -0.23489 | 121.8447 | 121.7884 | 121.9849 | 121.7482 | -0.017236 | 121.8222 | 121.8796 | 121.6081 | 121.7747 | -0.25112
1228.0312 | 121.994 | -121.7468 | 0.1236 | 1.4211e-13 | -0.029609 | 0.014039 | -0.0038527 | -0.012546 | 0.019057 | -0.24059 | -0.0012156 | -0.00033976 | -0.0032025 | 0.032871 | 0.010322 | 0.069723 | 0.0243 | 0.032795 | 0.11622 | 0.055306 | 0.25643 | 0.092626 | 0.078886 | 0.03241 | 0.007751 | 0.10282 | 0.15564 | -0.0884 | -0.1321 | 121.8395 | -0.007371 | 121.8165 | 121.7796 | -0.059831 | -0.06829 | 0.13284 | 121.6147 | -0.020774 | 121.8257 | 121.7546 | 0.13985 | 0.032047 | -0.212 | 121.8631 | 121.8021 | 122.0033 | 121.7711 | -0.03097 | 121.8496 | 121.9025 | 121.6584 | 121.7792 | -0.25569
1229.7031 | 122.0398 | -121.7422 | 0.10529 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0040665 | -0.012119 | 0.01927 | -0.22533 | -0.0014292 | -0.00033976 | -0.0036299 | 0.033085 | 0.010108 | 0.074302 | 0.028878 | 0.028217 | 0.11165 | 0.059885 | 0.26101 | 0.097205 | 0.078886 | 0.050725 | 0.007751 | 0.084508 | 0.16022 | -0.12503 | -0.12752 | 121.8395 | 0.006361 | 121.8166 | 121.7705 | -0.068988 | -0.045401 | 0.15572 | 121.6147 | -0.020778 | 121.8211 | 121.75 | 0.13527 | 0.054936 | -0.23031 | 121.8539 | 121.8021 | 122.0033 | 121.7711 | -0.008081 | 121.8268 | 121.9025 | 121.6172 | 121.793 | -0.2328
1231.4531 | 121.9711 | -121.7514 | 0.1236 | 1.4211e-13 | -0.029822 | 0.014466 | -0.0036391 | -0.012119 | 0.018843 | -0.22533 | -0.0014292 | -0.00033976 | -0.0036299 | 0.032658 | 0.010322 | 0.074302 | 0.019721 | 0.028217 | 0.11622 | 0.055306 | 0.25185 | 0.10178 | 0.078886 | 0.041567 | 0.007751 | 0.093665 | 0.15564 | -0.097557 | -0.12752 | 121.8532 | -0.007371 | 121.8257 | 121.7796 | -0.073567 | -0.06829 | 0.12826 | 121.6239 | -0.029931 | 121.8303 | 121.7592 | 0.13527 | 0.032047 | -0.22115 | 121.8676 | 121.8067 | 122.0033 | 121.7711 | -0.021812 | 121.8451 | 121.907 | 121.6538 | 121.793 | -0.25111
1233.1406 | 122.0123 | -121.7606 | 0.1236 | 1.4211e-13 | -0.03025 | 0.014252 | -0.0038527 | -0.012333 | 0.01927 | -0.22533 | -0.0012156 | -0.00012596 | -0.0034163 | 0.033085 | 0.0098942 | 0.074302 | 0.028878 | 0.023639 | 0.11165 | 0.064464 | 0.25643 | 0.092626 | 0.078886 | 0.050725 | 0.016908 | 0.089087 | 0.16022 | -0.060928 | -0.12294 | 121.8532 | -0.011949 | 121.8349 | 121.7842 | -0.068987 | -0.059132 | 0.13284 | 121.6376 | -0.034509 | 121.8394 | 121.7775 | 0.13985 | 0.036626 | -0.18452 | 121.8722 | 121.825 | 122.017 | 121.7894 | -0.03097 | 121.8496 | 121.9208 | 121.6996 | 121.8113 | -0.24654
1234.875 | 121.9803 | -121.7468 | 0.15106 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0034253 | -0.012546 | 0.01927 | -0.22533 | -0.0018566 | -0.00076696 | -0.0038435 | 0.033085 | 0.010322 | 0.074302 | 0.0243 | 0.028217 | 0.10707 | 0.059885 | 0.25643 | 0.10178 | 0.088043 | 0.036989 | 0.003172 | 0.089087 | 0.16022 | -0.11129 | -0.13668 | 121.8486 | -0.043994 | 121.8211 | 121.775 | -0.073567 | -0.091177 | 0.10537 | 121.6102 | -0.061975 | 121.8349 | 121.75 | 0.13985 | 0.00916 | -0.26236 | 121.8539 | 121.8067 | 122.0033 | 121.7711 | -0.049278 | 121.8359 | 121.907 | 121.6355 | 121.7838 | -0.28774
1236.5469 | 121.962 | -121.7331 | 0.13275 | 1.4211e-13 | -0.030036 | 0.014039 | -0.0036391 | -0.012119 | 0.018843 | -0.24822 | -0.0012156 | -0.00033976 | -0.0032025 | 0.032871 | 0.010322 | 0.069723 | 0.033457 | 0.023639 | 0.11622 | 0.059885 | 0.25185 | 0.10636 | 0.078886 | 0.036989 | 0.003172 | 0.093665 | 0.1648 | -0.097557 | -0.13668 | 121.8395 | -0.016526 | 121.8028 | 121.7567 | -0.082724 | -0.072866 | 0.1191 | 121.5964 | -0.039086 | 121.812 | 121.7363 | 0.13985 | 0.032049 | -0.23031 | 121.8493 | 121.793 | 121.9849 | 121.7665 | -0.026388 | 121.8268 | 121.8979 | 121.6355 | 121.7701 | -0.26943
1238.2969 | 121.9711 | -121.7377 | 0.12817 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0038527 | -0.012333 | 0.018843 | -0.23296 | -0.0014292 | -0.00012596 | -0.0032025 | 0.033299 | 0.010108 | 0.07888 | 0.028878 | 0.01906 | 0.11165 | 0.055306 | 0.25643 | 0.10178 | 0.069728 | 0.036989 | 0.007751 | 0.089087 | 0.1648 | -0.10214 | -0.12752 | 121.8395 | -0.016527 | 121.8166 | 121.7567 | -0.082724 | -0.072868 | 0.12826 | 121.6102 | -0.039087 | 121.8074 | 121.7454 | 0.13527 | 0.036626 | -0.23031 | 121.8493 | 121.793 | 121.9941 | 121.7665 | -0.02639 | 121.8268 | 121.9025 | 121.6355 | 121.7747 | -0.25569
1239.9688 | 122.0123 | -121.7056 | 0.10986 | 1.4211e-13 | -0.029822 | 0.014252 | -0.0036391 | -0.012119 | 0.019057 | -0.23296 | -0.001002 | -0.00012596 | -0.0034163 | 0.033085 | 0.010108 | 0.065145 | 0.0243 | 0.028217 | 0.1208 | 0.059885 | 0.25185 | 0.092626 | 0.074307 | 0.046146 | 0.007751 | 0.084508 | 0.1648 | -0.11587 | -0.1321 | 121.7983 | 0.010941 | 121.7708 | 121.7338 | -0.064409 | -0.049978 | 0.14199 | 121.5735 | -0.025355 | 121.7799 | 121.7134 | 0.13985 | 0.054937 | -0.22574 | 121.8264 | 121.7655 | 121.9575 | 121.7299 | -0.017237 | 121.7901 | 121.8704 | 121.5898 | 121.7518 | -0.24196
1241.7031 | 121.9711 | -121.7651 | 0.13733 | 1.4211e-13 | -0.029822 | 0.014466 | -0.0036391 | -0.012546 | 0.01927 | -0.23296 | -0.0012156 | 8.7636e-05 | -0.0032025 | 0.033085 | 0.010108 | 0.074302 | 0.028878 | 0.028217 | 0.11622 | 0.050727 | 0.25185 | 0.092626 | 0.074307 | 0.036989 | 0.01233 | 0.089087 | 0.1648 | -0.074664 | -0.12752 | 121.8578 | -0.021104 | 121.8394 | 121.7934 | -0.064409 | -0.086602 | 0.11452 | 121.6376 | -0.048242 | 121.8394 | 121.7775 | 0.13985 | 0.027471 | -0.21199 | 121.8814 | 121.8159 | 122.017 | 121.794 | -0.044703 | 121.8542 | 121.9299 | 121.6905 | 121.8021 | -0.26485
1243.3906 | 122.0169 | -121.7148 | 0.10071 | 1.4211e-13 | -0.029609 | 0.014252 | -0.0034253 | -0.012546 | 0.018843 | -0.23296 | -0.00078837 | 0.00030124 | -0.0025617 | 0.032871 | 0.010322 | 0.074302 | 0.019721 | 0.028217 | 0.11622 | 0.059885 | 0.24727 | 0.1201 | 0.074307 | 0.041567 | 0.003172 | 0.089087 | 0.16022 | -0.0884 | -0.1321 | 121.8349 | 0.015517 | 121.7891 | 121.743 | -0.091883 | -0.040823 | 0.14657 | 121.5827 | -0.011621 | 121.7891 | 121.718 | 0.13527 | 0.059514 | -0.18911 | 121.831 | 121.7747 | 121.9621 | 121.7345 | 0.019392 | 121.8039 | 121.875 | 121.6264 | 121.7563 | -0.2328
1245.125 | 121.962 | -121.7422 | 0.12817 | 1.4211e-13 | -0.030036 | 0.014039 | -0.0036391 | -0.012546 | 0.019057 | -0.24059 | -0.0012156 | 0.00030124 | -0.0029889 | 0.032871 | 0.010322 | 0.074302 | 0.0243 | 0.028217 | 0.10707 | 0.059885 | 0.26101 | 0.097205 | 0.074307 | 0.041567 | 0.007751 | 0.098244 | 0.16022 | -0.0884 | -0.1321 | 121.8395 | -0.021106 | 121.8166 | 121.7705 | -0.068988 | -0.068289 | 0.13284 | 121.6102 | -0.02993 | 121.8166 | 121.75 | 0.13985 | 0.032048 | -0.21657 | 121.8493 | 121.8021 | 122.0033 | 121.7665 | -0.030969 | 121.8405 | 121.9025 | 121.6538 | 121.7838 | -0.26027
1246.875 | 122.081 | -121.7148 | 0.10529 | 1.4211e-13 | -0.029822 | 0.014252 | -0.0036391 | -0.012546 | 0.01927 | -0.23296 | -0.00057477 | 0.00030124 | -0.0025617 | 0.032871 | 0.010322 | 0.07888 | 0.0243 | 0.023639 | 0.1208 | 0.064464 | 0.25185 | 0.11094 | 0.074307 | 0.046146 | 0.003172 | 0.093665 | 0.15564 | -0.042614 | -0.13668 | 121.8257 | 0.015518 | 121.7937 | 121.7384 | -0.087303 | -0.040822 | 0.14657 | 121.5781 | -0.011621 | 121.7891 | 121.718 | 0.13985 | 0.050357 | -0.1479 | 121.8356 | 121.7792 | 121.9666 | 121.7391 | 0.005656 | 121.8084 | 121.8704 | 121.6722 | 121.7609 | -0.24196
1248.5625 | 122.0123 | -121.7468 | 0.1236 | 1.4211e-13 | -0.029395 | 0.014466 | -0.0038527 | -0.012546 | 0.019057 | -0.23296 | -0.00057477 | 0.00030124 | -0.0027753 | 0.033085 | 0.010108 | 0.07888 | 0.019721 | 0.028217 | 0.10707 | 0.055306 | 0.25185 | 0.1201 | 0.074307 | 0.036989 | 0.016908 | 0.089087 | 0.15107 | -0.12961 | -0.13668 | 121.8669 | -0.016528 | 121.8257 | 121.775 | -0.091883 | -0.06829 | 0.12826 | 121.6102 | -0.034509 | 121.8211 | 121.7637 | 0.15358 | 0.027469 | -0.2532 | 121.8539 | 121.8021 | 121.9987 | 121.7665 | -0.003496 | 121.8359 | 121.8979 | 121.6172 | 121.7838 | -0.26027
1250.2969 | 122.0398 | -121.7056 | 0.10986 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0036391 | -0.012546 | 0.019057 | -0.24822 | -0.00057477 | 0.00051484 | -0.0027753 | 0.033085 | 0.010322 | 0.065145 | 0.028878 | 0.028217 | 0.11165 | 0.055306 | 0.25643 | 0.11094 | 0.074307 | 0.046146 | 0.007751 | 0.084508 | 0.15564 | -0.11129 | -0.13668 | 121.8166 | 0.001784 | 121.7708 | 121.7338 | -0.082725 | -0.054557 | 0.14657 | 121.569 | -0.025355 | 121.7799 | 121.7134 | 0.14443 | 0.04578 | -0.22116 | 121.8173 | 121.7609 | 121.9621 | 121.7345 | 0.001079 | 121.7901 | 121.8613 | 121.5943 | 121.7518 | -0.24654
1252.0312 | 122.081 | -121.7331 | 0.11444 | 1.4211e-13 | -0.029822 | 0.014252 | -0.0038527 | -0.012119 | 0.019057 | -0.22533 | -0.00078837 | 0.00051484 | -0.0027753 | 0.033085 | 0.010108 | 0.07888 | 0.0243 | 0.028217 | 0.11622 | 0.050727 | 0.25185 | 0.10178 | 0.074307 | 0.036989 | 0.01233 | 0.089087 | 0.15564 | -0.12045 | -0.1321 | 121.8349 | 0.001784 | 121.812 | 121.7613 | -0.073567 | -0.063714 | 0.13741 | 121.601 | -0.025354 | 121.8074 | 121.7454 | 0.14443 | 0.041202 | -0.23489 | 121.8493 | 121.7838 | 121.9849 | 121.7574 | -0.012657 | 121.8222 | 121.8887 | 121.6126 | 121.7701 | -0.24654
1253.7656 | 122.0535 | -121.7285 | 0.10071 | 1.4211e-13 | -0.029822 | 0.014466 | -0.0036391 | -0.012333 | 0.01927 | -0.24822 | -0.00057477 | 8.7636e-05 | -0.0027753 | 0.033299 | 0.0098942 | 0.074302 | 0.028878 | 0.023639 | 0.1208 | 0.055306 | 0.26559 | 0.097205 | 0.074307 | 0.046146 | 0.007751 | 0.089087 | 0.16022 | -0.083821 | -0.1321 | 121.8257 | 0.020096 | 121.8028 | 121.7522 | -0.073566 | -0.045402 | 0.16488 | 121.5964 | -0.011621 | 121.8028 | 121.7363 | 0.13985 | 0.059514 | -0.18453 | 121.8493 | 121.7838 | 121.9941 | 121.7574 | -0.003503 | 121.8176 | 121.8887 | 121.6447 | 121.7747 | -0.2328
1255.4375 | 121.962 | -121.756 | 0.12817 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0038527 | -0.012333 | 0.019057 | -0.24059 | -0.001002 | 0.00030124 | -0.0027753 | 0.032871 | 0.010108 | 0.074302 | 0.033457 | 0.028217 | 0.11165 | 0.050727 | 0.26101 | 0.092626 | 0.074307 | 0.041567 | 0.01233 | 0.089087 | 0.16938 | -0.074664 | -0.1321 | 121.8486 | -0.016527 | 121.8303 | 121.7842 | -0.064409 | -0.077447 | 0.13284 | 121.6239 | -0.039087 | 121.8303 | 121.7683 | 0.14443 | 0.041205 | -0.20284 | 121.8676 | 121.8067 | 122.017 | 121.7894 | -0.035548 | 121.8451 | 121.9254 | 121.6813 | 121.7975 | -0.26027
1257.1094 | 122.0352 | -121.7285 | 0.10986 | 1.4211e-13 | -0.029822 | 0.014252 | -0.0038527 | -0.012333 | 0.019057 | -0.24059 | -0.00078837 | 8.7636e-05 | -0.0029889 | 0.033299 | 0.010322 | 0.074302 | 0.0243 | 0.023639 | 0.11622 | 0.055306 | 0.25643 | 0.11094 | 0.078886 | 0.041567 | 0.007751 | 0.089087 | 0.16022 | -0.12503 | -0.12752 | 121.8395 | 0.006362 | 121.8028 | 121.7522 | -0.087303 | -0.054557 | 0.14657 | 121.601 | -0.020776 | 121.8074 | 121.7363 | 0.13527 | 0.050359 | -0.23489 | 121.8447 | 121.7838 | 121.9849 | 121.7528 | 0.001079 | 121.8176 | 121.8887 | 121.6035 | 121.7701 | -0.23738
1258.8438 | 121.9528 | -121.7514 | 0.13733 | 1.4211e-13 | -0.030036 | 0.013825 | -0.0038527 | -0.012119 | 0.01927 | -0.24059 | -0.0014292 | -0.00033976 | -0.0034163 | 0.033085 | 0.010108 | 0.069723 | 0.0243 | 0.023639 | 0.11165 | 0.055306 | 0.25643 | 0.088047 | 0.078886 | 0.041567 | 0.01233 | 0.084508 | 0.16022 | -0.097557 | -0.13668 | 121.8395 | -0.025682 | 121.8211 | 121.775 | -0.064408 | -0.082023 | 0.1191 | 121.6147 | -0.052821 | 121.8303 | 121.7637 | 0.14901 | 0.022893 | -0.23489 | 121.8631 | 121.8067 | 122.0078 | 121.7757 | -0.049282 | 121.8359 | 121.9116 | 121.6538 | 121.793 | -0.274
1260.5781 | 121.907 | -121.7514 | 0.13733 | 1.4211e-13 | -0.030036 | 0.014039 | -0.0040665 | -0.012119 | 0.018843 | -0.24059 | -0.0014292 | -0.00055336 | -0.0038435 | 0.033299 | 0.010108 | 0.074302 | 0.0243 | 0.028217 | 0.11622 | 0.059885 | 0.25185 | 0.10178 | 0.074307 | 0.036989 | 0.003172 | 0.089087 | 0.15564 | -0.047193 | -0.12294 | 121.8532 | -0.021104 | 121.8257 | 121.7796 | -0.073567 | -0.077444 | 0.11452 | 121.6285 | -0.048242 | 121.8257 | 121.7546 | 0.12611 | 0.018314 | -0.18452 | 121.8676 | 121.8113 | 122.0033 | 121.7757 | -0.035545 | 121.8405 | 121.907 | 121.7042 | 121.7884 | -0.26027
1262.3125 | 122.0169 | -121.7606 | 0.12817 | 1.4211e-13 | -0.030036 | 0.014252 | -0.0038527 | -0.01276 | 0.018843 | -0.23296 | -0.001643 | -0.00055336 | -0.0036299 | 0.033299 | 0.010108 | 0.074302 | 0.0243 | 0.028217 | 0.11165 | 0.059885 | 0.25643 | 0.097205 | 0.074307 | 0.041567 | 0.007751 | 0.093665 | 0.15564 | -0.065507 | -0.12752 | 121.8578 | -0.016527 | 121.8349 | 121.7888 | -0.068988 | -0.068289 | 0.12826 | 121.633 | -0.034509 | 121.8349 | 121.7683 | 0.13527 | 0.027469 | -0.19368 | 121.8722 | 121.8204 | 122.017 | 121.7849 | -0.030969 | 121.8542 | 121.9162 | 121.6951 | 121.8021 | -0.25569
1263.9844 | 122.049 | -121.7468 | 0.11902 | 1.4211e-13 | -0.030036 | 0.014252 | -0.0034253 | -0.012119 | 0.019057 | -0.24059 | -0.001643 | -0.00033976 | -0.0036299 | 0.033299 | 0.010108 | 0.074302 | 0.028878 | 0.023639 | 0.11165 | 0.059885 | 0.25643 | 0.092626 | 0.074307 | 0.041567 | 0.007751 | 0.093665 | 0.15107 | -0.11587 | -0.1321 | 121.8395 | -0.007372 | 121.8211 | 121.7705 | -0.068987 | -0.059134 | 0.13741 | 121.6147 | -0.025354 | 121.8211 | 121.7546 | 0.13985 | 0.032046 | -0.23489 | 121.8585 | 121.8067 | 122.0033 | 121.7757 | -0.026393 | 121.8405 | 121.8979 | 121.631 | 121.7884 | -0.25112
1265.7188 | 122.0123 | -121.7422 | 0.10071 | 1.4211e-13 | -0.030036 | 0.014252 | -0.0038527 | -0.012333 | 0.019057 | -0.23296 | -0.0014292 | -0.00033976 | -0.0034163 | 0.033085 | 0.010108 | 0.069723 | 0.0243 | 0.023639 | 0.12538 | 0.055306 | 0.25185 | 0.10178 | 0.074307 | 0.041567 | 0.01233 | 0.093665 | 0.16938 | -0.12503 | -0.13668 | 121.844 | 0.024674 | 121.812 | 121.7659 | -0.078145 | -0.045402 | 0.15114 | 121.6056 | -0.007043 | 121.8166 | 121.7546 | 0.14901 | 0.068671 | -0.22574 | 121.8676 | 121.7976 | 121.9941 | 121.7665 | 0.001076 | 121.8359 | 121.9116 | 121.6172 | 121.7838 | -0.23738
1267.4531 | 122.0535 | -121.7285 | 0.10529 | 1.4211e-13 | -0.030036 | 0.013825 | -0.0038527 | -0.012333 | 0.018629 | -0.24059 | -0.0018566 | -0.00076696 | -0.0038435 | 0.033299 | 0.010322 | 0.069723 | 0.0243 | 0.023639 | 0.1208 | 0.055306 | 0.26101 | 0.10178 | 0.078886 | 0.046146 | 0.01233 | 0.089087 | 0.1648 | -0.079243 | -0.1321 | 121.8303 | 0.015518 | 121.7982 | 121.7522 | -0.078145 | -0.04998 | 0.15572 | 121.5964 | -0.016199 | 121.8074 | 121.7408 | 0.14443 | 0.059514 | -0.18453 | 121.8493 | 121.7838 | 121.9895 | 121.7528 | -0.003502 | 121.8176 | 121.8933 | 121.6493 | 121.7747 | -0.23738
1269.1875 | 122.0078 | -121.7331 | 0.12817 | 1.4211e-13 | -0.030036 | 0.014252 | -0.0036391 | -0.012333 | 0.019484 | -0.22533 | -0.0020702 | -0.00055336 | -0.0042707 | 0.033085 | 0.010108 | 0.065145 | 0.028878 | 0.032795 | 0.11622 | 0.064464 | 0.25643 | 0.097205 | 0.078886 | 0.041567 | 0.003172 | 0.093665 | 0.1648 | -0.11129 | -0.1321 | 121.8303 | -0.011949 | 121.7982 | 121.7659 | -0.06441 | -0.06371 | 0.12826 | 121.601 | -0.034509 | 121.812 | 121.7363 | 0.13527 | 0.036626 | -0.23947 | 121.8493 | 121.7976 | 121.9895 | 121.762 | -0.030969 | 121.8268 | 121.8979 | 121.6218 | 121.7747 | -0.26027
1270.9531 | 121.9666 | -121.7697 | 0.1236 | 1.4211e-13 | -0.030036 | 0.014252 | -0.0038527 | -0.012546 | 0.019057 | -0.22533 | -0.0020702 | -0.00098076 | -0.0042707 | 0.033299 | 0.010322 | 0.074302 | 0.0243 | 0.028217 | 0.1208 | 0.059885 | 0.25643 | 0.11094 | 0.074307 | 0.046146 | 0.01233 | 0.093665 | 0.1648 | -0.092979 | -0.13668 | 121.8807 | -0.002792 | 121.844 | 121.7979 | -0.082725 | -0.063711 | 0.13284 | 121.633 | -0.029931 | 121.844 | 121.782 | 0.14901 | 0.041204 | -0.21658 | 121.8905 | 121.8296 | 122.0261 | 121.794 | -0.012654 | 121.8634 | 121.9345 | 121.6767 | 121.8159 | -0.26027
1272.6406 | 122.0306 | -121.7285 | 0.11902 | 1.4211e-13 | -0.029822 | 0.013825 | -0.0036391 | -0.012546 | 0.01927 | -0.24059 | -0.0018566 | -0.00076696 | -0.0040571 | 0.033299 | 0.0098942 | 0.074302 | 0.028878 | 0.023639 | 0.11622 | 0.059885 | 0.25643 | 0.11552 | 0.069728 | 0.036989 | 0.016908 | 0.07993 | 0.16938 | -0.083821 | -0.13668 | 121.844 | -0.002794 | 121.8028 | 121.7522 | -0.091882 | -0.059134 | 0.13741 | 121.5918 | -0.039089 | 121.7982 | 121.7454 | 0.15358 | 0.05036 | -0.20284 | 121.8447 | 121.7884 | 121.9849 | 121.7574 | -0.003498 | 121.8084 | 121.8979 | 121.6447 | 121.7655 | -0.2557
1274.3906 | 122.0627 | -121.7148 | 0.10986 | 1.4211e-13 | -0.030036 | 0.014039 | -0.0038527 | -0.012546 | 0.018843 | -0.23296 | -0.0018566 | -0.00076696 | -0.0042707 | 0.033299 | 0.010322 | 0.069723 | 0.019721 | 0.028217 | 0.11622 | 0.055306 | 0.26101 | 0.10178 | 0.083464 | 0.046146 | 0.01233 | 0.093665 | 0.15564 | -0.074664 | -0.12752 | 121.8166 | 0.006362 | 121.7845 | 121.743 | -0.073567 | -0.054557 | 0.15115 | 121.5873 | -0.016198 | 121.7982 | 121.7271 | 0.13985 | 0.04578 | -0.18453 | 121.831 | 121.7701 | 121.9758 | 121.7345 | -0.008079 | 121.8084 | 121.8704 | 121.6401 | 121.7609 | -0.23738
1276.0625 | 121.9986 | -121.7194 | 0.11902 | 1.4211e-13 | -0.029822 | 0.013611 | -0.0038527 | -0.012546 | 0.018629 | -0.23296 | -0.0018566 | -0.00076696 | -0.0040571 | 0.032871 | 0.010322 | 0.074302 | 0.028878 | 0.023639 | 0.11622 | 0.064464 | 0.25643 | 0.10636 | 0.074307 | 0.050725 | 0.016908 | 0.089087 | 0.1648 | -0.12045 | -0.1321 | 121.8257 | -0.002794 | 121.7937 | 121.743 | -0.082724 | -0.054555 | 0.13741 | 121.5873 | -0.029932 | 121.7937 | 121.7363 | 0.149 | 0.045781 | -0.23947 | 121.8356 | 121.7838 | 121.9758 | 121.7482 | -0.012656 | 121.8084 | 121.8842 | 121.5989 | 121.7701 | -0.25112
1277.8125 | 122.0261 | -121.7194 | 0.11444 | 1.4211e-13 | -0.03025 | 0.014466 | -0.0038527 | -0.012119 | 0.018843 | -0.23296 | -0.001643 | -0.00055336 | -0.0040571 | 0.033299 | 0.010322 | 0.074302 | 0.0243 | 0.028217 | 0.11622 | 0.064464 | 0.25185 | 0.10178 | 0.074307 | 0.041567 | 0.007751 | 0.093665 | 0.16938 | -0.12961 | -0.12752 | 121.8211 | 0.001784 | 121.7937 | 121.7476 | -0.073567 | -0.049977 | 0.13741 | 121.5918 | -0.020776 | 121.7937 | 121.7271 | 0.13527 | 0.054938 | -0.24405 | 121.8356 | 121.7838 | 121.9712 | 121.7437 | -0.012657 | 121.813 | 121.8887 | 121.5898 | 121.7609 | -0.24196
1279.5625 | 121.994 | -121.7239 | 0.09613 | 1.4211e-13 | -0.030036 | 0.014039 | -0.0038527 | -0.012546 | 0.019057 | -0.24059 | -0.0018566 | -0.00076696 | -0.0040571 | 0.033085 | 0.010108 | 0.074302 | 0.028878 | 0.023639 | 0.11165 | 0.059885 | 0.25643 | 0.10178 | 0.074307 | 0.046146 | 0.016908 | 0.093665 | 0.16938 | -0.10671 | -0.1321 | 121.8257 | 0.015517 | 121.7982 | 121.7476 | -0.078145 | -0.036245 | 0.1603 | 121.5918 | -0.002465 | 121.7982 | 121.7408 | 0.149 | 0.073249 | -0.20284 | 121.8356 | 121.7838 | 121.9804 | 121.7528 | 0.005654 | 121.8176 | 121.8933 | 121.6172 | 121.7701 | -0.22823
1281.2969 | 121.9803 | -121.7285 | 0.1236 | 1.4211e-13 | -0.030036 | 0.014039 | -0.0034253 | -0.012333 | 0.019057 | -0.23296 | -0.0018566 | -0.00076696 | -0.0040571 | 0.033299 | 0.0098942 | 0.074302 | 0.0243 | 0.028217 | 0.1208 | 0.059885 | 0.25643 | 0.11552 | 0.074307 | 0.041567 | 0.007751 | 0.093665 | 0.16938 | -0.0884 | -0.12752 | 121.844 | -0.002792 | 121.8028 | 121.7567 | -0.087304 | -0.063711 | 0.13284 | 121.601 | -0.029931 | 121.8028 | 121.7363 | 0.13527 | 0.045783 | -0.212 | 121.8493 | 121.7884 | 121.9849 | 121.7528 | -0.008075 | 121.8222 | 121.8979 | 121.6401 | 121.7701 | -0.25111
1282.9844 | 121.8933 | -121.7285 | 0.13733 | 1.4211e-13 | -0.030036 | 0.014252 | -0.0036391 | -0.012546 | 0.019057 | -0.23296 | -0.0022838 | -0.00098076 | -0.0042707 | 0.033299 | 0.010108 | 0.074302 | 0.028878 | 0.023639 | 0.11622 | 0.055306 | 0.25643 | 0.10636 | 0.078886 | 0.046146 | 0.007751 | 0.098244 | 0.16022 | -0.070086 | -0.1321 | 121.8349 | -0.021104 | 121.8028 | 121.7522 | -0.082724 | -0.082023 | 0.1191 | 121.5964 | -0.039085 | 121.8074 | 121.7363 | 0.13985 | 0.022893 | -0.20742 | 121.8447 | 121.7838 | 121.9849 | 121.7574 | -0.030966 | 121.8268 | 121.8887 | 121.6584 | 121.7747 | -0.26943
1284.7344 | 121.8155 | -120.8679 | 0.79651 | 1.4211e-13 | -0.03025 | 0.014039 | -0.0038527 | -0.01276 | 0.019057 | -0.23296 | 0.028694 | 0.029359 | 0.026067 | 0.033299 | 0.0096806 | 0.07888 | 0.033457 | 0.037373 | 0.12996 | 0.059885 | 0.26101 | 0.097205 | 0.21625 | 0.18809 | 0.15885 | 0.24476 | 0.31589 | 0.168 | 0.014425 | 120.9651 | -0.66655 | 120.9468 | 120.9053 | -0.059832 | -0.73662 | -0.5355 | 120.8823 | -0.55175 | 121.0842 | 121.0268 | 0.14442 | -0.48062 | -0.62851 | 120.9979 | 120.9278 | 121.1289 | 120.9014 | -0.6993 | 121.1127 | 121.1838 | 121.0359 | 121.056 | -0.78208
1286.4844 | 121.4813 | -9.1187 | 112.5916 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0040665 | -0.012333 | 0.019057 | -0.24822 | 0.018012 | 0.019958 | 0.014957 | 0.033512 | 0.010322 | 0.010204 | -0.030644 | -0.031301 | 0.056706 | -0.063746 | 0.19691 | -0.085952 | 0.023941 | -0.022535 | -0.065509 | 0.024988 | 0.091543 | -0.13419 | -0.20994 | 9.0327 | -112.5348 | 9.1289 | 9.0874 | 0.054651 | -112.6553 | -112.3946 | 8.9087 | -112.5666 | 9.1426 | 9.0531 | 0.14443 | -112.5 | -112.7257 | 9.1754 | 9.0549 | 9.3156 | 9.088 | -112.6775 | 9.1436 | 9.2102 | 8.9845 | 9.0961 | -112.8015
1288.2344 | 121.6873 | -8.7753 | 112.9669 | 1.4211e-13 | -0.029822 | 0.013825 | -0.0040665 | -0.012546 | 0.019057 | -0.24059 | 0.018225 | 0.019958 | 0.014957 | 0.033085 | 0.0098942 | 0.014783 | -0.035222 | -0.040457 | 0.061284 | -0.063746 | 0.19233 | -0.11342 | 0.019362 | -0.017956 | -0.06093 | 0.020409 | 0.091543 | -0.12961 | -0.20994 | 8.6619 | -112.9056 | 8.7901 | 8.7349 | 0.072968 | -113.0307 | -112.7746 | 8.5654 | -112.9465 | 8.7947 | 8.7144 | 0.14901 | -112.8754 | -113.0965 | 8.8366 | 8.7116 | 8.9677 | 8.7401 | -113.0803 | 8.7957 | 8.8669 | 8.6457 | 8.7574 | -113.1769
1289.9219 | 121.7194 | -9.2148 | 112.5229 | 1.4211e-13 | -0.030036 | 0.014039 | -0.0040665 | -0.012546 | 0.018629 | -0.22533 | 0.018012 | 0.019958 | 0.014957 | 0.033085 | 0.0098942 | 0.010204 | -0.035222 | -0.031301 | 0.042971 | -0.072904 | 0.19691 | -0.118 | 0.023941 | -0.017956 | -0.06093 | 0.020409 | 0.091543 | -0.12961 | -0.20078 | 9.0968 | -112.4799 | 9.225 | 9.1835 | 0.086703 | -112.5958 | -112.326 | 9.014 | -112.5025 | 9.2387 | 9.1539 | 0.13985 | -112.4313 | -112.6525 | 9.2578 | 9.1419 | 9.4117 | 9.1796 | -112.6409 | 9.2352 | 9.3063 | 9.0852 | 9.1968 | -112.7237
1291.6719 | 121.6919 | -8.8806 | 112.8845 | 1.4211e-13 | -0.030036 | 0.014252 | -0.0038527 | -0.012333 | 0.019057 | -0.22533 | 0.018012 | 0.019744 | 0.014744 | 0.033299 | 0.010322 | 0.010204 | -0.030644 | -0.035879 | 0.056706 | -0.072904 | 0.19233 | -0.11342 | 0.019362 | -0.027113 | -0.065509 | 0.015831 | 0.091543 | -0.14334 | -0.20994 | 8.7672 | -112.8278 | 8.8908 | 8.8447 | 0.077546 | -112.9574 | -112.6922 | 8.6707 | -112.8687 | 8.9 | 8.8151 | 0.14443 | -112.793 | -113.0279 | 8.9373 | 8.8077 | 9.0729 | 8.85 | -112.9979 | 8.8964 | 8.9722 | 8.7373 | 8.8535 | -113.0945
1293.4219 | 121.8796 | -8.6472 | 113.0859 | 1.4211e-13 | -0.030036 | 0.014039 | -0.0036391 | -0.01276 | 0.018843 | -0.23296 | 0.018012 | 0.019744 | 0.015171 | 0.033299 | 0.0098942 | 0.019361 | -0.035222 | -0.040457 | 0.047549 | -0.063746 | 0.19233 | -0.11342 | 0.010205 | -0.017956 | -0.056351 | 0.011252 | 0.086964 | -0.13419 | -0.20994 | 8.5337 | -113.0384 | 8.6665 | 8.6067 | 0.072968 | -113.1497 | -112.8936 | 8.4372 | -113.0747 | 8.6574 | 8.5908 | 0.15359 | -112.999 | -113.2201 | 8.6947 | 8.5834 | 8.8395 | 8.6119 | -113.1994 | 8.6584 | 8.7341 | 8.513 | 8.6292 | -113.2959
1295.1562 | 121.7972 | -9.2514 | 112.4771 | 1.4211e-13 | -0.029822 | 0.014252 | -0.0036391 | -0.012333 | 0.019057 | -0.23296 | 0.018012 | 0.019744 | 0.014744 | 0.033299 | 0.010322 | 0.010204 | -0.039801 | -0.035879 | 0.052128 | -0.063746 | 0.19691 | -0.11342 | 0.014784 | -0.017956 | -0.06093 | 0.024988 | 0.091543 | -0.13876 | -0.20536 | 9.138 | -112.425 | 9.2616 | 9.2155 | 0.077546 | -112.5409 | -112.2802 | 9.046 | -112.4521 | 9.2662 | 9.1905 | 0.14443 | -112.3856 | -112.6159 | 9.3035 | 9.1877 | 9.4483 | 9.2116 | -112.5905 | 9.2764 | 9.3429 | 9.1126 | 9.2334 | -112.6825
1296.9062 | 121.8155 | -9.3063 | 112.4634 | 1.4211e-13 | -0.029822 | 0.013825 | -0.0034253 | -0.012546 | 0.018629 | -0.22533 | 0.018012 | 0.01953 | 0.015812 | 0.033512 | 0.0098942 | 0.005626 | -0.030644 | -0.031301 | 0.056706 | -0.068325 | 0.18775 | -0.076794 | 0.019362 | -0.017956 | -0.06093 | 0.029566 | 0.091543 | -0.13876 | -0.20536 | 9.2295 | -112.4067 | 9.312 | 9.275 | 0.045493 | -112.5317 | -112.2756 | 9.101 | -112.4338 | 9.3257 | 9.2454 | 0.14443 | -112.3718 | -112.6021 | 9.363 | 9.238 | 9.4941 | 9.2757 | -112.5402 | 9.3359 | 9.3979 | 9.1676 | 9.2884 | -112.6687
1298.5938 | 121.8384 | -8.8486 | 112.9028 | 1.4211e-13 | -0.03025 | 0.014039 | -0.0036391 | -0.012546 | 0.018629 | -0.24822 | 0.018225 | 0.019744 | 0.016026 | 0.033085 | 0.010322 | 0.014783 | -0.035222 | -0.035879 | 0.052128 | -0.059167 | 0.19691 | -0.13174 | 0.010205 | -0.022535 | -0.070087 | 0.015831 | 0.091543 | -0.13876 | -0.1962 | 8.7168 | -112.8507 | 8.8634 | 8.8127 | 0.095862 | -112.962 | -112.7059 | 8.6524 | -112.887 | 8.8588 | 8.7785 | 0.12611 | -112.8113 | -113.0416 | 8.9007 | 8.7894 | 9.0455 | 8.8134 | -113.0346 | 8.8644 | 8.9401 | 8.7098 | 8.826 | -113.099
1300.3438 | 121.8246 | -8.3817 | 113.4064 | 1.4211e-13 | -0.03025 | 0.014039 | -0.0038527 | -0.012546 | 0.019057 | -0.23296 | 0.018439 | 0.019744 | 0.016239 | 0.033299 | 0.010108 | 0.014783 | -0.035222 | -0.031301 | 0.056706 | -0.068325 | 0.19233 | -0.090531 | 0.014784 | -0.022535 | -0.065509 | 0.020409 | 0.096121 | -0.13876 | -0.20536 | 8.2911 | -113.3497 | 8.3964 | 8.3504 | 0.05923 | -113.4747 | -113.214 | 8.1763 | -113.386 | 8.3964 | 8.3161 | 0.13985 | -113.3103 | -113.5451 | 8.4384 | 8.3133 | 8.574 | 8.3464 | -113.4969 | 8.4021 | 8.4778 | 8.2429 | 8.3591 | -113.6117
1302.0625 | 121.7743 | -8.8989 | 112.9211 | 1.4211e-13 | -0.030036 | 0.014252 | -0.0036391 | -0.012974 | 0.018843 | -0.24059 | 0.018225 | 0.020171 | 0.015812 | 0.033512 | 0.010108 | 0.010204 | -0.026065 | -0.031301 | 0.061284 | -0.063746 | 0.20149 | -0.09511 | 0.014784 | -0.027113 | -0.065509 | 0.020409 | 0.086964 | -0.13876 | -0.20536 | 8.8038 | -112.8599 | 8.9091 | 8.8676 | 0.063809 | -112.9849 | -112.7197 | 8.6936 | -112.9007 | 8.9137 | 8.8334 | 0.13985 | -112.8342 | -113.0599 | 8.9602 | 8.8352 | 9.1004 | 8.8729 | -113.0163 | 8.9193 | 8.9859 | 8.7602 | 8.8718 | -113.1265
1303.7656 | 121.9162 | -8.1116 | 113.6261 | 1.4211e-13 | -0.030036 | 0.014252 | -0.0036391 | -0.012546 | 0.01927 | -0.23296 | 0.018012 | 0.019958 | 0.016026 | 0.033512 | 0.0098942 | 0.014783 | -0.035222 | -0.031301 | 0.047549 | -0.059167 | 0.20149 | -0.12716 | 0.019362 | -0.022535 | -0.06093 | 0.015831 | 0.086964 | -0.13876 | -0.20078 | 7.9844 | -113.5785 | 8.1264 | 8.0803 | 0.095861 | -113.6853 | -113.4246 | 7.9108 | -113.6103 | 8.1309 | 8.0506 | 0.13985 | -113.5391 | -113.7649 | 8.1591 | 8.0524 | 8.3131 | 8.0764 | -113.7533 | 8.1274 | 8.1985 | 7.9728 | 8.089 | -113.8269
1305.4531 | 121.9574 | -8.4457 | 113.2874 | 1.4211e-13 | -0.029822 | 0.014252 | -0.0036391 | -0.012333 | 0.019057 | -0.23296 | 0.018012 | 0.019744 | 0.015812 | 0.033512 | 0.010108 | 0.019361 | -0.035222 | -0.031301 | 0.047549 | -0.059167 | 0.19233 | -0.13174 | 0.019362 | -0.013377 | -0.065509 | 0.015831 | 0.091543 | -0.13419 | -0.20536 | 8.314 | -113.2398 | 8.4651 | 8.4144 | 0.10044 | -113.3465 | -113.095 | 8.2404 | -113.2715 | 8.4651 | 8.3802 | 0.13985 | -113.1958 | -113.4215 | 8.4933 | 8.3866 | 8.6381 | 8.4105 | -113.4191 | 8.4616 | 8.5373 | 8.3116 | 8.4324 | -113.4927
1307.1562 | 121.907 | -8.8852 | 112.8616 | 1.4211e-13 | -0.03025 | 0.014039 | -0.0038527 | -0.012546 | 0.01927 | -0.24822 | 0.018225 | 0.020171 | 0.015812 | 0.033299 | 0.010535 | 0.019361 | -0.026065 | -0.040457 | 0.052128 | -0.063746 | 0.18317 | -0.10427 | 0.014784 | -0.022535 | -0.065509 | 0.020409 | 0.091543 | -0.13876 | -0.20536 | 8.7809 | -112.8095 | 8.9046 | 8.8447 | 0.063811 | -112.9254 | -112.6785 | 8.6798 | -112.8412 | 8.9 | 8.8197 | 0.13985 | -112.7701 | -113.0004 | 8.9373 | 8.8214 | 9.0684 | 8.8591 | -112.9659 | 8.9056 | 8.9767 | 8.7464 | 8.8627 | -113.067
1308.8438 | 121.9345 | -8.2855 | 113.4842 | 1.4211e-13 | -0.029822 | 0.014466 | -0.0034253 | -0.012546 | 0.019057 | -0.24822 | 0.018225 | 0.019958 | 0.016026 | 0.033512 | 0.010108 | 0.005626 | -0.039801 | -0.031301 | 0.056706 | -0.063746 | 0.20149 | -0.09511 | 0.019362 | -0.022535 | -0.065509 | 0.015831 | 0.091543 | -0.13419 | -0.20994 | 8.1904 | -113.4275 | 8.2911 | 8.2542 | 0.063809 | -113.5479 | -113.2827 | 8.0756 | -113.4684 | 8.3049 | 8.22 | 0.14443 | -113.3926 | -113.6184 | 8.3422 | 8.2218 | 8.487 | 8.2457 | -113.5793 | 8.3014 | 8.3771 | 8.1513 | 8.263 | -113.6941
1310.5469 | 121.9666 | -8.931 | 112.8204 | 1.4211e-13 | -0.029822 | 0.013825 | -0.0038527 | -0.012546 | 0.018843 | -0.2177 | 0.018012 | 0.018889 | 0.015598 | 0.033512 | 0.0098942 | 0.014783 | -0.035222 | -0.031301 | 0.052128 | -0.063746 | 0.19233 | -0.081373 | 0.019362 | -0.017956 | -0.070087 | 0.024988 | 0.086964 | -0.13876 | -0.20994 | 8.8496 | -112.7683 | 8.9458 | 8.8997 | 0.050072 | -112.8842 | -112.6281 | 8.721 | -112.7954 | 8.9503 | 8.8609 | 0.13985 | -112.7335 | -112.9592 | 8.9831 | 8.8672 | 9.1233 | 8.8957 | -112.9018 | 8.956 | 9.0179 | 8.7922 | 8.913 | -113.0304
1312.2344 | 121.8658 | -8.6197 | 113.1821 | 1.4211e-13 | -0.030036 | 0.014252 | -0.0036391 | -0.01276 | 0.018629 | -0.22533 | 0.018012 | 0.018676 | 0.016026 | 0.033512 | 0.010108 | 0.005626 | -0.030644 | -0.035879 | 0.052128 | -0.054588 | 0.19233 | -0.09511 | 0.02852 | -0.017956 | -0.070087 | 0.024988 | 0.096121 | -0.13876 | -0.20536 | 8.5246 | -113.1299 | 8.6253 | 8.5838 | 0.059231 | -113.2367 | -112.9897 | 8.4143 | -113.1571 | 8.6482 | 8.5496 | 0.13527 | -113.0859 | -113.3208 | 8.6718 | 8.5651 | 8.812 | 8.589 | -113.2772 | 8.6447 | 8.7158 | 8.4809 | 8.6017 | -113.3874
1313.9375 | 121.8704 | -8.9539 | 112.8708 | 1.4211e-13 | -0.03025 | 0.014039 | -0.0038527 | -0.012546 | 0.018843 | -0.23296 | 0.018439 | 0.018676 | 0.015812 | 0.033512 | 0.010535 | 0.014783 | -0.035222 | -0.031301 | 0.052128 | -0.063746 | 0.19233 | -0.11342 | 0.023941 | -0.022535 | -0.056351 | 0.015831 | 0.082386 | -0.13419 | -0.21452 | 8.8404 | -112.8187 | 8.9686 | 8.9226 | 0.082124 | -112.9345 | -112.6785 | 8.7393 | -112.855 | 8.9778 | 8.8975 | 0.15817 | -112.7884 | -113.005 | 9.006 | 8.8901 | 9.1462 | 8.9186 | -112.9842 | 8.9697 | 9.0362 | 8.8197 | 8.9313 | -113.0853
1315.6094 | 121.8658 | -8.9722 | 112.8662 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0036391 | -0.01276 | 0.019057 | -0.23296 | 0.018012 | 0.018676 | 0.016239 | 0.033512 | 0.010108 | 0.010204 | -0.030644 | -0.031301 | 0.061284 | -0.059167 | 0.19691 | -0.10427 | 0.019362 | -0.022535 | -0.065509 | 0.020409 | 0.082386 | -0.13419 | -0.20994 | 8.8679 | -112.8049 | 8.9824 | 8.9409 | 0.072967 | -112.9254 | -112.6693 | 8.7622 | -112.8458 | 8.9915 | 8.9067 | 0.14443 | -112.7838 | -113.0004 | 9.0335 | 8.913 | 9.1691 | 8.9415 | -112.9705 | 8.9926 | 9.0546 | 8.838 | 8.9496 | -113.0761
1317.2812 | 121.907 | -8.5281 | 113.2507 | 1.4211e-13 | -0.03025 | 0.013611 | -0.0036391 | -0.012119 | 0.019057 | -0.23296 | 0.018225 | 0.018676 | 0.015812 | 0.033726 | 0.0098942 | 0.010204 | -0.030644 | -0.031301 | 0.056706 | -0.063746 | 0.18775 | -0.11342 | 0.019362 | -0.017956 | -0.065509 | 0.015831 | 0.082386 | -0.13419 | -0.20536 | 8.4147 | -113.194 | 8.5383 | 8.4968 | 0.082124 | -113.3145 | -113.063 | 8.3228 | -113.2349 | 8.5475 | 8.4626 | 0.13985 | -113.1683 | -113.3849 | 8.5848 | 8.4644 | 8.7159 | 8.4975 | -113.3642 | 8.544 | 8.6105 | 8.394 | 8.5102 | -113.4561
1318.9688 | 121.9711 | -8.725 | 113.0493 | 1.4211e-13 | -0.029822 | 0.013825 | -0.0032117 | -0.012546 | 0.018843 | -0.23296 | 0.018012 | 0.018889 | 0.016239 | 0.033726 | 0.0098942 | 0.010204 | -0.030644 | -0.035879 | 0.052128 | -0.059167 | 0.19233 | -0.12716 | 0.023941 | -0.027113 | -0.06093 | 0.020409 | 0.091543 | -0.13419 | -0.20536 | 8.5978 | -112.9972 | 8.7352 | 8.6891 | 0.091283 | -113.1085 | -112.857 | 8.5196 | -113.0289 | 8.7489 | 8.664 | 0.14443 | -112.9578 | -113.1835 | 8.7771 | 8.6658 | 8.9173 | 8.6943 | -113.1765 | 8.7454 | 8.8165 | 8.5908 | 8.6979 | -113.2547
1320.6406 | 121.9666 | -9.05 | 112.7563 | 1.4211e-13 | -0.03025 | 0.014252 | -0.0038527 | -0.01276 | 0.018843 | -0.24059 | 0.018012 | 0.018676 | 0.016026 | 0.033085 | 0.010322 | 0.005626 | -0.030644 | -0.035879 | 0.056706 | -0.063746 | 0.19233 | -0.118 | 0.019362 | -0.022535 | -0.065509 | 0.024988 | 0.091543 | -0.13876 | -0.20536 | 8.932 | -112.6996 | 9.0556 | 9.0141 | 0.082125 | -112.8201 | -112.564 | 8.8446 | -112.7314 | 9.0694 | 8.9845 | 0.13985 | -112.6648 | -112.8951 | 9.1067 | 8.9862 | 9.2423 | 9.0193 | -112.8744 | 9.075 | 9.1415 | 8.9112 | 9.0275 | -112.9617
1322.3281 | 121.9803 | -8.6929 | 113.0676 | 1.4211e-13 | -0.03025 | 0.014252 | -0.0034253 | -0.012546 | 0.019057 | -0.24059 | 0.017798 | 0.018676 | 0.016239 | 0.033512 | 0.0098942 | 0.005626 | -0.035222 | -0.035879 | 0.047549 | -0.063746 | 0.20149 | -0.10885 | 0.023941 | -0.017956 | -0.065509 | 0.020409 | 0.091543 | -0.13876 | -0.20536 | 8.5841 | -113.0201 | 8.6986 | 8.6571 | 0.072968 | -113.1314 | -112.8661 | 8.4876 | -113.0472 | 8.7169 | 8.6274 | 0.13985 | -112.9761 | -113.2064 | 8.7405 | 8.6292 | 8.8944 | 8.6577 | -113.1765 | 8.7133 | 8.7845 | 8.5542 | 8.675 | -113.273
1324 | 121.962 | -8.6746 | 113.0722 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0034253 | -0.012546 | 0.018843 | -0.22533 | 0.018439 | 0.019103 | 0.015812 | 0.033512 | 0.010108 | 0.005626 | -0.030644 | -0.035879 | 0.056706 | -0.059167 | 0.20607 | -0.12258 | 0.02852 | -0.022535 | -0.06093 | 0.015831 | 0.091543 | -0.13419 | -0.20536 | 8.552 | -113.0155 | 8.6802 | 8.6387 | 0.086704 | -113.1314 | -112.8661 | 8.4693 | -113.0564 | 8.7031 | 8.6137 | 0.14443 | -112.9807 | -113.2064 | 8.7313 | 8.6155 | 8.8807 | 8.644 | -113.1948 | 8.6905 | 8.7662 | 8.5404 | 8.6521 | -113.2776
1325.6875 | 121.9162 | -8.7341 | 113.0402 | 1.4211e-13 | -0.03025 | 0.014039 | -0.0040665 | -0.01276 | 0.018843 | -0.24059 | 0.018012 | 0.018889 | 0.015812 | 0.033512 | 0.010108 | 0.010204 | -0.030644 | -0.040457 | 0.056706 | -0.072904 | 0.19691 | -0.12258 | 0.014784 | -0.027113 | -0.06093 | 0.015831 | 0.091543 | -0.13419 | -0.20536 | 8.6115 | -112.9835 | 8.7443 | 8.6937 | 0.082126 | -113.1131 | -112.8433 | 8.5288 | -113.0243 | 8.7489 | 8.6732 | 0.14443 | -112.9486 | -113.1743 | 8.7908 | 8.6612 | 8.931 | 8.7035 | -113.1627 | 8.75 | 8.8257 | 8.5999 | 8.707 | -113.2455
1327.4062 | 121.9299 | -14.6896 | 107.1259 | 1.4211e-13 | -0.030036 | 0.014039 | -0.0038527 | -0.01276 | 0.018843 | -0.24059 | 0.018012 | 0.018889 | 0.015598 | 0.033512 | 0.010108 | 0.019361 | -0.035222 | -0.026723 | 0.056706 | -0.063746 | 0.19233 | -0.10885 | 0.02852 | -0.027113 | -0.06093 | 0.029566 | 0.091543 | -0.13419 | -0.20536 | 14.5808 | -107.0691 | 14.709 | 14.6629 | 0.082124 | -107.1896 | -106.9335 | 14.4843 | -107.0963 | 14.7182 | 14.6287 | 0.14443 | -107.0343 | -107.26 | 14.7463 | 14.6259 | 14.882 | 14.6544 | -107.2347 | 14.7192 | 14.7812 | 14.5555 | 14.6625 | -107.3312
1329.0938 | 121.8567 | -12.4008 | 109.4604 | 1.4211e-13 | -0.03025 | 0.014039 | -0.0034253 | -0.012546 | 0.019057 | -0.23296 | 0.018012 | 0.019103 | 0.015812 | 0.033512 | 0.010108 | 0.005626 | -0.039801 | -0.031301 | 0.056706 | -0.059167 | 0.19691 | -0.118 | 0.023941 | -0.017956 | -0.065509 | 0.024988 | 0.091543 | -0.13876 | -0.20078 | 12.2828 | -109.4037 | 12.4064 | 12.3695 | 0.086703 | -109.5196 | -109.2635 | 12.2 | -109.4355 | 12.4248 | 12.3353 | 0.13527 | -109.3689 | -109.5992 | 12.4575 | 12.3417 | 12.5977 | 12.361 | -109.5785 | 12.4258 | 12.4924 | 12.2621 | 12.3829 | -109.6612
1330.8594 | 121.843 | -11.3068 | 110.5362 | 1.4211e-13 | -0.03025 | 0.014039 | -0.0036391 | -0.012333 | 0.019057 | -0.2177 | 0.018225 | 0.018676 | 0.015812 | 0.033512 | 0.010108 | 0.014783 | -0.035222 | -0.031301 | 0.047549 | -0.063746 | 0.19691 | -0.11342 | 0.014784 | -0.022535 | -0.065509 | 0.020409 | 0.096121 | -0.13419 | -0.20078 | 11.1933 | -110.4886 | 11.3215 | 11.2755 | 0.082124 | -110.5999 | -110.3393 | 11.106 | -110.5158 | 11.3215 | 11.2413 | 0.13527 | -110.4401 | -110.6704 | 11.3543 | 11.243 | 11.5037 | 11.2715 | -110.6496 | 11.3272 | 11.4029 | 11.1726 | 11.2842 | -110.737
1332.5938 | 121.8384 | -11.5036 | 110.3806 | 1.4211e-13 | -0.030036 | 0.014039 | -0.0038527 | -0.012333 | 0.018843 | -0.24059 | 0.018439 | 0.018676 | 0.015598 | 0.033512 | 0.010108 | 0.010204 | -0.035222 | -0.031301 | 0.061284 | -0.059167 | 0.19691 | -0.067636 | 0.019362 | -0.027113 | -0.070087 | 0.029566 | 0.091543 | -0.14334 | -0.20994 | 11.436 | -110.3193 | 11.5138 | 11.4723 | 0.036335 | -110.4397 | -110.1836 | 11.2937 | -110.351 | 11.523 | 11.4335 | 0.13985 | -110.289 | -110.5239 | 11.5649 | 11.4444 | 11.7005 | 11.4684 | -110.4482 | 11.5332 | 11.5951 | 11.3603 | 11.4765 | -110.5905
1334.2812 | 121.9254 | -11.2015 | 110.5728 | 1.4211e-13 | -0.03025 | 0.014039 | -0.0038527 | -0.012546 | 0.018843 | -0.22533 | 0.018012 | 0.018889 | 0.015598 | 0.033512 | 0.0098942 | 0.010204 | -0.026065 | -0.035879 | 0.052128 | -0.063746 | 0.20149 | -0.118 | 0.023941 | -0.022535 | -0.065509 | 0.015831 | 0.1007 | -0.13419 | -0.20078 | 11.0835 | -110.5207 | 11.2117 | 11.1656 | 0.082125 | -110.6366 | -110.3713 | 11.0007 | -110.557 | 11.2254 | 11.136 | 0.13527 | -110.4721 | -110.707 | 11.2536 | 11.1377 | 11.403 | 11.1754 | -110.6908 | 11.2173 | 11.3022 | 11.0673 | 11.1789 | -110.7736
1336.0312 | 121.8521 | -11.1786 | 110.6873 | 1.4211e-13 | -0.029822 | 0.014252 | -0.0036391 | -0.012974 | 0.018629 | -0.22533 | 0.018012 | 0.018889 | 0.015598 | 0.033726 | 0.010108 | 0.019361 | -0.030644 | -0.026723 | 0.056706 | -0.068325 | 0.20149 | -0.099689 | 0.014784 | -0.022535 | -0.065509 | 0.020409 | 0.096121 | -0.13419 | -0.20536 | 11.0789 | -110.6305 | 11.198 | 11.1519 | 0.072966 | -110.7556 | -110.4858 | 10.9732 | -110.6668 | 11.1934 | 11.1131 | 0.13985 | -110.5911 | -110.8214 | 11.2353 | 11.1103 | 11.3801 | 11.1479 | -110.7869 | 11.199 | 11.2747 | 11.0444 | 11.1561 | -110.8926
1337.7812 | 121.9757 | -11.3388 | 110.4538 | 1.4211e-13 | -0.030463 | 0.014039 | -0.0040665 | -0.012333 | 0.019057 | -0.23296 | 0.018012 | 0.018462 | 0.015812 | 0.033299 | 0.010108 | 0.010204 | -0.035222 | -0.031301 | 0.052128 | -0.059167 | 0.19691 | -0.10885 | 0.023941 | -0.017956 | -0.06093 | 0.020409 | 0.1007 | -0.13419 | -0.20078 | 11.23 | -110.4017 | 11.349 | 11.3075 | 0.077546 | -110.513 | -110.2569 | 11.138 | -110.4334 | 11.3627 | 11.2779 | 0.13985 | -110.3531 | -110.588 | 11.3909 | 11.2796 | 11.5357 | 11.3036 | -110.5626 | 11.3592 | 11.4395 | 11.2046 | 11.3209 | -110.6546
1339.5312 | 121.8384 | -11.2473 | 110.582 | 1.4211e-13 | -0.030036 | 0.014252 | -0.0036391 | -0.012974 | 0.019057 | -0.24059 | 0.018225 | 0.019103 | 0.015812 | 0.033299 | 0.010108 | 0.005626 | -0.030644 | -0.031301 | 0.065863 | -0.063746 | 0.20149 | -0.118 | 0.023941 | -0.013377 | -0.056351 | 0.020409 | 0.096121 | -0.13419 | -0.20536 | 11.1292 | -110.5161 | 11.2529 | 11.216 | 0.086703 | -110.6457 | -110.3805 | 11.0419 | -110.5616 | 11.2712 | 11.1909 | 0.14901 | -110.4858 | -110.7162 | 11.3131 | 11.1835 | 11.4487 | 11.2166 | -110.7 | 11.2677 | 11.3434 | 11.1131 | 11.2339 | -110.7873
1341.2188 | 121.8796 | -11.1832 | 110.6598 | 1.4211e-13 | -0.03025 | 0.014039 | -0.0036391 | -0.012546 | 0.018629 | -0.2177 | 0.018225 | 0.018889 | 0.015812 | 0.033726 | 0.010108 | 0.014783 | -0.035222 | -0.031301 | 0.052128 | -0.063746 | 0.19691 | -0.09511 | 0.014784 | -0.017956 | -0.065509 | 0.024988 | 0.091543 | -0.12961 | -0.20078 | 11.0881 | -110.6077 | 11.1979 | 11.1519 | 0.063809 | -110.7235 | -110.4629 | 10.9824 | -110.6348 | 11.198 | 11.1177 | 0.13527 | -110.5682 | -110.7894 | 11.2353 | 11.1194 | 11.3801 | 11.1479 | -110.7549 | 11.2082 | 11.2747 | 11.0536 | 11.1652 | -110.8606
1342.9531 | 121.9666 | -9.6359 | 112.1384 | 1.4211e-13 | -0.030036 | 0.014039 | -0.0038527 | -0.012546 | 0.019057 | -0.24059 | 0.018439 | 0.018676 | 0.016026 | 0.033085 | 0.010108 | 0.010204 | -0.030644 | -0.035879 | 0.056706 | -0.063746 | 0.20149 | -0.13174 | 0.023941 | -0.027113 | -0.056351 | 0.024988 | 0.096121 | -0.14334 | -0.20536 | 9.5042 | -112.0817 | 9.6461 | 9.6 | 0.095862 | -112.2021 | -111.9369 | 9.4306 | -112.1134 | 9.6599 | 9.5796 | 0.14901 | -112.0422 | -112.2817 | 9.6926 | 9.5722 | 9.8374 | 9.6053 | -112.2701 | 9.6609 | 9.732 | 9.4926 | 9.6088 | -112.3437
1344.7031 | 121.8658 | -9.4711 | 112.3856 | 1.4211e-13 | -0.029822 | 0.014252 | -0.0036391 | -0.012546 | 0.019057 | -0.23296 | 0.018225 | 0.018889 | 0.016026 | 0.033299 | 0.010108 | 0.014783 | -0.035222 | -0.031301 | 0.052128 | -0.063746 | 0.19691 | -0.10885 | 0.019362 | -0.022535 | -0.065509 | 0.024988 | 0.096121 | -0.13419 | -0.20994 | 9.3623 | -112.3334 | 9.4859 | 9.4398 | 0.077546 | -112.4493 | -112.1886 | 9.2612 | -112.3606 | 9.4905 | 9.4056 | 0.14443 | -112.2894 | -112.5197 | 9.5233 | 9.4074 | 9.668 | 9.4359 | -112.4944 | 9.4961 | 9.5673 | 9.3369 | 9.4486 | -112.5955
1346.4531 | 121.8658 | -9.8923 | 111.9781 | 1.4211e-13 | -0.03025 | 0.014039 | -0.0038527 | -0.012546 | 0.019057 | -0.23296 | 0.018012 | 0.018889 | 0.016026 | 0.033512 | 0.010108 | 0.019361 | -0.035222 | -0.031301 | 0.056706 | -0.059167 | 0.19691 | -0.072215 | 0.019362 | -0.017956 | -0.06093 | 0.020409 | 0.091543 | -0.13876 | -0.20078 | 9.8201 | -111.9214 | 9.9116 | 9.861 | 0.040914 | -112.0373 | -111.7812 | 9.6915 | -111.9577 | 9.9116 | 9.8313 | 0.13985 | -111.8866 | -112.1169 | 9.949 | 9.8331 | 10.0892 | 9.8571 | -112.0504 | 9.9127 | 9.9838 | 9.7535 | 9.8743 | -112.1789
1348.1406 | 117.5903 | -7.814 | 109.8175 | 1.4211e-13 | -0.030463 | 0.014252 | -0.0040665 | -0.012119 | 0.018629 | -0.24059 | 0.018012 | 0.018676 | 0.016026 | 0.033512 | 0.010108 | 0.014783 | -0.039801 | -0.031301 | 0.052128 | -0.059167 | 0.20149 | -0.12716 | 0.019362 | -0.022535 | -0.070087 | 0.024988 | 0.1007 | -0.13419 | -0.20994 | 7.6869 | -109.7654 | 7.8288 | 7.7827 | 0.095861 | -109.8767 | -109.616 | 7.6041 | -109.7925 | 7.8334 | 7.7439 | 0.13985 | -109.7168 | -109.9517 | 7.8662 | 7.7549 | 8.0155 | 7.7742 | -109.9447 | 7.839 | 7.9147 | 7.6798 | 7.7915 | -110.0274
1349.875 | 116.9998 | -9.7595 | 107.2861 | 1.4211e-13 | -0.03025 | 0.014252 | -0.0040665 | -0.012333 | 0.018416 | -0.23296 | 0.018012 | 0.019103 | 0.016026 | 0.03394 | 0.010108 | 0.014783 | -0.035222 | -0.031301 | 0.056706 | -0.063746 | 0.20149 | -0.072215 | 0.02852 | -0.022535 | -0.06093 | 0.029566 | 0.082386 | -0.13419 | -0.20536 | 9.6873 | -107.2294 | 9.7743 | 9.7282 | 0.040914 | -107.3498 | -107.0846 | 9.5542 | -107.2565 | 9.788 | 9.6986 | 0.14443 | -107.2037 | -107.4203 | 9.8162 | 9.6958 | 9.961 | 9.7243 | -107.3583 | 9.7891 | 9.8419 | 9.6253 | 9.737 | -107.4914
1351.5469 | 116.7206 | -9.5673 | 107.0206 | 1.4211e-13 | -0.030463 | 0.013825 | -0.0040665 | -0.012546 | 0.018202 | -0.23296 | 0.018012 | 0.018889 | 0.015598 | 0.03394 | 0.010535 | 0.014783 | -0.030644 | -0.031301 | 0.056706 | -0.059167 | 0.19233 | -0.090531 | 0.014784 | -0.022535 | -0.065509 | 0.024988 | 0.096121 | -0.13419 | -0.20536 | 9.4767 | -106.9639 | 9.582 | 9.536 | 0.05923 | -107.0797 | -106.8282 | 9.3619 | -106.9956 | 9.582 | 9.5018 | 0.13985 | -106.9244 | -107.1548 | 9.624 | 9.5081 | 9.7596 | 9.5366 | -107.1111 | 9.5922 | 9.6634 | 9.4331 | 9.5447 | -107.2259
1353.2812 | 116.4322 | -9.0866 | 107.1487 | 1.4211e-13 | -0.030463 | 0.014466 | -0.0038527 | -0.012333 | 0.018202 | -0.24059 | 0.018225 | 0.018462 | 0.016026 | 0.033512 | 0.010108 | 0.010204 | -0.026065 | -0.040457 | 0.056706 | -0.063746 | 0.19233 | -0.11342 | 0.02852 | -0.017956 | -0.051772 | 0.015831 | 0.096121 | -0.13876 | -0.20536 | 8.9732 | -107.092 | 9.0968 | 9.0462 | 0.072968 | -107.2125 | -106.9564 | 8.8813 | -107.1329 | 9.1151 | 9.0348 | 0.15359 | -107.0526 | -107.2875 | 9.1433 | 9.0229 | 9.2789 | 9.0605 | -107.2622 | 9.1024 | 9.1827 | 8.9478 | 9.0687 | -107.3541
1354.9531 | 116.0568 | -9.1461 | 106.9199 | 1.4211e-13 | -0.03025 | 0.013825 | -0.0042801 | -0.011905 | 0.018202 | -0.23296 | 0.018012 | 0.018676 | 0.015598 | 0.033512 | 0.010535 | 0.010204 | -0.030644 | -0.022144 | 0.061284 | -0.059167 | 0.20607 | -0.11342 | 0.019362 | -0.022535 | -0.06093 | 0.020409 | 0.096121 | -0.13419 | -0.1962 | 9.0327 | -106.8586 | 9.1563 | 9.124 | 0.091281 | -106.979 | -106.7138 | 8.9499 | -106.8995 | 9.1655 | 9.0852 | 0.13527 | -106.8237 | -107.054 | 9.2074 | 9.087 | 9.3522 | 9.1155 | -107.0333 | 9.1665 | 9.2422 | 9.0119 | 9.1236 | -107.1161
1356.6875 | 115.9012 | -9.137 | 106.6315 | 1.4211e-13 | -0.030463 | 0.014039 | -0.0040665 | -0.012546 | 0.017988 | -0.23296 | 0.018012 | 0.018676 | 0.016453 | 0.033726 | 0.010322 | 0.010204 | -0.035222 | -0.026723 | 0.061284 | -0.068325 | 0.19691 | -0.090531 | 0.019362 | -0.022535 | -0.056351 | 0.015831 | 0.096121 | -0.14334 | -0.20078 | 9.0464 | -106.5702 | 9.1472 | 9.1102 | 0.063808 | -106.6998 | -106.4346 | 8.9362 | -106.6156 | 9.1563 | 9.0806 | 0.14443 | -106.5353 | -106.7748 | 9.1982 | 9.0686 | 9.3339 | 9.1017 | -106.722 | 9.1528 | 9.2331 | 8.9936 | 9.1144 | -106.8322
1358.375 | 115.6998 | -89.6942 | 25.795 | 1.4211e-13 | -0.03025 | 0.014252 | -0.0040665 | -0.012333 | 0.018202 | -0.22533 | 0.018225 | 0.018676 | 0.016026 | 0.033726 | 0.010322 | 0.060567 | 0.005985 | 0.005325 | 0.097912 | 0.018675 | 0.24727 | -0.12716 | 0.06515 | 0.018674 | -0.019721 | 0.066194 | 0.14191 | -0.13419 | -0.15499 | 89.5671 | -25.6971 | 89.7548 | 89.6995 | 0.13249 | -25.7763 | -25.5477 | 89.5392 | -25.7288 | 89.7594 | 89.6745 | 0.13527 | -25.6531 | -25.9292 | 89.7921 | 89.7129 | 89.9415 | 89.7002 | -25.9221 | 89.7604 | 89.8361 | 89.56 | 89.7129 | -25.95
1360.0469 | 115.6952 | -89.5706 | 25.7172 | 1.4211e-13 | -0.030463 | 0.014039 | -0.0040665 | -0.012119 | 0.018416 | -0.23296 | 0.017798 | 0.018889 | 0.015812 | 0.033299 | 0.010322 | 0.055988 | 0.001407 | 0.009904 | 0.097912 | 0.050727 | 0.24269 | 0.023942 | 0.069728 | 0.014095 | -0.015143 | 0.070773 | 0.14191 | -0.13419 | -0.16415 | 89.5946 | -25.6193 | 89.6266 | 89.5805 | -0.014038 | -25.6664 | -25.4745 | 89.4065 | -25.6464 | 89.6403 | 89.5555 | 0.14901 | -25.5753 | -25.8513 | 89.6685 | 89.6213 | 89.8133 | 89.572 | -25.6932 | 89.6414 | 89.7125 | 89.4364 | 89.5847 | -25.8813
1361.7812 | 115.5487 | -89.5569 | 25.6897 | 1.4211e-13 | -0.030036 | 0.013825 | -0.0040665 | -0.012546 | 0.018202 | -0.23296 | 0.018012 | 0.019103 | 0.016026 | 0.033512 | 0.010535 | 0.055988 | 0.015142 | 0.014482 | 0.10707 | 0.041569 | 0.24727 | 0.0331 | 0.074307 | 0.014095 | -0.015143 | 0.070773 | 0.14191 | -0.12503 | -0.15499 | 89.59 | -25.5826 | 89.6129 | 89.5714 | -0.018618 | -25.6481 | -25.4424 | 89.4019 | -25.6189 | 89.6312 | 89.5417 | 0.13985 | -25.5478 | -25.8147 | 89.664 | 89.5985 | 89.8042 | 89.572 | -25.6566 | 89.6277 | 89.6988 | 89.4319 | 89.571 | -25.8447
1363.4688 | 115.3473 | -89.4974 | 25.7034 | 1.4211e-13 | -0.03025 | 0.013611 | -0.0040665 | -0.012546 | 0.018202 | -0.24822 | 0.018012 | 0.018676 | 0.015812 | 0.033726 | 0.010108 | 0.05141 | 0.010564 | 0.009904 | 0.10707 | 0.046148 | 0.24727 | 0.0331 | 0.074307 | 0.014095 | -0.005985 | 0.075351 | 0.13275 | -0.13876 | -0.15957 | 89.5305 | -25.5964 | 89.5488 | 89.5073 | -0.023196 | -25.6573 | -25.4562 | 89.3378 | -25.6281 | 89.5717 | 89.4914 | 0.15358 | -25.5707 | -25.8422 | 89.6044 | 89.5435 | 89.7446 | 89.5079 | -25.6703 | 89.5727 | 89.6301 | 89.3586 | 89.5115 | -25.863
1365.2188 | 115.2237 | -89.4608 | 25.6668 | 1.4211e-13 | -0.030036 | 0.014039 | -0.0044937 | -0.012546 | 0.018629 | -0.24059 | 0.018225 | 0.018889 | 0.015598 | 0.033512 | 0.010108 | 0.055988 | 0.005985 | 0.009904 | 0.097912 | 0.041569 | 0.24269 | 0.0331 | 0.06515 | 0.018674 | -0.015143 | 0.070773 | 0.13733 | -0.13419 | -0.15957 | 89.4939 | -25.5689 | 89.5167 | 89.4707 | -0.023196 | -25.6252 | -25.4241 | 89.3012 | -25.596 | 89.5259 | 89.4456 | 0.14443 | -25.5295 | -25.801 | 89.5587 | 89.5023 | 89.7034 | 89.4667 | -25.6337 | 89.5315 | 89.5981 | 89.3266 | 89.4794 | -25.8264
1366.9531 | 115.1733 | -89.4012 | 25.6348 | 1.4211e-13 | -0.03025 | 0.014039 | -0.0040665 | -0.012546 | 0.018202 | -0.23296 | 0.018439 | 0.018676 | 0.015812 | 0.033726 | 0.010322 | 0.060567 | 0.010564 | 0.000747 | 0.10707 | 0.046148 | 0.24269 | 0.023942 | 0.055992 | 0.018674 | -0.015143 | 0.066194 | 0.14191 | -0.13876 | -0.15499 | 89.4252 | -25.5277 | 89.4618 | 89.402 | -0.023195 | -25.5886 | -25.3921 | 89.2463 | -25.5686 | 89.4572 | 89.3861 | 0.13985 | -25.4929 | -25.7735 | 89.5083 | 89.4474 | 89.6439 | 89.4118 | -25.6108 | 89.4674 | 89.5432 | 89.2625 | 89.4199 | -25.7898
1368.6406 | 115.2145 | -89.3143 | 25.6073 | 1.4211e-13 | -0.03025 | 0.014039 | -0.0038527 | -0.01276 | 0.018629 | -0.22533 | 0.018225 | 0.018462 | 0.015812 | 0.033726 | 0.010108 | 0.046831 | 0.015142 | 0.009904 | 0.10249 | 0.041569 | 0.24269 | 0.0331 | 0.06515 | 0.027831 | -0.015143 | 0.061616 | 0.13275 | -0.13876 | -0.15499 | 89.3474 | -25.5048 | 89.3611 | 89.3242 | -0.023196 | -25.5657 | -25.3646 | 89.1593 | -25.5457 | 89.3794 | 89.2991 | 0.13985 | -25.4745 | -25.7461 | 89.4168 | 89.3558 | 89.557 | 89.3294 | -25.5742 | 89.3759 | 89.447 | 89.1755 | 89.3421 | -25.7623
1370.3906 | 115.1047 | -89.3417 | 25.6256 | 1.4211e-13 | -0.03025 | 0.013825 | -0.0042801 | -0.012546 | 0.018416 | -0.23296 | 0.018012 | 0.018676 | 0.015812 | 0.033512 | 0.010322 | 0.046831 | 0.005985 | 0.000747 | 0.10707 | 0.050727 | 0.24269 | 0.023942 | 0.046835 | 0.018674 | -0.015143 | 0.070773 | 0.13733 | -0.14334 | -0.15957 | 89.3657 | -25.5185 | 89.3886 | 89.3425 | -0.023195 | -25.5749 | -25.3829 | 89.1822 | -25.5548 | 89.3886 | 89.3266 | 0.14443 | -25.4883 | -25.769 | 89.4488 | 89.3925 | 89.5844 | 89.3477 | -25.6017 | 89.4125 | 89.4791 | 89.1984 | 89.3604 | -25.7852
1372.125 | 115.0269 | -89.2868 | 25.589 | 1.4211e-13 | -0.030036 | 0.014039 | -0.0040665 | -0.012333 | 0.018416 | -0.23296 | 0.018439 | 0.018676 | 0.015812 | 0.033512 | 0.010322 | 0.05141 | 0.005985 | 0.009904 | 0.10249 | 0.041569 | 0.24727 | 0.028521 | 0.055992 | 0.018674 | -0.015143 | 0.075351 | 0.13733 | -0.14334 | -0.16415 | 89.3153 | -25.4865 | 89.3382 | 89.2967 | -0.018617 | -25.5474 | -25.3417 | 89.1227 | -25.5136 | 89.3428 | 89.2717 | 0.14901 | -25.4517 | -25.7323 | 89.3893 | 89.3284 | 89.5341 | 89.2928 | -25.5605 | 89.3622 | 89.4241 | 89.1435 | 89.3055 | -25.7531
1373.875 | 115.0772 | -89.2685 | 25.5569 | 1.4211e-13 | -0.03025 | 0.014252 | -0.0042801 | -0.012546 | 0.018629 | -0.24059 | 0.018439 | 0.018889 | 0.015812 | 0.033299 | 0.010535 | 0.05141 | 0.010564 | 0.009904 | 0.097912 | 0.046148 | 0.24269 | 0.023942 | 0.055992 | 0.018674 | -0.015143 | 0.070773 | 0.13733 | -0.13876 | -0.15957 | 89.2924 | -25.459 | 89.3199 | 89.2784 | -0.014038 | -25.5108 | -25.3143 | 89.1089 | -25.4862 | 89.3245 | 89.2534 | 0.14443 | -25.4196 | -25.6957 | 89.3664 | 89.3146 | 89.5112 | 89.2791 | -25.533 | 89.3393 | 89.4058 | 89.1297 | 89.2872 | -25.7165
1375.5625 | 114.9673 | -89.2593 | 25.5341 | 1.4211e-13 | -0.03025 | 0.014039 | -0.0038527 | -0.012333 | 0.018202 | -0.22533 | 0.018012 | 0.018889 | 0.015598 | 0.033726 | 0.0096806 | 0.060567 | 0.010564 | 0.005325 | 0.10249 | 0.041569 | 0.24269 | 0.042258 | 0.055992 | 0.018674 | -0.015143 | 0.075351 | 0.13733 | -0.13419 | -0.15499 | 89.3016 | -25.4316 | 89.3199 | 89.2647 | -0.036933 | -25.4925 | -25.2914 | 89.1043 | -25.4587 | 89.3153 | 89.2442 | 0.13985 | -25.3967 | -25.6682 | 89.3618 | 89.3009 | 89.502 | 89.2699 | -25.4918 | 89.3347 | 89.3967 | 89.1252 | 89.278 | -25.689
1377.3125 | 114.9765 | -89.2731 | 25.5753 | 1.4211e-13 | -0.030036 | 0.014252 | -0.0040665 | -0.012974 | 0.018202 | -0.23296 | 0.018012 | 0.018676 | 0.015598 | 0.033512 | 0.010535 | 0.060567 | 0.005985 | 0.005325 | 0.097912 | 0.046148 | 0.24269 | 0.028521 | 0.055992 | 0.018674 | -0.015143 | 0.070773 | 0.13733 | -0.13876 | -0.15041 | 89.3016 | -25.4773 | 89.3336 | 89.2784 | -0.023196 | -25.5291 | -25.3326 | 89.1227 | -25.5045 | 89.3291 | 89.2579 | 0.13527 | -25.4379 | -25.714 | 89.371 | 89.3192 | 89.5158 | 89.2791 | -25.5467 | 89.3438 | 89.4104 | 89.1343 | 89.2917 | -25.7257
1379.0625 | 115.004 | -89.2365 | 25.5203 | 1.4211e-13 | -0.03025 | 0.014039 | -0.0040665 | -0.012546 | 0.018416 | -0.24059 | 0.018012 | 0.019103 | 0.015598 | 0.033512 | 0.010108 | 0.065145 | 0.001407 | 0.009904 | 0.10707 | 0.046148 | 0.24269 | 0.023942 | 0.055992 | 0.018674 | -0.010564 | 0.070773 | 0.13733 | -0.13876 | -0.16415 | 89.2604 | -25.4133 | 89.3016 | 89.2464 | -0.014038 | -25.4742 | -25.2776 | 89.0723 | -25.4496 | 89.2924 | 89.2259 | 0.15358 | -25.383 | -25.6591 | 89.3435 | 89.2826 | 89.4791 | 89.2379 | -25.4964 | 89.3072 | 89.3738 | 89.0977 | 89.2551 | -25.6845
1380.75 | 114.8895 | -89.2502 | 25.5524 | 1.4211e-13 | -0.030036 | 0.014039 | -0.0040665 | -0.012333 | 0.018416 | -0.23296 | 0.018225 | 0.018889 | 0.015812 | 0.03394 | 0.0098942 | 0.05141 | 0.005985 | 0.009904 | 0.10249 | 0.046148 | 0.23812 | 0.028521 | 0.051413 | 0.014095 | -0.0243 | 0.066194 | 0.13275 | -0.13419 | -0.15957 | 89.2787 | -25.4499 | 89.3016 | 89.2601 | -0.018617 | -25.5062 | -25.3143 | 89.0906 | -25.4862 | 89.3016 | 89.2259 | 0.13527 | -25.4196 | -25.6866 | 89.3527 | 89.2963 | 89.4883 | 89.2562 | -25.5238 | 89.3164 | 89.3829 | 89.116 | 89.2643 | -25.7119
1382.4844 | 114.949 | -89.2456 | 25.5249 | 1.4211e-13 | -0.030463 | 0.014039 | -0.0038527 | -0.012119 | 0.017988 | -0.23296 | 0.018012 | 0.018889 | 0.015812 | 0.033512 | 0.010322 | 0.060567 | 0.019721 | 0.014482 | 0.10249 | 0.050727 | 0.23812 | 0.051416 | 0.055992 | 0.018674 | -0.019721 | 0.075351 | 0.13275 | -0.13419 | -0.15957 | 89.297 | -25.4224 | 89.3062 | 89.2601 | -0.036934 | -25.4742 | -25.2868 | 89.086 | -25.4496 | 89.3016 | 89.2259 | 0.13985 | -25.3922 | -25.6591 | 89.3481 | 89.2963 | 89.4837 | 89.2653 | -25.4735 | 89.321 | 89.3784 | 89.1114 | 89.2643 | -25.6845
1384.1719 | 114.9902 | -89.2227 | 25.502 | 1.4211e-13 | -0.03025 | 0.013611 | -0.0040665 | -0.012333 | 0.018202 | -0.23296 | 0.018225 | 0.018889 | 0.015598 | 0.033512 | 0.010108 | 0.05141 | 0.010564 | 0.009904 | 0.10249 | 0.055306 | 0.24727 | 0.046837 | 0.060571 | 0.023253 | -0.010564 | 0.061616 | 0.14191 | -0.14334 | -0.15957 | 89.2696 | -25.3995 | 89.2741 | 89.2326 | -0.036933 | -25.4467 | -25.2547 | 89.0631 | -25.4404 | 89.2833 | 89.2122 | 0.14901 | -25.3601 | -25.6454 | 89.3252 | 89.278 | 89.47 | 89.2333 | -25.4552 | 89.2843 | 89.3646 | 89.0794 | 89.246 | -25.6616
1385.9375 | 115.004 | -89.2639 | 25.5249 | 1.4211e-13 | -0.03025 | 0.013611 | -0.0042801 | -0.012333 | 0.018202 | -0.24822 | 0.017798 | 0.018676 | 0.016026 | 0.03394 | 0.010322 | 0.05141 | 0.001407 | 0.009904 | 0.10707 | 0.055306 | 0.23812 | 0.042258 | 0.051413 | 0.018674 | -0.010564 | 0.066194 | 0.14191 | -0.12961 | -0.16415 | 89.3062 | -25.4178 | 89.3153 | 89.2738 | -0.032354 | -25.4696 | -25.2868 | 89.0998 | -25.4587 | 89.3153 | 89.2534 | 0.15358 | -25.383 | -25.6545 | 89.371 | 89.3192 | 89.502 | 89.2653 | -25.4826 | 89.3301 | 89.4058 | 89.1343 | 89.2826 | -25.6891
1387.6875 | 118.0756 | -117.6453 | 0.32044 | 1.4211e-13 | -0.030036 | 0.014039 | -0.0038527 | -0.01276 | 0.019057 | -0.24822 | 0.018012 | 0.018676 | 0.015812 | 0.033726 | 0.0098942 | 0.065145 | 0.010564 | 0.023639 | 0.11165 | 0.055306 | 0.25643 | 0.078889 | 0.060571 | 0.03241 | -0.005985 | 0.084508 | 0.15107 | -0.070086 | -0.15041 | 117.7242 | -0.20879 | 117.7104 | 117.6689 | -0.05525 | -0.26513 | -0.064004 | 117.4949 | -0.23593 | 117.7058 | 117.6393 | 0.14443 | -0.16937 | -0.39052 | 117.7569 | 117.7006 | 117.9017 | 117.6558 | -0.24155 | 117.7298 | 117.7963 | 117.5752 | 117.6777 | -0.47085
1389.3594 | 118.5196 | -117.9565 | 0.27008 | 1.4211e-13 | -0.030036 | 0.014039 | -0.0038527 | -0.012333 | 0.019057 | -0.24059 | 0.017798 | 0.018676 | 0.015812 | 0.033726 | 0.010749 | 0.065145 | 0.019721 | 0.023639 | 0.11165 | 0.059885 | 0.26101 | 0.069732 | 0.069728 | 0.036989 | -0.005985 | 0.089087 | 0.15564 | -0.12503 | -0.14125 | 118.0263 | -0.15843 | 118.0217 | 117.9802 | -0.046093 | -0.2102 | -0.009071 | 117.8153 | -0.18099 | 118.0263 | 117.9506 | 0.13527 | -0.11444 | -0.39511 | 118.0682 | 118.0164 | 118.2176 | 117.9763 | -0.20035 | 118.0456 | 118.1122 | 117.8315 | 117.9935 | -0.41134
1391.0312 | 118.5425 | -118.2083 | 0.3067 | 1.4211e-13 | -0.030036 | 0.014252 | -0.0036391 | -0.012546 | 0.018843 | -0.24059 | 0.018653 | 0.019103 | 0.015812 | 0.033299 | 0.010108 | 0.069723 | 0.0243 | 0.028217 | 0.11165 | 0.050727 | 0.25643 | 0.055995 | 0.074307 | 0.036989 | 0.003172 | 0.075351 | 0.15107 | -0.12503 | -0.15041 | 118.2643 | -0.19505 | 118.278 | 118.2365 | -0.027778 | -0.25597 | -0.050271 | 118.0579 | -0.23135 | 118.2826 | 118.2115 | 0.15358 | -0.15564 | -0.43173 | 118.32 | 118.259 | 118.4647 | 118.2326 | -0.25071 | 118.2837 | 118.3594 | 118.0833 | 118.2453 | -0.45711
1392.7656 | 118.689 | -118.2495 | 0.32501 | 1.4211e-13 | -0.030036 | 0.013825 | -0.0038527 | -0.01276 | 0.018843 | -0.23296 | 0.018225 | 0.018889 | 0.015598 | 0.033512 | 0.0096806 | 0.074302 | 0.028878 | 0.028217 | 0.1208 | 0.055306 | 0.25185 | 0.069732 | 0.06515 | 0.03241 | 0.007751 | 0.084508 | 0.15564 | -0.13419 | -0.14583 | 118.3192 | -0.20421 | 118.3238 | 118.2777 | -0.041515 | -0.26971 | -0.07316 | 118.1037 | -0.2405 | 118.3147 | 118.2573 | 0.15358 | -0.16937 | -0.4592 | 118.3703 | 118.3048 | 118.5014 | 118.2784 | -0.25528 | 118.334 | 118.4052 | 118.1153 | 118.2819 | -0.47085
1394.5156 | 118.8263 | -118.3228 | 0.3479 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0034253 | -0.012546 | 0.018629 | -0.23296 | 0.018012 | 0.019103 | 0.015812 | 0.033512 | 0.0098942 | 0.069723 | 0.019721 | 0.023639 | 0.11165 | 0.050727 | 0.25185 | 0.060574 | 0.069728 | 0.036989 | 0.007751 | 0.089087 | 0.15564 | -0.092979 | -0.15041 | 118.3833 | -0.23625 | 118.3925 | 118.3464 | -0.036935 | -0.29717 | -0.096048 | 118.1723 | -0.25881 | 118.3925 | 118.3305 | 0.15816 | -0.19226 | -0.44088 | 118.4344 | 118.3735 | 118.5746 | 118.3425 | -0.28733 | 118.4118 | 118.4784 | 118.2298 | 118.3597 | -0.49831
1396.1875 | 118.8538 | -118.5242 | 0.27466 | 1.4211e-13 | -0.030036 | 0.014039 | -0.0036391 | -0.01276 | 0.019057 | -0.24059 | 0.018012 | 0.018462 | 0.016026 | 0.033512 | 0.010108 | 0.069723 | 0.015142 | 0.028217 | 0.11622 | 0.055306 | 0.25643 | 0.069732 | 0.074307 | 0.03241 | -0.001407 | 0.07993 | 0.15564 | -0.060928 | -0.15041 | 118.5939 | -0.15843 | 118.5939 | 118.5524 | -0.041515 | -0.21935 | -0.018227 | 118.3738 | -0.19473 | 118.5985 | 118.5228 | 0.149 | -0.11902 | -0.33559 | 118.6404 | 118.5795 | 118.7806 | 118.5393 | -0.20493 | 118.6041 | 118.6798 | 118.4632 | 118.5566 | -0.42507
1397.9375 | 119.0369 | -118.5791 | 0.24719 | 1.4211e-13 | -0.030036 | 0.013825 | -0.0036391 | -0.01276 | 0.019057 | -0.23296 | 0.018012 | 0.019103 | 0.015812 | 0.033512 | 0.010322 | 0.060567 | 0.015142 | 0.014482 | 0.1208 | 0.059885 | 0.25643 | 0.060574 | 0.069728 | 0.03241 | -0.001407 | 0.07993 | 0.15107 | -0.12045 | -0.15041 | 118.6397 | -0.12639 | 118.6397 | 118.5936 | -0.046092 | -0.18731 | 0.009239 | 118.4287 | -0.16726 | 118.6488 | 118.5777 | 0.149 | -0.096127 | -0.36764 | 118.6999 | 118.639 | 118.8355 | 118.5942 | -0.18662 | 118.659 | 118.7302 | 118.4587 | 118.6115 | -0.3976
1399.6875 | 119.0231 | -118.7119 | 0.27466 | 1.4211e-13 | -0.030036 | 0.014039 | -0.0034253 | -0.01276 | 0.01927 | -0.24059 | 0.018012 | 0.018889 | 0.015598 | 0.03394 | 0.010108 | 0.065145 | 0.019721 | 0.023639 | 0.11165 | 0.055306 | 0.25185 | 0.069732 | 0.06515 | 0.027831 | -0.005985 | 0.084508 | 0.15107 | -0.092979 | -0.14583 | 118.7816 | -0.16301 | 118.777 | 118.7355 | -0.046093 | -0.21935 | -0.022806 | 118.566 | -0.19015 | 118.777 | 118.7059 | 0.13985 | -0.12359 | -0.36764 | 118.8235 | 118.7672 | 118.9637 | 118.7316 | -0.20493 | 118.7964 | 118.8629 | 118.6189 | 118.7397 | -0.42049
1401.4219 | 119.0964 | -118.7668 | 0.27466 | 1.4211e-13 | -0.030036 | 0.013611 | -0.0034253 | -0.01276 | 0.018843 | -0.23296 | 0.018439 | 0.018889 | 0.016026 | 0.033726 | 0.010108 | 0.069723 | 0.010564 | 0.023639 | 0.11165 | 0.055306 | 0.25643 | 0.055995 | 0.069728 | 0.041567 | -0.005985 | 0.07993 | 0.15564 | -0.12045 | -0.15041 | 118.8228 | -0.16301 | 118.8365 | 118.7904 | -0.032356 | -0.21935 | -0.018227 | 118.6164 | -0.19473 | 118.8365 | 118.7608 | 0.14443 | -0.11902 | -0.39511 | 118.8784 | 118.8221 | 119.0232 | 118.7773 | -0.21866 | 118.8467 | 118.9224 | 118.6463 | 118.8084 | -0.42507
1403.1094 | 119.1925 | -118.8538 | 0.29755 | 1.4211e-13 | -0.030036 | 0.014039 | -0.0038527 | -0.01276 | 0.01927 | -0.23296 | 0.018012 | 0.018676 | 0.015385 | 0.033512 | 0.0098942 | 0.069723 | 0.0243 | 0.028217 | 0.11165 | 0.055306 | 0.25643 | 0.060574 | 0.06515 | 0.036989 | -0.001407 | 0.084508 | 0.14649 | -0.12503 | -0.14125 | 118.9143 | -0.1859 | 118.9235 | 118.882 | -0.032357 | -0.24224 | -0.041115 | 118.7125 | -0.21304 | 118.9189 | 118.8524 | 0.13985 | -0.15106 | -0.42257 | 118.9654 | 118.9091 | 119.1102 | 118.8781 | -0.23697 | 118.9383 | 119.0002 | 118.7287 | 118.8907 | -0.4388
1404.8594 | 119.3253 | -118.9041 | 0.27008 | 1.4211e-13 | -0.03025 | 0.014039 | -0.0038527 | -0.012974 | 0.018843 | -0.22533 | 0.018012 | 0.018889 | 0.015385 | 0.033726 | 0.010322 | 0.074302 | 0.019721 | 0.01906 | 0.11165 | 0.059885 | 0.25643 | 0.051416 | 0.069728 | 0.027831 | -0.001407 | 0.084508 | 0.14649 | -0.0884 | -0.14583 | 118.9555 | -0.15843 | 118.9784 | 118.9232 | -0.032356 | -0.2102 | -0.01365 | 118.7583 | -0.18557 | 118.9738 | 118.9027 | 0.14443 | -0.1236 | -0.35848 | 119.0158 | 118.964 | 119.1605 | 118.9238 | -0.21866 | 118.9886 | 119.0506 | 118.8157 | 118.9319 | -0.41591
1406.5938 | 119.4397 | -118.9728 | 0.2655 | 1.4211e-13 | -0.030036 | 0.013825 | -0.0040665 | -0.012546 | 0.018629 | -0.24059 | 0.018012 | 0.018889 | 0.015598 | 0.033726 | 0.0098942 | 0.065145 | 0.019721 | 0.028217 | 0.10707 | 0.055306 | 0.26101 | 0.060574 | 0.069728 | 0.036989 | -0.005985 | 0.089087 | 0.15564 | -0.051771 | -0.14583 | 119.0334 | -0.15843 | 119.0379 | 119.001 | -0.032357 | -0.2102 | -0.004493 | 118.8269 | -0.17642 | 119.0425 | 118.9668 | 0.13985 | -0.10986 | -0.31727 | 119.0798 | 119.0281 | 119.2338 | 118.9925 | -0.20493 | 119.0619 | 119.1284 | 118.921 | 119.0098 | -0.41134
1408.2656 | 119.4214 | -118.9865 | 0.31128 | 1.4211e-13 | -0.029609 | 0.014252 | -0.0038527 | -0.01276 | 0.018843 | -0.2177 | 0.018225 | 0.018462 | 0.015598 | 0.033726 | 0.010108 | 0.065145 | 0.019721 | 0.023639 | 0.11622 | 0.055306 | 0.25185 | 0.07431 | 0.069728 | 0.027831 | -0.001407 | 0.084508 | 0.15107 | -0.10214 | -0.14583 | 119.0608 | -0.19505 | 119.0517 | 119.0101 | -0.050671 | -0.25597 | -0.059427 | 118.8407 | -0.22677 | 119.0562 | 118.9851 | 0.14443 | -0.16021 | -0.41341 | 119.1027 | 119.0418 | 119.2384 | 119.0062 | -0.23697 | 119.071 | 119.1376 | 118.8844 | 119.0143 | -0.45711
1410.0156 | 119.5541 | -119.0552 | 0.29755 | 1.4211e-13 | -0.03025 | 0.014039 | -0.0034253 | -0.01276 | 0.018629 | -0.23296 | 0.018225 | 0.018676 | 0.015598 | 0.033512 | 0.0098942 | 0.065145 | 0.019721 | 0.01906 | 0.11622 | 0.055306 | 0.26101 | 0.07431 | 0.069728 | 0.036989 | -0.005985 | 0.084508 | 0.16022 | -0.10671 | -0.14583 | 119.1295 | -0.18132 | 119.1203 | 119.0742 | -0.05525 | -0.24224 | -0.036536 | 118.9093 | -0.21304 | 119.1249 | 119.0492 | 0.13985 | -0.13732 | -0.40426 | 119.1714 | 119.1105 | 119.3162 | 119.0749 | -0.22324 | 119.1397 | 119.2154 | 118.9485 | 119.0922 | -0.44338
1411.75 | 119.4946 | -119.1422 | 0.32501 | 1.4211e-13 | -0.030036 | 0.013825 | -0.0038527 | -0.01276 | 0.019057 | -0.24059 | 0.018439 | 0.018889 | 0.016026 | 0.033726 | 0.010108 | 0.074302 | 0.015142 | 0.028217 | 0.10707 | 0.055306 | 0.26101 | 0.060574 | 0.06515 | 0.036989 | -0.001407 | 0.089087 | 0.15107 | -0.11129 | -0.14583 | 119.2027 | -0.21794 | 119.2165 | 119.1704 | -0.032357 | -0.26971 | -0.064002 | 118.9963 | -0.23593 | 119.2073 | 119.1407 | 0.14443 | -0.17395 | -0.43631 | 119.2492 | 119.1975 | 119.4032 | 119.1573 | -0.26444 | 119.2312 | 119.2932 | 119.0309 | 119.1791 | -0.47085
1413.4219 | 119.6548 | -119.1742 | 0.31128 | 1.4211e-13 | -0.030036 | 0.013825 | -0.0038527 | -0.013187 | 0.018843 | -0.23296 | 0.018225 | 0.018676 | 0.015598 | 0.033512 | 0.0098942 | 0.074302 | 0.0243 | 0.023639 | 0.11622 | 0.059885 | 0.25643 | 0.046837 | 0.06515 | 0.036989 | -0.001407 | 0.084508 | 0.16022 | -0.13419 | -0.14583 | 119.221 | -0.19505 | 119.2485 | 119.1978 | -0.023198 | -0.25139 | -0.054848 | 119.0284 | -0.22677 | 119.2393 | 119.1728 | 0.14443 | -0.15106 | -0.44546 | 119.2904 | 119.2341 | 119.4306 | 119.1985 | -0.26444 | 119.2587 | 119.3344 | 119.04 | 119.2112 | -0.45711
1415.1719 | 119.7876 | -119.252 | 0.27924 | 1.4211e-13 | -0.029609 | 0.014039 | -0.0038527 | -0.01276 | 0.018843 | -0.24059 | 0.018225 | 0.018889 | 0.015598 | 0.033726 | 0.010108 | 0.069723 | 0.015142 | 0.023639 | 0.11165 | 0.059885 | 0.26101 | 0.069732 | 0.06515 | 0.027831 | -0.005985 | 0.07993 | 0.15564 | -0.12503 | -0.14125 | 119.3217 | -0.16759 | 119.3217 | 119.2757 | -0.046093 | -0.21935 | -0.018226 | 119.1108 | -0.19931 | 119.3172 | 119.246 | 0.13527 | -0.12359 | -0.40426 | 119.3637 | 119.3119 | 119.513 | 119.2672 | -0.2095 | 119.3319 | 119.4077 | 119.127 | 119.2798 | -0.42049
1416.9219 | 119.8059 | -119.2474 | 0.28839 | 1.4211e-13 | -0.030036 | 0.013825 | -0.0040665 | -0.012974 | 0.018629 | -0.23296 | 0.018012 | 0.018676 | 0.015598 | 0.033726 | 0.0098942 | 0.069723 | 0.010564 | 0.028217 | 0.11622 | 0.055306 | 0.26101 | 0.060574 | 0.06515 | 0.03241 | -0.001407 | 0.07993 | 0.15107 | -0.12961 | -0.14125 | 119.308 | -0.17217 | 119.3172 | 119.2757 | -0.032357 | -0.23309 | -0.027381 | 119.1062 | -0.20846 | 119.3126 | 119.246 | 0.13985 | -0.13733 | -0.418 | 119.3637 | 119.3027 | 119.5084 | 119.258 | -0.22782 | 119.3274 | 119.3985 | 119.1178 | 119.2798 | -0.42965
1418.6562 | 119.8471 | -119.3344 | 0.3067 | 1.4211e-13 | -0.030463 | 0.013825 | -0.0038527 | -0.012546 | 0.018843 | -0.24059 | 0.018012 | 0.018462 | 0.015812 | 0.033726 | 0.010108 | 0.069723 | 0.0243 | 0.023639 | 0.11165 | 0.055306 | 0.25643 | 0.083468 | 0.06515 | 0.027831 | -0.005985 | 0.084508 | 0.15107 | -0.12045 | -0.14125 | 119.4179 | -0.19505 | 119.4041 | 119.3581 | -0.059829 | -0.2514 | -0.050271 | 119.1932 | -0.22219 | 119.3996 | 119.3284 | 0.13527 | -0.15564 | -0.42715 | 119.4461 | 119.3897 | 119.5908 | 119.3587 | -0.22323 | 119.4189 | 119.4855 | 119.214 | 119.3622 | -0.44796
1420.4062 | 119.8242 | -119.426 | 0.32959 | 1.4211e-13 | -0.030036 | 0.013398 | -0.0038527 | -0.01276 | 0.018843 | -0.24059 | 0.018225 | 0.018676 | 0.015812 | 0.033512 | 0.010108 | 0.065145 | 0.019721 | 0.023639 | 0.11165 | 0.059885 | 0.24727 | 0.051416 | 0.06515 | 0.027831 | -0.001407 | 0.084508 | 0.15564 | -0.097557 | -0.15041 | 119.4774 | -0.21794 | 119.4911 | 119.4496 | -0.027777 | -0.2697 | -0.082316 | 119.2756 | -0.24508 | 119.4911 | 119.4246 | 0.149 | -0.17395 | -0.42715 | 119.5376 | 119.4858 | 119.6732 | 119.4457 | -0.27817 | 119.5105 | 119.5816 | 119.3284 | 119.4538 | -0.48
1422.0781 | 119.8425 | -119.4855 | 0.34332 | 1.4211e-13 | -0.029609 | 0.014039 | -0.0040665 | -0.012546 | 0.019484 | -0.22533 | 0.018012 | 0.018889 | 0.015385 | 0.03394 | 0.0098942 | 0.060567 | 0.028878 | 0.028217 | 0.11165 | 0.050727 | 0.25643 | 0.069732 | 0.055992 | 0.036989 | 0.003172 | 0.084508 | 0.15107 | -0.12503 | -0.14125 | 119.5552 | -0.23168 | 119.546 | 119.5137 | -0.041515 | -0.2926 | -0.086892 | 119.3442 | -0.25882 | 119.5415 | 119.4886 | 0.14443 | -0.19226 | -0.46835 | 119.5971 | 119.5362 | 119.7419 | 119.5144 | -0.27359 | 119.57 | 119.6365 | 119.3604 | 119.5225 | -0.48458
1423.8281 | 119.9707 | -119.5038 | 0.35248 | 1.4211e-13 | -0.029822 | 0.013611 | -0.0036391 | -0.01276 | 0.018843 | -0.23296 | 0.018012 | 0.018676 | 0.015598 | 0.03394 | 0.010108 | 0.069723 | 0.019721 | 0.01906 | 0.11622 | 0.055306 | 0.25643 | 0.055995 | 0.069728 | 0.03241 | -0.005985 | 0.089087 | 0.15107 | -0.11129 | -0.14583 | 119.5598 | -0.23625 | 119.5735 | 119.5228 | -0.036935 | -0.29717 | -0.096047 | 119.358 | -0.26339 | 119.5735 | 119.4978 | 0.13985 | -0.20141 | -0.46377 | 119.62 | 119.5591 | 119.7602 | 119.5235 | -0.29648 | 119.5929 | 119.6548 | 119.3925 | 119.5362 | -0.49831
1425.5781 | 119.9203 | -119.6182 | 0.30212 | 1.4211e-13 | -0.030036 | 0.014039 | -0.0042801 | -0.012546 | 0.019057 | -0.23296 | 0.018225 | 0.018889 | 0.016239 | 0.033512 | 0.0098942 | 0.060567 | 0.019721 | 0.028217 | 0.11165 | 0.050727 | 0.26101 | 0.046837 | 0.060571 | 0.027831 | -0.010564 | 0.084508 | 0.14649 | -0.12503 | -0.15041 | 119.6651 | -0.19048 | 119.6788 | 119.6464 | -0.01862 | -0.2514 | -0.041114 | 119.4678 | -0.21762 | 119.6788 | 119.6077 | 0.13985 | -0.15564 | -0.42715 | 119.7299 | 119.669 | 119.8792 | 119.6379 | -0.25529 | 119.7027 | 119.7647 | 119.4932 | 119.6461 | -0.45254
1427.3281 | 120.0485 | -119.664 | 0.29297 | 1.4211e-13 | -0.030036 | 0.014039 | -0.0038527 | -0.01276 | 0.018843 | -0.22533 | 0.018439 | 0.018889 | 0.015171 | 0.033726 | 0.010108 | 0.060567 | 0.010564 | 0.014482 | 0.10249 | 0.055306 | 0.26101 | 0.042258 | 0.055992 | 0.027831 | -0.015143 | 0.084508 | 0.14649 | -0.11587 | -0.14583 | 119.7063 | -0.19048 | 119.7246 | 119.6785 | -0.027776 | -0.23766 | -0.031959 | 119.5182 | -0.20846 | 119.72 | 119.6489 | 0.13069 | -0.14648 | -0.40884 | 119.7665 | 119.7193 | 119.925 | 119.6746 | -0.25071 | 119.7485 | 119.8105 | 119.5481 | 119.6918 | -0.4388
1429.0781 | 120.0806 | -119.7372 | 0.31586 | 1.4211e-13 | -0.029822 | 0.013825 | -0.0036391 | -0.01276 | 0.018843 | -0.23296 | 0.018225 | 0.018676 | 0.016026 | 0.033726 | 0.0096806 | 0.060567 | 0.015142 | 0.014482 | 0.10707 | 0.050727 | 0.25185 | 0.037679 | 0.069728 | 0.023253 | -0.001407 | 0.066194 | 0.14191 | -0.10214 | -0.14583 | 119.7749 | -0.20879 | 119.7978 | 119.7517 | -0.023197 | -0.26513 | -0.064005 | 119.5914 | -0.24966 | 119.807 | 119.7358 | 0.14443 | -0.17395 | -0.41799 | 119.8443 | 119.788 | 119.9891 | 119.7524 | -0.27818 | 119.8034 | 119.8792 | 119.6351 | 119.7605 | -0.46169
1430.8281 | 120.2545 | -119.7189 | 0.27924 | 1.4211e-13 | -0.030036 | 0.014039 | -0.0038527 | -0.01276 | 0.019057 | -0.23296 | 0.018225 | 0.018889 | 0.015812 | 0.033512 | 0.010108 | 0.069723 | 0.015142 | 0.01906 | 0.11165 | 0.050727 | 0.25643 | 0.042258 | 0.069728 | 0.027831 | -0.005985 | 0.07993 | 0.15107 | -0.12961 | -0.14583 | 119.7612 | -0.16759 | 119.7887 | 119.738 | -0.023198 | -0.22851 | -0.022805 | 119.5731 | -0.19931 | 119.7887 | 119.7129 | 0.13985 | -0.12817 | -0.40884 | 119.8306 | 119.7697 | 119.9754 | 119.7341 | -0.23698 | 119.7989 | 119.87 | 119.5893 | 119.7468 | -0.42507
1432.5156 | 120.2774 | -119.7556 | 0.28839 | 1.4211e-13 | -0.03025 | 0.014252 | -0.0036391 | -0.012974 | 0.019057 | -0.22533 | 0.018012 | 0.018676 | 0.015385 | 0.033512 | 0.0098942 | 0.065145 | 0.015142 | 0.023639 | 0.10249 | 0.059885 | 0.26101 | 0.046837 | 0.06515 | 0.036989 | -0.001407 | 0.07993 | 0.15107 | -0.11129 | -0.14583 | 119.8024 | -0.1859 | 119.8207 | 119.7792 | -0.023198 | -0.22851 | -0.027381 | 119.6097 | -0.20846 | 119.8207 | 119.7541 | 0.14443 | -0.13733 | -0.39968 | 119.858 | 119.8154 | 120.0166 | 119.7707 | -0.24155 | 119.8355 | 119.9066 | 119.6443 | 119.7925 | -0.43422
1434.2656 | 120.3323 | -119.783 | 0.27924 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0036391 | -0.01276 | 0.018416 | -0.23296 | 0.018225 | 0.018889 | 0.015812 | 0.033726 | 0.0096806 | 0.060567 | 0.019721 | 0.023639 | 0.11165 | 0.050727 | 0.25643 | 0.0331 | 0.060571 | 0.03241 | 0.003172 | 0.084508 | 0.15107 | -0.13419 | -0.15499 | 119.8161 | -0.16759 | 119.8436 | 119.8067 | -0.009461 | -0.22851 | -0.022805 | 119.628 | -0.19473 | 119.8436 | 119.7862 | 0.15816 | -0.12817 | -0.41342 | 119.8947 | 119.8337 | 120.0395 | 119.8027 | -0.24614 | 119.8675 | 119.9341 | 119.6488 | 119.8154 | -0.43423
1436.0156 | 120.2545 | -119.8975 | 0.30212 | 1.4211e-13 | -0.030036 | 0.014039 | -0.0038527 | -0.012546 | 0.018843 | -0.24059 | 0.018012 | 0.018889 | 0.016026 | 0.033512 | 0.010108 | 0.060567 | 0.019721 | 0.023639 | 0.10249 | 0.059885 | 0.25643 | 0.055995 | 0.060571 | 0.03241 | -0.001407 | 0.07993 | 0.15564 | -0.12503 | -0.15041 | 119.9535 | -0.19963 | 119.958 | 119.9211 | -0.032356 | -0.24224 | -0.045693 | 119.747 | -0.22219 | 119.958 | 119.8961 | 0.149 | -0.14648 | -0.42715 | 120 | 119.9573 | 120.1539 | 119.9172 | -0.24613 | 119.9774 | 120.0531 | 119.7724 | 119.9299 | -0.45254
1437.6875 | 120.3049 | -119.9158 | 0.31586 | 1.4211e-13 | -0.030036 | 0.013825 | -0.0040665 | -0.012974 | 0.019057 | -0.23296 | 0.018225 | 0.018249 | 0.015812 | 0.033512 | 0.0096806 | 0.065145 | 0.015142 | 0.01906 | 0.11165 | 0.050727 | 0.25643 | 0.042258 | 0.06515 | 0.027831 | -0.005985 | 0.07993 | 0.14649 | -0.13419 | -0.15041 | 119.958 | -0.20421 | 119.9809 | 119.9348 | -0.023198 | -0.26513 | -0.059426 | 119.7654 | -0.23593 | 119.9809 | 119.9098 | 0.14443 | -0.16937 | -0.45004 | 120.0274 | 119.9665 | 120.1722 | 119.9309 | -0.2736 | 119.9957 | 120.0623 | 119.7816 | 119.9436 | -0.46627
1439.4375 | 120.4239 | -119.9112 | 0.29297 | 1.4211e-13 | -0.030036 | 0.014039 | -0.0038527 | -0.013187 | 0.018629 | -0.24059 | 0.018225 | 0.018676 | 0.015812 | 0.033512 | 0.009467 | 0.069723 | 0.0243 | 0.01906 | 0.11165 | 0.059885 | 0.26101 | 0.0331 | 0.06515 | 0.03241 | -0.005985 | 0.089087 | 0.15107 | -0.12961 | -0.14583 | 119.9443 | -0.18132 | 119.9809 | 119.9303 | -0.01404 | -0.23308 | -0.031959 | 119.7654 | -0.20388 | 119.9763 | 119.9052 | 0.13985 | -0.1419 | -0.42258 | 120.0228 | 119.9711 | 120.1722 | 119.9355 | -0.25987 | 120.0003 | 120.0623 | 119.7816 | 119.9436 | -0.4388
1441.1094 | 120.4285 | -119.957 | 0.31128 | 1.4211e-13 | -0.029822 | 0.013825 | -0.0038527 | -0.012546 | 0.018843 | -0.22533 | 0.018225 | 0.018462 | 0.015812 | 0.033726 | 0.010108 | 0.060567 | 0.010564 | 0.014482 | 0.10707 | 0.050727 | 0.25643 | 0.046837 | 0.060571 | 0.023253 | -0.010564 | 0.084508 | 0.16022 | -0.10214 | -0.15499 | 120.0038 | -0.20421 | 120.0175 | 119.9715 | -0.032355 | -0.26055 | -0.054848 | 119.802 | -0.22677 | 120.0175 | 119.9464 | 0.14443 | -0.15106 | -0.41341 | 120.064 | 120.0077 | 120.2134 | 119.9675 | -0.26444 | 120.0415 | 120.1172 | 119.8548 | 119.9802 | -0.46627
1442.8594 | 120.4514 | -120.0348 | 0.33417 | 1.4211e-13 | -0.03025 | 0.014252 | -0.0036391 | -0.012974 | 0.018843 | -0.23296 | 0.018012 | 0.018676 | 0.015385 | 0.033512 | 0.0098942 | 0.060567 | 0.019721 | 0.023639 | 0.11165 | 0.050727 | 0.25643 | 0.046837 | 0.060571 | 0.023253 | -0.001407 | 0.084508 | 0.15564 | -0.10214 | -0.15041 | 120.0816 | -0.22252 | 120.0954 | 120.0584 | -0.023198 | -0.28344 | -0.077736 | 119.8844 | -0.24966 | 120.0954 | 120.0334 | 0.149 | -0.17852 | -0.4363 | 120.1464 | 120.0855 | 120.2912 | 120.0545 | -0.28733 | 120.1193 | 120.1904 | 119.9327 | 120.058 | -0.48458
1444.5469 | 120.5154 | -120.0485 | 0.30212 | 1.4211e-13 | -0.03025 | 0.014252 | -0.0036391 | -0.01276 | 0.018843 | -0.24059 | 0.018225 | 0.018676 | 0.016239 | 0.034153 | 0.010108 | 0.060567 | 0.019721 | 0.023639 | 0.11165 | 0.055306 | 0.26101 | 0.0331 | 0.06515 | 0.03241 | -0.005985 | 0.075351 | 0.15107 | -0.0884 | -0.14583 | 120.0816 | -0.19048 | 120.1091 | 120.0722 | -0.009461 | -0.24682 | -0.041114 | 119.9027 | -0.22677 | 120.1137 | 120.0425 | 0.13985 | -0.15106 | -0.39052 | 120.1602 | 120.1038 | 120.3095 | 120.0682 | -0.26902 | 120.1239 | 120.1996 | 119.9601 | 120.0809 | -0.44796
1446.2969 | 120.5887 | -120.0623 | 0.29755 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0036391 | -0.012974 | 0.01927 | -0.24822 | 0.018225 | 0.018462 | 0.016239 | 0.03394 | 0.010108 | 0.060567 | 0.015142 | 0.01906 | 0.10707 | 0.050727 | 0.25185 | 0.051416 | 0.06515 | 0.036989 | -0.001407 | 0.07993 | 0.15564 | -0.12503 | -0.15499 | 120.1137 | -0.19048 | 120.1228 | 120.0813 | -0.032356 | -0.24682 | -0.045694 | 119.9073 | -0.21762 | 120.1274 | 120.0608 | 0.15358 | -0.1419 | -0.42257 | 120.1693 | 120.113 | 120.3141 | 120.0774 | -0.24613 | 120.1422 | 120.2179 | 119.9372 | 120.0992 | -0.45254
1447.9844 | 120.5154 | -120.1492 | 0.32044 | 1.4211e-13 | -0.030463 | 0.014039 | -0.0034253 | -0.012974 | 0.019057 | -0.23296 | 0.018225 | 0.018889 | 0.015598 | 0.03394 | 0.010108 | 0.060567 | 0.019721 | 0.023639 | 0.11622 | 0.059885 | 0.26559 | 0.046837 | 0.060571 | 0.036989 | -0.005985 | 0.084508 | 0.15564 | -0.10671 | -0.14583 | 120.1961 | -0.20421 | 120.2098 | 120.1729 | -0.023198 | -0.26055 | -0.054847 | 120.0034 | -0.23593 | 120.2098 | 120.1432 | 0.13985 | -0.16479 | -0.42715 | 120.2655 | 120.2091 | 120.4148 | 120.169 | -0.2736 | 120.2337 | 120.3049 | 120.0425 | 120.1862 | -0.46627
1449.7344 | 120.6299 | -120.1538 | 0.32044 | 1.4211e-13 | -0.030036 | 0.014039 | -0.0040665 | -0.012974 | 0.018843 | -0.23296 | 0.017798 | 0.018889 | 0.015598 | 0.03394 | 0.0098942 | 0.065145 | 0.019721 | 0.023639 | 0.10707 | 0.059885 | 0.26101 | 0.042258 | 0.055992 | 0.027831 | -0.010564 | 0.084508 | 0.16022 | -0.11129 | -0.14583 | 120.1961 | -0.21337 | 120.219 | 120.1774 | -0.018619 | -0.26055 | -0.059425 | 120.008 | -0.23593 | 120.2098 | 120.1432 | 0.13527 | -0.16021 | -0.43173 | 120.2609 | 120.2137 | 120.4148 | 120.1735 | -0.27818 | 120.2383 | 120.314 | 120.0425 | 120.1816 | -0.46627
1451.4062 | 120.5658 | -120.2316 | 0.32501 | 1.4211e-13 | -0.029609 | 0.014039 | -0.0038527 | -0.01276 | 0.019057 | -0.22533 | 0.018225 | 0.019103 | 0.015598 | 0.033726 | 0.0098942 | 0.055988 | 0.019721 | 0.023639 | 0.11165 | 0.055306 | 0.26101 | 0.046837 | 0.060571 | 0.027831 | -0.005985 | 0.075351 | 0.14649 | -0.12503 | -0.15041 | 120.2785 | -0.21337 | 120.2876 | 120.2553 | -0.023198 | -0.26971 | -0.064002 | 120.0812 | -0.24966 | 120.2922 | 120.2256 | 0.14443 | -0.17853 | -0.45004 | 120.3433 | 120.2869 | 120.4926 | 120.2513 | -0.27818 | 120.307 | 120.3781 | 120.1066 | 120.2595 | -0.47542
1453.0938 | 120.7031 | -120.2179 | 0.27924 | 1.4211e-13 | -0.030036 | 0.014252 | -0.0036391 | -0.01276 | 0.019057 | -0.22533 | 0.018012 | 0.018676 | 0.015385 | 0.03394 | 0.010108 | 0.069723 | 0.015142 | 0.023639 | 0.11165 | 0.050727 | 0.25643 | 0.055995 | 0.060571 | 0.023253 | -0.010564 | 0.07993 | 0.15107 | -0.097557 | -0.15041 | 120.2739 | -0.16759 | 120.2876 | 120.2415 | -0.032356 | -0.22851 | -0.022805 | 120.0675 | -0.19931 | 120.2785 | 120.2073 | 0.13985 | -0.12817 | -0.37679 | 120.3295 | 120.2686 | 120.4743 | 120.233 | -0.22324 | 120.2978 | 120.369 | 120.1203 | 120.2411 | -0.42965
1454.8281 | 120.6207 | -120.2316 | 0.31586 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0034253 | -0.01276 | 0.019057 | -0.24059 | 0.018012 | 0.018676 | 0.016026 | 0.033726 | 0.0098942 | 0.065145 | 0.015142 | 0.01906 | 0.10707 | 0.055306 | 0.25643 | 0.0331 | 0.060571 | 0.027831 | -0.010564 | 0.07993 | 0.15107 | -0.12503 | -0.14125 | 120.2647 | -0.20879 | 120.2968 | 120.2507 | -0.01404 | -0.26055 | -0.059426 | 120.0904 | -0.23593 | 120.2922 | 120.2211 | 0.13069 | -0.16479 | -0.44089 | 120.3387 | 120.2869 | 120.4881 | 120.2468 | -0.28276 | 120.3116 | 120.3827 | 120.1066 | 120.2595 | -0.45711
1456.5 | 120.7169 | -120.2637 | 0.3067 | 1.4211e-13 | -0.029822 | 0.014252 | -0.0034253 | -0.01276 | 0.019057 | -0.24822 | 0.018225 | 0.018676 | 0.015171 | 0.033726 | 0.010108 | 0.060567 | 0.015142 | 0.01906 | 0.10707 | 0.055306 | 0.25185 | 0.037679 | 0.06515 | 0.027831 | -0.005985 | 0.089087 | 0.14649 | -0.12503 | -0.15041 | 120.3014 | -0.19963 | 120.3242 | 120.2827 | -0.018619 | -0.2514 | -0.05485 | 120.1133 | -0.21761 | 120.3288 | 120.2577 | 0.14443 | -0.16022 | -0.43173 | 120.3707 | 120.319 | 120.5155 | 120.2788 | -0.26902 | 120.3528 | 120.4102 | 120.1386 | 120.2915 | -0.45711
1458.25 | 120.6528 | -120.314 | 0.33875 | 1.4211e-13 | -0.029822 | 0.013825 | -0.0034253 | -0.013187 | 0.018629 | -0.24822 | 0.017798 | 0.018676 | 0.015812 | 0.03394 | 0.0098942 | 0.060567 | 0.015142 | 0.01906 | 0.10249 | 0.050727 | 0.25643 | 0.037679 | 0.060571 | 0.027831 | -0.005985 | 0.07993 | 0.14649 | -0.12503 | -0.15041 | 120.3517 | -0.23626 | 120.3746 | 120.3331 | -0.018619 | -0.28802 | -0.082314 | 120.1636 | -0.25882 | 120.3746 | 120.308 | 0.14443 | -0.19226 | -0.46377 | 120.4165 | 120.3648 | 120.5705 | 120.3292 | -0.30107 | 120.394 | 120.4605 | 120.189 | 120.3419 | -0.48916
1459.9844 | 120.7031 | -120.369 | 0.31586 | 1.4211e-13 | -0.029822 | 0.013825 | -0.0038527 | -0.01276 | 0.018843 | -0.22533 | 0.018012 | 0.018889 | 0.015812 | 0.03394 | 0.010108 | 0.060567 | 0.005985 | 0.014482 | 0.10249 | 0.059885 | 0.25185 | 0.046837 | 0.060571 | 0.027831 | -0.005985 | 0.084508 | 0.15564 | -0.092979 | -0.15041 | 120.4158 | -0.21337 | 120.4295 | 120.3834 | -0.032355 | -0.25597 | -0.064005 | 120.2185 | -0.23135 | 120.4295 | 120.363 | 0.14443 | -0.16021 | -0.40884 | 120.4714 | 120.4288 | 120.6208 | 120.3749 | -0.26902 | 120.4535 | 120.5246 | 120.276 | 120.3968 | -0.46627
1461.6562 | 120.8588 | -120.3369 | 0.3067 | 1.4211e-13 | -0.03025 | 0.014039 | -0.0038527 | -0.01276 | 0.019057 | -0.24822 | 0.017798 | 0.018462 | 0.015812 | 0.03394 | 0.0096806 | 0.060567 | 0.019721 | 0.01906 | 0.10249 | 0.050727 | 0.25185 | 0.065153 | 0.060571 | 0.03241 | -0.005985 | 0.07993 | 0.15107 | -0.11129 | -0.15499 | 120.4021 | -0.20421 | 120.3975 | 120.356 | -0.046093 | -0.25597 | -0.05485 | 120.1819 | -0.22677 | 120.3975 | 120.3309 | 0.14901 | -0.15564 | -0.418 | 120.4394 | 120.3876 | 120.5888 | 120.3566 | -0.24155 | 120.4168 | 120.488 | 120.2256 | 120.3693 | -0.46169
1463.4062 | 120.813 | -120.3644 | 0.34332 | 1.4211e-13 | -0.029609 | 0.013825 | -0.0036391 | -0.012974 | 0.018843 | -0.22533 | 0.018225 | 0.018889 | 0.015598 | 0.033726 | 0.0098942 | 0.065145 | 0.019721 | 0.023639 | 0.11165 | 0.055306 | 0.25185 | 0.069732 | 0.069728 | 0.036989 | -0.005985 | 0.084508 | 0.14649 | -0.10214 | -0.15041 | 120.4341 | -0.23168 | 120.4295 | 120.388 | -0.046093 | -0.28802 | -0.091471 | 120.214 | -0.25882 | 120.4341 | 120.3584 | 0.14443 | -0.19684 | -0.44546 | 120.476 | 120.4197 | 120.6162 | 120.3841 | -0.27359 | 120.4489 | 120.5109 | 120.2622 | 120.4014 | -0.49373
1465.0938 | 120.8862 | -120.3873 | 0.28381 | 1.4211e-13 | -0.029822 | 0.014252 | -0.0036391 | -0.01276 | 0.018843 | -0.23296 | 0.018012 | 0.018889 | 0.016026 | 0.033726 | 0.010322 | 0.055988 | 0.010564 | 0.023639 | 0.10707 | 0.055306 | 0.26101 | 0.07431 | 0.060571 | 0.027831 | -0.001407 | 0.084508 | 0.15107 | -0.10671 | -0.14583 | 120.4616 | -0.17674 | 120.4433 | 120.4109 | -0.050671 | -0.22851 | -0.022803 | 120.2414 | -0.1993 | 120.4478 | 120.3859 | 0.14443 | -0.13275 | -0.39053 | 120.4943 | 120.4426 | 120.6483 | 120.3978 | -0.2095 | 120.4718 | 120.5383 | 120.2806 | 120.4151 | -0.42965
1466.8438 | 120.8176 | -120.4514 | 0.32501 | 1.4211e-13 | -0.03025 | 0.014039 | -0.0036391 | -0.012974 | 0.019057 | -0.23296 | 0.018439 | 0.018676 | 0.015812 | 0.03394 | 0.0096806 | 0.060567 | 0.019721 | 0.023639 | 0.11165 | 0.055306 | 0.25185 | 0.051416 | 0.060571 | 0.03241 | -0.005985 | 0.07993 | 0.14649 | -0.11587 | -0.15957 | 120.5028 | -0.21337 | 120.5119 | 120.475 | -0.027777 | -0.26971 | -0.07316 | 120.2918 | -0.24508 | 120.5119 | 120.4454 | 0.15358 | -0.17853 | -0.44088 | 120.563 | 120.5067 | 120.7032 | 120.4711 | -0.2736 | 120.5313 | 120.5978 | 120.3355 | 120.4838 | -0.48458
1468.5781 | 120.8313 | -120.4651 | 0.32501 | 1.4211e-13 | -0.029395 | 0.013825 | -0.0038527 | -0.01276 | 0.019057 | -0.2177 | 0.018225 | 0.018676 | 0.015598 | 0.034153 | 0.010108 | 0.065145 | 0.010564 | 0.028217 | 0.11622 | 0.050727 | 0.25185 | 0.055995 | 0.069728 | 0.03241 | -0.001407 | 0.084508 | 0.15107 | -0.12045 | -0.15041 | 120.5211 | -0.20879 | 120.5302 | 120.4933 | -0.027778 | -0.27429 | -0.07316 | 120.3147 | -0.2405 | 120.5348 | 120.4637 | 0.149 | -0.17395 | -0.44546 | 120.5813 | 120.5158 | 120.7169 | 120.4757 | -0.26902 | 120.5496 | 120.6162 | 120.3446 | 120.4975 | -0.47542
1470.2656 | 120.9412 | -120.4559 | 0.32501 | 1.4211e-13 | -0.029822 | 0.014252 | -0.0036391 | -0.012546 | 0.019057 | -0.22533 | 0.018012 | 0.018462 | 0.015598 | 0.03394 | 0.0098942 | 0.065145 | 0.019721 | 0.01906 | 0.10707 | 0.059885 | 0.25643 | 0.051416 | 0.06515 | 0.023253 | 0.003172 | 0.084508 | 0.14649 | -0.12045 | -0.15499 | 120.5073 | -0.21794 | 120.5211 | 120.475 | -0.032356 | -0.26513 | -0.068581 | 120.3009 | -0.2405 | 120.5211 | 120.4591 | 0.15816 | -0.17853 | -0.44546 | 120.563 | 120.5158 | 120.7124 | 120.4757 | -0.2736 | 120.5404 | 120.6024 | 120.3355 | 120.4792 | -0.48
1472 | 120.9915 | -120.4697 | 0.28839 | 1.4211e-13 | -0.029822 | 0.013825 | -0.0036391 | -0.012546 | 0.018843 | -0.24822 | 0.018225 | 0.018676 | 0.015598 | 0.033726 | 0.010108 | 0.065145 | 0.015142 | 0.01906 | 0.11622 | 0.059885 | 0.25643 | 0.060574 | 0.060571 | 0.036989 | -0.010564 | 0.07993 | 0.15107 | -0.097557 | -0.15499 | 120.5302 | -0.17217 | 120.5348 | 120.4887 | -0.041514 | -0.22851 | -0.03196 | 120.3147 | -0.20846 | 120.5302 | 120.4591 | 0.14443 | -0.13733 | -0.38595 | 120.5859 | 120.5296 | 120.7261 | 120.4848 | -0.22782 | 120.5496 | 120.6207 | 120.3721 | 120.5067 | -0.44338
1473.7344 | 121.0007 | -120.52 | 0.30212 | 1.4211e-13 | -0.030036 | 0.014466 | -0.0042801 | -0.01276 | 0.018416 | -0.23296 | 0.018225 | 0.018676 | 0.015598 | 0.03394 | 0.0096806 | 0.065145 | 0.015142 | 0.023639 | 0.11165 | 0.055306 | 0.25643 | 0.078889 | 0.06515 | 0.03241 | -0.001407 | 0.070773 | 0.16022 | -0.11129 | -0.15041 | 120.5989 | -0.19048 | 120.5852 | 120.5437 | -0.05525 | -0.24682 | -0.045693 | 120.3696 | -0.23135 | 120.5852 | 120.5186 | 0.149 | -0.1419 | -0.41342 | 120.6317 | 120.5753 | 120.7765 | 120.5352 | -0.22324 | 120.5908 | 120.6802 | 120.4087 | 120.5524 | -0.45254
1475.4844 | 121.019 | -120.5475 | 0.32044 | 1.4211e-13 | -0.029822 | 0.014252 | -0.0038527 | -0.012546 | 0.018629 | -0.23296 | 0.018225 | 0.018676 | 0.015812 | 0.03394 | 0.0098942 | 0.060567 | 0.015142 | 0.01906 | 0.11165 | 0.055306 | 0.26101 | 0.055995 | 0.060571 | 0.027831 | -0.010564 | 0.070773 | 0.16022 | -0.038035 | -0.14125 | 120.6035 | -0.20879 | 120.6081 | 120.5665 | -0.036935 | -0.26513 | -0.059425 | 120.4062 | -0.24966 | 120.6081 | 120.5369 | 0.13069 | -0.16021 | -0.35847 | 120.6591 | 120.6028 | 120.8085 | 120.5626 | -0.26444 | 120.6183 | 120.7077 | 120.5095 | 120.5753 | -0.46169
1477.1562 | 120.9457 | -120.5658 | 0.3479 | 1.4211e-13 | -0.029609 | 0.014039 | -0.0038527 | -0.012546 | 0.019057 | -0.22533 | 0.018012 | 0.019103 | 0.015598 | 0.033726 | 0.010108 | 0.060567 | 0.015142 | 0.023639 | 0.10707 | 0.059885 | 0.26559 | 0.037679 | 0.060571 | 0.03241 | -0.010564 | 0.070773 | 0.15107 | -0.13419 | -0.14583 | 120.6035 | -0.24083 | 120.6264 | 120.5894 | -0.01404 | -0.28801 | -0.082312 | 120.42 | -0.27713 | 120.6264 | 120.5552 | 0.13527 | -0.19683 | -0.48209 | 120.6729 | 120.6257 | 120.8314 | 120.5809 | -0.31022 | 120.6366 | 120.7169 | 120.4316 | 120.5982 | -0.49373
1478.9062 | 120.9686 | -120.6162 | 0.33875 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0034253 | -0.012546 | 0.019057 | -0.24059 | 0.018012 | 0.018676 | 0.015812 | 0.033726 | 0.0096806 | 0.060567 | 0.015142 | 0.014482 | 0.11165 | 0.055306 | 0.25185 | 0.088047 | 0.060571 | 0.03241 | -0.010564 | 0.075351 | 0.15107 | -0.0884 | -0.15041 | 120.7042 | -0.2271 | 120.6767 | 120.6306 | -0.073565 | -0.28344 | -0.086893 | 120.4657 | -0.26339 | 120.6767 | 120.6056 | 0.13985 | -0.18768 | -0.42714 | 120.7278 | 120.6715 | 120.868 | 120.6313 | -0.2507 | 120.6915 | 120.7672 | 120.5278 | 120.6486 | -0.48916
1480.6719 | 120.9732 | -120.6345 | 0.33417 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0040665 | -0.01276 | 0.01927 | -0.23296 | 0.018012 | 0.018676 | 0.015812 | 0.03394 | 0.0098942 | 0.060567 | 0.019721 | 0.028217 | 0.11165 | 0.059885 | 0.25643 | 0.055995 | 0.060571 | 0.03241 | -0.001407 | 0.070773 | 0.14649 | -0.12503 | -0.15041 | 120.6905 | -0.22252 | 120.695 | 120.6627 | -0.027778 | -0.27428 | -0.077736 | 120.484 | -0.26339 | 120.695 | 120.6331 | 0.149 | -0.18768 | -0.4592 | 120.7461 | 120.6943 | 120.8909 | 120.6542 | -0.27817 | 120.7052 | 120.7809 | 120.5094 | 120.6669 | -0.48458
1482.3438 | 121.019 | -120.639 | 0.33875 | 1.4211e-13 | -0.029609 | 0.013825 | -0.0034253 | -0.013187 | 0.018843 | -0.23296 | 0.018225 | 0.018889 | 0.016026 | 0.03394 | 0.010108 | 0.060567 | 0.0243 | 0.023639 | 0.1208 | 0.055306 | 0.25643 | 0.060574 | 0.055992 | 0.027831 | -0.005985 | 0.070773 | 0.14649 | -0.12503 | -0.15499 | 120.6996 | -0.21794 | 120.6996 | 120.6627 | -0.036935 | -0.28344 | -0.082314 | 120.484 | -0.26797 | 120.695 | 120.6331 | 0.14901 | -0.19226 | -0.46377 | 120.7598 | 120.6943 | 120.8955 | 120.6633 | -0.27817 | 120.7098 | 120.7855 | 120.514 | 120.6669 | -0.49374
1484.0156 | 121.1243 | -120.6024 | 0.29755 | 1.4211e-13 | -0.029609 | 0.013825 | -0.0036391 | -0.012546 | 0.018843 | -0.23296 | 0.018012 | 0.018889 | 0.016026 | 0.03394 | 0.0098942 | 0.065145 | 0.015142 | 0.023639 | 0.10707 | 0.055306 | 0.25185 | 0.051416 | 0.055992 | 0.027831 | -0.010564 | 0.066194 | 0.15107 | -0.10671 | -0.16415 | 120.6538 | -0.19048 | 120.6676 | 120.6261 | -0.027777 | -0.24224 | -0.045694 | 120.4383 | -0.23135 | 120.6584 | 120.5919 | 0.15358 | -0.14648 | -0.40426 | 120.7095 | 120.6577 | 120.8543 | 120.6176 | -0.24613 | 120.6686 | 120.7535 | 120.4957 | 120.6302 | -0.46169
1485.7656 | 121.1746 | -120.6299 | 0.31128 | 1.4211e-13 | -0.030036 | 0.014039 | -0.0038527 | -0.01276 | 0.018629 | -0.24059 | 0.017798 | 0.018676 | 0.015598 | 0.03394 | 0.0096806 | 0.060567 | 0.019721 | 0.023639 | 0.11165 | 0.059885 | 0.25643 | 0.046837 | 0.069728 | 0.023253 | -0.005985 | 0.066194 | 0.14649 | -0.10671 | -0.14583 | 120.6767 | -0.19963 | 120.6905 | 120.6535 | -0.023198 | -0.25139 | -0.054848 | 120.4841 | -0.24508 | 120.6996 | 120.6239 | 0.13985 | -0.16479 | -0.41799 | 120.7415 | 120.6898 | 120.8863 | 120.6496 | -0.26444 | 120.6961 | 120.7764 | 120.5232 | 120.6531 | -0.45711
1487.5 | 121.1746 | -120.6619 | 0.30212 | 1.4211e-13 | -0.029822 | 0.013825 | -0.0038527 | -0.012974 | 0.018843 | -0.22533 | 0.018225 | 0.018676 | 0.016026 | 0.033726 | 0.0096806 | 0.060567 | 0.019721 | 0.014482 | 0.11165 | 0.050727 | 0.25185 | 0.07431 | 0.055992 | 0.03241 | -0.005985 | 0.066194 | 0.15107 | -0.083821 | -0.15041 | 120.7362 | -0.19048 | 120.7225 | 120.6764 | -0.059828 | -0.2514 | -0.050272 | 120.5115 | -0.23593 | 120.7179 | 120.6559 | 0.14443 | -0.15106 | -0.38594 | 120.7736 | 120.7127 | 120.9138 | 120.6816 | -0.22781 | 120.7281 | 120.813 | 120.5781 | 120.6943 | -0.45254
1489.2344 | 121.0922 | -120.7214 | 0.34332 | 1.4211e-13 | -0.030036 | 0.014039 | -0.0036391 | -0.01276 | 0.018843 | -0.24059 | 0.018439 | 0.018889 | 0.015598 | 0.034153 | 0.0098942 | 0.060567 | 0.015142 | 0.01906 | 0.11622 | 0.059885 | 0.25643 | 0.046837 | 0.06515 | 0.027831 | 0.003172 | 0.07993 | 0.14649 | -0.12961 | -0.15957 | 120.7683 | -0.2271 | 120.782 | 120.7405 | -0.027777 | -0.28344 | -0.086892 | 120.5619 | -0.26339 | 120.7866 | 120.7246 | 0.16274 | -0.19684 | -0.47293 | 120.8377 | 120.7813 | 120.9779 | 120.7366 | -0.29649 | 120.8014 | 120.8679 | 120.5918 | 120.7493 | -0.50289
1490.9844 | 121.2021 | -120.6802 | 0.3067 | 1.4211e-13 | -0.029822 | 0.013825 | -0.0034253 | -0.012974 | 0.019057 | -0.24059 | 0.018012 | 0.018676 | 0.015385 | 0.03394 | 0.010108 | 0.060567 | 0.015142 | 0.023639 | 0.11622 | 0.059885 | 0.25643 | 0.051416 | 0.06515 | 0.036989 | -0.005985 | 0.061616 | 0.15107 | -0.12961 | -0.15041 | 120.7317 | -0.19048 | 120.7408 | 120.7039 | -0.027777 | -0.24682 | -0.050271 | 120.5298 | -0.24509 | 120.7454 | 120.6743 | 0.14443 | -0.15564 | -0.43631 | 120.7965 | 120.7401 | 120.9367 | 120.6954 | -0.25529 | 120.7419 | 120.8313 | 120.5506 | 120.7172 | -0.45711
1492.6562 | 121.2387 | -120.6985 | 0.29755 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0036391 | -0.012974 | 0.018629 | -0.23296 | 0.018012 | 0.018676 | 0.015812 | 0.03394 | 0.0098942 | 0.065145 | 0.015142 | 0.01906 | 0.10707 | 0.059885 | 0.25185 | 0.046837 | 0.06515 | 0.027831 | -0.005985 | 0.070773 | 0.15107 | -0.12045 | -0.15041 | 120.7454 | -0.19048 | 120.7637 | 120.7176 | -0.027777 | -0.23766 | -0.045694 | 120.5481 | -0.22677 | 120.7637 | 120.6926 | 0.14443 | -0.14648 | -0.418 | 120.8056 | 120.7584 | 120.9504 | 120.7137 | -0.25071 | 120.7693 | 120.8496 | 120.5781 | 120.7264 | -0.44796
1494.3906 | 121.2204 | -120.7306 | 0.32959 | 1.4211e-13 | -0.030036 | 0.014039 | -0.0036391 | -0.012974 | 0.018843 | -0.23296 | 0.018012 | 0.018676 | 0.015598 | 0.034153 | 0.0098942 | 0.060567 | 0.010564 | 0.028217 | 0.10707 | 0.055306 | 0.26101 | 0.055995 | 0.06515 | 0.027831 | -0.005985 | 0.075351 | 0.16022 | -0.11587 | -0.15499 | 120.7866 | -0.22252 | 120.7912 | 120.7588 | -0.027778 | -0.27428 | -0.06858 | 120.5756 | -0.25424 | 120.7957 | 120.7246 | 0.14901 | -0.16937 | -0.44546 | 120.8377 | 120.7859 | 120.9916 | 120.7412 | -0.27359 | 120.8059 | 120.8908 | 120.6147 | 120.7584 | -0.48458
1496.125 | 121.2158 | -120.7764 | 0.31128 | 1.4211e-13 | -0.029822 | 0.014252 | -0.0032117 | -0.012974 | 0.019057 | -0.23296 | 0.018012 | 0.018676 | 0.015812 | 0.03394 | 0.0096806 | 0.065145 | 0.019721 | 0.023639 | 0.11165 | 0.055306 | 0.26101 | 0.046837 | 0.060571 | 0.023253 | -0.005985 | 0.070773 | 0.16022 | -0.13419 | -0.15499 | 120.8232 | -0.19963 | 120.8415 | 120.8 | -0.023198 | -0.25597 | -0.050269 | 120.6214 | -0.24051 | 120.8369 | 120.7704 | 0.14901 | -0.15106 | -0.44546 | 120.888 | 120.8317 | 121.0374 | 120.7961 | -0.26444 | 120.8471 | 120.9366 | 120.6422 | 120.7996 | -0.46627
1497.7969 | 121.2799 | -120.7718 | 0.27924 | 1.4211e-13 | -0.029395 | 0.013825 | -0.0034253 | -0.01276 | 0.018843 | -0.23296 | 0.018012 | 0.018676 | 0.016026 | 0.034153 | 0.0098942 | 0.055988 | 0.019721 | 0.023639 | 0.11165 | 0.064464 | 0.25643 | 0.046837 | 0.06515 | 0.03241 | -0.010564 | 0.070773 | 0.14649 | -0.12045 | -0.14583 | 120.8186 | -0.16759 | 120.8278 | 120.7954 | -0.023198 | -0.21477 | -0.022805 | 120.626 | -0.20846 | 120.8369 | 120.7612 | 0.13527 | -0.13275 | -0.39969 | 120.8834 | 120.8363 | 121.0282 | 120.7915 | -0.2324 | 120.8426 | 120.9183 | 120.6513 | 120.8042 | -0.42507
1499.5312 | 121.3074 | -120.8084 | 0.2655 | 1.4211e-13 | -0.030036 | 0.013825 | -0.0038527 | -0.01276 | 0.019057 | -0.23296 | 0.018225 | 0.018462 | 0.015598 | 0.03394 | 0.0096806 | 0.065145 | 0.010564 | 0.014482 | 0.11622 | 0.046148 | 0.26101 | 0.065153 | 0.06515 | 0.027831 | -0.010564 | 0.070773 | 0.15107 | -0.10671 | -0.16415 | 120.8736 | -0.14928 | 120.8736 | 120.8229 | -0.050671 | -0.21935 | -0.004493 | 120.6443 | -0.19473 | 120.8736 | 120.7978 | 0.15358 | -0.11444 | -0.37222 | 120.9246 | 120.8546 | 121.0694 | 120.819 | -0.20035 | 120.8792 | 120.9595 | 120.7017 | 120.8362 | -0.42965
1501.2188 | 121.2845 | -120.7993 | 0.28381 | 1.4211e-13 | -0.029822 | 0.013825 | -0.0038527 | -0.013187 | 0.018843 | -0.23296 | 0.018012 | 0.018462 | 0.015598 | 0.033726 | 0.0096806 | 0.060567 | 0.015142 | 0.023639 | 0.11622 | 0.055306 | 0.25643 | 0.037679 | 0.060571 | 0.023253 | -0.005985 | 0.075351 | 0.1648 | -0.11587 | -0.15041 | 120.8369 | -0.16759 | 120.8598 | 120.8229 | -0.01404 | -0.22851 | -0.027382 | 120.6488 | -0.20846 | 120.8598 | 120.7933 | 0.14443 | -0.11901 | -0.39968 | 120.9155 | 120.8546 | 121.0557 | 120.8144 | -0.24613 | 120.8746 | 120.9641 | 120.6834 | 120.8225 | -0.43422
1502.9531 | 121.2524 | -120.8725 | 0.28381 | 1.4211e-13 | -0.029822 | 0.014252 | -0.0036391 | -0.01276 | 0.019057 | -0.23296 | 0.018225 | 0.018676 | 0.016026 | 0.03394 | 0.010108 | 0.060567 | 0.0243 | 0.023639 | 0.11165 | 0.064464 | 0.26101 | 0.0331 | 0.06515 | 0.03241 | -0.005985 | 0.075351 | 0.15564 | -0.097557 | -0.14583 | 120.9056 | -0.17217 | 120.9331 | 120.8961 | -0.009461 | -0.21935 | -0.022803 | 120.7267 | -0.20846 | 120.9376 | 120.8665 | 0.13985 | -0.12817 | -0.38137 | 120.9841 | 120.937 | 121.1335 | 120.8968 | -0.25071 | 120.9478 | 121.0281 | 120.7749 | 120.9049 | -0.42965
1504.625 | 121.2067 | -120.9091 | 0.29755 | 1.4211e-13 | -0.029822 | 0.013611 | -0.0038527 | -0.012974 | 0.018629 | -0.22533 | 0.018012 | 0.018249 | 0.015812 | 0.033726 | 0.0096806 | 0.065145 | 0.010564 | 0.01906 | 0.11165 | 0.050727 | 0.26101 | 0.046837 | 0.06515 | 0.027831 | -0.010564 | 0.070773 | 0.15564 | -0.12045 | -0.14583 | 120.956 | -0.1859 | 120.9743 | 120.9282 | -0.027777 | -0.24682 | -0.036536 | 120.7633 | -0.22677 | 120.9743 | 120.8986 | 0.13527 | -0.1419 | -0.418 | 121.0208 | 120.9598 | 121.1701 | 120.9197 | -0.25071 | 120.9799 | 121.0648 | 120.7887 | 120.937 | -0.44338
1506.375 | 121.2341 | -120.8908 | 0.31586 | 1.4211e-13 | -0.030036 | 0.013825 | -0.0036391 | -0.012974 | 0.018843 | -0.24059 | 0.018225 | 0.018676 | 0.015598 | 0.03394 | 0.0096806 | 0.069723 | 0.015142 | 0.023639 | 0.11622 | 0.059885 | 0.25643 | 0.037679 | 0.06515 | 0.023253 | -0.001407 | 0.070773 | 0.15107 | -0.083821 | -0.14583 | 120.9285 | -0.19963 | 120.9605 | 120.9144 | -0.01404 | -0.25597 | -0.059426 | 120.745 | -0.24508 | 120.956 | 120.8894 | 0.14443 | -0.16479 | -0.39968 | 121.007 | 120.9507 | 121.1472 | 120.906 | -0.27818 | 120.9616 | 121.0419 | 120.807 | 120.9141 | -0.46169
1508.1094 | 121.2708 | -120.9274 | 0.27924 | 1.4211e-13 | -0.029822 | 0.014252 | -0.0036391 | -0.012546 | 0.018843 | -0.22533 | 0.018012 | 0.018889 | 0.015812 | 0.03394 | 0.010108 | 0.060567 | 0.015142 | 0.023639 | 0.10707 | 0.055306 | 0.24727 | 0.055995 | 0.06515 | 0.027831 | -0.005985 | 0.070773 | 0.15564 | -0.12503 | -0.15499 | 120.9834 | -0.17217 | 120.988 | 120.9511 | -0.032356 | -0.22393 | -0.031962 | 120.7724 | -0.20846 | 120.9926 | 120.9214 | 0.14901 | -0.12359 | -0.40426 | 121.0345 | 120.9827 | 121.1747 | 120.9426 | -0.22324 | 120.9982 | 121.0831 | 120.8024 | 120.9553 | -0.43423
1509.8594 | 121.3531 | -120.9183 | 0.29297 | 1.4211e-13 | -0.03025 | 0.014252 | -0.0038527 | -0.013187 | 0.018629 | -0.24059 | 0.018012 | 0.018676 | 0.015812 | 0.033726 | 0.010108 | 0.060567 | 0.019721 | 0.01906 | 0.11165 | 0.059885 | 0.25643 | 0.055995 | 0.069728 | 0.027831 | -0.010564 | 0.070773 | 0.16022 | -0.10671 | -0.15041 | 120.9743 | -0.18132 | 120.9788 | 120.9373 | -0.036935 | -0.23308 | -0.036538 | 120.7679 | -0.2222 | 120.988 | 120.9077 | 0.13985 | -0.13275 | -0.39968 | 121.0299 | 120.9782 | 121.1747 | 120.938 | -0.23697 | 120.989 | 121.0785 | 120.8116 | 120.9461 | -0.44338
1511.5469 | 121.2891 | -120.9869 | 0.3067 | 1.4211e-13 | -0.029822 | 0.014252 | -0.0036391 | -0.01276 | 0.018629 | -0.24059 | 0.018012 | 0.018462 | 0.015598 | 0.033726 | 0.0096806 | 0.065145 | 0.0243 | 0.032795 | 0.10707 | 0.059885 | 0.25643 | 0.07431 | 0.055992 | 0.023253 | -0.005985 | 0.061616 | 0.16022 | -0.0884 | -0.14583 | 121.0612 | -0.19963 | 121.0521 | 121.0197 | -0.041515 | -0.24682 | -0.050271 | 120.8411 | -0.24509 | 121.0429 | 120.981 | 0.13985 | -0.14648 | -0.3951 | 121.094 | 121.0468 | 121.2434 | 121.0112 | -0.23239 | 121.0486 | 121.1472 | 120.8985 | 121.0102 | -0.45253
1513.2969 | 121.4218 | -120.9229 | 0.27008 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0038527 | -0.01276 | 0.019057 | -0.23296 | 0.018012 | 0.018676 | 0.015812 | 0.034153 | 0.0096806 | 0.055988 | 0.010564 | 0.032795 | 0.11165 | 0.055306 | 0.25643 | 0.060574 | 0.06515 | 0.027831 | -0.005985 | 0.070773 | 0.16022 | -0.11587 | -0.15499 | 120.9834 | -0.15843 | 120.9788 | 120.9556 | -0.027779 | -0.21478 | -0.01365 | 120.7679 | -0.19931 | 120.988 | 120.9169 | 0.14901 | -0.10986 | -0.38595 | 121.0345 | 120.9782 | 121.1793 | 120.9334 | -0.20951 | 120.9936 | 121.0831 | 120.807 | 120.9507 | -0.42507
1514.9688 | 121.4447 | -120.9503 | 0.25635 | 1.4211e-13 | -0.030036 | 0.014039 | -0.0036391 | -0.012974 | 0.018629 | -0.24059 | 0.018225 | 0.018889 | 0.015812 | 0.033512 | 0.0098942 | 0.060567 | 0.019721 | 0.01906 | 0.11165 | 0.055306 | 0.25643 | 0.055995 | 0.06515 | 0.027831 | -0.005985 | 0.066194 | 0.16022 | -0.0884 | -0.15041 | 121.0063 | -0.1447 | 121.0109 | 120.9694 | -0.036935 | -0.20104 | 8.3e-05 | 120.7999 | -0.19015 | 121.0155 | 120.9443 | 0.14443 | -0.096126 | -0.34475 | 121.062 | 121.0056 | 121.2067 | 120.97 | -0.20035 | 121.0165 | 121.1105 | 120.8619 | 120.9781 | -0.40676
1516.7188 | 121.3715 | -120.9778 | 0.27008 | 1.4211e-13 | -0.030036 | 0.014039 | -0.0036391 | -0.012974 | 0.019057 | -0.2177 | 0.017798 | 0.018462 | 0.015385 | 0.033726 | 0.0096806 | 0.065145 | 0.015142 | 0.01906 | 0.10707 | 0.059885 | 0.25185 | 0.060574 | 0.06515 | 0.03241 | -0.005985 | 0.075351 | 0.16022 | -0.12503 | -0.15041 | 121.0384 | -0.16301 | 121.0429 | 120.9968 | -0.041514 | -0.2102 | -0.018229 | 120.8274 | -0.19473 | 121.0429 | 120.9718 | 0.14443 | -0.10986 | -0.39511 | 121.0849 | 121.0377 | 121.2296 | 120.9929 | -0.20951 | 121.0531 | 121.138 | 120.8528 | 121.0102 | -0.42049
1518.4531 | 121.4264 | -120.9686 | 0.28381 | 1.4211e-13 | -0.030036 | 0.014039 | -0.0036391 | -0.012546 | 0.018843 | -0.22533 | 0.017798 | 0.018676 | 0.015385 | 0.03394 | 0.0098942 | 0.060567 | 0.019721 | 0.023639 | 0.11165 | 0.055306 | 0.25643 | 0.055995 | 0.060571 | 0.018674 | -0.001407 | 0.061616 | 0.16022 | -0.083821 | -0.15041 | 121.0246 | -0.17217 | 121.0292 | 120.9923 | -0.032356 | -0.22851 | -0.027382 | 120.8182 | -0.2222 | 121.0292 | 120.9672 | 0.149 | -0.12359 | -0.36763 | 121.0803 | 121.0239 | 121.2251 | 120.9883 | -0.22782 | 121.0302 | 121.1288 | 120.8848 | 120.9873 | -0.43422
1520.125 | 121.344 | -121.2158 | 0.14191 | 1.4211e-13 | -0.030036 | 0.014252 | -0.0038527 | -0.01276 | 0.018629 | -0.24059 | 0.017798 | 0.018889 | 0.015598 | 0.03394 | 0.0096806 | 0.065145 | 0.019721 | 0.023639 | 0.11622 | 0.059885 | 0.26101 | 0.060574 | 0.06515 | 0.027831 | -0.010564 | 0.066194 | 0.15564 | -0.13419 | -0.15957 | 121.2764 | -0.025682 | 121.281 | 121.2395 | -0.036935 | -0.082022 | 0.1191 | 121.0562 | -0.075713 | 121.281 | 121.2053 | 0.14901 | 0.013736 | -0.27609 | 121.332 | 121.2757 | 121.4768 | 121.2355 | -0.081333 | 121.282 | 121.3715 | 121.0816 | 121.2437 | -0.30148
1521.875 | 121.4355 | -121.1563 | 0.10986 | 1.4211e-13 | -0.030036 | 0.014252 | -0.0036391 | -0.012546 | 0.018843 | -0.22533 | 0.018225 | 0.018889 | 0.016026 | 0.03394 | 0.0096806 | 0.060567 | 0.010564 | 0.032795 | 0.10707 | 0.059885 | 0.25185 | 0.046837 | 0.06515 | 0.023253 | -0.005985 | 0.075351 | 0.15107 | -0.12503 | -0.15499 | 121.2031 | -0.002795 | 121.2169 | 121.1891 | -0.014042 | -0.049978 | 0.14199 | 121.0013 | -0.034512 | 121.2215 | 121.1503 | 0.14901 | 0.041202 | -0.23489 | 121.2634 | 121.2162 | 121.4082 | 121.1669 | -0.063026 | 121.2317 | 121.3074 | 121.0313 | 121.1796 | -0.26485
1523.625 | 121.3898 | -121.2296 | 0.14191 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0036391 | -0.01276 | 0.019484 | -0.23296 | 0.017798 | 0.018462 | 0.015812 | 0.034153 | 0.0098942 | 0.060567 | 0.005985 | 0.01906 | 0.11165 | 0.059885 | 0.25643 | 0.037679 | 0.055992 | 0.027831 | -0.005985 | 0.066194 | 0.15107 | -0.12045 | -0.15499 | 121.2672 | -0.03026 | 121.2901 | 121.2486 | -0.018619 | -0.082022 | 0.11452 | 121.0746 | -0.075713 | 121.2855 | 121.2236 | 0.14901 | 0.009158 | -0.26236 | 121.3412 | 121.2894 | 121.486 | 121.2355 | -0.10423 | 121.2957 | 121.3806 | 121.1091 | 121.2574 | -0.2969
1525.375 | 121.4264 | -121.2158 | 0.13733 | 1.4211e-13 | -0.030036 | 0.014252 | -0.0040665 | -0.01276 | 0.019057 | -0.2177 | 0.018225 | 0.018889 | 0.015598 | 0.03394 | 0.0098942 | 0.055988 | 0.019721 | 0.01906 | 0.10707 | 0.055306 | 0.25185 | 0.028521 | 0.060571 | 0.03241 | -0.005985 | 0.075351 | 0.15564 | -0.070086 | -0.15041 | 121.2443 | -0.030261 | 121.2718 | 121.2349 | -0.009461 | -0.082023 | 0.11452 | 121.0654 | -0.061978 | 121.2764 | 121.2098 | 0.14443 | 0.018314 | -0.20742 | 121.3229 | 121.2711 | 121.4677 | 121.2355 | -0.10881 | 121.2912 | 121.3715 | 121.1457 | 121.2482 | -0.28774
1527.0469 | 121.4035 | -121.2479 | 0.13275 | 1.4211e-13 | -0.030036 | 0.013611 | -0.0038527 | -0.012974 | 0.019057 | -0.24059 | 0.018012 | 0.018889 | 0.015812 | 0.034153 | 0.010108 | 0.069723 | 0.010564 | 0.023639 | 0.11622 | 0.059885 | 0.25643 | 0.060574 | 0.051413 | 0.036989 | -0.005985 | 0.070773 | 0.15107 | -0.12045 | -0.15041 | 121.3084 | -0.016526 | 121.3176 | 121.2715 | -0.036935 | -0.072866 | 0.12368 | 121.0975 | -0.061978 | 121.2993 | 121.2419 | 0.14443 | 0.018314 | -0.2532 | 121.3641 | 121.3077 | 121.5043 | 121.2584 | -0.072177 | 121.3186 | 121.3989 | 121.1274 | 121.2849 | -0.28316
1528.7969 | 121.4172 | -121.2387 | 0.14648 | 1.4211e-13 | -0.030036 | 0.014252 | -0.0036391 | -0.012974 | 0.018629 | -0.24059 | 0.018439 | 0.018676 | 0.015385 | 0.03394 | 0.0096806 | 0.060567 | 0.019721 | 0.023639 | 0.11622 | 0.050727 | 0.25643 | 0.046837 | 0.074307 | 0.036989 | -0.010564 | 0.070773 | 0.15107 | -0.10214 | -0.15499 | 121.2855 | -0.030259 | 121.2993 | 121.2623 | -0.023198 | -0.095757 | 0.10995 | 121.0837 | -0.075711 | 121.313 | 121.2281 | 0.14443 | 0.004581 | -0.24862 | 121.3549 | 121.2894 | 121.4951 | 121.2584 | -0.099647 | 121.3095 | 121.3898 | 121.1366 | 121.2757 | -0.30147
1530.5625 | 121.5042 | -121.2662 | 0.10071 | 1.4211e-13 | -0.030036 | 0.013611 | -0.0038527 | -0.01276 | 0.019057 | -0.23296 | 0.018012 | 0.018889 | 0.015812 | 0.03394 | 0.0096806 | 0.060567 | 0.0243 | 0.023639 | 0.11165 | 0.055306 | 0.25185 | 0.069732 | 0.060571 | 0.027831 | -0.005985 | 0.075351 | 0.14649 | -0.10214 | -0.14583 | 121.3359 | 0.010939 | 121.3267 | 121.2898 | -0.046093 | -0.045402 | 0.15114 | 121.1203 | -0.025357 | 121.3267 | 121.2602 | 0.13985 | 0.045778 | -0.20284 | 121.3778 | 121.3215 | 121.518 | 121.2905 | -0.030976 | 121.3415 | 121.4127 | 121.164 | 121.294 | -0.24654
1532.25 | 121.5042 | -121.2616 | 0.10071 | 1.4211e-13 | -0.029822 | 0.013611 | -0.0036391 | -0.012974 | 0.018416 | -0.23296 | 0.018012 | 0.018462 | 0.015812 | 0.03394 | 0.0098942 | 0.060567 | 0.019721 | 0.023639 | 0.11165 | 0.064464 | 0.25643 | 0.051416 | 0.06515 | 0.027831 | -0.001407 | 0.075351 | 0.14649 | -0.083821 | -0.15041 | 121.313 | 0.010939 | 121.3222 | 121.2852 | -0.027777 | -0.036244 | 0.15572 | 121.1112 | -0.025357 | 121.3267 | 121.2602 | 0.149 | 0.045778 | -0.18453 | 121.3732 | 121.3261 | 121.518 | 121.2813 | -0.049292 | 121.3369 | 121.4081 | 121.1778 | 121.2894 | -0.25112
1534 | 121.4447 | -121.2753 | 0.13733 | 1.4211e-13 | -0.030036 | 0.014252 | -0.0040665 | -0.012333 | 0.018629 | -0.24822 | 0.018012 | 0.018889 | 0.015598 | 0.03394 | 0.0096806 | 0.065145 | 0.015142 | 0.023639 | 0.11165 | 0.055306 | 0.26559 | 0.051416 | 0.060571 | 0.03241 | -0.005985 | 0.070773 | 0.14649 | -0.11587 | -0.15041 | 121.3267 | -0.025682 | 121.3405 | 121.299 | -0.027777 | -0.082023 | 0.12826 | 121.1249 | -0.066556 | 121.3359 | 121.2693 | 0.14443 | 0.009157 | -0.2532 | 121.387 | 121.3306 | 121.5409 | 121.2905 | -0.085913 | 121.3461 | 121.4218 | 121.1595 | 121.3077 | -0.28774
1535.6875 | 121.4584 | -121.2936 | 0.11444 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0038527 | -0.01276 | 0.019057 | -0.22533 | 0.018225 | 0.018889 | 0.015812 | 0.03394 | 0.0096806 | 0.065145 | 0.015142 | 0.01906 | 0.10707 | 0.064464 | 0.25643 | 0.069732 | 0.06515 | 0.03241 | -0.001407 | 0.066194 | 0.15107 | -0.10214 | -0.15499 | 121.3634 | -0.007373 | 121.3588 | 121.3127 | -0.050672 | -0.049977 | 0.14199 | 121.1386 | -0.048247 | 121.3588 | 121.2922 | 0.15358 | 0.036624 | -0.21658 | 121.4007 | 121.3581 | 121.5501 | 121.3088 | -0.044709 | 121.3598 | 121.4447 | 121.1915 | 121.326 | -0.26943
1537.4219 | 121.5363 | -121.2845 | 0.10529 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0036391 | -0.012546 | 0.019057 | -0.2177 | 0.018225 | 0.018676 | 0.015171 | 0.03394 | 0.0098942 | 0.055988 | 0.005985 | 0.023639 | 0.10249 | 0.055306 | 0.25643 | 0.055995 | 0.055992 | 0.027831 | -0.005985 | 0.075351 | 0.1648 | -0.12961 | -0.15041 | 121.3405 | -0.002796 | 121.3405 | 121.3081 | -0.032356 | -0.04998 | 0.15115 | 121.1341 | -0.029935 | 121.3405 | 121.2785 | 0.14443 | 0.059514 | -0.23489 | 121.387 | 121.3398 | 121.5409 | 121.2905 | -0.049291 | 121.3598 | 121.4493 | 121.1549 | 121.3123 | -0.2557
1539.1719 | 121.4539 | -121.3165 | 0.13275 | 1.4211e-13 | -0.029609 | 0.013825 | -0.0034253 | -0.01276 | 0.019057 | -0.2177 | 0.018439 | 0.018462 | 0.015385 | 0.03394 | 0.0098942 | 0.055988 | 0.010564 | 0.023639 | 0.11622 | 0.055306 | 0.26101 | 0.042258 | 0.060571 | 0.018674 | -0.010564 | 0.070773 | 0.15564 | -0.12045 | -0.15041 | 121.3588 | -0.016526 | 121.3725 | 121.3402 | -0.018619 | -0.077445 | 0.12826 | 121.1661 | -0.061978 | 121.3771 | 121.306 | 0.13985 | 0.022892 | -0.2532 | 121.4328 | 121.3718 | 121.5775 | 121.3271 | -0.090493 | 121.3873 | 121.4722 | 121.1961 | 121.3352 | -0.28316
1540.9375 | 121.5729 | -121.2708 | 0.082397 | 1.4211e-13 | -0.029609 | 0.013825 | -0.0036391 | -0.012546 | 0.018843 | -0.23296 | 0.018225 | 0.018676 | 0.015812 | 0.03394 | 0.0098942 | 0.060567 | 0.019721 | 0.01906 | 0.11165 | 0.055306 | 0.25643 | 0.042258 | 0.055992 | 0.03241 | -0.005985 | 0.075351 | 0.1648 | -0.074664 | -0.15957 | 121.313 | 0.02925 | 121.3313 | 121.2898 | -0.023198 | -0.027091 | 0.17403 | 121.1112 | -0.007046 | 121.3267 | 121.2648 | 0.15358 | 0.082403 | -0.15706 | 121.3824 | 121.3261 | 121.5272 | 121.2905 | -0.040139 | 121.3461 | 121.4356 | 121.1961 | 121.3032 | -0.24197
1542.625 | 121.637 | -121.2845 | 0.10986 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0038527 | -0.01276 | 0.019057 | -0.24059 | 0.018225 | 0.018676 | 0.015598 | 0.034153 | 0.0098942 | 0.055988 | 0.010564 | 0.028217 | 0.11622 | 0.055306 | 0.26101 | 0.060574 | 0.060571 | 0.03241 | -0.010564 | 0.066194 | 0.15564 | -0.0884 | -0.15499 | 121.3451 | 0.006362 | 121.3405 | 121.3127 | -0.032357 | -0.054557 | 0.15115 | 121.1295 | -0.043669 | 121.3451 | 121.2739 | 0.14443 | 0.04578 | -0.19826 | 121.4007 | 121.3398 | 121.5455 | 121.295 | -0.049289 | 121.3507 | 121.4401 | 121.1961 | 121.3169 | -0.26485
1544.375 | 121.6324 | -121.3028 | 0.086975 | 1.4211e-13 | -0.029822 | 0.014466 | -0.0036391 | -0.01276 | 0.018843 | -0.23296 | 0.018225 | 0.018676 | 0.015598 | 0.033726 | 0.0098942 | 0.060567 | 0.010564 | 0.023639 | 0.10707 | 0.055306 | 0.26559 | 0.065153 | 0.060571 | 0.03241 | -0.010564 | 0.070773 | 0.15107 | -0.092979 | -0.15957 | 121.3679 | 0.020093 | 121.3634 | 121.3264 | -0.041514 | -0.031669 | 0.17861 | 121.1432 | -0.016202 | 121.3634 | 121.2922 | 0.14901 | 0.06409 | -0.17995 | 121.4099 | 121.3581 | 121.5684 | 121.3134 | -0.021822 | 121.3736 | 121.4539 | 121.2098 | 121.3352 | -0.24654
1546.0469 | 121.6553 | -121.3074 | 0.09613 | 1.4211e-13 | -0.030036 | 0.013825 | -0.0034253 | -0.01276 | 0.01927 | -0.23296 | 0.017798 | 0.018676 | 0.015812 | 0.034367 | 0.0098942 | 0.065145 | 0.019721 | 0.028217 | 0.11165 | 0.059885 | 0.25643 | 0.046837 | 0.060571 | 0.027831 | -0.010564 | 0.070773 | 0.15564 | -0.11587 | -0.15041 | 121.3542 | 0.015517 | 121.3725 | 121.3356 | -0.01862 | -0.036245 | 0.1603 | 121.157 | -0.025357 | 121.3679 | 121.2968 | 0.13985 | 0.059513 | -0.212 | 121.419 | 121.3673 | 121.5638 | 121.3271 | -0.049293 | 121.3781 | 121.463 | 121.1915 | 121.3352 | -0.24654
1547.7969 | 121.5271 | -121.3531 | 0.1236 | 1.4211e-13 | -0.030036 | 0.014039 | -0.0038527 | -0.01276 | 0.018843 | -0.24059 | 0.018225 | 0.018676 | 0.015812 | 0.03394 | 0.010108 | 0.055988 | 0.015142 | 0.023639 | 0.11622 | 0.059885 | 0.26101 | 0.051416 | 0.074307 | 0.041567 | -0.010564 | 0.070773 | 0.16022 | -0.097557 | -0.15499 | 121.4046 | -0.007371 | 121.4091 | 121.3768 | -0.027777 | -0.063711 | 0.13741 | 121.1982 | -0.052823 | 121.4275 | 121.3426 | 0.14443 | 0.036626 | -0.22115 | 121.4694 | 121.413 | 121.6142 | 121.3683 | -0.07218 | 121.4239 | 121.5134 | 121.2556 | 121.3947 | -0.27859
1549.5312 | 121.6278 | -121.3486 | 0.11444 | 1.4211e-13 | -0.029822 | 0.013825 | -0.0036391 | -0.012974 | 0.018843 | -0.23296 | 0.018225 | 0.018676 | 0.015598 | 0.03394 | 0.0096806 | 0.060567 | 0.015142 | 0.023639 | 0.10707 | 0.059885 | 0.25643 | 0.037679 | 0.055992 | 0.027831 | 0.007751 | 0.075351 | 0.15564 | -0.11587 | -0.15957 | 121.3863 | -0.007373 | 121.4091 | 121.3722 | -0.01404 | -0.054556 | 0.14199 | 121.189 | -0.03909 | 121.4046 | 121.3563 | 0.16732 | 0.041202 | -0.23031 | 121.4556 | 121.4085 | 121.605 | 121.3637 | -0.076762 | 121.4239 | 121.5042 | 121.2327 | 121.3764 | -0.27401
1551.2656 | 121.6141 | -121.3669 | 0.11444 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0034253 | -0.012974 | 0.019057 | -0.22533 | 0.018439 | 0.018889 | 0.016026 | 0.03394 | 0.010322 | 0.055988 | 0.015142 | 0.01906 | 0.11165 | 0.059885 | 0.26559 | 0.042258 | 0.06515 | 0.03241 | -0.010564 | 0.061616 | 0.15107 | -0.13419 | -0.15499 | 121.4091 | -0.002794 | 121.4229 | 121.3859 | -0.023198 | -0.054556 | 0.15115 | 121.2119 | -0.052825 | 121.432 | 121.3563 | 0.14443 | 0.036624 | -0.24863 | 121.4785 | 121.4268 | 121.6325 | 121.382 | -0.072183 | 121.4285 | 121.5179 | 121.2327 | 121.3993 | -0.26943
1552.9375 | 121.5408 | -121.4127 | 0.14191 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0036391 | -0.012333 | 0.019057 | -0.25585 | 0.018439 | 0.018676 | 0.015598 | 0.033726 | 0.0098942 | 0.065145 | 0.015142 | 0.023639 | 0.11165 | 0.055306 | 0.25643 | 0.060574 | 0.055992 | 0.03241 | -0.010564 | 0.070773 | 0.15107 | -0.11587 | -0.15041 | 121.4732 | -0.03026 | 121.4778 | 121.4363 | -0.036935 | -0.086601 | 0.11452 | 121.2622 | -0.071134 | 121.4687 | 121.4021 | 0.13985 | 0.009158 | -0.25778 | 121.5243 | 121.468 | 121.6691 | 121.4278 | -0.081333 | 121.4834 | 121.5637 | 121.2968 | 121.4451 | -0.29232
1554.6719 | 121.5729 | -121.3943 | 0.14191 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0034253 | -0.01276 | 0.019057 | -0.23296 | 0.018012 | 0.018676 | 0.015812 | 0.03394 | 0.010108 | 0.065145 | 0.015142 | 0.014482 | 0.11165 | 0.050727 | 0.25643 | 0.028521 | 0.06515 | 0.023253 | -0.001407 | 0.075351 | 0.15107 | -0.12961 | -0.15499 | 121.4229 | -0.03026 | 121.4595 | 121.4088 | -0.014039 | -0.09118 | 0.11452 | 121.2394 | -0.066556 | 121.4595 | 121.3929 | 0.15358 | 0.009158 | -0.27151 | 121.506 | 121.4451 | 121.6508 | 121.4095 | -0.11339 | 121.4697 | 121.5454 | 121.2647 | 121.4176 | -0.2969
1556.4219 | 121.6644 | -121.3943 | 0.09613 | 1.4211e-13 | -0.029822 | 0.013825 | -0.0038527 | -0.012974 | 0.018843 | -0.23296 | 0.018012 | 0.018676 | 0.015598 | 0.03394 | 0.0098942 | 0.060567 | 0.015142 | 0.023639 | 0.10707 | 0.055306 | 0.26101 | 0.046837 | 0.06515 | 0.027831 | -0.001407 | 0.070773 | 0.15564 | -0.060928 | -0.15041 | 121.4412 | 0.010938 | 121.4549 | 121.418 | -0.023198 | -0.040824 | 0.16488 | 121.2439 | -0.025357 | 121.4595 | 121.3929 | 0.149 | 0.059513 | -0.15706 | 121.5014 | 121.4497 | 121.6554 | 121.4095 | -0.049293 | 121.4651 | 121.55 | 121.3334 | 121.4222 | -0.24654
1558.1719 | 121.582 | -121.4355 | 0.13275 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0036391 | -0.01276 | 0.019057 | -0.22533 | 0.018012 | 0.018676 | 0.015598 | 0.03394 | 0.0098942 | 0.060567 | 0.015142 | 0.023639 | 0.10707 | 0.055306 | 0.26101 | 0.055995 | 0.069728 | 0.03241 | -0.005985 | 0.075351 | 0.15564 | -0.12503 | -0.14583 | 121.4915 | -0.025683 | 121.4961 | 121.4592 | -0.032356 | -0.077445 | 0.12826 | 121.2897 | -0.0574 | 121.5053 | 121.4296 | 0.13985 | 0.022892 | -0.25778 | 121.5426 | 121.4909 | 121.6966 | 121.4507 | -0.076756 | 121.5109 | 121.5912 | 121.3105 | 121.468 | -0.27858
1559.9062 | 121.6461 | -121.4264 | 0.12817 | 1.4211e-13 | -0.030463 | 0.014039 | -0.0040665 | -0.012974 | 0.018843 | -0.24059 | 0.018439 | 0.018462 | 0.015812 | 0.03394 | 0.0096806 | 0.060567 | 0.015142 | 0.028217 | 0.10707 | 0.055306 | 0.26101 | 0.069732 | 0.06515 | 0.027831 | -0.001407 | 0.075351 | 0.15564 | -0.097557 | -0.15041 | 121.4961 | -0.021106 | 121.487 | 121.4546 | -0.041515 | -0.072868 | 0.13284 | 121.276 | -0.052823 | 121.4915 | 121.425 | 0.149 | 0.027469 | -0.22573 | 121.5335 | 121.4817 | 121.6874 | 121.4415 | -0.058442 | 121.5017 | 121.582 | 121.3288 | 121.4542 | -0.27859
1561.5781 | 121.6965 | -121.4081 | 0.11444 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0038527 | -0.012974 | 0.018843 | -0.24059 | 0.018012 | 0.018462 | 0.015812 | 0.03394 | 0.0098942 | 0.060567 | 0.015142 | 0.028217 | 0.11622 | 0.059885 | 0.26101 | 0.051416 | 0.06515 | 0.03241 | -0.001407 | 0.075351 | 0.15107 | -0.11587 | -0.15041 | 121.4595 | 0.001784 | 121.4686 | 121.4363 | -0.023199 | -0.054556 | 0.14657 | 121.2577 | -0.03909 | 121.4732 | 121.4067 | 0.149 | 0.036624 | -0.23031 | 121.5243 | 121.468 | 121.6691 | 121.4232 | -0.063025 | 121.4834 | 121.5591 | 121.2922 | 121.4405 | -0.26485
1563.3438 | 121.6095 | -121.4493 | 0.15106 | 1.4211e-13 | -0.030036 | 0.013398 | -0.0036391 | -0.01276 | 0.018629 | -0.24059 | 0.018012 | 0.019103 | 0.015598 | 0.03394 | 0.0096806 | 0.055988 | 0.015142 | 0.023639 | 0.11622 | 0.059885 | 0.26101 | 0.046837 | 0.055992 | 0.027831 | -0.010564 | 0.066194 | 0.15564 | -0.10214 | -0.14583 | 121.4961 | -0.034837 | 121.5053 | 121.4729 | -0.023198 | -0.091177 | 0.10995 | 121.3034 | -0.084868 | 121.5053 | 121.4387 | 0.13527 | 0.004581 | -0.2532 | 121.5655 | 121.5092 | 121.7103 | 121.4644 | -0.10423 | 121.5155 | 121.6049 | 121.3471 | 121.4771 | -0.2969
1565.0312 | 121.6141 | -121.4676 | 0.12817 | 1.4211e-13 | -0.029609 | 0.014039 | -0.0036391 | -0.01276 | 0.018843 | -0.22533 | 0.018225 | 0.018249 | 0.015598 | 0.034367 | 0.0096806 | 0.060567 | 0.010564 | 0.023639 | 0.10707 | 0.059885 | 0.26101 | 0.046837 | 0.06515 | 0.023253 | -0.005985 | 0.070773 | 0.15564 | -0.13419 | -0.15041 | 121.5144 | -0.021106 | 121.5282 | 121.4912 | -0.023198 | -0.068289 | 0.13284 | 121.3172 | -0.057401 | 121.5327 | 121.4616 | 0.14443 | 0.027469 | -0.26236 | 121.5747 | 121.5275 | 121.7286 | 121.4782 | -0.081337 | 121.5384 | 121.6232 | 121.3334 | 121.4908 | -0.27859
1566.7812 | 121.7056 | -121.4447 | 0.11902 | 1.4211e-13 | -0.029822 | 0.014252 | -0.0038527 | -0.01276 | 0.018843 | -0.23296 | 0.017798 | 0.018889 | 0.015598 | 0.03394 | 0.0098942 | 0.060567 | 0.019721 | 0.01906 | 0.10707 | 0.059885 | 0.25643 | 0.042258 | 0.06515 | 0.027831 | -0.005985 | 0.075351 | 0.16022 | -0.12503 | -0.15499 | 121.487 | -0.011951 | 121.5053 | 121.4638 | -0.023198 | -0.059134 | 0.13741 | 121.2897 | -0.043668 | 121.5099 | 121.4387 | 0.14901 | 0.041203 | -0.24405 | 121.5518 | 121.5046 | 121.7011 | 121.4644 | -0.076761 | 121.5201 | 121.6049 | 121.3197 | 121.4725 | -0.27401
1568.5156 | 121.6736 | -121.4676 | 0.13275 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0036391 | -0.01276 | 0.018843 | -0.24059 | 0.017798 | 0.018676 | 0.015812 | 0.03394 | 0.010108 | 0.060567 | 0.010564 | 0.01906 | 0.10707 | 0.055306 | 0.27017 | 0.055995 | 0.06515 | 0.027831 | -0.005985 | 0.070773 | 0.15564 | -0.12503 | -0.14125 | 121.5236 | -0.025683 | 121.5282 | 121.4866 | -0.036935 | -0.077445 | 0.13742 | 121.3263 | -0.061978 | 121.5327 | 121.4616 | 0.13527 | 0.022892 | -0.25778 | 121.5747 | 121.5229 | 121.7378 | 121.4782 | -0.076756 | 121.5384 | 121.6232 | 121.3426 | 121.4954 | -0.27401
1570.25 | 121.7194 | -121.4676 | 0.10071 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0036391 | -0.012546 | 0.019057 | -0.23296 | 0.018012 | 0.018676 | 0.015385 | 0.034153 | 0.0098942 | 0.060567 | 0.010564 | 0.01906 | 0.10707 | 0.055306 | 0.26101 | 0.051416 | 0.06515 | 0.03241 | -0.010564 | 0.066194 | 0.15107 | -0.13419 | -0.15041 | 121.519 | 0.00636 | 121.5282 | 121.4866 | -0.032356 | -0.045402 | 0.1603 | 121.3172 | -0.034514 | 121.5327 | 121.457 | 0.13985 | 0.050357 | -0.23489 | 121.5747 | 121.5229 | 121.7286 | 121.4782 | -0.049292 | 121.5338 | 121.6187 | 121.3334 | 121.5 | -0.25112
1571.9375 | 121.6599 | -121.4767 | 0.11444 | 1.4211e-13 | -0.029609 | 0.014039 | -0.0042801 | -0.012546 | 0.018843 | -0.22533 | 0.018225 | 0.018889 | 0.015598 | 0.03394 | 0.0096806 | 0.060567 | 0.005985 | 0.028217 | 0.10707 | 0.064464 | 0.26101 | 0.051416 | 0.060571 | 0.023253 | -0.001407 | 0.066194 | 0.16022 | -0.11129 | -0.15957 | 121.5282 | -0.007373 | 121.5373 | 121.505 | -0.023199 | -0.049977 | 0.14657 | 121.3172 | -0.048247 | 121.5373 | 121.4753 | 0.15816 | 0.045781 | -0.22573 | 121.5838 | 121.5412 | 121.7378 | 121.4827 | -0.063025 | 121.5429 | 121.637 | 121.3655 | 121.5 | -0.27401
1573.6719 | 121.788 | -121.4813 | 0.13733 | 1.4211e-13 | -0.029609 | 0.013825 | -0.0036391 | -0.01276 | 0.018843 | -0.24822 | 0.018225 | 0.018462 | 0.015812 | 0.03394 | 0.0096806 | 0.060567 | 0.005985 | 0.023639 | 0.10707 | 0.055306 | 0.25643 | 0.065153 | 0.06515 | 0.027831 | -0.010564 | 0.057037 | 0.15564 | -0.12045 | -0.15499 | 121.5465 | -0.030261 | 121.5419 | 121.505 | -0.041514 | -0.082023 | 0.1191 | 121.3263 | -0.080292 | 121.5465 | 121.4708 | 0.14443 | 0.018314 | -0.25778 | 121.5884 | 121.5366 | 121.7378 | 121.4873 | -0.072176 | 121.5384 | 121.637 | 121.3609 | 121.5092 | -0.29232
1575.4062 | 121.7972 | -121.4447 | 0.086975 | 1.4211e-13 | -0.029822 | 0.013825 | -0.0038527 | -0.01276 | 0.018843 | -0.24059 | 0.018012 | 0.018462 | 0.015812 | 0.03394 | 0.0096806 | 0.055988 | 0.0243 | 0.028217 | 0.11165 | 0.059885 | 0.26101 | 0.046837 | 0.060571 | 0.027831 | -0.005985 | 0.075351 | 0.15107 | -0.12503 | -0.15041 | 121.4915 | 0.024672 | 121.5007 | 121.4729 | -0.01862 | -0.02709 | 0.17404 | 121.2943 | -0.011624 | 121.5053 | 121.4387 | 0.14443 | 0.06409 | -0.212 | 121.5563 | 121.5046 | 121.7057 | 121.469 | -0.040138 | 121.5201 | 121.5958 | 121.3197 | 121.4725 | -0.23739
1577.0938 | 121.7331 | -121.4996 | 0.11902 | 1.4211e-13 | -0.030036 | 0.013825 | -0.0040665 | -0.012546 | 0.018843 | -0.24059 | 0.018012 | 0.018462 | 0.015598 | 0.03394 | 0.010108 | 0.065145 | 0.015142 | 0.01906 | 0.1208 | 0.055306 | 0.26101 | 0.051416 | 0.055992 | 0.027831 | -0.001407 | 0.070773 | 0.14649 | -0.12503 | -0.15499 | 121.5511 | 0.001785 | 121.5648 | 121.5187 | -0.032356 | -0.063713 | 0.14199 | 121.3446 | -0.048246 | 121.5556 | 121.4982 | 0.15358 | 0.027467 | -0.24405 | 121.6204 | 121.5549 | 121.7606 | 121.5148 | -0.067603 | 121.5704 | 121.6461 | 121.3746 | 121.5275 | -0.27401
1578.8438 | 121.6919 | -121.5179 | 0.11444 | 1.4211e-13 | -0.029822 | 0.014252 | -0.0036391 | -0.01276 | 0.018843 | -0.23296 | 0.018653 | 0.018889 | 0.015812 | 0.03394 | 0.0096806 | 0.065145 | 0.005985 | 0.01906 | 0.11165 | 0.064464 | 0.26559 | 0.046837 | 0.060571 | 0.03241 | -0.010564 | 0.070773 | 0.15107 | -0.10214 | -0.15041 | 121.5648 | -0.002794 | 121.5831 | 121.537 | -0.027777 | -0.049977 | 0.15115 | 121.3675 | -0.043668 | 121.5785 | 121.5074 | 0.13985 | 0.036624 | -0.21658 | 121.6296 | 121.5824 | 121.7835 | 121.5239 | -0.067604 | 121.5887 | 121.669 | 121.4158 | 121.5504 | -0.26485
1580.5938 | 121.7331 | -121.5271 | 0.11902 | 1.4211e-13 | -0.03025 | 0.014039 | -0.0036391 | -0.012974 | 0.019057 | -0.23296 | 0.018012 | 0.018676 | 0.015598 | 0.034153 | 0.0098942 | 0.055988 | 0.015142 | 0.01906 | 0.10249 | 0.059885 | 0.25185 | 0.042258 | 0.06515 | 0.03241 | -0.005985 | 0.075351 | 0.16022 | -0.074664 | -0.14583 | 121.5694 | -0.016529 | 121.5831 | 121.5462 | -0.023198 | -0.059134 | 0.13283 | 121.3813 | -0.043668 | 121.5923 | 121.5211 | 0.13985 | 0.041203 | -0.19368 | 121.6296 | 121.587 | 121.779 | 121.5422 | -0.076761 | 121.6025 | 121.6873 | 121.4524 | 121.5595 | -0.26485
1582.3438 | 121.7926 | -121.5134 | 0.11444 | 1.4211e-13 | -0.029609 | 0.014039 | -0.0038527 | -0.01276 | 0.018629 | -0.23296 | 0.018439 | 0.018676 | 0.015812 | 0.034367 | 0.0098942 | 0.055988 | 0.015142 | 0.023639 | 0.11165 | 0.059885 | 0.26101 | 0.042258 | 0.060571 | 0.027831 | -0.010564 | 0.075351 | 0.15107 | -0.12503 | -0.15499 | 121.5556 | -0.002794 | 121.5694 | 121.537 | -0.018619 | -0.054556 | 0.14657 | 121.3584 | -0.03909 | 121.5739 | 121.5028 | 0.14443 | 0.036624 | -0.23947 | 121.625 | 121.5733 | 121.7744 | 121.5285 | -0.072183 | 121.5887 | 121.6644 | 121.3883 | 121.5412 | -0.26943
1584.0938 | 121.7834 | -121.4996 | 0.10529 | 1.4211e-13 | -0.03025 | 0.014252 | -0.0036391 | -0.012974 | 0.019057 | -0.22533 | 0.018225 | 0.018676 | 0.015812 | 0.03394 | 0.0096806 | 0.069723 | 0.005985 | 0.023639 | 0.11165 | 0.059885 | 0.26101 | 0.037679 | 0.055992 | 0.03241 | -0.010564 | 0.075351 | 0.14649 | -0.12045 | -0.15499 | 121.5373 | 0.006361 | 121.5694 | 121.5233 | -0.01404 | -0.045401 | 0.15572 | 121.3446 | -0.029935 | 121.5556 | 121.4891 | 0.14443 | 0.0412 | -0.22574 | 121.6113 | 121.5595 | 121.7606 | 121.5056 | -0.067607 | 121.575 | 121.6461 | 121.3792 | 121.532 | -0.26028
1585.8594 | 121.7239 | -121.5546 | 0.13275 | 1.4211e-13 | -0.030036 | 0.013611 | -0.0034253 | -0.012974 | 0.019057 | -0.23296 | 0.018012 | 0.018889 | 0.015385 | 0.03394 | 0.009467 | 0.065145 | 0.015142 | 0.01906 | 0.10707 | 0.069043 | 0.26559 | 0.051416 | 0.069728 | 0.03241 | -0.001407 | 0.070773 | 0.15107 | -0.13419 | -0.15041 | 121.606 | -0.025683 | 121.6197 | 121.5736 | -0.032356 | -0.063708 | 0.13284 | 121.4042 | -0.061978 | 121.6243 | 121.5532 | 0.149 | 0.018314 | -0.26694 | 121.6616 | 121.6236 | 121.8202 | 121.5697 | -0.081335 | 121.6253 | 121.7056 | 121.4204 | 121.587 | -0.28316
1587.5469 | 121.7514 | -121.5363 | 0.11444 | 1.4211e-13 | -0.029822 | 0.014466 | -0.0036391 | -0.01276 | 0.018629 | -0.23296 | 0.018012 | 0.018462 | 0.015598 | 0.03394 | 0.009467 | 0.069723 | 0.010564 | 0.023639 | 0.11622 | 0.055306 | 0.26101 | 0.042258 | 0.055992 | 0.027831 | -0.005985 | 0.061616 | 0.15564 | -0.12961 | -0.15499 | 121.5785 | 0.001784 | 121.606 | 121.5599 | -0.018619 | -0.059135 | 0.14657 | 121.3813 | -0.052825 | 121.5922 | 121.5303 | 0.14901 | 0.041202 | -0.24405 | 121.6525 | 121.5916 | 121.7973 | 121.5468 | -0.072183 | 121.5979 | 121.6919 | 121.4066 | 121.5641 | -0.26943
1589.2969 | 121.8155 | -121.5271 | 0.10529 | 1.4211e-13 | -0.029822 | 0.013825 | -0.0036391 | -0.012974 | 0.018843 | -0.23296 | 0.018012 | 0.018462 | 0.015812 | 0.034367 | 0.0096806 | 0.065145 | 0.015142 | 0.014482 | 0.11165 | 0.059885 | 0.26101 | 0.037679 | 0.060571 | 0.027831 | -0.010564 | 0.066194 | 0.14649 | -0.12961 | -0.15041 | 121.5648 | 0.006361 | 121.5922 | 121.5416 | -0.023197 | -0.045401 | 0.15572 | 121.3767 | -0.039092 | 121.5877 | 121.5165 | 0.13985 | 0.0412 | -0.23489 | 121.6387 | 121.587 | 121.7881 | 121.5422 | -0.067607 | 121.5933 | 121.6736 | 121.3975 | 121.5549 | -0.2557
1591.0469 | 121.8246 | -121.5363 | 0.13275 | 1.4211e-13 | -0.029395 | 0.014039 | -0.0038527 | -0.013187 | 0.01927 | -0.23296 | 0.018012 | 0.018676 | 0.015812 | 0.03394 | 0.009467 | 0.065145 | 0.010564 | 0.028217 | 0.11622 | 0.059885 | 0.26559 | 0.042258 | 0.060571 | 0.036989 | -0.005985 | 0.075351 | 0.15564 | -0.10214 | -0.15957 | 121.5785 | -0.016526 | 121.6014 | 121.5645 | -0.014041 | -0.072866 | 0.13284 | 121.3767 | -0.0574 | 121.5968 | 121.5303 | 0.15358 | 0.022892 | -0.23489 | 121.6525 | 121.5961 | 121.8018 | 121.5468 | -0.090493 | 121.6116 | 121.6919 | 121.4341 | 121.5732 | -0.29232
1592.7344 | 121.7148 | -121.5683 | 0.13733 | 1.4211e-13 | -0.03025 | 0.013825 | -0.0038527 | -0.012546 | 0.018843 | -0.23296 | 0.018012 | 0.018676 | 0.015598 | 0.03394 | 0.0098942 | 0.065145 | 0.005985 | 0.023639 | 0.11165 | 0.064464 | 0.27017 | -0.09511 | 0.06515 | 0.023253 | -0.015143 | 0.070773 | 0.1648 | -0.10214 | -0.15041 | 121.4732 | -0.025682 | 121.6334 | 121.5919 | 0.11875 | -0.072865 | 0.13284 | 121.4179 | -0.066556 | 121.6334 | 121.5532 | 0.13527 | 0.027471 | -0.23947 | 121.6799 | 121.6328 | 121.8385 | 121.5743 | -0.23244 | 121.6391 | 121.7331 | 121.4662 | 121.5916 | -0.28774
1594.4688 | 121.8521 | -121.5317 | 0.10529 | 1.4211e-13 | -0.029609 | 0.014039 | -0.0036391 | -0.01276 | 0.019057 | -0.23296 | 0.018225 | 0.018462 | 0.015812 | 0.034153 | 0.0098942 | 0.060567 | 0.005985 | 0.01906 | 0.11622 | 0.050727 | 0.26101 | 0.042258 | 0.055992 | 0.036989 | -0.005985 | 0.070773 | 0.16022 | -0.12503 | -0.15957 | 121.5739 | 0.010939 | 121.5922 | 121.5507 | -0.023198 | -0.054559 | 0.15572 | 121.3721 | -0.034513 | 121.5877 | 121.5257 | 0.15358 | 0.054936 | -0.23031 | 121.6479 | 121.5824 | 121.7927 | 121.5377 | -0.063028 | 121.6025 | 121.6919 | 121.4066 | 121.5687 | -0.26486
1596.2344 | 121.843 | -121.5317 | 0.10071 | 1.4211e-13 | -0.029609 | 0.013825 | -0.0034253 | -0.012974 | 0.018629 | -0.24059 | 0.018012 | 0.018889 | 0.015598 | 0.03394 | 0.0098942 | 0.060567 | 0.019721 | 0.023639 | 0.11165 | 0.055306 | 0.26101 | 0.037679 | 0.06515 | 0.023253 | -0.010564 | 0.070773 | 0.15564 | -0.10671 | -0.15499 | 121.5694 | 0.010939 | 121.5922 | 121.5553 | -0.01404 | -0.045402 | 0.1603 | 121.3767 | -0.029935 | 121.5968 | 121.5211 | 0.14443 | 0.054935 | -0.20742 | 121.6433 | 121.587 | 121.7927 | 121.5514 | -0.063029 | 121.6025 | 121.6873 | 121.425 | 121.5549 | -0.2557
1597.9375 | 121.8338 | -121.5775 | 0.13275 | 1.4211e-13 | -0.030036 | 0.014039 | -0.0042801 | -0.01276 | 0.018843 | -0.23296 | 0.018225 | 0.018676 | 0.015598 | 0.034153 | 0.0098942 | 0.065145 | 0.010564 | 0.028217 | 0.1208 | 0.059885 | 0.26559 | 0.042258 | 0.060571 | 0.03241 | -0.005985 | 0.07993 | 0.16022 | -0.12503 | -0.15041 | 121.6197 | -0.011947 | 121.6426 | 121.6057 | -0.014041 | -0.072866 | 0.13284 | 121.427 | -0.052821 | 121.638 | 121.5715 | 0.14443 | 0.027471 | -0.25778 | 121.6983 | 121.6373 | 121.843 | 121.588 | -0.090493 | 121.6574 | 121.7377 | 121.4524 | 121.6099 | -0.28316
1599.6875 | 121.7651 | -121.6278 | 0.12817 | 1.4211e-13 | -0.030036 | 0.014252 | -0.0040665 | -0.012974 | 0.018843 | -0.24059 | 0.018012 | 0.018676 | 0.015385 | 0.034367 | 0.010108 | 0.065145 | 0.019721 | 0.01906 | 0.10707 | 0.059885 | 0.26101 | 0.037679 | 0.06515 | 0.041567 | -0.005985 | 0.075351 | 0.15564 | -0.12503 | -0.15041 | 121.6655 | -0.021106 | 121.693 | 121.6469 | -0.018619 | -0.068289 | 0.13284 | 121.4774 | -0.052823 | 121.693 | 121.6218 | 0.14443 | 0.027469 | -0.2532 | 121.7349 | 121.6877 | 121.8888 | 121.6475 | -0.090495 | 121.7032 | 121.7835 | 121.5028 | 121.6694 | -0.27859
1601.375 | 121.8887 | -121.5729 | 0.10071 | 1.4211e-13 | -0.029609 | 0.014039 | -0.0038527 | -0.013187 | 0.018843 | -0.2177 | 0.017798 | 0.018676 | 0.015598 | 0.034153 | 0.0096806 | 0.060567 | 0.015142 | 0.014482 | 0.11165 | 0.064464 | 0.25643 | 0.0331 | 0.060571 | 0.03241 | -0.005985 | 0.075351 | 0.15564 | -0.079243 | -0.15041 | 121.606 | 0.010939 | 121.6334 | 121.5874 | -0.018618 | -0.036244 | 0.15572 | 121.4225 | -0.025357 | 121.6334 | 121.5669 | 0.14443 | 0.054935 | -0.17995 | 121.6845 | 121.6373 | 121.8293 | 121.588 | -0.067608 | 121.6482 | 121.7285 | 121.4936 | 121.6053 | -0.25112
1603.1094 | 121.9116 | -121.5775 | 0.10071 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0034253 | -0.012974 | 0.018629 | -0.24059 | 0.018012 | 0.018249 | 0.015385 | 0.03394 | 0.009467 | 0.065145 | 0.015142 | 0.032795 | 0.11165 | 0.059885 | 0.26101 | 0.051416 | 0.055992 | 0.027831 | -0.005985 | 0.075351 | 0.16022 | -0.10671 | -0.15041 | 121.6289 | 0.010939 | 121.6426 | 121.6102 | -0.018621 | -0.040823 | 0.1603 | 121.427 | -0.025357 | 121.6334 | 121.5715 | 0.14443 | 0.059514 | -0.20742 | 121.6891 | 121.6373 | 121.8385 | 121.5926 | -0.049292 | 121.6528 | 121.7377 | 121.4707 | 121.6053 | -0.25112
1604.8594 | 121.8475 | -121.6141 | 0.11444 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0034253 | -0.01276 | 0.018629 | -0.23296 | 0.018012 | 0.019103 | 0.015598 | 0.03394 | 0.0090396 | 0.060567 | 0.019721 | 0.023639 | 0.11165 | 0.050727 | 0.26101 | 0.028521 | 0.055992 | 0.036989 | -0.005985 | 0.070773 | 0.16022 | -0.097557 | -0.15499 | 121.6426 | -0.002794 | 121.6746 | 121.6377 | -0.004882 | -0.063714 | 0.14657 | 121.4591 | -0.043668 | 121.6701 | 121.6081 | 0.14901 | 0.045781 | -0.212 | 121.7257 | 121.6648 | 121.8751 | 121.6338 | -0.08592 | 121.6848 | 121.7743 | 121.5165 | 121.6511 | -0.26943
1606.6094 | 121.8292 | -121.5958 | 0.12817 | 1.4211e-13 | -0.029609 | 0.013611 | -0.0036391 | -0.013401 | 0.019057 | -0.24059 | 0.018225 | 0.018676 | 0.015598 | 0.034153 | 0.0098942 | 0.065145 | 0.015142 | 0.023639 | 0.11622 | 0.059885 | 0.26559 | 0.037679 | 0.069728 | 0.03241 | 0.003172 | 0.070773 | 0.15107 | -0.11587 | -0.15957 | 121.6334 | -0.011949 | 121.6609 | 121.6194 | -0.01404 | -0.068289 | 0.13741 | 121.4362 | -0.057401 | 121.6655 | 121.5989 | 0.16274 | 0.022891 | -0.24405 | 121.712 | 121.6556 | 121.8614 | 121.6109 | -0.090495 | 121.6665 | 121.7468 | 121.4799 | 121.6282 | -0.28774
1608.3125 | 121.843 | -121.6278 | 0.1236 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0036391 | -0.013187 | 0.019057 | -0.24059 | 0.017798 | 0.018889 | 0.015598 | 0.034581 | 0.009467 | 0.065145 | 0.010564 | 0.009904 | 0.11622 | 0.064464 | 0.25185 | 0.028521 | 0.06515 | 0.03241 | -0.001407 | 0.070773 | 0.15107 | -0.10214 | -0.15499 | 121.6563 | -0.007371 | 121.693 | 121.6377 | -0.018617 | -0.059132 | 0.12826 | 121.4728 | -0.052823 | 121.693 | 121.6264 | 0.15358 | 0.027469 | -0.22573 | 121.744 | 121.6923 | 121.8797 | 121.6384 | -0.095075 | 121.6986 | 121.7789 | 121.5257 | 121.6602 | -0.27859
1610.0469 | 121.8109 | -121.6599 | 0.13733 | 1.4211e-13 | -0.029822 | 0.013611 | -0.0038527 | -0.013187 | 0.019057 | -0.24822 | 0.018225 | 0.018249 | 0.015812 | 0.034153 | 0.0098942 | 0.060567 | 0.010564 | 0.01906 | 0.11165 | 0.059885 | 0.25643 | 0.046837 | 0.06515 | 0.03241 | -0.005985 | 0.070773 | 0.14649 | -0.11129 | -0.15499 | 121.7067 | -0.025682 | 121.7204 | 121.6789 | -0.027777 | -0.077444 | 0.1191 | 121.5049 | -0.066556 | 121.725 | 121.6539 | 0.14901 | 0.009157 | -0.24862 | 121.7715 | 121.7197 | 121.9163 | 121.6704 | -0.090492 | 121.7306 | 121.8063 | 121.5486 | 121.6923 | -0.29232
1611.7344 | 121.9025 | -121.6278 | 0.07782 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0036391 | -0.012974 | 0.019057 | -0.24059 | 0.018225 | 0.018249 | 0.015598 | 0.034367 | 0.0096806 | 0.060567 | 0.005985 | 0.01906 | 0.11165 | 0.050727 | 0.26559 | 0.0331 | 0.060571 | 0.03241 | -0.010564 | 0.070773 | 0.15107 | -0.11587 | -0.15041 | 121.6609 | 0.033827 | 121.6884 | 121.6469 | -0.01404 | -0.027093 | 0.18777 | 121.4774 | -0.007047 | 121.6884 | 121.6172 | 0.13985 | 0.073245 | -0.19369 | 121.7395 | 121.6785 | 121.8934 | 121.6338 | -0.04472 | 121.6986 | 121.7789 | 121.5119 | 121.6602 | -0.22823
1613.4844 | 121.9482 | -121.582 | 0.10529 | 1.4211e-13 | -0.030463 | 0.013825 | -0.0036391 | -0.01276 | 0.018843 | -0.23296 | 0.018225 | 0.018676 | 0.015598 | 0.03394 | 0.009467 | 0.065145 | 0.015142 | 0.01906 | 0.11165 | 0.064464 | 0.26101 | 0.037679 | 0.06515 | 0.03241 | -0.005985 | 0.07993 | 0.15564 | -0.028878 | -0.15041 | 121.6197 | 0.006361 | 121.6472 | 121.6011 | -0.018619 | -0.040822 | 0.15572 | 121.4316 | -0.025356 | 121.6472 | 121.576 | 0.14443 | 0.050357 | -0.13416 | 121.6937 | 121.6465 | 121.843 | 121.5972 | -0.067607 | 121.662 | 121.7377 | 121.5532 | 121.6144 | -0.2557
1615.1719 | 121.9437 | -121.6187 | 0.10986 | 1.4211e-13 | -0.030036 | 0.014252 | -0.0034253 | -0.013187 | 0.018629 | -0.24822 | 0.018012 | 0.018889 | 0.015385 | 0.034153 | 0.0096806 | 0.055988 | 0.010564 | 0.01906 | 0.11165 | 0.064464 | 0.26101 | 0.0331 | 0.06515 | 0.027831 | -0.001407 | 0.075351 | 0.16022 | -0.092979 | -0.16415 | 121.6518 | 0.001784 | 121.6746 | 121.6377 | -0.01404 | -0.045399 | 0.15115 | 121.4545 | -0.034512 | 121.6838 | 121.6172 | 0.16274 | 0.050359 | -0.20284 | 121.7303 | 121.6831 | 121.8797 | 121.6292 | -0.076763 | 121.694 | 121.7789 | 121.5257 | 121.6465 | -0.27401
1616.9219 | 121.9574 | -121.6049 | 0.082397 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0036391 | -0.012974 | 0.018843 | -0.23296 | 0.017798 | 0.018889 | 0.015812 | 0.034367 | 0.0098942 | 0.060567 | 0.015142 | 0.01906 | 0.10249 | 0.055306 | 0.26559 | 0.042258 | 0.060571 | 0.027831 | -0.010564 | 0.070773 | 0.15564 | -0.13419 | -0.15957 | 121.6472 | 0.020093 | 121.6655 | 121.624 | -0.023198 | -0.027091 | 0.18319 | 121.4453 | -0.011624 | 121.6655 | 121.5944 | 0.14901 | 0.073246 | -0.21658 | 121.7074 | 121.6602 | 121.8705 | 121.6201 | -0.040139 | 121.6757 | 121.7606 | 121.4707 | 121.6328 | -0.24197
1618.6562 | 121.9666 | -121.6324 | 0.082397 | 1.4211e-13 | -0.030036 | 0.013825 | -0.0038527 | -0.013187 | 0.019057 | -0.23296 | 0.017798 | 0.018462 | 0.015812 | 0.03394 | 0.009467 | 0.055988 | 0.010564 | 0.014482 | 0.11165 | 0.059885 | 0.26559 | 0.0331 | 0.060571 | 0.027831 | -0.010564 | 0.07993 | 0.14649 | -0.11587 | -0.15041 | 121.6655 | 0.02925 | 121.6884 | 121.6469 | -0.018618 | -0.022512 | 0.18319 | 121.482 | -0.002467 | 121.693 | 121.6218 | 0.13985 | 0.064089 | -0.19827 | 121.744 | 121.6923 | 121.898 | 121.6429 | -0.049297 | 121.7123 | 121.7789 | 121.5165 | 121.6602 | -0.23281
1620.3281 | 121.9437 | -121.669 | 0.10071 | 1.4211e-13 | -0.029822 | 0.013825 | -0.0038527 | -0.01276 | 0.018843 | -0.24059 | 0.018012 | 0.018889 | 0.015812 | 0.034153 | 0.0096806 | 0.065145 | 0.0243 | 0.023639 | 0.11165 | 0.059885 | 0.26101 | 0.055995 | 0.06515 | 0.036989 | -0.010564 | 0.070773 | 0.16022 | -0.10214 | -0.15041 | 121.725 | 0.010939 | 121.7342 | 121.6926 | -0.032356 | -0.040823 | 0.1603 | 121.5186 | -0.029935 | 121.7342 | 121.6584 | 0.13985 | 0.059514 | -0.20284 | 121.7807 | 121.7289 | 121.93 | 121.6933 | -0.044713 | 121.7398 | 121.8292 | 121.5669 | 121.706 | -0.25112
1622.0781 | 121.9757 | -121.6415 | 0.068665 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0038527 | -0.012974 | 0.019057 | -0.24059 | 0.018012 | 0.018889 | 0.016026 | 0.034153 | 0.0098942 | 0.055988 | 0.010564 | 0.01906 | 0.10707 | 0.059885 | 0.26101 | 0.046837 | 0.060571 | 0.027831 | -0.005985 | 0.075351 | 0.15107 | -0.10671 | -0.15499 | 121.6884 | 0.038403 | 121.6975 | 121.6606 | -0.027777 | -0.00878 | 0.19235 | 121.4866 | 0.006686 | 121.7021 | 121.6356 | 0.14901 | 0.0824 | -0.17538 | 121.7486 | 121.7014 | 121.9026 | 121.6521 | -0.021828 | 121.7169 | 121.7926 | 121.5348 | 121.6694 | -0.22366
1623.7656 | 121.9711 | -121.6232 | 0.082397 | 1.4211e-13 | -0.029822 | 0.013825 | -0.0034253 | -0.012546 | 0.018629 | -0.23296 | 0.018012 | 0.018889 | 0.015812 | 0.03394 | 0.0096806 | 0.060567 | 0.005985 | 0.01906 | 0.10707 | 0.059885 | 0.26101 | 0.042258 | 0.06515 | 0.027831 | -0.010564 | 0.070773 | 0.16022 | -0.097557 | -0.15957 | 121.6655 | 0.024671 | 121.6838 | 121.6423 | -0.023198 | -0.022512 | 0.17861 | 121.4637 | -0.011624 | 121.6884 | 121.6127 | 0.14901 | 0.077825 | -0.17995 | 121.7303 | 121.6831 | 121.8842 | 121.6292 | -0.040139 | 121.694 | 121.7835 | 121.5257 | 121.6511 | -0.24197
1625.5156 | 121.9162 | -121.6827 | 0.11444 | 1.4211e-13 | -0.030036 | 0.013825 | -0.0038527 | -0.013187 | 0.018843 | -0.23296 | 0.018012 | 0.018676 | 0.016026 | 0.03394 | 0.0096806 | 0.065145 | 0.005985 | 0.01906 | 0.10249 | 0.055306 | 0.26559 | 0.046837 | 0.055992 | 0.036989 | -0.010564 | 0.075351 | 0.15107 | -0.092979 | -0.15957 | 121.7296 | -0.011951 | 121.7479 | 121.7018 | -0.027777 | -0.059135 | 0.15115 | 121.5232 | -0.03909 | 121.7387 | 121.6722 | 0.14901 | 0.036624 | -0.20742 | 121.7852 | 121.738 | 121.9483 | 121.6887 | -0.067604 | 121.7581 | 121.8338 | 121.5898 | 121.7197 | -0.27401
1627.25 | 121.875 | -121.7102 | 0.11444 | 1.4211e-13 | -0.03025 | 0.013825 | -0.0036391 | -0.012974 | 0.018843 | -0.23296 | 0.018012 | 0.018889 | 0.015598 | 0.034153 | 0.010108 | 0.069723 | 0.010564 | 0.023639 | 0.1208 | 0.059885 | 0.26559 | 0.051416 | 0.060571 | 0.03241 | -0.010564 | 0.075351 | 0.15107 | -0.11587 | -0.15041 | 121.7616 | 0.006363 | 121.7799 | 121.7338 | -0.027777 | -0.054556 | 0.15115 | 121.5598 | -0.03909 | 121.7708 | 121.6996 | 0.13985 | 0.036624 | -0.23031 | 121.831 | 121.7701 | 121.9758 | 121.7208 | -0.063025 | 121.7856 | 121.8613 | 121.5943 | 121.7426 | -0.26485
1629 | 121.994 | -121.6507 | 0.086975 | 1.4211e-13 | -0.030036 | 0.014039 | -0.0040665 | -0.012974 | 0.018629 | -0.24059 | 0.018012 | 0.018676 | 0.015385 | 0.033726 | 0.0096806 | 0.065145 | 0.010564 | 0.028217 | 0.11622 | 0.059885 | 0.26559 | 0.037679 | 0.060571 | 0.023253 | -0.005985 | 0.075351 | 0.15564 | -0.033457 | -0.15499 | 121.6884 | 0.02925 | 121.7158 | 121.6789 | -0.009462 | -0.02709 | 0.17861 | 121.4957 | -0.011624 | 121.7113 | 121.6447 | 0.14901 | 0.068668 | -0.12043 | 121.7669 | 121.7106 | 121.9163 | 121.6613 | -0.049296 | 121.726 | 121.8063 | 121.6172 | 121.6739 | -0.24197
1630.75 | 122.0078 | -121.6644 | 0.10529 | 1.4211e-13 | -0.03025 | 0.013825 | -0.0034253 | -0.012974 | 0.018843 | -0.24059 | 0.018225 | 0.018676 | 0.015385 | 0.034367 | 0.009467 | 0.065145 | 0.015142 | 0.01906 | 0.11165 | 0.055306 | 0.25643 | 0.028521 | 0.060571 | 0.027831 | -0.010564 | 0.075351 | 0.15564 | -0.092979 | -0.15957 | 121.6929 | 0.006361 | 121.7296 | 121.6835 | -0.009461 | -0.04998 | 0.15115 | 121.5049 | -0.029935 | 121.725 | 121.6539 | 0.14901 | 0.050357 | -0.19827 | 121.7761 | 121.7197 | 121.9209 | 121.6796 | -0.076765 | 121.7398 | 121.8201 | 121.5714 | 121.6923 | -0.26486
1632.4375 | 122.0123 | -121.6736 | 0.10071 | 1.4211e-13 | -0.030036 | 0.013611 | -0.0032117 | -0.012974 | 0.018629 | -0.23296 | 0.018225 | 0.019103 | 0.015812 | 0.033726 | 0.009467 | 0.055988 | 0.010564 | 0.023639 | 0.11622 | 0.055306 | 0.26101 | 0.0331 | 0.06515 | 0.036989 | -0.010564 | 0.075351 | 0.14649 | -0.038035 | -0.15957 | 121.7067 | 0.015517 | 121.7296 | 121.6972 | -0.009461 | -0.045402 | 0.1603 | 121.514 | -0.025357 | 121.7387 | 121.663 | 0.14901 | 0.045778 | -0.13874 | 121.7898 | 121.7289 | 121.9346 | 121.6841 | -0.067608 | 121.7489 | 121.8201 | 121.6355 | 121.7106 | -0.26028
1634.1875 | 121.9025 | -121.7285 | 0.10986 | 1.4211e-13 | -0.03025 | 0.014252 | -0.0038527 | -0.012974 | 0.019057 | -0.24059 | 0.018012 | 0.018889 | 0.015598 | 0.034153 | 0.009467 | 0.060567 | 0.015142 | 0.014482 | 0.11165 | 0.055306 | 0.25643 | 0.028521 | 0.055992 | 0.027831 | -0.010564 | 0.075351 | 0.16022 | -0.079243 | -0.15499 | 121.757 | 0.001784 | 121.7891 | 121.743 | -0.014039 | -0.054557 | 0.14657 | 121.5735 | -0.034512 | 121.7845 | 121.718 | 0.14443 | 0.050359 | -0.18911 | 121.8402 | 121.7838 | 121.9849 | 121.7437 | -0.081342 | 121.8039 | 121.8887 | 121.6493 | 121.7563 | -0.26485
1635.875 | 121.8933 | -121.7377 | 0.13733 | 1.4211e-13 | -0.03025 | 0.014039 | -0.0034253 | -0.012974 | 0.018629 | -0.23296 | 0.018012 | 0.018462 | 0.015598 | 0.034367 | 0.0092534 | 0.060567 | 0.015142 | 0.009904 | 0.1208 | 0.059885 | 0.26101 | 0.042258 | 0.06515 | 0.03241 | -0.005985 | 0.070773 | 0.1648 | -0.10214 | -0.15499 | 121.7799 | -0.016525 | 121.7982 | 121.7476 | -0.032354 | -0.077444 | 0.12368 | 121.5827 | -0.066556 | 121.8028 | 121.7317 | 0.14901 | 0.027471 | -0.23947 | 121.8585 | 121.7976 | 121.9987 | 121.7528 | -0.095071 | 121.8084 | 121.9025 | 121.6355 | 121.7701 | -0.29232
1637.625 | 121.9345 | -121.7285 | 0.1236 | 1.4211e-13 | -0.030036 | 0.013825 | -0.0036391 | -0.01276 | 0.018843 | -0.23296 | 0.018225 | 0.018462 | 0.015812 | 0.034367 | 0.009467 | 0.055988 | 0.015142 | 0.014482 | 0.11165 | 0.069043 | 0.26101 | 0.046837 | 0.06515 | 0.03241 | -0.005985 | 0.07993 | 0.15564 | -0.13419 | -0.15499 | 121.7754 | -0.011949 | 121.7845 | 121.743 | -0.032355 | -0.054553 | 0.13741 | 121.5735 | -0.043666 | 121.7937 | 121.7225 | 0.14901 | 0.032047 | -0.25778 | 121.8402 | 121.7976 | 121.9895 | 121.7437 | -0.076759 | 121.8084 | 121.8842 | 121.5943 | 121.7609 | -0.27859
1639.375 | 122.0215 | -121.6873 | 0.09613 | 1.4211e-13 | -0.029822 | 0.014252 | -0.0038527 | -0.012974 | 0.019057 | -0.23296 | 0.018225 | 0.018889 | 0.015598 | 0.033726 | 0.0096806 | 0.069723 | 0.010564 | 0.01906 | 0.10707 | 0.059885 | 0.26101 | 0.042258 | 0.060571 | 0.036989 | -0.001407 | 0.070773 | 0.16022 | -0.10214 | -0.15499 | 121.7296 | 0.010938 | 121.757 | 121.7064 | -0.023198 | -0.036245 | 0.16488 | 121.5323 | -0.025357 | 121.7479 | 121.6859 | 0.15358 | 0.064092 | -0.19827 | 121.7944 | 121.7472 | 121.9483 | 121.6979 | -0.053872 | 121.7581 | 121.8475 | 121.5852 | 121.7243 | -0.25112
1641.0469 | 122.0352 | -121.6965 | 0.086975 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0036391 | -0.01276 | 0.018843 | -0.23296 | 0.018653 | 0.018462 | 0.016026 | 0.034581 | 0.009467 | 0.060567 | 0.015142 | 0.014482 | 0.11165 | 0.055306 | 0.26559 | 0.0331 | 0.060571 | 0.027831 | -0.010564 | 0.075351 | 0.15107 | -0.10214 | -0.15499 | 121.7296 | 0.024672 | 121.757 | 121.711 | -0.018618 | -0.031669 | 0.17861 | 121.5415 | -0.011624 | 121.757 | 121.6859 | 0.14443 | 0.06409 | -0.18911 | 121.8081 | 121.7518 | 121.9621 | 121.7116 | -0.053875 | 121.7718 | 121.8475 | 121.5943 | 121.7243 | -0.24197
1642.7969 | 121.9574 | -121.7285 | 0.13275 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0040665 | -0.012974 | 0.018629 | -0.24822 | 0.018225 | 0.018889 | 0.015385 | 0.03394 | 0.0092534 | 0.060567 | 0.015142 | 0.009904 | 0.11165 | 0.059885 | 0.26101 | 0.051416 | 0.060571 | 0.03241 | 0.003172 | 0.070773 | 0.1648 | -0.10671 | -0.15041 | 121.7799 | -0.021104 | 121.7891 | 121.7384 | -0.041512 | -0.072866 | 0.12826 | 121.5781 | -0.061978 | 121.7891 | 121.7317 | 0.15358 | 0.032049 | -0.23947 | 121.8402 | 121.7884 | 121.9895 | 121.7437 | -0.081335 | 121.7993 | 121.8933 | 121.6218 | 121.7609 | -0.28316
1644.5312 | 121.9254 | -121.7194 | 0.14191 | 1.4211e-13 | -0.030036 | 0.014039 | -0.0038527 | -0.012974 | 0.019057 | -0.23296 | 0.018225 | 0.018676 | 0.015812 | 0.034153 | 0.0096806 | 0.055988 | 0.010564 | 0.023639 | 0.11622 | 0.059885 | 0.26101 | 0.051416 | 0.069728 | 0.036989 | -0.010564 | 0.075351 | 0.16938 | -0.12503 | -0.15499 | 121.7708 | -0.025682 | 121.7753 | 121.743 | -0.027777 | -0.082022 | 0.1191 | 121.5644 | -0.066556 | 121.7891 | 121.7088 | 0.14443 | 0.027472 | -0.26694 | 121.8356 | 121.7792 | 121.9804 | 121.7299 | -0.090491 | 121.7947 | 121.8887 | 121.5943 | 121.7563 | -0.2969
1646.2031 | 122.049 | -121.7148 | 0.10529 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0038527 | -0.012974 | 0.01927 | -0.24059 | 0.017798 | 0.018676 | 0.015385 | 0.034367 | 0.0096806 | 0.05141 | 0.010564 | 0.014482 | 0.11165 | 0.055306 | 0.25643 | 0.042258 | 0.055992 | 0.036989 | -0.010564 | 0.070773 | 0.14649 | -0.097557 | -0.15041 | 121.757 | 0.006361 | 121.7662 | 121.7293 | -0.027776 | -0.04998 | 0.15115 | 121.5644 | -0.034513 | 121.7708 | 121.7042 | 0.13985 | 0.0412 | -0.20284 | 121.8264 | 121.7701 | 121.9712 | 121.7253 | -0.063028 | 121.7856 | 121.8613 | 121.6172 | 121.7518 | -0.2557
1647.9531 | 121.962 | -121.7468 | 0.1236 | 1.4211e-13 | -0.030036 | 0.014039 | -0.0038527 | -0.012974 | 0.018629 | -0.22533 | 0.018439 | 0.018889 | 0.015385 | 0.03394 | 0.009467 | 0.060567 | 0.015142 | 0.023639 | 0.11165 | 0.059885 | 0.25643 | 0.0331 | 0.060571 | 0.027831 | -0.005985 | 0.070773 | 0.15564 | -0.074664 | -0.15499 | 121.7799 | -0.011949 | 121.8074 | 121.7705 | -0.009461 | -0.063711 | 0.13284 | 121.5918 | -0.052823 | 121.8074 | 121.7408 | 0.14901 | 0.032047 | -0.19826 | 121.8585 | 121.8067 | 122.0033 | 121.762 | -0.090496 | 121.8176 | 121.9025 | 121.6722 | 121.7747 | -0.27859
1649.6875 | 121.9666 | -121.7743 | 0.11902 | 1.4211e-13 | -0.03025 | 0.014039 | -0.0036391 | -0.012974 | 0.018843 | -0.22533 | 0.018012 | 0.018676 | 0.015812 | 0.034153 | 0.0096806 | 0.065145 | 0.015142 | 0.01906 | 0.11165 | 0.055306 | 0.26559 | 0.083468 | 0.060571 | 0.036989 | -0.010564 | 0.066194 | 0.15107 | -0.13876 | -0.15041 | 121.8578 | -0.007372 | 121.8394 | 121.7934 | -0.064408 | -0.063713 | 0.14657 | 121.6239 | -0.052825 | 121.8349 | 121.7637 | 0.13985 | 0.032046 | -0.25778 | 121.8859 | 121.8296 | 122.0399 | 121.7894 | -0.035551 | 121.8405 | 121.9254 | 121.6355 | 121.8113 | -0.26943
1651.3594 | 121.9528 | -121.7697 | 0.11444 | 1.4211e-13 | -0.030036 | 0.014252 | -0.0038527 | -0.012974 | 0.018843 | -0.23296 | 0.018012 | 0.018676 | 0.015598 | 0.034153 | 0.0096806 | 0.060567 | 0.019721 | 0.023639 | 0.11165 | 0.055306 | 0.27017 | 0.042258 | 0.06515 | 0.036989 | -0.001407 | 0.075351 | 0.1648 | -0.10671 | -0.15499 | 121.812 | -0.002794 | 121.8303 | 121.7934 | -0.018619 | -0.059135 | 0.15573 | 121.6147 | -0.03909 | 121.8349 | 121.7683 | 0.15358 | 0.050359 | -0.22115 | 121.8814 | 121.825 | 122.0399 | 121.7894 | -0.072183 | 121.8451 | 121.9345 | 121.663 | 121.8067 | -0.26943
1653.1094 | 122.081 | -121.7239 | 0.091553 | 1.4211e-13 | -0.029822 | 0.013611 | -0.0036391 | -0.012974 | 0.018843 | -0.23296 | 0.017798 | 0.018676 | 0.015812 | 0.034153 | 0.0096806 | 0.055988 | 0.015142 | 0.028217 | 0.11165 | 0.064464 | 0.25643 | 0.0331 | 0.060571 | 0.027831 | -0.010564 | 0.075351 | 0.1648 | -0.11587 | -0.15499 | 121.757 | 0.020094 | 121.7799 | 121.7522 | -0.004883 | -0.027089 | 0.16488 | 121.5689 | -0.016202 | 121.7845 | 121.7134 | 0.14443 | 0.073247 | -0.20742 | 121.8356 | 121.7884 | 121.9804 | 121.7391 | -0.058453 | 121.7993 | 121.8887 | 121.6081 | 121.7518 | -0.24654
1654.8438 | 122.0215 | -121.756 | 0.10071 | 1.4211e-13 | -0.030036 | 0.013825 | -0.0038527 | -0.012546 | 0.018629 | -0.23296 | 0.018439 | 0.018676 | 0.015385 | 0.034153 | 0.0096806 | 0.065145 | 0.010564 | 0.01906 | 0.11165 | 0.064464 | 0.27017 | 0.037679 | 0.055992 | 0.03241 | -0.005985 | 0.070773 | 0.15564 | -0.12503 | -0.15041 | 121.7937 | 0.010939 | 121.8211 | 121.775 | -0.018619 | -0.036244 | 0.16946 | 121.6056 | -0.029935 | 121.812 | 121.75 | 0.14443 | 0.054935 | -0.22574 | 121.8676 | 121.8204 | 122.0261 | 121.7665 | -0.063029 | 121.8268 | 121.9116 | 121.631 | 121.7884 | -0.25112
1656.5781 | 122.0306 | -121.7697 | 0.1236 | 1.4211e-13 | -0.029822 | 0.013825 | -0.0038527 | -0.012974 | 0.018629 | -0.24059 | 0.018012 | 0.018676 | 0.015812 | 0.034367 | 0.0096806 | 0.060567 | 0.010564 | 0.028217 | 0.11165 | 0.064464 | 0.26559 | 0.051416 | 0.055992 | 0.027831 | -0.010564 | 0.066194 | 0.15564 | -0.12503 | -0.15041 | 121.8211 | -0.011949 | 121.8303 | 121.7979 | -0.023199 | -0.059132 | 0.14199 | 121.6193 | -0.057402 | 121.8257 | 121.7591 | 0.13985 | 0.032047 | -0.24862 | 121.8814 | 121.8342 | 122.0353 | 121.7803 | -0.07218 | 121.8359 | 121.9254 | 121.6447 | 121.7975 | -0.27401
1658.25 | 121.9437 | -121.8018 | 0.1236 | 1.4211e-13 | -0.030036 | 0.013825 | -0.0036391 | -0.012974 | 0.018629 | -0.24059 | 0.018439 | 0.018676 | 0.015385 | 0.03394 | 0.0096806 | 0.055988 | 0.010564 | 0.023639 | 0.10707 | 0.059885 | 0.26559 | 0.028521 | 0.06515 | 0.036989 | -0.001407 | 0.070773 | 0.15107 | -0.12503 | -0.15499 | 121.8303 | -0.016528 | 121.8577 | 121.8254 | -0.004882 | -0.063711 | 0.14199 | 121.6468 | -0.052823 | 121.8669 | 121.8004 | 0.15358 | 0.027469 | -0.24862 | 121.9088 | 121.8616 | 122.0673 | 121.8123 | -0.095075 | 121.8725 | 121.9528 | 121.6767 | 121.8387 | -0.27859
1659.9844 | 121.9849 | -121.8109 | 0.13733 | 1.4211e-13 | -0.030036 | 0.014039 | -0.0036391 | -0.012974 | 0.018843 | -0.24059 | 0.018012 | 0.018676 | 0.015598 | 0.034153 | 0.0096806 | 0.065145 | 0.015142 | 0.01906 | 0.11165 | 0.059885 | 0.25185 | 0.046837 | 0.060571 | 0.036989 | -0.005985 | 0.066194 | 0.15107 | -0.097557 | -0.15499 | 121.8577 | -0.025682 | 121.8761 | 121.83 | -0.027777 | -0.077444 | 0.11452 | 121.6559 | -0.071135 | 121.8715 | 121.8049 | 0.14901 | 0.013736 | -0.23489 | 121.9226 | 121.8708 | 122.0628 | 121.8261 | -0.090492 | 121.8771 | 121.962 | 121.7134 | 121.8479 | -0.29232
1661.7188 | 122.0856 | -121.7514 | 0.10529 | 1.4211e-13 | -0.030036 | 0.013825 | -0.0036391 | -0.01276 | 0.018843 | -0.22533 | 0.017798 | 0.018889 | 0.015598 | 0.03394 | 0.0098942 | 0.055988 | 0.005985 | 0.01906 | 0.11622 | 0.059885 | 0.26559 | 0.014784 | 0.060571 | 0.041567 | -0.001407 | 0.070773 | 0.15564 | -0.12961 | -0.15957 | 121.7662 | 0.010939 | 121.8074 | 121.7705 | 0.004276 | -0.045401 | 0.1603 | 121.5918 | -0.034513 | 121.812 | 121.75 | 0.15816 | 0.050357 | -0.23489 | 121.8676 | 121.8113 | 122.017 | 121.7574 | -0.090502 | 121.8222 | 121.907 | 121.6218 | 121.793 | -0.26486
1663.4844 | 122.0627 | -121.7789 | 0.073242 | 1.4211e-13 | -0.030036 | 0.013825 | -0.0034253 | -0.01276 | 0.018416 | -0.24059 | 0.018225 | 0.018462 | 0.015598 | 0.034367 | 0.0098942 | 0.060567 | 0.005985 | 0.028217 | 0.11622 | 0.064464 | 0.26101 | 0.046837 | 0.055992 | 0.027831 | -0.001407 | 0.07993 | 0.14649 | -0.11129 | -0.15499 | 121.8257 | 0.042983 | 121.8394 | 121.8071 | -0.01862 | -0.008778 | 0.18777 | 121.6239 | 0.006688 | 121.8349 | 121.7775 | 0.15358 | 0.073244 | -0.18454 | 121.8951 | 121.8433 | 122.0399 | 121.7849 | -0.026405 | 121.8588 | 121.9254 | 121.6676 | 121.8067 | -0.22823
1665.1562 | 122.0947 | -121.7789 | 0.11444 | 1.4211e-13 | -0.03025 | 0.013825 | -0.0038527 | -0.013187 | 0.018416 | -0.24059 | 0.018439 | 0.018676 | 0.015385 | 0.034367 | 0.0096806 | 0.060567 | 0.015142 | 0.01906 | 0.11165 | 0.059885 | 0.25643 | 0.037679 | 0.06515 | 0.03241 | -0.010564 | 0.075351 | 0.15564 | -0.097557 | -0.15499 | 121.8165 | -0.002794 | 121.8394 | 121.7979 | -0.018619 | -0.054556 | 0.14199 | 121.6239 | -0.03909 | 121.844 | 121.7683 | 0.14443 | 0.041202 | -0.212 | 121.8905 | 121.8388 | 122.0353 | 121.794 | -0.076762 | 121.8542 | 121.9345 | 121.6813 | 121.8113 | -0.26943
1666.9062 | 122.0856 | -121.7697 | 0.11444 | 1.4211e-13 | -0.029822 | 0.013825 | -0.0036391 | -0.01276 | 0.018629 | -0.23296 | 0.018012 | 0.018462 | 0.015598 | 0.034153 | 0.0098942 | 0.065145 | 0.019721 | 0.028217 | 0.11622 | 0.059885 | 0.26101 | 0.028521 | 0.060571 | 0.027831 | -0.001407 | 0.070773 | 0.16022 | -0.092979 | -0.15957 | 121.7982 | 0.001784 | 121.8349 | 121.7979 | -0.000304 | -0.054556 | 0.14657 | 121.6101 | -0.043668 | 121.8303 | 121.7683 | 0.15816 | 0.045781 | -0.20742 | 121.8859 | 121.8296 | 122.0307 | 121.7894 | -0.08592 | 121.8405 | 121.9299 | 121.6767 | 121.7975 | -0.27401
1668.5938 | 121.994 | -121.8246 | 0.14648 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0038527 | -0.012974 | 0.018843 | -0.23296 | 0.018439 | 0.018676 | 0.015385 | 0.034153 | 0.0090396 | 0.060567 | 0.015142 | 0.01906 | 0.11165 | 0.059885 | 0.26559 | 0.028521 | 0.060571 | 0.03241 | -0.005985 | 0.070773 | 0.14649 | -0.13419 | -0.15499 | 121.8532 | -0.034837 | 121.8852 | 121.8437 | -0.009461 | -0.086599 | 0.1191 | 121.6697 | -0.075711 | 121.8852 | 121.8187 | 0.14901 | 2e-06 | -0.28067 | 121.9363 | 121.8845 | 122.0902 | 121.8398 | -0.11796 | 121.8954 | 121.9711 | 121.6905 | 121.8571 | -0.30147
1670.3438 | 122.1222 | -121.8018 | 0.11902 | 1.4211e-13 | -0.030036 | 0.014039 | -0.0038527 | -0.012974 | 0.018843 | -0.23296 | 0.018012 | 0.018889 | 0.015171 | 0.034367 | 0.0098942 | 0.060567 | 0.015142 | 0.014482 | 0.11165 | 0.059885 | 0.27017 | 0.019363 | 0.06515 | 0.03241 | -0.010564 | 0.075351 | 0.16022 | -0.11587 | -0.15041 | 121.8211 | -0.007372 | 121.8623 | 121.8162 | -0.004881 | -0.059134 | 0.15115 | 121.6513 | -0.043668 | 121.8669 | 121.7912 | 0.13985 | 0.041203 | -0.23489 | 121.9134 | 121.8616 | 122.0719 | 121.8169 | -0.099656 | 121.8771 | 121.962 | 121.6859 | 121.8342 | -0.26943
1672.0156 | 122.0078 | -121.8246 | 0.11902 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0034253 | -0.013187 | 0.018416 | -0.24059 | 0.018012 | 0.018676 | 0.015598 | 0.034367 | 0.0096806 | 0.060567 | 0.019721 | 0.023639 | 0.11622 | 0.059885 | 0.26559 | 0.023942 | 0.060571 | 0.036989 | -0.001407 | 0.075351 | 0.1648 | -0.097557 | -0.15499 | 121.8486 | -0.002794 | 121.8852 | 121.8483 | -0.000303 | -0.059134 | 0.14657 | 121.6697 | -0.043668 | 121.8852 | 121.8232 | 0.15358 | 0.045781 | -0.21658 | 121.9409 | 121.8845 | 122.0902 | 121.8444 | -0.095077 | 121.9 | 121.9894 | 121.7271 | 121.8616 | -0.27401
1673.75 | 122.0352 | -121.8109 | 0.11902 | 1.4211e-13 | -0.029822 | 0.013825 | -0.0038527 | -0.012974 | 0.018843 | -0.23296 | 0.018225 | 0.018676 | 0.015598 | 0.034367 | 0.0096806 | 0.060567 | 0.019721 | 0.023639 | 0.10249 | 0.064464 | 0.27475 | 0.046837 | 0.060571 | 0.027831 | -0.001407 | 0.075351 | 0.15107 | -0.12503 | -0.15041 | 121.8577 | -0.016529 | 121.8715 | 121.8346 | -0.023198 | -0.054555 | 0.15573 | 121.6605 | -0.043668 | 121.8715 | 121.8095 | 0.149 | 0.032046 | -0.24405 | 121.9134 | 121.8754 | 122.0857 | 121.8306 | -0.072182 | 121.8863 | 121.962 | 121.6859 | 121.8387 | -0.26943
1675.5 | 122.0352 | -121.7789 | 0.10986 | 1.4211e-13 | -0.030036 | 0.013825 | -0.0038527 | -0.01276 | 0.018843 | -0.23296 | 0.017798 | 0.018676 | 0.015385 | 0.034367 | 0.0096806 | 0.060567 | 0.015142 | 0.023639 | 0.10707 | 0.064464 | 0.25643 | 0.0331 | 0.060571 | 0.027831 | -0.015143 | 0.070773 | 0.15564 | -0.10671 | -0.15041 | 121.812 | -0.002795 | 121.8394 | 121.8025 | -0.009461 | -0.045399 | 0.14657 | 121.6285 | -0.03909 | 121.8394 | 121.7637 | 0.13527 | 0.04578 | -0.21658 | 121.8859 | 121.8433 | 122.0353 | 121.794 | -0.076763 | 121.8496 | 121.9345 | 121.6722 | 121.8067 | -0.26027
1677.2188 | 122.113 | -121.7926 | 0.10986 | 1.4211e-13 | -0.029822 | 0.013825 | -0.0042801 | -0.01276 | 0.018629 | -0.24822 | 0.018012 | 0.018889 | 0.015812 | 0.03394 | 0.0096806 | 0.060567 | 0.010564 | 0.023639 | 0.11622 | 0.064464 | 0.26101 | 0.037679 | 0.060571 | 0.03241 | -0.010564 | 0.070773 | 0.15107 | -0.0884 | -0.15499 | 121.8303 | 0.006362 | 121.8532 | 121.8162 | -0.01404 | -0.045399 | 0.15115 | 121.6376 | -0.03909 | 121.8532 | 121.782 | 0.14443 | 0.041202 | -0.19826 | 121.9088 | 121.8571 | 122.0536 | 121.8032 | -0.072184 | 121.8634 | 121.9437 | 121.7042 | 121.825 | -0.26485
1678.9062 | 122.1039 | -121.7697 | 0.16479 | 1.4211e-13 | -0.029822 | 0.013825 | -0.0036391 | -0.012974 | 0.018843 | -0.22533 | 0.018012 | 0.018889 | 0.015812 | 0.034367 | 0.009467 | 0.055988 | 0.010564 | 0.023639 | 0.11622 | 0.064464 | 0.26101 | 0.023942 | 0.06515 | 0.03241 | -0.001407 | 0.070773 | 0.15107 | -0.092979 | -0.15041 | 121.7937 | -0.04857 | 121.8257 | 121.7934 | -0.000303 | -0.10033 | 0.096215 | 121.6193 | -0.094022 | 121.8349 | 121.7683 | 0.149 | -0.01373 | -0.25777 | 121.8859 | 121.8342 | 122.0307 | 121.7803 | -0.14085 | 121.8405 | 121.9208 | 121.6767 | 121.8021 | -0.31521
1680.6562 | 122.1359 | -121.8475 | 0.09613 | 1.4211e-13 | -0.030036 | 0.013825 | -0.0040665 | -0.01276 | 0.018416 | -0.23296 | 0.018225 | 0.018676 | 0.015385 | 0.034367 | 0.009467 | 0.055988 | 0.010564 | 0.023639 | 0.11622 | 0.064464 | 0.26559 | 0.046837 | 0.06515 | 0.03241 | -0.010564 | 0.075351 | 0.15564 | -0.12045 | -0.15499 | 121.8944 | 0.020095 | 121.9035 | 121.8712 | -0.023198 | -0.031666 | 0.16946 | 121.6925 | -0.020779 | 121.9127 | 121.837 | 0.14443 | 0.059513 | -0.21658 | 121.9638 | 121.912 | 122.1131 | 121.8581 | -0.049293 | 121.9229 | 122.0032 | 121.7271 | 121.8799 | -0.25112
1682.3906 | 122.1222 | -121.8292 | 0.10986 | 1.4211e-13 | -0.029609 | 0.014039 | -0.0036391 | -0.013187 | 0.018629 | -0.22533 | 0.018012 | 0.018462 | 0.015812 | 0.034367 | 0.0096806 | 0.065145 | 0.010564 | 0.023639 | 0.11622 | 0.064464 | 0.26559 | 0.028521 | 0.06515 | 0.023253 | -0.005985 | 0.075351 | 0.16022 | -0.097557 | -0.15499 | 121.8577 | 0.006362 | 121.8944 | 121.8529 | -0.004882 | -0.045399 | 0.15573 | 121.6742 | -0.034512 | 121.8944 | 121.8232 | 0.14901 | 0.050359 | -0.20742 | 121.9454 | 121.8937 | 122.0948 | 121.8398 | -0.081342 | 121.9046 | 121.9894 | 121.7317 | 121.8525 | -0.26485
1684.0781 | 122.1313 | -121.8338 | 0.10986 | 1.4211e-13 | -0.030036 | 0.013825 | -0.0038527 | -0.013187 | 0.01927 | -0.22533 | 0.017798 | 0.018462 | 0.015812 | 0.034581 | 0.010108 | 0.060567 | 0.015142 | 0.01906 | 0.11622 | 0.055306 | 0.27017 | 0.0331 | 0.06515 | 0.027831 | -0.010564 | 0.070773 | 0.15564 | -0.079243 | -0.15499 | 121.8669 | 0.006362 | 121.8944 | 121.8529 | -0.01404 | -0.054557 | 0.1603 | 121.6788 | -0.03909 | 121.899 | 121.8232 | 0.14443 | 0.04578 | -0.18911 | 121.95 | 121.8891 | 122.104 | 121.8489 | -0.076763 | 121.9046 | 121.9894 | 121.7546 | 121.8616 | -0.26485
1685.75 | 122.0215 | -121.8521 | 0.14191 | 1.4211e-13 | -0.029822 | 0.013611 | -0.0036391 | -0.01276 | 0.018843 | -0.23296 | 0.018012 | 0.018889 | 0.015598 | 0.034153 | 0.0096806 | 0.065145 | 0.015142 | 0.01906 | 0.1208 | 0.064464 | 0.26101 | 0.037679 | 0.06515 | 0.027831 | -0.010564 | 0.075351 | 0.15564 | -0.0884 | -0.15041 | 121.8898 | -0.021103 | 121.9173 | 121.8712 | -0.018619 | -0.077443 | 0.1191 | 121.7017 | -0.066556 | 121.9173 | 121.8415 | 0.13985 | 0.013736 | -0.23031 | 121.9729 | 121.9166 | 122.1131 | 121.8673 | -0.10423 | 121.9275 | 122.0078 | 121.7637 | 121.8799 | -0.29232
1687.4844 | 122.1405 | -121.8338 | 0.10529 | 1.4211e-13 | -0.030036 | 0.013398 | -0.0036391 | -0.012974 | 0.018843 | -0.23296 | 0.017798 | 0.019103 | 0.015385 | 0.034367 | 0.0096806 | 0.055988 | 0.015142 | 0.014482 | 0.11622 | 0.059885 | 0.26559 | 0.037679 | 0.060571 | 0.03241 | -0.005985 | 0.066194 | 0.16022 | -0.10214 | -0.15499 | 121.8715 | 0.010939 | 121.8898 | 121.8483 | -0.023197 | -0.045401 | 0.1603 | 121.6788 | -0.039092 | 121.8944 | 121.8278 | 0.14901 | 0.054936 | -0.20742 | 121.95 | 121.8937 | 122.0994 | 121.8489 | -0.067607 | 121.9 | 121.994 | 121.7317 | 121.8662 | -0.26028
1689.1719 | 122.0398 | -121.8567 | 0.14648 | 1.4211e-13 | -0.030036 | 0.013825 | -0.0036391 | -0.01276 | 0.018629 | -0.24059 | 0.018225 | 0.018676 | 0.015598 | 0.034367 | 0.009467 | 0.055988 | 0.005985 | 0.01906 | 0.11622 | 0.064464 | 0.27017 | 0.028521 | 0.06515 | 0.03241 | -0.015143 | 0.075351 | 0.15564 | -0.12045 | -0.15041 | 121.8852 | -0.030259 | 121.9127 | 121.8757 | -0.009461 | -0.08202 | 0.12368 | 121.7063 | -0.071133 | 121.9218 | 121.8415 | 0.13527 | 0.009159 | -0.26693 | 121.9729 | 121.9212 | 122.1269 | 121.8627 | -0.11796 | 121.932 | 122.0123 | 121.7362 | 121.8891 | -0.2969
1690.9375 | 122.0764 | -121.8567 | 0.1236 | 1.4211e-13 | -0.030036 | 0.014039 | -0.0036391 | -0.012974 | 0.018843 | -0.23296 | 0.018225 | 0.018676 | 0.015385 | 0.034153 | 0.009467 | 0.060567 | 0.005985 | 0.01906 | 0.11165 | 0.055306 | 0.26559 | 0.023942 | 0.060571 | 0.03241 | -0.015143 | 0.07993 | 0.15564 | -0.12961 | -0.15499 | 121.8806 | -0.011949 | 121.9173 | 121.8757 | -0.004882 | -0.06829 | 0.14199 | 121.7017 | -0.043666 | 121.9173 | 121.8415 | 0.13985 | 0.032047 | -0.2532 | 121.9683 | 121.912 | 122.1223 | 121.8627 | -0.099654 | 121.9366 | 122.0123 | 121.7271 | 121.8891 | -0.27859
1692.6875 | 122.1313 | -121.7834 | 0.14191 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0038527 | -0.013187 | 0.018202 | -0.24059 | 0.018225 | 0.018676 | 0.015812 | 0.034367 | 0.009467 | 0.060567 | 0.010564 | 0.023639 | 0.11622 | 0.059885 | 0.26101 | 0.0331 | 0.06515 | 0.03241 | -0.001407 | 0.070773 | 0.15564 | -0.079243 | -0.14583 | 121.8165 | -0.025682 | 121.844 | 121.8071 | -0.009461 | -0.082022 | 0.1191 | 121.6376 | -0.071134 | 121.8486 | 121.782 | 0.14443 | 0.013736 | -0.22115 | 121.8997 | 121.8433 | 122.0445 | 121.794 | -0.10881 | 121.8542 | 121.9391 | 121.7042 | 121.8159 | -0.28774
1694.4219 | 122.113 | -121.843 | 0.13733 | 1.4211e-13 | -0.030036 | 0.014039 | -0.0036391 | -0.01276 | 0.018629 | -0.24059 | 0.017798 | 0.018676 | 0.015598 | 0.034367 | 0.0092534 | 0.05141 | 0.005985 | 0.023639 | 0.11622 | 0.069043 | 0.27017 | -0.044742 | 0.069728 | 0.036989 | -0.001407 | 0.070773 | 0.15564 | -0.0884 | -0.15499 | 121.7982 | -0.021104 | 121.8944 | 121.8666 | 0.068381 | -0.068286 | 0.13284 | 121.688 | -0.066556 | 121.9127 | 121.8415 | 0.15358 | 0.018314 | -0.22573 | 121.9592 | 121.912 | 122.1131 | 121.8489 | -0.18207 | 121.9137 | 121.9986 | 121.7546 | 121.8799 | -0.29232
1696.0938 | 122.049 | -121.8201 | 0.22888 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0038527 | -0.01276 | 0.018629 | -0.22533 | 0.018225 | 0.018462 | 0.015171 | 0.034367 | 0.009467 | 0.069723 | 0.010564 | 0.01906 | 0.11165 | 0.064464 | 0.26101 | -0.021847 | 0.06515 | 0.03241 | -0.010564 | 0.075351 | 0.15564 | -0.12961 | -0.15041 | 121.7982 | -0.11724 | 121.8898 | 121.8391 | 0.040907 | -0.16442 | 0.032128 | 121.6697 | -0.15353 | 121.8852 | 121.8095 | 0.13985 | -0.073239 | -0.35849 | 121.9317 | 121.8845 | 122.0811 | 121.8306 | -0.25073 | 121.8954 | 121.9757 | 121.6905 | 121.8525 | -0.37929
1697.8438 | 122.113 | -121.875 | 0.13275 | 1.4211e-13 | -0.029609 | 0.014039 | -0.0034253 | -0.012974 | 0.018843 | -0.22533 | 0.018225 | 0.018889 | 0.015385 | 0.034581 | 0.009467 | 0.060567 | 0.015142 | 0.023639 | 0.10707 | 0.055306 | 0.27017 | 0.010206 | 0.060571 | 0.036989 | -0.005985 | 0.070773 | 0.16022 | -0.074664 | -0.15499 | 121.8852 | -0.025683 | 121.9356 | 121.8986 | 0.013433 | -0.077445 | 0.13742 | 121.72 | -0.061978 | 121.9356 | 121.869 | 0.14901 | 0.027471 | -0.20742 | 121.9821 | 121.9303 | 122.1452 | 121.8901 | -0.12255 | 121.9458 | 122.0352 | 121.8003 | 121.912 | -0.28774
1699.5156 | 122.0306 | -121.8842 | 0.14191 | 1.4211e-13 | -0.030463 | 0.014039 | -0.0038527 | -0.01276 | 0.018629 | -0.22533 | 0.018012 | 0.018676 | 0.015598 | 0.03394 | 0.009467 | 0.065145 | 0.005985 | 0.01906 | 0.10707 | 0.055306 | 0.26559 | -0.021847 | 0.06515 | 0.036989 | -0.005985 | 0.075351 | 0.1648 | -0.10214 | -0.15041 | 121.8623 | -0.034839 | 121.9493 | 121.9032 | 0.040907 | -0.086601 | 0.12368 | 121.7337 | -0.066556 | 121.9493 | 121.8782 | 0.14443 | 0.022893 | -0.24404 | 121.9912 | 121.9395 | 122.1497 | 121.8901 | -0.16375 | 121.9595 | 122.049 | 121.782 | 121.9211 | -0.29232
1701.25 | 122.0261 | -121.8887 | 0.14648 | 1.4211e-13 | -0.029609 | 0.013611 | -0.0034253 | -0.01276 | 0.018629 | -0.24059 | 0.018012 | 0.018249 | 0.015598 | 0.03394 | 0.0096806 | 0.055988 | 0.010564 | 0.023639 | 0.10707 | 0.059885 | 0.26559 | 0.001048 | 0.06515 | 0.036989 | -0.005985 | 0.075351 | 0.1648 | -0.10214 | -0.15499 | 121.8898 | -0.039416 | 121.9447 | 121.9124 | 0.022591 | -0.086599 | 0.1191 | 121.7337 | -0.071133 | 121.9539 | 121.8827 | 0.14901 | 0.018316 | -0.24862 | 121.9958 | 121.9486 | 122.1543 | 121.8993 | -0.14544 | 121.9641 | 122.0535 | 121.7866 | 121.9257 | -0.30147
1703 | 122.0627 | -121.8887 | 0.13275 | 1.4211e-13 | -0.029822 | 0.013825 | -0.0038527 | -0.012974 | 0.019057 | -0.23296 | 0.018012 | 0.018889 | 0.015385 | 0.034367 | 0.009467 | 0.065145 | 0.019721 | 0.01906 | 0.10707 | 0.059885 | 0.27017 | -0.00811 | 0.06515 | 0.036989 | -0.005985 | 0.066194 | 0.16022 | -0.12045 | -0.15957 | 121.8806 | -0.025683 | 121.9539 | 121.9078 | 0.02717 | -0.072866 | 0.13742 | 121.7292 | -0.066557 | 121.9539 | 121.8827 | 0.15358 | 0.027471 | -0.2532 | 121.9958 | 121.9486 | 122.1589 | 121.9085 | -0.14086 | 121.9549 | 122.049 | 121.7683 | 121.9257 | -0.29232
1704.6719 | 122.1405 | -121.8704 | 0.11902 | 1.4211e-13 | -0.03025 | 0.013825 | -0.0038527 | -0.01276 | 0.018843 | -0.24059 | 0.018012 | 0.018676 | 0.015385 | 0.034367 | 0.0092534 | 0.055988 | 0.010564 | 0.01906 | 0.11165 | 0.059885 | 0.26559 | 0.001048 | 0.060571 | 0.03241 | -0.001407 | 0.070773 | 0.15564 | -0.065507 | -0.15499 | 121.8715 | -0.007372 | 121.9264 | 121.8895 | 0.018012 | -0.059134 | 0.14657 | 121.7154 | -0.048246 | 121.931 | 121.869 | 0.15358 | 0.036624 | -0.18453 | 121.9821 | 121.9303 | 122.136 | 121.881 | -0.11797 | 121.9412 | 122.0261 | 121.8049 | 121.9028 | -0.27401
1706.4219 | 122.2 | -121.8658 | 0.1236 | 1.4211e-13 | -0.029822 | 0.013398 | -0.0038527 | -0.013187 | 0.018843 | -0.24059 | 0.018012 | 0.018676 | 0.016026 | 0.034153 | 0.009467 | 0.065145 | 0.010564 | 0.014482 | 0.10707 | 0.064464 | 0.26101 | -0.072215 | 0.06515 | 0.041567 | -0.005985 | 0.061616 | 0.15107 | -0.12503 | -0.14125 | 121.7936 | -0.016528 | 121.931 | 121.8803 | 0.086697 | -0.059132 | 0.13741 | 121.7246 | -0.06198 | 121.931 | 121.8599 | 0.13527 | 0.027469 | -0.24862 | 121.9729 | 121.9303 | 122.1269 | 121.8764 | -0.19581 | 121.9275 | 122.0169 | 121.7408 | 121.9074 | -0.26485
1708.1094 | 122.0947 | -121.8842 | 0.13733 | 1.4211e-13 | -0.030036 | 0.014252 | -0.0034253 | -0.013187 | 0.018629 | -0.23296 | 0.018012 | 0.018889 | 0.016026 | 0.034367 | 0.009467 | 0.055988 | 0.005985 | 0.009904 | 0.11622 | 0.064464 | 0.26559 | 0.028521 | 0.060571 | 0.041567 | -0.010564 | 0.075351 | 0.16022 | -0.10214 | -0.15957 | 121.9127 | -0.021104 | 121.9401 | 121.8941 | -0.018617 | -0.072865 | 0.12826 | 121.7246 | -0.061978 | 121.9447 | 121.8736 | 0.14901 | 0.022893 | -0.23947 | 122.0004 | 121.9486 | 122.1497 | 121.8901 | -0.10881 | 121.9595 | 122.0444 | 121.782 | 121.9257 | -0.2969
1709.8594 | 122.1771 | -121.8475 | 0.11902 | 1.4211e-13 | -0.029822 | 0.013825 | -0.0038527 | -0.013187 | 0.018629 | -0.23296 | 0.018012 | 0.018676 | 0.015812 | 0.034367 | 0.009467 | 0.065145 | 0.010564 | 0.023639 | 0.11622 | 0.059885 | 0.26559 | 0.0331 | 0.060571 | 0.041567 | -0.005985 | 0.070773 | 0.1648 | -0.12961 | -0.15041 | 121.8806 | -0.002794 | 121.9127 | 121.8712 | -0.009461 | -0.059134 | 0.14657 | 121.6971 | -0.048246 | 121.9081 | 121.8415 | 0.14443 | 0.045781 | -0.24863 | 121.9638 | 121.9074 | 122.1131 | 121.8581 | -0.085919 | 121.9183 | 122.0123 | 121.7179 | 121.8891 | -0.26943
1711.5469 | 122.0581 | -121.9025 | 0.14648 | 1.4211e-13 | -0.029822 | 0.013611 | -0.0038527 | -0.013187 | 0.018843 | -0.23296 | 0.018225 | 0.018462 | 0.015385 | 0.034367 | 0.009467 | 0.060567 | 0.005985 | 0.01906 | 0.11165 | 0.050727 | 0.26559 | -0.063057 | 0.060571 | 0.027831 | -0.010564 | 0.075351 | 0.16022 | -0.060928 | -0.15041 | 121.8394 | -0.034837 | 121.963 | 121.9215 | 0.082117 | -0.095757 | 0.1191 | 121.7521 | -0.071133 | 121.963 | 121.8919 | 0.13985 | 0.013738 | -0.20741 | 122.0141 | 121.9532 | 122.1681 | 121.9085 | -0.20954 | 121.9778 | 122.0627 | 121.8415 | 121.9303 | -0.2969
1713.2969 | 122.1268 | -121.7972 | 0.10986 | 1.4211e-13 | -0.029822 | 0.013825 | -0.0036391 | -0.01276 | 0.018843 | -0.24822 | 0.018225 | 0.018676 | 0.015598 | 0.034367 | 0.0098942 | 0.055988 | 0.005985 | 0.01906 | 0.10707 | 0.055306 | 0.26559 | 0.037679 | 0.060571 | 0.03241 | -0.005985 | 0.066194 | 0.15564 | -0.083821 | -0.15499 | 121.8349 | -0.002795 | 121.8532 | 121.8162 | -0.018619 | -0.054557 | 0.15573 | 121.6422 | -0.043669 | 121.8578 | 121.7912 | 0.14901 | 0.04578 | -0.19368 | 121.9042 | 121.8525 | 122.0628 | 121.8032 | -0.072184 | 121.8634 | 121.9528 | 121.7134 | 121.8296 | -0.26485
1715.0469 | 122.1268 | -121.7926 | 0.11902 | 1.4211e-13 | -0.03025 | 0.013825 | -0.0040665 | -0.012974 | 0.018416 | -0.23296 | 0.018225 | 0.018676 | 0.015598 | 0.034581 | 0.0098942 | 0.065145 | 0.010564 | 0.01906 | 0.11165 | 0.055306 | 0.26559 | -0.012689 | 0.06515 | 0.036989 | -0.010564 | 0.075351 | 0.16022 | -0.12045 | -0.15041 | 121.7799 | -0.007372 | 121.8577 | 121.8117 | 0.031749 | -0.063713 | 0.14657 | 121.6422 | -0.043668 | 121.8578 | 121.782 | 0.13985 | 0.041203 | -0.23947 | 121.9043 | 121.8479 | 122.0582 | 121.8032 | -0.13171 | 121.868 | 121.9528 | 121.6722 | 121.8296 | -0.26943
1716.7344 | 122.0718 | -121.8384 | 0.14191 | 1.4211e-13 | -0.030036 | 0.013611 | -0.0040665 | -0.012974 | 0.018416 | -0.22533 | 0.018012 | 0.018249 | 0.015812 | 0.034367 | 0.009467 | 0.055988 | 0.010564 | 0.01906 | 0.11622 | 0.073622 | 0.26559 | 0.023942 | 0.069728 | 0.036989 | -0.001407 | 0.066194 | 0.1648 | -0.097557 | -0.15499 | 121.8623 | -0.025682 | 121.8944 | 121.8574 | -0.004882 | -0.068285 | 0.12368 | 121.6834 | -0.075713 | 121.9081 | 121.837 | 0.15358 | 0.022893 | -0.23946 | 121.9546 | 121.912 | 122.104 | 121.8489 | -0.11797 | 121.9046 | 122.0032 | 121.7408 | 121.8754 | -0.2969
1718.5 | 122.0947 | -121.8109 | 0.11444 | 1.4211e-13 | -0.029609 | 0.013825 | -0.0038527 | -0.012974 | 0.018843 | -0.23296 | 0.017798 | 0.018676 | 0.015171 | 0.034367 | 0.0096806 | 0.065145 | 0.015142 | 0.023639 | 0.1208 | 0.064464 | 0.26101 | 0.023942 | 0.06515 | 0.03241 | -0.005985 | 0.07993 | 0.16022 | -0.0884 | -0.15499 | 121.8349 | 0.006363 | 121.8761 | 121.8346 | -0.000303 | -0.049977 | 0.14657 | 121.6559 | -0.034511 | 121.8761 | 121.8049 | 0.14901 | 0.045781 | -0.20284 | 121.9317 | 121.8754 | 122.0719 | 121.8261 | -0.090499 | 121.8908 | 121.9711 | 121.7225 | 121.8433 | -0.26943
1720.2344 | 122.1085 | -121.788 | 0.12817 | 1.4211e-13 | -0.030036 | 0.013611 | -0.0036391 | -0.013187 | 0.018843 | -0.22533 | 0.018012 | 0.018676 | 0.015385 | 0.034153 | 0.009467 | 0.060567 | 0.015142 | 0.014482 | 0.1208 | 0.064464 | 0.26559 | 0.001048 | 0.060571 | 0.041567 | -0.005985 | 0.070773 | 0.15107 | -0.097557 | -0.15041 | 121.7891 | -0.00737 | 121.8486 | 121.8025 | 0.013434 | -0.06371 | 0.13741 | 121.6376 | -0.057401 | 121.8486 | 121.782 | 0.14443 | 0.022891 | -0.22573 | 121.9088 | 121.8525 | 122.0536 | 121.8032 | -0.12713 | 121.8588 | 121.9391 | 121.6905 | 121.8296 | -0.27859
1721.9219 | 122.0306 | -121.7972 | 0.13733 | 1.4211e-13 | -0.030036 | 0.013611 | -0.0036391 | -0.013187 | 0.018843 | -0.23296 | 0.018012 | 0.018889 | 0.015598 | 0.034367 | 0.0096806 | 0.060567 | 0.015142 | 0.01906 | 0.11622 | 0.059885 | 0.26559 | -0.003531 | 0.06515 | 0.03241 | -0.001407 | 0.075351 | 0.16022 | -0.11129 | -0.15041 | 121.7936 | -0.021104 | 121.8577 | 121.8162 | 0.022591 | -0.077444 | 0.12826 | 121.6468 | -0.061978 | 121.8623 | 121.7958 | 0.149 | 0.022893 | -0.24862 | 121.9134 | 121.8571 | 122.0628 | 121.8123 | -0.14086 | 121.8725 | 121.9574 | 121.6859 | 121.8296 | -0.28774
1723.6719 | 121.9345 | -121.8109 | 0.16479 | 1.4211e-13 | -0.030036 | 0.013825 | -0.0036391 | -0.01276 | 0.018843 | -0.24059 | 0.018012 | 0.018676 | 0.015598 | 0.034153 | 0.0090396 | 0.055988 | 0.015142 | 0.01906 | 0.11165 | 0.059885 | 0.26559 | -0.053899 | 0.060571 | 0.03241 | -0.005985 | 0.084508 | 0.16022 | -0.097557 | -0.15499 | 121.757 | -0.053148 | 121.8669 | 121.83 | 0.072959 | -0.10491 | 0.10079 | 121.6559 | -0.080287 | 121.8715 | 121.8049 | 0.14901 | -0.004573 | -0.26235 | 121.9226 | 121.8708 | 122.0765 | 121.8261 | -0.21869 | 121.8954 | 121.9711 | 121.7134 | 121.8433 | -0.31979
1725.4219 | 122.0718 | -121.6461 | 0.2243 | 1.4211e-13 | -0.029609 | 0.013825 | -0.0038527 | -0.013187 | 0.018843 | -0.22533 | 0.018225 | 0.018462 | 0.015598 | 0.034153 | 0.0092534 | 0.060567 | 0.010564 | 0.023639 | 0.11165 | 0.055306 | 0.26559 | -0.021847 | 0.06515 | 0.036989 | -0.001407 | 0.07993 | 0.16022 | -0.11587 | -0.14583 | 121.6243 | -0.11266 | 121.7067 | 121.6698 | 0.045486 | -0.169 | 0.041284 | 121.5003 | -0.14437 | 121.7113 | 121.6447 | 0.14443 | -0.064082 | -0.34018 | 121.7578 | 121.7014 | 121.9117 | 121.6567 | -0.24615 | 121.726 | 121.8063 | 121.5302 | 121.6831 | -0.37014
1727.0938 | 121.9711 | -121.8475 | 0.14191 | 1.4211e-13 | -0.03025 | 0.014039 | -0.0038527 | -0.012974 | 0.018843 | -0.24822 | 0.018012 | 0.018676 | 0.015812 | 0.034367 | 0.0092534 | 0.060567 | 0.015142 | 0.014482 | 0.1208 | 0.059885 | 0.27017 | -0.076794 | 0.060571 | 0.036989 | -0.010564 | 0.075351 | 0.15564 | -0.097557 | -0.15041 | 121.7707 | -0.021103 | 121.9081 | 121.862 | 0.091276 | -0.082022 | 0.12826 | 121.6971 | -0.066556 | 121.9081 | 121.837 | 0.13985 | 0.013736 | -0.23946 | 121.9683 | 121.9074 | 122.1177 | 121.8627 | -0.2187 | 121.9229 | 122.0032 | 121.75 | 121.8845 | -0.29232
1728.8438 | 121.9757 | -121.8567 | 0.15564 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0038527 | -0.013187 | 0.018629 | -0.22533 | 0.017798 | 0.018676 | 0.015385 | 0.03394 | 0.0096806 | 0.065145 | 0.010564 | 0.01906 | 0.11165 | 0.050727 | 0.27475 | 0.023942 | 0.060571 | 0.03241 | -0.005985 | 0.075351 | 0.14649 | -0.12503 | -0.15041 | 121.8806 | -0.043993 | 121.9218 | 121.8757 | -0.004882 | -0.10491 | 0.11911 | 121.7063 | -0.080289 | 121.9173 | 121.8507 | 0.14443 | -0.009154 | -0.28067 | 121.9683 | 121.9074 | 122.1314 | 121.8673 | -0.1317 | 121.932 | 122.0032 | 121.7317 | 121.8891 | -0.30605
1730.5938 | 122.0581 | -121.7972 | 0.12817 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0038527 | -0.013187 | 0.018629 | -0.23296 | 0.018012 | 0.018462 | 0.015812 | 0.034581 | 0.0090396 | 0.060567 | 0.015142 | 0.01906 | 0.11165 | 0.069043 | 0.26101 | 0.0331 | 0.060571 | 0.041567 | -0.001407 | 0.075351 | 0.15564 | -0.083821 | -0.15957 | 121.8303 | -0.016527 | 121.8577 | 121.8162 | -0.01404 | -0.059131 | 0.13284 | 121.6376 | -0.052823 | 121.8578 | 121.7958 | 0.15816 | 0.027469 | -0.212 | 121.9088 | 121.8662 | 122.0582 | 121.8123 | -0.095074 | 121.8725 | 121.9528 | 121.7134 | 121.8387 | -0.28774
1732.2812 | 121.962 | -121.8246 | 0.16022 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0038527 | -0.013187 | 0.018629 | -0.22533 | 0.018225 | 0.018676 | 0.015598 | 0.034367 | 0.009467 | 0.060567 | 0.019721 | 0.01906 | 0.1208 | 0.055306 | 0.27017 | 0.023942 | 0.060571 | 0.036989 | -0.015143 | 0.066194 | 0.1648 | -0.083821 | -0.15499 | 121.8486 | -0.039413 | 121.8852 | 121.8437 | -0.004882 | -0.10491 | 0.10995 | 121.6697 | -0.094023 | 121.8852 | 121.8095 | 0.13985 | 0.004583 | -0.24404 | 121.9455 | 121.88 | 122.0948 | 121.8444 | -0.13628 | 121.8908 | 121.9894 | 121.7408 | 121.8616 | -0.31521
1734.0312 | 121.9986 | -121.7834 | 0.18768 | 1.4211e-13 | -0.029822 | 0.013611 | -0.0036391 | -0.01276 | 0.018843 | -0.23296 | 0.017798 | 0.018676 | 0.015598 | 0.034367 | 0.0096806 | 0.065145 | 0.005985 | 0.023639 | 0.10707 | 0.055306 | 0.26559 | 0.037679 | 0.069728 | 0.03241 | -0.005985 | 0.070773 | 0.16022 | -0.12045 | -0.15957 | 121.8211 | -0.080615 | 121.8486 | 121.8071 | -0.01404 | -0.13238 | 0.077905 | 121.6239 | -0.11691 | 121.8532 | 121.7775 | 0.15358 | -0.027461 | -0.30813 | 121.8905 | 121.8388 | 122.049 | 121.7894 | -0.15 | 121.8542 | 121.9437 | 121.663 | 121.8159 | -0.34725
1735.7812 | 122.0581 | -121.7972 | 0.10529 | 1.4211e-13 | -0.030036 | 0.013825 | -0.0038527 | -0.013187 | 0.018629 | -0.23296 | 0.018225 | 0.018676 | 0.015598 | 0.034581 | 0.009467 | 0.060567 | 0.010564 | 0.014482 | 0.11165 | 0.055306 | 0.25643 | 0.010206 | 0.055992 | 0.036989 | -0.010564 | 0.066194 | 0.15107 | -0.13419 | -0.15041 | 121.8074 | 0.006361 | 121.8577 | 121.8117 | 0.004276 | -0.04998 | 0.15115 | 121.6468 | -0.039092 | 121.8532 | 121.7866 | 0.13985 | 0.045779 | -0.23947 | 121.9088 | 121.8525 | 122.0536 | 121.8077 | -0.09508 | 121.8634 | 121.9482 | 121.663 | 121.8342 | -0.2557
1737.4531 | 121.9437 | -121.8292 | 0.16937 | 1.4211e-13 | -0.030036 | 0.014252 | -0.0036391 | -0.013401 | 0.018416 | -0.23296 | 0.018225 | 0.018462 | 0.015385 | 0.034367 | 0.0092534 | 0.065145 | 0.005985 | 0.014482 | 0.1208 | 0.059885 | 0.26559 | 0.028521 | 0.060571 | 0.03241 | -0.005985 | 0.07993 | 0.1648 | -0.11129 | -0.15499 | 121.8577 | -0.048569 | 121.8944 | 121.8437 | -0.014039 | -0.10949 | 0.096215 | 121.6742 | -0.089443 | 121.8898 | 121.8232 | 0.14901 | -0.004573 | -0.28067 | 121.95 | 121.8891 | 122.0948 | 121.8352 | -0.14085 | 121.9092 | 121.994 | 121.7179 | 121.8616 | -0.32436
1739.2031 | 122.0947 | -121.7606 | 0.11902 | 1.4211e-13 | -0.030036 | 0.013611 | -0.0036391 | -0.013187 | 0.018629 | -0.24059 | 0.018225 | 0.018462 | 0.015598 | 0.03394 | 0.0092534 | 0.055988 | 0.010564 | 0.023639 | 0.11165 | 0.059885 | 0.27017 | -0.012689 | 0.060571 | 0.03241 | -0.015143 | 0.075351 | 0.1648 | -0.092979 | -0.15499 | 121.7479 | -0.007372 | 121.8165 | 121.7842 | 0.036328 | -0.059134 | 0.15115 | 121.6056 | -0.043668 | 121.8211 | 121.7454 | 0.13985 | 0.045781 | -0.212 | 121.8722 | 121.8204 | 122.0307 | 121.7711 | -0.13171 | 121.8359 | 121.9254 | 121.6676 | 121.793 | -0.27401
1740.8906 | 121.9757 | -121.8292 | 0.13275 | 1.4211e-13 | -0.030036 | 0.014252 | -0.0036391 | -0.013401 | 0.018416 | -0.24822 | 0.018012 | 0.018889 | 0.015812 | 0.034367 | 0.0090396 | 0.060567 | 0.019721 | 0.014482 | 0.11622 | 0.055306 | 0.26559 | 0.014784 | 0.060571 | 0.03241 | -0.001407 | 0.075351 | 0.16022 | -0.065507 | -0.14583 | 121.844 | -0.016526 | 121.8898 | 121.8437 | -0.000302 | -0.077445 | 0.13284 | 121.6834 | -0.0574 | 121.8898 | 121.8278 | 0.14443 | 0.027471 | -0.19826 | 121.9454 | 121.8845 | 122.0948 | 121.8489 | -0.11797 | 121.9046 | 121.9894 | 121.7637 | 121.8616 | -0.27858
1742.6406 | 121.9803 | -121.7743 | 0.12817 | 1.4211e-13 | -0.029822 | 0.013825 | -0.0042801 | -0.013187 | 0.018629 | -0.22533 | 0.018225 | 0.018676 | 0.015385 | 0.034367 | 0.009467 | 0.055988 | 0.010564 | 0.023639 | 0.11165 | 0.050727 | 0.26559 | -0.10885 | 0.06515 | 0.027831 | -0.010564 | 0.070773 | 0.15564 | -0.11587 | -0.15499 | 121.6654 | -0.016527 | 121.8303 | 121.7979 | 0.13249 | -0.077447 | 0.13741 | 121.6193 | -0.057401 | 121.8394 | 121.7637 | 0.14443 | 0.027469 | -0.24405 | 121.8859 | 121.825 | 122.0399 | 121.7849 | -0.23702 | 121.8451 | 121.9299 | 121.6584 | 121.8021 | -0.28317
1744.3906 | 122.0901 | -121.7834 | 0.10071 | 1.4211e-13 | -0.030036 | 0.014252 | -0.0038527 | -0.013187 | 0.018629 | -0.23296 | 0.018012 | 0.018249 | 0.015171 | 0.034581 | 0.009467 | 0.055988 | 0.005985 | 0.014482 | 0.11165 | 0.055306 | 0.27017 | -0.021847 | 0.060571 | 0.041567 | -0.005985 | 0.075351 | 0.16022 | -0.0884 | -0.15499 | 121.7616 | 0.010939 | 121.8394 | 121.7979 | 0.036329 | -0.045402 | 0.16946 | 121.6285 | -0.025357 | 121.844 | 121.7775 | 0.14901 | 0.059514 | -0.18911 | 121.8951 | 121.8388 | 122.0536 | 121.7894 | -0.12255 | 121.8588 | 121.9437 | 121.695 | 121.825 | -0.2557
1746.1406 | 121.9803 | -121.788 | 0.14648 | 1.4211e-13 | -0.030036 | 0.013825 | -0.0038527 | -0.012974 | 0.018416 | -0.24059 | 0.018439 | 0.018462 | 0.015598 | 0.034367 | 0.0096806 | 0.065145 | 0.005985 | 0.01906 | 0.11165 | 0.069043 | 0.27017 | 0.037679 | 0.055992 | 0.03241 | -0.001407 | 0.066194 | 0.15564 | -0.12503 | -0.15041 | 121.8257 | -0.034837 | 121.8532 | 121.8071 | -0.018619 | -0.077441 | 0.12368 | 121.6376 | -0.08029 | 121.844 | 121.7866 | 0.149 | 0.009159 | -0.27151 | 121.8997 | 121.8571 | 122.0582 | 121.794 | -0.10881 | 121.8542 | 121.9437 | 121.663 | 121.8204 | -0.2969
1747.875 | 121.962 | -121.8018 | 0.14648 | 1.4211e-13 | -0.029395 | 0.014039 | -0.0036391 | -0.013187 | 0.018629 | -0.23296 | 0.018012 | 0.018676 | 0.015385 | 0.03394 | 0.009467 | 0.060567 | 0.015142 | 0.014482 | 0.10707 | 0.059885 | 0.26559 | -0.021847 | 0.055992 | 0.03241 | -0.010564 | 0.075351 | 0.15564 | -0.10214 | -0.15499 | 121.7799 | -0.039416 | 121.8623 | 121.8162 | 0.036329 | -0.086599 | 0.1191 | 121.6468 | -0.071133 | 121.8578 | 121.7912 | 0.14443 | 0.009159 | -0.24862 | 121.9088 | 121.8616 | 122.0673 | 121.8169 | -0.16833 | 121.8771 | 121.9574 | 121.6996 | 121.8342 | -0.30147
1749.5469 | 122.0627 | -121.5363 | 0.32501 | 1.4211e-13 | -0.03025 | 0.013611 | -0.0038527 | -0.013187 | 0.018629 | -0.23296 | 0.018225 | 0.018676 | 0.015171 | 0.034581 | 0.0092534 | 0.060567 | 0.010564 | 0.01906 | 0.11622 | 0.055306 | 0.27017 | -0.031005 | 0.069728 | 0.036989 | -0.001407 | 0.07993 | 0.1648 | -0.060928 | -0.15499 | 121.5053 | -0.20879 | 121.5968 | 121.5553 | 0.050065 | -0.26971 | -0.054845 | 121.3813 | -0.24508 | 121.606 | 121.5348 | 0.15358 | -0.16021 | -0.38594 | 121.6525 | 121.5916 | 121.8064 | 121.5468 | -0.35602 | 121.6162 | 121.7011 | 121.4753 | 121.5732 | -0.48
1751.2344 | 122.0169 | -121.7789 | 0.14191 | 1.4211e-13 | -0.029822 | 0.013825 | -0.0036391 | -0.013187 | 0.018843 | -0.23296 | 0.018012 | 0.018676 | 0.015385 | 0.034367 | 0.009467 | 0.060567 | 0.005985 | 0.023639 | 0.11165 | 0.059885 | 0.27475 | 0.042258 | 0.060571 | 0.036989 | -0.010564 | 0.075351 | 0.1648 | -0.12503 | -0.15957 | 121.8211 | -0.03026 | 121.8394 | 121.8025 | -0.018619 | -0.082022 | 0.13284 | 121.6193 | -0.066556 | 121.8394 | 121.7683 | 0.14901 | 0.022893 | -0.26694 | 121.8905 | 121.8388 | 122.0536 | 121.7849 | -0.099649 | 121.8542 | 121.9437 | 121.6538 | 121.8159 | -0.30148
1752.9844 | 122.0169 | -121.7651 | 0.13275 | 1.4211e-13 | -0.030036 | 0.013611 | -0.0038527 | -0.013187 | 0.018629 | -0.23296 | 0.018012 | 0.018676 | 0.015171 | 0.034367 | 0.0096806 | 0.060567 | 0.015142 | 0.023639 | 0.10707 | 0.055306 | 0.27017 | 0.037679 | 0.060571 | 0.03241 | -0.001407 | 0.075351 | 0.15107 | -0.10671 | -0.15499 | 121.8028 | -0.025683 | 121.8257 | 121.7888 | -0.01404 | -0.077445 | 0.13742 | 121.6101 | -0.0574 | 121.8257 | 121.7637 | 0.15358 | 0.018314 | -0.23947 | 121.8722 | 121.8204 | 122.0353 | 121.7803 | -0.095072 | 121.8405 | 121.9162 | 121.6584 | 121.7975 | -0.28774
1754.6719 | 122.0764 | -121.7697 | 0.13275 | 1.4211e-13 | -0.029822 | 0.013611 | -0.0036391 | -0.013187 | 0.018629 | -0.2177 | 0.018439 | 0.018676 | 0.015812 | 0.034153 | 0.009467 | 0.055988 | 0.005985 | 0.01906 | 0.11165 | 0.059885 | 0.27017 | 0.0331 | 0.060571 | 0.036989 | -0.010564 | 0.075351 | 0.15564 | -0.097557 | -0.15499 | 121.8028 | -0.021104 | 121.8257 | 121.7888 | -0.01404 | -0.072866 | 0.13742 | 121.6147 | -0.0574 | 121.8303 | 121.7591 | 0.14443 | 0.022892 | -0.23031 | 121.8814 | 121.8296 | 122.0399 | 121.7757 | -0.099651 | 121.8451 | 121.9254 | 121.6722 | 121.8067 | -0.28774
1756.4219 | 122.049 | -121.7606 | 0.10529 | 1.4211e-13 | -0.029822 | 0.013611 | -0.0034253 | -0.012974 | 0.018843 | -0.23296 | 0.018012 | 0.018676 | 0.015812 | 0.034795 | 0.009467 | 0.060567 | 0.015142 | 0.01906 | 0.11622 | 0.064464 | 0.27017 | 0.023942 | 0.051413 | 0.023253 | -0.010564 | 0.075351 | 0.15107 | -0.079243 | -0.16415 | 121.7845 | 0.010939 | 121.8211 | 121.7796 | -0.004882 | -0.040822 | 0.16488 | 121.5964 | -0.029935 | 121.812 | 121.75 | 0.15358 | 0.045779 | -0.18453 | 121.8768 | 121.825 | 122.0307 | 121.7757 | -0.081344 | 121.8359 | 121.9116 | 121.6813 | 121.7838 | -0.26943
1758.1719 | 121.994 | -121.8063 | 0.14191 | 1.4211e-13 | -0.030036 | 0.014039 | -0.0038527 | -0.01276 | 0.018843 | -0.23296 | 0.018439 | 0.018676 | 0.015385 | 0.034367 | 0.009467 | 0.065145 | 0.015142 | 0.023639 | 0.1208 | 0.055306 | 0.26559 | -0.017268 | 0.051413 | 0.027831 | -0.005985 | 0.070773 | 0.15564 | -0.12045 | -0.15041 | 121.7891 | -0.021103 | 121.8715 | 121.83 | 0.040907 | -0.086601 | 0.12368 | 121.6559 | -0.071134 | 121.8577 | 121.8004 | 0.14443 | 0.013736 | -0.26236 | 121.9271 | 121.8616 | 122.0719 | 121.8215 | -0.15918 | 121.8771 | 121.962 | 121.6859 | 121.8342 | -0.29232
1759.8438 | 122.0764 | -121.7651 | 0.11444 | 1.4211e-13 | -0.030036 | 0.013825 | -0.0036391 | -0.013187 | 0.018843 | -0.24059 | 0.017584 | 0.018676 | 0.015598 | 0.034367 | 0.0092534 | 0.060567 | 0.005985 | 0.014482 | 0.10249 | 0.059885 | 0.26101 | -0.044742 | 0.051413 | 0.036989 | -0.010564 | 0.07993 | 0.15564 | -0.12961 | -0.15957 | 121.7204 | -0.011951 | 121.8257 | 121.7796 | 0.059224 | -0.054556 | 0.14657 | 121.6056 | -0.034511 | 121.8165 | 121.7546 | 0.14901 | 0.041202 | -0.24405 | 121.8676 | 121.825 | 122.0261 | 121.7711 | -0.15918 | 121.8451 | 121.9208 | 121.6355 | 121.8021 | -0.27401
1761.5938 | 122.1039 | -121.8704 | 0.10529 | 1.4211e-13 | -0.030036 | 0.013825 | -0.0038527 | -0.013401 | 0.018629 | -0.22533 | 0.018225 | 0.019103 | 0.015598 | 0.034153 | 0.009467 | 0.055988 | 0.010564 | 0.028217 | 0.10707 | 0.064464 | 0.26101 | 0.028521 | 0.060571 | 0.03241 | -0.015143 | 0.075351 | 0.15564 | -0.12503 | -0.15957 | 121.8989 | 0.001782 | 121.9264 | 121.8986 | -0.000304 | -0.040822 | 0.15572 | 121.7109 | -0.029935 | 121.931 | 121.8553 | 0.14443 | 0.050357 | -0.23031 | 121.9775 | 121.9349 | 122.1314 | 121.881 | -0.076765 | 121.9458 | 122.0261 | 121.7454 | 121.9028 | -0.26486
1763.3438 | 122.081 | -121.8979 | 0.10071 | 1.4211e-13 | -0.030036 | 0.013611 | -0.0038527 | -0.012974 | 0.018843 | -0.23296 | 0.018012 | 0.018676 | 0.015598 | 0.034367 | 0.0096806 | 0.055988 | 0.005985 | 0.01906 | 0.11165 | 0.050727 | 0.26559 | 0.0331 | 0.051413 | 0.027831 | -0.015143 | 0.066194 | 0.16022 | -0.092979 | -0.15499 | 121.931 | 0.010939 | 121.9539 | 121.9169 | -0.01404 | -0.049981 | 0.16488 | 121.7429 | -0.034514 | 121.9493 | 121.8827 | 0.13985 | 0.059514 | -0.19369 | 122.0095 | 121.9486 | 122.1635 | 121.9039 | -0.067608 | 121.9641 | 122.0581 | 121.8049 | 121.9257 | -0.2557
1765.0312 | 122.0581 | -121.8887 | 0.1236 | 1.4211e-13 | -0.029609 | 0.013825 | -0.0038527 | -0.013187 | 0.018629 | -0.22533 | 0.018225 | 0.018676 | 0.015812 | 0.03394 | 0.0090396 | 0.055988 | 0.010564 | 0.023639 | 0.10707 | 0.059885 | 0.26101 | 0.028521 | 0.055992 | 0.027831 | -0.005985 | 0.070773 | 0.15107 | -0.12503 | -0.15957 | 121.9173 | -0.016528 | 121.9447 | 121.9124 | -0.004882 | -0.063711 | 0.13741 | 121.7292 | -0.052823 | 121.9447 | 121.8827 | 0.15358 | 0.027469 | -0.24862 | 121.9958 | 121.9486 | 122.1497 | 121.8993 | -0.095075 | 121.9595 | 122.0398 | 121.7637 | 121.9166 | -0.28317
1766.7812 | 122.1634 | -121.8704 | 0.10071 | 1.4211e-13 | -0.030036 | 0.014252 | -0.0038527 | -0.013401 | 0.019057 | -0.23296 | 0.018012 | 0.018462 | 0.015812 | 0.034367 | 0.0090396 | 0.060567 | 0.005985 | 0.028217 | 0.11165 | 0.059885 | 0.25643 | 0.019363 | 0.055992 | 0.027831 | -0.019721 | 0.070773 | 0.15107 | -0.11129 | -0.16873 | 121.8898 | 0.010939 | 121.931 | 121.8986 | 0.008854 | -0.040823 | 0.15572 | 121.7017 | -0.029935 | 121.9264 | 121.8507 | 0.14901 | 0.050357 | -0.212 | 121.9821 | 121.9303 | 122.1269 | 121.8764 | -0.081345 | 121.9412 | 122.0215 | 121.7591 | 121.8983 | -0.26944
1768.5156 | 122.0901 | -121.9299 | 0.13733 | 1.4211e-13 | -0.030036 | 0.014039 | -0.0040665 | -0.013187 | 0.018629 | -0.24822 | 0.018439 | 0.018462 | 0.015385 | 0.034367 | 0.0092534 | 0.055988 | 0.005985 | 0.023639 | 0.11165 | 0.055306 | 0.26559 | 0.019363 | 0.060571 | 0.03241 | -0.010564 | 0.066194 | 0.14191 | -0.12961 | -0.15957 | 121.9493 | -0.025682 | 121.9859 | 121.9536 | 0.004276 | -0.082023 | 0.12826 | 121.7704 | -0.071135 | 121.9905 | 121.9194 | 0.14901 | 0.004578 | -0.26694 | 122.0416 | 121.9852 | 122.1955 | 121.9359 | -0.11797 | 121.9961 | 122.0718 | 121.8003 | 121.9623 | -0.2969
1770.1875 | 122.1268 | -121.8979 | 0.10071 | 1.4211e-13 | -0.029609 | 0.013825 | -0.0036391 | -0.012974 | 0.018843 | -0.22533 | 0.018439 | 0.018676 | 0.015385 | 0.034153 | 0.0092534 | 0.055988 | 0.015142 | 0.023639 | 0.10707 | 0.055306 | 0.26559 | 0.028521 | 0.051413 | 0.027831 | -0.010564 | 0.066194 | 0.15107 | -0.12961 | -0.16873 | 121.9264 | 0.00636 | 121.9539 | 121.9215 | -0.004882 | -0.045402 | 0.16488 | 121.7292 | -0.034514 | 121.9493 | 121.8873 | 0.15816 | 0.050357 | -0.23031 | 122.005 | 121.9532 | 122.1635 | 121.913 | -0.072187 | 121.9641 | 122.049 | 121.7683 | 121.9257 | -0.26944
1771.9219 | 122.1222 | -121.9254 | 0.10529 | 1.4211e-13 | -0.03025 | 0.014039 | -0.0036391 | -0.013401 | 0.018629 | -0.24059 | 0.017798 | 0.018462 | 0.015812 | 0.034581 | 0.0096806 | 0.046831 | 0.005985 | 0.01906 | 0.10249 | 0.064464 | 0.26559 | 0.028521 | 0.055992 | 0.03241 | -0.010564 | 0.075351 | 0.15107 | -0.0884 | -0.16873 | 121.9539 | -0.002796 | 121.9722 | 121.9444 | -0.009461 | -0.040822 | 0.1603 | 121.7566 | -0.029935 | 121.9813 | 121.9148 | 0.15816 | 0.045779 | -0.19369 | 122.0278 | 121.9898 | 122.1909 | 121.9313 | -0.076765 | 122.0007 | 122.0764 | 121.837 | 121.9578 | -0.27401
1773.6094 | 122.0993 | -121.9391 | 0.11444 | 1.4211e-13 | -0.03025 | 0.013825 | -0.0042801 | -0.012974 | 0.018416 | -0.23296 | 0.018012 | 0.018889 | 0.015598 | 0.034367 | 0.0092534 | 0.05141 | 0.005985 | 0.023639 | 0.10707 | 0.055306 | 0.27017 | 0.028521 | 0.055992 | 0.027831 | -0.015143 | 0.066194 | 0.14191 | -0.060928 | -0.16873 | 121.9676 | -0.007373 | 121.9905 | 121.9627 | -0.004882 | -0.059135 | 0.15573 | 121.7704 | -0.048247 | 121.9951 | 121.9239 | 0.15358 | 0.027466 | -0.17537 | 122.0462 | 121.9944 | 122.2093 | 121.9451 | -0.08592 | 122.0053 | 122.081 | 121.8782 | 121.9669 | -0.28317
1775.3438 | 122.1725 | -121.9162 | 0.10071 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0040665 | -0.012974 | 0.019057 | -0.2177 | 0.018225 | 0.018676 | 0.015598 | 0.034581 | 0.0092534 | 0.055988 | 0.010564 | 0.01906 | 0.10249 | 0.059885 | 0.26101 | 0.023942 | 0.055992 | 0.027831 | -0.015143 | 0.070773 | 0.15107 | -0.092979 | -0.15957 | 121.9401 | 0.001782 | 121.9722 | 121.9353 | -0.004882 | -0.040823 | 0.1603 | 121.7566 | -0.029935 | 121.9722 | 121.9011 | 0.14443 | 0.050357 | -0.19369 | 122.0187 | 121.9761 | 122.1772 | 121.9268 | -0.076766 | 121.987 | 122.0673 | 121.8232 | 121.944 | -0.26028
1777.0781 | 122.1863 | -121.9162 | 0.086975 | 1.4211e-13 | -0.03025 | 0.014039 | -0.0038527 | -0.013401 | 0.018843 | -0.23296 | 0.018012 | 0.018249 | 0.015598 | 0.034367 | 0.0090396 | 0.060567 | 0.010564 | 0.028217 | 0.10707 | 0.050727 | 0.27017 | 0.028521 | 0.06515 | 0.023253 | -0.010564 | 0.075351 | 0.15107 | -0.12045 | -0.15957 | 121.9447 | 0.020093 | 121.9768 | 121.9444 | -0.000304 | -0.036248 | 0.18319 | 121.7566 | -0.011624 | 121.9813 | 121.9056 | 0.14901 | 0.06409 | -0.20742 | 122.0233 | 121.9669 | 122.1864 | 121.9268 | -0.058454 | 121.9916 | 122.0673 | 121.7957 | 121.9395 | -0.24654
1778.7656 | 122.1634 | -121.9437 | 0.11444 | 1.4211e-13 | -0.030036 | 0.013825 | -0.0038527 | -0.013187 | 0.018629 | -0.24059 | 0.018225 | 0.018462 | 0.015171 | 0.034153 | 0.0092534 | 0.060567 | 0.010564 | 0.023639 | 0.11165 | 0.055306 | 0.26101 | 0.023942 | 0.060571 | 0.023253 | -0.015143 | 0.066194 | 0.16022 | -0.12045 | -0.16415 | 121.9676 | -0.002794 | 122.0042 | 121.9673 | -0.000303 | -0.059135 | 0.14657 | 121.7795 | -0.048247 | 122.0042 | 121.9285 | 0.14901 | 0.045781 | -0.23489 | 122.0553 | 121.999 | 122.2047 | 121.9542 | -0.090499 | 122.0099 | 122.1039 | 121.8232 | 121.9669 | -0.27859
1780.5156 | 122.2366 | -121.9025 | 0.10071 | 1.4211e-13 | -0.030036 | 0.013825 | -0.0038527 | -0.012974 | 0.018843 | -0.24059 | 0.018012 | 0.018889 | 0.015385 | 0.034367 | 0.009467 | 0.05141 | 0.005985 | 0.023639 | 0.11165 | 0.064464 | 0.26559 | 0.028521 | 0.055992 | 0.027831 | -0.010564 | 0.075351 | 0.16022 | -0.11587 | -0.15499 | 121.931 | 0.010939 | 121.9539 | 121.9261 | -0.004882 | -0.036244 | 0.16488 | 121.7475 | -0.025357 | 121.9585 | 121.8919 | 0.14443 | 0.059514 | -0.21658 | 122.0141 | 121.9669 | 122.1681 | 121.9085 | -0.072187 | 121.9778 | 122.0627 | 121.7866 | 121.9303 | -0.2557
1782.25 | 122.287 | -121.9345 | 0.07782 | 1.4211e-13 | -0.03025 | 0.013825 | -0.0040665 | -0.012974 | 0.018416 | -0.23296 | 0.018225 | 0.018676 | 0.015812 | 0.034795 | 0.009467 | 0.055988 | 0.005985 | 0.023639 | 0.10707 | 0.059885 | 0.26101 | 0.028521 | 0.055992 | 0.03241 | -0.015143 | 0.070773 | 0.15564 | -0.12961 | -0.15957 | 121.963 | 0.029248 | 121.9905 | 121.9581 | -0.004882 | -0.017935 | 0.18319 | 121.7749 | -0.007047 | 121.9905 | 121.9194 | 0.14443 | 0.077823 | -0.20743 | 122.0416 | 121.9944 | 122.1955 | 121.9405 | -0.049299 | 122.0053 | 122.0902 | 121.8049 | 121.9669 | -0.23739
1783.9219 | 122.2412 | -121.9025 | 0.082397 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0034253 | -0.013187 | 0.019057 | -0.22533 | 0.017798 | 0.018889 | 0.015598 | 0.034581 | 0.009467 | 0.060567 | 0.005985 | 0.023639 | 0.11165 | 0.055306 | 0.27017 | 0.023942 | 0.055992 | 0.03241 | -0.019721 | 0.066194 | 0.15107 | -0.12961 | -0.15957 | 121.9264 | 0.02925 | 121.963 | 121.9261 | -0.000303 | -0.027091 | 0.18777 | 121.7429 | -0.016203 | 121.9585 | 121.8827 | 0.13985 | 0.068668 | -0.212 | 122.0141 | 121.9578 | 122.1726 | 121.9085 | -0.058455 | 121.9687 | 122.0535 | 121.7729 | 121.9349 | -0.24197
1785.6719 | 122.2229 | -121.9254 | 0.09613 | 1.4211e-13 | -0.03025 | 0.013825 | -0.0038527 | -0.012974 | 0.018629 | -0.22533 | 0.018012 | 0.018462 | 0.016026 | 0.034367 | 0.0092534 | 0.060567 | 0.001407 | 0.014482 | 0.10249 | 0.055306 | 0.26559 | 0.023942 | 0.055992 | 0.03241 | -0.019721 | 0.066194 | 0.16022 | -0.13419 | -0.16415 | 121.9493 | 0.00636 | 121.9859 | 121.9398 | -0.00946 | -0.040824 | 0.16946 | 121.7612 | -0.029936 | 121.9813 | 121.9056 | 0.14443 | 0.064092 | -0.23032 | 122.0278 | 121.9807 | 122.1909 | 121.9268 | -0.072188 | 121.9915 | 122.0856 | 121.7912 | 121.9578 | -0.26028
1787.4219 | 122.1542 | -122.0032 | 0.11444 | 1.4211e-13 | -0.03025 | 0.014039 | -0.0036391 | -0.013401 | 0.018843 | -0.2177 | 0.018012 | 0.018676 | 0.015171 | 0.034367 | 0.009467 | 0.055988 | 0.010564 | 0.023639 | 0.11165 | 0.055306 | 0.26101 | 0.037679 | 0.055992 | 0.03241 | -0.015143 | 0.066194 | 0.15564 | -0.10214 | -0.16415 | 122.0409 | -0.002794 | 122.0592 | 122.0268 | -0.01404 | -0.059135 | 0.14657 | 121.839 | -0.048247 | 122.0592 | 121.988 | 0.14901 | 0.041202 | -0.21658 | 122.1148 | 122.0585 | 122.2642 | 122.0137 | -0.076762 | 122.0694 | 122.1588 | 121.901 | 122.0356 | -0.27859
1789.1094 | 122.2092 | -121.9528 | 0.11444 | 1.4211e-13 | -0.03025 | 0.014039 | -0.0036391 | -0.012974 | 0.018843 | -0.24059 | 0.018012 | 0.018676 | 0.015385 | 0.034795 | 0.0092534 | 0.05141 | 0.010564 | 0.01906 | 0.11165 | 0.055306 | 0.26559 | 0.023942 | 0.051413 | 0.03241 | -0.015143 | 0.070773 | 0.16022 | -0.12961 | -0.16415 | 121.9768 | -0.002794 | 122.0042 | 121.9719 | -0.004882 | -0.059135 | 0.15115 | 121.7887 | -0.043668 | 122.0042 | 121.9377 | 0.14901 | 0.045781 | -0.24405 | 122.0645 | 122.0081 | 122.2184 | 121.9634 | -0.090499 | 122.0236 | 122.113 | 121.8232 | 121.9852 | -0.27859
1790.875 | 122.1817 | -121.962 | 0.1236 | 1.4211e-13 | -0.030036 | 0.014039 | -0.0038527 | -0.01276 | 0.018629 | -0.22533 | 0.018012 | 0.018889 | 0.015598 | 0.034367 | 0.0090396 | 0.046831 | 0.001407 | 0.023639 | 0.10249 | 0.064464 | 0.26559 | 0.014784 | 0.055992 | 0.03241 | -0.015143 | 0.061616 | 0.15564 | -0.12961 | -0.15499 | 121.9768 | -0.021106 | 122.0088 | 121.9856 | 0.008855 | -0.059132 | 0.14199 | 121.807 | -0.06198 | 122.018 | 121.9468 | 0.13985 | 0.032047 | -0.2532 | 122.0645 | 122.0264 | 122.2276 | 121.9634 | -0.10881 | 122.0236 | 122.1176 | 121.8324 | 121.9944 | -0.27859
1792.6094 | 122.2366 | -121.962 | 0.086975 | 1.4211e-13 | -0.030036 | 0.014039 | -0.0038527 | -0.013187 | 0.018843 | -0.23296 | 0.018225 | 0.018676 | 0.015598 | 0.034795 | 0.0092534 | 0.055988 | 0.001407 | 0.023639 | 0.11165 | 0.064464 | 0.27017 | 0.023942 | 0.055992 | 0.03241 | -0.019721 | 0.070773 | 0.16022 | -0.12961 | -0.16415 | 121.9859 | 0.024672 | 122.018 | 121.9856 | -0.000303 | -0.022511 | 0.18319 | 121.7978 | -0.016202 | 122.018 | 121.9423 | 0.14443 | 0.073247 | -0.21658 | 122.0736 | 122.0264 | 122.2321 | 121.9634 | -0.063033 | 122.0327 | 122.1222 | 121.8324 | 121.9944 | -0.25112
1794.2969 | 122.1863 | -121.9894 | 0.10529 | 1.4211e-13 | -0.030036 | 0.014039 | -0.0038527 | -0.012974 | 0.018416 | -0.24059 | 0.018012 | 0.018462 | 0.015171 | 0.034581 | 0.009467 | 0.055988 | 0.005985 | 0.028217 | 0.10707 | 0.055306 | 0.26559 | 0.0331 | 0.055992 | 0.027831 | -0.015143 | 0.070773 | 0.15564 | -0.13419 | -0.15957 | 122.0225 | 0.001782 | 122.0454 | 122.0177 | -0.004883 | -0.04998 | 0.1603 | 121.8299 | -0.034513 | 122.0454 | 121.9743 | 0.14443 | 0.050357 | -0.23947 | 122.0965 | 122.0447 | 122.255 | 121.9954 | -0.072186 | 122.0602 | 122.1451 | 121.8553 | 122.0173 | -0.26486
1796.0469 | 122.1542 | -121.9803 | 0.13275 | 1.4211e-13 | -0.030036 | 0.014466 | -0.0038527 | -0.012974 | 0.018843 | -0.23296 | 0.018012 | 0.018249 | 0.015385 | 0.034581 | 0.0092534 | 0.055988 | 0.005985 | 0.01906 | 0.10249 | 0.055306 | 0.26559 | 0.019363 | 0.060571 | 0.036989 | -0.015143 | 0.057037 | 0.15564 | -0.12045 | -0.15499 | 121.9996 | -0.030261 | 122.0363 | 121.9993 | -0.000303 | -0.077445 | 0.13284 | 121.8253 | -0.075714 | 122.0409 | 121.9651 | 0.13985 | 0.022892 | -0.2532 | 122.0828 | 122.0356 | 122.2459 | 121.9863 | -0.11339 | 122.0373 | 122.1359 | 121.8598 | 122.0173 | -0.28774
1797.7344 | 122.2916 | -121.962 | 0.086975 | 1.4211e-13 | -0.03025 | 0.013825 | -0.0038527 | -0.01276 | 0.018843 | -0.24059 | 0.018012 | 0.018676 | 0.015598 | 0.034367 | 0.0092534 | 0.05141 | 0.001407 | 0.023639 | 0.10249 | 0.055306 | 0.27017 | 0.019363 | 0.051413 | 0.027831 | -0.010564 | 0.066194 | 0.15564 | -0.12961 | -0.15957 | 121.9813 | 0.015515 | 122.0134 | 121.9856 | 0.004276 | -0.031669 | 0.18319 | 121.8024 | -0.020781 | 122.0134 | 121.9514 | 0.14901 | 0.068668 | -0.21658 | 122.0645 | 122.0173 | 122.2321 | 121.9634 | -0.067612 | 122.0282 | 122.1176 | 121.8324 | 121.9898 | -0.24654
1799.4844 | 122.1634 | -121.9757 | 0.1236 | 1.4211e-13 | -0.03025 | 0.013825 | -0.0038527 | -0.013187 | 0.018843 | -0.24059 | 0.018225 | 0.018462 | 0.015385 | 0.034153 | 0.0090396 | 0.05141 | 0.010564 | 0.01906 | 0.11165 | 0.055306 | 0.25643 | 0.023942 | 0.055992 | 0.027831 | -0.015143 | 0.066194 | 0.15107 | -0.097557 | -0.15499 | 121.9997 | -0.011949 | 122.0271 | 121.9948 | -0.004882 | -0.06829 | 0.13284 | 121.8207 | -0.057402 | 122.0317 | 121.9606 | 0.13985 | 0.027469 | -0.22115 | 122.0874 | 122.031 | 122.2321 | 121.9863 | -0.099654 | 122.0419 | 122.1268 | 121.8782 | 122.0035 | -0.27859
1801.1562 | 122.3007 | -121.9574 | 0.07782 | 1.4211e-13 | -0.03025 | 0.013825 | -0.0038527 | -0.013187 | 0.018843 | -0.24822 | 0.018225 | 0.018676 | 0.016026 | 0.034581 | 0.009467 | 0.05141 | 0.005985 | 0.014482 | 0.11165 | 0.059885 | 0.27017 | 0.023942 | 0.055992 | 0.023253 | -0.019721 | 0.066194 | 0.15564 | -0.12503 | -0.15957 | 121.9813 | 0.033827 | 122.0088 | 121.9719 | -0.00946 | -0.017935 | 0.19235 | 121.7978 | -0.011626 | 122.0134 | 121.9377 | 0.13985 | 0.077823 | -0.20285 | 122.069 | 122.0173 | 122.2276 | 121.9634 | -0.053878 | 122.0236 | 122.113 | 121.8324 | 121.9806 | -0.23739
1802.9062 | 122.3099 | -121.9666 | 0.10071 | 1.4211e-13 | -0.03025 | 0.013611 | -0.0038527 | -0.013401 | 0.018416 | -0.24059 | 0.018012 | 0.018462 | 0.015598 | 0.034795 | 0.009467 | 0.060567 | 0.005985 | 0.014482 | 0.10249 | 0.055306 | 0.26559 | 0.019363 | 0.055992 | 0.03241 | -0.015143 | 0.070773 | 0.15107 | -0.12961 | -0.15957 | 121.9859 | 0.001782 | 122.0271 | 121.981 | -0.004881 | -0.045402 | 0.16488 | 121.807 | -0.029935 | 122.0225 | 121.9514 | 0.14443 | 0.050357 | -0.23031 | 122.069 | 122.0219 | 122.2321 | 121.9725 | -0.081345 | 122.0373 | 122.1176 | 121.8369 | 121.999 | -0.26028
1804.5938 | 122.1863 | -121.9849 | 0.1236 | 1.4211e-13 | -0.030036 | 0.013611 | -0.0040665 | -0.012974 | 0.018843 | -0.22533 | 0.017584 | 0.018676 | 0.015598 | 0.034367 | 0.0090396 | 0.05141 | 0.010564 | 0.014482 | 0.10707 | 0.055306 | 0.26101 | 0.028521 | 0.051413 | 0.023253 | -0.019721 | 0.066194 | 0.16022 | -0.13419 | -0.15957 | 122.0134 | -0.016528 | 122.0363 | 121.9993 | -0.014039 | -0.06829 | 0.13741 | 121.8253 | -0.057402 | 122.0363 | 121.9651 | 0.13985 | 0.036626 | -0.25778 | 122.0919 | 122.0402 | 122.2459 | 121.9954 | -0.095075 | 122.0511 | 122.1451 | 121.8507 | 122.0081 | -0.28317
1806.3438 | 122.1451 | -122.0261 | 0.12817 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0036391 | -0.012974 | 0.018629 | -0.2177 | 0.018225 | 0.018462 | 0.015598 | 0.034581 | 0.009467 | 0.05141 | 0.010564 | 0.023639 | 0.11165 | 0.055306 | 0.26559 | 0.023942 | 0.055992 | 0.03241 | -0.015143 | 0.061616 | 0.15107 | -0.11587 | -0.15957 | 122.05 | -0.016527 | 122.0775 | 122.0497 | -0.000303 | -0.072868 | 0.13741 | 121.8665 | -0.066558 | 122.0821 | 122.0109 | 0.14443 | 0.022891 | -0.24405 | 122.1377 | 122.0814 | 122.2916 | 122.0366 | -0.10423 | 122.0877 | 122.1771 | 121.9102 | 122.0585 | -0.28774
1808.0938 | 122.168 | -122.0261 | 0.11444 | 1.4211e-13 | -0.03025 | 0.014039 | -0.0040665 | -0.01276 | 0.018629 | -0.23296 | 0.018225 | 0.018249 | 0.015812 | 0.034581 | 0.0092534 | 0.05141 | 0.001407 | 0.028217 | 0.11165 | 0.055306 | 0.26559 | 0.028521 | 0.055992 | 0.027831 | -0.015143 | 0.070773 | 0.15564 | -0.12961 | -0.16873 | 122.0546 | -0.002794 | 122.0775 | 122.0543 | -0.000304 | -0.059135 | 0.15115 | 121.8573 | -0.043668 | 122.0821 | 122.0109 | 0.15358 | 0.041202 | -0.24405 | 122.1377 | 122.0814 | 122.2916 | 122.0275 | -0.08592 | 122.0968 | 122.1817 | 121.8965 | 122.0539 | -0.28317
1809.8438 | 122.2824 | -122.0078 | 0.10071 | 1.4211e-13 | -0.03025 | 0.014039 | -0.0038527 | -0.013187 | 0.018416 | -0.23296 | 0.018439 | 0.018462 | 0.015598 | 0.034367 | 0.009467 | 0.055988 | 0.005985 | 0.023639 | 0.1208 | 0.055306 | 0.26101 | 0.023942 | 0.055992 | 0.027831 | -0.010564 | 0.066194 | 0.15107 | -0.12503 | -0.16415 | 122.0317 | 0.020096 | 122.0637 | 122.0314 | -0.000303 | -0.045402 | 0.1603 | 121.8436 | -0.034514 | 122.0637 | 121.9972 | 0.15358 | 0.050357 | -0.22574 | 122.1286 | 122.0631 | 122.2688 | 122.0137 | -0.076766 | 122.0739 | 122.1588 | 121.8827 | 122.0356 | -0.26486
1811.5781 | 122.1909 | -122.0718 | 0.11444 | 1.4211e-13 | -0.030463 | 0.013825 | -0.0038527 | -0.012974 | 0.018629 | -0.24059 | 0.018012 | 0.018462 | 0.015171 | 0.034581 | 0.0092534 | 0.05141 | 0.005985 | 0.023639 | 0.11165 | 0.055306 | 0.26101 | 0.019363 | 0.055992 | 0.027831 | -0.010564 | 0.066194 | 0.15107 | -0.097557 | -0.16415 | 122.0912 | -0.002794 | 122.1232 | 122.0955 | 0.004276 | -0.059135 | 0.14657 | 121.9077 | -0.048247 | 122.1278 | 122.0613 | 0.15358 | 0.036624 | -0.212 | 122.1835 | 122.1271 | 122.3328 | 122.0778 | -0.095078 | 122.138 | 122.2229 | 121.9743 | 122.0997 | -0.27859
1813.2656 | 122.319 | -121.9849 | 0.07782 | 1.4211e-13 | -0.029822 | 0.014252 | -0.0036391 | -0.013401 | 0.018843 | -0.24059 | 0.018012 | 0.018462 | 0.015598 | 0.034367 | 0.009467 | 0.055988 | 0.010564 | 0.023639 | 0.11622 | 0.055306 | 0.27017 | 0.028521 | 0.051413 | 0.03241 | -0.019721 | 0.066194 | 0.15107 | -0.11129 | -0.15957 | 122.0134 | 0.038405 | 122.0409 | 122.0085 | -0.004882 | -0.022514 | 0.19235 | 121.8253 | -0.011626 | 122.0363 | 121.9651 | 0.13985 | 0.073245 | -0.18911 | 122.1011 | 122.0402 | 122.255 | 121.9954 | -0.049299 | 122.0511 | 122.1359 | 121.8736 | 122.0173 | -0.23739
1815.0156 | 122.3145 | -121.9757 | 0.10071 | 1.4211e-13 | -0.03025 | 0.013825 | -0.0038527 | -0.013187 | 0.018629 | -0.24059 | 0.018012 | 0.018462 | 0.015385 | 0.034581 | 0.0090396 | 0.055988 | 0.005985 | 0.01906 | 0.1208 | 0.069043 | 0.26559 | 0.028521 | 0.051413 | 0.027831 | -0.019721 | 0.066194 | 0.16022 | -0.12503 | -0.16873 | 122.0042 | 0.020096 | 122.0317 | 121.9948 | -0.009461 | -0.031665 | 0.16488 | 121.807 | -0.034514 | 122.0271 | 121.956 | 0.14901 | 0.059514 | -0.22574 | 122.0965 | 122.0448 | 122.2413 | 121.9817 | -0.072187 | 122.0419 | 122.1359 | 121.8507 | 122.0035 | -0.26944
1816.7031 | 122.287 | -122.0352 | 0.086975 | 1.4211e-13 | -0.030036 | 0.013611 | -0.0036391 | -0.01276 | 0.018629 | -0.23296 | 0.018012 | 0.018676 | 0.015385 | 0.034581 | 0.009467 | 0.060567 | 0.010564 | 0.028217 | 0.11165 | 0.064464 | 0.27017 | 0.023942 | 0.055992 | 0.03241 | -0.010564 | 0.066194 | 0.15107 | -0.12961 | -0.15957 | 122.0592 | 0.024672 | 122.0958 | 122.0634 | 0.004275 | -0.022511 | 0.18319 | 121.8756 | -0.020781 | 122.0912 | 122.0247 | 0.14901 | 0.06409 | -0.21658 | 122.1469 | 122.0997 | 122.3054 | 122.0458 | -0.063033 | 122.1014 | 122.1863 | 121.9056 | 122.0676 | -0.24654
1818.4531 | 122.2137 | -122.049 | 0.10986 | 1.4211e-13 | -0.030036 | 0.013825 | -0.0040665 | -0.012974 | 0.019057 | -0.23296 | 0.018225 | 0.018676 | 0.015598 | 0.034581 | 0.0090396 | 0.055988 | 0.005985 | 0.01906 | 0.11165 | 0.059885 | 0.26101 | 0.023942 | 0.051413 | 0.036989 | -0.015143 | 0.061616 | 0.15564 | -0.12503 | -0.16873 | 122.0729 | 0.001784 | 122.1049 | 122.068 | -0.004882 | -0.049978 | 0.15115 | 121.8802 | -0.048247 | 122.1004 | 122.0338 | 0.15358 | 0.04578 | -0.23489 | 122.1606 | 122.1088 | 122.31 | 122.0549 | -0.085921 | 122.1106 | 122.2046 | 121.9239 | 122.0859 | -0.27859
1820.1406 | 122.2229 | -122.0673 | 0.12817 | 1.4211e-13 | -0.03025 | 0.013825 | -0.0040665 | -0.013187 | 0.018843 | -0.22533 | 0.018225 | 0.018676 | 0.015812 | 0.034581 | 0.009467 | 0.060567 | 0.005985 | 0.023639 | 0.11165 | 0.059885 | 0.27017 | 0.023942 | 0.055992 | 0.027831 | -0.010564 | 0.061616 | 0.15564 | -0.13876 | -0.15957 | 122.0912 | -0.016527 | 122.1278 | 122.0909 | -0.000303 | -0.068289 | 0.14199 | 121.9077 | -0.066558 | 122.1233 | 122.0567 | 0.14901 | 0.027469 | -0.26694 | 122.1789 | 122.1271 | 122.3374 | 122.0732 | -0.10423 | 122.1289 | 122.2229 | 121.9285 | 122.0951 | -0.28774
1821.8906 | 122.3328 | -122.0032 | 0.082397 | 1.4211e-13 | -0.03025 | 0.013611 | -0.0038527 | -0.012974 | 0.018416 | -0.24822 | 0.018439 | 0.018249 | 0.015598 | 0.034367 | 0.009467 | 0.05141 | 0.005985 | 0.028217 | 0.10707 | 0.055306 | 0.26101 | 0.028521 | 0.051413 | 0.036989 | -0.015143 | 0.052459 | 0.16022 | -0.12503 | -0.16415 | 122.0317 | 0.024671 | 122.0546 | 122.0314 | -0.000304 | -0.027091 | 0.17861 | 121.839 | -0.029938 | 122.0546 | 121.988 | 0.14901 | 0.077825 | -0.20743 | 122.1102 | 122.0585 | 122.2642 | 122.0092 | -0.053876 | 122.0556 | 122.1634 | 121.8781 | 122.0402 | -0.24655
1823.6406 | 122.2137 | -122.0947 | 0.11902 | 1.4211e-13 | -0.030463 | 0.014039 | -0.0040665 | -0.013187 | 0.019057 | -0.23296 | 0.017798 | 0.018462 | 0.016026 | 0.034581 | 0.0090396 | 0.055988 | 0.015142 | 0.01906 | 0.1208 | 0.050727 | 0.26559 | 0.023942 | 0.060571 | 0.03241 | -0.019721 | 0.066194 | 0.15564 | -0.092979 | -0.16415 | 122.1187 | 0.001785 | 122.1507 | 122.1138 | -0.004882 | -0.068292 | 0.14657 | 121.9306 | -0.052825 | 122.1553 | 122.075 | 0.14443 | 0.036624 | -0.212 | 122.2155 | 122.1455 | 122.3603 | 122.1099 | -0.095077 | 122.1609 | 122.2504 | 122.0017 | 122.1271 | -0.28317
1825.3906 | 122.2961 | -122.0352 | 0.09613 | 1.4211e-13 | -0.029609 | 0.013825 | -0.0036391 | -0.012974 | 0.018629 | -0.24822 | 0.018225 | 0.018462 | 0.014957 | 0.034367 | 0.0090396 | 0.055988 | 0.005985 | 0.028217 | 0.11622 | 0.059885 | 0.27017 | 0.023942 | 0.051413 | 0.027831 | -0.010564 | 0.070773 | 0.16022 | -0.13876 | -0.15957 | 122.0592 | 0.020095 | 122.0912 | 122.0634 | 0.004275 | -0.036245 | 0.17404 | 121.8756 | -0.025357 | 122.0866 | 122.0247 | 0.14901 | 0.064092 | -0.23489 | 122.1514 | 122.0951 | 122.3054 | 122.0412 | -0.072188 | 122.106 | 122.1954 | 121.8965 | 122.063 | -0.2557
1827.125 | 122.2824 | -122.0627 | 0.10986 | 1.4211e-13 | -0.030463 | 0.013825 | -0.0036391 | -0.013187 | 0.018629 | -0.22533 | 0.018012 | 0.019103 | 0.015598 | 0.034153 | 0.0090396 | 0.055988 | 0.010564 | 0.023639 | 0.11165 | 0.069043 | 0.26101 | 0.023942 | 0.055992 | 0.03241 | -0.010564 | 0.066194 | 0.16022 | -0.13419 | -0.16415 | 122.0866 | 0.001784 | 122.1187 | 122.0863 | -0.000303 | -0.04082 | 0.15115 | 121.8985 | -0.043669 | 122.1187 | 122.0521 | 0.15358 | 0.050359 | -0.24405 | 122.1743 | 122.1317 | 122.3237 | 122.0732 | -0.085921 | 122.1289 | 122.2229 | 121.9285 | 122.0951 | -0.27401
1828.8594 | 122.2458 | -122.0764 | 0.10986 | 1.4211e-13 | -0.029609 | 0.013825 | -0.0038527 | -0.013187 | 0.018629 | -0.22533 | 0.018012 | 0.018676 | 0.015598 | 0.034367 | 0.0090396 | 0.055988 | 0.010564 | 0.01906 | 0.11165 | 0.059885 | 0.26101 | 0.023942 | 0.046835 | 0.027831 | -0.010564 | 0.061616 | 0.15564 | -0.13419 | -0.15957 | 122.1004 | 0.001784 | 122.1324 | 122.0955 | -0.004882 | -0.049978 | 0.15115 | 121.9168 | -0.048247 | 122.1233 | 122.0659 | 0.14901 | 0.04578 | -0.24405 | 122.1881 | 122.1363 | 122.3374 | 122.087 | -0.085921 | 122.138 | 122.2321 | 121.9422 | 122.1042 | -0.26943
1830.5469 | 122.2458 | -122.0718 | 0.10529 | 1.4211e-13 | -0.03025 | 0.013825 | -0.0038527 | -0.013187 | 0.018629 | -0.23296 | 0.018225 | 0.018249 | 0.015598 | 0.034367 | 0.0092534 | 0.055988 | 0.005985 | 0.023639 | 0.10707 | 0.059885 | 0.26559 | 0.019363 | 0.055992 | 0.036989 | -0.010564 | 0.070773 | 0.15564 | -0.12045 | -0.16415 | 122.0912 | 0.001782 | 122.1278 | 122.0955 | 0.004276 | -0.045401 | 0.1603 | 121.9077 | -0.034513 | 122.1278 | 122.0613 | 0.15358 | 0.050357 | -0.22574 | 122.1789 | 122.1317 | 122.3374 | 122.0778 | -0.085923 | 122.1426 | 122.2275 | 121.9514 | 122.1088 | -0.26943
1832.2812 | 122.2641 | -122.0856 | 0.10529 | 1.4211e-13 | -0.03025 | 0.013825 | -0.0038527 | -0.013401 | 0.018843 | -0.23296 | 0.018225 | 0.018676 | 0.015598 | 0.034367 | 0.0090396 | 0.05141 | 0.010564 | 0.028217 | 0.11165 | 0.059885 | 0.27017 | 0.019363 | 0.051413 | 0.03241 | -0.019721 | 0.061616 | 0.15107 | -0.12045 | -0.16415 | 122.1049 | 0.006361 | 122.137 | 122.1138 | 0.008854 | -0.045401 | 0.16488 | 121.9214 | -0.04367 | 122.137 | 122.0658 | 0.14443 | 0.045779 | -0.22574 | 122.1972 | 122.1455 | 122.3557 | 122.0961 | -0.085923 | 122.1472 | 122.2366 | 121.9651 | 122.118 | -0.26943
1834.0312 | 122.2961 | -122.0581 | 0.10986 | 1.4211e-13 | -0.030036 | 0.013825 | -0.0040665 | -0.013401 | 0.018629 | -0.24059 | 0.018012 | 0.018889 | 0.015598 | 0.034367 | 0.009467 | 0.055988 | 0.001407 | 0.023639 | 0.10707 | 0.059885 | 0.26559 | 0.028521 | 0.055992 | 0.023253 | -0.015143 | 0.070773 | 0.15564 | -0.13419 | -0.16415 | 122.0866 | -0.002795 | 122.1141 | 122.0817 | -0.004882 | -0.049978 | 0.15573 | 121.894 | -0.03909 | 122.1141 | 122.043 | 0.14901 | 0.04578 | -0.24405 | 122.1652 | 122.118 | 122.3237 | 122.0595 | -0.081342 | 122.1289 | 122.2137 | 121.9239 | 122.0814 | -0.27401
1835.7188 | 122.2321 | -122.0993 | 0.15106 | 1.4211e-13 | -0.030463 | 0.014039 | -0.0042801 | -0.012974 | 0.018629 | -0.22533 | 0.018012 | 0.018676 | 0.015598 | 0.034367 | 0.0096806 | 0.060567 | 0.001407 | 0.01906 | 0.10707 | 0.059885 | 0.26559 | 0.019363 | 0.055992 | 0.027831 | -0.010564 | 0.070773 | 0.16022 | -0.13876 | -0.16415 | 122.1187 | -0.043994 | 122.1599 | 122.1184 | -0.000303 | -0.091177 | 0.11453 | 121.9352 | -0.080289 | 122.1553 | 122.0887 | 0.15358 | 0.00916 | -0.28983 | 122.2064 | 122.1592 | 122.3649 | 122.1007 | -0.1317 | 122.1701 | 122.2595 | 121.9605 | 122.1271 | -0.31521
1837.4688 | 122.2458 | -122.0993 | 0.1236 | 1.4211e-13 | -0.03025 | 0.014039 | -0.0036391 | -0.013187 | 0.018843 | -0.23296 | 0.018225 | 0.018462 | 0.015598 | 0.034367 | 0.009467 | 0.055988 | 0.010564 | 0.032795 | 0.10707 | 0.059885 | 0.26101 | 0.023942 | 0.051413 | 0.027831 | -0.015143 | 0.070773 | 0.16022 | -0.097557 | -0.16415 | 122.1232 | -0.016528 | 122.1553 | 122.1321 | 0.008853 | -0.063711 | 0.13741 | 121.9352 | -0.052823 | 122.1507 | 122.0842 | 0.14901 | 0.036626 | -0.22115 | 122.2064 | 122.1592 | 122.3603 | 122.1099 | -0.099654 | 122.1701 | 122.2595 | 122.0017 | 122.1271 | -0.28774
1839.1562 | 122.2412 | -122.0947 | 0.13275 | 1.4211e-13 | -0.03025 | 0.014039 | -0.0038527 | -0.013187 | 0.018629 | -0.2177 | 0.018012 | 0.018676 | 0.015385 | 0.034367 | 0.009467 | 0.055988 | 0.005985 | 0.023639 | 0.11165 | 0.050727 | 0.26559 | 0.023942 | 0.051413 | 0.023253 | -0.019721 | 0.066194 | 0.16022 | -0.092979 | -0.16415 | 122.1187 | -0.021104 | 122.1507 | 122.1184 | -0.000303 | -0.082024 | 0.13284 | 121.9306 | -0.066557 | 122.1461 | 122.075 | 0.14443 | 0.027471 | -0.22573 | 122.2064 | 122.1455 | 122.3603 | 122.1007 | -0.10881 | 122.1609 | 122.2549 | 122.0017 | 122.118 | -0.2969
1840.9219 | 122.3465 | -122.0718 | 0.086975 | 1.4211e-13 | -0.03025 | 0.013825 | -0.0038527 | -0.012974 | 0.018843 | -0.24059 | 0.018012 | 0.018249 | 0.015598 | 0.034581 | 0.0090396 | 0.055988 | 0.001407 | 0.023639 | 0.11165 | 0.059885 | 0.26559 | 0.023942 | 0.055992 | 0.03241 | -0.010564 | 0.070773 | 0.16022 | -0.13419 | -0.16873 | 122.0958 | 0.024672 | 122.1278 | 122.0955 | -0.000303 | -0.02709 | 0.17861 | 121.9031 | -0.016202 | 122.1278 | 122.0613 | 0.15816 | 0.073247 | -0.22116 | 122.1835 | 122.1317 | 122.3374 | 122.0732 | -0.063033 | 122.1426 | 122.2321 | 121.9377 | 122.1042 | -0.2557
1842.6562 | 122.3099 | -122.0993 | 0.10986 | 1.4211e-13 | -0.029822 | 0.013825 | -0.0040665 | -0.013401 | 0.019057 | -0.24059 | 0.018012 | 0.018462 | 0.015812 | 0.034581 | 0.0092534 | 0.055988 | 0.005985 | 0.023639 | 0.11165 | 0.064464 | 0.26559 | 0.028521 | 0.051413 | 0.036989 | -0.019721 | 0.066194 | 0.15564 | -0.12961 | -0.16415 | 122.1278 | 0.001784 | 122.1553 | 122.1229 | -0.004882 | -0.045399 | 0.15573 | 121.9352 | -0.043669 | 122.1507 | 122.0796 | 0.14443 | 0.04578 | -0.23947 | 122.211 | 122.1638 | 122.3649 | 122.1053 | -0.081342 | 122.1655 | 122.2549 | 121.9697 | 122.1363 | -0.27401
1844.4062 | 122.374 | -122.081 | 0.086975 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0038527 | -0.013187 | 0.018843 | -0.24059 | 0.018012 | 0.018889 | 0.015598 | 0.034367 | 0.0092534 | 0.055988 | 0.005985 | 0.028217 | 0.11165 | 0.059885 | 0.26101 | 0.014784 | 0.060571 | 0.03241 | -0.010564 | 0.061616 | 0.15564 | -0.12961 | -0.15957 | 122.0958 | 0.024672 | 122.137 | 122.1092 | 0.013433 | -0.02709 | 0.17404 | 121.9214 | -0.025359 | 122.1416 | 122.0704 | 0.14901 | 0.068668 | -0.21658 | 122.1926 | 122.1409 | 122.342 | 122.087 | -0.072191 | 122.1426 | 122.2366 | 121.9514 | 122.1134 | -0.24654
1846.0781 | 122.2321 | -122.1085 | 0.13275 | 1.4211e-13 | -0.029822 | 0.013825 | -0.0038527 | -0.01276 | 0.018843 | -0.23296 | 0.018012 | 0.018462 | 0.015385 | 0.034367 | 0.0090396 | 0.055988 | 0.005985 | 0.014482 | 0.1208 | 0.055306 | 0.27475 | 0.023942 | 0.046835 | 0.03241 | -0.015143 | 0.066194 | 0.16022 | -0.12045 | -0.15957 | 122.1324 | -0.011947 | 122.1644 | 122.1229 | -0.00946 | -0.077445 | 0.14199 | 121.9489 | -0.066557 | 122.1553 | 122.0933 | 0.14443 | 0.027471 | -0.2532 | 122.2293 | 122.1638 | 122.3832 | 122.1144 | -0.10881 | 122.1747 | 122.2687 | 121.988 | 122.1409 | -0.29232
1847.8125 | 122.2687 | -122.1085 | 0.11902 | 1.4211e-13 | -0.03025 | 0.013825 | -0.0038527 | -0.013187 | 0.018629 | -0.22533 | 0.018225 | 0.018889 | 0.015385 | 0.034795 | 0.0090396 | 0.055988 | 0.001407 | 0.023639 | 0.11165 | 0.064464 | 0.27017 | 0.0331 | 0.051413 | 0.027831 | -0.019721 | 0.066194 | 0.15107 | -0.12045 | -0.16415 | 122.1416 | -0.007372 | 122.1644 | 122.1321 | -0.009461 | -0.054555 | 0.15115 | 121.9443 | -0.052825 | 122.1599 | 122.0887 | 0.14443 | 0.032046 | -0.23947 | 122.2201 | 122.1729 | 122.3786 | 122.1099 | -0.085919 | 122.1747 | 122.2595 | 121.988 | 122.1363 | -0.28317
1849.5625 | 122.3785 | -122.0627 | 0.09613 | 1.4211e-13 | -0.030036 | 0.014252 | -0.0042801 | -0.013615 | 0.018629 | -0.24059 | 0.018012 | 0.018676 | 0.015598 | 0.034367 | 0.0092534 | 0.05141 | 0.015142 | 0.023639 | 0.097912 | 0.059885 | 0.26559 | 0.028521 | 0.055992 | 0.03241 | -0.019721 | 0.070773 | 0.15564 | -0.12961 | -0.16415 | 122.0912 | 0.001782 | 122.1141 | 122.0863 | -0.004882 | -0.036245 | 0.16946 | 121.8985 | -0.025357 | 122.1187 | 122.043 | 0.14443 | 0.059513 | -0.22574 | 122.1606 | 122.1226 | 122.3283 | 122.0778 | -0.067609 | 122.1335 | 122.2183 | 121.9331 | 122.0951 | -0.26028
1851.25 | 122.2824 | -122.113 | 0.09613 | 1.4211e-13 | -0.030036 | 0.014039 | -0.0038527 | -0.013187 | 0.018843 | -0.23296 | 0.018012 | 0.018676 | 0.015385 | 0.034795 | 0.009467 | 0.055988 | 0.010564 | 0.032795 | 0.10707 | 0.064464 | 0.26559 | 0.019363 | 0.055992 | 0.03241 | -0.010564 | 0.070773 | 0.16022 | -0.12961 | -0.16873 | 122.1324 | 0.010938 | 122.169 | 122.1458 | 0.013432 | -0.031666 | 0.16946 | 121.9443 | -0.025357 | 122.169 | 122.1025 | 0.15816 | 0.064092 | -0.22574 | 122.2201 | 122.1775 | 122.3786 | 122.1236 | -0.076767 | 122.1838 | 122.2733 | 121.9834 | 122.1454 | -0.26486
1852.9844 | 122.2687 | -122.1039 | 0.11444 | 1.4211e-13 | -0.03025 | 0.014252 | -0.0036391 | -0.013187 | 0.018416 | -0.23296 | 0.018012 | 0.018676 | 0.015598 | 0.034367 | 0.0092534 | 0.065145 | 0.001407 | 0.028217 | 0.11165 | 0.055306 | 0.27017 | 0.028521 | 0.051413 | 0.027831 | -0.010564 | 0.075351 | 0.16022 | -0.13419 | -0.15957 | 122.1324 | -0.002794 | 122.169 | 122.1321 | -0.000304 | -0.059135 | 0.15573 | 121.9443 | -0.03909 | 122.1553 | 122.0933 | 0.14901 | 0.045781 | -0.24863 | 122.2155 | 122.1592 | 122.374 | 122.1053 | -0.08592 | 122.1792 | 122.2641 | 121.9697 | 122.1317 | -0.27401
1854.7344 | 122.3602 | -122.0764 | 0.10529 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0038527 | -0.012974 | 0.018629 | -0.24059 | 0.018225 | 0.018462 | 0.015598 | 0.034581 | 0.0092534 | 0.05141 | 0.001407 | 0.023639 | 0.11165 | 0.064464 | 0.26559 | 0.023942 | 0.060571 | 0.03241 | -0.010564 | 0.066194 | 0.16022 | -0.13419 | -0.16415 | 122.1004 | 0.006361 | 122.1278 | 122.1001 | -0.000303 | -0.040822 | 0.1603 | 121.9123 | -0.039092 | 122.137 | 122.0659 | 0.15358 | 0.054936 | -0.23947 | 122.1881 | 122.1409 | 122.342 | 122.0778 | -0.081344 | 122.1426 | 122.2366 | 121.9422 | 122.1088 | -0.26943
1856.4688 | 122.3694 | -122.1313 | 0.10529 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0038527 | -0.013401 | 0.019057 | -0.23296 | 0.018012 | 0.018462 | 0.015598 | 0.034581 | 0.0090396 | 0.055988 | 0.005985 | 0.023639 | 0.11165 | 0.055306 | 0.26559 | 0.023942 | 0.051413 | 0.036989 | -0.010564 | 0.070773 | 0.16022 | -0.12961 | -0.16415 | 122.1553 | 0.006361 | 122.1873 | 122.155 | -0.000303 | -0.04998 | 0.1603 | 121.9672 | -0.034513 | 122.1828 | 122.1208 | 0.15358 | 0.054936 | -0.23489 | 122.243 | 122.1867 | 122.3969 | 122.1373 | -0.081344 | 122.2021 | 122.2916 | 122.0017 | 122.1683 | -0.26943
1858.1406 | 122.3328 | -122.1176 | 0.11444 | 1.4211e-13 | -0.03025 | 0.013825 | -0.0040665 | -0.012974 | 0.018629 | -0.24059 | 0.018225 | 0.018462 | 0.015812 | 0.034367 | 0.008826 | 0.060567 | 0.010564 | 0.01906 | 0.11165 | 0.055306 | 0.27017 | 0.023942 | 0.046835 | 0.03241 | -0.015143 | 0.066194 | 0.1648 | -0.12503 | -0.16415 | 122.1416 | -0.002794 | 122.1782 | 122.1367 | -0.004882 | -0.059135 | 0.15573 | 121.9535 | -0.048247 | 122.1645 | 122.1025 | 0.14901 | 0.050359 | -0.23947 | 122.2293 | 122.1729 | 122.3878 | 122.1282 | -0.090499 | 122.1838 | 122.2824 | 121.9926 | 122.15 | -0.27859
1859.8906 | 122.3831 | -122.0947 | 0.10529 | 1.4211e-13 | -0.03025 | 0.014466 | -0.0036391 | -0.012974 | 0.018629 | -0.24059 | 0.018012 | 0.018676 | 0.015171 | 0.034581 | 0.0092534 | 0.055988 | 0.010564 | 0.028217 | 0.11622 | 0.055306 | 0.26559 | 0.023942 | 0.051413 | 0.03241 | -0.010564 | 0.066194 | 0.15564 | -0.083821 | -0.16415 | 122.1187 | 0.010939 | 122.1507 | 122.1229 | 0.004275 | -0.04998 | 0.1603 | 121.9306 | -0.039092 | 122.1461 | 122.0842 | 0.15358 | 0.050357 | -0.18911 | 122.211 | 122.15 | 122.3603 | 122.1053 | -0.081344 | 122.1609 | 122.2504 | 122.0109 | 122.1271 | -0.26943
1861.6406 | 122.3145 | -122.1359 | 0.10529 | 1.4211e-13 | -0.030036 | 0.013825 | -0.0038527 | -0.013401 | 0.018843 | -0.24059 | 0.018012 | 0.018462 | 0.015171 | 0.034581 | 0.0090396 | 0.060567 | 0.005985 | 0.01906 | 0.11165 | 0.064464 | 0.27017 | 0.028521 | 0.055992 | 0.03241 | -0.015143 | 0.066194 | 0.16022 | -0.12503 | -0.17331 | 122.1644 | 0.006361 | 122.1965 | 122.155 | -0.009461 | -0.040822 | 0.16488 | 121.9626 | -0.039092 | 122.1919 | 122.1208 | 0.15816 | 0.054936 | -0.23031 | 122.2476 | 122.2004 | 122.4061 | 122.1419 | -0.076765 | 122.2021 | 122.2961 | 122.0109 | 122.1683 | -0.27859
1863.3281 | 122.4152 | -122.0901 | 0.10071 | 1.4211e-13 | -0.030036 | 0.014039 | -0.0036391 | -0.013187 | 0.018629 | -0.24822 | 0.017798 | 0.018889 | 0.015598 | 0.034581 | 0.0092534 | 0.055988 | 0.005985 | 0.023639 | 0.11165 | 0.059885 | 0.27017 | 0.028521 | 0.051413 | 0.03241 | -0.010564 | 0.066194 | 0.15564 | -0.13419 | -0.16415 | 122.1187 | 0.010939 | 122.1461 | 122.1138 | -0.004882 | -0.040823 | 0.16946 | 121.926 | -0.034514 | 122.1416 | 122.0796 | 0.15358 | 0.054935 | -0.23489 | 122.2018 | 122.15 | 122.3603 | 122.0961 | -0.072187 | 122.1563 | 122.2458 | 121.956 | 122.1226 | -0.26486
1865.0781 | 122.4014 | -122.1039 | 0.07782 | 1.4211e-13 | -0.03025 | 0.013825 | -0.0038527 | -0.012974 | 0.018416 | -0.22533 | 0.017798 | 0.018462 | 0.015598 | 0.034367 | 0.0092534 | 0.060567 | 0.005985 | 0.023639 | 0.11165 | 0.069043 | 0.26101 | 0.023942 | 0.060571 | 0.03241 | -0.010564 | 0.061616 | 0.16022 | -0.12961 | -0.16415 | 122.1278 | 0.033827 | 122.1644 | 122.1275 | -0.000303 | -0.008777 | 0.18319 | 121.9397 | -0.016204 | 122.1645 | 122.0933 | 0.15358 | 0.082402 | -0.20743 | 122.2155 | 122.1729 | 122.3649 | 122.1099 | -0.053878 | 122.1655 | 122.2641 | 121.9743 | 122.1363 | -0.24197
1866.8281 | 122.3557 | -122.1268 | 0.10986 | 1.4211e-13 | -0.030036 | 0.013825 | -0.0040665 | -0.013401 | 0.018416 | -0.22533 | 0.018012 | 0.018676 | 0.015598 | 0.035008 | 0.009467 | 0.046831 | 0.005985 | 0.01906 | 0.10707 | 0.059885 | 0.27475 | 0.028521 | 0.051413 | 0.03241 | -0.010564 | 0.066194 | 0.16022 | -0.12961 | -0.15957 | 122.1553 | -0.002795 | 122.1736 | 122.1458 | -0.009461 | -0.049978 | 0.16488 | 121.9672 | -0.043669 | 122.1782 | 122.1162 | 0.14901 | 0.050359 | -0.23947 | 122.2338 | 122.1867 | 122.4015 | 122.1328 | -0.081342 | 122.193 | 122.287 | 121.9972 | 122.1592 | -0.26943
1868.5 | 122.4014 | -122.0901 | 0.11902 | 1.4211e-13 | -0.03025 | 0.014252 | -0.0040665 | -0.01276 | 0.019057 | -0.23296 | 0.018225 | 0.018462 | 0.015598 | 0.034581 | 0.009467 | 0.060567 | 0.005985 | 0.01906 | 0.11165 | 0.050727 | 0.26559 | 0.023942 | 0.051413 | 0.027831 | -0.010564 | 0.066194 | 0.16022 | -0.13419 | -0.16873 | 122.1141 | -0.007372 | 122.1507 | 122.1092 | -0.004882 | -0.068292 | 0.14657 | 121.9214 | -0.052825 | 122.1416 | 122.0796 | 0.15816 | 0.041203 | -0.25321 | 122.2018 | 122.1409 | 122.3557 | 122.0961 | -0.095077 | 122.1563 | 122.2504 | 121.956 | 122.118 | -0.28775
1870.25 | 122.2916 | -122.1588 | 0.13733 | 1.4211e-13 | -0.03025 | 0.014252 | -0.0040665 | -0.013187 | 0.018629 | -0.23296 | 0.018012 | 0.018462 | 0.015171 | 0.034581 | 0.009467 | 0.060567 | 0.005985 | 0.023639 | 0.11165 | 0.064464 | 0.27017 | 0.023942 | 0.060571 | 0.03241 | -0.005985 | 0.066194 | 0.15107 | -0.12503 | -0.17331 | 122.1828 | -0.025682 | 122.2194 | 122.1825 | -0.000303 | -0.072865 | 0.13284 | 121.9855 | -0.071135 | 122.2194 | 122.1528 | 0.16732 | 0.013736 | -0.26236 | 122.2705 | 122.2233 | 122.429 | 122.1648 | -0.11339 | 122.225 | 122.3099 | 122.0338 | 122.1912 | -0.31063
1871.9844 | 122.3099 | -122.1588 | 0.11902 | 1.4211e-13 | -0.029822 | 0.014252 | -0.0040665 | -0.013187 | 0.018843 | -0.22533 | 0.018225 | 0.018889 | 0.015598 | 0.034795 | 0.008826 | 0.055988 | 0.010564 | 0.023639 | 0.10707 | 0.059885 | 0.26559 | 0.019363 | 0.060571 | 0.03241 | -0.015143 | 0.066194 | 0.15564 | -0.13419 | -0.15957 | 122.1782 | -0.011951 | 122.2148 | 122.1825 | 0.004276 | -0.059134 | 0.14657 | 121.9992 | -0.052825 | 122.2194 | 122.1437 | 0.14443 | 0.036624 | -0.25321 | 122.2659 | 122.2187 | 122.4244 | 122.1694 | -0.099656 | 122.225 | 122.3145 | 122.0246 | 122.1912 | -0.27859
1873.7344 | 122.3877 | -122.1222 | 0.11444 | 1.4211e-13 | -0.03025 | 0.014039 | -0.0038527 | -0.012974 | 0.018843 | -0.22533 | 0.018225 | 0.018462 | 0.015598 | 0.034795 | 0.009467 | 0.05141 | 0.010564 | 0.023639 | 0.10707 | 0.059885 | 0.27017 | 0.0331 | 0.051413 | 0.027831 | -0.015143 | 0.066194 | 0.15107 | -0.12045 | -0.17331 | 122.1553 | -0.007373 | 122.1736 | 122.1458 | -0.009461 | -0.054556 | 0.15573 | 121.9489 | -0.048247 | 122.1736 | 122.107 | 0.15816 | 0.036624 | -0.23489 | 122.2293 | 122.1821 | 122.3924 | 122.1328 | -0.081341 | 122.1884 | 122.2733 | 122.0017 | 122.15 | -0.28775
1875.4219 | 122.4335 | -122.1222 | 0.091553 | 1.4211e-13 | -0.029822 | 0.013825 | -0.0036391 | -0.012974 | 0.018843 | -0.24059 | 0.018012 | 0.018889 | 0.015385 | 0.035008 | 0.0092534 | 0.055988 | 0.005985 | 0.01906 | 0.10707 | 0.059885 | 0.27475 | 0.028521 | 0.060571 | 0.023253 | -0.015143 | 0.075351 | 0.15107 | -0.12503 | -0.16873 | 122.1507 | 0.015515 | 122.1782 | 122.1413 | -0.009461 | -0.031668 | 0.18319 | 121.9535 | -0.016202 | 122.1828 | 122.107 | 0.15358 | 0.059512 | -0.21658 | 122.2293 | 122.1821 | 122.3969 | 122.1282 | -0.063032 | 122.1975 | 122.2733 | 121.9972 | 122.1454 | -0.26028
1877.1562 | 122.4472 | -122.1222 | 0.091553 | 1.4211e-13 | -0.030036 | 0.013611 | -0.0036391 | -0.013615 | 0.018843 | -0.23296 | 0.018012 | 0.018462 | 0.015598 | 0.034581 | 0.0086124 | 0.065145 | 0.005985 | 0.01906 | 0.11165 | 0.064464 | 0.26559 | 0.014784 | 0.051413 | 0.027831 | -0.005985 | 0.066194 | 0.15564 | -0.12045 | -0.16415 | 122.137 | 0.020094 | 122.1873 | 122.1413 | 0.004276 | -0.027089 | 0.17403 | 121.958 | -0.025359 | 122.1736 | 122.1162 | 0.15816 | 0.06409 | -0.212 | 122.2338 | 122.1867 | 122.3878 | 122.1282 | -0.076769 | 122.1884 | 122.2778 | 122.0017 | 122.15 | -0.2557
1878.9062 | 122.3053 | -122.1542 | 0.14191 | 1.4211e-13 | -0.030036 | 0.014039 | -0.0040665 | -0.013187 | 0.018416 | -0.22533 | 0.018012 | 0.018462 | 0.015385 | 0.034581 | 0.008826 | 0.055988 | 0.005985 | 0.023639 | 0.11165 | 0.064464 | 0.27475 | 0.023942 | 0.055992 | 0.03241 | -0.015143 | 0.061616 | 0.15564 | -0.12961 | -0.15957 | 122.1782 | -0.03026 | 122.2102 | 122.1779 | -0.000303 | -0.077443 | 0.13284 | 121.9947 | -0.080291 | 122.2102 | 122.1391 | 0.14443 | 0.013736 | -0.27151 | 122.2659 | 122.2187 | 122.429 | 122.1602 | -0.11797 | 122.2159 | 122.3099 | 122.0246 | 122.1866 | -0.30148
1880.5938 | 122.3145 | -122.168 | 0.10986 | 1.4211e-13 | -0.030036 | 0.014039 | -0.0036391 | -0.013187 | 0.019057 | -0.24059 | 0.017798 | 0.018889 | 0.016026 | 0.035008 | 0.009467 | 0.055988 | 0.005985 | 0.01906 | 0.11622 | 0.059885 | 0.26559 | 0.023942 | 0.055992 | 0.027831 | -0.005985 | 0.070773 | 0.15107 | -0.11587 | -0.16415 | 122.1919 | 0.006362 | 122.224 | 122.187 | -0.004882 | -0.049978 | 0.15573 | 122.0038 | -0.03909 | 122.224 | 122.162 | 0.15816 | 0.041202 | -0.22574 | 122.2842 | 122.2279 | 122.4336 | 122.174 | -0.085921 | 122.2387 | 122.319 | 122.0521 | 122.1958 | -0.27401
1882.3281 | 122.4106 | -122.1497 | 0.10071 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0038527 | -0.012974 | 0.018416 | -0.24059 | 0.017798 | 0.018676 | 0.015171 | 0.034581 | 0.0090396 | 0.055988 | 0.005985 | 0.023639 | 0.1208 | 0.059885 | 0.27475 | 0.028521 | 0.055992 | 0.036989 | -0.010564 | 0.070773 | 0.15107 | -0.060928 | -0.16873 | 122.1782 | 0.020096 | 122.2056 | 122.1733 | -0.004882 | -0.040823 | 0.17404 | 121.9809 | -0.029935 | 122.2057 | 122.1391 | 0.15816 | 0.050357 | -0.16164 | 122.2705 | 122.2095 | 122.4244 | 122.1556 | -0.072187 | 122.2204 | 122.3007 | 122.0887 | 122.1866 | -0.26944
1884.0781 | 122.3877 | -122.1176 | 0.09613 | 1.4211e-13 | -0.03025 | 0.013825 | -0.0038527 | -0.013187 | 0.018629 | -0.23296 | 0.017798 | 0.018676 | 0.015598 | 0.034367 | 0.009467 | 0.065145 | 0.005985 | 0.023639 | 0.10707 | 0.064464 | 0.26101 | 0.0331 | 0.060571 | 0.023253 | -0.015143 | 0.066194 | 0.15107 | -0.12045 | -0.15957 | 122.1507 | 0.010938 | 122.1828 | 122.1413 | -0.009461 | -0.031666 | 0.16488 | 121.958 | -0.029936 | 122.1782 | 122.1025 | 0.14443 | 0.054935 | -0.21658 | 122.2247 | 122.1821 | 122.3786 | 122.1236 | -0.06303 | 122.1838 | 122.2687 | 121.9972 | 122.1409 | -0.2557
1885.8594 | 122.4609 | -122.1039 | 0.10071 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0040665 | -0.013828 | 0.018843 | -0.23296 | 0.018225 | 0.018676 | 0.015171 | 0.034367 | 0.0092534 | 0.05141 | 0.001407 | 0.023639 | 0.10707 | 0.059885 | 0.27017 | 0.028521 | 0.055992 | 0.027831 | -0.019721 | 0.061616 | 0.15564 | -0.12503 | -0.15957 | 122.1324 | 0.00636 | 122.1553 | 122.1275 | -0.004882 | -0.040823 | 0.16946 | 121.9443 | -0.039092 | 122.1599 | 122.0842 | 0.13985 | 0.054935 | -0.22574 | 122.2109 | 122.1638 | 122.374 | 122.1053 | -0.072187 | 122.1655 | 122.2595 | 121.9789 | 122.1317 | -0.26028
1887.5469 | 122.3969 | -122.1588 | 0.091553 | 1.4211e-13 | -0.030036 | 0.014039 | -0.0038527 | -0.013401 | 0.018843 | -0.23296 | 0.018225 | 0.018462 | 0.015598 | 0.034795 | 0.0092534 | 0.055988 | 0.005985 | 0.01906 | 0.11622 | 0.059885 | 0.27017 | 0.0331 | 0.055992 | 0.036989 | -0.010564 | 0.066194 | 0.15107 | -0.13876 | -0.16873 | 122.1919 | 0.024672 | 122.2148 | 122.1779 | -0.01404 | -0.031668 | 0.17861 | 121.9901 | -0.025359 | 122.2148 | 122.1482 | 0.15816 | 0.059512 | -0.23032 | 122.275 | 122.2187 | 122.429 | 122.1648 | -0.058453 | 122.225 | 122.3099 | 122.02 | 122.1958 | -0.26028
1889.2969 | 122.4518 | -122.1405 | 0.07782 | 1.4211e-13 | -0.029609 | 0.014039 | -0.0040665 | -0.013401 | 0.018843 | -0.22533 | 0.018225 | 0.018462 | 0.015598 | 0.034581 | 0.009467 | 0.055988 | 0.005985 | 0.028217 | 0.097912 | 0.064464 | 0.26559 | 0.028521 | 0.051413 | 0.036989 | -0.010564 | 0.075351 | 0.15107 | -0.13419 | -0.16873 | 122.169 | 0.020092 | 122.1965 | 122.1687 | -0.000304 | -0.013356 | 0.18777 | 121.9718 | -0.002469 | 122.1919 | 122.1299 | 0.15816 | 0.073245 | -0.21201 | 122.2384 | 122.205 | 122.4061 | 122.1465 | -0.049299 | 122.2159 | 122.2916 | 122.0063 | 122.1775 | -0.24655
1891.0469 | 122.3419 | -122.168 | 0.10986 | 1.4211e-13 | -0.029822 | 0.014252 | -0.0038527 | -0.013187 | 0.018843 | -0.23296 | 0.018225 | 0.018676 | 0.015812 | 0.034795 | 0.009467 | 0.060567 | 0.001407 | 0.023639 | 0.10707 | 0.059885 | 0.27017 | 0.028521 | 0.055992 | 0.03241 | -0.015143 | 0.061616 | 0.15564 | -0.083821 | -0.15957 | 122.1965 | -0.002795 | 122.2285 | 122.1916 | -0.004882 | -0.049978 | 0.1603 | 122.0084 | -0.048247 | 122.224 | 122.1528 | 0.14443 | 0.04578 | -0.19368 | 122.275 | 122.2279 | 122.4381 | 122.1694 | -0.081342 | 122.2296 | 122.3236 | 122.0841 | 122.2004 | -0.26943
1892.7188 | 122.4243 | -122.1542 | 0.10986 | 1.4211e-13 | -0.030036 | 0.013611 | -0.0040665 | -0.013187 | 0.019057 | -0.23296 | 0.017798 | 0.018676 | 0.015812 | 0.034581 | 0.0090396 | 0.05141 | 0.005985 | 0.023639 | 0.11165 | 0.055306 | 0.27017 | 0.023942 | 0.060571 | 0.027831 | -0.010564 | 0.075351 | 0.15564 | -0.12045 | -0.15957 | 122.1782 | 0.001784 | 122.2056 | 122.1779 | -0.000303 | -0.054557 | 0.1603 | 121.9947 | -0.034512 | 122.2148 | 122.1437 | 0.14901 | 0.04578 | -0.23031 | 122.2659 | 122.2095 | 122.4244 | 122.1602 | -0.085921 | 122.2296 | 122.3099 | 122.0338 | 122.1821 | -0.26943
1894.4531 | 122.4609 | -122.1634 | 0.091553 | 1.4211e-13 | -0.03025 | 0.013825 | -0.0040665 | -0.013615 | 0.018843 | -0.23296 | 0.018012 | 0.018462 | 0.015385 | 0.034367 | 0.0090396 | 0.05141 | 0.001407 | 0.01906 | 0.10249 | 0.059885 | 0.27017 | 0.019363 | 0.055992 | 0.027831 | -0.010564 | 0.066194 | 0.15564 | -0.097557 | -0.15957 | 122.1828 | 0.010937 | 122.2148 | 122.1825 | -0.000303 | -0.031668 | 0.17861 | 122.0038 | -0.025359 | 122.2194 | 122.1528 | 0.14901 | 0.06409 | -0.18911 | 122.2659 | 122.2233 | 122.4336 | 122.1648 | -0.07219 | 122.2296 | 122.319 | 122.0658 | 122.1912 | -0.25112
1896.1406 | 122.4792 | -122.1542 | 0.09613 | 1.4211e-13 | -0.03025 | 0.013398 | -0.0038527 | -0.013187 | 0.018416 | -0.23296 | 0.018012 | 0.018462 | 0.015598 | 0.034795 | 0.0092534 | 0.055988 | 0.005985 | 0.028217 | 0.11165 | 0.064464 | 0.26559 | 0.023942 | 0.055992 | 0.036989 | -0.005985 | 0.070773 | 0.15564 | -0.10214 | -0.15957 | 122.1782 | 0.015517 | 122.2102 | 122.1825 | 0.004275 | -0.031666 | 0.16946 | 121.9947 | -0.025357 | 122.2102 | 122.1483 | 0.15358 | 0.059513 | -0.19827 | 122.2659 | 122.2187 | 122.4198 | 122.1602 | -0.072188 | 122.225 | 122.3099 | 122.0521 | 122.1912 | -0.2557
1897.875 | 122.4518 | -122.1085 | 0.091553 | 1.4211e-13 | -0.030036 | 0.014039 | -0.0042801 | -0.012974 | 0.018843 | -0.24059 | 0.018012 | 0.018249 | 0.015385 | 0.034795 | 0.0090396 | 0.055988 | 0.010564 | 0.014482 | 0.11165 | 0.059885 | 0.27017 | 0.023942 | 0.055992 | 0.027831 | -0.005985 | 0.066194 | 0.15564 | -0.11587 | -0.17331 | 122.1324 | 0.020094 | 122.1644 | 122.1229 | -0.00946 | -0.031668 | 0.17861 | 121.9352 | -0.025359 | 122.1645 | 122.1025 | 0.16732 | 0.06409 | -0.20742 | 122.2201 | 122.1683 | 122.3786 | 122.119 | -0.067611 | 122.1747 | 122.2641 | 121.9926 | 122.1363 | -0.26486
1899.5625 | 122.4335 | -122.1313 | 0.086975 | 1.4211e-13 | -0.030036 | 0.014039 | -0.0038527 | -0.012974 | 0.018629 | -0.23296 | 0.018012 | 0.018462 | 0.015598 | 0.035008 | 0.0090396 | 0.046831 | 0.010564 | 0.028217 | 0.11165 | 0.059885 | 0.26559 | 0.014784 | 0.051413 | 0.03241 | -0.010564 | 0.066194 | 0.16022 | -0.10671 | -0.16415 | 122.1461 | 0.024672 | 122.1782 | 122.1596 | 0.013433 | -0.02709 | 0.17861 | 121.9672 | -0.020781 | 122.1828 | 122.1208 | 0.15358 | 0.073247 | -0.19369 | 122.243 | 122.1912 | 122.3969 | 122.1419 | -0.072191 | 122.1975 | 122.2916 | 122.0246 | 122.1638 | -0.25112
1901.25 | 122.3328 | -122.1909 | 0.12817 | 1.4211e-13 | -0.030036 | 0.013825 | -0.0038527 | -0.013401 | 0.018629 | -0.23296 | 0.018225 | 0.018676 | 0.015385 | 0.034367 | 0.0092534 | 0.055988 | 0.005985 | 0.014482 | 0.11165 | 0.059885 | 0.27017 | 0.023942 | 0.051413 | 0.041567 | -0.015143 | 0.066194 | 0.15564 | -0.12961 | -0.16873 | 122.2148 | -0.016527 | 122.2468 | 122.2053 | -0.00946 | -0.068289 | 0.14199 | 122.0221 | -0.06198 | 122.2423 | 122.1757 | 0.15358 | 0.027469 | -0.25778 | 122.3025 | 122.2507 | 122.461 | 122.1968 | -0.10423 | 122.2571 | 122.3465 | 122.0613 | 122.2324 | -0.2969
1902.9844 | 122.3648 | -122.1771 | 0.10529 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0038527 | -0.013401 | 0.018629 | -0.23296 | 0.017584 | 0.018889 | 0.015385 | 0.034581 | 0.0090396 | 0.046831 | 0.010564 | 0.01906 | 0.11622 | 0.055306 | 0.27017 | 0.0331 | 0.051413 | 0.03241 | -0.005985 | 0.070773 | 0.15107 | -0.092979 | -0.16415 | 122.2102 | 0.010939 | 122.224 | 122.1962 | -0.01404 | -0.04998 | 0.16488 | 122.013 | -0.034513 | 122.2285 | 122.1711 | 0.15816 | 0.045779 | -0.19827 | 122.2933 | 122.2324 | 122.4473 | 122.1877 | -0.072186 | 122.2479 | 122.3282 | 122.0841 | 122.2095 | -0.26943
1904.7188 | 122.4152 | -122.1863 | 0.086975 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0038527 | -0.013187 | 0.018629 | -0.23296 | 0.018225 | 0.018462 | 0.015385 | 0.034581 | 0.0090396 | 0.055988 | 0.001407 | 0.01906 | 0.10707 | 0.059885 | 0.26559 | 0.023942 | 0.055992 | 0.036989 | -0.015143 | 0.066194 | 0.15107 | -0.12961 | -0.15499 | 122.2102 | 0.020093 | 122.2423 | 122.2053 | -0.004882 | -0.02709 | 0.17861 | 122.0313 | -0.020781 | 122.2423 | 122.1711 | 0.13985 | 0.06409 | -0.21658 | 122.2933 | 122.2462 | 122.4519 | 122.1877 | -0.063033 | 122.2525 | 122.3373 | 122.0567 | 122.2233 | -0.24197
1906.4688 | 122.3831 | -122.2092 | 0.11444 | 1.4211e-13 | -0.029822 | 0.013825 | -0.0038527 | -0.013187 | 0.018843 | -0.22533 | 0.018012 | 0.018889 | 0.015385 | 0.034367 | 0.0092534 | 0.060567 | 0.005985 | 0.01906 | 0.11165 | 0.064464 | 0.27017 | 0.019363 | 0.051413 | 0.03241 | -0.015143 | 0.066194 | 0.16022 | -0.097557 | -0.16415 | 122.2285 | -0.002794 | 122.2697 | 122.2282 | -0.000303 | -0.049977 | 0.15573 | 122.045 | -0.048247 | 122.2606 | 122.194 | 0.14901 | 0.045781 | -0.212 | 122.3208 | 122.2736 | 122.4793 | 122.2152 | -0.095078 | 122.2754 | 122.3694 | 122.1116 | 122.2416 | -0.27859
1908.1562 | 122.3877 | -122.1817 | 0.10529 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0034253 | -0.013615 | 0.018843 | -0.22533 | 0.018012 | 0.018462 | 0.015598 | 0.034581 | 0.008826 | 0.060567 | 0.001407 | 0.023639 | 0.11165 | 0.059885 | 0.27932 | 0.023942 | 0.055992 | 0.03241 | -0.010564 | 0.070773 | 0.17396 | -0.083821 | -0.16415 | 122.2056 | 0.006361 | 122.2423 | 122.2053 | -0.000303 | -0.045401 | 0.17404 | 122.0176 | -0.034513 | 122.2377 | 122.1711 | 0.15358 | 0.068672 | -0.18911 | 122.2933 | 122.2416 | 122.461 | 122.1831 | -0.081344 | 122.2525 | 122.3557 | 122.0979 | 122.2141 | -0.26943
1909.9062 | 122.4243 | -122.1863 | 0.13275 | 1.4211e-13 | -0.030036 | 0.01468 | -0.0038527 | -0.013187 | 0.018843 | -0.23296 | 0.018225 | 0.018676 | 0.015385 | 0.034795 | 0.0090396 | 0.055988 | 0.005985 | 0.01906 | 0.11622 | 0.059885 | 0.27017 | 0.023942 | 0.051413 | 0.036989 | -0.015143 | 0.070773 | 0.15564 | -0.097557 | -0.16415 | 122.2102 | -0.016526 | 122.2423 | 122.2053 | -0.004882 | -0.072866 | 0.13742 | 122.0221 | -0.061978 | 122.2377 | 122.1711 | 0.14901 | 0.022892 | -0.23031 | 122.3025 | 122.2462 | 122.4564 | 122.1923 | -0.10881 | 122.2571 | 122.3419 | 122.0887 | 122.2233 | -0.2969
1911.6562 | 122.4792 | -122.1634 | 0.059509 | 1.4211e-13 | -0.030036 | 0.014039 | -0.0038527 | -0.013401 | 0.018843 | -0.23296 | 0.018012 | 0.018462 | 0.015598 | 0.035008 | 0.009467 | 0.05141 | 0.010564 | 0.009904 | 0.11165 | 0.064464 | 0.26559 | 0.023942 | 0.055992 | 0.036989 | -0.015143 | 0.066194 | 0.1648 | -0.074664 | -0.15957 | 122.1873 | 0.052138 | 122.2148 | 122.1733 | -0.014038 | 0.004955 | 0.20608 | 122.0038 | 0.006685 | 122.2194 | 122.1482 | 0.14443 | 0.10529 | -0.13417 | 122.275 | 122.2279 | 122.429 | 122.174 | -0.035567 | 122.2296 | 122.3282 | 122.0887 | 122.2004 | -0.21908
1913.3438 | 122.3465 | -122.2 | 0.11902 | 1.4211e-13 | -0.029609 | 0.014039 | -0.0038527 | -0.013187 | 0.018629 | -0.24059 | 0.018012 | 0.018462 | 0.015385 | 0.034581 | 0.0092534 | 0.055988 | 0.015142 | 0.01906 | 0.10707 | 0.059885 | 0.26559 | 0.023942 | 0.051413 | 0.03241 | -0.010564 | 0.066194 | 0.16022 | -0.12961 | -0.16873 | 122.224 | -0.011951 | 122.256 | 122.2191 | -0.004882 | -0.059134 | 0.14657 | 122.0313 | -0.052825 | 122.2514 | 122.1894 | 0.15816 | 0.041203 | -0.24863 | 122.3071 | 122.2599 | 122.4656 | 122.2152 | -0.095077 | 122.2662 | 122.3602 | 122.0704 | 122.2324 | -0.28775
1915.0312 | 122.4106 | -122.1909 | 0.10986 | 1.4211e-13 | -0.030036 | 0.014039 | -0.0038527 | -0.013187 | 0.018629 | -0.24059 | 0.018012 | 0.018889 | 0.015385 | 0.034367 | 0.009467 | 0.055988 | 0.005985 | 0.014482 | 0.10707 | 0.064464 | 0.27017 | 0.023942 | 0.055992 | 0.027831 | -0.015143 | 0.066194 | 0.16022 | -0.11587 | -0.16415 | 122.2148 | -0.002795 | 122.2468 | 122.2053 | -0.00946 | -0.045399 | 0.1603 | 122.0267 | -0.043669 | 122.2468 | 122.1757 | 0.14901 | 0.050359 | -0.22574 | 122.2979 | 122.2553 | 122.461 | 122.1968 | -0.085921 | 122.2571 | 122.3511 | 122.075 | 122.2187 | -0.27401
1916.7812 | 122.4701 | -122.1725 | 0.10986 | 1.4211e-13 | -0.029822 | 0.014252 | -0.0042801 | -0.013187 | 0.018629 | -0.23296 | 0.018012 | 0.018462 | 0.015598 | 0.034153 | 0.0092534 | 0.055988 | 0.005985 | 0.01906 | 0.11622 | 0.059885 | 0.26559 | 0.023942 | 0.055992 | 0.027831 | -0.019721 | 0.061616 | 0.16022 | -0.11587 | -0.16415 | 122.1965 | 0.006362 | 122.2285 | 122.1916 | -0.004882 | -0.049978 | 0.15573 | 122.0084 | -0.048247 | 122.2285 | 122.1528 | 0.14443 | 0.050359 | -0.22574 | 122.2888 | 122.2324 | 122.4381 | 122.1785 | -0.085921 | 122.2342 | 122.3328 | 122.0567 | 122.2004 | -0.27401
1918.5312 | 122.4976 | -122.1909 | 0.073242 | 1.4211e-13 | -0.029609 | 0.013611 | -0.0034253 | -0.013615 | 0.018629 | -0.23296 | 0.018225 | 0.018676 | 0.015385 | 0.034581 | 0.009467 | 0.060567 | 0.005985 | 0.023639 | 0.10707 | 0.055306 | 0.26559 | 0.023942 | 0.051413 | 0.027831 | -0.019721 | 0.070773 | 0.15564 | -0.083821 | -0.16415 | 122.2148 | 0.033826 | 122.2514 | 122.2145 | -0.000303 | -0.017936 | 0.19235 | 122.0267 | -0.002469 | 122.2423 | 122.1711 | 0.14443 | 0.082401 | -0.15706 | 122.2979 | 122.2462 | 122.4564 | 122.1968 | -0.0493 | 122.2616 | 122.3465 | 122.107 | 122.2187 | -0.23739
1920.2188 | 122.374 | -122.2229 | 0.1236 | 1.4211e-13 | -0.030036 | 0.013825 | -0.0036391 | -0.012974 | 0.018843 | -0.22533 | 0.017798 | 0.018676 | 0.015598 | 0.034795 | 0.0092534 | 0.060567 | 0.001407 | 0.023639 | 0.11165 | 0.055306 | 0.26559 | 0.019363 | 0.046835 | 0.027831 | -0.019721 | 0.066194 | 0.15564 | -0.10214 | -0.16415 | 122.2423 | -0.011949 | 122.2835 | 122.2465 | 0.004276 | -0.06829 | 0.14199 | 122.0588 | -0.057402 | 122.2697 | 122.2032 | 0.14443 | 0.032047 | -0.22573 | 122.3345 | 122.2782 | 122.4885 | 122.2243 | -0.10423 | 122.2891 | 122.3785 | 122.1208 | 122.2507 | -0.28774
1921.9531 | 122.4518 | -122.1954 | 0.10529 | 1.4211e-13 | -0.029609 | 0.013825 | -0.0038527 | -0.013615 | 0.018629 | -0.23296 | 0.018012 | 0.018676 | 0.015598 | 0.034367 | 0.0092534 | 0.055988 | 0.010564 | 0.01906 | 0.11165 | 0.055306 | 0.27017 | 0.028521 | 0.055992 | 0.03241 | -0.015143 | 0.066194 | 0.15564 | -0.0884 | -0.15957 | 122.224 | 0.006361 | 122.2514 | 122.2145 | -0.009461 | -0.04998 | 0.16488 | 122.0359 | -0.039092 | 122.2514 | 122.1803 | 0.14443 | 0.050357 | -0.19369 | 122.3071 | 122.2507 | 122.4656 | 122.206 | -0.076765 | 122.2616 | 122.3511 | 122.107 | 122.2278 | -0.26486
1923.625 | 122.3785 | -122.2137 | 0.1236 | 1.4211e-13 | -0.029822 | 0.013825 | -0.0038527 | -0.013401 | 0.018416 | -0.22533 | 0.018439 | 0.018676 | 0.015385 | 0.034581 | 0.0090396 | 0.05141 | 0.010564 | 0.014482 | 0.11622 | 0.064464 | 0.27017 | 0.019363 | 0.051413 | 0.023253 | -0.010564 | 0.070773 | 0.16022 | -0.12961 | -0.16415 | 122.2331 | -0.007371 | 122.2652 | 122.2282 | -0.004881 | -0.059132 | 0.14657 | 122.0496 | -0.052823 | 122.2652 | 122.2032 | 0.15358 | 0.036626 | -0.2532 | 122.33 | 122.2782 | 122.4839 | 122.2243 | -0.10423 | 122.2845 | 122.374 | 122.0841 | 122.237 | -0.28774
1925.3594 | 122.3694 | -122.2275 | 0.12817 | 1.4211e-13 | -0.029822 | 0.014252 | -0.0038527 | -0.013187 | 0.018629 | -0.22533 | 0.017798 | 0.018462 | 0.015385 | 0.034581 | 0.009467 | 0.05141 | 0.010564 | 0.023639 | 0.10707 | 0.059885 | 0.26559 | 0.028521 | 0.055992 | 0.03241 | -0.005985 | 0.070773 | 0.15564 | -0.074664 | -0.15957 | 122.256 | -0.021106 | 122.2789 | 122.2511 | -0.004882 | -0.068289 | 0.13741 | 122.0679 | -0.057401 | 122.2835 | 122.2215 | 0.15358 | 0.027469 | -0.20284 | 122.3345 | 122.2874 | 122.4931 | 122.238 | -0.099653 | 122.2983 | 122.3831 | 122.1528 | 122.2599 | -0.28774
1927.0469 | 122.4472 | -122.1863 | 0.10529 | 1.4211e-13 | -0.029822 | 0.013825 | -0.0040665 | -0.013401 | 0.018843 | -0.2177 | 0.017798 | 0.018889 | 0.015598 | 0.034367 | 0.008826 | 0.05141 | 0.010564 | 0.01906 | 0.11165 | 0.055306 | 0.27017 | 0.019363 | 0.055992 | 0.027831 | -0.015143 | 0.070773 | 0.15564 | -0.10671 | -0.16415 | 122.2056 | 0.006361 | 122.2377 | 122.2053 | -0.000303 | -0.04998 | 0.16488 | 122.0221 | -0.034513 | 122.2423 | 122.1711 | 0.14901 | 0.050357 | -0.212 | 122.2979 | 122.2416 | 122.4564 | 122.1968 | -0.085923 | 122.2571 | 122.3419 | 122.0796 | 122.2141 | -0.26943
1928.7969 | 122.4518 | -122.1909 | 0.10071 | 1.4211e-13 | -0.029822 | 0.014252 | -0.0040665 | -0.012974 | 0.018416 | -0.24059 | 0.018225 | 0.018462 | 0.015812 | 0.034795 | 0.0090396 | 0.060567 | 0.001407 | 0.014482 | 0.11165 | 0.059885 | 0.27017 | 0.023942 | 0.055992 | 0.027831 | -0.010564 | 0.066194 | 0.15564 | -0.12503 | -0.15957 | 122.2148 | 0.010939 | 122.2514 | 122.2053 | -0.00946 | -0.040823 | 0.16946 | 122.0313 | -0.034514 | 122.2468 | 122.1803 | 0.14901 | 0.054935 | -0.22574 | 122.3025 | 122.2507 | 122.461 | 122.1923 | -0.076766 | 122.2571 | 122.3465 | 122.0658 | 122.2187 | -0.26028
1930.5469 | 122.4243 | -122.2275 | 0.1236 | 1.4211e-13 | -0.030036 | 0.014039 | -0.0040665 | -0.013615 | 0.018629 | -0.22533 | 0.018225 | 0.018676 | 0.015598 | 0.035008 | 0.0092534 | 0.05141 | 0.015142 | 0.014482 | 0.11622 | 0.059885 | 0.27017 | 0.023942 | 0.055992 | 0.036989 | -0.015143 | 0.066194 | 0.15564 | -0.11587 | -0.15499 | 122.2514 | -0.007371 | 122.2789 | 122.242 | -0.00946 | -0.063711 | 0.14657 | 122.0725 | -0.057402 | 122.2835 | 122.2123 | 0.13985 | 0.032047 | -0.23947 | 122.3437 | 122.2874 | 122.4976 | 122.2426 | -0.099654 | 122.2937 | 122.3831 | 122.1116 | 122.2645 | -0.27859
1932.2812 | 122.4518 | -122.2275 | 0.10071 | 1.4211e-13 | -0.030036 | 0.014039 | -0.0038527 | -0.013401 | 0.019057 | -0.23296 | 0.018012 | 0.018676 | 0.015598 | 0.034581 | 0.008826 | 0.05141 | 0.005985 | 0.01906 | 0.11165 | 0.050727 | 0.27017 | 0.023942 | 0.055992 | 0.027831 | -0.019721 | 0.066194 | 0.1648 | -0.12503 | -0.16415 | 122.2514 | 0.010939 | 122.2789 | 122.2465 | -0.004882 | -0.049981 | 0.16946 | 122.0633 | -0.034514 | 122.2835 | 122.2078 | 0.14443 | 0.064092 | -0.22574 | 122.3391 | 122.2782 | 122.4976 | 122.2335 | -0.076766 | 122.2937 | 122.3923 | 122.1024 | 122.2553 | -0.26486
1934.0156 | 122.493 | -122.2046 | 0.086975 | 1.4211e-13 | -0.029822 | 0.014252 | -0.0038527 | -0.013187 | 0.019057 | -0.23296 | 0.018225 | 0.018676 | 0.015598 | 0.034581 | 0.008826 | 0.060567 | 0.001407 | 0.01906 | 0.11165 | 0.059885 | 0.26559 | 0.019363 | 0.055992 | 0.041567 | -0.010564 | 0.075351 | 0.15564 | -0.097557 | -0.16415 | 122.224 | 0.024672 | 122.2652 | 122.2236 | -0.000303 | -0.02709 | 0.17861 | 122.0404 | -0.011624 | 122.2606 | 122.194 | 0.15358 | 0.068668 | -0.18453 | 122.3162 | 122.2645 | 122.4702 | 122.206 | -0.067612 | 122.2799 | 122.3602 | 122.107 | 122.2462 | -0.25112
1935.7812 | 122.3969 | -122.2366 | 0.10529 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0038527 | -0.013401 | 0.018416 | -0.23296 | 0.018225 | 0.018462 | 0.015598 | 0.034795 | 0.009467 | 0.055988 | 0.005985 | 0.01906 | 0.10249 | 0.059885 | 0.27932 | 0.019363 | 0.055992 | 0.027831 | -0.015143 | 0.066194 | 0.16022 | -0.12045 | -0.16873 | 122.256 | -0.002796 | 122.2926 | 122.2557 | -0.000303 | -0.045401 | 0.17404 | 122.0679 | -0.039092 | 122.2926 | 122.2215 | 0.15358 | 0.054936 | -0.22574 | 122.3391 | 122.2965 | 122.516 | 122.2426 | -0.085923 | 122.3028 | 122.3969 | 122.1162 | 122.2645 | -0.27401
1937.4531 | 122.5113 | -122.1863 | 0.073242 | 1.4211e-13 | -0.029609 | 0.013825 | -0.0036391 | -0.013401 | 0.018843 | -0.22533 | 0.018225 | 0.018462 | 0.015598 | 0.034581 | 0.0090396 | 0.05141 | 0.001407 | 0.01906 | 0.11622 | 0.055306 | 0.26559 | 0.023942 | 0.051413 | 0.03241 | -0.019721 | 0.070773 | 0.15564 | -0.10671 | -0.15957 | 122.2102 | 0.042983 | 122.2377 | 122.2053 | -0.004882 | -0.017936 | 0.19235 | 122.0267 | -0.002469 | 122.2377 | 122.1666 | 0.13985 | 0.082401 | -0.17996 | 122.3025 | 122.2416 | 122.4519 | 122.1877 | -0.0493 | 122.2571 | 122.3419 | 122.0796 | 122.2187 | -0.23281
1939.1875 | 122.4701 | -122.2229 | 0.082397 | 1.4211e-13 | -0.029609 | 0.014252 | -0.0040665 | -0.013401 | 0.019057 | -0.23296 | 0.018225 | 0.018462 | 0.015598 | 0.034581 | 0.009467 | 0.05141 | 0.005985 | 0.023639 | 0.11165 | 0.055306 | 0.26559 | 0.023942 | 0.051413 | 0.03241 | -0.010564 | 0.066194 | 0.15564 | -0.12503 | -0.15957 | 122.2468 | 0.02925 | 122.2743 | 122.2465 | -0.000303 | -0.027091 | 0.18319 | 122.0633 | -0.016203 | 122.2743 | 122.2123 | 0.14901 | 0.073246 | -0.20743 | 122.3345 | 122.2782 | 122.4885 | 122.2289 | -0.058455 | 122.2891 | 122.3785 | 122.0979 | 122.2553 | -0.24197
1940.9531 | 122.4106 | -122.2275 | 0.11902 | 1.4211e-13 | -0.029609 | 0.014039 | -0.0038527 | -0.013401 | 0.018843 | -0.22533 | 0.018012 | 0.018249 | 0.015385 | 0.034795 | 0.0090396 | 0.055988 | 0.005985 | 0.014482 | 0.1208 | 0.059885 | 0.26559 | 0.0331 | 0.055992 | 0.03241 | -0.019721 | 0.075351 | 0.16022 | -0.083821 | -0.15499 | 122.2606 | 0.001785 | 122.2835 | 122.242 | -0.018618 | -0.059134 | 0.14657 | 122.0725 | -0.043668 | 122.2835 | 122.2078 | 0.13527 | 0.041203 | -0.20284 | 122.3483 | 122.2874 | 122.4931 | 122.2335 | -0.085919 | 122.3028 | 122.3877 | 122.1437 | 122.2599 | -0.27401
1942.625 | 122.5204 | -122.1771 | 0.07782 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0040665 | -0.013187 | 0.019057 | -0.22533 | 0.017798 | 0.018676 | 0.015598 | 0.034795 | 0.0090396 | 0.060567 | 0.001407 | 0.01906 | 0.11165 | 0.059885 | 0.27017 | 0.023942 | 0.051413 | 0.036989 | -0.010564 | 0.070773 | 0.15564 | -0.092979 | -0.16873 | 122.2011 | 0.033827 | 122.2377 | 122.1962 | -0.004882 | -0.017935 | 0.19235 | 122.0084 | -0.007047 | 122.2285 | 122.1666 | 0.15816 | 0.077823 | -0.1708 | 122.2888 | 122.237 | 122.4473 | 122.1785 | -0.053878 | 122.2479 | 122.3328 | 122.0841 | 122.2141 | -0.24655
1944.2969 | 122.5159 | -122.2321 | 0.10071 | 1.4211e-13 | -0.029181 | 0.014252 | -0.0040665 | -0.013187 | 0.018629 | -0.23296 | 0.018012 | 0.018249 | 0.015598 | 0.035008 | 0.0092534 | 0.055988 | 0.005985 | 0.023639 | 0.11165 | 0.064464 | 0.26101 | 0.019363 | 0.051413 | 0.027831 | -0.010564 | 0.070773 | 0.15564 | -0.097557 | -0.16873 | 122.2514 | 0.010939 | 122.288 | 122.2557 | 0.004276 | -0.036244 | 0.1603 | 122.0633 | -0.029935 | 122.2835 | 122.2215 | 0.15816 | 0.054935 | -0.19827 | 122.3437 | 122.2965 | 122.4931 | 122.238 | -0.081345 | 122.3028 | 122.3877 | 122.1345 | 122.2599 | -0.26944
1946.0469 | 122.3969 | -122.2458 | 0.10986 | 1.4211e-13 | -0.029395 | 0.014039 | -0.0040665 | -0.012974 | 0.018843 | -0.22533 | 0.018225 | 0.018249 | 0.015812 | 0.034153 | 0.0092534 | 0.05141 | 0.005985 | 0.023639 | 0.11165 | 0.069043 | 0.27017 | 0.023942 | 0.055992 | 0.027831 | -0.010564 | 0.070773 | 0.15107 | -0.0884 | -0.16415 | 122.2697 | 0.001784 | 122.2972 | 122.2694 | -0.000303 | -0.04082 | 0.1603 | 122.0816 | -0.03909 | 122.3018 | 122.2352 | 0.15358 | 0.041202 | -0.19826 | 122.3574 | 122.3148 | 122.516 | 122.2518 | -0.085921 | 122.3166 | 122.3969 | 122.1574 | 122.2736 | -0.27401
1947.7344 | 122.493 | -122.2137 | 0.086975 | 1.4211e-13 | -0.029609 | 0.014039 | -0.0038527 | -0.013187 | 0.019057 | -0.23296 | 0.018012 | 0.018676 | 0.015598 | 0.034795 | 0.0090396 | 0.060567 | 0.001407 | 0.023639 | 0.11165 | 0.069043 | 0.27017 | 0.023942 | 0.055992 | 0.03241 | -0.015143 | 0.066194 | 0.15564 | -0.0884 | -0.16873 | 122.2377 | 0.024672 | 122.2743 | 122.2374 | -0.000303 | -0.017932 | 0.18319 | 122.045 | -0.020781 | 122.2697 | 122.1986 | 0.15358 | 0.068668 | -0.17538 | 122.3254 | 122.2828 | 122.4839 | 122.2152 | -0.063033 | 122.2799 | 122.3694 | 122.1253 | 122.2462 | -0.2557
1949.4688 | 122.3877 | -122.2778 | 0.13275 | 1.4211e-13 | -0.029609 | 0.014039 | -0.0042801 | -0.012974 | 0.018629 | -0.22533 | 0.018225 | 0.018462 | 0.015385 | 0.034581 | 0.008826 | 0.055988 | 0.001407 | 0.014482 | 0.11165 | 0.055306 | 0.27932 | 0.023942 | 0.051413 | 0.03241 | -0.015143 | 0.070773 | 0.16022 | -0.10214 | -0.16415 | 122.3018 | -0.021104 | 122.3338 | 122.2923 | -0.00946 | -0.077445 | 0.14657 | 122.1137 | -0.061978 | 122.3292 | 122.2627 | 0.14901 | 0.027471 | -0.23489 | 122.3895 | 122.3331 | 122.5572 | 122.2792 | -0.10881 | 122.3486 | 122.4381 | 122.1757 | 122.3102 | -0.2969
1951.1562 | 122.4289 | -122.2687 | 0.11444 | 1.4211e-13 | -0.029609 | 0.014252 | -0.0036391 | -0.013187 | 0.018629 | -0.23296 | 0.018012 | 0.018462 | 0.015598 | 0.034795 | 0.0092534 | 0.055988 | 0.005985 | 0.01906 | 0.1208 | 0.059885 | 0.27017 | 0.023942 | 0.055992 | 0.03241 | -0.015143 | 0.070773 | 0.16022 | -0.12503 | -0.16415 | 122.2926 | 0.006363 | 122.3247 | 122.2877 | -0.004882 | -0.054556 | 0.15573 | 122.1045 | -0.043668 | 122.3247 | 122.2535 | 0.14901 | 0.045781 | -0.23947 | 122.3895 | 122.3286 | 122.5388 | 122.2747 | -0.090499 | 122.3394 | 122.4289 | 122.1436 | 122.3011 | -0.27859
1952.9062 | 122.5388 | -122.2229 | 0.091553 | 1.4211e-13 | -0.029822 | 0.014466 | -0.0038527 | -0.013401 | 0.019057 | -0.23296 | 0.018439 | 0.018889 | 0.015598 | 0.035008 | 0.0092534 | 0.060567 | 0.005985 | 0.01906 | 0.11165 | 0.064464 | 0.26101 | 0.028521 | 0.060571 | 0.03241 | -0.015143 | 0.066194 | 0.15107 | -0.12045 | -0.16415 | 122.2514 | 0.020094 | 122.2835 | 122.242 | -0.009461 | -0.027089 | 0.16946 | 122.0588 | -0.025359 | 122.2835 | 122.2078 | 0.14901 | 0.059512 | -0.212 | 122.3345 | 122.2874 | 122.4839 | 122.2289 | -0.063032 | 122.2891 | 122.374 | 122.1024 | 122.2553 | -0.2557
1954.6562 | 122.5204 | -122.2 | 0.10529 | 1.4211e-13 | -0.029609 | 0.014039 | -0.0038527 | -0.012974 | 0.018629 | -0.24059 | 0.018225 | 0.018249 | 0.015171 | 0.034795 | 0.008826 | 0.05141 | 0.005985 | 0.023639 | 0.10707 | 0.059885 | 0.26559 | 0.023942 | 0.055992 | 0.03241 | -0.019721 | 0.066194 | 0.16022 | -0.10214 | -0.15957 | 122.224 | 0.001782 | 122.2514 | 122.2237 | -0.000303 | -0.045401 | 0.1603 | 122.0404 | -0.039092 | 122.256 | 122.1803 | 0.13985 | 0.054936 | -0.20742 | 122.3071 | 122.2599 | 122.4656 | 122.206 | -0.081344 | 122.2662 | 122.3602 | 122.0979 | 122.2324 | -0.26486
1956.3438 | 122.4564 | -122.2504 | 0.13275 | 1.4211e-13 | -0.029609 | 0.014039 | -0.0042801 | -0.012974 | 0.019057 | -0.22533 | 0.018653 | 0.018889 | 0.015598 | 0.034581 | 0.0092534 | 0.055988 | 0.005985 | 0.01906 | 0.11622 | 0.050727 | 0.27017 | 0.019363 | 0.055992 | 0.03241 | -0.0243 | 0.066194 | 0.14649 | -0.12045 | -0.16873 | 122.2697 | -0.016526 | 122.3064 | 122.2694 | -0.000303 | -0.082024 | 0.13742 | 122.0816 | -0.066557 | 122.3064 | 122.2261 | 0.14443 | 0.013735 | -0.2532 | 122.3666 | 122.3011 | 122.5205 | 122.2564 | -0.11339 | 122.3166 | 122.3969 | 122.1299 | 122.2828 | -0.30148
1958.0938 | 122.4152 | -122.2778 | 0.11902 | 1.4211e-13 | -0.029609 | 0.014039 | -0.0036391 | -0.013187 | 0.019057 | -0.22533 | 0.018225 | 0.018462 | 0.015598 | 0.034581 | 0.0090396 | 0.05141 | 0.001407 | 0.01906 | 0.11622 | 0.059885 | 0.26559 | 0.028521 | 0.051413 | 0.03241 | -0.015143 | 0.066194 | 0.15564 | -0.083821 | -0.16873 | 122.3064 | -0.002794 | 122.3292 | 122.2969 | -0.009461 | -0.059134 | 0.14657 | 122.1091 | -0.052825 | 122.3292 | 122.2627 | 0.15358 | 0.036624 | -0.20284 | 122.3941 | 122.3377 | 122.5434 | 122.2792 | -0.090498 | 122.344 | 122.4335 | 122.194 | 122.3102 | -0.28775
1959.8438 | 122.5388 | -122.2504 | 0.073242 | 1.4211e-13 | -0.029609 | 0.013825 | -0.0034253 | -0.012974 | 0.019057 | -0.24059 | 0.018225 | 0.018462 | 0.015385 | 0.034367 | 0.0090396 | 0.05141 | 0.005985 | 0.023639 | 0.10707 | 0.059885 | 0.27017 | 0.023942 | 0.051413 | 0.023253 | -0.010564 | 0.070773 | 0.15107 | -0.10671 | -0.16415 | 122.2743 | 0.033826 | 122.3018 | 122.274 | -0.000303 | -0.013357 | 0.19692 | 122.0862 | -0.002469 | 122.3018 | 122.2398 | 0.15358 | 0.077823 | -0.17996 | 122.3574 | 122.3103 | 122.5205 | 122.2564 | -0.0493 | 122.3211 | 122.4014 | 122.1437 | 122.2736 | -0.23739
1961.5312 | 122.4609 | -122.2458 | 0.09613 | 1.4211e-13 | -0.029609 | 0.014039 | -0.0038527 | -0.013401 | 0.018629 | -0.24059 | 0.018225 | 0.018462 | 0.015171 | 0.034795 | 0.0090396 | 0.060567 | 0.010564 | 0.023639 | 0.10707 | 0.064464 | 0.26559 | 0.019363 | 0.051413 | 0.027831 | -0.015143 | 0.066194 | 0.16022 | -0.12961 | -0.17331 | 122.2652 | 0.010938 | 122.3064 | 122.2694 | 0.004276 | -0.031666 | 0.16946 | 122.0725 | -0.029936 | 122.2972 | 122.2306 | 0.15816 | 0.064092 | -0.22574 | 122.3529 | 122.3103 | 122.5114 | 122.2564 | -0.076767 | 122.312 | 122.406 | 122.1162 | 122.2736 | -0.26944
1963.2812 | 122.4701 | -122.2549 | 0.10529 | 1.4211e-13 | -0.029609 | 0.013611 | -0.0038527 | -0.013187 | 0.018629 | -0.2177 | 0.018225 | 0.018462 | 0.015385 | 0.034367 | 0.009467 | 0.065145 | 0.005985 | 0.014482 | 0.11622 | 0.055306 | 0.27017 | 0.014784 | 0.060571 | 0.03241 | -0.005985 | 0.066194 | 0.1648 | -0.13419 | -0.16415 | 122.2697 | 0.010939 | 122.3201 | 122.2694 | -0.000302 | -0.04998 | 0.16488 | 122.0908 | -0.039092 | 122.3155 | 122.249 | 0.15816 | 0.059514 | -0.23947 | 122.3712 | 122.3102 | 122.5251 | 122.2609 | -0.090502 | 122.3211 | 122.4197 | 122.1208 | 122.2874 | -0.26943
1965.0312 | 122.4747 | -122.2641 | 0.091553 | 1.4211e-13 | -0.029609 | 0.013825 | -0.0038527 | -0.013187 | 0.018629 | -0.23296 | 0.018012 | 0.018462 | 0.015812 | 0.034581 | 0.0092534 | 0.065145 | 0.005985 | 0.023639 | 0.11165 | 0.059885 | 0.26559 | 0.023942 | 0.055992 | 0.03241 | -0.010564 | 0.066194 | 0.1648 | -0.12045 | -0.16415 | 122.288 | 0.020094 | 122.3292 | 122.2877 | -0.000303 | -0.031668 | 0.17403 | 122.1 | -0.025359 | 122.3201 | 122.2535 | 0.15358 | 0.073247 | -0.212 | 122.3757 | 122.324 | 122.5297 | 122.2701 | -0.067611 | 122.3303 | 122.4289 | 122.1436 | 122.2965 | -0.2557
1966.7188 | 122.4609 | -122.2916 | 0.1236 | 1.4211e-13 | -0.029822 | 0.014252 | -0.0038527 | -0.013401 | 0.017988 | -0.24059 | 0.017798 | 0.018462 | 0.015598 | 0.034795 | 0.0090396 | 0.055988 | 0.015142 | 0.014482 | 0.11622 | 0.064464 | 0.27017 | 0.019363 | 0.051413 | 0.027831 | -0.015143 | 0.061616 | 0.16022 | -0.12045 | -0.15499 | 122.3109 | -0.007371 | 122.3476 | 122.306 | -0.004881 | -0.059132 | 0.14657 | 122.1366 | -0.06198 | 122.343 | 122.2764 | 0.13985 | 0.036626 | -0.24405 | 122.4078 | 122.356 | 122.5617 | 122.3067 | -0.10423 | 122.3532 | 122.4518 | 122.1711 | 122.3194 | -0.27859
1968.4688 | 122.5479 | -122.2046 | 0.09613 | 1.4211e-13 | -0.029609 | 0.014039 | -0.0036391 | -0.013187 | 0.018202 | -0.23296 | 0.018012 | 0.018462 | 0.015812 | 0.034581 | 0.0092534 | 0.05141 | 0.001407 | 0.01906 | 0.11165 | 0.055306 | 0.27017 | 0.019363 | 0.055992 | 0.023253 | -0.0243 | 0.066194 | 0.15107 | -0.10214 | -0.16415 | 122.224 | 0.015517 | 122.256 | 122.2236 | -0.000303 | -0.040824 | 0.17404 | 122.0404 | -0.029936 | 122.2606 | 122.1803 | 0.13985 | 0.054935 | -0.19827 | 122.3162 | 122.2599 | 122.4748 | 122.206 | -0.076767 | 122.2708 | 122.3557 | 122.1025 | 122.2278 | -0.26028
1970.1562 | 122.5433 | -122.2412 | 0.082397 | 1.4211e-13 | -0.029395 | 0.014039 | -0.0034253 | -0.013401 | 0.018629 | -0.2177 | 0.018012 | 0.018676 | 0.015385 | 0.034581 | 0.009467 | 0.060567 | 0.010564 | 0.023639 | 0.10707 | 0.064464 | 0.26559 | 0.023942 | 0.055992 | 0.023253 | -0.015143 | 0.075351 | 0.16022 | -0.12045 | -0.16415 | 122.2652 | 0.024671 | 122.3018 | 122.2649 | -0.000303 | -0.017933 | 0.18319 | 122.0771 | -0.007046 | 122.2972 | 122.2261 | 0.14901 | 0.077825 | -0.20285 | 122.3483 | 122.3057 | 122.5068 | 122.2518 | -0.058455 | 122.3166 | 122.4014 | 122.1208 | 122.2645 | -0.24655
1971.9062 | 122.4152 | -122.2778 | 0.13275 | 1.4211e-13 | -0.029609 | 0.014252 | -0.0038527 | -0.013401 | 0.018843 | -0.22533 | 0.018012 | 0.018249 | 0.015812 | 0.034581 | 0.0092534 | 0.05141 | 0.005985 | 0.028217 | 0.11165 | 0.059885 | 0.27932 | 0.023942 | 0.060571 | 0.03241 | -0.010564 | 0.061616 | 0.1648 | -0.12503 | -0.16873 | 122.3018 | -0.021104 | 122.3292 | 122.306 | 0.004275 | -0.072866 | 0.14657 | 122.1091 | -0.071135 | 122.3384 | 122.2673 | 0.15816 | 0.032049 | -0.25778 | 122.3895 | 122.3377 | 122.5572 | 122.2838 | -0.10881 | 122.3394 | 122.4426 | 122.1528 | 122.3102 | -0.30148
1973.6562 | 122.5662 | -122.2641 | 0.09613 | 1.4211e-13 | -0.029395 | 0.013825 | -0.0038527 | -0.013187 | 0.018843 | -0.24059 | 0.017798 | 0.018462 | 0.015812 | 0.034367 | 0.0090396 | 0.055988 | 0.005985 | 0.01906 | 0.11622 | 0.064464 | 0.27475 | 0.028521 | 0.051413 | 0.027831 | -0.015143 | 0.07993 | 0.16022 | -0.12503 | -0.16415 | 122.2926 | 0.020095 | 122.3201 | 122.2832 | -0.009461 | -0.031666 | 0.17862 | 122.1 | -0.0162 | 122.3155 | 122.249 | 0.14901 | 0.064092 | -0.22116 | 122.3803 | 122.3286 | 122.5388 | 122.2701 | -0.067609 | 122.344 | 122.4243 | 122.1391 | 122.2919 | -0.26028
1975.4062 | 122.4335 | -122.2961 | 0.11902 | 1.4211e-13 | -0.029395 | 0.014466 | -0.0038527 | -0.013187 | 0.018629 | -0.22533 | 0.018012 | 0.018462 | 0.015812 | 0.034367 | 0.0092534 | 0.065145 | 0.019721 | 0.023639 | 0.11622 | 0.059885 | 0.27475 | 0.023942 | 0.051413 | 0.03241 | -0.010564 | 0.066194 | 0.15564 | -0.12503 | -0.16415 | 122.3201 | -0.002794 | 122.3613 | 122.3198 | -0.000303 | -0.059134 | 0.15573 | 122.132 | -0.052825 | 122.3476 | 122.2856 | 0.15358 | 0.036624 | -0.24405 | 122.4124 | 122.356 | 122.5709 | 122.3159 | -0.095077 | 122.3623 | 122.4518 | 122.1711 | 122.3286 | -0.28317
1977.0938 | 122.5708 | -122.2366 | 0.086975 | 1.4211e-13 | -0.029181 | 0.014039 | -0.0034253 | -0.013187 | 0.019057 | -0.23296 | 0.017798 | 0.019103 | 0.015385 | 0.034581 | 0.0090396 | 0.065145 | 0.005985 | 0.01906 | 0.11165 | 0.055306 | 0.27932 | 0.019363 | 0.060571 | 0.027831 | -0.019721 | 0.075351 | 0.16022 | -0.12503 | -0.16415 | 122.256 | 0.024672 | 122.3018 | 122.2557 | -0.000303 | -0.031669 | 0.19235 | 122.0725 | -0.011624 | 122.2972 | 122.2169 | 0.14443 | 0.073247 | -0.212 | 122.3483 | 122.2919 | 122.516 | 122.2426 | -0.067612 | 122.312 | 122.3969 | 122.1116 | 122.2645 | -0.25112
1978.8281 | 122.525 | -122.2595 | 0.10529 | 1.4211e-13 | -0.029395 | 0.014039 | -0.0038527 | -0.013187 | 0.018629 | -0.23296 | 0.018012 | 0.018676 | 0.015812 | 0.034581 | 0.0092534 | 0.055988 | 0.005985 | 0.01906 | 0.10707 | 0.059885 | 0.26559 | 0.023942 | 0.055992 | 0.03241 | -0.019721 | 0.066194 | 0.15564 | -0.070086 | -0.15957 | 122.2835 | 0.001782 | 122.3155 | 122.2786 | -0.004882 | -0.045401 | 0.1603 | 122.1 | -0.039092 | 122.3155 | 122.2398 | 0.13985 | 0.050357 | -0.17537 | 122.3666 | 122.3194 | 122.5251 | 122.2655 | -0.081344 | 122.3257 | 122.4152 | 122.1894 | 122.2919 | -0.26486
1980.5781 | 122.493 | -122.2824 | 0.11902 | 1.4211e-13 | -0.029395 | 0.013825 | -0.0036391 | -0.012974 | 0.018843 | -0.22533 | 0.018439 | 0.018676 | 0.015598 | 0.034367 | 0.0090396 | 0.060567 | 0.005985 | 0.01906 | 0.11165 | 0.064464 | 0.27475 | 0.023942 | 0.060571 | 0.027831 | -0.015143 | 0.075351 | 0.15564 | -0.092979 | -0.16873 | 122.3064 | -0.007372 | 122.343 | 122.3015 | -0.004882 | -0.054555 | 0.15573 | 122.1137 | -0.043668 | 122.343 | 122.2673 | 0.15358 | 0.036624 | -0.212 | 122.3941 | 122.3469 | 122.5572 | 122.2884 | -0.095077 | 122.3578 | 122.4381 | 122.1894 | 122.3102 | -0.28775
1982.2656 | 122.5388 | -122.2641 | 0.07782 | 1.4211e-13 | -0.029395 | 0.013825 | -0.0036391 | -0.013187 | 0.018843 | -0.23296 | 0.018225 | 0.018462 | 0.015385 | 0.034581 | 0.009467 | 0.055988 | 0.010564 | 0.028217 | 0.11165 | 0.064464 | 0.27017 | 0.019363 | 0.051413 | 0.036989 | -0.010564 | 0.070773 | 0.16022 | -0.0884 | -0.16415 | 122.2835 | 0.033827 | 122.3201 | 122.2923 | 0.008854 | -0.013356 | 0.19235 | 122.1 | -0.007047 | 122.3155 | 122.2535 | 0.15358 | 0.082402 | -0.16622 | 122.3757 | 122.3286 | 122.5343 | 122.2747 | -0.058457 | 122.3349 | 122.4243 | 122.1757 | 122.3011 | -0.24197
1984 | 122.5525 | -122.2641 | 0.10071 | 1.4211e-13 | -0.029395 | 0.013611 | -0.0038527 | -0.013615 | 0.019057 | -0.23296 | 0.018225 | 0.018462 | 0.015598 | 0.034581 | 0.0090396 | 0.060567 | 0.005985 | 0.01906 | 0.11622 | 0.064464 | 0.27475 | 0.019363 | 0.055992 | 0.027831 | -0.019721 | 0.070773 | 0.15107 | -0.0884 | -0.16873 | 122.2835 | 0.015517 | 122.3247 | 122.2832 | -0.000303 | -0.036244 | 0.17404 | 122.0954 | -0.029935 | 122.3201 | 122.2444 | 0.14901 | 0.050357 | -0.18911 | 122.3803 | 122.3286 | 122.5388 | 122.2701 | -0.081345 | 122.3349 | 122.4152 | 122.1757 | 122.2919 | -0.26944
1985.6719 | 122.4472 | -122.2778 | 0.10986 | 1.4211e-13 | -0.029609 | 0.014466 | -0.0040665 | -0.013401 | 0.018843 | -0.24059 | 0.018653 | 0.018676 | 0.015385 | 0.034795 | 0.0090396 | 0.055988 | 0.005985 | 0.014482 | 0.11165 | 0.059885 | 0.26559 | 0.019363 | 0.051413 | 0.03241 | -0.015143 | 0.066194 | 0.15107 | -0.0884 | -0.16415 | 122.2972 | 0.001784 | 122.3338 | 122.2923 | -0.004881 | -0.049978 | 0.15573 | 122.1137 | -0.043669 | 122.3292 | 122.2627 | 0.14901 | 0.041202 | -0.19826 | 122.3895 | 122.3377 | 122.5434 | 122.2838 | -0.0905 | 122.344 | 122.4289 | 122.1894 | 122.3102 | -0.27401
1987.4219 | 122.5296 | -122.2641 | 0.09613 | 1.4211e-13 | -0.029609 | 0.014039 | -0.0040665 | -0.013615 | 0.018843 | -0.22533 | 0.018225 | 0.018462 | 0.015598 | 0.034795 | 0.008826 | 0.060567 | 0.010564 | 0.023639 | 0.11165 | 0.064464 | 0.27017 | 0.023942 | 0.051413 | 0.03241 | -0.010564 | 0.066194 | 0.15107 | -0.0884 | -0.15957 | 122.288 | 0.015517 | 122.3247 | 122.2877 | -0.000303 | -0.031666 | 0.17404 | 122.1045 | -0.029936 | 122.3155 | 122.2535 | 0.14901 | 0.054935 | -0.18453 | 122.3757 | 122.3286 | 122.5343 | 122.2747 | -0.072188 | 122.3303 | 122.4152 | 122.1757 | 122.2965 | -0.2557
1989.1094 | 122.5479 | -122.3099 | 0.10529 | 1.4211e-13 | -0.029609 | 0.013825 | -0.0040665 | -0.013401 | 0.018843 | -0.22533 | 0.018012 | 0.018889 | 0.015385 | 0.034581 | 0.008826 | 0.065145 | 0.010564 | 0.01906 | 0.10707 | 0.064464 | 0.26559 | 0.019363 | 0.055992 | 0.036989 | -0.015143 | 0.070773 | 0.15107 | -0.10214 | -0.16415 | 122.3292 | 0.001782 | 122.375 | 122.3289 | -0.000303 | -0.040822 | 0.1603 | 122.1457 | -0.034513 | 122.3659 | 122.2947 | 0.14901 | 0.045779 | -0.20742 | 122.4169 | 122.3743 | 122.5755 | 122.3204 | -0.085923 | 122.3806 | 122.4609 | 122.2077 | 122.3469 | -0.26943
1990.8594 | 122.5388 | -122.2549 | 0.082397 | 1.4211e-13 | -0.029609 | 0.014039 | -0.0040665 | -0.013401 | 0.018629 | -0.24059 | 0.018012 | 0.018462 | 0.015385 | 0.034795 | 0.0090396 | 0.055988 | 0.010564 | 0.023639 | 0.11165 | 0.064464 | 0.27475 | 0.023942 | 0.046835 | 0.03241 | -0.015143 | 0.066194 | 0.15564 | -0.10214 | -0.16415 | 122.2789 | 0.02925 | 122.3109 | 122.2786 | -0.000303 | -0.017933 | 0.19235 | 122.0908 | -0.016203 | 122.3018 | 122.2398 | 0.14901 | 0.073246 | -0.18453 | 122.3666 | 122.3194 | 122.5297 | 122.2655 | -0.058455 | 122.3211 | 122.4106 | 122.1528 | 122.2874 | -0.24655
1992.6094 | 122.5891 | -122.2687 | 0.068665 | 1.4211e-13 | -0.029609 | 0.014039 | -0.0036391 | -0.013401 | 0.018416 | -0.23296 | 0.018439 | 0.018889 | 0.015598 | 0.035008 | 0.0090396 | 0.05141 | 0.005985 | 0.01906 | 0.11165 | 0.059885 | 0.27475 | 0.023942 | 0.055992 | 0.027831 | -0.015143 | 0.066194 | 0.16022 | -0.042614 | -0.15957 | 122.2926 | 0.042982 | 122.3201 | 122.2877 | -0.004882 | -0.00878 | 0.20608 | 122.1091 | -0.002471 | 122.3247 | 122.2535 | 0.14443 | 0.091557 | -0.11128 | 122.3803 | 122.3286 | 122.5434 | 122.2747 | -0.044723 | 122.3349 | 122.4289 | 122.2261 | 122.2965 | -0.22823
1994.375 | 122.5891 | -122.2778 | 0.086975 | 1.4211e-13 | -0.029395 | 0.013825 | -0.0038527 | -0.013401 | 0.018843 | -0.24059 | 0.018439 | 0.018462 | 0.015598 | 0.034581 | 0.0092534 | 0.046831 | 0.015142 | 0.014482 | 0.11165 | 0.059885 | 0.26559 | 0.023942 | 0.055992 | 0.03241 | -0.015143 | 0.061616 | 0.15564 | -0.092979 | -0.17331 | 122.3018 | 0.024672 | 122.3247 | 122.2923 | -0.00946 | -0.02709 | 0.17861 | 122.1045 | -0.025359 | 122.3338 | 122.2627 | 0.15816 | 0.068668 | -0.17995 | 122.3895 | 122.3377 | 122.5434 | 122.293 | -0.063033 | 122.3394 | 122.4335 | 122.1849 | 122.3102 | -0.26028
1996.0625 | 122.5342 | -122.2961 | 0.1236 | 1.4211e-13 | -0.029395 | 0.013825 | -0.0036391 | -0.01276 | 0.018629 | -0.23296 | 0.018012 | 0.018462 | 0.015385 | 0.034581 | 0.0092534 | 0.055988 | 0.015142 | 0.028217 | 0.11622 | 0.064464 | 0.27017 | 0.019363 | 0.055992 | 0.027831 | -0.010564 | 0.066194 | 0.15107 | -0.12045 | -0.16415 | 122.3155 | -0.007371 | 122.3521 | 122.3244 | 0.008854 | -0.059132 | 0.14657 | 122.132 | -0.057402 | 122.3521 | 122.2856 | 0.15358 | 0.027469 | -0.24405 | 122.4124 | 122.3606 | 122.5663 | 122.3113 | -0.10423 | 122.3623 | 122.4472 | 122.1757 | 122.324 | -0.28774
1997.8125 | 122.4838 | -122.287 | 0.10529 | 1.4211e-13 | -0.029609 | 0.014039 | -0.0034253 | -0.013187 | 0.018843 | -0.23296 | 0.018012 | 0.018676 | 0.015598 | 0.034795 | 0.0090396 | 0.05141 | 0.015142 | 0.023639 | 0.11165 | 0.059885 | 0.27932 | 0.023942 | 0.051413 | 0.03241 | -0.019721 | 0.066194 | 0.15564 | -0.079243 | -0.16415 | 122.3109 | 0.006361 | 122.3384 | 122.3106 | -0.000303 | -0.045401 | 0.17404 | 122.1228 | -0.039092 | 122.3384 | 122.2673 | 0.14443 | 0.050357 | -0.18453 | 122.3986 | 122.3469 | 122.5663 | 122.3021 | -0.081344 | 122.3532 | 122.4426 | 122.2077 | 122.3194 | -0.26943
1999.5625 | 122.4655 | -122.3007 | 0.1236 | 1.4211e-13 | -0.029822 | 0.013825 | -0.0038527 | -0.012974 | 0.018629 | -0.23296 | 0.018225 | 0.018676 | 0.015598 | 0.034795 | 0.0090396 | 0.055988 | 0.005985 | 0.01906 | 0.11165 | 0.059885 | 0.27017 | 0.019363 | 0.055992 | 0.036989 | -0.015143 | 0.070773 | 0.16022 | -0.083821 | -0.16873 | 122.3201 | -0.011949 | 122.3567 | 122.3198 | -0.000303 | -0.063711 | 0.14657 | 122.132 | -0.052823 | 122.3567 | 122.2856 | 0.15358 | 0.036626 | -0.20742 | 122.4124 | 122.3606 | 122.5709 | 122.3067 | -0.10423 | 122.3715 | 122.4609 | 122.2169 | 122.3377 | -0.29232
2001.2344 | 122.5708 | -122.2733 | 0.07782 | 1.4211e-13 | -0.029395 | 0.013825 | -0.0044937 | -0.013401 | 0.018629 | -0.22533 | 0.017798 | 0.018676 | 0.015385 | 0.034795 | 0.0090396 | 0.055988 | 0.005985 | 0.014482 | 0.10707 | 0.059885 | 0.27017 | 0.019363 | 0.055992 | 0.03241 | -0.005985 | 0.070773 | 0.1648 | -0.10214 | -0.16415 | 122.2926 | 0.029248 | 122.3292 | 122.2877 | -0.004881 | -0.017935 | 0.19235 | 122.1091 | -0.007047 | 122.3292 | 122.2673 | 0.15816 | 0.08698 | -0.17996 | 122.3803 | 122.3331 | 122.5434 | 122.2792 | -0.058457 | 122.344 | 122.4381 | 122.1711 | 122.3057 | -0.24197
2002.9688 | 122.4701 | -122.3373 | 0.12817 | 1.4211e-13 | -0.029822 | 0.014252 | -0.0036391 | -0.013401 | 0.019057 | -0.23296 | 0.018012 | 0.018462 | 0.015598 | 0.034581 | 0.008826 | 0.055988 | 0.010564 | 0.023639 | 0.11622 | 0.055306 | 0.27017 | 0.019363 | 0.060571 | 0.027831 | -0.015143 | 0.066194 | 0.15107 | -0.11129 | -0.16415 | 122.3567 | -0.011949 | 122.3933 | 122.361 | 0.004276 | -0.072868 | 0.14199 | 122.1732 | -0.06198 | 122.3979 | 122.3222 | 0.14901 | 0.022891 | -0.23947 | 122.4536 | 122.3926 | 122.6075 | 122.3479 | -0.10881 | 122.4035 | 122.4884 | 122.226 | 122.3652 | -0.29232
2004.7031 | 122.4976 | -122.2916 | 0.11444 | 1.4211e-13 | -0.029822 | 0.014039 | -0.0042801 | -0.013187 | 0.018629 | -0.23296 | 0.018225 | 0.018676 | 0.015385 | 0.034367 | 0.0090396 | 0.055988 | 0.010564 | 0.014482 | 0.1208 | 0.059885 | 0.27475 | -0.003531 | 0.051413 | 0.03241 | -0.005985 | 0.070773 | 0.15564 | -0.05635 | -0.16415 | 122.288 | 0.006363 | 122.3476 | 122.306 | 0.018013 | -0.054556 | 0.1603 | 122.1274 | -0.043668 | 122.343 | 122.2856 | 0.15816 | 0.041202 | -0.17079 | 122.4124 | 122.3514 | 122.5663 | 122.3021 | -0.11797 | 122.3623 | 122.4472 | 122.2352 | 122.324 | -0.27859
2006.4531 | 122.6212 | -122.2824 | 0.07782 | 1.4211e-13 | -0.029181 | 0.013825 | -0.0040665 | -0.013401 | 0.018629 | -0.24059 | 0.018225 | 0.018889 | 0.015385 | 0.034581 | 0.0092534 | 0.060567 | 0.010564 | 0.023639 | 0.11622 | 0.064464 | 0.27475 | 0.023942 | 0.060571 | 0.03241 | -0.015143 | 0.066194 | 0.16022 | -0.05635 | -0.15957 | 122.3064 | 0.038405 | 122.343 | 122.306 | -0.000303 | -0.013356 | 0.19693 | 122.1228 | -0.011626 | 122.343 | 122.2673 | 0.14443 | 0.082402 | -0.13417 | 122.3986 | 122.3469 | 122.5572 | 122.293 | -0.053878 | 122.3486 | 122.4426 | 122.2261 | 122.3148 | -0.23739
2008.125 | 122.5296 | -122.3053 | 0.11444 | 1.4211e-13 | -0.029181 | 0.014039 | -0.0040665 | -0.013187 | 0.018416 | -0.23296 | 0.018225 | 0.018676 | 0.015812 | 0.034581 | 0.0090396 | 0.060567 | 0.005985 | 0.01906 | 0.11165 | 0.069043 | 0.27475 | 0.023942 | 0.051413 | 0.03241 | -0.015143 | 0.061616 | 0.1648 | -0.05635 | -0.15957 | 122.3292 | -0.002794 | 122.3659 | 122.3244 | -0.004882 | -0.045398 | 0.1603 | 122.1457 | -0.052825 | 122.3567 | 122.2902 | 0.14443 | 0.050359 | -0.17079 | 122.4169 | 122.3743 | 122.58 | 122.3113 | -0.090499 | 122.3669 | 122.4701 | 122.2489 | 122.3377 | -0.27401
2009.875 | 122.5571 | -122.2961 | 0.086975 | 1.4211e-13 | -0.029181 | 0.014039 | -0.0038527 | -0.013401 | 0.018629 | -0.22533 | 0.018439 | 0.018889 | 0.015598 | 0.034795 | 0.0090396 | 0.05141 | 0.010564 | 0.014482 | 0.11165 | 0.064464 | 0.27017 | 0.023942 | 0.051413 | 0.036989 | -0.010564 | 0.075351 | 0.16022 | -0.051771 | -0.16415 | 122.3201 | 0.024672 | 122.3476 | 122.3106 | -0.00946 | -0.022511 | 0.18319 | 122.132 | -0.011624 | 122.3476 | 122.2856 | 0.15358 | 0.073247 | -0.13875 | 122.4078 | 122.3606 | 122.5663 | 122.3067 | -0.063033 | 122.3715 | 122.4564 | 122.2444 | 122.3331 | -0.25112
2011.5625 | 122.4564 | -122.3236 | 0.11444 | 1.4211e-13 | -0.029609 | 0.014252 | -0.0036391 | -0.013401 | 0.018629 | -0.2177 | 0.018012 | 0.018249 | 0.015598 | 0.034581 | 0.0092534 | 0.05141 | 0.005985 | 0.014482 | 0.11165 | 0.055306 | 0.27017 | 0.023942 | 0.051413 | 0.03241 | -0.015143 | 0.070773 | 0.1648 | -0.12045 | -0.16873 | 122.3475 | -0.002794 | 122.375 | 122.3381 | -0.00946 | -0.059135 | 0.15573 | 122.1549 | -0.043668 | 122.375 | 122.3085 | 0.15358 | 0.050359 | -0.23489 | 122.4353 | 122.3789 | 122.5938 | 122.3296 | -0.090499 | 122.3944 | 122.4884 | 122.2032 | 122.356 | -0.28317
2013.2344 | 122.5983 | -122.2733 | 0.07782 | 1.4211e-13 | -0.029609 | 0.014252 | -0.0040665 | -0.013187 | 0.018629 | -0.24059 | 0.018012 | 0.018462 | 0.016026 | 0.035222 | 0.0092534 | 0.055988 | 0.005985 | 0.014482 | 0.11165 | 0.064464 | 0.27475 | 0.023942 | 0.060571 | 0.027831 | -0.010564 | 0.075351 | 0.16022 | -0.097557 | -0.16415 | 122.2972 | 0.033827 | 122.3292 | 122.2877 | -0.00946 | -0.013356 | 0.19693 | 122.1091 | -0.002469 | 122.3338 | 122.2627 | 0.15358 | 0.082402 | -0.17538 | 122.3849 | 122.3377 | 122.548 | 122.2792 | -0.053878 | 122.3486 | 122.4335 | 122.1757 | 122.3011 | -0.24197
2014.9688 | 122.6028 | -122.2916 | 0.082397 | 1.4211e-13 | -0.029609 | 0.013825 | -0.0040665 | -0.013401 | 0.018629 | -0.2177 | 0.018012 | 0.018676 | 0.015171 | 0.034581 | 0.0090396 | 0.069723 | 0.005985 | 0.014482 | 0.11165 | 0.059885 | 0.27017 | 0.019363 | 0.051413 | 0.027831 | -0.010564 | 0.066194 | 0.15564 | -0.12503 | -0.16873 | 122.3109 | 0.02925 | 122.3613 | 122.306 | -0.004881 | -0.022512 | 0.18777 | 122.1228 | -0.016203 | 122.343 | 122.281 | 0.15816 | 0.073246 | -0.20743 | 122.4032 | 122.3514 | 122.5617 | 122.2976 | -0.063034 | 122.3578 | 122.4472 | 122.1665 | 122.3194 | -0.25112
2016.6562 | 122.4655 | -122.3282 | 0.1236 | 1.4211e-13 | -0.029395 | 0.013825 | -0.0038527 | -0.012974 | 0.018843 | -0.24059 | 0.018225 | 0.018462 | 0.015598 | 0.034795 | 0.0090396 | 0.05141 | 0.010564 | 0.009904 | 0.1208 | 0.059885 | 0.27475 | 0.023942 | 0.051413 | 0.03241 | -0.010564 | 0.066194 | 0.16022 | -0.097557 | -0.15957 | 122.3521 | -0.002792 | 122.3796 | 122.3381 | -0.014038 | -0.063711 | 0.15115 | 122.1686 | -0.057402 | 122.3796 | 122.3176 | 0.14901 | 0.036626 | -0.22115 | 122.449 | 122.3881 | 122.6029 | 122.3388 | -0.099654 | 122.3944 | 122.4884 | 122.2306 | 122.3606 | -0.28317
2018.4062 | 122.6028 | -122.3145 | 0.091553 | 1.4211e-13 | -0.029395 | 0.014252 | -0.0038527 | -0.013401 | 0.018416 | -0.24059 | 0.018225 | 0.018462 | 0.015598 | 0.034795 | 0.0092534 | 0.055988 | 0.001407 | 0.023639 | 0.10707 | 0.064464 | 0.27017 | 0.019363 | 0.060571 | 0.036989 | -0.015143 | 0.066194 | 0.16022 | -0.065507 | -0.16415 | 122.3338 | 0.015515 | 122.3704 | 122.3381 | 0.004276 | -0.027089 | 0.17861 | 122.1503 | -0.025359 | 122.375 | 122.2993 | 0.14901 | 0.068669 | -0.15706 | 122.4215 | 122.3789 | 122.5846 | 122.3159 | -0.07219 | 122.3806 | 122.4747 | 122.2489 | 122.3514 | -0.2557
2020.1406 | 122.6166 | -122.3145 | 0.091553 | 1.4211e-13 | -0.029609 | 0.014039 | -0.0038527 | -0.013187 | 0.019057 | -0.23296 | 0.018012 | 0.018462 | 0.015598 | 0.034795 | 0.008826 | 0.060567 | 0.001407 | 0.01906 | 0.1208 | 0.064464 | 0.27475 | 0.019363 | 0.055992 | 0.036989 | -0.015143 | 0.075351 | 0.15564 | -0.11587 | -0.16415 | 122.3338 | 0.029251 | 122.375 | 122.3335 | -0.000303 | -0.027089 | 0.18319 | 122.1503 | -0.016202 | 122.3704 | 122.2993 | 0.14901 | 0.06409 | -0.20742 | 122.4353 | 122.3789 | 122.5892 | 122.3159 | -0.07219 | 122.3898 | 122.4701 | 122.1986 | 122.3514 | -0.2557
2021.8906 | 122.4838 | -122.3328 | 0.11444 | 1.4211e-13 | -0.029609 | 0.013825 | -0.0034253 | -0.013401 | 0.018416 | -0.23296 | 0.018012 | 0.018462 | 0.015385 | 0.034795 | 0.009467 | 0.05141 | 0.005985 | 0.023639 | 0.11165 | 0.059885 | 0.26101 | 0.023942 | 0.060571 | 0.027831 | -0.015143 | 0.070773 | 0.16022 | -0.12045 | -0.16873 | 122.3567 | -0.002794 | 122.3842 | 122.3564 | -0.000303 | -0.054556 | 0.14657 | 122.164 | -0.043668 | 122.3933 | 122.3176 | 0.15358 | 0.045781 | -0.23489 | 122.4444 | 122.3926 | 122.5938 | 122.3387 | -0.090499 | 122.4035 | 122.493 | 122.2123 | 122.3606 | -0.28317
2023.5781 | 122.5296 | -122.3328 | 0.11444 | 1.4211e-13 | -0.029395 | 0.014252 | -0.0038527 | -0.013187 | 0.018629 | -0.23296 | 0.017798 | 0.018462 | 0.015598 | 0.034795 | 0.0090396 | 0.055988 | 0.005985 | 0.01906 | 0.11622 | 0.059885 | 0.26559 | 0.014784 | 0.060571 | 0.03241 | -0.015143 | 0.070773 | 0.16022 | -0.097557 | -0.16873 | 122.3475 | 0.001784 | 122.3888 | 122.3518 | 0.004276 | -0.054556 | 0.15115 | 122.164 | -0.043668 | 122.3933 | 122.3176 | 0.15358 | 0.045781 | -0.212 | 122.449 | 122.3926 | 122.5984 | 122.3387 | -0.099657 | 122.4035 | 122.493 | 122.2352 | 122.3652 | -0.28317
2025.3125 | 122.525 | -122.3328 | 0.10986 | 1.4211e-13 | -0.029395 | 0.014039 | -0.0036391 | -0.013615 | 0.018629 | -0.24059 | 0.018225 | 0.018676 | 0.015171 | 0.035222 | 0.0092534 | 0.060567 | 0.005985 | 0.01906 | 0.11622 | 0.064464 | 0.27017 | 0.019363 | 0.060571 | 0.036989 | -0.019721 | 0.075351 | 0.16022 | -0.097557 | -0.16873 | 122.3521 | 0.006362 | 122.3933 | 122.3518 | -0.000303 | -0.045399 | 0.1603 | 122.164 | -0.034512 | 122.3933 | 122.313 | 0.14901 | 0.050359 | -0.20742 | 122.449 | 122.3972 | 122.6029 | 122.3387 | -0.0905 | 122.4081 | 122.493 | 122.2352 | 122.3698 | -0.27859
2027.0469 | 122.5845 | -122.3053 | 0.09613 | 1.4211e-13 | -0.029609 | 0.014252 | -0.0038527 | -0.013187 | 0.018629 | -0.23296 | 0.018012 | 0.018676 | 0.015385 | 0.034581 | 0.0090396 | 0.060567 | 0.005985 | 0.01906 | 0.11165 | 0.055306 | 0.27017 | 0.037679 | 0.051413 | 0.036989 | -0.010564 | 0.066194 | 0.15107 | -0.079243 | -0.16415 | 122.343 | 0.015517 | 122.3659 | 122.3244 | -0.018619 | -0.040824 | 0.17404 | 122.1411 | -0.029936 | 122.3567 | 122.2947 | 0.15358 | 0.054935 | -0.17537 | 122.4169 | 122.3606 | 122.5755 | 122.3113 | -0.058451 | 122.3715 | 122.4564 | 122.2261 | 122.3423 | -0.26028
2028.7969 | 122.5433 | -122.3282 | 0.09613 | 1.4211e-13 | -0.029609 | 0.014039 | -0.0036391 | -0.012974 | 0.018843 | -0.23296 | 0.018439 | 0.018676 | 0.015812 | 0.034581 | 0.0090396 | 0.055988 | 0.005985 | 0.01906 | 0.10707 | 0.059885 | 0.27017 | 0.023942 | 0.042256 | 0.03241 | -0.010564 | 0.066194 | 0.15564 | -0.11587 | -0.16415 | 122.3521 | 0.010938 | 122.3842 | 122.3472 | -0.004882 | -0.036245 | 0.17404 | 122.164 | -0.029936 | 122.3704 | 122.3176 | 0.15358 | 0.059513 | -0.212 | 122.4353 | 122.3881 | 122.5984 | 122.3342 | -0.072188 | 122.3944 | 122.4838 | 122.2123 | 122.3606 | -0.26028
2030.4688 | 122.5983 | -122.3145 | 0.086975 | 1.4211e-13 | -0.029609 | 0.013825 | -0.0036391 | -0.013187 | 0.018629 | -0.23296 | 0.018012 | 0.018676 | 0.015385 | 0.035008 | 0.0092534 | 0.046831 | 0.005985 | 0.023639 | 0.11165 | 0.059885 | 0.26559 | 0.019363 | 0.060571 | 0.03241 | -0.019721 | 0.066194 | 0.16022 | -0.060928 | -0.16415 | 122.3338 | 0.024672 | 122.3613 | 122.3381 | 0.004276 | -0.02709 | 0.17861 | 122.1503 | -0.020781 | 122.375 | 122.2947 | 0.14443 | 0.073247 | -0.1479 | 122.4261 | 122.3743 | 122.58 | 122.3204 | -0.067612 | 122.3806 | 122.4747 | 122.2535 | 122.3469 | -0.25112
2032.2031 | 122.5662 | -122.3236 | 0.10071 | 1.4211e-13 | -0.029395 | 0.014039 | -0.0036391 | -0.013401 | 0.018629 | -0.24059 | 0.018012 | 0.018676 | 0.015385 | 0.034795 | 0.0092534 | 0.060567 | 0.010564 | 0.028217 | 0.1208 | 0.055306 | 0.27475 | 0.019363 | 0.051413 | 0.036989 | -0.0243 | 0.070773 | 0.15564 | -0.10214 | -0.16415 | 122.343 | 0.020096 | 122.3842 | 122.3518 | 0.008854 | -0.045402 | 0.17404 | 122.1595 | -0.029935 | 122.375 | 122.2993 | 0.13985 | 0.054935 | -0.20284 | 122.4444 | 122.3789 | 122.5984 | 122.3342 | -0.081345 | 122.3944 | 122.4793 | 122.2215 | 122.3606 | -0.26486
2033.9531 | 122.5754 | -122.319 | 0.09613 | 1.4211e-13 | -0.029181 | 0.014466 | -0.0036391 | -0.013401 | 0.018629 | -0.23296 | 0.018225 | 0.018676 | 0.015385 | 0.035008 | 0.0090396 | 0.055988 | 0.015142 | 0.023639 | 0.11165 | 0.059885 | 0.27475 | 0.023942 | 0.051413 | 0.023253 | -0.010564 | 0.070773 | 0.16022 | -0.11129 | -0.16873 | 122.343 | 0.015517 | 122.375 | 122.3427 | -0.000303 | -0.036245 | 0.17862 | 122.1503 | -0.025357 | 122.3704 | 122.3085 | 0.15816 | 0.064092 | -0.20742 | 122.4307 | 122.3789 | 122.5938 | 122.3342 | -0.072188 | 122.3898 | 122.4793 | 122.2077 | 122.3423 | -0.26486
2035.625 | 122.5021 | -122.3511 | 0.13733 | 1.4211e-13 | -0.029609 | 0.014252 | -0.0038527 | -0.013187 | 0.019057 | -0.22533 | 0.018439 | 0.018676 | 0.015385 | 0.034795 | 0.008826 | 0.055988 | 0.010564 | 0.01906 | 0.11622 | 0.059885 | 0.27475 | 0.023942 | 0.055992 | 0.036989 | -0.019721 | 0.066194 | 0.1648 | -0.097557 | -0.15957 | 122.375 | -0.021104 | 122.4071 | 122.3701 | -0.004882 | -0.077444 | 0.13742 | 122.1915 | -0.071135 | 122.4071 | 122.3314 | 0.13985 | 0.027471 | -0.23489 | 122.4673 | 122.411 | 122.6258 | 122.3616 | -0.11339 | 122.4173 | 122.5159 | 122.2535 | 122.3881 | -0.2969
2037.3906 | 122.5754 | -122.3145 | 0.091553 | 1.4211e-13 | -0.029395 | 0.014252 | -0.0038527 | -0.013187 | 0.018629 | -0.23296 | 0.018225 | 0.018249 | 0.015385 | 0.034581 | 0.0090396 | 0.065145 | 0.005985 | 0.01906 | 0.11622 | 0.073622 | 0.27475 | 0.023942 | 0.051413 | 0.03241 | -0.0243 | 0.066194 | 0.1648 | -0.079243 | -0.16873 | 122.3384 | 0.024672 | 122.3796 | 122.3335 | -0.004882 | -0.017931 | 0.18319 | 122.1457 | -0.025359 | 122.3659 | 122.2902 | 0.14443 | 0.073247 | -0.1708 | 122.4307 | 122.3881 | 122.5892 | 122.3204 | -0.067611 | 122.3806 | 122.4793 | 122.2352 | 122.3469 | -0.26028
2039.0625 | 122.5067 | -122.374 | 0.11902 | 1.4211e-13 | -0.029609 | 0.014466 | -0.0038527 | -0.013187 | 0.018843 | -0.22533 | 0.018225 | 0.018676 | 0.015385 | 0.034795 | 0.0092534 | 0.060567 | 0.019721 | 0.01906 | 0.11165 | 0.059885 | 0.27017 | 0.028521 | 0.055992 | 0.03241 | -0.015143 | 0.070773 | 0.15564 | -0.10671 | -0.16415 | 122.4025 | -0.007372 | 122.4345 | 122.393 | -0.009461 | -0.059134 | 0.15115 | 122.2098 | -0.048246 | 122.43 | 122.3588 | 0.14901 | 0.036624 | -0.22573 | 122.4856 | 122.4338 | 122.6441 | 122.3937 | -0.090498 | 122.4447 | 122.5296 | 122.2672 | 122.4064 | -0.28317
2040.7969 | 122.5571 | -122.3602 | 0.13275 | 1.4211e-13 | -0.029395 | 0.013825 | -0.0038527 | -0.012974 | 0.018629 | -0.23296 | 0.018012 | 0.018676 | 0.015598 | 0.034367 | 0.0092534 | 0.065145 | 0.005985 | 0.023639 | 0.12538 | 0.059885 | 0.26559 | 0.023942 | 0.055992 | 0.036989 | -0.015143 | 0.066194 | 0.16022 | -0.079243 | -0.16873 | 122.3842 | -0.007369 | 122.4254 | 122.3839 | -0.000303 | -0.072866 | 0.13284 | 122.1915 | -0.066557 | 122.4162 | 122.3451 | 0.15358 | 0.027471 | -0.21199 | 122.4856 | 122.4201 | 122.6258 | 122.3662 | -0.10881 | 122.4264 | 122.5205 | 122.281 | 122.3972 | -0.30148
2042.5 | 122.5845 | -122.3373 | 0.091553 | 1.4211e-13 | -0.029181 | 0.014252 | -0.0040665 | -0.013401 | 0.018629 | -0.24059 | 0.018225 | 0.018676 | 0.015385 | 0.034581 | 0.0090396 | 0.060567 | 0.010564 | 0.01906 | 0.11622 | 0.055306 | 0.27017 | 0.023942 | 0.055992 | 0.03241 | -0.010564 | 0.066194 | 0.16022 | -0.092979 | -0.15957 | 122.3613 | 0.024672 | 122.3979 | 122.3564 | -0.004882 | -0.036247 | 0.17861 | 122.1778 | -0.025359 | 122.3933 | 122.3268 | 0.14901 | 0.068669 | -0.18453 | 122.4536 | 122.3926 | 122.6075 | 122.3479 | -0.067611 | 122.4035 | 122.4976 | 122.2444 | 122.3698 | -0.25112
2044.25 | 122.6395 | -122.3282 | 0.09613 | 1.4211e-13 | -0.029609 | 0.013825 | -0.0040665 | -0.013401 | 0.018843 | -0.24059 | 0.018225 | 0.018462 | 0.015598 | 0.034581 | 0.0092534 | 0.055988 | 0.010564 | 0.023639 | 0.10707 | 0.059885 | 0.27475 | 0.019363 | 0.055992 | 0.036989 | -0.015143 | 0.070773 | 0.16022 | -0.051771 | -0.16415 | 122.3475 | 0.010938 | 122.3842 | 122.3518 | 0.004276 | -0.036245 | 0.17862 | 122.164 | -0.025357 | 122.3842 | 122.313 | 0.14901 | 0.064092 | -0.1479 | 122.4353 | 122.3881 | 122.6029 | 122.3388 | -0.076767 | 122.399 | 122.4884 | 122.2764 | 122.3652 | -0.26028
2046 | 122.5204 | -122.374 | 0.11444 | 1.4211e-13 | -0.029609 | 0.014039 | -0.0038527 | -0.013187 | 0.018629 | -0.2177 | 0.018225 | 0.018462 | 0.015385 | 0.034795 | 0.0090396 | 0.060567 | 0.005985 | 0.01906 | 0.11165 | 0.059885 | 0.27932 | 0.019363 | 0.060571 | 0.03241 | -0.015143 | 0.070773 | 0.16022 | -0.074664 | -0.16873 | 122.3933 | -0.002794 | 122.4345 | 122.393 | -0.000303 | -0.054556 | 0.16488 | 122.2052 | -0.043668 | 122.4345 | 122.3588 | 0.15358 | 0.045781 | -0.1891 | 122.4856 | 122.4338 | 122.6533 | 122.3799 | -0.095078 | 122.4447 | 122.5342 | 122.2993 | 122.4064 | -0.28317
2047.6719 | 122.5891 | -122.3557 | 0.09613 | 1.4211e-13 | -0.029609 | 0.014039 | -0.0038527 | -0.013615 | 0.018416 | -0.23296 | 0.018012 | 0.018249 | 0.015598 | 0.034367 | 0.0090396 | 0.055988 | 0.010564 | 0.014482 | 0.11165 | 0.059885 | 0.27932 | 0.019363 | 0.051413 | 0.036989 | -0.019721 | 0.070773 | 0.15564 | -0.065507 | -0.16873 | 122.375 | 0.015517 | 122.4116 | 122.3701 | -0.004881 | -0.036245 | 0.18319 | 122.1869 | -0.025357 | 122.4071 | 122.3359 | 0.14901 | 0.059513 | -0.16164 | 122.4673 | 122.4155 | 122.635 | 122.3662 | -0.076767 | 122.4264 | 122.5113 | 122.2901 | 122.3926 | -0.26486
2049.4219 | 122.5891 | -122.3419 | 0.10071 | 1.4211e-13 | -0.029609 | 0.013825 | -0.0038527 | -0.013187 | 0.018416 | -0.23296 | 0.018225 | 0.018676 | 0.015385 | 0.034367 | 0.008826 | 0.060567 | 0.015142 | 0.023639 | 0.11622 | 0.064464 | 0.27017 | 0.014784 | 0.055992 | 0.027831 | -0.010564 | 0.066194 | 0.15564 | -0.083821 | -0.15957 | 122.3567 | 0.015517 | 122.4025 | 122.3656 | 0.008855 | -0.036244 | 0.16946 | 122.1823 | -0.034514 | 122.3979 | 122.3314 | 0.14901 | 0.054935 | -0.18453 | 122.4581 | 122.4064 | 122.6121 | 122.3571 | -0.085924 | 122.4081 | 122.4976 | 122.2581 | 122.3698 | -0.26028
2051.1562 | 122.5159 | -122.3877 | 0.13733 | 1.4211e-13 | -0.029395 | 0.014039 | -0.0038527 | -0.013187 | 0.018843 | -0.22533 | 0.018012 | 0.018889 | 0.015385 | 0.034795 | 0.0090396 | 0.060567 | 0.010564 | 0.014482 | 0.11165 | 0.064464 | 0.27017 | 0.014784 | 0.060571 | 0.023253 | -0.015143 | 0.070773 | 0.15107 | -0.12045 | -0.16415 | 122.4025 | -0.025682 | 122.4483 | 122.4022 | -0.000302 | -0.072865 | 0.13284 | 122.2235 | -0.066556 | 122.4483 | 122.3726 | 0.14901 | 0.013736 | -0.25778 | 122.4993 | 122.4522 | 122.6579 | 122.3983 | -0.12255 | 122.4585 | 122.5388 | 122.2672 | 122.4109 | -0.30148
2052.9062 | 122.6212 | -122.3373 | 0.082397 | 1.4211e-13 | -0.029181 | 0.014252 | -0.0036391 | -0.013187 | 0.018843 | -0.24059 | 0.018012 | 0.018676 | 0.015385 | 0.034581 | 0.008826 | 0.05141 | 0.015142 | 0.014482 | 0.11165 | 0.059885 | 0.27017 | 0.019363 | 0.051413 | 0.03241 | -0.019721 | 0.070773 | 0.16022 | -0.038035 | -0.16415 | 122.3567 | 0.02925 | 122.3888 | 122.3518 | -0.004881 | -0.022512 | 0.18777 | 122.1732 | -0.011624 | 122.3888 | 122.3176 | 0.14443 | 0.077825 | -0.12043 | 122.449 | 122.3972 | 122.6075 | 122.3525 | -0.063034 | 122.4081 | 122.4976 | 122.2993 | 122.3698 | -0.24655
2054.5781 | 122.5662 | -122.3557 | 0.1236 | 1.4211e-13 | -0.029609 | 0.013825 | -0.0040665 | -0.013187 | 0.018843 | -0.24822 | 0.018225 | 0.018676 | 0.015385 | 0.034581 | 0.0090396 | 0.060567 | 0.005985 | 0.01906 | 0.1208 | 0.059885 | 0.27475 | 0.023942 | 0.046835 | 0.027831 | -0.010564 | 0.070773 | 0.16022 | -0.074664 | -0.16873 | 122.3796 | -0.002792 | 122.4162 | 122.3747 | -0.004882 | -0.063711 | 0.15115 | 122.1869 | -0.052823 | 122.4025 | 122.3451 | 0.15816 | 0.036626 | -0.19826 | 122.4765 | 122.4155 | 122.6304 | 122.3616 | -0.099654 | 122.4264 | 122.5159 | 122.281 | 122.3835 | -0.29232
2056.3281 | 122.6349 | -122.3099 | 0.07782 | 1.4211e-13 | -0.029609 | 0.013825 | -0.0040665 | -0.013401 | 0.018629 | -0.24059 | 0.018012 | 0.018676 | 0.015385 | 0.035008 | 0.008826 | 0.060567 | 0.010564 | 0.032795 | 0.10707 | 0.064464 | 0.27017 | 0.023942 | 0.055992 | 0.027831 | -0.019721 | 0.066194 | 0.16022 | -0.092979 | -0.15957 | 122.3338 | 0.029248 | 122.3704 | 122.3427 | 0.008853 | -0.013356 | 0.19235 | 122.1503 | -0.011626 | 122.3659 | 122.2902 | 0.13985 | 0.082402 | -0.1708 | 122.4169 | 122.3743 | 122.58 | 122.3204 | -0.053878 | 122.3761 | 122.4701 | 122.2169 | 122.3377 | -0.23739
2058.0781 | 122.6486 | -122.3419 | 0.086975 | 1.4211e-13 | -0.029395 | 0.014039 | -0.0036391 | -0.013401 | 0.018416 | -0.22533 | 0.017798 | 0.018462 | 0.015385 | 0.034367 | 0.0090396 | 0.060567 | 0.019721 | 0.023639 | 0.11622 | 0.069043 | 0.27932 | 0.019363 | 0.046835 | 0.03241 | -0.010564 | 0.066194 | 0.16022 | -0.083821 | -0.16415 | 122.3613 | 0.02925 | 122.4025 | 122.3656 | 0.004276 | -0.017932 | 0.19235 | 122.1778 | -0.020781 | 122.3888 | 122.3314 | 0.15358 | 0.073247 | -0.1708 | 122.4581 | 122.411 | 122.6212 | 122.3616 | -0.067612 | 122.4081 | 122.5021 | 122.2581 | 122.3743 | -0.25112
2059.8281 | 122.5159 | -122.3465 | 0.10529 | 1.4211e-13 | -0.029395 | 0.014466 | -0.0038527 | -0.013187 | 0.018843 | -0.23296 | 0.018225 | 0.018462 | 0.015598 | 0.034581 | 0.0090396 | 0.05141 | 0.005985 | 0.023639 | 0.11622 | 0.064464 | 0.27932 | 0.019363 | 0.055992 | 0.041567 | -0.019721 | 0.070773 | 0.16022 | -0.10214 | -0.16415 | 122.3659 | 0.010939 | 122.3979 | 122.3701 | 0.004276 | -0.040822 | 0.17404 | 122.1823 | -0.034513 | 122.4025 | 122.3268 | 0.14443 | 0.054936 | -0.20742 | 122.4627 | 122.411 | 122.6258 | 122.3525 | -0.085923 | 122.4173 | 122.5067 | 122.2444 | 122.3881 | -0.26943
2061.5156 | 122.5708 | -122.3557 | 0.1236 | 1.4211e-13 | -0.028968 | 0.014039 | -0.0034253 | -0.013187 | 0.018416 | -0.24822 | 0.018225 | 0.018676 | 0.015598 | 0.034795 | 0.0090396 | 0.060567 | 0.010564 | 0.023639 | 0.11165 | 0.069043 | 0.27017 | 0.023942 | 0.055992 | 0.027831 | -0.010564 | 0.061616 | 0.16022 | -0.047193 | -0.15957 | 122.3796 | -0.011949 | 122.4162 | 122.3793 | -0.000303 | -0.054553 | 0.14657 | 122.1961 | -0.06198 | 122.4116 | 122.3451 | 0.14901 | 0.036626 | -0.17079 | 122.4673 | 122.4247 | 122.6258 | 122.3662 | -0.099654 | 122.4173 | 122.5159 | 122.3085 | 122.3835 | -0.28317
2063.2656 | 122.5616 | -122.3602 | 0.11444 | 1.4211e-13 | -0.029395 | 0.013825 | -0.0038527 | -0.012974 | 0.018416 | -0.2177 | 0.018439 | 0.018462 | 0.014957 | 0.034795 | 0.0092534 | 0.05141 | 0.010564 | 0.01906 | 0.11622 | 0.064464 | 0.27017 | 0.019363 | 0.051413 | 0.03241 | -0.015143 | 0.070773 | 0.15564 | -0.010564 | -0.16873 | 122.3796 | 0.001784 | 122.4116 | 122.3793 | -0.000303 | -0.049977 | 0.15573 | 122.1915 | -0.043668 | 122.4116 | 122.3451 | 0.15358 | 0.041202 | -0.12501 | 122.4765 | 122.4247 | 122.6304 | 122.3708 | -0.095078 | 122.431 | 122.5159 | 122.3497 | 122.3926 | -0.28317
2065.0156 | 122.5983 | -122.3511 | 0.09613 | 1.4211e-13 | -0.029181 | 0.014039 | -0.0038527 | -0.013401 | 0.018843 | -0.24059 | 0.018439 | 0.018462 | 0.015171 | 0.034367 | 0.0090396 | 0.055988 | 0.010564 | 0.023639 | 0.10707 | 0.059885 | 0.27932 | 0.019363 | 0.051413 | 0.03241 | -0.015143 | 0.070773 | 0.16022 | -0.097557 | -0.16415 | 122.3704 | 0.010938 | 122.4071 | 122.3747 | 0.004276 | -0.036245 | 0.18319 | 122.1869 | -0.025357 | 122.4025 | 122.3359 | 0.14901 | 0.064092 | -0.19369 | 122.4581 | 122.411 | 122.6304 | 122.3616 | -0.076767 | 122.4218 | 122.5113 | 122.2535 | 122.3835 | -0.26028
2066.7031 | 122.6395 | -122.3465 | 0.091553 | 1.4211e-13 | -0.029181 | 0.014039 | -0.0038527 | -0.013615 | 0.018629 | -0.23296 | 0.017798 | 0.019103 | 0.015598 | 0.034795 | 0.0092534 | 0.065145 | 0.005985 | 0.01906 | 0.1208 | 0.064464 | 0.27932 | 0.023942 | 0.055992 | 0.03241 | -0.010564 | 0.066194 | 0.16022 | -0.070086 | -0.16415 | 122.3704 | 0.029251 | 122.4116 | 122.3656 | -0.004882 | -0.027089 | 0.18777 | 122.1823 | -0.025359 | 122.4025 | 122.3359 | 0.15358 | 0.068669 | -0.16164 | 122.4673 | 122.411 | 122.6258 | 122.3525 | -0.067611 | 122.4127 | 122.5067 | 122.2764 | 122.3789 | -0.2557
2068.4531 | 122.5021 | -122.3877 | 0.10071 | 1.4211e-13 | -0.029395 | 0.014039 | -0.0038527 | -0.013187 | 0.018629 | -0.23296 | 0.018012 | 0.018035 | 0.015598 | 0.034367 | 0.008826 | 0.055988 | 0.010564 | 0.01906 | 0.11622 | 0.064464 | 0.27475 | 0.023942 | 0.055992 | 0.041567 | -0.015143 | 0.075351 | 0.15564 | -0.0884 | -0.16873 | 122.4116 | 0.015517 | 122.4437 | 122.4068 | -0.004882 | -0.036244 | 0.17404 | 122.219 | -0.025357 | 122.4437 | 122.3726 | 0.15358 | 0.054935 | -0.18911 | 122.5039 | 122.4522 | 122.6624 | 122.3983 | -0.076766 | 122.463 | 122.5433 | 122.2993 | 122.4293 | -0.26944
2070.125 | 122.644 | -122.3511 | 0.086975 | 1.4211e-13 | -0.029609 | 0.014039 | -0.0034253 | -0.013187 | 0.018629 | -0.24059 | 0.018225 | 0.018462 | 0.015598 | 0.034581 | 0.0092534 | 0.055988 | 0.005985 | 0.01906 | 0.11165 | 0.059885 | 0.27475 | 0.023942 | 0.051413 | 0.03241 | -0.015143 | 0.066194 | 0.15564 | -0.047193 | -0.16873 | 122.375 | 0.024672 | 122.4071 | 122.3701 | -0.004882 | -0.02709 | 0.18777 | 122.1823 | -0.020781 | 122.4025 | 122.3359 | 0.15358 | 0.068668 | -0.13417 | 122.4627 | 122.411 | 122.6258 | 122.3571 | -0.063033 | 122.4173 | 122.5067 | 122.3039 | 122.3835 | -0.2557
2071.8594 | 122.612 | -122.3557 | 0.10071 | 1.4211e-13 | -0.029181 | 0.014039 | -0.0038527 | -0.013401 | 0.018416 | -0.24059 | 0.018012 | 0.018462 | 0.015385 | 0.034795 | 0.0090396 | 0.05141 | 0.005985 | 0.01906 | 0.11165 | 0.064464 | 0.27932 | 0.019363 | 0.055992 | 0.036989 | -0.015143 | 0.070773 | 0.14649 | -0.0243 | -0.16415 | 122.375 | 0.010939 | 122.4071 | 122.3747 | -0.000303 | -0.036244 | 0.17862 | 122.1915 | -0.029935 | 122.4116 | 122.3405 | 0.14901 | 0.045778 | -0.12501 | 122.4673 | 122.4201 | 122.635 | 122.3616 | -0.081345 | 122.4264 | 122.5021 | 122.3314 | 122.3926 | -0.26486
2073.6094 | 122.612 | -122.3557 | 0.10529 | 1.4211e-13 | -0.029609 | 0.013825 | -0.0038527 | -0.013187 | 0.018843 | -0.23296 | 0.018225 | 0.018889 | 0.015385 | 0.035008 | 0.0092534 | 0.055988 | 0.010564 | 0.01906 | 0.11165 | 0.064464 | 0.27932 | 0.019363 | 0.046835 | 0.03241 | -0.010564 | 0.075351 | 0.15564 | -0.028878 | -0.16415 | 122.375 | 0.006361 | 122.4116 | 122.3747 | -0.000303 | -0.040822 | 0.17404 | 122.1915 | -0.029935 | 122.4025 | 122.3451 | 0.15358 | 0.050357 | -0.13416 | 122.4673 | 122.4201 | 122.635 | 122.3662 | -0.085923 | 122.431 | 122.5113 | 122.3268 | 122.3881 | -0.26943
2075.3438 | 122.5571 | -122.3831 | 0.09613 | 1.4211e-13 | -0.029609 | 0.013825 | -0.0038527 | -0.013401 | 0.018629 | -0.23296 | 0.018225 | 0.018462 | 0.015598 | 0.034795 | 0.0090396 | 0.055988 | 0.010564 | 0.023639 | 0.11622 | 0.064464 | 0.27932 | 0.014784 | 0.055992 | 0.027831 | -0.019721 | 0.070773 | 0.16022 | -0.097557 | -0.16873 | 122.3979 | 0.020095 | 122.4391 | 122.4068 | 0.008855 | -0.031666 | 0.18319 | 122.2144 | -0.025357 | 122.4391 | 122.3634 | 0.14901 | 0.064092 | -0.19369 | 122.4993 | 122.4476 | 122.6624 | 122.3937 | -0.081346 | 122.4539 | 122.5433 | 122.2856 | 122.4109 | -0.26486
2077.0938 | 122.6669 | -122.3602 | 0.082397 | 1.4211e-13 | -0.029181 | 0.013825 | -0.0036391 | -0.013401 | 0.018629 | -0.23296 | 0.018225 | 0.018676 | 0.014957 | 0.034367 | 0.0090396 | 0.05141 | 0.005985 | 0.01906 | 0.11165 | 0.064464 | 0.27932 | 0.019363 | 0.055992 | 0.03241 | -0.010564 | 0.075351 | 0.16022 | -0.047193 | -0.16873 | 122.3796 | 0.02925 | 122.4116 | 122.3793 | -0.000303 | -0.017933 | 0.19693 | 122.1915 | -0.007046 | 122.4162 | 122.3497 | 0.15816 | 0.077825 | -0.12959 | 122.4719 | 122.4247 | 122.6396 | 122.3662 | -0.063034 | 122.4356 | 122.5205 | 122.313 | 122.3926 | -0.25112
2078.7812 | 122.6028 | -122.3694 | 0.11444 | 1.4211e-13 | -0.029395 | 0.014252 | -0.0040665 | -0.013401 | 0.018843 | -0.23296 | 0.018225 | 0.018249 | 0.015385 | 0.034795 | 0.0090396 | 0.055988 | 0.015142 | 0.028217 | 0.10707 | 0.059885 | 0.27017 | 0.019363 | 0.055992 | 0.036989 | -0.0243 | 0.070773 | 0.15564 | -0.11587 | -0.17331 | 122.3887 | -0.007373 | 122.4254 | 122.3976 | 0.008854 | -0.054556 | 0.15573 | 122.1961 | -0.043668 | 122.4254 | 122.3451 | 0.14901 | 0.041202 | -0.23031 | 122.4765 | 122.4293 | 122.6396 | 122.3845 | -0.095078 | 122.4402 | 122.525 | 122.2535 | 122.4064 | -0.28775
2080.5312 | 122.6852 | -122.374 | 0.073242 | 1.4211e-13 | -0.028968 | 0.014039 | -0.0038527 | -0.013401 | 0.018629 | -0.24059 | 0.018225 | 0.018676 | 0.015598 | 0.034367 | 0.009467 | 0.055988 | 0.005985 | 0.028217 | 0.11622 | 0.059885 | 0.27475 | 0.014784 | 0.055992 | 0.03241 | -0.019721 | 0.070773 | 0.15564 | -0.047193 | -0.16873 | 122.3887 | 0.042983 | 122.43 | 122.4022 | 0.013433 | -0.013357 | 0.2015 | 122.2052 | -0.002469 | 122.43 | 122.3542 | 0.14901 | 0.082401 | -0.12044 | 122.4902 | 122.4338 | 122.6487 | 122.3799 | -0.058458 | 122.4447 | 122.5296 | 122.3268 | 122.4064 | -0.24197
2082.2656 | 122.612 | -122.374 | 0.10071 | 1.4211e-13 | -0.028968 | 0.013611 | -0.0040665 | -0.013401 | 0.018843 | -0.23296 | 0.018439 | 0.018249 | 0.015598 | 0.034581 | 0.008826 | 0.060567 | 0.010564 | 0.023639 | 0.11165 | 0.064464 | 0.27932 | 0.019363 | 0.051413 | 0.03241 | -0.015143 | 0.070773 | 0.1648 | -0.070086 | -0.16415 | 122.3933 | 0.010939 | 122.4345 | 122.3976 | 0.004276 | -0.036244 | 0.17862 | 122.2098 | -0.029935 | 122.4254 | 122.3588 | 0.14901 | 0.064092 | -0.17079 | 122.4856 | 122.4384 | 122.6533 | 122.3845 | -0.081345 | 122.4447 | 122.5388 | 122.3039 | 122.4064 | -0.26486
2083.9375 | 122.6395 | -122.3511 | 0.086975 | 1.4211e-13 | -0.029181 | 0.013825 | -0.0038527 | -0.012974 | 0.018843 | -0.22533 | 0.018225 | 0.018249 | 0.015598 | 0.034581 | 0.008826 | 0.05141 | 0.015142 | 0.014482 | 0.11165 | 0.059885 | 0.27932 | 0.014784 | 0.051413 | 0.03241 | -0.015143 | 0.070773 | 0.16938 | -0.047193 | -0.16415 | 122.3659 | 0.024672 | 122.4025 | 122.3656 | -0.000302 | -0.02709 | 0.19235 | 122.1869 | -0.016202 | 122.4025 | 122.3359 | 0.14901 | 0.082404 | -0.13417 | 122.4627 | 122.411 | 122.6304 | 122.3662 | -0.072191 | 122.4218 | 122.5205 | 122.3039 | 122.3835 | -0.25112
2085.6875 | 122.5479 | -122.3969 | 0.1236 | 1.4211e-13 | -0.029181 | 0.013825 | -0.0038527 | -0.013401 | 0.018843 | -0.23296 | 0.018225 | 0.018676 | 0.015598 | 0.034367 | 0.0092534 | 0.05141 | 0.001407 | 0.01906 | 0.11165 | 0.069043 | 0.27475 | 0.023942 | 0.06515 | 0.03241 | -0.019721 | 0.070773 | 0.16022 | -0.083821 | -0.16873 | 122.4208 | -0.011949 | 122.4483 | 122.4159 | -0.004882 | -0.054553 | 0.15115 | 122.2281 | -0.052823 | 122.462 | 122.3771 | 0.14901 | 0.036626 | -0.20742 | 122.5085 | 122.4659 | 122.6716 | 122.3983 | -0.099654 | 122.4676 | 122.5571 | 122.313 | 122.4293 | -0.29232
2087.4531 | 122.5708 | -122.3923 | 0.1236 | 1.4211e-13 | -0.029395 | 0.014252 | -0.0038527 | -0.013401 | 0.018629 | -0.23296 | 0.017798 | 0.018676 | 0.015171 | 0.034581 | 0.0090396 | 0.055988 | 0.015142 | 0.014482 | 0.11622 | 0.064464 | 0.27475 | 0.019363 | 0.060571 | 0.041567 | -0.010564 | 0.070773 | 0.16938 | -0.042614 | -0.16415 | 122.4116 | -0.007371 | 122.4483 | 122.4068 | -0.004881 | -0.059132 | 0.15115 | 122.2281 | -0.052823 | 122.4528 | 122.3817 | 0.15358 | 0.045783 | -0.16621 | 122.5085 | 122.4567 | 122.667 | 122.4074 | -0.10423 | 122.463 | 122.5617 | 122.3497 | 122.4338 | -0.28774
2089.125 | 122.5433 | -122.4197 | 0.13275 | 1.4211e-13 | -0.028968 | 0.014252 | -0.0038527 | -0.01276 | 0.018629 | -0.24059 | 0.018439 | 0.018462 | 0.015385 | 0.034795 | 0.008826 | 0.055988 | 0.001407 | 0.01906 | 0.10707 | 0.059885 | 0.27017 | 0.023942 | 0.055992 | 0.036989 | -0.019721 | 0.066194 | 0.16938 | -0.079243 | -0.16415 | 122.4437 | -0.025683 | 122.4757 | 122.4388 | -0.004882 | -0.072866 | 0.13742 | 122.2556 | -0.066557 | 122.4757 | 122.4 | 0.14443 | 0.036628 | -0.21199 | 122.5268 | 122.4796 | 122.6899 | 122.4211 | -0.10881 | 122.4859 | 122.5891 | 122.3405 | 122.4567 | -0.2969
2090.875 | 122.612 | -122.3877 | 0.09613 | 1.4211e-13 | -0.029181 | 0.014039 | -0.0038527 | -0.013615 | 0.018629 | -0.24059 | 0.018012 | 0.018676 | 0.015385 | 0.034795 | 0.0090396 | 0.05141 | 0.010564 | 0.01906 | 0.11622 | 0.064464 | 0.27475 | 0.010206 | 0.060571 | 0.027831 | -0.015143 | 0.070773 | 0.16022 | -0.065507 | -0.17331 | 122.3979 | 0.020095 | 122.4391 | 122.4068 | 0.008854 | -0.031666 | 0.17862 | 122.2144 | -0.025357 | 122.4483 | 122.3726 | 0.15816 | 0.064092 | -0.16164 | 122.5039 | 122.4522 | 122.6624 | 122.3983 | -0.085924 | 122.4585 | 122.5479 | 122.3222 | 122.4155 | -0.26944
2092.625 | 122.5937 | -122.3602 | 0.10986 | 1.4211e-13 | -0.029181 | 0.014252 | -0.0038527 | -0.013187 | 0.018843 | -0.23296 | 0.018225 | 0.018462 | 0.015171 | 0.034795 | 0.0090396 | 0.060567 | 0.001407 | 0.023639 | 0.11165 | 0.064464 | 0.27017 | 0.019363 | 0.06515 | 0.03241 | -0.015143 | 0.070773 | 0.15564 | -0.042614 | -0.16873 | 122.3796 | 0.001784 | 122.4208 | 122.3839 | 0.004276 | -0.045399 | 0.1603 | 122.1915 | -0.03909 | 122.4254 | 122.3451 | 0.15358 | 0.04578 | -0.15248 | 122.4719 | 122.4247 | 122.6304 | 122.3616 | -0.0905 | 122.431 | 122.5159 | 122.3176 | 122.3926 | -0.27859
2094.3594 | 122.5433 | -122.3877 | 0.13275 | 1.4211e-13 | -0.029395 | 0.014252 | -0.0038527 | -0.013401 | 0.018843 | -0.23296 | 0.017798 | 0.018676 | 0.015598 | 0.034581 | 0.0092534 | 0.060567 | 0.010564 | 0.01906 | 0.1208 | 0.050727 | 0.27475 | 0.019363 | 0.060571 | 0.03241 | -0.010564 | 0.066194 | 0.16022 | -0.079243 | -0.16873 | 122.4071 | -0.011947 | 122.4483 | 122.4068 | -0.000303 | -0.082024 | 0.14199 | 122.219 | -0.066557 | 122.4483 | 122.3771 | 0.15816 | 0.027471 | -0.21199 | 122.5085 | 122.4384 | 122.6624 | 122.3983 | -0.11339 | 122.4539 | 122.5479 | 122.3085 | 122.4201 | -0.30148
2096.0938 | 122.6578 | -122.3694 | 0.07782 | 1.4211e-13 | -0.029181 | 0.014466 | -0.0038527 | -0.013187 | 0.018843 | -0.22533 | 0.018439 | 0.018676 | 0.015598 | 0.034795 | 0.0086124 | 0.060567 | 0.010564 | 0.01906 | 0.11622 | 0.069043 | 0.27932 | 0.014784 | 0.055992 | 0.03241 | -0.010564 | 0.075351 | 0.16938 | -0.070086 | -0.15957 | 122.3842 | 0.038405 | 122.43 | 122.3884 | 0.004276 | -0.008777 | 0.2015 | 122.2098 | -0.002469 | 122.4254 | 122.3588 | 0.14901 | 0.091559 | -0.14791 | 122.4856 | 122.4384 | 122.6487 | 122.3799 | -0.063036 | 122.4447 | 122.5388 | 122.2993 | 122.4018 | -0.23739
2097.8594 | 122.6761 | -122.3694 | 0.086975 | 1.4211e-13 | -0.029609 | 0.013825 | -0.0038527 | -0.012974 | 0.018843 | -0.23296 | 0.017798 | 0.018676 | 0.015598 | 0.034795 | 0.008826 | 0.05141 | 0.005985 | 0.014482 | 0.11165 | 0.064464 | 0.27932 | 0.019363 | 0.051413 | 0.03241 | -0.015143 | 0.075351 | 0.1648 | -0.065507 | -0.16873 | 122.3887 | 0.024672 | 122.4208 | 122.3839 | -0.004881 | -0.022511 | 0.19235 | 122.2007 | -0.011624 | 122.4208 | 122.3542 | 0.15358 | 0.077825 | -0.15248 | 122.481 | 122.4338 | 122.6487 | 122.3754 | -0.067612 | 122.4447 | 122.5342 | 122.3039 | 122.4018 | -0.2557
2099.5469 | 122.6624 | -122.406 | 0.086975 | 1.4211e-13 | -0.029395 | 0.014039 | -0.0040665 | -0.013187 | 0.018416 | -0.24059 | 0.018225 | 0.018676 | 0.015385 | 0.034367 | 0.008826 | 0.060567 | 0.001407 | 0.023639 | 0.11165 | 0.069043 | 0.27017 | 0.014784 | 0.051413 | 0.036989 | -0.015143 | 0.075351 | 0.15107 | -0.074664 | -0.15957 | 122.4208 | 0.024672 | 122.4666 | 122.4296 | 0.008855 | -0.017932 | 0.18319 | 122.2464 | -0.011624 | 122.4574 | 122.3909 | 0.14443 | 0.06409 | -0.16164 | 122.5177 | 122.475 | 122.6762 | 122.4074 | -0.072191 | 122.4814 | 122.5571 | 122.3313 | 122.443 | -0.24654
2101.2969 | 122.5662 | -122.406 | 0.11444 | 1.4211e-13 | -0.029181 | 0.013825 | -0.0038527 | -0.013187 | 0.018629 | -0.23296 | 0.018225 | 0.018462 | 0.015598 | 0.034795 | 0.0092534 | 0.055988 | 0.001407 | 0.023639 | 0.11165 | 0.059885 | 0.27932 | 0.019363 | 0.060571 | 0.03241 | -0.015143 | 0.075351 | 0.15564 | -0.038035 | -0.17331 | 122.4254 | -0.002794 | 122.462 | 122.4296 | 0.004276 | -0.054556 | 0.16488 | 122.2327 | -0.03909 | 122.4666 | 122.3909 | 0.15816 | 0.041202 | -0.15248 | 122.5177 | 122.4659 | 122.6853 | 122.4074 | -0.095078 | 122.4814 | 122.5616 | 122.368 | 122.4384 | -0.28775
2103.0312 | 122.6486 | -122.374 | 0.086975 | 1.4211e-13 | -0.029609 | 0.014039 | -0.0038527 | -0.013187 | 0.018843 | -0.24059 | 0.018439 | 0.018462 | 0.015598 | 0.034581 | 0.0090396 | 0.060567 | 0.005985 | 0.009904 | 0.11622 | 0.055306 | 0.27475 | 0.014784 | 0.055992 | 0.036989 | -0.019721 | 0.075351 | 0.15564 | -0.0884 | -0.16873 | 122.3887 | 0.02925 | 122.4345 | 122.3839 | -0.00488 | -0.031669 | 0.18777 | 122.2052 | -0.011624 | 122.43 | 122.3542 | 0.14901 | 0.068668 | -0.17538 | 122.4902 | 122.4293 | 122.6487 | 122.3799 | -0.072191 | 122.4493 | 122.5296 | 122.2856 | 122.411 | -0.2557
2104.7031 | 122.6532 | -122.3511 | 0.10071 | 1.4211e-13 | -0.028968 | 0.014039 | -0.0036391 | -0.012974 | 0.018629 | -0.22533 | 0.018012 | 0.018249 | 0.015812 | 0.034795 | 0.0090396 | 0.055988 | 0.010564 | 0.01906 | 0.11622 | 0.064464 | 0.26559 | 0.019363 | 0.06515 | 0.03241 | -0.019721 | 0.075351 | 0.16938 | -0.097557 | -0.16415 | 122.3704 | 0.015517 | 122.4071 | 122.3701 | -0.000303 | -0.036244 | 0.16488 | 122.1869 | -0.025357 | 122.4162 | 122.3314 | 0.14443 | 0.068671 | -0.19827 | 122.4673 | 122.4155 | 122.6167 | 122.3616 | -0.081345 | 122.4264 | 122.5205 | 122.2535 | 122.3835 | -0.26486
2106.4531 | 122.612 | -122.4243 | 0.1236 | 1.4211e-13 | -0.029181 | 0.014252 | -0.0038527 | -0.013615 | 0.018629 | -0.24059 | 0.018012 | 0.018676 | 0.015812 | 0.034367 | 0.0090396 | 0.060567 | 0.010564 | 0.028217 | 0.11622 | 0.055306 | 0.27475 | 0.019363 | 0.055992 | 0.03241 | -0.005985 | 0.070773 | 0.16022 | -0.047193 | -0.17331 | 122.4437 | -0.007371 | 122.4849 | 122.4525 | 0.008854 | -0.06829 | 0.15115 | 122.251 | -0.052823 | 122.4803 | 122.4183 | 0.16732 | 0.036626 | -0.17079 | 122.5405 | 122.4796 | 122.6991 | 122.4349 | -0.10423 | 122.4951 | 122.5845 | 122.3771 | 122.4567 | -0.2969
2108.2031 | 122.644 | -122.3694 | 0.10529 | 1.4211e-13 | -0.028968 | 0.014039 | -0.0038527 | -0.013401 | 0.018416 | -0.22533 | 0.018225 | 0.018676 | 0.015598 | 0.034795 | 0.0086124 | 0.060567 | 0.005985 | 0.014482 | 0.11165 | 0.064464 | 0.27475 | 0.019363 | 0.051413 | 0.03241 | -0.010564 | 0.066194 | 0.16022 | -0.065507 | -0.16873 | 122.3887 | 0.006361 | 122.43 | 122.3839 | -0.004881 | -0.040822 | 0.16946 | 122.2007 | -0.039092 | 122.4208 | 122.3588 | 0.15816 | 0.054936 | -0.17079 | 122.481 | 122.4338 | 122.6441 | 122.3754 | -0.085923 | 122.4356 | 122.5296 | 122.3039 | 122.4018 | -0.27401
2109.8906 | 122.7173 | -122.3831 | 0.086975 | 1.4211e-13 | -0.029181 | 0.014252 | -0.0040665 | -0.013401 | 0.018843 | -0.23296 | 0.018012 | 0.018462 | 0.015171 | 0.034795 | 0.0092534 | 0.060567 | 0.015142 | 0.01906 | 0.10249 | 0.069043 | 0.27017 | 0.019363 | 0.060571 | 0.036989 | -0.015143 | 0.070773 | 0.16022 | -0.083821 | -0.16873 | 122.4025 | 0.015515 | 122.4437 | 122.4022 | -0.000303 | -0.017932 | 0.18319 | 122.2144 | -0.016202 | 122.4437 | 122.368 | 0.15358 | 0.073247 | -0.1708 | 122.4856 | 122.4522 | 122.6533 | 122.3983 | -0.067612 | 122.4539 | 122.5433 | 122.2993 | 122.4201 | -0.2557
2111.625 | 122.6898 | -122.3557 | 0.086975 | 1.4211e-13 | -0.028968 | 0.014252 | -0.0040665 | -0.013187 | 0.018629 | -0.22533 | 0.018225 | 0.019103 | 0.015598 | 0.034581 | 0.0090396 | 0.055988 | 0.010564 | 0.023639 | 0.11165 | 0.064464 | 0.27932 | 0.019363 | 0.051413 | 0.03241 | -0.010564 | 0.075351 | 0.16022 | -0.097557 | -0.16873 | 122.375 | 0.024672 | 122.4116 | 122.3793 | 0.004276 | -0.022511 | 0.19235 | 122.1869 | -0.011624 | 122.4071 | 122.3451 | 0.15816 | 0.073247 | -0.18453 | 122.4673 | 122.4201 | 122.635 | 122.3662 | -0.067612 | 122.431 | 122.5159 | 122.2581 | 122.3881 | -0.2557
2113.375 | 122.7081 | -122.3694 | 0.07782 | 1.4211e-13 | -0.029395 | 0.014252 | -0.0034253 | -0.012974 | 0.018629 | -0.24059 | 0.018225 | 0.018462 | 0.015385 | 0.034795 | 0.0092534 | 0.055988 | 0.010564 | 0.023639 | 0.11165 | 0.055306 | 0.27017 | 0.023942 | 0.055992 | 0.027831 | -0.015143 | 0.070773 | 0.16022 | -0.097557 | -0.16415 | 122.3933 | 0.033827 | 122.4254 | 122.393 | -0.000303 | -0.022514 | 0.19235 | 122.2052 | -0.007047 | 122.4254 | 122.3542 | 0.14901 | 0.082402 | -0.17538 | 122.481 | 122.4247 | 122.6396 | 122.3799 | -0.053878 | 122.4402 | 122.5296 | 122.2718 | 122.3972 | -0.24197
2115.0625 | 122.6532 | -122.3831 | 0.09613 | 1.4211e-13 | -0.029181 | 0.014039 | -0.0038527 | -0.013187 | 0.018629 | -0.24822 | 0.017798 | 0.018676 | 0.015598 | 0.034581 | 0.0090396 | 0.05141 | 0.010564 | 0.014482 | 0.11165 | 0.064464 | 0.27017 | 0.019363 | 0.055992 | 0.023253 | -0.015143 | 0.075351 | 0.15107 | -0.079243 | -0.16415 | 122.4025 | 0.015517 | 122.4345 | 122.3976 | -0.004881 | -0.031666 | 0.17404 | 122.219 | -0.020779 | 122.4391 | 122.368 | 0.14901 | 0.054935 | -0.17537 | 122.4948 | 122.4476 | 122.6533 | 122.3937 | -0.076767 | 122.4585 | 122.5342 | 122.3039 | 122.4064 | -0.26028
2116.8125 | 122.5571 | -122.4106 | 0.11902 | 1.4211e-13 | -0.02854 | 0.014466 | -0.0040665 | -0.012974 | 0.018629 | -0.22533 | 0.018012 | 0.018676 | 0.015385 | 0.034795 | 0.0090396 | 0.05141 | 0.005985 | 0.01906 | 0.11165 | 0.059885 | 0.27475 | 0.014784 | 0.060571 | 0.027831 | -0.010564 | 0.07993 | 0.16022 | -0.001407 | -0.16873 | 122.4254 | -0.007372 | 122.462 | 122.4296 | 0.004276 | -0.059134 | 0.15573 | 122.2419 | -0.039089 | 122.4712 | 122.4 | 0.15816 | 0.041203 | -0.12043 | 122.5222 | 122.4705 | 122.6853 | 122.4166 | -0.10423 | 122.4905 | 122.5708 | 122.4092 | 122.4384 | -0.28775
2118.5625 | 122.612 | -122.4243 | 0.12817 | 1.4211e-13 | -0.029181 | 0.014252 | -0.0038527 | -0.013187 | 0.018843 | -0.23296 | 0.018012 | 0.018889 | 0.015812 | 0.034153 | 0.0092534 | 0.055988 | 0.005985 | 0.023639 | 0.10707 | 0.064464 | 0.27475 | 0.019363 | 0.055992 | 0.03241 | -0.010564 | 0.061616 | 0.16022 | -0.038035 | -0.16873 | 122.4437 | -0.021106 | 122.4803 | 122.448 | 0.004276 | -0.06371 | 0.14657 | 122.2556 | -0.066558 | 122.4803 | 122.4138 | 0.15816 | 0.032048 | -0.16621 | 122.5314 | 122.4888 | 122.6991 | 122.4303 | -0.10881 | 122.4859 | 122.5845 | 122.3863 | 122.4567 | -0.2969
2120.2969 | 122.5983 | -122.4197 | 0.09613 | 1.4211e-13 | -0.029395 | 0.014252 | -0.0040665 | -0.013187 | 0.018843 | -0.23296 | 0.018439 | 0.018676 | 0.015598 | 0.035008 | 0.008826 | 0.055988 | 0.005985 | 0.014482 | 0.11165 | 0.055306 | 0.27017 | 0.023942 | 0.046835 | 0.03241 | -0.015143 | 0.075351 | 0.16022 | -0.047193 | -0.15957 | 122.4437 | 0.015517 | 122.4757 | 122.4342 | -0.00946 | -0.040824 | 0.17404 | 122.2602 | -0.020779 | 122.4666 | 122.4046 | 0.14443 | 0.064092 | -0.14332 | 122.5314 | 122.475 | 122.6899 | 122.4257 | -0.072188 | 122.4951 | 122.58 | 122.3725 | 122.4521 | -0.2557
2122.0312 | 122.6624 | -122.406 | 0.086975 | 1.4211e-13 | -0.029181 | 0.014466 | -0.0038527 | -0.013401 | 0.018629 | -0.22533 | 0.018012 | 0.018462 | 0.015385 | 0.034581 | 0.0090396 | 0.055988 | 0.015142 | 0.023639 | 0.11622 | 0.064464 | 0.27475 | 0.023942 | 0.055992 | 0.036989 | -0.010564 | 0.075351 | 0.16022 | -0.079243 | -0.16415 | 122.4299 | 0.02925 | 122.462 | 122.4296 | -0.000303 | -0.022511 | 0.18777 | 122.2419 | -0.011624 | 122.462 | 122.3954 | 0.15358 | 0.073247 | -0.16622 | 122.5222 | 122.4705 | 122.6808 | 122.4211 | -0.063033 | 122.4814 | 122.5662 | 122.3268 | 122.443 | -0.25112
2123.7188 | 122.6624 | -122.3923 | 0.086975 | 1.4211e-13 | -0.028968 | 0.014252 | -0.0038527 | -0.013401 | 0.018843 | -0.23296 | 0.018225 | 0.018889 | 0.015385 | 0.034581 | 0.0090396 | 0.05141 | 0.005985 | 0.01906 | 0.11622 | 0.059885 | 0.26559 | 0.023942 | 0.051413 | 0.027831 | -0.010564 | 0.075351 | 0.1648 | -0.05635 | -0.16415 | 122.4162 | 0.02925 | 122.4437 | 122.4113 | -0.004882 | -0.02709 | 0.17861 | 122.2281 | -0.011624 | 122.4437 | 122.3817 | 0.15358 | 0.077825 | -0.14332 | 122.5085 | 122.4522 | 122.6579 | 122.3983 | -0.063033 | 122.4676 | 122.5571 | 122.3359 | 122.4201 | -0.25112
2125.4531 | 122.7081 | -122.3831 | 0.091553 | 1.4211e-13 | -0.028968 | 0.014039 | -0.0040665 | -0.013187 | 0.018629 | -0.23296 | 0.018225 | 0.018249 | 0.015812 | 0.034795 | 0.008826 | 0.055988 | 0.005985 | 0.01906 | 0.1208 | 0.069043 | 0.27475 | 0.014784 | 0.055992 | 0.03241 | -0.015143 | 0.066194 | 0.16938 | -0.060928 | -0.15957 | 122.3979 | 0.029251 | 122.4391 | 122.4022 | 0.004276 | -0.02251 | 0.18319 | 122.2235 | -0.025359 | 122.4391 | 122.368 | 0.14443 | 0.077826 | -0.15248 | 122.5039 | 122.4522 | 122.6579 | 122.3891 | -0.076769 | 122.4493 | 122.5525 | 122.3222 | 122.4155 | -0.25112
2127.1875 | 122.5662 | -122.4518 | 0.12817 | 1.4211e-13 | -0.028968 | 0.01468 | -0.0040665 | -0.013401 | 0.019057 | -0.23296 | 0.018012 | 0.018462 | 0.015385 | 0.034795 | 0.0090396 | 0.055988 | 0.010564 | 0.028217 | 0.11622 | 0.064464 | 0.27017 | 0.019363 | 0.055992 | 0.036989 | -0.015143 | 0.066194 | 0.16022 | -0.033457 | -0.16415 | 122.4711 | -0.011949 | 122.5078 | 122.48 | 0.008854 | -0.06371 | 0.14199 | 122.2876 | -0.06198 | 122.5078 | 122.4366 | 0.14901 | 0.032048 | -0.16163 | 122.568 | 122.5162 | 122.7219 | 122.4623 | -0.10881 | 122.518 | 122.612 | 122.4183 | 122.4888 | -0.29232
2128.875 | 122.5937 | -122.4472 | 0.11444 | 1.4211e-13 | -0.029181 | 0.014039 | -0.0040665 | -0.013401 | 0.018629 | -0.23296 | 0.018225 | 0.018462 | 0.015598 | 0.034367 | 0.008826 | 0.05141 | 0.015142 | 0.01906 | 0.11622 | 0.059885 | 0.27932 | 0.023942 | 0.055992 | 0.036989 | -0.019721 | 0.075351 | 0.16022 | -0.12045 | -0.16415 | 122.4711 | 0.001784 | 122.4986 | 122.4663 | -0.004882 | -0.054556 | 0.16488 | 122.2831 | -0.03909 | 122.5032 | 122.4275 | 0.14443 | 0.045781 | -0.23489 | 122.5634 | 122.5071 | 122.7265 | 122.4623 | -0.090499 | 122.5226 | 122.6074 | 122.3268 | 122.4842 | -0.27859
2130.6094 | 122.6212 | -122.4197 | 0.10071 | 1.4211e-13 | -0.029181 | 0.014252 | -0.0038527 | -0.012974 | 0.018416 | -0.23296 | 0.018012 | 0.018462 | 0.015171 | 0.034795 | 0.008826 | 0.05141 | 0.010564 | 0.023639 | 0.11165 | 0.059885 | 0.27017 | 0.028521 | 0.051413 | 0.027831 | -0.019721 | 0.070773 | 0.16022 | -0.070086 | -0.16873 | 122.4483 | 0.010939 | 122.4711 | 122.4434 | -0.004882 | -0.040823 | 0.16946 | 122.251 | -0.029935 | 122.4712 | 122.4 | 0.14901 | 0.059514 | -0.17079 | 122.5314 | 122.4796 | 122.6899 | 122.4303 | -0.072187 | 122.4905 | 122.58 | 122.3497 | 122.4476 | -0.26944
2132.3594 | 122.5845 | -122.4472 | 0.11902 | 1.4211e-13 | -0.029181 | 0.014039 | -0.0040665 | -0.013187 | 0.018629 | -0.22533 | 0.018012 | 0.018676 | 0.015598 | 0.034581 | 0.008826 | 0.060567 | 0.015142 | 0.023639 | 0.1208 | 0.064464 | 0.27932 | 0.023942 | 0.051413 | 0.03241 | -0.015143 | 0.070773 | 0.16022 | -0.047193 | -0.17331 | 122.4711 | 0.001785 | 122.5078 | 122.4708 | -0.000303 | -0.054555 | 0.16031 | 122.2739 | -0.048246 | 122.4986 | 122.4321 | 0.15816 | 0.041203 | -0.16621 | 122.568 | 122.5117 | 122.7265 | 122.4623 | -0.095077 | 122.518 | 122.6074 | 122.4 | 122.4796 | -0.29233
2134.0469 | 122.7127 | -122.3923 | 0.091553 | 1.4211e-13 | -0.028968 | 0.014466 | -0.0040665 | -0.013401 | 0.018843 | -0.22533 | 0.018225 | 0.018249 | 0.015171 | 0.034795 | 0.009467 | 0.055988 | 0.005985 | 0.01906 | 0.11622 | 0.059885 | 0.27932 | 0.023942 | 0.060571 | 0.036989 | -0.015143 | 0.070773 | 0.1648 | -0.11129 | -0.16873 | 122.4162 | 0.024672 | 122.4483 | 122.4113 | -0.004882 | -0.031668 | 0.18777 | 122.2235 | -0.02078 | 122.4528 | 122.3771 | 0.15358 | 0.073247 | -0.20285 | 122.5085 | 122.4522 | 122.6716 | 122.3983 | -0.067611 | 122.463 | 122.5571 | 122.281 | 122.4293 | -0.26028
2135.7969 | 122.6395 | -122.4289 | 0.10071 | 1.4211e-13 | -0.029609 | 0.014252 | -0.0038527 | -0.013401 | 0.018629 | -0.22533 | 0.018012 | 0.018676 | 0.015598 | 0.035008 | 0.0092534 | 0.05141 | 0.005985 | 0.01906 | 0.11622 | 0.059885 | 0.26559 | 0.019363 | 0.051413 | 0.036989 | -0.010564 | 0.075351 | 0.1648 | -0.065507 | -0.15957 | 122.4483 | 0.015517 | 122.4803 | 122.448 | -0.000303 | -0.040823 | 0.16488 | 122.2693 | -0.025357 | 122.4803 | 122.4183 | 0.14901 | 0.064092 | -0.16622 | 122.5451 | 122.4888 | 122.6945 | 122.4349 | -0.081345 | 122.5042 | 122.5937 | 122.3634 | 122.4659 | -0.26028
2137.5312 | 122.7219 | -122.4197 | 0.086975 | 1.4211e-13 | -0.028754 | 0.014039 | -0.0042801 | -0.013401 | 0.018416 | -0.23296 | 0.017798 | 0.018462 | 0.015385 | 0.034581 | 0.008826 | 0.05141 | 0.001407 | 0.028217 | 0.10249 | 0.064464 | 0.27017 | 0.023942 | 0.051413 | 0.03241 | -0.015143 | 0.075351 | 0.16938 | -0.074664 | -0.16873 | 122.4437 | 0.015515 | 122.4711 | 122.448 | 0.004275 | -0.022511 | 0.18319 | 122.251 | -0.011624 | 122.4712 | 122.4046 | 0.15358 | 0.082404 | -0.16164 | 122.5222 | 122.4842 | 122.6899 | 122.4211 | -0.063033 | 122.4951 | 122.5891 | 122.3451 | 122.4521 | -0.2557
2139.2812 | 122.6761 | -122.4014 | 0.064087 | 1.4211e-13 | -0.029181 | 0.014039 | -0.0038527 | -0.013401 | 0.018629 | -0.23296 | 0.018439 | 0.018676 | 0.015598 | 0.034581 | 0.0092534 | 0.055988 | 0.015142 | 0.01906 | 0.11165 | 0.059885 | 0.27017 | 0.023942 | 0.055992 | 0.036989 | -0.010564 | 0.070773 | 0.15564 | -0.074664 | -0.15957 | 122.4254 | 0.04756 | 122.4574 | 122.4205 | -0.004882 | -0.004202 | 0.20608 | 122.2419 | 0.006686 | 122.4574 | 122.3909 | 0.14901 | 0.091556 | -0.13875 | 122.5131 | 122.4613 | 122.6716 | 122.4166 | -0.040145 | 122.4722 | 122.5571 | 122.3268 | 122.4384 | -0.22366
2141.0312 | 122.6852 | -122.3831 | 0.07782 | 1.4211e-13 | -0.028968 | 0.014252 | -0.0038527 | -0.013187 | 0.018629 | -0.23296 | 0.018225 | 0.018249 | 0.015598 | 0.034367 | 0.0090396 | 0.05141 | 0.015142 | 0.01906 | 0.11165 | 0.064464 | 0.27475 | 0.019363 | 0.051413 | 0.036989 | -0.015143 | 0.066194 | 0.15107 | -0.065507 | -0.17331 | 122.4025 | 0.033827 | 122.4345 | 122.4022 | -0.000303 | -0.013356 | 0.19693 | 122.2098 | -0.011626 | 122.4345 | 122.368 | 0.15816 | 0.073245 | -0.14333 | 122.4948 | 122.4476 | 122.6579 | 122.3983 | -0.058457 | 122.4493 | 122.5342 | 122.3176 | 122.4201 | -0.25113
2142.7656 | 122.7036 | -122.3923 | 0.082397 | 1.4211e-13 | -0.028968 | 0.014252 | -0.0038527 | -0.012974 | 0.018629 | -0.23296 | 0.018225 | 0.018462 | 0.015385 | 0.034581 | 0.008826 | 0.055988 | 0.005985 | 0.014482 | 0.11165 | 0.059885 | 0.27475 | 0.023942 | 0.051413 | 0.03241 | -0.019721 | 0.075351 | 0.15564 | -0.0884 | -0.16415 | 122.4162 | 0.02925 | 122.4483 | 122.4068 | -0.00946 | -0.022512 | 0.19235 | 122.2281 | -0.007046 | 122.4437 | 122.3726 | 0.14443 | 0.073246 | -0.1708 | 122.5039 | 122.4522 | 122.667 | 122.3983 | -0.058455 | 122.4676 | 122.5479 | 122.3039 | 122.4247 | -0.24655
2144.4531 | 122.5983 | -122.4335 | 0.11902 | 1.4211e-13 | -0.029181 | 0.014039 | -0.0036391 | -0.013615 | 0.018843 | -0.23296 | 0.018012 | 0.018462 | 0.015598 | 0.034581 | 0.008826 | 0.055988 | 0.010564 | 0.014482 | 0.11165 | 0.069043 | 0.27475 | 0.019363 | 0.055992 | 0.03241 | -0.010564 | 0.066194 | 0.15564 | -0.051771 | -0.15499 | 122.4528 | -0.007372 | 122.4895 | 122.448 | -0.004881 | -0.049976 | 0.15573 | 122.2785 | -0.052825 | 122.4895 | 122.4229 | 0.14443 | 0.036624 | -0.17079 | 122.5451 | 122.5025 | 122.7082 | 122.444 | -0.099656 | 122.4997 | 122.5891 | 122.3817 | 122.4659 | -0.27401
2146.2031 | 122.6669 | -122.4335 | 0.09613 | 1.4211e-13 | -0.028754 | 0.014466 | -0.0038527 | -0.013187 | 0.018629 | -0.24822 | 0.017584 | 0.018462 | 0.015385 | 0.034581 | 0.0090396 | 0.055988 | 0.005985 | 0.01906 | 0.11622 | 0.069043 | 0.27932 | 0.014784 | 0.051413 | 0.03241 | -0.015143 | 0.075351 | 0.1648 | -0.0884 | -0.16415 | 122.4483 | 0.020095 | 122.4895 | 122.4525 | 0.004276 | -0.027087 | 0.18319 | 122.2693 | -0.020779 | 122.4849 | 122.4183 | 0.14901 | 0.06867 | -0.18453 | 122.5497 | 122.5025 | 122.7128 | 122.4395 | -0.081346 | 122.5088 | 122.5983 | 122.3451 | 122.4659 | -0.26028
2147.9531 | 122.6578 | -122.4335 | 0.1236 | 1.4211e-13 | -0.029181 | 0.014252 | -0.0038527 | -0.013401 | 0.018629 | -0.23296 | 0.018225 | 0.018889 | 0.015171 | 0.034581 | 0.0090396 | 0.055988 | 0.015142 | 0.023639 | 0.11622 | 0.059885 | 0.27475 | 0.010206 | 0.055992 | 0.036989 | -0.010564 | 0.070773 | 0.15107 | -0.092979 | -0.16873 | 122.4437 | -0.007371 | 122.4895 | 122.4571 | 0.013433 | -0.063711 | 0.15115 | 122.2647 | -0.052823 | 122.4895 | 122.4229 | 0.15816 | 0.027469 | -0.21658 | 122.5497 | 122.4934 | 122.7082 | 122.4486 | -0.11339 | 122.5042 | 122.5845 | 122.3405 | 122.4705 | -0.29232
2149.6406 | 122.7264 | -122.4106 | 0.086975 | 1.4211e-13 | -0.029609 | 0.014039 | -0.0038527 | -0.013401 | 0.018843 | -0.24059 | 0.018225 | 0.018462 | 0.015385 | 0.035008 | 0.0090396 | 0.05141 | 0.001407 | 0.01906 | 0.11622 | 0.059885 | 0.27475 | 0.028521 | 0.051413 | 0.03241 | -0.015143 | 0.070773 | 0.16022 | -0.092979 | -0.16415 | 122.4391 | 0.02925 | 122.462 | 122.4296 | -0.009461 | -0.02709 | 0.18777 | 122.2464 | -0.016202 | 122.462 | 122.3954 | 0.14901 | 0.073247 | -0.17995 | 122.5268 | 122.4705 | 122.6853 | 122.412 | -0.058454 | 122.4814 | 122.5708 | 122.3176 | 122.443 | -0.25112
2151.3906 | 122.7081 | -122.4243 | 0.10071 | 1.4211e-13 | -0.029395 | 0.014252 | -0.0038527 | -0.012974 | 0.018843 | -0.24059 | 0.018012 | 0.018676 | 0.015385 | 0.034581 | 0.0092534 | 0.05141 | 0.015142 | 0.023639 | 0.11165 | 0.069043 | 0.27475 | 0.014784 | 0.042256 | 0.027831 | -0.010564 | 0.070773 | 0.16938 | -0.097557 | -0.16873 | 122.4391 | 0.010939 | 122.4757 | 122.448 | 0.008855 | -0.031665 | 0.17404 | 122.2556 | -0.029935 | 122.4666 | 122.4138 | 0.15816 | 0.068671 | -0.19827 | 122.536 | 122.4934 | 122.6991 | 122.4395 | -0.085924 | 122.4951 | 122.5937 | 122.3268 | 122.4521 | -0.26944
2153.0625 | 122.644 | -122.4243 | 0.10986 | 1.4211e-13 | -0.029181 | 0.014252 | -0.0038527 | -0.012974 | 0.018629 | -0.22533 | 0.018012 | 0.018676 | 0.015171 | 0.034795 | 0.008826 | 0.055988 | 0.005985 | 0.01906 | 0.11622 | 0.064464 | 0.27475 | 0.010206 | 0.051413 | 0.036989 | -0.015143 | 0.075351 | 0.1648 | -0.10214 | -0.17331 | 122.4345 | 0.006362 | 122.4803 | 122.4434 | 0.008854 | -0.045399 | 0.16488 | 122.251 | -0.034512 | 122.4757 | 122.4092 | 0.15816 | 0.054937 | -0.212 | 122.5405 | 122.4888 | 122.6991 | 122.4303 | -0.099657 | 122.4997 | 122.5891 | 122.3222 | 122.4613 | -0.28317
2154.8125 | 122.6898 | -122.4197 | 0.09613 | 1.4211e-13 | -0.029181 | 0.014252 | -0.0038527 | -0.013615 | 0.019057 | -0.23296 | 0.018439 | 0.018249 | 0.015385 | 0.034581 | 0.0090396 | 0.055988 | 0.010564 | 0.028217 | 0.11622 | 0.073622 | 0.27475 | 0.014784 | 0.055992 | 0.027831 | -0.010564 | 0.070773 | 0.17396 | -0.038035 | -0.16415 | 122.4345 | 0.020095 | 122.4757 | 122.448 | 0.013433 | -0.022508 | 0.17862 | 122.2556 | -0.025357 | 122.4757 | 122.4092 | 0.15358 | 0.077828 | -0.13416 | 122.536 | 122.4934 | 122.6945 | 122.4303 | -0.081346 | 122.4905 | 122.5937 | 122.3817 | 122.4476 | -0.26028
2156.5625 | 122.7173 | -122.406 | 0.064087 | 1.4211e-13 | -0.029609 | 0.014466 | -0.0036391 | -0.013615 | 0.018843 | -0.23296 | 0.018439 | 0.018676 | 0.015598 | 0.034367 | 0.0092534 | 0.060567 | 0.015142 | 0.01906 | 0.10707 | 0.059885 | 0.27475 | 0.019363 | 0.055992 | 0.03241 | -0.015143 | 0.07993 | 0.1648 | -0.10214 | -0.16415 | 122.4254 | 0.042981 | 122.4666 | 122.4251 | -0.000303 | -0.004202 | 0.21066 | 122.2419 | 0.015843 | 122.462 | 122.3909 | 0.14901 | 0.10071 | -0.16622 | 122.5131 | 122.4659 | 122.6808 | 122.4211 | -0.044724 | 122.4859 | 122.5708 | 122.3039 | 122.4384 | -0.22824
2158.25 | 122.5983 | -122.4655 | 0.10529 | 1.4211e-13 | -0.029181 | 0.013825 | -0.0036391 | -0.013401 | 0.018843 | -0.24059 | 0.018225 | 0.018676 | 0.015385 | 0.034581 | 0.0090396 | 0.046831 | 0.005985 | 0.014482 | 0.11165 | 0.069043 | 0.27932 | 0.023942 | 0.055992 | 0.036989 | -0.0243 | 0.070773 | 0.16938 | -0.051771 | -0.15957 | 122.4895 | 0.006361 | 122.5123 | 122.48 | -0.00946 | -0.036243 | 0.17404 | 122.3059 | -0.034513 | 122.5215 | 122.4412 | 0.13527 | 0.064093 | -0.15706 | 122.5772 | 122.5346 | 122.7448 | 122.4715 | -0.081344 | 122.5363 | 122.6349 | 122.4137 | 122.5025 | -0.26486
2160 | 122.644 | -122.4655 | 0.10986 | 1.4211e-13 | -0.029181 | 0.014039 | -0.0038527 | -0.013615 | 0.018629 | -0.24822 | 0.018012 | 0.018676 | 0.015598 | 0.034795 | 0.0090396 | 0.05141 | 0.015142 | 0.014482 | 0.11165 | 0.064464 | 0.27932 | 0.019363 | 0.055992 | 0.03241 | -0.015143 | 0.070773 | 0.16022 | -0.10214 | -0.16415 | 122.4849 | 0.001784 | 122.5169 | 122.48 | -0.004881 | -0.045399 | 0.16946 | 122.3014 | -0.03909 | 122.5215 | 122.4504 | 0.14901 | 0.050359 | -0.212 | 122.5772 | 122.53 | 122.7448 | 122.4807 | -0.0905 | 122.5363 | 122.6257 | 122.3634 | 122.4979 | -0.27401
2161.6719 | 122.731 | -122.4152 | 0.07782 | 1.4211e-13 | -0.029181 | 0.014039 | -0.0036391 | -0.013401 | 0.018843 | -0.21007 | 0.018012 | 0.018462 | 0.015385 | 0.034795 | 0.0090396 | 0.055988 | 0.005985 | 0.01906 | 0.11622 | 0.069043 | 0.27475 | 0.019363 | 0.055992 | 0.03241 | -0.015143 | 0.066194 | 0.1648 | -0.0243 | -0.16873 | 122.4345 | 0.038405 | 122.4711 | 122.4342 | -0.000303 | -0.008777 | 0.19693 | 122.2464 | -0.011626 | 122.4712 | 122.4 | 0.15358 | 0.08698 | -0.10212 | 122.5314 | 122.4842 | 122.6899 | 122.4211 | -0.058457 | 122.4814 | 122.58 | 122.3909 | 122.4476 | -0.24655
2163.4219 | 122.6852 | -122.4335 | 0.09613 | 1.4211e-13 | -0.029395 | 0.014252 | -0.0040665 | -0.013187 | 0.018629 | -0.23296 | 0.018225 | 0.018889 | 0.015171 | 0.035008 | 0.0090396 | 0.055988 | 0.010564 | 0.014482 | 0.11622 | 0.073622 | 0.27932 | 0.019363 | 0.060571 | 0.03241 | -0.015143 | 0.070773 | 0.16022 | -0.047193 | -0.16415 | 122.4528 | 0.020095 | 122.4895 | 122.448 | -0.004881 | -0.022508 | 0.18319 | 122.2693 | -0.025357 | 122.494 | 122.4183 | 0.14901 | 0.064092 | -0.14332 | 122.5497 | 122.5071 | 122.7128 | 122.444 | -0.076767 | 122.5042 | 122.5937 | 122.3863 | 122.4659 | -0.26028
2165.0938 | 122.699 | -122.4197 | 0.10529 | 1.4211e-13 | -0.028968 | 0.014252 | -0.0038527 | -0.013187 | 0.018629 | -0.22533 | 0.018225 | 0.018676 | 0.015598 | 0.034795 | 0.008826 | 0.060567 | 0.005985 | 0.01906 | 0.11622 | 0.064464 | 0.27932 | 0.023942 | 0.060571 | 0.03241 | -0.015143 | 0.075351 | 0.16938 | -0.10671 | -0.16873 | 122.4437 | 0.010939 | 122.4803 | 122.4388 | -0.004882 | -0.040822 | 0.17404 | 122.251 | -0.029935 | 122.4803 | 122.4046 | 0.15358 | 0.064093 | -0.212 | 122.536 | 122.4842 | 122.6991 | 122.4257 | -0.081344 | 122.4951 | 122.5891 | 122.313 | 122.4521 | -0.27401
2166.8281 | 122.6944 | -122.4472 | 0.10986 | 1.4211e-13 | -0.029181 | 0.014039 | -0.0034253 | -0.013187 | 0.018629 | -0.23296 | 0.018225 | 0.018462 | 0.015385 | 0.034367 | 0.0090396 | 0.060567 | 0.010564 | 0.023639 | 0.11165 | 0.059885 | 0.27932 | 0.014784 | 0.051413 | 0.023253 | -0.010564 | 0.066194 | 0.16022 | -0.10671 | -0.16415 | 122.462 | 0.001784 | 122.5078 | 122.4708 | 0.008855 | -0.049978 | 0.16946 | 122.2831 | -0.043669 | 122.4986 | 122.4366 | 0.15358 | 0.050359 | -0.21658 | 122.5589 | 122.5071 | 122.7265 | 122.4578 | -0.095079 | 122.5134 | 122.6074 | 122.3405 | 122.4705 | -0.27401
2168.5938 | 122.6257 | -122.4564 | 0.10071 | 1.4211e-13 | -0.028968 | 0.014039 | -0.0034253 | -0.013187 | 0.018629 | -0.23296 | 0.018012 | 0.018676 | 0.015598 | 0.034367 | 0.009467 | 0.055988 | 0.001407 | 0.01906 | 0.11165 | 0.064464 | 0.27475 | 0.023942 | 0.055992 | 0.036989 | -0.015143 | 0.066194 | 0.1648 | -0.051771 | -0.16873 | 122.4803 | 0.010939 | 122.5123 | 122.4754 | -0.004882 | -0.036244 | 0.17404 | 122.2876 | -0.034514 | 122.5124 | 122.4412 | 0.15358 | 0.064092 | -0.15248 | 122.568 | 122.5208 | 122.7311 | 122.4578 | -0.076766 | 122.5226 | 122.6212 | 122.4046 | 122.4933 | -0.26944
2170.2812 | 122.7585 | -122.4289 | 0.10071 | 1.4211e-13 | -0.029181 | 0.014039 | -0.0038527 | -0.013187 | 0.019057 | -0.24059 | 0.018225 | 0.018676 | 0.015598 | 0.034795 | 0.0092534 | 0.055988 | 0.010564 | 0.028217 | 0.1208 | 0.069043 | 0.27475 | 0.019363 | 0.055992 | 0.03241 | -0.015143 | 0.075351 | 0.1648 | -0.05635 | -0.16873 | 122.4483 | 0.020096 | 122.4849 | 122.4571 | 0.008854 | -0.031665 | 0.17404 | 122.2602 | -0.025357 | 122.4849 | 122.4138 | 0.15358 | 0.064092 | -0.15706 | 122.5497 | 122.4979 | 122.7036 | 122.4395 | -0.081345 | 122.5042 | 122.5937 | 122.3725 | 122.4613 | -0.26944
2172.0156 | 122.6257 | -122.4609 | 0.10071 | 1.4211e-13 | -0.029181 | 0.014252 | -0.0038527 | -0.013187 | 0.017988 | -0.23296 | 0.017798 | 0.018676 | 0.015171 | 0.034581 | 0.008826 | 0.05141 | 0.010564 | 0.028217 | 0.11622 | 0.073622 | 0.27932 | 0.023942 | 0.055992 | 0.036989 | -0.005985 | 0.066194 | 0.16022 | -0.083821 | -0.16873 | 122.4849 | 0.015517 | 122.5123 | 122.4892 | 0.004275 | -0.027086 | 0.17862 | 122.2922 | -0.034514 | 122.5169 | 122.455 | 0.16274 | 0.059514 | -0.18453 | 122.5772 | 122.5346 | 122.7403 | 122.4715 | -0.076766 | 122.5271 | 122.6212 | 122.3771 | 122.4979 | -0.26944
2173.7031 | 122.7356 | -122.4197 | 0.082397 | 1.4211e-13 | -0.029181 | 0.014252 | -0.0038527 | -0.013401 | 0.018843 | -0.23296 | 0.018225 | 0.018249 | 0.015598 | 0.034367 | 0.008826 | 0.065145 | 0.010564 | 0.028217 | 0.10707 | 0.064464 | 0.27932 | 0.001048 | 0.060571 | 0.027831 | -0.015143 | 0.066194 | 0.1648 | -0.038035 | -0.16415 | 122.4208 | 0.024671 | 122.4849 | 122.448 | 0.027169 | -0.017933 | 0.19693 | 122.2556 | -0.016203 | 122.4803 | 122.4046 | 0.14901 | 0.082403 | -0.12043 | 122.5268 | 122.4842 | 122.6991 | 122.4303 | -0.081349 | 122.4859 | 122.5845 | 122.3817 | 122.4476 | -0.24655
2175.4375 | 122.699 | -122.4518 | 0.091553 | 1.4211e-13 | -0.029181 | 0.014252 | -0.0036391 | -0.013401 | 0.019057 | -0.23296 | 0.018012 | 0.018249 | 0.016026 | 0.034795 | 0.0090396 | 0.060567 | 0.005985 | 0.023639 | 0.11622 | 0.059885 | 0.2839 | 0.014784 | 0.051413 | 0.036989 | -0.019721 | 0.07993 | 0.16022 | -0.083821 | -0.16415 | 122.4666 | 0.024672 | 122.5123 | 122.4754 | 0.008855 | -0.031668 | 0.19235 | 122.2876 | -0.011623 | 122.5032 | 122.4321 | 0.14443 | 0.068669 | -0.17537 | 122.568 | 122.5117 | 122.7357 | 122.4578 | -0.076769 | 122.5317 | 122.612 | 122.368 | 122.4888 | -0.2557
2177.1094 | 122.731 | -122.4243 | 0.10071 | 1.4211e-13 | -0.028968 | 0.014039 | -0.0038527 | -0.013615 | 0.018843 | -0.23296 | 0.018653 | 0.018249 | 0.015598 | 0.034795 | 0.0086124 | 0.055988 | 0.005985 | 0.01906 | 0.11165 | 0.064464 | 0.27475 | 0.019363 | 0.055992 | 0.027831 | -0.0243 | 0.084508 | 0.16938 | -0.033457 | -0.17331 | 122.4437 | 0.010939 | 122.4803 | 122.4434 | -0.000303 | -0.036244 | 0.17404 | 122.251 | -0.0162 | 122.4803 | 122.4 | 0.14901 | 0.068671 | -0.13417 | 122.536 | 122.4888 | 122.6991 | 122.4303 | -0.081345 | 122.5088 | 122.5937 | 122.3909 | 122.4521 | -0.27401
2178.875 | 122.7539 | -122.4243 | 0.091553 | 1.4211e-13 | -0.029395 | 0.014252 | -0.0038527 | -0.013615 | 0.018843 | -0.2177 | 0.018225 | 0.018676 | 0.015171 | 0.034581 | 0.0090396 | 0.05141 | 0.015142 | 0.023639 | 0.11622 | 0.064464 | 0.2839 | 0.019363 | 0.051413 | 0.03241 | -0.010564 | 0.07993 | 0.1648 | -0.092979 | -0.17331 | 122.4437 | 0.024672 | 122.4757 | 122.448 | 0.004276 | -0.027089 | 0.19235 | 122.251 | -0.011623 | 122.4757 | 122.4138 | 0.16274 | 0.073247 | -0.18453 | 122.5405 | 122.4888 | 122.7082 | 122.4395 | -0.07219 | 122.5042 | 122.5891 | 122.3313 | 122.4567 | -0.26486
2180.5625 | 122.6257 | -122.493 | 0.091553 | 1.4211e-13 | -0.029395 | 0.013825 | -0.0040665 | -0.013615 | 0.018843 | -0.23296 | 0.018012 | 0.018249 | 0.015385 | 0.034367 | 0.0090396 | 0.05141 | 0.010564 | 0.023639 | 0.11622 | 0.069043 | 0.27475 | 0.028521 | 0.060571 | 0.027831 | -0.015143 | 0.084508 | 0.16938 | -0.038035 | -0.16415 | 122.5215 | 0.024672 | 122.5444 | 122.5166 | -0.004882 | -0.02251 | 0.18319 | 122.3288 | -0.007045 | 122.5536 | 122.4778 | 0.14901 | 0.077826 | -0.12959 | 122.6092 | 122.562 | 122.7677 | 122.5035 | -0.063032 | 122.5775 | 122.6624 | 122.4549 | 122.5208 | -0.2557
2182.3125 | 122.7493 | -122.4106 | 0.073242 | 1.4211e-13 | -0.029395 | 0.014252 | -0.0040665 | -0.013187 | 0.018843 | -0.23296 | 0.018225 | 0.018676 | 0.015385 | 0.034581 | 0.0090396 | 0.055988 | 0.001407 | 0.023639 | 0.11622 | 0.064464 | 0.27017 | 0.023942 | 0.055992 | 0.03241 | -0.019721 | 0.084508 | 0.1648 | -0.10214 | -0.16873 | 122.4345 | 0.042983 | 122.4666 | 122.4342 | -0.000303 | -0.008778 | 0.19692 | 122.2419 | 0.011266 | 122.4666 | 122.3909 | 0.14901 | 0.091558 | -0.17538 | 122.5268 | 122.475 | 122.6808 | 122.412 | -0.0493 | 122.4951 | 122.5754 | 122.3084 | 122.443 | -0.24197
2184.0156 | 122.7448 | -122.438 | 0.09613 | 1.4211e-13 | -0.029181 | 0.014252 | -0.0040665 | -0.013187 | 0.018843 | -0.23296 | 0.018225 | 0.018249 | 0.015812 | 0.034795 | 0.0092534 | 0.055988 | 0.015142 | 0.023639 | 0.10249 | 0.059885 | 0.27932 | 0.019363 | 0.060571 | 0.03241 | -0.010564 | 0.089087 | 0.16938 | -0.079243 | -0.16873 | 122.4574 | 0.00636 | 122.494 | 122.4617 | 0.004276 | -0.036245 | 0.18319 | 122.2693 | -0.007043 | 122.4986 | 122.4275 | 0.15816 | 0.073249 | -0.17537 | 122.5405 | 122.4979 | 122.7174 | 122.4532 | -0.076767 | 122.5271 | 122.6074 | 122.3588 | 122.4705 | -0.26486
2185.7656 | 122.7356 | -122.4472 | 0.082397 | 1.4211e-13 | -0.029181 | 0.013825 | -0.0036391 | -0.013187 | 0.019057 | -0.22533 | 0.018439 | 0.018462 | 0.015385 | 0.034795 | 0.0092534 | 0.046831 | 0.019721 | 0.01906 | 0.11622 | 0.059885 | 0.2839 | 0.019363 | 0.055992 | 0.023253 | -0.015143 | 0.07993 | 0.16938 | -0.092979 | -0.17331 | 122.4666 | 0.033828 | 122.494 | 122.4663 | -0.000303 | -0.022512 | 0.20151 | 122.2739 | -0.002467 | 122.5032 | 122.4321 | 0.15816 | 0.086982 | -0.17538 | 122.5634 | 122.5071 | 122.7311 | 122.4669 | -0.063034 | 122.5271 | 122.6166 | 122.3542 | 122.4705 | -0.2557
2187.5 | 122.612 | -122.4472 | 0.10986 | 1.4211e-13 | -0.028968 | 0.013825 | -0.0038527 | -0.013401 | 0.018843 | -0.22533 | 0.018225 | 0.018249 | 0.015812 | 0.034581 | 0.0090396 | 0.046831 | 0.005985 | 0.01906 | 0.11165 | 0.059885 | 0.2839 | 0.019363 | 0.051413 | 0.036989 | -0.015143 | 0.084508 | 0.16022 | -0.083821 | -0.16873 | 122.4666 | 0.001784 | 122.494 | 122.4663 | -0.000303 | -0.049978 | 0.17404 | 122.2785 | -0.025355 | 122.4986 | 122.4321 | 0.15358 | 0.050359 | -0.19368 | 122.5589 | 122.5071 | 122.7311 | 122.4532 | -0.0905 | 122.5317 | 122.6074 | 122.3634 | 122.4842 | -0.27859
2189.2344 | 122.7036 | -122.4564 | 0.07782 | 1.4211e-13 | -0.029181 | 0.014039 | -0.0038527 | -0.013401 | 0.019057 | -0.22533 | 0.018012 | 0.018676 | 0.015598 | 0.034581 | 0.0090396 | 0.046831 | 0.010564 | 0.028217 | 0.11165 | 0.059885 | 0.27475 | 0.019363 | 0.051413 | 0.036989 | -0.019721 | 0.089087 | 0.1648 | -0.047193 | -0.16873 | 122.4757 | 0.033827 | 122.5032 | 122.4846 | 0.008854 | -0.017935 | 0.19693 | 122.2876 | 0.011267 | 122.5078 | 122.4366 | 0.14901 | 0.08698 | -0.12501 | 122.568 | 122.5162 | 122.7311 | 122.4669 | -0.058457 | 122.5454 | 122.6212 | 122.4092 | 122.4933 | -0.24655
2190.9375 | 122.7814 | -122.4289 | 0.09613 | 1.4211e-13 | -0.028968 | 0.013825 | -0.0038527 | -0.013615 | 0.018629 | -0.23296 | 0.018012 | 0.018462 | 0.015385 | 0.034795 | 0.0090396 | 0.055988 | 0.005985 | 0.023639 | 0.11165 | 0.069043 | 0.27017 | 0.019363 | 0.051413 | 0.03241 | -0.010564 | 0.084508 | 0.1648 | -0.074664 | -0.16873 | 122.4483 | 0.015517 | 122.4849 | 122.4525 | 0.004276 | -0.027087 | 0.17404 | 122.2602 | -0.011622 | 122.4803 | 122.4183 | 0.15816 | 0.06867 | -0.17079 | 122.5405 | 122.4979 | 122.6991 | 122.4349 | -0.076767 | 122.5134 | 122.5937 | 122.3542 | 122.4613 | -0.26486
2192.6875 | 122.6166 | -122.4838 | 0.13275 | 1.4211e-13 | -0.029181 | 0.013825 | -0.0038527 | -0.013401 | 0.018629 | -0.22533 | 0.018439 | 0.018462 | 0.015385 | 0.034795 | 0.0092534 | 0.05141 | 0.010564 | 0.01906 | 0.1208 | 0.064464 | 0.27932 | 0.019363 | 0.060571 | 0.041567 | -0.005985 | 0.089087 | 0.1648 | -0.079243 | -0.16873 | 122.5032 | -0.011947 | 122.5352 | 122.5029 | -0.000303 | -0.068287 | 0.14657 | 122.3151 | -0.043664 | 122.5444 | 122.4778 | 0.16274 | 0.032049 | -0.21199 | 122.6046 | 122.5483 | 122.7631 | 122.4944 | -0.11339 | 122.5729 | 122.6486 | 122.4046 | 122.5254 | -0.30148
2194.3906 | 122.6669 | -122.4609 | 0.10529 | 1.4211e-13 | -0.029395 | 0.013825 | -0.0038527 | -0.013187 | 0.018416 | -0.23296 | 0.018225 | 0.018676 | 0.015598 | 0.034581 | 0.0092534 | 0.05141 | 0.005985 | 0.023639 | 0.10707 | 0.064464 | 0.27475 | 0.028521 | 0.060571 | 0.03241 | -0.015143 | 0.07993 | 0.16022 | -0.083821 | -0.16415 | 122.4895 | 0.001782 | 122.5123 | 122.4846 | -0.004882 | -0.040822 | 0.16946 | 122.2968 | -0.025356 | 122.5215 | 122.4458 | 0.14901 | 0.054936 | -0.18911 | 122.568 | 122.5254 | 122.7357 | 122.4669 | -0.076765 | 122.5409 | 122.6212 | 122.3771 | 122.4933 | -0.26943
2196.1562 | 122.6486 | -122.4701 | 0.10986 | 1.4211e-13 | -0.028968 | 0.014252 | -0.0038527 | -0.012974 | 0.018629 | -0.23296 | 0.018012 | 0.018676 | 0.015598 | 0.035008 | 0.008826 | 0.055988 | 0.010564 | 0.023639 | 0.11165 | 0.069043 | 0.27475 | 0.019363 | 0.051413 | 0.03241 | -0.019721 | 0.093665 | 0.1648 | -0.065507 | -0.16873 | 122.4895 | 0.001784 | 122.5261 | 122.4937 | 0.004276 | -0.04082 | 0.16488 | 122.3014 | -0.016198 | 122.5215 | 122.4504 | 0.14901 | 0.054937 | -0.17537 | 122.5817 | 122.5391 | 122.7448 | 122.4807 | -0.0905 | 122.5638 | 122.6349 | 122.4046 | 122.5025 | -0.27859
2197.9062 | 122.6715 | -122.4747 | 0.10529 | 1.4211e-13 | -0.028968 | 0.014252 | -0.0040665 | -0.013187 | 0.018202 | -0.2177 | 0.018012 | 0.018676 | 0.015598 | 0.034581 | 0.0090396 | 0.05141 | 0.015142 | 0.023639 | 0.11165 | 0.069043 | 0.27475 | 0.001048 | 0.046835 | 0.036989 | -0.015143 | 0.084508 | 0.16022 | -0.070086 | -0.16415 | 122.4757 | 0.006361 | 122.5261 | 122.4983 | 0.022591 | -0.036243 | 0.16946 | 122.3105 | -0.020778 | 122.5215 | 122.4595 | 0.14901 | 0.054936 | -0.17537 | 122.5863 | 122.5437 | 122.7494 | 122.4898 | -0.10424 | 122.5592 | 122.6349 | 122.4046 | 122.5117 | -0.26943
2199.6094 | 122.6669 | -122.4701 | 0.12817 | 1.4211e-13 | -0.028968 | 0.014039 | -0.0040665 | -0.013615 | 0.019057 | -0.22533 | 0.018225 | 0.018462 | 0.015598 | 0.034795 | 0.0096806 | 0.055988 | 0.005985 | 0.028217 | 0.11622 | 0.059885 | 0.27932 | 0.010206 | 0.051413 | 0.03241 | -0.010564 | 0.07993 | 0.16022 | -0.070086 | -0.16415 | 122.4803 | -0.011949 | 122.5261 | 122.4983 | 0.018011 | -0.068289 | 0.15115 | 122.3059 | -0.048244 | 122.5215 | 122.4595 | 0.15358 | 0.032048 | -0.19826 | 122.5863 | 122.53 | 122.7494 | 122.4761 | -0.11797 | 122.55 | 122.6303 | 122.4 | 122.5025 | -0.29232
2201.2969 | 122.7173 | -122.4564 | 0.10071 | 1.4211e-13 | -0.029181 | 0.014039 | -0.0038527 | -0.013615 | 0.018416 | -0.24059 | 0.018012 | 0.018676 | 0.015812 | 0.034795 | 0.008826 | 0.05141 | -0.003172 | 0.023639 | 0.11165 | 0.064464 | 0.27475 | 0.001048 | 0.055992 | 0.036989 | -0.015143 | 0.089087 | 0.16938 | -0.10214 | -0.17331 | 122.4574 | 0.010939 | 122.5078 | 122.48 | 0.022591 | -0.036244 | 0.17404 | 122.2831 | -0.011621 | 122.5124 | 122.4412 | 0.15816 | 0.068671 | -0.20284 | 122.568 | 122.5208 | 122.7311 | 122.4532 | -0.09966 | 122.5454 | 122.6257 | 122.3542 | 122.4933 | -0.27401
2203.0469 | 122.7219 | -122.4884 | 0.10986 | 1.4211e-13 | -0.029181 | 0.014466 | -0.0038527 | -0.013401 | 0.018843 | -0.24059 | 0.018225 | 0.018676 | 0.015598 | 0.034581 | 0.009467 | 0.060567 | 0.001407 | 0.01906 | 0.11165 | 0.069043 | 0.27475 | 0.019363 | 0.046835 | 0.03241 | -0.015143 | 0.07993 | 0.15107 | -0.10671 | -0.16873 | 122.5078 | 0.001784 | 122.549 | 122.5075 | -0.000303 | -0.04082 | 0.16488 | 122.3197 | -0.029933 | 122.5352 | 122.4733 | 0.15358 | 0.041202 | -0.21658 | 122.6001 | 122.5574 | 122.7631 | 122.4898 | -0.0905 | 122.5683 | 122.6395 | 122.3817 | 122.5208 | -0.27859
2204.7344 | 122.6807 | -122.4564 | 0.10071 | 1.4211e-13 | -0.028754 | 0.014039 | -0.0040665 | -0.013401 | 0.018629 | -0.23296 | 0.018012 | 0.018676 | 0.015385 | 0.034581 | 0.0090396 | 0.046831 | 0.015142 | 0.023639 | 0.11622 | 0.064464 | 0.27932 | 0.014784 | 0.046835 | 0.03241 | -0.005985 | 0.07993 | 0.16022 | -0.038035 | -0.16415 | 122.4711 | 0.015517 | 122.5032 | 122.48 | 0.008855 | -0.036244 | 0.17862 | 122.2922 | -0.020778 | 122.5032 | 122.4504 | 0.15816 | 0.059514 | -0.13874 | 122.5726 | 122.5208 | 122.7357 | 122.4715 | -0.085924 | 122.5363 | 122.6166 | 122.4183 | 122.4888 | -0.26486
2206.4844 | 122.7722 | -122.4335 | 0.082397 | 1.4211e-13 | -0.028754 | 0.014039 | -0.0040665 | -0.013401 | 0.018629 | -0.23296 | 0.018012 | 0.018462 | 0.015385 | 0.035008 | 0.0090396 | 0.055988 | 0.010564 | 0.01906 | 0.11165 | 0.064464 | 0.27475 | 0.019363 | 0.051413 | 0.036989 | -0.010564 | 0.075351 | 0.16022 | -0.092979 | -0.17331 | 122.4528 | 0.02925 | 122.4895 | 122.4525 | -0.000303 | -0.017933 | 0.19235 | 122.2602 | -0.007046 | 122.4849 | 122.4229 | 0.16274 | 0.077825 | -0.17538 | 122.5451 | 122.4979 | 122.7082 | 122.444 | -0.063034 | 122.5088 | 122.5937 | 122.3405 | 122.4705 | -0.2557
2208.1719 | 122.644 | -122.4792 | 0.10986 | 1.4211e-13 | -0.028968 | 0.014252 | -0.0038527 | -0.013401 | 0.018416 | -0.23296 | 0.018225 | 0.018889 | 0.015385 | 0.034581 | 0.0090396 | 0.055988 | 0.010564 | 0.023639 | 0.11622 | 0.069043 | 0.27932 | 0.019363 | 0.055992 | 0.036989 | -0.015143 | 0.089087 | 0.16022 | -0.079243 | -0.17331 | 122.4986 | 0.006362 | 122.5352 | 122.5029 | 0.004276 | -0.04082 | 0.16946 | 122.3059 | -0.020776 | 122.5352 | 122.4641 | 0.15816 | 0.050359 | -0.18911 | 122.5955 | 122.5483 | 122.7586 | 122.4898 | -0.0905 | 122.5683 | 122.6395 | 122.4 | 122.5162 | -0.28317
2209.9219 | 122.6761 | -122.4838 | 0.091553 | 1.4211e-13 | -0.028968 | 0.014039 | -0.0038527 | -0.013187 | 0.018416 | -0.23296 | 0.018653 | 0.018676 | 0.015812 | 0.034581 | 0.0090396 | 0.055988 | 0.015142 | 0.01906 | 0.1208 | 0.055306 | 0.27932 | 0.0331 | 0.06515 | 0.03241 | -0.010564 | 0.07993 | 0.16938 | -0.060928 | -0.16415 | 122.5169 | 0.029251 | 122.5398 | 122.5029 | -0.01404 | -0.036247 | 0.18777 | 122.3197 | -0.011623 | 122.549 | 122.4733 | 0.15358 | 0.077826 | -0.15248 | 122.6046 | 122.5391 | 122.7631 | 122.499 | -0.058453 | 122.5638 | 122.6532 | 122.4229 | 122.5162 | -0.2557
2211.6562 | 122.7264 | -122.4747 | 0.086975 | 1.4211e-13 | -0.028968 | 0.014252 | -0.0040665 | -0.013187 | 0.018843 | -0.24059 | 0.018225 | 0.018462 | 0.015598 | 0.034795 | 0.0090396 | 0.046831 | 0.015142 | 0.023639 | 0.11165 | 0.059885 | 0.27475 | 0.019363 | 0.046835 | 0.03241 | -0.019721 | 0.084508 | 0.16022 | -0.060928 | -0.17331 | 122.494 | 0.024672 | 122.5215 | 122.4983 | 0.004276 | -0.02709 | 0.18777 | 122.3014 | -0.002467 | 122.5215 | 122.4549 | 0.15358 | 0.073247 | -0.1479 | 122.5863 | 122.5346 | 122.7494 | 122.4898 | -0.067612 | 122.5592 | 122.6349 | 122.4137 | 122.5071 | -0.26028
2213.4062 | 122.6898 | -122.4655 | 0.10071 | 1.4211e-13 | -0.028968 | 0.013825 | -0.0038527 | -0.013401 | 0.019057 | -0.24059 | 0.018012 | 0.018462 | 0.015598 | 0.034581 | 0.0090396 | 0.055988 | 0.010564 | 0.028217 | 0.11165 | 0.064464 | 0.27932 | 0.028521 | 0.055992 | 0.023253 | -0.015143 | 0.084508 | 0.1648 | -0.051771 | -0.17331 | 122.494 | 0.010939 | 122.5215 | 122.4937 | -0.000304 | -0.036244 | 0.17862 | 122.2922 | -0.0162 | 122.5215 | 122.4504 | 0.15816 | 0.064092 | -0.15248 | 122.5772 | 122.53 | 122.7448 | 122.4761 | -0.072187 | 122.55 | 122.6303 | 122.4137 | 122.4888 | -0.27401
2215.0938 | 122.7493 | -122.493 | 0.064087 | 1.4211e-13 | -0.02854 | 0.014252 | -0.0038527 | -0.013615 | 0.018629 | -0.23296 | 0.018012 | 0.018462 | 0.015385 | 0.034795 | 0.0090396 | 0.060567 | 0.001407 | 0.023639 | 0.11165 | 0.069043 | 0.27475 | 0.019363 | 0.051413 | 0.03241 | -0.015143 | 0.075351 | 0.1648 | -0.042614 | -0.16415 | 122.5123 | 0.04756 | 122.5535 | 122.5166 | 0.004276 | 0.004956 | 0.21066 | 122.3288 | 0.011264 | 122.5444 | 122.4778 | 0.14901 | 0.10071 | -0.1067 | 122.6046 | 122.562 | 122.7677 | 122.4944 | -0.044724 | 122.5683 | 122.6578 | 122.4504 | 122.5254 | -0.22824
2216.8281 | 122.7264 | -122.4564 | 0.10071 | 1.4211e-13 | -0.028754 | 0.014252 | -0.0038527 | -0.013401 | 0.018416 | -0.24822 | 0.018012 | 0.018676 | 0.015385 | 0.035008 | 0.008826 | 0.055988 | 0.010564 | 0.028217 | 0.11622 | 0.064464 | 0.27017 | 0.019363 | 0.055992 | 0.03241 | -0.015143 | 0.075351 | 0.16022 | -0.10671 | -0.17331 | 122.4757 | 0.015517 | 122.5123 | 122.4846 | 0.008854 | -0.036244 | 0.16946 | 122.2831 | -0.025357 | 122.5124 | 122.4412 | 0.15816 | 0.059514 | -0.20742 | 122.5726 | 122.5208 | 122.7265 | 122.4669 | -0.081345 | 122.5317 | 122.6166 | 122.3496 | 122.4888 | -0.27401
2218.5 | 122.6486 | -122.4701 | 0.11902 | 1.4211e-13 | -0.028754 | 0.014466 | -0.0038527 | -0.013401 | 0.018629 | -0.23296 | 0.018225 | 0.018249 | 0.015385 | 0.035008 | 0.0090396 | 0.055988 | 0.010564 | 0.023639 | 0.11165 | 0.059885 | 0.27475 | 0.023942 | 0.055992 | 0.027831 | -0.015143 | 0.093665 | 0.1648 | -0.11587 | -0.16873 | 122.494 | -0.007372 | 122.5261 | 122.4937 | -0.000303 | -0.059134 | 0.15573 | 122.3014 | -0.025354 | 122.5261 | 122.455 | 0.15358 | 0.045781 | -0.23489 | 122.5817 | 122.53 | 122.7448 | 122.4807 | -0.095077 | 122.5638 | 122.6349 | 122.3542 | 122.4979 | -0.28775
2220.1875 | 122.6303 | -122.4976 | 0.12817 | 1.4211e-13 | -0.028327 | 0.014039 | -0.0036391 | -0.013187 | 0.019057 | -0.22533 | 0.018225 | 0.018676 | 0.015598 | 0.034581 | 0.0090396 | 0.05141 | 0.001407 | 0.023639 | 0.12538 | 0.064464 | 0.27475 | 0.023942 | 0.055992 | 0.03241 | -0.010564 | 0.07993 | 0.16022 | 0.012329 | -0.16873 | 122.5215 | -0.002792 | 122.549 | 122.5212 | -0.000303 | -0.06371 | 0.14657 | 122.3288 | -0.048244 | 122.5536 | 122.487 | 0.15816 | 0.032048 | -0.11585 | 122.6229 | 122.562 | 122.7723 | 122.499 | -0.10423 | 122.5775 | 122.6578 | 122.5099 | 122.53 | -0.2969
2221.9219 | 122.6944 | -122.5067 | 0.13275 | 1.4211e-13 | -0.028968 | 0.014039 | -0.0038527 | -0.013187 | 0.018629 | -0.24059 | 0.018225 | 0.018889 | 0.015598 | 0.034367 | 0.0090396 | 0.05141 | 0.010564 | 0.01906 | 0.11622 | 0.064464 | 0.2839 | 0.014784 | 0.055992 | 0.027831 | -0.010564 | 0.089087 | 0.16938 | -0.11587 | -0.16415 | 122.5215 | -0.016526 | 122.5581 | 122.5258 | 0.004276 | -0.068287 | 0.15115 | 122.3426 | -0.043664 | 122.5627 | 122.4962 | 0.15358 | 0.036628 | -0.24862 | 122.6229 | 122.5712 | 122.7906 | 122.5173 | -0.11797 | 122.5958 | 122.6761 | 122.3908 | 122.5345 | -0.2969
2223.6875 | 122.7676 | -122.4701 | 0.086975 | 1.4211e-13 | -0.028754 | 0.013825 | -0.0040665 | -0.013401 | 0.018629 | -0.24059 | 0.017798 | 0.018249 | 0.015812 | 0.034795 | 0.0092534 | 0.055988 | 0.001407 | 0.01906 | 0.11622 | 0.069043 | 0.27932 | 0.019363 | 0.055992 | 0.03241 | -0.010564 | 0.084508 | 0.16022 | -0.079243 | -0.16873 | 122.4895 | 0.02925 | 122.5261 | 122.4892 | -0.000303 | -0.017932 | 0.19235 | 122.3014 | -0.002467 | 122.5261 | 122.4595 | 0.15816 | 0.073247 | -0.16622 | 122.5863 | 122.5391 | 122.7494 | 122.4715 | -0.067612 | 122.5546 | 122.6303 | 122.3909 | 122.5025 | -0.2557
2225.375 | 122.8043 | -122.4701 | 0.091553 | 1.4211e-13 | -0.029181 | 0.014252 | -0.0040665 | -0.013615 | 0.018202 | -0.24059 | 0.018225 | 0.018462 | 0.015171 | 0.034795 | 0.008826 | 0.055988 | 0.015142 | 0.01906 | 0.11622 | 0.073622 | 0.27932 | 0.019363 | 0.051413 | 0.03241 | -0.005985 | 0.075351 | 0.16938 | -0.083821 | -0.15957 | 122.4895 | 0.024672 | 122.5261 | 122.4892 | -0.000303 | -0.017931 | 0.18777 | 122.3105 | -0.016202 | 122.5215 | 122.4641 | 0.15358 | 0.077826 | -0.17537 | 122.5863 | 122.5437 | 122.7494 | 122.4852 | -0.07219 | 122.5454 | 122.6395 | 122.3863 | 122.5025 | -0.25112
2227.1094 | 122.7951 | -122.4426 | 0.082397 | 1.4211e-13 | -0.028754 | 0.014039 | -0.0040665 | -0.013401 | 0.018629 | -0.23296 | 0.018439 | 0.018676 | 0.015598 | 0.034795 | 0.0090396 | 0.05141 | 0.015142 | 0.023639 | 0.11622 | 0.073622 | 0.2839 | 0.019363 | 0.055992 | 0.036989 | -0.019721 | 0.084508 | 0.16938 | -0.079243 | -0.16415 | 122.462 | 0.033828 | 122.494 | 122.4663 | 0.004276 | -0.008775 | 0.20151 | 122.2785 | 0.002111 | 122.4986 | 122.4229 | 0.14443 | 0.086982 | -0.16164 | 122.5589 | 122.5162 | 122.7265 | 122.4578 | -0.063034 | 122.5271 | 122.612 | 122.3634 | 122.4796 | -0.24655
2228.875 | 122.7722 | -122.438 | 0.082397 | 1.4211e-13 | -0.02854 | 0.014039 | -0.0038527 | -0.013187 | 0.018629 | -0.23296 | 0.018225 | 0.018249 | 0.015598 | 0.034581 | 0.008826 | 0.055988 | 0.010564 | 0.023639 | 0.11165 | 0.055306 | 0.27475 | 0.028521 | 0.051413 | 0.023253 | -0.015143 | 0.07993 | 0.16938 | -0.097557 | -0.16873 | 122.4666 | 0.02925 | 122.494 | 122.4617 | -0.004882 | -0.027091 | 0.19235 | 122.2693 | -0.002467 | 122.4895 | 122.4229 | 0.15358 | 0.086982 | -0.17995 | 122.5497 | 122.4934 | 122.7128 | 122.4486 | -0.053876 | 122.518 | 122.6074 | 122.3405 | 122.4613 | -0.25112
2230.5625 | 122.7814 | -122.4609 | 0.086975 | 1.4211e-13 | -0.028968 | 0.014252 | -0.0040665 | -0.013401 | 0.018416 | -0.24822 | 0.018439 | 0.018676 | 0.015385 | 0.034795 | 0.0090396 | 0.055988 | 0.010564 | 0.023639 | 0.11165 | 0.064464 | 0.27932 | 0.019363 | 0.051413 | 0.027831 | -0.015143 | 0.07993 | 0.1648 | -0.060928 | -0.16873 | 122.4803 | 0.024672 | 122.5169 | 122.4846 | 0.004276 | -0.022511 | 0.19235 | 122.2922 | -0.007045 | 122.5123 | 122.4458 | 0.15358 | 0.077825 | -0.1479 | 122.5726 | 122.5254 | 122.7403 | 122.4715 | -0.067612 | 122.5409 | 122.6257 | 122.4 | 122.4888 | -0.2557
2232.3125 | 122.644 | -122.4976 | 0.1236 | 1.4211e-13 | -0.028754 | 0.014252 | -0.0036391 | -0.013401 | 0.018843 | -0.23296 | 0.018225 | 0.018462 | 0.015385 | 0.034581 | 0.0092534 | 0.055988 | 0.005985 | 0.023639 | 0.11165 | 0.064464 | 0.27932 | 0.023942 | 0.055992 | 0.03241 | -0.015143 | 0.084508 | 0.16938 | -0.0243 | -0.17331 | 122.5215 | -0.011949 | 122.5535 | 122.5212 | -0.000303 | -0.059132 | 0.15573 | 122.3243 | -0.039088 | 122.5536 | 122.4824 | 0.15816 | 0.045783 | -0.1479 | 122.6092 | 122.562 | 122.7769 | 122.5035 | -0.099654 | 122.5821 | 122.6669 | 122.4733 | 122.53 | -0.2969
2234 | 122.6624 | -122.5021 | 0.12817 | 1.4211e-13 | -0.028968 | 0.014466 | -0.0036391 | -0.013187 | 0.018416 | -0.24059 | 0.018439 | 0.018462 | 0.015385 | 0.034581 | 0.0090396 | 0.05141 | 0.015142 | 0.028217 | 0.11622 | 0.059885 | 0.2839 | 0.019363 | 0.051413 | 0.03241 | -0.015143 | 0.070773 | 0.1648 | -0.0884 | -0.16415 | 122.5215 | -0.011949 | 122.5535 | 122.5304 | 0.008854 | -0.068289 | 0.15573 | 122.338 | -0.057401 | 122.5535 | 122.487 | 0.14901 | 0.036626 | -0.21657 | 122.6184 | 122.562 | 122.786 | 122.5173 | -0.10881 | 122.5729 | 122.6669 | 122.4137 | 122.5345 | -0.29232
2235.75 | 122.7127 | -122.4701 | 0.10529 | 1.4211e-13 | -0.028754 | 0.014252 | -0.0038527 | -0.013187 | 0.018843 | -0.22533 | 0.018653 | 0.018462 | 0.015385 | 0.034795 | 0.008826 | 0.055988 | 0.005985 | 0.01906 | 0.11622 | 0.064464 | 0.27932 | 0.019363 | 0.055992 | 0.036989 | -0.0243 | 0.089087 | 0.1648 | -0.028878 | -0.16873 | 122.4895 | 0.010939 | 122.5261 | 122.4892 | -0.000303 | -0.040822 | 0.17404 | 122.3014 | -0.016199 | 122.5261 | 122.4458 | 0.14443 | 0.059514 | -0.13416 | 122.5863 | 122.5346 | 122.7494 | 122.4761 | -0.085923 | 122.5592 | 122.6349 | 122.4412 | 122.5071 | -0.27401
2237.4375 | 122.7402 | -122.4838 | 0.091553 | 1.4211e-13 | -0.028327 | 0.014466 | -0.0038527 | -0.013401 | 0.019057 | -0.23296 | 0.018012 | 0.018889 | 0.015598 | 0.034795 | 0.0092534 | 0.05141 | 0.015142 | 0.023639 | 0.11622 | 0.073622 | 0.27475 | 0.019363 | 0.051413 | 0.03241 | -0.010564 | 0.084508 | 0.16938 | -0.047193 | -0.16415 | 122.5032 | 0.024672 | 122.5352 | 122.5075 | 0.004276 | -0.017931 | 0.18319 | 122.3197 | -0.007045 | 122.5352 | 122.4733 | 0.15358 | 0.077826 | -0.13875 | 122.6001 | 122.5574 | 122.7586 | 122.499 | -0.07219 | 122.5683 | 122.6532 | 122.4366 | 122.5162 | -0.2557
2239.1875 | 122.7905 | -122.4609 | 0.073242 | 1.4211e-13 | -0.02854 | 0.014252 | -0.0036391 | -0.013401 | 0.018843 | -0.22533 | 0.018225 | 0.018462 | 0.015598 | 0.035008 | 0.008826 | 0.060567 | 0.010564 | 0.023639 | 0.1208 | 0.069043 | 0.27932 | 0.028521 | 0.051413 | 0.036989 | -0.019721 | 0.07993 | 0.16022 | -0.047193 | -0.16873 | 122.4895 | 0.047562 | 122.5215 | 122.4846 | -0.004882 | -0.004199 | 0.20608 | 122.2922 | 0.006688 | 122.5123 | 122.4412 | 0.14901 | 0.08698 | -0.12044 | 122.5817 | 122.53 | 122.7403 | 122.4715 | -0.044721 | 122.5409 | 122.6212 | 122.4137 | 122.4979 | -0.24197
2240.9531 | 122.6761 | -122.5296 | 0.11444 | 1.4211e-13 | -0.028754 | 0.014252 | -0.0038527 | -0.013615 | 0.01927 | -0.2177 | 0.018225 | 0.018676 | 0.015812 | 0.034581 | 0.008826 | 0.060567 | 0.015142 | 0.023639 | 0.11165 | 0.069043 | 0.27932 | 0.014784 | 0.051413 | 0.027831 | -0.015143 | 0.084508 | 0.1648 | -0.083821 | -0.15957 | 122.5444 | -0.002794 | 122.5902 | 122.5532 | 0.008855 | -0.045398 | 0.16488 | 122.37 | -0.029933 | 122.581 | 122.5145 | 0.14443 | 0.050359 | -0.19826 | 122.6412 | 122.5986 | 122.8089 | 122.5447 | -0.099657 | 122.6141 | 122.6944 | 122.4458 | 122.5574 | -0.27401
2242.7031 | 122.644 | -122.525 | 0.11444 | 1.4211e-13 | -0.02854 | 0.014252 | -0.0038527 | -0.013187 | 0.018843 | -0.23296 | 0.018225 | 0.018676 | 0.015385 | 0.034795 | 0.0092534 | 0.060567 | 0.010564 | 0.01906 | 0.11165 | 0.064464 | 0.27017 | 0.014784 | 0.055992 | 0.03241 | -0.010564 | 0.084508 | 0.1648 | -0.097557 | -0.16873 | 122.5398 | -0.002794 | 122.5856 | 122.5441 | 0.004276 | -0.049977 | 0.15573 | 122.3563 | -0.029933 | 122.581 | 122.5145 | 0.15816 | 0.050359 | -0.212 | 122.6367 | 122.5895 | 122.7952 | 122.5356 | -0.099657 | 122.6095 | 122.6898 | 122.4275 | 122.5574 | -0.28317
2244.375 | 122.731 | -122.493 | 0.11444 | 1.4211e-13 | -0.029181 | 0.013611 | -0.0038527 | -0.013401 | 0.018629 | -0.23296 | 0.018012 | 0.018462 | 0.015598 | 0.034581 | 0.0092534 | 0.055988 | 0.005985 | 0.014482 | 0.11165 | 0.069043 | 0.27932 | 0.005627 | 0.055992 | 0.036989 | -0.015143 | 0.084508 | 0.16938 | -0.074664 | -0.16873 | 122.4986 | -0.002794 | 122.549 | 122.5075 | 0.008855 | -0.045398 | 0.16488 | 122.3243 | -0.029933 | 122.549 | 122.4778 | 0.15358 | 0.054938 | -0.1891 | 122.6046 | 122.562 | 122.7723 | 122.499 | -0.10881 | 122.5775 | 122.6624 | 122.4183 | 122.53 | -0.28317
2246.125 | 122.6532 | -122.525 | 0.11902 | 1.4211e-13 | -0.028754 | 0.013825 | -0.0038527 | -0.013401 | 0.018843 | -0.22533 | 0.018225 | 0.018462 | 0.015598 | 0.034795 | 0.0092534 | 0.05141 | 0.010564 | 0.028217 | 0.11165 | 0.069043 | 0.27017 | 0.023942 | 0.051413 | 0.027831 | -0.015143 | 0.089087 | 0.1648 | -0.079243 | -0.16415 | 122.549 | -0.007372 | 122.5764 | 122.5532 | 0.004275 | -0.049976 | 0.15115 | 122.3609 | -0.029932 | 122.5764 | 122.5099 | 0.14901 | 0.045781 | -0.19826 | 122.6367 | 122.5941 | 122.7952 | 122.5356 | -0.095077 | 122.6141 | 122.6898 | 122.4458 | 122.5529 | -0.28317
2247.875 | 122.7585 | -122.4884 | 0.09613 | 1.4211e-13 | -0.02854 | 0.013825 | -0.0038527 | -0.013187 | 0.018416 | -0.23296 | 0.018225 | 0.018676 | 0.015385 | 0.034367 | 0.008826 | 0.055988 | 0.015142 | 0.01906 | 0.11622 | 0.069043 | 0.27017 | 0.014784 | 0.051413 | 0.023253 | -0.015143 | 0.07993 | 0.16022 | -0.065507 | -0.16415 | 122.5032 | 0.020095 | 122.5444 | 122.5075 | 0.004276 | -0.027087 | 0.17404 | 122.3243 | -0.0162 | 122.5398 | 122.4733 | 0.14901 | 0.064092 | -0.16164 | 122.6046 | 122.5574 | 122.7586 | 122.5035 | -0.081346 | 122.5683 | 122.6486 | 122.4229 | 122.5117 | -0.26028
2249.625 | 122.6624 | -122.4838 | 0.10529 | 1.4211e-13 | -0.028754 | 0.014252 | -0.0040665 | -0.012974 | 0.018416 | -0.22533 | 0.018225 | 0.018462 | 0.015385 | 0.034795 | 0.0090396 | 0.05141 | 0.005985 | 0.009904 | 0.11165 | 0.064464 | 0.27932 | 0.014784 | 0.051413 | 0.036989 | -0.010564 | 0.084508 | 0.1648 | -0.05635 | -0.16873 | 122.4986 | 0.006361 | 122.5352 | 122.4937 | -0.00488 | -0.040822 | 0.17404 | 122.3151 | -0.020778 | 122.5352 | 122.4733 | 0.15816 | 0.059514 | -0.16164 | 122.5955 | 122.5483 | 122.7631 | 122.4898 | -0.090502 | 122.5683 | 122.6486 | 122.4275 | 122.5208 | -0.27401
2251.3125 | 122.7997 | -122.4792 | 0.07782 | 1.4211e-13 | -0.02854 | 0.014466 | -0.0038527 | -0.013401 | 0.018843 | -0.23296 | 0.018012 | 0.018462 | 0.015385 | 0.035008 | 0.0090396 | 0.05141 | 0.010564 | 0.01906 | 0.11622 | 0.073622 | 0.27932 | 0.019363 | 0.055992 | 0.027831 | -0.019721 | 0.089087 | 0.15564 | -0.060928 | -0.16873 | 122.4986 | 0.038405 | 122.5307 | 122.4983 | -0.000303 | -0.004198 | 0.2015 | 122.3105 | 0.011267 | 122.5352 | 122.4595 | 0.14901 | 0.077823 | -0.13875 | 122.5955 | 122.5529 | 122.7586 | 122.4898 | -0.058457 | 122.5683 | 122.6349 | 122.4183 | 122.5071 | -0.24655
2253.0625 | 122.7997 | -122.4655 | 0.086975 | 1.4211e-13 | -0.02854 | 0.014039 | -0.0036391 | -0.013401 | 0.018629 | -0.22533 | 0.018012 | 0.018249 | 0.015598 | 0.034581 | 0.0090396 | 0.055988 | 0.005985 | 0.014482 | 0.11165 | 0.064464 | 0.27932 | 0.019363 | 0.051413 | 0.036989 | -0.015143 | 0.084508 | 0.16022 | -0.097557 | -0.17331 | 122.4849 | 0.024672 | 122.5215 | 122.48 | -0.004881 | -0.022511 | 0.19235 | 122.2922 | -0.002467 | 122.5169 | 122.4504 | 0.15816 | 0.073247 | -0.18453 | 122.5772 | 122.53 | 122.7448 | 122.4715 | -0.067612 | 122.55 | 122.6257 | 122.368 | 122.5025 | -0.26028
2254.8281 | 122.7219 | -122.4976 | 0.11444 | 1.4211e-13 | -0.028754 | 0.014252 | -0.0038527 | -0.013615 | 0.018843 | -0.23296 | 0.017798 | 0.018462 | 0.015385 | 0.034367 | 0.0096806 | 0.05141 | 0.010564 | 0.023639 | 0.11165 | 0.055306 | 0.27932 | 0.028521 | 0.046835 | 0.03241 | -0.015143 | 0.07993 | 0.1648 | -0.0884 | -0.16873 | 122.5261 | -0.002794 | 122.549 | 122.5212 | -0.004882 | -0.059135 | 0.16488 | 122.3288 | -0.034511 | 122.5444 | 122.4824 | 0.15358 | 0.050359 | -0.20284 | 122.6092 | 122.5529 | 122.7769 | 122.5081 | -0.08592 | 122.5775 | 122.6624 | 122.4092 | 122.53 | -0.28317
2256.5156 | 122.7448 | -122.493 | 0.10071 | 1.4211e-13 | -0.028754 | 0.014466 | -0.0038527 | -0.013401 | 0.018843 | -0.23296 | 0.018225 | 0.018249 | 0.015812 | 0.035008 | 0.0090396 | 0.060567 | 0.010564 | 0.01906 | 0.10707 | 0.064464 | 0.27475 | 0.023942 | 0.046835 | 0.041567 | -0.010564 | 0.07993 | 0.16022 | -0.0884 | -0.16873 | 122.5169 | 0.00636 | 122.5535 | 122.512 | -0.004882 | -0.036244 | 0.17404 | 122.3243 | -0.020778 | 122.5398 | 122.4824 | 0.15816 | 0.059514 | -0.18911 | 122.6 | 122.5574 | 122.7677 | 122.5035 | -0.076766 | 122.5729 | 122.6532 | 122.4046 | 122.5345 | -0.26944
2258.2656 | 122.6761 | -122.5296 | 0.1236 | 1.4211e-13 | -0.028754 | 0.014466 | -0.0036391 | -0.013401 | 0.018629 | -0.23296 | 0.018012 | 0.018462 | 0.015385 | 0.034795 | 0.0090396 | 0.046831 | 0.010564 | 0.01906 | 0.11165 | 0.069043 | 0.2839 | 0.023942 | 0.042256 | 0.03241 | -0.015143 | 0.084508 | 0.1648 | -0.10214 | -0.17331 | 122.5535 | -0.011949 | 122.5764 | 122.5487 | -0.004882 | -0.054553 | 0.16031 | 122.3563 | -0.039088 | 122.5719 | 122.5145 | 0.15816 | 0.041204 | -0.22573 | 122.6412 | 122.5986 | 122.8135 | 122.5402 | -0.099654 | 122.6141 | 122.6944 | 122.4275 | 122.562 | -0.2969
2260.0156 | 122.6669 | -122.5204 | 0.12817 | 1.4211e-13 | -0.028754 | 0.014039 | -0.0040665 | -0.013401 | 0.019057 | -0.24059 | 0.018012 | 0.018676 | 0.015598 | 0.034795 | 0.0090396 | 0.05141 | 0.015142 | 0.014482 | 0.11622 | 0.059885 | 0.28848 | 0.019363 | 0.060571 | 0.03241 | -0.015143 | 0.07993 | 0.15564 | -0.092979 | -0.16415 | 122.5398 | -0.011949 | 122.5719 | 122.5349 | -0.004881 | -0.068289 | 0.16031 | 122.3563 | -0.048244 | 122.581 | 122.5053 | 0.14901 | 0.027469 | -0.22115 | 122.6367 | 122.5803 | 122.8089 | 122.5356 | -0.10881 | 122.6004 | 122.6761 | 122.4275 | 122.5529 | -0.29232
2261.7031 | 122.7768 | -122.4884 | 0.10529 | 1.4211e-13 | -0.028754 | 0.014039 | -0.0038527 | -0.013401 | 0.018843 | -0.24059 | 0.018225 | 0.018462 | 0.015598 | 0.034795 | 0.009467 | 0.055988 | 0.015142 | 0.028217 | 0.1208 | 0.064464 | 0.27475 | 0.019363 | 0.060571 | 0.036989 | -0.015143 | 0.084508 | 0.1648 | -0.070086 | -0.16415 | 122.5078 | 0.015518 | 122.5444 | 122.5166 | 0.008854 | -0.040822 | 0.16946 | 122.3243 | -0.020778 | 122.549 | 122.4733 | 0.14901 | 0.059514 | -0.17537 | 122.6092 | 122.5529 | 122.7631 | 122.5035 | -0.085923 | 122.5729 | 122.6532 | 122.4183 | 122.5254 | -0.26943
2263.4531 | 122.8134 | -122.4976 | 0.082397 | 1.4211e-13 | -0.028327 | 0.014252 | -0.0036391 | -0.013401 | 0.018843 | -0.24059 | 0.018012 | 0.018249 | 0.015385 | 0.034795 | 0.008826 | 0.05141 | 0.010564 | 0.028217 | 0.11165 | 0.059885 | 0.27475 | 0.010206 | 0.055992 | 0.036989 | -0.010564 | 0.084508 | 0.16938 | -0.065507 | -0.16873 | 122.5078 | 0.02925 | 122.549 | 122.5258 | 0.018011 | -0.022512 | 0.19235 | 122.3288 | 0.002111 | 122.5536 | 122.487 | 0.15816 | 0.086982 | -0.1479 | 122.6092 | 122.5574 | 122.7723 | 122.5081 | -0.072191 | 122.5821 | 122.6669 | 122.4321 | 122.5345 | -0.25112
2265.1406 | 122.7722 | -122.4701 | 0.091553 | 1.4211e-13 | -0.028968 | 0.014466 | -0.0038527 | -0.013187 | 0.018629 | -0.24059 | 0.018012 | 0.018035 | 0.015385 | 0.034153 | 0.0090396 | 0.05141 | 0.010564 | 0.01906 | 0.11165 | 0.064464 | 0.27017 | 0.019363 | 0.051413 | 0.027831 | -0.019721 | 0.084508 | 0.14649 | -0.10671 | -0.15957 | 122.4895 | 0.020094 | 122.5215 | 122.4892 | -0.000303 | -0.027089 | 0.17861 | 122.3105 | -0.007045 | 122.5215 | 122.4504 | 0.13985 | 0.054933 | -0.19827 | 122.5817 | 122.5346 | 122.7403 | 122.4807 | -0.07219 | 122.5546 | 122.6166 | 122.3634 | 122.4979 | -0.25112
2266.875 | 122.7951 | -122.4838 | 0.091553 | 1.4211e-13 | -0.02854 | 0.014039 | -0.0040665 | -0.012974 | 0.018843 | -0.24059 | 0.018225 | 0.018676 | 0.015385 | 0.034581 | 0.0090396 | 0.060567 | 0.010564 | 0.023639 | 0.11622 | 0.059885 | 0.27017 | 0.019363 | 0.060571 | 0.036989 | -0.015143 | 0.084508 | 0.15564 | -0.051771 | -0.16415 | 122.5032 | 0.024672 | 122.5444 | 122.5075 | 0.004276 | -0.031668 | 0.17861 | 122.3197 | -0.007045 | 122.5444 | 122.4687 | 0.14901 | 0.06409 | -0.14332 | 122.6001 | 122.5437 | 122.754 | 122.4944 | -0.07219 | 122.5683 | 122.6395 | 122.4321 | 122.5208 | -0.2557
2268.6094 | 122.7951 | -122.4884 | 0.068665 | 1.4211e-13 | -0.028754 | 0.014252 | -0.0036391 | -0.013187 | 0.018843 | -0.23296 | 0.018225 | 0.018249 | 0.015598 | 0.034795 | 0.0090396 | 0.060567 | 0.010564 | 0.014482 | 0.11165 | 0.064464 | 0.27475 | 0.019363 | 0.051413 | 0.03241 | -0.010564 | 0.089087 | 0.16022 | -0.0884 | -0.17331 | 122.5078 | 0.042982 | 122.549 | 122.5029 | -0.004881 | -0.004201 | 0.20608 | 122.3151 | 0.020422 | 122.5398 | 122.4778 | 0.16274 | 0.091557 | -0.15707 | 122.6001 | 122.5529 | 122.7631 | 122.499 | -0.049302 | 122.5775 | 122.6486 | 122.4 | 122.5208 | -0.24197
2270.3594 | 122.7219 | -122.5204 | 0.10071 | 1.4211e-13 | -0.028754 | 0.014252 | -0.0040665 | -0.013187 | 0.018629 | -0.24059 | 0.018012 | 0.018676 | 0.015598 | 0.034795 | 0.008826 | 0.060567 | 0.005985 | 0.023639 | 0.1208 | 0.059885 | 0.27475 | 0.019363 | 0.051413 | 0.03241 | -0.019721 | 0.07993 | 0.15564 | -0.042614 | -0.17331 | 122.5398 | 0.020096 | 122.581 | 122.5441 | 0.004276 | -0.040823 | 0.17404 | 122.3471 | -0.020778 | 122.5719 | 122.5007 | 0.15358 | 0.054935 | -0.14332 | 122.6413 | 122.5803 | 122.7952 | 122.5264 | -0.081345 | 122.6004 | 122.6761 | 122.4778 | 122.5529 | -0.27401
2272.1094 | 122.6761 | -122.5204 | 0.1236 | 1.4211e-13 | -0.028327 | 0.01468 | -0.0038527 | -0.013828 | 0.018843 | -0.24059 | 0.018012 | 0.018676 | 0.015598 | 0.035008 | 0.0090396 | 0.046831 | 0.015142 | 0.023639 | 0.1208 | 0.055306 | 0.2839 | 0.023942 | 0.051413 | 0.036989 | -0.010564 | 0.07993 | 0.1648 | -0.070086 | -0.16873 | 122.5444 | -0.002792 | 122.5673 | 122.5441 | -0.000303 | -0.06829 | 0.16031 | 122.3517 | -0.043666 | 122.5719 | 122.5099 | 0.15816 | 0.041204 | -0.19368 | 122.6413 | 122.5758 | 122.8043 | 122.5356 | -0.099654 | 122.6004 | 122.6852 | 122.4504 | 122.5574 | -0.29232
2273.875 | 122.8134 | -122.4838 | 0.091553 | 1.4211e-13 | -0.028327 | 0.013825 | -0.0038527 | -0.013187 | 0.019057 | -0.23296 | 0.018225 | 0.018462 | 0.015812 | 0.034795 | 0.0086124 | 0.05141 | 0.015142 | 0.01906 | 0.11165 | 0.069043 | 0.27475 | 0.019363 | 0.051413 | 0.027831 | -0.015143 | 0.07993 | 0.15564 | -0.0884 | -0.16415 | 122.5032 | 0.020094 | 122.5352 | 122.5029 | -0.000303 | -0.02251 | 0.18319 | 122.3197 | -0.011623 | 122.5352 | 122.4687 | 0.14901 | 0.06409 | -0.17995 | 122.5955 | 122.5529 | 122.7586 | 122.499 | -0.07219 | 122.5638 | 122.6395 | 122.3954 | 122.5117 | -0.2557
2275.5625 | 122.7264 | -122.5159 | 0.10071 | 1.4211e-13 | -0.02854 | 0.014252 | -0.0038527 | -0.013187 | 0.019057 | -0.2177 | 0.018225 | 0.018676 | 0.015171 | 0.034795 | 0.0092534 | 0.055988 | 0.010564 | 0.01906 | 0.11622 | 0.059885 | 0.27932 | 0.023942 | 0.060571 | 0.036989 | -0.015143 | 0.084508 | 0.1648 | -0.079243 | -0.17331 | 122.5398 | 0.015517 | 122.5719 | 122.5349 | -0.004882 | -0.040823 | 0.17862 | 122.3426 | -0.0162 | 122.5764 | 122.5007 | 0.15816 | 0.064092 | -0.17995 | 122.6321 | 122.5758 | 122.7952 | 122.5264 | -0.076766 | 122.6004 | 122.6807 | 122.4366 | 122.5529 | -0.27401
2277.2969 | 122.7173 | -122.5479 | 0.086975 | 1.4211e-13 | -0.028754 | 0.014039 | -0.0040665 | -0.013615 | 0.018202 | -0.23296 | 0.018225 | 0.018676 | 0.015598 | 0.034581 | 0.0090396 | 0.060567 | 0.005985 | 0.028217 | 0.11622 | 0.069043 | 0.27932 | 0.014784 | 0.055992 | 0.036989 | -0.015143 | 0.07993 | 0.15564 | -0.070086 | -0.16873 | 122.5627 | 0.02925 | 122.6085 | 122.5761 | 0.013433 | -0.017932 | 0.19235 | 122.3792 | -0.007045 | 122.6039 | 122.5328 | 0.15358 | 0.068668 | -0.15706 | 122.6641 | 122.617 | 122.8272 | 122.5539 | -0.072191 | 122.6278 | 122.7036 | 122.4778 | 122.5849 | -0.2557
2279.0625 | 122.7081 | -122.5342 | 0.10986 | 1.4211e-13 | -0.028754 | 0.014039 | -0.0038527 | -0.013828 | 0.018416 | -0.23296 | 0.018225 | 0.018462 | 0.015385 | 0.034581 | 0.008826 | 0.055988 | 0.010564 | 0.023639 | 0.11622 | 0.064464 | 0.27475 | 0.014784 | 0.060571 | 0.027831 | -0.015143 | 0.089087 | 0.16022 | -0.11587 | -0.16873 | 122.549 | 0.006362 | 122.5902 | 122.5578 | 0.008855 | -0.045399 | 0.16488 | 122.3655 | -0.020776 | 122.5948 | 122.519 | 0.15358 | 0.050359 | -0.22574 | 122.6504 | 122.5986 | 122.8089 | 122.5447 | -0.095079 | 122.6233 | 122.6944 | 122.4183 | 122.562 | -0.27859
2280.75 | 122.7173 | -122.525 | 0.11444 | 1.4211e-13 | -0.02854 | 0.014252 | -0.0038527 | -0.013615 | 0.018629 | -0.24059 | 0.018225 | 0.018462 | 0.015385 | 0.034581 | 0.009467 | 0.05141 | 0.010564 | 0.01906 | 0.11165 | 0.064464 | 0.27475 | 0.023942 | 0.051413 | 0.03241 | -0.015143 | 0.089087 | 0.15564 | -0.079243 | -0.16873 | 122.549 | -0.002794 | 122.5764 | 122.5441 | -0.004882 | -0.049977 | 0.1603 | 122.3563 | -0.025354 | 122.5764 | 122.5099 | 0.15358 | 0.041202 | -0.19368 | 122.6367 | 122.5895 | 122.7998 | 122.5356 | -0.090499 | 122.6141 | 122.6807 | 122.4458 | 122.5574 | -0.28317
2282.4844 | 122.731 | -122.5388 | 0.10986 | 1.4211e-13 | -0.028327 | 0.013825 | -0.0038527 | -0.013615 | 0.018843 | -0.23296 | 0.018012 | 0.018462 | 0.015385 | 0.034581 | 0.0090396 | 0.060567 | 0.015142 | 0.023639 | 0.11622 | 0.055306 | 0.27932 | 0.005627 | 0.055992 | 0.036989 | -0.019721 | 0.093665 | 0.16022 | -0.083821 | -0.16873 | 122.5444 | 0.006362 | 122.5993 | 122.5624 | 0.018012 | -0.054557 | 0.16946 | 122.37 | -0.016198 | 122.5947 | 122.519 | 0.14901 | 0.050359 | -0.19368 | 122.655 | 122.5941 | 122.8181 | 122.5539 | -0.10424 | 122.6324 | 122.699 | 122.4549 | 122.5757 | -0.27859
2284.2031 | 122.6669 | -122.5525 | 0.10529 | 1.4211e-13 | -0.02854 | 0.01468 | -0.0036391 | -0.013615 | 0.018629 | -0.23296 | 0.017798 | 0.018249 | 0.015385 | 0.035008 | 0.0090396 | 0.055988 | 0.005985 | 0.014482 | 0.1208 | 0.059885 | 0.2839 | 0.019363 | 0.051413 | 0.03241 | -0.010564 | 0.084508 | 0.1648 | -0.079243 | -0.16415 | 122.5719 | 0.015518 | 122.6085 | 122.567 | -0.004881 | -0.045401 | 0.17862 | 122.3883 | -0.020778 | 122.6039 | 122.5419 | 0.15358 | 0.059514 | -0.18453 | 122.6733 | 122.6124 | 122.8364 | 122.5585 | -0.085923 | 122.637 | 122.7173 | 122.4732 | 122.5849 | -0.26943
2285.9219 | 122.7676 | -122.5021 | 0.091553 | 1.4211e-13 | -0.028327 | 0.014252 | -0.0040665 | -0.013615 | 0.019057 | -0.22533 | 0.018225 | 0.018676 | 0.015598 | 0.034581 | 0.0090396 | 0.05141 | 0.001407 | 0.01906 | 0.10707 | 0.064464 | 0.2839 | 0.019363 | 0.055992 | 0.03241 | -0.019721 | 0.084508 | 0.16938 | -0.047193 | -0.16415 | 122.5215 | 0.015515 | 122.5535 | 122.5212 | -0.000303 | -0.027089 | 0.19235 | 122.338 | -0.007045 | 122.5581 | 122.4824 | 0.14443 | 0.077826 | -0.13875 | 122.6092 | 122.5666 | 122.786 | 122.5035 | -0.07219 | 122.5866 | 122.6715 | 122.4549 | 122.5345 | -0.2557
2287.6719 | 122.7859 | -122.4976 | 0.086975 | 1.4211e-13 | -0.02854 | 0.013825 | -0.0040665 | -0.013187 | 0.018843 | -0.23296 | 0.018012 | 0.018462 | 0.015812 | 0.034795 | 0.0092534 | 0.046831 | 0.010564 | 0.01906 | 0.11622 | 0.069043 | 0.2839 | 0.019363 | 0.055992 | 0.027831 | -0.015143 | 0.07993 | 0.1648 | -0.12503 | -0.16415 | 122.5169 | 0.02925 | 122.5444 | 122.5166 | -0.000303 | -0.017932 | 0.19693 | 122.3334 | -0.007045 | 122.5536 | 122.4824 | 0.14901 | 0.077825 | -0.212 | 122.6138 | 122.5666 | 122.7815 | 122.5081 | -0.067612 | 122.5775 | 122.6624 | 122.3725 | 122.5254 | -0.25112
2289.4219 | 122.7676 | -122.5021 | 0.10529 | 1.4211e-13 | -0.028327 | 0.014252 | -0.0040665 | -0.013615 | 0.018629 | -0.23296 | 0.018439 | 0.018249 | 0.015598 | 0.034367 | 0.0090396 | 0.055988 | 0.005985 | 0.023639 | 0.11622 | 0.069043 | 0.2839 | 0.019363 | 0.055992 | 0.036989 | -0.015143 | 0.089087 | 0.16938 | -0.028878 | -0.16873 | 122.5215 | 0.010939 | 122.5581 | 122.5258 | 0.004276 | -0.036243 | 0.17862 | 122.3334 | -0.016199 | 122.5581 | 122.487 | 0.15358 | 0.064093 | -0.13416 | 122.6184 | 122.5712 | 122.786 | 122.5081 | -0.085923 | 122.5912 | 122.6715 | 122.4733 | 122.5391 | -0.27401
2291.125 | 122.6944 | -122.5525 | 0.13275 | 1.4211e-13 | -0.02854 | 0.014039 | -0.0038527 | -0.013401 | 0.018843 | -0.23296 | 0.018225 | 0.018676 | 0.015385 | 0.034795 | 0.008826 | 0.05141 | 0.015142 | 0.014482 | 0.11622 | 0.064464 | 0.27475 | 0.023942 | 0.051413 | 0.036989 | -0.015143 | 0.084508 | 0.1648 | -0.074664 | -0.16415 | 122.5764 | -0.016526 | 122.6039 | 122.567 | -0.00946 | -0.068287 | 0.14199 | 122.3883 | -0.048243 | 122.6039 | 122.5373 | 0.14901 | 0.032049 | -0.20742 | 122.6687 | 122.617 | 122.8272 | 122.5676 | -0.10881 | 122.637 | 122.7173 | 122.4778 | 122.5895 | -0.2969
2292.875 | 122.699 | -122.5021 | 0.11444 | 1.4211e-13 | -0.028968 | 0.014466 | -0.0038527 | -0.013401 | 0.018416 | -0.23296 | 0.018225 | 0.018462 | 0.015385 | 0.034367 | 0.0092534 | 0.05141 | 0.010564 | 0.028217 | 0.11165 | 0.064464 | 0.27932 | 0.019363 | 0.055992 | 0.036989 | -0.0243 | 0.089087 | 0.1648 | -0.092979 | -0.15957 | 122.5215 | -0.002794 | 122.5535 | 122.5304 | 0.008854 | -0.049977 | 0.16488 | 122.3426 | -0.025354 | 122.5581 | 122.4778 | 0.13527 | 0.050359 | -0.20742 | 122.6138 | 122.5666 | 122.7815 | 122.5127 | -0.095078 | 122.5912 | 122.6669 | 122.4092 | 122.5391 | -0.27401
2294.5469 | 122.8546 | -122.4792 | 0.068665 | 1.4211e-13 | -0.028327 | 0.014252 | -0.0040665 | -0.013401 | 0.018843 | -0.23296 | 0.017798 | 0.018462 | 0.015385 | 0.034581 | 0.0090396 | 0.05141 | 0.015142 | 0.028217 | 0.10707 | 0.064464 | 0.27475 | 0.019363 | 0.060571 | 0.03241 | -0.019721 | 0.07993 | 0.1648 | -0.05635 | -0.17331 | 122.4986 | 0.038403 | 122.5307 | 122.5075 | 0.008854 | -0.004201 | 0.20608 | 122.3059 | 0.011265 | 122.5398 | 122.4595 | 0.15358 | 0.096135 | -0.12501 | 122.5863 | 122.5437 | 122.754 | 122.4944 | -0.049302 | 122.5592 | 122.644 | 122.4229 | 122.5117 | -0.24197
2296.2969 | 122.699 | -122.5479 | 0.13275 | 1.4211e-13 | -0.02854 | 0.014252 | -0.0042801 | -0.013615 | 0.018416 | -0.23296 | 0.018225 | 0.018462 | 0.015598 | 0.034795 | 0.0092534 | 0.060567 | 0.015142 | 0.023639 | 0.11622 | 0.064464 | 0.2839 | 0.023942 | 0.055992 | 0.036989 | -0.010564 | 0.084508 | 0.16938 | -0.097557 | -0.15957 | 122.5719 | -0.016526 | 122.6085 | 122.5716 | -0.000303 | -0.068287 | 0.15115 | 122.3883 | -0.048243 | 122.6039 | 122.5373 | 0.14901 | 0.036628 | -0.23031 | 122.6641 | 122.6124 | 122.8318 | 122.5631 | -0.10881 | 122.6324 | 122.7173 | 122.4504 | 122.5849 | -0.29232
2297.9688 | 122.6898 | -122.5616 | 0.11902 | 1.4211e-13 | -0.028754 | 0.014252 | -0.0040665 | -0.013401 | 0.018629 | -0.2177 | 0.018439 | 0.018462 | 0.015385 | 0.034795 | 0.0092534 | 0.055988 | 0.005985 | 0.014482 | 0.11165 | 0.069043 | 0.27932 | 0.0331 | 0.051413 | 0.03241 | -0.019721 | 0.07993 | 0.16938 | -0.0884 | -0.16415 | 122.5947 | -0.007372 | 122.6176 | 122.5761 | -0.018618 | -0.049976 | 0.16031 | 122.3975 | -0.039089 | 122.6131 | 122.5419 | 0.14443 | 0.05036 | -0.20742 | 122.6733 | 122.6307 | 122.841 | 122.5676 | -0.085919 | 122.6416 | 122.731 | 122.4732 | 122.5941 | -0.28317
2299.7188 | 122.7264 | -122.5388 | 0.091553 | 1.4211e-13 | -0.028968 | 0.014039 | -0.0038527 | -0.013187 | 0.018843 | -0.23296 | 0.018225 | 0.018676 | 0.015385 | 0.034367 | 0.0092534 | 0.042253 | 0.005985 | 0.023639 | 0.11622 | 0.055306 | 0.27932 | 0.019363 | 0.051413 | 0.041567 | -0.010564 | 0.084508 | 0.16938 | -0.092979 | -0.17331 | 122.5581 | 0.024672 | 122.581 | 122.5624 | 0.004276 | -0.036247 | 0.18777 | 122.3655 | -0.007045 | 122.5902 | 122.5282 | 0.16274 | 0.077826 | -0.18453 | 122.655 | 122.5941 | 122.8181 | 122.5447 | -0.07219 | 122.6233 | 122.7081 | 122.4458 | 122.5803 | -0.26486
2301.4062 | 122.731 | -122.5296 | 0.10071 | 1.4211e-13 | -0.02854 | 0.014252 | -0.0038527 | -0.013828 | 0.018416 | -0.23296 | 0.018012 | 0.018462 | 0.015598 | 0.034795 | 0.0090396 | 0.046831 | 0.015142 | 0.023639 | 0.1208 | 0.069043 | 0.27932 | 0.019363 | 0.055992 | 0.036989 | -0.019721 | 0.084508 | 0.1648 | -0.097557 | -0.16873 | 122.549 | 0.020096 | 122.5764 | 122.5532 | 0.004276 | -0.031665 | 0.17862 | 122.3609 | -0.0162 | 122.5856 | 122.5099 | 0.14901 | 0.064092 | -0.19827 | 122.6504 | 122.5986 | 122.8089 | 122.5447 | -0.081345 | 122.6141 | 122.6944 | 122.432 | 122.5666 | -0.26944
2303.1406 | 122.6852 | -122.5662 | 0.11444 | 1.4211e-13 | -0.028754 | 0.014252 | -0.0042801 | -0.013401 | 0.018843 | -0.23296 | 0.018225 | 0.018249 | 0.015385 | 0.034581 | 0.0090396 | 0.060567 | 0.005985 | 0.023639 | 0.11165 | 0.069043 | 0.27475 | 0.023942 | 0.051413 | 0.03241 | -0.010564 | 0.07993 | 0.16022 | -0.051771 | -0.15957 | 122.5902 | -0.002794 | 122.6268 | 122.5899 | -0.000303 | -0.045398 | 0.1603 | 122.4067 | -0.034511 | 122.6176 | 122.5557 | 0.14901 | 0.045781 | -0.16621 | 122.6779 | 122.6353 | 122.841 | 122.5722 | -0.090499 | 122.6462 | 122.7264 | 122.5145 | 122.5986 | -0.27401
2304.8906 | 122.7768 | -122.525 | 0.10529 | 1.4211e-13 | -0.02854 | 0.014252 | -0.0040665 | -0.013401 | 0.018843 | -0.23296 | 0.018225 | 0.018249 | 0.015385 | 0.034581 | 0.0092534 | 0.055988 | 0.010564 | 0.01906 | 0.11165 | 0.069043 | 0.27932 | 0.028521 | 0.051413 | 0.03241 | -0.019721 | 0.084508 | 0.16022 | -0.0884 | -0.17331 | 122.5535 | 0.006361 | 122.581 | 122.5441 | -0.009461 | -0.036243 | 0.17404 | 122.3517 | -0.020778 | 122.5764 | 122.5053 | 0.15358 | 0.054936 | -0.19369 | 122.6367 | 122.5941 | 122.8043 | 122.5356 | -0.076765 | 122.6095 | 122.6852 | 122.4366 | 122.5574 | -0.27859
2306.5781 | 122.6898 | -122.5433 | 0.1236 | 1.4211e-13 | -0.028754 | 0.014466 | -0.0042801 | -0.013401 | 0.018416 | -0.22533 | 0.018012 | 0.018249 | 0.015812 | 0.034367 | 0.0090396 | 0.055988 | 0.010564 | 0.01906 | 0.11622 | 0.064464 | 0.27932 | 0.014784 | 0.051413 | 0.03241 | -0.015143 | 0.084508 | 0.16938 | -0.074664 | -0.16873 | 122.5581 | -0.007371 | 122.5993 | 122.5624 | 0.004276 | -0.059132 | 0.15573 | 122.3746 | -0.039088 | 122.5947 | 122.5282 | 0.15358 | 0.045783 | -0.19826 | 122.6596 | 122.6078 | 122.8227 | 122.5539 | -0.10881 | 122.6278 | 122.7127 | 122.4687 | 122.5757 | -0.29232
2308.3281 | 122.7493 | -122.5342 | 0.10529 | 1.4211e-13 | -0.028327 | 0.014252 | -0.0040665 | -0.013615 | 0.018416 | -0.23296 | 0.018225 | 0.018462 | 0.015598 | 0.034581 | 0.009467 | 0.05141 | 0.010564 | 0.01906 | 0.10707 | 0.064464 | 0.27932 | 0.023942 | 0.055992 | 0.027831 | -0.019721 | 0.07993 | 0.1648 | -0.10214 | -0.16415 | 122.5581 | 0.001782 | 122.5856 | 122.5532 | -0.004882 | -0.040822 | 0.17404 | 122.37 | -0.025356 | 122.5902 | 122.5145 | 0.14443 | 0.059514 | -0.20742 | 122.6412 | 122.5986 | 122.8135 | 122.5447 | -0.081344 | 122.6141 | 122.699 | 122.432 | 122.562 | -0.26943
2310.0781 | 122.7814 | -122.5204 | 0.073242 | 1.4211e-13 | -0.028327 | 0.014039 | -0.0038527 | -0.012974 | 0.019057 | -0.23296 | 0.018012 | 0.018462 | 0.015385 | 0.034795 | 0.009467 | 0.060567 | 0.005985 | 0.014482 | 0.11622 | 0.059885 | 0.27932 | 0.019363 | 0.046835 | 0.027831 | -0.015143 | 0.084508 | 0.16938 | -0.079243 | -0.17331 | 122.5398 | 0.042983 | 122.581 | 122.5349 | -0.004881 | -0.013357 | 0.20608 | 122.3471 | 0.011266 | 122.5673 | 122.5053 | 0.15816 | 0.096137 | -0.15248 | 122.6367 | 122.5803 | 122.7998 | 122.5264 | -0.053879 | 122.605 | 122.6898 | 122.4412 | 122.5483 | -0.24655
2311.8281 | 122.7859 | -122.5113 | 0.086975 | 1.4211e-13 | -0.028754 | 0.014252 | -0.0040665 | -0.013187 | 0.018843 | -0.2177 | 0.018225 | 0.018462 | 0.015385 | 0.034581 | 0.008826 | 0.055988 | 0.010564 | 0.023639 | 0.11165 | 0.064464 | 0.27932 | 0.023942 | 0.055992 | 0.027831 | -0.0243 | 0.089087 | 0.1648 | -0.047193 | -0.17331 | 122.5352 | 0.024672 | 122.5673 | 122.5349 | -0.000303 | -0.022511 | 0.19235 | 122.338 | 0.002112 | 122.5673 | 122.487 | 0.14901 | 0.077825 | -0.13417 | 122.6229 | 122.5758 | 122.7906 | 122.5219 | -0.063033 | 122.6004 | 122.6761 | 122.4641 | 122.5391 | -0.26028
2313.5938 | 122.7402 | -122.5479 | 0.11444 | 1.4211e-13 | -0.028327 | 0.014039 | -0.0038527 | -0.013401 | 0.018843 | -0.23296 | 0.018225 | 0.018462 | 0.015598 | 0.034367 | 0.0090396 | 0.046831 | 0.010564 | 0.023639 | 0.11622 | 0.069043 | 0.2839 | 0.014784 | 0.051413 | 0.03241 | -0.019721 | 0.084508 | 0.16938 | -0.083821 | -0.17331 | 122.5627 | 0.001784 | 122.5947 | 122.5716 | 0.008855 | -0.045398 | 0.16946 | 122.3746 | -0.029933 | 122.5993 | 122.5282 | 0.15358 | 0.054938 | -0.19826 | 122.6641 | 122.617 | 122.8318 | 122.5585 | -0.099657 | 122.6324 | 122.7173 | 122.4641 | 122.5803 | -0.28775
2315.2812 | 122.8409 | -122.525 | 0.086975 | 1.4211e-13 | -0.02854 | 0.014252 | -0.0036391 | -0.013401 | 0.018629 | -0.22533 | 0.018439 | 0.018462 | 0.015598 | 0.034581 | 0.008826 | 0.055988 | 0.010564 | 0.023639 | 0.11622 | 0.064464 | 0.27932 | 0.019363 | 0.055992 | 0.036989 | -0.005985 | 0.07993 | 0.16022 | -0.070086 | -0.17331 | 122.5444 | 0.02925 | 122.581 | 122.5487 | 0.004276 | -0.022511 | 0.19235 | 122.3517 | -0.007045 | 122.581 | 122.519 | 0.16732 | 0.073247 | -0.15706 | 122.6412 | 122.5895 | 122.8043 | 122.5356 | -0.067612 | 122.605 | 122.6852 | 122.4549 | 122.562 | -0.26028
2317.0312 | 122.7219 | -122.5662 | 0.10529 | 1.4211e-13 | -0.028968 | 0.014252 | -0.0038527 | -0.013187 | 0.018629 | -0.24059 | 0.018012 | 0.018462 | 0.015385 | 0.034367 | 0.0090396 | 0.046831 | 0.010564 | 0.014482 | 0.10707 | 0.059885 | 0.2839 | 0.019363 | 0.055992 | 0.03241 | -0.010564 | 0.084508 | 0.1648 | -0.10671 | -0.16873 | 122.5856 | 0.001782 | 122.6131 | 122.5807 | -0.004881 | -0.045401 | 0.17862 | 122.3975 | -0.020778 | 122.6222 | 122.5557 | 0.15816 | 0.059514 | -0.212 | 122.6733 | 122.6261 | 122.8501 | 122.5768 | -0.085923 | 122.6507 | 122.731 | 122.4595 | 122.5986 | -0.27401
2318.7812 | 122.7448 | -122.5388 | 0.10529 | 1.4211e-13 | -0.02854 | 0.014466 | -0.0034253 | -0.013401 | 0.019057 | -0.22533 | 0.018012 | 0.018035 | 0.015385 | 0.035008 | 0.0090396 | 0.060567 | 0.015142 | 0.028217 | 0.1208 | 0.059885 | 0.27475 | 0.023942 | 0.051413 | 0.036989 | -0.010564 | 0.084508 | 0.16022 | -0.083821 | -0.16873 | 122.5627 | 0.015518 | 122.5993 | 122.567 | 0.004275 | -0.045401 | 0.16946 | 122.37 | -0.020778 | 122.5902 | 122.5282 | 0.15816 | 0.054936 | -0.18911 | 122.6596 | 122.5986 | 122.8135 | 122.5539 | -0.081344 | 122.6233 | 122.699 | 122.4549 | 122.5757 | -0.27401
2320.4688 | 122.699 | -122.5433 | 0.12817 | 1.4211e-13 | -0.028327 | 0.014252 | -0.0040665 | -0.013401 | 0.018843 | -0.23296 | 0.018439 | 0.018676 | 0.015385 | 0.035008 | 0.0092534 | 0.055988 | 0.005985 | 0.01906 | 0.11165 | 0.064464 | 0.27932 | 0.014784 | 0.051413 | 0.036989 | -0.019721 | 0.084508 | 0.16022 | -0.10671 | -0.16415 | 122.5581 | -0.016527 | 122.5993 | 122.5624 | 0.004276 | -0.06371 | 0.15115 | 122.3792 | -0.043666 | 122.5947 | 122.5236 | 0.14443 | 0.032048 | -0.23489 | 122.655 | 122.6078 | 122.8227 | 122.5493 | -0.11339 | 122.6278 | 122.7036 | 122.4366 | 122.5803 | -0.29232
2322.2031 | 122.7585 | -122.5388 | 0.10986 | 1.4211e-13 | -0.02854 | 0.014252 | -0.0036391 | -0.013401 | 0.018843 | -0.24059 | 0.018012 | 0.018462 | 0.015385 | 0.034581 | 0.0090396 | 0.055988 | 0.005985 | 0.023639 | 0.11165 | 0.064464 | 0.27475 | 0.023942 | 0.051413 | 0.03241 | -0.010564 | 0.07993 | 0.1648 | -0.0884 | -0.16873 | 122.5627 | 0.001784 | 122.5947 | 122.5624 | -0.000303 | -0.045399 | 0.16488 | 122.37 | -0.029933 | 122.5902 | 122.5282 | 0.15816 | 0.054937 | -0.19826 | 122.6504 | 122.6032 | 122.8135 | 122.5447 | -0.085921 | 122.6187 | 122.7036 | 122.4504 | 122.5712 | -0.27859
2323.9531 | 122.7951 | -122.5204 | 0.09613 | 1.4211e-13 | -0.028754 | 0.014252 | -0.0038527 | -0.013187 | 0.018629 | -0.22533 | 0.018012 | 0.018249 | 0.015598 | 0.034367 | 0.009467 | 0.055988 | 0.019721 | 0.023639 | 0.11165 | 0.069043 | 0.27932 | 0.019363 | 0.055992 | 0.036989 | -0.015143 | 0.07993 | 0.1648 | -0.092979 | -0.16873 | 122.5398 | 0.015517 | 122.5764 | 122.5441 | 0.004276 | -0.027087 | 0.18319 | 122.3517 | -0.0162 | 122.5764 | 122.5053 | 0.15358 | 0.06867 | -0.18911 | 122.6321 | 122.5895 | 122.7998 | 122.5402 | -0.076767 | 122.6004 | 122.6852 | 122.4275 | 122.5574 | -0.26486
2325.7188 | 122.8363 | -122.4976 | 0.09613 | 1.4211e-13 | -0.02854 | 0.013825 | -0.0036391 | -0.013187 | 0.018843 | -0.23296 | 0.018225 | 0.018676 | 0.015598 | 0.034367 | 0.0092534 | 0.055988 | 0.005985 | 0.023639 | 0.1208 | 0.064464 | 0.27017 | 0.014784 | 0.051413 | 0.03241 | -0.019721 | 0.084508 | 0.16022 | -0.083821 | -0.17331 | 122.5123 | 0.024674 | 122.5535 | 122.5212 | 0.008855 | -0.031666 | 0.17404 | 122.3243 | -0.011622 | 122.549 | 122.4778 | 0.15358 | 0.064092 | -0.17995 | 122.6184 | 122.562 | 122.7677 | 122.5035 | -0.081346 | 122.5821 | 122.6578 | 122.4137 | 122.53 | -0.26944
2327.3906 | 122.8455 | -122.5067 | 0.10986 | 1.4211e-13 | -0.028754 | 0.014252 | -0.0034253 | -0.013615 | 0.018843 | -0.23296 | 0.018439 | 0.018676 | 0.015385 | 0.034367 | 0.008826 | 0.046831 | 0.019721 | 0.014482 | 0.1208 | 0.064464 | 0.28848 | 0.019363 | 0.051413 | 0.036989 | -0.015143 | 0.084508 | 0.1648 | -0.11587 | -0.16873 | 122.5261 | 0.010941 | 122.5535 | 122.5212 | -0.004881 | -0.045399 | 0.17862 | 122.338 | -0.025355 | 122.5581 | 122.4916 | 0.15358 | 0.054937 | -0.22574 | 122.6275 | 122.5712 | 122.7952 | 122.5264 | -0.0905 | 122.5912 | 122.6715 | 122.3908 | 122.5437 | -0.27859
2329.0781 | 122.8226 | -122.5113 | 0.082397 | 1.4211e-13 | -0.02854 | 0.014252 | -0.0038527 | -0.013187 | 0.018416 | -0.23296 | 0.018225 | 0.018462 | 0.015385 | 0.034367 | 0.0090396 | 0.05141 | 0.019721 | 0.01906 | 0.11622 | 0.064464 | 0.27932 | 0.019363 | 0.055992 | 0.03241 | -0.015143 | 0.084508 | 0.17396 | -0.038035 | -0.16873 | 122.5307 | 0.033828 | 122.5627 | 122.5304 | -0.000303 | -0.017933 | 0.19693 | 122.3426 | 0.002111 | 122.5673 | 122.4961 | 0.15358 | 0.091561 | -0.12043 | 122.6275 | 122.5758 | 122.7906 | 122.531 | -0.063034 | 122.5958 | 122.6852 | 122.4733 | 122.5437 | -0.25112
2330.8438 | 122.7722 | -122.5433 | 0.082397 | 1.4211e-13 | -0.02854 | 0.014252 | -0.0038527 | -0.013187 | 0.018843 | -0.22533 | 0.018012 | 0.018676 | 0.015171 | 0.034581 | 0.0090396 | 0.055988 | 0.005985 | 0.023639 | 0.12538 | 0.064464 | 0.27932 | 0.019363 | 0.055992 | 0.03241 | -0.010564 | 0.07993 | 0.1648 | -0.074664 | -0.16873 | 122.5627 | 0.042985 | 122.5993 | 122.567 | 0.004276 | -0.017933 | 0.19693 | 122.3746 | -0.002467 | 122.5993 | 122.5328 | 0.15816 | 0.082403 | -0.15706 | 122.6687 | 122.6078 | 122.8227 | 122.5493 | -0.063034 | 122.6233 | 122.7081 | 122.4687 | 122.5757 | -0.25112
2332.5938 | 122.731 | -122.5571 | 0.11444 | 1.4211e-13 | -0.02854 | 0.014039 | -0.0038527 | -0.013401 | 0.018843 | -0.23296 | 0.018225 | 0.018462 | 0.015385 | 0.034581 | 0.0090396 | 0.055988 | 0.010564 | 0.01906 | 0.11622 | 0.055306 | 0.28848 | 0.019363 | 0.055992 | 0.03241 | -0.015143 | 0.07993 | 0.16938 | -0.0884 | -0.16873 | 122.5764 | 0.001784 | 122.6131 | 122.5761 | -0.000303 | -0.059135 | 0.17404 | 122.3883 | -0.034511 | 122.6131 | 122.5419 | 0.15358 | 0.054938 | -0.20284 | 122.6733 | 122.6124 | 122.8455 | 122.5676 | -0.095078 | 122.637 | 122.7264 | 122.4687 | 122.5895 | -0.28317
2334.3438 | 122.7356 | -122.5479 | 0.091553 | 1.4211e-13 | -0.02854 | 0.01468 | -0.0036391 | -0.013187 | 0.018416 | -0.24059 | 0.018225 | 0.018462 | 0.015598 | 0.034581 | 0.0092534 | 0.055988 | 0.010564 | 0.023639 | 0.11165 | 0.069043 | 0.2839 | 0.023942 | 0.051413 | 0.027831 | -0.0243 | 0.084508 | 0.16938 | -0.060928 | -0.16873 | 122.5719 | 0.020094 | 122.6039 | 122.5716 | -0.000303 | -0.02251 | 0.19235 | 122.3792 | -0.007045 | 122.5993 | 122.5236 | 0.14443 | 0.077826 | -0.15248 | 122.6596 | 122.617 | 122.8318 | 122.5585 | -0.067611 | 122.6324 | 122.7173 | 122.487 | 122.5757 | -0.26028
2336.1094 | 122.7448 | -122.5388 | 0.1236 | 1.4211e-13 | -0.02854 | 0.014466 | -0.0038527 | -0.013401 | 0.018629 | -0.23296 | 0.018439 | 0.018249 | 0.015598 | 0.034367 | 0.0092534 | 0.065145 | 0.010564 | 0.023639 | 0.1208 | 0.064464 | 0.2839 | 0.019363 | 0.055992 | 0.036989 | -0.010564 | 0.084508 | 0.1648 | -0.083821 | -0.17788 | 122.5581 | -0.002792 | 122.6039 | 122.5624 | 0.004276 | -0.059132 | 0.16031 | 122.3609 | -0.039088 | 122.5947 | 122.5282 | 0.16732 | 0.041204 | -0.20742 | 122.6596 | 122.6032 | 122.8227 | 122.5493 | -0.10423 | 122.6233 | 122.7036 | 122.4549 | 122.5757 | -0.30148
2337.7969 | 122.7356 | -122.5708 | 0.10529 | 1.4211e-13 | -0.028327 | 0.014039 | -0.0036391 | -0.013187 | 0.018843 | -0.24059 | 0.018439 | 0.018035 | 0.015598 | 0.034581 | 0.0092534 | 0.05141 | 0.015142 | 0.023639 | 0.11622 | 0.059885 | 0.2839 | 0.019363 | 0.051413 | 0.03241 | -0.010564 | 0.089087 | 0.16022 | -0.051771 | -0.16873 | 122.5902 | 0.010939 | 122.6222 | 122.5944 | 0.004276 | -0.045401 | 0.17862 | 122.4021 | -0.016199 | 122.6222 | 122.5602 | 0.15816 | 0.054936 | -0.15706 | 122.687 | 122.6307 | 122.8547 | 122.5859 | -0.085923 | 122.6599 | 122.731 | 122.519 | 122.6032 | -0.27401
2339.5469 | 122.85 | -122.5388 | 0.082397 | 1.4211e-13 | -0.028327 | 0.014252 | -0.0040665 | -0.013401 | 0.019057 | -0.23296 | 0.018012 | 0.018889 | 0.015812 | 0.034795 | 0.0090396 | 0.05141 | 0.010564 | 0.014482 | 0.11165 | 0.069043 | 0.27932 | 0.019363 | 0.051413 | 0.036989 | -0.015143 | 0.084508 | 0.1648 | -0.092979 | -0.16415 | 122.5581 | 0.02925 | 122.5902 | 122.5532 | -0.004881 | -0.013354 | 0.19693 | 122.3746 | 0.002111 | 122.5902 | 122.5236 | 0.14901 | 0.082403 | -0.17538 | 122.6504 | 122.6078 | 122.8181 | 122.5493 | -0.063034 | 122.6233 | 122.7036 | 122.4458 | 122.5757 | -0.24655
2341.2969 | 122.7448 | -122.5616 | 0.086975 | 1.4211e-13 | -0.028327 | 0.014252 | -0.0036391 | -0.013187 | 0.019057 | -0.22533 | 0.018225 | 0.018462 | 0.015598 | 0.034795 | 0.0092534 | 0.05141 | 0.010564 | 0.01906 | 0.11165 | 0.064464 | 0.27932 | 0.019363 | 0.055992 | 0.041567 | -0.015143 | 0.084508 | 0.17396 | -0.092979 | -0.16415 | 122.581 | 0.024672 | 122.6131 | 122.5807 | -0.000303 | -0.022511 | 0.19235 | 122.3975 | -0.002467 | 122.6176 | 122.5465 | 0.14901 | 0.086983 | -0.17995 | 122.6733 | 122.6261 | 122.841 | 122.5722 | -0.067612 | 122.6462 | 122.7356 | 122.4687 | 122.6032 | -0.25112
2343.0469 | 122.7814 | -122.5571 | 0.1236 | 1.4211e-13 | -0.028327 | 0.014466 | -0.0038527 | -0.013401 | 0.018843 | -0.24059 | 0.018012 | 0.018249 | 0.015385 | 0.034581 | 0.0090396 | 0.055988 | 0.015142 | 0.014482 | 0.11165 | 0.064464 | 0.27932 | 0.019363 | 0.055992 | 0.03241 | -0.010564 | 0.084508 | 0.16022 | -0.097557 | -0.16415 | 122.5764 | -0.011949 | 122.6131 | 122.5716 | -0.004881 | -0.059132 | 0.15573 | 122.3929 | -0.039088 | 122.6131 | 122.5465 | 0.15358 | 0.036626 | -0.22115 | 122.6687 | 122.6215 | 122.8364 | 122.5722 | -0.10423 | 122.6416 | 122.7173 | 122.4595 | 122.5895 | -0.28774
2344.7344 | 122.8455 | -122.5113 | 0.082397 | 1.4211e-13 | -0.028113 | 0.01468 | -0.0040665 | -0.012974 | 0.018843 | -0.22533 | 0.018439 | 0.018249 | 0.015598 | 0.034367 | 0.0090396 | 0.05141 | 0.010564 | 0.01906 | 0.11165 | 0.064464 | 0.29306 | 0.014784 | 0.046835 | 0.03241 | -0.019721 | 0.07993 | 0.1648 | -0.051771 | -0.15957 | 122.5261 | 0.02925 | 122.5627 | 122.5304 | 0.004276 | -0.017933 | 0.21066 | 122.3517 | -0.002467 | 122.5581 | 122.4916 | 0.13985 | 0.082403 | -0.13417 | 122.6229 | 122.5758 | 122.8044 | 122.5219 | -0.067613 | 122.5912 | 122.6761 | 122.4595 | 122.5437 | -0.24197
2346.5 | 122.7127 | -122.5891 | 0.11902 | 1.4211e-13 | -0.028327 | 0.01468 | -0.0038527 | -0.013828 | 0.018629 | -0.23296 | 0.018225 | 0.018676 | 0.015171 | 0.034367 | 0.0090396 | 0.055988 | 0.010564 | 0.014482 | 0.11165 | 0.064464 | 0.27932 | 0.019363 | 0.055992 | 0.036989 | -0.015143 | 0.084508 | 0.16938 | -0.0884 | -0.16873 | 122.6085 | -0.007372 | 122.6451 | 122.6036 | -0.004881 | -0.054555 | 0.16031 | 122.4204 | -0.034511 | 122.6451 | 122.574 | 0.15358 | 0.05036 | -0.20742 | 122.7008 | 122.6536 | 122.8684 | 122.5997 | -0.099656 | 122.6736 | 122.7585 | 122.5007 | 122.6261 | -0.28775
2348.1719 | 122.7173 | -122.58 | 0.10529 | 1.4211e-13 | -0.02854 | 0.014039 | -0.0034253 | -0.013187 | 0.018629 | -0.23296 | 0.018225 | 0.018462 | 0.015598 | 0.034367 | 0.0092534 | 0.055988 | 0.015142 | 0.01906 | 0.10707 | 0.069043 | 0.27932 | 0.028521 | 0.060571 | 0.03241 | -0.015143 | 0.07993 | 0.16022 | -0.074664 | -0.16415 | 122.6085 | 0.001782 | 122.6359 | 122.599 | -0.009461 | -0.036243 | 0.17404 | 122.4158 | -0.025356 | 122.6405 | 122.5648 | 0.14901 | 0.054936 | -0.17995 | 122.687 | 122.649 | 122.8593 | 122.5951 | -0.076765 | 122.6599 | 122.7402 | 122.5053 | 122.6124 | -0.26943
2349.9062 | 122.8592 | -122.5021 | 0.064087 | 1.4211e-13 | -0.028327 | 0.014252 | -0.0038527 | -0.013401 | 0.018843 | -0.22533 | 0.018225 | 0.018249 | 0.015598 | 0.034795 | 0.0092534 | 0.055988 | 0.019721 | 0.01906 | 0.11165 | 0.064464 | 0.27017 | 0.019363 | 0.055992 | 0.023253 | -0.015143 | 0.075351 | 0.1648 | -0.092979 | -0.16873 | 122.5215 | 0.04756 | 122.5581 | 122.5212 | -0.000303 | 0.000377 | 0.20608 | 122.3334 | 0.011264 | 122.5581 | 122.487 | 0.15358 | 0.10071 | -0.15707 | 122.6138 | 122.5666 | 122.7723 | 122.5219 | -0.044724 | 122.5775 | 122.6669 | 122.4092 | 122.5254 | -0.23281
2351.5938 | 122.818 | -122.525 | 0.082397 | 1.4211e-13 | -0.02854 | 0.014039 | -0.0038527 | -0.013401 | 0.019057 | -0.24059 | 0.018225 | 0.018462 | 0.015385 | 0.034367 | 0.0092534 | 0.05141 | 0.019721 | 0.01906 | 0.11622 | 0.069043 | 0.27475 | 0.014784 | 0.055992 | 0.027831 | -0.010564 | 0.075351 | 0.1648 | -0.092979 | -0.17331 | 122.5398 | 0.033828 | 122.5764 | 122.5441 | 0.004276 | -0.013354 | 0.19235 | 122.3517 | -0.007046 | 122.581 | 122.5145 | 0.16274 | 0.082403 | -0.17538 | 122.6412 | 122.5941 | 122.7998 | 122.5447 | -0.067613 | 122.6004 | 122.6898 | 122.432 | 122.5529 | -0.2557
2353.3281 | 122.8592 | -122.5479 | 0.054932 | 1.4211e-13 | -0.028113 | 0.014252 | -0.0042801 | -0.013615 | 0.018629 | -0.23296 | 0.018439 | 0.018462 | 0.015385 | 0.03394 | 0.0092534 | 0.055988 | 0.010564 | 0.01906 | 0.11622 | 0.069043 | 0.27932 | 0.023942 | 0.055992 | 0.036989 | -0.010564 | 0.084508 | 0.16022 | -0.097557 | -0.17331 | 122.5719 | 0.061293 | 122.6039 | 122.567 | -0.004882 | 0.014111 | 0.22439 | 122.3746 | 0.029576 | 122.6039 | 122.5373 | 0.16274 | 0.10529 | -0.15249 | 122.6641 | 122.617 | 122.8272 | 122.5585 | -0.03099 | 122.6324 | 122.7081 | 122.4504 | 122.5849 | -0.22824
2355.0625 | 122.7448 | -122.5616 | 0.11902 | 1.4211e-13 | -0.02854 | 0.014252 | -0.0038527 | -0.013401 | 0.018629 | -0.24822 | 0.018439 | 0.018462 | 0.015385 | 0.034581 | 0.0090396 | 0.05141 | 0.015142 | 0.023639 | 0.11165 | 0.059885 | 0.27475 | 0.014784 | 0.055992 | 0.036989 | -0.010564 | 0.084508 | 0.16022 | -0.033457 | -0.16873 | 122.5764 | -0.007372 | 122.6131 | 122.5853 | 0.008855 | -0.059134 | 0.15573 | 122.3929 | -0.034511 | 122.6176 | 122.5511 | 0.15816 | 0.041203 | -0.15248 | 122.6733 | 122.6215 | 122.8364 | 122.5768 | -0.10423 | 122.6462 | 122.7219 | 122.5282 | 122.5986 | -0.28775
2356.8125 | 122.8271 | -122.5479 | 0.073242 | 1.4211e-13 | -0.028327 | 0.013825 | -0.0040665 | -0.013401 | 0.018629 | -0.22533 | 0.018225 | 0.018462 | 0.015598 | 0.034795 | 0.0092534 | 0.055988 | 0.015142 | 0.023639 | 0.11165 | 0.059885 | 0.28848 | 0.028521 | 0.055992 | 0.03241 | -0.015143 | 0.084508 | 0.16022 | -0.070086 | -0.17331 | 122.5764 | 0.038405 | 122.6039 | 122.5716 | -0.004882 | -0.013357 | 0.21524 | 122.3746 | 0.011266 | 122.6039 | 122.5328 | 0.15816 | 0.08698 | -0.14333 | 122.6596 | 122.6078 | 122.8364 | 122.5631 | -0.044721 | 122.6324 | 122.7081 | 122.4778 | 122.5803 | -0.24655
2358.5 | 122.8043 | -122.5433 | 0.09613 | 1.4211e-13 | -0.028327 | 0.014039 | -0.0038527 | -0.013401 | 0.018843 | -0.23296 | 0.018012 | 0.018249 | 0.015385 | 0.034581 | 0.009467 | 0.05141 | 0.015142 | 0.014482 | 0.11165 | 0.064464 | 0.2839 | 0.019363 | 0.055992 | 0.027831 | -0.010564 | 0.084508 | 0.1648 | -0.083821 | -0.17331 | 122.5627 | 0.015517 | 122.5947 | 122.5578 | -0.004881 | -0.031666 | 0.18777 | 122.37 | -0.011622 | 122.5993 | 122.5328 | 0.16274 | 0.06867 | -0.17995 | 122.655 | 122.6078 | 122.8272 | 122.5585 | -0.076767 | 122.6278 | 122.7081 | 122.4595 | 122.5712 | -0.26944
2360.25 | 122.7402 | -122.5571 | 0.11444 | 1.4211e-13 | -0.02854 | 0.013825 | -0.0038527 | -0.013401 | 0.018629 | -0.22533 | 0.018012 | 0.018676 | 0.015385 | 0.034581 | 0.0090396 | 0.055988 | 0.005985 | 0.023639 | 0.11165 | 0.064464 | 0.28848 | 0.023942 | 0.060571 | 0.03241 | -0.015143 | 0.07993 | 0.16938 | -0.10671 | -0.15957 | 122.581 | -0.002794 | 122.6131 | 122.5807 | -0.000303 | -0.049977 | 0.17404 | 122.3975 | -0.034511 | 122.6176 | 122.5419 | 0.14443 | 0.054938 | -0.22115 | 122.6687 | 122.6215 | 122.8455 | 122.5631 | -0.090499 | 122.637 | 122.7264 | 122.4504 | 122.5895 | -0.27401
2362 | 122.7814 | -122.5525 | 0.10529 | 1.4211e-13 | -0.028754 | 0.013825 | -0.0040665 | -0.013401 | 0.018843 | -0.23296 | 0.018012 | 0.018035 | 0.015385 | 0.034581 | 0.0090396 | 0.060567 | 0.019721 | 0.01906 | 0.11165 | 0.073622 | 0.27932 | 0.028521 | 0.055992 | 0.03241 | -0.010564 | 0.07993 | 0.1648 | -0.070086 | -0.16873 | 122.581 | 0.006361 | 122.6131 | 122.5716 | -0.009461 | -0.031664 | 0.17404 | 122.3838 | -0.025356 | 122.6085 | 122.5419 | 0.15816 | 0.059514 | -0.17537 | 122.6641 | 122.6261 | 122.8318 | 122.5722 | -0.076765 | 122.6324 | 122.7173 | 122.4824 | 122.5849 | -0.27401
2363.75 | 122.7356 | -122.5891 | 0.11444 | 1.4211e-13 | -0.028113 | 0.014039 | -0.0038527 | -0.013187 | 0.018629 | -0.24059 | 0.018439 | 0.018462 | 0.015598 | 0.034581 | 0.0090396 | 0.046831 | 0.005985 | 0.023639 | 0.1208 | 0.059885 | 0.27932 | 0.023942 | 0.046835 | 0.03241 | -0.015143 | 0.07993 | 0.1648 | -0.065507 | -0.16873 | 122.6131 | 0.006363 | 122.6359 | 122.6128 | -0.000303 | -0.054556 | 0.16488 | 122.4204 | -0.034511 | 122.6359 | 122.574 | 0.15358 | 0.050359 | -0.17995 | 122.7099 | 122.649 | 122.8684 | 122.5951 | -0.090499 | 122.669 | 122.7539 | 122.5236 | 122.6215 | -0.28317
2365.4219 | 122.8134 | -122.5342 | 0.086975 | 1.4211e-13 | -0.028754 | 0.014252 | -0.0040665 | -0.013615 | 0.019057 | -0.23296 | 0.018439 | 0.018462 | 0.015385 | 0.034581 | 0.0090396 | 0.046831 | 0.010564 | 0.023639 | 0.11622 | 0.069043 | 0.27475 | 0.014784 | 0.051413 | 0.027831 | -0.015143 | 0.07993 | 0.1648 | -0.097557 | -0.16415 | 122.549 | 0.02925 | 122.581 | 122.5578 | 0.008855 | -0.017932 | 0.18777 | 122.37 | -0.007045 | 122.5856 | 122.519 | 0.14901 | 0.077825 | -0.18453 | 122.6504 | 122.6032 | 122.8089 | 122.5447 | -0.072191 | 122.6141 | 122.699 | 122.4366 | 122.562 | -0.25112
2367.1719 | 122.7402 | -122.5845 | 0.1236 | 1.4211e-13 | -0.028327 | 0.014039 | -0.0038527 | -0.013401 | 0.018629 | -0.23296 | 0.018225 | 0.018676 | 0.015385 | 0.034795 | 0.0090396 | 0.055988 | 0.015142 | 0.023639 | 0.11622 | 0.064464 | 0.2839 | 0.019363 | 0.060571 | 0.046146 | -0.005985 | 0.084508 | 0.15564 | -0.0884 | -0.16873 | 122.6039 | -0.007371 | 122.6405 | 122.6082 | 0.004276 | -0.059132 | 0.16031 | 122.4158 | -0.039088 | 122.6451 | 122.5785 | 0.16274 | 0.032047 | -0.212 | 122.7008 | 122.649 | 122.8684 | 122.5997 | -0.10423 | 122.669 | 122.7402 | 122.4961 | 122.6307 | -0.29232
2368.8594 | 122.8638 | -122.5616 | 0.09613 | 1.4211e-13 | -0.028327 | 0.014466 | -0.0036391 | -0.013615 | 0.018416 | -0.23296 | 0.018225 | 0.018462 | 0.015385 | 0.034153 | 0.0090396 | 0.05141 | 0.015142 | 0.023639 | 0.10707 | 0.073622 | 0.2839 | 0.019363 | 0.055992 | 0.03241 | -0.010564 | 0.07993 | 0.16022 | -0.0884 | -0.16415 | 122.581 | 0.010938 | 122.6131 | 122.5853 | 0.004276 | -0.022508 | 0.18777 | 122.3975 | -0.0162 | 122.6176 | 122.5511 | 0.15358 | 0.064092 | -0.18453 | 122.6687 | 122.6353 | 122.8455 | 122.5768 | -0.076767 | 122.6416 | 122.7219 | 122.4732 | 122.5941 | -0.26028
2370.6094 | 122.731 | -122.5571 | 0.10529 | 1.4211e-13 | -0.02854 | 0.01468 | -0.0038527 | -0.013615 | 0.019057 | -0.24059 | 0.018012 | 0.018249 | 0.015598 | 0.034581 | 0.0090396 | 0.055988 | 0.005985 | 0.028217 | 0.11622 | 0.064464 | 0.28848 | 0.019363 | 0.055992 | 0.036989 | -0.010564 | 0.089087 | 0.17396 | -0.11587 | -0.16873 | 122.5764 | 0.010939 | 122.6131 | 122.5853 | 0.008854 | -0.040822 | 0.18319 | 122.3883 | -0.016199 | 122.6131 | 122.5465 | 0.15816 | 0.068672 | -0.22116 | 122.6733 | 122.6215 | 122.8455 | 122.5631 | -0.085923 | 122.6462 | 122.731 | 122.4412 | 122.5941 | -0.27401
2372.2969 | 122.7768 | -122.5708 | 0.11444 | 1.4211e-13 | -0.02854 | 0.014039 | -0.0040665 | -0.013615 | 0.018629 | -0.22533 | 0.018012 | 0.018676 | 0.015598 | 0.034581 | 0.008826 | 0.055988 | 0.010564 | 0.028217 | 0.11622 | 0.069043 | 0.28848 | 0.014784 | 0.051413 | 0.041567 | -0.015143 | 0.07993 | 0.16938 | -0.10671 | -0.16415 | 122.5856 | 0.001784 | 122.6268 | 122.599 | 0.013433 | -0.045398 | 0.17404 | 122.4067 | -0.034511 | 122.6222 | 122.5557 | 0.14901 | 0.054938 | -0.22115 | 122.687 | 122.6398 | 122.8593 | 122.5814 | -0.099657 | 122.6507 | 122.7402 | 122.4641 | 122.6124 | -0.27859
2373.9688 | 122.7448 | -122.5845 | 0.1236 | 1.4211e-13 | -0.027899 | 0.014039 | -0.0038527 | -0.013615 | 0.01927 | -0.23296 | 0.018225 | 0.018462 | 0.015171 | 0.034581 | 0.009467 | 0.05141 | 0.015142 | 0.028217 | 0.1208 | 0.064464 | 0.2839 | 0.019363 | 0.055992 | 0.023253 | -0.015143 | 0.084508 | 0.16022 | -0.097557 | -0.16873 | 122.6039 | -0.002792 | 122.6359 | 122.6128 | 0.008854 | -0.059132 | 0.16031 | 122.4158 | -0.039088 | 122.6405 | 122.5694 | 0.15358 | 0.036626 | -0.22115 | 122.7053 | 122.649 | 122.8684 | 122.5997 | -0.10423 | 122.669 | 122.7448 | 122.487 | 122.6078 | -0.29232
2375.6562 | 122.8683 | -122.5342 | 0.082397 | 1.4211e-13 | -0.028327 | 0.014466 | -0.0040665 | -0.013401 | 0.018629 | -0.23296 | 0.018439 | 0.018249 | 0.015598 | 0.034795 | 0.0092534 | 0.055988 | 0.005985 | 0.028217 | 0.11165 | 0.073622 | 0.27932 | 0.028521 | 0.055992 | 0.03241 | -0.015143 | 0.075351 | 0.1648 | -0.051771 | -0.17331 | 122.5627 | 0.02925 | 122.5902 | 122.5624 | -0.000304 | -0.008775 | 0.19693 | 122.3609 | -0.007046 | 122.5902 | 122.519 | 0.15816 | 0.082403 | -0.13417 | 122.6458 | 122.6078 | 122.8135 | 122.5402 | -0.053876 | 122.6095 | 122.699 | 122.4824 | 122.5666 | -0.2557
2377.3906 | 122.8546 | -122.5433 | 0.091553 | 1.4211e-13 | -0.028327 | 0.014039 | -0.0036391 | -0.013615 | 0.019057 | -0.22533 | 0.018012 | 0.018249 | 0.015385 | 0.034581 | 0.009467 | 0.060567 | 0.015142 | 0.028217 | 0.10707 | 0.069043 | 0.27475 | 0.014784 | 0.060571 | 0.036989 | -0.010564 | 0.084508 | 0.1648 | -0.10214 | -0.16873 | 122.5581 | 0.015515 | 122.6039 | 122.5716 | 0.013433 | -0.02251 | 0.18319 | 122.3746 | -0.007045 | 122.6039 | 122.5328 | 0.15816 | 0.073247 | -0.19369 | 122.6504 | 122.6124 | 122.8181 | 122.5585 | -0.076769 | 122.6278 | 122.7081 | 122.4412 | 122.5803 | -0.26028
2379.0781 | 122.7219 | -122.5845 | 0.1236 | 1.4211e-13 | -0.028113 | 0.014039 | -0.0038527 | -0.013615 | 0.019057 | -0.23296 | 0.018225 | 0.018462 | 0.015385 | 0.034581 | 0.0090396 | 0.060567 | 0.010564 | 0.028217 | 0.11165 | 0.069043 | 0.28848 | 0.023942 | 0.060571 | 0.036989 | -0.015143 | 0.089087 | 0.16938 | -0.070086 | -0.16873 | 122.6085 | -0.011949 | 122.6451 | 122.6128 | 0.004275 | -0.054553 | 0.16489 | 122.4158 | -0.034509 | 122.6451 | 122.5694 | 0.15358 | 0.045783 | -0.19368 | 122.6962 | 122.6536 | 122.873 | 122.5951 | -0.099654 | 122.6736 | 122.7539 | 122.5144 | 122.6215 | -0.29232
2380.8281 | 122.8271 | -122.5616 | 0.07782 | 1.4211e-13 | -0.028113 | 0.014252 | -0.0038527 | -0.013187 | 0.018629 | -0.23296 | 0.018225 | 0.018462 | 0.015812 | 0.034581 | 0.0092534 | 0.055988 | 0.015142 | 0.023639 | 0.11165 | 0.069043 | 0.28848 | 0.019363 | 0.060571 | 0.036989 | -0.015143 | 0.07993 | 0.1648 | -0.070086 | -0.16873 | 122.581 | 0.033827 | 122.6176 | 122.5853 | 0.004276 | -0.008777 | 0.21066 | 122.3929 | 0.00211 | 122.6222 | 122.5465 | 0.15358 | 0.08698 | -0.14791 | 122.6733 | 122.6307 | 122.8501 | 122.5768 | -0.058457 | 122.6416 | 122.7264 | 122.4916 | 122.5986 | -0.24655
2382.5781 | 122.7493 | -122.58 | 0.13275 | 1.4211e-13 | -0.027899 | 0.014252 | -0.0038527 | -0.013828 | 0.018629 | -0.23296 | 0.018225 | 0.018462 | 0.015598 | 0.034581 | 0.0092534 | 0.055988 | 0.010564 | 0.032795 | 0.11165 | 0.073622 | 0.27475 | 0.019363 | 0.060571 | 0.027831 | -0.010564 | 0.084508 | 0.16938 | -0.083821 | -0.16873 | 122.5993 | -0.021104 | 122.6359 | 122.6128 | 0.013432 | -0.059129 | 0.14199 | 122.4112 | -0.048243 | 122.6405 | 122.5694 | 0.15816 | 0.036628 | -0.21657 | 122.6916 | 122.6536 | 122.8547 | 122.5905 | -0.11339 | 122.6645 | 122.7493 | 122.4961 | 122.6078 | -0.30148
2384.3281 | 122.8683 | -122.5433 | 0.086975 | 1.4211e-13 | -0.028327 | 0.014039 | -0.0040665 | -0.013187 | 0.018843 | -0.22533 | 0.018012 | 0.018462 | 0.015385 | 0.034367 | 0.0092534 | 0.05141 | 0.010564 | 0.023639 | 0.11622 | 0.069043 | 0.2839 | 0.023942 | 0.055992 | 0.03241 | -0.010564 | 0.084508 | 0.16022 | -0.047193 | -0.16873 | 122.5673 | 0.02925 | 122.5947 | 122.567 | -0.000303 | -0.017932 | 0.19693 | 122.3746 | -0.002467 | 122.5993 | 122.5328 | 0.15816 | 0.073247 | -0.13417 | 122.6596 | 122.6124 | 122.8272 | 122.5539 | -0.063033 | 122.6278 | 122.7036 | 122.4961 | 122.5757 | -0.2557
2386.0781 | 122.8134 | -122.5845 | 0.09613 | 1.4211e-13 | -0.028113 | 0.014466 | -0.0036391 | -0.013401 | 0.018629 | -0.22533 | 0.018012 | 0.018462 | 0.015385 | 0.034795 | 0.0092534 | 0.060567 | 0.005985 | 0.023639 | 0.11165 | 0.059885 | 0.2839 | 0.019363 | 0.051413 | 0.041567 | -0.010564 | 0.075351 | 0.16022 | -0.092979 | -0.16415 | 122.6039 | 0.015517 | 122.6451 | 122.6082 | 0.004276 | -0.036245 | 0.18777 | 122.4204 | -0.020779 | 122.6359 | 122.574 | 0.15358 | 0.064092 | -0.18911 | 122.6962 | 122.6444 | 122.8684 | 122.5905 | -0.076767 | 122.6599 | 122.7448 | 122.4916 | 122.6261 | -0.26028
2387.8125 | 122.7402 | -122.6074 | 0.11902 | 1.4211e-13 | -0.028327 | 0.014252 | -0.0036391 | -0.013187 | 0.018629 | -0.24059 | 0.018439 | 0.018676 | 0.015385 | 0.034367 | 0.0090396 | 0.055988 | 0.010564 | 0.028217 | 0.11165 | 0.064464 | 0.2839 | 0.019363 | 0.055992 | 0.036989 | -0.019721 | 0.07993 | 0.1648 | -0.047193 | -0.16873 | 122.6268 | -0.007372 | 122.6634 | 122.6356 | 0.008854 | -0.054555 | 0.16488 | 122.4387 | -0.039089 | 122.6634 | 122.5877 | 0.14901 | 0.045781 | -0.16621 | 122.7191 | 122.6719 | 122.8913 | 122.618 | -0.099656 | 122.6874 | 122.7722 | 122.5602 | 122.6444 | -0.28775
2389.4844 | 122.7448 | -122.5937 | 0.091553 | 1.4211e-13 | -0.028113 | 0.014252 | -0.0040665 | -0.012974 | 0.018416 | -0.22533 | 0.018012 | 0.018676 | 0.016026 | 0.034581 | 0.0090396 | 0.05141 | 0.010564 | 0.023639 | 0.11622 | 0.064464 | 0.27932 | 0.014784 | 0.051413 | 0.027831 | -0.015143 | 0.070773 | 0.16022 | -0.097557 | -0.16873 | 122.6085 | 0.024672 | 122.6451 | 122.6173 | 0.008855 | -0.027089 | 0.18777 | 122.425 | -0.02078 | 122.6451 | 122.5785 | 0.15358 | 0.068669 | -0.18911 | 122.7099 | 122.6582 | 122.873 | 122.6043 | -0.076769 | 122.6645 | 122.7539 | 122.4961 | 122.6215 | -0.26028
2391.2344 | 122.8683 | -122.5388 | 0.086975 | 1.4211e-13 | -0.028113 | 0.014039 | -0.0036391 | -0.013401 | 0.019057 | -0.23296 | 0.018225 | 0.018462 | 0.015812 | 0.034367 | 0.0086124 | 0.046831 | 0.010564 | 0.01906 | 0.11165 | 0.059885 | 0.27932 | 0.019363 | 0.051413 | 0.036989 | -0.019721 | 0.084508 | 0.16022 | -0.10214 | -0.17331 | 122.5581 | 0.024672 | 122.5856 | 122.5578 | -0.000303 | -0.02709 | 0.19235 | 122.3655 | -0.002467 | 122.5902 | 122.519 | 0.15358 | 0.073247 | -0.18911 | 122.6504 | 122.5986 | 122.8181 | 122.5493 | -0.067612 | 122.6233 | 122.699 | 122.4366 | 122.5757 | -0.26028
2392.9219 | 122.7356 | -122.5845 | 0.11444 | 1.4211e-13 | -0.02854 | 0.014039 | -0.0042801 | -0.013401 | 0.018629 | -0.23296 | 0.018439 | 0.017821 | 0.015598 | 0.034367 | 0.0092534 | 0.05141 | 0.010564 | 0.028217 | 0.10707 | 0.069043 | 0.27932 | 0.023942 | 0.051413 | 0.03241 | -0.015143 | 0.075351 | 0.1648 | -0.092979 | -0.16873 | 122.6085 | -0.007373 | 122.6359 | 122.6128 | 0.004275 | -0.045398 | 0.16488 | 122.4158 | -0.03909 | 122.6359 | 122.5694 | 0.15358 | 0.050359 | -0.20742 | 122.6916 | 122.6536 | 122.8639 | 122.5951 | -0.090499 | 122.6599 | 122.7493 | 122.4916 | 122.6169 | -0.28317
2394.6719 | 122.8821 | -122.5525 | 0.086975 | 1.4211e-13 | -0.028113 | 0.013825 | -0.0038527 | -0.013187 | 0.018629 | -0.22533 | 0.017798 | 0.018462 | 0.015171 | 0.034367 | 0.0090396 | 0.060567 | 0.015142 | 0.023639 | 0.11622 | 0.064464 | 0.27932 | 0.019363 | 0.051413 | 0.036989 | -0.005985 | 0.066194 | 0.16938 | -0.0884 | -0.16415 | 122.5719 | 0.02925 | 122.6131 | 122.5761 | 0.004276 | -0.022511 | 0.19235 | 122.3883 | -0.020781 | 122.6039 | 122.5465 | 0.15816 | 0.082404 | -0.17538 | 122.6687 | 122.617 | 122.8318 | 122.5676 | -0.067612 | 122.6187 | 122.7219 | 122.4641 | 122.5895 | -0.25112
2396.4375 | 122.8729 | -122.5571 | 0.07782 | 1.4211e-13 | -0.028113 | 0.014252 | -0.0038527 | -0.013187 | 0.019057 | -0.23296 | 0.018225 | 0.018462 | 0.015598 | 0.034367 | 0.0092534 | 0.046831 | 0.001407 | 0.01906 | 0.11165 | 0.059885 | 0.27932 | 0.023942 | 0.051413 | 0.03241 | -0.015143 | 0.075351 | 0.16938 | -0.12045 | -0.15957 | 122.581 | 0.033827 | 122.6039 | 122.5761 | -0.004882 | -0.017935 | 0.2015 | 122.3975 | -0.002469 | 122.6085 | 122.5419 | 0.14443 | 0.091559 | -0.19827 | 122.6687 | 122.617 | 122.8364 | 122.5585 | -0.053878 | 122.6324 | 122.7264 | 122.4366 | 122.5895 | -0.23739
2398.1094 | 122.8729 | -122.5479 | 0.11444 | 1.4211e-13 | -0.028327 | 0.014039 | -0.0038527 | -0.013615 | 0.018416 | -0.24822 | 0.018439 | 0.018462 | 0.015598 | 0.034581 | 0.0092534 | 0.05141 | 0.010564 | 0.023639 | 0.11622 | 0.069043 | 0.2839 | 0.014784 | 0.055992 | 0.027831 | -0.010564 | 0.066194 | 0.16938 | -0.11587 | -0.16873 | 122.5627 | 0.001784 | 122.5993 | 122.5716 | 0.008855 | -0.045398 | 0.16946 | 122.3792 | -0.048247 | 122.6039 | 122.5373 | 0.15816 | 0.054938 | -0.23031 | 122.6641 | 122.617 | 122.8318 | 122.5585 | -0.099657 | 122.6141 | 122.7173 | 122.432 | 122.5757 | -0.28317
2399.8594 | 122.8958 | -122.5479 | 0.073242 | 1.4211e-13 | -0.02854 | 0.014466 | -0.0040665 | -0.013401 | 0.018629 | -0.23296 | 0.017798 | 0.018676 | 0.015812 | 0.034795 | 0.0092534 | 0.05141 | 0.005985 | 0.01906 | 0.11165 | 0.069043 | 0.27932 | 0.019363 | 0.051413 | 0.036989 | -0.010564 | 0.070773 | 0.16938 | -0.10671 | -0.17331 | 122.5673 | 0.038405 | 122.5993 | 122.567 | -0.000303 | -0.004199 | 0.20608 | 122.3746 | -0.002469 | 122.5993 | 122.5373 | 0.16274 | 0.096137 | -0.17996 | 122.6596 | 122.617 | 122.8272 | 122.5539 | -0.053879 | 122.6187 | 122.7173 | 122.4412 | 122.5849 | -0.24655
2401.5625 | 122.8317 | -122.5754 | 0.07782 | 1.4211e-13 | -0.028327 | 0.014039 | -0.0040665 | -0.012974 | 0.018629 | -0.24059 | 0.017798 | 0.018676 | 0.015385 | 0.034581 | 0.0090396 | 0.05141 | 0.010564 | 0.023639 | 0.11165 | 0.064464 | 0.27932 | 0.014784 | 0.060571 | 0.027831 | -0.019721 | 0.07993 | 0.16938 | -0.11129 | -0.16873 | 122.5902 | 0.033827 | 122.6268 | 122.599 | 0.008855 | -0.013356 | 0.2015 | 122.4066 | 0.00211 | 122.6359 | 122.5557 | 0.14901 | 0.091559 | -0.18911 | 122.687 | 122.6398 | 122.8547 | 122.5859 | -0.063036 | 122.6553 | 122.7448 | 122.4641 | 122.6032 | -0.24655

## Thermal Data
Fire Time | B Position - Tray - Middle | D Position - 3' | D Position - Middle | D Position - 7'
-0.6521 | 8.3904 | 8.7226 | 8.9391 | 9.1304
0.3479 | 8.4021 | 8.7223 | 8.9368 | 9.1227
1.3479 | 8.3969 | 8.7281 | 8.9402 | 9.1225
2.3479 | 8.396 | 8.7265 | 8.9472 | 9.1288
3.3479 | 8.3933 | 8.7247 | 8.9364 | 9.1283
4.3479 | 8.3849 | 8.7228 | 8.9467 | 9.1309
5.3479 | 8.377 | 8.7287 | 8.9466 | 9.1313
6.3479 | 8.3778 | 8.7159 | 8.9431 | 9.1419
7.3479 | 8.3751 | 8.7214 | 8.9591 | 9.1373
8.3479 | 8.3643 | 8.7182 | 8.9509 | 9.1418
9.3479 | 8.3657 | 8.735 | 9.0033 | 9.138
10.3479 | 8.3853 | 8.8056 | 9.3678 | 9.1769
11.3479 | 8.4461 | 8.8167 | 10.1256 | 9.1933
12.3479 | 8.9291 | 8.8896 | 10.7955 | 9.4277
13.3479 | 9.6074 | 9.6256 | 12.2755 | 10.0204
14.3479 | 10.8227 | 11.1179 | 14.9358 | 11.1338
15.3479 | 12.3648 | 12.9705 | 17.6633 | 11.6566
16.3479 | 14.326 | 15.9452 | 21.4652 | 12.4693
17.3479 | 16.3186 | 18.7013 | 25.8345 | 13.6754
18.3479 | 18.6458 | 21.3915 | 31.1198 | 15.2184
19.3479 | 21.1644 | 24.7169 | 35.6621 | 16.4091
20.3479 | 23.6847 | 28.602 | 40.2139 | 17.8927
21.3479 | 26.3148 | 31.4608 | 45.3636 | 19.4871
22.3479 | 29.8526 | 35.3153 | 49.8693 | 22.5897
23.3479 | 33.7732 | 37.9095 | 56.8248 | 24.9875
24.3479 | 36.9402 | 41.1215 | 61.1181 | 26.654
25.3479 | 39.4387 | 44.0889 | 66.0871 | 29.465
26.3479 | 42.3454 | 46.4959 | 71.7811 | 32.0977
27.3479 | 44.9516 | 49.1573 | 76.2848 | 33.87
28.3635 | 48.1349 | 52.1088 | 82.1126 | 37.683
29.3479 | 50.4804 | 54.9021 | 85.1065 | 40.2315
30.3479 | 52.5706 | 57.981 | 88.7704 | 42.9183
31.3479 | 55.6334 | 61.249 | 93.6723 | 46.0203
32.3479 | 58.4649 | 63.3538 | 98.0333 | 50.5142
33.3479 | 61.4369 | 67.0195 | 101.7869 | 53.9619
34.3479 | 64.1266 | 69.0416 | 107.0979 | 56.6008
35.3479 | 66.4786 | 73.0635 | 111.9718 | 58.8709
36.3479 | 68.8715 | 76.4136 | 114.3823 | 61.9838
37.3479 | 70.7295 | 80.1321 | 116.4689 | 65.016
38.3479 | 72.4062 | 81.6728 | 119.7646 | 67.8479
39.3479 | 74.8624 | 83.1728 | 122.2224 | 70.5556
40.3479 | 77.0016 | 84.9189 | 124.8157 | 72.3135
41.3479 | 79.2881 | 87.1484 | 127.2985 | 74.4399
42.3479 | 82.4389 | 89.1051 | 129.3108 | 77.238
43.3479 | 84.6468 | 92.7118 | 130.6121 | 80.5044
44.3479 | 85.9249 | 94.6574 | 132.1059 | 82.9248
45.3479 | 87.8505 | 96.2465 | 132.8888 | 85.3105
46.3479 | 88.599 | 98.0403 | 134.1165 | 88.8757
47.3479 | 89.5101 | 98.6193 | 136.5777 | 90.9358
48.3479 | 91.0657 | 99.8119 | 137.6981 | 93.1927
49.3479 | 92.7904 | 100.6305 | 139.7043 | 96.2432
50.3479 | 95.1632 | 101.8538 | 142.2219 | 98.6324
51.3479 | 97.7746 | 103.4459 | 143.2724 | 100.2478
52.3479 | 98.2368 | 103.9747 | 144.5491 | 102.7187
53.3479 | 98.1179 | 104.9835 | 146.3396 | 105.1657
54.3479 | 97.8816 | 105.6452 | 147.5398 | 106.5805
55.3635 | 98.4408 | 105.9526 | 148.5046 | 108.0742
56.3479 | 99.3506 | 107.6457 | 149.6477 | 109.4381
57.3479 | 100.5354 | 109.3352 | 151.7362 | 110.5242
58.3479 | 101.3682 | 111.1894 | 153.8676 | 112.3351
59.3479 | 102.2335 | 113.7384 | 154.6317 | 114.4619
60.3479 | 103.5718 | 116.6468 | 155.6816 | 115.7475
61.3479 | 104.4736 | 119.8053 | 156.9683 | 117.1797
62.3479 | 104.9255 | 121.425 | 158.4194 | 119.4354
63.3479 | 105.9802 | 123.6866 | 159.8112 | 120.7854
64.3479 | 107.0373 | 126.3207 | 160.8386 | 122.7156
65.3479 | 107.5496 | 128.9539 | 162.2039 | 123.9187
66.3479 | 107.7194 | 130.0008 | 163.4423 | 125.4131
67.3479 | 108.0523 | 131.0526 | 164.456 | 126.355
68.3479 | 108.8248 | 131.83 | 164.469 | 127.2466
69.3479 | 108.6351 | 133.4563 | 164.8365 | 128.1043
70.3479 | 108.6658 | 134.4525 | 166.0062 | 129.1022
71.3479 | 109.7081 | 134.616 | 167.494 | 130.1829
72.3479 | 110.3827 | 134.559 | 167.8232 | 131.5561
73.3479 | 110.8645 | 134.3585 | 166.8863 | 131.8026
74.3479 | 111.3022 | 134.3843 | 167.2491 | 132.3367
75.3479 | 111.8404 | 134.663 | 167.967 | 132.4935
76.3479 | 112.1188 | 135.1286 | 167.9419 | 132.9796
77.3479 | 112.4657 | 135.2904 | 167.1524 | 133.7348
78.3479 | 113.1567 | 136.2712 | 167.389 | 134.7921
79.3479 | 113.4907 | 136.4738 | 168.1451 | 135.7726
80.3479 | 114.7779 | 136.8341 | 168.4328 | 136.7967
81.3479 | 115.3008 | 136.7278 | 168.7336 | 137.7923
82.3479 | 115.4408 | 136.8249 | 168.5174 | 138.1884
83.3479 | 115.7439 | 136.5669 | 168.6751 | 138.9324
84.3479 | 115.7304 | 137.1731 | 169.6073 | 140.1688
85.3479 | 116.213 | 137.5295 | 168.7527 | 140.493
86.3479 | 116.8047 | 137.445 | 167.8261 | 141.2247
87.3479 | 116.6779 | 137.5194 | 166.8316 | 141.9395
88.3479 | 116.993 | 137.8127 | 165.723 | 141.8682
89.3479 | 117.8312 | 138.0481 | 165.3183 | 142.8423
90.3479 | 118.5693 | 139.1142 | 166.0071 | 143.2404
91.3479 | 119.3214 | 139.6624 | 166.1055 | 143.6051
92.3479 | 120.2318 | 140.0061 | 166.4634 | 145.5674
93.3479 | 121.0007 | 139.7809 | 167.6406 | 145.9994
94.3479 | 121.8555 | 139.7144 | 167.0327 | 147.6564
95.3479 | 122.9333 | 139.6099 | 166.2426 | 148.4702
96.3479 | 124.7083 | 139.3024 | 165.716 | 148.9304
97.3479 | 124.7308 | 139.4059 | 165.6803 | 149.8226
98.3479 | 125.2608 | 139.5043 | 166.2373 | 150.6795
99.3479 | 125.7435 | 139.3313 | 166.4777 | 152.051
100.3479 | 126.7639 | 139.0033 | 166.196 | 153.0321
101.3479 | 126.7956 | 138.8393 | 166.0558 | 153.8671
102.3479 | 127.1621 | 138.6934 | 166.859 | 155.2063
103.3479 | 126.9261 | 138.9057 | 167.7154 | 156.3842
104.3479 | 126.8985 | 139.1839 | 167.5743 | 157.1762
105.3479 | 127.3453 | 139.0078 | 168.5746 | 157.7732
106.3479 | 129.062 | 140.0965 | 169.3239 | 158.7353
107.3479 | 130.0972 | 140.3515 | 170.3351 | 160.3964
108.3479 | 130.3784 | 140.8524 | 171.3593 | 160.9092
109.3479 | 130.98 | 141.2878 | 172.4878 | 161.1332
110.3479 | 131.952 | 141.5629 | 174.1133 | 161.5756
111.3479 | 132.5672 | 141.4854 | 175.1104 | 161.5117
112.3479 | 133.787 | 141.9609 | 175.8999 | 162.2069
113.3479 | 134.6032 | 141.5767 | 176.1124 | 162.4563
114.3479 | 135.3948 | 141.9451 | 177.1473 | 162.7495
115.3479 | 136.7007 | 143.798 | 179.8261 | 163.6402
116.3479 | 138.0252 | 144.5353 | 181.7759 | 164.0637
117.3479 | 139.821 | 146.4075 | 182.8628 | 165.1952
118.3479 | 140.816 | 146.2616 | 183.8242 | 165.3308
119.3479 | 142.4394 | 146.6573 | 184.0302 | 165.8568
120.3479 | 144.049 | 148.163 | 184.9292 | 166.5644
121.3479 | 146.1309 | 149.0475 | 186.2124 | 167.278
122.3479 | 146.9483 | 149.878 | 186.7774 | 167.7688
123.3479 | 148.5615 | 150.2125 | 187.0667 | 168.8107
124.3479 | 149.6361 | 150.5083 | 187.5204 | 169.0978
125.3479 | 150.4394 | 150.5193 | 187.16 | 169.8762
126.3479 | 150.4858 | 151.1727 | 188.4868 | 170.2154
127.3479 | 152.6285 | 150.8693 | 187.7761 | 171.1633
128.3479 | 153.037 | 151.1251 | 188.5501 | 170.5116
129.3479 | 153.6362 | 151.4198 | 187.1017 | 172.343
130.3479 | 153.4294 | 151.5345 | 186.8438 | 174.0333
131.3479 | 152.695 | 151.7222 | 187.2208 | 175.7962
132.3479 | 153.7779 | 151.6481 | 187.8773 | 177.0193
133.3479 | 153.7577 | 151.9734 | 188.4942 | 177.9299
134.3479 | 153.6122 | 151.9671 | 188.2603 | 178.1149
135.3479 | 153.61 | 152.5876 | 189.705 | 178.6601
136.3479 | 154.2429 | 152.6716 | 191.1539 | 179.3745
137.3479 | 154.5788 | 153.5089 | 191.9667 | 179.6908
138.3479 | 154.8838 | 153.5178 | 192.9221 | 181.7078
139.3479 | 156.302 | 153.2328 | 192.5441 | 182.1631
140.3479 | 157.1158 | 152.7173 | 193.3484 | 183.2284
141.3479 | 157.2778 | 152.5808 | 194.9709 | 184.4299
142.3479 | 157.4464 | 152.2404 | 193.9012 | 183.6215
143.3479 | 157.3545 | 151.8782 | 193.8503 | 183.5916
144.3479 | 158.5225 | 151.4596 | 193.399 | 183.2769
145.3479 | 159.3801 | 151.7598 | 194.3163 | 183.0771
146.3479 | 160.7795 | 152.0663 | 196.4921 | 182.7023
147.3479 | 161.7383 | 153.61 | 197.7916 | 182.4215
148.3479 | 162.6771 | 154.4318 | 198.978 | 182.9248
149.3479 | 163.2378 | 154.693 | 199.0486 | 182.4632
150.3479 | 165.1912 | 155.309 | 198.9485 | 182.9571
151.3479 | 166.983 | 155.7713 | 199.7988 | 182.8983
152.3479 | 167.3069 | 156.2359 | 201.4818 | 184.3492
153.3479 | 168.0293 | 157.0189 | 202.5758 | 185.0311
154.3479 | 169.1712 | 157.1672 | 202.4136 | 186.1167
155.3479 | 170.3095 | 156.9276 | 202.3295 | 186.2659
156.3479 | 171.8454 | 156.7651 | 201.8391 | 187.4606
157.3479 | 172.7131 | 156.5073 | 201.1097 | 189.2217
158.3479 | 173.4344 | 156.1803 | 200.4409 | 190.2869
159.3479 | 174.0763 | 156.8026 | 201.024 | 190.9673
160.3479 | 174.8393 | 157.4391 | 201.8369 | 192.4305
161.3479 | 175.8856 | 157.8387 | 202.2779 | 191.7081
162.3479 | 177.1162 | 157.5158 | 202.3421 | 192.6645
163.3479 | 177.7338 | 157.1784 | 202.3877 | 192.1069
164.3479 | 178.4697 | 157.4975 | 201.6871 | 193.4614
165.3479 | 179.1161 | 158.1076 | 201.5318 | 194.253
166.3479 | 179.5153 | 158.1016 | 200.8388 | 195.5481
167.3479 | 180.0256 | 158.2218 | 200.5867 | 195.1583
168.3479 | 180.9529 | 157.8369 | 200.0011 | 195.4199
169.3479 | 181.5956 | 157.677 | 200.173 | 195.2936
170.3479 | 182.1013 | 157.7509 | 199.5164 | 194.767
171.3479 | 182.3472 | 157.8244 | 199.3896 | 194.8959
172.3479 | 181.7558 | 158.2402 | 199.2665 | 194.8901
173.3479 | 181.8952 | 157.9671 | 199.9392 | 195.2387
174.3479 | 182.3779 | 157.8977 | 200.9832 | 194.7116
175.3479 | 182.1615 | 157.8065 | 200.6448 | 193.6457
176.3479 | 182.2208 | 157.4012 | 200.8381 | 192.5413
177.3479 | 183.5417 | 157.2119 | 201.1702 | 192.8206
178.3479 | 185.606 | 157.5819 | 202.3467 | 192.8496
179.3479 | 185.8259 | 157.4408 | 201.5243 | 193.0459
180.3479 | 186.2903 | 157.2109 | 201.803 | 192.9411
181.3479 | 188.1918 | 156.9567 | 202.2049 | 194.4982
182.3479 | 189.6627 | 157.2417 | 201.7919 | 194.8077
183.3479 | 189.4396 | 157.0645 | 202.222 | 194.3431
184.3479 | 189.6267 | 157.658 | 202.3878 | 193.8114
185.3479 | 190.1211 | 158.0952 | 203.9823 | 193.5983
186.3479 | 190.4714 | 158.4589 | 205.5938 | 193.6313
187.3479 | 191.584 | 159.1133 | 206.5751 | 194.2403
188.3479 | 192.1406 | 159.793 | 207.7249 | 194.3761
189.3479 | 192.1342 | 160.2997 | 207.6643 | 195.1094
190.3479 | 193.3956 | 161.204 | 207.4329 | 196.4245
191.3479 | 195.5643 | 162.008 | 207.3296 | 197.5991
192.3479 | 195.783 | 162.5836 | 208.1516 | 197.5586
193.3479 | 195.8521 | 163.5961 | 209.2692 | 197.2522
194.3479 | 196.1531 | 163.9007 | 210.5903 | 196.8699
195.3479 | 196.1505 | 165.486 | 213.8387 | 197.0144
196.3479 | 196.0919 | 166.6153 | 214.8957 | 196.8865
197.3479 | 196.8357 | 167.0404 | 213.9312 | 197.4273
198.3479 | 197.5958 | 167.9166 | 213.7337 | 198.0883
199.3479 | 197.8587 | 168.7263 | 214.1414 | 198.5532
200.3479 | 199.5127 | 169.2348 | 213.5065 | 198.8787
201.3479 | 199.6157 | 168.8678 | 212.3324 | 200.1974
202.3479 | 199.906 | 168.3566 | 213.2903 | 200.6144
203.3479 | 200.042 | 168.5906 | 212.0504 | 201.6042
204.3479 | 201.3649 | 169.0434 | 212.8292 | 202.5589
205.3479 | 200.2951 | 169.4412 | 213.7125 | 202.9676
206.3479 | 200.4394 | 169.3467 | 213.7142 | 203.4314
207.3479 | 200.4319 | 169.217 | 214.2501 | 203.5344
208.3479 | 200.4188 | 169.8121 | 214.0582 | 203.8521
209.3479 | 200.6215 | 170.6716 | 214.3099 | 204.7941
210.3479 | 201.6712 | 170.8915 | 215.0883 | 205.7181
211.3479 | 201.707 | 171.3537 | 215.3895 | 206.1766
212.3479 | 201.8096 | 171.9282 | 215.4358 | 206.3801
213.3479 | 203.0288 | 171.6605 | 215.9165 | 206.1135
214.3479 | 203.0568 | 171.7992 | 216.1702 | 205.5547
215.3479 | 203.168 | 172.8746 | 216.5805 | 205.9219
216.3479 | 202.6881 | 172.79 | 217.1683 | 206.5572
217.3479 | 202.6696 | 173.3431 | 217.3126 | 206.1234
218.3479 | 203.4837 | 173.5486 | 217.5292 | 207.4268
219.3479 | 203.5503 | 173.9384 | 217.7448 | 207.6269
220.3479 | 203.7578 | 173.5075 | 216.5876 | 209.0169
221.3479 | 205.2413 | 173.2056 | 217.0029 | 211.6851
222.3479 | 205.0533 | 173.1771 | 218.0622 | 212.2486
223.3479 | 205.8632 | 173.1161 | 217.8468 | 213.6861
224.3479 | 207.2644 | 173.1047 | 218.0953 | 213.6053
225.3479 | 208.3656 | 174.0247 | 219.1606 | 213.6734
226.3479 | 209.5396 | 174.5317 | 219.0059 | 214.203
227.3479 | 210.4417 | 175.1198 | 221.0144 | 214.081
228.3479 | 211.5906 | 175.3542 | 221.5289 | 213.7005
229.3479 | 213.0545 | 176.3786 | 222.6032 | 214.4489
230.3479 | 214.6668 | 177.1959 | 222.8491 | 215.4508
231.3479 | 215.2847 | 176.5632 | 225.3559 | 215.9041
232.3479 | 216.0035 | 176.7223 | 226.2728 | 216.9702
233.3479 | 217.8758 | 177.8801 | 227.8729 | 217.8766
234.3479 | 218.6342 | 178.355 | 229.7113 | 219.6432
235.3479 | 219.0066 | 179.1173 | 230.2028 | 220.177
236.3479 | 219.944 | 179.6454 | 230.9997 | 220.9313
237.3479 | 221.2406 | 179.9763 | 231.5552 | 221.908
238.3479 | 223.268 | 180.2733 | 232.3659 | 222.9476
239.3479 | 223.2569 | 180.3464 | 232.6439 | 224.1592
240.3479 | 224.3563 | 180.0727 | 232.922 | 225.3354
241.3479 | 224.5159 | 179.9788 | 233.0249 | 227.5
242.3479 | 225.1345 | 179.8192 | 233.3825 | 228.5113
243.3479 | 225.9037 | 180.4116 | 233.7147 | 227.7509
244.3479 | 226.3594 | 181.4143 | 234.3488 | 228.7649
245.3479 | 227.521 | 181.5636 | 234.3473 | 229.6005
246.3479 | 227.511 | 182.2246 | 235.1323 | 229.7394
247.3479 | 227.7084 | 182.1019 | 235.5228 | 230.8644
248.3479 | 228.4085 | 182.1929 | 235.9406 | 230.438
249.3479 | 229.0878 | 182.478 | 237.4305 | 232.8633
250.3479 | 229.0734 | 182.9965 | 237.4693 | 232.5117
251.3479 | 229.1686 | 183.0463 | 238.2579 | 232.4721
252.3479 | 229.1522 | 184.0332 | 238.9521 | 233.336
253.3479 | 228.8014 | 184.2128 | 238.8229 | 236.2831
254.3479 | 228.2795 | 183.6466 | 238.9683 | 236.7215
255.3479 | 227.8958 | 184.2251 | 238.3597 | 236.2334
256.3479 | 228.4505 | 184.4452 | 238.5434 | 237.6316
257.3479 | 228.0843 | 185.5941 | 238.6304 | 238.1686
258.3479 | 228.1989 | 185.6576 | 238.9278 | 238.583
259.3479 | 227.7178 | 186.4817 | 239.5676 | 239.1586
260.3479 | 228.5193 | 186.2003 | 240.8805 | 239.1029
261.3479 | 228.4907 | 186.4425 | 241.9298 | 241.3513
262.3479 | 229.7335 | 188.6556 | 244.3272 | 241.8022
263.3479 | 230.1462 | 188.8781 | 244.6204 | 241.8732
264.3479 | 230.4207 | 189.9312 | 245.0933 | 242.6932
265.3479 | 230.4039 | 190.2767 | 245.3448 | 242.9005
266.3479 | 231.2598 | 191.8988 | 246.438 | 245.5208
267.3479 | 232.5599 | 191.7219 | 246.2611 | 245.4339
268.3479 | 233.4154 | 191.8446 | 246.2735 | 245.1372
269.3479 | 233.4041 | 191.8289 | 246.8294 | 245.7139
270.3479 | 233.549 | 191.5156 | 248.2588 | 246.2554
271.3479 | 235.6409 | 195.0934 | 248.8436 | 239.7669
272.3479 | 233.2171 | 191.8783 | 247.8768 | 246.9871
273.3479 | 233.7941 | 192.9537 | 248.4937 | 247.0124
274.3479 | 233.8447 | 193.2411 | 250.1631 | 246.6604
275.3479 | 234.3364 | 193.7448 | 250.1362 | 247.4756
276.3479 | 234.0205 | 193.904 | 251.1123 | 247.9281
277.3479 | 234.1931 | 194.1254 | 251.4556 | 248.0009
278.3479 | 234.4322 | 193.6602 | 250.564 | 249.3495
279.3479 | 234.6592 | 193.3885 | 250.0825 | 248.6639
280.3479 | 235.7368 | 193.2679 | 251.8791 | 248.8151
281.3479 | 236.9497 | 193.4572 | 252.6952 | 248.5123
282.3479 | 237.166 | 195.0215 | 253.9792 | 247.9477
283.3479 | 237.7291 | 195.3265 | 254.4307 | 247.349
284.3479 | 237.9742 | 195.2522 | 253.9764 | 247.3789
285.3479 | 238.1425 | 195.2039 | 253.9151 | 247.0866
286.3479 | 238.8506 | 195.8042 | 254.9207 | 246.0614
287.3479 | 240.9435 | 196.3916 | 256.4481 | 245.6099
288.3479 | 241.8373 | 197.0881 | 257.7852 | 245.6943
289.3479 | 242.2076 | 197.5294 | 259.4495 | 245.4802
290.3479 | 242.632 | 199.3611 | 262.7592 | 246.104
291.3479 | 243.284 | 200.3141 | 264.1192 | 246.5766
292.3479 | 243.1716 | 200.2901 | 263.5014 | 247.4392
293.3479 | 243.1076 | 200.2958 | 262.8304 | 248.1738
294.3479 | 243.1492 | 199.9473 | 262.4232 | 249.3043
295.3479 | 244.0475 | 199.6608 | 262.3886 | 248.9798
296.3479 | 245.2345 | 200.4255 | 263.2605 | 249.1293
297.3479 | 245.6448 | 202.5962 | 264.1339 | 250.1522
298.3479 | 245.8387 | 203.0444 | 265.3614 | 250.6728
299.3479 | 245.7718 | 203.5302 | 265.7898 | 252.0311
300.3479 | 245.7369 | 203.3695 | 264.9433 | 253.7833
301.3479 | 245.9801 | 203.3753 | 265.4226 | 254.2368
302.3479 | 246.052 | 203.7057 | 264.2363 | 255.3294
303.3479 | 247.1432 | 203.6162 | 264.0876 | 255.0803
304.3479 | 247.7042 | 204.4587 | 265.9639 | 255.1046
305.3479 | 248.099 | 205.597 | 267.9737 | 255.4617
306.3479 | 248.6199 | 206.6869 | 268.4945 | 256.3787
307.3479 | 248.1669 | 206.937 | 269.1598 | 256.8192
308.3479 | 247.5447 | 206.7863 | 269.2264 | 257.6421
309.3479 | 247.3237 | 206.99 | 268.7643 | 258.4871
310.3479 | 247.747 | 208.2942 | 268.5789 | 259.6565
311.3479 | 248.0328 | 208.551 | 269.2956 | 260.3193
312.3479 | 247.8417 | 209.1747 | 270.142 | 262.0873
313.3479 | 248.2153 | 210.0268 | 270.4454 | 262.5127
314.3479 | 248.2514 | 210.9794 | 270.6517 | 263.2197
315.3479 | 248.5326 | 211.4042 | 270.3683 | 263.9209
316.3479 | 248.6007 | 211.4204 | 272.5238 | 265.0239
317.3479 | 249.046 | 212.5303 | 273.5319 | 265.8442
318.3479 | 249.9203 | 213.4981 | 274.5919 | 265.3723
319.3479 | 250.3767 | 213.4509 | 274.7559 | 265.5697
320.3479 | 251.0888 | 213.9068 | 276.2546 | 265.1246
321.3479 | 251.7598 | 215.1961 | 277.2086 | 264.4626
322.3479 | 252.3893 | 216.288 | 278.7781 | 264.6939
323.3479 | 253.567 | 218.017 | 281.122 | 265.0814
324.3479 | 255.6393 | 218.3343 | 283.6002 | 265.4953
325.3479 | 256.1306 | 219.0909 | 284.8217 | 267.0139
326.3479 | 257.4465 | 220.6773 | 288.0042 | 267.8117
327.3479 | 258.1237 | 221.3824 | 289.5353 | 267.81
328.3479 | 258.6555 | 223.1208 | 291.0963 | 268.1381
329.3479 | 260.4345 | 223.4596 | 291.7298 | 268.4054
330.3479 | 261.3586 | 223.072 | 292.3004 | 267.9247
331.3479 | 261.9287 | 223.4117 | 292.3792 | 268.3895
332.3479 | 262.56 | 224.0186 | 291.5656 | 269.4739
333.3479 | 263.9828 | 224.9044 | 292.0478 | 269.0004
334.3479 | 263.9911 | 224.4392 | 291.3454 | 270.2657
335.3479 | 264.6728 | 224.7078 | 290.5231 | 271.0717
336.3479 | 266.7163 | 224.6245 | 291.4331 | 271.4822
337.3479 | 267.6594 | 224.265 | 292.4939 | 271.8048
338.3479 | 268.0595 | 224.741 | 293.5505 | 272.6659
339.3479 | 268.486 | 224.2409 | 293.5632 | 273.2346
340.3479 | 269.5685 | 224.4143 | 294.8739 | 273.3445
341.3479 | 269.9152 | 224.4008 | 294.8986 | 273.7469
342.3479 | 270.4286 | 224.2486 | 295.1423 | 273.6973
343.3479 | 270.8633 | 223.6009 | 295.1331 | 272.6058
344.3479 | 272.4968 | 223.7557 | 293.7843 | 272.1199
345.3479 | 273.7278 | 223.7676 | 293.782 | 271.1602
346.3479 | 274.8409 | 224.2634 | 293.6383 | 270.6293
347.3479 | 275.9831 | 224.7482 | 295.446 | 271.4041
348.3479 | 276.554 | 225.5847 | 296.4158 | 272.9905
349.3479 | 276.7443 | 226.8816 | 296.084 | 273.5397
350.3479 | 277.8177 | 228.0931 | 299.1888 | 274.0245
351.3479 | 278.8232 | 228.6909 | 299.4883 | 275.565
352.3479 | 279.5793 | 228.8475 | 298.6738 | 275.641
353.3479 | 280.1992 | 228.999 | 299.3672 | 275.1038
354.3479 | 281.2541 | 228.959 | 298.6113 | 275.7084
355.3479 | 282.9019 | 228.7639 | 299.2111 | 276.7082
356.3479 | 283.4504 | 228.7905 | 299.7171 | 278.3401
357.3479 | 284.712 | 228.4732 | 299.8469 | 280.7942
358.3479 | 285.9121 | 229.0606 | 301.0253 | 282.4579
359.3479 | 286.4414 | 229.6131 | 299.8325 | 282.3141
360.3479 | 287.4336 | 229.3317 | 299.7123 | 281.8736
361.3479 | 287.3318 | 230.0516 | 300.8124 | 281.1263
362.3479 | 287.1173 | 231.089 | 301.5987 | 280.9972
363.3479 | 286.5124 | 231.5637 | 302.9818 | 280.8344
364.3479 | 287.3589 | 232.7666 | 304.0607 | 280.8587
365.3479 | 287.8327 | 232.3296 | 305.1453 | 281.3943
366.3479 | 288.5248 | 233.3042 | 306.4291 | 281.2272
367.3479 | 289.829 | 233.7261 | 306.941 | 280.7077
368.3479 | 290.4164 | 235.3877 | 307.5972 | 281.9134
369.3479 | 291.3718 | 235.901 | 308.4597 | 282.1476
370.3479 | 292.2545 | 236.9514 | 308.1669 | 282.2372
371.3479 | 292.2524 | 237.3945 | 308.3383 | 281.4344
372.3479 | 292.0216 | 237.7943 | 309.9212 | 281.5142
373.3479 | 292.1179 | 238.72 | 310.9969 | 279.9848
374.3479 | 292.8291 | 243.0175 | 311.0735 | 280.2069
375.3479 | 294.4936 | 244.4231 | 315.2026 | 280.0475
376.3479 | 295.5532 | 246.2886 | 317.1537 | 280.426
377.3479 | 295.9637 | 245.5345 | 318.8249 | 281.1647
378.3479 | 298.1726 | 245.9137 | 318.4998 | 281.7129
379.3479 | 299.6035 | 245.2442 | 319.0919 | 282.1797
380.3479 | 300.9447 | 245.4125 | 318.4085 | 282.237
381.3479 | 300.987 | 244.7761 | 318.7847 | 281.5821
382.3479 | 301.7668 | 245.6972 | 318.4971 | 281.9354
383.3479 | 301.6884 | 247.4153 | 320.0255 | 282.777
384.3479 | 301.8204 | 249.2144 | 322.1132 | 282.6958
385.3479 | 302.3059 | 249.7026 | 322.8424 | 282.3267
386.3479 | 304.3093 | 250.3817 | 325.7852 | 283.6334
387.3479 | 305.9677 | 249.9266 | 325.9347 | 283.3466
388.3479 | 306.0212 | 249.464 | 329.1666 | 283.0408
389.3479 | 306.0346 | 249.8116 | 330.1538 | 283.7563
390.3479 | 307.624 | 250.0685 | 329.4597 | 284.5256
391.3479 | 309.8251 | 250.4405 | 329.2956 | 285.9041
392.3479 | 309.8785 | 249.9986 | 329.8138 | 286.492
393.3479 | 310.1814 | 249.2988 | 329.7365 | 286.269
394.3479 | 311.1837 | 249.6972 | 331.6639 | 287.5608
395.3479 | 312.6003 | 249.8314 | 332.8052 | 288.1247
396.3479 | 312.4006 | 250.09 | 335.3682 | 288.2563
397.3479 | 313.7211 | 249.8566 | 335.7221 | 290.2073
398.3479 | 313.5002 | 251.3917 | 337.6197 | 289.8713
399.3479 | 314.5513 | 251.9418 | 338.7129 | 289.6502
400.3479 | 315.2567 | 252.198 | 339.4525 | 289.7856
401.3479 | 315.5379 | 252.5376 | 340.2605 | 290.6898
402.3479 | 316.1815 | 252.375 | 339.3748 | 291.4648
403.3479 | 316.6808 | 251.9914 | 342.661 | 292.0122
404.3479 | 318.5467 | 252.8086 | 345.3418 | 291.3777
405.3479 | 320.1945 | 254.038 | 349.4902 | 292.1861
406.3479 | 322.9845 | 253.8951 | 353.8368 | 292.7704
407.3479 | 323.2717 | 253.8146 | 352.8113 | 294.8443
408.3479 | 324.4928 | 254.1966 | 352.6615 | 296.0135
409.3479 | 324.4962 | 255.002 | 361.7826 | 296.4583
410.3479 | 325.7612 | 255.7304 | 366.4485 | 297.2773
411.3479 | 325.9494 | 256.0143 | 363.947 | 298.115
412.3479 | 325.8152 | 256.6161 | 360.1146 | 299.3023
413.3479 | 327.1113 | 255.7431 | 356.7563 | 303.8799
414.3479 | 329.8578 | 255.5099 | 357.5135 | 305.5458
415.3479 | 330.813 | 255.2071 | 359.6212 | 307.8777
416.3479 | 332.2059 | 254.5275 | 356.3761 | 308.9459
417.3479 | 331.6307 | 255.1129 | 355.5748 | 309.2381
418.3479 | 332.08 | 254.9661 | 356.4979 | 309.8256
419.3479 | 332.0292 | 255.1611 | 357.0494 | 309.2793
420.3479 | 331.888 | 256.2094 | 357.9493 | 308.2871
421.3479 | 333.2941 | 257.705 | 366.1226 | 307.3204
422.3479 | 333.8167 | 257.5386 | 363.455 | 307.7173
423.3479 | 334.0887 | 257.5569 | 362.8193 | 308.475
424.3479 | 333.1303 | 257.7709 | 360.6149 | 307.6459
425.3479 | 333.962 | 258.4819 | 359.8905 | 308.6065
426.3479 | 334.9342 | 258.7896 | 360.4433 | 309.4338
427.3479 | 335.1017 | 259.2153 | 360.4516 | 311.3252
428.3479 | 336.1166 | 260.0777 | 360.9264 | 311.0789
429.3479 | 338.0613 | 260.5491 | 363.0799 | 310.6723
430.3479 | 337.9581 | 260.8896 | 363.6374 | 309.7038
431.3479 | 336.6204 | 261.6003 | 362.5666 | 308.8577
432.3479 | 338.012 | 260.9119 | 362.5597 | 308.7223
433.3479 | 339.6185 | 260.8274 | 365.8255 | 310.2546
434.3479 | 340.1058 | 261.896 | 368.064 | 310.8571
435.3479 | 340.5892 | 263.0539 | 369.0251 | 311.448
436.3479 | 342.4342 | 262.7694 | 371.611 | 312.4811
437.3479 | 343.1739 | 262.6003 | 376.8464 | 311.6088
438.3479 | 343.8075 | 264.698 | 377.4823 | 313.0713
439.3479 | 344.8652 | 267.1488 | 378.6588 | 312.0569
440.3479 | 345.9075 | 268.651 | 376.7817 | 313.4958
441.3479 | 345.5728 | 269.3604 | 374.6997 | 313.6429
442.3479 | 347.3905 | 270.6368 | 375.6939 | 312.4261
443.3479 | 348.0501 | 270.9869 | 375.198 | 312.0125
444.3479 | 348.1703 | 270.5714 | 375.5576 | 312.0537
445.3479 | 349.6959 | 271.1165 | 379.4833 | 313.3071
446.3479 | 351.1896 | 272.8574 | 387.1369 | 314.5482
447.3479 | 353.4064 | 273.6433 | 396.6055 | 315.3136
448.3479 | 355.9329 | 274.0968 | 406.9608 | 317.2308
449.3479 | 359.4575 | 274.3485 | 412.5415 | 319.01
450.3479 | 360.2809 | 275.8139 | 418.3042 | 320.3622
451.3479 | 366.5834 | 276.1672 | 420.9163 | 323.3026
452.3479 | 369.3534 | 277.6845 | 424.0973 | 322.7998
453.3479 | 371.4124 | 277.5198 | 432.0934 | 328.8968
454.3479 | 374.8196 | 277.2798 | 434.3509 | 329.2754
455.3479 | 376.0484 | 277.7561 | 439.8517 | 330.9761
456.3479 | 377.5816 | 279.0661 | 438.7399 | 333.9856
457.3479 | 379.5049 | 279.361 | 443.2214 | 335.4155
458.3479 | 381.5798 | 279.9941 | 446.5465 | 336.6495
459.3479 | 381.3921 | 279.8738 | 447.4749 | 334.5769
460.3479 | 380.4085 | 281.4137 | 443.7621 | 332.3831
461.3479 | 379.1836 | 283.4746 | 440.349 | 329.4763
462.3479 | 378.7603 | 286.1269 | 437.344 | 328.7686
463.3479 | 376.2026 | 286.028 | 430.8099 | 328.1674
464.3479 | 377.2893 | 285.3341 | 427.3715 | 327.6945
465.3479 | 379.2365 | 285.4421 | 424.9872 | 329.5207
466.3479 | 380.4155 | 285.0387 | 427.4035 | 331.5486
467.3479 | 380.7092 | 284.061 | 424.5618 | 332.8435
468.3479 | 382.7402 | 283.1563 | 424.5943 | 335.7756
469.3479 | 385.2602 | 283.1948 | 427.8091 | 334.3845
470.3479 | 383.8621 | 284.7249 | 430.9316 | 335.9045
471.3479 | 383.8564 | 285.4111 | 432.6555 | 335.4713
472.3479 | 385.0003 | 285.0329 | 442.2822 | 337.2263
473.3479 | 384.0765 | 286.5775 | 446.362 | 338.111
474.3479 | 385.7901 | 287.172 | 448.8334 | 339.5177
475.3479 | 387.7429 | 287.0907 | 447.6634 | 338.7877
476.3479 | 388.3096 | 287.6197 | 446.8277 | 338.0469
477.3479 | 388.0439 | 287.9931 | 440.7981 | 339.2378
478.3479 | 387.9706 | 287.5468 | 436.1187 | 340.9947
479.3479 | 388.9232 | 286.1819 | 434.0949 | 342.2684
480.3479 | 391.0239 | 286.8715 | 431.5091 | 344.6597
481.3479 | 393.8748 | 285.6869 | 431.8782 | 343.6404
482.3479 | 395.8517 | 285.1956 | 434.3456 | 344.6798
483.3479 | 396.2512 | 284.2637 | 433.2451 | 345.3306
484.3479 | 397.9713 | 283.7191 | 436.9658 | 346.1896
485.3479 | 400.7888 | 282.976 | 441.9703 | 348.1104
486.3479 | 407.189 | 281.9468 | 444.2995 | 349.1159
487.3479 | 409.474 | 282.2939 | 449.1899 | 352.3844
488.3479 | 410.5956 | 282.0024 | 458.0403 | 351.572
489.3479 | 412.0051 | 282.3102 | 462.6571 | 352.5893
490.3479 | 413.4642 | 283.1091 | 466.3813 | 353.3082
491.3479 | 414.1738 | 284.3054 | 466.2996 | 354.0455
492.3479 | 413.8066 | 284.0907 | 465.23 | 351.0349
493.3479 | 412.8115 | 284.5356 | 458.6134 | 349.0739
494.3479 | 411.64 | 284.7037 | 450.9197 | 347.9211
495.3479 | 410.3884 | 283.7339 | 446.0854 | 346.8493
496.3479 | 413.3966 | 283.3545 | 444.7035 | 345.1051
497.3479 | 413.769 | 284.7391 | 446.615 | 343.4892
498.3479 | 416.6059 | 284.2096 | 448.8387 | 344.142
499.3479 | 418.9881 | 284.7165 | 451.2986 | 343.3025
500.3479 | 422.8094 | 284.1324 | 453.0598 | 344.5655
501.3479 | 423.1332 | 283.4259 | 461.4945 | 342.7255
502.3479 | 422.5535 | 282.5757 | 466.0105 | 341.4773
503.3479 | 420.6578 | 283.6392 | 463.9283 | 339.5567
504.3479 | 419.3131 | 284.7026 | 471.2514 | 339.7237
505.3479 | 420.8872 | 284.2893 | 472.1391 | 339.9237
506.3479 | 419.4664 | 283.9459 | 474.401 | 341.2723
507.3479 | 420.6935 | 284.4361 | 466.7045 | 340.7526
508.3479 | 422.3922 | 284.7921 | 467.5705 | 340.7595
509.3479 | 423.3346 | 285.6596 | 466.5045 | 339.7942
510.3479 | 426.0441 | 287.0477 | 468.8791 | 338.7459
511.3479 | 428.556 | 287.4617 | 475.2016 | 340.3205
512.3479 | 430.2569 | 289.1349 | 471.1489 | 340.3596
513.3479 | 429.8337 | 288.4204 | 468.4642 | 341.9676
514.3479 | 430.749 | 288.7688 | 464.6441 | 342.1217
515.3479 | 429.878 | 288.5264 | 461.0916 | 344.6499
516.3479 | 431.7081 | 288.1112 | 461.2983 | 344.5876
517.3479 | 435.1057 | 289.1956 | 460.443 | 345.4901
518.3479 | 437.982 | 288.2803 | 461.3896 | 347.0741
519.3479 | 440.3674 | 288.8857 | 469.1374 | 344.9217
520.3479 | 444.5127 | 289.3071 | 467.0116 | 344.8
521.3479 | 448.2023 | 289.5523 | 469.9554 | 346.1982
522.3479 | 449.2613 | 289.1148 | 471.3022 | 345.0216
523.3479 | 450.2997 | 288.5824 | 478.276 | 345.1113
524.3479 | 450.8634 | 288.204 | 491.6939 | 343.9308
525.3479 | 453.7866 | 289.402 | 493.4751 | 344.093
526.3479 | 454.6824 | 290.7876 | 502.6495 | 344.6776
527.3479 | 456.0249 | 291.2965 | 515.433 | 346.6993
528.3479 | 459.6272 | 292.3096 | 515.6192 | 346.8965
529.3479 | 462.1281 | 292.8103 | 523.6727 | 347.1114
530.3479 | 466.3331 | 293.7396 | 529.5978 | 349.3388
531.3479 | 466.2807 | 295.1994 | 525.2462 | 350.3058
532.3479 | 466.8297 | 295.8338 | 527.2008 | 350.2097
533.3479 | 466.1314 | 296.865 | 527.5124 | 350.4822
534.3479 | 467.8709 | 299.8342 | 531.279 | 351.4774
535.3479 | 469.1376 | 300.1756 | 532.532 | 350.6619
536.3479 | 469.2804 | 302.5804 | 537.8056 | 351.9817
537.3479 | 471.4884 | 303.9287 | 540.7348 | 353.431
538.3479 | 472.8345 | 304.1208 | 536.9051 | 353.6534
539.3479 | 475.3937 | 305.3229 | 542.735 | 355.1475
540.3479 | 476.6855 | 306.6292 | 547.8165 | 355.4807
541.3479 | 478.1346 | 307.0451 | 546.7366 | 356.1591
542.3479 | 481.139 | 308.4345 | 546.3862 | 357.9608
543.3479 | 485.0111 | 309.7823 | 541.5546 | 357.7336
544.3479 | 488.0601 | 309.6439 | 542.8529 | 357.5384
545.3479 | 490.9295 | 309.6008 | 540.3419 | 356.7922
546.3479 | 492.0051 | 308.634 | 544.7939 | 357.6043
547.3479 | 492.9978 | 308.6866 | 544.3488 | 358.3158
548.3479 | 492.2966 | 309.4133 | 541.1254 | 359.4827
549.3479 | 492.6853 | 310.7142 | 544.398 | 358.0449
550.3479 | 496.9736 | 313.6497 | 546.5919 | 357.7835
551.3479 | 500.0279 | 312.6526 | 545.7551 | 357.7576
552.3479 | 505.0114 | 314.9066 | 548.3709 | 355.9974
553.3479 | 506.1362 | 315.797 | 546.0338 | 357.0722
554.3479 | 506.3946 | 314.7908 | 548.2167 | 361.7638
555.3479 | 508.4861 | 314.8428 | 543.8431 | 364.9665
556.3479 | 506.7279 | 313.7278 | 549.7579 | 366.0244
557.3479 | 504.5249 | 314.5208 | 551.3584 | 366.1205
558.3479 | 505.0091 | 316.0213 | 552.5637 | 366.9174
559.3479 | 505.137 | 318.3627 | 553.0536 | 366.2177
560.3479 | 507.5186 | 321.0501 | 555.7746 | 366.4267
561.3479 | 509.9789 | 323.7567 | 560.0455 | 368.0545
562.3479 | 513.0416 | 325.9923 | 559.4582 | 368.8242
563.3479 | 512.1123 | 327.2804 | 558.7818 | 368.7824
564.3479 | 517.5903 | 327.1527 | 564.5085 | 371.0291
565.3479 | 520.9566 | 327.927 | 563.3468 | 373.9823
566.3635 | 524.9275 | 328.7772 | 560.0487 | 378.6222
567.3479 | 526.4341 | 329.6922 | 564.8487 | 383.4688
568.3479 | 527.9341 | 331.8001 | 569.3561 | 387.0861
569.3479 | 528.645 | 332.5218 | 565.5646 | 387.4646
570.3479 | 529.6552 | 335.6647 | 567.6756 | 388.4215
571.3479 | 530.2614 | 337.0934 | 571.5693 | 389.2101
572.3479 | 529.2457 | 338.8257 | 580.3464 | 395.9938
573.3479 | 530.5596 | 338.2916 | 583.9599 | 395.4405
574.3479 | 531.3184 | 339.5886 | 580.8529 | 399.5458
575.3479 | 531.8158 | 340.5468 | 587.3069 | 399.58
576.3479 | 531.0564 | 340.0973 | 584.1498 | 398.7285
577.3479 | 528.5577 | 339.0487 | 583.0658 | 403.3994
578.3479 | 529.1813 | 337.0961 | 584.2486 | 404.1423
579.3479 | 528.4069 | 341.6011 | 583.2806 | 404.4372
580.3479 | 530.4562 | 341.2646 | 587.22 | 403.2984
581.3479 | 532.1389 | 342.7294 | 587.6856 | 405.9461
582.3479 | 530.2704 | 344.3914 | 584.0798 | 404.9968
583.3479 | 530.6221 | 343.2991 | 584.8847 | 402.3497
584.3479 | 533.7981 | 346.9251 | 587.7371 | 401.2344
585.3479 | 536.0674 | 347.0262 | 588.3357 | 399.1285
586.3479 | 537.5574 | 348.2395 | 592.9066 | 396.7895
587.3479 | 540.2139 | 347.7395 | 597.6727 | 398.8429
588.3479 | 542.3608 | 347.419 | 598.4445 | 396.8312
589.3479 | 544.3909 | 349.7716 | 601.2519 | 395.374
590.3479 | 546.3358 | 350.4331 | 601.2562 | 394.2255
591.3479 | 549.3063 | 353.325 | 599.3257 | 392.0251
592.3479 | 550.7356 | 354.0848 | 598.925 | 392.3254
593.3479 | 553.1997 | 355.6588 | 601.4059 | 394.9463
594.3479 | 556.511 | 355.1756 | 603.1734 | 395.9215
595.3479 | 558.1507 | 355.8788 | 601.3678 | 395.656
596.3635 | 560.6536 | 356.5266 | 599.9106 | 395.4184
597.3479 | 560.9631 | 363.2296 | 602.2829 | 393.4463
598.3479 | 560.7041 | 365.9104 | 601.2081 | 392.2743
599.3479 | 560.9803 | 369.1467 | 595.7325 | 391.8996
600.3479 | 561.8036 | 369.1541 | 596.6804 | 391.5034
601.3479 | 560.6721 | 369.6307 | 594.8481 | 391.0846
602.3479 | 557.6992 | 369.9933 | 599.1016 | 394.3084
603.3479 | 556.5728 | 370.0032 | 597.2567 | 392.9723
604.3479 | 555.4974 | 369.2862 | 595.168 | 395.5956
605.3479 | 557.9367 | 370.3134 | 601.9694 | 395.1232
606.3479 | 557.6763 | 370.8203 | 599.2543 | 398.2785
607.3479 | 558.3413 | 371.8164 | 603.462 | 398.0296
608.3479 | 558.4499 | 370.4298 | 598.9815 | 396.8014
609.3479 | 557.0139 | 368.9974 | 598.3274 | 395.6203
610.3479 | 556.6512 | 372.6724 | 598.7044 | 398.3405
611.3479 | 555.0775 | 371.0994 | 599.2035 | 399.8835
612.3479 | 558.0492 | 370.0399 | 602.0528 | 400.2473
613.3479 | 556.8158 | 368.537 | 599.1731 | 398.5337
614.3479 | 557.0881 | 370.6999 | 601.6773 | 399.2553
615.3479 | 557.0233 | 377.0665 | 605.2033 | 398.1672
616.3479 | 559.3339 | 376.8722 | 606.8632 | 397.6733
617.3479 | 562.6688 | 377.2198 | 608.619 | 398.4548
618.3479 | 563.0908 | 375.5379 | 610.1154 | 401.0655
619.3479 | 563.0581 | 374.1618 | 612.3174 | 403.317
620.3479 | 562.5614 | 374.8841 | 609.2851 | 404.2093
621.3479 | 562.5138 | 376.8329 | 611.6504 | 403.5022
622.3479 | 559.8306 | 377.463 | 612.7889 | 402.8373
623.3479 | 557.1503 | 379.6637 | 611.3048 | 404.6122
624.3479 | 558.5409 | 380.2503 | 605.077 | 403.375
625.3479 | 559.7056 | 383.4795 | 605.0627 | 401.538
626.3479 | 560.9403 | 385.8447 | 605.7752 | 400.9474
627.3479 | 560.613 | 386.268 | 607.9325 | 401.3757
628.3479 | 557.171 | 384.9385 | 606.6395 | 400.1776
629.3479 | 556.9074 | 386.3581 | 613.6442 | 401.1667
630.3479 | 559.327 | 384.861 | 618.1006 | 399.9819
631.3479 | 557.6976 | 385.7275 | 623.1423 | 399.1972
632.3479 | 557.3061 | 388.7197 | 619.4591 | 398.0461
633.3479 | 554.7504 | 388.9152 | 624.0496 | 397.2548
634.3479 | 555.3609 | 389.5371 | 625.5584 | 397.2221
635.3479 | 557.329 | 392.4683 | 628.7942 | 395.6946
636.3479 | 565.9799 | 394.3932 | 624.7093 | 394.6351
637.3479 | 567.1282 | 394.3905 | 617.8712 | 394.435
638.3479 | 565.2402 | 395.184 | 616.4526 | 393.8304
639.3479 | 563.0145 | 396.1181 | 614.9149 | 398.3097
640.3479 | 562.6739 | 394.2998 | 618.5246 | 398.8065
641.3479 | 562.9361 | 393.8548 | 612.9908 | 399.1184
642.3479 | 562.339 | 391.4846 | 611.0955 | 398.026
643.3479 | 565.3794 | 390.1136 | 612.6322 | 398.277
644.3479 | 566.2209 | 388.0243 | 614.8175 | 403.2309
645.3479 | 567.0696 | 387.794 | 614.0108 | 406.6521
646.3479 | 566.7779 | 385.6008 | 614.067 | 404.849
647.3479 | 565.0339 | 385.3334 | 610.0373 | 402.4625
648.3479 | 564.3585 | 386.8103 | 615.9973 | 401.03
649.3479 | 567.6624 | 387.4127 | 616.5288 | 400.3301
650.3479 | 567.6137 | 388.3225 | 617.6478 | 400.3727
651.3479 | 568.7386 | 389.1816 | 615.9475 | 400.4676
652.3479 | 568.6172 | 387.6886 | 616.8771 | 400.3026
653.3479 | 571.8127 | 389.6189 | 613.7775 | 398.7474
654.3479 | 572.7396 | 392.2603 | 611.6076 | 396.7823
655.3479 | 573.2028 | 390.6853 | 608.4749 | 396.1594
656.3479 | 571.8052 | 392.2935 | 611.6338 | 396.149
657.3479 | 573.3395 | 393.9335 | 612.4554 | 395.2837
658.3479 | 574.1179 | 398.0033 | 612.5403 | 395.3452
659.3479 | 580.7061 | 398.8439 | 616.206 | 393.5856
660.3479 | 584.8799 | 397.9543 | 614.4449 | 392.6114
661.3479 | 587.1401 | 398.5695 | 613.7358 | 391.0705
662.3479 | 588.5901 | 398.909 | 612.0038 | 390.5341
663.3479 | 592.4247 | 398.0208 | 613.2062 | 390.6106
664.3479 | 600.5961 | 396.5412 | 611.7355 | 393.3594
665.3479 | 597.0586 | 395.6113 | 605.3917 | 392.3947
666.3479 | 590.8216 | 393.514 | 608.6772 | 397.242
667.3479 | 594.2098 | 395.4842 | 616.314 | 396.4272
668.3479 | 592.8803 | 394.54 | 613.348 | 395.4114
669.3479 | 591.1431 | 393.0701 | 612.5309 | 394.7867
670.3479 | 587.7631 | 392.4264 | 618.3931 | 395.0455
671.3479 | 589.6293 | 394.1666 | 616.573 | 395.9469
672.3479 | 585.5784 | 393.1714 | 615.9435 | 396.1623
673.3479 | 589.9478 | 390.8388 | 615.2022 | 396.3009
674.3479 | 590.0538 | 391.6707 | 611.5808 | 394.7524
675.3479 | 591.638 | 393.8453 | 605.6708 | 394.6807
676.3479 | 591.9106 | 393.3443 | 602.7904 | 393.7778
677.3479 | 598.5443 | 393.0216 | 600.1168 | 391.8836
678.3479 | 593.9778 | 391.5573 | 609.276 | 392.6784
679.3479 | 589.4526 | 390.134 | 619.698 | 392.723
680.3479 | 588.8133 | 388.4557 | 620.8322 | 392.8238
681.3479 | 588.5755 | 385.7298 | 616.0132 | 393.7356
682.3479 | 583.6108 | 385.8009 | 621.9857 | 393.5989
683.3479 | 582.0723 | 383.8998 | 628.8195 | 393.6951
684.3479 | 578.3887 | 381.9582 | 627.6326 | 391.8172
685.3479 | 578.5731 | 385.6322 | 627.1085 | 392.3386
686.3479 | 578.191 | 387.314 | 629.1025 | 391.4611
687.3479 | 581.2815 | 389.4423 | 630.6846 | 389.9472
688.3479 | 581.1325 | 389.4295 | 630.2955 | 388.5036
689.3479 | 577.4166 | 389.4782 | 635.8263 | 389.2244
690.3479 | 573.5468 | 388.1984 | 637.2405 | 388.9748
691.3479 | 572.773 | 387.0567 | 627.3114 | 388.9072
692.3479 | 572.1386 | 385.9503 | 621.8344 | 392.356
693.3479 | 568.016 | 383.5253 | 627.1747 | 392.5366
694.3479 | 564.9733 | 383.4975 | 622.244 | 392.057
695.3479 | 562.9457 | 386.1319 | 629.4344 | 390.4949
696.3479 | 559.6542 | 390.3928 | 628.0703 | 391.1029
697.3479 | 557.852 | 393.1689 | 626.7709 | 391.5361
698.3479 | 558.8795 | 391.587 | 629.8594 | 390.6085
699.3479 | 560.4497 | 392.2226 | 628.7223 | 390.0863
700.3479 | 568.8969 | 392.7455 | 622.8834 | 388.6885
701.3479 | 569.6332 | 394.2934 | 619.851 | 389.4507
702.3479 | 566.6347 | 397.1668 | 623.6504 | 390.1159
703.3479 | 563.2801 | 397.4805 | 629.3646 | 390.6375
704.3479 | 561.4899 | 396.593 | 628.7423 | 390.5895
705.3479 | 560.7585 | 399.6001 | 626.2963 | 390.5294
706.3479 | 582.5758 | 400.8683 | 625.4579 | 390.4929
707.3479 | 591.7602 | 403.4927 | 620.3831 | 389.8352
708.3479 | 587.7289 | 403.0279 | 623.2124 | 389.0408
709.3479 | 583.7249 | 402.5401 | 623.0767 | 390.5497
710.3479 | 579.6342 | 401.4428 | 628.5032 | 391.2556
711.3479 | 574.6606 | 398.4828 | 630.622 | 390.9777
712.3479 | 574.9306 | 396.5342 | 633.4594 | 391.9572
713.3479 | 572.2487 | 396.364 | 632.3577 | 391.6207
714.3479 | 570.0928 | 394.2391 | 632.6892 | 389.7309
715.3479 | 568.6645 | 398.6565 | 630.4158 | 390.5573
716.3479 | 566.3764 | 399.9003 | 628.1685 | 390.4238
717.3479 | 566.0185 | 398.3177 | 636.3457 | 391.7412
718.3479 | 568.9324 | 398.621 | 637.0385 | 391.4071
719.3479 | 570.5288 | 397.2688 | 628.0165 | 390.6843
720.3479 | 576.9252 | 399.2981 | 622.3387 | 392.093
721.3479 | 577.2675 | 402.8111 | 617.611 | 391.4499
722.3479 | 580.1606 | 403.8231 | 611.2992 | 390.354
723.3479 | 579.462 | 405.0712 | 605.872 | 391.3539
724.3479 | 577.0121 | 407.3 | 604.6414 | 390.0995
725.3479 | 575.1652 | 413.0669 | 602.7885 | 389.2201
726.3479 | 580.0571 | 414.0304 | 601.3868 | 388.0897
727.3479 | 577.6556 | 412.4579 | 593.3826 | 387.8267
728.3479 | 577.7459 | 411.9061 | 602.5481 | 388.0376
729.3479 | 575.9108 | 413.5991 | 606.608 | 389.1193
730.3479 | 573.7848 | 413.7434 | 608.1458 | 388.3868
731.3479 | 572.6728 | 414.2819 | 611.5557 | 388.8283
732.3479 | 571.0286 | 414.3551 | 610.9198 | 389.9246
733.3479 | 568.1838 | 413.7605 | 613.0012 | 391.6458
734.3479 | 566.3089 | 412.6408 | 629.298 | 395.527
735.3479 | 566.4306 | 409.6731 | 631.6304 | 397.3226
736.3479 | 566.2747 | 407.9564 | 630.109 | 397.9841
737.3479 | 567.3678 | 410.2728 | 631.8397 | 397.2871
738.3479 | 567.4438 | 408.9681 | 624.8289 | 396.4441
739.3479 | 566.0612 | 409.7069 | 627.074 | 396.3728
740.3479 | 565.8716 | 415.5153 | 622.3517 | 395.6153
741.3479 | 564.1811 | 414.9769 | 620.8093 | 395.6064
742.3479 | 565.7201 | 416.7071 | 623.4863 | 401.4619
743.3479 | 565.5804 | 417.4918 | 623.1731 | 399.6321
744.3479 | 564.1072 | 418.0818 | 616.9847 | 398.4031
745.3479 | 564.5755 | 417.1509 | 615.4936 | 400.1506
746.3479 | 564.2311 | 415.7894 | 616.6982 | 399.4765
747.3479 | 562.2907 | 413.8894 | 622.4594 | 399.2963
748.3479 | 560.5652 | 415.4611 | 629.0987 | 400.1612
749.3479 | 561.8167 | 414.9232 | 631.4199 | 400.4512
750.3479 | 559.5229 | 414.2808 | 633.2665 | 400.0303
751.3479 | 559.3459 | 412.83 | 629.9 | 397.731
752.3479 | 560.6425 | 412.8868 | 628.7034 | 397.001
753.3479 | 560.5342 | 412.9814 | 629.0964 | 396.2652
754.3479 | 572.5284 | 412.6757 | 627.1338 | 396.9666
755.3479 | 574.3829 | 416.3482 | 621.8612 | 398.7929
756.3479 | 573.8339 | 415.3992 | 618.44 | 399.5705
757.3479 | 573.5791 | 415.6963 | 618.5616 | 400.441
758.3479 | 571.5321 | 416.3332 | 634.1796 | 400.5245
759.3479 | 569.3649 | 417.4677 | 636.8188 | 399.8531
760.3479 | 566.0085 | 415.7649 | 637.0424 | 399.3473
761.3479 | 560.3113 | 413.6138 | 644.7025 | 397.6397
762.3479 | 557.2339 | 412.1753 | 649.1093 | 395.851
763.3479 | 557.6712 | 412.5258 | 656.4976 | 396.0174
764.3479 | 555.6879 | 412.481 | 657.7434 | 396.5188
765.3479 | 553.6685 | 411.773 | 653.1807 | 398.715
766.3479 | 550.9805 | 412.6624 | 647.8486 | 400.4665
767.3479 | 549.1279 | 411.5404 | 654.8634 | 399.7056
768.3479 | 548.9544 | 412.0683 | 657.9214 | 399.3502
769.3479 | 551.3951 | 415.4575 | 656.091 | 398.4892
770.3479 | 551.8822 | 414.9971 | 653.5101 | 400.8117
771.3479 | 553.0629 | 416.885 | 656.325 | 399.399
772.3479 | 552.8592 | 417.8839 | 652.2158 | 400.1601
773.3479 | 551.8246 | 417.7147 | 652.1523 | 399.1419
774.3479 | 551.6981 | 419.0999 | 657.2949 | 399.7412
775.3479 | 552.7847 | 419.1176 | 662.9876 | 399.0867
776.3479 | 555.4795 | 418.9949 | 659.6067 | 398.7087
777.3479 | 558.4208 | 419.0909 | 658.8225 | 399.6712
778.3479 | 559.9763 | 419.4544 | 656.5824 | 399.4523
779.3479 | 560.693 | 421.0192 | 663.0434 | 400.7399
780.3479 | 557.9635 | 419.3072 | 659.0613 | 399.8568
781.3479 | 555.4737 | 416.1973 | 669.1445 | 401.5071
782.3479 | 555.0447 | 416.1673 | 667.5261 | 400.6682
783.3479 | 551.0013 | 414.6587 | 666.5488 | 401.4935
784.3479 | 548.8095 | 416.1772 | 663.739 | 402.0214
785.3479 | 550.147 | 415.2141 | 669.1706 | 403.1277
786.3479 | 551.1632 | 414.0071 | 674.189 | 403.0058
787.3479 | 551.6522 | 415.8966 | 669.9045 | 402.6894
788.3479 | 551.0504 | 420.1982 | 666.859 | 405.2247
789.3479 | 554.087 | 420.3772 | 659.348 | 404.8755
790.3479 | 556.6815 | 420.1978 | 659.9887 | 404.4771
791.3479 | 558.5434 | 421.5454 | 657.6201 | 403.4674
792.3479 | 558.5389 | 420.815 | 661.8726 | 402.8104
793.3479 | 558.6511 | 421.9063 | 660.3898 | 402.7501
794.3479 | 560.6974 | 421.1027 | 661.2212 | 404.1703
795.3479 | 563.2615 | 422.8804 | 663.8378 | 404.0567
796.3479 | 567.2207 | 424.7598 | 667.2563 | 403.0614
797.3479 | 568.182 | 432.1073 | 661.6652 | 402.7298
798.3479 | 568.0036 | 431.7213 | 673.8907 | 401.5731
799.3479 | 574.7509 | 431.6406 | 667.2229 | 400.5261
800.3479 | 581.0564 | 432.2153 | 669.3306 | 399.5991
801.3479 | 583.1679 | 433.7369 | 668.1192 | 402.8796
802.3479 | 584.1964 | 433.6391 | 670.2919 | 404.3832
803.3479 | 582.2181 | 434.1206 | 663.1772 | 404.3819
804.3479 | 580.4211 | 435.3786 | 662.5837 | 405.61
805.3479 | 579.1605 | 432.5128 | 655.6552 | 404.5544
806.3479 | 578.4618 | 431.9269 | 653.0362 | 404.667
807.3479 | 578.7925 | 430.502 | 655.0695 | 405.0139
808.3479 | 580.4406 | 430.1224 | 655.1469 | 404.5727
809.3479 | 583.1074 | 429.428 | 653.1816 | 403.6656
810.3479 | 581.7471 | 432.3478 | 655.6026 | 408.0144
811.3479 | 582.3358 | 431.3753 | 660.5131 | 409.5231
812.3479 | 582.7682 | 432.0271 | 665.3217 | 407.7857
813.3479 | 583.2853 | 432.6072 | 663.7465 | 407.2647
814.3479 | 583.9884 | 433.2748 | 662.0827 | 407.3913
815.3479 | 584.2222 | 431.7961 | 656.5134 | 406.7248
816.3479 | 585.8048 | 432.7556 | 664.1741 | 405.7633
817.3479 | 586.102 | 432.6503 | 663.6536 | 405.3007
818.3479 | 584.2545 | 432.8347 | 663.9133 | 403.6635
819.3479 | 582.6116 | 430.4605 | 668.1357 | 404.3116
820.3479 | 582.4347 | 429.8426 | 664.8536 | 403.9368
821.3479 | 581.6848 | 429.4823 | 662.3142 | 404.1869
822.3479 | 582.4205 | 428.5595 | 661.9327 | 405.5383
823.3479 | 584.6778 | 426.4741 | 666.0211 | 405.3449
824.3479 | 586.9352 | 425.4627 | 662.3227 | 408.2081
825.3479 | 587.0077 | 423.8862 | 662.4919 | 410.451
826.3479 | 588.6664 | 423.2038 | 664.6382 | 415.7207
827.3479 | 589.6368 | 421.3074 | 659.335 | 417.4984
828.3479 | 591.0155 | 418.782 | 654.0568 | 419.264
829.3479 | 592.4499 | 420.9102 | 659.6681 | 418.2671
830.3479 | 592.6459 | 419.752 | 660.0305 | 419.3905
831.3479 | 593.3691 | 422.8017 | 655.9813 | 418.5145
832.3479 | 592.3151 | 423.7262 | 655.5508 | 417.9833
833.3479 | 590.6868 | 427.0522 | 660.8569 | 419.6396
834.3479 | 593.6246 | 426.4895 | 661.6325 | 419.1074
835.3479 | 595.9219 | 426.5132 | 656.3046 | 419.9018
836.3479 | 595.5698 | 426.689 | 651.0455 | 418.0144
837.3479 | 594.9905 | 426.9958 | 651.3149 | 418.0502
838.3479 | 596.2447 | 431.0232 | 645.37 | 418.4756
839.3479 | 596.5122 | 433.9044 | 642.3977 | 416.7485
840.3479 | 596.2703 | 434.9283 | 641.626 | 418.7491
841.3479 | 596.0321 | 435.738 | 640.4609 | 417.6844
842.3479 | 594.2565 | 435.3235 | 638.2096 | 417.5842
843.3479 | 591.4649 | 433.481 | 643.6377 | 417.6829
844.3479 | 588.0663 | 434.3779 | 641.996 | 417.4462
845.3479 | 583.3562 | 435.4836 | 647.2867 | 415.3043
846.3479 | 580.5618 | 438.3984 | 644.165 | 411.9333
847.3479 | 583.6052 | 443.2141 | 655.0694 | 412.4119
848.3479 | 581.7786 | 445.2553 | 654.6307 | 412.6976
849.3479 | 581.138 | 447.0868 | 653.4953 | 413.0722
850.3479 | 579.8011 | 448.3125 | 656.8596 | 410.0657
851.3479 | 577.7005 | 448.0093 | 665.0174 | 408.8517
852.3479 | 577.0568 | 445.5934 | 664.2121 | 408.5957
853.3479 | 576.972 | 446.6789 | 662.8364 | 411.8745
854.3479 | 577.6527 | 444.5495 | 656.4705 | 411.845
855.3479 | 577.8043 | 445.6199 | 653.7195 | 410.5234
856.3479 | 579.9836 | 443.5393 | 651.6911 | 418.0164
857.3479 | 581.3735 | 441.7745 | 654.4866 | 416.2952
858.3479 | 579.1902 | 442.0823 | 650.2787 | 416.171
859.3479 | 577.9848 | 441.0797 | 655.8132 | 416.593
860.3479 | 579.9051 | 441.3791 | 655.0171 | 416.2914
861.3479 | 583.2968 | 438.9141 | 658.2651 | 417.5247
862.3479 | 585.3158 | 440.1995 | 658.7948 | 414.7659
863.3479 | 583.9055 | 440.8503 | 658.6312 | 413.7225
864.3479 | 583.9418 | 439.7175 | 671.4394 | 412.517
865.3479 | 586.5984 | 439.0047 | 665.0229 | 411.1816
866.3479 | 588.8621 | 438.4202 | 650.6754 | 408.7904
867.3479 | 590.43 | 440.2801 | 647.1496 | 407.5996
868.3479 | 591.3277 | 439.5114 | 643.1982 | 406.5312
869.3479 | 593.4573 | 444.6482 | 652.352 | 406.0683
870.3479 | 592.8929 | 443.339 | 653.7212 | 405.3427
871.3479 | 593.3169 | 444.5096 | 650.0854 | 405.5143
872.3479 | 593.3777 | 446.3632 | 653.0935 | 404.9655
873.3479 | 594.1681 | 444.9842 | 646.505 | 404.6959
874.3479 | 593.0319 | 445.2605 | 642.5433 | 403.7802
875.3635 | 594.0224 | 444.555 | 646.6236 | 404.8996
876.3479 | 593.7014 | 444.3205 | 645.7269 | 404.5501
877.3479 | 594.9565 | 441.657 | 643.8564 | 403.7909
878.3479 | 596.0914 | 439.8285 | 638.3578 | 403.984
879.3479 | 596.5975 | 441.504 | 631.0101 | 403.346
880.3479 | 598.8453 | 443.0792 | 638.4586 | 404.4724
881.3479 | 602.8439 | 443.5926 | 634.5535 | 403.4664
882.3479 | 604.5817 | 443.0976 | 638.3973 | 403.1515
883.3479 | 603.1893 | 447.6266 | 639.1107 | 402.4531
884.3479 | 601.2361 | 447.1898 | 646.3825 | 402.2924
885.3479 | 601.2452 | 446.3191 | 644.4101 | 403.8045
886.3479 | 604.3258 | 444.7283 | 647.1519 | 402.2931
887.3479 | 605.4049 | 444.9098 | 642.2227 | 402.0106
888.3479 | 604.5656 | 448.1207 | 652.1635 | 402.3271
889.3479 | 604.2487 | 451.224 | 657.8524 | 402.4335
890.3479 | 606.7706 | 449.697 | 652.3786 | 403.4404
891.3479 | 607.3218 | 448.8594 | 655.6802 | 403.392
892.3479 | 606.267 | 447.4492 | 661.4413 | 403.9259
893.3479 | 601.9232 | 448.2614 | 653.7768 | 403.6377
894.3479 | 600.5958 | 444.6442 | 659.7373 | 402.4355
895.3479 | 600.3495 | 442.6745 | 661.475 | 401.6558
896.3479 | 599.5947 | 442.3083 | 670.5191 | 406.0905
897.3479 | 601.5888 | 442.3371 | 670.7915 | 406.1971
898.3479 | 604.037 | 443.4445 | 666.286 | 409.7328
899.3479 | 606.2745 | 442.8906 | 662.1221 | 411.7607
900.3479 | 604.4671 | 444.028 | 660.1495 | 410.8506
901.3479 | 605.1157 | 443.3993 | 658.0671 | 413.1613
902.3479 | 604.663 | 443.7398 | 659.8373 | 410.6673
903.3479 | 601.691 | 443.2769 | 653.6064 | 409.0406
904.3479 | 601.1704 | 445.9414 | 646.3697 | 408.7496
905.3479 | 600.2454 | 445.6978 | 643.0304 | 408.3814
906.3479 | 596.9334 | 450.5186 | 645.7615 | 407.0255
907.3479 | 592.3202 | 450.7024 | 637.5609 | 405.2773
908.3479 | 586.916 | 452.0599 | 633.993 | 403.6437
909.3479 | 581.3051 | 450.7041 | 644.0667 | 402.7377
910.3479 | 577.4967 | 450.5865 | 647.5406 | 402.3181
911.3479 | 580.6976 | 449.5712 | 648.5613 | 401.5045
912.3479 | 582.5818 | 447.8106 | 650.5127 | 400.378
913.3479 | 582.4648 | 448.1316 | 652.1141 | 401.592
914.3479 | 581.7833 | 445.7067 | 659.1909 | 405.3622
915.3479 | 579.0748 | 443.6469 | 652.8492 | 404.7839
916.3479 | 579.9976 | 449.4369 | 660.0925 | 405.2913
917.3479 | 579.3509 | 452.4561 | 664.7125 | 404.4534
918.3479 | 578.721 | 453.666 | 678.3307 | 407.0938
919.3479 | 578.29 | 453.8284 | 672.9971 | 406.3255
920.3479 | 580.1058 | 453.9132 | 673.9898 | 407.9871
921.3479 | 581.4049 | 455.7068 | 669.585 | 407.1441
922.3479 | 584.0221 | 459.4999 | 671.3404 | 406.4902
923.3479 | 584.9179 | 458.8006 | 670.7373 | 407.1249
924.3479 | 593.4226 | 457.1456 | 669.7705 | 406.966
925.3479 | 597.6253 | 459.028 | 669.7964 | 407.4362
926.3479 | 599.1412 | 461.5146 | 668.8109 | 406.068
927.3479 | 600.6108 | 461.8978 | 666.0673 | 406.817
928.3479 | 601.7601 | 458.34 | 669.0538 | 410.2493
929.3479 | 603.1132 | 455.9279 | 665.2962 | 411.1069
930.3479 | 601.2727 | 456.0299 | 666.5193 | 411.2276
931.3479 | 598.822 | 458.4454 | 663.3531 | 410.9942
932.3479 | 599.6375 | 460.8606 | 669.3306 | 411.2295
933.3479 | 602.0613 | 462.0079 | 668.0654 | 410.5448
934.3479 | 604.2415 | 460.5658 | 661.5619 | 414.916
935.3479 | 602.9262 | 458.3571 | 662.2482 | 416.4959
936.3479 | 602.0218 | 457.8059 | 659.9933 | 419.8227
937.3479 | 602.2886 | 456.5556 | 665.3047 | 419.9137
938.3479 | 600.6386 | 459.1881 | 660.0946 | 419.0111
939.3479 | 598.0989 | 466.3223 | 664.2533 | 420.2131
940.3479 | 598.1315 | 467.9917 | 671.3564 | 419.7972
941.3479 | 595.0059 | 466.8872 | 662.9854 | 421.0562
942.3479 | 592.2649 | 466.7989 | 653.8214 | 420.7796
943.3479 | 589.0554 | 467.9181 | 650.6586 | 419.7362
944.3479 | 588.1203 | 468.7334 | 664.4422 | 420.0625
945.3479 | 587.6006 | 467.8368 | 672.1879 | 418.9042
946.3479 | 586.5889 | 466.3251 | 675.5135 | 421.9658
947.3479 | 587.1067 | 465.9859 | 675.6626 | 422.7843
948.3479 | 590.357 | 464.3784 | 677.7159 | 423.8093
949.3479 | 590.7878 | 464.3193 | 678.5421 | 422.9691
950.3479 | 593.267 | 464.0394 | 679.0978 | 421.1797
951.3479 | 600.6249 | 467.721 | 692.1937 | 420.9642
952.3479 | 601.2138 | 465.966 | 690.8765 | 422.7515
953.3479 | 600.1611 | 468.381 | 692.6586 | 423.0561
954.3479 | 599.1763 | 470.6989 | 689.0099 | 422.999
955.3479 | 606.5654 | 473.3635 | 690.6648 | 422.8217
956.3479 | 604.7294 | 473.7079 | 685.9333 | 422.8476
957.3479 | 603.1246 | 475.9389 | 686.7913 | 424.0889
958.3479 | 604.5266 | 480.98 | 696.7306 | 424.125
959.3479 | 608.8242 | 481.9076 | 701.5113 | 426.3132
960.3479 | 609.0798 | 485.9883 | 705.63 | 427.8448
961.3479 | 609.154 | 485.6834 | 710.8018 | 428.57
962.3479 | 606.0029 | 484.7456 | 705.6658 | 427.6425
963.3479 | 602.1319 | 489.9908 | 697.5187 | 428.7519
964.3479 | 598.7249 | 495.1446 | 695.5757 | 427.6033
965.3479 | 594.6656 | 495.3472 | 692.2259 | 426.0412
966.3479 | 591.819 | 494.7773 | 688.6777 | 424.5474
967.3479 | 591.0897 | 492.3345 | 694.7768 | 424.2371
968.3479 | 591.988 | 492.2812 | 694.1706 | 423.6735
969.3479 | 589.5479 | 488.143 | 700.6323 | 422.8273
970.3479 | 587.8027 | 487.1625 | 701.7185 | 421.8883
971.3479 | 585.9353 | 487.081 | 698.2886 | 419.6284
972.3479 | 584.664 | 487.4646 | 699.1895 | 418.9997
973.3479 | 582.9742 | 489.3796 | 695.1403 | 419.4772
974.3479 | 580.5214 | 486.6602 | 691.1355 | 417.8062
975.3479 | 577.1695 | 490.3325 | 702.1211 | 416.6047
976.3479 | 579.7781 | 493.0937 | 710.9624 | 418.9986
977.3479 | 583.0942 | 497.936 | 718.3715 | 417.8972
978.3479 | 585.6967 | 496.7838 | 707.4845 | 417.9861
979.3479 | 589.3943 | 496.7357 | 704.8056 | 419.8742
980.3479 | 588.9156 | 495.4219 | 694.6032 | 420.3905
981.3479 | 587.7789 | 497.9507 | 697.1166 | 419.3958
982.3479 | 586.4271 | 500.2957 | 697.6349 | 419.397
983.3479 | 583.6432 | 499.6908 | 698.7481 | 419.0359
984.3479 | 582.1017 | 503.2446 | 698.6048 | 421.6521
985.3479 | 582.0921 | 504.9166 | 685.9058 | 422.3001
986.3479 | 585.3133 | 503.3261 | 697.0911 | 425.5585
987.3479 | 586.8273 | 503.0311 | 692.2941 | 426.2149
988.3479 | 587.785 | 505.3676 | 701.7955 | 429.5196
989.3479 | 586.5132 | 505.1956 | 701.0702 | 431.5794
990.3479 | 585.6011 | 505.3345 | 682.7997 | 430.9826
991.3479 | 587.654 | 508.4303 | 681.0497 | 433.0817
992.3479 | 589.9365 | 512.8162 | 691.3804 | 434.0717
993.3479 | 591.0597 | 517.4255 | 698.3638 | 435.5932
994.3479 | 590.8393 | 519.5189 | 690.3273 | 436.6784
995.3479 | 589.2596 | 518.1521 | 696.2506 | 435.3398
996.3479 | 590.639 | 516.256 | 695.5665 | 434.3569
997.3479 | 589.6936 | 522.5917 | 689.2742 | 434.1235
998.3479 | 588.1408 | 519.1411 | 697.3507 | 432.242
999.3479 | 592.338 | 516.5788 | 698.7615 | 432.4317
1000.3479 | 599.569 | 515.59 | 709.3654 | 433.4027
1001.3479 | 603.3155 | 511.7585 | 705.0277 | 432.4393
1002.3479 | 601.9568 | 511.8875 | 697.0364 | 429.8438
1003.3479 | 599.3721 | 511.5287 | 698.403 | 428.7594
1004.3479 | 597.3121 | 508.8502 | 700.7474 | 427.4544
1005.3479 | 593.3941 | 505.5822 | 705.802 | 425.3949
1006.3479 | 589.3734 | 505.8057 | 704.955 | 424.8335
1007.3479 | 584.0792 | 503.2021 | 707.5373 | 424.187
1008.3479 | 592.0253 | 502.9181 | 713.3802 | 423.5946
1009.3479 | 593.8547 | 500.6223 | 718.94 | 423.1686
1010.3479 | 594.2891 | 500.0181 | 724.0175 | 422.6726
1011.3479 | 596.9853 | 501.0855 | 722.4857 | 422.4201
1012.3479 | 601.1955 | 503.5622 | 722.6925 | 423.075
1013.3479 | 602.0361 | 503.3443 | 716.4585 | 423.1348
1014.3479 | 599.4972 | 503.7195 | 716.4749 | 421.7207
1015.3479 | 597.2111 | 502.7183 | 715.9431 | 422.1046
1016.3479 | 595.5133 | 504.1194 | 705.6658 | 421.8207
1017.3479 | 592.7773 | 509.1483 | 707.8189 | 423.83
1018.3479 | 589.5184 | 511.1659 | 719.1964 | 423.1097
1019.3479 | 586.5803 | 511.9627 | 713.5721 | 422.7298
1020.3479 | 589.0751 | 516.9491 | 721.752 | 423.7313
1021.3479 | 595.974 | 520.0494 | 719.6348 | 422.9362
1022.3479 | 600.1471 | 521.2489 | 713.447 | 423.0515
1023.3479 | 599.5623 | 526.3606 | 721.3791 | 423.3693
1024.3479 | 600.1305 | 528.0363 | 710.8905 | 423.9929
1025.3479 | 602.9271 | 531.7981 | 721.1178 | 424.6832
1026.3479 | 600.7895 | 534.986 | 722.7533 | 427.0315
1027.3479 | 598.6717 | 541.2829 | 720.6355 | 427.5639
1028.3479 | 597.124 | 540.7384 | 714.0092 | 426.9497
1029.3479 | 595.3435 | 542.6012 | 712.6981 | 427.6803
1030.3479 | 595.5679 | 543.6563 | 706.256 | 426.4552
1031.3479 | 594.3357 | 538.06 | 702.6114 | 425.5935
1032.3479 | 597.1626 | 537 | 702.9776 | 424.3224
1033.3479 | 594.6194 | 537.5242 | 704.0032 | 423.4942
1034.3479 | 591.3719 | 538.035 | 705.0096 | 422.4333
1035.3479 | 587.7904 | 535.6955 | 712.0569 | 421.9219
1036.3479 | 592.0949 | 535.076 | 708.9413 | 421.5434
1037.3479 | 593.2311 | 536.6006 | 715.6393 | 422.6133
1038.3479 | 597.0977 | 536.6576 | 711.7163 | 423.5072
1039.3479 | 596.851 | 538.1438 | 719.4956 | 425.5066
1040.3479 | 597.6804 | 539.2655 | 721.5323 | 428.8982
1041.3479 | 597.8073 | 539.3799 | 718.9549 | 429.2176
1042.3479 | 594.6392 | 539.4134 | 721.0141 | 429.0028
1043.3479 | 589.0707 | 543.4528 | 720.1746 | 428.5812
1044.3479 | 587.1009 | 546.5597 | 714.1839 | 431.1104
1045.3479 | 584.4857 | 550.4567 | 713.4278 | 429.1064
1046.3479 | 581.6363 | 554.0221 | 707.6218 | 429.7003
1047.3479 | 577.9017 | 557.0984 | 705.7996 | 429.03
1048.3479 | 578.7364 | 559.7943 | 709.0931 | 430.4371
1049.3479 | 577.8439 | 562.8731 | 702.2501 | 430.1553
1050.3479 | 575.2194 | 565.1336 | 705.5543 | 430.6258
1051.3479 | 574.2506 | 560.913 | 709.5008 | 430.5604
1052.3479 | 573.6021 | 562.4689 | 700.8827 | 431.9879
1053.3479 | 572.8644 | 561.5347 | 708.6376 | 434.0604
1054.3479 | 571.585 | 565.8219 | 700.3507 | 434.0716
1055.3479 | 567.3187 | 567.7621 | 695.9405 | 432.3563
1056.3479 | 565.7939 | 565.8353 | 696.4519 | 431.5556
1057.3479 | 565.1417 | 569.394 | 697.3224 | 430.9432
1058.3479 | 562.4062 | 572.7906 | 694.9623 | 429.5691
1059.3479 | 561.5966 | 574.5736 | 691.4194 | 429.4541
1060.3479 | 561.0475 | 575.1417 | 683.7278 | 429.8296
1061.3479 | 561.1034 | 571.6147 | 682.614 | 430.3646
1062.3479 | 560.1727 | 568.2018 | 679.9829 | 430.5787
1063.3479 | 559.1164 | 568.5045 | 684.8315 | 430.6523
1064.3479 | 557.8809 | 568.1848 | 686.2401 | 430.1663
1065.3479 | 557.3762 | 566.9883 | 681.0838 | 429.3493
1066.3479 | 558.8457 | 569.3289 | 677.1044 | 430.182
1067.3479 | 558.9497 | 570.8544 | 681.7209 | 430.4748
1068.3479 | 559.3105 | 573.7024 | 682.2862 | 431.2421
1069.3479 | 559.3094 | 575.1922 | 669.833 | 430.4851
1070.3479 | 558.842 | 577.9232 | 667.6203 | 429.9246
1071.3479 | 558.6924 | 584.9041 | 670.901 | 429.0836
1072.3479 | 560.6613 | 588.6029 | 682.5207 | 429.8898
1073.3479 | 562.7502 | 592.157 | 685.1942 | 431.2764
1074.3479 | 563.9295 | 597.5249 | 684.0279 | 430.677
1075.3479 | 576.686 | 589.361 | 688.5519 | 430.3072
1076.3479 | 578.1555 | 590.7421 | 684.0253 | 430.3425
1077.3479 | 576.7308 | 594.0336 | 679.1007 | 429.3871
1078.3479 | 575.8486 | 591.2 | 678.0317 | 429.8152
1079.3479 | 581.3411 | 588.7166 | 676.6045 | 431.9172
1080.3479 | 582.757 | 590.972 | 689.5966 | 433.0679
1081.3479 | 582.2627 | 591.8245 | 685.6585 | 433.6777
1082.3479 | 580.2389 | 590.6111 | 681.6224 | 432.6803
1083.3479 | 581.3934 | 590.2408 | 687.7535 | 433.1484
1084.3479 | 582.2003 | 588.6547 | 684.9154 | 433.4715
1085.3479 | 585.4211 | 585.7536 | 676.9535 | 432.9424
1086.3479 | 588.2671 | 578.1748 | 677.4074 | 431.5327
1087.3479 | 587.3857 | 575.1833 | 679.9934 | 430.2198
1088.3479 | 592.098 | 571.0987 | 673.2879 | 429.6831
1089.3479 | 596.9211 | 567.838 | 670.7857 | 430.3732
1090.3479 | 601.1194 | 569.2467 | 673.9546 | 430.1798
1091.3479 | 602.3574 | 573.9239 | 673.1032 | 430.4754
1092.3479 | 600.1226 | 581.4067 | 666.0173 | 429.8421
1093.3479 | 599.177 | 584.0086 | 675.4586 | 429.5905
1094.3479 | 606.2487 | 582.8331 | 682.1118 | 429.9395
1095.3479 | 607.4058 | 586.2045 | 677.9695 | 429.4296
1096.3479 | 607.7133 | 591.1682 | 681.4728 | 429.304
1097.3479 | 610.7477 | 589.6895 | 680.8215 | 428.4273
1098.3479 | 613.0466 | 588.8143 | 690.1919 | 428.3384
1099.3479 | 615.6109 | 585.7355 | 696.4756 | 430.1192
1100.3479 | 613.6746 | 585.1644 | 696.8214 | 431.4875
1101.3479 | 612.1243 | 583.9487 | 696.497 | 432.2459
1102.3479 | 610.1997 | 583.0507 | 698.0648 | 434.3785
1103.3479 | 606.1938 | 581.651 | 710.3399 | 433.5157
1104.3479 | 605.2891 | 583.152 | 714.2205 | 433.585
1105.3479 | 599.9836 | 583.3386 | 707.7553 | 433.7798
1106.3479 | 600.3761 | 584.3404 | 718.1738 | 433.8925
1107.3479 | 604.0823 | 586.7018 | 721.6909 | 434.0313
1108.3479 | 610.7944 | 588.2715 | 721.5529 | 434.167
1109.3479 | 612.682 | 589.168 | 720.8235 | 434.8796
1110.3479 | 613.8114 | 590.1566 | 719.4637 | 435.4436
1111.3479 | 612.8824 | 593.934 | 717.0044 | 434.9683
1112.3479 | 619.9263 | 591.5671 | 712.6207 | 435.3714
1113.3479 | 619.8522 | 589.8947 | 709.6861 | 435.4627
1114.3479 | 615.8833 | 590.6004 | 705.8115 | 435.3776
1115.3479 | 610.5997 | 597.4252 | 698.1367 | 436.444
1116.3479 | 607.9879 | 594.3606 | 699.5494 | 437.3147
1117.3479 | 606.7491 | 593.0475 | 702.967 | 436.64
1118.3479 | 603.3335 | 594.3661 | 718.4636 | 437.5855
1119.3479 | 600.7129 | 594.6197 | 711.2321 | 437.8586
1120.3479 | 595.8556 | 597.3222 | 704.2352 | 438.9489
1121.3479 | 592.547 | 598.8656 | 706.855 | 440.1821
1122.3479 | 600.9009 | 601.0833 | 714.0868 | 439.8712
1123.3479 | 602.8083 | 600.0438 | 715.1355 | 441.4835
1124.3479 | 600.7577 | 598.3285 | 702.12 | 440.9198
1125.3479 | 599.5846 | 603.4907 | 703.7136 | 440.1197
1126.3479 | 607.1096 | 606.2268 | 707.1056 | 440.4396
1127.3479 | 610.0304 | 602.8914 | 710.2458 | 441.2661
1128.3479 | 608.433 | 606.2766 | 707.5035 | 440.7099
1129.3479 | 611.2743 | 604.946 | 704.6357 | 441.3877
1130.3479 | 613.9906 | 606.2451 | 702.171 | 441.9894
1131.3479 | 615.4086 | 609.259 | 690.72 | 441.5114
1132.3479 | 614.1776 | 609.738 | 689.3676 | 441.4626
1133.3479 | 612.9132 | 618.0057 | 696.0805 | 442.0281
1134.3479 | 610.6156 | 626.2987 | 683.7549 | 442.9269
1135.3479 | 606.3204 | 626.0812 | 673.0922 | 443.6142
1136.3479 | 605.8243 | 621.4766 | 688.0302 | 445.3142
1137.3479 | 603.7069 | 624.9289 | 686.2696 | 448.062
1138.3479 | 601.9196 | 630.9167 | 685.6655 | 448.4374
1139.3479 | 600.9897 | 632.745 | 691.6385 | 449.2227
1140.3479 | 608.1761 | 631.0587 | 684.2449 | 449.2712
1141.3479 | 613.3447 | 633.5772 | 691.2059 | 452.5876
1142.3479 | 616.6549 | 634.8446 | 693.3415 | 453.8475
1143.3479 | 622.1798 | 631.33 | 686.1898 | 456.7474
1144.3479 | 622.2676 | 637.7446 | 694.0466 | 458.1133
1145.3479 | 622.3396 | 637.5373 | 686.3021 | 457.0637
1146.3479 | 625.8435 | 632.4312 | 690.9189 | 456.462
1147.3479 | 624.853 | 636.739 | 691.6064 | 456.1834
1148.3479 | 620.5559 | 637.4381 | 684.0217 | 456.6016
1149.3479 | 623.8411 | 638.8865 | 689.9799 | 456.5673
1150.3479 | 624.134 | 645.8405 | 681.7606 | 457.6338
1151.3479 | 622.2327 | 641.87 | 686.1616 | 457.0951
1152.3479 | 619.7492 | 646.6917 | 679.0222 | 459.6644
1153.3479 | 616.8168 | 646.5194 | 677.5189 | 461.4722
1154.3479 | 618.1525 | 643.5618 | 692.4553 | 461.2003
1155.3479 | 622.2114 | 645.4036 | 692.1469 | 460.9223
1156.3479 | 621.2183 | 641.7423 | 685.3307 | 460.2666
1157.3479 | 618.1922 | 639.3997 | 686.6286 | 459.6723
1158.3479 | 623.291 | 640.9359 | 697.8022 | 460.0197
1159.3479 | 629.3911 | 637.5026 | 698.6994 | 462.1265
1160.3479 | 636.1761 | 634.9276 | 694.7046 | 464.3098
1161.3479 | 637.4432 | 641.7568 | 695.8916 | 466.8418
1162.3479 | 636.7985 | 644.1298 | 697.3975 | 467.4853
1163.3479 | 638.19 | 644.5437 | 700.1235 | 467.8534
1164.3479 | 638.8531 | 645.9626 | 701.3372 | 468.3856
1165.3479 | 638.8472 | 651.5309 | 701.6031 | 471.449
1166.3479 | 643.494 | 647.9004 | 694.8695 | 470.8427
1167.3479 | 653.7777 | 648.4986 | 698.2246 | 473.0066
1168.3479 | 653.3064 | 646.1708 | 695.4706 | 474.3214
1169.3479 | 661.8779 | 646.2734 | 693.501 | 474.3268
1170.3479 | 656.2656 | 649.2042 | 685.803 | 474.9411
1171.3479 | 656.9678 | 648.9886 | 680.6924 | 475.0979
1172.3479 | 652.0746 | 644.9162 | 681.1444 | 475.9112
1173.3479 | 652.9878 | 647.0284 | 681.7315 | 474.5647
1174.3479 | 655.5519 | 648.8033 | 670.0457 | 472.7806
1175.3479 | 652.5362 | 644.475 | 669.8448 | 471.6983
1176.3479 | 651.1751 | 644.2398 | 677.0086 | 470.8001
1177.3479 | 652.9491 | 644.5514 | 677.4925 | 470.4866
1178.3479 | 652.7836 | 651.7232 | 676.493 | 472.783
1179.3479 | 651.4213 | 648.5813 | 676.9215 | 470.2724
1180.3479 | 647.7035 | 646.1074 | 674.0747 | 470.2481
1181.3479 | 649.9602 | 648.5061 | 687.5277 | 468.2503
1182.3479 | 651.4885 | 648.9168 | 687.2261 | 469.3881
1183.3479 | 656.7196 | 646.917 | 682.5854 | 470.5589
1184.3479 | 660.451 | 649.6875 | 675.9314 | 470.9344
1185.3479 | 659.3939 | 651.8799 | 682.0152 | 473.3066
1186.3479 | 656.0193 | 660.1393 | 676.1919 | 471.9007
1187.3479 | 661.0909 | 658.44 | 682.3108 | 470.9712
1188.3479 | 661.5894 | 656.554 | 685.2563 | 472.2359
1189.3479 | 669.93 | 650.2029 | 676.0313 | 472.3695
1190.3479 | 673.0548 | 646.8561 | 680.3974 | 471.501
1191.3479 | 673.2645 | 643.4 | 682.8891 | 471.5999
1192.3479 | 673.6523 | 643.2942 | 694.0147 | 470.9381
1193.3479 | 672.3203 | 640.0717 | 696.3985 | 469.7874
1194.3479 | 669.0393 | 641.2557 | 687.5675 | 469.6696
1195.3479 | 666.835 | 645.3878 | 693.815 | 469.4345
1196.3479 | 662.6406 | 645.9182 | 682.0796 | 469.3937
1197.3479 | 663.6003 | 648.9901 | 673.6519 | 470.7504
1198.3479 | 659.9035 | 650.3846 | 669.1219 | 469.9412
1199.3479 | 651.2255 | 652.112 | 678.1018 | 467.5362
1200.3479 | 656.3215 | 650.204 | 684.3347 | 466.4242
1201.3479 | 654.5802 | 648.5753 | 682.8852 | 466.0978
1202.3479 | 655.321 | 646.832 | 674.2959 | 465.4466
1203.3479 | 655.8771 | 645.744 | 674.9558 | 467.6485
1204.3479 | 660.7702 | 648.6823 | 674.5761 | 471.5867
1205.3479 | 661.9262 | 648.6436 | 671.1805 | 472.8183
1206.3479 | 665.8481 | 649.3599 | 676.8313 | 473.3452
1207.3479 | 671.5465 | 651.9453 | 672.227 | 472.8372
1208.3479 | 674.009 | 649.3149 | 661.5013 | 475.4578
1209.3479 | 672.6031 | 653.2436 | 668.9213 | 476.5214
1210.3479 | 670.9169 | 651.5785 | 673.6939 | 478.0904
1211.3479 | 668.8609 | 656.5912 | 665.3732 | 479.629
1212.3479 | 670.5619 | 659.6288 | 661.9069 | 482.6436
1213.3479 | 669.7946 | 664.7414 | 667.9854 | 484.0778
1214.3479 | 666.9374 | 671.2471 | 660.6261 | 484.9769
1215.3479 | 665.2733 | 674.663 | 654.9753 | 483.2486
1216.3479 | 665.2159 | 674.2797 | 654.8259 | 482.8359
1217.3479 | 665.6968 | 682.091 | 657.0848 | 481.2994
1218.3479 | 665.8011 | 681.8833 | 659.4384 | 479.4225
1219.3479 | 665.7991 | 674.5565 | 671.9828 | 479.843
1220.3479 | 666.6081 | 675.2665 | 669.8726 | 479.0763
1221.3479 | 667.3328 | 674.742 | 668.5893 | 480.0782
1222.3479 | 667.3726 | 679.0124 | 665.246 | 477.98
1223.3479 | 668.9031 | 671.8469 | 670.5271 | 479.9445
1224.3479 | 670.7135 | 670.4598 | 675.7597 | 477.2578
1225.3479 | 674.1969 | 668.9694 | 679.0438 | 477.7639
1226.3479 | 675.002 | 667.5752 | 684.8986 | 478.8563
1227.3479 | 678.6253 | 665.9831 | 683.1136 | 480.1465
1228.3479 | 678.5845 | 660.3896 | 685.0272 | 479.1208
1229.3479 | 678.1774 | 668.7515 | 680.3438 | 478.2185
1230.3479 | 677.7321 | 674.1368 | 678.8013 | 477.5294
1231.3479 | 681.8045 | 668.8213 | 677.0611 | 476.5437
1232.3479 | 684.3178 | 661.9043 | 668.7883 | 477.2241
1233.3479 | 685.1958 | 652.0935 | 672.424 | 477.2719
1234.3479 | 684.7959 | 650.4606 | 682.4516 | 478.0317
1235.3479 | 686.5239 | 657.6076 | 690.7333 | 478.2622
1236.3479 | 684.4206 | 659.1158 | 683.5929 | 479.4488
1237.3479 | 679.503 | 663.9537 | 691.172 | 480.4646
1238.3479 | 676.632 | 663.8807 | 686.0869 | 480.1139
1239.3479 | 675.8472 | 663.6944 | 683.9844 | 485.1732
1240.3479 | 674.2961 | 668.1926 | 687.7918 | 483.638
1241.3479 | 673.5385 | 677.8606 | 678.1644 | 483.5398
1242.3479 | 675.1303 | 676.167 | 669.652 | 483.6474
1243.3479 | 677.5945 | 675.3791 | 665.6295 | 487.8434
1244.3479 | 678.6362 | 677.3425 | 676.2212 | 489.0812
1245.3479 | 676.5808 | 681.7626 | 671.2775 | 488.0883
1246.3479 | 676.1496 | 682.7445 | 664.4021 | 488.727
1247.3479 | 678.1155 | 674.2945 | 665.2744 | 487.6618
1248.3479 | 677.477 | 679.6836 | 659.4512 | 489.8369
1249.3479 | 680.01 | 673.0688 | 658.6015 | 488.8599
1250.3479 | 678.5706 | 675.2017 | 652.1552 | 487.4811
1251.3479 | 678.0409 | 671.2373 | 641.7531 | 486.1695
1252.3479 | 680.1378 | 672.5076 | 635.1192 | 486.7757
1253.3479 | 679.0719 | 666.4193 | 647.614 | 486.1476
1254.3479 | 678.0583 | 668.8427 | 646.9825 | 485.8429
1255.3479 | 676.9616 | 674.6568 | 640.5198 | 483.6135
1256.3479 | 676.2252 | 675.6246 | 637.7847 | 480.5733
1257.3479 | 678.6061 | 677.836 | 633.5004 | 483.0449
1258.3479 | 676.1931 | 672.4733 | 628.8653 | 482.9594
1259.3479 | 679.9837 | 671.1038 | 631.8654 | 483.3702
1260.3479 | 678.4259 | 678.0435 | 628.4472 | 483.3019
1261.3479 | 677.6626 | 688.3945 | 635.4917 | 481.8181
1262.3479 | 680.0856 | 683.3571 | 645.4056 | 484.8905
1263.3479 | 676.8708 | 678.538 | 638.1803 | 483.2569
1264.3479 | 674.0561 | 687.7158 | 630.2144 | 482.76
1265.3479 | 677.1447 | 692.5487 | 629.0797 | 481.7121
1266.3479 | 676.3738 | 692.9056 | 623.5611 | 483.3321
1267.3479 | 674.2848 | 694.5424 | 621.2092 | 483.4236
1268.3479 | 672.8043 | 701.3881 | 624.2674 | 483.3721
1269.3479 | 674.5462 | 698.9958 | 621.1257 | 484.6588
1270.3479 | 670.3767 | 694.7746 | 614.5724 | 484.3912
1271.3479 | 671.5991 | 688.9775 | 623.5178 | 486.7347
1272.3479 | 670.6447 | 689.2642 | 629.0898 | 484.9634
1273.3479 | 670.3259 | 693.9257 | 642.6037 | 486.6894
1274.3479 | 671.8865 | 699.2141 | 644.0776 | 489.7931
1275.3479 | 671.7496 | 697.7513 | 654.0434 | 489.6326
1276.3479 | 671.4609 | 698.4864 | 650.6638 | 488.907
1277.3479 | 671.7497 | 697.9662 | 642.4647 | 488.0871
1278.3479 | 672.3764 | 700.9858 | 643.0511 | 487.6055
1279.3479 | 672.9518 | 697.3459 | 646.4799 | 486.6471
1280.3479 | 672.9085 | 700.2555 | 648.3144 | 488.1121
1281.3479 | 676.3068 | 699.4346 | 659.7873 | 488.3477
1282.3479 | 676.9153 | 700.7155 | 668.3122 | 488.5103
1283.3479 | 677.3572 | 697.9565 | 670.0838 | 490.6842
1284.3479 | 677.0833 | 697.7694 | 685.0792 | 491.6053
1285.3479 | 677.6837 | 697.2974 | 688.1361 | 489.7454
1286.3479 | 683.9162 | 689.3966 | 688.2235 | 492.0057
1287.3479 | 684.5896 | 686.9618 | 689.9264 | 491.1043
1288.3479 | 687.0086 | 690.5692 | 695.268 | 491.1944
1289.3479 | 687.7764 | 700.5807 | 687.9692 | 490.5234
1290.3479 | 686.2536 | 700.62 | 688.0004 | 492.1637
1291.3479 | 685.9269 | 700.7497 | 684.3294 | 493.4055
1292.3479 | 685.1132 | 694.5947 | 685.249 | 496.1207
1293.3479 | 684.2893 | 687.4768 | 682.2536 | 493.3921
1294.3479 | 684.1486 | 689.0752 | 686.4081 | 493.0623
1295.3479 | 682.3864 | 689.7442 | 688.4017 | 491.6181
1296.3479 | 682.5759 | 686.7169 | 685.6267 | 490.406
1297.3479 | 682.5747 | 683.9438 | 688.3434 | 490.5108
1298.3479 | 681.3035 | 692.1939 | 691.0613 | 490.647
1299.3479 | 680.8214 | 693.8472 | 682.883 | 493.4166
1300.3479 | 683.0804 | 690.2682 | 670.7435 | 495.2393
1301.3479 | 684.171 | 691.2278 | 673.5439 | 495.5504
1302.3479 | 685.1985 | 694.9082 | 661.5113 | 495.8841
1303.3479 | 684.1811 | 686.1918 | 650.5003 | 496.4046
1304.3479 | 689.8632 | 684.6863 | 643.4042 | 496.4878
1305.3479 | 687.0698 | 677.5458 | 638.9626 | 498.8378
1306.3479 | 685.4865 | 683.3932 | 632.6367 | 499.1866
1307.3479 | 684.5842 | 677.6665 | 623.7288 | 497.057
1308.3479 | 683.0364 | 669.9686 | 617.273 | 495.1072
1309.3479 | 682.6045 | 679.1426 | 622.2406 | 497.4895
1310.3479 | 680.2422 | 685.9143 | 628.078 | 500.9411
1311.3479 | 678.1424 | 687.8856 | 633.1171 | 501.4872
1312.3479 | 676.2608 | 698.712 | 630.9641 | 502.0652
1313.3479 | 678.7091 | 708.9117 | 626.44 | 499.9152
1314.3479 | 679.2495 | 707.0777 | 622.3128 | 499.7609
1315.3479 | 680.419 | 711.8165 | 622.1432 | 498.4182
1316.3479 | 680.4168 | 718.0113 | 620.893 | 500.86
1317.3479 | 679.9544 | 720.1471 | 618.4717 | 501.0168
1318.3479 | 679.4086 | 712.7395 | 611.5569 | 502.933
1319.3479 | 677.2625 | 712.8274 | 604.6145 | 513.8425
1320.3479 | 674.7873 | 711.3421 | 612.5014 | 514.9805
1321.3479 | 674.6996 | 723.069 | 617.4719 | 515.2813
1322.3479 | 674.4954 | 727.3288 | 622.6283 | 514.298
1323.3479 | 672.6423 | 727.4856 | 629.4973 | 515.5057
1324.3479 | 671.8286 | 727.1333 | 625.7943 | 519.9185
1325.3479 | 669.8489 | 722.3384 | 621.5164 | 520.83
1326.3479 | 668.0774 | 714.8308 | 616.3673 | 518.4045
1327.3479 | 669.1569 | 719.7156 | 611.2713 | 518.4295
1328.3479 | 669.3365 | 716.8335 | 607.9008 | 519.1348
1329.3479 | 669.7963 | 708.8797 | 606.6015 | 516.5363
1330.3479 | 668.6005 | 719.216 | 607.8964 | 518.1976
1331.3479 | 667.0505 | 720.9513 | 612.8655 | 523.3548
1332.3479 | 666.333 | 728.9485 | 611.6344 | 524.3084
1333.3479 | 667.0634 | 731.6285 | 609.6974 | 521.495
1334.3479 | 668.5296 | 735.9917 | 613.3684 | 519.386
1335.3479 | 668.7986 | 731.7179 | 618.6578 | 515.9403
1336.3479 | 668.6721 | 723.7348 | 620.9212 | 513.0225
1337.3479 | 666.5048 | 729.6627 | 629.4729 | 514.1267
1338.3479 | 666.1015 | 740.4916 | 629.6772 | 512.7856
1339.3479 | 670.4181 | 738.9679 | 629.1072 | 511.1297
1340.3479 | 671.4665 | 727.8973 | 643.6365 | 512.4386
1341.3479 | 670.9627 | 731.7133 | 649.609 | 512.1055
1342.3479 | 673.8034 | 732.7257 | 649.5991 | 510.6196
1343.3479 | 673.003 | 734.7749 | 654.2377 | 512.216
1344.3479 | 673.9807 | 727.0084 | 650.5315 | 510.4607
1345.3479 | 674.2917 | 730.2576 | 651.0704 | 510.4367
1346.3479 | 675.7677 | 730.6996 | 640.4869 | 509.4502
1347.3479 | 675.103 | 719.1187 | 634.5374 | 511.1659
1348.3479 | 678.0343 | 713.0639 | 629.4666 | 509.7075
1349.3479 | 677.8738 | 714.7009 | 636.8519 | 508.7984
1350.3479 | 685.9735 | 715.8237 | 632.1632 | 506.8798
1351.3479 | 684.466 | 713.2718 | 624.3871 | 505.346
1352.3479 | 684.3715 | 710.4126 | 630.0279 | 503.5931
1353.3479 | 687.8961 | 713.4822 | 639.2518 | 505.5569
1354.3479 | 689.9307 | 715.7077 | 633.6569 | 506.0675
1355.3479 | 687.9172 | 720.3027 | 626.6698 | 505.6327
1356.3479 | 692.7668 | 719.1691 | 618.4513 | 507.6472
1357.3479 | 689.5028 | 718.2986 | 612.0931 | 509.6471
1358.3479 | 684.8133 | 730.6373 | 611.727 | 507.4275
1359.3479 | 684.6353 | 733.4748 | 622.6638 | 505.3188
1360.3479 | 681.4694 | 732.3924 | 628.3994 | 505.3632
1361.3479 | 679.0956 | 732.9107 | 621.7013 | 504.528
1362.3479 | 678.5698 | 729.2654 | 615.2436 | 503.4978
1363.3479 | 675.6051 | 741.0612 | 612.4115 | 504.8605
1364.3479 | 673.0023 | 740.9705 | 606.5185 | 508.6148
1365.3479 | 670.045 | 744.0398 | 603.1607 | 508.5218
1366.3479 | 668.7018 | 745.6981 | 615.7924 | 508.6376
1367.3479 | 671.1859 | 749.8692 | 628.0821 | 509.2638
1368.3479 | 671.385 | 747.4202 | 644.2936 | 509.7674
1369.3479 | 670.977 | 744.826 | 637.3266 | 510.2602
1370.3479 | 671.7262 | 735.2244 | 629.6754 | 514.4854
1371.3479 | 671.2784 | 734.2575 | 639.6754 | 513.6006
1372.3479 | 673.7068 | 737.9175 | 648.4429 | 514.9426
1373.3479 | 673.9909 | 738.4559 | 656.848 | 514.5246
1374.3479 | 674.6767 | 742.7162 | 664.2651 | 513.3416
1375.3479 | 674.7041 | 745.1815 | 666.8699 | 512.8142
1376.3479 | 675.6512 | 742.9171 | 674.0867 | 511.2949
1377.3479 | 676.2421 | 743.1088 | 677.3185 | 512.2743
1378.3479 | 676.4135 | 746.953 | 685.6872 | 511.9931
1379.3479 | 675.8311 | 746.5366 | 693.2426 | 511.0007
1380.3479 | 675.3606 | 743.6044 | 694.2753 | 511.514
1381.3479 | 676.0969 | 739.4131 | 697.6097 | 511.5839
1382.3479 | 677.9375 | 745.7873 | 697.9851 | 516.5879
1383.3479 | 678.1507 | 739.9322 | 695.9112 | 516.6744
1384.3479 | 678.5556 | 738.9245 | 701.5963 | 520.1644
1385.3479 | 678.5489 | 737.075 | 689.3465 | 519.2118
1386.3479 | 680.039 | 738.4778 | 676.5076 | 520.5075
1387.3479 | 679.955 | 736.3421 | 666.1222 | 522.738
1388.3479 | 678.3382 | 740.3952 | 657.2165 | 524.7468
1389.3479 | 677.1169 | 737.4641 | 666.4176 | 522.3259
1390.3479 | 677.7911 | 747.1617 | 670.071 | 520.1065
1391.3479 | 681.768 | 747.2827 | 664.4365 | 520.4449
1392.3479 | 679.337 | 749.1089 | 669.2446 | 522.1351
1393.3479 | 679.994 | 755.4091 | 678.8539 | 524.4362
1394.3479 | 679.3028 | 747.6783 | 685.6647 | 524.1997
1395.3479 | 679.0592 | 754.3503 | 692.5826 | 522.5483
1396.3479 | 679.7325 | 756.0487 | 690.5984 | 520.444
1397.3479 | 680.2472 | 754.6873 | 695.2456 | 520.4586
1398.3479 | 679.6794 | 748.8502 | 697.7565 | 518.9101
1399.3479 | 678.6894 | 751.7333 | 708.8043 | 517.9421
1400.3479 | 680.302 | 757.462 | 704.5169 | 514.3141
1401.3479 | 683.4022 | 749.5499 | 701.3049 | 513.7768
1402.3479 | 687.0227 | 750.7895 | 704.4515 | 512.6829
1403.3479 | 686.3143 | 745.6313 | 709.7811 | 513.5
1404.3479 | 686.1178 | 732.8338 | 720.674 | 515.2947
1405.3479 | 683.9989 | 738.3016 | 712.0041 | 514.7901
1406.3479 | 682.6944 | 740.3089 | 715.2771 | 516.8416
1407.3479 | 680.1648 | 747.1941 | 718.825 | 514.9675
1408.3479 | 679.1458 | 758.3952 | 723.4056 | 517.9074
1409.3479 | 677.9616 | 762.4003 | 717.3714 | 517.9253
1410.3479 | 681.9279 | 762.916 | 724.2777 | 519.5047
1411.3479 | 678.1464 | 762.7124 | 722.313 | 519.7526
1412.3479 | 676.3583 | 760.6463 | 711.0046 | 522.644
1413.3479 | 679.4545 | 754.0676 | 715.0055 | 524.9405
1414.3479 | 677.5139 | 757.677 | 710.2412 | 523.4341
1415.3479 | 673.7962 | 768.1027 | 720.5556 | 525.4312
1416.3479 | 669.7892 | 761.5021 | 709.0637 | 524.3745
1417.3479 | 665.8295 | 762.3765 | 716.8336 | 523.5041
1418.3479 | 666.7161 | 764.2337 | 726.0737 | 523.3988
1419.3479 | 666.1484 | 761.7763 | 736.9084 | 523.0335
1420.3479 | 665.2251 | 766.2371 | 724.9079 | 524.6079
1421.3479 | 665.4236 | 770.6396 | 720.3815 | 533.5104
1422.3479 | 665.0036 | 776.7997 | 723.4605 | 538.7431
1423.3479 | 665.3576 | 776.2145 | 724.3255 | 542.0632
1424.3479 | 664.1854 | 783.0404 | 723.49 | 549.6065
1425.3479 | 662.1794 | 778.0059 | 722.5303 | 546.7798
1426.3479 | 661.6316 | 775.7301 | 717.0075 | 543.5596
1427.3479 | 660.0008 | 772.8249 | 716.761 | 540.3275
1428.3479 | 655.9917 | 770.3032 | 714.4261 | 541.0065
1429.3479 | 652.1718 | 770.899 | 710.356 | 541.0949
1430.3479 | 652.2612 | 766.5185 | 707.9329 | 538.9678
1431.3479 | 653.3459 | 762.6289 | 708.9942 | 537.5198
1432.3479 | 652.7015 | 759.0394 | 707.5162 | 536.9716
1433.3479 | 652.8743 | 761.1091 | 701.9452 | 537.9598
1434.3479 | 652.7737 | 753.2491 | 697.274 | 540.1995
1435.3479 | 654.0942 | 754.2922 | 689.8212 | 537.6098
1436.3479 | 654.058 | 748.3936 | 685.614 | 535.5856
1437.3479 | 654.2296 | 752.1832 | 689.0933 | 533.3751
1438.3479 | 653.5916 | 754.8192 | 691.8401 | 535.0479
1439.3479 | 654.2987 | 746.8658 | 682.6513 | 534.7293
1440.3479 | 653.2859 | 748.7813 | 680.9319 | 534.1909
1441.3479 | 653.2847 | 748.8243 | 678.8138 | 538.1934
1442.3479 | 655.7047 | 749.1108 | 673.5616 | 535.361
1443.3479 | 654.6672 | 754.1015 | 669.7006 | 534.2354
1444.3479 | 654.1918 | 751.716 | 667.195 | 534.7586
1445.3479 | 655.5968 | 752.1055 | 672.3428 | 533.9481
1446.3479 | 655.7456 | 753.2862 | 675.0959 | 531.7092
1447.3479 | 654.5534 | 743.481 | 675.1348 | 529.2748
1448.3479 | 652.2071 | 741.0511 | 669.9211 | 527.0576
1449.3479 | 653.0219 | 739.0079 | 674.6396 | 534.8318
1450.3479 | 653.0485 | 744.1916 | 671.3296 | 538.9216
1451.3479 | 651.6564 | 744.1358 | 661.9011 | 535.8852
1452.3479 | 652.7966 | 747.5649 | 667.6889 | 535.996
1453.3479 | 656.7122 | 751.7933 | 679.8488 | 534.7273
1454.3479 | 656.6533 | 754.6494 | 674.8582 | 532.5323
1455.3479 | 657.8239 | 760.5814 | 673.6821 | 530.7473
1456.3479 | 657.6535 | 748.1058 | 679.3389 | 528.4775
1457.3479 | 658.2647 | 741.469 | 680.6945 | 526.6302
1458.3479 | 658.5406 | 734.0821 | 677.0918 | 529.5277
1459.3479 | 656.74 | 733.0268 | 680.6957 | 528.8104
1460.3479 | 652.6049 | 731.6796 | 683.8805 | 527.2052
1461.3479 | 651.3925 | 730.4831 | 672.4101 | 525.3422
1462.3479 | 651.2058 | 727.0752 | 676.2968 | 523.2785
1463.3479 | 652.1674 | 728.1938 | 675.9843 | 522.1632
1464.3479 | 653.7005 | 730.3888 | 686.6372 | 524.9382
1465.3479 | 651.9573 | 738.2525 | 682.2131 | 526.0163
1466.3479 | 649.4703 | 735.3634 | 672.6154 | 528.8802
1467.3479 | 647.9105 | 736.6589 | 666.5912 | 527.1089
1468.3479 | 645.8728 | 744.6399 | 663.5413 | 526.778
1469.3479 | 645.2997 | 747.0735 | 653.5359 | 523.5328
1470.3479 | 644.8431 | 745.0565 | 647.1381 | 524.491
1471.3479 | 648.6846 | 752.6492 | 641.8924 | 525.2342
1472.3479 | 647.5671 | 747.6387 | 647.8446 | 523.119
1473.3479 | 646.5904 | 738.2408 | 636.0623 | 521.2635
1474.3479 | 644.9093 | 738.4875 | 633.43 | 521.507
1475.3479 | 643.0298 | 740.8614 | 631.157 | 522.304
1476.3479 | 642.1928 | 748.0939 | 630.864 | 525.1489
1477.3479 | 642.8731 | 744.988 | 631.6025 | 524.5858
1478.3479 | 643.7601 | 750.7642 | 641.9333 | 523.6717
1479.3479 | 645.3129 | 749.1029 | 648.2182 | 524.2657
1480.3479 | 645.9501 | 748.6698 | 643.4072 | 527.3164
1481.3479 | 646.999 | 750.1181 | 644.5578 | 526.8434
1482.3479 | 645.6918 | 752.4072 | 642.2511 | 525.6216
1483.3479 | 645.2012 | 743.959 | 637.5374 | 530.5002
1484.3479 | 643.3664 | 754.1064 | 633.0237 | 529.3911
1485.3479 | 643.5005 | 749.0757 | 635.505 | 530.6487
1486.3479 | 646.1535 | 749.8915 | 633.2257 | 531.6663
1487.3479 | 643.9868 | 752.9481 | 635.1549 | 530.6951
1488.3479 | 643.2183 | 756.196 | 630.7964 | 529.4741
1489.3479 | 643.9664 | 757.0418 | 631.4679 | 530.845
1490.3479 | 646.4108 | 759.557 | 630.4008 | 529.4101
1491.3479 | 645.6747 | 758.3915 | 631.2153 | 527.0123
1492.3479 | 646.5808 | 760.7569 | 624.8088 | 526.864
1493.3479 | 646.4435 | 758.1247 | 626.8031 | 527.3435
1494.3479 | 643.3758 | 754.0099 | 619.832 | 526.9992
1495.3479 | 641.1501 | 746.9647 | 614.7821 | 526.1611
1496.3479 | 641.9103 | 753.0537 | 608.4181 | 525.8803
1497.3479 | 640.8005 | 754.4366 | 602.6519 | 527.1539
1498.3479 | 642.4047 | 763.3561 | 601.9884 | 527.3927
1499.3479 | 641.8994 | 761.0156 | 602.7081 | 528.5437
1500.3479 | 642.1865 | 771.1737 | 599.9385 | 531.2699
1501.3479 | 641.6613 | 769.68 | 599.9754 | 531.3621
1502.3479 | 640.2013 | 774.8142 | 598.4322 | 529.9932
1503.3479 | 641.2808 | 774.989 | 601.1105 | 536.5315
1504.3479 | 641.7207 | 775.1921 | 603.4183 | 532.7003
1505.3479 | 641.4179 | 768.0751 | 602.9364 | 530.545
1506.3479 | 642.7275 | 773.6968 | 598.8892 | 531.2112
1507.3479 | 647.5029 | 771.6418 | 594.826 | 530.3675
1508.3479 | 645.67 | 780.9921 | 592.1815 | 530.3635
1509.3479 | 645.4054 | 781.6513 | 593.5706 | 529.6066
1510.3479 | 645.5986 | 776.3751 | 594.94 | 527.6328
1511.3479 | 646.7222 | 779.3894 | 593.1466 | 526.1843
1512.3479 | 645.2876 | 778.2671 | 597.7345 | 525.1177
1513.3479 | 643.9946 | 779.7622 | 597.1606 | 523.6536
1514.3479 | 641.7218 | 777.0955 | 601.6607 | 523.6119
1515.3479 | 641.9757 | 780.5721 | 599.7117 | 524.2841
1516.3479 | 646.2991 | 777.4616 | 596.9245 | 526.0607
1517.3479 | 647.8482 | 777.2902 | 596.1552 | 526.4759
1518.3479 | 647.1156 | 777.8519 | 593.2009 | 527.9001
1519.3479 | 648.9048 | 768.3887 | 589.0563 | 528.2354
1520.3479 | 650.0735 | 755.684 | 585.2763 | 527.4723
1521.3479 | 648.4002 | 761.2758 | 585.1765 | 528.1753
1522.3479 | 648.5048 | 757.9418 | 588.1754 | 531.7921
1523.3479 | 647.7932 | 762.8747 | 585.5606 | 529.2328
1524.3479 | 647.2537 | 760.5311 | 583.4605 | 528.3606
1525.3479 | 646.5313 | 760.5585 | 583.3529 | 525.8711
1526.3479 | 645.603 | 756.7519 | 583.1714 | 527.9493
1527.3479 | 645.3722 | 754.076 | 581.8121 | 528.5035
1528.3479 | 645.0402 | 752.5588 | 580.97 | 527.875
1529.3479 | 645.5088 | 752.3569 | 584.1559 | 529.1985
1530.3479 | 650.6446 | 748.9055 | 585.6155 | 529.7542
1531.3479 | 651.9096 | 749.9655 | 587.8864 | 529.7302
1532.3479 | 651.9956 | 756.0672 | 595.6114 | 529.9863
1533.3479 | 654.6334 | 751.1049 | 591.798 | 530.1654
1534.3479 | 654.9289 | 748.5908 | 589.5774 | 538.849
1535.3479 | 654.6169 | 748.0464 | 586.6218 | 539.7287
1536.3479 | 654.9794 | 749.2233 | 588.1155 | 537.8097
1537.3479 | 654.8173 | 752.3165 | 587.0604 | 535.829
1538.3479 | 654.373 | 752.4787 | 585.4118 | 534.654
1539.3479 | 654.5921 | 745.8204 | 584.0921 | 532.3356
1540.3479 | 655.4568 | 745.6885 | 582.7277 | 530.9813
1541.3479 | 654.3622 | 744.6262 | 582.5614 | 527.7886
1542.3479 | 653.2787 | 750.311 | 581.8501 | 528.4967
1543.3479 | 655.7269 | 748.0942 | 580.2971 | 527.9623
1544.3479 | 652.4887 | 737.3237 | 576.0789 | 527.935
1545.3479 | 648.1618 | 734.0683 | 573.856 | 529.2937
1546.3479 | 645.6175 | 738.9732 | 573.2292 | 527.2152
1547.3479 | 645.2473 | 744.0211 | 573.1749 | 528.7717
1548.3479 | 645.0444 | 746.9246 | 571.6875 | 526.1691
1549.3479 | 645.334 | 751.9116 | 571.0437 | 525.3082
1550.3479 | 642.9815 | 753.7425 | 570.4715 | 525.5294
1551.3479 | 641.311 | 753.9484 | 568.625 | 524.5905
1552.3479 | 641.8343 | 750.3836 | 567.3598 | 525.6299
1553.3479 | 641.698 | 749.382 | 566.7078 | 527.5201
1554.3479 | 641.7278 | 749.3979 | 565.718 | 529.2299
1555.3479 | 642.8802 | 749.1351 | 565.8926 | 528.9625
1556.3479 | 642.877 | 754.4976 | 565.6311 | 533.6771
1557.3479 | 643.4625 | 749.5121 | 565.3923 | 534.0431
1558.3479 | 645.0101 | 746.8683 | 564.1858 | 533.8265
1559.3479 | 647.6579 | 746.1194 | 564.093 | 535.27
1560.3479 | 650.0019 | 753.4546 | 564.5382 | 535.2511
1561.3479 | 650.3606 | 752.0492 | 564.9782 | 536.4669
1562.3479 | 650.084 | 754.8369 | 566.3127 | 535.3267
1563.3479 | 649.2134 | 754.2038 | 565.7919 | 533.8356
1564.3479 | 649.7694 | 752.9953 | 565.0942 | 533.2401
1565.3479 | 650.4291 | 749.561 | 565.409 | 534.1366
1566.3479 | 649.3027 | 757.859 | 567.7316 | 532.5374
1567.3479 | 647.3062 | 757.0013 | 566.846 | 533.6921
1568.3479 | 646.6674 | 754.0656 | 565.556 | 532.8599
1569.3479 | 646.9672 | 751.6325 | 564.5055 | 530.7127
1570.3479 | 646.7746 | 755.2873 | 564.3372 | 532.765
1571.3479 | 645.5807 | 757.3933 | 565.153 | 532.8321
1572.3479 | 644.7155 | 766.1936 | 564.423 | 534.5073
1573.3479 | 645.4713 | 764.4879 | 565.4027 | 532.549
1574.3479 | 645.5982 | 764.8049 | 564.4734 | 531.2537
1575.3479 | 647.4967 | 754.6236 | 564.5359 | 537.3419
1576.3479 | 648.3016 | 756.6186 | 567.9012 | 541.5346
1577.3479 | 649.9977 | 742.5883 | 567.6396 | 541.5145
1578.3479 | 649.4033 | 738.5484 | 566.6295 | 540.5875
1579.3479 | 648.662 | 746.4221 | 566.3938 | 536.9864
1580.3479 | 649.43 | 747.9923 | 566.0854 | 536.7155
1581.3479 | 648.8833 | 757.3169 | 566.2736 | 540.2897
1582.3479 | 649.0613 | 754.8573 | 566.0354 | 541.8269
1583.3479 | 648.4023 | 755.1886 | 565.8129 | 541.1984
1584.3479 | 647.101 | 751.3824 | 565.0345 | 540.3237
1585.3479 | 645.6886 | 745.3997 | 563.1877 | 537.2396
1586.3479 | 643.7572 | 737.3795 | 560.782 | 539.4673
1587.3479 | 641.9281 | 723.334 | 559.9247 | 542.7169
1588.3479 | 642.3024 | 744.3024 | 559.4085 | 540.1508
1589.3479 | 646.3189 | 733.9576 | 559.1305 | 539.1687
1590.3479 | 644.3299 | 745.2202 | 560.4803 | 537.3863
1591.3479 | 642.1983 | 746.8061 | 559.9294 | 536.7484
1592.3479 | 641.0964 | 759.0341 | 559.7829 | 535.3973
1593.3479 | 639.7554 | 758.5217 | 559.9478 | 534.2218
1594.3479 | 639.3261 | 748.356 | 559.9286 | 536.6141
1595.3479 | 640.9785 | 738.2222 | 557.2663 | 534.5809
1596.3479 | 641.2087 | 742.0768 | 557.1576 | 533.8509
1597.3479 | 642.266 | 741.5356 | 556.6542 | 533.3162
1598.3479 | 641.1756 | 745.5115 | 557.7922 | 531.9494
1599.3479 | 640.524 | 743.0026 | 558.3023 | 530.9981
1600.3479 | 645.2713 | 735.0461 | 559.3243 | 530.6175
1601.3479 | 645.7473 | 730.4215 | 561.2703 | 532.8898
1602.3479 | 645.1757 | 734.6462 | 564.0534 | 530.7389
1603.3479 | 644.883 | 731.8981 | 563.5615 | 529.7116
1604.3479 | 644.0775 | 726.0546 | 562.6322 | 528.8555
1605.3479 | 645.4735 | 735.8399 | 561.7871 | 527.6653
1606.3479 | 645.4833 | 736.5505 | 561.8713 | 526.5661
1607.3479 | 644.2823 | 743.7868 | 561.8521 | 524.2264
1608.3479 | 641.8757 | 742.1831 | 560.4289 | 524.186
1609.3479 | 644.05 | 735.9052 | 559.9171 | 521.8173
1610.3479 | 644.1948 | 728.6595 | 560.3532 | 521.0669
1611.3479 | 643.1357 | 722.3465 | 559.469 | 522.3387
1612.3479 | 642.7403 | 724.1448 | 559.4784 | 522.4997
1613.3479 | 640.0636 | 734.2864 | 560.4965 | 524.8142
1614.3479 | 639.0599 | 742.416 | 559.1789 | 523.3445
1615.3479 | 639.4227 | 749.5582 | 560.0224 | 521.638
1616.3479 | 638.8992 | 753.0097 | 562.1595 | 521.9291
1617.3635 | 641.145 | 748.2989 | 564.8015 | 523.2754
1618.3479 | 640.2653 | 750.2151 | 562.1257 | 523.5455
1619.3479 | 641.3369 | 749.8318 | 560.7195 | 522.7508
1620.3479 | 641.4218 | 760.1782 | 560.9117 | 523.9084
1621.3479 | 642.0395 | 746.2916 | 560.131 | 524.4558
1622.3479 | 642.4868 | 745.0754 | 559.1221 | 522.6736
1623.3479 | 643.6444 | 745.4813 | 559.2657 | 523.5467
1624.3479 | 645.9615 | 756.1795 | 559.7096 | 522.0845
1625.3479 | 648.3784 | 744.3558 | 560.9754 | 526.1472
1626.3479 | 650.3131 | 741.3151 | 561.7078 | 525.716
1627.3479 | 649.7974 | 731.7703 | 560.4711 | 526.5878
1628.3479 | 646.0361 | 717.1888 | 560.2165 | 525.0571
1629.3479 | 644.1746 | 714.7503 | 560.3521 | 522.9464
1630.3479 | 643.9845 | 720.8904 | 559.7126 | 522.3052
1631.3479 | 644.7171 | 707.8176 | 559.7279 | 520.7961
1632.3479 | 644.2498 | 702.8347 | 559.6987 | 524.2202
1633.3479 | 642.6232 | 715.298 | 559.025 | 523.1396
1634.3479 | 640.9476 | 726.1309 | 558.3954 | 521.0081
1635.3479 | 639.3946 | 728.0848 | 558.235 | 520.0669
1636.3479 | 637.1597 | 729.485 | 558.8802 | 519.0109
1637.3479 | 634.6435 | 728.6339 | 557.6281 | 518.8374
1638.3479 | 634.0296 | 730.9079 | 556.8233 | 519.9792
1639.3479 | 633.7681 | 735.7156 | 557.4507 | 521.0357
1640.3479 | 628.7837 | 741.1731 | 556.6305 | 520.7388
1641.3479 | 625.665 | 738.9354 | 555.395 | 521.3059
1642.3479 | 625.3653 | 740.3081 | 555.4138 | 519.7032
1643.3479 | 624.3269 | 739.8716 | 555.221 | 518.613
1644.3479 | 624.4814 | 732.1562 | 555.2586 | 519.1368
1645.3479 | 624.5031 | 741.9808 | 554.0307 | 521.3626
1646.3479 | 625.4583 | 739.1902 | 553.7337 | 521.5078
1647.3635 | 624.3764 | 736.4309 | 553.0837 | 522.7744
1648.3479 | 624.2051 | 732.3629 | 552.7999 | 521.7874
1649.3479 | 625.3845 | 727.7843 | 552.6467 | 522.9409
1650.3479 | 626.5896 | 733.5521 | 552.3609 | 526.9202
1651.3479 | 627.5761 | 739.7019 | 554.4507 | 528.6309
1652.3479 | 627.3702 | 738.3623 | 555.3862 | 528.3828
1653.3479 | 625.1487 | 744.2398 | 554.085 | 526.714
1654.3479 | 625.5377 | 749.1731 | 554.091 | 525.8351
1655.3479 | 627.2241 | 737.6388 | 556.102 | 526.9876
1656.3479 | 629.0366 | 745.1288 | 556.5546 | 525.8439
1657.3479 | 628.8418 | 743.081 | 556.5624 | 525.2073
1658.3479 | 627.6912 | 743.7516 | 556.7548 | 524.3626
1659.3479 | 628.3283 | 731.4038 | 556.6027 | 522.4963
1660.3479 | 626.8572 | 727.9185 | 556.7445 | 521.7949
1661.3479 | 628.0386 | 732.0233 | 556.3064 | 520.3958
1662.3479 | 631.8026 | 723.9542 | 556.8288 | 523.0985
1663.3479 | 633.8896 | 715.0548 | 556.602 | 522.3753
1664.3479 | 632.65 | 698.6734 | 556.4539 | 522.5669
1665.3479 | 631.701 | 695.7122 | 557.099 | 522.558
1666.3479 | 632.1397 | 695.2049 | 558.1171 | 520.6449
1667.3479 | 632.5902 | 704.2844 | 556.5321 | 519.4058
1668.3479 | 631.587 | 700.3493 | 555.1007 | 520.9929
1669.3479 | 629.4841 | 689.4074 | 552.1352 | 523.6022
1670.3479 | 624.107 | 692.0602 | 550.98 | 527.4928
1671.3479 | 622.2952 | 700.8293 | 551.2026 | 526.7351
1672.3479 | 622.32 | 698.1456 | 551.1265 | 526.1222
1673.3479 | 621.7445 | 689.9345 | 551.3242 | 523.3826
1674.3479 | 621.7478 | 685.6274 | 551.068 | 522.8013
1675.3479 | 622.0985 | 687.6431 | 551.1764 | 521.5969
1676.3479 | 622.8845 | 691.2406 | 550.901 | 519.2037
1677.3479 | 621.6737 | 685.7321 | 549.8394 | 519.0096
1678.3479 | 620.6568 | 693.3904 | 548.0514 | 519.7429
1679.3479 | 617.9116 | 684.7592 | 546.468 | 518.9596
1680.3479 | 618.9241 | 683.7188 | 544.8679 | 519.6381
1681.3479 | 616.9014 | 674.8471 | 543.4239 | 519.4694
1682.3479 | 616.167 | 677.4093 | 542.8519 | 520.1815
1683.3479 | 618.4643 | 677.5882 | 544.0243 | 519.5096
1684.3479 | 618.6493 | 678.7527 | 545.8831 | 518.3439
1685.3479 | 616.8676 | 680.4555 | 546.3021 | 518.4245
1686.3479 | 616.9137 | 685.7526 | 547.9301 | 516.9325
1687.3479 | 617.009 | 685.064 | 547.7556 | 516.5988
1688.3479 | 617.2468 | 681.048 | 547.7124 | 517.0437
1689.3479 | 618.1848 | 678.0663 | 547.5337 | 517.3316
1690.3479 | 620.4179 | 670.5572 | 547.7751 | 516.5029
1691.3479 | 621.5072 | 671.9029 | 548.6561 | 517.4407
1692.3479 | 623.6487 | 667.2136 | 548.9771 | 517.9995
1693.3479 | 624.3757 | 674.4058 | 549.6253 | 516.1463
1694.3479 | 625.437 | 678.399 | 548.791 | 514.3149
1695.3479 | 625.3469 | 672.1956 | 548.9929 | 516.0908
1696.3479 | 624.7644 | 678.5923 | 549.3656 | 513.7837
1697.3479 | 625.7478 | 676.1575 | 548.3958 | 512.6801
1698.3479 | 628.0193 | 671.693 | 549.3665 | 519.3448
1699.3479 | 626.6717 | 668.8065 | 548.682 | 523.4151
1700.3479 | 627.4219 | 682.4997 | 549.9493 | 522.3976
1701.3479 | 627.8472 | 689.9282 | 549.1597 | 521.2712
1702.3479 | 626.1655 | 703.2718 | 548.6426 | 518.6988
1703.3479 | 626.218 | 702.2745 | 548.9929 | 517.4341
1704.3479 | 627.0159 | 703.05 | 549.4956 | 518.0962
1705.3479 | 626.8293 | 694.5077 | 548.2741 | 518.5121
1706.3479 | 628.8114 | 685.0544 | 546.7968 | 518.9479
1707.3479 | 628.7598 | 686.9855 | 545.6877 | 519.3563
1708.3479 | 625.3656 | 682.3292 | 544.1155 | 519.3238
1709.3479 | 625.3707 | 676.8395 | 541.7294 | 517.6277
1710.3479 | 624.2573 | 692.9493 | 539.6483 | 517.1588
1711.3479 | 625.4128 | 692.5586 | 539.5035 | 515.2687
1712.3479 | 625.8307 | 684.7662 | 539.0776 | 513.3223
1713.3479 | 626.5589 | 680.3579 | 538.6649 | 513.2728
1714.3479 | 626.2003 | 669.7611 | 538.7435 | 514.3753
1715.3479 | 625.8683 | 671.8035 | 540.3953 | 515.469
1716.3479 | 624.9219 | 675.4329 | 540.5672 | 515.2272
1717.3479 | 624.5311 | 665.016 | 538.7085 | 512.9601
1718.3479 | 622.9289 | 657.6716 | 538.9343 | 512.9349
1719.3479 | 622.0623 | 667.5117 | 539.9993 | 511.1447
1720.3479 | 621.3987 | 681.4565 | 541.096 | 512.3153
1721.3479 | 621.9244 | 686.2297 | 542.5421 | 512.3886
1722.3479 | 621.9419 | 685.1606 | 542.9093 | 510.7022
1723.3479 | 619.0924 | 690.8842 | 543.8316 | 507.9816
1724.3479 | 616.7325 | 699.8935 | 543.8448 | 507.8019
1725.3479 | 616.7259 | 706.0756 | 542.9825 | 505.2394
1726.3479 | 615.9746 | 708.3799 | 543.7075 | 505.0956
1727.3479 | 613.3162 | 718.0149 | 543.5977 | 503.5866
1728.3479 | 612.6666 | 718.5714 | 542.4324 | 502.2983
1729.3479 | 613.3861 | 710.1402 | 541.4062 | 504.6284
1730.3479 | 615.156 | 698.9179 | 541.9081 | 503.3598
1731.3479 | 615.9415 | 686.9736 | 541.851 | 504.7583
1732.3479 | 617.1698 | 681.5148 | 542.0332 | 504.9514
1733.3479 | 618.7949 | 682.5917 | 542.6399 | 505.7144
1734.3479 | 618.5994 | 676.0931 | 542.0968 | 506.8526
1735.3479 | 619.3458 | 677.8213 | 542.9038 | 508.3859
1736.3479 | 619.3949 | 672.7861 | 543.9017 | 509.2543
1737.3479 | 620.2557 | 672.1973 | 544.7304 | 510.9381
1738.3479 | 622.536 | 673.5255 | 545.3947 | 511.6177
1739.3479 | 623.4018 | 667.2697 | 543.3187 | 510.8749
1740.3479 | 620.9457 | 662.3504 | 539.8132 | 511.7755
1741.3479 | 620.169 | 660.1571 | 538.5338 | 513.5804
1742.3479 | 620.1308 | 659.653 | 538.0693 | 515.4258
1743.3479 | 618.0383 | 659.856 | 538.9682 | 514.8378
1744.3479 | 618.4514 | 671.0102 | 539.8105 | 513.3785
1745.3479 | 618.7597 | 668.5579 | 540.7774 | 511.2633
1746.3479 | 615.8528 | 662.0571 | 540.2644 | 513.7179
1747.3479 | 615.6506 | 655.144 | 539.6373 | 511.7487
1748.3479 | 615.7237 | 647.8814 | 539.8068 | 511.7557
1749.3479 | 615.6014 | 640.8146 | 538.773 | 512.1896
1750.3479 | 614.9005 | 635.2241 | 538.1646 | 512.6107
1751.3479 | 613.1758 | 632.5108 | 537.5983 | 510.6412
1752.3479 | 613.6678 | 628.2324 | 536.287 | 510.3573
1753.3479 | 614.1676 | 629.9231 | 537.0503 | 514.187
1754.3479 | 614.7628 | 625.9861 | 537.0139 | 512.3018
1755.3479 | 615.2936 | 629.4737 | 539.1437 | 512.2008
1756.3479 | 612.8481 | 633.3278 | 539.6778 | 510.6893
1757.3479 | 611.4366 | 641.2507 | 539.2378 | 510.232
1758.3479 | 610.1732 | 645.5537 | 538.8374 | 508.625
1759.3479 | 606.6706 | 652.7382 | 538.2569 | 506.6846
1760.3479 | 608.9766 | 655.1208 | 539.7847 | 506.9115
1761.3479 | 609.5885 | 659.9697 | 539.9791 | 505.7517
1762.3479 | 610.8818 | 662.7309 | 540.0498 | 503.6949
1763.3479 | 612.0429 | 654.8111 | 540.2376 | 503.8351
1764.3479 | 613.5429 | 658.709 | 540.3836 | 502.466
1765.3479 | 613.0547 | 655.5252 | 539.6963 | 501.5692
1766.3479 | 613.5046 | 649.8911 | 540.5813 | 500.729
1767.3479 | 612.6512 | 645.5263 | 541.198 | 500.1899
1768.3479 | 611.0688 | 646.3883 | 541.7648 | 501.7584
1769.3479 | 611.4245 | 642.3889 | 541.7222 | 500.4339
1770.3479 | 613.3103 | 648.0924 | 542.5911 | 500.5335
1771.3479 | 614.1374 | 651.3292 | 543.5553 | 502.0294
1772.3479 | 613.5406 | 644.0642 | 543.3156 | 502.9154
1773.3479 | 616.0186 | 647.5819 | 540.9256 | 503.8182
1774.3479 | 617.7563 | 648.0338 | 541.2673 | 507.5973
1775.3479 | 617.4512 | 645.386 | 540.4811 | 505.896
1776.3479 | 618.8421 | 644.896 | 541.0258 | 505.6289
1777.3479 | 618.7663 | 639.158 | 540.5377 | 505.1059
1778.3479 | 619.8153 | 643.5013 | 540.7193 | 504.9424
1779.3479 | 618.2821 | 641.434 | 542.5704 | 503.287
1780.3479 | 618.9911 | 639.4673 | 542.4247 | 505.256
1781.3479 | 621.1978 | 638.2792 | 541.4632 | 504.1892
1782.3479 | 621.114 | 643.6431 | 540.9181 | 504.4506
1783.3479 | 621.7725 | 640.4309 | 540.376 | 506.2659
1784.3479 | 622.5477 | 635.9351 | 540.3988 | 505.9047
1785.3479 | 621.6551 | 631.2246 | 540.5062 | 505.1802
1786.3479 | 621.645 | 626.3282 | 540.0612 | 507.3653
1787.3479 | 621.2523 | 623.0914 | 539.7961 | 506.7402
1788.3479 | 619.8771 | 625.5185 | 540.4925 | 508.5266
1789.3479 | 618.7615 | 623.0392 | 540.2012 | 509.2527
1790.3479 | 619.6299 | 620.9504 | 541.0396 | 509.2922
1791.3479 | 620.5396 | 619.8889 | 541.1198 | 509.3105
1792.3479 | 621.7715 | 617.4349 | 541.971 | 507.4373
1793.3479 | 620.3185 | 618.8356 | 541.3941 | 505.9606
1794.3479 | 619.1484 | 613.7666 | 540.7681 | 505.5394
1795.3479 | 619.7609 | 613.4712 | 539.7901 | 503.7947
1796.3479 | 618.7347 | 616.6016 | 540.5276 | 501.7826
1797.3635 | 619.055 | 618.8608 | 542.2922 | 500.8502
1798.3479 | 619.9696 | 622.65 | 543.0668 | 499.3346
1799.3479 | 619.9146 | 620.0719 | 542.612 | 498.7441
1800.3479 | 614.947 | 618.552 | 542.2289 | 496.4402
1801.3479 | 613.846 | 617.1259 | 542.8767 | 495.0614
1802.3479 | 614.3242 | 617.8668 | 543.2151 | 493.989
1803.3479 | 615.7336 | 613.9931 | 542.7604 | 493.9075
1804.3479 | 615.8079 | 618.4229 | 543.5958 | 493.7308
1805.3479 | 618.0296 | 616.8565 | 543.3449 | 492.6263
1806.3479 | 618.89 | 617.6267 | 541.8358 | 491.343
1807.3479 | 618.6262 | 618.0387 | 541.4759 | 491.7316
1808.3479 | 619.8514 | 614.3568 | 541.0727 | 491.2843
1809.3479 | 621.0304 | 614.9778 | 540.5168 | 490.7141
1810.3479 | 618.8492 | 613.4045 | 540.9525 | 489.7729
1811.3479 | 619.1512 | 611.5509 | 539.783 | 487.8642
1812.3479 | 617.7876 | 609.8939 | 540.5589 | 486.5985
1813.3479 | 614.6374 | 608.9764 | 541.5759 | 486.1754
1814.3479 | 615.8475 | 610.0101 | 541.3757 | 486.3199
1815.3479 | 617.4746 | 607.6451 | 540.9356 | 485.401
1816.3479 | 618.4161 | 611.4635 | 541.3532 | 484.3248
1817.3479 | 619.2212 | 610.9589 | 541.7283 | 484.204
1818.3479 | 617.3724 | 609.6703 | 540.4465 | 484.4419
1819.3479 | 616.3869 | 609.202 | 539.1763 | 484.3557
1820.3479 | 615.4932 | 622.2294 | 540.1577 | 485.2256
1821.3479 | 616.4429 | 627.9848 | 538.47 | 487.208
1822.3479 | 619.159 | 636.1585 | 538.215 | 491.2251
1823.3479 | 618.6873 | 634.4608 | 538.2659 | 492.6804
1824.3479 | 619.2341 | 631.481 | 539.772 | 493.0179
1825.3479 | 618.9514 | 628.6581 | 538.1935 | 497.0945
1826.3479 | 618.2401 | 628.6004 | 539.6195 | 496.3044
1827.3479 | 619.2687 | 623.8217 | 540.2902 | 495.0991
1828.3479 | 620.3601 | 622.5962 | 539.7215 | 494.8676
1829.3479 | 621.0714 | 625.5623 | 538.9694 | 493.4343
1830.3479 | 620.413 | 624.4175 | 537.8257 | 492.4621
1831.3479 | 619.6992 | 619.1965 | 538.4963 | 492.7666
1832.3479 | 621.1981 | 618.0165 | 537.6176 | 497.5631
1833.3479 | 622.3034 | 621.5234 | 539.45 | 497.7684
1834.3479 | 624.1095 | 624 | 538.3953 | 496.6591
1835.3479 | 621.2424 | 627.6411 | 536.2874 | 499.6388
1836.3479 | 620.7941 | 624.7986 | 536.0147 | 499.2511
1837.3479 | 619.2532 | 619.7833 | 536.5932 | 498.5161
1838.3479 | 618.7427 | 613.1954 | 536.5868 | 498.2994
1839.3479 | 620.1138 | 613.1246 | 536.6126 | 498.409
1840.3479 | 620.0056 | 611.3236 | 535.3268 | 498.1977
1841.3479 | 620.7182 | 608.7072 | 535.0864 | 498.8872
1842.3479 | 620.4693 | 611.431 | 535.0878 | 496.8091
1843.3479 | 622.0586 | 607.7759 | 535.4951 | 495.5119
1844.3479 | 622.0671 | 606.3569 | 534.2433 | 496.0632
1845.3479 | 622.0184 | 602.961 | 532.9991 | 496.6303
1846.3479 | 621.2769 | 601.4352 | 533.1602 | 495.4351
1847.3479 | 621.0633 | 602.509 | 534.409 | 496.9856
1848.3479 | 619.8492 | 621.5657 | 529.784 | 496.8848
1849.3479 | 618.6577 | 629.4141 | 528.2821 | 496.5058
1850.3479 | 620.788 | 633.0609 | 525.9493 | 494.5147
1851.3479 | 619.6687 | 638.7687 | 526.3916 | 492.8576
1852.3479 | 619.4566 | 641.8965 | 527.1312 | 492.6004
1853.3479 | 619.8177 | 635.6747 | 528.3813 | 492.7734
1854.3479 | 618.5653 | 631.4105 | 530.2893 | 491.2603
1855.3479 | 616.937 | 626.533 | 531.683 | 491.4844
1856.3479 | 618.118 | 622.9445 | 530.6745 | 491.7693
1857.3479 | 618.6571 | 618.1386 | 532.9656 | 491.0553
1858.3479 | 615.2601 | 625.3866 | 533.0123 | 490.0552
1859.3479 | 615.3705 | 623.6104 | 534.0063 | 489.6575
1860.3479 | 617.065 | 621.956 | 532.8446 | 489.9445
1861.3479 | 618.9468 | 616.8284 | 534.6072 | 490.3906
1862.3479 | 620.7383 | 610.6525 | 536.3392 | 490.0934
1863.3479 | 621.2283 | 615.2527 | 536.6108 | 489.822
1864.3479 | 622.7535 | 611.0821 | 535.7211 | 489.2892
1865.3479 | 623.7618 | 607.0477 | 536.2839 | 489.251
1866.3479 | 623.5787 | 613.9438 | 537.4582 | 489.5676
1867.3479 | 625.6741 | 616.1146 | 535.5239 | 488.8489
1868.3479 | 625.9702 | 627.9038 | 533.8471 | 488.2588
1869.3479 | 627.2985 | 625.4419 | 532.4682 | 488.0698
1870.3479 | 627.5546 | 626.0963 | 534.1167 | 490.4344
1871.3479 | 626.2993 | 632.3616 | 534.599 | 489.7775
1872.3479 | 623.9872 | 638.2436 | 535.238 | 489.4004
1873.3479 | 624.9899 | 643.582 | 533.3714 | 489.0872
1874.3479 | 626.0592 | 650.7753 | 530.3176 | 487.4391
1875.3479 | 625.2357 | 667.0401 | 529.3909 | 489.9496
1876.3479 | 625.2993 | 661.64 | 529.4822 | 489.4448
1877.3479 | 624.1256 | 652.2028 | 530.9107 | 493.2938
1878.3479 | 626.0317 | 648.3496 | 532.0134 | 492.1833
1879.3479 | 625.6811 | 668.2466 | 532.7588 | 493.0867
1880.3479 | 623.7307 | 664.9598 | 532.6916 | 491.5282
1881.3479 | 623.6677 | 658.3212 | 531.1433 | 490.6098
1882.3479 | 623.9394 | 652.8709 | 529.2903 | 491.2851
1883.3479 | 624.2265 | 661.6257 | 529.4982 | 491.0817
1884.3479 | 623.8651 | 666.9024 | 529.4452 | 490.3702
1885.3479 | 620.6214 | 661.1666 | 529.1228 | 488.7674
1886.3479 | 619.8955 | 655.9032 | 527.9213 | 488.021
1887.3479 | 617.8822 | 652.3339 | 530.1182 | 486.6946
1888.3479 | 617.3146 | 662.7215 | 533.8677 | 486.0489
1889.3479 | 619.3276 | 661.7988 | 534.9801 | 485.9496
1890.3479 | 618.9232 | 659.9922 | 534.9718 | 485.2964
1891.3479 | 619.5726 | 661.2641 | 537.7597 | 484.9354
1892.3479 | 619.5397 | 656.8392 | 539.1838 | 484.9386
1893.3479 | 616.8727 | 662.5713 | 539.5499 | 483.5736
1894.3479 | 615.8394 | 656.2915 | 541.5057 | 482.8687
1895.3479 | 617.5233 | 650.0098 | 542.1768 | 483.0237
1896.3479 | 619.8542 | 642.7952 | 542.0309 | 481.9254
1897.3479 | 621.9717 | 636.095 | 541.8525 | 480.8019
1898.3479 | 622.5767 | 640.7397 | 542.2478 | 480.9977
1899.3479 | 623.3577 | 634.5514 | 541.6185 | 479.5681
1900.3479 | 623.4974 | 641.6194 | 539.379 | 478.4752
1901.3479 | 625.8456 | 659.8475 | 538.1492 | 477.5526
1902.3479 | 626.3274 | 649.8319 | 538.6566 | 477.0266
1903.3479 | 625.0001 | 643.7364 | 538.7112 | 475.8489
1904.3479 | 622.9729 | 636.2874 | 538.1408 | 474.173
1905.3479 | 620.7956 | 632.8165 | 538.8852 | 473.281
1906.3479 | 619.5735 | 633.3633 | 539.0869 | 473.0388
1907.3479 | 622.1923 | 634.6226 | 539.8585 | 473.1719
1908.3479 | 621.0299 | 637.911 | 538.7835 | 472.823
1909.3479 | 623.6998 | 630.3924 | 538.2463 | 472.5109
1910.3479 | 623.5039 | 635.0904 | 538.1789 | 471.5193
1911.3479 | 622.1737 | 631.6224 | 537.4326 | 470.9568
1912.3479 | 621.277 | 626.5055 | 537.0231 | 470.934
1913.3479 | 618.2032 | 619.1656 | 535.7569 | 471.1014
1914.3479 | 614.9396 | 622.6937 | 533.6043 | 470.6789
1915.3479 | 614.5963 | 627.4052 | 533.6872 | 470.0275
1916.3479 | 613.8242 | 630.9806 | 530.9582 | 469.0594
1917.3479 | 616.3673 | 630.9871 | 532.6866 | 468.4144
1918.3479 | 615.4319 | 633.4931 | 533.302 | 468.0684
1919.3479 | 619.4637 | 629.8828 | 534.8601 | 468.085
1920.3479 | 620.2835 | 628.6977 | 534.3789 | 468.1787
1921.3479 | 620.3218 | 633.8386 | 532.5888 | 467.6149
1922.3479 | 622.7197 | 638.5308 | 530.3328 | 467.492
1923.3479 | 624.2063 | 641.2198 | 530.2976 | 467.6304
1924.3479 | 625.3707 | 646.1704 | 531.7965 | 467.7861
1925.3479 | 625.3293 | 651.7599 | 533.6487 | 468.6566
1926.3479 | 625.5767 | 645.8318 | 534.4149 | 472.1468
1927.3479 | 625.4419 | 637.0165 | 535.5078 | 472.7371
1928.3479 | 623.5968 | 633.2762 | 535.4792 | 474.0707
1929.3479 | 623.5967 | 630.216 | 536.5504 | 473.7523
1930.3479 | 621.0344 | 626.2259 | 535.6193 | 472.5548
1931.3479 | 622.8289 | 621.4285 | 535.1204 | 473.4496
1932.3479 | 622.7661 | 616.9482 | 535.5051 | 472.7381
1933.3479 | 623.4138 | 615.2669 | 535.5927 | 472.7871
1934.3479 | 624.3393 | 612.6736 | 537.5436 | 471.5463
1935.3479 | 624.0383 | 609.6865 | 537.0215 | 471.5252
1936.3479 | 626.9727 | 614.4149 | 535.9696 | 471.9475
1937.3479 | 626.8415 | 620.1055 | 535.0995 | 472.6141
1938.3479 | 627.5734 | 620.2958 | 534.7128 | 473.4556
1939.3479 | 626.8867 | 633.9809 | 531.7069 | 473.0487
1940.3479 | 626.5728 | 651.5166 | 531.069 | 472.4355
1941.3479 | 626.3237 | 651.8182 | 531.9726 | 472.1558
1942.3479 | 625.3852 | 655.03 | 532.7832 | 474.0134
1943.3479 | 625.2182 | 652.8822 | 532.6115 | 473.6985
1944.3479 | 625.0522 | 657.2292 | 532.0415 | 472.9199
1945.3479 | 622.232 | 654.8001 | 533.1864 | 474.3458
1946.3479 | 621.3362 | 647.6264 | 534.1121 | 474.2677
1947.3479 | 621.838 | 644.8709 | 536.1252 | 474.0636
1948.3479 | 622.9398 | 644.0638 | 536.0744 | 472.5055
1949.3479 | 620.1892 | 647.4328 | 537.6693 | 472.559
1950.3479 | 622.6092 | 642.2788 | 536.0885 | 471.2786
1951.3479 | 619.8361 | 637.5833 | 536.5136 | 471.4194
1952.3479 | 622.3611 | 643.0832 | 537.2337 | 471.2434
1953.3479 | 622.608 | 641.7601 | 536.3999 | 470.9908
1954.3479 | 622.4008 | 647.65 | 537.2417 | 471.3614
1955.3479 | 622.0251 | 648.9798 | 538.1028 | 471.4204
1956.3479 | 621.2928 | 645.9123 | 539.2471 | 470.1796
1957.3479 | 622.3059 | 640.5681 | 538.0483 | 471.3845
1958.3479 | 624.5567 | 637.8164 | 538.219 | 473.4388
1959.3479 | 624.198 | 634.5912 | 537.8117 | 471.6391
1960.3479 | 625.4188 | 634.5572 | 538.3823 | 471.0848
1961.3479 | 626.6442 | 636.1324 | 539.4015 | 470.338
1962.3479 | 626.328 | 635.2803 | 540.7444 | 470.3187
1963.3479 | 626.5171 | 629.5282 | 541.5491 | 473.8712
1964.3479 | 627.5525 | 622.4063 | 540.6398 | 473.6999
1965.3479 | 628.2826 | 626.8805 | 539.5094 | 472.3208
1966.3479 | 629.21 | 629.9383 | 540.8336 | 474.4866
1967.3479 | 629.3561 | 625.8038 | 539.4882 | 474.4715
1968.3479 | 629.6136 | 623.3461 | 539.1438 | 472.912
1969.3479 | 631.8786 | 622.3351 | 537.804 | 473.0229
1970.3479 | 632.6912 | 633.0797 | 538.5563 | 473.8587
1971.3479 | 632.0464 | 635.7074 | 536.507 | 472.8284
1972.3479 | 629.096 | 642.3577 | 535.1623 | 472.6539
1973.3479 | 630.9464 | 634.1271 | 535.7093 | 474.4097
1974.3479 | 630.8825 | 632.0811 | 537.7656 | 474.8957
1975.3479 | 630.6638 | 631.8882 | 537.1228 | 473.9992
1976.3479 | 630.6869 | 626.1522 | 539.0691 | 475.2645
1977.3479 | 630.424 | 629.1547 | 539.7685 | 474.9968
1978.3479 | 628.8326 | 625.7426 | 539.1732 | 475.403
1979.3479 | 626.8439 | 626.0599 | 540.3077 | 474.5556
1980.3479 | 627.3896 | 626.1652 | 540.5558 | 475.375
1981.3479 | 625.6876 | 622.4291 | 541.3959 | 474.5494
1982.3479 | 624.3915 | 617.2679 | 540.6514 | 474.3591
1983.3479 | 623.3233 | 612.5498 | 539.3796 | 473.5596
1984.3479 | 624.0956 | 610.5267 | 539.9534 | 473.2058
1985.3479 | 625.5543 | 622.0498 | 538.4639 | 472.9117
1986.3479 | 626.0547 | 616.8935 | 540.3074 | 473.4153
1987.3479 | 627.3362 | 618.6902 | 540.6166 | 472.4056
1988.3479 | 628.802 | 621.2845 | 538.6968 | 473.0433
1989.3479 | 628.9978 | 624.2193 | 539.0927 | 473.8073
1990.3479 | 627.6309 | 622.1433 | 540.037 | 473.9733
1991.3479 | 628.4186 | 622.9391 | 540.8517 | 473.7833
1992.3479 | 628.406 | 616.8387 | 539.6913 | 473.7016
1993.3479 | 629.5126 | 610.7949 | 539.3067 | 472.5542
1994.3479 | 630.3979 | 604.9307 | 539.2796 | 471.7114
1995.3479 | 630.6141 | 602.8481 | 538.8617 | 471.7345
1996.3479 | 632.0822 | 598.5811 | 538.5801 | 472.4861
1997.3479 | 632.3518 | 595.1869 | 538.5093 | 471.4497
1998.3479 | 632.9937 | 593.2906 | 537.5386 | 470.4474
1999.3479 | 631.2018 | 590.6373 | 537.1357 | 471.159
2000.3479 | 633.3756 | 588.219 | 539.765 | 471.762
2001.3479 | 632.5394 | 583.8855 | 541.58 | 472.1924
2002.3479 | 633.6559 | 581.573 | 540.8427 | 472.2957
2003.3479 | 633.2752 | 579.928 | 539.4709 | 471.0321
2004.3479 | 633.1549 | 579.4957 | 539.9895 | 475.7301
2005.3479 | 633.1058 | 577.3798 | 540.0161 | 476.2982
2006.3479 | 634.8914 | 575.2055 | 540.8918 | 475.5537
2007.3479 | 635.5823 | 572.1324 | 540.6963 | 474.1505
2008.3479 | 635.178 | 569.0541 | 540.4812 | 473.445
2009.3479 | 636.4034 | 567.3916 | 541.22 | 472.986
2010.3479 | 634.725 | 567.1323 | 541.3489 | 473.5149
2011.3479 | 633.1442 | 565.5132 | 540.463 | 473.2132
2012.3479 | 634.2192 | 564.2031 | 541.2665 | 472.3328
2013.3479 | 633.3333 | 564.8629 | 542.632 | 473.0312
2014.3479 | 633.9569 | 563.3948 | 543.6167 | 473.1536
2015.3479 | 632.9106 | 563.2828 | 544.9096 | 472.9027
2016.3479 | 635.3963 | 563.4641 | 543.9403 | 471.4819
2017.3479 | 634.7165 | 561.9411 | 543.8286 | 471.2455
2018.3479 | 635.5203 | 561.122 | 543.5284 | 470.5933
2019.3479 | 636.9794 | 559.5179 | 545.0296 | 471.1552
2020.3479 | 637.5902 | 558.4387 | 545.7084 | 470.6007
2021.3479 | 636.5652 | 557.3921 | 544.0859 | 470.6186
2022.3479 | 635.3033 | 556.0263 | 543.4589 | 470.1979
2023.3479 | 629.7898 | 556.218 | 543.5989 | 471.0805
2024.3479 | 630.5058 | 556.2663 | 542.3384 | 471.8716
2025.3479 | 630.9974 | 555.2099 | 541.5784 | 471.6161
2026.3479 | 632.2056 | 554.9378 | 543.0043 | 471.7879
2027.3479 | 633.5553 | 554.1336 | 542.912 | 470.6293
2028.3479 | 633.5846 | 553.7543 | 541.7798 | 471.1025
2029.3479 | 634.9231 | 552.7853 | 541.2725 | 470.5554
2030.3479 | 636.1933 | 552.8274 | 541.1598 | 471.2177
2031.3479 | 635.6745 | 553.1414 | 541.6305 | 472.2511
2032.3479 | 634.7194 | 551.4698 | 540.7027 | 471.59
2033.3479 | 634.8005 | 551.9592 | 540.7721 | 471.432
2034.3479 | 635.0471 | 551.0335 | 541.4355 | 473.907
2035.3479 | 634.7297 | 550.3026 | 541.3525 | 473.3739
2036.3479 | 631.8417 | 548.8292 | 539.6296 | 472.3988
2037.3479 | 631.9071 | 549.2932 | 538.921 | 472.7352
2038.3479 | 630.9277 | 548.7276 | 539.5214 | 472.6338
2039.3479 | 631.467 | 548.097 | 538.2722 | 471.8509
2040.3479 | 629.7794 | 546.131 | 539.3589 | 470.3605
2041.3479 | 631.1513 | 545.1653 | 539.8098 | 469.6113
2042.3479 | 632.4515 | 545.1491 | 538.3591 | 469.69
2043.3479 | 633.1302 | 546.1848 | 539.8062 | 468.8937
2044.3479 | 634.2693 | 544.8982 | 540.0234 | 469.5389
2045.3479 | 633.6121 | 543.8207 | 541.2111 | 469.1882
2046.3479 | 631.217 | 543.5744 | 540.4491 | 468.9771
2047.3479 | 630.0136 | 543.0917 | 539.9595 | 467.7867
2048.3479 | 631.875 | 542.4204 | 539.3646 | 467.0628
2049.3479 | 633.6816 | 544.4877 | 540.2794 | 466.0302
2050.3479 | 634.3503 | 544.1073 | 538.7723 | 465.8002
2051.3479 | 634.5612 | 543.793 | 539.2067 | 465.4228
2052.3479 | 631.92 | 541.9015 | 536.5752 | 465.6446
2053.3479 | 630.8286 | 542.2904 | 536.2451 | 467.2145
2054.3479 | 630.4324 | 543.1211 | 537.4201 | 466.5762
2055.3479 | 630.3971 | 543.4754 | 535.2232 | 466.5207
2056.3479 | 630.2682 | 543.6103 | 535.4801 | 466.0229
2057.3479 | 630.1779 | 542.803 | 533.0012 | 464.8661
2058.3479 | 631.7178 | 540.7605 | 533.9921 | 464.4702
2059.3479 | 631.5953 | 539.8439 | 535.188 | 464.3657
2060.3479 | 631.3906 | 538.7468 | 534.0398 | 465.1839
2061.3479 | 631.1781 | 536.6437 | 533.5784 | 467.756
2062.3479 | 628.9548 | 535.7054 | 535.9547 | 467.0007
2063.3479 | 628.608 | 533.8233 | 535.5742 | 467.8821
2064.3479 | 628.0634 | 533.0095 | 535.4557 | 467.5054
2065.3479 | 626.3828 | 533.3043 | 535.1732 | 466.9899
2066.3479 | 619.5501 | 534.4157 | 534.7132 | 465.9939
2067.3479 | 616.4896 | 536.8203 | 532.0347 | 465.0052
2068.3479 | 616.397 | 537.4314 | 532.2916 | 464.1007
2069.3479 | 618.622 | 537.3625 | 533.108 | 463.7752
2070.3479 | 615.9395 | 537.2012 | 534.8977 | 463.5514
2071.3479 | 619.5179 | 536.9016 | 533.4479 | 463.4804
2072.3479 | 622.6634 | 538.0161 | 532.1252 | 463.162
2073.3479 | 624.3004 | 538.594 | 533.4197 | 463.2539
2074.3479 | 624.6304 | 538.047 | 532.1151 | 462.8033
2075.3479 | 624.1234 | 538.4356 | 532.1737 | 462.3088
2076.3479 | 624.9476 | 537.6257 | 532.236 | 462.2717
2077.3479 | 625.4264 | 537.0609 | 531.8368 | 461.5458
2078.3479 | 627.1056 | 536.7032 | 533.001 | 461.4341
2079.3479 | 626.3521 | 536.4823 | 532.6856 | 460.959
2080.3479 | 627.5358 | 535.7509 | 531.8106 | 461.1855
2081.3479 | 627.695 | 535.7383 | 530.4795 | 461.7657
2082.3479 | 626.6271 | 535.5772 | 532.0178 | 461.4909
2083.3479 | 626.9821 | 535.3252 | 531.6568 | 462.1836
2084.3479 | 626.2015 | 534.8915 | 530.4894 | 464.0645
2085.3479 | 627.3395 | 533.8675 | 532.0848 | 463.4883
2086.3479 | 627.8923 | 533.7066 | 530.8408 | 463.6405
2087.3479 | 628.2298 | 533.5993 | 530.6273 | 464.1344
2088.3479 | 630.1414 | 533.7627 | 532.4045 | 465.2542
2089.3479 | 629.3037 | 534.4038 | 530.9506 | 464.5108
2090.3479 | 629.987 | 535.0024 | 533.3098 | 463.5748
2091.3479 | 630.2526 | 535.5241 | 534.3328 | 463.1769
2092.3479 | 629.4971 | 534.6888 | 535.9067 | 462.4792
2093.3479 | 626.9553 | 534.1091 | 536.2452 | 461.5088
2094.3479 | 628.905 | 533.6777 | 537.1002 | 460.6051
2095.3479 | 630.0549 | 534.1184 | 537.1769 | 459.9672
2096.3479 | 628.4865 | 534.4894 | 538.3699 | 459.8409
2097.3635 | 626.893 | 533.4745 | 537.8304 | 459.7951
2098.3479 | 627.5003 | 533.2564 | 540.3003 | 459.3767
2099.3479 | 624.2778 | 532.2048 | 542.2568 | 458.728
2100.3479 | 625.3688 | 530.5533 | 541.0526 | 458.3777
2101.3479 | 625.0366 | 529.4568 | 539.9171 | 459.6652
2102.3479 | 625.2205 | 527.8832 | 538.5447 | 458.449
2103.3479 | 621.8098 | 527.7466 | 538.113 | 457.6073
2104.3479 | 621.6089 | 528.7117 | 538.0044 | 457.9021
2105.3479 | 620.2441 | 528.7415 | 538.2766 | 457.7716
2106.3479 | 620.1497 | 528.4229 | 539.183 | 457.5231
2107.3479 | 621.3599 | 527.2465 | 539.3509 | 457.5204
2108.3479 | 621.0481 | 526.6808 | 536.043 | 456.0443
2109.3479 | 622.3658 | 527.0005 | 536.7388 | 455.6245
2110.3479 | 621.7323 | 526.9146 | 537.192 | 455.9908
2111.3479 | 621.91 | 526.9099 | 536.7832 | 457.3671
2112.3479 | 623.4852 | 527.4227 | 536.0811 | 456.6498
2113.3479 | 623.9006 | 527.6643 | 536.3984 | 456.4811
2114.3479 | 626.4326 | 526.1663 | 536.048 | 456.5401
2115.3479 | 627.2908 | 525.6006 | 535.8299 | 456.5773
2116.3479 | 627.2099 | 525.6782 | 534.9672 | 456.7338
2117.3479 | 626.811 | 525.6598 | 535.6052 | 457.0614
2118.3479 | 626.1559 | 525.7977 | 535.7449 | 456.9059
2119.3479 | 626.6567 | 525.2861 | 536.1241 | 456.5927
2120.3479 | 626.5188 | 525.7741 | 537.0012 | 457.2896
2121.3479 | 627.9656 | 525.7264 | 536.8532 | 456.5353
2122.3479 | 628.4843 | 524.9803 | 536.0018 | 455.7173
2123.3479 | 627.6254 | 524.7048 | 534.0004 | 455.3627
2124.3479 | 626.9358 | 523.7978 | 532.7467 | 455.353
2125.3479 | 626.1384 | 523.6615 | 532.5589 | 455.3371
2126.3479 | 624.7006 | 525.0047 | 532.3118 | 455.124
2127.3479 | 622.6319 | 526.2658 | 533.9238 | 455.1697
2128.3479 | 623.4945 | 526.875 | 534.097 | 454.801
2129.3479 | 623.6768 | 527.0279 | 533.4621 | 454.3055
2130.3479 | 622.7955 | 527.1847 | 533.3623 | 455.7547
2131.3479 | 625.7657 | 527.2481 | 536.5994 | 457.3458
2132.3479 | 627.7078 | 528.9249 | 536.9143 | 458.4462
2133.3479 | 628.9126 | 530.2673 | 537.9612 | 458.4213
2134.3479 | 631.4002 | 529.9458 | 540.9837 | 458.9428
2135.3479 | 632.2149 | 531.3 | 543.3435 | 459.2044
2136.3479 | 634.6321 | 532.5014 | 544.1329 | 458.9888
2137.3479 | 636.047 | 533.0067 | 546.7801 | 459.9344
2138.3479 | 639.5274 | 534.6946 | 547.7034 | 460.8081
2139.3479 | 640.8666 | 535.5909 | 550.2437 | 461.1426
2140.3479 | 642.2911 | 537.4109 | 554.1695 | 461.0086
2141.3479 | 642.7422 | 538.2833 | 557.0293 | 461.8076
2142.3479 | 643.5856 | 538.5252 | 556.3255 | 461.8647
2143.3479 | 641.6653 | 539.6291 | 556.8316 | 462.0417
2144.3479 | 642.4414 | 540.8914 | 557.2537 | 461.9709
2145.3479 | 641.7228 | 541.7791 | 557.7367 | 461.925
2146.3479 | 640.8125 | 542.1476 | 559.3251 | 462.8069
2147.3479 | 640.4426 | 541.9423 | 562.4008 | 465.4153
2148.3479 | 640.8272 | 541.7206 | 560.5711 | 464.7217
2149.3479 | 640.5258 | 543.1132 | 563.1369 | 465.1214
2150.3479 | 640.5345 | 545.1124 | 562.5118 | 465.1671
2151.3479 | 640.5551 | 545.8396 | 563.2454 | 466.6693
2152.3479 | 641.3992 | 545.253 | 562.7281 | 467.4351
2153.3479 | 641.8131 | 545.9932 | 564.5237 | 468.0871
2154.3479 | 643.1106 | 544.1695 | 565.2408 | 468.0122
2155.3479 | 644.3491 | 544.5773 | 564.9807 | 467.3653
2156.3479 | 645.8404 | 543.4389 | 564.5646 | 466.4678
2157.3479 | 643.3545 | 543.6011 | 566.5806 | 465.9394
2158.3479 | 643.5889 | 542.9832 | 566.1147 | 465.8419
2159.3479 | 642.6535 | 542.7648 | 565.5283 | 464.8885
2160.3479 | 643.8546 | 543.2975 | 566.0979 | 464.977
2161.3479 | 645.5304 | 543.579 | 566.9142 | 465.2959
2162.3479 | 644.738 | 543.3627 | 567.9885 | 464.5043
2163.3479 | 642.389 | 545.0527 | 569.1555 | 464.4957
2164.3479 | 643.3112 | 544.7333 | 568.9417 | 464.2452
2165.3479 | 643.2521 | 543.6856 | 568.8056 | 464.9829
2166.3479 | 644.82 | 543.3485 | 568.1145 | 465.2066
2167.3479 | 644.9061 | 542.6872 | 569.0898 | 464.9383
2168.3479 | 646.4255 | 542.7877 | 571.1033 | 464.8066
2169.3479 | 647.4482 | 542.1395 | 571.7756 | 465.1409
2170.3479 | 645.6683 | 541.3076 | 571.9314 | 464.7088
2171.3479 | 645.2518 | 541.2469 | 571.7681 | 464.7669
2172.3479 | 644.8938 | 540.6654 | 569.4487 | 465.0727
2173.3479 | 643.9048 | 539.3814 | 567.336 | 465.9633
2174.3479 | 644.8195 | 538.2072 | 566.3833 | 467.0586
2175.3479 | 641.6449 | 536.4931 | 565.8132 | 469.8758
2176.3479 | 642.4949 | 535.4328 | 569.0507 | 470.9723
2177.3479 | 641.2401 | 534.2711 | 569.063 | 471.4734
2178.3479 | 639.4945 | 534.2382 | 569.4297 | 474.3219
2179.3479 | 638.5995 | 532.6649 | 568.0146 | 474.694
2180.3479 | 636.2997 | 530.5942 | 567.0471 | 473.906
2181.3479 | 635.5894 | 530.074 | 567.8881 | 473.3358
2182.3479 | 636.6868 | 529.812 | 566.4579 | 472.5125
2183.3479 | 637.4386 | 529.6237 | 565.5232 | 471.733
2184.3479 | 638.5343 | 529.383 | 565.8103 | 471.2476
2185.3479 | 639.3476 | 529.155 | 565.5695 | 470.9516
2186.3479 | 638.5786 | 529.0552 | 566.1218 | 469.8811
2187.3479 | 638.6719 | 529.6633 | 563.8081 | 468.2519
2188.3479 | 638.1967 | 530.3776 | 563.5236 | 467.7831
2189.3479 | 639.9541 | 530.2185 | 563.2496 | 467.3586
2190.3479 | 641.8596 | 531.1867 | 563.0345 | 466.4518
2191.3479 | 640.0329 | 532.7782 | 561.4523 | 465.8667
2192.3479 | 641.6853 | 532.7635 | 558.7232 | 465.8308
2193.3479 | 641.4909 | 532.2441 | 559.0016 | 465.6585
2194.3479 | 641.9316 | 532.0208 | 561.0643 | 465.1397
2195.3479 | 642.4826 | 533.1593 | 562.5412 | 464.5436
2196.3479 | 640.421 | 534.312 | 563.8674 | 464.3354
2197.3479 | 639.3391 | 535.0685 | 565.1765 | 464.3141
2198.3635 | 641.6782 | 535.3207 | 567.0823 | 464.1694
2199.3479 | 640.899 | 535.5423 | 566.2195 | 464.6763
2200.3479 | 642.8719 | 535.9568 | 563.5497 | 463.5662
2201.3479 | 641.9789 | 536.9258 | 563.141 | 462.8354
2202.3479 | 644.7622 | 538.193 | 561.2382 | 463.1665
2203.3479 | 644.7649 | 539.0939 | 561.1023 | 462.6947
2204.3479 | 645.5915 | 539.462 | 561.9408 | 463.9197
2205.3479 | 643.5072 | 538.5054 | 561.8086 | 463.4681
2206.3479 | 643.9662 | 539.475 | 562.362 | 462.1518
2207.3479 | 644.4413 | 538.9102 | 561.6394 | 463.3586
2208.3479 | 643.4199 | 538.2064 | 560.28 | 462.6432
2209.3479 | 644.644 | 538.4975 | 560.6936 | 462.027
2210.3479 | 644.9499 | 537.8021 | 560.5077 | 464.0535
2211.3479 | 645.0487 | 536.7551 | 562.2902 | 464.8294
2212.3479 | 643.0472 | 535.7657 | 564.1303 | 466.0709
2213.3479 | 643.3874 | 535.1973 | 564.1181 | 465.55
2214.3479 | 643.2313 | 534.5612 | 564.7147 | 464.8741
2215.3479 | 640.5777 | 535.4337 | 565.6267 | 463.9938
2216.3479 | 641.7877 | 535.8202 | 564.7389 | 463.2743
2217.3479 | 641.9229 | 535.541 | 563.3608 | 463.5026
2218.3479 | 641.3144 | 536.367 | 563.5379 | 462.4834
2219.3479 | 641.9269 | 537.1586 | 564.9434 | 461.8078
2220.3479 | 638.753 | 537.6314 | 565.2082 | 461.3886
2221.3479 | 636.1933 | 539.4852 | 566.0455 | 460.5763
2222.3479 | 639.2059 | 540.1993 | 566.5615 | 460.5565
2223.3479 | 641.2722 | 540.2483 | 567.9116 | 460.5008
2224.3479 | 640.0437 | 541.2365 | 567.9082 | 459.7867
2225.3479 | 639.1511 | 542.0881 | 567.8779 | 459.0387
2226.3479 | 633.9296 | 542.4259 | 568.401 | 459.3427
2227.3479 | 632.7018 | 544.1215 | 568.6945 | 458.5025
2228.3479 | 632.3979 | 545.219 | 566.4193 | 457.5845
2229.3479 | 634.6931 | 544.3884 | 564.3442 | 456.9067
2230.3479 | 635.5865 | 543.6999 | 561.5669 | 456.5383
2231.3479 | 637.6984 | 541.802 | 559.642 | 456.8857
2232.3479 | 636.2459 | 540.7826 | 559.3117 | 456.3631
2233.3479 | 638.9551 | 540.0591 | 559.4974 | 456.0067
2234.3479 | 640.3934 | 539.2563 | 559.234 | 455.9875
2235.3479 | 639.8429 | 538.9609 | 561.4133 | 458.2193
2236.3479 | 637.8443 | 539.6799 | 562.8197 | 458.7837
2237.3479 | 634.8416 | 540.0153 | 562.1946 | 457.6692
2238.3479 | 634.8402 | 540.2204 | 563.233 | 457.712
2239.3479 | 635.7632 | 540.4183 | 564.1484 | 457.3552
2240.3479 | 634.4702 | 541.5581 | 564.7306 | 457.1853
2241.3479 | 634.2642 | 542.4546 | 564.0893 | 456.2727
2242.3479 | 635.7608 | 543.0566 | 563.0962 | 456.2584
2243.3479 | 634.5125 | 542.2687 | 564.1452 | 457.7134
2244.3479 | 634.7965 | 541.8832 | 564.0856 | 457.4675
2245.3479 | 634.2793 | 541.7146 | 563.8618 | 457.5963
2246.3479 | 633.4708 | 540.8808 | 562.7188 | 457.781
2247.3479 | 632.7216 | 540.9587 | 562.2464 | 458.2859
2248.3479 | 629.8351 | 541.6224 | 563.9708 | 458.5386
2249.3479 | 629.9512 | 542.263 | 563.2135 | 457.6853
2250.3479 | 632.4951 | 541.6568 | 562.3909 | 456.8619
2251.3479 | 635.0883 | 540.7886 | 560.0216 | 456.4041
2252.3479 | 636.4822 | 540.0463 | 562.0692 | 457.0133
2253.3479 | 637.8897 | 539.9952 | 561.2039 | 455.9008
2254.3479 | 637.408 | 541.0684 | 560.0593 | 455.575
2255.3479 | 639.1898 | 541.5167 | 560.6857 | 455.2383
2256.3479 | 636.775 | 542.7054 | 559.6623 | 455.219
2257.3479 | 636.998 | 542.8553 | 560.6137 | 455.0493
2258.3479 | 634.9814 | 543.3323 | 564.1246 | 456.0962
2259.3479 | 636.7963 | 544.5079 | 563.7857 | 455.8068
2260.3479 | 639.0427 | 544.4575 | 564.991 | 456.7695
2261.3479 | 640.7342 | 543.8106 | 566.0711 | 458.4431
2262.3479 | 642.3569 | 542.1585 | 566.3163 | 458.7999
2263.3479 | 640.4208 | 542.363 | 568.3339 | 458.7697
2264.3479 | 640.6162 | 542.2652 | 568.4906 | 458.2662
2265.3479 | 639.7767 | 542.5818 | 568.3412 | 458.4403
2266.3479 | 643.5934 | 542.4672 | 569.8169 | 458.9269
2267.3479 | 644.6585 | 543.539 | 568.0054 | 459.5087
2268.3479 | 644.0615 | 543.8273 | 567.4979 | 458.6936
2269.3479 | 644.6013 | 545.3296 | 568.4906 | 458.5071
2270.3479 | 645.5837 | 546.1518 | 571.8969 | 458.7746
2271.3479 | 646.2107 | 546.6436 | 571.1194 | 458.729
2272.3479 | 647.3657 | 546.8022 | 570.1081 | 458.694
2273.3479 | 645.9723 | 546.2111 | 569.2442 | 458.871
2274.3479 | 646.0198 | 545.056 | 568.0028 | 460.9855
2275.3479 | 646.8057 | 543.7218 | 568.3746 | 460.9797
2276.3479 | 645.2387 | 543.1993 | 568.7895 | 461.1492
2277.3479 | 644.6495 | 543.1888 | 568.55 | 460.6769
2278.3479 | 646.0681 | 543.5836 | 568.2186 | 460.3056
2279.3479 | 645.4747 | 543.7705 | 567.8395 | 460.8136
2280.3479 | 647.976 | 544.1625 | 564.4589 | 459.775
2281.3479 | 651.6488 | 545.069 | 564.8208 | 460.1089
2282.3479 | 651.9686 | 546.946 | 566.6861 | 459.7549
2283.3479 | 654.4149 | 547.5518 | 568.3086 | 460.0922
2284.3479 | 656.2599 | 547.7097 | 568.4042 | 460.9853
2285.3479 | 657.9366 | 548.138 | 569.3877 | 460.4071
2286.3479 | 658.9817 | 547.3065 | 569.7854 | 460.8557
2287.3479 | 657.0391 | 547.4165 | 568.6729 | 460.3726
2288.3479 | 657.7453 | 546.914 | 567.4056 | 460.8283
2289.3479 | 656.79 | 546.0609 | 568.7773 | 460.6081
2290.3479 | 654.931 | 545.6677 | 570.7133 | 461.1722
2291.3479 | 654.2487 | 545.0212 | 571.9746 | 464.3903
2292.3479 | 652.0066 | 544.5836 | 570.5217 | 466.4749
2293.3479 | 649.9624 | 544.3136 | 571.9031 | 467.3443
2294.3479 | 647.468 | 543.3273 | 571.0473 | 467.2607
2295.3479 | 647.4895 | 542.512 | 569.7543 | 468.7905
2296.3479 | 647.8745 | 541.0593 | 568.5624 | 469.4018
2297.3479 | 648.1755 | 539.5852 | 569.5475 | 470.2149
2298.3479 | 648.5087 | 538.6358 | 569.5471 | 469.4465
2299.3479 | 650.1413 | 539.823 | 569.7528 | 470.0568
2300.3479 | 650.7851 | 540.2478 | 568.4391 | 471.5615
2301.3479 | 650.0814 | 539.2392 | 569.0506 | 474.2283
2302.3479 | 649.4227 | 538.1556 | 568.0848 | 472.9392
2303.3479 | 649.5544 | 538.1236 | 566.7455 | 471.3417
2304.3479 | 649.1597 | 538.1467 | 567.2964 | 470.3163
2305.3479 | 648.2931 | 537.6477 | 567.5085 | 469.2663
2306.3479 | 646.9138 | 537.3054 | 567.8566 | 469.5107
2307.3479 | 647.5489 | 538.0718 | 568.4895 | 468.9908
2308.3479 | 648.5253 | 539.4471 | 568.4719 | 468.2059
2309.3479 | 649.0616 | 540.6772 | 568.8404 | 467.8906
2310.3479 | 648.3805 | 540.673 | 569.2103 | 468.6794
2311.3479 | 649.1898 | 539.8899 | 571.1203 | 468.7392
2312.3479 | 650.9335 | 540.8674 | 571.0027 | 468.1283
2313.3479 | 651.3927 | 540.7374 | 570.6447 | 468.2748
2314.3479 | 652.4307 | 540.6853 | 571.5079 | 467.4145
2315.3479 | 650.2852 | 542.4227 | 572.9489 | 466.3729
2316.3479 | 651.8888 | 543.9996 | 571.1352 | 465.1856
2317.3479 | 652.0915 | 544.7534 | 569.023 | 464.7435
2318.3479 | 652.6489 | 544.6924 | 568.9707 | 464.4087
2319.3479 | 651.0401 | 543.3197 | 571.3679 | 464.1595
2320.3479 | 652.3019 | 542.9258 | 571.5936 | 463.4479
2321.3479 | 648.7869 | 544.0023 | 571.0537 | 462.6893
2322.3479 | 647.3393 | 544.8621 | 570.1793 | 461.4619
2323.3479 | 649.9941 | 545.474 | 565.2591 | 460.6117
2324.3479 | 652.9565 | 547.3377 | 565.9304 | 460.3293
2325.3479 | 652.3853 | 548.5731 | 565.3244 | 459.8356
2326.3479 | 653.6896 | 549.3297 | 565.1204 | 459.2687
2327.3479 | 653.7492 | 549.7368 | 566.0205 | 458.9421
2328.3479 | 653.2166 | 550.0133 | 566.8806 | 460.179
2329.3479 | 652.4443 | 549.0479 | 568.2847 | 461.6067
2330.3479 | 650.5219 | 547.3733 | 569.4538 | 463.6419
2331.3479 | 651.9623 | 545.9882 | 568.6768 | 465.8158
2332.3479 | 650.1334 | 544.8838 | 569.2979 | 466.2726
2333.3479 | 649.2755 | 545.0371 | 569.1631 | 465.4485
2334.3479 | 648.0255 | 545.1149 | 569.28 | 466.677
2335.3479 | 648.9529 | 544.3818 | 569.1407 | 467.4341
2336.3479 | 647.0824 | 543.9943 | 569.8967 | 467.7319
2337.3479 | 644.3106 | 543.7441 | 570.8719 | 468.8835
2338.3479 | 644.57 | 543.3472 | 570.6308 | 468.4616
2339.3479 | 642.8805 | 543.7993 | 569.4259 | 467.729
2340.3479 | 641.9413 | 544.8407 | 568.9009 | 467.5664
2341.3479 | 642.0839 | 544.2909 | 570.6445 | 468.7007
2342.3479 | 644.4787 | 542.7567 | 570.8144 | 469.3831
2343.3479 | 645.4338 | 542.2156 | 571.575 | 469.4765
2344.3479 | 645.8988 | 542.312 | 571.9903 | 469.7277
2345.3479 | 642.6486 | 541.6728 | 572.7907 | 470.9577
2346.3479 | 642.7336 | 540.5597 | 572.2168 | 471.5779
2347.3479 | 642.7334 | 540.5387 | 571.42 | 470.7636
2348.3479 | 642.6326 | 540.4028 | 571.9723 | 473.4917
2349.3479 | 642.174 | 540.0463 | 572.4542 | 474.9811
2350.3479 | 642.413 | 538.8835 | 572.7975 | 477.6909
2351.3479 | 642.6359 | 536.7513 | 571.7962 | 477.6492
2352.3479 | 642.9021 | 535.5078 | 571.8531 | 479.1471
2353.3479 | 641.8513 | 535.0856 | 571.618 | 481.5405
2354.3479 | 641.3574 | 534.3077 | 571.1716 | 480.5527
2355.3479 | 642.4802 | 534.3213 | 571.7365 | 480.1873
2356.3479 | 641.0925 | 534.221 | 569.8615 | 478.1496
2357.3479 | 642.4525 | 535.404 | 567.4641 | 476.6185
2358.3479 | 641.9813 | 536.9454 | 568.1555 | 475.3138
2359.3479 | 640.9422 | 537.0288 | 568.5703 | 474.5937
2360.3479 | 638.0061 | 537.05 | 568.5165 | 473.676
2361.3479 | 638.1009 | 537.4584 | 568.3064 | 472.3111
2362.3479 | 637.8888 | 537.4818 | 567.2122 | 470.8117
2363.3479 | 636.483 | 537.512 | 565.3408 | 469.6864
2364.3479 | 637.1772 | 536.8108 | 565.7696 | 469.955
2365.3479 | 637.7666 | 537.3911 | 566.5052 | 469.1072
2366.3479 | 637.1088 | 537.7026 | 564.4071 | 467.9011
2367.3479 | 634.8454 | 538.0807 | 562.3012 | 466.5752
2368.3479 | 634.0343 | 537.588 | 560.6406 | 465.3742
2369.3479 | 637.1658 | 538.0787 | 560.8505 | 464.9127
2370.3479 | 637.6082 | 539.1555 | 560.0885 | 463.5545
2371.3479 | 639.2046 | 540.0836 | 557.3124 | 462.7636
2372.3479 | 639.7101 | 540.1959 | 558.1436 | 462.6037
2373.3479 | 641.7296 | 539.1578 | 560.6616 | 462.6389
2374.3479 | 641.108 | 538.9052 | 562.4215 | 463.2337
2375.3479 | 641.8273 | 537.9771 | 560.9396 | 463.7277
2376.3479 | 642.7445 | 537.5885 | 561.8058 | 464.3149
2377.3479 | 643.1094 | 537.277 | 561.7472 | 464.2329
2378.3635 | 644.207 | 536.7988 | 561.303 | 463.9632
2379.3479 | 645.5585 | 538.0889 | 560.3762 | 462.766
2380.3479 | 640.5725 | 540.3942 | 561.4145 | 463.2138
2381.3479 | 642.6231 | 542.2293 | 565.0538 | 462.5182
2382.3479 | 643.1834 | 541.5432 | 566.1001 | 462.2044
2383.3479 | 644.8078 | 542.1168 | 567.6245 | 462.1032
2384.3479 | 645.3417 | 541.9933 | 566.2842 | 464.2496
2385.3479 | 645.134 | 541.0565 | 569.0827 | 466.3294
2386.3479 | 645.9885 | 540.4597 | 568.3546 | 467.1046
2387.3479 | 646.642 | 540.9641 | 569.0315 | 467.6878
2388.3479 | 649.2196 | 540.9607 | 569.6337 | 467.7416
2389.3479 | 648.6308 | 541.8923 | 570.1485 | 467.3394
2390.3479 | 647.6123 | 542.4249 | 568.6534 | 466.9228
2391.3479 | 646.6611 | 543.2328 | 567.5859 | 465.9539
2392.3479 | 646.3556 | 544.4463 | 566.8835 | 465.0679
2393.3479 | 646.7422 | 545.6081 | 566.7564 | 464.5001
2394.3479 | 647.6438 | 546.3025 | 566.3553 | 463.7331
2395.3479 | 648.9016 | 545.8319 | 565.3549 | 462.575
2396.3479 | 648.3806 | 546.9765 | 566.2847 | 461.4278
2397.3479 | 649.5046 | 546.5073 | 565.3149 | 460.4949
2398.3479 | 651.8038 | 546.7026 | 566.0282 | 460.0586
2399.3479 | 652.8072 | 546.4213 | 565.0673 | 461.8111
2400.3479 | 650.5914 | 544.7421 | 564.0988 | 461.4068