## Test Conditions
DESIREE-FIRE Intermediate Scale Test Number 8 - Circuit Simulator Data Only
Test Date: | 2009-11-17
DCSim DAQ Start Time | 10:35
DCSim Time for Synchronization | 10:38
Heat Source Synchronization | 0:03 | hour:minutes:seconds
Heat Source DAQ Start Time | 10:35
Heat Source Start Time | 11:34
DCSim Offset | 0:59 | hour:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 3565 | seconds
Heat Source Offset | 0:59 | hour:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 3568 | seconds
Heat Source Stop Time | 12:16
Test Duration | 0:42 | hour:minutes:seconds
| 2495 | seconds
CT500 Turns | 2 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 Turns | 5 | 1 or 5
Pre-Test Baseline: | Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
SWGR Close | PE/PVC, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 8, 9, and 10 represents the air temperature 3', 5', and 7' down the cable tray located in E-Position. These are labeled as "E Position - 3'", "E Position - Middle", "E Position - 7'", respectively.
SWGR Trip | PE/PVC, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 8, 9, and 10 represents the air temperature 3', 5', and 7' down the cable tray located in E-Position. These are labeled as "E Position - 3'", "E Position - Middle", "E Position - 7'", respectively.
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | SWGR_CT500 | SWGR-a_CT35_1_PC | SWGR-a_CT35_2_N1 | SWGR-b_CT35_1_PT | SWGR-b_CT35_2_G | SWGR-b_CT35_3_R | SWGR-b_CT35_4_N2 | SWGR-a_VT7_1_C1 | SWGR-a_VTU_1_PC | SWGR-a_VTU_2_N1 | SWGR-b_VT7_1_G | SWGR-b_VT7_2_R | SWGR-b_VT7_3_T | SWGR-b_VT7_4_SP | SWGR-b_VT7_5_SP | SWGR-b_VTU_1_PT | SWGR-b_VTU_2_N2 | {SWGR-C} V(N1) - V(Batt -) | {SWGR-C} V(PC) - V(Batt +) | {SWGR-C} V(C1) - V(Batt +) | {SWGR-T} V(G) - V(Batt -) | {SWGR-T} V(R) - V(Batt +) | {SWGR-T} V(N2) - V(Batt -) | {SWGR-T} V(PT) - V(Batt +) | {SWGR-C} V(C1) - V(N1) | {SWGR-T} V(SP1) - V(Batt -) | {SWGR-T} V(SP2) - V(Batt -) | {SWGR-T} V(R) - V(Batt -) | {SWGR-T} V(PC) - V(Batt -) | {SWGR-T} V(C1) - V(Batt -) | {SWGR-T} V(PT) - V(Batt -) | {SWGR-T} V(T) - V(Batt -) | {SWGR-T} V(N2) - V(Batt -) | {SWGR-C} V(PC) - V(Batt -) | {SWGR-C} V(C1) - V(Batt -) | {SWGR-T} V(T) - V(Batt -) | {SWGR-T} V(R) - V(Batt -) | {SWGR-T} V(PT) - V(Batt -) | {SWGR-C} V(N1) - V(Batt +) | {SWGR-T} V(N2) - V(Batt +)
-1.5156 | 121.7834 | -61.7889 | 59.8022 | -0.25368 | 0.015554 | 0.010692 | 0.0031701 | 0.057531 | -0.0069811 | 0.064044 | -61.8027 | 59.5734 | -61.6425 | -61.8851 | 59.6329 | 0.32044 | 0.44861 | 0.30212 | 59.7702 | -61.8164 | 0.14648 | -0.22888 | -0.013733 | -0.096131 | -0.16937 | -0.027466 | -0.032043 | -0.16022 | 62.2375 | 62.0911 | 121.4218 | 121.3623 | -0.013733 | 121.5591 | 62.1094 | -0.027466 | 121.3623 | -0.013733 | 62.1094 | 121.4218 | 121.5591 | -121.4447 | -121.6187
0.23438 | 121.8613 | -61.7935 | 59.7427 | 0.089645 | 0.016622 | 0.011974 | 0.0070155 | 0.057744 | -0.0063403 | 0.066608 | -61.9263 | 59.4864 | -61.7569 | -62.0453 | 59.4589 | -0.073242 | -0.24719 | -0.3891 | 59.642 | -61.9217 | 0.036621 | -0.25635 | -0.13275 | -0.25177 | -0.28381 | -0.12817 | -0.10071 | -0.16937 | 61.5463 | 61.4044 | 121.2524 | 121.2799 | -0.13275 | 121.4355 | 61.7203 | -0.12817 | 121.2799 | -0.13275 | 61.7203 | 121.2524 | 121.4355 | -121.4996 | -121.6644
1.9844 | 121.8979 | -61.6882 | 59.8434 | 0.0057222 | 0.015981 | 0.016673 | 0.0012475 | 0.058172 | -0.0050585 | 0.067249 | -61.7844 | 59.5505 | -61.5967 | -61.8805 | 59.6741 | 0.15564 | 0.1236 | 0.17395 | 59.7061 | -61.821 | 0.091552 | -0.29297 | -0.096131 | -0.19226 | -0.16937 | -0.13275 | -0.13733 | -0.18768 | 61.8118 | 61.8622 | 121.3623 | 121.2387 | -0.096131 | 121.3943 | 61.8439 | -0.13275 | 121.2387 | -0.096131 | 61.8439 | 121.3623 | 121.3943 | -121.4401 | -121.6644
3.6562 | 121.8567 | -61.7889 | 59.7427 | 0.066757 | 0.01769 | 0.015605 | 0.010006 | 0.058599 | -0.0059131 | 0.06554 | -61.9171 | 59.4635 | -61.7569 | -62.0453 | 59.4589 | -0.068665 | -0.19684 | -0.37994 | 59.6649 | -61.9308 | 0.032043 | -0.27924 | -0.12817 | -0.25635 | -0.28381 | -0.14191 | -0.07782 | -0.16022 | 61.5921 | 61.409 | 121.2479 | 121.2524 | -0.12817 | 121.4539 | 61.7203 | -0.14191 | 121.2524 | -0.12817 | 61.7203 | 121.2479 | 121.4539 | -121.4996 | -121.6736
5.3906 | 121.8704 | -61.7661 | 59.7244 | 0.097275 | 0.017049 | 0.015605 | 0.0063745 | 0.060308 | -0.0052721 | 0.06618 | -61.9537 | 59.4589 | -61.7615 | -62.0453 | 59.4727 | -0.10071 | -0.24719 | -0.42114 | 59.6695 | -61.9217 | 0.004577 | -0.2655 | -0.18768 | -0.27924 | -0.25177 | -0.15564 | -0.054931 | -0.19226 | 61.5189 | 61.3449 | 121.2387 | 121.225 | -0.18768 | 121.4355 | 61.6653 | -0.15564 | 121.225 | -0.18768 | 61.6653 | 121.2387 | 121.4355 | -121.4859 | -121.6461
7.125 | 121.8796 | -61.7615 | 59.761 | 0.13542 | 0.018758 | 0.015819 | 0.0057337 | 0.060949 | -0.0054859 | 0.064258 | -61.9034 | 59.4681 | -61.7386 | -62.0178 | 59.5047 | -0.10071 | -0.3479 | -0.3891 | 59.6603 | -61.9171 | 0.022889 | -0.29297 | -0.14191 | -0.25635 | -0.25635 | -0.15564 | -0.10071 | -0.1648 | 61.4136 | 61.3724 | 121.2662 | 121.2296 | -0.14191 | 121.4218 | 61.6608 | -0.15564 | 121.2296 | -0.14191 | 61.6608 | 121.2662 | 121.4218 | -121.4996 | -121.6782
8.875 | 121.7743 | -61.8073 | 59.7519 | -0.16212 | 0.016622 | 0.011333 | 0.0048791 | 0.060094 | -0.0063403 | 0.06618 | -61.8118 | 59.5688 | -61.6699 | -61.9034 | 59.5963 | 0.27466 | 0.25177 | 0.11902 | 59.7794 | -61.8484 | 0.13733 | -0.1831 | -0.004578 | -0.09613 | -0.15564 | -0.041199 | 0.027466 | -0.14191 | 62.059 | 61.9263 | 121.4035 | 121.376 | -0.004578 | 121.5866 | 62.0819 | -0.041199 | 121.376 | -0.004578 | 62.0819 | 121.4035 | 121.5866 | -121.4218 | -121.6003
10.5469 | 121.8842 | -61.6745 | 59.8251 | 0.097275 | 0.016622 | 0.014537 | 0.0016749 | 0.058385 | -0.0050585 | 0.065326 | -61.7752 | 59.5184 | -61.6516 | -61.8896 | 59.6329 | 0.064087 | -0.07782 | 0 | 59.7107 | -61.8256 | 0.022889 | -0.3067 | -0.10071 | -0.21515 | -0.19226 | -0.15106 | -0.11444 | -0.1236 | 61.5967 | 61.6745 | 121.3074 | 121.1929 | -0.10071 | 121.3852 | 61.7386 | -0.15106 | 121.1929 | -0.10071 | 61.7386 | 121.3074 | 121.3852 | -121.4767 | -121.6507
12.2812 | 121.8796 | -61.7111 | 59.8251 | 0.043869 | 0.016408 | 0.015819 | 0.0018885 | 0.05924 | -0.0065539 | 0.064471 | -61.7889 | 59.5047 | -61.6287 | -61.8896 | 59.6375 | 0.073242 | -0.054932 | 0.018311 | 59.7336 | -61.8393 | 0.082398 | -0.32043 | -0.077819 | -0.17853 | -0.18768 | -0.12817 | -0.091552 | -0.16022 | 61.6562 | 61.7294 | 121.3486 | 121.2158 | -0.077819 | 121.4447 | 61.7844 | -0.12817 | 121.2158 | -0.077819 | 61.7844 | 121.3486 | 121.4447 | -121.4539 | -121.6644
14.0312 | 121.7514 | -61.7294 | 59.8709 | -0.1545 | 0.017263 | 0.014324 | 0.0025293 | 0.054754 | -0.0035631 | 0.06554 | -61.6653 | 59.5596 | -61.5738 | -61.7386 | 59.761 | 0.40741 | 0.3067 | 0.48065 | 59.7519 | -61.7752 | 0.15564 | -0.31128 | 0.064087 | -0.009155 | -0.10986 | -0.045777 | -0.11902 | -0.091552 | 62.0361 | 62.2101 | 121.4905 | 121.2891 | 0.064087 | 121.4813 | 62.1368 | -0.045777 | 121.2891 | 0.064087 | 62.1368 | 121.4905 | 121.4813 | -121.4447 | -121.6461
15.7812 | 121.8338 | -61.734 | 59.7977 | 0.15831 | 0.016408 | 0.014537 | 0.0087243 | 0.057958 | -0.0052721 | 0.067249 | -61.7889 | 59.4315 | -61.7203 | -61.8942 | 59.6008 | -0.009155 | -0.41199 | -0.21057 | 59.6283 | -61.8668 | 0.013733 | -0.36621 | -0.054931 | -0.16022 | -0.19684 | -0.13275 | -0.16937 | -0.068664 | 61.322 | 61.5234 | 121.3348 | 121.1655 | -0.054931 | 121.3623 | 61.7249 | -0.13275 | 121.1655 | -0.054931 | 61.7249 | 121.3348 | 121.3623 | -121.5179 | -121.6644
17.4688 | 121.7468 | -61.8347 | 59.7519 | -0.14687 | 0.016836 | 0.013469 | 0.0089381 | 0.056035 | -0.0056995 | 0.06319 | -61.8118 | 59.5505 | -61.6699 | -61.8988 | 59.5917 | 0.25177 | 0.20142 | 0.086975 | 59.729 | -61.8576 | 0.16479 | -0.20142 | 0.022888 | -0.064087 | -0.16022 | -0.022888 | -0.022888 | -0.14191 | 62.0361 | 61.9217 | 121.4264 | 121.3852 | 0.022888 | 121.5637 | 62.0865 | -0.022888 | 121.3852 | 0.022888 | 62.0865 | 121.4264 | 121.5637 | -121.4218 | -121.6095
19.2188 | 121.875 | -61.6699 | 59.8526 | 0.020981 | 0.017049 | 0.012828 | 0.0021021 | 0.056676 | -0.0035631 | 0.065326 | -61.7752 | 59.5642 | -61.6104 | -61.8668 | 59.6512 | 0.15106 | 0.10071 | 0.14648 | 59.7153 | -61.8393 | 0.059509 | -0.28839 | -0.10529 | -0.19684 | -0.20142 | -0.16937 | -0.13733 | -0.16479 | 61.7706 | 61.8164 | 121.3211 | 121.2341 | -0.10529 | 121.3852 | 61.821 | -0.16937 | 121.2341 | -0.10529 | 61.821 | 121.3211 | 121.3852 | -121.463 | -121.6919
20.8906 | 121.7697 | -61.821 | 59.7427 | -0.1545 | 0.016408 | 0.012615 | 0.0078699 | 0.057317 | -0.0069811 | 0.062976 | -61.8073 | 59.5825 | -61.6699 | -61.8896 | 59.6008 | 0.26093 | 0.23804 | 0.10529 | 59.761 | -61.8393 | 0.15106 | -0.16022 | 0.013733 | -0.068664 | -0.14191 | -0.01831 | 0.01831 | -0.13733 | 62.059 | 61.9263 | 121.4218 | 121.4035 | 0.013733 | 121.582 | 62.0819 | -0.01831 | 121.4035 | 0.013733 | 62.0819 | 121.4218 | 121.582 | -121.4127 | -121.582
22.6406 | 121.756 | -61.8439 | 59.7565 | -0.047684 | 0.014486 | 0.013255 | 0.0078699 | 0.058599 | -0.0044177 | 0.064685 | -61.821 | 59.4864 | -61.7432 | -61.94 | 59.5596 | 0.13275 | -0.10071 | -0.15106 | 59.6603 | -61.8805 | 0.10071 | -0.27008 | 0.022888 | -0.09613 | -0.19684 | -0.036621 | -0.096131 | -0.07782 | 61.7432 | 61.6928 | 121.4035 | 121.3303 | 0.022888 | 121.5042 | 61.9766 | -0.036621 | 121.3303 | 0.022888 | 61.9766 | 121.4035 | 121.5042 | -121.4996 | -121.637
24.3906 | 121.8475 | -61.6608 | 59.8434 | -0.062942 | 0.014699 | 0.013255 | 0.0018885 | 0.056035 | -0.0050585 | 0.067035 | -61.7203 | 59.5963 | -61.5921 | -61.8027 | 59.7198 | 0.29297 | 0.20599 | 0.32959 | 59.7061 | -61.7935 | 0.068665 | -0.24719 | -0.059509 | -0.14191 | -0.1236 | -0.13275 | -0.13733 | -0.12817 | 61.8668 | 61.9904 | 121.3806 | 121.257 | -0.059509 | 121.3669 | 61.9537 | -0.13275 | 121.257 | -0.059509 | 61.9537 | 121.3806 | 121.3669 | -121.4355 | -121.637
26.0625 | 121.8475 | -61.6882 | 59.8434 | -0.070572 | 0.016622 | 0.010478 | 0.0016749 | 0.055822 | -0.0033495 | 0.063617 | -61.734 | 59.5413 | -61.6058 | -61.8027 | 59.7198 | 0.29297 | 0.20142 | 0.32044 | 59.7244 | -61.7798 | 0.082397 | -0.30212 | -0.045777 | -0.11444 | -0.1236 | -0.091553 | -0.11902 | -0.12817 | 61.8896 | 62.0087 | 121.4081 | 121.2296 | -0.045777 | 121.4127 | 61.9812 | -0.091553 | 121.2296 | -0.045777 | 61.9812 | 121.4081 | 121.4127 | -121.4493 | -121.6232
27.8125 | 121.875 | -61.7569 | 59.7336 | 0.12016 | 0.016622 | 0.012401 | 0.0074427 | 0.058385 | -0.0067675 | 0.064899 | -61.8942 | 59.4772 | -61.7615 | -62.0132 | 59.4864 | -0.09613 | -0.34332 | -0.39368 | 59.6786 | -61.9263 | -0.004578 | -0.25635 | -0.13733 | -0.25635 | -0.24719 | -0.16937 | -0.054932 | -0.13275 | 61.4136 | 61.3632 | 121.2433 | 121.2341 | -0.13733 | 121.4355 | 61.6608 | -0.16937 | 121.2341 | -0.13733 | 61.6608 | 121.2433 | 121.4355 | -121.4951 | -121.6599
29.5625 | 121.8384 | -61.7432 | 59.7427 | 0.18883 | 0.017904 | 0.016673 | 0.0089381 | 0.060094 | -0.0054859 | 0.065753 | -61.8896 | 59.4543 | -61.7569 | -61.9812 | 59.523 | -0.073242 | -0.38452 | -0.37079 | 59.6695 | -61.8988 | -0.013733 | -0.28839 | -0.14648 | -0.23804 | -0.21973 | -0.15564 | -0.073242 | -0.13275 | 61.3586 | 61.3724 | 121.2662 | 121.1975 | -0.14648 | 121.4127 | 61.6699 | -0.15564 | 121.1975 | -0.14648 | 61.6699 | 121.2662 | 121.4127 | -121.4996 | -121.6415
31.25 | 121.8887 | -61.6653 | 59.8526 | 0.013352 | 0.017904 | 0.012401 | 0.0023157 | 0.056463 | -0.0020679 | 0.067462 | -61.7844 | 59.5276 | -61.6058 | -61.8668 | 59.6466 | 0.1236 | 0.059509 | 0.11444 | 59.6878 | -61.8164 | 0.059509 | -0.32501 | -0.11902 | -0.20142 | -0.20599 | -0.15106 | -0.1648 | -0.17853 | 61.7249 | 61.7798 | 121.3119 | 121.1929 | -0.11902 | 121.3531 | 61.7889 | -0.15106 | 121.1929 | -0.11902 | 61.7889 | 121.3119 | 121.3531 | -121.4584 | -121.669
33 | 121.788 | -61.8256 | 59.7061 | 0.066757 | 0.016836 | 0.015392 | 0.0095789 | 0.057744 | -0.0065539 | 0.065967 | -61.8988 | 59.4635 | -61.7706 | -61.9949 | 59.4818 | -0.018311 | -0.1831 | -0.32044 | 59.6603 | -61.9171 | 0.054932 | -0.24262 | -0.073242 | -0.16937 | -0.2243 | -0.091552 | -0.045777 | -0.12817 | 61.6425 | 61.5051 | 121.3074 | 121.2891 | -0.073242 | 121.4859 | 61.8073 | -0.091552 | 121.2891 | -0.073242 | 61.8073 | 121.3074 | 121.4859 | -121.4767 | -121.6232
34.6719 | 121.7697 | -61.6974 | 59.8755 | -0.085831 | 0.01534 | 0.013896 | 0.00082026 | 0.058172 | -0.0067675 | 0.065112 | -61.6699 | 59.5734 | -61.5829 | -61.7477 | 59.7473 | 0.37079 | 0.23804 | 0.4303 | 59.7656 | -61.7569 | 0.11444 | -0.30212 | 0.027466 | -0.050354 | -0.12817 | -0.059509 | -0.10986 | -0.086975 | 61.9354 | 62.1277 | 121.4447 | 121.2708 | 0.027466 | 121.463 | 62.0682 | -0.059509 | 121.2708 | 0.027466 | 62.0682 | 121.4447 | 121.463 | -121.4584 | -121.6324
36.4219 | 121.7377 | -61.7111 | 59.8755 | -0.13924 | 0.01769 | 0.014324 | 0.0048791 | 0.057317 | -0.0052721 | 0.064258 | -61.6928 | 59.5413 | -61.5921 | -61.7615 | 59.7244 | 0.41657 | 0.3479 | 0.45319 | 59.7153 | -61.7752 | 0.11902 | -0.33417 | 0.018311 | -0.050354 | -0.15106 | -0.064087 | -0.16022 | -0.10071 | 62.059 | 62.1643 | 121.4355 | 121.2524 | 0.018311 | 121.4264 | 62.1277 | -0.064087 | 121.2524 | 0.018311 | 62.1277 | 121.4355 | 121.4264 | -121.4676 | -121.6507
38.1719 | 121.8658 | -61.6745 | 59.8389 | 0.051498 | 0.017476 | 0.012828 | 0.0018885 | 0.055608 | -0.0061267 | 0.06618 | -61.7569 | 59.5505 | -61.6379 | -61.8301 | 59.6741 | 0.2243 | 0.15564 | 0.23804 | 59.7015 | -61.8118 | 0.036622 | -0.28839 | -0.082397 | -0.15564 | -0.16479 | -0.13733 | -0.13733 | -0.11902 | 61.8301 | 61.9125 | 121.3486 | 121.225 | -0.082397 | 121.376 | 61.8988 | -0.13733 | 121.225 | -0.082397 | 61.8988 | 121.3486 | 121.376 | -121.4767 | -121.6507
39.9062 | 121.7514 | -61.7477 | 59.8389 | -0.18501 | 0.014486 | 0.010478 | 0.0048791 | 0.055608 | -0.0033495 | 0.063831 | -61.702 | 59.5917 | -61.5921 | -61.7752 | 59.7153 | 0.41199 | 0.42114 | 0.44403 | 59.7427 | -61.7981 | 0.15564 | -0.24719 | 0.045777 | -0.027466 | -0.1236 | -0.050354 | -0.09613 | -0.10986 | 62.1689 | 62.1918 | 121.463 | 121.3394 | 0.045777 | 121.4905 | 62.1597 | -0.050354 | 121.3394 | 0.045777 | 62.1597 | 121.463 | 121.4905 | -121.431 | -121.637
41.5938 | 121.8292 | -61.7386 | 59.761 | 0.17357 | 0.016408 | 0.01411 | 0.0082971 | 0.059453 | -0.0048449 | 0.064685 | -61.8393 | 59.4498 | -61.7294 | -61.9034 | 59.5871 | -0.018311 | -0.39825 | -0.25177 | 59.6283 | -61.8988 | 0.009155 | -0.31128 | -0.10071 | -0.1648 | -0.17395 | -0.16022 | -0.13275 | -0.10986 | 61.3403 | 61.4868 | 121.3257 | 121.1884 | -0.10071 | 121.3669 | 61.7203 | -0.16022 | 121.1884 | -0.10071 | 61.7203 | 121.3257 | 121.3669 | -121.4905 | -121.6599
43.3438 | 121.7789 | -61.7844 | 59.7794 | -0.2079 | 0.018545 | 0.0094101 | 0.0057337 | 0.056035 | -0.0031359 | 0.064471 | -61.8027 | 59.5963 | -61.6287 | -61.8759 | 59.6329 | 0.31128 | 0.46692 | 0.27008 | 59.7931 | -61.7889 | 0.15564 | -0.18311 | -0.01831 | -0.091553 | -0.14648 | -0.004577 | 0.013733 | -0.17395 | 62.2513 | 62.0544 | 121.4172 | 121.3806 | -0.01831 | 121.5775 | 62.0956 | -0.004577 | 121.3806 | -0.01831 | 62.0956 | 121.4172 | 121.5775 | -121.4081 | -121.5683
45.0781 | 121.7239 | -61.8256 | 59.7519 | -0.070572 | 0.019613 | 0.0083419 | 0.0085107 | 0.059026 | -0.0082629 | 0.065967 | -61.821 | 59.5276 | -61.702 | -61.8805 | 59.6054 | 0.23346 | 0.10529 | 0.050354 | 59.6832 | -61.8759 | 0.1236 | -0.2243 | 0.004578 | -0.054931 | -0.14648 | -0.050354 | -0.068664 | -0.11902 | 61.9308 | 61.8759 | 121.431 | 121.3531 | 0.004578 | 121.5088 | 62.059 | -0.050354 | 121.3531 | 0.004578 | 62.059 | 121.431 | 121.5088 | -121.4539 | -121.6278
46.75 | 121.8201 | -61.7477 | 59.7839 | 0.074387 | 0.016622 | 0.011333 | 0.0068017 | 0.060308 | -0.0063403 | 0.065326 | -61.7844 | 59.4177 | -61.7523 | -61.8988 | 59.5917 | -0.009155 | -0.40741 | -0.24261 | 59.6237 | -61.853 | -0.004577 | -0.36621 | -0.036621 | -0.15106 | -0.19226 | -0.10528 | -0.16022 | -0.032044 | 61.3403 | 61.5051 | 121.3394 | 121.1655 | -0.036621 | 121.3715 | 61.7386 | -0.10528 | 121.1655 | -0.036621 | 61.7386 | 121.3394 | 121.3715 | -121.5363 | -121.637
48.5 | 121.7514 | -61.8164 | 59.7336 | -0.17738 | 0.018545 | 0.014537 | 0.0063745 | 0.058599 | -0.0065539 | 0.065967 | -61.8118 | 59.5596 | -61.6745 | -61.8942 | 59.6054 | 0.27924 | 0.27008 | 0.11902 | 59.7473 | -61.8347 | 0.14191 | -0.17395 | 0.004577 | -0.07782 | -0.12817 | -0.018311 | 0.013732 | -0.13733 | 62.0865 | 61.9354 | 121.4218 | 121.376 | 0.004577 | 121.5637 | 62.0956 | -0.018311 | 121.376 | 0.004577 | 62.0956 | 121.4218 | 121.5637 | -121.4081 | -121.5683
50.2344 | 121.875 | -61.7752 | 59.7153 | 0.097275 | 0.015554 | 0.016033 | 0.0068017 | 0.058385 | -0.0054859 | 0.065112 | -61.9034 | 59.4635 | -61.7661 | -62.0041 | 59.5001 | -0.091553 | -0.32044 | -0.41199 | 59.61 | -61.9125 | 0.009156 | -0.25177 | -0.12817 | -0.22888 | -0.21515 | -0.13733 | -0.10529 | -0.13733 | 61.4548 | 61.3632 | 121.2753 | 121.2387 | -0.12817 | 121.3852 | 61.6837 | -0.13733 | 121.2387 | -0.12817 | 61.6837 | 121.2753 | 121.3852 | -121.4813 | -121.6278
51.9844 | 121.7606 | -61.6928 | 59.8526 | -0.078201 | 0.01769 | 0.013042 | 0.00082026 | 0.054326 | -0.0046313 | 0.065753 | -61.6882 | 59.5459 | -61.5692 | -61.7661 | 59.7519 | 0.36621 | 0.23804 | 0.43945 | 59.7061 | -61.7661 | 0.1236 | -0.3067 | 0.004578 | -0.073242 | -0.10071 | -0.073242 | -0.14648 | -0.11902 | 61.9308 | 62.1323 | 121.4447 | 121.2387 | 0.004578 | 121.3989 | 62.059 | -0.073242 | 121.2387 | 0.004578 | 62.059 | 121.4447 | 121.3989 | -121.4218 | -121.6187
53.6875 | 121.7468 | -61.7065 | 59.8892 | -0.1545 | 0.014699 | 0.013683 | 0.0027429 | 0.058385 | -0.0042041 | 0.065967 | -61.6562 | 59.5688 | -61.5875 | -61.7294 | 59.7656 | 0.41199 | 0.32959 | 0.48065 | 59.7473 | -61.7432 | 0.11902 | -0.32043 | 0.050354 | -0.022888 | -0.1236 | -0.036621 | -0.14191 | -0.068665 | 62.0361 | 62.1872 | 121.4722 | 121.2753 | 0.050354 | 121.4539 | 62.1185 | -0.036621 | 121.2753 | 0.050354 | 62.1185 | 121.4722 | 121.4539 | -121.4767 | -121.6324
55.4531 | 121.8613 | -61.7706 | 59.6924 | 0.14305 | 0.01769 | 0.015392 | 0.0087243 | 0.058385 | -0.0082629 | 0.06554 | -61.9308 | 59.4406 | -61.7752 | -62.0453 | 59.4589 | -0.11444 | -0.29755 | -0.4303 | 59.6695 | -61.8805 | -0.004578 | -0.25177 | -0.16022 | -0.27466 | -0.23346 | -0.10986 | -0.022888 | -0.15564 | 61.4731 | 61.3403 | 121.2296 | 121.2112 | -0.16022 | 121.4401 | 61.6562 | -0.10986 | 121.2112 | -0.16022 | 61.6562 | 121.2296 | 121.4401 | -121.4676 | -121.5729
57.1406 | 121.7834 | -61.7477 | 59.8022 | -0.26131 | 0.016408 | 0.011546 | 0.0035975 | 0.05689 | -0.0044177 | 0.067035 | -61.7889 | 59.5734 | -61.6425 | -61.8805 | 59.6237 | 0.32501 | 0.45319 | 0.31128 | 59.7839 | -61.7935 | 0.10529 | -0.22888 | -0.041198 | -0.13275 | -0.17853 | -0.045776 | -0.01831 | -0.14648 | 62.2009 | 62.059 | 121.3715 | 121.3211 | -0.041198 | 121.5317 | 62.0728 | -0.045776 | 121.3211 | -0.041198 | 62.0728 | 121.3715 | 121.5317 | -121.4447 | -121.5958
58.8906 | 121.7972 | -61.6928 | 59.8709 | -0.13161 | 0.017476 | 0.014964 | 0.0027429 | 0.056249 | -0.0048449 | 0.063831 | -61.6882 | 59.5779 | -61.5784 | -61.7661 | 59.7382 | 0.34332 | 0.22888 | 0.38452 | 59.7473 | -61.7615 | 0.11444 | -0.29297 | 0.004578 | -0.073242 | -0.13275 | -0.068665 | -0.1236 | -0.10986 | 61.9217 | 62.0773 | 121.431 | 121.2708 | 0.004578 | 121.4401 | 62.0361 | -0.068665 | 121.2708 | 0.004578 | 62.0361 | 121.431 | 121.4401 | -121.4493 | -121.6324
60.625 | 121.843 | -61.6791 | 59.8343 | -0.017166 | 0.016836 | 0.015392 | 0.0033839 | 0.056035 | -0.0048449 | 0.066608 | -61.7477 | 59.5413 | -61.6196 | -61.8347 | 59.6924 | 0.23804 | 0.17395 | 0.24261 | 59.7153 | -61.7844 | 0.059509 | -0.29297 | -0.068665 | -0.15564 | -0.14191 | -0.10529 | -0.11902 | -0.12817 | 61.853 | 61.9217 | 121.3715 | 121.2204 | -0.068665 | 121.3943 | 61.9171 | -0.10529 | 121.2204 | -0.068665 | 61.9171 | 121.3715 | 121.3943 | -121.4539 | -121.6187
62.3594 | 121.7377 | -61.702 | 59.8801 | -0.078201 | 0.018117 | 0.010692 | 0.0053065 | 0.057317 | -0.0044177 | 0.064685 | -61.6653 | 59.5505 | -61.5921 | -61.7249 | 59.761 | 0.39368 | 0.2655 | 0.44403 | 59.7382 | -61.7706 | 0.10986 | -0.32959 | 0.036621 | -0.022889 | -0.11902 | -0.068665 | -0.14191 | -0.073242 | 61.9675 | 62.146 | 121.463 | 121.2524 | 0.036621 | 121.4401 | 62.0956 | -0.068665 | 121.2524 | 0.036621 | 62.0956 | 121.463 | 121.4401 | -121.4722 | -121.6507
64.1094 | 121.843 | -61.7798 | 59.6924 | 0.1049 | 0.018972 | 0.013896 | 0.0093653 | 0.057317 | -0.0061267 | 0.066394 | -61.9354 | 59.4269 | -61.7935 | -62.027 | 59.4315 | -0.10529 | -0.27008 | -0.43945 | 59.6649 | -61.9217 | -0.013733 | -0.2655 | -0.15564 | -0.24719 | -0.26093 | -0.14191 | -0.027466 | -0.14191 | 61.5097 | 61.3403 | 121.2112 | 121.2067 | -0.15564 | 121.4447 | 61.6745 | -0.14191 | 121.2067 | -0.15564 | 61.6745 | 121.2112 | 121.4447 | -121.4859 | -121.6141
65.7969 | 121.8063 | -61.7203 | 59.8068 | 0.16594 | 0.018117 | 0.015178 | 0.0072291 | 0.05924 | -0.0065539 | 0.06554 | -61.7844 | 59.436 | -61.6791 | -61.8668 | 59.6146 | 0.018311 | -0.35248 | -0.16022 | 59.6146 | -61.8622 | 0.041199 | -0.37079 | -0.064087 | -0.14648 | -0.19226 | -0.14191 | -0.19226 | -0.10529 | 61.3678 | 61.5601 | 121.3348 | 121.1563 | -0.064087 | 121.3348 | 61.7386 | -0.14191 | 121.1563 | -0.064087 | 61.7386 | 121.3348 | 121.3348 | -121.4859 | -121.669
67.5469 | 121.7102 | -61.821 | 59.7427 | -0.09346 | 0.016195 | 0.012828 | 0.0095789 | 0.059881 | -0.0046313 | 0.068744 | -61.8027 | 59.5047 | -61.7157 | -61.8988 | 59.5871 | 0.21515 | 0.041199 | -0.004578 | 59.6878 | -61.8622 | 0.10529 | -0.23804 | 0.018311 | -0.07782 | -0.15564 | -0.041199 | -0.054932 | -0.086975 | 61.8622 | 61.8164 | 121.4081 | 121.3257 | 0.018311 | 121.5088 | 62.0361 | -0.041199 | 121.3257 | 0.018311 | 62.0361 | 121.4081 | 121.5088 | -121.4584 | -121.6049
69.2969 | 121.8109 | -61.6974 | 59.7931 | 0.16594 | 0.017263 | 0.013683 | 0.0055201 | 0.05924 | -0.0054859 | 0.065326 | -61.7798 | 59.4498 | -61.6882 | -61.8851 | 59.6054 | 0.004578 | -0.41199 | -0.24261 | 59.6283 | -61.8896 | 0.009156 | -0.34332 | -0.082397 | -0.18768 | -0.18768 | -0.19226 | -0.16479 | -0.091553 | 61.2854 | 61.4548 | 121.3028 | 121.1472 | -0.082397 | 121.3257 | 61.702 | -0.19226 | 121.1472 | -0.082397 | 61.702 | 121.3028 | 121.3257 | -121.4813 | -121.6827
71.0469 | 121.8475 | -61.6653 | 59.8389 | -0.024795 | 0.016408 | 0.012401 | 0.0016749 | 0.058599 | -0.0018543 | 0.064685 | -61.7569 | 59.5413 | -61.6287 | -61.8347 | 59.6695 | 0.21515 | 0.16022 | 0.25177 | 59.7198 | -61.7935 | 0.036621 | -0.29755 | -0.091553 | -0.16937 | -0.16937 | -0.12817 | -0.11902 | -0.12817 | 61.8256 | 61.9171 | 121.3348 | 121.2067 | -0.091553 | 121.3852 | 61.8805 | -0.12817 | 121.2067 | -0.091553 | 61.8805 | 121.3348 | 121.3852 | -121.4676 | -121.6324
72.7188 | 121.7239 | -61.7203 | 59.8572 | -0.19264 | 0.017263 | 0.016033 | 0.0031701 | 0.057104 | -0.0048449 | 0.063831 | -61.6745 | 59.5688 | -61.5646 | -61.7294 | 59.7519 | 0.42114 | 0.33417 | 0.48523 | 59.7336 | -61.7523 | 0.15564 | -0.28839 | 0.045776 | -0.009155 | -0.10529 | -0.032043 | -0.1236 | -0.10986 | 62.0544 | 62.2055 | 121.4722 | 121.2891 | 0.045776 | 121.4539 | 62.1414 | -0.032043 | 121.2891 | 0.045776 | 62.1414 | 121.4722 | 121.4539 | -121.4218 | -121.6095
74.4688 | 121.7056 | -61.8347 | 59.761 | -0.078201 | 0.01769 | 0.012187 | 0.0097925 | 0.05689 | -0.0071947 | 0.066608 | -61.821 | 59.5047 | -61.7203 | -61.9034 | 59.5871 | 0.19226 | 0.018311 | -0.022888 | 59.6832 | -61.8668 | 0.11444 | -0.25635 | 0.013733 | -0.068664 | -0.17395 | -0.032043 | -0.077819 | -0.10071 | 61.853 | 61.8118 | 121.4218 | 121.3394 | 0.013733 | 121.5179 | 62.027 | -0.032043 | 121.3394 | 0.013733 | 62.027 | 121.4218 | 121.5179 | -121.4813 | -121.6278
76.2031 | 121.8246 | -61.734 | 59.7565 | 0.18883 | 0.014913 | 0.01411 | 0.0050929 | 0.058385 | -0.0067675 | 0.067249 | -61.8073 | 59.4452 | -61.7569 | -61.8805 | 59.6008 | -0.013733 | -0.41657 | -0.2655 | 59.6283 | -61.8805 | -0.022888 | -0.31128 | -0.073242 | -0.14648 | -0.15564 | -0.14648 | -0.12817 | -0.050354 | 61.3174 | 61.4685 | 121.3348 | 121.1792 | -0.073242 | 121.3623 | 61.7203 | -0.14648 | 121.1792 | -0.073242 | 61.7203 | 121.3348 | 121.3623 | -121.5134 | -121.637
77.9688 | 121.8796 | -61.6562 | 59.8206 | 0.097275 | 0.016622 | 0.012828 | 0.0021021 | 0.057958 | -0.0042041 | 0.065112 | -61.7752 | 59.5322 | -61.6333 | -61.8896 | 59.6146 | 0.082397 | -0.073242 | 0.004578 | 59.6786 | -61.8027 | 0.022888 | -0.28839 | -0.11902 | -0.23346 | -0.20599 | -0.14648 | -0.14191 | -0.14191 | 61.5829 | 61.6608 | 121.2708 | 121.1884 | -0.11902 | 121.3348 | 61.7386 | -0.14648 | 121.1884 | -0.11902 | 61.7386 | 121.2708 | 121.3348 | -121.4539 | -121.6232
79.6562 | 121.8155 | -61.7111 | 59.8206 | 0.16594 | 0.017049 | 0.0094101 | 0.0070155 | 0.059026 | -0.0061267 | 0.065753 | -61.7844 | 59.4223 | -61.734 | -61.8851 | 59.61 | 0.009155 | -0.40283 | -0.20599 | 59.6054 | -61.8622 | -0.022888 | -0.39825 | -0.073242 | -0.17395 | -0.21057 | -0.15106 | -0.21515 | -0.050354 | 61.3083 | 61.5051 | 121.3211 | 121.1334 | -0.073242 | 121.3165 | 61.7203 | -0.15106 | 121.1334 | -0.073242 | 61.7203 | 121.3211 | 121.3165 | -121.5546 | -121.6827
81.3906 | 121.8201 | -61.7065 | 59.8206 | 0.1049 | 0.015127 | 0.013469 | 0.0033839 | 0.057317 | -0.0037769 | 0.065112 | -61.7798 | 59.4772 | -61.6699 | -61.8713 | 59.6283 | 0.032043 | -0.28381 | -0.11444 | 59.6603 | -61.853 | 0.036621 | -0.34332 | -0.073242 | -0.16479 | -0.19226 | -0.14648 | -0.16022 | -0.10986 | 61.4227 | 61.5921 | 121.3348 | 121.1838 | -0.073242 | 121.3669 | 61.7386 | -0.14648 | 121.1838 | -0.073242 | 61.7386 | 121.3348 | 121.3669 | -121.4905 | -121.6736
83.1406 | 121.7285 | -61.8347 | 59.7382 | -0.047684 | 0.017049 | 0.011974 | 0.011288 | 0.058812 | -0.0074085 | 0.067035 | -61.8027 | 59.4818 | -61.7294 | -61.8988 | 59.5596 | 0.10986 | -0.07782 | -0.13733 | 59.7061 | -61.8576 | 0.10529 | -0.25635 | 0.032044 | -0.064087 | -0.17853 | -0.022888 | -0.032043 | -0.073242 | 61.7569 | 61.6974 | 121.3943 | 121.3165 | 0.032044 | 121.5408 | 61.9446 | -0.022888 | 121.3165 | 0.032044 | 61.9446 | 121.3943 | 121.5408 | -121.4676 | -121.5958
84.8906 | 121.7331 | -61.7203 | 59.848 | -0.14687 | 0.015767 | 0.013683 | 0.0012475 | 0.055822 | -0.0044177 | 0.065326 | -61.6562 | 59.5688 | -61.5646 | -61.7249 | 59.7702 | 0.41199 | 0.3067 | 0.48065 | 59.7473 | -61.7615 | 0.15564 | -0.27923 | 0.064087 | -0.004578 | -0.077819 | -0.041199 | -0.10071 | -0.091553 | 62.027 | 62.2009 | 121.4905 | 121.2891 | 0.064087 | 121.4676 | 62.1323 | -0.041199 | 121.2891 | 0.064087 | 62.1323 | 121.4905 | 121.4676 | -121.4127 | -121.6095
86.5781 | 121.8063 | -61.7432 | 59.761 | 0.13542 | 0.017476 | 0.01176 | 0.0082971 | 0.059881 | -0.0050585 | 0.066608 | -61.8256 | 59.4315 | -61.7065 | -61.8851 | 59.5779 | -0.009155 | -0.40741 | -0.27924 | 59.6329 | -61.8484 | 0.036621 | -0.32959 | -0.082398 | -0.14191 | -0.1831 | -0.10529 | -0.12817 | -0.11902 | 61.3358 | 61.4639 | 121.3211 | 121.1746 | -0.082398 | 121.376 | 61.734 | -0.10529 | 121.1746 | -0.082398 | 61.734 | 121.3211 | 121.376 | -121.4676 | -121.6095
88.3281 | 121.7331 | -61.7432 | 59.8434 | -0.14687 | 0.015767 | 0.014537 | 0.0035975 | 0.055608 | -0.0037769 | 0.065753 | -61.6928 | 59.5367 | -61.6013 | -61.7569 | 59.7198 | 0.40283 | 0.37079 | 0.45776 | 59.7336 | -61.7661 | 0.14191 | -0.3067 | 0.050354 | -0.013733 | -0.1236 | -0.022888 | -0.10986 | -0.091553 | 62.114 | 62.2009 | 121.463 | 121.2799 | 0.050354 | 121.4767 | 62.146 | -0.022888 | 121.2799 | 0.050354 | 62.146 | 121.463 | 121.4767 | -121.4447 | -121.6095
90.0781 | 121.8704 | -61.7569 | 59.7061 | 0.12779 | 0.017476 | 0.013042 | 0.0074427 | 0.057104 | -0.0071947 | 0.065326 | -61.908 | 59.4543 | -61.7477 | -62.0041 | 59.4818 | -0.09613 | -0.28839 | -0.39825 | 59.642 | -61.8759 | 0.009155 | -0.25177 | -0.15106 | -0.24719 | -0.2243 | -0.11902 | -0.064087 | -0.16022 | 61.4685 | 61.3586 | 121.2387 | 121.2112 | -0.15106 | 121.3989 | 61.6608 | -0.11902 | 121.2112 | -0.15106 | 61.6608 | 121.2387 | 121.3989 | -121.4539 | -121.582
91.75 | 121.843 | -61.6333 | 59.8343 | 0.15068 | 0.016836 | 0.0094101 | 0.0029565 | 0.057317 | -0.0037769 | 0.065112 | -61.7752 | 59.4452 | -61.6653 | -61.8759 | 59.6237 | 0.050354 | -0.16479 | -0.050354 | 59.6512 | -61.8301 | -0.032043 | -0.3891 | -0.14191 | -0.24261 | -0.21057 | -0.19684 | -0.18311 | -0.10986 | 61.4685 | 61.5829 | 121.257 | 121.0785 | -0.14191 | 121.2845 | 61.6837 | -0.19684 | 121.0785 | -0.14191 | 61.6837 | 121.257 | 121.2845 | -121.4996 | -121.6644
93.5 | 121.6965 | -61.8439 | 59.7336 | -0.09346 | 0.016622 | 0.013042 | 0.0087243 | 0.059026 | -0.0067675 | 0.065967 | -61.7981 | 59.4772 | -61.7294 | -61.908 | 59.5734 | 0.20142 | 0.013733 | -0.013733 | 59.6832 | -61.8484 | 0.11444 | -0.25635 | 0.045776 | -0.064087 | -0.16022 | -0.004578 | -0.050354 | -0.068665 | 61.8576 | 61.8301 | 121.4172 | 121.3211 | 0.045776 | 121.5271 | 62.0453 | -0.004578 | 121.3211 | 0.045776 | 62.0453 | 121.4172 | 121.5271 | -121.463 | -121.582
95.25 | 121.8613 | -61.6562 | 59.8434 | 0.013352 | 0.016195 | 0.011974 | 0.00060666 | 0.057531 | -0.0033495 | 0.064899 | -61.7661 | 59.5367 | -61.6196 | -61.8668 | 59.6695 | 0.16479 | 0.11444 | 0.16022 | 59.7198 | -61.8164 | 0.036621 | -0.3067 | -0.10986 | -0.21057 | -0.17395 | -0.16022 | -0.1236 | -0.14648 | 61.7706 | 61.8164 | 121.3257 | 121.1929 | -0.10986 | 121.376 | 61.821 | -0.16022 | 121.1929 | -0.10986 | 61.821 | 121.3257 | 121.376 | -121.463 | -121.6599
97 | 121.7743 | -61.7569 | 59.8022 | -0.14687 | 0.018331 | 0.015178 | 0.0048791 | 0.057531 | -0.0065539 | 0.066394 | -61.7798 | 59.5688 | -61.6241 | -61.8759 | 59.61 | 0.32501 | 0.45776 | 0.31128 | 59.7656 | -61.7935 | 0.13275 | -0.23346 | -0.022888 | -0.11902 | -0.19226 | -0.036621 | -0.036621 | -0.15564 | 62.2147 | 62.0682 | 121.3669 | 121.3257 | -0.022888 | 121.5225 | 62.0819 | -0.036621 | 121.3257 | -0.022888 | 62.0819 | 121.3669 | 121.5225 | -121.4264 | -121.5958
98.75 | 121.8567 | -61.7844 | 59.7015 | 0.15831 | 0.01769 | 0.014751 | 0.0074427 | 0.056463 | -0.0074085 | 0.065967 | -61.9217 | 59.4727 | -61.7615 | -62.0316 | 59.4498 | -0.10986 | -0.27466 | -0.4303 | 59.6558 | -61.9217 | 0.022888 | -0.22888 | -0.13733 | -0.24719 | -0.25177 | -0.13733 | -0.045776 | -0.16022 | 61.5097 | 61.3541 | 121.2341 | 121.257 | -0.13733 | 121.4401 | 61.6745 | -0.13733 | 121.257 | -0.13733 | 61.6745 | 121.2341 | 121.4401 | -121.463 | -121.6232
100.4531 | 121.875 | -61.6379 | 59.8343 | 0.0057222 | 0.018758 | 0.014964 | 0.0012475 | 0.055181 | -0.0048449 | 0.065112 | -61.7615 | 59.523 | -61.6196 | -61.8576 | 59.6375 | 0.13275 | 0.041199 | 0.09613 | 59.6924 | -61.821 | 0.01831 | -0.31128 | -0.1236 | -0.21973 | -0.19684 | -0.18311 | -0.14191 | -0.14191 | 61.6791 | 61.734 | 121.2753 | 121.1609 | -0.1236 | 121.3303 | 61.7706 | -0.18311 | 121.1609 | -0.1236 | 61.7706 | 121.2753 | 121.3303 | -121.4539 | -121.6553
102.1875 | 121.7606 | -61.7569 | 59.7794 | -0.17738 | 0.01769 | 0.0085555 | 0.0063745 | 0.053899 | -0.0039905 | 0.066608 | -61.7935 | 59.5871 | -61.6333 | -61.8576 | 59.6191 | 0.32501 | 0.44403 | 0.29755 | 59.761 | -61.8164 | 0.1236 | -0.19226 | -0.036621 | -0.10071 | -0.16022 | -0.059509 | -0.018311 | -0.16022 | 62.2009 | 62.0544 | 121.376 | 121.344 | -0.036621 | 121.5179 | 62.0819 | -0.059509 | 121.344 | -0.036621 | 62.0819 | 121.376 | 121.5179 | -121.4127 | -121.5958
103.9375 | 121.7606 | -61.7889 | 59.7656 | -0.13161 | 0.018758 | 0.012401 | 0.0072291 | 0.056676 | -0.0074085 | 0.065326 | -61.7935 | 59.6237 | -61.647 | -61.9034 | 59.6008 | 0.28839 | 0.33417 | 0.17395 | 59.7427 | -61.8118 | 0.14191 | -0.14191 | -0.004578 | -0.11444 | -0.16479 | -0.022889 | -0.022888 | -0.14648 | 62.1231 | 61.9629 | 121.3898 | 121.4127 | -0.004578 | 121.5317 | 62.0773 | -0.022889 | 121.4127 | -0.004578 | 62.0773 | 121.3898 | 121.5317 | -121.4127 | -121.5775
105.6875 | 121.7834 | -61.7844 | 59.7336 | 0.089645 | 0.017263 | 0.016033 | 0.0076563 | 0.05924 | -0.0084765 | 0.065326 | -61.8942 | 59.4727 | -61.7661 | -61.9858 | 59.4864 | -0.022888 | -0.17395 | -0.34332 | 59.6558 | -61.8942 | 0.018311 | -0.26093 | -0.10986 | -0.20142 | -0.24719 | -0.10986 | -0.07782 | -0.12817 | 61.6104 | 61.441 | 121.2708 | 121.257 | -0.10986 | 121.4401 | 61.7615 | -0.10986 | 121.257 | -0.10986 | 61.7615 | 121.2708 | 121.4401 | -121.4996 | -121.6278
107.375 | 121.8292 | -61.6608 | 59.8343 | -0.0019073 | 0.018117 | 0.011333 | 0.00082026 | 0.058599 | -0.0042041 | 0.067249 | -61.7844 | 59.5596 | -61.6241 | -61.8668 | 59.642 | 0.18768 | 0.12817 | 0.18768 | 59.6924 | -61.7935 | 0.036621 | -0.27466 | -0.1236 | -0.20599 | -0.19226 | -0.13275 | -0.14191 | -0.16022 | 61.7889 | 61.8484 | 121.3028 | 121.2204 | -0.1236 | 121.3531 | 61.8484 | -0.13275 | 121.2204 | -0.1236 | 61.8484 | 121.3028 | 121.3531 | -121.4584 | -121.6278
109.125 | 121.7743 | -61.7477 | 59.7931 | -0.2079 | 0.018331 | 0.014964 | 0.0046655 | 0.05689 | -0.0024951 | 0.064471 | -61.7889 | 59.5871 | -61.615 | -61.8622 | 59.6375 | 0.33875 | 0.4715 | 0.31586 | 59.7656 | -61.821 | 0.13275 | -0.20599 | -0.041198 | -0.11444 | -0.15564 | -0.073242 | -0.027466 | -0.17395 | 62.2192 | 62.0636 | 121.3852 | 121.3348 | -0.041198 | 121.5134 | 62.0865 | -0.073242 | 121.3348 | -0.041198 | 62.0865 | 121.3852 | 121.5134 | -121.4081 | -121.6141
110.7969 | 121.8475 | -61.6241 | 59.8434 | 0.043869 | 0.017263 | 0.011119 | 0.0029565 | 0.055822 | -0.0052721 | 0.064044 | -61.7706 | 59.5505 | -61.6241 | -61.8622 | 59.6191 | 0.13733 | 0.091553 | 0.11444 | 59.7153 | -61.8073 | 0 | -0.29297 | -0.14648 | -0.23804 | -0.2243 | -0.1831 | -0.12817 | -0.14648 | 61.7157 | 61.7386 | 121.2433 | 121.1746 | -0.14648 | 121.3394 | 61.7615 | -0.1831 | 121.1746 | -0.14648 | 61.7615 | 121.2433 | 121.3394 | -121.4676 | -121.6507
112.5469 | 121.7377 | -61.7432 | 59.8663 | -0.1545 | 0.016836 | 0.010265 | 0.0042383 | 0.055395 | -0.0037769 | 0.065967 | -61.6882 | 59.5505 | -61.5921 | -61.7569 | 59.729 | 0.41199 | 0.35248 | 0.48065 | 59.7061 | -61.7706 | 0.15106 | -0.31586 | 0.054932 | -0.013733 | -0.13733 | -0.027466 | -0.16022 | -0.09613 | 62.0956 | 62.2238 | 121.4722 | 121.2936 | 0.054932 | 121.4493 | 62.1552 | -0.027466 | 121.2936 | 0.054932 | 62.1552 | 121.4722 | 121.4493 | -121.4584 | -121.637
114.2969 | 121.843 | -61.7432 | 59.7336 | 0.097275 | 0.015767 | 0.011333 | 0.0089381 | 0.056463 | -0.0065539 | 0.065753 | -61.908 | 59.4498 | -61.7661 | -61.9949 | 59.4864 | -0.091553 | -0.28839 | -0.40741 | 59.6375 | -61.9034 | -0.022888 | -0.28381 | -0.16479 | -0.25177 | -0.24719 | -0.16022 | -0.096131 | -0.14191 | 61.4548 | 61.3358 | 121.2296 | 121.1929 | -0.16479 | 121.3806 | 61.6516 | -0.16022 | 121.1929 | -0.16479 | 61.6516 | 121.2296 | 121.3806 | -121.4996 | -121.637
116.0312 | 121.8384 | -61.7844 | 59.6878 | 0.12016 | 0.020681 | 0.010478 | 0.0097925 | 0.059453 | -0.0084765 | 0.067889 | -61.9125 | 59.4498 | -61.7569 | -62.0178 | 59.4452 | -0.10071 | -0.27924 | -0.43488 | 59.6558 | -61.9171 | 0.027466 | -0.23804 | -0.12817 | -0.23346 | -0.24262 | -0.13275 | -0.032043 | -0.15564 | 61.5051 | 61.3495 | 121.2296 | 121.2341 | -0.12817 | 121.4401 | 61.6837 | -0.13275 | 121.2341 | -0.12817 | 61.6837 | 121.2296 | 121.4401 | -121.4447 | -121.6049
117.7188 | 121.7056 | -61.8301 | 59.7565 | -0.078201 | 0.016836 | 0.012828 | 0.0087243 | 0.059026 | -0.0080493 | 0.06554 | -61.7981 | 59.4955 | -61.6974 | -61.8851 | 59.5917 | 0.2243 | 0.07782 | 0.018311 | 59.6649 | -61.8668 | 0.13275 | -0.26093 | 0.032043 | -0.054932 | -0.16479 | -0.036621 | -0.091553 | -0.10071 | 61.908 | 61.8484 | 121.4218 | 121.3257 | 0.032043 | 121.4951 | 62.0544 | -0.036621 | 121.3257 | 0.032043 | 62.0544 | 121.4218 | 121.4951 | -121.4539 | -121.6232
119.4688 | 121.7422 | -61.7065 | 59.8526 | -0.12398 | 0.015981 | 0.0074875 | 0.0027429 | 0.058812 | -0.0054859 | 0.063403 | -61.6562 | 59.5688 | -61.5555 | -61.7294 | 59.7656 | 0.40283 | 0.28381 | 0.4715 | 59.761 | -61.7432 | 0.15106 | -0.28381 | 0.050354 | -0.022888 | -0.086975 | -0.036621 | -0.091553 | -0.10071 | 61.9904 | 62.178 | 121.4722 | 121.2753 | 0.050354 | 121.4676 | 62.1094 | -0.036621 | 121.2753 | 0.050354 | 62.1094 | 121.4722 | 121.4676 | -121.4081 | -121.5958
121.2188 | 121.7651 | -61.7981 | 59.761 | -0.23079 | 0.017263 | 0.0098373 | 0.0070155 | 0.056035 | -0.0054859 | 0.066608 | -61.7889 | 59.5825 | -61.6425 | -61.8988 | 59.5917 | 0.3067 | 0.41199 | 0.2243 | 59.7656 | -61.7981 | 0.15564 | -0.17853 | 0.009156 | -0.10071 | -0.16937 | 0 | 0.004578 | -0.14648 | 62.2101 | 62.0224 | 121.3898 | 121.3806 | 0.009156 | 121.5637 | 62.1048 | 0 | 121.3806 | 0.009156 | 62.1048 | 121.3898 | 121.5637 | -121.4035 | -121.5591
122.9844 | 121.8521 | -61.6562 | 59.8022 | 0.051498 | 0.014486 | 0.011546 | 0.0016749 | 0.056249 | -0.0035631 | 0.064899 | -61.7569 | 59.5093 | -61.6516 | -61.8759 | 59.6191 | 0.082397 | -0.09613 | -0.004578 | 59.6695 | -61.821 | 0.004578 | -0.29297 | -0.10071 | -0.21973 | -0.1831 | -0.1648 | -0.13275 | -0.10529 | 61.5601 | 61.6516 | 121.2753 | 121.1655 | -0.10071 | 121.3257 | 61.7386 | -0.1648 | 121.1655 | -0.10071 | 61.7386 | 121.2753 | 121.3257 | -121.4539 | -121.6232
124.7344 | 121.8475 | -61.7661 | 59.7198 | 0.12016 | 0.016622 | 0.0074875 | 0.0076563 | 0.057744 | -0.0056995 | 0.06618 | -61.9034 | 59.4315 | -61.7432 | -61.9858 | 59.4955 | -0.086975 | -0.3479 | -0.3891 | 59.6146 | -61.8942 | 0.022888 | -0.28839 | -0.13733 | -0.21973 | -0.22431 | -0.12817 | -0.10529 | -0.16022 | 61.4182 | 61.377 | 121.2616 | 121.1975 | -0.13733 | 121.3806 | 61.6791 | -0.12817 | 121.1975 | -0.13733 | 61.6791 | 121.2616 | 121.3806 | -121.463 | -121.6141
126.4062 | 121.7102 | -61.7157 | 59.8434 | -0.14687 | 0.018545 | 0.014751 | 0.0055201 | 0.054326 | -0.0046313 | 0.064258 | -61.6791 | 59.5825 | -61.5417 | -61.7661 | 59.7198 | 0.41657 | 0.34332 | 0.48065 | 59.7244 | -61.7798 | 0.17395 | -0.26093 | 0.036621 | -0.050354 | -0.1236 | -0.064087 | -0.11902 | -0.13733 | 62.059 | 62.1964 | 121.4355 | 121.2982 | 0.036621 | 121.4401 | 62.1323 | -0.064087 | 121.2982 | 0.036621 | 62.1323 | 121.4355 | 121.4401 | -121.3852 | -121.6232
128.1562 | 121.8155 | -61.7157 | 59.7839 | 0.15068 | 0.016622 | 0.017955 | 0.0068017 | 0.058599 | -0.0054859 | 0.066608 | -61.8027 | 59.4681 | -61.6974 | -61.9034 | 59.5779 | -0.018311 | -0.41199 | -0.25177 | 59.61 | -61.8896 | 0.01831 | -0.31586 | -0.086975 | -0.18768 | -0.20599 | -0.17395 | -0.17395 | -0.10529 | 61.3037 | 61.4639 | 121.2936 | 121.1838 | -0.086975 | 121.3257 | 61.6974 | -0.17395 | 121.1838 | -0.086975 | 61.6974 | 121.2936 | 121.3257 | -121.4813 | -121.6736
129.9219 | 121.8521 | -61.7661 | 59.6924 | 0.16594 | 0.016622 | 0.010692 | 0.0082971 | 0.057744 | -0.0050585 | 0.065967 | -61.9217 | 59.4589 | -61.7752 | -62.0178 | 59.4498 | -0.10071 | -0.27466 | -0.42572 | 59.6329 | -61.8851 | -0.009156 | -0.23346 | -0.15564 | -0.25177 | -0.24262 | -0.11902 | -0.059509 | -0.14648 | 61.4914 | 61.3403 | 121.2158 | 121.225 | -0.15564 | 121.3989 | 61.6653 | -0.11902 | 121.225 | -0.15564 | 61.6653 | 121.2158 | 121.3989 | -121.4676 | -121.5775
131.6094 | 121.7056 | -61.8393 | 59.7427 | -0.11635 | 0.019399 | 0.015605 | 0.0078699 | 0.058812 | -0.0059131 | 0.065753 | -61.7935 | 59.5459 | -61.6928 | -61.8896 | 59.5963 | 0.24261 | 0.1236 | 0.068665 | 59.697 | -61.853 | 0.14648 | -0.19684 | 0.045776 | -0.050354 | -0.14648 | -0.013733 | -0.045777 | -0.10071 | 61.9629 | 61.908 | 121.4355 | 121.3852 | 0.045776 | 121.5363 | 62.0819 | -0.013733 | 121.3852 | 0.045776 | 62.0819 | 121.4355 | 121.5363 | -121.4355 | -121.5958
133.3594 | 121.7972 | -61.7203 | 59.7931 | 0.17357 | 0.015554 | 0.014324 | 0.0063745 | 0.060094 | -0.0042041 | 0.066821 | -61.8118 | 59.4498 | -61.7157 | -61.8988 | 59.5917 | -0.009155 | -0.41657 | -0.2655 | 59.6146 | -61.8622 | 0.004578 | -0.34332 | -0.091553 | -0.17853 | -0.20142 | -0.14191 | -0.17853 | -0.096131 | 61.3037 | 61.4548 | 121.312 | 121.17 | -0.091553 | 121.3348 | 61.7111 | -0.14191 | 121.17 | -0.091553 | 61.7111 | 121.312 | 121.3348 | -121.5088 | -121.6553
135.1094 | 121.7056 | -61.7844 | 59.7519 | -0.070572 | 0.019826 | 0.01646 | 0.0091517 | 0.060949 | -0.0080493 | 0.064044 | -61.7889 | 59.5184 | -61.6837 | -61.8896 | 59.5734 | 0.22888 | 0.068665 | 0.032043 | 59.697 | -61.8439 | 0.10071 | -0.23346 | -0.004577 | -0.10529 | -0.17853 | -0.059509 | -0.054932 | -0.10528 | 61.853 | 61.8164 | 121.3577 | 121.3028 | -0.004577 | 121.4813 | 62.0132 | -0.059509 | 121.3028 | -0.004577 | 62.0132 | 121.3577 | 121.4813 | -121.4355 | -121.5958
136.7812 | 121.8063 | -61.7065 | 59.7977 | 0.15068 | 0.017263 | 0.011546 | 0.0059473 | 0.060094 | -0.0061267 | 0.063831 | -61.7798 | 59.436 | -61.6791 | -61.8896 | 59.5917 | 0.004578 | -0.42572 | -0.2243 | 59.5963 | -61.8759 | 0.027466 | -0.36163 | -0.073242 | -0.1831 | -0.20599 | -0.16937 | -0.20142 | -0.10071 | 61.2808 | 61.4822 | 121.2982 | 121.1426 | -0.073242 | 121.3028 | 61.7111 | -0.16937 | 121.1426 | -0.073242 | 61.7111 | 121.2982 | 121.3028 | -121.4767 | -121.6736
138.5312 | 121.8384 | -61.6653 | 59.848 | -0.0095368 | 0.01534 | 0.012828 | 0.0012475 | 0.05689 | -0.0039905 | 0.064471 | -61.7752 | 59.5642 | -61.6196 | -61.8439 | 59.6466 | 0.20142 | 0.13733 | 0.22888 | 59.6924 | -61.7981 | 0.045776 | -0.28381 | -0.10986 | -0.17853 | -0.20142 | -0.13275 | -0.15564 | -0.15564 | 61.8027 | 61.8942 | 121.3119 | 121.2296 | -0.10986 | 121.3577 | 61.8668 | -0.13275 | 121.2296 | -0.10986 | 61.8668 | 121.3119 | 121.3577 | -121.4676 | -121.6461
140.2812 | 121.8384 | -61.7706 | 59.7198 | 0.089645 | 0.018331 | 0.016246 | 0.0080835 | 0.057531 | -0.0042041 | 0.066608 | -61.9492 | 59.4589 | -61.7706 | -62.027 | 59.436 | -0.091553 | -0.27008 | -0.41199 | 59.6283 | -61.9263 | 0 | -0.26093 | -0.17853 | -0.25635 | -0.28381 | -0.15564 | -0.091553 | -0.17853 | 61.5005 | 61.3586 | 121.2067 | 121.2296 | -0.17853 | 121.3989 | 61.6791 | -0.15564 | 121.2296 | -0.17853 | 61.6791 | 121.2067 | 121.3989 | -121.4905 | -121.6461
142.0156 | 121.7468 | -61.7889 | 59.7473 | -0.017166 | 0.017049 | 0.012187 | 0.0093653 | 0.05924 | -0.0050585 | 0.06554 | -61.8164 | 59.5001 | -61.7477 | -61.9217 | 59.5367 | 0.09613 | -0.10529 | -0.19684 | 59.6786 | -61.8851 | 0.041198 | -0.24719 | -0.027466 | -0.13275 | -0.21057 | -0.096131 | -0.068664 | -0.068664 | 61.6837 | 61.5921 | 121.3257 | 121.2891 | -0.027466 | 121.4676 | 61.8851 | -0.096131 | 121.2891 | -0.027466 | 61.8851 | 121.3257 | 121.4676 | -121.4951 | -121.6324
143.75 | 121.8338 | -61.7523 | 59.7382 | 0.19646 | 0.018331 | 0.010478 | 0.0046655 | 0.058812 | -0.0042041 | 0.06554 | -61.8805 | 59.4543 | -61.7386 | -61.9675 | 59.5047 | -0.082397 | -0.37994 | -0.36163 | 59.61 | -61.908 | 0.013733 | -0.28381 | -0.12817 | -0.21515 | -0.23346 | -0.15564 | -0.12817 | -0.14191 | 61.3724 | 61.3907 | 121.257 | 121.2067 | -0.12817 | 121.3623 | 61.6699 | -0.15564 | 121.2067 | -0.12817 | 61.6699 | 121.257 | 121.3623 | -121.4767 | -121.6461
145.5156 | 121.7148 | -61.7294 | 59.8206 | -0.18501 | 0.013418 | 0.012187 | 0.0025293 | 0.058172 | -0.0063403 | 0.062976 | -61.6837 | 59.5367 | -61.5921 | -61.7706 | 59.7153 | 0.42114 | 0.36621 | 0.4715 | 59.7794 | -61.7661 | 0.13733 | -0.28381 | 0.045776 | -0.041199 | -0.10529 | -0.036621 | -0.041199 | -0.091553 | 62.0956 | 62.2009 | 121.4447 | 121.2662 | 0.045776 | 121.5088 | 62.1506 | -0.036621 | 121.2662 | 0.045776 | 62.1506 | 121.4447 | 121.5088 | -121.4127 | -121.5866
147.2031 | 121.8155 | -61.7569 | 59.7198 | 0.1812 | 0.016622 | 0.012401 | 0.0065881 | 0.059881 | -0.0052721 | 0.065326 | -61.8713 | 59.4452 | -61.7477 | -61.9446 | 59.5184 | -0.064087 | -0.38452 | -0.35706 | 59.6237 | -61.8851 | 0.009155 | -0.27466 | -0.11444 | -0.18768 | -0.20142 | -0.12817 | -0.096131 | -0.1236 | 61.3724 | 61.3998 | 121.2753 | 121.2021 | -0.11444 | 121.3806 | 61.6928 | -0.12817 | 121.2021 | -0.11444 | 61.6928 | 121.2753 | 121.3806 | -121.4676 | -121.6049
148.9375 | 121.7285 | -61.7111 | 59.8663 | -0.2079 | 0.01769 | 0.013042 | 0.0035975 | 0.058599 | -0.0054859 | 0.063831 | -61.6516 | 59.5871 | -61.5509 | -61.7294 | 59.7427 | 0.41657 | 0.33875 | 0.48523 | 59.7015 | -61.7889 | 0.16022 | -0.27924 | 0.05951 | -0.01831 | -0.1236 | -0.077819 | -0.16479 | -0.10071 | 62.0499 | 62.1963 | 121.4539 | 121.2982 | 0.05951 | 121.4127 | 62.1277 | -0.077819 | 121.2982 | 0.05951 | 62.1277 | 121.4539 | 121.4127 | -121.4172 | -121.6553
150.625 | 121.8613 | -61.7935 | 59.6924 | 0.14305 | 0.018331 | 0.013042 | 0.0095789 | 0.057958 | -0.0078357 | 0.066821 | -61.9217 | 59.4635 | -61.7569 | -62.0178 | 59.4543 | -0.10986 | -0.29297 | -0.42572 | 59.6558 | -61.8896 | 0.036621 | -0.22888 | -0.12817 | -0.2243 | -0.23804 | -0.09613 | -0.036621 | -0.16479 | 61.5005 | 61.3678 | 121.2479 | 121.257 | -0.12817 | 121.4493 | 61.6837 | -0.09613 | 121.257 | -0.12817 | 61.6837 | 121.2479 | 121.4493 | -121.4493 | -121.582
152.375 | 121.7514 | -61.8256 | 59.7107 | 0.020981 | 0.018117 | 0.013469 | 0.010433 | 0.059453 | -0.0089037 | 0.063831 | -61.8896 | 59.4727 | -61.7706 | -61.9858 | 59.4818 | 0.004578 | -0.17853 | -0.29755 | 59.6741 | -61.8668 | 0.054932 | -0.23804 | -0.064086 | -0.16022 | -0.22888 | -0.041198 | -0.036621 | -0.11902 | 61.647 | 61.528 | 121.3074 | 121.2982 | -0.064086 | 121.4996 | 61.8301 | -0.041198 | 121.2982 | -0.064086 | 61.8301 | 121.3074 | 121.4996 | -121.4813 | -121.5775
154.125 | 121.701 | -61.853 | 59.7107 | -0.078201 | 0.018972 | 0.01411 | 0.0078699 | 0.058172 | -0.0071947 | 0.063403 | -61.8164 | 59.5139 | -61.6974 | -61.8896 | 59.5596 | 0.18768 | 0.009155 | -0.018311 | 59.697 | -61.853 | 0.15564 | -0.19684 | 0.036621 | -0.036621 | -0.15106 | 0 | -0.013733 | -0.11902 | 61.8622 | 61.8347 | 121.4127 | 121.3669 | 0.036621 | 121.55 | 62.0407 | 0 | 121.3669 | 0.036621 | 62.0407 | 121.4127 | 121.55 | -121.4081 | -121.5637
155.8125 | 121.788 | -61.6562 | 59.848 | -0.070572 | 0.015767 | 0.01176 | -0.00046134 | 0.057744 | -0.0037769 | 0.064685 | -61.6928 | 59.5642 | -61.5417 | -61.7615 | 59.729 | 0.33417 | 0.21973 | 0.37994 | 59.697 | -61.7798 | 0.11444 | -0.28381 | -0.036621 | -0.10529 | -0.11902 | -0.1236 | -0.15106 | -0.15106 | 61.8759 | 62.0361 | 121.3852 | 121.2204 | -0.036621 | 121.3531 | 61.9904 | -0.1236 | 121.2204 | -0.036621 | 61.9904 | 121.3852 | 121.3531 | -121.3898 | -121.6278
157.5625 | 121.7194 | -61.7386 | 59.8434 | -0.1545 | 0.015767 | 0.014751 | 0.0038111 | 0.055822 | -0.0027087 | 0.064044 | -61.6837 | 59.6008 | -61.5784 | -61.7752 | 59.7153 | 0.41657 | 0.35706 | 0.4715 | 59.729 | -61.7798 | 0.16022 | -0.24262 | 0.054931 | -0.036622 | -0.12817 | -0.041199 | -0.11444 | -0.10529 | 62.0956 | 62.2101 | 121.4539 | 121.3394 | 0.054931 | 121.4676 | 62.1552 | -0.041199 | 121.3394 | 0.054931 | 62.1552 | 121.4539 | 121.4676 | -121.4218 | -121.6232
159.2969 | 121.7194 | -61.8393 | 59.7153 | -0.070572 | 0.016408 | 0.015819 | 0.0072291 | 0.058812 | -0.0071947 | 0.06554 | -61.8164 | 59.5001 | -61.734 | -61.8942 | 59.5642 | 0.16022 | -0.050354 | -0.086975 | 59.6603 | -61.8576 | 0.10529 | -0.21515 | 0.022888 | -0.054932 | -0.15106 | -0.018311 | -0.054932 | -0.082397 | 61.7889 | 61.7523 | 121.4035 | 121.3394 | 0.022888 | 121.4996 | 61.9995 | -0.018311 | 121.3394 | 0.022888 | 61.9995 | 121.4035 | 121.4996 | -121.4493 | -121.5729
161.0312 | 121.8109 | -61.7432 | 59.7794 | 0.19646 | 0.01534 | 0.010051 | 0.0059473 | 0.058599 | -0.0054859 | 0.065753 | -61.853 | 59.4452 | -61.7386 | -61.9263 | 59.5459 | -0.041199 | -0.3891 | -0.28381 | 59.6283 | -61.8484 | 0.004578 | -0.33417 | -0.10986 | -0.18311 | -0.23346 | -0.10529 | -0.15106 | -0.11444 | 61.3541 | 61.4594 | 121.2891 | 121.1884 | -0.10986 | 121.3715 | 61.702 | -0.10529 | 121.1884 | -0.10986 | 61.702 | 121.2891 | 121.3715 | -121.5179 | -121.6278
162.7812 | 121.7926 | -61.7249 | 59.7794 | 0.082016 | 0.016408 | 0.012401 | 0.0048791 | 0.060735 | -0.0039905 | 0.066608 | -61.7981 | 59.4406 | -61.6928 | -61.8988 | 59.5779 | -0.004578 | -0.40741 | -0.23346 | 59.6283 | -61.8759 | 0.032044 | -0.33875 | -0.073242 | -0.17395 | -0.20142 | -0.15106 | -0.15106 | -0.10529 | 61.3174 | 61.4914 | 121.3028 | 121.1655 | -0.073242 | 121.3531 | 61.7203 | -0.15106 | 121.1655 | -0.073242 | 61.7203 | 121.3028 | 121.3531 | -121.4722 | -121.6553
164.5312 | 121.8384 | -61.6379 | 59.8343 | 0.020981 | 0.016408 | 0.0096237 | 0.00017946 | 0.054967 | -0.0039905 | 0.065753 | -61.7615 | 59.5413 | -61.5967 | -61.8027 | 59.6741 | 0.27008 | 0.1831 | 0.29297 | 59.7336 | -61.7844 | 0.041198 | -0.29297 | -0.1236 | -0.16479 | -0.16022 | -0.14648 | -0.10071 | -0.16479 | 61.821 | 61.9308 | 121.3119 | 121.1792 | -0.1236 | 121.3715 | 61.908 | -0.14648 | 121.1792 | -0.1236 | 61.908 | 121.3119 | 121.3715 | -121.431 | -121.6187
166.2812 | 121.7468 | -61.7752 | 59.7656 | -0.21553 | 0.018758 | 0.011974 | 0.0080835 | 0.058172 | -0.0074085 | 0.065326 | -61.7798 | 59.6237 | -61.6333 | -61.8851 | 59.5779 | 0.29297 | 0.36621 | 0.21057 | 59.7702 | -61.8256 | 0.14191 | -0.14191 | -0.004577 | -0.10986 | -0.18768 | -0.050354 | 0.004578 | -0.14648 | 62.1414 | 61.9858 | 121.3531 | 121.3989 | -0.004577 | 121.5454 | 62.0682 | -0.050354 | 121.3989 | -0.004577 | 62.0682 | 121.3531 | 121.5454 | -121.3989 | -121.5912
167.9688 | 121.7422 | -61.7523 | 59.7656 | -0.2079 | 0.016622 | 0.0070603 | 0.0050929 | 0.056676 | -0.0054859 | 0.064044 | -61.7981 | 59.5871 | -61.6379 | -61.8576 | 59.6375 | 0.32044 | 0.45319 | 0.27924 | 59.7794 | -61.7981 | 0.11444 | -0.17853 | -0.045777 | -0.10529 | -0.12817 | -0.045777 | 0.013733 | -0.16022 | 62.2055 | 62.0316 | 121.3898 | 121.3394 | -0.045777 | 121.5317 | 62.0728 | -0.045777 | 121.3394 | -0.045777 | 62.0728 | 121.3898 | 121.5317 | -121.4035 | -121.5637
169.7188 | 121.7789 | -61.7569 | 59.7931 | -0.13924 | 0.018331 | 0.015178 | 0.0033839 | 0.05689 | -0.0044177 | 0.065753 | -61.7615 | 59.5734 | -61.6241 | -61.853 | 59.6146 | 0.32959 | 0.46692 | 0.32959 | 59.7565 | -61.7935 | 0.13275 | -0.21973 | -0.004578 | -0.09613 | -0.17853 | -0.036621 | -0.036621 | -0.13733 | 62.2238 | 62.0865 | 121.3715 | 121.3303 | -0.004578 | 121.5134 | 62.0865 | -0.036621 | 121.3303 | -0.004578 | 62.0865 | 121.3715 | 121.5134 | -121.4172 | -121.5866
171.4844 | 121.8338 | -61.6333 | 59.8297 | 0.02861 | 0.014486 | 0.011974 | 0.0018885 | 0.057104 | -0.0052721 | 0.067249 | -61.7706 | 59.5551 | -61.5967 | -61.8347 | 59.6375 | 0.1831 | 0.1236 | 0.1831 | 59.7107 | -61.7981 | 0.036621 | -0.27466 | -0.13733 | -0.20142 | -0.19226 | -0.16479 | -0.11902 | -0.17395 | 61.7569 | 61.8164 | 121.2708 | 121.1884 | -0.13733 | 121.344 | 61.8164 | -0.16479 | 121.1884 | -0.13733 | 61.8164 | 121.2708 | 121.344 | -121.4264 | -121.6278
173.2344 | 121.7102 | -61.7065 | 59.848 | -0.2079 | 0.015554 | 0.012187 | 0.0050929 | 0.056463 | -0.0046313 | 0.064471 | -61.6608 | 59.5688 | -61.5646 | -61.7249 | 59.7519 | 0.40741 | 0.31586 | 0.49896 | 59.7061 | -61.7294 | 0.14191 | -0.27923 | 0.045776 | -0.018311 | -0.09613 | -0.022888 | -0.14191 | -0.096131 | 62.0224 | 62.2055 | 121.4584 | 121.2753 | 0.045776 | 121.4127 | 62.114 | -0.022888 | 121.2753 | 0.045776 | 62.114 | 121.4584 | 121.4127 | -121.4127 | -121.5775
175 | 121.6919 | -61.8118 | 59.7244 | -0.078201 | 0.017049 | 0.014964 | 0.0082971 | 0.057958 | -0.0063403 | 0.064258 | -61.7935 | 59.491 | -61.702 | -61.8713 | 59.5596 | 0.19684 | 0.022888 | -0.004578 | 59.7015 | -61.8301 | 0.10986 | -0.23346 | 0.018311 | -0.059509 | -0.16479 | -0.01831 | -0.022888 | -0.091553 | 61.8347 | 61.8073 | 121.3715 | 121.3028 | 0.018311 | 121.5134 | 62.0087 | -0.01831 | 121.3028 | 0.018311 | 62.0087 | 121.3715 | 121.5134 | -121.4264 | -121.5546
176.6719 | 121.8521 | -61.6379 | 59.8251 | 0.0057222 | 0.017263 | 0.011333 | 0.0010339 | 0.058385 | -0.0054859 | 0.063831 | -61.7661 | 59.5276 | -61.6058 | -61.8439 | 59.61 | 0.13733 | 0.059509 | 0.10986 | 59.7107 | -61.8164 | 0.032043 | -0.29755 | -0.12817 | -0.20599 | -0.21515 | -0.17853 | -0.11444 | -0.16022 | 61.6974 | 61.7477 | 121.2479 | 121.1655 | -0.12817 | 121.3486 | 61.7752 | -0.17853 | 121.1655 | -0.12817 | 61.7752 | 121.2479 | 121.3486 | -121.431 | -121.6415
178.4219 | 121.8155 | -61.7615 | 59.6786 | 0.11253 | 0.015554 | 0.014964 | 0.0072291 | 0.058172 | -0.0067675 | 0.06554 | -61.9308 | 59.4452 | -61.7798 | -62.0041 | 59.4543 | -0.073242 | -0.25635 | -0.39825 | 59.6283 | -61.908 | -0.01831 | -0.23346 | -0.16937 | -0.24261 | -0.2243 | -0.14648 | -0.050354 | -0.15106 | 61.5051 | 61.3632 | 121.2158 | 121.2067 | -0.16937 | 121.3898 | 61.6882 | -0.14648 | 121.2067 | -0.16937 | 61.6882 | 121.2158 | 121.3898 | -121.4584 | -121.5866
180.1094 | 121.7651 | -61.7661 | 59.7794 | -0.26894 | 0.017049 | 0.010265 | 0.0042383 | 0.055608 | -0.0056995 | 0.062976 | -61.7798 | 59.6237 | -61.5921 | -61.8622 | 59.5963 | 0.32501 | 0.45776 | 0.31128 | 59.7565 | -61.821 | 0.17395 | -0.15564 | -0.013733 | -0.096131 | -0.18311 | -0.054932 | -0.022888 | -0.18768 | 62.2238 | 62.0773 | 121.3623 | 121.3898 | -0.013733 | 121.5225 | 62.0911 | -0.054932 | 121.3898 | -0.013733 | 62.0911 | 121.3623 | 121.5225 | -121.3715 | -121.6003
181.8438 | 121.843 | -61.6699 | 59.816 | 0.089645 | 0.016622 | 0.01411 | 0.0031701 | 0.054967 | -0.0033495 | 0.067462 | -61.7752 | 59.4681 | -61.6333 | -61.8713 | 59.6146 | 0.059509 | -0.11444 | 0 | 59.642 | -61.8027 | 0.036621 | -0.3479 | -0.10529 | -0.20142 | -0.20142 | -0.13275 | -0.17395 | -0.14191 | 61.5555 | 61.6699 | 121.2845 | 121.138 | -0.10529 | 121.312 | 61.7294 | -0.13275 | 121.138 | -0.10529 | 61.7294 | 121.2845 | 121.312 | -121.4493 | -121.6187
183.5781 | 121.8796 | -61.6562 | 59.8343 | 0.043869 | 0.014913 | 0.0079147 | 0.0046655 | 0.056249 | -0.0059131 | 0.065967 | -61.7615 | 59.5047 | -61.6058 | -61.853 | 59.6283 | 0.1236 | 0.045776 | 0.11444 | 59.7198 | -61.7935 | 0.050354 | -0.32959 | -0.10529 | -0.19684 | -0.20599 | -0.13733 | -0.11444 | -0.15564 | 61.702 | 61.7706 | 121.2845 | 121.1609 | -0.10529 | 121.376 | 61.7798 | -0.13733 | 121.1609 | -0.10529 | 61.7798 | 121.2845 | 121.376 | -121.4401 | -121.6278
185.2656 | 121.7194 | -61.7203 | 59.8343 | -0.16975 | 0.016408 | 0.010478 | 0.0061609 | 0.056463 | -0.0046313 | 0.064044 | -61.6608 | 59.5505 | -61.5738 | -61.7523 | 59.6924 | 0.40741 | 0.3479 | 0.4715 | 59.7519 | -61.7661 | 0.14648 | -0.28381 | 0.059509 | -0.032043 | -0.14191 | -0.045776 | -0.082398 | -0.086975 | 62.0682 | 62.1918 | 121.4127 | 121.2708 | 0.059509 | 121.4722 | 62.1277 | -0.045776 | 121.2708 | 0.059509 | 62.1277 | 121.4127 | 121.4722 | -121.4081 | -121.6003
187 | 121.6965 | -61.8118 | 59.7244 | -0.085831 | 0.014913 | 0.016887 | 0.010647 | 0.059026 | -0.0089037 | 0.06554 | -61.7935 | 59.4589 | -61.7111 | -61.8668 | 59.5596 | 0.16937 | -0.059509 | -0.059509 | 59.6786 | -61.8164 | 0.10071 | -0.2655 | 0.018311 | -0.054931 | -0.16479 | -0.004577 | -0.045776 | -0.082397 | 61.7523 | 61.7523 | 121.3715 | 121.2708 | 0.018311 | 121.4905 | 61.9812 | -0.004577 | 121.2708 | 0.018311 | 61.9812 | 121.3715 | 121.4905 | -121.4355 | -121.5408
188.7344 | 121.7102 | -61.8073 | 59.7382 | -0.032425 | 0.015981 | 0.010906 | 0.0080835 | 0.05924 | -0.0061267 | 0.065753 | -61.7889 | 59.4681 | -61.7065 | -61.8942 | 59.5551 | 0.17395 | -0.045776 | -0.07782 | 59.6695 | -61.8301 | 0.10071 | -0.27008 | 0.018311 | -0.086975 | -0.18311 | -0.022888 | -0.068664 | -0.082397 | 61.7615 | 61.7294 | 121.3623 | 121.2753 | 0.018311 | 121.4767 | 61.9812 | -0.022888 | 121.2753 | 0.018311 | 61.9812 | 121.3623 | 121.4767 | -121.4447 | -121.5683
190.5 | 121.8521 | -61.6333 | 59.816 | -0.0019073 | 0.015981 | 0.0087693 | 0.00039306 | 0.056249 | -0.0044177 | 0.066394 | -61.7477 | 59.5551 | -61.6104 | -61.8393 | 59.6329 | 0.17395 | 0.10529 | 0.17395 | 59.7244 | -61.7981 | 0.022888 | -0.26093 | -0.11444 | -0.20599 | -0.1831 | -0.16479 | -0.091553 | -0.13733 | 61.7386 | 61.8073 | 121.2662 | 121.1884 | -0.11444 | 121.3577 | 61.8073 | -0.16479 | 121.1884 | -0.11444 | 61.8073 | 121.2662 | 121.3577 | -121.4264 | -121.6141
192.1719 | 121.8201 | -61.7706 | 59.7153 | 0.12016 | 0.017476 | 0.010906 | 0.0082971 | 0.058385 | -0.0054859 | 0.064044 | -61.8805 | 59.4406 | -61.7569 | -61.9675 | 59.4727 | -0.086975 | -0.36621 | -0.37537 | 59.6283 | -61.9034 | 0.013733 | -0.27466 | -0.10986 | -0.19684 | -0.24262 | -0.13275 | -0.086975 | -0.1236 | 61.4044 | 61.3953 | 121.2433 | 121.2112 | -0.10986 | 121.3989 | 61.6837 | -0.13275 | 121.2112 | -0.10986 | 61.6837 | 121.2433 | 121.3989 | -121.4722 | -121.6187
193.9219 | 121.8384 | -61.6562 | 59.8206 | 0.013352 | 0.017263 | 0.0087693 | 0.0021021 | 0.055822 | -0.0027087 | 0.06554 | -61.7615 | 59.5367 | -61.6013 | -61.8576 | 59.6283 | 0.15106 | 0.091553 | 0.14191 | 59.7107 | -61.7935 | 0.054932 | -0.28381 | -0.10529 | -0.20142 | -0.19226 | -0.13733 | -0.10986 | -0.16022 | 61.7477 | 61.7981 | 121.2845 | 121.1929 | -0.10529 | 121.3669 | 61.8073 | -0.13733 | 121.1929 | -0.10529 | 61.8073 | 121.2845 | 121.3669 | -121.4218 | -121.6141
195.6719 | 121.7972 | -61.7706 | 59.7015 | 0.082016 | 0.016836 | 0.017101 | 0.0085107 | 0.056249 | -0.0065539 | 0.065967 | -61.8851 | 59.4315 | -61.7661 | -61.9904 | 59.4589 | -0.036621 | -0.1831 | -0.33875 | 59.6603 | -61.8668 | 0.004578 | -0.27008 | -0.11444 | -0.21973 | -0.24262 | -0.09613 | -0.041199 | -0.11902 | 61.5875 | 61.4319 | 121.2296 | 121.2021 | -0.11444 | 121.431 | 61.734 | -0.09613 | 121.2021 | -0.11444 | 61.734 | 121.2296 | 121.431 | -121.4676 | -121.5683
197.3594 | 121.7056 | -61.702 | 59.8343 | -0.16212 | 0.015767 | 0.012187 | 0.0027429 | 0.056249 | -0.0063403 | 0.064471 | -61.6653 | 59.5642 | -61.5601 | -61.734 | 59.7473 | 0.40741 | 0.33417 | 0.50354 | 59.7198 | -61.7661 | 0.14191 | -0.27008 | 0.036621 | -0.032044 | -0.086976 | -0.064087 | -0.11444 | -0.10528 | 62.0361 | 62.2055 | 121.4493 | 121.2662 | 0.036621 | 121.4218 | 62.1094 | -0.064087 | 121.2662 | 0.036621 | 62.1094 | 121.4493 | 121.4218 | -121.3943 | -121.6003
199.1094 | 121.7834 | -61.647 | 59.8663 | -0.085831 | 0.015767 | 0.013042 | 0.0025293 | 0.055395 | -0.0061267 | 0.06554 | -61.6974 | 59.5596 | -61.5829 | -61.7706 | 59.7336 | 0.3067 | 0.21515 | 0.35706 | 59.7015 | -61.7661 | 0.064087 | -0.3067 | -0.050354 | -0.1236 | -0.13275 | -0.11902 | -0.16479 | -0.11444 | 61.8622 | 62.0041 | 121.3806 | 121.2067 | -0.050354 | 121.3486 | 61.9537 | -0.11902 | 121.2067 | -0.050354 | 61.9537 | 121.3806 | 121.3486 | -121.4493 | -121.6324
200.8594 | 121.8246 | -61.6425 | 59.8297 | 0.097275 | 0.016622 | 0.011333 | 0.0055201 | 0.056463 | -0.0061267 | 0.067035 | -61.7706 | 59.4681 | -61.6425 | -61.8622 | 59.6054 | 0.073242 | -0.09613 | 0.004578 | 59.6832 | -61.8073 | 0 | -0.36163 | -0.12817 | -0.21973 | -0.2243 | -0.16479 | -0.14648 | -0.12817 | 61.5463 | 61.647 | 121.2479 | 121.1105 | -0.12817 | 121.3257 | 61.7157 | -0.16479 | 121.1105 | -0.12817 | 61.7157 | 121.2479 | 121.3257 | -121.4722 | -121.637
202.6094 | 121.7422 | -61.7615 | 59.7427 | -0.20027 | 0.016195 | 0.011333 | 0.0068017 | 0.055395 | -0.0052721 | 0.065967 | -61.7203 | 59.5871 | -61.6287 | -61.8118 | 59.6329 | 0.34332 | 0.46692 | 0.37537 | 59.7473 | -61.7523 | 0.13275 | -0.15564 | 0.041199 | -0.050354 | -0.10986 | 0.009156 | 0.004577 | -0.091553 | 62.2284 | 62.1368 | 121.3943 | 121.3486 | 0.041199 | 121.5088 | 62.1048 | 0.009156 | 121.3486 | 0.041199 | 62.1048 | 121.3943 | 121.5088 | -121.3715 | -121.4951
204.3594 | 121.8155 | -61.647 | 59.8068 | 0.013352 | 0.019185 | 0.0062057 | 0.0046655 | 0.055608 | -0.0044177 | 0.06618 | -61.7477 | 59.5139 | -61.6013 | -61.821 | 59.6283 | 0.14191 | 0.09613 | 0.15564 | 59.697 | -61.8164 | 0.045777 | -0.29297 | -0.10071 | -0.17395 | -0.17853 | -0.16937 | -0.10986 | -0.14649 | 61.7432 | 61.8027 | 121.2753 | 121.1609 | -0.10071 | 121.344 | 61.7889 | -0.16937 | 121.1609 | -0.10071 | 61.7889 | 121.2753 | 121.344 | -121.4081 | -121.6232
206.0469 | 121.7285 | -61.8073 | 59.6924 | -0.0095368 | 0.018758 | 0.013469 | 0.011288 | 0.059881 | -0.0061267 | 0.06554 | -61.8256 | 59.4681 | -61.7477 | -61.9354 | 59.491 | 0.050354 | -0.14191 | -0.23804 | 59.6786 | -61.853 | 0.059509 | -0.2243 | -0.018311 | -0.12817 | -0.20142 | -0.045776 | -0.013733 | -0.07782 | 61.6653 | 61.5692 | 121.2982 | 121.2753 | -0.018311 | 121.4859 | 61.8576 | -0.045776 | 121.2753 | -0.018311 | 61.8576 | 121.2982 | 121.4859 | -121.4401 | -121.5454
207.7969 | 121.8384 | -61.7523 | 59.6924 | 0.097275 | 0.015767 | 0.011974 | 0.0076563 | 0.05924 | -0.0063403 | 0.06554 | -61.8805 | 59.4315 | -61.7523 | -61.9675 | 59.4772 | -0.091553 | -0.29297 | -0.37994 | 59.6466 | -61.8576 | 0 | -0.26093 | -0.12817 | -0.21515 | -0.21515 | -0.10529 | -0.045777 | -0.12817 | 61.4594 | 61.3724 | 121.2296 | 121.1838 | -0.12817 | 121.3989 | 61.6608 | -0.10529 | 121.1838 | -0.12817 | 61.6608 | 121.2296 | 121.3989 | -121.4447 | -121.55
209.4844 | 121.7285 | -61.8027 | 59.7061 | 0.020981 | 0.016836 | 0.012828 | 0.0065881 | 0.060308 | -0.0084765 | 0.067249 | -61.8439 | 59.4772 | -61.7249 | -61.9629 | 59.4955 | 0.045776 | -0.15106 | -0.23804 | 59.6329 | -61.8896 | 0.077819 | -0.22888 | -0.041199 | -0.16022 | -0.21057 | -0.086975 | -0.073242 | -0.11902 | 61.6516 | 61.5646 | 121.2982 | 121.2799 | -0.041199 | 121.4355 | 61.8484 | -0.086975 | 121.2799 | -0.041199 | 61.8484 | 121.2982 | 121.4355 | -121.431 | -121.5958
211.2344 | 121.7102 | -61.6882 | 59.8434 | -0.11635 | 0.017904 | 0.011546 | 0.0025293 | 0.057104 | -0.0042041 | 0.064258 | -61.6653 | 59.5505 | -61.5509 | -61.7111 | 59.7473 | 0.3891 | 0.2655 | 0.43945 | 59.7107 | -61.7386 | 0.13733 | -0.29297 | 0.022888 | -0.022889 | -0.096131 | -0.050354 | -0.13275 | -0.11444 | 61.9537 | 62.1277 | 121.4355 | 121.2387 | 0.022888 | 121.3989 | 62.0773 | -0.050354 | 121.2387 | 0.022888 | 62.0773 | 121.4355 | 121.3989 | -121.3943 | -121.582
212.9844 | 121.8155 | -61.734 | 59.7107 | 0.11253 | 0.017263 | 0.010906 | 0.0085107 | 0.05924 | -0.0037769 | 0.065753 | -61.8713 | 59.5047 | -61.7523 | -61.9629 | 59.4727 | -0.10071 | -0.32959 | -0.38452 | 59.6375 | -61.8942 | -0.01831 | -0.20599 | -0.13733 | -0.22888 | -0.23804 | -0.16022 | -0.073242 | -0.11902 | 61.4044 | 61.3495 | 121.2067 | 121.2387 | -0.13733 | 121.3715 | 61.6333 | -0.16022 | 121.2387 | -0.13733 | 61.6333 | 121.2067 | 121.3715 | -121.463 | -121.6049
214.6719 | 121.701 | -61.8073 | 59.729 | -0.070572 | 0.014272 | 0.010478 | 0.0082971 | 0.058599 | -0.0071947 | 0.06554 | -61.821 | 59.4818 | -61.7203 | -61.9034 | 59.5551 | 0.16937 | -0.064087 | -0.086975 | 59.6603 | -61.8347 | 0.086975 | -0.24719 | -0.013733 | -0.09613 | -0.17395 | -0.027466 | -0.068665 | -0.10071 | 61.7432 | 61.7203 | 121.3623 | 121.2891 | -0.013733 | 121.4676 | 61.9766 | -0.027466 | 121.2891 | -0.013733 | 61.9766 | 121.3623 | 121.4676 | -121.4493 | -121.5637
216.4219 | 121.7056 | -61.8073 | 59.7198 | -0.10872 | 0.017476 | 0.01176 | 0.0082971 | 0.059667 | -0.0078357 | 0.063831 | -61.7935 | 59.5459 | -61.6837 | -61.8759 | 59.5825 | 0.25177 | 0.1236 | 0.073242 | 59.6878 | -61.8393 | 0.1236 | -0.17395 | 0.013733 | -0.068665 | -0.13733 | -0.032043 | -0.032044 | -0.10986 | 61.9308 | 61.8805 | 121.3898 | 121.3531 | 0.013733 | 121.4951 | 62.059 | -0.032043 | 121.3531 | 0.013733 | 62.059 | 121.3898 | 121.4951 | -121.4035 | -121.5591
218.1094 | 121.7972 | -61.6608 | 59.848 | -0.062942 | 0.016195 | 0.013683 | 0.00017946 | 0.057531 | -0.0067675 | 0.062763 | -61.7249 | 59.5551 | -61.6104 | -61.7706 | 59.6924 | 0.28839 | 0.19684 | 0.33875 | 59.7336 | -61.7477 | 0.050354 | -0.29297 | -0.064087 | -0.10986 | -0.15564 | -0.086975 | -0.11444 | -0.11444 | 61.8576 | 61.9995 | 121.3531 | 121.2158 | -0.064087 | 121.3943 | 61.9492 | -0.086975 | 121.2158 | -0.064087 | 61.9492 | 121.3531 | 121.3943 | -121.4584 | -121.5958
219.8594 | 121.7239 | -61.702 | 59.8114 | -0.18501 | 0.014486 | 0.0094101 | 0.0044519 | 0.055822 | -0.0050585 | 0.066394 | -61.6974 | 59.5596 | -61.5738 | -61.7661 | 59.697 | 0.40283 | 0.41657 | 0.44403 | 59.7565 | -61.7615 | 0.12817 | -0.25177 | 0.004577 | -0.064087 | -0.11444 | -0.05951 | -0.054931 | -0.1236 | 62.1185 | 62.146 | 121.3989 | 121.2616 | 0.004577 | 121.4584 | 62.1048 | -0.05951 | 121.2616 | 0.004577 | 62.1048 | 121.3989 | 121.4584 | -121.3852 | -121.5729
221.5469 | 121.8246 | -61.615 | 59.8251 | 0.0057222 | 0.015554 | 0.011546 | 0.0042383 | 0.054754 | -0.0037769 | 0.06618 | -61.7615 | 59.5322 | -61.647 | -61.8439 | 59.6237 | 0.17395 | 0.11902 | 0.18768 | 59.6924 | -61.7981 | -0.032044 | -0.29297 | -0.14648 | -0.22888 | -0.20142 | -0.18311 | -0.13275 | -0.11444 | 61.734 | 61.8027 | 121.2387 | 121.1472 | -0.14648 | 121.3074 | 61.7889 | -0.18311 | 121.1472 | -0.14648 | 61.7889 | 121.2387 | 121.3074 | -121.4722 | -121.6232
223.2812 | 121.7194 | -61.7477 | 59.8251 | -0.16975 | 0.01534 | 0.014324 | 0.0057337 | 0.055608 | -0.0052721 | 0.062335 | -61.6928 | 59.5459 | -61.5692 | -61.7615 | 59.6924 | 0.42572 | 0.40283 | 0.46692 | 59.7244 | -61.7798 | 0.17853 | -0.27924 | 0.054932 | -0.013733 | -0.13275 | -0.032043 | -0.10071 | -0.1236 | 62.1506 | 62.2147 | 121.4401 | 121.2936 | 0.054932 | 121.4722 | 62.1735 | -0.032043 | 121.2936 | 0.054932 | 62.1735 | 121.4401 | 121.4722 | -121.3943 | -121.6049
225.0312 | 121.7789 | -61.6653 | 59.816 | -0.062942 | 0.015767 | 0.010906 | 0.0038111 | 0.055608 | -0.0044177 | 0.06319 | -61.6791 | 59.5596 | -61.5829 | -61.7569 | 59.7153 | 0.32959 | 0.21973 | 0.40283 | 59.7198 | -61.7706 | 0.082397 | -0.25635 | -0.013733 | -0.091553 | -0.10071 | -0.10529 | -0.09613 | -0.09613 | 61.8851 | 62.0682 | 121.3806 | 121.225 | -0.013733 | 121.3852 | 61.9949 | -0.10529 | 121.225 | -0.013733 | 61.9949 | 121.3806 | 121.3852 | -121.3989 | -121.5866
226.7031 | 121.7468 | -61.8073 | 59.6924 | 0.066757 | 0.016836 | 0.01176 | 0.011288 | 0.058812 | -0.0091173 | 0.064044 | -61.8622 | 59.4452 | -61.7569 | -61.9675 | 59.4727 | 0 | -0.16479 | -0.28839 | 59.6649 | -61.8988 | 0.050354 | -0.24719 | -0.054932 | -0.16022 | -0.21973 | -0.091553 | -0.027466 | -0.10529 | 61.6425 | 61.5189 | 121.2799 | 121.2524 | -0.054932 | 121.4722 | 61.8073 | -0.091553 | 121.2524 | -0.054932 | 61.8073 | 121.2799 | 121.4722 | -121.4493 | -121.5912
228.4531 | 121.7743 | -61.6653 | 59.816 | -0.070572 | 0.016408 | 0.011333 | 0.0021021 | 0.056249 | -0.0046313 | 0.065753 | -61.6837 | 59.5596 | -61.5692 | -61.7386 | 59.7244 | 0.32959 | 0.21973 | 0.3891 | 59.761 | -61.7569 | 0.09613 | -0.25635 | -0.018311 | -0.073242 | -0.091553 | -0.091553 | -0.054932 | -0.11444 | 61.8851 | 62.0544 | 121.3898 | 121.225 | -0.018311 | 121.4264 | 61.9949 | -0.091553 | 121.225 | -0.018311 | 61.9949 | 121.3898 | 121.4264 | -121.3852 | -121.5729
230.125 | 121.7377 | -61.7889 | 59.697 | 0.02861 | 0.015127 | 0.012828 | 0.012356 | 0.058599 | -0.0074085 | 0.065112 | -61.8668 | 59.4543 | -61.7432 | -61.9583 | 59.4772 | 0.022888 | -0.16022 | -0.28381 | 59.6512 | -61.8896 | 0.045776 | -0.24261 | -0.07782 | -0.16937 | -0.21973 | -0.10071 | -0.045776 | -0.1236 | 61.6287 | 61.5051 | 121.2662 | 121.2433 | -0.07782 | 121.4401 | 61.8118 | -0.10071 | 121.2433 | -0.07782 | 61.8118 | 121.2662 | 121.4401 | -121.4401 | -121.5866
231.8594 | 121.7834 | -61.6974 | 59.7656 | 0.097275 | 0.014913 | 0.01411 | 0.0059473 | 0.062444 | -0.0069811 | 0.06554 | -61.8027 | 59.4223 | -61.7111 | -61.8713 | 59.5825 | 0.009155 | -0.39825 | -0.24261 | 59.61 | -61.8576 | -0.013733 | -0.34332 | -0.10529 | -0.17395 | -0.1831 | -0.16022 | -0.15564 | -0.091552 | 61.2991 | 61.4548 | 121.2799 | 121.1197 | -0.10529 | 121.3074 | 61.7065 | -0.16022 | 121.1197 | -0.10529 | 61.7065 | 121.2799 | 121.3074 | -121.4767 | -121.6232
233.5938 | 121.788 | -61.6837 | 59.7839 | 0.14305 | 0.015554 | 0.014751 | 0.0025293 | 0.05689 | -0.0056995 | 0.065753 | -61.7798 | 59.4452 | -61.6791 | -61.8439 | 59.61 | 0.036621 | -0.28839 | -0.09613 | 59.6237 | -61.8439 | 0.004578 | -0.33875 | -0.09613 | -0.16022 | -0.17395 | -0.16022 | -0.16022 | -0.10071 | 61.3953 | 61.5875 | 121.2936 | 121.1288 | -0.09613 | 121.3074 | 61.7203 | -0.16022 | 121.1288 | -0.09613 | 61.7203 | 121.2936 | 121.3074 | -121.463 | -121.6278
235.3438 | 121.7468 | -61.7615 | 59.7427 | -0.2079 | 0.016195 | 0.0098373 | 0.0061609 | 0.056463 | -0.0069811 | 0.065967 | -61.7844 | 59.5917 | -61.6287 | -61.8622 | 59.5825 | 0.30212 | 0.42114 | 0.25177 | 59.7794 | -61.7935 | 0.13275 | -0.15106 | -0.022888 | -0.10071 | -0.16022 | -0.032043 | 0.036621 | -0.15564 | 62.1826 | 62.0132 | 121.344 | 121.3531 | -0.022888 | 121.5408 | 62.0636 | -0.032043 | 121.3531 | -0.022888 | 62.0636 | 121.344 | 121.5408 | -121.3715 | -121.5363
237.0469 | 121.6782 | -61.8256 | 59.729 | -0.062942 | 0.01534 | 0.011333 | 0.0078699 | 0.05924 | -0.0076221 | 0.064044 | -61.7935 | 59.4818 | -61.7111 | -61.8805 | 59.5459 | 0.16022 | -0.036621 | -0.07782 | 59.6649 | -61.8622 | 0.11444 | -0.24719 | 0.032044 | -0.054931 | -0.18311 | -0.036621 | -0.064087 | -0.082397 | 61.7889 | 61.7477 | 121.3715 | 121.3074 | 0.032044 | 121.4905 | 61.9858 | -0.036621 | 121.3074 | 0.032044 | 61.9858 | 121.3715 | 121.4905 | -121.4401 | -121.5912
238.7969 | 121.7285 | -61.7981 | 59.7015 | -0.017166 | 0.016195 | 0.012401 | 0.0063745 | 0.059667 | -0.0059131 | 0.063403 | -61.8118 | 59.4681 | -61.7157 | -61.9171 | 59.523 | 0.082397 | -0.12817 | -0.19684 | 59.6558 | -61.8713 | 0.082398 | -0.23346 | -0.013733 | -0.11902 | -0.17853 | -0.073242 | -0.045776 | -0.096131 | 61.6699 | 61.6013 | 121.3211 | 121.2662 | -0.013733 | 121.4539 | 61.8805 | -0.073242 | 121.2662 | -0.013733 | 61.8805 | 121.3211 | 121.4539 | -121.4172 | -121.5729
240.5469 | 121.8292 | -61.6516 | 59.8343 | 0.082016 | 0.016622 | 0.014751 | 0.0016749 | 0.059667 | -0.0039905 | 0.064685 | -61.7706 | 59.4727 | -61.6104 | -61.8439 | 59.6191 | 0.091553 | -0.11444 | -0.013733 | 59.6741 | -61.8027 | 0.041198 | -0.36163 | -0.11902 | -0.19226 | -0.21515 | -0.15106 | -0.16022 | -0.16022 | 61.5372 | 61.6379 | 121.2708 | 121.1243 | -0.11902 | 121.3257 | 61.7432 | -0.15106 | 121.1243 | -0.11902 | 61.7432 | 121.2708 | 121.3257 | -121.4447 | -121.637
242.2344 | 121.8246 | -61.7432 | 59.7107 | 0.11253 | 0.018972 | 0.01411 | 0.0072291 | 0.058599 | -0.0078357 | 0.064044 | -61.8668 | 59.4955 | -61.7294 | -61.9675 | 59.4818 | -0.09613 | -0.35706 | -0.37537 | 59.6466 | -61.9217 | 0.013733 | -0.21515 | -0.1236 | -0.2243 | -0.22888 | -0.17853 | -0.064087 | -0.13733 | 61.3861 | 61.3678 | 121.225 | 121.2387 | -0.1236 | 121.3898 | 61.647 | -0.17853 | 121.2387 | -0.1236 | 61.647 | 121.225 | 121.3898 | -121.4401 | -121.6324
243.9844 | 121.7056 | -61.7065 | 59.8297 | -0.1545 | 0.01534 | 0.013042 | 0.0027429 | 0.057531 | -0.0039905 | 0.066394 | -61.6333 | 59.5734 | -61.5463 | -61.7157 | 59.7427 | 0.41199 | 0.31586 | 0.49439 | 59.729 | -61.7477 | 0.16022 | -0.25635 | 0.073242 | -0.009155 | -0.086975 | -0.041199 | -0.10071 | -0.086975 | 62.0224 | 62.2009 | 121.4493 | 121.2799 | 0.073242 | 121.4355 | 62.1185 | -0.041199 | 121.2799 | 0.073242 | 62.1185 | 121.4493 | 121.4355 | -121.376 | -121.5775
245.7344 | 121.7056 | -61.8118 | 59.7427 | -0.11635 | 0.016195 | 0.010051 | 0.0089381 | 0.059667 | -0.0063403 | 0.065112 | -61.7981 | 59.523 | -61.7157 | -61.8713 | 59.5688 | 0.25635 | 0.17853 | 0.10071 | 59.7244 | -61.8073 | 0.096131 | -0.21973 | 0.013733 | -0.059509 | -0.17395 | 0.004578 | -0.018311 | -0.082398 | 61.9904 | 61.9125 | 121.3806 | 121.3348 | 0.013733 | 121.5363 | 62.0682 | 0.004578 | 121.3348 | 0.013733 | 62.0682 | 121.3806 | 121.5363 | -121.4584 | -121.55
247.4219 | 121.7148 | -61.8256 | 59.7198 | -0.13161 | 0.016195 | 0.014964 | 0.0082971 | 0.059026 | -0.0071947 | 0.06554 | -61.7889 | 59.5596 | -61.6653 | -61.8622 | 59.5688 | 0.24719 | 0.16479 | 0.10071 | 59.6741 | -61.8622 | 0.16022 | -0.16022 | 0.036622 | -0.036621 | -0.15106 | -0.036621 | -0.045777 | -0.1236 | 61.9904 | 61.9263 | 121.3943 | 121.3852 | 0.036622 | 121.4996 | 62.0728 | -0.036621 | 121.3852 | 0.036622 | 62.0728 | 121.3943 | 121.4996 | -121.3852 | -121.582
249.1562 | 121.6965 | -61.8439 | 59.729 | -0.078201 | 0.017049 | 0.014324 | 0.0095789 | 0.059026 | -0.0084765 | 0.066394 | -61.7935 | 59.5047 | -61.702 | -61.8896 | 59.5642 | 0.19684 | -0.018311 | -0.032043 | 59.6741 | -61.8439 | 0.14191 | -0.2243 | 0.050354 | -0.045776 | -0.1648 | 0 | -0.054932 | -0.091553 | 61.8256 | 61.8118 | 121.4081 | 121.3486 | 0.050354 | 121.5179 | 62.0407 | 0 | 121.3486 | 0.050354 | 62.0407 | 121.4081 | 121.5179 | -121.431 | -121.5729
250.8438 | 121.8475 | -61.6425 | 59.8022 | 0.059128 | 0.02004 | 0.013683 | -0.00024774 | 0.058812 | -0.0020679 | 0.065112 | -61.7615 | 59.5139 | -61.6104 | -61.8484 | 59.6146 | 0.12817 | 0.018311 | 0.07782 | 59.7015 | -61.8256 | 0.032043 | -0.28839 | -0.11902 | -0.20599 | -0.18768 | -0.18311 | -0.10071 | -0.15106 | 61.6608 | 61.7203 | 121.257 | 121.1563 | -0.11902 | 121.344 | 61.7706 | -0.18311 | 121.1563 | -0.11902 | 61.7706 | 121.257 | 121.344 | -121.4127 | -121.6278
252.5938 | 121.7056 | -61.8073 | 59.7153 | -0.055313 | 0.015554 | 0.0085555 | 0.0074427 | 0.059026 | -0.0052721 | 0.067035 | -61.8164 | 59.4818 | -61.7203 | -61.8713 | 59.5551 | 0.16022 | -0.050354 | -0.07782 | 59.6741 | -61.8439 | 0.086975 | -0.23346 | -0.009155 | -0.064087 | -0.16022 | -0.036621 | -0.041199 | -0.09613 | 61.7569 | 61.7294 | 121.3623 | 121.2891 | -0.009155 | 121.4813 | 61.9675 | -0.036621 | 121.2891 | -0.009155 | 61.9675 | 121.3623 | 121.4813 | -121.4355 | -121.5591
254.3281 | 121.8292 | -61.7523 | 59.7107 | 0.082016 | 0.019613 | 0.010692 | 0.0093653 | 0.060521 | -0.0080493 | 0.064899 | -61.8988 | 59.5047 | -61.7294 | -62.0041 | 59.4452 | -0.068665 | -0.22888 | -0.37994 | 59.6375 | -61.94 | 0.022888 | -0.20599 | -0.14648 | -0.25177 | -0.2655 | -0.18768 | -0.073242 | -0.16937 | 61.5234 | 61.3724 | 121.1975 | 121.257 | -0.14648 | 121.3898 | 61.6837 | -0.18768 | 121.257 | -0.14648 | 61.6837 | 121.1975 | 121.3898 | -121.4401 | -121.6507
256 | 121.8384 | -61.6379 | 59.8297 | 0.02861 | 0.014058 | 0.011119 | 0.00017946 | 0.058385 | -0.0067675 | 0.065753 | -61.7752 | 59.5093 | -61.647 | -61.8393 | 59.6191 | 0.13275 | 0.045776 | 0.11444 | 59.6924 | -61.7798 | -0.009156 | -0.32044 | -0.13733 | -0.20142 | -0.21057 | -0.14191 | -0.13733 | -0.12817 | 61.6837 | 61.7523 | 121.257 | 121.1472 | -0.13733 | 121.3303 | 61.7706 | -0.14191 | 121.1472 | -0.13733 | 61.7706 | 121.257 | 121.3303 | -121.4767 | -121.6095
257.7344 | 121.6919 | -61.6974 | 59.8526 | -0.18501 | 0.015554 | 0.011974 | 0.0035975 | 0.055181 | -0.0063403 | 0.064685 | -61.6379 | 59.5871 | -61.5326 | -61.7249 | 59.729 | 0.42572 | 0.34332 | 0.49439 | 59.7015 | -61.7615 | 0.16479 | -0.2655 | 0.05951 | -0.027466 | -0.1236 | -0.064087 | -0.15106 | -0.10529 | 62.0407 | 62.1918 | 121.4264 | 121.2845 | 0.05951 | 121.3989 | 62.1231 | -0.064087 | 121.2845 | 0.05951 | 62.1231 | 121.4264 | 121.3989 | -121.3852 | -121.6141
259.4844 | 121.7743 | -61.6882 | 59.7565 | 0.12016 | 0.016836 | 0.010478 | 0.0072291 | 0.060521 | -0.0050585 | 0.066394 | -61.8027 | 59.4131 | -61.734 | -61.8759 | 59.5642 | -0.009155 | -0.41657 | -0.24261 | 59.6237 | -61.8668 | -0.045777 | -0.34332 | -0.11444 | -0.18768 | -0.19226 | -0.17853 | -0.13275 | -0.068664 | 61.2717 | 61.4456 | 121.2524 | 121.1014 | -0.11444 | 121.3119 | 61.6791 | -0.17853 | 121.1014 | -0.11444 | 61.6791 | 121.2524 | 121.3119 | -121.4905 | -121.6232
261.1719 | 121.8246 | -61.7523 | 59.7107 | 0.089645 | 0.015767 | 0.011119 | 0.0091517 | 0.058599 | -0.0048449 | 0.065112 | -61.9125 | 59.4681 | -61.7661 | -61.9995 | 59.4406 | -0.07782 | -0.25635 | -0.38452 | 59.6283 | -61.9171 | -0.013733 | -0.24261 | -0.16022 | -0.24719 | -0.27008 | -0.16479 | -0.082397 | -0.14648 | 61.496 | 61.3678 | 121.1929 | 121.2204 | -0.16022 | 121.3806 | 61.6745 | -0.16479 | 121.2204 | -0.16022 | 61.6745 | 121.1929 | 121.3806 | -121.4767 | -121.6278
262.9219 | 121.6873 | -61.7157 | 59.8434 | -0.18501 | 0.01534 | 0.01176 | 0.0050929 | 0.05689 | -0.0071947 | 0.064258 | -61.6516 | 59.61 | -61.5372 | -61.734 | 59.7061 | 0.41199 | 0.32044 | 0.48065 | 59.6878 | -61.7706 | 0.17853 | -0.23346 | 0.064087 | -0.018311 | -0.13733 | -0.054932 | -0.15564 | -0.11444 | 62.0361 | 62.1964 | 121.4218 | 121.3257 | 0.064087 | 121.4035 | 62.1277 | -0.054932 | 121.3257 | 0.064087 | 62.1277 | 121.4218 | 121.4035 | -121.3806 | -121.6141
264.6719 | 121.6919 | -61.6699 | 59.8389 | -0.1545 | 0.015767 | 0.0068467 | 0.0035975 | 0.057104 | -0.0050585 | 0.065112 | -61.6516 | 59.5779 | -61.5646 | -61.7111 | 59.7427 | 0.40741 | 0.31586 | 0.50354 | 59.7519 | -61.7615 | 0.10529 | -0.26093 | 0.018311 | -0.041199 | -0.09613 | -0.091553 | -0.086975 | -0.086975 | 61.9858 | 62.1735 | 121.4127 | 121.2479 | 0.018311 | 121.4218 | 62.0773 | -0.091553 | 121.2479 | 0.018311 | 62.0773 | 121.4127 | 121.4218 | -121.4035 | -121.6003
266.3594 | 121.7743 | -61.7111 | 59.7702 | 0.17357 | 0.016622 | 0.012401 | 0.0070155 | 0.060094 | -0.0061267 | 0.066394 | -61.7706 | 59.4269 | -61.7203 | -61.853 | 59.5688 | 0.027466 | -0.37994 | -0.15564 | 59.6375 | -61.8668 | -0.009155 | -0.34332 | -0.059509 | -0.14191 | -0.20142 | -0.15564 | -0.13275 | -0.050354 | 61.3312 | 61.5555 | 121.2799 | 121.138 | -0.059509 | 121.3486 | 61.7386 | -0.15564 | 121.138 | -0.059509 | 61.7386 | 121.2799 | 121.3486 | -121.4905 | -121.637
268.1094 | 121.7743 | -61.6974 | 59.761 | 0.14305 | 0.015981 | 0.013469 | 0.0053065 | 0.059667 | -0.0071947 | 0.064044 | -61.7615 | 59.4223 | -61.6791 | -61.8622 | 59.5825 | 0.018311 | -0.41199 | -0.20599 | 59.6191 | -61.8256 | 0.018311 | -0.33874 | -0.064087 | -0.1648 | -0.17853 | -0.12817 | -0.14191 | -0.082398 | 61.2854 | 61.4914 | 121.2799 | 121.1197 | -0.064087 | 121.3165 | 61.7157 | -0.12817 | 121.1197 | -0.064087 | 61.7157 | 121.2799 | 121.3165 | -121.4401 | -121.5866
269.7969 | 121.8384 | -61.6516 | 59.8114 | 0.066757 | 0.016622 | 0.012615 | 0.0044519 | 0.053686 | -0.0042041 | 0.061694 | -61.7706 | 59.5093 | -61.6287 | -61.8393 | 59.6054 | 0.086975 | -0.073242 | 0.018311 | 59.6786 | -61.8301 | 0.022888 | -0.30212 | -0.11902 | -0.18768 | -0.20599 | -0.17853 | -0.13275 | -0.14191 | 61.5784 | 61.6699 | 121.257 | 121.1609 | -0.11902 | 121.3303 | 61.7386 | -0.17853 | 121.1609 | -0.11902 | 61.7386 | 121.257 | 121.3303 | -121.4401 | -121.6415
271.5469 | 121.8109 | -61.6562 | 59.8206 | -0.0019073 | 0.014486 | 0.014751 | 0.0048791 | 0.05454 | -0.0056995 | 0.064899 | -61.7477 | 59.5551 | -61.6196 | -61.821 | 59.6329 | 0.21515 | 0.11444 | 0.24261 | 59.6786 | -61.7935 | 0.036621 | -0.2655 | -0.091553 | -0.1648 | -0.18768 | -0.13733 | -0.14191 | -0.12817 | 61.7706 | 61.8988 | 121.2891 | 121.2112 | -0.091553 | 121.3348 | 61.8713 | -0.13733 | 121.2112 | -0.091553 | 61.8713 | 121.2891 | 121.3348 | -121.4401 | -121.6141
273.2812 | 121.7834 | -61.7157 | 59.7656 | 0.1812 | 0.015127 | 0.01176 | 0.0091517 | 0.057958 | -0.0052721 | 0.065112 | -61.8439 | 59.4406 | -61.7294 | -61.9034 | 59.523 | -0.041199 | -0.40741 | -0.27924 | 59.5871 | -61.8622 | -0.013733 | -0.32501 | -0.12817 | -0.18768 | -0.24262 | -0.14648 | -0.17853 | -0.11444 | 61.3083 | 61.4365 | 121.2387 | 121.1563 | -0.12817 | 121.3028 | 61.6745 | -0.14648 | 121.1563 | -0.12817 | 61.6745 | 121.2387 | 121.3028 | -121.4951 | -121.6278
275.0312 | 121.843 | -61.6516 | 59.8114 | 0.02861 | 0.018331 | 0.010265 | 0.0035975 | 0.057104 | -0.0065539 | 0.063617 | -61.7523 | 59.5322 | -61.6241 | -61.821 | 59.6008 | 0.11902 | 0.045776 | 0.10529 | 59.7107 | -61.8073 | 0.027465 | -0.27923 | -0.10071 | -0.16937 | -0.21057 | -0.15564 | -0.10071 | -0.12817 | 61.6974 | 61.7569 | 121.2524 | 121.1838 | -0.10071 | 121.3623 | 61.7706 | -0.15564 | 121.1838 | -0.10071 | 61.7706 | 121.2524 | 121.3623 | -121.4355 | -121.6187
276.7812 | 121.7972 | -61.7752 | 59.6832 | 0.066757 | 0.016836 | 0.010478 | 0.010647 | 0.056035 | -0.0078357 | 0.067889 | -61.8942 | 59.4406 | -61.7615 | -61.9766 | 59.4543 | -0.041199 | -0.19684 | -0.3479 | 59.642 | -61.9125 | 0.013733 | -0.24262 | -0.11902 | -0.20142 | -0.22888 | -0.13733 | -0.041199 | -0.13275 | 61.5784 | 61.4273 | 121.2296 | 121.2158 | -0.11902 | 121.4172 | 61.734 | -0.13733 | 121.2158 | -0.11902 | 61.734 | 121.2296 | 121.4172 | -121.4447 | -121.5958
278.4531 | 121.7377 | -61.7249 | 59.7931 | -0.13161 | 0.014913 | 0.011974 | 0.0050929 | 0.057531 | -0.0039905 | 0.062976 | -61.7432 | 59.61 | -61.5967 | -61.8439 | 59.61 | 0.33417 | 0.45319 | 0.32959 | 59.7473 | -61.7798 | 0.12817 | -0.18311 | -0.01831 | -0.11902 | -0.18311 | -0.054931 | -0.045777 | -0.14648 | 62.178 | 62.0544 | 121.3348 | 121.3348 | -0.01831 | 121.4722 | 62.059 | -0.054931 | 121.3348 | -0.01831 | 62.059 | 121.3348 | 121.4722 | -121.3898 | -121.5729
280.1875 | 121.7056 | -61.702 | 59.8297 | -0.16975 | 0.015981 | 0.0096237 | 0.0040247 | 0.055822 | -0.0050585 | 0.064899 | -61.6608 | 59.5505 | -61.5784 | -61.734 | 59.7015 | 0.39825 | 0.33875 | 0.4715 | 59.697 | -61.7981 | 0.1236 | -0.27924 | 0.041198 | -0.032044 | -0.12817 | -0.096131 | -0.13275 | -0.082398 | 62.0407 | 62.1735 | 121.4035 | 121.2524 | 0.041198 | 121.3989 | 62.1002 | -0.096131 | 121.2524 | 0.041198 | 62.1002 | 121.4035 | 121.3989 | -121.4081 | -121.6278
281.9375 | 121.6919 | -61.702 | 59.816 | -0.17738 | 0.016408 | 0.0096237 | 0.0040247 | 0.057744 | -0.0059131 | 0.064471 | -61.6562 | 59.5734 | -61.5601 | -61.7294 | 59.7244 | 0.41199 | 0.33417 | 0.47607 | 59.7565 | -61.7569 | 0.14191 | -0.24262 | 0.045776 | -0.027466 | -0.091553 | -0.054932 | -0.059509 | -0.09613 | 62.0361 | 62.178 | 121.4264 | 121.2753 | 0.045776 | 121.4584 | 62.114 | -0.054932 | 121.2753 | 0.045776 | 62.114 | 121.4264 | 121.4584 | -121.376 | -121.5729
283.6875 | 121.701 | -61.7981 | 59.7198 | -0.10109 | 0.015767 | 0.014964 | 0.011501 | 0.057317 | -0.0086901 | 0.064685 | -61.7798 | 59.5047 | -61.6837 | -61.8484 | 59.5688 | 0.25635 | 0.16479 | 0.09613 | 59.7107 | -61.8347 | 0.11444 | -0.21515 | 0.018311 | -0.050354 | -0.15106 | -0.036621 | -0.009156 | -0.09613 | 61.9629 | 61.8942 | 121.3669 | 121.3028 | 0.018311 | 121.5088 | 62.0544 | -0.036621 | 121.3028 | 0.018311 | 62.0544 | 121.3669 | 121.5088 | -121.4035 | -121.5546
285.375 | 121.7697 | -61.702 | 59.7702 | 0.15068 | 0.017476 | 0.013683 | 0.0061609 | 0.05924 | -0.0067675 | 0.06554 | -61.821 | 59.4681 | -61.6974 | -61.8942 | 59.5413 | -0.022888 | -0.40741 | -0.30212 | 59.6237 | -61.8622 | 0.004577 | -0.30212 | -0.11902 | -0.19226 | -0.22888 | -0.16022 | -0.14649 | -0.1236 | 61.2946 | 61.3998 | 121.2433 | 121.17 | -0.11902 | 121.3257 | 61.6791 | -0.16022 | 121.17 | -0.11902 | 61.6791 | 121.2433 | 121.3257 | -121.4676 | -121.6324
287.1406 | 121.7651 | -61.7889 | 59.7153 | 0.059128 | 0.016408 | 0.0094101 | 0.0087243 | 0.060094 | -0.0080493 | 0.06554 | -61.8942 | 59.4681 | -61.7752 | -61.9629 | 59.4681 | -0.013733 | -0.17395 | -0.31128 | 59.6558 | -61.8942 | 0.013732 | -0.24719 | -0.10529 | -0.17395 | -0.24719 | -0.10529 | -0.059509 | -0.11902 | 61.615 | 61.4777 | 121.257 | 121.257 | -0.10529 | 121.4447 | 61.7752 | -0.10529 | 121.257 | -0.10529 | 61.7752 | 121.257 | 121.4447 | -121.4905 | -121.6095
288.8281 | 121.7148 | -61.7294 | 59.8114 | -0.2079 | 0.016195 | 0.011333 | 0.0016749 | 0.057744 | -0.0046313 | 0.065753 | -61.6928 | 59.5688 | -61.5875 | -61.7798 | 59.6832 | 0.39368 | 0.41657 | 0.44861 | 59.7473 | -61.7752 | 0.14191 | -0.24261 | 0.036621 | -0.050354 | -0.12817 | -0.045777 | -0.064087 | -0.10529 | 62.146 | 62.178 | 121.4127 | 121.2982 | 0.036621 | 121.4767 | 62.1231 | -0.045777 | 121.2982 | 0.036621 | 62.1231 | 121.4127 | 121.4767 | -121.3989 | -121.5866
290.5781 | 121.7789 | -61.7065 | 59.7519 | 0.18883 | 0.016408 | 0.01646 | 0.0072291 | 0.058599 | -0.0082629 | 0.065753 | -61.8347 | 59.4315 | -61.7386 | -61.9125 | 59.5276 | -0.045776 | -0.40283 | -0.27924 | 59.6329 | -61.8942 | -0.032043 | -0.32043 | -0.12817 | -0.20599 | -0.2243 | -0.18768 | -0.11902 | -0.096131 | 61.3037 | 61.4273 | 121.2341 | 121.138 | -0.12817 | 121.3394 | 61.6608 | -0.18768 | 121.138 | -0.12817 | 61.6608 | 121.2341 | 121.3394 | -121.4905 | -121.6461
292.3281 | 121.7697 | -61.702 | 59.7702 | 0.12779 | 0.017049 | 0.010478 | 0.0029565 | 0.057531 | -0.0056995 | 0.066394 | -61.7661 | 59.4498 | -61.6928 | -61.8484 | 59.5963 | 0.041199 | -0.29755 | -0.10986 | 59.6237 | -61.8301 | 0.009155 | -0.32044 | -0.064087 | -0.14648 | -0.17395 | -0.12817 | -0.14649 | -0.073242 | 61.4044 | 61.5921 | 121.2982 | 121.1517 | -0.064087 | 121.3257 | 61.7432 | -0.12817 | 121.1517 | -0.064087 | 61.7432 | 121.2982 | 121.3257 | -121.463 | -121.6003
294 | 121.6827 | -61.7111 | 59.8389 | -0.18501 | 0.01534 | 0.010906 | 0.0029565 | 0.056035 | -0.0044177 | 0.063831 | -61.6608 | 59.5596 | -61.5555 | -61.7111 | 59.7198 | 0.41199 | 0.32044 | 0.48981 | 59.6924 | -61.7386 | 0.15564 | -0.27924 | 0.050354 | 0 | -0.11902 | -0.027465 | -0.14648 | -0.10529 | 62.0316 | 62.2009 | 121.431 | 121.2708 | 0.050354 | 121.4035 | 62.1231 | -0.027465 | 121.2708 | 0.050354 | 62.1231 | 121.431 | 121.4035 | -121.3943 | -121.5775
295.7344 | 121.7239 | -61.7111 | 59.7656 | -0.19264 | 0.014913 | 0.01411 | 0.0053065 | 0.056676 | -0.0054859 | 0.064044 | -61.734 | 59.5825 | -61.5967 | -61.8118 | 59.6283 | 0.35248 | 0.45319 | 0.35706 | 59.7565 | -61.7798 | 0.11444 | -0.1831 | -0.022888 | -0.10071 | -0.13733 | -0.068664 | -0.009155 | -0.13733 | 62.1643 | 62.0682 | 121.3394 | 121.2936 | -0.022888 | 121.4676 | 62.0636 | -0.068664 | 121.2936 | -0.022888 | 62.0636 | 121.3394 | 121.4676 | -121.3623 | -121.5454
297.4219 | 121.6827 | -61.702 | 59.848 | -0.16975 | 0.016195 | 0.01176 | 0.0027429 | 0.055181 | -0.0054859 | 0.067035 | -61.6516 | 59.5596 | -61.5601 | -61.7294 | 59.7015 | 0.40741 | 0.32959 | 0.48065 | 59.697 | -61.7889 | 0.14191 | -0.28839 | 0.050354 | -0.027466 | -0.14648 | -0.086975 | -0.15106 | -0.091552 | 62.0316 | 62.1826 | 121.4035 | 121.2616 | 0.050354 | 121.3989 | 62.1094 | -0.086975 | 121.2616 | 0.050354 | 62.1094 | 121.4035 | 121.3989 | -121.4081 | -121.637
299.1562 | 121.7285 | -61.7294 | 59.7656 | -0.2079 | 0.01534 | 0.013042 | 0.0076563 | 0.05454 | -0.0039905 | 0.064899 | -61.7432 | 59.6054 | -61.5921 | -61.8027 | 59.6191 | 0.35248 | 0.46692 | 0.35248 | 59.7656 | -61.7844 | 0.13733 | -0.16022 | -0.013733 | -0.073242 | -0.14648 | -0.054932 | 0 | -0.15106 | 62.1963 | 62.0819 | 121.3486 | 121.3348 | -0.013733 | 121.4951 | 62.0819 | -0.054932 | 121.3348 | -0.013733 | 62.0819 | 121.3486 | 121.4951 | -121.3577 | -121.55
300.9062 | 121.7743 | -61.6699 | 59.7794 | 0.1812 | 0.014058 | 0.011974 | 0.0072291 | 0.058385 | -0.0046313 | 0.064044 | -61.7661 | 59.4498 | -61.7065 | -61.8439 | 59.5917 | 0.022888 | -0.33875 | -0.13275 | 59.6191 | -61.8668 | -0.036621 | -0.32959 | -0.09613 | -0.17395 | -0.18768 | -0.19684 | -0.16022 | -0.059509 | 61.3312 | 61.5372 | 121.2616 | 121.1197 | -0.09613 | 121.2891 | 61.6928 | -0.19684 | 121.1197 | -0.09613 | 61.6928 | 121.2616 | 121.2891 | -121.4859 | -121.6461
302.5938 | 121.7651 | -61.6974 | 59.7702 | 0.15831 | 0.017263 | 0.011119 | 0.0070155 | 0.056463 | -0.0078357 | 0.064685 | -61.7752 | 59.4131 | -61.7111 | -61.853 | 59.5825 | 0.004578 | -0.39825 | -0.17395 | 59.6054 | -61.8622 | -0.013733 | -0.35706 | -0.07782 | -0.15564 | -0.18768 | -0.1648 | -0.1648 | -0.064087 | 61.2991 | 61.5234 | 121.2799 | 121.1105 | -0.07782 | 121.3028 | 61.702 | -0.1648 | 121.1105 | -0.07782 | 61.702 | 121.2799 | 121.3028 | -121.4813 | -121.6324
304.3438 | 121.8201 | -61.6287 | 59.816 | 0.02861 | 0.015981 | 0.0091965 | 0.0023157 | 0.055395 | -0.0044177 | 0.067462 | -61.7615 | 59.5276 | -61.6104 | -61.8393 | 59.6008 | 0.13275 | 0.068665 | 0.12817 | 59.6695 | -61.8073 | 0.01831 | -0.28839 | -0.13275 | -0.21057 | -0.21515 | -0.17853 | -0.14648 | -0.15106 | 61.6974 | 61.7569 | 121.2296 | 121.1563 | -0.13275 | 121.2982 | 61.7615 | -0.17853 | 121.1563 | -0.13275 | 61.7615 | 121.2296 | 121.2982 | -121.4264 | -121.6232
306.0312 | 121.8109 | -61.7386 | 59.6878 | 0.12016 | 0.01534 | 0.010692 | 0.0095789 | 0.056249 | -0.0069811 | 0.065753 | -61.8805 | 59.4406 | -61.7569 | -61.9583 | 59.4635 | -0.086975 | -0.32044 | -0.38452 | 59.6512 | -61.908 | -0.018311 | -0.24719 | -0.14191 | -0.21973 | -0.2243 | -0.16937 | -0.036621 | -0.1236 | 61.4182 | 61.3541 | 121.2021 | 121.1792 | -0.14191 | 121.3898 | 61.6516 | -0.16937 | 121.1792 | -0.14191 | 61.6516 | 121.2021 | 121.3898 | -121.4447 | -121.5958
307.7812 | 121.7239 | -61.702 | 59.8068 | -0.20027 | 0.016195 | 0.0064193 | 0.0027429 | 0.055822 | -0.0046313 | 0.066394 | -61.6837 | 59.5551 | -61.5784 | -61.7523 | 59.6786 | 0.40283 | 0.40741 | 0.45319 | 59.7748 | -61.7844 | 0.1236 | -0.25177 | 0.01831 | -0.050354 | -0.12817 | -0.082398 | -0.032044 | -0.10529 | 62.1094 | 62.1552 | 121.3806 | 121.257 | 0.01831 | 121.4767 | 62.1048 | -0.082398 | 121.257 | 0.01831 | 62.1048 | 121.3806 | 121.4767 | -121.3852 | -121.5912
309.4688 | 121.8201 | -61.6425 | 59.7839 | 0.059128 | 0.017263 | 0.0096237 | 0.0044519 | 0.056249 | -0.0044177 | 0.062335 | -61.7615 | 59.4955 | -61.6653 | -61.8393 | 59.5963 | 0.09613 | -0.045776 | 0.050354 | 59.7015 | -61.7935 | -0.022888 | -0.28839 | -0.11902 | -0.19684 | -0.18768 | -0.15106 | -0.082398 | -0.096131 | 61.5967 | 61.6928 | 121.2387 | 121.138 | -0.11902 | 121.344 | 61.7386 | -0.15106 | 121.138 | -0.11902 | 61.7386 | 121.2387 | 121.344 | -121.4493 | -121.5775
311.2188 | 121.7056 | -61.8073 | 59.7107 | -0.047684 | 0.017049 | 0.0079147 | 0.0093653 | 0.05689 | -0.0080493 | 0.064685 | -61.7844 | 59.4818 | -61.7203 | -61.853 | 59.5413 | 0.11444 | -0.07782 | -0.10986 | 59.697 | -61.853 | 0.086975 | -0.22888 | 0.022888 | -0.045776 | -0.16937 | -0.045776 | -0.013733 | -0.064087 | 61.7294 | 61.6974 | 121.3486 | 121.2891 | 0.022888 | 121.5042 | 61.9217 | -0.045776 | 121.2891 | 0.022888 | 61.9217 | 121.3486 | 121.5042 | -121.431 | -121.5637
312.9062 | 121.7285 | -61.7615 | 59.761 | -0.21553 | 0.016622 | 0.011333 | 0.0072291 | 0.057958 | -0.0052721 | 0.064044 | -61.7706 | 59.5917 | -61.6196 | -61.8347 | 59.61 | 0.32959 | 0.45776 | 0.3067 | 59.761 | -61.7981 | 0.14191 | -0.16937 | -0.009155 | -0.073242 | -0.15106 | -0.036621 | 0 | -0.15106 | 62.2192 | 62.0682 | 121.3715 | 121.3531 | -0.009155 | 121.5225 | 62.0911 | -0.036621 | 121.3531 | -0.009155 | 62.0911 | 121.3715 | 121.5225 | -121.3806 | -121.5591
314.6562 | 121.8201 | -61.7432 | 59.697 | 0.089645 | 0.01534 | 0.0089829 | 0.0078699 | 0.057317 | -0.0067675 | 0.064471 | -61.8942 | 59.4589 | -61.7386 | -61.9766 | 59.4681 | -0.082397 | -0.29755 | -0.37994 | 59.6512 | -61.8896 | 0.004578 | -0.23804 | -0.15106 | -0.23346 | -0.22888 | -0.14648 | -0.045776 | -0.15564 | 61.4456 | 61.3632 | 121.2112 | 121.2021 | -0.15106 | 121.3943 | 61.6608 | -0.14648 | 121.2021 | -0.15106 | 61.6608 | 121.2112 | 121.3943 | -121.4355 | -121.5866
316.3438 | 121.7743 | -61.6425 | 59.8251 | -0.032425 | 0.015981 | 0.013255 | 0.0014613 | 0.056035 | -0.0050585 | 0.065967 | -61.6791 | 59.5551 | -61.5738 | -61.7432 | 59.697 | 0.32044 | 0.20599 | 0.38452 | 59.7107 | -61.7661 | 0.068664 | -0.27008 | -0.036621 | -0.10071 | -0.12817 | -0.1236 | -0.11444 | -0.10529 | 61.8484 | 62.027 | 121.3394 | 121.1975 | -0.036621 | 121.3531 | 61.9629 | -0.1236 | 121.1975 | -0.036621 | 61.9629 | 121.3394 | 121.3531 | -121.3989 | -121.5912
318.0938 | 121.6827 | -61.8118 | 59.729 | -0.040054 | 0.017476 | 0.013042 | 0.0087243 | 0.057317 | -0.0054859 | 0.064471 | -61.7844 | 59.5093 | -61.702 | -61.8622 | 59.5505 | 0.15564 | -0.059509 | -0.082397 | 59.6603 | -61.8622 | 0.10986 | -0.21973 | 0.027466 | -0.050354 | -0.17853 | -0.050354 | -0.068665 | -0.082398 | 61.7523 | 61.7294 | 121.3623 | 121.3211 | 0.027466 | 121.4722 | 61.9675 | -0.050354 | 121.3211 | 0.027466 | 61.9675 | 121.3623 | 121.4722 | -121.431 | -121.5912
319.7812 | 121.7056 | -61.702 | 59.8572 | -0.11635 | 0.014058 | 0.0087693 | 0.0023157 | 0.058172 | -0.0052721 | 0.062763 | -61.6379 | 59.5459 | -61.5601 | -61.702 | 59.7382 | 0.38452 | 0.28381 | 0.4715 | 59.7427 | -61.7249 | 0.14191 | -0.31128 | 0.064087 | 0 | -0.11902 | -0.022889 | -0.11444 | -0.077819 | 61.9858 | 62.1735 | 121.4401 | 121.2479 | 0.064087 | 121.4447 | 62.0865 | -0.022889 | 121.2479 | 0.064087 | 62.0865 | 121.4401 | 121.4447 | -121.4172 | -121.582
321.5156 | 121.7697 | -61.7065 | 59.7565 | 0.15068 | 0.012777 | 0.010478 | 0.0055201 | 0.057531 | -0.0074085 | 0.066394 | -61.7661 | 59.4269 | -61.6882 | -61.8301 | 59.5825 | 0.018311 | -0.35248 | -0.12817 | 59.61 | -61.8484 | 0.018311 | -0.32959 | -0.059509 | -0.1236 | -0.17395 | -0.14191 | -0.14648 | -0.07782 | 61.3541 | 61.5784 | 121.2891 | 121.1334 | -0.059509 | 121.3165 | 61.7249 | -0.14191 | 121.1334 | -0.059509 | 61.7249 | 121.2891 | 121.3165 | -121.4447 | -121.6049
323.2656 | 121.701 | -61.6882 | 59.8297 | -0.13161 | 0.017049 | 0.015392 | 0.0040247 | 0.056035 | -0.0037769 | 0.064471 | -61.6562 | 59.5322 | -61.5784 | -61.6882 | 59.7198 | 0.3891 | 0.29297 | 0.4715 | 59.7061 | -61.7523 | 0.10986 | -0.29755 | 0.032043 | 0 | -0.10986 | -0.064087 | -0.1236 | -0.07782 | 61.9812 | 62.1597 | 121.4081 | 121.2204 | 0.032043 | 121.3943 | 62.0773 | -0.064087 | 121.2204 | 0.032043 | 62.0773 | 121.4081 | 121.3943 | -121.4081 | -121.582
325.0156 | 121.7056 | -61.7935 | 59.729 | -0.14687 | 0.015127 | 0.010051 | 0.0089381 | 0.057531 | -0.0063403 | 0.065112 | -61.7844 | 59.5276 | -61.6791 | -61.8576 | 59.5688 | 0.26093 | 0.17853 | 0.11902 | 59.6878 | -61.8347 | 0.11444 | -0.20142 | 0.009155 | -0.064087 | -0.16022 | -0.041199 | -0.041199 | -0.10529 | 61.972 | 61.9125 | 121.3623 | 121.3211 | 0.009155 | 121.4813 | 62.0544 | -0.041199 | 121.3211 | 0.009155 | 62.0544 | 121.3623 | 121.4813 | -121.4081 | -121.5637
326.7656 | 121.8155 | -61.7706 | 59.7153 | 0.11253 | 0.017263 | 0.011546 | 0.0093653 | 0.057958 | -0.0080493 | 0.064899 | -61.8896 | 59.4177 | -61.7661 | -61.9766 | 59.4543 | -0.086975 | -0.29297 | -0.39368 | 59.6741 | -61.8988 | 0.004578 | -0.29755 | -0.11902 | -0.20599 | -0.26093 | -0.12817 | -0.041199 | -0.1236 | 61.4777 | 61.377 | 121.225 | 121.1884 | -0.11902 | 121.4447 | 61.6837 | -0.12817 | 121.1884 | -0.11902 | 61.6837 | 121.225 | 121.4447 | -121.4813 | -121.6141
328.4531 | 121.6736 | -61.821 | 59.6832 | -0.070572 | 0.012563 | 0.01176 | 0.011501 | 0.058172 | -0.0061267 | 0.064471 | -61.7844 | 59.4772 | -61.7111 | -61.8576 | 59.5505 | 0.1831 | -0.013733 | -0.032043 | 59.6649 | -61.8576 | 0.10986 | -0.20599 | 0.036621 | -0.036621 | -0.13275 | -0.036621 | -0.018311 | -0.073242 | 61.8073 | 61.7889 | 121.3715 | 121.2982 | 0.036621 | 121.4859 | 62.0041 | -0.036621 | 121.2982 | 0.036621 | 62.0041 | 121.3715 | 121.4859 | -121.3943 | -121.5408
330.2188 | 121.6644 | -61.8301 | 59.6878 | -0.055313 | 0.016836 | 0.01411 | 0.0068017 | 0.056676 | -0.0097583 | 0.064258 | -61.7935 | 59.4818 | -61.6837 | -61.8439 | 59.5642 | 0.1831 | -0.041199 | -0.054932 | 59.6832 | -61.853 | 0.14648 | -0.20599 | 0.036621 | -0.013733 | -0.1236 | -0.022888 | -0.004577 | -0.10986 | 61.7889 | 61.7752 | 121.3943 | 121.312 | 0.036621 | 121.5134 | 62.0132 | -0.022888 | 121.312 | 0.036621 | 62.0132 | 121.3943 | 121.5134 | -121.3715 | -121.5408
331.9844 | 121.7377 | -61.7569 | 59.7656 | -0.20027 | 0.016195 | 0.0085555 | 0.0027429 | 0.05689 | -0.0071947 | 0.063617 | -61.7935 | 59.5963 | -61.615 | -61.8622 | 59.5963 | 0.3067 | 0.4303 | 0.25635 | 59.7839 | -61.7752 | 0.14191 | -0.16937 | -0.036621 | -0.10529 | -0.16937 | -0.018311 | 0.018311 | -0.17853 | 62.1872 | 62.0132 | 121.3531 | 121.3531 | -0.036621 | 121.5408 | 62.0636 | -0.018311 | 121.3531 | -0.036621 | 62.0636 | 121.3531 | 121.5408 | -121.3806 | -121.5408
333.6719 | 121.6919 | -61.702 | 59.8297 | -0.13161 | 0.016622 | 0.012828 | 0.0012475 | 0.053686 | -0.0065539 | 0.064899 | -61.6333 | 59.5734 | -61.5555 | -61.702 | 59.7565 | 0.3891 | 0.28839 | 0.46234 | 59.7656 | -61.7432 | 0.14648 | -0.25635 | 0.068664 | 0 | -0.073242 | -0.041199 | -0.064087 | -0.07782 | 61.9904 | 62.1643 | 121.4584 | 121.2753 | 0.068664 | 121.4676 | 62.0911 | -0.041199 | 121.2753 | 0.068664 | 62.0911 | 121.4584 | 121.4676 | -121.3852 | -121.5729
335.4219 | 121.7148 | -61.8027 | 59.729 | -0.0095368 | 0.018331 | 0.013683 | 0.0091517 | 0.058385 | -0.0074085 | 0.066608 | -61.7935 | 59.4543 | -61.7111 | -61.8988 | 59.5322 | 0.10529 | -0.10071 | -0.16479 | 59.6786 | -61.8347 | 0.091552 | -0.27466 | 0.009155 | -0.096131 | -0.19684 | -0.032044 | -0.050354 | -0.082397 | 61.702 | 61.6379 | 121.3348 | 121.257 | 0.009155 | 121.4813 | 61.908 | -0.032044 | 121.257 | 0.009155 | 61.908 | 121.3348 | 121.4813 | -121.4401 | -121.5637
337.125 | 121.6782 | -61.8118 | 59.7153 | -0.055313 | 0.016622 | 0.0083419 | 0.0085107 | 0.05924 | -0.0082629 | 0.066394 | -61.7935 | 59.4727 | -61.7157 | -61.8851 | 59.5322 | 0.13275 | -0.07782 | -0.1236 | 59.6786 | -61.8622 | 0.096131 | -0.24262 | 0.018311 | -0.073242 | -0.18311 | -0.050354 | -0.036621 | -0.07782 | 61.734 | 61.6882 | 121.344 | 121.2845 | 0.018311 | 121.4905 | 61.9446 | -0.050354 | 121.2845 | 0.018311 | 61.9446 | 121.344 | 121.4905 | -121.431 | -121.5775
338.8594 | 121.7834 | -61.7111 | 59.7427 | 0.21935 | 0.018758 | 0.010051 | 0.0048791 | 0.057744 | -0.0061267 | 0.063617 | -61.853 | 59.4406 | -61.7157 | -61.9308 | 59.5184 | -0.045776 | -0.38452 | -0.31128 | 59.642 | -61.8576 | -0.004577 | -0.30212 | -0.14191 | -0.21973 | -0.2243 | -0.14648 | -0.10071 | -0.13733 | 61.3266 | 61.3998 | 121.2296 | 121.1517 | -0.14191 | 121.3531 | 61.6653 | -0.14648 | 121.1517 | -0.14191 | 61.6653 | 121.2296 | 121.3531 | -121.4584 | -121.6003
340.5938 | 121.7651 | -61.7752 | 59.6832 | 0.074387 | 0.017263 | 0.01176 | 0.0080835 | 0.058599 | -0.0078357 | 0.06618 | -61.8713 | 59.4543 | -61.7432 | -61.9675 | 59.4452 | 0.009155 | -0.16022 | -0.31586 | 59.6786 | -61.8805 | 0.032044 | -0.22888 | -0.09613 | -0.19226 | -0.23804 | -0.10529 | -0.004578 | -0.12817 | 61.615 | 61.4594 | 121.2204 | 121.2296 | -0.09613 | 121.4539 | 61.7844 | -0.10529 | 121.2296 | -0.09613 | 61.7844 | 121.2204 | 121.4539 | -121.4264 | -121.5637
342.3438 | 121.7697 | -61.6928 | 59.7748 | 0.097275 | 0.016195 | 0.012615 | 0.0027429 | 0.057531 | -0.0039905 | 0.063831 | -61.7569 | 59.4589 | -61.6562 | -61.8622 | 59.5917 | 0.036621 | -0.26093 | -0.073242 | 59.642 | -61.8484 | 0.036621 | -0.31586 | -0.064087 | -0.16937 | -0.1831 | -0.15564 | -0.13275 | -0.10071 | 61.4319 | 61.6196 | 121.2845 | 121.1517 | -0.064087 | 121.3348 | 61.7294 | -0.15564 | 121.1517 | -0.064087 | 61.7294 | 121.2845 | 121.3348 | -121.431 | -121.6232
344.0781 | 121.7651 | -61.7157 | 59.761 | 0.14305 | 0.014272 | 0.011119 | 0.0055201 | 0.058812 | -0.0078357 | 0.064899 | -61.7798 | 59.3857 | -61.7157 | -61.8484 | 59.5642 | 0.004578 | -0.40741 | -0.2243 | 59.6329 | -61.8576 | 0 | -0.37537 | -0.064087 | -0.13275 | -0.19684 | -0.14191 | -0.12817 | -0.064087 | 61.3083 | 61.4914 | 121.2799 | 121.1014 | -0.064087 | 121.3486 | 61.7203 | -0.14191 | 121.1014 | -0.064087 | 61.7203 | 121.2799 | 121.3486 | -121.4767 | -121.6187
345.8281 | 121.8246 | -61.6516 | 59.7794 | 0.051498 | 0.015981 | 0.010906 | 0.0027429 | 0.055181 | -0.0050585 | 0.065112 | -61.7569 | 59.5093 | -61.6104 | -61.853 | 59.5917 | 0.11444 | -0.018311 | 0.054932 | 59.6695 | -61.8439 | 0.041198 | -0.27008 | -0.10529 | -0.20142 | -0.18768 | -0.19226 | -0.10986 | -0.14648 | 61.6333 | 61.7065 | 121.2433 | 121.1609 | -0.10529 | 121.3211 | 61.7661 | -0.19226 | 121.1609 | -0.10529 | 61.7661 | 121.2433 | 121.3211 | -121.3898 | -121.6232
347.5312 | 121.7377 | -61.7065 | 59.7473 | -0.21553 | 0.015767 | 0.010906 | 0.0055201 | 0.056463 | -0.0069811 | 0.064471 | -61.7569 | 59.5917 | -61.6333 | -61.8256 | 59.5917 | 0.32044 | 0.45776 | 0.33417 | 59.7839 | -61.8118 | 0.073242 | -0.15564 | -0.050354 | -0.11902 | -0.15564 | -0.10529 | 0.036622 | -0.1236 | 62.1643 | 62.0407 | 121.2982 | 121.2982 | -0.050354 | 121.4905 | 62.027 | -0.10529 | 121.2982 | -0.050354 | 62.027 | 121.2982 | 121.4905 | -121.3806 | -121.5591
349.2656 | 121.8109 | -61.6333 | 59.8114 | 0.013352 | 0.014699 | 0.012615 | 0.0027429 | 0.05689 | -0.0050585 | 0.066821 | -61.7615 | 59.5093 | -61.6104 | -61.8301 | 59.6191 | 0.17395 | 0.10071 | 0.17853 | 59.6924 | -61.8301 | 0.022888 | -0.30212 | -0.12817 | -0.19684 | -0.19226 | -0.19684 | -0.11902 | -0.15106 | 61.734 | 61.8118 | 121.2524 | 121.1426 | -0.12817 | 121.3257 | 61.8073 | -0.19684 | 121.1426 | -0.12817 | 61.8073 | 121.2524 | 121.3257 | -121.4218 | -121.6415
351.0156 | 121.7377 | -61.7615 | 59.761 | -0.19264 | 0.016195 | 0.01176 | 0.0059473 | 0.055181 | -0.0091173 | 0.064685 | -61.7844 | 59.5596 | -61.6516 | -61.853 | 59.5688 | 0.30212 | 0.37994 | 0.2243 | 59.7656 | -61.8027 | 0.10986 | -0.20142 | -0.022888 | -0.091552 | -0.19226 | -0.041198 | 0.004578 | -0.13275 | 62.1414 | 61.9858 | 121.3303 | 121.3211 | -0.022888 | 121.5271 | 62.0636 | -0.041198 | 121.3211 | -0.022888 | 62.0636 | 121.3303 | 121.5271 | -121.4127 | -121.5637
352.7188 | 121.7377 | -61.7981 | 59.6878 | 0.043869 | 0.017476 | 0.011546 | 0.0085107 | 0.058385 | -0.0082629 | 0.065112 | -61.8622 | 59.4589 | -61.7432 | -61.9583 | 59.4498 | 0.013733 | -0.16022 | -0.27008 | 59.6649 | -61.8713 | 0.054932 | -0.22888 | -0.064087 | -0.16022 | -0.23804 | -0.073242 | -0.022888 | -0.11902 | 61.6379 | 61.528 | 121.2479 | 121.257 | -0.064087 | 121.463 | 61.8118 | -0.073242 | 121.257 | -0.064087 | 61.8118 | 121.2479 | 121.463 | -121.431 | -121.5591
354.4688 | 121.6965 | -61.8256 | 59.7107 | -0.0095368 | 0.014699 | 0.011974 | 0.0085107 | 0.057958 | -0.0076221 | 0.066821 | -61.821 | 59.4635 | -61.7065 | -61.9171 | 59.4864 | 0.064087 | -0.13275 | -0.21515 | 59.6603 | -61.908 | 0.11902 | -0.24719 | 0.004578 | -0.091552 | -0.2243 | -0.082397 | -0.050354 | -0.11444 | 61.6928 | 61.6104 | 121.312 | 121.2891 | 0.004578 | 121.4859 | 61.8896 | -0.082397 | 121.2891 | 0.004578 | 61.8896 | 121.312 | 121.4859 | -121.4172 | -121.6187
356.2188 | 121.8018 | -61.6013 | 59.8068 | 0.02861 | 0.01534 | 0.0087693 | 0.00017946 | 0.057317 | -0.0052721 | 0.063831 | -61.7569 | 59.5276 | -61.6058 | -61.8393 | 59.6191 | 0.15564 | 0.082397 | 0.14648 | 59.7107 | -61.7981 | -0.004578 | -0.27924 | -0.15564 | -0.23804 | -0.18768 | -0.19684 | -0.096131 | -0.15106 | 61.6837 | 61.7477 | 121.2204 | 121.1288 | -0.15564 | 121.3119 | 61.7569 | -0.19684 | 121.1288 | -0.15564 | 61.7569 | 121.2204 | 121.3119 | -121.4127 | -121.6049
357.9062 | 121.7468 | -61.6928 | 59.7473 | 0.15831 | 0.017476 | 0.012401 | 0.0061609 | 0.059667 | -0.0067675 | 0.062763 | -61.7661 | 59.4269 | -61.6791 | -61.8622 | 59.5505 | 0.004578 | -0.41199 | -0.19684 | 59.6283 | -61.8942 | 0.013733 | -0.32043 | -0.073242 | -0.16937 | -0.19684 | -0.20142 | -0.11902 | -0.086975 | 61.2808 | 61.496 | 121.2433 | 121.1197 | -0.073242 | 121.3211 | 61.6974 | -0.20142 | 121.1197 | -0.073242 | 61.6974 | 121.2433 | 121.3211 | -121.4264 | -121.6415
359.6562 | 121.843 | -61.6425 | 59.8114 | 0.043869 | 0.014486 | 0.010478 | 0.0016749 | 0.056463 | -0.0071947 | 0.063617 | -61.7432 | 59.5001 | -61.6104 | -61.8347 | 59.6008 | 0.1236 | 0.036621 | 0.091553 | 59.697 | -61.7981 | 0.032043 | -0.31128 | -0.10071 | -0.19226 | -0.21057 | -0.15564 | -0.11444 | -0.13275 | 61.6791 | 61.734 | 121.2433 | 121.1426 | -0.10071 | 121.3394 | 61.7661 | -0.15564 | 121.1426 | -0.10071 | 61.7661 | 121.2433 | 121.3394 | -121.4218 | -121.6095
361.3438 | 121.7148 | -61.702 | 59.7977 | -0.22316 | 0.013204 | 0.012828 | 0.0065881 | 0.058385 | -0.0080493 | 0.066394 | -61.6837 | 59.5596 | -61.6058 | -61.7661 | 59.6741 | 0.39368 | 0.42572 | 0.44861 | 59.761 | -61.7615 | 0.09613 | -0.23804 | 0.01831 | -0.064087 | -0.1236 | -0.05951 | -0.036621 | -0.07782 | 62.1277 | 62.1506 | 121.376 | 121.2616 | 0.01831 | 121.463 | 62.0956 | -0.05951 | 121.2616 | 0.01831 | 62.0956 | 121.376 | 121.463 | -121.4035 | -121.5591
363.0938 | 121.669 | -61.6745 | 59.8526 | -0.19264 | 0.015767 | 0.0087693 | 0.0063745 | 0.056463 | -0.0065539 | 0.064685 | -61.6425 | 59.5688 | -61.5601 | -61.6974 | 59.7244 | 0.42114 | 0.32501 | 0.48981 | 59.7107 | -61.7615 | 0.11444 | -0.28381 | 0.032044 | -0.022888 | -0.12817 | -0.086975 | -0.14191 | -0.082397 | 61.9995 | 62.1643 | 121.3989 | 121.2433 | 0.032044 | 121.3852 | 62.0956 | -0.086975 | 121.2433 | 0.032044 | 62.0956 | 121.3989 | 121.3852 | -121.4127 | -121.6141
364.7812 | 121.7926 | -61.6699 | 59.7794 | 0.1049 | 0.015767 | 0.0087693 | 0.0068017 | 0.058385 | -0.0074085 | 0.062976 | -61.734 | 59.436 | -61.6653 | -61.8439 | 59.5825 | 0.064087 | -0.2655 | -0.086975 | 59.6191 | -61.8073 | 0.004578 | -0.34332 | -0.064087 | -0.17395 | -0.19684 | -0.13733 | -0.16022 | -0.068665 | 61.4044 | 61.5829 | 121.2524 | 121.106 | -0.064087 | 121.2891 | 61.734 | -0.13733 | 121.106 | -0.064087 | 61.734 | 121.2524 | 121.2891 | -121.4447 | -121.5866
366.5156 | 121.8155 | -61.6516 | 59.8114 | 0.15068 | 0.014913 | 0.012401 | 0.0057337 | 0.056463 | -0.0061267 | 0.064685 | -61.7569 | 59.4543 | -61.6699 | -61.8347 | 59.5779 | 0.064087 | -0.17853 | -0.027466 | 59.6695 | -61.8027 | -0.018311 | -0.35705 | -0.10529 | -0.18311 | -0.23346 | -0.15106 | -0.14191 | -0.086975 | 61.4731 | 61.6241 | 121.2296 | 121.106 | -0.10529 | 121.3211 | 61.7157 | -0.15106 | 121.106 | -0.10529 | 61.7157 | 121.2296 | 121.3211 | -121.4813 | -121.6141
368.2031 | 121.6736 | -61.6882 | 59.8572 | -0.19264 | 0.015981 | 0.011546 | 0.0065881 | 0.057531 | -0.0046313 | 0.064258 | -61.6379 | 59.5688 | -61.5372 | -61.6974 | 59.7244 | 0.40741 | 0.32959 | 0.50354 | 59.7382 | -61.7523 | 0.15106 | -0.28839 | 0.050354 | -0.009156 | -0.13275 | -0.064087 | -0.11902 | -0.10071 | 62.0178 | 62.1918 | 121.4127 | 121.257 | 0.050354 | 121.4264 | 62.0956 | -0.064087 | 121.257 | 0.050354 | 62.0956 | 121.4127 | 121.4264 | -121.3943 | -121.6095
369.9375 | 121.8063 | -61.6241 | 59.8251 | 0.0057222 | 0.016622 | 0.01176 | 0.0044519 | 0.056249 | -0.0061267 | 0.064258 | -61.7294 | 59.5139 | -61.6425 | -61.8118 | 59.6146 | 0.15106 | 0.10071 | 0.16022 | 59.7061 | -61.7661 | -0.01831 | -0.31128 | -0.10528 | -0.18768 | -0.21057 | -0.14191 | -0.11902 | -0.086975 | 61.7249 | 61.7844 | 121.2387 | 121.138 | -0.10528 | 121.3303 | 61.7752 | -0.14191 | 121.138 | -0.10528 | 61.7752 | 121.2387 | 121.3303 | -121.4676 | -121.5912
371.6719 | 121.8018 | -61.6241 | 59.8068 | 0.02861 | 0.017263 | 0.010478 | 0.0074427 | 0.054754 | -0.0048449 | 0.064899 | -61.7432 | 59.523 | -61.615 | -61.8027 | 59.61 | 0.18768 | 0.10529 | 0.19226 | 59.6832 | -61.8027 | 0.009156 | -0.28381 | -0.11902 | -0.17853 | -0.19684 | -0.17853 | -0.1236 | -0.12817 | 61.7294 | 61.8164 | 121.2341 | 121.1472 | -0.11902 | 121.3074 | 61.8118 | -0.17853 | 121.1472 | -0.11902 | 61.8118 | 121.2341 | 121.3074 | -121.4218 | -121.6095
373.3594 | 121.7972 | -61.6287 | 59.816 | 0.0057222 | 0.015127 | 0.0081283 | 0.0059473 | 0.056249 | -0.0054859 | 0.06618 | -61.7432 | 59.5047 | -61.6287 | -61.821 | 59.6191 | 0.14191 | 0.073242 | 0.13733 | 59.7015 | -61.7935 | 0 | -0.31128 | -0.11444 | -0.19226 | -0.19684 | -0.16479 | -0.11444 | -0.11444 | 61.702 | 61.7661 | 121.2479 | 121.1334 | -0.11444 | 121.3303 | 61.7706 | -0.16479 | 121.1334 | -0.11444 | 61.7706 | 121.2479 | 121.3303 | -121.4447 | -121.6095
375.1094 | 121.8338 | -61.615 | 59.7977 | 0.066757 | 0.017049 | 0.011974 | 0.0076563 | 0.056249 | -0.0069811 | 0.064044 | -61.7432 | 59.5093 | -61.6196 | -61.8256 | 59.5963 | 0.1236 | 0.009155 | 0.091553 | 59.6924 | -61.8118 | -0.004578 | -0.28839 | -0.12817 | -0.21057 | -0.20142 | -0.19684 | -0.10529 | -0.1236 | 61.6241 | 61.7065 | 121.2112 | 121.1243 | -0.12817 | 121.3074 | 61.7386 | -0.19684 | 121.1243 | -0.12817 | 61.7386 | 121.2112 | 121.3074 | -121.4172 | -121.6095
376.7969 | 121.701 | -61.7111 | 59.8206 | -0.13924 | 0.016836 | 0.010265 | 0.0068017 | 0.054326 | -0.0080493 | 0.064899 | -61.6745 | 59.5505 | -61.6058 | -61.7111 | 59.6924 | 0.40741 | 0.40283 | 0.46234 | 59.7519 | -61.7386 | 0.10529 | -0.27008 | 0.036621 | 0 | -0.12817 | -0.027465 | -0.068665 | -0.068665 | 62.114 | 62.1735 | 121.4035 | 121.2616 | 0.036621 | 121.463 | 62.1185 | -0.027465 | 121.2616 | 0.036621 | 62.1185 | 121.4035 | 121.463 | -121.4264 | -121.5591
378.5469 | 121.7697 | -61.7523 | 59.7015 | 0.059128 | 0.017476 | 0.013469 | 0.010647 | 0.058385 | -0.0089037 | 0.064685 | -61.8851 | 59.4589 | -61.7477 | -61.9492 | 59.4315 | -0.022888 | -0.17853 | -0.32501 | 59.6558 | -61.9125 | 0.004577 | -0.24262 | -0.13275 | -0.19684 | -0.27008 | -0.16022 | -0.045776 | -0.13733 | 61.5738 | 61.4273 | 121.1838 | 121.2112 | -0.13275 | 121.4081 | 61.7294 | -0.16022 | 121.2112 | -0.13275 | 61.7294 | 121.1838 | 121.4081 | -121.4493 | -121.6141
380.2812 | 121.7606 | -61.6974 | 59.7702 | 0.15831 | 0.014913 | 0.013255 | 0.0068017 | 0.056463 | -0.0078357 | 0.067035 | -61.7477 | 59.436 | -61.6745 | -61.8256 | 59.5917 | 0.022888 | -0.3479 | -0.11444 | 59.6146 | -61.8439 | 0.022888 | -0.33417 | -0.050354 | -0.12817 | -0.17853 | -0.14648 | -0.15564 | -0.073242 | 61.3495 | 61.5829 | 121.2891 | 121.1334 | -0.050354 | 121.312 | 61.7203 | -0.14648 | 121.1334 | -0.050354 | 61.7203 | 121.2891 | 121.312 | -121.4447 | -121.6141
382.0156 | 121.7926 | -61.6333 | 59.8297 | 0.043869 | 0.015981 | 0.012401 | 0.0021021 | 0.055395 | -0.0056995 | 0.064899 | -61.7386 | 59.5276 | -61.615 | -61.8439 | 59.61 | 0.14648 | 0.050354 | 0.1236 | 59.697 | -61.8164 | 0.018311 | -0.30212 | -0.10528 | -0.21057 | -0.21973 | -0.1831 | -0.13275 | -0.1236 | 61.6837 | 61.7569 | 121.2433 | 121.1609 | -0.10528 | 121.3303 | 61.7798 | -0.1831 | 121.1609 | -0.10528 | 61.7798 | 121.2433 | 121.3303 | -121.4447 | -121.6461
383.7031 | 121.6461 | -61.7889 | 59.729 | -0.047684 | 0.015554 | 0.010692 | 0.0093653 | 0.057958 | -0.0093311 | 0.065753 | -61.7752 | 59.4681 | -61.6928 | -61.8439 | 59.5596 | 0.21057 | 0 | 0 | 59.6832 | -61.8301 | 0.09613 | -0.26093 | 0.013732 | -0.054932 | -0.16937 | -0.041199 | -0.045776 | -0.082398 | 61.7889 | 61.7889 | 121.3486 | 121.257 | 0.013732 | 121.4722 | 61.9995 | -0.041199 | 121.257 | 0.013732 | 61.9995 | 121.3486 | 121.4722 | -121.4218 | -121.5591
385.4688 | 121.701 | -61.7065 | 59.8297 | -0.18501 | 0.014058 | 0.013042 | 0.0029565 | 0.055395 | -0.0080493 | 0.065112 | -61.6745 | 59.5505 | -61.5967 | -61.7386 | 59.6832 | 0.41199 | 0.40283 | 0.46234 | 59.729 | -61.7432 | 0.10986 | -0.27924 | 0.032043 | -0.032043 | -0.14648 | -0.036621 | -0.10071 | -0.07782 | 62.1094 | 62.1689 | 121.3898 | 121.257 | 0.032043 | 121.4355 | 62.1185 | -0.036621 | 121.257 | 0.032043 | 62.1185 | 121.3898 | 121.4355 | -121.4264 | -121.5729
387.1562 | 121.7651 | -61.6791 | 59.761 | 0.16594 | 0.018545 | 0.0083419 | 0.0080835 | 0.059881 | -0.0056995 | 0.065967 | -61.7661 | 59.4131 | -61.6699 | -61.8347 | 59.5963 | 0.013733 | -0.35706 | -0.14648 | 59.6191 | -61.8622 | 0.009155 | -0.3479 | -0.086975 | -0.15564 | -0.16479 | -0.18311 | -0.14191 | -0.09613 | 61.322 | 61.5326 | 121.2753 | 121.0922 | -0.086975 | 121.2982 | 61.6928 | -0.18311 | 121.0922 | -0.086975 | 61.6928 | 121.2753 | 121.2982 | -121.431 | -121.6232
388.9062 | 121.6827 | -61.6837 | 59.8206 | -0.16975 | 0.015127 | 0.010265 | 0.0029565 | 0.056249 | -0.0052721 | 0.064258 | -61.6287 | 59.5779 | -61.5417 | -61.6974 | 59.7382 | 0.4303 | 0.31128 | 0.50354 | 59.7473 | -61.7249 | 0.14191 | -0.24262 | 0.054932 | -0.013733 | -0.082398 | -0.041199 | -0.073243 | -0.086975 | 61.9949 | 62.1872 | 121.4218 | 121.2616 | 0.054932 | 121.431 | 62.114 | -0.041199 | 121.2616 | 0.054932 | 62.114 | 121.4218 | 121.431 | -121.3623 | -121.5454
390.6406 | 121.6507 | -61.7935 | 59.6924 | -0.055313 | 0.016408 | 0.011546 | 0.0093653 | 0.059026 | -0.0097583 | 0.064258 | -61.7661 | 59.491 | -61.7249 | -61.8484 | 59.5596 | 0.19684 | 0.004578 | -0.013733 | 59.7015 | -61.821 | 0.068664 | -0.20142 | 0.027466 | -0.054932 | -0.13275 | -0.027466 | 0.009155 | -0.041198 | 61.7981 | 61.7798 | 121.3531 | 121.2845 | 0.027466 | 121.4951 | 61.9904 | -0.027466 | 121.2845 | 0.027466 | 61.9904 | 121.3531 | 121.4951 | -121.4172 | -121.5134
392.3281 | 121.7102 | -61.6562 | 59.8297 | -0.11635 | 0.018117 | 0.013683 | 0.0021021 | 0.057531 | -0.0050585 | 0.064471 | -61.6562 | 59.5184 | -61.5601 | -61.7203 | 59.7198 | 0.37537 | 0.20599 | 0.41657 | 59.7107 | -61.7523 | 0.09613 | -0.31128 | 0 | -0.064087 | -0.10986 | -0.09613 | -0.11902 | -0.09613 | 61.8622 | 62.0728 | 121.376 | 121.1746 | 0 | 121.3669 | 62.0316 | -0.09613 | 121.1746 | 0 | 62.0316 | 121.376 | 121.3669 | -121.3898 | -121.582
394.0781 | 121.669 | -61.8118 | 59.697 | -0.078201 | 0.01769 | 0.011333 | 0.010861 | 0.056035 | -0.01104 | 0.063403 | -61.7569 | 59.5276 | -61.6882 | -61.8668 | 59.5596 | 0.19684 | -0.009155 | -0.018311 | 59.6695 | -61.8668 | 0.1236 | -0.16937 | 0.054932 | -0.054931 | -0.13733 | -0.054931 | -0.027465 | -0.068665 | 61.8027 | 61.7935 | 121.3715 | 121.3394 | 0.054932 | 121.4813 | 62.0087 | -0.054931 | 121.3394 | 0.054932 | 62.0087 | 121.3715 | 121.4813 | -121.3852 | -121.5637
395.8125 | 121.7468 | -61.7111 | 59.7244 | 0.15831 | 0.015554 | 0.010051 | 0.0053065 | 0.058599 | -0.0082629 | 0.067889 | -61.8347 | 59.4223 | -61.7386 | -61.8988 | 59.5276 | -0.018311 | -0.40741 | -0.3067 | 59.6237 | -61.8805 | -0.027465 | -0.30212 | -0.1236 | -0.18768 | -0.19684 | -0.16937 | -0.10071 | -0.096131 | 61.3037 | 61.4044 | 121.2387 | 121.1334 | -0.1236 | 121.3348 | 61.6928 | -0.16937 | 121.1334 | -0.1236 | 61.6928 | 121.2387 | 121.3348 | -121.463 | -121.6049
397.5625 | 121.6965 | -61.702 | 59.8022 | -0.16212 | 0.014272 | 0.013469 | 0.0021021 | 0.057744 | -0.0071947 | 0.064899 | -61.6699 | 59.5459 | -61.5646 | -61.7432 | 59.697 | 0.42572 | 0.3891 | 0.48523 | 59.697 | -61.7844 | 0.13733 | -0.25635 | 0.032043 | -0.041199 | -0.10529 | -0.082398 | -0.10529 | -0.10529 | 62.0911 | 62.1872 | 121.3989 | 121.2479 | 0.032043 | 121.3989 | 62.1277 | -0.082398 | 121.2479 | 0.032043 | 62.1277 | 121.3989 | 121.3989 | -121.3669 | -121.5866
399.2656 | 121.8063 | -61.6287 | 59.7885 | -0.017166 | 0.015981 | 0.0096237 | 0.0027429 | 0.057958 | -0.0039905 | 0.066821 | -61.7615 | 59.5322 | -61.6104 | -61.8393 | 59.6237 | 0.20142 | 0.10986 | 0.20599 | 59.697 | -61.7935 | 0.01831 | -0.25635 | -0.13275 | -0.21057 | -0.1648 | -0.16479 | -0.091553 | -0.15106 | 61.7386 | 61.8347 | 121.2524 | 121.1609 | -0.13275 | 121.3257 | 61.8301 | -0.16479 | 121.1609 | -0.13275 | 61.8301 | 121.2524 | 121.3257 | -121.3989 | -121.582
401.0156 | 121.7422 | -61.7569 | 59.697 | 0.066757 | 0.014486 | 0.012615 | 0.0089381 | 0.057744 | -0.0052721 | 0.06554 | -61.8713 | 59.4452 | -61.7569 | -61.9629 | 59.4589 | 0 | -0.16937 | -0.31128 | 59.6466 | -61.8668 | 0 | -0.25177 | -0.11444 | -0.20599 | -0.23804 | -0.10986 | -0.050354 | -0.11444 | 61.5875 | 61.4456 | 121.2158 | 121.2021 | -0.11444 | 121.4035 | 61.7569 | -0.10986 | 121.2021 | -0.11444 | 61.7569 | 121.2158 | 121.4035 | -121.4539 | -121.5637
402.6875 | 121.6965 | -61.8073 | 59.7244 | -0.0019073 | 0.017904 | 0.013896 | 0.0080835 | 0.056676 | -0.0078357 | 0.06554 | -61.8118 | 59.5139 | -61.7065 | -61.9354 | 59.4727 | 0.059509 | -0.14648 | -0.23804 | 59.6786 | -61.908 | 0.10071 | -0.21057 | -0.004578 | -0.12817 | -0.25177 | -0.10071 | -0.045776 | -0.10529 | 61.6608 | 61.5692 | 121.2799 | 121.3211 | -0.004578 | 121.4859 | 61.8668 | -0.10071 | 121.3211 | -0.004578 | 61.8668 | 121.2799 | 121.4859 | -121.431 | -121.6324
404.4375 | 121.7972 | -61.7523 | 59.6603 | 0.12779 | 0.018117 | 0.01176 | 0.0074427 | 0.05924 | -0.0065539 | 0.06554 | -61.8988 | 59.4681 | -61.7661 | -61.9812 | 59.4315 | -0.082397 | -0.27466 | -0.39368 | 59.6191 | -61.8988 | -0.013733 | -0.19226 | -0.14648 | -0.22888 | -0.22888 | -0.14648 | -0.041198 | -0.13275 | 61.4777 | 61.3586 | 121.1838 | 121.2204 | -0.14648 | 121.3715 | 61.6699 | -0.14648 | 121.2204 | -0.14648 | 61.6699 | 121.1838 | 121.3715 | -121.4264 | -121.5591
406.1875 | 121.8018 | -61.7386 | 59.7153 | 0.1049 | 0.01769 | 0.015605 | 0.0068017 | 0.057744 | -0.0089037 | 0.067676 | -61.8668 | 59.4864 | -61.7477 | -61.9675 | 59.4864 | -0.059509 | -0.31128 | -0.38452 | 59.6237 | -61.9171 | -0.009156 | -0.22888 | -0.12817 | -0.22888 | -0.22888 | -0.17853 | -0.091553 | -0.11902 | 61.4273 | 61.3541 | 121.225 | 121.225 | -0.12817 | 121.3623 | 61.6791 | -0.17853 | 121.225 | -0.12817 | 61.6791 | 121.225 | 121.3623 | -121.463 | -121.6324
407.8906 | 121.6599 | -61.8118 | 59.7427 | -0.11635 | 0.013845 | 0.0091965 | 0.0038111 | 0.057744 | -0.0069811 | 0.066821 | -61.7889 | 59.5184 | -61.6882 | -61.8576 | 59.5642 | 0.24719 | 0.09613 | 0.064087 | 59.6741 | -61.853 | 0.1236 | -0.2243 | 0.022889 | -0.045776 | -0.17853 | -0.041198 | -0.068665 | -0.10071 | 61.908 | 61.8759 | 121.376 | 121.3303 | 0.022889 | 121.4859 | 62.059 | -0.041198 | 121.3303 | 0.022889 | 62.059 | 121.376 | 121.4859 | -121.431 | -121.5958
409.625 | 121.6553 | -61.8027 | 59.7107 | -0.062942 | 0.01534 | 0.01646 | 0.0068017 | 0.05689 | -0.0093311 | 0.064685 | -61.7752 | 59.5276 | -61.6745 | -61.8622 | 59.5596 | 0.21515 | 0.027466 | 0.018311 | 59.6786 | -61.8622 | 0.12817 | -0.1831 | 0.027465 | -0.05951 | -0.15106 | -0.05951 | -0.032043 | -0.10071 | 61.8301 | 61.821 | 121.3623 | 121.3303 | 0.027465 | 121.4813 | 62.0178 | -0.05951 | 121.3303 | 0.027465 | 62.0178 | 121.3623 | 121.4813 | -121.3852 | -121.5729
411.3125 | 121.8201 | -61.6379 | 59.8251 | 0.020981 | 0.014272 | 0.013896 | -3.414e-05 | 0.057958 | -0.0059131 | 0.065753 | -61.7661 | 59.5367 | -61.6379 | -61.8439 | 59.6008 | 0.12817 | 0.022888 | 0.10071 | 59.697 | -61.8073 | 0 | -0.28839 | -0.12817 | -0.20599 | -0.2243 | -0.16937 | -0.12817 | -0.12817 | 61.6608 | 61.7386 | 121.2387 | 121.1746 | -0.12817 | 121.3348 | 61.7661 | -0.16937 | 121.1746 | -0.12817 | 61.7661 | 121.2387 | 121.3348 | -121.463 | -121.6324
413.0625 | 121.7972 | -61.7294 | 59.7107 | 0.097275 | 0.01769 | 0.0089829 | 0.0048791 | 0.057531 | -0.0039905 | 0.065753 | -61.8759 | 59.4543 | -61.734 | -61.9583 | 59.4589 | -0.068665 | -0.32959 | -0.36621 | 59.6329 | -61.8988 | -0.004578 | -0.25635 | -0.14648 | -0.22888 | -0.25177 | -0.16937 | -0.077819 | -0.14191 | 61.3998 | 61.3632 | 121.1884 | 121.1838 | -0.14648 | 121.3623 | 61.6608 | -0.16937 | 121.1838 | -0.14648 | 61.6608 | 121.1884 | 121.3623 | -121.4447 | -121.6095
414.8125 | 121.6827 | -61.8347 | 59.7198 | -0.047684 | 0.016408 | 0.0094101 | 0.0082971 | 0.058599 | -0.0076221 | 0.065967 | -61.7844 | 59.4864 | -61.6974 | -61.8713 | 59.5413 | 0.19226 | -0.041199 | -0.064087 | 59.6695 | -61.8439 | 0.13733 | -0.23346 | 0.050354 | -0.036621 | -0.17853 | -0.009155 | -0.050354 | -0.086975 | 61.7935 | 61.7706 | 121.376 | 121.3211 | 0.050354 | 121.5042 | 62.027 | -0.009155 | 121.3211 | 0.050354 | 62.027 | 121.376 | 121.5042 | -121.4172 | -121.5637
416.5469 | 121.7468 | -61.6653 | 59.7702 | 0.18883 | 0.016408 | 0.012615 | 0.0038111 | 0.057531 | -0.0044177 | 0.064258 | -61.7752 | 59.3994 | -61.6837 | -61.8576 | 59.5642 | 0.018311 | -0.3891 | -0.16479 | 59.61 | -61.8622 | -0.018311 | -0.37079 | -0.10986 | -0.19226 | -0.20599 | -0.19684 | -0.16022 | -0.091553 | 61.2762 | 61.5005 | 121.2296 | 121.0648 | -0.10986 | 121.2753 | 61.6837 | -0.19684 | 121.0648 | -0.10986 | 61.6837 | 121.2296 | 121.2753 | -121.4539 | -121.6324
418.2344 | 121.8201 | -61.615 | 59.8206 | -0.0019073 | 0.014913 | 0.010265 | -0.00046134 | 0.056035 | -0.0052721 | 0.065967 | -61.7386 | 59.5276 | -61.5875 | -61.8347 | 59.6008 | 0.19684 | 0.10986 | 0.19684 | 59.6741 | -61.8073 | 0.027466 | -0.29297 | -0.1236 | -0.21973 | -0.21973 | -0.19226 | -0.14648 | -0.15106 | 61.7249 | 61.8118 | 121.2158 | 121.1426 | -0.1236 | 121.2891 | 61.8118 | -0.19226 | 121.1426 | -0.1236 | 61.8118 | 121.2158 | 121.2891 | -121.4081 | -121.6278
419.9844 | 121.7102 | -61.7249 | 59.7473 | -0.18501 | 0.016622 | 0.0081283 | 0.0068017 | 0.056463 | -0.0080493 | 0.065753 | -61.7752 | 59.5688 | -61.6425 | -61.8347 | 59.5871 | 0.33417 | 0.45776 | 0.32044 | 59.7702 | -61.7798 | 0.082398 | -0.17853 | -0.050354 | -0.10986 | -0.16022 | -0.054931 | 0.022889 | -0.13275 | 62.1826 | 62.0453 | 121.312 | 121.2936 | -0.050354 | 121.4951 | 62.059 | -0.054931 | 121.2936 | -0.050354 | 62.059 | 121.312 | 121.4951 | -121.3898 | -121.5271
421.7344 | 121.6553 | -61.8256 | 59.7336 | -0.09346 | 0.015981 | 0.0096237 | 0.0095789 | 0.056035 | -0.0099719 | 0.06319 | -61.7706 | 59.5047 | -61.6837 | -61.8622 | 59.5459 | 0.23346 | 0.036621 | 0.041199 | 59.6786 | -61.8301 | 0.14191 | -0.22888 | 0.054932 | -0.036621 | -0.18768 | -0.004577 | -0.054932 | -0.086975 | 61.8622 | 61.8668 | 121.3715 | 121.3303 | 0.054932 | 121.5042 | 62.059 | -0.004577 | 121.3303 | 0.054932 | 62.059 | 121.3715 | 121.5042 | -121.4172 | -121.5637
423.4375 | 121.6736 | -61.7706 | 59.729 | -0.09346 | 0.016622 | 0.011119 | 0.010006 | 0.056676 | -0.0061267 | 0.065326 | -61.7798 | 59.4864 | -61.6653 | -61.8576 | 59.5459 | 0.24261 | 0.09613 | 0.059509 | 59.6649 | -61.821 | 0.10529 | -0.24262 | -0.009155 | -0.086975 | -0.18311 | -0.050354 | -0.064087 | -0.11444 | 61.8668 | 61.8301 | 121.3165 | 121.257 | -0.009155 | 121.4355 | 62.0132 | -0.050354 | 121.257 | -0.009155 | 62.0132 | 121.3165 | 121.4355 | -121.3943 | -121.55
425.1875 | 121.8063 | -61.615 | 59.8068 | 0.013352 | 0.016408 | 0.013469 | -0.00067514 | 0.057531 | -0.0039905 | 0.066394 | -61.7477 | 59.5551 | -61.5738 | -61.8347 | 59.61 | 0.16479 | 0.10071 | 0.16022 | 59.7015 | -61.8164 | 0.041198 | -0.25177 | -0.13275 | -0.21973 | -0.19684 | -0.20142 | -0.10529 | -0.17395 | 61.7157 | 61.7752 | 121.225 | 121.17 | -0.13275 | 121.3165 | 61.7798 | -0.20142 | 121.17 | -0.13275 | 61.7798 | 121.225 | 121.3165 | -121.3806 | -121.6232
426.9219 | 121.7285 | -61.7477 | 59.729 | -0.21553 | 0.017476 | 0.010265 | 0.0057337 | 0.058385 | -0.0069811 | 0.065326 | -61.7661 | 59.5779 | -61.6196 | -61.8439 | 59.5779 | 0.32501 | 0.44403 | 0.27008 | 59.7839 | -61.7844 | 0.12817 | -0.15106 | -0.01831 | -0.09613 | -0.15106 | -0.036621 | 0.054932 | -0.14648 | 62.1918 | 62.0178 | 121.3257 | 121.3257 | -0.01831 | 121.5317 | 62.0728 | -0.036621 | 121.3257 | -0.01831 | 62.0728 | 121.3257 | 121.5317 | -121.3486 | -121.5134
428.6719 | 121.756 | -61.6425 | 59.8251 | -0.085831 | 0.017476 | 0.012615 | 0.0018885 | 0.058172 | -0.0054859 | 0.067035 | -61.6837 | 59.5459 | -61.6013 | -61.7294 | 59.6878 | 0.31128 | 0.21057 | 0.37537 | 59.7382 | -61.7432 | 0.041199 | -0.27924 | -0.041199 | -0.086975 | -0.13733 | -0.10071 | -0.086975 | -0.082398 | 61.853 | 62.0178 | 121.3303 | 121.1884 | -0.041199 | 121.3806 | 61.9537 | -0.10071 | 121.1884 | -0.041199 | 61.9537 | 121.3303 | 121.3806 | -121.4264 | -121.5683
430.4219 | 121.6782 | -61.7706 | 59.7153 | -0.14687 | 0.015554 | 0.013255 | 0.0097925 | 0.059453 | -0.0086901 | 0.064471 | -61.7706 | 59.5413 | -61.6837 | -61.8393 | 59.5505 | 0.26093 | 0.17395 | 0.14191 | 59.729 | -61.8164 | 0.086975 | -0.17395 | 0 | -0.068664 | -0.16479 | -0.045776 | 0.013733 | -0.086975 | 61.9446 | 61.9125 | 121.3211 | 121.312 | 0 | 121.4996 | 62.0316 | -0.045776 | 121.312 | 0 | 62.0316 | 121.3211 | 121.4996 | -121.3989 | -121.5317
432.1094 | 121.8246 | -61.6013 | 59.7885 | -0.0019073 | 0.015981 | 0.013255 | 0.0027429 | 0.056676 | -0.0076221 | 0.065967 | -61.7477 | 59.5093 | -61.615 | -61.8393 | 59.5963 | 0.15106 | 0.027466 | 0.1236 | 59.7153 | -61.7981 | -0.013733 | -0.27924 | -0.14649 | -0.23804 | -0.19226 | -0.19684 | -0.073242 | -0.13275 | 61.6287 | 61.7249 | 121.1975 | 121.1105 | -0.14649 | 121.3165 | 61.7523 | -0.19684 | 121.1105 | -0.14649 | 61.7523 | 121.1975 | 121.3165 | -121.4035 | -121.5866
433.8594 | 121.6873 | -61.7935 | 59.729 | -0.13161 | 0.016836 | 0.0089829 | 0.011501 | 0.058599 | -0.0078357 | 0.065753 | -61.7844 | 59.5184 | -61.6837 | -61.8439 | 59.5505 | 0.27466 | 0.15106 | 0.11902 | 59.697 | -61.8576 | 0.10986 | -0.21057 | 0.009155 | -0.050354 | -0.17853 | -0.064087 | -0.032044 | -0.10071 | 61.9446 | 61.9125 | 121.344 | 121.312 | 0.009155 | 121.4905 | 62.0682 | -0.064087 | 121.312 | 0.009155 | 62.0682 | 121.344 | 121.4905 | -121.4127 | -121.5866
435.6094 | 121.7102 | -61.6837 | 59.8251 | -0.09346 | 0.018331 | 0.0089829 | 0.0040247 | 0.053686 | -0.0048449 | 0.066608 | -61.6608 | 59.5505 | -61.5601 | -61.7157 | 59.7107 | 0.37079 | 0.22888 | 0.43945 | 59.7015 | -61.7661 | 0.1236 | -0.27466 | 0.022888 | -0.032043 | -0.11444 | -0.082397 | -0.1236 | -0.10071 | 61.9125 | 62.1231 | 121.3943 | 121.2341 | 0.022888 | 121.3852 | 62.0544 | -0.082397 | 121.2341 | 0.022888 | 62.0544 | 121.3943 | 121.3852 | -121.3852 | -121.5912
437.2969 | 121.788 | -61.6745 | 59.8068 | 0.0057222 | 0.016836 | 0.017101 | 0.0025293 | 0.057744 | -0.0046313 | 0.064471 | -61.734 | 59.523 | -61.6241 | -61.8073 | 59.6191 | 0.21057 | 0.12817 | 0.22888 | 59.7244 | -61.7935 | 0.050354 | -0.28381 | -0.059509 | -0.13275 | -0.18768 | -0.11902 | -0.082398 | -0.10986 | 61.8027 | 61.9034 | 121.2936 | 121.1975 | -0.059509 | 121.3989 | 61.8851 | -0.11902 | 121.1975 | -0.059509 | 61.8851 | 121.2936 | 121.3989 | -121.431 | -121.6003
439.0469 | 121.6873 | -61.8164 | 59.7015 | -0.024795 | 0.014699 | 0.0077011 | 0.010433 | 0.057958 | -0.0086901 | 0.065326 | -61.7889 | 59.4727 | -61.734 | -61.8576 | 59.5459 | 0.15564 | -0.059509 | -0.07782 | 59.6878 | -61.821 | 0.082397 | -0.22888 | 0.027466 | -0.041199 | -0.15564 | -0.004578 | -0.013733 | -0.054931 | 61.7569 | 61.7386 | 121.3623 | 121.2891 | 0.027466 | 121.5042 | 61.972 | -0.004578 | 121.2891 | 0.027466 | 61.972 | 121.3623 | 121.5042 | -121.4355 | -121.5225
440.7812 | 121.7606 | -61.6974 | 59.7473 | 0.1049 | 0.016408 | 0.0087693 | 0.0065881 | 0.059453 | -0.0069811 | 0.06554 | -61.7798 | 59.4177 | -61.7249 | -61.8576 | 59.5551 | 0.004578 | -0.40283 | -0.24261 | 59.6146 | -61.8622 | -0.027466 | -0.32959 | -0.082397 | -0.16022 | -0.19226 | -0.1648 | -0.13275 | -0.054931 | 61.2946 | 61.4548 | 121.2524 | 121.1151 | -0.082397 | 121.312 | 61.702 | -0.1648 | 121.1151 | -0.082397 | 61.702 | 121.2524 | 121.312 | -121.4722 | -121.6095
442.4688 | 121.7651 | -61.6653 | 59.7656 | 0.15068 | 0.016195 | 0.012615 | 0.0074427 | 0.05689 | -0.0061267 | 0.065753 | -61.7615 | 59.4315 | -61.6837 | -61.8301 | 59.5688 | 0.054932 | -0.33875 | -0.10986 | 59.6054 | -61.8576 | -0.018311 | -0.33417 | -0.096131 | -0.1648 | -0.19684 | -0.19226 | -0.16022 | -0.07782 | 61.3266 | 61.5555 | 121.2341 | 121.0968 | -0.096131 | 121.2708 | 61.7203 | -0.19226 | 121.0968 | -0.096131 | 61.7203 | 121.2341 | 121.2708 | -121.4493 | -121.6232
444.2188 | 121.8018 | -61.6745 | 59.7931 | 0.043869 | 0.015981 | 0.0062057 | 0.0048791 | 0.05689 | -0.0063403 | 0.063617 | -61.7615 | 59.5047 | -61.6287 | -61.8301 | 59.6008 | 0.11902 | -0.032043 | 0.054932 | 59.7015 | -61.8073 | 0.045777 | -0.28839 | -0.086975 | -0.15564 | -0.19226 | -0.13275 | -0.091553 | -0.13275 | 61.6425 | 61.7294 | 121.2753 | 121.1792 | -0.086975 | 121.376 | 61.7935 | -0.13275 | 121.1792 | -0.086975 | 61.7935 | 121.2753 | 121.376 | -121.4218 | -121.6003
445.9062 | 121.7239 | -61.7157 | 59.7794 | -0.19264 | 0.015981 | 0.016033 | 0.0057337 | 0.056676 | -0.0061267 | 0.064899 | -61.7111 | 59.5779 | -61.5875 | -61.7981 | 59.6054 | 0.34332 | 0.45319 | 0.37537 | 59.7519 | -61.8027 | 0.12817 | -0.20142 | 0.004577 | -0.082398 | -0.17395 | -0.086975 | -0.027466 | -0.1236 | 62.1689 | 62.0911 | 121.3211 | 121.2936 | 0.004577 | 121.4676 | 62.059 | -0.086975 | 121.2936 | 0.004577 | 62.059 | 121.3211 | 121.4676 | -121.3669 | -121.582
447.6406 | 121.701 | -61.6837 | 59.8297 | -0.13161 | 0.016622 | 0.011119 | 0.0040247 | 0.054326 | -0.0044177 | 0.063617 | -61.6562 | 59.5551 | -61.5738 | -61.7157 | 59.7107 | 0.38452 | 0.24261 | 0.45319 | 59.6924 | -61.7569 | 0.10986 | -0.27466 | 0.027466 | -0.032043 | -0.11902 | -0.073242 | -0.13733 | -0.082397 | 61.9263 | 62.1368 | 121.3943 | 121.2387 | 0.027466 | 121.376 | 62.0682 | -0.073242 | 121.2387 | 0.027466 | 62.0682 | 121.3943 | 121.376 | -121.4035 | -121.5866
449.3281 | 121.8246 | -61.6379 | 59.7931 | 0.03624 | 0.015554 | 0.0070603 | 0.0025293 | 0.055608 | -0.0037769 | 0.065112 | -61.7432 | 59.5322 | -61.6333 | -61.8073 | 59.5963 | 0.14191 | 0.022888 | 0.10986 | 59.6695 | -61.8118 | 0.004577 | -0.26093 | -0.10529 | -0.16937 | -0.19684 | -0.17395 | -0.1236 | -0.10986 | 61.6608 | 61.7477 | 121.2341 | 121.17 | -0.10529 | 121.3074 | 61.7798 | -0.17395 | 121.17 | -0.10529 | 61.7798 | 121.2341 | 121.3074 | -121.4264 | -121.6049
451.0781 | 121.7194 | -61.7477 | 59.7519 | -0.18501 | 0.017263 | 0.0089829 | 0.010647 | 0.054113 | -0.0082629 | 0.067035 | -61.7798 | 59.5779 | -61.6608 | -61.8439 | 59.5551 | 0.29297 | 0.37537 | 0.2243 | 59.7656 | -61.7889 | 0.086975 | -0.17395 | -0.032043 | -0.09613 | -0.19684 | -0.041198 | 0.013733 | -0.11902 | 62.1231 | 61.972 | 121.3028 | 121.3257 | -0.032043 | 121.5134 | 62.0407 | -0.041198 | 121.3257 | -0.032043 | 62.0407 | 121.3028 | 121.5134 | -121.4127 | -121.5408
452.8125 | 121.7697 | -61.7203 | 59.7015 | 0.17357 | 0.016195 | 0.013042 | 0.0082971 | 0.05924 | -0.0086901 | 0.064685 | -61.853 | 59.4498 | -61.7294 | -61.9125 | 59.4818 | -0.045776 | -0.38452 | -0.33417 | 59.6146 | -61.8622 | -0.009155 | -0.25177 | -0.13275 | -0.19226 | -0.21973 | -0.14191 | -0.086975 | -0.1236 | 61.3358 | 61.3861 | 121.2021 | 121.17 | -0.13275 | 121.3348 | 61.6745 | -0.14191 | 121.17 | -0.13275 | 61.6745 | 121.2021 | 121.3348 | -121.431 | -121.5637
454.5625 | 121.7194 | -61.7523 | 59.7336 | -0.17738 | 0.016195 | 0.011119 | 0.0061609 | 0.056676 | -0.0091173 | 0.065326 | -61.7615 | 59.5871 | -61.6196 | -61.8347 | 59.5825 | 0.33417 | 0.4715 | 0.32044 | 59.7519 | -61.7935 | 0.13275 | -0.14648 | -0.009156 | -0.082398 | -0.15106 | -0.041199 | 0.01831 | -0.14191 | 62.2238 | 62.0728 | 121.3348 | 121.3394 | -0.009156 | 121.5042 | 62.0865 | -0.041199 | 121.3394 | -0.009156 | 62.0865 | 121.3348 | 121.5042 | -121.3531 | -121.5271
456.2344 | 121.7514 | -61.6699 | 59.7748 | 0.16594 | 0.014486 | 0.010906 | 0.0057337 | 0.05924 | -0.0091173 | 0.067035 | -61.7477 | 59.404 | -61.6928 | -61.8301 | 59.5917 | 0.041199 | -0.36621 | -0.14191 | 59.61 | -61.8393 | -0.022888 | -0.37079 | -0.07782 | -0.16022 | -0.1831 | -0.16937 | -0.16479 | -0.054932 | 61.3037 | 61.528 | 121.2616 | 121.0739 | -0.07782 | 121.2799 | 61.7111 | -0.16937 | 121.0739 | -0.07782 | 61.7111 | 121.2616 | 121.2799 | -121.4676 | -121.6141
457.9844 | 121.7148 | -61.7203 | 59.7794 | -0.21553 | 0.01534 | 0.0072739 | 0.0055201 | 0.052617 | -0.0056995 | 0.064044 | -61.6928 | 59.5322 | -61.5784 | -61.7798 | 59.6375 | 0.39368 | 0.44403 | 0.41657 | 59.7244 | -61.7798 | 0.14191 | -0.24719 | 0.027466 | -0.059509 | -0.14191 | -0.059509 | -0.054932 | -0.11444 | 62.1643 | 62.1368 | 121.3577 | 121.2524 | 0.027466 | 121.4447 | 62.114 | -0.059509 | 121.2524 | 0.027466 | 62.114 | 121.3577 | 121.4447 | -121.3577 | -121.5591
459.75 | 121.7606 | -61.6333 | 59.8297 | -0.085831 | 0.015554 | 0.0085555 | 0.0038111 | 0.055181 | -0.0069811 | 0.06554 | -61.6745 | 59.5322 | -61.5829 | -61.7386 | 59.697 | 0.32959 | 0.20599 | 0.37537 | 59.7061 | -61.7569 | 0.050354 | -0.29755 | -0.041199 | -0.10528 | -0.13275 | -0.1236 | -0.1236 | -0.091553 | 61.8393 | 62.0087 | 121.3303 | 121.1655 | -0.041199 | 121.3394 | 61.9629 | -0.1236 | 121.1655 | -0.041199 | 61.9629 | 121.3303 | 121.3394 | -121.4127 | -121.5866
461.4375 | 121.7514 | -61.7157 | 59.7748 | 0.13542 | 0.016622 | 0.0091965 | 0.0074427 | 0.057104 | -0.0063403 | 0.065967 | -61.7523 | 59.3948 | -61.6745 | -61.8256 | 59.6008 | 0.050354 | -0.32959 | -0.11902 | 59.6329 | -61.8439 | 0.041198 | -0.37994 | -0.036621 | -0.10986 | -0.17395 | -0.12817 | -0.14191 | -0.077819 | 61.3861 | 61.5967 | 121.3165 | 121.1105 | -0.036621 | 121.3486 | 61.7661 | -0.12817 | 121.1105 | -0.036621 | 61.7661 | 121.3165 | 121.3486 | -121.4493 | -121.6187
463.1875 | 121.6644 | -61.7065 | 59.816 | -0.16212 | 0.01534 | 0.0091965 | 0.0065881 | 0.056676 | -0.0061267 | 0.063617 | -61.6516 | 59.5413 | -61.5784 | -61.7386 | 59.6786 | 0.42114 | 0.35248 | 0.48523 | 59.729 | -61.7569 | 0.12817 | -0.27466 | 0.054932 | -0.032043 | -0.13733 | -0.050354 | -0.086975 | -0.073242 | 62.059 | 62.1918 | 121.3852 | 121.2479 | 0.054932 | 121.4355 | 62.1277 | -0.050354 | 121.2479 | 0.054932 | 62.1277 | 121.3852 | 121.4355 | -121.3943 | -121.5729
464.9531 | 121.7194 | -61.734 | 59.7656 | -0.2079 | 0.017263 | 0.01176 | 0.0078699 | 0.055395 | -0.0080493 | 0.06554 | -61.7249 | 59.5642 | -61.6196 | -61.8027 | 59.5917 | 0.3479 | 0.45776 | 0.35248 | 59.7656 | -61.7844 | 0.11444 | -0.20142 | 0.009155 | -0.068664 | -0.17395 | -0.050354 | 0 | -0.10529 | 62.1918 | 62.0865 | 121.3257 | 121.2982 | 0.009155 | 121.4996 | 62.0819 | -0.050354 | 121.2982 | 0.009155 | 62.0819 | 121.3257 | 121.4996 | -121.3852 | -121.55
466.6406 | 121.8155 | -61.6425 | 59.8022 | 0.043869 | 0.015127 | 0.011119 | 0.0059473 | 0.055608 | -0.0059131 | 0.066608 | -61.7432 | 59.4681 | -61.6379 | -61.8301 | 59.5734 | 0.10529 | -0.068665 | 0.036621 | 59.7015 | -61.8118 | 0.004578 | -0.33417 | -0.10071 | -0.18768 | -0.22888 | -0.16937 | -0.10071 | -0.10529 | 61.5738 | 61.6791 | 121.2158 | 121.1105 | -0.10071 | 121.344 | 61.7477 | -0.16937 | 121.1105 | -0.10071 | 61.7477 | 121.2158 | 121.344 | -121.4401 | -121.6141
468.375 | 121.7789 | -61.6196 | 59.816 | 0.0057222 | 0.015767 | 0.0098373 | 0.0057337 | 0.054754 | -0.0046313 | 0.065967 | -61.7432 | 59.5276 | -61.6287 | -61.7844 | 59.6283 | 0.21057 | 0.10071 | 0.21973 | 59.6878 | -61.7935 | -0.009155 | -0.28839 | -0.1236 | -0.16479 | -0.18768 | -0.17395 | -0.12817 | -0.11444 | 61.7203 | 61.8393 | 121.2479 | 121.1472 | -0.1236 | 121.3074 | 61.8301 | -0.17395 | 121.1472 | -0.1236 | 61.8301 | 121.2479 | 121.3074 | -121.4447 | -121.6095
470.125 | 121.701 | -61.8027 | 59.7061 | 0.020981 | 0.016622 | 0.010906 | 0.012997 | 0.057744 | -0.0093311 | 0.066608 | -61.8118 | 59.4681 | -61.7477 | -61.8942 | 59.4772 | 0.064087 | -0.15106 | -0.20599 | 59.6283 | -61.8759 | 0.054931 | -0.23804 | -0.009156 | -0.091553 | -0.22888 | -0.073243 | -0.07782 | -0.064087 | 61.6516 | 61.5967 | 121.2799 | 121.2708 | -0.009156 | 121.431 | 61.8668 | -0.073243 | 121.2708 | -0.009156 | 61.8668 | 121.2799 | 121.431 | -121.4539 | -121.582
471.875 | 121.6919 | -61.7661 | 59.7107 | -0.040054 | 0.016408 | 0.01176 | 0.0095789 | 0.059453 | -0.0080493 | 0.065753 | -61.7935 | 59.4772 | -61.7157 | -61.8713 | 59.523 | 0.12817 | -0.091553 | -0.14191 | 59.6786 | -61.8713 | 0.050354 | -0.23346 | -0.027466 | -0.10529 | -0.18768 | -0.10529 | -0.032043 | -0.07782 | 61.6745 | 61.6241 | 121.2891 | 121.2433 | -0.027466 | 121.4447 | 61.8942 | -0.10529 | 121.2433 | -0.027466 | 61.8942 | 121.2891 | 121.4447 | -121.4264 | -121.582
473.625 | 121.6919 | -61.7569 | 59.697 | -0.18501 | 0.017476 | 0.012828 | 0.0082971 | 0.057744 | -0.0056995 | 0.064044 | -61.7615 | 59.5779 | -61.6425 | -61.8301 | 59.5642 | 0.27924 | 0.2655 | 0.14191 | 59.7153 | -61.8622 | 0.11444 | -0.11902 | -0.004578 | -0.073242 | -0.13275 | -0.10529 | 0.018311 | -0.11902 | 62.0224 | 61.8988 | 121.3211 | 121.3348 | -0.004578 | 121.4722 | 62.0361 | -0.10529 | 121.3348 | -0.004578 | 62.0361 | 121.3211 | 121.4722 | -121.3394 | -121.5591
475.3125 | 121.7422 | -61.7615 | 59.6832 | 0.1049 | 0.017263 | 0.010906 | 0.0082971 | 0.05924 | -0.0071947 | 0.065967 | -61.8668 | 59.4543 | -61.7523 | -61.9583 | 59.4498 | 0.009155 | -0.17395 | -0.30212 | 59.6512 | -61.8851 | 0.009156 | -0.22888 | -0.10529 | -0.19684 | -0.23346 | -0.1236 | -0.032044 | -0.11444 | 61.5875 | 61.4594 | 121.2112 | 121.2158 | -0.10529 | 121.4127 | 61.7706 | -0.1236 | 121.2158 | -0.10529 | 61.7706 | 121.2112 | 121.4127 | -121.4355 | -121.5683
477.0469 | 121.6553 | -61.821 | 59.6924 | -0.055313 | 0.01534 | 0.0094101 | 0.0070155 | 0.058172 | -0.0078357 | 0.063403 | -61.7889 | 59.491 | -61.6974 | -61.853 | 59.5505 | 0.21057 | -0.018311 | -0.027466 | 59.697 | -61.8256 | 0.1236 | -0.20142 | 0.032044 | -0.032043 | -0.14191 | -0.004578 | 0.004577 | -0.091552 | 61.8027 | 61.7935 | 121.3715 | 121.312 | 0.032044 | 121.5179 | 62.0316 | -0.004578 | 121.312 | 0.032044 | 62.0316 | 121.3715 | 121.5179 | -121.3898 | -121.5179
478.7969 | 121.7697 | -61.6608 | 59.7794 | 0.1049 | 0.015127 | 0.011974 | 0.00039306 | 0.057958 | -0.0069811 | 0.065753 | -61.7523 | 59.4727 | -61.647 | -61.8393 | 59.5779 | 0.07782 | -0.24261 | -0.054932 | 59.6512 | -61.821 | 0.013733 | -0.3067 | -0.091552 | -0.17853 | -0.20142 | -0.16022 | -0.12817 | -0.10529 | 61.4182 | 61.6058 | 121.2387 | 121.1334 | -0.091552 | 121.312 | 61.7386 | -0.16022 | 121.1334 | -0.091552 | 61.7386 | 121.2387 | 121.312 | -121.4264 | -121.6003
480.5469 | 121.6782 | -61.7661 | 59.7107 | -0.085831 | 0.016408 | 0.0085555 | 0.0070155 | 0.057744 | -0.0076221 | 0.06554 | -61.7615 | 59.5322 | -61.702 | -61.853 | 59.5779 | 0.24719 | 0.086975 | 0.050354 | 59.6878 | -61.821 | 0.064087 | -0.17853 | 0.004577 | -0.086975 | -0.13275 | -0.054932 | -0.022888 | -0.05951 | 61.853 | 61.8164 | 121.344 | 121.2982 | 0.004577 | 121.4539 | 62.0132 | -0.054932 | 121.2982 | 0.004577 | 62.0132 | 121.344 | 121.4539 | -121.4127 | -121.5317
482.2188 | 121.8018 | -61.5784 | 59.7977 | 0.03624 | 0.014486 | 0.0077011 | 0.0010339 | 0.057317 | -0.0074085 | 0.064685 | -61.7386 | 59.523 | -61.5875 | -61.821 | 59.5963 | 0.17853 | 0.09613 | 0.14191 | 59.7153 | -61.7798 | -0.009155 | -0.27466 | -0.16022 | -0.24262 | -0.20142 | -0.20142 | -0.082397 | -0.15106 | 61.6745 | 61.7203 | 121.1746 | 121.1014 | -0.16022 | 121.2936 | 61.7569 | -0.20142 | 121.1014 | -0.16022 | 61.7569 | 121.1746 | 121.2936 | -121.3852 | -121.5775
483.9688 | 121.7514 | -61.7065 | 59.7107 | 0.1812 | 0.014486 | 0.0091965 | 0.0089381 | 0.056249 | -0.0063403 | 0.067035 | -61.8622 | 59.4635 | -61.7432 | -61.9171 | 59.4864 | -0.032043 | -0.37994 | -0.31586 | 59.5963 | -61.8622 | -0.036621 | -0.24719 | -0.15564 | -0.21057 | -0.2243 | -0.15564 | -0.11444 | -0.11902 | 61.3266 | 61.3907 | 121.1929 | 121.17 | -0.15564 | 121.3028 | 61.6745 | -0.15564 | 121.17 | -0.15564 | 61.6745 | 121.1929 | 121.3028 | -121.4539 | -121.5729
485.7188 | 121.701 | -61.734 | 59.7198 | -0.13924 | 0.01534 | 0.0072739 | 0.0080835 | 0.058812 | -0.0071947 | 0.06618 | -61.7798 | 59.5413 | -61.6562 | -61.853 | 59.5642 | 0.30212 | 0.32959 | 0.1831 | 59.7473 | -61.8073 | 0.07782 | -0.17853 | -0.045776 | -0.11902 | -0.15564 | -0.073242 | 0.027465 | -0.1236 | 62.0636 | 61.9171 | 121.2982 | 121.2753 | -0.045776 | 121.4813 | 62.0361 | -0.073242 | 121.2753 | -0.045776 | 62.0361 | 121.2982 | 121.4813 | -121.376 | -121.5271
487.4062 | 121.8063 | -61.5967 | 59.8206 | 0.051498 | 0.014699 | 0.0079147 | 0.0016749 | 0.056035 | -0.0074085 | 0.065112 | -61.7432 | 59.5322 | -61.5921 | -61.8256 | 59.6008 | 0.16937 | 0.064087 | 0.11902 | 59.697 | -61.7615 | 0.004578 | -0.28839 | -0.14648 | -0.22888 | -0.21973 | -0.16479 | -0.1236 | -0.15106 | 61.6608 | 61.7157 | 121.1975 | 121.1288 | -0.14648 | 121.2936 | 61.7661 | -0.16479 | 121.1288 | -0.14648 | 61.7661 | 121.1975 | 121.2936 | -121.4127 | -121.582
489.1562 | 121.7148 | -61.734 | 59.7382 | -0.23842 | 0.014913 | 0.0072739 | 0.0072291 | 0.057744 | -0.0063403 | 0.06554 | -61.7661 | 59.5917 | -61.6287 | -61.8347 | 59.5871 | 0.34332 | 0.43488 | 0.28381 | 59.761 | -61.7706 | 0.10529 | -0.14648 | -0.032043 | -0.10071 | -0.15106 | -0.036621 | 0.022888 | -0.13733 | 62.1689 | 62.0178 | 121.3211 | 121.3257 | -0.032043 | 121.4951 | 62.0773 | -0.036621 | 121.3257 | -0.032043 | 62.0773 | 121.3211 | 121.4951 | -121.3669 | -121.5088
490.9062 | 121.7194 | -61.7294 | 59.7656 | -0.17738 | 0.014486 | 0.010051 | 0.0055201 | 0.05689 | -0.0056995 | 0.06554 | -61.7615 | 59.61 | -61.6241 | -61.821 | 59.5917 | 0.34332 | 0.46692 | 0.32501 | 59.7885 | -61.7889 | 0.10528 | -0.15564 | -0.032044 | -0.091553 | -0.17395 | -0.059509 | 0.022888 | -0.13733 | 62.1963 | 62.0544 | 121.3211 | 121.3394 | -0.032044 | 121.5179 | 62.0728 | -0.059509 | 121.3394 | -0.032044 | 62.0728 | 121.3211 | 121.5179 | -121.3898 | -121.5546
492.5938 | 121.7422 | -61.6882 | 59.7519 | 0.19646 | 0.015981 | 0.01176 | 0.0074427 | 0.058812 | -0.0078357 | 0.065112 | -61.7615 | 59.4177 | -61.6699 | -61.8484 | 59.5734 | 0.027466 | -0.40741 | -0.2243 | 59.6054 | -61.8439 | 0.01831 | -0.33417 | -0.073243 | -0.16022 | -0.17853 | -0.15564 | -0.14648 | -0.091553 | 61.2808 | 61.4639 | 121.2616 | 121.106 | -0.073243 | 121.2936 | 61.7157 | -0.15564 | 121.106 | -0.073243 | 61.7157 | 121.2616 | 121.2936 | -121.4218 | -121.5958
494.3438 | 121.6736 | -61.8073 | 59.6924 | -0.055313 | 0.016836 | 0.013683 | 0.012142 | 0.058172 | -0.0089037 | 0.065112 | -61.7706 | 59.4498 | -61.7111 | -61.8668 | 59.5276 | 0.16937 | -0.064087 | -0.082397 | 59.6878 | -61.8256 | 0.09613 | -0.24262 | 0.036621 | -0.059509 | -0.16479 | -0.018311 | -0.004578 | -0.059509 | 61.7432 | 61.7249 | 121.3348 | 121.257 | 0.036621 | 121.4951 | 61.9766 | -0.018311 | 121.257 | 0.036621 | 61.9766 | 121.3348 | 121.4951 | -121.4035 | -121.5179
496.0938 | 121.7926 | -61.7569 | 59.6649 | 0.15068 | 0.014058 | 0.011546 | 0.0093653 | 0.060094 | -0.01104 | 0.064258 | -61.8759 | 59.4452 | -61.7569 | -61.972 | 59.4223 | -0.059509 | -0.27466 | -0.37994 | 59.6649 | -61.8759 | 0 | -0.21973 | -0.11902 | -0.21515 | -0.24262 | -0.11902 | 0 | -0.11902 | 61.4822 | 61.377 | 121.1792 | 121.2021 | -0.11902 | 121.4218 | 61.6974 | -0.11902 | 121.2021 | -0.11902 | 61.6974 | 121.1792 | 121.4218 | -121.4218 | -121.5408
497.7812 | 121.7972 | -61.6287 | 59.8022 | 0.020981 | 0.016195 | 0.011546 | 0.0025293 | 0.054967 | -0.0063403 | 0.064899 | -61.7477 | 59.5367 | -61.6058 | -61.821 | 59.6054 | 0.15564 | 0.064087 | 0.12817 | 59.7015 | -61.821 | 0.022888 | -0.2655 | -0.11902 | -0.19226 | -0.19684 | -0.19226 | -0.10071 | -0.14191 | 61.6928 | 61.7569 | 121.2341 | 121.1655 | -0.11902 | 121.3303 | 61.7844 | -0.19226 | 121.1655 | -0.11902 | 61.7844 | 121.2341 | 121.3303 | -121.4081 | -121.6232
499.5312 | 121.6873 | -61.7935 | 59.7153 | -0.017166 | 0.014699 | 0.014324 | 0.0091517 | 0.056676 | -0.0091173 | 0.06554 | -61.8073 | 59.4681 | -61.7111 | -61.8851 | 59.5001 | 0.11902 | -0.09613 | -0.16937 | 59.642 | -61.8851 | 0.082397 | -0.24719 | -0.013733 | -0.091553 | -0.21515 | -0.091553 | -0.073242 | -0.09613 | 61.6974 | 61.6241 | 121.2936 | 121.2616 | -0.013733 | 121.4355 | 61.9125 | -0.091553 | 121.2616 | -0.013733 | 61.9125 | 121.2936 | 121.4355 | -121.4264 | -121.6003
501.2812 | 121.8246 | -61.6287 | 59.7656 | 0.043869 | 0.01534 | 0.010478 | 0.00060666 | 0.05454 | -0.0054859 | 0.065753 | -61.7661 | 59.5093 | -61.6058 | -61.8393 | 59.5779 | 0.10986 | -0.073242 | 0.022888 | 59.6558 | -61.7981 | 0.022888 | -0.25635 | -0.13733 | -0.21057 | -0.18768 | -0.16937 | -0.10986 | -0.16022 | 61.5555 | 61.6516 | 121.2067 | 121.138 | -0.13733 | 121.2845 | 61.7386 | -0.16937 | 121.138 | -0.13733 | 61.7386 | 121.2067 | 121.2845 | -121.3715 | -121.5637
503.0312 | 121.7331 | -61.734 | 59.7473 | -0.21553 | 0.015127 | 0.011546 | 0.0057337 | 0.055395 | -0.0048449 | 0.064899 | -61.7615 | 59.6146 | -61.6196 | -61.8347 | 59.5871 | 0.3479 | 0.46234 | 0.30212 | 59.7565 | -61.8073 | 0.11444 | -0.13275 | -0.027466 | -0.10071 | -0.16022 | -0.073242 | 0.009156 | -0.14191 | 62.1964 | 62.0361 | 121.3211 | 121.3486 | -0.027466 | 121.4905 | 62.0819 | -0.073242 | 121.3486 | -0.027466 | 62.0819 | 121.3211 | 121.4905 | -121.3669 | -121.5546
504.7031 | 121.7239 | -61.7294 | 59.7702 | -0.20027 | 0.016408 | 0.0074875 | 0.0048791 | 0.056035 | -0.0074085 | 0.064685 | -61.7111 | 59.6008 | -61.5829 | -61.7935 | 59.61 | 0.36163 | 0.43945 | 0.36163 | 59.7473 | -61.7844 | 0.14648 | -0.16937 | 0.01831 | -0.064087 | -0.16022 | -0.054932 | -0.022889 | -0.12817 | 62.1689 | 62.0911 | 121.3394 | 121.3303 | 0.01831 | 121.4767 | 62.0911 | -0.054932 | 121.3303 | 0.01831 | 62.0911 | 121.3394 | 121.4767 | -121.3531 | -121.5546
506.4531 | 121.7926 | -61.6104 | 59.8297 | 0.013352 | 0.014913 | 0.0098373 | 0.0021021 | 0.056249 | -0.0052721 | 0.06554 | -61.7386 | 59.5001 | -61.6287 | -61.821 | 59.5917 | 0.1831 | 0.09613 | 0.16479 | 59.7244 | -61.7661 | -0.01831 | -0.32959 | -0.12817 | -0.21057 | -0.23804 | -0.15564 | -0.10529 | -0.10986 | 61.7065 | 61.7752 | 121.2021 | 121.1105 | -0.12817 | 121.3348 | 61.7935 | -0.15564 | 121.1105 | -0.12817 | 61.7935 | 121.2021 | 121.3348 | -121.4584 | -121.5958
508.1406 | 121.788 | -61.7294 | 59.6649 | 0.082016 | 0.013418 | 0.0081283 | 0.011288 | 0.057744 | -0.0089037 | 0.065326 | -61.8805 | 59.4589 | -61.7386 | -61.9812 | 59.4177 | -0.045776 | -0.21057 | -0.34332 | 59.6466 | -61.8713 | -0.009155 | -0.20599 | -0.15106 | -0.25177 | -0.24719 | -0.14191 | -0.018311 | -0.14191 | 61.5189 | 61.3861 | 121.1472 | 121.1884 | -0.15106 | 121.376 | 61.6837 | -0.14191 | 121.1884 | -0.15106 | 61.6837 | 121.1472 | 121.376 | -121.4035 | -121.5363
509.8906 | 121.701 | -61.7111 | 59.7794 | -0.23842 | 0.014272 | 0.010906 | 0.0038111 | 0.056035 | -0.0076221 | 0.06618 | -61.6837 | 59.5963 | -61.5646 | -61.7661 | 59.6283 | 0.40741 | 0.4303 | 0.4303 | 59.7519 | -61.7615 | 0.14648 | -0.18311 | 0.027466 | -0.054931 | -0.15106 | -0.050354 | -0.027466 | -0.11902 | 62.1414 | 62.1414 | 121.3394 | 121.3074 | 0.027466 | 121.463 | 62.1185 | -0.050354 | 121.3074 | 0.027466 | 62.1185 | 121.3394 | 121.463 | -121.344 | -121.5408
511.5781 | 121.756 | -61.7111 | 59.7519 | 0.20409 | 0.020254 | 0.012828 | 0.0095789 | 0.059453 | -0.0063403 | 0.065753 | -61.8301 | 59.4543 | -61.702 | -61.908 | 59.5047 | -0.022888 | -0.39368 | -0.29755 | 59.6375 | -61.8576 | 0.009156 | -0.29755 | -0.11902 | -0.19684 | -0.24719 | -0.14648 | -0.11444 | -0.12817 | 61.3174 | 61.4136 | 121.2158 | 121.1655 | -0.11902 | 121.3486 | 61.6882 | -0.14648 | 121.1655 | -0.11902 | 61.6882 | 121.2158 | 121.3486 | -121.4539 | -121.6095
513.3281 | 121.6736 | -61.7111 | 59.8251 | -0.12398 | 0.014486 | 0.013255 | 0.0046655 | 0.052831 | -0.0052721 | 0.067249 | -61.6562 | 59.5551 | -61.5829 | -61.6928 | 59.729 | 0.3891 | 0.2655 | 0.46234 | 59.729 | -61.7661 | 0.12817 | -0.27008 | 0.054932 | 0.018311 | -0.09613 | -0.054931 | -0.09613 | -0.073242 | 61.9766 | 62.1735 | 121.4401 | 121.2662 | 0.054932 | 121.4401 | 62.1002 | -0.054931 | 121.2662 | 0.054932 | 62.1002 | 121.4401 | 121.4401 | -121.4081 | -121.5912
515.0781 | 121.7834 | -61.734 | 59.6786 | 0.11253 | 0.018758 | 0.013042 | 0.0082971 | 0.057744 | -0.0074085 | 0.065753 | -61.8439 | 59.4772 | -61.7477 | -61.9308 | 59.4589 | -0.032043 | -0.29755 | -0.36163 | 59.642 | -61.9171 | -0.013733 | -0.20142 | -0.10986 | -0.19684 | -0.21973 | -0.1831 | -0.036621 | -0.09613 | 61.4365 | 61.3724 | 121.1929 | 121.2112 | -0.10986 | 121.376 | 61.702 | -0.1831 | 121.2112 | -0.10986 | 61.702 | 121.1929 | 121.376 | -121.4264 | -121.5958
516.7656 | 121.7148 | -61.7065 | 59.7748 | -0.2079 | 0.016408 | 0.0087693 | 0.0055201 | 0.054967 | -0.0039905 | 0.064899 | -61.7569 | 59.5871 | -61.6241 | -61.8118 | 59.5963 | 0.33417 | 0.45776 | 0.32044 | 59.7931 | -61.7752 | 0.082397 | -0.18768 | -0.050354 | -0.10529 | -0.17853 | -0.068665 | 0.018311 | -0.13275 | 62.1643 | 62.027 | 121.3028 | 121.2936 | -0.050354 | 121.4996 | 62.0407 | -0.068665 | 121.2936 | -0.050354 | 62.0407 | 121.3028 | 121.4996 | -121.3989 | -121.55
518.5 | 121.669 | -61.7752 | 59.7153 | -0.032425 | 0.014272 | 0.0083419 | 0.010647 | 0.056249 | -0.0082629 | 0.06554 | -61.8027 | 59.4589 | -61.6837 | -61.8759 | 59.5047 | 0.13275 | -0.086975 | -0.13733 | 59.6741 | -61.8393 | 0.091553 | -0.25635 | -0.027465 | -0.10071 | -0.21057 | -0.064086 | -0.041199 | -0.11902 | 61.6882 | 61.6379 | 121.2799 | 121.2341 | -0.027465 | 121.4493 | 61.908 | -0.064086 | 121.2341 | -0.027465 | 61.908 | 121.2799 | 121.4493 | -121.3989 | -121.5546
520.2031 | 121.7926 | -61.6241 | 59.8068 | 0.03624 | 0.012777 | 0.0091965 | 0.0012475 | 0.055822 | -0.0056995 | 0.064258 | -61.7523 | 59.5459 | -61.6058 | -61.8347 | 59.6008 | 0.15564 | 0.054932 | 0.11902 | 59.7061 | -61.8073 | 0.018311 | -0.26093 | -0.12817 | -0.21057 | -0.20599 | -0.1831 | -0.10071 | -0.14648 | 61.6791 | 61.7432 | 121.225 | 121.17 | -0.12817 | 121.3303 | 61.7798 | -0.1831 | 121.17 | -0.12817 | 61.7798 | 121.225 | 121.3303 | -121.4127 | -121.6141
521.9375 | 121.8063 | -61.6058 | 59.8251 | 0.03624 | 0.017049 | 0.013255 | 0.0027429 | 0.055608 | -0.0076221 | 0.065967 | -61.7523 | 59.5413 | -61.6104 | -61.8347 | 59.5917 | 0.16937 | 0.045776 | 0.13275 | 59.7061 | -61.8118 | -0.004578 | -0.28381 | -0.14648 | -0.22888 | -0.23346 | -0.20599 | -0.11902 | -0.14191 | 61.6516 | 61.7386 | 121.1975 | 121.1472 | -0.14648 | 121.312 | 61.7752 | -0.20599 | 121.1472 | -0.14648 | 61.7752 | 121.1975 | 121.312 | -121.4355 | -121.637
523.6875 | 121.7056 | -61.7157 | 59.7931 | -0.23079 | 0.014699 | 0.011974 | 0.0065881 | 0.055181 | -0.0080493 | 0.063831 | -61.6882 | 59.5596 | -61.6058 | -61.7569 | 59.6375 | 0.40283 | 0.43488 | 0.42572 | 59.7473 | -61.7752 | 0.10986 | -0.23346 | 0.027466 | -0.041199 | -0.15564 | -0.05951 | -0.045777 | -0.082397 | 62.1506 | 62.1414 | 121.3531 | 121.2753 | 0.027466 | 121.463 | 62.1185 | -0.05951 | 121.2753 | 0.027466 | 62.1185 | 121.3531 | 121.463 | -121.3989 | -121.5683
525.4531 | 121.7834 | -61.734 | 59.6924 | 0.12016 | 0.014272 | 0.010265 | 0.010006 | 0.056463 | -0.0061267 | 0.066608 | -61.8805 | 59.4635 | -61.7569 | -61.9446 | 59.4543 | -0.054932 | -0.29297 | -0.36621 | 59.6649 | -61.8668 | -0.022888 | -0.22888 | -0.14648 | -0.21057 | -0.23804 | -0.13275 | -0.027466 | -0.1236 | 61.441 | 61.3678 | 121.1884 | 121.1975 | -0.14648 | 121.3989 | 61.6791 | -0.13275 | 121.1975 | -0.14648 | 61.6791 | 121.1884 | 121.3989 | -121.4493 | -121.5591
527.1406 | 121.7148 | -61.7523 | 59.7748 | -0.16212 | 0.014272 | 0.014751 | 0.0046655 | 0.054754 | -0.0056995 | 0.066608 | -61.7844 | 59.5963 | -61.6058 | -61.8256 | 59.5871 | 0.33875 | 0.46234 | 0.32959 | 59.7473 | -61.8073 | 0.14648 | -0.17853 | -0.032044 | -0.073243 | -0.18768 | -0.054932 | -0.027466 | -0.17853 | 62.2147 | 62.0819 | 121.3394 | 121.3486 | -0.032044 | 121.4996 | 62.0911 | -0.054932 | 121.3486 | -0.032044 | 62.0911 | 121.3394 | 121.4996 | -121.3806 | -121.582
528.875 | 121.6782 | -61.6837 | 59.8297 | -0.09346 | 0.015554 | 0.0091965 | 0.0044519 | 0.054754 | -0.0048449 | 0.064044 | -61.647 | 59.5688 | -61.5509 | -61.6974 | 59.729 | 0.3891 | 0.26093 | 0.45319 | 59.6741 | -61.7706 | 0.13275 | -0.26093 | 0.036621 | -0.013733 | -0.10071 | -0.086975 | -0.15564 | -0.096131 | 61.9446 | 62.1368 | 121.4127 | 121.2524 | 0.036621 | 121.3577 | 62.0728 | -0.086975 | 121.2524 | 0.036621 | 62.0728 | 121.4127 | 121.3577 | -121.3806 | -121.6003
530.625 | 121.6599 | -61.6608 | 59.8343 | -0.1545 | 0.014699 | 0.0094101 | 0.0057337 | 0.054113 | -0.0069811 | 0.063617 | -61.6241 | 59.5596 | -61.5829 | -61.6837 | 59.7107 | 0.41657 | 0.30212 | 0.50812 | 59.7427 | -61.7432 | 0.07782 | -0.27466 | 0.036621 | -0.022888 | -0.1236 | -0.082397 | -0.091553 | -0.041199 | 61.9629 | 62.1689 | 121.3715 | 121.2204 | 0.036621 | 121.4035 | 62.0773 | -0.082397 | 121.2204 | 0.036621 | 62.0773 | 121.3715 | 121.4035 | -121.4172 | -121.5775
532.3281 | 121.7056 | -61.7249 | 59.7336 | -0.2079 | 0.015554 | 0.011546 | 0.0076563 | 0.055395 | -0.0091173 | 0.064899 | -61.7706 | 59.5642 | -61.6608 | -61.8256 | 59.5596 | 0.31128 | 0.3891 | 0.26093 | 59.7519 | -61.7706 | 0.064087 | -0.16937 | -0.045776 | -0.10071 | -0.17395 | -0.045776 | 0.01831 | -0.10986 | 62.114 | 61.9858 | 121.2845 | 121.2891 | -0.045776 | 121.4767 | 62.0361 | -0.045776 | 121.2891 | -0.045776 | 62.0361 | 121.2845 | 121.4767 | -121.3943 | -121.5042
534.0625 | 121.6278 | -61.7798 | 59.7244 | -0.09346 | 0.016408 | 0.011119 | 0.0095789 | 0.057317 | -0.0052721 | 0.064899 | -61.7615 | 59.5413 | -61.6653 | -61.8301 | 59.5596 | 0.24261 | 0.064087 | 0.041199 | 59.6786 | -61.8713 | 0.11444 | -0.1831 | 0.01831 | -0.050354 | -0.16479 | -0.091553 | -0.045776 | -0.096131 | 61.8439 | 61.821 | 121.3394 | 121.3211 | 0.01831 | 121.4584 | 62.0224 | -0.091553 | 121.3211 | 0.01831 | 62.0224 | 121.3394 | 121.4584 | -121.3898 | -121.5958
535.75 | 121.7239 | -61.7294 | 59.7565 | -0.1545 | 0.017263 | 0.0068467 | 0.0023157 | 0.054326 | -0.0071947 | 0.063831 | -61.7432 | 59.6008 | -61.6196 | -61.821 | 59.5963 | 0.35248 | 0.45319 | 0.34332 | 59.7336 | -61.8073 | 0.10986 | -0.15564 | -0.013733 | -0.091553 | -0.16022 | -0.07782 | -0.022888 | -0.1236 | 62.1826 | 62.0728 | 121.3257 | 121.3303 | -0.013733 | 121.463 | 62.0819 | -0.07782 | 121.3303 | -0.013733 | 62.0819 | 121.3257 | 121.463 | -121.376 | -121.5637
537.5 | 121.756 | -61.6974 | 59.729 | 0.1049 | 0.016408 | 0.010906 | 0.0065881 | 0.057317 | -0.0050585 | 0.064044 | -61.8027 | 59.4543 | -61.6928 | -61.853 | 59.5551 | 0.032043 | -0.40283 | -0.21515 | 59.5871 | -61.8851 | 0.004578 | -0.27466 | -0.10529 | -0.15564 | -0.17395 | -0.18768 | -0.14191 | -0.10986 | 61.2946 | 61.4822 | 121.2524 | 121.1517 | -0.10529 | 121.2845 | 61.7294 | -0.18768 | 121.1517 | -0.10529 | 61.7294 | 121.2524 | 121.2845 | -121.4218 | -121.6141
539.25 | 121.788 | -61.6379 | 59.8114 | -0.0095368 | 0.013631 | 0.0068467 | 0.0021021 | 0.05454 | -0.0052721 | 0.06554 | -61.7569 | 59.5642 | -61.6196 | -61.8164 | 59.61 | 0.21057 | 0.10986 | 0.20142 | 59.6741 | -61.7981 | 0.01831 | -0.24719 | -0.11902 | -0.17853 | -0.20142 | -0.16022 | -0.13733 | -0.13733 | 61.7477 | 61.8393 | 121.2479 | 121.2021 | -0.11902 | 121.3119 | 61.8484 | -0.16022 | 121.2021 | -0.11902 | 61.8484 | 121.2479 | 121.3119 | -121.431 | -121.6095
540.9375 | 121.7743 | -61.615 | 59.7931 | -0.032425 | 0.014272 | 0.010051 | 0.0031701 | 0.053045 | -0.0042041 | 0.064471 | -61.7203 | 59.523 | -61.6104 | -61.7752 | 59.6603 | 0.27466 | 0.16937 | 0.3067 | 59.7061 | -61.7752 | 0.004577 | -0.27008 | -0.10529 | -0.16022 | -0.13275 | -0.16022 | -0.086975 | -0.10986 | 61.7844 | 61.9217 | 121.2753 | 121.138 | -0.10529 | 121.3211 | 61.8896 | -0.16022 | 121.138 | -0.10529 | 61.8896 | 121.2753 | 121.3211 | -121.4035 | -121.5683
542.6875 | 121.788 | -61.7111 | 59.7198 | 0.12779 | 0.015127 | 0.012401 | 0.0097925 | 0.057531 | -0.0071947 | 0.065967 | -61.8301 | 59.5001 | -61.7386 | -61.9263 | 59.4727 | -0.054932 | -0.35248 | -0.35706 | 59.642 | -61.8622 | -0.027465 | -0.21973 | -0.11902 | -0.21515 | -0.24719 | -0.15106 | -0.07782 | -0.091553 | 61.3586 | 61.3541 | 121.1838 | 121.2112 | -0.11902 | 121.3531 | 61.6562 | -0.15106 | 121.2112 | -0.11902 | 61.6562 | 121.1838 | 121.3531 | -121.4584 | -121.582
544.4531 | 121.7926 | -61.7249 | 59.7244 | 0.11253 | 0.016836 | 0.0096237 | 0.01022 | 0.058385 | -0.0059131 | 0.065326 | -61.8622 | 59.4818 | -61.7477 | -61.9263 | 59.4635 | -0.045776 | -0.32501 | -0.37994 | 59.6329 | -61.8805 | -0.022888 | -0.24261 | -0.13733 | -0.20142 | -0.26093 | -0.15564 | -0.091552 | -0.11444 | 61.3998 | 61.3449 | 121.1884 | 121.2067 | -0.13733 | 121.3577 | 61.6791 | -0.15564 | 121.2067 | -0.13733 | 61.6791 | 121.1884 | 121.3577 | -121.4722 | -121.6049
546.1406 | 121.7468 | -61.6791 | 59.761 | 0.15068 | 0.014272 | 0.0079147 | 0.0055201 | 0.055395 | -0.0074085 | 0.066394 | -61.7706 | 59.436 | -61.6928 | -61.8301 | 59.5596 | 0.018311 | -0.40283 | -0.20599 | 59.6146 | -61.8484 | -0.013733 | -0.32501 | -0.091553 | -0.15106 | -0.20142 | -0.16937 | -0.14648 | -0.07782 | 61.2762 | 61.4731 | 121.2387 | 121.1151 | -0.091553 | 121.2936 | 61.6974 | -0.16937 | 121.1151 | -0.091553 | 61.6974 | 121.2387 | 121.2936 | -121.4539 | -121.6095
547.875 | 121.701 | -61.7065 | 59.7382 | -0.2079 | 0.016836 | 0.0085555 | 0.0050929 | 0.055395 | -0.0061267 | 0.063831 | -61.7661 | 59.6008 | -61.615 | -61.8301 | 59.5734 | 0.32959 | 0.41657 | 0.25635 | 59.7794 | -61.7981 | 0.091553 | -0.13733 | -0.059509 | -0.1236 | -0.1648 | -0.091553 | 0.041199 | -0.15106 | 62.1231 | 61.9629 | 121.2799 | 121.3074 | -0.059509 | 121.4859 | 62.0361 | -0.091553 | 121.3074 | -0.059509 | 62.0361 | 121.2799 | 121.4859 | -121.3531 | -121.5363
549.625 | 121.7697 | -61.7203 | 59.7015 | 0.17357 | 0.017049 | 0.011333 | 0.0076563 | 0.057958 | -0.0050585 | 0.064258 | -61.8439 | 59.4864 | -61.7157 | -61.908 | 59.4955 | -0.036621 | -0.36163 | -0.32044 | 59.6237 | -61.8805 | 0.004578 | -0.21515 | -0.1236 | -0.18768 | -0.20599 | -0.16022 | -0.07782 | -0.12817 | 61.3586 | 61.3998 | 121.2158 | 121.2067 | -0.1236 | 121.344 | 61.6837 | -0.16022 | 121.2067 | -0.1236 | 61.6837 | 121.2158 | 121.344 | -121.4172 | -121.582
551.3594 | 121.756 | -61.6745 | 59.7748 | 0.16594 | 0.014058 | 0.015392 | 0.0040247 | 0.058172 | -0.0084765 | 0.065967 | -61.7569 | 59.4086 | -61.6745 | -61.8256 | 59.5734 | 0.054932 | -0.38452 | -0.16479 | 59.61 | -61.8256 | 0 | -0.36621 | -0.082397 | -0.15106 | -0.20142 | -0.15106 | -0.16479 | -0.082397 | 61.29 | 61.5097 | 121.2479 | 121.0831 | -0.082397 | 121.2845 | 61.7294 | -0.15106 | 121.0831 | -0.082397 | 61.7294 | 121.2479 | 121.2845 | -121.4493 | -121.6003
553.0938 | 121.756 | -61.6745 | 59.7931 | 0.13542 | 0.01534 | 0.0089829 | 0.0029565 | 0.057317 | -0.0065539 | 0.065967 | -61.7294 | 59.4315 | -61.6699 | -61.8118 | 59.5825 | 0.064087 | -0.31586 | -0.10071 | 59.6375 | -61.8164 | 0.004578 | -0.36163 | -0.054931 | -0.13733 | -0.21057 | -0.14191 | -0.15564 | -0.059509 | 61.3586 | 61.5738 | 121.257 | 121.106 | -0.054931 | 121.312 | 61.7386 | -0.14191 | 121.106 | -0.054931 | 61.7386 | 121.257 | 121.312 | -121.463 | -121.6095
554.8438 | 121.7422 | -61.6699 | 59.7977 | 0.14305 | 0.015127 | 0.012828 | 0.0068017 | 0.055822 | -0.0067675 | 0.064258 | -61.734 | 59.4223 | -61.6745 | -61.7981 | 59.5871 | 0.064087 | -0.31586 | -0.09613 | 59.6512 | -61.8164 | -0.004578 | -0.37537 | -0.064087 | -0.12817 | -0.21057 | -0.14648 | -0.14648 | -0.059509 | 61.3541 | 61.5738 | 121.257 | 121.0922 | -0.064087 | 121.3211 | 61.734 | -0.14648 | 121.0922 | -0.064087 | 61.734 | 121.257 | 121.3211 | -121.4722 | -121.6141
556.5312 | 121.701 | -61.7661 | 59.7061 | 0.02861 | 0.015767 | 0.010692 | 0.011074 | 0.057958 | -0.0074085 | 0.065112 | -61.8256 | 59.4818 | -61.7249 | -61.9125 | 59.4727 | 0.050354 | -0.15564 | -0.24719 | 59.6466 | -61.8713 | 0.041198 | -0.2243 | -0.05951 | -0.14648 | -0.23346 | -0.10529 | -0.05951 | -0.10071 | 61.6104 | 61.5189 | 121.2387 | 121.2479 | -0.05951 | 121.4127 | 61.8164 | -0.10529 | 121.2479 | -0.05951 | 61.8164 | 121.2387 | 121.4127 | -121.431 | -121.5775
558.2812 | 121.7972 | -61.7249 | 59.7015 | 0.1049 | 0.016408 | 0.010692 | 0.0074427 | 0.059667 | -0.0065539 | 0.065326 | -61.8301 | 59.491 | -61.702 | -61.9171 | 59.4772 | -0.054932 | -0.28839 | -0.3479 | 59.6649 | -61.8622 | 0.022889 | -0.21057 | -0.10529 | -0.19226 | -0.2243 | -0.13733 | -0.036621 | -0.12817 | 61.4365 | 61.377 | 121.2021 | 121.2158 | -0.10529 | 121.3898 | 61.6699 | -0.13733 | 121.2158 | -0.10529 | 61.6699 | 121.2021 | 121.3898 | -121.4035 | -121.5637
560.0312 | 121.701 | -61.7065 | 59.7839 | -0.13161 | 0.016622 | 0.0047103 | 0.0048791 | 0.054754 | -0.0059131 | 0.064044 | -61.7157 | 59.6191 | -61.5875 | -61.7935 | 59.61 | 0.35706 | 0.46234 | 0.34332 | 59.7656 | -61.7615 | 0.11902 | -0.16479 | -0.009155 | -0.086975 | -0.17395 | -0.054932 | -0.018311 | -0.12817 | 62.1689 | 62.0499 | 121.3165 | 121.3257 | -0.009155 | 121.4722 | 62.0636 | -0.054932 | 121.3257 | -0.009155 | 62.0636 | 121.3165 | 121.4722 | -121.3715 | -121.5454
561.7812 | 121.6736 | -61.7798 | 59.7473 | -0.032425 | 0.016836 | 0.013042 | 0.0089381 | 0.057104 | -0.0091173 | 0.066608 | -61.7569 | 59.5184 | -61.6882 | -61.8393 | 59.5551 | 0.16022 | -0.07782 | -0.10529 | 59.7015 | -61.8301 | 0.091553 | -0.22888 | 0.022888 | -0.059509 | -0.19226 | -0.050354 | -0.045776 | -0.068665 | 61.702 | 61.6745 | 121.3348 | 121.2982 | 0.022888 | 121.4813 | 61.94 | -0.050354 | 121.2982 | 0.022888 | 61.94 | 121.3348 | 121.4813 | -121.4355 | -121.5775
563.4688 | 121.756 | -61.6562 | 59.7931 | 0.12016 | 0.01534 | 0.010906 | 0.0029565 | 0.056676 | -0.0063403 | 0.067249 | -61.734 | 59.4818 | -61.6516 | -61.8118 | 59.5917 | 0.07782 | -0.28381 | -0.086975 | 59.6466 | -61.8347 | 0.004578 | -0.31128 | -0.07782 | -0.15564 | -0.20142 | -0.17853 | -0.14648 | -0.082398 | 61.3724 | 61.5692 | 121.2479 | 121.138 | -0.07782 | 121.3028 | 61.734 | -0.17853 | 121.138 | -0.07782 | 61.734 | 121.2479 | 121.3028 | -121.4447 | -121.6278
565.2344 | 121.7926 | -61.5967 | 59.8206 | -0.0095368 | 0.017049 | 0.010478 | 0.0027429 | 0.054754 | -0.0046313 | 0.065753 | -61.734 | 59.5276 | -61.5784 | -61.7935 | 59.6466 | 0.22888 | 0.11902 | 0.22888 | 59.7061 | -61.7752 | 0.018311 | -0.29297 | -0.13733 | -0.19684 | -0.17395 | -0.17853 | -0.11444 | -0.15564 | 61.7157 | 61.8256 | 121.2433 | 121.1243 | -0.13733 | 121.3028 | 61.8256 | -0.17853 | 121.1243 | -0.13733 | 61.8256 | 121.2433 | 121.3028 | -121.3989 | -121.5958
566.9219 | 121.7194 | -61.6974 | 59.7656 | -0.20027 | 0.015554 | 0.010692 | 0.0068017 | 0.056463 | -0.0076221 | 0.063617 | -61.734 | 59.6283 | -61.6058 | -61.8027 | 59.61 | 0.3479 | 0.45776 | 0.31128 | 59.7885 | -61.7615 | 0.091553 | -0.13733 | -0.036621 | -0.10529 | -0.15564 | -0.064087 | 0.022888 | -0.12817 | 62.1552 | 62.0087 | 121.3074 | 121.3257 | -0.036621 | 121.4859 | 62.0453 | -0.064087 | 121.3257 | -0.036621 | 62.0453 | 121.3074 | 121.4859 | -121.3715 | -121.5271
568.6719 | 121.7743 | -61.6928 | 59.7244 | 0.097275 | 0.016622 | 0.0089829 | 0.0095789 | 0.056463 | -0.0086901 | 0.065967 | -61.821 | 59.4772 | -61.7111 | -61.9308 | 59.4818 | -0.036621 | -0.33875 | -0.35706 | 59.6191 | -61.8668 | -0.018311 | -0.24719 | -0.12817 | -0.23804 | -0.24261 | -0.17395 | -0.10529 | -0.10986 | 61.3541 | 61.3358 | 121.1746 | 121.17 | -0.12817 | 121.312 | 61.6562 | -0.17395 | 121.17 | -0.12817 | 61.6562 | 121.1746 | 121.312 | -121.4355 | -121.5912
570.4375 | 121.6919 | -61.6745 | 59.8251 | -0.18501 | 0.012563 | 0.0077011 | 0.0040247 | 0.056676 | -0.0071947 | 0.065112 | -61.6562 | 59.5917 | -61.5372 | -61.7065 | 59.6832 | 0.41199 | 0.41657 | 0.46692 | 59.761 | -61.7111 | 0.13733 | -0.23346 | 0.018311 | -0.032043 | -0.14191 | -0.036621 | -0.064087 | -0.11902 | 62.0911 | 62.1414 | 121.3577 | 121.2662 | 0.018311 | 121.4355 | 62.0865 | -0.036621 | 121.2662 | 0.018311 | 62.0865 | 121.3577 | 121.4355 | -121.3623 | -121.5363
572.125 | 121.756 | -61.6653 | 59.7382 | 0.19646 | 0.014913 | 0.011119 | 0.0087243 | 0.055181 | -0.0067675 | 0.067035 | -61.8027 | 59.4681 | -61.6974 | -61.8668 | 59.523 | -0.022888 | -0.38452 | -0.30212 | 59.6649 | -61.8393 | -0.032044 | -0.27008 | -0.13733 | -0.20142 | -0.21515 | -0.17395 | -0.073242 | -0.10529 | 61.2808 | 61.3632 | 121.1884 | 121.1334 | -0.13733 | 121.3303 | 61.6425 | -0.17395 | 121.1334 | -0.13733 | 61.6425 | 121.1884 | 121.3303 | -121.4355 | -121.5775
573.8594 | 121.7789 | -61.6104 | 59.8297 | 0.013352 | 0.015981 | 0.0096237 | 0.00039306 | 0.056463 | -0.0065539 | 0.063403 | -61.7065 | 59.5871 | -61.5601 | -61.7523 | 59.6466 | 0.23346 | 0.11902 | 0.2243 | 59.7244 | -61.7523 | 0.050354 | -0.24262 | -0.09613 | -0.14191 | -0.18311 | -0.14191 | -0.10529 | -0.14648 | 61.7294 | 61.8347 | 121.257 | 121.1975 | -0.09613 | 121.3348 | 61.8439 | -0.14191 | 121.1975 | -0.09613 | 61.8439 | 121.257 | 121.3348 | -121.3898 | -121.582
575.5938 | 121.701 | -61.734 | 59.761 | -0.1545 | 0.016836 | 0.0051377 | 0.0089381 | 0.057958 | -0.0067675 | 0.064685 | -61.7432 | 59.5917 | -61.6241 | -61.7798 | 59.6054 | 0.32044 | 0.34332 | 0.21973 | 59.7794 | -61.7615 | 0.10986 | -0.16937 | -0.009155 | -0.045776 | -0.15564 | -0.027466 | 0.018311 | -0.11902 | 62.0773 | 61.9537 | 121.3394 | 121.3257 | -0.009155 | 121.5134 | 62.0544 | -0.027466 | 121.3257 | -0.009155 | 62.0544 | 121.3394 | 121.5134 | -121.3852 | -121.5225
577.3281 | 121.6736 | -61.7386 | 59.7519 | -0.047684 | 0.014699 | 0.010265 | 0.0095789 | 0.058812 | -0.010186 | 0.065326 | -61.7386 | 59.523 | -61.6562 | -61.8027 | 59.5779 | 0.21057 | 0.004578 | 0.013733 | 59.7153 | -61.7889 | 0.082397 | -0.22888 | 0 | -0.064087 | -0.17395 | -0.050354 | -0.036621 | -0.082397 | 61.7432 | 61.7523 | 121.3165 | 121.2616 | 0 | 121.4539 | 61.9492 | -0.050354 | 121.2616 | 0 | 61.9492 | 121.3165 | 121.4539 | -121.4081 | -121.5408
579.0781 | 121.6644 | -61.7432 | 59.7519 | -0.0019073 | 0.014913 | 0.011974 | 0.010006 | 0.057958 | -0.0080493 | 0.065326 | -61.7661 | 59.5367 | -61.6425 | -61.8301 | 59.5413 | 0.11444 | -0.10986 | -0.15106 | 59.7244 | -61.8347 | 0.10071 | -0.21515 | -0.022888 | -0.086975 | -0.21057 | -0.091553 | -0.027466 | -0.1236 | 61.6333 | 61.5921 | 121.2845 | 121.2799 | -0.022888 | 121.4676 | 61.8576 | -0.091553 | 121.2799 | -0.022888 | 61.8576 | 121.2845 | 121.4676 | -121.3943 | -121.5866
580.7656 | 121.7468 | -61.6608 | 59.7702 | 0.1812 | 0.015554 | 0.0089829 | 0.0042383 | 0.058172 | -0.0063403 | 0.068103 | -61.7661 | 59.4727 | -61.6837 | -61.8347 | 59.5825 | 0.036621 | -0.39368 | -0.25177 | 59.6603 | -61.8256 | -0.022888 | -0.29755 | -0.10529 | -0.17395 | -0.18768 | -0.16479 | -0.10986 | -0.082397 | 61.2671 | 61.409 | 121.2433 | 121.1334 | -0.10529 | 121.3211 | 61.6974 | -0.16479 | 121.1334 | -0.10529 | 61.6974 | 121.2433 | 121.3211 | -121.4539 | -121.5958
582.5156 | 121.8018 | -61.5875 | 59.8343 | 0.082016 | 0.015554 | 0.0083419 | 0.0010339 | 0.057958 | -0.0035631 | 0.064258 | -61.7065 | 59.5505 | -61.5692 | -61.7844 | 59.6191 | 0.1236 | -0.041199 | 0.054932 | 59.7107 | -61.7569 | 0.01831 | -0.28381 | -0.11902 | -0.19684 | -0.21515 | -0.16937 | -0.1236 | -0.13733 | 61.5463 | 61.6425 | 121.2067 | 121.138 | -0.11902 | 121.2982 | 61.7111 | -0.16937 | 121.138 | -0.11902 | 61.7111 | 121.2067 | 121.2982 | -121.4035 | -121.5912
584.2656 | 121.6782 | -61.7386 | 59.7656 | -0.024795 | 0.017049 | 0.012401 | 0.0095789 | 0.057104 | -0.0095447 | 0.062976 | -61.7294 | 59.5184 | -61.6562 | -61.7981 | 59.5642 | 0.1831 | -0.073242 | -0.10529 | 59.7198 | -61.7889 | 0.082397 | -0.24719 | 0.009155 | -0.05951 | -0.20142 | -0.050354 | -0.045776 | -0.073242 | 61.6653 | 61.6333 | 121.3028 | 121.257 | 0.009155 | 121.4584 | 61.9217 | -0.050354 | 121.257 | 0.009155 | 61.9217 | 121.3028 | 121.4584 | -121.4218 | -121.5546
585.9531 | 121.7102 | -61.6653 | 59.8114 | -0.20027 | 0.015767 | 0.0087693 | 0.0027429 | 0.056249 | -0.0095447 | 0.064685 | -61.7294 | 59.61 | -61.5692 | -61.7844 | 59.6329 | 0.34332 | 0.45319 | 0.33417 | 59.7931 | -61.734 | 0.09613 | -0.20142 | -0.064087 | -0.11902 | -0.17853 | -0.068665 | -0.01831 | -0.16022 | 62.1185 | 61.9995 | 121.2982 | 121.2753 | -0.064087 | 121.4584 | 62.0087 | -0.068665 | 121.2753 | -0.064087 | 62.0087 | 121.2982 | 121.4584 | -121.3806 | -121.5454
587.7031 | 121.6461 | -61.7111 | 59.7519 | -0.062942 | 0.015554 | 0.0089829 | 0.0082971 | 0.055608 | -0.0076221 | 0.065753 | -61.7203 | 59.5642 | -61.6379 | -61.7981 | 59.5963 | 0.24261 | 0.018311 | 0.022888 | 59.7153 | -61.8073 | 0.073243 | -0.18768 | -0.009155 | -0.086975 | -0.15564 | -0.09613 | -0.036621 | -0.082398 | 61.7294 | 61.734 | 121.3074 | 121.2753 | -0.009155 | 121.4264 | 61.9537 | -0.09613 | 121.2753 | -0.009155 | 61.9537 | 121.3074 | 121.4264 | -121.3898 | -121.5591
589.4688 | 121.6965 | -61.6928 | 59.7656 | -0.17738 | 0.01534 | 0.0062057 | 0.0038111 | 0.058172 | -0.0086901 | 0.063617 | -61.7249 | 59.6008 | -61.5921 | -61.7889 | 59.6146 | 0.3067 | 0.32501 | 0.21057 | 59.7702 | -61.7386 | 0.10071 | -0.16479 | -0.032044 | -0.09613 | -0.15106 | -0.045776 | 0.004578 | -0.13275 | 62.0178 | 61.9034 | 121.3074 | 121.2936 | -0.032044 | 121.463 | 61.9995 | -0.045776 | 121.2936 | -0.032044 | 61.9995 | 121.3074 | 121.463 | -121.3577 | -121.5042
591.1562 | 121.7056 | -61.6516 | 59.8434 | -0.21553 | 0.015554 | 0.0087693 | 0.0025293 | 0.054113 | -0.0078357 | 0.062763 | -61.6333 | 59.6603 | -61.5097 | -61.7249 | 59.6741 | 0.39368 | 0.45776 | 0.39825 | 59.8022 | -61.7065 | 0.14191 | -0.18311 | 0.01831 | -0.073243 | -0.16937 | -0.054932 | -0.041199 | -0.1236 | 62.1094 | 62.0499 | 121.3257 | 121.3119 | 0.01831 | 121.4539 | 62.0453 | -0.054932 | 121.3119 | 0.01831 | 62.0453 | 121.3257 | 121.4539 | -121.3531 | -121.55
592.9219 | 121.7148 | -61.6791 | 59.8068 | -0.23079 | 0.013418 | 0.01176 | 0.0059473 | 0.05689 | -0.0082629 | 0.064258 | -61.7065 | 59.642 | -61.5646 | -61.7752 | 59.6329 | 0.3479 | 0.41657 | 0.26093 | 59.8297 | -61.6974 | 0.11444 | -0.16479 | -0.027466 | -0.096131 | -0.17395 | -0.018311 | 0.022888 | -0.14191 | 62.0956 | 61.94 | 121.312 | 121.3211 | -0.027466 | 121.5088 | 62.027 | -0.018311 | 121.3211 | -0.027466 | 62.027 | 121.312 | 121.5088 | -121.3715 | -121.5042
594.6719 | 121.6736 | -61.7294 | 59.7839 | -0.032425 | 0.015554 | 0.0096237 | 0.0087243 | 0.058599 | -0.0082629 | 0.066821 | -61.6974 | 59.5551 | -61.6379 | -61.7981 | 59.5871 | 0.17395 | -0.059509 | -0.10071 | 59.761 | -61.7798 | 0.091553 | -0.22888 | 0.032043 | -0.068665 | -0.19684 | -0.050354 | -0.022889 | -0.05951 | 61.6699 | 61.6287 | 121.3165 | 121.2845 | 0.032043 | 121.4905 | 61.9034 | -0.050354 | 121.2845 | 0.032043 | 61.9034 | 121.3165 | 121.4905 | -121.4218 | -121.5637
596.3594 | 121.7194 | -61.7111 | 59.7702 | -0.16212 | 0.014913 | 0.0062057 | 0.0091517 | 0.057104 | -0.0082629 | 0.064258 | -61.7844 | 59.5505 | -61.6516 | -61.8668 | 59.5276 | 0.045776 | -0.15106 | -0.25635 | 59.7153 | -61.8073 | 0.05951 | -0.21973 | -0.073242 | -0.15564 | -0.24262 | -0.09613 | -0.054932 | -0.13275 | 61.5601 | 61.4548 | 121.2387 | 121.2616 | -0.073242 | 121.4264 | 61.7569 | -0.09613 | 121.2616 | -0.073242 | 61.7569 | 121.2387 | 121.4264 | -121.4218 | -121.5775
598.1094 | 121.7697 | -61.647 | 59.7839 | 0.074387 | 0.015127 | 0.011119 | 0.0050929 | 0.058172 | -0.0074085 | 0.06618 | -61.7981 | 59.5322 | -61.6608 | -61.8668 | 59.523 | -0.032043 | -0.30212 | -0.35706 | 59.7107 | -61.8027 | -0.013733 | -0.25177 | -0.15106 | -0.21973 | -0.26093 | -0.15564 | -0.073243 | -0.13733 | 61.3449 | 61.29 | 121.17 | 121.1792 | -0.15106 | 121.3577 | 61.615 | -0.15564 | 121.1792 | -0.15106 | 61.615 | 121.17 | 121.3577 | -121.4447 | -121.5866
599.8594 | 121.7514 | -61.6379 | 59.848 | 0.16594 | 0.014699 | 0.011333 | 0.0048791 | 0.056676 | -0.0069811 | 0.06618 | -61.7294 | 59.5413 | -61.6333 | -61.7844 | 59.6191 | 0.022888 | -0.41199 | -0.25177 | 59.6741 | -61.7844 | 0.004577 | -0.3067 | -0.091553 | -0.14648 | -0.22888 | -0.14648 | -0.17395 | -0.09613 | 61.2259 | 61.3861 | 121.257 | 121.1792 | -0.091553 | 121.3119 | 61.6608 | -0.14648 | 121.1792 | -0.091553 | 61.6608 | 121.257 | 121.3119 | -121.4813 | -121.6324
601.5625 | 121.8018 | -61.5372 | 59.8801 | 0.03624 | 0.015127 | 0.012828 | 0.0029565 | 0.056463 | -0.0080493 | 0.064899 | -61.6425 | 59.6237 | -61.496 | -61.7523 | 59.6786 | 0.10986 | -0.082397 | 0.027466 | 59.7839 | -61.7111 | 0.041198 | -0.25635 | -0.10529 | -0.21515 | -0.20142 | -0.17395 | -0.09613 | -0.14648 | 61.4548 | 61.5646 | 121.2158 | 121.1609 | -0.10529 | 121.3211 | 61.647 | -0.17395 | 121.1609 | -0.10529 | 61.647 | 121.2158 | 121.3211 | -121.376 | -121.5912
603.3281 | 121.7148 | -61.6196 | 59.8709 | -0.12398 | 0.017904 | 0.010906 | 0.0072291 | 0.055608 | -0.0071947 | 0.064899 | -61.647 | 59.7153 | -61.5051 | -61.7157 | 59.6649 | 0.3479 | 0.47607 | 0.35248 | 59.8938 | -61.6837 | 0.11444 | -0.15564 | -0.027466 | -0.09613 | -0.20599 | -0.064087 | 0.022888 | -0.14191 | 62.0956 | 61.972 | 121.2845 | 121.3348 | -0.027466 | 121.5134 | 61.9675 | -0.064087 | 121.3348 | -0.027466 | 61.9675 | 121.2845 | 121.5134 | -121.376 | -121.5546
605 | 121.756 | -61.6013 | 59.7794 | 0.14305 | 0.017476 | 0.010265 | 0.0082971 | 0.057744 | -0.0082629 | 0.067035 | -61.7523 | 59.5596 | -61.647 | -61.8301 | 59.5688 | -0.022888 | -0.36163 | -0.3479 | 59.7519 | -61.7752 | -0.045777 | -0.21973 | -0.15106 | -0.22888 | -0.21057 | -0.17395 | -0.027466 | -0.10529 | 61.2396 | 61.2534 | 121.17 | 121.1609 | -0.15106 | 121.3531 | 61.5784 | -0.17395 | 121.1609 | -0.15106 | 61.5784 | 121.17 | 121.3531 | -121.4264 | -121.5546
606.75 | 121.6782 | -61.5692 | 59.9533 | -0.14687 | 0.014058 | 0.010478 | -3.414e-05 | 0.056463 | -0.0065539 | 0.063831 | -61.5143 | 59.6603 | -61.4365 | -61.5784 | 59.8206 | 0.41199 | 0.28381 | 0.48065 | 59.8526 | -61.5875 | 0.13275 | -0.29297 | 0.054932 | -0.009155 | -0.13275 | -0.01831 | -0.10071 | -0.07782 | 61.853 | 62.0499 | 121.3898 | 121.2296 | 0.054932 | 121.4218 | 61.9812 | -0.01831 | 121.2296 | 0.054932 | 61.9812 | 121.3898 | 121.4218 | -121.3898 | -121.5408
608.5 | 121.7697 | -61.6104 | 59.7977 | 0.11253 | 0.01299 | 0.013042 | 0.011501 | 0.058385 | -0.0078357 | 0.064899 | -61.7523 | 59.5779 | -61.6333 | -61.8393 | 59.5505 | -0.022888 | -0.26093 | -0.36621 | 59.7794 | -61.734 | -0.022888 | -0.21973 | -0.14191 | -0.22888 | -0.24719 | -0.1236 | -0.01831 | -0.11902 | 61.3495 | 61.2442 | 121.1609 | 121.1884 | -0.14191 | 121.3898 | 61.5875 | -0.1236 | 121.1884 | -0.14191 | 61.5875 | 121.1609 | 121.3898 | -121.431 | -121.5317
610.2344 | 121.6919 | -61.5326 | 59.9854 | -0.10109 | 0.014486 | 0.0089829 | 0.0023157 | 0.055608 | -0.0061267 | 0.065326 | -61.5143 | 59.6786 | -61.4456 | -61.5875 | 59.816 | 0.38452 | 0.22888 | 0.44403 | 59.8343 | -61.6241 | 0.086975 | -0.3067 | 0.018311 | -0.054931 | -0.16937 | -0.091553 | -0.15106 | -0.068664 | 61.7615 | 61.9766 | 121.3486 | 121.2112 | 0.018311 | 121.3669 | 61.9171 | -0.091553 | 121.2112 | 0.018311 | 61.9171 | 121.3486 | 121.3669 | -121.431 | -121.6095
611.9219 | 121.7331 | -61.5005 | 59.9716 | -0.12398 | 0.014913 | 0.0094101 | 0.0023157 | 0.056249 | -0.0063403 | 0.065326 | -61.528 | 59.697 | -61.4273 | -61.5829 | 59.8114 | 0.3479 | 0.21057 | 0.3891 | 59.8618 | -61.6287 | 0.073242 | -0.27466 | -0.027466 | -0.082398 | -0.16022 | -0.12817 | -0.10986 | -0.10071 | 61.7111 | 61.8896 | 121.3119 | 121.1975 | -0.027466 | 121.3623 | 61.8484 | -0.12817 | 121.1975 | -0.027466 | 61.8484 | 121.3119 | 121.3623 | -121.3989 | -121.6003
613.6562 | 121.6873 | -61.5143 | 59.9579 | -0.22316 | 0.013418 | 0.010478 | 0.0059473 | 0.056035 | -0.0061267 | 0.067462 | -61.4868 | 59.7336 | -61.4227 | -61.5601 | 59.8434 | 0.43488 | 0.32501 | 0.49896 | 59.8755 | -61.6104 | 0.091553 | -0.2243 | 0.027466 | -0.045777 | -0.11444 | -0.096131 | -0.082398 | -0.064087 | 61.8393 | 62.0132 | 121.3577 | 121.2479 | 0.027466 | 121.3898 | 61.9492 | -0.096131 | 121.2479 | 0.027466 | 61.9492 | 121.3577 | 121.3898 | -121.3806 | -121.5683
615.3438 | 121.7468 | -61.5509 | 59.9167 | 0.17357 | 0.016836 | 0.0074875 | 0.0095789 | 0.057104 | -0.0074085 | 0.065112 | -61.6058 | 59.5963 | -61.5738 | -61.6837 | 59.6878 | 0.059509 | -0.40741 | -0.17853 | 59.7565 | -61.7203 | -0.022889 | -0.32044 | -0.054932 | -0.13275 | -0.22888 | -0.16937 | -0.16022 | -0.032043 | 61.1435 | 61.3724 | 121.2387 | 121.1472 | -0.054932 | 121.3074 | 61.6104 | -0.16937 | 121.1472 | -0.054932 | 61.6104 | 121.2387 | 121.3074 | -121.4905 | -121.637
617.0938 | 121.788 | -61.5829 | 59.8297 | 0.074387 | 0.014699 | 0.012615 | 0.010006 | 0.057531 | -0.0059131 | 0.066608 | -61.7432 | 59.61 | -61.6241 | -61.8301 | 59.5688 | 0 | -0.23346 | -0.3479 | 59.7885 | -61.7477 | -0.041199 | -0.21973 | -0.16022 | -0.24719 | -0.26093 | -0.1648 | -0.041199 | -0.11902 | 61.3495 | 61.235 | 121.1517 | 121.1929 | -0.16022 | 121.3715 | 61.5829 | -0.1648 | 121.1929 | -0.16022 | 61.5829 | 121.1517 | 121.3715 | -121.4539 | -121.5775
618.7812 | 121.6644 | -61.5326 | 59.9716 | -0.1545 | 0.014272 | 0.0096237 | 0.0027429 | 0.054754 | -0.0061267 | 0.063617 | -61.5097 | 59.6878 | -61.4456 | -61.5646 | 59.8297 | 0.44861 | 0.36621 | 0.48981 | 59.8526 | -61.5921 | 0.086975 | -0.28381 | 0.022888 | -0.032043 | -0.14191 | -0.059509 | -0.11902 | -0.064087 | 61.8988 | 62.0224 | 121.3623 | 121.2204 | 0.022888 | 121.3852 | 61.9812 | -0.059509 | 121.2204 | 0.022888 | 61.9812 | 121.3623 | 121.3852 | -121.4172 | -121.5637
620.5312 | 121.6507 | -61.6241 | 59.9121 | -0.10109 | 0.015981 | 0.0074875 | 0.011288 | 0.056463 | -0.0080493 | 0.064685 | -61.5829 | 59.729 | -61.5051 | -61.6608 | 59.7198 | 0.27008 | 0.13733 | 0.09613 | 59.8526 | -61.702 | 0.11902 | -0.1831 | 0.041199 | -0.036621 | -0.19226 | -0.077819 | -0.059509 | -0.07782 | 61.7615 | 61.7203 | 121.344 | 121.3531 | 0.041199 | 121.4767 | 61.8942 | -0.077819 | 121.3531 | 0.041199 | 61.8942 | 121.344 | 121.4767 | -121.4172 | -121.6141
622.2812 | 121.7789 | -61.4594 | 59.9487 | -0.0019073 | 0.011709 | 0.0053513 | 0.0018885 | 0.05689 | -0.0056995 | 0.062976 | -61.5875 | 59.6924 | -61.4502 | -61.6562 | 59.761 | 0.21057 | 0.09613 | 0.18768 | 59.8572 | -61.6425 | 0.009156 | -0.25635 | -0.12817 | -0.19684 | -0.18768 | -0.18311 | -0.091552 | -0.13733 | 61.5555 | 61.647 | 121.2204 | 121.1517 | -0.12817 | 121.3165 | 61.6699 | -0.18311 | 121.1517 | -0.12817 | 61.6699 | 121.2204 | 121.3165 | -121.3989 | -121.5912
623.9688 | 121.7239 | -61.6058 | 59.8618 | -0.0019073 | 0.015767 | 0.0091965 | 0.0089381 | 0.056249 | -0.010399 | 0.06554 | -61.6928 | 59.6237 | -61.6013 | -61.7661 | 59.6146 | 0.050354 | -0.15564 | -0.27008 | 59.8297 | -61.7249 | 0.004578 | -0.23804 | -0.086975 | -0.16022 | -0.24719 | -0.11902 | -0.032043 | -0.091553 | 61.4502 | 61.3358 | 121.2204 | 121.2296 | -0.086975 | 121.4355 | 61.6562 | -0.11902 | 121.2296 | -0.086975 | 61.6562 | 121.2204 | 121.4355 | -121.463 | -121.5866
625.7188 | 121.788 | -61.4502 | 59.967 | -0.017166 | 0.018117 | 0.011974 | 0.0048791 | 0.057317 | -0.0069811 | 0.064471 | -61.5738 | 59.7015 | -61.4227 | -61.6287 | 59.7931 | 0.23804 | 0.13275 | 0.23346 | 59.8801 | -61.6241 | 0.027466 | -0.2655 | -0.1236 | -0.17853 | -0.17395 | -0.17395 | -0.086975 | -0.15106 | 61.5829 | 61.6837 | 121.2433 | 121.1517 | -0.1236 | 121.3303 | 61.6882 | -0.17395 | 121.1517 | -0.1236 | 61.6882 | 121.2433 | 121.3303 | -121.3898 | -121.5912
627.4844 | 121.6507 | -61.6013 | 59.9121 | -0.078201 | 0.016836 | 0.0091965 | 0.010647 | 0.058385 | -0.0074085 | 0.06319 | -61.5784 | 59.6924 | -61.5097 | -61.6379 | 59.7336 | 0.27008 | 0.068665 | 0.041199 | 59.8755 | -61.6516 | 0.091552 | -0.21973 | 0.022888 | -0.036621 | -0.17853 | -0.050354 | -0.036621 | -0.068664 | 61.6699 | 61.6425 | 121.3348 | 121.2936 | 0.022888 | 121.4767 | 61.8713 | -0.050354 | 121.2936 | 0.022888 | 61.8713 | 121.3348 | 121.4767 | -121.4218 | -121.5637
629.1719 | 121.6736 | -61.496 | 60.0174 | -0.13924 | 0.013631 | 0.011119 | 0.0053065 | 0.054967 | -0.0067675 | 0.063617 | -61.4731 | 59.7565 | -61.3312 | -61.5143 | 59.8663 | 0.43488 | 0.33417 | 0.48065 | 59.9075 | -61.5692 | 0.1648 | -0.26093 | 0.022889 | -0.01831 | -0.15106 | -0.073242 | -0.10986 | -0.14191 | 61.8301 | 61.9766 | 121.3623 | 121.2524 | 0.022889 | 121.4035 | 61.9308 | -0.073242 | 121.2524 | 0.022889 | 61.9308 | 121.3623 | 121.4035 | -121.3486 | -121.5866
630.9219 | 121.7697 | -61.528 | 59.8984 | 0.12779 | 0.01534 | 0.012615 | 0.0076563 | 0.057958 | -0.0082629 | 0.067035 | -61.6653 | 59.6649 | -61.5555 | -61.7432 | 59.6603 | -0.022888 | -0.33875 | -0.33875 | 59.816 | -61.702 | -0.027466 | -0.23346 | -0.13733 | -0.21515 | -0.23804 | -0.17395 | -0.082397 | -0.10986 | 61.1893 | 61.1893 | 121.1884 | 121.1929 | -0.13733 | 121.344 | 61.5051 | -0.17395 | 121.1929 | -0.13733 | 61.5051 | 121.1884 | 121.344 | -121.4539 | -121.6003
632.6719 | 121.7834 | -61.4868 | 59.8938 | 0.12016 | 0.01534 | 0.0096237 | 0.0065881 | 0.058172 | -0.0069811 | 0.063617 | -61.647 | 59.6603 | -61.5326 | -61.7249 | 59.6603 | -0.036621 | -0.32959 | -0.36163 | 59.8572 | -61.6653 | -0.045777 | -0.23346 | -0.16022 | -0.23804 | -0.23346 | -0.17853 | -0.036621 | -0.11444 | 61.1572 | 61.1252 | 121.1472 | 121.1472 | -0.16022 | 121.344 | 61.4502 | -0.17853 | 121.1472 | -0.16022 | 61.4502 | 121.1472 | 121.344 | -121.4264 | -121.5591
634.3594 | 121.7056 | -61.5967 | 59.8984 | 0.0057222 | 0.014913 | 0.0094101 | 0.010433 | 0.059453 | -0.0067675 | 0.066821 | -61.6333 | 59.6924 | -61.5234 | -61.7203 | 59.6603 | 0.091553 | -0.12817 | -0.2243 | 59.8206 | -61.6882 | 0.073243 | -0.20599 | -0.036621 | -0.1236 | -0.23804 | -0.091552 | -0.077819 | -0.10986 | 61.4685 | 61.3724 | 121.257 | 121.2891 | -0.036621 | 121.4172 | 61.6882 | -0.091552 | 121.2891 | -0.036621 | 61.6882 | 121.257 | 121.4172 | -121.4218 | -121.5866
636.1094 | 121.7743 | -61.4319 | 59.9808 | 0.0057222 | 0.013418 | 0.0079147 | 0.0029565 | 0.056035 | -0.0050585 | 0.064899 | -61.5601 | 59.729 | -61.4182 | -61.6013 | 59.8114 | 0.2243 | 0.1236 | 0.21973 | 59.8846 | -61.5692 | 0.013733 | -0.25177 | -0.12817 | -0.16937 | -0.16937 | -0.13733 | -0.09613 | -0.14191 | 61.5555 | 61.6516 | 121.2433 | 121.1609 | -0.12817 | 121.3165 | 61.6562 | -0.13733 | 121.1609 | -0.12817 | 61.6562 | 121.2433 | 121.3165 | -121.3989 | -121.55
637.8594 | 121.7194 | -61.5784 | 59.8892 | 0.043869 | 0.017263 | 0.0087693 | 0.011715 | 0.055395 | -0.0076221 | 0.066608 | -61.6516 | 59.6649 | -61.5189 | -61.734 | 59.6512 | 0.045776 | -0.14191 | -0.27008 | 59.8526 | -61.6791 | 0.059509 | -0.2243 | -0.073242 | -0.15564 | -0.23804 | -0.10071 | -0.036621 | -0.13275 | 61.4365 | 61.3083 | 121.2296 | 121.2433 | -0.073242 | 121.431 | 61.6241 | -0.10071 | 121.2433 | -0.073242 | 61.6241 | 121.2296 | 121.431 | -121.4081 | -121.5683
639.5469 | 121.6599 | -61.4594 | 60.054 | -0.14687 | 0.016195 | 0.011333 | 0.0038111 | 0.052831 | -0.0059131 | 0.064258 | -61.3907 | 59.7748 | -61.3541 | -61.4685 | 59.9213 | 0.42572 | 0.28839 | 0.50354 | 59.935 | -61.528 | 0.10529 | -0.27924 | 0.068665 | -0.009155 | -0.13275 | -0.068664 | -0.11902 | -0.036621 | 61.7477 | 61.9629 | 121.3806 | 121.2341 | 0.068665 | 121.3943 | 61.8851 | -0.068664 | 121.2341 | 0.068665 | 61.8851 | 121.3806 | 121.3943 | -121.4081 | -121.582
641.3125 | 121.6644 | -61.441 | 60.0677 | -0.13924 | 0.01534 | 0.011974 | 0.0023157 | 0.052404 | -0.0063403 | 0.06319 | -61.4273 | 59.7794 | -61.3266 | -61.4868 | 59.9304 | 0.43488 | 0.29297 | 0.49896 | 59.9487 | -61.5326 | 0.11444 | -0.28839 | 0.013733 | -0.045776 | -0.13733 | -0.091553 | -0.11902 | -0.10071 | 61.734 | 61.94 | 121.3715 | 121.2204 | 0.013733 | 121.3898 | 61.8759 | -0.091553 | 121.2204 | 0.013733 | 61.8759 | 121.3715 | 121.3898 | -121.3943 | -121.6003
643.0625 | 121.669 | -61.5738 | 59.9396 | -0.047684 | 0.016408 | 0.0081283 | 0.011715 | 0.053899 | -0.010186 | 0.065112 | -61.5646 | 59.7244 | -61.4731 | -61.6196 | 59.7519 | 0.20142 | -0.050354 | -0.07782 | 59.8984 | -61.6562 | 0.10071 | -0.21515 | 0.009156 | -0.045776 | -0.18768 | -0.082397 | -0.041199 | -0.091553 | 61.5234 | 61.496 | 121.3257 | 121.2982 | 0.009156 | 121.4722 | 61.7752 | -0.082397 | 121.2982 | 0.009156 | 61.7752 | 121.3257 | 121.4722 | -121.4127 | -121.5958
644.7344 | 121.788 | -61.3861 | 60.0174 | 0.020981 | 0.013845 | 0.0068467 | 0.0046655 | 0.056249 | -0.0059131 | 0.066821 | -61.5372 | 59.7565 | -61.3678 | -61.5967 | 59.816 | 0.20599 | 0.086975 | 0.16479 | 59.9258 | -61.5784 | 0.01831 | -0.26093 | -0.15106 | -0.21057 | -0.20142 | -0.19226 | -0.091553 | -0.16937 | 61.4731 | 61.5509 | 121.2021 | 121.1426 | -0.15106 | 121.3119 | 61.5921 | -0.19226 | 121.1426 | -0.15106 | 61.5921 | 121.2021 | 121.3119 | -121.3852 | -121.5958
646.5 | 121.7514 | -61.4594 | 59.9396 | 0.13542 | 0.015127 | 0.0081283 | 0.0070155 | 0.055822 | -0.0052721 | 0.065326 | -61.5738 | 59.6649 | -61.4822 | -61.615 | 59.7656 | 0.041199 | -0.40741 | -0.21515 | 59.8206 | -61.5875 | -0.022888 | -0.27466 | -0.11444 | -0.15564 | -0.17395 | -0.12817 | -0.11902 | -0.091553 | 61.0519 | 61.2442 | 121.225 | 121.1243 | -0.11444 | 121.2799 | 61.5005 | -0.12817 | 121.1243 | -0.11444 | 61.5005 | 121.225 | 121.2799 | -121.4218 | -121.5271
648.1875 | 121.669 | -61.4273 | 60.1089 | -0.16975 | 0.01534 | 0.0079147 | 0.0046655 | 0.054326 | -0.0059131 | 0.064471 | -61.4044 | 59.8022 | -61.3129 | -61.441 | 59.9533 | 0.44861 | 0.32959 | 0.50812 | 59.9396 | -61.5051 | 0.11444 | -0.3067 | 0.022888 | -0.013733 | -0.15564 | -0.07782 | -0.16937 | -0.091553 | 61.7569 | 61.9354 | 121.3806 | 121.2296 | 0.022888 | 121.3669 | 61.8759 | -0.07782 | 121.2296 | 0.022888 | 61.8759 | 121.3806 | 121.3669 | -121.4218 | -121.6141
649.9375 | 121.6324 | -61.5417 | 59.9762 | -0.12398 | 0.015767 | 0.011546 | 0.012997 | 0.057104 | -0.0091173 | 0.064044 | -61.5326 | 59.7473 | -61.4594 | -61.5921 | 59.7885 | 0.27924 | 0.10986 | 0.091553 | 59.935 | -61.5509 | 0.082397 | -0.22888 | 0.009155 | -0.050354 | -0.18768 | -0.009155 | -0.041198 | -0.073242 | 61.6516 | 61.6333 | 121.3303 | 121.2891 | 0.009155 | 121.4767 | 61.821 | -0.009155 | 121.2891 | 0.009155 | 61.821 | 121.3303 | 121.4767 | -121.4355 | -121.5271
652.1094 | 121.788 | -61.4639 | 59.9304 | 0.1049 | 0.013418 | 0.0081283 | 0.0065881 | 0.057317 | -0.0078357 | 0.064685 | -61.615 | 59.6878 | -61.4914 | -61.6974 | 59.6832 | -0.032043 | -0.27466 | -0.35706 | 59.8984 | -61.6104 | -0.027466 | -0.24262 | -0.15106 | -0.23346 | -0.24719 | -0.14648 | -0.032044 | -0.1236 | 61.1893 | 61.1069 | 121.1472 | 121.1517 | -0.15106 | 121.3623 | 61.4319 | -0.14648 | 121.1517 | -0.15106 | 61.4319 | 121.1472 | 121.3623 | -121.4218 | -121.5408
654 | 121.6644 | -61.4456 | 60.054 | -0.16975 | 0.014699 | 0.0079147 | 0.0027429 | 0.056676 | -0.0061267 | 0.065112 | -61.409 | 59.8022 | -61.3083 | -61.4639 | 59.9304 | 0.44861 | 0.32959 | 0.49896 | 59.9899 | -61.5143 | 0.13733 | -0.25177 | 0.036621 | -0.01831 | -0.1236 | -0.068664 | -0.064087 | -0.10071 | 61.7752 | 61.9446 | 121.376 | 121.2479 | 0.036621 | 121.4355 | 61.8942 | -0.068664 | 121.2479 | 0.036621 | 61.8942 | 121.376 | 121.4355 | -121.3623 | -121.5683
655.7031 | 121.7972 | -61.377 | 60.0311 | 0.097275 | 0.014272 | 0.0096237 | 0.0044519 | 0.056463 | -0.0056995 | 0.064471 | -61.4777 | 59.761 | -61.3449 | -61.5646 | 59.8389 | 0.1236 | -0.10071 | 0.004578 | 59.9213 | -61.528 | 0.032043 | -0.27008 | -0.10071 | -0.18768 | -0.19226 | -0.15106 | -0.10986 | -0.13275 | 61.2762 | 61.3815 | 121.2158 | 121.138 | -0.10071 | 121.2982 | 61.5005 | -0.15106 | 121.138 | -0.10071 | 61.5005 | 121.2158 | 121.2982 | -121.376 | -121.5591
657.4062 | 121.7606 | -61.4639 | 59.9167 | 0.066757 | 0.016408 | 0.015819 | 0.010861 | 0.05689 | -0.0080493 | 0.064258 | -61.6058 | 59.729 | -61.5005 | -61.7065 | 59.6603 | 0.004578 | -0.20142 | -0.32501 | 59.935 | -61.6058 | -0.036621 | -0.18768 | -0.14191 | -0.24262 | -0.25635 | -0.14191 | 0.018311 | -0.10529 | 61.2625 | 61.1389 | 121.1243 | 121.1929 | -0.14191 | 121.3989 | 61.4685 | -0.14191 | 121.1929 | -0.14191 | 61.4685 | 121.1243 | 121.3989 | -121.4172 | -121.5225
659.2344 | 121.8201 | -61.3541 | 60.1135 | 0.02861 | 0.014058 | 0.0068467 | 0.0029565 | 0.054754 | -0.0086901 | 0.065326 | -61.4685 | 59.8022 | -61.3541 | -61.5463 | 59.8663 | 0.17395 | 0.018311 | 0.11444 | 59.9487 | -61.5051 | 0 | -0.31128 | -0.11444 | -0.19226 | -0.24719 | -0.15106 | -0.1648 | -0.11444 | 61.3724 | 61.4685 | 121.2204 | 121.1563 | -0.11444 | 121.3028 | 61.528 | -0.15106 | 121.1563 | -0.11444 | 61.528 | 121.2204 | 121.3028 | -121.4676 | -121.6187
660.9688 | 121.6782 | -61.3724 | 60.0906 | -0.10872 | 0.016408 | 0.0089829 | 0.0053065 | 0.056676 | -0.0054859 | 0.064471 | -61.3815 | 59.8114 | -61.3174 | -61.4273 | 59.9808 | 0.42572 | 0.24261 | 0.44861 | 59.967 | -61.4777 | 0.054931 | -0.27924 | -0.009156 | -0.054932 | -0.10986 | -0.10529 | -0.1236 | -0.064087 | 61.615 | 61.821 | 121.3531 | 121.1838 | -0.009156 | 121.3394 | 61.7981 | -0.10529 | 121.1838 | -0.009156 | 61.7981 | 121.3531 | 121.3394 | -121.4081 | -121.5683
662.6562 | 121.788 | -61.4319 | 59.967 | 0.13542 | 0.017263 | 0.010051 | 0.011074 | 0.057317 | -0.0091173 | 0.067035 | -61.5646 | 59.7427 | -61.4639 | -61.6608 | 59.7107 | -0.027466 | -0.2655 | -0.35248 | 59.9213 | -61.6013 | -0.032043 | -0.2243 | -0.13275 | -0.22888 | -0.25635 | -0.16937 | -0.045776 | -0.10071 | 61.1664 | 61.0794 | 121.1426 | 121.1746 | -0.13275 | 121.3531 | 61.4044 | -0.16937 | 121.1746 | -0.13275 | 61.4044 | 121.1426 | 121.3531 | -121.431 | -121.5683
664.3594 | 121.7056 | -61.4502 | 60.0174 | -0.20027 | 0.017904 | 0.010478 | 0.0078699 | 0.057104 | -0.0061267 | 0.064899 | -61.4639 | 59.9075 | -61.3266 | -61.5326 | 59.848 | 0.33417 | 0.38452 | 0.23346 | 60.0357 | -61.5143 | 0.1236 | -0.10986 | -0.013733 | -0.082398 | -0.16937 | -0.064087 | 0.018311 | -0.13733 | 61.8347 | 61.6837 | 121.2982 | 121.3577 | -0.013733 | 121.4859 | 61.7844 | -0.064087 | 121.3577 | -0.013733 | 61.7844 | 121.2982 | 121.4859 | -121.344 | -121.5317
666.1094 | 121.7377 | -61.3815 | 60.0494 | 0.16594 | 0.015981 | 0.0087693 | 0.0061609 | 0.055608 | -0.0071947 | 0.064899 | -61.4731 | 59.7336 | -61.4227 | -61.5601 | 59.8526 | 0.068665 | -0.40741 | -0.17853 | 59.8663 | -61.5692 | -0.041198 | -0.31586 | -0.091552 | -0.17853 | -0.19684 | -0.18768 | -0.18311 | -0.050354 | 60.9741 | 61.203 | 121.2341 | 121.1151 | -0.091552 | 121.2479 | 61.4502 | -0.18768 | 121.1151 | -0.091552 | 61.4502 | 121.2341 | 121.2479 | -121.4722 | -121.6187
667.8125 | 121.7834 | -61.3358 | 60.0952 | -0.0019073 | 0.014699 | 0.013042 | 0.0021021 | 0.056676 | -0.0048449 | 0.064471 | -61.4502 | 59.8206 | -61.322 | -61.5097 | 59.903 | 0.24719 | 0.11902 | 0.22888 | 59.9762 | -61.4868 | 0.013733 | -0.27466 | -0.11444 | -0.17395 | -0.19226 | -0.15106 | -0.11902 | -0.12817 | 61.4548 | 61.5646 | 121.2387 | 121.1563 | -0.11444 | 121.3119 | 61.5829 | -0.15106 | 121.1563 | -0.11444 | 61.5829 | 121.2387 | 121.3119 | -121.4172 | -121.582
669.5156 | 121.7148 | -61.3861 | 60.0677 | -0.20027 | 0.01534 | 0.011119 | 0.0050929 | 0.053472 | -0.0080493 | 0.066608 | -61.4594 | 59.9213 | -61.3312 | -61.5005 | 59.8984 | 0.36621 | 0.46234 | 0.32959 | 60.0769 | -61.4594 | 0.054931 | -0.14648 | -0.073243 | -0.11444 | -0.16937 | -0.073243 | 0.009155 | -0.12817 | 61.8484 | 61.7157 | 121.2845 | 121.3074 | -0.073243 | 121.463 | 61.7523 | -0.073243 | 121.3074 | -0.073243 | 61.7523 | 121.2845 | 121.463 | -121.3989 | -121.5271
671.2031 | 121.6553 | -61.3861 | 60.141 | -0.14687 | 0.01534 | 0.0042831 | 0.0038111 | 0.055181 | -0.0061267 | 0.063403 | -61.3358 | 59.8938 | -61.2488 | -61.3953 | 59.9991 | 0.44861 | 0.35248 | 0.48981 | 60.0128 | -61.4227 | 0.13733 | -0.24719 | 0.050354 | -0.009156 | -0.14191 | -0.036621 | -0.12817 | -0.086975 | 61.7386 | 61.8759 | 121.3852 | 121.2799 | 0.050354 | 121.3989 | 61.8347 | -0.036621 | 121.2799 | 0.050354 | 61.8347 | 121.3852 | 121.3989 | -121.3898 | -121.5637
672.9375 | 121.7148 | -61.3678 | 60.0998 | -0.23079 | 0.014486 | 0.011974 | 0.0080835 | 0.05689 | -0.0097583 | 0.064899 | -61.3998 | 59.9579 | -61.2671 | -61.4639 | 59.9396 | 0.3479 | 0.44403 | 0.28839 | 60.1547 | -61.3998 | 0.10071 | -0.14191 | -0.032043 | -0.09613 | -0.16022 | -0.032043 | 0.054932 | -0.13275 | 61.8118 | 61.6562 | 121.3074 | 121.3257 | -0.032043 | 121.5225 | 61.7157 | -0.032043 | 121.3257 | -0.032043 | 61.7157 | 121.3074 | 121.5225 | -121.3669 | -121.4996
674.625 | 121.7697 | -61.3632 | 60.0494 | 0.089645 | 0.014913 | 0.010906 | 0.0091517 | 0.058172 | -0.0080493 | 0.064899 | -61.4914 | 59.8297 | -61.3815 | -61.5784 | 59.8022 | -0.032043 | -0.29297 | -0.3479 | 60.0174 | -61.5372 | -0.018311 | -0.21973 | -0.12817 | -0.21515 | -0.24719 | -0.17395 | -0.032043 | -0.10986 | 61.0703 | 61.0153 | 121.1655 | 121.1929 | -0.12817 | 121.3806 | 61.3312 | -0.17395 | 121.1929 | -0.12817 | 61.3312 | 121.1655 | 121.3806 | -121.431 | -121.5866
676.3438 | 121.7789 | -61.377 | 60.0266 | 0.082016 | 0.015981 | 0.010692 | 0.0095789 | 0.057104 | -0.0080493 | 0.065326 | -61.5326 | 59.8251 | -61.4044 | -61.615 | 59.7702 | 0.004578 | -0.21973 | -0.3479 | 59.9991 | -61.5509 | -0.027466 | -0.20142 | -0.15564 | -0.23804 | -0.25635 | -0.17395 | -0.027466 | -0.12817 | 61.1572 | 61.0291 | 121.1472 | 121.2021 | -0.15564 | 121.376 | 61.3815 | -0.17395 | 121.2021 | -0.15564 | 61.3815 | 121.1472 | 121.376 | -121.431 | -121.5775
678.0312 | 121.7972 | -61.2442 | 60.1547 | 0.059128 | 0.012777 | 0.0077011 | 0.0027429 | 0.057531 | -0.0063403 | 0.064685 | -61.3815 | 59.8984 | -61.2305 | -61.4456 | 59.9625 | 0.14648 | -0.036621 | 0.059509 | 60.0403 | -61.409 | 0.013733 | -0.25635 | -0.13733 | -0.20142 | -0.19226 | -0.16479 | -0.11444 | -0.15106 | 61.2076 | 61.3037 | 121.2067 | 121.1426 | -0.13733 | 121.2845 | 61.3907 | -0.16479 | 121.1426 | -0.13733 | 61.3907 | 121.2067 | 121.2845 | -121.3852 | -121.5637
679.7188 | 121.6507 | -61.3998 | 60.0723 | -0.10872 | 0.014486 | 0.01176 | 0.0095789 | 0.057744 | -0.0074085 | 0.066394 | -61.4044 | 59.8755 | -61.3312 | -61.4502 | 59.9213 | 0.29297 | 0.10986 | 0.10071 | 60.0403 | -61.4594 | 0.068664 | -0.19684 | -0.004578 | -0.050354 | -0.15106 | -0.05951 | -0.032044 | -0.073242 | 61.5097 | 61.5005 | 121.3211 | 121.2753 | -0.004578 | 121.4401 | 61.6928 | -0.05951 | 121.2753 | -0.004578 | 61.6928 | 121.3211 | 121.4401 | -121.4035 | -121.5317
681.4531 | 121.6873 | -61.2854 | 60.2097 | -0.10872 | 0.01534 | 0.011333 | 0.00039306 | 0.056463 | -0.0054859 | 0.064685 | -61.2671 | 59.935 | -61.1801 | -61.322 | 60.0815 | 0.39368 | 0.2243 | 0.44403 | 60.0998 | -61.3586 | 0.10529 | -0.27466 | 0.01831 | -0.036621 | -0.12817 | -0.073243 | -0.10986 | -0.086975 | 61.5097 | 61.7294 | 121.3669 | 121.2204 | 0.01831 | 121.3852 | 61.6791 | -0.073243 | 121.2204 | 0.01831 | 61.6791 | 121.3669 | 121.3852 | -121.3898 | -121.5683
683.2031 | 121.701 | -61.3266 | 60.1776 | -0.22316 | 0.014058 | 0.0051377 | 0.0063745 | 0.055395 | -0.0080493 | 0.064044 | -61.322 | 59.9625 | -61.2122 | -61.4044 | 59.9945 | 0.38452 | 0.46692 | 0.39368 | 60.1593 | -61.3632 | 0.11444 | -0.21515 | 0.004578 | -0.07782 | -0.18311 | -0.036621 | -0.01831 | -0.10986 | 61.7935 | 61.7203 | 121.3211 | 121.2891 | 0.004578 | 121.4859 | 61.7111 | -0.036621 | 121.2891 | 0.004578 | 61.7111 | 121.3211 | 121.4859 | -121.3898 | -121.5408
684.9688 | 121.7834 | -61.2213 | 60.1959 | -0.0019073 | 0.01534 | 0.0057785 | 0.0040247 | 0.054967 | -0.0067675 | 0.064471 | -61.3541 | 59.9167 | -61.2213 | -61.4136 | 59.9762 | 0.21973 | 0.091553 | 0.16937 | 60.0769 | -61.4136 | 0 | -0.27924 | -0.13275 | -0.19226 | -0.21973 | -0.19226 | -0.11902 | -0.13275 | 61.3129 | 61.3907 | 121.1975 | 121.138 | -0.13275 | 121.2982 | 61.441 | -0.19226 | 121.138 | -0.13275 | 61.441 | 121.1975 | 121.2982 | -121.4172 | -121.6095
686.7188 | 121.6736 | -61.4319 | 60.0677 | -0.055313 | 0.016408 | 0.011546 | 0.0095789 | 0.057317 | -0.0071947 | 0.065326 | -61.3953 | 59.8984 | -61.3358 | -61.4822 | 59.8984 | 0.20599 | -0.050354 | -0.059509 | 60.0037 | -61.4914 | 0.096131 | -0.16937 | 0.036621 | -0.050354 | -0.16937 | -0.059509 | -0.064087 | -0.05951 | 61.3815 | 61.3724 | 121.3303 | 121.3303 | 0.036621 | 121.4355 | 61.6379 | -0.059509 | 121.3303 | 0.036621 | 61.6379 | 121.3303 | 121.4355 | -121.4035 | -121.5591
688.4688 | 121.6736 | -61.4136 | 60.0769 | -0.10872 | 0.012563 | 0.015178 | 0.0093653 | 0.055608 | -0.0074085 | 0.064685 | -61.3815 | 59.8846 | -61.2854 | -61.4319 | 59.9487 | 0.30212 | 0.15106 | 0.1236 | 60.0632 | -61.4365 | 0.12817 | -0.19226 | 0.032043 | -0.018311 | -0.12817 | -0.022888 | -0.013733 | -0.096131 | 61.5646 | 61.5372 | 121.3623 | 121.2982 | 0.032043 | 121.4767 | 61.7157 | -0.022888 | 121.2982 | 0.032043 | 61.7157 | 121.3623 | 121.4767 | -121.3623 | -121.5134
690.2344 | 121.7972 | -61.171 | 60.2554 | 0.11253 | 0.014913 | 0.010478 | 0.0080835 | 0.055395 | -0.0063403 | 0.067035 | -61.3403 | 60.0494 | -61.1847 | -61.377 | 60.0037 | 0.004578 | -0.24719 | -0.36163 | 60.1868 | -61.3495 | -0.013733 | -0.20599 | -0.16937 | -0.20599 | -0.25177 | -0.17853 | -0.068664 | -0.15564 | 60.9238 | 60.8093 | 121.1746 | 121.2204 | -0.16937 | 121.3577 | 61.1755 | -0.17853 | 121.2204 | -0.16937 | 61.1755 | 121.1746 | 121.3577 | -121.4401 | -121.6049
691.9844 | 121.6782 | -61.0336 | 60.4843 | -0.16212 | 0.013204 | 0.0068467 | 0.0025293 | 0.054326 | -0.0067675 | 0.063617 | -61.0382 | 60.1913 | -60.9283 | -61.0794 | 60.3149 | 0.46692 | 0.39368 | 0.50354 | 60.3561 | -61.0931 | 0.10529 | -0.29297 | -0.004578 | -0.045777 | -0.16937 | -0.05951 | -0.12817 | -0.10986 | 61.4273 | 61.5372 | 121.3486 | 121.225 | -0.004578 | 121.3898 | 61.5005 | -0.05951 | 121.225 | -0.004578 | 61.5005 | 121.3486 | 121.3898 | -121.4127 | -121.5775
693.7344 | 121.6644 | -61.1023 | 60.3882 | -0.1545 | 0.014058 | 0.0085555 | 0.0078699 | 0.056463 | -0.0080493 | 0.064258 | -61.084 | 60.1913 | -60.9924 | -61.1435 | 60.2371 | 0.3067 | 0.16479 | 0.13275 | 60.4111 | -61.1298 | 0.10986 | -0.19684 | 0.018311 | -0.041199 | -0.15106 | -0.027466 | 0.022888 | -0.091552 | 61.2671 | 61.235 | 121.3394 | 121.2936 | 0.018311 | 121.5134 | 61.409 | -0.027466 | 121.2936 | 0.018311 | 61.409 | 121.3394 | 121.5134 | -121.3806 | -121.5179
695.4219 | 121.788 | -60.965 | 60.4752 | 0.15068 | 0.015127 | 0.011974 | 0.0033839 | 0.056463 | -0.0054859 | 0.066394 | -61.0794 | 60.1456 | -60.965 | -61.1435 | 60.2737 | 0.1236 | -0.15564 | -0.018311 | 60.3516 | -61.1435 | 0 | -0.32959 | -0.11444 | -0.17853 | -0.20142 | -0.17853 | -0.1236 | -0.11444 | 60.8093 | 60.9467 | 121.2387 | 121.1105 | -0.11444 | 121.3165 | 61.0886 | -0.17853 | 121.1105 | -0.11444 | 61.0886 | 121.2387 | 121.3165 | -121.4401 | -121.6187
697.1719 | 121.7514 | -61.0794 | 60.3882 | 0.1049 | 0.017476 | 0.0077011 | 0.0095789 | 0.056249 | -0.0074085 | 0.068103 | -61.1984 | 60.1181 | -61.0886 | -61.2946 | 60.1044 | 0.041199 | -0.15106 | -0.29755 | 60.3149 | -61.235 | -0.009155 | -0.27008 | -0.11902 | -0.21515 | -0.28381 | -0.15564 | -0.073243 | -0.10986 | 60.9283 | 60.7819 | 121.1838 | 121.1975 | -0.11902 | 121.3943 | 61.1206 | -0.15564 | 121.1975 | -0.11902 | 61.1206 | 121.1838 | 121.3943 | -121.4767 | -121.6232
698.9219 | 121.6553 | -61.0519 | 60.4706 | -0.1545 | 0.015127 | 0.01176 | 0.0031701 | 0.055822 | -0.0067675 | 0.064258 | -61.0153 | 60.2051 | -60.9375 | -61.0748 | 60.3287 | 0.47607 | 0.31128 | 0.51727 | 60.3424 | -61.1206 | 0.11444 | -0.2655 | 0.036621 | -0.022888 | -0.14191 | -0.068664 | -0.12817 | -0.07782 | 61.3632 | 61.5692 | 121.3806 | 121.257 | 0.036621 | 121.3943 | 61.528 | -0.068664 | 121.257 | 0.036621 | 61.528 | 121.3806 | 121.3943 | -121.4081 | -121.5912
700.6094 | 121.7377 | -61.116 | 60.3012 | 0.16594 | 0.017904 | 0.0094101 | 0.0072291 | 0.057744 | -0.0061267 | 0.064899 | -61.1938 | 60.0128 | -61.1252 | -61.2717 | 60.1089 | 0.082397 | -0.39825 | -0.16479 | 60.1364 | -61.2991 | -0.009155 | -0.28839 | -0.07782 | -0.15564 | -0.19226 | -0.1831 | -0.16479 | -0.068665 | 60.7178 | 60.9512 | 121.225 | 121.1288 | -0.07782 | 121.2524 | 61.1984 | -0.1831 | 121.1288 | -0.07782 | 61.1984 | 121.225 | 121.2524 | -121.4264 | -121.6003
702.3906 | 121.788 | -61.1618 | 60.2646 | 0.11253 | 0.014058 | 0.0062057 | 0.011715 | 0.055181 | -0.0065539 | 0.064471 | -61.3174 | 60.054 | -61.171 | -61.3861 | 59.9991 | -0.009155 | -0.23804 | -0.36621 | 60.1959 | -61.3358 | -0.009155 | -0.21057 | -0.15564 | -0.2243 | -0.2655 | -0.17395 | -0.068664 | -0.14648 | 60.9238 | 60.7956 | 121.1609 | 121.2158 | -0.15564 | 121.3577 | 61.1526 | -0.17395 | 121.2158 | -0.15564 | 61.1526 | 121.1609 | 121.3577 | -121.4355 | -121.6003
704.0781 | 121.6507 | -61.0886 | 60.3836 | -0.0095368 | 0.016836 | 0.010906 | 0.0087243 | 0.059453 | -0.0069811 | 0.064258 | -61.1206 | 60.1822 | -61.0474 | -61.2122 | 60.1685 | 0.17395 | -0.054932 | -0.10529 | 60.3333 | -61.2076 | 0.041199 | -0.20142 | -0.032043 | -0.1236 | -0.21515 | -0.11902 | -0.050354 | -0.073242 | 61.0336 | 60.9833 | 121.257 | 121.2708 | -0.032043 | 121.4218 | 61.2625 | -0.11902 | 121.2708 | -0.032043 | 61.2625 | 121.257 | 121.4218 | -121.431 | -121.5912
705.8125 | 121.6736 | -61.0657 | 60.4156 | -0.0019073 | 0.014058 | 0.014324 | 0.0087243 | 0.058385 | -0.010186 | 0.065753 | -61.1023 | 60.2234 | -61.0199 | -61.1801 | 60.1547 | 0.12817 | -0.10986 | -0.17853 | 60.3378 | -61.1755 | 0.045777 | -0.19226 | -0.036621 | -0.11444 | -0.26093 | -0.10986 | -0.077819 | -0.082398 | 60.9558 | 60.8871 | 121.2204 | 121.2891 | -0.036621 | 121.4035 | 61.1938 | -0.10986 | 121.2891 | -0.036621 | 61.1938 | 121.2204 | 121.4035 | -121.4355 | -121.5912
707.5625 | 121.6507 | -60.8826 | 60.6308 | -0.16975 | 0.014272 | 0.0089829 | 0.00039306 | 0.056035 | -0.0071947 | 0.065753 | -60.8185 | 60.3836 | -60.7407 | -60.8963 | 60.5209 | 0.45776 | 0.32959 | 0.51727 | 60.5392 | -60.9329 | 0.14191 | -0.24719 | 0.064087 | -0.013733 | -0.10986 | -0.050354 | -0.091552 | -0.077819 | 61.2122 | 61.3998 | 121.4035 | 121.2662 | 0.064087 | 121.4218 | 61.3403 | -0.050354 | 121.2662 | 0.064087 | 61.3403 | 121.4035 | 121.4218 | -121.3715 | -121.5637
709.25 | 121.7651 | -60.7452 | 60.6308 | 0.1812 | 0.015127 | 0.014324 | 0.0076563 | 0.057317 | -0.0095447 | 0.066608 | -60.9055 | 60.2875 | -60.8597 | -60.9787 | 60.4202 | 0.07782 | -0.35706 | -0.13733 | 60.4706 | -61.0062 | -0.11444 | -0.34332 | -0.16022 | -0.23346 | -0.21057 | -0.26093 | -0.16022 | -0.045777 | 60.3882 | 60.6079 | 121.1655 | 121.0327 | -0.16022 | 121.2158 | 60.8231 | -0.26093 | 121.0327 | -0.16022 | 60.8231 | 121.1655 | 121.2158 | -121.4905 | -121.637
711 | 121.6827 | -6.7383 | 114.917 | 0.12016 | 0.011068 | 0.0064193 | 0.0029565 | 0.055608 | -0.0089037 | 0.064044 | -6.6559 | 114.5737 | -6.6284 | -6.633 | 114.3906 | 1.8585 | -0.041199 | 0.14648 | 114.8438 | -6.7245 | 0.10986 | -0.34332 | 0.082397 | 0.10528 | -0.52643 | 0.013733 | -0.073242 | -0.027466 | 6.6971 | 6.8848 | 121.1288 | 121.3119 | 0.082397 | 121.582 | 8.5968 | 0.013733 | 121.3119 | 0.082397 | 8.5968 | 121.1288 | 121.582 | -121.5454 | -121.6415
712.7656 | 121.6141 | -5.603 | 116.1209 | -0.13924 | 0.01534 | 0.0038559 | 0.0025293 | 0.054754 | -0.0065539 | 0.06319 | -5.484 | 115.7043 | -5.4794 | -5.4153 | 115.5762 | 1.6937 | 0.3891 | 0.60883 | 115.9561 | -5.5847 | 0.1236 | -0.41657 | 0.11902 | 0.18768 | -0.54474 | 0.01831 | -0.1648 | -0.004578 | 5.9921 | 6.2119 | 121.1792 | 121.3074 | 0.11902 | 121.5591 | 7.2968 | 0.01831 | 121.3074 | 0.11902 | 7.2968 | 121.1792 | 121.5591 | -121.6003 | -121.7056
714.4688 | 121.6553 | -5.0079 | 116.6702 | -0.12398 | 0.014058 | 0.0042831 | 0.0059473 | 0.053899 | -0.0071947 | 0.065326 | -4.9622 | 116.3177 | -4.9393 | -4.9393 | 116.0614 | 1.5793 | 0.6134 | 0.50354 | 116.5924 | -5.0079 | 0.068665 | -0.35248 | 0.045777 | 0.068665 | -0.60883 | 0 | -0.07782 | -0.022888 | 5.6213 | 5.5115 | 121.0693 | 121.3257 | 0.045777 | 121.6003 | 6.5872 | 0 | 121.3257 | 0.045777 | 6.5872 | 121.0693 | 121.6003 | -121.6095 | -121.6782
716.2344 | 121.7422 | -4.9438 | 116.6565 | 0.02861 | 0.015554 | 0.0091965 | 0.0050929 | 0.056035 | -0.0061267 | 0.06319 | -4.9026 | 116.3269 | -4.8569 | -4.8798 | 116.1026 | 1.3367 | 0.16937 | 0.2243 | 116.6016 | -4.9576 | 0.086975 | -0.32959 | 0.041199 | 0.064087 | -0.55389 | -0.013733 | -0.054932 | -0.045776 | 5.1132 | 5.1682 | 121.0464 | 121.2708 | 0.041199 | 121.5454 | 6.2805 | -0.013733 | 121.2708 | 0.041199 | 6.2805 | 121.0464 | 121.5454 | -121.5134 | -121.6141
717.9844 | 121.7422 | -5.2597 | 116.3406 | 0.13542 | 0.015981 | 0.010692 | 0.011074 | 0.056035 | -0.0099719 | 0.063403 | -5.3101 | 115.9882 | -5.246 | -5.2643 | 115.7135 | 1.1948 | -0.09613 | -0.24261 | 116.3361 | -5.3146 | 0.013733 | -0.35248 | -0.050354 | -0.004577 | -0.62714 | -0.054931 | -0.004577 | -0.064087 | 5.1636 | 5.0171 | 120.9732 | 121.2479 | -0.050354 | 121.5958 | 6.4545 | -0.054931 | 121.2479 | -0.050354 | 6.4545 | 120.9732 | 121.5958 | -121.5866 | -121.6553
719.6719 | 121.6324 | -4.2618 | 117.4438 | -0.16975 | 0.013845 | 0.0079147 | 0.0040247 | 0.054754 | -0.0061267 | 0.064044 | -4.1245 | 117.0364 | -4.1428 | -4.0833 | 116.9083 | 1.5701 | 0.45776 | 0.6134 | 117.3203 | -4.2252 | 0.11902 | -0.40741 | 0.13733 | 0.17853 | -0.53558 | 0.036621 | -0.1236 | 0.01831 | 4.7195 | 4.8752 | 121.17 | 121.2982 | 0.13733 | 121.582 | 5.8319 | 0.036621 | 121.2982 | 0.13733 | 5.8319 | 121.17 | 121.582 | -121.5866 | -121.669
721.4375 | 121.6644 | -4.3854 | 117.2562 | -0.22316 | 0.017904 | 0.0081283 | 0.0070155 | 0.057317 | -0.011254 | 0.061908 | -4.3762 | 116.9174 | -4.3533 | -4.3579 | 116.629 | 1.4969 | 0.60883 | 0.46234 | 117.1967 | -4.4449 | 0.032043 | -0.33875 | 0.009155 | 0.027466 | -0.62714 | -0.059509 | -0.05951 | -0.022888 | 4.9942 | 4.8477 | 121.0144 | 121.3028 | 0.009155 | 121.582 | 5.8823 | -0.059509 | 121.3028 | 0.009155 | 5.8823 | 121.0144 | 121.582 | -121.6095 | -121.701
723.1875 | 121.7422 | -4.0329 | 117.5491 | 0.12779 | 0.016195 | 0.0053513 | 0.0035975 | 0.057104 | -0.0076221 | 0.064044 | -3.9505 | 117.215 | -3.9734 | -3.9734 | 117.0227 | 1.2314 | -0.054932 | 0.064087 | 117.54 | -4.0558 | 0.059509 | -0.33417 | 0.082398 | 0.059509 | -0.52643 | -0.022888 | -0.009155 | 0.022889 | 3.978 | 4.097 | 121.0556 | 121.2479 | 0.082398 | 121.5729 | 5.2643 | -0.022888 | 121.2479 | 0.082398 | 5.2643 | 121.0556 | 121.5729 | -121.5225 | -121.6049
724.9375 | 121.6415 | -4.747 | 116.9128 | -0.14687 | 0.01769 | 0.0089829 | 0.0070155 | 0.055822 | -0.0069811 | 0.064044 | -4.6738 | 116.4825 | -4.6646 | -4.6417 | 116.3498 | 1.5152 | 0.47607 | 0.58594 | 116.7938 | -4.7745 | 0.082397 | -0.4303 | 0.073242 | 0.10529 | -0.56305 | -0.027466 | -0.11902 | -0.009155 | 5.2231 | 5.3329 | 121.0968 | 121.2296 | 0.073242 | 121.5408 | 6.2622 | -0.027466 | 121.2296 | 0.073242 | 6.2622 | 121.0968 | 121.5408 | -121.5775 | -121.6873
726.6875 | 121.7102 | -4.6326 | 116.9769 | -0.024795 | 0.014913 | 0.0085555 | 0.0063745 | 0.055822 | -0.0061267 | 0.064899 | -4.5593 | 116.6382 | -4.541 | -4.5044 | 116.4825 | 1.3458 | 0.23346 | 0.42572 | 116.9128 | -4.66 | 0.091552 | -0.33875 | 0.073242 | 0.12817 | -0.49438 | -0.027466 | -0.064087 | -0.01831 | 4.866 | 5.0583 | 121.1151 | 121.2708 | 0.073242 | 121.5454 | 5.9784 | -0.027466 | 121.2708 | 0.073242 | 5.9784 | 121.1151 | 121.5454 | -121.5179 | -121.637
728.375 | 121.6461 | -4.7287 | 116.9083 | -0.17738 | 0.016195 | 0.012828 | 0.0070155 | 0.056035 | -0.0052721 | 0.062976 | -4.4952 | 116.6565 | -4.5227 | -4.4403 | 116.5329 | 1.5106 | 0.44403 | 0.60425 | 116.9724 | -4.5914 | 0.20599 | -0.25177 | 0.23346 | 0.28839 | -0.37537 | 0.13733 | 0.064087 | 0.027466 | 5.1727 | 5.3329 | 121.2616 | 121.3852 | 0.23346 | 121.7011 | 6.2393 | 0.13733 | 121.3852 | 0.23346 | 6.2393 | 121.2616 | 121.7011 | -121.431 | -121.4996
730.125 | 121.6461 | -4.2068 | 117.4438 | -0.16212 | 0.014058 | 0.0091965 | 0.012142 | 0.056676 | -0.0097583 | 0.063831 | -4.1702 | 117.1143 | -4.1473 | -4.1199 | 116.8533 | 1.4603 | 0.35248 | 0.27466 | 117.4164 | -4.1977 | 0.059509 | -0.32959 | 0.036621 | 0.086975 | -0.59051 | 0.009155 | -0.027466 | -0.022888 | 4.5593 | 4.4815 | 121.0602 | 121.3211 | 0.036621 | 121.6232 | 5.6671 | 0.009155 | 121.3211 | 0.036621 | 5.6671 | 121.0602 | 121.6232 | -121.5912 | -121.6415
731.8125 | 121.7194 | -4.4586 | 117.1051 | 0.18883 | 0.017476 | 0.0081283 | 0.0076563 | 0.060949 | -0.0078357 | 0.064044 | -4.454 | 116.8259 | -4.4312 | -4.4266 | 116.5741 | 1.1719 | -0.25177 | -0.17395 | 117.0776 | -4.5136 | 0.027466 | -0.27924 | 0.004577 | 0.032043 | -0.53101 | -0.054932 | -0.027466 | -0.022889 | 4.2068 | 4.2847 | 121.0327 | 121.2845 | 0.004577 | 121.5363 | 5.6305 | -0.054932 | 121.2845 | 0.004577 | 5.6305 | 121.0327 | 121.5363 | -121.5363 | -121.6187
733.5625 | 121.6965 | -4.5181 | 117.1143 | -0.22316 | 0.015127 | 0.0081283 | 0.0080835 | 0.056463 | -0.0076221 | 0.06319 | -4.5044 | 116.8396 | -4.4357 | -4.4678 | 116.5192 | 1.4465 | 0.56763 | 0.40741 | 117.1143 | -4.5273 | 0.082397 | -0.27466 | 0.013732 | 0.050354 | -0.59509 | -0.009156 | 0 | -0.068665 | 5.0858 | 4.9255 | 121.0373 | 121.3577 | 0.013732 | 121.6324 | 5.9647 | -0.009156 | 121.3577 | 0.013732 | 5.9647 | 121.0373 | 121.6324 | -121.55 | -121.6415
735.2969 | 121.6965 | -4.2252 | 117.3981 | -0.16975 | 0.01534 | 0.0089829 | 0.0085107 | 0.058385 | -0.0071947 | 0.064258 | -4.184 | 117.1051 | -4.1245 | -4.1656 | 116.8304 | 1.4282 | 0.48981 | 0.32959 | 117.4118 | -4.2252 | 0.10071 | -0.29297 | 0.041199 | 0.05951 | -0.56763 | 0 | 0.013733 | -0.059509 | 4.715 | 4.5547 | 121.0556 | 121.3303 | 0.041199 | 121.637 | 5.6534 | 0 | 121.3303 | 0.041199 | 5.6534 | 121.0556 | 121.637 | -121.5225 | -121.6232
737.0469 | 121.8887 | -58.8135 | 62.4115 | 0.051498 | 0.013845 | 0.011974 | 0.0048791 | 0.057317 | -0.0067675 | 0.064471 | -57.4722 | 64.4348 | -56.8314 | -56.6437 | 64.7598 | 1.3229 | 0.50354 | 0.55847 | 64.4714 | -57.1518 | 1.9821 | 2.0233 | 1.3412 | 2.1698 | 2.3483 | 1.6617 | 2.0599 | -0.64087 | 59.317 | 59.3719 | 123.5733 | 123.2483 | 1.3412 | 123.2849 | 60.1364 | 1.6617 | 123.2483 | 1.3412 | 60.1364 | 123.5733 | 123.2849 | -119.2429 | -119.5633
738.8125 | 121.7239 | -5.0812 | 116.5558 | 0.1049 | 0.017263 | 0.0034287 | 0.0076563 | 0.057958 | -0.0071947 | 0.063831 | -5.0262 | 116.2857 | -4.9713 | -5.0079 | 115.979 | 1.2222 | -0.14648 | -0.2243 | 116.5787 | -5.0491 | 0.10986 | -0.27008 | 0.054932 | 0.073242 | -0.57678 | 0.032044 | 0.022888 | -0.054932 | 4.9347 | 4.8569 | 121.0602 | 121.3669 | 0.054932 | 121.6599 | 6.3034 | 0.032044 | 121.3669 | 0.054932 | 6.3034 | 121.0602 | 121.6599 | -121.5271 | -121.6049
740.5 | 121.7148 | -59.2804 | 62.1231 | -0.1545 | 0.013845 | 0.0077011 | 0.0087243 | 0.057317 | -0.0067675 | 0.064899 | -59.3399 | 61.8988 | -59.2529 | -59.3903 | 62.0132 | 0.15106 | 0.33875 | 0.42114 | 62.1048 | -59.3811 | 0.027466 | -0.2243 | -0.059509 | -0.10986 | -0.10986 | -0.10071 | -0.018311 | -0.086975 | 59.6191 | 59.7015 | 121.2936 | 121.1792 | -0.059509 | 121.3852 | 59.4315 | -0.10071 | 121.1792 | -0.059509 | 59.4315 | 121.2936 | 121.3852 | -121.376 | -121.5042
742.25 | 121.7972 | -58.4518 | 62.9059 | 0.051498 | 0.015981 | 0.010051 | 0.011074 | 0.054326 | -0.0076221 | 0.06618 | -58.6853 | 62.6907 | -58.5251 | -58.7357 | 62.6358 | -0.1236 | -0.21515 | -0.35248 | 62.8601 | -58.6304 | -0.073242 | -0.21515 | -0.23346 | -0.28381 | -0.27008 | -0.17853 | -0.045777 | -0.16022 | 58.2367 | 58.0994 | 121.0876 | 121.1426 | -0.23346 | 121.3119 | 58.3282 | -0.17853 | 121.1426 | -0.23346 | 58.3282 | 121.0876 | 121.3119 | -121.431 | -121.5363
744 | 121.8063 | -57.8796 | 63.5284 | -0.017166 | 0.01299 | 0.0079147 | 0.0029565 | 0.052617 | -0.0067675 | 0.06618 | -58.0444 | 63.2538 | -57.8888 | -58.0856 | 63.3133 | 0.1831 | 0.10071 | 0.2243 | 63.414 | -58.0582 | -0.009155 | -0.27466 | -0.1648 | -0.20599 | -0.21515 | -0.17853 | -0.11444 | -0.15564 | 57.9803 | 58.1039 | 121.1929 | 121.1334 | -0.1648 | 121.2936 | 58.0627 | -0.17853 | 121.1334 | -0.1648 | 58.0627 | 121.1929 | 121.2936 | -121.4172 | -121.5866
745.6875 | 121.8292 | -57.399 | 64.0228 | 0.059128 | 0.015767 | 0.0089829 | 0.0046655 | 0.055608 | -0.0050585 | 0.064471 | -57.5455 | 63.7207 | -57.3944 | -57.6141 | 63.7939 | 0.16022 | -0.036621 | 0.041199 | 63.9496 | -57.5546 | 0.004578 | -0.30212 | -0.14648 | -0.21515 | -0.22888 | -0.15564 | -0.073242 | -0.15106 | 57.3624 | 57.4402 | 121.1929 | 121.1197 | -0.14648 | 121.3486 | 57.5592 | -0.15564 | 121.1197 | -0.14648 | 57.5592 | 121.1929 | 121.3486 | -121.4172 | -121.5775
747.4219 | 121.1014 | -7.0496 | 114.7018 | -0.17738 | 0.014058 | 0.0057785 | 0.0027429 | 0.053899 | -0.0082629 | 0.062335 | -6.9855 | 114.2303 | -6.9397 | -6.926 | 114.0839 | 3.1403 | 0.64545 | 0.81024 | 114.5187 | -7.0404 | 0.10986 | -0.4715 | 0.064087 | 0.1236 | -0.61798 | 0.009156 | -0.1831 | -0.045777 | 7.695 | 7.8598 | 121.1334 | 121.2799 | 0.064087 | 121.5683 | 10.1898 | 0.009156 | 121.2799 | 0.064087 | 10.1898 | 121.1334 | 121.5683 | -121.6415 | -121.7422
749.1719 | 121.6232 | -5.3833 | 116.3498 | -0.10109 | 0.013845 | 0.0064193 | 0.0033839 | 0.055822 | -0.0065539 | 0.064685 | -5.2231 | 115.9698 | -5.2094 | -5.1773 | 115.8234 | 1.68 | 0.36163 | 0.60425 | 116.1942 | -5.3375 | 0.17395 | -0.37994 | 0.16022 | 0.20599 | -0.52643 | 0.045777 | -0.15564 | -0.013732 | 5.7449 | 5.9875 | 121.2067 | 121.3531 | 0.16022 | 121.5775 | 7.0633 | 0.045777 | 121.3531 | 0.16022 | 7.0633 | 121.2067 | 121.5775 | -121.5591 | -121.6873
750.9219 | 121.7239 | -5.127 | 116.5009 | 0.14305 | 0.016408 | 0.0072739 | 0.011074 | 0.057744 | -0.0080493 | 0.063403 | -5.1727 | 116.1346 | -5.0995 | -5.1224 | 115.8279 | 1.2543 | -0.09613 | -0.2243 | 116.4734 | -5.1682 | 0.027466 | -0.36621 | -0.045776 | 0.004578 | -0.67291 | -0.041199 | -0.027465 | -0.073242 | 5.0308 | 4.9026 | 120.9549 | 121.2616 | -0.045776 | 121.6003 | 6.3812 | -0.041199 | 121.2616 | -0.045776 | 6.3812 | 120.9549 | 121.6003 | -121.6003 | -121.669
752.625 | 121.6324 | -4.9484 | 116.7709 | -0.16975 | 0.017263 | 0.0072739 | 0.0059473 | 0.055181 | -0.0059131 | 0.065326 | -4.8111 | 116.3818 | -4.8157 | -4.7699 | 116.217 | 1.6159 | 0.4715 | 0.63171 | 116.6061 | -4.9026 | 0.13275 | -0.3891 | 0.13733 | 0.17853 | -0.55389 | 0.045776 | -0.16479 | 0.004578 | 5.4199 | 5.5801 | 121.1655 | 121.3303 | 0.13733 | 121.5546 | 6.5643 | 0.045776 | 121.3303 | 0.13733 | 6.5643 | 121.1655 | 121.5546 | -121.5866 | -121.6736
754.3594 | 121.6278 | -4.9393 | 116.7389 | -0.055313 | 0.011922 | 0.0094101 | 0.012142 | 0.055181 | -0.0074085 | 0.065112 | -4.8935 | 116.3681 | -4.8569 | -4.834 | 116.1301 | 1.4328 | 0.11902 | 0.11444 | 116.6107 | -4.9393 | 0.082397 | -0.37079 | 0.045776 | 0.10529 | -0.60883 | 0 | -0.12817 | -0.036621 | 5.0583 | 5.0537 | 121.0693 | 121.3074 | 0.045776 | 121.55 | 6.3721 | 0 | 121.3074 | 0.045776 | 6.3721 | 121.0693 | 121.55 | -121.5958 | -121.6782
756.0938 | 121.7514 | -4.6097 | 116.9678 | 0.14305 | 0.016195 | 0.0070603 | 0.01022 | 0.056463 | -0.0076221 | 0.064258 | -4.6509 | 116.6748 | -4.5868 | -4.6417 | 116.3544 | 1.2222 | -0.11444 | -0.23804 | 116.9449 | -4.6738 | 0.022888 | -0.29297 | -0.041199 | -0.032044 | -0.6134 | -0.064087 | -0.022888 | -0.064087 | 4.4952 | 4.3716 | 120.9641 | 121.2845 | -0.041199 | 121.5546 | 5.8319 | -0.064087 | 121.2845 | -0.041199 | 5.8319 | 120.9641 | 121.5546 | -121.5546 | -121.6415
757.7812 | 121.6965 | -4.8248 | 116.8121 | 0.38719 | 0.014699 | 0.01176 | 0.01022 | 0.05454 | -0.0063403 | 0.06618 | -4.6738 | 116.5924 | -4.6051 | -4.66 | 116.3132 | 1.3 | 0.018311 | -0.11902 | 116.9083 | -4.715 | 0.21973 | -0.21973 | 0.15106 | 0.1648 | -0.49896 | 0.10986 | 0.09613 | -0.068664 | 4.8431 | 4.7058 | 121.138 | 121.4172 | 0.15106 | 121.7331 | 6.1249 | 0.10986 | 121.4172 | 0.15106 | 6.1249 | 121.138 | 121.7331 | -121.4172 | -121.5271
759.5312 | 121.7697 | -4.8294 | 116.7526 | 0.12779 | 0.015981 | 0.0094101 | 0.0055201 | 0.057317 | -0.0099719 | 0.065326 | -4.8798 | 116.4093 | -4.7882 | -4.8614 | 116.1484 | 1.1856 | -0.13275 | -0.23804 | 116.748 | -4.8935 | 0.041199 | -0.34332 | -0.050354 | -0.032043 | -0.60425 | -0.064087 | -0.004578 | -0.091553 | 4.6967 | 4.5914 | 120.9778 | 121.2387 | -0.050354 | 121.5775 | 6.015 | -0.064087 | 121.2387 | -0.050354 | 6.015 | 120.9778 | 121.5775 | -121.5408 | -121.6461
761.2188 | 121.637 | -5.8182 | 115.8417 | 0.082016 | 0.016195 | 0.010051 | 0.0085107 | 0.057317 | -0.0078357 | 0.06618 | -5.8044 | 115.535 | -5.7129 | -5.7907 | 115.2191 | 1.2863 | 0.004578 | -0.17395 | 115.8325 | -5.8044 | 0.10529 | -0.3067 | 0.013733 | 0.027466 | -0.62256 | 0.013733 | -0.009155 | -0.091552 | 5.8228 | 5.6442 | 121.0373 | 121.3531 | 0.013733 | 121.6507 | 7.1045 | 0.013733 | 121.3531 | 0.013733 | 7.1045 | 121.0373 | 121.6507 | -121.5546 | -121.6461
762.9844 | 121.5912 | -5.3055 | 116.3956 | -0.11635 | 0.016195 | 0.0059921 | 0.0078699 | 0.054754 | -0.0093311 | 0.065326 | -5.3558 | 115.9195 | -5.3238 | -5.3329 | 115.6906 | 1.4465 | 0.28381 | 0.23346 | 116.2079 | -5.3833 | -0.018311 | -0.47607 | -0.050354 | -0.027466 | -0.70496 | -0.07782 | -0.18768 | -0.032043 | 5.5893 | 5.5389 | 120.9961 | 121.225 | -0.050354 | 121.5134 | 6.752 | -0.07782 | 121.225 | -0.050354 | 6.752 | 120.9961 | 121.5134 | -121.7194 | -121.7789
764.6719 | 121.6095 | -5.0079 | 116.7114 | -0.20027 | 0.014272 | 0.010692 | 0.0023157 | 0.053686 | -0.0074085 | 0.06554 | -4.8477 | 116.3406 | -4.8477 | -4.8248 | 116.1713 | 1.5701 | 0.43945 | 0.60425 | 116.6153 | -4.9576 | 0.16022 | -0.37079 | 0.16022 | 0.18311 | -0.54016 | 0.050354 | -0.096131 | 0 | 5.4474 | 5.6122 | 121.1792 | 121.3486 | 0.16022 | 121.6232 | 6.5781 | 0.050354 | 121.3486 | 0.16022 | 6.5781 | 121.1792 | 121.6232 | -121.5591 | -121.669
766.4219 | 121.7194 | -8.6792 | 112.9349 | 0.1812 | 0.014699 | 0.012615 | 0.0097925 | 0.056249 | -0.0046313 | 0.065753 | -8.757 | 112.5916 | -8.638 | -8.6929 | 112.3627 | 1.1581 | -0.25635 | -0.16937 | 112.8571 | -8.725 | 0.041199 | -0.34332 | -0.07782 | -0.013733 | -0.5722 | -0.045777 | -0.077819 | -0.11902 | 8.4229 | 8.5098 | 121.0419 | 121.2708 | -0.07782 | 121.5363 | 9.8373 | -0.045777 | 121.2708 | -0.07782 | 9.8373 | 121.0419 | 121.5363 | -121.5729 | -121.6599
768.1719 | 121.669 | -6.9305 | 114.7339 | -0.21553 | 0.015127 | 0.011119 | 0.0057337 | 0.056035 | -0.0067675 | 0.063617 | -6.9168 | 114.3814 | -6.8481 | -6.9122 | 114.1022 | 1.4694 | 0.59509 | 0.48981 | 114.6332 | -6.9763 | 0.082397 | -0.35248 | 0.013733 | 0.018311 | -0.63171 | -0.045776 | -0.10071 | -0.068664 | 7.5256 | 7.4203 | 121.0327 | 121.312 | 0.013733 | 121.5637 | 8.4 | -0.045776 | 121.312 | 0.013733 | 8.4 | 121.0327 | 121.5637 | -121.582 | -121.7102
769.9219 | 121.669 | -6.6742 | 114.9673 | -0.0095368 | 0.015554 | 0.0094101 | 0.010006 | 0.057104 | -0.0076221 | 0.064685 | -6.6559 | 114.6423 | -6.5735 | -6.633 | 114.3677 | 1.2817 | 0.032043 | -0.045776 | 114.9353 | -6.6742 | 0.10071 | -0.32501 | 0.01831 | 0.041198 | -0.59967 | 0 | -0.032043 | -0.082398 | 6.7062 | 6.6284 | 121.0419 | 121.3165 | 0.01831 | 121.6095 | 7.9559 | 0 | 121.3165 | 0.01831 | 7.9559 | 121.0419 | 121.6095 | -121.5408 | -121.6415
771.625 | 121.701 | -6.4682 | 115.1276 | 0.1812 | 0.015767 | 0.0085555 | 0.0053065 | 0.055822 | -0.0076221 | 0.064471 | -6.3995 | 114.8117 | -6.3812 | -6.3721 | 114.6423 | 1.2268 | -0.24719 | -0.027466 | 115.0131 | -6.4911 | 0.086975 | -0.31586 | 0.068665 | 0.096131 | -0.48523 | -0.022888 | -0.11444 | -0.01831 | 6.221 | 6.4407 | 121.1105 | 121.2799 | 0.068665 | 121.4813 | 7.695 | -0.022888 | 121.2799 | 0.068665 | 7.695 | 121.1105 | 121.4813 | -121.5088 | -121.6187
773.3906 | 121.7514 | -6.1707 | 115.3839 | 0.19646 | 0.015554 | 0.0087693 | 0.01022 | 0.057104 | -0.0056995 | 0.064899 | -6.2393 | 115.1413 | -6.102 | -6.2073 | 114.8117 | 1.1536 | -0.12817 | -0.25635 | 115.3976 | -6.2256 | 0.068664 | -0.24262 | -0.068665 | -0.036621 | -0.5722 | -0.054932 | 0.013733 | -0.13733 | 6.0425 | 5.9143 | 120.9824 | 121.3119 | -0.068665 | 121.5683 | 7.3242 | -0.054932 | 121.3119 | -0.068665 | 7.3242 | 120.9824 | 121.5683 | -121.4859 | -121.6095
775.1406 | 121.7514 | -5.777 | 115.8005 | 0.11253 | 0.014486 | 0.010478 | 0.0048791 | 0.057744 | -0.0061267 | 0.06618 | -5.7358 | 115.48 | -5.7037 | -5.7266 | 115.274 | 1.2772 | -0.10071 | 0.041199 | 115.741 | -5.8136 | 0.073243 | -0.32043 | 0.041199 | 0.050354 | -0.52643 | -0.036621 | -0.059509 | -0.032044 | 5.6763 | 5.8182 | 121.051 | 121.257 | 0.041199 | 121.5179 | 7.0541 | -0.036621 | 121.257 | 0.041199 | 7.0541 | 121.051 | 121.5179 | -121.5042 | -121.6141
776.8438 | 121.7194 | -6.0425 | 115.5441 | 0.15831 | 0.017049 | 0.010478 | 0.0087243 | 0.05689 | -0.0080493 | 0.063617 | -6.0287 | 115.2283 | -5.9875 | -5.9738 | 115.036 | 1.2131 | -0.2655 | -0.12817 | 115.4846 | -6.0608 | 0.054931 | -0.31586 | 0.013732 | 0.068664 | -0.50812 | -0.018311 | -0.059509 | -0.041199 | 5.777 | 5.9143 | 121.0785 | 121.2708 | 0.013732 | 121.5271 | 7.2556 | -0.018311 | 121.2708 | 0.013732 | 7.2556 | 121.0785 | 121.5271 | -121.5317 | -121.6049
778.5938 | 121.6599 | -5.9921 | 115.6677 | -0.11635 | 0.014486 | 0.0064193 | 0.0025293 | 0.05454 | -0.0056995 | 0.064258 | -5.8914 | 115.2924 | -5.864 | -5.8365 | 115.1642 | 1.5106 | 0.32501 | 0.54474 | 115.5487 | -5.9738 | 0.12817 | -0.37537 | 0.10071 | 0.15564 | -0.50354 | 0.01831 | -0.11902 | -0.027465 | 6.3171 | 6.5369 | 121.1563 | 121.2845 | 0.10071 | 121.5408 | 7.5027 | 0.01831 | 121.2845 | 0.10071 | 7.5027 | 121.1563 | 121.5408 | -121.5317 | -121.6415
780.3594 | 121.7697 | -5.7632 | 115.8096 | 0.11253 | 0.017263 | 0.013469 | 0.010647 | 0.055608 | -0.0071947 | 0.064899 | -5.809 | 115.5121 | -5.7541 | -5.7999 | 115.1962 | 1.1948 | -0.09613 | -0.23346 | 115.8142 | -5.8273 | 0.009156 | -0.29755 | -0.045776 | -0.036621 | -0.6134 | -0.064087 | 0.004578 | -0.054932 | 5.6671 | 5.5298 | 120.9595 | 121.2753 | -0.045776 | 121.5775 | 6.958 | -0.064087 | 121.2753 | -0.045776 | 6.958 | 120.9595 | 121.5775 | -121.5637 | -121.637
782.0469 | 121.6919 | -5.8273 | 115.7776 | -0.22316 | 0.016408 | 0.0066329 | 0.0070155 | 0.056249 | -0.0069811 | 0.06319 | -5.8685 | 115.5167 | -5.7678 | -5.8502 | 115.1733 | 1.4511 | 0.54474 | 0.40283 | 115.7867 | -5.8777 | 0.05951 | -0.26093 | -0.041198 | -0.022888 | -0.60425 | -0.050354 | 0.009155 | -0.10071 | 6.3721 | 6.2302 | 121.0007 | 121.344 | -0.041198 | 121.6141 | 7.2784 | -0.050354 | 121.344 | -0.041198 | 7.2784 | 121.0007 | 121.6141 | -121.5454 | -121.6553
783.7969 | 121.7285 | -6.015 | 115.5762 | 0.12016 | 0.015554 | 0.0096237 | 0.0068017 | 0.056676 | -0.0071947 | 0.06554 | -5.9601 | 115.242 | -5.928 | -5.9235 | 115.0772 | 1.2497 | -0.27466 | -0.09613 | 115.5212 | -6.0333 | 0.086975 | -0.33417 | 0.054932 | 0.091553 | -0.49896 | -0.01831 | -0.054932 | -0.032043 | 5.7404 | 5.9189 | 121.0922 | 121.257 | 0.054932 | 121.5363 | 7.2647 | -0.01831 | 121.257 | 0.054932 | 7.2647 | 121.0922 | 121.5363 | -121.5042 | -121.6095
785.4844 | 121.637 | -5.7037 | 115.9515 | -0.12398 | 0.015767 | 0.0098373 | 0.0074427 | 0.055822 | -0.0078357 | 0.064044 | -5.6992 | 115.6174 | -5.6305 | -5.6396 | 115.3656 | 1.4877 | 0.33417 | 0.27466 | 115.8966 | -5.7175 | 0.073242 | -0.33417 | 0.004577 | 0.064087 | -0.58594 | -0.013733 | -0.054932 | -0.068665 | 6.0379 | 5.9784 | 121.0693 | 121.3211 | 0.004577 | 121.6003 | 7.1915 | -0.013733 | 121.3211 | 0.004577 | 7.1915 | 121.0693 | 121.6003 | -121.582 | -121.669
787.2344 | 121.7331 | -5.6854 | 115.9332 | 0.1812 | 0.014272 | 0.0068467 | 0.0063745 | 0.057104 | -0.0084765 | 0.062335 | -5.5756 | 115.6174 | -5.5389 | -5.5573 | 115.4434 | 1.2634 | -0.27466 | -0.082397 | 115.8737 | -5.6396 | 0.14649 | -0.31586 | 0.10986 | 0.12817 | -0.48981 | 0.045777 | -0.05951 | -0.036622 | 5.4108 | 5.603 | 121.1288 | 121.3028 | 0.10986 | 121.5591 | 6.9489 | 0.045777 | 121.3028 | 0.10986 | 6.9489 | 121.1288 | 121.5591 | -121.4722 | -121.5729
789 | 121.6461 | -5.658 | 116.0477 | -0.16975 | 0.013418 | 0.0072739 | 0.0046655 | 0.056249 | -0.0061267 | 0.063617 | -5.5206 | 115.6677 | -5.4932 | -5.4703 | 115.5258 | 1.5701 | 0.4303 | 0.58594 | 115.9378 | -5.5939 | 0.16479 | -0.37994 | 0.13733 | 0.18768 | -0.52185 | 0.064087 | -0.10986 | -0.027466 | 6.0883 | 6.2439 | 121.1838 | 121.3257 | 0.13733 | 121.5958 | 7.2281 | 0.064087 | 121.3257 | 0.13733 | 7.2281 | 121.1838 | 121.5958 | -121.5408 | -121.6415
790.75 | 121.8018 | -5.4611 | 116.1163 | 0.059128 | 0.014272 | 0.0053513 | 0.0046655 | 0.056035 | -0.0059131 | 0.063617 | -5.4337 | 115.8371 | -5.3696 | -5.3925 | 115.5991 | 1.3138 | 0.10529 | 0.17853 | 116.098 | -5.4611 | 0.091553 | -0.27924 | 0.027466 | 0.068665 | -0.51727 | 0 | -0.018311 | -0.064087 | 5.5664 | 5.6396 | 121.0602 | 121.2982 | 0.027466 | 121.5591 | 6.7749 | 0 | 121.2982 | 0.027466 | 6.7749 | 121.0602 | 121.5591 | -121.4859 | -121.5775
792.5 | 121.6782 | -5.7953 | 115.8188 | -0.16212 | 0.015767 | 0.0085555 | 0.0089381 | 0.05454 | -0.0067675 | 0.064471 | -5.8777 | 115.4709 | -5.7907 | -5.809 | 115.1733 | 1.4877 | 0.50354 | 0.35248 | 115.741 | -5.8502 | 0.004578 | -0.3479 | -0.082398 | -0.013733 | -0.64545 | -0.054932 | -0.07782 | -0.086976 | 6.2988 | 6.1478 | 120.9686 | 121.2662 | -0.082398 | 121.5363 | 7.283 | -0.054932 | 121.2662 | -0.082398 | 7.283 | 120.9686 | 121.5363 | -121.6095 | -121.669
794.2031 | 121.7834 | -5.6396 | 115.9195 | 0.1049 | 0.016195 | 0.011333 | 0.011501 | 0.055822 | -0.0080493 | 0.065967 | -5.6946 | 115.6677 | -5.603 | -5.658 | 115.3015 | 1.2314 | -0.10071 | -0.22888 | 115.9058 | -5.6946 | 0.036621 | -0.25177 | -0.054932 | -0.018311 | -0.61798 | -0.054932 | -0.013733 | -0.091553 | 5.5389 | 5.4108 | 120.9412 | 121.3074 | -0.054932 | 121.5454 | 6.871 | -0.054932 | 121.3074 | -0.054932 | 6.871 | 120.9412 | 121.5454 | -121.5225 | -121.6141
795.9531 | 121.7285 | -5.7678 | 115.8325 | -0.085831 | 0.013418 | 0.0055649 | 0.0021021 | 0.054967 | -0.0048449 | 0.065326 | -5.7861 | 115.4434 | -5.7266 | -5.6992 | 115.3107 | 1.4969 | 0.29755 | 0.4715 | 115.7135 | -5.8411 | 0.041198 | -0.3891 | -0.018311 | 0.068664 | -0.52185 | -0.073242 | -0.11902 | -0.059509 | 6.0654 | 6.2393 | 121.0785 | 121.2112 | -0.018311 | 121.4813 | 7.2647 | -0.073242 | 121.2112 | -0.018311 | 7.2647 | 121.0785 | 121.4813 | -121.5591 | -121.6736
797.6406 | 121.7743 | -5.6808 | 115.8875 | 0.1049 | 0.015554 | 0.0087693 | 0.010006 | 0.058172 | -0.0063403 | 0.064899 | -5.7266 | 115.6036 | -5.6488 | -5.7037 | 115.2786 | 1.2497 | -0.10529 | -0.21973 | 115.9103 | -5.7175 | 0.032043 | -0.28381 | -0.045777 | -0.022888 | -0.60883 | -0.036621 | 0.022888 | -0.07782 | 5.5756 | 5.4611 | 120.9595 | 121.2845 | -0.045777 | 121.5912 | 6.9305 | -0.036621 | 121.2845 | -0.045777 | 6.9305 | 120.9595 | 121.5912 | -121.5363 | -121.6049
799.4062 | 121.6324 | -5.6213 | 116.0248 | -0.10872 | 0.013845 | 0.0096237 | 0.010433 | 0.054967 | -0.0086901 | 0.063403 | -5.5573 | 115.6815 | -5.5527 | -5.5298 | 115.4434 | 1.4648 | 0.21515 | 0.1831 | 116.0019 | -5.6122 | 0.068665 | -0.34332 | 0.064087 | 0.091553 | -0.58136 | 0.009155 | -0.022888 | -0.004578 | 5.8365 | 5.8044 | 121.0648 | 121.3028 | 0.064087 | 121.6232 | 7.0862 | 0.009155 | 121.3028 | 0.064087 | 7.0862 | 121.0648 | 121.6232 | -121.5775 | -121.637
801.0938 | 121.7743 | -5.5206 | 116.0843 | 0.1049 | 0.015554 | 0.0077011 | 0.0029565 | 0.057531 | -0.0044177 | 0.063831 | -5.4474 | 115.7684 | -5.4153 | -5.4382 | 115.567 | 1.2955 | -0.073242 | 0.059509 | 116.0294 | -5.5115 | 0.10529 | -0.31586 | 0.073242 | 0.082398 | -0.51727 | 0.009155 | -0.054932 | -0.032044 | 5.4474 | 5.5801 | 121.0876 | 121.2891 | 0.073242 | 121.55 | 6.8161 | 0.009155 | 121.2891 | 0.073242 | 6.8161 | 121.0876 | 121.55 | -121.4996 | -121.5958
802.8438 | 121.637 | -5.159 | 116.5237 | -0.055313 | 0.014699 | 0.0096237 | 0.0087243 | 0.056249 | -0.0089037 | 0.065326 | -5.0858 | 116.1758 | -5.0446 | -5.0537 | 115.9241 | 1.5015 | 0.18768 | 0.1831 | 116.4505 | -5.1498 | 0.11444 | -0.3479 | 0.073243 | 0.10529 | -0.59967 | 0.009156 | -0.073243 | -0.041198 | 5.3467 | 5.3421 | 121.0831 | 121.3348 | 0.073243 | 121.6095 | 6.6605 | 0.009156 | 121.3348 | 0.073243 | 6.6605 | 121.0831 | 121.6095 | -121.5683 | -121.6736
804.5938 | 121.788 | -5.2597 | 116.3315 | 0.12779 | 0.015554 | 0.0036423 | 0.0093653 | 0.056035 | -0.0052721 | 0.064471 | -5.2551 | 116.0614 | -5.1865 | -5.2689 | 115.7272 | 1.2039 | -0.17395 | -0.24261 | 116.3406 | -5.2963 | 0.073243 | -0.27008 | 0.004578 | -0.009155 | -0.60425 | -0.036621 | 0.009155 | -0.068665 | 5.0858 | 5.0171 | 120.9869 | 121.3211 | 0.004578 | 121.6003 | 6.4636 | -0.036621 | 121.3211 | 0.004578 | 6.4636 | 120.9869 | 121.6003 | -121.5179 | -121.6278
806.3438 | 121.6873 | -5.2872 | 116.3864 | -0.18501 | 0.016622 | 0.0072739 | 0.0061609 | 0.057531 | -0.0067675 | 0.064044 | -5.2689 | 116.1072 | -5.1727 | -5.2322 | 115.773 | 1.5198 | 0.48065 | 0.33875 | 116.391 | -5.2734 | 0.11444 | -0.27924 | 0.01831 | 0.054931 | -0.6134 | 0.013733 | 0.004577 | -0.096131 | 5.7678 | 5.6259 | 121.0602 | 121.3943 | 0.01831 | 121.6782 | 6.8069 | 0.013733 | 121.3943 | 0.01831 | 6.8069 | 121.0602 | 121.6782 | -121.5591 | -121.6599
808.0156 | 121.8109 | -5.3192 | 116.2491 | 0.020981 | 0.013631 | 0.0059921 | 0.0025293 | 0.054113 | -0.0061267 | 0.064471 | -5.3101 | 115.9424 | -5.246 | -5.3055 | 115.7181 | 1.3687 | 0.11902 | 0.19684 | 116.2399 | -5.3329 | 0.073242 | -0.3067 | 0.009155 | 0.013733 | -0.531 | -0.013733 | -0.009155 | -0.064087 | 5.4382 | 5.5161 | 121.0373 | 121.2616 | 0.009155 | 121.5591 | 6.6879 | -0.013733 | 121.2616 | 0.009155 | 6.6879 | 121.0373 | 121.5591 | -121.4951 | -121.582
809.7656 | 121.7377 | -5.2322 | 116.3315 | 0.082016 | 0.014699 | 0.010265 | 0.0080835 | 0.056676 | -0.0080493 | 0.064899 | -5.159 | 116.0202 | -5.1453 | -5.1315 | 115.86 | 1.2909 | -0.27924 | -0.1236 | 116.3361 | -5.2277 | 0.086975 | -0.31128 | 0.073242 | 0.10071 | -0.4715 | 0.004578 | 0.004578 | -0.013733 | 4.953 | 5.1086 | 121.0922 | 121.2524 | 0.073242 | 121.5683 | 6.5231 | 0.004578 | 121.2524 | 0.073242 | 6.5231 | 121.0922 | 121.5683 | -121.4767 | -121.5591
811.5156 | 121.6461 | -5.3329 | 116.3086 | -0.12398 | 0.013631 | 0.0040695 | 0.0055201 | 0.055822 | -0.0065539 | 0.065112 | -5.2048 | 115.9561 | -5.2002 | -5.1636 | 115.8325 | 1.5793 | 0.36163 | 0.54932 | 116.2491 | -5.3146 | 0.13275 | -0.35248 | 0.12817 | 0.16937 | -0.47607 | 0.018311 | -0.05951 | -0.004578 | 5.6946 | 5.8823 | 121.1655 | 121.2891 | 0.12817 | 121.582 | 6.9122 | 0.018311 | 121.2891 | 0.12817 | 6.9122 | 121.1655 | 121.582 | -121.5088 | -121.6232
813.2656 | 121.6782 | -5.2963 | 116.3544 | -0.13161 | 0.015767 | 0.0051377 | 0.0057337 | 0.053899 | -0.0054859 | 0.064685 | -5.1773 | 116.0248 | -5.1865 | -5.1224 | 115.8554 | 1.5793 | 0.32501 | 0.53558 | 116.2811 | -5.2872 | 0.10986 | -0.32959 | 0.11902 | 0.17395 | -0.49896 | 0.009156 | -0.073242 | 0.009155 | 5.6213 | 5.8319 | 121.1517 | 121.3211 | 0.11902 | 121.5775 | 6.8756 | 0.009156 | 121.3211 | 0.11902 | 6.8756 | 121.1517 | 121.5775 | -121.5408 | -121.6415
815.0156 | 121.7697 | -4.7699 | 116.803 | 0.11253 | 0.015767 | 0.0074875 | 0.0065881 | 0.054754 | -0.0065539 | 0.064685 | -4.6921 | 116.4917 | -4.6509 | -4.6738 | 116.2903 | 1.3367 | -0.036621 | 0.068665 | 116.8076 | -4.7562 | 0.11902 | -0.31128 | 0.077819 | 0.09613 | -0.5127 | 0.013732 | 0.004577 | -0.041199 | 4.7333 | 4.8386 | 121.0602 | 121.2616 | 0.077819 | 121.5775 | 6.1066 | 0.013732 | 121.2616 | 0.077819 | 6.1066 | 121.0602 | 121.5775 | -121.4539 | -121.5591
816.7031 | 121.7422 | -5.2689 | 116.3177 | -0.062942 | 0.013631 | 0.0089829 | 0.0035975 | 0.053045 | -0.0071947 | 0.064471 | -5.2048 | 116.0156 | -5.1773 | -5.1498 | 115.8325 | 1.506 | 0.28381 | 0.46234 | 116.2857 | -5.2917 | 0.091553 | -0.30212 | 0.064087 | 0.11902 | -0.48523 | -0.022888 | -0.032043 | -0.027466 | 5.5527 | 5.7312 | 121.1014 | 121.2845 | 0.064087 | 121.5546 | 6.7749 | -0.022888 | 121.2845 | 0.064087 | 6.7749 | 121.1014 | 121.5546 | -121.4951 | -121.6095
818.4375 | 121.7056 | -5.2917 | 116.3589 | -0.21553 | 0.015981 | 0.010478 | 0.0091517 | 0.055822 | -0.0074085 | 0.062335 | -5.2689 | 116.098 | -5.2048 | -5.2551 | 115.7181 | 1.5564 | 0.54016 | 0.39825 | 116.3498 | -5.3146 | 0.086975 | -0.26093 | 0.022888 | 0.036621 | -0.64087 | -0.022888 | -0.009156 | -0.064087 | 5.8319 | 5.69 | 121.0098 | 121.3898 | 0.022888 | 121.6415 | 6.8481 | -0.022888 | 121.3898 | 0.022888 | 6.8481 | 121.0098 | 121.6415 | -121.5637 | -121.6736
820.1875 | 121.669 | -5.0903 | 116.5512 | -0.13924 | 0.014913 | 0.0081283 | 0.01022 | 0.055181 | -0.01104 | 0.064685 | -5.0812 | 116.2033 | -5.0217 | -5.0217 | 115.9607 | 1.5701 | 0.43488 | 0.31586 | 116.5283 | -5.0995 | 0.068665 | -0.3479 | 0.009155 | 0.068665 | -0.59051 | -0.009155 | -0.022888 | -0.05951 | 5.5252 | 5.4062 | 121.051 | 121.2936 | 0.009155 | 121.6187 | 6.6605 | -0.009155 | 121.2936 | 0.009155 | 6.6605 | 121.051 | 121.6187 | -121.5729 | -121.6507
821.9375 | 121.7239 | -5.3192 | 116.2994 | 0.13542 | 0.016622 | 0.010906 | 0.0078699 | 0.058172 | -0.0082629 | 0.064044 | -5.2277 | 115.9744 | -5.2277 | -5.2048 | 115.7822 | 1.3184 | -0.28381 | -0.073242 | 116.2537 | -5.3146 | 0.091553 | -0.32501 | 0.091553 | 0.11444 | -0.51727 | 0.004578 | -0.045776 | 0 | 5.0354 | 5.246 | 121.1014 | 121.2936 | 0.091553 | 121.5729 | 6.6376 | 0.004578 | 121.2936 | 0.091553 | 6.6376 | 121.1014 | 121.5729 | -121.5271 | -121.6141
823.6406 | 121.6415 | -5.2734 | 116.3818 | -0.1545 | 0.016622 | 0.0083419 | 0.0065881 | 0.054113 | -0.0059131 | 0.064471 | -5.159 | 116.0568 | -5.1498 | -5.1224 | 115.892 | 1.6479 | 0.45319 | 0.58594 | 116.3315 | -5.2643 | 0.1236 | -0.32501 | 0.11444 | 0.15106 | -0.48981 | 0.009155 | -0.050354 | -0.009156 | 5.7266 | 5.8594 | 121.1655 | 121.3303 | 0.11444 | 121.6049 | 6.9214 | 0.009155 | 121.3303 | 0.11444 | 6.9214 | 121.1655 | 121.6049 | -121.5317 | -121.6461
825.375 | 121.6553 | -5.2963 | 116.3498 | -0.047684 | 0.016195 | 0.0072739 | 0.011074 | 0.055395 | -0.010399 | 0.065753 | -5.1819 | 116.098 | -5.1498 | -5.1682 | 115.8279 | 1.4145 | 0.073242 | 0.018311 | 116.3635 | -5.2414 | 0.14648 | -0.25177 | 0.11444 | 0.12817 | -0.52185 | 0.054932 | 0.013733 | -0.032044 | 5.3696 | 5.3146 | 121.1243 | 121.3943 | 0.11444 | 121.6599 | 6.7108 | 0.054932 | 121.3943 | 0.11444 | 6.7108 | 121.1243 | 121.6599 | -121.4996 | -121.5912
827.125 | 121.7972 | -5.2185 | 116.3589 | 0.051498 | 0.016622 | 0.010478 | 0.0046655 | 0.056249 | -0.0084765 | 0.062763 | -5.1956 | 116.098 | -5.1086 | -5.1544 | 115.8417 | 1.3687 | 0.059509 | 0.13733 | 116.3818 | -5.2322 | 0.10986 | -0.26093 | 0.022888 | 0.064087 | -0.51727 | -0.013733 | 0.022888 | -0.086975 | 5.278 | 5.3558 | 121.0602 | 121.3165 | 0.022888 | 121.6003 | 6.5872 | -0.013733 | 121.3165 | 0.022888 | 6.5872 | 121.0602 | 121.6003 | -121.4676 | -121.5912
828.8281 | 121.7789 | -4.8065 | 116.7801 | 0.0057222 | 0.015767 | 0.0053513 | 0.0035975 | 0.055395 | -0.0059131 | 0.064471 | -4.7791 | 116.5009 | -4.7058 | -4.7424 | 116.2674 | 1.4465 | 0.19226 | 0.27924 | 116.7984 | -4.8203 | 0.10071 | -0.27924 | 0.027466 | 0.064087 | -0.5127 | -0.013732 | 0.018311 | -0.073242 | 4.9988 | 5.0858 | 121.0739 | 121.3074 | 0.027466 | 121.6049 | 6.2531 | -0.013732 | 121.3074 | 0.027466 | 6.2531 | 121.0739 | 121.6049 | -121.4859 | -121.6003
830.5781 | 121.7697 | -5.0171 | 116.5192 | 0.020981 | 0.016622 | 0.0066329 | 0.0061609 | 0.056249 | -0.0063403 | 0.063617 | -5.0171 | 116.2399 | -4.9576 | -4.9988 | 115.9927 | 1.4145 | 0.16937 | 0.25177 | 116.5649 | -5.0674 | 0.059509 | -0.27924 | 0 | 0.018311 | -0.52643 | -0.050354 | 0.045776 | -0.059509 | 5.1865 | 5.2689 | 121.0098 | 121.257 | 0 | 121.582 | 6.4316 | -0.050354 | 121.257 | 0 | 6.4316 | 121.0098 | 121.582 | -121.4767 | -121.5866
832.3281 | 121.6507 | -4.953 | 116.7389 | -0.17738 | 0.016195 | 0.0057785 | 0.0070155 | 0.056463 | -0.0056995 | 0.062122 | -4.8157 | 116.3818 | -4.7882 | -4.7653 | 116.217 | 1.6617 | 0.43488 | 0.60425 | 116.6702 | -4.8935 | 0.16479 | -0.35706 | 0.13733 | 0.18768 | -0.52185 | 0.059509 | -0.068665 | -0.027466 | 5.3879 | 5.5573 | 121.17 | 121.3348 | 0.13733 | 121.6232 | 6.6147 | 0.059509 | 121.3348 | 0.13733 | 6.6147 | 121.17 | 121.6232 | -121.5271 | -121.6324
834.0938 | 121.7834 | -5.0446 | 116.5466 | 0.0057222 | 0.01534 | 0.010051 | 0.0048791 | 0.052617 | -0.0061267 | 0.064044 | -4.985 | 116.272 | -4.9301 | -4.9667 | 116.0294 | 1.3733 | 0.16937 | 0.21515 | 116.5558 | -5.0171 | 0.11444 | -0.27466 | 0.05951 | 0.07782 | -0.51727 | 0.027466 | 0.009155 | -0.054931 | 5.2139 | 5.2597 | 121.0739 | 121.3165 | 0.05951 | 121.6003 | 6.4178 | 0.027466 | 121.3165 | 0.05951 | 6.4178 | 121.0739 | 121.6003 | -121.4767 | -121.5637
835.7812 | 121.6827 | -4.9667 | 116.6611 | -0.21553 | 0.013845 | 0.0077011 | 0.0087243 | 0.050908 | -0.0074085 | 0.063831 | -4.953 | 116.3635 | -4.8889 | -4.9118 | 116.0614 | 1.6159 | 0.57678 | 0.41657 | 116.6885 | -4.9576 | 0.07782 | -0.29755 | 0.013733 | 0.054932 | -0.59967 | 0.009155 | 0.027466 | -0.064087 | 5.5435 | 5.3833 | 121.0281 | 121.3303 | 0.013733 | 121.6553 | 6.5826 | 0.009155 | 121.3303 | 0.013733 | 6.5826 | 121.0281 | 121.6553 | -121.55 | -121.6187
837.5312 | 121.7834 | -4.921 | 116.6565 | 0.11253 | 0.018117 | 0.0072739 | 0.0072291 | 0.054754 | -0.0076221 | 0.065753 | -4.953 | 116.3681 | -4.8798 | -4.9393 | 116.0339 | 1.2955 | -0.11902 | -0.22888 | 116.684 | -4.9759 | 0.041198 | -0.28839 | -0.032044 | -0.018311 | -0.62256 | -0.054932 | 0.027466 | -0.073242 | 4.8019 | 4.6921 | 120.9549 | 121.2891 | -0.032044 | 121.6049 | 6.2164 | -0.054932 | 121.2891 | -0.032044 | 6.2164 | 120.9549 | 121.6049 | -121.5363 | -121.6324
839.2188 | 121.7606 | -4.9484 | 116.6382 | -0.032425 | 0.015554 | 0.0066329 | 0.0031701 | 0.055822 | -0.0065539 | 0.064471 | -4.9118 | 116.3727 | -4.8386 | -4.8614 | 116.1301 | 1.506 | 0.24719 | 0.36621 | 116.6199 | -4.9713 | 0.10986 | -0.2655 | 0.036621 | 0.086975 | -0.50812 | -0.022888 | -0.018311 | -0.073242 | 5.1956 | 5.3146 | 121.0785 | 121.3211 | 0.036621 | 121.5683 | 6.4545 | -0.022888 | 121.3211 | 0.036621 | 6.4545 | 121.0785 | 121.5683 | -121.4767 | -121.6095
840.9688 | 121.7239 | -4.8111 | 116.7572 | 0.16594 | 0.014272 | 0.0064193 | 0.0078699 | 0.056676 | -0.0071947 | 0.064258 | -4.7928 | 116.4597 | -4.7607 | -4.7653 | 116.2033 | 1.3092 | -0.26093 | -0.16479 | 116.7389 | -4.834 | 0.050354 | -0.29755 | 0.01831 | 0.045776 | -0.55389 | -0.022888 | -0.01831 | -0.032044 | 4.5502 | 4.6463 | 121.0144 | 121.2708 | 0.01831 | 121.55 | 6.1203 | -0.022888 | 121.2708 | 0.01831 | 6.1203 | 121.0144 | 121.55 | -121.5179 | -121.5912
842.6562 | 121.6553 | -4.7287 | 116.954 | -0.024795 | 0.015127 | 0.0074875 | 0.010861 | 0.055822 | -0.0084765 | 0.063617 | -4.6875 | 116.5466 | -4.6783 | -4.66 | 116.3132 | 1.474 | 0.082397 | 0.041199 | 116.8671 | -4.7379 | 0.050354 | -0.40741 | 0.041199 | 0.068665 | -0.64087 | -0.009155 | -0.086976 | -0.009155 | 4.8111 | 4.7699 | 121.0419 | 121.2753 | 0.041199 | 121.5958 | 6.2027 | -0.009155 | 121.2753 | 0.041199 | 6.2027 | 121.0419 | 121.5958 | -121.6324 | -121.6919
844.4062 | 121.6553 | -4.8523 | 116.7984 | -0.16212 | 0.014913 | 0.0042831 | 0.0089381 | 0.056035 | -0.010826 | 0.064044 | -4.834 | 116.5054 | -4.7791 | -4.8019 | 116.2079 | 1.6159 | 0.42572 | 0.31586 | 116.7709 | -4.8477 | 0.073242 | -0.29297 | 0.018311 | 0.050354 | -0.59051 | 0.004578 | -0.027466 | -0.054931 | 5.278 | 5.1682 | 121.0602 | 121.3577 | 0.018311 | 121.6232 | 6.4682 | 0.004578 | 121.3577 | 0.018311 | 6.4682 | 121.0602 | 121.6232 | -121.5775 | -121.6461
846.1406 | 121.7651 | -4.7424 | 116.7984 | 0.15068 | 0.014913 | 0.011546 | 0.0091517 | 0.057104 | -0.0076221 | 0.065112 | -4.8203 | 116.5375 | -4.7287 | -4.7928 | 116.2079 | 1.3275 | -0.12817 | -0.25177 | 116.8121 | -4.8157 | 0.013733 | -0.26093 | -0.077819 | -0.050354 | -0.59051 | -0.073242 | 0.013733 | -0.091552 | 4.6143 | 4.4907 | 120.9503 | 121.2799 | -0.077819 | 121.5546 | 6.0699 | -0.073242 | 121.2799 | -0.077819 | 6.0699 | 120.9503 | 121.5546 | -121.5271 | -121.6141
847.8906 | 121.7102 | -4.5547 | 117.0456 | 0.15068 | 0.015127 | 0.0089829 | 0.0057337 | 0.057104 | -0.0082629 | 0.063403 | -4.4769 | 116.7572 | -4.4449 | -4.4495 | 116.5375 | 1.3733 | -0.28381 | -0.12817 | 117.009 | -4.5639 | 0.10986 | -0.28839 | 0.07782 | 0.10529 | -0.50812 | -0.009155 | -0.036621 | -0.032044 | 4.2709 | 4.4266 | 121.0922 | 121.312 | 0.07782 | 121.5637 | 5.928 | -0.009155 | 121.312 | 0.07782 | 5.928 | 121.0922 | 121.5637 | -121.4905 | -121.6095
849.5781 | 121.7194 | -4.5364 | 117.0639 | 0.13542 | 0.014699 | 0.0057785 | 0.0068017 | 0.059026 | -0.0095447 | 0.06554 | -4.4312 | 116.7618 | -4.4312 | -4.4037 | 116.5787 | 1.3916 | -0.27466 | -0.07782 | 117.0593 | -4.5136 | 0.10529 | -0.30212 | 0.10529 | 0.13275 | -0.48523 | 0.022888 | -0.004578 | 0 | 4.2618 | 4.4586 | 121.1151 | 121.2982 | 0.10529 | 121.5958 | 5.928 | 0.022888 | 121.2982 | 0.10529 | 5.928 | 121.1151 | 121.5958 | -121.4951 | -121.5775
851.3281 | 121.7102 | -3.8956 | 117.7368 | 0.19646 | 0.01235 | 0.010051 | 0.0046655 | 0.056676 | -0.0078357 | 0.061267 | -3.7949 | 117.3752 | -3.8086 | -3.9413 | 115.2466 | -0.76904 | -2.1652 | -1.0117 | 116.3361 | -5.0491 | 0.086975 | -0.36163 | 0.10071 | -0.045776 | -2.4902 | -1.1536 | -1.4008 | 0.013733 | 1.7303 | 2.8839 | 119.1422 | 121.2708 | 0.10071 | 120.2316 | 3.1265 | -1.1536 | 121.2708 | 0.10071 | 3.1265 | 119.1422 | 120.2316 | -121.5454 | -122.7859
853.0156 | 121.6644 | -6.6971 | 114.9399 | -0.16975 | 0.014272 | 0.0087693 | 0.0068017 | 0.053686 | -0.0097583 | 0.064685 | -3.2959 | 117.9337 | -3.3371 | -3.3096 | 117.6544 | 1.9958 | 0.80109 | 0.6958 | 118.2404 | -3.3875 | 3.36 | 2.9938 | 3.4012 | 3.3875 | 2.7145 | 3.3096 | 3.3005 | 0.041199 | 7.4982 | 7.3929 | 124.3515 | 124.6307 | 3.4012 | 124.9374 | 8.6929 | 3.3096 | 124.6307 | 3.4012 | 8.6929 | 124.3515 | 124.9374 | -118.277 | -118.3273
854.7812 | 121.7651 | -2.1378 | 119.4992 | 0.0057222 | 0.015554 | 0.0085555 | 0.0053065 | 0.055395 | -0.0050585 | 0.062549 | -2.0599 | 119.1834 | -2.037 | -2.0508 | 118.927 | 1.6205 | 0.24261 | 0.3479 | 119.4672 | -2.1332 | 0.10071 | -0.31586 | 0.077819 | 0.086975 | -0.5722 | 0.004577 | -0.032044 | -0.022889 | 2.3804 | 2.4857 | 121.0648 | 121.3211 | 0.077819 | 121.6049 | 3.7582 | 0.004577 | 121.3211 | 0.077819 | 3.7582 | 121.0648 | 121.6049 | -121.5363 | -121.6324
856.4688 | 121.7606 | -5.7632 | 116.6656 | -0.0095368 | 0.015981 | 0.0062057 | 0.0033839 | 0.055608 | -0.0063403 | 0.065326 | -6.5872 | 115.3702 | -5.3604 | -4.4174 | 116.5787 | 2.4216 | -1.2177 | -2.3758 | 114.949 | -5.9601 | 0.40283 | -1.2955 | -0.82397 | 1.3458 | -0.086975 | -0.19684 | -1.7166 | -1.2268 | 4.5456 | 3.3875 | 122.3419 | 121.1334 | -0.82397 | 120.7123 | 8.1848 | -0.19684 | 121.1334 | -0.82397 | 8.1848 | 122.3419 | 120.7123 | -122.0261 | -122.6257
858.2188 | 121.6553 | -1.2543 | 120.4559 | 0.013352 | 0.015554 | 0.012615 | 0.011501 | 0.05454 | -0.011254 | 0.06319 | -1.149 | 120.1355 | -1.1307 | -1.149 | 119.7876 | 1.561 | 0.050354 | -0.050354 | 120.4147 | -1.2405 | 0.1236 | -0.32044 | 0.10529 | 0.10529 | -0.66833 | 0.013732 | -0.041199 | -0.018311 | 1.3046 | 1.2039 | 121.0419 | 121.3898 | 0.10529 | 121.669 | 2.8152 | 0.013732 | 121.3898 | 0.10529 | 2.8152 | 121.0419 | 121.669 | -121.5866 | -121.6965
859.9688 | 121.6827 | -37.1658 | 84.8511 | -0.12398 | 0.014272 | 0.0072739 | 0.0044519 | 0.054326 | -0.0069811 | 0.064258 | -36.6898 | 84.8923 | -36.3327 | -36.7538 | 84.7046 | -3.0945 | -1.6296 | -0.7782 | 84.7412 | -36.5295 | 0.83313 | 0.041199 | 0.47608 | 0.41199 | -0.14648 | 0.63629 | -0.10986 | -0.35705 | 35.5362 | 36.3876 | 121.8704 | 122.0581 | 0.47608 | 121.907 | 34.0714 | 0.63629 | 122.0581 | 0.47608 | 34.0714 | 121.8704 | 121.907 | -121.1838 | -121.3806
861.6562 | 121.6278 | -0.89264 | 120.7993 | -0.19264 | 0.015981 | 0.0074875 | 0.0057337 | 0.055395 | -0.0091173 | 0.063617 | -0.76446 | 120.4971 | -0.75989 | -0.78278 | 120.1584 | 1.8219 | 0.6134 | 0.52185 | 120.7764 | -0.87891 | 0.13275 | -0.30212 | 0.12817 | 0.10986 | -0.64087 | 0.013733 | -0.022888 | -0.004577 | 1.506 | 1.4145 | 121.051 | 121.3898 | 0.12817 | 121.669 | 2.7145 | 0.013733 | 121.3898 | 0.12817 | 2.7145 | 121.051 | 121.669 | -121.5591 | -121.6782
863.4062 | 121.7468 | -0.82398 | 120.7901 | 0.059128 | 0.016195 | 0.0038559 | 0.0050929 | 0.055181 | -0.0061267 | 0.065967 | -0.74158 | 120.5063 | -0.72327 | -0.73242 | 120.2316 | 1.5701 | 0.086975 | 0.1831 | 120.7901 | -0.83771 | 0.10071 | -0.28381 | 0.082398 | 0.091553 | -0.55847 | -0.013733 | 0 | -0.01831 | 0.91095 | 1.0071 | 121.0556 | 121.3303 | 0.082398 | 121.6141 | 2.3941 | -0.013733 | 121.3303 | 0.082398 | 2.3941 | 121.0556 | 121.6141 | -121.5134 | -121.6278
865.1719 | 121.7422 | -1.1444 | 120.4468 | 0.12016 | 0.015767 | 0.0070603 | 0.011288 | 0.055395 | -0.0071947 | 0.064258 | -1.1307 | 120.195 | -1.0666 | -1.1215 | 119.8288 | 1.4603 | -0.091553 | -0.21973 | 120.4926 | -1.1719 | 0.07782 | -0.25177 | 0.013733 | 0.022888 | -0.61798 | -0.027466 | 0.045777 | -0.064087 | 1.0529 | 0.92468 | 120.9732 | 121.3394 | 0.013733 | 121.637 | 2.6047 | -0.027466 | 121.3394 | 0.013733 | 2.6047 | 120.9732 | 121.637 | -121.5134 | -121.6187
866.9219 | 121.6782 | -1.181 | 120.4926 | -0.21553 | 0.014913 | 0.0062057 | 0.0087243 | 0.054967 | -0.0086901 | 0.06554 | -1.149 | 120.1996 | -1.1032 | -1.1215 | 119.8471 | 1.767 | 0.57678 | 0.40741 | 120.4651 | -1.1948 | 0.07782 | -0.29297 | 0.032043 | 0.059509 | -0.64545 | -0.013733 | -0.027466 | -0.045777 | 1.7578 | 1.5884 | 121.0281 | 121.3806 | 0.032043 | 121.6461 | 2.948 | -0.013733 | 121.3806 | 0.032043 | 2.948 | 121.0281 | 121.6461 | -121.5958 | -121.6873
868.6094 | 121.7285 | -1.2451 | 120.3644 | 0.12016 | 0.016408 | 0.0081283 | 0.0048791 | 0.055822 | -0.0069811 | 0.063831 | -1.1261 | 120.076 | -1.1536 | -1.1261 | 119.8196 | 1.5427 | -0.091553 | 0.073242 | 120.3323 | -1.2451 | 0.091553 | -0.28839 | 0.11902 | 0.11902 | -0.54474 | 0 | -0.032044 | 0.027465 | 1.1536 | 1.3184 | 121.0648 | 121.3211 | 0.11902 | 121.5775 | 2.7878 | 0 | 121.3211 | 0.11902 | 2.7878 | 121.0648 | 121.5775 | -121.5179 | -121.6095
870.3594 | 121.6827 | -0.78278 | 120.8817 | 0.13542 | 0.01534 | 0.0096237 | 0.012356 | 0.056463 | -0.0084765 | 0.065112 | -0.72327 | 120.5658 | -0.68665 | -0.71411 | 120.2408 | 1.5564 | 0.032043 | -0.10986 | 120.9137 | -0.76446 | 0.09613 | -0.31586 | 0.059509 | 0.068665 | -0.64087 | 0.018311 | 0.032043 | -0.036621 | 0.81482 | 0.67291 | 121.0236 | 121.3486 | 0.059509 | 121.6965 | 2.3392 | 0.018311 | 121.3486 | 0.059509 | 2.3392 | 121.0236 | 121.6965 | -121.5683 | -121.6461
872.1094 | 121.701 | -0.50354 | 121.138 | 0.15831 | 0.010427 | 0.0083419 | 0.0057337 | 0.058385 | -0.0093311 | 0.064258 | -0.38452 | 120.7901 | -0.3891 | -0.35706 | 120.6024 | 1.5747 | -0.25177 | -0.045776 | 121.1197 | -0.4715 | 0.11444 | -0.3479 | 0.11902 | 0.14648 | -0.53558 | 0.032043 | -0.01831 | 0.004578 | 0.25177 | 0.45776 | 121.106 | 121.2936 | 0.11902 | 121.6232 | 2.0782 | 0.032043 | 121.2936 | 0.11902 | 2.0782 | 121.106 | 121.6232 | -121.5271 | -121.6095
873.7969 | 121.7377 | -0.66834 | 120.9412 | 0.059128 | 0.015554 | 0.0083419 | 0.010433 | 0.055822 | -0.0082629 | 0.065112 | -0.67749 | 120.6482 | -0.62714 | -0.67749 | 120.282 | 1.5244 | 0 | -0.16022 | 120.9778 | -0.72327 | 0.041199 | -0.29297 | -0.009155 | -0.009155 | -0.65918 | -0.054932 | 0.036621 | -0.050354 | 0.66834 | 0.50812 | 120.9503 | 121.3165 | -0.009155 | 121.6461 | 2.1927 | -0.054932 | 121.3165 | -0.009155 | 2.1927 | 120.9503 | 121.6461 | -121.5683 | -121.6644
875.5469 | 121.6827 | -0.77362 | 120.9229 | -0.21553 | 0.014699 | 0.0053513 | 0.0046655 | 0.052404 | -0.0078357 | 0.064899 | -0.70496 | 120.5933 | -0.64087 | -0.68207 | 120.282 | 1.8036 | 0.59967 | 0.50812 | 120.8771 | -0.75073 | 0.13275 | -0.32959 | 0.068665 | 0.091553 | -0.64087 | 0.022889 | -0.045777 | -0.064087 | 1.3733 | 1.2817 | 121.0556 | 121.3669 | 0.068665 | 121.6507 | 2.5772 | 0.022889 | 121.3669 | 0.068665 | 2.5772 | 121.0556 | 121.6507 | -121.5637 | -121.6736
877.2969 | 121.7834 | -0.59052 | 121.0007 | 0.03624 | 0.014272 | 0.0023605 | 0.0027429 | 0.055395 | -0.0086901 | 0.064258 | -0.50812 | 120.7306 | -0.48981 | -0.49896 | 120.4559 | 1.6022 | 0.11902 | 0.18768 | 121.0144 | -0.58136 | 0.10071 | -0.27008 | 0.082397 | 0.091553 | -0.54474 | 0.009155 | 0.013733 | -0.018311 | 0.70953 | 0.7782 | 121.0464 | 121.3211 | 0.082397 | 121.6049 | 2.1927 | 0.009155 | 121.3211 | 0.082397 | 2.1927 | 121.0464 | 121.6049 | -121.4905 | -121.582
879.0469 | 121.669 | -0.59052 | 121.106 | -0.16975 | 0.011922 | 0.0049241 | 0.0080835 | 0.054967 | -0.0076221 | 0.064044 | -0.52643 | 120.7855 | -0.49896 | -0.49896 | 120.4468 | 1.7899 | 0.50354 | 0.37079 | 121.0876 | -0.58594 | 0.091553 | -0.32044 | 0.064087 | 0.091553 | -0.65918 | 0.004578 | -0.018311 | -0.027466 | 1.0941 | 0.9613 | 121.0373 | 121.376 | 0.064087 | 121.6782 | 2.3804 | 0.004578 | 121.376 | 0.064087 | 2.3804 | 121.0373 | 121.6782 | -121.6049 | -121.6919
880.75 | 121.6415 | -0.5722 | 121.1288 | -0.032425 | 0.013418 | 0.0068467 | 0.0093653 | 0.053899 | -0.0086901 | 0.064685 | -0.59052 | 120.7489 | -0.51727 | -0.61798 | 120.3598 | 1.6067 | 0.10986 | 0.068665 | 121.0281 | -0.62256 | 0.054932 | -0.37994 | -0.01831 | -0.045776 | -0.76904 | -0.050354 | -0.10071 | -0.073242 | 0.68207 | 0.64087 | 120.932 | 121.3211 | -0.01831 | 121.6003 | 2.179 | -0.050354 | 121.3211 | -0.01831 | 2.179 | 120.932 | 121.6003 | -121.6461 | -121.7514
882.5 | 121.7102 | -0.48065 | 121.17 | 0.15068 | 0.012563 | 0.0094101 | 0.0074427 | 0.057317 | -0.0082629 | 0.064471 | -0.31586 | 120.8405 | -0.33875 | -0.31586 | 120.639 | 1.5884 | -0.2655 | -0.050354 | 121.1472 | -0.46234 | 0.14191 | -0.32959 | 0.1648 | 0.1648 | -0.53101 | 0.018311 | -0.022888 | 0.022888 | 0.21515 | 0.4303 | 121.1197 | 121.3211 | 0.1648 | 121.6278 | 2.0691 | 0.018311 | 121.3211 | 0.1648 | 2.0691 | 121.1197 | 121.6278 | -121.5088 | -121.6324
884.1719 | 121.6919 | -0.63629 | 121.0327 | -0.18501 | 0.014058 | 0.0077011 | 0.0080835 | 0.053686 | -0.0071947 | 0.064471 | -0.70038 | 120.694 | -0.5722 | -0.64087 | 120.3369 | 1.7899 | 0.58136 | 0.42572 | 121.0098 | -0.68665 | 0.064087 | -0.33875 | -0.064086 | -0.004577 | -0.6958 | -0.050354 | -0.022888 | -0.12817 | 1.2177 | 1.062 | 120.9732 | 121.3303 | -0.064086 | 121.6461 | 2.4261 | -0.050354 | 121.3303 | -0.064086 | 2.4261 | 120.9732 | 121.6461 | -121.6049 | -121.7194
885.9219 | 121.7056 | -1.0162 | 120.639 | -0.085831 | 0.013418 | 0.0062057 | 0.0029565 | 0.053258 | -0.0061267 | 0.063617 | -0.8606 | 120.3186 | -0.90637 | -0.79651 | 120.1584 | 1.7899 | 0.33417 | 0.52643 | 120.6162 | -0.97504 | 0.10986 | -0.32043 | 0.15564 | 0.21973 | -0.48065 | 0.041198 | -0.022888 | 0.045776 | 1.3504 | 1.5427 | 121.1746 | 121.3348 | 0.15564 | 121.6324 | 2.8061 | 0.041198 | 121.3348 | 0.15564 | 2.8061 | 121.1746 | 121.6324 | -121.5454 | -121.6141
887.6094 | 121.7194 | -0.46234 | 121.1792 | -0.070572 | 0.014913 | 0.0036423 | 0.0040247 | 0.054754 | -0.0071947 | 0.062549 | -0.35248 | 120.8679 | -0.33875 | -0.32501 | 120.6528 | 2.0187 | 0.32044 | 0.47607 | 121.1563 | -0.46234 | 0.1236 | -0.31128 | 0.10986 | 0.13733 | -0.52643 | 0 | -0.022888 | -0.013733 | 0.78278 | 0.93841 | 121.1151 | 121.3303 | 0.10986 | 121.6187 | 2.4811 | 0 | 121.3303 | 0.10986 | 2.4811 | 121.1151 | 121.6187 | -121.5179 | -121.6415
889.3594 | 121.6278 | -0.64545 | 121.0556 | -0.085831 | 0.015127 | 0.0042831 | 0.011715 | 0.055822 | -0.0093311 | 0.062763 | -0.54016 | 120.7077 | -0.54474 | -0.52643 | 120.4147 | 1.8127 | 0.28839 | 0.24719 | 121.0464 | -0.63171 | 0.10071 | -0.3479 | 0.10529 | 0.11902 | -0.64087 | 0.013733 | -0.009155 | 0.004578 | 0.93384 | 0.89264 | 121.0602 | 121.3531 | 0.10529 | 121.6919 | 2.4582 | 0.013733 | 121.3531 | 0.10529 | 2.4582 | 121.0602 | 121.6919 | -121.6003 | -121.6873
891.1094 | 121.6827 | -0.74616 | 120.8908 | -0.078201 | 0.013418 | 0.0032151 | 0.0050929 | 0.054326 | -0.0078357 | 0.06554 | -0.64087 | 120.5521 | -0.64087 | -0.58594 | 120.4056 | 1.8631 | 0.3479 | 0.51727 | 120.8908 | -0.70038 | 0.10529 | -0.33875 | 0.10529 | 0.16022 | -0.48523 | 0.045777 | 0 | 0 | 1.0941 | 1.2634 | 121.1517 | 121.2982 | 0.10529 | 121.637 | 2.6093 | 0.045777 | 121.2982 | 0.10529 | 2.6093 | 121.1517 | 121.637 | -121.5317 | -121.5912
892.8125 | 121.637 | -0.76446 | 120.9183 | -0.18501 | 0.014699 | 0.0074875 | 0.0046655 | 0.056249 | -0.0071947 | 0.065112 | -0.66376 | 120.5154 | -0.65918 | -0.55389 | 120.3735 | 1.8814 | 0.41199 | 0.54474 | 120.8221 | -0.76904 | 0.10528 | -0.40283 | 0.10071 | 0.21057 | -0.54474 | -0.004578 | -0.09613 | -0.004577 | 1.1765 | 1.3092 | 121.138 | 121.2799 | 0.10071 | 121.5866 | 2.6459 | -0.004578 | 121.2799 | 0.10071 | 2.6459 | 121.138 | 121.5866 | -121.5775 | -121.6873
894.5625 | 121.7377 | -0.86517 | 120.7306 | 0.12016 | 0.014486 | 0.013042 | 0.0085107 | 0.055822 | -0.0063403 | 0.06618 | -0.73242 | 120.4559 | -0.75989 | -0.74616 | 120.1859 | 1.7166 | -0.045776 | 0.10071 | 120.7352 | -0.85144 | 0.10528 | -0.27466 | 0.13275 | 0.11902 | -0.54474 | 0.013733 | 0.004577 | 0.027466 | 0.8194 | 0.96588 | 121.051 | 121.3211 | 0.13275 | 121.6003 | 2.5818 | 0.013733 | 121.3211 | 0.13275 | 2.5818 | 121.051 | 121.6003 | -121.4905 | -121.582
896.25 | 121.6827 | -0.55847 | 121.0327 | 0.19646 | 0.013204 | 0.010265 | 0.0082971 | 0.05454 | -0.0065539 | 0.065112 | -0.37537 | 120.7764 | -0.43488 | -0.39368 | 120.5292 | 1.6434 | -0.16937 | 0.022888 | 121.0648 | -0.50812 | 0.1236 | -0.25635 | 0.18311 | 0.16479 | -0.50354 | 0.050354 | 0.032043 | 0.059509 | 0.3891 | 0.58136 | 121.0876 | 121.3348 | 0.18311 | 121.6232 | 2.2018 | 0.050354 | 121.3348 | 0.18311 | 2.2018 | 121.0876 | 121.6232 | -121.4676 | -121.5408
897.9844 | 121.6095 | -3.2547 | 118.3456 | -0.21553 | 0.014699 | 0.0085555 | 0.0068017 | 0.052404 | -0.0063403 | 0.062335 | -3.2318 | 117.9062 | -3.273 | -3.2089 | 117.7185 | 1.5701 | 0.3891 | 0.5722 | 118.1351 | -3.3371 | -0.01831 | -0.43945 | 0.022888 | 0.045777 | -0.62714 | -0.082397 | -0.21057 | 0.041198 | 3.6438 | 3.8269 | 120.9732 | 121.1609 | 0.022888 | 121.3898 | 4.8248 | -0.082397 | 121.1609 | 0.022888 | 4.8248 | 120.9732 | 121.3898 | -121.6187 | -121.6827
899.6875 | 121.6919 | -98.8403 | 22.4854 | -0.13161 | 0.01235 | 0.0030013 | 0.010647 | 0.057958 | -0.0091173 | 0.064471 | -98.2681 | 22.9111 | -98.3597 | -98.4055 | 22.9523 | -7.2144 | -0.67749 | -0.82855 | 22.9935 | -98.5382 | 0.48065 | 0.42572 | 0.5722 | 0.43488 | 0.46692 | 0.30212 | 0.50812 | 0.091553 | 98.1628 | 98.0118 | 121.7926 | 121.7514 | 0.5722 | 121.8338 | 91.626 | 0.30212 | 121.7514 | 0.5722 | 91.626 | 121.7926 | 121.8338 | -120.845 | -121.0236
901.4531 | 121.701 | -109.758 | 11.7004 | -0.10872 | 0.01235 | 0.0053513 | 0.0046655 | 0.058385 | -0.0078357 | 0.067035 | -109.5383 | 11.5128 | -109.6848 | -109.5978 | 11.792 | -1.4099 | -0.036621 | 0.19226 | 11.6318 | -109.8724 | 0.073243 | -0.18768 | 0.21973 | 0.16022 | 0.091553 | -0.11444 | -0.068664 | 0.14648 | 109.7214 | 109.9503 | 121.55 | 121.2708 | 0.21973 | 121.3898 | 108.3481 | -0.11444 | 121.2708 | 0.21973 | 108.3481 | 121.55 | 121.3898 | -121.3852 | -121.5729
903.2031 | 121.669 | -110.8475 | 10.6155 | -0.070572 | 0.014486 | 0.0091965 | 0.011288 | 0.057317 | -0.0089037 | 0.064471 | -110.6918 | 10.4736 | -110.8337 | -110.7651 | 10.5927 | -1.2955 | -0.07782 | -0.082397 | 10.5743 | -110.9665 | 0.013733 | -0.14191 | 0.15564 | 0.082397 | -0.022889 | -0.11902 | -0.041199 | 0.14191 | 110.7697 | 110.7651 | 121.4401 | 121.3211 | 0.15564 | 121.4218 | 109.552 | -0.11902 | 121.3211 | 0.15564 | 109.552 | 121.4401 | 121.4218 | -121.4493 | -121.582
904.9688 | 121.8063 | -111.3281 | 10.1028 | 0.12779 | 0.011495 | 0.011333 | 0.0027429 | 0.056676 | -0.0074085 | 0.065753 | -111.2045 | 9.9289 | -111.2961 | -111.2915 | 10.1212 | -1.4191 | -0.42572 | -0.23804 | 10.025 | -111.4975 | 0.032043 | -0.17395 | 0.1236 | 0.036621 | 0.018311 | -0.16937 | -0.07782 | 0.091553 | 110.9024 | 111.0901 | 121.4493 | 121.257 | 0.1236 | 121.3531 | 109.9091 | -0.16937 | 121.257 | 0.1236 | 109.9091 | 121.4493 | 121.3531 | -121.3989 | -121.6003
906.6562 | 121.8475 | -111.6394 | 9.7916 | 0.043869 | 0.013845 | 0.0074875 | 0.0033839 | 0.053686 | -0.0067675 | 0.067462 | -111.5341 | 9.6359 | -111.5982 | -111.6119 | 9.8099 | -1.3229 | -0.20599 | -0.09613 | 9.7504 | -111.8042 | 0.041198 | -0.15564 | 0.10528 | 0.027466 | 0.01831 | -0.16479 | -0.041199 | 0.064087 | 111.4334 | 111.5433 | 121.4493 | 121.2753 | 0.10528 | 121.3898 | 110.3165 | -0.16479 | 121.2753 | 0.10528 | 110.3165 | 121.4493 | 121.3898 | -121.3898 | -121.5958
908.4062 | 121.7239 | -111.8042 | 9.7137 | -0.13161 | 0.012563 | 0.0034287 | 0.0046655 | 0.053686 | -0.0056995 | 0.065753 | -111.5982 | 9.5398 | -111.7126 | -111.6714 | 9.7412 | -1.0757 | 0.027466 | 0.25177 | 9.6085 | -111.9644 | 0.091553 | -0.17395 | 0.20599 | 0.13275 | 0.027466 | -0.16022 | -0.10529 | 0.11444 | 111.8317 | 112.056 | 121.5454 | 121.344 | 0.20599 | 121.4127 | 110.7285 | -0.16022 | 121.344 | 0.20599 | 110.7285 | 121.5454 | 121.4127 | -121.4264 | -121.6782
910.0938 | 121.7468 | -111.9919 | 9.4666 | -0.2079 | 0.014058 | 0.012615 | 0.0070155 | 0.054326 | -0.0069811 | 0.064258 | -111.8912 | 9.3796 | -111.9461 | -111.9736 | 9.4208 | -1.0803 | 0.23346 | 0.11444 | 9.4849 | -112.1613 | 0.045776 | -0.086975 | 0.10071 | 0.01831 | -0.045777 | -0.16937 | 0.01831 | 0.054932 | 112.2253 | 112.1063 | 121.4127 | 121.3715 | 0.10071 | 121.4767 | 110.9116 | -0.16937 | 121.3715 | 0.10071 | 110.9116 | 121.4127 | 121.4767 | -121.4127 | -121.6278
911.8438 | 121.6827 | -111.9415 | 9.581 | -0.09346 | 0.012777 | 0.0070603 | 0.010433 | 0.055822 | -0.0071947 | 0.066608 | -111.7722 | 9.4437 | -111.882 | -111.8317 | 9.5444 | -1.0574 | 0.013733 | 0 | 9.5398 | -112.0651 | 0.059509 | -0.13733 | 0.16937 | 0.10986 | -0.036621 | -0.1236 | -0.041199 | 0.10986 | 111.9553 | 111.9415 | 121.4859 | 121.3852 | 0.16937 | 121.4813 | 110.8841 | -0.1236 | 121.3852 | 0.16937 | 110.8841 | 121.4859 | 121.4813 | -121.463 | -121.6461
913.5938 | 121.7834 | -112.0148 | 9.4437 | 0.17357 | 0.011922 | 0.0089829 | 0.0076563 | 0.056676 | -0.0078357 | 0.067462 | -111.8912 | 9.3018 | -111.9553 | -111.9598 | 9.4437 | -1.3 | -0.54474 | -0.39368 | 9.3933 | -112.1933 | 0.05951 | -0.14191 | 0.1236 | 0.054932 | 0 | -0.17853 | -0.050354 | 0.064087 | 111.47 | 111.6211 | 121.4584 | 121.3165 | 0.1236 | 121.4081 | 110.7147 | -0.17853 | 121.3165 | 0.1236 | 110.7147 | 121.4584 | 121.4081 | -121.3989 | -121.637
915.3438 | 121.7285 | -111.9049 | 9.5856 | -0.17738 | 0.014486 | 0.0077011 | 0.0061609 | 0.056463 | -0.0069811 | 0.06319 | -111.8683 | 9.3933 | -111.8866 | -111.9415 | 9.4849 | -1.0437 | 0.3067 | 0.20599 | 9.5261 | -112.0972 | 0.01831 | -0.19226 | 0.036621 | -0.036621 | -0.10071 | -0.19226 | -0.059509 | 0.018311 | 112.2116 | 112.1109 | 121.3898 | 121.2982 | 0.036621 | 121.431 | 110.8612 | -0.19226 | 121.2982 | 0.036621 | 110.8612 | 121.3898 | 121.431 | -121.4722 | -121.6827
917.0938 | 121.701 | -111.9324 | 9.5901 | -0.024795 | 0.012563 | 0.0079147 | 0.010647 | 0.058812 | -0.0095447 | 0.066608 | -111.7905 | 9.4437 | -111.8774 | -111.8912 | 9.5444 | -1.1948 | -0.23346 | -0.29297 | 9.5352 | -112.0605 | 0.054932 | -0.14648 | 0.14191 | 0.041199 | -0.045776 | -0.12817 | -0.054932 | 0.086975 | 111.6989 | 111.6394 | 121.4767 | 121.376 | 0.14191 | 121.4676 | 110.7376 | -0.12817 | 121.376 | 0.14191 | 110.7376 | 121.4767 | 121.4676 | -121.4676 | -121.6507
918.8438 | 121.6827 | -111.8729 | 9.668 | -0.078201 | 0.014913 | 0.0057785 | 0.0085107 | 0.056249 | -0.0093311 | 0.064471 | -111.6852 | 9.5261 | -111.7676 | -111.7813 | 9.6451 | -1.0712 | -0.045776 | -0.050354 | 9.6039 | -112.0285 | 0.10529 | -0.14191 | 0.18768 | 0.091553 | -0.022888 | -0.15564 | -0.064087 | 0.082397 | 111.8271 | 111.8225 | 121.5179 | 121.3989 | 0.18768 | 121.4767 | 110.8017 | -0.15564 | 121.3989 | 0.18768 | 110.8017 | 121.5179 | 121.4767 | -121.4355 | -121.6965
920.5469 | 121.8155 | -111.6852 | 9.7595 | 0.11253 | 0.013845 | 0.0079147 | 0.0074427 | 0.057744 | -0.0061267 | 0.065753 | -111.6486 | 9.6222 | -111.6989 | -111.7447 | 9.6909 | -1.3138 | -0.47607 | -0.4715 | 9.7183 | -111.8774 | -0.013733 | -0.13733 | 0.036621 | -0.059509 | -0.068664 | -0.19226 | -0.041198 | 0.050354 | 111.2091 | 111.2137 | 121.376 | 121.3074 | 0.036621 | 121.4035 | 110.3714 | -0.19226 | 121.3074 | 0.036621 | 110.3714 | 121.376 | 121.4035 | -121.4584 | -121.637
922.2969 | 121.7789 | -111.6852 | 9.7961 | 0.15068 | 0.013845 | 0.0098373 | 0.0048791 | 0.05689 | -0.0052721 | 0.065112 | -111.5112 | 9.5993 | -111.5936 | -111.6028 | 9.8465 | -1.2177 | -0.47607 | -0.24261 | 9.7366 | -111.8454 | 0.091553 | -0.19684 | 0.17395 | 0.082398 | 0.050354 | -0.16022 | -0.05951 | 0.082398 | 111.2091 | 111.4426 | 121.5317 | 121.2845 | 0.17395 | 121.4218 | 110.4675 | -0.16022 | 121.2845 | 0.17395 | 110.4675 | 121.5317 | 121.4218 | -121.3898 | -121.6415
923.9844 | 121.6736 | -111.9965 | 9.5535 | -0.11635 | 0.012136 | 0.0036423 | 0.0087243 | 0.055181 | -0.0084765 | 0.064685 | -111.8408 | 9.3796 | -111.937 | -111.937 | 9.494 | -1.0254 | 0.022888 | 0.009155 | 9.4803 | -112.1384 | 0.059509 | -0.17395 | 0.15564 | 0.059509 | -0.059509 | -0.14191 | -0.073242 | 0.096131 | 112.0193 | 112.0056 | 121.4905 | 121.376 | 0.15564 | 121.4767 | 110.9711 | -0.14191 | 121.376 | 0.15564 | 110.9711 | 121.4905 | 121.4767 | -121.4905 | -121.6919
925.7344 | 121.701 | -112.1979 | 9.3384 | -0.10109 | 0.014272 | 0.0023605 | 0.0016749 | 0.054754 | -0.0054859 | 0.065967 | -111.9919 | 9.1599 | -112.0605 | -112.0422 | 9.4116 | -0.9613 | 0.086975 | 0.31128 | 9.2606 | -112.3352 | 0.13733 | -0.17853 | 0.20599 | 0.15564 | 0.073242 | -0.13733 | -0.07782 | 0.068665 | 112.2849 | 112.5092 | 121.6095 | 121.3577 | 0.20599 | 121.4584 | 111.2366 | -0.13733 | 121.3577 | 0.20599 | 111.2366 | 121.6095 | 121.4584 | -121.3989 | -121.6736
927.4844 | 121.6873 | -112.3123 | 9.2011 | -0.078201 | 0.014913 | 0.0059921 | 0.010006 | 0.056249 | -0.0080493 | 0.06554 | -112.1567 | 9.0683 | -112.3032 | -112.2299 | 9.2011 | -1.0803 | -0.11444 | -0.10071 | 9.1644 | -112.4313 | 0.009155 | -0.13275 | 0.15564 | 0.082398 | 0 | -0.11902 | -0.036621 | 0.14648 | 112.1979 | 112.2116 | 121.5134 | 121.3806 | 0.15564 | 121.4767 | 111.232 | -0.11902 | 121.3806 | 0.15564 | 111.232 | 121.5134 | 121.4767 | -121.5042 | -121.6324
929.2344 | 121.6644 | -112.4222 | 9.1324 | -0.085831 | 0.012136 | 0.0079147 | 0.0087243 | 0.057317 | -0.0095447 | 0.065967 | -112.2482 | 8.9676 | -112.3489 | -112.3306 | 9.1141 | -1.0483 | -0.059509 | -0.041199 | 9.0637 | -112.5183 | 0.073242 | -0.16479 | 0.17395 | 0.091553 | -0.01831 | -0.096131 | -0.068664 | 0.10071 | 112.3627 | 112.381 | 121.5363 | 121.3898 | 0.17395 | 121.4859 | 111.3739 | -0.096131 | 121.3898 | 0.17395 | 111.3739 | 121.5363 | 121.4859 | -121.4813 | -121.6507
930.9844 | 121.8109 | -112.2345 | 9.2331 | 0.12016 | 0.014486 | 0.0040695 | 0.0070155 | 0.058599 | -0.0065539 | 0.066608 | -112.2345 | 9.0683 | -112.2711 | -112.3306 | 9.1095 | -1.2772 | -0.37994 | -0.45319 | 9.1827 | -112.4817 | -0.036621 | -0.16479 | 0 | -0.09613 | -0.1236 | -0.24719 | -0.050354 | 0.036621 | 111.8546 | 111.7813 | 121.344 | 121.3028 | 0 | 121.4172 | 110.9573 | -0.24719 | 121.3028 | 0 | 110.9573 | 121.344 | 121.4172 | -121.5042 | -121.7148
932.6719 | 121.7468 | -111.5616 | 9.9792 | -0.20027 | 0.013418 | 0.0055649 | 0.0023157 | 0.053258 | -0.0091173 | 0.065753 | -111.4609 | 9.8373 | -111.5021 | -111.5433 | 9.9243 | -1.0162 | 0.26093 | 0.1236 | 9.9426 | -111.6943 | 0.059509 | -0.14191 | 0.10071 | 0.01831 | -0.054932 | -0.13275 | -0.036621 | 0.041199 | 111.8225 | 111.6852 | 121.4859 | 121.3989 | 0.10071 | 121.5042 | 110.5453 | -0.13275 | 121.3989 | 0.10071 | 110.5453 | 121.4859 | 121.5042 | -121.4813 | -121.6736
934.4219 | 121.7834 | -111.2366 | 10.2722 | 0.082016 | 0.011709 | 0.0077011 | 0.0059473 | 0.05689 | -0.0067675 | 0.067249 | -111.0489 | 10.1303 | -111.113 | -111.0855 | 10.3867 | -1.1261 | -0.44403 | -0.25177 | 10.2722 | -111.3052 | 0.1236 | -0.14191 | 0.18768 | 0.15106 | 0.11444 | -0.068665 | 0 | 0.064087 | 110.7925 | 110.9848 | 121.6232 | 121.3669 | 0.18768 | 121.5088 | 110.1105 | -0.068665 | 121.3669 | 0.18768 | 110.1105 | 121.6232 | 121.5088 | -121.3852 | -121.5775
936.1719 | 121.7972 | -110.9894 | 10.5194 | -0.055313 | 0.012136 | 0.0072739 | 0.00017946 | 0.054754 | -0.0063403 | 0.066608 | -110.8292 | 10.3683 | -110.8978 | -110.9207 | 10.5881 | -0.99792 | 0.018311 | 0.21515 | 10.4645 | -111.1359 | 0.091553 | -0.15106 | 0.16022 | 0.068665 | 0.068665 | -0.14648 | -0.054931 | 0.068664 | 111.0077 | 111.2045 | 121.5775 | 121.3577 | 0.16022 | 121.4539 | 109.9915 | -0.14648 | 121.3577 | 0.16022 | 109.9915 | 121.5775 | 121.4539 | -121.4172 | -121.6553
937.8594 | 121.7422 | -111.6028 | 9.9243 | -0.17738 | 0.014058 | 0.0081283 | 0.0048791 | 0.054113 | -0.0069811 | 0.065112 | -111.4609 | 9.7595 | -111.5341 | -111.5707 | 9.906 | -0.98419 | 0.30212 | 0.24719 | 9.8648 | -111.7538 | 0.068664 | -0.16479 | 0.14191 | 0.032043 | -0.01831 | -0.15106 | -0.059509 | 0.073243 | 111.9049 | 111.85 | 121.5088 | 121.3623 | 0.14191 | 121.4676 | 110.6186 | -0.15106 | 121.3623 | 0.14191 | 110.6186 | 121.5088 | 121.4676 | -121.4584 | -121.6782
939.5938 | 121.6187 | -83.931 | 37.3215 | -0.22316 | 0.013631 | 0.0081283 | 0.0065881 | 0.053899 | -0.0089037 | 0.066608 | -83.2809 | 37.4496 | -83.4915 | -84.4345 | 36.6669 | -0.43945 | 1.0574 | 0.1831 | 37.4725 | -84.1095 | 0.43945 | 0.12817 | 0.65002 | -0.50354 | -0.6546 | -0.17853 | 0.15106 | 0.21057 | 84.9884 | 84.1141 | 120.5978 | 121.3806 | 0.65002 | 121.4035 | 83.4915 | -0.17853 | 121.3806 | 0.65002 | 83.4915 | 120.5978 | 121.4035 | -120.813 | -121.431
941.3438 | 121.582 | -96.7163 | 24.5087 | -0.24605 | 0.015767 | 0.0032151 | 0.0046655 | 0.055181 | -0.0078357 | 0.064258 | -96.9223 | 24.1013 | -96.8216 | -95.6818 | 25.7996 | 0.37537 | -0.064087 | -0.4303 | 25.2319 | -95.993 | -0.10529 | -0.40741 | -0.20599 | 1.0345 | 1.2909 | 0.72327 | 0.72327 | -0.10071 | 96.6522 | 96.286 | 122.5159 | 120.8176 | -0.20599 | 121.9482 | 97.0917 | 0.72327 | 120.8176 | -0.20599 | 97.0917 | 122.5159 | 121.9482 | -121.3303 | -120.5017
943.0312 | 121.4722 | -113.9832 | 7.0404 | 0.1049 | 0.012777 | 0.0053513 | 0.011715 | 0.057104 | -0.0080493 | 0.065967 | -113.9648 | 6.9763 | -114.0244 | -114.0472 | 6.9992 | -1.5015 | -0.40283 | -0.48065 | 7.0724 | -114.1846 | -0.041199 | -0.064087 | 0.01831 | -0.064087 | -0.041198 | -0.20142 | 0.032044 | 0.059509 | 113.5803 | 113.5025 | 120.9824 | 120.9595 | 0.01831 | 121.0556 | 112.4817 | -0.20142 | 120.9595 | 0.01831 | 112.4817 | 120.9824 | 121.0556 | -121.0648 | -121.225
944.7812 | 121.4172 | -114.8666 | 6.1981 | 0.11253 | 0.011922 | 0.0057785 | 0.0070155 | 0.057104 | -0.0082629 | 0.066821 | -114.7705 | 6.0837 | -114.8346 | -114.8621 | 6.134 | -1.4786 | -0.43945 | -0.49896 | 6.1661 | -115.0269 | 0.032043 | -0.11444 | 0.09613 | 0.004577 | -0.064087 | -0.16022 | -0.032043 | 0.064087 | 114.4272 | 114.3677 | 121.0007 | 120.9503 | 0.09613 | 121.0327 | 113.3881 | -0.16022 | 120.9503 | 0.09613 | 113.3881 | 121.0007 | 121.0327 | -121.0327 | -121.225
946.5312 | 121.2296 | -115.2283 | 5.8319 | -0.070572 | 0.012777 | 0.0083419 | 0.01022 | 0.057744 | -0.0078357 | 0.066821 | -115.0543 | 5.6992 | -115.1779 | -115.155 | 5.8044 | -1.2222 | -0.15106 | -0.12817 | 5.7953 | -115.3564 | 0.050354 | -0.13275 | 0.17395 | 0.073242 | -0.027466 | -0.12817 | -0.036621 | 0.1236 | 115.0772 | 115.1001 | 121.0327 | 120.9274 | 0.17395 | 121.0236 | 114.006 | -0.12817 | 120.9274 | 0.17395 | 114.006 | 121.0327 | 121.0236 | -121.0098 | -121.1884
948.2344 | 121.2433 | -115.3839 | 5.658 | -0.20027 | 0.014486 | 0.0051377 | 0.0048791 | 0.055608 | -0.0084765 | 0.064471 | -115.2786 | 5.5023 | -115.3336 | -115.3702 | 5.5847 | -1.1536 | 0.28381 | 0.16937 | 5.6213 | -115.567 | 0.050354 | -0.15564 | 0.10529 | 0.013733 | -0.073242 | -0.18311 | -0.036621 | 0.054932 | 115.6677 | 115.5533 | 120.9686 | 120.8862 | 0.10529 | 121.0052 | 114.2303 | -0.18311 | 120.8862 | 0.10529 | 114.2303 | 120.9686 | 121.0052 | -120.9915 | -121.225
949.9844 | 121.2524 | -115.5167 | 5.4611 | 0.11253 | 0.013845 | 0.0096237 | 0.0057337 | 0.058812 | -0.0086901 | 0.06319 | -115.3061 | 5.2963 | -115.4297 | -115.4205 | 5.5023 | -1.3824 | -0.56305 | -0.34332 | 5.4016 | -115.6357 | 0.086976 | -0.1648 | 0.21057 | 0.096131 | 0.041198 | -0.11902 | -0.05951 | 0.1236 | 114.9536 | 115.1733 | 121.019 | 120.813 | 0.21057 | 120.9183 | 114.1342 | -0.11902 | 120.813 | 0.21057 | 114.1342 | 121.019 | 120.9183 | -120.8908 | -121.0968
951.6875 | 121.1609 | -115.7181 | 5.3009 | -0.1545 | 0.01534 | 0.0066329 | -0.00067514 | 0.056676 | -0.0067675 | 0.062763 | -115.4297 | 5.1407 | -115.5807 | -115.5212 | 5.3787 | -1.1032 | 0.09613 | 0.35248 | 5.2322 | -115.7959 | 0.13733 | -0.16022 | 0.28839 | 0.19684 | 0.07782 | -0.077819 | -0.068664 | 0.15106 | 115.8142 | 116.0706 | 121.0968 | 120.8588 | 0.28839 | 120.9503 | 114.6149 | -0.077819 | 120.8588 | 0.28839 | 114.6149 | 121.0968 | 120.9503 | -120.8817 | -121.0968
953.4375 | 121.1563 | -115.7318 | 5.2048 | -0.23079 | 0.014486 | 0.0064193 | 0.0068017 | 0.053472 | -0.0078357 | 0.063831 | -115.6403 | 5.072 | -115.7181 | -115.7181 | 5.1315 | -1.1627 | 0.29755 | 0.16022 | 5.1865 | -115.9058 | 0.013733 | -0.13275 | 0.091553 | 0.013733 | -0.073242 | -0.17395 | -0.018311 | 0.07782 | 116.0294 | 115.892 | 120.8633 | 120.8038 | 0.091553 | 120.9183 | 114.5691 | -0.17395 | 120.8038 | 0.091553 | 114.5691 | 120.8633 | 120.9183 | -120.9229 | -121.1105
955.1875 | 121.1792 | -115.773 | 5.0858 | 0.15831 | 0.012136 | 0.010692 | 0.0080835 | 0.058172 | -0.011681 | 0.06554 | -115.6174 | 4.9576 | -115.7639 | -115.7227 | 5.1224 | -1.4053 | -0.56305 | -0.36163 | 5.0583 | -115.9424 | 0.009155 | -0.12817 | 0.15564 | 0.050354 | 0.036621 | -0.16937 | -0.027465 | 0.14648 | 115.21 | 115.4114 | 120.8954 | 120.7306 | 0.15564 | 120.8313 | 114.3677 | -0.16937 | 120.7306 | 0.15564 | 114.3677 | 120.8954 | 120.8313 | -120.8496 | -121.0281
956.9531 | 121.1838 | -115.7776 | 5.0812 | 0.11253 | 0.014699 | 0.0089829 | 0.0074427 | 0.059667 | -0.0095447 | 0.066821 | -115.6769 | 4.9622 | -115.7684 | -115.773 | 5.0308 | -1.4557 | -0.4715 | -0.48065 | 5.0674 | -115.9332 | 0.009155 | -0.11902 | 0.10071 | 0.004578 | -0.050354 | -0.15564 | -0.013733 | 0.091553 | 115.3061 | 115.2969 | 120.8084 | 120.7397 | 0.10071 | 120.845 | 114.3219 | -0.15564 | 120.7397 | 0.10071 | 114.3219 | 120.8084 | 120.845 | -120.8496 | -121.0144
958.6562 | 121.0281 | -115.892 | 5.0262 | -0.19264 | 0.014058 | 0.0070603 | 0.0027429 | 0.052404 | -0.0071947 | 0.067249 | -115.654 | 4.8294 | -115.773 | -115.7364 | 5.072 | -1.0986 | 0.14191 | 0.3479 | 4.9255 | -116.0065 | 0.11902 | -0.19684 | 0.23804 | 0.15564 | 0.045776 | -0.11444 | -0.10071 | 0.11902 | 116.0339 | 116.2399 | 120.9641 | 120.7214 | 0.23804 | 120.8176 | 114.7934 | -0.11444 | 120.7214 | 0.23804 | 114.7934 | 120.9641 | 120.8176 | -120.7993 | -121.0327
960.4219 | 121.0327 | -115.8188 | 5.0674 | -0.10109 | 0.014486 | 0.0055649 | 0.0053065 | 0.056249 | -0.0067675 | 0.064899 | -115.5899 | 4.866 | -115.7181 | -115.6769 | 5.1178 | -1.149 | 0.036621 | 0.30212 | 4.9805 | -115.9515 | 0.10071 | -0.20142 | 0.22888 | 0.14191 | 0.050354 | -0.13275 | -0.086975 | 0.12817 | 115.8554 | 116.1209 | 120.9366 | 120.6848 | 0.22888 | 120.7993 | 114.6698 | -0.13275 | 120.6848 | 0.22888 | 114.6698 | 120.9366 | 120.7993 | -120.7855 | -121.019
962.1094 | 120.9915 | -115.9103 | 4.9347 | -0.16975 | 0.011495 | 0.0042831 | 0.0053065 | 0.053472 | -0.0095447 | 0.063617 | -115.6906 | 4.7424 | -115.8188 | -115.773 | 4.9805 | -1.0941 | 0.16022 | 0.34332 | 4.8477 | -116.0339 | 0.091552 | -0.19226 | 0.21973 | 0.13733 | 0.045777 | -0.1236 | -0.086975 | 0.12817 | 116.0706 | 116.2537 | 120.8908 | 120.6528 | 0.21973 | 120.7581 | 114.8163 | -0.1236 | 120.6528 | 0.21973 | 114.8163 | 120.8908 | 120.7581 | -120.7535 | -120.9686
963.8594 | 120.9686 | -115.9103 | 4.9393 | -0.040054 | 0.015554 | 0.0085555 | 0.012142 | 0.057104 | -0.0089037 | 0.06554 | -115.7227 | 4.7699 | -115.8783 | -115.8142 | 4.8981 | -1.2955 | -0.20599 | -0.19684 | 4.8706 | -116.0294 | 0.032043 | -0.16937 | 0.18768 | 0.09613 | -0.041199 | -0.11902 | -0.068665 | 0.15564 | 115.7043 | 115.7135 | 120.8084 | 120.6802 | 0.18768 | 120.7809 | 114.6149 | -0.11902 | 120.6802 | 0.18768 | 114.6149 | 120.8084 | 120.7809 | -120.8176 | -120.9686
965.5469 | 120.9503 | -115.7776 | 5.0354 | -0.040054 | 0.01299 | 0.0062057 | 0.0085107 | 0.057104 | -0.010399 | 0.062976 | -115.5991 | 4.8798 | -115.7455 | -115.7043 | 4.9805 | -1.3184 | -0.21973 | -0.23346 | 4.9713 | -115.9607 | 0.032044 | -0.15564 | 0.17853 | 0.073242 | -0.054931 | -0.18311 | -0.064087 | 0.14648 | 115.5579 | 115.5441 | 120.7581 | 120.6573 | 0.17853 | 120.7489 | 114.4592 | -0.18311 | 120.6573 | 0.17853 | 114.4592 | 120.7581 | 120.7489 | -120.7809 | -120.9961
967.2969 | 121.0236 | -115.8508 | 4.8706 | 0.1812 | 0.01299 | 0.0062057 | 0.0057337 | 0.055608 | -0.0076221 | 0.066821 | -115.7318 | 4.7562 | -115.8234 | -115.8005 | 4.8843 | -1.4603 | -0.55389 | -0.41657 | 4.8386 | -116.0339 | 0.027466 | -0.11444 | 0.11902 | 0.050354 | 0.013733 | -0.18311 | -0.032043 | 0.091552 | 115.2969 | 115.4343 | 120.7352 | 120.607 | 0.11902 | 120.6894 | 114.3906 | -0.18311 | 120.607 | 0.11902 | 114.3906 | 120.7352 | 120.6894 | -120.694 | -120.9045
969.0469 | 120.9686 | -115.8417 | 4.8294 | 0.16594 | 0.012136 | 0.010265 | 0.0053065 | 0.058599 | -0.0093311 | 0.06618 | -115.6952 | 4.6738 | -115.8051 | -115.7639 | 4.8843 | -1.4328 | -0.57678 | -0.37079 | 4.7882 | -116.0019 | 0.036621 | -0.15564 | 0.14648 | 0.07782 | 0.054931 | -0.16022 | -0.041199 | 0.10986 | 115.2649 | 115.4709 | 120.726 | 120.5154 | 0.14648 | 120.6299 | 114.4089 | -0.16022 | 120.5154 | 0.14648 | 114.4089 | 120.726 | 120.6299 | -120.6345 | -120.8313
970.8125 | 120.932 | -115.8417 | 4.8614 | 0.074387 | 0.013845 | 0.0053513 | 0.011501 | 0.056035 | -0.010613 | 0.067035 | -115.7318 | 4.7333 | -115.8508 | -115.8417 | 4.7836 | -1.4053 | -0.29297 | -0.37079 | 4.8157 | -116.0339 | -0.009155 | -0.12817 | 0.10986 | 0 | -0.07782 | -0.19226 | -0.045776 | 0.11902 | 115.5487 | 115.4709 | 120.6253 | 120.575 | 0.10986 | 120.6573 | 114.4363 | -0.19226 | 120.575 | 0.10986 | 114.4363 | 120.6253 | 120.6573 | -120.7123 | -120.8954
972.5 | 120.8771 | -115.8508 | 4.8843 | -0.032425 | 0.015767 | 0.0062057 | 0.0080835 | 0.05689 | -0.0097583 | 0.064258 | -115.686 | 4.7104 | -115.8005 | -115.7822 | 4.8386 | -1.3046 | -0.21515 | -0.19684 | 4.8248 | -115.9973 | 0.050354 | -0.17395 | 0.16479 | 0.068664 | -0.045776 | -0.14648 | -0.059509 | 0.11444 | 115.6357 | 115.654 | 120.6894 | 120.5612 | 0.16479 | 120.6757 | 114.5462 | -0.14648 | 120.5612 | 0.16479 | 114.5462 | 120.6894 | 120.6757 | -120.6848 | -120.8817
974.25 | 120.8954 | -115.8829 | 4.8065 | -0.19264 | 0.01299 | 0.0038559 | 0.0050929 | 0.056249 | -0.0091173 | 0.063617 | -115.8051 | 4.6692 | -115.8188 | -115.8829 | 4.7287 | -1.2039 | 0.27466 | 0.14648 | 4.7699 | -116.0568 | 0.064087 | -0.13733 | 0.07782 | 0 | -0.07782 | -0.17395 | -0.036622 | 0.013733 | 116.1575 | 116.0294 | 120.6116 | 120.5521 | 0.07782 | 120.6528 | 114.679 | -0.17395 | 120.5521 | 0.07782 | 114.679 | 120.6116 | 120.6528 | -120.6253 | -120.8633
976 | 120.9412 | -115.8096 | 4.8203 | 0.020981 | 0.014058 | 0.0074875 | 0.00082026 | 0.05454 | -0.0054859 | 0.064685 | -115.6677 | 4.6738 | -115.741 | -115.7822 | 4.8386 | -1.3458 | -0.10529 | 0 | 4.7928 | -116.0019 | 0.068664 | -0.14648 | 0.14191 | 0.027465 | 0.018311 | -0.19226 | -0.027465 | 0.073242 | 115.7043 | 115.8096 | 120.6482 | 120.4834 | 0.14191 | 120.6024 | 114.4638 | -0.19226 | 120.4834 | 0.14191 | 114.4638 | 120.6482 | 120.6024 | -120.5612 | -120.8221
977.7656 | 120.8633 | -115.7043 | 4.9347 | 0.074387 | 0.015127 | 0.0047103 | 0.010861 | 0.057104 | -0.0089037 | 0.063831 | -115.6036 | 4.7791 | -115.7089 | -115.7135 | 4.8111 | -1.4053 | -0.29755 | -0.38452 | 4.8843 | -115.8737 | -0.004577 | -0.15564 | 0.10071 | -0.009155 | -0.1236 | -0.16937 | -0.050354 | 0.10528 | 115.4068 | 115.3198 | 120.5154 | 120.4834 | 0.10071 | 120.5887 | 114.299 | -0.16937 | 120.4834 | 0.10071 | 114.299 | 120.5154 | 120.5887 | -120.6436 | -120.8084
979.5312 | 120.9045 | -115.8691 | 4.6921 | 0.11253 | 0.015554 | 0.0051377 | 0.0078699 | 0.055822 | -0.0086901 | 0.064685 | -115.8051 | 4.5731 | -115.8737 | -115.9195 | 4.6463 | -1.5244 | -0.4715 | -0.49896 | 4.6738 | -116.0889 | -0.004577 | -0.11902 | 0.064087 | -0.050354 | -0.045777 | -0.21973 | -0.018311 | 0.068664 | 115.3976 | 115.3702 | 120.5154 | 120.4422 | 0.064087 | 120.5429 | 114.3448 | -0.21973 | 120.4422 | 0.064087 | 114.3448 | 120.5154 | 120.5429 | -120.5658 | -120.7809
981.2188 | 120.8954 | -115.7501 | 4.7836 | 0.16594 | 0.013631 | 0.0072739 | 0.0085107 | 0.056463 | -0.0089037 | 0.06618 | -115.7043 | 4.6783 | -115.7867 | -115.7867 | 4.747 | -1.5244 | -0.42572 | -0.52185 | 4.7699 | -115.979 | -0.036621 | -0.10528 | 0.045776 | -0.036621 | -0.036621 | -0.22888 | -0.013733 | 0.082397 | 115.3244 | 115.2283 | 120.4971 | 120.4285 | 0.045776 | 120.52 | 114.2258 | -0.22888 | 120.4285 | 0.045776 | 114.2258 | 120.4971 | 120.52 | -120.5704 | -120.7626
982.9062 | 120.7352 | -115.7867 | 4.8386 | -0.078201 | 0.013418 | 0.0068467 | 0.0087243 | 0.053899 | -0.0095447 | 0.065967 | -115.5945 | 4.6829 | -115.7547 | -115.6906 | 4.8203 | -1.268 | -0.16937 | -0.13275 | 4.7836 | -115.9287 | 0.032043 | -0.15564 | 0.19226 | 0.09613 | -0.018311 | -0.14191 | -0.054932 | 0.16022 | 115.6174 | 115.654 | 120.607 | 120.4697 | 0.19226 | 120.5704 | 114.5187 | -0.14191 | 120.4697 | 0.19226 | 114.5187 | 120.607 | 120.5704 | -120.5933 | -120.7672
984.6406 | 120.8496 | -115.7089 | 4.8111 | 0.12016 | 0.01235 | 0.0066329 | 0.0014613 | 0.055395 | -0.0061267 | 0.066394 | -115.5716 | 4.6555 | -115.6677 | -115.6998 | 4.8248 | -1.442 | -0.33875 | -0.19684 | 4.747 | -115.9378 | 0.041198 | -0.15564 | 0.13733 | 0.009155 | 0.013733 | -0.22888 | -0.064087 | 0.096131 | 115.3702 | 115.5121 | 120.5338 | 120.3644 | 0.13733 | 120.4559 | 114.267 | -0.22888 | 120.3644 | 0.13733 | 114.267 | 120.5338 | 120.4559 | -120.4788 | -120.7489
986.4062 | 120.7123 | -115.9058 | 4.6692 | -0.1545 | 0.013418 | 0.0085555 | 0.0021021 | 0.053899 | -0.0067675 | 0.064044 | -115.6631 | 4.4952 | -115.7867 | -115.7547 | 4.7379 | -1.1902 | 0.082397 | 0.32044 | 4.5914 | -116.0339 | 0.11902 | -0.17395 | 0.24262 | 0.15106 | 0.068665 | -0.12817 | -0.077819 | 0.1236 | 115.9882 | 116.2262 | 120.6436 | 120.401 | 0.24262 | 120.4971 | 114.7156 | -0.12817 | 120.401 | 0.24262 | 114.7156 | 120.6436 | 120.4971 | -120.4559 | -120.7031
988.1562 | 120.8313 | -115.6769 | 4.7974 | 0.097275 | 0.012563 | 0.0077011 | 0.011929 | 0.055395 | -0.0097583 | 0.064258 | -115.6036 | 4.6738 | -115.6906 | -115.7135 | 4.7562 | -1.5518 | -0.45319 | -0.52185 | 4.7745 | -115.8554 | -0.013733 | -0.1236 | 0.073242 | -0.036621 | -0.041198 | -0.17853 | -0.022888 | 0.086975 | 115.2237 | 115.155 | 120.433 | 120.3506 | 0.073242 | 120.4514 | 114.1251 | -0.17853 | 120.3506 | 0.073242 | 114.1251 | 120.433 | 120.4514 | -120.488 | -120.6528
989.8438 | 120.7077 | -115.8463 | 4.7012 | -0.23842 | 0.011709 | 0.0081283 | 0.0031701 | 0.051763 | -0.0076221 | 0.063617 | -115.6586 | 4.5181 | -115.7684 | -115.7547 | 4.6967 | -1.1902 | 0.22888 | 0.29297 | 4.6555 | -115.9973 | 0.077819 | -0.18311 | 0.18768 | 0.091552 | -0.004578 | -0.15106 | -0.045776 | 0.10986 | 116.0751 | 116.1392 | 120.5429 | 120.3644 | 0.18768 | 120.5017 | 114.6561 | -0.15106 | 120.3644 | 0.18768 | 114.6561 | 120.5429 | 120.5017 | -120.4697 | -120.6985
991.6094 | 120.6619 | -115.686 | 4.8706 | -0.2079 | 0.013418 | 0.0062057 | 0.0040247 | 0.052617 | -0.0097583 | 0.064258 | -115.4343 | 4.6875 | -115.5716 | -115.5075 | 4.921 | -1.1719 | 0.11444 | 0.33417 | 4.7928 | -115.8096 | 0.11444 | -0.18311 | 0.25177 | 0.17853 | 0.050354 | -0.1236 | -0.077819 | 0.13733 | 115.8005 | 116.0202 | 120.607 | 120.3735 | 0.25177 | 120.4788 | 114.5142 | -0.1236 | 120.3735 | 0.25177 | 114.5142 | 120.607 | 120.4788 | -120.4422 | -120.6802
993.3594 | 120.7214 | -115.8691 | 4.6005 | 0.066757 | 0.01299 | 0.0064193 | 0.010861 | 0.055395 | -0.010613 | 0.063403 | -115.7684 | 4.4586 | -115.8691 | -115.8966 | 4.5136 | -1.4923 | -0.33417 | -0.42572 | 4.5639 | -116.0522 | 0 | -0.14191 | 0.10071 | -0.027465 | -0.086975 | -0.1831 | -0.036621 | 0.10071 | 115.535 | 115.4434 | 120.3827 | 120.3278 | 0.10071 | 120.433 | 114.3768 | -0.1831 | 120.3278 | 0.10071 | 114.3768 | 120.3827 | 120.433 | -120.4697 | -120.6528
995.1094 | 120.7489 | -115.9744 | 4.4586 | -0.024795 | 0.012777 | 0.0042831 | 0.0021021 | 0.055181 | -0.0050585 | 0.066821 | -115.8463 | 4.3121 | -115.9195 | -115.9195 | 4.4815 | -1.3641 | -0.082397 | 0.073242 | 4.4174 | -116.1667 | 0.054931 | -0.14648 | 0.12817 | 0.054931 | 0.022888 | -0.19226 | -0.041199 | 0.073243 | 115.892 | 116.0477 | 120.4559 | 120.2866 | 0.12817 | 120.3918 | 114.6103 | -0.19226 | 120.2866 | 0.12817 | 114.6103 | 120.4559 | 120.3918 | -120.3781 | -120.6253
996.8125 | 120.6619 | -116.0202 | 4.4403 | -0.24605 | 0.011922 | 0.0057785 | 0.0065881 | 0.053045 | -0.0086901 | 0.06319 | -115.9103 | 4.2892 | -116.0065 | -115.9973 | 4.3762 | -1.2772 | 0.27008 | 0.14648 | 4.4083 | -116.1667 | 0.013733 | -0.15106 | 0.10986 | 0.022889 | -0.064087 | -0.14648 | -0.032044 | 0.096131 | 116.2903 | 116.1667 | 120.3964 | 120.3094 | 0.10986 | 120.4285 | 114.743 | -0.14648 | 120.3094 | 0.10986 | 114.743 | 120.3964 | 120.4285 | -120.4468 | -120.607
998.5625 | 120.5841 | -116.0294 | 4.4083 | -0.10872 | 0.011709 | 0.0064193 | 0.010861 | 0.05454 | -0.0071947 | 0.064471 | -115.8737 | 4.2206 | -116.0339 | -115.9561 | 4.3854 | -1.3733 | -0.12817 | -0.10986 | 4.3625 | -116.2079 | -0.004578 | -0.18768 | 0.15564 | 0.073242 | -0.022888 | -0.17853 | -0.045776 | 0.16022 | 115.9012 | 115.9195 | 120.4147 | 120.2499 | 0.15564 | 120.3918 | 114.6561 | -0.17853 | 120.2499 | 0.15564 | 114.6561 | 120.4147 | 120.3918 | -120.4422 | -120.6162
1000.25 | 120.5795 | -115.8829 | 4.5776 | -0.16212 | 0.013418 | 0.0077011 | 0.0029565 | 0.051763 | -0.0061267 | 0.064044 | -115.6403 | 4.3991 | -115.7318 | -115.741 | 4.6234 | -1.2131 | 0.1236 | 0.32044 | 4.5181 | -116.0202 | 0.15106 | -0.17853 | 0.24262 | 0.14191 | 0.045776 | -0.13733 | -0.05951 | 0.091553 | 116.0065 | 116.2033 | 120.5063 | 120.282 | 0.24262 | 120.401 | 114.6698 | -0.13733 | 120.282 | 0.24262 | 114.6698 | 120.5063 | 120.401 | -120.3094 | -120.5978
1002.0156 | 120.6207 | -115.9607 | 4.4632 | -0.20027 | 0.011068 | 0.0038559 | 0.0057337 | 0.054967 | -0.0086901 | 0.062976 | -115.8508 | 4.3167 | -115.9195 | -115.9378 | 4.3854 | -1.2772 | 0.2655 | 0.13275 | 4.4449 | -116.1301 | 0.041198 | -0.14649 | 0.10986 | 0.022888 | -0.07782 | -0.16937 | -0.018311 | 0.068665 | 116.2262 | 116.0934 | 120.3461 | 120.2774 | 0.10986 | 120.4056 | 114.6835 | -0.16937 | 120.2774 | 0.10986 | 114.6835 | 120.3461 | 120.4056 | -120.3827 | -120.5933
1003.7656 | 120.6848 | -115.9698 | 4.3808 | 0.02861 | 0.013204 | 0.0064193 | 0.0044519 | 0.053686 | -0.0059131 | 0.065753 | -115.8417 | 4.2389 | -115.9195 | -115.9378 | 4.39 | -1.4603 | -0.15106 | -0.054932 | 4.3396 | -116.153 | 0.050354 | -0.14191 | 0.12817 | 0.032044 | 0.009156 | -0.1831 | -0.041198 | 0.07782 | 115.8188 | 115.9149 | 120.3598 | 120.2087 | 0.12817 | 120.3094 | 114.5096 | -0.1831 | 120.2087 | 0.12817 | 114.5096 | 120.3598 | 120.3094 | -120.3003 | -120.5338
1005.4531 | 120.6573 | -115.8829 | 4.4449 | 0.074387 | 0.013845 | 0.0038559 | 0.010433 | 0.057317 | -0.0080493 | 0.063617 | -115.7822 | 4.3488 | -115.9012 | -115.9103 | 4.4037 | -1.561 | -0.39825 | -0.48981 | 4.4724 | -116.0477 | -0.01831 | -0.09613 | 0.10071 | -0.027465 | -0.041198 | -0.16479 | 0.027466 | 0.11902 | 115.4846 | 115.3931 | 120.2866 | 120.2316 | 0.10071 | 120.3552 | 114.3219 | -0.16479 | 120.2316 | 0.10071 | 114.3219 | 120.2866 | 120.3552 | -120.3461 | -120.4926
1007.2188 | 120.5612 | -115.8234 | 4.5319 | -0.0019073 | 0.013204 | 0.0053513 | 0.010006 | 0.056035 | -0.0080493 | 0.066821 | -115.7089 | 4.3991 | -115.8142 | -115.8142 | 4.4632 | -1.506 | -0.32044 | -0.39825 | 4.5044 | -116.0019 | 0.009155 | -0.13275 | 0.11444 | 0.009155 | -0.068664 | -0.17853 | -0.027465 | 0.10529 | 115.5029 | 115.4251 | 120.2866 | 120.2225 | 0.11444 | 120.3278 | 114.3173 | -0.17853 | 120.2225 | 0.11444 | 114.3173 | 120.2866 | 120.3278 | -120.3461 | -120.5338
1008.9688 | 120.52 | -115.8966 | 4.4861 | -0.055313 | 0.01235 | 0.0070603 | 0.0085107 | 0.057744 | -0.010399 | 0.06554 | -115.7227 | 4.3213 | -115.8691 | -115.8142 | 4.4586 | -1.3916 | -0.2243 | -0.19684 | 4.4312 | -116.0385 | 0.027465 | -0.16479 | 0.17395 | 0.082397 | -0.027466 | -0.14191 | -0.054932 | 0.14648 | 115.6723 | 115.6998 | 120.3552 | 120.2179 | 0.17395 | 120.3278 | 114.505 | -0.14191 | 120.2179 | 0.17395 | 114.505 | 120.3552 | 120.3278 | -120.3552 | -120.5246
1010.6562 | 120.5063 | -115.947 | 4.422 | -0.024795 | 0.011709 | 0.010265 | 0.0080835 | 0.056463 | -0.010826 | 0.065967 | -115.7959 | 4.2618 | -115.9241 | -115.892 | 4.3579 | -1.442 | -0.2655 | -0.29755 | 4.3716 | -116.0706 | 0.022888 | -0.16022 | 0.15106 | 0.054931 | -0.064087 | -0.1236 | -0.050354 | 0.12817 | 115.6815 | 115.6494 | 120.3049 | 120.2087 | 0.15106 | 120.3186 | 114.505 | -0.1236 | 120.2087 | 0.15106 | 114.505 | 120.3049 | 120.3186 | -120.3461 | -120.4926
1012.4062 | 120.6116 | -115.9744 | 4.2938 | 0.1049 | 0.011068 | 0.0072739 | 0.0070155 | 0.057744 | -0.0063403 | 0.065967 | -115.9378 | 4.1428 | -115.9836 | -116.0294 | 4.2114 | -1.6205 | -0.46234 | -0.54932 | 4.2709 | -116.2033 | -0.009156 | -0.15106 | 0.036621 | -0.054932 | -0.082397 | -0.22888 | -0.022888 | 0.045777 | 115.5121 | 115.4251 | 120.1859 | 120.1172 | 0.036621 | 120.2454 | 114.3539 | -0.22888 | 120.1172 | 0.036621 | 114.3539 | 120.1859 | 120.2454 | -120.2774 | -120.4971
1014.1562 | 120.5933 | -115.9287 | 4.3213 | 0.097275 | 0.013631 | 0.0081283 | 0.0063745 | 0.056035 | -0.0076221 | 0.063403 | -115.9058 | 4.1977 | -115.9515 | -115.9973 | 4.2709 | -1.6113 | -0.44403 | -0.53101 | 4.303 | -116.1621 | -0.022888 | -0.1236 | 0.022888 | -0.068664 | -0.050354 | -0.23346 | -0.01831 | 0.045776 | 115.4846 | 115.3976 | 120.1996 | 120.1263 | 0.022888 | 120.2316 | 114.3173 | -0.23346 | 120.1263 | 0.022888 | 114.3173 | 120.1996 | 120.2316 | -120.2728 | -120.4834
1015.9062 | 120.4376 | -115.8279 | 4.4724 | -0.11635 | 0.014058 | 0.0047103 | 0.0055201 | 0.05454 | -0.0082629 | 0.065753 | -115.6586 | 4.3396 | -115.7959 | -115.7501 | 4.4632 | -1.3458 | -0.10529 | -0.086975 | 4.4174 | -115.9561 | 0.032044 | -0.13275 | 0.16937 | 0.07782 | -0.009155 | -0.12817 | -0.054932 | 0.13733 | 115.7227 | 115.741 | 120.2911 | 120.1675 | 0.16937 | 120.2454 | 114.4821 | -0.12817 | 120.1675 | 0.16937 | 114.4821 | 120.2911 | 120.2454 | -120.2682 | -120.4285
1017.5938 | 120.4788 | -115.9195 | 4.3671 | -0.14687 | 0.011922 | 0.010478 | 0.0061609 | 0.054113 | -0.0078357 | 0.064044 | -115.8096 | 4.2252 | -115.8691 | -115.8829 | 4.3396 | -1.3458 | 0.09613 | 0.018311 | 4.335 | -116.1209 | 0.050354 | -0.14191 | 0.10986 | 0.036621 | -0.027465 | -0.20142 | -0.032043 | 0.05951 | 116.0156 | 115.9378 | 120.2591 | 120.1447 | 0.10986 | 120.2545 | 114.5737 | -0.20142 | 120.1447 | 0.10986 | 114.5737 | 120.2591 | 120.2545 | -120.2362 | -120.488
1019.3438 | 120.575 | -115.9058 | 4.303 | 0.020981 | 0.013418 | 0.0027877 | 0.0012475 | 0.053258 | -0.0071947 | 0.064685 | -115.8005 | 4.1748 | -115.8691 | -115.9195 | 4.3259 | -1.5518 | -0.28839 | -0.16479 | 4.2801 | -116.1118 | 0.036621 | -0.12817 | 0.10529 | -0.013733 | 0.022888 | -0.20599 | -0.022889 | 0.068665 | 115.6174 | 115.741 | 120.2316 | 120.0806 | 0.10529 | 120.1859 | 114.3539 | -0.20599 | 120.0806 | 0.10529 | 114.3539 | 120.2316 | 120.1859 | -120.1721 | -120.4147
1021.0312 | 120.4193 | -115.86 | 4.4037 | -0.055313 | 0.011495 | 0.0057785 | 0.01022 | 0.055181 | -0.011681 | 0.061908 | -115.6952 | 4.248 | -115.8371 | -115.7822 | 4.3762 | -1.4511 | -0.27008 | -0.26093 | 4.3808 | -116.0019 | 0.022888 | -0.15564 | 0.16479 | 0.077819 | -0.027466 | -0.14191 | -0.022889 | 0.14191 | 115.5899 | 115.5991 | 120.2362 | 120.108 | 0.16479 | 120.2408 | 114.4089 | -0.14191 | 120.108 | 0.16479 | 114.4089 | 120.2362 | 120.2408 | -120.2408 | -120.4056
1022.7812 | 120.4468 | -115.8646 | 4.3533 | -0.13161 | 0.011922 | 0.0010787 | 0.0014613 | 0.053258 | -0.0069811 | 0.064471 | -115.6906 | 4.1794 | -115.8142 | -115.7776 | 4.4312 | -1.3321 | -0.054932 | 0.21057 | 4.2938 | -116.0568 | 0.050354 | -0.17395 | 0.17395 | 0.086975 | 0.077819 | -0.19226 | -0.05951 | 0.1236 | 115.8096 | 116.0751 | 120.2957 | 120.0439 | 0.17395 | 120.1584 | 114.5325 | -0.19226 | 120.0439 | 0.17395 | 114.5325 | 120.2957 | 120.1584 | -120.1675 | -120.4102
1024.4688 | 120.3918 | -115.9332 | 4.3304 | -0.13924 | 0.011922 | 0.0083419 | 0.0061609 | 0.053472 | -0.0054859 | 0.061481 | -115.7227 | 4.1153 | -115.8646 | -115.8005 | 4.3579 | -1.2909 | 0.11444 | 0.28381 | 4.2297 | -116.1209 | 0.068665 | -0.21515 | 0.21057 | 0.13275 | 0.027466 | -0.18768 | -0.10071 | 0.14191 | 116.0477 | 116.217 | 120.2911 | 120.0485 | 0.21057 | 120.163 | 114.6423 | -0.18768 | 120.0485 | 0.21057 | 114.6423 | 120.2911 | 120.163 | -120.195 | -120.4514
1026.2031 | 120.3873 | -115.8554 | 4.39 | -0.055313 | 0.013418 | 0.0072739 | 0.0097925 | 0.054326 | -0.011681 | 0.064044 | -115.6952 | 4.2068 | -115.8508 | -115.8005 | 4.3442 | -1.506 | -0.2655 | -0.28381 | 4.3304 | -116.0156 | 0.004578 | -0.18311 | 0.16022 | 0.054932 | -0.045777 | -0.16022 | -0.05951 | 0.15564 | 115.5899 | 115.5716 | 120.1996 | 120.0623 | 0.16022 | 120.1859 | 114.3494 | -0.16022 | 120.0623 | 0.16022 | 114.3494 | 120.1996 | 120.1859 | -120.2408 | -120.4056
1027.9531 | 120.369 | -115.7639 | 4.4907 | -0.070572 | 0.011922 | 0.0068467 | 0.0078699 | 0.053472 | -0.0084765 | 0.066394 | -115.5762 | 4.3121 | -115.7135 | -115.686 | 4.4449 | -1.4877 | -0.27924 | -0.27008 | 4.4266 | -115.8966 | 0.050354 | -0.17853 | 0.18768 | 0.07782 | -0.045777 | -0.13275 | -0.064087 | 0.13733 | 115.4846 | 115.4938 | 120.2087 | 120.076 | 0.18768 | 120.1904 | 114.2761 | -0.13275 | 120.076 | 0.18768 | 114.2761 | 120.2087 | 120.1904 | -120.2042 | -120.3873
1029.7031 | 120.3964 | -115.7043 | 4.4815 | -0.22316 | 0.016408 | 0.0047103 | 0.0044519 | 0.051763 | -0.0069811 | 0.062763 | -115.6448 | 4.3259 | -115.6998 | -115.741 | 4.4266 | -1.3824 | 0.16022 | 0.064087 | 4.4128 | -115.9332 | 0.004578 | -0.15564 | 0.05951 | -0.036621 | -0.054931 | -0.22888 | -0.068664 | 0.054932 | 115.8646 | 115.7684 | 120.1309 | 120.0302 | 0.05951 | 120.1172 | 114.3219 | -0.22888 | 120.0302 | 0.05951 | 114.3219 | 120.1309 | 120.1172 | -120.1813 | -120.4147
1031.3906 | 120.3232 | -115.892 | 4.3167 | -0.16975 | 0.014913 | 0.0036423 | 0.00082026 | 0.054113 | -0.0067675 | 0.065326 | -115.654 | 4.1245 | -115.7913 | -115.7593 | 4.3762 | -1.3184 | 0.032043 | 0.2655 | 4.2297 | -116.011 | 0.10071 | -0.19226 | 0.23804 | 0.13275 | 0.05951 | -0.11902 | -0.086975 | 0.13733 | 115.9241 | 116.1575 | 120.2682 | 120.0165 | 0.23804 | 120.1218 | 114.5737 | -0.11902 | 120.0165 | 0.23804 | 114.5737 | 120.2682 | 120.1218 | -120.108 | -120.3278
1033.1406 | 120.401 | -115.6586 | 4.4724 | 0.24986 | 0.0099996 | 0.0066329 | 0.010647 | 0.057531 | -0.0091173 | 0.063617 | -115.4755 | 4.3213 | -115.6265 | -115.6036 | 4.5181 | -1.6342 | -0.67291 | -0.43488 | 4.4174 | -115.7913 | 0.032043 | -0.15106 | 0.1831 | 0.054931 | 0.045776 | -0.13275 | -0.054932 | 0.15106 | 114.9857 | 115.2237 | 120.1767 | 119.9799 | 0.1831 | 120.076 | 114.0244 | -0.13275 | 119.9799 | 0.1831 | 114.0244 | 120.1767 | 120.076 | -120.0989 | -120.2637
1034.8906 | 120.401 | -115.741 | 4.4128 | 0.24986 | 0.013418 | 0.011974 | 0.0055201 | 0.056676 | -0.0099719 | 0.06554 | -115.5029 | 4.2664 | -115.6403 | -115.6403 | 4.4678 | -1.6342 | -0.63171 | -0.35248 | 4.3488 | -115.8554 | 0.10071 | -0.14649 | 0.23804 | 0.10071 | 0.054931 | -0.11444 | -0.064087 | 0.13733 | 115.1093 | 115.3885 | 120.2087 | 120.0073 | 0.23804 | 120.0897 | 114.1068 | -0.11444 | 120.0073 | 0.23804 | 114.1068 | 120.2087 | 120.0897 | -120.0531 | -120.2682
1036.5938 | 120.3323 | -115.6219 | 4.5044 | -0.17738 | 0.012563 | 0.010265 | 0.0070155 | 0.053899 | -0.0082629 | 0.063831 | -115.4388 | 4.3488 | -115.567 | -115.5853 | 4.4952 | -1.3779 | 0.17395 | 0.16937 | 4.4815 | -115.8142 | 0.054931 | -0.15564 | 0.1831 | 0.036621 | -0.009156 | -0.19226 | -0.022889 | 0.12817 | 115.7959 | 115.7913 | 120.1172 | 119.9707 | 0.1831 | 120.1035 | 114.2441 | -0.19226 | 119.9707 | 0.1831 | 114.2441 | 120.1172 | 120.1035 | -120.0714 | -120.3186
1038.3438 | 120.3735 | -115.6265 | 4.4586 | 0.15831 | 0.015767 | 0.0079147 | 0.0093653 | 0.05454 | -0.011681 | 0.064258 | -115.4617 | 4.3213 | -115.6128 | -115.5807 | 4.4815 | -1.6754 | -0.67749 | -0.48065 | 4.3945 | -115.8005 | 0.013733 | -0.13733 | 0.16479 | 0.045776 | 0.022888 | -0.17395 | -0.064087 | 0.15106 | 114.949 | 115.1459 | 120.108 | 119.9478 | 0.16479 | 120.0211 | 113.9511 | -0.17395 | 119.9478 | 0.16479 | 113.9511 | 120.108 | 120.0211 | -120.0714 | -120.2591
1040.0781 | 120.3049 | -115.6357 | 4.5273 | -0.16975 | 0.012777 | 0.0064193 | 0.0029565 | 0.05219 | -0.0056995 | 0.062763 | -115.4114 | 4.3396 | -115.5716 | -115.5075 | 4.5547 | -1.3367 | 0.091553 | 0.25177 | 4.4586 | -115.7822 | 0.064087 | -0.18768 | 0.2243 | 0.12817 | 0.027466 | -0.14648 | -0.068665 | 0.16022 | 115.7272 | 115.8875 | 120.1904 | 119.9753 | 0.2243 | 120.0943 | 114.299 | -0.14648 | 119.9753 | 0.2243 | 114.299 | 120.1904 | 120.0943 | -120.0989 | -120.3094
1041.8438 | 120.3186 | -115.7455 | 4.4174 | -0.16212 | 0.012777 | 0.0036423 | 0.0063745 | 0.052404 | -0.010613 | 0.067035 | -115.5899 | 4.2618 | -115.6952 | -115.6952 | 4.3488 | -1.4145 | 0.16937 | 0.1236 | 4.3671 | -115.8966 | 0.050354 | -0.15564 | 0.15564 | 0.050354 | -0.068664 | -0.15106 | -0.050354 | 0.10528 | 115.9149 | 115.8691 | 120.0943 | 120.0073 | 0.15564 | 120.1126 | 114.3311 | -0.15106 | 120.0073 | 0.15564 | 114.3311 | 120.0943 | 120.1126 | -120.1126 | -120.314
1043.5312 | 120.3827 | -115.6815 | 4.3991 | 0.013352 | 0.010213 | 0.0081283 | 0.0044519 | 0.053472 | -0.0074085 | 0.06618 | -115.5075 | 4.2664 | -115.5991 | -115.6448 | 4.4174 | -1.5839 | -0.21973 | -0.09613 | 4.3579 | -115.8554 | 0.082398 | -0.13275 | 0.17395 | 0.036622 | 0.01831 | -0.17395 | -0.041199 | 0.091553 | 115.4617 | 115.5853 | 120.0989 | 119.9478 | 0.17395 | 120.0394 | 114.0976 | -0.17395 | 119.9478 | 0.17395 | 114.0976 | 120.0989 | 120.0394 | -119.9982 | -120.2545
1045.2656 | 120.2774 | -115.7135 | 4.4128 | -0.17738 | 0.013845 | 0.0047103 | 0.011288 | 0.052404 | -0.0091173 | 0.064471 | -115.5624 | 4.2755 | -115.7181 | -115.6403 | 4.3671 | -1.442 | 0.004578 | -0.036621 | 4.3488 | -115.892 | -0.004578 | -0.13733 | 0.15106 | 0.073242 | -0.045777 | -0.17853 | -0.064087 | 0.15564 | 115.7181 | 115.6769 | 120.0806 | 119.989 | 0.15106 | 120.0623 | 114.2715 | -0.17853 | 119.989 | 0.15106 | 114.2715 | 120.0806 | 120.0623 | -120.1309 | -120.3049
1047.0312 | 120.2728 | -115.6174 | 4.4769 | -0.10872 | 0.013845 | 0.0017197 | 0.0031701 | 0.055181 | -0.0056995 | 0.064685 | -115.3702 | 4.335 | -115.4984 | -115.4572 | 4.5685 | -1.3916 | -0.086975 | 0.20142 | 4.4174 | -115.773 | 0.11902 | -0.14191 | 0.24719 | 0.16022 | 0.091552 | -0.15564 | -0.05951 | 0.12817 | 115.5304 | 115.8188 | 120.1859 | 119.9524 | 0.24719 | 120.0348 | 114.2258 | -0.15564 | 119.9524 | 0.24719 | 114.2258 | 120.1859 | 120.0348 | -119.9753 | -120.2499
1048.7031 | 120.369 | -115.6357 | 4.39 | 0.15831 | 0.013204 | 0.0059921 | 0.01022 | 0.055608 | -0.0093311 | 0.06554 | -115.5579 | 4.2755 | -115.6723 | -115.6677 | 4.3488 | -1.767 | -0.54016 | -0.60425 | 4.3854 | -115.8188 | -0.036621 | -0.11444 | 0.07782 | -0.032044 | -0.041199 | -0.18311 | -0.004578 | 0.11444 | 115.0955 | 115.0314 | 119.9844 | 119.9112 | 0.07782 | 120.0211 | 113.8687 | -0.18311 | 119.9112 | 0.07782 | 113.8687 | 119.9844 | 120.0211 | -120.0623 | -120.2087
1050.4531 | 120.2271 | -115.7593 | 4.3533 | -0.13924 | 0.0093588 | 0.0077011 | 0.0082971 | 0.05454 | -0.0093311 | 0.065326 | -115.6036 | 4.2068 | -115.7227 | -115.6815 | 4.2892 | -1.4557 | -0.10071 | -0.07782 | 4.3121 | -115.9241 | 0.036621 | -0.14649 | 0.15564 | 0.077819 | -0.064087 | -0.16479 | -0.041199 | 0.11902 | 115.6586 | 115.6815 | 120.0485 | 119.9661 | 0.15564 | 120.0714 | 114.3036 | -0.16479 | 119.9661 | 0.15564 | 114.3036 | 120.0485 | 120.0714 | -120.076 | -120.2774
1052.2031 | 120.2728 | -115.4022 | 4.5959 | 0.074387 | 0.010427 | 0.0083419 | 0.0089381 | 0.055822 | -0.010399 | 0.064044 | -115.3336 | 4.4495 | -115.4297 | -115.4251 | 4.5181 | -1.6754 | -0.42572 | -0.5127 | 4.5822 | -115.5807 | -0.027465 | -0.14648 | 0.068665 | -0.022888 | -0.07782 | -0.17853 | -0.013733 | 0.09613 | 114.9765 | 114.8895 | 119.9203 | 119.8517 | 0.068665 | 119.9844 | 113.7268 | -0.17853 | 119.8517 | 0.068665 | 113.7268 | 119.9203 | 119.9844 | -120.0256 | -120.1767
1053.9531 | 120.2499 | -115.6906 | 4.39 | -0.10872 | 0.010427 | 0.0064193 | 0.00039306 | 0.05454 | -0.0069811 | 0.063831 | -115.4572 | 4.2297 | -115.5762 | -115.535 | 4.4678 | -1.4236 | -0.07782 | 0.19226 | 4.3396 | -115.8005 | 0.11444 | -0.16022 | 0.23346 | 0.15564 | 0.077819 | -0.10986 | -0.050354 | 0.11902 | 115.6128 | 115.8829 | 120.1584 | 119.9203 | 0.23346 | 120.0302 | 114.267 | -0.10986 | 119.9203 | 0.23346 | 114.267 | 120.1584 | 120.0302 | -119.9661 | -120.1904
1055.6406 | 120.2957 | -115.6815 | 4.335 | 0.059128 | 0.014913 | 0.0098373 | 0.0063745 | 0.057744 | -0.0091173 | 0.062763 | -115.4892 | 4.1977 | -115.6494 | -115.5991 | 4.39 | -1.712 | -0.70496 | -0.46234 | 4.2801 | -115.8234 | 0.032044 | -0.13733 | 0.19226 | 0.082398 | 0.054932 | -0.14191 | -0.054932 | 0.16022 | 114.9765 | 115.2191 | 120.0714 | 119.8792 | 0.19226 | 119.9615 | 113.9694 | -0.14191 | 119.8792 | 0.19226 | 113.9694 | 120.0714 | 119.9615 | -119.9844 | -120.1584
1057.3906 | 120.1492 | -115.6952 | 4.39 | -0.047684 | 0.010641 | 0.0068467 | 0.0082971 | 0.056676 | -0.0084765 | 0.066821 | -115.5487 | 4.184 | -115.6998 | -115.6174 | 4.3259 | -1.5472 | -0.31586 | -0.25177 | 4.2847 | -115.8646 | -0.004578 | -0.20599 | 0.14648 | 0.077819 | -0.064087 | -0.16937 | -0.10529 | 0.15106 | 115.3793 | 115.4434 | 120.0211 | 119.8791 | 0.14648 | 119.9799 | 114.1479 | -0.16937 | 119.8791 | 0.14648 | 114.1479 | 120.0211 | 119.9799 | -120.0897 | -120.2545
1059.1406 | 120.2957 | -115.7501 | 4.2938 | -0.062942 | 0.0099996 | 0.0074875 | 0.0010339 | 0.052617 | -0.0076221 | 0.063617 | -115.5624 | 4.1382 | -115.6677 | -115.6494 | 4.3488 | -1.5427 | -0.14648 | 0.068665 | 4.2389 | -115.8966 | 0.082397 | -0.15564 | 0.18768 | 0.10071 | 0.054932 | -0.14648 | -0.054931 | 0.10529 | 115.6036 | 115.8188 | 120.0989 | 119.8883 | 0.18768 | 119.989 | 114.2075 | -0.14648 | 119.8883 | 0.18768 | 114.2075 | 120.0989 | 119.989 | -119.9615 | -120.1904
1060.8906 | 120.3094 | -115.7364 | 4.2114 | 0.11253 | 0.013418 | 0.0087693 | 0.0093653 | 0.056249 | -0.0078357 | 0.064899 | -115.6723 | 4.1199 | -115.7776 | -115.7822 | 4.1794 | -1.8173 | -0.59509 | -0.60883 | 4.2023 | -115.9287 | -0.041199 | -0.091553 | 0.064087 | -0.045777 | -0.032044 | -0.19226 | -0.009155 | 0.10529 | 115.1413 | 115.1276 | 119.9158 | 119.8563 | 0.064087 | 119.9387 | 113.9191 | -0.19226 | 119.8563 | 0.064087 | 113.9191 | 119.9158 | 119.9387 | -119.989 | -120.1401
1062.5781 | 118.2083 | -67.6392 | 50.5096 | -0.16975 | 0.011709 | 0.0064193 | -0.00067514 | 0.049413 | -0.0056995 | 0.06319 | -65.8768 | 51.709 | -65.8447 | -66.9525 | 51.059 | 7.0496 | 3.6667 | 4.3167 | 51.4526 | -66.0919 | 1.7944 | 1.1993 | 1.7624 | 0.68664 | 0.54932 | 1.5472 | 0.94299 | -0.032043 | 71.3058 | 71.9559 | 118.6981 | 119.3481 | 1.7624 | 119.0918 | 74.6887 | 1.5472 | 119.3481 | 1.7624 | 74.6887 | 118.6981 | 119.0918 | -116.3544 | -116.6016
1064.3281 | 116.2766 | -63.8626 | 52.5101 | 0.16594 | 0.010641 | 0.0017197 | 0.0048791 | 0.051763 | -0.0069811 | 0.065112 | -62.8647 | 53.4348 | -62.677 | -64.7781 | 51.6403 | -0.022888 | -0.95673 | -0.83313 | 51.8555 | -64.8651 | 1.1856 | 0.92468 | 0.99792 | -0.91553 | -0.86975 | -1.0025 | -0.6546 | -0.18768 | 62.9059 | 63.0295 | 115.5029 | 117.2974 | 0.99792 | 115.7181 | 63.8397 | -1.0025 | 117.2974 | 0.99792 | 63.8397 | 115.5029 | 115.7181 | -115.1871 | -117.3752
1066.0625 | 120.2637 | -118.689 | 1.1948 | 0.082016 | 0.013418 | 0.0049241 | 0.010647 | 0.054113 | -0.0076221 | 0.065112 | -118.689 | 1.0849 | -118.7988 | -118.7805 | 1.1353 | -2.0233 | -0.50354 | -0.57678 | 1.1719 | -118.9865 | -0.10986 | -0.10986 | 0 | -0.091553 | -0.059509 | -0.29755 | -0.022888 | 0.10986 | 118.1854 | 118.1122 | 119.8242 | 119.7739 | 0 | 119.8608 | 116.6656 | -0.29755 | 119.7739 | 0 | 116.6656 | 119.8242 | 119.8608 | -119.9936 | -120.1813
1067.7656 | 120.401 | -119.5908 | 0.3891 | 0.12016 | 0.014272 | 0.010906 | 0.010433 | 0.053258 | -0.0080493 | 0.065112 | -119.5999 | 0.29755 | -119.6915 | -119.6915 | 0.35248 | -2.0279 | -0.59967 | -0.64545 | 0.37079 | -119.8929 | -0.10071 | -0.091553 | -0.009156 | -0.10071 | -0.036621 | -0.30212 | -0.01831 | 0.091552 | 118.9911 | 118.9453 | 119.9432 | 119.8883 | -0.009156 | 119.9615 | 117.5629 | -0.30212 | 119.8883 | -0.009156 | 117.5629 | 119.9432 | 119.9615 | -120.0806 | -120.282
1069.5156 | 120.369 | -119.7189 | 0.43945 | -0.040054 | 0.013845 | 0.0062057 | 0.0085107 | 0.057531 | -0.010613 | 0.065112 | -119.5953 | 0.29297 | -119.751 | -119.6869 | 0.4303 | -1.8356 | -0.39825 | -0.37994 | 0.39368 | -119.9158 | -0.032044 | -0.14648 | 0.1236 | 0.032043 | -0.009155 | -0.19684 | -0.045776 | 0.15564 | 119.3207 | 119.339 | 120.1492 | 120.0119 | 0.1236 | 120.1126 | 117.8833 | -0.19684 | 120.0119 | 0.1236 | 117.8833 | 120.1492 | 120.1126 | -120.1904 | -120.3552
1071.2031 | 120.433 | -119.8059 | 0.42114 | -0.21553 | 0.012777 | 0.0059921 | 0.0031701 | 0.05454 | -0.0071947 | 0.066608 | -119.7235 | 0.27924 | -119.8242 | -119.7922 | 0.39368 | -1.7029 | 0.10986 | 0.032043 | 0.39825 | -120.0211 | -0.018311 | -0.14191 | 0.082397 | 0.013733 | -0.027466 | -0.21515 | -0.022889 | 0.10071 | 119.9158 | 119.838 | 120.1996 | 120.0851 | 0.082397 | 120.2042 | 118.103 | -0.21515 | 120.0851 | 0.082397 | 118.103 | 120.1996 | 120.2042 | -120.2454 | -120.4422
1072.9688 | 120.5246 | -119.8013 | 0.43488 | 0.12779 | 0.011709 | 0.00086511 | 0.0033839 | 0.05454 | -0.0061267 | 0.064685 | -119.6228 | 0.27008 | -119.783 | -119.7418 | 0.5127 | -1.918 | -0.61798 | -0.36621 | 0.38452 | -119.989 | 0.018311 | -0.16479 | 0.17853 | 0.05951 | 0.07782 | -0.18768 | -0.050354 | 0.16022 | 119.1834 | 119.4351 | 120.314 | 120.0714 | 0.17853 | 120.1859 | 117.8833 | -0.18768 | 120.0714 | 0.17853 | 117.8833 | 120.314 | 120.1859 | -120.2179 | -120.4239
1074.7188 | 120.4742 | -119.902 | 0.42572 | -0.22316 | 0.012136 | 0.0049241 | 0.0044519 | 0.054113 | -0.0074085 | 0.065112 | -119.7189 | 0.25177 | -119.87 | -119.8059 | 0.44861 | -1.6617 | 0.07782 | 0.11444 | 0.37079 | -120.0577 | 0.032044 | -0.17395 | 0.18311 | 0.096131 | 0.022888 | -0.15564 | -0.054931 | 0.15106 | 119.9799 | 120.0165 | 120.3506 | 120.1538 | 0.18311 | 120.2728 | 118.2404 | -0.15564 | 120.1538 | 0.18311 | 118.2404 | 120.3506 | 120.2728 | -120.2957 | -120.4834
1076.4062 | 120.5063 | -119.8791 | 0.4303 | -0.10872 | 0.011709 | 0.0072739 | 0.0061609 | 0.053472 | -0.0048449 | 0.065753 | -119.6823 | 0.2655 | -119.8196 | -119.7464 | 0.54474 | -1.6846 | -0.16937 | 0.10071 | 0.39368 | -120.0485 | 0.059509 | -0.1648 | 0.19684 | 0.13275 | 0.11444 | -0.16937 | -0.036621 | 0.13733 | 119.7098 | 119.9799 | 120.4239 | 120.1447 | 0.19684 | 120.2728 | 118.1946 | -0.16937 | 120.1447 | 0.19684 | 118.1946 | 120.4239 | 120.2728 | -120.2499 | -120.4788
1078.1562 | 120.575 | -119.8791 | 0.44861 | 0.1812 | 0.013845 | 0.0074875 | 0.0091517 | 0.053258 | -0.0095447 | 0.064471 | -119.7556 | 0.31128 | -119.8837 | -119.8288 | 0.48065 | -2.0142 | -0.737 | -0.61798 | 0.42572 | -120.0302 | -0.004578 | -0.13733 | 0.1236 | 0.050354 | 0.032044 | -0.15106 | -0.022888 | 0.12817 | 119.1422 | 119.2612 | 120.3598 | 120.1904 | 0.1236 | 120.3049 | 117.865 | -0.15106 | 120.1904 | 0.1236 | 117.865 | 120.3598 | 120.3049 | -120.3323 | -120.4788
1079.8906 | 120.6345 | -119.838 | 0.48523 | 0.0057222 | 0.011922 | 0.0057785 | 0.0031701 | 0.052617 | -0.0061267 | 0.065112 | -119.7372 | 0.35706 | -119.7968 | -119.8059 | 0.53101 | -1.8768 | -0.31128 | -0.16022 | 0.44403 | -120.0394 | 0.041199 | -0.12817 | 0.10071 | 0.032044 | 0.045777 | -0.20142 | -0.041198 | 0.059509 | 119.5267 | 119.6777 | 120.369 | 120.195 | 0.10071 | 120.282 | 117.9611 | -0.20142 | 120.195 | 0.10071 | 117.9611 | 120.369 | 120.282 | -120.282 | -120.5246
1081.6406 | 120.6299 | -119.8425 | 0.53558 | 0.16594 | 0.010427 | 0.0077011 | 0.01022 | 0.054754 | -0.0076221 | 0.064471 | -119.6503 | 0.39368 | -119.8288 | -119.7327 | 0.60883 | -1.9638 | -0.76904 | -0.55389 | 0.48065 | -119.9799 | 0.013733 | -0.14191 | 0.19226 | 0.10986 | 0.073243 | -0.13733 | -0.054931 | 0.17853 | 119.0735 | 119.2886 | 120.4514 | 120.2362 | 0.19226 | 120.3232 | 117.8787 | -0.13733 | 120.2362 | 0.19226 | 117.8787 | 120.4514 | 120.3232 | -120.3644 | -120.5154
1083.3906 | 120.6024 | -119.8425 | 0.5722 | -0.22316 | 0.010854 | 0.0027877 | 0.010647 | 0.054754 | -0.0082629 | 0.06618 | -119.7464 | 0.44403 | -119.8425 | -119.8059 | 0.55389 | -1.7395 | 0.086975 | -0.004578 | 0.56763 | -120.0256 | 0 | -0.12817 | 0.09613 | 0.036621 | -0.018311 | -0.18311 | -0.004578 | 0.09613 | 119.9295 | 119.838 | 120.3964 | 120.2866 | 0.09613 | 120.4102 | 118.103 | -0.18311 | 120.2866 | 0.09613 | 118.103 | 120.3964 | 120.4102 | -120.4147 | -120.5978
1085.0781 | 120.5841 | -119.8746 | 0.59967 | -0.18501 | 0.012563 | 0.0070603 | 0.0053065 | 0.054113 | -0.0089037 | 0.064899 | -119.6594 | 0.43488 | -119.7693 | -119.7418 | 0.6546 | -1.6617 | 0 | 0.14191 | 0.52643 | -120.0119 | 0.10529 | -0.1648 | 0.21515 | 0.13275 | 0.054932 | -0.13733 | -0.073242 | 0.10986 | 119.8746 | 120.0165 | 120.5292 | 120.3094 | 0.21515 | 120.401 | 118.2129 | -0.13733 | 120.3094 | 0.21515 | 118.2129 | 120.5292 | 120.401 | -120.369 | -120.6116
1086.8281 | 120.7123 | -119.8013 | 0.60883 | 0.082016 | 0.013204 | 0.0057785 | 0.0080835 | 0.054754 | -0.0097583 | 0.064899 | -119.7189 | 0.48065 | -119.8151 | -119.8105 | 0.58594 | -2.0645 | -0.67749 | -0.68665 | 0.59509 | -120.0073 | -0.013732 | -0.12817 | 0.082398 | -0.009155 | -0.022889 | -0.20599 | -0.013733 | 0.09613 | 119.1238 | 119.1147 | 120.3873 | 120.282 | 0.082398 | 120.3964 | 117.7368 | -0.20599 | 120.282 | 0.082398 | 117.7368 | 120.3873 | 120.3964 | -120.4239 | -120.6161
1088.5938 | 120.6162 | -119.8059 | 0.70496 | -0.032425 | 0.011922 | 0.0064193 | 0.0082971 | 0.05454 | -0.0071947 | 0.063403 | -119.6411 | 0.51727 | -119.7968 | -119.7235 | 0.67291 | -1.8677 | -0.44403 | -0.39825 | 0.61798 | -119.9753 | 0.009155 | -0.18768 | 0.16479 | 0.082397 | -0.032043 | -0.16937 | -0.086975 | 0.15564 | 119.3619 | 119.4077 | 120.4788 | 120.3232 | 0.16479 | 120.4239 | 117.9382 | -0.16937 | 120.3232 | 0.16479 | 117.9382 | 120.4788 | 120.4239 | -120.5017 | -120.6802
1090.3438 | 120.6894 | -119.751 | 0.66834 | 0.15068 | 0.014272 | 0.0074875 | 0.0063745 | 0.05454 | -0.0086901 | 0.066394 | -119.6136 | 0.55389 | -119.7739 | -119.7098 | 0.75073 | -2.0142 | -0.80109 | -0.62256 | 0.63171 | -119.9844 | -0.022888 | -0.11444 | 0.13733 | 0.041199 | 0.082397 | -0.23346 | -0.036621 | 0.16022 | 118.9499 | 119.1284 | 120.5017 | 120.3049 | 0.13733 | 120.3827 | 117.7368 | -0.23346 | 120.3049 | 0.13733 | 117.7368 | 120.5017 | 120.3827 | -120.4422 | -120.6528
1092.0938 | 120.639 | -119.7922 | 0.72784 | -0.16212 | 0.011281 | 0.0032151 | 0.0029565 | 0.051977 | -0.0076221 | 0.063831 | -119.5587 | 0.54016 | -119.7052 | -119.6594 | 0.80566 | -1.7029 | -0.12817 | 0.13733 | 0.66376 | -119.9249 | 0.086975 | -0.18768 | 0.23346 | 0.13275 | 0.07782 | -0.13275 | -0.064087 | 0.14648 | 119.664 | 119.9295 | 120.5978 | 120.3323 | 0.23346 | 120.4559 | 118.0893 | -0.13275 | 120.3323 | 0.23346 | 118.0893 | 120.5978 | 120.4559 | -120.433 | -120.6528
1093.8438 | 120.7489 | -119.7968 | 0.68207 | 0.074387 | 0.01299 | 0.0070603 | 0.0093653 | 0.055395 | -0.0099719 | 0.06618 | -119.7006 | 0.56305 | -119.8288 | -119.8105 | 0.64545 | -2.0233 | -0.5722 | -0.66376 | 0.68665 | -119.9707 | -0.032043 | -0.11902 | 0.09613 | -0.013733 | -0.036621 | -0.17395 | 0.004578 | 0.12817 | 119.2245 | 119.133 | 120.4422 | 120.3598 | 0.09613 | 120.4834 | 117.7734 | -0.17395 | 120.3598 | 0.09613 | 117.7734 | 120.4422 | 120.4834 | -120.5109 | -120.6528
1095.5312 | 120.7077 | -119.8654 | 0.70038 | -0.12398 | 0.016408 | 0.0072739 | 0.0050929 | 0.053258 | -0.0076221 | 0.065967 | -119.7052 | 0.55847 | -119.8059 | -119.7968 | 0.68207 | -1.7807 | 0.032043 | -0.009155 | 0.6546 | -120.0348 | 0.059509 | -0.14191 | 0.16022 | 0.068664 | -0.01831 | -0.16937 | -0.045776 | 0.10071 | 119.8975 | 119.8563 | 120.5475 | 120.4239 | 0.16022 | 120.52 | 118.0847 | -0.16937 | 120.4239 | 0.16022 | 118.0847 | 120.5475 | 120.52 | -120.5063 | -120.7352
1097.2656 | 120.7718 | -119.8196 | 0.66376 | 0.082016 | 0.013845 | 0.0087693 | 0.010433 | 0.056035 | -0.0091173 | 0.065112 | -119.7418 | 0.54016 | -119.8654 | -119.8517 | 0.64087 | -2.0462 | -0.56763 | -0.63171 | 0.6546 | -120.0485 | -0.045776 | -0.1236 | 0.07782 | -0.032044 | -0.022888 | -0.22888 | -0.009155 | 0.1236 | 119.252 | 119.1879 | 120.4605 | 120.3598 | 0.07782 | 120.4742 | 117.7734 | -0.22888 | 120.3598 | 0.07782 | 117.7734 | 120.4605 | 120.4742 | -120.5292 | -120.7123
1099.0312 | 120.7764 | -119.9158 | 0.62256 | 0.1049 | 0.012777 | 0.0072739 | 0.0063745 | 0.055822 | -0.0076221 | 0.064044 | -119.7144 | 0.46692 | -119.8517 | -119.7968 | 0.70496 | -2.0279 | -0.84686 | -0.56763 | 0.5722 | -120.0943 | 0.064086 | -0.15564 | 0.20142 | 0.11902 | 0.082397 | -0.17853 | -0.050354 | 0.13733 | 119.0689 | 119.3481 | 120.6207 | 120.3827 | 0.20142 | 120.488 | 117.8879 | -0.17853 | 120.3827 | 0.20142 | 117.8879 | 120.6207 | 120.488 | -120.4742 | -120.7169
1100.7188 | 120.8176 | -119.8608 | 0.59052 | 0.12779 | 0.0093588 | 0.0040695 | 0.0080835 | 0.056249 | -0.0074085 | 0.064685 | -119.8242 | 0.48981 | -119.9341 | -119.9203 | 0.58594 | -2.1103 | -0.71869 | -0.71869 | 0.60883 | -120.1309 | -0.073242 | -0.10071 | 0.036621 | -0.059509 | -0.004578 | -0.27008 | 0.018311 | 0.10986 | 119.1422 | 119.1422 | 120.4468 | 120.3506 | 0.036621 | 120.4697 | 117.7505 | -0.27008 | 120.3506 | 0.036621 | 117.7505 | 120.4468 | 120.4697 | -120.5246 | -120.7214
1102.4688 | 116.3315 | -95.4666 | 20.7275 | -0.23079 | 0.013204 | 0.0027877 | 6.9557 | -0.0071969 | -0.010613 | 7.0134 | -95.343 | 20.6085 | -95.3293 | -0.17395 | 15.1566 | -0.004578 | 0.42572 | 0.20599 | 14.4104 | -87.9547 | 0.13733 | -0.11902 | 0.1236 | 95.2927 | -5.571 | 7.5119 | -6.3171 | -0.013733 | 95.8923 | 95.6726 | 110.6232 | 116.0751 | 0.1236 | 109.877 | 95.462 | 7.5119 | 116.0751 | 0.1236 | 95.462 | 110.6232 | 109.877 | -116.0568 | -108.6823
1104.2344 | 116.0065 | -94.3222 | 21.4188 | 0.043869 | 0.011495 | 0.0064193 | 6.9557 | -0.0091195 | -0.010613 | 7.0134 | -94.3451 | 21.2997 | -94.4046 | -0.009155 | 15.7654 | -0.51727 | -0.16479 | -0.29755 | 14.7491 | -87.236 | -0.082397 | -0.11902 | -0.022888 | 94.313 | -5.6534 | 7.0862 | -6.6696 | 0.059509 | 94.1574 | 94.0247 | 110.0876 | 115.6219 | -0.022888 | 109.0714 | 93.8049 | 7.0862 | 115.6219 | -0.022888 | 93.8049 | 110.0876 | 109.0714 | -115.8234 | -108.6548
1106 | 115.7181 | -93.1 | 22.3434 | 0.20409 | 0.016195 | 0.0068467 | 6.9557 | -0.0074105 | -0.0059131 | 7.0134 | -92.9398 | 21.9955 | -93.1641 | 0.25635 | 16.6443 | -0.77362 | -0.78278 | -0.10986 | 15.4266 | -85.8994 | -0.064086 | -0.3479 | 0.16022 | 93.3563 | -5.6992 | 7.2006 | -6.9168 | 0.2243 | 92.3172 | 92.9901 | 109.7443 | 115.0955 | 0.16022 | 108.5266 | 92.3264 | 7.2006 | 115.0955 | 0.16022 | 92.3264 | 109.7443 | 108.5266 | -115.5075 | -108.2428
1107.6875 | 115.4388 | -93.4204 | 21.9086 | -0.20027 | 0.010641 | 0.0032151 | 6.9557 | -0.0063425 | -0.0093311 | 7.0134 | -92.9901 | 21.6339 | -93.3792 | 0.054932 | 16.2277 | -0.23346 | 0.19226 | 0.20599 | 15.239 | -86.1557 | 0.041199 | -0.27466 | 0.4303 | 93.4753 | -5.6808 | 7.2647 | -6.6696 | 0.3891 | 93.6127 | 93.6264 | 109.6481 | 115.0543 | 0.4303 | 108.6594 | 93.187 | 7.2647 | 115.0543 | 0.4303 | 93.187 | 109.6481 | 108.6594 | -115.2878 | -108.0643
1109.4375 | 115.3931 | -94.0109 | 20.993 | -0.0095368 | 0.011068 | 0.0064193 | 6.9557 | -0.0071969 | -0.0082629 | 7.0134 | -93.5806 | 21.254 | -93.5944 | -0.09613 | 15.8569 | -0.60883 | -0.10071 | -0.082397 | 14.7995 | -86.5356 | 0.41657 | 0.26093 | 0.4303 | 93.9148 | -5.1361 | 7.4753 | -6.1935 | 0.013733 | 93.9102 | 93.9285 | 109.8679 | 115.2649 | 0.4303 | 108.8104 | 93.4021 | 7.4753 | 115.2649 | 0.4303 | 93.4021 | 109.8679 | 108.8104 | -114.5874 | -107.5287
1111.1875 | 115.21 | -94.0292 | 20.9335 | -0.16975 | 0.01235 | 0.0064193 | 6.9557 | -0.0082651 | -0.010186 | 7.0134 | -93.7546 | 20.6589 | -93.9423 | -0.10986 | 15.6601 | -0.31128 | 0.13275 | 0.018311 | 14.4836 | -86.8835 | 0.086975 | -0.27466 | 0.27466 | 93.9194 | -5.2734 | 7.1457 | -6.4499 | 0.18768 | 94.162 | 94.0475 | 109.6893 | 114.6881 | 0.27466 | 108.5129 | 93.718 | 7.1457 | 114.6881 | 0.27466 | 93.718 | 109.6893 | 108.5129 | -114.8758 | -107.8171
1112.9375 | 115.1505 | -94.455 | 20.3247 | 0.020981 | 0.012563 | 0.0068467 | 6.9557 | -0.0074105 | -0.0086901 | 7.0134 | -94.3954 | 20.1645 | -94.4641 | -0.10529 | 15.0055 | -0.75073 | -0.17395 | -0.43488 | 14.1129 | -87.3688 | -0.009155 | -0.16022 | 0.059509 | 94.3497 | -5.3192 | 7.0862 | -6.2119 | 0.068664 | 94.281 | 94.0201 | 109.4604 | 114.6194 | 0.059509 | 108.5678 | 93.7042 | 7.0862 | 114.6194 | 0.059509 | 93.7042 | 109.4604 | 108.5678 | -114.7888 | -107.6935
1114.625 | 115.0269 | -94.5557 | 20.137 | -0.040054 | 0.01235 | 0.0042831 | 6.9557 | -0.0074105 | -0.010826 | 7.0134 | -94.5328 | 19.9448 | -94.5923 | -0.050354 | 14.8407 | -0.7782 | -0.10071 | -0.1831 | 13.9526 | -87.5244 | -0.036621 | -0.19226 | 0.022888 | 94.5053 | -5.2963 | 7.0312 | -6.1844 | 0.059509 | 94.455 | 94.3726 | 109.3964 | 114.5004 | 0.022888 | 108.5083 | 93.7775 | 7.0312 | 114.5004 | 0.022888 | 93.7775 | 109.3964 | 108.5083 | -114.7293 | -107.6614
1116.3594 | 114.83 | -94.043 | 20.6955 | -0.085831 | 0.0082906 | 0.010692 | 6.9557 | -0.0039925 | -0.010826 | 7.0134 | -93.9926 | 20.2744 | -94.2398 | 0.20599 | 15.2115 | -0.94299 | -0.17395 | 0.022888 | 14.4196 | -86.9476 | -0.19684 | -0.42114 | 0.050354 | 94.249 | -5.484 | 7.0953 | -6.2759 | 0.24719 | 93.869 | 94.0659 | 109.2545 | 114.3173 | 0.050354 | 108.4625 | 93.1 | 7.0953 | 114.3173 | 0.050354 | 93.1 | 109.2545 | 108.4625 | -114.9353 | -107.6431
1118.1094 | 114.8117 | -96.6568 | 17.8894 | -0.23079 | 0.013845 | 0.0057785 | 6.9557 | -0.0074105 | -0.0093311 | 7.0134 | -96.579 | 17.7246 | -96.6843 | -0.14191 | 13.2202 | -0.80109 | 0.11902 | -0.13275 | 12.4283 | -89.5294 | -0.027466 | -0.16479 | 0.07782 | 96.5149 | -4.6692 | 7.1274 | -5.4611 | 0.10529 | 96.7758 | 96.524 | 109.877 | 114.3814 | 0.07782 | 109.0851 | 95.8557 | 7.1274 | 114.3814 | 0.07782 | 95.8557 | 109.877 | 109.0851 | -114.5737 | -107.4188
1119.7969 | 114.8987 | -95.9518 | 18.5806 | -0.29182 | 0.0089316 | 0.0062057 | 6.9557 | -0.0074105 | -0.0099719 | 7.0134 | -96.5698 | 18.0176 | -96.3043 | -0.27924 | 13.6963 | -1.2268 | -0.50354 | -0.45319 | 12.767 | -88.9709 | -0.35248 | -0.56305 | -0.61798 | 95.6726 | -4.8843 | 6.9809 | -5.8136 | -0.2655 | 95.4483 | 95.4987 | 109.6481 | 113.9694 | -0.61798 | 108.7189 | 94.725 | 6.9809 | 113.9694 | -0.61798 | 94.725 | 109.6481 | 108.7189 | -114.8849 | -107.5516
1121.5469 | 114.8117 | -97.8561 | 16.6306 | 0.097275 | 0.010641 | 0.0032151 | 6.9557 | -0.0057015 | -0.0095447 | 7.0134 | -97.7875 | 16.4108 | -97.8699 | -0.15564 | 12.2726 | -1.1673 | -0.46234 | -0.66376 | 11.5082 | -90.7654 | -0.013733 | -0.21973 | 0.068664 | 97.7005 | -4.3579 | 7.0908 | -5.1224 | 0.082397 | 97.3938 | 97.1924 | 110.1288 | 114.267 | 0.068664 | 109.3643 | 96.6888 | 7.0908 | 114.267 | 0.068664 | 96.6888 | 110.1288 | 109.3643 | -114.5004 | -107.3959
1123.2969 | 114.7934 | -98.3414 | 16.0584 | 0.089645 | 0.01299 | 0.0019333 | 6.9557 | -0.0071969 | -0.0078357 | 7.0134 | -98.3368 | 15.9348 | -98.41 | -0.23804 | 11.8195 | -1.3458 | -0.62256 | -0.97961 | 11.174 | -91.3193 | -0.068664 | -0.1236 | 0.004578 | 98.1033 | -4.2389 | 7.0221 | -4.8843 | 0.073242 | 97.7188 | 97.3618 | 110.1608 | 114.2761 | 0.004578 | 109.5154 | 96.9955 | 7.0221 | 114.2761 | 0.004578 | 96.9955 | 110.1608 | 109.5154 | -114.4684 | -107.3776
1124.9844 | 114.7705 | -95.0958 | 19.455 | -0.024795 | 0.011495 | 0.0094101 | 6.9557 | -0.0050607 | -0.010399 | 7.0134 | -94.9402 | 19.3085 | -95.1233 | -0.14648 | 14.0259 | -1.2543 | -0.29755 | -0.65002 | 13.5178 | -88.3896 | -0.027466 | -0.14648 | 0.15564 | 94.9493 | -5.4291 | 6.7062 | -5.9372 | 0.1831 | 94.7983 | 94.4458 | 109.1217 | 114.4043 | 0.15564 | 108.6136 | 93.8416 | 6.7062 | 114.4043 | 0.15564 | 93.8416 | 109.1217 | 108.6136 | -114.5782 | -107.8445
1126.7344 | 114.8117 | -97.4945 | 16.9464 | 0.0057222 | 0.014913 | 0.0017197 | 6.9557 | -0.010188 | -0.0061267 | 7.0134 | -97.4258 | 16.8274 | -97.4396 | -0.15564 | 12.5931 | -1.2039 | -0.25177 | -0.50354 | 11.7874 | -90.6235 | 0.054932 | -0.11902 | 0.068665 | 97.3389 | -4.3533 | 6.871 | -5.159 | 0.013733 | 97.2427 | 96.991 | 110.0876 | 114.3219 | 0.068665 | 109.2819 | 96.2906 | 6.871 | 114.3219 | 0.068665 | 96.2906 | 110.0876 | 109.2819 | -114.386 | -107.5699
1128.4844 | 114.8438 | -95.7413 | 18.75 | 0.089645 | 0.012777 | 0.0036423 | 6.9557 | -0.0052743 | -0.010186 | 7.0134 | -95.5811 | 18.5989 | -95.6772 | -0.036621 | 13.9893 | -1.3138 | -0.62714 | -0.85144 | 13.0646 | -89.0259 | 0.064087 | -0.15106 | 0.16022 | 95.7047 | -4.7607 | 6.7154 | -5.6854 | 0.09613 | 95.1141 | 94.8898 | 109.7305 | 114.3402 | 0.16022 | 108.8058 | 94.4275 | 6.7154 | 114.3402 | 0.16022 | 94.4275 | 109.7305 | 108.8058 | -114.4272 | -107.7759
1130.2344 | 114.8483 | -95.668 | 18.8004 | -0.0019073 | 0.011281 | 0.0062057 | 6.9557 | -0.0069833 | -0.011254 | 7.0134 | -95.4575 | 18.8141 | -95.4712 | -0.050354 | 14.0259 | -1.2955 | -0.29297 | -0.59052 | 13.2385 | -88.8428 | 0.19684 | 0.013733 | 0.21057 | 95.6177 | -4.7745 | 6.8253 | -5.5618 | 0.013733 | 95.3751 | 95.0775 | 109.6939 | 114.4821 | 0.21057 | 108.9066 | 94.3726 | 6.8253 | 114.4821 | 0.21057 | 94.3726 | 109.6939 | 108.9066 | -114.2715 | -107.6431
1132 | 114.7202 | -97.9614 | 16.5207 | -0.0019073 | 0.012777 | 0.0064193 | 6.9557 | -0.0052743 | -0.011467 | 7.0134 | -97.9385 | 16.3376 | -97.9889 | -0.20142 | 12.1216 | -1.4465 | -0.49439 | -1.0025 | 11.4807 | -91.1865 | -0.027466 | -0.18311 | 0.022888 | 97.76 | -4.3991 | 6.7749 | -5.04 | 0.050354 | 97.467 | 96.9589 | 110.083 | 114.299 | 0.022888 | 109.4421 | 96.5149 | 6.7749 | 114.299 | 0.022888 | 96.5149 | 110.083 | 109.4421 | -114.5096 | -107.7072
1133.7031 | 114.7018 | -99.5636 | 14.8956 | -0.10872 | 0.011068 | 0.0070603 | 6.9557 | -0.0093331 | -0.010613 | 7.0134 | -99.4446 | 14.6988 | -99.5132 | -0.12817 | 11.0687 | -1.3458 | -0.27008 | -0.46692 | 10.2859 | -92.6285 | 0.050354 | -0.19684 | 0.11902 | 99.4354 | -3.8269 | 6.9351 | -4.6097 | 0.068665 | 99.2935 | 99.0967 | 110.6323 | 114.2624 | 0.11902 | 109.8495 | 98.2178 | 6.9351 | 114.2624 | 0.11902 | 98.2178 | 110.6323 | 109.8495 | -114.4089 | -107.5241
1135.4531 | 114.7568 | -99.9207 | 14.5157 | 0.1812 | 0.009786 | 0.0089829 | 6.9557 | -0.0074105 | -0.010613 | 7.0134 | -99.7604 | 14.3646 | -99.8611 | -0.15564 | 10.7941 | -1.6663 | -0.75989 | -1.0849 | 10.08 | -92.9672 | 0.059509 | -0.15106 | 0.16022 | 99.765 | -3.7216 | 6.9534 | -4.4357 | 0.10071 | 99.1608 | 98.8358 | 110.7147 | 114.2853 | 0.16022 | 110.0006 | 98.2544 | 6.9534 | 114.2853 | 0.16022 | 98.2544 | 110.7147 | 110.0006 | -114.3768 | -107.4829
1137.2031 | 118.0984 | -117.7231 | 0.032043 | 0.17357 | 0.013204 | 0.0032151 | 0.11233 | -0.010401 | -0.0054859 | 0.028156 | -117.6041 | -0.13733 | -117.7689 | 0.041199 | 0.10529 | -2.9984 | -0.87433 | -1.5015 | -0.018311 | -117.952 | -0.045777 | -0.16937 | 0.11902 | 117.7643 | 0.073243 | -0.22888 | -0.050354 | 0.16479 | 116.8488 | 116.2216 | 117.8284 | 117.5858 | 0.11902 | 117.7048 | 114.7247 | -0.22888 | 117.5858 | 0.11902 | 114.7247 | 117.8284 | 117.7048 | -117.8009 | -117.984
1138.9531 | 118.3456 | -117.9932 | 0.045776 | -0.040054 | 0.012563 | 0.0042831 | 0.11041 | -0.011256 | -0.0071947 | 0.027087 | -117.8558 | -0.1236 | -117.9611 | 0 | 0.091553 | -2.8519 | -0.39825 | -1.03 | -0.022888 | -118.19 | 0.032043 | -0.16937 | 0.13733 | 117.9932 | 0.045777 | -0.19684 | -0.068664 | 0.10529 | 117.5949 | 116.9632 | 118.0847 | 117.8696 | 0.13733 | 117.9703 | 115.1413 | -0.19684 | 117.8696 | 0.13733 | 115.1413 | 118.0847 | 117.9703 | -118.0069 | -118.2358
1140.6406 | 118.5013 | -118.1305 | 0.018311 | 0.02861 | 0.012777 | 0.0038559 | 0.11169 | -0.013392 | -0.0065539 | 0.027087 | -118.0069 | -0.11902 | -118.1168 | -0.036621 | 0.059509 | -3.0258 | -0.52185 | -1.2085 | -0.041199 | -118.3594 | 0.013733 | -0.13733 | 0.1236 | 118.0939 | 0.041198 | -0.22888 | -0.05951 | 0.10986 | 117.6086 | 116.922 | 118.19 | 118.0115 | 0.1236 | 118.0893 | 115.1047 | -0.22888 | 118.0115 | 0.1236 | 115.1047 | 118.19 | 118.0893 | -118.1351 | -118.3777
1142.375 | 118.5242 | -118.2953 | 0.059509 | -0.21553 | 0.0099996 | 0.00065151 | 0.11532 | -0.011256 | -0.0074085 | 0.027515 | -118.1534 | -0.09613 | -118.2678 | -0.054932 | 0.018311 | -2.8656 | -0.09613 | -0.79193 | 0.013733 | -118.4235 | 0.027466 | -0.15564 | 0.14191 | 118.2404 | -0.041198 | -0.12817 | -0.045776 | 0.11444 | 118.1992 | 117.5034 | 118.3136 | 118.1992 | 0.14191 | 118.309 | 115.4297 | -0.12817 | 118.1992 | 0.14191 | 115.4297 | 118.3136 | 118.309 | -118.3273 | -118.483
1144.125 | 118.6111 | -118.3914 | 0.041199 | -0.17738 | 0.01299 | 0.0062057 | 0.11959 | -0.011683 | -0.0082629 | 0.02431 | -118.2632 | -0.082397 | -118.4097 | -0.073242 | 0.018311 | -2.9114 | -0.1831 | -0.85602 | 0.009155 | -118.5928 | -0.018311 | -0.1236 | 0.12817 | 118.3182 | -0.022888 | -0.20142 | -0.032044 | 0.14648 | 118.2083 | 117.5354 | 118.4097 | 118.309 | 0.12817 | 118.4006 | 115.48 | -0.20142 | 118.309 | 0.12817 | 115.48 | 118.4097 | 118.4006 | -118.4509 | -118.634
1145.875 | 118.7347 | -118.4555 | 0.022888 | 0.074387 | 0.009786 | 0.0042831 | 0.12365 | -0.0084787 | -0.0074085 | 0.025378 | -118.3685 | -0.10529 | -118.4875 | -0.068665 | -0.027466 | -3.1311 | -0.54016 | -1.2726 | 0.009155 | -118.6523 | -0.032044 | -0.12817 | 0.086975 | 118.3868 | -0.050354 | -0.19684 | -0.013733 | 0.11902 | 117.9153 | 117.1829 | 118.428 | 118.3502 | 0.086975 | 118.4647 | 115.3244 | -0.19684 | 118.3502 | 0.086975 | 115.3244 | 118.428 | 118.4647 | -118.5104 | -118.6752
1147.625 | 118.7668 | -118.5791 | 0.032043 | -0.1545 | 0.01299 | 0.0055649 | 0.12024 | -0.012324 | -0.0069811 | 0.02431 | -118.4372 | -0.073242 | -118.5379 | -0.050354 | 0.018311 | -2.9251 | -0.20142 | -0.78278 | 0.009155 | -118.7256 | 0.041199 | -0.10529 | 0.14191 | 118.5287 | -0.013732 | -0.14648 | -0.022888 | 0.10071 | 118.3777 | 117.7963 | 118.5974 | 118.5059 | 0.14191 | 118.5883 | 115.654 | -0.14648 | 118.5059 | 0.14191 | 115.654 | 118.5974 | 118.5883 | -118.5699 | -118.7576
1149.3281 | 118.9362 | -118.6157 | 0.009155 | 0.12779 | 0.011495 | 0.011333 | 0.12579 | -0.010829 | -0.0054859 | 0.024738 | -118.5471 | -0.086975 | -118.6203 | -0.07782 | -0.022888 | -3.2135 | -0.58594 | -1.2955 | 0.004578 | -118.8538 | -0.004577 | -0.09613 | 0.068665 | 118.5379 | -0.032043 | -0.23804 | -0.004577 | 0.073242 | 118.0298 | 117.3203 | 118.5928 | 118.5287 | 0.068665 | 118.6203 | 115.4022 | -0.23804 | 118.5287 | 0.068665 | 115.4022 | 118.5928 | 118.6203 | -118.6295 | -118.8629
1151.0781 | 118.9545 | -118.7622 | 0.004578 | 0.17357 | 0.012777 | 0.0057785 | 0.052944 | -0.010829 | -0.0054859 | 0.023669 | -118.5516 | -0.14648 | -118.6523 | 0.032043 | 0.10071 | 0.17395 | -0.6546 | -1.0941 | -0.032043 | -118.8812 | 0.10986 | -0.15106 | 0.21057 | 118.7943 | 0.09613 | -0.11902 | -0.036621 | 0.10071 | 118.1076 | 117.6682 | 118.8629 | 118.6157 | 0.21057 | 118.7302 | 118.9362 | -0.11902 | 118.6157 | 0.21057 | 118.9362 | 118.8629 | 118.7302 | -118.6569 | -118.8858
1152.7656 | 119.0689 | -118.8217 | -0.009155 | 0.097275 | 0.011495 | 0.0077011 | 0.058712 | -0.012965 | -0.0086901 | 0.022388 | -118.7393 | -0.10529 | -118.8309 | -0.086975 | -0.054932 | -0.1236 | -0.54932 | -1.2543 | -0.009155 | -119.0186 | -0.009156 | -0.096131 | 0.082397 | 118.7347 | -0.045777 | -0.19684 | 0 | 0.091553 | 118.2724 | 117.5674 | 118.7668 | 118.7164 | 0.082397 | 118.8126 | 118.6981 | -0.19684 | 118.7164 | 0.082397 | 118.6981 | 118.7668 | 118.8126 | -118.8217 | -119.0094
1154.5312 | 119.1696 | -118.8721 | -0.018311 | 0.03624 | 0.01299 | 0.0081283 | 0.052303 | -0.012538 | -0.0044177 | 0.020679 | -118.7393 | -0.14648 | -118.8309 | -0.027466 | 0.054932 | -2.9572 | -0.42114 | -0.97504 | -0.050354 | -119.0781 | 0.041198 | -0.12817 | 0.13275 | 118.8446 | 0.073243 | -0.20599 | -0.032043 | 0.091553 | 118.4509 | 117.897 | 118.927 | 118.7256 | 0.13275 | 118.8217 | 115.9149 | -0.20599 | 118.7256 | 0.13275 | 115.9149 | 118.927 | 118.8217 | -118.8126 | -119.0598
1156.2812 | 119.1101 | -118.9911 | 0.045776 | -0.09346 | 0.010641 | 0.0081283 | 0.059994 | -0.010188 | -0.0078357 | 0.022174 | -118.808 | -0.1236 | -118.9636 | -0.013733 | 0.041199 | -2.9434 | -0.4303 | -0.92926 | -0.009155 | -119.1101 | 0.027466 | -0.16937 | 0.18311 | 118.9774 | -0.004577 | -0.11902 | -0.054931 | 0.15564 | 118.5608 | 118.0618 | 119.0323 | 118.8675 | 0.18311 | 118.9819 | 116.0477 | -0.11902 | 118.8675 | 0.18311 | 116.0477 | 119.0323 | 118.9819 | -119.0094 | -119.1559
1158.0156 | 119.2474 | -119.0094 | -0.009155 | 0.11253 | 0.011709 | 0.0053513 | 0.057858 | -0.0099741 | -0.0091173 | 0.019824 | -118.927 | -0.10986 | -119.046 | -0.07782 | -0.027466 | 0.022888 | -0.47607 | -1.1444 | -0.013733 | -119.2062 | -0.036622 | -0.10071 | 0.082397 | 118.9316 | -0.018311 | -0.19684 | -0.004578 | 0.11902 | 118.5333 | 117.865 | 118.9819 | 118.8995 | 0.082397 | 118.9957 | 119.0323 | -0.19684 | 118.8995 | 0.082397 | 119.0323 | 118.9819 | 118.9957 | -119.0369 | -119.1971
1159.7656 | 119.2474 | -119.101 | 0.036621 | -0.062942 | 0.012563 | 0.0036423 | 0.05978 | -0.0093331 | -0.0084765 | 0.023029 | -118.9316 | -0.13275 | -119.0826 | -0.009155 | 0.041199 | 0.054932 | -0.42114 | -0.91553 | -0.013733 | -119.2749 | 0.01831 | -0.16937 | 0.16937 | 119.0918 | 0.004578 | -0.17395 | -0.050354 | 0.15106 | 118.6798 | 118.1854 | 119.1422 | 118.9682 | 0.16937 | 119.0872 | 119.1559 | -0.17395 | 118.9682 | 0.16937 | 119.1559 | 119.1422 | 119.0872 | -119.1193 | -119.3115
1161.4531 | 119.3573 | -119.1834 | 0.018311 | -0.2079 | 0.011709 | 0.0085555 | 0.053799 | -0.01211 | -0.0052721 | 0.020679 | -119.0826 | -0.11902 | -119.1422 | -0.082397 | -0.009155 | -0.027466 | -0.054932 | -0.62256 | -0.009155 | -119.3802 | 0.041199 | -0.13733 | 0.10071 | 119.101 | -0.027466 | -0.19684 | -0.027466 | 0.059509 | 119.1284 | 118.5608 | 119.1742 | 119.0643 | 0.10071 | 119.1742 | 119.1559 | -0.19684 | 119.0643 | 0.10071 | 119.1559 | 119.1742 | 119.1742 | -119.1605 | -119.3985
1163.2188 | 119.3756 | -119.2474 | 0.018311 | -0.16975 | 0.010641 | 0.0077011 | 0.053372 | -0.012751 | -0.0067675 | 0.019824 | -119.0414 | -0.14191 | -119.165 | 0.041199 | 0.10071 | 0.16022 | -0.17395 | -0.47607 | -0.050354 | -119.3756 | 0.082398 | -0.16022 | 0.20599 | 119.2886 | 0.082397 | -0.12817 | -0.068665 | 0.1236 | 119.0735 | 118.7714 | 119.3481 | 119.1055 | 0.20599 | 119.1971 | 119.4077 | -0.12817 | 119.1055 | 0.20599 | 119.4077 | 119.3481 | 119.1971 | -119.1833 | -119.3939
1164.9062 | 119.5587 | -119.2657 | 0.018311 | 0.0057222 | 0.0099996 | 0.0051377 | 0.05209 | -0.011469 | -0.0056995 | 0.019611 | -119.133 | -0.12817 | -119.2245 | 0.004578 | 0.064087 | 0.086975 | -0.3067 | -0.77362 | -0.032043 | -119.4672 | 0.041199 | -0.14649 | 0.13275 | 119.2703 | 0.045776 | -0.20142 | -0.050354 | 0.091552 | 118.959 | 118.4921 | 119.3298 | 119.1376 | 0.13275 | 119.2337 | 119.3527 | -0.20142 | 119.1376 | 0.13275 | 119.3527 | 119.3298 | 119.2337 | -119.2429 | -119.4855
1166.6562 | 119.5267 | -119.3481 | 0.022888 | -0.032425 | 0.0091452 | 0.010265 | 0.061703 | -0.010188 | -0.010186 | 0.019611 | -119.2017 | -0.13275 | -119.3848 | -0.036621 | -0.004578 | 0.027466 | -0.4715 | -1.0666 | -0.013733 | -119.5038 | -0.036621 | -0.15564 | 0.14648 | 119.3115 | -0.027466 | -0.15564 | -0.036621 | 0.18311 | 118.8766 | 118.2816 | 119.3436 | 119.2154 | 0.14648 | 119.3344 | 119.3756 | -0.15564 | 119.2154 | 0.14648 | 119.3756 | 119.3436 | 119.3344 | -119.4077 | -119.5267
1168.4062 | 119.5862 | -119.4122 | 0.032043 | -0.18501 | 0.012563 | 0.0047103 | 0.056576 | -0.011897 | -0.0069811 | 0.019611 | -119.22 | -0.15106 | -119.339 | 0.009155 | 0.068665 | 0.11444 | -0.13733 | -0.53101 | -0.018311 | -119.6045 | 0.073242 | -0.18311 | 0.19226 | 119.4214 | 0.036622 | -0.19226 | -0.050354 | 0.11902 | 119.2749 | 118.8812 | 119.4809 | 119.2612 | 0.19226 | 119.3939 | 119.5267 | -0.19226 | 119.2612 | 0.19226 | 119.5267 | 119.4809 | 119.3939 | -119.371 | -119.6365
1170.1562 | 119.6045 | -119.4992 | 0.036621 | -0.070572 | 0.011495 | 0.0072739 | 0.061703 | -0.0093331 | -0.010613 | 0.019397 | -119.3024 | -0.14191 | -119.4443 | -0.009155 | 0.059509 | 0.018311 | -0.44403 | -0.93842 | -0.009155 | -119.6091 | 0.054932 | -0.17853 | 0.19684 | 119.4901 | 0.022888 | -0.10986 | -0.045776 | 0.14191 | 119.0552 | 118.5608 | 119.5587 | 119.3573 | 0.19684 | 119.4901 | 119.5175 | -0.10986 | 119.3573 | 0.19684 | 119.5175 | 119.5587 | 119.4901 | -119.4809 | -119.6457
1171.8438 | 119.7006 | -119.5129 | 0.027466 | -0.1545 | 0.010641 | 0.0036423 | 0.056789 | -0.011042 | -0.0091173 | 0.019397 | -119.4122 | -0.10986 | -119.5129 | -0.059509 | 0 | 0.004578 | -0.20142 | -0.76446 | 0 | -119.6777 | 0 | -0.13733 | 0.10071 | 119.4534 | -0.027466 | -0.16479 | -0.027466 | 0.10071 | 119.3115 | 118.7485 | 119.5129 | 119.4031 | 0.10071 | 119.5129 | 119.5175 | -0.16479 | 119.4031 | 0.10071 | 119.5175 | 119.5129 | 119.5129 | -119.5404 | -119.7052
1173.5938 | 119.8242 | -119.545 | 0.009155 | -0.070572 | 0.0095724 | 0.0057785 | 0.051876 | -0.012324 | -0.0042041 | 0.021533 | -119.3939 | -0.14191 | -119.5267 | 0.018311 | 0.09613 | -0.10071 | -0.27924 | -0.73242 | -0.027466 | -119.7464 | 0.018311 | -0.15106 | 0.15106 | 119.5633 | 0.086975 | -0.20142 | -0.036621 | 0.13275 | 119.2657 | 118.8126 | 119.6411 | 119.4031 | 0.15106 | 119.5175 | 119.4443 | -0.20142 | 119.4031 | 0.15106 | 119.4443 | 119.6411 | 119.5175 | -119.5358 | -119.7556
1175.3438 | 119.8105 | -119.6228 | 0.013733 | -0.16975 | 0.011922 | 0.0062057 | 0.060421 | -0.011897 | -0.0093311 | 0.020679 | -119.5038 | -0.10071 | -119.6503 | -0.050354 | -0.004578 | 0.064087 | -0.2243 | -0.79193 | 0.004578 | -119.8105 | -0.027466 | -0.11444 | 0.11902 | 119.5724 | -0.018311 | -0.18768 | -0.009155 | 0.14648 | 119.3985 | 118.8309 | 119.6182 | 119.5221 | 0.11902 | 119.6274 | 119.6869 | -0.18768 | 119.5221 | 0.11902 | 119.6869 | 119.6182 | 119.6274 | -119.664 | -119.8242
1177.1094 | 119.8517 | -119.6457 | 0.018311 | -0.1545 | 0.011281 | 0.0032151 | 0.057217 | -0.01446 | -0.0091173 | 0.018756 | -119.5633 | -0.11444 | -119.6823 | -0.068665 | -0.004578 | -0.059509 | -0.20599 | -0.79651 | -0.013733 | -119.8517 | -0.036621 | -0.13275 | 0.082398 | 119.577 | -0.022889 | -0.20599 | -0.032044 | 0.11902 | 119.4397 | 118.8492 | 119.6411 | 119.5312 | 0.082398 | 119.632 | 119.5862 | -0.20599 | 119.5312 | 0.082398 | 119.5862 | 119.6411 | 119.632 | -119.7006 | -119.87
1178.8594 | 119.9112 | -119.7098 | 0 | -0.19264 | 0.01299 | 0.0094101 | 0.058926 | -0.012751 | -0.0067675 | 0.019824 | -119.6182 | -0.09613 | -119.6823 | -0.082397 | -0.022888 | 0.041199 | -0.15106 | -0.7782 | 0.013733 | -119.9249 | 0.027466 | -0.09613 | 0.091553 | 119.6274 | -0.022888 | -0.21515 | 0.013733 | 0.064087 | 119.5587 | 118.9316 | 119.6869 | 119.6136 | 0.091553 | 119.7235 | 119.751 | -0.21515 | 119.6136 | 0.091553 | 119.751 | 119.6869 | 119.7235 | -119.6823 | -119.9249
1180.5469 | 119.9615 | -119.751 | 0.032043 | -0.19264 | 0.012777 | 0.0066329 | 0.058926 | -0.010829 | -0.0065539 | 0.020252 | -119.6503 | -0.10529 | -119.7464 | -0.073242 | -0.018311 | -0.036621 | -0.17395 | -0.83313 | -0.013733 | -119.9432 | 0.004578 | -0.13733 | 0.10071 | 119.6777 | -0.050354 | -0.19226 | -0.045776 | 0.09613 | 119.577 | 118.9178 | 119.7327 | 119.6457 | 0.10071 | 119.7372 | 119.7144 | -0.19226 | 119.6457 | 0.10071 | 119.7144 | 119.7327 | 119.7372 | -119.7784 | -119.9753
1182.2969 | 120.0531 | -119.7693 | 0.009155 | 0.066757 | 0.011281 | 0.0021469 | 0.060635 | -0.0099741 | -0.01104 | 0.018329 | -119.6869 | -0.10986 | -119.8105 | -0.10529 | -0.059509 | 0.018311 | -0.5127 | -1.3962 | 0.004578 | -119.9844 | -0.041199 | -0.11902 | 0.082397 | 119.664 | -0.068664 | -0.21515 | -0.004577 | 0.1236 | 119.2566 | 118.3731 | 119.7098 | 119.6594 | 0.082397 | 119.7739 | 119.7876 | -0.21515 | 119.6594 | 0.082397 | 119.7876 | 119.7098 | 119.7739 | -119.8196 | -119.9936
1183.9844 | 120.0897 | -119.8105 | 0.009155 | 0.18883 | 0.011281 | 0.0089829 | 0.057858 | -0.0099741 | -0.0063403 | 0.020679 | -119.7189 | -0.13275 | -119.8242 | -0.045776 | 0.036621 | 0.10071 | -0.66376 | -1.4465 | -0.013733 | -119.989 | -0.013733 | -0.14191 | 0.091553 | 119.7647 | 0.027466 | -0.17853 | -0.022888 | 0.10529 | 119.1467 | 118.364 | 119.8471 | 119.6777 | 0.091553 | 119.7968 | 119.9112 | -0.17853 | 119.6777 | 0.091553 | 119.9112 | 119.8471 | 119.7968 | -119.8334 | -119.9982
1185.7344 | 120.1218 | -119.8791 | 0.022888 | 0.097275 | 0.012563 | 0.0072739 | 0.054867 | -0.010829 | -0.0071947 | 0.020252 | -119.6823 | -0.16022 | -119.7968 | 0.018311 | 0.07782 | 0.14648 | -0.6134 | -1.3 | -0.045776 | -120.0531 | 0.082397 | -0.1831 | 0.19684 | 119.8975 | 0.054932 | -0.17395 | -0.068664 | 0.11444 | 119.2657 | 118.5791 | 119.957 | 119.7189 | 0.19684 | 119.8334 | 120.0256 | -0.17395 | 119.7189 | 0.19684 | 120.0256 | 119.957 | 119.8334 | -119.8196 | -120.076
1187.4219 | 120.1996 | -119.8975 | 0.004578 | 0.12779 | 0.010427 | 0.0053513 | 0.058712 | -0.0080515 | -0.0093311 | 0.01897 | -119.8013 | -0.11902 | -119.9341 | -0.059509 | 0 | 0.059509 | -0.62256 | -1.561 | -0.004578 | -120.0897 | -0.036621 | -0.1236 | 0.09613 | 119.838 | -0.004578 | -0.19226 | -0.009156 | 0.13275 | 119.2749 | 118.3365 | 119.8975 | 119.7784 | 0.09613 | 119.8929 | 119.957 | -0.19226 | 119.7784 | 0.09613 | 119.957 | 119.8975 | 119.8929 | -119.9387 | -120.0943
1189.1719 | 120.2316 | -119.9249 | 0.009155 | 0.082016 | 0.010854 | 0.0081283 | 0.054867 | -0.010615 | -0.0069811 | 0.018329 | -119.7784 | -0.15106 | -119.8883 | 0 | 0.059509 | 0.14191 | -0.54474 | -1.3229 | -0.032043 | -120.1309 | 0.036621 | -0.16022 | 0.14648 | 119.9249 | 0.050354 | -0.20599 | -0.041198 | 0.10986 | 119.3802 | 118.602 | 119.9844 | 119.7739 | 0.14648 | 119.8929 | 120.0668 | -0.20599 | 119.7739 | 0.14648 | 120.0668 | 119.9844 | 119.8929 | -119.8975 | -120.1401
1190.9219 | 120.2728 | -119.9615 | 0 | 0.12016 | 0.011709 | 0.0070603 | 0.060848 | -0.011683 | -0.0082629 | 0.01897 | -119.8837 | -0.13275 | -120.0073 | -0.064087 | -0.013733 | 0.054932 | -0.92468 | -0.96588 | -0.013733 | -120.163 | -0.045776 | -0.13275 | 0.07782 | 119.8975 | -0.013733 | -0.20142 | -0.013733 | 0.1236 | 119.0369 | 118.9957 | 119.9478 | 119.8288 | 0.07782 | 119.9478 | 120.0165 | -0.20142 | 119.8288 | 0.07782 | 120.0165 | 119.9478 | 119.9478 | -120.0073 | -120.163
1192.6094 | 120.2728 | -120.0256 | 0.018311 | 0.15831 | 0.0095724 | 0.0062057 | 0.058498 | -0.0097605 | -0.0080493 | 0.01897 | -119.8288 | -0.16022 | -120.0165 | 0.041199 | 0.091553 | 0.1831 | -1.0208 | -0.76446 | -0.059509 | -120.1721 | 0.009156 | -0.17853 | 0.19684 | 120.0668 | 0.073242 | -0.14648 | -0.07782 | 0.18768 | 119.0048 | 119.2612 | 120.1172 | 119.8654 | 0.19684 | 119.9661 | 120.2087 | -0.14648 | 119.8654 | 0.19684 | 120.2087 | 120.1172 | 119.9661 | -120.0348 | -120.1904
1194.3594 | 120.2499 | -120.0668 | 0.009155 | -0.0019073 | 0.011068 | 0.0070603 | 0.061489 | -0.012538 | -0.0086901 | 0.017474 | -119.9341 | -0.12817 | -120.076 | -0.059509 | -0.009155 | 0.045776 | -0.8194 | -0.86975 | -0.004578 | -120.2499 | -0.009156 | -0.13733 | 0.13275 | 120.0073 | -0.01831 | -0.18311 | -0.013733 | 0.14191 | 119.2474 | 119.1971 | 120.0577 | 119.9387 | 0.13275 | 120.0623 | 120.1126 | -0.18311 | 119.9387 | 0.13275 | 120.1126 | 120.0577 | 120.0623 | -120.0851 | -120.2591
1196.125 | 120.2957 | -120.108 | 0.059509 | -0.10872 | 0.010427 | 0.0038559 | 0.053799 | -0.014033 | -0.0080493 | 0.01897 | -119.902 | -0.16022 | -120.0348 | 0.050354 | 0.13733 | 0.19226 | -0.64545 | -0.36621 | -0.050354 | -120.2866 | 0.073242 | -0.21973 | 0.20599 | 120.1584 | 0.07782 | -0.17853 | -0.10986 | 0.13275 | 119.4626 | 119.7418 | 120.2454 | 119.9478 | 0.20599 | 120.0577 | 120.3003 | -0.17853 | 119.9478 | 0.20599 | 120.3003 | 120.2454 | 120.0577 | -120.0943 | -120.3461
1197.8281 | 120.4422 | -120.1126 | 0.009155 | 0.043869 | 0.011495 | 0.0040695 | 0.057644 | -0.01446 | -0.0080493 | 0.017688 | -119.9799 | -0.14648 | -120.1035 | -0.013733 | 0.045776 | 0.07782 | -0.78278 | -0.67291 | -0.032043 | -120.3094 | 0.009155 | -0.15564 | 0.13275 | 120.0989 | 0.036621 | -0.19684 | -0.041198 | 0.1236 | 119.3298 | 119.4397 | 120.1584 | 119.9661 | 0.13275 | 120.0806 | 120.1904 | -0.19684 | 119.9661 | 0.13275 | 120.1904 | 120.1584 | 120.0806 | -120.1126 | -120.3186
1199.7188 | 120.4742 | -120.1401 | 0 | 0.1049 | 0.010854 | 0.0062057 | 0.060635 | -0.013178 | -0.0061267 | 0.01897 | -120.0668 | -0.11444 | -120.195 | -0.07782 | -0.032043 | 0.041199 | -1.03 | -1.0849 | 0.004578 | -120.369 | -0.054931 | -0.11444 | 0.073243 | 120.0623 | -0.032043 | -0.22888 | 0.004578 | 0.12817 | 119.1101 | 119.0552 | 120.108 | 120.0256 | 0.073243 | 120.1447 | 120.1813 | -0.22888 | 120.0256 | 0.073243 | 120.1813 | 120.108 | 120.1447 | -120.195 | -120.369
1201.4688 | 120.4926 | -120.1767 | -0.009155 | 0.066757 | 0.011281 | 0.0068467 | 0.055294 | -0.013178 | -0.0076221 | 0.018115 | -120.0668 | -0.15564 | -120.1538 | -0.022888 | 0.041199 | 0.11902 | -0.90637 | -0.78278 | -0.045776 | -120.3644 | 0.022888 | -0.14649 | 0.10986 | 120.1538 | 0.050354 | -0.18768 | -0.036621 | 0.086976 | 119.2703 | 119.3939 | 120.2179 | 120.0211 | 0.10986 | 120.1309 | 120.2957 | -0.18768 | 120.0211 | 0.10986 | 120.2957 | 120.2179 | 120.1309 | -120.1447 | -120.3552
1203.2188 | 120.3873 | -120.2637 | 0.027466 | -0.1545 | 0.010213 | 0.0038559 | 0.058285 | -0.014247 | -0.0067675 | 0.016834 | -120.0348 | -0.15564 | -120.1813 | 0.036621 | 0.10071 | 0.15106 | -0.6958 | -0.50812 | -0.045776 | -120.401 | 0.082398 | -0.18311 | 0.22888 | 120.3003 | 0.073242 | -0.13733 | -0.073242 | 0.14648 | 119.5679 | 119.7556 | 120.3644 | 120.108 | 0.22888 | 120.2179 | 120.4147 | -0.13733 | 120.108 | 0.22888 | 120.4147 | 120.3644 | 120.2179 | -120.2087 | -120.4285
1204.9688 | 120.4559 | -120.2591 | 0.041199 | -0.17738 | 0.008718 | 0.0049241 | 0.060207 | -0.01446 | -0.0071947 | 0.018115 | -120.163 | -0.12817 | -120.2637 | -0.073242 | 0 | 0.041199 | -0.49439 | -0.56305 | -0.009155 | -120.4926 | -0.004578 | -0.16937 | 0.09613 | 120.1859 | -0.041199 | -0.23346 | -0.050354 | 0.10071 | 119.7647 | 119.696 | 120.2591 | 120.1309 | 0.09613 | 120.2499 | 120.3003 | -0.23346 | 120.1309 | 0.09613 | 120.3003 | 120.2591 | 120.2499 | -120.3049 | -120.5338
1206.7188 | 120.575 | -120.2682 | 0 | 0.1049 | 0.013418 | 0.0057785 | 0.056149 | -0.015101 | -0.0086901 | 0.017047 | -120.1309 | -0.14191 | -120.2408 | -0.004578 | 0.054932 | 0.11444 | -0.91095 | -0.75989 | -0.041199 | -120.433 | 0.027466 | -0.14191 | 0.13733 | 120.2637 | 0.054932 | -0.16479 | -0.041199 | 0.10986 | 119.3573 | 119.5084 | 120.3232 | 120.1263 | 0.13733 | 120.2271 | 120.3827 | -0.16479 | 120.1263 | 0.13733 | 120.3827 | 120.3232 | 120.2271 | -120.2408 | -120.433
1208.4688 | 120.4559 | -120.3278 | 0.018311 | -0.085831 | 0.010427 | 0.0044967 | 0.065121 | -0.012324 | -0.01104 | 0.01897 | -120.1584 | -0.12817 | -120.3644 | 0 | 0.036621 | 0.09613 | -0.85144 | -0.82855 | -0.013733 | -120.52 | -0.036621 | -0.14649 | 0.16937 | 120.3278 | 0.01831 | -0.19226 | -0.032044 | 0.20599 | 119.4763 | 119.4992 | 120.3644 | 120.1996 | 0.16937 | 120.314 | 120.4239 | -0.19226 | 120.1996 | 0.16937 | 120.4239 | 120.3644 | 120.314 | -120.3827 | -120.5383
1210.1562 | 120.5795 | -120.3415 | -0.013733 | 0.1812 | 0.0093588 | 0.0091965 | 0.059567 | -0.011256 | -0.0069811 | 0.018115 | -120.163 | -0.16479 | -120.3369 | 0.027466 | 0.07782 | 0.15564 | -1.1627 | -0.95215 | -0.045776 | -120.5292 | 0.004578 | -0.15106 | 0.17853 | 120.369 | 0.091553 | -0.18768 | -0.032043 | 0.17395 | 119.1788 | 119.3893 | 120.4193 | 120.1767 | 0.17853 | 120.2957 | 120.4971 | -0.18768 | 120.1767 | 0.17853 | 120.4971 | 120.4193 | 120.2957 | -120.3232 | -120.5154
1211.9062 | 120.5292 | -120.4285 | 0.032043 | -0.18501 | 0.011068 | 0.0074875 | 0.056362 | -0.012751 | -0.0076221 | 0.017902 | -120.1904 | -0.13733 | -120.3323 | 0.059509 | 0.1236 | 0.15564 | -0.72327 | -0.52185 | -0.045776 | -120.52 | 0.096131 | -0.16937 | 0.23804 | 120.488 | 0.091553 | -0.091553 | -0.077819 | 0.14191 | 119.7052 | 119.9066 | 120.5521 | 120.2911 | 0.23804 | 120.3827 | 120.5841 | -0.091553 | 120.2911 | 0.23804 | 120.5841 | 120.5521 | 120.3827 | -120.3644 | -120.5521
1213.6562 | 120.6573 | -120.3873 | -0.004578 | 0.12779 | 0.014058 | 0.0040695 | 0.062771 | -0.013819 | -0.0091173 | 0.018756 | -120.2728 | -0.13275 | -120.3964 | -0.059509 | -0.004578 | 0.082397 | -1.1627 | -1.1307 | -0.004578 | -120.5978 | -0.009155 | -0.12817 | 0.11444 | 120.3278 | 0 | -0.21057 | 0 | 0.1236 | 119.2245 | 119.2566 | 120.3827 | 120.2545 | 0.11444 | 120.3827 | 120.4697 | -0.21057 | 120.2545 | 0.11444 | 120.4697 | 120.3827 | 120.3827 | -120.3918 | -120.5933
1215.3594 | 120.6665 | -120.4193 | 0.004578 | 0.1049 | 0.010427 | 0.0030013 | 0.057217 | -0.01211 | -0.0065539 | 0.016193 | -120.2362 | -0.16022 | -120.3918 | 0.027466 | 0.086975 | 0.16937 | -1.1856 | -0.97046 | -0.036621 | -120.5933 | 0.027466 | -0.16479 | 0.18311 | 120.4468 | 0.082397 | -0.17395 | -0.041199 | 0.15564 | 119.2337 | 119.4489 | 120.5063 | 120.2591 | 0.18311 | 120.3827 | 120.5887 | -0.17395 | 120.2591 | 0.18311 | 120.5887 | 120.5063 | 120.3827 | -120.3964 | -120.5978
1217.1094 | 120.694 | -120.4514 | 0.004578 | 0.15831 | 0.0099996 | 0.0027877 | 0.057858 | -0.012751 | -0.0063403 | 0.017474 | -120.2499 | -0.1831 | -120.4239 | 0.045776 | 0.10529 | 0.14648 | -1.2497 | -1.0117 | -0.032043 | -120.6207 | 0.027466 | -0.18768 | 0.20142 | 120.4971 | 0.10071 | -0.16937 | -0.036621 | 0.17395 | 119.2017 | 119.4397 | 120.5566 | 120.2683 | 0.20142 | 120.4193 | 120.5978 | -0.16937 | 120.2683 | 0.20142 | 120.5978 | 120.5566 | 120.4193 | -120.4285 | -120.6253
1218.7969 | 120.726 | -120.4605 | 0.004578 | 0.1812 | 0.010213 | 0.0094101 | 0.062771 | -0.014247 | -0.0091173 | 0.018329 | -120.3461 | -0.1236 | -120.4651 | -0.022888 | 0.032043 | 0.10529 | -1.2634 | -1.1719 | -0.032043 | -120.6528 | -0.004578 | -0.12817 | 0.11444 | 120.4376 | 0.027465 | -0.19226 | -0.036621 | 0.11902 | 119.1971 | 119.2886 | 120.4926 | 120.3369 | 0.11444 | 120.4285 | 120.5658 | -0.19226 | 120.3369 | 0.11444 | 120.5658 | 120.4926 | 120.4285 | -120.4697 | -120.6573
1220.5469 | 120.6894 | -120.52 | 0.013733 | -0.017166 | 0.014486 | 0.0066329 | 0.062557 | -0.011683 | -0.0089037 | 0.019611 | -120.3735 | -0.14191 | -120.52 | -0.041199 | 0.022888 | 0.013733 | -1.0803 | -1.1078 | -0.022888 | -120.6619 | 0 | -0.15564 | 0.14648 | 120.4788 | 0.009155 | -0.14191 | -0.036621 | 0.14648 | 119.4397 | 119.4122 | 120.5429 | 120.3781 | 0.14648 | 120.4971 | 120.5338 | -0.14191 | 120.3781 | 0.14648 | 120.5338 | 120.5429 | 120.4971 | -120.5338 | -120.6757
1222.25 | 120.7397 | -120.5063 | 0.004578 | 0.1049 | 0.012563 | 0.0038559 | 0.05978 | -0.0091195 | -0.0080493 | 0.018543 | -120.4285 | -0.1236 | -120.5429 | -0.073242 | -0.004578 | 0.013733 | -1.1078 | -1.1993 | -0.004578 | -120.7214 | -0.036621 | -0.12817 | 0.07782 | 120.433 | -0.009156 | -0.21515 | -0.009156 | 0.11444 | 119.3985 | 119.3069 | 120.5017 | 120.3827 | 0.07782 | 120.5017 | 120.52 | -0.21515 | 120.3827 | 0.07782 | 120.52 | 120.5017 | 120.5017 | -120.5475 | -120.726
1224 | 120.7214 | -120.5795 | 0.018311 | -0.16975 | 0.01235 | 0.0038559 | 0.053158 | -0.011042 | -0.0089037 | 0.018756 | -120.3644 | -0.15106 | -120.5017 | 0.050354 | 0.12817 | 0.15564 | -0.87433 | -0.6958 | -0.059509 | -120.7672 | 0.07782 | -0.16937 | 0.21515 | 120.6299 | 0.10986 | -0.18768 | -0.07782 | 0.13733 | 119.7052 | 119.8837 | 120.7077 | 120.4285 | 0.21515 | 120.52 | 120.7352 | -0.18768 | 120.4285 | 0.21515 | 120.7352 | 120.7077 | 120.52 | -120.52 | -120.7855
1225.75 | 120.8542 | -120.5429 | -0.013733 | 0.051498 | 0.010427 | 0.0042831 | 0.057003 | -0.013606 | -0.0069811 | 0.01662 | -120.4285 | -0.15564 | -120.5429 | -0.022888 | 0.068665 | 0.086975 | -1.0803 | -0.97046 | -0.018311 | -120.7306 | 0 | -0.14191 | 0.11444 | 120.52 | 0.082398 | -0.18768 | -0.004578 | 0.11444 | 119.4626 | 119.5724 | 120.6116 | 120.3873 | 0.11444 | 120.5246 | 120.6299 | -0.18768 | 120.3873 | 0.11444 | 120.6299 | 120.6116 | 120.5246 | -120.5292 | -120.7169
1227.5 | 120.726 | -120.6024 | 0.036621 | -0.085831 | 0.008718 | 0.0053513 | 0.060207 | -0.013392 | -0.010826 | 0.017688 | -120.4376 | -0.13733 | -120.6024 | -0.004578 | 0.054932 | 0.064087 | -1.0574 | -1.0254 | -0.009155 | -120.7626 | 0 | -0.17395 | 0.16479 | 120.5978 | 0.018311 | -0.16022 | -0.045776 | 0.16479 | 119.545 | 119.577 | 120.6573 | 120.4651 | 0.16479 | 120.5933 | 120.6665 | -0.16022 | 120.4651 | 0.16479 | 120.6665 | 120.6573 | 120.5933 | -120.639 | -120.7993
1229.2031 | 120.8359 | -120.6299 | 0.032043 | -0.10872 | 0.014272 | 0.0030013 | 0.052517 | -0.013819 | -0.0054859 | 0.017047 | -120.4239 | -0.15106 | -120.5704 | 0.041199 | 0.11444 | 0.13275 | -0.99792 | -0.7782 | -0.022888 | -120.7901 | 0.059509 | -0.18311 | 0.20599 | 120.6711 | 0.082398 | -0.16022 | -0.054931 | 0.14648 | 119.632 | 119.8517 | 120.7443 | 120.4788 | 0.20599 | 120.607 | 120.7626 | -0.16022 | 120.4788 | 0.20599 | 120.7626 | 120.7443 | 120.607 | -120.6024 | -120.8221
1230.9375 | 120.7672 | -120.6253 | 0.022888 | -0.078201 | 0.011068 | 0.0068467 | 0.063625 | -0.013819 | -0.010399 | 0.018115 | -120.488 | -0.12817 | -120.6711 | -0.013733 | 0.036621 | 0.091553 | -1.1124 | -1.0803 | -0.018311 | -120.8359 | -0.045777 | -0.15106 | 0.13733 | 120.6116 | 0.013733 | -0.21057 | -0.041199 | 0.18311 | 119.5129 | 119.545 | 120.6619 | 120.4971 | 0.13733 | 120.607 | 120.7169 | -0.21057 | 120.4971 | 0.13733 | 120.7169 | 120.6619 | 120.607 | -120.694 | -120.8588
1232.6875 | 120.8954 | -120.6345 | 0.009155 | 0.097275 | 0.013631 | 0.0072739 | 0.058071 | -0.015101 | -0.0048449 | 0.01662 | -120.4605 | -0.14648 | -120.5887 | 0.027466 | 0.11444 | -1.0849 | -1.3 | -1.0712 | -0.045776 | -120.8588 | 0.045776 | -0.15564 | 0.17395 | 120.6619 | 0.10529 | -0.22431 | -0.054931 | 0.12817 | 119.3344 | 119.5633 | 120.7489 | 120.488 | 0.17395 | 120.5887 | 119.5496 | -0.22431 | 120.488 | 0.17395 | 119.5496 | 120.7489 | 120.5887 | -120.5978 | -120.8679
1234.4531 | 120.8633 | -120.694 | 0.036621 | -0.10872 | 0.011281 | 0.0062057 | 0.053799 | -0.015101 | -0.0067675 | 0.017047 | -120.4697 | -0.15564 | -120.6345 | 0.045776 | 0.12817 | -4.2847 | -1.1169 | -0.87433 | -0.036621 | -120.8725 | 0.05951 | -0.19226 | 0.2243 | 120.7397 | 0.091553 | -0.17853 | -0.073242 | 0.16479 | 119.577 | 119.8196 | 120.8221 | 120.5383 | 0.2243 | 120.6573 | 116.4093 | -0.17853 | 120.5383 | 0.2243 | 116.4093 | 120.8221 | 120.6573 | -120.6711 | -120.9091
1236.1406 | 120.9045 | -120.7031 | 0.018311 | -0.23079 | 0.011922 | 0.0049241 | 0.060207 | -0.015101 | -0.0061267 | 0.017261 | -120.5887 | -0.10529 | -120.726 | -0.073242 | 0.022888 | -0.082397 | -0.98419 | -1.0849 | 0 | -120.9229 | -0.022888 | -0.1236 | 0.11444 | 120.6299 | 0.004577 | -0.21973 | -0.018311 | 0.13733 | 119.7189 | 119.6182 | 120.726 | 120.5978 | 0.11444 | 120.7031 | 120.6207 | -0.21973 | 120.5978 | 0.11444 | 120.6207 | 120.726 | 120.7031 | -120.7443 | -120.9412
1237.8906 | 120.8862 | -120.7443 | 0.018311 | -0.13161 | 0.011068 | 0.0032151 | 0.057003 | -0.01681 | -0.0086901 | 0.017261 | -120.5109 | -0.15106 | -120.6802 | 0.054932 | 0.13275 | 0.082397 | -1.1444 | -0.91095 | -0.050354 | -120.8771 | 0.064087 | -0.16937 | 0.23346 | 120.7993 | 0.11444 | -0.13275 | -0.068665 | 0.16937 | 119.5999 | 119.8334 | 120.8771 | 120.5933 | 0.23346 | 120.694 | 120.8267 | -0.13275 | 120.5933 | 0.23346 | 120.8267 | 120.8771 | 120.694 | -120.6985 | -120.8954
1239.6562 | 120.9 | -120.7306 | 0.036621 | -0.070572 | 0.010854 | 0.0062057 | 0.062344 | -0.012538 | -0.0086901 | 0.017261 | -120.575 | -0.1236 | -120.7764 | 0.004578 | 0.050354 | -6.1432 | -1.3641 | -1.3229 | -0.032043 | -120.8725 | -0.045776 | -0.16022 | 0.15564 | 120.7352 | 0.013733 | -0.14191 | -0.068664 | 0.20142 | 119.3665 | 119.4077 | 120.7809 | 120.607 | 0.15564 | 120.6985 | 114.5874 | -0.14191 | 120.607 | 0.15564 | 114.5874 | 120.7809 | 120.6985 | -120.813 | -120.9091
1241.3438 | 120.9229 | -120.7855 | 0.036621 | -0.14687 | 0.011495 | 0.0070603 | 0.055508 | -0.01446 | -0.0074085 | 0.018543 | -120.5612 | -0.16479 | -120.6894 | 0.036621 | 0.13733 | -6.5689 | -1.2451 | -1.0071 | -0.045776 | -120.932 | 0.09613 | -0.20142 | 0.2243 | 120.8221 | 0.10071 | -0.14648 | -0.082397 | 0.12817 | 119.5404 | 119.7784 | 120.9229 | 120.6207 | 0.2243 | 120.7397 | 114.2166 | -0.14648 | 120.6207 | 0.2243 | 114.2166 | 120.9229 | 120.7397 | -120.726 | -120.9686
1243.0938 | 120.9824 | -120.7947 | 0.022888 | -0.19264 | 0.011495 | 0.00022431 | 0.059139 | -0.012751 | -0.0078357 | 0.017261 | -120.6848 | -0.11444 | -120.8313 | -0.064087 | 0.018311 | -7.0541 | -1.1536 | -1.2817 | 0.004578 | -120.9641 | -0.036621 | -0.13733 | 0.10986 | 120.7306 | -0.004577 | -0.16937 | -0.01831 | 0.14648 | 119.6411 | 119.5129 | 120.813 | 120.6802 | 0.10986 | 120.7993 | 113.7405 | -0.16937 | 120.6802 | 0.10986 | 113.7405 | 120.813 | 120.7993 | -120.8542 | -120.9869
1245.4688 | 121.0464 | -120.7718 | 0.018311 | -0.032425 | 0.010854 | -0.00063009 | 0.055508 | -0.013606 | -0.0039905 | 0.018115 | -120.6345 | -0.14648 | -120.7855 | 0.004578 | 0.10986 | -7.0816 | -1.3458 | -1.1673 | -0.036621 | -121.0007 | -0.013732 | -0.16479 | 0.13733 | 120.7764 | 0.091552 | -0.22888 | -0.054932 | 0.15106 | 119.426 | 119.6045 | 120.8817 | 120.6253 | 0.13733 | 120.7352 | 113.6902 | -0.22888 | 120.6253 | 0.13733 | 113.6902 | 120.8817 | 120.7352 | -120.8038 | -121.019
1248.7812 | 121.0648 | -120.8038 | 0 | 0.074387 | 0.0091452 | 0.0055649 | 0.063625 | -0.011897 | -0.0093311 | 0.01662 | -120.726 | -0.11444 | -120.8496 | -0.082397 | -0.018311 | -7.3059 | -1.6617 | -1.7624 | -0.004578 | -121.0464 | -0.045776 | -0.11444 | 0.07782 | 120.7214 | -0.018311 | -0.24262 | -0.004578 | 0.1236 | 119.1422 | 119.0414 | 120.7855 | 120.6894 | 0.07782 | 120.7993 | 113.4979 | -0.24262 | 120.6894 | 0.07782 | 113.4979 | 120.7855 | 120.7993 | -120.8496 | -121.0464
1252.2656 | 121.1014 | -120.8405 | 0.009155 | 0.15831 | 0.010641 | 0.0059921 | 0.035427 | -0.012751 | -0.0097583 | 0.014484 | -0.29755 | -0.22888 | -0.3479 | 0.032043 | 0.082397 | 0.073242 | -0.31586 | -0.13733 | -0.045776 | -0.37079 | 120.4926 | -0.23804 | 120.5429 | 120.8725 | 0.073242 | 120.4697 | -0.054931 | 0.050354 | 120.5246 | 120.7031 | 120.9229 | 120.6116 | 120.5429 | 120.7947 | 120.9137 | 120.4697 | 120.6116 | 120.5429 | 120.9137 | 120.9229 | 120.7947 | -0.35706 | -0.37994
1257.8594 | 121.1243 | -120.9045 | 0.022888 | -0.12398 | 0.011495 | 0.0030013 | 0.034786 | -0.015101 | -0.0084765 | 0.014911 | 0.10529 | 0.068665 | 0.11444 | -0.054932 | 0.022888 | 0.21515 | 0.20142 | 0.11444 | -0.022888 | -0.027466 | 121.019 | 0.045777 | 121.0098 | 120.8496 | 0 | 120.8771 | -0.045776 | -0.009155 | 121.106 | 121.019 | 120.9274 | 120.9732 | 121.0098 | 120.8817 | 121.1197 | 120.8771 | 120.9732 | 121.0098 | 121.1197 | 120.9274 | 120.8817 | 0.091553 | -0.050354
1259.6406 | 121.1334 | -120.9229 | 0.054932 | -0.23079 | 0.009786 | 0.0021469 | 0.037563 | -0.01446 | -0.010399 | 0.015765 | 0.15106 | 0.054932 | 0.16022 | -0.022888 | 0.041199 | 0.22888 | 0.18768 | 0.17395 | -0.022888 | -0.004578 | 121.0831 | 0 | 121.0739 | 120.9 | -0.013733 | 120.9183 | -0.07782 | -0.009155 | 121.1105 | 121.0968 | 120.9641 | 120.9778 | 121.0739 | 120.9 | 121.1517 | 120.9183 | 120.9778 | 121.0739 | 121.1517 | 120.9641 | 120.9 | 0.10528 | -0.05951
1261.3438 | 121.1334 | -120.9366 | 0.027466 | -0.017166 | 0.0095724 | 0.0038559 | 0.041195 | -0.011469 | -0.010399 | 0.015552 | -0.13733 | -0.20599 | -0.16479 | -0.041199 | 0.009155 | 0.004578 | -0.14191 | -0.19226 | -0.022888 | -0.2243 | 120.7718 | -0.23346 | 120.7993 | 120.8954 | -0.018311 | 120.7123 | -0.050354 | 0.027466 | 120.7947 | 120.7443 | 120.9457 | 120.7306 | 120.7993 | 120.9137 | 120.9412 | 120.7123 | 120.7306 | 120.7993 | 120.9412 | 120.9457 | 120.9137 | -0.19226 | -0.25177
1263.0469 | 121.0922 | -120.9641 | 0.032043 | -0.062942 | 0.011922 | 0.0040695 | 0.041195 | -0.013819 | -0.0095447 | 0.014697 | -0.045776 | -0.15106 | -0.054932 | -0.004578 | 0.064087 | 0.11444 | -0.09613 | -0.064087 | -0.032043 | -0.16022 | 120.9091 | -0.18311 | 120.9183 | 120.9595 | 0.032044 | 120.8038 | -0.064086 | 0.009156 | 120.8679 | 120.9 | 121.0281 | 120.813 | 120.9183 | 120.932 | 121.0785 | 120.8038 | 120.813 | 120.9183 | 121.0785 | 121.0281 | 120.932 | -0.086975 | -0.19226
1264.7969 | 121.225 | -120.9412 | 0 | -0.055313 | 0.0091452 | 0.0051377 | 0.034145 | -0.015742 | -0.0082629 | 0.016406 | 0.1236 | 0.022888 | 0.082397 | 0.009155 | 0.11444 | 0.24261 | 0.036621 | 0.20142 | -0.036621 | 0 | 121.0236 | 0.022888 | 121.0648 | 120.9503 | 0.11444 | 120.9412 | -0.036621 | 0.041199 | 120.9778 | 121.1426 | 121.0556 | 120.9641 | 121.0648 | 120.9045 | 121.1838 | 120.9412 | 120.9641 | 121.0648 | 121.1838 | 121.0556 | 120.9045 | 0.082397 | 0
1266.5625 | 121.1838 | -120.9778 | 0.018311 | -0.20027 | 0.010641 | 0.0051377 | 0.039272 | -0.012965 | -0.010186 | 0.015765 | 0.091553 | 0 | 0.10071 | -0.059509 | 0.027466 | 0.20142 | 0.082397 | 0.21515 | -0.009155 | 0.009155 | 121.0785 | -0.018311 | 121.0693 | 120.9183 | 0.009155 | 120.9869 | -0.027466 | -0.009155 | 121.0602 | 121.1929 | 121.0052 | 120.9778 | 121.0693 | 120.9686 | 121.1792 | 120.9869 | 120.9778 | 121.0693 | 121.1792 | 121.0052 | 120.9686 | 0.082397 | -0.009156
1268.25 | 121.1609 | -121.0007 | 0.022888 | -0.16212 | 0.013204 | 0.0010787 | 0.040768 | -0.012965 | -0.0091173 | 0.015765 | 0.07782 | 0 | 0.064087 | -0.059509 | 0.027466 | 0.17853 | 0.045776 | 0.19226 | 0 | 0 | 121.0648 | -0.022888 | 121.0785 | 120.9412 | 0.004578 | 121.0007 | -0.022888 | 0.013733 | 121.0464 | 121.1929 | 121.0281 | 121.0007 | 121.0785 | 121.0007 | 121.1792 | 121.0007 | 121.0007 | 121.0785 | 121.1792 | 121.0281 | 121.0007 | 0.041199 | -0.022888
1270 | 121.1975 | -121.0327 | 0.027466 | 0.03624 | 0.013204 | 0.0059921 | 0.041836 | -0.011469 | -0.0082629 | 0.015552 | -0.11902 | -0.20599 | -0.13275 | -0.036621 | 0.027466 | -0.018311 | -0.13733 | -0.16479 | -0.027466 | -0.19226 | 120.9 | -0.23346 | 120.9137 | 120.9961 | 0 | 120.8405 | -0.054932 | 0.013732 | 120.8954 | 120.8679 | 121.0602 | 120.8267 | 120.9137 | 121.0052 | 121.0144 | 120.8405 | 120.8267 | 120.9137 | 121.0144 | 121.0602 | 121.0052 | -0.16022 | -0.21973
1271.75 | 121.1838 | -121.0419 | 0.045776 | -0.11635 | 0.010427 | 0.0053513 | 0.040981 | -0.011042 | -0.0091173 | 0.017902 | 0.045776 | -0.073242 | 0.054932 | -0.018311 | 0.064087 | 0.17395 | -0.018311 | 0.12817 | -0.004578 | -0.050354 | 121.0968 | -0.11902 | 121.0876 | 121.0236 | 0.018311 | 120.9915 | -0.050354 | -0.009156 | 121.0236 | 121.17 | 121.106 | 120.9686 | 121.0876 | 121.0373 | 121.2158 | 120.9915 | 120.9686 | 121.0876 | 121.2158 | 121.106 | 121.0373 | 0.009156 | -0.09613
1273.4375 | 121.2158 | -121.0419 | 0.018311 | -0.14687 | 0.011922 | 0.0042831 | 0.039059 | -0.011469 | -0.0093311 | 0.015979 | 0.059509 | -0.013733 | 0.059509 | -0.054932 | 0.022888 | 0.16937 | 0.11902 | 0.032043 | -0.013733 | 0 | 121.1014 | -0.032044 | 121.1014 | 120.9869 | 0.004577 | 121.0419 | -0.032044 | 0 | 121.1609 | 121.0739 | 121.0648 | 121.0281 | 121.1014 | 121.0281 | 121.2112 | 121.0419 | 121.0281 | 121.1014 | 121.2112 | 121.0648 | 121.0281 | 0.041198 | -0.018311
1275.1094 | 121.257 | -121.0648 | 0.041199 | -0.12398 | 0.012563 | 0.0017197 | 0.032009 | -0.013392 | -0.0063403 | 0.014484 | 0.19684 | 0 | 0.11902 | 0.050354 | 0.13733 | 0.27466 | 0.013733 | 0.25177 | -0.027466 | 0.022888 | 121.1838 | -0.041199 | 121.2616 | 121.1151 | 0.09613 | 121.0876 | -0.068665 | 0.077819 | 121.0785 | 121.3165 | 121.2021 | 121.0648 | 121.2616 | 121.0373 | 121.3394 | 121.0876 | 121.0648 | 121.2616 | 121.3394 | 121.2021 | 121.0373 | 0.07782 | -0.018311
1276.7969 | 121.225 | -121.0876 | 0.027466 | -0.1545 | 0.0099996 | 0.0049241 | 0.036709 | -0.012751 | -0.0089037 | 0.017474 | 0.19684 | 0.004578 | 0.1831 | 0.032043 | 0.11444 | 0.31128 | 0.073242 | 0.23804 | -0.054932 | 0.064087 | 121.2708 | -0.022888 | 121.2845 | 121.1197 | 0.086975 | 121.1517 | -0.082398 | 0.013733 | 121.1609 | 121.3257 | 121.2021 | 121.0922 | 121.2845 | 121.0327 | 121.3989 | 121.1517 | 121.0922 | 121.2845 | 121.3989 | 121.2021 | 121.0327 | 0.15564 | 0.036621
1278.4844 | 121.3257 | -121.0327 | 0.022888 | 0.12779 | 0.012563 | 0.0032151 | 0.039913 | -0.01446 | -0.0078357 | 0.017047 | -0.041199 | -0.19684 | -0.091553 | 0.032043 | 0.10071 | 0.045776 | -0.26093 | -0.022888 | -0.050354 | -0.1831 | 120.9412 | -0.21973 | 120.9915 | 121.0648 | 0.07782 | 120.8496 | -0.073242 | 0.050354 | 120.7718 | 121.0098 | 121.1334 | 120.8359 | 120.9915 | 120.9824 | 121.0785 | 120.8496 | 120.8359 | 120.9915 | 121.0785 | 121.1334 | 120.9824 | -0.11444 | -0.20599
1280.1875 | 121.4081 | -121.0693 | 0.004578 | 0.03624 | 0.010641 | 0.00065151 | 0.036282 | -0.01446 | -0.0052721 | 0.015552 | 0 | -0.07782 | 0.013733 | -0.022888 | 0.064087 | 0.086975 | -0.059509 | 0.07782 | -0.054932 | -0.064087 | 121.0831 | -0.082398 | 121.0693 | 121.0464 | 0.059509 | 121.0052 | -0.05951 | -0.013733 | 121.0098 | 121.1472 | 121.1334 | 120.9915 | 121.0693 | 121.0144 | 121.1563 | 121.0052 | 120.9915 | 121.0693 | 121.1563 | 121.1334 | 121.0144 | 0.009155 | -0.068665
1281.8906 | 121.376 | -121.0693 | 0.009155 | 0.02861 | 0.011068 | 0.0057785 | 0.03735 | -0.012965 | -0.0059131 | 0.015552 | 0.041199 | -0.050354 | 0.032043 | -0.018311 | 0.068665 | 0.12817 | -0.050354 | 0.12817 | -0.041199 | -0.059509 | 121.1014 | -0.059509 | 121.1105 | 121.051 | 0.05951 | 121.0098 | -0.050354 | 0.009156 | 121.019 | 121.1975 | 121.138 | 121.019 | 121.1105 | 121.0281 | 121.1975 | 121.0098 | 121.019 | 121.1105 | 121.1975 | 121.138 | 121.0281 | 0.022888 | -0.068664
1283.5781 | 121.4218 | -121.0739 | 0.013733 | 0.020981 | 0.0074362 | -0.0016983 | 0.035854 | -0.012965 | -0.010826 | 0.014911 | 0.009155 | -0.086975 | -0.004578 | -0.022888 | 0.059509 | 0.068665 | -0.068665 | 0.073242 | -0.036621 | -0.054932 | 121.0693 | -0.10071 | 121.0831 | 121.051 | 0.045776 | 121.019 | -0.050354 | 0.013733 | 121.0052 | 121.1472 | 121.1334 | 120.9869 | 121.0831 | 121.0373 | 121.1426 | 121.019 | 120.9869 | 121.0831 | 121.1426 | 121.1334 | 121.0373 | -0.018311 | -0.068665
1285.3125 | 121.3257 | -121.1105 | 0.027466 | -0.16975 | 0.010213 | 0.0017197 | 0.041836 | -0.015528 | -0.0091173 | 0.015125 | 0.12817 | 0.013733 | 0.15106 | -0.045776 | 0.004578 | 0.18768 | 0.1236 | 0.27466 | -0.009155 | 0.027466 | 121.2616 | -0.013733 | 121.2387 | 121.0648 | -0.022888 | 121.138 | -0.036621 | -0.022888 | 121.2341 | 121.3852 | 121.1151 | 121.1243 | 121.2387 | 121.1014 | 121.2982 | 121.138 | 121.1243 | 121.2387 | 121.2982 | 121.1151 | 121.1014 | 0.1236 | 0
1287.0156 | 121.4035 | -121.106 | 0.009155 | 0.059128 | 0.012777 | 0.0077011 | 0.044613 | -0.013392 | -0.0089037 | 0.015765 | -0.16479 | -0.21515 | -0.13733 | -0.09613 | -0.022888 | -0.07782 | -0.1236 | -0.25177 | -0.018311 | -0.21973 | 120.9686 | -0.2243 | 120.9412 | 121.0098 | -0.032043 | 120.8862 | -0.027466 | -0.027466 | 120.9824 | 120.8542 | 121.0831 | 120.8908 | 120.9412 | 121.0876 | 121.0281 | 120.8862 | 120.8908 | 120.9412 | 121.0281 | 121.0831 | 121.0876 | -0.14648 | -0.22888
1288.7656 | 121.344 | -121.1563 | 0.032043 | -0.2079 | 0.010854 | -0.0016983 | 0.039486 | -0.012965 | -0.0089037 | 0.015979 | 0.09613 | 0.032043 | 0.12817 | -0.064087 | 0.018311 | 0.16937 | 0.15564 | 0.23346 | 0 | 0.032043 | 121.2845 | 0 | 121.2524 | 121.0922 | -0.013732 | 121.1884 | -0.032043 | -0.032044 | 121.312 | 121.3898 | 121.1746 | 121.1884 | 121.2524 | 121.1563 | 121.3257 | 121.1884 | 121.1884 | 121.2524 | 121.3257 | 121.1746 | 121.1563 | 0.096131 | 0
1290.5156 | 121.3165 | -121.1792 | 0.041199 | -0.16212 | 0.01299 | 0.0010787 | 0.036923 | -0.013819 | -0.0084765 | 0.016193 | 0.20599 | 0.004578 | 0.17853 | 0.022888 | 0.11902 | 0.27466 | 0.064087 | 0.37537 | -0.032043 | 0.064087 | 121.3577 | -0.036621 | 121.3852 | 121.2021 | 0.07782 | 121.2433 | -0.073242 | 0.027466 | 121.2433 | 121.5546 | 121.2982 | 121.1838 | 121.3852 | 121.1472 | 121.4539 | 121.2433 | 121.1838 | 121.3852 | 121.4539 | 121.2982 | 121.1472 | 0.13733 | 0.022888
1292.2188 | 121.4172 | -121.1517 | -0.004578 | 0.15068 | 0.011709 | 0.0047103 | 0.040768 | -0.012538 | -0.0095447 | 0.015338 | -0.15564 | -0.19684 | -0.14648 | -0.036621 | 0.027466 | -0.073242 | -0.2243 | -0.23804 | -0.018311 | -0.19684 | 121.0052 | -0.19226 | 120.9961 | 121.1151 | 0.032044 | 120.9549 | -0.013733 | -0.009156 | 120.9274 | 120.9137 | 121.1792 | 120.9549 | 120.9961 | 121.1334 | 121.0785 | 120.9549 | 120.9549 | 120.9961 | 121.0785 | 121.1792 | 121.1334 | -0.14191 | -0.19226
1293.9688 | 121.3577 | -121.17 | 0.041199 | -0.055313 | 0.012777 | 0.0023605 | 0.041195 | -0.012965 | -0.0093311 | 0.016193 | -0.027466 | -0.1831 | -0.036621 | -0.009155 | 0.041199 | 0.059509 | -0.10529 | -0.032043 | -0.018311 | -0.11902 | 121.1334 | -0.2243 | 121.1426 | 121.1609 | 0 | 121.051 | -0.05951 | 0.009155 | 121.0648 | 121.138 | 121.2112 | 120.9869 | 121.1426 | 121.1517 | 121.2296 | 121.051 | 120.9869 | 121.1426 | 121.2296 | 121.2112 | 121.1517 | -0.07782 | -0.16022
1295.6562 | 121.3623 | -121.2067 | 0.036621 | -0.055313 | 0.01235 | 0.0068467 | 0.042049 | -0.012538 | -0.0086901 | 0.015338 | -0.018311 | -0.16937 | -0.036621 | -0.013733 | 0.041199 | 0.050354 | -0.10071 | -0.045776 | -0.018311 | -0.11902 | 121.17 | -0.20599 | 121.1884 | 121.1929 | 0.004578 | 121.0876 | -0.054932 | 0.01831 | 121.106 | 121.1609 | 121.2479 | 121.0373 | 121.1884 | 121.1884 | 121.257 | 121.0876 | 121.0373 | 121.1884 | 121.257 | 121.2479 | 121.1884 | -0.073242 | -0.15564
1297.4062 | 121.3623 | -121.1975 | 0.054932 | -0.12398 | 0.011281 | 0.00043791 | 0.032436 | -0.014033 | -0.0054859 | 0.016406 | 0.19684 | 0.004578 | 0.16937 | 0.045776 | 0.14191 | 0.28381 | 0.013733 | 0.37994 | -0.036621 | 0.054932 | 121.3669 | -0.050354 | 121.3943 | 121.2433 | 0.086975 | 121.2524 | -0.091553 | 0.027465 | 121.2112 | 121.5775 | 121.3394 | 121.2021 | 121.3943 | 121.1609 | 121.4813 | 121.2524 | 121.2021 | 121.3943 | 121.4813 | 121.3394 | 121.1609 | 0.11444 | 0
1299.1719 | 121.4996 | -121.1655 | 0.009155 | 0.020981 | 0.013204 | 0.0036423 | 0.036923 | -0.014033 | -0.0078357 | 0.017261 | 0.032043 | -0.07782 | 0.064087 | -0.027466 | 0.073242 | 0.10071 | -0.036621 | 0.091553 | -0.032043 | -0.054932 | 121.2296 | -0.086975 | 121.1975 | 121.138 | 0.064087 | 121.1105 | -0.041198 | -0.032044 | 121.1288 | 121.257 | 121.2387 | 121.0876 | 121.1975 | 121.1334 | 121.2662 | 121.1105 | 121.0876 | 121.1975 | 121.2662 | 121.2387 | 121.1334 | 0.054932 | -0.064087
1300.9219 | 121.5088 | -121.1975 | 0 | 0.097275 | 0.012136 | 0.0047103 | 0.039272 | -0.011683 | -0.0086901 | 0.015979 | -0.17395 | -0.22888 | -0.14648 | -0.064087 | -0.013733 | -0.10986 | -0.17395 | -0.27008 | -0.004578 | -0.21515 | 121.051 | -0.22888 | 121.0236 | 121.1334 | -0.013733 | 120.9824 | -0.004578 | -0.027466 | 121.0236 | 120.9274 | 121.1838 | 120.9686 | 121.0236 | 121.1929 | 121.0876 | 120.9824 | 120.9686 | 121.0236 | 121.0876 | 121.1838 | 121.1929 | -0.14648 | -0.21515
1302.625 | 121.4722 | -121.2021 | 0.013733 | 0.18883 | 0.010854 | 0.0030013 | 0.040341 | -0.0093331 | -0.0089037 | 0.017261 | -0.1236 | -0.21515 | -0.11902 | 0.009155 | 0.07782 | -0.018311 | -0.27466 | -0.16479 | -0.064087 | -0.1831 | 121.0831 | -0.22888 | 121.0785 | 121.2112 | 0.064087 | 121.019 | -0.07782 | -0.004577 | 120.9274 | 121.0373 | 121.2799 | 120.9869 | 121.0785 | 121.138 | 121.1838 | 121.019 | 120.9869 | 121.0785 | 121.1838 | 121.2799 | 121.138 | -0.13275 | -0.19684
1304.375 | 121.5271 | -121.2158 | 0.004578 | 0.020981 | 0.009786 | 0.0021469 | 0.034359 | -0.014033 | -0.0069811 | 0.015979 | 0.054932 | -0.054932 | 0.068665 | -0.022888 | 0.068665 | 0.11444 | -0.004578 | 0.13733 | -0.036621 | -0.018311 | 121.2845 | -0.05951 | 121.2708 | 121.1929 | 0.064087 | 121.1975 | -0.041199 | -0.013733 | 121.2112 | 121.3531 | 121.2845 | 121.1609 | 121.2708 | 121.1792 | 121.3303 | 121.1975 | 121.1609 | 121.2708 | 121.3303 | 121.2845 | 121.1792 | 0.064087 | -0.022889
1306.1406 | 121.5454 | -121.2158 | 0.018311 | 0.1049 | 0.010427 | 0.0012925 | 0.037136 | -0.013392 | -0.0093311 | 0.016834 | -0.009155 | -0.16937 | -0.022888 | -0.004578 | 0.086975 | 0.041199 | -0.12817 | 0 | -0.032043 | -0.11902 | 121.1929 | -0.18768 | 121.2067 | 121.2112 | 0.068664 | 121.0968 | -0.050354 | 0.013733 | 121.0876 | 121.2158 | 121.3028 | 121.0464 | 121.2067 | 121.1838 | 121.257 | 121.0968 | 121.0464 | 121.2067 | 121.257 | 121.3028 | 121.1838 | -0.041199 | -0.13733
1307.8281 | 121.5134 | -121.2204 | 0.018311 | 0.074387 | 0.010427 | 0.0040695 | 0.043758 | -0.012751 | -0.0093311 | 0.015125 | -0.14191 | -0.21515 | -0.091553 | -0.082397 | -0.022888 | -0.073242 | -0.10529 | -0.23346 | -0.009155 | -0.20142 | 121.1288 | -0.23346 | 121.0785 | 121.138 | -0.041199 | 121.019 | -0.027466 | -0.050354 | 121.1151 | 120.9869 | 121.1975 | 121.0052 | 121.0785 | 121.2112 | 121.1472 | 121.019 | 121.0052 | 121.0785 | 121.1472 | 121.1975 | 121.2112 | -0.10986 | -0.21973
1309.5625 | 121.5225 | -121.257 | 0.018311 | 0.11253 | 0.010854 | 0.0032151 | 0.036282 | -0.012324 | -0.0086901 | 0.015552 | -0.022888 | -0.17853 | -0.054932 | 0.013733 | 0.11444 | 0.032043 | -0.19226 | -0.009155 | -0.050354 | -0.13275 | 121.2021 | -0.19684 | 121.2341 | 121.2708 | 0.09613 | 121.1243 | -0.068665 | 0.032044 | 121.0648 | 121.2479 | 121.3715 | 121.0785 | 121.2341 | 121.2067 | 121.2891 | 121.1243 | 121.0785 | 121.2341 | 121.2891 | 121.3715 | 121.2067 | -0.073243 | -0.15106
1311.3281 | 121.5637 | -121.2479 | 0.004578 | 0.082016 | 0.014058 | 0.0053513 | 0.03735 | -0.014033 | -0.0071947 | 0.015765 | -0.022888 | -0.14648 | -0.027466 | -0.004578 | 0.064087 | 0.045776 | -0.11902 | 0.027466 | -0.050354 | -0.10986 | 121.2204 | -0.15106 | 121.225 | 121.2433 | 0.059509 | 121.138 | -0.054932 | 0.004578 | 121.1288 | 121.2753 | 121.312 | 121.1014 | 121.225 | 121.1975 | 121.2936 | 121.138 | 121.1014 | 121.225 | 121.2936 | 121.312 | 121.1975 | -0.032044 | -0.11444
1313.0781 | 121.5683 | -121.2387 | -0.004578 | 0.097275 | 0.0091452 | 0.0051377 | 0.043331 | -0.013178 | -0.0082629 | 0.015552 | -0.17853 | -0.21973 | -0.1236 | -0.086975 | -0.018311 | -0.086975 | -0.15106 | -0.24261 | -0.018311 | -0.17853 | 121.1151 | -0.21515 | 121.0602 | 121.1517 | -0.013733 | 121.0602 | -0.013733 | -0.054932 | 121.0876 | 120.9961 | 121.2204 | 121.019 | 121.0602 | 121.2204 | 121.1517 | 121.0602 | 121.019 | 121.0602 | 121.1517 | 121.2204 | 121.2204 | -0.11902 | -0.17395
1314.7656 | 121.5637 | -121.2891 | -0.009155 | 0.097275 | 0.012136 | 0.0042831 | 0.041409 | -0.012965 | -0.011681 | 0.014056 | -0.16479 | -0.21057 | -0.13733 | -0.082397 | -0.009155 | -0.091553 | -0.15564 | -0.24261 | -0.009155 | -0.18768 | 121.1517 | -0.20142 | 121.1243 | 121.2067 | 0 | 121.1014 | 0 | -0.027466 | 121.1334 | 121.0464 | 121.2799 | 121.0785 | 121.1243 | 121.2799 | 121.1975 | 121.1014 | 121.0785 | 121.1243 | 121.1975 | 121.2799 | 121.2799 | -0.12817 | -0.17853
1316.5156 | 121.5591 | -121.2845 | 0.018311 | 0.17357 | 0.010427 | 0.0025741 | 0.038845 | -0.011256 | -0.0080493 | 0.018329 | -0.10071 | -0.24261 | -0.10529 | 0.009155 | 0.091553 | 0.16022 | -0.27466 | -0.091553 | -0.054932 | -0.16022 | 121.1792 | -0.26093 | 121.1838 | 121.2936 | 0.073242 | 121.1243 | -0.073243 | 0.004578 | 121.0098 | 121.1929 | 121.376 | 121.0419 | 121.1838 | 121.2296 | 121.4447 | 121.1243 | 121.0419 | 121.1838 | 121.4447 | 121.376 | 121.2296 | -0.1236 | -0.17853
1318.2656 | 121.5408 | -121.3257 | 0.018311 | -0.13161 | 0.0099996 | 0.0027877 | 0.035214 | -0.012751 | -0.010186 | 0.015552 | 0.17853 | -0.018311 | 0.15564 | 0.032043 | 0.14191 | 0.18768 | -0.013733 | 0.3067 | -0.036621 | 0.054932 | 121.4813 | -0.036622 | 121.5042 | 121.3577 | 0.1236 | 121.3806 | -0.054932 | 0.022888 | 121.312 | 121.6324 | 121.4676 | 121.3074 | 121.5042 | 121.2891 | 121.5134 | 121.3806 | 121.3074 | 121.5042 | 121.5134 | 121.4676 | 121.2891 | 0.13733 | 0.036621
1320.0156 | 121.4767 | -121.3577 | 0.045776 | -0.16212 | 0.008718 | 0.0032151 | 0.036068 | -0.014674 | -0.0065539 | 0.013843 | 0.22888 | 0.004578 | 0.1831 | 0.041199 | 0.13733 | 0.16022 | 0.036621 | 0.37079 | -0.054932 | 0.086975 | 121.5408 | -0.041198 | 121.5866 | 121.3989 | 0.091553 | 121.4447 | -0.10071 | 0.045777 | 121.3943 | 121.7285 | 121.4951 | 121.3623 | 121.5866 | 121.3028 | 121.5179 | 121.4447 | 121.3623 | 121.5866 | 121.5179 | 121.4951 | 121.3028 | 0.13733 | 0.041199
1321.7188 | 121.5225 | -121.3257 | 0.009155 | -0.16212 | 0.0099996 | 0.0025741 | 0.040554 | -0.011469 | -0.0084765 | 0.014056 | 0.10529 | -0.009155 | 0.10986 | -0.054932 | 0.018311 | 0.041199 | 0.091553 | 0.13733 | -0.004578 | 0.022888 | 121.4355 | -0.01831 | 121.431 | 121.2708 | 0.009156 | 121.3486 | -0.013733 | -0.004577 | 121.4172 | 121.463 | 121.344 | 121.3165 | 121.431 | 121.3211 | 121.3669 | 121.3486 | 121.3165 | 121.431 | 121.3669 | 121.344 | 121.3211 | 0.10071 | 0.013733
1323.4844 | 121.6049 | -121.344 | 0.018311 | -0.062942 | 0.010213 | 1.071e-05 | 0.034573 | -0.013392 | -0.0065539 | 0.01662 | 0.14191 | -0.032043 | 0.10986 | 0.018311 | 0.11444 | 0.16937 | -0.004578 | 0.27466 | -0.036621 | 0.013733 | 121.4539 | -0.050354 | 121.4859 | 121.3623 | 0.09613 | 121.3577 | -0.054932 | 0.032044 | 121.3394 | 121.6187 | 121.4584 | 121.312 | 121.4859 | 121.3074 | 121.5134 | 121.3577 | 121.312 | 121.4859 | 121.5134 | 121.4584 | 121.3074 | 0.091552 | -0.004578
1325.1719 | 121.6232 | -121.344 | 0 | 0.082016 | 0.011709 | 0.0036423 | 0.043972 | -0.013819 | -0.010399 | 0.014484 | -0.13275 | -0.1831 | -0.10529 | -0.07782 | -0.022888 | 0.004578 | -0.091553 | -0.25635 | -0.009155 | -0.18768 | 121.2387 | -0.1831 | 121.2112 | 121.2662 | -0.022888 | 121.1563 | -0.009155 | -0.027465 | 121.2524 | 121.0876 | 121.3211 | 121.1609 | 121.2112 | 121.3348 | 121.3486 | 121.1563 | 121.1609 | 121.2112 | 121.3486 | 121.3211 | 121.3348 | -0.10529 | -0.18768
1326.9375 | 121.5958 | -121.3531 | 0.009155 | 0.16594 | 0.010427 | 0.0049241 | 0.039913 | -0.014033 | -0.0080493 | 0.017474 | -0.036621 | -0.21973 | -0.07782 | 0.036621 | 0.11444 | 0.17853 | -0.27466 | -0.073242 | -0.041199 | -0.16937 | 121.2753 | -0.22888 | 121.3165 | 121.3898 | 0.10529 | 121.1838 | -0.050354 | 0.041199 | 121.0785 | 121.2799 | 121.4676 | 121.1334 | 121.3165 | 121.3119 | 121.5317 | 121.1838 | 121.1334 | 121.3165 | 121.5317 | 121.4676 | 121.3119 | -0.086975 | -0.17853
1328.6875 | 121.5363 | -121.3989 | 0.045776 | -0.18501 | 0.009786 | 0.0015061 | 0.038845 | -0.015956 | -0.0069811 | 0.014911 | 0.19684 | -0.009155 | 0.16937 | 0.032043 | 0.10071 | 0.14191 | 0.086975 | 0.32501 | -0.027466 | 0.059509 | 121.5683 | -0.054931 | 121.5958 | 121.431 | 0.054932 | 121.4584 | -0.073242 | 0.027465 | 121.4859 | 121.7239 | 121.4996 | 121.3898 | 121.5958 | 121.3715 | 121.5408 | 121.4584 | 121.3898 | 121.5958 | 121.5408 | 121.4996 | 121.3715 | 0.1236 | 0.013733
1330.375 | 121.6507 | -121.3623 | 0.018311 | -0.032425 | 0.0089316 | 0.0030013 | 0.033932 | -0.015528 | -0.0054859 | 0.018115 | 0.10986 | -0.041199 | 0.11444 | 0.018311 | 0.10529 | 0.14648 | -0.004578 | 0.23346 | -0.054932 | 0.004578 | 121.4767 | -0.05951 | 121.4722 | 121.3806 | 0.086975 | 121.3669 | -0.073243 | -0.004578 | 121.3577 | 121.5958 | 121.4676 | 121.3211 | 121.4722 | 121.3074 | 121.5088 | 121.3669 | 121.3211 | 121.4722 | 121.5088 | 121.4676 | 121.3074 | 0.09613 | -0.013733
1332.125 | 121.5454 | -121.4172 | 0.041199 | -0.16212 | 0.011281 | 0.0023605 | 0.039272 | -0.014674 | -0.0059131 | 0.015338 | 0.2243 | -0.009155 | 0.21057 | 0.068665 | 0.13275 | 0.17853 | 0.013733 | 0.37537 | -0.054932 | 0.07782 | 121.6278 | -0.050354 | 121.6415 | 121.4859 | 0.091552 | 121.4951 | -0.096131 | 0.013733 | 121.431 | 121.7926 | 121.55 | 121.4081 | 121.6415 | 121.3623 | 121.5958 | 121.4951 | 121.4081 | 121.6415 | 121.5958 | 121.55 | 121.3623 | 0.16937 | 0.036621
1333.875 | 121.6599 | -121.376 | 0.004578 | 0.082016 | 0.013845 | 0.0064193 | 0.044186 | -0.010615 | -0.010613 | 0.01662 | -0.13733 | -0.19226 | -0.10529 | -0.091553 | -0.027466 | 0.022888 | -0.09613 | -0.24719 | -0.013733 | -0.1831 | 121.2708 | -0.19684 | 121.2387 | 121.2845 | -0.032044 | 121.1929 | -0.018311 | -0.032043 | 121.2799 | 121.1288 | 121.3486 | 121.1838 | 121.2387 | 121.3623 | 121.3989 | 121.1929 | 121.1838 | 121.2387 | 121.3989 | 121.3486 | 121.3623 | -0.10986 | -0.18768
1335.5625 | 121.5729 | -121.4264 | 0.036621 | -0.032425 | 0.012563 | 0.00065151 | 0.039486 | -0.012751 | -0.0097583 | 0.017688 | -0.004578 | -0.14648 | -0.013733 | -0.018311 | 0.045776 | 0.068665 | -0.10071 | -0.073242 | -0.022888 | -0.12817 | 121.4127 | -0.18311 | 121.4218 | 121.4081 | 0.009155 | 121.2982 | -0.059509 | 0.009155 | 121.3257 | 121.3532 | 121.4722 | 121.2799 | 121.4218 | 121.4035 | 121.4951 | 121.2982 | 121.2799 | 121.4218 | 121.4951 | 121.4722 | 121.4035 | -0.050354 | -0.1648
1337.3125 | 121.6141 | -121.4172 | 0.036621 | -0.20027 | 0.010854 | 0.0034287 | 0.038418 | -0.014674 | -0.0069811 | 0.01897 | 0.086975 | 0.009155 | 0.14648 | -0.064087 | 0.022888 | 0.050354 | 0.20599 | 0.073242 | 0.009155 | 0.027466 | 121.5637 | -0.027466 | 121.5042 | 121.3531 | -0.013733 | 121.4447 | -0.027466 | -0.059509 | 121.6232 | 121.4905 | 121.4401 | 121.4264 | 121.5042 | 121.4264 | 121.4676 | 121.4447 | 121.4264 | 121.5042 | 121.4676 | 121.4401 | 121.4264 | 0.10986 | -0.009155
1339.0625 | 121.6599 | -121.4172 | 0.013733 | 0.12016 | 0.011922 | 0.0042831 | 0.036709 | -0.013819 | -0.0080493 | 0.018115 | -0.036621 | -0.21515 | -0.036621 | 0.027466 | 0.12817 | 0.17853 | -0.22888 | -0.009155 | -0.073242 | -0.16022 | 121.3806 | -0.22888 | 121.3806 | 121.4447 | 0.11444 | 121.257 | -0.086975 | 0 | 121.1884 | 121.4081 | 121.5454 | 121.2021 | 121.3806 | 121.344 | 121.5958 | 121.257 | 121.2021 | 121.3806 | 121.5958 | 121.5454 | 121.344 | -0.050354 | -0.17395
1340.8125 | 121.6187 | -121.431 | 0.032043 | -0.19264 | 0.014058 | -0.00020289 | 0.03735 | -0.015742 | -0.0048449 | 0.015552 | 0.10986 | 0.022888 | 0.15106 | -0.064087 | 0.009155 | 0.032043 | 0.19226 | 0.10529 | 0.004578 | 0.022888 | 121.582 | -0.009155 | 121.5408 | 121.3669 | -0.022888 | 121.4539 | -0.027465 | -0.041199 | 121.6232 | 121.5363 | 121.4401 | 121.4539 | 121.5408 | 121.4355 | 121.463 | 121.4539 | 121.4539 | 121.5408 | 121.463 | 121.4401 | 121.4355 | 0.11902 | -0.009155
1342.5625 | 121.637 | -121.4355 | 0.022888 | -0.19264 | 0.01235 | 0.0034287 | 0.040127 | -0.013178 | -0.0078357 | 0.015979 | 0.082397 | -0.009155 | 0.15564 | -0.07782 | 0.009155 | 0.045776 | 0.13275 | 0.13275 | -0.004578 | 0.018311 | 121.5912 | -0.032043 | 121.5179 | 121.3577 | -0.013733 | 121.4539 | -0.027466 | -0.073243 | 121.5683 | 121.5683 | 121.4447 | 121.4264 | 121.5179 | 121.431 | 121.4813 | 121.4539 | 121.4264 | 121.5179 | 121.4813 | 121.4447 | 121.431 | 0.13275 | -0.004577
1344.3125 | 121.6415 | -121.4493 | 0.022888 | -0.22316 | 0.011281 | 0.0032151 | 0.039059 | -0.013606 | -0.0097583 | 0.015979 | 0.10071 | -0.009155 | 0.14648 | -0.068665 | 0.009155 | 0.041199 | 0.16022 | 0.14648 | -0.004578 | 0.036621 | 121.5958 | -0.032043 | 121.55 | 121.3806 | -0.013733 | 121.4859 | -0.027466 | -0.045776 | 121.6095 | 121.5958 | 121.4584 | 121.4401 | 121.55 | 121.4447 | 121.4905 | 121.4859 | 121.4401 | 121.55 | 121.4905 | 121.4584 | 121.4447 | 0.1236 | 0.013733
1346 | 121.7285 | -121.4355 | 0.022888 | 0.0057222 | 0.011495 | 0.00065151 | 0.035427 | -0.01211 | -0.0065539 | 0.015125 | 0.073242 | -0.054932 | 0.091553 | -0.018311 | 0.082397 | 0.1236 | -0.018311 | 0.15106 | -0.036621 | -0.018311 | 121.5271 | -0.07782 | 121.5088 | 121.4172 | 0.059509 | 121.4172 | -0.059509 | -0.018311 | 121.4172 | 121.5866 | 121.5179 | 121.3806 | 121.5088 | 121.3989 | 121.5591 | 121.4172 | 121.3806 | 121.5088 | 121.5591 | 121.5179 | 121.3989 | 0.068665 | -0.041199
1347.75 | 121.701 | -121.463 | 0.013733 | 0.097275 | 0.011068 | 0.0030013 | 0.036923 | -0.013606 | -0.0086901 | 0.01427 | -0.027466 | -0.18768 | -0.045776 | 0.013733 | 0.091553 | 0.15564 | -0.19226 | -0.013733 | -0.036621 | -0.1236 | 121.4172 | -0.20142 | 121.4355 | 121.4767 | 0.07782 | 121.3394 | -0.050354 | 0.01831 | 121.2708 | 121.4493 | 121.5546 | 121.2753 | 121.4355 | 121.4264 | 121.6187 | 121.3394 | 121.2753 | 121.4355 | 121.6187 | 121.5546 | 121.4264 | -0.059509 | -0.13733
1349.4375 | 121.6232 | -121.4676 | 0.041199 | -0.055313 | 0.011495 | 0.0040695 | 0.042904 | -0.011042 | -0.0089037 | 0.014697 | 0.004578 | -0.14648 | -0.009155 | -0.018311 | 0.045776 | 0.091553 | -0.082397 | -0.027466 | -0.004578 | -0.091553 | 121.4584 | -0.18768 | 121.4722 | 121.4493 | 0.004577 | 121.376 | -0.045777 | 0.013733 | 121.3852 | 121.4401 | 121.5134 | 121.3211 | 121.4722 | 121.463 | 121.5591 | 121.376 | 121.3211 | 121.4722 | 121.5591 | 121.5134 | 121.463 | -0.050354 | -0.13275
1351.2031 | 121.6415 | -121.5042 | 0.045776 | -0.14687 | 0.011495 | 0.0032151 | 0.034786 | -0.012324 | -0.0061267 | 0.015552 | 0.21973 | -0.013733 | 0.17395 | 0.050354 | 0.14648 | 0.18768 | 0.018311 | 0.34332 | -0.045776 | 0.064087 | 121.6782 | -0.059509 | 121.7239 | 121.5546 | 0.10071 | 121.5683 | -0.091552 | 0.045777 | 121.5225 | 121.8475 | 121.6507 | 121.4905 | 121.7239 | 121.4584 | 121.6919 | 121.5683 | 121.4905 | 121.7239 | 121.6919 | 121.6507 | 121.4584 | 0.12817 | 0.018311
1352.9688 | 121.6965 | -121.4722 | 0.013733 | -0.0019073 | 0.013631 | 0.0057785 | 0.04269 | -0.012965 | -0.011895 | 0.016834 | -0.1236 | -0.19684 | -0.07782 | -0.073242 | -0.009155 | 0.036621 | -0.086975 | -0.20142 | -0.009155 | -0.16479 | 121.3943 | -0.21057 | 121.3486 | 121.3989 | -0.022888 | 121.3074 | -0.022888 | -0.045776 | 121.3852 | 121.2708 | 121.463 | 121.2753 | 121.3486 | 121.463 | 121.5088 | 121.3074 | 121.2753 | 121.3486 | 121.5088 | 121.463 | 121.463 | -0.091553 | -0.17853
1354.7188 | 121.6461 | -121.5134 | 0.032043 | -0.14687 | 0.010213 | 0.0012925 | 0.035214 | -0.015101 | -0.0071947 | 0.016193 | 0.21057 | 0.009155 | 0.19226 | 0.036621 | 0.11902 | 0.15106 | 0.10986 | 0.23804 | -0.036621 | 0.073242 | 121.7056 | -0.022888 | 121.7239 | 121.55 | 0.086976 | 121.5866 | -0.068664 | 0.01831 | 121.6232 | 121.7514 | 121.6324 | 121.5225 | 121.7239 | 121.4767 | 121.6644 | 121.5866 | 121.5225 | 121.7239 | 121.6644 | 121.6324 | 121.4767 | 0.16022 | 0.041199
1356.4062 | 121.6507 | -121.5454 | 0.022888 | -0.16975 | 0.010427 | 0.0027877 | 0.034573 | -0.015315 | -0.0086901 | 0.01662 | 0.22888 | -0.018311 | 0.17853 | 0.059509 | 0.13733 | 0.1831 | 0.059509 | 0.27466 | -0.045776 | 0.064087 | 121.7239 | -0.041199 | 121.7743 | 121.6049 | 0.11444 | 121.6095 | -0.068664 | 0.050354 | 121.6049 | 121.8201 | 121.6827 | 121.5271 | 121.7743 | 121.4996 | 121.7285 | 121.6095 | 121.5271 | 121.7743 | 121.7285 | 121.6827 | 121.4996 | 0.15564 | 0.041199
1358.1562 | 121.6599 | -121.5637 | 0.032043 | -0.17738 | 0.010641 | 0.0027877 | 0.037777 | -0.013606 | -0.0080493 | 0.014911 | 0.2243 | 0 | 0.20599 | 0.045776 | 0.12817 | 0.16937 | 0.064087 | 0.27008 | -0.041199 | 0.064087 | 121.7697 | -0.032043 | 121.788 | 121.6095 | 0.096131 | 121.6278 | -0.073242 | 0.01831 | 121.6278 | 121.8338 | 121.6919 | 121.5637 | 121.788 | 121.5225 | 121.7331 | 121.6278 | 121.5637 | 121.788 | 121.7331 | 121.6919 | 121.5225 | 0.17395 | 0.032044
1359.8438 | 121.7926 | -121.4951 | 0 | 0.12016 | 0.010641 | 0.0044967 | 0.0397 | -0.012538 | -0.0086901 | 0.018543 | -0.16022 | -0.21515 | -0.1236 | -0.082397 | -0.018311 | 0.032043 | -0.15106 | -0.2243 | -0.004578 | -0.19684 | 121.3715 | -0.21515 | 121.3348 | 121.4127 | -0.018311 | 121.2982 | -0.004578 | -0.036621 | 121.344 | 121.2708 | 121.4767 | 121.2799 | 121.3348 | 121.4905 | 121.5271 | 121.2982 | 121.2799 | 121.3348 | 121.5271 | 121.4767 | 121.4905 | -0.1236 | -0.19684
1361.5938 | 121.7194 | -121.55 | 0.032043 | -0.23079 | 0.010641 | 0.0032151 | 0.036709 | -0.012751 | -0.0089037 | 0.014056 | 0.091553 | -0.004578 | 0.14191 | -0.068665 | 0.022888 | 0.036621 | 0.20142 | 0.082397 | -0.009155 | 0.041199 | 121.6919 | -0.036621 | 121.6415 | 121.4813 | -0.009155 | 121.5912 | -0.041198 | -0.050354 | 121.7514 | 121.6324 | 121.5729 | 121.5454 | 121.6415 | 121.5408 | 121.5866 | 121.5912 | 121.5454 | 121.6415 | 121.5866 | 121.5729 | 121.5408 | 0.10986 | 0.009156
1363.3438 | 121.7377 | -121.5271 | 0.032043 | -0.22316 | 0.012136 | 0.0049241 | 0.037991 | -0.013392 | -0.0069811 | 0.015338 | 0.10986 | 0.013733 | 0.14191 | -0.064087 | 0.009155 | 0.036621 | 0.17853 | 0.064087 | 0.004578 | 0.004578 | 121.669 | -0.01831 | 121.637 | 121.463 | -0.022888 | 121.5317 | -0.027465 | -0.032044 | 121.7056 | 121.5912 | 121.5363 | 121.5408 | 121.637 | 121.5317 | 121.5637 | 121.5317 | 121.5408 | 121.637 | 121.5637 | 121.5363 | 121.5317 | 0.10986 | -0.027465
1365.0312 | 121.7422 | -121.5408 | 0.027466 | -0.16975 | 0.0091452 | -0.00063009 | 0.036923 | -0.013178 | -0.0091173 | 0.015765 | 0.11902 | 0.022888 | 0.16479 | -0.068665 | 0.045776 | 0.045776 | 0.1831 | 0.11902 | -0.018311 | 0.027466 | 121.7056 | -0.004578 | 121.6599 | 121.4722 | 0.01831 | 121.5683 | -0.045777 | -0.045776 | 121.7239 | 121.6599 | 121.5866 | 121.5637 | 121.6599 | 121.5225 | 121.5866 | 121.5683 | 121.5637 | 121.6599 | 121.5866 | 121.5866 | 121.5225 | 0.13733 | 0
1366.7812 | 121.7606 | -121.5225 | 0.004578 | 0.051498 | 0.011495 | -0.00020289 | 0.040127 | -0.013178 | -0.0097583 | 0.016406 | -0.1236 | -0.2243 | -0.086975 | -0.09613 | -0.018311 | 0.036621 | -0.09613 | -0.17853 | -0.018311 | -0.15564 | 121.4355 | -0.22888 | 121.3989 | 121.4264 | -0.022889 | 121.3669 | -0.022889 | -0.036621 | 121.4264 | 121.344 | 121.5042 | 121.2982 | 121.3989 | 121.5042 | 121.5591 | 121.3669 | 121.2982 | 121.3989 | 121.5591 | 121.5042 | 121.5042 | -0.091553 | -0.16022
1368.4688 | 121.7743 | -121.5454 | 0.013733 | 0.051498 | 0.01235 | 1.071e-05 | 0.039486 | -0.014247 | -0.0091173 | 0.01427 | -0.11902 | -0.17853 | -0.091553 | -0.091553 | 0 | 0.027466 | -0.086975 | -0.19226 | 0 | -0.18768 | 121.4539 | -0.19226 | 121.4264 | 121.4539 | -0.013733 | 121.3577 | -0.013733 | -0.027466 | 121.4584 | 121.3531 | 121.5454 | 121.3669 | 121.4264 | 121.5454 | 121.5729 | 121.3577 | 121.3669 | 121.4264 | 121.5729 | 121.5454 | 121.5454 | -0.10529 | -0.20142
1370.2188 | 121.7514 | -121.5454 | 0.036621 | -0.18501 | 0.012563 | -0.00041649 | 0.034786 | -0.014247 | -0.0076221 | 0.015979 | 0.10529 | 0.009155 | 0.16022 | -0.082397 | 0.022888 | 0.045776 | 0.20142 | 0.082397 | -0.004578 | 0.050354 | 121.7056 | -0.027466 | 121.6507 | 121.463 | -0.013733 | 121.5958 | -0.041199 | -0.054931 | 121.7468 | 121.6278 | 121.5683 | 121.5546 | 121.6507 | 121.5408 | 121.5912 | 121.5958 | 121.5546 | 121.6507 | 121.5912 | 121.5683 | 121.5408 | 0.1236 | 0.013733
1371.9688 | 121.8384 | -121.5546 | -0.009155 | 0.14305 | 0.011709 | 0.0027877 | 0.034786 | -0.013392 | -0.0078357 | 0.018115 | -0.013733 | -0.15564 | -0.027466 | -0.004578 | 0.07782 | 0.13733 | -0.13275 | 0.027466 | -0.041199 | -0.11902 | 121.5271 | -0.14649 | 121.5408 | 121.55 | 0.086975 | 121.4355 | -0.032044 | 0.013733 | 121.4218 | 121.582 | 121.6324 | 121.3989 | 121.5408 | 121.5134 | 121.6919 | 121.4355 | 121.3989 | 121.5408 | 121.6919 | 121.6324 | 121.5134 | -0.018311 | -0.10986
1373.7344 | 121.7972 | -121.5591 | 0.009155 | 0.15831 | 0.0095724 | 0.0030013 | 0.038845 | -0.011683 | -0.0084765 | 0.015338 | -0.036621 | -0.21057 | -0.059509 | 0.036621 | 0.11902 | 0.17853 | -0.2655 | -0.054932 | -0.036621 | -0.15106 | 121.4996 | -0.21973 | 121.5225 | 121.5958 | 0.10986 | 121.4081 | -0.045776 | 0.022888 | 121.2936 | 121.5042 | 121.6782 | 121.3486 | 121.5225 | 121.5225 | 121.7377 | 121.4081 | 121.3486 | 121.5225 | 121.7377 | 121.6782 | 121.5225 | -0.068664 | -0.16022
1375.4219 | 121.8658 | -121.5408 | 0 | 0.12016 | 0.011709 | 0.0047103 | 0.0397 | -0.011897 | -0.0097583 | 0.016406 | -0.16937 | -0.19684 | -0.11902 | -0.068665 | -0.013733 | 0.050354 | -0.11444 | -0.23346 | -0.009155 | -0.20142 | 121.4218 | -0.19684 | 121.3715 | 121.4722 | -0.013733 | 121.3394 | -0.009155 | -0.050354 | 121.4264 | 121.3074 | 121.5271 | 121.344 | 121.3715 | 121.5317 | 121.5912 | 121.3394 | 121.344 | 121.3715 | 121.5912 | 121.5271 | 121.5317 | -0.11902 | -0.20142
1377.1719 | 121.7148 | -121.582 | 0.045776 | -0.11635 | 0.01235 | 0.0021469 | 0.040768 | -0.011683 | -0.010186 | 0.01662 | 0.064087 | -0.086975 | 0.073242 | -0.022888 | 0.059509 | 0.07782 | -0.013733 | 0.045776 | 0 | -0.050354 | 121.6553 | -0.13275 | 121.6461 | 121.5591 | 0.013733 | 121.5317 | -0.045776 | -0.009155 | 121.5683 | 121.6278 | 121.6415 | 121.4951 | 121.6461 | 121.582 | 121.6599 | 121.5317 | 121.4951 | 121.6461 | 121.6599 | 121.6415 | 121.582 | 0.027466 | -0.09613
1378.9219 | 121.7331 | -121.5958 | 0.036621 | -0.19264 | 0.013418 | 0.0023605 | 0.033077 | -0.01446 | -0.0093311 | 0.015125 | 0.2243 | 0 | 0.19684 | 0.036621 | 0.13733 | 0.17853 | 0.073242 | 0.28381 | -0.059509 | 0.07782 | 121.7926 | -0.036621 | 121.8201 | 121.6324 | 0.10071 | 121.6736 | -0.09613 | 0.027466 | 121.669 | 121.8796 | 121.7331 | 121.5958 | 121.8201 | 121.5363 | 121.7743 | 121.6736 | 121.5958 | 121.8201 | 121.7743 | 121.7331 | 121.5363 | 0.16022 | 0.041199
1380.625 | 121.8613 | -121.5683 | -0.013733 | 0.02861 | 0.012136 | -0.00084389 | 0.034145 | -0.014674 | -0.0061267 | 0.014484 | 0.036621 | -0.07782 | 0.082397 | -0.022888 | 0.064087 | 0.11444 | -0.018311 | 0.11444 | -0.054932 | -0.041199 | 121.6507 | -0.064087 | 121.6049 | 121.5454 | 0.07782 | 121.5271 | -0.041199 | -0.045776 | 121.55 | 121.6827 | 121.6324 | 121.4905 | 121.6049 | 121.5134 | 121.6827 | 121.5271 | 121.4905 | 121.6049 | 121.6827 | 121.6324 | 121.5134 | 0.09613 | -0.027466
1382.3906 | 121.8292 | -121.6049 | 0 | 0.13542 | 0.0095724 | 0.0030013 | 0.038204 | -0.011683 | -0.0076221 | 0.015338 | -0.036621 | -0.20142 | -0.041199 | 0.041199 | 0.11902 | 0.17395 | -0.24261 | -0.009155 | -0.045776 | -0.11444 | 121.5637 | -0.20142 | 121.5683 | 121.6461 | 0.11902 | 121.4905 | -0.045776 | 0.004578 | 121.3623 | 121.5958 | 121.7239 | 121.4035 | 121.5683 | 121.5591 | 121.7789 | 121.4905 | 121.4035 | 121.5683 | 121.7789 | 121.7239 | 121.5591 | -0.041199 | -0.11444
1384.1406 | 121.8063 | -121.6095 | 0.027466 | -0.22316 | 0.011495 | 0.0034287 | 0.0397 | -0.015101 | -0.0084765 | 0.013843 | 0.10071 | 0 | 0.16022 | -0.068665 | 0.009155 | 0.036621 | 0.19684 | 0.086975 | 0.004578 | 0.032043 | 121.7697 | -0.027466 | 121.7102 | 121.5408 | -0.018311 | 121.6415 | -0.022888 | -0.059509 | 121.8063 | 121.6965 | 121.6187 | 121.6095 | 121.7102 | 121.6141 | 121.6461 | 121.6415 | 121.6095 | 121.7102 | 121.6461 | 121.6187 | 121.6141 | 0.13275 | 0.004577
1385.875 | 121.8613 | -121.5775 | -0.004578 | 0.18883 | 0.011068 | -0.00020289 | 0.038204 | -0.011683 | -0.0095447 | 0.016406 | -0.15564 | -0.22888 | -0.09613 | -0.027466 | 0.045776 | 0.09613 | -0.21515 | -0.14191 | -0.027466 | -0.17395 | 121.4813 | -0.2243 | 121.4218 | 121.55 | 0.050354 | 121.4035 | -0.022888 | -0.05951 | 121.3623 | 121.4355 | 121.6232 | 121.3486 | 121.4218 | 121.55 | 121.6736 | 121.4035 | 121.3486 | 121.4218 | 121.6736 | 121.6232 | 121.55 | -0.091552 | -0.16937
1387.5625 | 121.8796 | -121.5729 | -0.004578 | -0.0095368 | 0.010854 | 0.0040695 | 0.033505 | -0.012751 | -0.0080493 | 0.015979 | 0.086975 | -0.059509 | 0.1236 | -0.009155 | 0.068665 | 0.13733 | -0.009155 | 0.15564 | -0.054932 | -0.022888 | 121.6965 | -0.054931 | 121.6599 | 121.5637 | 0.073243 | 121.55 | -0.050354 | -0.036621 | 121.5637 | 121.7285 | 121.6415 | 121.5134 | 121.6599 | 121.5179 | 121.7102 | 121.55 | 121.5134 | 121.6599 | 121.7102 | 121.6415 | 121.5179 | 0.12817 | -0.01831
1389.3281 | 121.7926 | -121.637 | 0.018311 | -0.21553 | 0.010427 | 0.0040695 | 0.035854 | -0.014674 | -0.0099719 | 0.01427 | 0.16022 | 0.018311 | 0.17853 | -0.027466 | 0.054932 | 0.091553 | 0.16479 | 0.16937 | -0.013733 | 0.07782 | 121.8155 | 0 | 121.7972 | 121.6095 | 0.036621 | 121.7148 | -0.032044 | -0.018311 | 121.8018 | 121.8063 | 121.6919 | 121.6553 | 121.7972 | 121.6232 | 121.7285 | 121.7148 | 121.6553 | 121.7972 | 121.7285 | 121.6919 | 121.6232 | 0.16022 | 0.059509
1391.0781 | 121.8658 | -121.6095 | 0.027466 | 0.14305 | 0.012136 | 0.0038559 | 0.036923 | -0.014674 | -0.0063403 | 0.015125 | -0.036621 | -0.23804 | -0.054932 | 0.041199 | 0.09613 | 0.16479 | -0.2655 | -0.032043 | -0.054932 | -0.15106 | 121.5546 | -0.2655 | 121.5729 | 121.6507 | 0.068664 | 121.4584 | -0.082398 | 0.018311 | 121.344 | 121.5775 | 121.7056 | 121.3715 | 121.5729 | 121.5546 | 121.7743 | 121.4584 | 121.3715 | 121.5729 | 121.7743 | 121.7056 | 121.5546 | -0.082398 | -0.17853
1392.7812 | 121.7697 | -121.6553 | 0.054932 | -0.16975 | 0.009786 | 0.0049241 | 0.035641 | -0.014674 | -0.0061267 | 0.015979 | 0.23346 | -0.009155 | 0.21973 | 0.064087 | 0.1236 | 0.14648 | 0.068665 | 0.27466 | -0.036621 | 0.073242 | 121.875 | -0.064087 | 121.8887 | 121.7194 | 0.068664 | 121.7285 | -0.091553 | 0.013732 | 121.7239 | 121.9299 | 121.7789 | 121.6461 | 121.8887 | 121.6187 | 121.8018 | 121.7285 | 121.6461 | 121.8887 | 121.8018 | 121.7789 | 121.6187 | 0.16479 | 0.01831
1394.5312 | 121.8018 | -121.637 | 0.018311 | -0.14687 | 0.010641 | 0.0042831 | 0.039913 | -0.015101 | -0.0093311 | 0.018543 | 0.073242 | -0.027466 | 0.1236 | -0.045776 | 0.009155 | 0.050354 | 0.13275 | 0.073242 | -0.018311 | 0.009155 | 121.7606 | -0.045777 | 121.7102 | 121.5912 | -0.009156 | 121.6461 | -0.036622 | -0.050354 | 121.7697 | 121.7102 | 121.6461 | 121.6095 | 121.7102 | 121.6187 | 121.6873 | 121.6461 | 121.6095 | 121.7102 | 121.6873 | 121.6461 | 121.6187 | 0.10528 | -0.009156
1396.2969 | 121.8384 | -121.6461 | 0.018311 | -0.17738 | 0.011068 | 0.0012925 | 0.03735 | -0.012751 | -0.010613 | 0.015979 | 0.091553 | -0.036621 | 0.16479 | -0.082397 | 0.018311 | 0.036621 | 0.15106 | 0.082397 | -0.009155 | 0.032043 | 121.8109 | -0.054932 | 121.7377 | 121.5637 | 0 | 121.6782 | -0.027466 | -0.073242 | 121.7972 | 121.7285 | 121.6644 | 121.6095 | 121.7377 | 121.637 | 121.6827 | 121.6782 | 121.6095 | 121.7377 | 121.6827 | 121.6644 | 121.637 | 0.14648 | 0.013732
1398 | 121.7926 | -121.6827 | 0.036621 | -0.10109 | 0.011281 | 0.0023605 | 0.040554 | -0.014247 | -0.0071947 | 0.015765 | 0.059509 | -0.10071 | 0.064087 | -0.013733 | 0.059509 | 0.086975 | 0 | 0.027466 | -0.004578 | -0.041199 | 121.7468 | -0.13733 | 121.7422 | 121.669 | 0.022888 | 121.6415 | -0.041199 | -0.004578 | 121.6827 | 121.7102 | 121.7422 | 121.582 | 121.7422 | 121.6782 | 121.7697 | 121.6415 | 121.582 | 121.7422 | 121.7697 | 121.7422 | 121.6782 | 0.027466 | -0.07782
1399.75 | 121.9391 | -121.6324 | -0.013733 | 0.013352 | 0.009786 | -0.00020289 | 0.032436 | -0.011469 | -0.0074085 | 0.014911 | 0.041199 | -0.07782 | 0.082397 | -0.027466 | 0.059509 | 0.11444 | 0.009155 | 0.10071 | -0.036621 | -0.045776 | 121.7148 | -0.064087 | 121.6736 | 121.6049 | 0.073242 | 121.5866 | -0.022888 | -0.041198 | 121.6415 | 121.7331 | 121.6919 | 121.5546 | 121.6736 | 121.5958 | 121.7468 | 121.5866 | 121.5546 | 121.6736 | 121.7468 | 121.6919 | 121.5958 | 0.09613 | -0.032043
1401.5 | 121.907 | -121.6507 | 0.022888 | 0.1812 | 0.0082906 | 0.0047103 | 0.037136 | -0.011042 | -0.0082629 | 0.017474 | -0.036621 | -0.2243 | -0.045776 | 0.045776 | 0.10986 | 0.15564 | -0.27008 | -0.009155 | -0.054932 | -0.15106 | 121.6049 | -0.24719 | 121.6141 | 121.6965 | 0.086975 | 121.4996 | -0.07782 | 0.009155 | 121.3806 | 121.6415 | 121.7606 | 121.4264 | 121.6141 | 121.5958 | 121.8063 | 121.4996 | 121.4264 | 121.6141 | 121.8063 | 121.7606 | 121.5958 | -0.068664 | -0.17395
1403.25 | 121.9299 | -121.6553 | 0.009155 | 0.0057222 | 0.011068 | -0.0012711 | 0.033932 | -0.013392 | -0.0097583 | 0.017047 | 0.07782 | -0.059509 | 0.11902 | -0.013733 | 0.091553 | 0.13733 | 0.013733 | 0.14191 | -0.027466 | -0.009155 | 121.7743 | -0.068664 | 121.7331 | 121.6415 | 0.082398 | 121.6461 | -0.036621 | -0.041199 | 121.669 | 121.7972 | 121.7468 | 121.5958 | 121.7331 | 121.6278 | 121.7926 | 121.6461 | 121.5958 | 121.7331 | 121.7926 | 121.7468 | 121.6278 | 0.10986 | -0.01831
1404.9375 | 121.8796 | -121.669 | 0.041199 | -0.21553 | 0.01235 | 1.071e-05 | 0.038632 | -0.012751 | -0.010186 | 0.013629 | 0.1831 | 0.013733 | 0.17853 | -0.041199 | 0.032043 | 0.050354 | 0.19226 | 0.17395 | 0 | 0.054932 | 121.8475 | -0.027466 | 121.8521 | 121.6278 | -0.009156 | 121.7239 | -0.041199 | 0.004577 | 121.8613 | 121.843 | 121.701 | 121.6827 | 121.8521 | 121.669 | 121.7194 | 121.7239 | 121.6827 | 121.8521 | 121.7194 | 121.701 | 121.669 | 0.13733 | 0.013733
1406.6875 | 121.8292 | -121.6736 | 0.032043 | -0.047684 | 0.010854 | 0.0034287 | 0.039913 | -0.013819 | -0.011254 | 0.017474 | 0.009155 | -0.16479 | -0.009155 | 0 | 0.050354 | 0.09613 | -0.064087 | -0.045776 | -0.027466 | -0.086975 | 121.6644 | -0.19684 | 121.6827 | 121.6736 | 0.018311 | 121.5866 | -0.059509 | 0.01831 | 121.6095 | 121.6278 | 121.7239 | 121.5088 | 121.6827 | 121.6461 | 121.7697 | 121.5866 | 121.5088 | 121.6827 | 121.7697 | 121.7239 | 121.6461 | -0.041198 | -0.11902
1408.4375 | 121.8521 | -121.6873 | 0.027466 | -0.16212 | 0.0091452 | 0.0017197 | 0.036068 | -0.01446 | -0.0093311 | 0.01662 | 0.20142 | 0 | 0.21057 | 0.027466 | 0.10986 | 0.12817 | 0.11902 | 0.24261 | -0.041199 | 0.073242 | 121.8979 | -0.027466 | 121.8887 | 121.7148 | 0.082397 | 121.7606 | -0.068665 | -0.009155 | 121.8063 | 121.9299 | 121.7972 | 121.6873 | 121.8887 | 121.6461 | 121.8155 | 121.7606 | 121.6873 | 121.8887 | 121.8155 | 121.7972 | 121.6461 | 0.18311 | 0.045776
1410.1875 | 121.962 | -121.669 | -0.009155 | 0.0057222 | 0.011068 | 0.0062057 | 0.034145 | -0.012538 | -0.0082629 | 0.014911 | 0.041199 | -0.07782 | 0.082397 | -0.018311 | 0.064087 | 0.11902 | -0.004578 | 0.091553 | -0.036621 | -0.022888 | 121.7514 | -0.068665 | 121.7102 | 121.6507 | 0.073242 | 121.6461 | -0.027466 | -0.041198 | 121.6644 | 121.7606 | 121.7331 | 121.5912 | 121.7102 | 121.6324 | 121.788 | 121.6461 | 121.5912 | 121.7102 | 121.788 | 121.7331 | 121.6324 | 0.091552 | -0.013733
1411.875 | 121.9482 | -121.6507 | 0.018311 | 0.097275 | 0.01299 | 0.0079147 | 0.041409 | -0.011042 | -0.010399 | 0.016406 | -0.14191 | -0.20142 | -0.10071 | -0.07782 | -0.009155 | 0.032043 | -0.1236 | -0.21515 | 0 | -0.1831 | 121.55 | -0.21973 | 121.5088 | 121.5729 | -0.027466 | 121.4676 | -0.018311 | -0.041199 | 121.5271 | 121.4355 | 121.6415 | 121.4493 | 121.5088 | 121.6507 | 121.6827 | 121.4676 | 121.4493 | 121.5088 | 121.6827 | 121.6415 | 121.6507 | -0.11902 | -0.20142
1413.625 | 121.843 | -121.7056 | 0.032043 | -0.18501 | 0.0093588 | 0.0030013 | 0.035214 | -0.015315 | -0.0097583 | 0.018329 | 0.22888 | -0.013733 | 0.20142 | 0.059509 | 0.13733 | 0.16479 | 0.073242 | 0.29755 | -0.036621 | 0.082397 | 121.907 | -0.045776 | 121.9345 | 121.7651 | 0.10529 | 121.788 | -0.068664 | 0.027466 | 121.7789 | 122.0032 | 121.843 | 121.6919 | 121.9345 | 121.669 | 121.8704 | 121.788 | 121.6919 | 121.9345 | 121.8704 | 121.843 | 121.669 | 0.16937 | 0.050354
1415.375 | 121.8338 | -121.7056 | 0.032043 | -0.055313 | 0.013418 | 0.0021469 | 0.038845 | -0.011683 | -0.010613 | 0.017474 | 0.036621 | -0.11902 | 0.041199 | -0.009155 | 0.054932 | 0.091553 | -0.027466 | -0.013733 | -0.009155 | -0.050354 | 121.7468 | -0.15106 | 121.7422 | 121.6965 | 0.022889 | 121.6553 | -0.041198 | -0.004578 | 121.6782 | 121.6919 | 121.7606 | 121.5866 | 121.7422 | 121.6965 | 121.7972 | 121.6553 | 121.5866 | 121.7422 | 121.7972 | 121.7606 | 121.6965 | 0.009156 | -0.082397
1417.0625 | 121.9162 | -121.701 | 0.032043 | -0.21553 | 0.01235 | 0.0042831 | 0.037563 | -0.012324 | -0.0091173 | 0.016834 | 0.10529 | 0.009155 | 0.13733 | -0.068665 | 0.018311 | 0.032043 | 0.18768 | 0.091553 | 0 | -0.064087 | 121.8384 | -0.022888 | 121.8063 | 121.6324 | -0.013732 | 121.637 | -0.032043 | -0.032043 | 121.8887 | 121.7926 | 121.7194 | 121.7102 | 121.8063 | 121.701 | 121.7331 | 121.637 | 121.7102 | 121.8063 | 121.7331 | 121.7194 | 121.701 | 0.10529 | -0.09613
1418.8125 | 121.8704 | -121.7148 | 0.054932 | -0.18501 | 0.014058 | 0.0027877 | 0.040341 | -0.011897 | -0.0091173 | 0.015765 | 0.086975 | -0.045776 | 0.11902 | -0.027466 | 0.036621 | 0.07782 | 0.064087 | 0.07782 | -0.013733 | -0.050354 | 121.8338 | -0.10071 | 121.8018 | 121.6873 | -0.018311 | 121.6644 | -0.068665 | -0.032044 | 121.7789 | 121.7926 | 121.7514 | 121.669 | 121.8018 | 121.701 | 121.7926 | 121.6644 | 121.669 | 121.8018 | 121.7926 | 121.7514 | 121.701 | 0.064087 | -0.10529
1420.5 | 121.907 | -121.701 | 0.018311 | -0.21553 | 0.011922 | 0.0038559 | 0.036495 | -0.011683 | -0.0091173 | 0.016406 | 0.091553 | 0.004578 | 0.15106 | -0.07782 | 0.027466 | 0.041199 | 0.20142 | 0.086975 | 0.004578 | -0.064087 | 121.8521 | -0.013733 | 121.7926 | 121.6232 | 0.009155 | 121.637 | -0.013733 | -0.059509 | 121.9025 | 121.788 | 121.7285 | 121.7056 | 121.7926 | 121.7056 | 121.7422 | 121.637 | 121.7056 | 121.7926 | 121.7422 | 121.7285 | 121.7056 | 0.13275 | -0.082398
1422.25 | 121.9528 | -121.7056 | 0.018311 | 0.15068 | 0.011068 | 0.0059921 | 0.036068 | -0.010615 | -0.0095447 | 0.015552 | -0.032043 | -0.21057 | -0.059509 | 0.045776 | 0.11902 | 0.17853 | -0.25635 | 0.004578 | -0.050354 | -0.027466 | 121.6461 | -0.22888 | 121.6736 | 121.7514 | 0.10071 | 121.6782 | -0.068665 | 0.027466 | 121.4493 | 121.7102 | 121.8246 | 121.4951 | 121.6736 | 121.6553 | 121.8842 | 121.6782 | 121.4951 | 121.6736 | 121.8842 | 121.8246 | 121.6553 | -0.07782 | -0.045777
1424 | 122.0169 | -121.7056 | -0.018311 | 0.12016 | 0.0089316 | 0.0070603 | 0.039272 | -0.011042 | -0.0089037 | 0.017261 | -0.14191 | -0.17395 | -0.082397 | -0.086975 | -0.013733 | 0.027466 | -0.1236 | -0.20599 | -0.013733 | -0.059509 | 121.6232 | -0.15564 | 121.5637 | 121.6187 | 0.004578 | 121.6461 | 0.004578 | -0.05951 | 121.582 | 121.4996 | 121.6919 | 121.5317 | 121.5637 | 121.6919 | 121.7331 | 121.6461 | 121.5317 | 121.5637 | 121.7331 | 121.6919 | 121.6919 | -0.064086 | -0.041198
1425.6875 | 121.9025 | -121.7514 | 0.036621 | -0.1545 | 0.009786 | 0.0049241 | 0.039059 | -0.01446 | -0.0084765 | 0.014911 | 0.086975 | -0.027466 | 0.13275 | -0.045776 | 0.032043 | 0.059509 | 0.11902 | 0.050354 | -0.004578 | -0.064087 | 121.8842 | -0.064087 | 121.8384 | 121.7056 | -0.004578 | 121.6873 | -0.041199 | -0.045776 | 121.8704 | 121.8018 | 121.7834 | 121.7239 | 121.8384 | 121.7468 | 121.8109 | 121.6873 | 121.7239 | 121.8384 | 121.8109 | 121.7834 | 121.7468 | 0.09613 | -0.10071
1427.4375 | 121.9757 | -121.7285 | 0 | 0.16594 | 0.012563 | 0.0059921 | 0.03735 | -0.011042 | -0.01104 | 0.017474 | -0.073242 | -0.21973 | -0.07782 | 0.013733 | 0.091553 | 0.15564 | -0.24261 | -0.064087 | -0.041199 | -0.045776 | 121.6507 | -0.21973 | 121.6553 | 121.7422 | 0.091553 | 121.6827 | -0.041199 | 0.004578 | 121.4859 | 121.6644 | 121.8201 | 121.5088 | 121.6553 | 121.6873 | 121.8842 | 121.6827 | 121.5088 | 121.6553 | 121.8842 | 121.8201 | 121.6873 | -0.07782 | -0.045776
1429.2031 | 121.9116 | -121.7422 | 0.009155 | -0.13924 | 0.011068 | 0.0047103 | 0.037777 | -0.010829 | -0.011467 | 0.016834 | 0.09613 | -0.004578 | 0.14191 | -0.064087 | 0.032043 | 0.050354 | 0.14191 | 0.045776 | 0 | -0.050354 | 121.8842 | -0.013733 | 121.8384 | 121.6782 | 0.022888 | 121.6919 | -0.009155 | -0.045777 | 121.8842 | 121.788 | 121.7743 | 121.7377 | 121.8384 | 121.7422 | 121.7926 | 121.6919 | 121.7377 | 121.8384 | 121.7926 | 121.7743 | 121.7422 | 0.13275 | -0.059509
1430.8906 | 121.9299 | -121.7606 | 0.036621 | -0.18501 | 0.0099996 | 1.071e-05 | 0.033505 | -0.012324 | -0.0097583 | 0.016834 | 0.18768 | -0.004578 | 0.19226 | 0.027466 | 0.10986 | 0.13275 | 0.14191 | 0.25635 | -0.036621 | -0.041199 | 121.9528 | -0.041199 | 121.9482 | 121.788 | 0.073242 | 121.7194 | -0.073242 | -0.004578 | 121.9025 | 122.0169 | 121.8704 | 121.756 | 121.9482 | 121.7239 | 121.8933 | 121.7194 | 121.756 | 121.9482 | 121.8933 | 121.8704 | 121.7239 | 0.15564 | -0.07782
1432.6406 | 121.8887 | -121.8155 | 0.032043 | -0.047684 | 0.011068 | 0.0042831 | 0.040554 | -0.012324 | -0.0089037 | 0.018329 | 0.050354 | -0.091553 | 0.064087 | 0 | 0.045776 | 0.09613 | -0.013733 | 0.018311 | -0.013733 | -0.050354 | 121.8796 | -0.1236 | 121.8658 | 121.8155 | 0.013733 | 121.7651 | -0.045776 | -0.013733 | 121.8018 | 121.8338 | 121.8613 | 121.7239 | 121.8658 | 121.8018 | 121.9116 | 121.7651 | 121.7239 | 121.8658 | 121.9116 | 121.8613 | 121.8018 | 0.032044 | -0.082397
1434.3594 | 122.0261 | -121.7468 | 0.009155 | -0.017166 | 0.010213 | 0.0053513 | 0.033291 | -0.013819 | -0.0067675 | 0.016834 | 0.086975 | -0.059509 | 0.10986 | 0 | 0.082397 | 0.15106 | 0.022888 | 0.17395 | -0.032043 | -0.027466 | 121.8567 | -0.068664 | 121.8338 | 121.7468 | 0.073242 | 121.7194 | -0.041198 | -0.022888 | 121.7697 | 121.9208 | 121.8292 | 121.6873 | 121.8338 | 121.7148 | 121.8979 | 121.7194 | 121.6873 | 121.8338 | 121.8979 | 121.8292 | 121.7148 | 0.10071 | -0.036621
1436.1094 | 122.0123 | -121.7606 | 0.013733 | 0.11253 | 0.0099996 | 0.0059921 | 0.037136 | -0.013819 | -0.0089037 | 0.016193 | -0.036621 | -0.17395 | -0.032043 | 0.027466 | 0.086975 | 0.15564 | -0.17395 | 0.027466 | -0.041199 | -0.013733 | 121.7285 | -0.18768 | 121.7239 | 121.788 | 0.073242 | 121.7468 | -0.054932 | -0.004578 | 121.5866 | 121.788 | 121.8475 | 121.5866 | 121.7239 | 121.7194 | 121.9162 | 121.7468 | 121.5866 | 121.7239 | 121.9162 | 121.8475 | 121.7194 | -0.045776 | -0.027466
1437.8594 | 121.9986 | -121.756 | 0.022888 | 0.12779 | 0.011068 | 0.0044967 | 0.036709 | -0.014674 | -0.0091173 | 0.017474 | -0.036621 | -0.21057 | -0.050354 | 0.032043 | 0.11444 | 0.17395 | -0.21973 | 0.032043 | -0.059509 | -0.013733 | 121.7056 | -0.23346 | 121.7194 | 121.788 | 0.091553 | 121.7422 | -0.082397 | 0.013733 | 121.5363 | 121.788 | 121.8704 | 121.5454 | 121.7194 | 121.6965 | 121.9299 | 121.7422 | 121.5454 | 121.7194 | 121.9299 | 121.8704 | 121.6965 | -0.073242 | -0.036621
1439.5469 | 122.0032 | -121.7377 | 0.027466 | 0.074387 | 0.013204 | 0.0064193 | 0.040768 | -0.015101 | -0.0091173 | 0.01662 | -0.091553 | -0.1831 | -0.064087 | -0.07782 | -0.027466 | 0.022888 | -0.059509 | -0.16022 | -0.013733 | -0.059509 | 121.6736 | -0.21057 | 121.6461 | 121.6599 | -0.054932 | 121.6782 | -0.041199 | -0.027466 | 121.6782 | 121.5775 | 121.7102 | 121.5546 | 121.6461 | 121.7239 | 121.7606 | 121.6782 | 121.5546 | 121.6461 | 121.7606 | 121.7102 | 121.7239 | -0.091553 | -0.086975
1441.3125 | 121.9482 | -121.7697 | 0.041199 | -0.23079 | 0.0076498 | 0.00065151 | 0.035641 | -0.01681 | -0.0095447 | 0.017688 | 0.1831 | -0.022888 | 0.19226 | -0.004578 | 0.068665 | 0.1236 | 0.14191 | 0.22888 | -0.032043 | -0.045776 | 121.962 | -0.064087 | 121.9528 | 121.7651 | 0.027466 | 121.7239 | -0.073242 | -0.009156 | 121.9116 | 121.9986 | 121.8384 | 121.7468 | 121.9528 | 121.7377 | 121.8933 | 121.7239 | 121.7468 | 121.9528 | 121.8933 | 121.8384 | 121.7377 | 0.15106 | -0.086975
1443.0625 | 121.9345 | -121.7972 | 0.041199 | -0.17738 | 0.010213 | 0.0015061 | 0.032009 | -0.015101 | -0.0074085 | 0.016193 | 0.21973 | -0.009155 | 0.20599 | 0.050354 | 0.12817 | 0.17395 | 0.064087 | 0.29755 | -0.054932 | -0.022888 | 122.0032 | -0.050354 | 122.0169 | 121.8475 | 0.086975 | 121.7743 | -0.096131 | 0.013733 | 121.8613 | 122.0947 | 121.9254 | 121.788 | 122.0169 | 121.7422 | 121.9711 | 121.7743 | 121.788 | 122.0169 | 121.9711 | 121.9254 | 121.7422 | 0.1648 | -0.064087
1444.8125 | 122.0535 | -121.7606 | 0 | 0.0057222 | 0.0089316 | 0.0021469 | 0.033505 | -0.012965 | -0.0078357 | 0.015338 | 0.068665 | -0.059509 | 0.10529 | -0.022888 | 0.059509 | 0.12817 | 0 | 0.13275 | -0.022888 | -0.045776 | 121.8658 | -0.059509 | 121.8292 | 121.7377 | 0.059509 | 121.7148 | -0.022888 | -0.036621 | 121.7606 | 121.8933 | 121.8201 | 121.701 | 121.8292 | 121.7377 | 121.8887 | 121.7148 | 121.701 | 121.8292 | 121.8887 | 121.8201 | 121.7377 | 0.10529 | -0.045776
1446.5156 | 121.9254 | -121.8018 | 0.027466 | -0.055313 | 0.010427 | 0.0051377 | 0.041409 | -0.011683 | -0.011467 | 0.013843 | 0.045776 | -0.11444 | 0.050354 | 0.004578 | 0.041199 | 0.086975 | -0.036621 | 0.013733 | -0.009155 | -0.059509 | 121.8521 | -0.14191 | 121.8475 | 121.8063 | 0.013733 | 121.7422 | -0.036621 | -0.004578 | 121.7651 | 121.8155 | 121.843 | 121.6873 | 121.8475 | 121.7926 | 121.8887 | 121.7422 | 121.6873 | 121.8475 | 121.8887 | 121.843 | 121.7926 | 0.022888 | -0.086975
1448.2812 | 122.0398 | -121.7651 | 0.022888 | 0.066757 | 0.011495 | 0.0027877 | 0.040554 | -0.011897 | -0.0097583 | 0.016406 | -0.11902 | -0.18768 | -0.07782 | -0.07782 | -0.022888 | 0.027466 | -0.07782 | -0.17395 | -0.004578 | -0.045776 | 121.6873 | -0.21057 | 121.6461 | 121.6873 | -0.045776 | 121.7194 | -0.027466 | -0.041199 | 121.6873 | 121.5912 | 121.7422 | 121.5775 | 121.6461 | 121.7606 | 121.7926 | 121.7194 | 121.5775 | 121.6461 | 121.7926 | 121.7422 | 121.7606 | -0.10071 | -0.068664
1450.0312 | 122.0718 | -121.7697 | 0.009155 | 0.089645 | 0.010641 | 0.0038559 | 0.033505 | -0.012965 | -0.0099719 | 0.016193 | -0.027466 | -0.16022 | 0.013733 | -0.022888 | 0.07782 | 0.13275 | -0.09613 | 0.045776 | -0.064087 | -0.018311 | 121.7834 | -0.16937 | 121.7422 | 121.7468 | 0.068665 | 121.7514 | -0.073242 | -0.041199 | 121.6736 | 121.8155 | 121.8475 | 121.6095 | 121.7422 | 121.7056 | 121.9025 | 121.7514 | 121.6095 | 121.7422 | 121.9025 | 121.8475 | 121.7056 | 0.004578 | -0.027466
1451.7812 | 121.9803 | -121.7972 | 0.013733 | 0.051498 | 0.012777 | 0.0030013 | 0.041195 | -0.012538 | -0.010826 | 0.016193 | -0.050354 | -0.16479 | -0.032043 | -0.068665 | 0.009155 | 0.041199 | -0.068665 | -0.12817 | -0.013733 | -0.059509 | 121.7651 | -0.17853 | 121.7468 | 121.7285 | -0.004578 | 121.7377 | -0.027466 | -0.018311 | 121.7285 | 121.669 | 121.8063 | 121.6324 | 121.7468 | 121.7834 | 121.8384 | 121.7377 | 121.6324 | 121.7468 | 121.8384 | 121.8063 | 121.7834 | -0.045776 | -0.073242
1453.4844 | 122.0306 | -121.7789 | 0.009155 | 0.12779 | 0.010427 | 0.00022431 | 0.036709 | -0.015315 | -0.0082629 | 0.017261 | -0.032043 | -0.20599 | -0.050354 | 0.041199 | 0.11444 | 0.1831 | -0.24261 | 0.022888 | -0.041199 | -0.022888 | 121.7285 | -0.21515 | 121.7468 | 121.8201 | 0.10529 | 121.756 | -0.050354 | 0.018311 | 121.5363 | 121.8018 | 121.8933 | 121.5729 | 121.7468 | 121.7377 | 121.962 | 121.756 | 121.5729 | 121.7468 | 121.962 | 121.8933 | 121.7377 | -0.059509 | -0.032043
1455.2344 | 121.9528 | -121.8246 | 0.027466 | -0.1545 | 0.011495 | 0.0034287 | 0.035854 | -0.015315 | -0.0071947 | 0.015338 | 0.21057 | -0.004578 | 0.19226 | 0.068665 | 0.11444 | 0.16479 | 0.07782 | 0.3067 | -0.036621 | -0.032043 | 122.0169 | -0.032044 | 122.0352 | 121.8933 | 0.086975 | 121.7926 | -0.064087 | 0.01831 | 121.9025 | 122.1313 | 121.9391 | 121.8201 | 122.0352 | 121.788 | 121.9894 | 121.7926 | 121.8201 | 122.0352 | 121.9894 | 121.9391 | 121.788 | 0.16479 | -0.059509
1456.9844 | 122.0123 | -121.8155 | 0.032043 | -0.16212 | 0.009786 | 0.00065151 | 0.035214 | -0.013606 | -0.0086901 | 0.014697 | 0.15106 | 0.009155 | 0.17853 | -0.032043 | 0.041199 | 0.059509 | 0.20599 | 0.16022 | -0.004578 | -0.064087 | 121.994 | -0.022888 | 121.9666 | 121.7834 | 0.009156 | 121.7514 | -0.036621 | -0.027466 | 122.0215 | 121.9757 | 121.8567 | 121.8246 | 121.9666 | 121.8109 | 121.875 | 121.7514 | 121.8246 | 121.9666 | 121.875 | 121.8567 | 121.8109 | 0.14648 | -0.09613
1458.6719 | 121.9894 | -121.8338 | 0.027466 | -0.16212 | 0.013418 | 0.0044967 | 0.038204 | -0.013178 | -0.0093311 | 0.016193 | 0.09613 | -0.041199 | 0.14191 | -0.036621 | 0.027466 | 0.041199 | 0.11444 | 0.07782 | -0.018311 | -0.054932 | 121.9757 | -0.068665 | 121.9299 | 121.7972 | 0 | 121.7789 | -0.045777 | -0.045777 | 121.9482 | 121.9116 | 121.8613 | 121.7926 | 121.9299 | 121.8155 | 121.875 | 121.7789 | 121.7926 | 121.9299 | 121.875 | 121.8613 | 121.8155 | 0.11444 | -0.082398
1460.4219 | 122.0352 | -121.8567 | 0.022888 | -0.16212 | 0.011281 | 0.0012925 | 0.032223 | -0.013606 | -0.0080493 | 0.016406 | 0.16022 | -0.032043 | 0.14191 | 0.041199 | 0.13275 | 0.17395 | 0.032043 | 0.26093 | -0.041199 | -0.050354 | 121.9986 | -0.054931 | 122.0169 | 121.8979 | 0.10986 | 121.8063 | -0.064087 | 0.01831 | 121.8887 | 122.1176 | 121.9894 | 121.8246 | 122.0169 | 121.8155 | 122.0306 | 121.8063 | 121.8246 | 122.0169 | 122.0306 | 121.9894 | 121.8155 | 0.11902 | -0.073242
1462.1875 | 122.0535 | -121.8109 | -0.022888 | 0.15831 | 0.011922 | 0.0010787 | 0.039486 | -0.011683 | -0.0089037 | 0.01662 | -0.064087 | -0.21057 | -0.059509 | 0.022888 | 0.07782 | 0.15106 | -0.24719 | -0.036621 | -0.018311 | -0.036621 | 121.7514 | -0.18768 | 121.7468 | 121.8338 | 0.10071 | 121.7743 | 0.004577 | -0.004578 | 121.5637 | 121.7743 | 121.8887 | 121.6003 | 121.7468 | 121.7926 | 121.962 | 121.7743 | 121.6003 | 121.7468 | 121.962 | 121.8887 | 121.7926 | -0.036621 | -0.013733
1463.8906 | 121.9849 | -121.8567 | 0.036621 | -0.1545 | 0.011495 | -0.0014847 | 0.034573 | -0.014887 | -0.0093311 | 0.016193 | 0.2243 | -0.027466 | 0.20142 | 0.054932 | 0.13275 | 0.16479 | 0.064087 | 0.35248 | -0.036621 | -0.027466 | 122.0581 | -0.064087 | 122.081 | 121.9116 | 0.09613 | 121.8292 | -0.073242 | 0.022888 | 121.9208 | 122.2092 | 121.9894 | 121.8292 | 122.081 | 121.8201 | 122.0215 | 121.8292 | 121.8292 | 122.081 | 122.0215 | 121.9894 | 121.8201 | 0.1648 | -0.064087
1465.6406 | 122.0673 | -121.8063 | -0.013733 | 0.17357 | 0.01235 | 0.00043791 | 0.038632 | -0.013819 | -0.0093311 | 0.015979 | -0.073242 | -0.21973 | -0.064087 | 0.018311 | 0.091553 | 0.15106 | -0.23804 | -0.064087 | -0.054932 | -0.027466 | 121.7422 | -0.20599 | 121.7331 | 121.8246 | 0.10529 | 121.7789 | -0.041199 | -0.009155 | 121.5683 | 121.7422 | 121.8979 | 121.5866 | 121.7331 | 121.7514 | 121.9574 | 121.7789 | 121.5866 | 121.7331 | 121.9574 | 121.8979 | 121.7514 | -0.050354 | -0.013733
1467.3281 | 122.0718 | -121.8384 | 0 | 0.12016 | 0.010641 | 0.0030013 | 0.036282 | -0.011897 | -0.0097583 | 0.016406 | -0.064087 | -0.22888 | -0.068665 | 0.032043 | 0.10529 | 0.16479 | -0.26093 | -0.036621 | -0.041199 | -0.027466 | 121.7697 | -0.22888 | 121.7743 | 121.8704 | 0.10529 | 121.8109 | -0.041199 | 0.004578 | 121.5775 | 121.8018 | 121.9437 | 121.6095 | 121.7743 | 121.7972 | 122.0032 | 121.8109 | 121.6095 | 121.7743 | 122.0032 | 121.9437 | 121.7972 | -0.068665 | -0.027466
1469.0781 | 122.0673 | -121.843 | 0.018311 | 0.15831 | 0.011281 | 0.0012925 | 0.036068 | -0.013606 | -0.0099719 | 0.015338 | -0.041199 | -0.2243 | -0.054932 | 0.045776 | 0.11444 | 0.17853 | -0.25177 | 0 | -0.068665 | -0.009155 | 121.788 | -0.24261 | 121.8018 | 121.8887 | 0.09613 | 121.8338 | -0.086976 | 0.013733 | 121.5912 | 121.843 | 121.9574 | 121.6187 | 121.8018 | 121.7743 | 122.0215 | 121.8338 | 121.6187 | 121.8018 | 122.0215 | 121.9574 | 121.7743 | -0.073243 | -0.027466
1470.7656 | 122.1268 | -121.8246 | 0.013733 | 0.097275 | 0.0095724 | 0.0027877 | 0.034145 | -0.012965 | -0.0065539 | 0.019397 | -0.032043 | -0.16937 | -0.018311 | 0.004578 | 0.073242 | 0.13733 | -0.11444 | 0.054932 | -0.041199 | -0.032043 | 121.8063 | -0.18311 | 121.7926 | 121.8292 | 0.059509 | 121.7926 | -0.054932 | -0.013732 | 121.7102 | 121.8796 | 121.8979 | 121.6553 | 121.7926 | 121.7834 | 121.962 | 121.7926 | 121.6553 | 121.7926 | 121.962 | 121.8979 | 121.7834 | -0.032044 | -0.045776
1472.5312 | 122.0993 | -121.8063 | 0.009155 | 0.16594 | 0.0099996 | 0.0059921 | 0.038418 | -0.012965 | -0.010399 | 0.016834 | -0.11902 | -0.20142 | -0.091553 | -0.022888 | 0.041199 | 0.091553 | -0.20599 | -0.11902 | -0.036621 | -0.036621 | 121.7148 | -0.21057 | 121.6873 | 121.7834 | 0.032044 | 121.7697 | -0.045776 | -0.027466 | 121.6003 | 121.6873 | 121.8475 | 121.6049 | 121.6873 | 121.7697 | 121.8979 | 121.7697 | 121.6049 | 121.6873 | 121.8979 | 121.8475 | 121.7697 | -0.10071 | -0.045776
1474.2188 | 121.994 | -121.8704 | 0.027466 | -0.12398 | 0.014058 | 0.0038559 | 0.035214 | -0.015101 | -0.0074085 | 0.015552 | 0.19684 | -0.018311 | 0.16937 | 0.059509 | 0.16022 | 0.1831 | 0.068665 | 0.30212 | -0.045776 | -0.036621 | 122.0398 | -0.045777 | 122.0673 | 121.9299 | 0.13275 | 121.8338 | -0.073242 | 0.027465 | 121.9391 | 122.1725 | 122.0306 | 121.8521 | 122.0673 | 121.8246 | 122.0535 | 121.8338 | 121.8521 | 122.0673 | 122.0535 | 122.0306 | 121.8246 | 0.14191 | -0.064087
1475.9688 | 122.0627 | -121.8292 | 0.013733 | -0.21553 | 0.011709 | 0.00043791 | 0.039272 | -0.014887 | -0.0095447 | 0.014911 | 0.11444 | -0.018311 | 0.15564 | -0.059509 | 0.009155 | 0.027466 | 0.21057 | 0.10529 | 0.013733 | -0.059509 | 121.9849 | -0.032044 | 121.9437 | 121.7697 | -0.004578 | 121.7697 | 0 | -0.041199 | 122.0398 | 121.9345 | 121.8384 | 121.8109 | 121.9437 | 121.843 | 121.8567 | 121.7697 | 121.8109 | 121.9437 | 121.8567 | 121.8384 | 121.843 | 0.14191 | -0.073242
1477.7188 | 122.049 | -121.8658 | 0.022888 | -0.09346 | 0.011495 | 0.00086511 | 0.034573 | -0.013392 | -0.0086901 | 0.015338 | 0.17395 | -0.022888 | 0.16022 | 0.054932 | 0.1236 | 0.18768 | 0.027466 | 0.28381 | -0.054932 | -0.013733 | 122.0261 | -0.045776 | 122.0398 | 121.9208 | 0.10071 | 121.8521 | -0.07782 | 0.013733 | 121.8933 | 122.1497 | 121.9894 | 121.843 | 122.0398 | 121.8109 | 122.0535 | 121.8521 | 121.843 | 122.0398 | 122.0535 | 121.9894 | 121.8109 | 0.13733 | -0.036621
1479.4219 | 122.1634 | -121.8475 | -0.004578 | 0.066757 | 0.008718 | 0.0023605 | 0.036495 | -0.014033 | -0.0089037 | 0.015338 | -0.022888 | -0.15564 | -0.013733 | -0.009155 | 0.064087 | 0.13275 | -0.086975 | 0.068665 | -0.045776 | -0.041199 | 121.8338 | -0.15106 | 121.8246 | 121.8384 | 0.068665 | 121.8063 | -0.041198 | -0.009155 | 121.7606 | 121.9162 | 121.9116 | 121.6919 | 121.8246 | 121.8018 | 121.9803 | 121.8063 | 121.6919 | 121.8246 | 121.9803 | 121.9116 | 121.8018 | -0.009155 | -0.036621
1481.1875 | 122.049 | -121.8613 | 0.009155 | -0.13924 | 0.0078634 | -0.0014847 | 0.034145 | -0.015315 | -0.0071947 | 0.015338 | 0.19226 | -0.022888 | 0.17395 | 0.073242 | 0.13733 | 0.17853 | 0.032043 | 0.27924 | -0.045776 | -0.022888 | 122.0352 | -0.032043 | 122.0535 | 121.9345 | 0.12817 | 121.8384 | -0.054931 | 0.018311 | 121.8933 | 122.1405 | 121.9986 | 121.8384 | 122.0535 | 121.8155 | 122.0398 | 121.8384 | 121.8384 | 122.0535 | 122.0398 | 121.9986 | 121.8155 | 0.16479 | -0.032043
1482.9375 | 122.0993 | -121.8796 | -0.004578 | 0.14305 | 0.011281 | 0.0040695 | 0.040127 | -0.011042 | -0.0097583 | 0.015552 | -0.032043 | -0.22888 | -0.050354 | 0.054932 | 0.10986 | 0.17395 | -0.27008 | -0.022888 | -0.054932 | 0.004578 | 121.8292 | -0.2243 | 121.8475 | 121.9345 | 0.11444 | 121.8842 | -0.050354 | 0.018311 | 121.6095 | 121.8567 | 121.9894 | 121.6507 | 121.8475 | 121.8246 | 122.0535 | 121.8842 | 121.6507 | 121.8475 | 122.0535 | 121.9894 | 121.8246 | -0.045776 | 0.009156
1484.6406 | 122.1863 | -121.8613 | -0.013733 | 0.020981 | 0.011068 | 0.00086511 | 0.034359 | -0.011897 | -0.0061267 | 0.016406 | 0.027466 | -0.091553 | 0.032043 | -0.004578 | 0.059509 | 0.11902 | -0.004578 | 0.11902 | -0.041199 | -0.036621 | 121.8933 | -0.07782 | 121.8887 | 121.8567 | 0.073242 | 121.8246 | -0.027466 | -0.004577 | 121.8567 | 121.9803 | 121.9208 | 121.7697 | 121.8887 | 121.8201 | 121.9803 | 121.8246 | 121.7697 | 121.8887 | 121.9803 | 121.9208 | 121.8201 | 0.045776 | -0.022888
1486.4062 | 122.0856 | -121.9116 | 0.022888 | -0.22316 | 0.013204 | 0.0036423 | 0.037991 | -0.013392 | -0.0099719 | 0.01662 | 0.11902 | 0.009155 | 0.15564 | -0.059509 | 0.013733 | 0.041199 | 0.2243 | 0.13733 | -0.009155 | -0.064087 | 122.0673 | -0.013733 | 122.0306 | 121.8521 | -0.009155 | 121.8475 | -0.032043 | -0.036621 | 122.1359 | 122.0489 | 121.9254 | 121.9208 | 122.0306 | 121.9025 | 121.9528 | 121.8475 | 121.9208 | 122.0306 | 121.9528 | 121.9254 | 121.9025 | 0.13275 | -0.086975
1488.1562 | 122.1405 | -121.8475 | -0.009155 | 0.12016 | 0.010854 | 0.0017197 | 0.040554 | -0.012324 | -0.01104 | 0.017902 | -0.13733 | -0.2243 | -0.091553 | -0.050354 | 0.018311 | 0.073242 | -0.17395 | -0.13733 | -0.022888 | -0.045776 | 121.756 | -0.21515 | 121.7102 | 121.7972 | 0.027466 | 121.8018 | -0.013733 | -0.045776 | 121.6736 | 121.7102 | 121.8658 | 121.6232 | 121.7102 | 121.8246 | 121.9208 | 121.8018 | 121.6232 | 121.7102 | 121.9208 | 121.8658 | 121.8246 | -0.082398 | -0.036621
1489.9062 | 122.1451 | -121.8521 | 0.009155 | 0.11253 | 0.010641 | 0.0042831 | 0.038632 | -0.013606 | -0.010613 | 0.015552 | -0.14648 | -0.19226 | -0.07782 | -0.086975 | -0.004578 | 0.027466 | -0.10529 | -0.19684 | -0.013733 | -0.050354 | 121.7743 | -0.20142 | 121.7056 | 121.7651 | -0.013733 | 121.8018 | -0.022888 | -0.068664 | 121.7468 | 121.6553 | 121.8475 | 121.6599 | 121.7056 | 121.8384 | 121.8796 | 121.8018 | 121.6599 | 121.7056 | 121.8796 | 121.8475 | 121.8384 | -0.086975 | -0.059509
1491.5938 | 122.1634 | -121.8521 | -0.018311 | 0.13542 | 0.012136 | 0.0034287 | 0.037563 | -0.013392 | -0.0082629 | 0.017902 | -0.15564 | -0.21057 | -0.091553 | -0.07782 | 0 | 0.032043 | -0.11444 | -0.1831 | 0 | -0.07782 | 121.7606 | -0.19226 | 121.6965 | 121.7743 | 0.018311 | 121.7743 | 0.018311 | -0.064087 | 121.7377 | 121.669 | 121.8521 | 121.6415 | 121.6965 | 121.8521 | 121.8842 | 121.7743 | 121.6415 | 121.6965 | 121.8842 | 121.8521 | 121.8521 | -0.073242 | -0.059509
1493.2812 | 122.1359 | -121.8704 | -0.009155 | 0.16594 | 0.0095724 | 0.0010787 | 0.035 | -0.011256 | -0.010186 | 0.017047 | -0.11902 | -0.21973 | -0.073242 | -0.009155 | 0.073242 | 0.1236 | -0.22888 | -0.068665 | -0.050354 | -0.050354 | 121.7972 | -0.21057 | 121.7514 | 121.8613 | 0.082397 | 121.8201 | -0.041199 | -0.045777 | 121.6415 | 121.8018 | 121.9437 | 121.6507 | 121.7514 | 121.8201 | 121.994 | 121.8201 | 121.6507 | 121.7514 | 121.994 | 121.9437 | 121.8201 | -0.064087 | -0.041199
1495.0469 | 122.0398 | -121.9299 | 0.036621 | -0.1545 | 0.0099996 | 0.0021469 | 0.033932 | -0.014887 | -0.0080493 | 0.017688 | 0.22888 | -0.009155 | 0.21057 | 0.050354 | 0.13275 | 0.16022 | 0.10071 | 0.32501 | -0.027466 | -0.018311 | 122.1405 | -0.045776 | 122.1588 | 121.9803 | 0.09613 | 121.9116 | -0.064087 | 0.018311 | 122.0306 | 122.2549 | 122.0627 | 121.9208 | 122.1588 | 121.9025 | 122.0901 | 121.9116 | 121.9208 | 122.1588 | 122.0901 | 122.0627 | 121.9025 | 0.17395 | -0.054932
1496.7969 | 122.1863 | -121.8842 | 0 | 0.11253 | 0.0085042 | 0.0019333 | 0.031796 | -0.01681 | -0.0084765 | 0.017047 | -0.032043 | -0.16937 | -0.009155 | -0.009155 | 0.073242 | 0.12817 | -0.07782 | 0.059509 | -0.045776 | -0.022888 | 121.875 | -0.16937 | 121.8521 | 121.875 | 0.073242 | 121.8613 | -0.045776 | -0.022888 | 121.8063 | 121.9437 | 121.9574 | 121.7148 | 121.8521 | 121.8384 | 122.0123 | 121.8613 | 121.7148 | 121.8521 | 122.0123 | 121.9574 | 121.8384 | -0.009155 | -0.022888
1498.4844 | 122.1359 | -121.8933 | 0.004578 | 0.066757 | 0.012136 | 0.0049241 | 0.040554 | -0.012538 | -0.013604 | 0.017902 | -0.11444 | -0.18768 | -0.045776 | -0.09613 | -0.013733 | 0.018311 | -0.07782 | -0.16937 | -0.013733 | -0.059509 | 121.8475 | -0.19226 | 121.7789 | 121.7972 | -0.018311 | 121.8338 | -0.018311 | -0.068665 | 121.8155 | 121.7239 | 121.8796 | 121.7056 | 121.7789 | 121.8796 | 121.9116 | 121.8338 | 121.7056 | 121.7789 | 121.9116 | 121.8796 | 121.8796 | -0.050354 | -0.064087
1500.25 | 122.1909 | -121.8933 | 0.009155 | 0.11253 | 0.0095724 | 0.0047103 | 0.037777 | -0.013606 | -0.0095447 | 0.017047 | -0.14648 | -0.20142 | -0.10986 | -0.091553 | -0.004578 | 0.036621 | -0.1236 | -0.19684 | -0.018311 | -0.054932 | 121.7834 | -0.21057 | 121.7468 | 121.8018 | -0.013733 | 121.8384 | -0.027466 | -0.036621 | 121.7697 | 121.6965 | 121.8887 | 121.6919 | 121.7468 | 121.875 | 121.9299 | 121.8384 | 121.6919 | 121.7468 | 121.9299 | 121.8887 | 121.875 | -0.11902 | -0.064087
1502 | 122.113 | -121.9254 | 0.022888 | -0.2079 | 0.009786 | 0.0044967 | 0.033718 | -0.014247 | -0.0076221 | 0.016193 | 0.11902 | 0.022888 | 0.17853 | -0.064087 | 0.018311 | 0.036621 | 0.23804 | 0.16022 | -0.018311 | -0.068665 | 122.1039 | 0 | 122.0444 | 121.8613 | -0.004577 | 121.8567 | -0.041199 | -0.059509 | 122.1634 | 122.0856 | 121.9437 | 121.9482 | 122.0444 | 121.907 | 121.962 | 121.8567 | 121.9482 | 122.0444 | 121.962 | 121.9437 | 121.907 | 0.15564 | -0.091553
1503.7031 | 122.0581 | -121.9254 | 0.036621 | -0.070572 | 0.010641 | 0.0049241 | 0.038845 | -0.011256 | -0.012322 | 0.016406 | 0.022888 | -0.11444 | 0.027466 | 0 | 0.054932 | 0.10529 | -0.041199 | 0.004578 | -0.018311 | -0.045776 | 121.9528 | -0.15106 | 121.9482 | 121.9254 | 0.018311 | 121.8796 | -0.054932 | -0.004578 | 121.8842 | 121.9299 | 121.9803 | 121.8109 | 121.9482 | 121.907 | 122.0306 | 121.8796 | 121.8109 | 121.9482 | 122.0306 | 121.9803 | 121.907 | -0.009155 | -0.082397
1505.4688 | 122.1497 | -121.9025 | 0 | 0.11253 | 0.010854 | 0.0074875 | 0.038845 | -0.010829 | -0.0097583 | 0.017047 | -0.1236 | -0.1831 | -0.064087 | -0.10071 | -0.009155 | 0.027466 | -0.059509 | -0.17395 | -0.004578 | -0.050354 | 121.8384 | -0.1831 | 121.7789 | 121.8018 | -0.009155 | 121.8521 | -0.004578 | -0.059509 | 121.843 | 121.7285 | 121.8933 | 121.7194 | 121.7789 | 121.8979 | 121.9299 | 121.8521 | 121.7194 | 121.7789 | 121.9299 | 121.8933 | 121.8979 | -0.064087 | -0.050354
1507.1719 | 122.2137 | -121.8979 | -0.009155 | 0.1049 | 0.011709 | -0.00084389 | 0.036495 | -0.012965 | -0.0082629 | 0.01897 | -0.15106 | -0.21057 | -0.11444 | -0.07782 | 0 | 0.050354 | -0.11902 | -0.14648 | -0.004578 | -0.068665 | 121.7834 | -0.20142 | 121.7468 | 121.8201 | 0.009155 | 121.8292 | 0.004577 | -0.036621 | 121.7789 | 121.7514 | 121.8979 | 121.6873 | 121.7468 | 121.8933 | 121.9482 | 121.8292 | 121.6873 | 121.7468 | 121.9482 | 121.8979 | 121.8933 | -0.10529 | -0.05951
1508.9375 | 122.1588 | -121.9116 | 0.022888 | 0.15831 | 0.013204 | 0.0015061 | 0.035 | -0.012965 | -0.0059131 | 0.016406 | -0.050354 | -0.21973 | -0.032043 | 0.036621 | 0.1236 | 0.17395 | -0.25177 | 0.004578 | -0.068665 | -0.018311 | 121.8796 | -0.24261 | 121.8613 | 121.9482 | 0.10071 | 121.8933 | -0.091553 | -0.018311 | 121.6599 | 121.9162 | 122.0352 | 121.6919 | 121.8613 | 121.843 | 122.0856 | 121.8933 | 121.6919 | 121.8613 | 122.0856 | 122.0352 | 121.843 | -0.054931 | -0.041199
1510.625 | 122.2275 | -121.8933 | -0.009155 | 0.11253 | 0.011281 | 0.0015061 | 0.039272 | -0.014247 | -0.0078357 | 0.016406 | -0.16479 | -0.21515 | -0.09613 | -0.07782 | -0.013733 | 0.045776 | -0.10529 | -0.1831 | -0.013733 | -0.054932 | 121.7972 | -0.20599 | 121.7285 | 121.8155 | -0.004578 | 121.8384 | -0.004578 | -0.068665 | 121.788 | 121.7102 | 121.8796 | 121.6782 | 121.7285 | 121.8796 | 121.9391 | 121.8384 | 121.6782 | 121.7285 | 121.9391 | 121.8796 | 121.8796 | -0.086975 | -0.045777
1512.3906 | 122.1954 | -121.8933 | -0.004578 | 0.13542 | 0.011709 | 0.0012925 | 0.036068 | -0.012324 | -0.01104 | 0.017474 | -0.14191 | -0.20142 | -0.10529 | -0.07782 | 0.013733 | 0.064087 | -0.15106 | -0.14648 | -0.018311 | -0.045776 | 121.788 | -0.19684 | 121.7514 | 121.8155 | 0.018311 | 121.8475 | -0.013733 | -0.036621 | 121.7422 | 121.7468 | 121.907 | 121.6919 | 121.7514 | 121.875 | 121.9574 | 121.8475 | 121.6919 | 121.7514 | 121.9574 | 121.907 | 121.875 | -0.10071 | -0.041198
1514.0781 | 122.2321 | -121.9254 | -0.018311 | 0.0057222 | 0.0061544 | 0.00043791 | 0.030727 | -0.014674 | -0.0080493 | 0.017261 | -0.018311 | -0.13275 | 0.032043 | -0.027466 | 0.064087 | 0.13275 | -0.027466 | 0.086975 | -0.022888 | -0.032043 | 121.9574 | -0.11444 | 121.907 | 121.8979 | 0.082398 | 121.8933 | -0.004577 | -0.050354 | 121.8979 | 122.0123 | 121.9894 | 121.7926 | 121.907 | 121.9025 | 122.0581 | 121.8933 | 121.7926 | 121.907 | 122.0581 | 121.9894 | 121.9025 | 0.050354 | -0.013732
1515.8281 | 122.1176 | -121.9437 | 0.027466 | -0.040054 | 0.012136 | 0.0040695 | 0.04269 | -0.013819 | -0.011254 | 0.017474 | -0.009155 | -0.16479 | 0.004578 | -0.027466 | 0.036621 | 0.068665 | -0.054932 | -0.059509 | -0.018311 | -0.050354 | 121.9482 | -0.19226 | 121.9345 | 121.9162 | 0.009155 | 121.8933 | -0.045777 | -0.013733 | 121.8887 | 121.8842 | 121.9803 | 121.7789 | 121.9345 | 121.9254 | 122.0123 | 121.8933 | 121.7789 | 121.9345 | 122.0123 | 121.9803 | 121.9254 | -0.022888 | -0.07782
1517.5156 | 122.0856 | -121.9437 | 0.032043 | -0.14687 | 0.011495 | 0.0036423 | 0.033291 | -0.015742 | -0.010826 | 0.01662 | 0.20142 | 0.004578 | 0.21515 | 0.027466 | 0.1236 | 0.15564 | 0.10529 | 0.30212 | -0.036621 | -0.009155 | 122.1588 | -0.027465 | 122.1451 | 121.9711 | 0.091553 | 121.9345 | -0.068664 | -0.013733 | 122.049 | 122.2458 | 122.0673 | 121.9482 | 122.1451 | 121.907 | 122.0993 | 121.9345 | 121.9482 | 122.1451 | 122.0993 | 122.0673 | 121.907 | 0.18311 | -0.041198
1519.2812 | 122.1039 | -121.9757 | 0.045776 | -0.085831 | 0.012136 | -0.0031937 | 0.038204 | -0.011897 | -0.011467 | 0.017688 | 0.027466 | -0.12817 | 0.027466 | 0.004578 | 0.050354 | 0.091553 | -0.027466 | 0.018311 | -0.018311 | -0.041199 | 122.0032 | -0.17395 | 122.0032 | 121.9803 | 0.004578 | 121.9345 | -0.064087 | 0 | 121.9482 | 121.994 | 122.0261 | 121.8475 | 122.0032 | 121.9574 | 122.0673 | 121.9345 | 121.8475 | 122.0032 | 122.0673 | 122.0261 | 121.9574 | -0.01831 | -0.086975
1521.0312 | 122.0947 | -121.9849 | 0.036621 | -0.19264 | 0.010427 | -0.0031937 | 0.032009 | -0.014247 | -0.0089037 | 0.016193 | 0.21057 | -0.013733 | 0.19226 | 0.064087 | 0.1236 | 0.19226 | 0.10529 | 0.33875 | -0.054932 | -0.018311 | 122.1771 | -0.050354 | 122.1954 | 122.049 | 0.086975 | 121.9666 | -0.091553 | 0.01831 | 122.0901 | 122.3236 | 122.1085 | 121.9711 | 122.1954 | 121.9299 | 122.1771 | 121.9666 | 121.9711 | 122.1954 | 122.1771 | 122.1085 | 121.9299 | 0.15564 | -0.054932
1522.7188 | 122.2366 | -121.9254 | -0.004578 | 0.074387 | 0.011068 | -0.0019119 | 0.034786 | -0.013392 | -0.010186 | 0.014911 | -0.009155 | -0.17853 | -0.004578 | -0.013733 | 0.073242 | 0.12817 | -0.050354 | 0.07782 | -0.045776 | -0.027466 | 121.9208 | -0.17395 | 121.9162 | 121.9116 | 0.07782 | 121.8979 | -0.041198 | -0.004577 | 121.875 | 122.0032 | 121.9986 | 121.7468 | 121.9162 | 121.8796 | 122.0535 | 121.8979 | 121.7468 | 121.9162 | 122.0535 | 121.9986 | 121.8796 | 0 | -0.022888
1524.4688 | 122.2366 | -121.9162 | 0.018311 | 0.02861 | 0.011495 | 0.0040695 | 0.033932 | -0.014887 | -0.0093311 | 0.016193 | 0.054932 | -0.091553 | 0.091553 | -0.022888 | 0.068665 | 0.10986 | 0.027466 | 0.13733 | -0.027466 | -0.032043 | 122.0078 | -0.10986 | 121.9711 | 121.8933 | 0.050354 | 121.8842 | -0.045777 | -0.036621 | 121.9437 | 122.0535 | 121.9849 | 121.8246 | 121.9711 | 121.8887 | 122.0261 | 121.8842 | 121.8246 | 121.9711 | 122.0261 | 121.9849 | 121.8887 | 0.073242 | -0.050354
1526.2188 | 122.1359 | -121.9666 | 0.036621 | -0.1545 | 0.011922 | 0.00022431 | 0.040127 | -0.014674 | -0.0093311 | 0.015552 | 0.082397 | -0.013733 | 0.1236 | -0.050354 | 0.018311 | 0.050354 | 0.1831 | 0.10529 | -0.004578 | -0.068665 | 122.0901 | -0.050354 | 122.049 | 121.9162 | -0.01831 | 121.8979 | -0.041199 | -0.041199 | 122.1497 | 122.0718 | 121.9849 | 121.9528 | 122.049 | 121.962 | 122.0169 | 121.8979 | 121.9528 | 122.049 | 122.0169 | 121.9849 | 121.962 | 0.086975 | -0.10529
1527.9062 | 122.1954 | -121.9757 | 0.013733 | -0.070572 | 0.0085042 | 0.00022431 | 0.031155 | -0.015956 | -0.0086901 | 0.015552 | 0.14648 | -0.050354 | 0.15564 | 0.032043 | 0.10071 | 0.16022 | 0.050354 | 0.28839 | -0.032043 | -0.009155 | 122.1313 | -0.064087 | 122.1222 | 122.0078 | 0.086975 | 121.9666 | -0.045776 | -0.009156 | 122.0261 | 122.2641 | 122.0764 | 121.9254 | 122.1222 | 121.9437 | 122.1359 | 121.9666 | 121.9254 | 122.1222 | 122.1359 | 122.0764 | 121.9437 | 0.14191 | -0.022888
1529.6562 | 122.1954 | -121.9666 | 0.004578 | 0.15831 | 0.010641 | 0.0017197 | 0.037563 | -0.011897 | -0.0091173 | 0.015979 | -0.018311 | -0.25177 | -0.022888 | 0.050354 | 0.10986 | 0.17853 | -0.26093 | 0.013733 | -0.059509 | 0 | 121.9437 | -0.25635 | 121.9482 | 122.0169 | 0.10529 | 121.9666 | -0.064087 | 0.004577 | 121.7056 | 121.9803 | 122.0764 | 121.7148 | 121.9482 | 121.907 | 122.1451 | 121.9666 | 121.7148 | 121.9482 | 122.1451 | 122.0764 | 121.907 | -0.027466 | -0.004578
1531.4062 | 122.1634 | -121.9757 | 0.032043 | -0.21553 | 0.011495 | 0.00086511 | 0.035854 | -0.013392 | -0.010186 | 0.01662 | 0.15564 | 0.032043 | 0.19226 | -0.027466 | 0.041199 | 0.064087 | 0.20599 | 0.23804 | -0.022888 | -0.054932 | 122.168 | 0 | 122.1313 | 121.9482 | 0.009156 | 121.9208 | -0.054931 | -0.036621 | 122.1817 | 122.2137 | 122.0169 | 122.0078 | 122.1313 | 121.9528 | 122.0398 | 121.9208 | 122.0078 | 122.1313 | 122.0398 | 122.0169 | 121.9528 | 0.16022 | -0.086975
1533.0938 | 122.1313 | -121.9803 | 0.045776 | -0.16975 | 0.0093588 | 0.0040695 | 0.034359 | -0.015956 | -0.0084765 | 0.014697 | 0.21515 | -0.004578 | 0.19226 | 0.068665 | 0.11902 | 0.1831 | 0.091553 | 0.35248 | -0.045776 | -0.022888 | 122.1725 | -0.050354 | 122.1954 | 122.049 | 0.073243 | 121.9574 | -0.091552 | 0.022888 | 122.0718 | 122.3328 | 122.0993 | 121.9757 | 122.1954 | 121.9345 | 122.1634 | 121.9574 | 121.9757 | 122.1954 | 122.1634 | 122.0993 | 121.9345 | 0.14648 | -0.068664
1534.8438 | 122.2458 | -121.9437 | -0.018311 | 0.12779 | 0.010641 | 0.0051377 | 0.038418 | -0.010615 | -0.0082629 | 0.017261 | -0.13275 | -0.22888 | -0.086975 | -0.064087 | -0.022888 | 0.045776 | -0.11902 | -0.18768 | -0.013733 | -0.045776 | 121.8567 | -0.21057 | 121.8109 | 121.8796 | -0.004577 | 121.8979 | 0.004578 | -0.045776 | 121.8246 | 121.756 | 121.9208 | 121.7148 | 121.8109 | 121.9299 | 121.9894 | 121.8979 | 121.7148 | 121.8109 | 121.9894 | 121.9208 | 121.9299 | -0.068664 | -0.027465
1536.5938 | 122.2275 | -121.9528 | 0.009155 | 0.097275 | 0.0095724 | 0.0023605 | 0.035427 | -0.012324 | -0.0074085 | 0.017474 | 0.004578 | -0.19684 | -0.004578 | 0.022888 | 0.09613 | 0.16022 | -0.16022 | 0.045776 | -0.032043 | -0.041199 | 121.9482 | -0.20599 | 121.9574 | 121.9757 | 0.086975 | 121.9116 | -0.041198 | 0.009156 | 121.7926 | 121.9986 | 122.049 | 121.756 | 121.9574 | 121.9208 | 122.113 | 121.9116 | 121.756 | 121.9574 | 122.113 | 122.049 | 121.9208 | -0.013733 | -0.050354
1538.3594 | 122.2092 | -121.9666 | 0.009155 | 0.17357 | 0.011922 | 0.0025741 | 0.036495 | -0.016383 | -0.0065539 | 0.017688 | -0.013733 | -0.22888 | -0.036621 | 0.045776 | 0.10986 | 0.17395 | -0.24719 | 0.027466 | -0.059509 | -0.009155 | 121.9299 | -0.23804 | 121.9528 | 122.0123 | 0.10071 | 121.9574 | -0.068664 | 0.022888 | 121.7194 | 121.994 | 122.0764 | 121.7377 | 121.9528 | 121.907 | 122.1405 | 121.9574 | 121.7377 | 121.9528 | 122.1405 | 122.0764 | 121.907 | -0.045776 | -0.01831
1540.0625 | 122.1451 | -122.0215 | 0.013733 | -0.070572 | 0.011281 | 0.0025741 | 0.042263 | -0.012965 | -0.010399 | 0.015979 | 0.018311 | -0.16022 | 0.009155 | 0 | 0.036621 | 0.068665 | -0.050354 | -0.022888 | -0.013733 | -0.036621 | 122.0306 | -0.17395 | 122.0398 | 122.0215 | 0.022888 | 121.9849 | -0.027466 | 0.009156 | 121.9711 | 121.9986 | 122.0581 | 121.8613 | 122.0398 | 122.0078 | 122.0901 | 121.9849 | 121.8613 | 122.0398 | 122.0901 | 122.0581 | 122.0078 | -0.004578 | -0.050354
1541.7969 | 122.2687 | -121.9574 | 0 | 0.15068 | 0.010427 | 0.0057785 | 0.037136 | -0.011897 | -0.0091173 | 0.018115 | -0.13733 | -0.21515 | -0.086975 | -0.086975 | -0.009155 | 0.027466 | -0.11902 | -0.19226 | -0.013733 | -0.045776 | 121.8704 | -0.21515 | 121.8201 | 121.8704 | -0.009155 | 121.9116 | -0.013733 | -0.050354 | 121.8384 | 121.7651 | 121.9482 | 121.7422 | 121.8201 | 121.9437 | 121.9849 | 121.9116 | 121.7422 | 121.8201 | 121.9849 | 121.9482 | 121.9437 | -0.086975 | -0.045776
1543.5625 | 122.1542 | -122.0078 | 0.041199 | -0.1545 | 0.0091452 | 0.0025741 | 0.032223 | -0.01446 | -0.0069811 | 0.016834 | 0.21057 | 0.018311 | 0.19684 | 0.036621 | 0.11902 | 0.14648 | 0.13275 | 0.30212 | -0.041199 | -0.045776 | 122.2046 | -0.022888 | 122.2183 | 122.0444 | 0.07782 | 121.962 | -0.082398 | 0.013733 | 122.1405 | 122.3099 | 122.1268 | 122.0261 | 122.2183 | 121.9666 | 122.1542 | 121.962 | 122.0261 | 122.2183 | 122.1542 | 122.1268 | 121.9666 | 0.15564 | -0.086975
1545.25 | 122.1542 | -122.0123 | 0.013733 | -0.12398 | 0.011709 | 0.00065151 | 0.038418 | -0.01446 | -0.0086901 | 0.017902 | 0.082397 | -0.054932 | 0.11444 | -0.027466 | 0.041199 | 0.068665 | 0.068665 | 0.07782 | -0.009155 | -0.036621 | 122.1268 | -0.068665 | 122.0947 | 121.9849 | 0.027466 | 121.9757 | -0.022888 | -0.032044 | 122.081 | 122.0901 | 122.0535 | 121.9574 | 122.0947 | 122.0032 | 122.081 | 121.9757 | 121.9574 | 122.0947 | 122.081 | 122.0535 | 122.0032 | 0.10071 | -0.050354
1546.9844 | 122.2778 | -121.9757 | -0.004578 | 0.097275 | 0.0091452 | 0.0023605 | 0.032223 | -0.014674 | -0.0078357 | 0.015979 | -0.004578 | -0.16022 | 0.027466 | -0.018311 | 0.07782 | 0.13275 | -0.064087 | 0.082397 | -0.050354 | -0.027466 | 122.0032 | -0.15564 | 121.9711 | 121.9574 | 0.082398 | 121.9482 | -0.045776 | -0.032044 | 121.9116 | 122.0581 | 122.0535 | 121.8155 | 121.9711 | 121.9254 | 122.1085 | 121.9482 | 121.8155 | 121.9711 | 122.1085 | 122.0535 | 121.9254 | 0.032044 | -0.022888
1548.6719 | 122.2366 | -121.9757 | 0.004578 | 0.16594 | 0.0082906 | 0.00022431 | 0.034573 | -0.012538 | -0.0099719 | 0.017688 | -0.018311 | -0.22888 | -0.032043 | 0.041199 | 0.09613 | 0.17395 | -0.2243 | 0.027466 | -0.068665 | -0.018311 | 121.9437 | -0.23346 | 121.9574 | 122.0169 | 0.091552 | 121.9574 | -0.073243 | 0.013732 | 121.7514 | 122.0032 | 122.0718 | 121.7468 | 121.9574 | 121.907 | 122.1497 | 121.9574 | 121.7468 | 121.9574 | 122.1497 | 122.0718 | 121.907 | -0.036621 | -0.022889
1550.3594 | 122.1588 | -122.0444 | 0.009155 | -0.12398 | 0.0095724 | -0.00084389 | 0.034786 | -0.014033 | -0.0067675 | 0.015125 | 0.21515 | -0.013733 | 0.17853 | 0.054932 | 0.13275 | 0.19226 | 0.054932 | 0.3479 | -0.041199 | -0.009155 | 122.2229 | -0.022888 | 122.2595 | 122.0993 | 0.1236 | 122.0352 | -0.050354 | 0.036621 | 122.0993 | 122.3923 | 122.1771 | 122.0306 | 122.2595 | 122.0032 | 122.2366 | 122.0352 | 122.0306 | 122.2595 | 122.2366 | 122.1771 | 122.0032 | 0.16937 | -0.01831
1552.1094 | 122.2824 | -121.9711 | -0.004578 | 0.12779 | 0.008718 | 0.0032151 | 0.040127 | -0.01211 | -0.011681 | 0.016406 | -0.13275 | -0.21973 | -0.07782 | -0.073242 | -0.013733 | 0.022888 | -0.10071 | -0.17853 | 0.013733 | -0.036621 | 121.8933 | -0.21515 | 121.8384 | 121.8979 | -0.009155 | 121.9345 | 0.018311 | -0.054931 | 121.8704 | 121.7926 | 121.9574 | 121.7514 | 121.8384 | 121.9849 | 121.994 | 121.9345 | 121.7514 | 121.8384 | 121.994 | 121.9574 | 121.9849 | -0.073242 | -0.032043
1553.7969 | 122.2687 | -121.9803 | 0.009155 | 0.074387 | 0.010641 | 0.00086511 | 0.037563 | -0.011897 | -0.0099719 | 0.016193 | -0.12817 | -0.19226 | -0.068665 | -0.091553 | -0.022888 | 0.018311 | -0.041199 | -0.16479 | -0.009155 | -0.059509 | 121.9116 | -0.20142 | 121.8521 | 121.8887 | -0.032043 | 121.9208 | -0.01831 | -0.059509 | 121.9391 | 121.8155 | 121.9574 | 121.788 | 121.8521 | 121.9711 | 121.9986 | 121.9208 | 121.788 | 121.8521 | 121.9986 | 121.9574 | 121.9711 | -0.07782 | -0.068664
1555.5469 | 122.1725 | -122.0215 | 0.018311 | -0.040054 | 0.012136 | 0.0015061 | 0.037777 | -0.014247 | -0.0099719 | 0.017047 | -0.018311 | -0.16479 | 0.018311 | -0.036621 | 0.032043 | 0.073242 | -0.059509 | -0.050354 | 0 | -0.059509 | 122.0398 | -0.18311 | 122.0032 | 121.9849 | 0.013732 | 121.962 | -0.018311 | -0.036622 | 121.962 | 121.9711 | 122.0535 | 121.8567 | 122.0032 | 122.0215 | 122.0947 | 121.962 | 121.8567 | 122.0032 | 122.0947 | 122.0535 | 122.0215 | 0 | -0.07782
1557.2344 | 122.1634 | -122.0169 | 0.041199 | -0.18501 | 0.010213 | 0.0015061 | 0.03265 | -0.013819 | -0.0086901 | 0.015338 | 0.21057 | 0.004578 | 0.20599 | 0.045776 | 0.13275 | 0.16937 | 0.10529 | 0.32959 | -0.068665 | -0.027466 | 122.2229 | -0.036621 | 122.2275 | 122.0627 | 0.091552 | 121.9894 | -0.10986 | 0.004577 | 122.1222 | 122.3465 | 122.1497 | 122.0215 | 122.2275 | 121.9482 | 122.1863 | 121.9894 | 122.0215 | 122.2275 | 122.1863 | 122.1497 | 121.9482 | 0.1648 | -0.068665
1559 | 122.1634 | -122.0398 | 0.027466 | -0.17738 | 0.009786 | 0.00022431 | 0.031582 | -0.013819 | -0.0082629 | 0.017261 | 0.19226 | 0.004578 | 0.20142 | 0.036621 | 0.1236 | 0.17395 | 0.13275 | 0.35248 | -0.041199 | -0.032043 | 122.2412 | -0.022888 | 122.2321 | 122.0764 | 0.09613 | 122.0078 | -0.068665 | -0.009155 | 122.1725 | 122.3923 | 122.1634 | 122.0444 | 122.2321 | 121.9986 | 122.2137 | 122.0078 | 122.0444 | 122.2321 | 122.2137 | 122.1634 | 121.9986 | 0.17395 | -0.059509
1560.7656 | 122.287 | -121.9986 | 0 | 0.1049 | 0.01235 | 0.0010787 | 0.033718 | -0.013606 | -0.011254 | 0.015552 | -0.004578 | -0.21515 | -0.027466 | 0.013733 | 0.091553 | 0.14648 | -0.17395 | 0.045776 | -0.041199 | -0.045776 | 121.9711 | -0.21515 | 121.994 | 122.0123 | 0.091553 | 121.9528 | -0.041199 | 0.022888 | 121.8246 | 122.0444 | 122.0901 | 121.7834 | 121.994 | 121.9574 | 122.1451 | 121.9528 | 121.7834 | 121.994 | 122.1451 | 122.0901 | 121.9574 | -0.027466 | -0.045776
1562.4688 | 122.2229 | -122.0398 | 0.036621 | -0.16975 | 0.0091452 | 0.0038559 | 0.037563 | -0.01681 | -0.0084765 | 0.017261 | 0.10529 | 0.027466 | 0.13733 | -0.064087 | 0.022888 | 0.032043 | 0.26093 | 0.17853 | -0.004578 | -0.073242 | 122.1771 | -0.009155 | 122.1451 | 121.9757 | -0.013733 | 121.9666 | -0.041199 | -0.032043 | 122.3007 | 122.2183 | 122.0627 | 122.0673 | 122.1451 | 122.0352 | 122.0718 | 121.9666 | 122.0673 | 122.1451 | 122.0718 | 122.0627 | 122.0352 | 0.10071 | -0.10986
1564.2188 | 122.2641 | -122.0169 | -0.013733 | 0.13542 | 0.0085042 | 0.0023605 | 0.034786 | -0.012324 | -0.010186 | 0.017261 | -0.018311 | -0.23346 | -0.045776 | 0.036621 | 0.11902 | 0.15106 | -0.21057 | 0.059509 | -0.054932 | -0.009155 | 121.9711 | -0.21973 | 121.9986 | 122.0535 | 0.13275 | 122.0078 | -0.041199 | 0.027465 | 121.8063 | 122.0764 | 122.1359 | 121.7834 | 121.9986 | 121.962 | 122.168 | 122.0078 | 121.7834 | 121.9986 | 122.168 | 122.1359 | 121.962 | -0.032043 | 0.004578
1565.9062 | 122.1725 | -122.0673 | 0.036621 | -0.13924 | 0.011922 | 0.0012925 | 0.036709 | -0.012324 | -0.010186 | 0.016406 | 0.22888 | 0 | 0.19684 | 0.050354 | 0.10529 | 0.14648 | 0.13733 | 0.33417 | -0.045776 | -0.027466 | 122.2641 | -0.036621 | 122.2961 | 122.1176 | 0.068665 | 122.0398 | -0.082397 | 0.032044 | 122.2046 | 122.4014 | 122.1725 | 122.0673 | 122.2961 | 122.0215 | 122.2137 | 122.0398 | 122.0673 | 122.2961 | 122.2137 | 122.1725 | 122.0215 | 0.16022 | -0.064087
1567.6562 | 122.2504 | -121.9894 | 0.027466 | 0.051498 | 0.010854 | -0.0014847 | 0.039913 | -0.013819 | -0.0089037 | 0.017047 | -0.091553 | -0.19684 | -0.054932 | -0.064087 | -0.013733 | 0.032043 | -0.054932 | -0.15106 | 0 | -0.054932 | 121.9345 | -0.2243 | 121.8979 | 121.9254 | -0.041199 | 121.9345 | -0.027466 | -0.036621 | 121.9345 | 121.8384 | 121.9757 | 121.7926 | 121.8979 | 121.9894 | 122.0215 | 121.9345 | 121.7926 | 121.8979 | 122.0215 | 121.9757 | 121.9894 | -0.082398 | -0.082398
1569.4219 | 122.2595 | -122.0352 | -0.004578 | 0.051498 | 0.011068 | 0.0049241 | 0.039913 | -0.012751 | -0.010399 | 0.017047 | -0.10529 | -0.17853 | -0.045776 | -0.073242 | -0.009155 | 0.018311 | -0.064087 | -0.15564 | -0.004578 | -0.045776 | 121.9894 | -0.17395 | 121.9299 | 121.962 | -0.004577 | 121.9894 | 0 | -0.05951 | 121.9711 | 121.8796 | 122.0261 | 121.8567 | 121.9299 | 122.0306 | 122.0535 | 121.9894 | 121.8567 | 121.9299 | 122.0535 | 122.0261 | 122.0306 | -0.041198 | -0.041198
1571.1719 | 122.3053 | -122.0261 | -0.004578 | -0.017166 | 0.010854 | 0.0040695 | 0.030727 | -0.012751 | -0.0069811 | 0.018543 | 0.07782 | -0.073242 | 0.10986 | -0.009155 | 0.09613 | 0.11902 | 0.041199 | 0.19684 | -0.050354 | -0.041199 | 122.1359 | -0.068664 | 122.1039 | 122.0169 | 0.10071 | 121.9849 | -0.045776 | -0.032043 | 122.0673 | 122.2229 | 122.1222 | 121.9528 | 122.1039 | 121.9757 | 122.1451 | 121.9849 | 121.9528 | 122.1039 | 122.1451 | 122.1222 | 121.9757 | 0.11444 | -0.036621
1572.9219 | 122.319 | -122.0306 | 0.013733 | -0.0019073 | 0.011709 | 0.0012925 | 0.031582 | -0.013392 | -0.010613 | 0.017474 | 0.064087 | -0.086975 | 0.091553 | -0.018311 | 0.068665 | 0.12817 | 0.032043 | 0.15564 | -0.027466 | -0.045776 | 122.1222 | -0.10071 | 122.0947 | 122.0123 | 0.054932 | 121.9849 | -0.041199 | -0.027466 | 122.0627 | 122.1863 | 122.0993 | 121.9437 | 122.0947 | 122.0032 | 122.1588 | 121.9849 | 121.9437 | 122.0947 | 122.1588 | 122.0993 | 122.0032 | 0.07782 | -0.059509
1574.6719 | 122.2275 | -122.0627 | 0.027466 | -0.12398 | 0.010427 | 0.0021469 | 0.036068 | -0.01211 | -0.0091173 | 0.016834 | 0.1831 | -0.041199 | 0.16479 | 0.068665 | 0.15564 | 0.17853 | 0.064087 | 0.32501 | -0.054932 | -0.004578 | 122.2275 | -0.068665 | 122.2458 | 122.1313 | 0.12817 | 122.0581 | -0.082398 | 0.01831 | 122.1268 | 122.3877 | 122.2183 | 122.0215 | 122.2458 | 122.0078 | 122.2412 | 122.0581 | 122.0215 | 122.2458 | 122.2412 | 122.2183 | 122.0078 | 0.13733 | -0.032044
1576.3594 | 122.319 | -122.0123 | 0 | 0.013352 | 0.011281 | 0.0036423 | 0.033718 | -0.015956 | -0.0082629 | 0.016193 | 0.054932 | -0.10529 | 0.054932 | -0.032043 | 0.064087 | 0.11444 | 0.032043 | 0.14191 | -0.032043 | -0.054932 | 122.0673 | -0.10529 | 122.0673 | 121.9803 | 0.064087 | 121.9574 | -0.032043 | 0 | 122.0444 | 122.1542 | 122.0764 | 121.907 | 122.0673 | 121.9803 | 122.1268 | 121.9574 | 121.907 | 122.0673 | 122.1268 | 122.0764 | 121.9803 | 0.054932 | -0.054932
1578.0938 | 122.1817 | -122.0673 | 0.032043 | -0.055313 | 0.01299 | 0.0015061 | 0.043545 | -0.012324 | -0.011681 | 0.017047 | 0.054932 | -0.10986 | 0.032043 | 0.004578 | 0.050354 | 0.086975 | -0.009155 | 0.041199 | -0.022888 | -0.027466 | 122.0993 | -0.14191 | 122.1222 | 122.0718 | 0.018311 | 122.0398 | -0.054931 | 0.022889 | 122.0581 | 122.1085 | 122.1176 | 121.9574 | 122.1222 | 122.0444 | 122.1542 | 122.0398 | 121.9574 | 122.1222 | 122.1542 | 122.1176 | 122.0444 | 0 | -0.059509
1579.8594 | 122.3236 | -122.0215 | 0.004578 | 0.11253 | 0.011922 | 0.0044967 | 0.038418 | -0.012324 | -0.010613 | 0.016834 | -0.12817 | -0.20142 | -0.073242 | -0.082397 | -0.004578 | 0.027466 | -0.10071 | -0.17853 | -0.009155 | -0.045776 | 121.9482 | -0.20599 | 121.8933 | 121.9391 | -0.009156 | 121.9757 | -0.013733 | -0.054932 | 121.9208 | 121.843 | 122.0169 | 121.8201 | 121.8933 | 122.0123 | 122.049 | 121.9757 | 121.8201 | 121.8933 | 122.049 | 122.0169 | 122.0123 | -0.07782 | -0.050354
1581.5469 | 122.3007 | -122.0444 | 0.009155 | 0.082016 | 0.012563 | 0.0010787 | 0.038418 | -0.012751 | -0.010399 | 0.018115 | -0.11444 | -0.19684 | -0.041199 | -0.068665 | -0.013733 | 0.022888 | -0.059509 | -0.15106 | -0.004578 | -0.054932 | 122.0032 | -0.20599 | 121.9299 | 121.9757 | -0.022888 | 121.9894 | -0.013733 | -0.073242 | 121.9849 | 121.8933 | 122.0306 | 121.8475 | 121.9299 | 122.0398 | 122.0673 | 121.9894 | 121.8475 | 121.9299 | 122.0673 | 122.0306 | 122.0398 | -0.050354 | -0.064087
1583.2969 | 122.3053 | -122.0352 | -0.004578 | 0.066757 | 0.008718 | 0.00043791 | 0.038845 | -0.014247 | -0.0086901 | 0.018115 | -0.13275 | -0.19684 | -0.07782 | -0.09613 | -0.018311 | 0.009155 | -0.059509 | -0.16479 | -0.004578 | -0.064087 | 121.9574 | -0.19226 | 121.9025 | 121.9391 | -0.013733 | 121.9711 | 0 | -0.054931 | 121.9757 | 121.8704 | 122.0169 | 121.8384 | 121.9025 | 122.0306 | 122.0444 | 121.9711 | 121.8384 | 121.9025 | 122.0444 | 122.0169 | 122.0306 | -0.073242 | -0.059509
1585 | 122.2137 | -122.0993 | 0.027466 | -0.13161 | 0.011495 | -0.00041649 | 0.030727 | -0.015528 | -0.0054859 | 0.017474 | 0.19226 | -0.018311 | 0.17853 | 0.059509 | 0.14648 | 0.17395 | 0.09613 | 0.35248 | -0.050354 | -0.041199 | 122.2778 | -0.045777 | 122.2916 | 122.1588 | 0.11902 | 122.0581 | -0.07782 | 0.013733 | 122.1954 | 122.4518 | 122.2458 | 122.081 | 122.2916 | 122.049 | 122.2733 | 122.0581 | 122.081 | 122.2916 | 122.2733 | 122.2458 | 122.049 | 0.15106 | -0.068665
1586.7656 | 122.3007 | -122.049 | 0.004578 | 0.20409 | 0.012136 | 0.00043791 | 0.038845 | -0.013178 | -0.0074085 | 0.017688 | -0.1236 | -0.23804 | -0.068665 | -0.018311 | 0.064087 | 0.1236 | -0.23804 | -0.086975 | -0.050354 | -0.027466 | 121.9803 | -0.24261 | 121.9254 | 122.0306 | 0.059509 | 122.0215 | -0.054932 | -0.054931 | 121.8109 | 121.962 | 122.113 | 121.8109 | 121.9254 | 121.9986 | 122.1725 | 122.0215 | 121.8109 | 121.9254 | 122.1725 | 122.113 | 121.9986 | -0.073243 | -0.032044
1588.5156 | 122.2 | -122.0947 | 0.018311 | -0.085831 | 0.0093588 | 0.0030013 | 0.037991 | -0.013178 | -0.0089037 | 0.014697 | 0.050354 | -0.09613 | 0.054932 | -0.013733 | 0.045776 | 0.10071 | 0.027466 | 0.059509 | 0 | -0.032043 | 122.1497 | -0.11444 | 122.1451 | 122.081 | 0.027465 | 122.0627 | -0.018311 | -0.004578 | 122.1222 | 122.1542 | 122.1405 | 121.9986 | 122.1451 | 122.0947 | 122.1954 | 122.0627 | 121.9986 | 122.1451 | 122.1954 | 122.1405 | 122.0947 | 0.036621 | -0.050354
1590.2656 | 122.2549 | -122.0581 | 0.018311 | -0.14687 | 0.011709 | 0.0049241 | 0.035854 | -0.012538 | -0.010186 | 0.017261 | 0.086975 | 0 | 0.15106 | -0.059509 | 0.027466 | 0.045776 | 0.20599 | 0.13275 | -0.032043 | -0.059509 | 122.2092 | -0.018311 | 122.1451 | 121.9986 | 0.009155 | 121.9986 | -0.050354 | -0.064087 | 122.2641 | 122.1909 | 122.0856 | 122.0581 | 122.1451 | 122.0261 | 122.1039 | 121.9986 | 122.0581 | 122.1451 | 122.1039 | 122.0856 | 122.0261 | 0.13275 | -0.07782
1592.0156 | 122.3099 | -122.0581 | -0.009155 | 0.16594 | 0.011068 | 0.0051377 | 0.035641 | -0.012538 | -0.0080493 | 0.013629 | -0.10071 | -0.23346 | -0.07782 | -0.018311 | 0.082397 | 0.14191 | -0.21515 | -0.054932 | -0.045776 | -0.041199 | 121.9803 | -0.2243 | 121.9574 | 122.0398 | 0.091552 | 122.0169 | -0.036621 | -0.022888 | 121.843 | 122.0032 | 122.1405 | 121.8246 | 121.9574 | 122.0123 | 122.2 | 122.0169 | 121.8246 | 121.9574 | 122.2 | 122.1405 | 122.0123 | -0.068665 | -0.032044
1593.7188 | 122.2916 | -122.0581 | 0 | 0.17357 | 0.0099996 | 0.0049241 | 0.032864 | -0.013606 | -0.0093311 | 0.01662 | -0.022888 | -0.22888 | -0.027466 | 0.036621 | 0.13275 | 0.16937 | -0.23804 | 0.013733 | -0.054932 | -0.032043 | 122.0306 | -0.22888 | 122.0352 | 122.0947 | 0.13275 | 122.0261 | -0.054932 | 0.004578 | 121.8201 | 122.0718 | 122.1909 | 121.8292 | 122.0352 | 122.0032 | 122.2275 | 122.0261 | 121.8292 | 122.0352 | 122.2275 | 122.1909 | 122.0032 | -0.027466 | -0.032043
1595.4844 | 122.3648 | -122.0581 | 0 | 0.051498 | 0.011281 | 0.0021469 | 0.03265 | -0.013178 | -0.0065539 | 0.015765 | -0.009155 | -0.15106 | 0.036621 | -0.036621 | 0.068665 | 0.11902 | -0.032043 | 0.091553 | -0.041199 | -0.032043 | 122.0947 | -0.15106 | 122.0489 | 122.0215 | 0.068665 | 122.0261 | -0.041199 | -0.045776 | 122.0261 | 122.1497 | 122.1268 | 121.907 | 122.0489 | 122.0169 | 122.1771 | 122.0261 | 121.907 | 122.0489 | 122.1771 | 122.1268 | 122.0169 | 0.036621 | -0.032043
1597.2344 | 122.2275 | -122.081 | 0.032043 | -0.047684 | 0.0099996 | 0.0038559 | 0.040554 | -0.013178 | -0.0093311 | 0.016406 | 0.018311 | -0.13275 | 0.045776 | 0.004578 | 0.059509 | 0.091553 | -0.027466 | 0.022888 | -0.032043 | -0.036621 | 122.1268 | -0.16479 | 122.0993 | 122.0856 | 0.027466 | 122.0444 | -0.064086 | -0.027465 | 122.0535 | 122.1039 | 122.1405 | 121.9482 | 122.0993 | 122.049 | 122.1725 | 122.0444 | 121.9482 | 122.0993 | 122.1725 | 122.1405 | 122.049 | 0.013733 | -0.068664
1599 | 122.3465 | -122.0398 | -0.013733 | 0.13542 | 0.011709 | -0.0027665 | 0.0397 | -0.014033 | -0.0071947 | 0.017902 | -0.16022 | -0.20142 | -0.07782 | -0.09613 | -0.004578 | 0.045776 | -0.1236 | -0.19684 | -0.004578 | -0.054932 | 121.962 | -0.18768 | 121.8796 | 121.9437 | 0.009155 | 121.9849 | 0.009155 | -0.082397 | 121.9162 | 121.843 | 122.0352 | 121.8384 | 121.8796 | 122.0352 | 122.0856 | 121.9849 | 121.8384 | 121.8796 | 122.0856 | 122.0352 | 122.0352 | -0.064087 | -0.041199
1600.6875 | 122.3373 | -122.0535 | -0.009155 | 0.12016 | 0.011281 | 0.0017197 | 0.036068 | -0.012965 | -0.0097583 | 0.017261 | -0.16022 | -0.21973 | -0.10986 | -0.082397 | -0.004578 | 0.041199 | -0.12817 | -0.17853 | -0.004578 | -0.054932 | 121.9437 | -0.21057 | 121.8933 | 121.9711 | 0.004577 | 121.9986 | 0.004577 | -0.050354 | 121.9254 | 121.875 | 122.049 | 121.8338 | 121.8933 | 122.049 | 122.0947 | 121.9986 | 121.8338 | 121.8933 | 122.0947 | 122.049 | 122.049 | -0.10071 | -0.045777
1602.4531 | 122.3511 | -122.0673 | 0.013733 | 0.03624 | 0.011922 | -0.00020289 | 0.031368 | -0.013819 | -0.0069811 | 0.016834 | 0.009155 | -0.09613 | 0.054932 | -0.022888 | 0.064087 | 0.11444 | 0.013733 | 0.13275 | -0.045776 | -0.036621 | 122.1222 | -0.10986 | 122.0764 | 122.0444 | 0.050354 | 122.0306 | -0.059509 | -0.045777 | 122.081 | 122.2 | 122.1313 | 121.9711 | 122.0764 | 122.0215 | 122.1817 | 122.0306 | 121.9711 | 122.0764 | 122.1817 | 122.1313 | 122.0215 | 0.041199 | -0.050354
1604.2031 | 122.2412 | -122.1405 | 0.027466 | -0.078201 | 0.0082906 | -0.00041649 | 0.039913 | -0.012751 | -0.010186 | 0.014484 | 0.036621 | -0.13275 | 0.032043 | -0.009155 | 0.059509 | 0.10529 | -0.004578 | 0.036621 | 0.004578 | -0.036621 | 122.1725 | -0.16022 | 122.1771 | 122.1313 | 0.032043 | 122.1039 | -0.022888 | 0.004578 | 122.1359 | 122.1771 | 122.2 | 122.0078 | 122.1771 | 122.1451 | 122.2458 | 122.1039 | 122.0078 | 122.1771 | 122.2458 | 122.2 | 122.1451 | 0.004577 | -0.064087
1605.9531 | 122.2595 | -122.0901 | 0.027466 | -0.032425 | 0.012563 | -0.00020289 | 0.037563 | -0.011683 | -0.011681 | 0.017688 | -0.013733 | -0.16479 | 0.004578 | -0.009155 | 0.036621 | 0.07782 | -0.036621 | -0.022888 | -0.009155 | -0.041199 | 122.0947 | -0.19226 | 122.0764 | 122.081 | 0.009155 | 122.0489 | -0.036621 | -0.018311 | 122.0535 | 122.0673 | 122.1268 | 121.9254 | 122.0764 | 122.081 | 122.168 | 122.0489 | 121.9254 | 122.0764 | 122.168 | 122.1268 | 122.081 | -0.022888 | -0.068665
1607.7031 | 122.2595 | -122.1268 | 0.027466 | -0.12398 | 0.011495 | 0.0034287 | 0.029873 | -0.015528 | -0.0086901 | 0.017261 | 0.19226 | -0.022888 | 0.17853 | 0.054932 | 0.15564 | 0.1831 | 0.10071 | 0.35248 | -0.045776 | -0.032043 | 122.3053 | -0.050354 | 122.319 | 122.1817 | 0.12817 | 122.0947 | -0.073242 | 0.013733 | 122.2275 | 122.4792 | 122.2824 | 122.1039 | 122.319 | 122.081 | 122.3099 | 122.0947 | 122.1039 | 122.319 | 122.3099 | 122.2824 | 122.081 | 0.15106 | -0.059509
1609.4688 | 122.3145 | -122.113 | 0.009155 | -0.10109 | 0.010213 | 0.0036423 | 0.029659 | -0.014887 | -0.0086901 | 0.015979 | 0.1236 | -0.041199 | 0.14648 | 0.041199 | 0.12817 | 0.17395 | 0.064087 | 0.3067 | -0.045776 | -0.009155 | 122.2595 | -0.050354 | 122.2366 | 122.1542 | 0.11902 | 122.1039 | -0.054931 | -0.022888 | 122.1771 | 122.4197 | 122.2412 | 122.0718 | 122.2366 | 122.0673 | 122.287 | 122.1039 | 122.0718 | 122.2366 | 122.287 | 122.2412 | 122.0673 | 0.13733 | -0.01831
1611.1719 | 122.2916 | -122.0993 | 0.013733 | -0.18501 | 0.011709 | 0.00022431 | 0.037136 | -0.014674 | -0.010186 | 0.015125 | 0.086975 | 0.013733 | 0.13733 | -0.068665 | 0.018311 | 0.036621 | 0.23346 | 0.15106 | 0 | -0.054932 | 122.2366 | 0 | 122.1863 | 122.0306 | 0.004578 | 122.0444 | -0.013733 | -0.050354 | 122.3328 | 122.2504 | 122.1176 | 122.113 | 122.1863 | 122.0993 | 122.1359 | 122.0444 | 122.113 | 122.1863 | 122.1359 | 122.1176 | 122.0993 | 0.1236 | -0.068665
1612.9375 | 122.3511 | -122.0993 | 0.018311 | -0.10872 | 0.009786 | -0.00084389 | 0.030727 | -0.013606 | -0.0076221 | 0.018329 | 0.1236 | -0.045776 | 0.13275 | 0.045776 | 0.11444 | 0.16479 | 0.086975 | 0.29297 | -0.032043 | -0.018311 | 122.2321 | -0.064087 | 122.2229 | 122.1451 | 0.09613 | 122.081 | -0.050354 | -0.009155 | 122.1863 | 122.3923 | 122.2137 | 122.0535 | 122.2229 | 122.0673 | 122.2641 | 122.081 | 122.0535 | 122.2229 | 122.2641 | 122.2137 | 122.0673 | 0.11444 | -0.036622
1614.6406 | 122.2961 | -122.1176 | 0.041199 | -0.24605 | 0.008718 | -0.00020289 | 0.034573 | -0.014033 | -0.011467 | 0.01427 | 0.1831 | 0.032043 | 0.19226 | -0.004578 | 0.082397 | 0.11444 | 0.24261 | 0.30212 | -0.027466 | -0.036621 | 122.3099 | -0.009156 | 122.3007 | 122.113 | 0.041198 | 122.081 | -0.068665 | -0.009156 | 122.3602 | 122.4197 | 122.2 | 122.1497 | 122.3007 | 122.0901 | 122.2321 | 122.081 | 122.1497 | 122.3007 | 122.2321 | 122.2 | 122.0901 | 0.15106 | -0.07782
1616.4062 | 122.3419 | -122.0901 | -0.009155 | 0.16594 | 0.011068 | 0.00086511 | 0.036709 | -0.011683 | -0.010399 | 0.015125 | -0.059509 | -0.26093 | -0.054932 | 0.018311 | 0.10071 | 0.15106 | -0.25177 | -0.054932 | -0.041199 | -0.013733 | 122.0352 | -0.25177 | 122.0306 | 122.1085 | 0.10986 | 122.0764 | -0.032044 | -0.004577 | 121.8384 | 122.0352 | 122.1909 | 121.8292 | 122.0306 | 122.0489 | 122.2412 | 122.0764 | 121.8292 | 122.0306 | 122.2412 | 122.1909 | 122.0489 | -0.045777 | -0.004578
1618.0938 | 122.3831 | -122.0673 | -0.022888 | 0.097275 | 0.010854 | 0.0032151 | 0.03735 | -0.013178 | -0.011681 | 0.017902 | -0.14191 | -0.21057 | -0.059509 | -0.068665 | -0.009155 | 0.022888 | -0.10071 | -0.19226 | -0.013733 | -0.050354 | 122.0078 | -0.18768 | 121.9254 | 121.9986 | 0.013733 | 122.0169 | 0.009155 | -0.082398 | 121.9666 | 121.875 | 122.0581 | 121.8567 | 121.9254 | 122.0535 | 122.0901 | 122.0169 | 121.8567 | 121.9254 | 122.0901 | 122.0581 | 122.0535 | -0.036621 | -0.027466
1619.8438 | 122.3694 | -122.0901 | -0.013733 | 0.066757 | 0.011922 | 0.0027877 | 0.037777 | -0.012751 | -0.0097583 | 0.016834 | -0.1236 | -0.20142 | -0.068665 | -0.091553 | -0.018311 | 0.027466 | -0.09613 | -0.16022 | -0.004578 | -0.045776 | 122.0215 | -0.18768 | 121.9666 | 121.9986 | -0.004578 | 122.0444 | 0.009155 | -0.054931 | 121.994 | 121.9299 | 122.0718 | 121.8887 | 121.9666 | 122.0856 | 122.1176 | 122.0444 | 121.8887 | 121.9666 | 122.1176 | 122.0718 | 122.0856 | -0.054932 | -0.032043
1621.6094 | 122.3602 | -122.1039 | 0.009155 | 0.12016 | 0.010427 | 0.0023605 | 0.028164 | -0.014674 | -0.0078357 | 0.015338 | -0.013733 | -0.20599 | -0.004578 | -0.009155 | 0.082397 | 0.13733 | -0.10986 | 0.068665 | -0.045776 | -0.022888 | 122.0993 | -0.21515 | 122.0901 | 122.0947 | 0.073242 | 122.081 | -0.054931 | -0.009155 | 121.994 | 122.1725 | 122.1863 | 121.8979 | 122.0901 | 122.0581 | 122.2412 | 122.081 | 121.8979 | 122.0901 | 122.2412 | 122.1863 | 122.0581 | -0.013733 | -0.032043
1623.3594 | 122.2778 | -122.1405 | 0.018311 | -0.1545 | 0.009786 | -0.0019119 | 0.031582 | -0.014674 | -0.010826 | 0.016193 | 0.21057 | 0.022888 | 0.21515 | 0.045776 | 0.11902 | 0.14648 | 0.16022 | 0.3479 | -0.059509 | -0.022888 | 122.3557 | 0.004577 | 122.3511 | 122.1863 | 0.10071 | 122.1176 | -0.07782 | -0.004578 | 122.3007 | 122.4884 | 122.2595 | 122.1634 | 122.3511 | 122.081 | 122.287 | 122.1176 | 122.1634 | 122.3511 | 122.287 | 122.2595 | 122.081 | 0.19684 | -0.041199
1625.0469 | 122.2778 | -122.113 | 0.045776 | -0.16212 | 0.0085042 | 0.00065151 | 0.038632 | -0.013606 | -0.01104 | 0.017047 | 0.07782 | -0.004578 | 0.10071 | -0.022888 | 0.027466 | 0.059509 | 0.13275 | 0.11902 | -0.013733 | -0.050354 | 122.2137 | -0.050354 | 122.1909 | 122.0901 | -0.01831 | 122.0627 | -0.059509 | -0.022888 | 122.2458 | 122.2321 | 122.1405 | 122.1085 | 122.1909 | 122.0993 | 122.1725 | 122.0627 | 122.1085 | 122.1909 | 122.1725 | 122.1405 | 122.0993 | 0.054932 | -0.09613
1626.7969 | 122.3145 | -122.1313 | 0.022888 | -0.2079 | 0.010854 | 0.0017197 | 0.033718 | -0.011256 | -0.010186 | 0.01662 | 0.091553 | 0.036621 | 0.13733 | -0.068665 | 0.009155 | 0.018311 | 0.27008 | 0.17395 | 0.004578 | -0.064087 | 122.2687 | 0.013733 | 122.2229 | 122.0627 | -0.013733 | 122.0673 | -0.01831 | -0.045776 | 122.4014 | 122.3053 | 122.1405 | 122.168 | 122.2229 | 122.1359 | 122.1497 | 122.0673 | 122.168 | 122.2229 | 122.1497 | 122.1405 | 122.1359 | 0.11444 | -0.086975
1628.5469 | 122.3877 | -122.113 | -0.004578 | 0.17357 | 0.012136 | 0.0034287 | 0.036709 | -0.01211 | -0.0097583 | 0.017261 | -0.10986 | -0.25177 | -0.082397 | -0.050354 | 0.045776 | 0.091553 | -0.20142 | -0.14191 | -0.022888 | -0.045776 | 122.0306 | -0.24719 | 122.0032 | 122.0627 | 0.050354 | 122.0673 | -0.01831 | -0.027466 | 121.9116 | 121.9711 | 122.1588 | 121.8613 | 122.0032 | 122.0901 | 122.2046 | 122.0673 | 121.8613 | 122.0032 | 122.2046 | 122.1588 | 122.0901 | -0.077819 | -0.041198
1630.3125 | 122.3236 | -122.1222 | 0.022888 | -0.18501 | 0.013631 | -0.0016983 | 0.035 | -0.013606 | -0.0095447 | 0.015979 | 0.073242 | 0.018311 | 0.12817 | -0.073242 | 0.018311 | 0.041199 | 0.21515 | 0.15106 | 0 | -0.068665 | 122.2504 | -0.004577 | 122.1954 | 122.049 | -0.004577 | 122.0535 | -0.022888 | -0.054932 | 122.3373 | 122.2733 | 122.1405 | 122.1405 | 122.1954 | 122.1222 | 122.1634 | 122.0535 | 122.1405 | 122.1954 | 122.1634 | 122.1405 | 122.1222 | 0.10529 | -0.091553
1632.0625 | 122.3648 | -122.1176 | 0 | 0.18883 | 0.009786 | 0.0023605 | 0.034786 | -0.011256 | -0.011895 | 0.016834 | -0.073242 | -0.24719 | -0.045776 | 0.013733 | 0.10071 | 0.1236 | -0.24719 | -0.045776 | -0.041199 | -0.027466 | 122.0718 | -0.24719 | 122.0444 | 122.1313 | 0.10071 | 122.0901 | -0.041199 | -0.027466 | 121.8704 | 122.0718 | 122.2183 | 121.8704 | 122.0444 | 122.0764 | 122.2412 | 122.0901 | 121.8704 | 122.0444 | 122.2412 | 122.2183 | 122.0764 | -0.045776 | -0.027466
1633.75 | 122.2916 | -122.1497 | 0.013733 | -0.032425 | 0.011709 | 0.0040695 | 0.037777 | -0.01211 | -0.010826 | 0.016406 | -0.013733 | -0.14191 | 0 | -0.036621 | 0.036621 | 0.082397 | -0.036621 | -0.027466 | -0.022888 | -0.050354 | 122.1497 | -0.15564 | 122.1359 | 122.113 | 0.022888 | 122.0993 | -0.036621 | -0.013733 | 122.113 | 122.1222 | 122.1863 | 122.0078 | 122.1359 | 122.1268 | 122.2321 | 122.0993 | 122.0078 | 122.1359 | 122.2321 | 122.1863 | 122.1268 | -0.013733 | -0.064087
1635.5156 | 122.287 | -122.1359 | 0.027466 | -0.032425 | 0.011495 | 0.0010787 | 0.037777 | -0.013178 | -0.010613 | 0.016406 | 0.004578 | -0.16022 | 0.013733 | -0.009155 | 0.041199 | 0.059509 | -0.027466 | -0.004578 | 0 | -0.018311 | 122.1497 | -0.18768 | 122.1405 | 122.1268 | 0.013733 | 122.1176 | -0.027466 | -0.009155 | 122.1085 | 122.1313 | 122.1771 | 121.9757 | 122.1405 | 122.1359 | 122.1954 | 122.1176 | 121.9757 | 122.1405 | 122.1954 | 122.1771 | 122.1359 | -0.013733 | -0.045777
1637.2656 | 122.3282 | -122.1359 | 0.004578 | -0.23842 | 0.010641 | -0.0021255 | 0.029446 | -0.011897 | -0.0095447 | 0.018756 | 0.16937 | 0.045776 | 0.18768 | -0.022888 | 0.064087 | 0.086975 | 0.24719 | 0.26093 | -0.018311 | -0.045776 | 122.3236 | 0.041198 | 122.3053 | 122.113 | 0.059509 | 122.0901 | -0.022889 | -0.01831 | 122.3831 | 122.3969 | 122.2 | 122.1817 | 122.3053 | 122.1176 | 122.2229 | 122.0901 | 122.1817 | 122.3053 | 122.2229 | 122.2 | 122.1176 | 0.1831 | -0.050354
1639.0156 | 122.4106 | -122.1222 | -0.027466 | 0.12016 | 0.010213 | -0.0012711 | 0.035641 | -0.012965 | -0.0078357 | 0.019611 | -0.14191 | -0.26093 | -0.07782 | -0.10071 | 0 | 0.045776 | -0.13733 | -0.17853 | -0.013733 | -0.050354 | 122.0444 | -0.23346 | 121.9803 | 122.0215 | 0.027466 | 122.0718 | 0.013733 | -0.064087 | 121.9849 | 121.9437 | 122.1222 | 121.8613 | 121.9803 | 122.1085 | 122.168 | 122.0718 | 121.8613 | 121.9803 | 122.168 | 122.1222 | 122.1085 | -0.050354 | -0.022888
1640.7031 | 122.3877 | -122.1313 | 0.004578 | 0.082016 | 0.011281 | 0.0021469 | 0.036495 | -0.011469 | -0.0078357 | 0.018756 | -0.13275 | -0.20599 | -0.082397 | -0.10071 | -0.013733 | 0.022888 | -0.050354 | -0.16937 | -0.009155 | -0.050354 | 122.049 | -0.21057 | 121.9986 | 122.0306 | -0.018311 | 122.081 | -0.013733 | -0.050354 | 122.081 | 121.962 | 122.1176 | 121.9254 | 121.9986 | 122.1222 | 122.1542 | 122.081 | 121.9254 | 121.9986 | 122.1542 | 122.1176 | 122.1222 | -0.086975 | -0.054932
1642.4531 | 122.3145 | -122.1588 | 0.009155 | -0.1545 | 0.01235 | -0.0010575 | 0.033718 | -0.011469 | -0.0097583 | 0.016193 | 0.07782 | 0.022888 | 0.12817 | -0.068665 | 0.022888 | 0.068665 | 0.20142 | 0.13275 | -0.018311 | -0.050354 | 122.287 | 0.013733 | 122.2366 | 122.0901 | 0.013733 | 122.1085 | -0.027466 | -0.050354 | 122.3602 | 122.2916 | 122.1817 | 122.1817 | 122.2366 | 122.1405 | 122.2275 | 122.1085 | 122.1817 | 122.2366 | 122.2275 | 122.1817 | 122.1405 | 0.11902 | -0.059509
1644.2031 | 122.374 | -122.1405 | 0 | 0.12779 | 0.011068 | 0.00043791 | 0.029873 | -0.011897 | -0.0091173 | 0.016193 | -0.022888 | -0.2243 | -0.009155 | 0.032043 | 0.11902 | 0.17395 | -0.21515 | 0.045776 | -0.064087 | -0.013733 | 122.1313 | -0.2243 | 122.1176 | 122.1725 | 0.11902 | 122.1268 | -0.064087 | -0.013733 | 121.9254 | 122.1863 | 122.2595 | 121.9162 | 122.1176 | 122.0764 | 122.3145 | 122.1268 | 121.9162 | 122.1176 | 122.3145 | 122.2595 | 122.0764 | -0.009155 | -0.013733
1645.9062 | 122.374 | -122.1451 | 0 | 0.15068 | 0.009786 | 0.0034287 | 0.033718 | -0.012751 | -0.0050585 | 0.016834 | -0.022888 | -0.27466 | -0.050354 | 0.036621 | 0.11444 | 0.16937 | -0.24261 | -0.004578 | -0.068665 | -0.013733 | 122.0947 | -0.27466 | 122.1222 | 122.1817 | 0.11444 | 122.1313 | -0.068665 | 0.027466 | 121.9025 | 122.1405 | 122.2595 | 121.8704 | 122.1222 | 122.0764 | 122.3145 | 122.1313 | 121.8704 | 122.1222 | 122.3145 | 122.2595 | 122.0764 | -0.050354 | -0.013733
1647.6562 | 122.3236 | -122.1542 | 0.013733 | 0.020981 | 0.0091452 | 0.0047103 | 0.037777 | -0.013178 | -0.010186 | 0.017047 | -0.036621 | -0.16937 | -0.022888 | -0.050354 | 0 | 0.059509 | -0.045776 | -0.086975 | 0.009155 | -0.036621 | 122.1313 | -0.18311 | 122.1176 | 122.1039 | -0.013733 | 122.1176 | -0.004578 | -0.013733 | 122.1085 | 122.0673 | 122.1542 | 121.9849 | 122.1176 | 122.1634 | 122.2137 | 122.1176 | 121.9849 | 122.1176 | 122.2137 | 122.1542 | 122.1634 | -0.036621 | -0.050354
1649.4219 | 122.3785 | -122.1176 | 0 | 0.17357 | 0.011068 | 0.0032151 | 0.036923 | -0.012965 | -0.0080493 | 0.017261 | -0.068665 | -0.23346 | -0.036621 | 0.004578 | 0.086975 | 0.14648 | -0.23804 | -0.036621 | -0.045776 | -0.018311 | 122.081 | -0.23346 | 122.049 | 122.1222 | 0.086975 | 122.0993 | -0.045776 | -0.032044 | 121.8796 | 122.081 | 122.2046 | 121.8842 | 122.049 | 122.0718 | 122.2641 | 122.0993 | 121.8842 | 122.049 | 122.2641 | 122.2046 | 122.0718 | -0.036621 | -0.018311
1651.1719 | 122.3145 | -122.1725 | 0.022888 | -0.055313 | 0.012136 | 0.0040695 | 0.036923 | -0.0099741 | -0.012322 | 0.015765 | 0.004578 | -0.14191 | 0.032043 | -0.004578 | 0.050354 | 0.082397 | -0.022888 | 0.018311 | -0.009155 | -0.045776 | 122.2046 | -0.16479 | 122.1771 | 122.168 | 0.027466 | 122.1268 | -0.032043 | -0.027465 | 122.1497 | 122.1909 | 122.2229 | 122.0306 | 122.1771 | 122.1634 | 122.2549 | 122.1268 | 122.0306 | 122.1771 | 122.2549 | 122.2229 | 122.1634 | 0.009155 | -0.068664
1652.9219 | 122.3099 | -122.1863 | 0.027466 | -0.16975 | 0.008077 | -0.00041649 | 0.030087 | -0.01446 | -0.0089037 | 0.015338 | 0.17395 | 0.018311 | 0.20599 | 0.013733 | 0.091553 | 0.13733 | 0.19226 | 0.33417 | -0.004578 | -0.032043 | 122.3923 | -0.009155 | 122.3602 | 122.2 | 0.064087 | 122.1542 | -0.032044 | -0.032044 | 122.3785 | 122.5204 | 122.2778 | 122.2046 | 122.3602 | 122.1817 | 122.3236 | 122.1542 | 122.2046 | 122.3602 | 122.3236 | 122.2778 | 122.1817 | 0.17853 | -0.059509
1654.6094 | 122.4014 | -122.1359 | -0.013733 | 0.18883 | 0.011709 | 0.00022431 | 0.035 | -0.01211 | -0.0076221 | 0.017261 | -0.10986 | -0.25635 | -0.073242 | -0.022888 | 0.041199 | 0.10529 | -0.21057 | -0.10071 | -0.032043 | -0.036621 | 122.0627 | -0.24262 | 122.0261 | 122.113 | 0.054932 | 122.0993 | -0.01831 | -0.036621 | 121.9254 | 122.0352 | 122.1771 | 121.8796 | 122.0261 | 122.1039 | 122.2412 | 122.0993 | 121.8796 | 122.0261 | 122.2412 | 122.1771 | 122.1039 | -0.059509 | -0.022888
1656.375 | 122.3923 | -122.1588 | 0.004578 | 0.097275 | 0.010427 | 0.0036423 | 0.032223 | -0.01446 | -0.0076221 | 0.019183 | 0.004578 | -0.21973 | -0.004578 | 0.013733 | 0.10071 | 0.16479 | -0.16937 | 0.045776 | -0.050354 | -0.022888 | 122.1542 | -0.22431 | 122.1634 | 122.1725 | 0.09613 | 122.1359 | -0.054932 | 0.009156 | 121.9894 | 122.2046 | 122.2595 | 121.9391 | 122.1634 | 122.1085 | 122.3236 | 122.1359 | 121.9391 | 122.1634 | 122.3236 | 122.2595 | 122.1085 | -0.009156 | -0.027466
1658.0625 | 122.3831 | -122.1451 | -0.009155 | 0.16594 | 0.012136 | -0.0010575 | 0.036923 | -0.014033 | -0.0069811 | 0.017902 | -0.09613 | -0.26093 | -0.068665 | -0.009155 | 0.07782 | 0.1236 | -0.21057 | -0.073242 | -0.041199 | -0.036621 | 122.0764 | -0.25177 | 122.049 | 122.1359 | 0.086975 | 122.1085 | -0.032044 | -0.027465 | 121.9345 | 122.0718 | 122.2229 | 121.8842 | 122.049 | 122.1039 | 122.2687 | 122.1085 | 121.8842 | 122.049 | 122.2687 | 122.2229 | 122.1039 | -0.05951 | -0.027466
1659.7969 | 122.3877 | -122.1588 | 0 | 0.1049 | 0.010641 | 0.00043791 | 0.035 | -0.015101 | -0.0091173 | 0.015765 | -0.022888 | -0.28381 | -0.027466 | 0.032043 | 0.10529 | 0.17395 | -0.23346 | -0.009155 | -0.036621 | -0.022888 | 122.1313 | -0.28381 | 122.1359 | 122.1909 | 0.10529 | 122.1359 | -0.036621 | 0.004578 | 121.9254 | 122.1497 | 122.2641 | 121.875 | 122.1359 | 122.1222 | 122.3328 | 122.1359 | 121.875 | 122.1359 | 122.3328 | 122.2641 | 122.1222 | -0.027466 | -0.022888
1661.5469 | 122.3373 | -122.1863 | 0.009155 | -0.0019073 | 0.008718 | -0.0021255 | 0.038204 | -0.011683 | -0.0069811 | 0.017047 | -0.045776 | -0.1831 | -0.013733 | -0.045776 | 0 | 0.050354 | -0.041199 | -0.091553 | -0.022888 | -0.054932 | 122.1725 | -0.19226 | 122.1405 | 122.1405 | -0.009155 | 122.1313 | -0.032043 | -0.032043 | 122.1451 | 122.0947 | 122.1863 | 122.0032 | 122.1405 | 122.1634 | 122.2366 | 122.1313 | 122.0032 | 122.1405 | 122.2366 | 122.1863 | 122.1634 | -0.022888 | -0.064087
1663.2969 | 122.438 | -122.1405 | 0 | -0.0019073 | 0.011068 | 0.0010787 | 0.031368 | -0.013606 | -0.0097583 | 0.01662 | 0.041199 | -0.10986 | 0.086975 | -0.036621 | 0.059509 | 0.12817 | 0.054932 | 0.13733 | -0.036621 | -0.036621 | 122.2275 | -0.10986 | 122.1817 | 122.1039 | 0.059509 | 122.1039 | -0.036621 | -0.045776 | 122.1954 | 122.2778 | 122.2 | 122.0306 | 122.1817 | 122.1039 | 122.2687 | 122.1039 | 122.0306 | 122.1817 | 122.2687 | 122.2 | 122.1039 | 0.086975 | -0.036621
1665.0469 | 122.319 | -122.2 | 0.022888 | -0.055313 | 0.011281 | 0.0034287 | 0.036923 | -0.013178 | -0.0084765 | 0.017047 | -0.004578 | -0.15564 | 0.013733 | -0.013733 | 0.041199 | 0.086975 | -0.022888 | -0.004578 | -0.009155 | -0.050354 | 122.2137 | -0.17853 | 122.1954 | 122.1863 | 0.018311 | 122.1497 | -0.032043 | -0.018311 | 122.1771 | 122.1954 | 122.2412 | 122.0444 | 122.1954 | 122.1909 | 122.287 | 122.1497 | 122.0444 | 122.1954 | 122.287 | 122.2412 | 122.1909 | -0.009155 | -0.073242
1666.7344 | 122.374 | -122.1634 | 0.009155 | 0.17357 | 0.010854 | -0.0049027 | 0.03265 | -0.013392 | -0.0093311 | 0.017688 | -0.032043 | -0.26093 | -0.018311 | 0.036621 | 0.10986 | 0.17395 | -0.23804 | 0.009155 | -0.041199 | -0.004578 | 122.1451 | -0.27008 | 122.1313 | 122.2 | 0.10071 | 122.1588 | -0.050354 | -0.013732 | 121.9254 | 122.1725 | 122.2733 | 121.9025 | 122.1313 | 122.1222 | 122.3373 | 122.1588 | 121.9025 | 122.1313 | 122.3373 | 122.2733 | 122.1222 | -0.027466 | -0.013733
1668.4844 | 122.319 | -122.1909 | 0.032043 | -0.14687 | 0.010213 | -0.0029801 | 0.031582 | -0.014033 | -0.0097583 | 0.016193 | 0.18768 | 0.018311 | 0.19226 | 0.041199 | 0.11444 | 0.16937 | 0.15106 | 0.32959 | -0.032043 | -0.022888 | 122.3831 | -0.013732 | 122.3785 | 122.2321 | 0.082398 | 122.168 | -0.064086 | -0.004578 | 122.3419 | 122.5204 | 122.3053 | 122.2092 | 122.3785 | 122.1588 | 122.3602 | 122.168 | 122.2092 | 122.3785 | 122.3602 | 122.3053 | 122.1588 | 0.16022 | -0.054931
1670.2344 | 122.4518 | -122.1588 | -0.004578 | 0.12016 | 0.009786 | 0.0034287 | 0.036495 | -0.012751 | -0.010186 | 0.019183 | -0.13275 | -0.25177 | -0.086975 | -0.086975 | -0.004578 | 0.041199 | -0.10986 | -0.16937 | -0.013733 | -0.050354 | 122.0718 | -0.24719 | 122.0261 | 122.0718 | 0 | 122.1085 | -0.009155 | -0.045776 | 122.0489 | 121.9894 | 122.1542 | 121.907 | 122.0261 | 122.1451 | 122.2 | 122.1085 | 121.907 | 122.0261 | 122.2 | 122.1542 | 122.1451 | -0.082397 | -0.045776
1672 | 122.3419 | -122.2137 | 0.041199 | -0.16212 | 0.010427 | 1.071e-05 | 0.030087 | -0.015956 | -0.0074085 | 0.015765 | 0.19684 | -0.022888 | 0.19226 | 0.054932 | 0.14191 | 0.15106 | 0.12817 | 0.36163 | -0.041199 | -0.036621 | 122.406 | -0.064087 | 122.4106 | 122.2687 | 0.10071 | 122.1771 | -0.082398 | 0.004577 | 122.3419 | 122.5754 | 122.3557 | 122.1909 | 122.4106 | 122.1725 | 122.3648 | 122.1771 | 122.1909 | 122.4106 | 122.3648 | 122.3557 | 122.1725 | 0.15106 | -0.07782
1673.7656 | 122.4564 | -122.1451 | -0.013733 | 0.02861 | 0.0099996 | 0.0027877 | 0.033505 | -0.013606 | -0.0078357 | 0.015765 | 0.013733 | -0.16022 | 0.041199 | -0.013733 | 0.050354 | 0.11444 | -0.022888 | 0.10071 | -0.022888 | -0.032043 | 122.1863 | -0.14648 | 122.1588 | 122.1313 | 0.064087 | 122.113 | -0.009155 | -0.027466 | 122.1222 | 122.2458 | 122.1954 | 121.9849 | 122.1588 | 122.1222 | 122.2595 | 122.113 | 121.9849 | 122.1588 | 122.2595 | 122.1954 | 122.1222 | 0.054932 | -0.01831
1675.4531 | 122.4747 | -122.1451 | 0 | 0.03624 | 0.0085042 | -0.0010575 | 0.033291 | -0.014674 | -0.0091173 | 0.017261 | 0.027466 | -0.15106 | 0.059509 | -0.022888 | 0.059509 | 0.11444 | -0.013733 | 0.11444 | -0.036621 | -0.041199 | 122.2046 | -0.15106 | 122.1725 | 122.1222 | 0.059509 | 122.1039 | -0.036621 | -0.032043 | 122.1313 | 122.2595 | 122.2046 | 121.994 | 122.1725 | 122.1085 | 122.2595 | 122.1039 | 121.994 | 122.1725 | 122.2595 | 122.2046 | 122.1085 | 0.059509 | -0.041199
1677.2188 | 122.3785 | -122.2 | 0.027466 | -0.2079 | 0.010427 | 0.0023605 | 0.034786 | -0.015315 | -0.010399 | 0.014697 | 0.17395 | 0.009155 | 0.17853 | -0.022888 | 0.027466 | 0.082397 | 0.24261 | 0.23346 | -0.013733 | -0.050354 | 122.3785 | -0.018311 | 122.374 | 122.1771 | 0 | 122.1497 | -0.041199 | -0.004578 | 122.4426 | 122.4335 | 122.2275 | 122.2092 | 122.374 | 122.1863 | 122.2824 | 122.1497 | 122.2092 | 122.374 | 122.2824 | 122.2275 | 122.1863 | 0.15106 | -0.07782
1678.9688 | 122.4335 | -122.2046 | 0 | -0.032425 | 0.010213 | 0.0038559 | 0.031796 | -0.015528 | -0.012108 | 0.015125 | 0.11444 | -0.082397 | 0.13733 | 0.027466 | 0.10071 | 0.16479 | 0.059509 | 0.26093 | -0.036621 | -0.018311 | 122.3419 | -0.082397 | 122.319 | 122.2321 | 0.10071 | 122.1863 | -0.036621 | -0.022888 | 122.2641 | 122.4655 | 122.3053 | 122.1222 | 122.319 | 122.168 | 122.3694 | 122.1863 | 122.1222 | 122.319 | 122.3694 | 122.3053 | 122.168 | 0.13733 | -0.018311
1680.6562 | 122.4747 | -122.1588 | -0.004578 | 0.020981 | 0.010427 | 0.0030013 | 0.032436 | -0.015528 | -0.0082629 | 0.014911 | 0.027466 | -0.13733 | 0.073242 | -0.009155 | 0.073242 | 0.11902 | -0.013733 | 0.11444 | -0.027466 | -0.045776 | 122.2321 | -0.13275 | 122.1863 | 122.1497 | 0.07782 | 122.113 | -0.022888 | -0.045776 | 122.1451 | 122.2733 | 122.2321 | 122.0215 | 122.1863 | 122.1313 | 122.2778 | 122.113 | 122.0215 | 122.1863 | 122.2778 | 122.2321 | 122.1313 | 0.07782 | -0.041198
1682.4062 | 122.4197 | -122.1909 | 0.004578 | -0.1545 | 0.0093588 | -0.00063009 | 0.032864 | -0.015315 | -0.0063403 | 0.015338 | 0.16479 | -0.027466 | 0.16937 | 0.064087 | 0.1236 | 0.16022 | 0.082397 | 0.3067 | -0.032043 | -0.013733 | 122.3602 | -0.032044 | 122.3557 | 122.2549 | 0.11902 | 122.1771 | -0.036621 | -0.004578 | 122.2733 | 122.4976 | 122.3145 | 122.1634 | 122.3557 | 122.1588 | 122.3511 | 122.1771 | 122.1634 | 122.3557 | 122.3511 | 122.3145 | 122.1588 | 0.16479 | -0.018311
1684.1562 | 122.4609 | -122.168 | -0.018311 | 0.082016 | 0.011922 | 0.0010787 | 0.0397 | -0.013178 | -0.010186 | 0.016406 | -0.15106 | -0.20599 | -0.068665 | -0.073242 | -0.018311 | 0.027466 | -0.09613 | -0.16937 | -0.022888 | -0.054932 | 122.0993 | -0.18768 | 122.0169 | 122.0947 | 0 | 122.113 | -0.004577 | -0.082397 | 122.0718 | 121.9986 | 122.1497 | 121.962 | 122.0169 | 122.1451 | 122.1954 | 122.113 | 121.962 | 122.0169 | 122.1954 | 122.1497 | 122.1451 | -0.050354 | -0.036621
1685.9219 | 122.3831 | -122.2 | 0.009155 | -0.17738 | 0.010213 | -0.0034073 | 0.035 | -0.011469 | -0.01104 | 0.016406 | 0.07782 | 0.018311 | 0.14191 | -0.050354 | 0.009155 | 0.045776 | 0.22888 | 0.12817 | -0.004578 | -0.059509 | 122.3419 | 0.009156 | 122.2778 | 122.1497 | 0 | 122.1405 | -0.013733 | -0.064087 | 122.4289 | 122.3282 | 122.2092 | 122.2183 | 122.2778 | 122.1954 | 122.2458 | 122.1405 | 122.2183 | 122.2778 | 122.2458 | 122.2092 | 122.1954 | 0.13275 | -0.068664
1687.6094 | 122.3282 | -122.2046 | 0.027466 | -0.062942 | 0.0089316 | 0.0019333 | 0.037563 | -0.013178 | -0.010826 | 0.017261 | 0.050354 | -0.10529 | 0.022888 | -0.004578 | 0.064087 | 0.082397 | 0.004578 | 0.045776 | -0.018311 | -0.036621 | 122.2275 | -0.13275 | 122.2549 | 122.2 | 0.036621 | 122.168 | -0.045777 | 0.027466 | 122.2092 | 122.2504 | 122.2687 | 122.0993 | 122.2549 | 122.1863 | 122.287 | 122.168 | 122.0993 | 122.2549 | 122.287 | 122.2687 | 122.1863 | -0.004578 | -0.064087
1689.375 | 122.4609 | -122.1863 | -0.027466 | 0.097275 | 0.01299 | 0.0064193 | 0.036923 | -0.012965 | -0.0093311 | 0.017474 | -0.13275 | -0.21057 | -0.091553 | -0.082397 | -0.013733 | 0.032043 | -0.10529 | -0.17853 | -0.027466 | -0.054932 | 122.0947 | -0.18311 | 122.0535 | 122.1039 | 0.013733 | 122.1313 | 0 | -0.041198 | 122.081 | 122.0078 | 122.1725 | 121.9757 | 122.0535 | 122.1588 | 122.2183 | 122.1313 | 121.9757 | 122.0535 | 122.2183 | 122.1725 | 122.1588 | -0.064087 | -0.027466
1691.0781 | 122.493 | -122.168 | -0.013733 | 0.03624 | 0.010854 | 0.0049241 | 0.02795 | -0.013178 | -0.0078357 | 0.016834 | 0.013733 | -0.13733 | 0.050354 | -0.018311 | 0.07782 | 0.1236 | -0.018311 | 0.09613 | -0.050354 | -0.041199 | 122.2183 | -0.1236 | 122.1817 | 122.1497 | 0.091553 | 122.1268 | -0.036621 | -0.036621 | 122.1497 | 122.2641 | 122.2458 | 122.0306 | 122.1817 | 122.1176 | 122.2916 | 122.1268 | 122.0306 | 122.1817 | 122.2916 | 122.2458 | 122.1176 | 0.064087 | -0.027466
1692.8281 | 122.3419 | -122.2183 | 0.018311 | -0.078201 | 0.009786 | 0.0015061 | 0.035854 | -0.012965 | -0.010826 | 0.018115 | 0.022888 | -0.09613 | 0.032043 | -0.004578 | 0.068665 | 0.10071 | 0.009155 | 0.032043 | -0.022888 | -0.050354 | 122.2504 | -0.11444 | 122.2412 | 122.2137 | 0.050354 | 122.168 | -0.041199 | -0.009155 | 122.2275 | 122.2504 | 122.287 | 122.1222 | 122.2412 | 122.1954 | 122.319 | 122.168 | 122.1222 | 122.2412 | 122.319 | 122.287 | 122.1954 | 0.013732 | -0.068665
1694.5781 | 122.3419 | -122.2092 | 0.032043 | -0.12398 | 0.011495 | 0.00086511 | 0.033505 | -0.014887 | -0.0097583 | 0.015979 | 0.059509 | -0.036621 | 0.10071 | -0.022888 | 0.045776 | 0.082397 | 0.086975 | 0.10071 | -0.004578 | -0.054932 | 122.3099 | -0.068664 | 122.2687 | 122.1863 | 0.013733 | 122.1542 | -0.036621 | -0.041199 | 122.2961 | 122.3099 | 122.2549 | 122.1725 | 122.2687 | 122.2046 | 122.2916 | 122.1542 | 122.1725 | 122.2687 | 122.2916 | 122.2549 | 122.2046 | 0.068665 | -0.086975
1696.2656 | 122.4655 | -122.1725 | -0.022888 | 0.11253 | 0.010854 | 0.0042831 | 0.036068 | -0.011042 | -0.010826 | 0.01897 | -0.15564 | -0.19226 | -0.068665 | -0.091553 | -0.004578 | 0.041199 | -0.082397 | -0.16479 | -0.018311 | -0.054932 | 122.1039 | -0.16937 | 122.0169 | 122.081 | 0.01831 | 122.1176 | 0.004577 | -0.086975 | 122.0901 | 122.0078 | 122.168 | 121.9803 | 122.0169 | 122.1542 | 122.2137 | 122.1176 | 121.9803 | 122.0169 | 122.2137 | 122.168 | 122.1542 | -0.045777 | -0.032044
1698 | 122.4335 | -122.1771 | 0.004578 | 0.12779 | 0.0095724 | 0.0027877 | 0.031582 | -0.014247 | -0.0089037 | 0.01662 | -0.064087 | -0.25177 | -0.041199 | 0.018311 | 0.11444 | 0.15106 | -0.22888 | -0.027466 | -0.054932 | -0.018311 | 122.1359 | -0.25635 | 122.113 | 122.1954 | 0.10986 | 122.1588 | -0.05951 | -0.022888 | 121.9482 | 122.1497 | 122.2916 | 121.9254 | 122.113 | 122.1222 | 122.3282 | 122.1588 | 121.9254 | 122.113 | 122.3282 | 122.2916 | 122.1222 | -0.045777 | -0.022889
1699.6875 | 122.3511 | -122.2321 | 0.027466 | -0.16975 | 0.008718 | 0.00043791 | 0.029446 | -0.014887 | -0.0095447 | 0.016406 | 0.20599 | -0.004578 | 0.20599 | 0.036621 | 0.11444 | 0.14648 | 0.16937 | 0.31128 | -0.036621 | -0.018311 | 122.4381 | -0.032044 | 122.4381 | 122.2687 | 0.086975 | 122.2137 | -0.064087 | 0 | 122.4014 | 122.5433 | 122.3465 | 122.2275 | 122.4381 | 122.1954 | 122.3785 | 122.2137 | 122.2275 | 122.4381 | 122.3785 | 122.3465 | 122.1954 | 0.17853 | -0.045777
1701.4531 | 122.3877 | -122.2229 | 0.009155 | -0.14687 | 0.011068 | 0.0036423 | 0.034359 | -0.013178 | -0.010613 | 0.017261 | 0.059509 | 0.018311 | 0.13733 | -0.045776 | 0.013733 | 0.050354 | 0.18768 | 0.11444 | -0.009155 | -0.059509 | 122.3602 | 0.009156 | 122.2824 | 122.1771 | 0.004578 | 122.1634 | -0.01831 | -0.07782 | 122.4106 | 122.3373 | 122.2366 | 122.2412 | 122.2824 | 122.2137 | 122.2733 | 122.1634 | 122.2412 | 122.2824 | 122.2733 | 122.2366 | 122.2137 | 0.12817 | -0.068664
1703.1406 | 122.4014 | -122.2137 | 0.022888 | -0.23842 | 0.0093588 | -0.00084389 | 0.033291 | -0.013819 | -0.010826 | 0.017047 | 0.086975 | 0.050354 | 0.14648 | -0.068665 | 0.009155 | 0.027466 | 0.26093 | 0.16022 | 0 | -0.050354 | 122.3602 | 0.027466 | 122.3007 | 122.1451 | -0.013733 | 122.1634 | -0.022888 | -0.059509 | 122.4747 | 122.374 | 122.2229 | 122.2641 | 122.3007 | 122.2137 | 122.2412 | 122.1634 | 122.2641 | 122.3007 | 122.2412 | 122.2229 | 122.2137 | 0.1236 | -0.073242
1704.8906 | 122.4701 | -122.2 | -0.009155 | 0.12779 | 0.012136 | 1.071e-05 | 0.033718 | -0.013392 | -0.0080493 | 0.015125 | -0.14191 | -0.19684 | -0.091553 | -0.07782 | -0.004578 | 0.036621 | -0.091553 | -0.17395 | -0.004578 | -0.050354 | 122.1085 | -0.18768 | 122.0581 | 122.1222 | 0.004577 | 122.1497 | 0.004577 | -0.050354 | 122.1085 | 122.0261 | 122.1954 | 122.0032 | 122.0581 | 122.1954 | 122.2366 | 122.1497 | 122.0032 | 122.0581 | 122.2366 | 122.1954 | 122.1954 | -0.082398 | -0.041199
1706.6562 | 122.4701 | -122.1954 | -0.004578 | 0.059128 | 0.010854 | 0.0042831 | 0.035214 | -0.011897 | -0.0082629 | 0.017261 | -0.15106 | -0.19684 | -0.064087 | -0.086975 | -0.009155 | 0.022888 | -0.07782 | -0.16937 | -0.004578 | -0.050354 | 122.1313 | -0.19226 | 122.0444 | 122.1085 | -0.004577 | 122.1451 | 0 | -0.086975 | 122.1176 | 122.0261 | 122.1863 | 121.9986 | 122.0444 | 122.1909 | 122.2183 | 122.1451 | 121.9986 | 122.0444 | 122.2183 | 122.1863 | 122.1909 | -0.059509 | -0.045776
1708.4062 | 122.4106 | -122.2229 | 0.018311 | -0.18501 | 0.0076498 | 0.0015061 | 0.03265 | -0.012538 | -0.0089037 | 0.017047 | 0.10986 | 0.032043 | 0.16022 | -0.073242 | 0.022888 | 0.050354 | 0.27466 | 0.19226 | 0 | -0.050354 | 122.3831 | 0.013732 | 122.3328 | 122.1497 | 0.004577 | 122.1725 | -0.018311 | -0.050354 | 122.4976 | 122.4152 | 122.2458 | 122.2549 | 122.3328 | 122.2229 | 122.2733 | 122.1725 | 122.2549 | 122.3328 | 122.2733 | 122.2458 | 122.2229 | 0.14191 | -0.068665
1710.0938 | 122.3831 | -122.2275 | 0.032043 | -0.20027 | 0.012777 | -0.00041649 | 0.035641 | -0.011897 | -0.0095447 | 0.015125 | 0.07782 | -0.004578 | 0.12817 | -0.036621 | 0.041199 | 0.068665 | 0.13733 | 0.10986 | -0.009155 | -0.054932 | 122.3557 | -0.036621 | 122.3053 | 122.1909 | 0.009156 | 122.1725 | -0.041198 | -0.050354 | 122.3648 | 122.3373 | 122.2687 | 122.2229 | 122.3053 | 122.2183 | 122.2961 | 122.1725 | 122.2229 | 122.3053 | 122.2961 | 122.2687 | 122.2183 | 0.096131 | -0.086975
1711.8438 | 122.3602 | -122.2412 | 0.018311 | -0.19264 | 0.0089316 | 0.0049241 | 0.029873 | -0.012751 | -0.0082629 | 0.016193 | 0.21057 | 0.009155 | 0.20599 | 0.045776 | 0.12817 | 0.16937 | 0.14191 | 0.33417 | -0.064087 | -0.032043 | 122.4472 | -0.009156 | 122.4518 | 122.287 | 0.10986 | 122.2092 | -0.082398 | 0.004577 | 122.3831 | 122.5754 | 122.3694 | 122.2504 | 122.4518 | 122.1771 | 122.4106 | 122.2092 | 122.2504 | 122.4518 | 122.4106 | 122.3694 | 122.1771 | 0.18768 | -0.050354
1713.5938 | 122.4838 | -122.2 | -0.022888 | 0.089645 | 0.010427 | 0.0051377 | 0.038204 | -0.012965 | -0.0095447 | 0.016834 | -0.14648 | -0.20142 | -0.07782 | -0.07782 | -0.009155 | 0.036621 | -0.082397 | -0.16022 | -0.004578 | -0.054932 | 122.1222 | -0.17853 | 122.0535 | 122.1222 | 0.013733 | 122.1451 | 0.01831 | -0.068664 | 122.1176 | 122.0398 | 122.1909 | 121.9986 | 122.0535 | 122.1954 | 122.2366 | 122.1451 | 121.9986 | 122.0535 | 122.2366 | 122.1909 | 122.1954 | -0.054932 | -0.032044
1715.3594 | 122.3877 | -122.2412 | 0.041199 | -0.017166 | 0.009786 | 0.00022431 | 0.038204 | -0.011469 | -0.013176 | 0.017047 | -0.036621 | -0.14648 | -0.032043 | -0.036621 | 0.022888 | 0.073242 | -0.041199 | -0.068665 | -0.013733 | -0.050354 | 122.2092 | -0.18768 | 122.2046 | 122.2046 | -0.018311 | 122.1909 | -0.054932 | -0.004578 | 122.2 | 122.1725 | 122.2641 | 122.0947 | 122.2046 | 122.2275 | 122.3145 | 122.1909 | 122.0947 | 122.2046 | 122.3145 | 122.2641 | 122.2275 | -0.073242 | -0.091553
1717.125 | 122.4838 | -122.2229 | 0 | 0.13542 | 0.0082906 | 0.0023605 | 0.029446 | -0.012751 | -0.0071947 | 0.018756 | -0.013733 | -0.23346 | -0.022888 | 0.041199 | 0.10986 | 0.15106 | -0.16479 | 0.054932 | -0.064087 | -0.013733 | 122.2 | -0.23346 | 122.2092 | 122.2641 | 0.10986 | 122.2092 | -0.064087 | 0.009155 | 122.0581 | 122.2778 | 122.3328 | 121.9894 | 122.2092 | 122.1588 | 122.374 | 122.2092 | 121.9894 | 122.2092 | 122.374 | 122.3328 | 122.1588 | -0.022888 | -0.013733
1718.875 | 122.4152 | -122.2458 | 0.018311 | -0.070572 | 0.0099996 | 0.0032151 | 0.037563 | -0.011256 | -0.010613 | 0.017902 | -0.086975 | -0.16479 | -0.027466 | -0.068665 | 0.009155 | 0.045776 | -0.064087 | -0.10986 | -0.018311 | -0.045776 | 122.2183 | -0.18311 | 122.1588 | 122.1771 | -0.009156 | 122.2 | -0.036622 | -0.059509 | 122.1817 | 122.1359 | 122.2549 | 122.081 | 122.1588 | 122.2275 | 122.2916 | 122.2 | 122.081 | 122.1588 | 122.2916 | 122.2549 | 122.2275 | -0.045777 | -0.064087
1720.5781 | 122.3785 | -122.2366 | 0.022888 | -0.13924 | 0.0082906 | 0.0044967 | 0.036282 | -0.011897 | -0.01104 | 0.018329 | 0.050354 | -0.027466 | 0.10071 | -0.036621 | 0.045776 | 0.068665 | 0.10529 | 0.10986 | -0.009155 | -0.064087 | 122.3373 | -0.050354 | 122.287 | 122.2 | 0.022888 | 122.1725 | -0.032043 | -0.050354 | 122.3419 | 122.3465 | 122.2824 | 122.2092 | 122.287 | 122.2275 | 122.3053 | 122.1725 | 122.2092 | 122.287 | 122.3053 | 122.2824 | 122.2275 | 0.07782 | -0.086975
1722.3281 | 122.4106 | -122.2275 | 0.009155 | -0.10872 | 0.010427 | -0.00063009 | 0.030514 | -0.015101 | -0.0080493 | 0.015552 | 0.11444 | 0.032043 | 0.16937 | -0.068665 | 0.022888 | 0.036621 | 0.28381 | 0.20599 | -0.004578 | -0.064087 | 122.3969 | 0.022888 | 122.3419 | 122.1588 | 0.013733 | 122.1634 | -0.013733 | -0.054932 | 122.5113 | 122.4335 | 122.2504 | 122.2595 | 122.3419 | 122.2229 | 122.2641 | 122.1634 | 122.2595 | 122.3419 | 122.2641 | 122.2504 | 122.2229 | 0.16022 | -0.073242
1724.0781 | 122.4792 | -122.2275 | 0 | 0.17357 | 0.0095724 | 1.071e-05 | 0.033291 | -0.013392 | -0.0097583 | 0.015765 | -0.1236 | -0.24261 | -0.073242 | -0.027466 | 0.059509 | 0.11902 | -0.23804 | -0.068665 | -0.032043 | -0.036621 | 122.1542 | -0.24261 | 122.1039 | 122.2 | 0.059509 | 122.1909 | -0.032043 | -0.050354 | 121.9894 | 122.1588 | 122.287 | 121.9849 | 122.1039 | 122.1954 | 122.3465 | 122.1909 | 121.9849 | 122.1039 | 122.3465 | 122.287 | 122.1954 | -0.073242 | -0.036621
1725.7656 | 122.3877 | -122.2458 | 0.032043 | -0.040054 | 0.010427 | 0.0036423 | 0.037777 | -0.013392 | -0.010186 | 0.01662 | -0.022888 | -0.15106 | 0.009155 | -0.027466 | 0.045776 | 0.064087 | -0.027466 | -0.022888 | -0.018311 | -0.054932 | 122.2549 | -0.18311 | 122.2229 | 122.2183 | 0.013733 | 122.1909 | -0.050354 | -0.032043 | 122.2183 | 122.2229 | 122.2916 | 122.0947 | 122.2229 | 122.2275 | 122.3099 | 122.1909 | 122.0947 | 122.2229 | 122.3099 | 122.2916 | 122.2275 | -0.022888 | -0.086975
1727.5469 | 122.5159 | -122.2137 | 0.004578 | 0.020981 | 0.0099996 | 0.00043791 | 0.02795 | -0.015315 | -0.0069811 | 0.017261 | 0.032043 | -0.11902 | 0.059509 | -0.032043 | 0.07782 | 0.11444 | 0.027466 | 0.13275 | -0.027466 | -0.036621 | 122.2733 | -0.1236 | 122.2458 | 122.1817 | 0.073242 | 122.1771 | -0.032044 | -0.027466 | 122.2412 | 122.3465 | 122.2916 | 122.0947 | 122.2458 | 122.1863 | 122.3282 | 122.1771 | 122.0947 | 122.2458 | 122.3282 | 122.2916 | 122.1863 | 0.054931 | -0.041199
1729.3125 | 122.4838 | -122.2275 | -0.004578 | 0.089645 | 0.011709 | 0.00065151 | 0.03265 | -0.013819 | -0.0080493 | 0.016834 | 0.004578 | -0.20599 | -0.009155 | 0.013733 | 0.09613 | 0.16479 | -0.16937 | 0.07782 | -0.050354 | -0.009155 | 122.2183 | -0.20142 | 122.2321 | 122.2412 | 0.10071 | 122.2183 | -0.045776 | 0.013733 | 122.0581 | 122.3053 | 122.3236 | 122.0215 | 122.2321 | 122.1771 | 122.3923 | 122.2183 | 122.0215 | 122.2321 | 122.3923 | 122.3236 | 122.1771 | -0.004577 | -0.004577
1731.0156 | 122.4792 | -122.2183 | -0.013733 | 0.1812 | 0.012136 | 0.0053513 | 0.036068 | -0.013392 | -0.01104 | 0.015338 | -0.073242 | -0.23346 | -0.054932 | 0.009155 | 0.082397 | 0.13733 | -0.17853 | -0.027466 | -0.041199 | -0.027466 | 122.1634 | -0.21973 | 122.1451 | 122.2275 | 0.09613 | 122.1909 | -0.027466 | -0.01831 | 122.0398 | 122.1909 | 122.3007 | 121.9849 | 122.1451 | 122.1771 | 122.3557 | 122.1909 | 121.9849 | 122.1451 | 122.3557 | 122.3007 | 122.1771 | -0.041199 | -0.013733
1732.7031 | 122.4838 | -122.2458 | 0.009155 | 0.17357 | 0.0093588 | 0.0047103 | 0.03265 | -0.01446 | -0.0091173 | 0.015552 | -0.013733 | -0.25177 | 0 | 0.036621 | 0.10529 | 0.15564 | -0.1831 | 0.073242 | -0.054932 | -0.009155 | 122.2458 | -0.26093 | 122.2321 | 122.2824 | 0.096131 | 122.2366 | -0.064087 | -0.013733 | 122.0627 | 122.319 | 122.3511 | 121.994 | 122.2321 | 122.1909 | 122.4014 | 122.2366 | 121.994 | 122.2321 | 122.4014 | 122.3511 | 122.1909 | -0.009155 | -0.01831
1734.4688 | 122.4106 | -122.2595 | 0.032043 | -0.032425 | 0.011709 | 0.00065151 | 0.037777 | -0.012965 | -0.0091173 | 0.018115 | 0.004578 | -0.13733 | 0.041199 | -0.022888 | 0.054932 | 0.068665 | 0.004578 | 0.036621 | -0.004578 | -0.054932 | 122.3007 | -0.16937 | 122.2641 | 122.2366 | 0.022889 | 122.2046 | -0.036621 | -0.036621 | 122.2641 | 122.2961 | 122.3145 | 122.1222 | 122.2641 | 122.2549 | 122.3282 | 122.2046 | 122.1222 | 122.2641 | 122.3282 | 122.3145 | 122.2549 | 0.009156 | -0.086975
1736.1562 | 122.4106 | -122.2687 | 0.027466 | -0.1545 | 0.0089316 | -0.0019119 | 0.034145 | -0.013178 | -0.0089037 | 0.017688 | 0.064087 | -0.013733 | 0.10071 | -0.041199 | 0.041199 | 0.059509 | 0.1236 | 0.10986 | -0.004578 | -0.032043 | 122.3694 | -0.041199 | 122.3328 | 122.2275 | 0.013733 | 122.2366 | -0.032044 | -0.036621 | 122.3923 | 122.3785 | 122.3099 | 122.2549 | 122.3328 | 122.2641 | 122.3282 | 122.2366 | 122.2549 | 122.3328 | 122.3282 | 122.3099 | 122.2641 | 0.073242 | -0.059509
1737.9375 | 122.4838 | -122.2 | -0.009155 | 0.17357 | 0.011068 | -0.0016983 | 0.034145 | -0.012324 | -0.010613 | 0.016406 | -0.12817 | -0.22888 | -0.073242 | -0.045776 | 0.050354 | 0.09613 | -0.12817 | -0.054932 | -0.022888 | -0.041199 | 122.1268 | -0.21973 | 122.0718 | 122.1542 | 0.059509 | 122.1588 | -0.013733 | -0.054932 | 122.0718 | 122.1451 | 122.2504 | 121.9711 | 122.0718 | 122.1771 | 122.2961 | 122.1588 | 121.9711 | 122.0718 | 122.2961 | 122.2504 | 122.1771 | -0.064087 | -0.032044
1739.6875 | 122.3923 | -122.2961 | 0.036621 | -0.062942 | 0.01235 | -0.00063009 | 0.033932 | -0.012538 | -0.012322 | 0.017047 | 0.018311 | -0.10529 | 0.013733 | -0.013733 | 0.054932 | 0.082397 | 0.009155 | 0.050354 | -0.013733 | -0.045776 | 122.3099 | -0.14191 | 122.3145 | 122.2824 | 0.018311 | 122.2504 | -0.050354 | 0.004578 | 122.3053 | 122.3465 | 122.3511 | 122.1909 | 122.3145 | 122.2824 | 122.3785 | 122.2504 | 122.1909 | 122.3145 | 122.3785 | 122.3511 | 122.2824 | -0.022888 | -0.082397
1741.3906 | 122.525 | -122.2137 | -0.027466 | 0.12016 | 0.01235 | -0.00041649 | 0.033718 | -0.010401 | -0.0084765 | 0.01427 | -0.13275 | -0.21057 | -0.073242 | -0.082397 | 0.009155 | 0.050354 | -0.064087 | -0.11902 | -0.004578 | -0.059509 | 122.1405 | -0.18311 | 122.081 | 122.1313 | 0.036621 | 122.1542 | 0.022888 | -0.059509 | 122.1497 | 122.0947 | 122.2229 | 122.0032 | 122.081 | 122.2092 | 122.2641 | 122.1542 | 122.0032 | 122.081 | 122.2641 | 122.2229 | 122.2092 | -0.045776 | -0.032043
1743.1719 | 122.374 | -122.2733 | 0.013733 | -0.078201 | 0.0074362 | 0.0025741 | 0.03735 | -0.014674 | -0.012963 | 0.015765 | 0.041199 | -0.091553 | 0.041199 | 0 | 0.054932 | 0.086975 | 0.036621 | 0.09613 | -0.013733 | -0.027466 | 122.3145 | -0.10529 | 122.3145 | 122.2733 | 0.041199 | 122.2458 | -0.027466 | 0 | 122.3099 | 122.3694 | 122.3282 | 122.1817 | 122.3145 | 122.2595 | 122.3602 | 122.2458 | 122.1817 | 122.3145 | 122.3602 | 122.3282 | 122.2595 | 0.027466 | -0.041199
1744.875 | 122.4289 | -122.3145 | -0.013733 | 0.089645 | 0.010427 | 0.0038559 | 0.033932 | -0.011897 | -0.0091173 | 0.018115 | -0.07782 | -0.16022 | -0.022888 | -0.073242 | -0.009155 | 0.041199 | 0 | -0.064087 | -0.009155 | -0.045776 | 122.2916 | -0.14648 | 122.2366 | 122.2412 | 0.004578 | 122.2687 | 0.004578 | -0.054932 | 122.3145 | 122.2504 | 122.3053 | 122.1542 | 122.2366 | 122.3053 | 122.3557 | 122.2687 | 122.1542 | 122.2366 | 122.3557 | 122.3053 | 122.3053 | -0.009155 | -0.032043
1746.625 | 122.3877 | -122.3373 | 0.018311 | -0.14687 | 0.008718 | 0.0017197 | 0.0303 | -0.015315 | -0.0082629 | 0.014056 | 0.19684 | -0.004578 | 0.1831 | 0.027466 | 0.10986 | 0.15564 | 0.1236 | 0.27466 | -0.036621 | -0.022888 | 122.5204 | -0.022889 | 122.5342 | 122.3648 | 0.091552 | 122.3145 | -0.054932 | 0.013733 | 122.4609 | 122.612 | 122.4472 | 122.3328 | 122.5342 | 122.3007 | 122.493 | 122.3145 | 122.3328 | 122.5342 | 122.493 | 122.4472 | 122.3007 | 0.16479 | -0.041199
1748.375 | 122.3923 | -122.2778 | 0.027466 | -0.16975 | 0.0085042 | 0.0012925 | 0.031796 | -0.014033 | -0.0084765 | 0.016193 | 0.20599 | -0.009155 | 0.20599 | 0.041199 | 0.11902 | 0.16022 | 0.091553 | 0.27466 | -0.054932 | -0.032043 | 122.4838 | -0.036621 | 122.4838 | 122.319 | 0.091553 | 122.2458 | -0.082398 | 0 | 122.3694 | 122.5525 | 122.3969 | 122.2687 | 122.4838 | 122.2229 | 122.438 | 122.2458 | 122.2687 | 122.4838 | 122.438 | 122.3969 | 122.2229 | 0.17853 | -0.059509
1750.0625 | 122.5388 | -122.2275 | 0.009155 | 0.02861 | 0.0099996 | 0.0025741 | 0.029232 | -0.014247 | -0.010186 | 0.016193 | 0.022888 | -0.11444 | 0.082397 | -0.013733 | 0.068665 | 0.10529 | 0.013733 | 0.11444 | -0.018311 | -0.041199 | 122.3099 | -0.1236 | 122.2504 | 122.2137 | 0.05951 | 122.1863 | -0.027466 | -0.059509 | 122.2412 | 122.3419 | 122.2961 | 122.113 | 122.2504 | 122.2092 | 122.3328 | 122.1863 | 122.113 | 122.2504 | 122.3328 | 122.2961 | 122.2092 | 0.073242 | -0.050354
1751.8125 | 122.5204 | -122.2366 | -0.009155 | 0.13542 | 0.010854 | 0.00065151 | 0.038845 | -0.011042 | -0.010186 | 0.016406 | -0.11902 | -0.18768 | -0.082397 | -0.07782 | -0.013733 | 0.041199 | -0.036621 | -0.10071 | 0.018311 | -0.050354 | 122.1542 | -0.17853 | 122.1176 | 122.1588 | -0.004578 | 122.1863 | 0.027466 | -0.036622 | 122.2 | 122.1359 | 122.2229 | 122.0489 | 122.1176 | 122.2549 | 122.2778 | 122.1863 | 122.0489 | 122.1176 | 122.2778 | 122.2229 | 122.2549 | -0.073242 | -0.041199
1753.5625 | 122.3923 | -122.2549 | 0.022888 | -0.085831 | 0.0093588 | 0.0012925 | 0.037991 | -0.012965 | -0.011467 | 0.01427 | 0.036621 | -0.073242 | 0.045776 | -0.013733 | 0.059509 | 0.086975 | 0.045776 | 0.09613 | -0.027466 | -0.036621 | 122.3007 | -0.09613 | 122.2916 | 122.2412 | 0.036621 | 122.2183 | -0.050354 | -0.009155 | 122.3007 | 122.3511 | 122.3145 | 122.1817 | 122.2916 | 122.2275 | 122.3419 | 122.2183 | 122.1817 | 122.2916 | 122.3419 | 122.3145 | 122.2275 | 0.022888 | -0.059509
1755.25 | 122.4014 | -122.2733 | 0.018311 | -0.070572 | 0.009786 | -0.00063009 | 0.035 | -0.015742 | -0.0097583 | 0.017902 | 0.027466 | -0.10529 | 0.050354 | -0.013733 | 0.073242 | 0.10071 | 0.009155 | 0.064087 | -0.027466 | -0.064087 | 122.3236 | -0.1236 | 122.3007 | 122.2595 | 0.054931 | 122.2092 | -0.045777 | -0.022888 | 122.2824 | 122.3373 | 122.3465 | 122.168 | 122.3007 | 122.2458 | 122.374 | 122.2092 | 122.168 | 122.3007 | 122.374 | 122.3465 | 122.2458 | 0.032043 | -0.082398
1757.0156 | 122.5021 | -122.2458 | -0.018311 | 0.14305 | 0.010641 | 0.0034287 | 0.033291 | -0.012751 | -0.0086901 | 0.017261 | -0.027466 | -0.23804 | -0.032043 | 0.022888 | 0.11444 | 0.16937 | -0.19684 | 0.041199 | -0.050354 | -0.036621 | 122.2137 | -0.21973 | 122.2183 | 122.2687 | 0.13275 | 122.2092 | -0.032043 | 0.004577 | 122.049 | 122.287 | 122.3602 | 122.0078 | 122.2183 | 122.1954 | 122.4152 | 122.2092 | 122.0078 | 122.2183 | 122.4152 | 122.3602 | 122.1954 | -0.013732 | -0.01831
1758.7188 | 122.4243 | -122.2641 | 0.022888 | -0.11635 | 0.0076498 | -0.0023391 | 0.034359 | -0.013178 | -0.0093311 | 0.017047 | 0.073242 | -0.041199 | 0.10529 | -0.018311 | 0.059509 | 0.073242 | 0.09613 | 0.10986 | -0.004578 | -0.054932 | 122.3694 | -0.064087 | 122.3373 | 122.2458 | 0.036621 | 122.2092 | -0.027466 | -0.032044 | 122.3602 | 122.374 | 122.3236 | 122.2229 | 122.3373 | 122.2595 | 122.3373 | 122.2092 | 122.2229 | 122.3373 | 122.3373 | 122.3236 | 122.2595 | 0.082398 | -0.07782
1760.5156 | 122.4564 | -122.2504 | 0.018311 | -0.16975 | 0.010854 | 1.071e-05 | 0.034359 | -0.015101 | -0.0089037 | 0.015125 | 0.07782 | 0.013733 | 0.12817 | -0.054932 | 0.018311 | 0.045776 | 0.19226 | 0.13275 | -0.009155 | -0.059509 | 122.3785 | -0.004578 | 122.3282 | 122.1954 | 0 | 122.1909 | -0.027466 | -0.050354 | 122.4426 | 122.3831 | 122.2687 | 122.2641 | 122.3282 | 122.2412 | 122.2961 | 122.1909 | 122.2641 | 122.3282 | 122.2961 | 122.2687 | 122.2412 | 0.10986 | -0.07782
1762.2031 | 122.5433 | -122.2137 | -0.027466 | 0.13542 | 0.0091452 | -0.0029801 | 0.035427 | -0.010829 | -0.0091173 | 0.015125 | -0.1236 | -0.20142 | -0.082397 | -0.082397 | 0.009155 | 0.050354 | -0.064087 | -0.10071 | -0.009155 | -0.036621 | 122.1313 | -0.17395 | 122.0901 | 122.1313 | 0.036621 | 122.1771 | 0.018311 | -0.041199 | 122.1497 | 122.113 | 122.2229 | 122.0123 | 122.0901 | 122.2046 | 122.2641 | 122.1771 | 122.0123 | 122.0901 | 122.2641 | 122.2229 | 122.2046 | -0.054931 | -0.009155
1763.9375 | 122.5067 | -122.2549 | 0.022888 | 0.12016 | 0.0085042 | 0.00022431 | 0.029873 | -0.011897 | -0.0086901 | 0.017902 | -0.013733 | -0.21515 | -0.009155 | 0.022888 | 0.11902 | 0.16479 | -0.16937 | 0.07782 | -0.054932 | -0.009155 | 122.2458 | -0.23804 | 122.2412 | 122.2778 | 0.096131 | 122.2458 | -0.07782 | -0.004578 | 122.0856 | 122.3328 | 122.374 | 122.0398 | 122.2412 | 122.2 | 122.4197 | 122.2458 | 122.0398 | 122.2412 | 122.4197 | 122.374 | 122.2 | -0.032043 | -0.032043
1765.625 | 122.525 | -122.2504 | 0 | 0.097275 | 0.009786 | -0.0014847 | 0.032436 | -0.014033 | -0.0082629 | 0.018329 | -0.013733 | -0.22888 | -0.013733 | 0.027466 | 0.09613 | 0.17395 | -0.15564 | 0.086975 | -0.041199 | -0.027466 | 122.2366 | -0.22888 | 122.2366 | 122.2778 | 0.09613 | 122.2229 | -0.041199 | 0 | 122.0947 | 122.3373 | 122.3465 | 122.0215 | 122.2366 | 122.2092 | 122.4243 | 122.2229 | 122.0215 | 122.2366 | 122.4243 | 122.3465 | 122.2092 | -0.013733 | -0.027466
1767.3125 | 122.4655 | -122.2733 | 0.032043 | -0.18501 | 0.010854 | -0.00063009 | 0.037136 | -0.012965 | -0.0078357 | 0.017261 | 0.068665 | 0.004578 | 0.11902 | -0.054932 | 0.004578 | 0.027466 | 0.20142 | 0.11902 | -0.004578 | -0.059509 | 122.3923 | -0.027465 | 122.3419 | 122.2183 | -0.027465 | 122.2137 | -0.036621 | -0.050354 | 122.4747 | 122.3923 | 122.2778 | 122.2778 | 122.3419 | 122.2687 | 122.3007 | 122.2137 | 122.2778 | 122.3419 | 122.3007 | 122.2778 | 122.2687 | 0.086976 | -0.091552
1769 | 122.5571 | -122.2275 | 0.004578 | 0.0057222 | 0.012136 | -0.0010575 | 0.027737 | -0.016596 | -0.0061267 | 0.017902 | 0.027466 | -0.12817 | 0.086975 | -0.018311 | 0.064087 | 0.1236 | 0 | 0.11902 | -0.045776 | -0.032043 | 122.3145 | -0.13275 | 122.2549 | 122.2092 | 0.059509 | 122.1954 | -0.050354 | -0.059509 | 122.2275 | 122.3465 | 122.2916 | 122.0993 | 122.2549 | 122.1817 | 122.3511 | 122.1954 | 122.0993 | 122.2549 | 122.3511 | 122.2916 | 122.1817 | 0.082397 | -0.036621
1770.6875 | 122.5388 | -122.2458 | -0.004578 | -0.040054 | 0.0085042 | -0.0023391 | 0.031368 | -0.015956 | -0.0082629 | 0.017261 | 0.091553 | -0.059509 | 0.11902 | 0.013733 | 0.10071 | 0.13275 | 0.018311 | 0.21973 | -0.059509 | -0.027466 | 122.3648 | -0.054931 | 122.3373 | 122.2595 | 0.10529 | 122.2183 | -0.054931 | -0.027466 | 122.2641 | 122.4655 | 122.3465 | 122.1863 | 122.3373 | 122.1863 | 122.3785 | 122.2183 | 122.1863 | 122.3373 | 122.3785 | 122.3465 | 122.1863 | 0.1236 | -0.022888
1772.375 | 122.5067 | -122.2549 | -0.004578 | 0.15831 | 0.010213 | -0.0014847 | 0.035427 | -0.013606 | -0.0084765 | 0.017902 | -0.009155 | -0.24261 | -0.027466 | 0.050354 | 0.1236 | 0.16479 | -0.21057 | 0.054932 | -0.041199 | -0.004578 | 122.2275 | -0.23804 | 122.2458 | 122.3053 | 0.12817 | 122.2504 | -0.036621 | 0.018311 | 122.0444 | 122.3099 | 122.3785 | 122.0123 | 122.2458 | 122.2137 | 122.4197 | 122.2504 | 122.0123 | 122.2458 | 122.4197 | 122.3785 | 122.2137 | -0.022888 | 0
1774.0625 | 122.4609 | -122.2687 | 0 | 0.013352 | 0.007009 | 0.00065151 | 0.036709 | -0.013819 | -0.0097583 | 0.017047 | -0.036621 | -0.15564 | -0.013733 | -0.054932 | 0.004578 | 0.045776 | -0.027466 | -0.022888 | -0.022888 | -0.036621 | 122.2549 | -0.15564 | 122.2321 | 122.2137 | 0.004578 | 122.2321 | -0.022888 | -0.022888 | 122.2412 | 122.2458 | 122.2733 | 122.113 | 122.2321 | 122.2458 | 122.3145 | 122.2321 | 122.113 | 122.2321 | 122.3145 | 122.2733 | 122.2458 | -0.013733 | -0.036621
1775.75 | 122.438 | -122.3099 | 0.036621 | -0.062942 | 0.0093588 | 0.0049241 | 0.036495 | -0.011897 | -0.012963 | 0.014697 | 0.009155 | -0.1236 | 0.018311 | -0.018311 | 0.054932 | 0.086975 | 0.004578 | 0.045776 | -0.022888 | -0.041199 | 122.3282 | -0.16022 | 122.319 | 122.2916 | 0.018311 | 122.2687 | -0.059509 | -0.009156 | 122.3145 | 122.3557 | 122.3648 | 122.1863 | 122.319 | 122.287 | 122.3969 | 122.2687 | 122.1863 | 122.319 | 122.3969 | 122.3648 | 122.287 | -0.01831 | -0.07782
1777.4375 | 122.4701 | -122.2961 | 0.013733 | -0.23842 | 0.0072226 | 0.0012925 | 0.030514 | -0.014674 | -0.0078357 | 0.015765 | 0.068665 | 0.027466 | 0.12817 | -0.073242 | 0.013733 | 0.032043 | 0.23346 | 0.12817 | -0.004578 | -0.045776 | 122.4243 | 0.013733 | 122.3648 | 122.2229 | 0 | 122.2504 | -0.018311 | -0.059509 | 122.5296 | 122.4243 | 122.3099 | 122.3236 | 122.3648 | 122.2916 | 122.3282 | 122.2504 | 122.3236 | 122.3648 | 122.3282 | 122.3099 | 122.2916 | 0.11444 | -0.059509
1779.1406 | 122.4884 | -122.2733 | 0.032043 | -0.1545 | 0.0089316 | 0.00086511 | 0.034145 | -0.012324 | -0.010826 | 0.015765 | 0.059509 | 0.009155 | 0.1236 | -0.059509 | 0.013733 | 0.036621 | 0.1831 | 0.10986 | -0.004578 | -0.059509 | 122.3969 | -0.022888 | 122.3328 | 122.2137 | -0.01831 | 122.2137 | -0.036621 | -0.064087 | 122.4564 | 122.3831 | 122.287 | 122.2824 | 122.3328 | 122.2687 | 122.3099 | 122.2137 | 122.2824 | 122.3328 | 122.3099 | 122.287 | 122.2687 | 0.091553 | -0.091552
1780.8438 | 122.4655 | -122.3053 | 0.027466 | -0.040054 | 0.0095724 | 0.0012925 | 0.035854 | -0.012965 | -0.0086901 | 0.018329 | -0.013733 | -0.14191 | 0.009155 | -0.027466 | 0.045776 | 0.064087 | 0.013733 | 0.009155 | -0.018311 | -0.045776 | 122.3145 | -0.16937 | 122.2916 | 122.2778 | 0.01831 | 122.2595 | -0.045777 | -0.022888 | 122.319 | 122.3145 | 122.3511 | 122.1634 | 122.2916 | 122.287 | 122.3694 | 122.2595 | 122.1634 | 122.2916 | 122.3694 | 122.3511 | 122.287 | -0.018311 | -0.073242
1782.5469 | 122.5479 | -122.2549 | -0.018311 | 0.097275 | 0.009786 | 0.0015061 | 0.034786 | -0.0097605 | -0.0086901 | 0.017047 | -0.10986 | -0.20142 | -0.064087 | -0.086975 | -0.018311 | 0.027466 | -0.050354 | -0.10986 | 0.013733 | -0.045776 | 122.1909 | -0.18311 | 122.1451 | 122.168 | 0 | 122.2092 | 0.032044 | -0.045776 | 122.2046 | 122.1451 | 122.2366 | 122.0535 | 122.1451 | 122.2687 | 122.2824 | 122.2092 | 122.0535 | 122.1451 | 122.2824 | 122.2366 | 122.2687 | -0.045776 | -0.027465
1784.2656 | 122.4792 | -122.3007 | 0.009155 | -0.17738 | 0.009786 | 0.0025741 | 0.030727 | -0.013392 | -0.0095447 | 0.015125 | 0.073242 | 0.027466 | 0.15564 | -0.064087 | 0.004578 | 0.041199 | 0.25635 | 0.14648 | -0.009155 | 0.032043 | 122.4564 | 0.018311 | 122.374 | 122.2366 | -0.004577 | 122.3328 | -0.01831 | -0.082398 | 122.5571 | 122.4472 | 122.3053 | 122.3282 | 122.374 | 122.2916 | 122.3419 | 122.3328 | 122.3282 | 122.374 | 122.3419 | 122.3053 | 122.2916 | 0.14649 | 0.022888
1785.9844 | 122.5296 | -122.2778 | 0 | 0.15068 | 0.010854 | -0.0010575 | 0.03265 | -0.011256 | -0.0093311 | 0.01897 | -0.09613 | -0.2243 | -0.073242 | -0.022888 | 0.045776 | 0.10986 | -0.15106 | -0.045776 | -0.018311 | -0.13733 | 122.2046 | -0.2243 | 122.1817 | 122.2549 | 0.045776 | 122.1405 | -0.018311 | -0.022888 | 122.1268 | 122.2321 | 122.3236 | 122.0535 | 122.1817 | 122.2595 | 122.3877 | 122.1405 | 122.0535 | 122.1817 | 122.3877 | 122.3236 | 122.2595 | -0.073242 | -0.13733
1787.6719 | 122.4655 | -122.3053 | 0.009155 | -0.13161 | 0.009786 | -0.00020289 | 0.033077 | -0.013178 | -0.010826 | 0.016193 | 0.050354 | -0.004578 | 0.10529 | -0.050354 | 0.022888 | 0.050354 | 0.19684 | 0.1236 | -0.004578 | 0.018311 | 122.4106 | -0.013733 | 122.3557 | 122.2549 | 0.013733 | 122.3236 | -0.013733 | -0.054932 | 122.5021 | 122.4289 | 122.3282 | 122.3007 | 122.3557 | 122.3007 | 122.3557 | 122.3236 | 122.3007 | 122.3557 | 122.3557 | 122.3282 | 122.3007 | 0.096131 | 0.009156
1789.4219 | 122.5204 | -122.3053 | 0.009155 | -0.085831 | 0.0093588 | -0.0019119 | 0.027737 | -0.014033 | -0.0082629 | 0.016834 | 0.15106 | -0.045776 | 0.15564 | 0.032043 | 0.13275 | 0.15564 | 0.032043 | 0.27008 | -0.045776 | 0.032043 | 122.4609 | -0.054931 | 122.4564 | 122.3373 | 0.1236 | 122.3373 | -0.054931 | -0.004578 | 122.3373 | 122.5754 | 122.438 | 122.2595 | 122.4564 | 122.2595 | 122.4609 | 122.3373 | 122.2595 | 122.4564 | 122.4609 | 122.438 | 122.2595 | 0.14649 | 0.022888
1791.1094 | 122.5708 | -122.2733 | -0.009155 | 0.059128 | 0.010854 | -0.0021255 | 0.030087 | -0.01446 | -0.0086901 | 0.017047 | 0.009155 | -0.16022 | 0.032043 | -0.013733 | 0.068665 | 0.1236 | -0.036621 | 0.09613 | -0.032043 | -0.059509 | 122.3053 | -0.15106 | 122.2824 | 122.2595 | 0.07782 | 122.2137 | -0.022888 | -0.022888 | 122.2366 | 122.3694 | 122.3419 | 122.113 | 122.2824 | 122.2412 | 122.3969 | 122.2137 | 122.113 | 122.2824 | 122.3969 | 122.3419 | 122.2412 | 0.041198 | -0.050354
1792.8438 | 122.5708 | -122.2687 | 0 | 0.11253 | 0.010641 | 0.0027877 | 0.036068 | -0.01211 | -0.010613 | 0.015552 | -0.13275 | -0.20599 | -0.068665 | -0.086975 | 0 | 0.032043 | -0.050354 | -0.12817 | 0.004578 | -0.15564 | 122.2 | -0.20599 | 122.1359 | 122.1817 | 0 | 122.113 | 0.004578 | -0.064086 | 122.2183 | 122.1405 | 122.2687 | 122.0627 | 122.1359 | 122.2733 | 122.3007 | 122.113 | 122.0627 | 122.1359 | 122.3007 | 122.2687 | 122.2733 | -0.068665 | -0.15564
1794.5469 | 122.5708 | -122.2778 | -0.018311 | 0.097275 | 0.0089316 | -0.0014847 | 0.036282 | -0.012751 | -0.0097583 | 0.01897 | -0.1236 | -0.2243 | -0.09613 | -0.07782 | 0.004578 | 0.050354 | -0.073242 | -0.091553 | -0.009155 | -0.15564 | 122.1817 | -0.20599 | 122.1542 | 122.2 | 0.022889 | 122.1222 | 0.009156 | -0.027466 | 122.2046 | 122.1863 | 122.2824 | 122.0535 | 122.1542 | 122.2687 | 122.3282 | 122.1222 | 122.0535 | 122.1542 | 122.3282 | 122.2824 | 122.2687 | -0.077819 | -0.13733
1796.2812 | 122.5388 | -122.2687 | 0.009155 | 0.16594 | 0.009786 | 0.0017197 | 0.032436 | -0.011897 | -0.0089037 | 0.018115 | -0.009155 | -0.23804 | -0.018311 | 0.032043 | 0.11444 | 0.16937 | -0.19684 | 0.064087 | -0.054932 | -0.11444 | 122.2504 | -0.24719 | 122.2595 | 122.3007 | 0.10529 | 122.1542 | -0.064087 | 0.009156 | 122.0718 | 122.3328 | 122.3831 | 122.0306 | 122.2595 | 122.2137 | 122.438 | 122.1542 | 122.0306 | 122.2595 | 122.438 | 122.3831 | 122.2137 | -0.027466 | -0.1236
1797.9844 | 122.5891 | -122.2733 | 0 | 0.051498 | 0.0089316 | -0.00084389 | 0.030514 | -0.01446 | -0.0076221 | 0.019397 | 0.004578 | -0.14191 | 0.054932 | -0.018311 | 0.068665 | 0.12817 | -0.013733 | 0.10071 | -0.050354 | -0.041199 | 122.3282 | -0.14191 | 122.2778 | 122.2549 | 0.068665 | 122.2321 | -0.050354 | -0.050354 | 122.2595 | 122.374 | 122.3419 | 122.1313 | 122.2778 | 122.2229 | 122.4014 | 122.2321 | 122.1313 | 122.2778 | 122.4014 | 122.3419 | 122.2229 | 0.054932 | -0.041199
1799.6875 | 122.5433 | -122.3007 | 0.004578 | -0.070572 | 0.0091452 | -0.00020289 | 0.030514 | -0.013392 | -0.010186 | 0.017902 | 0.12817 | -0.059509 | 0.12817 | 0.032043 | 0.10529 | 0.15564 | 0.036621 | 0.25177 | -0.064087 | 0.050354 | 122.4289 | -0.064087 | 122.4289 | 122.3328 | 0.10071 | 122.3511 | -0.068665 | 0 | 122.3373 | 122.5525 | 122.406 | 122.2412 | 122.4289 | 122.2366 | 122.4564 | 122.3511 | 122.2412 | 122.4289 | 122.4564 | 122.406 | 122.2366 | 0.1236 | 0.045776
1801.375 | 122.4655 | -122.3511 | 0.032043 | -0.21553 | 0.008077 | -0.0010575 | 0.031368 | -0.013392 | -0.0078357 | 0.016193 | 0.19226 | -0.027466 | 0.16479 | 0.064087 | 0.11902 | 0.16937 | 0.068665 | 0.31586 | -0.054932 | 0.059509 | 122.5159 | -0.059509 | 122.5433 | 122.4152 | 0.086976 | 122.4106 | -0.086975 | 0.027466 | 122.4197 | 122.6669 | 122.4701 | 122.3236 | 122.5433 | 122.2961 | 122.5204 | 122.4106 | 122.3236 | 122.5433 | 122.5204 | 122.4701 | 122.2961 | 0.13275 | 0.027466
1803.0625 | 122.5571 | -122.3007 | 0.009155 | 0.089645 | 0.010213 | 0.0025741 | 0.033932 | -0.014674 | -0.0091173 | 0.017474 | 0.009155 | -0.21057 | -0.004578 | 0.032043 | 0.09613 | 0.15106 | -0.15564 | 0.07782 | -0.054932 | -0.09613 | 122.2961 | -0.21973 | 122.3099 | 122.3328 | 0.086975 | 122.2046 | -0.064087 | 0.013733 | 122.1451 | 122.3785 | 122.3969 | 122.0901 | 122.3099 | 122.2458 | 122.4518 | 122.2046 | 122.0901 | 122.3099 | 122.4518 | 122.3969 | 122.2458 | -0.013733 | -0.10528
1804.7656 | 122.4792 | -122.3236 | 0.013733 | 0.013352 | 0.008077 | 0.0064193 | 0.037777 | -0.012538 | -0.013817 | 0.015979 | -0.045776 | -0.16479 | -0.041199 | -0.036621 | 0.013733 | 0.032043 | -0.004578 | -0.054932 | -0.022888 | -0.073242 | 122.2824 | -0.17853 | 122.2778 | 122.287 | 0 | 122.2504 | -0.036621 | -0.004577 | 122.319 | 122.2687 | 122.3373 | 122.1588 | 122.2778 | 122.3007 | 122.3557 | 122.2504 | 122.1588 | 122.2778 | 122.3557 | 122.3373 | 122.3007 | -0.054932 | -0.086975
1806.4844 | 122.4518 | -122.3236 | 0.013733 | -0.085831 | 0.01235 | -0.00084389 | 0.037777 | -0.013392 | -0.012749 | 0.015125 | 0.018311 | -0.11444 | 0.018311 | 0.009155 | 0.054932 | 0.086975 | 0.009155 | 0.054932 | 0 | -0.050354 | 122.3419 | -0.12817 | 122.3419 | 122.3328 | 0.041199 | 122.2733 | -0.013733 | 0 | 122.3328 | 122.3785 | 122.3785 | 122.2092 | 122.3419 | 122.3236 | 122.4106 | 122.2733 | 122.2092 | 122.3419 | 122.4106 | 122.3785 | 122.3236 | 0.004578 | -0.064087
1808.1719 | 122.5937 | -122.3007 | -0.004578 | 0.082016 | 0.0065816 | -0.00041649 | 0.02795 | -0.013606 | -0.0078357 | 0.016406 | -0.013733 | -0.17853 | 0.022888 | -0.013733 | 0.073242 | 0.13275 | -0.064087 | 0.09613 | -0.027466 | -0.086975 | 122.3236 | -0.17395 | 122.287 | 122.287 | 0.07782 | 122.2137 | -0.022888 | -0.036621 | 122.2366 | 122.3969 | 122.374 | 122.1222 | 122.287 | 122.2733 | 122.4335 | 122.2137 | 122.1222 | 122.287 | 122.4335 | 122.374 | 122.2733 | 0.027466 | -0.082397
1809.875 | 122.493 | -122.3236 | 0.018311 | -0.14687 | 0.0091452 | -0.0012711 | 0.032436 | -0.014033 | -0.010186 | 0.018115 | 0.041199 | -0.009155 | 0.091553 | -0.041199 | 0.018311 | 0.045776 | 0.17853 | 0.11902 | -0.004578 | 0.013733 | 122.4152 | -0.027466 | 122.3648 | 122.2824 | 0 | 122.3373 | -0.022889 | -0.050354 | 122.5021 | 122.4426 | 122.3419 | 122.3145 | 122.3648 | 122.319 | 122.3694 | 122.3373 | 122.3145 | 122.3648 | 122.3694 | 122.3419 | 122.319 | 0.073242 | -0.004578
1811.5781 | 122.4609 | -122.3373 | 0.009155 | -0.13924 | 0.0099996 | 0.00065151 | 0.036923 | -0.01446 | -0.010399 | 0.017902 | 0.059509 | -0.041199 | 0.10529 | -0.018311 | 0.036621 | 0.07782 | 0.10529 | 0.11444 | -0.013733 | 0 | 122.4426 | -0.050354 | 122.3969 | 122.319 | 0.027466 | 122.3373 | -0.022888 | -0.045777 | 122.4426 | 122.4518 | 122.374 | 122.2961 | 122.3969 | 122.3236 | 122.4152 | 122.3373 | 122.2961 | 122.3969 | 122.4152 | 122.374 | 122.3236 | 0.096131 | -0.009155
1813.2969 | 122.4609 | -122.3602 | 0.036621 | -0.18501 | 0.011281 | 1.071e-05 | 0.029232 | -0.01446 | -0.0097583 | 0.017261 | 0.20599 | -0.022888 | 0.20142 | 0.064087 | 0.1236 | 0.17395 | 0.086975 | 0.3067 | -0.045776 | 0.059509 | 122.5616 | -0.059509 | 122.5662 | 122.4243 | 0.086975 | 122.4197 | -0.082397 | 0.004578 | 122.4472 | 122.6669 | 122.4838 | 122.3373 | 122.5662 | 122.3145 | 122.5342 | 122.4197 | 122.3373 | 122.5662 | 122.5342 | 122.4838 | 122.3145 | 0.1648 | 0.022888
1815 | 122.5983 | -122.2824 | -0.004578 | 0.02861 | 0.0099996 | -0.0053299 | 0.029873 | -0.014887 | -0.0071947 | 0.015552 | 0.045776 | -0.10071 | 0.086975 | -0.013733 | 0.064087 | 0.10986 | 0.009155 | 0.11444 | -0.041199 | -0.022888 | 122.3694 | -0.09613 | 122.3282 | 122.2687 | 0.068665 | 122.2595 | -0.036621 | -0.041199 | 122.2916 | 122.3969 | 122.3465 | 122.1817 | 122.3282 | 122.2412 | 122.3923 | 122.2595 | 122.1817 | 122.3282 | 122.3923 | 122.3465 | 122.2412 | 0.091553 | -0.01831
1816.7188 | 122.5845 | -122.3145 | 0.009155 | -0.017166 | 0.010854 | -0.0014847 | 0.032009 | -0.015742 | -0.0089037 | 0.014056 | 0.10529 | -0.07782 | 0.10529 | 0.018311 | 0.10529 | 0.14191 | 0.041199 | 0.21057 | -0.041199 | -0.013733 | 122.4197 | -0.086975 | 122.4197 | 122.3328 | 0.096131 | 122.3007 | -0.050354 | 0 | 122.3557 | 122.525 | 122.4197 | 122.2366 | 122.4197 | 122.2733 | 122.4564 | 122.3007 | 122.2366 | 122.4197 | 122.4564 | 122.4197 | 122.2733 | 0.096131 | -0.022888
1818.4688 | 122.4747 | -122.3373 | 0.036621 | -0.070572 | 0.010854 | -0.00041649 | 0.039486 | -0.01211 | -0.0095447 | 0.015765 | 0.027466 | -0.10529 | 0.018311 | 0.004578 | 0.064087 | 0.086975 | 0.045776 | 0.07782 | -0.013733 | -0.032043 | 122.3557 | -0.14191 | 122.3648 | 122.3419 | 0.027466 | 122.3053 | -0.050354 | 0.009155 | 122.3831 | 122.4152 | 122.4014 | 122.2321 | 122.3648 | 122.3236 | 122.4243 | 122.3053 | 122.2321 | 122.3648 | 122.4243 | 122.4014 | 122.3236 | -0.01831 | -0.068664
1820.1719 | 122.4792 | -122.3282 | 0.032043 | -0.11635 | 0.01299 | 0.0030013 | 0.030941 | -0.016169 | -0.0069811 | 0.018115 | 0.19226 | -0.018311 | 0.16479 | 0.073242 | 0.15106 | 0.17395 | 0.032043 | 0.29755 | -0.059509 | 0.050354 | 122.493 | -0.050354 | 122.5204 | 122.4014 | 0.11902 | 122.3785 | -0.091552 | 0.027466 | 122.3602 | 122.6257 | 122.4792 | 122.3099 | 122.5204 | 122.2687 | 122.5021 | 122.3785 | 122.3099 | 122.5204 | 122.5021 | 122.4792 | 122.2687 | 0.13275 | 0.018311
1821.8594 | 122.525 | -122.319 | 0.013733 | -0.2079 | 0.010427 | -0.0061843 | 0.034359 | -0.014247 | -0.0089037 | 0.015979 | 0.07782 | 0.018311 | 0.11902 | -0.059509 | 0.013733 | 0.036621 | 0.25177 | 0.14648 | 0 | 0.045776 | 122.438 | 0.004578 | 122.3969 | 122.2595 | 0 | 122.3648 | -0.013733 | -0.041199 | 122.5708 | 122.4655 | 122.3328 | 122.3373 | 122.3969 | 122.319 | 122.3557 | 122.3648 | 122.3373 | 122.3969 | 122.3557 | 122.3328 | 122.319 | 0.10529 | 0.032043
1823.6562 | 122.4792 | -122.3328 | 0.032043 | -0.14687 | 0.0065816 | 1.071e-05 | 0.037136 | -0.014033 | -0.010826 | 0.017261 | 0.054932 | -0.036621 | 0.11444 | -0.022888 | 0.045776 | 0.073242 | 0.12817 | 0.1236 | -0.013733 | 0.004578 | 122.4472 | -0.068664 | 122.3877 | 122.3099 | 0.013733 | 122.3373 | -0.045776 | -0.059509 | 122.4609 | 122.4564 | 122.3785 | 122.2961 | 122.3877 | 122.319 | 122.406 | 122.3373 | 122.2961 | 122.3877 | 122.406 | 122.3785 | 122.319 | 0.082398 | -0.027465
1825.375 | 122.5525 | -122.3145 | 0 | 0.17357 | 0.0089316 | 0.0019333 | 0.032864 | -0.010188 | -0.0069811 | 0.017474 | -0.018311 | -0.24719 | -0.032043 | 0.045776 | 0.10986 | 0.16022 | -0.21057 | 0.036621 | -0.059509 | -0.11444 | 122.2824 | -0.24719 | 122.2961 | 122.3602 | 0.10986 | 122.2 | -0.059509 | 0.013732 | 122.1039 | 122.3511 | 122.4243 | 122.0673 | 122.2961 | 122.2549 | 122.4747 | 122.2 | 122.0673 | 122.2961 | 122.4747 | 122.4243 | 122.2549 | -0.032043 | -0.11444
1827.0625 | 122.5159 | -122.3328 | 0.027466 | -0.18501 | 0.0089316 | 0.00065151 | 0.034786 | -0.015956 | -0.0093311 | 0.01897 | 0.059509 | 0.009155 | 0.11902 | -0.073242 | 0.032043 | 0.027466 | 0.20142 | 0.11902 | -0.018311 | 0.018311 | 122.4518 | -0.018311 | 122.3923 | 122.2595 | 0.004577 | 122.3511 | -0.045777 | -0.05951 | 122.5342 | 122.4518 | 122.3648 | 122.3419 | 122.3923 | 122.3145 | 122.3602 | 122.3511 | 122.3419 | 122.3923 | 122.3602 | 122.3648 | 122.3145 | 0.091553 | -0.009155
1828.75 | 122.5159 | -122.3236 | 0.013733 | -0.18501 | 0.0091452 | 0.0027877 | 0.031582 | -0.014033 | -0.0099719 | 0.018329 | 0.11902 | 0.032043 | 0.17853 | -0.022888 | 0.032043 | 0.045776 | 0.22888 | 0.17853 | -0.004578 | 0.045776 | 122.5021 | 0.01831 | 122.4426 | 122.3007 | 0.01831 | 122.3694 | -0.018311 | -0.059509 | 122.5525 | 122.5021 | 122.3557 | 122.3557 | 122.4426 | 122.319 | 122.3694 | 122.3694 | 122.3557 | 122.4426 | 122.3694 | 122.3557 | 122.319 | 0.16479 | 0.032043
1830.4531 | 122.5113 | -122.3282 | 0.036621 | -0.19264 | 0.0076498 | 0.0042831 | 0.031155 | -0.01446 | -0.0091173 | 0.016406 | 0.14191 | 0 | 0.15106 | -0.027466 | 0.054932 | 0.068665 | 0.2243 | 0.19684 | 0 | 0.032043 | 122.4792 | -0.036621 | 122.4701 | 122.3007 | 0.018311 | 122.3602 | -0.036621 | -0.009155 | 122.5525 | 122.525 | 122.3831 | 122.3282 | 122.4701 | 122.3282 | 122.3969 | 122.3602 | 122.3282 | 122.4701 | 122.3969 | 122.3831 | 122.3282 | 0.11444 | -0.004578
1832.1719 | 122.4609 | -122.3419 | 0.036621 | -0.10872 | 0.010213 | 0.00022431 | 0.034786 | -0.014674 | -0.011254 | 0.019183 | 0.059509 | -0.064087 | 0.073242 | 0.004578 | 0.059509 | 0.086975 | 0.082397 | 0.10071 | -0.004578 | -0.018311 | 122.4152 | -0.10071 | 122.4014 | 122.3465 | 0.022888 | 122.3236 | -0.041199 | -0.013733 | 122.4243 | 122.4426 | 122.4014 | 122.2778 | 122.4014 | 122.3373 | 122.4289 | 122.3236 | 122.2778 | 122.4014 | 122.4289 | 122.4014 | 122.3373 | 0.036621 | -0.054932
1833.9219 | 122.5662 | -122.319 | -0.009155 | 0.17357 | 0.010854 | -0.0010575 | 0.032436 | -0.010829 | -0.011254 | 0.018756 | -0.091553 | -0.23804 | -0.059509 | 0.009155 | 0.073242 | 0.11444 | -0.17395 | -0.027466 | -0.027466 | -0.10529 | 122.2595 | -0.22888 | 122.2275 | 122.3282 | 0.082397 | 122.2137 | -0.018311 | -0.032044 | 122.1451 | 122.2916 | 122.3923 | 122.081 | 122.2275 | 122.2916 | 122.4335 | 122.2137 | 122.081 | 122.2275 | 122.4335 | 122.3923 | 122.2916 | -0.050354 | -0.096131
1835.6094 | 122.525 | -122.3465 | 0.045776 | -0.24605 | 0.010641 | -0.0027665 | 0.033291 | -0.015315 | -0.0086901 | 0.017047 | 0.14648 | 0 | 0.18768 | 0.013733 | 0.07782 | 0.10529 | 0.18768 | 0.26093 | -0.036621 | 0.036621 | 122.5342 | -0.045776 | 122.493 | 122.3602 | 0.032044 | 122.3831 | -0.082397 | -0.041199 | 122.5342 | 122.6074 | 122.4243 | 122.3465 | 122.493 | 122.3099 | 122.4518 | 122.3831 | 122.3465 | 122.493 | 122.4518 | 122.4243 | 122.3099 | 0.14191 | -0.009155
1837.3125 | 122.4792 | -122.3419 | 0.022888 | -0.047684 | 0.0093588 | 0.00065151 | 0.036709 | -0.012324 | -0.012322 | 0.01662 | 0.018311 | -0.12817 | 0.004578 | -0.004578 | 0.050354 | 0.091553 | 0.032043 | 0.054932 | -0.018311 | -0.059509 | 122.3465 | -0.15106 | 122.3602 | 122.3373 | 0.027466 | 122.2824 | -0.041199 | 0.013733 | 122.374 | 122.3969 | 122.3923 | 122.2137 | 122.3602 | 122.3236 | 122.4335 | 122.2824 | 122.2137 | 122.3602 | 122.4335 | 122.3923 | 122.3236 | -0.01831 | -0.082397
1839.0156 | 122.5754 | -122.3328 | -0.004578 | 0.1812 | 0.0093588 | 0.0010787 | 0.0303 | -0.01211 | -0.0097583 | 0.016406 | -0.022888 | -0.24261 | -0.022888 | 0.041199 | 0.12817 | 0.17395 | -0.21057 | 0.054932 | -0.045776 | -0.09613 | 122.3099 | -0.23804 | 122.3099 | 122.374 | 0.13275 | 122.2366 | -0.041198 | 0 | 122.1222 | 122.3877 | 122.4609 | 122.0901 | 122.3099 | 122.287 | 122.5067 | 122.2366 | 122.0901 | 122.3099 | 122.5067 | 122.4609 | 122.287 | -0.01831 | -0.091552
1840.7031 | 122.5571 | -122.3328 | 0.022888 | 0.059128 | 0.0089316 | 0.00086511 | 0.034786 | -0.012965 | -0.012749 | 0.018543 | -0.11444 | -0.17853 | -0.064087 | -0.073242 | -0.018311 | 0.022888 | 0.004578 | -0.082397 | -0.009155 | -0.1236 | 122.2687 | -0.20142 | 122.2183 | 122.2595 | -0.041199 | 122.2092 | -0.032043 | -0.050354 | 122.3373 | 122.2504 | 122.3145 | 122.1542 | 122.2183 | 122.3236 | 122.3557 | 122.2092 | 122.1542 | 122.2183 | 122.3557 | 122.3145 | 122.3236 | -0.086975 | -0.14648
1842.4219 | 122.6212 | -122.3099 | -0.018311 | 0.020981 | 0.010854 | -0.0014847 | 0.026669 | -0.014887 | -0.0074085 | 0.017474 | 0.059509 | -0.10529 | 0.07782 | -0.027466 | 0.068665 | 0.10986 | 0.036621 | 0.13733 | -0.036621 | -0.041199 | 122.3877 | -0.086975 | 122.3694 | 122.2824 | 0.086976 | 122.2687 | -0.01831 | -0.018311 | 122.3465 | 122.4472 | 122.3785 | 122.2046 | 122.3694 | 122.2733 | 122.4197 | 122.2687 | 122.2046 | 122.3694 | 122.4197 | 122.3785 | 122.2733 | 0.096131 | -0.022888
1844.125 | 122.4838 | -122.3602 | 0.027466 | -0.17738 | 0.0078634 | -0.0027665 | 0.032009 | -0.015742 | -0.011254 | 0.015125 | 0.19684 | -0.009155 | 0.18768 | 0.050354 | 0.11444 | 0.14648 | 0.13275 | 0.30212 | -0.041199 | 0.07782 | 122.5479 | -0.036621 | 122.5571 | 122.4106 | 0.086975 | 122.438 | -0.068665 | 0.009155 | 122.493 | 122.6624 | 122.4747 | 122.3511 | 122.5571 | 122.319 | 122.5067 | 122.438 | 122.3511 | 122.5571 | 122.5067 | 122.4747 | 122.319 | 0.16022 | 0.050354
1845.8594 | 122.5296 | -122.3465 | 0.018311 | -0.24605 | 0.011281 | 0.0010787 | 0.035427 | -0.015315 | -0.0091173 | 0.017688 | 0.073242 | 0.009155 | 0.13733 | -0.091553 | 0.004578 | 0.032043 | 0.2655 | 0.14191 | -0.009155 | 0.032043 | 122.4838 | -0.009156 | 122.4197 | 122.2549 | -0.013733 | 122.3785 | -0.027466 | -0.064087 | 122.612 | 122.4884 | 122.3511 | 122.3557 | 122.4197 | 122.3373 | 122.3785 | 122.3785 | 122.3557 | 122.4197 | 122.3785 | 122.3511 | 122.3373 | 0.11902 | 0.013732
1847.5625 | 122.493 | -122.3373 | 0.036621 | -0.16212 | 0.0089316 | 0.0021469 | 0.035 | -0.013606 | -0.0097583 | 0.017902 | 0.073242 | -0.036621 | 0.07782 | -0.032043 | 0.036621 | 0.073242 | 0.16937 | 0.11902 | 0.004578 | 0.004578 | 122.4152 | -0.073242 | 122.4106 | 122.3053 | 0 | 122.3419 | -0.032043 | -0.004578 | 122.5067 | 122.4564 | 122.374 | 122.3007 | 122.4106 | 122.3419 | 122.4106 | 122.3419 | 122.3007 | 122.4106 | 122.4106 | 122.374 | 122.3419 | 0.041199 | -0.032043
1849.2812 | 122.6074 | -122.3053 | 0.004578 | 0.12779 | 0.011068 | 0.0044967 | 0.033932 | -0.014033 | -0.0093311 | 0.018543 | -0.13275 | -0.21515 | -0.091553 | -0.068665 | 0.013733 | 0.064087 | -0.036621 | -0.082397 | -0.018311 | -0.13275 | 122.2137 | -0.21973 | 122.1725 | 122.2366 | 0.009155 | 122.1725 | -0.022889 | -0.041198 | 122.2687 | 122.2229 | 122.319 | 122.0901 | 122.1725 | 122.287 | 122.3694 | 122.1725 | 122.0901 | 122.1725 | 122.3694 | 122.319 | 122.287 | -0.096131 | -0.13733
1851 | 122.5708 | -122.3419 | -0.009155 | 0.18883 | 0.0099996 | 0.00086511 | 0.033291 | -0.014033 | -0.0086901 | 0.018756 | -0.013733 | -0.23346 | -0.018311 | 0.054932 | 0.13275 | 0.15106 | -0.17853 | 0.064087 | -0.045776 | -0.10986 | 122.3236 | -0.2243 | 122.3282 | 122.3969 | 0.14191 | 122.2321 | -0.036621 | 0.004578 | 122.1634 | 122.406 | 122.4747 | 122.1085 | 122.3282 | 122.2961 | 122.493 | 122.2321 | 122.1085 | 122.3282 | 122.493 | 122.4747 | 122.2961 | -0.009156 | -0.10071
1852.6875 | 122.6395 | -122.3236 | -0.004578 | 0.12016 | 0.0078634 | -0.00041649 | 0.034573 | -0.015528 | -0.0091173 | 0.015552 | -0.15564 | -0.21057 | -0.086975 | -0.07782 | -0.013733 | 0.036621 | -0.009155 | -0.11444 | -0.022888 | -0.14191 | 122.2366 | -0.20599 | 122.168 | 122.2458 | -0.009155 | 122.1817 | -0.01831 | -0.068665 | 122.3145 | 122.2092 | 122.3099 | 122.113 | 122.168 | 122.3007 | 122.3602 | 122.1817 | 122.113 | 122.168 | 122.3602 | 122.3099 | 122.3007 | -0.082397 | -0.13733
1854.4062 | 122.58 | -122.3419 | 0.018311 | 0.14305 | 0.0093588 | 1.071e-05 | 0.029232 | -0.014674 | -0.012108 | 0.017261 | -0.013733 | -0.24719 | -0.013733 | 0.041199 | 0.10986 | 0.17853 | -0.13275 | 0.073242 | -0.045776 | -0.10986 | 122.3282 | -0.2655 | 122.3282 | 122.3831 | 0.091552 | 122.2321 | -0.064087 | 0 | 122.2092 | 122.4152 | 122.4518 | 122.0947 | 122.3282 | 122.2961 | 122.5204 | 122.2321 | 122.0947 | 122.3282 | 122.5204 | 122.4518 | 122.2961 | -0.032044 | -0.12817
1856.0938 | 122.6028 | -122.3557 | 0.027466 | 0.089645 | 0.0095724 | 1.071e-05 | 0.030087 | -0.013819 | -0.0084765 | 0.019611 | -0.027466 | -0.21515 | -0.027466 | 0.018311 | 0.09613 | 0.15106 | -0.09613 | 0.086975 | -0.050354 | -0.10986 | 122.3282 | -0.24261 | 122.3282 | 122.374 | 0.068664 | 122.2458 | -0.07782 | 0 | 122.2595 | 122.4426 | 122.4518 | 122.1405 | 122.3282 | 122.3053 | 122.5067 | 122.2458 | 122.1405 | 122.3282 | 122.5067 | 122.4518 | 122.3053 | -0.054932 | -0.13733
1857.7969 | 122.5433 | -122.3648 | 0.027466 | -0.24605 | 0.010854 | -0.0034073 | 0.031796 | -0.013606 | -0.010613 | 0.015765 | 0.16022 | 0.009155 | 0.1831 | -0.009155 | 0.064087 | 0.09613 | 0.23346 | 0.24719 | -0.027466 | 0.036621 | 122.5479 | -0.018311 | 122.525 | 122.3557 | 0.036621 | 122.4014 | -0.054932 | -0.022888 | 122.5983 | 122.612 | 122.4289 | 122.374 | 122.525 | 122.3373 | 122.4609 | 122.4014 | 122.374 | 122.525 | 122.4609 | 122.4289 | 122.3373 | 0.15564 | 0.009155
1859.5 | 122.5113 | -122.3602 | 0.032043 | -0.032425 | 0.0099996 | 0.0030013 | 0.038418 | -0.013819 | -0.013817 | 0.016193 | -0.018311 | -0.15106 | -0.022888 | -0.036621 | 0.027466 | 0.059509 | 0.050354 | -0.009155 | -0.009155 | -0.07782 | 122.3373 | -0.18311 | 122.3419 | 122.3236 | -0.004577 | 122.2824 | -0.041198 | 0.004577 | 122.4106 | 122.3511 | 122.3877 | 122.2092 | 122.3419 | 122.3511 | 122.4197 | 122.2824 | 122.2092 | 122.3419 | 122.4197 | 122.3877 | 122.3511 | -0.054931 | -0.10986
1861.1875 | 122.6349 | -122.3236 | -0.004578 | 0.12016 | 0.008718 | -0.00041649 | 0.033932 | -0.014674 | -0.0099719 | 0.016193 | -0.14191 | -0.21057 | -0.073242 | -0.091553 | -0.013733 | 0.022888 | 0.022888 | -0.10986 | 0.009155 | -0.14648 | 122.2504 | -0.20599 | 122.1817 | 122.2321 | -0.009155 | 122.1771 | 0.013733 | -0.068665 | 122.3465 | 122.2137 | 122.3099 | 122.113 | 122.1817 | 122.3328 | 122.3465 | 122.1771 | 122.113 | 122.1817 | 122.3465 | 122.3099 | 122.3328 | -0.068664 | -0.14191
1862.9375 | 122.5891 | -122.3465 | 0 | 0.066757 | 0.0091452 | 0.0010787 | 0.034359 | -0.012324 | -0.010613 | 0.01662 | -0.14648 | -0.18768 | -0.068665 | -0.082397 | -0.027466 | 0.032043 | 0.09613 | -0.091553 | -0.004578 | -0.1236 | 122.2778 | -0.18768 | 122.2 | 122.2641 | -0.027466 | 122.2229 | -0.004578 | -0.077819 | 122.4426 | 122.2549 | 122.319 | 122.1588 | 122.2 | 122.3419 | 122.3785 | 122.2229 | 122.1588 | 122.2 | 122.3785 | 122.319 | 122.3419 | -0.068665 | -0.1236
1864.625 | 122.5845 | -122.3557 | 0.004578 | 0.12779 | 0.010427 | 0.0032151 | 0.029018 | -0.013392 | -0.01104 | 0.017047 | -0.018311 | -0.24719 | -0.027466 | 0.036621 | 0.1236 | 0.16937 | -0.13275 | 0.064087 | -0.068665 | -0.10071 | 122.3282 | -0.25177 | 122.3373 | 122.3923 | 0.11902 | 122.2549 | -0.073243 | 0.009155 | 122.2229 | 122.4197 | 122.4792 | 122.1085 | 122.3373 | 122.287 | 122.525 | 122.2549 | 122.1085 | 122.3373 | 122.525 | 122.4792 | 122.287 | -0.032044 | -0.10529
1866.3125 | 122.5525 | -122.374 | 0.032043 | -0.17738 | 0.0095724 | -0.0021255 | 0.032223 | -0.013392 | -0.010399 | 0.017688 | 0.064087 | 0.013733 | 0.11902 | -0.059509 | 0.004578 | 0.045776 | 0.27466 | 0.13733 | 0.004578 | 0.022888 | 122.493 | -0.01831 | 122.438 | 122.3145 | -0.027465 | 122.3969 | -0.027465 | -0.054932 | 122.6486 | 122.5113 | 122.3785 | 122.3877 | 122.438 | 122.3785 | 122.4197 | 122.3969 | 122.3877 | 122.438 | 122.4197 | 122.3785 | 122.3785 | 0.086976 | -0.009155
1868.0156 | 122.6715 | -122.3419 | 0.004578 | 0.02861 | 0.0099996 | -0.0014847 | 0.028164 | -0.014887 | -0.0061267 | 0.01662 | 0.018311 | -0.13275 | 0.068665 | -0.036621 | 0.068665 | 0.12817 | 0.059509 | 0.10986 | -0.050354 | -0.022888 | 122.4106 | -0.13733 | 122.3602 | 122.3053 | 0.064087 | 122.319 | -0.054932 | -0.050354 | 122.4014 | 122.4518 | 122.4106 | 122.2092 | 122.3602 | 122.2916 | 122.4701 | 122.319 | 122.2092 | 122.3602 | 122.4701 | 122.4106 | 122.2916 | 0.064087 | -0.027466
1869.7656 | 122.6486 | -122.319 | -0.009155 | 0.03624 | 0.010427 | -0.0010575 | 0.029873 | -0.013606 | -0.0091173 | 0.014056 | 0.036621 | -0.10529 | 0.091553 | -0.013733 | 0.068665 | 0.10986 | 0.050354 | 0.11902 | -0.027466 | -0.036621 | 122.4106 | -0.096131 | 122.3557 | 122.3053 | 0.07782 | 122.2824 | -0.018311 | -0.054932 | 122.3694 | 122.438 | 122.3877 | 122.2137 | 122.3557 | 122.2916 | 122.4289 | 122.2824 | 122.2137 | 122.3557 | 122.4289 | 122.3877 | 122.2916 | 0.10071 | -0.027466
1871.5312 | 122.6166 | -122.3557 | 0.022888 | 0.089645 | 0.0093588 | 0.00065151 | 0.03265 | -0.012538 | -0.010399 | 0.017261 | 0 | -0.20599 | 0 | 0.022888 | 0.10986 | 0.15106 | -0.064087 | 0.073242 | -0.059509 | -0.091553 | 122.3557 | -0.22888 | 122.3557 | 122.3785 | 0.086975 | 122.2641 | -0.082397 | 0 | 122.2916 | 122.4289 | 122.4655 | 122.1497 | 122.3557 | 122.2961 | 122.5067 | 122.2641 | 122.1497 | 122.3557 | 122.5067 | 122.4655 | 122.2961 | -0.022888 | -0.11444
1873.25 | 122.6532 | -122.3511 | -0.013733 | 0.03624 | 0.0082906 | 0.00043791 | 0.031796 | -0.01681 | -0.0074085 | 0.017047 | 0.013733 | -0.12817 | 0.064087 | -0.009155 | 0.064087 | 0.11902 | 0.09613 | 0.13275 | -0.041199 | -0.041199 | 122.4152 | -0.11444 | 122.3648 | 122.3419 | 0.07782 | 122.3099 | -0.027466 | -0.050354 | 122.4472 | 122.4838 | 122.4152 | 122.2229 | 122.3648 | 122.3099 | 122.4701 | 122.3099 | 122.2229 | 122.3648 | 122.4701 | 122.4152 | 122.3099 | 0.07782 | -0.027466
1875 | 122.5571 | -122.3831 | 0.027466 | -0.09346 | 0.0089316 | 0.0017197 | 0.030941 | -0.015101 | -0.0074085 | 0.014911 | 0.16479 | -0.045776 | 0.15106 | 0.041199 | 0.1236 | 0.17853 | 0.12817 | 0.31128 | -0.064087 | 0.027466 | 122.5342 | -0.073242 | 122.5479 | 122.4243 | 0.09613 | 122.4106 | -0.091553 | 0.013733 | 122.5113 | 122.6944 | 122.5067 | 122.3373 | 122.5479 | 122.319 | 122.5616 | 122.4106 | 122.3373 | 122.5479 | 122.5616 | 122.5067 | 122.319 | 0.1236 | 0
1876.7031 | 122.4976 | -122.4106 | 0.022888 | -0.13924 | 0.0085042 | -0.0023391 | 0.033505 | -0.015528 | -0.011254 | 0.017902 | 0.20142 | -0.027466 | 0.17853 | 0.07782 | 0.13275 | 0.16022 | 0.16022 | 0.32044 | -0.027466 | 0.059509 | 122.5891 | -0.050354 | 122.612 | 122.4884 | 0.10986 | 122.4701 | -0.050354 | 0.022888 | 122.5708 | 122.731 | 122.5433 | 122.3831 | 122.612 | 122.3831 | 122.5708 | 122.4701 | 122.3831 | 122.612 | 122.5708 | 122.5433 | 122.3831 | 0.15564 | 0.036621
1878.4844 | 122.5983 | -122.3373 | 0.004578 | 0.17357 | 0.0093588 | 0.0023605 | 0.036068 | -0.013606 | -0.011254 | 0.01662 | -0.022888 | -0.26093 | -0.032043 | 0.050354 | 0.10529 | 0.1831 | -0.09613 | 0.073242 | -0.041199 | -0.09613 | 122.3053 | -0.2655 | 122.3145 | 122.3877 | 0.10071 | 122.2412 | -0.045777 | 0.009155 | 122.2412 | 122.4106 | 122.4426 | 122.0764 | 122.3145 | 122.2961 | 122.5204 | 122.2412 | 122.0764 | 122.3145 | 122.5204 | 122.4426 | 122.2961 | -0.036621 | -0.10071
1880.1875 | 122.612 | -122.374 | 0.004578 | -0.017166 | 0.008718 | 0.00086511 | 0.032223 | -0.016383 | -0.0095447 | 0.017047 | 0.086975 | -0.10071 | 0.10529 | 0.018311 | 0.11444 | 0.15564 | 0.13275 | 0.23346 | -0.045776 | 0.018311 | 122.4792 | -0.10529 | 122.4609 | 122.3923 | 0.10986 | 122.3923 | -0.050354 | -0.018311 | 122.5067 | 122.6074 | 122.4884 | 122.2733 | 122.4609 | 122.3282 | 122.5296 | 122.3923 | 122.2733 | 122.4609 | 122.5296 | 122.4884 | 122.3282 | 0.10071 | 0.013733
1881.9219 | 122.6532 | -122.3373 | 0.009155 | 0.12016 | 0.0085042 | -0.0010575 | 0.037136 | -0.01446 | -0.010613 | 0.018329 | -0.12817 | -0.21057 | -0.086975 | -0.086975 | -0.018311 | 0.018311 | 0.068665 | -0.09613 | -0.009155 | -0.13275 | 122.2504 | -0.21973 | 122.2092 | 122.2504 | -0.027466 | 122.2046 | -0.01831 | -0.041199 | 122.406 | 122.2412 | 122.319 | 122.1268 | 122.2092 | 122.3282 | 122.3557 | 122.2046 | 122.1268 | 122.2092 | 122.3557 | 122.319 | 122.3282 | -0.09613 | -0.14191
1883.625 | 122.6257 | -122.3602 | -0.004578 | -0.032425 | 0.010213 | -0.00041649 | 0.029659 | -0.012751 | -0.0093311 | 0.017261 | 0.082397 | -0.086975 | 0.11444 | 0.022888 | 0.09613 | 0.14191 | 0.16479 | 0.21973 | -0.032043 | 0.013733 | 122.4747 | -0.082397 | 122.4426 | 122.3831 | 0.10071 | 122.374 | -0.027465 | -0.032044 | 122.525 | 122.58 | 122.4564 | 122.2733 | 122.4426 | 122.3282 | 122.5021 | 122.374 | 122.2733 | 122.4426 | 122.5021 | 122.4564 | 122.3282 | 0.11902 | 0.018311
1885.3594 | 122.6074 | -122.3602 | 0.004578 | 0.066757 | 0.011068 | 0.0012925 | 0.037563 | -0.010188 | -0.011467 | 0.016834 | -0.091553 | -0.16479 | -0.054932 | -0.054932 | -0.022888 | 0.022888 | 0.18768 | -0.068665 | 0.004578 | -0.10986 | 122.3053 | -0.16937 | 122.2687 | 122.3053 | -0.027466 | 122.2504 | 0 | -0.036621 | 122.5479 | 122.2916 | 122.3373 | 122.1954 | 122.2687 | 122.3648 | 122.3831 | 122.2504 | 122.1954 | 122.2687 | 122.3831 | 122.3373 | 122.3648 | -0.05951 | -0.11444
1887.0469 | 122.525 | -122.438 | 0.027466 | -0.16212 | 0.010641 | -0.0038345 | 0.029659 | -0.015101 | -0.0084765 | 0.016406 | 0.19226 | -0.041199 | 0.17853 | 0.064087 | 0.14191 | 0.16937 | 0.16937 | 0.32044 | -0.041199 | 0.045776 | 122.6166 | -0.068665 | 122.6303 | 122.5021 | 0.11444 | 122.4838 | -0.068665 | 0.013733 | 122.6074 | 122.7585 | 122.58 | 122.3969 | 122.6303 | 122.3969 | 122.6074 | 122.4838 | 122.3969 | 122.6303 | 122.6074 | 122.58 | 122.3969 | 0.15106 | 0.01831
1888.7188 | 122.5159 | -122.3785 | 0.022888 | -0.16212 | 0.0074362 | 0.0032151 | 0.034573 | -0.013606 | -0.0093311 | 0.01662 | 0.059509 | -0.032043 | 0.10986 | -0.004578 | 0.059509 | 0.064087 | 0.20142 | 0.13275 | -0.018311 | -0.004578 | 122.4884 | -0.054931 | 122.438 | 122.374 | 0.036621 | 122.374 | -0.041199 | -0.050354 | 122.58 | 122.5113 | 122.438 | 122.3465 | 122.438 | 122.3602 | 122.4426 | 122.374 | 122.3465 | 122.438 | 122.4426 | 122.438 | 122.3602 | 0.086975 | -0.027466
1890.4062 | 122.6486 | -122.3419 | 0 | -0.0095368 | 0.0093588 | 0.00086511 | 0.02795 | -0.014247 | -0.0089037 | 0.014697 | 0.068665 | -0.07782 | 0.10529 | 0 | 0.09613 | 0.13275 | 0.1236 | 0.17853 | -0.041199 | -0.013733 | 122.4472 | -0.07782 | 122.4106 | 122.3419 | 0.09613 | 122.3282 | -0.041199 | -0.036621 | 122.4655 | 122.5204 | 122.438 | 122.2641 | 122.4106 | 122.3007 | 122.4747 | 122.3282 | 122.2641 | 122.4106 | 122.4747 | 122.438 | 122.3007 | 0.10529 | -0.013733
1892.1094 | 122.5479 | -122.3923 | 0.027466 | -0.062942 | 0.010427 | 0.0044967 | 0.036923 | -0.01211 | -0.0091173 | 0.015552 | -0.013733 | -0.15564 | -0.027466 | -0.018311 | 0.050354 | 0.073242 | 0.11444 | 0.022888 | -0.004578 | -0.064087 | 122.3648 | -0.18311 | 122.3785 | 122.374 | 0.022888 | 122.3282 | -0.032044 | 0.013733 | 122.5067 | 122.4152 | 122.4426 | 122.2366 | 122.3785 | 122.3877 | 122.4655 | 122.3282 | 122.2366 | 122.3785 | 122.4655 | 122.4426 | 122.3877 | -0.054932 | -0.091553
1893.8906 | 122.6624 | -122.3465 | 0.004578 | 0.051498 | 0.0078634 | -0.0027665 | 0.027737 | -0.014674 | -0.01104 | 0.017047 | 0.013733 | -0.14191 | 0.050354 | -0.018311 | 0.07782 | 0.11444 | 0.073242 | 0.11902 | -0.041199 | -0.045776 | 122.3969 | -0.14649 | 122.3602 | 122.3282 | 0.073242 | 122.3007 | -0.045777 | -0.036621 | 122.4197 | 122.4655 | 122.4243 | 122.2046 | 122.3602 | 122.3053 | 122.4609 | 122.3007 | 122.2046 | 122.3602 | 122.4609 | 122.4243 | 122.3053 | 0.045776 | -0.050354
1895.5781 | 122.5296 | -122.406 | 0.036621 | -0.040054 | 0.0095724 | 0.0019333 | 0.035214 | -0.013606 | -0.0093311 | 0.019824 | 0 | -0.1236 | 0.009155 | 0 | 0.050354 | 0.068665 | 0.11444 | 0.050354 | -0.013733 | -0.07782 | 122.4152 | -0.16022 | 122.406 | 122.406 | 0.013733 | 122.3282 | -0.050354 | -0.009155 | 122.5204 | 122.4564 | 122.4564 | 122.2824 | 122.406 | 122.3923 | 122.4747 | 122.3282 | 122.2824 | 122.406 | 122.4747 | 122.4564 | 122.3923 | -0.027466 | -0.11444
1897.2969 | 122.5113 | -122.4243 | 0.018311 | -0.085831 | 0.0095724 | 0.0027877 | 0.032864 | -0.012751 | -0.0095447 | 0.015552 | 0.045776 | -0.091553 | 0.045776 | -0.013733 | 0.07782 | 0.082397 | 0.17853 | 0.10529 | -0.013733 | -0.032043 | 122.4701 | -0.10986 | 122.4701 | 122.4106 | 0.059509 | 122.3923 | -0.032044 | 0 | 122.6028 | 122.5296 | 122.5021 | 122.3328 | 122.4701 | 122.4106 | 122.5067 | 122.3923 | 122.3328 | 122.4701 | 122.5067 | 122.5021 | 122.4106 | 0.027465 | -0.050354
1899 | 122.5662 | -122.3923 | 0.018311 | 0.013352 | 0.0074362 | 0.0051377 | 0.033505 | -0.010829 | -0.01104 | 0.018115 | -0.050354 | -0.16022 | -0.022888 | -0.045776 | 0.009155 | 0.036621 | 0.12817 | -0.027466 | -0.013733 | -0.09613 | 122.3694 | -0.17853 | 122.3419 | 122.3465 | -0.009156 | 122.2961 | -0.032044 | -0.027466 | 122.5204 | 122.3648 | 122.4014 | 122.2321 | 122.3419 | 122.3785 | 122.4289 | 122.2961 | 122.2321 | 122.3419 | 122.4289 | 122.4014 | 122.3785 | -0.041199 | -0.11444
1900.6719 | 122.6669 | -122.3557 | 0.004578 | 0.013352 | 0.0082906 | 0.0027877 | 0.026882 | -0.012965 | -0.0065539 | 0.017261 | 0.041199 | -0.10529 | 0.082397 | -0.036621 | 0.086975 | 0.10986 | 0.15106 | 0.14191 | -0.036621 | -0.022888 | 122.438 | -0.10986 | 122.3969 | 122.319 | 0.082397 | 122.3328 | -0.041199 | -0.041198 | 122.5067 | 122.4976 | 122.4426 | 122.2504 | 122.3969 | 122.319 | 122.4655 | 122.3328 | 122.2504 | 122.3969 | 122.4655 | 122.4426 | 122.319 | 0.077819 | -0.027466
1902.375 | 122.5296 | -122.406 | 0.009155 | -0.16212 | 0.008718 | 0.0036423 | 0.035214 | -0.014033 | -0.010826 | 0.016834 | 0.050354 | -0.041199 | 0.10071 | -0.032043 | 0.045776 | 0.07782 | 0.23804 | 0.13275 | -0.004578 | 0.013733 | 122.5067 | -0.050354 | 122.4564 | 122.374 | 0.036621 | 122.4197 | -0.013733 | -0.050354 | 122.644 | 122.5388 | 122.4518 | 122.3648 | 122.4564 | 122.4014 | 122.4838 | 122.4197 | 122.3648 | 122.4564 | 122.4838 | 122.4518 | 122.4014 | 0.091553 | 0.004578
1904.0781 | 122.5845 | -122.374 | 0.004578 | -0.22316 | 0.010854 | -0.0014847 | 0.032864 | -0.013392 | -0.0082629 | 0.017474 | 0.068665 | 0.013733 | 0.12817 | -0.073242 | 0.004578 | 0.027466 | 0.33875 | 0.15564 | -0.004578 | 0.018311 | 122.5021 | 0.009155 | 122.4426 | 122.3007 | 0 | 122.3923 | -0.009156 | -0.059509 | 122.7127 | 122.5296 | 122.3785 | 122.3877 | 122.4426 | 122.3694 | 122.4014 | 122.3923 | 122.3877 | 122.4426 | 122.4014 | 122.3785 | 122.3694 | 0.1236 | 0.013733
1905.75 | 122.5433 | -122.4152 | 0.027466 | -0.024795 | 0.008718 | 0.0019333 | 0.035641 | -0.011469 | -0.012322 | 0.01662 | -0.032043 | -0.16479 | -0.022888 | -0.032043 | 0.032043 | 0.068665 | 0.16479 | 0.004578 | -0.004578 | -0.082397 | 122.3923 | -0.19226 | 122.3831 | 122.3831 | 0.004577 | 122.3328 | -0.032044 | -0.009155 | 122.58 | 122.4197 | 122.4472 | 122.2504 | 122.3831 | 122.4106 | 122.4838 | 122.3328 | 122.2504 | 122.3831 | 122.4838 | 122.4472 | 122.4106 | -0.050354 | -0.10986
1907.4219 | 122.6486 | -122.374 | 0.009155 | -0.032425 | 0.010427 | 0.0023605 | 0.027309 | -0.015528 | -0.0099719 | 0.017474 | 0.082397 | -0.064087 | 0.12817 | 0.013733 | 0.11902 | 0.14648 | 0.16937 | 0.21515 | -0.027466 | 0.004578 | 122.5021 | -0.073242 | 122.4564 | 122.3877 | 0.10986 | 122.3785 | -0.036621 | -0.045777 | 122.5433 | 122.5891 | 122.493 | 122.3099 | 122.4564 | 122.3465 | 122.5204 | 122.3785 | 122.3099 | 122.4564 | 122.5204 | 122.493 | 122.3465 | 0.11902 | -0.004577
1909.0938 | 122.5845 | -122.4289 | 0.013733 | -0.16212 | 0.010854 | -0.0042617 | 0.033932 | -0.012965 | -0.010186 | 0.016406 | 0.073242 | 0.018311 | 0.12817 | -0.073242 | 0.018311 | 0.041199 | 0.32959 | 0.14648 | 0.009155 | 0.036621 | 122.5571 | 0.004578 | 122.5021 | 122.3557 | 0.004578 | 122.4655 | -0.004578 | -0.054932 | 122.7585 | 122.5754 | 122.4472 | 122.4472 | 122.5021 | 122.438 | 122.4701 | 122.4655 | 122.4472 | 122.5021 | 122.4701 | 122.4472 | 122.438 | 0.11444 | 0.022888
1910.7812 | 122.6532 | -122.3419 | -0.009155 | 0.12779 | 0.011709 | -0.0012711 | 0.035641 | -0.011897 | -0.011895 | 0.017474 | -0.14191 | -0.21515 | -0.086975 | -0.068665 | -0.009155 | 0.036621 | 0.1236 | -0.068665 | -0.013733 | -0.13733 | 122.2549 | -0.20599 | 122.2 | 122.2733 | 0 | 122.2046 | -0.004578 | -0.054932 | 122.4655 | 122.2733 | 122.3328 | 122.1268 | 122.2 | 122.3282 | 122.3785 | 122.2046 | 122.1268 | 122.2 | 122.3785 | 122.3328 | 122.3282 | -0.07782 | -0.12817
1912.4688 | 122.5433 | -122.4243 | 0.027466 | -0.13161 | 0.010427 | 0.0036423 | 0.035 | -0.013178 | -0.0097583 | 0.016834 | 0.059509 | -0.050354 | 0.082397 | -0.032043 | 0.036621 | 0.07782 | 0.24719 | 0.11902 | -0.004578 | -0.013733 | 122.5067 | -0.07782 | 122.4838 | 122.3923 | 0.009155 | 122.4106 | -0.032044 | -0.022888 | 122.6715 | 122.5433 | 122.4609 | 122.374 | 122.4838 | 122.4197 | 122.5021 | 122.4106 | 122.374 | 122.4838 | 122.5021 | 122.4609 | 122.4197 | 0.054931 | -0.041199
1914.1562 | 122.6074 | -122.3785 | -0.004578 | 0.20409 | 0.0095724 | 0.00065151 | 0.031796 | -0.011256 | -0.01104 | 0.018115 | -0.09613 | -0.2243 | -0.059509 | 0.004578 | 0.091553 | 0.13275 | 0.009155 | 0.009155 | -0.032043 | -0.11444 | 122.319 | -0.21973 | 122.2824 | 122.3831 | 0.096131 | 122.2641 | -0.027465 | -0.036621 | 122.3877 | 122.3877 | 122.4701 | 122.1542 | 122.2824 | 122.3465 | 122.5113 | 122.2641 | 122.1542 | 122.2824 | 122.5113 | 122.4701 | 122.3465 | -0.054931 | -0.10986
1915.9219 | 122.6349 | -122.3877 | -0.004578 | 0.1049 | 0.0095724 | 0.0032151 | 0.028805 | -0.014033 | -0.01104 | 0.018115 | -0.009155 | -0.21515 | -0.009155 | 0.009155 | 0.10071 | 0.16479 | 0.050354 | 0.10529 | -0.059509 | -0.086975 | 122.3785 | -0.21057 | 122.3785 | 122.3969 | 0.10529 | 122.3007 | -0.054931 | 0 | 122.438 | 122.493 | 122.4884 | 122.1725 | 122.3785 | 122.3282 | 122.5525 | 122.3007 | 122.1725 | 122.3785 | 122.5525 | 122.4884 | 122.3282 | -0.004577 | -0.082397
1917.625 | 122.5571 | -122.4106 | 0.032043 | -0.017166 | 0.011068 | 0.0055649 | 0.034359 | -0.01211 | -0.011681 | 0.017047 | -0.018311 | -0.13733 | -0.009155 | -0.032043 | 0.013733 | 0.041199 | 0.18768 | -0.004578 | -0.004578 | -0.07782 | 122.4014 | -0.16937 | 122.3923 | 122.3785 | -0.01831 | 122.3328 | -0.036621 | -0.009156 | 122.5983 | 122.406 | 122.4243 | 122.2733 | 122.3923 | 122.406 | 122.4518 | 122.3328 | 122.2733 | 122.3923 | 122.4518 | 122.4243 | 122.406 | -0.041198 | -0.10986
1919.3438 | 122.5479 | -122.4106 | 0.022888 | -0.062942 | 0.007009 | -0.0021255 | 0.033077 | -0.012324 | -0.012108 | 0.018543 | 0.013733 | -0.14191 | 0.004578 | -0.013733 | 0.050354 | 0.086975 | 0.1831 | 0.068665 | -0.027466 | -0.059509 | 122.4152 | -0.16479 | 122.4243 | 122.3969 | 0.027466 | 122.3511 | -0.050354 | 0.009155 | 122.5937 | 122.4792 | 122.4609 | 122.2687 | 122.4243 | 122.3831 | 122.4976 | 122.3511 | 122.2687 | 122.4243 | 122.4976 | 122.4609 | 122.3831 | -0.01831 | -0.082397
1921.0781 | 122.5937 | -122.4197 | 0.018311 | -0.2079 | 0.009786 | 1.071e-05 | 0.03265 | -0.016383 | -0.0091173 | 0.017474 | 0.068665 | 0.032043 | 0.12817 | -0.073242 | 0.009155 | 0.022888 | 0.39368 | 0.15106 | -0.013733 | 0.022888 | 122.5479 | 0.013732 | 122.4884 | 122.3465 | -0.009156 | 122.4426 | -0.032044 | -0.059509 | 122.8134 | 122.5708 | 122.4289 | 122.4518 | 122.4884 | 122.406 | 122.4426 | 122.4426 | 122.4518 | 122.4884 | 122.4426 | 122.4289 | 122.406 | 0.10986 | 0.004577
1922.75 | 122.6578 | -122.3831 | 0.004578 | 0.12016 | 0.007009 | 0.0021469 | 0.027309 | -0.013392 | -0.0086901 | 0.016834 | -0.018311 | -0.2243 | -0.004578 | 0.009155 | 0.09613 | 0.15564 | 0.045776 | 0.1236 | -0.050354 | -0.086975 | 122.3785 | -0.22888 | 122.3648 | 122.3923 | 0.091552 | 122.2961 | -0.054932 | -0.013733 | 122.4289 | 122.5067 | 122.4792 | 122.1588 | 122.3648 | 122.3328 | 122.5388 | 122.2961 | 122.1588 | 122.3648 | 122.5388 | 122.4792 | 122.3328 | -0.009156 | -0.091553
1924.4688 | 122.6028 | -122.3877 | -0.004578 | -0.11635 | 0.008718 | 0.0019333 | 0.028378 | -0.01446 | -0.0063403 | 0.01662 | 0.15106 | -0.045776 | 0.15564 | 0.041199 | 0.13275 | 0.17395 | 0.17395 | 0.3067 | -0.054932 | 0.022888 | 122.5433 | -0.041198 | 122.5388 | 122.4289 | 0.13733 | 122.4106 | -0.050354 | -0.004578 | 122.5616 | 122.6944 | 122.5204 | 122.3419 | 122.5388 | 122.3328 | 122.5616 | 122.4106 | 122.3419 | 122.5388 | 122.5616 | 122.5204 | 122.3328 | 0.16022 | 0.027466
1926.1719 | 122.6074 | -122.3877 | 0.045776 | -0.2079 | 0.009786 | 0.00065151 | 0.032223 | -0.017665 | -0.0093311 | 0.016406 | 0.064087 | 0.009155 | 0.13275 | -0.064087 | -0.004578 | 0.022888 | 0.37994 | 0.16022 | 0.013733 | 0.041199 | 122.5204 | -0.036621 | 122.4518 | 122.3236 | -0.050354 | 122.4289 | -0.032043 | -0.068664 | 122.7676 | 122.5479 | 122.3831 | 122.3969 | 122.4518 | 122.4014 | 122.4106 | 122.4289 | 122.3969 | 122.4518 | 122.4106 | 122.3831 | 122.4014 | 0.086975 | -0.004577
1927.9219 | 122.6028 | -122.4014 | 0.013733 | -0.24605 | 0.0078634 | -0.0016983 | 0.033505 | -0.014033 | -0.0093311 | 0.017688 | 0.064087 | 0.018311 | 0.13275 | -0.064087 | 0 | 0.027466 | 0.36163 | 0.15564 | 0.022888 | 0.018311 | 122.5342 | 0.004578 | 122.4655 | 122.3373 | -0.013733 | 122.4197 | 0.009155 | -0.068664 | 122.7631 | 122.5571 | 122.4014 | 122.4197 | 122.4655 | 122.4243 | 122.4289 | 122.4197 | 122.4197 | 122.4655 | 122.4289 | 122.4014 | 122.4243 | 0.11902 | 0.004578
1929.6094 | 122.5845 | -122.4152 | 0 | -0.0019073 | 0.0093588 | -0.0019119 | 0.035 | -0.011683 | -0.013604 | 0.015552 | -0.045776 | -0.15564 | -0.036621 | -0.050354 | 0.013733 | 0.045776 | 0.19684 | -0.027466 | 0 | -0.09613 | 122.3785 | -0.15564 | 122.3694 | 122.3648 | 0.013733 | 122.319 | 0 | -0.009155 | 122.612 | 122.3877 | 122.4289 | 122.2595 | 122.3694 | 122.4152 | 122.4609 | 122.319 | 122.2595 | 122.3694 | 122.4609 | 122.4289 | 122.4152 | -0.036621 | -0.09613
1931.2969 | 122.5479 | -122.438 | 0.018311 | -0.070572 | 0.0093588 | -0.00041649 | 0.035 | -0.011897 | -0.012535 | 0.015338 | 0.018311 | -0.10986 | 0.036621 | 0 | 0.059509 | 0.086975 | 0.20142 | 0.10071 | -0.022888 | -0.045776 | 122.4747 | -0.12817 | 122.4564 | 122.438 | 0.041198 | 122.3923 | -0.041199 | -0.01831 | 122.6395 | 122.5388 | 122.4976 | 122.3282 | 122.4564 | 122.4152 | 122.525 | 122.3923 | 122.3282 | 122.4564 | 122.525 | 122.4976 | 122.4152 | 0.01831 | -0.064087
1933 | 122.5754 | -122.4289 | 0.018311 | -0.024795 | 0.0089316 | 0.0019333 | 0.033077 | -0.0093331 | -0.011467 | 0.017902 | -0.013733 | -0.14648 | -0.009155 | -0.036621 | 0.032043 | 0.064087 | 0.22888 | 0.022888 | -0.027466 | -0.068665 | 122.4197 | -0.16479 | 122.4152 | 122.3923 | 0.013732 | 122.3602 | -0.045777 | -0.004578 | 122.6578 | 122.4518 | 122.4609 | 122.2824 | 122.4152 | 122.4014 | 122.493 | 122.3602 | 122.2824 | 122.4152 | 122.493 | 122.4609 | 122.4014 | -0.027466 | -0.086976
1934.6875 | 122.6212 | -122.3969 | -0.004578 | 0.1812 | 0.0093588 | -0.0021255 | 0.029873 | -0.011469 | -0.0089037 | 0.018329 | -0.013733 | -0.25635 | -0.032043 | 0.045776 | 0.11902 | 0.1831 | 0.054932 | 0.07782 | -0.050354 | -0.10986 | 122.3648 | -0.25177 | 122.3831 | 122.4426 | 0.1236 | 122.287 | -0.045776 | 0.01831 | 122.4518 | 122.4747 | 122.5159 | 122.1405 | 122.3831 | 122.3465 | 122.58 | 122.287 | 122.1405 | 122.3831 | 122.58 | 122.5159 | 122.3465 | -0.027465 | -0.10529
1936.4062 | 122.5342 | -122.4152 | 0.036621 | -0.13924 | 0.008718 | 0.0062057 | 0.033291 | -0.01446 | -0.01104 | 0.015979 | 0.050354 | -0.064087 | 0.054932 | -0.018311 | 0.050354 | 0.086975 | 0.27924 | 0.14191 | -0.027466 | -0.022888 | 122.4701 | -0.10071 | 122.4655 | 122.3969 | 0.013733 | 122.3923 | -0.064087 | -0.004578 | 122.6944 | 122.5571 | 122.4655 | 122.3511 | 122.4655 | 122.3877 | 122.5021 | 122.3923 | 122.3511 | 122.4655 | 122.5021 | 122.4655 | 122.3877 | 0.018311 | -0.059509
1938.1406 | 122.6486 | -122.4014 | 0.004578 | 0.14305 | 0.0085042 | -0.00084389 | 0.031796 | -0.011897 | -0.0086901 | 0.018329 | -0.059509 | -0.23346 | -0.036621 | 0.013733 | 0.086975 | 0.15106 | 0.041199 | 0.054932 | -0.036621 | -0.11444 | 122.3648 | -0.23804 | 122.3419 | 122.4152 | 0.082397 | 122.287 | -0.041199 | -0.022888 | 122.4426 | 122.4564 | 122.4884 | 122.168 | 122.3419 | 122.3648 | 122.5525 | 122.287 | 122.168 | 122.3419 | 122.5525 | 122.4884 | 122.3648 | -0.041199 | -0.11902
1939.8281 | 122.5754 | -122.438 | 0.027466 | -0.0095368 | 0.011922 | 0.0015061 | 0.035 | -0.010401 | -0.0093311 | 0.015552 | -0.041199 | -0.16022 | -0.009155 | -0.041199 | 0.018311 | 0.050354 | 0.20142 | 0.004578 | -0.004578 | -0.091553 | 122.4289 | -0.18768 | 122.3969 | 122.3969 | -0.009155 | 122.3465 | -0.032044 | -0.032044 | 122.6395 | 122.4426 | 122.4564 | 122.2778 | 122.3969 | 122.4335 | 122.4884 | 122.3465 | 122.2778 | 122.3969 | 122.4884 | 122.4564 | 122.4335 | -0.036621 | -0.11902
1941.5312 | 122.7127 | -122.3923 | 0 | 0.059128 | 0.011281 | -0.0014847 | 0.028805 | -0.01681 | -0.0074085 | 0.016406 | 0.027466 | -0.1236 | 0.064087 | -0.018311 | 0.073242 | 0.11444 | 0.14191 | 0.1236 | -0.041199 | -0.045776 | 122.4564 | -0.1236 | 122.4197 | 122.374 | 0.073242 | 122.3465 | -0.041199 | -0.036621 | 122.5342 | 122.5159 | 122.4655 | 122.2687 | 122.4197 | 122.3511 | 122.5067 | 122.3465 | 122.2687 | 122.4197 | 122.5067 | 122.4655 | 122.3511 | 0.064087 | -0.045776
1943.2344 | 122.644 | -122.3923 | 0.022888 | 0.17357 | 0.0091452 | 0.0019333 | 0.032436 | -0.013178 | -0.011681 | 0.017261 | -0.009155 | -0.23346 | -0.018311 | 0.041199 | 0.1236 | 0.16022 | -0.009155 | 0.07782 | -0.054932 | -0.11444 | 122.374 | -0.25635 | 122.3831 | 122.4335 | 0.10071 | 122.2778 | -0.07782 | 0.009156 | 122.3831 | 122.4701 | 122.5159 | 122.1588 | 122.3831 | 122.3373 | 122.5525 | 122.2778 | 122.1588 | 122.3831 | 122.5525 | 122.5159 | 122.3373 | -0.041199 | -0.13733
1945.0156 | 122.6807 | -122.4152 | 0.004578 | 0.13542 | 0.011281 | 0.0032151 | 0.029659 | -0.01211 | -0.0071947 | 0.016406 | 0.009155 | -0.19226 | 0.009155 | -0.004578 | 0.064087 | 0.12817 | 0.059509 | 0.091553 | -0.041199 | -0.10529 | 122.4243 | -0.19684 | 122.4243 | 122.4106 | 0.059509 | 122.3099 | -0.045777 | 0 | 122.4747 | 122.5067 | 122.4792 | 122.2229 | 122.4243 | 122.374 | 122.5433 | 122.3099 | 122.2229 | 122.4243 | 122.5433 | 122.4792 | 122.374 | 0.004577 | -0.10986
1946.6875 | 122.644 | -122.4014 | 0.022888 | -0.13161 | 0.008718 | -0.0057571 | 0.030941 | -0.016169 | -0.0080493 | 0.01662 | 0.12817 | -0.059509 | 0.14191 | 0.041199 | 0.11444 | 0.18768 | 0.16479 | 0.31128 | -0.041199 | 0 | 122.5433 | -0.082397 | 122.5296 | 122.4426 | 0.091553 | 122.4014 | -0.064087 | -0.013733 | 122.5662 | 122.7127 | 122.5159 | 122.3419 | 122.5296 | 122.3602 | 122.5891 | 122.4014 | 122.3419 | 122.5296 | 122.5891 | 122.5159 | 122.3602 | 0.11902 | -0.022888
1948.4062 | 122.6852 | -122.3969 | 0.036621 | 0.0057222 | 0.0095724 | -0.0019119 | 0.032436 | -0.014887 | -0.0067675 | 0.015979 | 0.050354 | -0.10071 | 0.082397 | -0.004578 | 0.07782 | 0.11444 | 0.15106 | 0.16479 | -0.036621 | -0.018311 | 122.4792 | -0.13733 | 122.4472 | 122.3923 | 0.041199 | 122.3785 | -0.073242 | -0.032043 | 122.5479 | 122.5616 | 122.4747 | 122.2961 | 122.4472 | 122.3602 | 122.5113 | 122.3785 | 122.2961 | 122.4472 | 122.5113 | 122.4747 | 122.3602 | 0.045776 | -0.054932
1950.0938 | 122.7036 | -122.3969 | 0.027466 | 0.0057222 | 0.0091452 | 0.00086511 | 0.031155 | -0.015956 | -0.0065539 | 0.016406 | 0.032043 | -0.11444 | 0.068665 | -0.009155 | 0.064087 | 0.10986 | 0.15106 | 0.16479 | -0.027466 | -0.027466 | 122.4655 | -0.14191 | 122.4289 | 122.3877 | 0.036621 | 122.3694 | -0.054932 | -0.036622 | 122.5479 | 122.5616 | 122.4609 | 122.2824 | 122.4289 | 122.3694 | 122.5067 | 122.3694 | 122.2824 | 122.4289 | 122.5067 | 122.4609 | 122.3694 | 0.041199 | -0.054932
1951.7812 | 122.6532 | -122.406 | 0.013733 | -0.10872 | 0.010213 | -0.0049027 | 0.030727 | -0.017237 | -0.010613 | 0.014911 | 0.11902 | -0.082397 | 0.1236 | 0.059509 | 0.11902 | 0.17395 | 0.15564 | 0.29297 | -0.027466 | -0.036621 | 122.5296 | -0.09613 | 122.525 | 122.4655 | 0.10529 | 122.3694 | -0.041199 | -0.004577 | 122.5616 | 122.699 | 122.525 | 122.3236 | 122.525 | 122.3785 | 122.58 | 122.3694 | 122.3236 | 122.525 | 122.58 | 122.525 | 122.3785 | 0.10986 | -0.050354
1953.4688 | 122.5845 | -122.4243 | 0.013733 | -0.17738 | 0.0085042 | -0.00084389 | 0.036923 | -0.011897 | -0.012535 | 0.014056 | 0.041199 | -0.041199 | 0.086975 | -0.032043 | 0.022888 | 0.054932 | 0.27466 | 0.14648 | -0.013733 | -0.059509 | 122.5113 | -0.054932 | 122.4655 | 122.3923 | 0.009155 | 122.3648 | -0.027466 | -0.045776 | 122.699 | 122.5708 | 122.4472 | 122.3831 | 122.4655 | 122.4106 | 122.4792 | 122.3648 | 122.3831 | 122.4655 | 122.4792 | 122.4472 | 122.4106 | 0.073242 | -0.073242
1955.1719 | 122.644 | -122.4152 | 0.018311 | -0.23079 | 0.0091452 | -0.0010575 | 0.030941 | -0.015101 | -0.0076221 | 0.015338 | 0.11444 | -0.086975 | 0.10529 | 0.054932 | 0.1236 | 0.16937 | 0.15106 | 0.26093 | -0.050354 | -0.022888 | 122.5204 | -0.10529 | 122.5296 | 122.4701 | 0.10528 | 122.3923 | -0.068665 | 0.009155 | 122.5662 | 122.6761 | 122.5388 | 122.3282 | 122.5296 | 122.3648 | 122.5845 | 122.3923 | 122.3282 | 122.5296 | 122.5845 | 122.5388 | 122.3648 | 0.086975 | -0.041199
1956.8906 | 122.5616 | -122.4152 | 0.036621 | -0.1545 | 0.0082906 | -0.0012711 | 0.030727 | -0.015101 | -0.010613 | 0.015125 | 0.17395 | -0.045776 | 0.16022 | 0.068665 | 0.1236 | 0.14648 | 0.20142 | 0.30212 | -0.036621 | -0.013733 | 122.5754 | -0.082397 | 122.5891 | 122.4838 | 0.086975 | 122.4014 | -0.073242 | 0.013733 | 122.6166 | 122.7173 | 122.5388 | 122.3694 | 122.5891 | 122.3785 | 122.5616 | 122.4014 | 122.3694 | 122.5891 | 122.5616 | 122.5388 | 122.3785 | 0.1236 | -0.050354
1958.5625 | 122.6852 | -122.4014 | -0.009155 | 0.074387 | 0.0093588 | -0.0019119 | 0.039272 | -0.013392 | -0.013176 | 0.015552 | -0.1236 | -0.16937 | -0.059509 | -0.073242 | -0.022888 | 0.009155 | 0.18768 | -0.07782 | -0.018311 | -0.050354 | 122.3419 | -0.16022 | 122.2778 | 122.3282 | -0.013733 | 122.3511 | -0.009156 | -0.064087 | 122.5891 | 122.3236 | 122.3785 | 122.2321 | 122.2778 | 122.3831 | 122.4106 | 122.3511 | 122.2321 | 122.2778 | 122.4106 | 122.3785 | 122.3831 | -0.050354 | -0.041199
1960.25 | 122.5616 | -122.4564 | 0.032043 | -0.16212 | 0.0095724 | -0.00020289 | 0.029873 | -0.013819 | -0.0093311 | 0.016193 | 0.1831 | -0.027466 | 0.16022 | 0.059509 | 0.1236 | 0.15106 | 0.19684 | 0.3067 | -0.054932 | -0.032043 | 122.6166 | -0.059509 | 122.6395 | 122.5159 | 0.091553 | 122.4243 | -0.086975 | 0.022888 | 122.6532 | 122.7631 | 122.58 | 122.4289 | 122.6395 | 122.4014 | 122.6074 | 122.4243 | 122.4289 | 122.6395 | 122.6074 | 122.58 | 122.4014 | 0.12817 | -0.064086
1961.9219 | 122.5983 | -122.4564 | 0.036621 | -0.21553 | 0.0095724 | 0.0021469 | 0.034359 | -0.013819 | -0.0082629 | 0.013202 | 0.13733 | -0.045776 | 0.13733 | 0.018311 | 0.082397 | 0.10529 | 0.27924 | 0.24719 | -0.027466 | -0.059509 | 122.5937 | -0.082397 | 122.5937 | 122.4747 | 0.045776 | 122.3969 | -0.064087 | 0 | 122.7356 | 122.7036 | 122.5388 | 122.4106 | 122.5937 | 122.4289 | 122.5616 | 122.3969 | 122.4106 | 122.5937 | 122.5616 | 122.5388 | 122.4289 | 0.10071 | -0.09613
1963.6094 | 122.58 | -122.4335 | 0.032043 | -0.16975 | 0.009786 | 0.0025741 | 0.029873 | -0.016383 | -0.0084765 | 0.016406 | 0.16479 | -0.054932 | 0.14191 | 0.050354 | 0.13733 | 0.16479 | 0.20142 | 0.32044 | -0.059509 | -0.022888 | 122.5754 | -0.086975 | 122.5983 | 122.4838 | 0.10529 | 122.4106 | -0.091552 | 0.022888 | 122.6349 | 122.7539 | 122.5708 | 122.3785 | 122.5983 | 122.374 | 122.5983 | 122.4106 | 122.3785 | 122.5983 | 122.5983 | 122.5708 | 122.374 | 0.10986 | -0.054931
1965.2812 | 122.7127 | -122.3923 | -0.013733 | 0.097275 | 0.0099996 | 0.0021469 | 0.034573 | -0.010829 | -0.012749 | 0.017474 | -0.13275 | -0.2243 | -0.086975 | -0.068665 | -0.009155 | 0.050354 | 0.13275 | -0.064087 | 0 | -0.064087 | 122.3053 | -0.21057 | 122.2595 | 122.3236 | 0.004578 | 122.3282 | 0.013733 | -0.045776 | 122.525 | 122.3282 | 122.3831 | 122.168 | 122.2595 | 122.3923 | 122.4426 | 122.3282 | 122.168 | 122.2595 | 122.4426 | 122.3831 | 122.3923 | -0.073242 | -0.050354
1967.0156 | 122.6578 | -122.4335 | -0.004578 | 0.17357 | 0.008718 | -0.00063009 | 0.035427 | -0.013606 | -0.0082629 | 0.015979 | -0.009155 | -0.21515 | -0.022888 | 0.050354 | 0.11902 | 0.17853 | 0.004578 | 0.10986 | -0.036621 | -0.018311 | 122.4106 | -0.21057 | 122.4243 | 122.4838 | 0.1236 | 122.4152 | -0.032043 | 0.013733 | 122.438 | 122.5433 | 122.5525 | 122.2183 | 122.4243 | 122.3969 | 122.612 | 122.4152 | 122.2183 | 122.4243 | 122.612 | 122.5525 | 122.3969 | -0.01831 | -0.013733
1968.7031 | 122.6303 | -122.4472 | 0.018311 | -0.18501 | 0.007009 | -0.0014847 | 0.033077 | -0.014247 | -0.0099719 | 0.018329 | 0.045776 | -0.027466 | 0.09613 | -0.054932 | 0.013733 | 0.027466 | 0.35706 | 0.13275 | -0.004578 | -0.054932 | 122.5433 | -0.045777 | 122.493 | 122.3923 | -0.004578 | 122.3923 | -0.022889 | -0.050354 | 122.8043 | 122.58 | 122.4609 | 122.4197 | 122.493 | 122.4426 | 122.4747 | 122.3923 | 122.4197 | 122.493 | 122.4747 | 122.4609 | 122.4426 | 0.077819 | -0.073243
1970.4062 | 122.699 | -122.3969 | -0.009155 | 0.1049 | 0.0089316 | 0.0038559 | 0.034573 | -0.012965 | -0.011254 | 0.017047 | -0.13275 | -0.19684 | -0.059509 | -0.073242 | -0.009155 | 0.022888 | 0.17395 | -0.059509 | -0.004578 | -0.054932 | 122.3373 | -0.18768 | 122.2641 | 122.3236 | 0 | 122.3419 | 0.004577 | -0.073242 | 122.5708 | 122.3373 | 122.3877 | 122.2 | 122.2641 | 122.3923 | 122.4197 | 122.3419 | 122.2 | 122.2641 | 122.4197 | 122.3877 | 122.3923 | -0.050354 | -0.045777
1972.1094 | 122.5983 | -122.4564 | 0.013733 | 0.0057222 | 0.010854 | -0.0019119 | 0.033718 | -0.011042 | -0.011254 | 0.019397 | -0.050354 | -0.14191 | -0.004578 | -0.045776 | 0.004578 | 0.045776 | 0.19684 | -0.004578 | 0.009155 | -0.064087 | 122.4518 | -0.15564 | 122.406 | 122.4106 | -0.009155 | 122.3923 | -0.004578 | -0.045776 | 122.6532 | 122.4518 | 122.4609 | 122.3145 | 122.406 | 122.4655 | 122.5021 | 122.3923 | 122.3145 | 122.406 | 122.5021 | 122.4609 | 122.4655 | -0.018311 | -0.07782
1973.7812 | 122.6624 | -122.4518 | 0.004578 | 0.17357 | 0.0072226 | -0.00041649 | 0.032009 | -0.012324 | -0.0089037 | 0.017688 | -0.013733 | -0.23346 | -0.018311 | 0.050354 | 0.13275 | 0.16022 | 0.027466 | 0.073242 | -0.045776 | 0 | 122.4335 | -0.23804 | 122.438 | 122.5021 | 0.12817 | 122.4518 | -0.050354 | 0.004578 | 122.4792 | 122.525 | 122.5845 | 122.2183 | 122.438 | 122.406 | 122.612 | 122.4518 | 122.2183 | 122.438 | 122.612 | 122.5845 | 122.406 | -0.022889 | -0.004578
1975.4688 | 122.5571 | -122.4335 | 0.022888 | -0.085831 | 0.0076498 | 0.00043791 | 0.034786 | -0.012965 | -0.013176 | 0.016834 | 0.022888 | -0.10529 | 0.054932 | 0.004578 | 0.064087 | 0.082397 | 0.23804 | 0.11902 | -0.022888 | -0.054932 | 122.4884 | -0.12817 | 122.4564 | 122.438 | 0.041199 | 122.3785 | -0.045776 | -0.032044 | 122.6715 | 122.5525 | 122.4976 | 122.3282 | 122.4564 | 122.4106 | 122.5159 | 122.3785 | 122.3282 | 122.4564 | 122.5159 | 122.4976 | 122.4106 | 0.032044 | -0.07782
1977.1562 | 122.6715 | -122.438 | 0.018311 | -0.078201 | 0.0089316 | -0.0027665 | 0.027737 | -0.014674 | -0.0076221 | 0.017474 | 0.10986 | -0.07782 | 0.11444 | 0.027466 | 0.13275 | 0.16479 | 0.20599 | 0.27466 | -0.022888 | -0.032043 | 122.5525 | -0.096131 | 122.5479 | 122.4655 | 0.11444 | 122.406 | -0.041199 | -0.004578 | 122.644 | 122.7127 | 122.5708 | 122.3602 | 122.5479 | 122.4152 | 122.6028 | 122.406 | 122.3602 | 122.5479 | 122.6028 | 122.5708 | 122.4152 | 0.09613 | -0.050354
1978.8594 | 122.5845 | -122.4701 | 0.009155 | -0.062942 | 0.0099996 | 0.00022431 | 0.035641 | -0.01446 | -0.011467 | 0.019397 | 0.004578 | -0.15106 | 0.009155 | -0.004578 | 0.045776 | 0.07782 | 0.21973 | 0.082397 | -0.004578 | -0.045776 | 122.4792 | -0.16022 | 122.4747 | 122.4655 | 0.036621 | 122.4243 | -0.013733 | -0.004577 | 122.6898 | 122.5525 | 122.5159 | 122.319 | 122.4747 | 122.4655 | 122.5479 | 122.4243 | 122.319 | 122.4747 | 122.5479 | 122.5159 | 122.4655 | 0 | -0.054931
1980.5469 | 122.6578 | -122.4472 | 0.004578 | 0.051498 | 0.0093588 | 0.00043791 | 0.034359 | -0.01211 | -0.011895 | 0.018115 | -0.11902 | -0.16937 | -0.027466 | -0.07782 | 0 | 0.032043 | 0.22888 | -0.027466 | 0 | -0.068665 | 122.4197 | -0.17395 | 122.3282 | 122.3694 | -0.004578 | 122.3785 | -0.004578 | -0.091553 | 122.6761 | 122.4197 | 122.4472 | 122.2778 | 122.3282 | 122.4472 | 122.4792 | 122.3785 | 122.2778 | 122.3282 | 122.4792 | 122.4472 | 122.4472 | -0.032044 | -0.073243
1982.2188 | 122.731 | -122.406 | -0.004578 | 0.051498 | 0.011281 | -0.0019119 | 0.027737 | -0.013392 | -0.0082629 | 0.017902 | -0.009155 | -0.19226 | 0.027466 | -0.013733 | 0.07782 | 0.12817 | 0.068665 | 0.17853 | -0.032043 | -0.027466 | 122.4335 | -0.18768 | 122.3969 | 122.3923 | 0.082398 | 122.3785 | -0.027465 | -0.036621 | 122.4747 | 122.5845 | 122.4838 | 122.2137 | 122.3969 | 122.374 | 122.5342 | 122.3785 | 122.2137 | 122.3969 | 122.5342 | 122.4838 | 122.374 | 0.032044 | -0.022888
1983.8906 | 122.6257 | -122.4518 | 0.022888 | -0.10872 | 0.0095724 | -0.0016983 | 0.0303 | -0.016596 | -0.0065539 | 0.017474 | 0.15106 | -0.041199 | 0.16022 | 0.041199 | 0.14191 | 0.1831 | 0.086975 | 0.35706 | -0.036621 | -0.032043 | 122.612 | -0.064087 | 122.6028 | 122.493 | 0.11902 | 122.4197 | -0.059509 | -0.009155 | 122.5388 | 122.8088 | 122.5937 | 122.4106 | 122.6028 | 122.4152 | 122.6349 | 122.4197 | 122.4106 | 122.6028 | 122.6349 | 122.5937 | 122.4152 | 0.13733 | -0.054931
1985.6094 | 122.6807 | -122.4014 | -0.004578 | 0.1812 | 0.011495 | -0.00020289 | 0.035 | -0.012751 | -0.0093311 | 0.017047 | -0.10071 | -0.20599 | -0.07782 | -0.022888 | 0.054932 | 0.10529 | -0.009155 | 0.11444 | -0.009155 | -0.027466 | 122.3236 | -0.20142 | 122.3007 | 122.3785 | 0.05951 | 122.374 | -0.004577 | -0.022888 | 122.3923 | 122.5159 | 122.4564 | 122.1954 | 122.3007 | 122.3923 | 122.5067 | 122.374 | 122.1954 | 122.3007 | 122.5067 | 122.4564 | 122.3923 | -0.073242 | -0.022888
1987.2969 | 122.7127 | -122.438 | -0.004578 | 0.043869 | 0.0089316 | -0.0023391 | 0.029018 | -0.015101 | -0.0071947 | 0.016406 | 0.027466 | -0.12817 | 0.059509 | -0.022888 | 0.064087 | 0.10986 | 0.07782 | 0.20599 | -0.032043 | -0.045776 | 122.4976 | -0.1236 | 122.4655 | 122.4152 | 0.068665 | 122.3923 | -0.027465 | -0.032043 | 122.5159 | 122.644 | 122.5021 | 122.3099 | 122.4655 | 122.406 | 122.5479 | 122.3923 | 122.3099 | 122.4655 | 122.5479 | 122.5021 | 122.406 | 0.064087 | -0.041198
1989 | 122.5708 | -122.4472 | 0.027466 | -0.085831 | 0.0093588 | -0.0016983 | 0.035 | -0.015101 | -0.0097583 | 0.018543 | 0.050354 | -0.09613 | 0.059509 | 0.018311 | 0.050354 | 0.082397 | 0.11902 | 0.17395 | -0.013733 | -0.054932 | 122.5067 | -0.1236 | 122.4976 | 122.4655 | 0.022888 | 122.3923 | -0.041199 | -0.009155 | 122.5662 | 122.6212 | 122.4976 | 122.3511 | 122.4976 | 122.4335 | 122.5296 | 122.3923 | 122.3511 | 122.4976 | 122.5296 | 122.4976 | 122.4335 | 0.032043 | -0.082398
1990.7188 | 122.5937 | -122.4747 | 0.032043 | -0.17738 | 0.0074362 | -0.0036209 | 0.029659 | -0.01446 | -0.0093311 | 0.015979 | 0.18768 | -0.018311 | 0.17853 | 0.054932 | 0.1236 | 0.15564 | 0.10071 | 0.33417 | -0.045776 | -0.022888 | 122.6532 | -0.050354 | 122.6624 | 122.5296 | 0.091553 | 122.4518 | -0.077819 | 0.009155 | 122.5754 | 122.8088 | 122.5983 | 122.4564 | 122.6624 | 122.4289 | 122.6303 | 122.4518 | 122.4564 | 122.6624 | 122.6303 | 122.5983 | 122.4289 | 0.14648 | -0.054931
1992.4062 | 122.6669 | -122.4426 | 0 | 0.14305 | 0.008718 | 0.00043791 | 0.033932 | -0.012751 | -0.010613 | 0.015979 | -0.064087 | -0.22888 | -0.050354 | 0.009155 | 0.07782 | 0.1236 | -0.064087 | 0.11902 | -0.050354 | -0.032043 | 122.3923 | -0.22888 | 122.3785 | 122.4518 | 0.07782 | 122.4106 | -0.050354 | -0.013733 | 122.3785 | 122.5616 | 122.5204 | 122.2137 | 122.3785 | 122.3923 | 122.5662 | 122.4106 | 122.2137 | 122.3785 | 122.5662 | 122.5204 | 122.3923 | -0.050354 | -0.032043
1994.0781 | 122.644 | -122.4518 | 0.022888 | -0.21553 | 0.011922 | 0.0032151 | 0.033077 | -0.015528 | -0.010399 | 0.017474 | 0.10529 | 0.018311 | 0.13275 | -0.059509 | 0.018311 | 0.036621 | 0.24719 | 0.17395 | -0.013733 | -0.07782 | 122.5845 | -0.004577 | 122.5571 | 122.3923 | -0.004577 | 122.374 | -0.036621 | -0.027465 | 122.699 | 122.6257 | 122.4701 | 122.4701 | 122.5571 | 122.438 | 122.4884 | 122.374 | 122.4701 | 122.5571 | 122.4884 | 122.4701 | 122.438 | 0.10986 | -0.10071
1995.7656 | 122.7219 | -122.4289 | 0.004578 | 0.15068 | 0.009786 | 0.0015061 | 0.035 | -0.011469 | -0.0099719 | 0.017047 | -0.11444 | -0.19226 | -0.07782 | -0.07782 | -0.018311 | 0.027466 | 0.041199 | -0.004578 | 0.004578 | -0.073242 | 122.3511 | -0.19684 | 122.3145 | 122.3511 | -0.022889 | 122.3557 | 0 | -0.036621 | 122.4701 | 122.4243 | 122.4106 | 122.2366 | 122.3145 | 122.4335 | 122.4564 | 122.3557 | 122.2366 | 122.3145 | 122.4564 | 122.4106 | 122.4335 | -0.082398 | -0.07782
1997.4531 | 122.6486 | -122.4701 | 0.018311 | -0.18501 | 0.008718 | -0.0031937 | 0.029446 | -0.014887 | -0.0082629 | 0.018756 | 0.09613 | 0.013733 | 0.15564 | -0.022888 | 0.032043 | 0.059509 | 0.23346 | 0.20142 | 0 | -0.073242 | 122.6257 | -0.004578 | 122.5662 | 122.4472 | 0.013732 | 122.3969 | -0.018311 | -0.05951 | 122.7036 | 122.6715 | 122.5021 | 122.4838 | 122.5662 | 122.4701 | 122.5296 | 122.3969 | 122.4838 | 122.5662 | 122.5296 | 122.5021 | 122.4701 | 0.13733 | -0.091553
1999.1406 | 122.7264 | -122.4335 | -0.018311 | 0.13542 | 0.009786 | -0.00063009 | 0.034359 | -0.01211 | -0.010399 | 0.017047 | -0.13733 | -0.19684 | -0.082397 | -0.07782 | 0 | 0.032043 | 0.054932 | 0.009155 | 0.004578 | -0.041199 | 122.3511 | -0.17853 | 122.2961 | 122.3557 | 0.018311 | 122.3923 | 0.022889 | -0.054932 | 122.4884 | 122.4426 | 122.4335 | 122.2366 | 122.2961 | 122.438 | 122.4655 | 122.3923 | 122.2366 | 122.2961 | 122.4655 | 122.4335 | 122.438 | -0.064086 | -0.022888
2000.8594 | 122.7448 | -122.4518 | 0 | 0.059128 | 0.0082906 | -0.0044755 | 0.028378 | -0.014033 | -0.0084765 | 0.017047 | 0.013733 | -0.14191 | 0.050354 | -0.009155 | 0.064087 | 0.12817 | 0.054932 | 0.19226 | -0.036621 | -0.032043 | 122.5021 | -0.14191 | 122.4655 | 122.4426 | 0.064087 | 122.4197 | -0.036621 | -0.036621 | 122.5067 | 122.644 | 122.5159 | 122.3099 | 122.4655 | 122.4152 | 122.58 | 122.4197 | 122.3099 | 122.4655 | 122.58 | 122.5159 | 122.4152 | 0.050354 | -0.032043
2002.5469 | 122.6349 | -122.4655 | 0.009155 | 0.020981 | 0.0099996 | 0.0012925 | 0.034786 | -0.013819 | -0.011681 | 0.019611 | -0.050354 | -0.15564 | -0.018311 | -0.050354 | 0.009155 | 0.036621 | 0.09613 | 0.068665 | -0.022888 | -0.041199 | 122.4472 | -0.16479 | 122.4152 | 122.4152 | 0 | 122.4243 | -0.032043 | -0.032043 | 122.5616 | 122.5342 | 122.4747 | 122.3099 | 122.4152 | 122.4426 | 122.5021 | 122.4243 | 122.3099 | 122.4152 | 122.5021 | 122.4747 | 122.4426 | -0.027466 | -0.050354
2004.2344 | 122.6761 | -122.4564 | 0.009155 | 0.16594 | 0.010854 | 0.0012925 | 0.03265 | -0.012324 | -0.0089037 | 0.018329 | -0.009155 | -0.23346 | -0.027466 | 0.027466 | 0.11902 | 0.16479 | -0.10071 | 0.16937 | -0.054932 | -0.022888 | 122.4289 | -0.24261 | 122.4472 | 122.4838 | 0.10986 | 122.4335 | -0.064087 | 0.018311 | 122.3557 | 122.6257 | 122.5754 | 122.2229 | 122.4472 | 122.4014 | 122.6212 | 122.4335 | 122.2229 | 122.4472 | 122.6212 | 122.5754 | 122.4014 | -0.036621 | -0.032043
2005.9844 | 122.7081 | -122.4243 | 0.009155 | 0.1049 | 0.009786 | 0.0034287 | 0.032009 | -0.013819 | -0.0067675 | 0.017474 | -0.009155 | -0.20142 | -0.004578 | 0.032043 | 0.10529 | 0.15564 | -0.045776 | 0.19226 | -0.045776 | -0.018311 | 122.4197 | -0.21057 | 122.4152 | 122.4564 | 0.096131 | 122.406 | -0.054931 | -0.004577 | 122.3785 | 122.6166 | 122.5296 | 122.2229 | 122.4152 | 122.3785 | 122.58 | 122.406 | 122.2229 | 122.4152 | 122.58 | 122.5296 | 122.3785 | -0.013733 | -0.027466
2007.6719 | 122.644 | -122.4747 | 0.036621 | -0.21553 | 0.010213 | -0.0066117 | 0.032009 | -0.01681 | -0.010613 | 0.017261 | 0.14648 | -0.004578 | 0.17395 | -0.013733 | 0.059509 | 0.073242 | 0.21973 | 0.22888 | -0.004578 | -0.041199 | 122.6486 | -0.041199 | 122.6212 | 122.4609 | 0.022888 | 122.4335 | -0.041199 | -0.027466 | 122.6944 | 122.7036 | 122.5342 | 122.4701 | 122.6212 | 122.4701 | 122.5479 | 122.4335 | 122.4701 | 122.6212 | 122.5479 | 122.5342 | 122.4701 | 0.13733 | -0.07782
2009.375 | 122.6761 | -122.4426 | 0.004578 | 0.18883 | 0.008077 | 0.0034287 | 0.034573 | -0.013178 | -0.01104 | 0.014911 | -0.022888 | -0.2243 | -0.050354 | 0.045776 | 0.10071 | 0.16479 | -0.091553 | 0.17395 | -0.032043 | 0.004578 | 122.3923 | -0.22888 | 122.4197 | 122.4884 | 0.09613 | 122.4472 | -0.036621 | 0.027466 | 122.3511 | 122.6166 | 122.5433 | 122.2183 | 122.4197 | 122.4106 | 122.6074 | 122.4472 | 122.2183 | 122.4197 | 122.6074 | 122.5433 | 122.4106 | -0.054932 | 0
2011.1094 | 122.6761 | -122.438 | 0.018311 | 0.11253 | 0.0085042 | 1.071e-05 | 0.033718 | -0.013392 | -0.010613 | 0.017902 | -0.032043 | -0.23346 | -0.059509 | 0.032043 | 0.10071 | 0.16022 | -0.09613 | 0.16022 | -0.041199 | 0 | 122.3785 | -0.25177 | 122.406 | 122.4701 | 0.082397 | 122.438 | -0.05951 | 0.027466 | 122.3419 | 122.5983 | 122.5388 | 122.2046 | 122.406 | 122.3969 | 122.5983 | 122.438 | 122.2046 | 122.406 | 122.5983 | 122.5388 | 122.3969 | -0.07782 | -0.018311
2012.8125 | 122.5983 | -122.4838 | 0.022888 | -0.070572 | 0.009786 | 0.0027877 | 0.036709 | -0.013819 | -0.0097583 | 0.015552 | 0.064087 | -0.064087 | 0.064087 | -0.004578 | 0.050354 | 0.086975 | 0.11444 | 0.16022 | -0.009155 | -0.032043 | 122.5479 | -0.086975 | 122.5479 | 122.4792 | 0.027466 | 122.4518 | -0.032043 | 0 | 122.5983 | 122.644 | 122.5342 | 122.4197 | 122.5479 | 122.4747 | 122.5708 | 122.4518 | 122.4197 | 122.5479 | 122.5708 | 122.5342 | 122.4747 | 0.041199 | -0.054931
2014.5469 | 122.7264 | -122.4289 | -0.009155 | 0.097275 | 0.010213 | -0.0044755 | 0.035214 | -0.012324 | -0.0097583 | 0.017474 | -0.11902 | -0.1831 | -0.068665 | -0.07782 | 0.004578 | 0.032043 | 0.068665 | 0.022888 | -0.013733 | -0.064087 | 122.3602 | -0.17395 | 122.3099 | 122.3511 | 0.013733 | 122.3648 | -0.004578 | -0.050354 | 122.4976 | 122.4518 | 122.4335 | 122.2458 | 122.3099 | 122.4152 | 122.4609 | 122.3648 | 122.2458 | 122.3099 | 122.4609 | 122.4335 | 122.4152 | -0.05951 | -0.054932
2016.2344 | 122.7081 | -122.4426 | 0.009155 | 0.12779 | 0.0074362 | -0.00063009 | 0.028164 | -0.011042 | -0.0080493 | 0.018756 | 0 | -0.21973 | -0.018311 | 0.032043 | 0.11902 | 0.16479 | -0.054932 | 0.18768 | -0.036621 | -0.018311 | 122.4243 | -0.22888 | 122.4426 | 122.4747 | 0.10986 | 122.4243 | -0.045776 | 0.018311 | 122.3877 | 122.6303 | 122.5616 | 122.2229 | 122.4426 | 122.406 | 122.6074 | 122.4243 | 122.2229 | 122.4426 | 122.6074 | 122.5616 | 122.406 | -0.027466 | -0.027466
2018 | 122.6074 | -122.4976 | 0.013733 | -0.024795 | 0.010427 | 0.0036423 | 0.035427 | -0.011042 | -0.011254 | 0.01897 | -0.013733 | -0.13733 | -0.018311 | -0.032043 | 0.041199 | 0.064087 | 0.082397 | 0.086975 | -0.009155 | -0.059509 | 122.4792 | -0.15106 | 122.4838 | 122.4655 | 0.027466 | 122.438 | -0.022888 | 0.004578 | 122.58 | 122.5845 | 122.5388 | 122.3602 | 122.4838 | 122.4884 | 122.5616 | 122.438 | 122.3602 | 122.4838 | 122.5616 | 122.5388 | 122.4884 | -0.032044 | -0.073242
2019.6875 | 122.6532 | -122.4792 | 0.004578 | -0.19264 | 0.0099996 | 0.0027877 | 0.031368 | -0.014887 | -0.0074085 | 0.01662 | 0.07782 | 0.027466 | 0.15106 | -0.059509 | 0.018311 | 0.041199 | 0.23804 | 0.16937 | 0.004578 | -0.086975 | 122.6303 | 0.022888 | 122.5571 | 122.4197 | 0.013733 | 122.3923 | 0 | -0.073242 | 122.7173 | 122.6486 | 122.4976 | 122.5067 | 122.5571 | 122.4838 | 122.5204 | 122.3923 | 122.5067 | 122.5571 | 122.5204 | 122.4976 | 122.4838 | 0.14648 | -0.091553
2021.3906 | 122.7219 | -122.4289 | -0.009155 | 0.059128 | 0.009786 | 0.00086511 | 0.034786 | -0.011897 | -0.010826 | 0.015125 | -0.11444 | -0.17853 | -0.064087 | -0.07782 | -0.009155 | 0.018311 | 0.086975 | -0.013733 | -0.004578 | -0.054932 | 122.3648 | -0.16937 | 122.3145 | 122.3511 | 0 | 122.374 | 0.004577 | -0.050354 | 122.5159 | 122.4152 | 122.4197 | 122.2504 | 122.3145 | 122.4243 | 122.4472 | 122.374 | 122.2504 | 122.3145 | 122.4472 | 122.4197 | 122.4243 | -0.054932 | -0.045777
2023.125 | 122.7402 | -122.4335 | 0.018311 | 0.13542 | 0.011495 | -0.0012711 | 0.033718 | -0.011042 | -0.0086901 | 0.018115 | -0.10986 | -0.17853 | -0.073242 | -0.073242 | 0 | 0.032043 | 0.054932 | -0.013733 | -0.004578 | -0.064087 | 122.3602 | -0.19684 | 122.3236 | 122.3602 | -0.018311 | 122.3694 | -0.022889 | -0.036621 | 122.4884 | 122.4197 | 122.4335 | 122.2549 | 122.3236 | 122.4289 | 122.4655 | 122.3694 | 122.2549 | 122.3236 | 122.4655 | 122.4335 | 122.4289 | -0.091553 | -0.082398
2024.8125 | 122.6074 | -122.4976 | 0.036621 | -0.10872 | 0.0076498 | -0.0010575 | 0.034145 | -0.012324 | -0.011467 | 0.01662 | 0.050354 | -0.054932 | 0.073242 | -0.013733 | 0.050354 | 0.07782 | 0.12817 | 0.16022 | 0.004578 | -0.059509 | 122.5708 | -0.091553 | 122.5479 | 122.4838 | 0.013733 | 122.438 | -0.032043 | -0.022888 | 122.6257 | 122.6578 | 122.5479 | 122.4426 | 122.5479 | 122.5021 | 122.5754 | 122.438 | 122.4426 | 122.5479 | 122.5754 | 122.5479 | 122.5021 | 0.036621 | -0.09613
2026.5156 | 122.6898 | -122.4518 | 0.013733 | 0.089645 | 0.0091452 | 0.0019333 | 0.030727 | -0.012324 | -0.0099719 | 0.018329 | -0.054932 | -0.21973 | -0.041199 | 0.022888 | 0.09613 | 0.15564 | -0.10529 | 0.13275 | -0.036621 | -0.013733 | 122.4106 | -0.23346 | 122.3969 | 122.4747 | 0.082397 | 122.438 | -0.050354 | -0.013733 | 122.3465 | 122.5845 | 122.5479 | 122.2321 | 122.3969 | 122.4152 | 122.6074 | 122.438 | 122.2321 | 122.3969 | 122.6074 | 122.5479 | 122.4152 | -0.054932 | -0.027466
2028.2188 | 122.7676 | -122.4609 | 0.004578 | 0.043869 | 0.0093588 | -0.0029801 | 0.026882 | -0.013392 | -0.0078357 | 0.015979 | 0.018311 | -0.14648 | 0.059509 | -0.027466 | 0.064087 | 0.10986 | 0.018311 | 0.14648 | -0.036621 | -0.036621 | 122.5204 | -0.15106 | 122.4792 | 122.4335 | 0.059509 | 122.4243 | -0.041199 | -0.041198 | 122.4792 | 122.6074 | 122.525 | 122.3145 | 122.4792 | 122.4243 | 122.5708 | 122.4243 | 122.3145 | 122.4792 | 122.5708 | 122.525 | 122.4243 | 0.054931 | -0.041199
2029.9531 | 122.7356 | -122.4472 | 0.004578 | 0.059128 | 0.0099996 | -0.00041649 | 0.033291 | -0.013392 | -0.010399 | 0.017902 | -0.11902 | -0.16937 | -0.073242 | -0.082397 | -0.018311 | 0.009155 | 0.073242 | -0.022888 | -0.009155 | -0.041199 | 122.374 | -0.17395 | 122.3282 | 122.3648 | -0.022889 | 122.406 | -0.013733 | -0.045777 | 122.5204 | 122.4243 | 122.4289 | 122.2778 | 122.3282 | 122.438 | 122.4564 | 122.406 | 122.2778 | 122.3282 | 122.4564 | 122.4289 | 122.438 | -0.07782 | -0.045777
2031.6406 | 122.7036 | -122.4838 | 0.036621 | 0.15831 | 0.010427 | 0.0010787 | 0.029232 | -0.01211 | -0.011681 | 0.01427 | 0.027466 | -0.16479 | 0.041199 | 0.045776 | 0.09613 | 0.16937 | -0.10529 | 0.15106 | -0.059509 | -0.041199 | 122.525 | -0.20142 | 122.5113 | 122.5296 | 0.059509 | 122.4426 | -0.09613 | -0.013733 | 122.3785 | 122.6349 | 122.58 | 122.319 | 122.5113 | 122.4243 | 122.6532 | 122.4426 | 122.319 | 122.5113 | 122.6532 | 122.58 | 122.4243 | 0.004578 | -0.07782
2033.3594 | 122.6944 | -122.4335 | 0.022888 | 0.15068 | 0.010641 | 0.00065151 | 0.032436 | -0.013392 | -0.0099719 | 0.018756 | 0.050354 | -0.1831 | 0.041199 | 0.054932 | 0.10986 | 0.1831 | -0.12817 | 0.15564 | -0.054932 | -0.018311 | 122.4747 | -0.20599 | 122.4838 | 122.4884 | 0.086975 | 122.4152 | -0.07782 | 0.009155 | 122.3053 | 122.5891 | 122.5433 | 122.2504 | 122.4838 | 122.3785 | 122.6166 | 122.4152 | 122.2504 | 122.4838 | 122.6166 | 122.5433 | 122.3785 | 0.018311 | -0.041199
2035.0469 | 122.644 | -122.4792 | 0.013733 | -0.055313 | 0.0085042 | -0.0029801 | 0.036068 | -0.012965 | -0.010613 | 0.017474 | 0.027466 | -0.091553 | 0.036621 | -0.004578 | 0.041199 | 0.068665 | 0.07782 | 0.1236 | -0.018311 | -0.041199 | 122.5159 | -0.10529 | 122.5067 | 122.4747 | 0.027466 | 122.438 | -0.032044 | -0.009155 | 122.5571 | 122.6028 | 122.5204 | 122.3877 | 122.5067 | 122.4609 | 122.5479 | 122.438 | 122.3877 | 122.5067 | 122.5479 | 122.5204 | 122.4609 | 0.022888 | -0.054932
2036.7188 | 122.731 | -122.4472 | 0.004578 | -0.017166 | 0.010641 | -0.0031937 | 0.027096 | -0.014247 | -0.0082629 | 0.019183 | 0.022888 | -0.12817 | 0.054932 | -0.013733 | 0.082397 | 0.13275 | -0.032043 | 0.12817 | -0.032043 | -0.032043 | 122.5021 | -0.13275 | 122.4701 | 122.4335 | 0.077819 | 122.4152 | -0.036621 | -0.032044 | 122.4152 | 122.5754 | 122.5296 | 122.319 | 122.4701 | 122.4152 | 122.58 | 122.4152 | 122.319 | 122.4701 | 122.58 | 122.5296 | 122.4152 | 0.050354 | -0.036621
2038.4688 | 122.7585 | -122.4701 | 0.009155 | 0.059128 | 0.0082906 | 0.0015061 | 0.031796 | -0.013392 | -0.0080493 | 0.01662 | 0.009155 | -0.17395 | 0.032043 | -0.004578 | 0.068665 | 0.10986 | -0.036621 | 0.1236 | -0.027466 | -0.032043 | 122.5021 | -0.1831 | 122.4792 | 122.4655 | 0.05951 | 122.4381 | -0.036621 | -0.022888 | 122.4335 | 122.5937 | 122.5388 | 122.2961 | 122.4792 | 122.4426 | 122.58 | 122.4381 | 122.2961 | 122.4792 | 122.58 | 122.5388 | 122.4426 | 0.022888 | -0.041198
2040.25 | 122.7402 | -122.4564 | 0.013733 | -0.032425 | 0.0078634 | 0.0015061 | 0.030087 | -0.017451 | -0.0056995 | 0.018543 | 0.022888 | -0.11902 | 0.068665 | 0.004578 | 0.086975 | 0.14648 | -0.022888 | 0.14648 | -0.027466 | -0.041199 | 122.525 | -0.13275 | 122.4792 | 122.4609 | 0.073242 | 122.4152 | -0.041199 | -0.045777 | 122.4335 | 122.6028 | 122.5433 | 122.3373 | 122.4792 | 122.4289 | 122.6028 | 122.4152 | 122.3373 | 122.4792 | 122.6028 | 122.5433 | 122.4289 | 0.054932 | -0.054932
2041.9531 | 122.6761 | -122.4838 | 0.022888 | -0.16975 | 0.010641 | 0.0019333 | 0.035427 | -0.015101 | -0.010826 | 0.018329 | 0.032043 | -0.032043 | 0.07782 | -0.059509 | 0.009155 | 0.036621 | 0.11444 | 0.041199 | 0.018311 | -0.059509 | 122.5616 | -0.054931 | 122.5159 | 122.4243 | -0.013733 | 122.4243 | -0.004577 | -0.045777 | 122.5983 | 122.525 | 122.493 | 122.4518 | 122.5159 | 122.5021 | 122.5204 | 122.4243 | 122.4518 | 122.5159 | 122.5204 | 122.493 | 122.5021 | 0.054932 | -0.082397
2043.7031 | 122.6166 | -122.5159 | 0.027466 | -0.09346 | 0.008718 | 1.071e-05 | 0.036923 | -0.011256 | -0.012963 | 0.016193 | 0.050354 | -0.09613 | 0.054932 | -0.004578 | 0.054932 | 0.082397 | 0.032043 | 0.10986 | -0.022888 | -0.045776 | 122.5708 | -0.1236 | 122.5662 | 122.5113 | 0.027466 | 122.4701 | -0.050354 | -0.004578 | 122.5479 | 122.6257 | 122.5708 | 122.4197 | 122.5662 | 122.493 | 122.5983 | 122.4701 | 122.4197 | 122.5662 | 122.5983 | 122.5708 | 122.493 | 0.027466 | -0.073242
2045.4531 | 122.6944 | -122.4701 | -0.009155 | 0.16594 | 0.0082906 | -0.0044755 | 0.031582 | -0.013392 | -0.010399 | 0.017688 | 0.036621 | -0.17853 | 0.032043 | 0.032043 | 0.10529 | 0.16022 | -0.11444 | 0.14648 | -0.050354 | -0.004578 | 122.5021 | -0.16937 | 122.5067 | 122.5021 | 0.11444 | 122.4655 | -0.041199 | 0.004578 | 122.3557 | 122.6166 | 122.5754 | 122.2916 | 122.5067 | 122.4197 | 122.6303 | 122.4655 | 122.2916 | 122.5067 | 122.6303 | 122.5754 | 122.4197 | 0.041198 | 0.004577
2047.1406 | 122.7493 | -122.4655 | 0.013733 | 0.097275 | 0.0078634 | -0.00020289 | 0.027737 | -0.01446 | -0.0089037 | 0.016406 | -0.018311 | -0.19226 | 0.022888 | -0.004578 | 0.073242 | 0.11902 | -0.045776 | 0.10529 | -0.022888 | -0.027466 | 122.4884 | -0.20599 | 122.4472 | 122.4609 | 0.059509 | 122.438 | -0.036621 | -0.041199 | 122.4197 | 122.5708 | 122.5388 | 122.2733 | 122.4472 | 122.4426 | 122.5845 | 122.438 | 122.2733 | 122.4472 | 122.5845 | 122.5388 | 122.4426 | 0.009155 | -0.041199
2048.875 | 122.6212 | -122.5204 | 0.027466 | -0.12398 | 0.0072226 | 1.071e-05 | 0.029873 | -0.014247 | -0.0054859 | 0.01662 | 0.10071 | -0.11902 | 0.073242 | 0.07782 | 0.14191 | 0.17395 | -0.07782 | 0.20142 | -0.041199 | -0.018311 | 122.5937 | -0.14649 | 122.6212 | 122.5983 | 0.11444 | 122.5021 | -0.068665 | 0.027466 | 122.4426 | 122.7219 | 122.6624 | 122.4014 | 122.6212 | 122.4792 | 122.6944 | 122.5021 | 122.4014 | 122.6212 | 122.6944 | 122.6624 | 122.4792 | 0.045776 | -0.045777
2050.625 | 122.6578 | -122.4701 | 0.013733 | -0.13924 | 0.0091452 | 0.0027877 | 0.035854 | -0.012751 | -0.011467 | 0.017474 | -0.009155 | -0.12817 | 0.009155 | -0.036621 | 0 | 0.036621 | 0.064087 | 0.036621 | -0.004578 | -0.050354 | 122.4792 | -0.14191 | 122.4609 | 122.4335 | -0.013733 | 122.4197 | -0.018311 | -0.01831 | 122.5342 | 122.5067 | 122.4701 | 122.3419 | 122.4609 | 122.4655 | 122.5067 | 122.4197 | 122.3419 | 122.4609 | 122.5067 | 122.4701 | 122.4655 | -0.004578 | -0.064087
2052.375 | 122.6166 | -122.525 | 0.032043 | -0.20027 | 0.0095724 | -0.0025529 | 0.029873 | -0.014887 | -0.0091173 | 0.015979 | 0.09613 | -0.10986 | 0.07782 | 0.059509 | 0.13275 | 0.16022 | -0.045776 | 0.18768 | -0.050354 | -0.022888 | 122.6028 | -0.14191 | 122.6212 | 122.5845 | 0.10071 | 122.5021 | -0.082397 | 0.01831 | 122.4792 | 122.7127 | 122.6578 | 122.4152 | 122.6212 | 122.4747 | 122.6852 | 122.5021 | 122.4152 | 122.6212 | 122.6852 | 122.6578 | 122.4747 | 0.045777 | -0.054931
2054.0469 | 122.6166 | -122.5067 | 0.036621 | -0.055313 | 0.0089316 | -0.0019119 | 0.033718 | -0.012751 | -0.011467 | 0.017261 | 0.013733 | -0.09613 | 0.018311 | 0.004578 | 0.050354 | 0.07782 | 0.041199 | 0.09613 | -0.013733 | -0.041199 | 122.525 | -0.13275 | 122.5204 | 122.5113 | 0.013733 | 122.4655 | -0.050354 | -0.004578 | 122.5479 | 122.6028 | 122.5571 | 122.4106 | 122.5204 | 122.493 | 122.5845 | 122.4655 | 122.4106 | 122.5204 | 122.5845 | 122.5571 | 122.493 | -0.01831 | -0.07782
2055.7812 | 122.6212 | -122.5113 | 0.041199 | -0.055313 | 0.0091452 | -0.0010575 | 0.033505 | -0.014247 | -0.011681 | 0.015125 | 0.032043 | -0.11902 | 0.032043 | 0.009155 | 0.073242 | 0.086975 | 0.027466 | 0.10529 | -0.009155 | -0.041199 | 122.5433 | -0.16022 | 122.5433 | 122.5204 | 0.032043 | 122.4701 | -0.050354 | 0 | 122.5388 | 122.6166 | 122.5845 | 122.3923 | 122.5433 | 122.5021 | 122.5983 | 122.4701 | 122.3923 | 122.5433 | 122.5983 | 122.5845 | 122.5021 | -0.009156 | -0.082398
2057.5312 | 122.6852 | -122.4564 | 0.009155 | 0.02861 | 0.0099996 | -0.0014847 | 0.032223 | -0.011683 | -0.0084765 | 0.020038 | -0.050354 | -0.12817 | 0 | -0.059509 | -0.009155 | 0.013733 | 0.068665 | 0.013733 | -0.013733 | -0.064087 | 122.4564 | -0.13733 | 122.406 | 122.3969 | -0.01831 | 122.3923 | -0.022888 | -0.050354 | 122.525 | 122.4701 | 122.4472 | 122.3282 | 122.406 | 122.4426 | 122.4701 | 122.3923 | 122.3282 | 122.406 | 122.4701 | 122.4472 | 122.4426 | -0.009155 | -0.073242
2059.2188 | 122.6898 | -122.4701 | 0.027466 | -0.12398 | 0.0089316 | -0.0059707 | 0.024746 | -0.014674 | -0.0063403 | 0.017474 | 0.041199 | -0.11444 | 0.086975 | 0.050354 | 0.1236 | 0.16479 | -0.073242 | 0.1831 | -0.054932 | -0.036621 | 122.5571 | -0.14191 | 122.5113 | 122.5204 | 0.09613 | 122.4335 | -0.082398 | -0.045776 | 122.3969 | 122.6532 | 122.5937 | 122.3557 | 122.5113 | 122.4152 | 122.6349 | 122.4335 | 122.3557 | 122.5113 | 122.6349 | 122.5937 | 122.4152 | 0.059509 | -0.064087
2060.9688 | 122.612 | -122.5021 | 0.022888 | -0.078201 | 0.0093588 | 0.0010787 | 0.032009 | -0.011897 | -0.012535 | 0.015552 | 0.032043 | -0.09613 | 0.027466 | 0 | 0.054932 | 0.07782 | 0.036621 | 0.10071 | 0 | -0.041199 | 122.5296 | -0.11902 | 122.5342 | 122.5021 | 0.032044 | 122.4609 | -0.022888 | 0.004577 | 122.5388 | 122.6028 | 122.5571 | 122.406 | 122.5342 | 122.5021 | 122.58 | 122.4609 | 122.406 | 122.5342 | 122.58 | 122.5571 | 122.5021 | 0.004578 | -0.064087
2062.7188 | 122.644 | -122.5021 | 0.045776 | -0.14687 | 0.010213 | -0.0010575 | 0.027737 | -0.014247 | -0.011254 | 0.017047 | 0.073242 | -0.09613 | 0.091553 | 0.041199 | 0.10986 | 0.14191 | -0.013733 | 0.16022 | -0.050354 | -0.041199 | 122.5937 | -0.14191 | 122.5754 | 122.5433 | 0.064087 | 122.4609 | -0.09613 | -0.018311 | 122.4884 | 122.6624 | 122.612 | 122.406 | 122.5754 | 122.4518 | 122.644 | 122.4609 | 122.406 | 122.5754 | 122.644 | 122.612 | 122.4518 | 0.045777 | -0.086975
2064.4688 | 122.6166 | -122.4976 | 0.036621 | -0.10109 | 0.010854 | 0.0034287 | 0.034786 | -0.01446 | -0.011467 | 0.017902 | 0.041199 | -0.086975 | 0.059509 | -0.004578 | 0.050354 | 0.068665 | 0.036621 | 0.09613 | -0.009155 | -0.050354 | 122.5571 | -0.1236 | 122.5388 | 122.493 | 0.013733 | 122.4472 | -0.045776 | -0.01831 | 122.5342 | 122.5937 | 122.5479 | 122.4106 | 122.5388 | 122.4884 | 122.5662 | 122.4472 | 122.4106 | 122.5388 | 122.5662 | 122.5479 | 122.4884 | 0.022888 | -0.086975
2066.1406 | 122.7631 | -122.4609 | 0.009155 | 0.013352 | 0.008077 | 0.0036423 | 0.028164 | -0.013606 | -0.0084765 | 0.01897 | -0.004578 | -0.14648 | 0.036621 | -0.022888 | 0.050354 | 0.11902 | -0.032043 | 0.10071 | -0.018311 | -0.036621 | 122.4976 | -0.15564 | 122.4564 | 122.438 | 0.041199 | 122.4243 | -0.027466 | -0.041199 | 122.4289 | 122.5616 | 122.5113 | 122.3145 | 122.4564 | 122.4426 | 122.58 | 122.4243 | 122.3145 | 122.4564 | 122.58 | 122.5113 | 122.4426 | 0.027466 | -0.045776
2067.875 | 122.6395 | -122.5021 | 0.041199 | -0.16975 | 0.0074362 | -0.0066117 | 0.029873 | -0.012751 | -0.010613 | 0.014911 | 0.09613 | -0.10986 | 0.086975 | 0.073242 | 0.12817 | 0.16937 | -0.045776 | 0.20142 | -0.041199 | -0.018311 | 122.5891 | -0.15106 | 122.5983 | 122.5754 | 0.086975 | 122.4838 | -0.082398 | 0.009155 | 122.4564 | 122.7036 | 122.6303 | 122.3923 | 122.5983 | 122.4609 | 122.6715 | 122.4838 | 122.3923 | 122.5983 | 122.6715 | 122.6303 | 122.4609 | 0.045776 | -0.05951
2069.625 | 122.6349 | -122.5159 | 0.032043 | -0.047684 | 0.007009 | 0.00022431 | 0.03735 | -0.012751 | -0.01339 | 0.017688 | 0.022888 | -0.11902 | 0.027466 | -0.013733 | 0.041199 | 0.059509 | 0.050354 | 0.064087 | -0.009155 | -0.050354 | 122.5433 | -0.15106 | 122.5388 | 122.5021 | 0.009156 | 122.4655 | -0.041198 | -0.004578 | 122.5662 | 122.58 | 122.5571 | 122.3969 | 122.5388 | 122.5067 | 122.5754 | 122.4655 | 122.3969 | 122.5388 | 122.5754 | 122.5571 | 122.5067 | -0.004577 | -0.082397
2071.3125 | 122.6761 | -122.4701 | 0.032043 | -0.17738 | 0.010854 | -0.0012711 | 0.032223 | -0.014247 | -0.010399 | 0.019183 | -0.004578 | -0.045776 | 0.054932 | -0.059509 | 0.022888 | 0.036621 | 0.11444 | 0.041199 | -0.004578 | -0.07782 | 122.525 | -0.077819 | 122.4655 | 122.4106 | -0.009155 | 122.3923 | -0.036621 | -0.05951 | 122.5845 | 122.5113 | 122.493 | 122.4243 | 122.4655 | 122.4655 | 122.5067 | 122.3923 | 122.4243 | 122.4655 | 122.5067 | 122.493 | 122.4655 | 0.022889 | -0.10986
2073.125 | 122.7173 | -122.4472 | -0.013733 | 0.1812 | 0.008718 | 0.0027877 | 0.033505 | -0.011042 | -0.010613 | 0.016406 | -0.054932 | -0.14648 | -0.022888 | -0.027466 | 0.050354 | 0.091553 | -0.022888 | 0.068665 | -0.022888 | -0.036621 | 122.4243 | -0.13275 | 122.3923 | 122.4197 | 0.064087 | 122.4106 | -0.009155 | -0.032044 | 122.4243 | 122.5159 | 122.4976 | 122.3007 | 122.3923 | 122.4243 | 122.5388 | 122.4106 | 122.3007 | 122.3923 | 122.5388 | 122.4976 | 122.4243 | -0.009155 | -0.022888
2074.8281 | 122.7859 | -122.4792 | 0.013733 | 0.051498 | 0.0093588 | -0.00041649 | 0.028378 | -0.015956 | -0.0082629 | 0.018329 | -0.018311 | -0.17395 | 0.004578 | -0.004578 | 0.073242 | 0.12817 | -0.036621 | 0.1236 | -0.045776 | -0.032043 | 122.4838 | -0.18768 | 122.4609 | 122.4747 | 0.059509 | 122.4472 | -0.059509 | -0.022889 | 122.4426 | 122.6028 | 122.5525 | 122.3053 | 122.4609 | 122.4335 | 122.6074 | 122.4472 | 122.3053 | 122.4609 | 122.6074 | 122.5525 | 122.4335 | -0.009155 | -0.045776
2076.5469 | 122.6486 | -122.5021 | 0.032043 | -0.070572 | 0.0091452 | 0.00086511 | 0.035427 | -0.012751 | -0.013604 | 0.017688 | 0.009155 | -0.12817 | 0.009155 | 0 | 0.054932 | 0.086975 | 0.022888 | 0.10071 | -0.018311 | -0.032043 | 122.5113 | -0.16022 | 122.5113 | 122.5021 | 0.022889 | 122.4701 | -0.050354 | 0 | 122.525 | 122.6028 | 122.5571 | 122.374 | 122.5113 | 122.4838 | 122.5891 | 122.4701 | 122.374 | 122.5113 | 122.5891 | 122.5571 | 122.4838 | -0.022888 | -0.064086
2078.2344 | 122.7676 | -122.4518 | 0 | 0.13542 | 0.011495 | -0.0031937 | 0.031368 | -0.014033 | -0.0089037 | 0.017688 | -0.073242 | -0.14191 | -0.013733 | -0.07782 | 0 | 0.027466 | 0.07782 | 0.032043 | 0.009155 | -0.054932 | 122.438 | -0.14191 | 122.3785 | 122.374 | 0 | 122.3969 | 0.009155 | -0.059509 | 122.5296 | 122.4838 | 122.4518 | 122.3099 | 122.3785 | 122.4609 | 122.4792 | 122.3969 | 122.3099 | 122.3785 | 122.4792 | 122.4518 | 122.4609 | -0.013733 | -0.054932
2079.9062 | 122.7493 | -122.4564 | 0.013733 | 0.12016 | 0.0091452 | -0.0036209 | 0.025814 | -0.014674 | -0.0082629 | 0.017688 | 0.009155 | -0.19684 | 0.009155 | 0.018311 | 0.10529 | 0.15564 | -0.07782 | 0.14191 | -0.045776 | -0.018311 | 122.4655 | -0.21057 | 122.4655 | 122.4747 | 0.091553 | 122.438 | -0.059509 | 0 | 122.3785 | 122.5983 | 122.5616 | 122.2595 | 122.4655 | 122.4106 | 122.612 | 122.438 | 122.2595 | 122.4655 | 122.612 | 122.5616 | 122.4106 | -0.004578 | -0.032044
2081.5938 | 122.6807 | -122.493 | 0 | -0.21553 | 0.0095724 | -0.0057571 | 0.032223 | -0.01446 | -0.011467 | 0.018329 | -0.027466 | -0.091553 | 0.027466 | -0.059509 | 0.004578 | 0.041199 | 0.11444 | 0.054932 | 0.009155 | -0.068665 | 122.5204 | -0.091553 | 122.4655 | 122.4335 | 0.004578 | 122.4243 | 0.009155 | -0.054932 | 122.6074 | 122.5479 | 122.4976 | 122.4014 | 122.4655 | 122.5021 | 122.5342 | 122.4243 | 122.4014 | 122.4655 | 122.5342 | 122.4976 | 122.5021 | 0.027466 | -0.068665
2083.2812 | 122.7036 | -122.4838 | 0.018311 | -0.20027 | 0.011068 | -0.0036209 | 0.030727 | -0.013392 | -0.010399 | 0.018756 | -0.004578 | -0.07782 | 0.045776 | -0.073242 | 0.009155 | 0.032043 | 0.1236 | 0.059509 | 0.009155 | -0.059509 | 122.5296 | -0.096131 | 122.4792 | 122.4106 | -0.009156 | 122.4243 | -0.009156 | -0.050354 | 122.6074 | 122.5433 | 122.493 | 122.406 | 122.4792 | 122.493 | 122.5159 | 122.4243 | 122.406 | 122.4792 | 122.5159 | 122.493 | 122.493 | 0.027465 | -0.07782
2085 | 122.6807 | -122.4976 | 0.009155 | 0.0057222 | 0.0078634 | -0.0010575 | 0.034145 | -0.011256 | -0.011254 | 0.01897 | -0.032043 | -0.12817 | 0.022888 | -0.059509 | 0.013733 | 0.041199 | 0.064087 | 0.027466 | -0.009155 | -0.059509 | 122.5204 | -0.13733 | 122.4655 | 122.438 | 0.004578 | 122.438 | -0.01831 | -0.054931 | 122.5616 | 122.525 | 122.5113 | 122.3694 | 122.4655 | 122.4884 | 122.5388 | 122.438 | 122.3694 | 122.4655 | 122.5388 | 122.5113 | 122.4884 | 0.013733 | -0.068664
2086.7031 | 122.7768 | -122.4472 | -0.004578 | 0.1049 | 0.010213 | 0.0010787 | 0.033291 | -0.011042 | -0.011467 | 0.017688 | -0.073242 | -0.15564 | 0 | -0.07782 | -0.013733 | 0.018311 | 0.068665 | 0 | -0.004578 | -0.059509 | 122.4472 | -0.15106 | 122.374 | 122.3694 | -0.009155 | 122.3877 | 0 | -0.073242 | 122.5159 | 122.4472 | 122.4335 | 122.2916 | 122.374 | 122.4426 | 122.4655 | 122.3877 | 122.2916 | 122.374 | 122.4655 | 122.4335 | 122.4426 | 0.004578 | -0.054931
2088.4531 | 122.6807 | -122.5113 | 0.018311 | -0.16975 | 0.0093588 | -0.0027665 | 0.030514 | -0.013819 | -0.0097583 | 0.016406 | -0.018311 | -0.073242 | 0.036621 | -0.068665 | 0.018311 | 0.041199 | 0.1236 | 0.054932 | -0.022888 | -0.059509 | 122.5479 | -0.091553 | 122.493 | 122.4426 | 0 | 122.4518 | -0.041199 | -0.054932 | 122.6349 | 122.5662 | 122.5296 | 122.4381 | 122.493 | 122.4884 | 122.5525 | 122.4518 | 122.4381 | 122.493 | 122.5525 | 122.5296 | 122.4884 | 0.01831 | -0.07782
2090.1562 | 122.7493 | -122.4976 | -0.013733 | 0.18883 | 0.0085042 | 0.0015061 | 0.031796 | -0.012751 | -0.011681 | 0.017902 | -0.064087 | -0.15106 | -0.009155 | -0.022888 | 0.050354 | 0.11902 | -0.050354 | 0.10529 | -0.045776 | -0.036621 | 122.4884 | -0.13733 | 122.4335 | 122.4747 | 0.064087 | 122.4609 | -0.032043 | -0.054932 | 122.4472 | 122.6028 | 122.5479 | 122.3465 | 122.4335 | 122.4518 | 122.6166 | 122.4609 | 122.3465 | 122.4335 | 122.6166 | 122.5479 | 122.4518 | 0.004578 | -0.022888
2091.8594 | 122.7539 | -122.4792 | 0.022888 | 0.097275 | 0.0076498 | -0.0027665 | 0.029018 | -0.012965 | -0.0076221 | 0.016406 | 0.018311 | -0.19226 | 0.022888 | 0.013733 | 0.11902 | 0.15106 | -0.07782 | 0.14191 | -0.032043 | 0.009155 | 122.5021 | -0.21515 | 122.4976 | 122.493 | 0.096131 | 122.4884 | -0.054931 | -0.004577 | 122.4014 | 122.6212 | 122.5983 | 122.287 | 122.4976 | 122.4472 | 122.6303 | 122.4884 | 122.287 | 122.4976 | 122.6303 | 122.5983 | 122.4472 | 0 | -0.013733
2093.5625 | 122.7859 | -122.4655 | 0.009155 | -0.0095368 | 0.0089316 | -0.00041649 | 0.027523 | -0.01446 | -0.0091173 | 0.016406 | -0.004578 | -0.14191 | 0.022888 | -0.004578 | 0.073242 | 0.13275 | -0.027466 | 0.14191 | -0.022888 | -0.045776 | 122.4884 | -0.15106 | 122.4609 | 122.4609 | 0.064087 | 122.4197 | -0.032043 | -0.027466 | 122.438 | 122.6074 | 122.5388 | 122.3236 | 122.4609 | 122.4426 | 122.5983 | 122.4197 | 122.3236 | 122.4609 | 122.5983 | 122.5388 | 122.4426 | 0.013733 | -0.054931
2095.25 | 122.699 | -122.5113 | 0.032043 | -0.11635 | 0.0085042 | -0.0021255 | 0.031796 | -0.01681 | -0.0095447 | 0.017261 | 0.018311 | -0.07782 | 0.045776 | -0.045776 | 0.022888 | 0.054932 | 0.10071 | 0.082397 | 0 | -0.054932 | 122.5571 | -0.10986 | 122.5296 | 122.4655 | -0.009155 | 122.4564 | -0.032043 | -0.027465 | 122.612 | 122.5937 | 122.5342 | 122.4335 | 122.5296 | 122.5113 | 122.5662 | 122.4564 | 122.4335 | 122.5296 | 122.5662 | 122.5342 | 122.5113 | 0.013733 | -0.086975
2096.9375 | 122.7722 | -122.4655 | 0 | 0.1049 | 0.011281 | -0.00063009 | 0.032436 | -0.012751 | -0.014244 | 0.015979 | -0.059509 | -0.14191 | -0.027466 | -0.068665 | 0 | 0.059509 | 0.018311 | 0.032043 | -0.009155 | -0.041199 | 122.438 | -0.14191 | 122.406 | 122.3969 | 0 | 122.4243 | -0.009155 | -0.032043 | 122.4838 | 122.4976 | 122.4655 | 122.3236 | 122.406 | 122.4564 | 122.525 | 122.4243 | 122.3236 | 122.406 | 122.525 | 122.4655 | 122.4564 | -0.027466 | -0.041199
2098.625 | 122.7493 | -122.4609 | -0.009155 | 0.14305 | 0.012563 | 0.0032151 | 0.034359 | -0.014033 | -0.011895 | 0.017474 | -0.054932 | -0.15564 | -0.032043 | -0.032043 | 0.022888 | 0.082397 | -0.022888 | 0.059509 | -0.022888 | -0.045776 | 122.4289 | -0.14649 | 122.406 | 122.4289 | 0.032043 | 122.4152 | -0.013733 | -0.022889 | 122.438 | 122.5204 | 122.4838 | 122.3053 | 122.406 | 122.438 | 122.5433 | 122.4152 | 122.3053 | 122.406 | 122.5433 | 122.4838 | 122.438 | -0.022888 | -0.036621
2100.2969 | 122.7081 | -122.493 | 0.036621 | -0.055313 | 0.010427 | -0.0034073 | 0.026669 | -0.014674 | -0.0084765 | 0.016193 | 0.059509 | -0.12817 | 0.073242 | 0.045776 | 0.12817 | 0.16479 | -0.068665 | 0.19684 | -0.036621 | -0.045776 | 122.5662 | -0.1648 | 122.5525 | 122.5388 | 0.091553 | 122.4472 | -0.073242 | -0.013733 | 122.4243 | 122.6898 | 122.6212 | 122.3648 | 122.5525 | 122.4564 | 122.6578 | 122.4472 | 122.3648 | 122.5525 | 122.6578 | 122.6212 | 122.4564 | 0.036621 | -0.082397
2102.0156 | 122.7448 | -122.4884 | 0.004578 | 0.15831 | 0.0089316 | -0.00020289 | 0.032223 | -0.015315 | -0.0097583 | 0.017047 | 0.018311 | -0.20599 | 0.013733 | 0.050354 | 0.11902 | 0.15564 | -0.10529 | 0.16937 | -0.059509 | -0.013733 | 122.5021 | -0.21057 | 122.5067 | 122.5388 | 0.11444 | 122.4747 | -0.064087 | 0.004578 | 122.3831 | 122.6578 | 122.6074 | 122.2824 | 122.5067 | 122.4289 | 122.644 | 122.4747 | 122.2824 | 122.5067 | 122.644 | 122.6074 | 122.4289 | 0.009155 | -0.018311
2103.75 | 122.6715 | -122.5159 | 0.032043 | -0.078201 | 0.0085042 | 0.0021469 | 0.033718 | -0.012324 | -0.011467 | 0.017047 | 0.050354 | -0.11902 | 0.041199 | 0 | 0.041199 | 0.073242 | 0.036621 | 0.082397 | 0.004578 | -0.050354 | 122.5571 | -0.15106 | 122.5662 | 122.5159 | 0.009156 | 122.4655 | -0.027465 | 0.009155 | 122.5525 | 122.5983 | 122.5571 | 122.3969 | 122.5662 | 122.5204 | 122.5891 | 122.4655 | 122.3969 | 122.5662 | 122.5891 | 122.5571 | 122.5204 | 0.009156 | -0.082397
2105.4375 | 122.7448 | -122.4792 | 0.022888 | -0.078201 | 0.008718 | -0.0066117 | 0.028164 | -0.013392 | -0.0089037 | 0.016406 | 0.032043 | -0.14191 | 0.045776 | 0.045776 | 0.11902 | 0.16022 | -0.045776 | 0.18768 | -0.050354 | -0.022888 | 122.525 | -0.16479 | 122.5113 | 122.525 | 0.096131 | 122.4564 | -0.073242 | -0.013733 | 122.4335 | 122.6669 | 122.5983 | 122.3373 | 122.5113 | 122.4289 | 122.6395 | 122.4564 | 122.3373 | 122.5113 | 122.6395 | 122.5983 | 122.4289 | 0.022888 | -0.045776
2107.1406 | 122.7631 | -122.4426 | 0.009155 | 0.1049 | 0.008077 | -0.00020289 | 0.03265 | -0.01211 | -0.0097583 | 0.017474 | 0.004578 | -0.07782 | 0.032043 | -0.045776 | 0.022888 | 0.064087 | 0.009155 | 0.036621 | -0.013733 | -0.050354 | 122.4747 | -0.086975 | 122.4472 | 122.3969 | 0.013733 | 122.3923 | -0.022888 | -0.027465 | 122.4518 | 122.4792 | 122.4655 | 122.3648 | 122.4472 | 122.4289 | 122.5067 | 122.3923 | 122.3648 | 122.4472 | 122.5067 | 122.4655 | 122.4289 | 0.022888 | -0.059509
2108.8906 | 122.6761 | -122.5388 | 0.032043 | -0.16975 | 0.0091452 | -0.0019119 | 0.029659 | -0.014887 | -0.011254 | 0.018329 | 0.086975 | -0.10529 | 0.073242 | 0.032043 | 0.09613 | 0.11902 | 0.013733 | 0.16479 | -0.018311 | -0.032043 | 122.612 | -0.13733 | 122.6257 | 122.5708 | 0.064087 | 122.5067 | -0.050354 | 0.013733 | 122.5525 | 122.7036 | 122.6349 | 122.4335 | 122.6257 | 122.5204 | 122.6578 | 122.5067 | 122.4335 | 122.6257 | 122.6578 | 122.6349 | 122.5204 | 0.041199 | -0.064086
2110.5625 | 122.7356 | -122.5113 | 0.004578 | 0.15831 | 0.0091452 | 0.00043791 | 0.030087 | -0.011683 | -0.010613 | 0.01897 | 0.09613 | -0.11902 | 0.07782 | 0.050354 | 0.10986 | 0.16022 | -0.10986 | 0.15106 | -0.036621 | -0.018311 | 122.5891 | -0.1236 | 122.6074 | 122.5616 | 0.10529 | 122.493 | -0.041199 | 0.01831 | 122.4014 | 122.6624 | 122.6212 | 122.3923 | 122.6074 | 122.4747 | 122.6715 | 122.493 | 122.3923 | 122.6074 | 122.6715 | 122.6212 | 122.4747 | 0.073242 | -0.022889
2112.2812 | 122.7402 | -122.4976 | 0.022888 | 0.1812 | 0.008077 | 0.0017197 | 0.03265 | -0.015315 | -0.0093311 | 0.017688 | 0.10071 | -0.12817 | 0.073242 | 0.050354 | 0.10986 | 0.16479 | -0.11902 | 0.16022 | -0.054932 | -0.022888 | 122.5708 | -0.15106 | 122.5983 | 122.5479 | 0.086975 | 122.4747 | -0.07782 | 0.027466 | 122.3785 | 122.6578 | 122.6074 | 122.3694 | 122.5983 | 122.4426 | 122.6624 | 122.4747 | 122.3694 | 122.5983 | 122.6624 | 122.6074 | 122.4426 | 0.050354 | -0.045776
2113.9688 | 122.7036 | -122.5296 | 0.032043 | -0.23842 | 0.0076498 | -0.00084389 | 0.030514 | -0.015315 | -0.0095447 | 0.017688 | -0.032043 | -0.059509 | 0.018311 | -0.064087 | 0.013733 | 0.032043 | 0.12817 | 0.059509 | 0.018311 | -0.073242 | 122.5479 | -0.091552 | 122.4976 | 122.4655 | -0.01831 | 122.4564 | -0.013732 | -0.050354 | 122.6578 | 122.5891 | 122.5433 | 122.4701 | 122.4976 | 122.5479 | 122.5616 | 122.4564 | 122.4701 | 122.4976 | 122.5616 | 122.5433 | 122.5479 | -0.013732 | -0.10529
2115.7031 | 122.7859 | -122.4747 | 0.018311 | 0.13542 | 0.010427 | 0.0012925 | 0.033718 | -0.013819 | -0.0095447 | 0.017261 | 0 | -0.082397 | 0.032043 | -0.064087 | -0.013733 | 0.045776 | 0.045776 | 0.027466 | 0.013733 | -0.064087 | 122.5067 | -0.10071 | 122.4747 | 122.4106 | -0.032044 | 122.4106 | -0.004578 | -0.032043 | 122.5204 | 122.5021 | 122.4609 | 122.3923 | 122.4747 | 122.4884 | 122.5204 | 122.4106 | 122.3923 | 122.4747 | 122.5204 | 122.4609 | 122.4884 | 0.013732 | -0.082398
2117.4062 | 122.7356 | -122.493 | 0.009155 | 0.066757 | 0.0099996 | -0.00084389 | 0.032864 | -0.014674 | -0.010613 | 0.017047 | 0.07782 | -0.10986 | 0.064087 | 0.041199 | 0.09613 | 0.15564 | -0.09613 | 0.13733 | -0.032043 | -0.018311 | 122.5571 | -0.11902 | 122.5708 | 122.5342 | 0.086975 | 122.4747 | -0.041198 | 0.013733 | 122.3969 | 122.6303 | 122.5891 | 122.3831 | 122.5708 | 122.4609 | 122.6486 | 122.4747 | 122.3831 | 122.5708 | 122.6486 | 122.5891 | 122.4609 | 0.054932 | -0.027466
2119.0938 | 122.7768 | -122.493 | -0.009155 | 0.12779 | 0.0093588 | -0.0016983 | 0.03265 | -0.014887 | -0.010826 | 0.016406 | -0.018311 | -0.07782 | 0.022888 | -0.07782 | -0.009155 | 0.018311 | 0.045776 | 0.009155 | 0.018311 | -0.045776 | 122.5159 | -0.068665 | 122.4747 | 122.4152 | 0 | 122.4472 | 0.027466 | -0.041199 | 122.5388 | 122.5021 | 122.4838 | 122.4152 | 122.4747 | 122.5113 | 122.5113 | 122.4472 | 122.4152 | 122.4747 | 122.5113 | 122.4838 | 122.5113 | 0.032043 | -0.036621
2120.7812 | 122.7448 | -122.4976 | 0.018311 | 0.12016 | 0.0072226 | -0.0021255 | 0.031155 | -0.014033 | -0.0080493 | 0.017474 | 0.082397 | -0.11444 | 0.091553 | 0.036621 | 0.10986 | 0.16479 | -0.10529 | 0.15564 | -0.050354 | -0.018311 | 122.5891 | -0.13275 | 122.58 | 122.5342 | 0.091552 | 122.4792 | -0.068665 | -0.009156 | 122.3923 | 122.6532 | 122.6074 | 122.3831 | 122.58 | 122.4472 | 122.6624 | 122.4792 | 122.3831 | 122.58 | 122.6624 | 122.6074 | 122.4472 | 0.073242 | -0.036622
2122.4688 | 122.7219 | -122.5113 | 0.004578 | 0.15831 | 0.0091452 | 0.0010787 | 0.0303 | -0.015101 | -0.010826 | 0.017261 | 0.091553 | -0.11902 | 0.082397 | 0.045776 | 0.10071 | 0.16022 | -0.10986 | 0.16022 | -0.045776 | -0.004578 | 122.5937 | -0.1236 | 122.6028 | 122.5571 | 0.09613 | 122.5067 | -0.050354 | 0.009156 | 122.4014 | 122.6715 | 122.612 | 122.3923 | 122.6028 | 122.4655 | 122.6715 | 122.5067 | 122.3923 | 122.6028 | 122.6715 | 122.612 | 122.4655 | 0.077819 | -0.009156
2124.1406 | 122.699 | -122.5204 | 0.022888 | 0.043869 | 0.010641 | -0.0023391 | 0.036068 | -0.012751 | -0.01104 | 0.016834 | 0 | -0.073242 | 0.050354 | -0.045776 | 0.004578 | 0.041199 | 0.059509 | 0.018311 | -0.018311 | -0.045776 | 122.5708 | -0.09613 | 122.5204 | 122.4747 | -0.01831 | 122.4747 | -0.041199 | -0.050354 | 122.58 | 122.5388 | 122.525 | 122.4472 | 122.5204 | 122.5021 | 122.5616 | 122.4747 | 122.4472 | 122.5204 | 122.5616 | 122.525 | 122.5021 | 0.027466 | -0.068664
2125.875 | 122.7264 | -122.5159 | 0.045776 | -0.21553 | 0.010427 | -0.00084389 | 0.030941 | -0.013606 | -0.0091173 | 0.015552 | -0.009155 | -0.068665 | 0.041199 | -0.068665 | 0.018311 | 0.054932 | 0.10071 | 0.07782 | -0.009155 | -0.073242 | 122.5571 | -0.11444 | 122.5067 | 122.4472 | -0.027465 | 122.4426 | -0.054931 | -0.050354 | 122.6166 | 122.5937 | 122.5342 | 122.4472 | 122.5067 | 122.5067 | 122.5708 | 122.4426 | 122.4472 | 122.5067 | 122.5708 | 122.5342 | 122.5067 | -0.004577 | -0.11902
2127.5625 | 122.7631 | -122.4976 | 0.013733 | 0.12779 | 0.0076498 | -0.0019119 | 0.028591 | -0.011683 | -0.010826 | 0.013843 | 0.09613 | -0.10986 | 0.068665 | 0.018311 | 0.11902 | 0.13733 | -0.064087 | 0.14191 | -0.041199 | -0.032043 | 122.5662 | -0.1236 | 122.5937 | 122.5159 | 0.10529 | 122.4655 | -0.054932 | 0.027465 | 122.4335 | 122.6395 | 122.6166 | 122.3877 | 122.5937 | 122.4564 | 122.6349 | 122.4655 | 122.3877 | 122.5937 | 122.6349 | 122.6166 | 122.4564 | 0.054932 | -0.045776
2129.25 | 122.6624 | -122.5342 | 0.041199 | -0.09346 | 0.010641 | -0.0012711 | 0.035427 | -0.013606 | -0.0097583 | 0.017261 | 0.032043 | -0.09613 | 0.041199 | 0 | 0.064087 | 0.086975 | 0.045776 | 0.10071 | 0 | -0.059509 | 122.5754 | -0.13733 | 122.5662 | 122.5342 | 0.022888 | 122.4747 | -0.041199 | -0.009156 | 122.58 | 122.6349 | 122.5983 | 122.4381 | 122.5662 | 122.5342 | 122.6212 | 122.4747 | 122.4381 | 122.5662 | 122.6212 | 122.5983 | 122.5342 | 0 | -0.10071
2130.9844 | 122.7631 | -122.5113 | 0.004578 | 0.12016 | 0.008718 | -0.0036209 | 0.030087 | -0.013606 | -0.0080493 | 0.018115 | 0.073242 | -0.13733 | 0.082397 | 0.036621 | 0.10986 | 0.15106 | -0.10529 | 0.14648 | -0.036621 | -0.022888 | 122.5937 | -0.14191 | 122.5845 | 122.5479 | 0.10529 | 122.4884 | -0.041199 | -0.009155 | 122.406 | 122.6578 | 122.6212 | 122.374 | 122.5845 | 122.4747 | 122.6624 | 122.4884 | 122.374 | 122.5845 | 122.6624 | 122.6212 | 122.4747 | 0.077819 | -0.027466
2132.6719 | 122.6532 | -122.5342 | 0.036621 | -0.14687 | 0.0082906 | -0.0038345 | 0.033077 | -0.014033 | -0.011254 | 0.017047 | 0.013733 | -0.086975 | 0.032043 | -0.013733 | 0.059509 | 0.068665 | 0.050354 | 0.10071 | -0.022888 | -0.050354 | 122.5662 | -0.1236 | 122.5479 | 122.5204 | 0.022888 | 122.4838 | -0.059509 | -0.01831 | 122.5845 | 122.6349 | 122.5937 | 122.4472 | 122.5479 | 122.5113 | 122.6028 | 122.4838 | 122.4472 | 122.5479 | 122.6028 | 122.5937 | 122.5113 | -0.004578 | -0.086975
2134.4062 | 122.7539 | -122.5113 | 0.018311 | 0.15831 | 0.010854 | -0.0027665 | 0.033291 | -0.011042 | -0.0095447 | 0.01897 | 0.032043 | -0.10071 | 0.059509 | -0.004578 | 0.07782 | 0.1236 | -0.059509 | 0.11444 | -0.036621 | -0.036621 | 122.5708 | -0.11902 | 122.5433 | 122.5067 | 0.059509 | 122.4747 | -0.054932 | -0.027466 | 122.4518 | 122.6257 | 122.5891 | 122.4106 | 122.5433 | 122.4747 | 122.6349 | 122.4747 | 122.4106 | 122.5433 | 122.6349 | 122.5891 | 122.4747 | 0.041198 | -0.054932
2136.1094 | 122.7814 | -122.5159 | -0.004578 | 0.074387 | 0.010854 | -0.0023391 | 0.032864 | -0.015315 | -0.0093311 | 0.018543 | -0.032043 | -0.086975 | 0.045776 | -0.068665 | -0.004578 | 0.027466 | 0.09613 | 0.004578 | -0.013733 | -0.059509 | 122.5616 | -0.082397 | 122.4838 | 122.4472 | 0 | 122.4564 | -0.009155 | -0.077819 | 122.612 | 122.5204 | 122.5113 | 122.4289 | 122.4838 | 122.5021 | 122.5433 | 122.4564 | 122.4289 | 122.4838 | 122.5433 | 122.5113 | 122.5021 | 0.050354 | -0.054931
2137.7969 | 122.7539 | -122.5067 | 0.013733 | 0.16594 | 0.0091452 | 0.0015061 | 0.031368 | -0.011256 | -0.010826 | 0.017688 | -0.022888 | -0.17853 | -0.013733 | -0.013733 | 0.064087 | 0.1236 | -0.050354 | 0.11902 | -0.050354 | -0.041199 | 122.493 | -0.19226 | 122.4838 | 122.493 | 0.050354 | 122.4655 | -0.064087 | -0.009155 | 122.4564 | 122.6257 | 122.5708 | 122.3282 | 122.4838 | 122.4564 | 122.6303 | 122.4655 | 122.3282 | 122.4838 | 122.6303 | 122.5708 | 122.4564 | -0.027466 | -0.054932
2139.4844 | 122.7081 | -122.525 | 0.018311 | -0.17738 | 0.0091452 | -0.0029801 | 0.029659 | -0.014674 | -0.012322 | 0.01662 | -0.013733 | -0.07782 | 0.022888 | -0.064087 | 0.022888 | 0.050354 | 0.11902 | 0.073242 | -0.013733 | -0.086975 | 122.5479 | -0.096131 | 122.5113 | 122.4609 | 0.004577 | 122.438 | -0.032044 | -0.036621 | 122.644 | 122.5983 | 122.5479 | 122.4472 | 122.5113 | 122.5113 | 122.5754 | 122.438 | 122.4472 | 122.5113 | 122.5754 | 122.5479 | 122.5113 | 0.004577 | -0.10529
2141.1719 | 122.6761 | -122.5662 | 0.022888 | -0.17738 | 0.0078634 | 0.0019333 | 0.025387 | -0.011256 | -0.0078357 | 0.016834 | 0.082397 | -0.13733 | 0.07782 | 0.054932 | 0.15564 | 0.16937 | -0.041199 | 0.20142 | -0.041199 | -0.013733 | 122.644 | -0.16022 | 122.6486 | 122.6212 | 0.13275 | 122.5525 | -0.064087 | 0.004577 | 122.525 | 122.7676 | 122.7219 | 122.4289 | 122.6486 | 122.525 | 122.7356 | 122.5525 | 122.4289 | 122.6486 | 122.7356 | 122.7219 | 122.525 | 0.054932 | -0.036621
2142.8594 | 122.6761 | -122.5433 | 0.032043 | -0.17738 | 0.0091452 | -0.0036209 | 0.0303 | -0.01446 | -0.010826 | 0.015552 | 0.10529 | -0.11444 | 0.07782 | 0.059509 | 0.11902 | 0.16937 | -0.041199 | 0.19226 | -0.032043 | -0.018311 | 122.6212 | -0.14648 | 122.6486 | 122.6028 | 0.086976 | 122.525 | -0.064086 | 0.027466 | 122.5021 | 122.7356 | 122.6624 | 122.4289 | 122.6486 | 122.5113 | 122.7127 | 122.525 | 122.4289 | 122.6486 | 122.7127 | 122.6624 | 122.5113 | 0.045777 | -0.050354
2144.5469 | 122.7219 | -122.5296 | 0.018311 | -0.040054 | 0.008077 | -0.0010575 | 0.033077 | -0.014247 | -0.010186 | 0.017688 | 0 | -0.07782 | 0.032043 | -0.045776 | 0.013733 | 0.041199 | 0.10986 | 0.07782 | 0.004578 | -0.050354 | 122.5616 | -0.096131 | 122.5296 | 122.4838 | -0.004578 | 122.4792 | -0.013733 | -0.032043 | 122.6395 | 122.6074 | 122.5433 | 122.4518 | 122.5296 | 122.5342 | 122.5708 | 122.4792 | 122.4518 | 122.5296 | 122.5708 | 122.5433 | 122.5342 | 0.013732 | -0.068665
2146.25 | 122.8043 | -122.4976 | 0.009155 | -0.017166 | 0.0095724 | 0.00043791 | 0.029232 | -0.016169 | -0.0082629 | 0.017902 | 0.036621 | -0.11444 | 0.064087 | 0.009155 | 0.086975 | 0.12817 | -0.032043 | 0.13275 | -0.027466 | -0.022888 | 122.5616 | -0.1236 | 122.5342 | 122.5067 | 0.07782 | 122.4747 | -0.036621 | -0.027466 | 122.4655 | 122.6303 | 122.5845 | 122.3831 | 122.5342 | 122.4701 | 122.6257 | 122.4747 | 122.3831 | 122.5342 | 122.6257 | 122.5845 | 122.4701 | 0.054932 | -0.032043
2147.9844 | 122.6898 | -122.5433 | 0.036621 | -0.11635 | 0.0072226 | -0.0040481 | 0.032009 | -0.015528 | -0.0089037 | 0.018543 | 0.10529 | -0.10986 | 0.073242 | 0.064087 | 0.14648 | 0.18768 | -0.082397 | 0.2243 | -0.041199 | -0.018311 | 122.6166 | -0.14648 | 122.6486 | 122.6074 | 0.10986 | 122.525 | -0.07782 | 0.032044 | 122.4609 | 122.7676 | 122.6898 | 122.4335 | 122.6486 | 122.5021 | 122.731 | 122.525 | 122.4335 | 122.6486 | 122.731 | 122.6898 | 122.5021 | 0.036621 | -0.054932
2149.6875 | 122.6898 | -122.5433 | 0.018311 | -0.16975 | 0.010641 | -0.00084389 | 0.035214 | -0.012538 | -0.011254 | 0.017047 | -0.004578 | -0.086975 | 0.032043 | -0.027466 | 0.032043 | 0.045776 | 0.082397 | 0.07782 | -0.004578 | -0.045776 | 122.5754 | -0.10529 | 122.5388 | 122.5159 | 0.013732 | 122.4976 | -0.022889 | -0.036621 | 122.6257 | 122.6212 | 122.5754 | 122.4564 | 122.5388 | 122.5388 | 122.5891 | 122.4976 | 122.4564 | 122.5388 | 122.5891 | 122.5754 | 122.5388 | 0.013732 | -0.064087
2151.375 | 122.699 | -122.5616 | 0.022888 | -0.09346 | 0.007009 | 0.0012925 | 0.028591 | -0.014247 | -0.0097583 | 0.015552 | 0.09613 | -0.091553 | 0.091553 | 0.073242 | 0.16479 | 0.17853 | -0.041199 | 0.20599 | -0.041199 | -0.018311 | 122.6532 | -0.11444 | 122.6578 | 122.6349 | 0.14191 | 122.5433 | -0.064087 | 0.004577 | 122.5204 | 122.7676 | 122.7264 | 122.4701 | 122.6578 | 122.5204 | 122.7402 | 122.5433 | 122.4701 | 122.6578 | 122.7402 | 122.7264 | 122.5204 | 0.068665 | -0.041199
2153.0781 | 122.7676 | -122.5021 | 0.013733 | -0.055313 | 0.009786 | -0.0014847 | 0.028591 | -0.015101 | -0.0095447 | 0.017688 | 0.064087 | -0.10071 | 0.073242 | 0.032043 | 0.11444 | 0.14648 | -0.036621 | 0.16937 | -0.036621 | -0.032043 | 122.5754 | -0.11444 | 122.5662 | 122.5342 | 0.10071 | 122.4701 | -0.050354 | -0.009155 | 122.4655 | 122.6715 | 122.6166 | 122.4014 | 122.5662 | 122.4655 | 122.6486 | 122.4701 | 122.4014 | 122.5662 | 122.6486 | 122.6166 | 122.4655 | 0.059509 | -0.045776
2154.7656 | 122.7173 | -122.5433 | 0.032043 | -0.20027 | 0.0078634 | 0.00022431 | 0.033505 | -0.015742 | -0.0091173 | 0.015765 | 0.013733 | -0.10071 | 0.068665 | -0.027466 | 0.041199 | 0.059509 | 0.091553 | 0.07782 | -0.022888 | -0.050354 | 122.612 | -0.13275 | 122.5571 | 122.5159 | 0.009156 | 122.493 | -0.054931 | -0.054932 | 122.6349 | 122.6212 | 122.5845 | 122.4426 | 122.5571 | 122.5204 | 122.6028 | 122.493 | 122.4426 | 122.5571 | 122.6028 | 122.5845 | 122.5204 | 0.036622 | -0.082397
2156.4531 | 122.8043 | -122.5067 | 0.004578 | 0.059128 | 0.008718 | 0.00065151 | 0.031796 | -0.014887 | -0.0097583 | 0.018115 | 0.054932 | -0.11444 | 0.086975 | -0.004578 | 0.073242 | 0.11902 | -0.045776 | 0.11902 | -0.032043 | -0.036621 | 122.5937 | -0.11902 | 122.5616 | 122.5021 | 0.068664 | 122.4701 | -0.036621 | -0.032043 | 122.4609 | 122.6257 | 122.58 | 122.3923 | 122.5616 | 122.4747 | 122.6257 | 122.4701 | 122.3923 | 122.5616 | 122.6257 | 122.58 | 122.4747 | 0.082397 | -0.041199
2158.1406 | 122.7814 | -122.5159 | 0.009155 | -0.047684 | 0.0099996 | 0.0021469 | 0.028805 | -0.016169 | -0.0080493 | 0.017688 | 0.050354 | -0.086975 | 0.068665 | 0.022888 | 0.10071 | 0.15564 | -0.054932 | 0.17395 | -0.032043 | -0.041199 | 122.5845 | -0.09613 | 122.5662 | 122.5388 | 0.091553 | 122.4747 | -0.041198 | -0.018311 | 122.4609 | 122.6898 | 122.6166 | 122.4289 | 122.5662 | 122.4838 | 122.6715 | 122.4747 | 122.4289 | 122.5662 | 122.6715 | 122.6166 | 122.4838 | 0.05951 | -0.050354
2159.8438 | 122.8134 | -122.5296 | 0.004578 | 0.020981 | 0.0099996 | 0.0010787 | 0.032864 | -0.015101 | -0.0082629 | 0.016193 | 0.059509 | -0.13275 | 0.07782 | 0.009155 | 0.07782 | 0.11902 | -0.036621 | 0.1236 | -0.036621 | -0.022888 | 122.6074 | -0.13733 | 122.5891 | 122.5388 | 0.073242 | 122.5067 | -0.041199 | -0.018311 | 122.493 | 122.6532 | 122.6074 | 122.3969 | 122.5891 | 122.493 | 122.6486 | 122.5067 | 122.3969 | 122.5891 | 122.6486 | 122.6074 | 122.493 | 0.073242 | -0.027466
2161.5312 | 122.7493 | -122.5113 | 0.004578 | 0.18883 | 0.0085042 | -0.00084389 | 0.036495 | -0.015101 | -0.012108 | 0.016834 | 0.036621 | -0.10071 | 0.050354 | 0.045776 | 0.07782 | 0.14648 | -0.091553 | 0.1236 | -0.027466 | -0.036621 | 122.5616 | -0.10529 | 122.5479 | 122.5571 | 0.073242 | 122.4747 | -0.032044 | -0.013733 | 122.4197 | 122.6349 | 122.5891 | 122.4106 | 122.5479 | 122.4838 | 122.6578 | 122.4747 | 122.4106 | 122.5479 | 122.6578 | 122.5891 | 122.4838 | 0.045776 | -0.041199
2163.2344 | 122.818 | -122.5021 | 0 | 0.12779 | 0.0091452 | -0.00084389 | 0.034786 | -0.015101 | -0.0093311 | 0.017902 | -0.018311 | -0.091553 | 0.032043 | -0.068665 | -0.022888 | 0.032043 | 0.068665 | 0.022888 | 0 | -0.064087 | 122.5342 | -0.091553 | 122.4838 | 122.4335 | -0.022888 | 122.438 | 0 | -0.050354 | 122.5708 | 122.525 | 122.4792 | 122.4106 | 122.4838 | 122.5021 | 122.5342 | 122.438 | 122.4106 | 122.4838 | 122.5342 | 122.4792 | 122.5021 | 0.032043 | -0.064087
2164.9531 | 122.6944 | -122.5296 | 0.022888 | -0.032425 | 0.010854 | 0.0032151 | 0.035214 | -0.014887 | -0.010399 | 0.015979 | 0.036621 | -0.07782 | 0.041199 | -0.009155 | 0.045776 | 0.059509 | 0.036621 | 0.064087 | -0.004578 | -0.059509 | 122.5708 | -0.10071 | 122.5662 | 122.5204 | 0.022888 | 122.4701 | -0.027466 | -0.004578 | 122.5662 | 122.5937 | 122.5754 | 122.4518 | 122.5662 | 122.525 | 122.5891 | 122.4701 | 122.4518 | 122.5662 | 122.5891 | 122.5754 | 122.525 | 0.018311 | -0.082397
2166.6406 | 122.7264 | -122.525 | 0.032043 | -0.16212 | 0.0099996 | -0.0021255 | 0.031155 | -0.013178 | -0.010186 | 0.018329 | 0.004578 | -0.07782 | 0.041199 | -0.064087 | 0.013733 | 0.041199 | 0.10529 | 0.050354 | 0.013733 | -0.082397 | 122.5662 | -0.10986 | 122.5296 | 122.4609 | -0.01831 | 122.4426 | -0.01831 | -0.036621 | 122.6303 | 122.5754 | 122.5388 | 122.4472 | 122.5296 | 122.5388 | 122.5662 | 122.4426 | 122.4472 | 122.5296 | 122.5662 | 122.5388 | 122.5388 | 0.009156 | -0.11444
2168.3594 | 122.7951 | -122.4838 | -0.013733 | 0.089645 | 0.011281 | 0.00043791 | 0.03265 | -0.014674 | -0.0099719 | 0.018543 | -0.004578 | -0.07782 | 0.041199 | -0.068665 | 0.018311 | 0.064087 | 0.018311 | 0.036621 | -0.013733 | -0.050354 | 122.525 | -0.064087 | 122.4792 | 122.4152 | 0.032044 | 122.4335 | 0 | -0.045777 | 122.5021 | 122.5204 | 122.5021 | 122.406 | 122.4792 | 122.4701 | 122.5479 | 122.4335 | 122.406 | 122.4792 | 122.5479 | 122.5021 | 122.4701 | 0.054932 | -0.036621
2170.0625 | 122.7997 | -122.4884 | -0.009155 | 0.12779 | 0.009786 | 0.0023605 | 0.034145 | -0.010401 | -0.0099719 | 0.017261 | 0.009155 | -0.086975 | 0.045776 | -0.050354 | 0.036621 | 0.07782 | -0.009155 | 0.045776 | -0.018311 | -0.041199 | 122.5342 | -0.07782 | 122.4976 | 122.438 | 0.045776 | 122.4472 | -0.009156 | -0.036621 | 122.4792 | 122.5342 | 122.525 | 122.4014 | 122.4976 | 122.4701 | 122.5662 | 122.4472 | 122.4014 | 122.4976 | 122.5662 | 122.525 | 122.4701 | 0.054931 | -0.032044
2171.75 | 122.8134 | -122.5159 | 0.004578 | -0.0095368 | 0.0078634 | -0.0029801 | 0.025601 | -0.014247 | -0.0099719 | 0.017902 | 0.027466 | -0.10986 | 0.064087 | 0.013733 | 0.086975 | 0.11902 | -0.027466 | 0.1236 | -0.041199 | -0.041199 | 122.58 | -0.11444 | 122.5433 | 122.5296 | 0.082397 | 122.4747 | -0.045777 | -0.036621 | 122.4884 | 122.6395 | 122.6028 | 122.406 | 122.5433 | 122.4747 | 122.6349 | 122.4747 | 122.406 | 122.5433 | 122.6349 | 122.6028 | 122.4747 | 0.059509 | -0.045777
2173.4844 | 122.8134 | -122.5067 | -0.009155 | 0.13542 | 0.010641 | -0.0010575 | 0.034145 | -0.012751 | -0.010613 | 0.017047 | -0.009155 | -0.07782 | 0.022888 | -0.073242 | 0 | 0.050354 | 0.082397 | 0.022888 | 0 | -0.059509 | 122.5296 | -0.068665 | 122.4976 | 122.4335 | 0.009155 | 122.4472 | 0.009155 | -0.032043 | 122.5891 | 122.5296 | 122.5067 | 122.4289 | 122.4976 | 122.5067 | 122.5571 | 122.4472 | 122.4289 | 122.4976 | 122.5571 | 122.5067 | 122.5067 | 0.032043 | -0.050354
2175.1719 | 122.7127 | -122.5571 | 0.041199 | -0.18501 | 0.008077 | 0.00043791 | 0.029232 | -0.014674 | -0.011467 | 0.016834 | 0.054932 | -0.11444 | 0.068665 | 0.018311 | 0.11444 | 0.11902 | 0.027466 | 0.15564 | -0.027466 | -0.045776 | 122.6257 | -0.15564 | 122.612 | 122.5754 | 0.073242 | 122.5113 | -0.068665 | -0.013733 | 122.5845 | 122.7127 | 122.6715 | 122.4426 | 122.612 | 122.5296 | 122.6761 | 122.5113 | 122.4426 | 122.612 | 122.6761 | 122.6715 | 122.5296 | 0.027466 | -0.086975
2176.9219 | 122.731 | -122.5525 | 0.018311 | -0.2079 | 0.008718 | -0.0027665 | 0.032223 | -0.015315 | -0.010826 | 0.018756 | 0.013733 | -0.10986 | 0.032043 | -0.045776 | 0.032043 | 0.068665 | 0.082397 | 0.082397 | 0 | -0.050354 | 122.5845 | -0.12817 | 122.5662 | 122.5067 | 0.013732 | 122.5021 | -0.018311 | -0.01831 | 122.6349 | 122.6349 | 122.5845 | 122.4426 | 122.5662 | 122.5525 | 122.6212 | 122.5021 | 122.4426 | 122.5662 | 122.6212 | 122.5845 | 122.5525 | 0.013732 | -0.068665
2178.625 | 122.6624 | -122.5388 | 0.032043 | -0.09346 | 0.0095724 | 0.00065151 | 0.035 | -0.011897 | -0.012108 | 0.016406 | 0.027466 | -0.091553 | 0.018311 | 0.009155 | 0.059509 | 0.073242 | 0.045776 | 0.091553 | -0.013733 | -0.050354 | 122.5571 | -0.1236 | 122.5662 | 122.5479 | 0.027466 | 122.4884 | -0.045776 | 0.009155 | 122.5845 | 122.6303 | 122.5983 | 122.4472 | 122.5662 | 122.525 | 122.612 | 122.4884 | 122.4472 | 122.5662 | 122.612 | 122.5983 | 122.525 | -0.013732 | -0.082397
2180.3125 | 122.7448 | -122.5525 | 0.018311 | -0.2079 | 0.0072226 | 0.00065151 | 0.029873 | -0.013392 | -0.0099719 | 0.016406 | -0.004578 | -0.073242 | 0.022888 | -0.064087 | 0.013733 | 0.041199 | 0.13275 | 0.054932 | 0.009155 | -0.050354 | 122.5754 | -0.091553 | 122.5479 | 122.4884 | -0.004578 | 122.5021 | -0.009156 | -0.027466 | 122.6852 | 122.6074 | 122.5662 | 122.4792 | 122.5479 | 122.5616 | 122.5937 | 122.5021 | 122.4792 | 122.5479 | 122.5937 | 122.5662 | 122.5616 | 0.004577 | -0.068665
2182.0156 | 122.7814 | -122.525 | 0.004578 | 0.12016 | 0.0082906 | 0.0030013 | 0.029232 | -0.013606 | -0.01104 | 0.017688 | 0.091553 | -0.11902 | 0.10071 | 0.036621 | 0.10986 | 0.17853 | -0.10071 | 0.16022 | -0.045776 | -0.009155 | 122.6257 | -0.1236 | 122.6166 | 122.5616 | 0.10529 | 122.5159 | -0.050354 | -0.009155 | 122.4243 | 122.6852 | 122.6349 | 122.406 | 122.6166 | 122.4792 | 122.7036 | 122.5159 | 122.406 | 122.6166 | 122.7036 | 122.6349 | 122.4792 | 0.09613 | -0.013733
2183.7188 | 122.7402 | -122.5388 | 0.013733 | -0.18501 | 0.0067954 | 0.00065151 | 0.0303 | -0.01446 | -0.010186 | 0.017474 | -0.032043 | -0.086975 | 0.032043 | -0.054932 | 0.013733 | 0.036621 | 0.14191 | 0.064087 | 0.027466 | -0.054932 | 122.5708 | -0.10071 | 122.5067 | 122.4838 | 0 | 122.4838 | 0.013733 | -0.064086 | 122.6807 | 122.6028 | 122.5525 | 122.4518 | 122.5067 | 122.5662 | 122.5754 | 122.4838 | 122.4518 | 122.5067 | 122.5754 | 122.5525 | 122.5662 | 0.01831 | -0.068665
2185.4531 | 122.7768 | -122.5159 | 0.004578 | 0.15068 | 0.0093588 | -0.00063009 | 0.031796 | -0.013178 | -0.0093311 | 0.018543 | 0.07782 | -0.10529 | 0.064087 | 0.036621 | 0.10529 | 0.15564 | -0.082397 | 0.15106 | -0.041199 | 0.009155 | 122.58 | -0.10986 | 122.5937 | 122.5525 | 0.10071 | 122.525 | -0.045777 | 0.013733 | 122.4335 | 122.6669 | 122.6212 | 122.4106 | 122.5937 | 122.4747 | 122.6715 | 122.525 | 122.4106 | 122.5937 | 122.6715 | 122.6212 | 122.4747 | 0.059509 | 0.004577
2187.1719 | 122.7219 | -122.5571 | 0.018311 | 0.020981 | 0.011068 | 0.00022431 | 0.033505 | -0.01446 | -0.012535 | 0.017047 | 0.013733 | -0.07782 | 0.041199 | -0.032043 | 0.027466 | 0.050354 | 0.086975 | 0.045776 | 0.013733 | -0.032043 | 122.5983 | -0.096131 | 122.5708 | 122.525 | 0.009155 | 122.525 | -0.004578 | -0.027466 | 122.644 | 122.6028 | 122.5845 | 122.4792 | 122.5708 | 122.5708 | 122.6074 | 122.525 | 122.4792 | 122.5708 | 122.6074 | 122.5845 | 122.5708 | 0.022888 | -0.050354
2188.9375 | 122.7036 | -122.5525 | 0.036621 | -0.070572 | 0.0095724 | -0.0021255 | 0.035 | -0.012965 | -0.012535 | 0.01662 | 0.041199 | -0.09613 | 0.027466 | 0 | 0.073242 | 0.10071 | 0.041199 | 0.10529 | -0.018311 | -0.036621 | 122.58 | -0.13275 | 122.5937 | 122.5525 | 0.036621 | 122.5159 | -0.054932 | 0.013733 | 122.5937 | 122.6578 | 122.6257 | 122.4564 | 122.5937 | 122.5342 | 122.6532 | 122.5159 | 122.4564 | 122.5937 | 122.6532 | 122.6257 | 122.5342 | -0.009155 | -0.073242
2190.7031 | 122.8226 | -122.5021 | -0.004578 | -0.0095368 | 0.0089316 | -0.00063009 | 0.025814 | -0.012751 | -0.0065539 | 0.016834 | 0.045776 | -0.10529 | 0.082397 | -0.013733 | 0.086975 | 0.14191 | -0.027466 | 0.14648 | -0.027466 | -0.032043 | 122.5845 | -0.10071 | 122.5479 | 122.4884 | 0.091553 | 122.4701 | -0.022888 | -0.036621 | 122.4747 | 122.6486 | 122.5891 | 122.3968 | 122.5479 | 122.4747 | 122.644 | 122.4701 | 122.3968 | 122.5479 | 122.644 | 122.5891 | 122.4747 | 0.086975 | -0.027465
2192.5 | 122.8317 | -122.525 | 0.004578 | 0.12779 | 0.008718 | -0.00041649 | 0.032223 | -0.013392 | -0.010186 | 0.018756 | -0.018311 | -0.068665 | 0.036621 | -0.073242 | -0.004578 | 0.036621 | 0.073242 | 0.027466 | -0.004578 | -0.054932 | 122.5616 | -0.073243 | 122.5067 | 122.4518 | -0.009156 | 122.4701 | -0.009156 | -0.054932 | 122.5983 | 122.5525 | 122.5204 | 122.4564 | 122.5067 | 122.5204 | 122.5616 | 122.4701 | 122.4564 | 122.5067 | 122.5616 | 122.5204 | 122.5204 | 0.032043 | -0.05951
2194.2344 | 122.8043 | -122.5342 | 0.022888 | -0.032425 | 0.0067954 | -0.0021255 | 0.029873 | -0.015956 | -0.0089037 | 0.017474 | 0.059509 | -0.11902 | 0.068665 | 0.022888 | 0.10071 | 0.14191 | -0.036621 | 0.17853 | -0.018311 | -0.045776 | 122.6028 | -0.14191 | 122.5937 | 122.5571 | 0.07782 | 122.4884 | -0.041199 | -0.009156 | 122.4976 | 122.7127 | 122.6349 | 122.4152 | 122.5937 | 122.5159 | 122.6761 | 122.4884 | 122.4152 | 122.5937 | 122.6761 | 122.6349 | 122.5159 | 0.045777 | -0.068664
2195.9688 | 122.8363 | -122.5342 | 0.009155 | 0.043869 | 0.008077 | -0.0021255 | 0.029018 | -0.01446 | -0.0082629 | 0.017688 | 0.036621 | -0.10986 | 0.059509 | -0.009155 | 0.064087 | 0.1236 | -0.032043 | 0.11902 | -0.041199 | -0.027466 | 122.5937 | -0.11902 | 122.5708 | 122.525 | 0.054932 | 122.5067 | -0.050354 | -0.022888 | 122.5021 | 122.6532 | 122.5983 | 122.4243 | 122.5708 | 122.493 | 122.6578 | 122.5067 | 122.4243 | 122.5708 | 122.6578 | 122.5983 | 122.493 | 0.050354 | -0.036621
2197.6875 | 122.7814 | -122.5204 | -0.004578 | 0.13542 | 0.009786 | -0.0029801 | 0.033291 | -0.011897 | -0.010399 | 0.017047 | 0.009155 | -0.09613 | 0.041199 | -0.032043 | 0.032043 | 0.068665 | -0.013733 | 0.068665 | -0.018311 | -0.050354 | 122.5616 | -0.091552 | 122.5296 | 122.4884 | 0.036621 | 122.4701 | -0.013733 | -0.032044 | 122.5067 | 122.5891 | 122.5525 | 122.4243 | 122.5296 | 122.5021 | 122.5891 | 122.4701 | 122.4243 | 122.5296 | 122.5891 | 122.5525 | 122.5021 | 0.045777 | -0.045776
2199.375 | 122.6944 | -122.5708 | 0.013733 | -0.12398 | 0.0093588 | -0.00084389 | 0.034359 | -0.013819 | -0.01104 | 0.016193 | 0.004578 | -0.068665 | 0.027466 | -0.027466 | 0.045776 | 0.073242 | 0.064087 | 0.09613 | -0.009155 | -0.064087 | 122.5983 | -0.082398 | 122.5754 | 122.5433 | 0.032043 | 122.5067 | -0.022888 | -0.022888 | 122.6349 | 122.6669 | 122.6166 | 122.5021 | 122.5754 | 122.5616 | 122.644 | 122.5067 | 122.5021 | 122.5754 | 122.644 | 122.6166 | 122.5616 | 0.013733 | -0.07782
2201.0938 | 122.7127 | -122.5708 | 0.027466 | -0.040054 | 0.0089316 | -0.00063009 | 0.034786 | -0.012324 | -0.011681 | 0.017902 | -0.059509 | -0.17853 | -0.041199 | -0.041199 | 0.018311 | 0.064087 | 0.036621 | 0.059509 | 0.004578 | -0.045776 | 122.5296 | -0.20599 | 122.5113 | 122.5296 | -0.009155 | 122.525 | -0.022888 | -0.01831 | 122.6074 | 122.6303 | 122.5891 | 122.3923 | 122.5113 | 122.5754 | 122.6349 | 122.525 | 122.3923 | 122.5113 | 122.6349 | 122.5891 | 122.5754 | -0.068665 | -0.073242
2202.8125 | 122.7814 | -122.5296 | 0.018311 | 0.16594 | 0.0065816 | 0.00043791 | 0.031368 | -0.013819 | -0.0076221 | 0.019824 | -0.054932 | -0.25635 | -0.059509 | 0.036621 | 0.11444 | 0.15564 | -0.086975 | 0.16022 | -0.054932 | -0.022888 | 122.4701 | -0.27466 | 122.4747 | 122.5662 | 0.09613 | 122.5067 | -0.073243 | 0.004577 | 122.4426 | 122.6898 | 122.644 | 122.2733 | 122.4747 | 122.4747 | 122.6852 | 122.5067 | 122.2733 | 122.4747 | 122.6852 | 122.644 | 122.4747 | -0.07782 | -0.041199
2204.5312 | 122.8317 | -122.5113 | 0 | 0.11253 | 0.007009 | 0.0044967 | 0.02795 | -0.013606 | -0.0082629 | 0.019611 | 0.07782 | -0.11902 | 0.068665 | 0 | 0.09613 | 0.1236 | -0.059509 | 0.11902 | -0.041199 | -0.032043 | 122.58 | -0.11902 | 122.5891 | 122.5113 | 0.09613 | 122.4792 | -0.041199 | 0.009155 | 122.4518 | 122.6303 | 122.6074 | 122.3923 | 122.5891 | 122.4701 | 122.6349 | 122.4792 | 122.3923 | 122.5891 | 122.6349 | 122.6074 | 122.4701 | 0.068665 | -0.032043
2206.2344 | 122.7539 | -122.5571 | 0.018311 | -0.22316 | 0.0076498 | -0.0031937 | 0.032864 | -0.015956 | -0.0084765 | 0.017474 | -0.041199 | -0.10071 | 0.022888 | -0.064087 | 0.009155 | 0.032043 | 0.12817 | 0.059509 | 0.004578 | -0.07782 | 122.58 | -0.11902 | 122.5159 | 122.493 | -0.009156 | 122.4792 | -0.013733 | -0.064087 | 122.6852 | 122.6166 | 122.5662 | 122.4564 | 122.5159 | 122.5616 | 122.5891 | 122.4792 | 122.4564 | 122.5159 | 122.5891 | 122.5662 | 122.5616 | 0.004577 | -0.096131
2207.9844 | 122.7814 | -122.5433 | 0.027466 | 0.074387 | 0.0095724 | 0.00086511 | 0.030087 | -0.011897 | -0.01104 | 0.015552 | -0.009155 | -0.2243 | -0.013733 | 0.036621 | 0.10986 | 0.14648 | -0.10071 | 0.16479 | -0.054932 | -0.018311 | 122.5296 | -0.25177 | 122.5342 | 122.58 | 0.082397 | 122.525 | -0.082398 | 0.004578 | 122.4426 | 122.7081 | 122.6532 | 122.319 | 122.5342 | 122.4884 | 122.6898 | 122.525 | 122.319 | 122.5342 | 122.6898 | 122.6532 | 122.4884 | -0.041199 | -0.045777
2209.6719 | 122.7814 | -122.5525 | 0.013733 | -0.070572 | 0.0085042 | -0.0019119 | 0.030514 | -0.015956 | -0.0084765 | 0.015125 | 0.004578 | -0.17853 | -0.013733 | 0.059509 | 0.10986 | 0.15564 | -0.036621 | 0.1831 | -0.059509 | -0.045776 | 122.5388 | -0.19226 | 122.5571 | 122.612 | 0.09613 | 122.5067 | -0.073242 | 0.018311 | 122.5159 | 122.7356 | 122.6624 | 122.374 | 122.5571 | 122.493 | 122.7081 | 122.5067 | 122.374 | 122.5571 | 122.7081 | 122.6624 | 122.493 | -0.027466 | -0.059509
2211.375 | 122.7493 | -122.5616 | 0 | -0.0095368 | 0.008718 | -0.0042617 | 0.03735 | -0.01446 | -0.011895 | 0.016406 | 0.009155 | -0.073242 | 0.050354 | -0.059509 | -0.009155 | 0.027466 | 0.059509 | 0.032043 | 0.009155 | -0.050354 | 122.612 | -0.073242 | 122.5708 | 122.5021 | -0.009155 | 122.5113 | 0.009155 | -0.041199 | 122.6212 | 122.5937 | 122.5525 | 122.4884 | 122.5708 | 122.5708 | 122.5891 | 122.5113 | 122.4884 | 122.5708 | 122.5891 | 122.5525 | 122.5708 | 0.050354 | -0.050354
2213.1094 | 122.7173 | -122.5525 | 0.036621 | -0.1545 | 0.010427 | -0.0034073 | 0.033718 | -0.014247 | -0.012108 | 0.017047 | -0.022888 | -0.10529 | 0.009155 | -0.041199 | 0.032043 | 0.050354 | 0.10529 | 0.064087 | 0.004578 | -0.073242 | 122.5616 | -0.14191 | 122.5296 | 122.5113 | -0.004578 | 122.4792 | -0.032043 | -0.032043 | 122.6578 | 122.6166 | 122.5845 | 122.4472 | 122.5296 | 122.5571 | 122.6028 | 122.4792 | 122.4472 | 122.5296 | 122.6028 | 122.5845 | 122.5571 | -0.027466 | -0.10986
2214.8125 | 122.7905 | -122.5616 | 0.004578 | 0.19646 | 0.010427 | -0.0051163 | 0.032223 | -0.011042 | -0.010613 | 0.016193 | -0.022888 | -0.16479 | 0.004578 | 0.018311 | 0.086975 | 0.14191 | -0.07782 | 0.11902 | -0.032043 | -0.027466 | 122.5662 | -0.16937 | 122.5388 | 122.58 | 0.082397 | 122.5342 | -0.036621 | -0.027466 | 122.4838 | 122.6807 | 122.6486 | 122.3969 | 122.5388 | 122.5296 | 122.7036 | 122.5342 | 122.3969 | 122.5388 | 122.7036 | 122.6486 | 122.5296 | 0 | -0.032044
2216.5156 | 122.7539 | -122.5525 | 0.022888 | -0.19264 | 0.010854 | -0.0010575 | 0.031582 | -0.015742 | -0.0091173 | 0.016834 | -0.018311 | -0.082397 | 0.018311 | -0.073242 | 0.041199 | 0.041199 | 0.1236 | 0.068665 | 0.009155 | -0.054932 | 122.5708 | -0.10528 | 122.5342 | 122.4792 | 0.018311 | 122.4976 | -0.013733 | -0.036622 | 122.6761 | 122.6212 | 122.5937 | 122.4701 | 122.5342 | 122.5616 | 122.5937 | 122.4976 | 122.4701 | 122.5342 | 122.5937 | 122.5937 | 122.5616 | -0.004577 | -0.07782
2218.2031 | 122.7127 | -122.5708 | 0.032043 | -0.040054 | 0.010641 | 0.00043791 | 0.035 | -0.011683 | -0.010186 | 0.017688 | 0.004578 | -0.14648 | 0.009155 | -0.004578 | 0.050354 | 0.068665 | 0.045776 | 0.07782 | -0.004578 | -0.041199 | 122.58 | -0.17853 | 122.5754 | 122.5662 | 0.018311 | 122.5296 | -0.036621 | -0.004577 | 122.6166 | 122.6486 | 122.6212 | 122.4243 | 122.5754 | 122.5662 | 122.6395 | 122.5296 | 122.4243 | 122.5754 | 122.6395 | 122.6212 | 122.5662 | -0.022888 | -0.073242
2219.9531 | 122.7081 | -122.5525 | 0.041199 | -0.1545 | 0.0091452 | -0.0029801 | 0.027309 | -0.013819 | -0.01104 | 0.015338 | 0.059509 | -0.15106 | 0.059509 | 0.073242 | 0.12817 | 0.17853 | -0.054932 | 0.19684 | -0.045776 | -0.041199 | 122.612 | -0.19226 | 122.612 | 122.6257 | 0.086975 | 122.5113 | -0.086975 | 0 | 122.4976 | 122.7493 | 122.6807 | 122.4014 | 122.612 | 122.5067 | 122.731 | 122.5113 | 122.4014 | 122.612 | 122.731 | 122.6807 | 122.5067 | 0.01831 | -0.082398
2221.6562 | 122.8317 | -122.5204 | -0.004578 | 0.097275 | 0.0085042 | 1.071e-05 | 0.035 | -0.011683 | -0.012108 | 0.018115 | -0.009155 | -0.09613 | 0.045776 | -0.059509 | -0.013733 | 0.009155 | 0.068665 | -0.004578 | -0.004578 | -0.068665 | 122.5662 | -0.091552 | 122.5113 | 122.4609 | -0.009155 | 122.4518 | 0 | -0.054931 | 122.5891 | 122.5159 | 122.5067 | 122.4243 | 122.5113 | 122.5159 | 122.5296 | 122.4518 | 122.4243 | 122.5113 | 122.5296 | 122.5067 | 122.5159 | 0.050354 | -0.064087
2223.3438 | 122.8409 | -122.5113 | 0.009155 | 0.12779 | 0.0089316 | 0.00022431 | 0.033077 | -0.013392 | -0.0097583 | 0.019183 | -0.11902 | -0.17853 | -0.086975 | -0.07782 | -0.004578 | 0.032043 | 0.068665 | 0.013733 | 0.004578 | -0.073242 | 122.4243 | -0.18768 | 122.3923 | 122.4335 | -0.013733 | 122.4381 | -0.004577 | -0.032044 | 122.58 | 122.525 | 122.5067 | 122.3328 | 122.3923 | 122.5159 | 122.5433 | 122.4381 | 122.3328 | 122.3923 | 122.5433 | 122.5067 | 122.5159 | -0.09613 | -0.082397
2225.0625 | 122.7585 | -122.5525 | 0.009155 | -0.18501 | 0.0078634 | -0.0034073 | 0.030941 | -0.015742 | -0.01104 | 0.01897 | -0.036621 | -0.073242 | 0.032043 | -0.068665 | 0.004578 | 0.032043 | 0.13275 | 0.041199 | 0 | -0.050354 | 122.5845 | -0.082397 | 122.5159 | 122.4838 | -0.004577 | 122.5021 | -0.009155 | -0.068664 | 122.6852 | 122.5937 | 122.5571 | 122.4792 | 122.5159 | 122.5525 | 122.5845 | 122.5021 | 122.4792 | 122.5159 | 122.5845 | 122.5571 | 122.5525 | 0.022888 | -0.059509
2226.7656 | 122.8043 | -122.5433 | -0.004578 | 0.082016 | 0.0099996 | -0.0021255 | 0.035427 | -0.011683 | -0.011895 | 0.017261 | -0.11444 | -0.16937 | -0.073242 | -0.086975 | -0.022888 | 0.018311 | 0.091553 | -0.009155 | 0.013733 | -0.059509 | 122.4701 | -0.16479 | 122.4289 | 122.4564 | -0.01831 | 122.4838 | 0.018311 | -0.041199 | 122.6349 | 122.5342 | 122.5204 | 122.374 | 122.4289 | 122.5571 | 122.5616 | 122.4838 | 122.374 | 122.4289 | 122.5616 | 122.5204 | 122.5571 | -0.068664 | -0.054931
2228.5156 | 122.7356 | -122.58 | 0.045776 | -0.16212 | 0.008718 | -0.0014847 | 0.028591 | -0.014247 | -0.0097583 | 0.018543 | 0.022888 | -0.16479 | 0 | 0.009155 | 0.10071 | 0.13275 | 0.027466 | 0.14648 | -0.022888 | -0.045776 | 122.58 | -0.21057 | 122.6028 | 122.5891 | 0.054932 | 122.5342 | -0.068664 | 0.022888 | 122.6074 | 122.7264 | 122.6807 | 122.4152 | 122.6028 | 122.5571 | 122.7127 | 122.5342 | 122.4152 | 122.6028 | 122.7127 | 122.6807 | 122.5571 | -0.045776 | -0.091552
2230.2188 | 122.7905 | -122.5342 | -0.022888 | 0.20409 | 0.0093588 | -0.00020289 | 0.033291 | -0.013178 | -0.010186 | 0.017902 | -0.022888 | -0.16022 | -0.032043 | -0.018311 | 0.054932 | 0.11902 | -0.041199 | 0.091553 | -0.009155 | -0.036621 | 122.5021 | -0.13733 | 122.5113 | 122.5159 | 0.07782 | 122.4976 | 0.013733 | 0.009155 | 122.493 | 122.6257 | 122.5891 | 122.374 | 122.5113 | 122.525 | 122.6532 | 122.4976 | 122.374 | 122.5113 | 122.6532 | 122.5891 | 122.525 | -0.009155 | -0.013733
2231.9688 | 122.8592 | -122.5296 | 0.013733 | 0.02861 | 0.0082906 | -0.0044755 | 0.028164 | -0.013178 | -0.0067675 | 0.017902 | -0.032043 | -0.17395 | 0.022888 | -0.022888 | 0.073242 | 0.11902 | -0.018311 | 0.11902 | -0.022888 | -0.050354 | 122.5525 | -0.18768 | 122.4976 | 122.5067 | 0.059509 | 122.4792 | -0.036621 | -0.054931 | 122.5113 | 122.6486 | 122.6028 | 122.3557 | 122.4976 | 122.5067 | 122.6486 | 122.4792 | 122.3557 | 122.4976 | 122.6486 | 122.6028 | 122.5067 | 0.009155 | -0.064087
2233.7031 | 122.818 | -122.525 | 0.004578 | 0.066757 | 0.0072226 | 0.0017197 | 0.033718 | -0.012324 | -0.012963 | 0.017474 | -0.07782 | -0.13733 | -0.027466 | -0.082397 | -0.004578 | 0.022888 | 0.086975 | 0.004578 | 0.018311 | -0.045776 | 122.4976 | -0.14191 | 122.4472 | 122.4426 | -0.009156 | 122.4792 | 0.013733 | -0.050354 | 122.612 | 122.5296 | 122.5204 | 122.3877 | 122.4472 | 122.5433 | 122.5479 | 122.4792 | 122.3877 | 122.4472 | 122.5479 | 122.5204 | 122.5433 | -0.032044 | -0.050354
2235.5 | 122.85 | -122.525 | 0.004578 | 0.082016 | 0.008718 | -0.0040481 | 0.026669 | -0.013178 | -0.0095447 | 0.01897 | 0.032043 | -0.091553 | 0.064087 | -0.013733 | 0.064087 | 0.11902 | -0.036621 | 0.11444 | -0.032043 | -0.027466 | 122.5891 | -0.096131 | 122.5571 | 122.5113 | 0.059509 | 122.4976 | -0.036621 | -0.032044 | 122.4884 | 122.6395 | 122.5891 | 122.4335 | 122.5571 | 122.493 | 122.644 | 122.4976 | 122.4335 | 122.5571 | 122.644 | 122.5891 | 122.493 | 0.059509 | -0.032044
2237.2031 | 122.7081 | -122.6028 | 0.032043 | -0.078201 | 0.0095724 | -0.0044755 | 0.035427 | -0.01211 | -0.01104 | 0.016834 | 0.045776 | -0.09613 | 0.027466 | -0.013733 | 0.050354 | 0.086975 | 0.032043 | 0.10529 | -0.022888 | -0.041199 | 122.6303 | -0.12817 | 122.6486 | 122.5891 | 0.018311 | 122.5616 | -0.054931 | 0.01831 | 122.6349 | 122.7081 | 122.6532 | 122.5067 | 122.6486 | 122.58 | 122.6898 | 122.5616 | 122.5067 | 122.6486 | 122.6898 | 122.6532 | 122.58 | -0.004577 | -0.073242
2238.9688 | 122.7539 | -122.5616 | 0.027466 | -0.22316 | 0.009786 | -0.0051163 | 0.029446 | -0.01446 | -0.012108 | 0.017474 | -0.032043 | -0.086975 | 0.018311 | -0.068665 | 0.022888 | 0.036621 | 0.12817 | 0.050354 | 0.009155 | -0.082397 | 122.58 | -0.11444 | 122.5296 | 122.493 | -0.004578 | 122.4792 | -0.018311 | -0.050354 | 122.6898 | 122.612 | 122.5845 | 122.4747 | 122.5296 | 122.5708 | 122.5983 | 122.4792 | 122.4747 | 122.5296 | 122.5983 | 122.5845 | 122.5708 | -0.009155 | -0.10986
2240.7031 | 122.8363 | -122.5433 | -0.004578 | 0.1049 | 0.011922 | -0.0025529 | 0.029873 | -0.013178 | -0.011681 | 0.018115 | 0.004578 | -0.082397 | 0.018311 | -0.068665 | 0 | 0.041199 | 0.041199 | 0.032043 | -0.013733 | -0.045776 | 122.5616 | -0.077819 | 122.5479 | 122.4747 | 0.004578 | 122.4976 | -0.009155 | -0.013733 | 122.5845 | 122.5754 | 122.5433 | 122.4609 | 122.5479 | 122.5296 | 122.5845 | 122.4976 | 122.4609 | 122.5479 | 122.5845 | 122.5433 | 122.5296 | 0.022889 | -0.041198
2242.4062 | 122.7631 | -122.5754 | 0.032043 | -0.10109 | 0.0072226 | -0.0049027 | 0.028805 | -0.016169 | -0.011467 | 0.017688 | 0.07782 | -0.11902 | 0.082397 | 0.054932 | 0.12817 | 0.18768 | -0.082397 | 0.20142 | -0.036621 | -0.032043 | 122.6578 | -0.15106 | 122.6532 | 122.6303 | 0.096131 | 122.5433 | -0.068664 | -0.004577 | 122.493 | 122.7768 | 122.7036 | 122.4564 | 122.6532 | 122.5388 | 122.7631 | 122.5433 | 122.4564 | 122.6532 | 122.7631 | 122.7036 | 122.5388 | 0.050354 | -0.064086
2244.1094 | 122.731 | -122.5754 | 0.018311 | -0.16975 | 0.010427 | 0.0019333 | 0.034359 | -0.01681 | -0.0097583 | 0.015765 | 0 | -0.050354 | 0.032043 | -0.036621 | 0.009155 | 0.045776 | 0.091553 | 0.064087 | 0.004578 | -0.050354 | 122.6074 | -0.068665 | 122.5754 | 122.5388 | -0.009156 | 122.525 | -0.013733 | -0.032043 | 122.6669 | 122.6395 | 122.5845 | 122.525 | 122.5754 | 122.58 | 122.6212 | 122.525 | 122.525 | 122.5754 | 122.6212 | 122.5845 | 122.58 | 0.013732 | -0.068665
2245.8438 | 122.7081 | -122.6074 | 0.054932 | -0.16975 | 0.007009 | -0.0034073 | 0.028591 | -0.015528 | -0.0078357 | 0.017688 | 0.004578 | -0.16937 | 0.009155 | 0.050354 | 0.12817 | 0.16937 | -0.041199 | 0.20142 | -0.041199 | -0.036621 | 122.6166 | -0.22431 | 122.612 | 122.6578 | 0.073242 | 122.5708 | -0.096131 | -0.004577 | 122.5662 | 122.8088 | 122.7356 | 122.438 | 122.612 | 122.5662 | 122.7768 | 122.5708 | 122.438 | 122.612 | 122.7768 | 122.7356 | 122.5662 | -0.045777 | -0.091553
2247.5469 | 122.8043 | -122.5388 | 0.004578 | 0.074387 | 0.010427 | -0.0014847 | 0.035427 | -0.011042 | -0.012108 | 0.015979 | -0.11444 | -0.19226 | -0.064087 | -0.086975 | -0.022888 | 0.013733 | 0.086975 | 0.009155 | 0.004578 | -0.054932 | 122.4747 | -0.19684 | 122.4243 | 122.4518 | -0.027466 | 122.4838 | 0 | -0.050354 | 122.6257 | 122.5479 | 122.5159 | 122.3465 | 122.4243 | 122.5433 | 122.5525 | 122.4838 | 122.3465 | 122.4243 | 122.5525 | 122.5159 | 122.5433 | -0.068665 | -0.05951
2249.25 | 122.7081 | -122.6074 | 0.032043 | -0.17738 | 0.006368 | -0.0051163 | 0.029018 | -0.014033 | -0.0084765 | 0.019611 | 0.068665 | -0.14648 | 0.091553 | 0.059509 | 0.10986 | 0.14191 | -0.032043 | 0.17853 | -0.036621 | -0.041199 | 122.699 | -0.17853 | 122.6761 | 122.6669 | 0.07782 | 122.5662 | -0.068664 | -0.022888 | 122.5754 | 122.7859 | 122.7173 | 122.4609 | 122.6761 | 122.5708 | 122.7493 | 122.5662 | 122.4609 | 122.6761 | 122.7493 | 122.7173 | 122.5708 | 0.05951 | -0.073242
2251 | 122.818 | -122.5571 | 0.009155 | 0.059128 | 0.0085042 | -0.00063009 | 0.035854 | -0.011042 | -0.014031 | 0.01662 | -0.018311 | -0.073242 | 0.032043 | -0.09613 | -0.036621 | 0.009155 | 0.073242 | 0.013733 | -0.013733 | -0.054932 | 122.5891 | -0.082397 | 122.5388 | 122.4609 | -0.045776 | 122.5021 | -0.022888 | -0.050354 | 122.6303 | 122.5708 | 122.5204 | 122.4838 | 122.5388 | 122.5433 | 122.5662 | 122.5021 | 122.4838 | 122.5388 | 122.5662 | 122.5204 | 122.5433 | 0.022888 | -0.064087
2252.7188 | 122.85 | -122.58 | 0 | 0.013352 | 0.0093588 | -0.0040481 | 0.026028 | -0.01446 | -0.0084765 | 0.018756 | -0.054932 | -0.18768 | -0.027466 | -0.009155 | 0.054932 | 0.10529 | -0.027466 | 0.11444 | -0.050354 | -0.045776 | 122.5525 | -0.18768 | 122.525 | 122.5708 | 0.054932 | 122.5342 | -0.050354 | -0.027466 | 122.5525 | 122.6944 | 122.6349 | 122.3923 | 122.525 | 122.5296 | 122.6852 | 122.5342 | 122.3923 | 122.525 | 122.6852 | 122.6349 | 122.5296 | -0.027466 | -0.045776
2254.4219 | 122.8546 | -122.5296 | -0.013733 | 0.066757 | 0.0091452 | 0.0030013 | 0.028591 | -0.015101 | -0.0084765 | 0.017261 | -0.045776 | -0.21057 | -0.032043 | -0.009155 | 0.068665 | 0.11444 | -0.032043 | 0.11444 | -0.022888 | -0.036621 | 122.4976 | -0.19684 | 122.4838 | 122.5204 | 0.082398 | 122.493 | -0.009155 | -0.013733 | 122.4976 | 122.644 | 122.5983 | 122.319 | 122.4838 | 122.5067 | 122.644 | 122.493 | 122.319 | 122.4838 | 122.644 | 122.5983 | 122.5067 | -0.01831 | -0.022888
2256.1562 | 122.7997 | -122.5708 | -0.009155 | 0.1812 | 0.0089316 | -0.0042617 | 0.034573 | -0.014674 | -0.0095447 | 0.017902 | -0.082397 | -0.21515 | -0.045776 | 0 | 0.07782 | 0.12817 | -0.045776 | 0.11444 | -0.050354 | -0.032043 | 122.525 | -0.20599 | 122.4884 | 122.5708 | 0.086975 | 122.5388 | -0.041199 | -0.036621 | 122.525 | 122.6852 | 122.6486 | 122.3557 | 122.4884 | 122.5204 | 122.699 | 122.5388 | 122.3557 | 122.4884 | 122.699 | 122.6486 | 122.5204 | -0.036621 | -0.022888
2257.9062 | 122.7951 | -122.5662 | 0 | 0.15068 | 0.008718 | -0.0038345 | 0.032009 | -0.014033 | -0.0097583 | 0.018543 | -0.064087 | -0.22888 | -0.050354 | 0.004578 | 0.086975 | 0.14191 | -0.09613 | 0.1236 | -0.041199 | -0.027466 | 122.5159 | -0.22888 | 122.5021 | 122.5708 | 0.086975 | 122.5388 | -0.041199 | -0.013733 | 122.4701 | 122.6898 | 122.6532 | 122.3373 | 122.5021 | 122.525 | 122.7081 | 122.5388 | 122.3373 | 122.5021 | 122.7081 | 122.6532 | 122.525 | -0.050354 | -0.027466
2259.6406 | 122.7814 | -122.5754 | 0.009155 | -0.16212 | 0.0067954 | -0.00084389 | 0.032009 | -0.015528 | -0.0095447 | 0.018329 | -0.082397 | -0.12817 | -0.013733 | -0.054932 | 0.013733 | 0.036621 | 0.1236 | 0.068665 | -0.004578 | -0.068665 | 122.5616 | -0.13733 | 122.493 | 122.5204 | 0.004578 | 122.5067 | -0.013733 | -0.068664 | 122.699 | 122.644 | 122.5891 | 122.4472 | 122.493 | 122.5708 | 122.612 | 122.5067 | 122.4472 | 122.493 | 122.612 | 122.5891 | 122.5708 | -0.022888 | -0.07782
2261.3438 | 122.8455 | -122.5525 | 0 | 0.020981 | 0.0095724 | -0.00063009 | 0.026882 | -0.015101 | -0.0091173 | 0.017474 | -0.059509 | -0.19226 | -0.022888 | -0.013733 | 0.050354 | 0.11902 | -0.022888 | 0.11444 | -0.036621 | -0.045776 | 122.5296 | -0.19226 | 122.493 | 122.5388 | 0.050354 | 122.5067 | -0.036621 | -0.036621 | 122.5296 | 122.6669 | 122.6028 | 122.3602 | 122.493 | 122.5159 | 122.6715 | 122.5067 | 122.3602 | 122.493 | 122.6715 | 122.6028 | 122.5159 | -0.022888 | -0.045776
2263.0781 | 122.7814 | -122.5708 | 0.009155 | 0.074387 | 0.0089316 | 0.0023605 | 0.035854 | -0.013819 | -0.010186 | 0.01662 | -0.10071 | -0.16937 | -0.068665 | -0.054932 | -0.004578 | 0.032043 | 0.07782 | 0.041199 | -0.027466 | -0.064087 | 122.5021 | -0.17853 | 122.4701 | 122.5159 | -0.013733 | 122.5067 | -0.036621 | -0.032043 | 122.6486 | 122.612 | 122.5662 | 122.4014 | 122.4701 | 122.5433 | 122.6028 | 122.5067 | 122.4014 | 122.4701 | 122.6028 | 122.5662 | 122.5433 | -0.07782 | -0.073242
2264.8281 | 122.7173 | -122.6074 | 0.032043 | -0.17738 | 0.0091452 | -0.0061843 | 0.029873 | -0.015742 | -0.0086901 | 0.015979 | 0.050354 | -0.18768 | 0.018311 | 0.059509 | 0.1236 | 0.16479 | -0.036621 | 0.18768 | -0.036621 | -0.036621 | 122.6257 | -0.21973 | 122.6578 | 122.6669 | 0.091553 | 122.5708 | -0.068664 | 0.032043 | 122.5708 | 122.7951 | 122.731 | 122.4197 | 122.6578 | 122.5708 | 122.7722 | 122.5708 | 122.4197 | 122.6578 | 122.7722 | 122.731 | 122.5708 | -0.013732 | -0.068664
2266.5312 | 122.7905 | -122.5433 | 0.004578 | 0.17357 | 0.0082906 | -0.0021255 | 0.031796 | -0.013178 | -0.010613 | 0.018543 | -0.004578 | -0.22888 | -0.036621 | 0.050354 | 0.12817 | 0.16479 | -0.11902 | 0.16022 | -0.045776 | -0.018311 | 122.5067 | -0.23346 | 122.5388 | 122.5937 | 0.1236 | 122.525 | -0.050354 | 0.032043 | 122.4243 | 122.7036 | 122.6715 | 122.3145 | 122.5388 | 122.4976 | 122.7081 | 122.525 | 122.3145 | 122.5388 | 122.7081 | 122.6715 | 122.4976 | -0.041199 | -0.022889
2268.2344 | 122.731 | -122.6074 | 0.050354 | -0.16212 | 0.0076498 | -0.0023391 | 0.028164 | -0.017237 | -0.0099719 | 0.017474 | 0.009155 | -0.16937 | 0.009155 | 0.050354 | 0.12817 | 0.15564 | -0.059509 | 0.19684 | -0.041199 | -0.045776 | 122.6166 | -0.21973 | 122.6166 | 122.6578 | 0.07782 | 122.5616 | -0.091553 | 0 | 122.5479 | 122.8043 | 122.7356 | 122.438 | 122.6166 | 122.5662 | 122.7631 | 122.5616 | 122.438 | 122.6166 | 122.7631 | 122.7356 | 122.5662 | -0.041199 | -0.09613
2270 | 122.7219 | -122.6028 | 0.041199 | -0.10109 | 0.0085042 | -0.00063009 | 0.034573 | -0.01446 | -0.012108 | 0.017902 | -0.054932 | -0.13733 | -0.041199 | -0.018311 | 0.050354 | 0.082397 | 0.045776 | 0.10071 | -0.004578 | -0.036621 | 122.5616 | -0.17853 | 122.5479 | 122.5845 | 0.009155 | 122.5662 | -0.045777 | -0.013733 | 122.6486 | 122.7036 | 122.6532 | 122.4655 | 122.5479 | 122.5983 | 122.6852 | 122.5662 | 122.4655 | 122.5479 | 122.6852 | 122.6532 | 122.5983 | -0.082398 | -0.07782
2271.7031 | 122.8683 | -122.5342 | 0 | 0.020981 | 0.008718 | -0.0051163 | 0.028164 | -0.015742 | -0.0093311 | 0.01662 | -0.041199 | -0.21057 | -0.027466 | -0.013733 | 0.082397 | 0.11902 | -0.027466 | 0.10529 | -0.032043 | -0.032043 | 122.5067 | -0.21057 | 122.493 | 122.5204 | 0.082397 | 122.5021 | -0.032043 | -0.013733 | 122.5067 | 122.6395 | 122.6166 | 122.3236 | 122.493 | 122.5021 | 122.6532 | 122.5021 | 122.3236 | 122.493 | 122.6532 | 122.6166 | 122.5021 | -0.027466 | -0.032043
2273.4062 | 122.7356 | -122.5616 | 0.013733 | -0.0019073 | 0.0074362 | 1.071e-05 | 0.036923 | -0.012324 | -0.012749 | 0.015765 | -0.068665 | -0.1831 | -0.050354 | -0.032043 | 0.013733 | 0.041199 | 0.054932 | 0.059509 | -0.004578 | -0.059509 | 122.5113 | -0.19684 | 122.493 | 122.5296 | 0 | 122.5021 | -0.018311 | -0.018311 | 122.6166 | 122.6212 | 122.5754 | 122.3785 | 122.493 | 122.5571 | 122.6028 | 122.5021 | 122.3785 | 122.493 | 122.6028 | 122.5754 | 122.5571 | -0.064087 | -0.073242
2275.1094 | 122.731 | -122.58 | 0.054932 | -0.19264 | 0.0067954 | -0.00041649 | 0.029446 | -0.015315 | -0.0091173 | 0.017047 | 0.004578 | -0.18768 | -0.009155 | 0.064087 | 0.13275 | 0.17395 | -0.059509 | 0.18768 | -0.041199 | -0.036621 | 122.5708 | -0.24261 | 122.5845 | 122.644 | 0.077819 | 122.5433 | -0.096131 | 0.013733 | 122.5204 | 122.7676 | 122.7127 | 122.3923 | 122.5845 | 122.5388 | 122.7539 | 122.5433 | 122.3923 | 122.5845 | 122.7539 | 122.7127 | 122.5388 | -0.064087 | -0.091553
2276.8594 | 122.85 | -122.5754 | 0.009155 | 0.03624 | 0.0065816 | -0.0023391 | 0.028805 | -0.012965 | -0.0095447 | 0.015979 | -0.07782 | -0.21515 | -0.050354 | -0.004578 | 0.054932 | 0.11902 | -0.018311 | 0.10986 | -0.004578 | -0.041199 | 122.525 | -0.2243 | 122.4976 | 122.5708 | 0.045777 | 122.5342 | -0.013733 | -0.027466 | 122.5571 | 122.6852 | 122.6303 | 122.3602 | 122.4976 | 122.5708 | 122.6944 | 122.5342 | 122.3602 | 122.4976 | 122.6944 | 122.6303 | 122.5708 | -0.059509 | -0.050354
2278.5469 | 122.7264 | -122.6028 | 0.045776 | -0.10872 | 0.0099996 | -0.0012711 | 0.035427 | -0.01446 | -0.011467 | 0.017261 | -0.073242 | -0.16479 | -0.041199 | -0.013733 | 0.068665 | 0.068665 | 0.045776 | 0.091553 | 0 | -0.050354 | 122.5616 | -0.21057 | 122.5296 | 122.5891 | 0.022889 | 122.5525 | -0.045776 | -0.032043 | 122.6486 | 122.6944 | 122.6715 | 122.438 | 122.5296 | 122.6028 | 122.6715 | 122.5525 | 122.438 | 122.5296 | 122.6715 | 122.6715 | 122.6028 | -0.086975 | -0.09613
2280.2812 | 122.7722 | -122.5845 | 0.032043 | -0.1545 | 0.0095724 | -0.0019119 | 0.030941 | -0.014247 | -0.0099719 | 0.015979 | -0.045776 | -0.11444 | -0.009155 | -0.059509 | 0.013733 | 0.050354 | 0.091553 | 0.07782 | -0.004578 | -0.073242 | 122.5754 | -0.14648 | 122.5388 | 122.525 | -0.01831 | 122.5113 | -0.036621 | -0.036621 | 122.6761 | 122.6624 | 122.5983 | 122.4701 | 122.5388 | 122.58 | 122.6349 | 122.5113 | 122.4701 | 122.5388 | 122.6349 | 122.5983 | 122.58 | -0.041198 | -0.10529
2282.0312 | 122.8409 | -122.5708 | -0.009155 | -0.032425 | 0.0093588 | -0.0019119 | 0.029018 | -0.012965 | -0.0078357 | 0.016193 | -0.036621 | -0.17853 | -0.009155 | 0.009155 | 0.10071 | 0.12817 | -0.045776 | 0.13733 | -0.027466 | -0.050354 | 122.5616 | -0.16937 | 122.5342 | 122.58 | 0.10986 | 122.5204 | -0.018311 | -0.027466 | 122.525 | 122.7081 | 122.6715 | 122.3923 | 122.5342 | 122.5433 | 122.699 | 122.5204 | 122.3923 | 122.5342 | 122.699 | 122.6715 | 122.5433 | 0 | -0.041199
2283.75 | 122.7402 | -122.6166 | 0.041199 | -0.16975 | 0.0072226 | -0.0053299 | 0.030727 | -0.014033 | -0.010399 | 0.016406 | 0.009155 | -0.15564 | 0.018311 | 0.036621 | 0.10071 | 0.13733 | 0.018311 | 0.15106 | -0.022888 | -0.050354 | 122.6349 | -0.19684 | 122.6257 | 122.6532 | 0.059509 | 122.5662 | -0.064087 | -0.009156 | 122.6349 | 122.7676 | 122.7173 | 122.4609 | 122.6257 | 122.5937 | 122.7539 | 122.5662 | 122.4609 | 122.6257 | 122.7539 | 122.7173 | 122.5937 | -0.022888 | -0.091553
2285.4531 | 122.7997 | -122.5616 | 0.022888 | 0.13542 | 0.0074362 | -0.0025529 | 0.032223 | -0.013392 | -0.010613 | 0.018115 | -0.018311 | -0.23346 | -0.032043 | 0.054932 | 0.10071 | 0.16937 | -0.12817 | 0.15564 | -0.054932 | -0.027466 | 122.5296 | -0.25635 | 122.5433 | 122.6166 | 0.07782 | 122.5342 | -0.07782 | 0.013732 | 122.4335 | 122.7173 | 122.6624 | 122.3282 | 122.5433 | 122.5067 | 122.731 | 122.5342 | 122.3282 | 122.5433 | 122.731 | 122.6624 | 122.5067 | -0.054931 | -0.050354
2287.1562 | 122.7676 | -122.5937 | 0.032043 | -0.17738 | 0.0089316 | -0.0016983 | 0.035 | -0.015315 | -0.011254 | 0.017688 | -0.045776 | -0.12817 | -0.013733 | -0.041199 | 0.013733 | 0.041199 | 0.10986 | 0.068665 | 0.009155 | -0.064087 | 122.58 | -0.16022 | 122.5479 | 122.5525 | -0.01831 | 122.5296 | -0.022888 | -0.032043 | 122.7036 | 122.6624 | 122.6074 | 122.4655 | 122.5479 | 122.6028 | 122.6349 | 122.5296 | 122.4655 | 122.5479 | 122.6349 | 122.6074 | 122.6028 | -0.045776 | -0.09613
2288.875 | 122.7264 | -122.5983 | 0.027466 | -0.11635 | 0.0082906 | -0.0034073 | 0.033718 | -0.013178 | -0.012749 | 0.017474 | -0.018311 | -0.11444 | 0 | -0.004578 | 0.050354 | 0.068665 | 0.054932 | 0.09613 | 0.013733 | -0.041199 | 122.5983 | -0.14191 | 122.58 | 122.5937 | 0.022888 | 122.5571 | -0.013733 | -0.018311 | 122.6532 | 122.6944 | 122.6486 | 122.4838 | 122.58 | 122.612 | 122.6669 | 122.5571 | 122.4838 | 122.58 | 122.6669 | 122.6486 | 122.612 | -0.027466 | -0.068665
2290.5781 | 122.8226 | -122.5891 | 0.004578 | 0.19646 | 0.008718 | -0.00084389 | 0.029873 | -0.01211 | -0.0086901 | 0.014484 | 0.036621 | -0.2243 | 0.009155 | 0.064087 | 0.11444 | 0.16479 | -0.10986 | 0.15564 | -0.045776 | -0.022888 | 122.5983 | -0.22888 | 122.6257 | 122.6532 | 0.10986 | 122.5662 | -0.050354 | 0.027466 | 122.4792 | 122.7448 | 122.7036 | 122.3648 | 122.6257 | 122.5433 | 122.7539 | 122.5662 | 122.3648 | 122.6257 | 122.7539 | 122.7036 | 122.5433 | 0.004577 | -0.027466
2292.2969 | 122.7036 | -122.6212 | 0.018311 | -0.070572 | 0.0082906 | -0.0034073 | 0.033505 | -0.014033 | -0.012963 | 0.017688 | 0.009155 | -0.10986 | 0.027466 | -0.004578 | 0.068665 | 0.086975 | 0.027466 | 0.10986 | -0.022888 | -0.064087 | 122.6486 | -0.12817 | 122.6303 | 122.6166 | 0.050354 | 122.5571 | -0.041199 | -0.018311 | 122.6486 | 122.731 | 122.6898 | 122.5113 | 122.6303 | 122.5983 | 122.7081 | 122.5571 | 122.5113 | 122.6303 | 122.7081 | 122.6898 | 122.5983 | 0.009155 | -0.082398
2293.9844 | 122.8867 | -122.5662 | 0 | 0.066757 | 0.0082906 | -0.0021255 | 0.025601 | -0.013392 | -0.010399 | 0.019824 | -0.009155 | -0.19226 | 0.004578 | -0.009155 | 0.086975 | 0.12817 | -0.041199 | 0.11902 | -0.041199 | -0.045776 | 122.5708 | -0.19226 | 122.5571 | 122.5571 | 0.086975 | 122.5204 | -0.041199 | -0.013733 | 122.525 | 122.6852 | 122.6532 | 122.374 | 122.5571 | 122.525 | 122.6944 | 122.5204 | 122.374 | 122.5571 | 122.6944 | 122.6532 | 122.525 | 0.004578 | -0.045776
2295.7812 | 122.85 | -122.5525 | 0.013733 | 0.13542 | 0.010641 | -0.0010575 | 0.031796 | -0.012751 | -0.0097583 | 0.017047 | -0.091553 | -0.16479 | -0.045776 | -0.07782 | -0.013733 | 0.041199 | 0.068665 | 0.032043 | 0.018311 | -0.059509 | 122.5067 | -0.17853 | 122.4609 | 122.4747 | -0.027466 | 122.493 | 0.004578 | -0.045777 | 122.6212 | 122.5845 | 122.5388 | 122.3877 | 122.4609 | 122.5708 | 122.5937 | 122.493 | 122.3877 | 122.4609 | 122.5937 | 122.5388 | 122.5708 | -0.059509 | -0.073242
2297.4844 | 122.8638 | -122.5708 | 0 | 0.14305 | 0.0085042 | -0.0012711 | 0.032009 | -0.011683 | -0.010186 | 0.017902 | -0.091553 | -0.15564 | -0.050354 | -0.073242 | -0.009155 | 0.041199 | 0.059509 | 0.009155 | 0.004578 | -0.059509 | 122.5204 | -0.15564 | 122.4792 | 122.4976 | -0.009155 | 122.5113 | 0.004578 | -0.041199 | 122.6303 | 122.58 | 122.5616 | 122.4152 | 122.4792 | 122.5754 | 122.612 | 122.5113 | 122.4152 | 122.4792 | 122.612 | 122.5616 | 122.5754 | -0.050354 | -0.059509
2299.1875 | 122.8775 | -122.5525 | 0.013733 | 0.03624 | 0.0072226 | -0.0040481 | 0.025814 | -0.015315 | -0.010826 | 0.01897 | -0.059509 | -0.19684 | -0.036621 | -0.032043 | 0.064087 | 0.11444 | -0.018311 | 0.11444 | -0.041199 | -0.032043 | 122.5159 | -0.21057 | 122.493 | 122.5204 | 0.050354 | 122.5204 | -0.054932 | -0.022888 | 122.5342 | 122.6669 | 122.6166 | 122.3557 | 122.493 | 122.5113 | 122.6669 | 122.5204 | 122.3557 | 122.493 | 122.6669 | 122.6166 | 122.5113 | -0.050354 | -0.045776
2300.875 | 122.7768 | -122.5891 | 0.027466 | -0.2079 | 0.0076498 | -0.0023391 | 0.030514 | -0.016596 | -0.010826 | 0.01662 | -0.059509 | -0.10986 | -0.018311 | -0.059509 | 0.013733 | 0.036621 | 0.12817 | 0.054932 | 0.013733 | -0.082397 | 122.5708 | -0.13733 | 122.5296 | 122.5296 | -0.013733 | 122.5067 | -0.013733 | -0.041198 | 122.7173 | 122.644 | 122.6028 | 122.4792 | 122.5296 | 122.6028 | 122.6257 | 122.5067 | 122.4792 | 122.5296 | 122.6257 | 122.6028 | 122.6028 | -0.045777 | -0.10986
2302.5781 | 122.8592 | -122.5845 | 0.013733 | 0.11253 | 0.0099996 | 0.00065151 | 0.029446 | -0.01681 | -0.0074085 | 0.019611 | -0.045776 | -0.23804 | -0.041199 | 0.004578 | 0.07782 | 0.13275 | -0.068665 | 0.12817 | -0.041199 | -0.027466 | 122.5433 | -0.25177 | 122.5388 | 122.5891 | 0.064087 | 122.5571 | -0.054932 | -0.004577 | 122.5159 | 122.7127 | 122.6624 | 122.3465 | 122.5388 | 122.5433 | 122.7173 | 122.5571 | 122.3465 | 122.5388 | 122.7173 | 122.6624 | 122.5433 | -0.054932 | -0.041199
2304.2969 | 122.7264 | -122.6074 | 0.036621 | -0.078201 | 0.008718 | -0.0023391 | 0.033505 | -0.013819 | -0.011254 | 0.017902 | -0.032043 | -0.15564 | -0.045776 | 0.022888 | 0.054932 | 0.082397 | 0.041199 | 0.10529 | -0.013733 | -0.032043 | 122.5616 | -0.19226 | 122.5754 | 122.6303 | 0.018311 | 122.5754 | -0.050354 | 0.013733 | 122.6486 | 122.7127 | 122.6624 | 122.4518 | 122.5754 | 122.5937 | 122.6898 | 122.5754 | 122.4518 | 122.5754 | 122.6898 | 122.6624 | 122.5937 | -0.082397 | -0.068664
2306.0156 | 122.85 | -122.5616 | 0 | -0.0095368 | 0.0085042 | -0.0036209 | 0.026028 | -0.015528 | -0.0056995 | 0.017902 | -0.027466 | -0.16479 | 0.004578 | -0.013733 | 0.059509 | 0.1236 | -0.032043 | 0.13733 | -0.059509 | -0.041199 | 122.5662 | -0.16479 | 122.5342 | 122.5479 | 0.059509 | 122.5204 | -0.059509 | -0.032044 | 122.5296 | 122.699 | 122.6212 | 122.3969 | 122.5342 | 122.5021 | 122.6852 | 122.5204 | 122.3969 | 122.5342 | 122.6852 | 122.6212 | 122.5021 | 0.004578 | -0.041199
2307.7188 | 122.7676 | -122.6028 | 0.022888 | -0.21553 | 0.0085042 | -0.0055435 | 0.030514 | -0.016169 | -0.010613 | 0.017902 | -0.050354 | -0.13733 | 0.004578 | -0.032043 | 0.036621 | 0.059509 | 0.10529 | 0.082397 | 0.009155 | -0.064087 | 122.6074 | -0.16022 | 122.5525 | 122.5708 | 0.013733 | 122.5388 | -0.013733 | -0.054932 | 122.7081 | 122.6852 | 122.6395 | 122.4655 | 122.5525 | 122.612 | 122.6624 | 122.5388 | 122.4655 | 122.5525 | 122.6624 | 122.6395 | 122.612 | -0.01831 | -0.086975
2309.4531 | 122.7402 | -122.612 | 0.027466 | -0.16212 | 0.0074362 | -0.0016983 | 0.029873 | -0.013819 | -0.0084765 | 0.017474 | 0.013733 | -0.16479 | 0.022888 | 0.064087 | 0.12817 | 0.17853 | -0.045776 | 0.21057 | -0.045776 | -0.041199 | 122.6349 | -0.19226 | 122.6257 | 122.6761 | 0.10071 | 122.5708 | -0.073242 | -0.009155 | 122.5662 | 122.8226 | 122.7402 | 122.4472 | 122.6257 | 122.5662 | 122.7905 | 122.5708 | 122.4472 | 122.6257 | 122.7905 | 122.7402 | 122.5662 | -0.004578 | -0.068665
2311.1719 | 122.8729 | -122.5708 | -0.009155 | 0.013352 | 0.0091452 | -0.0029801 | 0.028164 | -0.01446 | -0.0086901 | 0.017261 | -0.054932 | -0.19684 | -0.004578 | -0.018311 | 0.068665 | 0.1236 | -0.013733 | 0.10529 | -0.032043 | -0.041199 | 122.5662 | -0.18768 | 122.5159 | 122.5525 | 0.07782 | 122.5296 | -0.022888 | -0.050354 | 122.5571 | 122.6761 | 122.6395 | 122.374 | 122.5159 | 122.5388 | 122.6944 | 122.5296 | 122.374 | 122.5159 | 122.6944 | 122.6395 | 122.5388 | 0.004577 | -0.032044
2312.9219 | 122.8134 | -122.5616 | -0.004578 | 0.066757 | 0.0093588 | -0.00084389 | 0.036923 | -0.014033 | -0.014031 | 0.016834 | -0.1236 | -0.2243 | -0.10071 | -0.064087 | -0.009155 | 0.022888 | 0.07782 | 0.018311 | 0.009155 | -0.054932 | 122.4609 | -0.21973 | 122.438 | 122.4976 | -0.004577 | 122.5067 | 0.013733 | -0.022888 | 122.6395 | 122.58 | 122.5525 | 122.3373 | 122.438 | 122.5708 | 122.5845 | 122.5067 | 122.3373 | 122.438 | 122.5845 | 122.5525 | 122.5708 | -0.09613 | -0.050354
2314.625 | 122.7631 | -122.5983 | 0.041199 | -0.23842 | 0.008077 | -0.0019119 | 0.029873 | -0.016169 | -0.0095447 | 0.016406 | -0.036621 | -0.16479 | 0 | 0.004578 | 0.07782 | 0.10529 | 0.041199 | 0.13733 | -0.027466 | -0.054932 | 122.5983 | -0.20599 | 122.5616 | 122.6028 | 0.036621 | 122.5433 | -0.068665 | -0.036621 | 122.6395 | 122.7356 | 122.6761 | 122.4335 | 122.5616 | 122.5708 | 122.7036 | 122.5433 | 122.4335 | 122.5616 | 122.7036 | 122.6761 | 122.5708 | -0.041199 | -0.096131
2316.3438 | 122.8363 | -122.5937 | -0.013733 | 0.16594 | 0.008718 | -0.00020289 | 0.036495 | -0.013392 | -0.010399 | 0.018115 | -0.073242 | -0.16022 | -0.050354 | -0.018311 | 0.045776 | 0.09613 | -0.027466 | 0.07782 | -0.013733 | -0.050354 | 122.5433 | -0.14648 | 122.5204 | 122.5754 | 0.059509 | 122.5433 | 0 | -0.022888 | 122.5662 | 122.6715 | 122.6395 | 122.4335 | 122.5204 | 122.58 | 122.6898 | 122.5433 | 122.4335 | 122.5204 | 122.6898 | 122.6395 | 122.58 | -0.036621 | -0.036621
2318.0625 | 122.8317 | -122.5937 | 0.013733 | 0.1049 | 0.0072226 | 0.00022431 | 0.029659 | -0.014033 | -0.0091173 | 0.01662 | -0.032043 | -0.21057 | -0.027466 | 0.032043 | 0.09613 | 0.16479 | -0.10071 | 0.14191 | -0.041199 | -0.032043 | 122.5662 | -0.2243 | 122.5616 | 122.6257 | 0.082397 | 122.5616 | -0.054932 | -0.004577 | 122.493 | 122.7356 | 122.6898 | 122.3831 | 122.5616 | 122.5525 | 122.7585 | 122.5616 | 122.3831 | 122.5616 | 122.7585 | 122.6898 | 122.5525 | -0.041199 | -0.045776
2319.75 | 122.8043 | -122.5754 | 0.022888 | 0.14305 | 0.0078634 | -0.0029801 | 0.031796 | -0.013606 | -0.0080493 | 0.015765 | -0.009155 | -0.21515 | -0.036621 | 0.036621 | 0.11902 | 0.16479 | -0.10071 | 0.16479 | -0.041199 | -0.022888 | 122.5388 | -0.23804 | 122.5662 | 122.612 | 0.096131 | 122.5525 | -0.064087 | 0.027466 | 122.4747 | 122.7402 | 122.6944 | 122.3602 | 122.5662 | 122.5342 | 122.7402 | 122.5525 | 122.3602 | 122.5662 | 122.7402 | 122.6944 | 122.5342 | -0.059509 | -0.045776
2321.4531 | 122.7768 | -122.5891 | 0.027466 | -0.2079 | 0.011068 | -0.0063981 | 0.030087 | -0.016383 | -0.0093311 | 0.017688 | -0.027466 | -0.082397 | 0.022888 | -0.045776 | 0.022888 | 0.041199 | 0.09613 | 0.064087 | -0.004578 | -0.059509 | 122.612 | -0.10986 | 122.5616 | 122.5433 | -0.004578 | 122.5296 | -0.032044 | -0.050354 | 122.6852 | 122.6532 | 122.612 | 122.5067 | 122.5616 | 122.5845 | 122.6303 | 122.5296 | 122.5067 | 122.5616 | 122.6303 | 122.612 | 122.5845 | -0.004578 | -0.086975
2323.1719 | 122.8409 | -122.58 | 0.004578 | 0.051498 | 0.0082906 | -0.0012711 | 0.035427 | -0.011897 | -0.013604 | 0.016193 | -0.10071 | -0.13733 | -0.050354 | -0.082397 | -0.009155 | 0.004578 | 0.082397 | 0.009155 | 0.013733 | -0.045776 | 122.5296 | -0.14191 | 122.4792 | 122.4976 | -0.013733 | 122.5342 | 0.009155 | -0.050354 | 122.6624 | 122.5891 | 122.5708 | 122.4426 | 122.4792 | 122.5937 | 122.5845 | 122.5342 | 122.4426 | 122.4792 | 122.5845 | 122.5708 | 122.5937 | -0.054932 | -0.050354
2324.9375 | 122.7402 | -122.612 | 0.036621 | -0.078201 | 0.0067954 | -0.00063009 | 0.033291 | -0.014674 | -0.011467 | 0.01897 | -0.07782 | -0.19226 | -0.050354 | -0.004578 | 0.064087 | 0.091553 | 0.045776 | 0.10986 | 0 | -0.036621 | 122.5616 | -0.22888 | 122.5342 | 122.6074 | 0.027466 | 122.5754 | -0.036621 | -0.027466 | 122.6578 | 122.7219 | 122.6761 | 122.4197 | 122.5342 | 122.612 | 122.7036 | 122.5754 | 122.4197 | 122.5342 | 122.7036 | 122.6761 | 122.612 | -0.086975 | -0.073242
2326.625 | 122.8729 | -122.5525 | 0.009155 | 0.13542 | 0.0061544 | 0.0010787 | 0.034145 | -0.01211 | -0.012535 | 0.017688 | -0.13733 | -0.20142 | -0.07782 | -0.068665 | 0 | 0.036621 | 0.054932 | 0.022888 | 0 | -0.059509 | 122.4747 | -0.21057 | 122.4152 | 122.4838 | -0.009155 | 122.493 | -0.009155 | -0.059509 | 122.6074 | 122.5754 | 122.5525 | 122.3511 | 122.4152 | 122.5525 | 122.5891 | 122.493 | 122.3511 | 122.4152 | 122.5891 | 122.5525 | 122.5525 | -0.086975 | -0.068664
2328.3281 | 122.7402 | -122.5983 | 0.045776 | -0.16975 | 0.008718 | -0.0066117 | 0.026241 | -0.013606 | -0.0078357 | 0.017688 | -0.027466 | -0.20599 | -0.022888 | 0.073242 | 0.13733 | 0.1831 | -0.045776 | 0.20599 | -0.041199 | -0.036621 | 122.5754 | -0.25177 | 122.5708 | 122.6715 | 0.091553 | 122.5616 | -0.086975 | -0.004578 | 122.5525 | 122.8043 | 122.7356 | 122.3923 | 122.5708 | 122.5571 | 122.7814 | 122.5616 | 122.3923 | 122.5708 | 122.7814 | 122.7356 | 122.5571 | -0.068664 | -0.082397
2330.0312 | 122.8088 | -122.58 | 0.041199 | -0.23079 | 0.0095724 | -0.0010575 | 0.031796 | -0.015315 | -0.0089037 | 0.017474 | -0.1236 | -0.15564 | -0.073242 | -0.073242 | 0 | 0.027466 | 0.13275 | 0.054932 | 0.004578 | -0.082397 | 122.5067 | -0.19684 | 122.4564 | 122.5067 | -0.041199 | 122.4976 | -0.036621 | -0.050354 | 122.7127 | 122.6349 | 122.58 | 122.4243 | 122.4564 | 122.5845 | 122.6074 | 122.4976 | 122.4243 | 122.4564 | 122.6074 | 122.58 | 122.5845 | -0.11444 | -0.1236
2331.7344 | 122.7768 | -122.5937 | 0.018311 | 0.02861 | 0.0078634 | -0.0029801 | 0.034145 | -0.01211 | -0.011895 | 0.017688 | -0.11902 | -0.21057 | -0.11902 | -0.045776 | 0.022888 | 0.036621 | 0.064087 | 0.045776 | -0.013733 | -0.045776 | 122.4747 | -0.22888 | 122.4747 | 122.5479 | 0.004577 | 122.5479 | -0.032044 | 0 | 122.6578 | 122.6395 | 122.6166 | 122.3831 | 122.4747 | 122.58 | 122.6303 | 122.5479 | 122.3831 | 122.4747 | 122.6303 | 122.6166 | 122.58 | -0.13733 | -0.064087
2333.4375 | 122.8409 | -122.5754 | -0.009155 | 0.18883 | 0.0091452 | -0.0010575 | 0.033077 | -0.013819 | -0.010613 | 0.017902 | -0.15106 | -0.26093 | -0.11902 | -0.022888 | 0.054932 | 0.091553 | -0.032043 | 0.086975 | -0.022888 | -0.050354 | 122.4564 | -0.25177 | 122.4243 | 122.5525 | 0.064087 | 122.525 | -0.013733 | -0.032043 | 122.5433 | 122.6624 | 122.6303 | 122.3145 | 122.4243 | 122.5525 | 122.6669 | 122.525 | 122.3145 | 122.4243 | 122.6669 | 122.6303 | 122.5525 | -0.10986 | -0.041199
2335.1406 | 122.8729 | -122.5296 | -0.009155 | 0.14305 | 0.0089316 | -0.0029801 | 0.032223 | -0.010188 | -0.0082629 | 0.018115 | -0.17853 | -0.24719 | -0.13275 | -0.082397 | -0.013733 | 0.027466 | 0.059509 | 0.027466 | 0.009155 | -0.054932 | 122.3969 | -0.23804 | 122.3511 | 122.4472 | -0.004578 | 122.4747 | 0.01831 | -0.045777 | 122.5891 | 122.5571 | 122.5159 | 122.2824 | 122.3511 | 122.5388 | 122.5571 | 122.4747 | 122.2824 | 122.3511 | 122.5571 | 122.5159 | 122.5388 | -0.1236 | -0.045777
2336.9531 | 122.7356 | -122.612 | 0.018311 | -0.1545 | 0.0085042 | -0.0044755 | 0.026455 | -0.014247 | -0.010613 | 0.016834 | -0.009155 | -0.21057 | -0.036621 | 0.045776 | 0.11444 | 0.15564 | -0.036621 | 0.19226 | -0.027466 | -0.032043 | 122.5754 | -0.22888 | 122.6028 | 122.6578 | 0.09613 | 122.58 | -0.045777 | 0.027466 | 122.5754 | 122.8043 | 122.7264 | 122.4014 | 122.6028 | 122.5845 | 122.7676 | 122.58 | 122.4014 | 122.6028 | 122.7676 | 122.7264 | 122.5845 | -0.054932 | -0.050354
2338.6875 | 122.8409 | -122.5891 | 0.022888 | 0.12016 | 0.0095724 | -0.00020289 | 0.030514 | -0.015528 | -0.0089037 | 0.01662 | -0.027466 | -0.21515 | -0.032043 | 0.022888 | 0.10986 | 0.16022 | -0.09613 | 0.16479 | -0.050354 | -0.027466 | 122.5571 | -0.23804 | 122.5616 | 122.612 | 0.086975 | 122.5616 | -0.073242 | 0.004577 | 122.493 | 122.7539 | 122.699 | 122.374 | 122.5616 | 122.5388 | 122.7493 | 122.5616 | 122.374 | 122.5616 | 122.7493 | 122.699 | 122.5388 | -0.054931 | -0.050354
2340.4219 | 122.7814 | -122.5891 | 0.045776 | -0.16975 | 0.009786 | -0.0046891 | 0.033077 | -0.015742 | -0.012108 | 0.018329 | -0.036621 | -0.09613 | 0.004578 | -0.054932 | 0.018311 | 0.032043 | 0.11444 | 0.064087 | -0.004578 | -0.073242 | 122.5937 | -0.14191 | 122.5525 | 122.5342 | -0.027465 | 122.5159 | -0.050354 | -0.041199 | 122.7036 | 122.6532 | 122.6074 | 122.493 | 122.5525 | 122.5845 | 122.6212 | 122.5159 | 122.493 | 122.5525 | 122.6212 | 122.6074 | 122.5845 | -0.041198 | -0.11902
2342.125 | 122.8363 | -122.5845 | -0.004578 | 0.15068 | 0.0059408 | -0.00063009 | 0.032223 | -0.013606 | -0.0099719 | 0.017474 | -0.059509 | -0.21057 | -0.050354 | 0.022888 | 0.082397 | 0.14648 | -0.073242 | 0.13275 | -0.027466 | -0.027466 | 122.5342 | -0.20599 | 122.525 | 122.6074 | 0.086975 | 122.5571 | -0.022888 | -0.009155 | 122.5113 | 122.7173 | 122.6669 | 122.374 | 122.525 | 122.5571 | 122.731 | 122.5571 | 122.374 | 122.525 | 122.731 | 122.6669 | 122.5571 | -0.045776 | -0.022888
2343.9062 | 122.9004 | -122.5616 | 0.013733 | -0.0095368 | 0.008077 | -0.0023391 | 0.028805 | -0.015101 | -0.0080493 | 0.016193 | -0.050354 | -0.1831 | -0.018311 | -0.032043 | 0.068665 | 0.11444 | -0.018311 | 0.10986 | -0.032043 | -0.054932 | 122.5433 | -0.19684 | 122.5113 | 122.5296 | 0.054932 | 122.5067 | -0.045776 | -0.032043 | 122.5433 | 122.6715 | 122.6303 | 122.3785 | 122.5113 | 122.5296 | 122.6761 | 122.5067 | 122.3785 | 122.5113 | 122.6761 | 122.6303 | 122.5296 | -0.032044 | -0.068665
2345.625 | 122.8363 | -122.5891 | 0.004578 | 0.12779 | 0.007009 | -0.0031937 | 0.029873 | -0.013178 | -0.010186 | 0.015338 | -0.022888 | -0.23346 | -0.036621 | 0.032043 | 0.10529 | 0.15106 | -0.10529 | 0.16479 | -0.018311 | -0.036621 | 122.5525 | -0.23804 | 122.5662 | 122.6212 | 0.10071 | 122.5525 | -0.022889 | 0.013733 | 122.4838 | 122.7539 | 122.6944 | 122.3557 | 122.5662 | 122.5708 | 122.7402 | 122.5525 | 122.3557 | 122.5662 | 122.7402 | 122.6944 | 122.5708 | -0.041199 | -0.041199
2347.3594 | 122.8409 | -122.5891 | 0.009155 | 0.1049 | 0.008077 | -0.0019119 | 0.029659 | -0.011897 | -0.010826 | 0.017902 | -0.013733 | -0.21973 | -0.041199 | 0.009155 | 0.091553 | 0.14191 | -0.086975 | 0.13275 | -0.032043 | -0.036621 | 122.5479 | -0.22888 | 122.5754 | 122.5983 | 0.082398 | 122.5525 | -0.041198 | 0.027466 | 122.5021 | 122.7219 | 122.6807 | 122.3694 | 122.5754 | 122.5571 | 122.731 | 122.5525 | 122.3694 | 122.5754 | 122.731 | 122.6807 | 122.5571 | -0.050354 | -0.045776
2349.0781 | 122.8317 | -122.58 | -0.004578 | 0.14305 | 0.0099996 | -0.0042617 | 0.034359 | -0.013819 | -0.0080493 | 0.018756 | -0.10071 | -0.18768 | -0.059509 | -0.032043 | 0.022888 | 0.10071 | -0.018311 | 0.082397 | -0.018311 | -0.045776 | 122.5204 | -0.1831 | 122.4792 | 122.5479 | 0.027466 | 122.5342 | -0.013733 | -0.041199 | 122.5616 | 122.6624 | 122.6028 | 122.3923 | 122.4792 | 122.5616 | 122.6807 | 122.5342 | 122.3923 | 122.4792 | 122.6807 | 122.6028 | 122.5616 | -0.054931 | -0.041198
2350.7812 | 122.8455 | -122.58 | -0.004578 | 0.059128 | 0.0072226 | -0.0021255 | 0.033291 | -0.013178 | -0.010399 | 0.01897 | -0.032043 | -0.21515 | -0.054932 | 0.041199 | 0.10071 | 0.15106 | -0.10529 | 0.16022 | -0.041199 | -0.009155 | 122.525 | -0.21057 | 122.5479 | 122.6212 | 0.10529 | 122.5708 | -0.036621 | 0.022889 | 122.4747 | 122.7402 | 122.6807 | 122.3648 | 122.5479 | 122.5388 | 122.731 | 122.5708 | 122.3648 | 122.5479 | 122.731 | 122.6807 | 122.5388 | -0.050354 | -0.004577
2352.5625 | 122.8409 | -122.6074 | 0.013733 | 0.1049 | 0.011281 | -0.0014847 | 0.027523 | -0.012538 | -0.010826 | 0.018756 | -0.064087 | -0.27008 | -0.059509 | 0.032043 | 0.11444 | 0.15564 | -0.10071 | 0.16937 | -0.036621 | -0.027466 | 122.5479 | -0.28381 | 122.5433 | 122.6395 | 0.10071 | 122.58 | -0.050354 | -0.004578 | 122.5067 | 122.7768 | 122.7219 | 122.3373 | 122.5433 | 122.5708 | 122.7631 | 122.58 | 122.3373 | 122.5433 | 122.7631 | 122.7219 | 122.5708 | -0.073242 | -0.041199
2354.2812 | 122.7585 | -122.6074 | 0.032043 | -0.23079 | 0.009786 | -0.0042617 | 0.029873 | -0.015956 | -0.011467 | 0.018329 | 0.050354 | -0.082397 | 0.036621 | -0.004578 | 0.045776 | 0.086975 | 0.059509 | 0.11444 | -0.013733 | -0.050354 | 122.644 | -0.11444 | 122.6578 | 122.6028 | 0.013733 | 122.5571 | -0.045776 | 0.013733 | 122.6669 | 122.7219 | 122.6532 | 122.525 | 122.6578 | 122.5937 | 122.6944 | 122.5571 | 122.525 | 122.6578 | 122.6944 | 122.6532 | 122.5937 | 0.004578 | -0.082397
2356 | 122.8043 | -122.5983 | 0.018311 | -0.16975 | 0.0095724 | -0.0042617 | 0.028164 | -0.014247 | -0.0089037 | 0.015125 | 0.086975 | -0.086975 | 0.07782 | 0.054932 | 0.13275 | 0.16937 | -0.073242 | 0.21057 | -0.036621 | -0.054932 | 122.6761 | -0.10529 | 122.6852 | 122.6532 | 0.11444 | 122.5433 | -0.054932 | 0.009155 | 122.525 | 122.8088 | 122.731 | 122.5113 | 122.6852 | 122.5616 | 122.7676 | 122.5433 | 122.5113 | 122.6852 | 122.7676 | 122.731 | 122.5616 | 0.059509 | -0.073243
2357.6875 | 122.7905 | -122.6074 | 0.032043 | -0.16975 | 0.008718 | -0.0031937 | 0.035 | -0.015742 | -0.011895 | 0.015552 | 0 | -0.059509 | 0.027466 | -0.050354 | 0 | 0.027466 | 0.11444 | 0.064087 | 0.004578 | -0.059509 | 122.6349 | -0.091552 | 122.6074 | 122.5571 | -0.032043 | 122.5479 | -0.027465 | -0.027466 | 122.7219 | 122.6715 | 122.6074 | 122.5479 | 122.6074 | 122.612 | 122.6349 | 122.5479 | 122.5479 | 122.6074 | 122.6349 | 122.6074 | 122.612 | -0.004577 | -0.091552
2359.375 | 122.7905 | -122.5754 | 0.013733 | 0.11253 | 0.0078634 | -0.0019119 | 0.036495 | -0.01211 | -0.01339 | 0.016406 | 0.013733 | -0.086975 | 0.027466 | -0.054932 | 0.013733 | 0.027466 | 0.073242 | 0.022888 | 0.004578 | -0.050354 | 122.6028 | -0.10071 | 122.5891 | 122.5204 | 0 | 122.525 | -0.009155 | -0.013733 | 122.6486 | 122.5983 | 122.5891 | 122.4884 | 122.5891 | 122.58 | 122.6028 | 122.525 | 122.4884 | 122.5891 | 122.6028 | 122.5891 | 122.58 | 0.013733 | -0.064087
2361.0781 | 122.8363 | -122.58 | 0.009155 | -0.062942 | 0.0078634 | -0.0049027 | 0.026882 | -0.014887 | -0.0093311 | 0.018756 | 0.045776 | -0.10071 | 0.068665 | 0.022888 | 0.1236 | 0.16022 | -0.059509 | 0.1831 | -0.036621 | -0.045776 | 122.6486 | -0.10986 | 122.6257 | 122.6028 | 0.11444 | 122.5342 | -0.045776 | -0.022889 | 122.5204 | 122.7631 | 122.7036 | 122.4792 | 122.6257 | 122.5433 | 122.7402 | 122.5342 | 122.4792 | 122.6257 | 122.7402 | 122.7036 | 122.5433 | 0.05951 | -0.054931
2362.7656 | 122.8867 | -122.5616 | 0.018311 | 0.0057222 | 0.0082906 | -0.0023391 | 0.027737 | -0.016383 | -0.0093311 | 0.016834 | 0.036621 | -0.11902 | 0.054932 | -0.013733 | 0.073242 | 0.10986 | -0.027466 | 0.10986 | -0.032043 | -0.041199 | 122.6166 | -0.13733 | 122.5983 | 122.5479 | 0.054931 | 122.5204 | -0.050354 | -0.018311 | 122.5342 | 122.6715 | 122.6349 | 122.4426 | 122.5983 | 122.5296 | 122.6715 | 122.5204 | 122.4426 | 122.5983 | 122.6715 | 122.6349 | 122.5296 | 0.036621 | -0.05951
2364.4531 | 122.8683 | -122.5525 | 0 | 0.1049 | 0.0078634 | 0.0015061 | 0.027096 | -0.015956 | -0.0089037 | 0.01662 | 0.054932 | -0.10986 | 0.082397 | 0.009155 | 0.073242 | 0.1236 | -0.041199 | 0.1236 | -0.036621 | -0.041199 | 122.6349 | -0.10986 | 122.6074 | 122.5616 | 0.073242 | 122.5113 | -0.036621 | -0.027465 | 122.5113 | 122.6761 | 122.6257 | 122.4426 | 122.6074 | 122.5159 | 122.6761 | 122.5113 | 122.4426 | 122.6074 | 122.6761 | 122.6257 | 122.5159 | 0.082397 | -0.041199
2366.1562 | 122.7402 | -122.6212 | 0.027466 | -0.1545 | 0.007009 | -0.0027665 | 0.029232 | -0.017024 | -0.0074085 | 0.016193 | 0.086975 | -0.11902 | 0.07782 | 0.064087 | 0.11902 | 0.16937 | -0.064087 | 0.20599 | -0.041199 | -0.032043 | 122.699 | -0.14649 | 122.7081 | 122.6852 | 0.091553 | 122.5891 | -0.068665 | 0.009155 | 122.5571 | 122.8271 | 122.7402 | 122.5021 | 122.7081 | 122.58 | 122.7905 | 122.5891 | 122.5021 | 122.7081 | 122.7905 | 122.7402 | 122.58 | 0.050354 | -0.059509
2367.8906 | 122.8317 | -122.5845 | 0 | 0.18883 | 0.008077 | -0.0031937 | 0.034145 | -0.013392 | -0.0093311 | 0.016193 | 0.064087 | -0.10986 | 0.064087 | 0.041199 | 0.09613 | 0.13733 | -0.09613 | 0.15106 | -0.041199 | -0.036621 | 122.6486 | -0.10986 | 122.6486 | 122.6257 | 0.09613 | 122.5479 | -0.041199 | 0 | 122.4884 | 122.7356 | 122.6807 | 122.4747 | 122.6486 | 122.5433 | 122.7219 | 122.5479 | 122.4747 | 122.6486 | 122.7219 | 122.6807 | 122.5433 | 0.064087 | -0.036621
2369.5938 | 122.8546 | -122.5983 | 0.009155 | -0.055313 | 0.007009 | -0.0046891 | 0.029232 | -0.013606 | -0.0084765 | 0.015125 | 0.050354 | -0.10986 | 0.054932 | 0.032043 | 0.10529 | 0.14191 | -0.036621 | 0.16479 | -0.036621 | -0.050354 | 122.6532 | -0.11902 | 122.6486 | 122.6303 | 0.096131 | 122.5479 | -0.045776 | -0.004578 | 122.5616 | 122.7631 | 122.7036 | 122.4884 | 122.6486 | 122.5616 | 122.7402 | 122.5479 | 122.4884 | 122.6486 | 122.7402 | 122.7036 | 122.5616 | 0.045777 | -0.059509
2371.2969 | 122.7631 | -122.5983 | 0.036621 | -0.19264 | 0.0095724 | -0.0027665 | 0.03265 | -0.012538 | -0.011895 | 0.015338 | 0 | -0.064087 | 0.009155 | -0.027466 | 0.027466 | 0.045776 | 0.09613 | 0.091553 | 0 | -0.059509 | 122.6074 | -0.10071 | 122.5983 | 122.5708 | -0.009155 | 122.5388 | -0.036621 | -0.009155 | 122.6944 | 122.6898 | 122.6257 | 122.5342 | 122.5983 | 122.5983 | 122.644 | 122.5388 | 122.5342 | 122.5983 | 122.644 | 122.6257 | 122.5983 | -0.027466 | -0.09613
2373.0156 | 122.7448 | -122.644 | 0.022888 | -0.055313 | 0.0074362 | -0.0087479 | 0.036068 | -0.012751 | -0.015313 | 0.017474 | 0.050354 | -0.082397 | 0.022888 | 0.009155 | 0.054932 | 0.082397 | 0.018311 | 0.10071 | -0.027466 | -0.054932 | 122.6669 | -0.10528 | 122.6944 | 122.6532 | 0.032044 | 122.5891 | -0.050354 | 0.027466 | 122.6624 | 122.7448 | 122.699 | 122.5616 | 122.6944 | 122.6166 | 122.7264 | 122.5891 | 122.5616 | 122.6944 | 122.7264 | 122.699 | 122.6166 | 0 | -0.07782
2374.7031 | 122.7676 | -122.6257 | 0.018311 | -0.14687 | 0.0074362 | -0.0031937 | 0.030514 | -0.014247 | -0.01339 | 0.017047 | 0.009155 | -0.073242 | 0.050354 | -0.032043 | 0.045776 | 0.054932 | 0.07782 | 0.086975 | -0.013733 | -0.059509 | 122.6761 | -0.091553 | 122.6349 | 122.5937 | 0.027465 | 122.5662 | -0.032044 | -0.041199 | 122.7036 | 122.7127 | 122.6715 | 122.5525 | 122.6349 | 122.612 | 122.6807 | 122.5662 | 122.5525 | 122.6349 | 122.6807 | 122.6715 | 122.612 | 0.032043 | -0.07782
2376.4062 | 122.8271 | -122.5983 | 0.013733 | 0.13542 | 0.0082906 | 0.0015061 | 0.030087 | -0.014033 | -0.0095447 | 0.017474 | 0.10986 | -0.11444 | 0.073242 | 0.027466 | 0.1236 | 0.17853 | -0.11444 | 0.16022 | -0.041199 | -0.018311 | 122.6715 | -0.12817 | 122.7081 | 122.6257 | 0.10986 | 122.58 | -0.054932 | 0.036621 | 122.4838 | 122.7585 | 122.7219 | 122.4838 | 122.7081 | 122.5571 | 122.7768 | 122.58 | 122.4838 | 122.7081 | 122.7768 | 122.7219 | 122.5571 | 0.059509 | -0.032044
2378.1094 | 122.7997 | -122.5891 | 0.045776 | -0.23079 | 0.0095724 | -0.0049027 | 0.029659 | -0.014033 | -0.0078357 | 0.017902 | 0.027466 | -0.082397 | 0.045776 | -0.050354 | 0.041199 | 0.064087 | 0.086975 | 0.086975 | -0.013733 | -0.068665 | 122.6349 | -0.12817 | 122.6166 | 122.5388 | -0.004577 | 122.5204 | -0.059509 | -0.01831 | 122.6761 | 122.6761 | 122.6303 | 122.5067 | 122.6166 | 122.5754 | 122.6532 | 122.5204 | 122.5067 | 122.6166 | 122.6532 | 122.6303 | 122.5754 | 0 | -0.11444
2379.8125 | 122.7814 | -122.612 | 0.013733 | -0.23842 | 0.0067954 | -0.0019119 | 0.027096 | -0.015528 | -0.011467 | 0.017261 | 0.050354 | -0.10071 | 0.068665 | 0 | 0.082397 | 0.091553 | 0.050354 | 0.1236 | -0.009155 | -0.050354 | 122.6807 | -0.11444 | 122.6624 | 122.612 | 0.068664 | 122.5616 | -0.022888 | -0.018311 | 122.6624 | 122.7356 | 122.6944 | 122.5113 | 122.6624 | 122.6028 | 122.7036 | 122.5616 | 122.5113 | 122.6624 | 122.7036 | 122.6944 | 122.6028 | 0.054932 | -0.064087
2381.5156 | 122.7905 | -122.5845 | 0.022888 | -0.1545 | 0.009786 | -0.0016983 | 0.029446 | -0.014887 | -0.0069811 | 0.016406 | 0 | -0.07782 | 0.041199 | -0.041199 | 0.018311 | 0.036621 | 0.10529 | 0.073242 | 0.009155 | -0.082397 | 122.6257 | -0.10071 | 122.5845 | 122.5433 | -0.004577 | 122.5021 | -0.013733 | -0.041199 | 122.6898 | 122.6578 | 122.6028 | 122.5067 | 122.5845 | 122.5937 | 122.6212 | 122.5021 | 122.5067 | 122.5845 | 122.6212 | 122.6028 | 122.5937 | 0.018311 | -0.10528
2383.2188 | 122.7951 | -122.612 | 0.018311 | -0.22316 | 0.009786 | -0.0068253 | 0.029873 | -0.013392 | -0.010613 | 0.01662 | -0.027466 | -0.07782 | 0.009155 | -0.064087 | 0.013733 | 0.027466 | 0.13733 | 0.054932 | 0.018311 | -0.059509 | 122.6212 | -0.096131 | 122.5845 | 122.5479 | -0.004578 | 122.5525 | 0 | -0.036621 | 122.7493 | 122.6669 | 122.6257 | 122.5342 | 122.5845 | 122.6303 | 122.6395 | 122.5525 | 122.5342 | 122.5845 | 122.6395 | 122.6257 | 122.6303 | -0.009156 | -0.07782
2384.9688 | 122.7585 | -122.6349 | 0.027466 | -0.017166 | 0.0078634 | -0.00084389 | 0.034359 | -0.012324 | -0.01104 | 0.01897 | 0.032043 | -0.068665 | 0.032043 | -0.009155 | 0.036621 | 0.068665 | 0.041199 | 0.068665 | 0 | -0.064087 | 122.6669 | -0.096131 | 122.6669 | 122.6257 | 0.009155 | 122.5708 | -0.027466 | 0 | 122.6761 | 122.7036 | 122.6715 | 122.5662 | 122.6669 | 122.6349 | 122.7036 | 122.5708 | 122.5662 | 122.6669 | 122.7036 | 122.6715 | 122.6349 | 0.004577 | -0.091553
2386.6719 | 122.8043 | -122.5983 | 0.013733 | 0.03624 | 0.0089316 | 0.0019333 | 0.034786 | -0.011897 | -0.012322 | 0.018756 | 0.018311 | -0.073242 | 0.045776 | -0.064087 | 0.018311 | 0.027466 | 0.07782 | 0.027466 | 0 | -0.054932 | 122.644 | -0.086975 | 122.6166 | 122.5342 | 0.004578 | 122.5433 | -0.013733 | -0.027465 | 122.6761 | 122.6257 | 122.6166 | 122.525 | 122.6166 | 122.5983 | 122.6257 | 122.5433 | 122.525 | 122.6166 | 122.6257 | 122.6166 | 122.5983 | 0.032043 | -0.068665
2388.375 | 122.7539 | -122.6166 | 0.027466 | -0.085831 | 0.0078634 | -0.0046891 | 0.031368 | -0.010401 | -0.010613 | 0.017902 | 0.041199 | -0.091553 | 0.032043 | 0 | 0.064087 | 0.09613 | 0.027466 | 0.11444 | 0 | -0.059509 | 122.6486 | -0.11902 | 122.6578 | 122.6166 | 0.036621 | 122.5571 | -0.027466 | 0.009156 | 122.644 | 122.731 | 122.6807 | 122.525 | 122.6578 | 122.6166 | 122.7127 | 122.5571 | 122.525 | 122.6578 | 122.7127 | 122.6807 | 122.6166 | 0.004577 | -0.086975
2390.0625 | 122.8043 | -122.6028 | 0.036621 | -0.16975 | 0.0078634 | -0.0014847 | 0.029446 | -0.01211 | -0.010613 | 0.016193 | -0.013733 | -0.064087 | 0.036621 | -0.073242 | 0.018311 | 0.041199 | 0.1236 | 0.054932 | 0.009155 | -0.073242 | 122.6395 | -0.10071 | 122.5891 | 122.5296 | -0.01831 | 122.5296 | -0.027466 | -0.050354 | 122.7264 | 122.6578 | 122.6212 | 122.5388 | 122.5891 | 122.612 | 122.644 | 122.5296 | 122.5388 | 122.5891 | 122.644 | 122.6212 | 122.612 | 0 | -0.10986
2391.75 | 122.7722 | -122.6532 | 0.045776 | -0.17738 | 0.0072226 | -0.0040481 | 0.025601 | -0.014887 | -0.011254 | 0.018115 | 0.086975 | -0.10071 | 0.068665 | 0.045776 | 0.13275 | 0.16022 | -0.032043 | 0.19684 | -0.027466 | -0.036621 | 122.7219 | -0.14648 | 122.7402 | 122.699 | 0.086975 | 122.6166 | -0.073242 | 0.01831 | 122.6212 | 122.85 | 122.7859 | 122.5525 | 122.7402 | 122.6257 | 122.8134 | 122.6166 | 122.5525 | 122.7402 | 122.8134 | 122.7859 | 122.6257 | 0.022889 | -0.082397
2393.4375 | 122.7585 | -122.612 | 0.036621 | -0.10109 | 0.0067954 | -0.00084389 | 0.034145 | -0.013392 | -0.012535 | 0.017688 | 0.036621 | -0.07782 | 0.009155 | -0.018311 | 0.050354 | 0.082397 | 0.050354 | 0.10529 | -0.004578 | -0.032043 | 122.6212 | -0.11444 | 122.6486 | 122.5937 | 0.013733 | 122.58 | -0.041199 | 0.027466 | 122.6624 | 122.7173 | 122.6624 | 122.5342 | 122.6486 | 122.6074 | 122.6944 | 122.58 | 122.5342 | 122.6486 | 122.6944 | 122.6624 | 122.6074 | -0.027466 | -0.068664
2395.125 | 122.7585 | -122.612 | 0.054932 | -0.085831 | 0.008718 | -0.0012711 | 0.033718 | -0.01446 | -0.0093311 | 0.016834 | 0.059509 | -0.082397 | 0.027466 | 0.004578 | 0.068665 | 0.09613 | 0.032043 | 0.10986 | -0.013733 | -0.045776 | 122.6395 | -0.13733 | 122.6715 | 122.6166 | 0.013733 | 122.5662 | -0.068665 | 0.032043 | 122.644 | 122.7219 | 122.6807 | 122.5296 | 122.6715 | 122.5983 | 122.7081 | 122.5662 | 122.5296 | 122.6715 | 122.7081 | 122.6807 | 122.5983 | -0.027466 | -0.10071
2396.8125 | 122.7905 | -122.5937 | 0.032043 | 0.013352 | 0.0072226 | -0.0031937 | 0.032436 | -0.010829 | -0.012963 | 0.01662 | 0.018311 | -0.086975 | 0.050354 | -0.064087 | 0.009155 | 0.050354 | 0.068665 | 0.045776 | 0.004578 | -0.059509 | 122.644 | -0.11902 | 122.612 | 122.5296 | -0.022888 | 122.5342 | -0.027465 | -0.032043 | 122.6624 | 122.6395 | 122.6028 | 122.5067 | 122.612 | 122.5983 | 122.644 | 122.5342 | 122.5067 | 122.612 | 122.644 | 122.6028 | 122.5983 | 0.018311 | -0.091552
2398.5 | 122.7722 | -122.5891 | 0.032043 | -0.1545 | 0.0074362 | -0.0012711 | 0.029873 | -0.01211 | -0.013176 | 0.016406 | 0 | -0.064087 | 0.041199 | -0.027466 | 0.045776 | 0.068665 | 0.07782 | 0.091553 | 0.009155 | -0.064087 | 122.6303 | -0.09613 | 122.5891 | 122.5616 | 0.013733 | 122.525 | -0.022888 | -0.041199 | 122.6669 | 122.6807 | 122.6349 | 122.525 | 122.5891 | 122.5983 | 122.6578 | 122.525 | 122.525 | 122.5891 | 122.6578 | 122.6349 | 122.5983 | 0.009156 | -0.09613
2400.2188 | 122.8317 | -122.5845 | 0.009155 | 0.15831 | 0.008718 | 0.0021469 | 0.028378 | -0.011469 | -0.010826 | 0.016193 | 0.09613 | -0.10071 | 0.073242 | 0.032043 | 0.10529 | 0.16022 | -0.10529 | 0.17395 | -0.036621 | -0.018311 | 122.6578 | -0.10986 | 122.6807 | 122.6166 | 0.096131 | 122.5662 | -0.045776 | 0.022888 | 122.4792 | 122.7585 | 122.6898 | 122.4838 | 122.6807 | 122.5479 | 122.7448 | 122.5662 | 122.4838 | 122.6807 | 122.7448 | 122.6898 | 122.5479 | 0.064087 | -0.027466
2401.9531 | 122.7997 | -122.612 | 0.036621 | -0.20027 | 0.0074362 | -0.0046891 | 0.031368 | -0.016596 | -0.0093311 | 0.015979 | 0 | -0.054932 | 0.036621 | -0.050354 | 0.027466 | 0.054932 | 0.10986 | 0.086975 | 0.004578 | -0.07782 | 122.6486 | -0.091553 | 122.612 | 122.5616 | -0.009155 | 122.5342 | -0.032043 | -0.036621 | 122.7219 | 122.699 | 122.6395 | 122.5571 | 122.612 | 122.6166 | 122.6669 | 122.5342 | 122.5571 | 122.612 | 122.6669 | 122.6395 | 122.6166 | 0 | -0.11444
2403.6562 | 122.7356 | -122.6303 | 0.041199 | -0.055313 | 0.0093588 | -0.0034073 | 0.033932 | -0.014033 | -0.010399 | 0.01662 | 0.036621 | -0.07782 | 0.050354 | 0 | 0.07782 | 0.10071 | 0.041199 | 0.10986 | -0.004578 | -0.045776 | 122.6807 | -0.11902 | 122.6669 | 122.6303 | 0.036621 | 122.5845 | -0.045777 | -0.013733 | 122.6715 | 122.7402 | 122.7081 | 122.5525 | 122.6669 | 122.6257 | 122.731 | 122.5845 | 122.5525 | 122.6669 | 122.731 | 122.7081 | 122.6257 | 0.009155 | -0.086975
2405.3438 | 122.8912 | -122.5708 | 0 | 0.13542 | 0.0085042 | -0.0029801 | 0.0303 | -0.014247 | -0.010186 | 0.016193 | -0.018311 | -0.07782 | 0.027466 | -0.09613 | -0.022888 | 0.032043 | 0.059509 | 0.022888 | 0.018311 | -0.073242 | 122.5983 | -0.07782 | 122.5525 | 122.4747 | -0.022888 | 122.4976 | 0.018311 | -0.045777 | 122.6303 | 122.5937 | 122.5479 | 122.493 | 122.5525 | 122.5891 | 122.6028 | 122.4976 | 122.493 | 122.5525 | 122.6028 | 122.5479 | 122.5891 | 0.027466 | -0.073242
2407.0469 | 122.8958 | -122.5937 | -0.009155 | 0.089645 | 0.007009 | -0.0034073 | 0.026669 | -0.01446 | -0.0071947 | 0.018115 | 0.036621 | -0.082397 | 0.073242 | -0.018311 | 0.073242 | 0.1236 | -0.041199 | 0.12817 | -0.022888 | -0.045776 | 122.6669 | -0.073242 | 122.6303 | 122.5754 | 0.082397 | 122.5479 | -0.013733 | -0.036621 | 122.5525 | 122.7219 | 122.6669 | 122.5113 | 122.6303 | 122.5708 | 122.7173 | 122.5479 | 122.5113 | 122.6303 | 122.7173 | 122.6669 | 122.5708 | 0.082397 | -0.036621
2408.7344 | 122.8958 | -122.58 | 0.009155 | -0.0095368 | 0.008077 | -0.0036209 | 0.02795 | -0.018733 | -0.0078357 | 0.015979 | 0.013733 | -0.10071 | 0.073242 | -0.027466 | 0.050354 | 0.10529 | 0 | 0.1236 | -0.036621 | -0.036621 | 122.6532 | -0.10986 | 122.5937 | 122.5525 | 0.041199 | 122.5433 | -0.045776 | -0.059509 | 122.58 | 122.7036 | 122.6303 | 122.4792 | 122.5937 | 122.5433 | 122.6852 | 122.5433 | 122.4792 | 122.5937 | 122.6852 | 122.6303 | 122.5433 | 0.064087 | -0.045776
2410.4375 | 122.7585 | -122.644 | 0.045776 | -0.1545 | 0.008077 | -0.0066117 | 0.029659 | -0.015742 | -0.010186 | 0.015338 | 0.07782 | -0.11444 | 0.086975 | 0.036621 | 0.10071 | 0.13733 | -0.004578 | 0.18768 | -0.022888 | -0.041199 | 122.731 | -0.16022 | 122.7219 | 122.6807 | 0.054932 | 122.6028 | -0.068664 | -0.009155 | 122.6395 | 122.8317 | 122.7448 | 122.5296 | 122.7219 | 122.6212 | 122.7814 | 122.6028 | 122.5296 | 122.7219 | 122.7814 | 122.7448 | 122.6212 | 0.041199 | -0.086975
2412.1406 | 122.8592 | -122.5754 | 0.004578 | 0.14305 | 0.0082906 | -0.0034073 | 0.033291 | -0.012751 | -0.011254 | 0.019183 | 0.013733 | -0.07782 | 0.032043 | -0.032043 | 0.022888 | 0.068665 | -0.022888 | 0.07782 | -0.013733 | -0.050354 | 122.6074 | -0.082398 | 122.5891 | 122.5433 | 0.01831 | 122.525 | -0.018311 | -0.01831 | 122.5525 | 122.6532 | 122.5983 | 122.4976 | 122.5891 | 122.5616 | 122.644 | 122.525 | 122.4976 | 122.5891 | 122.644 | 122.5983 | 122.5616 | 0.027465 | -0.054932
2413.8906 | 122.7493 | -122.6395 | 0.036621 | -0.1545 | 0.010427 | -0.0046891 | 0.027523 | -0.016383 | -0.010186 | 0.016834 | 0.09613 | -0.09613 | 0.073242 | 0.059509 | 0.10986 | 0.17395 | -0.050354 | 0.21057 | -0.045776 | -0.032043 | 122.7127 | -0.13275 | 122.7356 | 122.699 | 0.073242 | 122.6074 | -0.082397 | 0.022888 | 122.5891 | 122.85 | 122.7493 | 122.5433 | 122.7356 | 122.5937 | 122.8134 | 122.6074 | 122.5433 | 122.7356 | 122.8134 | 122.7493 | 122.5937 | 0.036621 | -0.068664
2415.5781 | 122.7493 | -122.6212 | 0.032043 | -0.14687 | 0.0082906 | -0.0031937 | 0.035214 | -0.012965 | -0.011254 | 0.018756 | 0.032043 | -0.07782 | 0.022888 | -0.013733 | 0.050354 | 0.059509 | 0.050354 | 0.10986 | 0.013733 | -0.064087 | 122.644 | -0.10986 | 122.6532 | 122.6074 | 0.018311 | 122.5571 | -0.01831 | 0.009155 | 122.6715 | 122.731 | 122.6715 | 122.5433 | 122.6532 | 122.6349 | 122.6807 | 122.5571 | 122.5433 | 122.6532 | 122.6807 | 122.6715 | 122.6349 | -0.009155 | -0.09613
2417.2656 | 122.8958 | -122.5845 | -0.009155 | 0.1049 | 0.0093588 | 0.00086511 | 0.034145 | -0.01446 | -0.01104 | 0.017474 | -0.004578 | -0.086975 | 0.022888 | -0.064087 | 0.004578 | 0.032043 | 0.064087 | 0.032043 | -0.004578 | -0.068665 | 122.6074 | -0.07782 | 122.58 | 122.5204 | 0.013733 | 122.5159 | 0.004577 | -0.027466 | 122.6486 | 122.6166 | 122.5891 | 122.4976 | 122.58 | 122.58 | 122.6166 | 122.5159 | 122.4976 | 122.58 | 122.6166 | 122.5891 | 122.58 | 0.032043 | -0.05951
2418.9844 | 122.8821 | -122.58 | -0.004578 | 0.074387 | 0.0078634 | -0.00063009 | 0.027523 | -0.01446 | -0.011254 | 0.018756 | 0.059509 | -0.09613 | 0.045776 | 0.004578 | 0.064087 | 0.12817 | -0.054932 | 0.13275 | -0.032043 | -0.027466 | 122.6257 | -0.091552 | 122.6395 | 122.5845 | 0.068665 | 122.5525 | -0.027465 | 0.013733 | 122.525 | 122.7127 | 122.644 | 122.4838 | 122.6395 | 122.5479 | 122.7081 | 122.5525 | 122.4838 | 122.6395 | 122.7081 | 122.644 | 122.5479 | 0.050354 | -0.022888
2420.6719 | 122.7631 | -122.6166 | 0.050354 | -0.10872 | 0.009786 | -0.0049027 | 0.029018 | -0.017024 | -0.0076221 | 0.015765 | 0.10071 | -0.10529 | 0.073242 | 0.07782 | 0.14191 | 0.16022 | -0.064087 | 0.21057 | -0.045776 | -0.027466 | 122.6898 | -0.15564 | 122.7173 | 122.6944 | 0.091553 | 122.5891 | -0.09613 | 0.027466 | 122.5525 | 122.8271 | 122.7585 | 122.5113 | 122.7173 | 122.5708 | 122.7768 | 122.5891 | 122.5113 | 122.7173 | 122.7768 | 122.7585 | 122.5708 | 0.022888 | -0.07782
2422.3906 | 122.8043 | -122.6028 | 0.032043 | -0.2079 | 0.0082906 | -0.0049027 | 0.030514 | -0.013819 | -0.010826 | 0.01662 | -0.032043 | -0.082397 | 0.027466 | -0.054932 | 0.022888 | 0.036621 | 0.11902 | 0.054932 | 0.004578 | -0.082397 | 122.6303 | -0.11444 | 122.5708 | 122.5479 | -0.009155 | 122.5204 | -0.027465 | -0.059509 | 122.7219 | 122.6578 | 122.6257 | 122.5204 | 122.5708 | 122.6074 | 122.6395 | 122.5204 | 122.5204 | 122.5708 | 122.6395 | 122.6257 | 122.6074 | -0.004577 | -0.11444
2424.0781 | 122.8683 | -122.5845 | 0.009155 | 0.089645 | 0.0093588 | -0.00020289 | 0.033932 | -0.013392 | -0.012535 | 0.017261 | -0.013733 | -0.064087 | 0.036621 | -0.073242 | -0.013733 | 0.022888 | 0.068665 | 0.022888 | -0.018311 | -0.054932 | 122.6212 | -0.073242 | 122.5708 | 122.5113 | -0.022888 | 122.5296 | -0.027466 | -0.050354 | 122.6532 | 122.6074 | 122.5708 | 122.5204 | 122.5708 | 122.5662 | 122.6074 | 122.5296 | 122.5204 | 122.5708 | 122.6074 | 122.5708 | 122.5662 | 0.027466 | -0.064087
2425.7656 | 122.8683 | -122.5616 | 0.013733 | 0.11253 | 0.0082906 | -0.0029801 | 0.032864 | -0.013392 | -0.010399 | 0.018756 | 0 | -0.073242 | 0.027466 | -0.050354 | 0.022888 | 0.059509 | 0.013733 | 0.059509 | 0.004578 | -0.050354 | 122.5891 | -0.086975 | 122.5616 | 122.5113 | 0.009155 | 122.5113 | -0.009155 | -0.027466 | 122.5754 | 122.6212 | 122.5845 | 122.4884 | 122.5616 | 122.5662 | 122.6212 | 122.5113 | 122.4884 | 122.5616 | 122.6212 | 122.5845 | 122.5662 | 0.013733 | -0.064087
2427.4688 | 122.7951 | -122.58 | 0.036621 | -0.19264 | 0.008077 | -0.0029801 | 0.027096 | -0.016383 | -0.0089037 | 0.016193 | -0.013733 | -0.068665 | 0.032043 | -0.054932 | 0.022888 | 0.041199 | 0.12817 | 0.068665 | 0.004578 | -0.064087 | 122.612 | -0.10529 | 122.5662 | 122.525 | -0.013733 | 122.5159 | -0.032043 | -0.045776 | 122.7081 | 122.6486 | 122.6028 | 122.5113 | 122.5662 | 122.5845 | 122.6212 | 122.5159 | 122.5113 | 122.5662 | 122.6212 | 122.6028 | 122.5845 | -0.004578 | -0.10071
2429.1719 | 122.7264 | -122.6074 | 0.022888 | -0.09346 | 0.0095724 | -0.0031937 | 0.033718 | -0.011256 | -0.01104 | 0.016834 | 0.041199 | -0.073242 | 0.050354 | -0.009155 | 0.050354 | 0.073242 | 0.036621 | 0.11902 | -0.009155 | -0.059509 | 122.6578 | -0.09613 | 122.6486 | 122.5983 | 0.027466 | 122.5479 | -0.032043 | -0.009155 | 122.644 | 122.7264 | 122.6578 | 122.5342 | 122.6486 | 122.5983 | 122.6807 | 122.5479 | 122.5342 | 122.6486 | 122.6807 | 122.6578 | 122.5983 | 0.027466 | -0.082397
2430.9219 | 122.7448 | -122.612 | 0.032043 | -0.1545 | 0.010641 | -0.0029801 | 0.026669 | -0.014887 | -0.0093311 | 0.014484 | 0.09613 | -0.10986 | 0.07782 | 0.054932 | 0.13733 | 0.16937 | -0.059509 | 0.20599 | -0.050354 | -0.041199 | 122.6898 | -0.14191 | 122.7081 | 122.6669 | 0.10529 | 122.5708 | -0.082397 | 0.01831 | 122.5525 | 122.818 | 122.7493 | 122.5021 | 122.7081 | 122.5616 | 122.7814 | 122.5708 | 122.5021 | 122.7081 | 122.7814 | 122.7493 | 122.5616 | 0.045777 | -0.073242
2432.6094 | 122.8226 | -122.6028 | 0.013733 | 0.066757 | 0.0082906 | -0.0021255 | 0.033505 | -0.015101 | -0.011895 | 0.017688 | -0.013733 | -0.091553 | 0.022888 | -0.086975 | -0.018311 | 0.022888 | 0.082397 | 0.018311 | 0.013733 | -0.064087 | 122.6257 | -0.10529 | 122.5891 | 122.5159 | -0.032044 | 122.5388 | 0 | -0.036621 | 122.6852 | 122.6212 | 122.5845 | 122.5113 | 122.5891 | 122.6166 | 122.6257 | 122.5388 | 122.5113 | 122.5891 | 122.6257 | 122.5845 | 122.6166 | 0.009155 | -0.07782
2434.3281 | 122.8958 | -122.5708 | 0.004578 | 0.059128 | 0.0078634 | -0.0010575 | 0.026669 | -0.014247 | -0.010186 | 0.017261 | 0.059509 | -0.09613 | 0.07782 | -0.018311 | 0.068665 | 0.10986 | -0.032043 | 0.1236 | -0.032043 | -0.041199 | 122.6486 | -0.10071 | 122.6303 | 122.5525 | 0.064087 | 122.5296 | -0.036621 | -0.018311 | 122.5388 | 122.6944 | 122.6395 | 122.4747 | 122.6303 | 122.5388 | 122.6807 | 122.5296 | 122.4747 | 122.6303 | 122.6807 | 122.6395 | 122.5388 | 0.073242 | -0.045777
2436.0469 | 122.7493 | -122.612 | 0.050354 | -0.16212 | 0.0076498 | -0.0040481 | 0.029873 | -0.017237 | -0.01104 | 0.017261 | 0.07782 | -0.11444 | 0.082397 | 0.041199 | 0.10071 | 0.13733 | -0.009155 | 0.19226 | -0.036621 | -0.036621 | 122.6944 | -0.16479 | 122.6898 | 122.6532 | 0.050354 | 122.5754 | -0.086975 | -0.004577 | 122.6028 | 122.8043 | 122.7127 | 122.4976 | 122.6898 | 122.5754 | 122.7493 | 122.5754 | 122.4976 | 122.6898 | 122.7493 | 122.7127 | 122.5754 | 0.032043 | -0.086975
2437.7656 | 122.7676 | -122.6212 | 0.032043 | -0.0019073 | 0.010854 | -0.0027665 | 0.035214 | -0.013178 | -0.012322 | 0.017047 | 0.045776 | -0.073242 | 0.032043 | -0.018311 | 0.032043 | 0.041199 | 0.059509 | 0.064087 | 0 | -0.050354 | 122.6532 | -0.10529 | 122.6669 | 122.6028 | 0 | 122.5708 | -0.032043 | 0.013733 | 122.6807 | 122.6852 | 122.6532 | 122.5479 | 122.6669 | 122.6212 | 122.6624 | 122.5708 | 122.5479 | 122.6669 | 122.6624 | 122.6532 | 122.6212 | 0 | -0.082397
2439.4844 | 122.8592 | -122.5708 | 0.032043 | -0.040054 | 0.0072226 | -0.0085343 | 0.026455 | -0.016169 | -0.0080493 | 0.016834 | 0.050354 | -0.086975 | 0.068665 | -0.009155 | 0.091553 | 0.13733 | -0.036621 | 0.14191 | -0.054932 | -0.032043 | 122.6395 | -0.11902 | 122.6212 | 122.5616 | 0.05951 | 122.5388 | -0.086975 | -0.018311 | 122.5342 | 122.7127 | 122.6624 | 122.4838 | 122.6212 | 122.5159 | 122.7081 | 122.5388 | 122.4838 | 122.6212 | 122.7081 | 122.6624 | 122.5159 | 0.036622 | -0.064086
2441.1719 | 122.7768 | -122.5845 | 0.027466 | -0.1545 | 0.008077 | -0.00041649 | 0.033291 | -0.015101 | -0.0093311 | 0.017902 | -0.013733 | -0.054932 | 0.018311 | -0.045776 | 0.018311 | 0.036621 | 0.1236 | 0.054932 | -0.009155 | -0.07782 | 122.6028 | -0.082398 | 122.5708 | 122.5388 | -0.009155 | 122.5067 | -0.036621 | -0.032044 | 122.7081 | 122.6395 | 122.6028 | 122.5296 | 122.5708 | 122.5754 | 122.6212 | 122.5067 | 122.5296 | 122.5708 | 122.6212 | 122.6028 | 122.5754 | -0.009155 | -0.10529
2442.9219 | 122.7539 | -122.612 | 0.041199 | -0.10109 | 0.0074362 | -0.0044755 | 0.028378 | -0.016169 | -0.0069811 | 0.015552 | 0.10071 | -0.10071 | 0.073242 | 0.064087 | 0.14191 | 0.16479 | -0.054932 | 0.20599 | -0.036621 | -0.045776 | 122.6852 | -0.14191 | 122.7127 | 122.6761 | 0.10071 | 122.5662 | -0.07782 | 0.027466 | 122.5571 | 122.818 | 122.7539 | 122.5113 | 122.7127 | 122.5754 | 122.7768 | 122.5662 | 122.5113 | 122.7127 | 122.7768 | 122.7539 | 122.5754 | 0.032043 | -0.086975
2444.6094 | 122.7814 | -122.5983 | 0.032043 | -0.14687 | 0.0061544 | -0.0034073 | 0.0303 | -0.015742 | -0.010186 | 0.017688 | -0.004578 | -0.091553 | 0.032043 | -0.032043 | 0.032043 | 0.054932 | 0.10529 | 0.091553 | 0.009155 | -0.068665 | 122.6303 | -0.1236 | 122.5937 | 122.5662 | 0 | 122.5296 | -0.022888 | -0.036621 | 122.7036 | 122.6898 | 122.6303 | 122.5067 | 122.5937 | 122.6074 | 122.6532 | 122.5296 | 122.5067 | 122.5937 | 122.6532 | 122.6303 | 122.6074 | 0 | -0.10071
2446.3281 | 122.8821 | -122.5479 | 0.013733 | 0.03624 | 0.006368 | -0.0029801 | 0.029873 | -0.015742 | -0.0063403 | 0.016193 | 0.036621 | -0.091553 | 0.064087 | -0.013733 | 0.054932 | 0.1236 | -0.027466 | 0.12817 | -0.032043 | -0.045776 | 122.612 | -0.10529 | 122.5845 | 122.5342 | 0.041199 | 122.5021 | -0.045776 | -0.027466 | 122.5204 | 122.6761 | 122.6028 | 122.4564 | 122.5845 | 122.5159 | 122.6715 | 122.5021 | 122.4564 | 122.5845 | 122.6715 | 122.6028 | 122.5159 | 0.050354 | -0.059509
2448.0312 | 122.7676 | -122.5845 | 0.045776 | -0.23079 | 0.0091452 | -0.0040481 | 0.030087 | -0.013606 | -0.010186 | 0.016406 | -0.018311 | -0.054932 | 0.027466 | -0.054932 | 0.009155 | 0.032043 | 0.12817 | 0.064087 | 0 | -0.082397 | 122.612 | -0.10071 | 122.5662 | 122.5296 | -0.036621 | 122.5021 | -0.045776 | -0.045777 | 122.7127 | 122.6486 | 122.5937 | 122.5296 | 122.5662 | 122.5845 | 122.6166 | 122.5021 | 122.5296 | 122.5662 | 122.6166 | 122.5937 | 122.5845 | -0.01831 | -0.12817
2449.7344 | 122.7631 | -122.6166 | 0.050354 | -0.0019073 | 0.008718 | -0.0014847 | 0.035641 | -0.012324 | -0.012535 | 0.018115 | 0.032043 | -0.073242 | 0.036621 | -0.045776 | 0.022888 | 0.050354 | 0.036621 | 0.054932 | -0.004578 | -0.059509 | 122.6532 | -0.1236 | 122.6486 | 122.5708 | -0.027466 | 122.5571 | -0.054932 | -0.004578 | 122.6532 | 122.6715 | 122.6395 | 122.5433 | 122.6486 | 122.612 | 122.6669 | 122.5571 | 122.5433 | 122.6486 | 122.6669 | 122.6395 | 122.612 | -0.013733 | -0.10986
2451.4219 | 122.7127 | -122.5983 | 0.045776 | -0.078201 | 0.008077 | -0.0019119 | 0.035 | -0.014247 | -0.010186 | 0.017047 | 0.050354 | -0.07782 | 0.036621 | 0 | 0.059509 | 0.07782 | 0.045776 | 0.11444 | -0.004578 | -0.054932 | 122.6349 | -0.1236 | 122.6486 | 122.5983 | 0.013733 | 122.5433 | -0.050354 | 0.013733 | 122.644 | 122.7127 | 122.6578 | 122.5204 | 122.6486 | 122.5937 | 122.6761 | 122.5433 | 122.5204 | 122.6486 | 122.6761 | 122.6578 | 122.5937 | -0.009155 | -0.10071
2453.125 | 122.8455 | -122.5708 | 0.022888 | 0.12016 | 0.0089316 | -0.0019119 | 0.028805 | -0.014887 | -0.0080493 | 0.017474 | 0.073242 | -0.10529 | 0.082397 | 0.018311 | 0.10986 | 0.14648 | -0.086975 | 0.15106 | -0.068665 | -0.041199 | 122.6532 | -0.12817 | 122.644 | 122.5891 | 0.086975 | 122.5296 | -0.091553 | -0.009155 | 122.4838 | 122.7219 | 122.6807 | 122.4655 | 122.644 | 122.5021 | 122.7173 | 122.5296 | 122.4655 | 122.644 | 122.7173 | 122.6807 | 122.5021 | 0.059509 | -0.064087
2454.8281 | 122.7356 | -122.6166 | 0.045776 | -0.13161 | 0.0076498 | -0.0029801 | 0.026882 | -0.012965 | -0.0095447 | 0.015979 | 0.10986 | -0.10986 | 0.064087 | 0.045776 | 0.13733 | 0.17853 | -0.050354 | 0.21973 | -0.036621 | -0.032043 | 122.6807 | -0.15564 | 122.7264 | 122.6624 | 0.091553 | 122.5845 | -0.082397 | 0.045776 | 122.5662 | 122.8363 | 122.7539 | 122.5067 | 122.7264 | 122.58 | 122.7951 | 122.5845 | 122.5067 | 122.7264 | 122.7951 | 122.7539 | 122.58 | 0.018311 | -0.077819
2456.5312 | 122.7768 | -122.6074 | 0.027466 | -0.14687 | 0.0095724 | -0.0036209 | 0.030941 | -0.015315 | -0.010399 | 0.016834 | -0.027466 | -0.059509 | 0.027466 | -0.059509 | 0.036621 | 0.054932 | 0.11902 | 0.068665 | 0 | -0.064087 | 122.6349 | -0.086975 | 122.58 | 122.5479 | 0.009155 | 122.5433 | -0.027466 | -0.054932 | 122.7264 | 122.6761 | 122.644 | 122.5479 | 122.58 | 122.6074 | 122.6624 | 122.5433 | 122.5479 | 122.58 | 122.6624 | 122.644 | 122.6074 | 0 | -0.091553
2458.2344 | 122.7951 | -122.5891 | 0.041199 | -0.21553 | 0.007009 | -0.0053299 | 0.031796 | -0.01446 | -0.011254 | 0.014484 | -0.032043 | -0.059509 | 0.022888 | -0.068665 | 0.009155 | 0.018311 | 0.14648 | 0.054932 | 0.027466 | -0.07782 | 122.612 | -0.10071 | 122.5571 | 122.5204 | -0.032044 | 122.5113 | -0.013733 | -0.054931 | 122.7356 | 122.644 | 122.5983 | 122.5296 | 122.5571 | 122.6166 | 122.6074 | 122.5113 | 122.5296 | 122.5571 | 122.6074 | 122.5983 | 122.6166 | -0.018311 | -0.11902
2459.9844 | 122.7722 | -122.5983 | 0.050354 | -0.23079 | 0.008077 | -0.0042617 | 0.030087 | -0.014887 | -0.010186 | 0.017261 | 0.032043 | -0.073242 | 0.032043 | -0.022888 | 0.045776 | 0.073242 | 0.086975 | 0.091553 | -0.022888 | -0.064087 | 122.6303 | -0.1236 | 122.6303 | 122.5754 | -0.004578 | 122.5342 | -0.073242 | 0 | 122.6852 | 122.6898 | 122.644 | 122.525 | 122.6303 | 122.5754 | 122.6715 | 122.5342 | 122.525 | 122.6303 | 122.6715 | 122.644 | 122.5754 | -0.018311 | -0.11444
2461.6875 | 122.8226 | -122.5433 | 0.009155 | 0.17357 | 0.008718 | -0.0019119 | 0.033077 | -0.013178 | -0.012749 | 0.01662 | 0.045776 | -0.09613 | 0.045776 | -0.027466 | 0.050354 | 0.091553 | -0.036621 | 0.10529 | -0.032043 | -0.054932 | 122.5891 | -0.10528 | 122.5891 | 122.5159 | 0.041199 | 122.4884 | -0.041198 | 0 | 122.5067 | 122.6486 | 122.5937 | 122.4472 | 122.5891 | 122.5113 | 122.6349 | 122.4884 | 122.4472 | 122.5891 | 122.6349 | 122.5937 | 122.5113 | 0.036621 | -0.064087
2463.3906 | 122.8638 | -122.5571 | 0.027466 | 0.02861 | 0.008718 | -0.0010575 | 0.027096 | -0.014033 | -0.0091173 | 0.018115 | 0.032043 | -0.082397 | 0.050354 | -0.018311 | 0.068665 | 0.10986 | -0.022888 | 0.11902 | -0.041199 | -0.022888 | 122.6074 | -0.10986 | 122.5891 | 122.5388 | 0.041199 | 122.5342 | -0.068665 | -0.018311 | 122.5342 | 122.6761 | 122.6257 | 122.4747 | 122.5891 | 122.5159 | 122.6669 | 122.5342 | 122.4747 | 122.5891 | 122.6669 | 122.6257 | 122.5159 | 0.022888 | -0.050354
2465.0938 | 122.7448 | -122.5845 | 0.041199 | 0.020981 | 0.0085042 | -0.0014847 | 0.034786 | -0.012324 | -0.012749 | 0.016406 | 0.022888 | -0.086975 | 0.041199 | -0.027466 | 0.013733 | 0.045776 | 0.050354 | 0.045776 | -0.009155 | -0.050354 | 122.6257 | -0.12817 | 122.6074 | 122.5571 | -0.027466 | 122.5342 | -0.050354 | -0.018311 | 122.6349 | 122.6303 | 122.5983 | 122.4976 | 122.6074 | 122.5754 | 122.6303 | 122.5342 | 122.4976 | 122.6074 | 122.6303 | 122.5983 | 122.5754 | 0 | -0.091553
2466.7969 | 122.8546 | -122.5021 | 0.022888 | 0.12016 | 0.009786 | -0.0051163 | 0.034573 | -0.01446 | -0.0095447 | 0.017688 | -0.009155 | -0.07782 | 0.022888 | -0.068665 | -0.013733 | 0.032043 | 0.059509 | 0.027466 | 0.013733 | -0.07782 | 122.525 | -0.10071 | 122.493 | 122.4335 | -0.036621 | 122.4243 | -0.009155 | -0.032043 | 122.5616 | 122.5296 | 122.4884 | 122.4243 | 122.493 | 122.5159 | 122.5342 | 122.4243 | 122.4243 | 122.493 | 122.5342 | 122.4884 | 122.5159 | 0 | -0.10071
2468.5781 | 122.7493 | -122.5708 | 0.054932 | -0.24605 | 0.0067954 | -0.00020289 | 0.030087 | -0.016596 | -0.0097583 | 0.019611 | 0.050354 | -0.086975 | 0.064087 | 0.004578 | 0.07782 | 0.10071 | 0.041199 | 0.13733 | -0.018311 | -0.045776 | 122.6349 | -0.14191 | 122.6212 | 122.5754 | 0.022888 | 122.525 | -0.073243 | -0.013733 | 122.612 | 122.7081 | 122.6486 | 122.4838 | 122.6212 | 122.5525 | 122.6715 | 122.525 | 122.4838 | 122.6212 | 122.6715 | 122.6486 | 122.5525 | 0.009155 | -0.10071
2470.3594 | 122.7951 | -122.5433 | 0.027466 | 0.15831 | 0.0089316 | -0.0051163 | 0.031582 | -0.015101 | -0.0089037 | 0.01662 | 0.091553 | -0.10529 | 0.07782 | 0.054932 | 0.10986 | 0.16937 | -0.1236 | 0.17853 | -0.032043 | -0.027466 | 122.6212 | -0.13275 | 122.6349 | 122.5983 | 0.082397 | 122.5159 | -0.059509 | 0.013733 | 122.4197 | 122.7219 | 122.6532 | 122.438 | 122.6349 | 122.5113 | 122.7127 | 122.5159 | 122.438 | 122.6349 | 122.7127 | 122.6532 | 122.5113 | 0.050354 | -0.054932
2472.125 | 122.8043 | -122.5479 | 0.022888 | 0.16594 | 0.0072226 | -0.0012711 | 0.032223 | -0.014674 | -0.012322 | 0.017047 | 0.091553 | -0.082397 | 0.073242 | 0.045776 | 0.10986 | 0.16022 | -0.11902 | 0.14648 | -0.027466 | -0.027466 | 122.6212 | -0.10528 | 122.6395 | 122.5937 | 0.086975 | 122.5204 | -0.050354 | 0.018311 | 122.4289 | 122.6944 | 122.6578 | 122.4655 | 122.6395 | 122.5204 | 122.7081 | 122.5204 | 122.4655 | 122.6395 | 122.7081 | 122.6578 | 122.5204 | 0.050354 | -0.050354
2473.8281 | 122.7905 | -122.525 | 0.064087 | -0.085831 | 0.0085042 | -0.0063981 | 0.027309 | -0.015742 | -0.010399 | 0.017047 | 0.050354 | -0.11444 | 0.059509 | 0.032043 | 0.12817 | 0.17395 | -0.064087 | 0.1831 | -0.036621 | -0.027466 | 122.5845 | -0.17853 | 122.5754 | 122.5571 | 0.064087 | 122.4976 | -0.10071 | -0.009155 | 122.4609 | 122.7081 | 122.6532 | 122.4106 | 122.5754 | 122.4884 | 122.699 | 122.4976 | 122.4106 | 122.5754 | 122.699 | 122.6532 | 122.4884 | -0.004578 | -0.091553
2475.5781 | 122.8134 | -122.5021 | 0.013733 | 0.043869 | 0.007009 | -0.0040481 | 0.028164 | -0.015528 | -0.0093311 | 0.017047 | 0.059509 | -0.09613 | 0.07782 | 0 | 0.086975 | 0.11444 | -0.050354 | 0.1236 | -0.036621 | -0.059509 | 122.58 | -0.10986 | 122.5616 | 122.5021 | 0.073242 | 122.4426 | -0.050354 | -0.018311 | 122.4518 | 122.6257 | 122.5891 | 122.406 | 122.5616 | 122.4655 | 122.6166 | 122.4426 | 122.406 | 122.5616 | 122.6166 | 122.5891 | 122.4655 | 0.064087 | -0.073242
2477.2812 | 122.5937 | -122.4335 | 0.041199 | -0.17738 | 0.0095724 | -0.00020289 | 0.035854 | -0.015528 | -0.0080493 | 0.016834 | 0.004578 | -0.064087 | 0.022888 | -0.036621 | 0.041199 | 0.050354 | 0.082397 | 0.091553 | -0.004578 | -0.068665 | 122.4564 | -0.10529 | 122.438 | 122.3969 | 0 | 122.3648 | -0.045777 | -0.01831 | 122.5159 | 122.525 | 122.4747 | 122.3694 | 122.438 | 122.4289 | 122.4838 | 122.3648 | 122.3694 | 122.438 | 122.4838 | 122.4747 | 122.4289 | -0.018311 | -0.10986
2479.0469 | 122.6578 | -122.4792 | 0.064087 | -0.16212 | 0.006368 | -0.0034073 | 0.032436 | -0.015101 | -0.010826 | 0.016406 | -0.009155 | -0.07782 | 0.018311 | -0.032043 | 0.022888 | 0.059509 | 0.082397 | 0.10071 | -0.004578 | -0.059509 | 122.4976 | -0.14191 | 122.4701 | 122.4472 | -0.041199 | 122.4197 | -0.068665 | -0.027466 | 122.5616 | 122.58 | 122.5021 | 122.4014 | 122.4701 | 122.4747 | 122.5388 | 122.4197 | 122.4014 | 122.4701 | 122.5388 | 122.5021 | 122.4747 | -0.045776 | -0.1236
2480.75 | 122.7539 | -122.4472 | 0.018311 | 0.082016 | 0.0085042 | -0.0021255 | 0.033932 | -0.010829 | -0.011254 | 0.017261 | -0.009155 | -0.086975 | 0.022888 | -0.07782 | -0.004578 | 0.018311 | 0.10529 | 0.013733 | 0.004578 | -0.064087 | 122.4701 | -0.10529 | 122.438 | 122.3694 | -0.022889 | 122.3831 | -0.013733 | -0.032043 | 122.5525 | 122.4609 | 122.4426 | 122.3602 | 122.438 | 122.4518 | 122.4655 | 122.3831 | 122.3602 | 122.438 | 122.4655 | 122.4426 | 122.4518 | 0.004577 | -0.082398
2482.5156 | 122.8592 | -122.493 | 0.018311 | 0.16594 | 0.006368 | -0.0025529 | 0.029873 | -0.013392 | -0.010399 | 0.017261 | 0.086975 | -0.11902 | 0.086975 | 0.036621 | 0.11902 | 0.17853 | -0.12817 | 0.17395 | -0.027466 | -0.004578 | 122.58 | -0.13733 | 122.58 | 122.5296 | 0.10071 | 122.4884 | -0.045777 | 0 | 122.3648 | 122.6669 | 122.612 | 122.374 | 122.58 | 122.4655 | 122.6715 | 122.4884 | 122.374 | 122.58 | 122.6715 | 122.612 | 122.4655 | 0.068664 | -0.022889
2484.2656 | 122.7127 | -122.4655 | 0.050354 | 0.12779 | 0.0072226 | -0.0012711 | 0.032864 | -0.010401 | -0.011467 | 0.017902 | 0.09613 | -0.10529 | 0.073242 | 0.045776 | 0.10986 | 0.17853 | -0.10529 | 0.16937 | -0.032043 | -0.018311 | 122.5388 | -0.15564 | 122.5616 | 122.5113 | 0.059509 | 122.4472 | -0.082397 | 0.022888 | 122.3602 | 122.6349 | 122.5754 | 122.3602 | 122.5616 | 122.4335 | 122.644 | 122.4472 | 122.3602 | 122.5616 | 122.644 | 122.5754 | 122.4335 | 0.022888 | -0.068665
2486.0156 | 122.6669 | -122.493 | 0.059509 | -0.22316 | 0.0076498 | -0.0053299 | 0.032009 | -0.015528 | -0.012749 | 0.016834 | 0.059509 | -0.09613 | 0.068665 | 0 | 0.073242 | 0.091553 | 0.064087 | 0.11902 | -0.013733 | -0.059509 | 122.5616 | -0.15564 | 122.5525 | 122.493 | 0.013733 | 122.4335 | -0.073242 | -0.009156 | 122.5571 | 122.612 | 122.5662 | 122.3969 | 122.5525 | 122.4792 | 122.5845 | 122.4335 | 122.3969 | 122.5525 | 122.5845 | 122.5662 | 122.4792 | 0.009156 | -0.11902
2487.7188 | 122.6807 | -122.4838 | 0.050354 | -0.12398 | 0.0085042 | -0.0019119 | 0.028591 | -0.01681 | -0.0099719 | 0.017688 | 0.10071 | -0.1236 | 0.07782 | 0.041199 | 0.14191 | 0.17853 | -0.059509 | 0.21515 | -0.045776 | -0.045776 | 122.5616 | -0.17395 | 122.5845 | 122.525 | 0.091553 | 122.438 | -0.09613 | 0.022888 | 122.4243 | 122.699 | 122.6257 | 122.3602 | 122.5845 | 122.438 | 122.6624 | 122.438 | 122.3602 | 122.5845 | 122.6624 | 122.6257 | 122.438 | 0.027466 | -0.09613
2489.4844 | 122.5571 | -122.3831 | 0.11902 | -0.16212 | 0.0076498 | -0.00041649 | 0.030514 | -0.01446 | -0.010186 | 0.015338 | 0.09613 | -0.091553 | 0.054932 | 0.064087 | 0.12817 | 0.15106 | -0.041199 | 0.18768 | -0.027466 | -0.032043 | 122.438 | -0.21057 | 122.4792 | 122.4472 | 0.009155 | 122.3511 | -0.14649 | 0.041198 | 122.3419 | 122.5708 | 122.5113 | 122.2916 | 122.4792 | 122.3557 | 122.5342 | 122.3511 | 122.2916 | 122.4792 | 122.5342 | 122.5113 | 122.3557 | -0.064087 | -0.15106
2491.1875 | 122.3328 | -121.9574 | 0.31586 | -0.070572 | 0.0091452 | -0.0083207 | 0.036709 | -0.012751 | -0.014031 | 0.01662 | 0.054932 | -0.07782 | 0.041199 | 0.013733 | 0.064087 | 0.073242 | 0.027466 | 0.11444 | 0.013733 | -0.036621 | 121.9986 | -0.39368 | 122.0123 | 121.9711 | -0.25177 | 121.9208 | -0.30212 | 0.013733 | 121.9849 | 122.0718 | 122.0215 | 121.8796 | 122.0123 | 121.9711 | 122.0306 | 121.9208 | 121.8796 | 122.0123 | 122.0306 | 122.0215 | 121.9711 | -0.27466 | -0.35248
2492.9531 | 122.5113 | -122.3007 | 0.004578 | -0.14687 | 0.0074362 | -0.0051163 | 0.027096 | -0.012751 | -0.0076221 | 0.017047 | 0.082397 | -0.10071 | 0.068665 | 0.059509 | 0.13733 | 0.17395 | -0.064087 | 0.21057 | -0.027466 | -0.041199 | 122.3694 | -0.10529 | 122.3831 | 122.3602 | 0.13275 | 122.2595 | -0.032044 | 0.013732 | 122.2366 | 122.5113 | 122.438 | 122.2 | 122.3831 | 122.2733 | 122.4747 | 122.2595 | 122.2 | 122.3831 | 122.4747 | 122.438 | 122.2733 | 0.064087 | -0.045777
2494.7031 | 122.6303 | -122.374 | 0.022888 | 0.1049 | 0.0055136 | -0.0038345 | 0.030514 | -0.014674 | -0.0099719 | 0.017688 | 0.073242 | -0.10529 | 0.068665 | 0.036621 | 0.11444 | 0.15564 | -0.10071 | 0.16479 | -0.054932 | -0.036621 | 122.4426 | -0.12817 | 122.4472 | 122.4106 | 0.091553 | 122.3373 | -0.07782 | 0.004577 | 122.2733 | 122.5388 | 122.4884 | 122.2687 | 122.4472 | 122.319 | 122.5296 | 122.3373 | 122.2687 | 122.4472 | 122.5296 | 122.4884 | 122.319 | 0.045777 | -0.059509
2496.4062 | 122.5891 | -122.438 | 0.041199 | -0.16975 | 0.0099996 | -0.0044755 | 0.031796 | -0.017878 | -0.012322 | 0.017902 | 0.091553 | -0.11902 | 0.068665 | 0.036621 | 0.10071 | 0.13275 | -0.009155 | 0.1831 | -0.036621 | -0.054932 | 122.5067 | -0.16022 | 122.5296 | 122.4747 | 0.059509 | 122.3831 | -0.07782 | 0.022888 | 122.4289 | 122.6212 | 122.5388 | 122.319 | 122.5296 | 122.4014 | 122.5708 | 122.3831 | 122.319 | 122.5296 | 122.5708 | 122.5388 | 122.4014 | 0.027466 | -0.096131

## Thermal Data
Fire Time | C Position - 3' | C Position - Middle | C Position - 7'
-0.0115 | 10.184 | 11.0177 | 10.7294
0.9885 | 10.3208 | 11.1248 | 10.9646
1.9885 | 10.5821 | 11.4872 | 11.3413
2.9885 | 11.1009 | 12.2135 | 12.3634
3.9885 | 11.7054 | 12.6569 | 13.5147
4.9885 | 12.3431 | 13.7354 | 14.177
5.9885 | 13.5371 | 14.5802 | 15.9515
6.9885 | 14.2982 | 15.1424 | 17.0973
7.9885 | 15.6583 | 16.7748 | 18.1374
8.9885 | 18.021 | 17.6755 | 19.259
9.9885 | 19.2964 | 18.9951 | 20.7693
10.9885 | 20.5155 | 20.4626 | 22.3277
11.9885 | 22.0632 | 21.7587 | 23.5003
12.9885 | 23.8556 | 23.3828 | 25.5834
13.9885 | 25.3416 | 25.1678 | 27.3661
14.9885 | 27.6511 | 27.0673 | 29.5144
15.9885 | 29.8083 | 28.7288 | 31.7035
16.9885 | 32.024 | 31.2379 | 34.1514
17.9885 | 33.3064 | 33.3156 | 36.5188
18.9885 | 35.5353 | 35.5103 | 39.5325
19.9885 | 37.8854 | 37.7398 | 42.1869
20.9885 | 41.3283 | 41.3718 | 44.7042
21.9885 | 43.9339 | 44.4337 | 46.9708
22.9885 | 46.3714 | 46.9103 | 49.3935
23.9885 | 47.8444 | 48.3753 | 51.1758
24.9885 | 50.1467 | 50.9909 | 53.1569
25.9885 | 51.8537 | 50.9125 | 55.999
26.9885 | 53.0108 | 55.3552 | 57.7964
27.9885 | 54.1795 | 54.9601 | 60.1405
28.9885 | 55.8281 | 55.4046 | 61.434
29.9885 | 57.4656 | 58.4652 | 63.3135
30.9885 | 59.0694 | 62.5808 | 64.616
31.9885 | 60.8116 | 63.7904 | 66.7494
32.9885 | 62.0121 | 62.8303 | 67.7897
33.9885 | 64.2942 | 64.7674 | 69.0395
34.9885 | 66.0651 | 67.9335 | 70.4023
35.9885 | 67.6843 | 66.2629 | 72.1834
36.9885 | 69.5644 | 68.5867 | 73.8715
37.9885 | 71.2358 | 70.0945 | 75.4608
38.9885 | 72.022 | 73.4755 | 77.5007
39.9885 | 72.6651 | 72.1922 | 78.7279
40.9885 | 74.2955 | 71.9599 | 80.6737
41.9885 | 74.9553 | 74.6389 | 81.7953
42.9885 | 75.9887 | 75.4001 | 83.7454
43.9885 | 76.976 | 76.9021 | 84.8059
44.9885 | 77.5995 | 79.7073 | 85.2163
45.9885 | 78.957 | 84.1308 | 86.3596
46.9885 | 80.4258 | 83.2153 | 88.22
47.9885 | 81.5239 | 87.6948 | 89.2155
48.9885 | 82.8581 | 88.9504 | 90.1456
49.9885 | 84.7556 | 90.2675 | 91.3262
50.9885 | 85.9471 | 87.2859 | 92.5027
51.9885 | 87.8626 | 92.6791 | 93.6736
52.9885 | 89.3272 | 93.6927 | 95.5255
53.9885 | 90.7166 | 94.8748 | 96.2869
54.9885 | 91.5412 | 95.9466 | 97.1943
55.9885 | 92.5495 | 97.4079 | 98.1131
56.9885 | 93.4801 | 97.8858 | 99.0594
57.9885 | 94.2102 | 99.125 | 100.168
58.9885 | 95.9653 | 99.8547 | 100.9438
59.9885 | 97.0212 | 100.5739 | 101.3444
60.9885 | 97.2585 | 101.4601 | 101.7307
61.9885 | 98.6709 | 102.5646 | 102.3507
62.9885 | 100.0866 | 103.4215 | 102.8597
63.9885 | 101.1129 | 104.1456 | 103.5843
64.9885 | 101.4871 | 105.8819 | 104.6981
65.9885 | 102.6842 | 106.8815 | 105.5483
66.9885 | 103.4088 | 107.714 | 106.0226
67.9885 | 105.0492 | 108.865 | 107.0941
68.9885 | 105.8484 | 109.4501 | 108.4074
69.9885 | 106.108 | 109.8377 | 109.2149
70.9885 | 106.4779 | 110.4655 | 110.0847
71.9885 | 106.9761 | 111.3002 | 110.7364
72.9885 | 108.2889 | 111.9792 | 111.2337
73.9885 | 108.6731 | 112.392 | 111.7909
74.9885 | 109.7969 | 113.201 | 112.2079
75.9885 | 109.7995 | 113.8149 | 113.9412
76.9885 | 110.527 | 114.6833 | 115.2498
77.9885 | 111.1803 | 115.2212 | 116.0226
78.9885 | 111.9079 | 116.0762 | 117.0611
79.9885 | 112.7225 | 116.5176 | 117.5365
80.9885 | 113.1946 | 117.0914 | 117.9918
81.9885 | 114.5258 | 117.6743 | 118.8654
82.9885 | 116.0447 | 118.4245 | 119.5129
83.9885 | 116.7308 | 119.4087 | 120.3067
84.9885 | 117.0763 | 120.1929 | 121.0538
85.9885 | 117.9291 | 121.4962 | 121.8764
86.9885 | 118.8798 | 121.9451 | 122.1789
87.9885 | 119.904 | 122.4667 | 122.7097
88.9885 | 119.7474 | 122.8691 | 123.2521
89.9885 | 119.7909 | 123.1729 | 123.7288
90.9885 | 121.072 | 123.6184 | 124.1538
91.9885 | 121.46 | 124.1615 | 124.0998
92.9885 | 122.3434 | 124.5784 | 124.1406
93.9885 | 122.7037 | 124.7502 | 124.1714
94.9885 | 122.3344 | 125.1237 | 124.9372
95.9885 | 122.6839 | 125.276 | 125.8846
96.9885 | 122.4226 | 125.3975 | 126.803
97.9885 | 122.6515 | 125.6374 | 127.1612
98.9885 | 122.787 | 125.7156 | 127.2854
99.9885 | 122.9593 | 125.8727 | 127.3789
100.9885 | 122.9679 | 126.1816 | 127.6474
101.9885 | 123.0656 | 126.4185 | 128.3245
102.9885 | 123.1774 | 126.5854 | 128.3271
103.9885 | 123.1076 | 126.8224 | 128.3462
104.9885 | 123.3761 | 127.01 | 128.6626
105.9885 | 123.8424 | 127.3385 | 129.3584
106.9885 | 124.4908 | 127.2211 | 129.8612
107.9885 | 124.7143 | 127.4776 | 130.4122
108.9885 | 125.05 | 127.54 | 130.9289
109.9885 | 125.4105 | 128.414 | 131.3012
110.9885 | 125.7535 | 128.5116 | 131.6993
111.9885 | 125.9805 | 128.998 | 132.6911
112.9885 | 126.6775 | 129.9879 | 133.5518
113.9885 | 127.2509 | 130.1242 | 134.2376
114.9885 | 127.491 | 130.5368 | 134.8273
115.9885 | 127.9086 | 130.6405 | 135.4237
116.9885 | 128.1963 | 130.3659 | 135.3087
117.9885 | 128.3615 | 130.0075 | 135.3071
118.9885 | 128.8448 | 130.0048 | 136.5358
119.9885 | 128.9645 | 129.7537 | 136.7133
120.9885 | 128.7893 | 130.0606 | 137.4149
121.9885 | 128.5478 | 130.0744 | 138.0706
122.9885 | 128.3055 | 130.0844 | 138.6525
123.9885 | 128.241 | 130.4059 | 138.6314
124.9885 | 128.0193 | 130.9429 | 138.3606
125.9885 | 128.3612 | 131.0375 | 138.3934
126.9885 | 128.5594 | 131.3996 | 138.5449
127.9885 | 128.6603 | 131.81 | 138.6511
128.9885 | 129.6656 | 132.346 | 138.78
129.9885 | 130.2081 | 133.1054 | 139.2789
130.9885 | 130.6202 | 133.3838 | 139.1419
131.9885 | 130.3838 | 133.6002 | 138.7301
132.9885 | 130.0657 | 133.7052 | 138.5225
133.9885 | 130.3902 | 134.0899 | 138.3383
134.9885 | 130.5329 | 133.9738 | 138.1524
135.9885 | 131.5356 | 134.3099 | 137.9953
136.9885 | 132.2567 | 134.8868 | 137.6281
137.9885 | 132.4833 | 134.995 | 137.4538
138.9885 | 132.7855 | 135.4246 | 137.3862
139.9885 | 133.6274 | 135.6372 | 137.3185
140.9885 | 134.0593 | 135.7988 | 137.7966
141.9885 | 133.8966 | 136.0639 | 138.1658
142.9885 | 134.5368 | 136.5057 | 138.5604
143.9885 | 135.0641 | 136.6335 | 138.9107
144.9885 | 135.695 | 137.1765 | 138.842
145.9885 | 135.7656 | 137.2605 | 139.019
146.9885 | 135.4342 | 137.4168 | 139.0956
147.9885 | 135.2384 | 137.9457 | 139.363
148.9885 | 135.4965 | 138.5659 | 139.8442
149.9885 | 135.7324 | 139.1433 | 139.979
150.9885 | 136.5484 | 139.3624 | 140.6416
151.9885 | 136.5663 | 139.3891 | 140.9969
152.9885 | 137.1955 | 139.8631 | 142.431
153.9885 | 137.3579 | 140.1076 | 142.4274
154.9885 | 137.6332 | 140.6965 | 142.9909
155.9885 | 138.0448 | 141.1906 | 143.7164
156.9885 | 138.6859 | 141.8787 | 143.5565
157.9885 | 139.4525 | 142.4081 | 143.7739
158.9885 | 139.9453 | 142.8324 | 144.0928
159.9885 | 140.7335 | 143.1348 | 144.024
160.9885 | 141.1777 | 143.1315 | 144.3541
161.9885 | 141.3035 | 143.2731 | 144.4561
162.9885 | 140.9248 | 143.0092 | 144.3662
163.9885 | 141.2508 | 143.0689 | 144.4306
164.9885 | 141.9206 | 142.8162 | 144.5913
165.9885 | 142.3716 | 142.9661 | 145.1149
166.9885 | 142.6203 | 143.2926 | 145.1484
167.9885 | 142.7552 | 143.7621 | 145.183
168.9885 | 142.5447 | 144.0669 | 145.7518
169.9885 | 143.2432 | 144.0125 | 145.9887
170.9885 | 143.772 | 144.1368 | 145.935
171.9885 | 143.7878 | 144.144 | 146.2656
172.9885 | 143.3414 | 144.653 | 146.15
173.9885 | 143.2545 | 145.2117 | 145.7668
174.9885 | 143.4351 | 145.0251 | 145.4318
175.9885 | 144.2295 | 145.0126 | 145.3207
176.9885 | 144.3382 | 145.0178 | 145.527
177.9885 | 143.935 | 144.9761 | 145.931
178.9885 | 143.473 | 145.0073 | 146.1354
179.9885 | 143.4019 | 145.0016 | 146.0161
180.9885 | 142.9672 | 144.8454 | 146.0022
181.9885 | 142.9383 | 144.7553 | 145.6835
182.9885 | 143.3303 | 145.123 | 146.1641
183.9885 | 143.3187 | 145.3726 | 146.6283
184.9885 | 143.3803 | 145.5671 | 146.822
185.9885 | 143.5349 | 145.7637 | 147.0496
186.9885 | 143.6908 | 146.0063 | 147.0186
187.9885 | 143.5929 | 145.7011 | 147.2449
188.9885 | 143.5292 | 145.7134 | 147.8302
189.9885 | 143.9663 | 145.6978 | 148.0897
190.9885 | 144.2979 | 145.7477 | 147.8617
191.9885 | 145.1621 | 145.7453 | 147.6589
192.9885 | 145.0194 | 145.8066 | 147.4317
193.9885 | 144.4103 | 145.778 | 147.5278
194.9885 | 143.8968 | 145.9865 | 147.5771
195.9885 | 144.277 | 146.1698 | 147.7079
196.9885 | 144.6936 | 146.4519 | 147.9581
197.9885 | 144.9748 | 146.5931 | 148.3199
198.9885 | 144.9213 | 146.7374 | 148.918
199.9885 | 144.7052 | 148.1972 | 149.1985
200.9885 | 145.0195 | 148.5779 | 149.4698
201.9885 | 145.8897 | 148.9113 | 150.4897
202.9885 | 146.2323 | 149.121 | 150.56
203.9885 | 147.4246 | 149.6237 | 150.6
204.9885 | 148.2149 | 149.9788 | 151.3644
205.9885 | 148.4621 | 150.5822 | 151.5133
206.9885 | 148.7871 | 151.2106 | 151.9178
207.9885 | 148.935 | 151.78 | 153.0285
208.9885 | 149.1711 | 151.8934 | 153.3792
209.9885 | 149.6242 | 152.2593 | 153.8282
210.9885 | 149.7349 | 152.4533 | 153.7217
211.9885 | 149.7855 | 153.1406 | 154.2787
212.9885 | 150.0816 | 153.3039 | 154.6416
213.9885 | 150.4574 | 153.5435 | 154.8321
214.9885 | 150.5338 | 153.8836 | 154.7701
215.9885 | 150.6602 | 153.9957 | 154.8711
216.9885 | 150.974 | 154.4624 | 154.7219
217.9885 | 151.232 | 154.7326 | 154.3781
218.9885 | 151.3744 | 154.8854 | 153.9653
219.9885 | 151.5654 | 155.1179 | 153.8528
220.9885 | 151.3738 | 155.538 | 154.5168
221.9885 | 151.9121 | 156.4729 | 154.9342
222.9885 | 152.149 | 156.4694 | 155.5007
223.9885 | 152.1763 | 156.6262 | 155.6191
224.9885 | 152.4747 | 156.8212 | 155.2772
225.9885 | 152.5813 | 157.0323 | 155.0455
226.9885 | 152.7534 | 157.2412 | 155.0148
227.9885 | 153.4884 | 157.6961 | 154.9282
228.9885 | 154.2229 | 158.039 | 154.9995
229.9885 | 154.5232 | 158.3096 | 154.9928
230.9885 | 154.349 | 158.4404 | 154.8346
231.9885 | 154.8458 | 158.6017 | 155.0409
232.9885 | 155.3038 | 158.6019 | 154.7738
233.9885 | 155.1585 | 158.7386 | 154.5009
234.9885 | 155.2765 | 158.7711 | 154.6392
235.9885 | 155.5741 | 158.9357 | 155.0076
236.9885 | 155.8083 | 158.9094 | 155.3783
237.9885 | 155.6366 | 158.9681 | 155.5158
238.9885 | 155.6075 | 159.0599 | 155.5256
239.9885 | 155.9159 | 159.4171 | 155.5778
240.9885 | 155.6343 | 160.7119 | 156.3356
241.9885 | 155.4521 | 160.7327 | 156.1854
242.9885 | 155.5361 | 160.6544 | 156.3371
243.9885 | 155.4235 | 161.0616 | 156.7234
244.9885 | 155.2313 | 161.5065 | 157.4167
245.9885 | 154.9817 | 161.3695 | 157.7319
246.9885 | 154.8086 | 161.3465 | 157.8427
247.9885 | 155.0992 | 161.2418 | 157.9646
248.9885 | 155.1839 | 161.2451 | 158.0014
249.9885 | 155.5977 | 161.0835 | 158.5003
250.9885 | 155.9075 | 161.1458 | 158.382
251.9885 | 156.5376 | 161.3432 | 158.6264
252.9885 | 156.9595 | 161.4651 | 158.7739
253.9885 | 157.0458 | 161.4307 | 158.8778
254.9885 | 157.4645 | 161.624 | 159.0307
255.9885 | 157.5105 | 162.3356 | 159.1209
256.9885 | 158.0205 | 162.6641 | 159.0349
257.9885 | 158.3768 | 162.7856 | 159.5265
258.9885 | 159.1135 | 163.1035 | 159.9165
259.9885 | 160.2321 | 163.7351 | 160.1803
260.9885 | 160.2035 | 163.9916 | 160.2999
261.9885 | 160.285 | 164.2576 | 160.7788
262.9885 | 161.1742 | 164.3557 | 160.7058
263.9885 | 161.3337 | 164.5552 | 160.6662
264.9885 | 161.79 | 164.8639 | 160.8396
265.9885 | 162.6512 | 166.1407 | 161.4208
266.9885 | 163.2008 | 166.4839 | 161.924
267.9885 | 162.7395 | 166.8516 | 162.0725
268.9885 | 162.6092 | 167.0662 | 162.2582
269.9885 | 162.3221 | 167.294 | 162.7361
270.9885 | 161.7233 | 167.4453 | 163.1377
271.9885 | 161.8805 | 167.5932 | 163.5659
272.9885 | 161.6126 | 167.7975 | 164.0966
273.9885 | 161.5907 | 167.9498 | 164.2058
274.9885 | 161.8014 | 168.0945 | 164.3192
275.9885 | 162.1733 | 168.0724 | 165.4139
276.9885 | 162.1353 | 168.4396 | 165.1018
277.9885 | 163.5471 | 168.7139 | 164.7424
278.9885 | 163.7325 | 169.1414 | 164.8348
279.9885 | 163.6997 | 169.621 | 165.0584
280.9885 | 164.2662 | 169.7869 | 165.0354
281.9885 | 164.666 | 169.755 | 165.2802
282.9885 | 164.8569 | 169.6773 | 165.5321
283.9885 | 165.146 | 169.7775 | 165.6951
284.9885 | 165.7689 | 169.9373 | 165.9597
285.9885 | 165.9695 | 170.3142 | 166.3385
286.9885 | 165.9455 | 170.6176 | 166.4406
287.9885 | 166.1909 | 171.0012 | 166.7222
288.9885 | 166.5573 | 171.0901 | 167.1387
289.9885 | 166.9647 | 171.6382 | 167.8426
290.9885 | 167.0771 | 171.7183 | 168.0992
291.9885 | 167.1666 | 171.8539 | 168.4305
292.9885 | 167.9768 | 172.1551 | 168.5581
293.9885 | 169.4338 | 172.5093 | 168.9277
294.9885 | 170.0156 | 172.5919 | 169.6932
295.9885 | 171.0531 | 172.6464 | 170.0001
296.9885 | 171.7747 | 173.034 | 170.5695
297.9885 | 171.3436 | 173.4146 | 170.788
298.9885 | 171.4478 | 173.8159 | 170.8545
299.9885 | 171.3462 | 174.0753 | 170.6303
300.9885 | 171.8923 | 174.168 | 170.6697
301.9885 | 172.1833 | 174.2467 | 170.7622
302.9885 | 171.7563 | 174.6215 | 170.6717
303.9885 | 172.0797 | 174.7848 | 170.5672
304.9885 | 171.9301 | 175.0761 | 171.8692
305.9885 | 171.7898 | 175.363 | 172.2148
306.9885 | 171.5934 | 175.343 | 172.2454
307.9885 | 171.7588 | 175.5057 | 172.4691
308.9885 | 172.0577 | 175.6047 | 172.4962
309.9885 | 172.0635 | 175.5834 | 172.8738
310.9885 | 171.6863 | 175.5302 | 173.3445
311.9885 | 171.5864 | 176.0389 | 173.8769
312.9885 | 172.0832 | 176.3023 | 174.4469
313.9885 | 172.2996 | 176.7783 | 174.6169
314.9885 | 172.9455 | 177.3246 | 174.9987
315.9885 | 172.6227 | 177.6868 | 175.1728
316.9885 | 172.6612 | 178.2535 | 175.7704
317.9885 | 173.0344 | 178.4836 | 176.4892
318.9885 | 173.7978 | 179.1472 | 176.836
319.9885 | 174.4409 | 179.2565 | 176.9568
320.9885 | 175.0079 | 179.4028 | 176.8972
321.9885 | 175.4199 | 179.4409 | 176.9438
322.9885 | 175.7656 | 179.5191 | 176.9767
323.9885 | 176.9257 | 179.7578 | 177.1046
324.9885 | 177.0683 | 179.7945 | 177.4823
325.9885 | 177.1268 | 179.9807 | 178.2011
326.9885 | 177.258 | 180.2784 | 178.7001
327.9885 | 177.4917 | 180.8043 | 179.2958
328.9885 | 177.4557 | 182.3904 | 180.1611
329.9885 | 177.8341 | 183.1138 | 180.799
330.9885 | 178.3289 | 183.441 | 181.1921
331.9885 | 178.8869 | 183.5839 | 181.8423
332.9885 | 179.0302 | 183.8845 | 181.6415
333.9885 | 179.6199 | 184.5911 | 181.5206
334.9885 | 179.499 | 184.4754 | 181.6574
335.9885 | 179.4916 | 184.4536 | 181.671
336.9885 | 180.1188 | 184.6786 | 181.9708
337.9885 | 181.1164 | 184.6339 | 182.2646
338.9885 | 181.7787 | 184.4446 | 182.2062
339.9885 | 182.1236 | 184.5397 | 182.1364
340.9885 | 182.6627 | 184.4428 | 182.1555
341.9885 | 182.6879 | 184.9307 | 182.3297
342.9885 | 182.9967 | 185.0944 | 182.5154
343.9885 | 182.7134 | 185.0486 | 182.8513
344.9885 | 182.5541 | 185.1439 | 182.8836
345.9885 | 183.0016 | 185.47 | 182.5265
346.9885 | 183.7041 | 185.2523 | 182.6642
347.9885 | 184.3299 | 185.7943 | 182.8117
348.9885 | 185.0718 | 186.3405 | 183.0187
349.9885 | 185.2589 | 186.0596 | 182.922
350.9885 | 185.7954 | 186.0358 | 183.1696
351.9885 | 186.3982 | 186.0591 | 183.4842
352.9885 | 186.7446 | 186.3141 | 184.1428
353.9885 | 187.5057 | 186.7408 | 184.3125
354.9885 | 188.223 | 187.3229 | 185.1583
355.9885 | 188.9636 | 187.8191 | 185.6547
356.9885 | 189.9306 | 188.337 | 186.1325
357.9885 | 190.1356 | 188.8916 | 186.871
358.9885 | 190.2366 | 188.5167 | 187.3537
359.9885 | 190.5646 | 189.4786 | 187.3908
360.9885 | 190.6616 | 189.6813 | 187.6342
361.9885 | 190.7586 | 189.8084 | 188.3059
362.9885 | 191.5308 | 189.8137 | 188.7219
363.9885 | 192.2679 | 190.1161 | 189.4143
364.9885 | 191.7667 | 190.2567 | 189.5021
365.9885 | 191.4843 | 190.3786 | 189.6976
366.9885 | 192.3419 | 191.1863 | 189.6059
367.9885 | 192.0543 | 191.5051 | 189.9444
368.9885 | 191.798 | 191.8715 | 190.6552
369.9885 | 192.3326 | 192.5619 | 191.2433
370.9885 | 192.416 | 192.8531 | 191.5199
371.9885 | 193.0848 | 192.8281 | 191.7545
372.9885 | 193.5954 | 193.5286 | 191.709
373.9885 | 193.7314 | 194.1952 | 192.0925
374.9885 | 193.9947 | 195.146 | 191.8896
375.9885 | 194.3433 | 194.9576 | 192.2066
376.9885 | 194.5799 | 195.3933 | 191.897
377.9885 | 194.0633 | 195.4982 | 191.8537
378.9885 | 193.7506 | 195.2238 | 191.6733
379.9885 | 193.8211 | 194.9524 | 191.7128
380.9885 | 193.9569 | 195.0992 | 192.2058
381.9885 | 193.9402 | 195.5667 | 192.7674
382.9885 | 194.3606 | 195.7205 | 192.8612
383.9885 | 195.1064 | 196.1695 | 192.7567
384.9885 | 196.2804 | 196.7443 | 192.9002
385.9885 | 196.8525 | 197.3057 | 193.2586
386.9885 | 197.4626 | 197.926 | 193.6215
387.9885 | 197.4203 | 198.4174 | 194.1684
388.9885 | 196.9176 | 198.7498 | 194.3381
389.9885 | 197.3749 | 199.0992 | 193.7893
390.9885 | 197.403 | 199.5298 | 194.2611
391.9885 | 197.2145 | 199.8536 | 194.548
392.9885 | 196.9034 | 200.1137 | 194.627
393.9885 | 197.2826 | 200.5692 | 194.8959
394.9885 | 197.6373 | 200.8071 | 195.387
395.9885 | 197.5666 | 201.2463 | 195.7622
396.9885 | 197.5764 | 201.6713 | 195.9503
397.9885 | 197.5001 | 201.7798 | 196.0432
398.9885 | 197.7329 | 201.7943 | 196.2379
399.9885 | 197.6903 | 202.2189 | 196.7278
400.9885 | 197.6068 | 202.4938 | 196.938
401.9885 | 197.3446 | 202.799 | 197.2733
402.9885 | 197.5208 | 202.7518 | 197.5837
403.9885 | 197.7485 | 202.5308 | 197.7687
404.9885 | 197.4398 | 202.3742 | 197.7976
405.9885 | 197.6451 | 201.9688 | 197.9561
406.9885 | 197.8047 | 202.4941 | 198.8287
407.9885 | 198.0377 | 202.6682 | 199.3303
408.9885 | 198.0422 | 202.918 | 200.296
409.9885 | 198.3429 | 203.2859 | 200.8746
410.9885 | 199.3491 | 203.1441 | 202.3616
411.9885 | 199.5138 | 203.2685 | 203.4247
412.9885 | 200.1041 | 202.9554 | 203.8423
413.9885 | 199.8695 | 202.7954 | 204.8002
414.9885 | 200.0496 | 203.0091 | 205.9031
415.9885 | 199.7773 | 203.5461 | 207.0507
416.9885 | 199.8066 | 203.7915 | 208.4688
417.9885 | 200.2034 | 205.0618 | 208.923
418.9885 | 200.5619 | 204.6632 | 208.8657
419.9885 | 201.2851 | 204.7144 | 209.5813
420.9885 | 201.5934 | 205.4776 | 209.9787
421.9885 | 201.9013 | 205.4574 | 210.4131
422.9885 | 202.4373 | 205.7102 | 210.7927
423.9885 | 203.4363 | 205.8598 | 211.1755
424.9885 | 203.8999 | 205.7548 | 211.8961
425.9885 | 204.4709 | 206.8749 | 213.1441
426.9885 | 204.6839 | 207.3392 | 212.9963
427.9885 | 204.4059 | 206.9725 | 213.2802
428.9885 | 203.7901 | 206.8056 | 213.0926
429.9885 | 203.5403 | 206.6772 | 213.1446
430.9885 | 203.6508 | 206.6876 | 213.1799
431.9885 | 203.3408 | 206.9923 | 212.9901
432.9885 | 202.7545 | 206.8424 | 212.8587
433.9885 | 202.5254 | 206.9333 | 212.3867
434.9885 | 202.5958 | 207.1592 | 212.4425
435.9885 | 203.2561 | 207.3736 | 212.3233
436.9885 | 203.4568 | 207.8144 | 212.2963
437.9885 | 203.5336 | 208.1035 | 212.1513
438.9885 | 202.995 | 208.4558 | 211.8599
439.9885 | 203.1519 | 208.2396 | 211.5367
440.9885 | 203.5739 | 207.9532 | 211.3657
441.9885 | 203.4424 | 207.8521 | 211.1775
442.9885 | 203.1601 | 207.7917 | 211.2208
443.9885 | 203.853 | 208.0229 | 211.9454
444.9885 | 203.6855 | 208.3071 | 212.6757
445.9885 | 203.1746 | 208.2318 | 213.0344
446.9885 | 203.1578 | 208.0429 | 213.1307
447.9885 | 203.2843 | 207.9957 | 213.3677
448.9885 | 204.9865 | 207.6892 | 213.4829
449.9885 | 205.4697 | 207.803 | 214.4021
450.9885 | 205.3945 | 207.738 | 214.6589
451.9885 | 204.9105 | 208.3831 | 215.256
452.9885 | 204.7898 | 208.7864 | 215.1689
453.9885 | 204.2252 | 209.2161 | 215.1614
454.9885 | 204.1986 | 210.01 | 214.9614
455.9885 | 204.0903 | 209.8793 | 215.2044
456.9885 | 204.2291 | 209.5986 | 215.2155
457.9885 | 204.8134 | 210.7917 | 215.4382
458.9885 | 204.9343 | 210.3929 | 214.8585
459.9885 | 205.439 | 210.3722 | 214.4259
460.9885 | 204.7422 | 210.452 | 214.3179
461.9885 | 204.7124 | 210.5643 | 214.0042
462.9885 | 204.8683 | 210.7406 | 213.6533
463.9885 | 204.1522 | 210.5451 | 213.7028
464.9885 | 204.8593 | 210.3123 | 214.0322
465.9885 | 205.4191 | 210.4775 | 214.4733
466.9885 | 205.8462 | 211.1638 | 214.874
467.9885 | 206.3324 | 211.5422 | 215.3686
468.9885 | 206.4423 | 211.7958 | 215.6933
469.9885 | 206.5505 | 212.2377 | 216.0318
470.9885 | 206.4688 | 212.4712 | 215.9403
471.9885 | 206.2038 | 212.5659 | 215.4507
472.9885 | 206.0582 | 212.6802 | 215.2006
473.9885 | 206.1711 | 212.6555 | 215.1985
474.9885 | 206.0543 | 212.661 | 214.8104
475.9885 | 205.8851 | 212.5132 | 214.9325
476.9885 | 206.2557 | 212.7245 | 215.0692
477.9885 | 206.5755 | 212.9496 | 214.7897
478.9885 | 206.5026 | 213.2865 | 214.8731
479.9885 | 207.2024 | 213.5964 | 215.0816
480.9885 | 207.1829 | 213.728 | 214.5458
481.9885 | 207.3225 | 213.4523 | 214.8576
482.9885 | 207.6142 | 213.6431 | 215.1527
483.9885 | 207.9677 | 213.9089 | 215.52
484.9885 | 208.0873 | 214.0722 | 215.7552
485.9885 | 207.1475 | 214.2997 | 216.0604
486.9885 | 206.6973 | 214.27 | 215.8677
487.9885 | 206.2489 | 214.1367 | 215.7007
488.9885 | 206.0156 | 213.7384 | 215.3354
489.9885 | 206.4746 | 213.5433 | 215.0372
490.9885 | 205.9111 | 213.4997 | 214.5207
491.9885 | 206.2024 | 213.6049 | 214.202
492.9885 | 206.4608 | 213.4627 | 214.2638
493.9885 | 207.0134 | 213.5071 | 214.1934
494.9885 | 207.1097 | 214.1022 | 214.4263
495.9885 | 207.1555 | 214.2558 | 215.0863
496.9885 | 206.9646 | 214.4263 | 214.3
497.9885 | 206.3941 | 214.5031 | 214.2744
498.9885 | 206.6411 | 214.596 | 213.8999
499.9885 | 207.1864 | 214.7847 | 214.2421
500.9885 | 206.7397 | 215.3215 | 215.3462
501.9885 | 206.909 | 215.2994 | 216.0378
502.9885 | 207.3277 | 215.0928 | 216.8779
503.9885 | 207.4791 | 215.0353 | 217.0304
504.9885 | 207.382 | 214.7044 | 217.1529
505.9885 | 207.8758 | 214.6345 | 217.6177
506.9885 | 207.8262 | 214.4489 | 217.3103
507.9885 | 207.1129 | 214.6876 | 217.4582
508.9885 | 206.6161 | 215.0366 | 217.5144
509.9885 | 206.4608 | 215.028 | 217.8229
510.9885 | 206.6659 | 215.0898 | 218.766
511.9885 | 206.7846 | 214.596 | 219.1389
512.9885 | 206.8143 | 214.4616 | 219.727
513.9885 | 207.5474 | 215.9592 | 219.837
514.9885 | 208.1281 | 215.6949 | 219.5995
515.9885 | 208.2839 | 215.7716 | 219.8614
516.9885 | 208.2705 | 215.7185 | 220.2767
517.9885 | 207.7685 | 215.2976 | 220.8855
518.9885 | 207.1369 | 214.8597 | 221.0228
519.9885 | 207.0593 | 214.8095 | 220.3491
520.9885 | 206.9323 | 214.6714 | 219.962
521.9885 | 207.2437 | 214.7688 | 219.6826
522.9885 | 207.627 | 214.7709 | 219.0993
523.9885 | 207.6659 | 214.4327 | 218.6486
524.9885 | 208.1266 | 214.7799 | 218.3425
525.9885 | 208.5599 | 214.7565 | 217.928
526.9885 | 209.0881 | 214.8407 | 218.0235
527.9885 | 209.169 | 214.9832 | 218.1624
528.9885 | 209.249 | 215.2323 | 217.8121
529.9885 | 209.8104 | 215.4303 | 218.1148
530.9885 | 209.9526 | 215.2976 | 217.9019
531.9885 | 209.6984 | 215.5047 | 218.6743
532.9885 | 209.5493 | 215.3521 | 218.8504
533.9885 | 210.0865 | 215.2862 | 219.2547
534.9885 | 210.8676 | 214.9266 | 218.9851
535.9885 | 211.0135 | 214.8729 | 218.6821
536.9885 | 212.2554 | 214.8149 | 218.3834
537.9885 | 212.4813 | 214.8736 | 218.2368
538.9885 | 212.0233 | 215.0254 | 218.6096
539.9885 | 211.3531 | 215.1722 | 218.1706
540.9885 | 211.2489 | 215.4885 | 217.7079
541.9885 | 210.8247 | 216.029 | 217.5223
542.9885 | 210.5397 | 216.2262 | 217.0477
543.9885 | 210.9596 | 216.725 | 216.9964
544.9885 | 211.2771 | 216.7665 | 216.5884
545.9885 | 211.1768 | 216.8058 | 217.0276
546.9885 | 210.93 | 216.7505 | 217.0312
547.9885 | 210.7227 | 216.7013 | 216.9991
548.9885 | 210.3626 | 216.6408 | 216.8102
549.9885 | 210.0135 | 216.5978 | 216.6367
550.9885 | 209.8704 | 216.659 | 216.9814
551.9885 | 210.016 | 216.7161 | 217.498
552.9885 | 209.9072 | 216.7353 | 217.3749
553.9885 | 210.1096 | 218.0248 | 217.4594
554.9885 | 210.1499 | 217.7371 | 217.9974
555.9885 | 210.3252 | 217.9536 | 218.5616
556.9885 | 210.3962 | 217.9713 | 218.4803
557.9885 | 210.5894 | 218.2683 | 218.5114
558.9885 | 210.9133 | 218.4064 | 218.9542
559.9885 | 210.7134 | 218.5122 | 218.9232
560.9885 | 210.8213 | 218.852 | 219.6576
561.9885 | 211.2167 | 218.4184 | 220.1224
562.9885 | 211.3967 | 218.0603 | 220.8471
563.9885 | 212.0758 | 217.744 | 221.9134
564.9885 | 212.7532 | 217.1416 | 222.255
565.9885 | 213.7876 | 217.1036 | 222.4158
566.9885 | 214.2464 | 216.6156 | 222.9423
567.9885 | 214.7658 | 216.2241 | 222.9484
568.9885 | 214.6369 | 215.929 | 223.3144
569.9885 | 215.2406 | 215.8401 | 224.0451
570.9885 | 215.2413 | 215.7306 | 223.5327
571.9885 | 215.3122 | 216.1591 | 223.5832
572.9885 | 215.8421 | 216.9254 | 223.1297
573.9885 | 215.9258 | 217.3668 | 223.0028
574.9885 | 216.2498 | 217.7371 | 223.8332
575.9885 | 216.3935 | 217.6362 | 223.5428
576.9885 | 216.3632 | 217.3578 | 223.8715
577.9885 | 217.12 | 217.271 | 224.208
578.9885 | 216.4014 | 217.1166 | 224.2062
579.9885 | 216.2992 | 216.9885 | 223.9904
580.9885 | 216.4805 | 216.6021 | 223.5338
581.9885 | 216.4488 | 216.5864 | 223.3221
582.9885 | 217.0259 | 216.5493 | 223.3052
583.9885 | 217.0718 | 216.8401 | 223.527
584.9885 | 216.4852 | 216.7999 | 223.3861
585.9885 | 216.2265 | 216.9366 | 223.0605
586.9885 | 216.093 | 216.6132 | 222.6563
587.9885 | 216.1036 | 216.5711 | 222.5831
588.9885 | 216.5083 | 216.3447 | 223.0827
589.9885 | 217.2108 | 217.076 | 223.1458
590.9885 | 217.4467 | 217.7875 | 223.6345
591.9885 | 217.9464 | 218.014 | 223.7233
592.9885 | 218.3487 | 218.1145 | 224.2149
593.9885 | 218.4457 | 218.0588 | 224.6656
594.9885 | 218.58 | 218.2422 | 224.9013
595.9885 | 218.9207 | 218.4669 | 225.6061
596.9885 | 219.4581 | 218.2882 | 225.4042
597.9885 | 219.9312 | 217.7719 | 224.9233
598.9885 | 220.3422 | 217.5953 | 224.9264
599.9885 | 220.6417 | 217.7811 | 224.9533
600.9885 | 221.4062 | 218.5404 | 225.3375
601.9885 | 221.5556 | 218.6693 | 226.0084
602.9885 | 221.606 | 219.5847 | 225.8206
603.9885 | 221.3273 | 220.096 | 226.6193
604.9885 | 221.47 | 220.1688 | 226.4655
605.9885 | 222.2502 | 220.1573 | 226.6557
606.9885 | 221.9052 | 220.1983 | 226.9475
607.9885 | 221.6827 | 220.1632 | 226.6994
608.9885 | 222.0504 | 220.0766 | 226.1376
609.9885 | 222.1931 | 220.4421 | 225.5816
610.9885 | 222.2031 | 220.0154 | 226.1871
611.9885 | 222.314 | 219.9992 | 226.2837
612.9885 | 222.5818 | 220.9046 | 227.0528
613.9885 | 223.4204 | 221.2509 | 227.3766
614.9885 | 223.9918 | 221.371 | 227.1932
615.9885 | 224.58 | 221.3517 | 227.2848
616.9885 | 225.1182 | 221.728 | 227.1841
617.9885 | 225.522 | 221.4482 | 227.512
618.9885 | 225.4808 | 221.0135 | 227.4884
619.9885 | 225.7966 | 221.501 | 227.3193
620.9885 | 226.1763 | 221.5293 | 227.7128
621.9885 | 226.1177 | 221.2382 | 227.729
622.9885 | 226.5891 | 222.0163 | 227.4156
623.9885 | 226.8279 | 221.9484 | 227.0922
624.9885 | 226.7469 | 221.3319 | 227.4399
625.9885 | 227.2914 | 220.7186 | 227.2593
626.9885 | 227.2974 | 220.7547 | 226.8124
627.9885 | 227.7365 | 220.775 | 226.9212
628.9885 | 227.9139 | 220.613 | 226.9832
629.9885 | 227.6651 | 220.7039 | 226.8412
630.9885 | 228.015 | 219.976 | 227.5965
631.9885 | 227.8327 | 219.9681 | 227.8662
632.9885 | 227.9131 | 220.0463 | 227.7804
633.9885 | 227.9079 | 219.8145 | 227.5989
634.9885 | 228.1015 | 219.6088 | 227.6441
635.9885 | 228.4453 | 219.3211 | 227.4686
636.9885 | 228.7549 | 219.1375 | 227.3335
637.9885 | 229.0204 | 218.9281 | 227.1227
638.9885 | 228.987 | 218.9277 | 227.0705
639.9885 | 229.1851 | 219.1092 | 227.583
640.9885 | 228.9989 | 219.4321 | 227.3654
641.9885 | 229.2356 | 219.5616 | 227.4673
642.9885 | 229.098 | 220.0239 | 227.76
643.9885 | 229.1518 | 220.0236 | 228.1167
644.9885 | 228.8499 | 220.145 | 228.0207
645.9885 | 228.9341 | 220.4412 | 227.4037
646.9885 | 228.5029 | 220.7323 | 226.9416
647.9885 | 228.3718 | 220.647 | 226.8559
648.9885 | 228.3121 | 220.7998 | 226.9251
649.9885 | 228.1421 | 220.5459 | 227.3261
650.9885 | 228.138 | 220.5726 | 227.1027
651.9885 | 228.1078 | 220.6756 | 226.7552
652.9885 | 228.262 | 220.8174 | 226.9976
653.9885 | 228.2442 | 221.0709 | 226.5479
654.9885 | 228.5138 | 221.1695 | 226.8007
655.9885 | 228.4699 | 221.6513 | 226.762
656.9885 | 228.2528 | 221.7294 | 226.5738
657.9885 | 228.1125 | 221.6904 | 226.3305
658.9885 | 228.4104 | 221.6732 | 226.0532
659.9885 | 229.0859 | 221.6677 | 226.2732
660.9885 | 229.3713 | 221.9061 | 226.501
661.9885 | 229.3613 | 222.321 | 226.1183
662.9885 | 229.6603 | 222.78 | 226.4316
663.9885 | 229.8241 | 223.018 | 226.5836
664.9885 | 229.8794 | 223.171 | 226.5129
665.9885 | 229.8306 | 223.4625 | 226.7217
666.9885 | 229.748 | 223.592 | 226.6593
667.9885 | 229.6512 | 223.526 | 226.7431
668.9885 | 230.0967 | 223.5185 | 226.2948
669.9885 | 230.2984 | 223.3941 | 226.2475
670.9885 | 230.6719 | 223.4268 | 226.7693
671.9885 | 230.7978 | 223.3644 | 226.7301
672.9885 | 230.4116 | 223.1165 | 226.5485
673.9885 | 230.2244 | 223.1124 | 226.9417
674.9885 | 230.19 | 221.9615 | 227.1837
675.9885 | 230.1809 | 222.0261 | 227.1838
676.9885 | 230.2506 | 221.7453 | 227.0541
677.9885 | 230.1961 | 221.5403 | 227.1034
678.9885 | 230.5205 | 221.551 | 227.26
679.9885 | 230.3253 | 221.8271 | 227.1111
680.9885 | 230.0371 | 221.669 | 227.3209
681.9885 | 229.7835 | 221.7656 | 227.5073
682.9885 | 229.2761 | 222.1552 | 227.8154
683.9885 | 228.6876 | 222.1746 | 227.6304
684.9885 | 228.9066 | 222.3662 | 227.3563
685.9885 | 228.9806 | 222.5574 | 227.2435
686.9885 | 228.9623 | 223.0789 | 227.0818
687.9885 | 228.9018 | 223.3178 | 227.2052
688.9885 | 229.5927 | 223.6892 | 228.3564
689.9885 | 229.6197 | 223.9155 | 228.8243
690.9885 | 229.7525 | 224.2716 | 229.4921
691.9885 | 229.2865 | 224.3369 | 229.3191
692.9885 | 229.1994 | 224.3276 | 229.596
693.9885 | 229.2723 | 224.595 | 229.623
694.9885 | 229.4372 | 224.5399 | 229.9651
695.9885 | 229.6697 | 224.8337 | 230.1816
696.9885 | 229.7105 | 224.3989 | 231.1813
697.9885 | 229.5008 | 224.2703 | 230.8678
698.9885 | 229.5346 | 224.4655 | 230.8058
699.9885 | 229.8563 | 225.0633 | 230.7563
700.9885 | 230.285 | 225.3286 | 230.7431
701.9885 | 230.8059 | 226.1485 | 230.9666
702.9885 | 231.0951 | 225.8279 | 230.7959
703.9885 | 231.8463 | 225.9346 | 230.9365
704.9885 | 231.8394 | 225.8851 | 230.6411
705.9885 | 231.9463 | 226.194 | 230.4658
706.9885 | 232.367 | 226.6236 | 231.125
707.9885 | 232.5681 | 226.0349 | 231.2686
708.9885 | 232.457 | 226.0713 | 231.6715
709.9885 | 232.4586 | 226.0883 | 231.7422
710.9885 | 232.7403 | 226.3319 | 231.7612
711.9885 | 232.165 | 225.9658 | 231.2003
712.9885 | 232.3528 | 226.039 | 230.8909
713.9885 | 232.4806 | 226.1814 | 230.3437
714.9885 | 232.5335 | 226.5805 | 230.2966
715.9885 | 232.3481 | 226.5374 | 230.6537
716.9885 | 232.0601 | 226.4008 | 230.5099
717.9885 | 232.1945 | 227.0988 | 230.2194
718.9885 | 232.1521 | 227.1521 | 230.3963
719.9885 | 232.1064 | 227.5952 | 230.4312
720.9885 | 231.9299 | 227.4532 | 230.1313
721.9885 | 231.9202 | 227.3328 | 230.1157
722.9885 | 230.9992 | 227.4493 | 229.891
723.9885 | 230.8533 | 227.3091 | 229.9828
724.9885 | 230.6521 | 227.7819 | 230.4375
725.9885 | 230.6897 | 228.35 | 230.5451
726.9885 | 230.9994 | 228.7328 | 230.3344
727.9885 | 231.0534 | 228.6596 | 230.0004
728.9885 | 230.7622 | 229.1932 | 230.1787
729.9885 | 230.785 | 230.3706 | 230.2394
730.9885 | 230.8599 | 230.5207 | 230.1386
731.9885 | 230.9974 | 230.6365 | 230.5115
732.9885 | 231.177 | 230.7568 | 230.5664
733.9885 | 231.4191 | 231.4881 | 230.556
734.9885 | 231.1884 | 231.3637 | 230.3005
735.9885 | 230.9179 | 231.1906 | 230.2813
736.9885 | 230.7876 | 231.3225 | 230.3626
737.9885 | 230.2741 | 231.3026 | 230.4411
738.9885 | 230.1531 | 231.2305 | 230.4931
739.9885 | 230.0438 | 231.2846 | 230.3519
740.9885 | 230.5661 | 231.2641 | 230.2637
741.9885 | 230.8755 | 231.2849 | 230.2789
742.9885 | 231.228 | 231.2604 | 230.0706
743.9885 | 231.3347 | 231.1615 | 229.8151
744.9885 | 231.5807 | 231.465 | 230.0076
745.9885 | 231.4758 | 231.3772 | 230.1563
746.9885 | 231.5194 | 230.8892 | 230.1652
747.9885 | 231.3999 | 231.0922 | 230.2942
748.9885 | 231.5995 | 231.2015 | 230.3603
749.9885 | 232.0366 | 231.5027 | 230.3461
750.9885 | 232.2126 | 231.6669 | 230.5592
751.9885 | 232.2495 | 231.9462 | 230.7692
752.9885 | 232.6795 | 232.2574 | 230.5926
753.9885 | 232.7947 | 232.2772 | 230.8695
754.9885 | 233.6264 | 232.4631 | 230.8236
755.9885 | 233.931 | 232.5982 | 231.039
756.9885 | 234.8345 | 232.8058 | 231.348
757.9885 | 235.5758 | 233.3959 | 232.1655
758.9885 | 236.454 | 233.4407 | 232.1402
759.9885 | 236.6969 | 233.6004 | 232.8484
760.9885 | 237.6018 | 234.4046 | 233.5884
761.9885 | 237.4648 | 234.0812 | 233.8523
762.9885 | 237.8347 | 234.7506 | 234.4264
763.9885 | 238.2382 | 234.8596 | 234.7191
764.9885 | 238.4027 | 235.3223 | 234.8058
765.9885 | 238.8516 | 235.5229 | 235.5989
766.9885 | 239.2863 | 235.1707 | 235.4673
767.9885 | 239.2733 | 234.9722 | 235.5843
768.9885 | 239.4958 | 235.779 | 235.2738
769.9885 | 239.4277 | 235.942 | 235.4737
770.9885 | 239.3615 | 235.9405 | 235.2952
771.9885 | 239.6947 | 235.5672 | 235.013
772.9885 | 240.1072 | 235.5438 | 235.2551
773.9885 | 240.6776 | 235.5278 | 235.05
774.9885 | 241.3661 | 236.8642 | 235.3661
775.9885 | 241.872 | 237.1998 | 235.7393
776.9885 | 241.7418 | 237.2922 | 235.8011
777.9885 | 241.8894 | 236.5375 | 236.2585
778.9885 | 242.4931 | 237.3129 | 236.269
779.9885 | 242.9368 | 237.4092 | 236.5015
780.9885 | 243.1253 | 237.5311 | 236.9974
781.9885 | 243.0147 | 239.7122 | 237.1988
782.9885 | 243.306 | 239.1335 | 237.3831
783.9885 | 243.5892 | 239.2111 | 237.877
784.9885 | 244.0538 | 239.5088 | 237.5782
785.9885 | 244.5623 | 239.3677 | 237.5334
786.9885 | 245.097 | 239.9072 | 237.9926
787.9885 | 245.7134 | 239.87 | 238.1183
788.9885 | 246.1784 | 239.9395 | 238.4675
789.9885 | 246.7185 | 239.5843 | 239.1206
790.9885 | 247.2177 | 240.1881 | 238.6307
791.9885 | 247.4451 | 241.0537 | 238.8713
792.9885 | 247.5557 | 241.336 | 239.0283
793.9885 | 247.7697 | 241.4314 | 239.2116
794.9885 | 247.8486 | 242.0639 | 239.5897
795.9885 | 248.3184 | 242.0884 | 239.8232
796.9885 | 248.1546 | 241.8524 | 239.8381
797.9885 | 248.4079 | 241.8175 | 239.8537
798.9885 | 248.4597 | 241.8812 | 239.4237
799.9885 | 248.5241 | 242.0222 | 239.4558
800.9885 | 248.5437 | 243.1022 | 239.7
801.9885 | 249.1236 | 243.2129 | 239.7435
802.9885 | 249.4569 | 242.2425 | 239.9612
803.9885 | 249.3181 | 241.682 | 240.1153
804.9885 | 249.2828 | 241.5393 | 240.3336
805.9885 | 249.3068 | 241.4365 | 240.6135
806.9885 | 249.3022 | 241.4629 | 240.9115
807.9885 | 249.5536 | 241.6784 | 241.3386
808.9885 | 249.5055 | 241.3503 | 241.1386
809.9885 | 249.5291 | 241.1998 | 240.7601
810.9885 | 249.7181 | 241.6967 | 240.8951
811.9885 | 250.2743 | 241.2334 | 241.6612
812.9885 | 250.2277 | 241.3163 | 241.762
813.9885 | 250.5526 | 242.0613 | 241.3888
814.9885 | 250.5414 | 242.3555 | 241.2056
815.9885 | 250.8468 | 242.9562 | 241.3583
816.9885 | 251.3583 | 242.523 | 241.7163
817.9885 | 251.9235 | 242.4884 | 241.6346
818.9885 | 252.3002 | 242.173 | 241.5763
819.9885 | 252.3087 | 242.3376 | 241.3417
820.9885 | 252.4571 | 242.9504 | 241.4446
821.9885 | 252.5775 | 243.2717 | 241.4618
822.9885 | 252.9191 | 243.4966 | 241.4852
823.9885 | 252.9292 | 243.2279 | 241.2295
824.9885 | 253.124 | 243.3729 | 241.2205
825.9885 | 253.3165 | 243.7517 | 241.094
826.9885 | 253.7726 | 244.0186 | 241.2836
827.9885 | 253.8506 | 244.4077 | 241.9553
828.9885 | 254.0028 | 243.9198 | 242.2406
829.9885 | 254.2374 | 243.9374 | 242.5954
830.9885 | 254.4614 | 244.1493 | 242.496
831.9885 | 254.5117 | 244.1527 | 243.054
832.9885 | 254.2247 | 245.1706 | 243.8242
833.9885 | 254.5876 | 246.0943 | 244.1761
834.9885 | 254.3814 | 245.8871 | 244.9829
835.9885 | 254.3986 | 245.8391 | 245.6085
836.9885 | 254.8573 | 246.0488 | 246.3986
837.9885 | 255.0814 | 245.9465 | 246.4361
838.9885 | 256.0631 | 247.8769 | 246.239
839.9885 | 256.0447 | 247.39 | 245.6311
840.9885 | 256.0869 | 247.6568 | 245.5393
841.9885 | 256.4543 | 247.992 | 245.6065
842.9885 | 256.4523 | 248.8851 | 245.8771
843.9885 | 256.7766 | 249.4522 | 245.5837
844.9885 | 256.5519 | 249.7655 | 245.545
845.9885 | 256.8917 | 250.6929 | 245.7879
846.9885 | 257.4919 | 250.9513 | 245.5183
847.9885 | 257.4174 | 251.3855 | 245.9993
848.9885 | 257.4488 | 251.9899 | 246.0085
849.9885 | 257.7506 | 252.2547 | 246.2305
850.9885 | 258.3619 | 252.1607 | 246.7768
851.9885 | 258.3369 | 252.8501 | 246.7183
852.9885 | 258.3356 | 253.7092 | 246.4706
853.9885 | 259.0794 | 253.7896 | 246.6302
854.9885 | 259.7815 | 254.6125 | 247.1106
855.9885 | 259.779 | 254.4766 | 246.5126
856.9885 | 260.5165 | 254.4465 | 246.5357
857.9885 | 259.9563 | 254.8234 | 246.8936
858.9885 | 259.7823 | 254.8141 | 246.4975
859.9885 | 258.932 | 254.6399 | 246.1203
860.9885 | 258.7405 | 255.0529 | 246.3194
861.9885 | 259.0535 | 254.1312 | 246.6784
862.9885 | 259.0333 | 253.923 | 246.6714
863.9885 | 259.1672 | 253.7498 | 246.2758
864.9885 | 259.7522 | 254.3596 | 245.9383
865.9885 | 260.5176 | 254.8913 | 245.4022
866.9885 | 261.115 | 255.4918 | 245.8411
867.9885 | 261.4026 | 256.0866 | 246.8368
868.9885 | 262.1649 | 256.6484 | 247.2054
869.9885 | 261.873 | 257.3198 | 247.485
870.9885 | 262.1176 | 258.2901 | 248.0796
871.9885 | 262.3044 | 259.1654 | 248.5024
872.9885 | 262.4627 | 259.6238 | 249.1037
873.9885 | 261.8949 | 260.3046 | 249.7749
874.9885 | 262.044 | 260.5154 | 249.861
875.9885 | 262.4084 | 260.4846 | 250.0897
876.9885 | 262.8412 | 260.4304 | 250.5422
877.9885 | 262.7211 | 260.569 | 250.2712
878.9885 | 262.8427 | 260.8366 | 250.3592
879.9885 | 263.6896 | 261.6686 | 250.8405
880.9885 | 264.4407 | 262.0042 | 251.1487
881.9885 | 264.8456 | 262.3477 | 251.7174
882.9885 | 265.2875 | 263.2243 | 252.7118
883.9885 | 266.1889 | 262.9129 | 252.9151
884.9885 | 266.6713 | 262.7568 | 252.5722
885.9885 | 266.9086 | 263.6003 | 253.2956
886.9885 | 266.9891 | 263.4431 | 253.5269
887.9885 | 267.2024 | 263.3531 | 253.5513
888.9885 | 267.5061 | 265.2788 | 254.0544
889.9885 | 267.8668 | 265.2898 | 254.1383
890.9885 | 268.1488 | 266.2518 | 254.2025
891.9885 | 267.9096 | 265.5922 | 254.922
892.9885 | 268.0433 | 264.9344 | 255.395
893.9885 | 267.8392 | 264.5545 | 255.7472
894.9885 | 268.0204 | 265.0415 | 256.6203
895.9885 | 267.9803 | 265.3776 | 256.7079
896.9885 | 268.313 | 265.6492 | 256.5863
897.9885 | 268.6495 | 265.9467 | 256.7466
898.9885 | 269.2096 | 266.3216 | 256.8268
899.9885 | 269.6578 | 266.1325 | 257.3498
900.9885 | 270.0142 | 266.1201 | 257.9537
901.9885 | 270.3064 | 266.1054 | 257.6192
902.9885 | 270.705 | 265.8177 | 257.7677
903.9885 | 270.5775 | 266.3346 | 257.3737
904.9885 | 271.1846 | 267.2666 | 257.1368
905.9885 | 271.3884 | 267.639 | 257.3235
906.9885 | 272.2594 | 268.8696 | 257.4852
908.0042 | 272.6304 | 269.896 | 257.6816
908.9885 | 273.0356 | 269.8522 | 257.5777
909.9885 | 273.0323 | 270.4258 | 257.4012
910.9885 | 273.1203 | 269.9694 | 257.5798
911.9885 | 273.474 | 269.8004 | 257.4866
912.9885 | 273.758 | 269.4349 | 257.3152
913.9885 | 274.5847 | 269.2093 | 257.7348
914.9885 | 275.2991 | 269.3658 | 258.4328
915.9885 | 275.0998 | 270.1813 | 258.3884
916.9885 | 275.1515 | 270.5616 | 258.4695
917.9885 | 275.6711 | 271.3306 | 259.0959
918.9885 | 276.1107 | 272.2775 | 259.418
919.9885 | 276.7661 | 272.4169 | 259.2007
920.9885 | 276.8942 | 272.3489 | 259.9633
921.9885 | 276.477 | 272.0422 | 260.2614
922.9885 | 276.525 | 271.8893 | 260.5864
923.9885 | 276.6987 | 271.8773 | 260.9141
924.9885 | 277.3983 | 272.2905 | 261.4452
925.9885 | 276.893 | 272.4534 | 261.5809
926.9885 | 276.9925 | 272.5117 | 260.5419
927.9885 | 276.7351 | 273.342 | 260.4559
928.9885 | 277.5641 | 273.3024 | 260.984
929.9885 | 277.7622 | 272.414 | 261.3566
930.9885 | 278.254 | 272.0014 | 261.5144
931.9885 | 278.2351 | 272.3119 | 262.0199
932.9885 | 278.3767 | 272.791 | 262.1309
933.9885 | 278.3711 | 273.2682 | 262.5192
934.9885 | 278.5077 | 273.3844 | 262.3238
935.9885 | 278.6639 | 273.4096 | 262.5707
936.9885 | 279.1119 | 273.4868 | 262.9047
937.9885 | 278.9444 | 273.3326 | 263.121
938.9885 | 279.2407 | 273.3779 | 263.6297
939.9885 | 279.4147 | 273.9757 | 264.1922
940.9885 | 279.6822 | 273.9711 | 264.2794
941.9885 | 279.703 | 274.0646 | 264.6123
942.9885 | 280.1892 | 274.4066 | 265.1746
943.9885 | 280.1544 | 274.8707 | 266.0759
944.9885 | 280.1165 | 276.0015 | 266.4751
945.9885 | 280.635 | 277.1161 | 266.0846
946.9885 | 280.8473 | 277.1637 | 265.9661
947.9885 | 281.0499 | 277.3785 | 266.0164
948.9885 | 281.9756 | 278.4337 | 266.7734
949.9885 | 282.4179 | 278.0712 | 267.4561
950.9885 | 283.2042 | 277.8993 | 267.1535
951.9885 | 283.5548 | 278.272 | 267.249
952.9885 | 283.8456 | 278.2914 | 267.6261
953.9885 | 284.0321 | 278.4134 | 268.0011
954.9885 | 284.1004 | 279.3427 | 268.2525
955.9885 | 283.9617 | 279.5816 | 268.8624
956.9885 | 283.698 | 279.5837 | 268.7378
957.9885 | 283.826 | 279.4758 | 268.6955
958.9885 | 284.1251 | 278.8071 | 268.7816
959.9885 | 284.5517 | 278.51 | 268.1447
960.9885 | 284.617 | 278.3012 | 268.3118
961.9885 | 284.5798 | 278.3628 | 267.761
962.9885 | 285.2245 | 278.5226 | 267.2957
963.9885 | 285.7179 | 278.6629 | 267.1979
964.9885 | 286.0068 | 279.2444 | 267.91
965.9885 | 285.5947 | 280.0895 | 268.7249
966.9885 | 285.7936 | 280.9195 | 269.3877
967.9885 | 285.2045 | 281.6007 | 269.7478
968.9885 | 284.7931 | 281.6652 | 270.185
969.9885 | 284.4179 | 281.5807 | 270.6857
970.9885 | 284.5638 | 281.6941 | 271.3632
971.9885 | 284.7197 | 282.0474 | 271.7678
972.9885 | 285.097 | 282.9282 | 272.4244
973.9885 | 285.3134 | 283.6837 | 273.2535
974.9885 | 285.8961 | 283.8954 | 273.4003
975.9885 | 285.7453 | 284.3219 | 273.8333
976.9885 | 285.9001 | 285.0561 | 273.697
977.9885 | 286.1239 | 285.2916 | 273.6291
978.9885 | 286.2447 | 285.7391 | 274.0162
979.9885 | 286.3815 | 286.0777 | 274.6294
980.9885 | 286.0999 | 286.0576 | 275.3558
981.9885 | 286.2921 | 286.4041 | 275.5983
982.9885 | 286.2455 | 286.826 | 275.8246
983.9885 | 286.3959 | 287.1717 | 276.1667
984.9885 | 286.7087 | 287.0917 | 276.0739
985.9885 | 286.7398 | 287.1662 | 276.1705
986.9885 | 286.8835 | 287.3093 | 276.2929
987.9885 | 287.118 | 288.7487 | 276.4697
988.9885 | 287.4323 | 288.8987 | 276.2768
989.9885 | 287.7722 | 289.1316 | 276.3593
990.9885 | 288.1861 | 288.9231 | 276.9596
991.9885 | 288.9998 | 289.382 | 277.7431
992.9885 | 289.6424 | 289.8312 | 278.3511
993.9885 | 290.0268 | 290.0247 | 278.6768
994.9885 | 290.8817 | 290.0641 | 278.7379
995.9885 | 291.5665 | 289.9529 | 278.6864
996.9885 | 291.4498 | 289.8159 | 277.7891
997.9885 | 291.546 | 289.9238 | 277.5233
998.9885 | 292.4735 | 289.9092 | 277.4534
999.9885 | 293.1993 | 289.7339 | 277.1153
1000.9885 | 293.2016 | 290.08 | 277.6893
1001.9885 | 293.7534 | 290.85 | 277.9985
1002.9885 | 293.9897 | 291.2263 | 277.9578
1003.9885 | 294.6925 | 291.2761 | 278.3278
1004.9885 | 295.0445 | 291.9278 | 278.5694
1005.9885 | 295.1338 | 292.6386 | 278.6124
1006.9885 | 295.15 | 292.8655 | 278.851
1007.9885 | 295.312 | 293.4034 | 279.145
1008.9885 | 295.4349 | 292.5652 | 279.6649
1009.9885 | 295.3963 | 292.423 | 279.4655
1010.9885 | 295.3581 | 292.4189 | 280.3056
1011.9885 | 296.1456 | 292.7028 | 280.3233
1012.9885 | 295.4867 | 293.0017 | 280.3918
1013.9885 | 295.5918 | 292.7473 | 280.6349
1014.9885 | 295.9506 | 292.8402 | 280.495
1015.9885 | 296.0392 | 292.1594 | 280.9827
1016.9885 | 296.2231 | 291.2556 | 281.4898
1017.9885 | 295.956 | 291.8791 | 281.5895
1018.9885 | 296.301 | 292.2214 | 282.0082
1019.9885 | 296.4192 | 292.4478 | 281.6691
1020.9885 | 296.6284 | 292.632 | 281.7401
1021.9885 | 297.2281 | 292.6649 | 281.6336
1022.9885 | 296.9019 | 292.2084 | 281.6725
1023.9885 | 297.5563 | 291.8958 | 281.2201
1024.9885 | 297.7477 | 292.4059 | 281.273
1025.9885 | 298.1991 | 293.58 | 281.9817
1026.9885 | 298.5076 | 293.2704 | 281.3116
1027.9885 | 298.5027 | 292.6673 | 280.8079
1028.9885 | 298.8872 | 292.0559 | 280.4264
1029.9885 | 299.0928 | 292.1515 | 279.581
1030.9885 | 299.2123 | 292.0156 | 278.9466
1031.9885 | 299.4176 | 291.1576 | 278.7448
1032.9885 | 299.3111 | 290.5387 | 278.7249
1033.9885 | 299.3886 | 291.4812 | 279.3615
1034.9885 | 299.7528 | 291.8633 | 278.9855
1035.9885 | 299.7769 | 292.8157 | 279.2734
1036.9885 | 299.573 | 293.6334 | 280.0276
1037.9885 | 299.6932 | 294.4923 | 280.2222
1038.9885 | 299.5832 | 294.4641 | 280.3269
1039.9885 | 299.5125 | 294.4293 | 280.7795
1040.9885 | 299.1385 | 294.2224 | 280.953
1041.9885 | 299.2957 | 293.9516 | 281.1168
1042.9885 | 299.6971 | 293.551 | 281.1047
1043.9885 | 299.9909 | 293.9078 | 280.7665
1044.9885 | 299.5181 | 294.1877 | 281.0077
1045.9885 | 299.6211 | 294.2415 | 280.7299
1046.9885 | 299.8959 | 294.1696 | 280.8957
1047.9885 | 299.5695 | 294.1188 | 281.1907
1048.9885 | 299.5372 | 294.0163 | 281.3525
1049.9885 | 299.8205 | 294.2249 | 281.539
1050.9885 | 300.2846 | 294.7863 | 282.0877
1051.9885 | 300.7452 | 294.925 | 282.1131
1052.9885 | 301.6037 | 294.685 | 282.0912
1053.9885 | 301.9114 | 295.5623 | 282.8058
1054.9885 | 302.0296 | 295.9571 | 283.4684
1055.9885 | 302.1442 | 295.6693 | 283.7189
1056.9885 | 302.1578 | 295.727 | 283.6731
1057.9885 | 302.0764 | 295.8283 | 283.8232
1058.9885 | 302.7679 | 295.9774 | 284.0695
1059.9885 | 303.2003 | 296.0232 | 283.4656
1060.9885 | 303.3368 | 296.1688 | 283.7546
1061.9885 | 303.433 | 295.5568 | 283.0176
1062.9885 | 303.9782 | 295.9679 | 282.8987
1063.9885 | 304.6724 | 296.7589 | 282.8351
1064.9885 | 305.2309 | 297.7583 | 282.5196
1065.9885 | 305.5594 | 298.2227 | 283.0139
1066.9885 | 306.0455 | 298.4297 | 284.2155
1067.9885 | 306.3413 | 299.0996 | 284.4883
1068.9885 | 305.8449 | 299.3386 | 284.8805
1069.9885 | 305.7845 | 299.2661 | 285.2473
1070.9885 | 305.7098 | 299.4933 | 285.2527
1071.9885 | 306.1641 | 299.7488 | 285.3449
1072.9885 | 306.1055 | 299.9178 | 285.346
1073.9885 | 306.1828 | 300.0682 | 285.4361
1074.9885 | 306.2236 | 299.946 | 285.0307
1075.9885 | 306.5042 | 299.8865 | 284.3722
1076.9885 | 306.481 | 299.8133 | 284.1665
1077.9885 | 306.4813 | 299.8439 | 284.8597
1078.9885 | 306.2503 | 299.2774 | 284.7772
1079.9885 | 306.1303 | 300.0847 | 285.3527
1080.9885 | 306.1261 | 300.2126 | 285.9257
1081.9885 | 306.3518 | 300.8882 | 286.2237
1082.9885 | 306.5194 | 301.1294 | 286.3571
1083.9885 | 307.1499 | 300.8404 | 285.8125
1084.9885 | 307.1008 | 300.9057 | 286.1144
1085.9885 | 307.4013 | 301.6479 | 286.0514
1086.9885 | 307.4175 | 301.873 | 286.1599
1087.9885 | 307.6198 | 301.647 | 285.9157
1088.9885 | 307.9226 | 302.5334 | 285.9599
1089.9885 | 308.3613 | 302.8744 | 285.4469
1090.9885 | 308.8322 | 303.2777 | 286.5067
1091.9885 | 308.8216 | 303.6709 | 286.4773
1092.9885 | 308.9016 | 302.9376 | 286.6508
1093.9885 | 308.7331 | 302.7516 | 286.9474
1094.9885 | 309.0815 | 303.0337 | 287.0462
1095.9885 | 309.4516 | 303.1967 | 288.5363
1096.9885 | 309.3462 | 303.0328 | 288.494
1097.9885 | 309.4533 | 303.1527 | 288.7262
1098.9885 | 309.3071 | 303.1195 | 288.6945
1099.9885 | 309.4592 | 303.2356 | 289.0562
1100.9885 | 309.8028 | 303.1579 | 289.0083
1101.9885 | 309.6362 | 303.2739 | 288.4772
1102.9885 | 309.6339 | 303.229 | 288.8263
1103.9885 | 309.6797 | 303.118 | 288.6637
1104.9885 | 309.526 | 303.4647 | 288.8454
1105.9885 | 308.9744 | 303.3864 | 288.9037
1106.9885 | 308.8509 | 303.5681 | 289.0911
1107.9885 | 308.8183 | 303.3671 | 288.5477
1108.9885 | 308.9524 | 303.1233 | 288.4097
1109.9885 | 309.0114 | 303.9636 | 288.624
1110.9885 | 308.5869 | 303.8342 | 288.2658
1111.9885 | 308.7178 | 303.4364 | 288.2334
1112.9885 | 309.4301 | 303.3849 | 288.122
1113.9885 | 310.1703 | 302.8296 | 288.6212
1114.9885 | 310.6113 | 302.6679 | 288.7792
1115.9885 | 310.7409 | 302.4324 | 288.5552
1116.9885 | 310.8186 | 302.4952 | 288.9454
1117.9885 | 310.4696 | 302.516 | 289.0688
1118.9885 | 310.0483 | 302.6608 | 290.8459
1119.9885 | 310.3025 | 303.0618 | 290.7876
1120.9885 | 310.8275 | 303.8989 | 291.4557
1121.9885 | 310.5161 | 304.0814 | 291.3992
1122.9885 | 310.4151 | 303.8607 | 291.7793
1123.9885 | 310.5108 | 303.7714 | 291.9734
1124.9885 | 310.9009 | 303.633 | 291.8249
1125.9885 | 310.834 | 303.4528 | 291.2975
1126.9885 | 310.7205 | 302.9983 | 291.0359
1127.9885 | 310.9925 | 303.0483 | 291.4007
1128.9885 | 310.8387 | 303.2078 | 291.6101
1129.9885 | 311.2628 | 303.295 | 291.5077
1130.9885 | 311.1354 | 303.7953 | 291.3957
1131.9885 | 310.9414 | 303.7325 | 291.3052
1132.9885 | 310.4539 | 303.6723 | 291.0685
1133.9885 | 310.7235 | 304.1046 | 291.2184
1134.9885 | 310.5988 | 303.9946 | 291.3123
1135.9885 | 310.5102 | 304.0251 | 291.1427
1136.9885 | 310.5589 | 304.2689 | 291.0648
1137.9885 | 310.4641 | 303.6336 | 291.0628
1138.9885 | 310.748 | 303.6229 | 290.7191
1139.9885 | 310.8573 | 303.6522 | 291.3166
1140.9885 | 310.6381 | 303.1288 | 291.5936
1141.9885 | 310.6526 | 303.0073 | 291.6495
1142.9885 | 310.9421 | 303.7461 | 292.0661
1143.9885 | 311.4024 | 303.0873 | 292.9625
1144.9885 | 310.8992 | 303.3224 | 292.7752
1145.9885 | 310.8311 | 303.5413 | 292.5492
1146.9885 | 310.5719 | 303.662 | 292.427
1147.9885 | 310.2482 | 303.821 | 292.1085
1148.9885 | 310.3503 | 303.9111 | 292.0248
1149.9885 | 310.1498 | 303.6314 | 291.4219
1150.9885 | 310.1235 | 304.2814 | 291.0568
1151.9885 | 310.1272 | 304.5564 | 291.19
1152.9885 | 310.2478 | 304.6278 | 291.03
1153.9885 | 310.6066 | 304.8131 | 292.025
1154.9885 | 310.975 | 305.5566 | 291.5469
1155.9885 | 310.8652 | 305.7148 | 291.5617
1156.9885 | 310.9992 | 305.2641 | 292.0232
1157.9885 | 310.8411 | 304.4964 | 292.0424
1158.9885 | 311.3453 | 303.712 | 291.729
1159.9885 | 311.4246 | 303.7577 | 291.6618
1160.9885 | 311.4111 | 304.0106 | 291.0928
1161.9885 | 311.1653 | 304.541 | 290.8875
1162.9885 | 310.8115 | 304.3662 | 291.1101
1163.9885 | 310.5948 | 304.513 | 291.6106
1164.9885 | 311.0489 | 304.3557 | 291.0816
1165.9885 | 311.3799 | 303.9376 | 291.0792
1166.9885 | 311.2101 | 303.8607 | 291.0871
1167.9885 | 311.1692 | 304.1142 | 290.9613
1168.9885 | 311.9806 | 303.196 | 292
1169.9885 | 312.0064 | 303.1477 | 291.7529
1170.9885 | 312.0713 | 303.3395 | 292.6001
1171.9885 | 312.1897 | 303.7696 | 293.2277
1172.9885 | 312.1562 | 304.8218 | 292.6495
1173.9885 | 312.0461 | 305.1871 | 292.2141
1174.9885 | 312.2649 | 305.2901 | 292.1145
1175.9885 | 312.1634 | 304.8483 | 292.1178
1176.9885 | 311.9976 | 304.7527 | 292.0822
1177.9885 | 312.281 | 305.0132 | 291.8622
1178.9885 | 312.1022 | 305.2132 | 291.9515
1179.9885 | 313.01 | 305.5868 | 291.8179
1180.9885 | 312.8935 | 305.6879 | 292.1693
1181.9885 | 312.7281 | 305.4738 | 292.412
1182.9885 | 312.4813 | 305.3404 | 292.35
1183.9885 | 312.3319 | 305.0704 | 292.3669
1184.9885 | 312.1825 | 305.3639 | 292.3663
1185.9885 | 312.1598 | 305.6394 | 292.1764
1186.9885 | 312.1155 | 305.8307 | 292.8452
1187.9885 | 312.4905 | 305.7501 | 293.1058
1188.9885 | 312.5309 | 305.7787 | 292.7113
1189.9885 | 312.6146 | 305.9279 | 292.5829
1190.9885 | 312.7478 | 305.8802 | 292.6
1191.9885 | 312.6672 | 305.9542 | 292.8258
1192.9885 | 312.7673 | 306.0012 | 292.7255
1193.9885 | 312.94 | 306.1705 | 293.1946
1194.9885 | 312.7854 | 305.7925 | 292.7605
1195.9885 | 312.9367 | 305.9772 | 292.7481
1196.9885 | 313.1158 | 305.8964 | 292.626
1197.9885 | 313.4948 | 305.7605 | 292.2288
1198.9885 | 313.2197 | 305.8083 | 292.0314
1199.9885 | 313.4935 | 306.133 | 292.0208
1200.9885 | 313.0503 | 305.9063 | 291.771
1201.9885 | 312.9582 | 305.5856 | 291.7839
1202.9885 | 312.7441 | 305.6106 | 292.3767
1203.9885 | 312.7398 | 306.2841 | 292.7797
1204.9885 | 313.5679 | 306.3147 | 293.1775
1205.9885 | 313.2757 | 306.4251 | 292.9578
1206.9885 | 313.2679 | 306.3769 | 292.9257
1207.9885 | 313.2394 | 306.8846 | 292.9946
1208.9885 | 312.8245 | 307.2701 | 292.6297
1209.9885 | 312.6595 | 307.5404 | 292.2263
1210.9885 | 312.8613 | 307.7707 | 292.6957
1211.9885 | 313.1814 | 308.1385 | 292.8783
1212.9885 | 312.6674 | 307.7778 | 292.7497
1213.9885 | 312.6158 | 307.2818 | 292.7706
1214.9885 | 312.8852 | 306.9262 | 293.0862
1215.9885 | 312.7761 | 307.0651 | 293.1136
1216.9885 | 312.963 | 307.8311 | 293.6971
1217.9885 | 312.7846 | 307.7923 | 293.7184
1218.9885 | 312.9657 | 307.854 | 294.0659
1219.9885 | 312.8814 | 308.057 | 294.0767
1220.9885 | 313.0712 | 308.4944 | 294.2838
1221.9885 | 313.5438 | 308.6056 | 294.2069
1222.9885 | 313.6662 | 309.2372 | 293.7524
1223.9885 | 313.9089 | 308.8651 | 294.05
1224.9885 | 313.7878 | 308.4805 | 293.9378
1225.9885 | 313.3978 | 307.7981 | 293.6241
1226.9885 | 313.4094 | 307.2344 | 293.3215
1227.9885 | 313.1978 | 306.578 | 293.3426
1228.9885 | 313.0132 | 306.6686 | 293.3586
1229.9885 | 313.1395 | 306.61 | 293.8506
1230.9885 | 312.7931 | 306.449 | 293.7223
1231.9885 | 312.7833 | 306.5496 | 293.4262
1232.9885 | 312.7481 | 307.2487 | 293.4615
1233.9885 | 312.6662 | 307.2211 | 293.4031
1234.9885 | 312.8746 | 307.8655 | 293.8078
1235.9885 | 313.2553 | 307.3267 | 293.3495
1236.9885 | 313.295 | 306.7585 | 292.9567
1237.9885 | 313.348 | 306.4489 | 292.477
1238.9885 | 313.3967 | 306.5243 | 292.2323
1239.9885 | 313.7084 | 306.0294 | 292.0756
1240.9885 | 313.8157 | 306.1652 | 292.3855
1241.9885 | 313.5537 | 306.155 | 292.1919
1242.9885 | 313.6504 | 306.3859 | 292.5222
1243.9885 | 314.2451 | 306.721 | 292.651
1244.9885 | 314.094 | 307.0569 | 293.148
1245.9885 | 314.9073 | 307.1749 | 293.3291
1246.9885 | 314.9009 | 307.3796 | 293.7185
1247.9885 | 315.2457 | 307.8116 | 294.3011
1248.9885 | 315.595 | 307.6969 | 294.0429
1249.9885 | 315.4027 | 308.4377 | 294.4239
1250.9885 | 315.8427 | 308.362 | 294.5469
1251.9885 | 315.4396 | 308.3606 | 294.3413
1252.9885 | 315.2695 | 308.5555 | 294.2043
1253.9885 | 315.3365 | 308.2408 | 294.3427
1254.9885 | 315.0263 | 308.3135 | 294.342
1255.9885 | 315.1114 | 308.3969 | 294.2821
1256.9885 | 315.2645 | 308.4847 | 294.8494
1257.9885 | 315.472 | 308.6675 | 295.3202
1258.9885 | 315.7104 | 308.7943 | 295.7388
1259.9885 | 315.8627 | 308.728 | 295.9599
1260.9885 | 316.2614 | 309.3477 | 296.2512
1261.9885 | 316.4363 | 309.2735 | 296.0799
1262.9885 | 316.1491 | 308.7172 | 296.07
1263.9885 | 316.3525 | 308.3022 | 295.774
1264.9885 | 316.1276 | 307.856 | 295.7746
1265.9885 | 315.6166 | 307.4941 | 295.8472
1266.9885 | 315.6249 | 307.0404 | 295.8589
1267.9885 | 315.3985 | 306.7793 | 295.5642
1268.9885 | 314.9464 | 306.8246 | 295.9126
1269.9885 | 314.4552 | 306.5705 | 295.9358
1270.9885 | 314.7224 | 306.5432 | 295.9124
1271.9885 | 314.7557 | 307.0547 | 295.563
1272.9885 | 314.6279 | 307.2849 | 295.9104
1273.9885 | 315.3637 | 307.3345 | 295.7561
1274.9885 | 315.2835 | 307.5062 | 295.9777
1275.9885 | 315.4041 | 307.3273 | 296.0326
1276.9885 | 315.616 | 307.0969 | 296.1589
1277.9885 | 315.4035 | 306.8793 | 296.2665
1278.9885 | 315.8226 | 307.2803 | 296.4535
1279.9885 | 315.546 | 307.2391 | 296.6391
1280.9885 | 315.4809 | 307.3297 | 296.6858
1281.9885 | 315.1173 | 307.5616 | 296.9162
1282.9885 | 315.0185 | 307.7575 | 296.2963
1283.9885 | 315.0623 | 307.939 | 296.3352
1284.9885 | 315.5463 | 307.4959 | 296.6842
1285.9885 | 315.3163 | 307.9328 | 296.9979
1286.9885 | 314.9872 | 307.8186 | 296.7738
1287.9885 | 314.8459 | 307.8812 | 296.6886
1288.9885 | 314.9315 | 307.5175 | 296.6833
1289.9885 | 315.06 | 307.5239 | 296.4656
1290.9885 | 315.0901 | 307.2036 | 296.3284
1291.9885 | 315.1205 | 306.7038 | 296.8155
1292.9885 | 315.501 | 306.7521 | 296.4415
1293.9885 | 315.6548 | 307.445 | 296.5538
1294.9885 | 315.3196 | 308.2482 | 296.7106
1295.9885 | 315.2405 | 308.4028 | 296.842
1296.9885 | 315.1044 | 308.8988 | 296.3285
1297.9885 | 315.3212 | 308.5942 | 296.93
1298.9885 | 315.5397 | 308.2836 | 297.161
1299.9885 | 315.3198 | 308.3835 | 296.7745
1300.9885 | 315.1092 | 308.358 | 296.4154
1301.9885 | 315.1867 | 308.2561 | 296.5437
1303.0042 | 315.055 | 308.5772 | 296.9975
1303.9885 | 315.5738 | 308.7059 | 296.9613
1304.9885 | 315.6879 | 308.8804 | 297.1364
1305.9885 | 315.4139 | 309.1344 | 296.8602
1306.9885 | 315.1261 | 309.0322 | 296.6954
1307.9885 | 315.7141 | 309.9042 | 297.3417
1308.9885 | 315.6374 | 309.2069 | 297.6581
1309.9885 | 315.9377 | 309.2877 | 297.558
1310.9885 | 315.9988 | 309.5661 | 297.772
1311.9885 | 316.1743 | 309.1482 | 297.662
1312.9885 | 316.3015 | 308.7568 | 297.463
1313.9885 | 316.3121 | 308.746 | 297.2051
1314.9885 | 316.5678 | 308.2802 | 297.3327
1315.9885 | 316.5632 | 307.3816 | 297.3071
1316.9885 | 316.739 | 307.0315 | 296.8654
1317.9885 | 317.3131 | 306.7894 | 296.8995
1318.9885 | 317.7399 | 307.1933 | 297.5598
1319.9885 | 317.8089 | 307.2404 | 297.5166
1320.9885 | 317.5117 | 307.2573 | 297.3742
1321.9885 | 317.597 | 307.3812 | 297.4732
1322.9885 | 317.7529 | 307.7874 | 297.6088
1323.9885 | 317.7715 | 308.036 | 297.2078
1324.9885 | 317.6917 | 308.3479 | 297.2597
1325.9885 | 318.1111 | 308.4912 | 297.3671
1326.9885 | 318.2146 | 308.2266 | 297.7771
1327.9885 | 318.3653 | 308.709 | 297.8688
1328.9885 | 318.465 | 309.3302 | 298.0755
1329.9885 | 318.7297 | 309.2105 | 298.0869
1330.9885 | 318.7583 | 309.2828 | 298.1127
1331.9885 | 319.5065 | 309.6398 | 297.6698
1332.9885 | 319.4749 | 309.8802 | 297.5502
1333.9885 | 319.7591 | 309.535 | 297.2977
1334.9885 | 319.5896 | 310.0568 | 297.0215
1335.9885 | 319.326 | 310.0258 | 296.5504
1336.9885 | 319.2876 | 309.8101 | 296.6136
1337.9885 | 318.9888 | 310.1636 | 297.2238
1338.9885 | 319.4314 | 310.0842 | 297.6705
1339.9885 | 319.8511 | 310.3198 | 297.8534
1340.9885 | 320.0225 | 310.7354 | 297.7419
1341.9885 | 319.8014 | 310.935 | 298.7898
1342.9885 | 319.6064 | 310.9946 | 298.7725
1343.9885 | 319.7437 | 310.8009 | 298.5577
1344.9885 | 319.6811 | 310.657 | 298.1347
1345.9885 | 319.8157 | 311.4359 | 299.1388
1346.9885 | 319.7882 | 311.2123 | 299.3919
1347.9885 | 320.2429 | 311.2307 | 299.7863
1348.9885 | 320.0738 | 311.1243 | 299.4692
1349.9885 | 319.973 | 310.9162 | 299.2212
1350.9885 | 320.0125 | 310.3273 | 298.7236
1351.9885 | 319.9646 | 310.3627 | 298.549
1352.9885 | 320.1009 | 310.173 | 298.8125
1353.9885 | 319.8307 | 310.1517 | 299.0906
1354.9885 | 320.1462 | 310.3315 | 298.6514
1355.9885 | 320.0579 | 310.4746 | 298.6551
1356.9885 | 320.3234 | 310.6499 | 299.0757
1357.9885 | 320.4686 | 310.9392 | 299.0678
1358.9885 | 320.3233 | 310.6328 | 299.0248
1359.9885 | 320.462 | 310.6313 | 298.814
1360.9885 | 320.4282 | 310.7416 | 298.8736
1361.9885 | 320.762 | 310.1466 | 298.8383
1362.9885 | 320.5369 | 309.4052 | 298.4731
1363.9885 | 320.2413 | 309.3232 | 298.4994
1364.9885 | 320.3496 | 308.9399 | 298.2525
1365.9885 | 320.3711 | 309.0863 | 297.8773
1366.9885 | 320.4429 | 309.2652 | 297.7631
1367.9885 | 320.6668 | 309.458 | 297.4447
1368.9885 | 320.862 | 310.2347 | 297.3686
1369.9885 | 320.2781 | 310.9115 | 297.5122
1370.9885 | 320.4494 | 311.3054 | 297.9853
1371.9885 | 320.0847 | 311.0733 | 298.1699
1372.9885 | 319.7328 | 310.9942 | 298.0946
1373.9885 | 319.8916 | 311.4984 | 298.756
1374.9885 | 319.6387 | 311.2181 | 298.4591
1375.9885 | 319.7144 | 311.2084 | 298.9728
1376.9885 | 319.6747 | 310.7306 | 299.5392
1377.9885 | 320.0183 | 311.026 | 299.4454
1378.9885 | 320.0737 | 311.4374 | 299.5999
1379.9885 | 320.3492 | 312.0877 | 299.3808
1380.9885 | 320.3287 | 312.2375 | 299.0352
1381.9885 | 320.3235 | 312.2328 | 299.0175
1382.9885 | 319.9674 | 311.7087 | 298.831
1383.9885 | 319.8553 | 310.9418 | 298.4393
1384.9885 | 319.5374 | 311.2116 | 298.1632
1385.9885 | 319.8495 | 310.6615 | 297.802
1386.9885 | 319.4421 | 310.4965 | 297.6299
1387.9885 | 319.3571 | 309.7763 | 297.6385
1388.9885 | 319.9685 | 309.6022 | 297.9238
1389.9885 | 320.5243 | 309.3062 | 297.9289
1390.9885 | 320.2013 | 308.7157 | 298.7234
1391.9885 | 320.3884 | 308.6673 | 298.9708
1392.9885 | 319.989 | 308.7624 | 299.438
1393.9885 | 320.028 | 309.0716 | 299.5271
1394.9885 | 320.01 | 309.4854 | 299.2083
1395.9885 | 319.7922 | 309.7193 | 299.2048
1396.9885 | 319.5525 | 309.7145 | 299.0371
1397.9885 | 319.3701 | 310.1162 | 298.909
1398.9885 | 319.1206 | 310.2229 | 299.0092
1399.9885 | 318.7188 | 310.3319 | 299.1172
1400.9885 | 318.3768 | 310.4337 | 298.6638
1401.9885 | 318.2618 | 310.3614 | 298.5799
1402.9885 | 318.2298 | 310.3435 | 298.3104
1403.9885 | 318.5567 | 310.5396 | 298.2365
1404.9885 | 318.5807 | 310.6568 | 298.2289
1405.9885 | 318.6129 | 310.9346 | 298.285
1406.9885 | 318.4555 | 311.2875 | 298.8492
1407.9885 | 318.3123 | 311.0293 | 298.9909
1408.9885 | 318.7203 | 311.1379 | 299.5401
1409.9885 | 318.3134 | 310.7783 | 299.3737
1410.9885 | 318.0199 | 310.681 | 299.2096
1411.9885 | 317.9523 | 310.378 | 299.1718
1412.9885 | 317.9299 | 310.6065 | 299.6148
1413.9885 | 318.3572 | 310.7295 | 299.5857
1414.9885 | 319.1348 | 311.8623 | 300.2872
1415.9885 | 320.1179 | 312.0106 | 301.9162
1416.9885 | 320.8953 | 312.8868 | 302.6088
1417.9885 | 320.9103 | 313.3295 | 303.3082
1418.9885 | 321.3659 | 313.7714 | 303.6993
1419.9885 | 321.7991 | 313.9694 | 303.6888
1421.0042 | 322.111 | 314.609 | 303.9286
1421.9885 | 322.8626 | 315.3415 | 304.1628
1422.9885 | 322.8599 | 315.8373 | 304.6366
1423.9885 | 322.933 | 316.3475 | 305.1962
1424.9885 | 323.1274 | 316.7504 | 305.5175
1425.9885 | 323.3639 | 317.2367 | 306.1406
1426.9885 | 323.413 | 317.5807 | 306.9356
1427.9885 | 324.3994 | 317.9812 | 307.6337
1428.9885 | 324.7395 | 318.4935 | 308.1968
1429.9885 | 325.4901 | 319.0567 | 308.9692
1430.9885 | 325.7477 | 319.3932 | 309.4452
1431.9885 | 325.9435 | 319.4197 | 309.9903
1432.9885 | 325.8047 | 319.6498 | 310.7384
1433.9885 | 326.1025 | 320.1193 | 310.8471
1434.9885 | 326.9151 | 320.5289 | 310.6947
1435.9885 | 327.2115 | 320.7113 | 311.1473
1436.9885 | 327.5583 | 321.2782 | 311.1822
1437.9885 | 328.04 | 322.0343 | 311.7559
1438.9885 | 328.2667 | 322.5384 | 312.1055
1439.9885 | 328.3504 | 323.7933 | 312.6193
1440.9885 | 328.1384 | 323.8952 | 313.0466
1441.9885 | 328.2477 | 323.6626 | 313.2292
1442.9885 | 328.18 | 323.4031 | 313.2309
1443.9885 | 328.4392 | 323.0788 | 312.975
1444.9885 | 328.3323 | 323.004 | 312.5715
1445.9885 | 328.2902 | 322.9909 | 312.1592
1446.9885 | 328.4525 | 323.165 | 311.949
1447.9885 | 328.5295 | 323.4705 | 311.9874
1448.9885 | 328.7977 | 323.5239 | 311.665
1449.9885 | 329.055 | 324.2594 | 311.5094
1450.9885 | 329.3547 | 324.7969 | 311.4891
1451.9885 | 330.0636 | 325.4301 | 312.2065
1452.9885 | 329.6551 | 325.4449 | 312.3218
1453.9885 | 329.7044 | 325.0807 | 312.3893
1454.9885 | 329.1595 | 324.3464 | 312.0923
1455.9885 | 329.8483 | 324.0937 | 311.6692
1456.9885 | 330.2971 | 323.5859 | 311.2619
1457.9885 | 330.3658 | 323.4157 | 311.2689
1458.9885 | 331.0168 | 323.9167 | 311.047
1459.9885 | 331.5293 | 324.0962 | 310.6031
1460.9885 | 331.9351 | 324.4639 | 310.3757
1461.9885 | 332.1563 | 325.0848 | 310.6185
1462.9885 | 332.3264 | 325.0067 | 310.7083
1463.9885 | 332.5028 | 325.2793 | 311.0337
1464.9885 | 332.8761 | 325.7676 | 311.6935
1465.9885 | 333.1086 | 325.9672 | 312.1222
1466.9885 | 333.4799 | 325.8135 | 312.1207
1467.9885 | 333.6404 | 326.0764 | 312.348
1468.9885 | 333.9002 | 326.3911 | 312.5414
1469.9885 | 333.7661 | 326.1832 | 312.9358
1470.9885 | 334.3182 | 326.1949 | 312.9422
1471.9885 | 334.6975 | 326.6078 | 313.0509
1472.9885 | 334.8346 | 326.9337 | 313.2605
1473.9885 | 335.2656 | 327.0496 | 313.8424
1474.9885 | 335.5359 | 327.0392 | 314.3855
1475.9885 | 335.5702 | 327.0165 | 314.3462
1476.9885 | 335.3682 | 326.503 | 313.9021
1477.9885 | 335.5302 | 326.5814 | 313.7662
1478.9885 | 335.6601 | 326.6432 | 313.6054
1479.9885 | 335.5099 | 325.9885 | 313.093
1480.9885 | 335.3907 | 325.9191 | 312.7689
1481.9885 | 335.7629 | 326.6774 | 314.0589
1482.9885 | 336.2167 | 326.9727 | 314.0712
1483.9885 | 336.1695 | 327.9543 | 314.5128
1484.9885 | 336.634 | 328.3399 | 314.5146
1485.9885 | 336.7279 | 328.3797 | 315.1188
1486.9885 | 337.0903 | 328.4044 | 315.3906
1487.9885 | 337.3079 | 328.4139 | 315.469
1488.9885 | 337.8772 | 329.4805 | 315.7278
1489.9885 | 338.0638 | 329.7244 | 315.9849
1490.9885 | 338.0735 | 329.7362 | 316.3541
1491.9885 | 338.5149 | 330.0714 | 316.9235
1492.9885 | 338.8191 | 330.1204 | 316.8377
1493.9885 | 338.8681 | 329.9319 | 317.2366
1494.9885 | 338.6427 | 329.497 | 317.872
1495.9885 | 339.1306 | 329.1193 | 318.1012
1496.9885 | 339.2834 | 328.9152 | 318.112
1497.9885 | 339.6002 | 328.4978 | 317.7121
1498.9885 | 340.1266 | 328.5954 | 317.3961
1499.9885 | 341.1691 | 329.7369 | 317.7816
1500.9885 | 341.8188 | 329.5685 | 317.4564
1501.9885 | 342.2976 | 329.2582 | 317.0256
1502.9885 | 342.0682 | 329.4378 | 316.9756
1503.9885 | 341.9984 | 329.3101 | 316.7467
1504.9885 | 341.5059 | 329.1157 | 316.795
1505.9885 | 341.5141 | 329.5313 | 316.2896
1506.9885 | 340.7858 | 329.8376 | 316.3772
1507.9885 | 340.5591 | 329.8415 | 316.4185
1508.9885 | 340.7051 | 329.975 | 316.0798
1509.9885 | 341.8166 | 330.4002 | 316.2066
1510.9885 | 341.9242 | 330.8039 | 316.5458
1511.9885 | 342.3372 | 330.3862 | 316.737
1512.9885 | 342.4548 | 331.0029 | 316.857
1513.9885 | 342.3565 | 331.0923 | 316.7945
1514.9885 | 342.4578 | 332.2909 | 317.2385
1515.9885 | 342.6498 | 332.4918 | 317.458
1516.9885 | 343.5094 | 333.3017 | 317.7105
1517.9885 | 343.5311 | 333.1411 | 317.8482
1518.9885 | 343.7892 | 332.9325 | 318.42
1519.9885 | 343.3628 | 333.4602 | 318.7246
1520.9885 | 342.9729 | 333.2621 | 319.3532
1521.9885 | 342.7989 | 333.7101 | 319.4219
1522.9885 | 342.8136 | 333.6315 | 319.3144
1523.9885 | 343.559 | 333.7832 | 319.747
1524.9885 | 343.75 | 333.2833 | 320.1618
1525.9885 | 344.1049 | 332.8255 | 320.1987
1526.9885 | 343.9931 | 332.3207 | 320.3273
1527.9885 | 344.2137 | 331.71 | 319.9553
1528.9885 | 343.9424 | 331.5514 | 319.744
1529.9885 | 344.2253 | 331.2901 | 319.6288
1530.9885 | 344.2722 | 331.1566 | 319.6418
1531.9885 | 344.1535 | 331.0064 | 319.7444
1532.9885 | 344.1944 | 331.1044 | 319.8292
1533.9885 | 344.007 | 331.3988 | 320.0021
1534.9885 | 344.0783 | 331.664 | 319.3477
1535.9885 | 344.0295 | 332.299 | 318.9381
1536.9885 | 344.0284 | 332.0281 | 319.2685
1537.9885 | 343.8773 | 331.8169 | 319.409
1538.9885 | 344.1678 | 332.0361 | 319.2742
1539.9885 | 344.0383 | 332.0878 | 319.1988
1540.9885 | 344.0492 | 331.9038 | 318.5833
1541.9885 | 343.5745 | 331.7367 | 319.1784
1542.9885 | 343.9224 | 331.9297 | 319.3275
1543.9885 | 344.2678 | 332.5031 | 319.4827
1544.9885 | 344.4567 | 333.2968 | 319.838
1545.9885 | 344.7854 | 333.7701 | 319.854
1546.9885 | 344.6687 | 334.3724 | 319.8911
1547.9885 | 344.9903 | 334.8898 | 320.297
1548.9885 | 344.7832 | 334.9879 | 320.9168
1549.9885 | 344.6516 | 335.3896 | 321.1593
1550.9885 | 344.7497 | 335.2507 | 322.3303
1551.9885 | 345.0785 | 335.4107 | 322.6207
1552.9885 | 345.8879 | 335.7296 | 322.1849
1553.9885 | 346.7398 | 335.9442 | 321.9829
1554.9885 | 347.2964 | 336.2915 | 322.3726
1555.9885 | 347.9251 | 336.0064 | 323.1913
1556.9885 | 348.0862 | 335.9213 | 323.7143
1557.9885 | 348.6414 | 337.1307 | 323.5194
1558.9885 | 349.3217 | 338.0891 | 324.1023
1559.9885 | 348.9581 | 338.4806 | 324.0397
1560.9885 | 349.0548 | 338.0492 | 323.6513
1561.9885 | 349.1775 | 338.2948 | 323.4291
1562.9885 | 349.747 | 338.3555 | 323.8232
1563.9885 | 349.8096 | 338.9303 | 324.2083
1564.9885 | 349.9984 | 338.8254 | 324.1848
1565.9885 | 350.4263 | 339.2443 | 324.0605
1566.9885 | 350.4946 | 340.1703 | 324.6576
1567.9885 | 350.497 | 340.1754 | 324.9864
1568.9885 | 351.0198 | 340.7997 | 325.4563
1569.9885 | 351.1102 | 341.3244 | 325.7685
1570.9885 | 351.461 | 341.1874 | 325.7519
1571.9885 | 351.8644 | 340.941 | 325.9186
1572.9885 | 351.5546 | 340.7324 | 325.7479
1573.9885 | 351.3571 | 340.4837 | 325.8624
1574.9885 | 351.7443 | 340.4831 | 325.3322
1575.9885 | 351.5603 | 340.0311 | 325.5701
1576.9885 | 351.6512 | 339.4346 | 325.0318
1577.9885 | 351.3128 | 339.658 | 324.7948
1578.9885 | 351.3914 | 339.78 | 325.4589
1579.9885 | 351.6942 | 339.842 | 325.1907
1580.9885 | 352.059 | 339.8962 | 324.8727
1581.9885 | 352.6957 | 340.3818 | 325.5182
1582.9885 | 352.6137 | 341.1325 | 326.0409
1583.9885 | 352.6211 | 341.1219 | 326.2849
1584.9885 | 352.8426 | 341.287 | 326.926
1585.9885 | 352.8161 | 341.7543 | 327.393
1586.9885 | 352.8695 | 342.4859 | 327.5545
1587.9885 | 352.9789 | 342.7849 | 327.6096
1588.9885 | 353.2078 | 342.7357 | 328.3614
1589.9885 | 353.129 | 342.0146 | 328.6126
1590.9885 | 353.3575 | 342.4792 | 328.8602
1591.9885 | 353.0575 | 342.1715 | 328.7818
1592.9885 | 353.3264 | 341.1265 | 329.3441
1593.9885 | 352.9007 | 340.821 | 329.4836
1594.9885 | 353.918 | 340.5221 | 329.0989
1595.9885 | 353.9065 | 340.6522 | 329.0062
1596.9885 | 354.2676 | 340.8563 | 329.5624
1597.9885 | 354.2282 | 340.9031 | 330.1392
1598.9885 | 354.0579 | 341.0656 | 329.7662
1599.9885 | 354.4019 | 341.0244 | 329.9079
1600.9885 | 354.4529 | 341.0493 | 330.243
1601.9885 | 354.5873 | 341.1364 | 329.9822
1602.9885 | 354.7755 | 340.9282 | 329.8246
1603.9885 | 354.7226 | 341.0233 | 329.491
1604.9885 | 355.0924 | 341.6005 | 329.565
1605.9885 | 355.3547 | 341.9709 | 329.7545
1606.9885 | 355.3751 | 342.8255 | 330.3542
1607.9885 | 355.9126 | 342.5319 | 330.7202
1608.9885 | 356.4562 | 342.6422 | 330.9723
1609.9885 | 357.0171 | 342.3745 | 330.9164
1610.9885 | 357.2597 | 343.0757 | 330.8788
1611.9885 | 357.5683 | 343.6369 | 331.5642
1612.9885 | 357.6678 | 344.1325 | 332.0683
1613.9885 | 357.603 | 344.3854 | 332.0549
1614.9885 | 358.1095 | 345.7027 | 332.8106
1615.9885 | 358.6508 | 345.6128 | 333.3791
1616.9885 | 359.7075 | 345.4758 | 334.062
1617.9885 | 360.0297 | 346.3193 | 334.0548
1618.9885 | 360.0018 | 346.5733 | 334.9792
1619.9885 | 360.7312 | 346.8543 | 335.3953
1620.9885 | 361.6504 | 346.8724 | 335.5602
1621.9885 | 361.7577 | 347.1705 | 335.8391
1622.9885 | 362.2466 | 347.1556 | 336.2568
1623.9885 | 362.8201 | 347.5288 | 336.503
1624.9885 | 362.9727 | 348.2183 | 337.1312
1625.9885 | 364.3537 | 349.7489 | 338.0416
1626.9885 | 364.0159 | 349.9644 | 338.5424
1627.9885 | 364.4653 | 350.1286 | 339.354
1628.9885 | 364.8114 | 350.8494 | 339.8355
1629.9885 | 364.7729 | 351.1199 | 339.988
1630.9885 | 364.621 | 350.8269 | 340.544
1631.9885 | 364.5157 | 350.6654 | 339.8182
1632.9885 | 364.5453 | 350.4811 | 340.3639
1633.9885 | 364.7116 | 350.4318 | 339.7695
1634.9885 | 365.0224 | 350.6196 | 339.6693
1635.9885 | 365.334 | 351.45 | 339.5941
1636.9885 | 365.3467 | 351.8318 | 339.5623
1637.9885 | 365.7142 | 352.0509 | 340.1062
1638.9885 | 365.6281 | 352.7856 | 340.4975
1639.9885 | 365.6743 | 352.9836 | 341.6794
1640.9885 | 365.8979 | 353.2374 | 341.7947
1641.9885 | 366.0557 | 353.353 | 341.7291
1642.9885 | 366.1704 | 353.2401 | 342.3548
1643.9885 | 365.8692 | 353.3409 | 342.9727
1644.9885 | 365.8629 | 353.2836 | 342.3035
1645.9885 | 365.9884 | 353.2139 | 342.398
1646.9885 | 366.5984 | 353.0256 | 341.7623
1647.9885 | 366.964 | 352.4823 | 340.8625
1648.9885 | 366.6254 | 352.22 | 341.1915
1649.9885 | 366.7929 | 351.7197 | 341.1793
1650.9885 | 367.2144 | 352.1702 | 341.1806
1651.9885 | 367.2202 | 352.2016 | 341.0883
1652.9885 | 367.2982 | 352.0239 | 340.6648
1653.9885 | 367.6277 | 352.1465 | 340.2711
1654.9885 | 368.142 | 352.3569 | 340.0742
1655.9885 | 367.8876 | 352.4388 | 340.3118
1656.9885 | 368.6865 | 352.4928 | 340.2072
1657.9885 | 369.5147 | 352.3842 | 339.9809
1658.9885 | 369.8528 | 352.2264 | 340.1785
1659.9885 | 370.3579 | 352.4782 | 339.9493
1660.9885 | 370.5669 | 352.308 | 339.861
1661.9885 | 371.3571 | 352.6614 | 339.9439
1662.9885 | 371.3811 | 352.9498 | 340.6064
1663.9885 | 371.2151 | 353.0826 | 341.0723
1664.9885 | 371.4543 | 353.515 | 341.3783
1665.9885 | 371.9192 | 353.7263 | 341.6244
1666.9885 | 372.5866 | 353.9157 | 341.7901
1667.9885 | 373.4635 | 354.5324 | 341.9727
1668.9885 | 373.8321 | 355.5156 | 342.0965
1669.9885 | 374.8031 | 356.1026 | 342.2233
1670.9885 | 374.8756 | 356.2646 | 342.7155
1671.9885 | 375.0499 | 356.4123 | 343.0464
1672.9885 | 374.9922 | 356.1957 | 343.2582
1673.9885 | 375.1885 | 356.8109 | 343.4373
1674.9885 | 375.2046 | 357.1818 | 343.5011
1675.9885 | 375.4989 | 357.5007 | 343.6647
1676.9885 | 375.5607 | 358.0793 | 343.7777
1677.9885 | 376.3938 | 358.0435 | 344.0319
1678.9885 | 376.736 | 359.0411 | 345.0114
1679.9885 | 376.5006 | 359.3284 | 344.797
1680.9885 | 377.0925 | 359.8672 | 345.2965
1681.9885 | 378.1066 | 360.1041 | 345.0665
1682.9885 | 378.8648 | 360.529 | 344.8515
1683.9885 | 379.4474 | 360.6895 | 344.2769
1684.9885 | 379.7989 | 361.3353 | 344.1361
1685.9885 | 380.0744 | 361.4184 | 344.8984
1686.9885 | 380.4177 | 361.9771 | 345.5742
1687.9885 | 380.8554 | 363.2222 | 346.5438
1688.9885 | 380.9174 | 364.1033 | 347.3547
1689.9885 | 381.038 | 364.3355 | 347.7766
1690.9885 | 381.0157 | 364.3177 | 347.7207
1691.9885 | 380.8949 | 364.2945 | 347.4731
1692.9885 | 380.9396 | 364.1031 | 347.0335
1693.9885 | 380.9503 | 363.9493 | 346.77
1694.9885 | 381.0619 | 364.3163 | 346.8795
1695.9885 | 380.905 | 364.1106 | 347.117
1696.9885 | 380.6195 | 364.2029 | 347.6734
1697.9885 | 380.2925 | 364.5848 | 348.9672
1698.9885 | 380.0471 | 364.7135 | 349.087
1699.9885 | 379.6431 | 364.5389 | 349.535
1700.9885 | 379.8034 | 364.6431 | 349.4121
1701.9885 | 380.0016 | 364.9323 | 349.3193
1702.9885 | 380.3461 | 365.3677 | 349.448
1703.9885 | 380.8758 | 365.5114 | 349.5032
1704.9885 | 380.8962 | 365.4966 | 350.0338
1705.9885 | 381.267 | 365.6291 | 350.1212
1706.9885 | 381.478 | 365.569 | 349.9936
1707.9885 | 381.9857 | 365.5075 | 350.22
1708.9885 | 382.2934 | 365.5165 | 350.1274
1709.9885 | 382.5138 | 365.5696 | 350.6791
1710.9885 | 382.7476 | 365.7474 | 350.7665
1711.9885 | 383.302 | 365.5193 | 350.6735
1712.9885 | 383.7036 | 365.5261 | 350.7955
1713.9885 | 383.8621 | 365.5408 | 351.3641
1714.9885 | 383.7623 | 365.7425 | 351.9164
1715.9885 | 383.9029 | 366.3636 | 352.0538
1716.9885 | 384.5303 | 366.5452 | 352.1786
1717.9885 | 384.703 | 366.3282 | 352.0735
1718.9885 | 385.2056 | 366.0865 | 351.8219
1719.9885 | 385.3052 | 366.0027 | 351.7005
1720.9885 | 385.4136 | 365.9665 | 351.501
1721.9885 | 385.146 | 365.8222 | 352.3661
1722.9885 | 385.7255 | 366.0352 | 351.853
1723.9885 | 385.9826 | 366.4551 | 352.2187
1724.9885 | 386.389 | 366.7262 | 352.3243
1725.9885 | 386.4924 | 367.0326 | 352.5399
1726.9885 | 386.8615 | 367.4639 | 352.6108
1727.9885 | 386.7992 | 367.3058 | 353.1536
1728.9885 | 386.9177 | 367.4255 | 353.5591
1729.9885 | 386.8611 | 367.0668 | 353.8147
1730.9885 | 387.0222 | 366.9023 | 353.7161
1731.9885 | 387.314 | 366.6229 | 353.6162
1732.9885 | 387.2023 | 366.8748 | 353.6887
1733.9885 | 387.3892 | 367.1335 | 353.3026
1734.9885 | 387.4551 | 367.769 | 353.902
1735.9885 | 388.2662 | 368.5832 | 353.853
1736.9885 | 388.859 | 369.1279 | 353.7177
1737.9885 | 389.4066 | 369.8084 | 353.8174
1738.9885 | 389.6436 | 370.1943 | 354.4284
1739.9885 | 389.758 | 370.5127 | 354.5991
1740.9885 | 389.8414 | 370.676 | 355.2233
1741.9885 | 390.1895 | 371.1246 | 354.962
1742.9885 | 390.465 | 371.517 | 354.8533
1743.9885 | 390.9074 | 371.6754 | 355.0634
1744.9885 | 391.6383 | 371.3269 | 355.0691
1745.9885 | 392.8897 | 371.3643 | 355.0295
1746.9885 | 393.5139 | 371.6881 | 355.8828
1747.9885 | 394.3204 | 371.6187 | 355.8845
1748.9885 | 394.4868 | 371.3067 | 356.361
1749.9885 | 394.6925 | 371.2494 | 357.0137
1750.9885 | 395.3589 | 371.8766 | 357.1978
1751.9885 | 395.797 | 371.958 | 357.4325
1752.9885 | 395.9857 | 372.6586 | 357.5448
1753.9885 | 395.6332 | 373.3893 | 357.4026
1754.9885 | 395.6065 | 373.9285 | 357.4092
1755.9885 | 396.7218 | 374.2654 | 357.419
1756.9885 | 397.2694 | 374.1147 | 358.2091
1757.9885 | 397.2506 | 374.1596 | 358.1995
1758.9885 | 397.1181 | 374.4249 | 358.5747
1759.9885 | 397.0694 | 374.4589 | 358.3467
1760.9885 | 396.815 | 374.2501 | 358.2832
1761.9885 | 398.2843 | 374.0334 | 357.9941
1762.9885 | 398.8344 | 374.3988 | 357.6206
1763.9885 | 399.4014 | 374.8335 | 357.8659
1764.9885 | 400.0134 | 375.1405 | 358.0578
1765.9885 | 400.1414 | 375.0146 | 358.1405
1766.9885 | 399.9258 | 375.3228 | 358.1632
1767.9885 | 400.3515 | 375.7485 | 358.5023
1768.9885 | 401.1338 | 375.921 | 358.968
1769.9885 | 401.2684 | 375.9192 | 359.0823
1770.9885 | 401.2599 | 376.1583 | 359.4217
1771.9885 | 401.3364 | 376.167 | 359.7372
1772.9885 | 401.7275 | 376.381 | 360.0975
1773.9885 | 401.8597 | 376.5917 | 360.3845
1774.9885 | 402.4802 | 376.3864 | 360.8666
1775.9885 | 403.056 | 376.2407 | 361.1963
1776.9885 | 403.7832 | 376.3996 | 361.397
1777.9885 | 404.4735 | 376.7102 | 361.428
1778.9885 | 404.9395 | 377.4335 | 361.8029
1779.9885 | 405.0624 | 377.3726 | 361.928
1780.9885 | 405.0204 | 377.6638 | 362.605
1781.9885 | 405.0058 | 377.8136 | 362.6102
1782.9885 | 405.1352 | 378.2291 | 362.5015
1783.9885 | 405.227 | 378.4859 | 362.2894
1784.9885 | 404.5642 | 378.3383 | 362.471
1785.9885 | 404.2282 | 378.5643 | 362.313
1786.9885 | 403.7328 | 378.7297 | 362.1473
1787.9885 | 403.4669 | 378.3533 | 362.0628
1788.9885 | 403.7942 | 378.0925 | 362.4114
1789.9885 | 403.5218 | 378.2203 | 362.4101
1790.9885 | 403.161 | 378.6027 | 362.2415
1791.9885 | 403.0558 | 378.7587 | 362.105
1792.9885 | 402.8634 | 378.9731 | 362.4181
1793.9885 | 402.4408 | 379.3849 | 362.5235
1794.9885 | 401.9352 | 379.3935 | 362.9933
1795.9885 | 401.391 | 379.0367 | 363.326
1796.9885 | 401.1571 | 378.5862 | 363.5029
1797.9885 | 400.9171 | 378.1157 | 362.7364
1798.9885 | 400.7409 | 377.5424 | 363.2433
1799.9885 | 401.2864 | 377.2014 | 363.0319
1800.9885 | 401.6029 | 378.2262 | 362.8581
1801.9885 | 401.9969 | 379.29 | 362.6743
1802.9885 | 402.2099 | 379.5702 | 362.89
1803.9885 | 402.0262 | 379.615 | 362.4606
1804.9885 | 402.6914 | 380.029 | 362.2998
1805.9885 | 402.6694 | 379.7152 | 362.217
1806.9885 | 402.8868 | 379.6823 | 362.4897
1807.9885 | 402.8408 | 379.2483 | 362.8372
1808.9885 | 402.8791 | 379.0494 | 362.9201
1809.9885 | 402.9151 | 378.6327 | 363.0002
1810.9885 | 403.4279 | 378.4164 | 363.641
1811.9885 | 403.2676 | 379.2555 | 363.6706
1812.9885 | 403.6399 | 379.6313 | 363.2722
1813.9885 | 403.692 | 380.2472 | 363.8154
1814.9885 | 404.0283 | 380.2827 | 363.7313
1815.9885 | 403.8964 | 380.1598 | 363.9112
1816.9885 | 403.6236 | 379.9471 | 363.7343
1817.9885 | 403.4071 | 379.7317 | 364.0603
1818.9885 | 403.6339 | 379.5307 | 364.3046
1819.9885 | 404.378 | 380.8499 | 364.2925
1820.9885 | 405.2338 | 382.2062 | 364.006
1821.9885 | 405.6571 | 383.4435 | 364.3836
1822.9885 | 405.5234 | 383.4927 | 364.7992
1823.9885 | 404.9382 | 383.9521 | 365.3157
1824.9885 | 404.952 | 384.3314 | 365.8824
1825.9885 | 404.7542 | 384.5863 | 366.2853
1826.9885 | 404.9884 | 385.5656 | 366.4167
1827.9885 | 405.8294 | 386.1102 | 366.677
1828.9885 | 406.1105 | 386.7695 | 367.7711
1829.9885 | 406.2765 | 387.1412 | 367.6932
1830.9885 | 406.3593 | 387.8336 | 367.6926
1831.9885 | 406.1131 | 388.2859 | 367.7833
1832.9885 | 406.0072 | 388.5452 | 367.3721
1833.9885 | 405.7706 | 388.5343 | 367.6376
1834.9885 | 406.0291 | 388.4525 | 367.7033
1835.9885 | 406.0159 | 388.4768 | 367.6246
1836.9885 | 406.8331 | 388.1448 | 367.5704
1837.9885 | 407.3771 | 387.818 | 367.824
1838.9885 | 407.5947 | 387.9692 | 368.2235
1839.9885 | 407.9995 | 387.9979 | 368.5274
1840.9885 | 409.0896 | 388.2454 | 369.9091
1841.9885 | 409.3199 | 389.2204 | 370.2604
1842.9885 | 410.1565 | 389.959 | 370.4481
1843.9885 | 411.2497 | 390.4254 | 370.6503
1844.9885 | 411.2067 | 390.9253 | 370.6517
1845.9885 | 411.3262 | 391.0672 | 371.1732
1846.9885 | 411.5483 | 391.0098 | 371.2534
1847.9885 | 411.9812 | 391.2603 | 371.5581
1848.9885 | 411.7964 | 391.3249 | 371.5207
1849.9885 | 412.0583 | 391.424 | 371.0491
1850.9885 | 411.5411 | 391.2038 | 371.0696
1851.9885 | 411.8849 | 390.9725 | 371.5505
1852.9885 | 412.024 | 390.659 | 372.2625
1853.9885 | 412.9425 | 391.0917 | 372.6009
1854.9885 | 412.8616 | 391.5075 | 373.0925
1855.9885 | 412.5028 | 391.8472 | 374.4517
1856.9885 | 412.0424 | 392.1144 | 375.2225
1857.9885 | 411.3934 | 392.3992 | 375.6011
1858.9885 | 410.7758 | 392.3871 | 375.3993
1859.9885 | 410.6577 | 392.1369 | 375.0552
1860.9885 | 411.0378 | 392.137 | 374.6126
1861.9885 | 411.009 | 391.7756 | 374.2685
1862.9885 | 411.1413 | 391.8959 | 374.393
1863.9885 | 411.4568 | 392.1257 | 375.605
1864.9885 | 411.2587 | 392.4703 | 376.6431
1865.9885 | 411.497 | 392.0382 | 377.1342
1866.9885 | 412.1084 | 391.9612 | 377.1347
1867.9885 | 412.0276 | 391.6448 | 376.9024
1868.9885 | 412.0734 | 391.6757 | 376.4043
1869.9885 | 412.9645 | 391.596 | 376.2643
1870.9885 | 412.9998 | 391.3441 | 376.1996
1871.9885 | 413.2065 | 391.0598 | 375.9694
1872.9885 | 413.251 | 390.9259 | 376.5597
1873.9885 | 413.4827 | 391.0625 | 377.1455
1874.9885 | 413.678 | 391.5017 | 377.601
1875.9885 | 413.9618 | 392.4041 | 378.2512
1876.9885 | 413.9453 | 392.9989 | 378.5471
1877.9885 | 413.8554 | 393.122 | 378.8389
1878.9885 | 413.8845 | 393.3075 | 378.9299
1879.9885 | 414.0589 | 393.65 | 378.9194
1880.9885 | 413.8679 | 393.9641 | 378.5239
1881.9885 | 413.9353 | 393.9435 | 378.0861
1882.9885 | 414.0505 | 394.1455 | 377.8063
1883.9885 | 414.0744 | 394.1423 | 378.0583
1884.9885 | 414.4331 | 394.9237 | 378.3147
1885.9885 | 414.3906 | 395.1919 | 378.2161
1886.9885 | 414.8883 | 394.9122 | 377.5725
1887.9885 | 415.2349 | 394.7797 | 377.1705
1888.9885 | 415.56 | 394.702 | 376.9752
1889.9885 | 415.4636 | 394.3455 | 376.9337
1890.9885 | 415.3934 | 394.6803 | 377.2582
1891.9885 | 416.2469 | 395.1466 | 377.4662
1892.9885 | 417.3785 | 395.3558 | 377.8337
1893.9885 | 417.2811 | 395.332 | 378.3913
1894.9885 | 417.4559 | 395.3157 | 378.5076
1895.9885 | 417.2181 | 395.5823 | 379.112
1896.9885 | 417.2673 | 396.0613 | 379.6221
1897.9885 | 417.4816 | 396.4674 | 380.9209
1898.9885 | 417.1114 | 397.1407 | 381.8477
1899.9885 | 416.6217 | 397.5043 | 382.4716
1900.9885 | 416.6358 | 397.6979 | 382.7405
1901.9885 | 416.6568 | 397.391 | 382.7372
1902.9885 | 416.6199 | 397.671 | 383.2402
1903.9885 | 416.6083 | 398.2134 | 383.5289
1904.9885 | 416.3141 | 398.081 | 383.732
1905.9885 | 416.6057 | 397.9796 | 384.5101
1906.9885 | 416.1753 | 398.0575 | 384.8705
1907.9885 | 416.5438 | 397.9968 | 385.1731
1908.9885 | 416.8243 | 397.578 | 386.0746
1909.9885 | 417.5737 | 397.3563 | 386.6139
1910.9885 | 417.8376 | 397.3905 | 386.758
1911.9885 | 418.4652 | 397.9402 | 386.9415
1912.9885 | 418.305 | 397.9668 | 387.0805
1913.9885 | 417.8931 | 398.0951 | 386.9826
1914.9885 | 417.9212 | 397.9395 | 386.98
1915.9885 | 417.9119 | 397.8284 | 387.1615
1916.9885 | 418.0161 | 398.051 | 387.1824
1917.9885 | 417.8932 | 398.5788 | 387.7008
1918.9885 | 417.6939 | 399.8498 | 388.3039
1919.9885 | 417.7211 | 400.0041 | 388.8345
1920.9885 | 418.0844 | 400.4003 | 389.2232
1921.9885 | 417.8923 | 400.7672 | 389.9792
1922.9885 | 418.1509 | 401.1745 | 390.3244
1923.9885 | 418.447 | 401.4174 | 390.7833
1924.9885 | 418.8069 | 401.778 | 391.0352
1925.9885 | 418.8566 | 401.6962 | 390.9826
1926.9885 | 418.977 | 401.6087 | 391.2298
1927.9885 | 418.8843 | 402.6039 | 391.4382
1928.9885 | 418.7938 | 402.6218 | 391.1866
1929.9885 | 418.606 | 402.1184 | 390.918
1930.9885 | 418.1363 | 401.6048 | 390.821
1931.9885 | 419.2726 | 401.384 | 390.5156
1932.9885 | 418.8701 | 400.9393 | 390.529
1933.9885 | 420.8117 | 400.998 | 390.703
1934.9885 | 421.5178 | 401.0955 | 390.3641
1935.9885 | 421.6102 | 401.2413 | 390.5607
1936.9885 | 422.0376 | 401.8309 | 390.678
1937.9885 | 422.05 | 402.2858 | 391.2867
1938.9885 | 422.2279 | 403.0526 | 391.8116
1939.9885 | 422.1249 | 403.8204 | 392.5037
1940.9885 | 422.4904 | 404.5319 | 392.9957
1941.9885 | 422.6073 | 404.8128 | 393.3521
1942.9885 | 423.5057 | 404.8019 | 393.6195
1943.9885 | 424.1671 | 404.7662 | 393.2877
1944.9885 | 423.9969 | 404.9865 | 392.4828
1945.9885 | 423.8775 | 405.1008 | 392.1808
1946.9885 | 424.0262 | 405.182 | 392.3216
1947.9885 | 424.4181 | 405.3924 | 392.6952
1948.9885 | 424.2929 | 405.1905 | 393.7062
1949.9885 | 424.2637 | 405.1632 | 393.9744
1950.9885 | 424.7408 | 405.451 | 394.6195
1951.9885 | 425.011 | 405.2049 | 394.4921
1952.9885 | 424.872 | 405.3352 | 394.9591
1953.9885 | 425.7317 | 405.8853 | 395.2457
1954.9885 | 426.0846 | 406.1617 | 395.8779
1955.9885 | 426.577 | 406.3561 | 396.2903
1956.9885 | 426.7348 | 406.6541 | 396.8148
1957.9885 | 427.0648 | 407.2891 | 396.2986
1958.9885 | 427.4653 | 407.4518 | 395.4705
1959.9885 | 427.7201 | 407.3114 | 394.7729
1960.9885 | 427.8685 | 407.4371 | 394.7465
1961.9885 | 428.5319 | 407.7217 | 394.7092
1962.9885 | 428.7102 | 407.4577 | 394.9421
1963.9885 | 429.3066 | 407.8156 | 395.4396
1964.9885 | 429.3996 | 408.0283 | 395.8678
1965.9885 | 429.5923 | 408.3159 | 396.5241
1966.9885 | 429.3536 | 408.7574 | 397.4816
1967.9885 | 429.4721 | 409.3858 | 397.9839
1968.9885 | 429.1751 | 409.6797 | 398.3978
1969.9885 | 428.7877 | 409.8513 | 398.7479
1970.9885 | 428.5115 | 409.7622 | 398.5409
1971.9885 | 428.1987 | 409.4973 | 398.659
1972.9885 | 427.9847 | 409.8872 | 398.6621
1973.9885 | 427.9864 | 409.9318 | 399.2773
1974.9885 | 427.926 | 409.9544 | 399.517
1975.9885 | 428.2473 | 410.0977 | 399.6886
1976.9885 | 428.2626 | 410.4706 | 399.8372
1977.9885 | 428.4886 | 410.6284 | 400.3266
1978.9885 | 428.779 | 410.5941 | 401.1451
1979.9885 | 430.2421 | 410.6994 | 401.0545
1980.9885 | 429.8649 | 410.5591 | 400.7039
1981.9885 | 430.0847 | 410.6936 | 400.506
1982.9885 | 430.5862 | 410.81 | 400.6145
1983.9885 | 431.0757 | 410.8234 | 400.5587
1984.9885 | 431.1516 | 410.7423 | 399.8371
1985.9885 | 431.1414 | 411.2497 | 399.7313
1986.9885 | 431.2593 | 411.4608 | 399.2872
1987.9885 | 431.66 | 411.4529 | 399.0414
1988.9885 | 431.3891 | 411.3592 | 398.9733
1989.9885 | 431.1585 | 411.6528 | 399.0393
1990.9885 | 431.3407 | 411.9998 | 399.6748
1991.9885 | 431.2527 | 412.0019 | 400.0827
1992.9885 | 431.7824 | 412.1344 | 400.66
1993.9885 | 431.7345 | 412.0939 | 400.3812
1994.9885 | 431.5478 | 412.1305 | 400.1469
1995.9885 | 432.3185 | 412.1756 | 400.9033
1996.9885 | 432.6299 | 412.3879 | 400.9968
1997.9885 | 432.3918 | 412.2574 | 400.9148
1998.9885 | 433.2523 | 412.2215 | 400.8537
1999.9885 | 434.2311 | 412.2998 | 401.0333
2000.9885 | 434.8098 | 412.679 | 401.2524
2001.9885 | 434.5345 | 413.1875 | 402.6871
2002.9885 | 434.3172 | 413.5493 | 403.2379
2003.9885 | 434.3295 | 413.946 | 404.1368
2004.9885 | 434.5728 | 414.0757 | 405.2451
2005.9885 | 434.3582 | 413.9615 | 405.4814
2006.9885 | 435.0878 | 414.4758 | 406.0479
2007.9885 | 435.0814 | 414.7913 | 405.8557
2008.9885 | 435.1391 | 414.8338 | 405.6031
2009.9885 | 435.7386 | 414.53 | 405.4552
2010.9885 | 436.2332 | 414.2162 | 405.2235
2011.9885 | 436.3709 | 414.0964 | 404.7011
2012.9885 | 436.1713 | 413.8205 | 404.5843
2013.9885 | 436.335 | 413.8866 | 404.9588
2014.9885 | 436.116 | 414.1589 | 404.7738
2015.9885 | 435.6312 | 414.3486 | 404.671
2016.9885 | 435.4306 | 414.2315 | 405.3957
2017.9885 | 435.043 | 413.9456 | 405.3523
2018.9885 | 435.3237 | 414.143 | 405.7054
2019.9885 | 435.825 | 414.6753 | 406.0136
2020.9885 | 436.5754 | 415.3158 | 406.2425
2021.9885 | 438.3729 | 415.588 | 406.2106
2022.9885 | 438.5547 | 415.7444 | 405.7892
2023.9885 | 438.8544 | 416.1 | 405.6398
2024.9885 | 438.1015 | 416.2173 | 405.7676
2025.9885 | 438.1235 | 416.822 | 406.3411
2026.9885 | 438.5418 | 417.1741 | 406.4325
2027.9885 | 438.2526 | 416.9361 | 406.6668
2028.9885 | 438.0762 | 416.9408 | 406.6306
2029.9885 | 437.8744 | 417.0368 | 406.6065
2030.9885 | 437.7165 | 418.2197 | 406.6391
2031.9885 | 438.0968 | 418.2028 | 406.4475
2032.9885 | 438.0138 | 417.9989 | 406.3393
2033.9885 | 438.6541 | 417.8193 | 406.9666
2034.9885 | 439.5068 | 417.7833 | 407.2766
2035.9885 | 439.947 | 418.1138 | 407.2436
2036.9885 | 439.7026 | 418.3578 | 408.0714
2037.9885 | 439.92 | 418.1456 | 408.6709
2038.9885 | 439.8475 | 418.24 | 408.8932
2039.9885 | 439.8217 | 418.4941 | 408.9537
2040.9885 | 440.2308 | 418.6993 | 409.2563
2041.9885 | 440.1483 | 418.802 | 409.4644
2042.9885 | 440.4404 | 419.3754 | 410.0244
2043.9885 | 440.425 | 419.3114 | 410.6586
2044.9885 | 440.9419 | 419.5988 | 410.8269
2045.9885 | 441.9481 | 420.1127 | 410.3905
2046.9885 | 441.7872 | 420.2723 | 410.367
2047.9885 | 441.8852 | 420.3455 | 410.573
2048.9885 | 442.115 | 420.9979 | 410.9013
2049.9885 | 442.1511 | 420.7378 | 411.2557
2050.9885 | 442.5716 | 420.9646 | 411.7874
2051.9885 | 443.2439 | 421.4818 | 412.0565
2052.9885 | 443.6026 | 421.5311 | 412.3459
2053.9885 | 444.2095 | 421.7324 | 412.524
2054.9885 | 444.7046 | 421.7515 | 413.1515
2055.9885 | 444.062 | 421.4904 | 413.0791
2056.9885 | 443.7435 | 421.3157 | 412.9539
2057.9885 | 443.9334 | 420.9638 | 412.5036
2058.9885 | 444.1173 | 420.8121 | 412.2036
2059.9885 | 444.8015 | 421.0045 | 411.7575
2060.9885 | 445.1796 | 421.0636 | 411.414
2061.9885 | 446.2649 | 420.9748 | 411.0284
2062.9885 | 447.1938 | 420.8387 | 410.7718
2063.9885 | 447.4062 | 420.8008 | 410.954
2064.9885 | 446.6328 | 421.6673 | 411.1208
2065.9885 | 446.7499 | 422.2728 | 411.1985
2066.9885 | 447.0701 | 422.96 | 411.4224
2067.9885 | 446.9481 | 423.3627 | 411.7027
2068.9885 | 446.8902 | 424.4706 | 412.3617
2069.9885 | 446.5381 | 424.8908 | 414.1989
2070.9885 | 446.8025 | 425.3639 | 414.883
2071.9885 | 447.2348 | 425.4654 | 415.2997
2072.9885 | 447.7088 | 425.562 | 415.6699
2073.9885 | 448.4313 | 425.8618 | 416.2983
2074.9885 | 448.0408 | 425.6951 | 417.4767
2075.9885 | 448.1461 | 426.3426 | 418.1165
2076.9885 | 448.7375 | 426.6432 | 417.9932
2077.9885 | 448.7087 | 427.176 | 417.6723
2078.9885 | 449.3593 | 427.3739 | 418.4936
2079.9885 | 449.4066 | 427.3895 | 418.5138
2080.9885 | 449.1564 | 428.1471 | 419.036
2081.9885 | 448.7914 | 428.0518 | 419.7467
2082.9885 | 448.6636 | 427.999 | 420.5452
2083.9885 | 448.7963 | 427.6761 | 421.004
2084.9885 | 448.8605 | 427.4975 | 421.1682
2085.9885 | 449.053 | 427.1795 | 420.6056
2086.9885 | 449.7272 | 427.3735 | 420.3155
2087.9885 | 449.5177 | 427.257 | 420.2081
2088.9885 | 449.6702 | 427.257 | 420.2809
2089.9885 | 450.3268 | 427.4322 | 420.5503
2090.9885 | 450.0609 | 427.6976 | 420.6223
2091.9885 | 449.8723 | 427.5266 | 421.1631
2092.9885 | 450.1767 | 428.4448 | 421.428
2093.9885 | 450.6573 | 428.4452 | 421.8317
2094.9885 | 451.6373 | 428.3475 | 421.7319
2095.9885 | 452.7251 | 428.4126 | 422.1216
2096.9885 | 452.8724 | 428.2844 | 422.3797
2097.9885 | 453.3901 | 427.9819 | 422.3965
2098.9885 | 453.1623 | 427.7279 | 422.7226
2099.9885 | 453.0183 | 427.5238 | 422.3971
2100.9885 | 452.9844 | 427.2205 | 421.6892
2101.9885 | 452.7252 | 427.402 | 421.4366
2102.9885 | 452.4482 | 427.4567 | 421.0451
2103.9885 | 452.306 | 428.0417 | 420.9052
2104.9885 | 452.3622 | 428.5765 | 421.0751
2105.9885 | 452.1592 | 428.74 | 421.6726
2106.9885 | 451.8296 | 428.957 | 422.1974
2107.9885 | 452.1723 | 429.0655 | 423.1456
2108.9885 | 451.9063 | 429.093 | 423.0817
2109.9885 | 452.3202 | 428.8387 | 423.118
2110.9885 | 453.9036 | 428.9274 | 423.3523
2112.0042 | 454.7933 | 429.3004 | 423.6884
2112.9885 | 454.8242 | 429.5918 | 423.7047
2113.9885 | 455.2963 | 429.8149 | 423.1789
2114.9885 | 456.4556 | 429.8834 | 422.6412
2115.9885 | 456.5954 | 429.7587 | 422.4132
2116.9885 | 456.7121 | 429.4962 | 422.074
2117.9885 | 457.5104 | 429.6629 | 421.8601
2118.9885 | 457.9726 | 430.3519 | 421.8854
2119.9885 | 458.2058 | 430.8572 | 421.8903
2120.9885 | 457.5027 | 430.9156 | 422.0389
2121.9885 | 457.6163 | 430.8562 | 422.0716
2122.9885 | 457.3414 | 430.4443 | 422.0419
2123.9885 | 457.5993 | 430.1499 | 422.382
2124.9885 | 457.8357 | 430.1286 | 422.2491
2125.9885 | 457.5018 | 429.6332 | 422.2171
2126.9885 | 457.0388 | 429.4698 | 423.0463
2127.9885 | 457.1928 | 429.5844 | 423.7784
2128.9885 | 457.8934 | 429.7055 | 423.2914
2129.9885 | 458.7443 | 429.5743 | 422.8655
2130.9885 | 459.4225 | 429.8551 | 422.5955
2131.9885 | 459.865 | 429.9353 | 422.4664
2132.9885 | 460.7455 | 430.199 | 422.778
2133.9885 | 461.9109 | 430.6901 | 423.1878
2134.9885 | 462.345 | 431.2776 | 423.7072
2135.9885 | 463.1559 | 432.4882 | 424.5359
2136.9885 | 463.169 | 433.5038 | 424.9809
2137.9885 | 462.674 | 434.2089 | 425.8539
2138.9885 | 462.4667 | 434.5011 | 426.4338
2139.9885 | 462.6826 | 434.699 | 427.1351
2140.9885 | 462.7174 | 434.6321 | 427.2282
2141.9885 | 462.8172 | 434.6924 | 427.7087
2142.9885 | 463.367 | 435.6442 | 427.9037
2143.9885 | 464.1317 | 435.9802 | 428.837
2144.9885 | 463.9355 | 436.6513 | 429.3535
2145.9885 | 464.0522 | 436.4989 | 429.3936
2146.9885 | 464.5427 | 436.3785 | 429.3034
2147.9885 | 464.4151 | 436.5854 | 429.5409
2148.9885 | 463.6904 | 437.1448 | 430.2213
2149.9885 | 464.4041 | 437.5625 | 430.6582
2150.9885 | 464.1403 | 438.0631 | 430.8811
2151.9885 | 463.456 | 438.3676 | 431.2008
2152.9885 | 463.5204 | 438.5624 | 432.271
2153.9885 | 463.5818 | 438.2988 | 432.414
2154.9885 | 463.6379 | 437.9473 | 432.454
2155.9885 | 463.3642 | 438.1348 | 432.0677
2156.9885 | 463.1861 | 437.9887 | 432.3564
2157.9885 | 463.5324 | 437.4102 | 432.2779
2158.9885 | 464.0013 | 437.0143 | 431.6373
2159.9885 | 464.4278 | 436.8833 | 431.1989
2160.9885 | 464.5693 | 436.6561 | 431.0943
2161.9885 | 464.7472 | 436.4807 | 431.1255
2162.9885 | 465.3377 | 436.3749 | 431.1158
2163.9885 | 465.8605 | 436.3394 | 431.4348
2164.9885 | 466.0963 | 436.5847 | 431.6128
2165.9885 | 466.4653 | 436.8554 | 431.9298
2166.9885 | 467.1375 | 437.0109 | 432.6697
2167.9885 | 467.4694 | 436.9827 | 432.9334
2168.9885 | 468.0538 | 437.0375 | 433.2997
2169.9885 | 468.2269 | 437.1036 | 433.0308
2170.9885 | 468.0536 | 437.2753 | 433.0645
2171.9885 | 468.6245 | 437.2666 | 432.9281
2172.9885 | 468.8722 | 437.3973 | 432.4835
2173.9885 | 469.8181 | 437.5532 | 432.3038
2174.9885 | 469.9914 | 437.7316 | 432.5357
2175.9885 | 470.1052 | 438.3734 | 432.0611
2176.9885 | 470.2474 | 438.6502 | 431.7335
2177.9885 | 469.8762 | 438.8683 | 431.6867
2178.9885 | 470.2869 | 438.8018 | 431.8356
2179.9885 | 470.5857 | 438.7277 | 431.6892
2180.9885 | 470.975 | 438.7417 | 431.5835
2181.9885 | 471.4919 | 438.8137 | 431.4128
2182.9885 | 471.6645 | 439.4833 | 431.1755
2183.9885 | 472.0433 | 440.0725 | 431.2316
2184.9885 | 472.1786 | 440.8044 | 431.0041
2185.9885 | 472.2235 | 441.1583 | 430.9317
2186.9885 | 473.3949 | 441.3536 | 431.5138
2187.9885 | 473.5024 | 441.6407 | 432.1261
2188.9885 | 474.0892 | 441.7552 | 432.1651
2189.9885 | 474.6722 | 441.6164 | 432.0466
2190.9885 | 475.4582 | 441.6818 | 431.4467
2191.9885 | 476.6883 | 442.3464 | 431.1481
2192.9885 | 476.8216 | 442.9973 | 431.4023
2193.9885 | 476.7394 | 444.21 | 431.9859
2194.9885 | 476.9129 | 445.1952 | 432.5188
2195.9885 | 477.1137 | 445.6359 | 432.9629
2196.9885 | 477.1418 | 445.4924 | 433.565
2197.9885 | 477.4264 | 445.8217 | 434.416
2198.9885 | 476.3725 | 446.4492 | 434.895
2199.9885 | 476.6693 | 446.1446 | 435.6439
2200.9885 | 476.2454 | 445.8576 | 435.6525
2201.9885 | 476.2828 | 445.968 | 435.822
2202.9885 | 477.2185 | 446.1329 | 435.9695
2203.9885 | 476.742 | 446.1688 | 436.4992
2204.9885 | 477.6713 | 446.3409 | 437.0024
2205.9885 | 478.1434 | 446.5043 | 437.501
2206.9885 | 478.7038 | 447.1814 | 438.1119
2207.9885 | 479.3224 | 447.4742 | 438.7191
2208.9885 | 479.5443 | 447.7219 | 439.5917
2209.9885 | 480.5743 | 447.9415 | 440.3751
2210.9885 | 480.8465 | 447.9307 | 440.7658
2211.9885 | 480.4305 | 447.7924 | 441.4162
2212.9885 | 480.398 | 447.7352 | 441.2636
2213.9885 | 480.5173 | 447.9965 | 441.5031
2214.9885 | 480.3011 | 448.019 | 441.7895
2215.9885 | 480.4331 | 448.0501 | 441.7489
2216.9885 | 480.3084 | 448.3101 | 441.2547
2217.9885 | 480.2257 | 447.9636 | 440.458
2218.9885 | 480.7527 | 447.6531 | 440.2211
2219.9885 | 480.5377 | 447.2772 | 439.6132
2220.9885 | 480.7785 | 446.9253 | 439.0445
2221.9885 | 480.55 | 446.884 | 438.454
2222.9885 | 480.6386 | 447.0667 | 438.0675
2223.9885 | 481.9393 | 447.2203 | 437.717
2224.9885 | 482.8878 | 448.0215 | 437.9006
2225.9885 | 483.5968 | 448.2871 | 438.7313
2226.9885 | 484.3586 | 447.925 | 439.6518
2227.9885 | 484.4141 | 447.762 | 439.9775
2228.9885 | 485.0531 | 447.5648 | 440.2083
2229.9885 | 484.4788 | 447.0866 | 440.3181
2230.9885 | 484.4168 | 446.9799 | 439.8573
2231.9885 | 484.5589 | 446.9312 | 439.6004
2232.9885 | 484.7276 | 447.0168 | 439.7996
2233.9885 | 483.9737 | 447.1865 | 439.6125
2234.9885 | 483.5394 | 447.6996 | 440.3993
2235.9885 | 483.0637 | 448.6736 | 441.927
2236.9885 | 482.914 | 448.7454 | 441.9292
2237.9885 | 483.0265 | 449.0683 | 441.9045
2238.9885 | 483.0618 | 448.9485 | 441.5352
2239.9885 | 483.238 | 448.7579 | 440.6687
2240.9885 | 484.0992 | 448.5415 | 440.5513
2241.9885 | 484.7526 | 448.9927 | 440.3415
2242.9885 | 484.8533 | 449.7226 | 440.9189
2243.9885 | 485.0774 | 450.5686 | 441.5223
2244.9885 | 485.2565 | 451.4939 | 441.8914
2245.9885 | 485.476 | 451.8688 | 442.2495
2246.9885 | 486.244 | 452.1754 | 442.9757
2247.9885 | 486.9914 | 453.3053 | 443.6087
2248.9885 | 486.9933 | 453.591 | 444.1674
2249.9885 | 487.8584 | 453.7769 | 444.1954
2250.9885 | 487.8474 | 454.0321 | 444.2287
2251.9885 | 488.3828 | 454.4651 | 444.425
2252.9885 | 489.3045 | 455.7272 | 444.2766
2253.9885 | 490.2614 | 456.1835 | 445.1259
2254.9885 | 490.7772 | 456.4503 | 445.5374
2255.9885 | 491.9024 | 457.1719 | 446.1842
2256.9885 | 492.0748 | 457.7507 | 446.2315
2257.9885 | 491.973 | 458.1819 | 446.7043
2258.9885 | 492.5725 | 458.1337 | 447.4147
2259.9885 | 492.4414 | 457.8555 | 447.4175
2260.9885 | 492.4697 | 458.2282 | 447.436
2261.9885 | 493.5669 | 458.9084 | 447.2537
2262.9885 | 493.0273 | 458.8331 | 448.9773
2263.9885 | 493.0206 | 458.7525 | 448.4953
2264.9885 | 492.8519 | 458.2083 | 449.3299
2265.9885 | 493.5368 | 458.2946 | 449.0247
2266.9885 | 493.7637 | 458.1685 | 448.6302
2267.9885 | 494.2245 | 458.2204 | 448.7425
2268.9885 | 493.8154 | 458.2263 | 448.7221
2269.9885 | 494.3561 | 458.6323 | 448.8211
2270.9885 | 495.2986 | 459.3362 | 449.0367
2271.9885 | 495.4047 | 460.075 | 449.9177
2272.9885 | 495.9157 | 460.7221 | 450.3307
2273.9885 | 495.3428 | 460.8481 | 450.5677
2274.9885 | 495.6273 | 461.5217 | 451.4878
2275.9885 | 496.7073 | 462.6852 | 451.358
2276.9885 | 497.6853 | 464.5537 | 451.7587
2277.9885 | 497.8053 | 464.599 | 451.722
2278.9885 | 498.4212 | 465.2559 | 451.8236
2279.9885 | 497.3864 | 464.8476 | 452.4289
2280.9885 | 497.8364 | 464.8287 | 452.3743
2281.9885 | 497.2563 | 464.8548 | 452.3264
2282.9885 | 497.1722 | 464.8975 | 452.2516
2283.9885 | 497.6626 | 465.6654 | 451.815
2284.9885 | 498.1693 | 465.9313 | 451.2999
2285.9885 | 498.3386 | 465.6282 | 451.132
2286.9885 | 498.4138 | 465.1894 | 450.992
2287.9885 | 499.8183 | 464.7068 | 451.3128
2288.9885 | 500.0193 | 465.4567 | 451.7032
2289.9885 | 500.9218 | 466.1425 | 451.6692
2290.9885 | 501.1433 | 465.8156 | 451.9583
2291.9885 | 501.6407 | 466.0657 | 451.7509
2292.9885 | 502.3932 | 467.1925 | 451.6989
2293.9885 | 503.102 | 468.1869 | 452.2926
2294.9885 | 503.096 | 468.4242 | 453.191
2295.9885 | 503.6167 | 468.5655 | 453.4568
2296.9885 | 503.5572 | 468.4292 | 453.6703
2297.9885 | 504.0481 | 468.7015 | 454.4877
2298.9885 | 504.7271 | 469.335 | 454.4909
2299.9885 | 505.5819 | 470.1467 | 454.8386
2300.9885 | 505.3668 | 470.0711 | 454.851
2301.9885 | 504.7187 | 469.6224 | 454.9474
2302.9885 | 505.6797 | 470.1642 | 454.7365
2303.9885 | 505.9259 | 470.338 | 455.1154
2304.9885 | 505.5289 | 470.3321 | 456.0622
2305.9885 | 505.5154 | 470.4731 | 456.5753
2306.9885 | 506.4138 | 471.0135 | 456.6925
2307.9885 | 506.0221 | 470.3302 | 457.2986
2308.9885 | 506.3834 | 470.8086 | 457.4406
2309.9885 | 506.737 | 470.978 | 456.8344
2310.9885 | 507.951 | 471.7714 | 457.2072
2311.9885 | 507.9852 | 471.5204 | 457.6322
2312.9885 | 507.572 | 471.7411 | 458.6545
2313.9885 | 508.5613 | 472.2052 | 458.4747
2314.9885 | 509.0919 | 471.8438 | 458.2411
2315.9885 | 509.1404 | 471.7175 | 458.6995
2316.9885 | 508.8471 | 471.9947 | 458.5055
2317.9885 | 508.9237 | 472.0795 | 458.3382
2318.9885 | 507.6148 | 471.155 | 458.859
2319.9885 | 508.4678 | 471.4153 | 458.1057
2320.9885 | 508.3822 | 471.0943 | 457.2183
2321.9885 | 508.4793 | 470.599 | 456.9823
2322.9885 | 510.122 | 471.5695 | 457.9988
2323.9885 | 509.1481 | 471.5533 | 457.9539
2324.9885 | 510.1556 | 472.5113 | 458.7062
2325.9885 | 509.6488 | 471.8669 | 458.4407
2326.9885 | 509.6078 | 471.7831 | 458.2238
2327.9885 | 510.724 | 472.4147 | 458.0719
2328.9885 | 510.17 | 471.4877 | 458.5026
2329.9885 | 511.9755 | 472.922 | 458.3965
2330.9885 | 513.6883 | 474.4101 | 458.6816
2331.9885 | 514.2097 | 474.8434 | 458.7021
2332.9885 | 515.1702 | 476.8744 | 459.6814
2333.9885 | 513.5584 | 475.6474 | 459.3277
2334.9885 | 512.8146 | 474.9849 | 458.7759
2335.9885 | 513.7809 | 475.3466 | 458.5022
2336.9885 | 512.9795 | 474.8856 | 458.8295
2337.9885 | 513.9723 | 475.997 | 459.2078
2338.9885 | 515.5805 | 476.6908 | 459.5188
2339.9885 | 515.0344 | 476.0448 | 459.9384
2340.9885 | 514.7434 | 475.4351 | 460.7898
2341.9885 | 514.0944 | 474.8101 | 460.4517
2342.9885 | 515.3245 | 475.1645 | 460.4176
2343.9885 | 516.6087 | 475.2884 | 460.0947
2344.9885 | 516.1894 | 474.8459 | 460.225
2345.9885 | 515.6083 | 474.9552 | 460.4283
2346.9885 | 514.9539 | 474.5993 | 460.9174
2347.9885 | 515.7525 | 475.092 | 460.5309
2348.9885 | 516.6056 | 476.0834 | 460.9855
2349.9885 | 517.8405 | 478.0187 | 461.1438
2350.9885 | 518.1455 | 478.5207 | 461.8115
2351.9885 | 517.3829 | 477.7592 | 462.3807
2352.9885 | 518.1885 | 478.0513 | 462.4662
2353.9885 | 519.6424 | 479.5342 | 462.9719
2354.9885 | 519.8287 | 480.5652 | 463.928
2355.9885 | 518.6668 | 480.1569 | 463.7704
2356.9885 | 518.8843 | 480.3276 | 464.349
2357.9885 | 519.6343 | 480.7091 | 465.1163
2358.9885 | 518.0364 | 479.5267 | 465.333
2359.9885 | 517.6885 | 478.9565 | 465.069
2360.9885 | 519.5482 | 480.3354 | 465.4146
2361.9885 | 519.5244 | 480.1698 | 465.6362
2362.9885 | 520.8683 | 481.6689 | 466.0372
2363.9885 | 521.0148 | 482.0759 | 467.0412
2364.9885 | 520.7073 | 482.4233 | 467.4043
2365.9885 | 519.6915 | 481.6346 | 467.4351
2366.9885 | 519.9514 | 481.4592 | 466.7662
2367.9885 | 519.4079 | 481.1048 | 467.2424
2368.9885 | 520.0644 | 481.2121 | 467.5484
2369.9885 | 518.8408 | 479.9416 | 467.126
2370.9885 | 520.2264 | 481.0994 | 467.294
2371.9885 | 521.2594 | 481.8348 | 468.3032
2372.9885 | 522.2543 | 482.6214 | 468.7
2373.9885 | 521.8128 | 482.8938 | 468.9366
2374.9885 | 520.6927 | 482.0189 | 468.7556
2375.9885 | 520.4065 | 481.8886 | 468.9025
2376.9885 | 521.7574 | 482.8365 | 469.6328
2377.9885 | 521.8611 | 482.832 | 469.5086
2378.9885 | 521.7496 | 482.9978 | 469.8682
2379.9885 | 523.8168 | 484.2585 | 469.9818
2380.9885 | 524.2106 | 485.334 | 470.8738
2381.9885 | 524.2647 | 485.5752 | 470.6912
2382.9885 | 523.3538 | 484.9499 | 470.25
2383.9885 | 525.1548 | 486.6184 | 470.8138
2384.9885 | 524.0238 | 486.4888 | 471.1772
2385.9885 | 524.0393 | 487.5143 | 471.3205
2386.9885 | 523.8544 | 487.2136 | 470.8148
2387.9885 | 524.2591 | 487.5081 | 470.5555
2388.9885 | 523.356 | 486.8913 | 470.9317
2389.9885 | 523.9192 | 487.6702 | 471.455
2390.9885 | 524.185 | 487.6236 | 471.815
2391.9885 | 523.4193 | 486.9096 | 471.1557
2392.9885 | 523.774 | 486.6878 | 470.4531
2393.9885 | 524.8461 | 486.8342 | 470.6381
2394.9885 | 525.4344 | 486.926 | 471.3845
2395.9885 | 526.3831 | 487.9715 | 471.9161
2396.9885 | 525.9459 | 487.9078 | 471.6476
2397.9885 | 525.4882 | 487.6764 | 472.0592
2398.9885 | 524.2559 | 486.8407 | 471.7966
2399.9885 | 524.6744 | 487.1858 | 471.4824
2400.9885 | 524.6348 | 487.6222 | 470.6668
2401.9885 | 525.2273 | 488.5944 | 471.753
2402.9885 | 525.0635 | 489.0539 | 471.5986
2403.9885 | 525.6495 | 489.6067 | 471.8392
2404.9885 | 524.4785 | 489.039 | 472.5971
2405.9885 | 525.0557 | 489.483 | 473.1759
2406.9885 | 524.8992 | 489.5482 | 473.1193
2407.9885 | 524.7059 | 489.632 | 473.391
2408.9885 | 524.9131 | 489.3158 | 473.5039
2409.9885 | 524.9087 | 490.2687 | 475.4725
2410.9885 | 525.0975 | 490.9838 | 475.3561
2411.9885 | 525.8904 | 491.2514 | 476.0091
2412.9885 | 524.876 | 491.2645 | 475.581
2413.9885 | 524.909 | 491.1716 | 475.0862
2414.9885 | 525.459 | 491.9735 | 475.5378
2415.9885 | 526.0165 | 491.9845 | 475.3809
2416.9885 | 524.6774 | 490.6279 | 476.0097
2417.9885 | 526.3233 | 491.4991 | 476.3253
2418.9885 | 526.998 | 491.7239 | 476.426
2419.9885 | 526.5227 | 491.4288 | 476.0055
2420.9885 | 527.2948 | 491.5212 | 475.9415
2421.9885 | 526.8435 | 490.7849 | 475.9431
2422.9885 | 525.5263 | 489.0496 | 475.119
2423.9885 | 525.8198 | 489.1708 | 475.4382
2424.9885 | 526.4456 | 490.1092 | 476.8598
2425.9885 | 526.5347 | 490.1647 | 476.871
2426.9885 | 526.3048 | 490.265 | 476.3609
2427.9885 | 526.9509 | 490.5948 | 475.7447
2428.9885 | 527.0482 | 490.3382 | 475.4418
2429.9885 | 526.5824 | 489.8156 | 475.2829
2430.9885 | 526.8503 | 489.356 | 475.3162
2431.9885 | 527.6873 | 489.6161 | 475.2679
2432.9885 | 527.697 | 490.254 | 476.2044
2433.9885 | 527.8014 | 490.5419 | 477.7908
2434.9885 | 527.6901 | 491.2733 | 477.1938
2435.9885 | 528.6349 | 492.2759 | 476.7906
2436.9885 | 527.1679 | 491.5023 | 477.1265
2437.9885 | 526.8836 | 490.8181 | 476.5024
2438.9885 | 526.6088 | 491.0788 | 476.7602
2439.9885 | 526.4395 | 490.8211 | 476.9993
2440.9885 | 527.0347 | 491.2017 | 477.1232
2441.9885 | 527.2366 | 490.7776 | 476.7463
2442.9885 | 526.7944 | 490.9199 | 476.5781
2443.9885 | 526.6275 | 490.8506 | 476.3313
2444.9885 | 527.4842 | 491.7758 | 475.9955
2445.9885 | 529.1057 | 492.3989 | 476.1031
2446.9885 | 528.2053 | 492.6016 | 477.4965
2447.9885 | 529.0946 | 492.957 | 477.6628
2448.9885 | 528.0795 | 492.7593 | 477.2976
2449.9885 | 529.4429 | 493.8558 | 477.2813
2450.9885 | 530.262 | 494.062 | 478.2102
2451.9885 | 529.5549 | 493.6369 | 477.5071
2452.9885 | 528.492 | 492.3717 | 477.0323
2453.9885 | 530.3127 | 493.1273 | 477.6905
2454.9885 | 528.1961 | 491.8099 | 477.99
2455.9885 | 528.9624 | 492.0618 | 478.2597
2456.9885 | 528.5469 | 492.2658 | 477.7998
2457.9885 | 529.1851 | 492.6013 | 477.8635
2458.9885 | 529.7145 | 493.0199 | 478.039
2459.9885 | 528.934 | 492.433 | 477.6744
2460.9885 | 529.0904 | 492.4774 | 477.8467
2461.9885 | 532.295 | 493.7017 | 479.2829
2462.9885 | 531.9524 | 493.6203 | 479.4727
2463.9885 | 532.1951 | 494.0237 | 480.3436
2464.9885 | 533.0581 | 495.0845 | 479.7171
2465.9885 | 532.43 | 495.7763 | 479.6582
2466.9885 | 530.3538 | 494.4048 | 479.4709
2467.9885 | 529.4948 | 493.911 | 478.8973
2468.9885 | 530.547 | 493.3949 | 479.4025
2469.9885 | 530.6082 | 493.7991 | 480.1459
2470.9885 | 531.3682 | 493.7963 | 480.6007
2471.9885 | 531.9863 | 493.2433 | 480.1847
2472.9885 | 532.4835 | 493.9161 | 480.5846
2473.9885 | 532.0793 | 493.7305 | 480.4711
2474.9885 | 530.7406 | 492.4607 | 480.5873
2475.9885 | 532.3073 | 493.4534 | 480.0161
2476.9885 | 533.1913 | 493.3997 | 480.3039
2477.9885 | 532.7474 | 493.4177 | 480.3576
2478.9885 | 533.6705 | 493.7302 | 480.5931
2479.9885 | 532.3379 | 493.0427 | 480.2188
2480.9885 | 530.9696 | 492.6124 | 480.638
2481.9885 | 531.6522 | 492.9552 | 480.5913
2482.9885 | 531.6817 | 492.8192 | 480.7212
2483.9885 | 530.5912 | 493.0185 | 481.8097
2484.9885 | 530.2725 | 492.8606 | 481.6245
2485.9885 | 530.0961 | 492.8725 | 482.8963
2486.9885 | 530.1646 | 492.9097 | 482.9026
2487.9885 | 530.7205 | 493.5012 | 482.8064
2488.9885 | 531.4273 | 493.4009 | 483.2133
2489.9885 | 529.8285 | 492.6538 | 483.2508
2490.9885 | 528.3725 | 491.6862 | 482.739
2491.9885 | 528.8552 | 492.1218 | 482.5382
2492.9885 | 530.9245 | 492.7861 | 482.8124
2493.9885 | 532.2087 | 493.6898 | 482.6908
2494.9885 | 531.3596 | 492.9437 | 482.7731
2495.9885 | 530.1749 | 492.4526 | 482.585