## Test Conditions
DESIREE-FIRE Intermediate Scale Test 10 - Circuit Simulator Data Only
Test Date: | 2010-03-25
DCSim DAQ Start Time | 10:11
DCSim Time for Synchronization | 10:40
Heat Source Synchronization | 0:00 | hours:minutes:seconds
Heat Source DAQ Start Time | 10:40
Fire Time | 11:27
Offset | 1:16 | hours:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 4560 | seconds
Heat Source Offset | 0:47 | hours:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 2811 | seconds
Heat Source Stop Time | 12:33
Test Duration | 1:06 | hours:minutes:seconds
| 3960 | seconds
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
Intercable Configuration | EPR/CPE, 7c, 12AWG |  | Cable thermocouples were not used in this test. | Channel 0 represented as "A Position - Middle" in the Temperature Data File is monitoring the air temperature in the middle of the tray at A Position.
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds.
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | Int-Cab_VT7-T1 | Int-Cab_VT7-T2 | Int-Cab_VT7-T3 | Int-Cab_VT7-T4 | Int-Cab_VT7-T5 | Int-Cab_VT7-T6 | Int-Cab_VT7-T7 | Int-Cab_VTU-S1+a | Int-Cab_VTU-S1+b | Int-Cab_VTU-S2+a | Int-Cab_VTU-S2+b | Int-Cab_VTU-S1-a | Int-Cab_VTU-S1-b | Int-Cab_VTU-S2-a | Int-Cab_VTU-S2-b | T1-V(Batt -) | T2 -V(Batt -) | T3 - V(Batt -) | T4 - V(Batt -) | T5 - V(Batt -) | T6 - V(Batt -) | T7 - V(Batt -) | {S1+a} - V(Batt - ) | {S1+b} - V(Batt - ) | {S2+a} - V(Batt - ) | {S2+b} - V(Batt - ) | {S1-a} - V(Batt -) | {S1-b} - V(Batt - ) | {S2-a} - V(Batt - ) | {S2-b} - V(Batt - ) | {S1+a} - {S1-a} | {S1+a} - {S2-a} | {S2+a} - {S1-a} | {S2+a} - {S2-a}
-1.2812 | 121.9574 | -61.0931 | 60.498 | 0.098959 | -0.017627 | 0.033786 | -0.034174 | 0.06831 | 0.058113 | -0.099343 | 60.2597 | 60.3319 | 60.3192 | 60.2773 | 61.2035 | 61.1953 | 60.9003 | 61.1154 | 0.14474 | 0.028149 | 0.079562 | 0.011602 | 0.11409 | 0.10389 | -0.053567 | 60.3055 | 60.3776 | 60.365 | 60.3231 | 61.2492 | 61.2411 | 60.9461 | 61.1612 | -0.94377 | -0.64058 | -0.88427 | -0.58108
0.46875 | 121.8567 | -61.1664 | 60.5072 | 0.098959 | -0.013048 | 0.038365 | -0.038752 | 0.077466 | 0.058113 | -0.10392 | 60.2597 | 60.3319 | 60.3238 | 60.2773 | 61.2035 | 61.1862 | 60.9049 | 61.12 | 0.14474 | 0.032728 | 0.084141 | 0.007024 | 0.12324 | 0.10389 | -0.058145 | 60.3055 | 60.3776 | 60.3696 | 60.3231 | 61.2492 | 61.232 | 60.9506 | 61.1658 | -0.94377 | -0.64516 | -0.87969 | -0.58107
2.2188 | 121.907 | -61.0977 | 60.5301 | 0.098959 | -0.00389 | 0.042944 | -0.038752 | 0.06831 | 0.053534 | -0.099343 | 60.2597 | 60.3227 | 60.3192 | 60.2819 | 61.2081 | 61.1908 | 60.9003 | 61.1154 | 0.14474 | 0.041886 | 0.08872 | 0.007024 | 0.11409 | 0.09931 | -0.053567 | 60.3055 | 60.3685 | 60.365 | 60.3277 | 61.2538 | 61.2365 | 60.9461 | 61.1612 | -0.94835 | -0.64058 | -0.88885 | -0.58108
3.9844 | 121.9666 | -61.0794 | 60.4935 | 0.10354 | -0.013048 | 0.038365 | -0.038752 | 0.06831 | 0.053534 | -0.10392 | 60.2597 | 60.3273 | 60.3284 | 60.2773 | 61.2035 | 61.1862 | 60.9003 | 61.1154 | 0.14931 | 0.032728 | 0.084141 | 0.007024 | 0.11409 | 0.09931 | -0.058145 | 60.3055 | 60.3731 | 60.3741 | 60.3231 | 61.2492 | 61.232 | 60.9461 | 61.1612 | -0.94377 | -0.64058 | -0.87511 | -0.57192
5.6719 | 121.9666 | -61.0748 | 60.5118 | 0.094381 | -0.008469 | 0.038365 | -0.029595 | 0.072888 | 0.053534 | -0.099343 | 60.2597 | 60.3273 | 60.3192 | 60.2727 | 61.1943 | 61.1953 | 60.9049 | 61.1154 | 0.14016 | 0.037307 | 0.084141 | 0.016181 | 0.11866 | 0.09931 | -0.053567 | 60.3055 | 60.3731 | 60.365 | 60.3185 | 61.2401 | 61.2411 | 60.9506 | 61.1612 | -0.93462 | -0.64516 | -0.87511 | -0.58565
7.3438 | 121.8338 | -61.1114 | 60.5713 | 0.094381 | -0.008469 | 0.047522 | -0.034174 | 0.072888 | 0.058113 | -0.099343 | 60.2597 | 60.3273 | 60.3146 | 60.2727 | 61.1943 | 61.1908 | 60.9003 | 61.12 | 0.14016 | 0.037307 | 0.093298 | 0.011602 | 0.11866 | 0.10389 | -0.053567 | 60.3055 | 60.3731 | 60.3604 | 60.3185 | 61.2401 | 61.2365 | 60.9461 | 61.1658 | -0.93462 | -0.64058 | -0.87969 | -0.58565
9.0312 | 121.8018 | -61.1664 | 60.5072 | 0.098959 | -0.008469 | 0.033786 | -0.034174 | 0.082044 | 0.058113 | -0.090186 | 60.2597 | 60.3365 | 60.3238 | 60.2727 | 61.1989 | 61.1908 | 60.9003 | 61.1109 | 0.14474 | 0.037307 | 0.079562 | 0.011602 | 0.12782 | 0.10389 | -0.04441 | 60.3055 | 60.3822 | 60.3696 | 60.3185 | 61.2447 | 61.2365 | 60.9461 | 61.1566 | -0.93919 | -0.64058 | -0.87511 | -0.5765
10.7188 | 121.9162 | -61.1343 | 60.4202 | 0.10354 | -0.008469 | 0.033786 | -0.038752 | 0.072888 | 0.053534 | -0.094765 | 60.2505 | 60.3273 | 60.3238 | 60.2819 | 61.2035 | 61.1908 | 60.9049 | 61.1109 | 0.14931 | 0.037307 | 0.079562 | 0.007024 | 0.11866 | 0.09931 | -0.048989 | 60.2963 | 60.3731 | 60.3696 | 60.3277 | 61.2492 | 61.2365 | 60.9506 | 61.1566 | -0.95293 | -0.65431 | -0.87969 | -0.58107
12.4531 | 121.9299 | -61.1664 | 60.4248 | 0.098959 | -0.013048 | 0.038365 | -0.043331 | 0.072888 | 0.058113 | -0.094765 | 60.2643 | 60.3319 | 60.3146 | 60.2773 | 61.1989 | 61.1908 | 60.9003 | 61.1154 | 0.14474 | 0.032728 | 0.084141 | 0.002445 | 0.11866 | 0.10389 | -0.048989 | 60.3101 | 60.3776 | 60.3604 | 60.3231 | 61.2447 | 61.2365 | 60.9461 | 61.1612 | -0.93462 | -0.636 | -0.88427 | -0.58565
14.1406 | 121.9482 | -61.1206 | 60.4477 | 0.10354 | -0.008469 | 0.042944 | -0.034174 | 0.06831 | 0.048956 | -0.090186 | 60.2643 | 60.3273 | 60.3146 | 60.2727 | 61.1989 | 61.1908 | 60.9049 | 61.1109 | 0.14931 | 0.037307 | 0.08872 | 0.011602 | 0.11409 | 0.094732 | -0.04441 | 60.3101 | 60.3731 | 60.3604 | 60.3185 | 61.2447 | 61.2365 | 60.9506 | 61.1566 | -0.93462 | -0.64058 | -0.88427 | -0.59023
15.8125 | 121.8018 | -61.116 | 60.5576 | 0.089802 | -0.008469 | 0.047522 | -0.034174 | 0.06831 | 0.058113 | -0.094765 | 60.2505 | 60.3227 | 60.3192 | 60.2773 | 61.1989 | 61.1862 | 60.8911 | 61.1063 | 0.13558 | 0.037307 | 0.093298 | 0.011602 | 0.11409 | 0.10389 | -0.048989 | 60.2963 | 60.3685 | 60.365 | 60.3231 | 61.2447 | 61.232 | 60.9369 | 61.1521 | -0.94835 | -0.64058 | -0.87969 | -0.57192
17.4844 | 121.8887 | -61.1389 | 60.4797 | 0.10354 | -0.022205 | 0.038365 | -0.034174 | 0.077466 | 0.053534 | -0.11308 | 60.2643 | 60.3273 | 60.31 | 60.2727 | 61.1943 | 61.177 | 60.9003 | 61.12 | 0.14931 | 0.023571 | 0.084141 | 0.011602 | 0.12324 | 0.09931 | -0.067301 | 60.3101 | 60.3731 | 60.3558 | 60.3185 | 61.2401 | 61.2228 | 60.9461 | 61.1658 | -0.93004 | -0.636 | -0.88427 | -0.59023
19.1719 | 121.9254 | -61.0886 | 60.5164 | 0.10354 | -0.017627 | 0.042944 | -0.034174 | 0.072888 | 0.053534 | -0.1085 | 60.2551 | 60.3273 | 60.3146 | 60.2682 | 61.2035 | 61.1816 | 60.9003 | 61.12 | 0.14931 | 0.028149 | 0.08872 | 0.011602 | 0.11866 | 0.09931 | -0.062723 | 60.3009 | 60.3731 | 60.3604 | 60.3139 | 61.2492 | 61.2274 | 60.9461 | 61.1658 | -0.94835 | -0.64516 | -0.88885 | -0.58565
20.9219 | 121.9025 | -61.1481 | 60.4706 | 0.098959 | -0.017627 | 0.038365 | -0.038752 | 0.06831 | 0.058113 | -0.094765 | 60.2505 | 60.3227 | 60.31 | 60.2819 | 61.2035 | 61.1816 | 60.8911 | 61.1109 | 0.14474 | 0.028149 | 0.084141 | 0.007024 | 0.11409 | 0.10389 | -0.048989 | 60.2963 | 60.3685 | 60.3558 | 60.3277 | 61.2492 | 61.2274 | 60.9369 | 61.1566 | -0.95293 | -0.64058 | -0.89343 | -0.58107
22.6094 | 121.8842 | -61.1298 | 60.4385 | 0.098959 | -0.017627 | 0.042944 | -0.038752 | 0.077466 | 0.058113 | -0.099343 | 60.2505 | 60.3273 | 60.3146 | 60.2727 | 61.1989 | 61.1862 | 60.8957 | 61.1063 | 0.14474 | 0.028149 | 0.08872 | 0.007024 | 0.12324 | 0.10389 | -0.053567 | 60.2963 | 60.3731 | 60.3604 | 60.3185 | 61.2447 | 61.232 | 60.9415 | 61.1521 | -0.94835 | -0.64516 | -0.88427 | -0.58107
24.3594 | 121.8613 | -61.0886 | 60.5392 | 0.094381 | -0.013048 | 0.042944 | -0.043331 | 0.077466 | 0.048956 | -0.094765 | 60.2597 | 60.3227 | 60.31 | 60.259 | 61.1989 | 61.1816 | 60.9003 | 61.1063 | 0.14016 | 0.032728 | 0.08872 | 0.002445 | 0.12324 | 0.094732 | -0.048989 | 60.3055 | 60.3685 | 60.3558 | 60.3048 | 61.2447 | 61.2274 | 60.9461 | 61.1521 | -0.93919 | -0.64058 | -0.88885 | -0.59023
26.0312 | 121.9391 | -61.1435 | 60.4294 | 0.10354 | -0.017627 | 0.042944 | -0.043331 | 0.072888 | 0.053534 | -0.099343 | 60.2505 | 60.3273 | 60.3146 | 60.2727 | 61.1989 | 61.1862 | 60.8957 | 61.1109 | 0.14931 | 0.028149 | 0.08872 | 0.002445 | 0.11866 | 0.09931 | -0.053567 | 60.2963 | 60.3731 | 60.3604 | 60.3185 | 61.2447 | 61.232 | 60.9415 | 61.1566 | -0.94835 | -0.64516 | -0.88427 | -0.58107
27.7188 | 121.9116 | -61.1252 | 60.4706 | 0.094381 | -0.013048 | 0.038365 | -0.038752 | 0.072888 | 0.048956 | -0.099343 | 60.2505 | 60.3181 | 60.3146 | 60.2682 | 61.1989 | 61.1862 | 60.9003 | 61.12 | 0.14016 | 0.032728 | 0.084141 | 0.007024 | 0.11866 | 0.094732 | -0.053567 | 60.2963 | 60.3639 | 60.3604 | 60.3139 | 61.2447 | 61.232 | 60.9461 | 61.1658 | -0.94835 | -0.64974 | -0.88427 | -0.58565
29.4688 | 121.8475 | -61.116 | 60.5118 | 0.10354 | -0.017627 | 0.038365 | -0.043331 | 0.063733 | 0.053534 | -0.085608 | 60.2551 | 60.3227 | 60.3146 | 60.2727 | 61.1897 | 61.1816 | 60.8957 | 61.1154 | 0.14931 | 0.028149 | 0.084141 | 0.002445 | 0.10951 | 0.09931 | -0.039832 | 60.3009 | 60.3685 | 60.3604 | 60.3185 | 61.2355 | 61.2274 | 60.9415 | 61.1612 | -0.93462 | -0.64058 | -0.87511 | -0.58107
31.1562 | 121.9482 | -61.1389 | 60.3836 | 0.10354 | -0.00389 | 0.047522 | -0.034174 | 0.072888 | 0.053534 | -0.094765 | 60.2597 | 60.3227 | 60.3146 | 60.2727 | 61.2035 | 61.1862 | 60.8911 | 61.1063 | 0.14931 | 0.041886 | 0.093298 | 0.011602 | 0.11866 | 0.09931 | -0.048989 | 60.3055 | 60.3685 | 60.3604 | 60.3185 | 61.2492 | 61.232 | 60.9369 | 61.1521 | -0.94377 | -0.63142 | -0.88885 | -0.5765
32.8438 | 121.788 | -61.1664 | 60.4843 | 0.10354 | -0.013048 | 0.038365 | -0.034174 | 0.072888 | 0.053534 | -0.090186 | 60.246 | 60.3136 | 60.3146 | 60.2636 | 61.1943 | 61.1816 | 60.8865 | 61.1063 | 0.14931 | 0.032728 | 0.084141 | 0.011602 | 0.11866 | 0.09931 | -0.04441 | 60.2917 | 60.3593 | 60.3604 | 60.3094 | 61.2401 | 61.2274 | 60.9323 | 61.1521 | -0.94835 | -0.64058 | -0.87969 | -0.57192
34.5312 | 121.788 | -61.1664 | 60.4752 | 0.10354 | -0.017627 | 0.042944 | -0.034174 | 0.072888 | 0.048956 | -0.10392 | 60.2505 | 60.3227 | 60.3146 | 60.2727 | 61.1852 | 61.1908 | 60.8911 | 61.1017 | 0.14931 | 0.028149 | 0.08872 | 0.011602 | 0.11866 | 0.094732 | -0.058145 | 60.2963 | 60.3685 | 60.3604 | 60.3185 | 61.2309 | 61.2365 | 60.9369 | 61.1475 | -0.93462 | -0.64058 | -0.87053 | -0.5765
36.2188 | 121.7789 | -61.1114 | 60.5759 | 0.089802 | -0.008469 | 0.038365 | -0.038752 | 0.06831 | 0.062691 | -0.099343 | 60.2551 | 60.3181 | 60.31 | 60.2682 | 61.1989 | 61.177 | 60.8911 | 61.1109 | 0.13558 | 0.037307 | 0.084141 | 0.007024 | 0.11409 | 0.10847 | -0.053567 | 60.3009 | 60.3639 | 60.3558 | 60.3139 | 61.2447 | 61.2228 | 60.9369 | 61.1566 | -0.94377 | -0.636 | -0.88885 | -0.58107
37.9844 | 121.8613 | -61.1114 | 60.4889 | 0.094381 | -0.022205 | 0.042944 | -0.038752 | 0.072888 | 0.053534 | -0.10392 | 60.2551 | 60.3136 | 60.3146 | 60.2682 | 61.1852 | 61.177 | 60.8957 | 61.1017 | 0.14016 | 0.023571 | 0.08872 | 0.007024 | 0.11866 | 0.09931 | -0.058145 | 60.3009 | 60.3593 | 60.3604 | 60.3139 | 61.2309 | 61.2228 | 60.9415 | 61.1475 | -0.93004 | -0.64058 | -0.87053 | -0.58107
39.7344 | 121.9299 | -61.0886 | 60.5072 | 0.098959 | -0.017627 | 0.042944 | -0.043331 | 0.077466 | 0.048956 | -0.085608 | 60.246 | 60.3136 | 60.31 | 60.2682 | 61.1989 | 61.1862 | 60.8911 | 61.1063 | 0.14474 | 0.028149 | 0.08872 | 0.002445 | 0.12324 | 0.094732 | -0.039832 | 60.2917 | 60.3593 | 60.3558 | 60.3139 | 61.2447 | 61.232 | 60.9369 | 61.1521 | -0.95293 | -0.64516 | -0.88885 | -0.58107
41.4062 | 121.843 | -61.1343 | 60.4935 | 0.098959 | -0.017627 | 0.042944 | -0.034174 | 0.06831 | 0.053534 | -0.094765 | 60.2505 | 60.3181 | 60.3146 | 60.2682 | 61.1897 | 61.177 | 60.882 | 61.1017 | 0.14474 | 0.028149 | 0.08872 | 0.011602 | 0.11409 | 0.09931 | -0.048989 | 60.2963 | 60.3639 | 60.3604 | 60.3139 | 61.2355 | 61.2228 | 60.9277 | 61.1475 | -0.9392 | -0.63142 | -0.87511 | -0.56734
43.1719 | 121.9482 | -61.0474 | 60.498 | 0.094381 | -0.008469 | 0.047522 | -0.043331 | 0.077466 | 0.058113 | -0.094765 | 60.2505 | 60.3181 | 60.3146 | 60.2682 | 61.1852 | 61.1816 | 60.8865 | 61.0971 | 0.14016 | 0.037307 | 0.093298 | 0.002445 | 0.12324 | 0.10389 | -0.048989 | 60.2963 | 60.3639 | 60.3604 | 60.3139 | 61.2309 | 61.2274 | 60.9323 | 61.1429 | -0.93462 | -0.636 | -0.87053 | -0.57192
44.9375 | 121.843 | -61.1343 | 60.4889 | 0.10354 | -0.008469 | 0.042944 | -0.034174 | 0.072888 | 0.058113 | -0.094765 | 60.2505 | 60.3227 | 60.3146 | 60.2727 | 61.1989 | 61.177 | 60.8911 | 61.1109 | 0.14931 | 0.037307 | 0.08872 | 0.011602 | 0.11866 | 0.10389 | -0.048989 | 60.2963 | 60.3685 | 60.3604 | 60.3185 | 61.2447 | 61.2228 | 60.9369 | 61.1566 | -0.94835 | -0.64058 | -0.88427 | -0.5765
46.625 | 121.8109 | -61.1389 | 60.4706 | 0.10354 | -0.017627 | 0.038365 | -0.034174 | 0.077466 | 0.053534 | -0.090186 | 60.246 | 60.3181 | 60.31 | 60.2636 | 61.1897 | 61.1724 | 60.8865 | 61.1017 | 0.14931 | 0.028149 | 0.084141 | 0.011602 | 0.12324 | 0.09931 | -0.04441 | 60.2917 | 60.3639 | 60.3558 | 60.3094 | 61.2355 | 61.2182 | 60.9323 | 61.1475 | -0.94378 | -0.64058 | -0.87969 | -0.5765
48.3594 | 121.9254 | -61.084 | 60.5026 | 0.094381 | -0.017627 | 0.038365 | -0.029595 | 0.072888 | 0.053534 | -0.094765 | 60.246 | 60.3181 | 60.3009 | 60.2727 | 61.1943 | 61.177 | 60.8957 | 61.1017 | 0.14016 | 0.028149 | 0.084141 | 0.016181 | 0.11866 | 0.09931 | -0.048989 | 60.2917 | 60.3639 | 60.3467 | 60.3185 | 61.2401 | 61.2228 | 60.9415 | 61.1475 | -0.94835 | -0.64974 | -0.89343 | -0.59481
50.0625 | 121.7697 | -61.1664 | 60.4843 | 0.094381 | -0.008469 | 0.052101 | -0.034174 | 0.077466 | 0.058113 | -0.094765 | 60.2551 | 60.3181 | 60.31 | 60.2682 | 61.1897 | 61.177 | 60.8865 | 61.1017 | 0.14016 | 0.037307 | 0.097877 | 0.011602 | 0.12324 | 0.10389 | -0.048989 | 60.3009 | 60.3639 | 60.3558 | 60.3139 | 61.2355 | 61.2228 | 60.9323 | 61.1475 | -0.93462 | -0.63142 | -0.87969 | -0.5765
51.7969 | 121.8796 | -61.1343 | 60.4385 | 0.094381 | -0.013048 | 0.047522 | -0.043331 | 0.077466 | 0.048956 | -0.10392 | 60.2505 | 60.3181 | 60.3055 | 60.2682 | 61.1897 | 61.1862 | 60.882 | 61.1017 | 0.14016 | 0.032728 | 0.093298 | 0.002445 | 0.12324 | 0.094732 | -0.058145 | 60.2963 | 60.3639 | 60.3512 | 60.3139 | 61.2355 | 61.232 | 60.9277 | 61.1475 | -0.9392 | -0.63142 | -0.88427 | -0.5765
53.4688 | 121.8063 | -61.1755 | 60.4752 | 0.10354 | -0.017627 | 0.042944 | -0.034174 | 0.077466 | 0.058113 | -0.094765 | 60.2551 | 60.3136 | 60.3055 | 60.2682 | 61.1852 | 61.177 | 60.8865 | 61.1017 | 0.14931 | 0.028149 | 0.08872 | 0.011602 | 0.12324 | 0.10389 | -0.048989 | 60.3009 | 60.3593 | 60.3512 | 60.3139 | 61.2309 | 61.2228 | 60.9323 | 61.1475 | -0.93004 | -0.63142 | -0.87969 | -0.58107
55.25 | 121.9162 | -61.1069 | 60.4752 | 0.094381 | -0.022205 | 0.047522 | -0.034174 | 0.077466 | 0.053534 | -0.10392 | 60.246 | 60.3181 | 60.3055 | 60.2636 | 61.1852 | 61.1862 | 60.882 | 61.0971 | 0.14016 | 0.023571 | 0.093298 | 0.011602 | 0.12324 | 0.09931 | -0.058145 | 60.2917 | 60.3639 | 60.3512 | 60.3094 | 61.2309 | 61.232 | 60.9277 | 61.1429 | -0.9392 | -0.636 | -0.87969 | -0.5765
57 | 121.9162 | -61.1618 | 60.4156 | 0.089802 | -0.017627 | 0.038365 | -0.043331 | 0.077466 | 0.058113 | -0.094765 | 60.246 | 60.3181 | 60.3009 | 60.2636 | 61.1806 | 61.177 | 60.8774 | 61.1017 | 0.13558 | 0.028149 | 0.084141 | 0.002445 | 0.12324 | 0.10389 | -0.048989 | 60.2917 | 60.3639 | 60.3467 | 60.3094 | 61.2264 | 61.2228 | 60.9232 | 61.1475 | -0.93462 | -0.63142 | -0.87969 | -0.5765
58.6875 | 121.8887 | -61.1389 | 60.4156 | 0.10354 | -0.013048 | 0.047522 | -0.034174 | 0.077466 | 0.053534 | -0.099343 | 60.246 | 60.3044 | 60.31 | 60.259 | 61.1897 | 61.1724 | 60.8774 | 61.1063 | 0.14931 | 0.032728 | 0.093298 | 0.011602 | 0.12324 | 0.09931 | -0.053567 | 60.2917 | 60.3502 | 60.3558 | 60.3048 | 61.2355 | 61.2182 | 60.9232 | 61.1521 | -0.94378 | -0.63142 | -0.87969 | -0.56734
60.4375 | 121.8292 | -61.0931 | 60.5347 | 0.10812 | -0.017627 | 0.038365 | -0.047909 | 0.072888 | 0.048956 | -0.094765 | 60.2505 | 60.3181 | 60.3009 | 60.2636 | 61.1852 | 61.1816 | 60.8865 | 61.1017 | 0.15389 | 0.028149 | 0.084141 | -0.002133 | 0.11866 | 0.094732 | -0.048989 | 60.2963 | 60.3639 | 60.3467 | 60.3094 | 61.2309 | 61.2274 | 60.9323 | 61.1475 | -0.93462 | -0.636 | -0.88427 | -0.58565
62.1875 | 121.9208 | -61.0657 | 60.4706 | 0.094381 | -0.013048 | 0.042944 | -0.043331 | 0.082044 | 0.053534 | -0.099343 | 60.246 | 60.3136 | 60.3055 | 60.259 | 61.1897 | 61.177 | 60.882 | 61.1017 | 0.14016 | 0.032728 | 0.08872 | 0.002445 | 0.12782 | 0.09931 | -0.053567 | 60.2917 | 60.3593 | 60.3512 | 60.3048 | 61.2355 | 61.2228 | 60.9277 | 61.1475 | -0.94378 | -0.636 | -0.88427 | -0.5765
63.875 | 121.9208 | -61.1481 | 60.3928 | 0.094381 | -0.008469 | 0.042944 | -0.043331 | 0.072888 | 0.053534 | -0.099343 | 60.2505 | 60.3181 | 60.31 | 60.2636 | 61.1897 | 61.1816 | 60.882 | 61.0971 | 0.14016 | 0.037307 | 0.08872 | 0.002445 | 0.11866 | 0.09931 | -0.053567 | 60.2963 | 60.3639 | 60.3558 | 60.3094 | 61.2355 | 61.2274 | 60.9277 | 61.1429 | -0.9392 | -0.63142 | -0.87969 | -0.57192
65.5625 | 121.8979 | -61.1572 | 60.4156 | 0.089802 | -0.013048 | 0.042944 | -0.038752 | 0.06831 | 0.053534 | -0.099343 | 60.246 | 60.3136 | 60.3009 | 60.2682 | 61.1806 | 61.1724 | 60.882 | 61.0971 | 0.13558 | 0.032728 | 0.08872 | 0.007024 | 0.11409 | 0.09931 | -0.053567 | 60.2917 | 60.3593 | 60.3467 | 60.3139 | 61.2264 | 61.2182 | 60.9277 | 61.1429 | -0.93462 | -0.636 | -0.87969 | -0.58107
67.2344 | 121.9254 | -61.0703 | 60.4706 | 0.098959 | -0.017627 | 0.047522 | -0.038752 | 0.072888 | 0.058113 | -0.099343 | 60.2322 | 60.3136 | 60.3055 | 60.2636 | 61.1852 | 61.177 | 60.882 | 61.0971 | 0.14474 | 0.028149 | 0.093298 | 0.007024 | 0.11866 | 0.10389 | -0.053567 | 60.278 | 60.3593 | 60.3512 | 60.3094 | 61.2309 | 61.2228 | 60.9277 | 61.1429 | -0.95293 | -0.64974 | -0.87969 | -0.5765
68.9219 | 121.9299 | -61.0703 | 60.4752 | 0.10354 | -0.022205 | 0.038365 | -0.038752 | 0.06831 | 0.053534 | -0.099343 | 60.246 | 60.309 | 60.3146 | 60.2636 | 61.1852 | 61.1724 | 60.8774 | 61.0971 | 0.14931 | 0.023571 | 0.084141 | 0.007024 | 0.11409 | 0.09931 | -0.053567 | 60.2917 | 60.3548 | 60.3604 | 60.3094 | 61.2309 | 61.2182 | 60.9232 | 61.1429 | -0.9392 | -0.63142 | -0.87053 | -0.56276
70.6719 | 121.9116 | -61.0519 | 60.4843 | 0.098959 | -0.022205 | 0.042944 | -0.043331 | 0.077466 | 0.053534 | -0.094765 | 60.2368 | 60.3044 | 60.3055 | 60.2636 | 61.1852 | 61.1724 | 60.882 | 61.0971 | 0.14474 | 0.023571 | 0.08872 | 0.002445 | 0.12324 | 0.09931 | -0.048989 | 60.2826 | 60.3502 | 60.3512 | 60.3094 | 61.2309 | 61.2182 | 60.9277 | 61.1429 | -0.94835 | -0.64516 | -0.87969 | -0.5765
72.3438 | 121.8292 | -61.1435 | 60.498 | 0.098959 | -0.022205 | 0.038365 | -0.034174 | 0.086622 | 0.053534 | -0.099343 | 60.246 | 60.309 | 60.3055 | 60.2636 | 61.1897 | 61.177 | 60.8774 | 61.0971 | 0.14474 | 0.023571 | 0.084141 | 0.011602 | 0.1324 | 0.09931 | -0.053567 | 60.2917 | 60.3548 | 60.3512 | 60.3094 | 61.2355 | 61.2228 | 60.9232 | 61.1429 | -0.94378 | -0.63142 | -0.88427 | -0.57192
74.0938 | 121.7834 | -61.1023 | 60.5484 | 0.098959 | -0.017627 | 0.047522 | -0.029595 | 0.072888 | 0.053534 | -0.099343 | 60.2414 | 60.309 | 60.3055 | 60.2636 | 61.1852 | 61.1724 | 60.8774 | 61.0926 | 0.14474 | 0.028149 | 0.093298 | 0.016181 | 0.11866 | 0.09931 | -0.053567 | 60.2872 | 60.3548 | 60.3512 | 60.3094 | 61.2309 | 61.2182 | 60.9232 | 61.1383 | -0.94378 | -0.636 | -0.87969 | -0.57192
75.7812 | 121.9299 | -61.0611 | 60.4797 | 0.098959 | -0.017627 | 0.042944 | -0.034174 | 0.06831 | 0.053534 | -0.090186 | 60.246 | 60.309 | 60.3055 | 60.2636 | 61.1897 | 61.1633 | 60.8774 | 61.1017 | 0.14474 | 0.028149 | 0.08872 | 0.011602 | 0.11409 | 0.09931 | -0.04441 | 60.2917 | 60.3548 | 60.3512 | 60.3094 | 61.2355 | 61.2091 | 60.9232 | 61.1475 | -0.94378 | -0.63142 | -0.88427 | -0.57192
77.4688 | 121.7972 | -61.0703 | 60.5576 | 0.10354 | -0.022205 | 0.042944 | -0.034174 | 0.077466 | 0.053534 | -0.094765 | 60.2505 | 60.309 | 60.3009 | 60.2636 | 61.1852 | 61.1724 | 60.8774 | 61.0926 | 0.14931 | 0.023571 | 0.08872 | 0.011602 | 0.12324 | 0.09931 | -0.048989 | 60.2963 | 60.3548 | 60.3467 | 60.3094 | 61.2309 | 61.2182 | 60.9232 | 61.1383 | -0.93462 | -0.62685 | -0.88427 | -0.5765
79.2344 | 121.7972 | -61.1206 | 60.5484 | 0.094381 | -0.026784 | 0.047522 | -0.034174 | 0.06831 | 0.053534 | -0.099343 | 60.246 | 60.2998 | 60.3009 | 60.2636 | 61.1852 | 61.1633 | 60.8682 | 61.0971 | 0.14016 | 0.018992 | 0.093298 | 0.011602 | 0.11409 | 0.09931 | -0.053567 | 60.2917 | 60.3456 | 60.3467 | 60.3094 | 61.2309 | 61.2091 | 60.914 | 61.1429 | -0.9392 | -0.62227 | -0.88427 | -0.56734
80.9375 | 121.7789 | -61.1938 | 60.4614 | 0.098959 | -0.022205 | 0.038365 | -0.029595 | 0.072888 | 0.053534 | -0.094765 | 60.2414 | 60.3136 | 60.3009 | 60.2682 | 61.1806 | 61.1679 | 60.8728 | 61.0926 | 0.14474 | 0.023571 | 0.084141 | 0.016181 | 0.11866 | 0.09931 | -0.048989 | 60.2872 | 60.3593 | 60.3467 | 60.3139 | 61.2264 | 61.2136 | 60.9186 | 61.1383 | -0.9392 | -0.63142 | -0.87969 | -0.57192
82.6875 | 121.7743 | -61.1755 | 60.4385 | 0.098959 | -0.026784 | 0.033786 | -0.029595 | 0.072888 | 0.048956 | -0.094765 | 60.246 | 60.309 | 60.3055 | 60.259 | 61.1852 | 61.1679 | 60.8682 | 61.0926 | 0.14474 | 0.018992 | 0.079562 | 0.016181 | 0.11866 | 0.094732 | -0.048989 | 60.2917 | 60.3548 | 60.3512 | 60.3048 | 61.2309 | 61.2136 | 60.914 | 61.1383 | -0.9392 | -0.62227 | -0.87969 | -0.56276
84.3594 | 121.7926 | -61.1664 | 60.4202 | 0.098959 | -0.022205 | 0.042944 | -0.029595 | 0.077466 | 0.053534 | -0.099343 | 60.246 | 60.309 | 60.3055 | 60.259 | 61.176 | 61.1724 | 60.8774 | 61.0971 | 0.14474 | 0.023571 | 0.08872 | 0.016181 | 0.12324 | 0.09931 | -0.053567 | 60.2917 | 60.3548 | 60.3512 | 60.3048 | 61.2218 | 61.2182 | 60.9232 | 61.1429 | -0.93004 | -0.63142 | -0.87054 | -0.57192
86.0469 | 121.8567 | -61.116 | 60.4431 | 0.098959 | -0.022205 | 0.047522 | -0.038752 | 0.077466 | 0.053534 | -0.099343 | 60.2368 | 60.3044 | 60.3009 | 60.2636 | 61.1806 | 61.1679 | 60.8774 | 61.0971 | 0.14474 | 0.023571 | 0.093298 | 0.007024 | 0.12324 | 0.09931 | -0.053567 | 60.2826 | 60.3502 | 60.3467 | 60.3094 | 61.2264 | 61.2136 | 60.9232 | 61.1429 | -0.94378 | -0.64058 | -0.87969 | -0.5765
87.7344 | 121.9254 | -61.0977 | 60.4843 | 0.094381 | -0.022205 | 0.042944 | -0.034174 | 0.077466 | 0.048956 | -0.094765 | 60.2414 | 60.3044 | 60.2963 | 60.2544 | 61.176 | 61.177 | 60.8728 | 61.0926 | 0.14016 | 0.023571 | 0.08872 | 0.011602 | 0.12324 | 0.094732 | -0.048989 | 60.2872 | 60.3502 | 60.3421 | 60.3002 | 61.2218 | 61.2228 | 60.9186 | 61.1383 | -0.93462 | -0.63142 | -0.87969 | -0.57649
89.4688 | 121.8567 | -61.1618 | 60.4111 | 0.094381 | -0.026784 | 0.047522 | -0.038752 | 0.072888 | 0.053534 | -0.090186 | 60.2414 | 60.3044 | 60.3009 | 60.2682 | 61.176 | 61.1679 | 60.882 | 61.088 | 0.14016 | 0.018992 | 0.093298 | 0.007024 | 0.11866 | 0.09931 | -0.04441 | 60.2872 | 60.3502 | 60.3467 | 60.3139 | 61.2218 | 61.2136 | 60.9277 | 61.1337 | -0.93462 | -0.64058 | -0.87511 | -0.58107
91.25 | 121.8246 | -61.1298 | 60.4248 | 0.098959 | -0.026784 | 0.038365 | -0.029595 | 0.072888 | 0.053534 | -0.094765 | 60.2414 | 60.3044 | 60.2963 | 60.2636 | 61.1806 | 61.1633 | 60.8774 | 61.088 | 0.14474 | 0.018992 | 0.084141 | 0.016181 | 0.11866 | 0.09931 | -0.048989 | 60.2872 | 60.3502 | 60.3421 | 60.3094 | 61.2264 | 61.2091 | 60.9232 | 61.1337 | -0.9392 | -0.636 | -0.88427 | -0.58107
93.0156 | 121.8018 | -61.1114 | 60.466 | 0.10812 | -0.026784 | 0.042944 | -0.029595 | 0.077466 | 0.053534 | -0.099343 | 60.2368 | 60.3044 | 60.3009 | 60.259 | 61.1806 | 61.1679 | 60.8728 | 61.0834 | 0.15389 | 0.018992 | 0.08872 | 0.016181 | 0.12324 | 0.09931 | -0.053567 | 60.2826 | 60.3502 | 60.3467 | 60.3048 | 61.2264 | 61.2136 | 60.9186 | 61.1292 | -0.94378 | -0.636 | -0.87969 | -0.57192
94.7188 | 121.7651 | -61.1801 | 60.4568 | 0.094381 | -0.035942 | 0.042944 | -0.034174 | 0.077466 | 0.053534 | -0.094765 | 60.246 | 60.3044 | 60.3055 | 60.259 | 61.1897 | 61.1633 | 60.8774 | 61.0926 | 0.14016 | 0.009834 | 0.08872 | 0.011602 | 0.12324 | 0.09931 | -0.048989 | 60.2917 | 60.3502 | 60.3512 | 60.3048 | 61.2355 | 61.2091 | 60.9232 | 61.1383 | -0.94378 | -0.63142 | -0.88427 | -0.57192
96.4688 | 121.8155 | -61.1526 | 60.4202 | 0.098959 | -0.022205 | 0.047522 | -0.029595 | 0.072888 | 0.053534 | -0.090186 | 60.2414 | 60.309 | 60.3009 | 60.2636 | 61.176 | 61.1679 | 60.8682 | 61.0971 | 0.14474 | 0.023571 | 0.093298 | 0.016181 | 0.11866 | 0.09931 | -0.04441 | 60.2872 | 60.3548 | 60.3467 | 60.3094 | 61.2218 | 61.2136 | 60.914 | 61.1429 | -0.93462 | -0.62685 | -0.87511 | -0.56734
98.25 | 121.9162 | -61.116 | 60.3928 | 0.098959 | -0.031363 | 0.052101 | -0.043331 | 0.077466 | 0.053534 | -0.090186 | 60.2368 | 60.3044 | 60.3055 | 60.259 | 61.1852 | 61.1541 | 60.8728 | 61.0926 | 0.14474 | 0.014413 | 0.097877 | 0.002445 | 0.12324 | 0.09931 | -0.04441 | 60.2826 | 60.3502 | 60.3512 | 60.3048 | 61.2309 | 61.1999 | 60.9186 | 61.1383 | -0.94835 | -0.636 | -0.87969 | -0.56734
99.9844 | 121.8475 | -61.0657 | 60.5118 | 0.10354 | -0.026784 | 0.042944 | -0.038752 | 0.06831 | 0.062691 | -0.094765 | 60.2368 | 60.2998 | 60.2963 | 60.2544 | 61.1806 | 61.1679 | 60.8774 | 61.0834 | 0.14931 | 0.018992 | 0.08872 | 0.007024 | 0.11409 | 0.10847 | -0.048989 | 60.2826 | 60.3456 | 60.3421 | 60.3002 | 61.2264 | 61.2136 | 60.9232 | 61.1292 | -0.94378 | -0.64058 | -0.88427 | -0.58107
101.7344 | 121.756 | -61.0748 | 60.5392 | 0.098959 | -0.026784 | 0.038365 | -0.029595 | 0.072888 | 0.058113 | -0.099343 | 60.2368 | 60.2907 | 60.3009 | 60.2544 | 61.176 | 61.1679 | 60.8774 | 61.088 | 0.14474 | 0.018992 | 0.084141 | 0.016181 | 0.11866 | 0.10389 | -0.053567 | 60.2826 | 60.3364 | 60.3467 | 60.3002 | 61.2218 | 61.2136 | 60.9232 | 61.1337 | -0.9392 | -0.64058 | -0.87511 | -0.5765
103.4062 | 121.9025 | -61.1343 | 60.379 | 0.10354 | -0.026784 | 0.038365 | -0.029595 | 0.06831 | 0.053534 | -0.094765 | 60.2414 | 60.2998 | 60.2917 | 60.259 | 61.176 | 61.1633 | 60.8682 | 61.0926 | 0.14931 | 0.018992 | 0.084141 | 0.016181 | 0.11409 | 0.09931 | -0.048989 | 60.2872 | 60.3456 | 60.3375 | 60.3048 | 61.2218 | 61.2091 | 60.914 | 61.1383 | -0.93462 | -0.62685 | -0.88427 | -0.5765
105.1875 | 121.8109 | -61.1206 | 60.4614 | 0.098959 | -0.022205 | 0.038365 | -0.029595 | 0.072888 | 0.058113 | -0.094765 | 60.2414 | 60.2998 | 60.3009 | 60.259 | 61.1806 | 61.1633 | 60.8682 | 61.088 | 0.14474 | 0.023571 | 0.084141 | 0.016181 | 0.11866 | 0.10389 | -0.048989 | 60.2872 | 60.3456 | 60.3467 | 60.3048 | 61.2264 | 61.2091 | 60.914 | 61.1337 | -0.9392 | -0.62685 | -0.87969 | -0.56734
107.0469 | 121.8155 | -61.1298 | 60.4752 | 0.094381 | -0.035942 | 0.038365 | -0.029595 | 0.077466 | 0.058113 | -0.099343 | 60.2368 | 60.3044 | 60.3055 | 60.2544 | 61.176 | 61.1633 | 60.8637 | 61.0926 | 0.14016 | 0.009834 | 0.084141 | 0.016181 | 0.12324 | 0.10389 | -0.053567 | 60.2826 | 60.3502 | 60.3512 | 60.3002 | 61.2218 | 61.2091 | 60.9094 | 61.1383 | -0.9392 | -0.62685 | -0.87054 | -0.55818
109.0156 | 121.843 | -61.0565 | 60.4889 | 0.098959 | -0.035942 | 0.042944 | -0.029595 | 0.072888 | 0.053534 | -0.094765 | 60.2322 | 60.2998 | 60.2963 | 60.2499 | 61.1714 | 61.1633 | 60.8774 | 61.0788 | 0.14474 | 0.009834 | 0.08872 | 0.016181 | 0.11866 | 0.09931 | -0.048989 | 60.278 | 60.3456 | 60.3421 | 60.2956 | 61.2172 | 61.2091 | 60.9232 | 61.1246 | -0.9392 | -0.64516 | -0.87511 | -0.58107
110.7031 | 121.8887 | -61.1206 | 60.4065 | 0.098959 | -0.031363 | 0.038365 | -0.034174 | 0.077466 | 0.048956 | -0.094765 | 60.2368 | 60.2998 | 60.2917 | 60.2499 | 61.176 | 61.1587 | 60.8728 | 61.088 | 0.14474 | 0.014413 | 0.084141 | 0.011602 | 0.12324 | 0.094732 | -0.048989 | 60.2826 | 60.3456 | 60.3375 | 60.2956 | 61.2218 | 61.2045 | 60.9186 | 61.1337 | -0.9392 | -0.636 | -0.88427 | -0.58107
112.4062 | 121.8567 | -61.1023 | 60.4385 | 0.094381 | -0.031363 | 0.038365 | -0.034174 | 0.082044 | 0.048956 | -0.094765 | 60.2368 | 60.2998 | 60.3009 | 60.259 | 61.1806 | 61.1587 | 60.8682 | 61.0788 | 0.14016 | 0.014413 | 0.084141 | 0.011602 | 0.12782 | 0.094732 | -0.048989 | 60.2826 | 60.3456 | 60.3467 | 60.3048 | 61.2264 | 61.2045 | 60.914 | 61.1246 | -0.94378 | -0.63142 | -0.87969 | -0.56734
114.1094 | 121.8796 | -61.0428 | 60.4843 | 0.098959 | -0.026784 | 0.038365 | -0.034174 | 0.072888 | 0.053534 | -0.099343 | 60.2368 | 60.2998 | 60.2963 | 60.259 | 61.1806 | 61.1587 | 60.8774 | 61.0834 | 0.14474 | 0.018992 | 0.084141 | 0.011602 | 0.11866 | 0.09931 | -0.053567 | 60.2826 | 60.3456 | 60.3421 | 60.3048 | 61.2264 | 61.2045 | 60.9232 | 61.1292 | -0.94378 | -0.64058 | -0.88427 | -0.58107
115.7812 | 121.8796 | -61.1114 | 60.3882 | 0.098959 | -0.031363 | 0.047522 | -0.029595 | 0.072888 | 0.053534 | -0.090186 | 60.2368 | 60.2998 | 60.2917 | 60.2544 | 61.1714 | 61.1633 | 60.8637 | 61.088 | 0.14474 | 0.014413 | 0.093298 | 0.016181 | 0.11866 | 0.09931 | -0.04441 | 60.2826 | 60.3456 | 60.3375 | 60.3002 | 61.2172 | 61.2091 | 60.9094 | 61.1337 | -0.93462 | -0.62685 | -0.87969 | -0.57192
117.4688 | 121.7926 | -61.1206 | 60.4294 | 0.094381 | -0.031363 | 0.042944 | -0.029595 | 0.072888 | 0.048956 | -0.094765 | 60.2414 | 60.2952 | 60.2963 | 60.259 | 61.176 | 61.1587 | 60.8637 | 61.0788 | 0.14016 | 0.014413 | 0.08872 | 0.016181 | 0.11866 | 0.094732 | -0.048989 | 60.2872 | 60.341 | 60.3421 | 60.3048 | 61.2218 | 61.2045 | 60.9094 | 61.1246 | -0.93462 | -0.62227 | -0.87969 | -0.56734
119.1406 | 121.788 | -61.1298 | 60.4706 | 0.098959 | -0.017627 | 0.038365 | -0.029595 | 0.077466 | 0.044377 | -0.094765 | 60.2414 | 60.2952 | 60.2963 | 60.2636 | 61.1714 | 61.1633 | 60.8682 | 61.0834 | 0.14474 | 0.028149 | 0.084141 | 0.016181 | 0.12324 | 0.090153 | -0.048989 | 60.2872 | 60.341 | 60.3421 | 60.3094 | 61.2172 | 61.2091 | 60.914 | 61.1292 | -0.93004 | -0.62685 | -0.87511 | -0.57192
120.8281 | 121.7972 | -61.0977 | 60.4752 | 0.098959 | -0.031363 | 0.038365 | -0.025017 | 0.072888 | 0.053534 | -0.094765 | 60.2368 | 60.2998 | 60.2963 | 60.2636 | 61.1714 | 61.1679 | 60.8637 | 61.088 | 0.14474 | 0.014413 | 0.084141 | 0.020759 | 0.11866 | 0.09931 | -0.048989 | 60.2826 | 60.3456 | 60.3421 | 60.3094 | 61.2172 | 61.2136 | 60.9094 | 61.1337 | -0.93462 | -0.62685 | -0.87511 | -0.56734
122.5 | 121.907 | -61.0565 | 60.4752 | 0.098959 | -0.031363 | 0.042944 | -0.034174 | 0.072888 | 0.053534 | -0.094765 | 60.2368 | 60.2952 | 60.3009 | 60.2544 | 61.1806 | 61.1633 | 60.8682 | 61.0834 | 0.14474 | 0.014413 | 0.08872 | 0.011602 | 0.11866 | 0.09931 | -0.048989 | 60.2826 | 60.341 | 60.3467 | 60.3002 | 61.2264 | 61.2091 | 60.914 | 61.1292 | -0.94378 | -0.63142 | -0.87969 | -0.56734
124.1875 | 121.7606 | -61.1618 | 60.4477 | 0.094381 | -0.026784 | 0.042944 | -0.029595 | 0.072888 | 0.058113 | -0.094765 | 60.2322 | 60.2952 | 60.2917 | 60.2544 | 61.1714 | 61.1633 | 60.8637 | 61.0834 | 0.14016 | 0.018992 | 0.08872 | 0.016181 | 0.11866 | 0.10389 | -0.048989 | 60.278 | 60.341 | 60.3375 | 60.3002 | 61.2172 | 61.2091 | 60.9094 | 61.1292 | -0.9392 | -0.63142 | -0.87969 | -0.57192
125.8438 | 121.7743 | -61.0886 | 60.5164 | 0.10354 | -0.022205 | 0.047522 | -0.025017 | 0.077466 | 0.053534 | -0.099343 | 60.2414 | 60.2998 | 60.2917 | 60.2544 | 61.176 | 61.1496 | 60.8637 | 61.0834 | 0.14931 | 0.023571 | 0.093298 | 0.020759 | 0.12324 | 0.09931 | -0.053567 | 60.2872 | 60.3456 | 60.3375 | 60.3002 | 61.2218 | 61.1953 | 60.9094 | 61.1292 | -0.93462 | -0.62227 | -0.88427 | -0.57192
127.5312 | 121.8704 | -61.1252 | 60.4202 | 0.098959 | -0.022205 | 0.029208 | -0.029595 | 0.072888 | 0.053534 | -0.094765 | 60.2322 | 60.2998 | 60.2963 | 60.2499 | 61.1668 | 61.1541 | 60.8637 | 61.088 | 0.14474 | 0.023571 | 0.074984 | 0.016181 | 0.11866 | 0.09931 | -0.048989 | 60.278 | 60.3456 | 60.3421 | 60.2956 | 61.2126 | 61.1999 | 60.9094 | 61.1337 | -0.93462 | -0.63142 | -0.87053 | -0.56734
129.2812 | 121.7606 | -61.1343 | 60.4706 | 0.098959 | -0.026784 | 0.038365 | -0.029595 | 0.072888 | 0.053534 | -0.094765 | 60.2322 | 60.2952 | 60.2963 | 60.2499 | 61.176 | 61.1541 | 60.8637 | 61.0834 | 0.14474 | 0.018992 | 0.084141 | 0.016181 | 0.11866 | 0.09931 | -0.048989 | 60.278 | 60.341 | 60.3421 | 60.2956 | 61.2218 | 61.1999 | 60.9094 | 61.1292 | -0.94378 | -0.63142 | -0.87969 | -0.56734
130.9531 | 121.8155 | -61.1206 | 60.4294 | 0.098959 | -0.017627 | 0.042944 | -0.029595 | 0.06831 | 0.048956 | -0.094765 | 60.2322 | 60.2952 | 60.3009 | 60.2544 | 61.1806 | 61.1541 | 60.8637 | 61.0788 | 0.14474 | 0.028149 | 0.08872 | 0.016181 | 0.11409 | 0.094732 | -0.048989 | 60.278 | 60.341 | 60.3467 | 60.3002 | 61.2264 | 61.1999 | 60.9094 | 61.1246 | -0.94835 | -0.63142 | -0.87969 | -0.56276
132.6406 | 121.8796 | -61.0794 | 60.4614 | 0.089802 | -0.026784 | 0.042944 | -0.038752 | 0.077466 | 0.048956 | -0.099343 | 60.2322 | 60.2907 | 60.2826 | 60.2499 | 61.176 | 61.1587 | 60.8682 | 61.088 | 0.13558 | 0.018992 | 0.08872 | 0.007024 | 0.12324 | 0.094732 | -0.053567 | 60.278 | 60.3364 | 60.3284 | 60.2956 | 61.2218 | 61.2045 | 60.914 | 61.1337 | -0.94378 | -0.636 | -0.89343 | -0.58565
134.3125 | 121.7972 | -61.1069 | 60.4156 | 0.10354 | -0.026784 | 0.038365 | -0.020438 | 0.077466 | 0.058113 | -0.094765 | 60.2368 | 60.2907 | 60.2963 | 60.2453 | 61.1806 | 61.1587 | 60.8545 | 61.088 | 0.14931 | 0.018992 | 0.084141 | 0.025338 | 0.12324 | 0.10389 | -0.048989 | 60.2826 | 60.3364 | 60.3421 | 60.2911 | 61.2264 | 61.2045 | 60.9003 | 61.1337 | -0.94378 | -0.61769 | -0.88427 | -0.55818
135.9844 | 121.7514 | -61.1298 | 60.466 | 0.098959 | -0.026784 | 0.042944 | -0.025017 | 0.077466 | 0.053534 | -0.10392 | 60.2322 | 60.2907 | 60.2963 | 60.2453 | 61.1714 | 61.1587 | 60.8591 | 61.0742 | 0.14474 | 0.018992 | 0.08872 | 0.020759 | 0.12324 | 0.09931 | -0.058145 | 60.278 | 60.3364 | 60.3421 | 60.2911 | 61.2172 | 61.2045 | 60.9048 | 61.12 | -0.9392 | -0.62685 | -0.87511 | -0.56276
137.6719 | 121.8246 | -61.0794 | 60.4431 | 0.094381 | -0.031363 | 0.047522 | -0.034174 | 0.072888 | 0.053534 | -0.094765 | 60.2414 | 60.2952 | 60.2917 | 60.2499 | 61.176 | 61.1633 | 60.8682 | 61.0742 | 0.14016 | 0.014413 | 0.093298 | 0.011602 | 0.11866 | 0.09931 | -0.048989 | 60.2872 | 60.341 | 60.3375 | 60.2956 | 61.2218 | 61.2091 | 60.914 | 61.12 | -0.93462 | -0.62685 | -0.88427 | -0.5765
139.3438 | 121.7468 | -61.1618 | 60.4385 | 0.10354 | -0.022205 | 0.047522 | -0.034174 | 0.072888 | 0.048956 | -0.090186 | 60.2368 | 60.2952 | 60.2917 | 60.2544 | 61.1714 | 61.1496 | 60.8682 | 61.0788 | 0.14931 | 0.023571 | 0.093298 | 0.011602 | 0.11866 | 0.094732 | -0.04441 | 60.2826 | 60.341 | 60.3375 | 60.3002 | 61.2172 | 61.1953 | 60.914 | 61.1246 | -0.93462 | -0.63142 | -0.87969 | -0.5765
141.0156 | 121.7514 | -61.171 | 60.4523 | 0.10354 | -0.022205 | 0.047522 | -0.029595 | 0.072888 | 0.058113 | -0.094765 | 60.2368 | 60.2907 | 60.2917 | 60.2544 | 61.1714 | 61.1587 | 60.8591 | 61.0788 | 0.14931 | 0.023571 | 0.093298 | 0.016181 | 0.11866 | 0.10389 | -0.048989 | 60.2826 | 60.3364 | 60.3375 | 60.3002 | 61.2172 | 61.2045 | 60.9048 | 61.1246 | -0.93462 | -0.62227 | -0.87969 | -0.56734
142.6875 | 121.7606 | -61.1389 | 60.4111 | 0.089802 | -0.026784 | 0.042944 | -0.034174 | 0.072888 | 0.062691 | -0.094765 | 60.2322 | 60.2907 | 60.2917 | 60.2544 | 61.1714 | 61.1633 | 60.8545 | 61.0742 | 0.13558 | 0.018992 | 0.08872 | 0.011602 | 0.11866 | 0.10847 | -0.048989 | 60.278 | 60.3364 | 60.3375 | 60.3002 | 61.2172 | 61.2091 | 60.9003 | 61.12 | -0.9392 | -0.62227 | -0.87969 | -0.56276
144.375 | 121.8979 | -61.1023 | 60.3836 | 0.10354 | -0.026784 | 0.047522 | -0.029595 | 0.072888 | 0.044377 | -0.094765 | 60.2276 | 60.2998 | 60.2963 | 60.2453 | 61.1714 | 61.1587 | 60.8545 | 61.0834 | 0.14931 | 0.018992 | 0.093298 | 0.016181 | 0.11866 | 0.090153 | -0.048989 | 60.2734 | 60.3456 | 60.3421 | 60.2911 | 61.2172 | 61.2045 | 60.9003 | 61.1292 | -0.94378 | -0.62685 | -0.87511 | -0.55818
146.0781 | 121.756 | -61.0931 | 60.5484 | 0.098959 | -0.022205 | 0.038365 | -0.038752 | 0.082044 | 0.048956 | -0.099343 | 60.2322 | 60.2907 | 60.2917 | 60.2499 | 61.1668 | 61.1541 | 60.8591 | 61.0788 | 0.14474 | 0.023571 | 0.084141 | 0.007024 | 0.12782 | 0.094732 | -0.053567 | 60.278 | 60.3364 | 60.3375 | 60.2956 | 61.2126 | 61.1999 | 60.9048 | 61.1246 | -0.93462 | -0.62685 | -0.87511 | -0.56734
147.75 | 121.7697 | -61.0886 | 60.5026 | 0.094381 | -0.017627 | 0.038365 | -0.034174 | 0.077466 | 0.053534 | -0.094765 | 60.2322 | 60.2861 | 60.2917 | 60.2499 | 61.1668 | 61.1541 | 60.8637 | 61.0788 | 0.14016 | 0.028149 | 0.084141 | 0.011602 | 0.12324 | 0.09931 | -0.048989 | 60.278 | 60.3319 | 60.3375 | 60.2956 | 61.2126 | 61.1999 | 60.9094 | 61.1246 | -0.93462 | -0.63142 | -0.87511 | -0.57192
149.4219 | 121.8613 | -61.0519 | 60.4431 | 0.10354 | -0.026784 | 0.033786 | -0.038752 | 0.072888 | 0.048956 | -0.099343 | 60.2276 | 60.2998 | 60.2872 | 60.2544 | 61.1668 | 61.1541 | 60.8591 | 61.088 | 0.14931 | 0.018992 | 0.079562 | 0.007024 | 0.11866 | 0.094732 | -0.053567 | 60.2734 | 60.3456 | 60.3329 | 60.3002 | 61.2126 | 61.1999 | 60.9048 | 61.1337 | -0.9392 | -0.63142 | -0.87969 | -0.57192
151.0938 | 121.8887 | -61.0519 | 60.4477 | 0.098959 | -0.022205 | 0.038365 | -0.029595 | 0.072888 | 0.048956 | -0.099343 | 60.2322 | 60.2907 | 60.2917 | 60.2453 | 61.1668 | 61.1541 | 60.8682 | 61.0697 | 0.14474 | 0.023571 | 0.084141 | 0.016181 | 0.11866 | 0.094732 | -0.053567 | 60.278 | 60.3364 | 60.3375 | 60.2911 | 61.2126 | 61.1999 | 60.914 | 61.1154 | -0.93462 | -0.636 | -0.87511 | -0.5765
152.7969 | 121.8109 | -61.0931 | 60.4111 | 0.094381 | -0.022205 | 0.038365 | -0.029595 | 0.077466 | 0.053534 | -0.099343 | 60.2368 | 60.2907 | 60.2917 | 60.2407 | 61.1806 | 61.1541 | 60.8637 | 61.0697 | 0.14016 | 0.023571 | 0.084141 | 0.016181 | 0.12324 | 0.09931 | -0.053567 | 60.2826 | 60.3364 | 60.3375 | 60.2865 | 61.2264 | 61.1999 | 60.9094 | 61.1154 | -0.94378 | -0.62685 | -0.88885 | -0.57192
154.4688 | 121.8796 | -61.0977 | 60.3607 | 0.098959 | -0.017627 | 0.042944 | -0.029595 | 0.077466 | 0.048956 | -0.094765 | 60.2322 | 60.2907 | 60.2872 | 60.2453 | 61.1714 | 61.1496 | 60.8591 | 61.0697 | 0.14474 | 0.028149 | 0.08872 | 0.016181 | 0.12324 | 0.094732 | -0.048989 | 60.278 | 60.3364 | 60.3329 | 60.2911 | 61.2172 | 61.1953 | 60.9048 | 61.1154 | -0.9392 | -0.62685 | -0.88427 | -0.57192
156.1719 | 121.7834 | -61.1069 | 60.498 | 0.098959 | -0.017627 | 0.042944 | -0.029595 | 0.06831 | 0.062691 | -0.099343 | 60.2322 | 60.2907 | 60.2917 | 60.2499 | 61.1668 | 61.145 | 60.8545 | 61.0742 | 0.14474 | 0.028149 | 0.08872 | 0.016181 | 0.11409 | 0.10847 | -0.053567 | 60.278 | 60.3364 | 60.3375 | 60.2956 | 61.2126 | 61.1908 | 60.9003 | 61.12 | -0.93462 | -0.62227 | -0.87511 | -0.56276
157.8438 | 121.7468 | -61.0703 | 60.498 | 0.098959 | -0.022205 | 0.042944 | -0.038752 | 0.077466 | 0.048956 | -0.099343 | 60.2231 | 60.2861 | 60.2826 | 60.2453 | 61.1668 | 61.1587 | 60.8591 | 61.0697 | 0.14474 | 0.023571 | 0.08872 | 0.007024 | 0.12324 | 0.094732 | -0.053567 | 60.2688 | 60.3319 | 60.3284 | 60.2911 | 61.2126 | 61.2045 | 60.9048 | 61.1154 | -0.94378 | -0.636 | -0.88427 | -0.5765
159.5156 | 121.7422 | -61.1526 | 60.4523 | 0.094381 | -0.017627 | 0.042944 | -0.029595 | 0.077466 | 0.058113 | -0.094765 | 60.2276 | 60.2907 | 60.2917 | 60.2453 | 61.1668 | 61.1587 | 60.8499 | 61.0788 | 0.14016 | 0.028149 | 0.08872 | 0.016181 | 0.12324 | 0.10389 | -0.048989 | 60.2734 | 60.3364 | 60.3375 | 60.2911 | 61.2126 | 61.2045 | 60.8957 | 61.1246 | -0.9392 | -0.62227 | -0.87511 | -0.55818
161.1875 | 121.7651 | -61.116 | 60.4614 | 0.098959 | -0.022205 | 0.033786 | -0.029595 | 0.077466 | 0.048956 | -0.094765 | 60.2322 | 60.2952 | 60.2963 | 60.2499 | 61.1714 | 61.1541 | 60.8499 | 61.0742 | 0.14474 | 0.023571 | 0.079562 | 0.016181 | 0.12324 | 0.094732 | -0.048989 | 60.278 | 60.341 | 60.3421 | 60.2956 | 61.2172 | 61.1999 | 60.8957 | 61.12 | -0.9392 | -0.61769 | -0.87511 | -0.5536
162.8594 | 121.7377 | -61.0886 | 60.5164 | 0.094381 | -0.017627 | 0.047522 | -0.029595 | 0.082044 | 0.053534 | -0.094765 | 60.2276 | 60.2907 | 60.2826 | 60.2407 | 61.1668 | 61.1541 | 60.8637 | 61.0788 | 0.14016 | 0.028149 | 0.093298 | 0.016181 | 0.12782 | 0.09931 | -0.048989 | 60.2734 | 60.3364 | 60.3284 | 60.2865 | 61.2126 | 61.1999 | 60.9094 | 61.1246 | -0.9392 | -0.636 | -0.88427 | -0.58107
164.5312 | 121.8338 | -61.0703 | 60.4889 | 0.098959 | -0.031363 | 0.042944 | -0.029595 | 0.072888 | 0.048956 | -0.094765 | 60.2322 | 60.2861 | 60.2872 | 60.2453 | 61.1714 | 61.1496 | 60.8591 | 61.0742 | 0.14474 | 0.014413 | 0.08872 | 0.016181 | 0.11866 | 0.094732 | -0.048989 | 60.278 | 60.3319 | 60.3329 | 60.2911 | 61.2172 | 61.1953 | 60.9048 | 61.12 | -0.9392 | -0.62685 | -0.88427 | -0.57192
166.2344 | 121.8704 | -61.0977 | 60.3836 | 0.098959 | -0.035942 | 0.038365 | -0.034174 | 0.077466 | 0.048956 | -0.094765 | 60.2276 | 60.2907 | 60.2963 | 60.2407 | 61.176 | 61.1541 | 60.8499 | 61.0742 | 0.14474 | 0.009834 | 0.084141 | 0.011602 | 0.12324 | 0.094732 | -0.048989 | 60.2734 | 60.3364 | 60.3421 | 60.2865 | 61.2218 | 61.1999 | 60.8957 | 61.12 | -0.94836 | -0.62227 | -0.87969 | -0.5536
167.9688 | 121.8201 | -61.0931 | 60.4385 | 0.098959 | -0.031363 | 0.047522 | -0.038752 | 0.072888 | 0.044377 | -0.10392 | 60.2322 | 60.2952 | 60.2917 | 60.2361 | 61.1668 | 61.1496 | 60.8591 | 61.0742 | 0.14474 | 0.014413 | 0.093298 | 0.007024 | 0.11866 | 0.090153 | -0.058145 | 60.278 | 60.341 | 60.3375 | 60.2819 | 61.2126 | 61.1953 | 60.9048 | 61.12 | -0.93462 | -0.62685 | -0.87511 | -0.56734
169.6562 | 121.843 | -61.084 | 60.4477 | 0.098959 | -0.026784 | 0.042944 | -0.029595 | 0.072888 | 0.058113 | -0.094765 | 60.2276 | 60.2861 | 60.2917 | 60.2453 | 61.1668 | 61.1496 | 60.8499 | 61.0697 | 0.14474 | 0.018992 | 0.08872 | 0.016181 | 0.11866 | 0.10389 | -0.048989 | 60.2734 | 60.3319 | 60.3375 | 60.2911 | 61.2126 | 61.1953 | 60.8957 | 61.1154 | -0.9392 | -0.62227 | -0.87511 | -0.55818
171.3281 | 121.8155 | -61.0336 | 60.5026 | 0.098959 | -0.031363 | 0.042944 | -0.029595 | 0.072888 | 0.053534 | -0.090186 | 60.2276 | 60.2907 | 60.2917 | 60.2453 | 61.1714 | 61.1496 | 60.8545 | 61.0742 | 0.14474 | 0.014413 | 0.08872 | 0.016181 | 0.11866 | 0.09931 | -0.04441 | 60.2734 | 60.3364 | 60.3375 | 60.2911 | 61.2172 | 61.1953 | 60.9003 | 61.12 | -0.94378 | -0.62685 | -0.87969 | -0.56276
173 | 121.8704 | -61.0474 | 60.4431 | 0.094381 | -0.026784 | 0.042944 | -0.034174 | 0.077466 | 0.048956 | -0.099343 | 60.2322 | 60.2952 | 60.2917 | 60.2407 | 61.1714 | 61.1541 | 60.8591 | 61.0697 | 0.14016 | 0.018992 | 0.08872 | 0.011602 | 0.12324 | 0.094732 | -0.053567 | 60.278 | 60.341 | 60.3375 | 60.2865 | 61.2172 | 61.1999 | 60.9048 | 61.1154 | -0.9392 | -0.62685 | -0.87969 | -0.56734
174.6719 | 121.8842 | -61.0336 | 60.4431 | 0.094381 | -0.026784 | 0.038365 | -0.034174 | 0.072888 | 0.044377 | -0.099343 | 60.2322 | 60.2861 | 60.2872 | 60.2453 | 61.1714 | 61.1496 | 60.8545 | 61.0697 | 0.14016 | 0.018992 | 0.084141 | 0.011602 | 0.11866 | 0.090153 | -0.053567 | 60.278 | 60.3319 | 60.3329 | 60.2911 | 61.2172 | 61.1953 | 60.9003 | 61.1154 | -0.9392 | -0.62227 | -0.88427 | -0.56734
176.375 | 121.7422 | -61.084 | 60.5164 | 0.098959 | -0.022205 | 0.038365 | -0.034174 | 0.072888 | 0.053534 | -0.099343 | 60.2231 | 60.2907 | 60.2917 | 60.2361 | 61.1668 | 61.1541 | 60.8545 | 61.0788 | 0.14474 | 0.023571 | 0.084141 | 0.011602 | 0.11866 | 0.09931 | -0.053567 | 60.2688 | 60.3364 | 60.3375 | 60.2819 | 61.2126 | 61.1999 | 60.9003 | 61.1246 | -0.94378 | -0.63142 | -0.87511 | -0.56276
178.1094 | 121.756 | -61.0794 | 60.4889 | 0.098959 | -0.031363 | 0.038365 | -0.034174 | 0.072888 | 0.053534 | -0.094765 | 60.2276 | 60.2907 | 60.2872 | 60.2407 | 61.1714 | 61.1496 | 60.8499 | 61.0742 | 0.14474 | 0.014413 | 0.084141 | 0.011602 | 0.11866 | 0.09931 | -0.048989 | 60.2734 | 60.3364 | 60.3329 | 60.2865 | 61.2172 | 61.1953 | 60.8957 | 61.12 | -0.94378 | -0.62227 | -0.88427 | -0.56276
179.8438 | 121.8155 | -61.0931 | 60.4431 | 0.098959 | -0.026784 | 0.042944 | -0.029595 | 0.077466 | 0.053534 | -0.099343 | 60.2231 | 60.2815 | 60.2872 | 60.2361 | 61.1668 | 61.1496 | 60.8499 | 61.0651 | 0.14474 | 0.018992 | 0.08872 | 0.016181 | 0.12324 | 0.09931 | -0.053567 | 60.2688 | 60.3273 | 60.3329 | 60.2819 | 61.2126 | 61.1953 | 60.8957 | 61.1109 | -0.94378 | -0.62684 | -0.87969 | -0.56276
181.5156 | 121.7422 | -61.0657 | 60.4935 | 0.094381 | -0.026784 | 0.038365 | -0.034174 | 0.082044 | 0.053534 | -0.090186 | 60.2322 | 60.2952 | 60.2826 | 60.2407 | 61.1714 | 61.1496 | 60.8499 | 61.0697 | 0.14016 | 0.018992 | 0.084141 | 0.011602 | 0.12782 | 0.09931 | -0.04441 | 60.278 | 60.341 | 60.3284 | 60.2865 | 61.2172 | 61.1953 | 60.8957 | 61.1154 | -0.9392 | -0.61769 | -0.88885 | -0.56734
183.1875 | 121.8246 | -61.0703 | 60.4431 | 0.098959 | -0.026784 | 0.033786 | -0.029595 | 0.06831 | 0.048956 | -0.099343 | 60.2231 | 60.2861 | 60.2826 | 60.2453 | 61.1668 | 61.145 | 60.8499 | 61.0742 | 0.14474 | 0.018992 | 0.079562 | 0.016181 | 0.11409 | 0.094732 | -0.053567 | 60.2688 | 60.3319 | 60.3284 | 60.2911 | 61.2126 | 61.1908 | 60.8957 | 61.12 | -0.94378 | -0.62684 | -0.88427 | -0.56734
184.8906 | 121.8613 | -61.0474 | 60.4523 | 0.094381 | -0.026784 | 0.042944 | -0.034174 | 0.072888 | 0.048956 | -0.099343 | 60.2368 | 60.2907 | 60.2917 | 60.2453 | 61.1623 | 61.1496 | 60.8591 | 61.0742 | 0.14016 | 0.018992 | 0.08872 | 0.011602 | 0.11866 | 0.094732 | -0.053567 | 60.2826 | 60.3364 | 60.3375 | 60.2911 | 61.208 | 61.1953 | 60.9048 | 61.12 | -0.92546 | -0.62227 | -0.87053 | -0.56734
186.5781 | 121.875 | -61.0611 | 60.4385 | 0.089802 | -0.031363 | 0.038365 | -0.038752 | 0.077466 | 0.053534 | -0.099343 | 60.2185 | 60.2861 | 60.2872 | 60.2407 | 61.1623 | 61.1541 | 60.8499 | 61.0697 | 0.13558 | 0.014413 | 0.084141 | 0.007024 | 0.12324 | 0.09931 | -0.053567 | 60.2643 | 60.3319 | 60.3329 | 60.2865 | 61.208 | 61.1999 | 60.8957 | 61.1154 | -0.94378 | -0.63142 | -0.87511 | -0.56276
188.3281 | 121.8613 | -61.0474 | 60.4431 | 0.089802 | -0.035942 | 0.033786 | -0.034174 | 0.077466 | 0.053534 | -0.10392 | 60.2276 | 60.2861 | 60.2826 | 60.2453 | 61.1623 | 61.1496 | 60.8545 | 61.0651 | 0.13558 | 0.009834 | 0.079562 | 0.011602 | 0.12324 | 0.09931 | -0.058145 | 60.2734 | 60.3319 | 60.3284 | 60.2911 | 61.208 | 61.1953 | 60.9003 | 61.1109 | -0.93462 | -0.62685 | -0.87969 | -0.57192
190.0312 | 121.8155 | -61.0977 | 60.4111 | 0.098959 | -0.031363 | 0.038365 | -0.038752 | 0.077466 | 0.053534 | -0.094765 | 60.2322 | 60.2861 | 60.2872 | 60.2407 | 61.1714 | 61.145 | 60.8499 | 61.0742 | 0.14474 | 0.014413 | 0.084141 | 0.007024 | 0.12324 | 0.09931 | -0.048989 | 60.278 | 60.3319 | 60.3329 | 60.2865 | 61.2172 | 61.1908 | 60.8957 | 61.12 | -0.9392 | -0.61769 | -0.88427 | -0.56276
191.7344 | 121.8201 | -61.1023 | 60.3973 | 0.098959 | -0.026784 | 0.042944 | -0.038752 | 0.082044 | 0.053534 | -0.090186 | 60.2322 | 60.2861 | 60.2826 | 60.2315 | 61.1668 | 61.1496 | 60.8362 | 61.0697 | 0.14474 | 0.018992 | 0.08872 | 0.007024 | 0.12782 | 0.09931 | -0.04441 | 60.278 | 60.3319 | 60.3284 | 60.2773 | 61.2126 | 61.1953 | 60.882 | 61.1154 | -0.93462 | -0.60395 | -0.88427 | -0.5536
193.4531 | 121.8613 | -61.1023 | 60.379 | 0.098959 | -0.026784 | 0.033786 | -0.034174 | 0.077466 | 0.053534 | -0.090186 | 60.2368 | 60.2815 | 60.2826 | 60.2407 | 61.1623 | 61.1496 | 60.8453 | 61.0651 | 0.14474 | 0.018992 | 0.079562 | 0.011602 | 0.12324 | 0.09931 | -0.04441 | 60.2826 | 60.3273 | 60.3284 | 60.2865 | 61.208 | 61.1953 | 60.8911 | 61.1109 | -0.92546 | -0.60853 | -0.87969 | -0.56276
195.1562 | 121.7285 | -61.0428 | 60.5118 | 0.10354 | -0.026784 | 0.042944 | -0.034174 | 0.077466 | 0.053534 | -0.094765 | 60.2231 | 60.2861 | 60.2826 | 60.2407 | 61.1668 | 61.145 | 60.8499 | 61.0651 | 0.14931 | 0.018992 | 0.08872 | 0.011602 | 0.12324 | 0.09931 | -0.048989 | 60.2688 | 60.3319 | 60.3284 | 60.2865 | 61.2126 | 61.1908 | 60.8957 | 61.1109 | -0.94378 | -0.62684 | -0.88427 | -0.56734
196.8438 | 121.7789 | -61.1023 | 60.4523 | 0.094381 | -0.026784 | 0.042944 | -0.025017 | 0.082044 | 0.053534 | -0.094765 | 60.2231 | 60.2952 | 60.278 | 60.2453 | 61.1668 | 61.1404 | 60.8453 | 61.0605 | 0.14016 | 0.018992 | 0.08872 | 0.020759 | 0.12782 | 0.09931 | -0.048989 | 60.2688 | 60.341 | 60.3238 | 60.2911 | 61.2126 | 61.1862 | 60.8911 | 61.1063 | -0.94378 | -0.62227 | -0.88885 | -0.56734
198.5156 | 121.8292 | -61.1069 | 60.3653 | 0.098959 | -0.026784 | 0.047522 | -0.029595 | 0.072888 | 0.062691 | -0.094765 | 60.2322 | 60.2815 | 60.2826 | 60.2407 | 61.1668 | 61.1496 | 60.8453 | 61.0651 | 0.14474 | 0.018992 | 0.093298 | 0.016181 | 0.11866 | 0.10847 | -0.048989 | 60.278 | 60.3273 | 60.3284 | 60.2865 | 61.2126 | 61.1953 | 60.8911 | 61.1109 | -0.93462 | -0.61311 | -0.88427 | -0.56276
200.2656 | 121.8109 | -61.0794 | 60.4156 | 0.098959 | -0.026784 | 0.038365 | -0.034174 | 0.077466 | 0.058113 | -0.099343 | 60.2322 | 60.2861 | 60.2917 | 60.2361 | 61.1623 | 61.1541 | 60.8453 | 61.0651 | 0.14474 | 0.018992 | 0.084141 | 0.011602 | 0.12324 | 0.10389 | -0.053567 | 60.278 | 60.3319 | 60.3375 | 60.2819 | 61.208 | 61.1999 | 60.8911 | 61.1109 | -0.93004 | -0.61311 | -0.87053 | -0.5536
201.9531 | 121.8063 | -61.0977 | 60.4248 | 0.094381 | -0.026784 | 0.038365 | -0.034174 | 0.077466 | 0.053534 | -0.099343 | 60.2276 | 60.2815 | 60.278 | 60.227 | 61.1623 | 61.145 | 60.8499 | 61.0651 | 0.14016 | 0.018992 | 0.084141 | 0.011602 | 0.12324 | 0.09931 | -0.053567 | 60.2734 | 60.3273 | 60.3238 | 60.2727 | 61.208 | 61.1908 | 60.8957 | 61.1109 | -0.93462 | -0.62227 | -0.88427 | -0.57192
203.625 | 121.8109 | -61.1023 | 60.3973 | 0.094381 | -0.026784 | 0.042944 | -0.043331 | 0.077466 | 0.053534 | -0.090186 | 60.2231 | 60.2907 | 60.278 | 60.2453 | 61.1668 | 61.145 | 60.8453 | 61.0697 | 0.14016 | 0.018992 | 0.08872 | 0.002445 | 0.12324 | 0.09931 | -0.04441 | 60.2688 | 60.3364 | 60.3238 | 60.2911 | 61.2126 | 61.1908 | 60.8911 | 61.1154 | -0.94378 | -0.62227 | -0.88885 | -0.56734
205.375 | 121.7697 | -61.084 | 60.4477 | 0.098959 | -0.026784 | 0.038365 | -0.025017 | 0.082044 | 0.053534 | -0.094765 | 60.2276 | 60.2861 | 60.2734 | 60.2453 | 61.1531 | 61.145 | 60.8499 | 61.0742 | 0.14474 | 0.018992 | 0.084141 | 0.020759 | 0.12782 | 0.09931 | -0.048989 | 60.2734 | 60.3319 | 60.3192 | 60.2911 | 61.1989 | 61.1908 | 60.8957 | 61.12 | -0.92546 | -0.62227 | -0.87969 | -0.5765
207.0625 | 121.8521 | -61.1069 | 60.3928 | 0.10812 | -0.031363 | 0.047522 | -0.034174 | 0.077466 | 0.044377 | -0.094765 | 60.2231 | 60.2907 | 60.278 | 60.2407 | 61.1668 | 61.1404 | 60.8408 | 61.0651 | 0.15389 | 0.014413 | 0.093298 | 0.011602 | 0.12324 | 0.090153 | -0.048989 | 60.2688 | 60.3364 | 60.3238 | 60.2865 | 61.2126 | 61.1862 | 60.8865 | 61.1109 | -0.94378 | -0.61769 | -0.88885 | -0.56276
208.7344 | 121.8246 | -61.0886 | 60.3836 | 0.094381 | -0.022205 | 0.038365 | -0.034174 | 0.077466 | 0.053534 | -0.094765 | 60.2322 | 60.2769 | 60.2826 | 60.2315 | 61.1577 | 61.1404 | 60.8453 | 61.0742 | 0.14016 | 0.023571 | 0.084141 | 0.011602 | 0.12324 | 0.09931 | -0.048989 | 60.278 | 60.3227 | 60.3284 | 60.2773 | 61.2035 | 61.1862 | 60.8911 | 61.12 | -0.92546 | -0.61311 | -0.87511 | -0.56276
210.4219 | 121.8567 | -61.0291 | 60.4614 | 0.098959 | -0.026784 | 0.052101 | -0.038752 | 0.072888 | 0.053534 | -0.099343 | 60.2185 | 60.2815 | 60.278 | 60.2315 | 61.1623 | 61.1496 | 60.8499 | 61.0651 | 0.14474 | 0.018992 | 0.097877 | 0.007024 | 0.11866 | 0.09931 | -0.053567 | 60.2643 | 60.3273 | 60.3238 | 60.2773 | 61.208 | 61.1953 | 60.8957 | 61.1109 | -0.94378 | -0.63142 | -0.88427 | -0.57192
212.1094 | 121.8018 | -61.0703 | 60.4202 | 0.098959 | -0.031363 | 0.047522 | -0.034174 | 0.072888 | 0.053534 | -0.094765 | 60.2322 | 60.2861 | 60.278 | 60.2361 | 61.1668 | 61.145 | 60.8408 | 61.0651 | 0.14474 | 0.014413 | 0.093298 | 0.011602 | 0.11866 | 0.09931 | -0.048989 | 60.278 | 60.3319 | 60.3238 | 60.2819 | 61.2126 | 61.1908 | 60.8865 | 61.1109 | -0.93462 | -0.60853 | -0.88885 | -0.56276
213.9062 | 121.7651 | -61.0886 | 60.4523 | 0.089802 | -0.026784 | 0.038365 | -0.034174 | 0.086622 | 0.053534 | -0.094765 | 60.2231 | 60.2815 | 60.2826 | 60.2361 | 61.1577 | 61.1404 | 60.8408 | 61.0605 | 0.13558 | 0.018992 | 0.084141 | 0.011602 | 0.1324 | 0.09931 | -0.048989 | 60.2688 | 60.3273 | 60.3284 | 60.2819 | 61.2035 | 61.1862 | 60.8865 | 61.1063 | -0.93462 | -0.61769 | -0.87511 | -0.55818
215.5938 | 121.7651 | -61.084 | 60.4568 | 0.10354 | -0.026784 | 0.042944 | -0.034174 | 0.077466 | 0.058113 | -0.099343 | 60.2276 | 60.2815 | 60.2826 | 60.2407 | 61.1577 | 61.1404 | 60.8362 | 61.0651 | 0.14931 | 0.018992 | 0.08872 | 0.011602 | 0.12324 | 0.10389 | -0.053567 | 60.2734 | 60.3273 | 60.3284 | 60.2865 | 61.2035 | 61.1862 | 60.882 | 61.1109 | -0.93004 | -0.60853 | -0.87511 | -0.5536
217.3438 | 121.788 | -61.1069 | 60.4111 | 0.094381 | -0.026784 | 0.042944 | -0.025017 | 0.077466 | 0.058113 | -0.090186 | 60.2185 | 60.2815 | 60.278 | 60.2315 | 61.1577 | 61.1404 | 60.8408 | 61.0605 | 0.14016 | 0.018992 | 0.08872 | 0.020759 | 0.12324 | 0.10389 | -0.04441 | 60.2643 | 60.3273 | 60.3238 | 60.2773 | 61.2035 | 61.1862 | 60.8865 | 61.1063 | -0.9392 | -0.62227 | -0.87969 | -0.56276
219.0469 | 121.7056 | -61.0565 | 60.5164 | 0.098959 | -0.026784 | 0.042944 | -0.029595 | 0.072888 | 0.058113 | -0.094765 | 60.2276 | 60.2952 | 60.2826 | 60.2361 | 61.1577 | 61.1404 | 60.8408 | 61.0651 | 0.14474 | 0.018992 | 0.08872 | 0.016181 | 0.11866 | 0.10389 | -0.048989 | 60.2734 | 60.341 | 60.3284 | 60.2819 | 61.2035 | 61.1862 | 60.8865 | 61.1109 | -0.93004 | -0.61311 | -0.87511 | -0.55818
220.7344 | 121.8063 | -61.0703 | 60.4156 | 0.10354 | -0.031363 | 0.042944 | -0.034174 | 0.072888 | 0.053534 | -0.099343 | 60.2185 | 60.2723 | 60.2826 | 60.2361 | 61.1577 | 61.1404 | 60.8453 | 61.0651 | 0.14931 | 0.014413 | 0.08872 | 0.011602 | 0.11866 | 0.09931 | -0.053567 | 60.2643 | 60.3181 | 60.3284 | 60.2819 | 61.2035 | 61.1862 | 60.8911 | 61.1109 | -0.9392 | -0.62685 | -0.87511 | -0.56276
222.4375 | 121.8704 | -61.0291 | 60.4706 | 0.10354 | -0.026784 | 0.042944 | -0.034174 | 0.082044 | 0.053534 | -0.099343 | 60.2231 | 60.2815 | 60.278 | 60.2361 | 61.1623 | 61.1404 | 60.8453 | 61.0651 | 0.14931 | 0.018992 | 0.08872 | 0.011602 | 0.12782 | 0.09931 | -0.053567 | 60.2688 | 60.3273 | 60.3238 | 60.2819 | 61.208 | 61.1862 | 60.8911 | 61.1109 | -0.9392 | -0.62227 | -0.88427 | -0.56734
224.25 | 121.7422 | -61.1343 | 60.3836 | 0.098959 | -0.022205 | 0.042944 | -0.029595 | 0.077466 | 0.048956 | -0.094765 | 60.2276 | 60.2861 | 60.278 | 60.2361 | 61.1623 | 61.1358 | 60.827 | 61.0605 | 0.14474 | 0.023571 | 0.08872 | 0.016181 | 0.12324 | 0.094732 | -0.048989 | 60.2734 | 60.3319 | 60.3238 | 60.2819 | 61.208 | 61.1816 | 60.8728 | 61.1063 | -0.93462 | -0.59938 | -0.88427 | -0.54902
226.0156 | 121.8475 | -61.0886 | 60.379 | 0.10354 | -0.031363 | 0.042944 | -0.034174 | 0.077466 | 0.044377 | -0.099343 | 60.2231 | 60.2861 | 60.2872 | 60.2361 | 61.1668 | 61.1404 | 60.8408 | 61.0605 | 0.14931 | 0.014413 | 0.08872 | 0.011602 | 0.12324 | 0.090153 | -0.053567 | 60.2688 | 60.3319 | 60.3329 | 60.2819 | 61.2126 | 61.1862 | 60.8865 | 61.1063 | -0.94378 | -0.61769 | -0.87969 | -0.5536
227.7969 | 121.7377 | -61.1206 | 60.4568 | 0.098959 | -0.026784 | 0.038365 | -0.034174 | 0.082044 | 0.053534 | -0.094765 | 60.2231 | 60.2815 | 60.2826 | 60.227 | 61.1623 | 61.1358 | 60.8362 | 61.0651 | 0.14474 | 0.018992 | 0.084141 | 0.011602 | 0.12782 | 0.09931 | -0.048989 | 60.2688 | 60.3273 | 60.3284 | 60.2727 | 61.208 | 61.1816 | 60.882 | 61.1109 | -0.9392 | -0.61311 | -0.87969 | -0.5536
229.4844 | 121.7468 | -61.0794 | 60.4614 | 0.10354 | -0.026784 | 0.038365 | -0.034174 | 0.077466 | 0.053534 | -0.090186 | 60.2185 | 60.2907 | 60.278 | 60.2315 | 61.1623 | 61.145 | 60.8362 | 61.0605 | 0.14931 | 0.018992 | 0.084141 | 0.011602 | 0.12324 | 0.09931 | -0.04441 | 60.2643 | 60.3364 | 60.3238 | 60.2773 | 61.208 | 61.1908 | 60.882 | 61.1063 | -0.94378 | -0.61769 | -0.88427 | -0.55818
231.25 | 121.7789 | -61.0748 | 60.4111 | 0.098959 | -0.031363 | 0.038365 | -0.034174 | 0.072888 | 0.058113 | -0.094765 | 60.2231 | 60.2907 | 60.278 | 60.2315 | 61.1623 | 61.1404 | 60.8362 | 61.0605 | 0.14474 | 0.014413 | 0.084141 | 0.011602 | 0.11866 | 0.10389 | -0.048989 | 60.2688 | 60.3364 | 60.3238 | 60.2773 | 61.208 | 61.1862 | 60.882 | 61.1063 | -0.9392 | -0.61311 | -0.88427 | -0.55818
233.0156 | 121.7972 | -61.0977 | 60.3973 | 0.094381 | -0.035942 | 0.042944 | -0.038752 | 0.077466 | 0.048956 | -0.094765 | 60.2276 | 60.2769 | 60.2826 | 60.2315 | 61.1531 | 61.1404 | 60.8316 | 61.0559 | 0.14016 | 0.009834 | 0.08872 | 0.007024 | 0.12324 | 0.094732 | -0.048989 | 60.2734 | 60.3227 | 60.3284 | 60.2773 | 61.1989 | 61.1862 | 60.8774 | 61.1017 | -0.92546 | -0.60395 | -0.87054 | -0.54903
234.7031 | 121.8201 | -61.0977 | 60.3745 | 0.10354 | -0.031363 | 0.038365 | -0.034174 | 0.072888 | 0.048956 | -0.094765 | 60.2276 | 60.2861 | 60.2826 | 60.2315 | 61.1577 | 61.1404 | 60.8362 | 61.0559 | 0.14931 | 0.014413 | 0.084141 | 0.011602 | 0.11866 | 0.094732 | -0.048989 | 60.2734 | 60.3319 | 60.3284 | 60.2773 | 61.2035 | 61.1862 | 60.882 | 61.1017 | -0.93004 | -0.60853 | -0.87511 | -0.5536
236.4531 | 121.7972 | -61.0291 | 60.4706 | 0.094381 | -0.040521 | 0.047522 | -0.034174 | 0.072888 | 0.053534 | -0.099343 | 60.2231 | 60.2861 | 60.2872 | 60.227 | 61.1623 | 61.1404 | 60.8316 | 61.0605 | 0.14016 | 0.005255 | 0.093298 | 0.011602 | 0.11866 | 0.09931 | -0.053567 | 60.2688 | 60.3319 | 60.3329 | 60.2727 | 61.208 | 61.1862 | 60.8774 | 61.1063 | -0.9392 | -0.60853 | -0.87511 | -0.54445
238.2344 | 121.8018 | -61.0703 | 60.4202 | 0.10354 | -0.035942 | 0.038365 | -0.029595 | 0.077466 | 0.048956 | -0.10392 | 60.2185 | 60.2815 | 60.2826 | 60.227 | 61.1623 | 61.1358 | 60.8362 | 61.0697 | 0.14931 | 0.009834 | 0.084141 | 0.016181 | 0.12324 | 0.094732 | -0.058145 | 60.2643 | 60.3273 | 60.3284 | 60.2727 | 61.208 | 61.1816 | 60.882 | 61.1154 | -0.94378 | -0.61769 | -0.87969 | -0.5536
239.9844 | 121.7972 | -61.0794 | 60.4111 | 0.098959 | -0.031363 | 0.047522 | -0.029595 | 0.077466 | 0.058113 | -0.090186 | 60.2231 | 60.2861 | 60.278 | 60.2361 | 61.1623 | 61.1404 | 60.8408 | 61.0605 | 0.14474 | 0.014413 | 0.093298 | 0.016181 | 0.12324 | 0.10389 | -0.04441 | 60.2688 | 60.3319 | 60.3238 | 60.2819 | 61.208 | 61.1862 | 60.8865 | 61.1063 | -0.9392 | -0.61769 | -0.88427 | -0.56276
241.6719 | 121.8475 | -61.0382 | 60.4477 | 0.098959 | -0.035942 | 0.047522 | -0.043331 | 0.077466 | 0.048956 | -0.094765 | 60.2276 | 60.2861 | 60.2826 | 60.2315 | 61.1668 | 61.1358 | 60.8362 | 61.0651 | 0.14474 | 0.009834 | 0.093298 | 0.002445 | 0.12324 | 0.094732 | -0.048989 | 60.2734 | 60.3319 | 60.3284 | 60.2773 | 61.2126 | 61.1816 | 60.882 | 61.1109 | -0.9392 | -0.60853 | -0.88427 | -0.5536
243.4375 | 121.7514 | -61.1206 | 60.3882 | 0.098959 | -0.026784 | 0.038365 | -0.038752 | 0.06831 | 0.062691 | -0.099343 | 60.2276 | 60.2861 | 60.278 | 60.2361 | 61.1623 | 61.1358 | 60.8316 | 61.0559 | 0.14474 | 0.018992 | 0.084141 | 0.007024 | 0.11409 | 0.10847 | -0.053567 | 60.2734 | 60.3319 | 60.3238 | 60.2819 | 61.208 | 61.1816 | 60.8774 | 61.1017 | -0.93462 | -0.60395 | -0.88427 | -0.5536
245.1875 | 121.788 | -61.0977 | 60.4248 | 0.094381 | -0.026784 | 0.047522 | -0.034174 | 0.06831 | 0.053534 | -0.099343 | 60.2185 | 60.2815 | 60.2826 | 60.2361 | 61.1531 | 61.1358 | 60.8316 | 61.0651 | 0.14016 | 0.018992 | 0.093298 | 0.011602 | 0.11409 | 0.09931 | -0.053567 | 60.2643 | 60.3273 | 60.3284 | 60.2819 | 61.1989 | 61.1816 | 60.8774 | 61.1109 | -0.93462 | -0.61311 | -0.87054 | -0.54903
246.8906 | 121.7468 | -61.0519 | 60.4797 | 0.089802 | -0.026784 | 0.042944 | -0.038752 | 0.072888 | 0.053534 | -0.094765 | 60.2185 | 60.2815 | 60.2734 | 60.2361 | 61.1577 | 61.1404 | 60.8316 | 61.0559 | 0.13558 | 0.018992 | 0.08872 | 0.007024 | 0.11866 | 0.09931 | -0.048989 | 60.2643 | 60.3273 | 60.3192 | 60.2819 | 61.2035 | 61.1862 | 60.8774 | 61.1017 | -0.9392 | -0.61311 | -0.88427 | -0.55818
248.6406 | 121.8613 | -61.0245 | 60.466 | 0.089802 | -0.026784 | 0.038365 | -0.034174 | 0.072888 | 0.058113 | -0.094765 | 60.2185 | 60.2861 | 60.2826 | 60.2224 | 61.1531 | 61.1358 | 60.8362 | 61.0605 | 0.13558 | 0.018992 | 0.084141 | 0.011602 | 0.11866 | 0.10389 | -0.048989 | 60.2643 | 60.3319 | 60.3284 | 60.2682 | 61.1989 | 61.1816 | 60.882 | 61.1063 | -0.93462 | -0.61769 | -0.87054 | -0.5536
250.3438 | 121.6965 | -61.0931 | 60.4385 | 0.10354 | -0.031363 | 0.042944 | -0.029595 | 0.082044 | 0.053534 | -0.099343 | 60.2185 | 60.2769 | 60.278 | 60.2361 | 61.1531 | 61.1404 | 60.8316 | 61.0651 | 0.14931 | 0.014413 | 0.08872 | 0.016181 | 0.12782 | 0.09931 | -0.053567 | 60.2643 | 60.3227 | 60.3238 | 60.2819 | 61.1989 | 61.1862 | 60.8774 | 61.1109 | -0.93462 | -0.61311 | -0.87511 | -0.5536
252.1094 | 121.701 | -61.0657 | 60.5072 | 0.094381 | -0.026784 | 0.042944 | -0.034174 | 0.077466 | 0.053534 | -0.099343 | 60.2231 | 60.2815 | 60.278 | 60.2315 | 61.1531 | 61.1358 | 60.8316 | 61.0605 | 0.14016 | 0.018992 | 0.08872 | 0.011602 | 0.12324 | 0.09931 | -0.053567 | 60.2688 | 60.3273 | 60.3238 | 60.2773 | 61.1989 | 61.1816 | 60.8774 | 61.1063 | -0.93004 | -0.60853 | -0.87511 | -0.5536
253.8594 | 121.7239 | -61.1114 | 60.4385 | 0.094381 | -0.022205 | 0.042944 | -0.038752 | 0.082044 | 0.058113 | -0.090186 | 60.2322 | 60.2769 | 60.2826 | 60.2361 | 61.1577 | 61.1358 | 60.8362 | 61.0559 | 0.14016 | 0.023571 | 0.08872 | 0.007024 | 0.12782 | 0.10389 | -0.04441 | 60.278 | 60.3227 | 60.3284 | 60.2819 | 61.2035 | 61.1816 | 60.882 | 61.1017 | -0.92546 | -0.60395 | -0.87511 | -0.5536
255.5469 | 121.7102 | -61.1389 | 60.4156 | 0.094381 | -0.026784 | 0.047522 | -0.029595 | 0.06831 | 0.058113 | -0.085608 | 60.2231 | 60.2769 | 60.278 | 60.2315 | 61.1577 | 61.1404 | 60.8316 | 61.0559 | 0.14016 | 0.018992 | 0.093298 | 0.016181 | 0.11409 | 0.10389 | -0.039832 | 60.2688 | 60.3227 | 60.3238 | 60.2773 | 61.2035 | 61.1862 | 60.8774 | 61.1017 | -0.93462 | -0.60853 | -0.87969 | -0.5536
257.2969 | 121.7285 | -61.1343 | 60.4248 | 0.10812 | -0.035942 | 0.038365 | -0.034174 | 0.072888 | 0.058113 | -0.099343 | 60.2139 | 60.2815 | 60.278 | 60.2361 | 61.1485 | 61.1358 | 60.827 | 61.0559 | 0.15389 | 0.009834 | 0.084141 | 0.011602 | 0.11866 | 0.10389 | -0.053567 | 60.2597 | 60.3273 | 60.3238 | 60.2819 | 61.1943 | 61.1816 | 60.8728 | 61.1017 | -0.93462 | -0.61311 | -0.87053 | -0.54902
259 | 121.756 | -61.0565 | 60.4568 | 0.089802 | -0.022205 | 0.042944 | -0.038752 | 0.072888 | 0.053534 | -0.094765 | 60.2139 | 60.2769 | 60.2826 | 60.2315 | 61.1577 | 61.1358 | 60.8316 | 61.0559 | 0.13558 | 0.023571 | 0.08872 | 0.007024 | 0.11866 | 0.09931 | -0.048989 | 60.2597 | 60.3227 | 60.3284 | 60.2773 | 61.2035 | 61.1816 | 60.8774 | 61.1017 | -0.94378 | -0.61769 | -0.87511 | -0.54903
260.7031 | 121.701 | -61.1252 | 60.4248 | 0.098959 | -0.017627 | 0.038365 | -0.034174 | 0.072888 | 0.058113 | -0.099343 | 60.2185 | 60.2815 | 60.2826 | 60.2315 | 61.1577 | 61.1358 | 60.827 | 61.0605 | 0.14474 | 0.028149 | 0.084141 | 0.011602 | 0.11866 | 0.10389 | -0.053567 | 60.2643 | 60.3273 | 60.3284 | 60.2773 | 61.2035 | 61.1816 | 60.8728 | 61.1063 | -0.9392 | -0.60853 | -0.87511 | -0.54445
262.4688 | 121.7789 | -61.084 | 60.3882 | 0.094381 | -0.035942 | 0.042944 | -0.034174 | 0.072888 | 0.058113 | -0.099343 | 60.2231 | 60.2769 | 60.2734 | 60.2315 | 61.1577 | 61.1312 | 60.8408 | 61.0559 | 0.14016 | 0.009834 | 0.08872 | 0.011602 | 0.11866 | 0.10389 | -0.053567 | 60.2688 | 60.3227 | 60.3192 | 60.2773 | 61.2035 | 61.177 | 60.8865 | 61.1017 | -0.93462 | -0.61769 | -0.88427 | -0.56734
264.1719 | 121.7606 | -61.0931 | 60.4477 | 0.10354 | -0.026784 | 0.042944 | -0.034174 | 0.082044 | 0.058113 | -0.094765 | 60.2185 | 60.2769 | 60.2734 | 60.2361 | 61.1531 | 61.1221 | 60.8316 | 61.0513 | 0.14931 | 0.018992 | 0.08872 | 0.011602 | 0.12782 | 0.10389 | -0.048989 | 60.2643 | 60.3227 | 60.3192 | 60.2819 | 61.1989 | 61.1679 | 60.8774 | 61.0971 | -0.93462 | -0.61311 | -0.87969 | -0.55818
265.875 | 121.8201 | -61.084 | 60.3561 | 0.098959 | -0.022205 | 0.047522 | -0.034174 | 0.072888 | 0.048956 | -0.099343 | 60.2231 | 60.2861 | 60.2826 | 60.227 | 61.1623 | 61.1312 | 60.8316 | 61.0605 | 0.14474 | 0.023571 | 0.093298 | 0.011602 | 0.11866 | 0.094732 | -0.053567 | 60.2688 | 60.3319 | 60.3284 | 60.2727 | 61.208 | 61.177 | 60.8774 | 61.1063 | -0.9392 | -0.60853 | -0.87969 | -0.54903
267.5781 | 121.7468 | -61.0794 | 60.466 | 0.098959 | -0.026784 | 0.052101 | -0.034174 | 0.086622 | 0.062691 | -0.090186 | 60.2185 | 60.2678 | 60.2826 | 60.2315 | 61.1577 | 61.1312 | 60.8316 | 61.0605 | 0.14474 | 0.018992 | 0.097877 | 0.011602 | 0.1324 | 0.10847 | -0.04441 | 60.2643 | 60.3135 | 60.3284 | 60.2773 | 61.2035 | 61.177 | 60.8774 | 61.1063 | -0.9392 | -0.61311 | -0.87511 | -0.54903
269.3281 | 121.8292 | -61.0611 | 60.379 | 0.098959 | -0.022205 | 0.042944 | -0.034174 | 0.072888 | 0.048956 | -0.099343 | 60.2231 | 60.2815 | 60.2872 | 60.2315 | 61.1531 | 61.1267 | 60.8224 | 61.0605 | 0.14474 | 0.023571 | 0.08872 | 0.011602 | 0.11866 | 0.094732 | -0.053567 | 60.2688 | 60.3273 | 60.3329 | 60.2773 | 61.1989 | 61.1724 | 60.8682 | 61.1063 | -0.93004 | -0.59937 | -0.86596 | -0.53529
271.0938 | 121.8155 | -61.084 | 60.4019 | 0.098959 | -0.026784 | 0.038365 | -0.029595 | 0.086622 | 0.048956 | -0.094765 | 60.2231 | 60.2815 | 60.2734 | 60.227 | 61.1531 | 61.1358 | 60.827 | 61.0513 | 0.14474 | 0.018992 | 0.084141 | 0.016181 | 0.1324 | 0.094732 | -0.048989 | 60.2688 | 60.3273 | 60.3192 | 60.2727 | 61.1989 | 61.1816 | 60.8728 | 61.0971 | -0.93004 | -0.60395 | -0.87969 | -0.5536
272.7969 | 121.7743 | -61.1069 | 60.4019 | 0.089802 | -0.022205 | 0.042944 | -0.034174 | 0.072888 | 0.053534 | -0.090186 | 60.2231 | 60.2769 | 60.2826 | 60.2315 | 61.1531 | 61.1358 | 60.8224 | 61.0559 | 0.13558 | 0.023571 | 0.08872 | 0.011602 | 0.11866 | 0.09931 | -0.04441 | 60.2688 | 60.3227 | 60.3284 | 60.2773 | 61.1989 | 61.1816 | 60.8682 | 61.1017 | -0.93004 | -0.59937 | -0.87054 | -0.53987
274.4844 | 121.6782 | -61.116 | 60.434 | 0.10354 | -0.026784 | 0.047522 | -0.034174 | 0.077466 | 0.053534 | -0.094765 | 60.2231 | 60.2769 | 60.2734 | 60.2224 | 61.1531 | 61.1312 | 60.827 | 61.0513 | 0.14931 | 0.018992 | 0.093298 | 0.011602 | 0.12324 | 0.09931 | -0.048989 | 60.2688 | 60.3227 | 60.3192 | 60.2682 | 61.1989 | 61.177 | 60.8728 | 61.0971 | -0.93004 | -0.60395 | -0.87969 | -0.5536
276.2656 | 121.8063 | -61.0199 | 60.4706 | 0.094381 | -0.026784 | 0.047522 | -0.029595 | 0.077466 | 0.048956 | -0.094765 | 60.2185 | 60.2769 | 60.2826 | 60.2315 | 61.1485 | 61.1312 | 60.8316 | 61.0513 | 0.14016 | 0.018992 | 0.093298 | 0.016181 | 0.12324 | 0.094732 | -0.048989 | 60.2643 | 60.3227 | 60.3284 | 60.2773 | 61.1943 | 61.177 | 60.8774 | 61.0971 | -0.93004 | -0.61311 | -0.86596 | -0.54903
278.0469 | 121.7972 | -61.0703 | 60.4065 | 0.098959 | -0.026784 | 0.042944 | -0.038752 | 0.077466 | 0.053534 | -0.094765 | 60.2185 | 60.2723 | 60.278 | 60.2315 | 61.1577 | 61.1267 | 60.827 | 61.0605 | 0.14474 | 0.018992 | 0.08872 | 0.007024 | 0.12324 | 0.09931 | -0.048989 | 60.2643 | 60.3181 | 60.3238 | 60.2773 | 61.2035 | 61.1724 | 60.8728 | 61.1063 | -0.9392 | -0.60853 | -0.87969 | -0.54902
279.75 | 121.6873 | -61.116 | 60.4431 | 0.094381 | -0.022205 | 0.042944 | -0.034174 | 0.077466 | 0.048956 | -0.099343 | 60.2185 | 60.2723 | 60.278 | 60.227 | 61.1531 | 61.1267 | 60.8224 | 61.0513 | 0.14016 | 0.023571 | 0.08872 | 0.011602 | 0.12324 | 0.094732 | -0.053567 | 60.2643 | 60.3181 | 60.3238 | 60.2727 | 61.1989 | 61.1724 | 60.8682 | 61.0971 | -0.93462 | -0.60395 | -0.87511 | -0.54445
281.5 | 121.6873 | -61.116 | 60.4202 | 0.094381 | -0.026784 | 0.042944 | -0.029595 | 0.077466 | 0.053534 | -0.090186 | 60.2185 | 60.2769 | 60.278 | 60.2315 | 61.1531 | 61.1312 | 60.8224 | 61.0559 | 0.14016 | 0.018992 | 0.08872 | 0.016181 | 0.12324 | 0.09931 | -0.04441 | 60.2643 | 60.3227 | 60.3238 | 60.2773 | 61.1989 | 61.177 | 60.8682 | 61.1017 | -0.93462 | -0.60395 | -0.87511 | -0.54445
283.2812 | 121.8246 | -61.0062 | 60.4477 | 0.094381 | -0.026784 | 0.042944 | -0.034174 | 0.072888 | 0.044377 | -0.090186 | 60.2185 | 60.2815 | 60.278 | 60.227 | 61.1485 | 61.1267 | 60.8224 | 61.0513 | 0.14016 | 0.018992 | 0.08872 | 0.011602 | 0.11866 | 0.090153 | -0.04441 | 60.2643 | 60.3273 | 60.3238 | 60.2727 | 61.1943 | 61.1724 | 60.8682 | 61.0971 | -0.93004 | -0.60395 | -0.87053 | -0.54445
285.0469 | 121.7331 | -61.0657 | 60.5026 | 0.098959 | -0.035942 | 0.047522 | -0.034174 | 0.082044 | 0.053534 | -0.094765 | 60.2185 | 60.2678 | 60.2826 | 60.2315 | 61.1485 | 61.1267 | 60.8224 | 61.0513 | 0.14474 | 0.009834 | 0.093298 | 0.011602 | 0.12782 | 0.09931 | -0.048989 | 60.2643 | 60.3135 | 60.3284 | 60.2773 | 61.1943 | 61.1724 | 60.8682 | 61.0971 | -0.93004 | -0.60395 | -0.86596 | -0.53987
286.75 | 121.7972 | -61.0748 | 60.434 | 0.098959 | -0.026784 | 0.042944 | -0.029595 | 0.072888 | 0.048956 | -0.094765 | 60.2231 | 60.2769 | 60.2688 | 60.227 | 61.1531 | 61.1267 | 60.827 | 61.0468 | 0.14474 | 0.018992 | 0.08872 | 0.016181 | 0.11866 | 0.094732 | -0.048989 | 60.2688 | 60.3227 | 60.3146 | 60.2727 | 61.1989 | 61.1724 | 60.8728 | 61.0925 | -0.93004 | -0.60395 | -0.88427 | -0.55818
288.5 | 121.7102 | -61.0977 | 60.4065 | 0.10812 | -0.026784 | 0.052101 | -0.025017 | 0.086622 | 0.048956 | -0.090186 | 60.2185 | 60.2723 | 60.278 | 60.227 | 61.1531 | 61.1312 | 60.8179 | 61.0513 | 0.15389 | 0.018992 | 0.097877 | 0.020759 | 0.1324 | 0.094732 | -0.04441 | 60.2643 | 60.3181 | 60.3238 | 60.2727 | 61.1989 | 61.177 | 60.8636 | 61.0971 | -0.93462 | -0.59938 | -0.87511 | -0.53987
290.2969 | 121.7468 | -61.0886 | 60.4431 | 0.094381 | -0.031363 | 0.042944 | -0.034174 | 0.072888 | 0.044377 | -0.099343 | 60.2185 | 60.2815 | 60.2734 | 60.2361 | 61.1531 | 61.1312 | 60.8224 | 61.0513 | 0.14016 | 0.014413 | 0.08872 | 0.011602 | 0.11866 | 0.090153 | -0.053567 | 60.2643 | 60.3273 | 60.3192 | 60.2819 | 61.1989 | 61.177 | 60.8682 | 61.0971 | -0.93462 | -0.60395 | -0.87969 | -0.54903
292.0625 | 121.8155 | -61.0977 | 60.3561 | 0.094381 | -0.022205 | 0.042944 | -0.029595 | 0.077466 | 0.053534 | -0.099343 | 60.2139 | 60.2861 | 60.278 | 60.2224 | 61.1485 | 61.1221 | 60.827 | 61.0559 | 0.14016 | 0.023571 | 0.08872 | 0.016181 | 0.12324 | 0.09931 | -0.053567 | 60.2597 | 60.3319 | 60.3238 | 60.2682 | 61.1943 | 61.1679 | 60.8728 | 61.1017 | -0.93462 | -0.61311 | -0.87053 | -0.54902
293.8281 | 121.7194 | -61.0931 | 60.434 | 0.10354 | -0.022205 | 0.047522 | -0.043331 | 0.077466 | 0.053534 | -0.099343 | 60.2185 | 60.2769 | 60.2826 | 60.2224 | 61.1485 | 61.1312 | 60.8316 | 61.0513 | 0.14931 | 0.023571 | 0.093298 | 0.002445 | 0.12324 | 0.09931 | -0.053567 | 60.2643 | 60.3227 | 60.3284 | 60.2682 | 61.1943 | 61.177 | 60.8774 | 61.0971 | -0.93004 | -0.61311 | -0.86596 | -0.54903
295.5156 | 121.7697 | -61.0931 | 60.3699 | 0.098959 | -0.031363 | 0.052101 | -0.034174 | 0.072888 | 0.048956 | -0.094765 | 60.2185 | 60.2723 | 60.2734 | 60.227 | 61.1531 | 61.1267 | 60.8224 | 61.0513 | 0.14474 | 0.014413 | 0.097877 | 0.011602 | 0.11866 | 0.094732 | -0.048989 | 60.2643 | 60.3181 | 60.3192 | 60.2727 | 61.1989 | 61.1724 | 60.8682 | 61.0971 | -0.93462 | -0.60395 | -0.87969 | -0.54903
297.2812 | 121.8613 | -61.0245 | 60.4294 | 0.098959 | -0.026784 | 0.042944 | -0.034174 | 0.072888 | 0.035221 | -0.099343 | 60.2185 | 60.2678 | 60.278 | 60.2224 | 61.1531 | 61.1312 | 60.8179 | 61.0559 | 0.14474 | 0.018992 | 0.08872 | 0.011602 | 0.11866 | 0.080997 | -0.053567 | 60.2643 | 60.3135 | 60.3238 | 60.2682 | 61.1989 | 61.177 | 60.8636 | 61.1017 | -0.93462 | -0.59938 | -0.87511 | -0.53987
299.0469 | 121.669 | -61.116 | 60.4111 | 0.098959 | -0.026784 | 0.038365 | -0.034174 | 0.077466 | 0.053534 | -0.090186 | 60.2093 | 60.2769 | 60.278 | 60.227 | 61.1485 | 61.1312 | 60.8224 | 61.0513 | 0.14474 | 0.018992 | 0.084141 | 0.011602 | 0.12324 | 0.09931 | -0.04441 | 60.2551 | 60.3227 | 60.3238 | 60.2727 | 61.1943 | 61.177 | 60.8682 | 61.0971 | -0.9392 | -0.61311 | -0.87053 | -0.54445
300.75 | 121.8201 | -61.0153 | 60.4202 | 0.10354 | -0.017627 | 0.047522 | -0.034174 | 0.072888 | 0.048956 | -0.090186 | 60.2185 | 60.2723 | 60.2734 | 60.2315 | 61.144 | 61.1267 | 60.8316 | 61.0468 | 0.14931 | 0.028149 | 0.093298 | 0.011602 | 0.11866 | 0.094732 | -0.04441 | 60.2643 | 60.3181 | 60.3192 | 60.2773 | 61.1897 | 61.1724 | 60.8774 | 61.0925 | -0.92546 | -0.61311 | -0.87054 | -0.55818
302.4531 | 121.6919 | -61.1114 | 60.4202 | 0.10354 | -0.022205 | 0.042944 | -0.029595 | 0.082044 | 0.058113 | -0.090186 | 60.2185 | 60.2769 | 60.278 | 60.2315 | 61.144 | 61.1221 | 60.8179 | 61.0513 | 0.14931 | 0.023571 | 0.08872 | 0.016181 | 0.12782 | 0.10389 | -0.04441 | 60.2643 | 60.3227 | 60.3238 | 60.2773 | 61.1897 | 61.1679 | 60.8636 | 61.0971 | -0.92546 | -0.59938 | -0.86596 | -0.53987
304.1562 | 121.8109 | -61.0886 | 60.379 | 0.098959 | -0.022205 | 0.038365 | -0.034174 | 0.077466 | 0.044377 | -0.090186 | 60.2231 | 60.2678 | 60.2826 | 60.227 | 61.1485 | 61.1221 | 60.8179 | 61.0513 | 0.14474 | 0.023571 | 0.084141 | 0.011602 | 0.12324 | 0.090153 | -0.04441 | 60.2688 | 60.3135 | 60.3284 | 60.2727 | 61.1943 | 61.1679 | 60.8636 | 61.0971 | -0.92546 | -0.5948 | -0.86596 | -0.53529
305.9062 | 121.8155 | -61.0886 | 60.3561 | 0.098959 | -0.026784 | 0.042944 | -0.034174 | 0.077466 | 0.058113 | -0.094765 | 60.2185 | 60.2723 | 60.2826 | 60.227 | 61.1531 | 61.1267 | 60.8224 | 61.0513 | 0.14474 | 0.018992 | 0.08872 | 0.011602 | 0.12324 | 0.10389 | -0.048989 | 60.2643 | 60.3181 | 60.3284 | 60.2727 | 61.1989 | 61.1724 | 60.8682 | 61.0971 | -0.93462 | -0.60395 | -0.87054 | -0.53987
307.6094 | 121.6873 | -61.0428 | 60.4477 | 0.089802 | -0.026784 | 0.038365 | -0.034174 | 0.06831 | 0.058113 | -0.090186 | 60.2185 | 60.2769 | 60.278 | 60.227 | 61.1485 | 61.1267 | 60.8133 | 61.0422 | 0.13558 | 0.018992 | 0.084141 | 0.011602 | 0.11409 | 0.10389 | -0.04441 | 60.2643 | 60.3227 | 60.3238 | 60.2727 | 61.1943 | 61.1724 | 60.8591 | 61.088 | -0.93004 | -0.5948 | -0.87053 | -0.53529
309.375 | 121.6827 | -61.0336 | 60.4614 | 0.098959 | -0.022205 | 0.042944 | -0.034174 | 0.082044 | 0.058113 | -0.090186 | 60.2185 | 60.2723 | 60.2734 | 60.2315 | 61.1485 | 61.1221 | 60.8179 | 61.0468 | 0.14474 | 0.023571 | 0.08872 | 0.011602 | 0.12782 | 0.10389 | -0.04441 | 60.2643 | 60.3181 | 60.3192 | 60.2773 | 61.1943 | 61.1679 | 60.8636 | 61.0925 | -0.93004 | -0.59938 | -0.87511 | -0.54445
311.1406 | 121.8155 | -61.0748 | 60.3607 | 0.098959 | -0.022205 | 0.042944 | -0.029595 | 0.082044 | 0.048956 | -0.094765 | 60.2139 | 60.2769 | 60.278 | 60.2315 | 61.144 | 61.1221 | 60.8179 | 61.0422 | 0.14474 | 0.023571 | 0.08872 | 0.016181 | 0.12782 | 0.094732 | -0.048989 | 60.2597 | 60.3227 | 60.3238 | 60.2773 | 61.1897 | 61.1679 | 60.8636 | 61.088 | -0.93004 | -0.60395 | -0.86596 | -0.53987
312.9062 | 121.7926 | -61.0794 | 60.3561 | 0.10354 | -0.026784 | 0.042944 | -0.029595 | 0.072888 | 0.048956 | -0.099343 | 60.2185 | 60.2723 | 60.2734 | 60.227 | 61.144 | 61.1175 | 60.8224 | 61.0513 | 0.14931 | 0.018992 | 0.08872 | 0.016181 | 0.11866 | 0.094732 | -0.053567 | 60.2643 | 60.3181 | 60.3192 | 60.2727 | 61.1897 | 61.1633 | 60.8682 | 61.0971 | -0.92546 | -0.60395 | -0.87054 | -0.54903
314.5938 | 121.7743 | -61.0748 | 60.4065 | 0.094381 | -0.017627 | 0.042944 | -0.043331 | 0.072888 | 0.053534 | -0.094765 | 60.2185 | 60.2723 | 60.2826 | 60.2315 | 61.1531 | 61.1175 | 60.8133 | 61.0468 | 0.14016 | 0.028149 | 0.08872 | 0.002445 | 0.11866 | 0.09931 | -0.048989 | 60.2643 | 60.3181 | 60.3284 | 60.2773 | 61.1989 | 61.1633 | 60.8591 | 61.0925 | -0.93462 | -0.5948 | -0.87054 | -0.53071
316.3438 | 121.8338 | -61.0016 | 60.4477 | 0.098959 | -0.022205 | 0.038365 | -0.038752 | 0.077466 | 0.053534 | -0.090186 | 60.2139 | 60.2723 | 60.2734 | 60.2224 | 61.1485 | 61.1267 | 60.8179 | 61.0513 | 0.14474 | 0.023571 | 0.084141 | 0.007024 | 0.12324 | 0.09931 | -0.04441 | 60.2597 | 60.3181 | 60.3192 | 60.2682 | 61.1943 | 61.1724 | 60.8636 | 61.0971 | -0.93462 | -0.60395 | -0.87511 | -0.54445
318.1094 | 121.8155 | -61.0336 | 60.4523 | 0.094381 | -0.022205 | 0.042944 | -0.038752 | 0.077466 | 0.048956 | -0.099343 | 60.2231 | 60.2769 | 60.2734 | 60.2315 | 61.1394 | 61.1267 | 60.8133 | 61.0468 | 0.14016 | 0.023571 | 0.08872 | 0.007024 | 0.12324 | 0.094732 | -0.053567 | 60.2688 | 60.3227 | 60.3192 | 60.2773 | 61.1852 | 61.1724 | 60.8591 | 61.0925 | -0.91631 | -0.59022 | -0.86596 | -0.53987
319.875 | 121.7194 | -61.0657 | 60.4523 | 0.089802 | -0.022205 | 0.042944 | -0.034174 | 0.082044 | 0.053534 | -0.099343 | 60.2185 | 60.2769 | 60.2826 | 60.227 | 61.1394 | 61.1221 | 60.8087 | 61.0422 | 0.13558 | 0.023571 | 0.08872 | 0.011602 | 0.12782 | 0.09931 | -0.053567 | 60.2643 | 60.3227 | 60.3284 | 60.2727 | 61.1852 | 61.1679 | 60.8545 | 61.088 | -0.92089 | -0.59022 | -0.8568 | -0.52613
321.5781 | 121.7331 | -61.0291 | 60.4523 | 0.094381 | -0.022205 | 0.042944 | -0.029595 | 0.077466 | 0.058113 | -0.094765 | 60.2231 | 60.2815 | 60.2734 | 60.2315 | 61.144 | 61.1175 | 60.8087 | 61.0422 | 0.14016 | 0.023571 | 0.08872 | 0.016181 | 0.12324 | 0.10389 | -0.048989 | 60.2688 | 60.3273 | 60.3192 | 60.2773 | 61.1897 | 61.1633 | 60.8545 | 61.088 | -0.92088 | -0.58564 | -0.87054 | -0.53529
323.3594 | 121.6736 | -61.0291 | 60.4843 | 0.098959 | -0.017627 | 0.047522 | -0.034174 | 0.082044 | 0.048956 | -0.090186 | 60.2231 | 60.2769 | 60.278 | 60.2315 | 61.1485 | 61.1221 | 60.8087 | 61.0468 | 0.14474 | 0.028149 | 0.093298 | 0.011602 | 0.12782 | 0.094732 | -0.04441 | 60.2688 | 60.3227 | 60.3238 | 60.2773 | 61.1943 | 61.1679 | 60.8545 | 61.0925 | -0.92546 | -0.58564 | -0.87053 | -0.53071
325.1406 | 121.7743 | -61.0291 | 60.4614 | 0.089802 | -0.022205 | 0.038365 | -0.038752 | 0.06831 | 0.053534 | -0.094765 | 60.2139 | 60.2678 | 60.2826 | 60.2315 | 61.1394 | 61.1267 | 60.8133 | 61.0422 | 0.13558 | 0.023571 | 0.084141 | 0.007024 | 0.11409 | 0.09931 | -0.048989 | 60.2597 | 60.3135 | 60.3284 | 60.2773 | 61.1852 | 61.1724 | 60.8591 | 61.088 | -0.92546 | -0.59938 | -0.8568 | -0.53071
326.8438 | 121.8018 | -61.0748 | 60.3836 | 0.094381 | -0.017627 | 0.047522 | -0.038752 | 0.072888 | 0.058113 | -0.094765 | 60.2139 | 60.2769 | 60.2734 | 60.2315 | 61.144 | 61.1175 | 60.8133 | 61.0468 | 0.14016 | 0.028149 | 0.093298 | 0.007024 | 0.11866 | 0.10389 | -0.048989 | 60.2597 | 60.3227 | 60.3192 | 60.2773 | 61.1897 | 61.1633 | 60.8591 | 61.0925 | -0.93004 | -0.59938 | -0.87054 | -0.53987
328.6094 | 121.7926 | -61.0062 | 60.4568 | 0.098959 | -0.022205 | 0.042944 | -0.038752 | 0.077466 | 0.044377 | -0.099343 | 60.2185 | 60.2769 | 60.278 | 60.227 | 61.144 | 61.1221 | 60.8179 | 61.0422 | 0.14474 | 0.023571 | 0.08872 | 0.007024 | 0.12324 | 0.090153 | -0.053567 | 60.2643 | 60.3227 | 60.3238 | 60.2727 | 61.1897 | 61.1679 | 60.8636 | 61.088 | -0.92546 | -0.59938 | -0.86596 | -0.53987
330.375 | 121.6919 | -61.0931 | 60.4248 | 0.10354 | -0.022205 | 0.042944 | -0.034174 | 0.077466 | 0.058113 | -0.094765 | 60.2185 | 60.2769 | 60.2826 | 60.2315 | 61.1348 | 61.1175 | 60.8087 | 61.0422 | 0.14931 | 0.023571 | 0.08872 | 0.011602 | 0.12324 | 0.10389 | -0.048989 | 60.2643 | 60.3227 | 60.3284 | 60.2773 | 61.1806 | 61.1633 | 60.8545 | 61.088 | -0.91631 | -0.59022 | -0.85222 | -0.52613
332.125 | 121.701 | -61.0977 | 60.434 | 0.094381 | -0.022205 | 0.042944 | -0.034174 | 0.06831 | 0.048956 | -0.094765 | 60.2231 | 60.2815 | 60.2826 | 60.2361 | 61.1348 | 61.1175 | 60.8041 | 61.0376 | 0.14016 | 0.023571 | 0.08872 | 0.011602 | 0.11409 | 0.094732 | -0.048989 | 60.2688 | 60.3273 | 60.3284 | 60.2819 | 61.1806 | 61.1633 | 60.8499 | 61.0834 | -0.91173 | -0.58106 | -0.85222 | -0.52155
333.8281 | 121.7422 | -61.0474 | 60.4477 | 0.10354 | -0.017627 | 0.033786 | -0.038752 | 0.082044 | 0.053534 | -0.094765 | 60.2185 | 60.2815 | 60.2826 | 60.2315 | 61.1394 | 61.1175 | 60.8087 | 61.0422 | 0.14931 | 0.028149 | 0.079562 | 0.007024 | 0.12782 | 0.09931 | -0.048989 | 60.2643 | 60.3273 | 60.3284 | 60.2773 | 61.1852 | 61.1633 | 60.8545 | 61.088 | -0.92089 | -0.59022 | -0.8568 | -0.52613
335.5938 | 121.6873 | -61.0886 | 60.4111 | 0.098959 | -0.017627 | 0.042944 | -0.029595 | 0.077466 | 0.058113 | -0.094765 | 60.2231 | 60.2815 | 60.2826 | 60.227 | 61.1394 | 61.1175 | 60.8041 | 61.0422 | 0.14474 | 0.028149 | 0.08872 | 0.016181 | 0.12324 | 0.10389 | -0.048989 | 60.2688 | 60.3273 | 60.3284 | 60.2727 | 61.1852 | 61.1633 | 60.8499 | 61.088 | -0.91631 | -0.58106 | -0.8568 | -0.52155
337.3594 | 121.7285 | -61.0474 | 60.466 | 0.098959 | -0.026784 | 0.042944 | -0.034174 | 0.077466 | 0.053534 | -0.090186 | 60.2231 | 60.2861 | 60.278 | 60.2224 | 61.1394 | 61.1175 | 60.8041 | 61.033 | 0.14474 | 0.018992 | 0.08872 | 0.011602 | 0.12324 | 0.09931 | -0.04441 | 60.2688 | 60.3319 | 60.3238 | 60.2682 | 61.1852 | 61.1633 | 60.8499 | 61.0788 | -0.91631 | -0.58106 | -0.86138 | -0.52613
339.0781 | 121.8246 | -61.0199 | 60.4706 | 0.094381 | -0.022205 | 0.038365 | -0.029595 | 0.072888 | 0.053534 | -0.090186 | 60.2139 | 60.2815 | 60.2826 | 60.2315 | 61.1348 | 61.1221 | 60.8133 | 61.033 | 0.14016 | 0.023571 | 0.084141 | 0.016181 | 0.11866 | 0.09931 | -0.04441 | 60.2597 | 60.3273 | 60.3284 | 60.2773 | 61.1806 | 61.1679 | 60.8591 | 61.0788 | -0.92089 | -0.59938 | -0.85222 | -0.53071
340.8438 | 121.7972 | -61.0611 | 60.3745 | 0.10354 | -0.022205 | 0.038365 | -0.043331 | 0.077466 | 0.048956 | -0.094765 | 60.2276 | 60.2815 | 60.2734 | 60.227 | 61.1394 | 61.1129 | 60.7996 | 61.033 | 0.14931 | 0.023571 | 0.084141 | 0.002445 | 0.12324 | 0.094732 | -0.048989 | 60.2734 | 60.3273 | 60.3192 | 60.2727 | 61.1852 | 61.1587 | 60.8453 | 61.0788 | -0.91173 | -0.57191 | -0.86596 | -0.52613
342.5312 | 121.7697 | -61.0519 | 60.4065 | 0.098959 | -0.031363 | 0.038365 | -0.038752 | 0.077466 | 0.053534 | -0.10392 | 60.2231 | 60.2769 | 60.2826 | 60.2361 | 61.1394 | 61.1084 | 60.8087 | 61.0376 | 0.14474 | 0.014413 | 0.084141 | 0.007024 | 0.12324 | 0.09931 | -0.058145 | 60.2688 | 60.3227 | 60.3284 | 60.2819 | 61.1852 | 61.1541 | 60.8545 | 61.0834 | -0.91631 | -0.58564 | -0.8568 | -0.52613
344.2969 | 121.7972 | -61.0474 | 60.3745 | 0.094381 | -0.026784 | 0.038365 | -0.034174 | 0.063733 | 0.044377 | -0.099343 | 60.2231 | 60.2815 | 60.278 | 60.2178 | 61.1348 | 61.1175 | 60.7996 | 61.0376 | 0.14016 | 0.018992 | 0.084141 | 0.011602 | 0.10951 | 0.090153 | -0.053567 | 60.2688 | 60.3273 | 60.3238 | 60.2636 | 61.1806 | 61.1633 | 60.8453 | 61.0834 | -0.91173 | -0.57648 | -0.8568 | -0.52155
346.0469 | 121.7606 | -61.0519 | 60.3836 | 0.098959 | -0.026784 | 0.042944 | -0.038752 | 0.077466 | 0.053534 | -0.094765 | 60.2231 | 60.2907 | 60.2826 | 60.2407 | 61.1348 | 61.1084 | 60.795 | 61.033 | 0.14474 | 0.018992 | 0.08872 | 0.007024 | 0.12324 | 0.09931 | -0.048989 | 60.2688 | 60.3364 | 60.3284 | 60.2865 | 61.1806 | 61.1541 | 60.8408 | 61.0788 | -0.91173 | -0.57191 | -0.85222 | -0.5124
347.7344 | 121.8292 | -61.0016 | 60.4431 | 0.094381 | -0.026784 | 0.033786 | -0.043331 | 0.06831 | 0.053534 | -0.099343 | 60.2231 | 60.2861 | 60.2826 | 60.2315 | 61.1348 | 61.1129 | 60.8041 | 61.0285 | 0.14016 | 0.018992 | 0.079562 | 0.002445 | 0.11409 | 0.09931 | -0.053567 | 60.2688 | 60.3319 | 60.3284 | 60.2773 | 61.1806 | 61.1587 | 60.8499 | 61.0742 | -0.91173 | -0.58106 | -0.85222 | -0.52155
349.5 | 121.7194 | -61.0657 | 60.4523 | 0.10812 | -0.022205 | 0.038365 | -0.034174 | 0.06831 | 0.058113 | -0.099343 | 60.2276 | 60.2815 | 60.2872 | 60.2361 | 61.1302 | 61.1084 | 60.795 | 61.0285 | 0.15389 | 0.023571 | 0.084141 | 0.011602 | 0.11409 | 0.10389 | -0.053567 | 60.2734 | 60.3273 | 60.3329 | 60.2819 | 61.176 | 61.1541 | 60.8408 | 61.0742 | -0.90257 | -0.56733 | -0.84307 | -0.50782
351.2656 | 121.8155 | -60.9924 | 60.4614 | 0.098959 | -0.031363 | 0.038365 | -0.038752 | 0.072888 | 0.053534 | -0.094765 | 60.2231 | 60.2861 | 60.2872 | 60.2361 | 61.1256 | 61.1129 | 60.7996 | 61.033 | 0.14474 | 0.014413 | 0.084141 | 0.007024 | 0.11866 | 0.09931 | -0.048989 | 60.2688 | 60.3319 | 60.3329 | 60.2819 | 61.1714 | 61.1587 | 60.8453 | 61.0788 | -0.90257 | -0.57648 | -0.83849 | -0.5124
353.0312 | 121.701 | -61.0794 | 60.4385 | 0.10812 | -0.031363 | 0.038365 | -0.034174 | 0.072888 | 0.048956 | -0.094765 | 60.2276 | 60.2769 | 60.2826 | 60.227 | 61.1256 | 61.1175 | 60.7904 | 61.0285 | 0.15389 | 0.014413 | 0.084141 | 0.011602 | 0.11866 | 0.094732 | -0.048989 | 60.2734 | 60.3227 | 60.3284 | 60.2727 | 61.1714 | 61.1633 | 60.8362 | 61.0742 | -0.898 | -0.56275 | -0.84307 | -0.50782
354.7344 | 121.7056 | -61.0245 | 60.4797 | 0.098959 | -0.026784 | 0.038365 | -0.038752 | 0.077466 | 0.048956 | -0.10392 | 60.2276 | 60.2861 | 60.2872 | 60.2407 | 61.1256 | 61.1038 | 60.7996 | 61.0285 | 0.14474 | 0.018992 | 0.084141 | 0.007024 | 0.12324 | 0.094732 | -0.058145 | 60.2734 | 60.3319 | 60.3329 | 60.2865 | 61.1714 | 61.1496 | 60.8453 | 61.0742 | -0.898 | -0.57191 | -0.83849 | -0.5124
356.4844 | 121.701 | -61.0245 | 60.4889 | 0.10354 | -0.022205 | 0.047522 | -0.038752 | 0.072888 | 0.048956 | -0.090186 | 60.2231 | 60.2907 | 60.2963 | 60.2453 | 61.1302 | 61.0992 | 60.795 | 61.0239 | 0.14931 | 0.023571 | 0.093298 | 0.007024 | 0.11866 | 0.094732 | -0.04441 | 60.2688 | 60.3364 | 60.3421 | 60.2911 | 61.176 | 61.145 | 60.8408 | 61.0697 | -0.90715 | -0.57191 | -0.83391 | -0.49866
358.1875 | 121.8155 | -61.0016 | 60.4523 | 0.098959 | -0.026784 | 0.047522 | -0.038752 | 0.072888 | 0.053534 | -0.094765 | 60.2276 | 60.2815 | 60.278 | 60.2315 | 61.1256 | 61.1038 | 60.7904 | 61.0285 | 0.14474 | 0.018992 | 0.093298 | 0.007024 | 0.11866 | 0.09931 | -0.048989 | 60.2734 | 60.3273 | 60.3238 | 60.2773 | 61.1714 | 61.1496 | 60.8362 | 61.0742 | -0.898 | -0.56275 | -0.84764 | -0.5124
359.9531 | 121.7194 | -61.0565 | 60.4385 | 0.10354 | -0.026784 | 0.038365 | -0.029595 | 0.077466 | 0.053534 | -0.094765 | 60.2322 | 60.2952 | 60.2917 | 60.2453 | 61.1256 | 61.0992 | 60.7812 | 61.0239 | 0.14931 | 0.018992 | 0.084141 | 0.016181 | 0.12324 | 0.09931 | -0.048989 | 60.278 | 60.341 | 60.3375 | 60.2911 | 61.1714 | 61.145 | 60.827 | 61.0697 | -0.89342 | -0.54901 | -0.83391 | -0.48951
361.6562 | 121.756 | -61.0519 | 60.4294 | 0.10812 | -0.026784 | 0.038365 | -0.038752 | 0.072888 | 0.044377 | -0.094765 | 60.2276 | 60.2907 | 60.2917 | 60.2453 | 61.1211 | 61.0992 | 60.7812 | 61.0193 | 0.15389 | 0.018992 | 0.084141 | 0.007024 | 0.11866 | 0.090153 | -0.048989 | 60.2734 | 60.3364 | 60.3375 | 60.2911 | 61.1668 | 61.145 | 60.827 | 61.0651 | -0.89342 | -0.55359 | -0.82933 | -0.48951
363.4219 | 121.7926 | -61.0428 | 60.3653 | 0.098959 | -0.017627 | 0.038365 | -0.034174 | 0.072888 | 0.048956 | -0.099343 | 60.2368 | 60.2907 | 60.3009 | 60.2407 | 61.1256 | 61.0992 | 60.7858 | 61.0193 | 0.14474 | 0.028149 | 0.084141 | 0.011602 | 0.11866 | 0.094732 | -0.053567 | 60.2826 | 60.3364 | 60.3467 | 60.2865 | 61.1714 | 61.145 | 60.8316 | 61.0651 | -0.88884 | -0.54901 | -0.82475 | -0.48493
365.125 | 121.7377 | -61.0382 | 60.466 | 0.098959 | -0.022205 | 0.038365 | -0.038752 | 0.072888 | 0.058113 | -0.099343 | 60.2276 | 60.2861 | 60.2963 | 60.2499 | 61.1256 | 61.0992 | 60.7858 | 61.0193 | 0.14474 | 0.023571 | 0.084141 | 0.007024 | 0.11866 | 0.10389 | -0.053567 | 60.2734 | 60.3319 | 60.3421 | 60.2956 | 61.1714 | 61.145 | 60.8316 | 61.0651 | -0.898 | -0.55817 | -0.82933 | -0.48951
366.9062 | 121.6644 | -61.0428 | 60.5255 | 0.10354 | -0.026784 | 0.038365 | -0.038752 | 0.072888 | 0.058113 | -0.090186 | 60.2322 | 60.2952 | 60.2963 | 60.2453 | 61.1165 | 61.09 | 60.7812 | 61.0147 | 0.14931 | 0.018992 | 0.084141 | 0.007024 | 0.11866 | 0.10389 | -0.04441 | 60.278 | 60.341 | 60.3421 | 60.2911 | 61.1623 | 61.1358 | 60.827 | 61.0605 | -0.88426 | -0.54901 | -0.82017 | -0.48493
368.6094 | 121.7468 | -61.0336 | 60.4568 | 0.098959 | -0.031363 | 0.038365 | -0.038752 | 0.077466 | 0.044377 | -0.10392 | 60.2414 | 60.2952 | 60.2872 | 60.2407 | 61.1256 | 61.1038 | 60.7858 | 61.0193 | 0.14474 | 0.014413 | 0.084141 | 0.007024 | 0.12324 | 0.090153 | -0.058145 | 60.2872 | 60.341 | 60.3329 | 60.2865 | 61.1714 | 61.1496 | 60.8316 | 61.0651 | -0.88426 | -0.54443 | -0.83849 | -0.49866
370.3594 | 121.7468 | -61.0016 | 60.4843 | 0.10354 | -0.026784 | 0.038365 | -0.043331 | 0.06831 | 0.048956 | -0.099343 | 60.2368 | 60.2952 | 60.3009 | 60.2453 | 61.1119 | 61.09 | 60.7858 | 61.0101 | 0.14931 | 0.018992 | 0.084141 | 0.002445 | 0.11409 | 0.094732 | -0.053567 | 60.2826 | 60.341 | 60.3467 | 60.2911 | 61.1577 | 61.1358 | 60.8316 | 61.0559 | -0.8751 | -0.54901 | -0.81102 | -0.48493
372.125 | 121.7331 | -61.0519 | 60.4477 | 0.098959 | -0.026784 | 0.033786 | -0.047909 | 0.072888 | 0.053534 | -0.094765 | 60.2322 | 60.2907 | 60.2917 | 60.2407 | 61.1165 | 61.0992 | 60.7812 | 61.0101 | 0.14474 | 0.018992 | 0.079562 | -0.002133 | 0.11866 | 0.09931 | -0.048989 | 60.278 | 60.3364 | 60.3375 | 60.2865 | 61.1623 | 61.145 | 60.827 | 61.0559 | -0.88426 | -0.54901 | -0.82475 | -0.48951
373.8906 | 121.7972 | -60.965 | 60.4568 | 0.098959 | -0.031363 | 0.029208 | -0.038752 | 0.06831 | 0.048956 | -0.10392 | 60.2368 | 60.2952 | 60.2963 | 60.2361 | 61.1119 | 61.0946 | 60.7904 | 61.0193 | 0.14474 | 0.014413 | 0.074984 | 0.007024 | 0.11409 | 0.094732 | -0.058145 | 60.2826 | 60.341 | 60.3421 | 60.2819 | 61.1577 | 61.1404 | 60.8362 | 61.0651 | -0.8751 | -0.55359 | -0.8156 | -0.49408
375.5781 | 121.7194 | -61.0199 | 60.4797 | 0.098959 | -0.031363 | 0.033786 | -0.047909 | 0.06831 | 0.048956 | -0.090186 | 60.2368 | 60.2907 | 60.2963 | 60.2453 | 61.1073 | 61.0946 | 60.7767 | 61.0101 | 0.14474 | 0.014413 | 0.079562 | -0.002133 | 0.11409 | 0.094732 | -0.04441 | 60.2826 | 60.3364 | 60.3421 | 60.2911 | 61.1531 | 61.1404 | 60.8224 | 61.0559 | -0.87053 | -0.53986 | -0.81102 | -0.48035
377.3438 | 121.7514 | -61.0153 | 60.4797 | 0.098959 | -0.031363 | 0.038365 | -0.047909 | 0.077466 | 0.044377 | -0.094765 | 60.2414 | 60.2952 | 60.3009 | 60.2499 | 61.1119 | 61.09 | 60.7767 | 61.0101 | 0.14474 | 0.014413 | 0.084141 | -0.002133 | 0.12324 | 0.090153 | -0.048989 | 60.2872 | 60.341 | 60.3467 | 60.2956 | 61.1577 | 61.1358 | 60.8224 | 61.0559 | -0.87052 | -0.53528 | -0.81102 | -0.47577
379.1094 | 121.7651 | -61.0153 | 60.4706 | 0.098959 | -0.031363 | 0.033786 | -0.043331 | 0.063733 | 0.039799 | -0.099343 | 60.246 | 60.3044 | 60.31 | 60.2499 | 61.1073 | 61.0855 | 60.7675 | 61.0101 | 0.14474 | 0.014413 | 0.079562 | 0.002445 | 0.10951 | 0.085575 | -0.053567 | 60.2917 | 60.3502 | 60.3558 | 60.2956 | 61.1531 | 61.1312 | 60.8133 | 61.0559 | -0.86137 | -0.52154 | -0.79728 | -0.45746
380.7969 | 121.7148 | -61.0016 | 60.5026 | 0.10812 | -0.031363 | 0.038365 | -0.043331 | 0.063733 | 0.044377 | -0.10392 | 60.2505 | 60.2998 | 60.3009 | 60.2499 | 61.1073 | 61.0855 | 60.7812 | 61.0056 | 0.15389 | 0.014413 | 0.084141 | 0.002445 | 0.10951 | 0.090153 | -0.058145 | 60.2963 | 60.3456 | 60.3467 | 60.2956 | 61.1531 | 61.1312 | 60.827 | 61.0513 | -0.85679 | -0.5307 | -0.80644 | -0.48035
382.5 | 121.6599 | -61.084 | 60.4431 | 0.10354 | -0.026784 | 0.038365 | -0.043331 | 0.072888 | 0.048956 | -0.094765 | 60.246 | 60.2998 | 60.3009 | 60.2544 | 61.1073 | 61.0855 | 60.7721 | 61.0056 | 0.14931 | 0.018992 | 0.084141 | 0.002445 | 0.11866 | 0.094732 | -0.048989 | 60.2917 | 60.3456 | 60.3467 | 60.3002 | 61.1531 | 61.1312 | 60.8179 | 61.0513 | -0.86137 | -0.52612 | -0.80644 | -0.47119
384.2031 | 121.8063 | -61.0428 | 60.3745 | 0.10354 | -0.026784 | 0.033786 | -0.052488 | 0.06831 | 0.039799 | -0.099343 | 60.246 | 60.2907 | 60.3009 | 60.2453 | 61.1119 | 61.09 | 60.7812 | 61.0147 | 0.14931 | 0.018992 | 0.079562 | -0.006712 | 0.11409 | 0.085575 | -0.053567 | 60.2917 | 60.3364 | 60.3467 | 60.2911 | 61.1577 | 61.1358 | 60.827 | 61.0605 | -0.86595 | -0.53528 | -0.81102 | -0.48035
385.8906 | 121.788 | -60.9558 | 60.4706 | 0.098959 | -0.031363 | 0.033786 | -0.043331 | 0.072888 | 0.048956 | -0.1085 | 60.2505 | 60.2952 | 60.3009 | 60.2636 | 61.1073 | 61.0809 | 60.7721 | 60.9964 | 0.14474 | 0.014413 | 0.079562 | 0.002445 | 0.11866 | 0.094732 | -0.062723 | 60.2963 | 60.341 | 60.3467 | 60.3094 | 61.1531 | 61.1267 | 60.8179 | 61.0422 | -0.85679 | -0.52154 | -0.80644 | -0.47119
387.5938 | 121.7468 | -61.0565 | 60.4019 | 0.10354 | -0.040521 | 0.029208 | -0.047909 | 0.063733 | 0.044377 | -0.10392 | 60.2551 | 60.3044 | 60.3009 | 60.2499 | 61.1028 | 61.0809 | 60.7721 | 61.0056 | 0.14931 | 0.005255 | 0.074984 | -0.002133 | 0.10951 | 0.090153 | -0.058145 | 60.3009 | 60.3502 | 60.3467 | 60.2956 | 61.1485 | 61.1267 | 60.8179 | 61.0513 | -0.84763 | -0.51696 | -0.80186 | -0.47119
389.2969 | 121.6873 | -61.0062 | 60.4935 | 0.10354 | -0.035942 | 0.020051 | -0.052488 | 0.059155 | 0.035221 | -0.10392 | 60.2414 | 60.3044 | 60.3055 | 60.2544 | 61.1119 | 61.0855 | 60.7721 | 60.9964 | 0.14931 | 0.009834 | 0.065827 | -0.006712 | 0.10493 | 0.080997 | -0.058145 | 60.2872 | 60.3502 | 60.3512 | 60.3002 | 61.1577 | 61.1312 | 60.8179 | 61.0422 | -0.87052 | -0.5307 | -0.80644 | -0.46661
391.0469 | 121.6644 | -61.0565 | 60.4614 | 0.098959 | -0.031363 | 0.038365 | -0.047909 | 0.059155 | 0.039799 | -0.099343 | 60.2551 | 60.3181 | 60.31 | 60.2544 | 61.0936 | 61.0672 | 60.7629 | 61.001 | 0.14474 | 0.014413 | 0.084141 | -0.002133 | 0.10493 | 0.085575 | -0.053567 | 60.3009 | 60.3639 | 60.3558 | 60.3002 | 61.1394 | 61.1129 | 60.8087 | 61.0468 | -0.83848 | -0.50781 | -0.78355 | -0.45288
392.7969 | 121.7102 | -61.0428 | 60.4523 | 0.10354 | -0.035942 | 0.029208 | -0.043331 | 0.054577 | 0.039799 | -0.11308 | 60.246 | 60.2998 | 60.31 | 60.2499 | 61.0982 | 61.0763 | 60.7675 | 60.9964 | 0.14931 | 0.009834 | 0.074984 | 0.002445 | 0.10035 | 0.085575 | -0.067301 | 60.2917 | 60.3456 | 60.3558 | 60.2956 | 61.144 | 61.1221 | 60.8133 | 61.0422 | -0.85221 | -0.52154 | -0.78813 | -0.45746
394.5 | 121.6644 | -61.1069 | 60.434 | 0.098959 | -0.040521 | 0.029208 | -0.038752 | 0.059155 | 0.039799 | -0.1085 | 60.2505 | 60.3136 | 60.31 | 60.2499 | 61.1073 | 61.0809 | 60.7675 | 60.9964 | 0.14474 | 0.005255 | 0.074984 | 0.007024 | 0.10493 | 0.085575 | -0.062723 | 60.2963 | 60.3593 | 60.3558 | 60.2956 | 61.1531 | 61.1267 | 60.8133 | 61.0422 | -0.85679 | -0.51696 | -0.79728 | -0.45746
396.25 | 121.7972 | -61.0245 | 60.3928 | 0.10354 | -0.035942 | 0.020051 | -0.047909 | 0.054577 | 0.039799 | -0.10392 | 60.2505 | 60.3136 | 60.3146 | 60.2544 | 61.0936 | 61.0809 | 60.7584 | 60.9964 | 0.14931 | 0.009834 | 0.065827 | -0.002133 | 0.10035 | 0.085575 | -0.058145 | 60.2963 | 60.3593 | 60.3604 | 60.3002 | 61.1394 | 61.1267 | 60.8041 | 61.0422 | -0.84305 | -0.50781 | -0.77897 | -0.44372
398.0156 | 121.7056 | -60.9924 | 60.498 | 0.10354 | -0.040521 | 0.020051 | -0.047909 | 0.054577 | 0.035221 | -0.11308 | 60.2505 | 60.2998 | 60.3055 | 60.2544 | 61.0936 | 61.0763 | 60.7629 | 60.9964 | 0.14931 | 0.005255 | 0.065827 | -0.002133 | 0.10035 | 0.080997 | -0.067301 | 60.2963 | 60.3456 | 60.3512 | 60.3002 | 61.1394 | 61.1221 | 60.8087 | 61.0422 | -0.84305 | -0.51239 | -0.78813 | -0.45746
399.7344 | 121.8018 | -60.965 | 60.434 | 0.098959 | -0.0451 | 0.010893 | -0.061645 | 0.054577 | 0.035221 | -0.11765 | 60.2505 | 60.309 | 60.3055 | 60.2499 | 61.0936 | 61.0809 | 60.7584 | 60.9918 | 0.14474 | 0.000676 | 0.056669 | -0.015869 | 0.10035 | 0.080997 | -0.071879 | 60.2963 | 60.3548 | 60.3512 | 60.2956 | 61.1394 | 61.1267 | 60.8041 | 61.0376 | -0.84305 | -0.50781 | -0.78813 | -0.45288
401.5 | 121.8018 | -60.9512 | 60.498 | 0.10812 | -0.040521 | 0.020051 | -0.057066 | 0.045421 | 0.035221 | -0.1085 | 60.2597 | 60.3273 | 60.3146 | 60.2682 | 61.0844 | 61.0672 | 60.7492 | 60.9781 | 0.15389 | 0.005255 | 0.065827 | -0.01129 | 0.091197 | 0.080997 | -0.062723 | 60.3055 | 60.3731 | 60.3604 | 60.3139 | 61.1302 | 61.1129 | 60.795 | 61.0239 | -0.82474 | -0.48949 | -0.76981 | -0.43457
403.2031 | 121.7514 | -61.0107 | 60.4385 | 0.10812 | -0.0451 | 0.020051 | -0.047909 | 0.049999 | 0.026064 | -0.11765 | 60.2597 | 60.3136 | 60.3192 | 60.2682 | 61.0936 | 61.0672 | 60.7492 | 60.9918 | 0.15389 | 0.000676 | 0.065827 | -0.002133 | 0.095775 | 0.07184 | -0.071879 | 60.3055 | 60.3593 | 60.365 | 60.3139 | 61.1394 | 61.1129 | 60.795 | 61.0376 | -0.8339 | -0.48949 | -0.77439 | -0.42999
404.9688 | 121.8018 | -61.0062 | 60.3882 | 0.10812 | -0.049678 | 0.020051 | -0.061645 | 0.049999 | 0.030642 | -0.11765 | 60.2643 | 60.3181 | 60.3238 | 60.2682 | 61.089 | 61.0717 | 60.7538 | 60.9827 | 0.15389 | -0.003902 | 0.065827 | -0.015869 | 0.095775 | 0.076418 | -0.071879 | 60.3101 | 60.3639 | 60.3696 | 60.3139 | 61.1348 | 61.1175 | 60.7995 | 61.0284 | -0.82474 | -0.48949 | -0.76524 | -0.42999
406.6562 | 121.6599 | -60.9741 | 60.5347 | 0.094381 | -0.049678 | 0.015472 | -0.061645 | 0.054577 | 0.030642 | -0.12223 | 60.2643 | 60.3227 | 60.3284 | 60.2682 | 61.0844 | 61.058 | 60.7492 | 60.9827 | 0.14016 | -0.003902 | 0.061248 | -0.015869 | 0.10035 | 0.076418 | -0.076458 | 60.3101 | 60.3685 | 60.3741 | 60.3139 | 61.1302 | 61.1038 | 60.795 | 61.0284 | -0.82016 | -0.48492 | -0.75608 | -0.42083
408.4219 | 121.6553 | -60.9833 | 60.5072 | 0.10354 | -0.054257 | 0.006315 | -0.070802 | 0.045421 | 0.026064 | -0.12223 | 60.2689 | 60.3273 | 60.3238 | 60.2636 | 61.0844 | 61.0534 | 60.7492 | 60.9827 | 0.14931 | -0.008481 | 0.052091 | -0.025026 | 0.091197 | 0.07184 | -0.076458 | 60.3146 | 60.3731 | 60.3696 | 60.3094 | 61.1302 | 61.0992 | 60.795 | 61.0284 | -0.81558 | -0.48034 | -0.76066 | -0.42541
410.125 | 121.6827 | -61.0062 | 60.5164 | 0.094381 | -0.058836 | 0.006315 | -0.066223 | 0.036265 | 0.016907 | -0.13139 | 60.2643 | 60.3273 | 60.3284 | 60.2682 | 61.089 | 61.058 | 60.7446 | 60.9735 | 0.14016 | -0.01306 | 0.052091 | -0.020447 | 0.082041 | 0.062683 | -0.085614 | 60.3101 | 60.3731 | 60.3741 | 60.3139 | 61.1348 | 61.1038 | 60.7904 | 61.0193 | -0.82474 | -0.48034 | -0.76066 | -0.41625
411.875 | 121.6736 | -61.0199 | 60.4568 | 0.10354 | -0.054257 | 0.010893 | -0.066223 | 0.045421 | 0.026064 | -0.12223 | 60.2643 | 60.3181 | 60.3192 | 60.2682 | 61.0799 | 61.0626 | 60.7492 | 60.9827 | 0.14931 | -0.008481 | 0.056669 | -0.020447 | 0.091197 | 0.07184 | -0.076458 | 60.3101 | 60.3639 | 60.365 | 60.3139 | 61.1256 | 61.1083 | 60.795 | 61.0284 | -0.81559 | -0.48492 | -0.76066 | -0.42999
413.5781 | 121.6827 | -60.9879 | 60.4843 | 0.10354 | -0.049678 | 0.010893 | -0.070802 | 0.040843 | 0.021485 | -0.12223 | 60.2734 | 60.341 | 60.3375 | 60.2865 | 61.0753 | 61.0443 | 60.7217 | 60.9598 | 0.14931 | -0.003902 | 0.056669 | -0.025026 | 0.086619 | 0.067261 | -0.076458 | 60.3192 | 60.3868 | 60.3833 | 60.3323 | 61.1211 | 61.09 | 60.7675 | 61.0056 | -0.80185 | -0.44829 | -0.73777 | -0.3842
415.3438 | 121.6553 | -61.0611 | 60.4752 | 0.10354 | -0.054257 | 0.006315 | -0.07538 | 0.031687 | 0.021485 | -0.13139 | 60.2826 | 60.3365 | 60.3375 | 60.2865 | 61.0753 | 61.0488 | 60.7355 | 60.9644 | 0.14931 | -0.008481 | 0.052091 | -0.029604 | 0.077463 | 0.067261 | -0.085614 | 60.3284 | 60.3822 | 60.3833 | 60.3323 | 61.1211 | 61.0946 | 60.7812 | 61.0101 | -0.79269 | -0.45287 | -0.73777 | -0.39794
417.1094 | 121.6644 | -60.9787 | 60.5804 | 0.098959 | -0.067994 | 0.001736 | -0.07538 | 0.036265 | 0.003172 | -0.13597 | 60.2689 | 60.3365 | 60.3238 | 60.2727 | 61.0753 | 61.0488 | 60.74 | 60.9781 | 0.14474 | -0.022218 | 0.047512 | -0.029604 | 0.082041 | 0.048948 | -0.090192 | 60.3146 | 60.3822 | 60.3696 | 60.3185 | 61.1211 | 61.0946 | 60.7858 | 61.0239 | -0.80643 | -0.47118 | -0.7515 | -0.41625
418.8594 | 121.7926 | -60.9924 | 60.3973 | 0.098959 | -0.067994 | -0.007421 | -0.084537 | 0.027109 | 0.012329 | -0.14055 | 60.2689 | 60.3227 | 60.3329 | 60.2727 | 61.0753 | 61.0534 | 60.7492 | 60.9781 | 0.14474 | -0.022218 | 0.038355 | -0.038761 | 0.072885 | 0.058105 | -0.09477 | 60.3146 | 60.3685 | 60.3787 | 60.3185 | 61.1211 | 61.0992 | 60.795 | 61.0239 | -0.80643 | -0.48034 | -0.74235 | -0.41625
420.5625 | 121.6644 | -60.9329 | 60.553 | 0.098959 | -0.072572 | -0.007421 | -0.079959 | 0.031687 | 0.012329 | -0.13597 | 60.2917 | 60.3502 | 60.3467 | 60.2956 | 61.0615 | 61.0351 | 60.7217 | 60.9552 | 0.14474 | -0.026796 | 0.038355 | -0.034183 | 0.077463 | 0.058105 | -0.090192 | 60.3375 | 60.396 | 60.3925 | 60.3414 | 61.1073 | 61.0809 | 60.7675 | 61.001 | -0.7698 | -0.42997 | -0.71487 | -0.37505
422.3125 | 121.6965 | -60.9833 | 60.5164 | 0.098959 | -0.072572 | -0.007421 | -0.084537 | 0.027109 | -0.001406 | -0.1497 | 60.2734 | 60.3319 | 60.3375 | 60.2773 | 61.0753 | 61.0443 | 60.7355 | 60.9644 | 0.14474 | -0.026796 | 0.038355 | -0.038761 | 0.072885 | 0.04437 | -0.10393 | 60.3192 | 60.3776 | 60.3833 | 60.3231 | 61.1211 | 61.09 | 60.7812 | 61.0101 | -0.80185 | -0.46202 | -0.73777 | -0.39794
424.0781 | 121.6599 | -61.0382 | 60.5026 | 0.10354 | -0.077151 | -0.016578 | -0.084537 | 0.022531 | -0.005985 | -0.15428 | 60.2734 | 60.3365 | 60.3375 | 60.2819 | 61.0707 | 61.0534 | 60.7171 | 60.9598 | 0.14931 | -0.031375 | 0.029198 | -0.038761 | 0.068307 | 0.039791 | -0.10851 | 60.3192 | 60.3822 | 60.3833 | 60.3277 | 61.1165 | 61.0992 | 60.7629 | 61.0056 | -0.79727 | -0.44371 | -0.73319 | -0.37963
425.7656 | 121.8018 | -60.997 | 60.4385 | 0.10354 | -0.090888 | -0.016578 | -0.098273 | 0.013375 | -0.001406 | -0.15428 | 60.2917 | 60.3548 | 60.3467 | 60.2911 | 61.0615 | 61.0397 | 60.7217 | 60.9506 | 0.14931 | -0.045112 | 0.029198 | -0.052497 | 0.059151 | 0.04437 | -0.10851 | 60.3375 | 60.4005 | 60.3925 | 60.3368 | 61.1073 | 61.0855 | 60.7675 | 60.9964 | -0.7698 | -0.42997 | -0.71487 | -0.37505
427.4688 | 121.8246 | -60.9512 | 60.498 | 0.098959 | -0.086309 | -0.012 | -0.093694 | 0.013375 | -0.010563 | -0.16344 | 60.2872 | 60.3502 | 60.3513 | 60.2911 | 61.057 | 61.0305 | 60.7171 | 60.946 | 0.14474 | -0.040533 | 0.033776 | -0.047918 | 0.059151 | 0.035213 | -0.11766 | 60.3329 | 60.396 | 60.397 | 60.3368 | 61.1027 | 61.0763 | 60.7629 | 60.9918 | -0.7698 | -0.42997 | -0.70572 | -0.36589
429.25 | 121.7651 | -60.9787 | 60.4935 | 0.094381 | -0.08173 | -0.030314 | -0.098273 | 0.008797 | -0.005985 | -0.15886 | 60.278 | 60.3365 | 60.3421 | 60.2865 | 61.0615 | 61.0534 | 60.7309 | 60.9598 | 0.14016 | -0.035954 | 0.015462 | -0.052497 | 0.054573 | 0.039791 | -0.11308 | 60.3238 | 60.3822 | 60.3879 | 60.3323 | 61.1073 | 61.0992 | 60.7767 | 61.0056 | -0.78354 | -0.45287 | -0.71945 | -0.38878
430.9531 | 121.7102 | -60.9558 | 60.5164 | 0.094381 | -0.090888 | -0.030314 | -0.10743 | -0.004937 | -0.024298 | -0.16801 | 60.2872 | 60.3456 | 60.3467 | 60.2911 | 61.0524 | 61.0397 | 60.7263 | 60.9598 | 0.14016 | -0.045112 | 0.015462 | -0.061654 | 0.040839 | 0.021478 | -0.12224 | 60.3329 | 60.3914 | 60.3925 | 60.3368 | 61.0982 | 61.0855 | 60.7721 | 61.0056 | -0.76522 | -0.43913 | -0.70572 | -0.37963
432.6562 | 121.6736 | -61.0474 | 60.4889 | 0.098959 | -0.1092 | -0.039471 | -0.11201 | -0.009515 | -0.024298 | -0.16801 | 60.2917 | 60.341 | 60.3467 | 60.2911 | 61.057 | 61.0351 | 60.7171 | 60.9506 | 0.14474 | -0.063427 | 0.006305 | -0.066232 | 0.036261 | 0.021478 | -0.12224 | 60.3375 | 60.3868 | 60.3925 | 60.3368 | 61.1027 | 61.0809 | 60.7629 | 60.9964 | -0.76522 | -0.42539 | -0.7103 | -0.37047
434.4375 | 121.6827 | -60.9467 | 60.5896 | 0.098959 | -0.11378 | -0.04405 | -0.11659 | -0.014093 | -0.033455 | -0.19091 | 60.2917 | 60.341 | 60.3467 | 60.2911 | 61.0524 | 61.0397 | 60.7217 | 60.9598 | 0.14474 | -0.068006 | 0.001726 | -0.070811 | 0.031683 | 0.012321 | -0.14513 | 60.3375 | 60.3868 | 60.3925 | 60.3368 | 61.0982 | 61.0855 | 60.7675 | 61.0056 | -0.76064 | -0.42997 | -0.70572 | -0.37505
436.2031 | 121.6873 | -61.0245 | 60.498 | 0.10812 | -0.10462 | -0.048628 | -0.12574 | -0.014093 | -0.033455 | -0.17717 | 60.278 | 60.341 | 60.3467 | 60.2865 | 61.0615 | 61.0443 | 60.7263 | 60.9598 | 0.15389 | -0.058848 | -0.002852 | -0.079968 | 0.031683 | 0.012321 | -0.1314 | 60.3238 | 60.3868 | 60.3925 | 60.3323 | 61.1073 | 61.09 | 60.7721 | 61.0056 | -0.78354 | -0.44829 | -0.71487 | -0.37963
437.8906 | 121.8063 | -60.9421 | 60.4843 | 0.098959 | -0.11378 | -0.048628 | -0.12574 | -0.027827 | -0.038034 | -0.18633 | 60.278 | 60.3227 | 60.3375 | 60.2773 | 61.0661 | 61.0534 | 60.7309 | 60.9644 | 0.14474 | -0.068006 | -0.002852 | -0.079968 | 0.017949 | 0.007742 | -0.14055 | 60.3238 | 60.3685 | 60.3833 | 60.3231 | 61.1119 | 61.0992 | 60.7767 | 61.0101 | -0.78811 | -0.45287 | -0.72861 | -0.39336
439.5938 | 121.8018 | -60.9421 | 60.498 | 0.094381 | -0.11836 | -0.053207 | -0.13032 | -0.023249 | -0.042612 | -0.19091 | 60.2689 | 60.3273 | 60.3329 | 60.2773 | 61.0661 | 61.0488 | 60.7355 | 60.9689 | 0.14016 | -0.072585 | -0.007431 | -0.084546 | 0.022527 | 0.003164 | -0.14513 | 60.3146 | 60.3731 | 60.3787 | 60.3231 | 61.1119 | 61.0946 | 60.7812 | 61.0147 | -0.79727 | -0.4666 | -0.73319 | -0.40252
441.3438 | 121.7834 | -61.0016 | 60.4385 | 0.10812 | -0.11836 | -0.066943 | -0.13032 | -0.027827 | -0.051769 | -0.19091 | 60.2963 | 60.3456 | 60.3513 | 60.3002 | 61.0478 | 61.0259 | 60.708 | 60.9415 | 0.15389 | -0.072585 | -0.021167 | -0.084546 | 0.017949 | -0.005993 | -0.14513 | 60.3421 | 60.3914 | 60.397 | 60.346 | 61.0936 | 61.0717 | 60.7538 | 60.9872 | -0.75149 | -0.41166 | -0.69656 | -0.35673
443.1094 | 121.7743 | -60.9375 | 60.5026 | 0.098959 | -0.12752 | -0.062364 | -0.14406 | -0.036983 | -0.051769 | -0.20006 | 60.2872 | 60.3502 | 60.3513 | 60.2956 | 61.0524 | 61.0259 | 60.708 | 60.9506 | 0.14474 | -0.081742 | -0.016588 | -0.098282 | 0.008793 | -0.005993 | -0.15429 | 60.3329 | 60.396 | 60.397 | 60.3414 | 61.0982 | 61.0717 | 60.7538 | 60.9964 | -0.76522 | -0.42082 | -0.70114 | -0.35673
444.8125 | 121.756 | -60.9283 | 60.5072 | 0.10354 | -0.14583 | -0.080679 | -0.15321 | -0.055294 | -0.060926 | -0.20922 | 60.3055 | 60.3593 | 60.3604 | 60.3048 | 61.0341 | 61.0168 | 60.6988 | 60.9415 | 0.14931 | -0.10006 | -0.034903 | -0.10744 | -0.009518 | -0.01515 | -0.16344 | 60.3513 | 60.4051 | 60.4062 | 60.3506 | 61.0799 | 61.0626 | 60.7446 | 60.9872 | -0.7286 | -0.39335 | -0.67367 | -0.33842
446.5781 | 121.8292 | -60.9146 | 60.5072 | 0.098959 | -0.14125 | -0.0761 | -0.15321 | -0.046138 | -0.074661 | -0.2138 | 60.2963 | 60.3502 | 60.3604 | 60.3002 | 61.0524 | 61.0259 | 60.7034 | 60.946 | 0.14474 | -0.095479 | -0.030324 | -0.10744 | -0.000362 | -0.028885 | -0.16802 | 60.3421 | 60.396 | 60.4062 | 60.346 | 61.0982 | 61.0717 | 60.7492 | 60.9918 | -0.75607 | -0.40708 | -0.69198 | -0.343
448.3438 | 121.7056 | -60.9558 | 60.5438 | 0.094381 | -0.15499 | -0.089836 | -0.15779 | -0.055294 | -0.079239 | -0.22295 | 60.3192 | 60.3731 | 60.3696 | 60.3231 | 61.0341 | 61.0076 | 60.6805 | 60.9277 | 0.14016 | -0.10921 | -0.04406 | -0.11202 | -0.009518 | -0.033463 | -0.17718 | 60.365 | 60.4189 | 60.4153 | 60.3689 | 61.0799 | 61.0534 | 60.7263 | 60.9735 | -0.71486 | -0.3613 | -0.66452 | -0.31095
450.1094 | 121.788 | -60.8734 | 60.5804 | 0.098959 | -0.15957 | -0.089836 | -0.16695 | -0.069028 | -0.083817 | -0.22753 | 60.3192 | 60.3822 | 60.3833 | 60.3323 | 61.0112 | 60.9893 | 60.6805 | 60.9186 | 0.14474 | -0.11379 | -0.04406 | -0.12117 | -0.023252 | -0.038041 | -0.18176 | 60.365 | 60.428 | 60.4291 | 60.3781 | 61.057 | 61.0351 | 60.7263 | 60.9644 | -0.69197 | -0.3613 | -0.62789 | -0.29722
451.8594 | 121.8201 | -60.8505 | 60.5988 | 0.10354 | -0.15957 | -0.098993 | -0.16695 | -0.059872 | -0.083817 | -0.22295 | 60.3604 | 60.4143 | 60.4291 | 60.3598 | 60.9837 | 60.9619 | 60.6393 | 60.8774 | 0.14931 | -0.11379 | -0.053217 | -0.12117 | -0.014096 | -0.038041 | -0.17718 | 60.4062 | 60.4601 | 60.4749 | 60.4055 | 61.0295 | 61.0076 | 60.6851 | 60.9232 | -0.6233 | -0.27889 | -0.55464 | -0.21023
453.5625 | 121.8018 | -60.7956 | 60.6079 | 0.094381 | -0.17331 | -0.10357 | -0.16695 | -0.069028 | -0.088396 | -0.23211 | 60.3971 | 60.4509 | 60.452 | 60.3918 | 60.9471 | 60.9207 | 60.621 | 60.8499 | 0.14016 | -0.12753 | -0.057796 | -0.12117 | -0.023252 | -0.04262 | -0.18633 | 60.4428 | 60.4967 | 60.4978 | 60.4376 | 60.9929 | 60.9664 | 60.6668 | 60.8957 | -0.55004 | -0.22394 | -0.49512 | -0.16902
455.3125 | 121.8109 | -60.7498 | 60.6949 | 0.098959 | -0.17788 | -0.10815 | -0.18069 | -0.078184 | -0.097553 | -0.24584 | 60.4566 | 60.515 | 60.5115 | 60.4605 | 60.8876 | 60.8749 | 60.5523 | 60.7858 | 0.14474 | -0.13211 | -0.062374 | -0.13491 | -0.032408 | -0.051777 | -0.20007 | 60.5024 | 60.5608 | 60.5573 | 60.5063 | 60.9334 | 60.9206 | 60.5981 | 60.8316 | -0.431 | -0.095747 | -0.37609 | -0.040829
457.0625 | 121.7926 | -60.6583 | 60.7681 | 0.094381 | -0.18704 | -0.12646 | -0.18069 | -0.08734 | -0.10671 | -0.24584 | 60.5619 | 60.6203 | 60.6214 | 60.575 | 60.7777 | 60.7513 | 60.4424 | 60.6759 | 0.14016 | -0.14127 | -0.080689 | -0.13491 | -0.041564 | -0.060933 | -0.20007 | 60.6077 | 60.6661 | 60.6671 | 60.6207 | 60.8235 | 60.797 | 60.4882 | 60.7217 | -0.21582 | 0.11944 | -0.15633 | 0.17893
458.75 | 121.6644 | -60.6079 | 60.8826 | 0.098959 | -0.1962 | -0.1402 | -0.20358 | -0.11023 | -0.12502 | -0.26874 | 60.6168 | 60.6753 | 60.6809 | 60.6345 | 60.7228 | 60.6963 | 60.3829 | 60.6164 | 0.14474 | -0.15042 | -0.094424 | -0.1578 | -0.064454 | -0.079247 | -0.22296 | 60.6626 | 60.7211 | 60.7267 | 60.6803 | 60.7685 | 60.7421 | 60.4287 | 60.6622 | -0.10594 | 0.2339 | -0.041876 | 0.29797
460.5 | 121.6736 | -60.6125 | 60.8826 | 0.10354 | -0.20994 | -0.14478 | -0.20816 | -0.10565 | -0.13418 | -0.26416 | 60.6306 | 60.6799 | 60.6809 | 60.6391 | 60.7136 | 60.6917 | 60.3738 | 60.6164 | 0.14931 | -0.16416 | -0.099003 | -0.16238 | -0.059876 | -0.088404 | -0.21838 | 60.6763 | 60.7256 | 60.7267 | 60.6848 | 60.7594 | 60.7375 | 60.4195 | 60.6622 | -0.083051 | 0.25679 | -0.03272 | 0.30712
462.2656 | 121.6736 | -60.5667 | 60.9787 | 0.098959 | -0.21452 | -0.15851 | -0.22647 | -0.11939 | -0.14334 | -0.28705 | 60.6809 | 60.7394 | 60.7496 | 60.6894 | 60.6495 | 60.6368 | 60.3142 | 60.5569 | 0.14474 | -0.16874 | -0.11274 | -0.18069 | -0.07361 | -0.097561 | -0.24127 | 60.7267 | 60.7852 | 60.7953 | 60.7352 | 60.6953 | 60.6826 | 60.36 | 60.6027 | 0.031406 | 0.36668 | 0.10005 | 0.43532
464.0156 | 121.6644 | -60.5438 | 60.9787 | 0.094381 | -0.22367 | -0.16767 | -0.22647 | -0.12854 | -0.15249 | -0.30078 | 60.6992 | 60.7577 | 60.7587 | 60.7078 | 60.6449 | 60.6139 | 60.3051 | 60.5386 | 0.14016 | -0.1779 | -0.1219 | -0.18069 | -0.082766 | -0.10672 | -0.25501 | 60.745 | 60.8035 | 60.8045 | 60.7535 | 60.6907 | 60.6597 | 60.3509 | 60.5844 | 0.054299 | 0.39415 | 0.11378 | 0.45363
465.7031 | 121.6736 | -60.553 | 60.9238 | 0.098959 | -0.23283 | -0.17683 | -0.24021 | -0.14228 | -0.15707 | -0.30536 | 60.745 | 60.7989 | 60.7999 | 60.7535 | 60.5992 | 60.5773 | 60.2639 | 60.4928 | 0.14474 | -0.18706 | -0.13105 | -0.19443 | -0.0965 | -0.1113 | -0.25958 | 60.7908 | 60.8447 | 60.8457 | 60.7993 | 60.6449 | 60.6231 | 60.3097 | 60.5386 | 0.14586 | 0.48114 | 0.20077 | 0.53604
467.4531 | 121.6782 | -60.5164 | 61.0062 | 0.098959 | -0.24199 | -0.17225 | -0.24936 | -0.14685 | -0.16623 | -0.30994 | 60.8 | 60.8539 | 60.8594 | 60.8039 | 60.5396 | 60.5224 | 60.1998 | 60.4333 | 0.14474 | -0.19621 | -0.12648 | -0.20359 | -0.10108 | -0.12045 | -0.26416 | 60.8457 | 60.8996 | 60.9052 | 60.8497 | 60.5854 | 60.5681 | 60.2456 | 60.4791 | 0.26032 | 0.60018 | 0.3198 | 0.65966
469.2031 | 121.7056 | -60.4202 | 61.084 | 0.098959 | -0.24199 | -0.18599 | -0.24479 | -0.14228 | -0.17081 | -0.31452 | 60.8366 | 60.8905 | 60.8961 | 60.8451 | 60.503 | 60.4766 | 60.1586 | 60.3967 | 0.14474 | -0.19621 | -0.14021 | -0.19901 | -0.0965 | -0.12503 | -0.26874 | 60.8824 | 60.9363 | 60.9418 | 60.8909 | 60.5488 | 60.5224 | 60.2044 | 60.4424 | 0.33358 | 0.67801 | 0.39305 | 0.73749
470.9062 | 121.8018 | -60.4019 | 61.0382 | 0.098959 | -0.2603 | -0.19057 | -0.26768 | -0.16059 | -0.18454 | -0.33283 | 60.8091 | 60.8676 | 60.8686 | 60.8085 | 60.5351 | 60.5132 | 60.1906 | 60.4287 | 0.14474 | -0.21453 | -0.14479 | -0.2219 | -0.11481 | -0.13877 | -0.28705 | 60.8549 | 60.9134 | 60.9144 | 60.8543 | 60.5808 | 60.559 | 60.2364 | 60.4745 | 0.27406 | 0.61849 | 0.33354 | 0.67797
472.6719 | 121.7239 | -60.6766 | 60.7544 | 0.10354 | -0.2603 | -0.19972 | -0.26768 | -0.16059 | -0.17996 | -0.32825 | 60.5939 | 60.6432 | 60.6443 | 60.5979 | 60.7457 | 60.7284 | 60.4104 | 60.6439 | 0.14931 | -0.21453 | -0.15395 | -0.2219 | -0.11481 | -0.13419 | -0.28248 | 60.6397 | 60.689 | 60.69 | 60.6436 | 60.7914 | 60.7741 | 60.4562 | 60.6897 | -0.15173 | 0.18354 | -0.10139 | 0.23387
474.4219 | 121.669 | -60.672 | 60.8093 | 0.098959 | -0.2832 | -0.22719 | -0.28599 | -0.18805 | -0.19828 | -0.35114 | 60.6306 | 60.6753 | 60.6855 | 60.6299 | 60.7136 | 60.6963 | 60.3692 | 60.6118 | 0.14474 | -0.23742 | -0.18142 | -0.24022 | -0.14228 | -0.1525 | -0.30537 | 60.6763 | 60.7211 | 60.7312 | 60.6757 | 60.7594 | 60.7421 | 60.415 | 60.6576 | -0.083051 | 0.26137 | -0.028142 | 0.31628
476.125 | 121.701 | -60.5896 | 60.8963 | 0.10354 | -0.31067 | -0.25467 | -0.31804 | -0.2201 | -0.23033 | -0.37403 | 60.6718 | 60.7165 | 60.7313 | 60.6757 | 60.677 | 60.6505 | 60.3326 | 60.5798 | 0.14931 | -0.26489 | -0.20889 | -0.27227 | -0.17433 | -0.18455 | -0.32826 | 60.7175 | 60.7623 | 60.777 | 60.7215 | 60.7228 | 60.6963 | 60.3783 | 60.6256 | -0.00522 | 0.3392 | 0.054266 | 0.39869
477.8281 | 121.6461 | -60.5759 | 60.9146 | 0.098959 | -0.33814 | -0.26382 | -0.33636 | -0.23383 | -0.2578 | -0.39692 | 60.7221 | 60.7852 | 60.777 | 60.7261 | 60.6312 | 60.6048 | 60.2776 | 60.5249 | 0.14474 | -0.29237 | -0.21805 | -0.29058 | -0.18806 | -0.21202 | -0.35115 | 60.7679 | 60.831 | 60.8228 | 60.7718 | 60.677 | 60.6505 | 60.3234 | 60.5706 | 0.090926 | 0.44451 | 0.14583 | 0.49941
479.5938 | 121.7514 | -60.3516 | 61.0794 | 0.098959 | -0.32899 | -0.2684 | -0.33636 | -0.22926 | -0.24864 | -0.39235 | 60.8732 | 60.9271 | 60.9281 | 60.8772 | 60.4664 | 60.4445 | 60.1265 | 60.3646 | 0.14474 | -0.28321 | -0.22263 | -0.29058 | -0.18348 | -0.20286 | -0.34657 | 60.919 | 60.9729 | 60.9739 | 60.923 | 60.5122 | 60.4903 | 60.1723 | 60.4104 | 0.40683 | 0.74669 | 0.46173 | 0.80158
481.3594 | 121.7102 | -60.2966 | 61.1755 | 0.098959 | -0.35646 | -0.28672 | -0.35467 | -0.24757 | -0.27611 | -0.41981 | 60.9465 | 61.0004 | 60.9922 | 60.955 | 60.3977 | 60.3667 | 60.0487 | 60.2914 | 0.14474 | -0.31068 | -0.24094 | -0.30889 | -0.20179 | -0.23033 | -0.37404 | 60.9922 | 61.0462 | 61.038 | 61.0008 | 60.4435 | 60.4125 | 60.0945 | 60.3371 | 0.54876 | 0.89778 | 0.5945 | 0.94351
483.0625 | 121.8063 | -60.26 | 61.1572 | 0.094381 | -0.38851 | -0.30961 | -0.37756 | -0.28419 | -0.299 | -0.44271 | 60.9602 | 61.0141 | 61.0197 | 60.9642 | 60.3794 | 60.3576 | 60.0441 | 60.2776 | 0.14016 | -0.34274 | -0.26383 | -0.33178 | -0.23842 | -0.25323 | -0.39693 | 61.006 | 61.0599 | 61.0655 | 61.01 | 60.4252 | 60.4033 | 60.0899 | 60.3234 | 0.58081 | 0.91609 | 0.64028 | 0.97556
484.8125 | 121.6507 | -60.4889 | 61.0245 | 0.094381 | -0.41141 | -0.33708 | -0.40503 | -0.30708 | -0.32189 | -0.47018 | 60.7313 | 60.7852 | 60.7908 | 60.7352 | 60.6083 | 60.5773 | 60.2547 | 60.4974 | 0.14016 | -0.36563 | -0.2913 | -0.35926 | -0.26131 | -0.27612 | -0.4244 | 60.7771 | 60.831 | 60.8365 | 60.781 | 60.6541 | 60.6231 | 60.3005 | 60.5432 | 0.12297 | 0.47656 | 0.18246 | 0.53604
486.5 | 121.6599 | -60.5621 | 60.9787 | 0.10354 | -0.41598 | -0.3554 | -0.41419 | -0.32539 | -0.34021 | -0.48849 | 60.7542 | 60.8081 | 60.8137 | 60.7673 | 60.5946 | 60.5544 | 60.241 | 60.4791 | 0.14931 | -0.37021 | -0.30962 | -0.36841 | -0.27962 | -0.29443 | -0.44271 | 60.8 | 60.8538 | 60.8594 | 60.8131 | 60.6404 | 60.6002 | 60.2868 | 60.5249 | 0.1596 | 0.51319 | 0.21908 | 0.57267
488.25 | 121.6736 | -60.5392 | 60.9421 | 0.094381 | -0.45261 | -0.38744 | -0.44624 | -0.33913 | -0.3631 | -0.51596 | 60.7588 | 60.8126 | 60.8045 | 60.7627 | 60.5854 | 60.559 | 60.241 | 60.4837 | 0.14016 | -0.40684 | -0.34167 | -0.40046 | -0.29335 | -0.31732 | -0.47018 | 60.8045 | 60.8584 | 60.8503 | 60.8085 | 60.6312 | 60.6048 | 60.2868 | 60.5294 | 0.17334 | 0.51776 | 0.21908 | 0.56351
490.0156 | 121.7285 | -60.5026 | 60.9421 | 0.098959 | -0.47093 | -0.40576 | -0.48287 | -0.37575 | -0.39515 | -0.53885 | 60.7816 | 60.8264 | 60.832 | 60.7764 | 60.5671 | 60.5361 | 60.2227 | 60.4562 | 0.14474 | -0.42515 | -0.35998 | -0.43709 | -0.32998 | -0.34937 | -0.49307 | 60.8274 | 60.8722 | 60.8777 | 60.8222 | 60.6129 | 60.5819 | 60.2685 | 60.502 | 0.21454 | 0.55897 | 0.26487 | 0.60929
491.7188 | 121.701 | -60.4477 | 61.0748 | 0.094381 | -0.48924 | -0.42407 | -0.48745 | -0.38949 | -0.41804 | -0.548 | 60.7954 | 60.8584 | 60.864 | 60.8039 | 60.5351 | 60.5178 | 60.1998 | 60.4287 | 0.14016 | -0.44347 | -0.3783 | -0.44167 | -0.34371 | -0.37226 | -0.50223 | 60.8412 | 60.9042 | 60.9098 | 60.8497 | 60.5808 | 60.5636 | 60.2456 | 60.4745 | 0.26032 | 0.5956 | 0.32896 | 0.66423
493.4688 | 121.6782 | -60.4477 | 61.0382 | 0.094381 | -0.54877 | -0.4836 | -0.54697 | -0.44442 | -0.4684 | -0.58463 | 60.7862 | 60.8447 | 60.8411 | 60.7948 | 60.5488 | 60.5269 | 60.2044 | 60.447 | 0.14016 | -0.50299 | -0.43782 | -0.50119 | -0.39865 | -0.42263 | -0.53885 | 60.832 | 60.8905 | 60.8869 | 60.8405 | 60.5946 | 60.5727 | 60.2501 | 60.4928 | 0.23743 | 0.58186 | 0.29233 | 0.63676
495.25 | 121.7834 | -60.4202 | 61.0016 | 0.085224 | -0.56708 | -0.49733 | -0.5607 | -0.46731 | -0.49129 | -0.60294 | 60.7908 | 60.8401 | 60.8457 | 60.7948 | 60.5534 | 60.5224 | 60.2089 | 60.4424 | 0.131 | -0.52131 | -0.45156 | -0.51492 | -0.42153 | -0.44552 | -0.55717 | 60.8366 | 60.8859 | 60.8915 | 60.8405 | 60.5991 | 60.5681 | 60.2547 | 60.4882 | 0.23743 | 0.58186 | 0.29233 | 0.63676
497.0156 | 121.6553 | -60.4294 | 61.0474 | 0.085224 | -0.59914 | -0.53854 | -0.59733 | -0.49478 | -0.50503 | -0.63499 | 60.8045 | 60.8539 | 60.8594 | 60.8085 | 60.5396 | 60.5086 | 60.1906 | 60.4287 | 0.131 | -0.55336 | -0.49276 | -0.55155 | -0.449 | -0.45925 | -0.58921 | 60.8503 | 60.8996 | 60.9052 | 60.8543 | 60.5854 | 60.5544 | 60.2364 | 60.4745 | 0.2649 | 0.61391 | 0.3198 | 0.66881
498.7031 | 121.6599 | -60.4477 | 61.0474 | 0.089802 | -0.63119 | -0.56601 | -0.63396 | -0.5314 | -0.54166 | -0.66246 | 60.832 | 60.8951 | 60.8961 | 60.8451 | 60.5076 | 60.472 | 60.154 | 60.3967 | 0.13558 | -0.58541 | -0.52024 | -0.58818 | -0.48563 | -0.49588 | -0.61668 | 60.8778 | 60.9408 | 60.9418 | 60.8909 | 60.5534 | 60.5178 | 60.1998 | 60.4424 | 0.32442 | 0.67801 | 0.38848 | 0.74207
500.4531 | 121.7377 | -60.4065 | 61.0336 | 0.085224 | -0.6495 | -0.5889 | -0.65227 | -0.54971 | -0.57371 | -0.68535 | 60.8732 | 60.9225 | 60.9281 | 60.8772 | 60.4618 | 60.44 | 60.1174 | 60.3646 | 0.131 | -0.60373 | -0.54313 | -0.6065 | -0.50394 | -0.52793 | -0.63957 | 60.919 | 60.9683 | 60.9739 | 60.923 | 60.5076 | 60.4857 | 60.1632 | 60.4104 | 0.41141 | 0.75584 | 0.46631 | 0.81074
502.2188 | 121.8109 | -60.3607 | 61.0611 | 0.089802 | -0.69071 | -0.61638 | -0.67974 | -0.59092 | -0.60575 | -0.7174 | 60.8549 | 60.9088 | 60.9144 | 60.8589 | 60.4939 | 60.4537 | 60.1448 | 60.3784 | 0.13558 | -0.64494 | -0.5706 | -0.63397 | -0.54514 | -0.55998 | -0.67162 | 60.9007 | 60.9546 | 60.9602 | 60.9046 | 60.5396 | 60.4995 | 60.1906 | 60.4241 | 0.36105 | 0.71006 | 0.42053 | 0.76954
503.9219 | 121.7194 | -60.3928 | 61.0565 | 0.089802 | -0.7365 | -0.6759 | -0.70721 | -0.63212 | -0.65154 | -0.76318 | 60.8229 | 60.8768 | 60.8869 | 60.8314 | 60.5167 | 60.4857 | 60.1677 | 60.415 | 0.13558 | -0.69072 | -0.63012 | -0.66144 | -0.58634 | -0.60576 | -0.7174 | 60.8686 | 60.9225 | 60.9327 | 60.8772 | 60.5625 | 60.5315 | 60.2135 | 60.4608 | 0.30611 | 0.65512 | 0.37016 | 0.71917
505.6875 | 121.7377 | -60.3653 | 61.0611 | 0.085224 | -0.77313 | -0.70337 | -0.74842 | -0.66874 | -0.69274 | -0.7998 | 60.8686 | 60.918 | 60.919 | 60.8726 | 60.4755 | 60.4445 | 60.1311 | 60.3738 | 0.131 | -0.72735 | -0.65759 | -0.70264 | -0.62296 | -0.64697 | -0.75403 | 60.9144 | 60.9637 | 60.9647 | 60.9184 | 60.5213 | 60.4903 | 60.1769 | 60.4196 | 0.3931 | 0.73753 | 0.44342 | 0.78785
507.4531 | 121.7606 | -60.3745 | 61.0519 | 0.085224 | -0.82808 | -0.75373 | -0.7942 | -0.72368 | -0.74311 | -0.85016 | 60.8366 | 60.8813 | 60.8869 | 60.8314 | 60.5122 | 60.472 | 60.1677 | 60.4012 | 0.131 | -0.7823 | -0.70796 | -0.74843 | -0.6779 | -0.69733 | -0.80439 | 60.8824 | 60.9271 | 60.9327 | 60.8772 | 60.5579 | 60.5178 | 60.2135 | 60.447 | 0.32442 | 0.66885 | 0.37474 | 0.71917
509.1719 | 121.669 | -60.3882 | 61.0931 | 0.085224 | -0.86929 | -0.80868 | -0.83999 | -0.76488 | -0.78431 | -0.90052 | 60.8366 | 60.8905 | 60.8915 | 60.8405 | 60.503 | 60.4812 | 60.1632 | 60.4012 | 0.131 | -0.82351 | -0.7629 | -0.79421 | -0.7191 | -0.73853 | -0.85475 | 60.8824 | 60.9363 | 60.9373 | 60.8863 | 60.5488 | 60.5269 | 60.2089 | 60.447 | 0.33358 | 0.67343 | 0.38848 | 0.72833
510.9375 | 121.7239 | -60.3882 | 61.0291 | 0.089802 | -0.90134 | -0.83615 | -0.86746 | -0.8015 | -0.81636 | -0.92799 | 60.8686 | 60.918 | 60.9327 | 60.8726 | 60.471 | 60.4445 | 60.122 | 60.3692 | 0.13558 | -0.85556 | -0.79037 | -0.82168 | -0.75573 | -0.77058 | -0.88222 | 60.9144 | 60.9637 | 60.9785 | 60.9184 | 60.5167 | 60.4903 | 60.1677 | 60.415 | 0.39767 | 0.74668 | 0.46173 | 0.81074
512.6562 | 121.6736 | -60.3928 | 61.0794 | 0.085224 | -0.93339 | -0.87735 | -0.90409 | -0.83813 | -0.84841 | -0.96004 | 60.8732 | 60.9271 | 60.9281 | 60.8772 | 60.4618 | 60.4354 | 60.1174 | 60.36 | 0.131 | -0.88761 | -0.83158 | -0.85831 | -0.79235 | -0.80263 | -0.91426 | 60.919 | 60.9729 | 60.9739 | 60.923 | 60.5076 | 60.4812 | 60.1632 | 60.4058 | 0.41141 | 0.75584 | 0.46631 | 0.81074
514.4219 | 121.6965 | -60.3287 | 61.1435 | 0.089802 | -0.97918 | -0.92314 | -0.96361 | -0.88391 | -0.90335 | -1.0104 | 60.919 | 60.9683 | 60.9785 | 60.9184 | 60.4206 | 60.3988 | 60.0807 | 60.3188 | 0.13558 | -0.9334 | -0.87737 | -0.91783 | -0.83813 | -0.85757 | -0.96462 | 60.9648 | 61.0141 | 61.0243 | 60.9642 | 60.4664 | 60.4445 | 60.1265 | 60.3646 | 0.4984 | 0.83825 | 0.55787 | 0.89773
516.1406 | 121.6919 | -60.2966 | 61.2076 | 0.085224 | -1.0295 | -0.95977 | -1.0002 | -0.92968 | -0.94913 | -1.0608 | 60.9327 | 60.9958 | 60.9968 | 60.9459 | 60.4023 | 60.3713 | 60.0579 | 60.2914 | 0.131 | -0.98377 | -0.91399 | -0.95446 | -0.88391 | -0.90336 | -1.015 | 60.9785 | 61.0416 | 61.0426 | 60.9916 | 60.4481 | 60.4171 | 60.1036 | 60.3371 | 0.53045 | 0.87488 | 0.5945 | 0.93894
517.8438 | 121.6232 | -60.2829 | 61.1984 | 0.085224 | -1.1394 | -1.0834 | -1.1147 | -1.0441 | -1.0544 | -1.1615 | 60.9602 | 61.0095 | 61.0197 | 60.9642 | 60.3702 | 60.353 | 60.0304 | 60.2685 | 0.131 | -1.0937 | -1.0376 | -1.0689 | -0.99836 | -1.0087 | -1.1157 | 61.006 | 61.0553 | 61.0655 | 61.01 | 60.416 | 60.3987 | 60.0762 | 60.3143 | 0.58996 | 0.92982 | 0.64944 | 0.9893
519.6094 | 121.7148 | -60.2783 | 61.1801 | 0.076067 | -1.1578 | -1.0971 | -1.1284 | -1.0579 | -1.0773 | -1.1935 | 60.9419 | 60.9958 | 61.0059 | 60.9459 | 60.3977 | 60.3576 | 60.0487 | 60.2868 | 0.12184 | -1.112 | -1.0514 | -1.0827 | -1.0121 | -1.0316 | -1.1478 | 60.9877 | 61.0416 | 61.0517 | 60.9916 | 60.4435 | 60.4033 | 60.0945 | 60.3326 | 0.54418 | 0.8932 | 0.60823 | 0.95725
521.375 | 121.7422 | -60.3333 | 61.0611 | 0.080646 | -1.1944 | -1.12 | -1.1559 | -1.0899 | -1.1094 | -1.221 | 60.9282 | 60.9866 | 60.9876 | 60.9413 | 60.4069 | 60.3804 | 60.067 | 60.3051 | 0.12642 | -1.1486 | -1.0742 | -1.1101 | -1.0441 | -1.0636 | -1.1752 | 60.9739 | 61.0324 | 61.0334 | 60.9871 | 60.4526 | 60.4262 | 60.1128 | 60.3509 | 0.52129 | 0.86115 | 0.58076 | 0.92062
523.0625 | 121.7377 | -60.26 | 61.171 | 0.071489 | -1.2539 | -1.1933 | -1.2246 | -1.154 | -1.1689 | -1.2759 | 60.9923 | 61.0416 | 61.0517 | 61.0008 | 60.3519 | 60.3163 | 60.0029 | 60.2319 | 0.11726 | -1.2081 | -1.1475 | -1.1788 | -1.1082 | -1.1231 | -1.2302 | 61.038 | 61.0874 | 61.0975 | 61.0466 | 60.3977 | 60.3621 | 60.0487 | 60.2776 | 0.64033 | 0.98934 | 0.6998 | 1.0488
524.8281 | 121.7377 | -60.1868 | 61.2671 | 0.076067 | -1.3226 | -1.2482 | -1.2887 | -1.2135 | -1.2376 | -1.3492 | 61.0426 | 61.0874 | 61.1021 | 61.0466 | 60.3062 | 60.266 | 59.9526 | 60.1952 | 0.12184 | -1.2768 | -1.2024 | -1.2429 | -1.1677 | -1.1918 | -1.3034 | 61.0884 | 61.1332 | 61.1479 | 61.0924 | 60.3519 | 60.3118 | 59.9983 | 60.241 | 0.73647 | 1.0901 | 0.79594 | 1.1495
526.5312 | 121.6644 | -60.1868 | 61.3403 | 0.071489 | -1.4096 | -1.3581 | -1.3757 | -1.3097 | -1.3246 | -1.4362 | 61.0838 | 61.1423 | 61.1387 | 61.097 | 60.2512 | 60.2111 | 59.9113 | 60.1449 | 0.11726 | -1.3638 | -1.3123 | -1.3299 | -1.2639 | -1.2788 | -1.3904 | 61.1296 | 61.1881 | 61.1845 | 61.1428 | 60.297 | 60.2568 | 59.9571 | 60.1906 | 0.83262 | 1.1725 | 0.8875 | 1.2274
528.2812 | 121.7514 | -60.1273 | 61.2625 | 0.062332 | -1.7072 | -1.6466 | -1.687 | -1.6164 | -1.6405 | -1.7429 | 61.1067 | 61.1606 | 61.1753 | 61.1199 | 60.2329 | 60.1927 | 59.8747 | 60.1174 | 0.10811 | -1.6614 | -1.6008 | -1.6412 | -1.5706 | -1.5947 | -1.6971 | 61.1525 | 61.2064 | 61.2211 | 61.1656 | 60.2787 | 60.2385 | 59.9205 | 60.1632 | 0.87382 | 1.232 | 0.94244 | 1.3006
529.9844 | 121.7285 | -60.0815 | 61.3541 | 0.06691 | -1.8492 | -1.7885 | -1.8244 | -1.7583 | -1.7778 | -1.8848 | 61.1708 | 61.211 | 61.2257 | 61.1702 | 60.1734 | 60.1378 | 59.8244 | 60.0625 | 0.11269 | -1.8034 | -1.7427 | -1.7786 | -1.7125 | -1.732 | -1.8391 | 61.2166 | 61.2568 | 61.2715 | 61.216 | 60.2192 | 60.1836 | 59.8701 | 60.1082 | 0.99743 | 1.3465 | 1.0523 | 1.4013
531.75 | 121.6873 | -60.0632 | 61.4136 | 0.062332 | -1.9682 | -1.9121 | -1.9434 | -1.8636 | -1.8877 | -1.9993 | 61.1937 | 61.2476 | 61.2486 | 61.2069 | 60.1368 | 60.1103 | 59.7923 | 60.035 | 0.10811 | -1.9224 | -1.8663 | -1.8976 | -1.8178 | -1.8419 | -1.9535 | 61.2395 | 61.2934 | 61.2944 | 61.2526 | 60.1825 | 60.1561 | 59.8381 | 60.0808 | 1.057 | 1.4014 | 1.1118 | 1.4563
533.4375 | 121.7743 | -60.0403 | 61.3632 | 0.062332 | -2.0323 | -1.9808 | -2.0121 | -1.9323 | -1.9655 | -2.0634 | 61.2212 | 61.2751 | 61.2806 | 61.2206 | 60.1184 | 60.0829 | 59.7694 | 60.0075 | 0.10811 | -1.9865 | -1.935 | -1.9663 | -1.8865 | -1.9198 | -2.0176 | 61.267 | 61.3209 | 61.3264 | 61.2664 | 60.1642 | 60.1286 | 59.8152 | 60.0533 | 1.1027 | 1.4518 | 1.1622 | 1.5112
535.2031 | 121.7377 | -59.9762 | 61.441 | 0.053175 | -2.0231 | -1.9487 | -1.9938 | -1.9185 | -1.9472 | -2.0542 | 61.2761 | 61.3301 | 61.3356 | 61.2801 | 60.0635 | 60.0234 | 59.7099 | 59.9572 | 0.098951 | -1.9774 | -1.903 | -1.948 | -1.8727 | -1.9014 | -2.0084 | 61.3219 | 61.3758 | 61.3814 | 61.3259 | 60.1093 | 60.0691 | 59.7557 | 60.0029 | 1.2126 | 1.5662 | 1.2721 | 1.6257
536.9062 | 121.6461 | -59.9167 | 61.5921 | 0.053175 | -2.1147 | -2.0586 | -2.0899 | -2.0238 | -2.0434 | -2.1458 | 61.2944 | 61.3529 | 61.3585 | 61.3076 | 60.036 | 60.005 | 59.6962 | 59.9297 | 0.098951 | -2.0689 | -2.0129 | -2.0441 | -1.978 | -1.9976 | -2.1 | 61.3402 | 61.3987 | 61.4043 | 61.3534 | 60.0818 | 60.0508 | 59.7419 | 59.9755 | 1.2584 | 1.5983 | 1.3224 | 1.6623
538.6094 | 121.7743 | -59.9625 | 61.4548 | 0.053175 | -2.2887 | -2.2418 | -2.2685 | -2.1978 | -2.1899 | -2.3243 | 61.2944 | 61.3575 | 61.3539 | 61.2985 | 60.0406 | 60.0142 | 59.6916 | 59.9343 | 0.098951 | -2.2429 | -2.196 | -2.2227 | -2.152 | -2.1441 | -2.2786 | 61.3402 | 61.4033 | 61.3997 | 61.3442 | 60.0864 | 60.06 | 59.7374 | 59.98 | 1.2538 | 1.6029 | 1.3133 | 1.6623
540.3906 | 121.7697 | -59.8572 | 61.5509 | 0.044018 | -2.3666 | -2.2967 | -2.3326 | -2.2619 | -2.2631 | -2.3839 | 61.3128 | 61.3667 | 61.3722 | 61.3122 | 60.0223 | 59.9913 | 59.6733 | 59.9114 | 0.089794 | -2.3208 | -2.2509 | -2.2868 | -2.2161 | -2.2174 | -2.3381 | 61.3585 | 61.4125 | 61.418 | 61.358 | 60.0681 | 60.0371 | 59.719 | 59.9572 | 1.2904 | 1.6395 | 1.3499 | 1.6989
542.1719 | 121.669 | -59.7977 | 61.6974 | 0.044018 | -2.5955 | -2.5302 | -2.5752 | -2.4953 | -2.5012 | -2.6265 | 61.3631 | 61.4216 | 61.4271 | 61.3717 | 59.9674 | 59.9272 | 59.6183 | 59.861 | 0.089794 | -2.5497 | -2.4845 | -2.5295 | -2.4496 | -2.4554 | -2.5807 | 61.4089 | 61.4674 | 61.4729 | 61.4175 | 60.0131 | 59.973 | 59.6641 | 59.9068 | 1.3957 | 1.7448 | 1.4598 | 1.8088
543.875 | 121.7697 | -59.935 | 61.5051 | 0.030283 | -2.797 | -2.7317 | -2.7767 | -2.6968 | -2.6935 | -2.8234 | 61.2944 | 61.3438 | 61.3585 | 61.2939 | 60.0406 | 60.0142 | 59.6962 | 59.9389 | 0.076059 | -2.7512 | -2.6859 | -2.7309 | -2.651 | -2.6477 | -2.7776 | 61.3402 | 61.3896 | 61.4043 | 61.3396 | 60.0864 | 60.06 | 59.7419 | 59.9846 | 1.2538 | 1.5983 | 1.3179 | 1.6623
545.5781 | 121.6919 | -60.0082 | 61.4639 | 0.030283 | -2.8794 | -2.8095 | -2.8545 | -2.7746 | -2.7896 | -2.9058 | 61.2258 | 61.2843 | 61.299 | 61.2389 | 60.1093 | 60.0646 | 59.7511 | 59.9938 | 0.076059 | -2.8336 | -2.7637 | -2.8088 | -2.7288 | -2.7439 | -2.86 | 61.2715 | 61.33 | 61.3447 | 61.2847 | 60.1551 | 60.1103 | 59.7969 | 60.0396 | 1.1165 | 1.4747 | 1.1897 | 1.5479
547.3438 | 121.7789 | -59.9579 | 61.4365 | 0.021127 | -2.9801 | -2.9194 | -2.9507 | -2.8753 | -2.8812 | -3.0156 | 61.3128 | 61.3713 | 61.3722 | 61.3168 | 60.0131 | 59.9821 | 59.6733 | 59.9114 | 0.066903 | -2.9343 | -2.8736 | -2.9049 | -2.8295 | -2.8354 | -2.9699 | 61.3585 | 61.417 | 61.418 | 61.3625 | 60.0589 | 60.0279 | 59.719 | 59.9572 | 1.2996 | 1.6395 | 1.3591 | 1.6989
549.125 | 121.637 | -59.9625 | 61.5326 | 0.021127 | -3.1679 | -3.1117 | -3.143 | -3.0676 | -3.0827 | -3.1942 | 61.3219 | 61.3804 | 61.3905 | 61.3351 | 60.004 | 59.9776 | 59.655 | 59.8931 | 0.066903 | -3.1221 | -3.0659 | -3.0972 | -3.0218 | -3.0369 | -3.1484 | 61.3677 | 61.4262 | 61.4363 | 61.3809 | 60.0498 | 60.0233 | 59.7007 | 59.9388 | 1.3179 | 1.667 | 1.3865 | 1.7356
550.8906 | 121.7743 | -60.0952 | 61.3083 | 0.01197 | -3.4746 | -3.4047 | -3.4406 | -3.3697 | -3.3803 | -3.4918 | 61.1113 | 61.1652 | 61.1708 | 61.1107 | 60.2192 | 60.1927 | 59.8747 | 60.1174 | 0.057746 | -3.4289 | -3.359 | -3.3948 | -3.324 | -3.3345 | -3.446 | 61.1571 | 61.211 | 61.2165 | 61.1565 | 60.2649 | 60.2385 | 59.9205 | 60.1632 | 0.89213 | 1.2366 | 0.9516 | 1.296
552.5938 | 121.7789 | -59.9854 | 61.3953 | -0.015501 | -3.9737 | -3.9084 | -3.9488 | -3.8779 | -3.8885 | -3.9954 | 61.18 | 61.2293 | 61.2349 | 61.1748 | 60.1551 | 60.1241 | 59.8106 | 60.0533 | 0.030275 | -3.9279 | -3.8626 | -3.903 | -3.8321 | -3.8427 | -3.9496 | 61.2258 | 61.2751 | 61.2806 | 61.2206 | 60.2008 | 60.1698 | 59.8564 | 60.0991 | 1.0249 | 1.3694 | 1.0798 | 1.4242
554.3438 | 121.756 | -60.0128 | 61.4136 | -0.015501 | -4.34 | -4.2747 | -4.3151 | -4.2395 | -4.2593 | -4.3616 | 61.2578 | 61.3163 | 61.3173 | 61.2618 | 60.0772 | 60.0462 | 59.7282 | 59.9617 | 0.030275 | -4.2943 | -4.2289 | -4.2693 | -4.1938 | -4.2135 | -4.3158 | 61.3036 | 61.3621 | 61.363 | 61.3076 | 60.123 | 60.092 | 59.774 | 60.0075 | 1.1806 | 1.5296 | 1.24 | 1.5891
556.0625 | 121.7239 | -59.9075 | 61.5051 | -0.024657 | -4.4637 | -4.4029 | -4.4387 | -4.3677 | -4.3783 | -4.4852 | 61.3082 | 61.3529 | 61.3631 | 61.3122 | 60.0315 | 59.9867 | 59.6778 | 59.9251 | 0.021119 | -4.4179 | -4.3571 | -4.3929 | -4.322 | -4.3326 | -4.4395 | 61.354 | 61.3987 | 61.4088 | 61.358 | 60.0772 | 60.0325 | 59.7236 | 59.9709 | 1.2767 | 1.6303 | 1.3316 | 1.6852
557.8281 | 121.6415 | -59.9396 | 61.5097 | -0.047549 | -4.9261 | -4.8699 | -4.9149 | -4.8301 | -4.8499 | -4.9476 | 61.354 | 61.4079 | 61.4134 | 61.3534 | 59.9857 | 59.9501 | 59.6321 | 59.8656 | -0.001773 | -4.8803 | -4.8241 | -4.8691 | -4.7843 | -4.8041 | -4.9019 | 61.3997 | 61.4537 | 61.4592 | 61.3992 | 60.0315 | 59.9959 | 59.6778 | 59.9114 | 1.3683 | 1.7219 | 1.4277 | 1.7813
559.5312 | 121.6782 | -59.8938 | 61.5509 | -0.056706 | -5.1276 | -5.0759 | -5.1071 | -5.0361 | -5.0468 | -5.1491 | 61.3402 | 61.3987 | 61.4043 | 61.3488 | 59.9903 | 59.9593 | 59.6412 | 59.8748 | -0.01093 | -5.0818 | -5.0302 | -5.0614 | -4.9903 | -5.001 | -5.1033 | 61.386 | 61.4445 | 61.45 | 61.3946 | 60.036 | 60.005 | 59.687 | 59.9205 | 1.35 | 1.699 | 1.414 | 1.763
561.2969 | 121.7606 | -59.8114 | 61.5967 | -0.07502 | -5.2512 | -5.1996 | -5.2353 | -5.1597 | -5.175 | -5.2727 | 61.3906 | 61.4445 | 61.4546 | 61.3992 | 59.9353 | 59.9043 | 59.5954 | 59.829 | -0.029244 | -5.2054 | -5.1538 | -5.1896 | -5.1139 | -5.1292 | -5.2269 | 61.4364 | 61.4903 | 61.5004 | 61.445 | 59.9811 | 59.9501 | 59.6412 | 59.8747 | 1.4553 | 1.7951 | 1.5193 | 1.8592
563 | 121.6965 | -59.7931 | 61.6745 | -0.070441 | -5.1322 | -5.0622 | -5.098 | -5.0407 | -5.0468 | -5.1491 | 61.4089 | 61.4583 | 61.4684 | 61.4175 | 59.9262 | 59.8906 | 59.5771 | 59.8107 | -0.024665 | -5.0864 | -5.0164 | -5.0522 | -4.9949 | -5.001 | -5.1033 | 61.4547 | 61.504 | 61.5141 | 61.4633 | 59.9719 | 59.9364 | 59.6229 | 59.8564 | 1.4827 | 1.8318 | 1.5422 | 1.8912
564.7969 | 121.6461 | -60.1868 | 61.3358 | -0.093333 | -5.851 | -5.7994 | -5.8397 | -5.7686 | -5.7931 | -5.8862 | 61.038 | 61.092 | 61.1021 | 61.042 | 60.297 | 60.266 | 59.9434 | 60.1815 | -0.047557 | -5.8053 | -5.7536 | -5.7939 | -5.7228 | -5.7473 | -5.8404 | 61.0838 | 61.1377 | 61.1479 | 61.0878 | 60.3428 | 60.3118 | 59.9892 | 60.2273 | 0.74105 | 1.0946 | 0.8051 | 1.1587
566.4844 | 121.7194 | -60.2188 | 61.2167 | -0.11165 | -6.025 | -5.9688 | -6.0045 | -5.9242 | -5.9579 | -6.0418 | 60.9327 | 61.0004 | 61.0014 | 60.9459 | 60.3886 | 60.3621 | 60.0395 | 60.2822 | -0.065871 | -5.9793 | -5.923 | -5.9588 | -5.8785 | -5.9121 | -5.996 | 60.9785 | 61.0462 | 61.0471 | 60.9916 | 60.4343 | 60.4079 | 60.0853 | 60.328 | 0.54418 | 0.89319 | 0.61281 | 0.96183
568.25 | 121.6415 | -60.1547 | 61.3495 | -0.11165 | -5.9426 | -5.8772 | -5.913 | -5.8418 | -5.8663 | -5.964 | 61.1021 | 61.1561 | 61.1616 | 61.1016 | 60.2237 | 60.2019 | 59.8793 | 60.122 | -0.065871 | -5.8968 | -5.8314 | -5.8672 | -5.7961 | -5.8205 | -5.9182 | 61.1479 | 61.2018 | 61.2074 | 61.1473 | 60.2695 | 60.2477 | 59.9251 | 60.1678 | 0.8784 | 1.2228 | 0.93786 | 1.2823
569.9375 | 121.756 | -60.1685 | 61.2396 | -0.10249 | -5.4481 | -5.3781 | -5.4139 | -5.3337 | -5.3673 | -5.4558 | 61.0564 | 61.1103 | 61.1112 | 61.0558 | 60.2787 | 60.2477 | 59.9251 | 60.1678 | -0.056714 | -5.4023 | -5.3323 | -5.3681 | -5.2879 | -5.3215 | -5.41 | 61.1021 | 61.156 | 61.157 | 61.1015 | 60.3245 | 60.2935 | 59.9709 | 60.2135 | 0.77768 | 1.1313 | 0.83257 | 1.1862
571.6406 | 121.7148 | -60.2051 | 61.2122 | -0.11622 | -5.6129 | -5.543 | -5.5742 | -5.4985 | -5.5275 | -5.6252 | 61.0655 | 61.1194 | 61.1296 | 61.0741 | 60.2695 | 60.2339 | 59.9251 | 60.1586 | -0.070449 | -5.5672 | -5.4972 | -5.5284 | -5.4527 | -5.4817 | -5.5794 | 61.1113 | 61.1652 | 61.1753 | 61.1199 | 60.3153 | 60.2797 | 59.9709 | 60.2044 | 0.79599 | 1.1404 | 0.86004 | 1.2045
573.3906 | 121.756 | -59.9213 | 61.4685 | -0.11622 | -5.3657 | -5.2957 | -5.3223 | -5.2513 | -5.2803 | -5.3826 | 61.2899 | 61.3529 | 61.3631 | 61.303 | 60.0269 | 60.0005 | 59.6824 | 59.9205 | -0.070449 | -5.3199 | -5.2499 | -5.2766 | -5.2055 | -5.2345 | -5.3368 | 61.3356 | 61.3987 | 61.4088 | 61.3488 | 60.0727 | 60.0462 | 59.7282 | 59.9663 | 1.263 | 1.6074 | 1.3362 | 1.6806
575.1719 | 121.6461 | -59.8846 | 61.5921 | -0.13454 | -5.6175 | -5.5521 | -5.5833 | -5.5122 | -5.5413 | -5.6435 | 61.299 | 61.3575 | 61.3631 | 61.303 | 60.0269 | 59.9913 | 59.6778 | 59.9068 | -0.088763 | -5.5717 | -5.5063 | -5.5375 | -5.4664 | -5.4955 | -5.5977 | 61.3448 | 61.4033 | 61.4088 | 61.3488 | 60.0727 | 60.0371 | 59.7236 | 59.9526 | 1.2721 | 1.6212 | 1.3362 | 1.6852
576.9375 | 121.7056 | -60.1318 | 61.2991 | -0.15285 | -5.9243 | -5.868 | -5.8855 | -5.8098 | -5.848 | -5.9365 | 61.093 | 61.1423 | 61.1525 | 61.097 | 60.2421 | 60.2111 | 59.8885 | 60.1266 | -0.10708 | -5.8785 | -5.8223 | -5.8397 | -5.764 | -5.8022 | -5.8907 | 61.1388 | 61.1881 | 61.1982 | 61.1428 | 60.2878 | 60.2568 | 59.9342 | 60.1723 | 0.85093 | 1.2045 | 0.91039 | 1.264
578.6406 | 121.7102 | -60.0815 | 61.3358 | -0.18948 | -6.2998 | -6.2343 | -6.2609 | -6.1943 | -6.228 | -6.3165 | 61.1433 | 61.1973 | 61.2028 | 61.1428 | 60.1963 | 60.1561 | 59.8381 | 60.0854 | -0.1437 | -6.254 | -6.1885 | -6.2152 | -6.1486 | -6.1822 | -6.2707 | 61.1891 | 61.243 | 61.2486 | 61.1885 | 60.2421 | 60.2019 | 59.8839 | 60.1311 | 0.94707 | 1.3053 | 1.0065 | 1.3647
580.3906 | 121.637 | -60.26 | 61.2167 | -0.21237 | -6.776 | -6.7151 | -6.7371 | -6.6704 | -6.7179 | -6.7881 | 60.9465 | 61.0004 | 61.0105 | 60.9504 | 60.3886 | 60.3484 | 60.0395 | 60.2822 | -0.16659 | -6.7302 | -6.6693 | -6.6913 | -6.6247 | -6.6721 | -6.7423 | 60.9922 | 61.0462 | 61.0563 | 60.9962 | 60.4343 | 60.3942 | 60.0853 | 60.328 | 0.55792 | 0.90693 | 0.62197 | 0.97098
582.0781 | 121.7148 | -60.5759 | 60.8368 | -0.23984 | -6.9225 | -6.8479 | -6.8699 | -6.8032 | -6.8461 | -6.9254 | 60.6626 | 60.7119 | 60.7267 | 60.6665 | 60.6724 | 60.6322 | 60.3188 | 60.5615 | -0.19407 | -6.8767 | -6.8021 | -6.8241 | -6.7574 | -6.8003 | -6.8796 | 60.7084 | 60.7577 | 60.7724 | 60.7123 | 60.7182 | 60.678 | 60.3646 | 60.6073 | -0.009798 | 0.34378 | 0.054267 | 0.40785
583.8438 | 121.6782 | -60.6491 | 60.8139 | -0.25816 | -7.0461 | -6.9806 | -7.0072 | -6.9405 | -6.9789 | -7.0536 | 60.5802 | 60.6387 | 60.6443 | 60.5887 | 60.7457 | 60.7101 | 60.3921 | 60.6439 | -0.21238 | -7.0003 | -6.9349 | -6.9614 | -6.8948 | -6.9331 | -7.0078 | 60.626 | 60.6844 | 60.69 | 60.6345 | 60.7914 | 60.7558 | 60.4379 | 60.6897 | -0.16546 | 0.18812 | -0.10139 | 0.25219
585.5469 | 121.7514 | -61.4319 | 59.9533 | -0.29478 | -7.4994 | -7.4385 | -7.4651 | -7.3846 | -7.4413 | -7.5114 | 59.8202 | 59.8786 | 59.8843 | 59.824 | 61.5102 | 61.47 | 61.1567 | 61.3947 | -0.24901 | -7.4536 | -7.3927 | -7.4193 | -7.3388 | -7.3955 | -7.4656 | 59.8659 | 59.9243 | 59.93 | 59.8698 | 61.556 | 61.5158 | 61.2024 | 61.4405 | -1.69 | -1.3365 | -1.6259 | -1.2724
587.3281 | 121.7651 | -60.7773 | 60.6171 | -0.31767 | -7.7192 | -7.6445 | -7.6757 | -7.5998 | -7.6427 | -7.7174 | 60.3284 | 60.3914 | 60.397 | 60.346 | 60.9883 | 60.9573 | 60.6393 | 60.882 | -0.2719 | -7.6734 | -7.5988 | -7.6299 | -7.554 | -7.597 | -7.6716 | 60.3742 | 60.4372 | 60.4428 | 60.3918 | 61.0341 | 61.0031 | 60.6851 | 60.9277 | -0.65992 | -0.31093 | -0.59126 | -0.24227
589.0312 | 121.7789 | -60.4843 | 60.9009 | -0.32683 | -7.71 | -7.64 | -7.6619 | -7.5906 | -7.6336 | -7.7128 | 60.6855 | 60.7302 | 60.777 | 60.7123 | 60.6541 | 60.6231 | 60.3188 | 60.5432 | -0.28105 | -7.6643 | -7.5942 | -7.6162 | -7.5448 | -7.5878 | -7.6671 | 60.7313 | 60.776 | 60.8228 | 60.7581 | 60.6999 | 60.6689 | 60.3646 | 60.5889 | 0.031407 | 0.36668 | 0.12294 | 0.45821
590.7969 | 121.6599 | -62.4481 | 59.0332 | -0.38177 | -8.3373 | -8.313 | -8.3304 | -8.2636 | -8.3112 | -8.3904 | 58.7396 | 58.798 | 58.7992 | 58.7937 | 62.5907 | 62.555 | 62.2463 | 62.4797 | -0.336 | -8.2916 | -8.2672 | -8.2846 | -8.2178 | -8.2654 | -8.3446 | 58.7854 | 58.8437 | 58.845 | 58.8395 | 62.6364 | 62.6008 | 62.2921 | 62.5255 | -3.851 | -3.5067 | -3.7914 | -3.4471
592.5781 | 121.7285 | -62.6266 | 58.754 | -0.43213 | -8.6945 | -8.661 | -8.6921 | -8.6115 | -8.6683 | -8.7338 | 58.671 | 58.7201 | 58.7443 | 58.7205 | 62.6685 | 62.6237 | 62.3058 | 62.5438 | -0.38636 | -8.6487 | -8.6152 | -8.6463 | -8.5657 | -8.6225 | -8.688 | 58.7167 | 58.7659 | 58.7901 | 58.7662 | 62.7143 | 62.6695 | 62.3516 | 62.5896 | -3.9975 | -3.6349 | -3.9242 | -3.5616
594.3438 | 121.6461 | -63.4964 | 57.9483 | -0.46418 | -8.9692 | -8.9449 | -8.9668 | -8.8908 | -8.9384 | -9.013 | 57.8377 | 57.8914 | 57.8881 | 57.8917 | 63.4926 | 63.4615 | 63.1437 | 63.3816 | -0.41841 | -8.9234 | -8.8991 | -8.921 | -8.845 | -8.8926 | -8.9673 | 57.8835 | 57.9371 | 57.9339 | 57.9374 | 63.5383 | 63.5073 | 63.1895 | 63.4274 | -5.6549 | -5.306 | -5.6044 | -5.2556
596.0938 | 121.7926 | -64.2883 | 57.1381 | -0.50997 | -9.2531 | -9.2287 | -9.2553 | -9.1746 | -9.2223 | -9.2923 | 56.9494 | 57.0031 | 57.0045 | 57.0033 | 64.3716 | 64.3496 | 64.0227 | 64.2652 | -0.46419 | -9.2073 | -9.1829 | -9.2095 | -9.1288 | -9.1765 | -9.2465 | 56.9952 | 57.0488 | 57.0503 | 57.0491 | 64.4173 | 64.3954 | 64.0685 | 64.311 | -7.4221 | -7.0733 | -7.367 | -7.0182
597.8594 | 121.6461 | -63.0432 | 58.4427 | -0.55117 | -9.4866 | -9.4531 | -9.4796 | -9.4081 | -9.4558 | -9.5258 | 58.1582 | 58.2119 | 58.2224 | 58.2168 | 63.1812 | 63.1456 | 62.8232 | 63.0612 | -0.5054 | -9.4408 | -9.4073 | -9.4338 | -9.3623 | -9.41 | -9.48 | 58.2039 | 58.2577 | 58.2681 | 58.2625 | 63.227 | 63.1914 | 62.869 | 63.1069 | -5.0231 | -4.665 | -4.9589 | -4.6008
599.5625 | 121.6782 | -63.7848 | 57.6691 | -0.60611 | -9.8758 | -9.8468 | -9.8688 | -9.788 | -9.8404 | -9.9195 | 57.4256 | 57.4793 | 57.4807 | 57.4795 | 63.9 | 63.8781 | 63.5512 | 63.7845 | -0.56034 | -9.83 | -9.8011 | -9.823 | -9.7423 | -9.7946 | -9.8737 | 57.4714 | 57.525 | 57.5264 | 57.5253 | 63.9458 | 63.9239 | 63.5969 | 63.8303 | -6.4744 | -6.1256 | -6.4193 | -6.0705
601.3125 | 121.7606 | -64.325 | 57.1106 | -0.64732 | -9.9811 | -9.9521 | -9.9787 | -9.8933 | -9.9457 | -10.0065 | 57.096 | 57.1542 | 57.151 | 57.1498 | 64.2388 | 64.2031 | 63.8717 | 64.1187 | -0.60154 | -9.9354 | -9.9064 | -9.9329 | -9.8476 | -9.8999 | -9.9607 | 57.1417 | 57.1999 | 57.1968 | 57.1956 | 64.2846 | 64.2489 | 63.9174 | 64.1645 | -7.1428 | -6.7757 | -7.0878 | -6.7206
603.0781 | 121.7651 | -64.769 | 56.6437 | -0.7572 | -10.9518 | -10.9274 | -10.9493 | -10.873 | -10.9209 | -10.9862 | 56.4412 | 56.4994 | 56.5009 | 56.4996 | 64.8797 | 64.8532 | 64.5264 | 64.7642 | -0.71142 | -10.9061 | -10.8816 | -10.9035 | -10.8272 | -10.8751 | -10.9405 | 56.487 | 56.5452 | 56.5467 | 56.5454 | 64.9255 | 64.899 | 64.5721 | 64.81 | -8.4385 | -8.0851 | -8.3788 | -8.0254
604.8594 | 121.6873 | -63.8351 | 57.6141 | -0.77551 | -10.8557 | -10.8267 | -10.8532 | -10.7677 | -10.8201 | -10.8901 | 57.3569 | 57.4152 | 57.4212 | 57.42 | 63.9733 | 63.9468 | 63.6153 | 63.8532 | -0.72974 | -10.8099 | -10.7809 | -10.8074 | -10.7219 | -10.7744 | -10.8443 | 57.4027 | 57.4609 | 57.4669 | 57.4658 | 64.019 | 63.9925 | 63.661 | 63.899 | -6.6163 | -6.2583 | -6.5521 | -6.1941
606.5625 | 121.7239 | -65.3 | 56.0898 | -0.83961 | -11.0159 | -11.0006 | -11.0226 | -10.9371 | -10.9895 | -11.0458 | 56.0704 | 56.1194 | 56.1301 | 56.1241 | 65.2597 | 65.2286 | 64.9018 | 65.1397 | -0.79383 | -10.9702 | -10.9549 | -10.9768 | -10.8913 | -10.9438 | -11 | 56.1162 | 56.1651 | 56.1759 | 56.1699 | 65.3055 | 65.2744 | 64.9476 | 65.1854 | -9.1894 | -8.8314 | -9.1297 | -8.7717
608.3438 | 121.7285 | -66.9388 | 54.4785 | -0.94034 | -11.776 | -11.747 | -11.7734 | -11.6787 | -11.7404 | -11.8012 | 54.3397 | 54.3931 | 54.3995 | 54.3979 | 66.9949 | 66.9591 | 66.6278 | 66.8656 | -0.89456 | -11.7303 | -11.7012 | -11.7277 | -11.633 | -11.6946 | -11.7554 | 54.3855 | 54.4389 | 54.4453 | 54.4436 | 67.0406 | 67.0049 | 66.6736 | 66.9114 | -12.6552 | -12.2881 | -12.5954 | -12.2284
610.1094 | 121.7468 | -67.3737 | 54.0756 | -1.0182 | -12.0187 | -11.985 | -12.0069 | -11.9122 | -11.9693 | -12.0438 | 53.8223 | 53.8803 | 53.8821 | 53.885 | 67.503 | 67.4719 | 67.1498 | 67.383 | -0.97239 | -11.9729 | -11.9393 | -11.9612 | -11.8664 | -11.9235 | -11.998 | 53.8681 | 53.9261 | 53.9279 | 53.9308 | 67.5488 | 67.5176 | 67.1956 | 67.4287 | -13.6807 | -13.3274 | -13.6209 | -13.2676
611.8125 | 121.7102 | -68.7469 | 52.6428 | -1.1509 | -12.9436 | -12.9237 | -12.9455 | -12.8507 | -12.9033 | -12.9732 | 52.5495 | 52.6028 | 52.6048 | 52.6075 | 68.7803 | 68.7491 | 68.4226 | 68.6557 | -1.1052 | -12.8979 | -12.8779 | -12.8998 | -12.8049 | -12.8575 | -12.9274 | 52.5953 | 52.6486 | 52.6506 | 52.6532 | 68.8261 | 68.7949 | 68.4683 | 68.7015 | -16.2308 | -15.8731 | -16.1755 | -15.8178
613.5312 | 121.6324 | -69.6899 | 51.7319 | -1.2883 | -13.7953 | -13.7707 | -13.7971 | -13.7022 | -13.7549 | -13.8339 | 51.73 | 51.7924 | 51.7899 | 51.7878 | 69.5998 | 69.5686 | 69.2329 | 69.466 | -1.2425 | -13.7495 | -13.7249 | -13.7514 | -13.6564 | -13.7091 | -13.7881 | 51.7757 | 51.8382 | 51.8356 | 51.8336 | 69.6456 | 69.6144 | 69.2787 | 69.5118 | -17.8699 | -17.503 | -17.81 | -17.4431
615.2969 | 121.6278 | -69.3878 | 52.0981 | -1.3387 | -13.8869 | -13.8714 | -13.8933 | -13.7892 | -13.8373 | -13.9117 | 52.0505 | 52.1083 | 52.1103 | 52.1083 | 69.2794 | 69.2527 | 68.9216 | 69.1501 | -1.2929 | -13.8411 | -13.8257 | -13.8475 | -13.7434 | -13.7915 | -13.8659 | 52.0962 | 52.1541 | 52.1561 | 52.1541 | 69.3251 | 69.2985 | 68.9674 | 69.1959 | -17.2289 | -16.8712 | -17.169 | -16.8113
617.0625 | 121.7056 | -69.6075 | 51.8097 | -1.4348 | -14.1387 | -14.1278 | -14.1359 | -14.0364 | -14.0937 | -14.1635 | 51.7345 | 51.7924 | 51.7899 | 51.797 | 69.5907 | 69.5549 | 69.2375 | 69.466 | -1.389 | -14.0929 | -14.0821 | -14.0902 | -13.9906 | -14.0479 | -14.1177 | 51.7803 | 51.8382 | 51.8356 | 51.8427 | 69.6365 | 69.6007 | 69.2833 | 69.5118 | -17.8561 | -17.503 | -17.8008 | -17.4477
618.8438 | 121.7194 | -69.0445 | 52.3636 | -1.4348 | -13.722 | -13.6883 | -13.7056 | -13.5969 | -13.6496 | -13.724 | 52.284 | 52.3373 | 52.3438 | 52.3419 | 69.0413 | 69.0101 | 68.6835 | 68.9258 | -1.389 | -13.6762 | -13.6425 | -13.6598 | -13.5511 | -13.6038 | -13.6782 | 52.3297 | 52.383 | 52.3896 | 52.3876 | 69.0871 | 69.0559 | 68.7293 | 68.9716 | -16.7573 | -16.3996 | -16.6975 | -16.3397
620.5469 | 121.7194 | -70.1431 | 51.2741 | -1.6134 | -14.679 | -14.6635 | -14.6716 | -14.5674 | -14.6156 | -14.6946 | 51.3316 | 51.3894 | 51.387 | 51.3848 | 70.0027 | 69.9669 | 69.6313 | 69.8781 | -1.5676 | -14.6332 | -14.6178 | -14.6258 | -14.5216 | -14.5698 | -14.6488 | 51.3774 | 51.4352 | 51.4328 | 51.4306 | 70.0485 | 70.0127 | 69.677 | 69.9238 | -18.6711 | -18.2996 | -18.6157 | -18.2443
622.2812 | 121.6461 | -69.5389 | 51.915 | -1.7644 | -15.32 | -15.3 | -15.308 | -15.2038 | -15.252 | -15.3355 | 51.5606 | 51.6275 | 51.6205 | 51.6275 | 69.7555 | 69.7243 | 69.3932 | 69.6354 | -1.7187 | -15.2743 | -15.2542 | -15.2623 | -15.158 | -15.2062 | -15.2897 | 51.6063 | 51.6733 | 51.6662 | 51.6733 | 69.8013 | 69.77 | 69.439 | 69.6812 | -18.1949 | -17.8326 | -18.135 | -17.7727
624.0469 | 121.6278 | -67.9047 | 53.5629 | -1.9613 | -16.3686 | -16.353 | -16.3565 | -16.243 | -16.3005 | -16.3839 | 53.3279 | 53.3904 | 53.3831 | 53.3859 | 67.9975 | 67.9571 | 67.6305 | 67.8774 | -1.9155 | -16.3228 | -16.3073 | -16.3107 | -16.1972 | -16.2547 | -16.3381 | 53.3736 | 53.4362 | 53.4289 | 53.4317 | 68.0433 | 68.0029 | 67.6763 | 67.9232 | -14.6696 | -14.3027 | -14.6144 | -14.2474
625.75 | 121.6415 | -75.0275 | 46.4539 | -2.4192 | -18.951 | -18.9354 | -18.9434 | -18.802 | -18.8781 | -18.966 | 47.3438 | 47.3784 | 47.4359 | 47.3919 | 73.9766 | 73.9453 | 73.6328 | 73.8336 | -2.3734 | -18.9053 | -18.8896 | -18.8976 | -18.7563 | -18.8323 | -18.9202 | 47.3895 | 47.4242 | 47.4817 | 47.4377 | 74.0224 | 73.991 | 73.6786 | 73.8794 | -26.6328 | -26.289 | -26.5407 | -26.1969
627.5312 | 121.7606 | -79.1428 | 42.1967 | -2.8358 | -21.2038 | -21.1972 | -21.1914 | -21.059 | -21.1261 | -21.2093 | 42.0281 | 42.067 | 42.1068 | 42.0711 | 79.2873 | 79.265 | 78.9208 | 79.1351 | -2.79 | -21.158 | -21.1514 | -21.1456 | -21.0132 | -21.0803 | -21.1635 | 42.0739 | 42.1127 | 42.1526 | 42.1169 | 79.333 | 79.3107 | 78.9666 | 79.1809 | -37.2591 | -36.8927 | -37.1805 | -36.814
629.2969 | 121.6827 | -74.4278 | 47.0306 | -2.6801 | -19.647 | -19.6267 | -19.6393 | -19.4842 | -19.5557 | -19.6619 | 46.9546 | 47.0167 | 47.0101 | 46.9661 | 74.1918 | 74.3344 | 73.9945 | 74.1541 | -2.6343 | -19.6012 | -19.581 | -19.5935 | -19.4384 | -19.5099 | -19.6161 | 47.0004 | 47.0624 | 47.0559 | 47.0119 | 74.2375 | 74.3802 | 74.0402 | 74.1999 | -27.2372 | -27.0399 | -27.1816 | -26.9843
631.0625 | 121.6644 | -81.0287 | 40.3976 | -3.2295 | -22.4493 | -22.4334 | -22.4459 | -22.2904 | -22.3531 | -22.4637 | 40.3158 | 40.3774 | 40.3625 | 40.3769 | 80.8393 | 80.9772 | 80.6377 | 80.8703 | -3.1838 | -22.4035 | -22.3876 | -22.4001 | -22.2447 | -22.3073 | -22.4179 | 40.3616 | 40.4232 | 40.4083 | 40.4226 | 80.885 | 81.0229 | 80.6835 | 80.916 | -40.5235 | -40.3219 | -40.4768 | -40.2752
632.7969 | 121.6782 | -79.3488 | 42.1005 | -3.3303 | -22.2798 | -22.2823 | -22.2719 | -22.1256 | -22.1883 | -22.2943 | 41.9823 | 42.0349 | 42.029 | 42.0345 | 79.182 | 79.3153 | 78.9712 | 79.1946 | -3.2845 | -22.2341 | -22.2365 | -22.2261 | -22.0799 | -22.1425 | -22.2486 | 42.0281 | 42.0807 | 42.0747 | 42.0802 | 79.2277 | 79.3611 | 79.017 | 79.2404 | -37.1996 | -36.9888 | -37.153 | -36.9422
634.5781 | 121.7789 | -86.5585 | 34.758 | -3.5821 | -22.9392 | -22.9645 | -22.9221 | -22.7803 | -22.843 | -22.949 | 37.0101 | 37.0211 | 37.0707 | 37.0433 | 84.1493 | 84.2917 | 83.9479 | 84.1665 | -3.5363 | -22.8934 | -22.9188 | -22.8763 | -22.7345 | -22.7972 | -22.9032 | 37.0559 | 37.0669 | 37.1165 | 37.0891 | 84.1951 | 84.3375 | 83.9937 | 84.2123 | -47.1392 | -46.9378 | -47.0786 | -46.8772
636.3594 | 121.7285 | -87.6663 | 33.7234 | -4.191 | -25.8101 | -25.8033 | -25.7928 | -25.6369 | -25.6953 | -25.8149 | 33.5488 | 33.6191 | 33.5912 | 33.6136 | 87.5921 | 87.7435 | 87.3863 | 87.6231 | -4.1452 | -25.7643 | -25.7575 | -25.747 | -25.5912 | -25.6495 | -25.7692 | 33.5945 | 33.6648 | 33.637 | 33.6594 | 87.6378 | 87.7893 | 87.432 | 87.6688 | -54.0433 | -53.8375 | -54.0009 | -53.795
638.125 | 121.6141 | -81.1066 | 40.3519 | -4.1086 | -24.6929 | -24.6495 | -24.6619 | -24.5016 | -24.5416 | -24.6887 | 37.9533 | 38.0468 | 38.0367 | 38.0324 | 83.1741 | 83.3257 | 82.9773 | 83.1502 | -4.0628 | -24.6471 | -24.6037 | -24.6161 | -24.4558 | -24.4958 | -24.6429 | 37.999 | 38.0925 | 38.0825 | 38.0782 | 83.2199 | 83.3715 | 83.023 | 83.196 | -45.2209 | -45.024 | -45.1374 | -44.9406
639.8281 | 121.756 | -82.7133 | 38.6673 | -4.2597 | -24.5509 | -24.5304 | -24.5245 | -24.4009 | -24.4363 | -24.5468 | 38.7087 | 38.7794 | 38.7509 | 38.7192 | 82.4325 | 82.5795 | 82.2401 | 82.3856 | -4.2139 | -24.5052 | -24.4846 | -24.4788 | -24.3551 | -24.3905 | -24.501 | 38.7545 | 38.8252 | 38.7967 | 38.765 | 82.4782 | 82.6253 | 82.2859 | 82.4314 | -43.7237 | -43.5314 | -43.6815 | -43.4892
641.5312 | 121.6782 | -84.8282 | 37.2299 | -5.0471 | -27.9072 | -27.9003 | -27.8852 | -27.7153 | -27.7739 | -27.9072 | 32.3629 | 32.4469 | 32.4329 | 32.4322 | 88.9472 | 88.9201 | 88.5675 | 88.7997 | -5.0014 | -27.8614 | -27.8545 | -27.8394 | -27.6695 | -27.7281 | -27.8614 | 32.4087 | 32.4927 | 32.4787 | 32.478 | 88.993 | 88.9659 | 88.6133 | 88.8454 | -56.5843 | -56.2045 | -56.5143 | -56.1346
643.3125 | 121.7743 | -89.0854 | 32.2678 | -5.3905 | -28.6032 | -28.5962 | -28.5948 | -28.4753 | -28.5019 | -28.6168 | 32.1844 | 32.25 | 32.2681 | 32.2582 | 89.1349 | 89.1032 | 88.7506 | 88.9736 | -5.3448 | -28.5574 | -28.5504 | -28.5491 | -28.4295 | -28.4561 | -28.571 | 32.2301 | 32.2958 | 32.3139 | 32.304 | 89.1807 | 89.149 | 88.7964 | 89.0194 | -56.9505 | -56.5662 | -56.8668 | -56.4825
645.0781 | 121.7651 | -89.5111 | 31.8375 | -5.9262 | -30.2699 | -30.2628 | -30.2706 | -30.1233 | -30.173 | -30.2878 | 31.7448 | 31.8104 | 31.7874 | 31.8141 | 89.5744 | 89.5519 | 89.1947 | 89.4177 | -5.8804 | -30.2241 | -30.2171 | -30.2248 | -30.0776 | -30.1272 | -30.242 | 31.7906 | 31.8562 | 31.8331 | 31.8598 | 89.6202 | 89.5977 | 89.2405 | 89.4635 | -57.8296 | -57.4499 | -57.7871 | -57.4074
646.7969 | 121.6278 | -90.9256 | 30.5008 | -6.4481 | -31.7946 | -31.7738 | -31.7815 | -31.6341 | -31.693 | -31.8078 | 30.1744 | 30.2628 | 30.217 | 30.248 | 91.1447 | 91.1084 | 90.7605 | 90.988 | -6.4024 | -31.7488 | -31.728 | -31.7357 | -31.5883 | -31.6472 | -31.762 | 30.2202 | 30.3086 | 30.2628 | 30.2938 | 91.1905 | 91.1542 | 90.8063 | 91.0338 | -60.9703 | -60.5861 | -60.9277 | -60.5435
648.5156 | 121.7606 | -87.5702 | 33.8242 | -6.7091 | -31.9457 | -31.9478 | -31.9646 | -31.8217 | -31.8533 | -31.9543 | 31.4198 | 31.5174 | 31.4486 | 31.4523 | 89.8354 | 89.8632 | 89.5106 | 89.729 | -6.6633 | -31.8999 | -31.902 | -31.9188 | -31.776 | -31.8075 | -31.9085 | 31.4655 | 31.5632 | 31.4943 | 31.4981 | 89.8811 | 89.909 | 89.5564 | 89.7748 | -58.4156 | -58.0909 | -58.3868 | -58.0621
650.2969 | 121.7239 | -97.6044 | 23.7488 | -8.0048 | -36.552 | -36.563 | -36.598 | -36.4363 | -36.4683 | -36.5828 | 23.27 | 23.3717 | 23.3404 | 23.352 | 98.0395 | 98.0121 | 97.651 | 97.8873 | -7.959 | -36.5062 | -36.5172 | -36.5523 | -36.3906 | -36.4225 | -36.537 | 23.3158 | 23.4174 | 23.3862 | 23.3978 | 98.0852 | 98.0579 | 97.6968 | 97.9331 | -74.7694 | -74.381 | -74.699 | -74.3106
652.0625 | 121.6599 | -90.4449 | 30.9769 | -7.8766 | -34.7708 | -34.7773 | -34.8078 | -34.6463 | -34.6827 | -34.7882 | 30.6918 | 30.7619 | 30.771 | 30.7609 | 90.4488 | 90.6048 | 90.2432 | 90.3974 | -7.8308 | -34.7251 | -34.7316 | -34.7621 | -34.6006 | -34.6369 | -34.7424 | 30.7376 | 30.8076 | 30.8168 | 30.8067 | 90.4946 | 90.6506 | 90.2889 | 90.4432 | -59.7571 | -59.5514 | -59.6779 | -59.4722
653.8281 | 121.6278 | -91.8594 | 29.5807 | -9.0212 | -38.292 | -38.312 | -38.3424 | -38.1668 | -38.1943 | -38.3134 | 28.9657 | 29.0402 | 29.0267 | 29.0254 | 92.2069 | 92.3216 | 91.9738 | 92.1371 | -8.9754 | -38.2462 | -38.2662 | -38.2967 | -38.121 | -38.1485 | -38.2676 | 29.0115 | 29.086 | 29.0724 | 29.0712 | 92.2526 | 92.3674 | 92.0196 | 92.1829 | -63.2412 | -63.0081 | -63.1802 | -62.9471
655.5312 | 121.5546 | -92.926 | 28.5004 | -9.0303 | -37.1152 | -37.1078 | -37.12 | -36.9765 | -37.0177 | -37.1368 | 28.2011 | 28.271 | 28.2483 | 28.2058 | 92.9211 | 93.0816 | 92.6972 | 92.8651 | -8.9846 | -37.0694 | -37.0621 | -37.0742 | -36.9308 | -36.9719 | -37.091 | 28.2469 | 28.3168 | 28.2941 | 28.2516 | 92.9668 | 93.1273 | 92.743 | 92.9108 | -64.72 | -64.4961 | -64.6727 | -64.4488
657.2812 | 121.6827 | -43.5699 | 77.8702 | -2.9869 | -12.7879 | -12.7268 | -12.7303 | -12.663 | -12.7522 | -12.8129 | -8.436 | -8.3962 | 77.7899 | 77.728 | 43.4035 | 43.524 | 43.2414 | 43.3979 | -2.9411 | -12.7422 | -12.681 | -12.6846 | -12.6172 | -12.7064 | -12.7672 | -8.3903 | -8.3504 | 77.8357 | 77.7738 | 43.4493 | 43.5698 | 43.2872 | 43.4437 | -51.8396 | -51.6775 | 34.3864 | 34.5485
659.0469 | 121.6415 | -43.6798 | 77.7466 | -3.2066 | -13.0123 | -12.9649 | -12.973 | -12.901 | -12.9949 | -13.051 | -9.3288 | -9.6828 | 77.5656 | 77.4991 | 43.6324 | 43.7575 | 43.4749 | 43.6406 | -3.1609 | -12.9665 | -12.9191 | -12.9272 | -12.8553 | -12.9491 | -13.0052 | -9.2831 | -9.637 | 77.6114 | 77.5448 | 43.6782 | 43.8033 | 43.5207 | 43.6863 | -52.9613 | -52.8038 | 33.9331 | 34.0907
660.75 | 121.5729 | -43.4784 | 78.0304 | -3.6233 | -14.1158 | -14.0637 | -14.0718 | -13.9998 | -14.0937 | -14.1589 | -9.3243 | -9.6828 | 77.8128 | 77.7463 | 43.4081 | 43.5194 | 43.2369 | 43.4071 | -3.5775 | -14.07 | -14.018 | -14.0261 | -13.954 | -14.0479 | -14.1131 | -9.2785 | -9.637 | 77.8586 | 77.7921 | 43.4539 | 43.5652 | 43.2826 | 43.4528 | -52.7324 | -52.5611 | 34.4047 | 34.576
662.5156 | 121.6644 | -41.5924 | 79.834 | -3.5638 | -13.4839 | -13.4365 | -13.4492 | -13.3817 | -13.4756 | -13.5363 | -9.3563 | -9.8385 | 79.6762 | 79.6054 | 41.5448 | 41.6607 | 41.3735 | 41.5346 | -3.518 | -13.4382 | -13.3907 | -13.4034 | -13.336 | -13.4298 | -13.4905 | -9.3105 | -9.7927 | 79.722 | 79.6512 | 41.5906 | 41.7065 | 41.4192 | 41.5804 | -50.9011 | -50.7298 | 38.1314 | 38.3027
664.2969 | 121.7102 | -41.4276 | 79.9713 | -3.8293 | -13.9647 | -13.9218 | -13.9253 | -13.867 | -13.9655 | -14.0216 | -9.1686 | -9.3394 | 79.9967 | 79.926 | 41.2381 | 41.3403 | 41.0759 | 41.2187 | -3.7835 | -13.9189 | -13.876 | -13.8796 | -13.8212 | -13.9197 | -13.9758 | -9.1228 | -9.2936 | 80.0424 | 79.9717 | 41.2838 | 41.386 | 41.1216 | 41.2645 | -50.4067 | -50.2445 | 38.7586 | 38.9208
666 | 121.7239 | -42.2699 | 79.1336 | -4.4703 | -15.7367 | -15.7074 | -15.7247 | -15.6066 | -15.7144 | -15.775 | -7.296 | -7.1919 | 79.0535 | 78.9873 | 42.1674 | 42.2833 | 42.0053 | 42.1664 | -4.4245 | -15.6909 | -15.6617 | -15.6789 | -15.5608 | -15.6687 | -15.7292 | -7.2502 | -7.1462 | 79.0993 | 79.033 | 42.2132 | 42.3291 | 42.051 | 42.2122 | -49.4634 | -49.3013 | 36.8861 | 37.0483
667.7812 | 121.6599 | -37.7884 | 83.6517 | -3.4172 | -11.8997 | -11.8523 | -11.865 | -11.7749 | -11.8961 | -11.9568 | -9.306 | -9.6233 | 83.8378 | 83.7723 | 37.4016 | 37.4947 | 37.2392 | 37.3913 | -3.3715 | -11.8539 | -11.8065 | -11.8192 | -11.7291 | -11.8503 | -11.911 | -9.2602 | -9.5775 | 83.8836 | 83.8181 | 37.4473 | 37.5405 | 37.2849 | 37.4371 | -46.7075 | -46.5451 | 46.4363 | 46.5987
669.4688 | 121.6919 | -44.1376 | 77.2705 | -4.9831 | -16.6021 | -16.5728 | -16.5854 | -16.4856 | -16.5843 | -16.6403 | -5.9362 | -5.8183 | 76.7781 | 76.7527 | 44.4611 | 44.5678 | 44.2945 | 44.5287 | -4.9373 | -16.5563 | -16.527 | -16.5397 | -16.4398 | -16.5386 | -16.5945 | -5.8904 | -5.7725 | 76.8239 | 76.7985 | 44.5069 | 44.6136 | 44.3402 | 44.5745 | -50.3973 | -50.2307 | 32.317 | 32.4837
671.2344 | 121.6553 | -45.4102 | 76.0437 | -5.4272 | -17.6415 | -17.603 | -17.6202 | -17.5111 | -17.6099 | -17.6704 | -4.1277 | -4.0097 | 75.8442 | 75.8277 | 45.3722 | 45.4971 | 45.2101 | 45.4489 | -5.3814 | -17.5957 | -17.5572 | -17.5744 | -17.4653 | -17.5641 | -17.6246 | -4.0819 | -3.9639 | 75.8899 | 75.8735 | 45.4179 | 45.5429 | 45.2559 | 45.4947 | -49.4998 | -49.3378 | 30.472 | 30.634
672.9375 | 121.7422 | -42.2379 | 79.1565 | -4.9602 | -15.7504 | -15.7166 | -15.7293 | -15.657 | -15.7327 | -15.7887 | -3.8713 | -3.7487 | 79.6762 | 79.5917 | 41.5768 | 41.679 | 41.4101 | 41.5712 | -4.9144 | -15.7047 | -15.6708 | -15.6835 | -15.6112 | -15.687 | -15.743 | -3.8255 | -3.7029 | 79.722 | 79.6375 | 41.6226 | 41.7248 | 41.4559 | 41.617 | -45.4481 | -45.2814 | 38.0993 | 38.2661
674.7031 | 121.7239 | -42.7368 | 78.6438 | -5.3722 | -16.6891 | -16.6461 | -16.677 | -16.6 | -16.6759 | -16.7273 | -3.299 | -3.1901 | 78.5133 | 78.4423 | 42.7031 | 42.8327 | 42.5455 | 42.7112 | -5.3264 | -16.6433 | -16.6003 | -16.6312 | -16.5543 | -16.6301 | -16.6815 | -3.2532 | -3.1443 | 78.5591 | 78.4881 | 42.7489 | 42.8785 | 42.5913 | 42.757 | -46.002 | -45.8445 | 35.8102 | 35.9678
676.3906 | 121.7194 | -42.3294 | 79.0787 | -5.537 | -16.7761 | -16.7285 | -16.7548 | -16.6779 | -16.7446 | -16.8051 | -2.8457 | -2.7322 | 78.9162 | 78.859 | 42.3048 | 42.4253 | 42.138 | 42.3037 | -5.4913 | -16.7303 | -16.6827 | -16.7091 | -16.6321 | -16.6988 | -16.7593 | -2.7999 | -2.6864 | 78.962 | 78.9048 | 42.3505 | 42.471 | 42.1838 | 42.3495 | -45.1505 | -44.9837 | 36.6114 | 36.7781
678.1562 | 121.6461 | -42.2836 | 79.1977 | -5.5782 | -16.5701 | -16.5224 | -16.5442 | -16.4535 | -16.5157 | -16.5991 | -2.5527 | -2.4391 | 79.0581 | 78.9918 | 42.1766 | 42.2788 | 42.0053 | 42.1572 | -5.5325 | -16.5243 | -16.4767 | -16.4985 | -16.4078 | -16.4699 | -16.5533 | -2.5069 | -2.3934 | 79.1039 | 79.0376 | 42.2224 | 42.3245 | 42.051 | 42.203 | -44.7293 | -44.5579 | 36.8815 | 37.0528
679.9531 | 121.669 | -41.5466 | 79.9164 | -5.6423 | -16.3503 | -16.3072 | -16.3245 | -16.2384 | -16.3142 | -16.3793 | -2.8045 | -2.6818 | 79.6304 | 79.5734 | 41.5997 | 41.7157 | 41.433 | 41.5987 | -5.5966 | -16.3045 | -16.2615 | -16.2787 | -16.1926 | -16.2684 | -16.3336 | -2.7587 | -2.636 | 79.6762 | 79.6191 | 41.6455 | 41.7614 | 41.4787 | 41.6445 | -44.4042 | -44.2375 | 38.0307 | 38.1974
681.6562 | 121.7285 | -41.4642 | 79.9576 | -5.7156 | -16.2175 | -16.1836 | -16.1963 | -16.1148 | -16.186 | -16.2511 | -2.7312 | -2.6269 | 79.8501 | 79.8206 | 41.3983 | 41.5097 | 41.2315 | 41.3927 | -5.6698 | -16.1717 | -16.1378 | -16.1505 | -16.069 | -16.1402 | -16.2054 | -2.6855 | -2.5811 | 79.8959 | 79.8664 | 41.4441 | 41.5554 | 41.2773 | 41.4384 | -44.1295 | -43.9628 | 38.4519 | 38.6186
683.4219 | 121.6415 | -40.3427 | 81.1478 | -5.6927 | -15.8466 | -15.8036 | -15.83 | -15.744 | -15.8243 | -15.8849 | -2.5389 | -2.4208 | 80.9398 | 80.9242 | 40.3133 | 40.4155 | 40.1419 | 40.3031 | -5.6469 | -15.8008 | -15.7578 | -15.7842 | -15.6982 | -15.7785 | -15.8391 | -2.4932 | -2.375 | 80.9856 | 80.97 | 40.359 | 40.4613 | 40.1876 | 40.3488 | -42.8522 | -42.6808 | 40.6265 | 40.7979
685.1875 | 121.756 | -47.0764 | 74.2676 | -7.5286 | -20.2697 | -20.2403 | -20.2437 | -20.1205 | -20.2241 | -20.2937 | -1.8796 | -1.7569 | 74.2234 | 74.1655 | 47.2034 | 47.1773 | 46.8858 | 47.1154 | -7.4829 | -20.224 | -20.1945 | -20.1979 | -20.0747 | -20.1784 | -20.2479 | -1.8339 | -1.7111 | 74.2692 | 74.2113 | 47.2492 | 47.2231 | 46.9316 | 47.1612 | -49.0831 | -48.7655 | 27.02 | 27.3376
686.9531 | 121.6278 | -46.6095 | 74.8672 | -7.6706 | -20.256 | -20.2265 | -20.2299 | -20.1022 | -20.2058 | -20.2891 | -1.9804 | -1.8714 | 74.7408 | 74.7242 | 46.6449 | 46.6096 | 46.3181 | 46.5568 | -7.6248 | -20.2102 | -20.1808 | -20.1841 | -20.0564 | -20.1601 | -20.2433 | -1.9346 | -1.8256 | 74.7866 | 74.77 | 46.6907 | 46.6554 | 46.3639 | 46.6026 | -48.6252 | -48.2985 | 28.0959 | 28.4227
688.6719 | 121.6644 | -46.7056 | 74.762 | -7.7713 | -20.2239 | -20.1624 | -20.1796 | -20.0564 | -20.1555 | -20.2433 | -2.0216 | -1.908 | 74.3837 | 74.3716 | 47.002 | 46.9621 | 46.6707 | 46.9048 | -7.7255 | -20.1782 | -20.1167 | -20.1338 | -20.0106 | -20.1097 | -20.1975 | -1.9758 | -1.8622 | 74.4295 | 74.4174 | 47.0478 | 47.0079 | 46.7164 | 46.9506 | -49.0236 | -48.6922 | 27.3817 | 27.713
690.4375 | 121.6141 | -45.5795 | 75.8972 | -8.5908 | -21.8357 | -21.7833 | -21.7912 | -21.7045 | -21.8128 | -21.8823 | -1.9529 | -1.8301 | 75.6107 | 75.5988 | 45.775 | 45.7306 | 45.4436 | 45.6824 | -8.545 | -21.7899 | -21.7375 | -21.7454 | -21.6587 | -21.7671 | -21.8365 | -1.9071 | -1.7844 | 75.6564 | 75.6445 | 45.8208 | 45.7764 | 45.4894 | 45.7282 | -47.7279 | -47.3965 | 29.8356 | 30.167
692.1875 | 121.6003 | -44.1696 | 77.3254 | -8.2474 | -20.6452 | -20.5837 | -20.5916 | -20.505 | -20.6225 | -20.7011 | -3.0655 | -2.9565 | 77.0711 | 77.0595 | 44.3054 | 44.2794 | 43.9877 | 44.222 | -8.2017 | -20.5994 | -20.5379 | -20.5458 | -20.4593 | -20.5767 | -20.6553 | -3.0197 | -2.9108 | 77.1169 | 77.1053 | 44.3512 | 44.3252 | 44.0335 | 44.2678 | -47.3709 | -47.0532 | 32.7657 | 33.0834
693.8906 | 121.756 | -42.9199 | 78.5019 | -8.0094 | -19.6882 | -19.6267 | -19.6347 | -19.5482 | -19.6747 | -19.7443 | -3.2166 | -3.0985 | 78.3622 | 78.3462 | 43.0327 | 42.9975 | 42.7103 | 42.9492 | -7.9636 | -19.6424 | -19.581 | -19.5889 | -19.5025 | -19.629 | -19.6985 | -3.1708 | -3.0527 | 78.408 | 78.392 | 43.0785 | 43.0433 | 42.7561 | 42.995 | -46.2493 | -45.9269 | 35.3295 | 35.6519
695.6562 | 121.6187 | -41.2354 | 80.278 | -7.7804 | -18.745 | -18.679 | -18.6778 | -18.6098 | -18.7545 | -18.7966 | -2.9281 | -2.8192 | 80.221 | 80.1961 | 41.174 | 41.1388 | 40.8607 | 41.0951 | -7.7347 | -18.6992 | -18.6332 | -18.632 | -18.564 | -18.7087 | -18.7508 | -2.8823 | -2.7734 | 80.2668 | 80.2419 | 41.2197 | 41.1846 | 40.9065 | 41.1409 | -44.1021 | -43.7888 | 39.047 | 39.3603
697.4219 | 121.6873 | -38.4979 | 82.9834 | -7.373 | -17.4812 | -17.429 | -17.4233 | -17.3417 | -17.4954 | -17.5468 | -3.5004 | -3.3869 | 82.7574 | 82.7466 | 38.6239 | 38.598 | 38.3288 | 38.5496 | -7.3272 | -17.4355 | -17.3832 | -17.3775 | -17.2959 | -17.4496 | -17.501 | -3.4546 | -3.3412 | 82.8031 | 82.7924 | 38.6697 | 38.6438 | 38.3746 | 38.5954 | -42.1243 | -41.8293 | 44.1334 | 44.4285
699.1875 | 121.6827 | -35.5728 | 85.8948 | -6.732 | -15.723 | -15.6479 | -15.6468 | -15.57 | -15.7282 | -15.7796 | -2.8869 | -2.7688 | 85.4219 | 85.4025 | 35.9686 | 35.9381 | 35.6688 | 35.8943 | -6.6862 | -15.6772 | -15.6022 | -15.6011 | -15.5242 | -15.6824 | -15.7338 | -2.8411 | -2.723 | 85.4677 | 85.4483 | 36.0144 | 35.9839 | 35.7146 | 35.9401 | -38.8555 | -38.5557 | 49.4533 | 49.7531
700.9531 | 121.7056 | -33.7692 | 87.7075 | -6.4527 | -14.8072 | -14.7276 | -14.7357 | -14.6544 | -14.8171 | -14.8594 | -3.125 | -3.0115 | 87.354 | 87.3348 | 34.0412 | 34.0062 | 33.7413 | 33.9715 | -6.4069 | -14.7614 | -14.6819 | -14.6899 | -14.6086 | -14.7713 | -14.8136 | -3.0792 | -2.9657 | 87.3997 | 87.3806 | 34.0869 | 34.052 | 33.7871 | 34.0172 | -37.1662 | -36.8663 | 53.3128 | 53.6127
702.6562 | 121.6141 | -32.4783 | 89.0396 | -6.1734 | -13.9006 | -13.8211 | -13.82 | -13.7571 | -13.9197 | -13.9621 | -3.9766 | -3.8631 | 89.0479 | 89.0199 | 32.3564 | 32.3123 | 32.061 | 32.2867 | -6.1277 | -13.8548 | -13.7753 | -13.7742 | -13.7113 | -13.8739 | -13.9163 | -3.9308 | -3.8174 | 89.0937 | 89.0657 | 32.4022 | 32.3581 | 32.1068 | 32.3325 | -36.333 | -36.0376 | 56.6915 | 56.9869
704.4219 | 121.7285 | -32.4005 | 89.0533 | -6.5351 | -14.4088 | -14.3384 | -14.3374 | -14.2744 | -14.4233 | -14.4748 | -3.3356 | -3.2221 | 88.9151 | 88.8413 | 32.48 | 32.4405 | 32.1938 | 32.4149 | -6.4893 | -14.3631 | -14.2927 | -14.2916 | -14.2287 | -14.3776 | -14.429 | -3.2898 | -3.1763 | 88.9609 | 88.8871 | 32.5258 | 32.4863 | 32.2396 | 32.4606 | -35.8156 | -35.5294 | 56.4351 | 56.7214
706.125 | 121.6553 | -31.7322 | 89.7995 | -6.4252 | -13.9372 | -13.8669 | -13.8704 | -13.8075 | -13.9518 | -14.0078 | -3.473 | -3.3595 | 89.7072 | 89.6335 | 31.688 | 31.6531 | 31.4063 | 31.6274 | -6.3795 | -13.8915 | -13.8211 | -13.8246 | -13.7617 | -13.906 | -13.9621 | -3.4272 | -3.3137 | 89.753 | 89.6793 | 31.7338 | 31.6989 | 31.4521 | 31.6732 | -35.1609 | -34.8793 | 58.0192 | 58.3009
707.8906 | 121.6782 | -30.8716 | 90.5914 | -6.3428 | -13.4931 | -13.4273 | -13.4263 | -13.3588 | -13.5214 | -13.5638 | -3.3631 | -3.245 | 90.5267 | 90.444 | 30.8731 | 30.8336 | 30.5868 | 30.8125 | -6.2971 | -13.4473 | -13.3815 | -13.3805 | -13.3131 | -13.4756 | -13.518 | -3.3173 | -3.1992 | 90.5725 | 90.4898 | 30.9189 | 30.8794 | 30.6325 | 30.8583 | -34.2361 | -33.9498 | 59.6536 | 59.9399
709.6562 | 121.637 | -28.9444 | 92.5827 | -5.8667 | -12.3301 | -12.246 | -12.2679 | -12.1915 | -12.3539 | -12.4009 | -3.3448 | -3.2313 | 92.239 | 92.1657 | 29.1471 | 29.1123 | 28.8745 | 29.0911 | -5.8209 | -12.2843 | -12.2003 | -12.2221 | -12.1457 | -12.3081 | -12.3551 | -3.299 | -3.1855 | 92.2848 | 92.2115 | 29.1929 | 29.158 | 28.9202 | 29.1369 | -32.4919 | -32.2192 | 63.0919 | 63.3645
711.3594 | 121.6507 | -28.0014 | 93.4982 | -5.8117 | -11.9821 | -11.8935 | -11.9016 | -11.8435 | -12.0059 | -12.0392 | -3.386 | -3.2725 | 93.1821 | 93.109 | 28.2132 | 28.1829 | 27.9405 | 28.148 | -5.766 | -11.9363 | -11.8477 | -11.8559 | -11.7978 | -11.9602 | -11.9934 | -3.3402 | -3.2267 | 93.2279 | 93.1548 | 28.2589 | 28.2287 | 27.9862 | 28.1938 | -31.5991 | -31.3264 | 64.9689 | 65.2416
713.125 | 121.6232 | -27.1408 | 94.3726 | -5.5004 | -11.1808 | -11.106 | -11.1096 | -11.0424 | -11.2001 | -11.2426 | -3.3676 | -3.2358 | 94.3084 | 94.2309 | 27.0778 | 27.043 | 26.8142 | 27.0355 | -5.4546 | -11.135 | -11.0602 | -11.0638 | -10.9966 | -11.1544 | -11.1968 | -3.3219 | -3.1901 | 94.3541 | 94.2766 | 27.1235 | 27.0887 | 26.86 | 27.0813 | -30.4454 | -30.1818 | 67.2306 | 67.4942
714.9062 | 121.6827 | -25.8591 | 95.6131 | -4.9739 | -9.9674 | -9.888 | -9.8963 | -9.8247 | -9.9914 | -10.034 | -3.244 | -3.126 | 95.485 | 95.3985 | 25.9149 | 25.8847 | 25.6421 | 25.8498 | -4.9281 | -9.9216 | -9.8423 | -9.8505 | -9.7789 | -9.9457 | -9.9882 | -3.1983 | -3.0802 | 95.5308 | 95.4443 | 25.9607 | 25.9305 | 25.6879 | 25.8955 | -29.1589 | -28.8861 | 69.5701 | 69.8429
716.5938 | 121.7422 | -24.646 | 96.7987 | -4.5893 | -9.0562 | -8.9906 | -8.9943 | -8.9182 | -9.0575 | -9.1229 | -3.1341 | -3.0161 | 96.6891 | 96.6165 | 24.6925 | 24.6669 | 24.438 | 24.6549 | -4.5435 | -9.0104 | -8.9449 | -8.9485 | -8.8724 | -9.0117 | -9.0771 | -3.0884 | -2.9703 | 96.7348 | 96.6623 | 24.7383 | 24.7127 | 24.4838 | 24.7006 | -27.8267 | -27.5721 | 71.9965 | 72.2511
718.3438 | 121.669 | -25.1633 | 96.3364 | -4.9373 | -9.5324 | -9.476 | -9.475 | -9.3989 | -9.5473 | -9.6036 | -3.1158 | -3.0069 | 96.2908 | 96.209 | 25.1092 | 25.0698 | 24.8455 | 25.0669 | -4.8915 | -9.4866 | -9.4302 | -9.4293 | -9.3531 | -9.5016 | -9.5579 | -3.0701 | -2.9611 | 96.3365 | 96.2548 | 25.1549 | 25.1156 | 24.8913 | 25.1127 | -28.225 | -27.9613 | 71.1816 | 71.4453
720.0938 | 121.6049 | -24.614 | 96.936 | -5.0838 | -9.6881 | -9.6225 | -9.6307 | -9.5454 | -9.6984 | -9.7593 | -3.0472 | -2.9291 | 96.625 | 96.5478 | 24.7658 | 24.7356 | 24.5158 | 24.719 | -5.038 | -9.6423 | -9.5767 | -9.5849 | -9.4996 | -9.6527 | -9.7135 | -3.0014 | -2.8833 | 96.6707 | 96.5936 | 24.8116 | 24.7814 | 24.5616 | 24.7647 | -27.8129 | -27.563 | 71.8592 | 72.1091
721.7969 | 121.701 | -24.1013 | 97.3892 | -4.9052 | -9.2348 | -9.16 | -9.1774 | -9.083 | -9.2452 | -9.3015 | -2.8869 | -2.7642 | 96.9958 | 96.9142 | 24.3904 | 24.3602 | 24.1358 | 24.3481 | -4.8594 | -9.189 | -9.1143 | -9.1317 | -9.0373 | -9.1994 | -9.2557 | -2.8411 | -2.7185 | 97.0416 | 96.9599 | 24.4362 | 24.406 | 24.1816 | 24.3939 | -27.2773 | -27.0227 | 72.6054 | 72.86
723.5625 | 121.6827 | -29.1504 | 92.3767 | -6.7503 | -12.3026 | -12.2872 | -12.2542 | -12.1823 | -12.3493 | -12.3734 | -2.9327 | -2.8054 | 92.5411 | 92.4496 | 28.9228 | 28.8833 | 28.6959 | 28.8485 | -6.7045 | -12.2568 | -12.2415 | -12.2084 | -12.1365 | -12.3035 | -12.3276 | -2.8869 | -2.7597 | 92.5869 | 92.4954 | 28.9686 | 28.9291 | 28.7417 | 28.8943 | -31.8555 | -31.6286 | 63.6184 | 63.8452
725.25 | 121.7194 | -27.5665 | 93.8828 | -6.3474 | -11.5883 | -11.5043 | -11.5079 | -11.4132 | -11.5756 | -11.6501 | -2.8777 | -2.7596 | 93.6079 | 93.5852 | 27.7782 | 27.7526 | 27.5147 | 27.736 | -6.3016 | -11.5425 | -11.4585 | -11.4621 | -11.3674 | -11.5298 | -11.6043 | -2.832 | -2.7139 | 93.6537 | 93.631 | 27.824 | 27.7983 | 27.5605 | 27.7818 | -30.656 | -30.3924 | 65.8297 | 66.0932
727 | 121.6278 | -28.9124 | 92.6147 | -6.004 | -10.7275 | -10.6985 | -10.6609 | -10.5846 | -10.7515 | -10.7985 | -2.6717 | -2.5628 | 93.2874 | 93.2143 | 28.1765 | 28.1234 | 27.9313 | 28.1068 | -5.9583 | -10.6817 | -10.6527 | -10.6151 | -10.5388 | -10.7057 | -10.7528 | -2.6259 | -2.517 | 93.3332 | 93.2601 | 28.2223 | 28.1692 | 27.9771 | 28.1526 | -30.8482 | -30.603 | 65.1109 | 65.3561
728.7656 | 121.6873 | -24.0692 | 97.4304 | -5.0426 | -9.0516 | -8.9632 | -8.9668 | -8.8587 | -9.0163 | -9.1138 | -1.9849 | -1.8759 | 96.712 | 96.6852 | 24.6651 | 24.6395 | 24.4197 | 24.6228 | -4.9968 | -9.0059 | -8.9174 | -8.921 | -8.8129 | -8.9705 | -9.068 | -1.9392 | -1.8302 | 96.7577 | 96.731 | 24.7108 | 24.6853 | 24.4655 | 24.6686 | -26.65 | -26.4046 | 72.0469 | 72.2923
730.4688 | 121.7377 | -18.837 | 102.6627 | -3.2066 | -5.7595 | -5.6803 | -5.6749 | -5.5763 | -5.7335 | -5.8312 | -1.4538 | -1.3448 | 102.2791 | 102.2075 | 19.1026 | 19.0726 | 18.8661 | 19.0649 | -3.1609 | -5.7137 | -5.6345 | -5.6291 | -5.5305 | -5.6878 | -5.7854 | -1.4081 | -1.299 | 102.3249 | 102.2533 | 19.1484 | 19.1183 | 18.9119 | 19.1107 | -20.5564 | -20.3199 | 83.1766 | 83.413
732.25 | 121.6827 | -17.0975 | 104.4205 | -2.497 | -4.4957 | -4.4075 | -4.4066 | -4.3174 | -4.4608 | -4.5676 | -1.2524 | -1.1433 | 104.2799 | 104.2086 | 17.1111 | 17.0765 | 16.8791 | 17.0826 | -2.4512 | -4.4499 | -4.3617 | -4.3609 | -4.2716 | -4.415 | -4.5219 | -1.2066 | -1.0976 | 104.3256 | 104.2543 | 17.1569 | 17.1223 | 16.9249 | 17.1283 | -18.3635 | -18.1315 | 87.1688 | 87.4008
733.9531 | 121.6553 | -17.9626 | 103.5919 | -3.0006 | -5.2787 | -5.1721 | -5.1621 | -5.1048 | -5.207 | -5.3093 | -1.0555 | -0.94186 | 103.4054 | 103.3843 | 17.9809 | 17.9509 | 17.7536 | 17.9433 | -2.9548 | -5.2329 | -5.1263 | -5.1163 | -5.059 | -5.1613 | -5.2635 | -1.0097 | -0.89608 | 103.4512 | 103.4301 | 18.0267 | 17.9967 | 17.7993 | 17.989 | -19.0364 | -18.8091 | 85.4245 | 85.6519
735.7188 | 121.7102 | -24.7787 | 96.698 | -6.0178 | -9.9766 | -9.9293 | -9.8871 | -9.8201 | -9.9914 | -10.0431 | -0.62971 | -0.50687 | 96.7898 | 96.7173 | 24.6697 | 24.6303 | 24.47 | 24.6137 | -5.972 | -9.9308 | -9.8835 | -9.8413 | -9.7743 | -9.9457 | -9.9974 | -0.58393 | -0.46109 | 96.8356 | 96.763 | 24.7154 | 24.6761 | 24.5158 | 24.6594 | -25.2994 | -25.0998 | 72.1201 | 72.3197
737.4062 | 121.6507 | -23.2727 | 98.259 | -5.4958 | -9.1341 | -9.0731 | -9.063 | -8.9594 | -9.117 | -9.2053 | -0.56561 | -0.44277 | 97.8886 | 97.8666 | 23.5114 | 23.4767 | 23.2476 | 23.4554 | -5.4501 | -9.0883 | -9.0273 | -9.0172 | -8.9136 | -9.0712 | -9.1596 | -0.51983 | -0.39699 | 97.9344 | 97.9124 | 23.5571 | 23.5224 | 23.2934 | 23.5012 | -24.077 | -23.8132 | 74.3772 | 74.641
739.1719 | 121.701 | -18.7042 | 102.7954 | -3.3348 | -5.59 | -5.5155 | -5.4963 | -5.4024 | -5.5458 | -5.6572 | -0.54272 | -0.43361 | 102.6866 | 102.6654 | 18.7089 | 18.6788 | 18.4769 | 18.6804 | -3.2891 | -5.5443 | -5.4697 | -5.4505 | -5.3566 | -5.5001 | -5.6115 | -0.49694 | -0.38783 | 102.7324 | 102.7112 | 18.7546 | 18.7246 | 18.5227 | 18.7261 | -19.2516 | -19.0197 | 83.9777 | 84.2097
740.9375 | 121.7331 | -17.6147 | 103.8712 | -2.8724 | -4.7933 | -4.7234 | -4.7042 | -4.6012 | -4.74 | -4.8652 | -0.56103 | -0.44277 | 103.7167 | 103.6911 | 17.6834 | 17.6534 | 17.4514 | 17.6503 | -2.8266 | -4.7476 | -4.6776 | -4.6585 | -4.5554 | -4.6943 | -4.8194 | -0.51525 | -0.39699 | 103.7625 | 103.7369 | 17.7291 | 17.6991 | 17.4972 | 17.696 | -18.2444 | -18.0124 | 86.0334 | 86.2653
742.6406 | 121.7514 | -16.2506 | 105.2399 | -2.3367 | -3.9234 | -3.8397 | -3.8389 | -3.7268 | -3.8564 | -3.9954 | -0.63429 | -0.52061 | 104.8796 | 104.8588 | 16.5113 | 16.4814 | 16.2793 | 16.4828 | -2.291 | -3.8776 | -3.7939 | -3.7931 | -3.681 | -3.8106 | -3.9496 | -0.58851 | -0.47483 | 104.9254 | 104.9046 | 16.5571 | 16.5271 | 16.3251 | 16.5286 | -17.1456 | -16.9136 | 88.3683 | 88.6003
744.4062 | 121.6736 | -16.5894 | 104.9469 | -2.9045 | -4.743 | -4.6547 | -4.6356 | -4.5783 | -4.6714 | -4.792 | -0.59766 | -0.48398 | 104.6461 | 104.5703 | 16.7494 | 16.724 | 16.5265 | 16.7255 | -2.8587 | -4.6972 | -4.6089 | -4.5898 | -4.5325 | -4.6256 | -4.7462 | -0.55188 | -0.4382 | 104.6919 | 104.6161 | 16.7952 | 16.7698 | 16.5723 | 16.7712 | -17.3471 | -17.1242 | 87.8967 | 88.1196
746.1562 | 121.6736 | -14.7354 | 106.7825 | -3.2616 | -5.2192 | -5.1217 | -5.1163 | -5.0132 | -5.1521 | -5.2773 | -0.7167 | -0.60303 | 104.5546 | 104.4879 | 16.8593 | 16.8339 | 16.6456 | 16.8353 | -3.2158 | -5.1734 | -5.0759 | -5.0705 | -4.9674 | -5.1063 | -5.2315 | -0.67092 | -0.55725 | 104.6003 | 104.5337 | 16.9051 | 16.8797 | 16.6914 | 16.8811 | -17.576 | -17.3623 | 87.6953 | 87.909
747.8594 | 121.6461 | -13.3759 | 108.2291 | -1.7553 | -2.9298 | -2.8507 | -2.8271 | -2.7609 | -2.8354 | -2.9973 | -0.72586 | -0.61676 | 107.8418 | 107.7573 | 13.5584 | 13.5194 | 13.3537 | 13.5345 | -1.7095 | -2.884 | -2.805 | -2.7813 | -2.7151 | -2.7897 | -2.9516 | -0.68008 | -0.57099 | 107.8875 | 107.8031 | 13.6042 | 13.5651 | 13.3995 | 13.5803 | -14.2843 | -14.0796 | 94.2833 | 94.488
749.625 | 121.7331 | -12.204 | 109.2865 | -1.4394 | -2.4169 | -2.3379 | -2.3234 | -2.2527 | -2.3272 | -2.4891 | -0.70754 | -0.59387 | 109.0596 | 108.9799 | 12.3269 | 12.3062 | 12.1313 | 12.3121 | -1.3936 | -2.3712 | -2.2922 | -2.2776 | -2.2069 | -2.2815 | -2.4434 | -0.66177 | -0.54809 | 109.1054 | 109.0257 | 12.3727 | 12.3519 | 12.1771 | 12.3579 | -13.0344 | -12.8388 | 96.7327 | 96.9283
751.3906 | 121.6461 | -10.1578 | 111.4426 | -0.26273 | -0.69071 | -0.60264 | -0.59733 | -0.51767 | -0.58286 | -0.75402 | -0.79453 | -0.68087 | 111.2984 | 111.2236 | 10.0973 | 10.0721 | 9.9062 | 10.078 | -0.21696 | -0.64494 | -0.55686 | -0.55155 | -0.47189 | -0.53709 | -0.70825 | -0.74876 | -0.63509 | 111.3441 | 111.2694 | 10.1431 | 10.1179 | 9.952 | 10.1237 | -10.8919 | -10.7007 | 101.201 | 101.3922
753.1562 | 121.7056 | -10.3821 | 111.1267 | -0.46418 | -0.96544 | -0.89109 | -0.87662 | -0.80608 | -0.86214 | -1.0333 | -0.69381 | -0.58929 | 111.0145 | 110.9352 | 10.372 | 10.3559 | 10.1992 | 10.3664 | -0.41841 | -0.91967 | -0.84531 | -0.83084 | -0.7603 | -0.81637 | -0.98751 | -0.64803 | -0.54351 | 111.0603 | 110.9809 | 10.4178 | 10.4017 | 10.245 | 10.4122 | -11.0658 | -10.893 | 100.6425 | 100.8153
754.8906 | 121.5912 | -10.0937 | 111.4929 | -0.23069 | -0.64035 | -0.55685 | -0.55154 | -0.47647 | -0.53708 | -0.70366 | -0.70754 | -0.58929 | 111.3167 | 111.2374 | 10.0836 | 10.0538 | 9.9016 | 10.0734 | -0.18491 | -0.59457 | -0.51108 | -0.50577 | -0.43069 | -0.4913 | -0.65789 | -0.66177 | -0.54351 | 111.3624 | 111.2832 | 10.1294 | 10.0995 | 9.9474 | 10.1192 | -10.7911 | -10.6092 | 101.2331 | 101.4151
756.6562 | 121.7377 | -9.3384 | 112.1933 | 0.06691 | -0.24199 | -0.13562 | -0.13948 | -0.046138 | -0.1296 | -0.30536 | -0.76248 | -0.64424 | 112.0034 | 111.9197 | 9.3969 | 9.3671 | 9.2194 | 9.3775 | 0.11269 | -0.19621 | -0.089846 | -0.093703 | -0.000362 | -0.083825 | -0.25958 | -0.71671 | -0.59846 | 112.0492 | 111.9654 | 9.4426 | 9.4128 | 9.2652 | 9.4233 | -10.1593 | -9.9819 | 102.6065 | 102.784
758.4219 | 121.6599 | -8.4778 | 113.0905 | 0.6621 | 0.52267 | 0.6931 | 0.64802 | 0.77332 | 0.63957 | 0.46835 | -0.84032 | -0.72666 | 112.942 | 112.8675 | 8.4538 | 8.424 | 8.2717 | 8.4436 | 0.70788 | 0.56845 | 0.73888 | 0.6938 | 0.81909 | 0.68534 | 0.51413 | -0.79454 | -0.68088 | 112.9877 | 112.9133 | 8.4995 | 8.4697 | 8.3175 | 8.4893 | -9.2941 | -9.112 | 104.4882 | 104.6703
760.125 | 121.7239 | -8.107 | 113.4064 | 0.7903 | 0.69667 | 0.86251 | 0.81743 | 0.94728 | 0.8227 | 0.63774 | -0.85863 | -0.74955 | 113.2853 | 113.2018 | 8.1104 | 8.0898 | 7.9375 | 8.1094 | 0.83607 | 0.74245 | 0.90829 | 0.8632 | 0.99306 | 0.86848 | 0.68352 | -0.81286 | -0.70377 | 113.3311 | 113.2476 | 8.1562 | 8.1355 | 7.9833 | 8.1551 | -8.969 | -8.7961 | 105.1749 | 105.3478
761.8906 | 121.6827 | -7.8964 | 113.6993 | 0.78114 | 0.67378 | 0.8442 | 0.79911 | 0.92439 | 0.78608 | 0.61485 | -0.8449 | -0.73581 | 113.5051 | 113.4216 | 7.8952 | 7.8654 | 7.7177 | 7.885 | 0.82692 | 0.71955 | 0.88998 | 0.84489 | 0.97017 | 0.83185 | 0.66063 | -0.79912 | -0.69004 | 113.5509 | 113.4673 | 7.941 | 7.9112 | 7.7635 | 7.9308 | -8.7401 | -8.5626 | 105.6099 | 105.7874
763.6406 | 121.6049 | -7.6492 | 113.9465 | 1.2344 | 1.269 | 1.4257 | 1.3806 | 1.5104 | 1.395 | 1.2192 | -0.79453 | -0.68087 | 113.7935 | 113.7101 | 7.6022 | 7.5816 | 7.4339 | 7.592 | 1.2802 | 1.3148 | 1.4715 | 1.4264 | 1.5561 | 1.4408 | 1.2649 | -0.74876 | -0.63509 | 113.8393 | 113.7558 | 7.648 | 7.6274 | 7.4796 | 7.6378 | -8.3968 | -8.2284 | 106.1913 | 106.3597
765.3906 | 121.6095 | -7.2372 | 114.386 | 1.6007 | 1.7086 | 1.8744 | 1.8201 | 1.9682 | 1.8483 | 1.6678 | -0.77622 | -0.66255 | 114.2285 | 114.1496 | 7.1765 | 7.1375 | 6.9989 | 7.1662 | 1.6464 | 1.7544 | 1.9202 | 1.8659 | 2.0139 | 1.894 | 1.7136 | -0.73044 | -0.61677 | 114.2742 | 114.1954 | 7.2222 | 7.1833 | 7.0447 | 7.212 | -7.9527 | -7.7751 | 107.052 | 107.2295
767.0938 | 121.7056 | -7.0129 | 114.5416 | 1.6602 | 1.7544 | 1.9247 | 1.8796 | 2.0185 | 1.894 | 1.7182 | -0.75333 | -0.64424 | 114.4024 | 114.3328 | 6.9887 | 6.9544 | 6.8204 | 6.9877 | 1.706 | 1.8002 | 1.9705 | 1.9254 | 2.0643 | 1.9398 | 1.764 | -0.70755 | -0.59846 | 114.4482 | 114.3786 | 7.0345 | 7.0002 | 6.8661 | 7.0335 | -7.7421 | -7.5737 | 107.4137 | 107.5821
768.875 | 121.6324 | -6.4133 | 115.2054 | 2.0539 | 2.2397 | 2.4238 | 2.3787 | 2.5129 | 2.3748 | 2.2081 | -0.74875 | -0.6305 | 114.993 | 114.9052 | 6.4027 | 6.3822 | 6.2481 | 6.4017 | 2.0997 | 2.2855 | 2.4696 | 2.4245 | 2.5587 | 2.4206 | 2.2538 | -0.70297 | -0.58472 | 115.0388 | 114.951 | 6.4485 | 6.4279 | 6.2938 | 6.4475 | -7.1515 | -6.9968 | 108.5903 | 108.745
770.6406 | 121.701 | -6.0928 | 115.4617 | 2.292 | 2.519 | 2.6802 | 2.6442 | 2.7922 | 2.6586 | 2.4782 | -0.74417 | -0.62592 | 115.2952 | 115.2166 | 6.096 | 6.0754 | 5.9367 | 6.0995 | 2.3378 | 2.5648 | 2.726 | 2.69 | 2.838 | 2.7044 | 2.5239 | -0.69839 | -0.58014 | 115.341 | 115.2623 | 6.1418 | 6.1212 | 5.9825 | 6.1453 | -6.8402 | -6.6809 | 109.1992 | 109.3585
772.3906 | 121.6049 | -5.8914 | 115.7089 | 2.3103 | 2.5145 | 2.6802 | 2.6305 | 2.7876 | 2.6541 | 2.4827 | -0.72586 | -0.61676 | 115.5424 | 115.4592 | 5.8579 | 5.8328 | 5.6895 | 5.8569 | 2.3561 | 2.5602 | 2.726 | 2.6763 | 2.8334 | 2.6998 | 2.5285 | -0.68008 | -0.57099 | 115.5882 | 115.505 | 5.9037 | 5.8786 | 5.7353 | 5.9027 | -6.5838 | -6.4154 | 109.6845 | 109.8529
774.0938 | 121.6324 | -5.6076 | 116.011 | 2.7498 | 3.0319 | 3.193 | 3.157 | 3.3141 | 3.1806 | 2.9909 | -0.7167 | -0.59845 | 115.8125 | 115.7386 | 5.5878 | 5.5581 | 5.4331 | 5.5959 | 2.7956 | 3.0776 | 3.2388 | 3.2028 | 3.3599 | 3.2263 | 3.0367 | -0.67092 | -0.55267 | 115.8583 | 115.7843 | 5.6336 | 5.6039 | 5.4789 | 5.6417 | -6.3045 | -6.1498 | 110.2247 | 110.3794
775.8438 | 121.669 | -5.4016 | 116.1758 | 2.9513 | 3.2425 | 3.4174 | 3.3997 | 3.5476 | 3.4003 | 3.2153 | -0.71212 | -0.60303 | 116.0003 | 115.9126 | 5.4093 | 5.3796 | 5.2454 | 5.4037 | 2.9971 | 3.2883 | 3.4632 | 3.4455 | 3.5933 | 3.4461 | 3.261 | -0.66634 | -0.55725 | 116.046 | 115.9583 | 5.4551 | 5.4253 | 5.2912 | 5.4494 | -6.1214 | -5.9575 | 110.591 | 110.7549
777.5312 | 121.6507 | -5.2551 | 116.3361 | 3.5785 | 3.9614 | 4.1454 | 4.1551 | 4.2938 | 4.142 | 3.9432 | -0.69381 | -0.58471 | 116.1696 | 116.0866 | 5.2307 | 5.2102 | 5.0714 | 5.2343 | 3.6243 | 4.0071 | 4.1911 | 4.2009 | 4.3395 | 4.1878 | 3.989 | -0.64803 | -0.53893 | 116.2154 | 116.1323 | 5.2765 | 5.2559 | 5.1172 | 5.28 | -5.9245 | -5.7652 | 110.9389 | 111.0982
779.2969 | 121.5912 | -5.0262 | 116.5787 | 3.8532 | 4.259 | 4.443 | 4.4619 | 4.6096 | 4.4442 | 4.2316 | -0.66176 | -0.54808 | 116.4031 | 116.3247 | 5.0064 | 4.963 | 4.8425 | 4.987 | 3.899 | 4.3048 | 4.4888 | 4.5077 | 4.6554 | 4.49 | 4.2774 | -0.61598 | -0.50231 | 116.4489 | 116.3705 | 5.0522 | 5.0087 | 4.8883 | 5.0328 | -5.6682 | -5.5043 | 111.3967 | 111.5606
781.0625 | 121.6827 | -4.7836 | 116.7664 | 4.2836 | 4.7581 | 4.9604 | 4.9976 | 5.1361 | 4.9295 | 4.7169 | -0.63887 | -0.52061 | 116.6137 | 116.5399 | 4.7775 | 4.7569 | 4.6273 | 4.781 | 4.3294 | 4.8039 | 5.0061 | 5.0434 | 5.1819 | 4.9753 | 4.7627 | -0.59309 | -0.47483 | 116.6595 | 116.5857 | 4.8233 | 4.8027 | 4.6731 | 4.8268 | -5.4164 | -5.2662 | 111.8363 | 111.9864
782.8281 | 121.6553 | -4.541 | 117.0776 | 3.9997 | 4.4192 | 4.6078 | 4.6313 | 4.7745 | 4.5816 | 4.3873 | -0.64344 | -0.52519 | 116.8747 | 116.7826 | 4.5394 | 4.5097 | 4.3847 | 4.5384 | 4.0455 | 4.465 | 4.6536 | 4.6771 | 4.8202 | 4.6273 | 4.433 | -0.59767 | -0.47941 | 116.9205 | 116.8284 | 4.5852 | 4.5555 | 4.4304 | 4.5842 | -5.1829 | -5.0281 | 112.3353 | 112.49
784.6094 | 121.6782 | -4.5776 | 116.9907 | 3.8532 | 4.2132 | 4.4018 | 4.4299 | 4.5776 | 4.3938 | 4.1904 | -0.62513 | -0.51145 | 116.8564 | 116.7688 | 4.5532 | 4.528 | 4.403 | 4.5613 | 3.899 | 4.259 | 4.4475 | 4.4756 | 4.6234 | 4.4396 | 4.2362 | -0.57935 | -0.46567 | 116.9022 | 116.8146 | 4.5989 | 4.5738 | 4.4487 | 4.607 | -5.1783 | -5.0281 | 112.3032 | 112.4534
786.3125 | 121.7377 | -4.303 | 117.2607 | 3.6793 | 3.9843 | 4.1912 | 4.2055 | 4.3441 | 4.1558 | 3.9523 | -0.59308 | -0.48398 | 117.0945 | 117.007 | 4.3197 | 4.29 | 4.1603 | 4.3095 | 3.725 | 4.03 | 4.2369 | 4.2513 | 4.3899 | 4.2015 | 3.9981 | -0.5473 | -0.4382 | 117.1402 | 117.0527 | 4.3654 | 4.3358 | 4.2061 | 4.3552 | -4.9128 | -4.7534 | 112.7748 | 112.9341
788.0781 | 121.6003 | -4.0924 | 117.5629 | 3.867 | 4.2132 | 4.4155 | 4.4482 | 4.5684 | 4.3572 | 4.1675 | -0.57934 | -0.46566 | 117.3417 | 117.2588 | 4.0541 | 4.029 | 3.9085 | 4.0714 | 3.9127 | 4.259 | 4.4613 | 4.4939 | 4.6142 | 4.403 | 4.2133 | -0.53357 | -0.41989 | 117.3875 | 117.3046 | 4.0999 | 4.0748 | 3.9543 | 4.1172 | -4.6335 | -4.4879 | 113.2876 | 113.4332
789.7812 | 121.6736 | -3.7811 | 117.778 | 4.8513 | 5.3533 | 5.5876 | 5.6569 | 5.7496 | 5.511 | 5.3029 | -0.55645 | -0.44735 | 117.5981 | 117.5198 | 3.8023 | 3.7772 | 3.6567 | 3.8059 | 4.8971 | 5.3991 | 5.6334 | 5.7027 | 5.7953 | 5.5567 | 5.3487 | -0.51068 | -0.40157 | 117.6438 | 117.5656 | 3.8481 | 3.823 | 3.7025 | 3.8516 | -4.3588 | -4.2131 | 113.7957 | 113.9414
791.4844 | 121.5958 | -3.5019 | 118.1213 | 4.6545 | 5.1335 | 5.3587 | 5.4188 | 5.4978 | 5.2729 | 5.074 | -0.54272 | -0.42445 | 117.9506 | 117.8724 | 3.4452 | 3.4293 | 3.3042 | 3.4533 | 4.7002 | 5.1793 | 5.4045 | 5.4646 | 5.5435 | 5.3187 | 5.1198 | -0.49694 | -0.37868 | 117.9964 | 117.9182 | 3.491 | 3.4751 | 3.3499 | 3.4991 | -3.988 | -3.8469 | 114.5054 | 114.6464
793.25 | 121.6049 | -3.3646 | 118.2404 | 4.6911 | 5.1793 | 5.3953 | 5.4738 | 5.5435 | 5.3187 | 5.1152 | -0.53356 | -0.42445 | 118.0834 | 118.0052 | 3.3171 | 3.2965 | 3.1805 | 3.3297 | 4.7369 | 5.2251 | 5.4411 | 5.5195 | 5.5893 | 5.3645 | 5.161 | -0.48778 | -0.37868 | 118.1291 | 118.051 | 3.3628 | 3.3423 | 3.2263 | 3.3755 | -3.8506 | -3.7141 | 114.7663 | 114.9028
795.0156 | 121.701 | -3.1586 | 118.4418 | 5.2725 | 5.8478 | 6.105 | 6.1972 | 6.2486 | 5.9917 | 5.7882 | -0.52898 | -0.40614 | 118.2665 | 118.1838 | 3.1477 | 3.1226 | 3.0066 | 3.1512 | 5.3183 | 5.8936 | 6.1508 | 6.2429 | 6.2943 | 6.0375 | 5.834 | -0.48321 | -0.36036 | 118.3123 | 118.2295 | 3.1934 | 3.1683 | 3.0523 | 3.197 | -3.6766 | -3.5355 | 115.1188 | 115.2599
796.7812 | 121.6415 | -3.0808 | 118.5196 | 5.7121 | 6.379 | 6.659 | 6.7786 | 6.7979 | 6.5274 | 6.3147 | -0.50609 | -0.38324 | 118.3581 | 118.2708 | 3.0561 | 3.0127 | 2.915 | 3.0688 | 5.7578 | 6.4248 | 6.7048 | 6.8244 | 6.8437 | 6.5732 | 6.3605 | -0.46031 | -0.33747 | 118.4038 | 118.3165 | 3.1019 | 3.0585 | 2.9608 | 3.1146 | -3.5622 | -3.4211 | 115.302 | 115.4431
798.5312 | 121.7239 | -2.9984 | 118.5654 | 5.8265 | 6.5392 | 6.801 | 6.9297 | 6.9536 | 6.6785 | 6.4658 | -0.4832 | -0.36951 | 118.4359 | 118.3532 | 2.9691 | 2.944 | 2.8326 | 2.9818 | 5.8723 | 6.585 | 6.8467 | 6.9755 | 6.9993 | 6.7242 | 6.5115 | -0.43742 | -0.32373 | 118.4817 | 118.399 | 3.0149 | 2.9898 | 2.8784 | 3.0276 | -3.4523 | -3.3158 | 115.4668 | 115.6033
800.2969 | 121.6141 | -2.9572 | 118.6661 | 5.7807 | 6.498 | 6.7735 | 6.9206 | 6.9352 | 6.651 | 6.4246 | -0.46946 | -0.36035 | 118.4725 | 118.3898 | 2.9325 | 2.8982 | 2.7822 | 2.9314 | 5.8265 | 6.5438 | 6.8193 | 6.9663 | 6.981 | 6.6968 | 6.4703 | -0.42369 | -0.31457 | 118.5183 | 118.4356 | 2.9783 | 2.944 | 2.828 | 2.9772 | -3.4019 | -3.2517 | 115.54 | 115.6903
802 | 121.7331 | -2.7878 | 118.7531 | 6.0875 | 6.9055 | 7.2039 | 7.3647 | 7.361 | 7.0493 | 6.8274 | -0.47404 | -0.36035 | 118.6145 | 118.5364 | 2.7951 | 2.7609 | 2.654 | 2.7941 | 6.1333 | 6.9513 | 7.2497 | 7.4104 | 7.4068 | 7.0951 | 6.8732 | -0.42826 | -0.31457 | 118.6602 | 118.5821 | 2.8409 | 2.8067 | 2.6998 | 2.8399 | -3.2692 | -3.1281 | 115.8193 | 115.9604
803.7656 | 121.5866 | -2.7466 | 118.8858 | 6.7285 | 7.6565 | 7.9777 | 8.1705 | 8.1438 | 7.8276 | 7.5783 | -0.46488 | -0.35577 | 118.7335 | 118.6462 | 2.6715 | 2.6465 | 2.5304 | 2.6842 | 6.7742 | 7.7022 | 8.0234 | 8.2163 | 8.1896 | 7.8734 | 7.624 | -0.41911 | -0.30999 | 118.7793 | 118.692 | 2.7173 | 2.6922 | 2.5762 | 2.73 | -3.1364 | -2.9953 | 116.062 | 116.2031
805.5469 | 121.6919 | -2.623 | 118.895 | 6.5957 | 7.5283 | 7.854 | 8.0514 | 8.0202 | 7.6903 | 7.4363 | -0.46488 | -0.34661 | 118.7884 | 118.7058 | 2.6166 | 2.5915 | 2.4755 | 2.6384 | 6.6415 | 7.574 | 7.8998 | 8.0972 | 8.066 | 7.7361 | 7.4821 | -0.41911 | -0.30084 | 118.8342 | 118.7516 | 2.6624 | 2.6373 | 2.5212 | 2.6842 | -3.0815 | -2.9404 | 116.1718 | 116.313
807.3125 | 121.7239 | -2.5772 | 118.9774 | 6.6552 | 7.6107 | 7.9548 | 8.1796 | 8.1301 | 7.759 | 7.505 | -0.4603 | -0.33746 | 118.8479 | 118.7607 | 2.5662 | 2.5412 | 2.4251 | 2.5835 | 6.701 | 7.6565 | 8.0005 | 8.2254 | 8.1759 | 7.8047 | 7.5508 | -0.41453 | -0.29168 | 118.8937 | 118.8065 | 2.612 | 2.5869 | 2.4709 | 2.6293 | -3.0265 | -2.8854 | 116.2817 | 116.4228
809.0156 | 121.5912 | -2.4811 | 119.1147 | 6.8246 | 7.8167 | 8.1562 | 8.404 | 8.3361 | 7.9741 | 7.7248 | -0.45572 | -0.34203 | 118.9487 | 118.866 | 2.4655 | 2.4404 | 2.3198 | 2.4736 | 6.8704 | 7.8625 | 8.202 | 8.4498 | 8.3819 | 8.0199 | 7.7705 | -0.40995 | -0.29626 | 118.9944 | 118.9118 | 2.5113 | 2.4862 | 2.3656 | 2.5194 | -2.9212 | -2.7755 | 116.4832 | 116.6289
810.7812 | 121.6095 | -2.4033 | 119.2154 | 7.1085 | 8.1327 | 8.5042 | 8.7703 | 8.6978 | 8.2992 | 8.0452 | -0.44657 | -0.33288 | 119.0402 | 118.9485 | 2.3694 | 2.3397 | 2.2374 | 2.3821 | 7.1542 | 8.1784 | 8.55 | 8.816 | 8.7435 | 8.345 | 8.091 | -0.40079 | -0.2871 | 119.086 | 118.9942 | 2.4151 | 2.3855 | 2.2832 | 2.4278 | -2.8159 | -2.684 | 116.6709 | 116.8028
812.5469 | 121.6187 | -2.2202 | 119.4168 | 7.1497 | 8.183 | 8.5408 | 8.8069 | 8.7344 | 8.3358 | 8.0773 | -0.44657 | -0.33746 | 119.2325 | 119.1408 | 2.1679 | 2.152 | 2.0359 | 2.1852 | 7.1955 | 8.2288 | 8.5866 | 8.8527 | 8.7802 | 8.3816 | 8.1231 | -0.40079 | -0.29168 | 119.2783 | 119.1866 | 2.2137 | 2.1978 | 2.0817 | 2.231 | -2.6145 | -2.4825 | 117.0646 | 117.1966
814.3125 | 121.5912 | -2.1744 | 119.4305 | 9.9471 | 11.5576 | 12.0114 | 12.2041 | 11.9939 | 11.5865 | 11.3552 | -0.45115 | -0.33746 | 119.26 | 119.1683 | 2.1405 | 2.1108 | 2.0039 | 2.1531 | 9.9928 | 11.6034 | 12.0572 | 12.2499 | 12.0397 | 11.6323 | 11.401 | -0.40537 | -0.29168 | 119.3058 | 119.214 | 2.1862 | 2.1566 | 2.0497 | 2.1989 | -2.5916 | -2.455 | 117.1195 | 117.2561
816.0156 | 121.7239 | -2.1149 | 119.4626 | 10.3774 | 11.9972 | 12.5196 | 12.6528 | 12.4151 | 11.9985 | 11.7627 | -0.44657 | -0.3283 | 119.3012 | 119.2186 | 2.0855 | 2.065 | 1.949 | 2.1028 | 10.4232 | 12.043 | 12.5654 | 12.6986 | 12.4608 | 12.0443 | 11.8085 | -0.40079 | -0.28252 | 119.347 | 119.2644 | 2.1313 | 2.1108 | 1.9947 | 2.1486 | -2.5321 | -2.3955 | 117.2157 | 117.3522
817.7812 | 121.6187 | -2.1881 | 119.4031 | 10.5056 | 12.1071 | 12.6433 | 12.781 | 12.5112 | 12.0993 | 11.8817 | -0.45115 | -0.3283 | 119.2096 | 119.1225 | 2.1038 | 2.0742 | 2.0039 | 2.1486 | 10.5514 | 12.1529 | 12.689 | 12.8268 | 12.557 | 12.145 | 11.9275 | -0.40537 | -0.28252 | 119.2554 | 119.1682 | 2.1496 | 2.12 | 2.0497 | 2.1943 | -2.555 | -2.455 | 117.1058 | 117.2057
819.5 | 121.6324 | -2.2018 | 119.2291 | 12.2134 | 14.0714 | 14.667 | 14.7086 | 14.3744 | 13.9489 | 13.7451 | -0.45115 | -0.34203 | 118.999 | 118.9118 | 2.0855 | 2.0605 | 2.0588 | 2.2081 | 12.2591 | 14.1172 | 14.7128 | 14.7544 | 14.4202 | 13.9947 | 13.7908 | -0.40537 | -0.29626 | 119.0448 | 118.9576 | 2.1313 | 2.1062 | 2.1046 | 2.2539 | -2.5367 | -2.51 | 116.9135 | 116.9402
821.25 | 121.5225 | -2.2751 | 119.0918 | 12.1767 | 14.0393 | 14.5892 | 14.6536 | 14.3149 | 13.8848 | 13.7084 | -0.43741 | -0.32372 | 118.9212 | 118.834 | 2.1908 | 2.1658 | 2.1138 | 2.2539 | 12.2225 | 14.0851 | 14.6349 | 14.6994 | 14.3607 | 13.9306 | 13.7542 | -0.39164 | -0.27794 | 118.967 | 118.8798 | 2.2366 | 2.2115 | 2.1596 | 2.2996 | -2.6282 | -2.5512 | 116.7304 | 116.8074
823.0156 | 121.3394 | -1.9226 | 119.3436 | -0.88539 | -1.0936 | -1.0284 | -1.0781 | -0.9892 | -1.0224 | -1.1432 | -0.4191 | -0.30083 | -0.62687 | -0.63295 | 1.1745 | 1.1586 | 1.7429 | 1.883 | -0.83962 | -1.0479 | -0.98267 | -1.0323 | -0.94342 | -0.97661 | -1.0974 | -0.37332 | -0.25505 | -0.58109 | -0.58718 | 1.2202 | 1.2044 | 1.7887 | 1.9288 | -1.5936 | -2.162 | -1.8013 | -2.3698
824.7812 | 121.5546 | -1.7487 | 119.5908 | -0.88997 | -1.1761 | -1.088 | -1.1284 | -1.0579 | -1.0773 | -1.1844 | -0.41452 | -0.3054 | -1.1717 | -1.1504 | 1.1516 | 1.1357 | 1.6422 | 1.7732 | -0.8442 | -1.1303 | -1.0422 | -1.0827 | -1.0121 | -1.0316 | -1.1386 | -0.36874 | -0.25963 | -1.1259 | -1.1046 | 1.1974 | 1.1815 | 1.688 | 1.8189 | -1.5661 | -2.0567 | -2.3233 | -2.8139
826.5312 | 121.6049 | -1.767 | 119.6457 | -0.90371 | -1.1806 | -1.1109 | -1.1422 | -1.0716 | -1.1048 | -1.2118 | -0.4191 | -0.30083 | -1.1534 | -1.1412 | 1.1195 | 1.0945 | 1.633 | 1.7777 | -0.85793 | -1.1349 | -1.0651 | -1.0964 | -1.0258 | -1.059 | -1.1661 | -0.37332 | -0.25505 | -1.1076 | -1.0955 | 1.1653 | 1.1403 | 1.6788 | 1.8235 | -1.5386 | -2.0521 | -2.2729 | -2.7864
828.2969 | 121.6232 | -1.7853 | 119.6686 | -0.95407 | -1.2493 | -1.1566 | -1.1971 | -1.1357 | -1.1597 | -1.2622 | -0.40994 | -0.29625 | -1.1763 | -1.1595 | 1.1424 | 1.1128 | 1.6468 | 1.7777 | -0.90829 | -1.2036 | -1.1109 | -1.1513 | -1.0899 | -1.114 | -1.2164 | -0.36416 | -0.25047 | -1.1305 | -1.1138 | 1.1882 | 1.1586 | 1.6926 | 1.8235 | -1.5524 | -2.0567 | -2.3187 | -2.823
830.0156 | 121.5912 | -1.799 | 119.7006 | -0.96781 | -1.2493 | -1.1704 | -1.2017 | -1.1403 | -1.1689 | -1.2714 | -0.42825 | -0.30998 | -1.19 | -1.1687 | 1.1424 | 1.1265 | 1.6422 | 1.7823 | -0.92203 | -1.2036 | -1.1246 | -1.1559 | -1.0945 | -1.1231 | -1.2256 | -0.38248 | -0.26421 | -1.1442 | -1.1229 | 1.1882 | 1.1723 | 1.688 | 1.8281 | -1.5707 | -2.0705 | -2.3324 | -2.8322
831.7969 | 121.5729 | -1.8402 | 119.6594 | -0.98612 | -1.2768 | -1.1887 | -1.2246 | -1.1677 | -1.1964 | -1.3034 | -0.42825 | -0.32372 | -1.1992 | -1.1824 | 1.1653 | 1.1311 | 1.6788 | 1.8235 | -0.94034 | -1.231 | -1.1429 | -1.1788 | -1.122 | -1.1506 | -1.2576 | -0.38248 | -0.27794 | -1.1534 | -1.1367 | 1.2111 | 1.1769 | 1.7246 | 1.8693 | -1.5936 | -2.1071 | -2.3645 | -2.878
833.5 | 121.5958 | -1.8539 | 119.6777 | -0.84419 | -1.1028 | -1.033 | -1.0689 | -0.9892 | -1.0178 | -1.1203 | -0.43741 | -0.31914 | -1.1671 | -1.1458 | 1.1195 | 1.0945 | 1.6697 | 1.8144 | -0.79841 | -1.057 | -0.98725 | -1.0231 | -0.94342 | -0.97203 | -1.0745 | -0.39164 | -0.27336 | -1.1213 | -1.1 | 1.1653 | 1.1403 | 1.7155 | 1.8601 | -1.5569 | -2.1071 | -2.2866 | -2.8368
835.2656 | 121.6324 | -1.8265 | 119.7189 | -0.84419 | -1.1211 | -1.0376 | -1.0781 | -0.99835 | -1.0315 | -1.1294 | -0.43283 | -0.31914 | -1.1488 | -1.1321 | 1.1104 | 1.0808 | 1.6514 | 1.8006 | -0.79841 | -1.0753 | -0.99183 | -1.0323 | -0.95258 | -0.98577 | -1.0837 | -0.38706 | -0.27336 | -1.103 | -1.0863 | 1.1561 | 1.1265 | 1.6971 | 1.8464 | -1.5432 | -2.0842 | -2.2592 | -2.8002
837.0312 | 121.582 | -1.7899 | 119.8242 | -0.85335 | -1.1303 | -1.0468 | -1.0872 | -1.0167 | -1.0407 | -1.1523 | -0.4191 | -0.30998 | -1.0801 | -1.0542 | 1.0325 | 1.0029 | 1.601 | 1.7457 | -0.80757 | -1.0845 | -1.001 | -1.0415 | -0.97089 | -0.99493 | -1.1065 | -0.37332 | -0.26421 | -1.0343 | -1.0084 | 1.0783 | 1.0487 | 1.6468 | 1.7915 | -1.4516 | -2.0201 | -2.1127 | -2.6811
838.7969 | 121.55 | -1.7349 | 119.8608 | -0.83503 | -1.1211 | -1.0284 | -1.0643 | -1.0029 | -1.0224 | -1.1386 | -0.42368 | -0.31456 | -1.0435 | -1.0359 | 1.0142 | 0.98004 | 1.5598 | 1.7091 | -0.78926 | -1.0753 | -0.98267 | -1.0186 | -0.95716 | -0.97661 | -1.0928 | -0.3779 | -0.26878 | -0.99771 | -0.99013 | 1.06 | 1.0258 | 1.6056 | 1.7548 | -1.4379 | -1.9835 | -2.0577 | -2.6033
840.5625 | 121.7102 | -1.6891 | 119.8151 | -0.83961 | -1.1074 | -1.033 | -1.0643 | -0.99378 | -1.0224 | -1.1294 | -0.41452 | -0.30083 | -1.0664 | -1.0405 | 1.0188 | 0.98461 | 1.5461 | 1.6816 | -0.79383 | -1.0616 | -0.98725 | -1.0186 | -0.948 | -0.97661 | -1.0837 | -0.36874 | -0.25505 | -1.0206 | -0.99471 | 1.0646 | 1.0304 | 1.5918 | 1.7274 | -1.4333 | -1.9606 | -2.0852 | -2.6124
842.3281 | 121.6782 | -1.6067 | 119.9066 | -0.75262 | -1.0112 | -0.9323 | -0.96361 | -0.89306 | -0.91251 | -1.0196 | -0.40994 | -0.29625 | -0.97481 | -0.94891 | 0.91351 | 0.89305 | 1.4682 | 1.6175 | -0.70684 | -0.96545 | -0.88652 | -0.91783 | -0.84728 | -0.86673 | -0.97378 | -0.36416 | -0.25047 | -0.92904 | -0.90313 | 0.95929 | 0.93883 | 1.514 | 1.6633 | -1.3235 | -1.8782 | -1.8883 | -2.443
844.0938 | 121.6232 | -1.6251 | 119.9707 | -0.71142 | -0.97002 | -0.88651 | -0.91782 | -0.84728 | -0.86672 | -0.9692 | -0.40078 | -0.29167 | -0.96566 | -0.93517 | 0.90435 | 0.8839 | 1.4408 | 1.5855 | -0.66564 | -0.92424 | -0.84074 | -0.87205 | -0.8015 | -0.82095 | -0.92342 | -0.35501 | -0.24589 | -0.91988 | -0.88939 | 0.95013 | 0.92967 | 1.4865 | 1.6312 | -1.3051 | -1.8415 | -1.87 | -2.4064
845.8125 | 121.6965 | -1.5427 | 119.9799 | -0.68395 | -0.91507 | -0.84988 | -0.88119 | -0.81066 | -0.8301 | -0.92799 | -0.3962 | -0.28251 | -0.94734 | -0.92143 | 0.88604 | 0.86558 | 1.395 | 1.5351 | -0.63817 | -0.8693 | -0.80411 | -0.83542 | -0.76488 | -0.78432 | -0.88222 | -0.35043 | -0.23673 | -0.90157 | -0.87566 | 0.93182 | 0.91136 | 1.4407 | 1.5809 | -1.2822 | -1.7912 | -1.8334 | -2.3423
847.5781 | 121.5683 | -1.5747 | 120.0577 | -0.66105 | -0.90592 | -0.81783 | -0.85372 | -0.78319 | -0.80262 | -0.90968 | -0.39163 | -0.29167 | -0.8512 | -0.83443 | 0.79906 | 0.76945 | 1.3858 | 1.5305 | -0.61528 | -0.86014 | -0.77206 | -0.80795 | -0.73741 | -0.75685 | -0.8639 | -0.34585 | -0.24589 | -0.80542 | -0.78865 | 0.84483 | 0.81522 | 1.4316 | 1.5763 | -1.1907 | -1.7774 | -1.6503 | -2.237
849.3438 | 121.5546 | -1.4236 | 120.2179 | -0.67937 | -0.91965 | -0.83615 | -0.87204 | -0.79235 | -0.82552 | -0.92799 | -0.3962 | -0.28251 | -0.87867 | -0.84817 | 0.81279 | 0.79234 | 1.2302 | 1.3749 | -0.63359 | -0.87388 | -0.79037 | -0.82626 | -0.74657 | -0.77974 | -0.88222 | -0.35043 | -0.23673 | -0.83289 | -0.80239 | 0.85857 | 0.83811 | 1.2759 | 1.4206 | -1.209 | -1.6264 | -1.6915 | -2.1088
851.0469 | 121.701 | -1.2863 | 120.2545 | -0.64732 | -0.87387 | -0.8041 | -0.82625 | -0.7603 | -0.77973 | -0.89137 | -0.3962 | -0.28709 | -0.81 | -0.77948 | 0.74412 | 0.71909 | 1.1477 | 1.2787 | -0.60154 | -0.82809 | -0.75832 | -0.78048 | -0.71452 | -0.73396 | -0.84559 | -0.35043 | -0.24131 | -0.76422 | -0.73371 | 0.78989 | 0.76486 | 1.1935 | 1.3245 | -1.1403 | -1.5439 | -1.5541 | -1.9577
852.8125 | 121.6599 | -1.2726 | 120.3049 | -0.68395 | -0.9105 | -0.83157 | -0.86288 | -0.79692 | -0.82552 | -0.93715 | -0.39163 | -0.27335 | -0.82831 | -0.80238 | 0.75785 | 0.73282 | 1.1248 | 1.2604 | -0.63817 | -0.86472 | -0.78579 | -0.81711 | -0.75115 | -0.77974 | -0.89137 | -0.34585 | -0.22758 | -0.78253 | -0.7566 | 0.80363 | 0.7786 | 1.1706 | 1.3062 | -1.1495 | -1.5165 | -1.5862 | -1.9532
854.5781 | 121.6553 | -1.2589 | 120.3278 | -0.66105 | -0.8876 | -0.79952 | -0.83541 | -0.7603 | -0.78889 | -0.90052 | -0.3962 | -0.27793 | -0.79168 | -0.76575 | 0.72123 | 0.70535 | 1.1111 | 1.2329 | -0.61528 | -0.84183 | -0.75374 | -0.78963 | -0.71452 | -0.74311 | -0.85475 | -0.35043 | -0.23216 | -0.74591 | -0.71997 | 0.767 | 0.75113 | 1.1569 | 1.2787 | -1.1174 | -1.5073 | -1.5129 | -1.9028
856.2656 | 121.6278 | -1.2543 | 120.3598 | -0.61527 | -0.83266 | -0.74458 | -0.78963 | -0.70537 | -0.73395 | -0.83643 | -0.39163 | -0.28709 | -0.75964 | -0.74285 | 0.69834 | 0.68246 | 1.0791 | 1.2055 | -0.56949 | -0.78688 | -0.6988 | -0.74385 | -0.65959 | -0.68817 | -0.79065 | -0.34585 | -0.24131 | -0.71386 | -0.69708 | 0.74411 | 0.72824 | 1.1248 | 1.2512 | -1.09 | -1.4707 | -1.458 | -1.8387
858.0312 | 121.6507 | -1.2268 | 120.369 | -0.60611 | -0.80976 | -0.73084 | -0.77589 | -0.70079 | -0.72021 | -0.82727 | -0.38705 | -0.27793 | -0.78253 | -0.77033 | 0.72581 | 0.69162 | 1.0653 | 1.2009 | -0.56034 | -0.76399 | -0.68506 | -0.73011 | -0.65501 | -0.67444 | -0.7815 | -0.34127 | -0.23216 | -0.73675 | -0.72455 | 0.77158 | 0.73739 | 1.1111 | 1.2467 | -1.1129 | -1.4524 | -1.5083 | -1.8479
859.7969 | 121.7056 | -1.1856 | 120.3506 | -0.64274 | -0.85555 | -0.77663 | -0.81252 | -0.73741 | -0.75226 | -0.87305 | -0.38705 | -0.26877 | -0.79168 | -0.76117 | 0.72581 | 0.70077 | 1.0516 | 1.1826 | -0.59696 | -0.80977 | -0.73085 | -0.76674 | -0.69163 | -0.70649 | -0.82728 | -0.34127 | -0.223 | -0.74591 | -0.71539 | 0.77158 | 0.74655 | 1.0974 | 1.2284 | -1.1129 | -1.4386 | -1.5175 | -1.8433
861.5469 | 121.6919 | -1.1536 | 120.4102 | -0.60611 | -0.81434 | -0.73084 | -0.76673 | -0.68705 | -0.71106 | -0.82727 | -0.37789 | -0.26877 | -0.73674 | -0.7108 | 0.66171 | 0.64584 | 1.015 | 1.1551 | -0.56034 | -0.76856 | -0.68506 | -0.72096 | -0.64128 | -0.66528 | -0.7815 | -0.33211 | -0.223 | -0.69097 | -0.66502 | 0.70749 | 0.69161 | 1.0607 | 1.2009 | -1.0396 | -1.3929 | -1.3985 | -1.7517
863.2969 | 121.5912 | -1.181 | 120.4514 | -0.53744 | -0.7365 | -0.65758 | -0.69806 | -0.61381 | -0.62407 | -0.74486 | -0.38247 | -0.25961 | -0.7047 | -0.6879 | 0.63882 | 0.61379 | 1.0012 | 1.1414 | -0.49166 | -0.69072 | -0.61181 | -0.65228 | -0.56803 | -0.57829 | -0.69909 | -0.33669 | -0.21384 | -0.65892 | -0.64213 | 0.6846 | 0.65957 | 1.047 | 1.1871 | -1.0213 | -1.3837 | -1.3435 | -1.7059
865.0156 | 121.6278 | -1.1581 | 120.4651 | -0.54202 | -0.74108 | -0.66216 | -0.69348 | -0.62296 | -0.6378 | -0.75402 | -0.37331 | -0.25961 | -0.70012 | -0.6879 | 0.63424 | 0.60921 | 0.98292 | 1.1185 | -0.49624 | -0.6953 | -0.61638 | -0.6477 | -0.57718 | -0.59203 | -0.70825 | -0.32754 | -0.21384 | -0.65434 | -0.64213 | 0.68002 | 0.65499 | 1.0287 | 1.1643 | -1.0076 | -1.3562 | -1.3344 | -1.683
866.7812 | 121.5775 | -1.1673 | 120.4788 | -0.59696 | -0.8006 | -0.70795 | -0.74842 | -0.67332 | -0.69274 | -0.80896 | -0.38247 | -0.25961 | -0.72301 | -0.69706 | 0.65713 | 0.6321 | 0.97834 | 1.1139 | -0.55118 | -0.75483 | -0.66217 | -0.70264 | -0.62754 | -0.64697 | -0.76318 | -0.33669 | -0.21384 | -0.67723 | -0.65129 | 0.70291 | 0.67788 | 1.0241 | 1.1597 | -1.0396 | -1.3608 | -1.3801 | -1.7013
868.5469 | 121.6873 | -1.0666 | 120.5109 | -0.57864 | -0.77313 | -0.68963 | -0.73011 | -0.65043 | -0.66985 | -0.79065 | -0.37789 | -0.25961 | -0.67723 | -0.64211 | 0.60677 | 0.5909 | 0.91882 | 1.0452 | -0.53287 | -0.72735 | -0.64386 | -0.68433 | -0.60465 | -0.62407 | -0.74487 | -0.33211 | -0.21384 | -0.63145 | -0.59634 | 0.65255 | 0.63668 | 0.9646 | 1.091 | -0.98466 | -1.2967 | -1.284 | -1.596
870.2969 | 121.6003 | -1.0529 | 120.5612 | -0.56491 | -0.76855 | -0.68048 | -0.71637 | -0.6367 | -0.66069 | -0.77233 | -0.38247 | -0.27335 | -0.65891 | -0.6238 | 0.59304 | 0.57259 | 0.87762 | 1.0178 | -0.51913 | -0.72278 | -0.6347 | -0.67059 | -0.59092 | -0.61492 | -0.72656 | -0.33669 | -0.22758 | -0.61314 | -0.57802 | 0.63881 | 0.61836 | 0.92339 | 1.0635 | -0.97551 | -1.2601 | -1.252 | -1.5365
872 | 121.6141 | -1.0712 | 120.5795 | -0.59238 | -0.78687 | -0.69879 | -0.73011 | -0.65501 | -0.67901 | -0.7998 | -0.38247 | -0.26877 | -0.67265 | -0.63753 | 0.61135 | 0.5909 | 0.87762 | 1.0132 | -0.5466 | -0.74109 | -0.65301 | -0.68433 | -0.60923 | -0.63323 | -0.75403 | -0.33669 | -0.223 | -0.62687 | -0.59176 | 0.65713 | 0.63668 | 0.92339 | 1.059 | -0.99382 | -1.2601 | -1.284 | -1.5503
873.7656 | 121.7056 | -0.96588 | 120.6024 | -0.56491 | -0.76397 | -0.68505 | -0.70721 | -0.62754 | -0.65154 | -0.76318 | -0.39163 | -0.26877 | -0.64518 | -0.61464 | 0.58388 | 0.55428 | 0.82725 | 0.9674 | -0.51913 | -0.7182 | -0.63928 | -0.66144 | -0.58176 | -0.60576 | -0.7174 | -0.34585 | -0.223 | -0.5994 | -0.56886 | 0.62966 | 0.60005 | 0.87303 | 1.0132 | -0.97551 | -1.2189 | -1.2291 | -1.4724
875.4844 | 121.6461 | -0.94299 | 120.6757 | -0.55117 | -0.74108 | -0.66216 | -0.70263 | -0.61381 | -0.6378 | -0.74944 | -0.38705 | -0.26877 | -0.63602 | -0.61006 | 0.58846 | 0.55885 | 0.78147 | 0.92162 | -0.5054 | -0.6953 | -0.61638 | -0.65686 | -0.56803 | -0.59203 | -0.70367 | -0.34127 | -0.223 | -0.59025 | -0.56428 | 0.63424 | 0.60463 | 0.82725 | 0.9674 | -0.97551 | -1.1685 | -1.2245 | -1.4175
877.25 | 121.669 | -0.91095 | 120.6757 | -0.53286 | -0.72734 | -0.63469 | -0.67058 | -0.60007 | -0.61949 | -0.73113 | -0.39163 | -0.27335 | -0.60397 | -0.57801 | 0.56099 | 0.53138 | 0.75858 | 0.88957 | -0.48708 | -0.68157 | -0.58891 | -0.62481 | -0.55429 | -0.57371 | -0.68535 | -0.34585 | -0.22758 | -0.5582 | -0.53223 | 0.60677 | 0.57716 | 0.80435 | 0.93535 | -0.95262 | -1.1502 | -1.165 | -1.3626
879.0312 | 121.6003 | -0.89722 | 120.7031 | -0.50997 | -0.69987 | -0.60722 | -0.65227 | -0.56803 | -0.60118 | -0.70366 | -0.38705 | -0.26877 | -0.60397 | -0.56885 | 0.55641 | 0.53596 | 0.72653 | 0.8621 | -0.46419 | -0.65409 | -0.56144 | -0.6065 | -0.52225 | -0.5554 | -0.65789 | -0.34127 | -0.223 | -0.5582 | -0.52307 | 0.60219 | 0.58174 | 0.7723 | 0.90788 | -0.94346 | -1.1136 | -1.1604 | -1.3305
880.8125 | 121.6324 | -0.89722 | 120.7214 | -0.5237 | -0.69987 | -0.62553 | -0.66143 | -0.57718 | -0.5966 | -0.71282 | -0.3962 | -0.27335 | -0.58108 | -0.55053 | 0.52437 | 0.49476 | 0.73569 | 0.86668 | -0.47793 | -0.65409 | -0.57976 | -0.61565 | -0.53141 | -0.55082 | -0.66704 | -0.35043 | -0.22758 | -0.53531 | -0.50476 | 0.57014 | 0.54054 | 0.78146 | 0.91246 | -0.92057 | -1.1319 | -1.1054 | -1.3168
882.5156 | 121.7239 | -0.82398 | 120.694 | -0.50081 | -0.69071 | -0.61638 | -0.64311 | -0.56345 | -0.58286 | -0.68535 | -0.38705 | -0.26419 | -0.57193 | -0.54595 | 0.51063 | 0.48561 | 0.71737 | 0.84837 | -0.45503 | -0.64494 | -0.5706 | -0.59734 | -0.51767 | -0.53709 | -0.63957 | -0.34127 | -0.21842 | -0.52615 | -0.50018 | 0.55641 | 0.53138 | 0.76315 | 0.89414 | -0.89768 | -1.1044 | -1.0826 | -1.2893
884.2812 | 121.6141 | -0.87433 | 120.726 | -0.51455 | -0.69529 | -0.63011 | -0.65227 | -0.57718 | -0.5966 | -0.70366 | -0.37789 | -0.25961 | -0.5765 | -0.55053 | 0.51521 | 0.49018 | 0.70364 | 0.84379 | -0.46877 | -0.64952 | -0.58433 | -0.6065 | -0.53141 | -0.55082 | -0.65789 | -0.33211 | -0.21384 | -0.53073 | -0.50476 | 0.56099 | 0.53596 | 0.74941 | 0.88957 | -0.8931 | -1.0815 | -1.0917 | -1.2801
886.0469 | 121.6736 | -0.84228 | 120.7443 | -0.52828 | -0.69987 | -0.63011 | -0.65685 | -0.5726 | -0.59202 | -0.70366 | -0.37331 | -0.26419 | -0.55819 | -0.53221 | 0.4969 | 0.46271 | 0.6899 | 0.82548 | -0.4825 | -0.65409 | -0.58433 | -0.61107 | -0.52683 | -0.54624 | -0.65789 | -0.32754 | -0.21842 | -0.51241 | -0.48644 | 0.54267 | 0.50849 | 0.73568 | 0.87125 | -0.87021 | -1.0632 | -1.0551 | -1.2481
887.75 | 121.6827 | -0.81482 | 120.7352 | -0.49623 | -0.66782 | -0.60264 | -0.63396 | -0.55429 | -0.56913 | -0.68077 | -0.38247 | -0.26419 | -0.52156 | -0.50016 | 0.45569 | 0.43525 | 0.68532 | 0.81174 | -0.45045 | -0.62204 | -0.55686 | -0.58818 | -0.50852 | -0.52335 | -0.63499 | -0.33669 | -0.21842 | -0.47579 | -0.45439 | 0.50147 | 0.48102 | 0.7311 | 0.85752 | -0.83816 | -1.0678 | -0.97726 | -1.2069
889.5 | 121.6278 | -0.80566 | 120.8221 | -0.49623 | -0.63577 | -0.56601 | -0.60191 | -0.52225 | -0.53708 | -0.64872 | -0.38247 | -0.26419 | -0.51241 | -0.49558 | 0.46027 | 0.43067 | 0.65785 | 0.79343 | -0.45045 | -0.58999 | -0.52024 | -0.55613 | -0.47647 | -0.4913 | -0.60295 | -0.33669 | -0.21842 | -0.46663 | -0.44981 | 0.50605 | 0.47644 | 0.70363 | 0.83921 | -0.84274 | -1.0403 | -0.97268 | -1.1703
891.2812 | 121.582 | -0.82398 | 120.8176 | -0.48707 | -0.63577 | -0.57517 | -0.60191 | -0.51767 | -0.53708 | -0.64872 | -0.37789 | -0.26419 | -0.52156 | -0.49558 | 0.45111 | 0.42609 | 0.64412 | 0.77512 | -0.4413 | -0.58999 | -0.52939 | -0.55613 | -0.47189 | -0.4913 | -0.60295 | -0.33211 | -0.21842 | -0.47579 | -0.44981 | 0.49689 | 0.47187 | 0.68989 | 0.82089 | -0.82901 | -1.022 | -0.97268 | -1.1657
893.0469 | 121.7239 | -0.76446 | 120.8038 | -0.4825 | -0.61745 | -0.54312 | -0.58359 | -0.50393 | -0.52334 | -0.63957 | -0.37331 | -0.25504 | -0.51241 | -0.491 | 0.44196 | 0.42151 | 0.63496 | 0.75223 | -0.43672 | -0.57168 | -0.49734 | -0.53782 | -0.45816 | -0.47757 | -0.59379 | -0.32754 | -0.20926 | -0.46663 | -0.44523 | 0.48773 | 0.46729 | 0.68074 | 0.798 | -0.81527 | -1.0083 | -0.95437 | -1.1474
894.7656 | 121.7422 | -0.75531 | 120.8176 | -0.49165 | -0.62661 | -0.53854 | -0.58359 | -0.50393 | -0.5325 | -0.64872 | -0.37331 | -0.25961 | -0.53988 | -0.50932 | 0.47401 | 0.43525 | 0.60749 | 0.74307 | -0.44588 | -0.58083 | -0.49276 | -0.53782 | -0.45816 | -0.48672 | -0.60295 | -0.32754 | -0.21384 | -0.4941 | -0.46354 | 0.51978 | 0.48102 | 0.65327 | 0.78885 | -0.84732 | -0.9808 | -1.0139 | -1.1474
896.5156 | 121.7377 | -0.73242 | 120.8359 | -0.47792 | -0.60829 | -0.53396 | -0.57444 | -0.48562 | -0.52334 | -0.63041 | -0.37789 | -0.25504 | -0.52614 | -0.50474 | 0.46027 | 0.43067 | 0.59376 | 0.72476 | -0.43214 | -0.56252 | -0.48818 | -0.52866 | -0.43985 | -0.47757 | -0.58464 | -0.33211 | -0.20926 | -0.48037 | -0.45897 | 0.50605 | 0.47644 | 0.63953 | 0.77053 | -0.83816 | -0.97165 | -0.98641 | -1.1199
898.2812 | 121.7148 | -0.71411 | 120.8359 | -0.4825 | -0.61287 | -0.54312 | -0.58817 | -0.49936 | -0.52334 | -0.63957 | -0.37789 | -0.26419 | -0.53988 | -0.50932 | 0.46943 | 0.4444 | 0.60749 | 0.73849 | -0.43672 | -0.5671 | -0.49734 | -0.5424 | -0.45358 | -0.47757 | -0.59379 | -0.33211 | -0.21842 | -0.4941 | -0.46354 | 0.5152 | 0.49018 | 0.65327 | 0.78427 | -0.84732 | -0.98538 | -1.0093 | -1.1474
899.9844 | 121.6415 | -0.7782 | 120.8221 | -0.4825 | -0.61745 | -0.53396 | -0.58817 | -0.50851 | -0.52792 | -0.63499 | -0.36873 | -0.25961 | -0.54446 | -0.51848 | 0.47858 | 0.44898 | 0.59376 | 0.72934 | -0.43672 | -0.57168 | -0.48818 | -0.5424 | -0.46274 | -0.48214 | -0.58921 | -0.32296 | -0.21384 | -0.49868 | -0.4727 | 0.52436 | 0.49476 | 0.63953 | 0.77511 | -0.84732 | -0.96249 | -1.023 | -1.1382
901.7656 | 121.6599 | -0.74158 | 120.8405 | -0.47334 | -0.59914 | -0.52938 | -0.56528 | -0.4902 | -0.51419 | -0.61668 | -0.37331 | -0.25504 | -0.5353 | -0.49558 | 0.45569 | 0.43067 | 0.5846 | 0.71102 | -0.42756 | -0.55336 | -0.48361 | -0.5195 | -0.44442 | -0.46841 | -0.5709 | -0.32754 | -0.20926 | -0.48952 | -0.44981 | 0.50147 | 0.47644 | 0.63037 | 0.7568 | -0.829 | -0.95791 | -0.99099 | -1.1199
903.5156 | 121.6919 | -0.73242 | 120.8405 | -0.46876 | -0.60372 | -0.52938 | -0.57901 | -0.49936 | -0.51419 | -0.62583 | -0.37331 | -0.25046 | -0.52156 | -0.50016 | 0.45111 | 0.42609 | 0.57544 | 0.70644 | -0.42298 | -0.55794 | -0.48361 | -0.53324 | -0.45358 | -0.46841 | -0.58006 | -0.32754 | -0.20468 | -0.47579 | -0.45439 | 0.49689 | 0.47187 | 0.62122 | 0.75222 | -0.82443 | -0.94875 | -0.97268 | -1.097
905.2188 | 121.6049 | -0.74158 | 120.8771 | -0.46418 | -0.60372 | -0.5248 | -0.5607 | -0.48105 | -0.50503 | -0.61668 | -0.36416 | -0.25504 | -0.51241 | -0.48185 | 0.43738 | 0.41236 | 0.58002 | 0.71102 | -0.41841 | -0.55794 | -0.47903 | -0.51492 | -0.43527 | -0.45925 | -0.5709 | -0.31838 | -0.20926 | -0.46663 | -0.43607 | 0.48316 | 0.45813 | 0.62579 | 0.7568 | -0.80153 | -0.94417 | -0.94979 | -1.0924
906.9844 | 121.5958 | -0.75989 | 120.8862 | -0.44129 | -0.57624 | -0.49733 | -0.53781 | -0.45815 | -0.48672 | -0.59379 | -0.36873 | -0.25504 | -0.50325 | -0.47269 | 0.41907 | 0.39404 | 0.57544 | 0.69729 | -0.39552 | -0.53047 | -0.45156 | -0.49203 | -0.41238 | -0.44094 | -0.54801 | -0.32296 | -0.20926 | -0.45748 | -0.42691 | 0.46484 | 0.43982 | 0.62122 | 0.74307 | -0.7878 | -0.94417 | -0.92232 | -1.0787
908.7656 | 121.6965 | -0.70953 | 120.8313 | -0.44129 | -0.57166 | -0.49733 | -0.53781 | -0.44442 | -0.48672 | -0.59379 | -0.37331 | -0.25046 | -0.48036 | -0.44979 | 0.40075 | 0.37115 | 0.57544 | 0.70644 | -0.39552 | -0.52589 | -0.45156 | -0.49203 | -0.39865 | -0.44094 | -0.54801 | -0.32754 | -0.20468 | -0.43458 | -0.40402 | 0.44653 | 0.41693 | 0.62122 | 0.75222 | -0.77407 | -0.94875 | -0.88112 | -1.0558
910.4844 | 121.7102 | -0.70953 | 120.8817 | -0.4596 | -0.57624 | -0.50649 | -0.55154 | -0.46273 | -0.49587 | -0.60294 | -0.37789 | -0.25961 | -0.48036 | -0.44521 | 0.39618 | 0.37573 | 0.56171 | 0.69729 | -0.41383 | -0.53047 | -0.46071 | -0.50577 | -0.41696 | -0.4501 | -0.55717 | -0.33211 | -0.21384 | -0.43458 | -0.39944 | 0.44195 | 0.42151 | 0.60748 | 0.74307 | -0.77407 | -0.9396 | -0.87654 | -1.0421
912.2344 | 121.7377 | -0.70038 | 120.845 | -0.44129 | -0.57624 | -0.50191 | -0.55154 | -0.46273 | -0.48214 | -0.59836 | -0.37789 | -0.26419 | -0.45747 | -0.43148 | 0.38244 | 0.362 | 0.56628 | 0.69271 | -0.39552 | -0.53047 | -0.45613 | -0.50577 | -0.41696 | -0.43636 | -0.55259 | -0.33211 | -0.21842 | -0.41169 | -0.3857 | 0.42822 | 0.40777 | 0.61206 | 0.73849 | -0.76033 | -0.94417 | -0.83991 | -1.0238
914 | 121.7377 | -0.69122 | 120.8588 | -0.44129 | -0.58082 | -0.49275 | -0.54239 | -0.449 | -0.48672 | -0.59836 | -0.38247 | -0.25961 | -0.46205 | -0.43148 | 0.37329 | 0.35742 | 0.56171 | 0.68355 | -0.39552 | -0.53504 | -0.44698 | -0.49661 | -0.40322 | -0.44094 | -0.55259 | -0.33669 | -0.21384 | -0.41627 | -0.3857 | 0.41906 | 0.40319 | 0.60748 | 0.72933 | -0.75575 | -0.94417 | -0.83533 | -1.0238
915.7031 | 121.7239 | -0.69122 | 120.8771 | -0.44129 | -0.56708 | -0.48817 | -0.53323 | -0.45358 | -0.48214 | -0.58463 | -0.37331 | -0.25504 | -0.46205 | -0.43148 | 0.37786 | 0.362 | 0.56628 | 0.67898 | -0.39552 | -0.52131 | -0.4424 | -0.48745 | -0.4078 | -0.43636 | -0.53885 | -0.32754 | -0.20926 | -0.41627 | -0.3857 | 0.42364 | 0.40777 | 0.61206 | 0.72475 | -0.75118 | -0.9396 | -0.83991 | -1.0283
917.4531 | 121.5912 | -0.70953 | 120.9229 | -0.43671 | -0.56251 | -0.47902 | -0.52865 | -0.44442 | -0.47756 | -0.58463 | -0.37331 | -0.25504 | -0.44373 | -0.42232 | 0.36871 | 0.34369 | 0.52966 | 0.66524 | -0.39094 | -0.51673 | -0.43324 | -0.48287 | -0.39865 | -0.43178 | -0.53885 | -0.32754 | -0.20926 | -0.39796 | -0.37654 | 0.41448 | 0.38946 | 0.57543 | 0.71102 | -0.74202 | -0.90297 | -0.81244 | -0.97339
919.2188 | 121.7422 | -0.68207 | 120.845 | -0.44587 | -0.57624 | -0.48817 | -0.54239 | -0.46273 | -0.49129 | -0.59379 | -0.37331 | -0.25504 | -0.44831 | -0.41774 | 0.37786 | 0.34369 | 0.54339 | 0.67898 | -0.40009 | -0.53047 | -0.4424 | -0.49661 | -0.41696 | -0.44552 | -0.54801 | -0.32754 | -0.20926 | -0.40254 | -0.37196 | 0.42364 | 0.38946 | 0.58917 | 0.72475 | -0.75118 | -0.9167 | -0.82618 | -0.99171
920.9375 | 121.6461 | -0.68665 | 120.9274 | -0.43213 | -0.55793 | -0.4836 | -0.53781 | -0.45358 | -0.46382 | -0.58005 | -0.37331 | -0.25046 | -0.45289 | -0.4269 | 0.37786 | 0.34826 | 0.52966 | 0.65151 | -0.38636 | -0.51215 | -0.43782 | -0.49203 | -0.4078 | -0.41805 | -0.53427 | -0.32754 | -0.20468 | -0.40712 | -0.38112 | 0.42364 | 0.39404 | 0.57543 | 0.69728 | -0.75118 | -0.90297 | -0.83075 | -0.98255
922.7031 | 121.5912 | -0.6958 | 120.9732 | -0.42298 | -0.55793 | -0.46986 | -0.51949 | -0.43984 | -0.45925 | -0.57547 | -0.37789 | -0.25961 | -0.44831 | -0.41774 | 0.37329 | 0.34369 | 0.51592 | 0.64693 | -0.3772 | -0.51215 | -0.42408 | -0.47372 | -0.39407 | -0.41347 | -0.5297 | -0.33211 | -0.21384 | -0.40254 | -0.37196 | 0.41906 | 0.38946 | 0.5617 | 0.69271 | -0.75118 | -0.89381 | -0.8216 | -0.96423
924.3906 | 121.5912 | -0.68665 | 120.9641 | -0.40924 | -0.54419 | -0.46528 | -0.51034 | -0.42611 | -0.45925 | -0.5709 | -0.36873 | -0.25961 | -0.43458 | -0.41316 | 0.3504 | 0.33911 | 0.49761 | 0.63319 | -0.36347 | -0.49841 | -0.41951 | -0.46456 | -0.38033 | -0.41347 | -0.52512 | -0.32296 | -0.21384 | -0.3888 | -0.36739 | 0.39617 | 0.38488 | 0.54338 | 0.67897 | -0.71913 | -0.86634 | -0.78497 | -0.93219
926.1562 | 121.7377 | -0.61798 | 120.9366 | -0.41382 | -0.55335 | -0.47444 | -0.51034 | -0.43527 | -0.45467 | -0.56632 | -0.37331 | -0.26419 | -0.45747 | -0.42232 | 0.37329 | 0.35284 | 0.50219 | 0.61946 | -0.36804 | -0.50757 | -0.42866 | -0.46456 | -0.38949 | -0.40889 | -0.52054 | -0.32754 | -0.21842 | -0.41169 | -0.37654 | 0.41906 | 0.39862 | 0.54796 | 0.66524 | -0.7466 | -0.8755 | -0.83076 | -0.95966
927.9062 | 121.5958 | -0.66376 | 120.9732 | -0.40466 | -0.53503 | -0.45612 | -0.50576 | -0.42153 | -0.44551 | -0.55716 | -0.37789 | -0.25961 | -0.44831 | -0.41774 | 0.36871 | 0.33911 | 0.49761 | 0.62404 | -0.35889 | -0.48926 | -0.41035 | -0.45998 | -0.37576 | -0.39973 | -0.51138 | -0.33211 | -0.21384 | -0.40254 | -0.37196 | 0.41448 | 0.38488 | 0.54338 | 0.66981 | -0.7466 | -0.8755 | -0.81702 | -0.94592
929.6094 | 121.5912 | -0.66376 | 120.9641 | -0.40924 | -0.54419 | -0.46528 | -0.51492 | -0.42153 | -0.45467 | -0.55716 | -0.37789 | -0.25961 | -0.45289 | -0.42232 | 0.36871 | 0.34369 | 0.48845 | 0.62404 | -0.36347 | -0.49841 | -0.41951 | -0.46914 | -0.37576 | -0.40889 | -0.51138 | -0.33211 | -0.21384 | -0.40712 | -0.37654 | 0.41448 | 0.38946 | 0.53423 | 0.66981 | -0.7466 | -0.86634 | -0.8216 | -0.94134
931.375 | 121.6644 | -0.65918 | 120.9641 | -0.40924 | -0.53961 | -0.4607 | -0.51492 | -0.41695 | -0.45009 | -0.56632 | -0.37331 | -0.25504 | -0.46205 | -0.43148 | 0.37786 | 0.35284 | 0.48845 | 0.62404 | -0.36347 | -0.49384 | -0.41493 | -0.46914 | -0.37118 | -0.40431 | -0.52054 | -0.32754 | -0.20926 | -0.41627 | -0.3857 | 0.42364 | 0.39862 | 0.53423 | 0.66981 | -0.75118 | -0.86176 | -0.83991 | -0.9505
933.0938 | 121.6919 | -0.63171 | 120.9595 | -0.39551 | -0.53045 | -0.44697 | -0.4966 | -0.41695 | -0.44093 | -0.54343 | -0.355 | -0.25504 | -0.45289 | -0.42232 | 0.36871 | 0.35284 | 0.4793 | 0.6103 | -0.34973 | -0.48468 | -0.40119 | -0.45083 | -0.37118 | -0.39516 | -0.49765 | -0.30922 | -0.20926 | -0.40712 | -0.37654 | 0.41448 | 0.39862 | 0.52507 | 0.65608 | -0.72371 | -0.83429 | -0.8216 | -0.93219
934.8594 | 121.6415 | -0.64545 | 120.9732 | -0.39551 | -0.52587 | -0.44239 | -0.4966 | -0.41237 | -0.43178 | -0.548 | -0.36873 | -0.25504 | -0.44831 | -0.43148 | 0.36871 | 0.33911 | 0.47472 | 0.6103 | -0.34973 | -0.4801 | -0.39661 | -0.45083 | -0.3666 | -0.386 | -0.50223 | -0.32296 | -0.20926 | -0.40254 | -0.3857 | 0.41448 | 0.38488 | 0.52049 | 0.65608 | -0.73744 | -0.84345 | -0.81702 | -0.92303
936.625 | 121.6782 | -0.60883 | 120.9732 | -0.39093 | -0.53045 | -0.44239 | -0.48745 | -0.41237 | -0.43635 | -0.548 | -0.36873 | -0.24588 | -0.44373 | -0.41774 | 0.36413 | 0.33911 | 0.48845 | 0.6103 | -0.34515 | -0.48468 | -0.39661 | -0.44167 | -0.3666 | -0.39058 | -0.50223 | -0.32296 | -0.2001 | -0.39796 | -0.37196 | 0.40991 | 0.38488 | 0.53423 | 0.65608 | -0.73286 | -0.85719 | -0.80786 | -0.93219
938.3906 | 121.6736 | -0.60425 | 121.0007 | -0.37719 | -0.51672 | -0.43323 | -0.47829 | -0.39406 | -0.42262 | -0.52969 | -0.36873 | -0.25961 | -0.44831 | -0.41774 | 0.35955 | 0.33911 | 0.47014 | 0.59657 | -0.33142 | -0.47094 | -0.38745 | -0.43251 | -0.34829 | -0.37684 | -0.48392 | -0.32296 | -0.21384 | -0.40254 | -0.37196 | 0.40533 | 0.38488 | 0.51591 | 0.64235 | -0.72829 | -0.83887 | -0.80786 | -0.91845
940.1094 | 121.6095 | -0.63629 | 121.0007 | -0.37261 | -0.51672 | -0.42865 | -0.47829 | -0.39406 | -0.41346 | -0.52053 | -0.37331 | -0.25046 | -0.45747 | -0.42232 | 0.36871 | 0.34369 | 0.46556 | 0.58741 | -0.32684 | -0.47094 | -0.38288 | -0.43251 | -0.34829 | -0.36769 | -0.47476 | -0.32754 | -0.20468 | -0.41169 | -0.37654 | 0.41448 | 0.38946 | 0.51134 | 0.63319 | -0.74202 | -0.83887 | -0.82618 | -0.92303
941.8906 | 121.6644 | -0.59967 | 120.9686 | -0.37719 | -0.52587 | -0.43781 | -0.47829 | -0.4078 | -0.4272 | -0.53885 | -0.36873 | -0.25504 | -0.45747 | -0.43148 | 0.38244 | 0.34826 | 0.46098 | 0.58283 | -0.33142 | -0.4801 | -0.39203 | -0.43251 | -0.36202 | -0.38142 | -0.49307 | -0.32296 | -0.20926 | -0.41169 | -0.3857 | 0.42822 | 0.39404 | 0.50676 | 0.62861 | -0.75118 | -0.82971 | -0.83991 | -0.91845
943.6562 | 121.6278 | -0.62256 | 121.0007 | -0.36804 | -0.50298 | -0.4195 | -0.47371 | -0.38949 | -0.41804 | -0.52511 | -0.35958 | -0.25046 | -0.44831 | -0.41774 | 0.36871 | 0.34826 | 0.4564 | 0.5691 | -0.32226 | -0.45721 | -0.37372 | -0.42793 | -0.34371 | -0.37226 | -0.47934 | -0.3138 | -0.20468 | -0.40254 | -0.37196 | 0.41448 | 0.39404 | 0.50218 | 0.61488 | -0.72828 | -0.81598 | -0.81702 | -0.90472
945.3594 | 121.6919 | -0.59052 | 120.9732 | -0.35888 | -0.49382 | -0.40576 | -0.46455 | -0.38033 | -0.40431 | -0.51596 | -0.36873 | -0.25504 | -0.43916 | -0.41316 | 0.35497 | 0.32995 | 0.44725 | 0.5691 | -0.3131 | -0.44805 | -0.35998 | -0.41878 | -0.33455 | -0.35853 | -0.47018 | -0.32296 | -0.20926 | -0.39338 | -0.36739 | 0.40075 | 0.37573 | 0.49302 | 0.61488 | -0.72371 | -0.81598 | -0.79413 | -0.8864
947.1406 | 121.6782 | -0.57678 | 121.0327 | -0.3543 | -0.47551 | -0.40576 | -0.45082 | -0.3666 | -0.39515 | -0.50222 | -0.36416 | -0.24588 | -0.43458 | -0.404 | 0.35955 | 0.32537 | 0.43809 | 0.55994 | -0.30852 | -0.42973 | -0.35998 | -0.40504 | -0.32082 | -0.34937 | -0.45645 | -0.31838 | -0.2001 | -0.3888 | -0.35823 | 0.40533 | 0.37115 | 0.48386 | 0.60572 | -0.72371 | -0.80224 | -0.79413 | -0.87267
948.8438 | 121.5775 | -0.59967 | 121.0373 | -0.34057 | -0.48467 | -0.40118 | -0.45082 | -0.35744 | -0.39057 | -0.49764 | -0.36416 | -0.24588 | -0.44373 | -0.41316 | 0.35955 | 0.33911 | 0.43809 | 0.55536 | -0.29479 | -0.43889 | -0.35541 | -0.40504 | -0.31166 | -0.34479 | -0.45187 | -0.31838 | -0.2001 | -0.39796 | -0.36739 | 0.40533 | 0.38488 | 0.48386 | 0.60114 | -0.72371 | -0.80224 | -0.80329 | -0.88182
950.5938 | 121.7239 | -0.55847 | 120.9961 | -0.33599 | -0.48009 | -0.40118 | -0.45082 | -0.36202 | -0.38141 | -0.50222 | -0.35958 | -0.2413 | -0.43916 | -0.404 | 0.35955 | 0.32537 | 0.43809 | 0.55079 | -0.29021 | -0.43431 | -0.35541 | -0.40504 | -0.31624 | -0.33564 | -0.45645 | -0.3138 | -0.19552 | -0.39338 | -0.35823 | 0.40533 | 0.37115 | 0.48386 | 0.59656 | -0.71913 | -0.79767 | -0.79871 | -0.87725
952.3594 | 121.6095 | -0.58136 | 121.0556 | -0.33599 | -0.47551 | -0.38744 | -0.44166 | -0.35286 | -0.37226 | -0.49307 | -0.35958 | -0.24588 | -0.43916 | -0.41316 | 0.35497 | 0.33453 | 0.41978 | 0.53705 | -0.29021 | -0.42973 | -0.34167 | -0.39588 | -0.30709 | -0.32648 | -0.44729 | -0.3138 | -0.2001 | -0.39338 | -0.36739 | 0.40075 | 0.3803 | 0.46555 | 0.58283 | -0.71455 | -0.77935 | -0.79413 | -0.85893
954.0625 | 121.6415 | -0.56305 | 121.051 | -0.32225 | -0.46635 | -0.38287 | -0.4325 | -0.34828 | -0.3631 | -0.48391 | -0.36873 | -0.25046 | -0.43458 | -0.39942 | 0.35497 | 0.32079 | 0.41062 | 0.53248 | -0.27648 | -0.42058 | -0.33709 | -0.38673 | -0.30251 | -0.31732 | -0.43813 | -0.32296 | -0.20468 | -0.3888 | -0.35365 | 0.40075 | 0.36657 | 0.45639 | 0.57825 | -0.72371 | -0.77935 | -0.78955 | -0.8452
955.8438 | 121.7194 | -0.53101 | 121.0373 | -0.31767 | -0.45719 | -0.37371 | -0.42792 | -0.33913 | -0.36768 | -0.47933 | -0.35958 | -0.23672 | -0.43 | -0.404 | 0.3504 | 0.32537 | 0.41062 | 0.53248 | -0.2719 | -0.41142 | -0.32793 | -0.38215 | -0.29335 | -0.3219 | -0.43356 | -0.3138 | -0.19094 | -0.38422 | -0.35823 | 0.39617 | 0.37115 | 0.45639 | 0.57825 | -0.70997 | -0.7702 | -0.78039 | -0.84062
957.6094 | 121.6873 | -0.52185 | 121.051 | -0.31767 | -0.45261 | -0.35997 | -0.40961 | -0.32997 | -0.35852 | -0.47018 | -0.355 | -0.23672 | -0.42542 | -0.38569 | 0.33208 | 0.30706 | 0.40604 | 0.51874 | -0.2719 | -0.40684 | -0.3142 | -0.36383 | -0.2842 | -0.31274 | -0.4244 | -0.30922 | -0.19094 | -0.37965 | -0.33991 | 0.37786 | 0.35284 | 0.45182 | 0.56452 | -0.68708 | -0.76104 | -0.7575 | -0.83146
959.375 | 121.6827 | -0.53558 | 121.0464 | -0.30852 | -0.44804 | -0.36913 | -0.41419 | -0.32997 | -0.35394 | -0.47018 | -0.35958 | -0.25046 | -0.41169 | -0.38569 | 0.3275 | 0.31164 | 0.39688 | 0.50043 | -0.26274 | -0.40226 | -0.32336 | -0.36841 | -0.2842 | -0.30817 | -0.4244 | -0.3138 | -0.20468 | -0.36591 | -0.33991 | 0.37328 | 0.35741 | 0.44266 | 0.5462 | -0.68708 | -0.75646 | -0.73919 | -0.80857
961.0938 | 121.6782 | -0.52643 | 121.0602 | -0.30394 | -0.44346 | -0.35997 | -0.41419 | -0.32539 | -0.35394 | -0.4656 | -0.355 | -0.23672 | -0.41169 | -0.39026 | 0.3275 | 0.30706 | 0.38773 | 0.50501 | -0.25816 | -0.39768 | -0.3142 | -0.36841 | -0.27962 | -0.30817 | -0.41982 | -0.30922 | -0.19094 | -0.36591 | -0.34449 | 0.37328 | 0.35284 | 0.4335 | 0.55078 | -0.6825 | -0.74272 | -0.73919 | -0.79941
962.875 | 121.6736 | -0.5127 | 121.0419 | -0.3131 | -0.45261 | -0.35997 | -0.41419 | -0.32997 | -0.35394 | -0.47018 | -0.355 | -0.25046 | -0.41626 | -0.38569 | 0.33666 | 0.30706 | 0.38773 | 0.50501 | -0.26732 | -0.40684 | -0.3142 | -0.36841 | -0.2842 | -0.30817 | -0.4244 | -0.30922 | -0.20468 | -0.37049 | -0.33991 | 0.38244 | 0.35284 | 0.4335 | 0.55078 | -0.69166 | -0.74272 | -0.75293 | -0.80399
964.5781 | 121.6736 | -0.52185 | 121.0831 | -0.30394 | -0.44804 | -0.35997 | -0.40961 | -0.32539 | -0.35394 | -0.46102 | -0.35042 | -0.24588 | -0.42084 | -0.38569 | 0.34582 | 0.32079 | 0.38773 | 0.49585 | -0.25816 | -0.40226 | -0.3142 | -0.36383 | -0.27962 | -0.30817 | -0.41524 | -0.30464 | -0.2001 | -0.37507 | -0.33991 | 0.39159 | 0.36657 | 0.4335 | 0.54163 | -0.69624 | -0.73815 | -0.76666 | -0.80857
966.3438 | 121.7148 | -0.50812 | 121.0693 | -0.30852 | -0.44346 | -0.36455 | -0.40503 | -0.31624 | -0.34936 | -0.45644 | -0.35042 | -0.23672 | -0.42084 | -0.39484 | 0.34582 | 0.31164 | 0.38315 | 0.49127 | -0.26274 | -0.39768 | -0.31878 | -0.35926 | -0.27046 | -0.30359 | -0.41066 | -0.30464 | -0.19094 | -0.37507 | -0.34907 | 0.39159 | 0.35741 | 0.42893 | 0.53705 | -0.69624 | -0.73357 | -0.76666 | -0.80399
968.0469 | 121.7377 | -0.49896 | 121.0785 | -0.29936 | -0.44346 | -0.36455 | -0.40045 | -0.32082 | -0.34479 | -0.46102 | -0.355 | -0.2413 | -0.43 | -0.39942 | 0.34124 | 0.31622 | 0.38773 | 0.49127 | -0.25359 | -0.39768 | -0.31878 | -0.35468 | -0.27504 | -0.29901 | -0.41524 | -0.30922 | -0.19552 | -0.38422 | -0.35365 | 0.38701 | 0.36199 | 0.4335 | 0.53705 | -0.69624 | -0.74272 | -0.77124 | -0.81773
969.8125 | 121.6873 | -0.5127 | 121.0922 | -0.29936 | -0.4343 | -0.35082 | -0.3913 | -0.31166 | -0.34021 | -0.45644 | -0.35042 | -0.23672 | -0.42542 | -0.38569 | 0.33666 | 0.30706 | 0.37857 | 0.49127 | -0.25359 | -0.38852 | -0.30504 | -0.34552 | -0.26588 | -0.29443 | -0.41066 | -0.30464 | -0.19094 | -0.37965 | -0.33991 | 0.38244 | 0.35284 | 0.42435 | 0.53705 | -0.68708 | -0.72899 | -0.76208 | -0.80399
971.5 | 121.6873 | -0.52185 | 121.0693 | -0.2902 | -0.43888 | -0.3554 | -0.3913 | -0.30708 | -0.34021 | -0.46102 | -0.34584 | -0.23672 | -0.43916 | -0.39942 | 0.3504 | 0.32995 | 0.36941 | 0.48669 | -0.24443 | -0.3931 | -0.30962 | -0.34552 | -0.26131 | -0.29443 | -0.41524 | -0.30007 | -0.19094 | -0.39338 | -0.35365 | 0.39617 | 0.37573 | 0.41519 | 0.53247 | -0.69624 | -0.71525 | -0.78955 | -0.80857
973.2656 | 121.7102 | -0.48981 | 121.0693 | -0.29478 | -0.4343 | -0.34624 | -0.3913 | -0.29793 | -0.33105 | -0.45644 | -0.35042 | -0.23214 | -0.43916 | -0.404 | 0.3504 | 0.32079 | 0.36941 | 0.47296 | -0.24901 | -0.38852 | -0.30046 | -0.34552 | -0.25215 | -0.28527 | -0.41066 | -0.30464 | -0.18637 | -0.39338 | -0.35823 | 0.39617 | 0.36657 | 0.41519 | 0.51873 | -0.70081 | -0.71983 | -0.78955 | -0.80857
975.0469 | 121.6324 | -0.52185 | 121.0876 | -0.27189 | -0.42514 | -0.33708 | -0.37756 | -0.29335 | -0.32189 | -0.45186 | -0.355 | -0.22756 | -0.42542 | -0.39942 | 0.34582 | 0.32079 | 0.36026 | 0.47754 | -0.22611 | -0.37937 | -0.2913 | -0.33178 | -0.24757 | -0.27612 | -0.40609 | -0.30922 | -0.18179 | -0.37965 | -0.35365 | 0.39159 | 0.36657 | 0.40603 | 0.52331 | -0.70081 | -0.71525 | -0.77124 | -0.78568
976.7656 | 121.7377 | -0.4715 | 121.0785 | -0.27647 | -0.41141 | -0.32334 | -0.37298 | -0.27961 | -0.31732 | -0.43813 | -0.34584 | -0.23214 | -0.43 | -0.38569 | 0.3275 | 0.32079 | 0.36026 | 0.45922 | -0.23069 | -0.36563 | -0.27757 | -0.32721 | -0.23384 | -0.27154 | -0.39235 | -0.30007 | -0.18637 | -0.38422 | -0.33991 | 0.37328 | 0.36657 | 0.40603 | 0.505 | -0.67335 | -0.7061 | -0.7575 | -0.79026
978.5156 | 121.6095 | -0.49896 | 121.1426 | -0.27647 | -0.41598 | -0.32792 | -0.37298 | -0.27961 | -0.31274 | -0.43813 | -0.34584 | -0.22756 | -0.43 | -0.38111 | 0.33666 | 0.31164 | 0.3511 | 0.45922 | -0.23069 | -0.37021 | -0.28215 | -0.32721 | -0.23384 | -0.26696 | -0.39235 | -0.30007 | -0.18179 | -0.38422 | -0.33533 | 0.38244 | 0.35741 | 0.39688 | 0.505 | -0.6825 | -0.69694 | -0.76666 | -0.7811
980.2969 | 121.6873 | -0.48981 | 121.0968 | -0.27189 | -0.41141 | -0.31877 | -0.37298 | -0.27504 | -0.31732 | -0.43355 | -0.34584 | -0.23214 | -0.42542 | -0.39026 | 0.33208 | 0.32079 | 0.34652 | 0.45922 | -0.22611 | -0.36563 | -0.27299 | -0.32721 | -0.22926 | -0.27154 | -0.38777 | -0.30007 | -0.18637 | -0.37965 | -0.34449 | 0.37786 | 0.36657 | 0.3923 | 0.505 | -0.67792 | -0.69236 | -0.7575 | -0.77194
982 | 121.7102 | -0.48065 | 121.0831 | -0.26731 | -0.40683 | -0.32334 | -0.36383 | -0.27961 | -0.31274 | -0.42897 | -0.34584 | -0.22756 | -0.41626 | -0.38111 | 0.3275 | 0.30706 | 0.3511 | 0.45465 | -0.22154 | -0.36105 | -0.27757 | -0.31805 | -0.23384 | -0.26696 | -0.3832 | -0.30007 | -0.18179 | -0.37049 | -0.33533 | 0.37328 | 0.35284 | 0.39688 | 0.50042 | -0.67335 | -0.69694 | -0.74377 | -0.76737
983.7656 | 121.6095 | -0.50354 | 121.1288 | -0.26731 | -0.40225 | -0.32334 | -0.3684 | -0.27046 | -0.30358 | -0.42439 | -0.34584 | -0.23214 | -0.41169 | -0.37653 | 0.3275 | 0.30248 | 0.34194 | 0.4638 | -0.22154 | -0.35647 | -0.27757 | -0.32263 | -0.22468 | -0.2578 | -0.37862 | -0.30007 | -0.18637 | -0.36591 | -0.33075 | 0.37328 | 0.34826 | 0.38772 | 0.50958 | -0.67335 | -0.68778 | -0.73919 | -0.75363
985.4688 | 121.7422 | -0.46234 | 121.1105 | -0.26273 | -0.39767 | -0.30961 | -0.35467 | -0.27046 | -0.28985 | -0.41981 | -0.33668 | -0.22756 | -0.39795 | -0.37653 | 0.31835 | 0.29333 | 0.34194 | 0.45007 | -0.21696 | -0.35189 | -0.26383 | -0.30889 | -0.22468 | -0.24407 | -0.37404 | -0.29091 | -0.18179 | -0.35218 | -0.33075 | 0.36412 | 0.3391 | 0.38772 | 0.49584 | -0.65503 | -0.67863 | -0.7163 | -0.73989
987.25 | 121.7148 | -0.45319 | 121.1105 | -0.249 | -0.39309 | -0.31419 | -0.35925 | -0.27046 | -0.299 | -0.41981 | -0.34584 | -0.21841 | -0.39795 | -0.36737 | 0.31835 | 0.28875 | 0.33737 | 0.44091 | -0.20322 | -0.34731 | -0.26841 | -0.31347 | -0.22468 | -0.25323 | -0.37404 | -0.30007 | -0.17263 | -0.35218 | -0.32159 | 0.36412 | 0.33452 | 0.38314 | 0.48669 | -0.66419 | -0.68321 | -0.7163 | -0.73532
989.0156 | 121.7422 | -0.46234 | 121.0922 | -0.25358 | -0.39767 | -0.31419 | -0.35925 | -0.2613 | -0.299 | -0.41524 | -0.34126 | -0.22298 | -0.39795 | -0.37195 | 0.31377 | 0.28417 | 0.33737 | 0.44091 | -0.2078 | -0.35189 | -0.26841 | -0.31347 | -0.21553 | -0.25323 | -0.36946 | -0.29549 | -0.17721 | -0.35218 | -0.32617 | 0.35955 | 0.32995 | 0.38314 | 0.48669 | -0.65503 | -0.67863 | -0.71172 | -0.73532
990.7969 | 121.7148 | -0.44861 | 121.1472 | -0.25816 | -0.39309 | -0.30503 | -0.35009 | -0.26588 | -0.28527 | -0.40608 | -0.34126 | -0.22756 | -0.40253 | -0.36737 | 0.30919 | 0.27959 | 0.32363 | 0.44549 | -0.21238 | -0.34731 | -0.25925 | -0.30431 | -0.2201 | -0.23949 | -0.3603 | -0.29549 | -0.18179 | -0.35675 | -0.32159 | 0.35497 | 0.32537 | 0.36941 | 0.49127 | -0.65046 | -0.66489 | -0.71172 | -0.72616
992.5 | 121.669 | -0.44403 | 121.1334 | -0.249 | -0.38393 | -0.30961 | -0.35467 | -0.26588 | -0.28527 | -0.41066 | -0.34584 | -0.22756 | -0.3888 | -0.36279 | 0.31377 | 0.28417 | 0.33279 | 0.43633 | -0.20322 | -0.33816 | -0.26383 | -0.30889 | -0.2201 | -0.23949 | -0.36488 | -0.30007 | -0.18179 | -0.34302 | -0.31701 | 0.35955 | 0.32995 | 0.37856 | 0.48211 | -0.65961 | -0.67863 | -0.70256 | -0.72158
994.2656 | 121.6003 | -0.47607 | 121.1655 | -0.23984 | -0.37935 | -0.29129 | -0.35467 | -0.25672 | -0.28069 | -0.40608 | -0.34126 | -0.22298 | -0.39795 | -0.35363 | 0.30919 | 0.27959 | 0.32821 | 0.43175 | -0.19407 | -0.33358 | -0.24552 | -0.30889 | -0.21095 | -0.23491 | -0.3603 | -0.29549 | -0.17721 | -0.35218 | -0.30786 | 0.35497 | 0.32537 | 0.37398 | 0.47753 | -0.65046 | -0.66947 | -0.70714 | -0.72616
996.0469 | 121.6232 | -0.48523 | 121.1517 | -0.23984 | -0.38851 | -0.29587 | -0.34551 | -0.25672 | -0.29442 | -0.41066 | -0.33668 | -0.22298 | -0.39795 | -0.36737 | 0.30919 | 0.28417 | 0.32363 | 0.43175 | -0.19407 | -0.34274 | -0.2501 | -0.29974 | -0.21095 | -0.24865 | -0.36488 | -0.29091 | -0.17721 | -0.35218 | -0.32159 | 0.35497 | 0.32995 | 0.36941 | 0.47753 | -0.64588 | -0.66031 | -0.70714 | -0.72158
997.8281 | 121.637 | -0.46234 | 121.1609 | -0.23526 | -0.37477 | -0.29587 | -0.34093 | -0.25672 | -0.27611 | -0.4015 | -0.34584 | -0.23214 | -0.3888 | -0.35363 | 0.30003 | 0.28417 | 0.31905 | 0.43633 | -0.18949 | -0.329 | -0.2501 | -0.29516 | -0.21095 | -0.23033 | -0.35573 | -0.30007 | -0.18637 | -0.34302 | -0.30786 | 0.34581 | 0.32995 | 0.36483 | 0.48211 | -0.64588 | -0.66489 | -0.68883 | -0.70785
999.5312 | 121.6644 | -0.43945 | 121.1472 | -0.23069 | -0.3702 | -0.29129 | -0.33636 | -0.25215 | -0.26695 | -0.39692 | -0.34126 | -0.23214 | -0.3888 | -0.35363 | 0.30003 | 0.28417 | 0.31447 | 0.42718 | -0.18491 | -0.32442 | -0.24552 | -0.29058 | -0.20637 | -0.22118 | -0.35115 | -0.29549 | -0.18637 | -0.34302 | -0.30786 | 0.34581 | 0.32995 | 0.36025 | 0.47295 | -0.6413 | -0.65574 | -0.68883 | -0.70327
1001.2969 | 121.7377 | -0.41657 | 121.1426 | -0.23526 | -0.3702 | -0.28214 | -0.33636 | -0.24757 | -0.26695 | -0.38777 | -0.32753 | -0.22298 | -0.37964 | -0.34905 | 0.29546 | 0.27959 | 0.31447 | 0.41802 | -0.18949 | -0.32442 | -0.23636 | -0.29058 | -0.20179 | -0.22118 | -0.34199 | -0.28175 | -0.17721 | -0.33386 | -0.30328 | 0.34123 | 0.32537 | 0.36025 | 0.4638 | -0.62298 | -0.642 | -0.6751 | -0.69411
1003.0781 | 121.6782 | -0.4303 | 121.1563 | -0.22153 | -0.36562 | -0.28214 | -0.33178 | -0.24299 | -0.27153 | -0.39235 | -0.34584 | -0.22756 | -0.38422 | -0.34447 | 0.29546 | 0.27044 | 0.30989 | 0.4226 | -0.17575 | -0.31984 | -0.23636 | -0.286 | -0.19722 | -0.22576 | -0.34657 | -0.30007 | -0.18179 | -0.33844 | -0.2987 | 0.34123 | 0.31621 | 0.35567 | 0.46837 | -0.6413 | -0.65574 | -0.67967 | -0.69411
1004.7812 | 121.7102 | -0.4303 | 121.1426 | -0.22611 | -0.36562 | -0.27756 | -0.33636 | -0.24757 | -0.26695 | -0.39235 | -0.33668 | -0.22756 | -0.37506 | -0.34447 | 0.29088 | 0.26128 | 0.30532 | 0.41344 | -0.18033 | -0.31984 | -0.23178 | -0.29058 | -0.20179 | -0.22118 | -0.34657 | -0.29091 | -0.18179 | -0.32928 | -0.2987 | 0.33665 | 0.30705 | 0.35109 | 0.45922 | -0.62756 | -0.642 | -0.66594 | -0.68038
1006.5469 | 121.6599 | -0.46234 | 121.1609 | -0.22611 | -0.37477 | -0.28672 | -0.34551 | -0.25215 | -0.27611 | -0.39235 | -0.33668 | -0.22298 | -0.37506 | -0.34905 | 0.29546 | 0.26586 | 0.30989 | 0.42718 | -0.18033 | -0.329 | -0.24094 | -0.29974 | -0.20637 | -0.23033 | -0.34657 | -0.29091 | -0.17721 | -0.32928 | -0.30328 | 0.34123 | 0.31163 | 0.35567 | 0.47295 | -0.63214 | -0.64658 | -0.67052 | -0.68495
1008.3125 | 121.6049 | -0.46692 | 121.1929 | -0.22611 | -0.3702 | -0.28214 | -0.33636 | -0.24757 | -0.2578 | -0.39235 | -0.33668 | -0.22756 | -0.37964 | -0.3399 | 0.2863 | 0.27044 | 0.30989 | 0.41344 | -0.18033 | -0.32442 | -0.23636 | -0.29058 | -0.20179 | -0.21202 | -0.34657 | -0.29091 | -0.18179 | -0.33386 | -0.29412 | 0.33208 | 0.31621 | 0.35567 | 0.45922 | -0.62299 | -0.64658 | -0.66594 | -0.68953
1010.0781 | 121.6553 | -0.45776 | 121.1746 | -0.21237 | -0.36562 | -0.27756 | -0.33178 | -0.23841 | -0.26238 | -0.39235 | -0.34126 | -0.23214 | -0.3659 | -0.33532 | 0.27714 | 0.25212 | 0.30532 | 0.40886 | -0.16659 | -0.31984 | -0.23178 | -0.286 | -0.19264 | -0.2166 | -0.34657 | -0.29549 | -0.18637 | -0.32013 | -0.28954 | 0.32292 | 0.2979 | 0.35109 | 0.45464 | -0.61841 | -0.64658 | -0.64305 | -0.67122
1011.7969 | 121.6782 | -0.41657 | 121.138 | -0.22611 | -0.36104 | -0.27298 | -0.34093 | -0.24757 | -0.26695 | -0.38777 | -0.35042 | -0.22756 | -0.36133 | -0.32616 | 0.27714 | 0.24754 | 0.30074 | 0.41802 | -0.18033 | -0.31526 | -0.2272 | -0.29516 | -0.20179 | -0.22118 | -0.34199 | -0.30464 | -0.18179 | -0.31555 | -0.28038 | 0.32292 | 0.29332 | 0.34651 | 0.4638 | -0.62756 | -0.65116 | -0.63847 | -0.66206
1013.4844 | 121.6827 | -0.41657 | 121.1792 | -0.22153 | -0.36562 | -0.27298 | -0.33636 | -0.24299 | -0.26695 | -0.39235 | -0.33668 | -0.22298 | -0.35675 | -0.33074 | 0.27257 | 0.2567 | 0.30532 | 0.40886 | -0.17575 | -0.31984 | -0.2272 | -0.29058 | -0.19722 | -0.22118 | -0.34657 | -0.29091 | -0.17721 | -0.31097 | -0.28496 | 0.31834 | 0.30248 | 0.35109 | 0.45464 | -0.60925 | -0.642 | -0.62931 | -0.66206
1015.25 | 121.6324 | -0.45319 | 121.1975 | -0.23526 | -0.3702 | -0.27298 | -0.33636 | -0.24757 | -0.27611 | -0.39692 | -0.34126 | -0.21841 | -0.3659 | -0.33074 | 0.27257 | 0.24754 | 0.30074 | 0.40429 | -0.18949 | -0.32442 | -0.2272 | -0.29058 | -0.20179 | -0.23033 | -0.35115 | -0.29549 | -0.17263 | -0.32013 | -0.28496 | 0.31834 | 0.29332 | 0.34651 | 0.45006 | -0.61383 | -0.642 | -0.63847 | -0.66664
1016.9688 | 121.7422 | -0.42114 | 121.1517 | -0.22611 | -0.3702 | -0.28672 | -0.34551 | -0.25215 | -0.27611 | -0.39235 | -0.34126 | -0.22298 | -0.35675 | -0.32616 | 0.27714 | 0.25212 | 0.30074 | 0.40429 | -0.18033 | -0.32442 | -0.24094 | -0.29974 | -0.20637 | -0.23033 | -0.34657 | -0.29549 | -0.17721 | -0.31097 | -0.28038 | 0.32292 | 0.2979 | 0.34651 | 0.45006 | -0.61841 | -0.642 | -0.63389 | -0.65748
1018.6719 | 121.6873 | -0.41199 | 121.1746 | -0.23069 | -0.3702 | -0.27756 | -0.33178 | -0.24757 | -0.26238 | -0.38777 | -0.34126 | -0.22298 | -0.35217 | -0.32158 | 0.27714 | 0.25212 | 0.30074 | 0.39971 | -0.18491 | -0.32442 | -0.23178 | -0.286 | -0.20179 | -0.2166 | -0.34199 | -0.29549 | -0.17721 | -0.30639 | -0.2758 | 0.32292 | 0.2979 | 0.34651 | 0.44548 | -0.61841 | -0.642 | -0.62931 | -0.65291
1020.4219 | 121.6415 | -0.4303 | 121.1975 | -0.22153 | -0.37477 | -0.2684 | -0.3272 | -0.24299 | -0.25322 | -0.38319 | -0.34126 | -0.22298 | -0.35675 | -0.32158 | 0.27714 | 0.24754 | 0.29158 | 0.40429 | -0.17575 | -0.329 | -0.22263 | -0.28142 | -0.19722 | -0.20744 | -0.33741 | -0.29549 | -0.17721 | -0.31097 | -0.2758 | 0.32292 | 0.29332 | 0.33736 | 0.45006 | -0.61841 | -0.63284 | -0.63389 | -0.64833
1022.2188 | 121.6553 | -0.43488 | 121.2158 | -0.22153 | -0.36562 | -0.27298 | -0.3272 | -0.23383 | -0.25322 | -0.38319 | -0.34126 | -0.22298 | -0.35675 | -0.32616 | 0.27714 | 0.25212 | 0.29616 | 0.39971 | -0.17575 | -0.31984 | -0.2272 | -0.28142 | -0.18806 | -0.20744 | -0.33741 | -0.29549 | -0.17721 | -0.31097 | -0.28038 | 0.32292 | 0.2979 | 0.34193 | 0.44548 | -0.61841 | -0.63742 | -0.63389 | -0.65291
1023.9219 | 121.7422 | -0.38452 | 121.1655 | -0.22153 | -0.36104 | -0.28214 | -0.33636 | -0.24299 | -0.26238 | -0.38777 | -0.33668 | -0.22756 | -0.35675 | -0.33532 | 0.26799 | 0.25212 | 0.287 | 0.39513 | -0.17575 | -0.31526 | -0.23636 | -0.29058 | -0.19722 | -0.2166 | -0.34199 | -0.29091 | -0.18179 | -0.31097 | -0.28954 | 0.31376 | 0.2979 | 0.33278 | 0.4409 | -0.60467 | -0.62369 | -0.62474 | -0.64375
1025.625 | 121.7239 | -0.38452 | 121.1884 | -0.22153 | -0.36562 | -0.27756 | -0.33636 | -0.23841 | -0.26695 | -0.38319 | -0.34126 | -0.21841 | -0.36133 | -0.317 | 0.27257 | 0.24754 | 0.28242 | 0.39055 | -0.17575 | -0.31984 | -0.23178 | -0.29058 | -0.19264 | -0.22118 | -0.33741 | -0.29549 | -0.17263 | -0.31555 | -0.27122 | 0.31834 | 0.29332 | 0.3282 | 0.43633 | -0.61383 | -0.62369 | -0.63389 | -0.64375
1027.3906 | 121.6965 | -0.41657 | 121.1975 | -0.22153 | -0.35646 | -0.26382 | -0.3272 | -0.23841 | -0.25322 | -0.37861 | -0.33668 | -0.22298 | -0.35217 | -0.32158 | 0.26799 | 0.24754 | 0.28242 | 0.38597 | -0.17575 | -0.31068 | -0.21805 | -0.28142 | -0.19264 | -0.20744 | -0.33283 | -0.29091 | -0.17721 | -0.30639 | -0.2758 | 0.31376 | 0.29332 | 0.3282 | 0.43175 | -0.60467 | -0.61911 | -0.62016 | -0.63459
1029.1719 | 121.6553 | -0.42572 | 121.225 | -0.20779 | -0.3473 | -0.26382 | -0.31804 | -0.22468 | -0.25322 | -0.37403 | -0.33668 | -0.21383 | -0.35217 | -0.317 | 0.26799 | 0.24754 | 0.27785 | 0.38139 | -0.16202 | -0.30153 | -0.21805 | -0.27227 | -0.1789 | -0.20744 | -0.32826 | -0.29091 | -0.16805 | -0.30639 | -0.27122 | 0.31376 | 0.29332 | 0.32362 | 0.42717 | -0.60467 | -0.61453 | -0.62016 | -0.63001
1030.8906 | 121.6599 | -0.4303 | 121.225 | -0.20779 | -0.35188 | -0.25924 | -0.30888 | -0.2201 | -0.24864 | -0.37861 | -0.33668 | -0.21841 | -0.35217 | -0.317 | 0.26341 | 0.23839 | 0.27785 | 0.37682 | -0.16202 | -0.3061 | -0.21347 | -0.26311 | -0.17433 | -0.20286 | -0.33283 | -0.29091 | -0.17263 | -0.30639 | -0.27122 | 0.30919 | 0.28417 | 0.32362 | 0.42259 | -0.60009 | -0.61453 | -0.61558 | -0.63001
1032.6094 | 121.7194 | -0.38452 | 121.17 | -0.20779 | -0.35188 | -0.25924 | -0.31346 | -0.21552 | -0.24864 | -0.36488 | -0.34126 | -0.22298 | -0.35217 | -0.31242 | 0.26341 | 0.23381 | 0.26411 | 0.37224 | -0.16202 | -0.3061 | -0.21347 | -0.26769 | -0.16975 | -0.20286 | -0.3191 | -0.29549 | -0.17721 | -0.30639 | -0.26665 | 0.30919 | 0.27959 | 0.30989 | 0.41801 | -0.60467 | -0.60537 | -0.61558 | -0.61628
1034.3594 | 121.7194 | -0.37994 | 121.1655 | -0.20321 | -0.34272 | -0.25924 | -0.31346 | -0.22468 | -0.24406 | -0.36945 | -0.33668 | -0.22298 | -0.34759 | -0.317 | 0.25883 | 0.24297 | 0.26411 | 0.37224 | -0.15744 | -0.29695 | -0.21347 | -0.26769 | -0.1789 | -0.19828 | -0.32368 | -0.29091 | -0.17721 | -0.30181 | -0.27122 | 0.30461 | 0.28874 | 0.30989 | 0.41801 | -0.59552 | -0.60079 | -0.60642 | -0.6117
1036.0625 | 121.6415 | -0.41657 | 121.2067 | -0.19864 | -0.34272 | -0.25924 | -0.30888 | -0.2201 | -0.23033 | -0.36945 | -0.34584 | -0.21841 | -0.34301 | -0.317 | 0.25883 | 0.23381 | 0.25953 | 0.36308 | -0.15286 | -0.29695 | -0.21347 | -0.26311 | -0.17433 | -0.18455 | -0.32368 | -0.30007 | -0.17263 | -0.29724 | -0.27122 | 0.30461 | 0.27959 | 0.30531 | 0.40886 | -0.60467 | -0.60537 | -0.60184 | -0.60254
1037.8281 | 121.6187 | -0.39825 | 121.2112 | -0.19406 | -0.33357 | -0.24551 | -0.30888 | -0.20637 | -0.23033 | -0.3603 | -0.33668 | -0.21841 | -0.34301 | -0.30784 | 0.25425 | 0.22923 | 0.25953 | 0.36766 | -0.14828 | -0.28779 | -0.19973 | -0.26311 | -0.16059 | -0.18455 | -0.31452 | -0.29091 | -0.17263 | -0.29724 | -0.26207 | 0.30003 | 0.27501 | 0.30531 | 0.41344 | -0.59094 | -0.59622 | -0.59726 | -0.60254
1039.5156 | 121.582 | -0.41199 | 121.257 | -0.1849 | -0.33814 | -0.24551 | -0.29973 | -0.20179 | -0.22575 | -0.35114 | -0.33668 | -0.20925 | -0.33843 | -0.31242 | 0.25425 | 0.23381 | 0.2458 | 0.35393 | -0.13912 | -0.29237 | -0.19973 | -0.25395 | -0.15601 | -0.17997 | -0.30537 | -0.29091 | -0.16347 | -0.29266 | -0.26665 | 0.30003 | 0.27959 | 0.29157 | 0.3997 | -0.59094 | -0.58248 | -0.59269 | -0.58423
1041.2656 | 121.6827 | -0.35706 | 121.2204 | -0.18948 | -0.32899 | -0.24551 | -0.29515 | -0.20179 | -0.23033 | -0.35572 | -0.33668 | -0.21383 | -0.33843 | -0.30326 | 0.25883 | 0.23839 | 0.2458 | 0.35393 | -0.1437 | -0.28321 | -0.19973 | -0.24937 | -0.15601 | -0.18455 | -0.30994 | -0.29091 | -0.16805 | -0.29266 | -0.25749 | 0.30461 | 0.28417 | 0.29157 | 0.3997 | -0.59552 | -0.58248 | -0.59727 | -0.58423
1042.9844 | 121.6141 | -0.3891 | 121.2616 | -0.18948 | -0.33357 | -0.23635 | -0.29973 | -0.20179 | -0.2349 | -0.3603 | -0.33211 | -0.21841 | -0.33843 | -0.29868 | 0.24968 | 0.22465 | 0.24122 | 0.35393 | -0.1437 | -0.28779 | -0.19057 | -0.25395 | -0.15601 | -0.18913 | -0.31452 | -0.28633 | -0.17263 | -0.29266 | -0.25291 | 0.29545 | 0.27043 | 0.287 | 0.3997 | -0.58178 | -0.57332 | -0.58811 | -0.57965
1044.7344 | 121.7194 | -0.34332 | 121.2296 | -0.1849 | -0.32441 | -0.23177 | -0.29515 | -0.19721 | -0.21659 | -0.34656 | -0.33668 | -0.20925 | -0.32928 | -0.30326 | 0.2451 | 0.22465 | 0.23664 | 0.34935 | -0.13912 | -0.27863 | -0.186 | -0.24937 | -0.15143 | -0.17081 | -0.30079 | -0.29091 | -0.16347 | -0.2835 | -0.25749 | 0.29087 | 0.27043 | 0.28242 | 0.39512 | -0.58178 | -0.57332 | -0.57437 | -0.56592
1046.4844 | 121.7331 | -0.33417 | 121.2341 | -0.17574 | -0.32441 | -0.23177 | -0.29057 | -0.20179 | -0.22117 | -0.35114 | -0.33211 | -0.20925 | -0.33386 | -0.29411 | 0.24968 | 0.22008 | 0.23206 | 0.34477 | -0.12997 | -0.27863 | -0.186 | -0.24479 | -0.15601 | -0.17539 | -0.30537 | -0.28633 | -0.16347 | -0.28808 | -0.24833 | 0.29545 | 0.26585 | 0.27784 | 0.39054 | -0.58178 | -0.56417 | -0.58353 | -0.56592
1048.25 | 121.6827 | -0.35248 | 121.2158 | -0.17117 | -0.31525 | -0.23177 | -0.29057 | -0.19263 | -0.22117 | -0.34656 | -0.32753 | -0.21383 | -0.32928 | -0.29868 | 0.2451 | 0.22923 | 0.23664 | 0.34477 | -0.12539 | -0.26947 | -0.186 | -0.24479 | -0.14686 | -0.17539 | -0.30079 | -0.28175 | -0.16805 | -0.2835 | -0.25291 | 0.29087 | 0.27501 | 0.28242 | 0.39054 | -0.57262 | -0.56417 | -0.57437 | -0.56592
1050.0156 | 121.637 | -0.3891 | 121.2524 | -0.17117 | -0.31525 | -0.22262 | -0.29057 | -0.18805 | -0.21659 | -0.34199 | -0.33668 | -0.21841 | -0.33386 | -0.31242 | 0.24968 | 0.22008 | 0.23206 | 0.34019 | -0.12539 | -0.26947 | -0.17684 | -0.24479 | -0.14228 | -0.17081 | -0.29621 | -0.29091 | -0.17263 | -0.28808 | -0.26665 | 0.29545 | 0.26585 | 0.27784 | 0.38597 | -0.58636 | -0.56875 | -0.58353 | -0.56592
1051.7656 | 121.7422 | -0.34332 | 121.2341 | -0.16659 | -0.31983 | -0.23177 | -0.28599 | -0.18348 | -0.21201 | -0.34199 | -0.33211 | -0.21383 | -0.33386 | -0.29868 | 0.24968 | 0.22008 | 0.22748 | 0.34019 | -0.12081 | -0.27405 | -0.186 | -0.24022 | -0.1377 | -0.16624 | -0.29621 | -0.28633 | -0.16805 | -0.28808 | -0.25291 | 0.29545 | 0.26585 | 0.27326 | 0.38597 | -0.58178 | -0.55959 | -0.58353 | -0.56134
1053.4531 | 121.6736 | -0.36163 | 121.2387 | -0.15743 | -0.30609 | -0.22262 | -0.27683 | -0.19263 | -0.20743 | -0.33283 | -0.33211 | -0.21841 | -0.33843 | -0.30326 | 0.24052 | 0.22008 | 0.22748 | 0.34019 | -0.11165 | -0.26032 | -0.17684 | -0.23106 | -0.14686 | -0.16166 | -0.28705 | -0.28633 | -0.17263 | -0.29266 | -0.25749 | 0.2863 | 0.26585 | 0.27326 | 0.38597 | -0.57263 | -0.55959 | -0.57895 | -0.56592
1055.2344 | 121.6507 | -0.37079 | 121.2662 | -0.16659 | -0.31067 | -0.21804 | -0.28599 | -0.18805 | -0.22117 | -0.32825 | -0.33211 | -0.21383 | -0.33843 | -0.29868 | 0.25425 | 0.22008 | 0.23206 | 0.33104 | -0.12081 | -0.26489 | -0.17226 | -0.24022 | -0.14228 | -0.17539 | -0.28248 | -0.28633 | -0.16805 | -0.29266 | -0.25291 | 0.30003 | 0.26585 | 0.27784 | 0.37681 | -0.58636 | -0.56417 | -0.59269 | -0.5705
1057.0156 | 121.6095 | -0.39368 | 121.2753 | -0.17117 | -0.31983 | -0.22719 | -0.28141 | -0.19263 | -0.21659 | -0.33741 | -0.32753 | -0.21841 | -0.33386 | -0.29868 | 0.2451 | 0.22465 | 0.2229 | 0.32646 | -0.12539 | -0.27405 | -0.18142 | -0.23564 | -0.14686 | -0.17081 | -0.29163 | -0.28175 | -0.17263 | -0.28808 | -0.25291 | 0.29087 | 0.27043 | 0.26868 | 0.37223 | -0.57262 | -0.55043 | -0.57895 | -0.55676
1058.7969 | 121.6553 | -0.37079 | 121.2799 | -0.16659 | -0.31067 | -0.22262 | -0.27683 | -0.18805 | -0.21201 | -0.33741 | -0.32753 | -0.21383 | -0.33386 | -0.29411 | 0.25425 | 0.22008 | 0.21375 | 0.32646 | -0.12081 | -0.26489 | -0.17684 | -0.23106 | -0.14228 | -0.16624 | -0.29163 | -0.28175 | -0.16805 | -0.28808 | -0.24833 | 0.30003 | 0.26585 | 0.25952 | 0.37223 | -0.58178 | -0.54127 | -0.58811 | -0.5476
1060.4844 | 121.6095 | -0.38452 | 121.2891 | -0.17574 | -0.31525 | -0.22262 | -0.28141 | -0.17432 | -0.21201 | -0.33283 | -0.33668 | -0.20925 | -0.33386 | -0.30784 | 0.24968 | 0.22008 | 0.21833 | 0.33104 | -0.12997 | -0.26947 | -0.17684 | -0.23564 | -0.12855 | -0.16624 | -0.28705 | -0.29091 | -0.16347 | -0.28808 | -0.26207 | 0.29545 | 0.26585 | 0.2641 | 0.37681 | -0.58636 | -0.55501 | -0.58353 | -0.55218
1062.2812 | 121.7697 | -0.34332 | 121.2433 | -0.17117 | -0.31983 | -0.22262 | -0.28599 | -0.19263 | -0.21201 | -0.33741 | -0.32753 | -0.21383 | -0.33386 | -0.30326 | 0.24968 | 0.22465 | 0.22748 | 0.34019 | -0.12539 | -0.27405 | -0.17684 | -0.24022 | -0.14686 | -0.16624 | -0.29163 | -0.28175 | -0.16805 | -0.28808 | -0.25749 | 0.29545 | 0.27043 | 0.27326 | 0.38597 | -0.5772 | -0.55501 | -0.58353 | -0.56134
1064.0625 | 121.6919 | -0.33875 | 121.2616 | -0.16659 | -0.31067 | -0.20888 | -0.27683 | -0.18348 | -0.20286 | -0.32825 | -0.33211 | -0.20925 | -0.32928 | -0.29411 | 0.24968 | 0.22465 | 0.21833 | 0.33561 | -0.12081 | -0.26489 | -0.1631 | -0.23106 | -0.1377 | -0.15708 | -0.28248 | -0.28633 | -0.16347 | -0.2835 | -0.24833 | 0.29545 | 0.27043 | 0.2641 | 0.38139 | -0.58178 | -0.55043 | -0.57895 | -0.5476
1065.8438 | 121.6095 | -0.39368 | 121.3028 | -0.15743 | -0.30151 | -0.20888 | -0.2631 | -0.16974 | -0.18454 | -0.32367 | -0.32753 | -0.20925 | -0.32928 | -0.28953 | 0.24052 | 0.2155 | 0.21833 | 0.3173 | -0.11165 | -0.25574 | -0.1631 | -0.21732 | -0.12397 | -0.13877 | -0.2779 | -0.28175 | -0.16347 | -0.2835 | -0.24375 | 0.2863 | 0.26127 | 0.2641 | 0.36308 | -0.56805 | -0.54585 | -0.5698 | -0.5476
1067.5312 | 121.6141 | -0.37994 | 121.2936 | -0.15285 | -0.30151 | -0.19972 | -0.26768 | -0.16517 | -0.1937 | -0.32367 | -0.32295 | -0.21383 | -0.32012 | -0.29411 | 0.23594 | 0.2155 | 0.21375 | 0.3173 | -0.10708 | -0.25574 | -0.15395 | -0.2219 | -0.11939 | -0.14792 | -0.2779 | -0.27717 | -0.16805 | -0.27435 | -0.24833 | 0.28172 | 0.26127 | 0.25952 | 0.36308 | -0.55889 | -0.5367 | -0.55606 | -0.53387
1069.2969 | 121.7468 | -0.3067 | 121.2479 | -0.14827 | -0.28778 | -0.19972 | -0.25852 | -0.16974 | -0.18912 | -0.31452 | -0.33211 | -0.21383 | -0.31554 | -0.28953 | 0.23594 | 0.20634 | 0.21375 | 0.3173 | -0.1025 | -0.242 | -0.15395 | -0.21274 | -0.12397 | -0.14334 | -0.26874 | -0.28633 | -0.16805 | -0.26977 | -0.24375 | 0.28172 | 0.25212 | 0.25952 | 0.36308 | -0.56805 | -0.54585 | -0.55148 | -0.52929
1071.0781 | 121.7606 | -0.33417 | 121.257 | -0.14827 | -0.29236 | -0.19972 | -0.25852 | -0.16517 | -0.17996 | -0.30994 | -0.32753 | -0.20467 | -0.31096 | -0.28037 | 0.23594 | 0.21092 | 0.20917 | 0.3173 | -0.1025 | -0.24658 | -0.15395 | -0.21274 | -0.11939 | -0.13419 | -0.26416 | -0.28175 | -0.15889 | -0.26519 | -0.23459 | 0.28172 | 0.2567 | 0.25495 | 0.36308 | -0.56347 | -0.5367 | -0.5469 | -0.52013
1072.7969 | 121.7514 | -0.31586 | 121.2524 | -0.14827 | -0.2832 | -0.19514 | -0.25394 | -0.16059 | -0.18912 | -0.3191 | -0.32753 | -0.20925 | -0.31554 | -0.28495 | 0.23594 | 0.21092 | 0.21375 | 0.3173 | -0.1025 | -0.23742 | -0.14937 | -0.20817 | -0.11481 | -0.14334 | -0.27332 | -0.28175 | -0.16347 | -0.26977 | -0.23917 | 0.28172 | 0.2567 | 0.25952 | 0.36308 | -0.56347 | -0.54127 | -0.55148 | -0.52929
1074.5 | 121.6461 | -0.35706 | 121.2662 | -0.14827 | -0.28778 | -0.19057 | -0.25394 | -0.16059 | -0.18912 | -0.30994 | -0.32295 | -0.20925 | -0.31096 | -0.28037 | 0.23136 | 0.20634 | 0.20917 | 0.3173 | -0.1025 | -0.242 | -0.14479 | -0.20817 | -0.11481 | -0.14334 | -0.26416 | -0.27717 | -0.16347 | -0.26519 | -0.23459 | 0.27714 | 0.25212 | 0.25495 | 0.36308 | -0.55431 | -0.53212 | -0.54233 | -0.52013
1076.2812 | 121.7148 | -0.33417 | 121.2616 | -0.13454 | -0.27404 | -0.19057 | -0.24936 | -0.14685 | -0.17539 | -0.30536 | -0.32753 | -0.21383 | -0.31554 | -0.28037 | 0.23136 | 0.20634 | 0.20001 | 0.3173 | -0.088763 | -0.22826 | -0.14479 | -0.20359 | -0.10108 | -0.12961 | -0.25958 | -0.28175 | -0.16805 | -0.26977 | -0.23459 | 0.27714 | 0.25212 | 0.24579 | 0.36308 | -0.55889 | -0.52754 | -0.5469 | -0.51555
1078.0469 | 121.7285 | -0.31128 | 121.2479 | -0.12538 | -0.27404 | -0.19057 | -0.24936 | -0.15601 | -0.17996 | -0.31452 | -0.32753 | -0.20925 | -0.31096 | -0.28495 | 0.22678 | 0.20176 | 0.20459 | 0.3173 | -0.079606 | -0.22826 | -0.14479 | -0.20359 | -0.11023 | -0.13419 | -0.26874 | -0.28175 | -0.16347 | -0.26519 | -0.23917 | 0.27256 | 0.24754 | 0.25037 | 0.36308 | -0.55431 | -0.53212 | -0.53775 | -0.51556
1079.8281 | 121.6919 | -0.32501 | 121.2708 | -0.12538 | -0.27862 | -0.19057 | -0.25394 | -0.15143 | -0.17081 | -0.29163 | -0.32295 | -0.20467 | -0.31554 | -0.28037 | 0.22678 | 0.20176 | 0.20459 | 0.3173 | -0.079606 | -0.23284 | -0.14479 | -0.20817 | -0.10566 | -0.12503 | -0.24585 | -0.27717 | -0.15889 | -0.26977 | -0.23459 | 0.27256 | 0.24754 | 0.25037 | 0.36308 | -0.54973 | -0.52754 | -0.54233 | -0.52013
1081.5156 | 121.7239 | -0.32044 | 121.2616 | -0.13912 | -0.2832 | -0.18599 | -0.24936 | -0.15143 | -0.18454 | -0.30078 | -0.32753 | -0.20467 | -0.31554 | -0.27121 | 0.22678 | 0.20176 | 0.20001 | 0.31272 | -0.093341 | -0.23742 | -0.14021 | -0.20359 | -0.10566 | -0.13877 | -0.25501 | -0.28175 | -0.15889 | -0.26977 | -0.22543 | 0.27256 | 0.24754 | 0.24579 | 0.3585 | -0.55431 | -0.52754 | -0.54233 | -0.51555
1083.2969 | 121.6324 | -0.36621 | 121.2936 | -0.13454 | -0.2832 | -0.18141 | -0.24479 | -0.16059 | -0.17539 | -0.30078 | -0.31837 | -0.20467 | -0.31554 | -0.27579 | 0.21763 | 0.20176 | 0.20459 | 0.31272 | -0.088763 | -0.23742 | -0.13563 | -0.19901 | -0.11481 | -0.12961 | -0.25501 | -0.27259 | -0.15889 | -0.26977 | -0.23001 | 0.2634 | 0.24754 | 0.25037 | 0.3585 | -0.536 | -0.52296 | -0.53317 | -0.52013
1085.0781 | 121.6965 | -0.31586 | 121.2799 | -0.12996 | -0.27862 | -0.18599 | -0.24021 | -0.14685 | -0.17539 | -0.30078 | -0.31379 | -0.21383 | -0.30639 | -0.27579 | 0.22221 | 0.20176 | 0.20001 | 0.30357 | -0.084184 | -0.23284 | -0.14021 | -0.19443 | -0.10108 | -0.12961 | -0.25501 | -0.26802 | -0.16805 | -0.26061 | -0.23001 | 0.26798 | 0.24754 | 0.24579 | 0.34934 | -0.536 | -0.51381 | -0.52859 | -0.5064
1086.8594 | 121.7285 | -0.31128 | 121.2799 | -0.1208 | -0.26488 | -0.17683 | -0.23563 | -0.1377 | -0.16165 | -0.28705 | -0.32295 | -0.20467 | -0.30639 | -0.27579 | 0.21763 | 0.19261 | 0.19086 | 0.30357 | -0.075028 | -0.21911 | -0.13105 | -0.18985 | -0.091922 | -0.11587 | -0.24127 | -0.27717 | -0.15889 | -0.26061 | -0.23001 | 0.2634 | 0.23838 | 0.23663 | 0.34934 | -0.54058 | -0.51381 | -0.52401 | -0.49724
1088.5625 | 121.7285 | -0.30212 | 121.2799 | -0.1208 | -0.26946 | -0.17683 | -0.23563 | -0.1377 | -0.16165 | -0.29163 | -0.31837 | -0.20009 | -0.30639 | -0.26663 | 0.22221 | 0.18803 | 0.20001 | 0.30357 | -0.075028 | -0.22369 | -0.13105 | -0.18985 | -0.091922 | -0.11587 | -0.24585 | -0.27259 | -0.15431 | -0.26061 | -0.22086 | 0.26798 | 0.23381 | 0.24579 | 0.34934 | -0.54058 | -0.51838 | -0.52859 | -0.5064
1090.3438 | 121.7148 | -0.31128 | 121.2845 | -0.11622 | -0.26946 | -0.17683 | -0.23563 | -0.13312 | -0.16165 | -0.28705 | -0.32295 | -0.20925 | -0.30639 | -0.26663 | 0.21305 | 0.18803 | 0.19086 | 0.30814 | -0.070449 | -0.22369 | -0.13105 | -0.18985 | -0.087344 | -0.11587 | -0.24127 | -0.27717 | -0.16347 | -0.26061 | -0.22086 | 0.25883 | 0.23381 | 0.23663 | 0.35392 | -0.536 | -0.51381 | -0.51944 | -0.49724
1092.0469 | 121.7377 | -0.32044 | 121.2708 | -0.12538 | -0.27404 | -0.17225 | -0.23105 | -0.12854 | -0.16623 | -0.2962 | -0.32295 | -0.20009 | -0.29265 | -0.26663 | 0.21305 | 0.19261 | 0.20001 | 0.30357 | -0.079606 | -0.22826 | -0.12648 | -0.18527 | -0.082766 | -0.12045 | -0.25043 | -0.27717 | -0.15431 | -0.24688 | -0.22086 | 0.25883 | 0.23838 | 0.24579 | 0.34934 | -0.536 | -0.52296 | -0.5057 | -0.49266
1093.8281 | 121.7331 | -0.28381 | 121.2524 | -0.1208 | -0.2603 | -0.17683 | -0.23105 | -0.14685 | -0.16623 | -0.29163 | -0.31837 | -0.20467 | -0.30181 | -0.26663 | 0.21763 | 0.18803 | 0.19086 | 0.29899 | -0.075028 | -0.21453 | -0.13105 | -0.18527 | -0.10108 | -0.12045 | -0.24585 | -0.27259 | -0.15889 | -0.25603 | -0.22086 | 0.2634 | 0.23381 | 0.23663 | 0.34476 | -0.536 | -0.50923 | -0.51944 | -0.49267
1095.5938 | 121.6049 | -0.34332 | 121.3303 | -0.1208 | -0.25115 | -0.16767 | -0.23105 | -0.13312 | -0.15707 | -0.27331 | -0.31837 | -0.20467 | -0.29723 | -0.25747 | 0.19931 | 0.18345 | 0.18628 | 0.29899 | -0.075028 | -0.20537 | -0.1219 | -0.18527 | -0.087344 | -0.1113 | -0.22754 | -0.27259 | -0.15889 | -0.25145 | -0.2117 | 0.24509 | 0.22923 | 0.23205 | 0.34476 | -0.51768 | -0.50465 | -0.49654 | -0.48351
1097.3125 | 121.7377 | -0.29297 | 121.2799 | -0.10707 | -0.2603 | -0.16309 | -0.22189 | -0.1377 | -0.15707 | -0.27789 | -0.32295 | -0.20467 | -0.29265 | -0.26205 | 0.21305 | 0.17887 | 0.19086 | 0.29899 | -0.061292 | -0.21453 | -0.11732 | -0.17612 | -0.091922 | -0.1113 | -0.23212 | -0.27717 | -0.15889 | -0.24688 | -0.21628 | 0.25883 | 0.22465 | 0.23663 | 0.34476 | -0.536 | -0.51381 | -0.5057 | -0.48351
1099.0938 | 121.6003 | -0.33875 | 121.3074 | -0.11165 | -0.25115 | -0.16309 | -0.23105 | -0.12854 | -0.15249 | -0.27789 | -0.32295 | -0.20009 | -0.29265 | -0.26205 | 0.20847 | 0.1743 | 0.18628 | 0.29899 | -0.065871 | -0.20537 | -0.11732 | -0.18527 | -0.082766 | -0.10672 | -0.23212 | -0.27717 | -0.15431 | -0.24688 | -0.21628 | 0.25425 | 0.22007 | 0.23205 | 0.34476 | -0.53142 | -0.50923 | -0.50112 | -0.47893
1100.8594 | 121.7285 | -0.31128 | 121.2982 | -0.10707 | -0.25572 | -0.16309 | -0.22647 | -0.12854 | -0.15707 | -0.27789 | -0.31837 | -0.20009 | -0.29723 | -0.26205 | 0.19931 | 0.1743 | 0.19543 | 0.29441 | -0.061292 | -0.20995 | -0.11732 | -0.18069 | -0.082766 | -0.1113 | -0.23212 | -0.27259 | -0.15431 | -0.25145 | -0.21628 | 0.24509 | 0.22007 | 0.24121 | 0.34019 | -0.51768 | -0.5138 | -0.49654 | -0.49266
1102.5781 | 121.6873 | -0.31586 | 121.312 | -0.097912 | -0.25115 | -0.16309 | -0.23105 | -0.12854 | -0.14334 | -0.27789 | -0.31379 | -0.20467 | -0.29723 | -0.25747 | 0.19931 | 0.18345 | 0.19543 | 0.30357 | -0.052136 | -0.20537 | -0.11732 | -0.18527 | -0.082766 | -0.097561 | -0.23212 | -0.26802 | -0.15889 | -0.25145 | -0.2117 | 0.24509 | 0.22923 | 0.24121 | 0.34934 | -0.51311 | -0.50923 | -0.49654 | -0.49266
1104.3594 | 121.7239 | -0.28381 | 121.2799 | -0.11165 | -0.25115 | -0.16767 | -0.22647 | -0.12854 | -0.15707 | -0.28247 | -0.31837 | -0.20009 | -0.29265 | -0.26663 | 0.20847 | 0.18803 | 0.17712 | 0.28983 | -0.065871 | -0.20537 | -0.1219 | -0.18069 | -0.082766 | -0.1113 | -0.23669 | -0.27259 | -0.15431 | -0.24688 | -0.22086 | 0.25425 | 0.23381 | 0.2229 | 0.33561 | -0.52684 | -0.49549 | -0.50112 | -0.46977
1106.125 | 121.6141 | -0.32959 | 121.3074 | -0.10249 | -0.25572 | -0.15394 | -0.22647 | -0.13312 | -0.15249 | -0.27331 | -0.31379 | -0.20467 | -0.29265 | -0.26205 | 0.20389 | 0.1743 | 0.18628 | 0.28525 | -0.056714 | -0.20995 | -0.10816 | -0.18069 | -0.087344 | -0.10672 | -0.22754 | -0.26802 | -0.15889 | -0.24688 | -0.21628 | 0.24967 | 0.22007 | 0.23205 | 0.33103 | -0.51769 | -0.50007 | -0.49655 | -0.47893
1107.8281 | 121.6003 | -0.33875 | 121.2982 | -0.10249 | -0.24657 | -0.15851 | -0.22647 | -0.12854 | -0.14334 | -0.27789 | -0.31379 | -0.20009 | -0.28807 | -0.25747 | 0.19931 | 0.1743 | 0.17712 | 0.28525 | -0.056714 | -0.20079 | -0.11274 | -0.18069 | -0.082766 | -0.097561 | -0.23212 | -0.26802 | -0.15431 | -0.2423 | -0.2117 | 0.24509 | 0.22007 | 0.2229 | 0.33103 | -0.51311 | -0.49091 | -0.48739 | -0.46519
1109.5781 | 121.6507 | -0.32501 | 121.2753 | -0.11165 | -0.25572 | -0.16309 | -0.23105 | -0.13312 | -0.15707 | -0.27331 | -0.31379 | -0.19551 | -0.29265 | -0.27121 | 0.20847 | 0.17887 | 0.1817 | 0.29441 | -0.065871 | -0.20995 | -0.11732 | -0.18527 | -0.087344 | -0.1113 | -0.22754 | -0.26802 | -0.14974 | -0.24688 | -0.22543 | 0.25425 | 0.22465 | 0.22748 | 0.34019 | -0.52226 | -0.49549 | -0.50112 | -0.47435
1111.3594 | 121.6919 | -0.32044 | 121.2845 | -0.10707 | -0.26488 | -0.16767 | -0.22189 | -0.12854 | -0.15707 | -0.28705 | -0.31379 | -0.20467 | -0.28807 | -0.26205 | 0.20847 | 0.17887 | 0.1817 | 0.29899 | -0.061292 | -0.21911 | -0.1219 | -0.17612 | -0.082766 | -0.1113 | -0.24127 | -0.26802 | -0.15889 | -0.2423 | -0.21628 | 0.25425 | 0.22465 | 0.22748 | 0.34476 | -0.52226 | -0.49549 | -0.49655 | -0.46977
1113.0781 | 121.7102 | -0.3067 | 121.2982 | -0.10707 | -0.25572 | -0.16309 | -0.23105 | -0.13312 | -0.15249 | -0.27789 | -0.32295 | -0.19551 | -0.29265 | -0.26205 | 0.20389 | 0.17887 | 0.17712 | 0.28525 | -0.061292 | -0.20995 | -0.11732 | -0.18527 | -0.087344 | -0.10672 | -0.23212 | -0.27717 | -0.14974 | -0.24688 | -0.21628 | 0.24967 | 0.22465 | 0.2229 | 0.33103 | -0.52684 | -0.50007 | -0.49655 | -0.46977
1114.8594 | 121.6461 | -0.31586 | 121.3165 | -0.11622 | -0.2603 | -0.16767 | -0.22189 | -0.13312 | -0.15249 | -0.28705 | -0.30921 | -0.19551 | -0.29265 | -0.26205 | 0.20389 | 0.17887 | 0.1817 | 0.28983 | -0.070449 | -0.21453 | -0.1219 | -0.17612 | -0.087344 | -0.10672 | -0.24127 | -0.26344 | -0.14974 | -0.24688 | -0.21628 | 0.24967 | 0.22465 | 0.22748 | 0.33561 | -0.51311 | -0.49091 | -0.49655 | -0.47435
1116.5469 | 121.5866 | -0.34332 | 121.3531 | -0.11165 | -0.2603 | -0.15851 | -0.22189 | -0.12854 | -0.15249 | -0.27789 | -0.32295 | -0.19093 | -0.28807 | -0.26663 | 0.21305 | 0.17887 | 0.17712 | 0.28983 | -0.065871 | -0.21453 | -0.11274 | -0.17612 | -0.082766 | -0.10672 | -0.23212 | -0.27717 | -0.14516 | -0.2423 | -0.22086 | 0.25883 | 0.22465 | 0.2229 | 0.33561 | -0.536 | -0.50007 | -0.50112 | -0.46519
1118.3125 | 121.701 | -0.31586 | 121.312 | -0.11165 | -0.25572 | -0.16309 | -0.22647 | -0.12854 | -0.15249 | -0.27331 | -0.31379 | -0.19093 | -0.29265 | -0.26205 | 0.20389 | 0.1743 | 0.17712 | 0.28983 | -0.065871 | -0.20995 | -0.11732 | -0.18069 | -0.082766 | -0.10672 | -0.22754 | -0.26802 | -0.14516 | -0.24688 | -0.21628 | 0.24967 | 0.22007 | 0.2229 | 0.33561 | -0.51769 | -0.49091 | -0.49655 | -0.46977
1120.0938 | 121.7377 | -0.27466 | 121.3028 | -0.11165 | -0.25115 | -0.16309 | -0.21731 | -0.12396 | -0.14334 | -0.26874 | -0.31379 | -0.20009 | -0.28807 | -0.25747 | 0.20847 | 0.18345 | 0.17712 | 0.28525 | -0.065871 | -0.20537 | -0.11732 | -0.17154 | -0.078188 | -0.097561 | -0.22296 | -0.26802 | -0.15431 | -0.2423 | -0.2117 | 0.25425 | 0.22923 | 0.2229 | 0.33103 | -0.52226 | -0.49091 | -0.49655 | -0.46519
1121.7969 | 121.6095 | -0.3479 | 121.3165 | -0.097912 | -0.24657 | -0.15394 | -0.21731 | -0.12396 | -0.14791 | -0.26874 | -0.31379 | -0.20009 | -0.28807 | -0.26205 | 0.19931 | 0.17887 | 0.16797 | 0.28525 | -0.052136 | -0.20079 | -0.10816 | -0.17154 | -0.078188 | -0.10214 | -0.22296 | -0.26802 | -0.15431 | -0.2423 | -0.21628 | 0.24509 | 0.22465 | 0.21374 | 0.33103 | -0.51311 | -0.48176 | -0.48739 | -0.45604
1123.5625 | 121.6141 | -0.32044 | 121.3531 | -0.097912 | -0.24657 | -0.15851 | -0.22647 | -0.11939 | -0.14334 | -0.27331 | -0.31379 | -0.19093 | -0.29265 | -0.25747 | 0.20389 | 0.17887 | 0.17254 | 0.2761 | -0.052136 | -0.20079 | -0.11274 | -0.18069 | -0.07361 | -0.097561 | -0.22754 | -0.26802 | -0.14516 | -0.24688 | -0.2117 | 0.24967 | 0.22465 | 0.21832 | 0.32187 | -0.51769 | -0.48634 | -0.49655 | -0.46519
1125.3438 | 121.7056 | -0.29297 | 121.3028 | -0.093333 | -0.25115 | -0.15851 | -0.21731 | -0.12396 | -0.14334 | -0.26874 | -0.31837 | -0.19551 | -0.29265 | -0.25747 | 0.20389 | 0.1743 | 0.16797 | 0.2761 | -0.047557 | -0.20537 | -0.11274 | -0.17154 | -0.078188 | -0.097561 | -0.22296 | -0.27259 | -0.14974 | -0.24688 | -0.2117 | 0.24967 | 0.22007 | 0.21374 | 0.32187 | -0.52226 | -0.48633 | -0.49655 | -0.46062
1127.0469 | 121.6873 | -0.29297 | 121.3028 | -0.097912 | -0.24657 | -0.15851 | -0.21731 | -0.12396 | -0.14334 | -0.27331 | -0.30921 | -0.20009 | -0.28807 | -0.25289 | 0.20389 | 0.1743 | 0.16797 | 0.2761 | -0.052136 | -0.20079 | -0.11274 | -0.17154 | -0.078188 | -0.097561 | -0.22754 | -0.26344 | -0.15431 | -0.2423 | -0.20712 | 0.24967 | 0.22007 | 0.21374 | 0.32187 | -0.51311 | -0.47718 | -0.49197 | -0.45604
1128.8281 | 121.7239 | -0.28381 | 121.3165 | -0.10249 | -0.23741 | -0.15394 | -0.21274 | -0.11939 | -0.14334 | -0.26874 | -0.30463 | -0.19551 | -0.29265 | -0.25747 | 0.19016 | 0.16514 | 0.16797 | 0.27152 | -0.056714 | -0.19163 | -0.10816 | -0.16696 | -0.07361 | -0.097561 | -0.22296 | -0.25886 | -0.14974 | -0.24688 | -0.2117 | 0.23594 | 0.21092 | 0.21374 | 0.31729 | -0.49479 | -0.4726 | -0.48281 | -0.46062
1130.5938 | 121.6324 | -0.31586 | 121.3394 | -0.097912 | -0.23741 | -0.15394 | -0.21731 | -0.11939 | -0.13876 | -0.26416 | -0.30463 | -0.19551 | -0.28807 | -0.25747 | 0.19931 | 0.1743 | 0.17254 | 0.26694 | -0.052136 | -0.19163 | -0.10816 | -0.17154 | -0.07361 | -0.092982 | -0.21838 | -0.25886 | -0.14974 | -0.2423 | -0.2117 | 0.24509 | 0.22007 | 0.21832 | 0.31272 | -0.50395 | -0.47718 | -0.48739 | -0.46062
1132.375 | 121.6324 | -0.34332 | 121.3303 | -0.097912 | -0.24199 | -0.15394 | -0.21731 | -0.11939 | -0.13876 | -0.26416 | -0.30463 | -0.19551 | -0.27892 | -0.25289 | 0.19474 | 0.1743 | 0.15881 | 0.27152 | -0.052136 | -0.19621 | -0.10816 | -0.17154 | -0.07361 | -0.092982 | -0.21838 | -0.25886 | -0.14974 | -0.23314 | -0.20712 | 0.24051 | 0.22007 | 0.20458 | 0.31729 | -0.49937 | -0.46344 | -0.47365 | -0.43772
1134.0781 | 121.7102 | -0.27924 | 121.2936 | -0.097912 | -0.23283 | -0.14478 | -0.21731 | -0.11939 | -0.14334 | -0.27789 | -0.31379 | -0.19093 | -0.28807 | -0.24374 | 0.19474 | 0.1743 | 0.16339 | 0.26236 | -0.052136 | -0.18706 | -0.099003 | -0.17154 | -0.07361 | -0.097561 | -0.23212 | -0.26802 | -0.14516 | -0.2423 | -0.19796 | 0.24051 | 0.22007 | 0.20916 | 0.30814 | -0.50853 | -0.47718 | -0.48281 | -0.45146
1135.8438 | 121.6187 | -0.33417 | 121.3348 | -0.10707 | -0.24199 | -0.14936 | -0.21274 | -0.11939 | -0.15249 | -0.26874 | -0.30921 | -0.19093 | -0.27892 | -0.24832 | 0.19016 | 0.1743 | 0.15881 | 0.2761 | -0.061292 | -0.19621 | -0.10358 | -0.16696 | -0.07361 | -0.10672 | -0.22296 | -0.26344 | -0.14516 | -0.23314 | -0.20254 | 0.23594 | 0.22007 | 0.20458 | 0.32187 | -0.49937 | -0.46802 | -0.46908 | -0.43772
1137.6094 | 121.7422 | -0.27924 | 121.3165 | -0.10249 | -0.24199 | -0.14936 | -0.22189 | -0.11939 | -0.14334 | -0.27331 | -0.30921 | -0.18635 | -0.27892 | -0.25289 | 0.19016 | 0.16972 | 0.16339 | 0.26694 | -0.056714 | -0.19621 | -0.10358 | -0.17612 | -0.07361 | -0.097561 | -0.22754 | -0.26344 | -0.14058 | -0.23314 | -0.20712 | 0.23594 | 0.21549 | 0.20916 | 0.31272 | -0.49937 | -0.4726 | -0.46908 | -0.4423
1139.3906 | 121.6873 | -0.29297 | 121.3348 | -0.093333 | -0.24199 | -0.14478 | -0.20816 | -0.11023 | -0.13876 | -0.25958 | -0.30921 | -0.19093 | -0.28349 | -0.24374 | 0.19016 | 0.16514 | 0.15423 | 0.27152 | -0.047557 | -0.19621 | -0.099003 | -0.16238 | -0.064454 | -0.092982 | -0.2138 | -0.26344 | -0.14516 | -0.23772 | -0.19796 | 0.23594 | 0.21092 | 0.2 | 0.31729 | -0.49937 | -0.46344 | -0.47365 | -0.43772
1141.1719 | 121.7377 | -0.2655 | 121.3165 | -0.097912 | -0.24657 | -0.14936 | -0.21274 | -0.11481 | -0.13876 | -0.26416 | -0.30921 | -0.19093 | -0.28349 | -0.24832 | 0.17642 | 0.16514 | 0.15423 | 0.26236 | -0.052136 | -0.20079 | -0.10358 | -0.16696 | -0.069032 | -0.092982 | -0.21838 | -0.26344 | -0.14516 | -0.23772 | -0.20254 | 0.2222 | 0.21092 | 0.2 | 0.30814 | -0.48564 | -0.46344 | -0.45992 | -0.43772
1142.9531 | 121.6507 | -0.31128 | 121.3577 | -0.093333 | -0.23283 | -0.14478 | -0.20816 | -0.12396 | -0.13876 | -0.27331 | -0.30463 | -0.19551 | -0.27434 | -0.24374 | 0.18558 | 0.16056 | 0.15423 | 0.26694 | -0.047557 | -0.18706 | -0.099003 | -0.16238 | -0.078188 | -0.092982 | -0.22754 | -0.25886 | -0.14974 | -0.22856 | -0.19796 | 0.23136 | 0.20634 | 0.2 | 0.31272 | -0.49022 | -0.45886 | -0.45992 | -0.42857
1144.6562 | 121.6644 | -0.30212 | 121.3394 | -0.093333 | -0.22825 | -0.15394 | -0.20816 | -0.11023 | -0.13418 | -0.27331 | -0.30463 | -0.19551 | -0.27892 | -0.23916 | 0.19016 | 0.16514 | 0.15423 | 0.26236 | -0.047557 | -0.18248 | -0.10816 | -0.16238 | -0.064454 | -0.088404 | -0.22754 | -0.25886 | -0.14974 | -0.23314 | -0.19338 | 0.23594 | 0.21092 | 0.2 | 0.30814 | -0.49479 | -0.45886 | -0.46908 | -0.43315
1146.4219 | 121.7148 | -0.29755 | 121.3165 | -0.097912 | -0.22367 | -0.14478 | -0.21274 | -0.11481 | -0.13418 | -0.25958 | -0.31379 | -0.19093 | -0.27434 | -0.24832 | 0.19016 | 0.16514 | 0.14965 | 0.25778 | -0.052136 | -0.1779 | -0.099003 | -0.16696 | -0.069032 | -0.088404 | -0.2138 | -0.26802 | -0.14516 | -0.22856 | -0.20254 | 0.23594 | 0.21092 | 0.19543 | 0.30356 | -0.50395 | -0.46344 | -0.4645 | -0.42399
1148.2031 | 121.6049 | -0.31128 | 121.3303 | -0.093333 | -0.23283 | -0.14478 | -0.20358 | -0.11481 | -0.1296 | -0.255 | -0.30921 | -0.19551 | -0.26976 | -0.24832 | 0.19016 | 0.16514 | 0.14965 | 0.25321 | -0.047557 | -0.18706 | -0.099003 | -0.1578 | -0.069032 | -0.083825 | -0.20922 | -0.26344 | -0.14974 | -0.22398 | -0.20254 | 0.23594 | 0.21092 | 0.19543 | 0.29898 | -0.49937 | -0.45886 | -0.45992 | -0.41941
1149.9688 | 121.7422 | -0.27008 | 121.344 | -0.097912 | -0.23283 | -0.14936 | -0.21274 | -0.11481 | -0.13418 | -0.255 | -0.30921 | -0.18635 | -0.27434 | -0.24374 | 0.19016 | 0.16514 | 0.15423 | 0.25778 | -0.052136 | -0.18706 | -0.10358 | -0.16696 | -0.069032 | -0.088404 | -0.20922 | -0.26344 | -0.14058 | -0.22856 | -0.19796 | 0.23594 | 0.21092 | 0.2 | 0.30356 | -0.49937 | -0.46344 | -0.4645 | -0.42857
1151.6719 | 121.6919 | -0.27466 | 121.3348 | -0.084176 | -0.22825 | -0.15851 | -0.20358 | -0.11023 | -0.13418 | -0.25958 | -0.30463 | -0.19093 | -0.27434 | -0.23916 | 0.18558 | 0.16514 | 0.14965 | 0.26236 | -0.0384 | -0.18248 | -0.11274 | -0.1578 | -0.064454 | -0.088404 | -0.2138 | -0.25886 | -0.14516 | -0.22856 | -0.19338 | 0.23136 | 0.21092 | 0.19543 | 0.30814 | -0.49022 | -0.45429 | -0.45992 | -0.42399
1153.4375 | 121.6919 | -0.25177 | 121.3028 | -0.088755 | -0.22825 | -0.15394 | -0.21274 | -0.11023 | -0.13876 | -0.26416 | -0.30921 | -0.19093 | -0.26976 | -0.23916 | 0.19016 | 0.16972 | 0.14049 | 0.25778 | -0.042979 | -0.18248 | -0.10816 | -0.16696 | -0.064454 | -0.092982 | -0.21838 | -0.26344 | -0.14516 | -0.22398 | -0.19338 | 0.23594 | 0.21549 | 0.18627 | 0.30356 | -0.49937 | -0.44971 | -0.45992 | -0.41025
1155.1719 | 121.756 | -0.27008 | 121.3211 | -0.093333 | -0.22367 | -0.14478 | -0.20358 | -0.10565 | -0.13418 | -0.25958 | -0.30463 | -0.19093 | -0.26976 | -0.23458 | 0.18558 | 0.16056 | 0.15423 | 0.25321 | -0.047557 | -0.1779 | -0.099003 | -0.1578 | -0.059876 | -0.088404 | -0.2138 | -0.25886 | -0.14516 | -0.22398 | -0.1888 | 0.23136 | 0.20634 | 0.2 | 0.29898 | -0.49022 | -0.45886 | -0.45534 | -0.42399
1156.9531 | 121.6919 | -0.27008 | 121.3348 | -0.093333 | -0.22825 | -0.1402 | -0.20816 | -0.11023 | -0.13876 | -0.26416 | -0.30463 | -0.18635 | -0.27434 | -0.23916 | 0.181 | 0.15598 | 0.14049 | 0.25321 | -0.047557 | -0.18248 | -0.094424 | -0.16238 | -0.064454 | -0.092982 | -0.21838 | -0.25886 | -0.14058 | -0.22856 | -0.19338 | 0.22678 | 0.20176 | 0.18627 | 0.29898 | -0.48564 | -0.44513 | -0.45534 | -0.41483
1158.7188 | 121.7331 | -0.23346 | 121.312 | -0.079598 | -0.2191 | -0.14478 | -0.20816 | -0.11023 | -0.13418 | -0.25958 | -0.30463 | -0.19093 | -0.27434 | -0.23458 | 0.18558 | 0.16056 | 0.14965 | 0.24863 | -0.033822 | -0.17332 | -0.099003 | -0.16238 | -0.064454 | -0.088404 | -0.2138 | -0.25886 | -0.14516 | -0.22856 | -0.1888 | 0.23136 | 0.20634 | 0.19543 | 0.2944 | -0.49022 | -0.45429 | -0.45992 | -0.42399
1160.4219 | 121.7239 | -0.25177 | 121.3165 | -0.088755 | -0.21452 | -0.14936 | -0.20816 | -0.11023 | -0.1296 | -0.25958 | -0.30006 | -0.19551 | -0.27434 | -0.23916 | 0.17642 | 0.15598 | 0.14965 | 0.25321 | -0.042979 | -0.16874 | -0.10358 | -0.16238 | -0.064454 | -0.083825 | -0.2138 | -0.25428 | -0.14974 | -0.22856 | -0.19338 | 0.2222 | 0.20176 | 0.19543 | 0.29898 | -0.47648 | -0.44971 | -0.45076 | -0.42399
1162.2031 | 121.7422 | -0.26093 | 121.344 | -0.088755 | -0.2191 | -0.14478 | -0.21274 | -0.10565 | -0.1296 | -0.255 | -0.30921 | -0.19551 | -0.26976 | -0.23916 | 0.18558 | 0.16056 | 0.14507 | 0.25778 | -0.042979 | -0.17332 | -0.099003 | -0.16696 | -0.059876 | -0.083825 | -0.20922 | -0.26344 | -0.14974 | -0.22398 | -0.19338 | 0.23136 | 0.20634 | 0.19085 | 0.30356 | -0.49479 | -0.45429 | -0.45534 | -0.41483
1163.9688 | 121.6049 | -0.30212 | 121.3806 | -0.084176 | -0.20994 | -0.15394 | -0.20358 | -0.10107 | -0.1296 | -0.25958 | -0.29548 | -0.19551 | -0.26976 | -0.23916 | 0.181 | 0.16056 | 0.14049 | 0.25321 | -0.0384 | -0.16416 | -0.10816 | -0.1578 | -0.055298 | -0.083825 | -0.2138 | -0.2497 | -0.14974 | -0.22398 | -0.19338 | 0.22678 | 0.20634 | 0.18627 | 0.29898 | -0.47648 | -0.43597 | -0.45076 | -0.41025
1165.7344 | 121.7239 | -0.25635 | 121.3211 | -0.093333 | -0.22367 | -0.1402 | -0.20358 | -0.11023 | -0.1296 | -0.255 | -0.30463 | -0.19093 | -0.27434 | -0.24374 | 0.18558 | 0.15598 | 0.14965 | 0.25321 | -0.047557 | -0.1779 | -0.094424 | -0.1578 | -0.064454 | -0.083825 | -0.20922 | -0.25886 | -0.14516 | -0.22856 | -0.19796 | 0.23136 | 0.20176 | 0.19543 | 0.29898 | -0.49022 | -0.45429 | -0.45992 | -0.42399
1167.4844 | 121.637 | -0.28381 | 121.3715 | -0.079598 | -0.20994 | -0.13562 | -0.19442 | -0.10565 | -0.1296 | -0.25958 | -0.30463 | -0.18635 | -0.27434 | -0.23458 | 0.181 | 0.15141 | 0.14965 | 0.24863 | -0.033822 | -0.16416 | -0.089846 | -0.14865 | -0.059876 | -0.083825 | -0.2138 | -0.25886 | -0.14058 | -0.22856 | -0.1888 | 0.22678 | 0.19718 | 0.19543 | 0.2944 | -0.48564 | -0.45429 | -0.45534 | -0.42399
1169.1875 | 121.6232 | -0.30212 | 121.3669 | -0.088755 | -0.20994 | -0.1402 | -0.199 | -0.10565 | -0.12502 | -0.255 | -0.30463 | -0.19093 | -0.26976 | -0.23 | 0.181 | 0.14683 | 0.14507 | 0.24405 | -0.042979 | -0.16416 | -0.094424 | -0.15322 | -0.059876 | -0.079247 | -0.20922 | -0.25886 | -0.14516 | -0.22398 | -0.18422 | 0.22678 | 0.1926 | 0.19085 | 0.28983 | -0.48564 | -0.44971 | -0.45076 | -0.41483
1170.9531 | 121.701 | -0.2655 | 121.3577 | -0.079598 | -0.20994 | -0.13104 | -0.18984 | -0.10107 | -0.12502 | -0.24584 | -0.30921 | -0.18177 | -0.2606 | -0.23 | 0.181 | 0.15141 | 0.14507 | 0.25321 | -0.033822 | -0.16416 | -0.085267 | -0.14407 | -0.055298 | -0.079247 | -0.20007 | -0.26344 | -0.136 | -0.21483 | -0.18422 | 0.22678 | 0.19718 | 0.19085 | 0.29898 | -0.49022 | -0.45429 | -0.44161 | -0.40568
1172.7188 | 121.7285 | -0.25177 | 121.3257 | -0.088755 | -0.20536 | -0.14936 | -0.199 | -0.10565 | -0.12044 | -0.25042 | -0.30463 | -0.18635 | -0.26518 | -0.23 | 0.181 | 0.14225 | 0.13592 | 0.24405 | -0.042979 | -0.15958 | -0.10358 | -0.15322 | -0.059876 | -0.074669 | -0.20465 | -0.25886 | -0.14058 | -0.21941 | -0.18422 | 0.22678 | 0.18803 | 0.18169 | 0.28983 | -0.48564 | -0.44055 | -0.44618 | -0.4011
1174.4688 | 121.756 | -0.25635 | 121.3394 | -0.084176 | -0.20994 | -0.1402 | -0.19442 | -0.10565 | -0.12502 | -0.25042 | -0.31837 | -0.19093 | -0.26518 | -0.23 | 0.17642 | 0.14683 | 0.14507 | 0.24863 | -0.0384 | -0.16416 | -0.094424 | -0.14865 | -0.059876 | -0.079247 | -0.20465 | -0.27259 | -0.14516 | -0.21941 | -0.18422 | 0.2222 | 0.1926 | 0.19085 | 0.2944 | -0.49479 | -0.46344 | -0.44161 | -0.41025
1176.1719 | 121.6415 | -0.29755 | 121.3623 | -0.079598 | -0.21452 | -0.13562 | -0.199 | -0.10107 | -0.1296 | -0.24584 | -0.30921 | -0.19093 | -0.25603 | -0.23 | 0.17185 | 0.14683 | 0.14049 | 0.24405 | -0.033822 | -0.16874 | -0.089846 | -0.15322 | -0.055298 | -0.083825 | -0.20007 | -0.26344 | -0.14516 | -0.21025 | -0.18422 | 0.21762 | 0.1926 | 0.18627 | 0.28983 | -0.48106 | -0.44971 | -0.42787 | -0.39652
1177.9375 | 121.6461 | -0.28839 | 121.3531 | -0.088755 | -0.20994 | -0.14478 | -0.199 | -0.091918 | -0.1296 | -0.255 | -0.30463 | -0.19093 | -0.26518 | -0.22542 | 0.17185 | 0.14225 | 0.14049 | 0.24863 | -0.042979 | -0.16416 | -0.099003 | -0.15322 | -0.046142 | -0.083825 | -0.20922 | -0.25886 | -0.14516 | -0.21941 | -0.17964 | 0.21762 | 0.18803 | 0.18627 | 0.2944 | -0.47648 | -0.44513 | -0.43703 | -0.40568
1179.7188 | 121.6461 | -0.28839 | 121.3577 | -0.079598 | -0.20994 | -0.13104 | -0.18984 | -0.10107 | -0.12502 | -0.25042 | -0.30463 | -0.19093 | -0.2606 | -0.23 | 0.17185 | 0.14683 | 0.13592 | 0.24863 | -0.033822 | -0.16416 | -0.085267 | -0.14407 | -0.055298 | -0.079247 | -0.20465 | -0.25886 | -0.14516 | -0.21483 | -0.18422 | 0.21762 | 0.1926 | 0.18169 | 0.2944 | -0.47648 | -0.44055 | -0.43245 | -0.39652
1181.4062 | 121.6782 | -0.29755 | 121.3486 | -0.084176 | -0.20994 | -0.12646 | -0.19442 | -0.096496 | -0.11129 | -0.25042 | -0.30921 | -0.18635 | -0.2606 | -0.22542 | 0.16269 | 0.15141 | 0.13134 | 0.24405 | -0.0384 | -0.16416 | -0.080689 | -0.14865 | -0.05072 | -0.065512 | -0.20465 | -0.26344 | -0.14058 | -0.21483 | -0.17964 | 0.20847 | 0.19718 | 0.17711 | 0.28983 | -0.4719 | -0.44055 | -0.42329 | -0.39194
1183.1875 | 121.6507 | -0.27466 | 121.3989 | -0.084176 | -0.20994 | -0.13562 | -0.19442 | -0.091918 | -0.11129 | -0.25042 | -0.30921 | -0.19093 | -0.2606 | -0.22542 | 0.16727 | 0.13767 | 0.13592 | 0.23947 | -0.0384 | -0.16416 | -0.089846 | -0.14865 | -0.046142 | -0.065512 | -0.20465 | -0.26344 | -0.14516 | -0.21483 | -0.17964 | 0.21304 | 0.18345 | 0.18169 | 0.28525 | -0.47648 | -0.44513 | -0.42787 | -0.39652
1184.9531 | 121.5912 | -0.28381 | 121.4035 | -0.070441 | -0.1962 | -0.12189 | -0.19442 | -0.096496 | -0.12044 | -0.24584 | -0.31379 | -0.19093 | -0.25145 | -0.21626 | 0.16269 | 0.14225 | 0.13592 | 0.24863 | -0.024665 | -0.15042 | -0.07611 | -0.14865 | -0.05072 | -0.074669 | -0.20007 | -0.26802 | -0.14516 | -0.20567 | -0.17049 | 0.20847 | 0.18803 | 0.18169 | 0.2944 | -0.47648 | -0.44971 | -0.41414 | -0.38736
1186.6562 | 121.7377 | -0.2655 | 121.344 | -0.079598 | -0.20536 | -0.1402 | -0.18984 | -0.096496 | -0.12502 | -0.24584 | -0.30463 | -0.19093 | -0.25145 | -0.22542 | 0.15811 | 0.14683 | 0.13134 | 0.24405 | -0.033822 | -0.15958 | -0.094424 | -0.14407 | -0.05072 | -0.079247 | -0.20007 | -0.25886 | -0.14516 | -0.20567 | -0.17964 | 0.20389 | 0.1926 | 0.17711 | 0.28983 | -0.46275 | -0.43597 | -0.40956 | -0.38278
1188.4219 | 121.7468 | -0.25635 | 121.3577 | -0.07502 | -0.20078 | -0.13104 | -0.18984 | -0.096496 | -0.11587 | -0.25042 | -0.30921 | -0.19093 | -0.2606 | -0.22542 | 0.17642 | 0.14683 | 0.13592 | 0.23947 | -0.029244 | -0.155 | -0.085267 | -0.14407 | -0.05072 | -0.07009 | -0.20465 | -0.26344 | -0.14516 | -0.21483 | -0.17964 | 0.2222 | 0.1926 | 0.18169 | 0.28525 | -0.48564 | -0.44513 | -0.43703 | -0.39652
1190.125 | 121.6827 | -0.2655 | 121.3806 | -0.070441 | -0.20536 | -0.1402 | -0.19442 | -0.091918 | -0.11587 | -0.24584 | -0.30921 | -0.18635 | -0.25603 | -0.22542 | 0.16269 | 0.14225 | 0.13592 | 0.23947 | -0.024665 | -0.15958 | -0.094424 | -0.14865 | -0.046142 | -0.07009 | -0.20007 | -0.26344 | -0.14058 | -0.21025 | -0.17964 | 0.20847 | 0.18803 | 0.18169 | 0.28525 | -0.4719 | -0.44513 | -0.41872 | -0.39194
1191.8906 | 121.6187 | -0.29297 | 121.3852 | -0.07502 | -0.20078 | -0.12646 | -0.19442 | -0.096496 | -0.12502 | -0.24127 | -0.30463 | -0.19093 | -0.25603 | -0.23 | 0.16727 | 0.13767 | 0.13592 | 0.24405 | -0.029244 | -0.155 | -0.080689 | -0.14865 | -0.05072 | -0.079247 | -0.19549 | -0.25886 | -0.14516 | -0.21025 | -0.18422 | 0.21304 | 0.18345 | 0.18169 | 0.28983 | -0.4719 | -0.44055 | -0.42329 | -0.39194
1193.6562 | 121.6278 | -0.27924 | 121.3531 | -0.079598 | -0.20078 | -0.13562 | -0.19442 | -0.091918 | -0.12044 | -0.24127 | -0.30006 | -0.18635 | -0.25603 | -0.22542 | 0.16727 | 0.14225 | 0.13592 | 0.23489 | -0.033822 | -0.155 | -0.089846 | -0.14865 | -0.046142 | -0.074669 | -0.19549 | -0.25428 | -0.14058 | -0.21025 | -0.17964 | 0.21304 | 0.18803 | 0.18169 | 0.28067 | -0.46732 | -0.43597 | -0.42329 | -0.39194
1195.3594 | 121.6461 | -0.27466 | 121.3669 | -0.070441 | -0.1962 | -0.12646 | -0.19442 | -0.096496 | -0.11129 | -0.24127 | -0.30921 | -0.19551 | -0.25603 | -0.22542 | 0.16727 | 0.14683 | 0.13592 | 0.23947 | -0.024665 | -0.15042 | -0.080689 | -0.14865 | -0.05072 | -0.065512 | -0.19549 | -0.26344 | -0.14974 | -0.21025 | -0.17964 | 0.21304 | 0.1926 | 0.18169 | 0.28525 | -0.47648 | -0.44513 | -0.42329 | -0.39194
1197.125 | 121.7194 | -0.24719 | 121.3348 | -0.07502 | -0.20078 | -0.13104 | -0.18984 | -0.091918 | -0.12044 | -0.24584 | -0.29548 | -0.19093 | -0.25145 | -0.22542 | 0.17642 | 0.15141 | 0.13134 | 0.23489 | -0.029244 | -0.155 | -0.085267 | -0.14407 | -0.046142 | -0.074669 | -0.20007 | -0.2497 | -0.14516 | -0.20567 | -0.17964 | 0.2222 | 0.19718 | 0.17711 | 0.28067 | -0.4719 | -0.42682 | -0.42787 | -0.38278
1198.8438 | 121.7285 | -0.23346 | 121.3394 | -0.079598 | -0.20078 | -0.13104 | -0.18984 | -0.096496 | -0.12044 | -0.24584 | -0.30006 | -0.19551 | -0.2606 | -0.22542 | 0.16727 | 0.14683 | 0.13134 | 0.23489 | -0.033822 | -0.155 | -0.085267 | -0.14407 | -0.05072 | -0.074669 | -0.20007 | -0.25428 | -0.14974 | -0.21483 | -0.17964 | 0.21304 | 0.1926 | 0.17711 | 0.28067 | -0.46732 | -0.43139 | -0.42787 | -0.39194
1200.5625 | 121.7239 | -0.2243 | 121.3348 | -0.070441 | -0.20994 | -0.13562 | -0.18069 | -0.096496 | -0.11587 | -0.24127 | -0.30463 | -0.18635 | -0.25603 | -0.22084 | 0.15811 | 0.14683 | 0.13134 | 0.23031 | -0.024665 | -0.16416 | -0.089846 | -0.13491 | -0.05072 | -0.07009 | -0.19549 | -0.25886 | -0.14058 | -0.21025 | -0.17507 | 0.20389 | 0.1926 | 0.17711 | 0.27609 | -0.46275 | -0.43597 | -0.41414 | -0.38736
1202.3281 | 121.7239 | -0.25177 | 121.376 | -0.07502 | -0.20078 | -0.12646 | -0.19442 | -0.096496 | -0.11587 | -0.24584 | -0.30463 | -0.18177 | -0.25145 | -0.22084 | 0.17185 | 0.14225 | 0.13134 | 0.23031 | -0.029244 | -0.155 | -0.080689 | -0.14865 | -0.05072 | -0.07009 | -0.20007 | -0.25886 | -0.136 | -0.20567 | -0.17507 | 0.21762 | 0.18803 | 0.17711 | 0.27609 | -0.47648 | -0.43597 | -0.42329 | -0.38278
1204.0938 | 121.6919 | -0.23804 | 121.3623 | -0.070441 | -0.1962 | -0.12189 | -0.18984 | -0.082762 | -0.12502 | -0.24127 | -0.29548 | -0.18177 | -0.25145 | -0.22084 | 0.17185 | 0.14225 | 0.12218 | 0.23489 | -0.024665 | -0.15042 | -0.07611 | -0.14407 | -0.036986 | -0.079247 | -0.19549 | -0.2497 | -0.136 | -0.20567 | -0.17507 | 0.21762 | 0.18803 | 0.16796 | 0.28067 | -0.46732 | -0.41766 | -0.42329 | -0.37363
1205.7969 | 121.6049 | -0.27924 | 121.3852 | -0.070441 | -0.20078 | -0.12189 | -0.18526 | -0.08734 | -0.12044 | -0.23669 | -0.29548 | -0.18635 | -0.25145 | -0.22084 | 0.16727 | 0.14683 | 0.12218 | 0.23031 | -0.024665 | -0.155 | -0.07611 | -0.13949 | -0.041564 | -0.074669 | -0.19091 | -0.2497 | -0.14058 | -0.20567 | -0.17507 | 0.21304 | 0.1926 | 0.16796 | 0.27609 | -0.46275 | -0.41766 | -0.41871 | -0.37363
1207.5469 | 121.669 | -0.27008 | 121.3989 | -0.07502 | -0.19162 | -0.12646 | -0.18984 | -0.091918 | -0.11129 | -0.25042 | -0.30006 | -0.1772 | -0.25603 | -0.23 | 0.16269 | 0.14683 | 0.12676 | 0.23489 | -0.029244 | -0.14585 | -0.080689 | -0.14407 | -0.046142 | -0.065512 | -0.20465 | -0.25428 | -0.13142 | -0.21025 | -0.18422 | 0.20847 | 0.1926 | 0.17253 | 0.28067 | -0.46275 | -0.42681 | -0.41872 | -0.38278
1209.3281 | 121.7789 | -0.2243 | 121.3486 | -0.070441 | -0.20078 | -0.12646 | -0.18984 | -0.091918 | -0.11129 | -0.25042 | -0.30006 | -0.19093 | -0.25603 | -0.23 | 0.16269 | 0.14225 | 0.13134 | 0.23947 | -0.024665 | -0.155 | -0.080689 | -0.14407 | -0.046142 | -0.065512 | -0.20465 | -0.25428 | -0.14516 | -0.21025 | -0.18422 | 0.20847 | 0.18803 | 0.17711 | 0.28525 | -0.46275 | -0.43139 | -0.41872 | -0.38736
1211.0312 | 121.6782 | -0.24719 | 121.3715 | -0.07502 | -0.1962 | -0.13104 | -0.18526 | -0.091918 | -0.11129 | -0.24127 | -0.30463 | -0.18177 | -0.25603 | -0.22084 | 0.16269 | 0.13767 | 0.12676 | 0.23031 | -0.029244 | -0.15042 | -0.085267 | -0.13949 | -0.046142 | -0.065512 | -0.19549 | -0.25886 | -0.136 | -0.21025 | -0.17507 | 0.20847 | 0.18345 | 0.17253 | 0.27609 | -0.46732 | -0.43139 | -0.41872 | -0.38278
1212.7969 | 121.7285 | -0.2243 | 121.344 | -0.061284 | -0.19162 | -0.12189 | -0.18069 | -0.096496 | -0.11129 | -0.24127 | -0.30006 | -0.1772 | -0.24687 | -0.23 | 0.16269 | 0.14225 | 0.12676 | 0.23031 | -0.015508 | -0.14585 | -0.07611 | -0.13491 | -0.05072 | -0.065512 | -0.19549 | -0.25428 | -0.13142 | -0.20109 | -0.18422 | 0.20847 | 0.18803 | 0.17253 | 0.27609 | -0.46275 | -0.42681 | -0.40956 | -0.37363
1214.5 | 121.7422 | -0.21973 | 121.3623 | -0.061284 | -0.1962 | -0.12189 | -0.18984 | -0.091918 | -0.11129 | -0.24127 | -0.30006 | -0.18635 | -0.25603 | -0.21626 | 0.17185 | 0.14225 | 0.12218 | 0.23031 | -0.015508 | -0.15042 | -0.07611 | -0.14407 | -0.046142 | -0.065512 | -0.19549 | -0.25428 | -0.14058 | -0.21025 | -0.17049 | 0.21762 | 0.18803 | 0.16796 | 0.27609 | -0.4719 | -0.42224 | -0.42787 | -0.37821
1216.2656 | 121.6736 | -0.27924 | 121.3669 | -0.065863 | -0.18704 | -0.13104 | -0.18526 | -0.091918 | -0.11129 | -0.25042 | -0.30006 | -0.18635 | -0.25145 | -0.22542 | 0.17185 | 0.14225 | 0.12218 | 0.22116 | -0.020087 | -0.14127 | -0.085267 | -0.13949 | -0.046142 | -0.065512 | -0.20465 | -0.25428 | -0.14058 | -0.20567 | -0.17964 | 0.21762 | 0.18803 | 0.16796 | 0.26693 | -0.4719 | -0.42224 | -0.42329 | -0.37363
1217.9688 | 121.7056 | -0.26093 | 121.3623 | -0.070441 | -0.1962 | -0.12189 | -0.18526 | -0.096496 | -0.11129 | -0.23669 | -0.30006 | -0.19551 | -0.25603 | -0.22542 | 0.16269 | 0.14225 | 0.12676 | 0.23031 | -0.024665 | -0.15042 | -0.07611 | -0.13949 | -0.05072 | -0.065512 | -0.19091 | -0.25428 | -0.14974 | -0.21025 | -0.17964 | 0.20847 | 0.18803 | 0.17253 | 0.27609 | -0.46275 | -0.42681 | -0.41872 | -0.38278
1219.7344 | 121.7056 | -0.2655 | 121.3623 | -0.070441 | -0.19162 | -0.12646 | -0.18069 | -0.08734 | -0.11587 | -0.24127 | -0.30463 | -0.18177 | -0.25145 | -0.22542 | 0.16727 | 0.13767 | 0.12676 | 0.23031 | -0.024665 | -0.14585 | -0.080689 | -0.13491 | -0.041564 | -0.07009 | -0.19549 | -0.25886 | -0.136 | -0.20567 | -0.17964 | 0.21304 | 0.18345 | 0.17253 | 0.27609 | -0.4719 | -0.43139 | -0.41871 | -0.37821
1221.4844 | 121.701 | -0.25635 | 121.3394 | -0.070441 | -0.20078 | -0.13104 | -0.18526 | -0.096496 | -0.11129 | -0.24584 | -0.30463 | -0.18177 | -0.25603 | -0.22084 | 0.16727 | 0.13309 | 0.1176 | 0.23031 | -0.024665 | -0.155 | -0.085267 | -0.13949 | -0.05072 | -0.065512 | -0.20007 | -0.25886 | -0.136 | -0.21025 | -0.17507 | 0.21304 | 0.17887 | 0.16338 | 0.27609 | -0.4719 | -0.42224 | -0.42329 | -0.37363
1223.1875 | 121.6827 | -0.24719 | 121.3623 | -0.070441 | -0.1962 | -0.12646 | -0.18069 | -0.08734 | -0.11129 | -0.24127 | -0.30463 | -0.18635 | -0.2606 | -0.21626 | 0.16727 | 0.13767 | 0.12218 | 0.23489 | -0.024665 | -0.15042 | -0.080689 | -0.13491 | -0.041564 | -0.065512 | -0.19549 | -0.25886 | -0.14058 | -0.21483 | -0.17049 | 0.21304 | 0.18345 | 0.16796 | 0.28067 | -0.4719 | -0.42682 | -0.42787 | -0.38278
1224.9688 | 121.6736 | -0.25177 | 121.3531 | -0.07502 | -0.18704 | -0.12189 | -0.17611 | -0.08734 | -0.11129 | -0.24127 | -0.29548 | -0.18177 | -0.25603 | -0.22542 | 0.16269 | 0.14225 | 0.12218 | 0.22574 | -0.029244 | -0.14127 | -0.07611 | -0.13033 | -0.041564 | -0.065512 | -0.19549 | -0.2497 | -0.136 | -0.21025 | -0.17964 | 0.20847 | 0.18803 | 0.16796 | 0.27151 | -0.45817 | -0.41766 | -0.41872 | -0.37821
1226.7188 | 121.7606 | -0.24719 | 121.3303 | -0.061284 | -0.18246 | -0.12189 | -0.18069 | -0.078184 | -0.10671 | -0.23669 | -0.30463 | -0.18635 | -0.25603 | -0.22542 | 0.16269 | 0.13767 | 0.1176 | 0.23031 | -0.015508 | -0.13669 | -0.07611 | -0.13491 | -0.032408 | -0.060933 | -0.19091 | -0.25886 | -0.14058 | -0.21025 | -0.17964 | 0.20847 | 0.18345 | 0.16338 | 0.27609 | -0.46732 | -0.42224 | -0.41872 | -0.37363
1228.4688 | 121.701 | -0.24719 | 121.3623 | -0.061284 | -0.1962 | -0.12189 | -0.17611 | -0.082762 | -0.10671 | -0.22753 | -0.30006 | -0.19093 | -0.24687 | -0.21626 | 0.15811 | 0.13767 | 0.1176 | 0.22574 | -0.015508 | -0.15042 | -0.07611 | -0.13033 | -0.036986 | -0.060933 | -0.18176 | -0.25428 | -0.14516 | -0.20109 | -0.17049 | 0.20389 | 0.18345 | 0.16338 | 0.27151 | -0.45817 | -0.41766 | -0.40498 | -0.36447
1230.25 | 121.6965 | -0.2243 | 121.3394 | -0.056706 | -0.19162 | -0.12189 | -0.17611 | -0.078184 | -0.10671 | -0.23669 | -0.30463 | -0.18177 | -0.25145 | -0.21168 | 0.15353 | 0.12851 | 0.1176 | 0.22116 | -0.01093 | -0.14585 | -0.07611 | -0.13033 | -0.032408 | -0.060933 | -0.19091 | -0.25886 | -0.136 | -0.20567 | -0.16591 | 0.19931 | 0.17429 | 0.16338 | 0.26693 | -0.45817 | -0.42224 | -0.40498 | -0.36905
1232 | 121.6049 | -0.28839 | 121.3898 | -0.056706 | -0.19162 | -0.11731 | -0.18069 | -0.082762 | -0.10671 | -0.24127 | -0.29548 | -0.1772 | -0.25603 | -0.21626 | 0.16727 | 0.13309 | 0.1176 | 0.23489 | -0.01093 | -0.14585 | -0.071531 | -0.13491 | -0.036986 | -0.060933 | -0.19549 | -0.2497 | -0.13142 | -0.21025 | -0.17049 | 0.21304 | 0.17887 | 0.16338 | 0.28067 | -0.46275 | -0.41308 | -0.42329 | -0.37363
1233.7031 | 121.7743 | -0.24261 | 121.3303 | -0.061284 | -0.18704 | -0.12189 | -0.18069 | -0.078184 | -0.097553 | -0.23211 | -0.30006 | -0.18177 | -0.25145 | -0.21168 | 0.15353 | 0.13309 | 0.12676 | 0.22574 | -0.015508 | -0.14127 | -0.07611 | -0.13491 | -0.032408 | -0.051777 | -0.18633 | -0.25428 | -0.136 | -0.20567 | -0.16591 | 0.19931 | 0.17887 | 0.17253 | 0.27151 | -0.45359 | -0.42681 | -0.40498 | -0.37821
1235.4688 | 121.7606 | -0.22888 | 121.3531 | -0.061284 | -0.18704 | -0.11731 | -0.17153 | -0.078184 | -0.10213 | -0.22753 | -0.30006 | -0.18635 | -0.25603 | -0.21626 | 0.15353 | 0.13309 | 0.1176 | 0.23031 | -0.015508 | -0.14127 | -0.071531 | -0.12575 | -0.032408 | -0.056355 | -0.18176 | -0.25428 | -0.14058 | -0.21025 | -0.17049 | 0.19931 | 0.17887 | 0.16338 | 0.27609 | -0.45359 | -0.41766 | -0.40956 | -0.37363
1237.1719 | 121.6095 | -0.27008 | 121.4172 | -0.056706 | -0.1962 | -0.10815 | -0.18069 | -0.082762 | -0.10213 | -0.23211 | -0.30463 | -0.18635 | -0.25603 | -0.22542 | 0.15811 | 0.13767 | 0.1176 | 0.22574 | -0.01093 | -0.15042 | -0.062374 | -0.13491 | -0.036986 | -0.056355 | -0.18633 | -0.25886 | -0.14058 | -0.21025 | -0.17964 | 0.20389 | 0.18345 | 0.16338 | 0.27151 | -0.46275 | -0.42224 | -0.41414 | -0.37363
1238.9375 | 121.701 | -0.24261 | 121.3623 | -0.061284 | -0.18246 | -0.11731 | -0.18069 | -0.073606 | -0.10213 | -0.23211 | -0.30463 | -0.18177 | -0.24687 | -0.21626 | 0.15811 | 0.13309 | 0.1176 | 0.22574 | -0.015508 | -0.13669 | -0.071531 | -0.13491 | -0.02783 | -0.056355 | -0.18633 | -0.25886 | -0.136 | -0.20109 | -0.17049 | 0.20389 | 0.17887 | 0.16338 | 0.27151 | -0.46275 | -0.42224 | -0.40498 | -0.36447
1240.7188 | 121.5958 | -0.28839 | 121.3943 | -0.065863 | -0.19162 | -0.12189 | -0.18069 | -0.082762 | -0.11129 | -0.23211 | -0.30921 | -0.18177 | -0.24687 | -0.22084 | 0.15353 | 0.13767 | 0.13134 | 0.23031 | -0.020087 | -0.14585 | -0.07611 | -0.13491 | -0.036986 | -0.065512 | -0.18633 | -0.26344 | -0.136 | -0.20109 | -0.17507 | 0.19931 | 0.18345 | 0.17711 | 0.27609 | -0.46275 | -0.44055 | -0.4004 | -0.37821
1242.4375 | 121.7239 | -0.25177 | 121.3531 | -0.065863 | -0.18704 | -0.11731 | -0.18069 | -0.08734 | -0.10671 | -0.23211 | -0.30006 | -0.18177 | -0.24687 | -0.21626 | 0.16269 | 0.13309 | 0.12218 | 0.22574 | -0.020087 | -0.14127 | -0.071531 | -0.13491 | -0.041564 | -0.060933 | -0.18633 | -0.25428 | -0.136 | -0.20109 | -0.17049 | 0.20847 | 0.17887 | 0.16796 | 0.27151 | -0.46275 | -0.42224 | -0.40956 | -0.36905
1244.2031 | 121.6507 | -0.27008 | 121.3943 | -0.061284 | -0.18704 | -0.11731 | -0.17153 | -0.082762 | -0.10671 | -0.22753 | -0.30006 | -0.18177 | -0.24687 | -0.22542 | 0.16269 | 0.13309 | 0.1176 | 0.23489 | -0.015508 | -0.14127 | -0.071531 | -0.12575 | -0.036986 | -0.060933 | -0.18176 | -0.25428 | -0.136 | -0.20109 | -0.17964 | 0.20847 | 0.17887 | 0.16338 | 0.28067 | -0.46275 | -0.41766 | -0.40956 | -0.36447
1245.9688 | 121.5912 | -0.25635 | 121.4081 | -0.056706 | -0.19162 | -0.12189 | -0.17611 | -0.078184 | -0.10213 | -0.23211 | -0.30463 | -0.18635 | -0.25145 | -0.21626 | 0.15811 | 0.14225 | 0.1176 | 0.21658 | -0.01093 | -0.14585 | -0.07611 | -0.13033 | -0.032408 | -0.056355 | -0.18633 | -0.25886 | -0.14058 | -0.20567 | -0.17049 | 0.20389 | 0.18803 | 0.16338 | 0.26236 | -0.46275 | -0.42224 | -0.40956 | -0.36905
1247.7188 | 121.6232 | -0.2655 | 121.4035 | -0.056706 | -0.18704 | -0.11731 | -0.18069 | -0.078184 | -0.10213 | -0.22753 | -0.30463 | -0.18635 | -0.24687 | -0.21626 | 0.15811 | 0.13767 | 0.1176 | 0.23031 | -0.01093 | -0.14127 | -0.071531 | -0.13491 | -0.032408 | -0.056355 | -0.18176 | -0.25886 | -0.14058 | -0.20109 | -0.17049 | 0.20389 | 0.18345 | 0.16338 | 0.27609 | -0.46275 | -0.42224 | -0.40498 | -0.36447
1249.4219 | 121.7697 | -0.22888 | 121.3531 | -0.056706 | -0.18704 | -0.12189 | -0.18069 | -0.082762 | -0.11129 | -0.23669 | -0.29548 | -0.18177 | -0.24687 | -0.22542 | 0.15811 | 0.13309 | 0.12218 | 0.23031 | -0.01093 | -0.14127 | -0.07611 | -0.13491 | -0.036986 | -0.065512 | -0.19091 | -0.2497 | -0.136 | -0.20109 | -0.17964 | 0.20389 | 0.17887 | 0.16796 | 0.27609 | -0.45359 | -0.41766 | -0.40498 | -0.36905
1251.2031 | 121.6736 | -0.2655 | 121.4081 | -0.056706 | -0.18704 | -0.11273 | -0.17611 | -0.073606 | -0.10213 | -0.22753 | -0.29548 | -0.18177 | -0.25145 | -0.21168 | 0.15811 | 0.13767 | 0.12676 | 0.22574 | -0.01093 | -0.14127 | -0.066953 | -0.13033 | -0.02783 | -0.056355 | -0.18176 | -0.2497 | -0.136 | -0.20567 | -0.16591 | 0.20389 | 0.18345 | 0.17253 | 0.27151 | -0.45359 | -0.42224 | -0.40956 | -0.37821
1252.9688 | 121.7285 | -0.23346 | 121.3806 | -0.056706 | -0.18704 | -0.12189 | -0.18526 | -0.082762 | -0.10671 | -0.23211 | -0.30006 | -0.18177 | -0.25145 | -0.21626 | 0.15811 | 0.12851 | 0.11302 | 0.22574 | -0.01093 | -0.14127 | -0.07611 | -0.13949 | -0.036986 | -0.060933 | -0.18633 | -0.25428 | -0.136 | -0.20567 | -0.17049 | 0.20389 | 0.17429 | 0.1588 | 0.27151 | -0.45817 | -0.41308 | -0.40956 | -0.36447
1254.75 | 121.5912 | -0.27466 | 121.4172 | -0.065863 | -0.18246 | -0.12189 | -0.18526 | -0.078184 | -0.10671 | -0.23669 | -0.30006 | -0.19093 | -0.24687 | -0.22084 | 0.16269 | 0.13767 | 0.12218 | 0.22116 | -0.020087 | -0.13669 | -0.07611 | -0.13949 | -0.032408 | -0.060933 | -0.19091 | -0.25428 | -0.14516 | -0.20109 | -0.17507 | 0.20847 | 0.18345 | 0.16796 | 0.26693 | -0.46275 | -0.42224 | -0.40956 | -0.36905
1256.5156 | 121.7194 | -0.25177 | 121.376 | -0.061284 | -0.17788 | -0.11273 | -0.18069 | -0.078184 | -0.10213 | -0.23211 | -0.30006 | -0.18177 | -0.24687 | -0.22542 | 0.16269 | 0.13767 | 0.12676 | 0.22574 | -0.015508 | -0.13211 | -0.066953 | -0.13491 | -0.032408 | -0.056355 | -0.18633 | -0.25428 | -0.136 | -0.20109 | -0.17964 | 0.20847 | 0.18345 | 0.17253 | 0.27151 | -0.46275 | -0.42681 | -0.40956 | -0.37363
1258.2188 | 121.6919 | -0.25177 | 121.376 | -0.061284 | -0.18246 | -0.11273 | -0.17153 | -0.073606 | -0.097553 | -0.22753 | -0.29548 | -0.18177 | -0.24229 | -0.21626 | 0.16269 | 0.14225 | 0.1176 | 0.22574 | -0.015508 | -0.13669 | -0.066953 | -0.12575 | -0.02783 | -0.051777 | -0.18176 | -0.2497 | -0.136 | -0.19651 | -0.17049 | 0.20847 | 0.18803 | 0.16338 | 0.27151 | -0.45817 | -0.41308 | -0.40498 | -0.35989
1259.9844 | 121.6644 | -0.25177 | 121.4081 | -0.056706 | -0.18246 | -0.10815 | -0.16695 | -0.073606 | -0.10213 | -0.22753 | -0.30006 | -0.18177 | -0.24687 | -0.21626 | 0.15811 | 0.13309 | 0.1176 | 0.22116 | -0.01093 | -0.13669 | -0.062374 | -0.12117 | -0.02783 | -0.056355 | -0.18176 | -0.25428 | -0.136 | -0.20109 | -0.17049 | 0.20389 | 0.17887 | 0.16338 | 0.26693 | -0.45817 | -0.41766 | -0.40498 | -0.36447
1261.6719 | 121.7056 | -0.23804 | 121.3806 | -0.061284 | -0.18704 | -0.11731 | -0.17153 | -0.073606 | -0.097553 | -0.23211 | -0.30006 | -0.1772 | -0.24687 | -0.22084 | 0.15811 | 0.12851 | 0.1176 | 0.22574 | -0.015508 | -0.14127 | -0.071531 | -0.12575 | -0.02783 | -0.051777 | -0.18633 | -0.25428 | -0.13142 | -0.20109 | -0.17507 | 0.20389 | 0.17429 | 0.16338 | 0.27151 | -0.45817 | -0.41766 | -0.40498 | -0.36447
1263.4375 | 121.6965 | -0.22888 | 121.3898 | -0.056706 | -0.18246 | -0.11273 | -0.18069 | -0.078184 | -0.10671 | -0.22753 | -0.2909 | -0.18177 | -0.24229 | -0.21626 | 0.16269 | 0.11936 | 0.1176 | 0.21658 | -0.01093 | -0.13669 | -0.066953 | -0.13491 | -0.032408 | -0.060933 | -0.18176 | -0.24512 | -0.136 | -0.19651 | -0.17049 | 0.20847 | 0.16514 | 0.16338 | 0.26236 | -0.45359 | -0.4085 | -0.40498 | -0.35989
1265.2188 | 121.6415 | -0.27008 | 121.4035 | -0.056706 | -0.17788 | -0.11731 | -0.17153 | -0.073606 | -0.10671 | -0.22753 | -0.30006 | -0.17262 | -0.25145 | -0.21168 | 0.15811 | 0.12851 | 0.12676 | 0.22574 | -0.01093 | -0.13211 | -0.071531 | -0.12575 | -0.02783 | -0.060933 | -0.18176 | -0.25428 | -0.12684 | -0.20567 | -0.16591 | 0.20389 | 0.17429 | 0.17253 | 0.27151 | -0.45817 | -0.42681 | -0.40956 | -0.37821
1266.9844 | 121.7377 | -0.23804 | 121.3898 | -0.052128 | -0.18704 | -0.10815 | -0.16695 | -0.073606 | -0.10213 | -0.23211 | -0.2909 | -0.18635 | -0.24229 | -0.22084 | 0.14896 | 0.13767 | 0.1176 | 0.22574 | -0.006352 | -0.14127 | -0.062374 | -0.12117 | -0.02783 | -0.056355 | -0.18633 | -0.24512 | -0.14058 | -0.19651 | -0.17507 | 0.19473 | 0.18345 | 0.16338 | 0.27151 | -0.43985 | -0.4085 | -0.39125 | -0.35989
1268.6875 | 121.7514 | -0.24719 | 121.3486 | -0.065863 | -0.18246 | -0.11273 | -0.17611 | -0.078184 | -0.10671 | -0.21838 | -0.2909 | -0.17262 | -0.23771 | -0.2071 | 0.14896 | 0.12394 | 0.1176 | 0.22116 | -0.020087 | -0.13669 | -0.066953 | -0.13033 | -0.032408 | -0.060933 | -0.1726 | -0.24512 | -0.12684 | -0.19194 | -0.16133 | 0.19473 | 0.16971 | 0.16338 | 0.26693 | -0.43985 | -0.4085 | -0.38667 | -0.35531
1270.4688 | 121.7285 | -0.22888 | 121.3577 | -0.052128 | -0.17788 | -0.12189 | -0.17153 | -0.073606 | -0.10213 | -0.23211 | -0.2909 | -0.18635 | -0.24229 | -0.21168 | 0.15353 | 0.12394 | 0.1176 | 0.22116 | -0.006352 | -0.13211 | -0.07611 | -0.12575 | -0.02783 | -0.056355 | -0.18633 | -0.24512 | -0.14058 | -0.19651 | -0.16591 | 0.19931 | 0.16971 | 0.16338 | 0.26693 | -0.44443 | -0.4085 | -0.39582 | -0.35989
1272.1719 | 121.7239 | -0.23804 | 121.376 | -0.047549 | -0.18704 | -0.11273 | -0.17153 | -0.073606 | -0.097553 | -0.22753 | -0.29548 | -0.18177 | -0.23771 | -0.21168 | 0.14896 | 0.12394 | 0.12218 | 0.22574 | -0.001773 | -0.14127 | -0.066953 | -0.12575 | -0.02783 | -0.051777 | -0.18176 | -0.2497 | -0.136 | -0.19194 | -0.16591 | 0.19473 | 0.16971 | 0.16796 | 0.27151 | -0.44443 | -0.41766 | -0.38667 | -0.35989
1273.9375 | 121.6553 | -0.27466 | 121.3989 | -0.052128 | -0.17788 | -0.10815 | -0.17153 | -0.073606 | -0.088396 | -0.22753 | -0.2909 | -0.17262 | -0.24687 | -0.21168 | 0.14896 | 0.12851 | 0.11302 | 0.22116 | -0.006352 | -0.13211 | -0.062374 | -0.12575 | -0.02783 | -0.04262 | -0.18176 | -0.24512 | -0.12684 | -0.20109 | -0.16591 | 0.19473 | 0.17429 | 0.1588 | 0.26693 | -0.43985 | -0.40392 | -0.39582 | -0.35989
1275.7031 | 121.6873 | -0.2243 | 121.344 | -0.061284 | -0.18246 | -0.12189 | -0.17153 | -0.069028 | -0.10213 | -0.22753 | -0.28632 | -0.1772 | -0.23771 | -0.19795 | 0.14438 | 0.12394 | 0.11302 | 0.22116 | -0.015508 | -0.13669 | -0.07611 | -0.12575 | -0.023252 | -0.056355 | -0.18176 | -0.24055 | -0.13142 | -0.19194 | -0.15217 | 0.19015 | 0.16971 | 0.1588 | 0.26693 | -0.4307 | -0.39935 | -0.38209 | -0.35074
1277.4062 | 121.7194 | -0.21057 | 121.3577 | -0.056706 | -0.18246 | -0.10357 | -0.17611 | -0.073606 | -0.10213 | -0.22753 | -0.30006 | -0.17262 | -0.23771 | -0.2071 | 0.14896 | 0.12394 | 0.11302 | 0.22116 | -0.01093 | -0.13669 | -0.057796 | -0.13033 | -0.02783 | -0.056355 | -0.18176 | -0.25428 | -0.12684 | -0.19194 | -0.16133 | 0.19473 | 0.16971 | 0.1588 | 0.26693 | -0.44901 | -0.41308 | -0.38667 | -0.35074
1279.1719 | 121.6049 | -0.27008 | 121.3989 | -0.061284 | -0.17331 | -0.10815 | -0.16695 | -0.06445 | -0.092974 | -0.21838 | -0.2909 | -0.17262 | -0.23771 | -0.21168 | 0.14896 | 0.11936 | 0.11302 | 0.212 | -0.015508 | -0.12753 | -0.062374 | -0.12117 | -0.018674 | -0.047198 | -0.1726 | -0.24512 | -0.12684 | -0.19194 | -0.16591 | 0.19473 | 0.16514 | 0.1588 | 0.25778 | -0.43985 | -0.40392 | -0.38667 | -0.35074
1280.875 | 121.6644 | -0.27466 | 121.3715 | -0.061284 | -0.17788 | -0.11273 | -0.17611 | -0.069028 | -0.092974 | -0.22753 | -0.28632 | -0.1772 | -0.23771 | -0.19337 | 0.14438 | 0.11936 | 0.11302 | 0.22116 | -0.015508 | -0.13211 | -0.066953 | -0.13033 | -0.023252 | -0.047198 | -0.18176 | -0.24055 | -0.13142 | -0.19194 | -0.14759 | 0.19015 | 0.16514 | 0.1588 | 0.26693 | -0.4307 | -0.39935 | -0.38209 | -0.35074
1282.6406 | 121.7514 | -0.21973 | 121.3669 | -0.052128 | -0.17331 | -0.11273 | -0.16695 | -0.073606 | -0.092974 | -0.22295 | -0.30006 | -0.1772 | -0.23771 | -0.20253 | 0.13522 | 0.12394 | 0.11302 | 0.212 | -0.006352 | -0.12753 | -0.066953 | -0.12117 | -0.02783 | -0.047198 | -0.17718 | -0.25428 | -0.13142 | -0.19194 | -0.15675 | 0.181 | 0.16971 | 0.1588 | 0.25778 | -0.43528 | -0.41308 | -0.37293 | -0.35074
1284.3906 | 121.7834 | -0.24261 | 121.3715 | -0.047549 | -0.17788 | -0.11273 | -0.18069 | -0.073606 | -0.097553 | -0.22753 | -0.29548 | -0.18177 | -0.22856 | -0.19795 | 0.1398 | 0.11478 | 0.10845 | 0.22116 | -0.001773 | -0.13211 | -0.066953 | -0.13491 | -0.02783 | -0.051777 | -0.18176 | -0.2497 | -0.136 | -0.18278 | -0.15217 | 0.18557 | 0.16056 | 0.15422 | 0.26693 | -0.43528 | -0.40392 | -0.36835 | -0.337
1286.0938 | 121.6232 | -0.25635 | 121.4218 | -0.047549 | -0.18246 | -0.10357 | -0.16695 | -0.073606 | -0.097553 | -0.22753 | -0.29548 | -0.1772 | -0.23771 | -0.20253 | 0.14896 | 0.11478 | 0.11302 | 0.22574 | -0.001773 | -0.13669 | -0.057796 | -0.12117 | -0.02783 | -0.051777 | -0.18176 | -0.2497 | -0.13142 | -0.19194 | -0.15675 | 0.19473 | 0.16056 | 0.1588 | 0.27151 | -0.44443 | -0.4085 | -0.38667 | -0.35074
1287.8594 | 121.7422 | -0.21057 | 121.376 | -0.052128 | -0.17788 | -0.10815 | -0.17153 | -0.069028 | -0.092974 | -0.22753 | -0.2909 | -0.1772 | -0.23771 | -0.19795 | 0.1398 | 0.12394 | 0.11302 | 0.22574 | -0.006352 | -0.13211 | -0.062374 | -0.12575 | -0.023252 | -0.047198 | -0.18176 | -0.24512 | -0.13142 | -0.19194 | -0.15217 | 0.18557 | 0.16971 | 0.1588 | 0.27151 | -0.4307 | -0.40392 | -0.37751 | -0.35074
1289.6094 | 121.6324 | -0.27008 | 121.4127 | -0.052128 | -0.16873 | -0.11731 | -0.17153 | -0.069028 | -0.088396 | -0.22753 | -0.2909 | -0.17262 | -0.22856 | -0.19795 | 0.1398 | 0.11478 | 0.11302 | 0.21658 | -0.006352 | -0.12295 | -0.071531 | -0.12575 | -0.023252 | -0.04262 | -0.18176 | -0.24512 | -0.12684 | -0.18278 | -0.15217 | 0.18557 | 0.16056 | 0.1588 | 0.26236 | -0.4307 | -0.40392 | -0.36835 | -0.34158
1291.3125 | 121.7377 | -0.23804 | 121.3852 | -0.047549 | -0.16873 | -0.098993 | -0.17153 | -0.06445 | -0.097553 | -0.22295 | -0.28632 | -0.1772 | -0.22856 | -0.20253 | 0.13522 | 0.11936 | 0.11302 | 0.21658 | -0.001773 | -0.12295 | -0.053217 | -0.12575 | -0.018674 | -0.051777 | -0.17718 | -0.24055 | -0.13142 | -0.18278 | -0.15675 | 0.181 | 0.16514 | 0.1588 | 0.26236 | -0.42154 | -0.39935 | -0.36378 | -0.34158
1293.0781 | 121.6644 | -0.25635 | 121.4127 | -0.052128 | -0.17788 | -0.10815 | -0.16695 | -0.069028 | -0.092974 | -0.23211 | -0.28632 | -0.17262 | -0.23771 | -0.20253 | 0.1398 | 0.11936 | 0.10845 | 0.22116 | -0.006352 | -0.13211 | -0.062374 | -0.12117 | -0.023252 | -0.047198 | -0.18633 | -0.24055 | -0.12684 | -0.19194 | -0.15675 | 0.18557 | 0.16514 | 0.15422 | 0.26693 | -0.42612 | -0.39477 | -0.37751 | -0.34616
1294.8281 | 121.6644 | -0.2655 | 121.4035 | -0.056706 | -0.17788 | -0.10815 | -0.16237 | -0.073606 | -0.097553 | -0.21838 | -0.2909 | -0.17262 | -0.23771 | -0.19795 | 0.1398 | 0.11478 | 0.10845 | 0.21658 | -0.01093 | -0.13211 | -0.062374 | -0.1166 | -0.02783 | -0.051777 | -0.1726 | -0.24512 | -0.12684 | -0.19194 | -0.15217 | 0.18557 | 0.16056 | 0.15422 | 0.26236 | -0.4307 | -0.39935 | -0.37751 | -0.34616
1296.5938 | 121.6919 | -0.23346 | 121.3989 | -0.042971 | -0.17788 | -0.10815 | -0.16695 | -0.059872 | -0.097553 | -0.22295 | -0.28632 | -0.17262 | -0.24229 | -0.19795 | 0.13522 | 0.11936 | 0.11302 | 0.21658 | 0.002805 | -0.13211 | -0.062374 | -0.12117 | -0.014096 | -0.051777 | -0.17718 | -0.24055 | -0.12684 | -0.19651 | -0.15217 | 0.181 | 0.16514 | 0.1588 | 0.26236 | -0.42154 | -0.39935 | -0.37751 | -0.35531
1298.375 | 121.6278 | -0.2655 | 121.3943 | -0.052128 | -0.17788 | -0.10357 | -0.16695 | -0.06445 | -0.092974 | -0.22753 | -0.28174 | -0.16804 | -0.22398 | -0.20253 | 0.1398 | 0.1102 | 0.10845 | 0.212 | -0.006352 | -0.13211 | -0.057796 | -0.12117 | -0.018674 | -0.047198 | -0.18176 | -0.23597 | -0.12226 | -0.1782 | -0.15675 | 0.18557 | 0.15598 | 0.15422 | 0.25778 | -0.42154 | -0.39019 | -0.36378 | -0.33242
1300.0781 | 121.7377 | -0.23804 | 121.3806 | -0.056706 | -0.17331 | -0.10815 | -0.16695 | -0.069028 | -0.092974 | -0.22295 | -0.28632 | -0.17262 | -0.22856 | -0.19795 | 0.13522 | 0.11478 | 0.10845 | 0.212 | -0.01093 | -0.12753 | -0.062374 | -0.12117 | -0.023252 | -0.047198 | -0.17718 | -0.24055 | -0.12684 | -0.18278 | -0.15217 | 0.181 | 0.16056 | 0.15422 | 0.25778 | -0.42154 | -0.39477 | -0.36378 | -0.337
1301.8438 | 121.637 | -0.27008 | 121.3989 | -0.047549 | -0.17788 | -0.10357 | -0.16695 | -0.059872 | -0.092974 | -0.21838 | -0.28632 | -0.17262 | -0.22856 | -0.19337 | 0.13522 | 0.11478 | 0.10845 | 0.212 | -0.001773 | -0.13211 | -0.057796 | -0.12117 | -0.014096 | -0.047198 | -0.1726 | -0.24055 | -0.12684 | -0.18278 | -0.14759 | 0.181 | 0.16056 | 0.15422 | 0.25778 | -0.42154 | -0.39477 | -0.36378 | -0.337
1303.6094 | 121.6232 | -0.25635 | 121.4172 | -0.042971 | -0.17331 | -0.098993 | -0.16695 | -0.069028 | -0.088396 | -0.2138 | -0.28174 | -0.17262 | -0.23313 | -0.20253 | 0.13522 | 0.1102 | 0.11302 | 0.212 | 0.002805 | -0.12753 | -0.053217 | -0.12117 | -0.023252 | -0.04262 | -0.16802 | -0.23597 | -0.12684 | -0.18736 | -0.15675 | 0.181 | 0.15598 | 0.1588 | 0.25778 | -0.41696 | -0.39477 | -0.36835 | -0.34616
1305.3125 | 121.7834 | -0.23346 | 121.3669 | -0.052128 | -0.16873 | -0.098993 | -0.16695 | -0.073606 | -0.097553 | -0.21838 | -0.27716 | -0.17262 | -0.22856 | -0.19795 | 0.1398 | 0.11936 | 0.10387 | 0.212 | -0.006352 | -0.12295 | -0.053217 | -0.12117 | -0.02783 | -0.051777 | -0.1726 | -0.23139 | -0.12684 | -0.18278 | -0.15217 | 0.18557 | 0.16514 | 0.14964 | 0.25778 | -0.41696 | -0.38103 | -0.36835 | -0.33242
1307.0781 | 121.7377 | -0.21515 | 121.3806 | -0.056706 | -0.17331 | -0.10357 | -0.16695 | -0.073606 | -0.097553 | -0.21838 | -0.2909 | -0.16804 | -0.22856 | -0.20253 | 0.1398 | 0.11936 | 0.10845 | 0.21658 | -0.01093 | -0.12753 | -0.057796 | -0.12117 | -0.02783 | -0.051777 | -0.1726 | -0.24512 | -0.12226 | -0.18278 | -0.15675 | 0.18557 | 0.16514 | 0.15422 | 0.26236 | -0.4307 | -0.39935 | -0.36835 | -0.337
1308.8438 | 121.756 | -0.22888 | 121.3669 | -0.047549 | -0.16873 | -0.10815 | -0.16237 | -0.069028 | -0.097553 | -0.21838 | -0.27716 | -0.15888 | -0.23313 | -0.19795 | 0.1398 | 0.1102 | 0.099289 | 0.212 | -0.001773 | -0.12295 | -0.062374 | -0.1166 | -0.023252 | -0.051777 | -0.1726 | -0.23139 | -0.1131 | -0.18736 | -0.15217 | 0.18557 | 0.15598 | 0.14506 | 0.25778 | -0.41696 | -0.37645 | -0.37293 | -0.33242
1310.6094 | 121.6232 | -0.25177 | 121.4218 | -0.047549 | -0.17331 | -0.10357 | -0.16237 | -0.069028 | -0.092974 | -0.21838 | -0.28174 | -0.16346 | -0.23771 | -0.19337 | 0.1398 | 0.1102 | 0.099289 | 0.21658 | -0.001773 | -0.12753 | -0.057796 | -0.1166 | -0.023252 | -0.047198 | -0.1726 | -0.23597 | -0.11768 | -0.19194 | -0.14759 | 0.18557 | 0.15598 | 0.14506 | 0.26236 | -0.42154 | -0.38103 | -0.37751 | -0.337
1312.375 | 121.6324 | -0.2655 | 121.4127 | -0.038393 | -0.16873 | -0.098993 | -0.16695 | -0.069028 | -0.083817 | -0.22295 | -0.28632 | -0.16804 | -0.22856 | -0.20253 | 0.1398 | 0.11478 | 0.10845 | 0.21658 | 0.007383 | -0.12295 | -0.053217 | -0.12117 | -0.023252 | -0.038041 | -0.17718 | -0.24055 | -0.12226 | -0.18278 | -0.15675 | 0.18557 | 0.16056 | 0.15422 | 0.26236 | -0.42612 | -0.39477 | -0.36835 | -0.337
1314.1406 | 121.669 | -0.25177 | 121.3989 | -0.042971 | -0.16415 | -0.10815 | -0.16237 | -0.069028 | -0.092974 | -0.2138 | -0.28632 | -0.16804 | -0.23313 | -0.19795 | 0.1398 | 0.11936 | 0.10845 | 0.22116 | 0.002805 | -0.11837 | -0.062374 | -0.1166 | -0.023252 | -0.047198 | -0.16802 | -0.24055 | -0.12226 | -0.18736 | -0.15217 | 0.18557 | 0.16514 | 0.15422 | 0.26693 | -0.42612 | -0.39477 | -0.37293 | -0.34158
1315.8438 | 121.6507 | -0.26093 | 121.4355 | -0.047549 | -0.16873 | -0.10815 | -0.16695 | -0.069028 | -0.092974 | -0.2138 | -0.28632 | -0.16346 | -0.23313 | -0.19795 | 0.1398 | 0.11936 | 0.10387 | 0.21658 | -0.001773 | -0.12295 | -0.062374 | -0.12117 | -0.023252 | -0.047198 | -0.16802 | -0.24055 | -0.11768 | -0.18736 | -0.15217 | 0.18557 | 0.16514 | 0.14964 | 0.26236 | -0.42612 | -0.39019 | -0.37293 | -0.337
1317.6094 | 121.6415 | -0.25177 | 121.431 | -0.047549 | -0.17331 | -0.10357 | -0.16695 | -0.069028 | -0.092974 | -0.2138 | -0.28632 | -0.17262 | -0.22856 | -0.20253 | 0.14438 | 0.11936 | 0.1176 | 0.212 | -0.001773 | -0.12753 | -0.057796 | -0.12117 | -0.023252 | -0.047198 | -0.16802 | -0.24055 | -0.12684 | -0.18278 | -0.15675 | 0.19015 | 0.16514 | 0.16338 | 0.25778 | -0.4307 | -0.40392 | -0.37293 | -0.34616
1319.375 | 121.6324 | -0.26093 | 121.4355 | -0.047549 | -0.16873 | -0.10357 | -0.16695 | -0.059872 | -0.083817 | -0.22295 | -0.28174 | -0.16804 | -0.23771 | -0.19795 | 0.14438 | 0.12394 | 0.10845 | 0.22116 | -0.001773 | -0.12295 | -0.057796 | -0.12117 | -0.014096 | -0.038041 | -0.17718 | -0.23597 | -0.12226 | -0.19194 | -0.15217 | 0.19015 | 0.16971 | 0.15422 | 0.26693 | -0.42612 | -0.39019 | -0.38209 | -0.34616
1321.0781 | 121.7377 | -0.22888 | 121.4035 | -0.042971 | -0.17788 | -0.10815 | -0.16695 | -0.073606 | -0.092974 | -0.22295 | -0.28632 | -0.17262 | -0.22856 | -0.19795 | 0.13522 | 0.11478 | 0.10845 | 0.20742 | 0.002805 | -0.13211 | -0.062374 | -0.12117 | -0.02783 | -0.047198 | -0.17718 | -0.24055 | -0.12684 | -0.18278 | -0.15217 | 0.181 | 0.16056 | 0.15422 | 0.2532 | -0.42154 | -0.39477 | -0.36378 | -0.337
1322.8438 | 121.7102 | -0.23804 | 121.3989 | -0.047549 | -0.16873 | -0.10357 | -0.16237 | -0.069028 | -0.083817 | -0.22295 | -0.27716 | -0.16804 | -0.22398 | -0.18879 | 0.13522 | 0.11478 | 0.11302 | 0.212 | -0.001773 | -0.12295 | -0.057796 | -0.1166 | -0.023252 | -0.038041 | -0.17718 | -0.23139 | -0.12226 | -0.1782 | -0.14301 | 0.181 | 0.16056 | 0.1588 | 0.25778 | -0.41239 | -0.39019 | -0.3592 | -0.337
1324.6094 | 121.6187 | -0.25635 | 121.4035 | -0.047549 | -0.17788 | -0.10815 | -0.16695 | -0.06445 | -0.092974 | -0.21838 | -0.2909 | -0.16804 | -0.22856 | -0.2071 | 0.13522 | 0.11936 | 0.10387 | 0.212 | -0.001773 | -0.13211 | -0.062374 | -0.12117 | -0.018674 | -0.047198 | -0.1726 | -0.24512 | -0.12226 | -0.18278 | -0.16133 | 0.181 | 0.16514 | 0.14964 | 0.25778 | -0.42612 | -0.39477 | -0.36378 | -0.33242
1326.3125 | 121.6095 | -0.2655 | 121.4127 | -0.042971 | -0.16873 | -0.10357 | -0.16237 | -0.06445 | -0.088396 | -0.2138 | -0.28632 | -0.16346 | -0.22398 | -0.2071 | 0.1398 | 0.11936 | 0.10845 | 0.20285 | 0.002805 | -0.12295 | -0.057796 | -0.1166 | -0.018674 | -0.04262 | -0.16802 | -0.24055 | -0.11768 | -0.1782 | -0.16133 | 0.18557 | 0.16514 | 0.15422 | 0.24862 | -0.42612 | -0.39477 | -0.36378 | -0.33242
1328.0625 | 121.7056 | -0.23346 | 121.3852 | -0.042971 | -0.16873 | -0.098993 | -0.16237 | -0.069028 | -0.092974 | -0.21838 | -0.28174 | -0.16346 | -0.22398 | -0.19795 | 0.1398 | 0.12394 | 0.099289 | 0.20285 | 0.002805 | -0.12295 | -0.053217 | -0.1166 | -0.023252 | -0.047198 | -0.1726 | -0.23597 | -0.11768 | -0.1782 | -0.15217 | 0.18557 | 0.16971 | 0.14506 | 0.24862 | -0.42154 | -0.38103 | -0.36378 | -0.32327
1329.7656 | 121.6141 | -0.27924 | 121.4447 | -0.047549 | -0.16873 | -0.10357 | -0.16695 | -0.06445 | -0.092974 | -0.21838 | -0.28174 | -0.17262 | -0.23313 | -0.19795 | 0.13522 | 0.11936 | 0.10387 | 0.212 | -0.001773 | -0.12295 | -0.057796 | -0.12117 | -0.018674 | -0.047198 | -0.1726 | -0.23597 | -0.12684 | -0.18736 | -0.15217 | 0.181 | 0.16514 | 0.14964 | 0.25778 | -0.41696 | -0.38561 | -0.36835 | -0.337
1331.5469 | 121.7514 | -0.22888 | 121.3715 | -0.042971 | -0.17331 | -0.10815 | -0.17153 | -0.059872 | -0.088396 | -0.21838 | -0.27716 | -0.1543 | -0.22856 | -0.19795 | 0.13522 | 0.11478 | 0.10845 | 0.212 | 0.002805 | -0.12753 | -0.062374 | -0.12575 | -0.014096 | -0.04262 | -0.1726 | -0.23139 | -0.10853 | -0.18278 | -0.15217 | 0.181 | 0.16056 | 0.15422 | 0.25778 | -0.41239 | -0.38561 | -0.36378 | -0.337
1333.25 | 121.7697 | -0.20599 | 121.3806 | -0.042971 | -0.17788 | -0.098993 | -0.16695 | -0.059872 | -0.083817 | -0.21838 | -0.28174 | -0.17262 | -0.22398 | -0.19795 | 0.13522 | 0.11936 | 0.10845 | 0.21658 | 0.002805 | -0.13211 | -0.053217 | -0.12117 | -0.014096 | -0.038041 | -0.1726 | -0.23597 | -0.12684 | -0.1782 | -0.15217 | 0.181 | 0.16514 | 0.15422 | 0.26236 | -0.41696 | -0.39019 | -0.3592 | -0.33242
1335.0156 | 121.7148 | -0.24261 | 121.4035 | -0.042971 | -0.17788 | -0.10815 | -0.16695 | -0.06445 | -0.097553 | -0.2138 | -0.2909 | -0.16346 | -0.22856 | -0.19795 | 0.1398 | 0.1102 | 0.10845 | 0.21658 | 0.002805 | -0.13211 | -0.062374 | -0.12117 | -0.018674 | -0.051777 | -0.16802 | -0.24512 | -0.11768 | -0.18278 | -0.15217 | 0.18557 | 0.15598 | 0.15422 | 0.26236 | -0.4307 | -0.39935 | -0.36835 | -0.337
1336.9531 | 121.5958 | -0.27008 | 121.4355 | -0.042971 | -0.16873 | -0.098993 | -0.17153 | -0.059872 | -0.083817 | -0.2138 | -0.28174 | -0.16346 | -0.22856 | -0.2071 | 0.14438 | 0.12394 | 0.11302 | 0.21658 | 0.002805 | -0.12295 | -0.053217 | -0.12575 | -0.014096 | -0.038041 | -0.16802 | -0.23597 | -0.11768 | -0.18278 | -0.16133 | 0.19015 | 0.16971 | 0.1588 | 0.26236 | -0.42612 | -0.39477 | -0.37293 | -0.34158
1338.7188 | 121.7651 | -0.21057 | 121.3943 | -0.038393 | -0.16873 | -0.10815 | -0.15321 | -0.069028 | -0.079239 | -0.21838 | -0.28174 | -0.16804 | -0.23313 | -0.19337 | 0.14438 | 0.1102 | 0.10387 | 0.212 | 0.007383 | -0.12295 | -0.062374 | -0.10744 | -0.023252 | -0.033463 | -0.1726 | -0.23597 | -0.12226 | -0.18736 | -0.14759 | 0.19015 | 0.15598 | 0.14964 | 0.25778 | -0.42612 | -0.38561 | -0.37751 | -0.337
1340.4844 | 121.7651 | -0.22888 | 121.3577 | -0.052128 | -0.16873 | -0.10815 | -0.16237 | -0.059872 | -0.092974 | -0.2138 | -0.28632 | -0.16346 | -0.23313 | -0.19337 | 0.14438 | 0.11478 | 0.10845 | 0.21658 | -0.006352 | -0.12295 | -0.062374 | -0.1166 | -0.014096 | -0.047198 | -0.16802 | -0.24055 | -0.11768 | -0.18736 | -0.14759 | 0.19015 | 0.16056 | 0.15422 | 0.26236 | -0.4307 | -0.39477 | -0.37751 | -0.34158
1342.2031 | 121.6873 | -0.23804 | 121.4264 | -0.042971 | -0.16873 | -0.10815 | -0.16237 | -0.069028 | -0.092974 | -0.21838 | -0.27716 | -0.16804 | -0.22856 | -0.20253 | 0.1398 | 0.11478 | 0.10845 | 0.212 | 0.002805 | -0.12295 | -0.062374 | -0.1166 | -0.023252 | -0.047198 | -0.1726 | -0.23139 | -0.12226 | -0.18278 | -0.15675 | 0.18557 | 0.16056 | 0.15422 | 0.25778 | -0.41696 | -0.38561 | -0.36835 | -0.337
1343.9688 | 121.7148 | -0.2243 | 121.4081 | -0.047549 | -0.17788 | -0.10357 | -0.16237 | -0.06445 | -0.088396 | -0.2138 | -0.28632 | -0.16346 | -0.23771 | -0.20253 | 0.1398 | 0.12394 | 0.10845 | 0.20742 | -0.001773 | -0.13211 | -0.057796 | -0.1166 | -0.018674 | -0.04262 | -0.16802 | -0.24055 | -0.11768 | -0.19194 | -0.15675 | 0.18557 | 0.16971 | 0.15422 | 0.2532 | -0.42612 | -0.39477 | -0.37751 | -0.34616
1345.6719 | 121.6278 | -0.27466 | 121.4447 | -0.042971 | -0.16415 | -0.098993 | -0.16695 | -0.059872 | -0.092974 | -0.21838 | -0.28632 | -0.16346 | -0.22856 | -0.19337 | 0.13522 | 0.11478 | 0.10845 | 0.20285 | 0.002805 | -0.11837 | -0.053217 | -0.12117 | -0.014096 | -0.047198 | -0.1726 | -0.24055 | -0.11768 | -0.18278 | -0.14759 | 0.181 | 0.16056 | 0.15422 | 0.24862 | -0.42154 | -0.39477 | -0.36378 | -0.337
1347.4375 | 121.637 | -0.28381 | 121.4493 | -0.042971 | -0.17331 | -0.10815 | -0.16237 | -0.06445 | -0.088396 | -0.2138 | -0.28632 | -0.16346 | -0.22856 | -0.19795 | 0.13522 | 0.11478 | 0.09471 | 0.212 | 0.002805 | -0.12753 | -0.062374 | -0.1166 | -0.018674 | -0.04262 | -0.16802 | -0.24055 | -0.11768 | -0.18278 | -0.15217 | 0.181 | 0.16056 | 0.14049 | 0.25778 | -0.42154 | -0.38103 | -0.36378 | -0.32327
1349.1406 | 121.7697 | -0.21515 | 121.3989 | -0.047549 | -0.17331 | -0.094414 | -0.15779 | -0.06445 | -0.088396 | -0.21838 | -0.27716 | -0.16346 | -0.23771 | -0.19795 | 0.13522 | 0.11936 | 0.10387 | 0.212 | -0.001773 | -0.12753 | -0.048638 | -0.11202 | -0.018674 | -0.04262 | -0.1726 | -0.23139 | -0.11768 | -0.19194 | -0.15217 | 0.181 | 0.16514 | 0.14964 | 0.25778 | -0.41239 | -0.38103 | -0.37293 | -0.34158
1350.9062 | 121.7468 | -0.21515 | 121.4035 | -0.042971 | -0.17788 | -0.098993 | -0.16695 | -0.059872 | -0.088396 | -0.20922 | -0.28632 | -0.16804 | -0.23313 | -0.19337 | 0.13064 | 0.11478 | 0.10845 | 0.20742 | 0.002805 | -0.13211 | -0.053217 | -0.12117 | -0.014096 | -0.04262 | -0.16344 | -0.24055 | -0.12226 | -0.18736 | -0.14759 | 0.17642 | 0.16056 | 0.15422 | 0.2532 | -0.41696 | -0.39477 | -0.36378 | -0.34158
1352.6719 | 121.7468 | -0.20599 | 121.3852 | -0.042971 | -0.16415 | -0.10357 | -0.16695 | -0.059872 | -0.092974 | -0.22295 | -0.28174 | -0.1543 | -0.22398 | -0.19795 | 0.1398 | 0.11478 | 0.10387 | 0.21658 | 0.002805 | -0.11837 | -0.057796 | -0.12117 | -0.014096 | -0.047198 | -0.17718 | -0.23597 | -0.10853 | -0.1782 | -0.15217 | 0.18557 | 0.16056 | 0.14964 | 0.26236 | -0.42154 | -0.38561 | -0.36378 | -0.32784
1354.375 | 121.6461 | -0.27466 | 121.4172 | -0.042971 | -0.17331 | -0.10357 | -0.15779 | -0.059872 | -0.088396 | -0.2138 | -0.28174 | -0.16346 | -0.22856 | -0.19337 | 0.1398 | 0.11936 | 0.099289 | 0.212 | 0.002805 | -0.12753 | -0.057796 | -0.11202 | -0.014096 | -0.04262 | -0.16802 | -0.23597 | -0.11768 | -0.18278 | -0.14759 | 0.18557 | 0.16514 | 0.14506 | 0.25778 | -0.42154 | -0.38103 | -0.36835 | -0.32784
1356.1406 | 121.6232 | -0.2655 | 121.4447 | -0.042971 | -0.16415 | -0.098993 | -0.16695 | -0.06445 | -0.097553 | -0.2138 | -0.28174 | -0.15888 | -0.23313 | -0.19337 | 0.1398 | 0.1102 | 0.09471 | 0.212 | 0.002805 | -0.11837 | -0.053217 | -0.12117 | -0.018674 | -0.051777 | -0.16802 | -0.23597 | -0.1131 | -0.18736 | -0.14759 | 0.18557 | 0.15598 | 0.14049 | 0.25778 | -0.42154 | -0.37645 | -0.37293 | -0.32784
1357.8438 | 121.7789 | -0.2243 | 121.3943 | -0.052128 | -0.15957 | -0.098993 | -0.15779 | -0.06445 | -0.088396 | -0.2138 | -0.27716 | -0.16804 | -0.23313 | -0.19795 | 0.13522 | 0.1102 | 0.10845 | 0.212 | -0.006352 | -0.11379 | -0.053217 | -0.11202 | -0.018674 | -0.04262 | -0.16802 | -0.23139 | -0.12226 | -0.18736 | -0.15217 | 0.181 | 0.15598 | 0.15422 | 0.25778 | -0.41239 | -0.38561 | -0.36835 | -0.34158
1359.5469 | 121.6599 | -0.24261 | 121.4172 | -0.042971 | -0.17331 | -0.10815 | -0.16237 | -0.059872 | -0.088396 | -0.2138 | -0.27716 | -0.15888 | -0.22398 | -0.18879 | 0.1398 | 0.11478 | 0.10387 | 0.20285 | 0.002805 | -0.12753 | -0.062374 | -0.1166 | -0.014096 | -0.04262 | -0.16802 | -0.23139 | -0.1131 | -0.1782 | -0.14301 | 0.18557 | 0.16056 | 0.14964 | 0.24862 | -0.41696 | -0.38103 | -0.36378 | -0.32784
1361.3125 | 121.6965 | -0.25177 | 121.4081 | -0.042971 | -0.15957 | -0.098993 | -0.16237 | -0.059872 | -0.088396 | -0.21838 | -0.26801 | -0.16346 | -0.22398 | -0.19795 | 0.1398 | 0.11478 | 0.099289 | 0.20742 | 0.002805 | -0.11379 | -0.053217 | -0.1166 | -0.014096 | -0.04262 | -0.1726 | -0.22223 | -0.11768 | -0.1782 | -0.15217 | 0.18557 | 0.16056 | 0.14506 | 0.2532 | -0.40781 | -0.3673 | -0.36378 | -0.32327
1363.0938 | 121.6461 | -0.2655 | 121.4355 | -0.038393 | -0.16415 | -0.098993 | -0.15779 | -0.059872 | -0.083817 | -0.20922 | -0.28632 | -0.16804 | -0.22398 | -0.18879 | 0.13522 | 0.11478 | 0.10845 | 0.212 | 0.007383 | -0.11837 | -0.053217 | -0.11202 | -0.014096 | -0.038041 | -0.16344 | -0.24055 | -0.12226 | -0.1782 | -0.14301 | 0.181 | 0.16056 | 0.15422 | 0.25778 | -0.42154 | -0.39477 | -0.3592 | -0.33242
1364.8594 | 121.6187 | -0.25635 | 121.431 | -0.042971 | -0.16415 | -0.10357 | -0.15321 | -0.055294 | -0.083817 | -0.20464 | -0.28174 | -0.16804 | -0.23313 | -0.19795 | 0.13522 | 0.1102 | 0.099289 | 0.212 | 0.002805 | -0.11837 | -0.057796 | -0.10744 | -0.009518 | -0.038041 | -0.15886 | -0.23597 | -0.12226 | -0.18736 | -0.15217 | 0.181 | 0.15598 | 0.14506 | 0.25778 | -0.41696 | -0.38103 | -0.36835 | -0.33242
1366.5781 | 121.6873 | -0.23804 | 121.4081 | -0.038393 | -0.15957 | -0.098993 | -0.15779 | -0.06445 | -0.083817 | -0.20922 | -0.27716 | -0.16346 | -0.22398 | -0.19337 | 0.13522 | 0.1102 | 0.09471 | 0.212 | 0.007383 | -0.11379 | -0.053217 | -0.11202 | -0.018674 | -0.038041 | -0.16344 | -0.23139 | -0.11768 | -0.1782 | -0.14759 | 0.181 | 0.15598 | 0.14049 | 0.25778 | -0.41239 | -0.37187 | -0.3592 | -0.31869
1368.3438 | 121.7422 | -0.20599 | 121.3898 | -0.033814 | -0.16415 | -0.098993 | -0.15779 | -0.059872 | -0.088396 | -0.21838 | -0.28174 | -0.16346 | -0.22398 | -0.18879 | 0.13064 | 0.1102 | 0.10387 | 0.19827 | 0.011962 | -0.11837 | -0.053217 | -0.11202 | -0.014096 | -0.04262 | -0.1726 | -0.23597 | -0.11768 | -0.1782 | -0.14301 | 0.17642 | 0.15598 | 0.14964 | 0.24404 | -0.41239 | -0.38561 | -0.35462 | -0.32784
1370.1094 | 121.6736 | -0.24261 | 121.4401 | -0.042971 | -0.16873 | -0.094414 | -0.15321 | -0.059872 | -0.092974 | -0.2138 | -0.27716 | -0.16346 | -0.22398 | -0.20253 | 0.13064 | 0.1102 | 0.099289 | 0.20285 | 0.002805 | -0.12295 | -0.048638 | -0.10744 | -0.014096 | -0.047198 | -0.16802 | -0.23139 | -0.11768 | -0.1782 | -0.15675 | 0.17642 | 0.15598 | 0.14506 | 0.24862 | -0.40781 | -0.37645 | -0.35462 | -0.32327
1371.875 | 121.7148 | -0.23804 | 121.3989 | -0.038393 | -0.16415 | -0.094414 | -0.15321 | -0.059872 | -0.088396 | -0.20922 | -0.28174 | -0.16346 | -0.22856 | -0.19795 | 0.1398 | 0.11936 | 0.099289 | 0.20285 | 0.007383 | -0.11837 | -0.048638 | -0.10744 | -0.014096 | -0.04262 | -0.16344 | -0.23597 | -0.11768 | -0.18278 | -0.15217 | 0.18557 | 0.16514 | 0.14506 | 0.24862 | -0.42154 | -0.38103 | -0.36835 | -0.32784
1373.5781 | 121.7514 | -0.21515 | 121.3989 | -0.038393 | -0.16873 | -0.089836 | -0.16237 | -0.06445 | -0.079239 | -0.20922 | -0.27716 | -0.15888 | -0.22398 | -0.19337 | 0.13522 | 0.11936 | 0.099289 | 0.20742 | 0.007383 | -0.12295 | -0.04406 | -0.1166 | -0.018674 | -0.033463 | -0.16344 | -0.23139 | -0.1131 | -0.1782 | -0.14759 | 0.181 | 0.16514 | 0.14506 | 0.2532 | -0.41239 | -0.37645 | -0.3592 | -0.32327
1375.2812 | 121.6873 | -0.24719 | 121.4264 | -0.038393 | -0.15957 | -0.094414 | -0.15779 | -0.059872 | -0.088396 | -0.20464 | -0.27716 | -0.15888 | -0.2194 | -0.18879 | 0.1398 | 0.11478 | 0.099289 | 0.20285 | 0.007383 | -0.11379 | -0.048638 | -0.11202 | -0.014096 | -0.04262 | -0.15886 | -0.23139 | -0.1131 | -0.17362 | -0.14301 | 0.18557 | 0.16056 | 0.14506 | 0.24862 | -0.41696 | -0.37645 | -0.3592 | -0.31869
1377 | 121.7056 | -0.20142 | 121.431 | -0.042971 | -0.15499 | -0.089836 | -0.15779 | -0.055294 | -0.083817 | -0.20922 | -0.2909 | -0.16346 | -0.22398 | -0.19795 | 0.13522 | 0.11478 | 0.09471 | 0.20285 | 0.002805 | -0.10921 | -0.04406 | -0.11202 | -0.009518 | -0.038041 | -0.16344 | -0.24512 | -0.11768 | -0.1782 | -0.15217 | 0.181 | 0.16056 | 0.14049 | 0.24862 | -0.42612 | -0.38561 | -0.3592 | -0.31869
1378.7656 | 121.7239 | -0.2243 | 121.4218 | -0.033814 | -0.16415 | -0.094414 | -0.16237 | -0.059872 | -0.088396 | -0.2138 | -0.27716 | -0.16804 | -0.22398 | -0.19337 | 0.1398 | 0.11478 | 0.10387 | 0.19369 | 0.011962 | -0.11837 | -0.048638 | -0.1166 | -0.014096 | -0.04262 | -0.16802 | -0.23139 | -0.12226 | -0.1782 | -0.14759 | 0.18557 | 0.16056 | 0.14964 | 0.23947 | -0.41696 | -0.38103 | -0.36378 | -0.32784
1380.4688 | 121.6095 | -0.25635 | 121.4539 | -0.042971 | -0.16873 | -0.098993 | -0.15321 | -0.046138 | -0.083817 | -0.2138 | -0.28174 | -0.16804 | -0.22856 | -0.18879 | 0.13522 | 0.10562 | 0.10387 | 0.19827 | 0.002805 | -0.12295 | -0.053217 | -0.10744 | -0.000362 | -0.038041 | -0.16802 | -0.23597 | -0.12226 | -0.18278 | -0.14301 | 0.181 | 0.1514 | 0.14964 | 0.24404 | -0.41696 | -0.38561 | -0.36378 | -0.33242
1382.2344 | 121.6324 | -0.24719 | 121.4081 | -0.033814 | -0.16415 | -0.098993 | -0.15321 | -0.06445 | -0.088396 | -0.20464 | -0.28174 | -0.16346 | -0.22398 | -0.18879 | 0.1398 | 0.11478 | 0.09471 | 0.20285 | 0.011962 | -0.11837 | -0.053217 | -0.10744 | -0.018674 | -0.04262 | -0.15886 | -0.23597 | -0.11768 | -0.1782 | -0.14301 | 0.18557 | 0.16056 | 0.14049 | 0.24862 | -0.42154 | -0.37645 | -0.36378 | -0.31869
1383.9844 | 121.637 | -0.2655 | 121.4401 | -0.042971 | -0.16415 | -0.098993 | -0.15779 | -0.055294 | -0.083817 | -0.20922 | -0.27716 | -0.16804 | -0.2194 | -0.19337 | 0.1398 | 0.1102 | 0.09471 | 0.20285 | 0.002805 | -0.11837 | -0.053217 | -0.11202 | -0.009518 | -0.038041 | -0.16344 | -0.23139 | -0.12226 | -0.17362 | -0.14759 | 0.18557 | 0.15598 | 0.14049 | 0.24862 | -0.41696 | -0.37187 | -0.3592 | -0.31411
1385.75 | 121.6644 | -0.25635 | 121.4401 | -0.033814 | -0.15499 | -0.094414 | -0.15779 | -0.055294 | -0.083817 | -0.2138 | -0.28174 | -0.15888 | -0.2194 | -0.19337 | 0.13064 | 0.1102 | 0.099289 | 0.20285 | 0.011962 | -0.10921 | -0.048638 | -0.11202 | -0.009518 | -0.038041 | -0.16802 | -0.23597 | -0.1131 | -0.17362 | -0.14759 | 0.17642 | 0.15598 | 0.14506 | 0.24862 | -0.41239 | -0.38103 | -0.35004 | -0.31869
1387.5156 | 121.7651 | -0.19684 | 121.3852 | -0.042971 | -0.16415 | -0.098993 | -0.15321 | -0.059872 | -0.083817 | -0.20922 | -0.28632 | -0.15888 | -0.23313 | -0.19337 | 0.13522 | 0.1102 | 0.090132 | 0.20285 | 0.002805 | -0.11837 | -0.053217 | -0.10744 | -0.014096 | -0.038041 | -0.16344 | -0.24055 | -0.1131 | -0.18736 | -0.14759 | 0.181 | 0.15598 | 0.13591 | 0.24862 | -0.42154 | -0.37645 | -0.36835 | -0.32327
1389.2812 | 121.6644 | -0.22888 | 121.4447 | -0.029236 | -0.15957 | -0.089836 | -0.16237 | -0.050716 | -0.083817 | -0.20464 | -0.27716 | -0.16804 | -0.22398 | -0.19795 | 0.13522 | 0.10562 | 0.09471 | 0.19827 | 0.01654 | -0.11379 | -0.04406 | -0.1166 | -0.00494 | -0.038041 | -0.15886 | -0.23139 | -0.12226 | -0.1782 | -0.15217 | 0.181 | 0.1514 | 0.14049 | 0.24404 | -0.41239 | -0.37187 | -0.3592 | -0.31869
1391.0625 | 121.701 | -0.23346 | 121.4172 | -0.033814 | -0.16415 | -0.089836 | -0.15779 | -0.059872 | -0.079239 | -0.2138 | -0.28174 | -0.16804 | -0.2194 | -0.18879 | 0.13064 | 0.096469 | 0.09471 | 0.19827 | 0.011962 | -0.11837 | -0.04406 | -0.11202 | -0.014096 | -0.033463 | -0.16802 | -0.23597 | -0.12226 | -0.17362 | -0.14301 | 0.17642 | 0.14225 | 0.14049 | 0.24404 | -0.41239 | -0.37645 | -0.35004 | -0.31411
1392.8438 | 121.6324 | -0.24261 | 121.431 | -0.033814 | -0.15957 | -0.089836 | -0.15779 | -0.055294 | -0.083817 | -0.20464 | -0.27716 | -0.17262 | -0.22398 | -0.18879 | 0.13522 | 0.10562 | 0.090132 | 0.20285 | 0.011962 | -0.11379 | -0.04406 | -0.11202 | -0.009518 | -0.038041 | -0.15886 | -0.23139 | -0.12684 | -0.1782 | -0.14301 | 0.181 | 0.1514 | 0.13591 | 0.24862 | -0.41239 | -0.3673 | -0.3592 | -0.31411
1394.5469 | 121.6415 | -0.2655 | 121.4539 | -0.033814 | -0.15499 | -0.094414 | -0.16237 | -0.046138 | -0.088396 | -0.20006 | -0.27716 | -0.1543 | -0.2194 | -0.19337 | 0.13522 | 0.1102 | 0.09471 | 0.19827 | 0.011962 | -0.10921 | -0.048638 | -0.1166 | -0.000362 | -0.04262 | -0.15429 | -0.23139 | -0.10853 | -0.17362 | -0.14759 | 0.181 | 0.15598 | 0.14049 | 0.24404 | -0.41239 | -0.37187 | -0.35462 | -0.31411
1396.3125 | 121.7606 | -0.19684 | 121.3989 | -0.033814 | -0.15041 | -0.094414 | -0.15779 | -0.050716 | -0.079239 | -0.20922 | -0.28174 | -0.16804 | -0.22398 | -0.18879 | 0.12607 | 0.1102 | 0.099289 | 0.20285 | 0.011962 | -0.10464 | -0.048638 | -0.11202 | -0.00494 | -0.033463 | -0.16344 | -0.23597 | -0.12226 | -0.1782 | -0.14301 | 0.17184 | 0.15598 | 0.14506 | 0.24862 | -0.40781 | -0.38103 | -0.35004 | -0.32327
1398.0781 | 121.6965 | -0.23804 | 121.431 | -0.033814 | -0.15957 | -0.089836 | -0.15321 | -0.055294 | -0.083817 | -0.20464 | -0.28174 | -0.16346 | -0.22856 | -0.19337 | 0.13522 | 0.10562 | 0.09471 | 0.20285 | 0.011962 | -0.11379 | -0.04406 | -0.10744 | -0.009518 | -0.038041 | -0.15886 | -0.23597 | -0.11768 | -0.18278 | -0.14759 | 0.181 | 0.1514 | 0.14049 | 0.24862 | -0.41696 | -0.37645 | -0.36378 | -0.32327
1399.8438 | 121.7422 | -0.20142 | 121.4035 | -0.038393 | -0.15957 | -0.094414 | -0.15779 | -0.055294 | -0.088396 | -0.20922 | -0.27716 | -0.16346 | -0.2194 | -0.19337 | 0.13522 | 0.10562 | 0.10387 | 0.20742 | 0.007383 | -0.11379 | -0.048638 | -0.11202 | -0.009518 | -0.04262 | -0.16344 | -0.23139 | -0.11768 | -0.17362 | -0.14759 | 0.181 | 0.1514 | 0.14964 | 0.2532 | -0.41239 | -0.38103 | -0.35462 | -0.32327
1401.5469 | 121.6736 | -0.24261 | 121.4127 | -0.042971 | -0.15499 | -0.089836 | -0.14864 | -0.055294 | -0.079239 | -0.20922 | -0.28632 | -0.16804 | -0.2194 | -0.18879 | 0.12607 | 0.10562 | 0.099289 | 0.19827 | 0.002805 | -0.10921 | -0.04406 | -0.10286 | -0.009518 | -0.033463 | -0.16344 | -0.24055 | -0.12226 | -0.17362 | -0.14301 | 0.17184 | 0.1514 | 0.14506 | 0.24404 | -0.41239 | -0.38561 | -0.34546 | -0.31869
1403.3125 | 121.6324 | -0.25177 | 121.4127 | -0.029236 | -0.15041 | -0.094414 | -0.15321 | -0.050716 | -0.083817 | -0.20006 | -0.28174 | -0.16346 | -0.2194 | -0.19337 | 0.13522 | 0.10562 | 0.090132 | 0.19827 | 0.01654 | -0.10464 | -0.048638 | -0.10744 | -0.00494 | -0.038041 | -0.15429 | -0.23597 | -0.11768 | -0.17362 | -0.14759 | 0.181 | 0.1514 | 0.13591 | 0.24404 | -0.41696 | -0.37187 | -0.35462 | -0.30953
1405.0156 | 121.6873 | -0.24261 | 121.4584 | -0.033814 | -0.15499 | -0.085257 | -0.15321 | -0.055294 | -0.074661 | -0.20464 | -0.28632 | -0.16804 | -0.22856 | -0.19795 | 0.13064 | 0.1102 | 0.10387 | 0.212 | 0.011962 | -0.10921 | -0.039481 | -0.10744 | -0.009518 | -0.028885 | -0.15886 | -0.24055 | -0.12226 | -0.18278 | -0.15217 | 0.17642 | 0.15598 | 0.14964 | 0.25778 | -0.41696 | -0.39019 | -0.3592 | -0.33242
1406.7812 | 121.6232 | -0.2655 | 121.4539 | -0.038393 | -0.15041 | -0.089836 | -0.16237 | -0.050716 | -0.088396 | -0.20922 | -0.28174 | -0.16804 | -0.2194 | -0.18421 | 0.13064 | 0.1102 | 0.099289 | 0.212 | 0.007383 | -0.10464 | -0.04406 | -0.1166 | -0.00494 | -0.04262 | -0.16344 | -0.23597 | -0.12226 | -0.17362 | -0.13843 | 0.17642 | 0.15598 | 0.14506 | 0.25778 | -0.41239 | -0.38103 | -0.35004 | -0.31869
1408.5469 | 121.7148 | -0.21973 | 121.4127 | -0.029236 | -0.15957 | -0.094414 | -0.15779 | -0.059872 | -0.083817 | -0.20464 | -0.28174 | -0.17262 | -0.2194 | -0.18421 | 0.13522 | 0.10562 | 0.099289 | 0.20742 | 0.01654 | -0.11379 | -0.048638 | -0.11202 | -0.014096 | -0.038041 | -0.15886 | -0.23597 | -0.12684 | -0.17362 | -0.13843 | 0.181 | 0.1514 | 0.14506 | 0.2532 | -0.41696 | -0.38103 | -0.35462 | -0.31869
1410.2656 | 121.7651 | -0.21973 | 121.4218 | -0.029236 | -0.15499 | -0.094414 | -0.14864 | -0.055294 | -0.079239 | -0.20922 | -0.28174 | -0.15888 | -0.22398 | -0.19337 | 0.13522 | 0.10562 | 0.10387 | 0.20742 | 0.01654 | -0.10921 | -0.048638 | -0.10286 | -0.009518 | -0.033463 | -0.16344 | -0.23597 | -0.1131 | -0.1782 | -0.14759 | 0.181 | 0.1514 | 0.14964 | 0.2532 | -0.41696 | -0.38561 | -0.3592 | -0.32784
1412.0312 | 121.7697 | -0.19684 | 121.3852 | -0.038393 | -0.15957 | -0.094414 | -0.15321 | -0.055294 | -0.074661 | -0.20006 | -0.28174 | -0.16346 | -0.21482 | -0.18879 | 0.13522 | 0.096469 | 0.099289 | 0.20742 | 0.007383 | -0.11379 | -0.048638 | -0.10744 | -0.009518 | -0.028885 | -0.15429 | -0.23597 | -0.11768 | -0.16904 | -0.14301 | 0.181 | 0.14225 | 0.14506 | 0.2532 | -0.41696 | -0.38103 | -0.35004 | -0.31411
1413.7344 | 121.6736 | -0.26093 | 121.4081 | -0.024657 | -0.15499 | -0.094414 | -0.15779 | -0.046138 | -0.079239 | -0.20922 | -0.28174 | -0.16346 | -0.21482 | -0.18879 | 0.13064 | 0.1102 | 0.10387 | 0.20285 | 0.021119 | -0.10921 | -0.048638 | -0.11202 | -0.000362 | -0.033463 | -0.16344 | -0.23597 | -0.11768 | -0.16904 | -0.14301 | 0.17642 | 0.15598 | 0.14964 | 0.24862 | -0.41239 | -0.38561 | -0.34546 | -0.31869
1415.5 | 121.7697 | -0.20142 | 121.376 | -0.029236 | -0.15957 | -0.10357 | -0.14864 | -0.050716 | -0.083817 | -0.20464 | -0.28632 | -0.16804 | -0.2194 | -0.18879 | 0.12607 | 0.1102 | 0.099289 | 0.20742 | 0.01654 | -0.11379 | -0.057796 | -0.10286 | -0.00494 | -0.038041 | -0.15886 | -0.24055 | -0.12226 | -0.17362 | -0.14301 | 0.17184 | 0.15598 | 0.14506 | 0.2532 | -0.41239 | -0.38561 | -0.34546 | -0.31869
1417.2188 | 121.7514 | -0.21515 | 121.4035 | -0.029236 | -0.15957 | -0.094414 | -0.15779 | -0.055294 | -0.079239 | -0.20464 | -0.28174 | -0.15888 | -0.22398 | -0.18879 | 0.13064 | 0.1102 | 0.09471 | 0.20742 | 0.01654 | -0.11379 | -0.048638 | -0.11202 | -0.009518 | -0.033463 | -0.15886 | -0.23597 | -0.1131 | -0.1782 | -0.14301 | 0.17642 | 0.15598 | 0.14049 | 0.2532 | -0.41239 | -0.37645 | -0.35462 | -0.31869
1418.9844 | 121.7285 | -0.21973 | 121.4355 | -0.038393 | -0.15041 | -0.085257 | -0.15779 | -0.059872 | -0.083817 | -0.20464 | -0.28174 | -0.16346 | -0.21024 | -0.18879 | 0.13522 | 0.10562 | 0.09471 | 0.19827 | 0.007383 | -0.10464 | -0.039481 | -0.11202 | -0.014096 | -0.038041 | -0.15886 | -0.23597 | -0.11768 | -0.16447 | -0.14301 | 0.181 | 0.1514 | 0.14049 | 0.24404 | -0.41696 | -0.37645 | -0.34546 | -0.30495
1420.6875 | 121.6553 | -0.24719 | 121.4172 | -0.029236 | -0.15957 | -0.094414 | -0.15321 | -0.050716 | -0.083817 | -0.20464 | -0.27259 | -0.1543 | -0.2194 | -0.19337 | 0.13064 | 0.1102 | 0.09471 | 0.20742 | 0.01654 | -0.11379 | -0.048638 | -0.10744 | -0.00494 | -0.038041 | -0.15886 | -0.22681 | -0.10853 | -0.17362 | -0.14759 | 0.17642 | 0.15598 | 0.14049 | 0.2532 | -0.40323 | -0.3673 | -0.35004 | -0.31411
1422.7344 | 121.7926 | -0.19684 | 121.3852 | -0.033814 | -0.15499 | -0.089836 | -0.15779 | -0.055294 | -0.083817 | -0.20922 | -0.27259 | -0.15888 | -0.2194 | -0.18879 | 0.12607 | 0.10562 | 0.09471 | 0.19827 | 0.011962 | -0.10921 | -0.04406 | -0.11202 | -0.009518 | -0.038041 | -0.16344 | -0.22681 | -0.1131 | -0.17362 | -0.14301 | 0.17184 | 0.1514 | 0.14049 | 0.24404 | -0.39865 | -0.3673 | -0.34546 | -0.31411
1426.4531 | 121.6736 | -0.23804 | 121.431 | -0.024657 | -0.15499 | -0.089836 | -0.15779 | -0.050716 | -0.079239 | -0.20464 | -0.27716 | -0.16804 | -0.2194 | -0.18421 | 0.12607 | 0.1102 | 0.099289 | 0.19369 | 0.021119 | -0.10921 | -0.04406 | -0.11202 | -0.00494 | -0.033463 | -0.15886 | -0.23139 | -0.12226 | -0.17362 | -0.13843 | 0.17184 | 0.15598 | 0.14506 | 0.23947 | -0.40323 | -0.37645 | -0.34546 | -0.31869
1430.0938 | 121.7194 | -0.21515 | 121.3989 | -0.033814 | -0.15957 | -0.089836 | -0.14864 | -0.050716 | -0.079239 | -0.20464 | -0.28174 | -0.16346 | -0.2194 | -0.18421 | 0.13522 | 0.10562 | 0.09471 | 0.19827 | 0.011962 | -0.11379 | -0.04406 | -0.10286 | -0.00494 | -0.033463 | -0.15886 | -0.23597 | -0.11768 | -0.17362 | -0.13843 | 0.181 | 0.1514 | 0.14049 | 0.24404 | -0.41696 | -0.37645 | -0.35462 | -0.31411
1435.9375 | 121.7697 | -0.21515 | 121.4081 | -0.033814 | -0.15041 | -0.089836 | -0.15779 | -0.050716 | -0.083817 | -0.20464 | -0.27716 | -0.1543 | -0.21482 | -0.18421 | 0.12607 | 0.10562 | 0.09471 | 0.19827 | 0.011962 | -0.10464 | -0.04406 | -0.11202 | -0.00494 | -0.038041 | -0.15886 | -0.23139 | -0.10853 | -0.16904 | -0.13843 | 0.17184 | 0.1514 | 0.14049 | 0.24404 | -0.40323 | -0.37187 | -0.34088 | -0.30953
1437.7031 | 121.6736 | -0.23346 | 121.4355 | -0.033814 | -0.14583 | -0.089836 | -0.15779 | -0.050716 | -0.079239 | -0.20464 | -0.27259 | -0.16346 | -0.22398 | -0.18879 | 0.13064 | 0.10562 | 0.090132 | 0.19827 | 0.011962 | -0.10006 | -0.04406 | -0.11202 | -0.00494 | -0.033463 | -0.15886 | -0.22681 | -0.11768 | -0.1782 | -0.14301 | 0.17642 | 0.1514 | 0.13591 | 0.24404 | -0.40323 | -0.36272 | -0.35462 | -0.31411
1439.4688 | 121.6644 | -0.24719 | 121.4355 | -0.029236 | -0.14583 | -0.094414 | -0.15321 | -0.046138 | -0.079239 | -0.20464 | -0.28174 | -0.16804 | -0.22398 | -0.18421 | 0.12607 | 0.1102 | 0.09471 | 0.19827 | 0.01654 | -0.10006 | -0.048638 | -0.10744 | -0.000362 | -0.033463 | -0.15886 | -0.23597 | -0.12226 | -0.1782 | -0.13843 | 0.17184 | 0.15598 | 0.14049 | 0.24404 | -0.40781 | -0.37645 | -0.35004 | -0.31869
1441.1719 | 121.637 | -0.25177 | 121.4722 | -0.029236 | -0.15041 | -0.085257 | -0.15321 | -0.050716 | -0.079239 | -0.20006 | -0.28174 | -0.16346 | -0.21482 | -0.18879 | 0.13522 | 0.10105 | 0.090132 | 0.20285 | 0.01654 | -0.10464 | -0.039481 | -0.10744 | -0.00494 | -0.033463 | -0.15429 | -0.23597 | -0.11768 | -0.16904 | -0.14301 | 0.181 | 0.14682 | 0.13591 | 0.24862 | -0.41696 | -0.37187 | -0.35004 | -0.30495
1442.9375 | 121.7651 | -0.2243 | 121.4218 | -0.033814 | -0.15041 | -0.085257 | -0.14864 | -0.050716 | -0.083817 | -0.20464 | -0.27716 | -0.15888 | -0.21482 | -0.18879 | 0.12607 | 0.1102 | 0.09471 | 0.20285 | 0.011962 | -0.10464 | -0.039481 | -0.10286 | -0.00494 | -0.038041 | -0.15886 | -0.23139 | -0.1131 | -0.16904 | -0.14301 | 0.17184 | 0.15598 | 0.14049 | 0.24862 | -0.40323 | -0.37187 | -0.34088 | -0.30953
1444.6562 | 121.7514 | -0.20142 | 121.4127 | -0.033814 | -0.15499 | -0.085257 | -0.15321 | -0.046138 | -0.074661 | -0.20464 | -0.27259 | -0.16804 | -0.21482 | -0.18879 | 0.13064 | 0.10562 | 0.090132 | 0.20742 | 0.011962 | -0.10921 | -0.039481 | -0.10744 | -0.000362 | -0.028885 | -0.15886 | -0.22681 | -0.12226 | -0.16904 | -0.14301 | 0.17642 | 0.1514 | 0.13591 | 0.2532 | -0.40323 | -0.36272 | -0.34546 | -0.30495
1446.4062 | 121.7285 | -0.21515 | 121.431 | -0.029236 | -0.15499 | -0.085257 | -0.15779 | -0.041561 | -0.079239 | -0.20006 | -0.28174 | -0.16346 | -0.21482 | -0.18421 | 0.13064 | 0.1102 | 0.085554 | 0.19369 | 0.01654 | -0.10921 | -0.039481 | -0.11202 | 0.004215 | -0.033463 | -0.15429 | -0.23597 | -0.11768 | -0.16904 | -0.13843 | 0.17642 | 0.15598 | 0.13133 | 0.23947 | -0.41239 | -0.3673 | -0.34546 | -0.30037
1448.1719 | 121.7697 | -0.18768 | 121.4035 | -0.029236 | -0.15041 | -0.089836 | -0.14864 | -0.046138 | -0.079239 | -0.20464 | -0.2909 | -0.15888 | -0.22398 | -0.18879 | 0.12607 | 0.10562 | 0.099289 | 0.20285 | 0.01654 | -0.10464 | -0.04406 | -0.10286 | -0.000362 | -0.033463 | -0.15886 | -0.24512 | -0.1131 | -0.1782 | -0.14301 | 0.17184 | 0.1514 | 0.14506 | 0.24862 | -0.41696 | -0.39019 | -0.35004 | -0.32327
1449.875 | 121.7697 | -0.20142 | 121.4493 | -0.033814 | -0.15041 | -0.080679 | -0.14864 | -0.046138 | -0.079239 | -0.19548 | -0.27259 | -0.15888 | -0.21482 | -0.18421 | 0.13064 | 0.10105 | 0.09471 | 0.19369 | 0.011962 | -0.10464 | -0.034903 | -0.10286 | -0.000362 | -0.033463 | -0.14971 | -0.22681 | -0.1131 | -0.16904 | -0.13843 | 0.17642 | 0.14682 | 0.14049 | 0.23947 | -0.40323 | -0.3673 | -0.34546 | -0.30953
1451.5781 | 121.7148 | -0.2243 | 121.3943 | -0.029236 | -0.15041 | -0.094414 | -0.15321 | -0.050716 | -0.079239 | -0.19548 | -0.28632 | -0.15888 | -0.21024 | -0.18421 | 0.13064 | 0.10562 | 0.099289 | 0.20285 | 0.01654 | -0.10464 | -0.048638 | -0.10744 | -0.00494 | -0.033463 | -0.14971 | -0.24055 | -0.1131 | -0.16447 | -0.13843 | 0.17642 | 0.1514 | 0.14506 | 0.24862 | -0.41696 | -0.38561 | -0.34088 | -0.30953
1453.3281 | 121.6507 | -0.26093 | 121.4401 | -0.024657 | -0.15041 | -0.085257 | -0.14864 | -0.050716 | -0.074661 | -0.19548 | -0.27716 | -0.16346 | -0.21482 | -0.19337 | 0.12607 | 0.10105 | 0.09471 | 0.19827 | 0.021119 | -0.10464 | -0.039481 | -0.10286 | -0.00494 | -0.028885 | -0.14971 | -0.23139 | -0.11768 | -0.16904 | -0.14759 | 0.17184 | 0.14682 | 0.14049 | 0.24404 | -0.40323 | -0.37187 | -0.34088 | -0.30953
1455.0469 | 121.7926 | -0.19226 | 121.3989 | -0.033814 | -0.15499 | -0.089836 | -0.15321 | -0.046138 | -0.079239 | -0.20006 | -0.27259 | -0.16804 | -0.2194 | -0.18879 | 0.12149 | 0.10562 | 0.090132 | 0.20285 | 0.011962 | -0.10921 | -0.04406 | -0.10744 | -0.000362 | -0.033463 | -0.15429 | -0.22681 | -0.12226 | -0.17362 | -0.14301 | 0.16726 | 0.1514 | 0.13591 | 0.24862 | -0.39407 | -0.36272 | -0.34088 | -0.30953
1456.8125 | 121.6415 | -0.27008 | 121.431 | -0.029236 | -0.15499 | -0.098993 | -0.14864 | -0.055294 | -0.088396 | -0.19548 | -0.27716 | -0.15888 | -0.21024 | -0.19337 | 0.13064 | 0.10105 | 0.080975 | 0.19827 | 0.01654 | -0.10921 | -0.053217 | -0.10286 | -0.009518 | -0.04262 | -0.14971 | -0.23139 | -0.1131 | -0.16447 | -0.14759 | 0.17642 | 0.14682 | 0.12675 | 0.24404 | -0.40781 | -0.35814 | -0.34088 | -0.29122
1458.5781 | 121.756 | -0.19684 | 121.4081 | -0.029236 | -0.14583 | -0.085257 | -0.15321 | -0.046138 | -0.074661 | -0.20006 | -0.28174 | -0.15888 | -0.2194 | -0.18879 | 0.13064 | 0.10105 | 0.09471 | 0.19369 | 0.01654 | -0.10006 | -0.039481 | -0.10744 | -0.000362 | -0.028885 | -0.15429 | -0.23597 | -0.1131 | -0.17362 | -0.14301 | 0.17642 | 0.14682 | 0.14049 | 0.23947 | -0.41239 | -0.37645 | -0.35004 | -0.31411
1460.2656 | 121.6324 | -0.24261 | 121.4493 | -0.029236 | -0.15499 | -0.085257 | -0.14406 | -0.050716 | -0.079239 | -0.20006 | -0.27716 | -0.16346 | -0.21482 | -0.18421 | 0.12607 | 0.10562 | 0.09471 | 0.19369 | 0.01654 | -0.10921 | -0.039481 | -0.098282 | -0.00494 | -0.033463 | -0.15429 | -0.23139 | -0.11768 | -0.16904 | -0.13843 | 0.17184 | 0.1514 | 0.14049 | 0.23947 | -0.40323 | -0.37187 | -0.34088 | -0.30953
1462.0312 | 121.7834 | -0.20142 | 121.4081 | -0.029236 | -0.15957 | -0.085257 | -0.14406 | -0.046138 | -0.074661 | -0.20006 | -0.28174 | -0.15888 | -0.21024 | -0.18879 | 0.12607 | 0.10105 | 0.099289 | 0.20285 | 0.01654 | -0.11379 | -0.039481 | -0.098282 | -0.000362 | -0.028885 | -0.15429 | -0.23597 | -0.1131 | -0.16447 | -0.14301 | 0.17184 | 0.14682 | 0.14506 | 0.24862 | -0.40781 | -0.38103 | -0.33631 | -0.30953
1463.7344 | 121.701 | -0.21973 | 121.4081 | -0.029236 | -0.15041 | -0.080679 | -0.15321 | -0.050716 | -0.079239 | -0.19548 | -0.28632 | -0.16804 | -0.2194 | -0.19337 | 0.13064 | 0.1102 | 0.09471 | 0.20285 | 0.01654 | -0.10464 | -0.034903 | -0.10744 | -0.00494 | -0.033463 | -0.14971 | -0.24055 | -0.12226 | -0.17362 | -0.14759 | 0.17642 | 0.15598 | 0.14049 | 0.24862 | -0.41696 | -0.38103 | -0.35004 | -0.31411
1465.5 | 121.6782 | -0.25177 | 121.4493 | -0.033814 | -0.15499 | -0.094414 | -0.14864 | -0.046138 | -0.088396 | -0.20006 | -0.28174 | -0.15888 | -0.2194 | -0.18421 | 0.12607 | 0.10105 | 0.09471 | 0.19827 | 0.011962 | -0.10921 | -0.048638 | -0.10286 | -0.000362 | -0.04262 | -0.15429 | -0.23597 | -0.1131 | -0.17362 | -0.13843 | 0.17184 | 0.14682 | 0.14049 | 0.24404 | -0.40781 | -0.37645 | -0.34546 | -0.31411
1467.2812 | 121.6278 | -0.25635 | 121.4584 | -0.024657 | -0.15041 | -0.085257 | -0.15321 | -0.055294 | -0.079239 | -0.19091 | -0.28174 | -0.16346 | -0.2194 | -0.18879 | 0.12607 | 0.11478 | 0.09471 | 0.19827 | 0.021119 | -0.10464 | -0.039481 | -0.10744 | -0.009518 | -0.033463 | -0.14513 | -0.23597 | -0.11768 | -0.17362 | -0.14301 | 0.17184 | 0.16056 | 0.14049 | 0.24404 | -0.40781 | -0.37645 | -0.34546 | -0.31411
1468.9844 | 121.7239 | -0.2243 | 121.4172 | -0.029236 | -0.15499 | -0.085257 | -0.15779 | -0.055294 | -0.079239 | -0.20464 | -0.28174 | -0.15888 | -0.21482 | -0.18421 | 0.13064 | 0.10562 | 0.099289 | 0.19827 | 0.01654 | -0.10921 | -0.039481 | -0.11202 | -0.009518 | -0.033463 | -0.15886 | -0.23597 | -0.1131 | -0.16904 | -0.13843 | 0.17642 | 0.1514 | 0.14506 | 0.24404 | -0.41239 | -0.38103 | -0.34546 | -0.31411
1470.7656 | 121.6324 | -0.24719 | 121.463 | -0.029236 | -0.15499 | -0.089836 | -0.14864 | -0.050716 | -0.074661 | -0.20464 | -0.28174 | -0.16804 | -0.21482 | -0.19795 | 0.12607 | 0.10562 | 0.09471 | 0.19369 | 0.01654 | -0.10921 | -0.04406 | -0.10286 | -0.00494 | -0.028885 | -0.15886 | -0.23597 | -0.12226 | -0.16904 | -0.15217 | 0.17184 | 0.1514 | 0.14049 | 0.23947 | -0.40781 | -0.37645 | -0.34088 | -0.30953
1472.4531 | 121.7697 | -0.1831 | 121.4127 | -0.024657 | -0.15041 | -0.085257 | -0.15321 | -0.050716 | -0.079239 | -0.20464 | -0.28632 | -0.16804 | -0.21482 | -0.18879 | 0.13064 | 0.096469 | 0.09471 | 0.19827 | 0.021119 | -0.10464 | -0.039481 | -0.10744 | -0.00494 | -0.033463 | -0.15886 | -0.24055 | -0.12226 | -0.16904 | -0.14301 | 0.17642 | 0.14225 | 0.14049 | 0.24404 | -0.41696 | -0.38103 | -0.34546 | -0.30953
1474.2344 | 121.756 | -0.21973 | 121.4127 | -0.024657 | -0.14583 | -0.089836 | -0.14864 | -0.050716 | -0.079239 | -0.20464 | -0.27716 | -0.15888 | -0.2194 | -0.18879 | 0.13522 | 0.10105 | 0.085554 | 0.18911 | 0.021119 | -0.10006 | -0.04406 | -0.10286 | -0.00494 | -0.033463 | -0.15886 | -0.23139 | -0.1131 | -0.17362 | -0.14301 | 0.181 | 0.14682 | 0.13133 | 0.23489 | -0.41239 | -0.36272 | -0.35462 | -0.30495
1476 | 121.756 | -0.19226 | 121.4081 | -0.029236 | -0.15041 | -0.085257 | -0.14406 | -0.046138 | -0.083817 | -0.20464 | -0.27716 | -0.16346 | -0.21482 | -0.18421 | 0.13064 | 0.10562 | 0.080975 | 0.19369 | 0.01654 | -0.10464 | -0.039481 | -0.098282 | -0.000362 | -0.038041 | -0.15886 | -0.23139 | -0.11768 | -0.16904 | -0.13843 | 0.17642 | 0.1514 | 0.12675 | 0.23947 | -0.40781 | -0.35814 | -0.34546 | -0.2958
1477.7031 | 121.7789 | -0.19226 | 121.4127 | -0.029236 | -0.14583 | -0.094414 | -0.15321 | -0.041561 | -0.083817 | -0.20922 | -0.27716 | -0.15888 | -0.2194 | -0.19337 | 0.13064 | 0.10562 | 0.09471 | 0.19369 | 0.01654 | -0.10006 | -0.048638 | -0.10744 | 0.004215 | -0.038041 | -0.16344 | -0.23139 | -0.1131 | -0.17362 | -0.14759 | 0.17642 | 0.1514 | 0.14049 | 0.23947 | -0.40781 | -0.37187 | -0.35004 | -0.31411
1479.4688 | 121.7606 | -0.18768 | 121.4035 | -0.033814 | -0.15499 | -0.080679 | -0.16237 | -0.050716 | -0.074661 | -0.20006 | -0.28174 | -0.15888 | -0.22398 | -0.18879 | 0.13522 | 0.10562 | 0.09471 | 0.19369 | 0.011962 | -0.10921 | -0.034903 | -0.1166 | -0.00494 | -0.028885 | -0.15429 | -0.23597 | -0.1131 | -0.1782 | -0.14301 | 0.181 | 0.1514 | 0.14049 | 0.23947 | -0.41696 | -0.37645 | -0.3592 | -0.31869
1481.1719 | 121.6873 | -0.20142 | 121.4172 | -0.029236 | -0.15957 | -0.089836 | -0.14864 | -0.050716 | -0.079239 | -0.20922 | -0.27716 | -0.16346 | -0.2194 | -0.18421 | 0.12149 | 0.1102 | 0.090132 | 0.19369 | 0.01654 | -0.11379 | -0.04406 | -0.10286 | -0.00494 | -0.033463 | -0.16344 | -0.23139 | -0.11768 | -0.17362 | -0.13843 | 0.16726 | 0.15598 | 0.13591 | 0.23947 | -0.39865 | -0.3673 | -0.34088 | -0.30953
1482.9375 | 121.7194 | -0.21057 | 121.4355 | -0.029236 | -0.15041 | -0.094414 | -0.14864 | -0.046138 | -0.079239 | -0.19548 | -0.27716 | -0.16346 | -0.21024 | -0.17963 | 0.12607 | 0.10562 | 0.090132 | 0.19369 | 0.01654 | -0.10464 | -0.048638 | -0.10286 | -0.000362 | -0.033463 | -0.14971 | -0.23139 | -0.11768 | -0.16447 | -0.13385 | 0.17184 | 0.1514 | 0.13591 | 0.23947 | -0.40323 | -0.3673 | -0.33631 | -0.30037
1484.6719 | 121.6827 | -0.23804 | 121.463 | -0.029236 | -0.15957 | -0.089836 | -0.14864 | -0.055294 | -0.079239 | -0.20006 | -0.27716 | -0.16346 | -0.2194 | -0.18421 | 0.13064 | 0.10562 | 0.099289 | 0.19369 | 0.01654 | -0.11379 | -0.04406 | -0.10286 | -0.009518 | -0.033463 | -0.15429 | -0.23139 | -0.11768 | -0.17362 | -0.13843 | 0.17642 | 0.1514 | 0.14506 | 0.23947 | -0.40781 | -0.37645 | -0.35004 | -0.31869
1486.4375 | 121.6232 | -0.25635 | 121.463 | -0.020079 | -0.14583 | -0.089836 | -0.14406 | -0.046138 | -0.083817 | -0.20006 | -0.28632 | -0.16346 | -0.21482 | -0.18879 | 0.13064 | 0.10562 | 0.090132 | 0.19369 | 0.025697 | -0.10006 | -0.04406 | -0.098282 | -0.000362 | -0.038041 | -0.15429 | -0.24055 | -0.11768 | -0.16904 | -0.14301 | 0.17642 | 0.1514 | 0.13591 | 0.23947 | -0.41696 | -0.37645 | -0.34546 | -0.30495
1488.1406 | 121.6461 | -0.23804 | 121.4584 | -0.024657 | -0.15041 | -0.098993 | -0.14864 | -0.046138 | -0.083817 | -0.19548 | -0.27259 | -0.15888 | -0.21482 | -0.17963 | 0.12607 | 0.1102 | 0.090132 | 0.19827 | 0.021119 | -0.10464 | -0.053217 | -0.10286 | -0.000362 | -0.038041 | -0.14971 | -0.22681 | -0.1131 | -0.16904 | -0.13385 | 0.17184 | 0.15598 | 0.13591 | 0.24404 | -0.39865 | -0.36272 | -0.34088 | -0.30495
1489.9062 | 121.7285 | -0.20599 | 121.4081 | -0.029236 | -0.14583 | -0.085257 | -0.14864 | -0.050716 | -0.074661 | -0.19548 | -0.28174 | -0.16804 | -0.22398 | -0.18421 | 0.12607 | 0.10562 | 0.090132 | 0.19827 | 0.01654 | -0.10006 | -0.039481 | -0.10286 | -0.00494 | -0.028885 | -0.14971 | -0.23597 | -0.12226 | -0.1782 | -0.13843 | 0.17184 | 0.1514 | 0.13591 | 0.24404 | -0.40781 | -0.37187 | -0.35004 | -0.31411
1491.6094 | 121.7651 | -0.20599 | 121.4447 | -0.029236 | -0.15041 | -0.089836 | -0.14864 | -0.050716 | -0.079239 | -0.20006 | -0.27716 | -0.15888 | -0.21482 | -0.18879 | 0.12607 | 0.10105 | 0.09471 | 0.19369 | 0.01654 | -0.10464 | -0.04406 | -0.10286 | -0.00494 | -0.033463 | -0.15429 | -0.23139 | -0.1131 | -0.16904 | -0.14301 | 0.17184 | 0.14682 | 0.14049 | 0.23947 | -0.40323 | -0.37187 | -0.34088 | -0.30953
1493.375 | 121.756 | -0.19226 | 121.4081 | -0.029236 | -0.15041 | -0.089836 | -0.14406 | -0.050716 | -0.079239 | -0.20006 | -0.28174 | -0.1543 | -0.21482 | -0.18421 | 0.13064 | 0.1102 | 0.090132 | 0.19369 | 0.01654 | -0.10464 | -0.04406 | -0.098282 | -0.00494 | -0.033463 | -0.15429 | -0.23597 | -0.10853 | -0.16904 | -0.13843 | 0.17642 | 0.15598 | 0.13591 | 0.23947 | -0.41239 | -0.37187 | -0.34546 | -0.30495
1495.0781 | 121.6782 | -0.24261 | 121.4218 | -0.029236 | -0.15499 | -0.089836 | -0.14864 | -0.059872 | -0.079239 | -0.20006 | -0.27259 | -0.16346 | -0.21482 | -0.18421 | 0.13064 | 0.10105 | 0.090132 | 0.19369 | 0.01654 | -0.10921 | -0.04406 | -0.10286 | -0.014096 | -0.033463 | -0.15429 | -0.22681 | -0.11768 | -0.16904 | -0.13843 | 0.17642 | 0.14682 | 0.13591 | 0.23947 | -0.40323 | -0.36272 | -0.34546 | -0.30495
1496.8438 | 121.6782 | -0.24261 | 121.463 | -0.033814 | -0.15957 | -0.085257 | -0.14406 | -0.050716 | -0.070082 | -0.20006 | -0.28632 | -0.16346 | -0.21482 | -0.18421 | 0.12607 | 0.10105 | 0.090132 | 0.19369 | 0.011962 | -0.11379 | -0.039481 | -0.098282 | -0.00494 | -0.024306 | -0.15429 | -0.24055 | -0.11768 | -0.16904 | -0.13843 | 0.17184 | 0.14682 | 0.13591 | 0.23947 | -0.41239 | -0.37645 | -0.34088 | -0.30495
1498.5469 | 121.7056 | -0.2243 | 121.4539 | -0.029236 | -0.15041 | -0.080679 | -0.15779 | -0.046138 | -0.083817 | -0.19548 | -0.27716 | -0.16346 | -0.2194 | -0.17963 | 0.13064 | 0.10105 | 0.080975 | 0.19369 | 0.01654 | -0.10464 | -0.034903 | -0.11202 | -0.000362 | -0.038041 | -0.14971 | -0.23139 | -0.11768 | -0.17362 | -0.13385 | 0.17642 | 0.14682 | 0.12675 | 0.23947 | -0.40781 | -0.35814 | -0.35004 | -0.30037
1500.3125 | 121.669 | -0.23346 | 121.4447 | -0.024657 | -0.14583 | -0.085257 | -0.14406 | -0.050716 | -0.083817 | -0.19548 | -0.27259 | -0.15888 | -0.21482 | -0.19337 | 0.12607 | 0.10105 | 0.09471 | 0.19369 | 0.021119 | -0.10006 | -0.039481 | -0.098282 | -0.00494 | -0.038041 | -0.14971 | -0.22681 | -0.1131 | -0.16904 | -0.14759 | 0.17184 | 0.14682 | 0.14049 | 0.23947 | -0.39865 | -0.3673 | -0.34088 | -0.30953
1502.0781 | 121.6919 | -0.23804 | 121.431 | -0.020079 | -0.15499 | -0.085257 | -0.14406 | -0.046138 | -0.079239 | -0.20006 | -0.27716 | -0.15888 | -0.21482 | -0.18879 | 0.12149 | 0.10562 | 0.090132 | 0.19369 | 0.025697 | -0.10921 | -0.039481 | -0.098282 | -0.000362 | -0.033463 | -0.15429 | -0.23139 | -0.1131 | -0.16904 | -0.14301 | 0.16726 | 0.1514 | 0.13591 | 0.23947 | -0.39865 | -0.3673 | -0.33631 | -0.30495
1503.7812 | 121.7239 | -0.21057 | 121.4127 | -0.029236 | -0.16415 | -0.080679 | -0.13948 | -0.050716 | -0.079239 | -0.20922 | -0.27716 | -0.15888 | -0.21482 | -0.18421 | 0.13064 | 0.10562 | 0.09471 | 0.19827 | 0.01654 | -0.11837 | -0.034903 | -0.093703 | -0.00494 | -0.033463 | -0.16344 | -0.23139 | -0.1131 | -0.16904 | -0.13843 | 0.17642 | 0.1514 | 0.14049 | 0.24404 | -0.40781 | -0.37187 | -0.34546 | -0.30953
1505.5625 | 121.756 | -0.20142 | 121.4172 | -0.038393 | -0.15957 | -0.089836 | -0.14864 | -0.046138 | -0.079239 | -0.20006 | -0.28174 | -0.15888 | -0.21024 | -0.19337 | 0.12607 | 0.11478 | 0.085554 | 0.19827 | 0.007383 | -0.11379 | -0.04406 | -0.10286 | -0.000362 | -0.033463 | -0.15429 | -0.23597 | -0.1131 | -0.16447 | -0.14759 | 0.17184 | 0.16056 | 0.13133 | 0.24404 | -0.40781 | -0.3673 | -0.33631 | -0.2958
1507.3281 | 121.6599 | -0.25177 | 121.4539 | -0.029236 | -0.15041 | -0.089836 | -0.14406 | -0.046138 | -0.083817 | -0.19548 | -0.28632 | -0.16346 | -0.21482 | -0.18879 | 0.13064 | 0.10105 | 0.090132 | 0.19369 | 0.01654 | -0.10464 | -0.04406 | -0.098282 | -0.000362 | -0.038041 | -0.14971 | -0.24055 | -0.11768 | -0.16904 | -0.14301 | 0.17642 | 0.14682 | 0.13591 | 0.23947 | -0.41696 | -0.37645 | -0.34546 | -0.30495
1509.0156 | 121.7651 | -0.20142 | 121.431 | -0.029236 | -0.15041 | -0.089836 | -0.14864 | -0.050716 | -0.074661 | -0.20464 | -0.27716 | -0.16346 | -0.21482 | -0.19337 | 0.12607 | 0.10105 | 0.090132 | 0.19369 | 0.01654 | -0.10464 | -0.04406 | -0.10286 | -0.00494 | -0.028885 | -0.15886 | -0.23139 | -0.11768 | -0.16904 | -0.14759 | 0.17184 | 0.14682 | 0.13591 | 0.23947 | -0.40323 | -0.3673 | -0.34088 | -0.30495
1510.7969 | 121.7239 | -0.23346 | 121.4493 | -0.024657 | -0.15041 | -0.089836 | -0.15321 | -0.050716 | -0.074661 | -0.20006 | -0.27716 | -0.15888 | -0.21024 | -0.17963 | 0.12607 | 0.10105 | 0.090132 | 0.19369 | 0.021119 | -0.10464 | -0.04406 | -0.10744 | -0.00494 | -0.028885 | -0.15429 | -0.23139 | -0.1131 | -0.16447 | -0.13385 | 0.17184 | 0.14682 | 0.13591 | 0.23947 | -0.40323 | -0.3673 | -0.33631 | -0.30037
1512.5 | 121.6599 | -0.22888 | 121.4539 | -0.024657 | -0.14583 | -0.085257 | -0.15321 | -0.041561 | -0.079239 | -0.20006 | -0.28632 | -0.16804 | -0.2194 | -0.18421 | 0.13064 | 0.096469 | 0.090132 | 0.18911 | 0.021119 | -0.10006 | -0.039481 | -0.10744 | 0.004215 | -0.033463 | -0.15429 | -0.24055 | -0.12226 | -0.17362 | -0.13843 | 0.17642 | 0.14225 | 0.13591 | 0.23489 | -0.41696 | -0.37645 | -0.35004 | -0.30953
1514.2656 | 121.6461 | -0.23804 | 121.4539 | -0.024657 | -0.14583 | -0.089836 | -0.14864 | -0.041561 | -0.079239 | -0.20006 | -0.27716 | -0.1543 | -0.21482 | -0.19337 | 0.13064 | 0.10562 | 0.085554 | 0.19369 | 0.021119 | -0.10006 | -0.04406 | -0.10286 | 0.004215 | -0.033463 | -0.15429 | -0.23139 | -0.10853 | -0.16904 | -0.14759 | 0.17642 | 0.1514 | 0.13133 | 0.23947 | -0.40781 | -0.36272 | -0.34546 | -0.30037
1516.0156 | 121.637 | -0.23804 | 121.463 | -0.024657 | -0.15041 | -0.089836 | -0.14406 | -0.050716 | -0.079239 | -0.19091 | -0.27716 | -0.15888 | -0.21024 | -0.17963 | 0.12149 | 0.10105 | 0.085554 | 0.18911 | 0.021119 | -0.10464 | -0.04406 | -0.098282 | -0.00494 | -0.033463 | -0.14513 | -0.23139 | -0.1131 | -0.16447 | -0.13385 | 0.16726 | 0.14682 | 0.13133 | 0.23489 | -0.39865 | -0.36272 | -0.33173 | -0.2958
1517.7188 | 121.7697 | -0.18768 | 121.4035 | -0.024657 | -0.15041 | -0.085257 | -0.14864 | -0.041561 | -0.079239 | -0.19091 | -0.28174 | -0.16346 | -0.21482 | -0.18879 | 0.13064 | 0.096469 | 0.090132 | 0.19369 | 0.021119 | -0.10464 | -0.039481 | -0.10286 | 0.004215 | -0.033463 | -0.14513 | -0.23597 | -0.11768 | -0.16904 | -0.14301 | 0.17642 | 0.14225 | 0.13591 | 0.23947 | -0.41239 | -0.37187 | -0.34546 | -0.30495
1519.4844 | 121.6278 | -0.25635 | 121.463 | -0.024657 | -0.15041 | -0.080679 | -0.14864 | -0.046138 | -0.079239 | -0.19091 | -0.27716 | -0.16346 | -0.21482 | -0.18421 | 0.12607 | 0.10562 | 0.076397 | 0.19369 | 0.021119 | -0.10464 | -0.034903 | -0.10286 | -0.000362 | -0.033463 | -0.14513 | -0.23139 | -0.11768 | -0.16904 | -0.13843 | 0.17184 | 0.1514 | 0.12217 | 0.23947 | -0.40323 | -0.35356 | -0.34088 | -0.29122
1521.25 | 121.7789 | -0.18768 | 121.4218 | -0.033814 | -0.14583 | -0.080679 | -0.13948 | -0.046138 | -0.074661 | -0.19548 | -0.27716 | -0.1543 | -0.21482 | -0.17963 | 0.13064 | 0.10105 | 0.085554 | 0.18911 | 0.011962 | -0.10006 | -0.034903 | -0.093703 | -0.000362 | -0.028885 | -0.14971 | -0.23139 | -0.10853 | -0.16904 | -0.13385 | 0.17642 | 0.14682 | 0.13133 | 0.23489 | -0.40781 | -0.36272 | -0.34546 | -0.30037
1522.9531 | 121.6461 | -0.22888 | 121.4493 | -0.020079 | -0.15957 | -0.080679 | -0.14406 | -0.046138 | -0.074661 | -0.20006 | -0.28174 | -0.1543 | -0.2194 | -0.17963 | 0.12607 | 0.10562 | 0.085554 | 0.19369 | 0.025697 | -0.11379 | -0.034903 | -0.098282 | -0.000362 | -0.028885 | -0.15429 | -0.23597 | -0.10853 | -0.17362 | -0.13385 | 0.17184 | 0.1514 | 0.13133 | 0.23947 | -0.40781 | -0.3673 | -0.34546 | -0.30495
1524.7344 | 121.6461 | -0.24261 | 121.4813 | -0.024657 | -0.15041 | -0.085257 | -0.14864 | -0.050716 | -0.074661 | -0.19548 | -0.27259 | -0.15888 | -0.21024 | -0.18421 | 0.13064 | 0.10562 | 0.090132 | 0.18911 | 0.021119 | -0.10464 | -0.039481 | -0.10286 | -0.00494 | -0.028885 | -0.14971 | -0.22681 | -0.1131 | -0.16447 | -0.13843 | 0.17642 | 0.1514 | 0.13591 | 0.23489 | -0.40323 | -0.36272 | -0.34088 | -0.30037
1526.4844 | 121.669 | -0.22888 | 121.4584 | -0.033814 | -0.15041 | -0.085257 | -0.14864 | -0.046138 | -0.079239 | -0.20006 | -0.27716 | -0.16346 | -0.21024 | -0.18879 | 0.12607 | 0.10105 | 0.080975 | 0.18911 | 0.011962 | -0.10464 | -0.039481 | -0.10286 | -0.000362 | -0.033463 | -0.15429 | -0.23139 | -0.11768 | -0.16447 | -0.14301 | 0.17184 | 0.14682 | 0.12675 | 0.23489 | -0.40323 | -0.35814 | -0.33631 | -0.29122
1528.1875 | 121.7194 | -0.21515 | 121.4218 | -0.024657 | -0.15499 | -0.080679 | -0.15321 | -0.041561 | -0.079239 | -0.20464 | -0.27259 | -0.1543 | -0.21024 | -0.18421 | 0.12607 | 0.096469 | 0.085554 | 0.19369 | 0.021119 | -0.10921 | -0.034903 | -0.10744 | 0.004215 | -0.033463 | -0.15886 | -0.22681 | -0.10853 | -0.16447 | -0.13843 | 0.17184 | 0.14225 | 0.13133 | 0.23947 | -0.39865 | -0.35814 | -0.33631 | -0.2958
1529.9531 | 121.6599 | -0.25635 | 121.4584 | -0.029236 | -0.15041 | -0.080679 | -0.14406 | -0.041561 | -0.074661 | -0.19548 | -0.26343 | -0.15888 | -0.2194 | -0.18421 | 0.13064 | 0.10562 | 0.090132 | 0.19369 | 0.01654 | -0.10464 | -0.034903 | -0.098282 | 0.004215 | -0.028885 | -0.14971 | -0.21765 | -0.1131 | -0.17362 | -0.13843 | 0.17642 | 0.1514 | 0.13591 | 0.23947 | -0.39407 | -0.35356 | -0.35004 | -0.30953
1531.7188 | 121.7606 | -0.17853 | 121.4172 | -0.029236 | -0.15041 | -0.085257 | -0.14864 | -0.041561 | -0.079239 | -0.20006 | -0.28174 | -0.16346 | -0.21024 | -0.18879 | 0.12149 | 0.096469 | 0.090132 | 0.19369 | 0.01654 | -0.10464 | -0.039481 | -0.10286 | 0.004215 | -0.033463 | -0.15429 | -0.23597 | -0.11768 | -0.16447 | -0.14301 | 0.16726 | 0.14225 | 0.13591 | 0.23947 | -0.40323 | -0.37187 | -0.33173 | -0.30037
1533.4688 | 121.7926 | -0.19226 | 121.4035 | -0.024657 | -0.15499 | -0.089836 | -0.13948 | -0.046138 | -0.070082 | -0.19548 | -0.27716 | -0.15888 | -0.20109 | -0.18879 | 0.11691 | 0.10562 | 0.09471 | 0.19369 | 0.021119 | -0.10921 | -0.04406 | -0.093703 | -0.000362 | -0.024306 | -0.14971 | -0.23139 | -0.1131 | -0.15531 | -0.14301 | 0.16268 | 0.1514 | 0.14049 | 0.23947 | -0.39407 | -0.37187 | -0.31799 | -0.2958
1535.25 | 121.7056 | -0.19684 | 121.4447 | -0.020079 | -0.15041 | -0.085257 | -0.14406 | -0.046138 | -0.079239 | -0.20006 | -0.28174 | -0.15888 | -0.21482 | -0.18421 | 0.12149 | 0.10105 | 0.085554 | 0.18911 | 0.025697 | -0.10464 | -0.039481 | -0.098282 | -0.000362 | -0.033463 | -0.15429 | -0.23597 | -0.1131 | -0.16904 | -0.13843 | 0.16726 | 0.14682 | 0.13133 | 0.23489 | -0.40323 | -0.3673 | -0.33631 | -0.30037
1536.9375 | 121.6324 | -0.25177 | 121.4539 | -0.024657 | -0.14125 | -0.080679 | -0.14406 | -0.050716 | -0.070082 | -0.19548 | -0.27716 | -0.16346 | -0.21482 | -0.17963 | 0.13064 | 0.10562 | 0.09471 | 0.18911 | 0.021119 | -0.095479 | -0.034903 | -0.098282 | -0.00494 | -0.024306 | -0.14971 | -0.23139 | -0.11768 | -0.16904 | -0.13385 | 0.17642 | 0.1514 | 0.14049 | 0.23489 | -0.40781 | -0.37187 | -0.34546 | -0.30953
1538.7031 | 121.7789 | -0.19226 | 121.4172 | -0.024657 | -0.14583 | -0.080679 | -0.14406 | -0.041561 | -0.083817 | -0.20006 | -0.27716 | -0.16346 | -0.21024 | -0.18879 | 0.12149 | 0.096469 | 0.090132 | 0.18911 | 0.021119 | -0.10006 | -0.034903 | -0.098282 | 0.004215 | -0.038041 | -0.15429 | -0.23139 | -0.11768 | -0.16447 | -0.14301 | 0.16726 | 0.14225 | 0.13591 | 0.23489 | -0.39865 | -0.3673 | -0.33173 | -0.30037
1540.4688 | 121.6324 | -0.25635 | 121.4584 | -0.024657 | -0.14583 | -0.089836 | -0.14406 | -0.046138 | -0.074661 | -0.20006 | -0.27716 | -0.15888 | -0.21024 | -0.18421 | 0.12149 | 0.10105 | 0.085554 | 0.19369 | 0.021119 | -0.10006 | -0.04406 | -0.098282 | -0.000362 | -0.028885 | -0.15429 | -0.23139 | -0.1131 | -0.16447 | -0.13843 | 0.16726 | 0.14682 | 0.13133 | 0.23947 | -0.39865 | -0.36272 | -0.33173 | -0.2958
1542.1875 | 121.756 | -0.17853 | 121.431 | -0.033814 | -0.15499 | -0.085257 | -0.14406 | -0.046138 | -0.074661 | -0.19548 | -0.26801 | -0.16346 | -0.2194 | -0.17963 | 0.13064 | 0.1102 | 0.085554 | 0.19369 | 0.011962 | -0.10921 | -0.039481 | -0.098282 | -0.000362 | -0.028885 | -0.14971 | -0.22223 | -0.11768 | -0.17362 | -0.13385 | 0.17642 | 0.15598 | 0.13133 | 0.23947 | -0.39865 | -0.35356 | -0.35004 | -0.30495
1543.9375 | 121.6415 | -0.22888 | 121.4401 | -0.020079 | -0.14583 | -0.080679 | -0.14406 | -0.041561 | -0.060926 | -0.19548 | -0.27716 | -0.15888 | -0.21482 | -0.17505 | 0.12607 | 0.10562 | 0.085554 | 0.18453 | 0.025697 | -0.10006 | -0.034903 | -0.098282 | 0.004215 | -0.01515 | -0.14971 | -0.23139 | -0.1131 | -0.16904 | -0.12928 | 0.17184 | 0.1514 | 0.13133 | 0.23031 | -0.40323 | -0.36272 | -0.34088 | -0.30037
1545.6562 | 121.7148 | -0.21973 | 121.4218 | -0.029236 | -0.15041 | -0.089836 | -0.14864 | -0.041561 | -0.079239 | -0.19548 | -0.28174 | -0.1543 | -0.21482 | -0.18879 | 0.13064 | 0.10105 | 0.076397 | 0.18911 | 0.01654 | -0.10464 | -0.04406 | -0.10286 | 0.004215 | -0.033463 | -0.14971 | -0.23597 | -0.10853 | -0.16904 | -0.14301 | 0.17642 | 0.14682 | 0.12217 | 0.23489 | -0.41239 | -0.35814 | -0.34546 | -0.29122
1547.4219 | 121.7468 | -0.17853 | 121.431 | -0.029236 | -0.15499 | -0.085257 | -0.15321 | -0.050716 | -0.074661 | -0.19548 | -0.27259 | -0.1543 | -0.2194 | -0.18421 | 0.11691 | 0.1102 | 0.090132 | 0.18453 | 0.01654 | -0.10921 | -0.039481 | -0.10744 | -0.00494 | -0.028885 | -0.14971 | -0.22681 | -0.10853 | -0.17362 | -0.13843 | 0.16268 | 0.15598 | 0.13591 | 0.23031 | -0.38949 | -0.36272 | -0.33631 | -0.30953
1549.125 | 121.7834 | -0.19226 | 121.4264 | -0.024657 | -0.15041 | -0.085257 | -0.14406 | -0.050716 | -0.070082 | -0.19548 | -0.27716 | -0.15888 | -0.21482 | -0.18879 | 0.12149 | 0.10105 | 0.090132 | 0.18453 | 0.021119 | -0.10464 | -0.039481 | -0.098282 | -0.00494 | -0.024306 | -0.14971 | -0.23139 | -0.1131 | -0.16904 | -0.14301 | 0.16726 | 0.14682 | 0.13591 | 0.23031 | -0.39865 | -0.3673 | -0.33631 | -0.30495
1550.8906 | 121.6873 | -0.20599 | 121.4676 | -0.020079 | -0.14583 | -0.085257 | -0.14406 | -0.050716 | -0.070082 | -0.19548 | -0.27716 | -0.1543 | -0.20566 | -0.18879 | 0.13522 | 0.10105 | 0.085554 | 0.19369 | 0.025697 | -0.10006 | -0.039481 | -0.098282 | -0.00494 | -0.024306 | -0.14971 | -0.23139 | -0.10853 | -0.15989 | -0.14301 | 0.181 | 0.14682 | 0.13133 | 0.23947 | -0.41239 | -0.36272 | -0.34088 | -0.29122
1552.5938 | 121.7834 | -0.19226 | 121.4447 | -0.029236 | -0.14583 | -0.085257 | -0.14864 | -0.046138 | -0.070082 | -0.19091 | -0.27716 | -0.1543 | -0.20566 | -0.18421 | 0.12149 | 0.10562 | 0.076397 | 0.19369 | 0.01654 | -0.10006 | -0.039481 | -0.10286 | -0.000362 | -0.024306 | -0.14513 | -0.23139 | -0.10853 | -0.15989 | -0.13843 | 0.16726 | 0.1514 | 0.12217 | 0.23947 | -0.39865 | -0.35356 | -0.32715 | -0.28206
1554.3594 | 121.7697 | -0.1831 | 121.431 | -0.024657 | -0.14125 | -0.085257 | -0.14864 | -0.050716 | -0.070082 | -0.19548 | -0.27259 | -0.16346 | -0.21024 | -0.17963 | 0.12149 | 0.1102 | 0.080975 | 0.19369 | 0.021119 | -0.095479 | -0.039481 | -0.10286 | -0.00494 | -0.024306 | -0.14971 | -0.22681 | -0.11768 | -0.16447 | -0.13385 | 0.16726 | 0.15598 | 0.12675 | 0.23947 | -0.39407 | -0.35356 | -0.33173 | -0.29122
1556.125 | 121.6507 | -0.24719 | 121.4676 | -0.024657 | -0.14125 | -0.080679 | -0.13948 | -0.041561 | -0.074661 | -0.19091 | -0.26801 | -0.16346 | -0.21024 | -0.19337 | 0.12607 | 0.10105 | 0.085554 | 0.18453 | 0.021119 | -0.095479 | -0.034903 | -0.093703 | 0.004215 | -0.028885 | -0.14513 | -0.22223 | -0.11768 | -0.16447 | -0.14759 | 0.17184 | 0.14682 | 0.13133 | 0.23031 | -0.39407 | -0.35356 | -0.33631 | -0.2958
1557.875 | 121.6507 | -0.24261 | 121.463 | -0.024657 | -0.14583 | -0.085257 | -0.15321 | -0.041561 | -0.079239 | -0.19548 | -0.27716 | -0.1543 | -0.21482 | -0.17963 | 0.13064 | 0.10562 | 0.080975 | 0.18453 | 0.021119 | -0.10006 | -0.039481 | -0.10744 | 0.004215 | -0.033463 | -0.14971 | -0.23139 | -0.10853 | -0.16904 | -0.13385 | 0.17642 | 0.1514 | 0.12675 | 0.23031 | -0.40781 | -0.35814 | -0.34546 | -0.2958
1559.5781 | 121.7606 | -0.17395 | 121.4264 | -0.020079 | -0.14125 | -0.0761 | -0.15321 | -0.046138 | -0.079239 | -0.19091 | -0.28174 | -0.15888 | -0.21482 | -0.18421 | 0.12607 | 0.10562 | 0.090132 | 0.19369 | 0.025697 | -0.095479 | -0.030324 | -0.10744 | -0.000362 | -0.033463 | -0.14513 | -0.23597 | -0.1131 | -0.16904 | -0.13843 | 0.17184 | 0.1514 | 0.13591 | 0.23947 | -0.40781 | -0.37187 | -0.34088 | -0.30495
1561.3438 | 121.7056 | -0.21515 | 121.4493 | -0.024657 | -0.14583 | -0.085257 | -0.14406 | -0.046138 | -0.079239 | -0.19548 | -0.28174 | -0.1543 | -0.21482 | -0.18421 | 0.13064 | 0.10105 | 0.080975 | 0.18453 | 0.021119 | -0.10006 | -0.039481 | -0.098282 | -0.000362 | -0.033463 | -0.14971 | -0.23597 | -0.10853 | -0.16904 | -0.13843 | 0.17642 | 0.14682 | 0.12675 | 0.23031 | -0.41239 | -0.36272 | -0.34546 | -0.2958
1563.1094 | 121.7285 | -0.21057 | 121.4172 | -0.029236 | -0.15041 | -0.085257 | -0.14406 | -0.050716 | -0.074661 | -0.19548 | -0.27259 | -0.16346 | -0.21482 | -0.17505 | 0.13064 | 0.10105 | 0.085554 | 0.18453 | 0.01654 | -0.10464 | -0.039481 | -0.098282 | -0.00494 | -0.028885 | -0.14971 | -0.22681 | -0.11768 | -0.16904 | -0.12928 | 0.17642 | 0.14682 | 0.13133 | 0.23031 | -0.40323 | -0.35814 | -0.34546 | -0.30037
1564.8906 | 121.6827 | -0.2243 | 121.4584 | -0.020079 | -0.14583 | -0.085257 | -0.14406 | -0.041561 | -0.070082 | -0.19548 | -0.27716 | -0.1543 | -0.21024 | -0.17963 | 0.12607 | 0.10105 | 0.085554 | 0.17996 | 0.025697 | -0.10006 | -0.039481 | -0.098282 | 0.004215 | -0.024306 | -0.14971 | -0.23139 | -0.10853 | -0.16447 | -0.13385 | 0.17184 | 0.14682 | 0.13133 | 0.22573 | -0.40323 | -0.36272 | -0.33631 | -0.2958
1566.6562 | 121.6553 | -0.24719 | 121.463 | -0.024657 | -0.14583 | -0.085257 | -0.14406 | -0.046138 | -0.074661 | -0.19091 | -0.27259 | -0.15888 | -0.21024 | -0.17963 | 0.12607 | 0.10562 | 0.090132 | 0.18911 | 0.021119 | -0.10006 | -0.039481 | -0.098282 | -0.000362 | -0.028885 | -0.14513 | -0.22681 | -0.1131 | -0.16447 | -0.13385 | 0.17184 | 0.1514 | 0.13591 | 0.23489 | -0.39865 | -0.36272 | -0.33631 | -0.30037
1568.3594 | 121.7743 | -0.1831 | 121.3989 | -0.024657 | -0.14125 | -0.085257 | -0.14406 | -0.041561 | -0.070082 | -0.19548 | -0.27259 | -0.15888 | -0.21024 | -0.17963 | 0.12607 | 0.10105 | 0.071818 | 0.18911 | 0.021119 | -0.095479 | -0.039481 | -0.098282 | 0.004215 | -0.024306 | -0.14971 | -0.22681 | -0.1131 | -0.16447 | -0.13385 | 0.17184 | 0.14682 | 0.11759 | 0.23489 | -0.39865 | -0.3444 | -0.33631 | -0.28206
1570.1406 | 121.6782 | -0.23804 | 121.4401 | -0.024657 | -0.15499 | -0.080679 | -0.13948 | -0.046138 | -0.074661 | -0.18633 | -0.28174 | -0.15888 | -0.20566 | -0.18879 | 0.12607 | 0.10562 | 0.080975 | 0.18911 | 0.021119 | -0.10921 | -0.034903 | -0.093703 | -0.000362 | -0.028885 | -0.14055 | -0.23597 | -0.1131 | -0.15989 | -0.14301 | 0.17184 | 0.1514 | 0.12675 | 0.23489 | -0.40781 | -0.36272 | -0.33173 | -0.28664
1571.9062 | 121.7789 | -0.19684 | 121.4355 | -0.033814 | -0.15499 | -0.080679 | -0.14406 | -0.036983 | -0.074661 | -0.20464 | -0.27259 | -0.15888 | -0.20566 | -0.18421 | 0.12607 | 0.10562 | 0.090132 | 0.18911 | 0.011962 | -0.10921 | -0.034903 | -0.098282 | 0.008793 | -0.028885 | -0.15886 | -0.22681 | -0.1131 | -0.15989 | -0.13843 | 0.17184 | 0.1514 | 0.13591 | 0.23489 | -0.39865 | -0.36272 | -0.33173 | -0.2958
1573.6094 | 121.7194 | -0.21057 | 121.463 | -0.024657 | -0.14583 | -0.089836 | -0.14406 | -0.046138 | -0.070082 | -0.20464 | -0.28174 | -0.15888 | -0.20109 | -0.18879 | 0.13064 | 0.10105 | 0.085554 | 0.18453 | 0.021119 | -0.10006 | -0.04406 | -0.098282 | -0.000362 | -0.024306 | -0.15886 | -0.23597 | -0.1131 | -0.15531 | -0.14301 | 0.17642 | 0.14682 | 0.13133 | 0.23031 | -0.41239 | -0.3673 | -0.33173 | -0.28664
1575.3906 | 121.7468 | -0.17853 | 121.4447 | -0.020079 | -0.14583 | -0.0761 | -0.14406 | -0.050716 | -0.074661 | -0.20006 | -0.28174 | -0.16346 | -0.2194 | -0.18421 | 0.12607 | 0.10562 | 0.085554 | 0.18911 | 0.025697 | -0.10006 | -0.030324 | -0.098282 | -0.00494 | -0.028885 | -0.15429 | -0.23597 | -0.11768 | -0.17362 | -0.13843 | 0.17184 | 0.1514 | 0.13133 | 0.23489 | -0.40781 | -0.3673 | -0.34546 | -0.30495
1577.0938 | 121.7239 | -0.20142 | 121.4722 | -0.029236 | -0.15041 | -0.080679 | -0.14406 | -0.046138 | -0.070082 | -0.19091 | -0.28174 | -0.15888 | -0.20109 | -0.17963 | 0.12149 | 0.10562 | 0.080975 | 0.18911 | 0.01654 | -0.10464 | -0.034903 | -0.098282 | -0.000362 | -0.024306 | -0.14513 | -0.23597 | -0.1131 | -0.15531 | -0.13385 | 0.16726 | 0.1514 | 0.12675 | 0.23489 | -0.40323 | -0.36272 | -0.32257 | -0.28206
1578.8594 | 121.7239 | -0.21973 | 121.4722 | -0.020079 | -0.15041 | -0.085257 | -0.14406 | -0.046138 | -0.070082 | -0.19548 | -0.27716 | -0.15888 | -0.21482 | -0.18421 | 0.13064 | 0.091891 | 0.085554 | 0.17996 | 0.025697 | -0.10464 | -0.039481 | -0.098282 | -0.000362 | -0.024306 | -0.14971 | -0.23139 | -0.1131 | -0.16904 | -0.13843 | 0.17642 | 0.13767 | 0.13133 | 0.22573 | -0.40781 | -0.36272 | -0.34546 | -0.30037
1580.5781 | 121.7834 | -0.1831 | 121.4355 | -0.024657 | -0.15041 | -0.080679 | -0.14406 | -0.036983 | -0.070082 | -0.19548 | -0.27716 | -0.16346 | -0.20566 | -0.18421 | 0.13064 | 0.10105 | 0.076397 | 0.18911 | 0.021119 | -0.10464 | -0.034903 | -0.098282 | 0.008793 | -0.024306 | -0.14971 | -0.23139 | -0.11768 | -0.15989 | -0.13843 | 0.17642 | 0.14682 | 0.12217 | 0.23489 | -0.40781 | -0.35356 | -0.33631 | -0.28206
1582.3438 | 121.7514 | -0.19226 | 121.4447 | -0.020079 | -0.13668 | -0.0761 | -0.14406 | -0.036983 | -0.070082 | -0.19091 | -0.28174 | -0.15888 | -0.20566 | -0.18421 | 0.12607 | 0.1102 | 0.080975 | 0.19369 | 0.025697 | -0.0909 | -0.030324 | -0.098282 | 0.008793 | -0.024306 | -0.14513 | -0.23597 | -0.1131 | -0.15989 | -0.13843 | 0.17184 | 0.15598 | 0.12675 | 0.23947 | -0.40781 | -0.36272 | -0.33173 | -0.28664
1584.0938 | 121.7926 | -0.20142 | 121.4401 | -0.033814 | -0.14125 | -0.080679 | -0.14406 | -0.046138 | -0.070082 | -0.19091 | -0.27716 | -0.1543 | -0.21024 | -0.17963 | 0.13064 | 0.10105 | 0.085554 | 0.19827 | 0.011962 | -0.095479 | -0.034903 | -0.098282 | -0.000362 | -0.024306 | -0.14513 | -0.23139 | -0.10853 | -0.16447 | -0.13385 | 0.17642 | 0.14682 | 0.13133 | 0.24404 | -0.40781 | -0.36272 | -0.34088 | -0.2958
1585.875 | 121.7194 | -0.20599 | 121.4264 | -0.024657 | -0.14583 | -0.0761 | -0.14406 | -0.046138 | -0.079239 | -0.18175 | -0.28174 | -0.16804 | -0.21024 | -0.17963 | 0.13064 | 0.10562 | 0.076397 | 0.18911 | 0.021119 | -0.10006 | -0.030324 | -0.098282 | -0.000362 | -0.033463 | -0.13597 | -0.23597 | -0.12226 | -0.16447 | -0.13385 | 0.17642 | 0.1514 | 0.12217 | 0.23489 | -0.41239 | -0.35814 | -0.34088 | -0.28664
1587.5781 | 121.6507 | -0.24719 | 121.4905 | -0.015501 | -0.14125 | -0.080679 | -0.14406 | -0.046138 | -0.060926 | -0.19548 | -0.27259 | -0.16346 | -0.20566 | -0.17963 | 0.13522 | 0.10562 | 0.080975 | 0.17996 | 0.030275 | -0.095479 | -0.034903 | -0.098282 | -0.000362 | -0.01515 | -0.14971 | -0.22681 | -0.11768 | -0.15989 | -0.13385 | 0.181 | 0.1514 | 0.12675 | 0.22573 | -0.40781 | -0.35356 | -0.34088 | -0.28664
1589.3438 | 121.6644 | -0.23804 | 121.4813 | -0.024657 | -0.14583 | -0.080679 | -0.13032 | -0.046138 | -0.070082 | -0.19548 | -0.27259 | -0.16346 | -0.20109 | -0.18879 | 0.12607 | 0.10105 | 0.080975 | 0.18911 | 0.021119 | -0.10006 | -0.034903 | -0.084546 | -0.000362 | -0.024306 | -0.14971 | -0.22681 | -0.11768 | -0.15531 | -0.14301 | 0.17184 | 0.14682 | 0.12675 | 0.23489 | -0.39865 | -0.35356 | -0.32715 | -0.28206
1591.1094 | 121.637 | -0.22888 | 121.463 | -0.024657 | -0.14125 | -0.080679 | -0.1349 | -0.041561 | -0.070082 | -0.19548 | -0.27716 | -0.1543 | -0.21482 | -0.18421 | 0.13522 | 0.10105 | 0.085554 | 0.18911 | 0.021119 | -0.095479 | -0.034903 | -0.089125 | 0.004215 | -0.024306 | -0.14971 | -0.23139 | -0.10853 | -0.16904 | -0.13843 | 0.181 | 0.14682 | 0.13133 | 0.23489 | -0.41239 | -0.36272 | -0.35004 | -0.30037
1592.875 | 121.6507 | -0.23804 | 121.4722 | -0.024657 | -0.14583 | -0.0761 | -0.14406 | -0.041561 | -0.074661 | -0.19548 | -0.28174 | -0.1543 | -0.21482 | -0.17963 | 0.12607 | 0.096469 | 0.085554 | 0.18453 | 0.021119 | -0.10006 | -0.030324 | -0.098282 | 0.004215 | -0.028885 | -0.14971 | -0.23597 | -0.10853 | -0.16904 | -0.13385 | 0.17184 | 0.14225 | 0.13133 | 0.23031 | -0.40781 | -0.3673 | -0.34088 | -0.30037
1594.6406 | 121.6507 | -0.24719 | 121.4767 | -0.015501 | -0.14583 | -0.071521 | -0.1349 | -0.041561 | -0.065504 | -0.19548 | -0.27716 | -0.15888 | -0.21024 | -0.17963 | 0.12607 | 0.10105 | 0.080975 | 0.18453 | 0.030275 | -0.10006 | -0.025745 | -0.089125 | 0.004215 | -0.019728 | -0.14971 | -0.23139 | -0.1131 | -0.16447 | -0.13385 | 0.17184 | 0.14682 | 0.12675 | 0.23031 | -0.40323 | -0.35814 | -0.33631 | -0.29122
1596.4062 | 121.637 | -0.23346 | 121.5134 | -0.024657 | -0.14125 | -0.080679 | -0.1349 | -0.036983 | -0.074661 | -0.19548 | -0.27716 | -0.15888 | -0.21482 | -0.17963 | 0.12607 | 0.096469 | 0.080975 | 0.18911 | 0.021119 | -0.095479 | -0.034903 | -0.089125 | 0.008793 | -0.028885 | -0.14971 | -0.23139 | -0.1131 | -0.16904 | -0.13385 | 0.17184 | 0.14225 | 0.12675 | 0.23489 | -0.40323 | -0.35814 | -0.34088 | -0.2958
1598.1094 | 121.669 | -0.23346 | 121.4905 | -0.029236 | -0.14125 | -0.0761 | -0.13032 | -0.046138 | -0.065504 | -0.19091 | -0.27259 | -0.15888 | -0.21482 | -0.17963 | 0.12149 | 0.10105 | 0.085554 | 0.19369 | 0.01654 | -0.095479 | -0.030324 | -0.084546 | -0.000362 | -0.019728 | -0.14513 | -0.22681 | -0.1131 | -0.16904 | -0.13385 | 0.16726 | 0.14682 | 0.13133 | 0.23947 | -0.39407 | -0.35814 | -0.33631 | -0.30037
1599.875 | 121.669 | -0.24719 | 121.4767 | -0.033814 | -0.15499 | -0.080679 | -0.14406 | -0.046138 | -0.070082 | -0.19548 | -0.27716 | -0.15888 | -0.20566 | -0.18421 | 0.12607 | 0.10105 | 0.076397 | 0.18453 | 0.011962 | -0.10921 | -0.034903 | -0.098282 | -0.000362 | -0.024306 | -0.14971 | -0.23139 | -0.1131 | -0.15989 | -0.13843 | 0.17184 | 0.14682 | 0.12217 | 0.23031 | -0.40323 | -0.35356 | -0.33173 | -0.28206
1601.6406 | 121.7285 | -0.21057 | 121.431 | -0.024657 | -0.14583 | -0.080679 | -0.14406 | -0.046138 | -0.074661 | -0.19091 | -0.27259 | -0.15888 | -0.21024 | -0.17963 | 0.12607 | 0.10105 | 0.085554 | 0.18453 | 0.021119 | -0.10006 | -0.034903 | -0.098282 | -0.000362 | -0.028885 | -0.14513 | -0.22681 | -0.1131 | -0.16447 | -0.13385 | 0.17184 | 0.14682 | 0.13133 | 0.23031 | -0.39865 | -0.35814 | -0.33631 | -0.2958
1603.3594 | 121.669 | -0.23346 | 121.4584 | -0.029236 | -0.15041 | -0.080679 | -0.13948 | -0.041561 | -0.065504 | -0.19091 | -0.26801 | -0.1543 | -0.21024 | -0.18421 | 0.12607 | 0.096469 | 0.085554 | 0.18911 | 0.01654 | -0.10464 | -0.034903 | -0.093703 | 0.004215 | -0.019728 | -0.14513 | -0.22223 | -0.10853 | -0.16447 | -0.13843 | 0.17184 | 0.14225 | 0.13133 | 0.23489 | -0.39407 | -0.35356 | -0.33631 | -0.2958
1605.125 | 121.7285 | -0.21057 | 121.4447 | -0.033814 | -0.14125 | -0.0761 | -0.13948 | -0.036983 | -0.074661 | -0.20006 | -0.26801 | -0.1543 | -0.21024 | -0.17505 | 0.12607 | 0.1102 | 0.080975 | 0.17996 | 0.011962 | -0.095479 | -0.030324 | -0.093703 | 0.008793 | -0.028885 | -0.15429 | -0.22223 | -0.10853 | -0.16447 | -0.12928 | 0.17184 | 0.15598 | 0.12675 | 0.22573 | -0.39407 | -0.34898 | -0.33631 | -0.29122
1606.9062 | 121.7651 | -0.18768 | 121.4264 | -0.024657 | -0.14583 | -0.080679 | -0.1349 | -0.041561 | -0.065504 | -0.18633 | -0.28174 | -0.1543 | -0.20566 | -0.17963 | 0.11233 | 0.10562 | 0.076397 | 0.17996 | 0.021119 | -0.10006 | -0.034903 | -0.089125 | 0.004215 | -0.019728 | -0.14055 | -0.23597 | -0.10853 | -0.15989 | -0.13385 | 0.15811 | 0.1514 | 0.12217 | 0.22573 | -0.39407 | -0.35814 | -0.31799 | -0.28206
1608.6719 | 121.6965 | -0.2243 | 121.4813 | -0.024657 | -0.14583 | -0.0761 | -0.1349 | -0.041561 | -0.074661 | -0.19548 | -0.27259 | -0.16346 | -0.20566 | -0.17963 | 0.13064 | 0.096469 | 0.080975 | 0.18453 | 0.021119 | -0.10006 | -0.030324 | -0.089125 | 0.004215 | -0.028885 | -0.14971 | -0.22681 | -0.11768 | -0.15989 | -0.13385 | 0.17642 | 0.14225 | 0.12675 | 0.23031 | -0.40323 | -0.35356 | -0.33631 | -0.28664
1610.4375 | 121.6873 | -0.21057 | 121.4676 | -0.024657 | -0.14583 | -0.085257 | -0.14406 | -0.041561 | -0.070082 | -0.19548 | -0.27716 | -0.15888 | -0.21024 | -0.17963 | 0.13064 | 0.10562 | 0.076397 | 0.17996 | 0.021119 | -0.10006 | -0.039481 | -0.098282 | 0.004215 | -0.024306 | -0.14971 | -0.23139 | -0.1131 | -0.16447 | -0.13385 | 0.17642 | 0.1514 | 0.12217 | 0.22573 | -0.40781 | -0.35356 | -0.34088 | -0.28664
1612.2188 | 121.7422 | -0.21973 | 121.4539 | -0.020079 | -0.14583 | -0.080679 | -0.14406 | -0.036983 | -0.065504 | -0.18633 | -0.27716 | -0.16346 | -0.21482 | -0.17047 | 0.12149 | 0.10105 | 0.080975 | 0.18453 | 0.025697 | -0.10006 | -0.034903 | -0.098282 | 0.008793 | -0.019728 | -0.14055 | -0.23139 | -0.11768 | -0.16904 | -0.1247 | 0.16726 | 0.14682 | 0.12675 | 0.23031 | -0.39865 | -0.35814 | -0.33631 | -0.2958
1613.9844 | 121.6919 | -0.21057 | 121.4722 | -0.024657 | -0.15041 | -0.0761 | -0.13948 | -0.036983 | -0.074661 | -0.18633 | -0.27259 | -0.15888 | -0.21024 | -0.18421 | 0.12149 | 0.10105 | 0.076397 | 0.17996 | 0.021119 | -0.10464 | -0.030324 | -0.093703 | 0.008793 | -0.028885 | -0.14055 | -0.22681 | -0.1131 | -0.16447 | -0.13843 | 0.16726 | 0.14682 | 0.12217 | 0.22573 | -0.39407 | -0.34898 | -0.33173 | -0.28664
1615.7031 | 121.6507 | -0.23346 | 121.4676 | -0.020079 | -0.14583 | -0.071521 | -0.14406 | -0.046138 | -0.074661 | -0.18633 | -0.26801 | -0.15888 | -0.21024 | -0.17963 | 0.12149 | 0.10105 | 0.076397 | 0.18453 | 0.025697 | -0.10006 | -0.025745 | -0.098282 | -0.000362 | -0.028885 | -0.14055 | -0.22223 | -0.1131 | -0.16447 | -0.13385 | 0.16726 | 0.14682 | 0.12217 | 0.23031 | -0.38949 | -0.3444 | -0.33173 | -0.28664
1617.4688 | 121.7377 | -0.1831 | 121.4493 | -0.024657 | -0.15041 | -0.080679 | -0.13948 | -0.046138 | -0.070082 | -0.19091 | -0.27259 | -0.14972 | -0.20566 | -0.17963 | 0.11691 | 0.10105 | 0.076397 | 0.17538 | 0.021119 | -0.10464 | -0.034903 | -0.093703 | -0.000362 | -0.024306 | -0.14513 | -0.22681 | -0.10395 | -0.15989 | -0.13385 | 0.16268 | 0.14682 | 0.12217 | 0.22115 | -0.38949 | -0.34898 | -0.32257 | -0.28206
1619.1719 | 121.7834 | -0.17853 | 121.4447 | -0.024657 | -0.14125 | -0.085257 | -0.13948 | -0.041561 | -0.070082 | -0.19091 | -0.26801 | -0.15888 | -0.21024 | -0.17505 | 0.13064 | 0.10562 | 0.076397 | 0.17996 | 0.021119 | -0.095479 | -0.039481 | -0.093703 | 0.004215 | -0.024306 | -0.14513 | -0.22223 | -0.1131 | -0.16447 | -0.12928 | 0.17642 | 0.1514 | 0.12217 | 0.22573 | -0.39865 | -0.3444 | -0.34088 | -0.28664
1620.9375 | 121.7697 | -0.17395 | 121.4584 | -0.029236 | -0.14125 | -0.0761 | -0.13948 | -0.041561 | -0.079239 | -0.19548 | -0.27259 | -0.15888 | -0.21024 | -0.18421 | 0.12149 | 0.10105 | 0.080975 | 0.17996 | 0.01654 | -0.095479 | -0.030324 | -0.093703 | 0.004215 | -0.033463 | -0.14971 | -0.22681 | -0.1131 | -0.16447 | -0.13843 | 0.16726 | 0.14682 | 0.12675 | 0.22573 | -0.39407 | -0.35356 | -0.33173 | -0.29122
1622.7031 | 121.7148 | -0.20599 | 121.4447 | -0.024657 | -0.15041 | -0.071521 | -0.14406 | -0.046138 | -0.074661 | -0.19091 | -0.27716 | -0.1543 | -0.21024 | -0.17505 | 0.13064 | 0.096469 | 0.071818 | 0.18911 | 0.021119 | -0.10464 | -0.025745 | -0.098282 | -0.000362 | -0.028885 | -0.14513 | -0.23139 | -0.10853 | -0.16447 | -0.12928 | 0.17642 | 0.14225 | 0.11759 | 0.23489 | -0.40781 | -0.34898 | -0.34088 | -0.28206
1624.4844 | 121.6919 | -0.21973 | 121.4584 | -0.024657 | -0.14125 | -0.080679 | -0.13032 | -0.041561 | -0.070082 | -0.19091 | -0.27259 | -0.1543 | -0.21024 | -0.18421 | 0.12149 | 0.10562 | 0.071818 | 0.17996 | 0.021119 | -0.095479 | -0.034903 | -0.084546 | 0.004215 | -0.024306 | -0.14513 | -0.22681 | -0.10853 | -0.16447 | -0.13843 | 0.16726 | 0.1514 | 0.11759 | 0.22573 | -0.39407 | -0.3444 | -0.33173 | -0.28206
1626.2656 | 121.7331 | -0.18768 | 121.463 | -0.020079 | -0.14583 | -0.080679 | -0.13948 | -0.046138 | -0.070082 | -0.19548 | -0.27259 | -0.1543 | -0.20566 | -0.18421 | 0.12149 | 0.10105 | 0.076397 | 0.18453 | 0.025697 | -0.10006 | -0.034903 | -0.093703 | -0.000362 | -0.024306 | -0.14971 | -0.22681 | -0.10853 | -0.15989 | -0.13843 | 0.16726 | 0.14682 | 0.12217 | 0.23031 | -0.39407 | -0.34898 | -0.32715 | -0.28206
1627.9531 | 121.7056 | -0.22888 | 121.4722 | -0.024657 | -0.14125 | -0.080679 | -0.1349 | -0.036983 | -0.070082 | -0.19091 | -0.27716 | -0.1543 | -0.21024 | -0.18421 | 0.12149 | 0.10105 | 0.080975 | 0.18911 | 0.021119 | -0.095479 | -0.034903 | -0.089125 | 0.008793 | -0.024306 | -0.14513 | -0.23139 | -0.10853 | -0.16447 | -0.13843 | 0.16726 | 0.14682 | 0.12675 | 0.23489 | -0.39865 | -0.35814 | -0.33173 | -0.29122
1629.7344 | 121.7834 | -0.18768 | 121.431 | -0.029236 | -0.14583 | -0.080679 | -0.14406 | -0.041561 | -0.074661 | -0.19091 | -0.27259 | -0.1543 | -0.20109 | -0.17963 | 0.13064 | 0.10105 | 0.071818 | 0.1708 | 0.01654 | -0.10006 | -0.034903 | -0.098282 | 0.004215 | -0.028885 | -0.14513 | -0.22681 | -0.10853 | -0.15531 | -0.13385 | 0.17642 | 0.14682 | 0.11759 | 0.21658 | -0.40323 | -0.3444 | -0.33173 | -0.2729
1631.4375 | 121.7056 | -0.23346 | 121.4676 | -0.024657 | -0.14583 | -0.080679 | -0.13948 | -0.036983 | -0.070082 | -0.19091 | -0.27259 | -0.1543 | -0.21024 | -0.17963 | 0.12607 | 0.10105 | 0.076397 | 0.18453 | 0.021119 | -0.10006 | -0.034903 | -0.093703 | 0.008793 | -0.024306 | -0.14513 | -0.22681 | -0.10853 | -0.16447 | -0.13385 | 0.17184 | 0.14682 | 0.12217 | 0.23031 | -0.39865 | -0.34898 | -0.33631 | -0.28664
1633.2031 | 121.6461 | -0.21057 | 121.4813 | -0.029236 | -0.14125 | -0.071521 | -0.13948 | -0.036983 | -0.070082 | -0.19091 | -0.27716 | -0.1543 | -0.20566 | -0.17505 | 0.12607 | 0.10105 | 0.071818 | 0.17996 | 0.01654 | -0.095479 | -0.025745 | -0.093703 | 0.008793 | -0.024306 | -0.14513 | -0.23139 | -0.10853 | -0.15989 | -0.12928 | 0.17184 | 0.14682 | 0.11759 | 0.22573 | -0.40323 | -0.34898 | -0.33173 | -0.27748
1634.9844 | 121.6782 | -0.23346 | 121.4722 | -0.024657 | -0.14125 | -0.0761 | -0.1349 | -0.036983 | -0.065504 | -0.18175 | -0.27259 | -0.1543 | -0.21482 | -0.17963 | 0.13064 | 0.096469 | 0.080975 | 0.17996 | 0.021119 | -0.095479 | -0.030324 | -0.089125 | 0.008793 | -0.019728 | -0.13597 | -0.22681 | -0.10853 | -0.16904 | -0.13385 | 0.17642 | 0.14225 | 0.12675 | 0.22573 | -0.40323 | -0.35356 | -0.34546 | -0.2958
1636.7031 | 121.6461 | -0.24261 | 121.463 | -0.033814 | -0.14125 | -0.0761 | -0.1349 | -0.046138 | -0.070082 | -0.19091 | -0.27259 | -0.14972 | -0.21024 | -0.18421 | 0.12149 | 0.096469 | 0.076397 | 0.17996 | 0.011962 | -0.095479 | -0.030324 | -0.089125 | -0.000362 | -0.024306 | -0.14513 | -0.22681 | -0.10395 | -0.16447 | -0.13843 | 0.16726 | 0.14225 | 0.12217 | 0.22573 | -0.39407 | -0.34898 | -0.33173 | -0.28664
1638.4688 | 121.756 | -0.20599 | 121.4676 | -0.024657 | -0.14125 | -0.085257 | -0.13948 | -0.046138 | -0.065504 | -0.19091 | -0.27259 | -0.1543 | -0.20566 | -0.17963 | 0.13064 | 0.10562 | 0.076397 | 0.18453 | 0.021119 | -0.095479 | -0.039481 | -0.093703 | -0.000362 | -0.019728 | -0.14513 | -0.22681 | -0.10853 | -0.15989 | -0.13385 | 0.17642 | 0.1514 | 0.12217 | 0.23031 | -0.40323 | -0.34898 | -0.33631 | -0.28206
1640.1719 | 121.7148 | -0.20599 | 121.4539 | -0.020079 | -0.14583 | -0.0761 | -0.13948 | -0.036983 | -0.065504 | -0.19091 | -0.27259 | -0.1543 | -0.20109 | -0.17963 | 0.12607 | 0.10105 | 0.076397 | 0.17996 | 0.025697 | -0.10006 | -0.030324 | -0.093703 | 0.008793 | -0.019728 | -0.14513 | -0.22681 | -0.10853 | -0.15531 | -0.13385 | 0.17184 | 0.14682 | 0.12217 | 0.22573 | -0.39865 | -0.34898 | -0.32715 | -0.27748
1641.9375 | 121.7743 | -0.19226 | 121.4401 | -0.029236 | -0.14125 | -0.080679 | -0.13948 | -0.046138 | -0.070082 | -0.18633 | -0.28174 | -0.15888 | -0.21024 | -0.18421 | 0.12149 | 0.10105 | 0.085554 | 0.17996 | 0.01654 | -0.095479 | -0.034903 | -0.093703 | -0.000362 | -0.024306 | -0.14055 | -0.23597 | -0.1131 | -0.16447 | -0.13843 | 0.16726 | 0.14682 | 0.13133 | 0.22573 | -0.40323 | -0.3673 | -0.33173 | -0.2958
1643.7031 | 121.6965 | -0.21515 | 121.4722 | -0.020079 | -0.13668 | -0.080679 | -0.13948 | -0.036983 | -0.065504 | -0.18633 | -0.27259 | -0.15888 | -0.21024 | -0.18421 | 0.12607 | 0.10105 | 0.080975 | 0.18453 | 0.025697 | -0.0909 | -0.034903 | -0.093703 | 0.008793 | -0.019728 | -0.14055 | -0.22681 | -0.1131 | -0.16447 | -0.13843 | 0.17184 | 0.14682 | 0.12675 | 0.23031 | -0.39865 | -0.35356 | -0.33631 | -0.29122
1645.4688 | 121.7743 | -0.19226 | 121.4264 | -0.024657 | -0.1321 | -0.071521 | -0.13032 | -0.036983 | -0.065504 | -0.19091 | -0.27716 | -0.1543 | -0.20109 | -0.17963 | 0.12607 | 0.096469 | 0.085554 | 0.17538 | 0.021119 | -0.086321 | -0.025745 | -0.084546 | 0.008793 | -0.019728 | -0.14513 | -0.23139 | -0.10853 | -0.15531 | -0.13385 | 0.17184 | 0.14225 | 0.13133 | 0.22115 | -0.40323 | -0.36272 | -0.32715 | -0.28664
1647.1875 | 121.6644 | -0.23804 | 121.4951 | -0.029236 | -0.1321 | -0.080679 | -0.1349 | -0.036983 | -0.065504 | -0.17717 | -0.27259 | -0.1543 | -0.20566 | -0.17963 | 0.12149 | 0.10105 | 0.080975 | 0.18453 | 0.01654 | -0.086321 | -0.034903 | -0.089125 | 0.008793 | -0.019728 | -0.1314 | -0.22681 | -0.10853 | -0.15989 | -0.13385 | 0.16726 | 0.14682 | 0.12675 | 0.23031 | -0.39407 | -0.35356 | -0.32715 | -0.28664
1648.9531 | 121.6827 | -0.20142 | 121.463 | -0.029236 | -0.14125 | -0.071521 | -0.13948 | -0.041561 | -0.065504 | -0.19091 | -0.27716 | -0.15888 | -0.20566 | -0.17963 | 0.12607 | 0.10562 | 0.076397 | 0.17996 | 0.01654 | -0.095479 | -0.025745 | -0.093703 | 0.004215 | -0.019728 | -0.14513 | -0.23139 | -0.1131 | -0.15989 | -0.13385 | 0.17184 | 0.1514 | 0.12217 | 0.22573 | -0.40323 | -0.35356 | -0.33173 | -0.28206
1650.7188 | 121.7789 | -0.19684 | 121.4401 | -0.029236 | -0.14125 | -0.0761 | -0.13948 | -0.032405 | -0.065504 | -0.18633 | -0.27259 | -0.1543 | -0.20566 | -0.18421 | 0.13064 | 0.096469 | 0.080975 | 0.18453 | 0.01654 | -0.095479 | -0.030324 | -0.093703 | 0.013371 | -0.019728 | -0.14055 | -0.22681 | -0.10853 | -0.15989 | -0.13843 | 0.17642 | 0.14225 | 0.12675 | 0.23031 | -0.40323 | -0.35356 | -0.33631 | -0.28664
1652.4688 | 121.6599 | -0.21973 | 121.4722 | -0.029236 | -0.14125 | -0.0761 | -0.1349 | -0.036983 | -0.060926 | -0.18175 | -0.27259 | -0.1543 | -0.21482 | -0.18421 | 0.12149 | 0.10105 | 0.076397 | 0.18453 | 0.01654 | -0.095479 | -0.030324 | -0.089125 | 0.008793 | -0.01515 | -0.13597 | -0.22681 | -0.10853 | -0.16904 | -0.13843 | 0.16726 | 0.14682 | 0.12217 | 0.23031 | -0.39407 | -0.34898 | -0.33631 | -0.29122
1654.25 | 121.6736 | -0.21515 | 121.4493 | -0.024657 | -0.14125 | -0.071521 | -0.1349 | -0.036983 | -0.070082 | -0.18633 | -0.27259 | -0.1543 | -0.21482 | -0.17963 | 0.12607 | 0.10105 | 0.080975 | 0.18453 | 0.021119 | -0.095479 | -0.025745 | -0.089125 | 0.008793 | -0.024306 | -0.14055 | -0.22681 | -0.10853 | -0.16904 | -0.13385 | 0.17184 | 0.14682 | 0.12675 | 0.23031 | -0.39865 | -0.35356 | -0.34088 | -0.2958
1655.9531 | 121.7377 | -0.21515 | 121.4584 | -0.024657 | -0.13668 | -0.0761 | -0.13948 | -0.041561 | -0.065504 | -0.18633 | -0.27259 | -0.15888 | -0.21024 | -0.18421 | 0.12149 | 0.10105 | 0.080975 | 0.18911 | 0.021119 | -0.0909 | -0.030324 | -0.093703 | 0.004215 | -0.019728 | -0.14055 | -0.22681 | -0.1131 | -0.16447 | -0.13843 | 0.16726 | 0.14682 | 0.12675 | 0.23489 | -0.39407 | -0.35356 | -0.33173 | -0.29122
1657.6719 | 121.669 | -0.2243 | 121.4859 | -0.024657 | -0.14125 | -0.071521 | -0.1349 | -0.041561 | -0.070082 | -0.18633 | -0.27716 | -0.15888 | -0.21024 | -0.17963 | 0.13064 | 0.10105 | 0.076397 | 0.18453 | 0.021119 | -0.095479 | -0.025745 | -0.089125 | 0.004215 | -0.024306 | -0.14055 | -0.23139 | -0.1131 | -0.16447 | -0.13385 | 0.17642 | 0.14682 | 0.12217 | 0.23031 | -0.40781 | -0.35356 | -0.34088 | -0.28664
1659.4375 | 121.7148 | -0.23346 | 121.4722 | -0.015501 | -0.14125 | -0.0761 | -0.14406 | -0.041561 | -0.065504 | -0.19548 | -0.27716 | -0.1543 | -0.21024 | -0.18421 | 0.12149 | 0.10562 | 0.071818 | 0.19369 | 0.030275 | -0.095479 | -0.030324 | -0.098282 | 0.004215 | -0.019728 | -0.14971 | -0.23139 | -0.10853 | -0.16447 | -0.13843 | 0.16726 | 0.1514 | 0.11759 | 0.23947 | -0.39865 | -0.34898 | -0.33173 | -0.28206
1661.1406 | 121.7377 | -0.21515 | 121.4584 | -0.020079 | -0.14125 | -0.080679 | -0.14406 | -0.041561 | -0.070082 | -0.19091 | -0.27716 | -0.1543 | -0.20566 | -0.17963 | 0.12607 | 0.10562 | 0.076397 | 0.18453 | 0.025697 | -0.095479 | -0.034903 | -0.098282 | 0.004215 | -0.024306 | -0.14513 | -0.23139 | -0.10853 | -0.15989 | -0.13385 | 0.17184 | 0.1514 | 0.12217 | 0.23031 | -0.40323 | -0.35356 | -0.33173 | -0.28206
1662.9062 | 121.7697 | -0.17395 | 121.4355 | -0.024657 | -0.14125 | -0.0761 | -0.13032 | -0.041561 | -0.070082 | -0.18633 | -0.27716 | -0.1543 | -0.20566 | -0.17963 | 0.12607 | 0.10562 | 0.071818 | 0.18453 | 0.021119 | -0.095479 | -0.030324 | -0.084546 | 0.004215 | -0.024306 | -0.14055 | -0.23139 | -0.10853 | -0.15989 | -0.13385 | 0.17184 | 0.1514 | 0.11759 | 0.23031 | -0.40323 | -0.34898 | -0.33173 | -0.27748
1664.6719 | 121.7651 | -0.1831 | 121.4401 | -0.020079 | -0.14125 | -0.080679 | -0.14406 | -0.046138 | -0.065504 | -0.19091 | -0.27716 | -0.16346 | -0.21024 | -0.18421 | 0.12607 | 0.1102 | 0.071818 | 0.19369 | 0.025697 | -0.095479 | -0.034903 | -0.098282 | -0.000362 | -0.019728 | -0.14513 | -0.23139 | -0.11768 | -0.16447 | -0.13843 | 0.17184 | 0.15598 | 0.11759 | 0.23947 | -0.40323 | -0.34898 | -0.33631 | -0.28206
1666.4375 | 121.7697 | -0.17853 | 121.4493 | -0.024657 | -0.13668 | -0.085257 | -0.14406 | -0.046138 | -0.070082 | -0.19548 | -0.28174 | -0.15888 | -0.21024 | -0.18421 | 0.13064 | 0.096469 | 0.080975 | 0.18453 | 0.021119 | -0.0909 | -0.039481 | -0.098282 | -0.000362 | -0.024306 | -0.14971 | -0.23597 | -0.1131 | -0.16447 | -0.13843 | 0.17642 | 0.14225 | 0.12675 | 0.23031 | -0.41239 | -0.36272 | -0.34088 | -0.29122
1668.1406 | 121.8063 | -0.19226 | 121.4355 | -0.015501 | -0.14583 | -0.0761 | -0.13948 | -0.036983 | -0.065504 | -0.19091 | -0.27259 | -0.16346 | -0.21024 | -0.17963 | 0.12607 | 0.091891 | 0.080975 | 0.17996 | 0.030275 | -0.10006 | -0.030324 | -0.093703 | 0.008793 | -0.019728 | -0.14513 | -0.22681 | -0.11768 | -0.16447 | -0.13385 | 0.17184 | 0.13767 | 0.12675 | 0.22573 | -0.39865 | -0.35356 | -0.33631 | -0.29122
1669.9219 | 121.7056 | -0.20142 | 121.4539 | -0.024657 | -0.14583 | -0.071521 | -0.1349 | -0.041561 | -0.070082 | -0.19548 | -0.27259 | -0.16346 | -0.21024 | -0.18879 | 0.13064 | 0.10562 | 0.080975 | 0.17996 | 0.021119 | -0.10006 | -0.025745 | -0.089125 | 0.004215 | -0.024306 | -0.14971 | -0.22681 | -0.11768 | -0.16447 | -0.14301 | 0.17642 | 0.1514 | 0.12675 | 0.22573 | -0.40323 | -0.35356 | -0.34088 | -0.29122
1671.625 | 121.7102 | -0.22888 | 121.4401 | -0.024657 | -0.14583 | -0.0761 | -0.1349 | -0.041561 | -0.065504 | -0.18633 | -0.28174 | -0.16346 | -0.21024 | -0.17963 | 0.13064 | 0.096469 | 0.076397 | 0.17996 | 0.021119 | -0.10006 | -0.030324 | -0.089125 | 0.004215 | -0.019728 | -0.14055 | -0.23597 | -0.11768 | -0.16447 | -0.13385 | 0.17642 | 0.14225 | 0.12217 | 0.22573 | -0.41239 | -0.35814 | -0.34088 | -0.28664
1673.3906 | 121.701 | -0.21515 | 121.4676 | -0.029236 | -0.14125 | -0.080679 | -0.13032 | -0.032405 | -0.065504 | -0.19548 | -0.28632 | -0.16804 | -0.21482 | -0.18421 | 0.13522 | 0.10562 | 0.076397 | 0.17996 | 0.01654 | -0.095479 | -0.034903 | -0.084546 | 0.013371 | -0.019728 | -0.14971 | -0.24055 | -0.12226 | -0.16904 | -0.13843 | 0.181 | 0.1514 | 0.12217 | 0.22573 | -0.42154 | -0.36272 | -0.35004 | -0.29122
1675.0938 | 121.6599 | -0.24261 | 121.4722 | -0.033814 | -0.14583 | -0.071521 | -0.13032 | -0.046138 | -0.070082 | -0.19091 | -0.28174 | -0.16804 | -0.21024 | -0.17963 | 0.12149 | 0.10562 | 0.080975 | 0.18911 | 0.011962 | -0.10006 | -0.025745 | -0.084546 | -0.000362 | -0.024306 | -0.14513 | -0.23597 | -0.12226 | -0.16447 | -0.13385 | 0.16726 | 0.1514 | 0.12675 | 0.23489 | -0.40323 | -0.36272 | -0.33173 | -0.29122
1676.875 | 121.7148 | -0.2243 | 121.4539 | -0.029236 | -0.14125 | -0.080679 | -0.13948 | -0.041561 | -0.070082 | -0.18633 | -0.27716 | -0.16804 | -0.20566 | -0.17963 | 0.12607 | 0.10105 | 0.085554 | 0.18453 | 0.01654 | -0.095479 | -0.034903 | -0.093703 | 0.004215 | -0.024306 | -0.14055 | -0.23139 | -0.12226 | -0.15989 | -0.13385 | 0.17184 | 0.14682 | 0.13133 | 0.23031 | -0.40323 | -0.36272 | -0.33173 | -0.29122
1678.6406 | 121.7377 | -0.21515 | 121.4218 | -0.033814 | -0.14125 | -0.080679 | -0.1349 | -0.041561 | -0.070082 | -0.19548 | -0.28174 | -0.16346 | -0.21024 | -0.18421 | 0.13064 | 0.10562 | 0.076397 | 0.18453 | 0.011962 | -0.095479 | -0.034903 | -0.089125 | 0.004215 | -0.024306 | -0.14971 | -0.23597 | -0.11768 | -0.16447 | -0.13843 | 0.17642 | 0.1514 | 0.12217 | 0.23031 | -0.41239 | -0.35814 | -0.34088 | -0.28664
1680.4062 | 121.7102 | -0.23346 | 121.4493 | -0.033814 | -0.1321 | -0.0761 | -0.13948 | -0.041561 | -0.070082 | -0.19548 | -0.28174 | -0.15888 | -0.21024 | -0.17963 | 0.12607 | 0.10105 | 0.080975 | 0.18453 | 0.011962 | -0.086321 | -0.030324 | -0.093703 | 0.004215 | -0.024306 | -0.14971 | -0.23597 | -0.1131 | -0.16447 | -0.13385 | 0.17184 | 0.14682 | 0.12675 | 0.23031 | -0.40781 | -0.36272 | -0.33631 | -0.29122
1682.125 | 121.7789 | -0.20142 | 121.4539 | -0.033814 | -0.15041 | -0.071521 | -0.1349 | -0.041561 | -0.074661 | -0.19091 | -0.28174 | -0.16346 | -0.20566 | -0.18421 | 0.13064 | 0.10562 | 0.080975 | 0.18453 | 0.011962 | -0.10464 | -0.025745 | -0.089125 | 0.004215 | -0.028885 | -0.14513 | -0.23597 | -0.11768 | -0.15989 | -0.13843 | 0.17642 | 0.1514 | 0.12675 | 0.23031 | -0.41239 | -0.36272 | -0.33631 | -0.28664
1683.8906 | 121.7194 | -0.21515 | 121.4355 | -0.024657 | -0.14125 | -0.080679 | -0.13948 | -0.032405 | -0.070082 | -0.19091 | -0.27716 | -0.16346 | -0.20109 | -0.17963 | 0.12149 | 0.10105 | 0.076397 | 0.18453 | 0.021119 | -0.095479 | -0.034903 | -0.093703 | 0.013371 | -0.024306 | -0.14513 | -0.23139 | -0.11768 | -0.15531 | -0.13385 | 0.16726 | 0.14682 | 0.12217 | 0.23031 | -0.39865 | -0.35356 | -0.32257 | -0.27748
1685.6562 | 121.6736 | -0.23346 | 121.4905 | -0.029236 | -0.14125 | -0.071521 | -0.1349 | -0.041561 | -0.070082 | -0.19091 | -0.28174 | -0.16346 | -0.20566 | -0.17505 | 0.12607 | 0.10105 | 0.076397 | 0.18453 | 0.01654 | -0.095479 | -0.025745 | -0.089125 | 0.004215 | -0.024306 | -0.14513 | -0.23597 | -0.11768 | -0.15989 | -0.12928 | 0.17184 | 0.14682 | 0.12217 | 0.23031 | -0.40781 | -0.35814 | -0.33173 | -0.28206
1687.4219 | 121.6278 | -0.21515 | 121.4767 | -0.029236 | -0.1321 | -0.0761 | -0.13948 | -0.041561 | -0.070082 | -0.18633 | -0.2909 | -0.15888 | -0.21024 | -0.18421 | 0.12607 | 0.10562 | 0.071818 | 0.18911 | 0.01654 | -0.086321 | -0.030324 | -0.093703 | 0.004215 | -0.024306 | -0.14055 | -0.24512 | -0.1131 | -0.16447 | -0.13843 | 0.17184 | 0.1514 | 0.11759 | 0.23489 | -0.41696 | -0.36272 | -0.33631 | -0.28206
1689.125 | 121.7148 | -0.23346 | 121.4447 | -0.024657 | -0.14583 | -0.080679 | -0.13032 | -0.041561 | -0.070082 | -0.19091 | -0.28174 | -0.16346 | -0.20566 | -0.18421 | 0.12149 | 0.1102 | 0.080975 | 0.18911 | 0.021119 | -0.10006 | -0.034903 | -0.084546 | 0.004215 | -0.024306 | -0.14513 | -0.23597 | -0.11768 | -0.15989 | -0.13843 | 0.16726 | 0.15598 | 0.12675 | 0.23489 | -0.40323 | -0.36272 | -0.32715 | -0.28664
1690.9062 | 121.669 | -0.22888 | 121.4813 | -0.024657 | -0.14583 | -0.085257 | -0.13032 | -0.041561 | -0.070082 | -0.19091 | -0.27716 | -0.15888 | -0.20566 | -0.18421 | 0.12607 | 0.10562 | 0.076397 | 0.17996 | 0.021119 | -0.10006 | -0.039481 | -0.084546 | 0.004215 | -0.024306 | -0.14513 | -0.23139 | -0.1131 | -0.15989 | -0.13843 | 0.17184 | 0.1514 | 0.12217 | 0.22573 | -0.40323 | -0.35356 | -0.33173 | -0.28206
1692.6875 | 121.637 | -0.23804 | 121.4859 | -0.020079 | -0.13668 | -0.0761 | -0.12574 | -0.046138 | -0.074661 | -0.19548 | -0.28174 | -0.16346 | -0.21024 | -0.17963 | 0.12607 | 0.096469 | 0.080975 | 0.18911 | 0.025697 | -0.0909 | -0.030324 | -0.079968 | -0.000362 | -0.028885 | -0.14971 | -0.23597 | -0.11768 | -0.16447 | -0.13385 | 0.17184 | 0.14225 | 0.12675 | 0.23489 | -0.40781 | -0.36272 | -0.33631 | -0.29122
1694.3906 | 121.6827 | -0.24261 | 121.4905 | -0.033814 | -0.14125 | -0.080679 | -0.1349 | -0.046138 | -0.070082 | -0.18633 | -0.28632 | -0.16804 | -0.21482 | -0.17963 | 0.12149 | 0.096469 | 0.076397 | 0.17996 | 0.011962 | -0.095479 | -0.034903 | -0.089125 | -0.000362 | -0.024306 | -0.14055 | -0.24055 | -0.12226 | -0.16904 | -0.13385 | 0.16726 | 0.14225 | 0.12217 | 0.22573 | -0.40781 | -0.36272 | -0.33631 | -0.29122
1696.1562 | 121.7239 | -0.20599 | 121.4447 | -0.038393 | -0.15041 | -0.071521 | -0.13948 | -0.036983 | -0.074661 | -0.19548 | -0.28174 | -0.1543 | -0.19651 | -0.17963 | 0.13522 | 0.096469 | 0.080975 | 0.18453 | 0.007383 | -0.10464 | -0.025745 | -0.093703 | 0.008793 | -0.028885 | -0.14971 | -0.23597 | -0.10853 | -0.15073 | -0.13385 | 0.181 | 0.14225 | 0.12675 | 0.23031 | -0.41696 | -0.36272 | -0.33173 | -0.27748
1697.8594 | 121.7102 | -0.19226 | 121.4859 | -0.015501 | -0.14583 | -0.080679 | -0.1349 | -0.046138 | -0.079239 | -0.19548 | -0.27716 | -0.16346 | -0.20566 | -0.17963 | 0.13064 | 0.10105 | 0.080975 | 0.17996 | 0.030275 | -0.10006 | -0.034903 | -0.089125 | -0.000362 | -0.033463 | -0.14971 | -0.23139 | -0.11768 | -0.15989 | -0.13385 | 0.17642 | 0.14682 | 0.12675 | 0.22573 | -0.40781 | -0.35814 | -0.33631 | -0.28664
1699.625 | 121.7194 | -0.22888 | 121.4767 | -0.024657 | -0.1321 | -0.080679 | -0.14406 | -0.041561 | -0.074661 | -0.18633 | -0.27716 | -0.16804 | -0.20566 | -0.18879 | 0.12607 | 0.096469 | 0.080975 | 0.18911 | 0.021119 | -0.086321 | -0.034903 | -0.098282 | 0.004215 | -0.028885 | -0.14055 | -0.23139 | -0.12226 | -0.15989 | -0.14301 | 0.17184 | 0.14225 | 0.12675 | 0.23489 | -0.40323 | -0.35814 | -0.33173 | -0.28664
1701.3281 | 121.7377 | -0.21057 | 121.4447 | -0.033814 | -0.14583 | -0.0761 | -0.1349 | -0.050716 | -0.074661 | -0.19548 | -0.27259 | -0.16346 | -0.20566 | -0.18421 | 0.13064 | 0.10105 | 0.080975 | 0.18911 | 0.011962 | -0.10006 | -0.030324 | -0.089125 | -0.00494 | -0.028885 | -0.14971 | -0.22681 | -0.11768 | -0.15989 | -0.13843 | 0.17642 | 0.14682 | 0.12675 | 0.23489 | -0.40323 | -0.35356 | -0.33631 | -0.28664
1703.1094 | 121.6736 | -0.23804 | 121.463 | -0.029236 | -0.14583 | -0.085257 | -0.14406 | -0.046138 | -0.074661 | -0.18633 | -0.27716 | -0.16346 | -0.20566 | -0.18421 | 0.13064 | 0.1102 | 0.076397 | 0.18911 | 0.01654 | -0.10006 | -0.039481 | -0.098282 | -0.000362 | -0.028885 | -0.14055 | -0.23139 | -0.11768 | -0.15989 | -0.13843 | 0.17642 | 0.15598 | 0.12217 | 0.23489 | -0.40781 | -0.35356 | -0.33631 | -0.28206
1704.8125 | 121.6644 | -0.21973 | 121.4905 | -0.033814 | -0.14125 | -0.0761 | -0.13948 | -0.046138 | -0.065504 | -0.19091 | -0.27716 | -0.16804 | -0.20109 | -0.17963 | 0.12149 | 0.10562 | 0.080975 | 0.17996 | 0.011962 | -0.095479 | -0.030324 | -0.093703 | -0.000362 | -0.019728 | -0.14513 | -0.23139 | -0.12226 | -0.15531 | -0.13385 | 0.16726 | 0.1514 | 0.12675 | 0.22573 | -0.39865 | -0.35814 | -0.32257 | -0.28206
1706.5781 | 121.6827 | -0.23346 | 121.4905 | -0.024657 | -0.12752 | -0.0761 | -0.14406 | -0.046138 | -0.070082 | -0.19091 | -0.27716 | -0.1543 | -0.20566 | -0.17963 | 0.13064 | 0.10105 | 0.090132 | 0.18453 | 0.021119 | -0.081742 | -0.030324 | -0.098282 | -0.000362 | -0.024306 | -0.14513 | -0.23139 | -0.10853 | -0.15989 | -0.13385 | 0.17642 | 0.14682 | 0.13591 | 0.23031 | -0.40781 | -0.3673 | -0.33631 | -0.2958
1708.3438 | 121.7789 | -0.17853 | 121.4493 | -0.033814 | -0.13668 | -0.085257 | -0.13948 | -0.041561 | -0.070082 | -0.19091 | -0.27716 | -0.16346 | -0.21024 | -0.18421 | 0.13064 | 0.10562 | 0.076397 | 0.19369 | 0.011962 | -0.0909 | -0.039481 | -0.093703 | 0.004215 | -0.024306 | -0.14513 | -0.23139 | -0.11768 | -0.16447 | -0.13843 | 0.17642 | 0.1514 | 0.12217 | 0.23947 | -0.40781 | -0.35356 | -0.34088 | -0.28664
1710.0469 | 121.6827 | -0.22888 | 121.4767 | -0.029236 | -0.14583 | -0.0761 | -0.13948 | -0.041561 | -0.074661 | -0.19548 | -0.2909 | -0.16346 | -0.21482 | -0.17963 | 0.12607 | 0.10105 | 0.080975 | 0.18453 | 0.01654 | -0.10006 | -0.030324 | -0.093703 | 0.004215 | -0.028885 | -0.14971 | -0.24512 | -0.11768 | -0.16904 | -0.13385 | 0.17184 | 0.14682 | 0.12675 | 0.23031 | -0.41696 | -0.37187 | -0.34088 | -0.2958
1711.8125 | 121.6599 | -0.23346 | 121.463 | -0.033814 | -0.14583 | -0.0761 | -0.13948 | -0.041561 | -0.070082 | -0.19091 | -0.27259 | -0.16804 | -0.21024 | -0.18421 | 0.12149 | 0.096469 | 0.071818 | 0.18911 | 0.011962 | -0.10006 | -0.030324 | -0.093703 | 0.004215 | -0.024306 | -0.14513 | -0.22681 | -0.12226 | -0.16447 | -0.13843 | 0.16726 | 0.14225 | 0.11759 | 0.23489 | -0.39407 | -0.3444 | -0.33173 | -0.28206
1713.5938 | 121.7239 | -0.21057 | 121.4584 | -0.033814 | -0.14125 | -0.0761 | -0.13948 | -0.036983 | -0.074661 | -0.19091 | -0.27259 | -0.15888 | -0.20109 | -0.18879 | 0.13064 | 0.10105 | 0.076397 | 0.18453 | 0.011962 | -0.095479 | -0.030324 | -0.093703 | 0.008793 | -0.028885 | -0.14513 | -0.22681 | -0.1131 | -0.15531 | -0.14301 | 0.17642 | 0.14682 | 0.12217 | 0.23031 | -0.40323 | -0.34898 | -0.33173 | -0.27748
1715.2969 | 121.701 | -0.2243 | 121.463 | -0.038393 | -0.13668 | -0.085257 | -0.1349 | -0.041561 | -0.074661 | -0.19091 | -0.27716 | -0.16804 | -0.20566 | -0.17963 | 0.12149 | 0.10562 | 0.080975 | 0.18453 | 0.007383 | -0.0909 | -0.039481 | -0.089125 | 0.004215 | -0.028885 | -0.14513 | -0.23139 | -0.12226 | -0.15989 | -0.13385 | 0.16726 | 0.1514 | 0.12675 | 0.23031 | -0.39865 | -0.35814 | -0.32715 | -0.28664
1717.0625 | 121.6965 | -0.22888 | 121.4767 | -0.033814 | -0.14125 | -0.0761 | -0.1349 | -0.041561 | -0.074661 | -0.19548 | -0.28632 | -0.16346 | -0.21024 | -0.18421 | 0.12607 | 0.1102 | 0.080975 | 0.18453 | 0.011962 | -0.095479 | -0.030324 | -0.089125 | 0.004215 | -0.028885 | -0.14971 | -0.24055 | -0.11768 | -0.16447 | -0.13843 | 0.17184 | 0.15598 | 0.12675 | 0.23031 | -0.41239 | -0.3673 | -0.33631 | -0.29122
1718.7656 | 121.701 | -0.22888 | 121.463 | -0.038393 | -0.14583 | -0.080679 | -0.13948 | -0.041561 | -0.070082 | -0.18633 | -0.28174 | -0.16804 | -0.21024 | -0.18421 | 0.13064 | 0.1102 | 0.080975 | 0.18453 | 0.007383 | -0.10006 | -0.034903 | -0.093703 | 0.004215 | -0.024306 | -0.14055 | -0.23597 | -0.12226 | -0.16447 | -0.13843 | 0.17642 | 0.15598 | 0.12675 | 0.23031 | -0.41239 | -0.36272 | -0.34088 | -0.29122
1720.5469 | 121.6599 | -0.24261 | 121.5042 | -0.033814 | -0.14125 | -0.080679 | -0.1349 | -0.036983 | -0.074661 | -0.19091 | -0.28174 | -0.16346 | -0.21024 | -0.17963 | 0.13522 | 0.10562 | 0.080975 | 0.19369 | 0.011962 | -0.095479 | -0.034903 | -0.089125 | 0.008793 | -0.028885 | -0.14513 | -0.23597 | -0.11768 | -0.16447 | -0.13385 | 0.181 | 0.1514 | 0.12675 | 0.23947 | -0.41696 | -0.36272 | -0.34546 | -0.29122
1722.3281 | 121.7468 | -0.21973 | 121.4767 | -0.029236 | -0.14583 | -0.0761 | -0.13948 | -0.046138 | -0.079239 | -0.18175 | -0.2909 | -0.16346 | -0.21482 | -0.18421 | 0.13064 | 0.10562 | 0.080975 | 0.18911 | 0.01654 | -0.10006 | -0.030324 | -0.093703 | -0.000362 | -0.033463 | -0.13597 | -0.24512 | -0.11768 | -0.16904 | -0.13843 | 0.17642 | 0.1514 | 0.12675 | 0.23489 | -0.42154 | -0.37187 | -0.34546 | -0.2958
1724.0938 | 121.669 | -0.26093 | 121.4767 | -0.033814 | -0.1321 | -0.080679 | -0.14864 | -0.041561 | -0.065504 | -0.19091 | -0.28174 | -0.17262 | -0.20566 | -0.19337 | 0.12149 | 0.1102 | 0.080975 | 0.18453 | 0.011962 | -0.086321 | -0.034903 | -0.10286 | 0.004215 | -0.019728 | -0.14513 | -0.23597 | -0.12684 | -0.15989 | -0.14759 | 0.16726 | 0.15598 | 0.12675 | 0.23031 | -0.40323 | -0.36272 | -0.32715 | -0.28664
1725.7969 | 121.8201 | -0.19684 | 121.4539 | -0.038393 | -0.14583 | -0.080679 | -0.1349 | -0.046138 | -0.074661 | -0.19091 | -0.2909 | -0.17262 | -0.21482 | -0.17963 | 0.12607 | 0.10562 | 0.090132 | 0.19369 | 0.007383 | -0.10006 | -0.034903 | -0.089125 | -0.000362 | -0.028885 | -0.14513 | -0.24512 | -0.12684 | -0.16904 | -0.13385 | 0.17184 | 0.1514 | 0.13591 | 0.23947 | -0.41696 | -0.38103 | -0.34088 | -0.30495
1727.5781 | 121.7606 | -0.18768 | 121.4539 | -0.033814 | -0.14583 | -0.0761 | -0.13948 | -0.055294 | -0.079239 | -0.19091 | -0.28632 | -0.16346 | -0.21482 | -0.18421 | 0.12607 | 0.1102 | 0.090132 | 0.19369 | 0.011962 | -0.10006 | -0.030324 | -0.093703 | -0.009518 | -0.033463 | -0.14513 | -0.24055 | -0.11768 | -0.16904 | -0.13843 | 0.17184 | 0.15598 | 0.13591 | 0.23947 | -0.41239 | -0.37645 | -0.34088 | -0.30495
1729.3594 | 121.7422 | -0.21515 | 121.4767 | -0.038393 | -0.14583 | -0.085257 | -0.14406 | -0.046138 | -0.079239 | -0.19091 | -0.2909 | -0.17262 | -0.2194 | -0.18879 | 0.13064 | 0.1102 | 0.085554 | 0.19827 | 0.007383 | -0.10006 | -0.039481 | -0.098282 | -0.000362 | -0.033463 | -0.14513 | -0.24512 | -0.12684 | -0.17362 | -0.14301 | 0.17642 | 0.15598 | 0.13133 | 0.24404 | -0.42154 | -0.37645 | -0.35004 | -0.30495
1731.0469 | 121.7789 | -0.19226 | 121.4493 | -0.033814 | -0.14583 | -0.089836 | -0.14406 | -0.036983 | -0.083817 | -0.19548 | -0.28632 | -0.1772 | -0.21024 | -0.19337 | 0.13064 | 0.1102 | 0.090132 | 0.19369 | 0.011962 | -0.10006 | -0.04406 | -0.098282 | 0.008793 | -0.038041 | -0.14971 | -0.24055 | -0.13142 | -0.16447 | -0.14759 | 0.17642 | 0.15598 | 0.13591 | 0.23947 | -0.41696 | -0.37645 | -0.34088 | -0.30037
1732.8281 | 121.7422 | -0.21515 | 121.4676 | -0.033814 | -0.15041 | -0.089836 | -0.14406 | -0.046138 | -0.070082 | -0.19548 | -0.2909 | -0.16804 | -0.21482 | -0.18421 | 0.13064 | 0.10105 | 0.09471 | 0.19369 | 0.011962 | -0.10464 | -0.04406 | -0.098282 | -0.000362 | -0.024306 | -0.14971 | -0.24512 | -0.12226 | -0.16904 | -0.13843 | 0.17642 | 0.14682 | 0.14049 | 0.23947 | -0.42154 | -0.38561 | -0.34546 | -0.30953
1734.5312 | 121.7697 | -0.19684 | 121.4447 | -0.038393 | -0.15041 | -0.080679 | -0.14406 | -0.041561 | -0.083817 | -0.19548 | -0.28632 | -0.16804 | -0.21024 | -0.19337 | 0.13064 | 0.11478 | 0.085554 | 0.18911 | 0.007383 | -0.10464 | -0.034903 | -0.098282 | 0.004215 | -0.038041 | -0.14971 | -0.24055 | -0.12226 | -0.16447 | -0.14759 | 0.17642 | 0.16056 | 0.13133 | 0.23489 | -0.41696 | -0.37188 | -0.34088 | -0.2958
1736.2969 | 121.6553 | -0.24261 | 121.463 | -0.038393 | -0.14583 | -0.085257 | -0.14864 | -0.055294 | -0.079239 | -0.19548 | -0.2909 | -0.16804 | -0.2194 | -0.19337 | 0.1398 | 0.1102 | 0.09471 | 0.19369 | 0.007383 | -0.10006 | -0.039481 | -0.10286 | -0.009518 | -0.033463 | -0.14971 | -0.24512 | -0.12226 | -0.17362 | -0.14759 | 0.18557 | 0.15598 | 0.14049 | 0.23947 | -0.4307 | -0.38561 | -0.3592 | -0.31411
1738 | 121.6919 | -0.24261 | 121.4584 | -0.033814 | -0.14583 | -0.085257 | -0.15321 | -0.055294 | -0.079239 | -0.20006 | -0.2909 | -0.16804 | -0.2194 | -0.18421 | 0.1398 | 0.1102 | 0.085554 | 0.18911 | 0.011962 | -0.10006 | -0.039481 | -0.10744 | -0.009518 | -0.033463 | -0.15429 | -0.24512 | -0.12226 | -0.17362 | -0.13843 | 0.18557 | 0.15598 | 0.13133 | 0.23489 | -0.4307 | -0.37645 | -0.3592 | -0.30495
1739.7656 | 121.7148 | -0.22888 | 121.4813 | -0.029236 | -0.15957 | -0.085257 | -0.14406 | -0.055294 | -0.074661 | -0.19091 | -0.28632 | -0.17262 | -0.2194 | -0.19337 | 0.1398 | 0.11478 | 0.090132 | 0.19827 | 0.01654 | -0.11379 | -0.039481 | -0.098282 | -0.009518 | -0.028885 | -0.14513 | -0.24055 | -0.12684 | -0.17362 | -0.14759 | 0.18557 | 0.16056 | 0.13591 | 0.24404 | -0.42612 | -0.37645 | -0.3592 | -0.30953
1741.4688 | 121.756 | -0.21057 | 121.463 | -0.038393 | -0.15499 | -0.085257 | -0.13948 | -0.055294 | -0.088396 | -0.19548 | -0.29548 | -0.17262 | -0.21482 | -0.18879 | 0.14438 | 0.11478 | 0.085554 | 0.20285 | 0.007383 | -0.10921 | -0.039481 | -0.093703 | -0.009518 | -0.04262 | -0.14971 | -0.2497 | -0.12684 | -0.16904 | -0.14301 | 0.19015 | 0.16056 | 0.13133 | 0.24862 | -0.43985 | -0.38103 | -0.3592 | -0.30037
1743.2344 | 121.7102 | -0.22888 | 121.4951 | -0.038393 | -0.15041 | -0.089836 | -0.14864 | -0.059872 | -0.079239 | -0.19548 | -0.30006 | -0.16804 | -0.22398 | -0.19337 | 0.13522 | 0.11478 | 0.090132 | 0.19827 | 0.007383 | -0.10464 | -0.04406 | -0.10286 | -0.014096 | -0.033463 | -0.14971 | -0.25428 | -0.12226 | -0.1782 | -0.14759 | 0.181 | 0.16056 | 0.13591 | 0.24404 | -0.43528 | -0.39019 | -0.3592 | -0.31411
1745.0156 | 121.7194 | -0.2243 | 121.4539 | -0.042971 | -0.15499 | -0.089836 | -0.14406 | -0.055294 | -0.079239 | -0.20006 | -0.2909 | -0.1772 | -0.22398 | -0.18879 | 0.14438 | 0.11936 | 0.09471 | 0.19827 | 0.002805 | -0.10921 | -0.04406 | -0.098282 | -0.009518 | -0.033463 | -0.15429 | -0.24512 | -0.13142 | -0.1782 | -0.14301 | 0.19015 | 0.16514 | 0.14049 | 0.24404 | -0.43528 | -0.38561 | -0.36835 | -0.31869
1746.7969 | 121.7834 | -0.19226 | 121.4355 | -0.038393 | -0.15041 | -0.085257 | -0.14406 | -0.055294 | -0.079239 | -0.20922 | -0.29548 | -0.17262 | -0.21482 | -0.19795 | 0.14438 | 0.11478 | 0.085554 | 0.18911 | 0.007383 | -0.10464 | -0.039481 | -0.098282 | -0.009518 | -0.033463 | -0.16344 | -0.2497 | -0.12684 | -0.16904 | -0.15217 | 0.19015 | 0.16056 | 0.13133 | 0.23489 | -0.43985 | -0.38103 | -0.3592 | -0.30037
1748.5 | 121.6599 | -0.24719 | 121.4447 | -0.047549 | -0.15499 | -0.089836 | -0.15321 | -0.059872 | -0.083817 | -0.20006 | -0.29548 | -0.18177 | -0.22398 | -0.20253 | 0.14896 | 0.11478 | 0.09471 | 0.19827 | -0.001773 | -0.10921 | -0.04406 | -0.10744 | -0.014096 | -0.038041 | -0.15429 | -0.2497 | -0.136 | -0.1782 | -0.15675 | 0.19473 | 0.16056 | 0.14049 | 0.24404 | -0.44443 | -0.39019 | -0.37293 | -0.31869
1750.25 | 121.7422 | -0.23346 | 121.4447 | -0.038393 | -0.15499 | -0.089836 | -0.15321 | -0.055294 | -0.088396 | -0.20922 | -0.29548 | -0.1772 | -0.2194 | -0.19795 | 0.1398 | 0.11936 | 0.090132 | 0.19827 | 0.007383 | -0.10921 | -0.04406 | -0.10744 | -0.009518 | -0.04262 | -0.16344 | -0.2497 | -0.13142 | -0.17362 | -0.15217 | 0.18557 | 0.16514 | 0.13591 | 0.24404 | -0.43528 | -0.38561 | -0.3592 | -0.30953
1752.0312 | 121.7972 | -0.17853 | 121.431 | -0.047549 | -0.14583 | -0.094414 | -0.14864 | -0.055294 | -0.088396 | -0.20464 | -0.29548 | -0.18177 | -0.22398 | -0.19337 | 0.14438 | 0.11936 | 0.09471 | 0.20742 | -0.001773 | -0.10006 | -0.048638 | -0.10286 | -0.009518 | -0.04262 | -0.15886 | -0.2497 | -0.136 | -0.1782 | -0.14759 | 0.19015 | 0.16514 | 0.14049 | 0.2532 | -0.43985 | -0.39019 | -0.36835 | -0.31869
1753.75 | 121.6461 | -0.23804 | 121.4951 | -0.042971 | -0.15041 | -0.094414 | -0.14864 | -0.055294 | -0.083817 | -0.20006 | -0.29548 | -0.18177 | -0.2194 | -0.18879 | 0.14438 | 0.11936 | 0.090132 | 0.20285 | 0.002805 | -0.10464 | -0.048638 | -0.10286 | -0.009518 | -0.038041 | -0.15429 | -0.2497 | -0.136 | -0.17362 | -0.14301 | 0.19015 | 0.16514 | 0.13591 | 0.24862 | -0.43985 | -0.38561 | -0.36378 | -0.30953
1755.5156 | 121.7606 | -0.21057 | 121.4355 | -0.047549 | -0.15041 | -0.098993 | -0.15321 | -0.059872 | -0.088396 | -0.20464 | -0.30006 | -0.1772 | -0.22398 | -0.20253 | 0.14896 | 0.12394 | 0.090132 | 0.20285 | -0.001773 | -0.10464 | -0.053217 | -0.10744 | -0.014096 | -0.04262 | -0.15886 | -0.25428 | -0.13142 | -0.1782 | -0.15675 | 0.19473 | 0.16971 | 0.13591 | 0.24862 | -0.44901 | -0.39019 | -0.37293 | -0.31411
1757.2969 | 121.7422 | -0.2243 | 121.431 | -0.042971 | -0.15957 | -0.094414 | -0.14864 | -0.069028 | -0.088396 | -0.2138 | -0.29548 | -0.17262 | -0.22856 | -0.20253 | 0.14896 | 0.12851 | 0.09471 | 0.20742 | 0.002805 | -0.11379 | -0.048638 | -0.10286 | -0.023252 | -0.04262 | -0.16802 | -0.2497 | -0.12684 | -0.18278 | -0.15675 | 0.19473 | 0.17429 | 0.14049 | 0.2532 | -0.44443 | -0.39019 | -0.37751 | -0.32327
1759 | 121.7422 | -0.21057 | 121.4584 | -0.052128 | -0.15957 | -0.098993 | -0.16237 | -0.06445 | -0.088396 | -0.20922 | -0.29548 | -0.18177 | -0.22856 | -0.20253 | 0.14896 | 0.12851 | 0.09471 | 0.20285 | -0.006352 | -0.11379 | -0.053217 | -0.1166 | -0.018674 | -0.04262 | -0.16344 | -0.2497 | -0.136 | -0.18278 | -0.15675 | 0.19473 | 0.17429 | 0.14049 | 0.24862 | -0.44443 | -0.39019 | -0.37751 | -0.32327
1760.7656 | 121.6553 | -0.27466 | 121.4813 | -0.052128 | -0.15957 | -0.094414 | -0.14406 | -0.06445 | -0.083817 | -0.20464 | -0.29548 | -0.18177 | -0.22398 | -0.20253 | 0.15353 | 0.12851 | 0.09471 | 0.20742 | -0.006352 | -0.11379 | -0.048638 | -0.098282 | -0.018674 | -0.038041 | -0.15886 | -0.2497 | -0.136 | -0.1782 | -0.15675 | 0.19931 | 0.17429 | 0.14049 | 0.2532 | -0.44901 | -0.39019 | -0.37751 | -0.31869
1762.5312 | 121.7422 | -0.2243 | 121.4447 | -0.047549 | -0.16415 | -0.098993 | -0.14406 | -0.06445 | -0.088396 | -0.20922 | -0.29548 | -0.1772 | -0.23313 | -0.19795 | 0.14438 | 0.11478 | 0.10387 | 0.20742 | -0.001773 | -0.11837 | -0.053217 | -0.098282 | -0.018674 | -0.04262 | -0.16344 | -0.2497 | -0.13142 | -0.18736 | -0.15217 | 0.19015 | 0.16056 | 0.14964 | 0.2532 | -0.43985 | -0.39935 | -0.37751 | -0.337
1764.2969 | 121.7789 | -0.19684 | 121.4355 | -0.052128 | -0.15957 | -0.10357 | -0.15321 | -0.059872 | -0.088396 | -0.20922 | -0.29548 | -0.18177 | -0.22856 | -0.20253 | 0.14896 | 0.12394 | 0.099289 | 0.20285 | -0.006352 | -0.11379 | -0.057796 | -0.10744 | -0.014096 | -0.04262 | -0.16344 | -0.2497 | -0.136 | -0.18278 | -0.15675 | 0.19473 | 0.16971 | 0.14506 | 0.24862 | -0.44443 | -0.39477 | -0.37751 | -0.32784
1766.0625 | 121.6553 | -0.27008 | 121.463 | -0.042971 | -0.15499 | -0.098993 | -0.15779 | -0.06445 | -0.083817 | -0.20464 | -0.30463 | -0.18635 | -0.22856 | -0.19795 | 0.15353 | 0.11936 | 0.09471 | 0.212 | 0.002805 | -0.10921 | -0.053217 | -0.11202 | -0.018674 | -0.038041 | -0.15886 | -0.25886 | -0.14058 | -0.18278 | -0.15217 | 0.19931 | 0.16514 | 0.14049 | 0.25778 | -0.45817 | -0.39935 | -0.38209 | -0.32327
1767.7812 | 121.7834 | -0.21973 | 121.4218 | -0.052128 | -0.15041 | -0.094414 | -0.15321 | -0.055294 | -0.088396 | -0.20464 | -0.30463 | -0.1772 | -0.22856 | -0.20253 | 0.14438 | 0.12394 | 0.099289 | 0.20285 | -0.006352 | -0.10464 | -0.048638 | -0.10744 | -0.009518 | -0.04262 | -0.15886 | -0.25886 | -0.13142 | -0.18278 | -0.15675 | 0.19015 | 0.16971 | 0.14506 | 0.24862 | -0.44901 | -0.40392 | -0.37293 | -0.32784
1769.5312 | 121.7972 | -0.20142 | 121.4172 | -0.047549 | -0.15499 | -0.094414 | -0.15321 | -0.06445 | -0.092974 | -0.20464 | -0.30006 | -0.1772 | -0.23313 | -0.20253 | 0.14896 | 0.12394 | 0.099289 | 0.20285 | -0.001773 | -0.10921 | -0.048638 | -0.10744 | -0.018674 | -0.047198 | -0.15886 | -0.25428 | -0.13142 | -0.18736 | -0.15675 | 0.19473 | 0.16971 | 0.14506 | 0.24862 | -0.44901 | -0.39935 | -0.38209 | -0.33242
1771.3125 | 121.7148 | -0.23346 | 121.4355 | -0.052128 | -0.15957 | -0.094414 | -0.15321 | -0.059872 | -0.083817 | -0.20464 | -0.30006 | -0.18177 | -0.22856 | -0.2071 | 0.14438 | 0.12394 | 0.10387 | 0.20742 | -0.006352 | -0.11379 | -0.048638 | -0.10744 | -0.014096 | -0.038041 | -0.15886 | -0.25428 | -0.136 | -0.18278 | -0.16133 | 0.19015 | 0.16971 | 0.14964 | 0.2532 | -0.44443 | -0.40392 | -0.37293 | -0.33242
1773.0938 | 121.7697 | -0.20599 | 121.4401 | -0.052128 | -0.15499 | -0.098993 | -0.15779 | -0.059872 | -0.088396 | -0.20922 | -0.30006 | -0.18177 | -0.22856 | -0.20253 | 0.14438 | 0.12394 | 0.099289 | 0.20285 | -0.006352 | -0.10921 | -0.053217 | -0.11202 | -0.014096 | -0.04262 | -0.16344 | -0.25428 | -0.136 | -0.18278 | -0.15675 | 0.19015 | 0.16971 | 0.14506 | 0.24862 | -0.44443 | -0.39935 | -0.37293 | -0.32784
1774.875 | 121.7056 | -0.24261 | 121.4676 | -0.047549 | -0.16415 | -0.098993 | -0.15321 | -0.059872 | -0.088396 | -0.20006 | -0.30006 | -0.18177 | -0.22856 | -0.20253 | 0.15353 | 0.11936 | 0.10387 | 0.20742 | -0.001773 | -0.11837 | -0.053217 | -0.10744 | -0.014096 | -0.04262 | -0.15429 | -0.25428 | -0.136 | -0.18278 | -0.15675 | 0.19931 | 0.16514 | 0.14964 | 0.2532 | -0.45359 | -0.40392 | -0.38209 | -0.33242
1776.5625 | 121.6599 | -0.27008 | 121.4859 | -0.042971 | -0.15957 | -0.098993 | -0.15321 | -0.06445 | -0.083817 | -0.20464 | -0.2909 | -0.1772 | -0.23771 | -0.19337 | 0.15353 | 0.11936 | 0.099289 | 0.20742 | 0.002805 | -0.11379 | -0.053217 | -0.10744 | -0.018674 | -0.038041 | -0.15886 | -0.24512 | -0.13142 | -0.19194 | -0.14759 | 0.19931 | 0.16514 | 0.14506 | 0.2532 | -0.44443 | -0.39019 | -0.39125 | -0.337
1778.3438 | 121.6553 | -0.26093 | 121.4996 | -0.047549 | -0.15499 | -0.098993 | -0.15321 | -0.059872 | -0.088396 | -0.20006 | -0.29548 | -0.18177 | -0.22398 | -0.20253 | 0.15353 | 0.11936 | 0.10387 | 0.20285 | -0.001773 | -0.10921 | -0.053217 | -0.10744 | -0.014096 | -0.04262 | -0.15429 | -0.2497 | -0.136 | -0.1782 | -0.15675 | 0.19931 | 0.16514 | 0.14964 | 0.24862 | -0.44901 | -0.39935 | -0.37751 | -0.32784
1780.0625 | 121.6827 | -0.2655 | 121.4676 | -0.056706 | -0.15041 | -0.098993 | -0.15779 | -0.059872 | -0.088396 | -0.19548 | -0.30006 | -0.1772 | -0.22398 | -0.20253 | 0.14896 | 0.12394 | 0.09471 | 0.20742 | -0.01093 | -0.10464 | -0.053217 | -0.11202 | -0.014096 | -0.04262 | -0.14971 | -0.25428 | -0.13142 | -0.1782 | -0.15675 | 0.19473 | 0.16971 | 0.14049 | 0.2532 | -0.44901 | -0.39477 | -0.37293 | -0.31869
1781.8438 | 121.756 | -0.2243 | 121.4447 | -0.052128 | -0.15957 | -0.094414 | -0.15779 | -0.069028 | -0.092974 | -0.2138 | -0.29548 | -0.1772 | -0.23313 | -0.20253 | 0.14896 | 0.11936 | 0.099289 | 0.20742 | -0.006352 | -0.11379 | -0.048638 | -0.11202 | -0.023252 | -0.047198 | -0.16802 | -0.2497 | -0.13142 | -0.18736 | -0.15675 | 0.19473 | 0.16514 | 0.14506 | 0.2532 | -0.44443 | -0.39477 | -0.38209 | -0.33242
1783.6094 | 121.7651 | -0.2243 | 121.431 | -0.052128 | -0.15499 | -0.094414 | -0.15779 | -0.06445 | -0.088396 | -0.20922 | -0.30463 | -0.18177 | -0.22856 | -0.19795 | 0.14896 | 0.11936 | 0.099289 | 0.20742 | -0.006352 | -0.10921 | -0.048638 | -0.11202 | -0.018674 | -0.04262 | -0.16344 | -0.25886 | -0.136 | -0.18278 | -0.15217 | 0.19473 | 0.16514 | 0.14506 | 0.2532 | -0.45359 | -0.40392 | -0.37751 | -0.32784
1785.375 | 121.7102 | -0.22888 | 121.4355 | -0.047549 | -0.15499 | -0.098993 | -0.15779 | -0.06445 | -0.083817 | -0.20922 | -0.30463 | -0.18177 | -0.23313 | -0.20253 | 0.14896 | 0.12394 | 0.10387 | 0.20742 | -0.001773 | -0.10921 | -0.053217 | -0.11202 | -0.018674 | -0.038041 | -0.16344 | -0.25886 | -0.136 | -0.18736 | -0.15675 | 0.19473 | 0.16971 | 0.14964 | 0.2532 | -0.45359 | -0.4085 | -0.38209 | -0.337
1787.0781 | 121.6507 | -0.27008 | 121.4539 | -0.052128 | -0.15957 | -0.098993 | -0.16237 | -0.059872 | -0.088396 | -0.20922 | -0.30463 | -0.18635 | -0.23313 | -0.2071 | 0.1398 | 0.12851 | 0.099289 | 0.21658 | -0.006352 | -0.11379 | -0.053217 | -0.1166 | -0.014096 | -0.04262 | -0.16344 | -0.25886 | -0.14058 | -0.18736 | -0.16133 | 0.18557 | 0.17429 | 0.14506 | 0.26236 | -0.44443 | -0.40392 | -0.37293 | -0.33242
1788.8594 | 121.7239 | -0.21515 | 121.4447 | -0.056706 | -0.15957 | -0.10357 | -0.15779 | -0.06445 | -0.088396 | -0.20464 | -0.29548 | -0.19093 | -0.23313 | -0.19795 | 0.14438 | 0.12851 | 0.09471 | 0.212 | -0.01093 | -0.11379 | -0.057796 | -0.11202 | -0.018674 | -0.04262 | -0.15886 | -0.2497 | -0.14516 | -0.18736 | -0.15217 | 0.19015 | 0.17429 | 0.14049 | 0.25778 | -0.43985 | -0.39019 | -0.37751 | -0.32784
1790.625 | 121.788 | -0.20142 | 121.4401 | -0.042971 | -0.16415 | -0.098993 | -0.15321 | -0.06445 | -0.097553 | -0.20922 | -0.30006 | -0.18635 | -0.23313 | -0.2071 | 0.14896 | 0.12851 | 0.099289 | 0.212 | 0.002805 | -0.11837 | -0.053217 | -0.10744 | -0.018674 | -0.051777 | -0.16344 | -0.25428 | -0.14058 | -0.18736 | -0.16133 | 0.19473 | 0.17429 | 0.14506 | 0.25778 | -0.44901 | -0.39935 | -0.38209 | -0.33242
1792.3906 | 121.7606 | -0.21973 | 121.4401 | -0.061284 | -0.16873 | -0.098993 | -0.15779 | -0.069028 | -0.097553 | -0.2138 | -0.30463 | -0.18177 | -0.23771 | -0.21168 | 0.14896 | 0.11936 | 0.10387 | 0.212 | -0.015508 | -0.12295 | -0.053217 | -0.11202 | -0.023252 | -0.051777 | -0.16802 | -0.25886 | -0.136 | -0.19194 | -0.16591 | 0.19473 | 0.16514 | 0.14964 | 0.25778 | -0.45359 | -0.4085 | -0.38667 | -0.34158
1794.0938 | 121.6873 | -0.24261 | 121.4493 | -0.070441 | -0.17331 | -0.12646 | -0.17153 | -0.078184 | -0.10671 | -0.22295 | -0.32295 | -0.20467 | -0.25145 | -0.22084 | 0.16727 | 0.14683 | 0.11302 | 0.23489 | -0.024665 | -0.12753 | -0.080689 | -0.12575 | -0.032408 | -0.060933 | -0.17718 | -0.27717 | -0.15889 | -0.20567 | -0.17507 | 0.21304 | 0.1926 | 0.1588 | 0.28067 | -0.49022 | -0.43597 | -0.41871 | -0.36447
1795.875 | 121.7651 | -0.23346 | 121.4035 | -0.065863 | -0.16873 | -0.10815 | -0.17153 | -0.073606 | -0.11587 | -0.22753 | -0.32295 | -0.20009 | -0.23771 | -0.21168 | 0.15811 | 0.14225 | 0.12218 | 0.22116 | -0.020087 | -0.12295 | -0.062374 | -0.12575 | -0.02783 | -0.07009 | -0.18176 | -0.27717 | -0.15431 | -0.19194 | -0.16591 | 0.20389 | 0.18803 | 0.16796 | 0.26693 | -0.48106 | -0.44513 | -0.39582 | -0.35989
1797.6562 | 121.6919 | -0.24261 | 121.4401 | -0.070441 | -0.17788 | -0.11273 | -0.17153 | -0.078184 | -0.10213 | -0.22295 | -0.30921 | -0.20009 | -0.24687 | -0.21626 | 0.16269 | 0.12851 | 0.12218 | 0.22574 | -0.024665 | -0.13211 | -0.066953 | -0.12575 | -0.032408 | -0.056355 | -0.17718 | -0.26344 | -0.15431 | -0.20109 | -0.17049 | 0.20847 | 0.17429 | 0.16796 | 0.27151 | -0.4719 | -0.43139 | -0.40956 | -0.36905
1799.3594 | 121.6827 | -0.26093 | 121.4401 | -0.061284 | -0.16873 | -0.10357 | -0.17153 | -0.069028 | -0.10213 | -0.22295 | -0.30921 | -0.19551 | -0.23313 | -0.21626 | 0.15811 | 0.14225 | 0.10845 | 0.22574 | -0.015508 | -0.12295 | -0.057796 | -0.12575 | -0.023252 | -0.056355 | -0.17718 | -0.26344 | -0.14974 | -0.18736 | -0.17049 | 0.20389 | 0.18803 | 0.15422 | 0.27151 | -0.46732 | -0.41766 | -0.39125 | -0.34158
1801.125 | 121.7422 | -0.23804 | 121.4264 | -0.061284 | -0.16873 | -0.10815 | -0.16695 | -0.073606 | -0.10671 | -0.2138 | -0.30921 | -0.18635 | -0.24687 | -0.21168 | 0.15811 | 0.13309 | 0.11302 | 0.21658 | -0.015508 | -0.12295 | -0.062374 | -0.12117 | -0.02783 | -0.060933 | -0.16802 | -0.26344 | -0.14058 | -0.20109 | -0.16591 | 0.20389 | 0.17887 | 0.1588 | 0.26236 | -0.46732 | -0.42224 | -0.40498 | -0.35989
1802.8906 | 121.7926 | -0.21973 | 121.4081 | -0.061284 | -0.16415 | -0.11731 | -0.17153 | -0.073606 | -0.10671 | -0.2138 | -0.30921 | -0.19093 | -0.24229 | -0.21168 | 0.16269 | 0.13767 | 0.11302 | 0.22574 | -0.015508 | -0.11837 | -0.071531 | -0.12575 | -0.02783 | -0.060933 | -0.16802 | -0.26344 | -0.14516 | -0.19651 | -0.16591 | 0.20847 | 0.18345 | 0.1588 | 0.27151 | -0.4719 | -0.42224 | -0.40498 | -0.35531
1804.6562 | 121.7514 | -0.24261 | 121.4127 | -0.065863 | -0.16873 | -0.11273 | -0.16695 | -0.073606 | -0.10213 | -0.22295 | -0.31837 | -0.19093 | -0.23771 | -0.21168 | 0.15353 | 0.13309 | 0.10845 | 0.22116 | -0.020087 | -0.12295 | -0.066953 | -0.12117 | -0.02783 | -0.056355 | -0.17718 | -0.27259 | -0.14516 | -0.19194 | -0.16591 | 0.19931 | 0.17887 | 0.15422 | 0.26693 | -0.4719 | -0.42682 | -0.39125 | -0.34616
1806.3594 | 121.7972 | -0.2243 | 121.3852 | -0.061284 | -0.16873 | -0.10815 | -0.16695 | -0.078184 | -0.10213 | -0.21838 | -0.31379 | -0.19093 | -0.24687 | -0.21626 | 0.17185 | 0.13309 | 0.11302 | 0.22116 | -0.015508 | -0.12295 | -0.062374 | -0.12117 | -0.032408 | -0.056355 | -0.1726 | -0.26802 | -0.14516 | -0.20109 | -0.17049 | 0.21762 | 0.17887 | 0.1588 | 0.26693 | -0.48564 | -0.42682 | -0.41871 | -0.35989
1808.1094 | 121.7239 | -0.23346 | 121.4355 | -0.061284 | -0.16873 | -0.11273 | -0.17153 | -0.06445 | -0.10671 | -0.22295 | -0.31379 | -0.18635 | -0.23771 | -0.22084 | 0.16269 | 0.12851 | 0.1176 | 0.22116 | -0.015508 | -0.12295 | -0.066953 | -0.12575 | -0.018674 | -0.060933 | -0.17718 | -0.26802 | -0.14058 | -0.19194 | -0.17507 | 0.20847 | 0.17429 | 0.16338 | 0.26693 | -0.47648 | -0.43139 | -0.4004 | -0.35531
1809.8906 | 121.7239 | -0.25635 | 121.4539 | -0.061284 | -0.16873 | -0.11273 | -0.17153 | -0.069028 | -0.097553 | -0.2138 | -0.30921 | -0.19093 | -0.24229 | -0.21626 | 0.15811 | 0.13767 | 0.11302 | 0.22116 | -0.015508 | -0.12295 | -0.066953 | -0.12575 | -0.023252 | -0.051777 | -0.16802 | -0.26344 | -0.14516 | -0.19651 | -0.17049 | 0.20389 | 0.18345 | 0.1588 | 0.26693 | -0.46732 | -0.42224 | -0.4004 | -0.35531
1811.5938 | 121.7926 | -0.22888 | 121.4401 | -0.065863 | -0.16873 | -0.10815 | -0.16237 | -0.069028 | -0.10213 | -0.21838 | -0.30463 | -0.19093 | -0.23771 | -0.21626 | 0.16269 | 0.13309 | 0.1176 | 0.21658 | -0.020087 | -0.12295 | -0.062374 | -0.1166 | -0.023252 | -0.056355 | -0.1726 | -0.25886 | -0.14516 | -0.19194 | -0.17049 | 0.20847 | 0.17887 | 0.16338 | 0.26236 | -0.46732 | -0.42224 | -0.4004 | -0.35531
1813.3594 | 121.7834 | -0.21973 | 121.3989 | -0.061284 | -0.16415 | -0.11731 | -0.16695 | -0.078184 | -0.092974 | -0.21838 | -0.30921 | -0.19551 | -0.23771 | -0.21168 | 0.16269 | 0.13309 | 0.10845 | 0.22116 | -0.015508 | -0.11837 | -0.071531 | -0.12117 | -0.032408 | -0.047198 | -0.1726 | -0.26344 | -0.14974 | -0.19194 | -0.16591 | 0.20847 | 0.17887 | 0.15422 | 0.26693 | -0.4719 | -0.41766 | -0.4004 | -0.34616
1815.125 | 121.7651 | -0.23346 | 121.4172 | -0.070441 | -0.17331 | -0.10815 | -0.16695 | -0.073606 | -0.10213 | -0.21838 | -0.31837 | -0.18635 | -0.23313 | -0.21626 | 0.15811 | 0.13767 | 0.11302 | 0.23031 | -0.024665 | -0.12753 | -0.062374 | -0.12117 | -0.02783 | -0.056355 | -0.1726 | -0.27259 | -0.14058 | -0.18736 | -0.17049 | 0.20389 | 0.18345 | 0.1588 | 0.27609 | -0.47648 | -0.43139 | -0.39125 | -0.34616
1816.8906 | 121.7606 | -0.2243 | 121.4401 | -0.061284 | -0.17331 | -0.11273 | -0.17611 | -0.078184 | -0.11129 | -0.21838 | -0.30921 | -0.19551 | -0.23771 | -0.21626 | 0.16269 | 0.13767 | 0.10845 | 0.22116 | -0.015508 | -0.12753 | -0.066953 | -0.13033 | -0.032408 | -0.065512 | -0.1726 | -0.26344 | -0.14974 | -0.19194 | -0.17049 | 0.20847 | 0.18345 | 0.15422 | 0.26693 | -0.4719 | -0.41766 | -0.4004 | -0.34616
1818.5938 | 121.7834 | -0.22888 | 121.4218 | -0.061284 | -0.16873 | -0.10815 | -0.17153 | -0.069028 | -0.10213 | -0.22295 | -0.31379 | -0.19551 | -0.24229 | -0.22084 | 0.15811 | 0.13309 | 0.12218 | 0.22574 | -0.015508 | -0.12295 | -0.062374 | -0.12575 | -0.023252 | -0.056355 | -0.17718 | -0.26802 | -0.14974 | -0.19651 | -0.17507 | 0.20389 | 0.17887 | 0.16796 | 0.27151 | -0.4719 | -0.43597 | -0.4004 | -0.36447
1820.3594 | 121.7377 | -0.25177 | 121.431 | -0.061284 | -0.17788 | -0.11273 | -0.16695 | -0.078184 | -0.10671 | -0.22753 | -0.30921 | -0.19093 | -0.24229 | -0.22084 | 0.16269 | 0.13767 | 0.11302 | 0.21658 | -0.015508 | -0.13211 | -0.066953 | -0.12117 | -0.032408 | -0.060933 | -0.18176 | -0.26344 | -0.14516 | -0.19651 | -0.17507 | 0.20847 | 0.18345 | 0.1588 | 0.26236 | -0.4719 | -0.42224 | -0.40498 | -0.35531
1822.0625 | 121.7285 | -0.25635 | 121.4493 | -0.056706 | -0.16873 | -0.11273 | -0.17153 | -0.082762 | -0.097553 | -0.22295 | -0.31379 | -0.19551 | -0.24229 | -0.21626 | 0.15811 | 0.13309 | 0.11302 | 0.22116 | -0.01093 | -0.12295 | -0.066953 | -0.12575 | -0.036986 | -0.051777 | -0.17718 | -0.26802 | -0.14974 | -0.19651 | -0.17049 | 0.20389 | 0.17887 | 0.1588 | 0.26693 | -0.4719 | -0.42682 | -0.4004 | -0.35531
1823.8438 | 121.7972 | -0.23346 | 121.3989 | -0.065863 | -0.16873 | -0.10815 | -0.17153 | -0.069028 | -0.11129 | -0.22295 | -0.31379 | -0.19551 | -0.23771 | -0.21626 | 0.16727 | 0.14225 | 0.12218 | 0.22116 | -0.020087 | -0.12295 | -0.062374 | -0.12575 | -0.023252 | -0.065512 | -0.17718 | -0.26802 | -0.14974 | -0.19194 | -0.17049 | 0.21304 | 0.18803 | 0.16796 | 0.26693 | -0.48106 | -0.43597 | -0.40498 | -0.35989
1825.5469 | 121.7697 | -0.22888 | 121.4264 | -0.065863 | -0.16873 | -0.11273 | -0.16237 | -0.073606 | -0.10213 | -0.2138 | -0.31379 | -0.19551 | -0.24687 | -0.21626 | 0.15811 | 0.13767 | 0.11302 | 0.22116 | -0.020087 | -0.12295 | -0.066953 | -0.1166 | -0.02783 | -0.056355 | -0.16802 | -0.26802 | -0.14974 | -0.20109 | -0.17049 | 0.20389 | 0.18345 | 0.1588 | 0.26693 | -0.4719 | -0.42682 | -0.40498 | -0.35989
1827.3125 | 121.6919 | -0.26093 | 121.4401 | -0.070441 | -0.17331 | -0.11273 | -0.17153 | -0.078184 | -0.10671 | -0.22295 | -0.31837 | -0.19551 | -0.25145 | -0.22084 | 0.16727 | 0.13309 | 0.12218 | 0.22116 | -0.024665 | -0.12753 | -0.066953 | -0.12575 | -0.032408 | -0.060933 | -0.17718 | -0.27259 | -0.14974 | -0.20567 | -0.17507 | 0.21304 | 0.17887 | 0.16796 | 0.26693 | -0.48564 | -0.44055 | -0.41871 | -0.37363
1829.0938 | 121.7468 | -0.23346 | 121.4264 | -0.065863 | -0.17331 | -0.11731 | -0.16695 | -0.078184 | -0.10213 | -0.22295 | -0.31379 | -0.19093 | -0.24687 | -0.22084 | 0.16269 | 0.13767 | 0.1176 | 0.23031 | -0.020087 | -0.12753 | -0.071531 | -0.12117 | -0.032408 | -0.056355 | -0.17718 | -0.26802 | -0.14516 | -0.20109 | -0.17507 | 0.20847 | 0.18345 | 0.16338 | 0.27609 | -0.47648 | -0.43139 | -0.40956 | -0.36447
1830.8594 | 121.8063 | -0.23346 | 121.3898 | -0.070441 | -0.17331 | -0.11731 | -0.17611 | -0.082762 | -0.10671 | -0.22295 | -0.31837 | -0.20467 | -0.24229 | -0.22542 | 0.16727 | 0.13767 | 0.1176 | 0.22116 | -0.024665 | -0.12753 | -0.071531 | -0.13033 | -0.036986 | -0.060933 | -0.17718 | -0.27259 | -0.15889 | -0.19651 | -0.17964 | 0.21304 | 0.18345 | 0.16338 | 0.26693 | -0.48564 | -0.43597 | -0.40956 | -0.35989
1832.5625 | 121.6782 | -0.27924 | 121.4447 | -0.061284 | -0.17788 | -0.12189 | -0.17153 | -0.082762 | -0.10213 | -0.22753 | -0.30921 | -0.20467 | -0.24687 | -0.21626 | 0.16269 | 0.13309 | 0.12218 | 0.23489 | -0.015508 | -0.13211 | -0.07611 | -0.12575 | -0.036986 | -0.056355 | -0.18176 | -0.26344 | -0.15889 | -0.20109 | -0.17049 | 0.20847 | 0.17887 | 0.16796 | 0.28067 | -0.4719 | -0.43139 | -0.40956 | -0.36905
1834.3281 | 121.8018 | -0.23346 | 121.4081 | -0.07502 | -0.17788 | -0.11731 | -0.17611 | -0.082762 | -0.11129 | -0.22295 | -0.32295 | -0.19551 | -0.25145 | -0.22542 | 0.16727 | 0.13767 | 0.12676 | 0.22116 | -0.029244 | -0.13211 | -0.071531 | -0.13033 | -0.036986 | -0.065512 | -0.17718 | -0.27717 | -0.14974 | -0.20567 | -0.17964 | 0.21304 | 0.18345 | 0.17253 | 0.26693 | -0.49022 | -0.44971 | -0.41871 | -0.37821
1836.0938 | 121.7056 | -0.26093 | 121.4264 | -0.070441 | -0.17788 | -0.11731 | -0.17611 | -0.082762 | -0.10671 | -0.22753 | -0.31837 | -0.20009 | -0.25145 | -0.22542 | 0.17185 | 0.14225 | 0.12218 | 0.22574 | -0.024665 | -0.13211 | -0.071531 | -0.13033 | -0.036986 | -0.060933 | -0.18176 | -0.27259 | -0.15431 | -0.20567 | -0.17964 | 0.21762 | 0.18803 | 0.16796 | 0.27151 | -0.49022 | -0.44055 | -0.42329 | -0.37363
1837.8125 | 121.7056 | -0.27008 | 121.4264 | -0.070441 | -0.17788 | -0.11273 | -0.17611 | -0.082762 | -0.10671 | -0.22295 | -0.32295 | -0.20925 | -0.25145 | -0.22542 | 0.16269 | 0.14683 | 0.12676 | 0.23031 | -0.024665 | -0.13211 | -0.066953 | -0.13033 | -0.036986 | -0.060933 | -0.17718 | -0.27717 | -0.16347 | -0.20567 | -0.17964 | 0.20847 | 0.1926 | 0.17253 | 0.27609 | -0.48564 | -0.44971 | -0.41414 | -0.37821
1839.5312 | 121.788 | -0.23346 | 121.3943 | -0.070441 | -0.17788 | -0.12646 | -0.17611 | -0.082762 | -0.11129 | -0.22753 | -0.31837 | -0.20467 | -0.25603 | -0.22084 | 0.17185 | 0.14225 | 0.1176 | 0.23031 | -0.024665 | -0.13211 | -0.080689 | -0.13033 | -0.036986 | -0.065512 | -0.18176 | -0.27259 | -0.15889 | -0.21025 | -0.17507 | 0.21762 | 0.18803 | 0.16338 | 0.27609 | -0.49022 | -0.43597 | -0.42787 | -0.37363
1841.2969 | 121.701 | -0.30212 | 121.4081 | -0.07502 | -0.17331 | -0.11273 | -0.17153 | -0.08734 | -0.10671 | -0.22753 | -0.31379 | -0.20009 | -0.25145 | -0.22542 | 0.15811 | 0.14225 | 0.12218 | 0.23031 | -0.029244 | -0.12753 | -0.066953 | -0.12575 | -0.041564 | -0.060933 | -0.18176 | -0.26802 | -0.15431 | -0.20567 | -0.17964 | 0.20389 | 0.18803 | 0.16796 | 0.27609 | -0.4719 | -0.43597 | -0.40956 | -0.37363
1843.0625 | 121.7468 | -0.23804 | 121.3989 | -0.07502 | -0.17788 | -0.12189 | -0.17611 | -0.08734 | -0.11587 | -0.23211 | -0.31837 | -0.19551 | -0.24687 | -0.22542 | 0.16727 | 0.14225 | 0.12676 | 0.23489 | -0.029244 | -0.13211 | -0.07611 | -0.13033 | -0.041564 | -0.07009 | -0.18633 | -0.27259 | -0.14974 | -0.20109 | -0.17964 | 0.21304 | 0.18803 | 0.17253 | 0.28067 | -0.48564 | -0.44513 | -0.41414 | -0.37363
1844.8438 | 121.7834 | -0.25177 | 121.4218 | -0.07502 | -0.18246 | -0.12189 | -0.17611 | -0.08734 | -0.11587 | -0.23211 | -0.32295 | -0.20009 | -0.25603 | -0.22084 | 0.16727 | 0.14683 | 0.12676 | 0.23947 | -0.029244 | -0.13669 | -0.07611 | -0.13033 | -0.041564 | -0.07009 | -0.18633 | -0.27717 | -0.15431 | -0.21025 | -0.17507 | 0.21304 | 0.1926 | 0.17253 | 0.28525 | -0.49022 | -0.44971 | -0.42329 | -0.38278
1846.5469 | 121.7926 | -0.24719 | 121.4127 | -0.07502 | -0.17788 | -0.12189 | -0.18069 | -0.08734 | -0.10671 | -0.22753 | -0.32295 | -0.20467 | -0.24229 | -0.22542 | 0.181 | 0.14683 | 0.12676 | 0.23489 | -0.029244 | -0.13211 | -0.07611 | -0.13491 | -0.041564 | -0.060933 | -0.18176 | -0.27717 | -0.15889 | -0.19651 | -0.17964 | 0.22678 | 0.1926 | 0.17253 | 0.28067 | -0.50395 | -0.44971 | -0.42329 | -0.36905
1848.3125 | 121.6461 | -0.28381 | 121.4218 | -0.079598 | -0.17788 | -0.12189 | -0.17611 | -0.08734 | -0.11587 | -0.22753 | -0.31837 | -0.20009 | -0.25145 | -0.22084 | 0.17642 | 0.15141 | 0.1176 | 0.23489 | -0.033822 | -0.13211 | -0.07611 | -0.13033 | -0.041564 | -0.07009 | -0.18176 | -0.27259 | -0.15431 | -0.20567 | -0.17507 | 0.2222 | 0.19718 | 0.16338 | 0.28067 | -0.49479 | -0.43597 | -0.42787 | -0.36905
1850.0469 | 121.6415 | -0.29755 | 121.4264 | -0.070441 | -0.18246 | -0.13104 | -0.18069 | -0.08734 | -0.11587 | -0.23211 | -0.32295 | -0.20467 | -0.25603 | -0.22084 | 0.17642 | 0.14683 | 0.12676 | 0.23947 | -0.024665 | -0.13669 | -0.085267 | -0.13491 | -0.041564 | -0.07009 | -0.18633 | -0.27717 | -0.15889 | -0.21025 | -0.17507 | 0.2222 | 0.1926 | 0.17253 | 0.28525 | -0.49937 | -0.44971 | -0.43245 | -0.38278
1851.8281 | 121.7056 | -0.28381 | 121.4539 | -0.07502 | -0.19162 | -0.12646 | -0.18984 | -0.078184 | -0.11587 | -0.22753 | -0.32295 | -0.21383 | -0.25603 | -0.22542 | 0.17185 | 0.15141 | 0.12218 | 0.23947 | -0.029244 | -0.14585 | -0.080689 | -0.14407 | -0.032408 | -0.07009 | -0.18176 | -0.27717 | -0.16805 | -0.21025 | -0.17964 | 0.21762 | 0.19718 | 0.16796 | 0.28525 | -0.49479 | -0.44513 | -0.42787 | -0.37821
1853.5938 | 121.7697 | -0.24719 | 121.4172 | -0.079598 | -0.18704 | -0.12646 | -0.18526 | -0.08734 | -0.12044 | -0.23211 | -0.32753 | -0.20925 | -0.25145 | -0.23 | 0.17185 | 0.14683 | 0.12676 | 0.23489 | -0.033822 | -0.14127 | -0.080689 | -0.13949 | -0.041564 | -0.074669 | -0.18633 | -0.28175 | -0.16347 | -0.20567 | -0.18422 | 0.21762 | 0.1926 | 0.17253 | 0.28067 | -0.49937 | -0.45429 | -0.42329 | -0.37821
1855.375 | 121.701 | -0.28381 | 121.4035 | -0.084176 | -0.18704 | -0.12646 | -0.18526 | -0.091918 | -0.12044 | -0.23211 | -0.32295 | -0.20925 | -0.25603 | -0.22084 | 0.17642 | 0.15141 | 0.12676 | 0.23489 | -0.0384 | -0.14127 | -0.080689 | -0.13949 | -0.046142 | -0.074669 | -0.18633 | -0.27717 | -0.16347 | -0.21025 | -0.17507 | 0.2222 | 0.19718 | 0.17253 | 0.28067 | -0.49937 | -0.44971 | -0.43245 | -0.38278
1857.0938 | 121.6599 | -0.3067 | 121.431 | -0.07502 | -0.19162 | -0.13562 | -0.17611 | -0.08734 | -0.11587 | -0.23211 | -0.32295 | -0.20925 | -0.25603 | -0.23916 | 0.17642 | 0.14683 | 0.12676 | 0.23947 | -0.029244 | -0.14585 | -0.089846 | -0.13033 | -0.041564 | -0.07009 | -0.18633 | -0.27717 | -0.16347 | -0.21025 | -0.19338 | 0.2222 | 0.1926 | 0.17253 | 0.28525 | -0.49937 | -0.44971 | -0.43245 | -0.38278
1858.875 | 121.756 | -0.22888 | 121.3852 | -0.079598 | -0.18704 | -0.13104 | -0.18526 | -0.10107 | -0.11587 | -0.23669 | -0.32295 | -0.20467 | -0.2606 | -0.23 | 0.17642 | 0.16056 | 0.12676 | 0.23947 | -0.033822 | -0.14127 | -0.085267 | -0.13949 | -0.055298 | -0.07009 | -0.19091 | -0.27717 | -0.15889 | -0.21483 | -0.18422 | 0.2222 | 0.20634 | 0.17253 | 0.28525 | -0.49937 | -0.44971 | -0.43703 | -0.38736
1860.5781 | 121.7606 | -0.25635 | 121.4401 | -0.084176 | -0.18704 | -0.13562 | -0.18069 | -0.08734 | -0.12502 | -0.23669 | -0.32753 | -0.20925 | -0.2606 | -0.23 | 0.17642 | 0.14683 | 0.13134 | 0.24405 | -0.0384 | -0.14127 | -0.089846 | -0.13491 | -0.041564 | -0.079247 | -0.19091 | -0.28175 | -0.16347 | -0.21483 | -0.18422 | 0.2222 | 0.1926 | 0.17711 | 0.28983 | -0.50395 | -0.45886 | -0.43703 | -0.39194
1862.3438 | 121.6599 | -0.28839 | 121.4584 | -0.084176 | -0.19162 | -0.13104 | -0.18526 | -0.10107 | -0.12044 | -0.23211 | -0.32295 | -0.20925 | -0.2606 | -0.23458 | 0.17642 | 0.14683 | 0.12676 | 0.23947 | -0.0384 | -0.14585 | -0.085267 | -0.13949 | -0.055298 | -0.074669 | -0.18633 | -0.27717 | -0.16347 | -0.21483 | -0.1888 | 0.2222 | 0.1926 | 0.17253 | 0.28525 | -0.49937 | -0.44971 | -0.43703 | -0.38736
1864.125 | 121.7926 | -0.22888 | 121.4127 | -0.079598 | -0.18704 | -0.12646 | -0.18069 | -0.091918 | -0.12044 | -0.22753 | -0.32753 | -0.20467 | -0.2606 | -0.23458 | 0.17642 | 0.15598 | 0.12676 | 0.24863 | -0.033822 | -0.14127 | -0.080689 | -0.13491 | -0.046142 | -0.074669 | -0.18176 | -0.28175 | -0.15889 | -0.21483 | -0.1888 | 0.2222 | 0.20176 | 0.17253 | 0.2944 | -0.50395 | -0.45429 | -0.43703 | -0.38736
1865.8281 | 121.6736 | -0.3067 | 121.4035 | -0.084176 | -0.1962 | -0.13104 | -0.18526 | -0.096496 | -0.12502 | -0.23669 | -0.32753 | -0.20925 | -0.25603 | -0.24374 | 0.181 | 0.15141 | 0.13134 | 0.24863 | -0.0384 | -0.15042 | -0.085267 | -0.13949 | -0.05072 | -0.079247 | -0.19091 | -0.28175 | -0.16347 | -0.21025 | -0.19796 | 0.22678 | 0.19718 | 0.17711 | 0.2944 | -0.50853 | -0.45886 | -0.43703 | -0.38736
1867.5938 | 121.8018 | -0.25177 | 121.3715 | -0.084176 | -0.1962 | -0.1402 | -0.18526 | -0.096496 | -0.12502 | -0.23669 | -0.33211 | -0.21841 | -0.26518 | -0.24374 | 0.17642 | 0.16056 | 0.13592 | 0.24863 | -0.0384 | -0.15042 | -0.094424 | -0.13949 | -0.05072 | -0.079247 | -0.19091 | -0.28633 | -0.17263 | -0.21941 | -0.19796 | 0.2222 | 0.20634 | 0.18169 | 0.2944 | -0.50853 | -0.46802 | -0.44161 | -0.4011
1869.3594 | 121.7194 | -0.29755 | 121.4355 | -0.093333 | -0.19162 | -0.13104 | -0.19442 | -0.10107 | -0.12502 | -0.24127 | -0.32753 | -0.21841 | -0.26518 | -0.23916 | 0.18558 | 0.16056 | 0.13134 | 0.24863 | -0.047557 | -0.14585 | -0.085267 | -0.14865 | -0.055298 | -0.079247 | -0.19549 | -0.28175 | -0.17263 | -0.21941 | -0.19338 | 0.23136 | 0.20634 | 0.17711 | 0.2944 | -0.51311 | -0.45886 | -0.45076 | -0.39652
1871.1406 | 121.7056 | -0.28839 | 121.4355 | -0.097912 | -0.20078 | -0.1402 | -0.18984 | -0.096496 | -0.1296 | -0.24584 | -0.33211 | -0.21841 | -0.26976 | -0.23916 | 0.18558 | 0.15141 | 0.14507 | 0.24863 | -0.052136 | -0.155 | -0.094424 | -0.14407 | -0.05072 | -0.083825 | -0.20007 | -0.28633 | -0.17263 | -0.22398 | -0.19338 | 0.23136 | 0.19718 | 0.19085 | 0.2944 | -0.51769 | -0.47718 | -0.45534 | -0.41483
1872.9062 | 121.7468 | -0.2655 | 121.3943 | -0.097912 | -0.20994 | -0.1402 | -0.19442 | -0.10107 | -0.13418 | -0.24584 | -0.35042 | -0.22298 | -0.27434 | -0.24832 | 0.18558 | 0.16972 | 0.14049 | 0.25321 | -0.052136 | -0.16416 | -0.094424 | -0.14865 | -0.055298 | -0.088404 | -0.20007 | -0.30464 | -0.17721 | -0.22856 | -0.20254 | 0.23136 | 0.21549 | 0.18627 | 0.29898 | -0.536 | -0.49091 | -0.45992 | -0.41483
1874.625 | 121.8613 | -0.29755 | 121.4035 | -0.097912 | -0.20994 | -0.14936 | -0.199 | -0.10565 | -0.1296 | -0.255 | -0.34584 | -0.22298 | -0.26976 | -0.25289 | 0.19474 | 0.1743 | 0.14507 | 0.25778 | -0.052136 | -0.16416 | -0.10358 | -0.15322 | -0.059876 | -0.083825 | -0.20922 | -0.30007 | -0.17721 | -0.22398 | -0.20712 | 0.24051 | 0.22007 | 0.19085 | 0.30356 | -0.54058 | -0.49091 | -0.4645 | -0.41483
1876.3906 | 121.788 | -0.27466 | 121.3943 | -0.088755 | -0.20078 | -0.14478 | -0.199 | -0.11023 | -0.13418 | -0.24584 | -0.34584 | -0.23214 | -0.27434 | -0.24832 | 0.19931 | 0.16972 | 0.14049 | 0.25778 | -0.042979 | -0.155 | -0.099003 | -0.15322 | -0.064454 | -0.088404 | -0.20007 | -0.30007 | -0.18637 | -0.22856 | -0.20254 | 0.24509 | 0.21549 | 0.18627 | 0.30356 | -0.54516 | -0.48634 | -0.47365 | -0.41483
1878.1719 | 121.6782 | -0.28839 | 121.3852 | -0.10707 | -0.2191 | -0.16309 | -0.20816 | -0.11939 | -0.14334 | -0.255 | -0.35042 | -0.23214 | -0.27892 | -0.25747 | 0.20847 | 0.1743 | 0.15423 | 0.27152 | -0.061292 | -0.17332 | -0.11732 | -0.16238 | -0.07361 | -0.097561 | -0.20922 | -0.30464 | -0.18637 | -0.23314 | -0.2117 | 0.25425 | 0.22007 | 0.2 | 0.31729 | -0.55889 | -0.50465 | -0.48739 | -0.43315
1879.8906 | 121.6553 | -0.28381 | 121.4218 | -0.097912 | -0.20536 | -0.14478 | -0.199 | -0.11023 | -0.13418 | -0.25958 | -0.34584 | -0.23214 | -0.27434 | -0.24832 | 0.19474 | 0.16514 | 0.14965 | 0.26236 | -0.052136 | -0.15958 | -0.099003 | -0.15322 | -0.064454 | -0.088404 | -0.2138 | -0.30007 | -0.18637 | -0.22856 | -0.20254 | 0.24051 | 0.21092 | 0.19543 | 0.30814 | -0.54058 | -0.49549 | -0.46908 | -0.42399
1881.6719 | 121.7056 | -0.31128 | 121.4172 | -0.097912 | -0.21452 | -0.1402 | -0.20358 | -0.11023 | -0.14334 | -0.255 | -0.35042 | -0.22756 | -0.27892 | -0.24374 | 0.19931 | 0.16514 | 0.14965 | 0.25778 | -0.052136 | -0.16874 | -0.094424 | -0.1578 | -0.064454 | -0.097561 | -0.20922 | -0.30464 | -0.18179 | -0.23314 | -0.19796 | 0.24509 | 0.21092 | 0.19543 | 0.30356 | -0.54973 | -0.50007 | -0.47823 | -0.42857
1883.375 | 121.7148 | -0.27924 | 121.3806 | -0.10707 | -0.2191 | -0.14936 | -0.20816 | -0.11481 | -0.13876 | -0.255 | -0.35042 | -0.22298 | -0.27434 | -0.25289 | 0.19931 | 0.1743 | 0.15423 | 0.25778 | -0.061292 | -0.17332 | -0.10358 | -0.16238 | -0.069032 | -0.092982 | -0.20922 | -0.30464 | -0.17721 | -0.22856 | -0.20712 | 0.24509 | 0.22007 | 0.2 | 0.30356 | -0.54973 | -0.50465 | -0.47365 | -0.42857
1885.1719 | 121.7789 | -0.25635 | 121.3852 | -0.10249 | -0.20994 | -0.15394 | -0.20358 | -0.11939 | -0.13876 | -0.25042 | -0.34584 | -0.23672 | -0.27892 | -0.24832 | 0.19931 | 0.17887 | 0.14965 | 0.25321 | -0.056714 | -0.16416 | -0.10816 | -0.1578 | -0.07361 | -0.092982 | -0.20465 | -0.30007 | -0.19094 | -0.23314 | -0.20254 | 0.24509 | 0.22465 | 0.19543 | 0.29898 | -0.54516 | -0.49549 | -0.47823 | -0.42857
1886.9375 | 121.7926 | -0.25635 | 121.3577 | -0.10707 | -0.21452 | -0.15394 | -0.20816 | -0.11939 | -0.14791 | -0.25042 | -0.35042 | -0.23214 | -0.27434 | -0.25747 | 0.20389 | 0.17887 | 0.14965 | 0.26694 | -0.061292 | -0.16874 | -0.10816 | -0.16238 | -0.07361 | -0.10214 | -0.20465 | -0.30464 | -0.18637 | -0.22856 | -0.2117 | 0.24967 | 0.22465 | 0.19543 | 0.31272 | -0.55431 | -0.50007 | -0.47823 | -0.42399
1888.6406 | 121.7743 | -0.27466 | 121.3669 | -0.10707 | -0.2191 | -0.15394 | -0.21274 | -0.11481 | -0.14791 | -0.25042 | -0.35042 | -0.23214 | -0.27434 | -0.25747 | 0.19931 | 0.1743 | 0.15423 | 0.27152 | -0.061292 | -0.17332 | -0.10816 | -0.16696 | -0.069032 | -0.10214 | -0.20465 | -0.30464 | -0.18637 | -0.22856 | -0.2117 | 0.24509 | 0.22007 | 0.2 | 0.31729 | -0.54973 | -0.50465 | -0.47365 | -0.42857
1890.4062 | 121.6873 | -0.31586 | 121.376 | -0.11165 | -0.21452 | -0.15394 | -0.20816 | -0.11481 | -0.14334 | -0.25958 | -0.355 | -0.2413 | -0.28349 | -0.25747 | 0.20389 | 0.1743 | 0.15881 | 0.26694 | -0.065871 | -0.16874 | -0.10816 | -0.16238 | -0.069032 | -0.097561 | -0.2138 | -0.30922 | -0.19552 | -0.23772 | -0.2117 | 0.24967 | 0.22007 | 0.20458 | 0.31272 | -0.55889 | -0.51381 | -0.48739 | -0.4423
1892.1875 | 121.7331 | -0.29755 | 121.3669 | -0.11165 | -0.22367 | -0.15394 | -0.21274 | -0.11481 | -0.15249 | -0.255 | -0.35958 | -0.23672 | -0.29265 | -0.26205 | 0.19931 | 0.18345 | 0.15881 | 0.27152 | -0.065871 | -0.1779 | -0.10816 | -0.16696 | -0.069032 | -0.10672 | -0.20922 | -0.3138 | -0.19094 | -0.24688 | -0.21628 | 0.24509 | 0.22923 | 0.20458 | 0.31729 | -0.55889 | -0.51838 | -0.49197 | -0.45146
1893.9531 | 121.7926 | -0.28839 | 121.3577 | -0.11622 | -0.22367 | -0.16309 | -0.21731 | -0.12396 | -0.15249 | -0.25958 | -0.355 | -0.2413 | -0.29265 | -0.26205 | 0.20847 | 0.18345 | 0.16797 | 0.27152 | -0.070449 | -0.1779 | -0.11732 | -0.17154 | -0.078188 | -0.10672 | -0.2138 | -0.30922 | -0.19552 | -0.24688 | -0.21628 | 0.25425 | 0.22923 | 0.21374 | 0.31729 | -0.56347 | -0.52296 | -0.50112 | -0.46062
1895.6719 | 121.669 | -0.32959 | 121.4127 | -0.11622 | -0.22825 | -0.15851 | -0.21731 | -0.11481 | -0.15249 | -0.27331 | -0.35958 | -0.25046 | -0.28807 | -0.27121 | 0.21305 | 0.18345 | 0.17254 | 0.2761 | -0.070449 | -0.18248 | -0.11274 | -0.17154 | -0.069032 | -0.10672 | -0.22754 | -0.3138 | -0.20468 | -0.2423 | -0.22543 | 0.25883 | 0.22923 | 0.21832 | 0.32187 | -0.57263 | -0.53212 | -0.50112 | -0.46062
1897.4375 | 121.6782 | -0.33417 | 121.4035 | -0.1208 | -0.22825 | -0.16309 | -0.21731 | -0.11939 | -0.16623 | -0.26416 | -0.36416 | -0.25961 | -0.29265 | -0.26663 | 0.21305 | 0.18803 | 0.16339 | 0.28525 | -0.075028 | -0.18248 | -0.11732 | -0.17154 | -0.07361 | -0.12045 | -0.21838 | -0.31838 | -0.21384 | -0.24688 | -0.22086 | 0.25883 | 0.23381 | 0.20916 | 0.33103 | -0.5772 | -0.52754 | -0.5057 | -0.45604
1899.1406 | 121.7514 | -0.28381 | 121.3577 | -0.1208 | -0.22825 | -0.16767 | -0.21274 | -0.12396 | -0.15707 | -0.26874 | -0.36416 | -0.24588 | -0.28807 | -0.27121 | 0.21763 | 0.18345 | 0.16797 | 0.28068 | -0.075028 | -0.18248 | -0.1219 | -0.16696 | -0.078188 | -0.1113 | -0.22296 | -0.31838 | -0.2001 | -0.2423 | -0.22543 | 0.2634 | 0.22923 | 0.21374 | 0.32645 | -0.58178 | -0.53212 | -0.5057 | -0.45604
1900.9219 | 121.7651 | -0.29755 | 121.3852 | -0.12538 | -0.22825 | -0.16767 | -0.22189 | -0.12854 | -0.16165 | -0.26874 | -0.36873 | -0.25961 | -0.28349 | -0.26663 | 0.21763 | 0.19261 | 0.16797 | 0.28068 | -0.079606 | -0.18248 | -0.1219 | -0.17612 | -0.082766 | -0.11587 | -0.22296 | -0.32296 | -0.21384 | -0.23772 | -0.22086 | 0.2634 | 0.23838 | 0.21374 | 0.32645 | -0.58636 | -0.5367 | -0.50112 | -0.45146
1902.6875 | 121.756 | -0.27466 | 121.376 | -0.12996 | -0.23283 | -0.16309 | -0.22189 | -0.12854 | -0.15707 | -0.26874 | -0.36416 | -0.24588 | -0.29265 | -0.26663 | 0.22221 | 0.20176 | 0.17254 | 0.28068 | -0.084184 | -0.18706 | -0.11732 | -0.17612 | -0.082766 | -0.1113 | -0.22296 | -0.31838 | -0.2001 | -0.24688 | -0.22086 | 0.26798 | 0.24754 | 0.21832 | 0.32645 | -0.58636 | -0.5367 | -0.51486 | -0.46519
1904.4688 | 121.8063 | -0.29297 | 121.3531 | -0.12538 | -0.22825 | -0.16309 | -0.21731 | -0.1377 | -0.15707 | -0.26874 | -0.37331 | -0.25046 | -0.29723 | -0.27121 | 0.21763 | 0.19719 | 0.17712 | 0.28068 | -0.079606 | -0.18248 | -0.11732 | -0.17154 | -0.091922 | -0.1113 | -0.22296 | -0.32754 | -0.20468 | -0.25145 | -0.22543 | 0.2634 | 0.24296 | 0.2229 | 0.32645 | -0.59094 | -0.55043 | -0.51486 | -0.47435
1906.1875 | 121.669 | -0.32959 | 121.376 | -0.12996 | -0.22825 | -0.17683 | -0.22189 | -0.1377 | -0.15707 | -0.27789 | -0.37331 | -0.25961 | -0.30639 | -0.27121 | 0.22221 | 0.19719 | 0.17254 | 0.28525 | -0.084184 | -0.18248 | -0.13105 | -0.17612 | -0.091922 | -0.1113 | -0.23212 | -0.32754 | -0.21384 | -0.26061 | -0.22543 | 0.26798 | 0.24296 | 0.21832 | 0.33103 | -0.59552 | -0.54585 | -0.52859 | -0.47893
1907.9688 | 121.7972 | -0.28381 | 121.3623 | -0.12996 | -0.23741 | -0.15851 | -0.22189 | -0.1377 | -0.15707 | -0.27789 | -0.37331 | -0.25961 | -0.30181 | -0.28037 | 0.21763 | 0.20176 | 0.1817 | 0.29441 | -0.084184 | -0.19163 | -0.11274 | -0.17612 | -0.091922 | -0.1113 | -0.23212 | -0.32754 | -0.21384 | -0.25603 | -0.23459 | 0.2634 | 0.24754 | 0.22748 | 0.34019 | -0.59094 | -0.55501 | -0.51944 | -0.48351
1909.75 | 121.7468 | -0.30212 | 121.3715 | -0.12538 | -0.22825 | -0.17683 | -0.22647 | -0.12854 | -0.17539 | -0.27331 | -0.37789 | -0.25504 | -0.30181 | -0.27579 | 0.22221 | 0.19719 | 0.17712 | 0.28983 | -0.079606 | -0.18248 | -0.13105 | -0.18069 | -0.082766 | -0.12961 | -0.22754 | -0.33211 | -0.20926 | -0.25603 | -0.23001 | 0.26798 | 0.24296 | 0.2229 | 0.33561 | -0.6001 | -0.55501 | -0.52401 | -0.47893
1911.4531 | 121.8201 | -0.29755 | 121.3577 | -0.12996 | -0.24199 | -0.17683 | -0.23105 | -0.1377 | -0.16623 | -0.28247 | -0.38247 | -0.26419 | -0.31096 | -0.28037 | 0.22221 | 0.20176 | 0.17712 | 0.29899 | -0.084184 | -0.19621 | -0.13105 | -0.18527 | -0.091922 | -0.12045 | -0.23669 | -0.33669 | -0.21842 | -0.26519 | -0.23459 | 0.26798 | 0.24754 | 0.2229 | 0.34476 | -0.60467 | -0.55959 | -0.53317 | -0.48808
1913.2188 | 121.6919 | -0.32501 | 121.3623 | -0.12996 | -0.23741 | -0.18141 | -0.22189 | -0.1377 | -0.16623 | -0.28247 | -0.38247 | -0.25961 | -0.30181 | -0.28037 | 0.22221 | 0.20176 | 0.1817 | 0.28983 | -0.084184 | -0.19163 | -0.13563 | -0.17612 | -0.091922 | -0.12045 | -0.23669 | -0.33669 | -0.21384 | -0.25603 | -0.23459 | 0.26798 | 0.24754 | 0.22748 | 0.33561 | -0.60467 | -0.56417 | -0.52401 | -0.48351
1915 | 121.6415 | -0.34332 | 121.3623 | -0.13454 | -0.24199 | -0.17683 | -0.23563 | -0.14685 | -0.17081 | -0.28705 | -0.37789 | -0.26419 | -0.31096 | -0.28037 | 0.23594 | 0.20634 | 0.18628 | 0.29899 | -0.088763 | -0.19621 | -0.13105 | -0.18985 | -0.10108 | -0.12503 | -0.24127 | -0.33211 | -0.21842 | -0.26519 | -0.23459 | 0.28172 | 0.25212 | 0.23205 | 0.34476 | -0.61383 | -0.56417 | -0.5469 | -0.49724
1916.7031 | 121.788 | -0.30212 | 121.3394 | -0.13454 | -0.24657 | -0.17683 | -0.23105 | -0.15143 | -0.17081 | -0.28247 | -0.38247 | -0.25961 | -0.31096 | -0.28037 | 0.23594 | 0.21092 | 0.18628 | 0.29441 | -0.088763 | -0.20079 | -0.13105 | -0.18527 | -0.10566 | -0.12503 | -0.23669 | -0.33669 | -0.21384 | -0.26519 | -0.23459 | 0.28172 | 0.2567 | 0.23205 | 0.34019 | -0.61841 | -0.56875 | -0.5469 | -0.49724
1918.4531 | 121.8109 | -0.31586 | 121.3303 | -0.15285 | -0.25572 | -0.19514 | -0.24936 | -0.16059 | -0.18454 | -0.29163 | -0.39163 | -0.27335 | -0.32012 | -0.30326 | 0.24968 | 0.2155 | 0.20001 | 0.30814 | -0.10708 | -0.20995 | -0.14937 | -0.20359 | -0.11481 | -0.13877 | -0.24585 | -0.34585 | -0.22758 | -0.27435 | -0.25749 | 0.29545 | 0.26127 | 0.24579 | 0.35392 | -0.6413 | -0.59164 | -0.5698 | -0.52013
1920.25 | 121.7056 | -0.33875 | 121.3669 | -0.13912 | -0.25115 | -0.19057 | -0.24021 | -0.15143 | -0.17539 | -0.29163 | -0.39163 | -0.26877 | -0.31554 | -0.28953 | 0.24052 | 0.20634 | 0.19543 | 0.30814 | -0.093341 | -0.20537 | -0.14479 | -0.19443 | -0.10566 | -0.12961 | -0.24585 | -0.34585 | -0.223 | -0.26977 | -0.24375 | 0.2863 | 0.25212 | 0.24121 | 0.35392 | -0.63214 | -0.58706 | -0.55606 | -0.51098
1922.0312 | 121.7606 | -0.31586 | 121.3577 | -0.14827 | -0.25115 | -0.19514 | -0.24936 | -0.15143 | -0.17996 | -0.28705 | -0.38247 | -0.27335 | -0.31554 | -0.28953 | 0.23594 | 0.22008 | 0.19086 | 0.30357 | -0.1025 | -0.20537 | -0.14937 | -0.20359 | -0.10566 | -0.13419 | -0.24127 | -0.33669 | -0.22758 | -0.26977 | -0.24375 | 0.28172 | 0.26585 | 0.23663 | 0.34934 | -0.61841 | -0.57333 | -0.55148 | -0.5064
1923.8125 | 121.7377 | -0.31586 | 121.3623 | -0.13912 | -0.24657 | -0.19514 | -0.23563 | -0.14685 | -0.17996 | -0.29163 | -0.38705 | -0.26877 | -0.31554 | -0.29411 | 0.24052 | 0.2155 | 0.19086 | 0.29899 | -0.093341 | -0.20079 | -0.14937 | -0.18985 | -0.10108 | -0.13419 | -0.24585 | -0.34127 | -0.223 | -0.26977 | -0.24833 | 0.2863 | 0.26127 | 0.23663 | 0.34476 | -0.62757 | -0.57791 | -0.55606 | -0.5064
1925.5312 | 121.6507 | -0.35248 | 121.3989 | -0.14369 | -0.24199 | -0.17683 | -0.22647 | -0.14685 | -0.17081 | -0.27789 | -0.38247 | -0.25961 | -0.30639 | -0.28495 | 0.23136 | 0.21092 | 0.18628 | 0.29899 | -0.097919 | -0.19621 | -0.13105 | -0.18069 | -0.10108 | -0.12503 | -0.23212 | -0.33669 | -0.21384 | -0.26061 | -0.23917 | 0.27714 | 0.2567 | 0.23205 | 0.34476 | -0.61383 | -0.56875 | -0.53775 | -0.49266
1927.2812 | 121.7697 | -0.30212 | 121.3257 | -0.13454 | -0.23741 | -0.18141 | -0.22647 | -0.14685 | -0.17539 | -0.28247 | -0.37331 | -0.25961 | -0.30639 | -0.28495 | 0.23136 | 0.21092 | 0.1817 | 0.29441 | -0.088763 | -0.19163 | -0.13563 | -0.18069 | -0.10108 | -0.12961 | -0.23669 | -0.32754 | -0.21384 | -0.26061 | -0.23917 | 0.27714 | 0.2567 | 0.22748 | 0.34019 | -0.60467 | -0.55501 | -0.53775 | -0.48809
1929.0469 | 121.6736 | -0.3479 | 121.3852 | -0.12996 | -0.23741 | -0.18141 | -0.23563 | -0.1377 | -0.16623 | -0.28705 | -0.37331 | -0.26419 | -0.30639 | -0.28037 | 0.23594 | 0.19719 | 0.1817 | 0.30357 | -0.084184 | -0.19163 | -0.13563 | -0.18985 | -0.091922 | -0.12045 | -0.24127 | -0.32754 | -0.21842 | -0.26061 | -0.23459 | 0.28172 | 0.24296 | 0.22748 | 0.34934 | -0.60925 | -0.55501 | -0.54233 | -0.48809
1930.7656 | 121.6782 | -0.34332 | 121.3989 | -0.12538 | -0.24199 | -0.17683 | -0.22647 | -0.14228 | -0.17081 | -0.28247 | -0.38247 | -0.25504 | -0.31096 | -0.28037 | 0.23136 | 0.20176 | 0.1817 | 0.29899 | -0.079606 | -0.19621 | -0.13105 | -0.18069 | -0.0965 | -0.12503 | -0.23669 | -0.33669 | -0.20926 | -0.26519 | -0.23459 | 0.27714 | 0.24754 | 0.22748 | 0.34476 | -0.61383 | -0.56417 | -0.54233 | -0.49266
1932.5312 | 121.7789 | -0.29755 | 121.3577 | -0.12538 | -0.23741 | -0.18141 | -0.22647 | -0.14228 | -0.17081 | -0.28705 | -0.37789 | -0.25504 | -0.30639 | -0.28037 | 0.23136 | 0.21092 | 0.17712 | 0.29441 | -0.079606 | -0.19163 | -0.13563 | -0.18069 | -0.0965 | -0.12503 | -0.24127 | -0.33211 | -0.20926 | -0.26061 | -0.23459 | 0.27714 | 0.2567 | 0.2229 | 0.34019 | -0.60925 | -0.55501 | -0.53775 | -0.48351
1934.2969 | 121.7606 | -0.31586 | 121.3211 | -0.13454 | -0.23283 | -0.18141 | -0.22647 | -0.14228 | -0.17081 | -0.27789 | -0.37789 | -0.25961 | -0.30181 | -0.28037 | 0.22221 | 0.20634 | 0.18628 | 0.29441 | -0.088763 | -0.18706 | -0.13563 | -0.18069 | -0.0965 | -0.12503 | -0.23212 | -0.33211 | -0.21384 | -0.25603 | -0.23459 | 0.26798 | 0.25212 | 0.23205 | 0.34019 | -0.6001 | -0.56417 | -0.52401 | -0.48809
1936 | 121.7926 | -0.32959 | 121.3531 | -0.12996 | -0.23283 | -0.16767 | -0.22189 | -0.13312 | -0.16623 | -0.28247 | -0.37789 | -0.25961 | -0.30639 | -0.27121 | 0.23136 | 0.19719 | 0.18628 | 0.29441 | -0.084184 | -0.18706 | -0.1219 | -0.17612 | -0.087344 | -0.12045 | -0.23669 | -0.33211 | -0.21384 | -0.26061 | -0.22543 | 0.27714 | 0.24296 | 0.23205 | 0.34019 | -0.60925 | -0.56417 | -0.53775 | -0.49266
1937.7656 | 121.7697 | -0.29755 | 121.3577 | -0.13454 | -0.24199 | -0.18141 | -0.22647 | -0.1377 | -0.16623 | -0.27789 | -0.37331 | -0.26419 | -0.30639 | -0.28495 | 0.23136 | 0.20176 | 0.1817 | 0.29441 | -0.088763 | -0.19621 | -0.13563 | -0.18069 | -0.091922 | -0.12045 | -0.23212 | -0.32754 | -0.21842 | -0.26061 | -0.23917 | 0.27714 | 0.24754 | 0.22748 | 0.34019 | -0.60467 | -0.55501 | -0.53775 | -0.48809
1939.4688 | 121.6553 | -0.34332 | 121.3989 | -0.12996 | -0.24657 | -0.17225 | -0.22189 | -0.1377 | -0.16165 | -0.28705 | -0.37789 | -0.25961 | -0.30181 | -0.27579 | 0.22678 | 0.2155 | 0.1817 | 0.29441 | -0.084184 | -0.20079 | -0.12648 | -0.17612 | -0.091922 | -0.11587 | -0.24127 | -0.33211 | -0.21384 | -0.25603 | -0.23001 | 0.27256 | 0.26127 | 0.22748 | 0.34019 | -0.60467 | -0.55959 | -0.52859 | -0.48351
1941.25 | 121.6873 | -0.32959 | 121.3852 | -0.13454 | -0.24657 | -0.17683 | -0.22189 | -0.1377 | -0.17081 | -0.27331 | -0.37331 | -0.25961 | -0.30639 | -0.28495 | 0.22678 | 0.20176 | 0.18628 | 0.28983 | -0.088763 | -0.20079 | -0.13105 | -0.17612 | -0.091922 | -0.12503 | -0.22754 | -0.32754 | -0.21384 | -0.26061 | -0.23917 | 0.27256 | 0.24754 | 0.23205 | 0.33561 | -0.6001 | -0.55959 | -0.53317 | -0.49266
1942.9688 | 121.7102 | -0.33417 | 121.3577 | -0.12996 | -0.24657 | -0.17683 | -0.21731 | -0.14228 | -0.16623 | -0.27789 | -0.37789 | -0.26419 | -0.30639 | -0.27579 | 0.22678 | 0.20176 | 0.18628 | 0.29899 | -0.084184 | -0.20079 | -0.13105 | -0.17154 | -0.0965 | -0.12045 | -0.23212 | -0.33211 | -0.21842 | -0.26061 | -0.23001 | 0.27256 | 0.24754 | 0.23205 | 0.34476 | -0.60467 | -0.56417 | -0.53317 | -0.49266
1944.6719 | 121.7239 | -0.33417 | 121.3806 | -0.13454 | -0.24199 | -0.17683 | -0.22647 | -0.1377 | -0.16623 | -0.28247 | -0.37789 | -0.25961 | -0.30181 | -0.28495 | 0.22678 | 0.21092 | 0.19086 | 0.29441 | -0.088763 | -0.19621 | -0.13105 | -0.18069 | -0.091922 | -0.12045 | -0.23669 | -0.33211 | -0.21384 | -0.25603 | -0.23917 | 0.27256 | 0.2567 | 0.23663 | 0.34019 | -0.60467 | -0.56875 | -0.52859 | -0.49267
1946.4375 | 121.7697 | -0.29755 | 121.3303 | -0.12996 | -0.24657 | -0.17683 | -0.23105 | -0.14228 | -0.17539 | -0.28247 | -0.38705 | -0.25504 | -0.30639 | -0.28037 | 0.23594 | 0.21092 | 0.1817 | 0.29899 | -0.084184 | -0.20079 | -0.13105 | -0.18527 | -0.0965 | -0.12961 | -0.23669 | -0.34127 | -0.20926 | -0.26061 | -0.23459 | 0.28172 | 0.2567 | 0.22748 | 0.34476 | -0.62299 | -0.56875 | -0.54233 | -0.48809
1948.2188 | 121.7194 | -0.32044 | 121.3715 | -0.12996 | -0.24199 | -0.17683 | -0.22647 | -0.14228 | -0.17081 | -0.28247 | -0.38247 | -0.25961 | -0.31096 | -0.28495 | 0.23594 | 0.21092 | 0.18628 | 0.29441 | -0.084184 | -0.19621 | -0.13105 | -0.18069 | -0.0965 | -0.12503 | -0.23669 | -0.33669 | -0.21384 | -0.26519 | -0.23917 | 0.28172 | 0.2567 | 0.23205 | 0.34019 | -0.61841 | -0.56875 | -0.5469 | -0.49724
1949.9219 | 121.7148 | -0.33417 | 121.344 | -0.12538 | -0.24199 | -0.19057 | -0.24021 | -0.14685 | -0.17996 | -0.29163 | -0.38247 | -0.26419 | -0.30181 | -0.28495 | 0.23594 | 0.20634 | 0.19086 | 0.30357 | -0.079606 | -0.19621 | -0.14479 | -0.19443 | -0.10108 | -0.13419 | -0.24585 | -0.33669 | -0.21842 | -0.25603 | -0.23917 | 0.28172 | 0.25212 | 0.23663 | 0.34934 | -0.61841 | -0.57333 | -0.53775 | -0.49267
1951.6406 | 121.788 | -0.32501 | 121.3303 | -0.13454 | -0.25115 | -0.19514 | -0.23105 | -0.15601 | -0.17081 | -0.28705 | -0.37789 | -0.25504 | -0.30639 | -0.28495 | 0.23594 | 0.2155 | 0.19086 | 0.29899 | -0.088763 | -0.20537 | -0.14937 | -0.18527 | -0.11023 | -0.12503 | -0.24127 | -0.33211 | -0.20926 | -0.26061 | -0.23917 | 0.28172 | 0.26127 | 0.23663 | 0.34476 | -0.61383 | -0.56875 | -0.54233 | -0.49724
1953.4062 | 121.8018 | -0.32501 | 121.344 | -0.13912 | -0.24657 | -0.19057 | -0.23105 | -0.15143 | -0.17081 | -0.28247 | -0.38705 | -0.25961 | -0.32012 | -0.28495 | 0.23594 | 0.2155 | 0.19086 | 0.30814 | -0.093341 | -0.20079 | -0.14479 | -0.18527 | -0.10566 | -0.12503 | -0.23669 | -0.34127 | -0.21384 | -0.27435 | -0.23917 | 0.28172 | 0.26127 | 0.23663 | 0.35392 | -0.62299 | -0.57791 | -0.55606 | -0.51098
1955.1875 | 121.7743 | -0.30212 | 121.344 | -0.13912 | -0.25115 | -0.18599 | -0.23563 | -0.15601 | -0.17996 | -0.28705 | -0.38247 | -0.27335 | -0.31096 | -0.28953 | 0.24052 | 0.22008 | 0.19086 | 0.31272 | -0.093341 | -0.20537 | -0.14021 | -0.18985 | -0.11023 | -0.13419 | -0.24127 | -0.33669 | -0.22758 | -0.26519 | -0.24375 | 0.2863 | 0.26585 | 0.23663 | 0.3585 | -0.62299 | -0.57333 | -0.55148 | -0.50182
1956.9062 | 121.8018 | -0.31128 | 121.3348 | -0.14827 | -0.25572 | -0.19514 | -0.24021 | -0.15601 | -0.17996 | -0.28705 | -0.3962 | -0.26419 | -0.31554 | -0.29411 | 0.2451 | 0.2155 | 0.19086 | 0.30814 | -0.1025 | -0.20995 | -0.14937 | -0.19443 | -0.11023 | -0.13419 | -0.24127 | -0.35043 | -0.21842 | -0.26977 | -0.24833 | 0.29087 | 0.26127 | 0.23663 | 0.35392 | -0.6413 | -0.58706 | -0.56064 | -0.5064
1958.6875 | 121.6873 | -0.35248 | 121.3486 | -0.13912 | -0.25572 | -0.19057 | -0.23563 | -0.15143 | -0.17081 | -0.29163 | -0.3962 | -0.27335 | -0.31554 | -0.28953 | 0.24052 | 0.22923 | 0.19086 | 0.30814 | -0.093341 | -0.20995 | -0.14479 | -0.18985 | -0.10566 | -0.12503 | -0.24585 | -0.35043 | -0.22758 | -0.26977 | -0.24375 | 0.2863 | 0.27501 | 0.23663 | 0.35392 | -0.63672 | -0.58706 | -0.55606 | -0.5064
1960.4531 | 121.7377 | -0.33875 | 121.3211 | -0.14369 | -0.2603 | -0.19514 | -0.24021 | -0.16059 | -0.17539 | -0.30078 | -0.39163 | -0.26877 | -0.32012 | -0.29411 | 0.25425 | 0.22465 | 0.20001 | 0.3173 | -0.097919 | -0.21453 | -0.14937 | -0.19443 | -0.11481 | -0.12961 | -0.25501 | -0.34585 | -0.223 | -0.27435 | -0.24833 | 0.30003 | 0.27043 | 0.24579 | 0.36308 | -0.64588 | -0.59164 | -0.57437 | -0.52013
1962.25 | 121.6782 | -0.35706 | 121.3623 | -0.14369 | -0.26488 | -0.19057 | -0.24021 | -0.16059 | -0.17996 | -0.30078 | -0.40078 | -0.27335 | -0.32012 | -0.29411 | 0.2451 | 0.22008 | 0.20917 | 0.32188 | -0.097919 | -0.21911 | -0.14479 | -0.19443 | -0.11481 | -0.13419 | -0.25501 | -0.35501 | -0.22758 | -0.27435 | -0.24833 | 0.29087 | 0.26585 | 0.25495 | 0.36766 | -0.64588 | -0.60995 | -0.56522 | -0.52929
1964.0156 | 121.7468 | -0.33875 | 121.3303 | -0.14827 | -0.25572 | -0.2043 | -0.24479 | -0.15601 | -0.19828 | -0.30078 | -0.3962 | -0.28251 | -0.32012 | -0.29411 | 0.2451 | 0.22923 | 0.21375 | 0.32188 | -0.1025 | -0.20995 | -0.15853 | -0.19901 | -0.11023 | -0.1525 | -0.25501 | -0.35043 | -0.23673 | -0.27435 | -0.24833 | 0.29087 | 0.27501 | 0.25952 | 0.36766 | -0.6413 | -0.60995 | -0.56522 | -0.53387
1965.7188 | 121.6507 | -0.37079 | 121.3623 | -0.15285 | -0.26488 | -0.19972 | -0.25394 | -0.16974 | -0.1937 | -0.30994 | -0.40078 | -0.28251 | -0.33386 | -0.30784 | 0.25883 | 0.22008 | 0.20917 | 0.32646 | -0.10708 | -0.21911 | -0.15395 | -0.20817 | -0.12397 | -0.14792 | -0.26416 | -0.35501 | -0.23673 | -0.28808 | -0.26207 | 0.30461 | 0.26585 | 0.25495 | 0.37223 | -0.65962 | -0.60995 | -0.59269 | -0.54303
1967.4844 | 121.6919 | -0.38452 | 121.344 | -0.17117 | -0.27404 | -0.2043 | -0.25394 | -0.17432 | -0.20286 | -0.30994 | -0.40994 | -0.28709 | -0.33386 | -0.31242 | 0.25425 | 0.23381 | 0.21833 | 0.33104 | -0.12539 | -0.22826 | -0.15853 | -0.20817 | -0.12855 | -0.15708 | -0.26416 | -0.36416 | -0.24131 | -0.28808 | -0.26665 | 0.30003 | 0.27959 | 0.2641 | 0.37681 | -0.66419 | -0.62827 | -0.58811 | -0.55218
1969.2812 | 121.7606 | -0.33417 | 121.2936 | -0.15285 | -0.26946 | -0.2043 | -0.25852 | -0.16974 | -0.18454 | -0.30994 | -0.40078 | -0.28251 | -0.33843 | -0.30784 | 0.26341 | 0.23381 | 0.21833 | 0.32188 | -0.10708 | -0.22369 | -0.15853 | -0.21274 | -0.12397 | -0.13877 | -0.26416 | -0.35501 | -0.23673 | -0.29266 | -0.26207 | 0.30919 | 0.27959 | 0.2641 | 0.36766 | -0.66419 | -0.61911 | -0.60184 | -0.55676
1971.0625 | 121.701 | -0.35706 | 121.3715 | -0.16201 | -0.26946 | -0.21346 | -0.24936 | -0.16974 | -0.19828 | -0.31452 | -0.40994 | -0.28709 | -0.32928 | -0.30784 | 0.25883 | 0.24754 | 0.21375 | 0.32646 | -0.11623 | -0.22369 | -0.16768 | -0.20359 | -0.12397 | -0.1525 | -0.26874 | -0.36416 | -0.24131 | -0.2835 | -0.26207 | 0.30461 | 0.29332 | 0.25952 | 0.37223 | -0.66877 | -0.62369 | -0.58811 | -0.54302
1972.7812 | 121.6873 | -0.35248 | 121.344 | -0.15743 | -0.26488 | -0.20888 | -0.25394 | -0.16517 | -0.19828 | -0.30536 | -0.40536 | -0.27793 | -0.32928 | -0.30326 | 0.25883 | 0.22923 | 0.21375 | 0.32646 | -0.11165 | -0.21911 | -0.1631 | -0.20817 | -0.11939 | -0.1525 | -0.25958 | -0.35959 | -0.23216 | -0.2835 | -0.25749 | 0.30461 | 0.27501 | 0.25952 | 0.37223 | -0.66419 | -0.61911 | -0.58811 | -0.54302
1974.5469 | 121.6827 | -0.36163 | 121.3394 | -0.16201 | -0.26488 | -0.2043 | -0.24021 | -0.16517 | -0.18912 | -0.30536 | -0.40536 | -0.28251 | -0.32928 | -0.29868 | 0.25425 | 0.23381 | 0.21375 | 0.32188 | -0.11623 | -0.21911 | -0.15853 | -0.19443 | -0.11939 | -0.14334 | -0.25958 | -0.35959 | -0.23673 | -0.2835 | -0.25291 | 0.30003 | 0.27959 | 0.25952 | 0.36766 | -0.65962 | -0.61911 | -0.58353 | -0.54302
1976.3281 | 121.7285 | -0.33875 | 121.3211 | -0.16201 | -0.26946 | -0.2043 | -0.24936 | -0.16059 | -0.18912 | -0.2962 | -0.40536 | -0.27793 | -0.32928 | -0.29868 | 0.26341 | 0.22465 | 0.20459 | 0.33104 | -0.11623 | -0.22369 | -0.15853 | -0.20359 | -0.11481 | -0.14334 | -0.25043 | -0.35959 | -0.23216 | -0.2835 | -0.25291 | 0.30919 | 0.27043 | 0.25037 | 0.37681 | -0.66877 | -0.60995 | -0.59269 | -0.53387
1978.0938 | 121.6919 | -0.37994 | 121.3623 | -0.15743 | -0.26488 | -0.19972 | -0.24936 | -0.16059 | -0.1937 | -0.2962 | -0.40078 | -0.27793 | -0.32928 | -0.30326 | 0.25425 | 0.22465 | 0.20459 | 0.32646 | -0.11165 | -0.21911 | -0.15395 | -0.20359 | -0.11481 | -0.14792 | -0.25043 | -0.35501 | -0.23216 | -0.2835 | -0.25749 | 0.30003 | 0.27043 | 0.25037 | 0.37223 | -0.65504 | -0.60537 | -0.58353 | -0.53387
1979.8125 | 121.6919 | -0.36621 | 121.3486 | -0.15743 | -0.2603 | -0.19972 | -0.24021 | -0.16974 | -0.1937 | -0.30536 | -0.40536 | -0.28709 | -0.32928 | -0.30326 | 0.24968 | 0.23381 | 0.20917 | 0.32188 | -0.11165 | -0.21453 | -0.15395 | -0.19443 | -0.12397 | -0.14792 | -0.25958 | -0.35959 | -0.24131 | -0.2835 | -0.25749 | 0.29545 | 0.27959 | 0.25495 | 0.36766 | -0.65504 | -0.61453 | -0.57895 | -0.53845
1981.5312 | 121.7148 | -0.34332 | 121.3531 | -0.15743 | -0.2603 | -0.19972 | -0.24936 | -0.16517 | -0.1937 | -0.30078 | -0.40078 | -0.27793 | -0.3247 | -0.30326 | 0.25425 | 0.22465 | 0.20459 | 0.32188 | -0.11165 | -0.21453 | -0.15395 | -0.20359 | -0.11939 | -0.14792 | -0.25501 | -0.35501 | -0.23216 | -0.27892 | -0.25749 | 0.30003 | 0.27043 | 0.25037 | 0.36766 | -0.65504 | -0.60537 | -0.57895 | -0.52929
1983.2969 | 121.7194 | -0.35706 | 121.3394 | -0.14827 | -0.26488 | -0.19972 | -0.25394 | -0.16517 | -0.18912 | -0.30078 | -0.40536 | -0.27793 | -0.32012 | -0.30326 | 0.25425 | 0.22465 | 0.20917 | 0.32646 | -0.1025 | -0.21911 | -0.15395 | -0.20817 | -0.11939 | -0.14334 | -0.25501 | -0.35959 | -0.23216 | -0.27435 | -0.25749 | 0.30003 | 0.27043 | 0.25495 | 0.37223 | -0.65962 | -0.61453 | -0.57437 | -0.52929
1985.0625 | 121.8018 | -0.32044 | 121.2982 | -0.14827 | -0.26488 | -0.2043 | -0.25394 | -0.16517 | -0.18912 | -0.30536 | -0.3962 | -0.27335 | -0.32012 | -0.29868 | 0.24968 | 0.22465 | 0.21375 | 0.32188 | -0.1025 | -0.21911 | -0.15853 | -0.20817 | -0.11939 | -0.14334 | -0.25958 | -0.35043 | -0.22758 | -0.27435 | -0.25291 | 0.29545 | 0.27043 | 0.25952 | 0.36766 | -0.64588 | -0.60995 | -0.5698 | -0.53387
1986.8438 | 121.8109 | -0.32044 | 121.3074 | -0.14827 | -0.26946 | -0.20888 | -0.25394 | -0.16517 | -0.1937 | -0.30536 | -0.40536 | -0.27793 | -0.33386 | -0.30784 | 0.24968 | 0.22465 | 0.20917 | 0.3173 | -0.1025 | -0.22369 | -0.1631 | -0.20817 | -0.11939 | -0.14792 | -0.25958 | -0.35959 | -0.23216 | -0.28808 | -0.26207 | 0.29545 | 0.27043 | 0.25495 | 0.36308 | -0.65504 | -0.61453 | -0.58353 | -0.54303
1988.5312 | 121.6736 | -0.39368 | 121.312 | -0.14827 | -0.2603 | -0.20888 | -0.24936 | -0.17432 | -0.1937 | -0.30994 | -0.3962 | -0.28709 | -0.3247 | -0.30326 | 0.25425 | 0.22923 | 0.20917 | 0.33104 | -0.1025 | -0.21453 | -0.1631 | -0.20359 | -0.12855 | -0.14792 | -0.26416 | -0.35043 | -0.24131 | -0.27892 | -0.25749 | 0.30003 | 0.27501 | 0.25495 | 0.37681 | -0.65046 | -0.60537 | -0.57895 | -0.53387
1990.3125 | 121.6827 | -0.36163 | 121.344 | -0.14827 | -0.2603 | -0.19972 | -0.24936 | -0.16059 | -0.18912 | -0.30078 | -0.40078 | -0.27335 | -0.32012 | -0.30784 | 0.24968 | 0.22923 | 0.20459 | 0.32188 | -0.1025 | -0.21453 | -0.15395 | -0.20359 | -0.11481 | -0.14334 | -0.25501 | -0.35501 | -0.22758 | -0.27435 | -0.26207 | 0.29545 | 0.27501 | 0.25037 | 0.36766 | -0.65046 | -0.60537 | -0.5698 | -0.52471
1992.0312 | 121.7468 | -0.33875 | 121.3257 | -0.14827 | -0.26946 | -0.19972 | -0.24479 | -0.16974 | -0.18912 | -0.30536 | -0.40078 | -0.28251 | -0.3247 | -0.29868 | 0.24968 | 0.22008 | 0.21375 | 0.32188 | -0.1025 | -0.22369 | -0.15395 | -0.19901 | -0.12397 | -0.14334 | -0.25958 | -0.35501 | -0.23673 | -0.27892 | -0.25291 | 0.29545 | 0.26585 | 0.25952 | 0.36766 | -0.65046 | -0.61453 | -0.57437 | -0.53845
1993.8125 | 121.669 | -0.36621 | 121.3348 | -0.14369 | -0.26488 | -0.20888 | -0.24479 | -0.16517 | -0.1937 | -0.30078 | -0.40536 | -0.27793 | -0.3247 | -0.31242 | 0.25425 | 0.23381 | 0.21375 | 0.3173 | -0.097919 | -0.21911 | -0.1631 | -0.19901 | -0.11939 | -0.14792 | -0.25501 | -0.35959 | -0.23216 | -0.27892 | -0.26665 | 0.30003 | 0.27959 | 0.25952 | 0.36308 | -0.65962 | -0.61911 | -0.57895 | -0.53845
1995.5156 | 121.7194 | -0.3479 | 121.3074 | -0.15285 | -0.26488 | -0.2043 | -0.24479 | -0.16059 | -0.18912 | -0.30078 | -0.3962 | -0.27335 | -0.3247 | -0.29868 | 0.24968 | 0.22465 | 0.20459 | 0.32646 | -0.10708 | -0.21911 | -0.15853 | -0.19901 | -0.11481 | -0.14334 | -0.25501 | -0.35043 | -0.22758 | -0.27892 | -0.25291 | 0.29545 | 0.27043 | 0.25037 | 0.37223 | -0.64588 | -0.6008 | -0.57437 | -0.52929
1997.2812 | 121.7743 | -0.33417 | 121.3028 | -0.14827 | -0.26488 | -0.19972 | -0.24479 | -0.16517 | -0.18912 | -0.30536 | -0.3962 | -0.27335 | -0.32012 | -0.29868 | 0.24968 | 0.22465 | 0.21375 | 0.32188 | -0.1025 | -0.21911 | -0.15395 | -0.19901 | -0.11939 | -0.14334 | -0.25958 | -0.35043 | -0.22758 | -0.27435 | -0.25291 | 0.29545 | 0.27043 | 0.25952 | 0.36766 | -0.64588 | -0.60995 | -0.5698 | -0.53387
1999.0625 | 121.7468 | -0.33417 | 121.2936 | -0.15743 | -0.26488 | -0.19972 | -0.24021 | -0.16059 | -0.18454 | -0.30078 | -0.40078 | -0.27793 | -0.32012 | -0.29411 | 0.24968 | 0.22465 | 0.21375 | 0.32646 | -0.11165 | -0.21911 | -0.15395 | -0.19443 | -0.11481 | -0.13877 | -0.25501 | -0.35501 | -0.23216 | -0.27435 | -0.24833 | 0.29545 | 0.27043 | 0.25952 | 0.37223 | -0.65046 | -0.61453 | -0.5698 | -0.53387
2000.8438 | 121.756 | -0.33875 | 121.3531 | -0.14827 | -0.26488 | -0.19972 | -0.24479 | -0.15601 | -0.18912 | -0.2962 | -0.40536 | -0.27335 | -0.32928 | -0.30326 | 0.2451 | 0.22923 | 0.21833 | 0.33104 | -0.1025 | -0.21911 | -0.15395 | -0.19901 | -0.11023 | -0.14334 | -0.25043 | -0.35959 | -0.22758 | -0.2835 | -0.25749 | 0.29087 | 0.27501 | 0.2641 | 0.37681 | -0.65046 | -0.62369 | -0.57437 | -0.5476
2002.6094 | 121.7789 | -0.35248 | 121.3257 | -0.15285 | -0.2603 | -0.20888 | -0.24936 | -0.16059 | -0.18912 | -0.2962 | -0.40078 | -0.27793 | -0.3247 | -0.29868 | 0.25425 | 0.22008 | 0.20917 | 0.31272 | -0.10708 | -0.21453 | -0.1631 | -0.20359 | -0.11481 | -0.14334 | -0.25043 | -0.35501 | -0.23216 | -0.27892 | -0.25291 | 0.30003 | 0.26585 | 0.25495 | 0.3585 | -0.65504 | -0.60995 | -0.57895 | -0.53387
2004.375 | 121.6644 | -0.36621 | 121.3303 | -0.15285 | -0.25572 | -0.19972 | -0.24479 | -0.15601 | -0.18912 | -0.30078 | -0.39163 | -0.27793 | -0.32928 | -0.30784 | 0.2451 | 0.22008 | 0.20459 | 0.32188 | -0.10708 | -0.20995 | -0.15395 | -0.19901 | -0.11023 | -0.14334 | -0.25501 | -0.34585 | -0.23216 | -0.2835 | -0.26207 | 0.29087 | 0.26585 | 0.25037 | 0.36766 | -0.63672 | -0.59622 | -0.57437 | -0.53387
2006.1719 | 121.6644 | -0.37994 | 121.3394 | -0.15743 | -0.2603 | -0.19057 | -0.24479 | -0.16059 | -0.18912 | -0.29163 | -0.3962 | -0.27793 | -0.3247 | -0.29411 | 0.24968 | 0.22008 | 0.20459 | 0.3173 | -0.11165 | -0.21453 | -0.14479 | -0.19901 | -0.11481 | -0.14334 | -0.24585 | -0.35043 | -0.23216 | -0.27892 | -0.24833 | 0.29545 | 0.26585 | 0.25037 | 0.36308 | -0.64588 | -0.6008 | -0.57437 | -0.52929
2007.8906 | 121.7789 | -0.33875 | 121.3211 | -0.14369 | -0.25572 | -0.19972 | -0.24479 | -0.15601 | -0.18912 | -0.2962 | -0.39163 | -0.27793 | -0.32012 | -0.30326 | 0.2451 | 0.22465 | 0.20917 | 0.33104 | -0.097919 | -0.20995 | -0.15395 | -0.19901 | -0.11023 | -0.14334 | -0.25043 | -0.34585 | -0.23216 | -0.27435 | -0.25749 | 0.29087 | 0.27043 | 0.25495 | 0.37681 | -0.63672 | -0.6008 | -0.56522 | -0.52929
2009.6562 | 121.7651 | -0.34332 | 121.312 | -0.15285 | -0.26488 | -0.19514 | -0.24479 | -0.16059 | -0.18912 | -0.2962 | -0.3962 | -0.28251 | -0.3247 | -0.30326 | 0.24968 | 0.22465 | 0.21375 | 0.32646 | -0.10708 | -0.21911 | -0.14937 | -0.19901 | -0.11481 | -0.14334 | -0.25043 | -0.35043 | -0.23673 | -0.27892 | -0.25749 | 0.29545 | 0.27043 | 0.25952 | 0.37223 | -0.64588 | -0.60995 | -0.57437 | -0.53845
2011.4219 | 121.6644 | -0.38452 | 121.3257 | -0.15743 | -0.26488 | -0.2043 | -0.25394 | -0.16974 | -0.1937 | -0.30078 | -0.40078 | -0.28251 | -0.33386 | -0.30784 | 0.25425 | 0.22923 | 0.2229 | 0.33561 | -0.11165 | -0.21911 | -0.15853 | -0.20817 | -0.12397 | -0.14792 | -0.25501 | -0.35501 | -0.23673 | -0.28808 | -0.26207 | 0.30003 | 0.27501 | 0.26868 | 0.38139 | -0.65504 | -0.62369 | -0.58811 | -0.55676
2013.2188 | 121.7422 | -0.35248 | 121.2891 | -0.15285 | -0.2603 | -0.19972 | -0.24479 | -0.16517 | -0.18454 | -0.30536 | -0.3962 | -0.27335 | -0.3247 | -0.29868 | 0.25883 | 0.22923 | 0.21833 | 0.33561 | -0.10708 | -0.21453 | -0.15395 | -0.19901 | -0.11939 | -0.13877 | -0.25958 | -0.35043 | -0.22758 | -0.27892 | -0.25291 | 0.30461 | 0.27501 | 0.2641 | 0.38139 | -0.65504 | -0.61453 | -0.58353 | -0.54303
2014.9219 | 121.7331 | -0.32959 | 121.3165 | -0.14827 | -0.26488 | -0.20888 | -0.24936 | -0.16974 | -0.18454 | -0.30078 | -0.40078 | -0.27335 | -0.32928 | -0.30326 | 0.24968 | 0.22923 | 0.21375 | 0.33104 | -0.1025 | -0.21911 | -0.1631 | -0.20359 | -0.12397 | -0.13877 | -0.25501 | -0.35501 | -0.22758 | -0.2835 | -0.25749 | 0.29545 | 0.27501 | 0.25952 | 0.37681 | -0.65046 | -0.61453 | -0.57895 | -0.54302
2016.6875 | 121.788 | -0.32501 | 121.2891 | -0.15743 | -0.26488 | -0.19972 | -0.24936 | -0.16974 | -0.18454 | -0.30078 | -0.40994 | -0.28251 | -0.32928 | -0.29868 | 0.25883 | 0.22465 | 0.2229 | 0.32646 | -0.11165 | -0.21911 | -0.15395 | -0.20359 | -0.12397 | -0.13877 | -0.25501 | -0.36416 | -0.23673 | -0.2835 | -0.25291 | 0.30461 | 0.27043 | 0.26868 | 0.37223 | -0.66877 | -0.63284 | -0.58811 | -0.55218
2018.4531 | 121.6553 | -0.37537 | 121.3074 | -0.14827 | -0.25572 | -0.19514 | -0.24479 | -0.16059 | -0.18454 | -0.2962 | -0.40078 | -0.27335 | -0.32012 | -0.29868 | 0.24968 | 0.22465 | 0.20001 | 0.32188 | -0.1025 | -0.20995 | -0.14937 | -0.19901 | -0.11481 | -0.13877 | -0.25043 | -0.35501 | -0.22758 | -0.27435 | -0.25291 | 0.29545 | 0.27043 | 0.24579 | 0.36766 | -0.65046 | -0.6008 | -0.5698 | -0.52013
2020.2344 | 121.6324 | -0.37994 | 121.3074 | -0.15285 | -0.25115 | -0.19514 | -0.24936 | -0.15601 | -0.18454 | -0.30078 | -0.3962 | -0.28251 | -0.32012 | -0.29868 | 0.24968 | 0.22008 | 0.20917 | 0.33104 | -0.10708 | -0.20537 | -0.14937 | -0.20359 | -0.11023 | -0.13877 | -0.25501 | -0.35043 | -0.23673 | -0.27435 | -0.25291 | 0.29545 | 0.26585 | 0.25495 | 0.37681 | -0.64588 | -0.60537 | -0.5698 | -0.52929
2021.9375 | 121.7194 | -0.33875 | 121.3303 | -0.15285 | -0.25572 | -0.19514 | -0.24479 | -0.15601 | -0.18454 | -0.2962 | -0.39163 | -0.26877 | -0.32012 | -0.29411 | 0.24968 | 0.2155 | 0.20917 | 0.33104 | -0.10708 | -0.20995 | -0.14937 | -0.19901 | -0.11023 | -0.13877 | -0.25043 | -0.34585 | -0.223 | -0.27435 | -0.24833 | 0.29545 | 0.26127 | 0.25495 | 0.37681 | -0.6413 | -0.6008 | -0.5698 | -0.52929
2023.7188 | 121.7743 | -0.32501 | 121.3303 | -0.14369 | -0.2603 | -0.19972 | -0.23563 | -0.16517 | -0.18912 | -0.2962 | -0.39163 | -0.27793 | -0.31554 | -0.28953 | 0.2451 | 0.22008 | 0.21375 | 0.32646 | -0.097919 | -0.21453 | -0.15395 | -0.18985 | -0.11939 | -0.14334 | -0.25043 | -0.34585 | -0.23216 | -0.26977 | -0.24375 | 0.29087 | 0.26585 | 0.25952 | 0.37223 | -0.63672 | -0.60537 | -0.56064 | -0.52929
2025.4844 | 121.788 | -0.32501 | 121.2845 | -0.14369 | -0.25572 | -0.19514 | -0.24021 | -0.15601 | -0.17996 | -0.2962 | -0.39163 | -0.27793 | -0.32012 | -0.29411 | 0.2451 | 0.22008 | 0.21375 | 0.32646 | -0.097919 | -0.20995 | -0.14937 | -0.19443 | -0.11023 | -0.13419 | -0.25043 | -0.34585 | -0.23216 | -0.27435 | -0.24833 | 0.29087 | 0.26585 | 0.25952 | 0.37223 | -0.63672 | -0.60537 | -0.56522 | -0.53387
2027.2812 | 121.7331 | -0.34332 | 121.3074 | -0.15285 | -0.26488 | -0.19514 | -0.23563 | -0.15143 | -0.1937 | -0.30078 | -0.3962 | -0.26877 | -0.32012 | -0.28953 | 0.2451 | 0.22465 | 0.21833 | 0.33104 | -0.10708 | -0.21911 | -0.14937 | -0.18985 | -0.10566 | -0.14792 | -0.25501 | -0.35043 | -0.223 | -0.27435 | -0.24375 | 0.29087 | 0.27043 | 0.2641 | 0.37681 | -0.6413 | -0.61453 | -0.56522 | -0.53845
2028.9844 | 121.7789 | -0.3479 | 121.2799 | -0.14827 | -0.26488 | -0.19972 | -0.25394 | -0.16517 | -0.18912 | -0.30536 | -0.40078 | -0.27793 | -0.3247 | -0.29868 | 0.24968 | 0.22923 | 0.21833 | 0.33561 | -0.1025 | -0.21911 | -0.15395 | -0.20817 | -0.11939 | -0.14334 | -0.25958 | -0.35501 | -0.23216 | -0.27892 | -0.25291 | 0.29545 | 0.27501 | 0.2641 | 0.38139 | -0.65046 | -0.61911 | -0.57437 | -0.54303
2030.7656 | 121.6415 | -0.40283 | 121.3257 | -0.15743 | -0.2603 | -0.21346 | -0.25394 | -0.16517 | -0.18454 | -0.30536 | -0.40994 | -0.28251 | -0.32928 | -0.30784 | 0.2451 | 0.22923 | 0.2229 | 0.34477 | -0.11165 | -0.21453 | -0.16768 | -0.20817 | -0.11939 | -0.13877 | -0.25958 | -0.36416 | -0.23673 | -0.2835 | -0.26207 | 0.29087 | 0.27501 | 0.26868 | 0.39054 | -0.65504 | -0.63284 | -0.57437 | -0.55218
2032.4844 | 121.7651 | -0.33875 | 121.2753 | -0.16659 | -0.26946 | -0.20888 | -0.25394 | -0.17432 | -0.19828 | -0.31452 | -0.40994 | -0.29167 | -0.33843 | -0.30784 | 0.26341 | 0.22923 | 0.21833 | 0.34477 | -0.12081 | -0.22369 | -0.1631 | -0.20817 | -0.12855 | -0.1525 | -0.26874 | -0.36416 | -0.24589 | -0.29266 | -0.26207 | 0.30919 | 0.27501 | 0.2641 | 0.39054 | -0.67335 | -0.62827 | -0.60184 | -0.55676
2034.2656 | 121.6965 | -0.39825 | 121.3165 | -0.17117 | -0.2832 | -0.21804 | -0.2631 | -0.1789 | -0.20286 | -0.31452 | -0.42368 | -0.29625 | -0.34301 | -0.32158 | 0.26799 | 0.24297 | 0.23206 | 0.3585 | -0.12539 | -0.23742 | -0.17226 | -0.21732 | -0.13312 | -0.15708 | -0.26874 | -0.3779 | -0.25047 | -0.29724 | -0.2758 | 0.31376 | 0.28874 | 0.27784 | 0.40428 | -0.69166 | -0.65574 | -0.611 | -0.57507
2036.0469 | 121.6324 | -0.43488 | 121.312 | -0.1849 | -0.28778 | -0.22719 | -0.27683 | -0.18805 | -0.21659 | -0.32825 | -0.42825 | -0.3054 | -0.34759 | -0.32158 | 0.2863 | 0.25212 | 0.23664 | 0.3585 | -0.13912 | -0.242 | -0.18142 | -0.23106 | -0.14228 | -0.17081 | -0.28248 | -0.38248 | -0.25963 | -0.30181 | -0.2758 | 0.33208 | 0.2979 | 0.28242 | 0.40428 | -0.71456 | -0.66489 | -0.63389 | -0.58423
2037.8281 | 121.7148 | -0.41199 | 121.2433 | -0.19864 | -0.30609 | -0.24551 | -0.28599 | -0.20637 | -0.23033 | -0.34199 | -0.44657 | -0.31456 | -0.37506 | -0.34447 | 0.29546 | 0.27044 | 0.25495 | 0.38139 | -0.15286 | -0.26032 | -0.19973 | -0.24022 | -0.16059 | -0.18455 | -0.29621 | -0.40079 | -0.26878 | -0.32928 | -0.2987 | 0.34123 | 0.31621 | 0.30073 | 0.42717 | -0.74203 | -0.70152 | -0.67052 | -0.63001
2039.5312 | 121.7285 | -0.3891 | 121.2753 | -0.17574 | -0.28778 | -0.21804 | -0.25852 | -0.1789 | -0.21201 | -0.3191 | -0.4191 | -0.29625 | -0.33386 | -0.317 | 0.27257 | 0.23839 | 0.23664 | 0.35393 | -0.12997 | -0.242 | -0.17226 | -0.21274 | -0.13312 | -0.16624 | -0.27332 | -0.37332 | -0.25047 | -0.28808 | -0.27122 | 0.31834 | 0.28417 | 0.28242 | 0.3997 | -0.69166 | -0.65574 | -0.60642 | -0.5705
2041.2969 | 121.7331 | -0.31128 | 121.3028 | -0.13454 | -0.25115 | -0.18141 | -0.23563 | -0.14685 | -0.17996 | -0.28247 | -0.38247 | -0.26419 | -0.30181 | -0.28953 | 0.23136 | 0.20176 | 0.20459 | 0.3173 | -0.088763 | -0.20537 | -0.13563 | -0.18985 | -0.10108 | -0.13419 | -0.23669 | -0.33669 | -0.21842 | -0.25603 | -0.24375 | 0.27714 | 0.24754 | 0.25037 | 0.36308 | -0.61383 | -0.58706 | -0.53317 | -0.5064
2043.0938 | 121.6507 | -0.37537 | 121.3577 | -0.14827 | -0.24657 | -0.18599 | -0.23105 | -0.14685 | -0.17996 | -0.28705 | -0.38247 | -0.26877 | -0.31554 | -0.28495 | 0.24052 | 0.21092 | 0.21375 | 0.32188 | -0.1025 | -0.20079 | -0.14021 | -0.18527 | -0.10108 | -0.13419 | -0.24127 | -0.33669 | -0.223 | -0.26977 | -0.23917 | 0.2863 | 0.2567 | 0.25952 | 0.36766 | -0.62299 | -0.59622 | -0.55606 | -0.52929
2044.8594 | 121.6553 | -0.37537 | 121.3348 | -0.14369 | -0.25115 | -0.18599 | -0.23563 | -0.15143 | -0.17539 | -0.28705 | -0.39163 | -0.26419 | -0.31096 | -0.28953 | 0.23594 | 0.22465 | 0.21375 | 0.33104 | -0.097919 | -0.20537 | -0.14021 | -0.18985 | -0.10566 | -0.12961 | -0.24127 | -0.34585 | -0.21842 | -0.26519 | -0.24375 | 0.28172 | 0.27043 | 0.25952 | 0.37681 | -0.62757 | -0.60537 | -0.5469 | -0.52471
2046.625 | 121.756 | -0.32501 | 121.3074 | -0.13912 | -0.2603 | -0.2043 | -0.23563 | -0.15601 | -0.18912 | -0.29163 | -0.38705 | -0.27335 | -0.31554 | -0.28953 | 0.2451 | 0.22008 | 0.21375 | 0.32646 | -0.093341 | -0.21453 | -0.15853 | -0.18985 | -0.11023 | -0.14334 | -0.24585 | -0.34127 | -0.22758 | -0.26977 | -0.24375 | 0.29087 | 0.26585 | 0.25952 | 0.37223 | -0.63214 | -0.6008 | -0.56064 | -0.52929
2048.3438 | 121.6507 | -0.38452 | 121.3074 | -0.13912 | -0.25572 | -0.19972 | -0.24479 | -0.15601 | -0.18912 | -0.29163 | -0.39163 | -0.28251 | -0.31554 | -0.29411 | 0.2451 | 0.2155 | 0.21375 | 0.34019 | -0.093341 | -0.20995 | -0.15395 | -0.19901 | -0.11023 | -0.14334 | -0.24585 | -0.34585 | -0.23673 | -0.26977 | -0.24833 | 0.29087 | 0.26127 | 0.25952 | 0.38597 | -0.63672 | -0.60537 | -0.56064 | -0.52929
2050.125 | 121.669 | -0.37994 | 121.312 | -0.15285 | -0.25572 | -0.19057 | -0.24021 | -0.15601 | -0.18912 | -0.30078 | -0.3962 | -0.27793 | -0.32012 | -0.29411 | 0.24052 | 0.22008 | 0.2229 | 0.34019 | -0.10708 | -0.20995 | -0.14479 | -0.19443 | -0.11023 | -0.14334 | -0.25501 | -0.35043 | -0.23216 | -0.27435 | -0.24833 | 0.2863 | 0.26585 | 0.26868 | 0.38597 | -0.63672 | -0.61911 | -0.56064 | -0.54303
2051.9062 | 121.7468 | -0.37079 | 121.2982 | -0.16201 | -0.26488 | -0.2043 | -0.24936 | -0.16974 | -0.18912 | -0.30994 | -0.41452 | -0.29625 | -0.33386 | -0.30784 | 0.25425 | 0.23839 | 0.22748 | 0.34935 | -0.11623 | -0.21911 | -0.15853 | -0.20359 | -0.12397 | -0.14334 | -0.26416 | -0.36874 | -0.25047 | -0.28808 | -0.26207 | 0.30003 | 0.28417 | 0.27326 | 0.39512 | -0.66877 | -0.642 | -0.58811 | -0.56134
2053.6875 | 121.701 | -0.40283 | 121.2479 | -0.16659 | -0.27862 | -0.20888 | -0.25852 | -0.17432 | -0.19828 | -0.3191 | -0.41452 | -0.29625 | -0.33386 | -0.30784 | 0.26341 | 0.23381 | 0.23664 | 0.36308 | -0.12081 | -0.23284 | -0.1631 | -0.21274 | -0.12855 | -0.1525 | -0.27332 | -0.36874 | -0.25047 | -0.28808 | -0.26207 | 0.30919 | 0.27959 | 0.28242 | 0.40886 | -0.67793 | -0.65116 | -0.59727 | -0.5705
2055.4531 | 121.756 | -0.37537 | 121.2753 | -0.17574 | -0.27862 | -0.21804 | -0.2631 | -0.18348 | -0.20286 | -0.31452 | -0.4191 | -0.29625 | -0.32928 | -0.32616 | 0.26799 | 0.24297 | 0.2458 | 0.36308 | -0.12997 | -0.23284 | -0.17226 | -0.21732 | -0.1377 | -0.15708 | -0.26874 | -0.37332 | -0.25047 | -0.2835 | -0.28038 | 0.31376 | 0.28874 | 0.29157 | 0.40886 | -0.68708 | -0.66489 | -0.59726 | -0.57507
2057.1719 | 121.7651 | -0.37994 | 121.2204 | -0.18032 | -0.28778 | -0.23177 | -0.2631 | -0.19263 | -0.20743 | -0.32367 | -0.42368 | -0.30998 | -0.35217 | -0.33074 | 0.28172 | 0.2567 | 0.25038 | 0.37682 | -0.13455 | -0.242 | -0.186 | -0.21732 | -0.14686 | -0.16166 | -0.2779 | -0.3779 | -0.26421 | -0.30639 | -0.28496 | 0.3275 | 0.30248 | 0.29615 | 0.42259 | -0.7054 | -0.67405 | -0.63389 | -0.60254
2058.9375 | 121.6278 | -0.44861 | 121.2845 | -0.19406 | -0.30609 | -0.23635 | -0.28141 | -0.20179 | -0.23033 | -0.34656 | -0.44199 | -0.33288 | -0.36133 | -0.33532 | 0.29546 | 0.26586 | 0.27327 | 0.39055 | -0.14828 | -0.26032 | -0.19057 | -0.23564 | -0.15601 | -0.18455 | -0.30079 | -0.39621 | -0.2871 | -0.31555 | -0.28954 | 0.34123 | 0.31163 | 0.31904 | 0.43633 | -0.73745 | -0.71526 | -0.65678 | -0.63459
2060.6406 | 121.6736 | -0.4715 | 121.2479 | -0.21237 | -0.32441 | -0.25924 | -0.29973 | -0.23841 | -0.24864 | -0.35572 | -0.46488 | -0.34661 | -0.38422 | -0.36279 | 0.31377 | 0.28875 | 0.29158 | 0.41344 | -0.16659 | -0.27863 | -0.21347 | -0.25395 | -0.19264 | -0.20286 | -0.30994 | -0.41911 | -0.30084 | -0.33844 | -0.31701 | 0.35955 | 0.33452 | 0.33736 | 0.45922 | -0.77865 | -0.75646 | -0.69799 | -0.6758
2062.4062 | 121.6324 | -0.4715 | 121.2296 | -0.22611 | -0.32899 | -0.26382 | -0.30888 | -0.23383 | -0.2578 | -0.36488 | -0.47404 | -0.35119 | -0.3888 | -0.36737 | 0.31835 | 0.29333 | 0.29616 | 0.40886 | -0.18033 | -0.28321 | -0.21805 | -0.26311 | -0.18806 | -0.21202 | -0.3191 | -0.42826 | -0.30542 | -0.34302 | -0.32159 | 0.36412 | 0.3391 | 0.34193 | 0.45464 | -0.79239 | -0.7702 | -0.70714 | -0.68495
2064.125 | 121.7697 | -0.42572 | 121.1838 | -0.21237 | -0.31983 | -0.26382 | -0.30888 | -0.22468 | -0.24864 | -0.36488 | -0.45572 | -0.34661 | -0.3888 | -0.34905 | 0.31835 | 0.28875 | 0.28242 | 0.41344 | -0.16659 | -0.27405 | -0.21805 | -0.26311 | -0.1789 | -0.20286 | -0.3191 | -0.40995 | -0.30084 | -0.34302 | -0.30328 | 0.36412 | 0.33452 | 0.3282 | 0.45922 | -0.77407 | -0.73815 | -0.70714 | -0.67122
2065.9062 | 121.7468 | -0.4303 | 121.1975 | -0.20321 | -0.31983 | -0.25924 | -0.29973 | -0.22468 | -0.24864 | -0.35572 | -0.4603 | -0.34203 | -0.37506 | -0.34905 | 0.31377 | 0.28417 | 0.287 | 0.40886 | -0.15744 | -0.27405 | -0.21347 | -0.25395 | -0.1789 | -0.20286 | -0.30994 | -0.41453 | -0.29626 | -0.32928 | -0.30328 | 0.35955 | 0.32995 | 0.33278 | 0.45464 | -0.77407 | -0.74731 | -0.68883 | -0.66206
2067.6875 | 121.6599 | -0.4303 | 121.2112 | -0.21695 | -0.31525 | -0.25467 | -0.3043 | -0.22468 | -0.24864 | -0.35572 | -0.45572 | -0.33746 | -0.37964 | -0.35821 | 0.30919 | 0.27959 | 0.287 | 0.41344 | -0.17117 | -0.26947 | -0.20889 | -0.25853 | -0.1789 | -0.20286 | -0.30994 | -0.40995 | -0.29168 | -0.33386 | -0.31244 | 0.35497 | 0.32537 | 0.33278 | 0.45922 | -0.76492 | -0.74273 | -0.68883 | -0.66664
2069.4531 | 121.7468 | -0.4303 | 121.1792 | -0.21695 | -0.32441 | -0.26382 | -0.3043 | -0.22468 | -0.24864 | -0.36488 | -0.45572 | -0.34203 | -0.38422 | -0.36279 | 0.30919 | 0.27959 | 0.29158 | 0.40886 | -0.17117 | -0.27863 | -0.21805 | -0.25853 | -0.1789 | -0.20286 | -0.3191 | -0.40995 | -0.29626 | -0.33844 | -0.31701 | 0.35497 | 0.32537 | 0.33736 | 0.45464 | -0.76492 | -0.74731 | -0.69341 | -0.6758
2071.2344 | 121.7697 | -0.43488 | 121.1746 | -0.21695 | -0.32441 | -0.27298 | -0.29973 | -0.22926 | -0.25322 | -0.35572 | -0.46488 | -0.34203 | -0.3888 | -0.37195 | 0.31377 | 0.28417 | 0.287 | 0.4226 | -0.17117 | -0.27863 | -0.2272 | -0.25395 | -0.18348 | -0.20744 | -0.30994 | -0.41911 | -0.29626 | -0.34302 | -0.32617 | 0.35955 | 0.32995 | 0.33278 | 0.46837 | -0.77865 | -0.75189 | -0.70256 | -0.6758
2072.9375 | 121.6827 | -0.46692 | 121.2021 | -0.22153 | -0.32441 | -0.2684 | -0.30888 | -0.22468 | -0.25322 | -0.3603 | -0.46488 | -0.34203 | -0.39337 | -0.36737 | 0.31377 | 0.28875 | 0.29616 | 0.4226 | -0.17575 | -0.27863 | -0.22263 | -0.26311 | -0.1789 | -0.20744 | -0.31452 | -0.41911 | -0.29626 | -0.3476 | -0.32159 | 0.35955 | 0.33452 | 0.34193 | 0.46837 | -0.77865 | -0.76104 | -0.70714 | -0.68953
2074.7188 | 121.6324 | -0.46692 | 121.2296 | -0.22153 | -0.32441 | -0.27298 | -0.30888 | -0.23383 | -0.25322 | -0.36488 | -0.46488 | -0.34661 | -0.38422 | -0.36737 | 0.31835 | 0.28875 | 0.30074 | 0.42718 | -0.17575 | -0.27863 | -0.2272 | -0.26311 | -0.18806 | -0.20744 | -0.3191 | -0.41911 | -0.30084 | -0.33844 | -0.32159 | 0.36412 | 0.33452 | 0.34651 | 0.47295 | -0.78323 | -0.76562 | -0.70256 | -0.68495
2076.4844 | 121.7972 | -0.43488 | 121.1929 | -0.22153 | -0.32899 | -0.27298 | -0.30888 | -0.23383 | -0.2578 | -0.36488 | -0.46946 | -0.35119 | -0.38422 | -0.36737 | 0.32293 | 0.30248 | 0.30989 | 0.43633 | -0.17575 | -0.28321 | -0.2272 | -0.26311 | -0.18806 | -0.21202 | -0.3191 | -0.42369 | -0.30542 | -0.33844 | -0.32159 | 0.3687 | 0.34826 | 0.35567 | 0.48211 | -0.79239 | -0.77936 | -0.70714 | -0.69411
2078.2812 | 121.6782 | -0.4715 | 121.2296 | -0.22153 | -0.33357 | -0.27756 | -0.31346 | -0.22926 | -0.2578 | -0.36488 | -0.46946 | -0.35577 | -0.39337 | -0.36737 | 0.31835 | 0.2979 | 0.30074 | 0.43175 | -0.17575 | -0.28779 | -0.23178 | -0.26769 | -0.18348 | -0.21202 | -0.3191 | -0.42369 | -0.30999 | -0.3476 | -0.32159 | 0.36412 | 0.34368 | 0.34651 | 0.47753 | -0.78781 | -0.7702 | -0.71172 | -0.69411
2079.9844 | 121.7148 | -0.43488 | 121.2021 | -0.19864 | -0.30609 | -0.25009 | -0.29057 | -0.2201 | -0.23948 | -0.34656 | -0.45572 | -0.33288 | -0.37048 | -0.3399 | 0.30003 | 0.27044 | 0.29158 | 0.40886 | -0.15286 | -0.26032 | -0.20431 | -0.24479 | -0.17433 | -0.19371 | -0.30079 | -0.40995 | -0.2871 | -0.32471 | -0.29412 | 0.34581 | 0.31621 | 0.33736 | 0.45464 | -0.75576 | -0.74731 | -0.67052 | -0.66206
2081.7656 | 121.6919 | -0.45776 | 121.2158 | -0.21237 | -0.31983 | -0.26382 | -0.29515 | -0.2201 | -0.25322 | -0.35572 | -0.45572 | -0.33288 | -0.37506 | -0.35363 | 0.30919 | 0.27959 | 0.29616 | 0.4226 | -0.16659 | -0.27405 | -0.21805 | -0.24937 | -0.17433 | -0.20744 | -0.30994 | -0.40995 | -0.2871 | -0.32928 | -0.30786 | 0.35497 | 0.32537 | 0.34193 | 0.46837 | -0.76492 | -0.75188 | -0.68425 | -0.67122
2083.5469 | 121.7239 | -0.43488 | 121.1746 | -0.21695 | -0.32441 | -0.25924 | -0.29515 | -0.22926 | -0.24864 | -0.3603 | -0.45572 | -0.34203 | -0.37964 | -0.35821 | 0.30919 | 0.29333 | 0.29616 | 0.41344 | -0.17117 | -0.27863 | -0.21347 | -0.24937 | -0.18348 | -0.20286 | -0.31452 | -0.40995 | -0.29626 | -0.33386 | -0.31244 | 0.35497 | 0.3391 | 0.34193 | 0.45922 | -0.76492 | -0.75188 | -0.68883 | -0.6758
2085.25 | 121.6553 | -0.46234 | 121.1792 | -0.21695 | -0.33357 | -0.2684 | -0.30888 | -0.22926 | -0.25322 | -0.37403 | -0.46488 | -0.34203 | -0.38422 | -0.36737 | 0.31835 | 0.27959 | 0.30074 | 0.43175 | -0.17117 | -0.28779 | -0.22263 | -0.26311 | -0.18348 | -0.20744 | -0.32826 | -0.41911 | -0.29626 | -0.33844 | -0.32159 | 0.36412 | 0.32537 | 0.34651 | 0.47753 | -0.78323 | -0.76562 | -0.70256 | -0.68495
2087.0312 | 121.7422 | -0.4303 | 121.1517 | -0.22153 | -0.33814 | -0.2684 | -0.31804 | -0.22926 | -0.26238 | -0.36945 | -0.46946 | -0.35119 | -0.3888 | -0.36737 | 0.31835 | 0.29333 | 0.30989 | 0.43633 | -0.17575 | -0.29237 | -0.22263 | -0.27227 | -0.18348 | -0.2166 | -0.32368 | -0.42369 | -0.30542 | -0.34302 | -0.32159 | 0.36412 | 0.3391 | 0.35567 | 0.48211 | -0.78781 | -0.77936 | -0.70714 | -0.69869
2088.7969 | 121.7422 | -0.43488 | 121.17 | -0.23069 | -0.3473 | -0.28672 | -0.31346 | -0.24299 | -0.27153 | -0.36945 | -0.4832 | -0.35577 | -0.39795 | -0.37195 | 0.3275 | 0.29333 | 0.31905 | 0.44091 | -0.18491 | -0.30153 | -0.24094 | -0.26769 | -0.19722 | -0.22576 | -0.32368 | -0.43742 | -0.30999 | -0.35218 | -0.32617 | 0.37328 | 0.3391 | 0.36483 | 0.48669 | -0.8107 | -0.80225 | -0.72545 | -0.717
2090.5 | 121.756 | -0.45776 | 121.1884 | -0.23526 | -0.33357 | -0.28672 | -0.32262 | -0.23841 | -0.26695 | -0.37861 | -0.47404 | -0.36035 | -0.39795 | -0.37195 | 0.3275 | 0.29333 | 0.30989 | 0.44549 | -0.18949 | -0.28779 | -0.24094 | -0.27684 | -0.19264 | -0.22118 | -0.33283 | -0.42826 | -0.31457 | -0.35218 | -0.32617 | 0.37328 | 0.3391 | 0.35567 | 0.49127 | -0.80154 | -0.78393 | -0.72545 | -0.70785
2092.2812 | 121.7606 | -0.42572 | 121.17 | -0.21237 | -0.31983 | -0.25924 | -0.30888 | -0.22468 | -0.25322 | -0.36488 | -0.4603 | -0.34661 | -0.37964 | -0.35821 | 0.30919 | 0.27959 | 0.30532 | 0.43175 | -0.16659 | -0.27405 | -0.21347 | -0.26311 | -0.1789 | -0.20744 | -0.3191 | -0.41453 | -0.30084 | -0.33386 | -0.31244 | 0.35497 | 0.32537 | 0.35109 | 0.47753 | -0.7695 | -0.76562 | -0.68883 | -0.68495
2094.0625 | 121.6415 | -0.46234 | 121.1929 | -0.21695 | -0.33357 | -0.26382 | -0.29973 | -0.22468 | -0.24864 | -0.3603 | -0.46946 | -0.34661 | -0.3888 | -0.35363 | 0.31377 | 0.29333 | 0.30989 | 0.43175 | -0.17117 | -0.28779 | -0.21805 | -0.25395 | -0.1789 | -0.20286 | -0.31452 | -0.42369 | -0.30084 | -0.34302 | -0.30786 | 0.35955 | 0.3391 | 0.35567 | 0.47753 | -0.78323 | -0.77936 | -0.70256 | -0.69869
2095.8438 | 121.7056 | -0.45319 | 121.1563 | -0.21695 | -0.32899 | -0.2684 | -0.30888 | -0.22468 | -0.26238 | -0.3603 | -0.46946 | -0.34661 | -0.37964 | -0.36279 | 0.31377 | 0.28875 | 0.31447 | 0.43633 | -0.17117 | -0.28321 | -0.22263 | -0.26311 | -0.1789 | -0.2166 | -0.31452 | -0.42369 | -0.30084 | -0.33386 | -0.31701 | 0.35955 | 0.33452 | 0.36025 | 0.48211 | -0.78323 | -0.78393 | -0.69341 | -0.69411
2097.5469 | 121.6324 | -0.50354 | 121.2021 | -0.22611 | -0.33357 | -0.27756 | -0.30888 | -0.23383 | -0.2578 | -0.36945 | -0.47862 | -0.35119 | -0.39795 | -0.37195 | 0.32293 | 0.29333 | 0.31447 | 0.44549 | -0.18033 | -0.28779 | -0.23178 | -0.26311 | -0.18806 | -0.21202 | -0.32368 | -0.43284 | -0.30542 | -0.35218 | -0.32617 | 0.3687 | 0.3391 | 0.36025 | 0.49127 | -0.80154 | -0.79309 | -0.72088 | -0.71242
2099.3281 | 121.6141 | -0.50812 | 121.1929 | -0.22611 | -0.3473 | -0.27298 | -0.31346 | -0.23841 | -0.26695 | -0.36945 | -0.47404 | -0.35577 | -0.39337 | -0.36737 | 0.32293 | 0.29333 | 0.31905 | 0.44091 | -0.18033 | -0.30153 | -0.2272 | -0.26769 | -0.19264 | -0.22118 | -0.32368 | -0.42826 | -0.30999 | -0.3476 | -0.32159 | 0.3687 | 0.3391 | 0.36483 | 0.48669 | -0.79696 | -0.79309 | -0.7163 | -0.71242
2101.1094 | 121.6461 | -0.48523 | 121.1929 | -0.23069 | -0.34272 | -0.27756 | -0.31804 | -0.23383 | -0.26695 | -0.36945 | -0.47404 | -0.35119 | -0.39337 | -0.36737 | 0.32293 | 0.30248 | 0.32363 | 0.45007 | -0.18491 | -0.29695 | -0.23178 | -0.27227 | -0.18806 | -0.22118 | -0.32368 | -0.42826 | -0.30542 | -0.3476 | -0.32159 | 0.3687 | 0.34826 | 0.36941 | 0.49584 | -0.79696 | -0.79767 | -0.7163 | -0.717
2102.8906 | 121.6003 | -0.53558 | 121.1792 | -0.23069 | -0.35188 | -0.28214 | -0.3272 | -0.24757 | -0.27153 | -0.37861 | -0.47404 | -0.36951 | -0.39795 | -0.37653 | 0.3275 | 0.30706 | 0.32821 | 0.44549 | -0.18491 | -0.3061 | -0.23636 | -0.28142 | -0.20179 | -0.22576 | -0.33283 | -0.42826 | -0.32373 | -0.35218 | -0.33075 | 0.37328 | 0.35284 | 0.37398 | 0.49127 | -0.80154 | -0.80225 | -0.72545 | -0.72616
2104.5938 | 121.637 | -0.50354 | 121.1563 | -0.249 | -0.3473 | -0.28672 | -0.33178 | -0.24299 | -0.27611 | -0.38777 | -0.48778 | -0.36951 | -0.41169 | -0.37653 | 0.3275 | 0.2979 | 0.32821 | 0.45465 | -0.20322 | -0.30153 | -0.24094 | -0.286 | -0.19722 | -0.23033 | -0.34199 | -0.442 | -0.32373 | -0.36591 | -0.33075 | 0.37328 | 0.34368 | 0.37398 | 0.50042 | -0.81528 | -0.81598 | -0.73919 | -0.73989
2106.3125 | 121.7194 | -0.48065 | 121.1563 | -0.249 | -0.35646 | -0.29587 | -0.34093 | -0.25215 | -0.27611 | -0.38777 | -0.48778 | -0.37409 | -0.41169 | -0.38111 | 0.34124 | 0.31622 | 0.33279 | 0.46838 | -0.20322 | -0.31068 | -0.2501 | -0.29516 | -0.20637 | -0.23033 | -0.34199 | -0.442 | -0.32831 | -0.36591 | -0.33533 | 0.38701 | 0.36199 | 0.37856 | 0.51416 | -0.82901 | -0.82056 | -0.75293 | -0.74447
2108.0938 | 121.6644 | -0.46692 | 121.2158 | -0.21695 | -0.32899 | -0.2684 | -0.31804 | -0.23383 | -0.2578 | -0.36945 | -0.46946 | -0.34661 | -0.38422 | -0.37195 | 0.31835 | 0.29333 | 0.32363 | 0.43633 | -0.17117 | -0.28321 | -0.22263 | -0.27227 | -0.18806 | -0.21202 | -0.32368 | -0.42369 | -0.30084 | -0.33844 | -0.32617 | 0.36412 | 0.3391 | 0.36941 | 0.48211 | -0.78781 | -0.79309 | -0.70256 | -0.70785
2109.875 | 121.7514 | -0.4715 | 121.138 | -0.23526 | -0.35188 | -0.27756 | -0.32262 | -0.23841 | -0.27153 | -0.37403 | -0.47862 | -0.36035 | -0.39795 | -0.37195 | 0.32293 | 0.30706 | 0.33279 | 0.45465 | -0.18949 | -0.3061 | -0.23178 | -0.27684 | -0.19264 | -0.22576 | -0.32826 | -0.43284 | -0.31457 | -0.35218 | -0.32617 | 0.3687 | 0.35284 | 0.37856 | 0.50042 | -0.80154 | -0.8114 | -0.72088 | -0.73074
2111.5781 | 121.7377 | -0.49439 | 121.1243 | -0.24442 | -0.36562 | -0.28672 | -0.33636 | -0.25672 | -0.27611 | -0.37861 | -0.47862 | -0.36951 | -0.40253 | -0.38569 | 0.34582 | 0.31622 | 0.33737 | 0.4638 | -0.19864 | -0.31984 | -0.24094 | -0.29058 | -0.21095 | -0.23033 | -0.33283 | -0.43284 | -0.32373 | -0.35675 | -0.33991 | 0.39159 | 0.36199 | 0.38314 | 0.50958 | -0.82444 | -0.81598 | -0.74835 | -0.73989
2113.3594 | 121.701 | -0.49439 | 121.1334 | -0.249 | -0.36104 | -0.29129 | -0.33636 | -0.26588 | -0.28985 | -0.39692 | -0.49235 | -0.37409 | -0.41169 | -0.39026 | 0.34124 | 0.32079 | 0.34652 | 0.46838 | -0.20322 | -0.31526 | -0.24552 | -0.29058 | -0.2201 | -0.24407 | -0.35115 | -0.44658 | -0.32831 | -0.36591 | -0.34449 | 0.38701 | 0.36657 | 0.3923 | 0.51416 | -0.83359 | -0.83888 | -0.75293 | -0.75821
2115.125 | 121.7468 | -0.48065 | 121.1014 | -0.25816 | -0.36562 | -0.30045 | -0.33636 | -0.2613 | -0.29442 | -0.39692 | -0.49693 | -0.37866 | -0.41626 | -0.39026 | 0.34582 | 0.32079 | 0.34194 | 0.47296 | -0.21238 | -0.31984 | -0.25468 | -0.29058 | -0.21553 | -0.24865 | -0.35115 | -0.45116 | -0.33289 | -0.37049 | -0.34449 | 0.39159 | 0.36657 | 0.38772 | 0.51873 | -0.84275 | -0.83888 | -0.76208 | -0.75821
2116.8906 | 121.6141 | -0.53101 | 121.1197 | -0.26273 | -0.3702 | -0.30961 | -0.34551 | -0.27046 | -0.29442 | -0.40608 | -0.50609 | -0.3924 | -0.43458 | -0.404 | 0.3504 | 0.33453 | 0.35568 | 0.49127 | -0.21696 | -0.32442 | -0.26383 | -0.29974 | -0.22468 | -0.24865 | -0.3603 | -0.46031 | -0.34663 | -0.3888 | -0.35823 | 0.39617 | 0.3803 | 0.40145 | 0.53705 | -0.85648 | -0.86177 | -0.78497 | -0.79026
2118.6562 | 121.701 | -0.53101 | 121.0922 | -0.28105 | -0.39767 | -0.3325 | -0.36383 | -0.28877 | -0.31732 | -0.42439 | -0.52898 | -0.40156 | -0.44373 | -0.4269 | 0.37329 | 0.34369 | 0.37857 | 0.50958 | -0.23527 | -0.35189 | -0.28673 | -0.31805 | -0.24299 | -0.27154 | -0.37862 | -0.48321 | -0.35578 | -0.39796 | -0.38112 | 0.41906 | 0.38946 | 0.42435 | 0.55536 | -0.90227 | -0.90755 | -0.81702 | -0.8223
2120.4219 | 121.6919 | -0.54474 | 121.0739 | -0.2902 | -0.40225 | -0.3325 | -0.37298 | -0.29335 | -0.31732 | -0.42439 | -0.53814 | -0.40614 | -0.44831 | -0.41774 | 0.37329 | 0.35742 | 0.37857 | 0.50501 | -0.24443 | -0.35647 | -0.28673 | -0.32721 | -0.24757 | -0.27154 | -0.37862 | -0.49236 | -0.36036 | -0.40254 | -0.37196 | 0.41906 | 0.40319 | 0.42435 | 0.55078 | -0.91142 | -0.91671 | -0.8216 | -0.82688
2122.125 | 121.6827 | -0.50812 | 121.0922 | -0.27189 | -0.38393 | -0.31419 | -0.35467 | -0.27046 | -0.30358 | -0.41524 | -0.51067 | -0.3924 | -0.43458 | -0.404 | 0.35955 | 0.33911 | 0.35568 | 0.49585 | -0.22611 | -0.33816 | -0.26841 | -0.30889 | -0.22468 | -0.2578 | -0.36946 | -0.46489 | -0.34663 | -0.3888 | -0.35823 | 0.40533 | 0.38488 | 0.40145 | 0.54163 | -0.87022 | -0.86634 | -0.79413 | -0.79026
2123.8906 | 121.7331 | -0.4715 | 121.0968 | -0.25816 | -0.3702 | -0.30045 | -0.34093 | -0.26588 | -0.28527 | -0.39692 | -0.50151 | -0.37866 | -0.41169 | -0.39942 | 0.34582 | 0.32537 | 0.3511 | 0.48669 | -0.21238 | -0.32442 | -0.25468 | -0.29516 | -0.2201 | -0.23949 | -0.35115 | -0.45573 | -0.33289 | -0.36591 | -0.35365 | 0.39159 | 0.37115 | 0.39688 | 0.53247 | -0.84733 | -0.85261 | -0.7575 | -0.76279
2125.6562 | 121.6324 | -0.50812 | 121.1243 | -0.24442 | -0.35188 | -0.29587 | -0.33636 | -0.25672 | -0.28985 | -0.38319 | -0.48778 | -0.36951 | -0.41169 | -0.38569 | 0.33666 | 0.31622 | 0.33737 | 0.4638 | -0.19864 | -0.3061 | -0.2501 | -0.29058 | -0.21095 | -0.24407 | -0.33741 | -0.442 | -0.32373 | -0.36591 | -0.33991 | 0.38244 | 0.36199 | 0.38314 | 0.50958 | -0.82444 | -0.82514 | -0.74835 | -0.74905
2127.3594 | 121.7377 | -0.48981 | 121.0968 | -0.23984 | -0.35646 | -0.28672 | -0.33178 | -0.24757 | -0.28069 | -0.38777 | -0.48778 | -0.36493 | -0.41169 | -0.39026 | 0.33208 | 0.30706 | 0.33737 | 0.47296 | -0.19407 | -0.31068 | -0.24094 | -0.286 | -0.20179 | -0.23491 | -0.34199 | -0.442 | -0.31915 | -0.36591 | -0.34449 | 0.37786 | 0.35284 | 0.38314 | 0.51873 | -0.81986 | -0.82514 | -0.74377 | -0.74905
2129.1406 | 121.637 | -0.48065 | 121.1609 | -0.22611 | -0.34272 | -0.2684 | -0.30888 | -0.23841 | -0.2578 | -0.36488 | -0.47404 | -0.35577 | -0.38422 | -0.36279 | 0.31835 | 0.29333 | 0.32363 | 0.45922 | -0.18033 | -0.29695 | -0.22263 | -0.26311 | -0.19264 | -0.21202 | -0.3191 | -0.42826 | -0.30999 | -0.33844 | -0.31701 | 0.36412 | 0.3391 | 0.36941 | 0.505 | -0.79239 | -0.79767 | -0.70256 | -0.70785
2130.9219 | 121.6827 | -0.46234 | 121.106 | -0.22153 | -0.33357 | -0.2684 | -0.30888 | -0.23383 | -0.27153 | -0.36488 | -0.46488 | -0.36035 | -0.38422 | -0.36279 | 0.31835 | 0.29333 | 0.32363 | 0.45922 | -0.17575 | -0.28779 | -0.22263 | -0.26311 | -0.18806 | -0.22576 | -0.3191 | -0.41911 | -0.31457 | -0.33844 | -0.31701 | 0.36412 | 0.3391 | 0.36941 | 0.505 | -0.78323 | -0.78851 | -0.70256 | -0.70785
2132.7031 | 121.7148 | -0.45319 | 121.0922 | -0.21695 | -0.33357 | -0.2684 | -0.30888 | -0.22926 | -0.26238 | -0.36488 | -0.47404 | -0.35119 | -0.3888 | -0.35821 | 0.30919 | 0.28417 | 0.32363 | 0.45465 | -0.17117 | -0.28779 | -0.22263 | -0.26311 | -0.18348 | -0.2166 | -0.3191 | -0.42826 | -0.30542 | -0.34302 | -0.31244 | 0.35497 | 0.32995 | 0.36941 | 0.50042 | -0.78323 | -0.79767 | -0.69799 | -0.71242
2134.4219 | 121.6965 | -0.46692 | 121.106 | -0.22153 | -0.32899 | -0.2684 | -0.31346 | -0.22926 | -0.2578 | -0.3603 | -0.46488 | -0.34203 | -0.38422 | -0.35363 | 0.31377 | 0.28417 | 0.32821 | 0.45465 | -0.17575 | -0.28321 | -0.22263 | -0.26769 | -0.18348 | -0.21202 | -0.31452 | -0.41911 | -0.29626 | -0.33844 | -0.30786 | 0.35955 | 0.32995 | 0.37398 | 0.50042 | -0.77865 | -0.79309 | -0.69799 | -0.71242
2136.2031 | 121.756 | -0.45319 | 121.1472 | -0.20779 | -0.31983 | -0.25009 | -0.29973 | -0.21094 | -0.25322 | -0.35572 | -0.4603 | -0.33288 | -0.35675 | -0.34905 | 0.29546 | 0.28417 | 0.30989 | 0.43633 | -0.16202 | -0.27405 | -0.20431 | -0.25395 | -0.16517 | -0.20744 | -0.30994 | -0.41453 | -0.2871 | -0.31097 | -0.30328 | 0.34123 | 0.32995 | 0.35567 | 0.48211 | -0.75576 | -0.7702 | -0.6522 | -0.66664
2138 | 121.5866 | -0.48523 | 121.17 | -0.22153 | -0.33357 | -0.26382 | -0.30888 | -0.22468 | -0.25322 | -0.36488 | -0.46946 | -0.34203 | -0.37506 | -0.35821 | 0.30461 | 0.27959 | 0.32363 | 0.45465 | -0.17575 | -0.28779 | -0.21805 | -0.26311 | -0.1789 | -0.20744 | -0.3191 | -0.42369 | -0.29626 | -0.32928 | -0.31244 | 0.35039 | 0.32537 | 0.36941 | 0.50042 | -0.77407 | -0.79309 | -0.67967 | -0.69869
2139.7656 | 121.5729 | -0.50354 | 121.1334 | -0.21695 | -0.32899 | -0.2684 | -0.3043 | -0.23383 | -0.25322 | -0.36945 | -0.46946 | -0.34203 | -0.38422 | -0.35821 | 0.30919 | 0.28417 | 0.32363 | 0.45465 | -0.17117 | -0.28321 | -0.22263 | -0.25853 | -0.18806 | -0.20744 | -0.32368 | -0.42369 | -0.29626 | -0.33844 | -0.31244 | 0.35497 | 0.32995 | 0.36941 | 0.50042 | -0.77865 | -0.79309 | -0.69341 | -0.70785
2141.4688 | 121.582 | -0.54016 | 121.1426 | -0.22611 | -0.34272 | -0.28214 | -0.32262 | -0.23383 | -0.26695 | -0.37403 | -0.4832 | -0.36035 | -0.3888 | -0.36737 | 0.32293 | 0.30248 | 0.33737 | 0.46838 | -0.18033 | -0.29695 | -0.23636 | -0.27684 | -0.18806 | -0.22118 | -0.32826 | -0.43742 | -0.31457 | -0.34302 | -0.32159 | 0.3687 | 0.34826 | 0.38314 | 0.51416 | -0.80612 | -0.82056 | -0.71172 | -0.72616
2143.25 | 121.5912 | -0.52185 | 121.106 | -0.24442 | -0.35188 | -0.29129 | -0.32262 | -0.25215 | -0.27611 | -0.37861 | -0.49235 | -0.37409 | -0.41169 | -0.37653 | 0.33208 | 0.30706 | 0.35568 | 0.47296 | -0.19864 | -0.3061 | -0.24552 | -0.27684 | -0.20637 | -0.23033 | -0.33283 | -0.44658 | -0.32831 | -0.36591 | -0.33075 | 0.37786 | 0.35284 | 0.40145 | 0.51873 | -0.82444 | -0.84803 | -0.74377 | -0.76736
2145.0156 | 121.669 | -0.48065 | 121.1426 | -0.22153 | -0.32899 | -0.26382 | -0.30888 | -0.23383 | -0.2578 | -0.36488 | -0.46946 | -0.34661 | -0.37964 | -0.36279 | 0.30919 | 0.29333 | 0.32821 | 0.4638 | -0.17575 | -0.28321 | -0.21805 | -0.26311 | -0.18806 | -0.21202 | -0.3191 | -0.42369 | -0.30084 | -0.33386 | -0.31701 | 0.35497 | 0.3391 | 0.37398 | 0.50958 | -0.77865 | -0.79767 | -0.68883 | -0.70785
2146.7969 | 121.582 | -0.48523 | 121.1426 | -0.21237 | -0.31525 | -0.25467 | -0.29515 | -0.22468 | -0.24864 | -0.35114 | -0.45572 | -0.33746 | -0.37048 | -0.34905 | 0.30003 | 0.27959 | 0.31905 | 0.45465 | -0.16659 | -0.26947 | -0.20889 | -0.24937 | -0.1789 | -0.20286 | -0.30537 | -0.40995 | -0.29168 | -0.32471 | -0.30328 | 0.34581 | 0.32537 | 0.36483 | 0.50042 | -0.75576 | -0.77478 | -0.67052 | -0.68953
2148.5625 | 121.637 | -0.48065 | 121.1151 | -0.21695 | -0.31983 | -0.26382 | -0.30888 | -0.21552 | -0.24864 | -0.3603 | -0.46946 | -0.34203 | -0.37964 | -0.35363 | 0.30919 | 0.27959 | 0.32821 | 0.45465 | -0.17117 | -0.27405 | -0.21805 | -0.26311 | -0.16975 | -0.20286 | -0.31452 | -0.42369 | -0.29626 | -0.33386 | -0.30786 | 0.35497 | 0.32537 | 0.37398 | 0.50042 | -0.77865 | -0.79767 | -0.68883 | -0.70785
2150.3281 | 121.5958 | -0.51727 | 121.1426 | -0.21237 | -0.32441 | -0.25924 | -0.30888 | -0.22468 | -0.2578 | -0.35572 | -0.46946 | -0.34661 | -0.37506 | -0.35821 | 0.30919 | 0.28417 | 0.32821 | 0.45922 | -0.16659 | -0.27863 | -0.21347 | -0.26311 | -0.1789 | -0.21202 | -0.30994 | -0.42369 | -0.30084 | -0.32928 | -0.31244 | 0.35497 | 0.32995 | 0.37398 | 0.505 | -0.77865 | -0.79767 | -0.68425 | -0.70327
2152.0938 | 121.6095 | -0.49896 | 121.1243 | -0.21695 | -0.32899 | -0.26382 | -0.31804 | -0.22926 | -0.2578 | -0.36945 | -0.46488 | -0.34203 | -0.38422 | -0.35821 | 0.31377 | 0.27959 | 0.33737 | 0.4638 | -0.17117 | -0.28321 | -0.21805 | -0.27227 | -0.18348 | -0.21202 | -0.32368 | -0.41911 | -0.29626 | -0.33844 | -0.31244 | 0.35955 | 0.32537 | 0.38314 | 0.50958 | -0.77865 | -0.80225 | -0.69799 | -0.72158
2153.7969 | 121.582 | -0.52643 | 121.106 | -0.21695 | -0.32899 | -0.2684 | -0.30888 | -0.22926 | -0.26238 | -0.36945 | -0.46488 | -0.34203 | -0.37964 | -0.36279 | 0.31377 | 0.27959 | 0.34194 | 0.47296 | -0.17117 | -0.28321 | -0.22263 | -0.26311 | -0.18348 | -0.2166 | -0.32368 | -0.41911 | -0.29626 | -0.33386 | -0.31701 | 0.35955 | 0.32537 | 0.38772 | 0.51873 | -0.77865 | -0.80683 | -0.69341 | -0.72158
2155.5625 | 121.6278 | -0.53101 | 121.1014 | -0.22153 | -0.33814 | -0.27298 | -0.31346 | -0.23383 | -0.2578 | -0.36945 | -0.46946 | -0.35577 | -0.37964 | -0.35821 | 0.31835 | 0.28417 | 0.33737 | 0.47296 | -0.17575 | -0.29237 | -0.2272 | -0.26769 | -0.18806 | -0.21202 | -0.32368 | -0.42369 | -0.30999 | -0.33386 | -0.31244 | 0.36412 | 0.32995 | 0.38314 | 0.51873 | -0.78781 | -0.80683 | -0.69799 | -0.717
2157.2656 | 121.5958 | -0.48065 | 121.138 | -0.19406 | -0.30609 | -0.24093 | -0.28141 | -0.20637 | -0.2349 | -0.34199 | -0.42825 | -0.32372 | -0.34759 | -0.33074 | 0.28172 | 0.2567 | 0.32363 | 0.44091 | -0.14828 | -0.26032 | -0.19515 | -0.23564 | -0.16059 | -0.18913 | -0.29621 | -0.38248 | -0.27794 | -0.30181 | -0.28496 | 0.3275 | 0.30248 | 0.36941 | 0.48669 | -0.70998 | -0.75188 | -0.62931 | -0.67122
2159.0469 | 121.6049 | -0.4715 | 121.138 | -0.17574 | -0.28778 | -0.21804 | -0.2631 | -0.18348 | -0.21201 | -0.32825 | -0.42368 | -0.30083 | -0.33843 | -0.317 | 0.26799 | 0.24297 | 0.30989 | 0.42718 | -0.12997 | -0.242 | -0.17226 | -0.21732 | -0.1377 | -0.16624 | -0.28248 | -0.3779 | -0.25505 | -0.29266 | -0.27122 | 0.31376 | 0.28874 | 0.35567 | 0.47295 | -0.69166 | -0.73357 | -0.60642 | -0.64833
2160.8281 | 121.6965 | -0.4303 | 121.1151 | -0.17574 | -0.28778 | -0.21804 | -0.2631 | -0.18348 | -0.21201 | -0.3191 | -0.41452 | -0.29625 | -0.3247 | -0.30326 | 0.25883 | 0.23839 | 0.30074 | 0.41802 | -0.12997 | -0.242 | -0.17226 | -0.21732 | -0.1377 | -0.16624 | -0.27332 | -0.36874 | -0.25047 | -0.27892 | -0.25749 | 0.30461 | 0.28417 | 0.34651 | 0.4638 | -0.67335 | -0.71526 | -0.58353 | -0.62544
2162.5938 | 121.7148 | -0.4303 | 121.1243 | -0.17117 | -0.2832 | -0.22262 | -0.2631 | -0.18348 | -0.20286 | -0.3191 | -0.4191 | -0.30083 | -0.32928 | -0.30784 | 0.25883 | 0.22923 | 0.30532 | 0.4226 | -0.12539 | -0.23742 | -0.17684 | -0.21732 | -0.1377 | -0.15708 | -0.27332 | -0.37332 | -0.25505 | -0.2835 | -0.26207 | 0.30461 | 0.27501 | 0.35109 | 0.46837 | -0.67793 | -0.72441 | -0.58811 | -0.63459
2164.3906 | 121.6187 | -0.49896 | 121.1334 | -0.18032 | -0.28778 | -0.21804 | -0.26768 | -0.18805 | -0.20743 | -0.32367 | -0.41452 | -0.29625 | -0.32928 | -0.31242 | 0.25883 | 0.23381 | 0.30074 | 0.43633 | -0.13455 | -0.242 | -0.17226 | -0.2219 | -0.14228 | -0.16166 | -0.2779 | -0.36874 | -0.25047 | -0.2835 | -0.26665 | 0.30461 | 0.27959 | 0.34651 | 0.48211 | -0.67335 | -0.71526 | -0.58811 | -0.63001
2166.1719 | 121.6827 | -0.42572 | 121.1609 | -0.13912 | -0.2603 | -0.19514 | -0.24021 | -0.16517 | -0.1937 | -0.30078 | -0.38247 | -0.27335 | -0.31096 | -0.28495 | 0.23594 | 0.21092 | 0.29158 | 0.40429 | -0.093341 | -0.21453 | -0.14937 | -0.19443 | -0.11939 | -0.14792 | -0.25501 | -0.33669 | -0.22758 | -0.26519 | -0.23917 | 0.28172 | 0.2567 | 0.33736 | 0.45006 | -0.61841 | -0.67405 | -0.5469 | -0.60254
2167.9375 | 121.6873 | -0.43488 | 121.106 | -0.16201 | -0.2832 | -0.21346 | -0.2631 | -0.1789 | -0.20286 | -0.31452 | -0.41452 | -0.29167 | -0.32928 | -0.29868 | 0.25883 | 0.22465 | 0.30532 | 0.42718 | -0.11623 | -0.23742 | -0.16768 | -0.21732 | -0.13312 | -0.15708 | -0.26874 | -0.36874 | -0.24589 | -0.2835 | -0.25291 | 0.30461 | 0.27043 | 0.35109 | 0.47295 | -0.67335 | -0.71984 | -0.58811 | -0.63459
2169.7031 | 121.5912 | -0.50812 | 121.17 | -0.17574 | -0.28778 | -0.20888 | -0.26768 | -0.18805 | -0.20743 | -0.32367 | -0.41452 | -0.29625 | -0.33386 | -0.31242 | 0.25425 | 0.23839 | 0.30989 | 0.43633 | -0.12997 | -0.242 | -0.1631 | -0.2219 | -0.14228 | -0.16166 | -0.2779 | -0.36874 | -0.25047 | -0.28808 | -0.26665 | 0.30003 | 0.28417 | 0.35567 | 0.48211 | -0.66877 | -0.72441 | -0.58811 | -0.64375
2171.4219 | 121.6599 | -0.44861 | 121.0739 | -0.17574 | -0.28778 | -0.22719 | -0.27226 | -0.18348 | -0.20743 | -0.3191 | -0.42825 | -0.29625 | -0.32928 | -0.31242 | 0.26799 | 0.24297 | 0.32363 | 0.44549 | -0.12997 | -0.242 | -0.18142 | -0.22648 | -0.1377 | -0.16166 | -0.27332 | -0.38248 | -0.25047 | -0.2835 | -0.26665 | 0.31376 | 0.28874 | 0.36941 | 0.49127 | -0.69624 | -0.75188 | -0.59726 | -0.65291
2173.1875 | 121.7148 | -0.45319 | 121.0739 | -0.18032 | -0.30151 | -0.22719 | -0.27226 | -0.18805 | -0.22117 | -0.32825 | -0.42368 | -0.3054 | -0.33843 | -0.317 | 0.27257 | 0.24297 | 0.31905 | 0.45465 | -0.13455 | -0.25574 | -0.18142 | -0.22648 | -0.14228 | -0.17539 | -0.28248 | -0.3779 | -0.25963 | -0.29266 | -0.27122 | 0.31834 | 0.28874 | 0.36483 | 0.50042 | -0.69624 | -0.74273 | -0.611 | -0.65748
2174.9688 | 121.6827 | -0.45319 | 121.0831 | -0.17574 | -0.30151 | -0.23635 | -0.27683 | -0.19721 | -0.22117 | -0.32825 | -0.42368 | -0.3054 | -0.34301 | -0.30784 | 0.27257 | 0.24754 | 0.32363 | 0.45007 | -0.12997 | -0.25574 | -0.19057 | -0.23106 | -0.15143 | -0.17539 | -0.28248 | -0.3779 | -0.25963 | -0.29724 | -0.26207 | 0.31834 | 0.29332 | 0.36941 | 0.49584 | -0.69624 | -0.74731 | -0.61558 | -0.66664
2176.6719 | 121.6827 | -0.48065 | 121.0831 | -0.18948 | -0.30151 | -0.23177 | -0.27683 | -0.19721 | -0.22575 | -0.34199 | -0.43741 | -0.3054 | -0.34301 | -0.32158 | 0.27714 | 0.24754 | 0.32821 | 0.4638 | -0.1437 | -0.25574 | -0.186 | -0.23106 | -0.15143 | -0.17997 | -0.29621 | -0.39164 | -0.25963 | -0.29724 | -0.2758 | 0.32292 | 0.29332 | 0.37398 | 0.50958 | -0.71456 | -0.76562 | -0.62016 | -0.67122
2178.4531 | 121.5958 | -0.52643 | 121.0785 | -0.19406 | -0.31067 | -0.24093 | -0.29515 | -0.21094 | -0.2349 | -0.34656 | -0.44199 | -0.32372 | -0.35217 | -0.33532 | 0.2863 | 0.2567 | 0.34194 | 0.47296 | -0.14828 | -0.26489 | -0.19515 | -0.24937 | -0.16517 | -0.18913 | -0.30079 | -0.39621 | -0.27794 | -0.30639 | -0.28954 | 0.33208 | 0.30248 | 0.38772 | 0.51873 | -0.72829 | -0.78393 | -0.63847 | -0.69411
2180.2344 | 121.6599 | -0.50354 | 121.0556 | -0.20779 | -0.31067 | -0.25009 | -0.29973 | -0.21552 | -0.23948 | -0.33741 | -0.44199 | -0.3283 | -0.35675 | -0.33532 | 0.29088 | 0.26128 | 0.34652 | 0.48212 | -0.16202 | -0.26489 | -0.20431 | -0.25395 | -0.16975 | -0.19371 | -0.29163 | -0.39621 | -0.28252 | -0.31097 | -0.28954 | 0.33665 | 0.30705 | 0.3923 | 0.52789 | -0.73287 | -0.78851 | -0.64763 | -0.70327
2182 | 121.669 | -0.50812 | 121.051 | -0.21695 | -0.32899 | -0.25467 | -0.3043 | -0.2201 | -0.25322 | -0.35572 | -0.45115 | -0.33288 | -0.36133 | -0.34447 | 0.30003 | 0.27501 | 0.35568 | 0.48212 | -0.17117 | -0.28321 | -0.20889 | -0.25853 | -0.17433 | -0.20744 | -0.30994 | -0.40537 | -0.2871 | -0.31555 | -0.2987 | 0.34581 | 0.32079 | 0.40145 | 0.52789 | -0.75118 | -0.80683 | -0.66136 | -0.717
2183.7188 | 121.6827 | -0.50812 | 121.019 | -0.20779 | -0.32441 | -0.25467 | -0.29515 | -0.22468 | -0.24864 | -0.3603 | -0.45115 | -0.3283 | -0.36133 | -0.3399 | 0.30461 | 0.27044 | 0.36026 | 0.49127 | -0.16202 | -0.27863 | -0.20889 | -0.24937 | -0.1789 | -0.20286 | -0.31452 | -0.40537 | -0.28252 | -0.31555 | -0.29412 | 0.35039 | 0.31621 | 0.40603 | 0.53705 | -0.75576 | -0.8114 | -0.66594 | -0.72158
2185.4844 | 121.6782 | -0.50354 | 121.0007 | -0.21237 | -0.33357 | -0.26382 | -0.30888 | -0.23383 | -0.26238 | -0.37403 | -0.46488 | -0.34661 | -0.3659 | -0.35363 | 0.30461 | 0.28875 | 0.36484 | 0.50043 | -0.16659 | -0.28779 | -0.21805 | -0.26311 | -0.18806 | -0.2166 | -0.32826 | -0.41911 | -0.30084 | -0.32013 | -0.30786 | 0.35039 | 0.33452 | 0.41061 | 0.5462 | -0.7695 | -0.82972 | -0.67052 | -0.73074
2187.2656 | 121.6553 | -0.51727 | 121.0236 | -0.21695 | -0.32441 | -0.25467 | -0.3043 | -0.22926 | -0.2578 | -0.3603 | -0.4603 | -0.33288 | -0.3659 | -0.34905 | 0.30003 | 0.27044 | 0.36484 | 0.48669 | -0.17117 | -0.27863 | -0.20889 | -0.25853 | -0.18348 | -0.21202 | -0.31452 | -0.41453 | -0.2871 | -0.32013 | -0.30328 | 0.34581 | 0.31621 | 0.41061 | 0.53247 | -0.76034 | -0.82514 | -0.66594 | -0.73074
2189.0469 | 121.637 | -0.52643 | 121.0373 | -0.21237 | -0.33357 | -0.2684 | -0.30888 | -0.22926 | -0.26695 | -0.37403 | -0.46488 | -0.35119 | -0.38422 | -0.35821 | 0.30461 | 0.27959 | 0.36941 | 0.50043 | -0.16659 | -0.28779 | -0.22263 | -0.26311 | -0.18348 | -0.22118 | -0.32826 | -0.41911 | -0.30542 | -0.33844 | -0.31244 | 0.35039 | 0.32537 | 0.41519 | 0.5462 | -0.7695 | -0.8343 | -0.68883 | -0.75363
2190.8125 | 121.5408 | -0.56763 | 121.0419 | -0.23069 | -0.33814 | -0.27756 | -0.31346 | -0.23383 | -0.26695 | -0.37861 | -0.47404 | -0.35119 | -0.3888 | -0.36737 | 0.32293 | 0.28875 | 0.37857 | 0.52332 | -0.18491 | -0.29237 | -0.23178 | -0.26769 | -0.18806 | -0.22118 | -0.33283 | -0.42826 | -0.30542 | -0.34302 | -0.32159 | 0.3687 | 0.33452 | 0.42435 | 0.56909 | -0.79696 | -0.85261 | -0.71172 | -0.76737
2192.5156 | 121.6003 | -0.56305 | 121.0464 | -0.21695 | -0.32441 | -0.26382 | -0.3043 | -0.23383 | -0.2578 | -0.36488 | -0.4603 | -0.35119 | -0.37506 | -0.34905 | 0.30919 | 0.27959 | 0.37399 | 0.50501 | -0.17117 | -0.27863 | -0.21805 | -0.25853 | -0.18806 | -0.21202 | -0.3191 | -0.41453 | -0.30542 | -0.32928 | -0.30328 | 0.35497 | 0.32537 | 0.41977 | 0.55078 | -0.7695 | -0.8343 | -0.68425 | -0.74905
2194.2969 | 121.6644 | -0.52185 | 121.0464 | -0.20321 | -0.31525 | -0.24093 | -0.29057 | -0.21094 | -0.2349 | -0.34199 | -0.44199 | -0.31456 | -0.35217 | -0.33074 | 0.27714 | 0.25212 | 0.36026 | 0.48212 | -0.15744 | -0.26947 | -0.19515 | -0.24479 | -0.16517 | -0.18913 | -0.29621 | -0.39621 | -0.26878 | -0.30639 | -0.28496 | 0.32292 | 0.2979 | 0.40603 | 0.52789 | -0.71913 | -0.80225 | -0.62931 | -0.71243
2196.0625 | 121.669 | -0.48981 | 120.9824 | -0.20779 | -0.32441 | -0.25467 | -0.29515 | -0.21552 | -0.25322 | -0.35572 | -0.44199 | -0.33288 | -0.36133 | -0.34447 | 0.30003 | 0.26128 | 0.36484 | 0.49585 | -0.16202 | -0.27863 | -0.20889 | -0.24937 | -0.16975 | -0.20744 | -0.30994 | -0.39621 | -0.2871 | -0.31555 | -0.2987 | 0.34581 | 0.30705 | 0.41061 | 0.54163 | -0.74202 | -0.80683 | -0.66136 | -0.72616
2197.8281 | 121.6507 | -0.53558 | 120.9778 | -0.21237 | -0.33357 | -0.25924 | -0.29973 | -0.2201 | -0.25322 | -0.34656 | -0.45572 | -0.33288 | -0.36133 | -0.3399 | 0.28172 | 0.26586 | 0.36484 | 0.50043 | -0.16659 | -0.28779 | -0.21347 | -0.25395 | -0.17433 | -0.20744 | -0.30079 | -0.40995 | -0.2871 | -0.31555 | -0.29412 | 0.3275 | 0.31163 | 0.41061 | 0.5462 | -0.73745 | -0.82056 | -0.64305 | -0.72616
2199.5469 | 121.6553 | -0.51727 | 120.9915 | -0.21237 | -0.32441 | -0.25009 | -0.29973 | -0.2201 | -0.24864 | -0.35572 | -0.45115 | -0.3283 | -0.36133 | -0.34905 | 0.29088 | 0.27044 | 0.37399 | 0.50501 | -0.16659 | -0.27863 | -0.20431 | -0.25395 | -0.17433 | -0.20286 | -0.30994 | -0.40537 | -0.28252 | -0.31555 | -0.30328 | 0.33665 | 0.31621 | 0.41977 | 0.55078 | -0.74203 | -0.82514 | -0.6522 | -0.73532
2201.3125 | 121.5454 | -0.58136 | 121.0419 | -0.21695 | -0.32441 | -0.26382 | -0.30888 | -0.22468 | -0.24864 | -0.3603 | -0.4603 | -0.34661 | -0.3659 | -0.33532 | 0.29546 | 0.27044 | 0.37857 | 0.50958 | -0.17117 | -0.27863 | -0.21805 | -0.26311 | -0.1789 | -0.20286 | -0.31452 | -0.41453 | -0.30084 | -0.32013 | -0.28954 | 0.34123 | 0.31621 | 0.42435 | 0.55536 | -0.75576 | -0.83887 | -0.66136 | -0.74447
2203.0938 | 121.5134 | -0.55847 | 121.0236 | -0.21237 | -0.32899 | -0.25009 | -0.29973 | -0.2201 | -0.24864 | -0.3603 | -0.45572 | -0.33746 | -0.3659 | -0.34447 | 0.29546 | 0.27044 | 0.36941 | 0.50501 | -0.16659 | -0.28321 | -0.20431 | -0.25395 | -0.17433 | -0.20286 | -0.31452 | -0.40995 | -0.29168 | -0.32013 | -0.2987 | 0.34123 | 0.31621 | 0.41519 | 0.55078 | -0.75118 | -0.82514 | -0.66136 | -0.73532
2204.875 | 121.669 | -0.52643 | 120.9824 | -0.21237 | -0.32899 | -0.26382 | -0.3043 | -0.23383 | -0.25322 | -0.36488 | -0.46946 | -0.33746 | -0.37048 | -0.34447 | 0.30919 | 0.27959 | 0.37857 | 0.50958 | -0.16659 | -0.28321 | -0.21805 | -0.25853 | -0.18806 | -0.20744 | -0.3191 | -0.42369 | -0.29168 | -0.32471 | -0.2987 | 0.35497 | 0.32537 | 0.42435 | 0.55536 | -0.77865 | -0.84803 | -0.67967 | -0.74905
2206.5781 | 121.637 | -0.53558 | 120.9595 | -0.22153 | -0.33357 | -0.26382 | -0.30888 | -0.22926 | -0.26238 | -0.36488 | -0.4603 | -0.34203 | -0.37048 | -0.34905 | 0.30919 | 0.27959 | 0.37399 | 0.51874 | -0.17575 | -0.28779 | -0.21805 | -0.26311 | -0.18348 | -0.2166 | -0.3191 | -0.41453 | -0.29626 | -0.32471 | -0.30328 | 0.35497 | 0.32537 | 0.41977 | 0.56452 | -0.7695 | -0.8343 | -0.67967 | -0.74447
2208.3594 | 121.5683 | -0.58136 | 121.019 | -0.22153 | -0.33357 | -0.2684 | -0.30888 | -0.23383 | -0.26695 | -0.36945 | -0.4603 | -0.35119 | -0.37048 | -0.35363 | 0.31835 | 0.27959 | 0.38773 | 0.51874 | -0.17575 | -0.28779 | -0.22263 | -0.26311 | -0.18806 | -0.22118 | -0.32368 | -0.41453 | -0.30542 | -0.32471 | -0.30786 | 0.36412 | 0.32537 | 0.4335 | 0.56452 | -0.77865 | -0.84803 | -0.68883 | -0.75821
2210.0625 | 121.6141 | -0.53558 | 120.9732 | -0.22611 | -0.33814 | -0.27298 | -0.31346 | -0.23841 | -0.2578 | -0.3603 | -0.46488 | -0.33746 | -0.37506 | -0.34905 | 0.30919 | 0.27959 | 0.39231 | 0.52332 | -0.18033 | -0.29237 | -0.2272 | -0.26769 | -0.19264 | -0.21202 | -0.31452 | -0.41911 | -0.29168 | -0.32928 | -0.30328 | 0.35497 | 0.32537 | 0.43808 | 0.56909 | -0.77407 | -0.85719 | -0.68425 | -0.76737
2211.8281 | 121.6507 | -0.50354 | 120.9869 | -0.19864 | -0.31067 | -0.24551 | -0.28599 | -0.20637 | -0.23948 | -0.35114 | -0.43741 | -0.31914 | -0.34759 | -0.33074 | 0.2863 | 0.26128 | 0.36026 | 0.50043 | -0.15286 | -0.26489 | -0.19973 | -0.24022 | -0.16059 | -0.19371 | -0.30537 | -0.39164 | -0.27336 | -0.30181 | -0.28496 | 0.33208 | 0.30705 | 0.40603 | 0.5462 | -0.72371 | -0.79767 | -0.63389 | -0.70785
2213.5938 | 121.5225 | -0.5722 | 121.0098 | -0.21237 | -0.31983 | -0.25467 | -0.29515 | -0.21094 | -0.23948 | -0.3603 | -0.45115 | -0.32372 | -0.3659 | -0.33532 | 0.29546 | 0.27044 | 0.37399 | 0.51416 | -0.16659 | -0.27405 | -0.20889 | -0.24937 | -0.16517 | -0.19371 | -0.31452 | -0.40537 | -0.27794 | -0.32013 | -0.28954 | 0.34123 | 0.31621 | 0.41977 | 0.55994 | -0.7466 | -0.82514 | -0.66136 | -0.7399
2215.3594 | 121.6461 | -0.51727 | 120.9686 | -0.21695 | -0.32441 | -0.25924 | -0.29515 | -0.22468 | -0.24864 | -0.35114 | -0.4603 | -0.33288 | -0.36133 | -0.3399 | 0.30461 | 0.27044 | 0.37857 | 0.50958 | -0.17117 | -0.27863 | -0.21347 | -0.24937 | -0.1789 | -0.20286 | -0.30537 | -0.41453 | -0.2871 | -0.31555 | -0.29412 | 0.35039 | 0.31621 | 0.42435 | 0.55536 | -0.76492 | -0.83887 | -0.66594 | -0.73989
2217.0781 | 121.5729 | -0.55847 | 121.0144 | -0.21237 | -0.32441 | -0.25924 | -0.29973 | -0.22468 | -0.24864 | -0.3603 | -0.45572 | -0.33746 | -0.35675 | -0.34447 | 0.30461 | 0.27959 | 0.38315 | 0.51874 | -0.16659 | -0.27863 | -0.21347 | -0.25395 | -0.1789 | -0.20286 | -0.31452 | -0.40995 | -0.29168 | -0.31097 | -0.2987 | 0.35039 | 0.32537 | 0.42893 | 0.56452 | -0.76034 | -0.83887 | -0.66136 | -0.7399
2218.8594 | 121.637 | -0.52643 | 120.9686 | -0.21695 | -0.33357 | -0.26382 | -0.29973 | -0.22468 | -0.2578 | -0.36488 | -0.4603 | -0.33746 | -0.36133 | -0.35363 | 0.30003 | 0.27959 | 0.38773 | 0.51874 | -0.17117 | -0.28779 | -0.21805 | -0.25395 | -0.1789 | -0.21202 | -0.3191 | -0.41453 | -0.29168 | -0.31555 | -0.30786 | 0.34581 | 0.32537 | 0.4335 | 0.56452 | -0.76034 | -0.84803 | -0.66136 | -0.74905
2220.5625 | 121.5683 | -0.56305 | 121.0052 | -0.21695 | -0.32441 | -0.25924 | -0.30888 | -0.2201 | -0.25322 | -0.36488 | -0.46488 | -0.34203 | -0.3659 | -0.35363 | 0.30461 | 0.27501 | 0.38773 | 0.52332 | -0.17117 | -0.27863 | -0.21347 | -0.26311 | -0.17433 | -0.20744 | -0.3191 | -0.41911 | -0.29626 | -0.32013 | -0.30786 | 0.35039 | 0.32079 | 0.4335 | 0.56909 | -0.7695 | -0.85261 | -0.67052 | -0.75363
2222.3281 | 121.6003 | -0.55389 | 120.9549 | -0.22611 | -0.32899 | -0.26382 | -0.30888 | -0.23841 | -0.26238 | -0.37403 | -0.46488 | -0.34203 | -0.37048 | -0.34905 | 0.30461 | 0.27501 | 0.38773 | 0.51874 | -0.18033 | -0.28321 | -0.21805 | -0.26311 | -0.19264 | -0.2166 | -0.32826 | -0.41911 | -0.29626 | -0.32471 | -0.30328 | 0.35039 | 0.32079 | 0.4335 | 0.56452 | -0.7695 | -0.85261 | -0.6751 | -0.75821
2224.0938 | 121.5042 | -0.58594 | 121.0236 | -0.22153 | -0.31983 | -0.25467 | -0.30888 | -0.22468 | -0.25322 | -0.35572 | -0.4603 | -0.33288 | -0.3659 | -0.3399 | 0.30003 | 0.27044 | 0.38315 | 0.51874 | -0.17575 | -0.27405 | -0.20889 | -0.26311 | -0.1789 | -0.20744 | -0.30994 | -0.41453 | -0.2871 | -0.32013 | -0.29412 | 0.34581 | 0.31621 | 0.42893 | 0.56452 | -0.76034 | -0.84345 | -0.66594 | -0.74905
2225.8594 | 121.6049 | -0.54932 | 120.9595 | -0.22153 | -0.33357 | -0.25924 | -0.3043 | -0.22468 | -0.25322 | -0.36488 | -0.45572 | -0.33288 | -0.3659 | -0.3399 | 0.30461 | 0.27959 | 0.38773 | 0.51874 | -0.17575 | -0.28779 | -0.21347 | -0.25853 | -0.1789 | -0.20744 | -0.3191 | -0.40995 | -0.2871 | -0.32013 | -0.29412 | 0.35039 | 0.32537 | 0.4335 | 0.56452 | -0.76034 | -0.84345 | -0.67052 | -0.75363
2227.625 | 121.5042 | -0.58594 | 120.9595 | -0.21237 | -0.32899 | -0.27298 | -0.3043 | -0.22468 | -0.24864 | -0.36945 | -0.4603 | -0.34661 | -0.37048 | -0.3399 | 0.30919 | 0.27501 | 0.39231 | 0.53248 | -0.16659 | -0.28321 | -0.2272 | -0.25853 | -0.1789 | -0.20286 | -0.32368 | -0.41453 | -0.30084 | -0.32471 | -0.29412 | 0.35497 | 0.32079 | 0.43808 | 0.57825 | -0.7695 | -0.85261 | -0.67967 | -0.76279
2229.4062 | 121.582 | -0.55847 | 120.9686 | -0.21237 | -0.32899 | -0.25924 | -0.31804 | -0.23383 | -0.26238 | -0.36945 | -0.46488 | -0.34203 | -0.37048 | -0.35363 | 0.30919 | 0.27044 | 0.39688 | 0.53248 | -0.16659 | -0.28321 | -0.21347 | -0.27227 | -0.18806 | -0.2166 | -0.32368 | -0.41911 | -0.29626 | -0.32471 | -0.30786 | 0.35497 | 0.31621 | 0.44266 | 0.57825 | -0.77407 | -0.86177 | -0.67967 | -0.76737
2231.1094 | 121.6507 | -0.54932 | 120.932 | -0.22153 | -0.32899 | -0.27298 | -0.31346 | -0.23383 | -0.26238 | -0.36945 | -0.46946 | -0.34203 | -0.37048 | -0.34905 | 0.31377 | 0.27959 | 0.39688 | 0.53248 | -0.17575 | -0.28321 | -0.2272 | -0.26769 | -0.18806 | -0.2166 | -0.32368 | -0.42369 | -0.29626 | -0.32471 | -0.30328 | 0.35955 | 0.32537 | 0.44266 | 0.57825 | -0.78323 | -0.86635 | -0.68425 | -0.76737
2232.875 | 121.5958 | -0.55847 | 120.9412 | -0.22611 | -0.3473 | -0.26382 | -0.30888 | -0.23841 | -0.26238 | -0.36945 | -0.46488 | -0.35577 | -0.37964 | -0.35363 | 0.31377 | 0.28417 | 0.39688 | 0.54163 | -0.18033 | -0.30153 | -0.21805 | -0.26311 | -0.19264 | -0.2166 | -0.32368 | -0.41911 | -0.30999 | -0.33386 | -0.30786 | 0.35955 | 0.32995 | 0.44266 | 0.58741 | -0.77865 | -0.86177 | -0.69341 | -0.77652
2234.5781 | 121.637 | -0.56763 | 120.9137 | -0.22153 | -0.33814 | -0.27756 | -0.30888 | -0.23383 | -0.26695 | -0.36945 | -0.47862 | -0.35577 | -0.37048 | -0.35363 | 0.30919 | 0.28875 | 0.40604 | 0.53705 | -0.17575 | -0.29237 | -0.23178 | -0.26311 | -0.18806 | -0.22118 | -0.32368 | -0.43284 | -0.30999 | -0.32471 | -0.30786 | 0.35497 | 0.33452 | 0.45182 | 0.58283 | -0.78781 | -0.88466 | -0.67967 | -0.77652
2236.3438 | 121.5042 | -0.58594 | 120.9503 | -0.23069 | -0.34272 | -0.27756 | -0.31804 | -0.24299 | -0.26695 | -0.37403 | -0.47862 | -0.35577 | -0.38422 | -0.36279 | 0.31835 | 0.29333 | 0.40604 | 0.54621 | -0.18491 | -0.29695 | -0.23178 | -0.27227 | -0.19722 | -0.22118 | -0.32826 | -0.43284 | -0.30999 | -0.33844 | -0.31701 | 0.36412 | 0.3391 | 0.45182 | 0.59198 | -0.79697 | -0.88466 | -0.70256 | -0.79026
2238.125 | 121.5546 | -0.59052 | 120.9457 | -0.23526 | -0.34272 | -0.28214 | -0.32262 | -0.25215 | -0.27611 | -0.39235 | -0.47404 | -0.36035 | -0.37964 | -0.36737 | 0.32293 | 0.28875 | 0.40604 | 0.55536 | -0.18949 | -0.29695 | -0.23636 | -0.27684 | -0.20637 | -0.23033 | -0.34657 | -0.42826 | -0.31457 | -0.33386 | -0.32159 | 0.3687 | 0.33452 | 0.45182 | 0.60114 | -0.79696 | -0.88008 | -0.70256 | -0.78568
2239.9062 | 121.6278 | -0.5722 | 120.9137 | -0.23069 | -0.35188 | -0.28214 | -0.32262 | -0.25215 | -0.28069 | -0.38319 | -0.47404 | -0.36035 | -0.39337 | -0.36279 | 0.32293 | 0.2979 | 0.4152 | 0.55994 | -0.18491 | -0.3061 | -0.23636 | -0.27684 | -0.20637 | -0.23491 | -0.33741 | -0.42826 | -0.31457 | -0.3476 | -0.31701 | 0.3687 | 0.34368 | 0.46097 | 0.60572 | -0.79696 | -0.88924 | -0.7163 | -0.80857
2241.6719 | 121.6232 | -0.57678 | 120.8954 | -0.23984 | -0.3473 | -0.29587 | -0.3272 | -0.24757 | -0.28069 | -0.39235 | -0.4832 | -0.36493 | -0.38422 | -0.36737 | 0.32293 | 0.30248 | 0.41062 | 0.55994 | -0.19407 | -0.30153 | -0.2501 | -0.28142 | -0.20179 | -0.23491 | -0.34657 | -0.43742 | -0.31915 | -0.33844 | -0.32159 | 0.3687 | 0.34826 | 0.45639 | 0.60572 | -0.80612 | -0.89382 | -0.70714 | -0.79484
2243.4375 | 121.6278 | -0.55847 | 120.9 | -0.23069 | -0.33814 | -0.27756 | -0.31346 | -0.24299 | -0.26695 | -0.37403 | -0.46946 | -0.35119 | -0.37506 | -0.35363 | 0.31377 | 0.28875 | 0.40604 | 0.54163 | -0.18491 | -0.29237 | -0.23178 | -0.26769 | -0.19722 | -0.22118 | -0.32826 | -0.42369 | -0.30542 | -0.32928 | -0.30786 | 0.35955 | 0.33452 | 0.45182 | 0.58741 | -0.78323 | -0.8755 | -0.68883 | -0.7811
2245.1562 | 121.5134 | -0.61798 | 120.9686 | -0.23069 | -0.35188 | -0.28672 | -0.3272 | -0.24757 | -0.27611 | -0.37861 | -0.47862 | -0.36035 | -0.38422 | -0.36279 | 0.31835 | 0.29333 | 0.41978 | 0.55079 | -0.18491 | -0.3061 | -0.24094 | -0.28142 | -0.20179 | -0.23033 | -0.33283 | -0.43284 | -0.31457 | -0.33844 | -0.31701 | 0.36412 | 0.3391 | 0.46555 | 0.59656 | -0.79697 | -0.89839 | -0.70256 | -0.80399
2246.9219 | 121.5729 | -0.59052 | 120.9366 | -0.23984 | -0.35646 | -0.28672 | -0.3272 | -0.25215 | -0.28527 | -0.38319 | -0.47862 | -0.36035 | -0.3888 | -0.37653 | 0.3275 | 0.29333 | 0.41978 | 0.55994 | -0.19407 | -0.31068 | -0.24094 | -0.28142 | -0.20637 | -0.23949 | -0.33741 | -0.43284 | -0.31457 | -0.34302 | -0.33075 | 0.37328 | 0.3391 | 0.46555 | 0.60572 | -0.80612 | -0.89839 | -0.7163 | -0.80857
2248.625 | 121.5042 | -0.61798 | 120.9412 | -0.23984 | -0.35646 | -0.29587 | -0.3272 | -0.25672 | -0.28069 | -0.38777 | -0.4832 | -0.36035 | -0.39337 | -0.36737 | 0.32293 | 0.30706 | 0.42893 | 0.56452 | -0.19407 | -0.31068 | -0.2501 | -0.28142 | -0.21095 | -0.23491 | -0.34199 | -0.43742 | -0.31457 | -0.3476 | -0.32159 | 0.3687 | 0.35284 | 0.47471 | 0.6103 | -0.80612 | -0.91213 | -0.7163 | -0.82231
2250.4062 | 121.5271 | -0.61798 | 120.9366 | -0.24442 | -0.35646 | -0.29129 | -0.33636 | -0.25215 | -0.28069 | -0.39692 | -0.4832 | -0.36035 | -0.39795 | -0.37653 | 0.33208 | 0.30706 | 0.42893 | 0.57368 | -0.19864 | -0.31068 | -0.24552 | -0.29058 | -0.20637 | -0.23491 | -0.35115 | -0.43742 | -0.31457 | -0.35218 | -0.33075 | 0.37786 | 0.35284 | 0.47471 | 0.61945 | -0.81528 | -0.91213 | -0.73003 | -0.82688
2252.125 | 121.4905 | -0.63171 | 120.9366 | -0.249 | -0.35188 | -0.28672 | -0.33178 | -0.25215 | -0.28069 | -0.38777 | -0.4832 | -0.36035 | -0.39795 | -0.37195 | 0.3275 | 0.30248 | 0.42893 | 0.55536 | -0.20322 | -0.3061 | -0.24094 | -0.286 | -0.20637 | -0.23491 | -0.34199 | -0.43742 | -0.31457 | -0.35218 | -0.32617 | 0.37328 | 0.34826 | 0.47471 | 0.60114 | -0.8107 | -0.91213 | -0.72545 | -0.82688
2253.9062 | 121.5408 | -0.6134 | 120.8771 | -0.249 | -0.36562 | -0.28214 | -0.33178 | -0.25672 | -0.28527 | -0.39235 | -0.48778 | -0.36493 | -0.3888 | -0.37653 | 0.3275 | 0.30248 | 0.42435 | 0.56452 | -0.20322 | -0.31984 | -0.23636 | -0.286 | -0.21095 | -0.23949 | -0.34657 | -0.442 | -0.31915 | -0.34302 | -0.33075 | 0.37328 | 0.34826 | 0.47013 | 0.6103 | -0.81528 | -0.91213 | -0.7163 | -0.81315
2255.625 | 121.4859 | -0.62714 | 120.9183 | -0.24442 | -0.36104 | -0.28214 | -0.3272 | -0.25215 | -0.28069 | -0.38777 | -0.48778 | -0.36493 | -0.39337 | -0.37195 | 0.33208 | 0.30706 | 0.42893 | 0.57826 | -0.19864 | -0.31526 | -0.23636 | -0.28142 | -0.20637 | -0.23491 | -0.34199 | -0.442 | -0.31915 | -0.3476 | -0.32617 | 0.37786 | 0.35284 | 0.47471 | 0.62403 | -0.81986 | -0.91671 | -0.72545 | -0.82231
2257.3906 | 121.4996 | -0.63629 | 120.9091 | -0.249 | -0.36104 | -0.29129 | -0.33178 | -0.25672 | -0.28069 | -0.39692 | -0.4832 | -0.36951 | -0.39795 | -0.37653 | 0.33666 | 0.30706 | 0.43809 | 0.57368 | -0.20322 | -0.31526 | -0.24552 | -0.286 | -0.21095 | -0.23491 | -0.35115 | -0.43742 | -0.32373 | -0.35218 | -0.33075 | 0.38244 | 0.35284 | 0.48386 | 0.61945 | -0.81986 | -0.92129 | -0.73461 | -0.83604
2259.1094 | 121.5271 | -0.63171 | 120.8862 | -0.25358 | -0.3702 | -0.30045 | -0.34551 | -0.26588 | -0.299 | -0.4015 | -0.50151 | -0.37866 | -0.40253 | -0.38569 | 0.34582 | 0.31622 | 0.43351 | 0.58283 | -0.2078 | -0.32442 | -0.25468 | -0.29974 | -0.2201 | -0.25323 | -0.35573 | -0.45573 | -0.33289 | -0.35675 | -0.33991 | 0.39159 | 0.36199 | 0.47929 | 0.62861 | -0.84733 | -0.93502 | -0.74835 | -0.83604
2260.8906 | 121.4951 | -0.65918 | 120.8725 | -0.26273 | -0.37477 | -0.30961 | -0.35009 | -0.27046 | -0.299 | -0.41066 | -0.51067 | -0.38782 | -0.41626 | -0.38569 | 0.3504 | 0.32537 | 0.44267 | 0.59657 | -0.21696 | -0.329 | -0.26383 | -0.30431 | -0.22468 | -0.25323 | -0.36488 | -0.46489 | -0.34205 | -0.37049 | -0.33991 | 0.39617 | 0.37115 | 0.48844 | 0.64235 | -0.86106 | -0.95334 | -0.76666 | -0.85893
2262.6562 | 121.5454 | -0.62714 | 120.8954 | -0.26731 | -0.38851 | -0.30961 | -0.35925 | -0.27961 | -0.30358 | -0.41066 | -0.50609 | -0.3924 | -0.42084 | -0.39942 | 0.35497 | 0.32995 | 0.45182 | 0.59199 | -0.22154 | -0.34274 | -0.26383 | -0.31347 | -0.23384 | -0.2578 | -0.36488 | -0.46031 | -0.34663 | -0.37507 | -0.35365 | 0.40075 | 0.37573 | 0.4976 | 0.63777 | -0.86106 | -0.95791 | -0.77582 | -0.87267
2264.4219 | 121.5775 | -0.63171 | 120.8359 | -0.28105 | -0.39309 | -0.32334 | -0.35467 | -0.27504 | -0.31732 | -0.41981 | -0.51525 | -0.3924 | -0.42542 | -0.39942 | 0.36413 | 0.33453 | 0.46098 | 0.60572 | -0.23527 | -0.34731 | -0.27757 | -0.30889 | -0.22926 | -0.27154 | -0.37404 | -0.46947 | -0.34663 | -0.37965 | -0.35365 | 0.40991 | 0.3803 | 0.50676 | 0.6515 | -0.87938 | -0.97623 | -0.78955 | -0.8864
2266.2031 | 121.4905 | -0.68207 | 120.8725 | -0.27189 | -0.39309 | -0.31877 | -0.3684 | -0.28419 | -0.31274 | -0.42439 | -0.51067 | -0.39698 | -0.41626 | -0.40858 | 0.36413 | 0.33453 | 0.47014 | 0.6103 | -0.22611 | -0.34731 | -0.27299 | -0.32263 | -0.23842 | -0.26696 | -0.37862 | -0.46489 | -0.3512 | -0.37049 | -0.36281 | 0.40991 | 0.3803 | 0.51591 | 0.65608 | -0.8748 | -0.9808 | -0.78039 | -0.8864
2267.9062 | 121.5271 | -0.6546 | 120.8496 | -0.28105 | -0.39767 | -0.32792 | -0.36383 | -0.28419 | -0.31274 | -0.42439 | -0.5244 | -0.40156 | -0.42542 | -0.40858 | 0.36413 | 0.34369 | 0.47014 | 0.61488 | -0.23527 | -0.35189 | -0.28215 | -0.31805 | -0.23842 | -0.26696 | -0.37862 | -0.47863 | -0.35578 | -0.37965 | -0.36281 | 0.40991 | 0.38946 | 0.51591 | 0.66066 | -0.88853 | -0.99454 | -0.78955 | -0.89556
2269.6875 | 121.4767 | -0.67291 | 120.9045 | -0.27647 | -0.39309 | -0.3325 | -0.36383 | -0.29335 | -0.31732 | -0.41981 | -0.5244 | -0.3924 | -0.42542 | -0.41316 | 0.36413 | 0.34369 | 0.46556 | 0.6103 | -0.23069 | -0.34731 | -0.28673 | -0.31805 | -0.24757 | -0.27154 | -0.37404 | -0.47863 | -0.34663 | -0.37965 | -0.36739 | 0.40991 | 0.38946 | 0.51134 | 0.65608 | -0.88853 | -0.98996 | -0.78955 | -0.89098
2271.4531 | 121.5637 | -0.67749 | 120.8359 | -0.28105 | -0.40225 | -0.3325 | -0.37756 | -0.29335 | -0.32189 | -0.42897 | -0.51982 | -0.40156 | -0.43 | -0.40858 | 0.35955 | 0.34369 | 0.47472 | 0.61488 | -0.23527 | -0.35647 | -0.28673 | -0.33178 | -0.24757 | -0.27612 | -0.3832 | -0.47405 | -0.35578 | -0.38422 | -0.36281 | 0.40533 | 0.38946 | 0.52049 | 0.66066 | -0.87938 | -0.99454 | -0.78955 | -0.90472
2273.1562 | 121.6049 | -0.63629 | 120.7993 | -0.28105 | -0.41141 | -0.33708 | -0.3684 | -0.3025 | -0.32189 | -0.43813 | -0.5244 | -0.41072 | -0.43458 | -0.41774 | 0.37786 | 0.33911 | 0.4793 | 0.62862 | -0.23527 | -0.36563 | -0.2913 | -0.32263 | -0.25673 | -0.27612 | -0.39235 | -0.47863 | -0.36494 | -0.3888 | -0.37196 | 0.42364 | 0.38488 | 0.52507 | 0.67439 | -0.90227 | -1.0037 | -0.81244 | -0.91387
2274.9219 | 121.6187 | -0.65002 | 120.7993 | -0.2902 | -0.40683 | -0.3325 | -0.37756 | -0.3025 | -0.33563 | -0.43355 | -0.53356 | -0.41987 | -0.43458 | -0.41774 | 0.37786 | 0.35284 | 0.4793 | 0.62404 | -0.24443 | -0.36105 | -0.28673 | -0.33178 | -0.25673 | -0.28985 | -0.38777 | -0.48778 | -0.3741 | -0.3888 | -0.37196 | 0.42364 | 0.39862 | 0.52507 | 0.66981 | -0.91142 | -1.0129 | -0.81244 | -0.91387
2276.6875 | 121.4676 | -0.69122 | 120.8176 | -0.28105 | -0.40225 | -0.33708 | -0.3684 | -0.29793 | -0.32189 | -0.42897 | -0.5244 | -0.41072 | -0.43 | -0.41316 | 0.37329 | 0.34826 | 0.47472 | 0.61946 | -0.23527 | -0.35647 | -0.2913 | -0.32263 | -0.25215 | -0.27612 | -0.3832 | -0.47863 | -0.36494 | -0.38422 | -0.36739 | 0.41906 | 0.39404 | 0.52049 | 0.66524 | -0.89769 | -0.99912 | -0.80329 | -0.90472
2278.4688 | 121.5134 | -0.68207 | 120.8542 | -0.28105 | -0.40225 | -0.3325 | -0.36383 | -0.28419 | -0.31732 | -0.42439 | -0.5244 | -0.41072 | -0.42542 | -0.41316 | 0.36871 | 0.34369 | 0.4793 | 0.62404 | -0.23527 | -0.35647 | -0.28673 | -0.31805 | -0.23842 | -0.27154 | -0.37862 | -0.47863 | -0.36494 | -0.37965 | -0.36739 | 0.41448 | 0.38946 | 0.52507 | 0.66981 | -0.89311 | -1.0037 | -0.79413 | -0.90472
2280.25 | 121.5912 | -0.62714 | 120.813 | -0.27647 | -0.38393 | -0.31877 | -0.36383 | -0.28419 | -0.31732 | -0.41066 | -0.5244 | -0.4153 | -0.43458 | -0.41316 | 0.37329 | 0.33911 | 0.4793 | 0.61946 | -0.23069 | -0.33816 | -0.27299 | -0.31805 | -0.23842 | -0.27154 | -0.36488 | -0.47863 | -0.36952 | -0.3888 | -0.36739 | 0.41906 | 0.38488 | 0.52507 | 0.66524 | -0.89769 | -1.0037 | -0.80786 | -0.91387
2281.9531 | 121.4584 | -0.67749 | 120.8633 | -0.26731 | -0.37935 | -0.31419 | -0.36383 | -0.27961 | -0.30816 | -0.40608 | -0.52898 | -0.4153 | -0.42542 | -0.41316 | 0.36871 | 0.34826 | 0.4793 | 0.62404 | -0.22154 | -0.33358 | -0.26841 | -0.31805 | -0.23384 | -0.26238 | -0.3603 | -0.48321 | -0.36952 | -0.37965 | -0.36739 | 0.41448 | 0.39404 | 0.52507 | 0.66981 | -0.89769 | -1.0083 | -0.79413 | -0.90472
2283.7344 | 121.463 | -0.69122 | 120.8588 | -0.27647 | -0.38393 | -0.30961 | -0.36383 | -0.28419 | -0.30816 | -0.41524 | -0.52898 | -0.41987 | -0.43458 | -0.42232 | 0.37329 | 0.35284 | 0.4793 | 0.61946 | -0.23069 | -0.33816 | -0.26383 | -0.31805 | -0.23842 | -0.26238 | -0.36946 | -0.48321 | -0.3741 | -0.3888 | -0.37654 | 0.41906 | 0.39862 | 0.52507 | 0.66524 | -0.90227 | -1.0083 | -0.80786 | -0.91387
2285.5156 | 121.4401 | -0.68207 | 120.8267 | -0.27189 | -0.38851 | -0.32334 | -0.36383 | -0.29335 | -0.30816 | -0.41981 | -0.54272 | -0.4153 | -0.44373 | -0.42232 | 0.37786 | 0.35284 | 0.4793 | 0.62862 | -0.22611 | -0.34274 | -0.27757 | -0.31805 | -0.24757 | -0.26238 | -0.37404 | -0.49694 | -0.36952 | -0.39796 | -0.37654 | 0.42364 | 0.39862 | 0.52507 | 0.67439 | -0.92058 | -1.022 | -0.8216 | -0.92303
2287.2969 | 121.5912 | -0.63629 | 120.7581 | -0.28105 | -0.39767 | -0.33708 | -0.3684 | -0.29793 | -0.32189 | -0.42897 | -0.53814 | -0.41987 | -0.43458 | -0.42232 | 0.37329 | 0.34826 | 0.48845 | 0.62862 | -0.23527 | -0.35189 | -0.2913 | -0.32263 | -0.25215 | -0.27612 | -0.3832 | -0.49236 | -0.3741 | -0.3888 | -0.37654 | 0.41906 | 0.39404 | 0.53423 | 0.67439 | -0.91142 | -1.0266 | -0.80786 | -0.92303
2289.0781 | 121.4813 | -0.68665 | 120.8313 | -0.26731 | -0.37935 | -0.32334 | -0.35467 | -0.28877 | -0.31274 | -0.41066 | -0.52898 | -0.41072 | -0.43916 | -0.41316 | 0.36871 | 0.34369 | 0.48387 | 0.62404 | -0.22154 | -0.33358 | -0.27757 | -0.30889 | -0.24299 | -0.26696 | -0.36488 | -0.48321 | -0.36494 | -0.39338 | -0.36739 | 0.41448 | 0.38946 | 0.52965 | 0.66981 | -0.89769 | -1.0129 | -0.80786 | -0.92303
2290.7969 | 121.5637 | -0.6546 | 120.7947 | -0.29478 | -0.40683 | -0.33708 | -0.37756 | -0.31166 | -0.33105 | -0.44271 | -0.54272 | -0.42445 | -0.43916 | -0.43148 | 0.38244 | 0.35742 | 0.49303 | 0.63777 | -0.24901 | -0.36105 | -0.2913 | -0.33178 | -0.26588 | -0.28527 | -0.39693 | -0.49694 | -0.37868 | -0.39338 | -0.3857 | 0.42822 | 0.40319 | 0.53881 | 0.68355 | -0.92516 | -1.0357 | -0.8216 | -0.93219
2292.5781 | 121.5454 | -0.67291 | 120.7764 | -0.29478 | -0.41598 | -0.34166 | -0.38214 | -0.3025 | -0.33105 | -0.43813 | -0.53814 | -0.41987 | -0.43916 | -0.42232 | 0.37786 | 0.35284 | 0.48387 | 0.64235 | -0.24901 | -0.37021 | -0.29588 | -0.33636 | -0.25673 | -0.28527 | -0.39235 | -0.49236 | -0.3741 | -0.39338 | -0.37654 | 0.42364 | 0.39862 | 0.52965 | 0.68813 | -0.916 | -1.022 | -0.81702 | -0.92303
2294.3594 | 121.6049 | -0.6546 | 120.7901 | -0.29478 | -0.41598 | -0.35082 | -0.37756 | -0.31166 | -0.33563 | -0.44271 | -0.54729 | -0.41987 | -0.44831 | -0.42232 | 0.38244 | 0.35742 | 0.49761 | 0.64235 | -0.24901 | -0.37021 | -0.30504 | -0.33178 | -0.26588 | -0.28985 | -0.39693 | -0.50152 | -0.3741 | -0.40254 | -0.37654 | 0.42822 | 0.40319 | 0.54338 | 0.68813 | -0.92974 | -1.0449 | -0.83076 | -0.94592
2296.1562 | 121.5729 | -0.66376 | 120.7489 | -0.30394 | -0.42056 | -0.35082 | -0.39587 | -0.31166 | -0.33563 | -0.43813 | -0.55187 | -0.42903 | -0.45289 | -0.43148 | 0.38702 | 0.36657 | 0.50219 | 0.65151 | -0.25816 | -0.37479 | -0.30504 | -0.3501 | -0.26588 | -0.28985 | -0.39235 | -0.5061 | -0.38326 | -0.40712 | -0.3857 | 0.4328 | 0.41235 | 0.54796 | 0.69728 | -0.93889 | -1.0541 | -0.83991 | -0.95508
2297.9375 | 121.4447 | -0.70953 | 120.7855 | -0.29936 | -0.42056 | -0.3554 | -0.38672 | -0.31624 | -0.34021 | -0.45186 | -0.55187 | -0.43819 | -0.45289 | -0.43606 | 0.3916 | 0.37573 | 0.50677 | 0.65151 | -0.25359 | -0.37479 | -0.30962 | -0.34094 | -0.27046 | -0.29443 | -0.40609 | -0.5061 | -0.39241 | -0.40712 | -0.39028 | 0.43737 | 0.42151 | 0.55254 | 0.69728 | -0.94347 | -1.0586 | -0.84449 | -0.95966
2299.6406 | 121.4767 | -0.71869 | 120.7855 | -0.3131 | -0.4343 | -0.35997 | -0.39587 | -0.31624 | -0.34021 | -0.45644 | -0.56103 | -0.43819 | -0.46205 | -0.44063 | 0.39618 | 0.362 | 0.51134 | 0.66524 | -0.26732 | -0.38852 | -0.3142 | -0.3501 | -0.27046 | -0.29443 | -0.41066 | -0.51525 | -0.39241 | -0.41627 | -0.39486 | 0.44195 | 0.40777 | 0.55712 | 0.71102 | -0.95721 | -1.0724 | -0.85822 | -0.97339
2301.3438 | 121.55 | -0.6546 | 120.7443 | -0.29478 | -0.41141 | -0.34624 | -0.3913 | -0.31624 | -0.34021 | -0.44728 | -0.54729 | -0.42903 | -0.44831 | -0.4269 | 0.3916 | 0.35742 | 0.49761 | 0.65151 | -0.24901 | -0.36563 | -0.30046 | -0.34552 | -0.27046 | -0.29443 | -0.40151 | -0.50152 | -0.38326 | -0.40254 | -0.38112 | 0.43737 | 0.40319 | 0.54338 | 0.69728 | -0.93889 | -1.0449 | -0.83991 | -0.94592
2303.125 | 121.5729 | -0.66376 | 120.7901 | -0.2902 | -0.40683 | -0.33708 | -0.37756 | -0.3025 | -0.33105 | -0.43355 | -0.55187 | -0.42903 | -0.44373 | -0.4269 | 0.38702 | 0.35742 | 0.50677 | 0.65151 | -0.24443 | -0.36105 | -0.2913 | -0.33178 | -0.25673 | -0.28527 | -0.38777 | -0.5061 | -0.38326 | -0.39796 | -0.38112 | 0.4328 | 0.40319 | 0.55254 | 0.69728 | -0.93889 | -1.0586 | -0.83075 | -0.9505
2304.9062 | 121.5271 | -0.68665 | 120.7352 | -0.29936 | -0.41141 | -0.34166 | -0.37756 | -0.30708 | -0.33105 | -0.43813 | -0.55645 | -0.43819 | -0.44831 | -0.44063 | 0.3916 | 0.36657 | 0.50677 | 0.66066 | -0.25359 | -0.36563 | -0.29588 | -0.33178 | -0.26131 | -0.28527 | -0.39235 | -0.51068 | -0.39241 | -0.40254 | -0.39486 | 0.43737 | 0.41235 | 0.55254 | 0.70644 | -0.94805 | -1.0632 | -0.83991 | -0.95508
2306.6875 | 121.4859 | -0.70496 | 120.7764 | -0.29478 | -0.41141 | -0.34624 | -0.37298 | -0.31624 | -0.33105 | -0.43355 | -0.56103 | -0.43819 | -0.45289 | -0.43148 | 0.3916 | 0.36657 | 0.51134 | 0.65609 | -0.24901 | -0.36563 | -0.30046 | -0.32721 | -0.27046 | -0.28527 | -0.38777 | -0.51525 | -0.39241 | -0.40712 | -0.3857 | 0.43737 | 0.41235 | 0.55712 | 0.70186 | -0.95263 | -1.0724 | -0.84449 | -0.96423
2308.4062 | 121.4447 | -0.71411 | 120.7855 | -0.2902 | -0.40683 | -0.34624 | -0.37298 | -0.30708 | -0.33563 | -0.43813 | -0.54729 | -0.43819 | -0.44831 | -0.42232 | 0.38244 | 0.36657 | 0.51134 | 0.65609 | -0.24443 | -0.36105 | -0.30046 | -0.32721 | -0.26131 | -0.28985 | -0.39235 | -0.50152 | -0.39241 | -0.40254 | -0.37654 | 0.42822 | 0.41235 | 0.55712 | 0.70186 | -0.92974 | -1.0586 | -0.83076 | -0.95966
2310.1875 | 121.5225 | -0.67291 | 120.726 | -0.29478 | -0.40683 | -0.34166 | -0.37298 | -0.3025 | -0.33105 | -0.43355 | -0.55645 | -0.42903 | -0.44831 | -0.43606 | 0.3916 | 0.37115 | 0.51134 | 0.65609 | -0.24901 | -0.36105 | -0.29588 | -0.32721 | -0.25673 | -0.28527 | -0.38777 | -0.51068 | -0.38326 | -0.40254 | -0.39028 | 0.43737 | 0.41693 | 0.55712 | 0.70186 | -0.94805 | -1.0678 | -0.83991 | -0.95966
2311.9688 | 121.5637 | -0.67291 | 120.7169 | -0.30394 | -0.42056 | -0.35082 | -0.37756 | -0.30708 | -0.34021 | -0.44728 | -0.55187 | -0.43819 | -0.46205 | -0.43606 | 0.39618 | 0.37115 | 0.51592 | 0.66982 | -0.25816 | -0.37479 | -0.30504 | -0.33178 | -0.26131 | -0.29443 | -0.40151 | -0.5061 | -0.39241 | -0.41627 | -0.39028 | 0.44195 | 0.41693 | 0.5617 | 0.7156 | -0.94805 | -1.0678 | -0.85822 | -0.97797
2313.6875 | 121.5134 | -0.70038 | 120.7535 | -0.30394 | -0.42056 | -0.35082 | -0.38214 | -0.31166 | -0.34936 | -0.43813 | -0.55645 | -0.43819 | -0.46205 | -0.43148 | 0.38702 | 0.37115 | 0.51592 | 0.66982 | -0.25816 | -0.37479 | -0.30504 | -0.33636 | -0.26588 | -0.30359 | -0.39235 | -0.51068 | -0.39241 | -0.41627 | -0.3857 | 0.4328 | 0.41693 | 0.5617 | 0.7156 | -0.94347 | -1.0724 | -0.84907 | -0.97797
2315.4688 | 121.5546 | -0.68207 | 120.7123 | -0.29478 | -0.41598 | -0.35082 | -0.38214 | -0.31166 | -0.34021 | -0.43813 | -0.55645 | -0.43819 | -0.45747 | -0.43606 | 0.3916 | 0.362 | 0.51592 | 0.66524 | -0.24901 | -0.37021 | -0.30504 | -0.33636 | -0.26588 | -0.29443 | -0.39235 | -0.51068 | -0.39241 | -0.41169 | -0.39028 | 0.43737 | 0.40777 | 0.5617 | 0.71102 | -0.94805 | -1.0724 | -0.84907 | -0.97339
2317.1875 | 121.4905 | -0.71869 | 120.7443 | -0.2902 | -0.40225 | -0.3554 | -0.38672 | -0.3025 | -0.34021 | -0.42897 | -0.54729 | -0.43361 | -0.45289 | -0.4269 | 0.38702 | 0.36657 | 0.51592 | 0.66524 | -0.24443 | -0.35647 | -0.30962 | -0.34094 | -0.25673 | -0.29443 | -0.3832 | -0.50152 | -0.38783 | -0.40712 | -0.38112 | 0.4328 | 0.41235 | 0.5617 | 0.71102 | -0.93432 | -1.0632 | -0.83991 | -0.96881
2318.9531 | 121.5134 | -0.69122 | 120.7397 | -0.2902 | -0.41141 | -0.34624 | -0.38214 | -0.30708 | -0.33563 | -0.43813 | -0.54729 | -0.42903 | -0.45747 | -0.43148 | 0.38702 | 0.362 | 0.51592 | 0.66982 | -0.24443 | -0.36563 | -0.30046 | -0.33636 | -0.26131 | -0.28985 | -0.39235 | -0.50152 | -0.38326 | -0.41169 | -0.3857 | 0.4328 | 0.40777 | 0.5617 | 0.7156 | -0.93432 | -1.0632 | -0.84449 | -0.97339
2320.7344 | 121.5271 | -0.71869 | 120.7214 | -0.30394 | -0.41141 | -0.35082 | -0.38214 | -0.31166 | -0.34021 | -0.42897 | -0.55187 | -0.43819 | -0.45289 | -0.43148 | 0.3916 | 0.36657 | 0.51592 | 0.66524 | -0.25816 | -0.36563 | -0.30504 | -0.33636 | -0.26588 | -0.29443 | -0.3832 | -0.5061 | -0.39241 | -0.40712 | -0.3857 | 0.43737 | 0.41235 | 0.5617 | 0.71102 | -0.94347 | -1.0678 | -0.84449 | -0.96881
2322.5 | 121.4905 | -0.72327 | 120.726 | -0.29936 | -0.42056 | -0.36455 | -0.3913 | -0.31624 | -0.34021 | -0.43355 | -0.55645 | -0.44277 | -0.46205 | -0.44063 | 0.39618 | 0.362 | 0.52508 | 0.66982 | -0.25359 | -0.37479 | -0.31878 | -0.34552 | -0.27046 | -0.29443 | -0.38777 | -0.51068 | -0.39699 | -0.41627 | -0.39486 | 0.44195 | 0.40777 | 0.57086 | 0.7156 | -0.95263 | -1.0815 | -0.85822 | -0.98713
2324.2188 | 121.5271 | -0.63629 | 120.7718 | -0.25816 | -0.37477 | -0.30961 | -0.34093 | -0.27504 | -0.299 | -0.4015 | -0.51067 | -0.39698 | -0.41626 | -0.39484 | 0.3504 | 0.32995 | 0.4793 | 0.62404 | -0.21238 | -0.329 | -0.26383 | -0.29516 | -0.22926 | -0.25323 | -0.35573 | -0.46489 | -0.3512 | -0.37049 | -0.34907 | 0.39617 | 0.37573 | 0.52507 | 0.66981 | -0.86106 | -0.98996 | -0.76666 | -0.89556
2326 | 121.55 | -0.51727 | 120.8542 | -0.12538 | -0.24199 | -0.18599 | -0.22189 | -0.14228 | -0.16165 | -0.27789 | -0.38247 | -0.26877 | -0.27892 | -0.26663 | 0.21763 | 0.19261 | 0.36941 | 0.50501 | -0.079606 | -0.19621 | -0.14021 | -0.17612 | -0.0965 | -0.11587 | -0.23212 | -0.33669 | -0.223 | -0.23314 | -0.22086 | 0.2634 | 0.23838 | 0.41519 | 0.55078 | -0.6001 | -0.75188 | -0.49654 | -0.64833
2327.7656 | 121.4172 | -0.75531 | 120.7443 | -0.3131 | -0.42514 | -0.36913 | -0.40045 | -0.32082 | -0.34936 | -0.45186 | -0.56561 | -0.44735 | -0.46663 | -0.45437 | 0.40991 | 0.38031 | 0.54339 | 0.68813 | -0.26732 | -0.37937 | -0.32336 | -0.35468 | -0.27504 | -0.30359 | -0.40609 | -0.51983 | -0.40157 | -0.42085 | -0.4086 | 0.45569 | 0.42608 | 0.58917 | 0.73391 | -0.97552 | -1.109 | -0.87654 | -1.01
2329.5312 | 121.4172 | -0.75531 | 120.7352 | -0.3131 | -0.4343 | -0.36913 | -0.40045 | -0.33455 | -0.35852 | -0.45186 | -0.57477 | -0.45193 | -0.4712 | -0.44979 | 0.41449 | 0.38947 | 0.53881 | 0.67898 | -0.26732 | -0.38852 | -0.32336 | -0.35468 | -0.28877 | -0.31274 | -0.40609 | -0.52899 | -0.40615 | -0.42543 | -0.40402 | 0.46026 | 0.43524 | 0.58459 | 0.72475 | -0.98925 | -1.1136 | -0.88569 | -1.01
2331.2656 | 121.5088 | -0.6958 | 120.7031 | -0.3131 | -0.42514 | -0.36913 | -0.40045 | -0.32997 | -0.35852 | -0.45186 | -0.56561 | -0.45193 | -0.4712 | -0.44521 | 0.40075 | 0.37573 | 0.53424 | 0.68355 | -0.26732 | -0.37937 | -0.32336 | -0.35468 | -0.2842 | -0.31274 | -0.40609 | -0.51983 | -0.40615 | -0.42543 | -0.39944 | 0.44653 | 0.42151 | 0.58001 | 0.72933 | -0.96636 | -1.0998 | -0.87196 | -1.0054
2333.0469 | 121.5454 | -0.70496 | 120.6619 | -0.3131 | -0.4343 | -0.36913 | -0.39587 | -0.32082 | -0.35394 | -0.46102 | -0.57019 | -0.45193 | -0.47578 | -0.44521 | 0.40533 | 0.38489 | 0.53424 | 0.69271 | -0.26732 | -0.38852 | -0.32336 | -0.3501 | -0.27504 | -0.30817 | -0.41524 | -0.52441 | -0.40615 | -0.43001 | -0.39944 | 0.45111 | 0.43066 | 0.58001 | 0.73849 | -0.97552 | -1.1044 | -0.88111 | -1.01
2334.75 | 121.463 | -0.74158 | 120.6848 | -0.31767 | -0.42972 | -0.36913 | -0.40045 | -0.32997 | -0.35394 | -0.47018 | -0.56561 | -0.44735 | -0.46205 | -0.44979 | 0.40533 | 0.38031 | 0.54339 | 0.68813 | -0.2719 | -0.38394 | -0.32336 | -0.35468 | -0.2842 | -0.30817 | -0.4244 | -0.51983 | -0.40157 | -0.41627 | -0.40402 | 0.45111 | 0.42608 | 0.58917 | 0.73391 | -0.97094 | -1.109 | -0.86738 | -1.0054
2336.5312 | 121.3943 | -0.75989 | 120.7077 | -0.32225 | -0.43888 | -0.36913 | -0.40045 | -0.32997 | -0.34936 | -0.4656 | -0.57019 | -0.44277 | -0.4712 | -0.44063 | 0.40533 | 0.38031 | 0.53881 | 0.69729 | -0.27648 | -0.3931 | -0.32336 | -0.35468 | -0.2842 | -0.30359 | -0.41982 | -0.52441 | -0.39699 | -0.42543 | -0.39486 | 0.45111 | 0.42608 | 0.58459 | 0.74307 | -0.97552 | -1.109 | -0.87654 | -1.01
2338.3125 | 121.4539 | -0.76446 | 120.7031 | -0.31767 | -0.43888 | -0.36913 | -0.40503 | -0.32997 | -0.35852 | -0.46102 | -0.57019 | -0.45193 | -0.4712 | -0.44521 | 0.40533 | 0.38489 | 0.54797 | 0.70187 | -0.2719 | -0.3931 | -0.32336 | -0.35926 | -0.2842 | -0.31274 | -0.41524 | -0.52441 | -0.40615 | -0.42543 | -0.39944 | 0.45111 | 0.43066 | 0.59375 | 0.74764 | -0.97552 | -1.1182 | -0.87654 | -1.0192
2340.0156 | 121.431 | -0.75531 | 120.7169 | -0.30852 | -0.42972 | -0.35082 | -0.3913 | -0.32082 | -0.34021 | -0.44728 | -0.55187 | -0.43819 | -0.46205 | -0.43148 | 0.3916 | 0.37115 | 0.52966 | 0.69729 | -0.26274 | -0.38394 | -0.30504 | -0.34552 | -0.27504 | -0.29443 | -0.40151 | -0.5061 | -0.39241 | -0.41627 | -0.3857 | 0.43737 | 0.41693 | 0.57543 | 0.74307 | -0.94347 | -1.0815 | -0.85365 | -0.9917
2341.7812 | 121.4081 | -0.74158 | 120.7077 | -0.30394 | -0.41598 | -0.35082 | -0.38214 | -0.30708 | -0.34021 | -0.44728 | -0.55187 | -0.42903 | -0.44831 | -0.43148 | 0.38702 | 0.36657 | 0.53424 | 0.67898 | -0.25816 | -0.37021 | -0.30504 | -0.33636 | -0.26131 | -0.29443 | -0.40151 | -0.5061 | -0.38326 | -0.40254 | -0.3857 | 0.4328 | 0.41235 | 0.58001 | 0.72475 | -0.93889 | -1.0861 | -0.83533 | -0.98255
2343.5469 | 121.431 | -0.75073 | 120.726 | -0.30394 | -0.41598 | -0.34624 | -0.38214 | -0.31166 | -0.34021 | -0.43813 | -0.55187 | -0.42445 | -0.45289 | -0.4269 | 0.3916 | 0.35742 | 0.52966 | 0.68813 | -0.25816 | -0.37021 | -0.30046 | -0.33636 | -0.26588 | -0.29443 | -0.39235 | -0.5061 | -0.37868 | -0.40712 | -0.38112 | 0.43737 | 0.40319 | 0.57543 | 0.73391 | -0.94347 | -1.0815 | -0.84449 | -0.98255
2345.3125 | 121.5363 | -0.70038 | 120.6573 | -0.30394 | -0.41598 | -0.3554 | -0.38672 | -0.31624 | -0.34021 | -0.44271 | -0.55187 | -0.43819 | -0.44373 | -0.43148 | 0.39618 | 0.362 | 0.54339 | 0.68355 | -0.25816 | -0.37021 | -0.30962 | -0.34094 | -0.27046 | -0.29443 | -0.39693 | -0.5061 | -0.39241 | -0.39796 | -0.3857 | 0.44195 | 0.40777 | 0.58917 | 0.72933 | -0.94805 | -1.0953 | -0.83991 | -0.98713
2347.0781 | 121.4447 | -0.74158 | 120.6848 | -0.30394 | -0.42514 | -0.35997 | -0.3913 | -0.32082 | -0.35852 | -0.45186 | -0.55645 | -0.44277 | -0.45289 | -0.43606 | 0.40533 | 0.36657 | 0.54339 | 0.70187 | -0.25816 | -0.37937 | -0.3142 | -0.34552 | -0.27504 | -0.31274 | -0.40609 | -0.51068 | -0.39699 | -0.40712 | -0.39028 | 0.45111 | 0.41235 | 0.58917 | 0.74764 | -0.96178 | -1.0998 | -0.85822 | -0.99628
2348.7812 | 121.4584 | -0.737 | 120.6985 | -0.30852 | -0.42972 | -0.3554 | -0.39587 | -0.32082 | -0.34936 | -0.46102 | -0.56561 | -0.44277 | -0.45289 | -0.44063 | 0.40075 | 0.37115 | 0.54339 | 0.69729 | -0.26274 | -0.38394 | -0.30962 | -0.3501 | -0.27504 | -0.30359 | -0.41524 | -0.51983 | -0.39699 | -0.40712 | -0.39486 | 0.44653 | 0.41693 | 0.58917 | 0.74307 | -0.96636 | -1.109 | -0.85365 | -0.99628
2350.5469 | 121.4218 | -0.7782 | 120.6802 | -0.3131 | -0.42514 | -0.36455 | -0.39587 | -0.32082 | -0.34936 | -0.45186 | -0.55645 | -0.43819 | -0.45747 | -0.43606 | 0.39618 | 0.37115 | 0.54339 | 0.69729 | -0.26732 | -0.37937 | -0.31878 | -0.3501 | -0.27504 | -0.30359 | -0.40609 | -0.51068 | -0.39241 | -0.41169 | -0.39028 | 0.44195 | 0.41693 | 0.58917 | 0.74307 | -0.95263 | -1.0998 | -0.85365 | -1.0009
2352.3281 | 121.4264 | -0.74616 | 120.6619 | -0.2902 | -0.41598 | -0.35082 | -0.37756 | -0.30708 | -0.33563 | -0.44271 | -0.54272 | -0.42445 | -0.44831 | -0.4269 | 0.38702 | 0.362 | 0.52966 | 0.67898 | -0.24443 | -0.37021 | -0.30504 | -0.33178 | -0.26131 | -0.28985 | -0.39693 | -0.49694 | -0.37868 | -0.40254 | -0.38112 | 0.4328 | 0.40777 | 0.57543 | 0.72475 | -0.92974 | -1.0724 | -0.83533 | -0.97797
2354.0469 | 121.5317 | -0.68665 | 120.639 | -0.29478 | -0.40683 | -0.34624 | -0.37756 | -0.31166 | -0.34479 | -0.44728 | -0.54729 | -0.42903 | -0.44373 | -0.42232 | 0.38702 | 0.362 | 0.53424 | 0.69271 | -0.24901 | -0.36105 | -0.30046 | -0.33178 | -0.26588 | -0.29901 | -0.40151 | -0.50152 | -0.38326 | -0.39796 | -0.37654 | 0.4328 | 0.40777 | 0.58001 | 0.73849 | -0.93432 | -1.0815 | -0.83075 | -0.97797
2355.8281 | 121.4035 | -0.74158 | 120.694 | -0.29936 | -0.42514 | -0.3554 | -0.37298 | -0.31624 | -0.34021 | -0.45186 | -0.55187 | -0.43819 | -0.45289 | -0.43606 | 0.39618 | 0.36657 | 0.54339 | 0.69271 | -0.25359 | -0.37937 | -0.30962 | -0.32721 | -0.27046 | -0.29443 | -0.40609 | -0.5061 | -0.39241 | -0.40712 | -0.39028 | 0.44195 | 0.41235 | 0.58917 | 0.73849 | -0.94805 | -1.0953 | -0.84907 | -0.99628
2357.5469 | 121.4859 | -0.71411 | 120.6253 | -0.28563 | -0.40683 | -0.34624 | -0.37298 | -0.30708 | -0.32647 | -0.43813 | -0.54272 | -0.41987 | -0.43458 | -0.42232 | 0.38244 | 0.362 | 0.52508 | 0.68355 | -0.23985 | -0.36105 | -0.30046 | -0.32721 | -0.26131 | -0.2807 | -0.39235 | -0.49694 | -0.3741 | -0.3888 | -0.37654 | 0.42822 | 0.40777 | 0.57086 | 0.72933 | -0.92516 | -1.0678 | -0.81702 | -0.95966
2359.3125 | 121.4401 | -0.71869 | 120.7077 | -0.28105 | -0.41598 | -0.34166 | -0.3684 | -0.29335 | -0.32189 | -0.42897 | -0.54272 | -0.42445 | -0.43458 | -0.41316 | 0.37329 | 0.35284 | 0.52966 | 0.68813 | -0.23527 | -0.37021 | -0.29588 | -0.32263 | -0.24757 | -0.27612 | -0.3832 | -0.49694 | -0.37868 | -0.3888 | -0.36739 | 0.41906 | 0.39862 | 0.57543 | 0.73391 | -0.916 | -1.0724 | -0.80786 | -0.96424
2361.0938 | 121.4722 | -0.74158 | 120.6116 | -0.31767 | -0.44346 | -0.37829 | -0.39587 | -0.33913 | -0.35852 | -0.4656 | -0.57477 | -0.4565 | -0.46663 | -0.44521 | 0.41449 | 0.38489 | 0.57086 | 0.72018 | -0.2719 | -0.39768 | -0.33251 | -0.3501 | -0.29335 | -0.31274 | -0.41982 | -0.52899 | -0.41073 | -0.42085 | -0.39944 | 0.46026 | 0.43066 | 0.61664 | 0.76596 | -0.98925 | -1.1456 | -0.88111 | -1.0375
2362.8594 | 121.3989 | -0.7782 | 120.6665 | -0.31767 | -0.4343 | -0.36455 | -0.3913 | -0.32539 | -0.35394 | -0.45644 | -0.56561 | -0.44277 | -0.46663 | -0.43606 | 0.39618 | 0.37115 | 0.55713 | 0.70644 | -0.2719 | -0.38852 | -0.31878 | -0.34552 | -0.27962 | -0.30817 | -0.41066 | -0.51983 | -0.39699 | -0.42085 | -0.39028 | 0.44195 | 0.41693 | 0.6029 | 0.75222 | -0.96179 | -1.1227 | -0.8628 | -1.0238
2364.5781 | 121.3898 | -0.75531 | 120.6573 | -0.3131 | -0.4343 | -0.36455 | -0.38672 | -0.32997 | -0.35394 | -0.45186 | -0.57019 | -0.45193 | -0.46663 | -0.44063 | 0.39618 | 0.36657 | 0.54797 | 0.70187 | -0.26732 | -0.38852 | -0.31878 | -0.34094 | -0.2842 | -0.30817 | -0.40609 | -0.52441 | -0.40615 | -0.42085 | -0.39486 | 0.44195 | 0.41235 | 0.59375 | 0.74764 | -0.96636 | -1.1182 | -0.8628 | -1.0146
2366.3594 | 121.4722 | -0.737 | 120.607 | -0.30852 | -0.42972 | -0.36455 | -0.39587 | -0.32539 | -0.34021 | -0.46102 | -0.55187 | -0.44277 | -0.46205 | -0.43606 | 0.39618 | 0.37115 | 0.56171 | 0.70644 | -0.26274 | -0.38394 | -0.31878 | -0.3501 | -0.27962 | -0.29443 | -0.41524 | -0.5061 | -0.39699 | -0.41627 | -0.39028 | 0.44195 | 0.41693 | 0.60748 | 0.75222 | -0.94805 | -1.1136 | -0.85822 | -1.0238
2368.0625 | 121.4081 | -0.75989 | 120.6573 | -0.3131 | -0.4343 | -0.35997 | -0.3913 | -0.32539 | -0.35394 | -0.45644 | -0.56103 | -0.44735 | -0.46205 | -0.43606 | 0.40533 | 0.37573 | 0.55255 | 0.71102 | -0.26732 | -0.38852 | -0.3142 | -0.34552 | -0.27962 | -0.30817 | -0.41066 | -0.51525 | -0.40157 | -0.41627 | -0.39028 | 0.45111 | 0.42151 | 0.59832 | 0.7568 | -0.96636 | -1.1136 | -0.86738 | -1.0146
2369.8281 | 121.431 | -0.76446 | 120.6528 | -0.3131 | -0.4343 | -0.35997 | -0.39587 | -0.32082 | -0.35394 | -0.45644 | -0.55187 | -0.44735 | -0.46205 | -0.44521 | 0.39618 | 0.37573 | 0.56171 | 0.71102 | -0.26732 | -0.38852 | -0.3142 | -0.3501 | -0.27504 | -0.30817 | -0.41066 | -0.5061 | -0.40157 | -0.41627 | -0.39944 | 0.44195 | 0.42151 | 0.60748 | 0.7568 | -0.94805 | -1.1136 | -0.85822 | -1.0238
2371.5469 | 121.4172 | -0.76446 | 120.6573 | -0.30394 | -0.4343 | -0.3554 | -0.3913 | -0.32082 | -0.35852 | -0.45186 | -0.56103 | -0.44277 | -0.45747 | -0.43606 | 0.3916 | 0.37573 | 0.55713 | 0.71102 | -0.25816 | -0.38852 | -0.30962 | -0.34552 | -0.27504 | -0.31274 | -0.40609 | -0.51525 | -0.39699 | -0.41169 | -0.39028 | 0.43737 | 0.42151 | 0.6029 | 0.7568 | -0.95263 | -1.1182 | -0.84907 | -1.0146
2373.3125 | 121.3623 | -0.76904 | 120.6436 | -0.30394 | -0.42972 | -0.35997 | -0.38214 | -0.31624 | -0.34021 | -0.44728 | -0.55645 | -0.44277 | -0.44831 | -0.43148 | 0.3916 | 0.36657 | 0.55255 | 0.70644 | -0.25816 | -0.38394 | -0.3142 | -0.33636 | -0.27046 | -0.29443 | -0.40151 | -0.51068 | -0.39699 | -0.40254 | -0.3857 | 0.43737 | 0.41235 | 0.59832 | 0.75222 | -0.94805 | -1.109 | -0.83991 | -1.0009
2375.0156 | 121.4996 | -0.72784 | 120.5887 | -0.30852 | -0.42972 | -0.36913 | -0.3913 | -0.32997 | -0.35394 | -0.45644 | -0.55645 | -0.44735 | -0.45289 | -0.44063 | 0.40075 | 0.37115 | 0.56628 | 0.72018 | -0.26274 | -0.38394 | -0.32336 | -0.34552 | -0.2842 | -0.30817 | -0.41066 | -0.51068 | -0.40157 | -0.40712 | -0.39486 | 0.44653 | 0.41693 | 0.61206 | 0.76596 | -0.95721 | -1.1227 | -0.85365 | -1.0192
2376.7969 | 121.4584 | -0.75073 | 120.6436 | -0.30852 | -0.4343 | -0.35997 | -0.38214 | -0.32082 | -0.34936 | -0.45186 | -0.56561 | -0.44277 | -0.45747 | -0.43606 | 0.39618 | 0.362 | 0.56171 | 0.7156 | -0.26274 | -0.38852 | -0.3142 | -0.33636 | -0.27504 | -0.30359 | -0.40609 | -0.51983 | -0.39699 | -0.41169 | -0.39028 | 0.44195 | 0.40777 | 0.60748 | 0.76138 | -0.96179 | -1.1273 | -0.85365 | -1.0192
2378.5781 | 121.4493 | -0.737 | 120.5933 | -0.3131 | -0.4343 | -0.35997 | -0.39587 | -0.31624 | -0.34479 | -0.45186 | -0.55187 | -0.43819 | -0.45289 | -0.43148 | 0.3916 | 0.37573 | 0.55713 | 0.70644 | -0.26732 | -0.38852 | -0.3142 | -0.3501 | -0.27046 | -0.29901 | -0.40609 | -0.5061 | -0.39241 | -0.40712 | -0.3857 | 0.43737 | 0.42151 | 0.6029 | 0.75222 | -0.94347 | -1.109 | -0.84449 | -1.01
2380.3594 | 121.3806 | -0.76904 | 120.6253 | -0.29936 | -0.42056 | -0.34624 | -0.3913 | -0.31166 | -0.34021 | -0.44728 | -0.55187 | -0.43819 | -0.44373 | -0.4269 | 0.3916 | 0.35742 | 0.55713 | 0.71102 | -0.25359 | -0.37479 | -0.30046 | -0.34552 | -0.26588 | -0.29443 | -0.40151 | -0.5061 | -0.39241 | -0.39796 | -0.38112 | 0.43737 | 0.40319 | 0.6029 | 0.7568 | -0.94347 | -1.109 | -0.83533 | -1.0009
2382.1406 | 121.4035 | -0.76904 | 120.6207 | -0.30394 | -0.42514 | -0.34166 | -0.38214 | -0.32082 | -0.33563 | -0.45186 | -0.55187 | -0.43361 | -0.44831 | -0.43148 | 0.3916 | 0.362 | 0.55713 | 0.70187 | -0.25816 | -0.37937 | -0.29588 | -0.33636 | -0.27504 | -0.28985 | -0.40609 | -0.5061 | -0.38783 | -0.40254 | -0.3857 | 0.43737 | 0.40777 | 0.6029 | 0.74764 | -0.94347 | -1.109 | -0.83991 | -1.0054
2383.9062 | 121.4355 | -0.74616 | 120.6162 | -0.30852 | -0.41598 | -0.35082 | -0.38672 | -0.31624 | -0.34021 | -0.45186 | -0.55187 | -0.44277 | -0.45289 | -0.43148 | 0.39618 | 0.362 | 0.56171 | 0.7156 | -0.26274 | -0.37021 | -0.30504 | -0.34094 | -0.27046 | -0.29443 | -0.40609 | -0.5061 | -0.39699 | -0.40712 | -0.3857 | 0.44195 | 0.40777 | 0.60748 | 0.76138 | -0.94805 | -1.1136 | -0.84907 | -1.0146
2385.6719 | 121.344 | -0.79193 | 120.6665 | -0.30394 | -0.42514 | -0.35997 | -0.38214 | -0.31624 | -0.34021 | -0.44728 | -0.55187 | -0.43361 | -0.44831 | -0.43148 | 0.39618 | 0.36657 | 0.55713 | 0.7156 | -0.25816 | -0.37937 | -0.3142 | -0.33636 | -0.27046 | -0.29443 | -0.40151 | -0.5061 | -0.38783 | -0.40254 | -0.3857 | 0.44195 | 0.41235 | 0.6029 | 0.76138 | -0.94805 | -1.109 | -0.84449 | -1.0054
2387.3906 | 121.3669 | -0.76446 | 120.6207 | -0.30852 | -0.4343 | -0.3554 | -0.38672 | -0.31624 | -0.34479 | -0.44271 | -0.55645 | -0.44277 | -0.45747 | -0.43148 | 0.39618 | 0.36657 | 0.55713 | 0.7156 | -0.26274 | -0.38852 | -0.30962 | -0.34094 | -0.27046 | -0.29901 | -0.39693 | -0.51068 | -0.39699 | -0.41169 | -0.3857 | 0.44195 | 0.41235 | 0.6029 | 0.76138 | -0.95263 | -1.1136 | -0.85365 | -1.0146
2389.1719 | 121.4127 | -0.78735 | 120.607 | -0.30394 | -0.42514 | -0.3554 | -0.38672 | -0.31166 | -0.34479 | -0.44271 | -0.55187 | -0.43361 | -0.45289 | -0.4269 | 0.38702 | 0.362 | 0.56628 | 0.7156 | -0.25816 | -0.37937 | -0.30962 | -0.34094 | -0.26588 | -0.29901 | -0.39693 | -0.5061 | -0.38783 | -0.40712 | -0.38112 | 0.4328 | 0.40777 | 0.61206 | 0.76138 | -0.93889 | -1.1182 | -0.83991 | -1.0192
2390.9375 | 121.431 | -0.75531 | 120.5933 | -0.30852 | -0.4343 | -0.35082 | -0.38672 | -0.31624 | -0.34479 | -0.45644 | -0.55645 | -0.43361 | -0.44831 | -0.4269 | 0.39618 | 0.362 | 0.56171 | 0.72476 | -0.26274 | -0.38852 | -0.30504 | -0.34094 | -0.27046 | -0.29901 | -0.41066 | -0.51068 | -0.38783 | -0.40254 | -0.38112 | 0.44195 | 0.40777 | 0.60748 | 0.77053 | -0.95263 | -1.1182 | -0.84449 | -1.01
2392.7188 | 121.4539 | -0.72784 | 120.575 | -0.30852 | -0.42514 | -0.3554 | -0.38214 | -0.32082 | -0.34479 | -0.44728 | -0.55187 | -0.43361 | -0.44831 | -0.43606 | 0.3916 | 0.35742 | 0.56628 | 0.72018 | -0.26274 | -0.37937 | -0.30962 | -0.33636 | -0.27504 | -0.29901 | -0.40151 | -0.5061 | -0.38783 | -0.40254 | -0.39028 | 0.43737 | 0.40319 | 0.61206 | 0.76596 | -0.94347 | -1.1182 | -0.83991 | -1.0146
2394.4219 | 121.3531 | -0.79651 | 120.6253 | -0.30394 | -0.42972 | -0.3554 | -0.38214 | -0.32082 | -0.34021 | -0.44271 | -0.55187 | -0.43361 | -0.44373 | -0.4269 | 0.38702 | 0.36657 | 0.57086 | 0.7156 | -0.25816 | -0.38394 | -0.30962 | -0.33636 | -0.27504 | -0.29443 | -0.39693 | -0.5061 | -0.38783 | -0.39796 | -0.38112 | 0.4328 | 0.41235 | 0.61664 | 0.76138 | -0.93889 | -1.1227 | -0.83075 | -1.0146
2396.2188 | 121.3486 | -0.80109 | 120.6162 | -0.29936 | -0.4343 | -0.3554 | -0.38214 | -0.32082 | -0.34936 | -0.45186 | -0.55645 | -0.44277 | -0.43916 | -0.43148 | 0.3916 | 0.36657 | 0.58002 | 0.72476 | -0.25359 | -0.38852 | -0.30962 | -0.33636 | -0.27504 | -0.30359 | -0.40609 | -0.51068 | -0.39699 | -0.39338 | -0.3857 | 0.43737 | 0.41235 | 0.62579 | 0.77053 | -0.94805 | -1.1365 | -0.83075 | -1.0192
2397.9844 | 121.4493 | -0.75073 | 120.575 | -0.30394 | -0.4343 | -0.35997 | -0.38672 | -0.32539 | -0.34021 | -0.44728 | -0.55645 | -0.44277 | -0.45289 | -0.43148 | 0.3916 | 0.37573 | 0.57086 | 0.72476 | -0.25816 | -0.38852 | -0.3142 | -0.34094 | -0.27962 | -0.29443 | -0.40151 | -0.51068 | -0.39699 | -0.40712 | -0.3857 | 0.43737 | 0.42151 | 0.61664 | 0.77053 | -0.94805 | -1.1273 | -0.84449 | -1.0238
2399.7031 | 121.4447 | -0.74616 | 120.5521 | -0.30852 | -0.42514 | -0.35997 | -0.38672 | -0.32539 | -0.34936 | -0.45186 | -0.56103 | -0.43819 | -0.45289 | -0.43148 | 0.3916 | 0.36657 | 0.57086 | 0.72934 | -0.26274 | -0.37937 | -0.3142 | -0.34094 | -0.27962 | -0.30359 | -0.40609 | -0.51525 | -0.39241 | -0.40712 | -0.3857 | 0.43737 | 0.41235 | 0.61664 | 0.77511 | -0.95263 | -1.1319 | -0.84449 | -1.0238
2401.4844 | 121.3348 | -0.80109 | 120.607 | -0.30394 | -0.42972 | -0.36913 | -0.3913 | -0.31624 | -0.34021 | -0.45186 | -0.55645 | -0.43819 | -0.45747 | -0.43148 | 0.3916 | 0.36657 | 0.58002 | 0.73849 | -0.25816 | -0.38394 | -0.32336 | -0.34552 | -0.27046 | -0.29443 | -0.40609 | -0.51068 | -0.39241 | -0.41169 | -0.3857 | 0.43737 | 0.41235 | 0.62579 | 0.78427 | -0.94805 | -1.1365 | -0.84907 | -1.0375
2403.2656 | 121.4584 | -0.76446 | 120.5566 | -0.29936 | -0.42056 | -0.3554 | -0.38672 | -0.31624 | -0.34479 | -0.44728 | -0.55187 | -0.43819 | -0.44373 | -0.42232 | 0.3916 | 0.36657 | 0.58002 | 0.73849 | -0.25359 | -0.37479 | -0.30962 | -0.34094 | -0.27046 | -0.29901 | -0.40151 | -0.5061 | -0.39241 | -0.39796 | -0.37654 | 0.43737 | 0.41235 | 0.62579 | 0.78427 | -0.94347 | -1.1319 | -0.83533 | -1.0238
2404.9688 | 121.4355 | -0.77362 | 120.5566 | -0.30852 | -0.42972 | -0.35997 | -0.3913 | -0.32539 | -0.34936 | -0.45186 | -0.55645 | -0.44277 | -0.45289 | -0.43606 | 0.3916 | 0.36657 | 0.5846 | 0.73391 | -0.26274 | -0.38394 | -0.3142 | -0.34552 | -0.27962 | -0.30359 | -0.40609 | -0.51068 | -0.39699 | -0.40712 | -0.39028 | 0.43737 | 0.41235 | 0.63037 | 0.77969 | -0.94805 | -1.141 | -0.84449 | -1.0375
2406.7656 | 121.3806 | -0.80566 | 120.5566 | -0.3131 | -0.42972 | -0.35082 | -0.38214 | -0.32082 | -0.34936 | -0.45644 | -0.56103 | -0.43361 | -0.45747 | -0.43606 | 0.38244 | 0.36657 | 0.59376 | 0.74765 | -0.26732 | -0.38394 | -0.30504 | -0.33636 | -0.27504 | -0.30359 | -0.41066 | -0.51525 | -0.38783 | -0.41169 | -0.39028 | 0.42822 | 0.41235 | 0.63953 | 0.79343 | -0.94347 | -1.1548 | -0.83991 | -1.0512
2408.4688 | 121.3394 | -0.80109 | 120.5612 | -0.30852 | -0.42972 | -0.3554 | -0.38672 | -0.33913 | -0.34936 | -0.45186 | -0.55645 | -0.44735 | -0.45289 | -0.43606 | 0.40075 | 0.36657 | 0.59833 | 0.74307 | -0.26274 | -0.38394 | -0.30962 | -0.34094 | -0.29335 | -0.30359 | -0.40609 | -0.51068 | -0.40157 | -0.40712 | -0.39028 | 0.44653 | 0.41235 | 0.64411 | 0.78885 | -0.95721 | -1.1548 | -0.85365 | -1.0512
2410.2344 | 121.376 | -0.81024 | 120.5475 | -0.30394 | -0.42972 | -0.3554 | -0.38672 | -0.31624 | -0.34479 | -0.44271 | -0.56103 | -0.44277 | -0.46205 | -0.43148 | 0.3916 | 0.36657 | 0.59376 | 0.74765 | -0.25816 | -0.38394 | -0.30962 | -0.34094 | -0.27046 | -0.29901 | -0.39693 | -0.51525 | -0.39699 | -0.41627 | -0.3857 | 0.43737 | 0.41235 | 0.63953 | 0.79343 | -0.95263 | -1.1548 | -0.85365 | -1.0558
2412.0156 | 121.3715 | -0.8194 | 120.5338 | -0.30852 | -0.42514 | -0.35997 | -0.38672 | -0.32539 | -0.34021 | -0.44728 | -0.55645 | -0.43819 | -0.45289 | -0.4269 | 0.3916 | 0.362 | 0.59833 | 0.75223 | -0.26274 | -0.37937 | -0.3142 | -0.34094 | -0.27962 | -0.29443 | -0.40151 | -0.51068 | -0.39241 | -0.40712 | -0.38112 | 0.43737 | 0.40777 | 0.64411 | 0.798 | -0.94805 | -1.1548 | -0.84449 | -1.0512
2413.75 | 121.3165 | -0.8194 | 120.5612 | -0.30852 | -0.4343 | -0.36913 | -0.3913 | -0.32539 | -0.34936 | -0.45186 | -0.56103 | -0.44277 | -0.44373 | -0.43606 | 0.3916 | 0.36657 | 0.59833 | 0.7568 | -0.26274 | -0.38852 | -0.32336 | -0.34552 | -0.27962 | -0.30359 | -0.40609 | -0.51525 | -0.39699 | -0.39796 | -0.39028 | 0.43737 | 0.41235 | 0.64411 | 0.80258 | -0.95263 | -1.1594 | -0.83533 | -1.0421
2415.5156 | 121.4401 | -0.78735 | 120.5063 | -0.30852 | -0.42972 | -0.3554 | -0.38672 | -0.32082 | -0.34479 | -0.44728 | -0.55187 | -0.43819 | -0.44831 | -0.4269 | 0.3916 | 0.36657 | 0.61207 | 0.75223 | -0.26274 | -0.38394 | -0.30962 | -0.34094 | -0.27504 | -0.29901 | -0.40151 | -0.5061 | -0.39241 | -0.40254 | -0.38112 | 0.43737 | 0.41235 | 0.65784 | 0.798 | -0.94347 | -1.1639 | -0.83991 | -1.0604
2417.25 | 121.3348 | -0.8194 | 120.5154 | -0.30852 | -0.42514 | -0.3554 | -0.3913 | -0.31624 | -0.33563 | -0.45186 | -0.55187 | -0.44277 | -0.44373 | -0.4269 | 0.3916 | 0.37115 | 0.61207 | 0.76138 | -0.26274 | -0.37937 | -0.30962 | -0.34552 | -0.27046 | -0.28985 | -0.40609 | -0.5061 | -0.39699 | -0.39796 | -0.38112 | 0.43737 | 0.41693 | 0.65784 | 0.80716 | -0.94347 | -1.1639 | -0.83533 | -1.0558
2419.0156 | 121.3257 | -0.8194 | 120.5429 | -0.29936 | -0.42514 | -0.35082 | -0.38672 | -0.32082 | -0.34479 | -0.45186 | -0.54729 | -0.42903 | -0.44373 | -0.43148 | 0.38702 | 0.35742 | 0.60291 | 0.76138 | -0.25359 | -0.37937 | -0.30504 | -0.34094 | -0.27504 | -0.29901 | -0.40609 | -0.50152 | -0.38326 | -0.39796 | -0.3857 | 0.4328 | 0.40319 | 0.64869 | 0.80716 | -0.93432 | -1.1502 | -0.83075 | -1.0466
2420.7969 | 121.3531 | -0.81024 | 120.5338 | -0.29936 | -0.42972 | -0.3554 | -0.38214 | -0.32082 | -0.33105 | -0.43813 | -0.55187 | -0.42903 | -0.44831 | -0.42232 | 0.39618 | 0.37115 | 0.60749 | 0.7568 | -0.25359 | -0.38394 | -0.30962 | -0.33636 | -0.27504 | -0.28527 | -0.39235 | -0.5061 | -0.38326 | -0.40254 | -0.37654 | 0.44195 | 0.41693 | 0.65327 | 0.80258 | -0.94805 | -1.1594 | -0.84449 | -1.0558
2422.5156 | 121.4035 | -0.80109 | 120.488 | -0.29936 | -0.42514 | -0.35082 | -0.38672 | -0.31624 | -0.34021 | -0.44728 | -0.54272 | -0.42445 | -0.44831 | -0.43148 | 0.3916 | 0.362 | 0.61207 | 0.7568 | -0.25359 | -0.37937 | -0.30504 | -0.34094 | -0.27046 | -0.29443 | -0.40151 | -0.49694 | -0.37868 | -0.40254 | -0.3857 | 0.43737 | 0.40777 | 0.65784 | 0.80258 | -0.93432 | -1.1548 | -0.83991 | -1.0604
2424.3125 | 121.4218 | -0.79193 | 120.4697 | -0.30394 | -0.42972 | -0.35082 | -0.38672 | -0.31624 | -0.34936 | -0.44728 | -0.54272 | -0.43819 | -0.44373 | -0.4269 | 0.3916 | 0.35742 | 0.61665 | 0.77512 | -0.25816 | -0.38394 | -0.30504 | -0.34094 | -0.27046 | -0.30359 | -0.40151 | -0.49694 | -0.39241 | -0.39796 | -0.38112 | 0.43737 | 0.40319 | 0.66242 | 0.82089 | -0.93432 | -1.1594 | -0.83533 | -1.0604
2426.0938 | 121.2845 | -0.86517 | 120.5109 | -0.30394 | -0.42972 | -0.36455 | -0.38672 | -0.32539 | -0.34479 | -0.46102 | -0.54729 | -0.43819 | -0.44831 | -0.43606 | 0.3916 | 0.37115 | 0.62123 | 0.77512 | -0.25816 | -0.38394 | -0.31878 | -0.34094 | -0.27962 | -0.29901 | -0.41524 | -0.50152 | -0.39241 | -0.40254 | -0.39028 | 0.43737 | 0.41693 | 0.667 | 0.82089 | -0.93889 | -1.1685 | -0.83991 | -1.0695
2427.875 | 121.3028 | -0.85602 | 120.4788 | -0.3131 | -0.4343 | -0.35997 | -0.3913 | -0.32997 | -0.34936 | -0.46102 | -0.55645 | -0.45193 | -0.45747 | -0.44063 | 0.40075 | 0.36657 | 0.63954 | 0.78427 | -0.26732 | -0.38852 | -0.3142 | -0.34552 | -0.2842 | -0.30359 | -0.41524 | -0.51068 | -0.40615 | -0.41169 | -0.39486 | 0.44653 | 0.41235 | 0.68532 | 0.83005 | -0.95721 | -1.196 | -0.85822 | -1.097
2429.5938 | 121.3943 | -0.83313 | 120.4376 | -0.31767 | -0.44346 | -0.36455 | -0.39587 | -0.32539 | -0.35852 | -0.45644 | -0.56103 | -0.44277 | -0.46205 | -0.43148 | 0.40075 | 0.37115 | 0.63038 | 0.78885 | -0.2719 | -0.39768 | -0.31878 | -0.3501 | -0.27962 | -0.31274 | -0.41066 | -0.51525 | -0.39699 | -0.41627 | -0.3857 | 0.44653 | 0.41693 | 0.67616 | 0.83463 | -0.96179 | -1.1914 | -0.8628 | -1.0924
2431.375 | 121.3715 | -0.82855 | 120.4468 | -0.31767 | -0.44346 | -0.36913 | -0.40045 | -0.32997 | -0.3631 | -0.45644 | -0.56561 | -0.4565 | -0.45747 | -0.43606 | 0.40533 | 0.37573 | 0.64412 | 0.79801 | -0.2719 | -0.39768 | -0.32336 | -0.35468 | -0.2842 | -0.31732 | -0.41066 | -0.51983 | -0.41073 | -0.41169 | -0.39028 | 0.45111 | 0.42151 | 0.68989 | 0.84379 | -0.97094 | -1.2097 | -0.8628 | -1.1016
2433.1094 | 121.4264 | -0.83771 | 120.4193 | -0.3131 | -0.44346 | -0.36455 | -0.40045 | -0.32997 | -0.35394 | -0.45644 | -0.56103 | -0.44735 | -0.45747 | -0.43148 | 0.40533 | 0.38031 | 0.6487 | 0.80259 | -0.26732 | -0.39768 | -0.31878 | -0.35468 | -0.2842 | -0.30817 | -0.41066 | -0.51525 | -0.40157 | -0.41169 | -0.3857 | 0.45111 | 0.42608 | 0.69447 | 0.84836 | -0.96636 | -1.2097 | -0.8628 | -1.1062
2434.875 | 121.2936 | -0.89264 | 120.4697 | -0.31767 | -0.43888 | -0.36913 | -0.39587 | -0.33455 | -0.3631 | -0.4656 | -0.56103 | -0.44735 | -0.45289 | -0.43606 | 0.40533 | 0.37573 | 0.65785 | 0.81632 | -0.2719 | -0.3931 | -0.32336 | -0.3501 | -0.28877 | -0.31732 | -0.41982 | -0.51525 | -0.40157 | -0.40712 | -0.39028 | 0.45111 | 0.42151 | 0.70363 | 0.8621 | -0.96636 | -1.2189 | -0.85822 | -1.1107
2436.6562 | 121.2845 | -0.91095 | 120.4376 | -0.33141 | -0.45261 | -0.38287 | -0.40961 | -0.34371 | -0.36768 | -0.47475 | -0.57934 | -0.46566 | -0.4712 | -0.44521 | 0.41449 | 0.38031 | 0.6899 | 0.83463 | -0.28563 | -0.40684 | -0.33709 | -0.36383 | -0.29793 | -0.3219 | -0.42898 | -0.53357 | -0.41989 | -0.42543 | -0.39944 | 0.46026 | 0.42608 | 0.73568 | 0.88041 | -0.99383 | -1.2692 | -0.88569 | -1.1611
2438.4375 | 121.3211 | -1.4923 | 119.7144 | -0.66105 | -0.77771 | -0.70795 | -0.72095 | -0.66416 | -0.66985 | -0.78607 | -0.90442 | -0.79076 | -0.76421 | -0.74285 | 0.70749 | 0.68704 | 1.3171 | 1.4756 | -0.61528 | -0.73193 | -0.66217 | -0.67517 | -0.61839 | -0.62407 | -0.74029 | -0.85864 | -0.74498 | -0.71844 | -0.69708 | 0.75327 | 0.73282 | 1.3629 | 1.5214 | -1.6119 | -2.2216 | -1.4717 | -2.0814
2440.2188 | 121.3257 | -1.4603 | 119.7372 | -0.50081 | -0.62203 | -0.5477 | -0.56986 | -0.52225 | -0.51876 | -0.63041 | -0.76248 | -0.64424 | -0.5994 | -0.57801 | 0.54268 | 0.52223 | 1.2393 | 1.4023 | -0.45503 | -0.57625 | -0.50192 | -0.52408 | -0.47647 | -0.47299 | -0.58464 | -0.71671 | -0.59846 | -0.55362 | -0.53223 | 0.58845 | 0.56801 | 1.2851 | 1.4481 | -1.3052 | -2.0018 | -1.1421 | -1.8387
2441.9219 | 121.1929 | -1.506 | 119.7189 | -0.43213 | -0.54877 | -0.4836 | -0.51034 | -0.449 | -0.45009 | -0.57547 | -0.68923 | -0.57555 | -0.52156 | -0.50016 | 0.46485 | 0.43982 | 1.2393 | 1.4069 | -0.38636 | -0.50299 | -0.43782 | -0.46456 | -0.40322 | -0.40431 | -0.5297 | -0.64345 | -0.52978 | -0.47579 | -0.45439 | 0.51062 | 0.4856 | 1.2851 | 1.4527 | -1.1541 | -1.9285 | -0.98641 | -1.7609
2443.7031 | 121.2753 | -1.506 | 119.6411 | -0.38635 | -0.4984 | -0.42865 | -0.44624 | -0.39406 | -0.39973 | -0.52053 | -0.64802 | -0.52977 | -0.46663 | -0.44063 | 0.40533 | 0.38031 | 1.2805 | 1.4435 | -0.34057 | -0.45263 | -0.38288 | -0.40046 | -0.34829 | -0.35395 | -0.47476 | -0.60225 | -0.48399 | -0.42085 | -0.39486 | 0.45111 | 0.42608 | 1.3263 | 1.4893 | -1.0534 | -1.9285 | -0.87196 | -1.7471
2445.4688 | 121.2204 | -1.5976 | 119.5541 | -0.36346 | -0.48009 | -0.40576 | -0.44166 | -0.37575 | -0.38599 | -0.50222 | -0.63887 | -0.52061 | -0.44373 | -0.41774 | 0.38244 | 0.35284 | 1.3355 | 1.4939 | -0.31768 | -0.43431 | -0.35998 | -0.39588 | -0.32998 | -0.34021 | -0.45645 | -0.59309 | -0.47483 | -0.39796 | -0.37196 | 0.42822 | 0.39862 | 1.3812 | 1.5397 | -1.0213 | -1.9743 | -0.82618 | -1.7792
2447.1875 | 121.2479 | -1.6708 | 119.4717 | -0.34514 | -0.45719 | -0.3966 | -0.42792 | -0.36202 | -0.36768 | -0.49764 | -0.62513 | -0.50229 | -0.42542 | -0.39484 | 0.36871 | 0.33453 | 1.3996 | 1.5717 | -0.29937 | -0.41142 | -0.35083 | -0.38215 | -0.31624 | -0.3219 | -0.45187 | -0.57935 | -0.45652 | -0.37965 | -0.34907 | 0.41448 | 0.3803 | 1.4453 | 1.6175 | -0.99384 | -2.0247 | -0.79413 | -1.825
2448.9531 | 121.2433 | -1.712 | 119.371 | -0.33599 | -0.45261 | -0.38744 | -0.41419 | -0.35286 | -0.36768 | -0.47475 | -0.61597 | -0.50229 | -0.40253 | -0.38111 | 0.34582 | 0.31622 | 1.4682 | 1.6267 | -0.29021 | -0.40684 | -0.34167 | -0.36841 | -0.30709 | -0.3219 | -0.42898 | -0.5702 | -0.45652 | -0.35675 | -0.33533 | 0.39159 | 0.36199 | 1.514 | 1.6724 | -0.96179 | -2.0842 | -0.74835 | -1.8708
2450.7188 | 121.2341 | -1.8494 | 119.252 | -0.34514 | -0.46177 | -0.39202 | -0.42335 | -0.34828 | -0.36768 | -0.48849 | -0.62971 | -0.51603 | -0.38422 | -0.36737 | 0.33666 | 0.31164 | 1.569 | 1.7365 | -0.29937 | -0.416 | -0.34625 | -0.37757 | -0.30251 | -0.3219 | -0.44271 | -0.58393 | -0.47025 | -0.33844 | -0.32159 | 0.38244 | 0.35741 | 1.6147 | 1.7823 | -0.96637 | -2.1987 | -0.72088 | -1.9532
2452.4219 | 121.1151 | -1.973 | 119.1467 | -0.35888 | -0.47551 | -0.40576 | -0.4325 | -0.37117 | -0.38141 | -0.49764 | -0.63429 | -0.52519 | -0.40253 | -0.39026 | 0.34582 | 0.32537 | 1.6697 | 1.8327 | -0.3131 | -0.42973 | -0.35998 | -0.38673 | -0.3254 | -0.33564 | -0.45187 | -0.58851 | -0.47941 | -0.35675 | -0.34449 | 0.39159 | 0.37115 | 1.7155 | 1.8785 | -0.9801 | -2.304 | -0.74835 | -2.0722
2454.1875 | 121.1563 | -2.3804 | 118.6752 | -0.4596 | -0.57624 | -0.50191 | -0.53323 | -0.47189 | -0.48214 | -0.59836 | -0.75791 | -0.63966 | -0.47578 | -0.46353 | 0.42822 | 0.40778 | 2.1 | 2.2584 | -0.41383 | -0.53047 | -0.45613 | -0.48745 | -0.42611 | -0.43636 | -0.55259 | -0.71213 | -0.59388 | -0.43001 | -0.41775 | 0.474 | 0.45355 | 2.1458 | 2.3042 | -1.1861 | -2.8579 | -0.90401 | -2.5758
2455.9688 | 121.0785 | -2.8427 | 118.2037 | -0.55575 | -0.65866 | -0.59348 | -0.61106 | -0.55429 | -0.55539 | -0.67619 | -0.86321 | -0.74039 | -0.5353 | -0.5139 | 0.47401 | 0.4444 | 2.4388 | 2.6155 | -0.50997 | -0.61289 | -0.54771 | -0.56529 | -0.50852 | -0.50961 | -0.63042 | -0.81743 | -0.69461 | -0.48952 | -0.46812 | 0.51978 | 0.49018 | 2.4846 | 2.6613 | -1.3372 | -3.3021 | -1.0093 | -2.9741
2457.6875 | 121.0602 | -4.8523 | 116.0294 | -1.0868 | -1.1669 | -1.12 | -1.1284 | -1.0899 | -1.0911 | -1.2073 | -1.4447 | -1.3219 | -0.94734 | -0.92143 | 0.89978 | 0.87016 | 4.1649 | 4.3324 | -1.0411 | -1.1211 | -1.0742 | -1.0827 | -1.0441 | -1.0453 | -1.1615 | -1.3989 | -1.2761 | -0.90157 | -0.87566 | 0.94555 | 0.91594 | 4.2107 | 4.3781 | -2.3445 | -5.6096 | -1.8471 | -5.1122
2459.4531 | 120.9274 | -4.4357 | 116.3589 | -0.62901 | -0.69987 | -0.66216 | -0.6889 | -0.6367 | -0.63322 | -0.76318 | -1.0418 | -0.91897 | -0.46205 | -0.44521 | 0.41449 | 0.38489 | 3.9543 | 4.1218 | -0.58323 | -0.65409 | -0.61638 | -0.64312 | -0.59092 | -0.58745 | -0.7174 | -0.996 | -0.87319 | -0.41627 | -0.39944 | 0.46026 | 0.43066 | 4.0001 | 4.1675 | -1.4563 | -4.9961 | -0.87654 | -4.4163
2461.1719 | 120.7855 | -6.5048 | 114.1525 | -0.93118 | -0.96086 | -0.94146 | -0.97734 | -0.92968 | -0.92166 | -1.047 | -1.55 | -1.4226 | -0.50325 | -0.48185 | 0.46027 | 0.43525 | 6.303 | 6.4749 | -0.8854 | -0.91509 | -0.89568 | -0.93157 | -0.88391 | -0.87589 | -1.0012 | -1.5042 | -1.3769 | -0.45748 | -0.43607 | 0.50605 | 0.48102 | 6.3488 | 6.5207 | -2.0103 | -7.853 | -0.96352 | -6.8063
2462.9375 | 120.694 | -7.9926 | 112.5092 | -0.94491 | -0.96544 | -0.96435 | -0.99108 | -0.95257 | -0.95829 | -1.0562 | -1.5729 | -1.4593 | -0.50783 | -0.48642 | 0.46943 | 0.43525 | 6.5273 | 6.6993 | -0.89914 | -0.91967 | -0.91857 | -0.9453 | -0.9068 | -0.91251 | -1.0104 | -1.5271 | -1.4135 | -0.46205 | -0.44065 | 0.5152 | 0.48102 | 6.5731 | 6.745 | -2.0423 | -8.1002 | -0.97726 | -7.0352
2464.7188 | 121.1014 | -0.40741 | 120.607 | 0.007391 | -0.10462 | -0.053207 | -0.098273 | -0.009515 | -0.042612 | -0.15428 | -0.24969 | -0.13141 | -0.14157 | -0.1201 | 0.080283 | 0.059844 | 0.24122 | 0.32188 | 0.053167 | -0.058848 | -0.007431 | -0.052497 | 0.036261 | 0.003164 | -0.10851 | -0.20392 | -0.085632 | -0.095792 | -0.074327 | 0.12606 | 0.10562 | 0.287 | 0.36766 | -0.32998 | -0.49091 | -0.22185 | -0.38279
2466.4219 | 121.17 | -0.40741 | 120.6711 | 0.007391 | -0.11378 | -0.04405 | -0.093694 | -0.000359 | -0.038034 | -0.16344 | -0.24054 | -0.13141 | -0.14157 | -0.12468 | 0.080283 | 0.059844 | 0.25038 | 0.3173 | 0.053167 | -0.068006 | 0.001726 | -0.047918 | 0.045417 | 0.007742 | -0.11766 | -0.19476 | -0.085632 | -0.095792 | -0.078906 | 0.12606 | 0.10562 | 0.29615 | 0.36308 | -0.32082 | -0.49091 | -0.22185 | -0.39194
2468.2031 | 121.2341 | -0.39368 | 120.7169 | 0.007391 | -0.1092 | -0.053207 | -0.098273 | -0.014093 | -0.04719 | -0.15886 | -0.24969 | -0.13141 | -0.15072 | -0.1201 | 0.094017 | 0.069001 | 0.25038 | 0.32188 | 0.053167 | -0.063427 | -0.007431 | -0.052497 | 0.031683 | -0.001414 | -0.11308 | -0.20392 | -0.085632 | -0.10495 | -0.074327 | 0.13979 | 0.11478 | 0.29615 | 0.36766 | -0.34371 | -0.50007 | -0.24474 | -0.4011
2469.9688 | 121.1105 | -0.43488 | 120.7764 | 0.01197 | -0.1092 | -0.04405 | -0.089116 | -0.009515 | -0.042612 | -0.15428 | -0.25427 | -0.13599 | -0.14615 | -0.12468 | 0.084861 | 0.059844 | 0.2458 | 0.32646 | 0.057746 | -0.063427 | 0.001726 | -0.04334 | 0.036261 | 0.003164 | -0.10851 | -0.2085 | -0.090211 | -0.10037 | -0.078906 | 0.13064 | 0.10562 | 0.29157 | 0.37223 | -0.33913 | -0.50007 | -0.23101 | -0.39194
2471.6875 | 121.2891 | -0.41199 | 120.7214 | -0.001765 | -0.11378 | -0.048628 | -0.098273 | -0.009515 | -0.038034 | -0.15886 | -0.24969 | -0.13141 | -0.15072 | -0.12468 | 0.084861 | 0.055266 | 0.26411 | 0.33561 | 0.044011 | -0.068006 | -0.002852 | -0.052497 | 0.036261 | 0.007742 | -0.11308 | -0.20392 | -0.085632 | -0.10495 | -0.078906 | 0.13064 | 0.10104 | 0.30989 | 0.38139 | -0.33455 | -0.5138 | -0.23558 | -0.41483
2473.4531 | 121.2158 | -0.41657 | 120.7535 | 0.007391 | -0.1092 | -0.048628 | -0.093694 | -0.009515 | -0.042612 | -0.16344 | -0.24969 | -0.13599 | -0.14157 | -0.12926 | 0.084861 | 0.064423 | 0.25953 | 0.33104 | 0.053167 | -0.063427 | -0.002852 | -0.047918 | 0.036261 | 0.003164 | -0.11766 | -0.20392 | -0.090211 | -0.095792 | -0.083485 | 0.13064 | 0.1102 | 0.30531 | 0.37681 | -0.33455 | -0.50923 | -0.22643 | -0.4011
2475.2344 | 121.1517 | -0.44861 | 120.7809 | 0.002813 | -0.11836 | -0.04405 | -0.093694 | -0.009515 | -0.042612 | -0.15886 | -0.24969 | -0.13141 | -0.15072 | -0.12926 | 0.089439 | 0.055266 | 0.25953 | 0.33104 | 0.048589 | -0.072585 | 0.001726 | -0.047918 | 0.036261 | 0.003164 | -0.11308 | -0.20392 | -0.085632 | -0.10495 | -0.083485 | 0.13522 | 0.10104 | 0.30531 | 0.37681 | -0.33913 | -0.50923 | -0.24016 | -0.41026
2476.9375 | 121.2021 | -0.43945 | 120.7672 | -0.001765 | -0.11836 | -0.048628 | -0.098273 | -0.009515 | -0.04719 | -0.16344 | -0.25885 | -0.14972 | -0.14615 | -0.13384 | 0.094017 | 0.069001 | 0.26869 | 0.34019 | 0.044011 | -0.072585 | -0.002852 | -0.052497 | 0.036261 | -0.001414 | -0.11766 | -0.21307 | -0.10395 | -0.10037 | -0.088064 | 0.13979 | 0.11478 | 0.31446 | 0.38597 | -0.35287 | -0.52754 | -0.24016 | -0.41484
2478.7031 | 121.2296 | -0.42572 | 120.7581 | -0.001765 | -0.11836 | -0.057786 | -0.11201 | -0.014093 | -0.051769 | -0.16344 | -0.25885 | -0.14514 | -0.14615 | -0.12926 | 0.098596 | 0.064423 | 0.26411 | 0.34477 | 0.044011 | -0.072585 | -0.01201 | -0.066232 | 0.031683 | -0.005993 | -0.11766 | -0.21307 | -0.099369 | -0.10037 | -0.083485 | 0.14437 | 0.1102 | 0.30989 | 0.39054 | -0.35745 | -0.52296 | -0.24474 | -0.41026
2480.4688 | 121.3028 | -0.41657 | 120.7672 | 0.007391 | -0.12294 | -0.057786 | -0.11201 | -0.014093 | -0.051769 | -0.15886 | -0.26343 | -0.14514 | -0.15072 | -0.13842 | 0.094017 | 0.073579 | 0.26411 | 0.34477 | 0.053167 | -0.077163 | -0.01201 | -0.066232 | 0.031683 | -0.005993 | -0.11308 | -0.21765 | -0.099369 | -0.10495 | -0.092643 | 0.13979 | 0.11936 | 0.30989 | 0.39054 | -0.35745 | -0.52754 | -0.24474 | -0.41483
2482.1875 | 121.225 | -0.44403 | 120.7718 | -0.001765 | -0.12294 | -0.057786 | -0.10743 | -0.018671 | -0.051769 | -0.16344 | -0.25885 | -0.14972 | -0.1553 | -0.13842 | 0.098596 | 0.069001 | 0.27785 | 0.35393 | 0.044011 | -0.077163 | -0.01201 | -0.061654 | 0.027105 | -0.005993 | -0.11766 | -0.21307 | -0.10395 | -0.10953 | -0.092643 | 0.14437 | 0.11478 | 0.32362 | 0.3997 | -0.35745 | -0.5367 | -0.2539 | -0.43315
2483.9688 | 121.1975 | -8.876 | 112.2345 | 0.06691 | -0.067994 | 0.006315 | -0.047909 | 0.049999 | 0.016907 | -0.1085 | -0.18102 | -0.058147 | -0.1141 | -0.092628 | 0.052814 | 0.032376 | -0.033484 | 0.060923 | 0.11269 | -0.022218 | 0.052091 | -0.002133 | 0.095775 | 0.062683 | -0.062723 | -0.13524 | -0.012371 | -0.068322 | -0.046852 | 0.09859 | 0.078152 | 0.012292 | 0.1067 | -0.23383 | -0.14753 | -0.16691 | -0.080614
2485.6719 | 121.1288 | -8.9264 | 112.2391 | 0.062332 | -0.067994 | 0.006315 | -0.043331 | 0.054577 | 0.021485 | -0.1085 | -0.17644 | -0.062726 | -0.10494 | -0.092628 | 0.057392 | 0.032376 | -0.028906 | 0.070079 | 0.10811 | -0.022218 | 0.052091 | 0.002445 | 0.10035 | 0.067261 | -0.062723 | -0.13066 | -0.01695 | -0.059166 | -0.046852 | 0.10317 | 0.078152 | 0.01687 | 0.11585 | -0.23383 | -0.14753 | -0.16233 | -0.076036
2487.4375 | 121.138 | -8.8257 | 112.3764 | 0.057754 | -0.063415 | 0.001736 | -0.038752 | 0.049999 | 0.021485 | -0.10392 | -0.17644 | -0.058147 | -0.11868 | -0.10179 | 0.057392 | 0.027798 | -0.033484 | 0.065501 | 0.10353 | -0.017639 | 0.047512 | 0.007024 | 0.095775 | 0.067261 | -0.058145 | -0.13066 | -0.012371 | -0.0729 | -0.05601 | 0.10317 | 0.073574 | 0.012292 | 0.11128 | -0.23383 | -0.14295 | -0.17607 | -0.085192
2489.1406 | 121.2341 | -10.0937 | 111.0626 | 0.062332 | -0.058836 | 0.001736 | -0.043331 | 0.045421 | 0.016907 | -0.099343 | -0.17186 | -0.062726 | -0.1141 | -0.092628 | 0.048236 | 0.036954 | -0.033484 | 0.065501 | 0.10811 | -0.01306 | 0.047512 | 0.002445 | 0.091197 | 0.062683 | -0.053567 | -0.12608 | -0.01695 | -0.068322 | -0.046852 | 0.094012 | 0.08273 | 0.012292 | 0.11128 | -0.22009 | -0.13837 | -0.16233 | -0.080614
2490.9219 | 121.1838 | -18.4433 | 103.7384 | 0.076067 | -0.049678 | 0.024629 | -0.029595 | 0.063733 | 0.035221 | -0.094765 | -0.15812 | -0.044411 | -0.086628 | -0.078891 | 0.039079 | 0.014064 | -0.033484 | 0.051766 | 0.12184 | -0.003902 | 0.070405 | 0.016181 | 0.10951 | 0.080997 | -0.048989 | -0.11235 | 0.001365 | -0.040852 | -0.033115 | 0.084855 | 0.05984 | 0.012292 | 0.097542 | -0.1972 | -0.12464 | -0.12571 | -0.053144
2492.7031 | 121.0236 | -70.9305 | 49.6674 | 0.19053 | 0.069371 | 0.14367 | 0.084867 | 0.17818 | 0.14052 | 0.015112 | -0.039082 | 0.074638 | 0.018672 | 0.035585 | -0.079953 | -0.10497 | -0.11132 | -0.071844 | 0.2363 | 0.11515 | 0.18945 | 0.13064 | 0.22396 | 0.1863 | 0.060888 | 0.006694 | 0.12041 | 0.064448 | 0.081361 | -0.034177 | -0.05919 | -0.065541 | -0.026068 | 0.040871 | 0.072235 | 0.098625 | 0.12999
2494.4844 | 120.8542 | -80.8319 | 39.6194 | 0.20426 | 0.078529 | 0.15283 | 0.089445 | 0.19649 | 0.15426 | 0.024268 | -0.034504 | 0.092954 | 0.036985 | 0.053901 | -0.093688 | -0.12328 | -0.12047 | -0.071844 | 0.25004 | 0.1243 | 0.19861 | 0.13522 | 0.24227 | 0.20004 | 0.070044 | 0.011272 | 0.13873 | 0.082761 | 0.099677 | -0.047912 | -0.077502 | -0.074698 | -0.026068 | 0.059184 | 0.08597 | 0.13067 | 0.15746
2496.2188 | 120.6894 | -86.2564 | 34.1721 | 0.18595 | 0.055634 | 0.13452 | 0.071132 | 0.16903 | 0.14052 | 0.001377 | -0.057396 | 0.060902 | 0.018672 | 0.031006 | -0.066219 | -0.09581 | -0.10674 | -0.062688 | 0.23172 | 0.10141 | 0.18029 | 0.11691 | 0.2148 | 0.1863 | 0.047153 | -0.01162 | 0.10668 | 0.064448 | 0.076782 | -0.020443 | -0.050034 | -0.060963 | -0.016912 | 0.008823 | 0.049343 | 0.084891 | 0.12541
2498 | 120.4514 | -85.4782 | 34.7763 | 0.18595 | 0.055634 | 0.12994 | 0.07571 | 0.16903 | 0.13595 | 0.001377 | -0.048239 | 0.065481 | 0.009515 | 0.031006 | -0.061641 | -0.09581 | -0.10216 | -0.053532 | 0.23172 | 0.10141 | 0.17571 | 0.12149 | 0.2148 | 0.18172 | 0.047153 | -0.002463 | 0.11126 | 0.055291 | 0.076782 | -0.015865 | -0.050034 | -0.056384 | -0.007756 | 0.013402 | 0.053921 | 0.071156 | 0.11167
2499.7812 | 120.2316 | -87.7579 | 32.4142 | 0.21342 | 0.083107 | 0.15741 | 0.098602 | 0.20565 | 0.16799 | 0.028846 | -0.025347 | 0.088375 | 0.036985 | 0.05848 | -0.098266 | -0.1187 | -0.12505 | -0.081001 | 0.2592 | 0.12888 | 0.20319 | 0.14438 | 0.25143 | 0.21377 | 0.074622 | 0.020429 | 0.13415 | 0.082761 | 0.10426 | -0.05249 | -0.072924 | -0.079276 | -0.035225 | 0.072919 | 0.099705 | 0.13525 | 0.16204
2501.5 | 120.9183 | -119.5312 | 1.149 | 0.15848 | 0.03274 | 0.10704 | 0.034504 | 0.14156 | 0.099318 | -0.035248 | -0.084867 | 0.038008 | -0.022532 | -0.005627 | -0.043328 | -0.063763 | -0.079268 | -0.016906 | 0.20425 | 0.078516 | 0.15282 | 0.08028 | 0.18733 | 0.14509 | 0.010528 | -0.039091 | 0.083784 | 0.023244 | 0.040149 | 0.002448 | -0.017987 | -0.033492 | 0.02887 | -0.041539 | -0.005599 | 0.020796 | 0.056736
2503.2969 | 121.0648 | -119.014 | 1.7349 | 0.15848 | 0.023583 | 0.10247 | 0.039082 | 0.14156 | 0.10848 | -0.026092 | -0.084867 | 0.019693 | -0.017954 | -0.005627 | -0.034171 | -0.063763 | -0.07469 | -0.021484 | 0.20425 | 0.069359 | 0.14824 | 0.084858 | 0.18733 | 0.15425 | 0.019684 | -0.039091 | 0.065469 | 0.027822 | 0.040149 | 0.011605 | -0.017987 | -0.028914 | 0.024292 | -0.050696 | -0.010177 | 0.016217 | 0.056736
2505 | 121.0052 | -118.5608 | 2.2202 | 0.1539 | 0.028162 | 0.10247 | 0.034504 | 0.13698 | 0.1039 | -0.03067 | -0.080288 | 0.02885 | -0.027111 | -0.010206 | -0.029593 | -0.054607 | -0.07469 | -0.026063 | 0.19968 | 0.073938 | 0.14824 | 0.08028 | 0.18276 | 0.14967 | 0.015106 | -0.034512 | 0.074626 | 0.018665 | 0.03557 | 0.016183 | -0.008831 | -0.028914 | 0.019713 | -0.050695 | -0.005598 | 0.002482 | 0.047579
2506.7969 | 121.0876 | -117.9337 | 2.8519 | 0.14932 | 0.028162 | 0.10247 | 0.043661 | 0.13698 | 0.099318 | -0.021514 | -0.084867 | 0.038008 | -0.027111 | -0.001048 | -0.034171 | -0.068341 | -0.07469 | -0.021484 | 0.1951 | 0.073938 | 0.14824 | 0.089437 | 0.18276 | 0.14509 | 0.024262 | -0.039091 | 0.083784 | 0.018665 | 0.044728 | 0.011605 | -0.022565 | -0.028914 | 0.024292 | -0.050696 | -0.010177 | 0.00706 | 0.047579
2508.5156 | 121.0144 | -117.7826 | 3.0441 | 0.1539 | 0.03274 | 0.097887 | 0.048239 | 0.14156 | 0.10848 | -0.035248 | -0.084867 | 0.024271 | -0.027111 | -0.001048 | -0.034171 | -0.059185 | -0.079268 | -0.016906 | 0.19968 | 0.078516 | 0.14366 | 0.094015 | 0.18733 | 0.15425 | 0.010528 | -0.039091 | 0.070047 | 0.018665 | 0.044728 | 0.011605 | -0.013409 | -0.033492 | 0.02887 | -0.050696 | -0.005599 | 0.00706 | 0.052157
2510.2812 | 121.0144 | -117.897 | 2.9892 | 0.14932 | 0.023583 | 0.10247 | 0.034504 | 0.14156 | 0.09474 | -0.021514 | -0.089445 | 0.02885 | -0.022532 | -0.010206 | -0.034171 | -0.063763 | -0.079268 | -0.026063 | 0.1951 | 0.069359 | 0.14824 | 0.08028 | 0.18733 | 0.14052 | 0.024262 | -0.043669 | 0.074626 | 0.023244 | 0.03557 | 0.011605 | -0.017987 | -0.033492 | 0.019713 | -0.055274 | -0.010177 | 0.011639 | 0.056736
2512.0469 | 121.0007 | -117.9474 | 2.9663 | 0.1539 | 0.023583 | 0.10704 | 0.048239 | 0.14156 | 0.1039 | -0.021514 | -0.094024 | 0.02885 | -0.022532 | -0.005627 | -0.034171 | -0.059185 | -0.083847 | -0.012328 | 0.19968 | 0.069359 | 0.15282 | 0.094015 | 0.18733 | 0.14967 | 0.024262 | -0.048248 | 0.074626 | 0.023244 | 0.040149 | 0.011605 | -0.013409 | -0.038071 | 0.033448 | -0.059853 | -0.010177 | 0.011639 | 0.061315
2513.7656 | 120.9824 | -117.8833 | 3.0167 | 0.14932 | 0.028162 | 0.097887 | 0.039082 | 0.14156 | 0.1039 | -0.035248 | -0.089445 | 0.024271 | -0.027111 | -0.005627 | -0.034171 | -0.054607 | -0.079268 | -0.026063 | 0.1951 | 0.073938 | 0.14366 | 0.084858 | 0.18733 | 0.14967 | 0.010528 | -0.043669 | 0.070047 | 0.018665 | 0.040149 | 0.011605 | -0.008831 | -0.033492 | 0.019713 | -0.055274 | -0.010177 | 0.00706 | 0.052157
2515.5312 | 121.1426 | -117.8146 | 3.0121 | 0.1539 | 0.023583 | 0.097887 | 0.048239 | 0.13698 | 0.099318 | -0.021514 | -0.084867 | 0.033429 | -0.017954 | -0.005627 | -0.034171 | -0.063763 | -0.07469 | -0.026063 | 0.19968 | 0.069359 | 0.14366 | 0.094015 | 0.18276 | 0.14509 | 0.024262 | -0.039091 | 0.079205 | 0.027822 | 0.040149 | 0.011605 | -0.017987 | -0.028914 | 0.019713 | -0.050696 | -0.010177 | 0.016217 | 0.056736
2517.25 | 121.0922 | -117.8513 | 3.0396 | 0.1539 | 0.019004 | 0.097887 | 0.034504 | 0.1324 | 0.099318 | -0.026092 | -0.089445 | 0.02885 | -0.027111 | -0.005627 | -0.034171 | -0.063763 | -0.079268 | -0.016906 | 0.19968 | 0.06478 | 0.14366 | 0.08028 | 0.17818 | 0.14509 | 0.019684 | -0.043669 | 0.074626 | 0.018665 | 0.040149 | 0.011605 | -0.017987 | -0.033492 | 0.02887 | -0.055274 | -0.010177 | 0.00706 | 0.052157
2519.0312 | 121.0556 | -117.6636 | 3.1952 | 0.15848 | 0.019004 | 0.10247 | 0.043661 | 0.13698 | 0.11305 | -0.026092 | -0.089445 | 0.02885 | -0.013376 | -0.005627 | -0.029593 | -0.059185 | -0.07469 | -0.021484 | 0.20425 | 0.06478 | 0.14824 | 0.089437 | 0.18276 | 0.15883 | 0.019684 | -0.043669 | 0.074626 | 0.0324 | 0.040149 | 0.016183 | -0.013409 | -0.028914 | 0.024292 | -0.059852 | -0.014755 | 0.016217 | 0.061314
2520.7344 | 121.1472 | -117.7094 | 3.1219 | 0.1539 | 0.019004 | 0.093308 | 0.034504 | 0.13698 | 0.1039 | -0.026092 | -0.080288 | 0.033429 | -0.027111 | -0.001048 | -0.034171 | -0.063763 | -0.07469 | -0.026063 | 0.19968 | 0.06478 | 0.13908 | 0.08028 | 0.18276 | 0.14967 | 0.019684 | -0.034512 | 0.079205 | 0.018665 | 0.044728 | 0.011605 | -0.017987 | -0.028914 | 0.019713 | -0.046117 | -0.005598 | 0.00706 | 0.047579
2522.5 | 121.0693 | -117.7505 | 3.1357 | 0.14932 | 0.028162 | 0.10247 | 0.039082 | 0.14156 | 0.11305 | -0.026092 | -0.089445 | 0.02885 | -0.017954 | -0.005627 | -0.034171 | -0.054607 | -0.079268 | -0.021484 | 0.1951 | 0.073938 | 0.14824 | 0.084858 | 0.18733 | 0.15883 | 0.019684 | -0.043669 | 0.074626 | 0.027822 | 0.040149 | 0.011605 | -0.008831 | -0.033492 | 0.024292 | -0.055274 | -0.010177 | 0.016217 | 0.061314
2524.2188 | 121.0098 | -117.7505 | 3.154 | 0.1539 | 0.023583 | 0.10704 | 0.039082 | 0.12782 | 0.099318 | -0.026092 | -0.084867 | 0.033429 | -0.017954 | -0.005627 | -0.03875 | -0.059185 | -0.07469 | -0.021484 | 0.19968 | 0.069359 | 0.15282 | 0.084858 | 0.1736 | 0.14509 | 0.019684 | -0.039091 | 0.079205 | 0.027822 | 0.040149 | 0.007026 | -0.013409 | -0.028914 | 0.024292 | -0.046117 | -0.010177 | 0.020796 | 0.056736
2525.9844 | 121.0373 | -117.8787 | 3.035 | 0.14474 | 0.028162 | 0.097887 | 0.039082 | 0.14156 | 0.1039 | -0.026092 | -0.084867 | 0.033429 | -0.027111 | -0.010206 | -0.03875 | -0.059185 | -0.083847 | -0.016906 | 0.19052 | 0.073938 | 0.14366 | 0.084858 | 0.18733 | 0.14967 | 0.019684 | -0.039091 | 0.079205 | 0.018665 | 0.03557 | 0.007026 | -0.013409 | -0.038071 | 0.02887 | -0.046117 | -0.00102 | 0.011639 | 0.056736
2527.7656 | 121.0922 | -117.7734 | 3.1036 | 0.14932 | 0.028162 | 0.093308 | 0.039082 | 0.13698 | 0.09474 | -0.021514 | -0.084867 | 0.038008 | -0.027111 | -0.010206 | -0.029593 | -0.054607 | -0.079268 | -0.016906 | 0.1951 | 0.073938 | 0.13908 | 0.084858 | 0.18276 | 0.14052 | 0.024262 | -0.039091 | 0.083784 | 0.018665 | 0.03557 | 0.016183 | -0.008831 | -0.033492 | 0.02887 | -0.055274 | -0.005599 | 0.002482 | 0.052157
2529.5469 | 121.1105 | -117.8421 | 3.0075 | 0.14932 | 0.019004 | 0.08873 | 0.034504 | 0.13698 | 0.099318 | -0.026092 | -0.089445 | 0.02885 | -0.017954 | -0.010206 | -0.034171 | -0.050029 | -0.07469 | -0.012328 | 0.1951 | 0.06478 | 0.13451 | 0.08028 | 0.18276 | 0.14509 | 0.019684 | -0.043669 | 0.074626 | 0.027822 | 0.03557 | 0.011605 | -0.004253 | -0.028914 | 0.033448 | -0.055274 | -0.014755 | 0.016217 | 0.056736
2531.3281 | 121.0236 | -117.9199 | 3.0167 | 0.14932 | 0.023583 | 0.10247 | 0.034504 | 0.14156 | 0.10848 | -0.03067 | -0.094024 | 0.033429 | -0.027111 | -0.005627 | -0.034171 | -0.063763 | -0.070112 | -0.021484 | 0.1951 | 0.069359 | 0.14824 | 0.08028 | 0.18733 | 0.15425 | 0.015106 | -0.048248 | 0.079205 | 0.018665 | 0.040149 | 0.011605 | -0.017987 | -0.024336 | 0.024292 | -0.059853 | -0.023912 | 0.00706 | 0.043001
2533.0312 | 121.0556 | -117.9153 | 2.9709 | 0.15848 | 0.023583 | 0.097887 | 0.048239 | 0.14156 | 0.099318 | -0.026092 | -0.094024 | 0.033429 | -0.022532 | -0.010206 | -0.03875 | -0.063763 | -0.079268 | -0.030641 | 0.20425 | 0.069359 | 0.14366 | 0.094015 | 0.18733 | 0.14509 | 0.019684 | -0.048248 | 0.079205 | 0.023244 | 0.03557 | 0.007026 | -0.017987 | -0.033492 | 0.015135 | -0.055274 | -0.014756 | 0.016218 | 0.056736
2534.8281 | 121.1151 | -115.0085 | 5.7953 | 0.14474 | 0.019004 | 0.097887 | 0.039082 | 0.13698 | 0.09474 | -0.03067 | -0.089445 | 0.02885 | -0.031689 | -0.005627 | -0.034171 | -0.054607 | -0.079268 | -0.021484 | 0.19052 | 0.06478 | 0.14366 | 0.084858 | 0.18276 | 0.14052 | 0.015106 | -0.043669 | 0.074626 | 0.014087 | 0.040149 | 0.011605 | -0.008831 | -0.033492 | 0.024292 | -0.055274 | -0.010177 | 0.002482 | 0.047579
2536.6094 | 121.138 | -115.0589 | 5.7632 | 0.1539 | 0.019004 | 0.093308 | 0.039082 | 0.13698 | 0.099318 | -0.03067 | -0.089445 | 0.02885 | -0.017954 | -0.010206 | -0.025015 | -0.054607 | -0.079268 | -0.016906 | 0.19968 | 0.06478 | 0.13908 | 0.084858 | 0.18276 | 0.14509 | 0.015106 | -0.043669 | 0.074626 | 0.027822 | 0.03557 | 0.020761 | -0.008831 | -0.033492 | 0.02887 | -0.06443 | -0.010177 | 0.007061 | 0.061314
2538.3906 | 121.1517 | -115.3336 | 5.4703 | 0.1539 | 0.019004 | 0.093308 | 0.039082 | 0.13698 | 0.099318 | -0.026092 | -0.094024 | 0.024271 | -0.027111 | -0.014785 | -0.025015 | -0.059185 | -0.07469 | -0.021484 | 0.19968 | 0.06478 | 0.13908 | 0.084858 | 0.18276 | 0.14509 | 0.019684 | -0.048248 | 0.070047 | 0.018665 | 0.030991 | 0.020761 | -0.013409 | -0.028914 | 0.024292 | -0.069009 | -0.019334 | -0.002096 | 0.047579
2540.0938 | 121.1792 | -115.6403 | 5.159 | 0.14474 | 0.019004 | 0.097887 | 0.034504 | 0.1324 | 0.099318 | -0.03067 | -0.084867 | 0.024271 | -0.022532 | -0.010206 | -0.025015 | -0.054607 | -0.07469 | -0.021484 | 0.19052 | 0.06478 | 0.14366 | 0.08028 | 0.17818 | 0.14509 | 0.015106 | -0.039091 | 0.070047 | 0.023244 | 0.03557 | 0.020761 | -0.008831 | -0.028914 | 0.024292 | -0.059852 | -0.010177 | 0.002483 | 0.052158
2541.8594 | 121.138 | -115.4572 | 5.3833 | 0.14932 | 0.009846 | 0.093308 | 0.034504 | 0.1324 | 0.1039 | -0.035248 | -0.084867 | 0.02885 | -0.022532 | -0.005627 | -0.03875 | -0.059185 | -0.079268 | -0.021484 | 0.1951 | 0.055622 | 0.13908 | 0.08028 | 0.17818 | 0.14967 | 0.010528 | -0.039091 | 0.074626 | 0.023244 | 0.040149 | 0.007026 | -0.013409 | -0.033492 | 0.024292 | -0.046117 | -0.005599 | 0.016218 | 0.056736
2543.5781 | 121.0007 | -115.7272 | 5.1819 | 0.1539 | 0.03274 | 0.10247 | 0.039082 | 0.1324 | 0.1039 | -0.026092 | -0.084867 | 0.038008 | -0.031689 | -0.010206 | -0.03875 | -0.059185 | -0.079268 | -0.021484 | 0.19968 | 0.078516 | 0.14824 | 0.084858 | 0.17818 | 0.14967 | 0.019684 | -0.039091 | 0.083784 | 0.014087 | 0.03557 | 0.007026 | -0.013409 | -0.033492 | 0.024292 | -0.046117 | -0.005599 | 0.007061 | 0.047579
2545.3438 | 121.1655 | -116.1484 | 4.6783 | 0.14932 | 0.019004 | 0.10247 | 0.039082 | 0.13698 | 0.1039 | -0.035248 | -0.084867 | 0.02885 | -0.022532 | -0.014785 | -0.034171 | -0.054607 | -0.079268 | -0.021484 | 0.1951 | 0.06478 | 0.14824 | 0.084858 | 0.18276 | 0.14967 | 0.010528 | -0.039091 | 0.074626 | 0.023244 | 0.030991 | 0.011605 | -0.008831 | -0.033492 | 0.024292 | -0.050696 | -0.005599 | 0.011639 | 0.056736
2547.0938 | 121.0144 | -116.3132 | 4.6051 | 0.14474 | 0.019004 | 0.097887 | 0.039082 | 0.13698 | 0.1039 | -0.03067 | -0.089445 | 0.02885 | -0.022532 | -0.010206 | -0.029593 | -0.054607 | -0.079268 | -0.021484 | 0.19052 | 0.06478 | 0.14366 | 0.084858 | 0.18276 | 0.14967 | 0.015106 | -0.043669 | 0.074626 | 0.023244 | 0.03557 | 0.016183 | -0.008831 | -0.033492 | 0.024292 | -0.059852 | -0.010177 | 0.007061 | 0.056736
2548.8281 | 121.1517 | -116.7664 | 4.0878 | 0.14474 | 0.019004 | 0.093308 | 0.039082 | 0.14156 | 0.1039 | -0.026092 | -0.080288 | 0.024271 | -0.027111 | -0.005627 | -0.03875 | -0.059185 | -0.079268 | -0.026063 | 0.19052 | 0.06478 | 0.13908 | 0.084858 | 0.18733 | 0.14967 | 0.019684 | -0.034512 | 0.070047 | 0.018665 | 0.040149 | 0.007026 | -0.013409 | -0.033492 | 0.019713 | -0.041538 | -0.00102 | 0.011639 | 0.052157
2550.5938 | 121.051 | -115.6082 | 5.3238 | 0.14474 | 0.019004 | 0.10247 | 0.039082 | 0.13698 | 0.1039 | -0.03067 | -0.089445 | 0.024271 | -0.027111 | -0.005627 | -0.029593 | -0.054607 | -0.07469 | -0.021484 | 0.19052 | 0.06478 | 0.14824 | 0.084858 | 0.18276 | 0.14967 | 0.015106 | -0.043669 | 0.070047 | 0.018665 | 0.040149 | 0.016183 | -0.008831 | -0.028914 | 0.024292 | -0.059852 | -0.014755 | 0.002482 | 0.047579
2552.2969 | 121.0739 | -115.8142 | 5.1086 | 0.14474 | 0.023583 | 0.093308 | 0.029925 | 0.13698 | 0.09474 | -0.026092 | -0.084867 | 0.02885 | -0.027111 | -0.010206 | -0.029593 | -0.059185 | -0.07469 | -0.021484 | 0.19052 | 0.069359 | 0.13908 | 0.075701 | 0.18276 | 0.14052 | 0.019684 | -0.039091 | 0.074626 | 0.018665 | 0.03557 | 0.016183 | -0.013409 | -0.028914 | 0.024292 | -0.055274 | -0.010177 | 0.002482 | 0.047579
2554.0625 | 121.0464 | -116.0019 | 4.9255 | 0.14474 | 0.023583 | 0.097887 | 0.039082 | 0.13698 | 0.10848 | -0.03067 | -0.098602 | 0.033429 | -0.017954 | -0.010206 | -0.029593 | -0.063763 | -0.083847 | -0.021484 | 0.19052 | 0.069359 | 0.14366 | 0.084858 | 0.18276 | 0.15425 | 0.015106 | -0.052826 | 0.079205 | 0.027822 | 0.03557 | 0.016183 | -0.017987 | -0.038071 | 0.024292 | -0.069009 | -0.014755 | 0.011639 | 0.065893
2555.8438 | 121.0785 | -116.1484 | 4.7424 | 0.1539 | 0.037319 | 0.10247 | 0.034504 | 0.1324 | 0.099318 | -0.026092 | -0.094024 | 0.024271 | -0.027111 | -0.001048 | -0.029593 | -0.059185 | -0.07469 | -0.016906 | 0.19968 | 0.083095 | 0.14824 | 0.08028 | 0.17818 | 0.14509 | 0.019684 | -0.048248 | 0.070047 | 0.018665 | 0.044728 | 0.016183 | -0.013409 | -0.028914 | 0.02887 | -0.064431 | -0.019334 | 0.002482 | 0.047579
2557.5469 | 121.051 | -116.3498 | 4.5685 | 0.14474 | 0.023583 | 0.097887 | 0.039082 | 0.13698 | 0.09474 | -0.026092 | -0.089445 | 0.02885 | -0.027111 | -0.010206 | -0.025015 | -0.054607 | -0.079268 | -0.021484 | 0.19052 | 0.069359 | 0.14366 | 0.084858 | 0.18276 | 0.14052 | 0.019684 | -0.043669 | 0.074626 | 0.018665 | 0.03557 | 0.020761 | -0.008831 | -0.033492 | 0.024292 | -0.06443 | -0.010177 | -0.002096 | 0.052157
2559.3125 | 121.0281 | -116.5009 | 4.39 | 0.1539 | 0.023583 | 0.093308 | 0.029925 | 0.14156 | 0.099318 | -0.03067 | -0.094024 | 0.033429 | -0.027111 | -0.010206 | -0.029593 | -0.059185 | -0.083847 | -0.012328 | 0.19968 | 0.069359 | 0.13908 | 0.075701 | 0.18733 | 0.14509 | 0.015106 | -0.048248 | 0.079205 | 0.018665 | 0.03557 | 0.016183 | -0.013409 | -0.038071 | 0.033448 | -0.064431 | -0.010177 | 0.002482 | 0.056736
2561.0312 | 121.0327 | -116.6702 | 4.2252 | 0.14932 | 0.023583 | 0.097887 | 0.034504 | 0.13698 | 0.09474 | -0.026092 | -0.084867 | 0.02885 | -0.027111 | -0.010206 | -0.029593 | -0.059185 | -0.083847 | -0.021484 | 0.1951 | 0.069359 | 0.14366 | 0.08028 | 0.18276 | 0.14052 | 0.019684 | -0.039091 | 0.074626 | 0.018665 | 0.03557 | 0.016183 | -0.013409 | -0.038071 | 0.024292 | -0.055274 | -0.00102 | 0.002482 | 0.056736
2562.7969 | 121.1288 | -116.272 | 4.5593 | 0.1539 | 0.023583 | 0.08873 | 0.034504 | 0.1324 | 0.1039 | -0.026092 | -0.084867 | 0.015114 | -0.027111 | -0.001048 | -0.03875 | -0.054607 | -0.083847 | -0.016906 | 0.19968 | 0.069359 | 0.13451 | 0.08028 | 0.17818 | 0.14967 | 0.019684 | -0.039091 | 0.06089 | 0.018665 | 0.044728 | 0.007026 | -0.008831 | -0.038071 | 0.02887 | -0.046117 | -0.00102 | 0.011639 | 0.056736
2564.5781 | 121.1746 | -117.1417 | 3.6987 | 0.14932 | 0.028162 | 0.097887 | 0.039082 | 0.13698 | 0.09474 | -0.026092 | -0.084867 | 0.024271 | -0.031689 | -0.010206 | -0.025015 | -0.063763 | -0.079268 | -0.021484 | 0.1951 | 0.073938 | 0.14366 | 0.084858 | 0.18276 | 0.14052 | 0.019684 | -0.039091 | 0.070047 | 0.014087 | 0.03557 | 0.020761 | -0.017987 | -0.033492 | 0.024292 | -0.059852 | -0.005599 | -0.006674 | 0.047579
2566.2969 | 121.0831 | -116.629 | 4.2755 | 0.14932 | 0.019004 | 0.097887 | 0.029925 | 0.14156 | 0.099318 | -0.026092 | -0.089445 | 0.02885 | -0.027111 | -0.001048 | -0.034171 | -0.059185 | -0.079268 | -0.021484 | 0.1951 | 0.06478 | 0.14366 | 0.075701 | 0.18733 | 0.14509 | 0.019684 | -0.043669 | 0.074626 | 0.018665 | 0.044728 | 0.011605 | -0.013409 | -0.033492 | 0.024292 | -0.055274 | -0.010177 | 0.00706 | 0.052157
2568.0469 | 121.1609 | -116.2811 | 4.5364 | 0.14932 | 0.023583 | 0.093308 | 0.029925 | 0.1324 | 0.1039 | -0.03067 | -0.089445 | 0.02885 | -0.027111 | -0.010206 | -0.025015 | -0.054607 | -0.079268 | -0.021484 | 0.1951 | 0.069359 | 0.13908 | 0.075701 | 0.17818 | 0.14967 | 0.015106 | -0.043669 | 0.074626 | 0.018665 | 0.03557 | 0.020761 | -0.008831 | -0.033492 | 0.024292 | -0.06443 | -0.010177 | -0.002096 | 0.052157
2569.8281 | 121.1243 | -116.2994 | 4.5547 | 0.14474 | 0.014425 | 0.08873 | 0.034504 | 0.13698 | 0.099318 | -0.026092 | -0.089445 | 0.033429 | -0.017954 | -0.005627 | -0.029593 | -0.050029 | -0.079268 | -0.012328 | 0.19052 | 0.060201 | 0.13451 | 0.08028 | 0.18276 | 0.14509 | 0.019684 | -0.043669 | 0.079205 | 0.027822 | 0.040149 | 0.016183 | -0.004253 | -0.033492 | 0.033448 | -0.059852 | -0.010177 | 0.011639 | 0.061314
2571.5938 | 121.019 | -116.185 | 4.7195 | 0.1539 | 0.014425 | 0.097887 | 0.039082 | 0.1324 | 0.099318 | -0.03067 | -0.089445 | 0.024271 | -0.017954 | -0.010206 | -0.029593 | -0.059185 | -0.079268 | -0.021484 | 0.19968 | 0.060201 | 0.14366 | 0.084858 | 0.17818 | 0.14509 | 0.015106 | -0.043669 | 0.070047 | 0.027822 | 0.03557 | 0.016183 | -0.013409 | -0.033492 | 0.024292 | -0.059852 | -0.010177 | 0.011639 | 0.061314
2573.3594 | 121.0739 | -116.4322 | 4.4861 | 0.14474 | 0.023583 | 0.097887 | 0.034504 | 0.1324 | 0.1039 | -0.03067 | -0.089445 | 0.02885 | -0.027111 | -0.005627 | -0.034171 | -0.054607 | -0.079268 | -0.021484 | 0.19052 | 0.069359 | 0.14366 | 0.08028 | 0.17818 | 0.14967 | 0.015106 | -0.043669 | 0.074626 | 0.018665 | 0.040149 | 0.011605 | -0.008831 | -0.033492 | 0.024292 | -0.055274 | -0.010177 | 0.00706 | 0.052157
2575.1406 | 121.051 | -116.5375 | 4.3945 | 0.14932 | 0.023583 | 0.10247 | 0.034504 | 0.1324 | 0.099318 | -0.026092 | -0.084867 | 0.02885 | -0.027111 | -0.010206 | -0.034171 | -0.059185 | -0.07469 | -0.026063 | 0.1951 | 0.069359 | 0.14824 | 0.08028 | 0.17818 | 0.14509 | 0.019684 | -0.039091 | 0.074626 | 0.018665 | 0.03557 | 0.011605 | -0.013409 | -0.028914 | 0.019713 | -0.050696 | -0.010177 | 0.00706 | 0.047579
2576.8594 | 121.0419 | -116.4368 | 4.5044 | 0.14932 | 0.023583 | 0.093308 | 0.039082 | 0.13698 | 0.1039 | -0.026092 | -0.080288 | 0.033429 | -0.022532 | -0.005627 | -0.034171 | -0.054607 | -0.079268 | -0.016906 | 0.1951 | 0.069359 | 0.13908 | 0.084858 | 0.18276 | 0.14967 | 0.019684 | -0.034512 | 0.079205 | 0.023244 | 0.040149 | 0.011605 | -0.008831 | -0.033492 | 0.02887 | -0.046117 | -0.00102 | 0.011639 | 0.056736
2578.625 | 121.0327 | -116.4093 | 4.4952 | 0.14932 | 0.028162 | 0.093308 | 0.034504 | 0.13698 | 0.09474 | -0.035248 | -0.084867 | 0.02885 | -0.027111 | -0.010206 | -0.034171 | -0.059185 | -0.07469 | -0.026063 | 0.1951 | 0.073938 | 0.13908 | 0.08028 | 0.18276 | 0.14052 | 0.010528 | -0.039091 | 0.074626 | 0.018665 | 0.03557 | 0.011605 | -0.013409 | -0.028914 | 0.019713 | -0.050696 | -0.010177 | 0.00706 | 0.047579
2580.4062 | 121.0693 | -116.3681 | 4.5456 | 0.1539 | 0.019004 | 0.10247 | 0.039082 | 0.13698 | 0.099318 | -0.021514 | -0.089445 | 0.024271 | -0.027111 | -0.010206 | -0.029593 | -0.059185 | -0.07469 | -0.016906 | 0.19968 | 0.06478 | 0.14824 | 0.084858 | 0.18276 | 0.14509 | 0.024262 | -0.043669 | 0.070047 | 0.018665 | 0.03557 | 0.016183 | -0.013409 | -0.028914 | 0.02887 | -0.059852 | -0.014755 | 0.002482 | 0.047579
2582.1094 | 121.0693 | -116.3361 | 4.5639 | 0.14932 | 0.028162 | 0.10247 | 0.043661 | 0.13698 | 0.1039 | -0.021514 | -0.089445 | 0.033429 | -0.022532 | -0.005627 | -0.029593 | -0.059185 | -0.079268 | -0.021484 | 0.1951 | 0.073938 | 0.14824 | 0.089437 | 0.18276 | 0.14967 | 0.024262 | -0.043669 | 0.079205 | 0.023244 | 0.040149 | 0.016183 | -0.013409 | -0.033492 | 0.024292 | -0.059852 | -0.010177 | 0.007061 | 0.056736
2583.8906 | 121.0968 | -116.423 | 4.4724 | 0.14932 | 0.023583 | 0.097887 | 0.034504 | 0.1324 | 0.1039 | -0.03067 | -0.089445 | 0.024271 | -0.022532 | -0.005627 | -0.025015 | -0.059185 | -0.07469 | -0.016906 | 0.1951 | 0.069359 | 0.14366 | 0.08028 | 0.17818 | 0.14967 | 0.015106 | -0.043669 | 0.070047 | 0.023244 | 0.040149 | 0.020761 | -0.013409 | -0.028914 | 0.02887 | -0.06443 | -0.014755 | 0.002483 | 0.052158
2585.6719 | 121.0922 | -116.4871 | 4.4128 | 0.14932 | 0.03274 | 0.08873 | 0.034504 | 0.1324 | 0.099318 | -0.03067 | -0.089445 | 0.033429 | -0.027111 | -0.010206 | -0.029593 | -0.059185 | -0.079268 | -0.026063 | 0.1951 | 0.078516 | 0.13451 | 0.08028 | 0.17818 | 0.14509 | 0.015106 | -0.043669 | 0.079205 | 0.018665 | 0.03557 | 0.016183 | -0.013409 | -0.033492 | 0.019713 | -0.059852 | -0.010177 | 0.002482 | 0.052157
2587.4375 | 121.1563 | -116.3315 | 4.4815 | 0.14474 | 0.023583 | 0.097887 | 0.039082 | 0.13698 | 0.10848 | -0.026092 | -0.084867 | 0.033429 | -0.022532 | -0.001048 | -0.025015 | -0.063763 | -0.079268 | -0.012328 | 0.19052 | 0.069359 | 0.14366 | 0.084858 | 0.18276 | 0.15425 | 0.019684 | -0.039091 | 0.079205 | 0.023244 | 0.044728 | 0.020761 | -0.017987 | -0.033492 | 0.033448 | -0.059852 | -0.005599 | 0.002483 | 0.056736
2589.1562 | 121.1197 | -116.4597 | 4.3762 | 0.14474 | 0.019004 | 0.08873 | 0.034504 | 0.13698 | 0.099318 | -0.03067 | -0.094024 | 0.033429 | -0.027111 | -0.005627 | -0.029593 | -0.059185 | -0.079268 | -0.016906 | 0.19052 | 0.06478 | 0.13451 | 0.08028 | 0.18276 | 0.14509 | 0.015106 | -0.048248 | 0.079205 | 0.018665 | 0.040149 | 0.016183 | -0.013409 | -0.033492 | 0.02887 | -0.064431 | -0.014756 | 0.002482 | 0.052157
2590.9375 | 121.0144 | -116.1667 | 4.7379 | 0.14932 | 0.019004 | 0.093308 | 0.034504 | 0.14156 | 0.10848 | -0.021514 | -0.089445 | 0.024271 | -0.027111 | 0.003531 | -0.034171 | -0.059185 | -0.07469 | -0.00775 | 0.1951 | 0.06478 | 0.13908 | 0.08028 | 0.18733 | 0.15425 | 0.024262 | -0.043669 | 0.070047 | 0.018665 | 0.049307 | 0.011605 | -0.013409 | -0.028914 | 0.038026 | -0.055274 | -0.014755 | 0.00706 | 0.047579
2592.7188 | 121.0098 | -116.3864 | 4.5181 | 0.1539 | 0.019004 | 0.093308 | 0.039082 | 0.1324 | 0.099318 | -0.021514 | -0.089445 | 0.024271 | -0.022532 | -0.010206 | -0.034171 | -0.063763 | -0.07469 | -0.026063 | 0.19968 | 0.06478 | 0.13908 | 0.084858 | 0.17818 | 0.14509 | 0.024262 | -0.043669 | 0.070047 | 0.023244 | 0.03557 | 0.011605 | -0.017987 | -0.028914 | 0.019713 | -0.055274 | -0.014755 | 0.011639 | 0.052158
2594.5 | 121.0785 | -116.4368 | 4.454 | 0.14017 | 0.023583 | 0.093308 | 0.039082 | 0.1324 | 0.1039 | -0.026092 | -0.084867 | 0.02885 | -0.027111 | -0.014785 | -0.029593 | -0.054607 | -0.07469 | -0.021484 | 0.18594 | 0.069359 | 0.13908 | 0.084858 | 0.17818 | 0.14967 | 0.019684 | -0.039091 | 0.074626 | 0.018665 | 0.030991 | 0.016183 | -0.008831 | -0.028914 | 0.024292 | -0.055274 | -0.010177 | 0.002482 | 0.047579
2596.2344 | 121.0556 | -111.1816 | 9.7412 | 0.14932 | 0.023583 | 0.093308 | 0.034504 | 0.1324 | 0.099318 | -0.035248 | -0.094024 | 0.015114 | -0.031689 | -0.014785 | -0.029593 | -0.050029 | -0.07469 | -0.016906 | 0.1951 | 0.069359 | 0.13908 | 0.08028 | 0.17818 | 0.14509 | 0.010528 | -0.048248 | 0.06089 | 0.014087 | 0.030991 | 0.016183 | -0.004253 | -0.028914 | 0.02887 | -0.064431 | -0.019334 | -0.002096 | 0.043001
2598 | 121.1334 | -112.6831 | 8.139 | 0.14017 | 0.014425 | 0.093308 | 0.029925 | 0.12782 | 0.09474 | -0.035248 | -0.084867 | 0.024271 | -0.022532 | -0.001048 | -0.025015 | -0.050029 | -0.070112 | -0.012328 | 0.18594 | 0.060201 | 0.13908 | 0.075701 | 0.1736 | 0.14052 | 0.010528 | -0.039091 | 0.070047 | 0.023244 | 0.044728 | 0.020761 | -0.004253 | -0.024336 | 0.033448 | -0.059852 | -0.014755 | 0.002483 | 0.04758
2599.7812 | 121.0236 | -114.2029 | 6.6879 | 0.14932 | 0.019004 | 0.097887 | 0.029925 | 0.1324 | 0.099318 | -0.026092 | -0.084867 | 0.033429 | -0.022532 | -0.001048 | -0.034171 | -0.054607 | -0.070112 | -0.016906 | 0.1951 | 0.06478 | 0.14366 | 0.075701 | 0.17818 | 0.14509 | 0.019684 | -0.039091 | 0.079205 | 0.023244 | 0.044728 | 0.011605 | -0.008831 | -0.024336 | 0.02887 | -0.050696 | -0.014755 | 0.011639 | 0.04758
2601.5625 | 121.0464 | -114.8712 | 6.0516 | 0.1539 | 0.023583 | 0.093308 | 0.034504 | 0.13698 | 0.099318 | -0.03067 | -0.089445 | 0.02885 | -0.022532 | -0.005627 | -0.025015 | -0.059185 | -0.079268 | -0.016906 | 0.19968 | 0.069359 | 0.13908 | 0.08028 | 0.18276 | 0.14509 | 0.015106 | -0.043669 | 0.074626 | 0.023244 | 0.040149 | 0.020761 | -0.013409 | -0.033492 | 0.02887 | -0.06443 | -0.010177 | 0.002483 | 0.056736
2603.3438 | 121.0693 | -111.5204 | 9.343 | 0.14474 | 0.019004 | 0.079572 | 0.029925 | 0.12325 | 0.090161 | -0.026092 | -0.084867 | 0.015114 | -0.031689 | -0.014785 | -0.025015 | -0.050029 | -0.065533 | -0.012328 | 0.19052 | 0.06478 | 0.12535 | 0.075701 | 0.16902 | 0.13594 | 0.019684 | -0.039091 | 0.06089 | 0.014087 | 0.030991 | 0.020761 | -0.004253 | -0.019757 | 0.033448 | -0.059852 | -0.019334 | -0.006674 | 0.033844
2605.0469 | 121.1014 | -111.3968 | 9.4025 | 0.14474 | 0.009846 | 0.093308 | 0.034504 | 0.12782 | 0.090161 | -0.035248 | -0.089445 | 0.015114 | -0.031689 | -0.014785 | -0.029593 | -0.054607 | -0.07469 | -0.016906 | 0.19052 | 0.055622 | 0.13908 | 0.08028 | 0.1736 | 0.13594 | 0.010528 | -0.043669 | 0.06089 | 0.014087 | 0.030991 | 0.016183 | -0.008831 | -0.028914 | 0.02887 | -0.059852 | -0.014755 | -0.002096 | 0.043001
2606.8125 | 121.1288 | -111.9324 | 8.8715 | 0.14474 | 0.019004 | 0.08873 | 0.034504 | 0.12782 | 0.090161 | -0.035248 | -0.094024 | 0.02885 | -0.027111 | -0.014785 | -0.020437 | -0.050029 | -0.07469 | -0.016906 | 0.19052 | 0.06478 | 0.13451 | 0.08028 | 0.1736 | 0.13594 | 0.010528 | -0.048248 | 0.074626 | 0.018665 | 0.030991 | 0.025339 | -0.004253 | -0.028914 | 0.02887 | -0.073587 | -0.019334 | -0.006674 | 0.047579
2608.5781 | 121.1655 | -112.294 | 8.5007 | 0.14017 | 0.009846 | 0.093308 | 0.029925 | 0.12782 | 0.099318 | -0.035248 | -0.094024 | 0.02885 | -0.027111 | -0.014785 | -0.025015 | -0.054607 | -0.070112 | -0.012328 | 0.18594 | 0.055622 | 0.13908 | 0.075701 | 0.1736 | 0.14509 | 0.010528 | -0.048248 | 0.074626 | 0.018665 | 0.030991 | 0.020761 | -0.008831 | -0.024336 | 0.033448 | -0.069009 | -0.023912 | -0.002096 | 0.043001
2610.3594 | 121.0739 | -112.532 | 8.3084 | 0.14474 | 0.019004 | 0.093308 | 0.029925 | 0.1324 | 0.09474 | -0.03067 | -0.089445 | 0.038008 | -0.027111 | -0.005627 | -0.029593 | -0.054607 | -0.070112 | -0.016906 | 0.19052 | 0.06478 | 0.13908 | 0.075701 | 0.17818 | 0.14052 | 0.015106 | -0.043669 | 0.083784 | 0.018665 | 0.040149 | 0.016183 | -0.008831 | -0.024336 | 0.02887 | -0.059852 | -0.019333 | 0.002482 | 0.043001
2612.0469 | 121.0922 | -112.5229 | 8.2901 | 0.14474 | 0.019004 | 0.08873 | 0.025347 | 0.1324 | 0.090161 | -0.035248 | -0.094024 | 0.02885 | -0.027111 | -0.010206 | -0.029593 | -0.054607 | -0.079268 | -0.021484 | 0.19052 | 0.06478 | 0.13451 | 0.071123 | 0.17818 | 0.13594 | 0.010528 | -0.048248 | 0.074626 | 0.018665 | 0.03557 | 0.016183 | -0.008831 | -0.033492 | 0.024292 | -0.064431 | -0.014756 | 0.002482 | 0.052157
2613.8281 | 121.1517 | -111.232 | 9.5673 | 0.14474 | 0.019004 | 0.084151 | 0.034504 | 0.12325 | 0.090161 | -0.026092 | -0.089445 | 0.024271 | -0.027111 | -0.014785 | -0.025015 | -0.054607 | -0.079268 | -0.016906 | 0.19052 | 0.06478 | 0.12993 | 0.08028 | 0.16902 | 0.13594 | 0.019684 | -0.043669 | 0.070047 | 0.018665 | 0.030991 | 0.020761 | -0.008831 | -0.033492 | 0.02887 | -0.06443 | -0.010177 | -0.002096 | 0.052157
2615.6094 | 121.0876 | -111.8408 | 8.9859 | 0.14474 | 0.014425 | 0.097887 | 0.039082 | 0.1324 | 0.099318 | -0.035248 | -0.089445 | 0.033429 | -0.027111 | -0.014785 | -0.025015 | -0.050029 | -0.07469 | -0.00775 | 0.19052 | 0.060201 | 0.14366 | 0.084858 | 0.17818 | 0.14509 | 0.010528 | -0.043669 | 0.079205 | 0.018665 | 0.030991 | 0.020761 | -0.004253 | -0.028914 | 0.038026 | -0.06443 | -0.014755 | -0.002096 | 0.047579
2617.3125 | 121.1334 | -112.0834 | 8.7112 | 0.14932 | 0.009846 | 0.08873 | 0.034504 | 0.1324 | 0.090161 | -0.03067 | -0.089445 | 0.02885 | -0.022532 | -0.010206 | -0.025015 | -0.050029 | -0.079268 | -0.012328 | 0.1951 | 0.055622 | 0.13451 | 0.08028 | 0.17818 | 0.13594 | 0.015106 | -0.043669 | 0.074626 | 0.023244 | 0.03557 | 0.020761 | -0.004253 | -0.033492 | 0.033448 | -0.06443 | -0.010177 | 0.002483 | 0.056736
2619.0781 | 121.0144 | -87.4832 | 33.4671 | 0.11727 | 0.000689 | 0.061258 | 0.01619 | 0.10951 | 0.076426 | -0.048983 | -0.11692 | 0.005956 | -0.05458 | -0.042259 | -0.006702 | -0.027139 | -0.056376 | 0.005985 | 0.16305 | 0.046465 | 0.10703 | 0.061966 | 0.15529 | 0.1222 | -0.003207 | -0.07114 | 0.051732 | -0.008804 | 0.003517 | 0.039074 | 0.018637 | -0.0106 | 0.051761 | -0.11021 | -0.06054 | -0.047878 | 0.001796
2620.8594 | 121.0144 | -89.4196 | 31.4941 | 0.12185 | -0.00389 | 0.079572 | 0.01619 | 0.11409 | 0.076426 | -0.053561 | -0.10776 | 0.005956 | -0.045424 | -0.03768 | -0.002124 | -0.040873 | -0.051798 | 0.010563 | 0.16763 | 0.041886 | 0.12535 | 0.061966 | 0.15987 | 0.1222 | -0.007785 | -0.061983 | 0.051732 | 0.000352 | 0.008096 | 0.043652 | 0.004903 | -0.006022 | 0.056339 | -0.10563 | -0.055961 | -0.0433 | 0.006374
2622.5781 | 121.1243 | -91.7404 | 29.0451 | 0.12185 | 0.000689 | 0.070415 | 0.025347 | 0.11409 | 0.076426 | -0.044405 | -0.11234 | 0.005956 | -0.050002 | -0.028522 | -0.015859 | -0.036295 | -0.056376 | -0.003172 | 0.16763 | 0.046465 | 0.11619 | 0.071123 | 0.15987 | 0.1222 | 0.001371 | -0.066562 | 0.051732 | -0.004226 | 0.017254 | 0.029917 | 0.009481 | -0.0106 | 0.042604 | -0.096479 | -0.055962 | -0.034143 | 0.006374
2624.3594 | 121.0876 | -94.4275 | 26.3992 | 0.12643 | 0.000689 | 0.070415 | 0.01619 | 0.11867 | 0.081005 | -0.039826 | -0.10318 | 0.005956 | -0.045424 | -0.028522 | -0.006702 | -0.036295 | -0.060955 | -0.003172 | 0.1722 | 0.046465 | 0.11619 | 0.061966 | 0.16444 | 0.12678 | 0.00595 | -0.057405 | 0.051732 | 0.000352 | 0.017254 | 0.039074 | 0.009481 | -0.015179 | 0.042604 | -0.096479 | -0.042226 | -0.038722 | 0.015531
2626.0781 | 121.106 | -92.0837 | 28.7338 | 0.13101 | 0.000689 | 0.070415 | 0.011611 | 0.10951 | 0.081005 | -0.048983 | -0.10776 | 0.005956 | -0.040846 | -0.023943 | -0.015859 | -0.036295 | -0.060955 | 0.001406 | 0.17678 | 0.046465 | 0.11619 | 0.057387 | 0.15529 | 0.12678 | -0.003207 | -0.061983 | 0.051732 | 0.00493 | 0.021833 | 0.029917 | 0.009481 | -0.015179 | 0.047182 | -0.0919 | -0.046804 | -0.024987 | 0.020109
2627.8594 | 121.0464 | -89.7675 | 31.0776 | 0.13101 | -0.00389 | 0.070415 | 0.011611 | 0.10951 | 0.085583 | -0.048983 | -0.11234 | 0.001377 | -0.045424 | -0.033101 | -0.002124 | -0.031717 | -0.060955 | 0.005985 | 0.17678 | 0.041886 | 0.11619 | 0.057387 | 0.15529 | 0.13136 | -0.003207 | -0.066562 | 0.047153 | 0.000352 | 0.012675 | 0.043652 | 0.014059 | -0.015179 | 0.051761 | -0.11021 | -0.051383 | -0.0433 | 0.015531
2629.5781 | 121.1426 | -87.8311 | 32.9773 | 0.12643 | -0.00389 | 0.065837 | 0.007033 | 0.10493 | 0.067269 | -0.048983 | -0.10776 | 0.001377 | -0.050002 | -0.03768 | 0.002454 | -0.031717 | -0.056376 | 0.001406 | 0.1722 | 0.041886 | 0.11161 | 0.052809 | 0.15071 | 0.11304 | -0.003207 | -0.061983 | 0.047153 | -0.004226 | 0.008096 | 0.04823 | 0.014059 | -0.0106 | 0.047182 | -0.11021 | -0.051383 | -0.052456 | 0.006374
2631.3594 | 121.1197 | -87.6755 | 33.1055 | 0.13101 | 0.000689 | 0.065837 | 0.007033 | 0.10493 | 0.076426 | -0.053561 | -0.11234 | 0.001377 | -0.050002 | -0.033101 | -0.006702 | -0.031717 | -0.060955 | 0.001406 | 0.17678 | 0.046465 | 0.11161 | 0.052809 | 0.15071 | 0.1222 | -0.007785 | -0.066562 | 0.047153 | -0.004226 | 0.012675 | 0.039074 | 0.014059 | -0.015179 | 0.047182 | -0.10564 | -0.051383 | -0.0433 | 0.010953
2633.125 | 121.0007 | -87.7716 | 33.0963 | 0.12185 | 0.000689 | 0.070415 | 0.011611 | 0.11409 | 0.085583 | -0.048983 | -0.10776 | 0.005956 | -0.050002 | -0.03768 | -0.002124 | -0.036295 | -0.060955 | 0.010563 | 0.16763 | 0.046465 | 0.11619 | 0.057387 | 0.15987 | 0.13136 | -0.003207 | -0.061983 | 0.051732 | -0.004226 | 0.008096 | 0.043652 | 0.009481 | -0.015179 | 0.056339 | -0.10563 | -0.046804 | -0.047878 | 0.010953
2634.9062 | 121.019 | -92.0151 | 28.775 | 0.12643 | -0.00389 | 0.074994 | 0.01619 | 0.11867 | 0.076426 | -0.035248 | -0.10318 | 0.010535 | -0.045424 | -0.033101 | -0.006702 | -0.036295 | -0.056376 | 0.001406 | 0.1722 | 0.041886 | 0.12077 | 0.061966 | 0.16444 | 0.1222 | 0.010528 | -0.057405 | 0.056311 | 0.000352 | 0.012675 | 0.039074 | 0.009481 | -0.0106 | 0.047182 | -0.096479 | -0.046805 | -0.038722 | 0.010952
2636.6875 | 120.9869 | -92.6102 | 28.1616 | 0.13559 | 0.000689 | 0.074994 | 0.007033 | 0.11409 | 0.085583 | -0.048983 | -0.10318 | 0.010535 | -0.050002 | -0.033101 | -0.011281 | -0.036295 | -0.060955 | 0.001406 | 0.18136 | 0.046465 | 0.12077 | 0.052809 | 0.15987 | 0.13136 | -0.003207 | -0.057405 | 0.056311 | -0.004226 | 0.012675 | 0.034495 | 0.009481 | -0.015179 | 0.047182 | -0.0919 | -0.042226 | -0.038721 | 0.010953
2638.4688 | 120.9412 | -91.8549 | 28.9215 | 0.12185 | 0.000689 | 0.070415 | 0.025347 | 0.11867 | 0.076426 | -0.048983 | -0.10776 | 0.005956 | -0.050002 | -0.033101 | -0.006702 | -0.022561 | -0.060955 | 0.005985 | 0.16763 | 0.046465 | 0.11619 | 0.071123 | 0.16444 | 0.1222 | -0.003207 | -0.061983 | 0.051732 | -0.004226 | 0.012675 | 0.039074 | 0.023215 | -0.015179 | 0.051761 | -0.10106 | -0.046804 | -0.0433 | 0.010953
2640.1875 | 120.9366 | -91.8869 | 28.8986 | 0.12643 | -0.00389 | 0.070415 | 0.01619 | 0.10951 | 0.071848 | -0.044405 | -0.11692 | 0.015114 | -0.040846 | -0.033101 | -0.002124 | -0.036295 | -0.065533 | 0.010563 | 0.1722 | 0.041886 | 0.11619 | 0.061966 | 0.15529 | 0.11762 | 0.001371 | -0.07114 | 0.06089 | 0.00493 | 0.012675 | 0.043652 | 0.009481 | -0.019757 | 0.056339 | -0.11479 | -0.051383 | -0.038722 | 0.024687
2641.9688 | 121.0327 | -91.6901 | 28.981 | 0.12185 | -0.00389 | 0.070415 | 0.01619 | 0.10951 | 0.076426 | -0.053561 | -0.11692 | 0.010535 | -0.040846 | -0.033101 | -0.002124 | -0.040873 | -0.065533 | 0.005985 | 0.16763 | 0.041886 | 0.11619 | 0.061966 | 0.15529 | 0.1222 | -0.007785 | -0.07114 | 0.056311 | 0.00493 | 0.012675 | 0.043652 | 0.004903 | -0.019757 | 0.051761 | -0.11479 | -0.051383 | -0.038722 | 0.024687
2643.75 | 120.9045 | -91.9373 | 28.8162 | 0.12185 | 0.005267 | 0.079572 | 0.011611 | 0.11867 | 0.071848 | -0.053561 | -0.10776 | 0.005956 | -0.040846 | -0.033101 | -0.006702 | -0.036295 | -0.065533 | -0.00775 | 0.16763 | 0.051043 | 0.12535 | 0.057387 | 0.16444 | 0.11762 | -0.007785 | -0.061983 | 0.051732 | 0.00493 | 0.012675 | 0.039074 | 0.009481 | -0.019757 | 0.038026 | -0.10106 | -0.042226 | -0.034144 | 0.024687
2645.5312 | 120.9824 | -40.8417 | 80.0812 | 0.080646 | -0.040521 | 0.024629 | -0.025017 | 0.06831 | 0.030642 | -0.090186 | -0.15354 | -0.030674 | -0.091207 | -0.069733 | 0.039079 | 0.004908 | -0.04722 | 0.051766 | 0.12642 | 0.005255 | 0.070405 | 0.020759 | 0.11409 | 0.076418 | -0.04441 | -0.10777 | 0.015102 | -0.045431 | -0.023957 | 0.084855 | 0.050684 | -0.001444 | 0.097542 | -0.19262 | -0.10632 | -0.13029 | -0.043987
2647.25 | 121.1014 | -40.5945 | 80.3055 | 0.085224 | -0.0451 | 0.024629 | -0.029595 | 0.063733 | 0.030642 | -0.08103 | -0.14897 | -0.030674 | -0.086628 | -0.069733 | 0.039079 | 0.009486 | -0.042641 | 0.04261 | 0.131 | 0.000676 | 0.070405 | 0.016181 | 0.10951 | 0.076418 | -0.035254 | -0.10319 | 0.015102 | -0.040852 | -0.023957 | 0.084855 | 0.055262 | 0.003135 | 0.088386 | -0.18804 | -0.10632 | -0.12571 | -0.043987
2649.0469 | 121.0968 | -40.4434 | 80.4474 | 0.089802 | -0.0451 | 0.024629 | -0.029595 | 0.06831 | 0.039799 | -0.094765 | -0.14897 | -0.035253 | -0.091207 | -0.069733 | 0.039079 | 0.004908 | -0.038063 | 0.04261 | 0.13558 | 0.000676 | 0.070405 | 0.016181 | 0.11409 | 0.085575 | -0.048989 | -0.10319 | 0.010523 | -0.045431 | -0.023957 | 0.084855 | 0.050684 | 0.007713 | 0.088386 | -0.18804 | -0.1109 | -0.13029 | -0.053144
2650.7656 | 121.0556 | -40.3656 | 80.5801 | 0.085224 | -0.040521 | 0.033786 | -0.025017 | 0.072888 | 0.026064 | -0.085608 | -0.14897 | -0.030674 | -0.091207 | -0.074312 | 0.034501 | 0.009486 | -0.042641 | 0.056344 | 0.131 | 0.005255 | 0.079562 | 0.020759 | 0.11866 | 0.07184 | -0.039832 | -0.10319 | 0.015102 | -0.045431 | -0.028536 | 0.080277 | 0.055262 | 0.003135 | 0.10212 | -0.18347 | -0.10632 | -0.12571 | -0.048566
2652.5312 | 121.1609 | -40.2466 | 80.6717 | 0.080646 | -0.040521 | 0.033786 | -0.029595 | 0.072888 | 0.039799 | -0.085608 | -0.15354 | -0.035253 | -0.095785 | -0.078891 | 0.034501 | 0.004908 | -0.038063 | 0.047188 | 0.12642 | 0.005255 | 0.079562 | 0.016181 | 0.11866 | 0.085575 | -0.039832 | -0.10777 | 0.010523 | -0.050009 | -0.033115 | 0.080277 | 0.050684 | 0.007713 | 0.092964 | -0.18805 | -0.11548 | -0.13029 | -0.057722
2654.2969 | 121.1746 | -40.1184 | 80.8182 | 0.080646 | -0.040521 | 0.033786 | -0.025017 | 0.063733 | 0.035221 | -0.085608 | -0.15354 | -0.044411 | -0.08205 | -0.074312 | 0.039079 | 0.004908 | -0.038063 | 0.04261 | 0.12642 | 0.005255 | 0.079562 | 0.020759 | 0.10951 | 0.080997 | -0.039832 | -0.10777 | 0.001365 | -0.036274 | -0.028536 | 0.084855 | 0.050684 | 0.007713 | 0.088386 | -0.19262 | -0.11548 | -0.12113 | -0.043987
2656.0312 | 121.1655 | -40.0314 | 80.928 | 0.089802 | -0.035942 | 0.024629 | -0.025017 | 0.072888 | 0.035221 | -0.090186 | -0.14439 | -0.026096 | -0.091207 | -0.074312 | 0.039079 | 0.009486 | -0.04722 | 0.047188 | 0.13558 | 0.009834 | 0.070405 | 0.020759 | 0.11866 | 0.080997 | -0.04441 | -0.098611 | 0.01968 | -0.045431 | -0.028536 | 0.084855 | 0.055262 | -0.001444 | 0.092964 | -0.18347 | -0.097167 | -0.13029 | -0.043987
2657.7969 | 121.1151 | -39.9536 | 81.0745 | 0.080646 | -0.0451 | 0.029208 | -0.020438 | 0.06831 | 0.035221 | -0.090186 | -0.14897 | -0.039832 | -0.086628 | -0.074312 | 0.039079 | 0.009486 | -0.042641 | 0.047188 | 0.12642 | 0.000676 | 0.074984 | 0.025338 | 0.11409 | 0.080997 | -0.04441 | -0.10319 | 0.005944 | -0.040852 | -0.028536 | 0.084855 | 0.055262 | 0.003135 | 0.092964 | -0.18804 | -0.10632 | -0.12571 | -0.043987
2659.5625 | 121.2708 | -39.7888 | 81.134 | 0.085224 | -0.0451 | 0.029208 | -0.034174 | 0.06831 | 0.039799 | -0.085608 | -0.14897 | -0.035253 | -0.086628 | -0.074312 | 0.034501 | 0.014064 | -0.038063 | 0.038032 | 0.131 | 0.000676 | 0.074984 | 0.011602 | 0.11409 | 0.085575 | -0.039832 | -0.10319 | 0.010523 | -0.040852 | -0.028536 | 0.080277 | 0.05984 | 0.007713 | 0.083808 | -0.18347 | -0.1109 | -0.12113 | -0.048565
2661.2656 | 121.2067 | -39.7202 | 81.2439 | 0.085224 | -0.0451 | 0.038365 | -0.029595 | 0.06831 | 0.035221 | -0.090186 | -0.15354 | -0.035253 | -0.086628 | -0.074312 | 0.039079 | 0.009486 | -0.042641 | 0.04261 | 0.131 | 0.000676 | 0.084141 | 0.016181 | 0.11409 | 0.080997 | -0.04441 | -0.10777 | 0.010523 | -0.040852 | -0.028536 | 0.084855 | 0.055262 | 0.003135 | 0.088386 | -0.19262 | -0.1109 | -0.12571 | -0.043987
2663.0469 | 121.2799 | -39.6057 | 81.3721 | 0.089802 | -0.0451 | 0.024629 | -0.034174 | 0.072888 | 0.035221 | -0.090186 | -0.14897 | -0.039832 | -0.086628 | -0.069733 | 0.034501 | 0.014064 | -0.04722 | 0.038032 | 0.13558 | 0.000676 | 0.070405 | 0.011602 | 0.11866 | 0.080997 | -0.04441 | -0.10319 | 0.005944 | -0.040852 | -0.023957 | 0.080277 | 0.05984 | -0.001444 | 0.083808 | -0.18347 | -0.10175 | -0.12113 | -0.039408
2664.8281 | 121.225 | -39.5279 | 81.4865 | 0.080646 | -0.040521 | 0.024629 | -0.029595 | 0.063733 | 0.039799 | -0.090186 | -0.15354 | -0.035253 | -0.086628 | -0.074312 | 0.039079 | 0.018642 | -0.042641 | 0.051766 | 0.12642 | 0.005255 | 0.070405 | 0.016181 | 0.10951 | 0.085575 | -0.04441 | -0.10777 | 0.010523 | -0.040852 | -0.028536 | 0.084855 | 0.064418 | 0.003135 | 0.097542 | -0.19262 | -0.1109 | -0.12571 | -0.043987
2666.6094 | 121.2204 | -39.2303 | 81.7657 | 0.085224 | -0.0451 | 0.020051 | -0.020438 | 0.06831 | 0.030642 | -0.090186 | -0.14897 | -0.039832 | -0.095785 | -0.078891 | 0.039079 | 0.014064 | -0.033484 | 0.056344 | 0.131 | 0.000676 | 0.065827 | 0.025338 | 0.11409 | 0.076418 | -0.04441 | -0.10319 | 0.005944 | -0.050009 | -0.033115 | 0.084855 | 0.05984 | 0.012292 | 0.10212 | -0.18804 | -0.11548 | -0.13486 | -0.062301
2668.3125 | 121.225 | -32.1213 | 88.9526 | 0.080646 | -0.049678 | 0.015472 | -0.034174 | 0.054577 | 0.026064 | -0.085608 | -0.15354 | -0.039832 | -0.091207 | -0.078891 | 0.048236 | 0.027798 | -0.038063 | 0.051766 | 0.12642 | -0.003902 | 0.061248 | 0.011602 | 0.10035 | 0.07184 | -0.039832 | -0.10777 | 0.005944 | -0.045431 | -0.033115 | 0.094012 | 0.073574 | 0.007713 | 0.097542 | -0.20178 | -0.11548 | -0.13944 | -0.053144
2670.0938 | 121.2982 | -31.929 | 89.0762 | 0.071489 | -0.049678 | 0.024629 | -0.034174 | 0.059155 | 0.021485 | -0.085608 | -0.15812 | -0.044411 | -0.095785 | -0.074312 | 0.052814 | 0.018642 | -0.042641 | 0.051766 | 0.11726 | -0.003902 | 0.070405 | 0.011602 | 0.10493 | 0.067261 | -0.039832 | -0.11235 | 0.001365 | -0.050009 | -0.028536 | 0.09859 | 0.064418 | 0.003135 | 0.097542 | -0.21094 | -0.11548 | -0.1486 | -0.053144
2671.875 | 121.2753 | -35.9299 | 85.0891 | 0.076067 | -0.0451 | 0.024629 | -0.029595 | 0.06831 | 0.035221 | -0.085608 | -0.15812 | -0.035253 | -0.091207 | -0.078891 | 0.043657 | 0.009486 | -0.04722 | 0.047188 | 0.12184 | 0.000676 | 0.070405 | 0.016181 | 0.11409 | 0.080997 | -0.039832 | -0.11235 | 0.010523 | -0.045431 | -0.033115 | 0.089433 | 0.055262 | -0.001444 | 0.092964 | -0.20178 | -0.1109 | -0.13486 | -0.043987
2673.6719 | 121.2708 | -29.892 | 91.1499 | 0.071489 | -0.049678 | 0.024629 | -0.034174 | 0.059155 | 0.021485 | -0.094765 | -0.15812 | -0.039832 | -0.095785 | -0.088049 | 0.052814 | 0.014064 | -0.04722 | 0.051766 | 0.11726 | -0.003902 | 0.070405 | 0.011602 | 0.10493 | 0.067261 | -0.048989 | -0.11235 | 0.005944 | -0.050009 | -0.042273 | 0.09859 | 0.05984 | -0.001444 | 0.097542 | -0.21094 | -0.1109 | -0.1486 | -0.048565
2675.4375 | 121.2799 | -29.1275 | 91.9235 | 0.071489 | -0.054257 | 0.020051 | -0.034174 | 0.059155 | 0.012329 | -0.094765 | -0.15354 | -0.039832 | -0.10036 | -0.074312 | 0.043657 | 0.014064 | -0.038063 | 0.056344 | 0.11726 | -0.008481 | 0.065827 | 0.011602 | 0.10493 | 0.058105 | -0.048989 | -0.10777 | 0.005944 | -0.054587 | -0.028536 | 0.089433 | 0.05984 | 0.007713 | 0.10212 | -0.1972 | -0.11548 | -0.14402 | -0.0623
2677.1562 | 121.2021 | -29.0085 | 92.1295 | 0.071489 | -0.054257 | 0.020051 | -0.034174 | 0.059155 | 0.026064 | -0.094765 | -0.1627 | -0.04899 | -0.10036 | -0.078891 | 0.043657 | 0.02322 | -0.038063 | 0.056344 | 0.11726 | -0.008481 | 0.065827 | 0.011602 | 0.10493 | 0.07184 | -0.048989 | -0.11693 | -0.003214 | -0.054587 | -0.033115 | 0.089433 | 0.068996 | 0.007713 | 0.10212 | -0.20636 | -0.12464 | -0.14402 | -0.0623
2678.9375 | 121.2158 | -28.3905 | 92.7292 | 0.080646 | -0.049678 | 0.024629 | -0.034174 | 0.054577 | 0.030642 | -0.090186 | -0.15354 | -0.039832 | -0.095785 | -0.08347 | 0.043657 | 0.018642 | -0.033484 | 0.051766 | 0.12642 | -0.003902 | 0.070405 | 0.011602 | 0.10035 | 0.076418 | -0.04441 | -0.10777 | 0.005944 | -0.050009 | -0.037694 | 0.089433 | 0.064418 | 0.012292 | 0.097542 | -0.1972 | -0.12006 | -0.13944 | -0.062301
2680.7188 | 121.2433 | -27.3331 | 93.7958 | 0.071489 | -0.054257 | 0.020051 | -0.025017 | 0.059155 | 0.035221 | -0.094765 | -0.1627 | -0.044411 | -0.10036 | -0.078891 | 0.052814 | 0.018642 | -0.042641 | 0.060923 | 0.11726 | -0.008481 | 0.065827 | 0.020759 | 0.10493 | 0.080997 | -0.048989 | -0.11693 | 0.001365 | -0.054587 | -0.033115 | 0.09859 | 0.064418 | 0.003135 | 0.1067 | -0.21552 | -0.12006 | -0.15318 | -0.057722
2682.4844 | 121.3394 | -28.1021 | 92.9443 | 0.076067 | -0.0451 | 0.020051 | -0.034174 | 0.059155 | 0.035221 | -0.094765 | -0.1627 | -0.04899 | -0.095785 | -0.08347 | 0.043657 | 0.018642 | -0.038063 | 0.060923 | 0.12184 | 0.000676 | 0.065827 | 0.011602 | 0.10493 | 0.080997 | -0.048989 | -0.11693 | -0.003214 | -0.050009 | -0.037694 | 0.089433 | 0.064418 | 0.007713 | 0.1067 | -0.20636 | -0.12464 | -0.13944 | -0.057722
2684.2031 | 121.3531 | -27.7634 | 93.2785 | 0.076067 | -0.054257 | 0.024629 | -0.038752 | 0.059155 | 0.030642 | -0.099343 | -0.16728 | -0.04899 | -0.10036 | -0.08347 | 0.052814 | 0.018642 | -0.042641 | 0.051766 | 0.12184 | -0.008481 | 0.070405 | 0.007024 | 0.10493 | 0.076418 | -0.053567 | -0.1215 | -0.003214 | -0.054587 | -0.037694 | 0.09859 | 0.064418 | 0.003135 | 0.097542 | -0.22009 | -0.12464 | -0.15318 | -0.057722
2685.9844 | 121.3211 | -24.1425 | 96.9635 | 0.076067 | -0.054257 | 0.024629 | -0.038752 | 0.049999 | 0.026064 | -0.099343 | -0.16728 | -0.04899 | -0.095785 | -0.092628 | 0.043657 | 0.02322 | -0.033484 | 0.056344 | 0.12184 | -0.008481 | 0.070405 | 0.007024 | 0.095775 | 0.07184 | -0.053567 | -0.1215 | -0.003214 | -0.050009 | -0.046852 | 0.089433 | 0.068996 | 0.012292 | 0.10212 | -0.21094 | -0.1338 | -0.13944 | -0.062301
2687.75 | 121.3257 | -24.3622 | 96.7667 | 0.071489 | -0.054257 | 0.020051 | -0.034174 | 0.054577 | 0.021485 | -0.10392 | -0.1627 | -0.044411 | -0.10036 | -0.08347 | 0.048236 | 0.014064 | -0.038063 | 0.051766 | 0.11726 | -0.008481 | 0.065827 | 0.011602 | 0.10035 | 0.067261 | -0.058145 | -0.11693 | 0.001365 | -0.054587 | -0.037694 | 0.094012 | 0.05984 | 0.007713 | 0.097542 | -0.21094 | -0.12464 | -0.1486 | -0.0623
2689.4531 | 121.3348 | -24.0875 | 96.9589 | 0.071489 | -0.054257 | 0.010893 | -0.029595 | 0.059155 | 0.030642 | -0.090186 | -0.15812 | -0.04899 | -0.095785 | -0.08347 | 0.048236 | 0.018642 | -0.038063 | 0.056344 | 0.11726 | -0.008481 | 0.056669 | 0.016181 | 0.10493 | 0.076418 | -0.04441 | -0.11235 | -0.003214 | -0.050009 | -0.037694 | 0.094012 | 0.064418 | 0.007713 | 0.10212 | -0.20636 | -0.12006 | -0.14402 | -0.057722
2691.2969 | 121.2067 | -23.9868 | 97.1832 | 0.071489 | -0.058836 | 0.015472 | -0.034174 | 0.054577 | 0.021485 | -0.094765 | -0.1627 | -0.053568 | -0.10494 | -0.08347 | 0.052814 | 0.02322 | -0.038063 | 0.065501 | 0.11726 | -0.01306 | 0.061248 | 0.011602 | 0.10035 | 0.067261 | -0.048989 | -0.11693 | -0.007792 | -0.059166 | -0.037694 | 0.09859 | 0.068996 | 0.007713 | 0.11128 | -0.21552 | -0.12464 | -0.15776 | -0.066879
2693.0781 | 121.257 | -23.8724 | 97.261 | 0.071489 | -0.058836 | 0.006315 | -0.034174 | 0.054577 | 0.016907 | -0.099343 | -0.1627 | -0.04899 | -0.095785 | -0.08347 | 0.052814 | 0.014064 | -0.033484 | 0.056344 | 0.11726 | -0.01306 | 0.052091 | 0.011602 | 0.10035 | 0.062683 | -0.053567 | -0.11693 | -0.003214 | -0.050009 | -0.037694 | 0.09859 | 0.05984 | 0.012292 | 0.10212 | -0.21552 | -0.12922 | -0.1486 | -0.062301
2694.8594 | 121.3257 | -24.7101 | 96.3913 | 0.076067 | -0.049678 | 0.015472 | -0.038752 | 0.059155 | 0.026064 | -0.099343 | -0.1627 | -0.04899 | -0.10494 | -0.078891 | 0.048236 | 0.02322 | -0.028906 | 0.060923 | 0.12184 | -0.003902 | 0.061248 | 0.007024 | 0.10493 | 0.07184 | -0.053567 | -0.11693 | -0.003214 | -0.059166 | -0.033115 | 0.094012 | 0.068996 | 0.01687 | 0.1067 | -0.21094 | -0.13379 | -0.15318 | -0.076036
2696.5781 | 121.3303 | -24.1287 | 97.0001 | 0.071489 | -0.054257 | 0.020051 | -0.038752 | 0.059155 | 0.026064 | -0.10392 | -0.1627 | -0.04899 | -0.10036 | -0.088049 | 0.048236 | 0.009486 | -0.038063 | 0.056344 | 0.11726 | -0.008481 | 0.065827 | 0.007024 | 0.10493 | 0.07184 | -0.058145 | -0.11693 | -0.003214 | -0.054587 | -0.042273 | 0.094012 | 0.055262 | 0.007713 | 0.10212 | -0.21094 | -0.12464 | -0.1486 | -0.0623
2698.3438 | 121.344 | -24.3027 | 96.7575 | 0.071489 | -0.054257 | 0.015472 | -0.038752 | 0.054577 | 0.026064 | -0.094765 | -0.1627 | -0.053568 | -0.10036 | -0.08347 | 0.043657 | 0.027798 | -0.038063 | 0.056344 | 0.11726 | -0.008481 | 0.061248 | 0.007024 | 0.10035 | 0.07184 | -0.048989 | -0.11693 | -0.007792 | -0.054587 | -0.037694 | 0.089433 | 0.073574 | 0.007713 | 0.10212 | -0.20636 | -0.12464 | -0.14402 | -0.0623
2700.0469 | 121.2845 | -24.5453 | 96.611 | 0.071489 | -0.0451 | 0.015472 | -0.034174 | 0.054577 | 0.026064 | -0.10392 | -0.1627 | -0.04899 | -0.10036 | -0.088049 | 0.052814 | 0.018642 | -0.033484 | 0.060923 | 0.11726 | 0.000676 | 0.061248 | 0.011602 | 0.10035 | 0.07184 | -0.058145 | -0.11693 | -0.003214 | -0.054587 | -0.042273 | 0.09859 | 0.064418 | 0.012292 | 0.1067 | -0.21552 | -0.12922 | -0.15318 | -0.066879
2701.8281 | 121.3303 | -23.2773 | 97.8653 | 0.071489 | -0.054257 | 0.015472 | -0.038752 | 0.059155 | 0.016907 | -0.10392 | -0.1627 | -0.04899 | -0.10494 | -0.092628 | 0.048236 | 0.02322 | -0.038063 | 0.060923 | 0.11726 | -0.008481 | 0.061248 | 0.007024 | 0.10493 | 0.062683 | -0.058145 | -0.11693 | -0.003214 | -0.059166 | -0.046852 | 0.094012 | 0.068996 | 0.007713 | 0.1067 | -0.21094 | -0.12464 | -0.15318 | -0.066879
2703.5469 | 121.2936 | -24.0784 | 97.0779 | 0.071489 | -0.054257 | 0.020051 | -0.034174 | 0.06831 | 0.030642 | -0.099343 | -0.15812 | -0.044411 | -0.10036 | -0.08347 | 0.052814 | 0.027798 | -0.042641 | 0.060923 | 0.11726 | -0.008481 | 0.065827 | 0.011602 | 0.11409 | 0.076418 | -0.053567 | -0.11235 | 0.001365 | -0.054587 | -0.037694 | 0.09859 | 0.073574 | 0.003135 | 0.1067 | -0.21094 | -0.11548 | -0.15318 | -0.057722
2705.3125 | 121.2662 | -24.0326 | 97.1512 | 0.071489 | -0.049678 | 0.020051 | -0.038752 | 0.054577 | 0.026064 | -0.090186 | -0.1627 | -0.044411 | -0.10036 | -0.078891 | 0.048236 | 0.014064 | -0.042641 | 0.056344 | 0.11726 | -0.003902 | 0.065827 | 0.007024 | 0.10035 | 0.07184 | -0.04441 | -0.11693 | 0.001365 | -0.054587 | -0.033115 | 0.094012 | 0.05984 | 0.003135 | 0.10212 | -0.21094 | -0.12006 | -0.1486 | -0.057722
2707.0938 | 121.4081 | -23.7808 | 97.3251 | 0.06691 | -0.054257 | 0.006315 | -0.043331 | 0.054577 | 0.016907 | -0.099343 | -0.15812 | -0.04899 | -0.095785 | -0.088049 | 0.052814 | 0.014064 | -0.038063 | 0.060923 | 0.11269 | -0.008481 | 0.052091 | 0.002445 | 0.10035 | 0.062683 | -0.053567 | -0.11235 | -0.003214 | -0.050009 | -0.042273 | 0.09859 | 0.05984 | 0.007713 | 0.1067 | -0.21094 | -0.12006 | -0.1486 | -0.057722
2708.8125 | 121.3257 | -23.5519 | 97.6135 | 0.071489 | -0.0451 | 0.020051 | -0.034174 | 0.059155 | 0.026064 | -0.094765 | -0.15812 | -0.04899 | -0.10036 | -0.088049 | 0.057392 | 0.02322 | -0.042641 | 0.051766 | 0.11726 | 0.000676 | 0.065827 | 0.011602 | 0.10493 | 0.07184 | -0.048989 | -0.11235 | -0.003214 | -0.054587 | -0.042273 | 0.10317 | 0.068996 | 0.003135 | 0.097542 | -0.21552 | -0.11548 | -0.15775 | -0.057722
2710.5938 | 121.3577 | -23.2864 | 97.847 | 0.06691 | -0.049678 | 0.010893 | -0.043331 | 0.054577 | 0.021485 | -0.10392 | -0.16728 | -0.044411 | -0.10036 | -0.097207 | 0.048236 | 0.02322 | -0.042641 | 0.060923 | 0.11269 | -0.003902 | 0.056669 | 0.002445 | 0.10035 | 0.067261 | -0.058145 | -0.1215 | 0.001365 | -0.054587 | -0.051431 | 0.094012 | 0.068996 | 0.003135 | 0.1067 | -0.21552 | -0.12464 | -0.1486 | -0.057722
2712.375 | 121.4035 | -23.2452 | 97.8745 | 0.071489 | -0.054257 | 0.015472 | -0.038752 | 0.054577 | 0.026064 | -0.10392 | -0.16728 | -0.044411 | -0.095785 | -0.092628 | 0.048236 | 0.02322 | -0.042641 | 0.060923 | 0.11726 | -0.008481 | 0.061248 | 0.007024 | 0.10035 | 0.07184 | -0.058145 | -0.1215 | 0.001365 | -0.050009 | -0.046852 | 0.094012 | 0.068996 | 0.003135 | 0.1067 | -0.21552 | -0.12464 | -0.14402 | -0.053144
2714.0938 | 121.312 | -22.7783 | 98.4009 | 0.071489 | -0.040521 | 0.010893 | -0.038752 | 0.054577 | 0.026064 | -0.094765 | -0.1627 | -0.04899 | -0.10494 | -0.08347 | 0.052814 | 0.02322 | -0.042641 | 0.056344 | 0.11726 | 0.005255 | 0.056669 | 0.007024 | 0.10035 | 0.07184 | -0.048989 | -0.11693 | -0.003214 | -0.059166 | -0.037694 | 0.09859 | 0.068996 | 0.003135 | 0.10212 | -0.21552 | -0.12006 | -0.15776 | -0.062301
2715.875 | 121.3074 | -24.0234 | 97.1512 | 0.080646 | -0.049678 | 0.015472 | -0.029595 | 0.054577 | 0.021485 | -0.099343 | -0.1627 | -0.044411 | -0.095785 | -0.08347 | 0.048236 | 0.02322 | -0.033484 | 0.056344 | 0.12642 | -0.003902 | 0.061248 | 0.016181 | 0.10035 | 0.067261 | -0.053567 | -0.11693 | 0.001365 | -0.050009 | -0.037694 | 0.094012 | 0.068996 | 0.012292 | 0.10212 | -0.21094 | -0.12922 | -0.14402 | -0.062301
2717.6562 | 121.3806 | -22.7325 | 98.3871 | 0.06691 | -0.054257 | 0.010893 | -0.034174 | 0.049999 | 0.021485 | -0.094765 | -0.16728 | -0.04899 | -0.10036 | -0.08347 | 0.052814 | 0.014064 | -0.038063 | 0.060923 | 0.11269 | -0.008481 | 0.056669 | 0.011602 | 0.095775 | 0.067261 | -0.048989 | -0.1215 | -0.003214 | -0.054587 | -0.037694 | 0.09859 | 0.05984 | 0.007713 | 0.1067 | -0.22009 | -0.12922 | -0.15318 | -0.0623
2719.375 | 121.2936 | -21.8719 | 99.3942 | 0.076067 | -0.054257 | 0.010893 | -0.043331 | 0.059155 | 0.026064 | -0.099343 | -0.16728 | -0.04899 | -0.10036 | -0.088049 | 0.048236 | 0.032376 | -0.038063 | 0.060923 | 0.12184 | -0.008481 | 0.056669 | 0.002445 | 0.10493 | 0.07184 | -0.053567 | -0.1215 | -0.003214 | -0.054587 | -0.042273 | 0.094012 | 0.078152 | 0.007713 | 0.1067 | -0.21552 | -0.12922 | -0.1486 | -0.0623
2721.1562 | 121.344 | -21.2402 | 99.9664 | 0.06691 | -0.054257 | 0.015472 | -0.034174 | 0.054577 | 0.021485 | -0.099343 | -0.15812 | -0.04899 | -0.095785 | -0.088049 | 0.048236 | 0.02322 | -0.04722 | 0.056344 | 0.11269 | -0.008481 | 0.061248 | 0.011602 | 0.10035 | 0.067261 | -0.053567 | -0.11235 | -0.003214 | -0.050009 | -0.042273 | 0.094012 | 0.068996 | -0.001444 | 0.10212 | -0.20636 | -0.1109 | -0.14402 | -0.048565
2722.9375 | 121.3394 | -21.0205 | 100.1862 | 0.071489 | -0.054257 | 0.020051 | -0.038752 | 0.049999 | 0.021485 | -0.099343 | -0.16728 | -0.044411 | -0.095785 | -0.088049 | 0.052814 | 0.02322 | -0.033484 | 0.060923 | 0.11726 | -0.008481 | 0.065827 | 0.007024 | 0.095775 | 0.067261 | -0.053567 | -0.1215 | 0.001365 | -0.050009 | -0.042273 | 0.09859 | 0.068996 | 0.012292 | 0.1067 | -0.22009 | -0.1338 | -0.1486 | -0.062301
2724.6562 | 121.4172 | -21.904 | 99.2477 | 0.076067 | -0.054257 | 0.015472 | -0.034174 | 0.054577 | 0.021485 | -0.094765 | -0.16728 | -0.053568 | -0.10036 | -0.088049 | 0.057392 | 0.027798 | -0.042641 | 0.060923 | 0.12184 | -0.008481 | 0.061248 | 0.011602 | 0.10035 | 0.067261 | -0.048989 | -0.1215 | -0.007792 | -0.054587 | -0.042273 | 0.10317 | 0.073574 | 0.003135 | 0.1067 | -0.22467 | -0.12464 | -0.15775 | -0.057722
2726.4375 | 121.3715 | -18.8049 | 102.42 | 0.06691 | -0.054257 | 0.010893 | -0.038752 | 0.049999 | 0.021485 | -0.099343 | -0.15812 | -0.053568 | -0.10494 | -0.088049 | 0.048236 | 0.027798 | -0.04722 | 0.070079 | 0.11269 | -0.008481 | 0.056669 | 0.007024 | 0.095775 | 0.067261 | -0.053567 | -0.11235 | -0.007792 | -0.059166 | -0.042273 | 0.094012 | 0.073574 | -0.001444 | 0.11585 | -0.20636 | -0.1109 | -0.15318 | -0.057722
2728.1562 | 121.376 | -17.4728 | 103.7109 | 0.06691 | -0.058836 | 0.006315 | -0.038752 | 0.049999 | 0.021485 | -0.10392 | -0.1627 | -0.04899 | -0.10494 | -0.088049 | 0.057392 | 0.032376 | -0.033484 | 0.060923 | 0.11269 | -0.01306 | 0.052091 | 0.007024 | 0.095775 | 0.067261 | -0.058145 | -0.11693 | -0.003214 | -0.059166 | -0.042273 | 0.10317 | 0.078152 | 0.012292 | 0.1067 | -0.22009 | -0.12922 | -0.16233 | -0.071458
2729.9375 | 121.4355 | -16.8365 | 104.3655 | 0.06691 | -0.054257 | 0.010893 | -0.047909 | 0.054577 | 0.026064 | -0.10392 | -0.1627 | -0.04899 | -0.10952 | -0.088049 | 0.057392 | 0.02322 | -0.042641 | 0.065501 | 0.11269 | -0.008481 | 0.056669 | -0.002133 | 0.10035 | 0.07184 | -0.058145 | -0.11693 | -0.003214 | -0.063744 | -0.042273 | 0.10317 | 0.068996 | 0.003135 | 0.11128 | -0.22009 | -0.12006 | -0.16691 | -0.066879
2731.6562 | 121.3531 | -16.6534 | 104.5761 | 0.076067 | -0.054257 | 0.006315 | -0.043331 | 0.054577 | 0.016907 | -0.099343 | -0.16728 | -0.04899 | -0.10952 | -0.092628 | 0.052814 | 0.02322 | -0.033484 | 0.060923 | 0.12184 | -0.008481 | 0.052091 | 0.002445 | 0.10035 | 0.062683 | -0.053567 | -0.1215 | -0.003214 | -0.063744 | -0.046852 | 0.09859 | 0.068996 | 0.012292 | 0.1067 | -0.22009 | -0.1338 | -0.16233 | -0.076036
2733.4219 | 121.3211 | -14.7446 | 106.5353 | 0.076067 | -0.058836 | 0.006315 | -0.052488 | 0.049999 | 0.026064 | -0.1085 | -0.16728 | -0.04899 | -0.10952 | -0.092628 | 0.057392 | 0.02322 | -0.033484 | 0.070079 | 0.12184 | -0.01306 | 0.052091 | -0.006712 | 0.095775 | 0.07184 | -0.062723 | -0.1215 | -0.003214 | -0.063744 | -0.046852 | 0.10317 | 0.068996 | 0.012292 | 0.11585 | -0.22467 | -0.1338 | -0.16691 | -0.076036
2735.125 | 121.344 | -10.8627 | 110.4309 | 0.062332 | -0.063415 | 0.006315 | -0.052488 | 0.049999 | 0.016907 | -0.10392 | -0.18102 | -0.058147 | -0.10952 | -0.092628 | 0.06197 | 0.027798 | -0.038063 | 0.065501 | 0.10811 | -0.017639 | 0.052091 | -0.006712 | 0.095775 | 0.062683 | -0.058145 | -0.13524 | -0.012371 | -0.063744 | -0.046852 | 0.10775 | 0.073574 | 0.007713 | 0.11128 | -0.24299 | -0.14295 | -0.17149 | -0.071457
2736.9062 | 121.3257 | -12.5931 | 108.7372 | 0.057754 | -0.058836 | 0.006315 | -0.047909 | 0.054577 | 0.016907 | -0.10392 | -0.16728 | -0.053568 | -0.10036 | -0.092628 | 0.06197 | 0.027798 | -0.038063 | 0.065501 | 0.10353 | -0.01306 | 0.052091 | -0.002133 | 0.10035 | 0.062683 | -0.058145 | -0.1215 | -0.007792 | -0.054587 | -0.046852 | 0.10775 | 0.073574 | 0.007713 | 0.11128 | -0.22925 | -0.12922 | -0.16233 | -0.0623
2738.6719 | 121.4218 | -11.3388 | 107.6431 | 0.062332 | -0.058836 | 0.001736 | -0.043331 | 0.054577 | 0.012329 | -0.1085 | -0.17644 | -0.053568 | -0.1141 | -0.092628 | 0.06197 | 0.032376 | -0.033484 | 0.060923 | 0.10811 | -0.01306 | 0.047512 | 0.002445 | 0.10035 | 0.058105 | -0.062723 | -0.13066 | -0.007792 | -0.068322 | -0.046852 | 0.10775 | 0.078152 | 0.012292 | 0.1067 | -0.23841 | -0.14295 | -0.17607 | -0.080614
2740.375 | 121.3623 | -10.1028 | 111.1588 | 0.06691 | -0.063415 | 0.006315 | -0.047909 | 0.049999 | 0.012329 | -0.10392 | -0.17186 | -0.053568 | -0.10494 | -0.092628 | 0.057392 | 0.032376 | -0.033484 | 0.065501 | 0.11269 | -0.017639 | 0.052091 | -0.002133 | 0.095775 | 0.058105 | -0.058145 | -0.12608 | -0.007792 | -0.059166 | -0.046852 | 0.10317 | 0.078152 | 0.012292 | 0.11128 | -0.22925 | -0.13837 | -0.16233 | -0.071458
2742.1562 | 121.344 | -9.6634 | 111.6623 | 0.071489 | -0.067994 | 0.006315 | -0.047909 | 0.054577 | 0.012329 | -0.1085 | -0.17644 | -0.058147 | -0.1141 | -0.092628 | 0.071126 | 0.032376 | -0.042641 | 0.065501 | 0.11726 | -0.022218 | 0.052091 | -0.002133 | 0.10035 | 0.058105 | -0.062723 | -0.13066 | -0.012371 | -0.068322 | -0.046852 | 0.1169 | 0.078152 | 0.003135 | 0.11128 | -0.24756 | -0.1338 | -0.18522 | -0.071457
2743.875 | 121.3898 | -9.4116 | 111.8958 | 0.06691 | -0.063415 | 0.015472 | -0.043331 | 0.045421 | 0.016907 | -0.11308 | -0.17644 | -0.058147 | -0.10952 | -0.092628 | 0.06197 | 0.032376 | -0.038063 | 0.070079 | 0.11269 | -0.017639 | 0.061248 | 0.002445 | 0.091197 | 0.062683 | -0.067301 | -0.13066 | -0.012371 | -0.063744 | -0.046852 | 0.10775 | 0.078152 | 0.007713 | 0.11585 | -0.23841 | -0.13837 | -0.17149 | -0.071457
2745.6562 | 121.431 | -13.3301 | 107.8766 | 0.062332 | -0.067994 | -0.002842 | -0.043331 | 0.054577 | 0.012329 | -0.10392 | -0.16728 | -0.04899 | -0.10494 | -0.092628 | 0.057392 | 0.032376 | -0.038063 | 0.070079 | 0.10811 | -0.022218 | 0.042934 | 0.002445 | 0.10035 | 0.058105 | -0.058145 | -0.1215 | -0.003214 | -0.059166 | -0.046852 | 0.10317 | 0.078152 | 0.007713 | 0.11585 | -0.22467 | -0.12922 | -0.16233 | -0.066879
2747.4375 | 121.4081 | -11.9888 | 109.2133 | 0.057754 | -0.063415 | 0.001736 | -0.043331 | 0.049999 | 0.012329 | -0.1085 | -0.16728 | -0.058147 | -0.10952 | -0.097207 | 0.057392 | 0.032376 | -0.038063 | 0.060923 | 0.10353 | -0.017639 | 0.047512 | 0.002445 | 0.095775 | 0.058105 | -0.062723 | -0.1215 | -0.012371 | -0.063744 | -0.051431 | 0.10317 | 0.078152 | 0.007713 | 0.1067 | -0.22467 | -0.12922 | -0.16691 | -0.071457
2749.1562 | 121.3257 | -10.9726 | 110.3806 | 0.057754 | -0.072572 | 0.001736 | -0.038752 | 0.049999 | 0.021485 | -0.10392 | -0.16728 | -0.053568 | -0.10952 | -0.088049 | 0.06197 | 0.027798 | -0.038063 | 0.074657 | 0.10353 | -0.026796 | 0.047512 | 0.007024 | 0.095775 | 0.067261 | -0.058145 | -0.1215 | -0.007792 | -0.063744 | -0.042273 | 0.10775 | 0.073574 | 0.007713 | 0.12043 | -0.22925 | -0.12922 | -0.17149 | -0.071457
2750.9219 | 121.3531 | -11.6318 | 109.6802 | 0.06691 | -0.058836 | 0.001736 | -0.047909 | 0.045421 | 0.012329 | -0.099343 | -0.16728 | -0.04899 | -0.10952 | -0.10179 | 0.06197 | 0.032376 | -0.033484 | 0.065501 | 0.11269 | -0.01306 | 0.047512 | -0.002133 | 0.091197 | 0.058105 | -0.053567 | -0.1215 | -0.003214 | -0.063744 | -0.05601 | 0.10775 | 0.078152 | 0.012292 | 0.11128 | -0.22925 | -0.1338 | -0.17149 | -0.076036
2752.6406 | 121.4767 | -9.1782 | 112.0377 | 0.057754 | -0.063415 | 0.006315 | -0.038752 | 0.049999 | 0.016907 | -0.10392 | -0.17186 | -0.04899 | -0.10952 | -0.08347 | 0.057392 | 0.032376 | -0.038063 | 0.070079 | 0.10353 | -0.017639 | 0.052091 | 0.007024 | 0.095775 | 0.062683 | -0.058145 | -0.12608 | -0.003214 | -0.063744 | -0.037694 | 0.10317 | 0.078152 | 0.007713 | 0.11585 | -0.22925 | -0.13379 | -0.16691 | -0.071457
2754.4219 | 121.4264 | -11.3937 | 109.8358 | 0.06691 | -0.067994 | 0.006315 | -0.047909 | 0.054577 | 0.016907 | -0.099343 | -0.1627 | -0.04899 | -0.1141 | -0.088049 | 0.06197 | 0.027798 | -0.033484 | 0.070079 | 0.11269 | -0.022218 | 0.052091 | -0.002133 | 0.10035 | 0.062683 | -0.053567 | -0.11693 | -0.003214 | -0.068322 | -0.042273 | 0.10775 | 0.073574 | 0.012292 | 0.11585 | -0.22467 | -0.12922 | -0.17607 | -0.080614
2756.1406 | 121.4676 | -12.735 | 108.4534 | 0.062332 | -0.063415 | 0.010893 | -0.043331 | 0.045421 | 0.016907 | -0.1085 | -0.17186 | -0.058147 | -0.10494 | -0.092628 | 0.057392 | 0.027798 | -0.038063 | 0.079235 | 0.10811 | -0.017639 | 0.056669 | 0.002445 | 0.091197 | 0.062683 | -0.062723 | -0.12608 | -0.012371 | -0.059166 | -0.046852 | 0.10317 | 0.073574 | 0.007713 | 0.12501 | -0.22925 | -0.13379 | -0.16233 | -0.066879
2757.9375 | 121.3623 | -12.5885 | 108.6777 | 0.06691 | -0.063415 | 0.001736 | -0.052488 | 0.049999 | 0.016907 | -0.10392 | -0.16728 | -0.053568 | -0.10494 | -0.088049 | 0.057392 | 0.027798 | -0.028906 | 0.065501 | 0.11269 | -0.017639 | 0.047512 | -0.006712 | 0.095775 | 0.062683 | -0.058145 | -0.1215 | -0.007792 | -0.059166 | -0.042273 | 0.10317 | 0.073574 | 0.01687 | 0.11128 | -0.22467 | -0.13837 | -0.16233 | -0.076036
2759.6562 | 121.4447 | -12.5015 | 108.6731 | 0.06691 | -0.058836 | 0.015472 | -0.047909 | 0.049999 | 0.016907 | -0.10392 | -0.16728 | -0.053568 | -0.10952 | -0.092628 | 0.057392 | 0.032376 | -0.033484 | 0.074657 | 0.11269 | -0.01306 | 0.061248 | -0.002133 | 0.095775 | 0.062683 | -0.058145 | -0.1215 | -0.007792 | -0.063744 | -0.046852 | 0.10317 | 0.078152 | 0.012292 | 0.12043 | -0.22467 | -0.1338 | -0.16691 | -0.076036
2761.4219 | 121.4767 | -8.9676 | 111.7813 | 0.057754 | -0.063415 | 0.001736 | -0.043331 | 0.045421 | 0.021485 | -0.1085 | -0.16728 | -0.058147 | -0.1141 | -0.097207 | 0.066548 | 0.032376 | -0.038063 | 0.079235 | 0.10353 | -0.017639 | 0.047512 | 0.002445 | 0.091197 | 0.067261 | -0.062723 | -0.1215 | -0.012371 | -0.068322 | -0.051431 | 0.11232 | 0.078152 | 0.007713 | 0.12501 | -0.23383 | -0.12922 | -0.18065 | -0.076035
2763.1875 | 121.3303 | -6.3171 | 115.1459 | 0.057754 | -0.058836 | 0.001736 | -0.052488 | 0.045421 | 0.016907 | -0.10392 | -0.17644 | -0.062726 | -0.10952 | -0.097207 | 0.057392 | 0.027798 | -0.038063 | 0.065501 | 0.10353 | -0.01306 | 0.047512 | -0.006712 | 0.091197 | 0.062683 | -0.058145 | -0.13066 | -0.01695 | -0.063744 | -0.051431 | 0.10317 | 0.073574 | 0.007713 | 0.11128 | -0.23383 | -0.13837 | -0.16691 | -0.071457
2764.8906 | 121.5225 | -4.8614 | 113.3881 | 0.057754 | -0.067994 | -0.007421 | -0.047909 | 0.045421 | 0.016907 | -0.10392 | -0.17186 | -0.062726 | -0.11868 | -0.092628 | 0.06197 | 0.032376 | -0.038063 | 0.070079 | 0.10353 | -0.022218 | 0.038355 | -0.002133 | 0.091197 | 0.062683 | -0.058145 | -0.12608 | -0.01695 | -0.0729 | -0.046852 | 0.10775 | 0.078152 | 0.007713 | 0.11585 | -0.23383 | -0.13379 | -0.18065 | -0.080613
2766.6719 | 121.3806 | -18.1274 | 103.1525 | 0.062332 | -0.063415 | 0.010893 | -0.043331 | 0.059155 | 0.016907 | -0.099343 | -0.1627 | -0.044411 | -0.10952 | -0.092628 | 0.066548 | 0.02322 | -0.042641 | 0.070079 | 0.10811 | -0.017639 | 0.056669 | 0.002445 | 0.10493 | 0.062683 | -0.053567 | -0.11693 | 0.001365 | -0.063744 | -0.046852 | 0.11232 | 0.068996 | 0.003135 | 0.11585 | -0.22925 | -0.12006 | -0.17607 | -0.066879
2768.4375 | 121.3028 | -15.5228 | 105.8624 | 0.06691 | -0.054257 | 0.015472 | -0.038752 | 0.049999 | 0.016907 | -0.099343 | -0.1627 | -0.053568 | -0.10494 | -0.088049 | 0.06197 | 0.032376 | -0.042641 | 0.065501 | 0.11269 | -0.008481 | 0.061248 | 0.007024 | 0.095775 | 0.062683 | -0.053567 | -0.11693 | -0.007792 | -0.059166 | -0.042273 | 0.10775 | 0.078152 | 0.003135 | 0.11128 | -0.22467 | -0.12006 | -0.16691 | -0.062301
2770.1562 | 121.3898 | -9.6039 | 111.5662 | 0.076067 | -0.054257 | 0.006315 | -0.052488 | 0.040843 | 0.021485 | -0.094765 | -0.15812 | -0.04899 | -0.10036 | -0.092628 | 0.057392 | 0.027798 | -0.038063 | 0.060923 | 0.12184 | -0.008481 | 0.052091 | -0.006712 | 0.086619 | 0.067261 | -0.048989 | -0.11235 | -0.003214 | -0.054587 | -0.046852 | 0.10317 | 0.073574 | 0.007713 | 0.1067 | -0.21552 | -0.12006 | -0.15775 | -0.0623
2771.9375 | 121.4081 | -20.5765 | 100.5615 | 0.076067 | -0.054257 | 0.015472 | -0.034174 | 0.059155 | 0.021485 | -0.099343 | -0.1627 | -0.044411 | -0.10036 | -0.092628 | 0.052814 | 0.018642 | -0.038063 | 0.056344 | 0.12184 | -0.008481 | 0.061248 | 0.011602 | 0.10493 | 0.067261 | -0.053567 | -0.11693 | 0.001365 | -0.054587 | -0.046852 | 0.09859 | 0.064418 | 0.007713 | 0.10212 | -0.21552 | -0.12464 | -0.15318 | -0.0623
2773.6562 | 121.3394 | -25.4288 | 95.7504 | 0.076067 | -0.058836 | 0.020051 | -0.034174 | 0.059155 | 0.026064 | -0.090186 | -0.1627 | -0.039832 | -0.10036 | -0.088049 | 0.052814 | 0.02322 | -0.042641 | 0.060923 | 0.12184 | -0.01306 | 0.065827 | 0.011602 | 0.10493 | 0.07184 | -0.04441 | -0.11693 | 0.005944 | -0.054587 | -0.042273 | 0.09859 | 0.068996 | 0.003135 | 0.1067 | -0.21552 | -0.12006 | -0.15318 | -0.057722
2775.4062 | 121.3898 | -29.6631 | 91.2323 | 0.085224 | -0.0451 | 0.020051 | -0.034174 | 0.059155 | 0.021485 | -0.094765 | -0.15354 | -0.04899 | -0.091207 | -0.078891 | 0.052814 | 0.02322 | -0.042641 | 0.051766 | 0.131 | 0.000676 | 0.065827 | 0.011602 | 0.10493 | 0.067261 | -0.048989 | -0.10777 | -0.003214 | -0.045431 | -0.033115 | 0.09859 | 0.068996 | 0.003135 | 0.097542 | -0.20636 | -0.1109 | -0.14402 | -0.048566
2777.1406 | 121.3303 | -36.026 | 84.9792 | 0.076067 | -0.054257 | 0.024629 | -0.025017 | 0.06831 | 0.030642 | -0.090186 | -0.15354 | -0.039832 | -0.091207 | -0.074312 | 0.039079 | 0.014064 | -0.038063 | 0.051766 | 0.12184 | -0.008481 | 0.070405 | 0.020759 | 0.11409 | 0.076418 | -0.04441 | -0.10777 | 0.005944 | -0.045431 | -0.028536 | 0.084855 | 0.05984 | 0.007713 | 0.097542 | -0.19262 | -0.11548 | -0.13029 | -0.053144
2778.9062 | 121.3531 | -34.8907 | 86.1099 | 0.076067 | -0.049678 | 0.020051 | -0.038752 | 0.063733 | 0.021485 | -0.094765 | -0.14897 | -0.044411 | -0.091207 | -0.074312 | 0.048236 | 0.018642 | -0.038063 | 0.060923 | 0.12184 | -0.003902 | 0.065827 | 0.007024 | 0.10951 | 0.067261 | -0.048989 | -0.10319 | 0.001365 | -0.045431 | -0.028536 | 0.094012 | 0.064418 | 0.007713 | 0.1067 | -0.1972 | -0.1109 | -0.13944 | -0.053144
2780.6719 | 121.2341 | -32.515 | 88.5635 | 0.076067 | -0.049678 | 0.020051 | -0.025017 | 0.063733 | 0.021485 | -0.090186 | -0.15354 | -0.039832 | -0.091207 | -0.078891 | 0.048236 | 0.014064 | -0.038063 | 0.056344 | 0.12184 | -0.003902 | 0.065827 | 0.020759 | 0.10951 | 0.067261 | -0.04441 | -0.10777 | 0.005944 | -0.045431 | -0.033115 | 0.094012 | 0.05984 | 0.007713 | 0.10212 | -0.20178 | -0.11548 | -0.13944 | -0.053144
2782.4375 | 121.1334 | -29.7913 | 91.3239 | 0.076067 | -0.0451 | 0.029208 | -0.029595 | 0.063733 | 0.030642 | -0.094765 | -0.14897 | -0.035253 | -0.08205 | -0.074312 | 0.043657 | 0.009486 | -0.038063 | 0.051766 | 0.12184 | 0.000676 | 0.074984 | 0.016181 | 0.10951 | 0.076418 | -0.048989 | -0.10319 | 0.010523 | -0.036274 | -0.028536 | 0.089433 | 0.055262 | 0.007713 | 0.097542 | -0.19262 | -0.1109 | -0.12571 | -0.043987
2784.1562 | 121.2524 | -45.1538 | 75.769 | 0.094381 | -0.035942 | 0.038365 | -0.025017 | 0.082044 | 0.039799 | -0.08103 | -0.14439 | -0.030674 | -0.08205 | -0.065154 | 0.039079 | 0.004908 | -0.051798 | 0.038032 | 0.14016 | 0.009834 | 0.084141 | 0.020759 | 0.12782 | 0.085575 | -0.035254 | -0.098611 | 0.015102 | -0.036274 | -0.019378 | 0.084855 | 0.050684 | -0.006022 | 0.083808 | -0.18347 | -0.092589 | -0.12113 | -0.030252
2785.9375 | 121.1334 | -45.3873 | 75.531 | 0.085224 | -0.040521 | 0.024629 | -0.025017 | 0.06831 | 0.035221 | -0.08103 | -0.14439 | -0.035253 | -0.086628 | -0.065154 | 0.029923 | 0.009486 | -0.042641 | 0.04261 | 0.131 | 0.005255 | 0.070405 | 0.020759 | 0.11409 | 0.080997 | -0.035254 | -0.098611 | 0.010523 | -0.040852 | -0.019378 | 0.075699 | 0.055262 | 0.003135 | 0.088386 | -0.17431 | -0.10175 | -0.11655 | -0.043987
2787.7188 | 120.8908 | -20.4941 | 102.0905 | 0.080646 | -0.054257 | 0.015472 | -0.038752 | 0.059155 | 0.030642 | -0.090186 | -0.15354 | -0.039832 | -0.095785 | -0.078891 | 0.052814 | 0.02322 | -0.038063 | 0.060923 | 0.12642 | -0.008481 | 0.061248 | 0.007024 | 0.10493 | 0.076418 | -0.04441 | -0.10777 | 0.005944 | -0.050009 | -0.033115 | 0.09859 | 0.068996 | 0.007713 | 0.1067 | -0.20636 | -0.11548 | -0.1486 | -0.057722
2789.4844 | 121.2067 | -13.5086 | 108.2565 | 0.06691 | -0.054257 | 0.015472 | -0.038752 | 0.054577 | 0.026064 | -0.094765 | -0.16728 | -0.039832 | -0.10494 | -0.092628 | 0.057392 | 0.02322 | -0.028906 | 0.060923 | 0.11269 | -0.008481 | 0.061248 | 0.007024 | 0.10035 | 0.07184 | -0.048989 | -0.1215 | 0.005944 | -0.059166 | -0.046852 | 0.10317 | 0.068996 | 0.01687 | 0.1067 | -0.22467 | -0.13837 | -0.16233 | -0.076036
2791.2031 | 121.1655 | -37.2757 | 83.7616 | 0.080646 | -0.040521 | 0.020051 | -0.034174 | 0.06831 | 0.030642 | -0.090186 | -0.14439 | -0.035253 | -0.086628 | -0.069733 | 0.039079 | 0.014064 | -0.04722 | 0.051766 | 0.12642 | 0.005255 | 0.065827 | 0.011602 | 0.11409 | 0.076418 | -0.04441 | -0.098611 | 0.010523 | -0.040852 | -0.023957 | 0.084855 | 0.05984 | -0.001444 | 0.097542 | -0.18347 | -0.097167 | -0.12571 | -0.039408
2792.9844 | 121.1746 | -44.87 | 75.9384 | 0.089802 | -0.040521 | 0.029208 | -0.020438 | 0.06831 | 0.035221 | -0.08103 | -0.14439 | -0.035253 | -0.08205 | -0.065154 | 0.039079 | 0.004908 | -0.04722 | 0.04261 | 0.13558 | 0.005255 | 0.074984 | 0.025338 | 0.11409 | 0.080997 | -0.035254 | -0.098611 | 0.010523 | -0.036274 | -0.019378 | 0.084855 | 0.050684 | -0.001444 | 0.088386 | -0.18347 | -0.097167 | -0.12113 | -0.03483
2794.75 | 121.138 | -48.4955 | 72.2809 | 0.089802 | -0.040521 | 0.033786 | -0.011281 | 0.077466 | 0.044377 | -0.076452 | -0.13981 | -0.026096 | -0.077472 | -0.060575 | 0.029923 | 0.009486 | -0.04722 | 0.038032 | 0.13558 | 0.005255 | 0.079562 | 0.034495 | 0.12324 | 0.090153 | -0.030676 | -0.094033 | 0.01968 | -0.031696 | -0.014799 | 0.075699 | 0.055262 | -0.001444 | 0.083808 | -0.16973 | -0.092589 | -0.1074 | -0.030252
2796.5156 | 121.2112 | -110.1791 | 10.8124 | 0.13101 | 0.005267 | 0.084151 | 0.020768 | 0.12325 | 0.090161 | -0.039826 | -0.089445 | 0.019693 | -0.027111 | -0.023943 | -0.015859 | -0.040873 | -0.07469 | -0.012328 | 0.17678 | 0.051043 | 0.12993 | 0.066544 | 0.16902 | 0.13594 | 0.00595 | -0.043669 | 0.065469 | 0.018665 | 0.021833 | 0.029917 | 0.004903 | -0.028914 | 0.033448 | -0.073586 | -0.014755 | -0.011252 | 0.047579
2798.25 | 121.1655 | -91.7084 | 29.3243 | 0.13101 | 0.000689 | 0.074994 | 0.01619 | 0.10493 | 0.071848 | -0.053561 | -0.10776 | 0.015114 | -0.045424 | -0.033101 | 0.002454 | -0.027139 | -0.051798 | 0.010563 | 0.17678 | 0.046465 | 0.12077 | 0.061966 | 0.15071 | 0.11762 | -0.007785 | -0.061983 | 0.06089 | 0.000352 | 0.012675 | 0.04823 | 0.018637 | -0.006022 | 0.056339 | -0.11021 | -0.055961 | -0.047878 | 0.006374
2800.0312 | 121.1517 | -89.7217 | 31.3293 | 0.13101 | -0.00389 | 0.065837 | 0.01619 | 0.11867 | 0.071848 | -0.053561 | -0.10776 | 0.005956 | -0.05458 | -0.03768 | 0.002454 | -0.031717 | -0.051798 | 0.010563 | 0.17678 | 0.041886 | 0.11161 | 0.061966 | 0.16444 | 0.11762 | -0.007785 | -0.061983 | 0.051732 | -0.008804 | 0.008096 | 0.04823 | 0.014059 | -0.006022 | 0.056339 | -0.11021 | -0.055961 | -0.057034 | -0.002782
2801.75 | 121.106 | -85.9085 | 35.1013 | 0.11727 | -0.00389 | 0.056679 | 0.002454 | 0.10951 | 0.062691 | -0.053561 | -0.11692 | 0.001377 | -0.059159 | -0.042259 | 0.002454 | -0.022561 | -0.056376 | 0.015141 | 0.16305 | 0.041886 | 0.10245 | 0.04823 | 0.15529 | 0.10847 | -0.007785 | -0.07114 | 0.047153 | -0.013383 | 0.003517 | 0.04823 | 0.023215 | -0.0106 | 0.060917 | -0.11937 | -0.06054 | -0.061613 | -0.002783
2803.5156 | 121.138 | -98.6938 | 22.2336 | 0.13559 | 0.000689 | 0.074994 | 0.020768 | 0.11867 | 0.085583 | -0.048983 | -0.094024 | 0.005956 | -0.040846 | -0.033101 | -0.006702 | -0.036295 | -0.060955 | 0.001406 | 0.18136 | 0.046465 | 0.12077 | 0.066544 | 0.16444 | 0.13136 | -0.003207 | -0.048248 | 0.051732 | 0.00493 | 0.012675 | 0.039074 | 0.009481 | -0.015179 | 0.047182 | -0.087322 | -0.033069 | -0.034144 | 0.020109
2805.2344 | 121.1609 | -98.1216 | 22.8287 | 0.13101 | 0.005267 | 0.074994 | 0.020768 | 0.11867 | 0.081005 | -0.058139 | -0.10776 | 0.010535 | -0.045424 | -0.023943 | -0.002124 | -0.031717 | -0.060955 | 0.010563 | 0.17678 | 0.051043 | 0.12077 | 0.066544 | 0.16444 | 0.12678 | -0.012363 | -0.061983 | 0.056311 | 0.000352 | 0.021833 | 0.043652 | 0.014059 | -0.015179 | 0.056339 | -0.10563 | -0.046804 | -0.0433 | 0.015531
2807.0156 | 121.2433 | -96.0114 | 24.9252 | 0.11727 | 0.000689 | 0.070415 | 0.002454 | 0.10951 | 0.076426 | -0.048983 | -0.10776 | 0.005956 | -0.045424 | -0.028522 | -0.002124 | -0.031717 | -0.060955 | 0.005985 | 0.16305 | 0.046465 | 0.11619 | 0.04823 | 0.15529 | 0.1222 | -0.003207 | -0.061983 | 0.051732 | 0.000352 | 0.017254 | 0.043652 | 0.014059 | -0.015179 | 0.051761 | -0.10563 | -0.046804 | -0.0433 | 0.015531
2808.7969 | 121.2524 | -99.9252 | 20.9427 | 0.13101 | 0.000689 | 0.070415 | 0.01619 | 0.10951 | 0.081005 | -0.048983 | -0.10318 | 0.010535 | -0.036267 | -0.023943 | 0.002454 | -0.040873 | -0.065533 | 0.001406 | 0.17678 | 0.046465 | 0.11619 | 0.061966 | 0.15529 | 0.12678 | -0.003207 | -0.057405 | 0.056311 | 0.009509 | 0.021833 | 0.04823 | 0.004903 | -0.019757 | 0.047182 | -0.10563 | -0.037648 | -0.038721 | 0.029266
2810.5625 | 121.1609 | -98.4558 | 22.5174 | 0.13101 | -0.00389 | 0.074994 | 0.011611 | 0.11867 | 0.081005 | -0.048983 | -0.098602 | 0.010535 | -0.045424 | -0.033101 | -0.020437 | -0.050029 | -0.088425 | -0.021484 | 0.17678 | 0.041886 | 0.12077 | 0.057387 | 0.16444 | 0.12678 | -0.003207 | -0.052826 | 0.056311 | 0.000352 | 0.012675 | 0.025339 | -0.004253 | -0.042649 | 0.024292 | -0.078165 | -0.010177 | -0.024987 | 0.043001
2812.3438 | 121.2387 | -100.296 | 20.5627 | 0.13101 | -0.00389 | 0.070415 | 0.01619 | 0.11867 | 0.081005 | -0.048983 | -0.098602 | 0.010535 | -0.036267 | -0.023943 | -0.011281 | -0.036295 | -0.060955 | 0.005985 | 0.17678 | 0.041886 | 0.11619 | 0.061966 | 0.16444 | 0.12678 | -0.003207 | -0.052826 | 0.056311 | 0.009509 | 0.021833 | 0.034495 | 0.009481 | -0.015179 | 0.051761 | -0.087321 | -0.037647 | -0.024986 | 0.024688
2814.0625 | 121.1288 | -100.8545 | 20.0729 | 0.13559 | 0.000689 | 0.070415 | 0.01619 | 0.11409 | 0.081005 | -0.044405 | -0.098602 | 0.015114 | -0.036267 | -0.023943 | -0.002124 | -0.036295 | -0.065533 | -0.003172 | 0.18136 | 0.046465 | 0.11619 | 0.061966 | 0.15987 | 0.12678 | 0.001371 | -0.052826 | 0.06089 | 0.009509 | 0.021833 | 0.043652 | 0.009481 | -0.019757 | 0.042604 | -0.096478 | -0.033069 | -0.034143 | 0.029266
2815.8438 | 121.1563 | -86.6501 | 34.2773 | 0.11269 | -0.00389 | 0.052101 | 0.011611 | 0.10036 | 0.071848 | -0.048983 | -0.10776 | -0.00778 | -0.05458 | -0.03768 | 0.002454 | -0.027139 | -0.060955 | 0.010563 | 0.15847 | 0.041886 | 0.097877 | 0.057387 | 0.14613 | 0.11762 | -0.003207 | -0.061983 | 0.037996 | -0.008804 | 0.008096 | 0.04823 | 0.018637 | -0.015179 | 0.056339 | -0.11021 | -0.046804 | -0.057034 | 0.006375
2817.625 | 121.1334 | -93.3426 | 27.5757 | 0.12643 | -0.00389 | 0.070415 | 0.01619 | 0.10951 | 0.076426 | -0.048983 | -0.10776 | 0.010535 | -0.050002 | -0.033101 | -0.006702 | -0.031717 | -0.060955 | 0.015141 | 0.1722 | 0.041886 | 0.11619 | 0.061966 | 0.15529 | 0.1222 | -0.003207 | -0.061983 | 0.056311 | -0.004226 | 0.012675 | 0.039074 | 0.014059 | -0.015179 | 0.060917 | -0.10106 | -0.046804 | -0.0433 | 0.010953
2819.3281 | 121.1014 | -90.4266 | 30.5374 | 0.12185 | -0.00389 | 0.065837 | 0.007033 | 0.10951 | 0.076426 | -0.048983 | -0.10318 | 0.010535 | -0.045424 | -0.03768 | -0.002124 | -0.031717 | -0.056376 | 0.005985 | 0.16763 | 0.041886 | 0.11161 | 0.052809 | 0.15529 | 0.1222 | -0.003207 | -0.057405 | 0.056311 | 0.000352 | 0.008096 | 0.043652 | 0.014059 | -0.0106 | 0.051761 | -0.10106 | -0.046805 | -0.0433 | 0.010952
2821.1094 | 121.2112 | -88.8748 | 32.0114 | 0.11727 | -0.00389 | 0.056679 | 0.011611 | 0.10493 | 0.071848 | -0.053561 | -0.11234 | 0.005956 | -0.045424 | -0.03768 | 0.002454 | -0.022561 | -0.056376 | 0.015141 | 0.16305 | 0.041886 | 0.10245 | 0.057387 | 0.15071 | 0.11762 | -0.007785 | -0.066562 | 0.051732 | 0.000352 | 0.008096 | 0.04823 | 0.023215 | -0.0106 | 0.060917 | -0.11479 | -0.055962 | -0.047878 | 0.010952
2822.9062 | 121.2387 | -101.1566 | 19.6747 | 0.13101 | -0.00389 | 0.070415 | 0.020768 | 0.11867 | 0.076426 | -0.039826 | -0.098602 | 0.015114 | -0.040846 | -0.023943 | -0.006702 | -0.040873 | -0.060955 | 0.001406 | 0.17678 | 0.041886 | 0.11619 | 0.066544 | 0.16444 | 0.1222 | 0.00595 | -0.052826 | 0.06089 | 0.00493 | 0.021833 | 0.039074 | 0.004903 | -0.015179 | 0.047182 | -0.0919 | -0.037647 | -0.034144 | 0.020109
2824.6719 | 121.106 | -103.2028 | 17.6697 | 0.13559 | 0.000689 | 0.074994 | 0.01619 | 0.11409 | 0.085583 | -0.044405 | -0.094024 | 0.019693 | -0.031689 | -0.014785 | -0.002124 | -0.045451 | -0.060955 | -0.012328 | 0.18136 | 0.046465 | 0.12077 | 0.061966 | 0.15987 | 0.13136 | 0.001371 | -0.048248 | 0.065469 | 0.014087 | 0.030991 | 0.043652 | 0.000325 | -0.015179 | 0.033448 | -0.0919 | -0.033069 | -0.029565 | 0.029266
2826.3906 | 121.138 | -98.1995 | 22.6959 | 0.12185 | -0.00389 | 0.074994 | 0.01619 | 0.10951 | 0.081005 | -0.044405 | -0.10318 | 0.001377 | -0.036267 | -0.028522 | -0.011281 | -0.027139 | -0.060955 | 0.005985 | 0.16763 | 0.041886 | 0.12077 | 0.061966 | 0.15529 | 0.12678 | 0.001371 | -0.057405 | 0.047153 | 0.009509 | 0.017254 | 0.034495 | 0.018637 | -0.015179 | 0.051761 | -0.0919 | -0.042226 | -0.024986 | 0.024688
2828.1719 | 121.1609 | -102.7405 | 18.1 | 0.13559 | 0.000689 | 0.079572 | 0.01619 | 0.11409 | 0.081005 | -0.039826 | -0.094024 | 0.015114 | -0.040846 | -0.023943 | -0.015859 | -0.040873 | -0.060955 | 0.001406 | 0.18136 | 0.046465 | 0.12535 | 0.061966 | 0.15987 | 0.12678 | 0.00595 | -0.048248 | 0.06089 | 0.00493 | 0.021833 | 0.029917 | 0.004903 | -0.015179 | 0.047182 | -0.078165 | -0.033069 | -0.024987 | 0.020109
2829.9531 | 121.225 | -101.1154 | 19.6701 | 0.12643 | 0.000689 | 0.079572 | 0.020768 | 0.11867 | 0.081005 | -0.039826 | -0.094024 | 0.015114 | -0.036267 | -0.023943 | -0.011281 | -0.040873 | -0.060955 | -0.003172 | 0.1722 | 0.046465 | 0.12535 | 0.066544 | 0.16444 | 0.12678 | 0.00595 | -0.048248 | 0.06089 | 0.009509 | 0.021833 | 0.034495 | 0.004903 | -0.015179 | 0.042604 | -0.082743 | -0.033069 | -0.024986 | 0.024688
2831.6719 | 121.1517 | -100.3601 | 20.3979 | 0.12643 | 0.000689 | 0.065837 | 0.011611 | 0.11409 | 0.076426 | -0.044405 | -0.098602 | 0.010535 | -0.036267 | -0.028522 | -0.006702 | -0.036295 | -0.056376 | 0.001406 | 0.1722 | 0.046465 | 0.11161 | 0.057387 | 0.15987 | 0.1222 | 0.001371 | -0.052826 | 0.056311 | 0.009509 | 0.017254 | 0.039074 | 0.009481 | -0.0106 | 0.047182 | -0.0919 | -0.042226 | -0.029565 | 0.020109
2833.4375 | 121.1609 | -100.3098 | 20.4758 | 0.13101 | -0.00389 | 0.070415 | 0.025347 | 0.10493 | 0.085583 | -0.044405 | -0.094024 | 0.010535 | -0.045424 | -0.023943 | -0.006702 | -0.036295 | -0.060955 | 0.001406 | 0.17678 | 0.041886 | 0.11619 | 0.071123 | 0.15071 | 0.13136 | 0.001371 | -0.048248 | 0.056311 | 0.000352 | 0.021833 | 0.039074 | 0.009481 | -0.015179 | 0.047182 | -0.087322 | -0.033069 | -0.038722 | 0.015531
2835.1562 | 121.1472 | -98.5062 | 22.2977 | 0.12185 | -0.00389 | 0.070415 | 0.011611 | 0.12325 | 0.081005 | -0.044405 | -0.10318 | 0.010535 | -0.045424 | -0.028522 | 0.002454 | -0.036295 | -0.060955 | 0.015141 | 0.16763 | 0.041886 | 0.11619 | 0.057387 | 0.16902 | 0.12678 | 0.001371 | -0.057405 | 0.056311 | 0.000352 | 0.017254 | 0.04823 | 0.009481 | -0.015179 | 0.060917 | -0.10563 | -0.042226 | -0.047878 | 0.015531
2836.9219 | 120.9595 | -29.4754 | 91.42 | 0.085224 | -0.0451 | 0.024629 | -0.029595 | 0.06831 | 0.030642 | -0.085608 | -0.14897 | -0.030674 | -0.08205 | -0.065154 | 0.039079 | 0.014064 | -0.038063 | 0.051766 | 0.131 | 0.000676 | 0.070405 | 0.016181 | 0.11409 | 0.076418 | -0.039832 | -0.10319 | 0.015102 | -0.036274 | -0.019378 | 0.084855 | 0.05984 | 0.007713 | 0.097542 | -0.18804 | -0.1109 | -0.12113 | -0.043987
2838.7188 | 121.1609 | -5.4291 | 115.654 | 0.062332 | -0.067994 | 0.006315 | -0.043331 | 0.045421 | 0.016907 | -0.10392 | -0.16728 | -0.058147 | -0.1141 | -0.088049 | 0.06197 | 0.032376 | -0.033484 | 0.074657 | 0.10811 | -0.022218 | 0.052091 | 0.002445 | 0.091197 | 0.062683 | -0.058145 | -0.1215 | -0.012371 | -0.068322 | -0.042273 | 0.10775 | 0.078152 | 0.012292 | 0.12043 | -0.22925 | -0.1338 | -0.17607 | -0.080614
2840.4219 | 121.1884 | -5.3513 | 115.7639 | 0.057754 | -0.072572 | 0.001736 | -0.047909 | 0.045421 | 0.016907 | -0.1085 | -0.16728 | -0.062726 | -0.10952 | -0.097207 | 0.066548 | 0.036954 | -0.038063 | 0.065501 | 0.10353 | -0.026796 | 0.047512 | -0.002133 | 0.091197 | 0.062683 | -0.062723 | -0.1215 | -0.01695 | -0.063744 | -0.051431 | 0.11232 | 0.08273 | 0.007713 | 0.11128 | -0.23383 | -0.12922 | -0.17607 | -0.071457
2842.2188 | 121.1563 | -5.1132 | 116.0934 | 0.048597 | -0.063415 | 0.010893 | -0.043331 | 0.045421 | 0.012329 | -0.1085 | -0.17186 | -0.053568 | -0.095785 | -0.092628 | 0.06197 | 0.032376 | -0.038063 | 0.065501 | 0.094373 | -0.017639 | 0.056669 | 0.002445 | 0.091197 | 0.058105 | -0.062723 | -0.12608 | -0.007792 | -0.050009 | -0.046852 | 0.10775 | 0.078152 | 0.007713 | 0.11128 | -0.23383 | -0.13379 | -0.15775 | -0.057722
2844 | 121.1609 | -5.0858 | 116.1255 | 0.057754 | -0.063415 | 0.001736 | -0.047909 | 0.049999 | 0.012329 | -0.1085 | -0.16728 | -0.053568 | -0.10036 | -0.092628 | 0.057392 | 0.027798 | -0.04722 | 0.070079 | 0.10353 | -0.017639 | 0.047512 | -0.002133 | 0.095775 | 0.058105 | -0.062723 | -0.1215 | -0.007792 | -0.054587 | -0.046852 | 0.10317 | 0.073574 | -0.001444 | 0.11585 | -0.22467 | -0.12006 | -0.15775 | -0.053143
2845.7188 | 121.3348 | -5.1132 | 116.0339 | 0.062332 | -0.067994 | 0.010893 | -0.052488 | 0.049999 | 0.00775 | -0.1085 | -0.17186 | -0.053568 | -0.10952 | -0.088049 | 0.057392 | 0.036954 | -0.033484 | 0.070079 | 0.10811 | -0.022218 | 0.056669 | -0.006712 | 0.095775 | 0.053526 | -0.062723 | -0.12608 | -0.007792 | -0.063744 | -0.042273 | 0.10317 | 0.08273 | 0.012292 | 0.11585 | -0.22925 | -0.13837 | -0.16691 | -0.076036
2847.4844 | 121.2616 | -4.834 | 116.3727 | 0.057754 | -0.067994 | 0.006315 | -0.047909 | 0.045421 | 0.016907 | -0.1085 | -0.17186 | -0.053568 | -0.10494 | -0.088049 | 0.071126 | 0.032376 | -0.038063 | 0.070079 | 0.10353 | -0.022218 | 0.052091 | -0.002133 | 0.091197 | 0.062683 | -0.062723 | -0.12608 | -0.007792 | -0.059166 | -0.042273 | 0.1169 | 0.078152 | 0.007713 | 0.11585 | -0.24298 | -0.13379 | -0.17607 | -0.066879
2849.2031 | 121.2982 | -4.8569 | 116.3132 | 0.057754 | -0.072572 | 0.010893 | -0.052488 | 0.049999 | 0.012329 | -0.1085 | -0.17644 | -0.04899 | -0.10952 | -0.097207 | 0.066548 | 0.041532 | -0.033484 | 0.074657 | 0.10353 | -0.026796 | 0.056669 | -0.006712 | 0.095775 | 0.058105 | -0.062723 | -0.13066 | -0.003214 | -0.063744 | -0.051431 | 0.11232 | 0.087308 | 0.012292 | 0.12043 | -0.24299 | -0.14295 | -0.17607 | -0.076036
2850.9844 | 121.2708 | -4.6051 | 116.6428 | 0.062332 | -0.067994 | 0.006315 | -0.043331 | 0.049999 | 0.016907 | -0.10392 | -0.17186 | -0.053568 | -0.10952 | -0.097207 | 0.066548 | 0.032376 | -0.033484 | 0.074657 | 0.10811 | -0.022218 | 0.052091 | 0.002445 | 0.095775 | 0.062683 | -0.058145 | -0.12608 | -0.007792 | -0.063744 | -0.051431 | 0.11232 | 0.078152 | 0.012292 | 0.12043 | -0.23841 | -0.13837 | -0.17607 | -0.076036
2852.7812 | 121.3165 | -4.6875 | 116.5649 | 0.057754 | -0.072572 | 0.010893 | -0.052488 | 0.045421 | 0.00775 | -0.10392 | -0.17186 | -0.04899 | -0.10952 | -0.097207 | 0.066548 | 0.032376 | -0.042641 | 0.070079 | 0.10353 | -0.026796 | 0.056669 | -0.006712 | 0.091197 | 0.053526 | -0.058145 | -0.12608 | -0.003214 | -0.063744 | -0.051431 | 0.11232 | 0.078152 | 0.003135 | 0.11585 | -0.23841 | -0.12922 | -0.17607 | -0.066879
2854.5625 | 121.3715 | -5.04 | 116.1896 | 0.053175 | -0.067994 | 0.006315 | -0.047909 | 0.045421 | 0.012329 | -0.1085 | -0.17186 | -0.04899 | -0.10952 | -0.088049 | 0.057392 | 0.036954 | -0.033484 | 0.074657 | 0.098951 | -0.022218 | 0.052091 | -0.002133 | 0.091197 | 0.058105 | -0.062723 | -0.12608 | -0.003214 | -0.063744 | -0.042273 | 0.10317 | 0.08273 | 0.012292 | 0.12043 | -0.22925 | -0.13837 | -0.16691 | -0.076036
2856.3438 | 121.3028 | -4.7607 | 116.5283 | 0.057754 | -0.072572 | 0.010893 | -0.043331 | 0.054577 | 0.012329 | -0.1085 | -0.16728 | -0.058147 | -0.1141 | -0.097207 | 0.06197 | 0.027798 | -0.042641 | 0.070079 | 0.10353 | -0.026796 | 0.056669 | 0.002445 | 0.10035 | 0.058105 | -0.062723 | -0.1215 | -0.012371 | -0.068322 | -0.051431 | 0.10775 | 0.073574 | 0.003135 | 0.11585 | -0.22925 | -0.12464 | -0.17607 | -0.071457
2858.0469 | 121.3074 | -4.7562 | 116.5466 | 0.057754 | -0.077151 | 0.006315 | -0.043331 | 0.054577 | 0.012329 | -0.099343 | -0.16728 | -0.053568 | -0.10036 | -0.088049 | 0.066548 | 0.027798 | -0.038063 | 0.074657 | 0.10353 | -0.031375 | 0.052091 | 0.002445 | 0.10035 | 0.058105 | -0.053567 | -0.1215 | -0.007792 | -0.054587 | -0.042273 | 0.11232 | 0.073574 | 0.007713 | 0.12043 | -0.23383 | -0.12922 | -0.16691 | -0.0623
2859.8281 | 121.376 | -4.6509 | 116.5878 | 0.053175 | -0.067994 | 0.001736 | -0.047909 | 0.045421 | 0.00775 | -0.10392 | -0.16728 | -0.058147 | -0.10036 | -0.092628 | 0.057392 | 0.032376 | -0.033484 | 0.074657 | 0.098951 | -0.022218 | 0.047512 | -0.002133 | 0.091197 | 0.053526 | -0.058145 | -0.1215 | -0.012371 | -0.054587 | -0.046852 | 0.10317 | 0.078152 | 0.012292 | 0.12043 | -0.22467 | -0.1338 | -0.15775 | -0.066879
2861.6094 | 121.3989 | -4.866 | 116.3864 | 0.06691 | -0.067994 | 0.006315 | -0.047909 | 0.045421 | 0.012329 | -0.10392 | -0.16728 | -0.04899 | -0.10952 | -0.092628 | 0.071126 | 0.032376 | -0.033484 | 0.070079 | 0.11269 | -0.022218 | 0.052091 | -0.002133 | 0.091197 | 0.058105 | -0.058145 | -0.1215 | -0.003214 | -0.063744 | -0.046852 | 0.1169 | 0.078152 | 0.012292 | 0.11585 | -0.23841 | -0.1338 | -0.18065 | -0.076036
2863.3906 | 121.4218 | -5.0812 | 116.1438 | 0.057754 | -0.072572 | 0.001736 | -0.047909 | 0.045421 | 0.00775 | -0.1085 | -0.17186 | -0.053568 | -0.10494 | -0.097207 | 0.057392 | 0.036954 | -0.028906 | 0.079235 | 0.10353 | -0.026796 | 0.047512 | -0.002133 | 0.091197 | 0.053526 | -0.062723 | -0.12608 | -0.007792 | -0.059166 | -0.051431 | 0.10317 | 0.08273 | 0.01687 | 0.12501 | -0.22925 | -0.14295 | -0.16233 | -0.076036
2865.1094 | 121.3623 | -5.2597 | 116.066 | 0.057754 | -0.063415 | 0.006315 | -0.043331 | 0.049999 | 0.00775 | -0.1085 | -0.16728 | -0.053568 | -0.10494 | -0.092628 | 0.06197 | 0.036954 | -0.04722 | 0.070079 | 0.10353 | -0.017639 | 0.052091 | 0.002445 | 0.095775 | 0.053526 | -0.062723 | -0.1215 | -0.007792 | -0.059166 | -0.046852 | 0.10775 | 0.08273 | -0.001444 | 0.11585 | -0.22925 | -0.12006 | -0.16691 | -0.057722
2866.8906 | 121.3943 | -5.1178 | 116.1987 | 0.06691 | -0.072572 | 0.010893 | -0.052488 | 0.049999 | 0.00775 | -0.1085 | -0.17186 | -0.053568 | -0.10494 | -0.097207 | 0.06197 | 0.032376 | -0.038063 | 0.070079 | 0.11269 | -0.026796 | 0.056669 | -0.006712 | 0.095775 | 0.053526 | -0.062723 | -0.12608 | -0.007792 | -0.059166 | -0.051431 | 0.10775 | 0.078152 | 0.007713 | 0.11585 | -0.23383 | -0.13379 | -0.16691 | -0.066879
2868.6875 | 121.3715 | -4.9576 | 116.4047 | 0.062332 | -0.067994 | 0.006315 | -0.047909 | 0.045421 | 0.016907 | -0.10392 | -0.17186 | -0.053568 | -0.10494 | -0.10637 | 0.06197 | 0.027798 | -0.038063 | 0.079235 | 0.10811 | -0.022218 | 0.052091 | -0.002133 | 0.091197 | 0.062683 | -0.058145 | -0.12608 | -0.007792 | -0.059166 | -0.060589 | 0.10775 | 0.073574 | 0.007713 | 0.12501 | -0.23383 | -0.13379 | -0.16691 | -0.066879
2870.4531 | 121.4264 | -5.3192 | 115.9836 | 0.053175 | -0.067994 | 0.006315 | -0.047909 | 0.049999 | 0.016907 | -0.1085 | -0.17186 | -0.04899 | -0.10494 | -0.092628 | 0.06197 | 0.032376 | -0.033484 | 0.070079 | 0.098951 | -0.022218 | 0.052091 | -0.002133 | 0.095775 | 0.062683 | -0.062723 | -0.12608 | -0.003214 | -0.059166 | -0.046852 | 0.10775 | 0.078152 | 0.012292 | 0.11585 | -0.23383 | -0.13837 | -0.16691 | -0.071458
2872.2344 | 121.4996 | -5.9784 | 115.2924 | 0.062332 | -0.072572 | 0.010893 | -0.047909 | 0.040843 | 0.012329 | -0.1085 | -0.16728 | -0.053568 | -0.10036 | -0.088049 | 0.06197 | 0.036954 | -0.024328 | 0.070079 | 0.10811 | -0.026796 | 0.056669 | -0.002133 | 0.086619 | 0.058105 | -0.062723 | -0.1215 | -0.007792 | -0.054587 | -0.042273 | 0.10775 | 0.08273 | 0.021448 | 0.11585 | -0.22925 | -0.14295 | -0.16233 | -0.076035
2873.9531 | 121.431 | -6.221 | 115.1001 | 0.062332 | -0.077151 | 0.010893 | -0.047909 | 0.045421 | 0.012329 | -0.1085 | -0.16728 | -0.053568 | -0.10952 | -0.08347 | 0.066548 | 0.032376 | -0.033484 | 0.074657 | 0.10811 | -0.031375 | 0.056669 | -0.002133 | 0.091197 | 0.058105 | -0.062723 | -0.1215 | -0.007792 | -0.063744 | -0.037694 | 0.11232 | 0.078152 | 0.012292 | 0.12043 | -0.23383 | -0.1338 | -0.17607 | -0.076036
2875.7344 | 121.3623 | -6.2942 | 115.0772 | 0.062332 | -0.063415 | 0.010893 | -0.043331 | 0.049999 | 0.016907 | -0.10392 | -0.16728 | -0.044411 | -0.10494 | -0.097207 | 0.066548 | 0.032376 | -0.042641 | 0.070079 | 0.10811 | -0.017639 | 0.056669 | 0.002445 | 0.095775 | 0.062683 | -0.058145 | -0.1215 | 0.001365 | -0.059166 | -0.051431 | 0.11232 | 0.078152 | 0.003135 | 0.11585 | -0.23383 | -0.12464 | -0.17149 | -0.062301
2877.5 | 121.5179 | -6.4133 | 114.8483 | 0.062332 | -0.072572 | 0.015472 | -0.043331 | 0.049999 | 0.00775 | -0.1085 | -0.1627 | -0.053568 | -0.10952 | -0.092628 | 0.06197 | 0.036954 | -0.033484 | 0.074657 | 0.10811 | -0.026796 | 0.061248 | 0.002445 | 0.095775 | 0.053526 | -0.062723 | -0.11693 | -0.007792 | -0.063744 | -0.046852 | 0.10775 | 0.08273 | 0.012292 | 0.12043 | -0.22467 | -0.12922 | -0.17149 | -0.076036
2879.2188 | 121.3898 | -6.7612 | 114.6103 | 0.062332 | -0.072572 | 0.006315 | -0.047909 | 0.054577 | 0.016907 | -0.10392 | -0.15812 | -0.053568 | -0.10494 | -0.097207 | 0.066548 | 0.032376 | -0.042641 | 0.074657 | 0.10811 | -0.026796 | 0.052091 | -0.002133 | 0.10035 | 0.062683 | -0.058145 | -0.11235 | -0.007792 | -0.059166 | -0.051431 | 0.11232 | 0.078152 | 0.003135 | 0.12043 | -0.22467 | -0.11548 | -0.17149 | -0.062301
2881.0156 | 121.4035 | -7.4432 | 113.9053 | 0.057754 | -0.067994 | 0.001736 | -0.047909 | 0.045421 | 0.016907 | -0.10392 | -0.15812 | -0.053568 | -0.10494 | -0.092628 | 0.06197 | 0.032376 | -0.042641 | 0.074657 | 0.10353 | -0.022218 | 0.047512 | -0.002133 | 0.091197 | 0.062683 | -0.058145 | -0.11235 | -0.007792 | -0.059166 | -0.046852 | 0.10775 | 0.078152 | 0.003135 | 0.12043 | -0.22009 | -0.11548 | -0.16691 | -0.062301
2882.7344 | 121.4218 | -7.489 | 113.8733 | 0.062332 | -0.072572 | 0.010893 | -0.043331 | 0.049999 | 0.016907 | -0.1085 | -0.1627 | -0.04899 | -0.1141 | -0.088049 | 0.057392 | 0.027798 | -0.033484 | 0.079235 | 0.10811 | -0.026796 | 0.056669 | 0.002445 | 0.095775 | 0.062683 | -0.062723 | -0.11693 | -0.003214 | -0.068322 | -0.042273 | 0.10317 | 0.073574 | 0.012292 | 0.12501 | -0.22009 | -0.12922 | -0.17149 | -0.080614
2884.5 | 121.4264 | -6.9122 | 114.4455 | 0.057754 | -0.063415 | 0.006315 | -0.043331 | 0.040843 | 0.021485 | -0.10392 | -0.1627 | -0.053568 | -0.10494 | -0.088049 | 0.057392 | 0.027798 | -0.038063 | 0.070079 | 0.10353 | -0.017639 | 0.052091 | 0.002445 | 0.086619 | 0.067261 | -0.058145 | -0.11693 | -0.007792 | -0.059166 | -0.042273 | 0.10317 | 0.073574 | 0.007713 | 0.11585 | -0.22009 | -0.12464 | -0.16233 | -0.066879
2886.2344 | 121.4401 | -7.0038 | 114.3036 | 0.057754 | -0.072572 | 0.006315 | -0.043331 | 0.040843 | 0.016907 | -0.10392 | -0.16728 | -0.062726 | -0.10494 | -0.08347 | 0.066548 | 0.027798 | -0.038063 | 0.070079 | 0.10353 | -0.026796 | 0.052091 | 0.002445 | 0.086619 | 0.062683 | -0.058145 | -0.1215 | -0.01695 | -0.059166 | -0.037694 | 0.11232 | 0.073574 | 0.007713 | 0.11585 | -0.23383 | -0.12922 | -0.17149 | -0.066879
2888 | 121.4035 | -6.752 | 114.7202 | 0.06691 | -0.077151 | 0.001736 | -0.038752 | 0.054577 | 0.012329 | -0.099343 | -0.16728 | -0.044411 | -0.10494 | -0.092628 | 0.06197 | 0.027798 | -0.028906 | 0.070079 | 0.11269 | -0.031375 | 0.047512 | 0.007024 | 0.10035 | 0.058105 | -0.053567 | -0.1215 | 0.001365 | -0.059166 | -0.046852 | 0.10775 | 0.073574 | 0.01687 | 0.11585 | -0.22925 | -0.13837 | -0.16691 | -0.076036
2889.7969 | 121.4767 | -43.9499 | 77.0966 | 0.080646 | -0.054257 | 0.038365 | -0.020438 | 0.082044 | 0.035221 | -0.08103 | -0.13981 | -0.026096 | -0.086628 | -0.060575 | 0.039079 | 0.004908 | -0.051798 | 0.051766 | 0.12642 | -0.008481 | 0.084141 | 0.025338 | 0.12782 | 0.080997 | -0.035254 | -0.094033 | 0.01968 | -0.040852 | -0.014799 | 0.084855 | 0.050684 | -0.006022 | 0.097542 | -0.17889 | -0.088011 | -0.12571 | -0.03483
2891.5312 | 121.463 | -44.1238 | 77.0554 | 0.089802 | -0.0451 | 0.024629 | -0.01586 | 0.072888 | 0.044377 | -0.085608 | -0.13523 | -0.021517 | -0.08205 | -0.069733 | 0.043657 | 0.009486 | -0.04722 | 0.047188 | 0.13558 | 0.000676 | 0.070405 | 0.029916 | 0.11866 | 0.090153 | -0.039832 | -0.089454 | 0.024259 | -0.036274 | -0.023957 | 0.089433 | 0.055262 | -0.001444 | 0.092964 | -0.17889 | -0.08801 | -0.12571 | -0.03483
2893.2969 | 121.4539 | -44.1788 | 77.092 | 0.089802 | -0.040521 | 0.033786 | -0.025017 | 0.077466 | 0.044377 | -0.076452 | -0.14897 | -0.021517 | -0.08205 | -0.065154 | 0.034501 | 0.004908 | -0.042641 | 0.047188 | 0.13558 | 0.005255 | 0.079562 | 0.020759 | 0.12324 | 0.090153 | -0.030676 | -0.10319 | 0.024259 | -0.036274 | -0.019378 | 0.080277 | 0.050684 | 0.003135 | 0.092964 | -0.18347 | -0.10632 | -0.11655 | -0.039409
2895.0781 | 121.5546 | -44.1101 | 77.1011 | 0.085224 | -0.040521 | 0.033786 | -0.025017 | 0.082044 | 0.035221 | -0.08103 | -0.13065 | -0.026096 | -0.072894 | -0.069733 | 0.034501 | -0.004248 | -0.042641 | 0.038032 | 0.131 | 0.005255 | 0.079562 | 0.020759 | 0.12782 | 0.080997 | -0.035254 | -0.084876 | 0.01968 | -0.027118 | -0.023957 | 0.080277 | 0.041528 | 0.003135 | 0.083808 | -0.16515 | -0.088011 | -0.10739 | -0.030253
2896.8594 | 121.463 | -43.9957 | 77.2797 | 0.085224 | -0.049678 | 0.029208 | -0.025017 | 0.06831 | 0.035221 | -0.08103 | -0.13981 | -0.030674 | -0.072894 | -0.069733 | 0.034501 | 0.014064 | -0.04722 | 0.047188 | 0.131 | -0.003902 | 0.074984 | 0.020759 | 0.11409 | 0.080997 | -0.035254 | -0.094033 | 0.015102 | -0.027118 | -0.023957 | 0.080277 | 0.05984 | -0.001444 | 0.092964 | -0.17431 | -0.092589 | -0.10739 | -0.025674
2898.6406 | 121.4355 | -43.9178 | 77.3849 | 0.085224 | -0.049678 | 0.038365 | -0.011281 | 0.082044 | 0.044377 | -0.076452 | -0.13523 | -0.026096 | -0.077472 | -0.065154 | 0.034501 | 0.004908 | -0.042641 | 0.047188 | 0.131 | -0.003902 | 0.084141 | 0.034495 | 0.12782 | 0.090153 | -0.030676 | -0.089454 | 0.01968 | -0.031696 | -0.019378 | 0.080277 | 0.050684 | 0.003135 | 0.092964 | -0.16973 | -0.092589 | -0.11197 | -0.034831
2900.3594 | 121.5225 | -43.7393 | 77.5131 | 0.085224 | -0.049678 | 0.042944 | -0.01586 | 0.082044 | 0.044377 | -0.08103 | -0.13981 | -0.035253 | -0.08205 | -0.069733 | 0.039079 | 0.009486 | -0.04722 | 0.038032 | 0.131 | -0.003902 | 0.08872 | 0.029916 | 0.12782 | 0.090153 | -0.035254 | -0.094033 | 0.010523 | -0.036274 | -0.023957 | 0.084855 | 0.055262 | -0.001444 | 0.083808 | -0.17889 | -0.092589 | -0.12113 | -0.03483
2902.1406 | 121.4859 | -43.959 | 77.3209 | 0.085224 | -0.0451 | 0.029208 | -0.025017 | 0.06831 | 0.035221 | -0.076452 | -0.13981 | -0.021517 | -0.072894 | -0.060575 | 0.029923 | 0.00033 | -0.042641 | 0.047188 | 0.131 | 0.000676 | 0.074984 | 0.020759 | 0.11409 | 0.080997 | -0.030676 | -0.094033 | 0.024259 | -0.027118 | -0.014799 | 0.075699 | 0.046106 | 0.003135 | 0.092964 | -0.16973 | -0.097168 | -0.10282 | -0.030253
2903.9219 | 121.5134 | -43.8766 | 77.3804 | 0.085224 | -0.0451 | 0.033786 | -0.020438 | 0.072888 | 0.044377 | -0.067295 | -0.14439 | -0.021517 | -0.077472 | -0.065154 | 0.043657 | 0.004908 | -0.042641 | 0.047188 | 0.131 | 0.000676 | 0.079562 | 0.025338 | 0.11866 | 0.090153 | -0.021519 | -0.098611 | 0.024259 | -0.031696 | -0.019378 | 0.089433 | 0.050684 | 0.003135 | 0.092964 | -0.18804 | -0.10175 | -0.12113 | -0.034831
2905.6406 | 121.5546 | -43.6203 | 77.6276 | 0.080646 | -0.040521 | 0.038365 | -0.020438 | 0.072888 | 0.039799 | -0.08103 | -0.13523 | -0.026096 | -0.077472 | -0.069733 | 0.034501 | 0.009486 | -0.042641 | 0.04261 | 0.12642 | 0.005255 | 0.084141 | 0.025338 | 0.11866 | 0.085575 | -0.035254 | -0.089454 | 0.01968 | -0.031696 | -0.023957 | 0.080277 | 0.055262 | 0.003135 | 0.088386 | -0.16973 | -0.092589 | -0.11197 | -0.034831
2907.4062 | 121.5683 | -43.4921 | 77.774 | 0.085224 | -0.049678 | 0.033786 | -0.025017 | 0.077466 | 0.039799 | -0.08103 | -0.13523 | -0.021517 | -0.072894 | -0.065154 | 0.034501 | 0.004908 | -0.04722 | 0.047188 | 0.131 | -0.003902 | 0.079562 | 0.020759 | 0.12324 | 0.085575 | -0.035254 | -0.089454 | 0.024259 | -0.027118 | -0.019378 | 0.080277 | 0.050684 | -0.001444 | 0.092964 | -0.16973 | -0.08801 | -0.10739 | -0.025674
2909.2031 | 121.4676 | -44.2886 | 77.0508 | 0.080646 | -0.054257 | 0.029208 | -0.01586 | 0.082044 | 0.044377 | -0.071874 | -0.13981 | -0.026096 | -0.077472 | -0.065154 | 0.034501 | 0.009486 | -0.051798 | 0.04261 | 0.12642 | -0.008481 | 0.074984 | 0.029916 | 0.12782 | 0.090153 | -0.026098 | -0.094033 | 0.01968 | -0.031696 | -0.019378 | 0.080277 | 0.055262 | -0.006022 | 0.088386 | -0.17431 | -0.088011 | -0.11197 | -0.025674
2910.9219 | 121.5546 | -44.1788 | 77.0828 | 0.089802 | -0.049678 | 0.029208 | -0.01586 | 0.072888 | 0.039799 | -0.08103 | -0.13981 | -0.021517 | -0.077472 | -0.060575 | 0.034501 | -0.004248 | -0.051798 | 0.047188 | 0.13558 | -0.003902 | 0.074984 | 0.029916 | 0.11866 | 0.085575 | -0.035254 | -0.094033 | 0.024259 | -0.031696 | -0.014799 | 0.080277 | 0.041528 | -0.006022 | 0.092964 | -0.17431 | -0.088011 | -0.11197 | -0.025674
2912.7031 | 121.4767 | -44.1376 | 77.179 | 0.085224 | -0.049678 | 0.029208 | -0.011281 | 0.077466 | 0.053534 | -0.076452 | -0.13523 | -0.021517 | -0.077472 | -0.069733 | 0.034501 | 0.009486 | -0.051798 | 0.04261 | 0.131 | -0.003902 | 0.074984 | 0.034495 | 0.12324 | 0.09931 | -0.030676 | -0.089454 | 0.024259 | -0.031696 | -0.023957 | 0.080277 | 0.055262 | -0.006022 | 0.088386 | -0.16973 | -0.083432 | -0.11197 | -0.025674
2914.4219 | 121.5363 | -44.0277 | 77.2476 | 0.089802 | -0.0451 | 0.024629 | -0.011281 | 0.082044 | 0.044377 | -0.085608 | -0.13523 | -0.021517 | -0.072894 | -0.060575 | 0.034501 | 0.004908 | -0.04722 | 0.047188 | 0.13558 | 0.000676 | 0.070405 | 0.034495 | 0.12782 | 0.090153 | -0.039832 | -0.089454 | 0.024259 | -0.027118 | -0.014799 | 0.080277 | 0.050684 | -0.001444 | 0.092964 | -0.16973 | -0.08801 | -0.10739 | -0.025674
2916.2031 | 121.6187 | -44.0094 | 77.2751 | 0.089802 | -0.0451 | 0.033786 | -0.01586 | 0.082044 | 0.044377 | -0.071874 | -0.13523 | -0.026096 | -0.072894 | -0.065154 | 0.039079 | 0.004908 | -0.042641 | 0.04261 | 0.13558 | 0.000676 | 0.079562 | 0.029916 | 0.12782 | 0.090153 | -0.026098 | -0.089454 | 0.01968 | -0.027118 | -0.019378 | 0.084855 | 0.050684 | 0.003135 | 0.088386 | -0.17431 | -0.092589 | -0.11197 | -0.030253
2917.9688 | 121.6095 | -44.1559 | 77.0966 | 0.085224 | -0.0451 | 0.024629 | -0.020438 | 0.072888 | 0.039799 | -0.071874 | -0.13981 | -0.016938 | -0.077472 | -0.069733 | 0.029923 | 0.004908 | -0.04722 | 0.04261 | 0.131 | 0.000676 | 0.070405 | 0.025338 | 0.11866 | 0.085575 | -0.026098 | -0.094033 | 0.028838 | -0.031696 | -0.023957 | 0.075699 | 0.050684 | -0.001444 | 0.088386 | -0.16973 | -0.092589 | -0.1074 | -0.030252
2919.75 | 121.6049 | -44.0186 | 77.2476 | 0.080646 | -0.040521 | 0.038365 | -0.01586 | 0.077466 | 0.039799 | -0.085608 | -0.13523 | -0.016938 | -0.072894 | -0.065154 | 0.034501 | 0.004908 | -0.051798 | 0.047188 | 0.12642 | 0.005255 | 0.084141 | 0.029916 | 0.12324 | 0.085575 | -0.039832 | -0.089454 | 0.028838 | -0.027118 | -0.019378 | 0.080277 | 0.050684 | -0.006022 | 0.092964 | -0.16973 | -0.083432 | -0.10739 | -0.021096
2921.5312 | 121.4767 | -43.9224 | 77.4307 | 0.094381 | -0.0451 | 0.038365 | -0.020438 | 0.077466 | 0.039799 | -0.076452 | -0.13981 | -0.016938 | -0.072894 | -0.060575 | 0.039079 | 0.004908 | -0.042641 | 0.038032 | 0.14016 | 0.000676 | 0.084141 | 0.025338 | 0.12324 | 0.085575 | -0.030676 | -0.094033 | 0.028838 | -0.027118 | -0.014799 | 0.084855 | 0.050684 | 0.003135 | 0.083808 | -0.17889 | -0.097168 | -0.11197 | -0.030253
2923.2344 | 121.6049 | -43.5928 | 77.7054 | 0.085224 | -0.040521 | 0.033786 | -0.01586 | 0.082044 | 0.039799 | -0.076452 | -0.13065 | -0.026096 | -0.077472 | -0.065154 | 0.034501 | 0.009486 | -0.04722 | 0.047188 | 0.131 | 0.005255 | 0.079562 | 0.029916 | 0.12782 | 0.085575 | -0.030676 | -0.084876 | 0.01968 | -0.031696 | -0.019378 | 0.080277 | 0.055262 | -0.001444 | 0.092964 | -0.16515 | -0.083432 | -0.11197 | -0.030252
2925.0156 | 121.6049 | -43.5196 | 77.774 | 0.080646 | -0.049678 | 0.038365 | -0.025017 | 0.082044 | 0.044377 | -0.08103 | -0.13065 | -0.021517 | -0.077472 | -0.069733 | 0.034501 | 0.009486 | -0.051798 | 0.047188 | 0.12642 | -0.003902 | 0.084141 | 0.020759 | 0.12782 | 0.090153 | -0.035254 | -0.084876 | 0.024259 | -0.031696 | -0.023957 | 0.080277 | 0.055262 | -0.006022 | 0.092964 | -0.16515 | -0.078854 | -0.11197 | -0.025674
2926.7344 | 121.5454 | -43.4967 | 77.8427 | 0.080646 | -0.040521 | 0.033786 | -0.011281 | 0.06831 | 0.044377 | -0.076452 | -0.13981 | -0.026096 | -0.077472 | -0.065154 | 0.034501 | 0.009486 | -0.042641 | 0.047188 | 0.12642 | 0.005255 | 0.079562 | 0.034495 | 0.11409 | 0.090153 | -0.030676 | -0.094033 | 0.01968 | -0.031696 | -0.019378 | 0.080277 | 0.055262 | 0.003135 | 0.092964 | -0.17431 | -0.097168 | -0.11197 | -0.034831
2928.5156 | 121.6187 | -43.4738 | 77.7924 | 0.085224 | -0.049678 | 0.033786 | -0.020438 | 0.077466 | 0.044377 | -0.085608 | -0.13981 | -0.016938 | -0.072894 | -0.065154 | 0.034501 | 0.004908 | -0.042641 | 0.047188 | 0.131 | -0.003902 | 0.079562 | 0.025338 | 0.12324 | 0.090153 | -0.039832 | -0.094033 | 0.028838 | -0.027118 | -0.019378 | 0.080277 | 0.050684 | 0.003135 | 0.092964 | -0.17431 | -0.097168 | -0.10739 | -0.030253
2930.25 | 121.55 | -43.5059 | 77.8473 | 0.080646 | -0.0451 | 0.033786 | -0.011281 | 0.082044 | 0.035221 | -0.076452 | -0.13981 | -0.021517 | -0.08205 | -0.069733 | 0.029923 | 0.004908 | -0.042641 | 0.04261 | 0.12642 | 0.000676 | 0.079562 | 0.034495 | 0.12782 | 0.080997 | -0.030676 | -0.094033 | 0.024259 | -0.036274 | -0.023957 | 0.075699 | 0.050684 | 0.003135 | 0.088386 | -0.16973 | -0.097168 | -0.11197 | -0.039409
2932.0312 | 121.5866 | -43.4509 | 77.8198 | 0.080646 | -0.040521 | 0.033786 | -0.020438 | 0.077466 | 0.044377 | -0.08103 | -0.13981 | -0.021517 | -0.072894 | -0.074312 | 0.039079 | 0.004908 | -0.04722 | 0.056344 | 0.12642 | 0.005255 | 0.079562 | 0.025338 | 0.12324 | 0.090153 | -0.035254 | -0.094033 | 0.024259 | -0.027118 | -0.028536 | 0.084855 | 0.050684 | -0.001444 | 0.10212 | -0.17889 | -0.092589 | -0.11197 | -0.025674
2933.75 | 121.5729 | -43.3456 | 77.9755 | 0.089802 | -0.040521 | 0.033786 | -0.020438 | 0.086622 | 0.039799 | -0.08103 | -0.13523 | -0.021517 | -0.077472 | -0.065154 | 0.029923 | 0.004908 | -0.056376 | 0.051766 | 0.13558 | 0.005255 | 0.079562 | 0.025338 | 0.1324 | 0.085575 | -0.035254 | -0.089454 | 0.024259 | -0.031696 | -0.019378 | 0.075699 | 0.050684 | -0.0106 | 0.097542 | -0.16515 | -0.078854 | -0.1074 | -0.021096
2935.5156 | 121.4813 | -43.3456 | 78.0121 | 0.080646 | -0.035942 | 0.042944 | -0.025017 | 0.072888 | 0.039799 | -0.076452 | -0.14439 | -0.030674 | -0.08205 | -0.060575 | 0.034501 | 0.009486 | -0.042641 | 0.051766 | 0.12642 | 0.009834 | 0.08872 | 0.020759 | 0.11866 | 0.085575 | -0.030676 | -0.098611 | 0.015102 | -0.036274 | -0.014799 | 0.080277 | 0.055262 | 0.003135 | 0.097542 | -0.17889 | -0.10175 | -0.11655 | -0.039409
2937.2344 | 121.5454 | -43.1671 | 78.186 | 0.089802 | -0.049678 | 0.024629 | -0.020438 | 0.072888 | 0.048956 | -0.076452 | -0.13981 | -0.012359 | -0.072894 | -0.060575 | 0.039079 | 0.004908 | -0.042641 | 0.047188 | 0.13558 | -0.003902 | 0.070405 | 0.025338 | 0.11866 | 0.094732 | -0.030676 | -0.094033 | 0.033417 | -0.027118 | -0.014799 | 0.084855 | 0.050684 | 0.003135 | 0.092964 | -0.17889 | -0.097168 | -0.11197 | -0.030253
2939.0156 | 121.4767 | -43.1717 | 78.2181 | 0.089802 | -0.0451 | 0.038365 | -0.020438 | 0.077466 | 0.044377 | -0.08103 | -0.13523 | -0.016938 | -0.08205 | -0.065154 | 0.034501 | 0.009486 | -0.042641 | 0.047188 | 0.13558 | 0.000676 | 0.084141 | 0.025338 | 0.12324 | 0.090153 | -0.035254 | -0.089454 | 0.028838 | -0.036274 | -0.019378 | 0.080277 | 0.055262 | 0.003135 | 0.092964 | -0.16973 | -0.092589 | -0.11655 | -0.039409
2940.7969 | 121.5775 | -43.0115 | 78.3646 | 0.080646 | -0.0451 | 0.029208 | -0.025017 | 0.072888 | 0.044377 | -0.08103 | -0.14439 | -0.016938 | -0.086628 | -0.065154 | 0.025345 | 0.009486 | -0.04722 | 0.047188 | 0.12642 | 0.000676 | 0.074984 | 0.020759 | 0.11866 | 0.090153 | -0.035254 | -0.098611 | 0.028838 | -0.040852 | -0.019378 | 0.071121 | 0.055262 | -0.001444 | 0.092964 | -0.16973 | -0.097167 | -0.11197 | -0.039408
2942.5156 | 121.5042 | -42.9932 | 78.4378 | 0.080646 | -0.0451 | 0.033786 | -0.020438 | 0.077466 | 0.039799 | -0.071874 | -0.13523 | -0.016938 | -0.08205 | -0.069733 | 0.034501 | 0.009486 | -0.04722 | 0.047188 | 0.12642 | 0.000676 | 0.079562 | 0.025338 | 0.12324 | 0.085575 | -0.026098 | -0.089454 | 0.028838 | -0.036274 | -0.023957 | 0.080277 | 0.055262 | -0.001444 | 0.092964 | -0.16973 | -0.08801 | -0.11655 | -0.03483
2944.2969 | 121.6232 | -43.0115 | 78.2547 | 0.085224 | -0.0451 | 0.038365 | -0.025017 | 0.086622 | 0.035221 | -0.076452 | -0.13981 | -0.026096 | -0.077472 | -0.060575 | 0.034501 | 0.014064 | -0.04722 | 0.051766 | 0.131 | 0.000676 | 0.084141 | 0.020759 | 0.1324 | 0.080997 | -0.030676 | -0.094033 | 0.01968 | -0.031696 | -0.014799 | 0.080277 | 0.05984 | -0.001444 | 0.097542 | -0.17431 | -0.092589 | -0.11197 | -0.030252
2946.0781 | 121.6095 | -43.0527 | 78.2639 | 0.089802 | -0.0451 | 0.029208 | -0.020438 | 0.072888 | 0.044377 | -0.076452 | -0.13523 | -0.021517 | -0.068315 | -0.065154 | 0.034501 | 0.004908 | -0.042641 | 0.047188 | 0.13558 | 0.000676 | 0.074984 | 0.025338 | 0.11866 | 0.090153 | -0.030676 | -0.089454 | 0.024259 | -0.022539 | -0.019378 | 0.080277 | 0.050684 | 0.003135 | 0.092964 | -0.16973 | -0.092589 | -0.10282 | -0.025674
2947.8594 | 121.6187 | -43.0252 | 78.2593 | 0.080646 | -0.040521 | 0.033786 | -0.025017 | 0.077466 | 0.044377 | -0.076452 | -0.13523 | -0.021517 | -0.077472 | -0.069733 | 0.034501 | 0.014064 | -0.042641 | 0.047188 | 0.12642 | 0.005255 | 0.079562 | 0.020759 | 0.12324 | 0.090153 | -0.030676 | -0.089454 | 0.024259 | -0.031696 | -0.023957 | 0.080277 | 0.05984 | 0.003135 | 0.092964 | -0.16973 | -0.092589 | -0.11197 | -0.034831
2949.5781 | 121.6599 | -43.1671 | 78.1311 | 0.085224 | -0.040521 | 0.033786 | -0.020438 | 0.072888 | 0.039799 | -0.08103 | -0.13981 | -0.026096 | -0.077472 | -0.065154 | 0.034501 | 0.004908 | -0.04722 | 0.051766 | 0.131 | 0.005255 | 0.079562 | 0.025338 | 0.11866 | 0.085575 | -0.035254 | -0.094033 | 0.01968 | -0.031696 | -0.019378 | 0.080277 | 0.050684 | -0.001444 | 0.097542 | -0.17431 | -0.092589 | -0.11197 | -0.030252
2951.3906 | 121.55 | -43.2678 | 78.1265 | 0.085224 | -0.031363 | 0.033786 | -0.01586 | 0.072888 | 0.030642 | -0.076452 | -0.13523 | -0.016938 | -0.08205 | -0.065154 | 0.043657 | 0.009486 | -0.051798 | 0.051766 | 0.131 | 0.014413 | 0.079562 | 0.029916 | 0.11866 | 0.076418 | -0.030676 | -0.089454 | 0.028838 | -0.036274 | -0.019378 | 0.089433 | 0.055262 | -0.006022 | 0.097542 | -0.17889 | -0.083432 | -0.12571 | -0.030252
2953.1094 | 121.6553 | -43.2678 | 78.0304 | 0.085224 | -0.040521 | 0.033786 | -0.025017 | 0.072888 | 0.039799 | -0.08103 | -0.13523 | -0.021517 | -0.08205 | -0.065154 | 0.039079 | 0.009486 | -0.04722 | 0.051766 | 0.131 | 0.005255 | 0.079562 | 0.020759 | 0.11866 | 0.085575 | -0.035254 | -0.089454 | 0.024259 | -0.036274 | -0.019378 | 0.084855 | 0.055262 | -0.001444 | 0.097542 | -0.17431 | -0.08801 | -0.12113 | -0.03483
2954.9062 | 121.5408 | -43.3411 | 78.0533 | 0.080646 | -0.054257 | 0.038365 | -0.020438 | 0.072888 | 0.044377 | -0.08103 | -0.14439 | -0.021517 | -0.072894 | -0.065154 | 0.034501 | 0.004908 | -0.04722 | 0.056344 | 0.12642 | -0.008481 | 0.084141 | 0.025338 | 0.11866 | 0.090153 | -0.035254 | -0.098611 | 0.024259 | -0.027118 | -0.019378 | 0.080277 | 0.050684 | -0.001444 | 0.10212 | -0.17889 | -0.097167 | -0.10739 | -0.025674
2956.6875 | 121.5363 | -43.3548 | 78.0579 | 0.089802 | -0.040521 | 0.033786 | -0.01586 | 0.06831 | 0.044377 | -0.08103 | -0.14439 | -0.016938 | -0.072894 | -0.065154 | 0.034501 | 0.004908 | -0.04722 | 0.04261 | 0.13558 | 0.005255 | 0.079562 | 0.029916 | 0.11409 | 0.090153 | -0.035254 | -0.098611 | 0.028838 | -0.027118 | -0.019378 | 0.080277 | 0.050684 | -0.001444 | 0.088386 | -0.17889 | -0.097167 | -0.10739 | -0.025674
2958.4531 | 121.6507 | -43.2724 | 78.0807 | 0.085224 | -0.049678 | 0.033786 | -0.01586 | 0.082044 | 0.039799 | -0.076452 | -0.13981 | -0.026096 | -0.08205 | -0.069733 | 0.034501 | 0.009486 | -0.038063 | 0.051766 | 0.131 | -0.003902 | 0.079562 | 0.029916 | 0.12782 | 0.085575 | -0.030676 | -0.094033 | 0.01968 | -0.036274 | -0.023957 | 0.080277 | 0.055262 | 0.007713 | 0.097542 | -0.17431 | -0.10175 | -0.11655 | -0.043987
2960.1875 | 121.5454 | -43.3228 | 78.0899 | 0.080646 | -0.0451 | 0.038365 | -0.020438 | 0.082044 | 0.044377 | -0.071874 | -0.14439 | -0.021517 | -0.077472 | -0.065154 | 0.029923 | 0.004908 | -0.04722 | 0.051766 | 0.12642 | 0.000676 | 0.084141 | 0.025338 | 0.12782 | 0.090153 | -0.026098 | -0.098611 | 0.024259 | -0.031696 | -0.019378 | 0.075699 | 0.050684 | -0.001444 | 0.097542 | -0.17431 | -0.097167 | -0.1074 | -0.030252
2961.9688 | 121.5271 | -43.364 | 78.0029 | 0.076067 | -0.0451 | 0.038365 | -0.025017 | 0.077466 | 0.039799 | -0.076452 | -0.13523 | -0.016938 | -0.08205 | -0.060575 | 0.034501 | 0.004908 | -0.04722 | 0.051766 | 0.12184 | 0.000676 | 0.084141 | 0.020759 | 0.12324 | 0.085575 | -0.030676 | -0.089454 | 0.028838 | -0.036274 | -0.014799 | 0.080277 | 0.050684 | -0.001444 | 0.097542 | -0.16973 | -0.08801 | -0.11655 | -0.03483
2963.7656 | 121.669 | -43.2724 | 78.0029 | 0.080646 | -0.040521 | 0.033786 | -0.020438 | 0.082044 | 0.044377 | -0.08103 | -0.13981 | -0.016938 | -0.08205 | -0.060575 | 0.043657 | 0.009486 | -0.04722 | 0.051766 | 0.12642 | 0.005255 | 0.079562 | 0.025338 | 0.12782 | 0.090153 | -0.035254 | -0.094033 | 0.028838 | -0.036274 | -0.014799 | 0.089433 | 0.055262 | -0.001444 | 0.097542 | -0.18347 | -0.092589 | -0.12571 | -0.03483
2965.4844 | 121.5591 | -43.4143 | 77.9984 | 0.080646 | -0.049678 | 0.033786 | -0.01586 | 0.072888 | 0.044377 | -0.08103 | -0.13981 | -0.021517 | -0.068315 | -0.065154 | 0.039079 | 0.009486 | -0.04722 | 0.038032 | 0.12642 | -0.003902 | 0.079562 | 0.029916 | 0.11866 | 0.090153 | -0.035254 | -0.094033 | 0.024259 | -0.022539 | -0.019378 | 0.084855 | 0.055262 | -0.001444 | 0.083808 | -0.17889 | -0.092589 | -0.10739 | -0.021095
2967.2812 | 121.5363 | -43.3548 | 78.0487 | 0.085224 | -0.040521 | 0.033786 | -0.020438 | 0.072888 | 0.035221 | -0.076452 | -0.14439 | -0.016938 | -0.077472 | -0.065154 | 0.039079 | 0.009486 | -0.042641 | 0.051766 | 0.131 | 0.005255 | 0.079562 | 0.025338 | 0.11866 | 0.080997 | -0.030676 | -0.098611 | 0.028838 | -0.031696 | -0.019378 | 0.084855 | 0.055262 | 0.003135 | 0.097542 | -0.18347 | -0.10175 | -0.11655 | -0.034831
2969.0625 | 121.669 | -43.2861 | 77.98 | 0.089802 | -0.0451 | 0.029208 | -0.020438 | 0.063733 | 0.039799 | -0.08103 | -0.13981 | -0.016938 | -0.08205 | -0.060575 | 0.039079 | 0.009486 | -0.04722 | 0.047188 | 0.13558 | 0.000676 | 0.074984 | 0.025338 | 0.10951 | 0.085575 | -0.035254 | -0.094033 | 0.028838 | -0.036274 | -0.014799 | 0.084855 | 0.055262 | -0.001444 | 0.092964 | -0.17889 | -0.092589 | -0.12113 | -0.03483
2970.8594 | 121.5363 | -43.2632 | 78.1311 | 0.071489 | -0.0451 | 0.029208 | -0.020438 | 0.082044 | 0.044377 | -0.090186 | -0.13523 | -0.016938 | -0.072894 | -0.060575 | 0.025345 | 0.004908 | -0.038063 | 0.056344 | 0.11726 | 0.000676 | 0.074984 | 0.025338 | 0.12782 | 0.090153 | -0.04441 | -0.089454 | 0.028838 | -0.027118 | -0.014799 | 0.071121 | 0.050684 | 0.007713 | 0.10212 | -0.16057 | -0.097167 | -0.098239 | -0.034831
2972.5625 | 121.5363 | -43.309 | 78.1036 | 0.089802 | -0.040521 | 0.029208 | -0.025017 | 0.082044 | 0.044377 | -0.085608 | -0.13981 | -0.016938 | -0.077472 | -0.060575 | 0.034501 | 0.014064 | -0.04722 | 0.047188 | 0.13558 | 0.005255 | 0.074984 | 0.020759 | 0.12782 | 0.090153 | -0.039832 | -0.094033 | 0.028838 | -0.031696 | -0.014799 | 0.080277 | 0.05984 | -0.001444 | 0.092964 | -0.17431 | -0.092589 | -0.11197 | -0.030252
2974.3438 | 121.637 | -43.2175 | 78.1494 | 0.076067 | -0.0451 | 0.033786 | -0.01586 | 0.077466 | 0.039799 | -0.08103 | -0.13523 | -0.016938 | -0.08205 | -0.055996 | 0.039079 | 0.009486 | -0.042641 | 0.047188 | 0.12184 | 0.000676 | 0.079562 | 0.029916 | 0.12324 | 0.085575 | -0.035254 | -0.089454 | 0.028838 | -0.036274 | -0.01022 | 0.084855 | 0.055262 | 0.003135 | 0.092964 | -0.17431 | -0.092589 | -0.12113 | -0.039409
2976.1406 | 121.6736 | -43.1946 | 78.1631 | 0.076067 | -0.049678 | 0.033786 | -0.025017 | 0.077466 | 0.039799 | -0.08103 | -0.13981 | -0.026096 | -0.072894 | -0.060575 | 0.039079 | 0.004908 | -0.042641 | 0.051766 | 0.12184 | -0.003902 | 0.079562 | 0.020759 | 0.12324 | 0.085575 | -0.035254 | -0.094033 | 0.01968 | -0.027118 | -0.014799 | 0.084855 | 0.050684 | 0.003135 | 0.097542 | -0.17889 | -0.097168 | -0.11197 | -0.030253
2977.9219 | 121.5591 | -43.1717 | 78.2639 | 0.085224 | -0.049678 | 0.029208 | -0.025017 | 0.077466 | 0.044377 | -0.08103 | -0.13981 | -0.021517 | -0.077472 | -0.060575 | 0.034501 | 0.00033 | -0.04722 | 0.051766 | 0.131 | -0.003902 | 0.074984 | 0.020759 | 0.12324 | 0.090153 | -0.035254 | -0.094033 | 0.024259 | -0.031696 | -0.014799 | 0.080277 | 0.046106 | -0.001444 | 0.097542 | -0.17431 | -0.092589 | -0.11197 | -0.030252
2979.6875 | 121.5363 | -43.1763 | 78.2501 | 0.080646 | -0.0451 | 0.033786 | -0.020438 | 0.072888 | 0.044377 | -0.076452 | -0.13523 | -0.012359 | -0.072894 | -0.065154 | 0.039079 | 0.00033 | -0.042641 | 0.047188 | 0.12642 | 0.000676 | 0.079562 | 0.025338 | 0.11866 | 0.090153 | -0.030676 | -0.089454 | 0.033417 | -0.027118 | -0.019378 | 0.084855 | 0.046106 | 0.003135 | 0.092964 | -0.17431 | -0.092589 | -0.11197 | -0.030253
2981.4219 | 121.6599 | -43.071 | 78.3279 | 0.089802 | -0.049678 | 0.038365 | -0.025017 | 0.082044 | 0.035221 | -0.076452 | -0.13981 | -0.016938 | -0.072894 | -0.069733 | 0.034501 | 0.004908 | -0.051798 | 0.051766 | 0.13558 | -0.003902 | 0.084141 | 0.020759 | 0.12782 | 0.080997 | -0.030676 | -0.094033 | 0.028838 | -0.027118 | -0.023957 | 0.080277 | 0.050684 | -0.006022 | 0.097542 | -0.17431 | -0.088011 | -0.10739 | -0.021096
2983.2031 | 121.6049 | -43.0252 | 78.3966 | 0.080646 | -0.049678 | 0.033786 | -0.01586 | 0.082044 | 0.048956 | -0.076452 | -0.13523 | -0.016938 | -0.077472 | -0.065154 | 0.039079 | 0.009486 | -0.04722 | 0.04261 | 0.12642 | -0.003902 | 0.079562 | 0.029916 | 0.12782 | 0.094732 | -0.030676 | -0.089454 | 0.028838 | -0.031696 | -0.019378 | 0.084855 | 0.055262 | -0.001444 | 0.088386 | -0.17431 | -0.08801 | -0.11655 | -0.030252
2984.9219 | 121.5546 | -43.1671 | 78.2867 | 0.089802 | -0.0451 | 0.029208 | -0.020438 | 0.072888 | 0.039799 | -0.08103 | -0.13981 | -0.021517 | -0.08205 | -0.060575 | 0.034501 | 0.009486 | -0.042641 | 0.047188 | 0.13558 | 0.000676 | 0.074984 | 0.025338 | 0.11866 | 0.085575 | -0.035254 | -0.094033 | 0.024259 | -0.036274 | -0.014799 | 0.080277 | 0.055262 | 0.003135 | 0.092964 | -0.17431 | -0.097168 | -0.11655 | -0.039409
2986.7188 | 121.7148 | -43.0298 | 78.3325 | 0.085224 | -0.049678 | 0.033786 | -0.020438 | 0.077466 | 0.035221 | -0.085608 | -0.13523 | -0.016938 | -0.077472 | -0.069733 | 0.034501 | 0.004908 | -0.04722 | 0.047188 | 0.131 | -0.003902 | 0.079562 | 0.025338 | 0.12324 | 0.080997 | -0.039832 | -0.089454 | 0.028838 | -0.031696 | -0.023957 | 0.080277 | 0.050684 | -0.001444 | 0.092964 | -0.16973 | -0.08801 | -0.11197 | -0.030252
2988.4219 | 121.6873 | -42.952 | 78.4012 | 0.089802 | -0.049678 | 0.033786 | -0.025017 | 0.072888 | 0.030642 | -0.08103 | -0.13981 | -0.016938 | -0.077472 | -0.060575 | 0.039079 | 0.004908 | -0.04722 | 0.04261 | 0.13558 | -0.003902 | 0.079562 | 0.020759 | 0.11866 | 0.076418 | -0.035254 | -0.094033 | 0.028838 | -0.031696 | -0.014799 | 0.084855 | 0.050684 | -0.001444 | 0.088386 | -0.17889 | -0.092589 | -0.11655 | -0.030252
2990.2031 | 121.6873 | -42.9382 | 78.4058 | 0.080646 | -0.0451 | 0.033786 | -0.020438 | 0.077466 | 0.044377 | -0.076452 | -0.13981 | -0.016938 | -0.072894 | -0.069733 | 0.039079 | 0.009486 | -0.038063 | 0.047188 | 0.12642 | 0.000676 | 0.079562 | 0.025338 | 0.12324 | 0.090153 | -0.030676 | -0.094033 | 0.028838 | -0.027118 | -0.023957 | 0.084855 | 0.055262 | 0.007713 | 0.092964 | -0.17889 | -0.10175 | -0.11197 | -0.034831
2991.9844 | 121.5591 | -42.9153 | 78.511 | 0.080646 | -0.049678 | 0.038365 | -0.029595 | 0.077466 | 0.044377 | -0.076452 | -0.13523 | -0.016938 | -0.077472 | -0.065154 | 0.039079 | -0.004248 | -0.042641 | 0.047188 | 0.12642 | -0.003902 | 0.084141 | 0.016181 | 0.12324 | 0.090153 | -0.030676 | -0.089454 | 0.028838 | -0.031696 | -0.019378 | 0.084855 | 0.041528 | 0.003135 | 0.092964 | -0.17431 | -0.092589 | -0.11655 | -0.034831
2993.7031 | 121.6873 | -42.8925 | 78.4744 | 0.080646 | -0.040521 | 0.033786 | -0.025017 | 0.072888 | 0.044377 | -0.085608 | -0.13981 | -0.016938 | -0.072894 | -0.065154 | 0.034501 | 0.00033 | -0.042641 | 0.047188 | 0.12642 | 0.005255 | 0.079562 | 0.020759 | 0.11866 | 0.090153 | -0.039832 | -0.094033 | 0.028838 | -0.027118 | -0.019378 | 0.080277 | 0.046106 | 0.003135 | 0.092964 | -0.17431 | -0.097168 | -0.10739 | -0.030253
2995.4688 | 121.6507 | -42.8421 | 78.5385 | 0.085224 | -0.049678 | 0.038365 | -0.020438 | 0.072888 | 0.039799 | -0.076452 | -0.12607 | -0.012359 | -0.072894 | -0.074312 | 0.039079 | 0.00033 | -0.04722 | 0.051766 | 0.131 | -0.003902 | 0.084141 | 0.025338 | 0.11866 | 0.085575 | -0.030676 | -0.080297 | 0.033417 | -0.027118 | -0.028536 | 0.084855 | 0.046106 | -0.001444 | 0.097542 | -0.16515 | -0.078853 | -0.11197 | -0.025674
2997.25 | 121.6599 | -42.8284 | 78.5385 | 0.080646 | -0.0451 | 0.024629 | -0.020438 | 0.082044 | 0.039799 | -0.076452 | -0.13523 | -0.021517 | -0.077472 | -0.060575 | 0.039079 | 0.014064 | -0.04722 | 0.051766 | 0.12642 | 0.000676 | 0.070405 | 0.025338 | 0.12782 | 0.085575 | -0.030676 | -0.089454 | 0.024259 | -0.031696 | -0.014799 | 0.084855 | 0.05984 | -0.001444 | 0.097542 | -0.17431 | -0.08801 | -0.11655 | -0.030252
2999.0312 | 121.5912 | -42.9062 | 78.4836 | 0.089802 | -0.049678 | 0.029208 | -0.020438 | 0.072888 | 0.039799 | -0.076452 | -0.13065 | -0.021517 | -0.077472 | -0.060575 | 0.039079 | 0.009486 | -0.04722 | 0.047188 | 0.13558 | -0.003902 | 0.074984 | 0.025338 | 0.11866 | 0.085575 | -0.030676 | -0.084876 | 0.024259 | -0.031696 | -0.014799 | 0.084855 | 0.055262 | -0.001444 | 0.092964 | -0.16973 | -0.083432 | -0.11655 | -0.030252
3000.75 | 121.6919 | -42.9016 | 78.4424 | 0.080646 | -0.0451 | 0.029208 | -0.025017 | 0.077466 | 0.035221 | -0.076452 | -0.13065 | -0.021517 | -0.072894 | -0.069733 | 0.043657 | 0.009486 | -0.04722 | 0.047188 | 0.12642 | 0.000676 | 0.074984 | 0.020759 | 0.12324 | 0.080997 | -0.030676 | -0.084876 | 0.024259 | -0.027118 | -0.023957 | 0.089433 | 0.055262 | -0.001444 | 0.092964 | -0.17431 | -0.083432 | -0.11655 | -0.025674
3002.5312 | 121.5683 | -42.8558 | 78.5934 | 0.085224 | -0.054257 | 0.033786 | -0.025017 | 0.06831 | 0.035221 | -0.076452 | -0.13065 | -0.016938 | -0.077472 | -0.060575 | 0.034501 | 0.004908 | -0.042641 | 0.04261 | 0.131 | -0.008481 | 0.079562 | 0.020759 | 0.11409 | 0.080997 | -0.030676 | -0.084876 | 0.028838 | -0.031696 | -0.014799 | 0.080277 | 0.050684 | 0.003135 | 0.088386 | -0.16515 | -0.088011 | -0.11197 | -0.034831
3004.2656 | 121.7377 | -42.746 | 78.6026 | 0.080646 | -0.049678 | 0.029208 | -0.020438 | 0.072888 | 0.035221 | -0.08103 | -0.13523 | -0.016938 | -0.08205 | -0.060575 | 0.029923 | 0.004908 | -0.042641 | 0.047188 | 0.12642 | -0.003902 | 0.074984 | 0.025338 | 0.11866 | 0.080997 | -0.035254 | -0.089454 | 0.028838 | -0.036274 | -0.014799 | 0.075699 | 0.050684 | 0.003135 | 0.092964 | -0.16515 | -0.092589 | -0.11197 | -0.039409
3006.0469 | 121.5866 | -42.8192 | 78.6346 | 0.080646 | -0.0451 | 0.038365 | -0.025017 | 0.077466 | 0.044377 | -0.076452 | -0.13523 | -0.016938 | -0.077472 | -0.060575 | 0.034501 | 0.009486 | -0.042641 | 0.047188 | 0.12642 | 0.000676 | 0.084141 | 0.020759 | 0.12324 | 0.090153 | -0.030676 | -0.089454 | 0.028838 | -0.031696 | -0.014799 | 0.080277 | 0.055262 | 0.003135 | 0.092964 | -0.16973 | -0.092589 | -0.11197 | -0.034831
3007.7656 | 121.7148 | -42.7414 | 78.5934 | 0.080646 | -0.0451 | 0.029208 | -0.025017 | 0.077466 | 0.035221 | -0.08103 | -0.13981 | -0.012359 | -0.072894 | -0.065154 | 0.039079 | 0.014064 | -0.042641 | 0.047188 | 0.12642 | 0.000676 | 0.074984 | 0.020759 | 0.12324 | 0.080997 | -0.035254 | -0.094033 | 0.033417 | -0.027118 | -0.019378 | 0.084855 | 0.05984 | 0.003135 | 0.092964 | -0.17889 | -0.097168 | -0.11197 | -0.030253
3009.5312 | 121.669 | -42.8467 | 78.5339 | 0.080646 | -0.0451 | 0.024629 | -0.025017 | 0.072888 | 0.039799 | -0.076452 | -0.13523 | -0.016938 | -0.077472 | -0.065154 | 0.039079 | 0.004908 | -0.042641 | 0.047188 | 0.12642 | 0.000676 | 0.070405 | 0.020759 | 0.11866 | 0.085575 | -0.030676 | -0.089454 | 0.028838 | -0.031696 | -0.019378 | 0.084855 | 0.050684 | 0.003135 | 0.092964 | -0.17431 | -0.092589 | -0.11655 | -0.034831
3011.3281 | 121.6003 | -42.9291 | 78.511 | 0.080646 | -0.0451 | 0.029208 | -0.025017 | 0.072888 | 0.039799 | -0.076452 | -0.13065 | -0.021517 | -0.077472 | -0.060575 | 0.034501 | 0.009486 | -0.04722 | 0.047188 | 0.12642 | 0.000676 | 0.074984 | 0.020759 | 0.11866 | 0.085575 | -0.030676 | -0.084876 | 0.024259 | -0.031696 | -0.014799 | 0.080277 | 0.055262 | -0.001444 | 0.092964 | -0.16515 | -0.083432 | -0.11197 | -0.030252
3013.0625 | 121.5866 | -42.5354 | 78.8818 | 0.080646 | -0.0451 | 0.038365 | -0.029595 | 0.077466 | 0.035221 | -0.076452 | -0.13523 | -0.021517 | -0.068315 | -0.065154 | 0.039079 | 0.009486 | -0.042641 | 0.047188 | 0.12642 | 0.000676 | 0.084141 | 0.016181 | 0.12324 | 0.080997 | -0.030676 | -0.089454 | 0.024259 | -0.022539 | -0.019378 | 0.084855 | 0.055262 | 0.003135 | 0.092964 | -0.17431 | -0.092589 | -0.10739 | -0.025674
3014.8438 | 121.5683 | -42.3065 | 79.1245 | 0.080646 | -0.040521 | 0.029208 | -0.025017 | 0.077466 | 0.039799 | -0.085608 | -0.13981 | -0.021517 | -0.077472 | -0.065154 | 0.039079 | 0.004908 | -0.042641 | 0.047188 | 0.12642 | 0.005255 | 0.074984 | 0.020759 | 0.12324 | 0.085575 | -0.039832 | -0.094033 | 0.024259 | -0.031696 | -0.019378 | 0.084855 | 0.050684 | 0.003135 | 0.092964 | -0.17889 | -0.097168 | -0.11655 | -0.034831
3016.625 | 121.6873 | -42.2699 | 79.1336 | 0.080646 | -0.0451 | 0.033786 | -0.034174 | 0.06831 | 0.035221 | -0.076452 | -0.13981 | -0.021517 | -0.072894 | -0.065154 | 0.034501 | 0.009486 | -0.04722 | 0.04261 | 0.12642 | 0.000676 | 0.079562 | 0.011602 | 0.11409 | 0.080997 | -0.030676 | -0.094033 | 0.024259 | -0.027118 | -0.019378 | 0.080277 | 0.055262 | -0.001444 | 0.088386 | -0.17431 | -0.092589 | -0.10739 | -0.025674
3018.3281 | 121.6095 | -42.1921 | 79.2618 | 0.085224 | -0.040521 | 0.033786 | -0.025017 | 0.082044 | 0.035221 | -0.08103 | -0.13981 | -0.016938 | -0.077472 | -0.060575 | 0.039079 | 0.004908 | -0.042641 | 0.051766 | 0.131 | 0.005255 | 0.079562 | 0.020759 | 0.12782 | 0.080997 | -0.035254 | -0.094033 | 0.028838 | -0.031696 | -0.014799 | 0.084855 | 0.050684 | 0.003135 | 0.097542 | -0.17889 | -0.097168 | -0.11655 | -0.034831
3020.0938 | 121.7056 | -42.1371 | 79.2114 | 0.085224 | -0.040521 | 0.033786 | -0.029595 | 0.072888 | 0.035221 | -0.085608 | -0.13981 | -0.021517 | -0.072894 | -0.055996 | 0.039079 | 0.004908 | -0.051798 | 0.051766 | 0.131 | 0.005255 | 0.079562 | 0.016181 | 0.11866 | 0.080997 | -0.039832 | -0.094033 | 0.024259 | -0.027118 | -0.01022 | 0.084855 | 0.050684 | -0.006022 | 0.097542 | -0.17889 | -0.088011 | -0.11197 | -0.021096
3021.875 | 121.5729 | -42.247 | 79.2206 | 0.080646 | -0.0451 | 0.024629 | -0.034174 | 0.082044 | 0.039799 | -0.076452 | -0.13065 | -0.021517 | -0.077472 | -0.060575 | 0.034501 | 0.004908 | -0.04722 | 0.047188 | 0.12642 | 0.000676 | 0.070405 | 0.011602 | 0.12782 | 0.085575 | -0.030676 | -0.084876 | 0.024259 | -0.031696 | -0.014799 | 0.080277 | 0.050684 | -0.001444 | 0.092964 | -0.16515 | -0.083432 | -0.11197 | -0.030252
3023.5781 | 121.5683 | -42.2195 | 79.2435 | 0.080646 | -0.0451 | 0.029208 | -0.020438 | 0.077466 | 0.044377 | -0.071874 | -0.13981 | -0.016938 | -0.077472 | -0.060575 | 0.039079 | 0.009486 | -0.038063 | 0.056344 | 0.12642 | 0.000676 | 0.074984 | 0.025338 | 0.12324 | 0.090153 | -0.026098 | -0.094033 | 0.028838 | -0.031696 | -0.014799 | 0.084855 | 0.055262 | 0.007713 | 0.10212 | -0.17889 | -0.10175 | -0.11655 | -0.039409
3025.3594 | 121.582 | -42.0868 | 79.3716 | 0.076067 | -0.0451 | 0.029208 | -0.029595 | 0.086622 | 0.044377 | -0.076452 | -0.13523 | -0.016938 | -0.077472 | -0.065154 | 0.039079 | 0.009486 | -0.042641 | 0.047188 | 0.12184 | 0.000676 | 0.074984 | 0.016181 | 0.1324 | 0.090153 | -0.030676 | -0.089454 | 0.028838 | -0.031696 | -0.019378 | 0.084855 | 0.055262 | 0.003135 | 0.092964 | -0.17431 | -0.092589 | -0.11655 | -0.034831
3027.1406 | 121.5591 | -42.0273 | 79.4449 | 0.085224 | -0.0451 | 0.033786 | -0.029595 | 0.06831 | 0.044377 | -0.076452 | -0.13523 | -0.026096 | -0.08205 | -0.065154 | 0.039079 | 0.014064 | -0.04722 | 0.047188 | 0.131 | 0.000676 | 0.079562 | 0.016181 | 0.11409 | 0.090153 | -0.030676 | -0.089454 | 0.01968 | -0.036274 | -0.019378 | 0.084855 | 0.05984 | -0.001444 | 0.092964 | -0.17431 | -0.08801 | -0.12113 | -0.03483
3028.9219 | 121.5591 | -41.8488 | 79.5822 | 0.080646 | -0.054257 | 0.029208 | -0.029595 | 0.072888 | 0.048956 | -0.085608 | -0.14439 | -0.021517 | -0.08205 | -0.069733 | 0.039079 | 0.004908 | -0.042641 | 0.051766 | 0.12642 | -0.008481 | 0.074984 | 0.016181 | 0.11866 | 0.094732 | -0.039832 | -0.098611 | 0.024259 | -0.036274 | -0.023957 | 0.084855 | 0.050684 | 0.003135 | 0.097542 | -0.18347 | -0.10175 | -0.12113 | -0.039409
3030.6875 | 121.6278 | -41.9357 | 79.5044 | 0.080646 | -0.040521 | 0.029208 | -0.025017 | 0.077466 | 0.039799 | -0.08103 | -0.13523 | -0.021517 | -0.077472 | -0.069733 | 0.039079 | 0.009486 | -0.042641 | 0.047188 | 0.12642 | 0.005255 | 0.074984 | 0.020759 | 0.12324 | 0.085575 | -0.035254 | -0.089454 | 0.024259 | -0.031696 | -0.023957 | 0.084855 | 0.055262 | 0.003135 | 0.092964 | -0.17431 | -0.092589 | -0.11655 | -0.034831
3032.4062 | 121.5683 | -41.7572 | 79.7241 | 0.080646 | -0.040521 | 0.033786 | -0.025017 | 0.06831 | 0.035221 | -0.076452 | -0.13523 | -0.016938 | -0.077472 | -0.065154 | 0.034501 | 0.004908 | -0.042641 | 0.051766 | 0.12642 | 0.005255 | 0.079562 | 0.020759 | 0.11409 | 0.080997 | -0.030676 | -0.089454 | 0.028838 | -0.031696 | -0.019378 | 0.080277 | 0.050684 | 0.003135 | 0.097542 | -0.16973 | -0.092589 | -0.11197 | -0.034831
3034.2031 | 121.6873 | -40.3931 | 80.983 | 0.080646 | -0.0451 | 0.033786 | -0.034174 | 0.077466 | 0.039799 | -0.076452 | -0.13523 | -0.016938 | -0.072894 | -0.069733 | 0.039079 | 0.004908 | -0.042641 | 0.051766 | 0.12642 | 0.000676 | 0.079562 | 0.011602 | 0.12324 | 0.085575 | -0.030676 | -0.089454 | 0.028838 | -0.027118 | -0.023957 | 0.084855 | 0.050684 | 0.003135 | 0.097542 | -0.17431 | -0.092589 | -0.11197 | -0.030253
3035.9844 | 121.6919 | -39.8026 | 81.5918 | 0.080646 | -0.040521 | 0.033786 | -0.029595 | 0.077466 | 0.035221 | -0.076452 | -0.14439 | -0.012359 | -0.068315 | -0.069733 | 0.043657 | 0.004908 | -0.038063 | 0.056344 | 0.12642 | 0.005255 | 0.079562 | 0.016181 | 0.12324 | 0.080997 | -0.030676 | -0.098611 | 0.033417 | -0.022539 | -0.023957 | 0.089433 | 0.050684 | 0.007713 | 0.10212 | -0.18804 | -0.10632 | -0.11197 | -0.030252
3037.7031 | 121.5637 | -39.8392 | 81.6284 | 0.085224 | -0.0451 | 0.033786 | -0.029595 | 0.077466 | 0.039799 | -0.067295 | -0.13523 | -0.016938 | -0.08205 | -0.065154 | 0.048236 | 0.014064 | -0.042641 | 0.051766 | 0.131 | 0.000676 | 0.079562 | 0.016181 | 0.12324 | 0.085575 | -0.021519 | -0.089454 | 0.028838 | -0.036274 | -0.019378 | 0.094012 | 0.05984 | 0.003135 | 0.097542 | -0.18347 | -0.092589 | -0.13029 | -0.039409
3039.4688 | 121.7102 | -39.1022 | 82.283 | 0.080646 | -0.054257 | 0.038365 | -0.025017 | 0.072888 | 0.044377 | -0.08103 | -0.14439 | -0.016938 | -0.08205 | -0.065154 | 0.034501 | 0.009486 | -0.04722 | 0.047188 | 0.12642 | -0.008481 | 0.084141 | 0.020759 | 0.11866 | 0.090153 | -0.035254 | -0.098611 | 0.028838 | -0.036274 | -0.019378 | 0.080277 | 0.055262 | -0.001444 | 0.092964 | -0.17889 | -0.097167 | -0.11655 | -0.03483
3041.2656 | 121.5683 | -38.8458 | 82.6355 | 0.080646 | -0.040521 | 0.029208 | -0.025017 | 0.077466 | 0.039799 | -0.08103 | -0.13523 | -0.021517 | -0.08205 | -0.065154 | 0.043657 | 0.009486 | -0.051798 | 0.051766 | 0.12642 | 0.005255 | 0.074984 | 0.020759 | 0.12324 | 0.085575 | -0.035254 | -0.089454 | 0.024259 | -0.036274 | -0.019378 | 0.089433 | 0.055262 | -0.006022 | 0.097542 | -0.17889 | -0.083432 | -0.12571 | -0.030252
3042.9844 | 121.6873 | -38.0402 | 83.3496 | 0.076067 | -0.040521 | 0.033786 | -0.034174 | 0.082044 | 0.035221 | -0.071874 | -0.14439 | -0.021517 | -0.08205 | -0.065154 | 0.039079 | 0.014064 | -0.038063 | 0.051766 | 0.12184 | 0.005255 | 0.079562 | 0.011602 | 0.12782 | 0.080997 | -0.026098 | -0.098611 | 0.024259 | -0.036274 | -0.019378 | 0.084855 | 0.05984 | 0.007713 | 0.097542 | -0.18347 | -0.10632 | -0.12113 | -0.043987
3044.6875 | 121.6827 | -37.1658 | 84.1919 | 0.076067 | -0.040521 | 0.029208 | -0.034174 | 0.06831 | 0.030642 | -0.08103 | -0.13065 | -0.021517 | -0.08205 | -0.065154 | 0.048236 | 0.009486 | -0.04722 | 0.056344 | 0.12184 | 0.005255 | 0.074984 | 0.011602 | 0.11409 | 0.076418 | -0.035254 | -0.084876 | 0.024259 | -0.036274 | -0.019378 | 0.094012 | 0.055262 | -0.001444 | 0.10212 | -0.17889 | -0.083432 | -0.13029 | -0.03483
3046.4688 | 121.6553 | -36.7996 | 84.5856 | 0.071489 | -0.035942 | 0.020051 | -0.034174 | 0.06831 | 0.035221 | -0.08103 | -0.14439 | -0.026096 | -0.072894 | -0.055996 | 0.039079 | 0.009486 | -0.04722 | 0.060923 | 0.11726 | 0.009834 | 0.065827 | 0.011602 | 0.11409 | 0.080997 | -0.035254 | -0.098611 | 0.01968 | -0.027118 | -0.01022 | 0.084855 | 0.055262 | -0.001444 | 0.1067 | -0.18347 | -0.097167 | -0.11197 | -0.025674
3048.25 | 121.5958 | -35.8154 | 85.6567 | 0.071489 | -0.035942 | 0.024629 | -0.038752 | 0.072888 | 0.039799 | -0.08103 | -0.13981 | -0.030674 | -0.077472 | -0.069733 | 0.048236 | 0.014064 | -0.042641 | 0.047188 | 0.11726 | 0.009834 | 0.070405 | 0.007024 | 0.11866 | 0.085575 | -0.035254 | -0.094033 | 0.015102 | -0.031696 | -0.023957 | 0.094012 | 0.05984 | 0.003135 | 0.092964 | -0.18804 | -0.097168 | -0.12571 | -0.034831
3049.9688 | 121.637 | -35.8429 | 85.524 | 0.076067 | -0.040521 | 0.033786 | -0.034174 | 0.072888 | 0.035221 | -0.08103 | -0.13523 | -0.021517 | -0.077472 | -0.065154 | 0.039079 | 0.018642 | -0.042641 | 0.051766 | 0.12184 | 0.005255 | 0.079562 | 0.011602 | 0.11866 | 0.080997 | -0.035254 | -0.089454 | 0.024259 | -0.031696 | -0.019378 | 0.084855 | 0.064418 | 0.003135 | 0.097542 | -0.17431 | -0.092589 | -0.11655 | -0.034831
3051.75 | 121.5637 | -35.4721 | 85.9726 | 0.076067 | -0.040521 | 0.024629 | -0.034174 | 0.072888 | 0.026064 | -0.076452 | -0.13523 | -0.026096 | -0.072894 | -0.065154 | 0.043657 | 0.009486 | -0.04722 | 0.051766 | 0.12184 | 0.005255 | 0.070405 | 0.011602 | 0.11866 | 0.07184 | -0.030676 | -0.089454 | 0.01968 | -0.027118 | -0.019378 | 0.089433 | 0.055262 | -0.001444 | 0.097542 | -0.17889 | -0.08801 | -0.11655 | -0.025674
3053.5 | 121.637 | -34.9823 | 86.3892 | 0.076067 | -0.040521 | 0.033786 | -0.034174 | 0.072888 | 0.035221 | -0.08103 | -0.13981 | -0.026096 | -0.08205 | -0.069733 | 0.043657 | 0.018642 | -0.04722 | 0.051766 | 0.12184 | 0.005255 | 0.079562 | 0.011602 | 0.11866 | 0.080997 | -0.035254 | -0.094033 | 0.01968 | -0.036274 | -0.023957 | 0.089433 | 0.064418 | -0.001444 | 0.097542 | -0.18347 | -0.092589 | -0.12571 | -0.03483
3055.2969 | 121.6782 | -34.5428 | 86.8469 | 0.080646 | -0.040521 | 0.024629 | -0.043331 | 0.06831 | 0.026064 | -0.076452 | -0.13981 | -0.012359 | -0.08205 | -0.060575 | 0.048236 | 0.009486 | -0.04722 | 0.060923 | 0.12642 | 0.005255 | 0.070405 | 0.002445 | 0.11409 | 0.07184 | -0.030676 | -0.094033 | 0.033417 | -0.036274 | -0.014799 | 0.094012 | 0.055262 | -0.001444 | 0.1067 | -0.18804 | -0.092589 | -0.13029 | -0.03483
3057.0781 | 121.5591 | -34.5062 | 86.9568 | 0.06691 | -0.040521 | 0.024629 | -0.029595 | 0.072888 | 0.035221 | -0.090186 | -0.14439 | -0.021517 | -0.08205 | -0.069733 | 0.048236 | 0.014064 | -0.042641 | 0.047188 | 0.11269 | 0.005255 | 0.070405 | 0.016181 | 0.11866 | 0.080997 | -0.04441 | -0.098611 | 0.024259 | -0.036274 | -0.023957 | 0.094012 | 0.05984 | 0.003135 | 0.092964 | -0.19262 | -0.10175 | -0.13029 | -0.039409
3058.8594 | 121.5683 | -34.3735 | 87.0895 | 0.080646 | -0.0451 | 0.029208 | -0.025017 | 0.06831 | 0.035221 | -0.085608 | -0.14439 | -0.026096 | -0.08205 | -0.069733 | 0.043657 | 0.009486 | -0.042641 | 0.047188 | 0.12642 | 0.000676 | 0.074984 | 0.020759 | 0.11409 | 0.080997 | -0.039832 | -0.098611 | 0.01968 | -0.036274 | -0.023957 | 0.089433 | 0.055262 | 0.003135 | 0.092964 | -0.18804 | -0.10175 | -0.12571 | -0.039409
3060.5625 | 121.5683 | -34.4604 | 86.9934 | 0.076067 | -0.040521 | 0.024629 | -0.034174 | 0.077466 | 0.030642 | -0.076452 | -0.13523 | -0.030674 | -0.08205 | -0.069733 | 0.039079 | 0.018642 | -0.04722 | 0.060923 | 0.12184 | 0.005255 | 0.070405 | 0.011602 | 0.12324 | 0.076418 | -0.030676 | -0.089454 | 0.015102 | -0.036274 | -0.023957 | 0.084855 | 0.064418 | -0.001444 | 0.1067 | -0.17431 | -0.08801 | -0.12113 | -0.03483
3062.3438 | 121.6736 | -33.7784 | 87.5839 | 0.076067 | -0.035942 | 0.020051 | -0.038752 | 0.063733 | 0.035221 | -0.085608 | -0.13523 | -0.026096 | -0.072894 | -0.065154 | 0.043657 | 0.009486 | -0.04722 | 0.056344 | 0.12184 | 0.009834 | 0.065827 | 0.007024 | 0.10951 | 0.080997 | -0.039832 | -0.089454 | 0.01968 | -0.027118 | -0.019378 | 0.089433 | 0.055262 | -0.001444 | 0.10212 | -0.17889 | -0.08801 | -0.11655 | -0.025674
3064.125 | 121.669 | -33.2611 | 88.0829 | 0.076067 | -0.040521 | 0.029208 | -0.034174 | 0.072888 | 0.035221 | -0.08103 | -0.13981 | -0.026096 | -0.086628 | -0.069733 | 0.043657 | 0.009486 | -0.04722 | 0.056344 | 0.12184 | 0.005255 | 0.074984 | 0.011602 | 0.11866 | 0.080997 | -0.035254 | -0.094033 | 0.01968 | -0.040852 | -0.023957 | 0.089433 | 0.055262 | -0.001444 | 0.10212 | -0.18347 | -0.092589 | -0.13028 | -0.039408
3065.9062 | 121.5866 | -32.2632 | 89.1403 | 0.080646 | -0.040521 | 0.029208 | -0.029595 | 0.072888 | 0.035221 | -0.085608 | -0.14439 | -0.030674 | -0.072894 | -0.074312 | 0.048236 | 0.014064 | -0.038063 | 0.056344 | 0.12642 | 0.005255 | 0.074984 | 0.016181 | 0.11866 | 0.080997 | -0.039832 | -0.098611 | 0.015102 | -0.027118 | -0.028536 | 0.094012 | 0.05984 | 0.007713 | 0.10212 | -0.19262 | -0.10632 | -0.12113 | -0.034831
3067.6719 | 121.5454 | -31.5399 | 89.9094 | 0.076067 | -0.049678 | 0.024629 | -0.034174 | 0.06831 | 0.030642 | -0.08103 | -0.13981 | -0.026096 | -0.086628 | -0.074312 | 0.039079 | 0.004908 | -0.04722 | 0.056344 | 0.12184 | -0.003902 | 0.070405 | 0.011602 | 0.11409 | 0.076418 | -0.035254 | -0.094033 | 0.01968 | -0.040852 | -0.028536 | 0.084855 | 0.050684 | -0.001444 | 0.10212 | -0.17889 | -0.092589 | -0.12571 | -0.039408
3069.3906 | 121.6507 | -30.9769 | 90.3854 | 0.071489 | -0.0451 | 0.020051 | -0.038752 | 0.072888 | 0.039799 | -0.085608 | -0.14897 | -0.030674 | -0.08205 | -0.069733 | 0.052814 | 0.009486 | -0.042641 | 0.056344 | 0.11726 | 0.000676 | 0.065827 | 0.007024 | 0.11866 | 0.085575 | -0.039832 | -0.10319 | 0.015102 | -0.036274 | -0.023957 | 0.09859 | 0.055262 | 0.003135 | 0.10212 | -0.20178 | -0.10632 | -0.13486 | -0.039409
3071.1875 | 121.5225 | -30.5969 | 90.8478 | 0.071489 | -0.049678 | 0.029208 | -0.034174 | 0.072888 | 0.035221 | -0.090186 | -0.13981 | -0.026096 | -0.08205 | -0.069733 | 0.043657 | 0.014064 | -0.042641 | 0.051766 | 0.11726 | -0.003902 | 0.074984 | 0.011602 | 0.11866 | 0.080997 | -0.04441 | -0.094033 | 0.01968 | -0.036274 | -0.023957 | 0.089433 | 0.05984 | 0.003135 | 0.097542 | -0.18347 | -0.097168 | -0.12571 | -0.039409
3072.9219 | 121.6553 | -30.2216 | 91.1179 | 0.076067 | -0.049678 | 0.024629 | -0.043331 | 0.06831 | 0.035221 | -0.08103 | -0.13981 | -0.030674 | -0.086628 | -0.065154 | 0.048236 | 0.014064 | -0.051798 | 0.060923 | 0.12184 | -0.003902 | 0.070405 | 0.002445 | 0.11409 | 0.080997 | -0.035254 | -0.094033 | 0.015102 | -0.040852 | -0.019378 | 0.094012 | 0.05984 | -0.006022 | 0.1067 | -0.18804 | -0.088011 | -0.13486 | -0.03483
3074.6875 | 121.5317 | -30.1987 | 91.2781 | 0.071489 | -0.031363 | 0.029208 | -0.034174 | 0.06831 | 0.039799 | -0.085608 | -0.13981 | -0.016938 | -0.086628 | -0.065154 | 0.043657 | 0.014064 | -0.04722 | 0.047188 | 0.11726 | 0.014413 | 0.074984 | 0.011602 | 0.11409 | 0.085575 | -0.039832 | -0.094033 | 0.028838 | -0.040852 | -0.019378 | 0.089433 | 0.05984 | -0.001444 | 0.092964 | -0.18347 | -0.092589 | -0.13028 | -0.039408
3076.4219 | 121.5179 | -30.1437 | 91.2964 | 0.076067 | -0.040521 | 0.033786 | -0.038752 | 0.077466 | 0.026064 | -0.085608 | -0.13981 | -0.021517 | -0.086628 | -0.069733 | 0.039079 | 0.014064 | -0.04722 | 0.047188 | 0.12184 | 0.005255 | 0.079562 | 0.007024 | 0.12324 | 0.07184 | -0.039832 | -0.094033 | 0.024259 | -0.040852 | -0.023957 | 0.084855 | 0.05984 | -0.001444 | 0.092964 | -0.17889 | -0.092589 | -0.12571 | -0.039408
3078.2188 | 121.5271 | -29.2877 | 92.1524 | 0.076067 | -0.040521 | 0.033786 | -0.029595 | 0.06831 | 0.030642 | -0.08103 | -0.14439 | -0.026096 | -0.086628 | -0.069733 | 0.048236 | 0.018642 | -0.042641 | 0.051766 | 0.12184 | 0.005255 | 0.079562 | 0.016181 | 0.11409 | 0.076418 | -0.035254 | -0.098611 | 0.01968 | -0.040852 | -0.023957 | 0.094012 | 0.064418 | 0.003135 | 0.097542 | -0.19262 | -0.10175 | -0.13486 | -0.043987
3080 | 121.6187 | -28.8437 | 92.5095 | 0.076067 | -0.0451 | 0.024629 | -0.043331 | 0.06831 | 0.030642 | -0.085608 | -0.14897 | -0.030674 | -0.077472 | -0.069733 | 0.048236 | 0.009486 | -0.042641 | 0.056344 | 0.12184 | 0.000676 | 0.070405 | 0.002445 | 0.11409 | 0.076418 | -0.039832 | -0.10319 | 0.015102 | -0.031696 | -0.023957 | 0.094012 | 0.055262 | 0.003135 | 0.10212 | -0.1972 | -0.10632 | -0.12571 | -0.034831
3081.7812 | 121.5546 | -27.4612 | 93.956 | 0.071489 | -0.049678 | 0.024629 | -0.034174 | 0.06831 | 0.026064 | -0.08103 | -0.13981 | -0.026096 | -0.08205 | -0.069733 | 0.057392 | 0.02322 | -0.042641 | 0.051766 | 0.11726 | -0.003902 | 0.070405 | 0.011602 | 0.11409 | 0.07184 | -0.035254 | -0.094033 | 0.01968 | -0.036274 | -0.023957 | 0.10317 | 0.068996 | 0.003135 | 0.097542 | -0.1972 | -0.097168 | -0.13944 | -0.039409
3083.4844 | 121.6415 | -27.0538 | 94.3588 | 0.076067 | -0.049678 | 0.024629 | -0.038752 | 0.06831 | 0.030642 | -0.08103 | -0.13981 | -0.030674 | -0.086628 | -0.065154 | 0.048236 | 0.014064 | -0.038063 | 0.056344 | 0.12184 | -0.003902 | 0.070405 | 0.007024 | 0.11409 | 0.076418 | -0.035254 | -0.094033 | 0.015102 | -0.040852 | -0.019378 | 0.094012 | 0.05984 | 0.007713 | 0.10212 | -0.18804 | -0.10175 | -0.13486 | -0.048565
3085.2656 | 121.5179 | -26.6556 | 94.812 | 0.076067 | -0.049678 | 0.020051 | -0.047909 | 0.06831 | 0.026064 | -0.085608 | -0.14439 | -0.021517 | -0.08205 | -0.069733 | 0.043657 | 0.014064 | -0.04722 | 0.056344 | 0.12184 | -0.003902 | 0.065827 | -0.002133 | 0.11409 | 0.07184 | -0.039832 | -0.098611 | 0.024259 | -0.036274 | -0.023957 | 0.089433 | 0.05984 | -0.001444 | 0.10212 | -0.18804 | -0.097167 | -0.12571 | -0.03483
3087.0469 | 121.6141 | -26.5686 | 94.7891 | 0.062332 | -0.058836 | 0.020051 | -0.043331 | 0.06831 | 0.021485 | -0.085608 | -0.13981 | -0.030674 | -0.08205 | -0.065154 | 0.043657 | 0.018642 | -0.042641 | 0.051766 | 0.10811 | -0.01306 | 0.065827 | 0.002445 | 0.11409 | 0.067261 | -0.039832 | -0.094033 | 0.015102 | -0.036274 | -0.019378 | 0.089433 | 0.064418 | 0.003135 | 0.097542 | -0.18347 | -0.097168 | -0.12571 | -0.039409
3088.8281 | 121.6415 | -26.8982 | 94.455 | 0.071489 | -0.049678 | 0.024629 | -0.043331 | 0.06831 | 0.030642 | -0.090186 | -0.14897 | -0.026096 | -0.086628 | -0.069733 | 0.043657 | 0.02322 | -0.038063 | 0.060923 | 0.11726 | -0.003902 | 0.070405 | 0.002445 | 0.11409 | 0.076418 | -0.04441 | -0.10319 | 0.01968 | -0.040852 | -0.023957 | 0.089433 | 0.068996 | 0.007713 | 0.1067 | -0.19262 | -0.1109 | -0.13028 | -0.048565
3090.5312 | 121.5408 | -26.6052 | 94.812 | 0.076067 | -0.0451 | 0.024629 | -0.043331 | 0.06831 | 0.026064 | -0.08103 | -0.14439 | -0.026096 | -0.077472 | -0.069733 | 0.048236 | 0.02322 | -0.04722 | 0.051766 | 0.12184 | 0.000676 | 0.070405 | 0.002445 | 0.11409 | 0.07184 | -0.035254 | -0.098611 | 0.01968 | -0.031696 | -0.023957 | 0.094012 | 0.068996 | -0.001444 | 0.097542 | -0.19262 | -0.097167 | -0.12571 | -0.030252
3092.3281 | 121.463 | -47.3465 | 73.8007 | 0.085224 | -0.0451 | 0.033786 | -0.034174 | 0.077466 | 0.039799 | -0.08103 | -0.13065 | -0.016938 | -0.063737 | -0.065154 | 0.034501 | 0.00033 | -0.04722 | 0.033454 | 0.131 | 0.000676 | 0.079562 | 0.011602 | 0.12324 | 0.085575 | -0.035254 | -0.084876 | 0.028838 | -0.017961 | -0.019378 | 0.080277 | 0.046106 | -0.001444 | 0.07923 | -0.16515 | -0.083432 | -0.098238 | -0.016517
3094.0938 | 121.257 | -45.7809 | 75.3204 | 0.089802 | -0.0451 | 0.033786 | -0.029595 | 0.072888 | 0.039799 | -0.076452 | -0.12607 | -0.016938 | -0.072894 | -0.065154 | 0.034501 | 0.009486 | -0.04722 | 0.047188 | 0.13558 | 0.000676 | 0.079562 | 0.016181 | 0.11866 | 0.085575 | -0.030676 | -0.080297 | 0.028838 | -0.027118 | -0.019378 | 0.080277 | 0.055262 | -0.001444 | 0.092964 | -0.16057 | -0.078853 | -0.10739 | -0.025674
3095.7969 | 121.1609 | -49.7726 | 71.2509 | 0.094381 | -0.031363 | 0.033786 | -0.034174 | 0.072888 | 0.039799 | -0.071874 | -0.13981 | -0.016938 | -0.072894 | -0.065154 | 0.039079 | 0.004908 | -0.051798 | 0.038032 | 0.14016 | 0.014413 | 0.079562 | 0.011602 | 0.11866 | 0.085575 | -0.026098 | -0.094033 | 0.028838 | -0.027118 | -0.019378 | 0.084855 | 0.050684 | -0.006022 | 0.083808 | -0.17889 | -0.088011 | -0.11197 | -0.021096
3097.5781 | 121.2524 | -29.9789 | 91.9693 | 0.080646 | -0.0451 | 0.020051 | -0.034174 | 0.072888 | 0.030642 | -0.085608 | -0.13981 | -0.016938 | -0.077472 | -0.069733 | 0.039079 | 0.009486 | -0.051798 | 0.047188 | 0.12642 | 0.000676 | 0.065827 | 0.011602 | 0.11866 | 0.076418 | -0.039832 | -0.094033 | 0.028838 | -0.031696 | -0.023957 | 0.084855 | 0.055262 | -0.006022 | 0.092964 | -0.17889 | -0.088011 | -0.11655 | -0.025674
3099.3438 | 121.0693 | -53.7186 | 67.1951 | 0.089802 | -0.035942 | 0.033786 | -0.025017 | 0.082044 | 0.048956 | -0.08103 | -0.13065 | -0.012359 | -0.063737 | -0.055996 | 0.025345 | -0.004248 | -0.051798 | 0.047188 | 0.13558 | 0.009834 | 0.079562 | 0.020759 | 0.12782 | 0.094732 | -0.035254 | -0.084876 | 0.033417 | -0.017961 | -0.01022 | 0.071121 | 0.041528 | -0.006022 | 0.092964 | -0.156 | -0.078854 | -0.089082 | -0.011939
3101.0625 | 120.6299 | -79.6783 | 40.5991 | 0.098959 | -0.017627 | 0.061258 | -0.01586 | 0.10036 | 0.062691 | -0.058139 | -0.11234 | 0.005956 | -0.05458 | -0.046838 | 0.016188 | -0.022561 | -0.051798 | 0.019719 | 0.14474 | 0.028149 | 0.10703 | 0.029916 | 0.14613 | 0.10847 | -0.012363 | -0.066562 | 0.051732 | -0.008804 | -0.001062 | 0.061964 | 0.023215 | -0.006022 | 0.065495 | -0.12853 | -0.06054 | -0.070768 | -0.002782
3102.8594 | 120.2774 | -73.2651 | 46.8338 | 0.10812 | -0.017627 | 0.052101 | -0.01586 | 0.10036 | 0.067269 | -0.062717 | -0.10776 | 0.001377 | -0.05458 | -0.03768 | 0.016188 | -0.008827 | -0.051798 | 0.033454 | 0.15389 | 0.028149 | 0.097877 | 0.029916 | 0.14613 | 0.11304 | -0.016941 | -0.061983 | 0.047153 | -0.008804 | 0.008096 | 0.061964 | 0.036949 | -0.006022 | 0.07923 | -0.12395 | -0.055961 | -0.070768 | -0.002782
3104.5781 | 120.0531 | -63.0341 | 57.2159 | 0.098959 | -0.026784 | 0.047522 | -0.020438 | 0.0912 | 0.048956 | -0.062717 | -0.12607 | -0.00778 | -0.059159 | -0.060575 | 0.020767 | -0.008827 | -0.04722 | 0.033454 | 0.14474 | 0.018992 | 0.093298 | 0.025338 | 0.13698 | 0.094732 | -0.016941 | -0.080297 | 0.037996 | -0.013383 | -0.014799 | 0.066543 | 0.036949 | -0.001444 | 0.07923 | -0.14684 | -0.078853 | -0.079926 | -0.011939
3106.375 | 119.1513 | -59.7702 | 59.3033 | 0.098959 | -0.035942 | 0.047522 | -0.01586 | 0.0912 | 0.058113 | -0.062717 | -0.1215 | -0.00778 | -0.059159 | -0.051417 | 0.025345 | -0.004248 | -0.051798 | 0.033454 | 0.14474 | 0.009834 | 0.093298 | 0.029916 | 0.13698 | 0.10389 | -0.016941 | -0.075719 | 0.037996 | -0.013383 | -0.005641 | 0.071121 | 0.041528 | -0.006022 | 0.07923 | -0.14684 | -0.069697 | -0.084504 | -0.007361
3108.0938 | 118.9041 | -68.7195 | 49.8825 | 0.098959 | -0.031363 | 0.047522 | -0.01586 | 0.0912 | 0.048956 | -0.062717 | -0.11692 | -0.003202 | -0.050002 | -0.042259 | 0.025345 | -0.008827 | -0.056376 | 0.033454 | 0.14474 | 0.014413 | 0.093298 | 0.029916 | 0.13698 | 0.094732 | -0.016941 | -0.07114 | 0.042574 | -0.004226 | 0.003517 | 0.071121 | 0.036949 | -0.0106 | 0.07923 | -0.14226 | -0.06054 | -0.075347 | 0.006374
3109.875 | 119.0094 | -61.9583 | 56.7947 | 0.089802 | -0.035942 | 0.042944 | -0.01586 | 0.086622 | 0.058113 | -0.067295 | -0.12607 | -0.003202 | -0.059159 | -0.051417 | 0.020767 | -0.008827 | -0.04722 | 0.033454 | 0.13558 | 0.009834 | 0.08872 | 0.029916 | 0.1324 | 0.10389 | -0.021519 | -0.080297 | 0.042574 | -0.013383 | -0.005641 | 0.066543 | 0.036949 | -0.001444 | 0.07923 | -0.14684 | -0.078853 | -0.079926 | -0.011939
3111.5938 | 117.8879 | -48.4863 | 69.5206 | 0.089802 | -0.035942 | 0.042944 | -0.034174 | 0.077466 | 0.053534 | -0.071874 | -0.1215 | -0.016938 | -0.063737 | -0.051417 | 0.029923 | 0.00033 | -0.042641 | 0.038032 | 0.13558 | 0.009834 | 0.08872 | 0.011602 | 0.12324 | 0.09931 | -0.026098 | -0.075719 | 0.028838 | -0.017961 | -0.005641 | 0.075699 | 0.046106 | 0.003135 | 0.083808 | -0.15142 | -0.078854 | -0.09366 | -0.021096
3113.3906 | 118.4143 | -42.4713 | 75.7462 | 0.085224 | -0.0451 | 0.038365 | -0.029595 | 0.072888 | 0.048956 | -0.08103 | -0.13065 | -0.012359 | -0.068315 | -0.065154 | 0.039079 | 0.009486 | -0.051798 | 0.04261 | 0.131 | 0.000676 | 0.084141 | 0.016181 | 0.11866 | 0.094732 | -0.035254 | -0.084876 | 0.033417 | -0.022539 | -0.019378 | 0.084855 | 0.055262 | -0.006022 | 0.088386 | -0.16973 | -0.078854 | -0.10739 | -0.016517
3115.1094 | 117.4072 | -60.9375 | 56.0303 | 0.098959 | -0.040521 | 0.033786 | -0.020438 | 0.086622 | 0.039799 | -0.062717 | -0.12607 | -0.003202 | -0.059159 | -0.046838 | 0.029923 | 0.004908 | -0.04722 | 0.028875 | 0.14474 | 0.005255 | 0.079562 | 0.025338 | 0.1324 | 0.085575 | -0.016941 | -0.080297 | 0.042574 | -0.013383 | -0.001062 | 0.075699 | 0.050684 | -0.001444 | 0.074651 | -0.156 | -0.078853 | -0.089082 | -0.011939
3116.8906 | 116.9952 | -60.6125 | 56.0852 | 0.094381 | -0.035942 | 0.042944 | -0.020438 | 0.086622 | 0.053534 | -0.071874 | -0.1215 | -0.00778 | -0.063737 | -0.042259 | 0.025345 | -0.004248 | -0.056376 | 0.033454 | 0.14016 | 0.009834 | 0.08872 | 0.025338 | 0.1324 | 0.09931 | -0.026098 | -0.075719 | 0.037996 | -0.017961 | 0.003517 | 0.071121 | 0.041528 | -0.0106 | 0.07923 | -0.14684 | -0.065119 | -0.089082 | -0.007361
3118.5938 | 118.6569 | -67.9047 | 50.2029 | 0.094381 | -0.026784 | 0.042944 | -0.01586 | 0.0912 | 0.053534 | -0.071874 | -0.11234 | -0.003202 | -0.05458 | -0.046838 | 0.016188 | -0.004248 | -0.051798 | 0.038032 | 0.14016 | 0.018992 | 0.08872 | 0.029916 | 0.13698 | 0.09931 | -0.026098 | -0.066562 | 0.042574 | -0.008804 | -0.001062 | 0.061964 | 0.041528 | -0.006022 | 0.083808 | -0.12853 | -0.06054 | -0.070768 | -0.002782
3120.375 | 117.778 | -64.7186 | 52.8122 | 0.10812 | -0.026784 | 0.052101 | -0.020438 | 0.0912 | 0.058113 | -0.062717 | -0.11234 | 0.001377 | -0.05458 | -0.051417 | 0.025345 | -0.013405 | -0.051798 | 0.024297 | 0.15389 | 0.018992 | 0.097877 | 0.025338 | 0.13698 | 0.10389 | -0.016941 | -0.066562 | 0.047153 | -0.008804 | -0.005641 | 0.071121 | 0.032371 | -0.006022 | 0.070073 | -0.13768 | -0.06054 | -0.079925 | -0.002782
3122.1562 | 117.4255 | -41.5421 | 75.3296 | 0.089802 | -0.035942 | 0.029208 | -0.029595 | 0.077466 | 0.044377 | -0.076452 | -0.13065 | -0.012359 | -0.068315 | -0.065154 | 0.039079 | 0.00033 | -0.051798 | 0.038032 | 0.13558 | 0.009834 | 0.074984 | 0.016181 | 0.12324 | 0.090153 | -0.030676 | -0.084876 | 0.033417 | -0.022539 | -0.019378 | 0.084855 | 0.046106 | -0.006022 | 0.083808 | -0.16973 | -0.078854 | -0.10739 | -0.016517
3123.875 | 118.158 | -4.9072 | 113.3835 | 0.071489 | -0.054257 | 0.020051 | -0.038752 | 0.063733 | 0.035221 | -0.094765 | -0.13523 | -0.026096 | -0.072894 | -0.060575 | 0.048236 | 0.014064 | -0.051798 | 0.051766 | 0.11726 | -0.008481 | 0.065827 | 0.007024 | 0.10951 | 0.080997 | -0.048989 | -0.089454 | 0.01968 | -0.027118 | -0.014799 | 0.094012 | 0.05984 | -0.006022 | 0.097542 | -0.18347 | -0.083432 | -0.12113 | -0.021096
3125.6406 | 118.634 | -9.3704 | 109.2453 | 0.06691 | -0.054257 | 0.020051 | -0.052488 | 0.054577 | 0.021485 | -0.090186 | -0.14439 | -0.035253 | -0.091207 | -0.08347 | 0.052814 | 0.018642 | -0.038063 | 0.065501 | 0.11269 | -0.008481 | 0.065827 | -0.006712 | 0.10035 | 0.067261 | -0.04441 | -0.098611 | 0.010523 | -0.045431 | -0.037694 | 0.09859 | 0.064418 | 0.007713 | 0.11128 | -0.1972 | -0.10632 | -0.14402 | -0.053144
3127.3438 | 117.3706 | -24.0189 | 93.1183 | 0.071489 | -0.040521 | 0.029208 | -0.034174 | 0.059155 | 0.035221 | -0.085608 | -0.13523 | -0.021517 | -0.08205 | -0.069733 | 0.043657 | 0.014064 | -0.04722 | 0.051766 | 0.11726 | 0.005255 | 0.074984 | 0.011602 | 0.10493 | 0.080997 | -0.039832 | -0.089454 | 0.024259 | -0.036274 | -0.023957 | 0.089433 | 0.05984 | -0.001444 | 0.097542 | -0.17889 | -0.08801 | -0.12571 | -0.03483
3129.1406 | 117.7185 | -20.8511 | 97.1924 | 0.076067 | -0.0451 | 0.020051 | -0.038752 | 0.072888 | 0.030642 | -0.085608 | -0.13523 | -0.030674 | -0.077472 | -0.078891 | 0.048236 | 0.018642 | -0.038063 | 0.060923 | 0.12184 | 0.000676 | 0.065827 | 0.007024 | 0.11866 | 0.076418 | -0.039832 | -0.089454 | 0.015102 | -0.031696 | -0.033115 | 0.094012 | 0.064418 | 0.007713 | 0.1067 | -0.18347 | -0.097167 | -0.12571 | -0.039409
3130.9375 | 117.6361 | -12.973 | 104.3976 | 0.076067 | -0.040521 | 0.015472 | -0.043331 | 0.059155 | 0.030642 | -0.090186 | -0.13981 | -0.030674 | -0.08205 | -0.074312 | 0.048236 | 0.014064 | -0.038063 | 0.056344 | 0.12184 | 0.005255 | 0.061248 | 0.002445 | 0.10493 | 0.076418 | -0.04441 | -0.094033 | 0.015102 | -0.036274 | -0.028536 | 0.094012 | 0.05984 | 0.007713 | 0.10212 | -0.18804 | -0.10175 | -0.13029 | -0.043987
3132.6562 | 116.7389 | -21.9818 | 94.4778 | 0.076067 | -0.0451 | 0.024629 | -0.043331 | 0.072888 | 0.035221 | -0.085608 | -0.13981 | -0.021517 | -0.08205 | -0.074312 | 0.043657 | 0.014064 | -0.04722 | 0.056344 | 0.12184 | 0.000676 | 0.070405 | 0.002445 | 0.11866 | 0.080997 | -0.039832 | -0.094033 | 0.024259 | -0.036274 | -0.028536 | 0.089433 | 0.05984 | -0.001444 | 0.10212 | -0.18347 | -0.092589 | -0.12571 | -0.03483
3134.4219 | 118.4326 | -6.4316 | 111.9965 | 0.062332 | -0.067994 | 0.010893 | -0.052488 | 0.063733 | 0.021485 | -0.099343 | -0.14897 | -0.035253 | -0.091207 | -0.08347 | 0.06197 | 0.02322 | -0.042641 | 0.065501 | 0.10811 | -0.022218 | 0.056669 | -0.006712 | 0.10951 | 0.067261 | -0.053567 | -0.10319 | 0.010523 | -0.045431 | -0.037694 | 0.10775 | 0.068996 | 0.003135 | 0.11128 | -0.21094 | -0.10632 | -0.15318 | -0.048566
3136.2031 | 117.6636 | -13.3026 | 103.894 | 0.062332 | -0.063415 | 0.015472 | -0.047909 | 0.063733 | 0.026064 | -0.085608 | -0.14439 | -0.030674 | -0.091207 | -0.078891 | 0.052814 | 0.032376 | -0.04722 | 0.065501 | 0.10811 | -0.017639 | 0.061248 | -0.002133 | 0.10951 | 0.07184 | -0.039832 | -0.098611 | 0.015102 | -0.045431 | -0.033115 | 0.09859 | 0.078152 | -0.001444 | 0.11128 | -0.1972 | -0.097167 | -0.14402 | -0.043987
3137.9844 | 118.5974 | -5.5252 | 112.8983 | 0.06691 | -0.063415 | 0.010893 | -0.047909 | 0.054577 | 0.021485 | -0.090186 | -0.15354 | -0.039832 | -0.095785 | -0.08347 | 0.06197 | 0.027798 | -0.04722 | 0.060923 | 0.11269 | -0.017639 | 0.056669 | -0.002133 | 0.10035 | 0.067261 | -0.04441 | -0.10777 | 0.005944 | -0.050009 | -0.037694 | 0.10775 | 0.073574 | -0.001444 | 0.1067 | -0.21551 | -0.10632 | -0.15775 | -0.048565
3139.7031 | 119.1834 | -0.58594 | 118.5791 | 0.06691 | -0.058836 | 0.010893 | -0.057066 | 0.054577 | 0.021485 | -0.094765 | -0.15812 | -0.035253 | -0.091207 | -0.088049 | 0.066548 | 0.027798 | -0.033484 | 0.070079 | 0.11269 | -0.01306 | 0.056669 | -0.01129 | 0.10035 | 0.067261 | -0.048989 | -0.11235 | 0.010523 | -0.045431 | -0.042273 | 0.11232 | 0.073574 | 0.012292 | 0.11585 | -0.22467 | -0.12464 | -0.15775 | -0.057723
3141.5 | 119.2383 | -0.54474 | 118.7988 | 0.06691 | -0.058836 | 0.010893 | -0.052488 | 0.054577 | 0.016907 | -0.090186 | -0.15354 | -0.035253 | -0.091207 | -0.08347 | 0.057392 | 0.027798 | -0.038063 | 0.060923 | 0.11269 | -0.01306 | 0.056669 | -0.006712 | 0.10035 | 0.062683 | -0.04441 | -0.10777 | 0.010523 | -0.045431 | -0.037694 | 0.10317 | 0.073574 | 0.007713 | 0.1067 | -0.21094 | -0.11548 | -0.1486 | -0.053144
3143.2188 | 119.3619 | -0.73242 | 118.5104 | 0.06691 | -0.067994 | 0.015472 | -0.057066 | 0.059155 | 0.021485 | -0.094765 | -0.14897 | -0.039832 | -0.095785 | -0.078891 | 0.057392 | 0.032376 | -0.042641 | 0.070079 | 0.11269 | -0.022218 | 0.061248 | -0.01129 | 0.10493 | 0.067261 | -0.048989 | -0.10319 | 0.005944 | -0.050009 | -0.033115 | 0.10317 | 0.078152 | 0.003135 | 0.11585 | -0.20636 | -0.10632 | -0.15318 | -0.053144
3145 | 119.5129 | -0.48523 | 118.8995 | 0.062332 | -0.058836 | 0.001736 | -0.057066 | 0.059155 | 0.021485 | -0.099343 | -0.15812 | -0.039832 | -0.095785 | -0.078891 | 0.066548 | 0.027798 | -0.042641 | 0.070079 | 0.10811 | -0.01306 | 0.047512 | -0.01129 | 0.10493 | 0.067261 | -0.053567 | -0.11235 | 0.005944 | -0.050009 | -0.033115 | 0.11232 | 0.073574 | 0.003135 | 0.11585 | -0.22467 | -0.11548 | -0.16233 | -0.053144
3146.7812 | 119.5541 | -0.48981 | 118.9407 | 0.057754 | -0.072572 | 0.006315 | -0.052488 | 0.049999 | 0.021485 | -0.10392 | -0.15354 | -0.039832 | -0.10036 | -0.088049 | 0.066548 | 0.02322 | -0.038063 | 0.070079 | 0.10353 | -0.026796 | 0.052091 | -0.006712 | 0.095775 | 0.067261 | -0.058145 | -0.10777 | 0.005944 | -0.054587 | -0.042273 | 0.11232 | 0.068996 | 0.007713 | 0.11585 | -0.22009 | -0.11548 | -0.16691 | -0.0623
3148.5 | 119.2932 | -2.742 | 116.4688 | 0.062332 | -0.067994 | 0.010893 | -0.057066 | 0.059155 | 0.016907 | -0.094765 | -0.14897 | -0.035253 | -0.095785 | -0.088049 | 0.057392 | 0.036954 | -0.038063 | 0.070079 | 0.10811 | -0.022218 | 0.056669 | -0.01129 | 0.10493 | 0.062683 | -0.048989 | -0.10319 | 0.010523 | -0.050009 | -0.042273 | 0.10317 | 0.08273 | 0.007713 | 0.11585 | -0.20636 | -0.1109 | -0.15318 | -0.057722
3150.2812 | 119.5999 | -0.72784 | 118.8263 | 0.057754 | -0.067994 | 0.010893 | -0.052488 | 0.054577 | 0.021485 | -0.094765 | -0.15354 | -0.035253 | -0.091207 | -0.088049 | 0.06197 | 0.032376 | -0.033484 | 0.070079 | 0.10353 | -0.022218 | 0.056669 | -0.006712 | 0.10035 | 0.067261 | -0.048989 | -0.10777 | 0.010523 | -0.045431 | -0.042273 | 0.10775 | 0.078152 | 0.012292 | 0.11585 | -0.21551 | -0.12006 | -0.15318 | -0.057723
3152.0469 | 119.6365 | -0.5127 | 119.0552 | 0.062332 | -0.067994 | 0.015472 | -0.043331 | 0.059155 | 0.016907 | -0.099343 | -0.15354 | -0.044411 | -0.095785 | -0.08347 | 0.06197 | 0.027798 | -0.042641 | 0.065501 | 0.10811 | -0.022218 | 0.061248 | 0.002445 | 0.10493 | 0.062683 | -0.053567 | -0.10777 | 0.001365 | -0.050009 | -0.037694 | 0.10775 | 0.073574 | 0.003135 | 0.11128 | -0.21551 | -0.1109 | -0.15775 | -0.053144
3153.8281 | 119.6136 | -0.59967 | 119.0826 | 0.062332 | -0.063415 | 0.006315 | -0.057066 | 0.059155 | 0.021485 | -0.099343 | -0.15812 | -0.039832 | -0.10036 | -0.078891 | 0.06197 | 0.032376 | -0.033484 | 0.070079 | 0.10811 | -0.017639 | 0.052091 | -0.01129 | 0.10493 | 0.067261 | -0.053567 | -0.11235 | 0.005944 | -0.054587 | -0.033115 | 0.10775 | 0.078152 | 0.012292 | 0.11585 | -0.22009 | -0.12464 | -0.16233 | -0.066879
3155.6094 | 119.7739 | -0.60425 | 118.9957 | 0.057754 | -0.063415 | 0.015472 | -0.052488 | 0.054577 | 0.016907 | -0.099343 | -0.14897 | -0.035253 | -0.095785 | -0.08347 | 0.06197 | 0.032376 | -0.042641 | 0.065501 | 0.10353 | -0.017639 | 0.061248 | -0.006712 | 0.10035 | 0.062683 | -0.053567 | -0.10319 | 0.010523 | -0.050009 | -0.037694 | 0.10775 | 0.078152 | 0.003135 | 0.11128 | -0.21094 | -0.10632 | -0.15775 | -0.053144
3157.3906 | 119.7876 | -0.64545 | 119.0277 | 0.057754 | -0.063415 | 0.015472 | -0.057066 | 0.054577 | 0.016907 | -0.094765 | -0.15812 | -0.035253 | -0.091207 | -0.08347 | 0.06197 | 0.032376 | -0.04722 | 0.070079 | 0.10353 | -0.017639 | 0.061248 | -0.01129 | 0.10035 | 0.062683 | -0.048989 | -0.11235 | 0.010523 | -0.045431 | -0.037694 | 0.10775 | 0.078152 | -0.001444 | 0.11585 | -0.22009 | -0.1109 | -0.15318 | -0.043987
3159.125 | 119.8059 | -1.0757 | 118.5837 | 0.057754 | -0.067994 | -0.002842 | -0.047909 | 0.059155 | 0.016907 | -0.094765 | -0.15354 | -0.039832 | -0.091207 | -0.088049 | 0.06197 | 0.02322 | -0.038063 | 0.070079 | 0.10353 | -0.022218 | 0.042934 | -0.002133 | 0.10493 | 0.062683 | -0.048989 | -0.10777 | 0.005944 | -0.045431 | -0.042273 | 0.10775 | 0.068996 | 0.007713 | 0.11585 | -0.21551 | -0.11548 | -0.15318 | -0.053144
3160.8906 | 119.6091 | -1.7807 | 117.9153 | 0.062332 | -0.067994 | 0.015472 | -0.052488 | 0.059155 | 0.016907 | -0.10392 | -0.15354 | -0.039832 | -0.095785 | -0.08347 | 0.06197 | 0.032376 | -0.042641 | 0.056344 | 0.10811 | -0.022218 | 0.061248 | -0.006712 | 0.10493 | 0.062683 | -0.058145 | -0.10777 | 0.005944 | -0.050009 | -0.037694 | 0.10775 | 0.078152 | 0.003135 | 0.10212 | -0.21551 | -0.1109 | -0.15775 | -0.053144
3162.6094 | 119.7876 | -1.1627 | 118.5013 | 0.057754 | -0.077151 | 0.006315 | -0.052488 | 0.054577 | 0.016907 | -0.099343 | -0.15354 | -0.035253 | -0.086628 | -0.078891 | 0.06197 | 0.02322 | -0.04722 | 0.070079 | 0.10353 | -0.031375 | 0.052091 | -0.006712 | 0.10035 | 0.062683 | -0.053567 | -0.10777 | 0.010523 | -0.040852 | -0.033115 | 0.10775 | 0.068996 | -0.001444 | 0.11585 | -0.21551 | -0.10632 | -0.1486 | -0.039408
3164.3906 | 119.7464 | -0.70038 | 119.0414 | 0.057754 | -0.067994 | 0.006315 | -0.043331 | 0.063733 | 0.021485 | -0.094765 | -0.14439 | -0.044411 | -0.095785 | -0.078891 | 0.057392 | 0.032376 | -0.038063 | 0.065501 | 0.10353 | -0.022218 | 0.052091 | 0.002445 | 0.10951 | 0.067261 | -0.048989 | -0.098611 | 0.001365 | -0.050009 | -0.033115 | 0.10317 | 0.078152 | 0.007713 | 0.11128 | -0.20178 | -0.10632 | -0.15318 | -0.057722
3166.1875 | 119.7281 | -2.4811 | 116.9907 | 0.062332 | -0.067994 | 0.006315 | -0.047909 | 0.049999 | 0.016907 | -0.099343 | -0.14897 | -0.035253 | -0.091207 | -0.088049 | 0.06197 | 0.027798 | -0.038063 | 0.070079 | 0.10811 | -0.022218 | 0.052091 | -0.002133 | 0.095775 | 0.062683 | -0.053567 | -0.10319 | 0.010523 | -0.045431 | -0.042273 | 0.10775 | 0.073574 | 0.007713 | 0.11585 | -0.21094 | -0.1109 | -0.15318 | -0.053144
3167.9062 | 119.5908 | -1.6846 | 117.9245 | 0.062332 | -0.067994 | 0.010893 | -0.061645 | 0.054577 | 0.016907 | -0.099343 | -0.15354 | -0.039832 | -0.091207 | -0.088049 | 0.066548 | 0.02322 | -0.042641 | 0.070079 | 0.10811 | -0.022218 | 0.056669 | -0.015869 | 0.10035 | 0.062683 | -0.053567 | -0.10777 | 0.005944 | -0.045431 | -0.042273 | 0.11232 | 0.068996 | 0.003135 | 0.11585 | -0.22009 | -0.1109 | -0.15775 | -0.048566
3169.6719 | 119.4809 | -4.4678 | 114.7842 | 0.062332 | -0.067994 | 0.015472 | -0.052488 | 0.054577 | 0.016907 | -0.090186 | -0.15354 | -0.035253 | -0.095785 | -0.078891 | 0.06197 | 0.027798 | -0.042641 | 0.070079 | 0.10811 | -0.022218 | 0.061248 | -0.006712 | 0.10035 | 0.062683 | -0.04441 | -0.10777 | 0.010523 | -0.050009 | -0.033115 | 0.10775 | 0.073574 | 0.003135 | 0.11585 | -0.21551 | -0.1109 | -0.15775 | -0.053144
3171.3906 | 119.3527 | -5.127 | 114.1937 | 0.057754 | -0.063415 | 0.015472 | -0.043331 | 0.059155 | 0.012329 | -0.090186 | -0.14439 | -0.039832 | -0.095785 | -0.08347 | 0.057392 | 0.027798 | -0.04722 | 0.074657 | 0.10353 | -0.017639 | 0.061248 | 0.002445 | 0.10493 | 0.058105 | -0.04441 | -0.098611 | 0.005944 | -0.050009 | -0.037694 | 0.10317 | 0.073574 | -0.001444 | 0.12043 | -0.20178 | -0.097167 | -0.15318 | -0.048565
3173.1719 | 119.1879 | -6.2622 | 112.912 | 0.062332 | -0.067994 | 0.015472 | -0.047909 | 0.054577 | 0.026064 | -0.099343 | -0.14897 | -0.030674 | -0.086628 | -0.08347 | 0.052814 | 0.02322 | -0.042641 | 0.060923 | 0.10811 | -0.022218 | 0.061248 | -0.002133 | 0.10035 | 0.07184 | -0.053567 | -0.10319 | 0.015102 | -0.040852 | -0.037694 | 0.09859 | 0.068996 | 0.003135 | 0.1067 | -0.20178 | -0.10632 | -0.13944 | -0.043987
3174.9375 | 118.7851 | -11.0275 | 107.5607 | 0.062332 | -0.058836 | 0.015472 | -0.052488 | 0.054577 | 0.021485 | -0.094765 | -0.15354 | -0.030674 | -0.091207 | -0.078891 | 0.06197 | 0.014064 | -0.042641 | 0.060923 | 0.10811 | -0.01306 | 0.061248 | -0.006712 | 0.10035 | 0.067261 | -0.048989 | -0.10777 | 0.015102 | -0.045431 | -0.033115 | 0.10775 | 0.05984 | 0.003135 | 0.1067 | -0.21551 | -0.1109 | -0.15318 | -0.048566
3176.7188 | 118.8263 | -6.4957 | 112.4039 | 0.06691 | -0.067994 | 0.006315 | -0.047909 | 0.049999 | 0.021485 | -0.090186 | -0.14897 | -0.039832 | -0.091207 | -0.078891 | 0.048236 | 0.02322 | -0.038063 | 0.060923 | 0.11269 | -0.022218 | 0.052091 | -0.002133 | 0.095775 | 0.067261 | -0.04441 | -0.10319 | 0.005944 | -0.045431 | -0.033115 | 0.094012 | 0.068996 | 0.007713 | 0.1067 | -0.1972 | -0.1109 | -0.13944 | -0.053144
3178.5 | 118.8538 | -5.9509 | 112.7838 | 0.06691 | -0.072572 | 0.015472 | -0.052488 | 0.054577 | 0.016907 | -0.090186 | -0.14897 | -0.035253 | -0.091207 | -0.074312 | 0.057392 | 0.02322 | -0.042641 | 0.060923 | 0.11269 | -0.026796 | 0.061248 | -0.006712 | 0.10035 | 0.062683 | -0.04441 | -0.10319 | 0.010523 | -0.045431 | -0.028536 | 0.10317 | 0.068996 | 0.003135 | 0.1067 | -0.20636 | -0.10632 | -0.1486 | -0.048566
3180.2969 | 118.4555 | -8.0704 | 110.2432 | 0.06691 | -0.063415 | 0.010893 | -0.047909 | 0.063733 | 0.021485 | -0.099343 | -0.14897 | -0.035253 | -0.091207 | -0.078891 | 0.06197 | 0.027798 | -0.038063 | 0.065501 | 0.11269 | -0.017639 | 0.056669 | -0.002133 | 0.10951 | 0.067261 | -0.053567 | -0.10319 | 0.010523 | -0.045431 | -0.033115 | 0.10775 | 0.073574 | 0.007713 | 0.11128 | -0.21094 | -0.1109 | -0.15318 | -0.053144
3182.0781 | 118.2541 | -11.7966 | 106.2744 | 0.06691 | -0.067994 | 0.015472 | -0.038752 | 0.059155 | 0.026064 | -0.085608 | -0.14897 | -0.030674 | -0.086628 | -0.074312 | 0.057392 | 0.02322 | -0.042641 | 0.056344 | 0.11269 | -0.022218 | 0.061248 | 0.007024 | 0.10493 | 0.07184 | -0.039832 | -0.10319 | 0.015102 | -0.040852 | -0.028536 | 0.10317 | 0.068996 | 0.003135 | 0.10212 | -0.20636 | -0.10632 | -0.14402 | -0.043987
3183.8594 | 117.6865 | -16.1499 | 101.4038 | 0.06691 | -0.058836 | 0.020051 | -0.047909 | 0.059155 | 0.026064 | -0.085608 | -0.14439 | -0.030674 | -0.08205 | -0.074312 | 0.048236 | 0.018642 | -0.051798 | 0.056344 | 0.11269 | -0.01306 | 0.065827 | -0.002133 | 0.10493 | 0.07184 | -0.039832 | -0.098611 | 0.015102 | -0.036274 | -0.028536 | 0.094012 | 0.064418 | -0.006022 | 0.10212 | -0.19262 | -0.092589 | -0.13029 | -0.030252
3185.5938 | 117.8192 | -12.2635 | 105.368 | 0.06691 | -0.067994 | 0.015472 | -0.038752 | 0.063733 | 0.026064 | -0.085608 | -0.13981 | -0.021517 | -0.086628 | -0.078891 | 0.066548 | 0.02322 | -0.04722 | 0.060923 | 0.11269 | -0.022218 | 0.061248 | 0.007024 | 0.10951 | 0.07184 | -0.039832 | -0.094033 | 0.024259 | -0.040852 | -0.033115 | 0.11232 | 0.068996 | -0.001444 | 0.1067 | -0.20636 | -0.092589 | -0.15318 | -0.039408
3187.3594 | 119.0094 | -0.55389 | 118.4052 | 0.062332 | -0.067994 | 0.010893 | -0.057066 | 0.049999 | 0.016907 | -0.099343 | -0.14897 | -0.035253 | -0.095785 | -0.088049 | 0.052814 | 0.032376 | -0.042641 | 0.065501 | 0.10811 | -0.022218 | 0.056669 | -0.01129 | 0.095775 | 0.062683 | -0.053567 | -0.10319 | 0.010523 | -0.050009 | -0.042273 | 0.09859 | 0.078152 | 0.003135 | 0.11128 | -0.20178 | -0.10632 | -0.1486 | -0.053144
3189.0781 | 119.3893 | -0.59967 | 118.8263 | 0.057754 | -0.067994 | 0.010893 | -0.057066 | 0.054577 | 0.021485 | -0.099343 | -0.1627 | -0.039832 | -0.095785 | -0.088049 | 0.057392 | 0.032376 | -0.042641 | 0.065501 | 0.10353 | -0.022218 | 0.056669 | -0.01129 | 0.10035 | 0.067261 | -0.053567 | -0.11693 | 0.005944 | -0.050009 | -0.042273 | 0.10317 | 0.078152 | 0.003135 | 0.11128 | -0.22009 | -0.12006 | -0.15318 | -0.053144
3190.8594 | 119.5129 | -0.60425 | 118.9865 | 0.057754 | -0.067994 | 0.010893 | -0.047909 | 0.054577 | 0.021485 | -0.099343 | -0.15354 | -0.039832 | -0.091207 | -0.08347 | 0.057392 | 0.027798 | -0.038063 | 0.074657 | 0.10353 | -0.022218 | 0.056669 | -0.002133 | 0.10035 | 0.067261 | -0.053567 | -0.10777 | 0.005944 | -0.045431 | -0.037694 | 0.10317 | 0.073574 | 0.007713 | 0.12043 | -0.21094 | -0.11548 | -0.1486 | -0.053144
3192.5781 | 119.5999 | -0.60883 | 118.9957 | 0.057754 | -0.063415 | 0.006315 | -0.052488 | 0.054577 | 0.016907 | -0.094765 | -0.15354 | -0.035253 | -0.10036 | -0.08347 | 0.06197 | 0.02322 | -0.042641 | 0.074657 | 0.10353 | -0.017639 | 0.052091 | -0.006712 | 0.10035 | 0.062683 | -0.048989 | -0.10777 | 0.010523 | -0.054587 | -0.037694 | 0.10775 | 0.068996 | 0.003135 | 0.12043 | -0.21551 | -0.1109 | -0.16233 | -0.057722
3194.3594 | 118.4784 | -5.5527 | 112.9578 | 0.06691 | -0.067994 | 0.010893 | -0.057066 | 0.054577 | 0.021485 | -0.094765 | -0.14897 | -0.030674 | -0.08205 | -0.08347 | 0.06197 | 0.02322 | -0.038063 | 0.065501 | 0.11269 | -0.022218 | 0.056669 | -0.01129 | 0.10035 | 0.067261 | -0.048989 | -0.10319 | 0.015102 | -0.036274 | -0.037694 | 0.10775 | 0.068996 | 0.007713 | 0.11128 | -0.21094 | -0.1109 | -0.14402 | -0.043987
3196.1406 | 119.6274 | -0.63171 | 118.9224 | 0.053175 | -0.067994 | 0.015472 | -0.052488 | 0.049999 | 0.021485 | -0.10392 | -0.15354 | -0.039832 | -0.095785 | -0.088049 | 0.06197 | 0.032376 | -0.04722 | 0.074657 | 0.098951 | -0.022218 | 0.061248 | -0.006712 | 0.095775 | 0.067261 | -0.058145 | -0.10777 | 0.005944 | -0.050009 | -0.042273 | 0.10775 | 0.078152 | -0.001444 | 0.12043 | -0.21551 | -0.10632 | -0.15775 | -0.048565
3197.9062 | 119.5221 | -0.72327 | 118.7851 | 0.053175 | -0.067994 | 0.006315 | -0.052488 | 0.059155 | 0.021485 | -0.094765 | -0.15812 | -0.039832 | -0.095785 | -0.08347 | 0.057392 | 0.032376 | -0.04722 | 0.060923 | 0.098951 | -0.022218 | 0.052091 | -0.006712 | 0.10493 | 0.067261 | -0.048989 | -0.11235 | 0.005944 | -0.050009 | -0.037694 | 0.10317 | 0.078152 | -0.001444 | 0.1067 | -0.21552 | -0.1109 | -0.15318 | -0.048565
3199.625 | 119.632 | -0.73242 | 118.9728 | 0.057754 | -0.077151 | 0.006315 | -0.047909 | 0.054577 | 0.021485 | -0.090186 | -0.14897 | -0.035253 | -0.10036 | -0.074312 | 0.052814 | 0.027798 | -0.04722 | 0.065501 | 0.10353 | -0.031375 | 0.052091 | -0.002133 | 0.10035 | 0.067261 | -0.04441 | -0.10319 | 0.010523 | -0.054587 | -0.028536 | 0.09859 | 0.073574 | -0.001444 | 0.11128 | -0.20178 | -0.10175 | -0.15318 | -0.053143
3201.4062 | 119.6228 | -0.71869 | 118.9911 | 0.062332 | -0.077151 | 0.010893 | -0.057066 | 0.054577 | 0.026064 | -0.090186 | -0.15354 | -0.030674 | -0.095785 | -0.078891 | 0.057392 | 0.027798 | -0.04722 | 0.065501 | 0.10811 | -0.031375 | 0.056669 | -0.01129 | 0.10035 | 0.07184 | -0.04441 | -0.10777 | 0.015102 | -0.050009 | -0.033115 | 0.10317 | 0.073574 | -0.001444 | 0.11128 | -0.21094 | -0.10632 | -0.15318 | -0.048565
3203.125 | 119.8242 | -0.70496 | 119.0277 | 0.062332 | -0.077151 | 0.006315 | -0.057066 | 0.049999 | 0.021485 | -0.099343 | -0.15812 | -0.035253 | -0.091207 | -0.078891 | 0.06197 | 0.032376 | -0.038063 | 0.070079 | 0.10811 | -0.031375 | 0.052091 | -0.01129 | 0.095775 | 0.067261 | -0.053567 | -0.11235 | 0.010523 | -0.045431 | -0.033115 | 0.10775 | 0.078152 | 0.007713 | 0.11585 | -0.22009 | -0.12006 | -0.15318 | -0.053144
3204.9062 | 119.7784 | -0.72327 | 119.1376 | 0.057754 | -0.072572 | 0.006315 | -0.052488 | 0.054577 | 0.021485 | -0.090186 | -0.1627 | -0.035253 | -0.095785 | -0.078891 | 0.06197 | 0.018642 | -0.042641 | 0.070079 | 0.10353 | -0.026796 | 0.052091 | -0.006712 | 0.10035 | 0.067261 | -0.04441 | -0.11693 | 0.010523 | -0.050009 | -0.033115 | 0.10775 | 0.064418 | 0.003135 | 0.11585 | -0.22467 | -0.12006 | -0.15775 | -0.053144
3206.6875 | 119.9707 | -0.6958 | 119.1193 | 0.057754 | -0.072572 | 0.001736 | -0.057066 | 0.054577 | 0.021485 | -0.099343 | -0.14897 | -0.039832 | -0.095785 | -0.088049 | 0.052814 | 0.032376 | -0.042641 | 0.065501 | 0.10353 | -0.026796 | 0.047512 | -0.01129 | 0.10035 | 0.067261 | -0.053567 | -0.10319 | 0.005944 | -0.050009 | -0.042273 | 0.09859 | 0.078152 | 0.003135 | 0.11128 | -0.20178 | -0.10632 | -0.1486 | -0.053144
3208.3906 | 119.1147 | -7.6218 | 111.2457 | 0.062332 | -0.077151 | 0.010893 | -0.057066 | 0.059155 | 0.026064 | -0.090186 | -0.14897 | -0.035253 | -0.086628 | -0.08347 | 0.066548 | 0.02322 | -0.04722 | 0.060923 | 0.10811 | -0.031375 | 0.056669 | -0.01129 | 0.10493 | 0.07184 | -0.04441 | -0.10319 | 0.010523 | -0.040852 | -0.037694 | 0.11232 | 0.068996 | -0.001444 | 0.1067 | -0.21551 | -0.10175 | -0.15318 | -0.039408
3210.1719 | 119.0277 | -3.9825 | 114.9994 | 0.062332 | -0.077151 | 0.015472 | -0.047909 | 0.054577 | 0.030642 | -0.090186 | -0.15354 | -0.035253 | -0.086628 | -0.078891 | 0.057392 | 0.018642 | -0.042641 | 0.065501 | 0.10811 | -0.031375 | 0.061248 | -0.002133 | 0.10035 | 0.076418 | -0.04441 | -0.10777 | 0.010523 | -0.040852 | -0.033115 | 0.10317 | 0.064418 | 0.003135 | 0.11128 | -0.21094 | -0.1109 | -0.14402 | -0.043987
3211.9531 | 118.1946 | -10.936 | 107.1945 | 0.062332 | -0.063415 | 0.015472 | -0.047909 | 0.063733 | 0.026064 | -0.090186 | -0.14439 | -0.035253 | -0.08205 | -0.078891 | 0.06197 | 0.02322 | -0.033484 | 0.065501 | 0.10811 | -0.017639 | 0.061248 | -0.002133 | 0.10951 | 0.07184 | -0.04441 | -0.098611 | 0.010523 | -0.036274 | -0.033115 | 0.10775 | 0.068996 | 0.012292 | 0.11128 | -0.20636 | -0.1109 | -0.14402 | -0.048566
3213.7188 | 118.6752 | -5.4428 | 113.0585 | 0.062332 | -0.063415 | 0.020051 | -0.047909 | 0.054577 | 0.021485 | -0.094765 | -0.14439 | -0.039832 | -0.08205 | -0.08347 | 0.06197 | 0.02322 | -0.042641 | 0.060923 | 0.10811 | -0.017639 | 0.065827 | -0.002133 | 0.10035 | 0.067261 | -0.048989 | -0.098611 | 0.005944 | -0.036274 | -0.037694 | 0.10775 | 0.068996 | 0.003135 | 0.1067 | -0.20636 | -0.10175 | -0.14402 | -0.039409
3215.4375 | 118.5287 | -6.3492 | 112.1017 | 0.06691 | -0.072572 | 0.020051 | -0.047909 | 0.059155 | 0.021485 | -0.094765 | -0.13981 | -0.030674 | -0.091207 | -0.08347 | 0.057392 | 0.027798 | -0.04722 | 0.060923 | 0.11269 | -0.026796 | 0.065827 | -0.002133 | 0.10493 | 0.067261 | -0.048989 | -0.094033 | 0.015102 | -0.045431 | -0.037694 | 0.10317 | 0.073574 | -0.001444 | 0.1067 | -0.1972 | -0.092589 | -0.1486 | -0.043987
3217.2188 | 119.4901 | -0.67291 | 118.7897 | 0.057754 | -0.077151 | 0.010893 | -0.057066 | 0.054577 | 0.016907 | -0.10392 | -0.14897 | -0.030674 | -0.086628 | -0.08347 | 0.06197 | 0.027798 | -0.042641 | 0.065501 | 0.10353 | -0.031375 | 0.056669 | -0.01129 | 0.10035 | 0.062683 | -0.058145 | -0.10319 | 0.015102 | -0.040852 | -0.037694 | 0.10775 | 0.073574 | 0.003135 | 0.11128 | -0.21094 | -0.10632 | -0.1486 | -0.043987
3219.0156 | 118.1076 | -11.2335 | 106.8604 | 0.062332 | -0.063415 | 0.015472 | -0.043331 | 0.063733 | 0.026064 | -0.099343 | -0.14897 | -0.026096 | -0.086628 | -0.078891 | 0.057392 | 0.02322 | -0.038063 | 0.065501 | 0.10811 | -0.017639 | 0.061248 | 0.002445 | 0.10951 | 0.07184 | -0.053567 | -0.10319 | 0.01968 | -0.040852 | -0.033115 | 0.10317 | 0.068996 | 0.007713 | 0.11128 | -0.20636 | -0.1109 | -0.14402 | -0.048565
3220.7344 | 119.1055 | -2.4307 | 116.5878 | 0.062332 | -0.077151 | 0.006315 | -0.047909 | 0.059155 | 0.012329 | -0.094765 | -0.14897 | -0.035253 | -0.091207 | -0.08347 | 0.06197 | 0.027798 | -0.042641 | 0.065501 | 0.10811 | -0.031375 | 0.052091 | -0.002133 | 0.10493 | 0.058105 | -0.048989 | -0.10319 | 0.010523 | -0.045431 | -0.037694 | 0.10775 | 0.073574 | 0.003135 | 0.11128 | -0.21094 | -0.10632 | -0.15318 | -0.048566
3222.5312 | 119.5404 | -1.355 | 118.0939 | 0.06691 | -0.077151 | 0.010893 | -0.052488 | 0.049999 | 0.016907 | -0.094765 | -0.15354 | -0.035253 | -0.08205 | -0.08347 | 0.057392 | 0.032376 | -0.051798 | 0.070079 | 0.11269 | -0.031375 | 0.056669 | -0.006712 | 0.095775 | 0.062683 | -0.048989 | -0.10777 | 0.010523 | -0.036274 | -0.037694 | 0.10317 | 0.078152 | -0.006022 | 0.11585 | -0.21094 | -0.10175 | -0.13944 | -0.030252
3224.2656 | 118.9774 | -6.5872 | 112.3581 | 0.062332 | -0.072572 | 0.020051 | -0.052488 | 0.054577 | 0.030642 | -0.094765 | -0.14439 | -0.035253 | -0.095785 | -0.08347 | 0.057392 | 0.018642 | -0.04722 | 0.056344 | 0.10811 | -0.026796 | 0.065827 | -0.006712 | 0.10035 | 0.076418 | -0.048989 | -0.098611 | 0.010523 | -0.050009 | -0.037694 | 0.10317 | 0.064418 | -0.001444 | 0.10212 | -0.20178 | -0.097167 | -0.15318 | -0.048565
3226.0312 | 118.8766 | -2.6413 | 116.1758 | 0.062332 | -0.067994 | 0.006315 | -0.052488 | 0.059155 | 0.016907 | -0.090186 | -0.14439 | -0.026096 | -0.086628 | -0.08347 | 0.057392 | 0.027798 | -0.042641 | 0.065501 | 0.10811 | -0.022218 | 0.052091 | -0.006712 | 0.10493 | 0.062683 | -0.04441 | -0.098611 | 0.01968 | -0.040852 | -0.037694 | 0.10317 | 0.073574 | 0.003135 | 0.11128 | -0.20178 | -0.10175 | -0.14402 | -0.043987
3227.8125 | 118.6523 | -7.3883 | 111.4105 | 0.062332 | -0.067994 | 0.015472 | -0.043331 | 0.059155 | 0.021485 | -0.090186 | -0.14439 | -0.035253 | -0.086628 | -0.08347 | 0.057392 | 0.02322 | -0.038063 | 0.056344 | 0.10811 | -0.022218 | 0.061248 | 0.002445 | 0.10493 | 0.067261 | -0.04441 | -0.098611 | 0.010523 | -0.040852 | -0.037694 | 0.10317 | 0.068996 | 0.007713 | 0.10212 | -0.20178 | -0.10632 | -0.14402 | -0.048565
3229.5938 | 119.1422 | -4.5181 | 114.4363 | 0.06691 | -0.077151 | 0.010893 | -0.057066 | 0.059155 | 0.016907 | -0.094765 | -0.15354 | -0.030674 | -0.091207 | -0.078891 | 0.057392 | 0.02322 | -0.042641 | 0.065501 | 0.11269 | -0.031375 | 0.056669 | -0.01129 | 0.10493 | 0.062683 | -0.048989 | -0.10777 | 0.015102 | -0.045431 | -0.033115 | 0.10317 | 0.068996 | 0.003135 | 0.11128 | -0.21094 | -0.1109 | -0.1486 | -0.048566
3231.3594 | 119.0964 | -1.7212 | 117.0456 | 0.062332 | -0.072572 | 0.010893 | -0.047909 | 0.059155 | 0.016907 | -0.094765 | -0.14897 | -0.026096 | -0.091207 | -0.074312 | 0.057392 | 0.027798 | -0.04722 | 0.074657 | 0.10811 | -0.026796 | 0.056669 | -0.002133 | 0.10493 | 0.062683 | -0.048989 | -0.10319 | 0.01968 | -0.045431 | -0.028536 | 0.10317 | 0.073574 | -0.001444 | 0.12043 | -0.20636 | -0.10175 | -0.1486 | -0.043987
3233.0781 | 119.1376 | -1.0208 | 118.0527 | 0.062332 | -0.072572 | 0.006315 | -0.057066 | 0.049999 | 0.016907 | -0.099343 | -0.15354 | -0.039832 | -0.091207 | -0.08347 | 0.057392 | 0.032376 | -0.042641 | 0.070079 | 0.10811 | -0.026796 | 0.052091 | -0.01129 | 0.095775 | 0.062683 | -0.053567 | -0.10777 | 0.005944 | -0.045431 | -0.037694 | 0.10317 | 0.078152 | 0.003135 | 0.11585 | -0.21094 | -0.1109 | -0.1486 | -0.048566
3234.8438 | 118.3823 | -11.3205 | 107.3547 | 0.06691 | -0.067994 | 0.015472 | -0.047909 | 0.063733 | 0.016907 | -0.085608 | -0.14439 | -0.026096 | -0.08205 | -0.08347 | 0.057392 | 0.02322 | -0.038063 | 0.065501 | 0.11269 | -0.022218 | 0.061248 | -0.002133 | 0.10951 | 0.062683 | -0.039832 | -0.098611 | 0.01968 | -0.036274 | -0.037694 | 0.10317 | 0.068996 | 0.007713 | 0.11128 | -0.20178 | -0.10632 | -0.13944 | -0.043987
3236.5625 | 119.3298 | -12.9089 | 106.5857 | 0.071489 | -0.067994 | 0.015472 | -0.047909 | 0.059155 | 0.026064 | -0.090186 | -0.14897 | -0.035253 | -0.091207 | -0.074312 | 0.057392 | 0.027798 | -0.04722 | 0.060923 | 0.11726 | -0.022218 | 0.061248 | -0.002133 | 0.10493 | 0.07184 | -0.04441 | -0.10319 | 0.010523 | -0.045431 | -0.028536 | 0.10317 | 0.073574 | -0.001444 | 0.1067 | -0.20636 | -0.10175 | -0.1486 | -0.043987
3238.3281 | 118.2587 | -14.328 | 103.5049 | 0.06691 | -0.067994 | 0.020051 | -0.052488 | 0.054577 | 0.030642 | -0.090186 | -0.14439 | -0.030674 | -0.08205 | -0.078891 | 0.057392 | 0.018642 | -0.051798 | 0.060923 | 0.11269 | -0.022218 | 0.065827 | -0.006712 | 0.10035 | 0.076418 | -0.04441 | -0.098611 | 0.015102 | -0.036274 | -0.033115 | 0.10317 | 0.064418 | -0.006022 | 0.1067 | -0.20178 | -0.092589 | -0.13944 | -0.030252
3240.0469 | 119.0369 | -7.0496 | 111.9507 | 0.062332 | -0.08173 | 0.010893 | -0.047909 | 0.054577 | 0.016907 | -0.090186 | -0.15354 | -0.035253 | -0.08205 | -0.078891 | 0.06197 | 0.032376 | -0.038063 | 0.060923 | 0.10811 | -0.035954 | 0.056669 | -0.002133 | 0.10035 | 0.062683 | -0.04441 | -0.10777 | 0.010523 | -0.036274 | -0.033115 | 0.10775 | 0.078152 | 0.007713 | 0.1067 | -0.21551 | -0.11548 | -0.14402 | -0.043987
3241.7812 | 119.3115 | -2.3987 | 116.7572 | 0.062332 | -0.077151 | 0.001736 | -0.052488 | 0.054577 | 0.016907 | -0.094765 | -0.14897 | -0.035253 | -0.091207 | -0.078891 | 0.06197 | 0.027798 | -0.038063 | 0.079235 | 0.10811 | -0.031375 | 0.047512 | -0.006712 | 0.10035 | 0.062683 | -0.048989 | -0.10319 | 0.010523 | -0.045431 | -0.033115 | 0.10775 | 0.073574 | 0.007713 | 0.12501 | -0.21094 | -0.1109 | -0.15318 | -0.053144
3243.5 | 119.0598 | -2.5497 | 116.6107 | 0.06691 | -0.072572 | 0.015472 | -0.047909 | 0.063733 | 0.021485 | -0.090186 | -0.15354 | -0.039832 | -0.10036 | -0.074312 | 0.052814 | 0.02322 | -0.042641 | 0.060923 | 0.11269 | -0.026796 | 0.061248 | -0.002133 | 0.10951 | 0.067261 | -0.04441 | -0.10777 | 0.005944 | -0.054587 | -0.028536 | 0.09859 | 0.068996 | 0.003135 | 0.1067 | -0.20636 | -0.1109 | -0.15318 | -0.057722
3245.2812 | 119.1376 | -4.509 | 114.4684 | 0.06691 | -0.077151 | 0.010893 | -0.043331 | 0.059155 | 0.016907 | -0.090186 | -0.14439 | -0.030674 | -0.08205 | -0.08347 | 0.057392 | 0.032376 | -0.04722 | 0.070079 | 0.11269 | -0.031375 | 0.056669 | 0.002445 | 0.10493 | 0.062683 | -0.04441 | -0.098611 | 0.015102 | -0.036274 | -0.037694 | 0.10317 | 0.078152 | -0.001444 | 0.11585 | -0.20178 | -0.097167 | -0.13944 | -0.03483
3247.0625 | 118.959 | -3.5339 | 115.5075 | 0.062332 | -0.072572 | 0.010893 | -0.052488 | 0.049999 | 0.021485 | -0.094765 | -0.14897 | -0.026096 | -0.095785 | -0.08347 | 0.057392 | 0.018642 | -0.04722 | 0.060923 | 0.10811 | -0.026796 | 0.056669 | -0.006712 | 0.095775 | 0.067261 | -0.048989 | -0.10319 | 0.01968 | -0.050009 | -0.037694 | 0.10317 | 0.064418 | -0.001444 | 0.1067 | -0.20636 | -0.10175 | -0.15318 | -0.048565
3248.7812 | 119.2108 | -2.8381 | 116.3361 | 0.062332 | -0.077151 | 0.010893 | -0.052488 | 0.054577 | 0.026064 | -0.090186 | -0.14897 | -0.039832 | -0.086628 | -0.078891 | 0.057392 | 0.027798 | -0.042641 | 0.065501 | 0.10811 | -0.031375 | 0.056669 | -0.006712 | 0.10035 | 0.07184 | -0.04441 | -0.10319 | 0.005944 | -0.040852 | -0.033115 | 0.10317 | 0.073574 | 0.003135 | 0.11128 | -0.20636 | -0.10632 | -0.14402 | -0.043987
3250.5 | 119.0186 | -4.8157 | 114.0335 | 0.062332 | -0.08173 | 0.015472 | -0.047909 | 0.049999 | 0.030642 | -0.094765 | -0.14897 | -0.035253 | -0.086628 | -0.078891 | 0.052814 | 0.02322 | -0.04722 | 0.060923 | 0.10811 | -0.035954 | 0.061248 | -0.002133 | 0.095775 | 0.076418 | -0.048989 | -0.10319 | 0.010523 | -0.040852 | -0.033115 | 0.09859 | 0.068996 | -0.001444 | 0.1067 | -0.20178 | -0.10175 | -0.13944 | -0.039408
3252.2969 | 119.0186 | -4.454 | 114.6011 | 0.06691 | -0.072572 | 0.006315 | -0.052488 | 0.054577 | 0.016907 | -0.10392 | -0.15812 | -0.030674 | -0.091207 | -0.088049 | 0.057392 | 0.02322 | -0.042641 | 0.065501 | 0.11269 | -0.026796 | 0.052091 | -0.006712 | 0.10035 | 0.062683 | -0.058145 | -0.11235 | 0.015102 | -0.045431 | -0.042273 | 0.10317 | 0.068996 | 0.003135 | 0.11128 | -0.21552 | -0.11548 | -0.1486 | -0.048566
3254.0781 | 118.8904 | -5.6534 | 113.3148 | 0.057754 | -0.08173 | 0.015472 | -0.057066 | 0.059155 | 0.021485 | -0.094765 | -0.14439 | -0.039832 | -0.086628 | -0.08347 | 0.052814 | 0.027798 | -0.04722 | 0.065501 | 0.10353 | -0.035954 | 0.061248 | -0.01129 | 0.10493 | 0.067261 | -0.048989 | -0.098611 | 0.005944 | -0.040852 | -0.037694 | 0.09859 | 0.073574 | -0.001444 | 0.11128 | -0.1972 | -0.097167 | -0.13944 | -0.039408
3255.8594 | 118.2358 | -9.8557 | 108.3069 | 0.06691 | -0.072572 | 0.015472 | -0.038752 | 0.06831 | 0.021485 | -0.090186 | -0.14439 | -0.035253 | -0.086628 | -0.074312 | 0.06197 | 0.027798 | -0.04722 | 0.065501 | 0.11269 | -0.026796 | 0.061248 | 0.007024 | 0.11409 | 0.067261 | -0.04441 | -0.098611 | 0.010523 | -0.040852 | -0.028536 | 0.10775 | 0.073574 | -0.001444 | 0.11128 | -0.20636 | -0.097167 | -0.1486 | -0.039408
3257.5781 | 118.2266 | -9.787 | 108.3252 | 0.062332 | -0.077151 | 0.020051 | -0.043331 | 0.059155 | 0.021485 | -0.090186 | -0.14439 | -0.035253 | -0.086628 | -0.078891 | 0.052814 | 0.02322 | -0.042641 | 0.065501 | 0.10811 | -0.031375 | 0.065827 | 0.002445 | 0.10493 | 0.067261 | -0.04441 | -0.098611 | 0.010523 | -0.040852 | -0.033115 | 0.09859 | 0.068996 | 0.003135 | 0.11128 | -0.1972 | -0.10175 | -0.13944 | -0.043987
3259.375 | 117.5858 | -14.3646 | 102.9739 | 0.06691 | -0.072572 | 0.010893 | -0.043331 | 0.049999 | 0.026064 | -0.08103 | -0.14897 | -0.026096 | -0.08205 | -0.074312 | 0.052814 | 0.018642 | -0.04722 | 0.056344 | 0.11269 | -0.026796 | 0.056669 | 0.002445 | 0.095775 | 0.07184 | -0.035254 | -0.10319 | 0.01968 | -0.036274 | -0.028536 | 0.09859 | 0.064418 | -0.001444 | 0.10212 | -0.20178 | -0.10175 | -0.13486 | -0.03483
3261.1562 | 117.7917 | -14.5569 | 103.1387 | 0.071489 | -0.072572 | 0.015472 | -0.043331 | 0.059155 | 0.026064 | -0.094765 | -0.13981 | -0.035253 | -0.08205 | -0.074312 | 0.057392 | 0.02322 | -0.04722 | 0.060923 | 0.11726 | -0.026796 | 0.061248 | 0.002445 | 0.10493 | 0.07184 | -0.048989 | -0.094033 | 0.010523 | -0.036274 | -0.028536 | 0.10317 | 0.068996 | -0.001444 | 0.1067 | -0.1972 | -0.092589 | -0.13944 | -0.03483
3262.8594 | 117.7963 | -9.2422 | 108.7372 | 0.06691 | -0.072572 | 0.015472 | -0.043331 | 0.063733 | 0.035221 | -0.090186 | -0.13981 | -0.035253 | -0.086628 | -0.078891 | 0.048236 | 0.032376 | -0.04722 | 0.056344 | 0.11269 | -0.026796 | 0.061248 | 0.002445 | 0.10951 | 0.080997 | -0.04441 | -0.094033 | 0.010523 | -0.040852 | -0.033115 | 0.094012 | 0.078152 | -0.001444 | 0.10212 | -0.18804 | -0.092589 | -0.13486 | -0.039408
3264.6562 | 117.8833 | -10.6476 | 107.0938 | 0.071489 | -0.072572 | 0.006315 | -0.047909 | 0.059155 | 0.021485 | -0.090186 | -0.14439 | -0.030674 | -0.091207 | -0.078891 | 0.057392 | 0.018642 | -0.04722 | 0.060923 | 0.11726 | -0.026796 | 0.052091 | -0.002133 | 0.10493 | 0.067261 | -0.04441 | -0.098611 | 0.015102 | -0.045431 | -0.033115 | 0.10317 | 0.064418 | -0.001444 | 0.1067 | -0.20178 | -0.097167 | -0.1486 | -0.043987
3266.375 | 118.1076 | -8.8257 | 109.0118 | 0.062332 | -0.077151 | 0.015472 | -0.047909 | 0.049999 | 0.026064 | -0.085608 | -0.15354 | -0.026096 | -0.086628 | -0.078891 | 0.057392 | 0.027798 | -0.042641 | 0.065501 | 0.10811 | -0.031375 | 0.061248 | -0.002133 | 0.095775 | 0.07184 | -0.039832 | -0.10777 | 0.01968 | -0.040852 | -0.033115 | 0.10317 | 0.073574 | 0.003135 | 0.11128 | -0.21094 | -0.1109 | -0.14402 | -0.043987
3268.1562 | 117.1188 | -8.7799 | 108.2932 | 0.06691 | -0.072572 | 0.015472 | -0.043331 | 0.059155 | 0.026064 | -0.090186 | -0.13981 | -0.030674 | -0.086628 | -0.065154 | 0.052814 | 0.02322 | -0.04722 | 0.060923 | 0.11269 | -0.026796 | 0.061248 | 0.002445 | 0.10493 | 0.07184 | -0.04441 | -0.094033 | 0.015102 | -0.040852 | -0.019378 | 0.09859 | 0.068996 | -0.001444 | 0.1067 | -0.19262 | -0.092589 | -0.13944 | -0.039408
3269.875 | 118.5928 | -7.9514 | 111.0947 | 0.06691 | -0.067994 | 0.015472 | -0.047909 | 0.059155 | 0.021485 | -0.090186 | -0.14439 | -0.035253 | -0.091207 | -0.074312 | 0.06197 | 0.027798 | -0.042641 | 0.056344 | 0.11269 | -0.022218 | 0.061248 | -0.002133 | 0.10493 | 0.067261 | -0.04441 | -0.098611 | 0.010523 | -0.045431 | -0.028536 | 0.10775 | 0.073574 | 0.003135 | 0.10212 | -0.20636 | -0.10175 | -0.15318 | -0.048566
3271.6562 | 117.8101 | -10.3775 | 107.3639 | 0.06691 | -0.072572 | 0.015472 | -0.043331 | 0.054577 | 0.026064 | -0.090186 | -0.13981 | -0.030674 | -0.08205 | -0.069733 | 0.048236 | 0.018642 | -0.04722 | 0.056344 | 0.11269 | -0.026796 | 0.061248 | 0.002445 | 0.10035 | 0.07184 | -0.04441 | -0.094033 | 0.015102 | -0.036274 | -0.023957 | 0.094012 | 0.064418 | -0.001444 | 0.10212 | -0.18804 | -0.092589 | -0.13029 | -0.03483
3273.375 | 117.8284 | -8.6197 | 109.0256 | 0.071489 | -0.063415 | 0.015472 | -0.043331 | 0.059155 | 0.021485 | -0.094765 | -0.13981 | -0.030674 | -0.077472 | -0.074312 | 0.052814 | 0.02322 | -0.042641 | 0.060923 | 0.11726 | -0.017639 | 0.061248 | 0.002445 | 0.10493 | 0.067261 | -0.048989 | -0.094033 | 0.015102 | -0.031696 | -0.028536 | 0.09859 | 0.068996 | 0.003135 | 0.1067 | -0.19262 | -0.097168 | -0.13029 | -0.034831
3275.1562 | 117.2333 | -15.9897 | 101.0788 | 0.071489 | -0.067994 | 0.020051 | -0.038752 | 0.06831 | 0.026064 | -0.090186 | -0.14439 | -0.035253 | -0.08205 | -0.074312 | 0.052814 | 0.018642 | -0.04722 | 0.056344 | 0.11726 | -0.022218 | 0.065827 | 0.007024 | 0.11409 | 0.07184 | -0.04441 | -0.098611 | 0.010523 | -0.036274 | -0.028536 | 0.09859 | 0.064418 | -0.001444 | 0.10212 | -0.1972 | -0.097167 | -0.13486 | -0.03483
3276.9375 | 118.0115 | -11.3022 | 106.8832 | 0.062332 | -0.067994 | 0.015472 | -0.043331 | 0.054577 | 0.021485 | -0.08103 | -0.14439 | -0.026096 | -0.091207 | -0.074312 | 0.06197 | 0.02322 | -0.04722 | 0.056344 | 0.10811 | -0.022218 | 0.061248 | 0.002445 | 0.10035 | 0.067261 | -0.035254 | -0.098611 | 0.01968 | -0.045431 | -0.028536 | 0.10775 | 0.068996 | -0.001444 | 0.10212 | -0.20636 | -0.097167 | -0.15318 | -0.043987
3278.7188 | 117.5491 | -14.4424 | 102.8687 | 0.071489 | -0.072572 | 0.010893 | -0.052488 | 0.06831 | 0.030642 | -0.090186 | -0.14439 | -0.030674 | -0.08205 | -0.069733 | 0.052814 | 0.014064 | -0.04722 | 0.056344 | 0.11726 | -0.026796 | 0.056669 | -0.006712 | 0.11409 | 0.076418 | -0.04441 | -0.098611 | 0.015102 | -0.036274 | -0.023957 | 0.09859 | 0.05984 | -0.001444 | 0.10212 | -0.1972 | -0.097167 | -0.13486 | -0.03483
3280.4375 | 116.7618 | -7.814 | 107.785 | 0.062332 | -0.077151 | 0.010893 | -0.047909 | 0.054577 | 0.030642 | -0.094765 | -0.13523 | -0.030674 | -0.091207 | -0.074312 | 0.057392 | 0.02322 | -0.042641 | 0.065501 | 0.10811 | -0.031375 | 0.056669 | -0.002133 | 0.10035 | 0.076418 | -0.048989 | -0.089454 | 0.015102 | -0.045431 | -0.028536 | 0.10317 | 0.068996 | 0.003135 | 0.11128 | -0.19262 | -0.092589 | -0.1486 | -0.048566
3282.2188 | 118.0206 | -9.5718 | 108.2108 | 0.062332 | -0.077151 | 0.020051 | -0.052488 | 0.059155 | 0.030642 | -0.099343 | -0.14439 | -0.039832 | -0.086628 | -0.08347 | 0.06197 | 0.018642 | -0.056376 | 0.060923 | 0.10811 | -0.031375 | 0.065827 | -0.006712 | 0.10493 | 0.076418 | -0.053567 | -0.098611 | 0.005944 | -0.040852 | -0.037694 | 0.10775 | 0.064418 | -0.0106 | 0.1067 | -0.20636 | -0.088011 | -0.1486 | -0.030252
3283.9844 | 118.5837 | -2.504 | 115.9653 | 0.057754 | -0.067994 | 0.015472 | -0.047909 | 0.049999 | 0.021485 | -0.094765 | -0.14439 | -0.035253 | -0.086628 | -0.078891 | 0.057392 | 0.02322 | -0.04722 | 0.065501 | 0.10353 | -0.022218 | 0.061248 | -0.002133 | 0.095775 | 0.067261 | -0.048989 | -0.098611 | 0.010523 | -0.040852 | -0.033115 | 0.10317 | 0.068996 | -0.001444 | 0.11128 | -0.20178 | -0.097167 | -0.14402 | -0.039408
3285.7656 | 118.7576 | -5.8319 | 112.9486 | 0.062332 | -0.072572 | 0.015472 | -0.052488 | 0.059155 | 0.016907 | -0.094765 | -0.14439 | -0.030674 | -0.08205 | -0.078891 | 0.06197 | 0.032376 | -0.051798 | 0.065501 | 0.10811 | -0.026796 | 0.061248 | -0.006712 | 0.10493 | 0.062683 | -0.048989 | -0.098611 | 0.015102 | -0.036274 | -0.033115 | 0.10775 | 0.078152 | -0.006022 | 0.11128 | -0.20636 | -0.092589 | -0.14402 | -0.030252
3287.5469 | 119.371 | -0.90179 | 118.5287 | 0.053175 | -0.077151 | 0.006315 | -0.052488 | 0.059155 | 0.016907 | -0.085608 | -0.15354 | -0.026096 | -0.091207 | -0.088049 | 0.06197 | 0.027798 | -0.042641 | 0.070079 | 0.098951 | -0.031375 | 0.052091 | -0.006712 | 0.10493 | 0.062683 | -0.039832 | -0.10777 | 0.01968 | -0.045431 | -0.042273 | 0.10775 | 0.073574 | 0.003135 | 0.11585 | -0.21551 | -0.1109 | -0.15318 | -0.048566
3289.2656 | 119.5679 | -0.76904 | 118.6615 | 0.071489 | -0.08173 | 0.006315 | -0.057066 | 0.054577 | 0.021485 | -0.094765 | -0.14897 | -0.039832 | -0.086628 | -0.069733 | 0.06197 | 0.02322 | -0.038063 | 0.065501 | 0.11726 | -0.035954 | 0.052091 | -0.01129 | 0.10035 | 0.067261 | -0.048989 | -0.10319 | 0.005944 | -0.040852 | -0.023957 | 0.10775 | 0.068996 | 0.007713 | 0.11128 | -0.21094 | -0.1109 | -0.1486 | -0.048565
3291.0469 | 119.3344 | -1.3275 | 118.0618 | 0.062332 | -0.072572 | 0.010893 | -0.047909 | 0.059155 | 0.021485 | -0.094765 | -0.14897 | -0.039832 | -0.091207 | -0.078891 | 0.06197 | 0.027798 | -0.042641 | 0.074657 | 0.10811 | -0.026796 | 0.056669 | -0.002133 | 0.10493 | 0.067261 | -0.048989 | -0.10319 | 0.005944 | -0.045431 | -0.033115 | 0.10775 | 0.073574 | 0.003135 | 0.12043 | -0.21094 | -0.10632 | -0.15318 | -0.048566
3292.8281 | 119.6869 | -0.84686 | 118.7439 | 0.06691 | -0.08173 | 0.010893 | -0.057066 | 0.045421 | 0.026064 | -0.090186 | -0.14897 | -0.035253 | -0.091207 | -0.08347 | 0.057392 | 0.02322 | -0.04722 | 0.065501 | 0.11269 | -0.035954 | 0.056669 | -0.01129 | 0.091197 | 0.07184 | -0.04441 | -0.10319 | 0.010523 | -0.045431 | -0.037694 | 0.10317 | 0.068996 | -0.001444 | 0.11128 | -0.20636 | -0.10175 | -0.1486 | -0.043987
3294.6094 | 119.7647 | -0.99792 | 118.602 | 0.06691 | -0.077151 | 0.010893 | -0.052488 | 0.054577 | 0.021485 | -0.094765 | -0.14897 | -0.039832 | -0.086628 | -0.08347 | 0.066548 | 0.02322 | -0.042641 | 0.065501 | 0.11269 | -0.031375 | 0.056669 | -0.006712 | 0.10035 | 0.067261 | -0.048989 | -0.10319 | 0.005944 | -0.040852 | -0.037694 | 0.11232 | 0.068996 | 0.003135 | 0.11128 | -0.21551 | -0.10632 | -0.15318 | -0.043987
3296.3906 | 119.8425 | -0.81024 | 118.9178 | 0.057754 | -0.077151 | 0.010893 | -0.047909 | 0.054577 | 0.021485 | -0.085608 | -0.15354 | -0.039832 | -0.091207 | -0.08347 | 0.066548 | 0.032376 | -0.042641 | 0.070079 | 0.10353 | -0.031375 | 0.056669 | -0.002133 | 0.10035 | 0.067261 | -0.039832 | -0.10777 | 0.005944 | -0.045431 | -0.037694 | 0.11232 | 0.078152 | 0.003135 | 0.11585 | -0.22009 | -0.1109 | -0.15775 | -0.048566
3298.0938 | 119.9066 | -0.78735 | 118.9316 | 0.06691 | -0.077151 | 0.010893 | -0.047909 | 0.054577 | 0.016907 | -0.090186 | -0.14897 | -0.035253 | -0.086628 | -0.088049 | 0.06197 | 0.032376 | -0.033484 | 0.074657 | 0.11269 | -0.031375 | 0.056669 | -0.002133 | 0.10035 | 0.062683 | -0.04441 | -0.10319 | 0.010523 | -0.040852 | -0.042273 | 0.10775 | 0.078152 | 0.012292 | 0.12043 | -0.21094 | -0.11548 | -0.1486 | -0.053144
3299.875 | 119.8013 | -0.85602 | 119.0277 | 0.076067 | -0.077151 | 0.006315 | -0.047909 | 0.059155 | 0.026064 | -0.094765 | -0.14439 | -0.044411 | -0.091207 | -0.078891 | 0.06197 | 0.027798 | -0.04722 | 0.070079 | 0.12184 | -0.031375 | 0.052091 | -0.002133 | 0.10493 | 0.07184 | -0.048989 | -0.098611 | 0.001365 | -0.045431 | -0.033115 | 0.10775 | 0.073574 | -0.001444 | 0.11585 | -0.20636 | -0.097167 | -0.15318 | -0.043987
3301.6094 | 119.8563 | -0.86517 | 119.0781 | 0.057754 | -0.077151 | 0.015472 | -0.052488 | 0.054577 | 0.016907 | -0.090186 | -0.14897 | -0.035253 | -0.091207 | -0.078891 | 0.06197 | 0.032376 | -0.04722 | 0.060923 | 0.10353 | -0.031375 | 0.061248 | -0.006712 | 0.10035 | 0.062683 | -0.04441 | -0.10319 | 0.010523 | -0.045431 | -0.033115 | 0.10775 | 0.078152 | -0.001444 | 0.1067 | -0.21094 | -0.10175 | -0.15318 | -0.043987
3303.3906 | 119.9158 | -0.86975 | 119.1284 | 0.057754 | -0.08173 | 0.006315 | -0.043331 | 0.054577 | 0.026064 | -0.090186 | -0.14897 | -0.039832 | -0.091207 | -0.088049 | 0.052814 | 0.02322 | -0.04722 | 0.070079 | 0.10353 | -0.035954 | 0.052091 | 0.002445 | 0.10035 | 0.07184 | -0.04441 | -0.10319 | 0.005944 | -0.045431 | -0.042273 | 0.09859 | 0.068996 | -0.001444 | 0.11585 | -0.20178 | -0.10175 | -0.14402 | -0.043987
3305.125 | 119.9707 | -0.90637 | 119.1147 | 0.062332 | -0.086309 | 0.010893 | -0.052488 | 0.059155 | 0.016907 | -0.085608 | -0.15812 | -0.035253 | -0.086628 | -0.08347 | 0.06197 | 0.027798 | -0.04722 | 0.065501 | 0.10811 | -0.040533 | 0.056669 | -0.006712 | 0.10493 | 0.062683 | -0.039832 | -0.11235 | 0.010523 | -0.040852 | -0.037694 | 0.10775 | 0.073574 | -0.001444 | 0.11128 | -0.22009 | -0.1109 | -0.1486 | -0.039408
3306.9062 | 120.0943 | -0.83771 | 119.1238 | 0.06691 | -0.08173 | 0.006315 | -0.047909 | 0.054577 | 0.021485 | -0.090186 | -0.14897 | -0.039832 | -0.091207 | -0.078891 | 0.06197 | 0.036954 | -0.04722 | 0.065501 | 0.11269 | -0.035954 | 0.052091 | -0.002133 | 0.10035 | 0.067261 | -0.04441 | -0.10319 | 0.005944 | -0.045431 | -0.033115 | 0.10775 | 0.08273 | -0.001444 | 0.11128 | -0.21094 | -0.10175 | -0.15318 | -0.043987
3308.625 | 120.0394 | -0.89264 | 119.1696 | 0.062332 | -0.072572 | 0.010893 | -0.052488 | 0.054577 | 0.021485 | -0.085608 | -0.14897 | -0.044411 | -0.091207 | -0.08347 | 0.066548 | 0.032376 | -0.042641 | 0.060923 | 0.10811 | -0.026796 | 0.056669 | -0.006712 | 0.10035 | 0.067261 | -0.039832 | -0.10319 | 0.001365 | -0.045431 | -0.037694 | 0.11232 | 0.078152 | 0.003135 | 0.1067 | -0.21551 | -0.10632 | -0.15775 | -0.048566
3310.4062 | 120.1859 | -0.86975 | 119.1925 | 0.062332 | -0.077151 | 0.001736 | -0.043331 | 0.054577 | 0.016907 | -0.094765 | -0.15354 | -0.044411 | -0.091207 | -0.08347 | 0.06197 | 0.027798 | -0.042641 | 0.074657 | 0.10811 | -0.031375 | 0.047512 | 0.002445 | 0.10035 | 0.062683 | -0.048989 | -0.10777 | 0.001365 | -0.045431 | -0.037694 | 0.10775 | 0.073574 | 0.003135 | 0.12043 | -0.21551 | -0.1109 | -0.15318 | -0.048566
3312.125 | 120.1172 | -0.90179 | 119.2657 | 0.062332 | -0.08173 | 0.006315 | -0.052488 | 0.049999 | 0.016907 | -0.099343 | -0.15354 | -0.044411 | -0.086628 | -0.088049 | 0.06197 | 0.027798 | -0.04722 | 0.065501 | 0.10811 | -0.035954 | 0.052091 | -0.006712 | 0.095775 | 0.062683 | -0.053567 | -0.10777 | 0.001365 | -0.040852 | -0.042273 | 0.10775 | 0.073574 | -0.001444 | 0.11128 | -0.21551 | -0.10632 | -0.1486 | -0.039408
3313.9062 | 120.1813 | -0.92926 | 119.2657 | 0.062332 | -0.08173 | 0.006315 | -0.047909 | 0.045421 | 0.021485 | -0.085608 | -0.14897 | -0.026096 | -0.086628 | -0.088049 | 0.06197 | 0.027798 | -0.051798 | 0.065501 | 0.10811 | -0.035954 | 0.052091 | -0.002133 | 0.091197 | 0.067261 | -0.039832 | -0.10319 | 0.01968 | -0.040852 | -0.042273 | 0.10775 | 0.073574 | -0.006022 | 0.11128 | -0.21094 | -0.097168 | -0.1486 | -0.03483
3315.7031 | 120.3186 | -0.90637 | 119.2566 | 0.053175 | -0.077151 | 0.010893 | -0.052488 | 0.063733 | 0.021485 | -0.094765 | -0.14897 | -0.044411 | -0.091207 | -0.078891 | 0.06197 | 0.02322 | -0.042641 | 0.070079 | 0.098951 | -0.031375 | 0.056669 | -0.006712 | 0.10951 | 0.067261 | -0.048989 | -0.10319 | 0.001365 | -0.045431 | -0.033115 | 0.10775 | 0.068996 | 0.003135 | 0.11585 | -0.21094 | -0.10632 | -0.15318 | -0.048566
3317.4688 | 120.3003 | -0.93384 | 119.2612 | 0.062332 | -0.086309 | 0.020051 | -0.043331 | 0.059155 | 0.021485 | -0.094765 | -0.15354 | -0.039832 | -0.091207 | -0.074312 | 0.057392 | 0.02322 | -0.04722 | 0.070079 | 0.10811 | -0.040533 | 0.065827 | 0.002445 | 0.10493 | 0.067261 | -0.048989 | -0.10777 | 0.005944 | -0.045431 | -0.028536 | 0.10317 | 0.068996 | -0.001444 | 0.11585 | -0.21094 | -0.10632 | -0.1486 | -0.043987
3319.2031 | 120.3781 | -0.95673 | 119.2886 | 0.062332 | -0.077151 | 0.020051 | -0.038752 | 0.049999 | 0.016907 | -0.090186 | -0.14897 | -0.035253 | -0.086628 | -0.08347 | 0.06197 | 0.032376 | -0.04722 | 0.074657 | 0.10811 | -0.031375 | 0.065827 | 0.007024 | 0.095775 | 0.062683 | -0.04441 | -0.10319 | 0.010523 | -0.040852 | -0.037694 | 0.10775 | 0.078152 | -0.001444 | 0.12043 | -0.21094 | -0.10175 | -0.1486 | -0.039408
3320.9844 | 120.2957 | -1.0071 | 119.339 | 0.057754 | -0.072572 | 0.010893 | -0.047909 | 0.054577 | 0.021485 | -0.090186 | -0.15354 | -0.044411 | -0.091207 | -0.078891 | 0.06197 | 0.027798 | -0.042641 | 0.056344 | 0.10353 | -0.026796 | 0.056669 | -0.002133 | 0.10035 | 0.067261 | -0.04441 | -0.10777 | 0.001365 | -0.045431 | -0.033115 | 0.10775 | 0.073574 | 0.003135 | 0.10212 | -0.21551 | -0.1109 | -0.15318 | -0.048566
3322.7656 | 120.4605 | -0.97961 | 119.2932 | 0.057754 | -0.072572 | 0.001736 | -0.052488 | 0.049999 | 0.021485 | -0.094765 | -0.15812 | -0.039832 | -0.086628 | -0.08347 | 0.057392 | 0.032376 | -0.04722 | 0.065501 | 0.10353 | -0.026796 | 0.047512 | -0.006712 | 0.095775 | 0.067261 | -0.048989 | -0.11235 | 0.005944 | -0.040852 | -0.037694 | 0.10317 | 0.078152 | -0.001444 | 0.11128 | -0.21552 | -0.1109 | -0.14402 | -0.039408
3324.5469 | 120.4788 | -0.97961 | 119.3527 | 0.06691 | -0.077151 | 0.010893 | -0.047909 | 0.054577 | 0.012329 | -0.085608 | -0.14897 | -0.035253 | -0.086628 | -0.08347 | 0.057392 | 0.032376 | -0.04722 | 0.065501 | 0.11269 | -0.031375 | 0.056669 | -0.002133 | 0.10035 | 0.058105 | -0.039832 | -0.10319 | 0.010523 | -0.040852 | -0.037694 | 0.10317 | 0.078152 | -0.001444 | 0.11128 | -0.20636 | -0.10175 | -0.14402 | -0.039408
3326.3438 | 120.369 | -1.0208 | 119.3939 | 0.062332 | -0.086309 | 0.006315 | -0.038752 | 0.049999 | 0.021485 | -0.090186 | -0.15354 | -0.039832 | -0.08205 | -0.074312 | 0.066548 | 0.027798 | -0.04722 | 0.070079 | 0.10811 | -0.040533 | 0.052091 | 0.007024 | 0.095775 | 0.067261 | -0.04441 | -0.10777 | 0.005944 | -0.036274 | -0.028536 | 0.11232 | 0.073574 | -0.001444 | 0.11585 | -0.22009 | -0.10632 | -0.1486 | -0.03483
3328.0469 | 120.3918 | -1.0254 | 119.4077 | 0.057754 | -0.072572 | 0.010893 | -0.047909 | 0.054577 | 0.021485 | -0.090186 | -0.14897 | -0.030674 | -0.095785 | -0.078891 | 0.066548 | 0.02322 | -0.042641 | 0.065501 | 0.10353 | -0.026796 | 0.056669 | -0.002133 | 0.10035 | 0.067261 | -0.04441 | -0.10319 | 0.015102 | -0.050009 | -0.033115 | 0.11232 | 0.068996 | 0.003135 | 0.11128 | -0.21551 | -0.10632 | -0.16233 | -0.053144
3329.8281 | 120.4651 | -3.3463 | 117.0547 | 0.071489 | -0.072572 | 0.015472 | -0.038752 | 0.049999 | 0.026064 | -0.085608 | -0.14897 | -0.035253 | -0.086628 | -0.08347 | 0.066548 | 0.02322 | -0.04722 | 0.056344 | 0.11726 | -0.026796 | 0.061248 | 0.007024 | 0.095775 | 0.07184 | -0.039832 | -0.10319 | 0.010523 | -0.040852 | -0.037694 | 0.11232 | 0.068996 | -0.001444 | 0.10212 | -0.21551 | -0.10175 | -0.15318 | -0.039408
3331.5469 | 120.4056 | -5.2917 | 115.1093 | 0.06691 | -0.072572 | 0.010893 | -0.043331 | 0.054577 | 0.030642 | -0.085608 | -0.14897 | -0.035253 | -0.091207 | -0.078891 | 0.06197 | 0.018642 | -0.051798 | 0.060923 | 0.11269 | -0.026796 | 0.056669 | 0.002445 | 0.10035 | 0.076418 | -0.039832 | -0.10319 | 0.010523 | -0.045431 | -0.033115 | 0.10775 | 0.064418 | -0.006022 | 0.1067 | -0.21094 | -0.097168 | -0.15318 | -0.039409
3333.3125 | 120.433 | -6.459 | 113.9648 | 0.06691 | -0.077151 | 0.015472 | -0.043331 | 0.059155 | 0.026064 | -0.085608 | -0.14439 | -0.035253 | -0.08205 | -0.08347 | 0.057392 | 0.027798 | -0.04722 | 0.060923 | 0.11269 | -0.031375 | 0.061248 | 0.002445 | 0.10493 | 0.07184 | -0.039832 | -0.098611 | 0.010523 | -0.036274 | -0.037694 | 0.10317 | 0.073574 | -0.001444 | 0.1067 | -0.20178 | -0.097167 | -0.13944 | -0.03483
3335.0156 | 120.5292 | -7.6355 | 112.7151 | 0.071489 | -0.072572 | 0.015472 | -0.052488 | 0.063733 | 0.021485 | -0.090186 | -0.14439 | -0.026096 | -0.086628 | -0.074312 | 0.057392 | 0.027798 | -0.04722 | 0.060923 | 0.11726 | -0.026796 | 0.061248 | -0.006712 | 0.10951 | 0.067261 | -0.04441 | -0.098611 | 0.01968 | -0.040852 | -0.028536 | 0.10317 | 0.073574 | -0.001444 | 0.1067 | -0.20178 | -0.097167 | -0.14402 | -0.039408
3336.8125 | 120.4285 | -6.9855 | 113.443 | 0.062332 | -0.077151 | 0.006315 | -0.043331 | 0.059155 | 0.026064 | -0.085608 | -0.13981 | -0.030674 | -0.077472 | -0.078891 | 0.052814 | 0.02322 | -0.042641 | 0.060923 | 0.10811 | -0.031375 | 0.052091 | 0.002445 | 0.10493 | 0.07184 | -0.039832 | -0.094033 | 0.015102 | -0.031696 | -0.033115 | 0.09859 | 0.068996 | 0.003135 | 0.1067 | -0.19262 | -0.097168 | -0.13029 | -0.034831
3338.5938 | 120.4788 | -6.5186 | 113.9648 | 0.057754 | -0.067994 | 0.020051 | -0.038752 | 0.063733 | 0.026064 | -0.076452 | -0.13981 | -0.035253 | -0.08205 | -0.078891 | 0.052814 | 0.027798 | -0.051798 | 0.060923 | 0.10353 | -0.022218 | 0.065827 | 0.007024 | 0.10951 | 0.07184 | -0.030676 | -0.094033 | 0.010523 | -0.036274 | -0.033115 | 0.09859 | 0.073574 | -0.006022 | 0.1067 | -0.19262 | -0.088011 | -0.13486 | -0.030252
3340.375 | 120.4788 | -10.08 | 110.408 | 0.06691 | -0.067994 | 0.020051 | -0.038752 | 0.059155 | 0.026064 | -0.090186 | -0.13523 | -0.039832 | -0.08205 | -0.074312 | 0.057392 | 0.02322 | -0.04722 | 0.060923 | 0.11269 | -0.022218 | 0.065827 | 0.007024 | 0.10493 | 0.07184 | -0.04441 | -0.089454 | 0.005944 | -0.036274 | -0.028536 | 0.10317 | 0.068996 | -0.001444 | 0.1067 | -0.19262 | -0.08801 | -0.13944 | -0.03483
3342.1094 | 120.6116 | -11.618 | 108.6823 | 0.071489 | -0.067994 | 0.015472 | -0.038752 | 0.063733 | 0.035221 | -0.08103 | -0.13523 | -0.035253 | -0.072894 | -0.069733 | 0.052814 | 0.014064 | -0.04722 | 0.056344 | 0.11726 | -0.022218 | 0.061248 | 0.007024 | 0.10951 | 0.080997 | -0.035254 | -0.089454 | 0.010523 | -0.027118 | -0.023957 | 0.09859 | 0.05984 | -0.001444 | 0.10212 | -0.18804 | -0.08801 | -0.12571 | -0.025674
3343.875 | 120.4468 | -16.4795 | 103.8757 | 0.071489 | -0.067994 | 0.024629 | -0.029595 | 0.059155 | 0.035221 | -0.08103 | -0.12607 | -0.030674 | -0.072894 | -0.074312 | 0.048236 | 0.018642 | -0.056376 | 0.051766 | 0.11726 | -0.022218 | 0.070405 | 0.016181 | 0.10493 | 0.080997 | -0.035254 | -0.080297 | 0.015102 | -0.027118 | -0.028536 | 0.094012 | 0.064418 | -0.0106 | 0.097542 | -0.17431 | -0.069697 | -0.12113 | -0.016518
3345.6562 | 120.5154 | -11.7828 | 108.5449 | 0.06691 | -0.067994 | 0.010893 | -0.043331 | 0.063733 | 0.035221 | -0.085608 | -0.14439 | -0.026096 | -0.077472 | -0.069733 | 0.057392 | 0.018642 | -0.042641 | 0.056344 | 0.11269 | -0.022218 | 0.056669 | 0.002445 | 0.10951 | 0.080997 | -0.039832 | -0.098611 | 0.01968 | -0.031696 | -0.023957 | 0.10317 | 0.064418 | 0.003135 | 0.10212 | -0.20178 | -0.10175 | -0.13486 | -0.034831
3347.3594 | 120.4697 | -16.0629 | 104.2282 | 0.076067 | -0.063415 | 0.029208 | -0.038752 | 0.06831 | 0.035221 | -0.085608 | -0.13065 | -0.026096 | -0.08205 | -0.065154 | 0.043657 | 0.018642 | -0.04722 | 0.056344 | 0.12184 | -0.017639 | 0.074984 | 0.007024 | 0.11409 | 0.080997 | -0.039832 | -0.084876 | 0.01968 | -0.036274 | -0.019378 | 0.089433 | 0.064418 | -0.001444 | 0.10212 | -0.17431 | -0.083432 | -0.12571 | -0.03483
3349.1406 | 120.575 | -6.5048 | 113.9465 | 0.062332 | -0.072572 | 0.015472 | -0.047909 | 0.059155 | 0.021485 | -0.085608 | -0.15354 | -0.030674 | -0.08205 | -0.069733 | 0.06197 | 0.027798 | -0.04722 | 0.065501 | 0.10811 | -0.026796 | 0.061248 | -0.002133 | 0.10493 | 0.067261 | -0.039832 | -0.10777 | 0.015102 | -0.036274 | -0.023957 | 0.10775 | 0.073574 | -0.001444 | 0.11128 | -0.21551 | -0.10632 | -0.14402 | -0.03483
3350.9062 | 120.5292 | -5.6946 | 114.8529 | 0.071489 | -0.067994 | 0.020051 | -0.047909 | 0.059155 | 0.030642 | -0.090186 | -0.13981 | -0.035253 | -0.086628 | -0.078891 | 0.057392 | 0.032376 | -0.051798 | 0.060923 | 0.11726 | -0.022218 | 0.065827 | -0.002133 | 0.10493 | 0.076418 | -0.04441 | -0.094033 | 0.010523 | -0.040852 | -0.033115 | 0.10317 | 0.078152 | -0.006022 | 0.1067 | -0.1972 | -0.088011 | -0.14402 | -0.03483
3352.625 | 120.5704 | -7.1503 | 113.3835 | 0.06691 | -0.072572 | 0.015472 | -0.047909 | 0.063733 | 0.021485 | -0.08103 | -0.14439 | -0.039832 | -0.086628 | -0.069733 | 0.052814 | 0.02322 | -0.04722 | 0.060923 | 0.11269 | -0.026796 | 0.061248 | -0.002133 | 0.10951 | 0.067261 | -0.035254 | -0.098611 | 0.005944 | -0.040852 | -0.023957 | 0.09859 | 0.068996 | -0.001444 | 0.1067 | -0.1972 | -0.097167 | -0.13944 | -0.039408
3354.4062 | 120.4926 | -15.3946 | 105.0613 | 0.085224 | -0.063415 | 0.020051 | -0.047909 | 0.06831 | 0.030642 | -0.08103 | -0.13981 | -0.021517 | -0.072894 | -0.065154 | 0.048236 | 0.018642 | -0.051798 | 0.056344 | 0.131 | -0.017639 | 0.065827 | -0.002133 | 0.11409 | 0.076418 | -0.035254 | -0.094033 | 0.024259 | -0.027118 | -0.019378 | 0.094012 | 0.064418 | -0.006022 | 0.10212 | -0.18804 | -0.088011 | -0.12113 | -0.021096
3356.1406 | 120.5109 | -8.9172 | 111.5845 | 0.076067 | -0.058836 | 0.015472 | -0.038752 | 0.063733 | 0.030642 | -0.090186 | -0.13523 | -0.026096 | -0.08205 | -0.074312 | 0.057392 | 0.014064 | -0.051798 | 0.056344 | 0.12184 | -0.01306 | 0.061248 | 0.007024 | 0.10951 | 0.076418 | -0.04441 | -0.089454 | 0.01968 | -0.036274 | -0.028536 | 0.10317 | 0.05984 | -0.006022 | 0.10212 | -0.19262 | -0.083432 | -0.13944 | -0.030252
3357.9062 | 120.4468 | -28.1708 | 91.9235 | 0.085224 | -0.049678 | 0.029208 | -0.025017 | 0.082044 | 0.044377 | -0.071874 | -0.12607 | -0.00778 | -0.063737 | -0.055996 | 0.034501 | 0.004908 | -0.051798 | 0.04261 | 0.131 | -0.003902 | 0.074984 | 0.020759 | 0.12782 | 0.090153 | -0.026098 | -0.080297 | 0.037996 | -0.017961 | -0.01022 | 0.080277 | 0.050684 | -0.006022 | 0.088386 | -0.16057 | -0.074275 | -0.098238 | -0.011939
3359.6875 | 120.3232 | -33.4671 | 86.5173 | 0.094381 | -0.0451 | 0.038365 | -0.020438 | 0.082044 | 0.053534 | -0.062717 | -0.11692 | -0.012359 | -0.059159 | -0.042259 | 0.029923 | 0.00033 | -0.051798 | 0.033454 | 0.14016 | 0.000676 | 0.084141 | 0.025338 | 0.12782 | 0.09931 | -0.016941 | -0.07114 | 0.033417 | -0.013383 | 0.003517 | 0.075699 | 0.046106 | -0.006022 | 0.07923 | -0.14684 | -0.065118 | -0.089082 | -0.007361
3361.4688 | 120.4239 | -31.3477 | 88.6597 | 0.094381 | -0.049678 | 0.038365 | -0.025017 | 0.072888 | 0.035221 | -0.062717 | -0.13065 | -0.012359 | -0.068315 | -0.055996 | 0.034501 | 0.004908 | -0.051798 | 0.04261 | 0.14016 | -0.003902 | 0.084141 | 0.020759 | 0.11866 | 0.080997 | -0.016941 | -0.084876 | 0.033417 | -0.022539 | -0.01022 | 0.080277 | 0.050684 | -0.006022 | 0.088386 | -0.16515 | -0.078854 | -0.10282 | -0.016517
3363.1875 | 120.4559 | -14.5981 | 105.5603 | 0.076067 | -0.063415 | 0.024629 | -0.038752 | 0.06831 | 0.030642 | -0.076452 | -0.13523 | -0.026096 | -0.072894 | -0.065154 | 0.039079 | 0.009486 | -0.042641 | 0.051766 | 0.12184 | -0.017639 | 0.070405 | 0.007024 | 0.11409 | 0.076418 | -0.030676 | -0.089454 | 0.01968 | -0.027118 | -0.019378 | 0.084855 | 0.055262 | 0.003135 | 0.097542 | -0.17431 | -0.092589 | -0.11197 | -0.030253
3364.9531 | 120.4147 | -21.2997 | 98.9365 | 0.076067 | -0.058836 | 0.033786 | -0.038752 | 0.077466 | 0.039799 | -0.067295 | -0.13065 | -0.021517 | -0.072894 | -0.065154 | 0.039079 | 0.009486 | -0.04722 | 0.056344 | 0.12184 | -0.01306 | 0.079562 | 0.007024 | 0.12324 | 0.085575 | -0.021519 | -0.084876 | 0.024259 | -0.027118 | -0.019378 | 0.084855 | 0.055262 | -0.001444 | 0.10212 | -0.16973 | -0.083432 | -0.11197 | -0.025674
3366.75 | 120.575 | -11.8103 | 108.5266 | 0.071489 | -0.072572 | 0.020051 | -0.038752 | 0.06831 | 0.026064 | -0.071874 | -0.13981 | -0.026096 | -0.072894 | -0.069733 | 0.048236 | 0.02322 | -0.051798 | 0.056344 | 0.11726 | -0.026796 | 0.065827 | 0.007024 | 0.11409 | 0.07184 | -0.026098 | -0.094033 | 0.01968 | -0.027118 | -0.023957 | 0.094012 | 0.068996 | -0.006022 | 0.10212 | -0.18804 | -0.088011 | -0.12113 | -0.021096
3368.4688 | 120.3964 | -15.5731 | 104.8462 | 0.080646 | -0.054257 | 0.033786 | -0.029595 | 0.06831 | 0.030642 | -0.08103 | -0.13523 | -0.026096 | -0.072894 | -0.060575 | 0.043657 | 0.009486 | -0.051798 | 0.038032 | 0.12642 | -0.008481 | 0.079562 | 0.016181 | 0.11409 | 0.076418 | -0.035254 | -0.089454 | 0.01968 | -0.027118 | -0.014799 | 0.089433 | 0.055262 | -0.006022 | 0.083808 | -0.17889 | -0.083432 | -0.11655 | -0.021096
3370.25 | 120.0714 | -44.7372 | 75.0458 | 0.10354 | -0.022205 | 0.052101 | -0.011281 | 0.10036 | 0.062691 | -0.048983 | -0.10318 | 0.010535 | -0.045424 | -0.03768 | 0.016188 | -0.022561 | -0.051798 | 0.028875 | 0.14931 | 0.023571 | 0.097877 | 0.034495 | 0.14613 | 0.10847 | -0.003207 | -0.057405 | 0.056311 | 0.000352 | 0.008096 | 0.061964 | 0.023215 | -0.006022 | 0.074651 | -0.11937 | -0.051383 | -0.061612 | 0.006374
3372.0312 | 120.5017 | -0.27466 | 120.2362 | 0.076067 | -0.058836 | 0.010893 | -0.034174 | 0.063733 | 0.026064 | -0.094765 | -0.13981 | -0.035253 | -0.086628 | -0.078891 | 0.057392 | 0.027798 | -0.04722 | 0.065501 | 0.12184 | -0.01306 | 0.056669 | 0.011602 | 0.10951 | 0.07184 | -0.048989 | -0.094033 | 0.010523 | -0.040852 | -0.033115 | 0.10317 | 0.073574 | -0.001444 | 0.11128 | -0.1972 | -0.092589 | -0.14402 | -0.039408
3373.8125 | 120.607 | -0.28839 | 120.4285 | 0.06691 | -0.067994 | 0.015472 | -0.038752 | 0.059155 | 0.021485 | -0.085608 | -0.14439 | -0.039832 | -0.077472 | -0.069733 | 0.052814 | 0.018642 | -0.042641 | 0.065501 | 0.11269 | -0.022218 | 0.061248 | 0.007024 | 0.10493 | 0.067261 | -0.039832 | -0.098611 | 0.005944 | -0.031696 | -0.023957 | 0.09859 | 0.064418 | 0.003135 | 0.11128 | -0.1972 | -0.10175 | -0.13029 | -0.034831
3375.5312 | 120.7306 | -0.24719 | 120.433 | 0.071489 | -0.072572 | 0.010893 | -0.047909 | 0.059155 | 0.026064 | -0.085608 | -0.13981 | -0.035253 | -0.08205 | -0.074312 | 0.057392 | 0.018642 | -0.04722 | 0.060923 | 0.11726 | -0.026796 | 0.056669 | -0.002133 | 0.10493 | 0.07184 | -0.039832 | -0.094033 | 0.010523 | -0.036274 | -0.028536 | 0.10317 | 0.064418 | -0.001444 | 0.1067 | -0.1972 | -0.092589 | -0.13944 | -0.03483
3377.3281 | 120.6802 | -0.28381 | 120.5292 | 0.071489 | -0.067994 | 0.010893 | -0.047909 | 0.063733 | 0.026064 | -0.090186 | -0.13981 | -0.035253 | -0.08205 | -0.074312 | 0.06197 | 0.027798 | -0.051798 | 0.060923 | 0.11726 | -0.022218 | 0.056669 | -0.002133 | 0.10951 | 0.07184 | -0.04441 | -0.094033 | 0.010523 | -0.036274 | -0.028536 | 0.10775 | 0.073574 | -0.006022 | 0.1067 | -0.20178 | -0.088011 | -0.14402 | -0.030252
3379.0938 | 120.7855 | -0.26093 | 120.5612 | 0.071489 | -0.072572 | 0.006315 | -0.043331 | 0.063733 | 0.030642 | -0.094765 | -0.14439 | -0.030674 | -0.091207 | -0.078891 | 0.06197 | 0.027798 | -0.04722 | 0.060923 | 0.11726 | -0.026796 | 0.052091 | 0.002445 | 0.10951 | 0.076418 | -0.048989 | -0.098611 | 0.015102 | -0.045431 | -0.033115 | 0.10775 | 0.073574 | -0.001444 | 0.1067 | -0.20636 | -0.097167 | -0.15318 | -0.043987
3380.875 | 120.8954 | -0.23804 | 120.5154 | 0.062332 | -0.067994 | 0.010893 | -0.043331 | 0.059155 | 0.026064 | -0.08103 | -0.14439 | -0.030674 | -0.086628 | -0.078891 | 0.06197 | 0.018642 | -0.042641 | 0.056344 | 0.10811 | -0.022218 | 0.056669 | 0.002445 | 0.10493 | 0.07184 | -0.035254 | -0.098611 | 0.015102 | -0.040852 | -0.033115 | 0.10775 | 0.064418 | 0.003135 | 0.10212 | -0.20636 | -0.10175 | -0.1486 | -0.043987
3382.6562 | 120.8817 | -0.24719 | 120.5933 | 0.071489 | -0.058836 | 0.020051 | -0.043331 | 0.054577 | 0.026064 | -0.090186 | -0.14897 | -0.035253 | -0.08205 | -0.074312 | 0.052814 | 0.018642 | -0.038063 | 0.060923 | 0.11726 | -0.01306 | 0.065827 | 0.002445 | 0.10035 | 0.07184 | -0.04441 | -0.10319 | 0.010523 | -0.036274 | -0.028536 | 0.09859 | 0.064418 | 0.007713 | 0.1067 | -0.20178 | -0.1109 | -0.13486 | -0.043987
3384.4375 | 120.8359 | -0.27466 | 120.5887 | 0.071489 | -0.067994 | 0.010893 | -0.043331 | 0.059155 | 0.030642 | -0.08103 | -0.14439 | -0.035253 | -0.077472 | -0.074312 | 0.06197 | 0.02322 | -0.042641 | 0.070079 | 0.11726 | -0.022218 | 0.056669 | 0.002445 | 0.10493 | 0.076418 | -0.035254 | -0.098611 | 0.010523 | -0.031696 | -0.028536 | 0.10775 | 0.068996 | 0.003135 | 0.11585 | -0.20636 | -0.10175 | -0.13944 | -0.034831
3386.2344 | 120.9824 | -0.24719 | 120.5566 | 0.071489 | -0.058836 | 0.006315 | -0.043331 | 0.063733 | 0.026064 | -0.085608 | -0.14897 | -0.035253 | -0.091207 | -0.08347 | 0.052814 | 0.027798 | -0.042641 | 0.060923 | 0.11726 | -0.01306 | 0.052091 | 0.002445 | 0.10951 | 0.07184 | -0.039832 | -0.10319 | 0.010523 | -0.045431 | -0.037694 | 0.09859 | 0.073574 | 0.003135 | 0.1067 | -0.20178 | -0.10632 | -0.14402 | -0.048566
3387.9375 | 120.9366 | -0.24719 | 120.5978 | 0.071489 | -0.067994 | 0.010893 | -0.047909 | 0.059155 | 0.021485 | -0.085608 | -0.13981 | -0.030674 | -0.091207 | -0.074312 | 0.057392 | 0.027798 | -0.04722 | 0.060923 | 0.11726 | -0.022218 | 0.056669 | -0.002133 | 0.10493 | 0.067261 | -0.039832 | -0.094033 | 0.015102 | -0.045431 | -0.028536 | 0.10317 | 0.073574 | -0.001444 | 0.1067 | -0.1972 | -0.092589 | -0.1486 | -0.043987
3389.7188 | 121.019 | -0.23346 | 120.5933 | 0.062332 | -0.067994 | 0.015472 | -0.038752 | 0.063733 | 0.026064 | -0.090186 | -0.14439 | -0.030674 | -0.077472 | -0.069733 | 0.057392 | 0.02322 | -0.042641 | 0.056344 | 0.10811 | -0.022218 | 0.061248 | 0.007024 | 0.10951 | 0.07184 | -0.04441 | -0.098611 | 0.015102 | -0.031696 | -0.023957 | 0.10317 | 0.068996 | 0.003135 | 0.10212 | -0.20178 | -0.10175 | -0.13486 | -0.034831
3391.4375 | 120.9686 | -0.25635 | 120.6436 | 0.071489 | -0.072572 | 0.015472 | -0.043331 | 0.054577 | 0.021485 | -0.08103 | -0.13981 | -0.039832 | -0.086628 | -0.074312 | 0.06197 | 0.027798 | -0.051798 | 0.060923 | 0.11726 | -0.026796 | 0.061248 | 0.002445 | 0.10035 | 0.067261 | -0.035254 | -0.094033 | 0.005944 | -0.040852 | -0.028536 | 0.10775 | 0.073574 | -0.006022 | 0.1067 | -0.20178 | -0.088011 | -0.1486 | -0.03483
3393.2031 | 121.0098 | -0.24719 | 120.6619 | 0.071489 | -0.072572 | 0.010893 | -0.047909 | 0.06831 | 0.021485 | -0.090186 | -0.13981 | -0.035253 | -0.086628 | -0.069733 | 0.057392 | 0.02322 | -0.042641 | 0.060923 | 0.11726 | -0.026796 | 0.056669 | -0.002133 | 0.11409 | 0.067261 | -0.04441 | -0.094033 | 0.010523 | -0.040852 | -0.023957 | 0.10317 | 0.068996 | 0.003135 | 0.1067 | -0.1972 | -0.097168 | -0.14402 | -0.043987
3394.9688 | 121.0419 | -0.23804 | 120.6619 | 0.071489 | -0.067994 | 0.015472 | -0.038752 | 0.054577 | 0.021485 | -0.085608 | -0.14897 | -0.030674 | -0.068315 | -0.078891 | 0.057392 | 0.02322 | -0.042641 | 0.056344 | 0.11726 | -0.022218 | 0.061248 | 0.007024 | 0.10035 | 0.067261 | -0.039832 | -0.10319 | 0.015102 | -0.022539 | -0.033115 | 0.10317 | 0.068996 | 0.003135 | 0.10212 | -0.20636 | -0.10632 | -0.12571 | -0.025674
3396.7656 | 121.019 | -0.27008 | 120.7169 | 0.062332 | -0.072572 | 0.010893 | -0.043331 | 0.059155 | 0.026064 | -0.085608 | -0.14897 | -0.035253 | -0.08205 | -0.078891 | 0.057392 | 0.018642 | -0.051798 | 0.070079 | 0.10811 | -0.026796 | 0.056669 | 0.002445 | 0.10493 | 0.07184 | -0.039832 | -0.10319 | 0.010523 | -0.036274 | -0.033115 | 0.10317 | 0.064418 | -0.006022 | 0.11585 | -0.20636 | -0.097168 | -0.13944 | -0.030252
3398.5469 | 120.9778 | -0.28381 | 120.7214 | 0.062332 | -0.067994 | 0.015472 | -0.047909 | 0.072888 | 0.021485 | -0.090186 | -0.14439 | -0.035253 | -0.086628 | -0.074312 | 0.057392 | 0.027798 | -0.042641 | 0.065501 | 0.10811 | -0.022218 | 0.061248 | -0.002133 | 0.11866 | 0.067261 | -0.04441 | -0.098611 | 0.010523 | -0.040852 | -0.028536 | 0.10317 | 0.073574 | 0.003135 | 0.11128 | -0.20178 | -0.10175 | -0.14402 | -0.043987
3400.2656 | 121.0419 | -0.25177 | 120.7397 | 0.06691 | -0.067994 | 0.010893 | -0.043331 | 0.059155 | 0.021485 | -0.094765 | -0.13981 | -0.035253 | -0.08205 | -0.069733 | 0.057392 | 0.02322 | -0.042641 | 0.065501 | 0.11269 | -0.022218 | 0.056669 | 0.002445 | 0.10493 | 0.067261 | -0.048989 | -0.094033 | 0.010523 | -0.036274 | -0.023957 | 0.10317 | 0.068996 | 0.003135 | 0.11128 | -0.1972 | -0.097168 | -0.13944 | -0.039409
3402.0469 | 121.0464 | -0.26093 | 120.7672 | 0.076067 | -0.063415 | 0.015472 | -0.038752 | 0.063733 | 0.021485 | -0.090186 | -0.14439 | -0.026096 | -0.077472 | -0.074312 | 0.06197 | 0.02322 | -0.051798 | 0.056344 | 0.12184 | -0.017639 | 0.061248 | 0.007024 | 0.10951 | 0.067261 | -0.04441 | -0.098611 | 0.01968 | -0.031696 | -0.028536 | 0.10775 | 0.068996 | -0.006022 | 0.10212 | -0.20636 | -0.092589 | -0.13944 | -0.025674
3403.8281 | 121.0236 | -0.27466 | 120.7718 | 0.071489 | -0.077151 | 0.010893 | -0.043331 | 0.063733 | 0.026064 | -0.085608 | -0.14439 | -0.035253 | -0.072894 | -0.069733 | 0.057392 | 0.032376 | -0.04722 | 0.060923 | 0.11726 | -0.031375 | 0.056669 | 0.002445 | 0.10951 | 0.07184 | -0.039832 | -0.098611 | 0.010523 | -0.027118 | -0.023957 | 0.10317 | 0.078152 | -0.001444 | 0.1067 | -0.20178 | -0.097167 | -0.13029 | -0.025674
3405.5469 | 121.0236 | -0.28381 | 120.8038 | 0.071489 | -0.067994 | 0.010893 | -0.047909 | 0.06831 | 0.026064 | -0.08103 | -0.13523 | -0.030674 | -0.086628 | -0.074312 | 0.052814 | 0.027798 | -0.04722 | 0.056344 | 0.11726 | -0.022218 | 0.056669 | -0.002133 | 0.11409 | 0.07184 | -0.035254 | -0.089454 | 0.015102 | -0.040852 | -0.028536 | 0.09859 | 0.073574 | -0.001444 | 0.10212 | -0.18804 | -0.08801 | -0.13944 | -0.039408
3407.3281 | 121.0648 | -0.27008 | 120.8405 | 0.06691 | -0.072572 | 0.010893 | -0.043331 | 0.059155 | 0.026064 | -0.090186 | -0.14439 | -0.030674 | -0.08205 | -0.069733 | 0.052814 | 0.018642 | -0.042641 | 0.065501 | 0.11269 | -0.026796 | 0.056669 | 0.002445 | 0.10493 | 0.07184 | -0.04441 | -0.098611 | 0.015102 | -0.036274 | -0.023957 | 0.09859 | 0.064418 | 0.003135 | 0.11128 | -0.1972 | -0.10175 | -0.13486 | -0.039409
3409.0469 | 121.1929 | -0.25177 | 120.7947 | 0.06691 | -0.067994 | 0.010893 | -0.047909 | 0.059155 | 0.026064 | -0.090186 | -0.14439 | -0.026096 | -0.077472 | -0.074312 | 0.057392 | 0.027798 | -0.04722 | 0.060923 | 0.11269 | -0.022218 | 0.056669 | -0.002133 | 0.10493 | 0.07184 | -0.04441 | -0.098611 | 0.01968 | -0.031696 | -0.028536 | 0.10317 | 0.073574 | -0.001444 | 0.1067 | -0.20178 | -0.097167 | -0.13486 | -0.030252
3410.8281 | 121.2067 | -0.25177 | 120.8038 | 0.071489 | -0.067994 | 0.015472 | -0.043331 | 0.054577 | 0.026064 | -0.085608 | -0.13523 | -0.030674 | -0.086628 | -0.074312 | 0.057392 | 0.027798 | -0.04722 | 0.056344 | 0.11726 | -0.022218 | 0.061248 | 0.002445 | 0.10035 | 0.07184 | -0.039832 | -0.089454 | 0.015102 | -0.040852 | -0.028536 | 0.10317 | 0.073574 | -0.001444 | 0.10212 | -0.19262 | -0.08801 | -0.14402 | -0.039408
3412.625 | 121.2021 | -0.25635 | 120.8221 | 0.071489 | -0.067994 | 0.015472 | -0.047909 | 0.063733 | 0.026064 | -0.090186 | -0.13981 | -0.035253 | -0.08205 | -0.074312 | 0.052814 | 0.02322 | -0.051798 | 0.060923 | 0.11726 | -0.022218 | 0.061248 | -0.002133 | 0.10951 | 0.07184 | -0.04441 | -0.094033 | 0.010523 | -0.036274 | -0.028536 | 0.09859 | 0.068996 | -0.006022 | 0.1067 | -0.19262 | -0.088011 | -0.13486 | -0.030252
3414.4062 | 121.1426 | -0.29755 | 120.8633 | 0.06691 | -0.067994 | 0.010893 | -0.043331 | 0.059155 | 0.021485 | -0.090186 | -0.14439 | -0.026096 | -0.077472 | -0.069733 | 0.057392 | 0.02322 | -0.04722 | 0.056344 | 0.11269 | -0.022218 | 0.056669 | 0.002445 | 0.10493 | 0.067261 | -0.04441 | -0.098611 | 0.01968 | -0.031696 | -0.023957 | 0.10317 | 0.068996 | -0.001444 | 0.10212 | -0.20178 | -0.097167 | -0.13486 | -0.030252
3416.125 | 121.106 | -0.28381 | 120.8954 | 0.06691 | -0.067994 | 0.015472 | -0.043331 | 0.059155 | 0.026064 | -0.090186 | -0.13523 | -0.039832 | -0.08205 | -0.078891 | 0.06197 | 0.018642 | -0.038063 | 0.056344 | 0.11269 | -0.022218 | 0.061248 | 0.002445 | 0.10493 | 0.07184 | -0.04441 | -0.089454 | 0.005944 | -0.036274 | -0.033115 | 0.10775 | 0.064418 | 0.007713 | 0.10212 | -0.1972 | -0.097167 | -0.14402 | -0.043987
3417.9219 | 121.1517 | -0.28839 | 120.9229 | 0.06691 | -0.063415 | 0.010893 | -0.047909 | 0.063733 | 0.026064 | -0.085608 | -0.14439 | -0.039832 | -0.08205 | -0.078891 | 0.057392 | 0.027798 | -0.04722 | 0.065501 | 0.11269 | -0.017639 | 0.056669 | -0.002133 | 0.10951 | 0.07184 | -0.039832 | -0.098611 | 0.005944 | -0.036274 | -0.033115 | 0.10317 | 0.073574 | -0.001444 | 0.11128 | -0.20178 | -0.097167 | -0.13944 | -0.03483
3419.7031 | 121.1517 | -0.28839 | 120.9137 | 0.071489 | -0.067994 | 0.015472 | -0.043331 | 0.059155 | 0.021485 | -0.08103 | -0.13981 | -0.035253 | -0.08205 | -0.078891 | 0.066548 | 0.018642 | -0.042641 | 0.065501 | 0.11726 | -0.022218 | 0.061248 | 0.002445 | 0.10493 | 0.067261 | -0.035254 | -0.094033 | 0.010523 | -0.036274 | -0.033115 | 0.11232 | 0.064418 | 0.003135 | 0.11128 | -0.20636 | -0.097168 | -0.1486 | -0.039409
3421.4688 | 121.2387 | -0.24261 | 120.8496 | 0.062332 | -0.067994 | 0.010893 | -0.047909 | 0.063733 | 0.026064 | -0.085608 | -0.14439 | -0.026096 | -0.072894 | -0.078891 | 0.057392 | 0.02322 | -0.042641 | 0.065501 | 0.10811 | -0.022218 | 0.056669 | -0.002133 | 0.10951 | 0.07184 | -0.039832 | -0.098611 | 0.01968 | -0.027118 | -0.033115 | 0.10317 | 0.068996 | 0.003135 | 0.11128 | -0.20178 | -0.10175 | -0.13029 | -0.030253
3423.1875 | 121.1655 | -0.28381 | 120.9641 | 0.076067 | -0.067994 | 0.015472 | -0.038752 | 0.06831 | 0.030642 | -0.085608 | -0.13981 | -0.030674 | -0.08205 | -0.069733 | 0.06197 | 0.027798 | -0.04722 | 0.060923 | 0.12184 | -0.022218 | 0.061248 | 0.007024 | 0.11409 | 0.076418 | -0.039832 | -0.094033 | 0.015102 | -0.036274 | -0.023957 | 0.10775 | 0.073574 | -0.001444 | 0.1067 | -0.20178 | -0.092589 | -0.14402 | -0.03483
3424.9531 | 121.2891 | -0.25635 | 120.9229 | 0.071489 | -0.072572 | 0.006315 | -0.043331 | 0.06831 | 0.026064 | -0.090186 | -0.13981 | -0.026096 | -0.077472 | -0.074312 | 0.052814 | 0.032376 | -0.042641 | 0.065501 | 0.11726 | -0.026796 | 0.052091 | 0.002445 | 0.11409 | 0.07184 | -0.04441 | -0.094033 | 0.01968 | -0.031696 | -0.028536 | 0.09859 | 0.078152 | 0.003135 | 0.11128 | -0.19262 | -0.097168 | -0.13029 | -0.034831
3426.7344 | 121.2936 | -0.23346 | 120.9091 | 0.06691 | -0.063415 | 0.010893 | -0.047909 | 0.059155 | 0.021485 | -0.085608 | -0.14897 | -0.030674 | -0.072894 | -0.078891 | 0.057392 | 0.032376 | -0.04722 | 0.060923 | 0.11269 | -0.017639 | 0.056669 | -0.002133 | 0.10493 | 0.067261 | -0.039832 | -0.10319 | 0.015102 | -0.027118 | -0.033115 | 0.10317 | 0.078152 | -0.001444 | 0.1067 | -0.20636 | -0.10175 | -0.13029 | -0.025674
3428.4531 | 121.2433 | -0.28381 | 120.9549 | 0.076067 | -0.063415 | 0.015472 | -0.043331 | 0.059155 | 0.021485 | -0.085608 | -0.13981 | -0.026096 | -0.077472 | -0.078891 | 0.057392 | 0.027798 | -0.051798 | 0.056344 | 0.12184 | -0.017639 | 0.061248 | 0.002445 | 0.10493 | 0.067261 | -0.039832 | -0.094033 | 0.01968 | -0.031696 | -0.033115 | 0.10317 | 0.073574 | -0.006022 | 0.10212 | -0.1972 | -0.088011 | -0.13486 | -0.025674
3430.25 | 121.2891 | -0.24719 | 120.9595 | 0.06691 | -0.063415 | 0.015472 | -0.043331 | 0.059155 | 0.026064 | -0.090186 | -0.14439 | -0.030674 | -0.08205 | -0.074312 | 0.052814 | 0.027798 | -0.04722 | 0.060923 | 0.11269 | -0.017639 | 0.061248 | 0.002445 | 0.10493 | 0.07184 | -0.04441 | -0.098611 | 0.015102 | -0.036274 | -0.028536 | 0.09859 | 0.073574 | -0.001444 | 0.1067 | -0.1972 | -0.097167 | -0.13486 | -0.03483
3432.0312 | 121.2433 | -0.27008 | 120.9732 | 0.062332 | -0.072572 | 0.020051 | -0.043331 | 0.06831 | 0.026064 | -0.085608 | -0.14439 | -0.030674 | -0.072894 | -0.069733 | 0.052814 | 0.02322 | -0.042641 | 0.056344 | 0.10811 | -0.026796 | 0.065827 | 0.002445 | 0.11409 | 0.07184 | -0.039832 | -0.098611 | 0.015102 | -0.027118 | -0.023957 | 0.09859 | 0.068996 | 0.003135 | 0.10212 | -0.1972 | -0.10175 | -0.12571 | -0.030253
3433.8281 | 121.3486 | -0.25177 | 120.9595 | 0.071489 | -0.067994 | 0.010893 | -0.043331 | 0.063733 | 0.030642 | -0.094765 | -0.14439 | -0.030674 | -0.077472 | -0.074312 | 0.06197 | 0.02322 | -0.051798 | 0.056344 | 0.11726 | -0.022218 | 0.056669 | 0.002445 | 0.10951 | 0.076418 | -0.048989 | -0.098611 | 0.015102 | -0.031696 | -0.028536 | 0.10775 | 0.068996 | -0.006022 | 0.10212 | -0.20636 | -0.092589 | -0.13944 | -0.025674
3435.6094 | 121.2479 | -0.29755 | 121.0052 | 0.071489 | -0.067994 | 0.001736 | -0.043331 | 0.059155 | 0.016907 | -0.08103 | -0.14897 | -0.030674 | -0.086628 | -0.074312 | 0.052814 | 0.027798 | -0.04722 | 0.060923 | 0.11726 | -0.022218 | 0.047512 | 0.002445 | 0.10493 | 0.062683 | -0.035254 | -0.10319 | 0.015102 | -0.040852 | -0.028536 | 0.09859 | 0.073574 | -0.001444 | 0.1067 | -0.20178 | -0.10175 | -0.13944 | -0.039408
3437.3906 | 121.2616 | -0.29755 | 121.0281 | 0.071489 | -0.072572 | 0.015472 | -0.038752 | 0.063733 | 0.026064 | -0.08103 | -0.14439 | -0.026096 | -0.08205 | -0.074312 | 0.066548 | 0.027798 | -0.04722 | 0.056344 | 0.11726 | -0.026796 | 0.061248 | 0.007024 | 0.10951 | 0.07184 | -0.035254 | -0.098611 | 0.01968 | -0.036274 | -0.028536 | 0.11232 | 0.073574 | -0.001444 | 0.10212 | -0.21093 | -0.097167 | -0.1486 | -0.03483
3439.1094 | 121.2982 | -0.28381 | 121.0144 | 0.071489 | -0.072572 | 0.010893 | -0.043331 | 0.063733 | 0.026064 | -0.085608 | -0.14439 | -0.035253 | -0.08205 | -0.069733 | 0.06197 | 0.018642 | -0.042641 | 0.060923 | 0.11726 | -0.026796 | 0.056669 | 0.002445 | 0.10951 | 0.07184 | -0.039832 | -0.098611 | 0.010523 | -0.036274 | -0.023957 | 0.10775 | 0.064418 | 0.003135 | 0.1067 | -0.20636 | -0.10175 | -0.14402 | -0.039409
3440.9062 | 121.2799 | -0.28839 | 121.0464 | 0.071489 | -0.067994 | 0.015472 | -0.038752 | 0.063733 | 0.030642 | -0.085608 | -0.13981 | -0.030674 | -0.08205 | -0.074312 | 0.06197 | 0.027798 | -0.04722 | 0.060923 | 0.11726 | -0.022218 | 0.061248 | 0.007024 | 0.10951 | 0.076418 | -0.039832 | -0.094033 | 0.015102 | -0.036274 | -0.028536 | 0.10775 | 0.073574 | -0.001444 | 0.1067 | -0.20178 | -0.092589 | -0.14402 | -0.03483
3442.6406 | 121.4264 | -0.24261 | 121.0236 | 0.06691 | -0.067994 | 0.010893 | -0.034174 | 0.054577 | 0.030642 | -0.08103 | -0.14439 | -0.030674 | -0.086628 | -0.074312 | 0.06197 | 0.018642 | -0.042641 | 0.065501 | 0.11269 | -0.022218 | 0.056669 | 0.011602 | 0.10035 | 0.076418 | -0.035254 | -0.098611 | 0.015102 | -0.040852 | -0.028536 | 0.10775 | 0.064418 | 0.003135 | 0.11128 | -0.20636 | -0.10175 | -0.1486 | -0.043987
3444.4219 | 121.3211 | -0.28839 | 121.0373 | 0.06691 | -0.067994 | 0.015472 | -0.043331 | 0.054577 | 0.030642 | -0.085608 | -0.15354 | -0.035253 | -0.08205 | -0.08347 | 0.057392 | 0.018642 | -0.04722 | 0.060923 | 0.11269 | -0.022218 | 0.061248 | 0.002445 | 0.10035 | 0.076418 | -0.039832 | -0.10777 | 0.010523 | -0.036274 | -0.037694 | 0.10317 | 0.064418 | -0.001444 | 0.1067 | -0.21094 | -0.10632 | -0.13944 | -0.03483
3446.1406 | 121.3165 | -0.32044 | 121.0464 | 0.06691 | -0.072572 | 0.015472 | -0.047909 | 0.054577 | 0.021485 | -0.090186 | -0.14439 | -0.030674 | -0.08205 | -0.078891 | 0.06197 | 0.032376 | -0.042641 | 0.065501 | 0.11269 | -0.026796 | 0.061248 | -0.002133 | 0.10035 | 0.067261 | -0.04441 | -0.098611 | 0.015102 | -0.036274 | -0.033115 | 0.10775 | 0.078152 | 0.003135 | 0.11128 | -0.20636 | -0.10175 | -0.14402 | -0.039409
3447.9219 | 121.3348 | -0.30212 | 121.0648 | 0.071489 | -0.077151 | 0.006315 | -0.043331 | 0.059155 | 0.016907 | -0.085608 | -0.14439 | -0.026096 | -0.086628 | -0.069733 | 0.057392 | 0.027798 | -0.04722 | 0.060923 | 0.11726 | -0.031375 | 0.052091 | 0.002445 | 0.10493 | 0.062683 | -0.039832 | -0.098611 | 0.01968 | -0.040852 | -0.023957 | 0.10317 | 0.073574 | -0.001444 | 0.1067 | -0.20178 | -0.097167 | -0.14402 | -0.039408
3449.6875 | 121.4584 | -0.24261 | 121.0373 | 0.076067 | -0.067994 | 0.010893 | -0.043331 | 0.063733 | 0.021485 | -0.085608 | -0.13981 | -0.035253 | -0.08205 | -0.074312 | 0.057392 | 0.027798 | -0.042641 | 0.056344 | 0.12184 | -0.022218 | 0.056669 | 0.002445 | 0.10951 | 0.067261 | -0.039832 | -0.094033 | 0.010523 | -0.036274 | -0.028536 | 0.10317 | 0.073574 | 0.003135 | 0.10212 | -0.1972 | -0.097168 | -0.13944 | -0.039409
3451.3906 | 121.344 | -0.29297 | 121.106 | 0.071489 | -0.063415 | 0.020051 | -0.043331 | 0.06831 | 0.030642 | -0.085608 | -0.14439 | -0.030674 | -0.08205 | -0.078891 | 0.057392 | 0.02322 | -0.042641 | 0.056344 | 0.11726 | -0.017639 | 0.065827 | 0.002445 | 0.11409 | 0.076418 | -0.039832 | -0.098611 | 0.015102 | -0.036274 | -0.033115 | 0.10317 | 0.068996 | 0.003135 | 0.10212 | -0.20178 | -0.10175 | -0.13944 | -0.039409
3453.1719 | 121.4401 | -0.27466 | 121.0739 | 0.071489 | -0.072572 | 0.015472 | -0.043331 | 0.054577 | 0.021485 | -0.090186 | -0.14439 | -0.030674 | -0.08205 | -0.069733 | 0.057392 | 0.027798 | -0.04722 | 0.065501 | 0.11726 | -0.026796 | 0.061248 | 0.002445 | 0.10035 | 0.067261 | -0.04441 | -0.098611 | 0.015102 | -0.036274 | -0.023957 | 0.10317 | 0.073574 | -0.001444 | 0.11128 | -0.20178 | -0.097167 | -0.13944 | -0.03483
3454.9531 | 121.4859 | -0.25177 | 121.051 | 0.071489 | -0.067994 | 0.010893 | -0.047909 | 0.059155 | 0.026064 | -0.085608 | -0.13523 | -0.035253 | -0.077472 | -0.065154 | 0.06197 | 0.018642 | -0.04722 | 0.060923 | 0.11726 | -0.022218 | 0.056669 | -0.002133 | 0.10493 | 0.07184 | -0.039832 | -0.089454 | 0.010523 | -0.031696 | -0.019378 | 0.10775 | 0.064418 | -0.001444 | 0.1067 | -0.1972 | -0.08801 | -0.13944 | -0.030252
3456.6719 | 121.3806 | -0.31128 | 121.0968 | 0.06691 | -0.058836 | 0.015472 | -0.038752 | 0.063733 | 0.030642 | -0.085608 | -0.13981 | -0.035253 | -0.08205 | -0.08347 | 0.057392 | 0.027798 | -0.042641 | 0.065501 | 0.11269 | -0.01306 | 0.061248 | 0.007024 | 0.10951 | 0.076418 | -0.039832 | -0.094033 | 0.010523 | -0.036274 | -0.037694 | 0.10317 | 0.073574 | 0.003135 | 0.11128 | -0.1972 | -0.097168 | -0.13944 | -0.039409
3458.4531 | 121.5088 | -0.2655 | 121.0922 | 0.06691 | -0.067994 | 0.024629 | -0.043331 | 0.063733 | 0.026064 | -0.085608 | -0.13981 | -0.035253 | -0.08205 | -0.078891 | 0.06197 | 0.02322 | -0.051798 | 0.060923 | 0.11269 | -0.022218 | 0.070405 | 0.002445 | 0.10951 | 0.07184 | -0.039832 | -0.094033 | 0.010523 | -0.036274 | -0.033115 | 0.10775 | 0.068996 | -0.006022 | 0.1067 | -0.20178 | -0.088011 | -0.14402 | -0.030252
3460.2344 | 121.5088 | -0.24719 | 121.106 | 0.057754 | -0.067994 | 0.015472 | -0.043331 | 0.059155 | 0.021485 | -0.085608 | -0.14439 | -0.030674 | -0.077472 | -0.069733 | 0.057392 | 0.02322 | -0.042641 | 0.065501 | 0.10353 | -0.022218 | 0.061248 | 0.002445 | 0.10493 | 0.067261 | -0.039832 | -0.098611 | 0.015102 | -0.031696 | -0.023957 | 0.10317 | 0.068996 | 0.003135 | 0.11128 | -0.20178 | -0.10175 | -0.13486 | -0.034831
3462.0156 | 121.4951 | -0.24719 | 121.1014 | 0.06691 | -0.067994 | 0.020051 | -0.043331 | 0.059155 | 0.026064 | -0.090186 | -0.14439 | -0.030674 | -0.08205 | -0.069733 | 0.071126 | 0.027798 | -0.04722 | 0.065501 | 0.11269 | -0.022218 | 0.065827 | 0.002445 | 0.10493 | 0.07184 | -0.04441 | -0.098611 | 0.015102 | -0.036274 | -0.023957 | 0.1169 | 0.073574 | -0.001444 | 0.11128 | -0.21551 | -0.097167 | -0.15318 | -0.03483
3463.75 | 121.5134 | -0.2655 | 121.1105 | 0.071489 | -0.063415 | 0.015472 | -0.038752 | 0.054577 | 0.026064 | -0.08103 | -0.14439 | -0.035253 | -0.077472 | -0.074312 | 0.057392 | 0.027798 | -0.04722 | 0.065501 | 0.11726 | -0.017639 | 0.061248 | 0.007024 | 0.10035 | 0.07184 | -0.035254 | -0.098611 | 0.010523 | -0.031696 | -0.028536 | 0.10317 | 0.073574 | -0.001444 | 0.11128 | -0.20178 | -0.097167 | -0.13486 | -0.030252
3465.5312 | 121.5179 | -0.26093 | 121.1243 | 0.071489 | -0.072572 | 0.006315 | -0.047909 | 0.063733 | 0.026064 | -0.085608 | -0.14439 | -0.035253 | -0.08205 | -0.074312 | 0.052814 | 0.027798 | -0.051798 | 0.060923 | 0.11726 | -0.026796 | 0.052091 | -0.002133 | 0.10951 | 0.07184 | -0.039832 | -0.098611 | 0.010523 | -0.036274 | -0.028536 | 0.09859 | 0.073574 | -0.006022 | 0.1067 | -0.1972 | -0.092589 | -0.13486 | -0.030252
3467.3125 | 121.5546 | -0.26093 | 121.138 | 0.071489 | -0.072572 | 0.010893 | -0.038752 | 0.059155 | 0.021485 | -0.085608 | -0.14439 | -0.030674 | -0.077472 | -0.069733 | 0.052814 | 0.027798 | -0.04722 | 0.056344 | 0.11726 | -0.026796 | 0.056669 | 0.007024 | 0.10493 | 0.067261 | -0.039832 | -0.098611 | 0.015102 | -0.031696 | -0.023957 | 0.09859 | 0.073574 | -0.001444 | 0.10212 | -0.1972 | -0.097167 | -0.13029 | -0.030252
3469.1094 | 121.4218 | -0.28381 | 121.1838 | 0.071489 | -0.072572 | 0.020051 | -0.038752 | 0.059155 | 0.030642 | -0.085608 | -0.13523 | -0.021517 | -0.08205 | -0.074312 | 0.057392 | 0.02322 | -0.042641 | 0.070079 | 0.11726 | -0.026796 | 0.065827 | 0.007024 | 0.10493 | 0.076418 | -0.039832 | -0.089454 | 0.024259 | -0.036274 | -0.028536 | 0.10317 | 0.068996 | 0.003135 | 0.11585 | -0.19262 | -0.092589 | -0.13944 | -0.039409
3470.8281 | 121.4813 | -0.30212 | 121.1884 | 0.062332 | -0.063415 | 0.020051 | -0.034174 | 0.059155 | 0.026064 | -0.076452 | -0.13981 | -0.026096 | -0.08205 | -0.074312 | 0.06197 | 0.014064 | -0.051798 | 0.065501 | 0.10811 | -0.017639 | 0.065827 | 0.011602 | 0.10493 | 0.07184 | -0.030676 | -0.094033 | 0.01968 | -0.036274 | -0.028536 | 0.10775 | 0.05984 | -0.006022 | 0.11128 | -0.20178 | -0.088011 | -0.14402 | -0.030252
3472.6094 | 121.55 | -0.25635 | 121.1472 | 0.076067 | -0.067994 | 0.015472 | -0.038752 | 0.06831 | 0.016907 | -0.08103 | -0.13981 | -0.026096 | -0.08205 | -0.074312 | 0.06197 | 0.018642 | -0.051798 | 0.060923 | 0.12184 | -0.022218 | 0.061248 | 0.007024 | 0.11409 | 0.062683 | -0.035254 | -0.094033 | 0.01968 | -0.036274 | -0.028536 | 0.10775 | 0.064418 | -0.006022 | 0.1067 | -0.20178 | -0.088011 | -0.14402 | -0.030252
3474.3906 | 121.4447 | -0.29755 | 121.2067 | 0.062332 | -0.067994 | 0.010893 | -0.043331 | 0.063733 | 0.030642 | -0.085608 | -0.13981 | -0.035253 | -0.077472 | -0.069733 | 0.048236 | 0.027798 | -0.051798 | 0.060923 | 0.10811 | -0.022218 | 0.056669 | 0.002445 | 0.10951 | 0.076418 | -0.039832 | -0.094033 | 0.010523 | -0.031696 | -0.023957 | 0.094012 | 0.073574 | -0.006022 | 0.1067 | -0.18804 | -0.088011 | -0.12571 | -0.025674
3476.1094 | 121.5775 | -0.25177 | 121.1609 | 0.06691 | -0.063415 | 0.015472 | -0.038752 | 0.054577 | 0.030642 | -0.090186 | -0.13981 | -0.030674 | -0.08205 | -0.074312 | 0.06197 | 0.02322 | -0.04722 | 0.065501 | 0.11269 | -0.017639 | 0.061248 | 0.007024 | 0.10035 | 0.076418 | -0.04441 | -0.094033 | 0.015102 | -0.036274 | -0.028536 | 0.10775 | 0.068996 | -0.001444 | 0.11128 | -0.20178 | -0.092589 | -0.14402 | -0.03483
3477.9062 | 121.5179 | -0.31128 | 121.2112 | 0.071489 | -0.072572 | 0.010893 | -0.047909 | 0.063733 | 0.026064 | -0.090186 | -0.14439 | -0.035253 | -0.086628 | -0.069733 | 0.06197 | 0.02322 | -0.042641 | 0.056344 | 0.11726 | -0.026796 | 0.056669 | -0.002133 | 0.10951 | 0.07184 | -0.04441 | -0.098611 | 0.010523 | -0.040852 | -0.023957 | 0.10775 | 0.068996 | 0.003135 | 0.10212 | -0.20636 | -0.10175 | -0.1486 | -0.043987
3479.6875 | 121.5775 | -0.27466 | 121.2021 | 0.076067 | -0.063415 | 0.015472 | -0.038752 | 0.063733 | 0.030642 | -0.090186 | -0.13981 | -0.026096 | -0.08205 | -0.074312 | 0.052814 | 0.027798 | -0.04722 | 0.060923 | 0.12184 | -0.017639 | 0.061248 | 0.007024 | 0.10951 | 0.076418 | -0.04441 | -0.094033 | 0.01968 | -0.036274 | -0.028536 | 0.09859 | 0.073574 | -0.001444 | 0.1067 | -0.19262 | -0.092589 | -0.13486 | -0.03483
3481.4688 | 121.5408 | -0.27466 | 121.1975 | 0.071489 | -0.067994 | 0.015472 | -0.034174 | 0.063733 | 0.021485 | -0.085608 | -0.13981 | -0.030674 | -0.077472 | -0.08347 | 0.052814 | 0.032376 | -0.038063 | 0.060923 | 0.11726 | -0.022218 | 0.061248 | 0.011602 | 0.10951 | 0.067261 | -0.039832 | -0.094033 | 0.015102 | -0.031696 | -0.037694 | 0.09859 | 0.078152 | 0.007713 | 0.1067 | -0.19262 | -0.10175 | -0.13029 | -0.039409
3483.1875 | 121.582 | -0.26093 | 121.2112 | 0.071489 | -0.072572 | 0.015472 | -0.043331 | 0.054577 | 0.026064 | -0.08103 | -0.13981 | -0.026096 | -0.08205 | -0.074312 | 0.06197 | 0.02322 | -0.04722 | 0.056344 | 0.11726 | -0.026796 | 0.061248 | 0.002445 | 0.10035 | 0.07184 | -0.035254 | -0.094033 | 0.01968 | -0.036274 | -0.028536 | 0.10775 | 0.068996 | -0.001444 | 0.10212 | -0.20178 | -0.092589 | -0.14402 | -0.03483
3484.9688 | 121.6095 | -0.26093 | 121.2112 | 0.062332 | -0.058836 | 0.010893 | -0.043331 | 0.059155 | 0.030642 | -0.090186 | -0.13981 | -0.030674 | -0.08205 | -0.069733 | 0.06197 | 0.02322 | -0.04722 | 0.060923 | 0.10811 | -0.01306 | 0.056669 | 0.002445 | 0.10493 | 0.076418 | -0.04441 | -0.094033 | 0.015102 | -0.036274 | -0.023957 | 0.10775 | 0.068996 | -0.001444 | 0.1067 | -0.20178 | -0.092589 | -0.14402 | -0.03483
3486.75 | 121.5088 | -0.31128 | 121.2112 | 0.06691 | -0.067994 | 0.020051 | -0.047909 | 0.063733 | 0.026064 | -0.090186 | -0.13981 | -0.030674 | -0.077472 | -0.069733 | 0.057392 | 0.02322 | -0.042641 | 0.065501 | 0.11269 | -0.022218 | 0.065827 | -0.002133 | 0.10951 | 0.07184 | -0.04441 | -0.094033 | 0.015102 | -0.031696 | -0.023957 | 0.10317 | 0.068996 | 0.003135 | 0.11128 | -0.1972 | -0.097168 | -0.13486 | -0.034831
3488.4688 | 121.6278 | -0.29297 | 121.2204 | 0.076067 | -0.067994 | 0.024629 | -0.038752 | 0.059155 | 0.016907 | -0.090186 | -0.13981 | -0.030674 | -0.091207 | -0.069733 | 0.066548 | 0.027798 | -0.04722 | 0.065501 | 0.12184 | -0.022218 | 0.070405 | 0.007024 | 0.10493 | 0.062683 | -0.04441 | -0.094033 | 0.015102 | -0.045431 | -0.023957 | 0.11232 | 0.073574 | -0.001444 | 0.11128 | -0.20636 | -0.092589 | -0.15775 | -0.043987
3490.25 | 121.5729 | -0.29297 | 121.2753 | 0.06691 | -0.063415 | 0.015472 | -0.043331 | 0.063733 | 0.026064 | -0.090186 | -0.14897 | -0.035253 | -0.077472 | -0.069733 | 0.06197 | 0.02322 | -0.042641 | 0.056344 | 0.11269 | -0.017639 | 0.061248 | 0.002445 | 0.10951 | 0.07184 | -0.04441 | -0.10319 | 0.010523 | -0.031696 | -0.023957 | 0.10775 | 0.068996 | 0.003135 | 0.10212 | -0.21094 | -0.10632 | -0.13944 | -0.034831
3492.0312 | 121.637 | -0.2655 | 121.2158 | 0.06691 | -0.058836 | 0.010893 | -0.038752 | 0.059155 | 0.026064 | -0.08103 | -0.13981 | -0.030674 | -0.08205 | -0.069733 | 0.06197 | 0.02322 | -0.056376 | 0.060923 | 0.11269 | -0.01306 | 0.056669 | 0.007024 | 0.10493 | 0.07184 | -0.035254 | -0.094033 | 0.015102 | -0.036274 | -0.023957 | 0.10775 | 0.068996 | -0.0106 | 0.1067 | -0.20178 | -0.083433 | -0.14402 | -0.025674
3493.8125 | 121.6049 | -0.29755 | 121.2387 | 0.071489 | -0.063415 | 0.020051 | -0.043331 | 0.063733 | 0.026064 | -0.090186 | -0.14439 | -0.026096 | -0.08205 | -0.074312 | 0.057392 | 0.018642 | -0.04722 | 0.065501 | 0.11726 | -0.017639 | 0.065827 | 0.002445 | 0.10951 | 0.07184 | -0.04441 | -0.098611 | 0.01968 | -0.036274 | -0.028536 | 0.10317 | 0.064418 | -0.001444 | 0.11128 | -0.20178 | -0.097167 | -0.13944 | -0.03483
3495.5938 | 121.4996 | -0.31586 | 121.2708 | 0.062332 | -0.063415 | 0.020051 | -0.043331 | 0.059155 | 0.030642 | -0.085608 | -0.13981 | -0.030674 | -0.08205 | -0.074312 | 0.052814 | 0.027798 | -0.04722 | 0.060923 | 0.10811 | -0.017639 | 0.065827 | 0.002445 | 0.10493 | 0.076418 | -0.039832 | -0.094033 | 0.015102 | -0.036274 | -0.028536 | 0.09859 | 0.073574 | -0.001444 | 0.1067 | -0.19262 | -0.092589 | -0.13486 | -0.03483
3497.3594 | 121.6187 | -0.27924 | 121.2387 | 0.062332 | -0.054257 | 0.010893 | -0.043331 | 0.059155 | 0.016907 | -0.085608 | -0.14439 | -0.030674 | -0.077472 | -0.065154 | 0.057392 | 0.027798 | -0.042641 | 0.060923 | 0.10811 | -0.008481 | 0.056669 | 0.002445 | 0.10493 | 0.062683 | -0.039832 | -0.098611 | 0.015102 | -0.031696 | -0.019378 | 0.10317 | 0.073574 | 0.003135 | 0.1067 | -0.20178 | -0.10175 | -0.13486 | -0.034831
3499.0938 | 121.6278 | -0.29297 | 121.2479 | 0.071489 | -0.067994 | 0.010893 | -0.043331 | 0.06831 | 0.026064 | -0.085608 | -0.13981 | -0.030674 | -0.077472 | -0.078891 | 0.06197 | 0.02322 | -0.042641 | 0.065501 | 0.11726 | -0.022218 | 0.056669 | 0.002445 | 0.11409 | 0.07184 | -0.039832 | -0.094033 | 0.015102 | -0.031696 | -0.033115 | 0.10775 | 0.068996 | 0.003135 | 0.11128 | -0.20178 | -0.097168 | -0.13944 | -0.034831
3500.875 | 121.6003 | -0.30212 | 121.2708 | 0.071489 | -0.063415 | 0.015472 | -0.038752 | 0.063733 | 0.030642 | -0.099343 | -0.13981 | -0.039832 | -0.08205 | -0.078891 | 0.057392 | 0.027798 | -0.051798 | 0.056344 | 0.11726 | -0.017639 | 0.061248 | 0.007024 | 0.10951 | 0.076418 | -0.053567 | -0.094033 | 0.005944 | -0.036274 | -0.033115 | 0.10317 | 0.073574 | -0.006022 | 0.10212 | -0.1972 | -0.088011 | -0.13944 | -0.030252
3502.6406 | 121.6003 | -0.32044 | 121.2662 | 0.06691 | -0.063415 | 0.020051 | -0.038752 | 0.06831 | 0.026064 | -0.085608 | -0.13981 | -0.030674 | -0.08205 | -0.074312 | 0.052814 | 0.018642 | -0.04722 | 0.060923 | 0.11269 | -0.017639 | 0.065827 | 0.007024 | 0.11409 | 0.07184 | -0.039832 | -0.094033 | 0.015102 | -0.036274 | -0.028536 | 0.09859 | 0.064418 | -0.001444 | 0.1067 | -0.19262 | -0.092589 | -0.13486 | -0.03483
3504.4219 | 121.5683 | -0.34332 | 121.2982 | 0.06691 | -0.067994 | 0.015472 | -0.043331 | 0.063733 | 0.026064 | -0.090186 | -0.13523 | -0.026096 | -0.08205 | -0.069733 | 0.057392 | 0.02322 | -0.04722 | 0.056344 | 0.11269 | -0.022218 | 0.061248 | 0.002445 | 0.10951 | 0.07184 | -0.04441 | -0.089454 | 0.01968 | -0.036274 | -0.023957 | 0.10317 | 0.068996 | -0.001444 | 0.10212 | -0.19262 | -0.08801 | -0.13944 | -0.03483
3506.1406 | 121.6461 | -0.29755 | 121.2753 | 0.06691 | -0.067994 | 0.010893 | -0.043331 | 0.063733 | 0.021485 | -0.085608 | -0.13523 | -0.035253 | -0.08205 | -0.074312 | 0.057392 | 0.027798 | -0.042641 | 0.060923 | 0.11269 | -0.022218 | 0.056669 | 0.002445 | 0.10951 | 0.067261 | -0.039832 | -0.089454 | 0.010523 | -0.036274 | -0.028536 | 0.10317 | 0.073574 | 0.003135 | 0.1067 | -0.19262 | -0.092589 | -0.13944 | -0.039409
3507.9219 | 121.5912 | -0.31128 | 121.312 | 0.062332 | -0.072572 | 0.015472 | -0.043331 | 0.059155 | 0.030642 | -0.08103 | -0.13981 | -0.035253 | -0.072894 | -0.078891 | 0.052814 | 0.032376 | -0.042641 | 0.060923 | 0.10811 | -0.026796 | 0.061248 | 0.002445 | 0.10493 | 0.076418 | -0.035254 | -0.094033 | 0.010523 | -0.027118 | -0.033115 | 0.09859 | 0.078152 | 0.003135 | 0.1067 | -0.19262 | -0.097168 | -0.12571 | -0.030253
3509.7031 | 121.6095 | -0.32044 | 121.2845 | 0.062332 | -0.067994 | 0.010893 | -0.043331 | 0.059155 | 0.026064 | -0.085608 | -0.13981 | -0.030674 | -0.08205 | -0.065154 | 0.057392 | 0.027798 | -0.038063 | 0.065501 | 0.10811 | -0.022218 | 0.056669 | 0.002445 | 0.10493 | 0.07184 | -0.039832 | -0.094033 | 0.015102 | -0.036274 | -0.019378 | 0.10317 | 0.073574 | 0.007713 | 0.11128 | -0.1972 | -0.10175 | -0.13944 | -0.043987
3511.4219 | 121.6782 | -0.29297 | 121.2753 | 0.06691 | -0.063415 | 0.015472 | -0.043331 | 0.063733 | 0.030642 | -0.090186 | -0.13981 | -0.039832 | -0.072894 | -0.08347 | 0.057392 | 0.02322 | -0.04722 | 0.056344 | 0.11269 | -0.017639 | 0.061248 | 0.002445 | 0.10951 | 0.076418 | -0.04441 | -0.094033 | 0.005944 | -0.027118 | -0.037694 | 0.10317 | 0.068996 | -0.001444 | 0.10212 | -0.1972 | -0.092589 | -0.13029 | -0.025674
3513.2031 | 121.6507 | -0.33417 | 121.3348 | 0.062332 | -0.063415 | 0.020051 | -0.038752 | 0.059155 | 0.026064 | -0.085608 | -0.13523 | -0.035253 | -0.072894 | -0.069733 | 0.057392 | 0.018642 | -0.051798 | 0.060923 | 0.10811 | -0.017639 | 0.065827 | 0.007024 | 0.10493 | 0.07184 | -0.039832 | -0.089454 | 0.010523 | -0.027118 | -0.023957 | 0.10317 | 0.064418 | -0.006022 | 0.1067 | -0.19262 | -0.083432 | -0.13029 | -0.021096
3514.9844 | 121.6553 | -0.32044 | 121.3257 | 0.071489 | -0.067994 | 0.010893 | -0.043331 | 0.059155 | 0.026064 | -0.090186 | -0.13523 | -0.021517 | -0.08205 | -0.08347 | 0.066548 | 0.027798 | -0.051798 | 0.060923 | 0.11726 | -0.022218 | 0.056669 | 0.002445 | 0.10493 | 0.07184 | -0.04441 | -0.089454 | 0.024259 | -0.036274 | -0.037694 | 0.11232 | 0.073574 | -0.006022 | 0.1067 | -0.20178 | -0.083432 | -0.1486 | -0.030252
3516.7031 | 121.7422 | -0.29297 | 121.2982 | 0.062332 | -0.067994 | 0.015472 | -0.038752 | 0.06831 | 0.030642 | -0.085608 | -0.14439 | -0.026096 | -0.077472 | -0.065154 | 0.057392 | 0.018642 | -0.04722 | 0.060923 | 0.10811 | -0.022218 | 0.061248 | 0.007024 | 0.11409 | 0.076418 | -0.039832 | -0.098611 | 0.01968 | -0.031696 | -0.019378 | 0.10317 | 0.064418 | -0.001444 | 0.1067 | -0.20178 | -0.097167 | -0.13486 | -0.030252
3518.5 | 121.5958 | -0.34332 | 121.3394 | 0.06691 | -0.063415 | 0.020051 | -0.047909 | 0.059155 | 0.026064 | -0.085608 | -0.14897 | -0.021517 | -0.077472 | -0.069733 | 0.057392 | 0.018642 | -0.051798 | 0.056344 | 0.11269 | -0.017639 | 0.065827 | -0.002133 | 0.10493 | 0.07184 | -0.039832 | -0.10319 | 0.024259 | -0.031696 | -0.023957 | 0.10317 | 0.064418 | -0.006022 | 0.10212 | -0.20636 | -0.097168 | -0.13486 | -0.025674
3520.2812 | 121.6278 | -0.33417 | 121.3394 | 0.06691 | -0.067994 | 0.015472 | -0.038752 | 0.059155 | 0.030642 | -0.08103 | -0.13981 | -0.030674 | -0.077472 | -0.069733 | 0.06197 | 0.018642 | -0.04722 | 0.056344 | 0.11269 | -0.022218 | 0.061248 | 0.007024 | 0.10493 | 0.076418 | -0.035254 | -0.094033 | 0.015102 | -0.031696 | -0.023957 | 0.10775 | 0.064418 | -0.001444 | 0.10212 | -0.20178 | -0.092589 | -0.13944 | -0.030252
3522.0156 | 121.7422 | -0.31586 | 121.3348 | 0.071489 | -0.063415 | 0.010893 | -0.043331 | 0.06831 | 0.021485 | -0.08103 | -0.13523 | -0.026096 | -0.08205 | -0.074312 | 0.057392 | 0.027798 | -0.04722 | 0.056344 | 0.11726 | -0.017639 | 0.056669 | 0.002445 | 0.11409 | 0.067261 | -0.035254 | -0.089454 | 0.01968 | -0.036274 | -0.028536 | 0.10317 | 0.073574 | -0.001444 | 0.10212 | -0.19262 | -0.08801 | -0.13944 | -0.03483
3523.7969 | 121.7606 | -0.31128 | 121.3211 | 0.06691 | -0.067994 | 0.010893 | -0.043331 | 0.059155 | 0.016907 | -0.08103 | -0.13981 | -0.026096 | -0.086628 | -0.069733 | 0.06197 | 0.02322 | -0.051798 | 0.060923 | 0.11269 | -0.022218 | 0.056669 | 0.002445 | 0.10493 | 0.062683 | -0.035254 | -0.094033 | 0.01968 | -0.040852 | -0.023957 | 0.10775 | 0.068996 | -0.006022 | 0.1067 | -0.20178 | -0.088011 | -0.1486 | -0.03483
3525.5781 | 121.7651 | -0.32044 | 121.2753 | 0.076067 | -0.063415 | 0.010893 | -0.047909 | 0.063733 | 0.021485 | -0.090186 | -0.13065 | -0.030674 | -0.08205 | -0.069733 | 0.06197 | 0.018642 | -0.042641 | 0.056344 | 0.12184 | -0.017639 | 0.056669 | -0.002133 | 0.10951 | 0.067261 | -0.04441 | -0.084876 | 0.015102 | -0.036274 | -0.023957 | 0.10775 | 0.064418 | 0.003135 | 0.10212 | -0.19262 | -0.088011 | -0.14402 | -0.039409
3527.2812 | 121.6461 | -0.34332 | 121.3394 | 0.06691 | -0.058836 | 0.015472 | -0.047909 | 0.063733 | 0.016907 | -0.08103 | -0.13523 | -0.030674 | -0.072894 | -0.069733 | 0.057392 | 0.027798 | -0.04722 | 0.060923 | 0.11269 | -0.01306 | 0.061248 | -0.002133 | 0.10951 | 0.062683 | -0.035254 | -0.089454 | 0.015102 | -0.027118 | -0.023957 | 0.10317 | 0.073574 | -0.001444 | 0.1067 | -0.19262 | -0.08801 | -0.13029 | -0.025674
3529.0781 | 121.6553 | -0.36163 | 121.3623 | 0.076067 | -0.063415 | 0.024629 | -0.034174 | 0.063733 | 0.026064 | -0.085608 | -0.13981 | -0.026096 | -0.08205 | -0.069733 | 0.06197 | 0.02322 | -0.04722 | 0.056344 | 0.12184 | -0.017639 | 0.070405 | 0.011602 | 0.10951 | 0.07184 | -0.039832 | -0.094033 | 0.01968 | -0.036274 | -0.023957 | 0.10775 | 0.068996 | -0.001444 | 0.10212 | -0.20178 | -0.092589 | -0.14402 | -0.03483
3530.8594 | 121.7926 | -0.31586 | 121.3348 | 0.06691 | -0.063415 | 0.020051 | -0.043331 | 0.063733 | 0.030642 | -0.085608 | -0.13523 | -0.030674 | -0.08205 | -0.069733 | 0.057392 | 0.027798 | -0.042641 | 0.065501 | 0.11269 | -0.017639 | 0.065827 | 0.002445 | 0.10951 | 0.076418 | -0.039832 | -0.089454 | 0.015102 | -0.036274 | -0.023957 | 0.10317 | 0.073574 | 0.003135 | 0.11128 | -0.19262 | -0.092589 | -0.13944 | -0.039409
3532.5781 | 121.6736 | -0.35706 | 121.3348 | 0.076067 | -0.058836 | 0.015472 | -0.043331 | 0.059155 | 0.021485 | -0.085608 | -0.14439 | -0.030674 | -0.072894 | -0.069733 | 0.057392 | 0.018642 | -0.042641 | 0.060923 | 0.12184 | -0.01306 | 0.061248 | 0.002445 | 0.10493 | 0.067261 | -0.039832 | -0.098611 | 0.015102 | -0.027118 | -0.023957 | 0.10317 | 0.064418 | 0.003135 | 0.1067 | -0.20178 | -0.10175 | -0.13029 | -0.030253
3534.375 | 121.669 | -0.37079 | 121.3531 | 0.071489 | -0.063415 | 0.015472 | -0.038752 | 0.063733 | 0.026064 | -0.085608 | -0.14439 | -0.026096 | -0.08205 | -0.074312 | 0.052814 | 0.02322 | -0.042641 | 0.060923 | 0.11726 | -0.017639 | 0.061248 | 0.007024 | 0.10951 | 0.07184 | -0.039832 | -0.098611 | 0.01968 | -0.036274 | -0.028536 | 0.09859 | 0.068996 | 0.003135 | 0.1067 | -0.1972 | -0.10175 | -0.13486 | -0.039409
3536.1406 | 121.7834 | -0.32501 | 121.3165 | 0.071489 | -0.067994 | 0.015472 | -0.047909 | 0.063733 | 0.026064 | -0.090186 | -0.13981 | -0.035253 | -0.072894 | -0.074312 | 0.057392 | 0.027798 | -0.04722 | 0.051766 | 0.11726 | -0.022218 | 0.061248 | -0.002133 | 0.10951 | 0.07184 | -0.04441 | -0.094033 | 0.010523 | -0.027118 | -0.028536 | 0.10317 | 0.073574 | -0.001444 | 0.097542 | -0.1972 | -0.092589 | -0.13029 | -0.025674
3537.8594 | 121.7972 | -0.31128 | 121.312 | 0.062332 | -0.067994 | 0.010893 | -0.047909 | 0.059155 | 0.026064 | -0.090186 | -0.14439 | -0.030674 | -0.077472 | -0.069733 | 0.06197 | 0.027798 | -0.04722 | 0.060923 | 0.10811 | -0.022218 | 0.056669 | -0.002133 | 0.10493 | 0.07184 | -0.04441 | -0.098611 | 0.015102 | -0.031696 | -0.023957 | 0.10775 | 0.073574 | -0.001444 | 0.1067 | -0.20636 | -0.097167 | -0.13944 | -0.030252
3539.6406 | 121.7239 | -0.37079 | 121.3394 | 0.071489 | -0.067994 | 0.015472 | -0.043331 | 0.059155 | 0.026064 | -0.085608 | -0.14439 | -0.035253 | -0.077472 | -0.069733 | 0.057392 | 0.02322 | -0.04722 | 0.056344 | 0.11726 | -0.022218 | 0.061248 | 0.002445 | 0.10493 | 0.07184 | -0.039832 | -0.098611 | 0.010523 | -0.031696 | -0.023957 | 0.10317 | 0.068996 | -0.001444 | 0.10212 | -0.20178 | -0.097167 | -0.13486 | -0.030252
3541.4219 | 121.756 | -0.93842 | 120.726 | 0.057754 | -0.063415 | 0.015472 | -0.043331 | 0.06831 | 0.021485 | -0.085608 | -0.13981 | -0.026096 | -0.08205 | -0.069733 | 0.057392 | 0.02322 | -0.042641 | 0.056344 | 0.10353 | -0.017639 | 0.061248 | 0.002445 | 0.11409 | 0.067261 | -0.039832 | -0.094033 | 0.01968 | -0.036274 | -0.023957 | 0.10317 | 0.068996 | 0.003135 | 0.10212 | -0.1972 | -0.097168 | -0.13944 | -0.039409
3543.2031 | 121.8018 | -0.98419 | 120.6573 | 0.071489 | -0.058836 | 0.015472 | -0.043331 | 0.059155 | 0.021485 | -0.085608 | -0.13981 | -0.026096 | -0.08205 | -0.069733 | 0.052814 | 0.02322 | -0.04722 | 0.060923 | 0.11726 | -0.01306 | 0.061248 | 0.002445 | 0.10493 | 0.067261 | -0.039832 | -0.094033 | 0.01968 | -0.036274 | -0.023957 | 0.09859 | 0.068996 | -0.001444 | 0.1067 | -0.19262 | -0.092589 | -0.13486 | -0.03483
3544.9219 | 121.7514 | -1.0574 | 120.5887 | 0.062332 | -0.063415 | 0.006315 | -0.038752 | 0.063733 | 0.021485 | -0.08103 | -0.13523 | -0.035253 | -0.077472 | -0.078891 | 0.06197 | 0.018642 | -0.051798 | 0.056344 | 0.10811 | -0.017639 | 0.052091 | 0.007024 | 0.10951 | 0.067261 | -0.035254 | -0.089454 | 0.010523 | -0.031696 | -0.033115 | 0.10775 | 0.064418 | -0.006022 | 0.10212 | -0.1972 | -0.083432 | -0.13944 | -0.025674
3546.7031 | 121.8063 | -1.0895 | 120.52 | 0.071489 | -0.063415 | 0.020051 | -0.038752 | 0.063733 | 0.021485 | -0.085608 | -0.13981 | -0.021517 | -0.077472 | -0.074312 | 0.057392 | 0.018642 | -0.04722 | 0.056344 | 0.11726 | -0.017639 | 0.065827 | 0.007024 | 0.10951 | 0.067261 | -0.039832 | -0.094033 | 0.024259 | -0.031696 | -0.028536 | 0.10317 | 0.064418 | -0.001444 | 0.10212 | -0.1972 | -0.092589 | -0.13486 | -0.030252
3548.4688 | 121.7697 | -1.1765 | 120.5246 | 0.06691 | -0.063415 | 0.015472 | -0.043331 | 0.059155 | 0.016907 | -0.08103 | -0.13523 | -0.035253 | -0.072894 | -0.065154 | 0.057392 | 0.02322 | -0.04722 | 0.056344 | 0.11269 | -0.017639 | 0.061248 | 0.002445 | 0.10493 | 0.062683 | -0.035254 | -0.089454 | 0.010523 | -0.027118 | -0.019378 | 0.10317 | 0.068996 | -0.001444 | 0.10212 | -0.19262 | -0.08801 | -0.13029 | -0.025674
3550.1875 | 121.8109 | -0.94757 | 120.7123 | 0.06691 | -0.067994 | 0.020051 | -0.047909 | 0.063733 | 0.026064 | -0.085608 | -0.13523 | -0.021517 | -0.077472 | -0.065154 | 0.057392 | 0.027798 | -0.042641 | 0.056344 | 0.11269 | -0.022218 | 0.065827 | -0.002133 | 0.10951 | 0.07184 | -0.039832 | -0.089454 | 0.024259 | -0.031696 | -0.019378 | 0.10317 | 0.073574 | 0.003135 | 0.10212 | -0.19262 | -0.092589 | -0.13486 | -0.034831
3551.9688 | 121.7285 | -0.96588 | 120.7352 | 0.06691 | -0.072572 | 0.024629 | -0.038752 | 0.06831 | 0.030642 | -0.085608 | -0.13523 | -0.030674 | -0.08205 | -0.069733 | 0.06197 | 0.027798 | -0.04722 | 0.051766 | 0.11269 | -0.026796 | 0.070405 | 0.007024 | 0.11409 | 0.076418 | -0.039832 | -0.089454 | 0.015102 | -0.036274 | -0.023957 | 0.10775 | 0.073574 | -0.001444 | 0.097542 | -0.1972 | -0.08801 | -0.14402 | -0.03483
3553.75 | 121.8018 | -0.99335 | 120.6573 | 0.062332 | -0.067994 | 0.010893 | -0.047909 | 0.054577 | 0.016907 | -0.085608 | -0.13523 | -0.026096 | -0.077472 | -0.069733 | 0.048236 | 0.027798 | -0.042641 | 0.056344 | 0.10811 | -0.022218 | 0.056669 | -0.002133 | 0.10035 | 0.062683 | -0.039832 | -0.089454 | 0.01968 | -0.031696 | -0.023957 | 0.094012 | 0.073574 | 0.003135 | 0.10212 | -0.18347 | -0.092589 | -0.12571 | -0.034831
3555.5312 | 121.6873 | -1.2085 | 120.52 | 0.076067 | -0.058836 | 0.015472 | -0.043331 | 0.06831 | 0.026064 | -0.076452 | -0.13981 | -0.030674 | -0.08205 | -0.069733 | 0.057392 | 0.02322 | -0.042641 | 0.065501 | 0.12184 | -0.01306 | 0.061248 | 0.002445 | 0.11409 | 0.07184 | -0.030676 | -0.094033 | 0.015102 | -0.036274 | -0.023957 | 0.10317 | 0.068996 | 0.003135 | 0.11128 | -0.1972 | -0.097168 | -0.13944 | -0.039409
3557.2344 | 121.7743 | -0.81482 | 120.8679 | 0.06691 | -0.063415 | 0.015472 | -0.034174 | 0.063733 | 0.026064 | -0.076452 | -0.13981 | -0.030674 | -0.077472 | -0.069733 | 0.052814 | 0.02322 | -0.056376 | 0.056344 | 0.11269 | -0.017639 | 0.061248 | 0.011602 | 0.10951 | 0.07184 | -0.030676 | -0.094033 | 0.015102 | -0.031696 | -0.023957 | 0.09859 | 0.068996 | -0.0106 | 0.10212 | -0.19262 | -0.083433 | -0.13029 | -0.021096
3559.0312 | 121.7102 | -1.1078 | 120.6436 | 0.06691 | -0.063415 | 0.006315 | -0.043331 | 0.063733 | 0.030642 | -0.08103 | -0.14439 | -0.026096 | -0.086628 | -0.074312 | 0.057392 | 0.018642 | -0.04722 | 0.060923 | 0.11269 | -0.017639 | 0.052091 | 0.002445 | 0.10951 | 0.076418 | -0.035254 | -0.098611 | 0.01968 | -0.040852 | -0.028536 | 0.10317 | 0.064418 | -0.001444 | 0.1067 | -0.20178 | -0.097167 | -0.14402 | -0.039408
3560.8125 | 121.8201 | -1.1765 | 120.5109 | 0.06691 | -0.067994 | 0.015472 | -0.038752 | 0.054577 | 0.026064 | -0.085608 | -0.13981 | -0.026096 | -0.072894 | -0.069733 | 0.066548 | 0.02322 | -0.038063 | 0.051766 | 0.11269 | -0.022218 | 0.061248 | 0.007024 | 0.10035 | 0.07184 | -0.039832 | -0.094033 | 0.01968 | -0.027118 | -0.023957 | 0.11232 | 0.068996 | 0.007713 | 0.097542 | -0.20636 | -0.10175 | -0.13944 | -0.034831
3562.5938 | 121.8338 | -1.7395 | 119.9295 | 0.06691 | -0.058836 | 0.010893 | -0.052488 | 0.059155 | 0.026064 | -0.090186 | -0.13981 | -0.021517 | -0.077472 | -0.069733 | 0.057392 | 0.02322 | -0.04722 | 0.060923 | 0.11269 | -0.01306 | 0.056669 | -0.006712 | 0.10493 | 0.07184 | -0.04441 | -0.094033 | 0.024259 | -0.031696 | -0.023957 | 0.10317 | 0.068996 | -0.001444 | 0.1067 | -0.1972 | -0.092589 | -0.13486 | -0.030252
3564.375 | 121.7651 | -1.8585 | 119.8013 | 0.076067 | -0.063415 | 0.020051 | -0.038752 | 0.059155 | 0.026064 | -0.076452 | -0.13981 | -0.035253 | -0.08205 | -0.069733 | 0.052814 | 0.018642 | -0.042641 | 0.056344 | 0.12184 | -0.017639 | 0.065827 | 0.007024 | 0.10493 | 0.07184 | -0.030676 | -0.094033 | 0.010523 | -0.036274 | -0.023957 | 0.09859 | 0.064418 | 0.003135 | 0.10212 | -0.19262 | -0.097168 | -0.13486 | -0.039409
3566.1406 | 121.8155 | -1.8082 | 119.8288 | 0.06691 | -0.063415 | 0.010893 | -0.043331 | 0.059155 | 0.030642 | -0.085608 | -0.14439 | -0.026096 | -0.068315 | -0.069733 | 0.06197 | 0.018642 | -0.04722 | 0.060923 | 0.11269 | -0.017639 | 0.056669 | 0.002445 | 0.10493 | 0.076418 | -0.039832 | -0.098611 | 0.01968 | -0.022539 | -0.023957 | 0.10775 | 0.064418 | -0.001444 | 0.1067 | -0.20636 | -0.097167 | -0.13028 | -0.021095
3567.9219 | 121.7606 | -1.8448 | 119.8471 | 0.071489 | -0.063415 | 0.010893 | -0.043331 | 0.059155 | 0.026064 | -0.085608 | -0.13523 | -0.021517 | -0.077472 | -0.074312 | 0.06197 | 0.02322 | -0.051798 | 0.056344 | 0.11726 | -0.017639 | 0.056669 | 0.002445 | 0.10493 | 0.07184 | -0.039832 | -0.089454 | 0.024259 | -0.031696 | -0.028536 | 0.10775 | 0.068996 | -0.006022 | 0.10212 | -0.1972 | -0.083432 | -0.13944 | -0.025674
3569.6562 | 121.7651 | -2.2614 | 119.4168 | 0.071489 | -0.063415 | 0.015472 | -0.038752 | 0.059155 | 0.030642 | -0.08103 | -0.13981 | -0.026096 | -0.08205 | -0.069733 | 0.052814 | 0.018642 | -0.04722 | 0.060923 | 0.11726 | -0.017639 | 0.061248 | 0.007024 | 0.10493 | 0.076418 | -0.035254 | -0.094033 | 0.01968 | -0.036274 | -0.023957 | 0.09859 | 0.064418 | -0.001444 | 0.1067 | -0.19262 | -0.092589 | -0.13486 | -0.03483
3571.4375 | 121.7697 | -2.0325 | 119.6182 | 0.076067 | -0.063415 | 0.010893 | -0.043331 | 0.063733 | 0.021485 | -0.085608 | -0.13523 | -0.021517 | -0.072894 | -0.065154 | 0.057392 | 0.02322 | -0.042641 | 0.056344 | 0.12184 | -0.017639 | 0.056669 | 0.002445 | 0.10951 | 0.067261 | -0.039832 | -0.089454 | 0.024259 | -0.027118 | -0.019378 | 0.10317 | 0.068996 | 0.003135 | 0.10212 | -0.19262 | -0.092589 | -0.13029 | -0.030253
3573.2188 | 121.7148 | -2.0462 | 119.6915 | 0.076067 | -0.054257 | 0.024629 | -0.043331 | 0.063733 | 0.035221 | -0.08103 | -0.13523 | -0.030674 | -0.077472 | -0.074312 | 0.048236 | 0.018642 | -0.038063 | 0.056344 | 0.12184 | -0.008481 | 0.070405 | 0.002445 | 0.10951 | 0.080997 | -0.035254 | -0.089454 | 0.015102 | -0.031696 | -0.028536 | 0.094012 | 0.064418 | 0.007713 | 0.10212 | -0.18347 | -0.097167 | -0.12571 | -0.039409
3574.9531 | 121.8201 | -2.2614 | 119.4214 | 0.071489 | -0.058836 | 0.020051 | -0.034174 | 0.063733 | 0.030642 | -0.08103 | -0.13523 | -0.030674 | -0.068315 | -0.069733 | 0.06197 | 0.02322 | -0.04722 | 0.060923 | 0.11726 | -0.01306 | 0.065827 | 0.011602 | 0.10951 | 0.076418 | -0.035254 | -0.089454 | 0.015102 | -0.022539 | -0.023957 | 0.10775 | 0.068996 | -0.001444 | 0.1067 | -0.1972 | -0.08801 | -0.13028 | -0.021095
3576.7344 | 121.7468 | -2.655 | 119.046 | 0.071489 | -0.058836 | 0.020051 | -0.038752 | 0.063733 | 0.026064 | -0.076452 | -0.13523 | -0.026096 | -0.072894 | -0.074312 | 0.06197 | 0.027798 | -0.056376 | 0.060923 | 0.11726 | -0.01306 | 0.065827 | 0.007024 | 0.10951 | 0.07184 | -0.030676 | -0.089454 | 0.01968 | -0.027118 | -0.028536 | 0.10775 | 0.073574 | -0.0106 | 0.1067 | -0.1972 | -0.078854 | -0.13486 | -0.016518
3578.5 | 121.6873 | -2.6688 | 119.0186 | 0.076067 | -0.054257 | 0.010893 | -0.043331 | 0.063733 | 0.026064 | -0.08103 | -0.13981 | -0.030674 | -0.077472 | -0.065154 | 0.048236 | 0.02322 | -0.056376 | 0.056344 | 0.12184 | -0.008481 | 0.056669 | 0.002445 | 0.10951 | 0.07184 | -0.035254 | -0.094033 | 0.015102 | -0.031696 | -0.019378 | 0.094012 | 0.068996 | -0.0106 | 0.10212 | -0.18804 | -0.083433 | -0.12571 | -0.021096
3580.2344 | 121.6827 | -2.7969 | 118.7988 | 0.076067 | -0.058836 | 0.015472 | -0.043331 | 0.059155 | 0.021485 | -0.085608 | -0.13981 | -0.026096 | -0.077472 | -0.074312 | 0.057392 | 0.018642 | -0.051798 | 0.056344 | 0.12184 | -0.01306 | 0.061248 | 0.002445 | 0.10493 | 0.067261 | -0.039832 | -0.094033 | 0.01968 | -0.031696 | -0.028536 | 0.10317 | 0.064418 | -0.006022 | 0.10212 | -0.1972 | -0.088011 | -0.13486 | -0.025674
3582.0469 | 121.6232 | -2.9114 | 118.7439 | 0.06691 | -0.058836 | 0.015472 | -0.034174 | 0.072888 | 0.026064 | -0.08103 | -0.13523 | -0.026096 | -0.077472 | -0.069733 | 0.06197 | 0.027798 | -0.04722 | 0.056344 | 0.11269 | -0.01306 | 0.061248 | 0.011602 | 0.11866 | 0.07184 | -0.035254 | -0.089454 | 0.01968 | -0.031696 | -0.023957 | 0.10775 | 0.073574 | -0.001444 | 0.10212 | -0.1972 | -0.08801 | -0.13944 | -0.030252
3583.8281 | 121.6736 | -2.9572 | 118.6111 | 0.076067 | -0.058836 | 0.024629 | -0.038752 | 0.059155 | 0.026064 | -0.085608 | -0.13981 | -0.030674 | -0.072894 | -0.074312 | 0.052814 | 0.018642 | -0.042641 | 0.051766 | 0.12184 | -0.01306 | 0.070405 | 0.007024 | 0.10493 | 0.07184 | -0.039832 | -0.094033 | 0.015102 | -0.027118 | -0.028536 | 0.09859 | 0.064418 | 0.003135 | 0.097542 | -0.19262 | -0.097168 | -0.12571 | -0.030253
3585.5469 | 121.6644 | -3.0396 | 118.5196 | 0.071489 | -0.058836 | 0.020051 | -0.034174 | 0.06831 | 0.026064 | -0.08103 | -0.13981 | -0.021517 | -0.068315 | -0.074312 | 0.057392 | 0.027798 | -0.04722 | 0.056344 | 0.11726 | -0.01306 | 0.065827 | 0.011602 | 0.11409 | 0.07184 | -0.035254 | -0.094033 | 0.024259 | -0.022539 | -0.028536 | 0.10317 | 0.073574 | -0.001444 | 0.10212 | -0.1972 | -0.092589 | -0.12571 | -0.021095
3587.3125 | 121.7056 | -3.0808 | 118.428 | 0.06691 | -0.058836 | 0.020051 | -0.043331 | 0.06831 | 0.026064 | -0.085608 | -0.13523 | -0.021517 | -0.068315 | -0.065154 | 0.052814 | 0.02322 | -0.04722 | 0.056344 | 0.11269 | -0.01306 | 0.065827 | 0.002445 | 0.11409 | 0.07184 | -0.039832 | -0.089454 | 0.024259 | -0.022539 | -0.019378 | 0.09859 | 0.068996 | -0.001444 | 0.10212 | -0.18804 | -0.08801 | -0.12113 | -0.021095
3589.0781 | 121.6461 | -3.1586 | 118.3777 | 0.06691 | -0.058836 | 0.024629 | -0.038752 | 0.063733 | 0.030642 | -0.085608 | -0.13523 | -0.026096 | -0.077472 | -0.069733 | 0.052814 | 0.032376 | -0.04722 | 0.056344 | 0.11269 | -0.01306 | 0.070405 | 0.007024 | 0.10951 | 0.076418 | -0.039832 | -0.089454 | 0.01968 | -0.031696 | -0.023957 | 0.09859 | 0.078152 | -0.001444 | 0.10212 | -0.18804 | -0.08801 | -0.13029 | -0.030252
3590.875 | 121.6187 | -3.186 | 118.3868 | 0.076067 | -0.058836 | 0.015472 | -0.034174 | 0.063733 | 0.030642 | -0.08103 | -0.13981 | -0.026096 | -0.077472 | -0.060575 | 0.057392 | 0.02322 | -0.04722 | 0.060923 | 0.12184 | -0.01306 | 0.061248 | 0.011602 | 0.10951 | 0.076418 | -0.035254 | -0.094033 | 0.01968 | -0.031696 | -0.014799 | 0.10317 | 0.068996 | -0.001444 | 0.1067 | -0.1972 | -0.092589 | -0.13486 | -0.030252
3592.5938 | 121.6599 | -3.9139 | 117.572 | 0.071489 | -0.063415 | 0.015472 | -0.034174 | 0.063733 | 0.026064 | -0.085608 | -0.13981 | -0.030674 | -0.068315 | -0.065154 | 0.048236 | 0.018642 | -0.051798 | 0.056344 | 0.11726 | -0.017639 | 0.061248 | 0.011602 | 0.10951 | 0.07184 | -0.039832 | -0.094033 | 0.015102 | -0.022539 | -0.019378 | 0.094012 | 0.064418 | -0.006022 | 0.10212 | -0.18804 | -0.088011 | -0.11655 | -0.016517
3594.375 | 121.6324 | -3.5751 | 118.0435 | 0.071489 | -0.063415 | 0.020051 | -0.038752 | 0.059155 | 0.026064 | -0.085608 | -0.14439 | -0.021517 | -0.08205 | -0.069733 | 0.052814 | 0.02322 | -0.04722 | 0.051766 | 0.11726 | -0.017639 | 0.065827 | 0.007024 | 0.10493 | 0.07184 | -0.039832 | -0.098611 | 0.024259 | -0.036274 | -0.023957 | 0.09859 | 0.068996 | -0.001444 | 0.097542 | -0.1972 | -0.097167 | -0.13486 | -0.03483
3596.1094 | 121.6553 | -7.7133 | 113.7268 | 0.076067 | -0.063415 | 0.020051 | -0.038752 | 0.072888 | 0.035221 | -0.071874 | -0.13065 | -0.030674 | -0.072894 | -0.065154 | 0.052814 | 0.014064 | -0.04722 | 0.047188 | 0.12184 | -0.017639 | 0.065827 | 0.007024 | 0.11866 | 0.080997 | -0.026098 | -0.084876 | 0.015102 | -0.027118 | -0.019378 | 0.09859 | 0.05984 | -0.001444 | 0.092964 | -0.18347 | -0.083432 | -0.12571 | -0.025674
3597.8906 | 121.6003 | -3.8727 | 117.7048 | 0.071489 | -0.054257 | 0.024629 | -0.038752 | 0.063733 | 0.026064 | -0.076452 | -0.13523 | -0.021517 | -0.072894 | -0.060575 | 0.052814 | 0.02322 | -0.051798 | 0.051766 | 0.11726 | -0.008481 | 0.070405 | 0.007024 | 0.10951 | 0.07184 | -0.030676 | -0.089454 | 0.024259 | -0.027118 | -0.014799 | 0.09859 | 0.068996 | -0.006022 | 0.097542 | -0.18804 | -0.083432 | -0.12571 | -0.021096
3599.6719 | 121.6141 | -4.1885 | 117.3615 | 0.071489 | -0.058836 | 0.024629 | -0.034174 | 0.06831 | 0.030642 | -0.076452 | -0.13523 | -0.030674 | -0.072894 | -0.069733 | 0.057392 | 0.018642 | -0.042641 | 0.056344 | 0.11726 | -0.01306 | 0.070405 | 0.011602 | 0.11409 | 0.076418 | -0.030676 | -0.089454 | 0.015102 | -0.027118 | -0.023957 | 0.10317 | 0.064418 | 0.003135 | 0.10212 | -0.19262 | -0.092589 | -0.13029 | -0.030253
3601.4375 | 121.7102 | -4.3121 | 117.2379 | 0.06691 | -0.058836 | 0.015472 | -0.034174 | 0.059155 | 0.030642 | -0.085608 | -0.13523 | -0.026096 | -0.077472 | -0.074312 | 0.052814 | 0.014064 | -0.051798 | 0.056344 | 0.11269 | -0.01306 | 0.061248 | 0.011602 | 0.10493 | 0.076418 | -0.039832 | -0.089454 | 0.01968 | -0.031696 | -0.028536 | 0.09859 | 0.05984 | -0.006022 | 0.10212 | -0.18804 | -0.083432 | -0.13029 | -0.025674
3603.1562 | 121.6827 | -4.3808 | 117.1143 | 0.071489 | -0.058836 | 0.020051 | -0.034174 | 0.054577 | 0.030642 | -0.085608 | -0.13981 | -0.030674 | -0.077472 | -0.065154 | 0.052814 | 0.027798 | -0.051798 | 0.060923 | 0.11726 | -0.01306 | 0.065827 | 0.011602 | 0.10035 | 0.076418 | -0.039832 | -0.094033 | 0.015102 | -0.031696 | -0.019378 | 0.09859 | 0.073574 | -0.006022 | 0.1067 | -0.19262 | -0.088011 | -0.13029 | -0.025674
3604.9375 | 121.6919 | -4.5181 | 116.9724 | 0.071489 | -0.058836 | 0.020051 | -0.034174 | 0.06831 | 0.030642 | -0.085608 | -0.13065 | -0.030674 | -0.072894 | -0.065154 | 0.057392 | 0.027798 | -0.04722 | 0.056344 | 0.11726 | -0.01306 | 0.065827 | 0.011602 | 0.11409 | 0.076418 | -0.039832 | -0.084876 | 0.015102 | -0.027118 | -0.019378 | 0.10317 | 0.073574 | -0.001444 | 0.10212 | -0.18804 | -0.083432 | -0.13029 | -0.025674
3606.6562 | 121.6095 | -6.3858 | 115.0635 | 0.076067 | -0.058836 | 0.015472 | -0.038752 | 0.072888 | 0.026064 | -0.085608 | -0.13523 | -0.026096 | -0.077472 | -0.069733 | 0.052814 | 0.018642 | -0.04722 | 0.051766 | 0.12184 | -0.01306 | 0.061248 | 0.007024 | 0.11866 | 0.07184 | -0.039832 | -0.089454 | 0.01968 | -0.031696 | -0.023957 | 0.09859 | 0.064418 | -0.001444 | 0.097542 | -0.18804 | -0.08801 | -0.13029 | -0.030252
3608.4219 | 121.6095 | -8.2214 | 113.1454 | 0.085224 | -0.054257 | 0.024629 | -0.043331 | 0.072888 | 0.030642 | -0.076452 | -0.12607 | -0.021517 | -0.072894 | -0.060575 | 0.057392 | 0.018642 | -0.051798 | 0.04261 | 0.131 | -0.008481 | 0.070405 | 0.002445 | 0.11866 | 0.076418 | -0.030676 | -0.080297 | 0.024259 | -0.027118 | -0.014799 | 0.10317 | 0.064418 | -0.006022 | 0.088386 | -0.18346 | -0.074275 | -0.13029 | -0.021096
3610.1562 | 121.5179 | -8.3496 | 113.0219 | 0.076067 | -0.058836 | 0.024629 | -0.038752 | 0.06831 | 0.026064 | -0.085608 | -0.12607 | -0.026096 | -0.068315 | -0.065154 | 0.048236 | 0.018642 | -0.060955 | 0.051766 | 0.12184 | -0.01306 | 0.070405 | 0.007024 | 0.11409 | 0.07184 | -0.039832 | -0.080297 | 0.01968 | -0.022539 | -0.019378 | 0.094012 | 0.064418 | -0.015179 | 0.097542 | -0.17431 | -0.065118 | -0.11655 | -0.00736
3611.9375 | 121.4355 | -10.8261 | 110.5499 | 0.076067 | -0.054257 | 0.029208 | -0.034174 | 0.06831 | 0.035221 | -0.076452 | -0.12607 | -0.026096 | -0.068315 | -0.069733 | 0.048236 | 0.009486 | -0.051798 | 0.04261 | 0.12184 | -0.008481 | 0.074984 | 0.011602 | 0.11409 | 0.080997 | -0.030676 | -0.080297 | 0.01968 | -0.022539 | -0.023957 | 0.094012 | 0.055262 | -0.006022 | 0.088386 | -0.17431 | -0.074275 | -0.11655 | -0.016517
3613.7188 | 121.4905 | -9.169 | 112.1613 | 0.076067 | -0.049678 | 0.020051 | -0.034174 | 0.063733 | 0.026064 | -0.071874 | -0.12607 | -0.012359 | -0.072894 | -0.065154 | 0.052814 | 0.014064 | -0.051798 | 0.047188 | 0.12184 | -0.003902 | 0.065827 | 0.011602 | 0.10951 | 0.07184 | -0.026098 | -0.080297 | 0.033417 | -0.027118 | -0.019378 | 0.09859 | 0.05984 | -0.006022 | 0.092964 | -0.17889 | -0.074275 | -0.12571 | -0.021096
3615.4531 | 121.4218 | -9.9976 | 111.3419 | 0.076067 | -0.058836 | 0.024629 | -0.029595 | 0.063733 | 0.035221 | -0.076452 | -0.12607 | -0.021517 | -0.063737 | -0.055996 | 0.048236 | 0.014064 | -0.04722 | 0.047188 | 0.12184 | -0.01306 | 0.070405 | 0.016181 | 0.10951 | 0.080997 | -0.030676 | -0.080297 | 0.024259 | -0.017961 | -0.01022 | 0.094012 | 0.05984 | -0.001444 | 0.092964 | -0.17431 | -0.078853 | -0.11197 | -0.016517
3617.2344 | 121.3348 | -11.4532 | 109.8404 | 0.076067 | -0.058836 | 0.033786 | -0.020438 | 0.06831 | 0.035221 | -0.076452 | -0.12607 | -0.016938 | -0.063737 | -0.065154 | 0.048236 | 0.018642 | -0.051798 | 0.04261 | 0.12184 | -0.01306 | 0.079562 | 0.025338 | 0.11409 | 0.080997 | -0.030676 | -0.080297 | 0.028838 | -0.017961 | -0.019378 | 0.094012 | 0.064418 | -0.006022 | 0.088386 | -0.17431 | -0.074275 | -0.11197 | -0.011939
3619.0156 | 121.4401 | -12.9227 | 108.2153 | 0.080646 | -0.063415 | 0.029208 | -0.034174 | 0.06831 | 0.039799 | -0.076452 | -0.12607 | -0.016938 | -0.072894 | -0.055996 | 0.048236 | 0.014064 | -0.051798 | 0.051766 | 0.12642 | -0.017639 | 0.074984 | 0.011602 | 0.11409 | 0.085575 | -0.030676 | -0.080297 | 0.028838 | -0.027118 | -0.01022 | 0.094012 | 0.05984 | -0.006022 | 0.097542 | -0.17431 | -0.074275 | -0.12113 | -0.021096
3620.7344 | 121.3211 | -13.8519 | 107.3135 | 0.076067 | -0.049678 | 0.020051 | -0.029595 | 0.06831 | 0.035221 | -0.076452 | -0.12607 | -0.016938 | -0.068315 | -0.060575 | 0.048236 | 0.014064 | -0.04722 | 0.04261 | 0.12184 | -0.003902 | 0.065827 | 0.016181 | 0.11409 | 0.080997 | -0.030676 | -0.080297 | 0.028838 | -0.022539 | -0.014799 | 0.094012 | 0.05984 | -0.001444 | 0.088386 | -0.17431 | -0.078853 | -0.11655 | -0.021095
3622.5156 | 121.3211 | -16.246 | 104.7775 | 0.089802 | -0.058836 | 0.024629 | -0.025017 | 0.077466 | 0.044377 | -0.071874 | -0.12607 | -0.012359 | -0.068315 | -0.060575 | 0.039079 | 0.009486 | -0.051798 | 0.038032 | 0.13558 | -0.01306 | 0.070405 | 0.020759 | 0.12324 | 0.090153 | -0.026098 | -0.080297 | 0.033417 | -0.022539 | -0.014799 | 0.084855 | 0.055262 | -0.006022 | 0.083808 | -0.16515 | -0.074275 | -0.10739 | -0.016517
3624.3125 | 121.2479 | -11.499 | 109.7351 | 0.080646 | -0.049678 | 0.029208 | -0.029595 | 0.077466 | 0.030642 | -0.08103 | -0.12607 | -0.021517 | -0.068315 | -0.060575 | 0.048236 | 0.009486 | -0.042641 | 0.056344 | 0.12642 | -0.003902 | 0.074984 | 0.016181 | 0.12324 | 0.076418 | -0.035254 | -0.080297 | 0.024259 | -0.022539 | -0.014799 | 0.094012 | 0.055262 | 0.003135 | 0.10212 | -0.17431 | -0.083432 | -0.11655 | -0.025674
3626.0312 | 121.3989 | -9.3704 | 111.795 | 0.080646 | -0.058836 | 0.024629 | -0.025017 | 0.077466 | 0.035221 | -0.08103 | -0.13065 | -0.016938 | -0.063737 | -0.065154 | 0.048236 | 0.018642 | -0.04722 | 0.051766 | 0.12642 | -0.01306 | 0.070405 | 0.020759 | 0.12324 | 0.080997 | -0.035254 | -0.084876 | 0.028838 | -0.017961 | -0.019378 | 0.094012 | 0.064418 | -0.001444 | 0.097542 | -0.17889 | -0.083432 | -0.11197 | -0.016517
3627.8125 | 121.1929 | -15.6143 | 105.4871 | 0.080646 | -0.054257 | 0.029208 | -0.025017 | 0.077466 | 0.030642 | -0.067295 | -0.12607 | -0.012359 | -0.068315 | -0.051417 | 0.043657 | 0.014064 | -0.04722 | 0.038032 | 0.12642 | -0.008481 | 0.074984 | 0.020759 | 0.12324 | 0.076418 | -0.021519 | -0.080297 | 0.033417 | -0.022539 | -0.005641 | 0.089433 | 0.05984 | -0.001444 | 0.083808 | -0.16973 | -0.078853 | -0.11197 | -0.021095
3629.5938 | 121.051 | -17.514 | 103.3997 | 0.089802 | -0.0451 | 0.038365 | -0.025017 | 0.077466 | 0.044377 | -0.062717 | -0.12607 | -0.012359 | -0.059159 | -0.055996 | 0.034501 | 0.009486 | -0.056376 | 0.04261 | 0.13558 | 0.000676 | 0.084141 | 0.020759 | 0.12324 | 0.090153 | -0.016941 | -0.080297 | 0.033417 | -0.013383 | -0.01022 | 0.080277 | 0.055262 | -0.0106 | 0.088386 | -0.16057 | -0.069697 | -0.09366 | -0.002783
3631.375 | 121.0098 | -23.6252 | 97.2107 | 0.089802 | -0.040521 | 0.038365 | -0.011281 | 0.082044 | 0.044377 | -0.067295 | -0.1215 | -0.003202 | -0.059159 | -0.055996 | 0.043657 | 0.004908 | -0.051798 | 0.038032 | 0.13558 | 0.005255 | 0.084141 | 0.034495 | 0.12782 | 0.090153 | -0.021519 | -0.075719 | 0.042574 | -0.013383 | -0.01022 | 0.089433 | 0.050684 | -0.006022 | 0.083808 | -0.16515 | -0.069697 | -0.10282 | -0.007361
3633.1094 | 120.9549 | -21.7667 | 99.0555 | 0.089802 | -0.040521 | 0.033786 | -0.025017 | 0.082044 | 0.048956 | -0.067295 | -0.10776 | -0.00778 | -0.059159 | -0.046838 | 0.029923 | 0.004908 | -0.04722 | 0.028875 | 0.13558 | 0.005255 | 0.079562 | 0.020759 | 0.12782 | 0.094732 | -0.021519 | -0.061983 | 0.037996 | -0.013383 | -0.001062 | 0.075699 | 0.050684 | -0.001444 | 0.074651 | -0.13768 | -0.060539 | -0.089082 | -0.011939
3634.8906 | 120.9366 | -23.1583 | 97.5128 | 0.098959 | -0.035942 | 0.038365 | -0.01586 | 0.086622 | 0.048956 | -0.058139 | -0.11234 | -0.003202 | -0.05458 | -0.042259 | 0.029923 | -0.008827 | -0.056376 | 0.028875 | 0.14474 | 0.009834 | 0.084141 | 0.029916 | 0.1324 | 0.094732 | -0.012363 | -0.066562 | 0.042574 | -0.008804 | 0.003517 | 0.075699 | 0.036949 | -0.0106 | 0.074651 | -0.14226 | -0.055962 | -0.084503 | 0.001796
3636.6719 | 120.7535 | -22.2839 | 98.2361 | 0.10354 | -0.040521 | 0.047522 | -0.01586 | 0.095778 | 0.058113 | -0.048983 | -0.10776 | 0.001377 | -0.045424 | -0.033101 | 0.020767 | -0.008827 | -0.051798 | 0.024297 | 0.14931 | 0.005255 | 0.093298 | 0.029916 | 0.14155 | 0.10389 | -0.003207 | -0.061983 | 0.047153 | 0.000352 | 0.012675 | 0.066543 | 0.036949 | -0.006022 | 0.070073 | -0.12853 | -0.055961 | -0.066191 | 0.006374
3638.375 | 120.7443 | -20.7825 | 99.678 | 0.10354 | -0.035942 | 0.042944 | -0.011281 | 0.0912 | 0.053534 | -0.058139 | -0.10776 | -0.003202 | -0.050002 | -0.042259 | 0.025345 | -0.004248 | -0.051798 | 0.028875 | 0.14931 | 0.009834 | 0.08872 | 0.034495 | 0.13698 | 0.09931 | -0.012363 | -0.061983 | 0.042574 | -0.004226 | 0.003517 | 0.071121 | 0.041528 | -0.006022 | 0.074651 | -0.1331 | -0.055961 | -0.075347 | 0.001796
3640.1562 | 120.5658 | -24.559 | 95.9427 | 0.10812 | -0.035942 | 0.047522 | -0.011281 | 0.0912 | 0.053534 | -0.053561 | -0.11234 | 0.010535 | -0.050002 | -0.042259 | 0.020767 | -0.008827 | -0.051798 | 0.033454 | 0.15389 | 0.009834 | 0.093298 | 0.034495 | 0.13698 | 0.09931 | -0.007785 | -0.066562 | 0.056311 | -0.004226 | 0.003517 | 0.066543 | 0.036949 | -0.006022 | 0.07923 | -0.13311 | -0.06054 | -0.070769 | 0.001796
3641.9375 | 120.4056 | -21.048 | 99.1974 | 0.094381 | -0.031363 | 0.047522 | -0.01586 | 0.0912 | 0.053534 | -0.053561 | -0.10776 | 0.001377 | -0.045424 | -0.042259 | 0.025345 | -0.004248 | -0.056376 | 0.033454 | 0.14016 | 0.014413 | 0.093298 | 0.029916 | 0.13698 | 0.09931 | -0.007785 | -0.061983 | 0.047153 | 0.000352 | 0.003517 | 0.071121 | 0.041528 | -0.0106 | 0.07923 | -0.1331 | -0.051383 | -0.070769 | 0.010952
3643.7188 | 120.0119 | -24.4171 | 95.5307 | 0.10812 | -0.031363 | 0.052101 | 0.002454 | 0.10036 | 0.058113 | -0.058139 | -0.10776 | 0.010535 | -0.045424 | -0.028522 | 0.020767 | -0.013405 | -0.051798 | 0.015141 | 0.15389 | 0.014413 | 0.097877 | 0.04823 | 0.14613 | 0.10389 | -0.012363 | -0.061983 | 0.056311 | 0.000352 | 0.017254 | 0.066543 | 0.032371 | -0.006022 | 0.060917 | -0.12853 | -0.055961 | -0.066191 | 0.006374
3645.5 | 121.0602 | -0.11444 | 120.8954 | 0.076067 | -0.067994 | 0.015472 | -0.034174 | 0.059155 | 0.026064 | -0.08103 | -0.13065 | -0.030674 | -0.072894 | -0.069733 | 0.052814 | 0.018642 | -0.042641 | 0.056344 | 0.12184 | -0.022218 | 0.061248 | 0.011602 | 0.10493 | 0.07184 | -0.035254 | -0.084876 | 0.015102 | -0.027118 | -0.023957 | 0.09859 | 0.064418 | 0.003135 | 0.10212 | -0.18347 | -0.088011 | -0.12571 | -0.030253
3647.2188 | 121.0693 | -0.15106 | 121.0602 | 0.071489 | -0.063415 | 0.015472 | -0.034174 | 0.072888 | 0.035221 | -0.08103 | -0.13981 | -0.030674 | -0.072894 | -0.060575 | 0.052814 | 0.027798 | -0.051798 | 0.051766 | 0.11726 | -0.017639 | 0.061248 | 0.011602 | 0.11866 | 0.080997 | -0.035254 | -0.094033 | 0.015102 | -0.027118 | -0.014799 | 0.09859 | 0.073574 | -0.006022 | 0.097542 | -0.19262 | -0.088011 | -0.12571 | -0.021096
3649 | 121.2753 | -0.11902 | 121.0373 | 0.06691 | -0.063415 | 0.020051 | -0.025017 | 0.063733 | 0.016907 | -0.08103 | -0.13981 | -0.026096 | -0.072894 | -0.065154 | 0.052814 | 0.018642 | -0.042641 | 0.056344 | 0.11269 | -0.017639 | 0.065827 | 0.020759 | 0.10951 | 0.062683 | -0.035254 | -0.094033 | 0.01968 | -0.027118 | -0.019378 | 0.09859 | 0.064418 | 0.003135 | 0.10212 | -0.19262 | -0.097168 | -0.12571 | -0.030253
3650.7812 | 121.257 | -0.12817 | 121.1105 | 0.071489 | -0.067994 | 0.020051 | -0.038752 | 0.06831 | 0.030642 | -0.085608 | -0.13523 | -0.021517 | -0.077472 | -0.069733 | 0.06197 | 0.018642 | -0.051798 | 0.051766 | 0.11726 | -0.022218 | 0.065827 | 0.007024 | 0.11409 | 0.076418 | -0.039832 | -0.089454 | 0.024259 | -0.031696 | -0.023957 | 0.10775 | 0.064418 | -0.006022 | 0.097542 | -0.1972 | -0.083432 | -0.13944 | -0.025674
3652.5625 | 121.2112 | -0.14648 | 121.138 | 0.071489 | -0.058836 | 0.020051 | -0.034174 | 0.072888 | 0.026064 | -0.08103 | -0.13981 | -0.021517 | -0.077472 | -0.069733 | 0.052814 | 0.02322 | -0.042641 | 0.051766 | 0.11726 | -0.01306 | 0.065827 | 0.011602 | 0.11866 | 0.07184 | -0.035254 | -0.094033 | 0.024259 | -0.031696 | -0.023957 | 0.09859 | 0.068996 | 0.003135 | 0.097542 | -0.19262 | -0.097168 | -0.13029 | -0.034831
3654.3438 | 121.3165 | -0.11902 | 121.1609 | 0.06691 | -0.063415 | 0.020051 | -0.038752 | 0.06831 | 0.030642 | -0.085608 | -0.13523 | -0.016938 | -0.077472 | -0.069733 | 0.057392 | 0.02322 | -0.051798 | 0.051766 | 0.11269 | -0.017639 | 0.065827 | 0.007024 | 0.11409 | 0.076418 | -0.039832 | -0.089454 | 0.028838 | -0.031696 | -0.023957 | 0.10317 | 0.068996 | -0.006022 | 0.097542 | -0.19262 | -0.083432 | -0.13486 | -0.025674
3656.0781 | 121.3394 | -0.1236 | 121.1838 | 0.076067 | -0.063415 | 0.015472 | -0.034174 | 0.06831 | 0.030642 | -0.08103 | -0.13065 | -0.030674 | -0.072894 | -0.074312 | 0.057392 | 0.018642 | -0.042641 | 0.047188 | 0.12184 | -0.017639 | 0.061248 | 0.011602 | 0.11409 | 0.076418 | -0.035254 | -0.084876 | 0.015102 | -0.027118 | -0.028536 | 0.10317 | 0.064418 | 0.003135 | 0.092964 | -0.18804 | -0.088011 | -0.13029 | -0.030253
3657.875 | 121.3715 | -0.1236 | 121.1838 | 0.06691 | -0.058836 | 0.010893 | -0.038752 | 0.059155 | 0.026064 | -0.08103 | -0.13981 | -0.026096 | -0.072894 | -0.065154 | 0.052814 | 0.018642 | -0.056376 | 0.056344 | 0.11269 | -0.01306 | 0.056669 | 0.007024 | 0.10493 | 0.07184 | -0.035254 | -0.094033 | 0.01968 | -0.027118 | -0.019378 | 0.09859 | 0.064418 | -0.0106 | 0.10212 | -0.19262 | -0.083433 | -0.12571 | -0.016518
3659.5938 | 121.4355 | -0.10986 | 121.2112 | 0.076067 | -0.058836 | 0.015472 | -0.034174 | 0.063733 | 0.021485 | -0.090186 | -0.13065 | -0.021517 | -0.072894 | -0.069733 | 0.057392 | 0.02322 | -0.051798 | 0.051766 | 0.12184 | -0.01306 | 0.061248 | 0.011602 | 0.10951 | 0.067261 | -0.04441 | -0.084876 | 0.024259 | -0.027118 | -0.023957 | 0.10317 | 0.068996 | -0.006022 | 0.097542 | -0.18804 | -0.078854 | -0.13029 | -0.021096
3661.3594 | 121.4264 | -0.10986 | 121.1838 | 0.076067 | -0.054257 | 0.006315 | -0.034174 | 0.063733 | 0.026064 | -0.085608 | -0.13523 | -0.026096 | -0.077472 | -0.060575 | 0.048236 | 0.02322 | -0.04722 | 0.060923 | 0.12184 | -0.008481 | 0.052091 | 0.011602 | 0.10951 | 0.07184 | -0.039832 | -0.089454 | 0.01968 | -0.031696 | -0.014799 | 0.094012 | 0.068996 | -0.001444 | 0.1067 | -0.18347 | -0.08801 | -0.12571 | -0.030252
3663.1406 | 121.3348 | -0.17395 | 121.2524 | 0.071489 | -0.054257 | 0.015472 | -0.034174 | 0.06831 | 0.021485 | -0.08103 | -0.13523 | -0.026096 | -0.068315 | -0.069733 | 0.052814 | 0.027798 | -0.056376 | 0.051766 | 0.11726 | -0.008481 | 0.061248 | 0.011602 | 0.11409 | 0.067261 | -0.035254 | -0.089454 | 0.01968 | -0.022539 | -0.023957 | 0.09859 | 0.073574 | -0.0106 | 0.097542 | -0.18804 | -0.078854 | -0.12113 | -0.011939
3664.8594 | 121.3806 | -0.16937 | 121.2616 | 0.06691 | -0.054257 | 0.015472 | -0.034174 | 0.063733 | 0.035221 | -0.076452 | -0.13065 | -0.026096 | -0.072894 | -0.069733 | 0.066548 | 0.02322 | -0.04722 | 0.056344 | 0.11269 | -0.008481 | 0.061248 | 0.011602 | 0.10951 | 0.080997 | -0.030676 | -0.084876 | 0.01968 | -0.027118 | -0.023957 | 0.11232 | 0.068996 | -0.001444 | 0.10212 | -0.1972 | -0.083432 | -0.13944 | -0.025674
3666.6406 | 121.463 | -0.10986 | 121.2616 | 0.080646 | -0.054257 | 0.015472 | -0.034174 | 0.063733 | 0.035221 | -0.08103 | -0.13981 | -0.021517 | -0.072894 | -0.069733 | 0.052814 | 0.02322 | -0.038063 | 0.056344 | 0.12642 | -0.008481 | 0.061248 | 0.011602 | 0.10951 | 0.080997 | -0.035254 | -0.094033 | 0.024259 | -0.027118 | -0.023957 | 0.09859 | 0.068996 | 0.007713 | 0.10212 | -0.19262 | -0.10175 | -0.12571 | -0.034831
3668.4062 | 121.4401 | -0.14648 | 121.2799 | 0.076067 | -0.049678 | 0.015472 | -0.029595 | 0.063733 | 0.035221 | -0.090186 | -0.13065 | -0.035253 | -0.072894 | -0.069733 | 0.052814 | 0.014064 | -0.042641 | 0.047188 | 0.12184 | -0.003902 | 0.061248 | 0.016181 | 0.10951 | 0.080997 | -0.04441 | -0.084876 | 0.010523 | -0.027118 | -0.023957 | 0.09859 | 0.05984 | 0.003135 | 0.092964 | -0.18347 | -0.088011 | -0.12571 | -0.030253
3670.1875 | 121.4996 | -0.12817 | 121.2753 | 0.076067 | -0.054257 | 0.015472 | -0.038752 | 0.06831 | 0.026064 | -0.085608 | -0.13523 | -0.016938 | -0.077472 | -0.074312 | 0.06197 | 0.02322 | -0.04722 | 0.051766 | 0.12184 | -0.008481 | 0.061248 | 0.007024 | 0.11409 | 0.07184 | -0.039832 | -0.089454 | 0.028838 | -0.031696 | -0.028536 | 0.10775 | 0.068996 | -0.001444 | 0.097542 | -0.1972 | -0.08801 | -0.13944 | -0.030252
3671.9844 | 121.5408 | -0.10529 | 121.2982 | 0.071489 | -0.054257 | 0.010893 | -0.038752 | 0.06831 | 0.026064 | -0.085608 | -0.14439 | -0.030674 | -0.077472 | -0.060575 | 0.052814 | 0.027798 | -0.051798 | 0.060923 | 0.11726 | -0.008481 | 0.056669 | 0.007024 | 0.11409 | 0.07184 | -0.039832 | -0.098611 | 0.015102 | -0.031696 | -0.014799 | 0.09859 | 0.073574 | -0.006022 | 0.1067 | -0.1972 | -0.092589 | -0.13029 | -0.025674
3673.7031 | 121.4127 | -0.16022 | 121.3486 | 0.080646 | -0.054257 | 0.010893 | -0.029595 | 0.06831 | 0.026064 | -0.085608 | -0.13523 | -0.026096 | -0.072894 | -0.060575 | 0.052814 | 0.018642 | -0.056376 | 0.047188 | 0.12642 | -0.008481 | 0.056669 | 0.016181 | 0.11409 | 0.07184 | -0.039832 | -0.089454 | 0.01968 | -0.027118 | -0.014799 | 0.09859 | 0.064418 | -0.0106 | 0.092964 | -0.18804 | -0.078854 | -0.12571 | -0.016518
3675.4688 | 121.4813 | -0.14191 | 121.3669 | 0.076067 | -0.058836 | 0.024629 | -0.038752 | 0.059155 | 0.026064 | -0.076452 | -0.13523 | -0.030674 | -0.072894 | -0.069733 | 0.048236 | 0.02322 | -0.042641 | 0.060923 | 0.12184 | -0.01306 | 0.070405 | 0.007024 | 0.10493 | 0.07184 | -0.030676 | -0.089454 | 0.015102 | -0.027118 | -0.023957 | 0.094012 | 0.068996 | 0.003135 | 0.1067 | -0.18347 | -0.092589 | -0.12113 | -0.030253
3677.25 | 121.5958 | -0.09613 | 121.3303 | 0.06691 | -0.054257 | 0.020051 | -0.034174 | 0.06831 | 0.026064 | -0.08103 | -0.13981 | -0.026096 | -0.08205 | -0.065154 | 0.057392 | 0.014064 | -0.051798 | 0.047188 | 0.11269 | -0.008481 | 0.065827 | 0.011602 | 0.11409 | 0.07184 | -0.035254 | -0.094033 | 0.01968 | -0.036274 | -0.019378 | 0.10317 | 0.05984 | -0.006022 | 0.092964 | -0.1972 | -0.088011 | -0.13944 | -0.030252
3678.9688 | 121.582 | -0.10986 | 121.3165 | 0.071489 | -0.049678 | 0.020051 | -0.034174 | 0.059155 | 0.026064 | -0.085608 | -0.13981 | -0.026096 | -0.072894 | -0.065154 | 0.052814 | 0.018642 | -0.04722 | 0.056344 | 0.11726 | -0.003902 | 0.065827 | 0.011602 | 0.10493 | 0.07184 | -0.039832 | -0.094033 | 0.01968 | -0.027118 | -0.019378 | 0.09859 | 0.064418 | -0.001444 | 0.10212 | -0.19262 | -0.092589 | -0.12571 | -0.025674
3680.75 | 121.5866 | -0.13733 | 121.3531 | 0.06691 | -0.058836 | 0.010893 | -0.034174 | 0.063733 | 0.030642 | -0.085608 | -0.13523 | -0.016938 | -0.068315 | -0.065154 | 0.057392 | 0.027798 | -0.04722 | 0.04261 | 0.11269 | -0.01306 | 0.056669 | 0.011602 | 0.10951 | 0.076418 | -0.039832 | -0.089454 | 0.028838 | -0.022539 | -0.019378 | 0.10317 | 0.073574 | -0.001444 | 0.088386 | -0.19262 | -0.08801 | -0.12571 | -0.021095
3682.5312 | 121.6141 | -0.10529 | 121.3577 | 0.071489 | -0.058836 | 0.015472 | -0.034174 | 0.063733 | 0.026064 | -0.085608 | -0.12607 | -0.026096 | -0.072894 | -0.065154 | 0.057392 | 0.018642 | -0.04722 | 0.051766 | 0.11726 | -0.01306 | 0.061248 | 0.011602 | 0.10951 | 0.07184 | -0.039832 | -0.080297 | 0.01968 | -0.027118 | -0.019378 | 0.10317 | 0.064418 | -0.001444 | 0.097542 | -0.18346 | -0.078853 | -0.13029 | -0.025674
3684.25 | 121.6003 | -0.13733 | 121.3623 | 0.071489 | -0.049678 | 0.020051 | -0.029595 | 0.072888 | 0.016907 | -0.090186 | -0.12607 | -0.021517 | -0.072894 | -0.065154 | 0.057392 | 0.02322 | -0.056376 | 0.047188 | 0.11726 | -0.003902 | 0.065827 | 0.016181 | 0.11866 | 0.062683 | -0.04441 | -0.080297 | 0.024259 | -0.027118 | -0.019378 | 0.10317 | 0.068996 | -0.0106 | 0.092964 | -0.18346 | -0.069697 | -0.13029 | -0.016518
3686.0156 | 121.5912 | -0.14191 | 121.3989 | 0.071489 | -0.058836 | 0.015472 | -0.038752 | 0.06831 | 0.021485 | -0.08103 | -0.13523 | -0.030674 | -0.068315 | -0.074312 | 0.06197 | 0.02322 | -0.04722 | 0.051766 | 0.11726 | -0.01306 | 0.061248 | 0.007024 | 0.11409 | 0.067261 | -0.035254 | -0.089454 | 0.015102 | -0.022539 | -0.028536 | 0.10775 | 0.068996 | -0.001444 | 0.097542 | -0.1972 | -0.08801 | -0.13028 | -0.021095
3687.7969 | 121.5179 | -0.17853 | 121.4172 | 0.071489 | -0.054257 | 0.015472 | -0.034174 | 0.072888 | 0.026064 | -0.08103 | -0.13065 | -0.026096 | -0.068315 | -0.069733 | 0.057392 | 0.018642 | -0.042641 | 0.056344 | 0.11726 | -0.008481 | 0.061248 | 0.011602 | 0.11866 | 0.07184 | -0.035254 | -0.084876 | 0.01968 | -0.022539 | -0.023957 | 0.10317 | 0.064418 | 0.003135 | 0.10212 | -0.18804 | -0.088011 | -0.12571 | -0.025674
3689.5 | 121.6507 | -0.10986 | 121.376 | 0.071489 | -0.058836 | 0.015472 | -0.034174 | 0.059155 | 0.026064 | -0.08103 | -0.13523 | -0.021517 | -0.072894 | -0.069733 | 0.052814 | 0.018642 | -0.042641 | 0.056344 | 0.11726 | -0.01306 | 0.061248 | 0.011602 | 0.10493 | 0.07184 | -0.035254 | -0.089454 | 0.024259 | -0.027118 | -0.023957 | 0.09859 | 0.064418 | 0.003135 | 0.10212 | -0.18804 | -0.092589 | -0.12571 | -0.030253
3691.2812 | 121.5546 | -0.15564 | 121.4401 | 0.071489 | -0.049678 | 0.020051 | -0.038752 | 0.063733 | 0.026064 | -0.08103 | -0.13981 | -0.026096 | -0.068315 | -0.069733 | 0.057392 | 0.02322 | -0.042641 | 0.056344 | 0.11726 | -0.003902 | 0.065827 | 0.007024 | 0.10951 | 0.07184 | -0.035254 | -0.094033 | 0.01968 | -0.022539 | -0.023957 | 0.10317 | 0.068996 | 0.003135 | 0.10212 | -0.1972 | -0.097168 | -0.12571 | -0.025674
3693.0469 | 121.5225 | -0.17853 | 121.4539 | 0.076067 | -0.049678 | 0.020051 | -0.034174 | 0.06831 | 0.030642 | -0.08103 | -0.13523 | -0.016938 | -0.08205 | -0.069733 | 0.057392 | 0.02322 | -0.04722 | 0.056344 | 0.12184 | -0.003902 | 0.065827 | 0.011602 | 0.11409 | 0.076418 | -0.035254 | -0.089454 | 0.028838 | -0.036274 | -0.023957 | 0.10317 | 0.068996 | -0.001444 | 0.10212 | -0.19262 | -0.08801 | -0.13944 | -0.03483
3694.8281 | 121.5775 | -0.17395 | 121.4905 | 0.071489 | -0.058836 | 0.020051 | -0.034174 | 0.063733 | 0.030642 | -0.08103 | -0.14439 | -0.021517 | -0.072894 | -0.060575 | 0.057392 | 0.02322 | -0.04722 | 0.051766 | 0.11726 | -0.01306 | 0.065827 | 0.011602 | 0.10951 | 0.076418 | -0.035254 | -0.098611 | 0.024259 | -0.027118 | -0.014799 | 0.10317 | 0.068996 | -0.001444 | 0.097542 | -0.20178 | -0.097167 | -0.13029 | -0.025674
3696.5625 | 121.6278 | -0.15564 | 121.4813 | 0.076067 | -0.049678 | 0.024629 | -0.034174 | 0.06831 | 0.026064 | -0.08103 | -0.13065 | -0.021517 | -0.072894 | -0.069733 | 0.048236 | 0.02322 | -0.051798 | 0.060923 | 0.12184 | -0.003902 | 0.070405 | 0.011602 | 0.11409 | 0.07184 | -0.035254 | -0.084876 | 0.024259 | -0.027118 | -0.023957 | 0.094012 | 0.068996 | -0.006022 | 0.1067 | -0.17889 | -0.078854 | -0.12113 | -0.021096
3698.3438 | 121.6782 | -0.13733 | 121.4447 | 0.071489 | -0.063415 | 0.024629 | -0.029595 | 0.06831 | 0.026064 | -0.085608 | -0.12607 | -0.026096 | -0.068315 | -0.069733 | 0.052814 | 0.027798 | -0.051798 | 0.056344 | 0.11726 | -0.017639 | 0.070405 | 0.016181 | 0.11409 | 0.07184 | -0.039832 | -0.080297 | 0.01968 | -0.022539 | -0.023957 | 0.09859 | 0.073574 | -0.006022 | 0.10212 | -0.17889 | -0.074275 | -0.12113 | -0.016517
3700.125 | 121.6049 | -0.15564 | 121.4676 | 0.06691 | -0.063415 | 0.015472 | -0.029595 | 0.063733 | 0.026064 | -0.08103 | -0.13981 | -0.030674 | -0.063737 | -0.065154 | 0.057392 | 0.02322 | -0.038063 | 0.060923 | 0.11269 | -0.017639 | 0.061248 | 0.016181 | 0.10951 | 0.07184 | -0.035254 | -0.094033 | 0.015102 | -0.017961 | -0.019378 | 0.10317 | 0.068996 | 0.007713 | 0.1067 | -0.1972 | -0.10175 | -0.12113 | -0.025674
3701.8438 | 121.7148 | -0.11902 | 121.4401 | 0.071489 | -0.058836 | 0.020051 | -0.038752 | 0.06831 | 0.030642 | -0.085608 | -0.13981 | -0.026096 | -0.077472 | -0.065154 | 0.052814 | 0.02322 | -0.042641 | 0.051766 | 0.11726 | -0.01306 | 0.065827 | 0.007024 | 0.11409 | 0.076418 | -0.039832 | -0.094033 | 0.01968 | -0.031696 | -0.019378 | 0.09859 | 0.068996 | 0.003135 | 0.097542 | -0.19262 | -0.097168 | -0.13029 | -0.034831
3703.5469 | 121.6553 | -0.13733 | 121.4859 | 0.071489 | -0.054257 | 0.010893 | -0.029595 | 0.06831 | 0.026064 | -0.076452 | -0.13523 | -0.030674 | -0.063737 | -0.078891 | 0.052814 | 0.02322 | -0.051798 | 0.056344 | 0.11726 | -0.008481 | 0.056669 | 0.016181 | 0.11409 | 0.07184 | -0.030676 | -0.089454 | 0.015102 | -0.017961 | -0.033115 | 0.09859 | 0.068996 | -0.006022 | 0.10212 | -0.18804 | -0.083432 | -0.11655 | -0.011939
3705.3281 | 121.6507 | -0.15564 | 121.4859 | 0.076067 | -0.058836 | 0.015472 | -0.025017 | 0.063733 | 0.026064 | -0.085608 | -0.13065 | -0.021517 | -0.08205 | -0.065154 | 0.052814 | 0.018642 | -0.04722 | 0.051766 | 0.12184 | -0.01306 | 0.061248 | 0.020759 | 0.10951 | 0.07184 | -0.039832 | -0.084876 | 0.024259 | -0.036274 | -0.019378 | 0.09859 | 0.064418 | -0.001444 | 0.097542 | -0.18347 | -0.083432 | -0.13486 | -0.03483
3707.0625 | 121.6232 | -0.15106 | 121.5179 | 0.071489 | -0.054257 | 0.015472 | -0.034174 | 0.059155 | 0.030642 | -0.08103 | -0.13065 | -0.026096 | -0.077472 | -0.065154 | 0.057392 | 0.02322 | -0.051798 | 0.047188 | 0.11726 | -0.008481 | 0.061248 | 0.011602 | 0.10493 | 0.076418 | -0.035254 | -0.084876 | 0.01968 | -0.031696 | -0.019378 | 0.10317 | 0.068996 | -0.006022 | 0.092964 | -0.18804 | -0.078854 | -0.13486 | -0.025674
3708.8594 | 121.7194 | -0.13733 | 121.5042 | 0.071489 | -0.054257 | 0.024629 | -0.029595 | 0.063733 | 0.026064 | -0.08103 | -0.13065 | -0.026096 | -0.077472 | -0.069733 | 0.057392 | 0.02322 | -0.04722 | 0.060923 | 0.11726 | -0.008481 | 0.070405 | 0.016181 | 0.10951 | 0.07184 | -0.035254 | -0.084876 | 0.01968 | -0.031696 | -0.023957 | 0.10317 | 0.068996 | -0.001444 | 0.1067 | -0.18804 | -0.083432 | -0.13486 | -0.030252
3710.5781 | 121.7514 | -0.14191 | 121.5042 | 0.076067 | -0.058836 | 0.015472 | -0.025017 | 0.06831 | 0.030642 | -0.08103 | -0.14439 | -0.026096 | -0.068315 | -0.069733 | 0.052814 | 0.027798 | -0.04722 | 0.051766 | 0.12184 | -0.01306 | 0.061248 | 0.020759 | 0.11409 | 0.076418 | -0.035254 | -0.098611 | 0.01968 | -0.022539 | -0.023957 | 0.09859 | 0.073574 | -0.001444 | 0.097542 | -0.1972 | -0.097167 | -0.12113 | -0.021095
3712.3438 | 121.7651 | -0.15564 | 121.4996 | 0.076067 | -0.063415 | 0.020051 | -0.038752 | 0.063733 | 0.030642 | -0.076452 | -0.13523 | -0.030674 | -0.08205 | -0.065154 | 0.06197 | 0.018642 | -0.04722 | 0.051766 | 0.12184 | -0.017639 | 0.065827 | 0.007024 | 0.10951 | 0.076418 | -0.030676 | -0.089454 | 0.015102 | -0.036274 | -0.019378 | 0.10775 | 0.064418 | -0.001444 | 0.097542 | -0.1972 | -0.08801 | -0.14402 | -0.03483
3714.125 | 121.669 | -0.16479 | 121.5363 | 0.071489 | -0.049678 | 0.024629 | -0.034174 | 0.054577 | 0.030642 | -0.08103 | -0.13523 | -0.026096 | -0.072894 | -0.069733 | 0.057392 | 0.018642 | -0.04722 | 0.056344 | 0.11726 | -0.003902 | 0.070405 | 0.011602 | 0.10035 | 0.076418 | -0.035254 | -0.089454 | 0.01968 | -0.027118 | -0.023957 | 0.10317 | 0.064418 | -0.001444 | 0.10212 | -0.19262 | -0.08801 | -0.13029 | -0.025674
3715.9062 | 121.7056 | -0.14648 | 121.5683 | 0.076067 | -0.063415 | 0.020051 | -0.034174 | 0.072888 | 0.030642 | -0.085608 | -0.13523 | -0.026096 | -0.072894 | -0.078891 | 0.052814 | 0.014064 | -0.04722 | 0.056344 | 0.12184 | -0.017639 | 0.065827 | 0.011602 | 0.11866 | 0.076418 | -0.039832 | -0.089454 | 0.01968 | -0.027118 | -0.033115 | 0.09859 | 0.05984 | -0.001444 | 0.10212 | -0.18804 | -0.08801 | -0.12571 | -0.025674
3717.6719 | 121.7331 | -0.1236 | 121.5454 | 0.071489 | -0.054257 | 0.024629 | -0.034174 | 0.06831 | 0.026064 | -0.085608 | -0.12607 | -0.026096 | -0.077472 | -0.069733 | 0.057392 | 0.018642 | -0.04722 | 0.051766 | 0.11726 | -0.008481 | 0.070405 | 0.011602 | 0.11409 | 0.07184 | -0.039832 | -0.080297 | 0.01968 | -0.031696 | -0.023957 | 0.10317 | 0.064418 | -0.001444 | 0.097542 | -0.18346 | -0.078853 | -0.13486 | -0.030252
3719.3906 | 121.8338 | -0.14191 | 121.5271 | 0.076067 | -0.058836 | 0.015472 | -0.029595 | 0.063733 | 0.026064 | -0.08103 | -0.13065 | -0.021517 | -0.077472 | -0.074312 | 0.057392 | 0.018642 | -0.042641 | 0.060923 | 0.12184 | -0.01306 | 0.061248 | 0.016181 | 0.10951 | 0.07184 | -0.035254 | -0.084876 | 0.024259 | -0.031696 | -0.028536 | 0.10317 | 0.064418 | 0.003135 | 0.1067 | -0.18804 | -0.088011 | -0.13486 | -0.034831
3721.1719 | 121.6736 | -0.16022 | 121.5775 | 0.071489 | -0.054257 | 0.024629 | -0.034174 | 0.06831 | 0.026064 | -0.076452 | -0.13981 | -0.026096 | -0.068315 | -0.065154 | 0.057392 | 0.02322 | -0.04722 | 0.056344 | 0.11726 | -0.008481 | 0.070405 | 0.011602 | 0.11409 | 0.07184 | -0.030676 | -0.094033 | 0.01968 | -0.022539 | -0.019378 | 0.10317 | 0.068996 | -0.001444 | 0.10212 | -0.1972 | -0.092589 | -0.12571 | -0.021095
3722.9531 | 121.7331 | -0.16937 | 121.5958 | 0.076067 | -0.054257 | 0.020051 | -0.034174 | 0.063733 | 0.030642 | -0.076452 | -0.13523 | -0.026096 | -0.072894 | -0.074312 | 0.06197 | 0.027798 | -0.04722 | 0.060923 | 0.12184 | -0.008481 | 0.065827 | 0.011602 | 0.10951 | 0.076418 | -0.030676 | -0.089454 | 0.01968 | -0.027118 | -0.028536 | 0.10775 | 0.073574 | -0.001444 | 0.1067 | -0.1972 | -0.08801 | -0.13486 | -0.025674
3724.6719 | 121.7697 | -0.13733 | 121.5546 | 0.076067 | -0.058836 | 0.015472 | -0.034174 | 0.06831 | 0.035221 | -0.085608 | -0.12607 | -0.021517 | -0.068315 | -0.060575 | 0.057392 | 0.014064 | -0.051798 | 0.047188 | 0.12184 | -0.01306 | 0.061248 | 0.011602 | 0.11409 | 0.080997 | -0.039832 | -0.080297 | 0.024259 | -0.022539 | -0.014799 | 0.10317 | 0.05984 | -0.006022 | 0.092964 | -0.18346 | -0.074275 | -0.12571 | -0.016517
3726.4375 | 121.6965 | -0.16937 | 121.6049 | 0.071489 | -0.054257 | 0.015472 | -0.025017 | 0.06831 | 0.026064 | -0.085608 | -0.13981 | -0.021517 | -0.063737 | -0.065154 | 0.052814 | 0.02322 | -0.04722 | 0.051766 | 0.11726 | -0.008481 | 0.061248 | 0.020759 | 0.11409 | 0.07184 | -0.039832 | -0.094033 | 0.024259 | -0.017961 | -0.019378 | 0.09859 | 0.068996 | -0.001444 | 0.097542 | -0.19262 | -0.092589 | -0.11655 | -0.016517
3728.2188 | 121.6965 | -0.17853 | 121.5866 | 0.076067 | -0.058836 | 0.024629 | -0.029595 | 0.06831 | 0.030642 | -0.090186 | -0.13523 | -0.016938 | -0.072894 | -0.069733 | 0.052814 | 0.018642 | -0.04722 | 0.051766 | 0.12184 | -0.01306 | 0.070405 | 0.016181 | 0.11409 | 0.076418 | -0.04441 | -0.089454 | 0.028838 | -0.027118 | -0.023957 | 0.09859 | 0.064418 | -0.001444 | 0.097542 | -0.18804 | -0.08801 | -0.12571 | -0.025674
3730 | 121.6873 | -0.19226 | 121.6003 | 0.080646 | -0.058836 | 0.024629 | -0.038752 | 0.063733 | 0.030642 | -0.085608 | -0.13523 | -0.026096 | -0.068315 | -0.065154 | 0.052814 | 0.02322 | -0.038063 | 0.051766 | 0.12642 | -0.01306 | 0.070405 | 0.007024 | 0.10951 | 0.076418 | -0.039832 | -0.089454 | 0.01968 | -0.022539 | -0.019378 | 0.09859 | 0.068996 | 0.007713 | 0.097542 | -0.18804 | -0.097167 | -0.12113 | -0.030252
3731.7344 | 121.7148 | -0.18768 | 121.6095 | 0.076067 | -0.054257 | 0.015472 | -0.034174 | 0.063733 | 0.030642 | -0.08103 | -0.13981 | -0.026096 | -0.077472 | -0.069733 | 0.052814 | 0.018642 | -0.051798 | 0.047188 | 0.12184 | -0.008481 | 0.061248 | 0.011602 | 0.10951 | 0.076418 | -0.035254 | -0.094033 | 0.01968 | -0.031696 | -0.023957 | 0.09859 | 0.064418 | -0.006022 | 0.092964 | -0.19262 | -0.088011 | -0.13029 | -0.025674
3733.5 | 121.7789 | -0.16022 | 121.6049 | 0.071489 | -0.058836 | 0.015472 | -0.029595 | 0.063733 | 0.026064 | -0.08103 | -0.13065 | -0.026096 | -0.068315 | -0.065154 | 0.057392 | 0.018642 | -0.042641 | 0.051766 | 0.11726 | -0.01306 | 0.061248 | 0.016181 | 0.10951 | 0.07184 | -0.035254 | -0.084876 | 0.01968 | -0.022539 | -0.019378 | 0.10317 | 0.064418 | 0.003135 | 0.097542 | -0.18804 | -0.088011 | -0.12571 | -0.025674
3735.2812 | 121.756 | -0.1831 | 121.6141 | 0.071489 | -0.058836 | 0.020051 | -0.029595 | 0.06831 | 0.026064 | -0.08103 | -0.13523 | -0.016938 | -0.072894 | -0.065154 | 0.06197 | 0.018642 | -0.04722 | 0.056344 | 0.11726 | -0.01306 | 0.065827 | 0.016181 | 0.11409 | 0.07184 | -0.035254 | -0.089454 | 0.028838 | -0.027118 | -0.019378 | 0.10775 | 0.064418 | -0.001444 | 0.10212 | -0.1972 | -0.08801 | -0.13486 | -0.025674
3737.0156 | 121.7651 | -0.17853 | 121.6187 | 0.080646 | -0.054257 | 0.015472 | -0.034174 | 0.06831 | 0.030642 | -0.08103 | -0.13523 | -0.021517 | -0.072894 | -0.069733 | 0.057392 | 0.018642 | -0.056376 | 0.056344 | 0.12642 | -0.008481 | 0.061248 | 0.011602 | 0.11409 | 0.076418 | -0.035254 | -0.089454 | 0.024259 | -0.027118 | -0.023957 | 0.10317 | 0.064418 | -0.0106 | 0.10212 | -0.19262 | -0.078854 | -0.13029 | -0.016518
3738.7969 | 121.7926 | -0.16022 | 121.6232 | 0.071489 | -0.063415 | 0.015472 | -0.034174 | 0.06831 | 0.035221 | -0.08103 | -0.13523 | -0.026096 | -0.072894 | -0.065154 | 0.052814 | 0.02322 | -0.051798 | 0.051766 | 0.11726 | -0.017639 | 0.061248 | 0.011602 | 0.11409 | 0.080997 | -0.035254 | -0.089454 | 0.01968 | -0.027118 | -0.019378 | 0.09859 | 0.068996 | -0.006022 | 0.097542 | -0.18804 | -0.083432 | -0.12571 | -0.021096
3740.5 | 121.8796 | -0.13733 | 121.5912 | 0.062332 | -0.054257 | 0.020051 | -0.038752 | 0.059155 | 0.021485 | -0.076452 | -0.13523 | -0.021517 | -0.072894 | -0.065154 | 0.052814 | 0.018642 | -0.04722 | 0.047188 | 0.10811 | -0.008481 | 0.065827 | 0.007024 | 0.10493 | 0.067261 | -0.030676 | -0.089454 | 0.024259 | -0.027118 | -0.019378 | 0.09859 | 0.064418 | -0.001444 | 0.092964 | -0.18804 | -0.08801 | -0.12571 | -0.025674
3742.2812 | 121.7651 | -0.1831 | 121.6599 | 0.071489 | -0.058836 | 0.020051 | -0.029595 | 0.063733 | 0.026064 | -0.071874 | -0.13065 | -0.026096 | -0.072894 | -0.069733 | 0.048236 | 0.018642 | -0.051798 | 0.051766 | 0.11726 | -0.01306 | 0.065827 | 0.016181 | 0.10951 | 0.07184 | -0.026098 | -0.084876 | 0.01968 | -0.027118 | -0.023957 | 0.094012 | 0.064418 | -0.006022 | 0.097542 | -0.17889 | -0.078854 | -0.12113 | -0.021096
3744.0469 | 121.7697 | -0.1831 | 121.6599 | 0.080646 | -0.058836 | 0.015472 | -0.034174 | 0.06831 | 0.030642 | -0.085608 | -0.13981 | -0.016938 | -0.068315 | -0.074312 | 0.052814 | 0.02322 | -0.04722 | 0.051766 | 0.12642 | -0.01306 | 0.061248 | 0.011602 | 0.11409 | 0.076418 | -0.039832 | -0.094033 | 0.028838 | -0.022539 | -0.028536 | 0.09859 | 0.068996 | -0.001444 | 0.097542 | -0.19262 | -0.092589 | -0.12113 | -0.021095
3745.7812 | 121.7926 | -0.19226 | 121.6232 | 0.06691 | -0.058836 | 0.006315 | -0.034174 | 0.059155 | 0.026064 | -0.08103 | -0.13523 | -0.026096 | -0.072894 | -0.065154 | 0.057392 | 0.02322 | -0.04722 | 0.056344 | 0.11269 | -0.01306 | 0.052091 | 0.011602 | 0.10493 | 0.07184 | -0.035254 | -0.089454 | 0.01968 | -0.027118 | -0.019378 | 0.10317 | 0.068996 | -0.001444 | 0.10212 | -0.19262 | -0.08801 | -0.13029 | -0.025674
3747.5625 | 121.7834 | -0.20142 | 121.6644 | 0.071489 | -0.054257 | 0.020051 | -0.034174 | 0.06831 | 0.026064 | -0.08103 | -0.13523 | -0.021517 | -0.072894 | -0.065154 | 0.043657 | 0.02322 | -0.04722 | 0.056344 | 0.11726 | -0.008481 | 0.065827 | 0.011602 | 0.11409 | 0.07184 | -0.035254 | -0.089454 | 0.024259 | -0.027118 | -0.019378 | 0.089433 | 0.068996 | -0.001444 | 0.10212 | -0.17889 | -0.08801 | -0.11655 | -0.025674
3749.3438 | 121.8338 | -0.16022 | 121.6644 | 0.076067 | -0.058836 | 0.020051 | -0.025017 | 0.06831 | 0.030642 | -0.08103 | -0.13523 | -0.021517 | -0.072894 | -0.065154 | 0.06197 | 0.018642 | -0.051798 | 0.056344 | 0.12184 | -0.01306 | 0.065827 | 0.020759 | 0.11409 | 0.076418 | -0.035254 | -0.089454 | 0.024259 | -0.027118 | -0.019378 | 0.10775 | 0.064418 | -0.006022 | 0.10212 | -0.1972 | -0.083432 | -0.13486 | -0.021096
3751.0781 | 121.8338 | -0.16937 | 121.6599 | 0.06691 | -0.054257 | 0.015472 | -0.034174 | 0.06831 | 0.021485 | -0.08103 | -0.13065 | -0.021517 | -0.068315 | -0.069733 | 0.052814 | 0.018642 | -0.04722 | 0.060923 | 0.11269 | -0.008481 | 0.061248 | 0.011602 | 0.11409 | 0.067261 | -0.035254 | -0.084876 | 0.024259 | -0.022539 | -0.023957 | 0.09859 | 0.064418 | -0.001444 | 0.1067 | -0.18347 | -0.083432 | -0.12113 | -0.021095
3752.8594 | 121.7926 | -0.20142 | 121.6827 | 0.071489 | -0.054257 | 0.020051 | -0.029595 | 0.063733 | 0.026064 | -0.076452 | -0.13981 | -0.021517 | -0.063737 | -0.060575 | 0.057392 | 0.02322 | -0.038063 | 0.056344 | 0.11726 | -0.008481 | 0.065827 | 0.016181 | 0.10951 | 0.07184 | -0.030676 | -0.094033 | 0.024259 | -0.017961 | -0.014799 | 0.10317 | 0.068996 | 0.007713 | 0.10212 | -0.1972 | -0.10175 | -0.12113 | -0.025674
3754.5781 | 121.8979 | -0.15106 | 121.6415 | 0.076067 | -0.058836 | 0.015472 | -0.038752 | 0.06831 | 0.021485 | -0.08103 | -0.13065 | -0.021517 | -0.072894 | -0.065154 | 0.057392 | 0.027798 | -0.042641 | 0.051766 | 0.12184 | -0.01306 | 0.061248 | 0.007024 | 0.11409 | 0.067261 | -0.035254 | -0.084876 | 0.024259 | -0.027118 | -0.019378 | 0.10317 | 0.073574 | 0.003135 | 0.097542 | -0.18804 | -0.088011 | -0.13029 | -0.030253
3756.3438 | 121.9162 | -0.14191 | 121.6599 | 0.071489 | -0.058836 | 0.015472 | -0.029595 | 0.072888 | 0.026064 | -0.085608 | -0.13065 | -0.026096 | -0.08205 | -0.069733 | 0.052814 | 0.02322 | -0.04722 | 0.047188 | 0.11726 | -0.01306 | 0.061248 | 0.016181 | 0.11866 | 0.07184 | -0.039832 | -0.084876 | 0.01968 | -0.036274 | -0.023957 | 0.09859 | 0.068996 | -0.001444 | 0.092964 | -0.18347 | -0.083432 | -0.13486 | -0.03483
3758.125 | 121.9574 | -0.15106 | 121.6461 | 0.071489 | -0.054257 | 0.015472 | -0.025017 | 0.063733 | 0.030642 | -0.076452 | -0.13981 | -0.026096 | -0.068315 | -0.065154 | 0.057392 | 0.018642 | -0.042641 | 0.056344 | 0.11726 | -0.008481 | 0.061248 | 0.020759 | 0.10951 | 0.076418 | -0.030676 | -0.094033 | 0.01968 | -0.022539 | -0.019378 | 0.10317 | 0.064418 | 0.003135 | 0.10212 | -0.1972 | -0.097168 | -0.12571 | -0.025674
3759.8438 | 121.8109 | -0.17395 | 121.6782 | 0.076067 | -0.054257 | 0.020051 | -0.029595 | 0.06831 | 0.026064 | -0.071874 | -0.13523 | -0.021517 | -0.072894 | -0.060575 | 0.06197 | 0.014064 | -0.051798 | 0.056344 | 0.12184 | -0.008481 | 0.065827 | 0.016181 | 0.11409 | 0.07184 | -0.026098 | -0.089454 | 0.024259 | -0.027118 | -0.014799 | 0.10775 | 0.05984 | -0.006022 | 0.10212 | -0.1972 | -0.083432 | -0.13486 | -0.021096
3761.625 | 121.9254 | -0.15106 | 121.6782 | 0.076067 | -0.063415 | 0.024629 | -0.034174 | 0.063733 | 0.030642 | -0.076452 | -0.13523 | -0.016938 | -0.068315 | -0.065154 | 0.06197 | 0.02322 | -0.04722 | 0.047188 | 0.12184 | -0.017639 | 0.070405 | 0.011602 | 0.10951 | 0.076418 | -0.030676 | -0.089454 | 0.028838 | -0.022539 | -0.019378 | 0.10775 | 0.068996 | -0.001444 | 0.092964 | -0.1972 | -0.08801 | -0.13028 | -0.021095
3763.4062 | 121.9528 | -0.12817 | 121.6553 | 0.071489 | -0.054257 | 0.020051 | -0.038752 | 0.06831 | 0.030642 | -0.085608 | -0.13523 | -0.021517 | -0.072894 | -0.069733 | 0.052814 | 0.02322 | -0.04722 | 0.047188 | 0.11726 | -0.008481 | 0.065827 | 0.007024 | 0.11409 | 0.076418 | -0.039832 | -0.089454 | 0.024259 | -0.027118 | -0.023957 | 0.09859 | 0.068996 | -0.001444 | 0.092964 | -0.18804 | -0.08801 | -0.12571 | -0.025674
3765.125 | 121.9711 | -0.14191 | 121.6873 | 0.071489 | -0.054257 | 0.015472 | -0.034174 | 0.072888 | 0.026064 | -0.08103 | -0.13523 | -0.016938 | -0.072894 | -0.065154 | 0.052814 | 0.02322 | -0.04722 | 0.056344 | 0.11726 | -0.008481 | 0.061248 | 0.011602 | 0.11866 | 0.07184 | -0.035254 | -0.089454 | 0.028838 | -0.027118 | -0.019378 | 0.09859 | 0.068996 | -0.001444 | 0.10212 | -0.18804 | -0.08801 | -0.12571 | -0.025674
3766.9062 | 121.8567 | -0.19226 | 121.6965 | 0.076067 | -0.063415 | 0.020051 | -0.029595 | 0.06831 | 0.035221 | -0.076452 | -0.13981 | -0.016938 | -0.072894 | -0.065154 | 0.043657 | 0.027798 | -0.051798 | 0.051766 | 0.12184 | -0.017639 | 0.065827 | 0.016181 | 0.11409 | 0.080997 | -0.030676 | -0.094033 | 0.028838 | -0.027118 | -0.019378 | 0.089433 | 0.073574 | -0.006022 | 0.097542 | -0.18347 | -0.088011 | -0.11655 | -0.021096
3768.6875 | 121.9803 | -0.16022 | 121.6873 | 0.080646 | -0.067994 | 0.015472 | -0.029595 | 0.06831 | 0.026064 | -0.08103 | -0.13981 | -0.026096 | -0.077472 | -0.069733 | 0.057392 | 0.027798 | -0.04722 | 0.056344 | 0.12642 | -0.022218 | 0.061248 | 0.016181 | 0.11409 | 0.07184 | -0.035254 | -0.094033 | 0.01968 | -0.031696 | -0.023957 | 0.10317 | 0.073574 | -0.001444 | 0.10212 | -0.1972 | -0.092589 | -0.13486 | -0.030252
3770.4531 | 121.9208 | -0.15564 | 121.6919 | 0.071489 | -0.054257 | 0.020051 | -0.029595 | 0.06831 | 0.030642 | -0.071874 | -0.13065 | -0.030674 | -0.063737 | -0.065154 | 0.048236 | 0.02322 | -0.051798 | 0.051766 | 0.11726 | -0.008481 | 0.065827 | 0.016181 | 0.11409 | 0.076418 | -0.026098 | -0.084876 | 0.015102 | -0.017961 | -0.019378 | 0.094012 | 0.068996 | -0.006022 | 0.097542 | -0.17889 | -0.078854 | -0.11197 | -0.011939
3772.1875 | 121.8979 | -0.17395 | 121.7194 | 0.076067 | -0.049678 | 0.020051 | -0.029595 | 0.072888 | 0.030642 | -0.076452 | -0.14439 | -0.012359 | -0.063737 | -0.065154 | 0.052814 | 0.02322 | -0.04722 | 0.056344 | 0.12184 | -0.003902 | 0.065827 | 0.016181 | 0.11866 | 0.076418 | -0.030676 | -0.098611 | 0.033417 | -0.017961 | -0.019378 | 0.09859 | 0.068996 | -0.001444 | 0.10212 | -0.1972 | -0.097167 | -0.11655 | -0.016517
3773.9844 | 121.9894 | -0.14191 | 121.7056 | 0.080646 | -0.058836 | 0.024629 | -0.025017 | 0.059155 | 0.035221 | -0.08103 | -0.13065 | -0.021517 | -0.072894 | -0.069733 | 0.048236 | 0.018642 | -0.051798 | 0.056344 | 0.12642 | -0.01306 | 0.070405 | 0.020759 | 0.10493 | 0.080997 | -0.035254 | -0.084876 | 0.024259 | -0.027118 | -0.023957 | 0.094012 | 0.064418 | -0.006022 | 0.10212 | -0.17889 | -0.078854 | -0.12113 | -0.021096
3775.7656 | 121.9986 | -0.12817 | 121.701 | 0.076067 | -0.058836 | 0.024629 | -0.01586 | 0.072888 | 0.026064 | -0.08103 | -0.13523 | -0.026096 | -0.068315 | -0.065154 | 0.06197 | 0.027798 | -0.04722 | 0.051766 | 0.12184 | -0.01306 | 0.070405 | 0.029916 | 0.11866 | 0.07184 | -0.035254 | -0.089454 | 0.01968 | -0.022539 | -0.019378 | 0.10775 | 0.073574 | -0.001444 | 0.097542 | -0.1972 | -0.08801 | -0.13028 | -0.021095
3777.4688 | 121.9711 | -0.13275 | 121.7285 | 0.076067 | -0.063415 | 0.020051 | -0.034174 | 0.063733 | 0.021485 | -0.08103 | -0.13523 | -0.016938 | -0.068315 | -0.065154 | 0.057392 | 0.02322 | -0.051798 | 0.056344 | 0.12184 | -0.017639 | 0.065827 | 0.011602 | 0.10951 | 0.067261 | -0.035254 | -0.089454 | 0.028838 | -0.022539 | -0.019378 | 0.10317 | 0.068996 | -0.006022 | 0.10212 | -0.19262 | -0.083432 | -0.12571 | -0.016517
3779.2656 | 121.9528 | -0.15106 | 121.7331 | 0.071489 | -0.058836 | 0.015472 | -0.029595 | 0.063733 | 0.021485 | -0.076452 | -0.13065 | -0.016938 | -0.063737 | -0.074312 | 0.057392 | 0.018642 | -0.042641 | 0.056344 | 0.11726 | -0.01306 | 0.061248 | 0.016181 | 0.10951 | 0.067261 | -0.030676 | -0.084876 | 0.028838 | -0.017961 | -0.028536 | 0.10317 | 0.064418 | 0.003135 | 0.10212 | -0.18804 | -0.088011 | -0.12113 | -0.021096
3781.0469 | 121.8475 | -0.19226 | 121.7514 | 0.06691 | -0.058836 | 0.024629 | -0.034174 | 0.077466 | 0.030642 | -0.076452 | -0.13065 | -0.016938 | -0.072894 | -0.069733 | 0.057392 | 0.02322 | -0.04722 | 0.047188 | 0.11269 | -0.01306 | 0.070405 | 0.011602 | 0.12324 | 0.076418 | -0.030676 | -0.084876 | 0.028838 | -0.027118 | -0.023957 | 0.10317 | 0.068996 | -0.001444 | 0.092964 | -0.18804 | -0.083432 | -0.13029 | -0.025674
3782.8281 | 121.962 | -0.14191 | 121.7194 | 0.071489 | -0.058836 | 0.020051 | -0.029595 | 0.06831 | 0.030642 | -0.08103 | -0.13065 | -0.026096 | -0.068315 | -0.074312 | 0.052814 | 0.027798 | -0.04722 | 0.051766 | 0.11726 | -0.01306 | 0.065827 | 0.016181 | 0.11409 | 0.076418 | -0.035254 | -0.084876 | 0.01968 | -0.022539 | -0.028536 | 0.09859 | 0.073574 | -0.001444 | 0.097542 | -0.18347 | -0.083432 | -0.12113 | -0.021095
3784.6094 | 121.8842 | -0.18768 | 121.7789 | 0.071489 | -0.058836 | 0.015472 | -0.029595 | 0.06831 | 0.026064 | -0.076452 | -0.12607 | -0.016938 | -0.072894 | -0.069733 | 0.057392 | 0.02322 | -0.04722 | 0.047188 | 0.11726 | -0.01306 | 0.061248 | 0.016181 | 0.11409 | 0.07184 | -0.030676 | -0.080297 | 0.028838 | -0.027118 | -0.023957 | 0.10317 | 0.068996 | -0.001444 | 0.092964 | -0.18346 | -0.078853 | -0.13029 | -0.025674
3786.3906 | 121.994 | -0.13275 | 121.7285 | 0.071489 | -0.058836 | 0.020051 | -0.029595 | 0.06831 | 0.026064 | -0.076452 | -0.13523 | -0.026096 | -0.068315 | -0.074312 | 0.06197 | 0.018642 | -0.04722 | 0.051766 | 0.11726 | -0.01306 | 0.065827 | 0.016181 | 0.11409 | 0.07184 | -0.030676 | -0.089454 | 0.01968 | -0.022539 | -0.028536 | 0.10775 | 0.064418 | -0.001444 | 0.097542 | -0.1972 | -0.08801 | -0.13028 | -0.021095
3788.1875 | 122.0123 | -0.13275 | 121.7285 | 0.076067 | -0.058836 | 0.010893 | -0.034174 | 0.06831 | 0.021485 | -0.08103 | -0.13523 | -0.016938 | -0.068315 | -0.060575 | 0.052814 | 0.018642 | -0.051798 | 0.047188 | 0.12184 | -0.01306 | 0.056669 | 0.011602 | 0.11409 | 0.067261 | -0.035254 | -0.089454 | 0.028838 | -0.022539 | -0.014799 | 0.09859 | 0.064418 | -0.006022 | 0.092964 | -0.18804 | -0.083432 | -0.12113 | -0.016517
3789.9062 | 121.875 | -0.17853 | 121.7651 | 0.080646 | -0.058836 | 0.020051 | -0.034174 | 0.072888 | 0.030642 | -0.071874 | -0.13065 | -0.021517 | -0.068315 | -0.069733 | 0.071126 | 0.02322 | -0.051798 | 0.047188 | 0.12642 | -0.01306 | 0.065827 | 0.011602 | 0.11866 | 0.076418 | -0.026098 | -0.084876 | 0.024259 | -0.022539 | -0.023957 | 0.1169 | 0.068996 | -0.006022 | 0.092964 | -0.20178 | -0.078854 | -0.13944 | -0.016517
3791.6875 | 122.0261 | -0.11444 | 121.7468 | 0.071489 | -0.054257 | 0.015472 | -0.025017 | 0.06831 | 0.030642 | -0.08103 | -0.13523 | -0.021517 | -0.068315 | -0.065154 | 0.06197 | 0.018642 | -0.04722 | 0.047188 | 0.11726 | -0.008481 | 0.061248 | 0.020759 | 0.11409 | 0.076418 | -0.035254 | -0.089454 | 0.024259 | -0.022539 | -0.019378 | 0.10775 | 0.064418 | -0.001444 | 0.092964 | -0.1972 | -0.08801 | -0.13028 | -0.021095
3793.4062 | 121.9162 | -0.17395 | 121.7834 | 0.071489 | -0.058836 | 0.015472 | -0.034174 | 0.063733 | 0.026064 | -0.08103 | -0.13065 | -0.021517 | -0.063737 | -0.065154 | 0.057392 | 0.02322 | -0.038063 | 0.056344 | 0.11726 | -0.01306 | 0.061248 | 0.011602 | 0.10951 | 0.07184 | -0.035254 | -0.084876 | 0.024259 | -0.017961 | -0.019378 | 0.10317 | 0.068996 | 0.007713 | 0.10212 | -0.18804 | -0.092589 | -0.12113 | -0.025674
3795.2031 | 121.9162 | -0.1831 | 121.7926 | 0.080646 | -0.054257 | 0.020051 | -0.029595 | 0.063733 | 0.026064 | -0.08103 | -0.13523 | -0.021517 | -0.068315 | -0.060575 | 0.052814 | 0.018642 | -0.04722 | 0.047188 | 0.12642 | -0.008481 | 0.065827 | 0.016181 | 0.10951 | 0.07184 | -0.035254 | -0.089454 | 0.024259 | -0.022539 | -0.014799 | 0.09859 | 0.064418 | -0.001444 | 0.092964 | -0.18804 | -0.08801 | -0.12113 | -0.021095
3796.9844 | 121.9894 | -0.14648 | 121.7834 | 0.062332 | -0.058836 | 0.010893 | -0.029595 | 0.063733 | 0.026064 | -0.076452 | -0.13065 | -0.021517 | -0.068315 | -0.069733 | 0.052814 | 0.018642 | -0.04722 | 0.056344 | 0.10811 | -0.01306 | 0.056669 | 0.016181 | 0.10951 | 0.07184 | -0.030676 | -0.084876 | 0.024259 | -0.022539 | -0.023957 | 0.09859 | 0.064418 | -0.001444 | 0.10212 | -0.18347 | -0.083432 | -0.12113 | -0.021095
3798.7031 | 121.9208 | -0.18768 | 121.8338 | 0.076067 | -0.058836 | 0.015472 | -0.029595 | 0.063733 | 0.030642 | -0.062717 | -0.1215 | -0.026096 | -0.072894 | -0.069733 | 0.057392 | 0.02322 | -0.038063 | 0.056344 | 0.12184 | -0.01306 | 0.061248 | 0.016181 | 0.10951 | 0.076418 | -0.016941 | -0.075719 | 0.01968 | -0.027118 | -0.023957 | 0.10317 | 0.068996 | 0.007713 | 0.10212 | -0.17889 | -0.083432 | -0.13029 | -0.034831
3800.4688 | 121.9254 | -0.17853 | 121.8201 | 0.076067 | -0.054257 | 0.015472 | -0.029595 | 0.06831 | 0.021485 | -0.085608 | -0.13523 | -0.021517 | -0.072894 | -0.065154 | 0.048236 | 0.018642 | -0.04722 | 0.051766 | 0.12184 | -0.008481 | 0.061248 | 0.016181 | 0.11409 | 0.067261 | -0.039832 | -0.089454 | 0.024259 | -0.027118 | -0.019378 | 0.094012 | 0.064418 | -0.001444 | 0.097542 | -0.18347 | -0.08801 | -0.12113 | -0.025674
3802.25 | 121.9345 | -0.20599 | 121.8018 | 0.06691 | -0.063415 | 0.010893 | -0.029595 | 0.06831 | 0.035221 | -0.076452 | -0.12607 | -0.026096 | -0.068315 | -0.069733 | 0.06197 | 0.018642 | -0.056376 | 0.04261 | 0.11269 | -0.017639 | 0.056669 | 0.016181 | 0.11409 | 0.080997 | -0.030676 | -0.080297 | 0.01968 | -0.022539 | -0.023957 | 0.10775 | 0.064418 | -0.0106 | 0.088386 | -0.18804 | -0.069697 | -0.13028 | -0.011939
3803.9844 | 121.9482 | -0.14648 | 121.8201 | 0.071489 | -0.058836 | 0.024629 | -0.025017 | 0.06831 | 0.030642 | -0.085608 | -0.12607 | -0.021517 | -0.072894 | -0.065154 | 0.052814 | 0.018642 | -0.051798 | 0.051766 | 0.11726 | -0.01306 | 0.070405 | 0.020759 | 0.11409 | 0.076418 | -0.039832 | -0.080297 | 0.024259 | -0.027118 | -0.019378 | 0.09859 | 0.064418 | -0.006022 | 0.097542 | -0.17889 | -0.074275 | -0.12571 | -0.021096
3805.7812 | 121.9345 | -0.20599 | 121.8063 | 0.071489 | -0.054257 | 0.024629 | -0.025017 | 0.063733 | 0.030642 | -0.08103 | -0.12607 | -0.021517 | -0.068315 | -0.069733 | 0.048236 | 0.02322 | -0.04722 | 0.051766 | 0.11726 | -0.008481 | 0.070405 | 0.020759 | 0.10951 | 0.076418 | -0.035254 | -0.080297 | 0.024259 | -0.022539 | -0.023957 | 0.094012 | 0.068996 | -0.001444 | 0.097542 | -0.17431 | -0.078853 | -0.11655 | -0.021095
3807.5 | 121.9437 | -0.1831 | 121.8155 | 0.076067 | -0.058836 | 0.020051 | -0.029595 | 0.06831 | 0.030642 | -0.076452 | -0.13065 | -0.021517 | -0.068315 | -0.069733 | 0.052814 | 0.014064 | -0.04722 | 0.051766 | 0.12184 | -0.01306 | 0.065827 | 0.016181 | 0.11409 | 0.076418 | -0.030676 | -0.084876 | 0.024259 | -0.022539 | -0.023957 | 0.09859 | 0.05984 | -0.001444 | 0.097542 | -0.18347 | -0.083432 | -0.12113 | -0.021095
3809.2812 | 122.0673 | -0.12817 | 121.7972 | 0.071489 | -0.049678 | 0.020051 | -0.029595 | 0.06831 | 0.026064 | -0.08103 | -0.13523 | -0.030674 | -0.072894 | -0.065154 | 0.06197 | 0.014064 | -0.051798 | 0.051766 | 0.11726 | -0.003902 | 0.065827 | 0.016181 | 0.11409 | 0.07184 | -0.035254 | -0.089454 | 0.015102 | -0.027118 | -0.019378 | 0.10775 | 0.05984 | -0.006022 | 0.097542 | -0.1972 | -0.083432 | -0.13486 | -0.021096
3811.0625 | 121.9849 | -0.16022 | 121.7926 | 0.071489 | -0.058836 | 0.024629 | -0.034174 | 0.063733 | 0.026064 | -0.071874 | -0.13065 | -0.021517 | -0.063737 | -0.060575 | 0.057392 | 0.02322 | -0.042641 | 0.047188 | 0.11726 | -0.01306 | 0.070405 | 0.011602 | 0.10951 | 0.07184 | -0.026098 | -0.084876 | 0.024259 | -0.017961 | -0.014799 | 0.10317 | 0.068996 | 0.003135 | 0.092964 | -0.18804 | -0.088011 | -0.12113 | -0.021096
3812.8594 | 121.9437 | -0.19226 | 121.8384 | 0.080646 | -0.054257 | 0.024629 | -0.029595 | 0.06831 | 0.030642 | -0.08103 | -0.13523 | -0.021517 | -0.063737 | -0.069733 | 0.057392 | 0.02322 | -0.04722 | 0.051766 | 0.12642 | -0.008481 | 0.070405 | 0.016181 | 0.11409 | 0.076418 | -0.035254 | -0.089454 | 0.024259 | -0.017961 | -0.023957 | 0.10317 | 0.068996 | -0.001444 | 0.097542 | -0.19262 | -0.08801 | -0.12113 | -0.016517
3814.5625 | 121.9803 | -0.16937 | 121.8063 | 0.080646 | -0.054257 | 0.015472 | -0.034174 | 0.072888 | 0.026064 | -0.076452 | -0.13523 | -0.021517 | -0.072894 | -0.065154 | 0.048236 | 0.027798 | -0.04722 | 0.056344 | 0.12642 | -0.008481 | 0.061248 | 0.011602 | 0.11866 | 0.07184 | -0.030676 | -0.089454 | 0.024259 | -0.027118 | -0.019378 | 0.094012 | 0.073574 | -0.001444 | 0.10212 | -0.18347 | -0.08801 | -0.12113 | -0.025674
3816.3438 | 122.0535 | -0.14191 | 121.8109 | 0.071489 | -0.054257 | 0.015472 | -0.025017 | 0.063733 | 0.030642 | -0.076452 | -0.12607 | -0.026096 | -0.077472 | -0.065154 | 0.057392 | 0.018642 | -0.051798 | 0.056344 | 0.11726 | -0.008481 | 0.061248 | 0.020759 | 0.10951 | 0.076418 | -0.030676 | -0.080297 | 0.01968 | -0.031696 | -0.019378 | 0.10317 | 0.064418 | -0.006022 | 0.10212 | -0.18346 | -0.074275 | -0.13486 | -0.025674
3818.0469 | 121.9666 | -0.17853 | 121.8338 | 0.06691 | -0.054257 | 0.020051 | -0.025017 | 0.06831 | 0.035221 | -0.08103 | -0.13981 | -0.016938 | -0.068315 | -0.069733 | 0.052814 | 0.018642 | -0.051798 | 0.056344 | 0.11269 | -0.008481 | 0.065827 | 0.020759 | 0.11409 | 0.080997 | -0.035254 | -0.094033 | 0.028838 | -0.022539 | -0.023957 | 0.09859 | 0.064418 | -0.006022 | 0.10212 | -0.19262 | -0.088011 | -0.12113 | -0.016517
3819.8438 | 121.994 | -0.17395 | 121.8384 | 0.071489 | -0.058836 | 0.015472 | -0.029595 | 0.077466 | 0.030642 | -0.08103 | -0.12607 | -0.016938 | -0.068315 | -0.065154 | 0.057392 | 0.018642 | -0.042641 | 0.056344 | 0.11726 | -0.01306 | 0.061248 | 0.016181 | 0.12324 | 0.076418 | -0.035254 | -0.080297 | 0.028838 | -0.022539 | -0.019378 | 0.10317 | 0.064418 | 0.003135 | 0.10212 | -0.18346 | -0.083432 | -0.12571 | -0.025674
3821.625 | 121.994 | -0.16937 | 121.8567 | 0.076067 | -0.049678 | 0.015472 | -0.029595 | 0.06831 | 0.016907 | -0.076452 | -0.13523 | -0.021517 | -0.077472 | -0.065154 | 0.052814 | 0.018642 | -0.04722 | 0.056344 | 0.12184 | -0.003902 | 0.061248 | 0.016181 | 0.11409 | 0.062683 | -0.030676 | -0.089454 | 0.024259 | -0.031696 | -0.019378 | 0.09859 | 0.064418 | -0.001444 | 0.10212 | -0.18804 | -0.08801 | -0.13029 | -0.030252
3823.3906 | 122.0581 | -0.15106 | 121.8155 | 0.076067 | -0.054257 | 0.015472 | -0.025017 | 0.06831 | 0.030642 | -0.076452 | -0.13523 | -0.026096 | -0.063737 | -0.060575 | 0.057392 | 0.018642 | -0.04722 | 0.056344 | 0.12184 | -0.008481 | 0.061248 | 0.020759 | 0.11409 | 0.076418 | -0.030676 | -0.089454 | 0.01968 | -0.017961 | -0.014799 | 0.10317 | 0.064418 | -0.001444 | 0.10212 | -0.19262 | -0.08801 | -0.12113 | -0.016517
3825.1875 | 122.0215 | -0.16937 | 121.8521 | 0.071489 | -0.049678 | 0.020051 | -0.043331 | 0.06831 | 0.026064 | -0.08103 | -0.12607 | -0.026096 | -0.068315 | -0.060575 | 0.057392 | 0.014064 | -0.042641 | 0.047188 | 0.11726 | -0.003902 | 0.065827 | 0.002445 | 0.11409 | 0.07184 | -0.035254 | -0.080297 | 0.01968 | -0.022539 | -0.014799 | 0.10317 | 0.05984 | 0.003135 | 0.092964 | -0.18346 | -0.083432 | -0.12571 | -0.025674
3826.9062 | 122.113 | -0.13275 | 121.8246 | 0.076067 | -0.058836 | 0.020051 | -0.034174 | 0.072888 | 0.030642 | -0.085608 | -0.13065 | -0.030674 | -0.068315 | -0.069733 | 0.052814 | 0.018642 | -0.04722 | 0.056344 | 0.12184 | -0.01306 | 0.065827 | 0.011602 | 0.11866 | 0.076418 | -0.039832 | -0.084876 | 0.015102 | -0.022539 | -0.023957 | 0.09859 | 0.064418 | -0.001444 | 0.10212 | -0.18347 | -0.083432 | -0.12113 | -0.021095
3828.7031 | 122.1176 | -0.14648 | 121.8201 | 0.071489 | -0.054257 | 0.015472 | -0.029595 | 0.063733 | 0.035221 | -0.08103 | -0.13523 | -0.026096 | -0.068315 | -0.074312 | 0.057392 | 0.027798 | -0.051798 | 0.047188 | 0.11726 | -0.008481 | 0.061248 | 0.016181 | 0.10951 | 0.080997 | -0.035254 | -0.089454 | 0.01968 | -0.022539 | -0.028536 | 0.10317 | 0.073574 | -0.006022 | 0.092964 | -0.19262 | -0.083432 | -0.12571 | -0.016517
3830.4062 | 122.1313 | -0.15106 | 121.8109 | 0.071489 | -0.058836 | 0.010893 | -0.029595 | 0.06831 | 0.026064 | -0.08103 | -0.13065 | -0.021517 | -0.072894 | -0.065154 | 0.052814 | 0.014064 | -0.042641 | 0.051766 | 0.11726 | -0.01306 | 0.056669 | 0.016181 | 0.11409 | 0.07184 | -0.035254 | -0.084876 | 0.024259 | -0.027118 | -0.019378 | 0.09859 | 0.05984 | 0.003135 | 0.097542 | -0.18347 | -0.088011 | -0.12571 | -0.030253
3832.1875 | 121.962 | -0.1831 | 121.875 | 0.071489 | -0.049678 | 0.020051 | -0.029595 | 0.072888 | 0.030642 | -0.076452 | -0.12607 | -0.026096 | -0.072894 | -0.065154 | 0.052814 | 0.018642 | -0.04722 | 0.047188 | 0.11726 | -0.003902 | 0.065827 | 0.016181 | 0.11866 | 0.076418 | -0.030676 | -0.080297 | 0.01968 | -0.027118 | -0.019378 | 0.09859 | 0.064418 | -0.001444 | 0.092964 | -0.17889 | -0.078853 | -0.12571 | -0.025674
3833.9688 | 122.0856 | -0.15106 | 121.843 | 0.071489 | -0.054257 | 0.015472 | -0.020438 | 0.072888 | 0.026064 | -0.08103 | -0.13065 | -0.026096 | -0.072894 | -0.065154 | 0.052814 | 0.02322 | -0.042641 | 0.047188 | 0.11726 | -0.008481 | 0.061248 | 0.025338 | 0.11866 | 0.07184 | -0.035254 | -0.084876 | 0.01968 | -0.027118 | -0.019378 | 0.09859 | 0.068996 | 0.003135 | 0.092964 | -0.18347 | -0.088011 | -0.12571 | -0.030253
3835.7656 | 122.1451 | -0.13733 | 121.8201 | 0.076067 | -0.0451 | 0.015472 | -0.034174 | 0.063733 | 0.026064 | -0.085608 | -0.14439 | -0.016938 | -0.072894 | -0.065154 | 0.057392 | 0.009486 | -0.04722 | 0.051766 | 0.12184 | 0.000676 | 0.061248 | 0.011602 | 0.10951 | 0.07184 | -0.039832 | -0.098611 | 0.028838 | -0.027118 | -0.019378 | 0.10317 | 0.055262 | -0.001444 | 0.097542 | -0.20178 | -0.097167 | -0.13029 | -0.025674
3837.5469 | 122.1039 | -0.14191 | 121.8246 | 0.071489 | -0.054257 | 0.015472 | -0.034174 | 0.072888 | 0.026064 | -0.08103 | -0.13065 | -0.021517 | -0.068315 | -0.069733 | 0.052814 | 0.027798 | -0.042641 | 0.051766 | 0.11726 | -0.008481 | 0.061248 | 0.011602 | 0.11866 | 0.07184 | -0.035254 | -0.084876 | 0.024259 | -0.022539 | -0.023957 | 0.09859 | 0.073574 | 0.003135 | 0.097542 | -0.18347 | -0.088011 | -0.12113 | -0.025674
3839.2812 | 122.0627 | -0.16022 | 121.875 | 0.076067 | -0.058836 | 0.020051 | -0.029595 | 0.06831 | 0.021485 | -0.08103 | -0.13523 | -0.016938 | -0.068315 | -0.074312 | 0.057392 | 0.02322 | -0.04722 | 0.051766 | 0.12184 | -0.01306 | 0.065827 | 0.016181 | 0.11409 | 0.067261 | -0.035254 | -0.089454 | 0.028838 | -0.022539 | -0.028536 | 0.10317 | 0.068996 | -0.001444 | 0.097542 | -0.19262 | -0.08801 | -0.12571 | -0.021095
3841.0781 | 122.0215 | -0.19226 | 121.9025 | 0.076067 | -0.054257 | 0.020051 | -0.020438 | 0.06831 | 0.026064 | -0.08103 | -0.12607 | -0.026096 | -0.072894 | -0.074312 | 0.057392 | 0.018642 | -0.051798 | 0.056344 | 0.12184 | -0.008481 | 0.065827 | 0.025338 | 0.11409 | 0.07184 | -0.035254 | -0.080297 | 0.01968 | -0.027118 | -0.028536 | 0.10317 | 0.064418 | -0.006022 | 0.10212 | -0.18346 | -0.074275 | -0.13029 | -0.021096
3842.875 | 122.1359 | -0.14191 | 121.8475 | 0.076067 | -0.054257 | 0.015472 | -0.034174 | 0.063733 | 0.030642 | -0.076452 | -0.13523 | -0.021517 | -0.068315 | -0.065154 | 0.052814 | 0.018642 | -0.04722 | 0.056344 | 0.12184 | -0.008481 | 0.061248 | 0.011602 | 0.10951 | 0.076418 | -0.030676 | -0.089454 | 0.024259 | -0.022539 | -0.019378 | 0.09859 | 0.064418 | -0.001444 | 0.10212 | -0.18804 | -0.08801 | -0.12113 | -0.021095
3844.5938 | 122.0352 | -0.18768 | 121.9162 | 0.06691 | -0.049678 | 0.020051 | -0.029595 | 0.063733 | 0.030642 | -0.08103 | -0.13065 | -0.016938 | -0.063737 | -0.065154 | 0.052814 | 0.02322 | -0.04722 | 0.056344 | 0.11269 | -0.003902 | 0.065827 | 0.016181 | 0.10951 | 0.076418 | -0.035254 | -0.084876 | 0.028838 | -0.017961 | -0.019378 | 0.09859 | 0.068996 | -0.001444 | 0.10212 | -0.18347 | -0.083432 | -0.11655 | -0.016517
3846.375 | 122.0306 | -0.19684 | 121.9162 | 0.076067 | -0.054257 | 0.024629 | -0.029595 | 0.06831 | 0.021485 | -0.076452 | -0.13523 | -0.012359 | -0.072894 | -0.074312 | 0.057392 | 0.02322 | -0.04722 | 0.056344 | 0.12184 | -0.008481 | 0.070405 | 0.016181 | 0.11409 | 0.067261 | -0.030676 | -0.089454 | 0.033417 | -0.027118 | -0.028536 | 0.10317 | 0.068996 | -0.001444 | 0.10212 | -0.19262 | -0.08801 | -0.13029 | -0.025674
3848.1719 | 122.1405 | -0.14648 | 121.8475 | 0.076067 | -0.054257 | 0.020051 | -0.038752 | 0.063733 | 0.030642 | -0.071874 | -0.13065 | -0.026096 | -0.063737 | -0.065154 | 0.052814 | 0.018642 | -0.04722 | 0.047188 | 0.12184 | -0.008481 | 0.065827 | 0.007024 | 0.10951 | 0.076418 | -0.026098 | -0.084876 | 0.01968 | -0.017961 | -0.019378 | 0.09859 | 0.064418 | -0.001444 | 0.092964 | -0.18347 | -0.083432 | -0.11655 | -0.016517
3849.9531 | 122.1634 | -0.14648 | 121.8704 | 0.085224 | -0.054257 | 0.020051 | -0.029595 | 0.063733 | 0.026064 | -0.08103 | -0.13523 | -0.021517 | -0.068315 | -0.065154 | 0.048236 | 0.02322 | -0.04722 | 0.056344 | 0.131 | -0.008481 | 0.065827 | 0.016181 | 0.10951 | 0.07184 | -0.035254 | -0.089454 | 0.024259 | -0.022539 | -0.019378 | 0.094012 | 0.068996 | -0.001444 | 0.10212 | -0.18347 | -0.08801 | -0.11655 | -0.021095
3851.6719 | 122.0673 | -0.16937 | 121.8887 | 0.076067 | -0.049678 | 0.020051 | -0.034174 | 0.063733 | 0.030642 | -0.08103 | -0.13523 | -0.016938 | -0.072894 | -0.060575 | 0.052814 | 0.027798 | -0.04722 | 0.051766 | 0.12184 | -0.003902 | 0.065827 | 0.011602 | 0.10951 | 0.076418 | -0.035254 | -0.089454 | 0.028838 | -0.027118 | -0.014799 | 0.09859 | 0.073574 | -0.001444 | 0.097542 | -0.18804 | -0.08801 | -0.12571 | -0.025674
3853.4531 | 122.1039 | -0.15106 | 121.8658 | 0.071489 | -0.058836 | 0.015472 | -0.029595 | 0.06831 | 0.026064 | -0.08103 | -0.13981 | -0.021517 | -0.063737 | -0.065154 | 0.06197 | 0.018642 | -0.051798 | 0.060923 | 0.11726 | -0.01306 | 0.061248 | 0.016181 | 0.11409 | 0.07184 | -0.035254 | -0.094033 | 0.024259 | -0.017961 | -0.019378 | 0.10775 | 0.064418 | -0.006022 | 0.1067 | -0.20178 | -0.088011 | -0.12571 | -0.011939
3855.1875 | 122.0352 | -0.19684 | 121.8933 | 0.076067 | -0.049678 | 0.015472 | -0.034174 | 0.063733 | 0.026064 | -0.08103 | -0.13981 | -0.021517 | -0.072894 | -0.065154 | 0.057392 | 0.018642 | -0.04722 | 0.056344 | 0.12184 | -0.003902 | 0.061248 | 0.011602 | 0.10951 | 0.07184 | -0.035254 | -0.094033 | 0.024259 | -0.027118 | -0.019378 | 0.10317 | 0.064418 | -0.001444 | 0.10212 | -0.1972 | -0.092589 | -0.13029 | -0.025674
3856.9844 | 122.0398 | -0.16479 | 121.8842 | 0.076067 | -0.049678 | 0.015472 | -0.029595 | 0.06831 | 0.021485 | -0.071874 | -0.14439 | -0.021517 | -0.068315 | -0.069733 | 0.057392 | 0.02322 | -0.04722 | 0.051766 | 0.12184 | -0.003902 | 0.061248 | 0.016181 | 0.11409 | 0.067261 | -0.026098 | -0.098611 | 0.024259 | -0.022539 | -0.023957 | 0.10317 | 0.068996 | -0.001444 | 0.097542 | -0.20178 | -0.097167 | -0.12571 | -0.021095
3858.7812 | 122.168 | -0.14648 | 121.8887 | 0.071489 | -0.058836 | 0.020051 | -0.034174 | 0.063733 | 0.030642 | -0.076452 | -0.13065 | -0.012359 | -0.068315 | -0.069733 | 0.057392 | 0.018642 | -0.04722 | 0.056344 | 0.11726 | -0.01306 | 0.065827 | 0.011602 | 0.10951 | 0.076418 | -0.030676 | -0.084876 | 0.033417 | -0.022539 | -0.023957 | 0.10317 | 0.064418 | -0.001444 | 0.10212 | -0.18804 | -0.083432 | -0.12571 | -0.021095
3860.5781 | 122.113 | -0.16022 | 121.8887 | 0.071489 | -0.054257 | 0.015472 | -0.025017 | 0.06831 | 0.021485 | -0.071874 | -0.13065 | -0.016938 | -0.068315 | -0.074312 | 0.057392 | 0.02322 | -0.04722 | 0.051766 | 0.11726 | -0.008481 | 0.061248 | 0.020759 | 0.11409 | 0.067261 | -0.026098 | -0.084876 | 0.028838 | -0.022539 | -0.028536 | 0.10317 | 0.068996 | -0.001444 | 0.097542 | -0.18804 | -0.083432 | -0.12571 | -0.021095
3862.375 | 122.0947 | -0.17853 | 121.907 | 0.076067 | -0.049678 | 0.020051 | -0.034174 | 0.06831 | 0.030642 | -0.08103 | -0.12607 | -0.021517 | -0.072894 | -0.069733 | 0.052814 | 0.02322 | -0.038063 | 0.051766 | 0.12184 | -0.003902 | 0.065827 | 0.011602 | 0.11409 | 0.076418 | -0.035254 | -0.080297 | 0.024259 | -0.027118 | -0.023957 | 0.09859 | 0.068996 | 0.007713 | 0.097542 | -0.17889 | -0.08801 | -0.12571 | -0.034831
3864.0938 | 122.1863 | -0.13275 | 121.9116 | 0.076067 | -0.054257 | 0.020051 | -0.029595 | 0.072888 | 0.021485 | -0.076452 | -0.13523 | -0.021517 | -0.068315 | -0.065154 | 0.057392 | 0.02322 | -0.04722 | 0.051766 | 0.12184 | -0.008481 | 0.065827 | 0.016181 | 0.11866 | 0.067261 | -0.030676 | -0.089454 | 0.024259 | -0.022539 | -0.019378 | 0.10317 | 0.068996 | -0.001444 | 0.097542 | -0.19262 | -0.08801 | -0.12571 | -0.021095
3865.8906 | 122.1039 | -0.16937 | 121.9208 | 0.071489 | -0.054257 | 0.024629 | -0.029595 | 0.06831 | 0.026064 | -0.08103 | -0.13065 | -0.016938 | -0.063737 | -0.065154 | 0.052814 | 0.027798 | -0.051798 | 0.051766 | 0.11726 | -0.008481 | 0.070405 | 0.016181 | 0.11409 | 0.07184 | -0.035254 | -0.084876 | 0.028838 | -0.017961 | -0.019378 | 0.09859 | 0.073574 | -0.006022 | 0.097542 | -0.18347 | -0.078854 | -0.11655 | -0.011939
3867.6719 | 122.1542 | -0.15106 | 121.9162 | 0.076067 | -0.0451 | 0.020051 | -0.025017 | 0.06831 | 0.026064 | -0.08103 | -0.13065 | -0.026096 | -0.063737 | -0.065154 | 0.06197 | 0.018642 | -0.042641 | 0.051766 | 0.12184 | 0.000676 | 0.065827 | 0.020759 | 0.11409 | 0.07184 | -0.035254 | -0.084876 | 0.01968 | -0.017961 | -0.019378 | 0.10775 | 0.064418 | 0.003135 | 0.097542 | -0.19262 | -0.088011 | -0.12571 | -0.021096
3869.4531 | 122.0673 | -0.20599 | 121.9666 | 0.076067 | -0.0451 | 0.024629 | -0.029595 | 0.06831 | 0.030642 | -0.067295 | -0.13981 | -0.026096 | -0.068315 | -0.065154 | 0.06197 | 0.02322 | -0.042641 | 0.051766 | 0.12184 | 0.000676 | 0.070405 | 0.016181 | 0.11409 | 0.076418 | -0.021519 | -0.094033 | 0.01968 | -0.022539 | -0.019378 | 0.10775 | 0.068996 | 0.003135 | 0.097542 | -0.20178 | -0.097168 | -0.13028 | -0.025674
3871.1719 | 122.1039 | -0.17853 | 121.9208 | 0.076067 | -0.054257 | 0.020051 | -0.025017 | 0.06831 | 0.026064 | -0.08103 | -0.13523 | -0.021517 | -0.068315 | -0.069733 | 0.057392 | 0.02322 | -0.04722 | 0.051766 | 0.12184 | -0.008481 | 0.065827 | 0.020759 | 0.11409 | 0.07184 | -0.035254 | -0.089454 | 0.024259 | -0.022539 | -0.023957 | 0.10317 | 0.068996 | -0.001444 | 0.097542 | -0.19262 | -0.08801 | -0.12571 | -0.021095
3872.9531 | 122.2046 | -0.14648 | 121.9025 | 0.071489 | -0.054257 | 0.020051 | -0.034174 | 0.059155 | 0.021485 | -0.085608 | -0.12607 | -0.012359 | -0.072894 | -0.060575 | 0.057392 | 0.02322 | -0.04722 | 0.047188 | 0.11726 | -0.008481 | 0.065827 | 0.011602 | 0.10493 | 0.067261 | -0.039832 | -0.080297 | 0.033417 | -0.027118 | -0.014799 | 0.10317 | 0.068996 | -0.001444 | 0.092964 | -0.18346 | -0.078853 | -0.13029 | -0.025674
3874.75 | 122.113 | -0.1831 | 121.9574 | 0.080646 | -0.0451 | 0.024629 | -0.034174 | 0.06831 | 0.026064 | -0.076452 | -0.13065 | -0.016938 | -0.063737 | -0.069733 | 0.057392 | 0.018642 | -0.04722 | 0.051766 | 0.12642 | 0.000676 | 0.070405 | 0.011602 | 0.11409 | 0.07184 | -0.030676 | -0.084876 | 0.028838 | -0.017961 | -0.023957 | 0.10317 | 0.064418 | -0.001444 | 0.097542 | -0.18804 | -0.083432 | -0.12113 | -0.016517
3876.4688 | 122.113 | -0.20142 | 121.9666 | 0.076067 | -0.0451 | 0.010893 | -0.034174 | 0.063733 | 0.026064 | -0.08103 | -0.12607 | -0.016938 | -0.072894 | -0.065154 | 0.057392 | 0.027798 | -0.051798 | 0.051766 | 0.12184 | 0.000676 | 0.056669 | 0.011602 | 0.10951 | 0.07184 | -0.035254 | -0.080297 | 0.028838 | -0.027118 | -0.019378 | 0.10317 | 0.073574 | -0.006022 | 0.097542 | -0.18346 | -0.074275 | -0.13029 | -0.021096
3878.2656 | 122.1268 | -0.1831 | 121.9666 | 0.076067 | -0.0451 | 0.015472 | -0.038752 | 0.072888 | 0.035221 | -0.071874 | -0.13523 | -0.016938 | -0.063737 | -0.060575 | 0.052814 | 0.018642 | -0.04722 | 0.056344 | 0.12184 | 0.000676 | 0.061248 | 0.007024 | 0.11866 | 0.080997 | -0.026098 | -0.089454 | 0.028838 | -0.017961 | -0.014799 | 0.09859 | 0.064418 | -0.001444 | 0.10212 | -0.18804 | -0.08801 | -0.11655 | -0.016517
3880 | 122.0718 | -0.17853 | 121.9666 | 0.076067 | -0.0451 | 0.020051 | -0.025017 | 0.06831 | 0.026064 | -0.076452 | -0.13065 | -0.026096 | -0.072894 | -0.060575 | 0.057392 | 0.018642 | -0.04722 | 0.047188 | 0.12184 | 0.000676 | 0.065827 | 0.020759 | 0.11409 | 0.07184 | -0.030676 | -0.084876 | 0.01968 | -0.027118 | -0.014799 | 0.10317 | 0.064418 | -0.001444 | 0.092964 | -0.18804 | -0.083432 | -0.13029 | -0.025674
3881.7812 | 122.2092 | -0.14191 | 121.9437 | 0.080646 | -0.049678 | 0.015472 | -0.025017 | 0.072888 | 0.030642 | -0.085608 | -0.13065 | -0.016938 | -0.063737 | -0.065154 | 0.052814 | 0.02322 | -0.056376 | 0.051766 | 0.12642 | -0.003902 | 0.061248 | 0.020759 | 0.11866 | 0.076418 | -0.039832 | -0.084876 | 0.028838 | -0.017961 | -0.019378 | 0.09859 | 0.068996 | -0.0106 | 0.097542 | -0.18347 | -0.074276 | -0.11655 | -0.007361
3883.5625 | 122.168 | -0.15564 | 121.9574 | 0.071489 | -0.054257 | 0.029208 | -0.029595 | 0.077466 | 0.030642 | -0.076452 | -0.1215 | -0.026096 | -0.063737 | -0.060575 | 0.06197 | 0.018642 | -0.042641 | 0.056344 | 0.11726 | -0.008481 | 0.074984 | 0.016181 | 0.12324 | 0.076418 | -0.030676 | -0.075719 | 0.01968 | -0.017961 | -0.014799 | 0.10775 | 0.064418 | 0.003135 | 0.10212 | -0.18346 | -0.078854 | -0.12571 | -0.021096
3885.375 | 122.1039 | -0.17853 | 121.962 | 0.076067 | -0.054257 | 0.020051 | -0.029595 | 0.063733 | 0.030642 | -0.08103 | -0.13523 | -0.016938 | -0.068315 | -0.065154 | 0.052814 | 0.02322 | -0.051798 | 0.051766 | 0.12184 | -0.008481 | 0.065827 | 0.016181 | 0.10951 | 0.076418 | -0.035254 | -0.089454 | 0.028838 | -0.022539 | -0.019378 | 0.09859 | 0.068996 | -0.006022 | 0.097542 | -0.18804 | -0.083432 | -0.12113 | -0.016517
3887.0938 | 122.1313 | -0.16479 | 121.9666 | 0.06691 | -0.0451 | 0.015472 | -0.034174 | 0.063733 | 0.026064 | -0.08103 | -0.12607 | -0.021517 | -0.072894 | -0.060575 | 0.052814 | 0.02322 | -0.051798 | 0.047188 | 0.11269 | 0.000676 | 0.061248 | 0.011602 | 0.10951 | 0.07184 | -0.035254 | -0.080297 | 0.024259 | -0.027118 | -0.014799 | 0.09859 | 0.068996 | -0.006022 | 0.092964 | -0.17889 | -0.074275 | -0.12571 | -0.021096
3888.875 | 122.0947 | -0.18768 | 121.9574 | 0.076067 | -0.049678 | 0.020051 | -0.038752 | 0.06831 | 0.026064 | -0.08103 | -0.13065 | -0.016938 | -0.068315 | -0.055996 | 0.06197 | 0.02322 | -0.060955 | 0.047188 | 0.12184 | -0.003902 | 0.065827 | 0.007024 | 0.11409 | 0.07184 | -0.035254 | -0.084876 | 0.028838 | -0.022539 | -0.01022 | 0.10775 | 0.068996 | -0.015179 | 0.092964 | -0.19262 | -0.069697 | -0.13028 | -0.00736
3890.6562 | 122.1542 | -0.15564 | 121.9528 | 0.076067 | -0.0451 | 0.020051 | -0.034174 | 0.063733 | 0.026064 | -0.076452 | -0.13981 | -0.021517 | -0.068315 | -0.069733 | 0.057392 | 0.02322 | -0.051798 | 0.047188 | 0.12184 | 0.000676 | 0.065827 | 0.011602 | 0.10951 | 0.07184 | -0.030676 | -0.094033 | 0.024259 | -0.022539 | -0.023957 | 0.10317 | 0.068996 | -0.006022 | 0.092964 | -0.1972 | -0.088011 | -0.12571 | -0.016517
3892.375 | 122.2321 | -0.16022 | 121.9345 | 0.071489 | -0.0451 | 0.024629 | -0.034174 | 0.063733 | 0.026064 | -0.08103 | -0.13523 | -0.021517 | -0.068315 | -0.055996 | 0.043657 | 0.018642 | -0.04722 | 0.051766 | 0.11726 | 0.000676 | 0.070405 | 0.011602 | 0.10951 | 0.07184 | -0.035254 | -0.089454 | 0.024259 | -0.022539 | -0.01022 | 0.089433 | 0.064418 | -0.001444 | 0.097542 | -0.17889 | -0.08801 | -0.11197 | -0.021095
3894.1719 | 122.1725 | -0.15106 | 121.9437 | 0.080646 | -0.049678 | 0.015472 | -0.038752 | 0.06831 | 0.026064 | -0.071874 | -0.13523 | -0.016938 | -0.068315 | -0.060575 | 0.052814 | 0.02322 | -0.04722 | 0.047188 | 0.12642 | -0.003902 | 0.061248 | 0.007024 | 0.11409 | 0.07184 | -0.026098 | -0.089454 | 0.028838 | -0.022539 | -0.014799 | 0.09859 | 0.068996 | -0.001444 | 0.092964 | -0.18804 | -0.08801 | -0.12113 | -0.021095
3895.9062 | 122.1771 | -0.17395 | 121.9757 | 0.076067 | -0.0451 | 0.020051 | -0.029595 | 0.06831 | 0.026064 | -0.085608 | -0.13981 | -0.016938 | -0.059159 | -0.065154 | 0.057392 | 0.02322 | -0.051798 | 0.04261 | 0.12184 | 0.000676 | 0.065827 | 0.016181 | 0.11409 | 0.07184 | -0.039832 | -0.094033 | 0.028838 | -0.013383 | -0.019378 | 0.10317 | 0.068996 | -0.006022 | 0.088386 | -0.1972 | -0.088011 | -0.11655 | -0.007361
3897.6719 | 122.2366 | -0.11902 | 121.9482 | 0.071489 | -0.049678 | 0.010893 | -0.034174 | 0.06831 | 0.030642 | -0.085608 | -0.13523 | -0.016938 | -0.072894 | -0.065154 | 0.057392 | 0.018642 | -0.04722 | 0.056344 | 0.11726 | -0.003902 | 0.056669 | 0.011602 | 0.11409 | 0.076418 | -0.039832 | -0.089454 | 0.028838 | -0.027118 | -0.019378 | 0.10317 | 0.064418 | -0.001444 | 0.10212 | -0.19262 | -0.08801 | -0.13029 | -0.025674
3899.3906 | 122.1497 | -0.18768 | 121.9986 | 0.071489 | -0.0451 | 0.015472 | -0.025017 | 0.072888 | 0.026064 | -0.08103 | -0.13981 | -0.021517 | -0.059159 | -0.065154 | 0.057392 | 0.018642 | -0.04722 | 0.056344 | 0.11726 | 0.000676 | 0.061248 | 0.020759 | 0.11866 | 0.07184 | -0.035254 | -0.094033 | 0.024259 | -0.013383 | -0.019378 | 0.10317 | 0.064418 | -0.001444 | 0.10212 | -0.1972 | -0.092589 | -0.11655 | -0.011939
3901.1719 | 122.1725 | -0.1831 | 121.9894 | 0.071489 | -0.049678 | 0.020051 | -0.029595 | 0.06831 | 0.021485 | -0.085608 | -0.13523 | -0.021517 | -0.063737 | -0.060575 | 0.057392 | 0.02322 | -0.04722 | 0.051766 | 0.11726 | -0.003902 | 0.065827 | 0.016181 | 0.11409 | 0.067261 | -0.039832 | -0.089454 | 0.024259 | -0.017961 | -0.014799 | 0.10317 | 0.068996 | -0.001444 | 0.097542 | -0.19262 | -0.08801 | -0.12113 | -0.016517
3902.9531 | 122.2412 | -0.15106 | 121.9711 | 0.071489 | -0.0451 | 0.015472 | -0.025017 | 0.06831 | 0.035221 | -0.08103 | -0.13065 | -0.012359 | -0.068315 | -0.065154 | 0.052814 | 0.02322 | -0.051798 | 0.056344 | 0.11726 | 0.000676 | 0.061248 | 0.020759 | 0.11409 | 0.080997 | -0.035254 | -0.084876 | 0.033417 | -0.022539 | -0.019378 | 0.09859 | 0.068996 | -0.006022 | 0.10212 | -0.18347 | -0.078854 | -0.12113 | -0.016517
3904.7344 | 122.1268 | -0.16479 | 121.9803 | 0.076067 | -0.049678 | 0.020051 | -0.029595 | 0.06831 | 0.030642 | -0.08103 | -0.13065 | -0.012359 | -0.063737 | -0.060575 | 0.057392 | 0.018642 | -0.051798 | 0.047188 | 0.12184 | -0.003902 | 0.065827 | 0.016181 | 0.11409 | 0.076418 | -0.035254 | -0.084876 | 0.033417 | -0.017961 | -0.014799 | 0.10317 | 0.064418 | -0.006022 | 0.092964 | -0.18804 | -0.078854 | -0.12113 | -0.011939
3906.4531 | 122.2137 | -0.11444 | 121.9254 | 0.06691 | -0.049678 | 0.010893 | -0.043331 | 0.06831 | 0.026064 | -0.085608 | -0.13523 | -0.016938 | -0.063737 | -0.069733 | 0.052814 | 0.02322 | -0.051798 | 0.056344 | 0.11269 | -0.003902 | 0.056669 | 0.002445 | 0.11409 | 0.07184 | -0.039832 | -0.089454 | 0.028838 | -0.017961 | -0.023957 | 0.09859 | 0.068996 | -0.006022 | 0.10212 | -0.18804 | -0.083432 | -0.11655 | -0.011939
3908.2656 | 122.1268 | -0.19684 | 122.0032 | 0.071489 | -0.049678 | 0.015472 | -0.038752 | 0.072888 | 0.030642 | -0.071874 | -0.12607 | -0.016938 | -0.063737 | -0.060575 | 0.057392 | 0.02322 | -0.042641 | 0.051766 | 0.11726 | -0.003902 | 0.061248 | 0.007024 | 0.11866 | 0.076418 | -0.026098 | -0.080297 | 0.028838 | -0.017961 | -0.014799 | 0.10317 | 0.068996 | 0.003135 | 0.097542 | -0.18346 | -0.083432 | -0.12113 | -0.021096
3909.9844 | 122.2549 | -0.13275 | 121.9757 | 0.085224 | -0.0451 | 0.024629 | -0.038752 | 0.06831 | 0.026064 | -0.076452 | -0.13065 | -0.021517 | -0.068315 | -0.065154 | 0.057392 | 0.02322 | -0.051798 | 0.047188 | 0.131 | 0.000676 | 0.070405 | 0.007024 | 0.11409 | 0.07184 | -0.030676 | -0.084876 | 0.024259 | -0.022539 | -0.019378 | 0.10317 | 0.068996 | -0.006022 | 0.092964 | -0.18804 | -0.078854 | -0.12571 | -0.016517
3911.7656 | 122.2458 | -0.15106 | 121.9894 | 0.085224 | -0.0451 | 0.010893 | -0.029595 | 0.063733 | 0.030642 | -0.076452 | -0.13065 | -0.016938 | -0.063737 | -0.060575 | 0.06197 | 0.018642 | -0.056376 | 0.051766 | 0.131 | 0.000676 | 0.056669 | 0.016181 | 0.10951 | 0.076418 | -0.030676 | -0.084876 | 0.028838 | -0.017961 | -0.014799 | 0.10775 | 0.064418 | -0.0106 | 0.097542 | -0.19262 | -0.074276 | -0.12571 | -0.007361
3913.5469 | 122.2687 | -0.12817 | 121.9711 | 0.080646 | -0.0451 | 0.020051 | -0.025017 | 0.06831 | 0.030642 | -0.08103 | -0.13065 | -0.021517 | -0.068315 | -0.065154 | 0.052814 | 0.02322 | -0.051798 | 0.051766 | 0.12642 | 0.000676 | 0.065827 | 0.020759 | 0.11409 | 0.076418 | -0.035254 | -0.084876 | 0.024259 | -0.022539 | -0.019378 | 0.09859 | 0.068996 | -0.006022 | 0.097542 | -0.18347 | -0.078854 | -0.12113 | -0.016517
3915.3594 | 122.2549 | -0.1236 | 122.0032 | 0.071489 | -0.040521 | 0.020051 | -0.029595 | 0.06831 | 0.030642 | -0.076452 | -0.13523 | -0.016938 | -0.068315 | -0.069733 | 0.052814 | 0.018642 | -0.051798 | 0.056344 | 0.11726 | 0.005255 | 0.065827 | 0.016181 | 0.11409 | 0.076418 | -0.030676 | -0.089454 | 0.028838 | -0.022539 | -0.023957 | 0.09859 | 0.064418 | -0.006022 | 0.10212 | -0.18804 | -0.083432 | -0.12113 | -0.016517
3917.1562 | 122.2046 | -0.15106 | 122.0215 | 0.076067 | -0.040521 | 0.020051 | -0.029595 | 0.063733 | 0.021485 | -0.08103 | -0.13065 | -0.021517 | -0.063737 | -0.065154 | 0.048236 | 0.02322 | -0.04722 | 0.047188 | 0.12184 | 0.005255 | 0.065827 | 0.016181 | 0.10951 | 0.067261 | -0.035254 | -0.084876 | 0.024259 | -0.017961 | -0.019378 | 0.094012 | 0.068996 | -0.001444 | 0.092964 | -0.17889 | -0.083432 | -0.11197 | -0.016517
3918.9375 | 122.2641 | -0.14191 | 121.9986 | 0.076067 | -0.054257 | 0.015472 | -0.025017 | 0.06831 | 0.026064 | -0.08103 | -0.13065 | -0.012359 | -0.068315 | -0.060575 | 0.052814 | 0.014064 | -0.051798 | 0.056344 | 0.12184 | -0.008481 | 0.061248 | 0.020759 | 0.11409 | 0.07184 | -0.035254 | -0.084876 | 0.033417 | -0.022539 | -0.014799 | 0.09859 | 0.05984 | -0.006022 | 0.10212 | -0.18347 | -0.078854 | -0.12113 | -0.016517
3920.6562 | 122.1497 | -0.16937 | 122.0215 | 0.080646 | -0.0451 | 0.015472 | -0.029595 | 0.059155 | 0.026064 | -0.071874 | -0.1215 | -0.021517 | -0.068315 | -0.069733 | 0.052814 | 0.02322 | -0.051798 | 0.056344 | 0.12642 | 0.000676 | 0.061248 | 0.016181 | 0.10493 | 0.07184 | -0.026098 | -0.075719 | 0.024259 | -0.022539 | -0.023957 | 0.09859 | 0.068996 | -0.006022 | 0.10212 | -0.17431 | -0.069697 | -0.12113 | -0.016517
3922.4375 | 122.1313 | -0.18768 | 122.0169 | 0.076067 | -0.040521 | 0.024629 | -0.038752 | 0.063733 | 0.035221 | -0.076452 | -0.12607 | -0.021517 | -0.068315 | -0.060575 | 0.052814 | 0.02322 | -0.04722 | 0.051766 | 0.12184 | 0.005255 | 0.070405 | 0.007024 | 0.10951 | 0.080997 | -0.030676 | -0.080297 | 0.024259 | -0.022539 | -0.014799 | 0.09859 | 0.068996 | -0.001444 | 0.097542 | -0.17889 | -0.078853 | -0.12113 | -0.021095
3924.1562 | 122.2321 | -0.16022 | 122.0123 | 0.071489 | -0.040521 | 0.015472 | -0.034174 | 0.077466 | 0.026064 | -0.067295 | -0.12607 | -0.016938 | -0.063737 | -0.074312 | 0.057392 | 0.02322 | -0.051798 | 0.047188 | 0.11726 | 0.005255 | 0.061248 | 0.011602 | 0.12324 | 0.07184 | -0.021519 | -0.080297 | 0.028838 | -0.017961 | -0.028536 | 0.10317 | 0.068996 | -0.006022 | 0.092964 | -0.18346 | -0.074275 | -0.12113 | -0.011939
3925.9375 | 122.1542 | -0.18768 | 122.0123 | 0.076067 | -0.0451 | 0.015472 | -0.020438 | 0.072888 | 0.026064 | -0.071874 | -0.12607 | -0.016938 | -0.063737 | -0.065154 | 0.06197 | 0.014064 | -0.04722 | 0.047188 | 0.12184 | 0.000676 | 0.061248 | 0.025338 | 0.11866 | 0.07184 | -0.026098 | -0.080297 | 0.028838 | -0.017961 | -0.019378 | 0.10775 | 0.05984 | -0.001444 | 0.092964 | -0.18804 | -0.078853 | -0.12571 | -0.016517
3927.7188 | 122.2092 | -0.16022 | 122.0123 | 0.076067 | -0.040521 | 0.015472 | -0.034174 | 0.072888 | 0.035221 | -0.08103 | -0.13523 | -0.026096 | -0.063737 | -0.065154 | 0.052814 | 0.018642 | -0.042641 | 0.051766 | 0.12184 | 0.005255 | 0.061248 | 0.011602 | 0.11866 | 0.080997 | -0.035254 | -0.089454 | 0.01968 | -0.017961 | -0.019378 | 0.09859 | 0.064418 | 0.003135 | 0.097542 | -0.18804 | -0.092589 | -0.11655 | -0.021096
3929.4375 | 122.1909 | -0.1831 | 122.0032 | 0.076067 | -0.049678 | 0.020051 | -0.029595 | 0.072888 | 0.030642 | -0.076452 | -0.13065 | -0.016938 | -0.072894 | -0.069733 | 0.057392 | 0.027798 | -0.051798 | 0.060923 | 0.12184 | -0.003902 | 0.065827 | 0.016181 | 0.11866 | 0.076418 | -0.030676 | -0.084876 | 0.028838 | -0.027118 | -0.023957 | 0.10317 | 0.073574 | -0.006022 | 0.1067 | -0.18804 | -0.078854 | -0.13029 | -0.021096
3931.2344 | 122.1863 | -0.17853 | 122.0352 | 0.076067 | -0.0451 | 0.024629 | -0.029595 | 0.06831 | 0.030642 | -0.071874 | -0.13523 | -0.016938 | -0.063737 | -0.065154 | 0.048236 | 0.02322 | -0.056376 | 0.060923 | 0.12184 | 0.000676 | 0.070405 | 0.016181 | 0.11409 | 0.076418 | -0.026098 | -0.089454 | 0.028838 | -0.017961 | -0.019378 | 0.094012 | 0.068996 | -0.0106 | 0.1067 | -0.18347 | -0.078854 | -0.11197 | -0.007361
3933.0156 | 122.2504 | -0.14191 | 121.9986 | 0.076067 | -0.049678 | 0.024629 | -0.025017 | 0.072888 | 0.026064 | -0.08103 | -0.13065 | -0.00778 | -0.063737 | -0.055996 | 0.057392 | 0.014064 | -0.04722 | 0.051766 | 0.12184 | -0.003902 | 0.070405 | 0.020759 | 0.11866 | 0.07184 | -0.035254 | -0.084876 | 0.037996 | -0.017961 | -0.01022 | 0.10317 | 0.05984 | -0.001444 | 0.097542 | -0.18804 | -0.083432 | -0.12113 | -0.016517
3934.7969 | 122.2092 | -0.16937 | 122.0398 | 0.076067 | -0.049678 | 0.033786 | -0.029595 | 0.072888 | 0.026064 | -0.076452 | -0.12607 | -0.016938 | -0.072894 | -0.069733 | 0.052814 | 0.018642 | -0.04722 | 0.047188 | 0.12184 | -0.003902 | 0.079562 | 0.016181 | 0.11866 | 0.07184 | -0.030676 | -0.080297 | 0.028838 | -0.027118 | -0.023957 | 0.09859 | 0.064418 | -0.001444 | 0.092964 | -0.17889 | -0.078853 | -0.12571 | -0.025674
3936.5 | 122.2549 | -0.14191 | 122.0169 | 0.071489 | -0.049678 | 0.010893 | -0.038752 | 0.063733 | 0.021485 | -0.076452 | -0.13065 | -0.012359 | -0.063737 | -0.065154 | 0.052814 | 0.018642 | -0.042641 | 0.056344 | 0.11726 | -0.003902 | 0.056669 | 0.007024 | 0.10951 | 0.067261 | -0.030676 | -0.084876 | 0.033417 | -0.017961 | -0.019378 | 0.09859 | 0.064418 | 0.003135 | 0.10212 | -0.18347 | -0.088011 | -0.11655 | -0.021096
3938.2812 | 122.2641 | -0.16022 | 122.0078 | 0.071489 | -0.0451 | 0.015472 | -0.029595 | 0.06831 | 0.026064 | -0.08103 | -0.12607 | -0.016938 | -0.059159 | -0.060575 | 0.052814 | 0.02322 | -0.04722 | 0.056344 | 0.11726 | 0.000676 | 0.061248 | 0.016181 | 0.11409 | 0.07184 | -0.035254 | -0.080297 | 0.028838 | -0.013383 | -0.014799 | 0.09859 | 0.068996 | -0.001444 | 0.10212 | -0.17889 | -0.078853 | -0.11197 | -0.011939
3940.0625 | 122.1497 | -0.17853 | 122.0718 | 0.080646 | -0.040521 | 0.020051 | -0.034174 | 0.06831 | 0.026064 | -0.076452 | -0.12607 | -0.026096 | -0.063737 | -0.065154 | 0.057392 | 0.02322 | -0.051798 | 0.047188 | 0.12642 | 0.005255 | 0.065827 | 0.011602 | 0.11409 | 0.07184 | -0.030676 | -0.080297 | 0.01968 | -0.017961 | -0.019378 | 0.10317 | 0.068996 | -0.006022 | 0.092964 | -0.18346 | -0.074275 | -0.12113 | -0.011939
3941.7812 | 122.2595 | -0.13733 | 122.0306 | 0.076067 | -0.054257 | 0.024629 | -0.025017 | 0.063733 | 0.026064 | -0.08103 | -0.1215 | -0.012359 | -0.063737 | -0.060575 | 0.052814 | 0.02322 | -0.04722 | 0.051766 | 0.12184 | -0.008481 | 0.070405 | 0.020759 | 0.10951 | 0.07184 | -0.035254 | -0.075719 | 0.033417 | -0.017961 | -0.014799 | 0.09859 | 0.068996 | -0.001444 | 0.097542 | -0.17431 | -0.074275 | -0.11655 | -0.016517
3943.5 | 122.2183 | -0.17395 | 122.0169 | 0.076067 | -0.040521 | 0.020051 | -0.029595 | 0.072888 | 0.030642 | -0.085608 | -0.13065 | -0.021517 | -0.059159 | -0.065154 | 0.052814 | 0.02322 | -0.04722 | 0.051766 | 0.12184 | 0.005255 | 0.065827 | 0.016181 | 0.11866 | 0.076418 | -0.039832 | -0.084876 | 0.024259 | -0.013383 | -0.019378 | 0.09859 | 0.068996 | -0.001444 | 0.097542 | -0.18347 | -0.083432 | -0.11197 | -0.011939
3945.2812 | 122.3007 | -0.13275 | 122.0032 | 0.076067 | -0.040521 | 0.010893 | -0.038752 | 0.06831 | 0.021485 | -0.08103 | -0.13065 | -0.021517 | -0.068315 | -0.065154 | 0.052814 | 0.018642 | -0.04722 | 0.051766 | 0.12184 | 0.005255 | 0.056669 | 0.007024 | 0.11409 | 0.067261 | -0.035254 | -0.084876 | 0.024259 | -0.022539 | -0.019378 | 0.09859 | 0.064418 | -0.001444 | 0.097542 | -0.18347 | -0.083432 | -0.12113 | -0.021095
3947.0625 | 122.1954 | -0.16937 | 122.0856 | 0.080646 | -0.0451 | 0.020051 | -0.038752 | 0.06831 | 0.030642 | -0.076452 | -0.13065 | -0.026096 | -0.068315 | -0.060575 | 0.057392 | 0.027798 | -0.04722 | 0.051766 | 0.12642 | 0.000676 | 0.065827 | 0.007024 | 0.11409 | 0.076418 | -0.030676 | -0.084876 | 0.01968 | -0.022539 | -0.014799 | 0.10317 | 0.073574 | -0.001444 | 0.097542 | -0.18804 | -0.083432 | -0.12571 | -0.021095
3948.8438 | 122.2137 | -0.18768 | 122.0215 | 0.076067 | -0.040521 | 0.020051 | -0.034174 | 0.063733 | 0.016907 | -0.076452 | -0.13065 | -0.016938 | -0.068315 | -0.065154 | 0.048236 | 0.02322 | -0.04722 | 0.047188 | 0.12184 | 0.005255 | 0.065827 | 0.011602 | 0.10951 | 0.062683 | -0.030676 | -0.084876 | 0.028838 | -0.022539 | -0.019378 | 0.094012 | 0.068996 | -0.001444 | 0.092964 | -0.17889 | -0.083432 | -0.11655 | -0.021095
3950.5469 | 122.2687 | -0.15564 | 122.0444 | 0.080646 | -0.0451 | 0.024629 | -0.025017 | 0.063733 | 0.030642 | -0.076452 | -0.12607 | -0.021517 | -0.068315 | -0.060575 | 0.052814 | 0.02322 | -0.04722 | 0.051766 | 0.12642 | 0.000676 | 0.070405 | 0.020759 | 0.10951 | 0.076418 | -0.030676 | -0.080297 | 0.024259 | -0.022539 | -0.014799 | 0.09859 | 0.068996 | -0.001444 | 0.097542 | -0.17889 | -0.078853 | -0.12113 | -0.021095
3952.3281 | 122.168 | -0.17853 | 122.0535 | 0.071489 | -0.0451 | 0.015472 | -0.034174 | 0.06831 | 0.035221 | -0.076452 | -0.13065 | -0.026096 | -0.072894 | -0.060575 | 0.052814 | 0.009486 | -0.04722 | 0.047188 | 0.11726 | 0.000676 | 0.061248 | 0.011602 | 0.11409 | 0.080997 | -0.030676 | -0.084876 | 0.01968 | -0.027118 | -0.014799 | 0.09859 | 0.055262 | -0.001444 | 0.092964 | -0.18347 | -0.083432 | -0.12571 | -0.025674
3954.1094 | 122.2778 | -0.14648 | 122.0261 | 0.071489 | -0.0451 | 0.024629 | -0.034174 | 0.063733 | 0.026064 | -0.076452 | -0.12607 | -0.021517 | -0.068315 | -0.069733 | 0.048236 | 0.018642 | -0.04722 | 0.051766 | 0.11726 | 0.000676 | 0.070405 | 0.011602 | 0.10951 | 0.07184 | -0.030676 | -0.080297 | 0.024259 | -0.022539 | -0.023957 | 0.094012 | 0.064418 | -0.001444 | 0.097542 | -0.17431 | -0.078853 | -0.11655 | -0.021095
3955.9062 | 122.3099 | -0.14191 | 122.0261 | 0.071489 | -0.049678 | 0.024629 | -0.034174 | 0.072888 | 0.026064 | -0.076452 | -0.13065 | -0.016938 | -0.063737 | -0.069733 | 0.057392 | 0.018642 | -0.042641 | 0.060923 | 0.11726 | -0.003902 | 0.070405 | 0.011602 | 0.11866 | 0.07184 | -0.030676 | -0.084876 | 0.028838 | -0.017961 | -0.023957 | 0.10317 | 0.064418 | 0.003135 | 0.1067 | -0.18804 | -0.088011 | -0.12113 | -0.021096
3957.625 | 122.2458 | -0.17395 | 122.049 | 0.076067 | -0.035942 | 0.024629 | -0.029595 | 0.063733 | 0.026064 | -0.076452 | -0.12607 | -0.016938 | -0.068315 | -0.074312 | 0.052814 | 0.027798 | -0.042641 | 0.051766 | 0.12184 | 0.009834 | 0.070405 | 0.016181 | 0.10951 | 0.07184 | -0.030676 | -0.080297 | 0.028838 | -0.022539 | -0.028536 | 0.09859 | 0.073574 | 0.003135 | 0.097542 | -0.17889 | -0.083432 | -0.12113 | -0.025674
3959.4062 | 122.3145 | -0.13275 | 122.0352 | 0.076067 | -0.049678 | 0.020051 | -0.034174 | 0.063733 | 0.030642 | -0.076452 | -0.13065 | -0.016938 | -0.068315 | -0.065154 | 0.052814 | 0.02322 | -0.04722 | 0.056344 | 0.12184 | -0.003902 | 0.065827 | 0.011602 | 0.10951 | 0.076418 | -0.030676 | -0.084876 | 0.028838 | -0.022539 | -0.019378 | 0.09859 | 0.068996 | -0.001444 | 0.10212 | -0.18347 | -0.083432 | -0.12113 | -0.021095
3961.2031 | 122.2092 | -0.17395 | 122.1039 | 0.071489 | -0.0451 | 0.024629 | -0.034174 | 0.072888 | 0.021485 | -0.08103 | -0.13523 | -0.021517 | -0.063737 | -0.069733 | 0.057392 | 0.02322 | -0.04722 | 0.051766 | 0.11726 | 0.000676 | 0.070405 | 0.011602 | 0.11866 | 0.067261 | -0.035254 | -0.089454 | 0.024259 | -0.017961 | -0.023957 | 0.10317 | 0.068996 | -0.001444 | 0.097542 | -0.19262 | -0.08801 | -0.12113 | -0.016517

## Thermal Data
Fire Time | A Position - Middle
-0.7458 | 7.2741
0.2542 | 7.2777
1.2542 | 7.2853
2.2542 | 7.2879
3.2542 | 7.2933
4.2542 | 7.2989
5.2542 | 7.3327
6.2542 | 7.7373
7.2542 | 8.3875
8.2542 | 9.4946
9.2542 | 12.528
10.2542 | 17.6079
11.2542 | 23.1033
12.2542 | 26.0513
13.2542 | 30.8239
14.2542 | 39.1317
15.2542 | 43.599
16.2542 | 49.7632
17.2542 | 53.2913
18.2542 | 56.9023
19.2542 | 61.8769
20.2542 | 66.9067
21.2542 | 72.4518
22.2542 | 79.9911
23.2542 | 90.6217
24.2542 | 102.6233
25.2542 | 110.1776
26.2542 | 117.2212
27.2542 | 118.0705
28.2542 | 119.0342
29.2542 | 123.1976
30.2542 | 124.259
31.2542 | 129.0992
32.2542 | 131.7444
33.2542 | 134.7257
34.2542 | 145.042
35.2542 | 151.7711
36.2542 | 155.4062
37.2542 | 161.6555
38.2542 | 165.1752
39.2542 | 169.0673
40.2542 | 171.4513
41.2542 | 175.6959
42.2542 | 179.5071
43.2542 | 180.575
44.2542 | 179.4576
45.2542 | 178.5191
46.2542 | 180.6325
47.2542 | 178.994
48.2542 | 178.2732
49.2542 | 178.2112
50.2542 | 180.5292
51.2542 | 185.2426
52.2542 | 187.3898
53.2542 | 188.9756
54.2542 | 191.4316
55.2542 | 193.3768
56.2542 | 197.3014
57.2542 | 197.4332
58.2542 | 197.8718
59.2542 | 196.9844
60.2542 | 199.3618
61.2542 | 202.4623
62.2542 | 202.321
63.2542 | 204.2431
64.2542 | 206.1534
65.2542 | 209.899
66.2542 | 212.709
67.2542 | 209.3702
68.2542 | 207.4114
69.2542 | 205.4338
70.2542 | 202.8154
71.2542 | 199.0848
72.2542 | 198.9269
73.2542 | 198.1573
74.2542 | 198.3143
75.2542 | 203.2452
76.2542 | 203.2861
77.2542 | 205.3801
78.2542 | 207.3513
79.2542 | 209.1269
80.2542 | 210.65
81.2542 | 212.0985
82.2542 | 211.2938
83.2542 | 216.6927
84.2542 | 219.7231
85.2542 | 222.4498
86.2542 | 222.6794
87.2542 | 222.8834
88.2542 | 224.6345
89.2542 | 226.4392
90.2542 | 226.0471
91.2542 | 226.8024
92.2542 | 228.4075
93.2542 | 227.6078
94.2542 | 226.9187
95.2542 | 227.0384
96.2542 | 225.5061
97.2542 | 227.3523
98.2542 | 227.0435
99.2542 | 229.4085
100.2542 | 235.8578
101.2542 | 238.1535
102.2542 | 240.8661
103.2542 | 245.3363
104.2542 | 247.6886
105.2542 | 248.7213
106.2542 | 252.9017
107.2542 | 255.4346
108.2542 | 255.3814
109.2542 | 253.4672
110.2542 | 254.4997
111.2542 | 255.5574
112.2542 | 258.2221
113.2542 | 257.3518
114.2542 | 259.5865
115.2542 | 260.2833
116.2542 | 262.5341
117.2542 | 262.9648
118.2542 | 262.1712
119.2542 | 258.5998
120.2542 | 258.0035
121.2542 | 256.0905
122.2542 | 254.8373
123.2542 | 254.4345
124.2542 | 254.4725
125.2542 | 253.3841
126.2542 | 253.1585
127.2542 | 254.7971
128.2542 | 259.9414
129.2542 | 259.6714
130.2542 | 259.0188
131.2542 | 262.8774
132.2542 | 263.568
133.2542 | 264.4192
134.2542 | 264.8032
135.2542 | 272.0715
136.2542 | 273.5725
137.2542 | 274.5758
138.2542 | 275.8914
139.2542 | 276.962
140.2542 | 276.2583
141.2542 | 276.0916
142.2542 | 276.0545
143.2542 | 276.0408
144.2542 | 276.063
145.2542 | 277.5793
146.2542 | 279.5421
147.2542 | 277.8326
148.2542 | 277.4718
149.2542 | 278.1453
150.2542 | 281.1367
151.2542 | 284.6047
152.2542 | 285.3507
153.2542 | 284.5174
154.2542 | 290.9578
155.2542 | 291.289
156.2542 | 292.304
157.2542 | 299.4129
158.2542 | 300.7019
159.2542 | 303.0134
160.2542 | 303.2127
161.2542 | 305.4216
162.2542 | 312.4183
163.2542 | 311.1414
164.2542 | 309.8133
165.2542 | 309.0806
166.2542 | 311.312
167.2542 | 314.86
168.2542 | 313.7216
169.2542 | 310.6691
170.2542 | 310.1683
171.2542 | 308.3623
172.2542 | 304.9137
173.2542 | 301.4705
174.2542 | 297.344
175.2542 | 298.8392
176.2542 | 299.1351
177.2542 | 298.3161
178.2542 | 297.5769
179.2542 | 297.7057
180.2542 | 297.2645
181.2542 | 296.7681
182.2542 | 292.2488
183.2542 | 293.8507
184.2542 | 292.0281
185.2542 | 287.8051
186.2542 | 286.5672
187.2542 | 287.0826
188.2542 | 287.408
189.2542 | 288.4082
190.2542 | 292.7771
191.2542 | 291.5527
192.2542 | 293.9694
193.2542 | 293.107
194.2542 | 292.8626
195.2542 | 292.3312
196.2542 | 292.2062
197.2542 | 292.7692
198.2542 | 291.6003
199.2542 | 288.2438
200.2542 | 288.3904
201.2542 | 288.5719
202.2542 | 288.4558
203.2542 | 289.89
204.2542 | 298.9301
205.2542 | 297.4741
206.2542 | 297.3724
207.2542 | 301.7491
208.2542 | 301.2747
209.2542 | 298.4918
210.2542 | 300.9146
211.2542 | 301.4405
212.2542 | 301.4696
213.2542 | 308.9216
214.2542 | 309.4468
215.2542 | 312.5409
216.2542 | 315
217.2542 | 318.2993
218.2542 | 316.6576
219.2542 | 315.5193
220.2542 | 318.7671
221.2542 | 320.8385
222.2542 | 319.72
223.2542 | 320.0098
224.2542 | 319.6848
225.2542 | 319.9445
226.2542 | 325.8941
227.2542 | 326.5479
228.2542 | 325.1439
229.2542 | 324.7415
230.2542 | 324.8776
231.2542 | 327.2954
232.2542 | 325.4109
233.2542 | 326.5569
234.2542 | 327.3457
235.2542 | 326.2721
236.2542 | 332.27
237.2542 | 332.9432
238.2542 | 340.2808
239.2542 | 343.6665
240.2542 | 342.3247
241.2542 | 342.4595
242.2542 | 341.8476
243.2542 | 339.9666
244.2542 | 343.5449
245.2542 | 349.7235
246.2542 | 351.2782
247.2542 | 354.9763
248.2542 | 352.9412
249.2542 | 360.2009
250.2542 | 363.5399
251.2542 | 364.7846
252.2542 | 376.7473
253.2542 | 378.057
254.2542 | 376.9155
255.2542 | 379.4095
256.2542 | 382.6039
257.2542 | 383.4027
258.2542 | 382.7044
259.2542 | 380.9881
260.2542 | 381.5211
261.2542 | 385.1787
262.2542 | 382.6988
263.2542 | 379.8647
264.2542 | 378.9187
265.2542 | 379.9459
266.2542 | 384.2257
267.2542 | 384.0079
268.2542 | 388.2011
269.2542 | 387.3564
270.2542 | 386.8993
271.2542 | 384.0656
272.2542 | 382.165
273.2542 | 383.3562
274.2542 | 390.6757
275.2542 | 390.4748
276.2542 | 390.5777
277.2542 | 393.3732
278.2542 | 390.9732
279.2542 | 388.5972
280.2542 | 389.6303
281.2542 | 395.0138
282.2542 | 396.6434
283.2542 | 401.6776
284.2542 | 408.96
285.2542 | 403.145
286.2542 | 400.2059
287.2542 | 403.1649
288.2542 | 405.7995
289.2542 | 406.9333
290.2542 | 402.405
291.2542 | 399.6659
292.2542 | 398.1138
293.2542 | 399.2788
294.2542 | 399.7138
295.2542 | 405.0278
296.2542 | 406.4445
297.2542 | 410.9318
298.2542 | 413.2044
299.2542 | 418.7799
300.2542 | 421.0533
301.2542 | 419.8218
302.2542 | 428.0797
303.2542 | 430.4427
304.2542 | 447.4205
305.2542 | 456.4361
306.2542 | 461.6996
307.2542 | 464.6399
308.2542 | 470.9562
309.2542 | 481.2966
310.2542 | 484.696
311.2542 | 489.7622
312.2542 | 487.522
313.2542 | 500.3374
314.2542 | 507.7247
315.2542 | 529.1473
316.2542 | 531.8409
317.2542 | 532.6371
318.2542 | 536.2138
319.2542 | 558.0316
320.2542 | 559.4125
321.2542 | 566.8076
322.2542 | 563.9162
323.2542 | 581.2641
324.2542 | 578.4569
325.2542 | 568.1353
326.2542 | 579.0836
327.2542 | 568.6799
328.2542 | 562.7383
329.2542 | 556.7146
330.2542 | 563.1258
331.2542 | 584.3379
332.2542 | 594.947
333.2542 | 606.6352
334.2542 | 606.3004
335.2542 | 612.3984
336.2542 | 616.5154
337.2542 | 628.931
338.2542 | 628.5902
339.2542 | 632.5953
340.2542 | 632.5709
341.2542 | 626.8629
342.2542 | 630.6611
343.2542 | 627.4364
344.2542 | 644.7984
345.2542 | 642.9479
346.2542 | 645.6501
347.2542 | 650.3639
348.2542 | 647.5046
349.2542 | 648.3768
350.2542 | 645.765
351.2542 | 624.9173
352.2542 | 614.5684
353.2542 | 607.2273
354.2542 | 601.093
355.2542 | 604.0086
356.2542 | 599.9993
357.2542 | 589.6908
358.2542 | 588.5174
359.2542 | 580.2052
360.2542 | 589.6252
361.2542 | 590.7949
362.2542 | 592.6251
363.2542 | 586.4916
364.2542 | 600.7325
365.2542 | 623.4917
366.2542 | 618.5723
367.2542 | 620.5876
368.2542 | 618.2232
369.2542 | 609.9254
370.2542 | 612.3763
371.2542 | 609.2378
372.2542 | 606.5104
373.2542 | 613.6594
374.2542 | 625.9032
375.2542 | 625.1971
376.2542 | 626.4372
377.2542 | 642.1572
378.2542 | 631.801
379.2542 | 620.8877
380.2542 | 614.5523
381.2542 | 616.4303
382.2542 | 611.666
383.2542 | 610.8706
384.2542 | 613.5791
385.2542 | 605.9629
386.2542 | 612.4452
387.2542 | 605.6988
388.2542 | 613.3797
389.2542 | 615.4119
390.2542 | 616.765
391.2542 | 609.6978
392.2542 | 600.7364
393.2542 | 590.8624
394.2542 | 583.0114
395.2542 | 583.6311
396.2542 | 583.8693
397.2542 | 586.0863
398.2542 | 583.5768
399.2542 | 584.6702
400.2542 | 580.6526
401.2542 | 581.8673
402.2542 | 580.3247
403.2542 | 581.5142
404.2542 | 576.1522
405.2542 | 573.4455
406.2542 | 580.515
407.2542 | 582.1887
408.2542 | 588.22
409.2542 | 587.4967
410.2542 | 586.8428
411.2542 | 586.5193
412.2542 | 584.4746
413.2542 | 582.1342
414.2542 | 577.9215
415.2542 | 592.0827
416.2542 | 584.8575
417.2542 | 579.6164
418.2542 | 581.6347
419.2542 | 576.5711
420.2542 | 588.1147
421.2542 | 590.857
422.2542 | 596.5277
423.2542 | 587.3276
424.2542 | 583.9541
425.2542 | 598.8271
426.2542 | 595.3901
427.2542 | 591.8292
428.2542 | 588.7376
429.2542 | 587.5814
430.2542 | 589.0887
431.2542 | 591.3931
432.2542 | 592.912
433.2542 | 593.7854
434.2542 | 596.7535
435.2542 | 595.4496
436.2542 | 603.5574
437.2542 | 603.9101
438.2542 | 601.8656
439.2542 | 600.6414
440.2542 | 602.0726
441.2542 | 603.0564
442.2542 | 602.0333
443.2542 | 605.0451
444.2542 | 602.6098
445.2542 | 605.2339
446.2542 | 604.7768
447.2542 | 610.546
448.2542 | 608.1164
449.2542 | 613.7058
450.2542 | 620.9576
451.2542 | 621.1826
452.2542 | 623.369
453.2542 | 619.4635
454.2542 | 615.7345
455.2542 | 613.3438
456.2542 | 618.9698
457.2542 | 617.6761
458.2542 | 618.524
459.2542 | 622.6873
460.2542 | 621.3051
461.2542 | 617.5619
462.2542 | 615.251
463.2542 | 621.4476
464.2542 | 618.2163
465.2542 | 621.3277
466.2542 | 625.3431
467.2542 | 625.7847
468.2542 | 624.7334
469.2542 | 625.6631
470.2542 | 620.51
471.2542 | 618.6542
472.2542 | 615.5309
473.2542 | 613.1394
474.2542 | 621.0976
475.2542 | 621.277
476.2542 | 615.721
477.2542 | 614.8178
478.2542 | 614.0107
479.2542 | 615.7889
480.2542 | 615.7451
481.2542 | 617.7102
482.2542 | 618.9998
483.2542 | 619.1376
484.2542 | 621.0489
485.2542 | 623.889
486.2542 | 622.2104
487.2542 | 620.0915
488.2542 | 617.9681
489.2542 | 623.1349
490.2542 | 619.0279
491.2542 | 623.1919
492.2542 | 627.1558
493.2542 | 631.0774
494.2542 | 634.2487
495.2542 | 10.8436
496.2542 | 9.335
497.2542 | 9.3639
498.2542 | 9.3232
499.2542 | 9.4034
500.2542 | 9.2522
501.2542 | 9.2917
502.2542 | 9.2779
503.2542 | 9.4061
504.2542 | 9.4983
505.2542 | 9.4934
506.2542 | 9.525
507.2542 | 9.7401
508.2542 | 9.6564
509.2542 | 9.4561
510.2542 | 9.4205
511.2542 | 9.5768
512.2542 | 9.6384
513.2542 | 9.7129
514.2542 | 9.5844
515.2542 | 9.5413
516.2542 | 9.6997
517.2542 | 9.8058
518.2542 | 9.8809
519.2542 | 9.8868
520.2542 | 9.9549
521.2542 | 10.053
522.2542 | 10.1453
523.2542 | 10.1144
524.2542 | 10.1969
525.2542 | 10.124
526.2542 | 10.2576
527.2542 | 10.253
528.2542 | 10.3457
529.2542 | 10.3967
530.2542 | 10.5751
531.2542 | 10.8531
532.2542 | 10.806
533.2542 | 10.9944
534.2542 | 11.1084
535.2542 | 11.237
536.2542 | 11.3409
537.2542 | 11.48
538.2542 | 11.539
539.2542 | 11.445
540.2542 | 11.6982
541.2542 | 11.6641
542.2542 | 11.9002
543.2542 | 11.8824
544.2542 | 12.0572
545.2542 | 11.9987
546.2542 | 11.9458
547.2542 | 12.2123
548.2542 | 12.3664
549.2542 | 12.4279
550.2542 | 12.4286
551.2542 | 12.3991
552.2542 | 12.5365
553.2542 | 12.7479
554.2542 | 12.8437
555.2542 | 12.9085
556.2542 | 12.8966
557.2542 | 13.0944
558.2542 | 13.2788
559.2542 | 13.3709
560.2542 | 13.5469
561.2542 | 13.5946
562.2542 | 13.6445
563.2542 | 13.8559
564.2542 | 14.0234
565.2542 | 14.1029
566.2542 | 14.0996
567.2542 | 14.119
568.2542 | 14.3062
569.2542 | 14.4065
570.2542 | 14.653
571.2542 | 14.5515
572.2542 | 14.4653
573.2542 | 14.5536
574.2542 | 14.5763
575.2542 | 14.7507
576.2542 | 14.8143
577.2542 | 15.3173
578.2542 | 15.405
579.2542 | 15.4565
580.2542 | 15.6354
581.2542 | 15.7187
582.2542 | 15.7171
583.2542 | 15.6808
584.2542 | 15.207
585.2542 | 14.4024
586.2542 | 13.9766
587.2542 | 13.5105
588.2542 | 13.5061
589.2542 | 12.8809
590.2542 | 12.8935
591.2542 | 12.8834
592.2542 | 15.6064
593.2542 | 14.9115
594.2542 | 15.3494
595.2542 | 15.417
596.2542 | 12.8943
597.2542 | 13.2076
598.2542 | 13.2609
599.2542 | 13.3447
600.2542 | 13.3499
601.2542 | 12.8635
602.2542 | 13.2903
603.2542 | 13.2879
604.2542 | 13.0295
605.2542 | 12.9991
606.2542 | 12.9891
607.2542 | 13.3882
608.2542 | 13.0459
609.2542 | 13.0928
610.2542 | 12.9909
611.2542 | 13.0312
612.2542 | 13.0235
613.2542 | 12.9659
614.2542 | 12.959
615.2542 | 12.9509
616.2542 | 12.9496
617.2542 | 12.9649
618.2542 | 13.1247
619.2542 | 13.0859
620.2542 | 12.9567
621.2542 | 12.9561
622.2542 | 12.9642
623.2542 | 12.9654
624.2542 | 12.9635
625.2542 | 12.9497
626.2542 | 12.9511
627.2542 | 12.9517
628.2542 | 12.9483
629.2542 | 12.9431
630.2542 | 12.9326
631.2542 | 12.9289
632.2542 | 12.9404
633.2542 | 12.9159
634.2542 | 12.8554
635.2542 | 12.8149
636.2542 | 12.8454
637.2542 | 12.7913
638.2542 | 12.8056
639.2542 | 12.8439
640.2542 | 12.8138
641.2542 | 12.7765
642.2542 | 12.6931
643.2542 | 12.731
644.2542 | 12.7038
645.2542 | 12.7346
646.2542 | 12.7922
647.2542 | 12.7725
648.2542 | 12.6866
649.2542 | 12.7192
650.2542 | 12.724
651.2542 | 12.7397
652.2542 | 12.6833
653.2542 | 12.7039
654.2542 | 12.7463
655.2542 | 12.8113
656.2542 | 12.7652
657.2542 | 12.7958
658.2542 | 12.8435
659.2542 | 12.8452
660.2542 | 12.8414
661.2542 | 12.7873
662.2542 | 12.8067
663.2542 | 12.691
664.2542 | 12.7089
665.2542 | 12.7196
666.2542 | 12.7211
667.2542 | 12.7268
668.2542 | 12.7535
669.2542 | 12.7538
670.2542 | 12.7534
671.2542 | 12.7561
672.2542 | 12.7556
673.2542 | 12.7535
674.2542 | 12.7652
675.2542 | 12.7671
676.2542 | 12.7753
677.2542 | 12.7879
678.2542 | 12.7853
679.2542 | 12.7704
680.2542 | 12.7725
681.2542 | 12.7716
682.2542 | 12.7822
683.2542 | 12.779
684.2542 | 12.7883
685.2542 | 12.782
686.2542 | 12.7836
687.2542 | 12.785
688.2542 | 12.7848
689.2542 | 12.7871
690.2542 | 12.7942
691.2542 | 12.7926
692.2542 | 12.8497
693.2542 | 12.8369
694.2542 | 12.8446
695.2542 | 12.8439
696.2542 | 12.8502
697.2542 | 12.8429
698.2542 | 12.8198
699.2542 | 12.8127
700.2542 | 12.8065
701.2542 | 12.7978
702.2542 | 12.801
703.2542 | 12.7949
704.2542 | 12.8058
705.2542 | 12.8052
706.2542 | 12.808
707.2542 | 12.813
708.2542 | 12.8618
709.2542 | 12.8943
710.2542 | 12.9124
711.2542 | 12.894
712.2542 | 12.8937
713.2542 | 12.9777
714.2542 | 13.2192
715.2542 | 14.0177
716.2542 | 14.0358
717.2542 | 15.0485
718.2542 | 15.4762
719.2542 | 15.4611
720.2542 | 15.6777
721.2542 | 15.6659
722.2542 | 15.3771
723.2542 | 14.616
724.2542 | 14.3925
725.2542 | 15.1082
726.2542 | 14.7407
727.2542 | 14.6517
728.2542 | 13.8605
729.2542 | 13.8854
730.2542 | 15.3036
731.2542 | 15.4535
732.2542 | 14.8646
733.2542 | 12.9666
734.2542 | 14.8071
735.2542 | 14.318
736.2542 | 11.0587
737.2542 | 9.2243
738.2542 | 8.6233
739.2542 | 8.6401
740.2542 | 9.1347
741.2542 | 8.6495
742.2542 | 15.5168
743.2542 | 14.5443
744.2542 | 13.5811
745.2542 | 176.5317
746.2542 | 9.0524
747.2542 | 8.6734
748.2542 | 8.6718
749.2542 | 8.6409
750.2542 | 13.1981
751.2542 | 8.6675
752.2542 | 409.3579
753.2542 | 641.0853
754.2542 | 642.4931
755.2542 | 641.3788
756.2542 | 640.5055
757.2542 | 639.3652
758.2542 | 644.5392
759.2542 | 641.794
760.2542 | 638.0098
761.2542 | 635.3805
762.2542 | 633.0144
763.2542 | 633.5222
764.2542 | 634.3473
765.2542 | 636.7943
766.2542 | 639.2828
767.2542 | 642.2575
768.2542 | 639.3282
769.2542 | 643.2547
770.2542 | 641.3966
771.2542 | 638.3001
772.2542 | 637.8452
773.2542 | 636.9256
774.2542 | 640.1015
775.2542 | 639.4452
776.2542 | 636.9263
777.2542 | 634.2198
778.2542 | 632.8192
779.2542 | 633.7705
780.2542 | 632.2457
781.2542 | 632.538
782.2542 | 632.3087
783.2542 | 630.8355
784.2542 | 629.1166
785.2542 | 626.7912
786.2542 | 627.8766
787.2542 | 628.687
788.2542 | 633.2448
789.2542 | 631.0811
790.2542 | 629.4288
791.2542 | 632.1259
792.2542 | 630.5867
793.2542 | 630.6523
794.2542 | 629.9989
795.2542 | 627.7961
796.2542 | 625.529
797.2542 | 624.5183
798.2542 | 621.4171
799.2542 | 622.4151
800.2542 | 620.9458
801.2542 | 620.3998
802.2542 | 620.9551
803.2542 | 620.2829
804.2542 | 620.0556
805.2542 | 618.682
806.2542 | 617.4395
807.2542 | 616.3189
808.2542 | 616.5803
809.2542 | 614.8015
810.2542 | 613.9451
811.2542 | 609.9099
812.2542 | 608.4745
813.2542 | 609.6115
814.2542 | 611.137
815.2542 | 612.1358
816.2542 | 614.7909
817.2542 | 615.6064
818.2542 | 617.7042
819.2542 | 617.1526
820.2542 | 616.2958
821.2542 | 615.355
822.2542 | 616.138
823.2542 | 614.3234
824.2542 | 612.4804
825.2542 | 611.0003
826.2542 | 610.631
827.2542 | 609.6242
828.2542 | 608.9971
829.2542 | 609.5757
830.2542 | 607.5683
831.2542 | 610.1672
832.2542 | 610.5562
833.2542 | 609.5208
834.2542 | 612.9859
835.2542 | 616.5549
836.2542 | 620.1861
837.2542 | 621.6284
838.2542 | 622.0943
839.2542 | 621.9492
840.2542 | 621.2531
841.2542 | 622.0157
842.2542 | 625.4839
843.2542 | 627.7137
844.2542 | 626.9078
845.2542 | 625.9819
846.2542 | 625.8375
847.2542 | 627.6038
848.2542 | 627.4968
849.2542 | 630.9567
850.2542 | 629.1732
851.2542 | 629.4674
852.2542 | 628.3647
853.2542 | 626.7367
854.2542 | 625.9699
855.2542 | 625.7601
856.2542 | 629.3171
857.2542 | 627.1363
858.2542 | 627.5331
859.2542 | 627.4088
860.2542 | 624.1796
861.2542 | 622.7595
862.2542 | 622.2162
863.2542 | 624.026
864.2542 | 625.697
865.2542 | 627.0215
866.2542 | 628.6836
867.2542 | 632.2431
868.2542 | 631.6402
869.2542 | 629.3823
870.2542 | 624.4332
871.2542 | 627.0698
872.2542 | 630.4
873.2542 | 629.955
874.2542 | 628.3186
875.2542 | 626.3131
876.2542 | 624.3404
877.2542 | 625.3326
878.2542 | 624.4904
879.2542 | 621.9887
880.2542 | 621.2535
881.2542 | 622.5254
882.2542 | 621.7881
883.2542 | 621.4408
884.2542 | 621.8719
885.2542 | 624.413
886.2542 | 627.1015
887.2542 | 631.9897
888.2542 | 632.2221
889.2542 | 634.723
890.2542 | 633.5802
891.2542 | 631.6805
892.2542 | 629.1446
893.2542 | 627.3151
894.2542 | 628.9187
895.2542 | 631.5731
896.2542 | 633.1355
897.2542 | 633.092
898.2542 | 631.4031
899.2542 | 633.6715
900.2542 | 640.708
901.2542 | 648.0427
902.2542 | 650.5795
903.2542 | 648.4656
904.2542 | 647.5859
905.2542 | 641.5231
906.2542 | 643.9918
907.2542 | 651.2102
908.2542 | 650.8664
909.2542 | 653.2679
910.2542 | 653.2578
911.2542 | 658.9696
912.2542 | 663.3594
913.2542 | 666.4702
914.2542 | 668.6461
915.2542 | 670.8763
916.2542 | 678.9796
917.2542 | 678.2044
918.2542 | 673.3724
919.2542 | 668.6027
920.2542 | 665.2031
921.2542 | 663.9294
922.2542 | 662.3084
923.2542 | 659.5707
924.2542 | 665.9893
925.2542 | 666.0835
926.2542 | 670.4782
927.2542 | 666.8413
928.2542 | 668.813
929.2542 | 668.2986
930.2542 | 676.3334
931.2542 | 676.6028
932.2542 | 676.4789
933.2542 | 673.9665
934.2542 | 675.6199
935.2542 | 679.9045
936.2542 | 676.5197
937.2542 | 675.7467
938.2542 | 680.5279
939.2542 | 680.4841
940.2542 | 685.0454
941.2542 | 684.2719
942.2542 | 680.2524
943.2542 | 680.0661
944.2542 | 680.2104
945.2542 | 679.5565
946.2542 | 677.6782
947.2542 | 670.9503
948.2542 | 670.9202
949.2542 | 666.9638
950.2542 | 663.9292
951.2542 | 663.9798
952.2542 | 665.5463
953.2542 | 665.6006
954.2542 | 665.3272
955.2542 | 663.7549
956.2542 | 664.1514
957.2542 | 664.79
958.2542 | 664.8165
959.2542 | 665.5993
960.2542 | 665.7042
961.2542 | 666.5981
962.2542 | 667.9231
963.2542 | 668.5186
964.2542 | 668.6882
965.2542 | 673.1273
966.2542 | 676.5166
967.2542 | 688.7308
968.2542 | 682.9849
969.2542 | 685.9771
970.2542 | 685.8792
971.2542 | 681.3282
972.2542 | 678.8387
973.2542 | 679.9324
974.2542 | 682.0853
975.2542 | 681.9211
976.2542 | 676.8875
977.2542 | 678.1777
978.2542 | 676.6167
979.2542 | 674.7171
980.2542 | 679.3211
981.2542 | 683.8485
982.2542 | 687.573
983.2542 | 684.1114
984.2542 | 692.0379
985.2542 | 692.2341
986.2542 | 686.8414
987.2542 | 680.915
988.2542 | 679.0332
989.2542 | 675.9753
990.2542 | 675.2309
991.2542 | 675.7433
992.2542 | 684.2656
993.2542 | 686.4042
994.2542 | 684.6409
995.2542 | 682.4686
996.2542 | 688.1902
997.2542 | 688.4636
998.2542 | 686.8437
999.2542 | 683.078
1000.2542 | 683.4701
1001.2542 | 677.9507
1002.2542 | 679.1201
1003.2542 | 678.2013
1004.2542 | 677.3773
1005.2542 | 682.5568
1006.2542 | 686.7039
1007.2542 | 688.2795
1008.2542 | 683.5787
1009.2542 | 681.1357
1010.2542 | 686.7673
1011.2542 | 686.0721
1012.2542 | 683.2133
1013.2542 | 679.8355
1014.2542 | 677.6085
1015.2542 | 677.2863
1016.2542 | 684.6434
1017.2542 | 685.012
1018.2542 | 688.6579
1019.2542 | 685.9088
1020.2542 | 684.1476
1021.2542 | 683.0628
1022.2542 | 687.225
1023.2542 | 684.7054
1024.2542 | 686.3248
1025.2542 | 685.8351
1026.2542 | 687.9062
1027.2542 | 690.1354
1028.2542 | 687.1267
1029.2542 | 683.9424
1030.2542 | 683.7333
1031.2542 | 683.9516
1032.2542 | 683.9142
1033.2542 | 681.9701
1034.2542 | 681.4151
1035.2542 | 680.9697
1036.2542 | 680.8034
1037.2542 | 682.3628
1038.2542 | 682.0666
1039.2542 | 686.8588
1040.2542 | 686.5878
1041.2542 | 684.1949
1042.2542 | 683.4559
1043.2542 | 683.9179
1044.2542 | 683.9087
1045.2542 | 684.9133
1046.2542 | 684.2024
1047.2542 | 684.6581
1048.2542 | 684.6235
1049.2542 | 688.2155
1050.2542 | 690.4413
1051.2542 | 690.2895
1052.2542 | 694.454
1053.2542 | 696.5566
1054.2542 | 693.908
1055.2542 | 698.9118
1056.2542 | 695.1652
1057.2542 | 691.8559
1058.2542 | 691.8322
1059.2542 | 695.0335
1060.2542 | 692.507
1061.2542 | 699.3851
1062.2542 | 696.9619
1063.2542 | 698.835
1064.2542 | 696.796
1065.2542 | 693.919
1066.2542 | 691.6518
1067.2542 | 690.6796
1068.2542 | 690.9015
1069.2542 | 691.9174
1070.2542 | 692.4444
1071.2542 | 690.5723
1072.2542 | 688.4373
1073.2542 | 687.7857
1074.2542 | 692.5717
1075.2542 | 691.7426
1076.2542 | 690.4124
1077.2542 | 697.1193
1078.2542 | 694.8334
1079.2542 | 692.9517
1080.2542 | 691.4214
1081.2542 | 689.841
1082.2542 | 689.353
1083.2542 | 688.3066
1084.2542 | 687.9908
1085.2542 | 686.3311
1086.2542 | 685.3319
1087.2542 | 688.192
1088.2542 | 687.7922
1089.2542 | 686.7995
1090.2542 | 684.5285
1091.2542 | 685.8561
1092.2542 | 685.5092
1093.2542 | 684.9422
1094.2542 | 684.5359
1095.2542 | 687.0811
1096.2542 | 688.034
1097.2542 | 688.9214
1098.2542 | 687.6654
1099.2542 | 685.8939
1100.2542 | 684.6793
1101.2542 | 686.1785
1102.2542 | 686.524
1103.2542 | 685.9802
1104.2542 | 685.9562
1105.2542 | 686.7681
1106.2542 | 690.6594
1107.2542 | 691.6768
1108.2542 | 694.0108
1109.2542 | 691.4254
1110.2542 | 690.7675
1111.2542 | 696.22
1112.2542 | 693.1621
1113.2542 | 691.8612
1114.2542 | 691.0341
1115.2542 | 690.3152
1116.2542 | 688.8676
1117.2542 | 686.3245
1118.2542 | 687.3521
1119.2542 | 688.4246
1120.2542 | 689.0745
1121.2542 | 688.0517
1122.2542 | 687.4
1123.2542 | 687.6473
1124.2542 | 687.8813
1125.2542 | 687.0452
1126.2542 | 687.0973
1127.2542 | 687.6121
1128.2542 | 686.8583
1129.2542 | 685.6766
1130.2542 | 683.9878
1131.2542 | 682.6589
1132.2542 | 683.2518
1133.2542 | 684.1949
1134.2542 | 684.5797
1135.2542 | 684.2046
1136.2542 | 684.6275
1137.2542 | 686.5002
1138.2542 | 684.9252
1139.2542 | 686.0544
1140.2542 | 685.5025
1141.2542 | 688.215
1142.2542 | 692.731
1143.2542 | 694.5209
1144.2542 | 691.5367
1145.2542 | 691.5677
1146.2542 | 695.9147
1147.2542 | 695.2229
1148.2542 | 695.1637
1149.2542 | 696.5256
1150.2542 | 694.012
1151.2542 | 694.9978
1152.2542 | 693.6812
1153.2542 | 693.5834
1154.2542 | 693.0272
1155.2542 | 691.8128
1156.2542 | 691.0307
1157.2542 | 690.6317
1158.2542 | 690.5019
1159.2542 | 688.9152
1160.2542 | 689.2367
1161.2542 | 688.6047
1162.2542 | 688.9086
1163.2542 | 689.5821
1164.2542 | 694.4629
1165.2542 | 698.2013
1166.2542 | 695.543
1167.2542 | 697.0205
1168.2542 | 697.2323
1169.2542 | 697.0204
1170.2542 | 696.4315
1171.2542 | 696.7663
1172.2542 | 696.5854
1173.2542 | 696.4221
1174.2542 | 699.0144
1175.2542 | 698.662
1176.2542 | 699.2681
1177.2542 | 698.3472
1178.2542 | 697.3896
1179.2542 | 696.8331
1180.2542 | 696.6399
1181.2542 | 696.362
1182.2542 | 698.6664
1183.2542 | 699.2812
1184.2542 | 699.4479
1185.2542 | 698.9554
1186.2542 | 700.5813
1187.2542 | 700.7653
1188.2542 | 701.9724
1189.2542 | 699.7009
1190.2542 | 703.801
1191.2542 | 702.7103
1192.2542 | 707.2959
1193.2542 | 707.2078
1194.2542 | 706.0766
1195.2542 | 704.9066
1196.2542 | 703.586
1197.2542 | 702.732
1198.2542 | 702.4101
1199.2542 | 702.4951
1200.2542 | 702.473
1201.2542 | 702.3391
1202.2542 | 702.5677
1203.2542 | 701.5065
1204.2542 | 703.2907
1205.2542 | 702.7456
1206.2542 | 703.8665
1207.2542 | 706.1176
1208.2542 | 711.1392
1209.2542 | 711.1693
1210.2542 | 711.2654
1211.2542 | 710.8228
1212.2542 | 711.6599
1213.2542 | 712.17
1214.2542 | 714.7436
1215.2542 | 712.8724
1216.2542 | 712.0696
1217.2542 | 711.2726
1218.2542 | 709.9296
1219.2542 | 714.6851
1220.2542 | 717.592
1221.2542 | 718.0198
1222.2542 | 718.309
1223.2542 | 720.8576
1224.2542 | 718.9362
1225.2542 | 717.6058
1226.2542 | 716.6083
1227.2542 | 717.8499
1228.2542 | 718.1538
1229.2542 | 717.8191
1230.2542 | 716.1132
1231.2542 | 713.4615
1232.2542 | 711.4188
1233.2542 | 709.851
1234.2542 | 712.645
1235.2542 | 713.3679
1236.2542 | 714.7165
1237.2542 | 714.0459
1238.2542 | 712.4745
1239.2542 | 710.7358
1240.2542 | 711.6512
1241.2542 | 711.8667
1242.2542 | 712.042
1243.2542 | 711.973
1244.2542 | 711.1806
1245.2542 | 712.9649
1246.2542 | 713.0306
1247.2542 | 712.8051
1248.2542 | 709.4247
1249.2542 | 708.6677
1250.2542 | 709.5126
1251.2542 | 711.3513
1252.2542 | 712.2178
1253.2542 | 713.5818
1254.2542 | 714.6481
1255.2542 | 715.8884
1256.2542 | 717.1429
1257.2542 | 715.7661
1258.2542 | 717.6824
1259.2542 | 718.2679
1260.2542 | 720.0101
1261.2542 | 719.3025
1262.2542 | 717.9796
1263.2542 | 716.4894
1264.2542 | 718.249
1265.2542 | 718.5682
1266.2542 | 716.5164
1267.2542 | 714.085
1268.2542 | 716.8204
1269.2542 | 716.4662
1270.2542 | 716.1317
1271.2542 | 717.5564
1272.2542 | 718.4673
1273.2542 | 716.4919
1274.2542 | 714.6105
1275.2542 | 712.201
1276.2542 | 711.4316
1277.2542 | 711.2499
1278.2542 | 711.6312
1279.2542 | 711.2061
1280.2542 | 713.3418
1281.2542 | 711.9146
1282.2542 | 712.5542
1283.2542 | 713.7401
1284.2542 | 714.0421
1285.2542 | 712.7643
1286.2542 | 712.6883
1287.2542 | 713.5639
1288.2542 | 715.9456
1289.2542 | 718.7539
1290.2542 | 723.6008
1291.2542 | 724.6962
1292.2542 | 721.7838
1293.2542 | 719.3093
1294.2542 | 718.0248
1295.2542 | 715.7938
1296.2542 | 715.2211
1297.2542 | 714.6061
1298.2542 | 714.4248
1299.2542 | 715.0828
1300.2542 | 712.4213
1301.2542 | 711.5999
1302.2542 | 715.6604
1303.2542 | 715.309
1304.2542 | 714.601
1305.2542 | 710.32
1306.2542 | 709.9958
1307.2542 | 708.8213
1308.2542 | 706.8905
1309.2542 | 709.0805
1310.2542 | 707.0399
1311.2542 | 705.0869
1312.2542 | 705.4855
1313.2542 | 708.3304
1314.2542 | 711.7507
1315.2542 | 710.9111
1316.2542 | 710.2304
1317.2542 | 712.5971
1318.2542 | 711.1221
1319.2542 | 712.3138
1320.2542 | 713.3808
1321.2542 | 716.0975
1322.2542 | 714.3296
1323.2542 | 711.9093
1324.2542 | 709.9391
1325.2542 | 709.0439
1326.2542 | 710.3423
1327.2542 | 711.72
1328.2542 | 710.7525
1329.2542 | 717.7519
1330.2542 | 718.2129
1331.2542 | 717.7874
1332.2542 | 713.8789
1333.2542 | 712.2809
1334.2542 | 710.3281
1335.2542 | 709.2338
1336.2542 | 705.8437
1337.2542 | 705.9312
1338.2542 | 704.254
1339.2542 | 702.4631
1340.2542 | 701.3358
1341.2542 | 701.4195
1342.2542 | 704.7886
1343.2542 | 707.6529
1344.2542 | 706.7841
1345.2542 | 707.7554
1346.2542 | 707.9339
1347.2542 | 705.9303
1348.2542 | 706.0448
1349.2542 | 704.3985
1350.2542 | 705.1549
1351.2542 | 704.228
1352.2542 | 704.9611
1353.2542 | 705.9129
1354.2542 | 706.2937
1355.2542 | 705.9181
1356.2542 | 707.5088
1357.2542 | 707.1403
1358.2542 | 708.7003
1359.2542 | 709.2529
1360.2542 | 709.0484
1361.2542 | 712.6397
1362.2542 | 713.6866
1363.2542 | 713.9554
1364.2542 | 715.731
1365.2542 | 717.2178
1366.2542 | 718.6882
1367.2542 | 718.4613
1368.2542 | 717.1128
1369.2542 | 717.1735
1370.2542 | 716.1002
1371.2542 | 714.459
1372.2542 | 713.2577
1373.2542 | 712.3707
1374.2542 | 714.7533
1375.2542 | 714.4583
1376.2542 | 712.713
1377.2542 | 713.002
1378.2542 | 713.7335
1379.2542 | 713.0763
1380.2542 | 715.8794
1381.2542 | 717.6175
1382.2542 | 717.0173
1383.2542 | 717.3574
1384.2542 | 716.6407
1385.2542 | 717.5361
1386.2542 | 716.0963
1387.2542 | 717.2038
1388.2542 | 715.7304
1389.2542 | 716.8937
1390.2542 | 716.9236
1391.2542 | 718.7274
1392.2542 | 715.1877
1393.2542 | 713.1544
1394.2542 | 713.5034
1395.2542 | 712.9126
1396.2542 | 715.4407
1397.2542 | 715.1819
1398.2542 | 714.4712
1399.2542 | 713.4861
1400.2542 | 715.8219
1401.2542 | 714.0065
1402.2542 | 714.2892
1403.2542 | 716.226
1404.2542 | 714.4755
1405.2542 | 714.0532
1406.2542 | 712.1311
1407.2542 | 715.5843
1408.2542 | 717.0018
1409.2542 | 716.1641
1410.2542 | 716.0115
1411.2542 | 715.2984
1412.2542 | 714.5966
1413.2542 | 713.6438
1414.2542 | 713.8429
1415.2542 | 715.4666
1416.2542 | 713.6001
1417.2542 | 712.1627
1418.2542 | 714.3445
1419.2542 | 718.6789
1420.2542 | 718.1661
1421.2542 | 717.5754
1422.2542 | 716.7875
1423.2542 | 718.0617
1424.2542 | 719.1816
1425.2542 | 717.6055
1426.2542 | 715.788
1427.2542 | 713.8666
1428.2542 | 712.2679
1429.2542 | 712.3924
1430.2542 | 711.6584
1431.2542 | 709.5615
1432.2542 | 709.136
1433.2542 | 709.4329
1434.2542 | 708.4454
1435.2542 | 708.1364
1436.2542 | 706.7293
1437.2542 | 707.7014
1438.2542 | 709.1957
1439.2542 | 708.3676
1440.2542 | 707.3036
1441.2542 | 707.8183
1442.2542 | 708.1586
1443.2542 | 708.3856
1444.2542 | 709.3218
1445.2542 | 711.2452
1446.2542 | 710.7844
1447.2542 | 709.4741
1448.2542 | 707.2055
1449.2542 | 706.4762
1450.2542 | 704.7882
1451.2542 | 705.2804
1452.2542 | 705.5184
1453.2542 | 706.39
1454.2542 | 706.2595
1455.2542 | 707.0427
1456.2698 | 708.2742
1457.2542 | 711.0953
1458.2542 | 708.3391
1459.2542 | 709.711
1460.2542 | 708.9736
1461.2542 | 708.705
1462.2542 | 707.6713
1463.2542 | 707.1434
1464.2542 | 704.2732
1465.2542 | 704.1095
1466.2542 | 705.3156
1467.2542 | 703.4899
1468.2542 | 702.7786
1469.2542 | 702.5895
1470.2542 | 704.3088
1471.2542 | 704.424
1472.2542 | 704.1004
1473.2542 | 710.8696
1474.2542 | 710.3105
1475.2542 | 711.0536
1476.2542 | 710.0047
1477.2542 | 708.314
1478.2542 | 707.1213
1479.2542 | 710.189
1480.2542 | 705.936
1481.2542 | 705.2846
1482.2542 | 707.0421
1483.2542 | 705.7817
1484.2542 | 705.5608
1485.2542 | 709.2673
1486.2542 | 709.2148
1487.2542 | 707.4631
1488.2542 | 704.6972
1489.2542 | 702.7816
1490.2542 | 708.5341
1491.2542 | 709.2817
1492.2542 | 709.905
1493.2542 | 707.1605
1494.2542 | 709.2068
1495.2542 | 708.7219
1496.2542 | 706.1106
1497.2542 | 706.7624
1498.2542 | 704.4623
1499.2542 | 702.5573
1500.2542 | 701.8398
1501.2542 | 700.35
1502.2542 | 702.5827
1503.2542 | 705.4132
1504.2542 | 709.4734
1505.2542 | 712.5401
1506.2542 | 711.2532
1507.2542 | 709.9403
1508.2542 | 709.8457
1509.2542 | 708.1373
1510.2542 | 708.8712
1511.2542 | 711.8001
1512.2542 | 712.2552
1513.2542 | 716.2049
1514.2542 | 714.2568
1515.2542 | 713.6332
1516.2542 | 713.0619
1517.2542 | 713.7095
1518.2542 | 713.2589
1519.2542 | 712.2293
1520.2542 | 711.0123
1521.2542 | 710.8447
1522.2542 | 713.2791
1523.2542 | 713.1126
1524.2542 | 712.2324
1525.2542 | 710.4451
1526.2542 | 710.073
1527.2542 | 708.1903
1528.2542 | 711.8435
1529.2542 | 711.8692
1530.2542 | 711.9749
1531.2542 | 711.9029
1532.2542 | 712.9333
1533.2542 | 713.2698
1534.2542 | 716.066
1535.2542 | 715.2811
1536.2542 | 716.8885
1537.2542 | 715.7681
1538.2542 | 715.5998
1539.2542 | 714.6198
1540.2542 | 714.6898
1541.2542 | 714.142
1542.2542 | 714.8441
1543.2542 | 713.8751
1544.2542 | 714.4071
1545.2542 | 712.7791
1546.2542 | 720.8576
1547.2542 | 720.7857
1548.2542 | 721.9542
1549.2542 | 725.3846
1550.2542 | 722.7278
1551.2542 | 720.5368
1552.2542 | 724.6899
1553.2542 | 722.2755
1554.2542 | 719.7193
1555.2542 | 718.4023
1556.2542 | 717.5028
1557.2542 | 713.852
1558.2542 | 713.627
1559.2542 | 717.8667
1560.2542 | 717.4375
1561.2542 | 722.8314
1562.2542 | 724.2623
1563.2542 | 723.6402
1564.2542 | 724.7616
1565.2542 | 723.0229
1566.2542 | 723.8383
1567.2542 | 723.6586
1568.2542 | 724.258
1569.2542 | 722.6909
1570.2542 | 721.5008
1571.2542 | 719.4211
1572.2542 | 720.6788
1573.2542 | 718.5375
1574.2542 | 715.799
1575.2542 | 713.6784
1576.2542 | 715.1295
1577.2542 | 716.4924
1578.2542 | 716.2425
1579.2542 | 716.4084
1580.2542 | 716.922
1581.2542 | 716.9854
1582.2542 | 716.8335
1583.2542 | 715.3652
1584.2542 | 715.2685
1585.2542 | 714.8146
1586.2542 | 715.4548
1587.2542 | 719.9222
1588.2542 | 716.6532
1589.2542 | 716.1825
1590.2542 | 716.2712
1591.2542 | 715.5432
1592.2542 | 715.9728
1593.2542 | 716.6609
1594.2542 | 717.3423
1595.2542 | 718.3834
1596.2542 | 717.9586
1597.2542 | 716.8471
1598.2542 | 716.9115
1599.2542 | 717.3582
1600.2542 | 716.4876
1601.2542 | 716.8144
1602.2542 | 715.2288
1603.2542 | 718.099
1604.2542 | 717.8205
1605.2542 | 720.0181
1606.2542 | 719.7894
1607.2542 | 719.3783
1608.2542 | 718.995
1609.2542 | 717.7947
1610.2542 | 717.6464
1611.2542 | 717.3182
1612.2542 | 715.7544
1613.2542 | 714.2046
1614.2542 | 714.4766
1615.2542 | 713.3531
1616.2542 | 717.2118
1617.2542 | 716.8423
1618.2542 | 719.9594
1619.2542 | 718.868
1620.2542 | 719.6356
1621.2542 | 721.256
1622.2542 | 722.118
1623.2542 | 720.7114
1624.2542 | 720.1816
1625.2542 | 720.5933
1626.2542 | 721.0386
1627.2542 | 720.3093
1628.2542 | 720.1924
1629.2542 | 720.7128
1630.2542 | 719.724
1631.2542 | 720.5928
1632.2542 | 719.898
1633.2542 | 718.7368
1634.2542 | 715.554
1635.2542 | 713.85
1636.2542 | 713.7635
1637.2542 | 715.3781
1638.2542 | 714.3914
1639.2542 | 713.5582
1640.2542 | 714.0268
1641.2542 | 716.1575
1642.2542 | 716.61
1643.2542 | 715.9232
1644.2542 | 715.8333
1645.2542 | 713.917
1646.2542 | 713.1618
1647.2542 | 713.8053
1648.2542 | 713.4368
1649.2542 | 711.4346
1650.2542 | 709.8124
1651.2542 | 711.5021
1652.2542 | 711.2666
1653.2542 | 711.7192
1654.2542 | 712.655
1655.2542 | 711.3687
1656.2542 | 710.4963
1657.2698 | 710.4069
1658.2542 | 709.8574
1659.2542 | 709.6546
1660.2542 | 709.8935
1661.2542 | 709.3904
1662.2542 | 708.7788
1663.2542 | 707.8331
1664.2542 | 708.8763
1665.2542 | 708.4782
1666.2542 | 706.1049
1667.2542 | 705.1099
1668.2542 | 705.1887
1669.2542 | 702.4449
1670.2542 | 701.9604
1671.2542 | 701.6942
1672.2542 | 702.1821
1673.2542 | 702.8848
1674.2542 | 705.8518
1675.2542 | 706.7154
1676.2542 | 707.5409
1677.2542 | 709.0693
1678.2542 | 708.6874
1679.2542 | 710.4455
1680.2542 | 710.4416
1681.2542 | 710.2467
1682.2542 | 711.2389
1683.2542 | 710.7934
1684.2542 | 710.3895
1685.2542 | 709.6132
1686.2542 | 710.6965
1687.2542 | 708.334
1688.2542 | 710.3597
1689.2542 | 713.5669
1690.2542 | 714.4342
1691.2542 | 713.5089
1692.2542 | 711.7526
1693.2542 | 709.6052
1694.2542 | 707.7981
1695.2542 | 707.646
1696.2542 | 707.7314
1697.2542 | 706.4389
1698.2542 | 705.8382
1699.2542 | 708.2273
1700.2542 | 708.6384
1701.2542 | 708.3228
1702.2542 | 710.2667
1703.2542 | 709.817
1704.2542 | 711.0902
1705.2542 | 710.9911
1706.2542 | 713.2319
1707.2542 | 713.4181
1708.2542 | 713.5115
1709.2542 | 712.9626
1710.2542 | 711.9769
1711.2542 | 711.3319
1712.2542 | 708.9552
1713.2542 | 708.5871
1714.2542 | 706.6496
1715.2542 | 706.7395
1716.2542 | 707.0486
1717.2542 | 705.9004
1718.2542 | 704.0901
1719.2542 | 704.464
1720.2542 | 702.2356
1721.2542 | 700.7471
1722.2542 | 700.4087
1723.2542 | 702.9795
1724.2542 | 701.8885
1725.2542 | 701.3451
1726.2542 | 701.515
1727.2542 | 701.1487
1728.2542 | 701.3099
1729.2542 | 699.9163
1730.2542 | 699.1544
1731.2542 | 698.9751
1732.2542 | 698.6155
1733.2542 | 697.373
1734.2542 | 694.6642
1735.2542 | 695.4887
1736.2542 | 696.3971
1737.2542 | 696.1989
1738.2542 | 697.2737
1739.2542 | 697.1944
1740.2542 | 698.7028
1741.2542 | 698.6248
1742.2542 | 698.9811
1743.2542 | 696.9406
1744.2542 | 694.4264
1745.2542 | 694.6148
1746.2542 | 693.4461
1747.2542 | 692.3079
1748.2542 | 690.1062
1749.2542 | 690.8539
1750.2542 | 687.6776
1751.2542 | 688.4049
1752.2542 | 689.233
1753.2542 | 688.0943
1754.2542 | 688.3299
1755.2542 | 688.8585
1756.2542 | 687.8261
1757.2542 | 686.4952
1758.2542 | 686.2358
1759.2542 | 686.2361
1760.2542 | 686.3269
1761.2542 | 684.934
1762.2542 | 684.1104
1763.2542 | 684.7418
1764.2542 | 685.3979
1765.2542 | 686.0225
1766.2542 | 686.1405
1767.2542 | 685.5226
1768.2542 | 686.9687
1769.2542 | 686.3852
1770.2542 | 684.5097
1771.2542 | 686.9452
1772.2542 | 687.2422
1773.2542 | 686.9612
1774.2542 | 685.2514
1775.2542 | 686.6529
1776.2542 | 687.9759
1777.2542 | 687.5327
1778.2542 | 687.0198
1779.2542 | 687.2062
1780.2542 | 687.5242
1781.2542 | 688.3793
1782.2542 | 688.3693
1783.2542 | 688.9316
1784.2542 | 687.5878
1785.2542 | 687.2382
1786.2542 | 688.5559
1787.2542 | 688.7819
1788.2542 | 689.5743
1789.2542 | 689.8858
1790.2542 | 690.1986
1791.2542 | 690.0886
1792.2542 | 689.4827
1793.2542 | 689.8346
1794.2542 | 689.5452
1795.2542 | 689.3986
1796.2542 | 688.4964
1797.2542 | 688.5719
1798.2542 | 689.4427
1799.2542 | 689.7516
1800.2542 | 689.6455
1801.2542 | 690.8129
1802.2542 | 690.7917
1803.2542 | 691.7459
1804.2542 | 692.7582
1805.2542 | 694.3463
1806.2542 | 695.0453
1807.2542 | 695.4075
1808.2542 | 696.0516
1809.2542 | 695.5813
1810.2542 | 697.0859
1811.2542 | 697.8905
1812.2542 | 699.462
1813.2542 | 699.2807
1814.2542 | 698.9234
1815.2542 | 698.4093
1816.2542 | 698.7011
1817.2542 | 699.6501
1818.2542 | 700.0192
1819.2542 | 700.0329
1820.2542 | 698.9001
1821.2542 | 700.8419
1822.2542 | 699.3837
1823.2542 | 697.473
1824.2542 | 697.3471
1825.2542 | 698.1464
1826.2542 | 697.5509
1827.2542 | 697.8692
1828.2542 | 698.5196
1829.2542 | 701.3774
1830.2542 | 702.978
1831.2542 | 704.4401
1832.2542 | 703.9109
1833.2542 | 706.0776
1834.2542 | 705.8864
1835.2542 | 703.9802
1836.2542 | 703.353
1837.2542 | 703.8048
1838.2542 | 704.01
1839.2542 | 703.4541
1840.2542 | 701.2299
1841.2542 | 700.9833
1842.2542 | 700.2085
1843.2542 | 699.4575
1844.2542 | 701.1932
1845.2542 | 701.9453
1846.2542 | 700.7863
1847.2542 | 700.5464
1848.2542 | 702.1956
1849.2542 | 701.4399
1850.2542 | 700.3899
1851.2542 | 699.7887
1852.2542 | 700.4874
1853.2542 | 698.7852
1854.2542 | 699.3097
1855.2542 | 700.9868
1856.2542 | 700.4136
1857.2542 | 701.0149
1858.2542 | 702.6969
1859.2542 | 706.4351
1860.2542 | 708.2839
1861.2542 | 709.2395
1862.2542 | 708.6918
1863.2542 | 707.9916
1864.2542 | 708.3441
1865.2542 | 707.2809
1866.2542 | 705.5245
1867.2542 | 705.479
1868.2542 | 704.6527
1869.2542 | 701.1431
1870.2542 | 701.5733
1871.2542 | 700.443
1872.2542 | 699.3681
1873.2542 | 696.6931
1874.2542 | 696.1956
1875.2542 | 695.8053
1876.2542 | 694.7689
1877.2542 | 694.0118
1878.2542 | 693.1646
1879.2542 | 693.2318
1880.2542 | 693.3143
1881.2542 | 693.5093
1882.2542 | 691.5644
1883.2542 | 690.7428
1884.2542 | 689.6483
1885.2542 | 689.0527
1886.2542 | 686.9198
1887.2542 | 682.8586
1888.2542 | 681.6982
1889.2542 | 683.7995
1890.2542 | 683.7707
1891.2542 | 682.1601
1892.2542 | 682.9985
1893.2542 | 681.5189
1894.2542 | 683.4208
1895.2542 | 684.4014
1896.2542 | 687.1337
1897.2542 | 686.6867
1898.2542 | 684.3379
1899.2542 | 685.1114
1900.2542 | 684.7261
1901.2542 | 684.8968
1902.2542 | 684.5868
1903.2542 | 684.1872
1904.2542 | 683.5214
1905.2542 | 683.7737
1906.2542 | 684.063
1907.2542 | 685.8787
1908.2542 | 687.5124
1909.2542 | 687.9676
1910.2542 | 687.5858
1911.2542 | 690.3482
1912.2542 | 693.2627
1913.2542 | 694.7445
1914.2542 | 694.0199
1915.2542 | 695.3431
1916.2542 | 695.7385
1917.2542 | 697.445
1918.2542 | 697.9628
1919.2542 | 700.1346
1920.2542 | 701.0817
1921.2542 | 701.4772
1922.2542 | 701.0636
1923.2542 | 700.4723
1924.2542 | 701.321
1925.2542 | 708.0653
1926.2542 | 707.8522
1927.2542 | 706.1159
1928.2542 | 705.3132
1929.2542 | 704.3154
1930.2542 | 705.5556
1931.2542 | 704.8964
1932.2542 | 707.6108
1933.2542 | 709.4563
1934.2542 | 711.5023
1935.2542 | 709.5341
1936.2542 | 707.4504
1937.2542 | 707.3374
1938.2542 | 707.7397
1939.2542 | 707.7681
1940.2542 | 708.3944
1941.2542 | 707.7313
1942.2542 | 707.1672
1943.2542 | 705.0827
1944.2542 | 704.762
1945.2542 | 703.8076
1946.2542 | 705.8331
1947.2542 | 705.8899
1948.2542 | 704.6327
1949.2542 | 704.44
1950.2542 | 705.8899
1951.2542 | 704.1387
1952.2542 | 702.8369
1953.2542 | 702.3088
1954.2542 | 700.1212
1955.2542 | 699.3846
1956.2542 | 699.684
1957.2542 | 698.5424
1958.2542 | 697.414
1959.2542 | 696.3146
1960.2542 | 694.8549
1961.2542 | 693.8495
1962.2542 | 695.9214
1963.2542 | 697.7088
1964.2542 | 694.0275
1965.2542 | 694.331
1966.2542 | 693.7417
1967.2542 | 693.0464
1968.2542 | 693.8698
1969.2542 | 692.5775
1970.2542 | 690.5512
1971.2542 | 693.2972
1972.2542 | 692.9098
1973.2542 | 694.5772
1974.2542 | 696.3133
1975.2542 | 694.0789
1976.2542 | 694.9757
1977.2542 | 697.1767
1978.2542 | 696.6474
1979.2542 | 693.7826
1980.2542 | 693.6471
1981.2542 | 694.4792
1982.2542 | 692.4919
1983.2542 | 691.2143
1984.2542 | 692.175
1985.2542 | 690.827
1986.2542 | 688.8118
1987.2542 | 687.401
1988.2542 | 688.6931
1989.2698 | 687.3859
1990.2542 | 685.8386
1991.2542 | 683.9324
1992.2542 | 681.994
1993.2542 | 682.1799
1994.2542 | 683.74
1995.2542 | 685.5333
1996.2542 | 685.1763
1997.2542 | 684.1833
1998.2542 | 683.0876
1999.2542 | 681.5774
2000.2542 | 680.4883
2001.2542 | 680.2689
2002.2542 | 680.6297
2003.2542 | 680.5864
2004.2542 | 681.1153
2005.2542 | 681
2006.2542 | 681.604
2007.2542 | 681.1714
2008.2542 | 678.6931
2009.2542 | 680.8566
2010.2542 | 681.877
2011.2542 | 681.9102
2012.2542 | 682.8917
2013.2542 | 683.6419
2014.2542 | 684.653
2015.2542 | 685.5333
2016.2542 | 685.5124
2017.2542 | 688.2736
2018.2542 | 690.5413
2019.2542 | 689.7002
2020.2542 | 690.1242
2021.2542 | 690.2676
2022.2542 | 692.6683
2023.2542 | 694.4645
2024.2542 | 694.5814
2025.2542 | 693.5783
2026.2542 | 691.9071
2027.2542 | 691.7189
2028.2542 | 688.5201
2029.2542 | 687.0813
2030.2542 | 685.2733
2031.2542 | 684.8416
2032.2542 | 683.6383
2033.2542 | 682.5817
2034.2542 | 679.8137
2035.2542 | 679.5404
2036.2542 | 679.8209
2037.2542 | 678.1411
2038.2542 | 677.8528
2039.2542 | 677.2146
2040.2542 | 676.6768
2041.2542 | 675.9491
2042.2542 | 675.883
2043.2542 | 675.9785
2044.2542 | 677.0286
2045.2542 | 675.906
2046.2542 | 673.4273
2047.2542 | 672.8746
2048.2542 | 673.8976
2049.2542 | 673.4866
2050.2542 | 674.97
2051.2542 | 675.9161
2052.2542 | 676.7498
2053.2542 | 675.7884
2054.2542 | 674.1584
2055.2542 | 673.9598
2056.2542 | 673.7627
2057.2542 | 673.6629
2058.2542 | 669.1987
2059.2542 | 672.1801
2060.2542 | 671.162
2061.2542 | 670.2513
2062.2542 | 670.6971
2063.2542 | 671.6663
2064.2542 | 672.5561
2065.2542 | 672.2746
2066.2542 | 672.58
2067.2542 | 671.7706
2068.2542 | 671.8634
2069.2542 | 673.1586
2070.2542 | 673.0347
2071.2542 | 672.5303
2072.2542 | 673.7824
2073.2542 | 674.8866
2074.2542 | 675.0671
2075.2542 | 675.6443
2076.2542 | 676.2759
2077.2542 | 676.3108
2078.2542 | 675.641
2079.2542 | 676.6463
2080.2542 | 675.153
2081.2542 | 674.6716
2082.2542 | 674.751
2083.2542 | 674.855
2084.2542 | 675.2084
2085.2542 | 674.2595
2086.2542 | 671.9428
2087.2542 | 671.7768
2088.2542 | 671.1319
2089.2542 | 673.9166
2090.2542 | 673.664
2091.2542 | 674.8369
2092.2542 | 676.8638
2093.2542 | 675.4338
2094.2542 | 678.1162
2095.2542 | 680.7325
2096.2542 | 678.995
2097.2542 | 680.4529
2098.2542 | 682.1244
2099.2542 | 685.1393
2100.2542 | 685.1401
2101.2542 | 683.6756
2102.2542 | 683.6834
2103.2542 | 683.2702
2104.2542 | 682.746
2105.2542 | 683.0232
2106.2542 | 683.3337
2107.2542 | 684.2636
2108.2542 | 685.0738
2109.2542 | 685.6542
2110.2542 | 686.4124
2111.2542 | 685.8953
2112.2542 | 685.8153
2113.2542 | 684.5356
2114.2542 | 682.1364
2115.2542 | 683.4305
2116.2542 | 682.6473
2117.2542 | 681.476
2118.2542 | 683.0447
2119.2542 | 683.1991
2120.2542 | 679.9704
2121.2542 | 683.8471
2122.2542 | 687.1852
2123.2542 | 689.2141
2124.2542 | 689.9969
2125.2542 | 690.3568
2126.2542 | 690.7086
2127.2542 | 689.3943
2128.2542 | 689.1387
2129.2542 | 689.6837
2130.2542 | 688.7036
2131.2542 | 686.8937
2132.2542 | 685.7936
2133.2542 | 685.9664
2134.2542 | 686.0249
2135.2542 | 684.6566
2136.2542 | 683.4697
2137.2542 | 682.2079
2138.2542 | 682.7389
2139.2542 | 682.7605
2140.2542 | 682.9546
2141.2542 | 683.6597
2142.2542 | 683.1788
2143.2542 | 682.0967
2144.2542 | 680.9981
2145.2542 | 681.3105
2146.2542 | 681.4224
2147.2542 | 680.1614
2148.2542 | 680.8174
2149.2542 | 681.9134
2150.2542 | 680.9779
2151.2542 | 680.1533
2152.2542 | 679.0735
2153.2542 | 678.8949
2154.2542 | 678.465
2155.2542 | 678.8624
2156.2542 | 679.2301
2157.2542 | 677.5569
2158.2542 | 676.1765
2159.2542 | 675.0567
2160.2542 | 675.7886
2161.2542 | 676.3764
2162.2542 | 677.0071
2163.2542 | 677.4959
2164.2542 | 676.4397
2165.2542 | 676.1602
2166.2542 | 676.8983
2167.2542 | 677.4333
2168.2542 | 676.9755
2169.2542 | 675.0048
2170.2542 | 675.1042
2171.2542 | 675.0051
2172.2542 | 674.7872
2173.2542 | 675.7243
2174.2542 | 677.3174
2175.2542 | 679.6258
2176.2542 | 679.0412
2177.2542 | 677.08
2178.2542 | 676.7423
2179.2542 | 677.7922
2180.2542 | 678.4997
2181.2542 | 678.1841
2182.2542 | 679.4489
2183.2542 | 679.3037
2184.2542 | 680.1097
2185.2542 | 680.8127
2186.2542 | 680.5658
2187.2542 | 680.3167
2188.2542 | 679.6813
2189.2542 | 678.5515
2190.2542 | 679.3731
2191.2542 | 678.8644
2192.2542 | 677.2566
2193.2542 | 677.0607
2194.2542 | 677.802
2195.2542 | 677.6777
2196.2542 | 675.6688
2197.2542 | 674.8261
2198.2542 | 673.7701
2199.2542 | 673.4923
2200.2542 | 674.9545
2201.2542 | 676.8083
2202.2542 | 677.2295
2203.2542 | 677.6538
2204.2542 | 676.7875
2205.2542 | 678.8284
2206.2542 | 679.5061
2207.2542 | 680.4958
2208.2542 | 681.136
2209.2542 | 679.7966
2210.2542 | 681.4622
2211.2542 | 680.8306
2212.2542 | 679.6096
2213.2542 | 678.3677
2214.2542 | 680.5192
2215.2542 | 677.985
2216.2542 | 673.7539
2217.2542 | 675.6716
2218.2542 | 681.2262
2219.2542 | 682.7355
2220.2542 | 678.0667
2221.2542 | 679.2896
2222.2542 | 678.175
2223.2542 | 680.5597
2224.2542 | 681.2024
2225.2542 | 682.6126
2226.2542 | 682.0778
2227.2542 | 681.4468
2228.2542 | 679.9413
2229.2542 | 680.1663
2230.2542 | 681.908
2231.2542 | 681.3489
2232.2542 | 682.3992
2233.2542 | 683.7243
2234.2542 | 683.8952
2235.2542 | 683.4753
2236.2542 | 682.878
2237.2542 | 682.2294
2238.2542 | 682.8895
2239.2542 | 681.7487
2240.2542 | 681.1727
2241.2542 | 679.3617
2242.2542 | 679.4041
2243.2542 | 679.7401
2244.2542 | 679.7399
2245.2542 | 678.5717
2246.2542 | 677.5713
2247.2542 | 678.0605
2248.2542 | 677.9377
2249.2542 | 677.4943
2250.2542 | 676.7363
2251.2542 | 675.7626
2252.2542 | 676.5906
2253.2542 | 678.2524
2254.2542 | 679.6209
2255.2542 | 677.178
2256.2542 | 678.3721
2257.2542 | 678.3151
2258.2542 | 678.9057
2259.2542 | 678.1956
2260.2542 | 678.4248
2261.2542 | 679.3041
2262.2542 | 679.2392
2263.2542 | 674.7021
2264.2542 | 673.4385
2265.2542 | 673.0666
2266.2542 | 671.9064
2267.2542 | 671.1482
2268.2542 | 672.0267
2269.2542 | 673.0133
2270.2542 | 669.9316
2271.2542 | 671.0217
2272.2542 | 670.6624
2273.2542 | 670.4793
2274.2542 | 671.9953
2275.2542 | 674.1411
2276.2542 | 674.4038
2277.2542 | 673.8048
2278.2542 | 671.3266
2279.2542 | 670.6852
2280.2542 | 670.6551
2281.2542 | 671.4916
2282.2542 | 671.5411
2283.2542 | 671.7862
2284.2542 | 671.8462
2285.2542 | 670.6848
2286.2542 | 671.8766
2287.2542 | 672.8385
2288.2542 | 671.5666
2289.2542 | 670.4071
2290.2542 | 669.2732
2291.2542 | 671.0531
2292.2542 | 671.3138
2293.2542 | 668.81
2294.2542 | 667.6341
2295.2542 | 670.3828
2296.2542 | 674.256
2297.2542 | 675.9564
2298.2542 | 679.8128
2299.2542 | 682.5807
2300.2542 | 684.5831
2301.2542 | 684.1335
2302.2542 | 687.7631
2303.2542 | 688.444
2304.2542 | 686.5933
2305.2542 | 682.3738
2306.2542 | 683.1136
2307.2542 | 683.4352
2308.2542 | 682.922
2309.2542 | 680.223
2310.2542 | 678.2986
2311.2542 | 678.5248
2312.2542 | 677.4784
2313.2542 | 677.9293
2314.2542 | 677.2239
2315.2542 | 677.9095
2316.2542 | 675.9893
2317.2542 | 676.0119
2318.2542 | 674.7009
2319.2542 | 672.7436
2320.2542 | 672.8828
2321.2542 | 671.1587
2322.2542 | 672.4984
2323.2542 | 671.7038
2324.2542 | 671.3017
2325.2542 | 672.4042
2326.2542 | 671.9377
2327.2542 | 673.3698
2328.2542 | 674.6425
2329.2542 | 677.7285
2330.2542 | 678.0387
2331.2542 | 679.2305
2332.2542 | 678.76
2333.2542 | 678.0183
2334.2542 | 678.639
2335.2542 | 680.4242
2336.2542 | 683.9707
2337.2542 | 685.2582
2338.2542 | 684.5488
2339.2542 | 683.5205
2340.2542 | 682.5441
2341.2542 | 679.4727
2342.2542 | 676.3855
2343.2542 | 675.5219
2344.2542 | 674.4051
2345.2542 | 674.8313
2346.2542 | 671.2452
2347.2542 | 674.301
2348.2542 | 675.0033
2349.2542 | 675.8429
2350.2542 | 676.838
2351.2542 | 679.0368
2352.2542 | 679.9548
2353.2542 | 677.9795
2354.2542 | 675.9513
2355.2542 | 675.743
2356.2542 | 674.3944
2357.2542 | 670.8246
2358.2542 | 669.0176
2359.2542 | 668.4138
2360.2542 | 667.5074
2361.2542 | 667.7368
2362.2542 | 667.8863
2363.2542 | 667.7502
2364.2542 | 668.0482
2365.2542 | 667.344
2366.2542 | 666.5864
2367.2542 | 668.1305
2368.2542 | 671.931
2369.2542 | 673.3282
2370.2542 | 674.1399
2371.2542 | 671.8289
2372.2542 | 670.8279
2373.2542 | 667.2383
2374.2542 | 663.8804
2375.2542 | 665.3691
2376.2542 | 663.162
2377.2542 | 663.0288
2378.2542 | 663.5169
2379.2542 | 664.0188
2380.2542 | 664.0607
2381.2542 | 664.5608
2382.2542 | 664.6937
2383.2542 | 667.119
2384.2542 | 667.4411
2385.2542 | 665.8941
2386.2542 | 667.644
2387.2542 | 667.9642
2388.2542 | 667.6601
2389.2542 | 669.1324
2390.2542 | 669.0872
2391.2542 | 669.8836
2392.2542 | 672.5126
2393.2542 | 674.0981
2394.2542 | 674.8268
2395.2542 | 674.5112
2396.2542 | 674.9708
2397.2542 | 674.8305
2398.2542 | 674.6002
2399.2542 | 675.8973
2400.2542 | 671.1903
2401.2542 | 669.6345
2402.2542 | 669.6517
2403.2542 | 670.4475
2404.2542 | 672.2477
2405.2542 | 673.4647
2406.2542 | 676.2036
2407.2542 | 678.5973
2408.2542 | 678.8993
2409.2542 | 677.3425
2410.2542 | 678.4232
2411.2542 | 679.5722
2412.2542 | 680.2094
2413.2542 | 680.8413
2414.2542 | 680.6694
2415.2542 | 682.162
2416.2542 | 681.2982
2417.2542 | 679.9407
2418.2542 | 680.7213
2419.2542 | 679.7615
2420.2542 | 680.7908
2421.2542 | 681.3423
2422.2542 | 680.7784
2423.2542 | 680.1652
2424.2542 | 679.4685
2425.2542 | 683.2088
2426.2542 | 686.0628
2427.2542 | 686.8441
2428.2542 | 687.3183
2429.2542 | 687.782
2430.2542 | 686.6588
2431.2542 | 684.0875
2432.2542 | 683.5932
2433.2542 | 684.438
2434.2542 | 684.6413
2435.2542 | 684.5686
2436.2542 | 684.8542
2437.2542 | 684.5406
2438.2542 | 683.8153
2439.2542 | 682.8814
2440.2542 | 681.6214
2441.2542 | 681.0413
2442.2542 | 682.2282
2443.2542 | 683.6216
2444.2542 | 683.0879
2445.2542 | 681.6967
2446.2542 | 680.4015
2447.2542 | 677.7598
2448.2542 | 674.9898
2449.2542 | 674.0411
2450.2542 | 672.4707
2451.2542 | 672.2239
2452.2542 | 672.8023
2453.2542 | 672.9046
2454.2542 | 671.1674
2455.2542 | 669.4895
2456.2542 | 670.2829
2457.2542 | 668.8666
2458.2542 | 667.7266
2459.2542 | 669.7027
2460.2542 | 667.8573
2461.2542 | 667.4309
2462.2542 | 667.1703
2463.2542 | 667.9413
2464.2542 | 668.5377
2465.2542 | 666.1467
2466.2542 | 668.0117
2467.2542 | 668.6028
2468.2542 | 667.6827
2469.2542 | 668.7536
2470.2542 | 668.8242
2471.2542 | 668.5577
2472.2542 | 668.5595
2473.2542 | 669.8479
2474.2542 | 667.2019
2475.2542 | 669.3035
2476.2542 | 664.8966
2477.2542 | 662.6969
2478.2542 | 662.8868
2479.2542 | 662.0558
2480.2542 | 662.6351
2481.2542 | 662.5627
2482.2542 | 664.3024
2483.2542 | 664.8598
2484.2542 | 667.0212
2485.2542 | 666.5298
2486.2542 | 664.7881
2487.2542 | 665.0971
2488.2542 | 664.5705
2489.2542 | 665.2853
2490.2542 | 666.6351
2491.2542 | 663.5453
2492.2542 | 662.7615
2493.2542 | 663.7532
2494.2542 | 663.7863
2495.2542 | 666.1035
2496.2542 | 666.1095
2497.2542 | 666.4006
2498.2542 | 665.5965
2499.2542 | 667.1789
2500.2542 | 667.84
2501.2542 | 668.1647
2502.2542 | 666.85
2503.2542 | 665.5017
2504.2542 | 663.0291
2505.2542 | 662.346
2506.2542 | 667.8933
2507.2542 | 675.6482
2508.2542 | 677.892
2509.2542 | 679.4306
2510.2542 | 677.9501
2511.2542 | 676.6152
2512.2542 | 674.614
2513.2542 | 673.731
2514.2542 | 671.9476
2515.2542 | 673.058
2516.2542 | 675.4482
2517.2542 | 674.5932
2518.2542 | 674.3236
2519.2542 | 672.7141
2520.2542 | 671.1311
2521.2542 | 671.5187
2522.2542 | 670.8849
2523.2542 | 671.959
2524.2542 | 671.0046
2525.2542 | 671.9169
2526.2542 | 671.4625
2527.2542 | 670.7714
2528.2542 | 672.606
2529.2542 | 672.6809
2530.2542 | 673.1044
2531.2542 | 673.0353
2532.2542 | 676.2049
2533.2542 | 678.6857
2534.2542 | 679.8139
2535.2542 | 678.6102
2536.2542 | 678.3956
2537.2542 | 678.3118
2538.2542 | 679.4081
2539.2542 | 677.8254
2540.2542 | 680.3241
2541.2542 | 683.0577
2542.2542 | 681.0798
2543.2542 | 682.3089
2544.2542 | 684.4565
2545.2542 | 684.7653
2546.2542 | 687.8421
2547.2542 | 689.0183
2548.2542 | 688.9954
2549.2542 | 688.7154
2550.2542 | 689.7589
2551.2542 | 683.7652
2552.2542 | 681.6102
2553.2542 | 685.5565
2554.2542 | 687.4421
2555.2542 | 687.2146
2556.2542 | 685.0514
2557.2542 | 684.1089
2558.2542 | 681.2041
2559.2542 | 678.3492
2560.2542 | 678.2673
2561.2542 | 677.2412
2562.2542 | 677.9187
2563.2542 | 677.7917
2564.2542 | 677.2279
2565.2542 | 675.0161
2566.2542 | 677.9241
2567.2542 | 680.4358
2568.2542 | 681.6541
2569.2542 | 682.1966
2570.2542 | 684.5357
2571.2542 | 684.5849
2572.2542 | 683.954
2573.2542 | 685.1108
2574.2542 | 682.7072
2575.2542 | 683.0042
2576.2542 | 679.1012
2577.2542 | 675.0807
2578.2542 | 674.1639
2579.2542 | 674.5468
2580.2542 | 675.44
2581.2542 | 676.1064
2582.2542 | 674.5336
2583.2542 | 674.7544
2584.2542 | 675.8617
2585.2542 | 677.4445
2586.2542 | 674.7377
2587.2542 | 674.5731
2588.2542 | 672.7951
2589.2542 | 672.7489
2590.2542 | 675.859
2591.2542 | 676.2049
2592.2542 | 674.4088
2593.2542 | 670.6321
2594.2542 | 671.4581
2595.2542 | 672.6065
2596.2542 | 673.3902
2597.2542 | 673.205
2598.2542 | 674.6323
2599.2542 | 674.754
2600.2542 | 672.8081
2601.2542 | 670.4087
2602.2542 | 670.0591
2603.2542 | 669.1504
2604.2542 | 668.4469
2605.2542 | 668.7691
2606.2542 | 667.4394
2607.2542 | 668.1336
2608.2542 | 668.3169
2609.2542 | 669.0162
2610.2542 | 668.6666
2611.2542 | 669.6074
2612.2542 | 668.1337
2613.2542 | 670.2625
2614.2542 | 673.71
2615.2542 | 672.3483
2616.2542 | 670.974
2617.2542 | 674.6325
2618.2542 | 677.2351
2619.2542 | 677.7432
2620.2542 | 678.4408
2621.2542 | 678.68
2622.2542 | 678.5488
2623.2542 | 678.0502
2624.2542 | 678.3918
2625.2542 | 678.4871
2626.2542 | 681.426
2627.2542 | 679.3292
2628.2542 | 683.3858
2629.2542 | 683.9653
2630.2542 | 682.4004
2631.2542 | 683.2178
2632.2542 | 683.6088
2633.2542 | 684.4385
2634.2542 | 685.3166
2635.2542 | 685.0332
2636.2542 | 685.3153
2637.2542 | 682.905
2638.2542 | 682.3994
2639.2542 | 684.6909
2640.2542 | 682.4663
2641.2542 | 681.0794
2642.2542 | 679.6233
2643.2542 | 679.3664
2644.2542 | 681.194
2645.2542 | 681.4026
2646.2542 | 678.8008
2647.2542 | 680.4341
2648.2542 | 682.7466
2649.2542 | 683.7528
2650.2542 | 684.3105
2651.2542 | 684.137
2652.2542 | 683.4224
2653.2542 | 683.6439
2654.2542 | 682.4611
2655.2542 | 680.8214
2656.2542 | 680.6421
2657.2542 | 683.3271
2658.2542 | 684.8636
2659.2542 | 683.585
2660.2542 | 683.5248
2661.2542 | 685.6421
2662.2542 | 685.2423
2663.2542 | 684.4626
2664.2542 | 685.7782
2665.2542 | 686.043
2666.2542 | 687.7867
2667.2542 | 688.8375
2668.2542 | 688.7547
2669.2542 | 688.274
2670.2542 | 687.3851
2671.2542 | 688.1389
2672.2542 | 690.2925
2673.2542 | 690.76
2674.2542 | 687.3742
2675.2542 | 686.9564
2676.2542 | 689.0796
2677.2542 | 689.3502
2678.2542 | 689.9444
2679.2542 | 691.3056
2680.2542 | 690.459
2681.2542 | 689.9095
2682.2542 | 689.4832
2683.2542 | 692.2351
2684.2542 | 695.5901
2685.2542 | 695.3599
2686.2542 | 694.7761
2687.2542 | 694.8059
2688.2542 | 693.1255
2689.2542 | 694.9642
2690.2542 | 695.6957
2691.2542 | 695.9029
2692.2542 | 695.9591
2693.2542 | 695.0416
2694.2542 | 692.0831
2695.2542 | 691.7949
2696.2542 | 689.3934
2697.2542 | 690.1326
2698.2542 | 692.5622
2699.2542 | 693.8392
2700.2542 | 694.3815
2701.2542 | 693.9889
2702.2542 | 693.8498
2703.2542 | 696.0214
2704.2542 | 700.4523
2705.2542 | 702.5833
2706.2542 | 700.5621
2707.2542 | 700.29
2708.2542 | 701.2723
2709.2542 | 701.5531
2710.2542 | 702.6248
2711.2542 | 704.7738
2712.2542 | 704.8129
2713.2542 | 706.2785
2714.2542 | 709.8452
2715.2542 | 714.0965
2716.2542 | 717.4611
2717.2542 | 722.021
2718.2542 | 723.8586
2719.2542 | 727.9395
2720.2542 | 730.2941
2721.2542 | 731.589
2722.2542 | 732.8285
2723.2542 | 731.6091
2724.2542 | 732.5606
2725.2542 | 734.7508
2726.2542 | 731.2488
2727.2542 | 730.7993
2728.2542 | 729.8689
2729.2542 | 728.8252
2730.2542 | 724.67
2731.2542 | 724.2602
2732.2542 | 721.3639
2733.2542 | 720.5236
2734.2542 | 717.3396
2735.2542 | 716.5304
2736.2542 | 716.3354
2737.2542 | 715.4368
2738.2542 | 715.9758
2739.2542 | 715.3969
2740.2542 | 716.007
2741.2542 | 714.6811
2742.2542 | 712.7325
2743.2542 | 710.7682
2744.2542 | 708.6631
2745.2542 | 708.11
2746.2542 | 707.5117
2747.2542 | 706.9124
2748.2542 | 707.9769
2749.2542 | 705.5811
2750.2542 | 706.2217
2751.2542 | 706.9524
2752.2542 | 708.6386
2753.2542 | 709.5512
2754.2542 | 708.0947
2755.2542 | 707.9141
2756.2542 | 708.5187
2757.2542 | 709.2787
2758.2542 | 709.7444
2759.2542 | 708.028
2760.2542 | 704.1124
2761.2542 | 702.8178
2762.2542 | 700.8008
2763.2542 | 699.5395
2764.2542 | 698.9836
2765.2542 | 696.9528
2766.2542 | 694.5285
2767.2542 | 693.7032
2768.2542 | 691.5527
2769.2542 | 689.7381
2770.2542 | 692.1549
2771.2542 | 694.7536
2772.2542 | 696.0678
2773.2542 | 698.2438
2774.2542 | 699.7542
2775.2542 | 700.702
2776.2542 | 703.1261
2777.2542 | 707.0176
2778.2542 | 710.7084
2779.2542 | 713.3518
2780.2542 | 717.5179
2781.2542 | 720.8547
2782.2542 | 720.413
2783.2542 | 720.8344
2784.2542 | 719.0704
2785.2542 | 718.86
2786.2542 | 718.2131
2787.2542 | 719.509
2788.2542 | 720.3731
2789.2542 | 721.337
2790.2542 | 721.1523
2791.2542 | 722.8126
2792.2542 | 724.8291
2793.2542 | 725.6465
2794.2542 | 728.0325
2795.2542 | 730.0677
2796.2542 | 728.8354
2797.2542 | 728.9354
2798.2542 | 729.9082
2799.2542 | 730.2793
2800.2542 | 731.4824
2801.2542 | 731.853
2802.2542 | 728.4722
2803.2542 | 726
2804.2542 | 726.6922
2805.2542 | 727.8113
2806.2542 | 728.9036
2807.2542 | 728.7381
2808.2542 | 730.7123
2809.2542 | 731.6823
2810.2542 | 732.061
2811.2542 | 731.9035
2812.2542 | 732.4292
2813.2542 | 730.24
2814.2542 | 727.8293
2815.2542 | 726.2162
2816.2542 | 725.7072
2817.2542 | 724.5
2818.2542 | 727.0372
2819.2542 | 729.4723
2820.2542 | 730.1846
2821.2542 | 729.9019
2822.2542 | 729.3992
2823.2542 | 729.9339
2824.2542 | 732.7724
2825.2542 | 737.4998
2826.2542 | 738.9333
2827.2542 | 740.4459
2828.2542 | 739.557
2829.2542 | 740.026
2830.2542 | 741.2375
2831.2542 | 741.7961
2832.2542 | 740.0644
2833.2542 | 738.7713
2834.2542 | 736.8295
2835.2542 | 733.4213
2836.2542 | 729.2919
2837.2542 | 723.9542
2838.2542 | 717.5098
2839.2542 | 710.4046
2840.2542 | 704.4345
2841.2542 | 700.137
2842.2542 | 697.3935
2843.2542 | 695.3625
2844.2542 | 693.629
2845.2542 | 691.4799
2846.2542 | 690.7274
2847.2542 | 688.9894
2848.2542 | 686.1139
2849.2542 | 687.0187
2850.2542 | 686.4878
2851.2542 | 688.4683
2852.2542 | 691.1882
2853.2542 | 691.3609
2854.2542 | 693.0086
2855.2542 | 692.6548
2856.2542 | 692.7527
2857.2542 | 692.4123
2858.2542 | 692.6268
2859.2542 | 694.7121
2860.2542 | 696.5331
2861.2542 | 696.5582
2862.2542 | 697.8795
2863.2542 | 696.9342
2864.2542 | 693.3461
2865.2542 | 689.6622
2866.2542 | 686.9597
2867.2542 | 686.5935
2868.2542 | 686.7079
2869.2542 | 686.1027
2870.2542 | 685.3226
2871.2542 | 686.7883
2872.2542 | 688.6129
2873.2542 | 688.7952
2874.2542 | 690.9928
2875.2542 | 691.3619
2876.2542 | 691.5378
2877.2542 | 690.5415
2878.2542 | 689.5802
2879.2542 | 690.4408
2880.2542 | 690.2712
2881.2542 | 692.5385
2882.2542 | 694.898
2883.2542 | 696.3531
2884.2542 | 698.2654
2885.2542 | 696.4049
2886.2542 | 694.9798
2887.2542 | 692.1372
2888.2542 | 690.9145
2889.2542 | 689.8293
2890.2542 | 688.9816
2891.2542 | 690.0387
2892.2542 | 689.0032
2893.2542 | 689.4951
2894.2542 | 689.3851
2895.2542 | 688.8499
2896.2542 | 689.3946
2897.2542 | 691.7768
2898.2542 | 690.4829
2899.2542 | 690.0763
2900.2542 | 688.5536
2901.2542 | 687.7795
2902.2542 | 686.6638
2903.2542 | 687.9547
2904.2542 | 688.911
2905.2542 | 687.9791
2906.2542 | 687.6853
2907.2542 | 687.0699
2908.2542 | 687.1569
2909.2542 | 684.8591
2910.2542 | 683.6844
2911.2542 | 683.0325
2912.2542 | 680.9116
2913.2542 | 681.004
2914.2542 | 681.6383
2915.2542 | 682.5966
2916.2542 | 685.105
2917.2542 | 686.2293
2918.2542 | 685.588
2919.2542 | 686.4536
2920.2542 | 684.3272
2921.2542 | 685.698
2922.2542 | 686.0307
2923.2542 | 686.2922
2924.2542 | 686.125
2925.2542 | 684.2489
2926.2542 | 686.2897
2927.2542 | 688.6993
2928.2542 | 691.3422
2929.2542 | 692.5424
2930.2542 | 691.5251
2931.2542 | 693.0055
2932.2542 | 693.2416
2933.2542 | 693.7074
2934.2542 | 690.4046
2935.2542 | 686.4478
2936.2542 | 686.6037
2937.2542 | 686.4098
2938.2542 | 684.1794
2939.2542 | 682.9336
2940.2542 | 682.2967
2941.2542 | 682.9933
2942.2542 | 684.7062
2943.2542 | 687.1245
2944.2542 | 687.991
2945.2542 | 688.7304
2946.2542 | 689.3371
2947.2542 | 687.1843
2948.2542 | 686.6524
2949.2542 | 684.9575
2950.2542 | 683.6241
2951.2542 | 681.4698
2952.2542 | 680.2481
2953.2542 | 681.8522
2954.2542 | 682.2572
2955.2542 | 679.737
2956.2542 | 680.1377
2957.2542 | 681.4283
2958.2542 | 682.5688
2959.2542 | 681.0094
2960.2542 | 679.6686
2961.2542 | 679.7221
2962.2542 | 682.2524
2963.2542 | 681.7273
2964.2542 | 683.3399
2965.2542 | 683.9879
2966.2542 | 684.3484
2967.2542 | 684.2999
2968.2542 | 681.7213
2969.2542 | 681.0561
2970.2542 | 680.9328
2971.2542 | 681.7484
2972.2542 | 681.0498
2973.2542 | 680.5439
2974.2542 | 680.2437
2975.2542 | 682.9707
2976.2542 | 685.6605
2977.2542 | 686.1025
2978.2542 | 684.4919
2979.2542 | 684.4603
2980.2542 | 683.5172
2981.2542 | 686.8677
2982.2542 | 692.361
2983.2542 | 697.2931
2984.2542 | 696.987
2985.2542 | 695.6149
2986.2542 | 694.2544
2987.2542 | 692.329
2988.2542 | 692.9933
2989.2542 | 694.3671
2990.2542 | 692.7384
2991.2542 | 692.4258
2992.2542 | 691.6653
2993.2542 | 690.6609
2994.2542 | 691.5998
2995.2542 | 691.4004
2996.2542 | 693.0941
2997.2542 | 694.1982
2998.2542 | 692.3144
2999.2542 | 695.9672
3000.2542 | 698.1084
3001.2542 | 698.7711
3002.2542 | 698.1156
3003.2542 | 699.2528
3004.2542 | 702.7987
3005.2542 | 704.1955
3006.2542 | 706.9581
3007.2542 | 706.4497
3008.2542 | 706.7779
3009.2542 | 707.1176
3010.2542 | 709.4196
3011.2542 | 711.7107
3012.2542 | 710.9258
3013.2542 | 708.6221
3014.2542 | 705.6536
3015.2542 | 703.9003
3016.2542 | 702.8861
3017.2542 | 702.7047
3018.2542 | 701.1038
3019.2542 | 700.8629
3020.2542 | 699.0083
3021.2542 | 696.5237
3022.2542 | 694.8646
3023.2542 | 694.5375
3024.2542 | 694.034
3025.2542 | 693.8915
3026.2542 | 694.7889
3027.2542 | 695.3381
3028.2542 | 694.9118
3029.2542 | 695.9458
3030.2542 | 693.9736
3031.2542 | 690.399
3032.2542 | 690.9136
3033.2542 | 691.5846
3034.2542 | 694.6556
3035.2542 | 695.8285
3036.2542 | 697.7672
3037.2542 | 698.072
3038.2542 | 696.9629
3039.2542 | 694.5512
3040.2542 | 692.7919
3041.2542 | 692.2529
3042.2542 | 691.2126
3043.2542 | 690.8331
3044.2542 | 689.9601
3045.2542 | 689.509
3046.2542 | 693.961
3047.2542 | 697.8946
3048.2542 | 696.9566
3049.2542 | 694.6213
3050.2542 | 690.8976
3051.2542 | 690.0006
3052.2542 | 686.8574
3053.2542 | 686.5867
3054.2542 | 687.607
3055.2542 | 688.1178
3056.2542 | 685.8724
3057.2542 | 687.3848
3058.2542 | 689.3565
3059.2542 | 690.7535
3060.2542 | 691.2004
3061.2542 | 689.9651
3062.2542 | 688.5432
3063.2542 | 686.0726
3064.2542 | 687.72
3065.2542 | 687.7299
3066.2542 | 688.0097
3067.2542 | 688.3509
3068.2542 | 686.6069
3069.2542 | 684.7094
3070.2542 | 683.8161
3071.2542 | 682.4103
3072.2542 | 684.1757
3073.2542 | 685.5188
3074.2542 | 688.311
3075.2542 | 689.8309
3076.2542 | 690.4881
3077.2542 | 690.7996
3078.2542 | 688.7667
3079.2542 | 688.8328
3080.2542 | 686.8071
3081.2542 | 684.4571
3082.2542 | 684.3237
3083.2542 | 686.8895
3084.2542 | 687.4599
3085.2542 | 686.2102
3086.2542 | 687.5372
3087.2542 | 687.3345
3088.2542 | 690.027
3089.2542 | 689.7681
3090.2542 | 689.9929
3091.2542 | 688.8898
3092.2542 | 686.8603
3093.2542 | 684.3274
3094.2542 | 685.6525
3095.2542 | 685.5818
3096.2542 | 686.2328
3097.2542 | 685.5497
3098.2542 | 685.7322
3099.2542 | 684.3021
3100.2542 | 685.4487
3101.2542 | 686.0348
3102.2542 | 688.5502
3103.2542 | 689.2589
3104.2542 | 689.3583
3105.2542 | 689.1753
3106.2542 | 689.7491
3107.2542 | 688.9388
3108.2542 | 688.8954
3109.2542 | 689.8925
3110.2542 | 691.1853
3111.2542 | 689.5298
3112.2542 | 689.2077
3113.2542 | 690.8466
3114.2542 | 692.699
3115.2542 | 692.5003
3116.2542 | 691.0288
3117.2542 | 690.8538
3118.2542 | 688.843
3119.2542 | 687.5849
3120.2542 | 688.365
3121.2542 | 688.8684
3122.2542 | 689.0243
3123.2542 | 689.374
3124.2542 | 689.5651
3125.2542 | 688.5277
3126.2542 | 688.2907
3127.2542 | 690.549
3128.2542 | 689.5976
3129.2542 | 687.759
3130.2542 | 687.1637
3131.2542 | 686.3796
3132.2542 | 683.8144
3133.2542 | 684.6625
3134.2542 | 684.0011
3135.2542 | 683.5223
3136.2542 | 682.1217
3137.2542 | 683.0615
3138.2542 | 682.5525
3139.2542 | 680.0341
3140.2542 | 681.2955
3141.2542 | 683.8009
3142.2542 | 686.0539
3143.2542 | 686.939
3144.2542 | 686.8133
3145.2542 | 685.5366
3146.2542 | 684.8334
3147.2542 | 684.6516
3148.2542 | 683.339
3149.2542 | 681.2059
3150.2542 | 681.1031
3151.2542 | 681.3983
3152.2542 | 681.4231
3153.2542 | 680.2913
3154.2542 | 682.5918
3155.2542 | 682.9099
3156.2542 | 682.2798
3157.2542 | 680.0211
3158.2542 | 681.7474
3159.2542 | 682.6969
3160.2542 | 684.512
3161.2542 | 687.2074
3162.2542 | 686.0228
3163.2542 | 685.1916
3164.2542 | 681.533
3165.2542 | 681.1658
3166.2542 | 684.7351
3167.2542 | 688.4087
3168.2542 | 689.1775
3169.2542 | 685.2678
3170.2542 | 684.8774
3171.2542 | 681.5925
3172.2542 | 682.1867
3173.2542 | 680.5457
3174.2542 | 679.5879
3175.2542 | 680.097
3176.2542 | 679.9731
3177.2542 | 681.0856
3178.2542 | 681.0767
3179.2542 | 680.7221
3180.2542 | 681.945
3181.2542 | 681.7899
3182.2542 | 682.155
3183.2542 | 681.627
3184.2542 | 681.2738
3185.2542 | 680.9917
3186.2542 | 683.2352
3187.2542 | 685.2311
3188.2542 | 685.5084
3189.2542 | 684.0609
3190.2542 | 685.5035
3191.2542 | 684.3888
3192.2542 | 683.0704
3193.2542 | 683.2811
3194.2542 | 683.4651
3195.2542 | 682.5647
3196.2542 | 680.7288
3197.2542 | 679.6648
3198.2542 | 680.0836
3199.2542 | 678.5632
3200.2542 | 679.1279
3201.2542 | 680.4494
3202.2542 | 680.8545
3203.2542 | 680.0864
3204.2542 | 679.0381
3205.2542 | 677.9436
3206.2542 | 678.285
3207.2542 | 677.0594
3208.2542 | 675.3345
3209.2542 | 675.8424
3210.2542 | 675.5909
3211.2542 | 676.6197
3212.2542 | 673.2571
3213.2542 | 672.9712
3214.2542 | 672.5614
3215.2542 | 671.9027
3216.2542 | 672.2978
3217.2542 | 672.2858
3218.2542 | 672.1921
3219.2542 | 675.1443
3220.2542 | 676.381
3221.2542 | 675.2494
3222.2542 | 673.1644
3223.2542 | 675.2246
3224.2542 | 677.4694
3225.2542 | 677.3034
3226.2542 | 676.5268
3227.2542 | 678.7621
3228.2542 | 683.19
3229.2542 | 684.1436
3230.2542 | 686.0051
3231.2542 | 686.2112
3232.2542 | 687.137
3233.2542 | 687.3174
3234.2542 | 686.3825
3235.2542 | 687.5985
3236.2542 | 688.7588
3237.2542 | 687.2124
3238.2542 | 685.7438
3239.2542 | 685.7504
3240.2542 | 683.7611
3241.2542 | 682.7742
3242.2542 | 681.5059
3243.2542 | 681.2062
3244.2542 | 683.8319
3245.2542 | 683.5779
3246.2542 | 683.3133
3247.2542 | 677.2123
3248.2542 | 674.9873
3249.2542 | 676.5806
3250.2542 | 677.5857
3251.2542 | 678.3242
3252.2542 | 678.5633
3253.2542 | 678.0332
3254.2542 | 679.6268
3255.2542 | 680.6261
3256.2542 | 680.5718
3257.2542 | 679.9558
3258.2542 | 681.661
3259.2542 | 684.3812
3260.2542 | 682.6351
3261.2542 | 679.7304
3262.2542 | 678.4631
3263.2542 | 678.9212
3264.2542 | 678.4715
3265.2542 | 679.3421
3266.2542 | 679.0993
3267.2542 | 681.7145
3268.2542 | 681.8218
3269.2542 | 680.1391
3270.2542 | 678.5415
3271.2542 | 678.5614
3272.2542 | 680.6606
3273.2542 | 683.6701
3274.2542 | 682.9102
3275.2542 | 682.4946
3276.2542 | 681.7008
3277.2542 | 680.2297
3278.2542 | 679.2929
3279.2542 | 680.2539
3280.2542 | 680.5312
3281.2542 | 679.7621
3282.2542 | 679.1663
3283.2542 | 678.025
3284.2542 | 677.5831
3285.2542 | 677.1372
3286.2542 | 676.463
3287.2542 | 675.3882
3288.2542 | 671.82
3289.2542 | 672.7796
3290.2542 | 674.7302
3291.2542 | 674.375
3292.2542 | 677.2431
3293.2542 | 678.2681
3294.2542 | 678.307
3295.2542 | 677.5548
3296.2542 | 678.4338
3297.2542 | 679.0532
3298.2542 | 680.7507
3299.2542 | 681.6998
3300.2542 | 681.6955
3301.2542 | 680.0755
3302.2542 | 678.0787
3303.2542 | 674.822
3304.2542 | 676.8944
3305.2542 | 680.5128
3306.2542 | 682.8541
3307.2542 | 682.2362
3308.2542 | 681.9205
3309.2542 | 681.6669
3310.2542 | 680.9142
3311.2542 | 682.5131
3312.2542 | 681.9301
3313.2542 | 681.2991
3314.2542 | 678.3415
3315.2542 | 675.9856
3316.2542 | 675.2851
3317.2542 | 676.2739
3318.2542 | 678.0596
3319.2542 | 680.1709
3320.2542 | 678.3138
3321.2542 | 676.2672
3322.2542 | 674.1829
3323.2542 | 674.1773
3324.2542 | 673.5
3325.2542 | 674.9973
3326.2542 | 674.997
3327.2542 | 671.4238
3328.2542 | 672.5629
3329.2542 | 674.6638
3330.2542 | 674.8116
3331.2542 | 674.9923
3332.2542 | 676.5567
3333.2542 | 676.9365
3334.2542 | 676.2062
3335.2542 | 673.5138
3336.2542 | 672.4897
3337.2542 | 671.442
3338.2542 | 673.0574
3339.2542 | 672.3478
3340.2542 | 674.4958
3341.2542 | 673.0773
3342.2542 | 675.5541
3343.2542 | 675.9342
3344.2542 | 674.594
3345.2542 | 673.9734
3346.2542 | 674.799
3347.2542 | 674.2393
3348.2542 | 673.6345
3349.2542 | 673.026
3350.2542 | 672.093
3351.2542 | 675.069
3352.2542 | 676.397
3353.2542 | 677.527
3354.2542 | 676.7711
3355.2542 | 677.1482
3356.2542 | 677.4103
3357.2542 | 676.9443
3358.2542 | 673.9264
3359.2542 | 674.2174
3360.2542 | 674.6077
3361.2542 | 674.1334
3362.2542 | 675.6628
3363.2542 | 675.9135
3364.2542 | 675.1802
3365.2542 | 675.0982
3366.2542 | 676.4419
3367.2542 | 674.7268
3368.2542 | 675.8867
3369.2542 | 676.8717
3370.2542 | 675.7264
3371.2542 | 672.3895
3372.2542 | 669.2234
3373.2542 | 670.4854
3374.2542 | 672.1518
3375.2542 | 675.7415
3376.2542 | 676.7801
3377.2542 | 676.9497
3378.2542 | 676.513
3379.2542 | 676.7272
3380.2542 | 677.7338
3381.2542 | 678.6883
3382.2542 | 678.2553
3383.2542 | 676.3575
3384.2542 | 678.6101
3385.2542 | 678.5092
3386.2542 | 677.6687
3387.2542 | 675.8835
3388.2542 | 675.4462
3389.2542 | 674.1316
3390.2542 | 673.5633
3391.2542 | 674.5943
3392.2542 | 675.2088
3393.2542 | 674.7359
3394.2542 | 673.7686
3395.2542 | 671.1976
3396.2542 | 672.8566
3397.2542 | 671.7783
3398.2542 | 668.4484
3399.2542 | 668.1258
3400.2542 | 665.9965
3401.2542 | 666.1141
3402.2542 | 666.2315
3403.2542 | 664.1927
3404.2542 | 663.108
3405.2542 | 662.2096
3406.2542 | 663.6471
3407.2542 | 662.763
3408.2542 | 663.2547
3409.2542 | 661.927
3410.2542 | 662.9841
3411.2542 | 662.3063
3412.2542 | 661.7284
3413.2542 | 661.9761
3414.2542 | 664.5927
3415.2542 | 665.8651
3416.2542 | 664.1454
3417.2542 | 665.0558
3418.2542 | 665.1013
3419.2542 | 665.9482
3420.2542 | 665.4511
3421.2542 | 667.0137
3422.2542 | 668.5962
3423.2542 | 668.7615
3424.2542 | 669.7291
3425.2542 | 668.7883
3426.2542 | 669.812
3427.2542 | 670.9816
3428.2542 | 672.1712
3429.2542 | 670.2643
3430.2542 | 670.5641
3431.2542 | 671.636
3432.2542 | 673.7532
3433.2542 | 673.3098
3434.2542 | 674.213
3435.2542 | 676.9314
3436.2542 | 676.5281
3437.2542 | 675.4687
3438.2542 | 674.5257
3439.2542 | 676.0721
3440.2542 | 675.74
3441.2542 | 674.9756
3442.2542 | 672.7477
3443.2542 | 672.461
3444.2542 | 672.4826
3445.2542 | 671.7282
3446.2542 | 670.287
3447.2542 | 672.0833
3448.2542 | 674.1669
3449.2542 | 676.1136
3450.2542 | 678.6532
3451.2542 | 679.2729
3452.2542 | 678.8205
3453.2542 | 679.1495
3454.2542 | 677.9385
3455.2542 | 676.9476
3456.2542 | 676.1509
3457.2542 | 675.2415
3458.2542 | 676.3854
3459.2542 | 674.1941
3460.2542 | 674.3938
3461.2542 | 675.5158
3462.2542 | 674.2551
3463.2542 | 673.2294
3464.2542 | 674.1886
3465.2542 | 672.3897
3466.2542 | 673.5993
3467.2542 | 674.3577
3468.2542 | 674.4836
3469.2542 | 674.4112
3470.2542 | 673.5962
3471.2542 | 675.0179
3472.2542 | 675.4934
3473.2542 | 677.027
3474.2542 | 677.7007
3475.2542 | 680.8544
3476.2542 | 682.8439
3477.2542 | 683.4536
3478.2542 | 681.4481
3479.2542 | 682.0721
3480.2542 | 682.5617
3481.2542 | 681.7533
3482.2542 | 679.39
3483.2542 | 676.47
3484.2542 | 675.2168
3485.2542 | 677.0933
3486.2542 | 678.5247
3487.2542 | 676.1593
3488.2542 | 675.8891
3489.2542 | 674.4915
3490.2542 | 673.372
3491.2542 | 673.8452
3492.2542 | 674.545
3493.2542 | 675.1526
3494.2542 | 675.0679
3495.2542 | 671.4769
3496.2542 | 671.7197
3497.2542 | 673.3877
3498.2542 | 674.412
3499.2542 | 672.5427
3500.2542 | 672.5218
3501.2542 | 674.2663
3502.2542 | 674.422
3503.2542 | 673.7437
3504.2542 | 675.7216
3505.2542 | 675.1425
3506.2542 | 673.6462
3507.2542 | 674.1981
3508.2542 | 673.1521
3509.2542 | 673.4921
3510.2542 | 674.1937
3511.2542 | 675.5368
3512.2542 | 673.2693
3513.2542 | 673.3734
3514.2542 | 671.2203
3515.2542 | 672.823
3516.2542 | 673.6097
3517.2542 | 673.4882
3518.2542 | 674.6032
3519.2542 | 673.2645
3520.2542 | 667.5092
3521.2542 | 666.3598
3522.2542 | 667.7536
3523.2542 | 668.5969
3524.2542 | 669.7299
3525.2542 | 671.9695
3526.2542 | 672.8747
3527.2542 | 673.9286
3528.2542 | 676.0013
3529.2542 | 674.571
3530.2542 | 673.7932
3531.2542 | 673.1524
3532.2542 | 674.2302
3533.2542 | 674.0796
3534.2542 | 672.3084
3535.2542 | 670.1055
3536.2542 | 671.9987
3537.2542 | 672.0519
3538.2542 | 672.6202
3539.2542 | 673.1718
3540.2542 | 673.5
3541.2542 | 672.981
3542.2542 | 672.2428
3543.2542 | 674.516
3544.2542 | 676.5229
3545.2542 | 678.9101
3546.2542 | 678.5442
3547.2542 | 679.5388
3548.2542 | 680.6485
3549.2542 | 680.1961
3550.2542 | 679.7628
3551.2542 | 678.5959
3552.2542 | 677.4983
3553.2542 | 677.5399
3554.2542 | 676.4562
3555.2542 | 676.1905
3556.2542 | 676.8565
3557.2542 | 677.4029
3558.2542 | 678.7997
3559.2542 | 676.2436
3560.2542 | 672.2698
3561.2542 | 670.4897
3562.2542 | 672.6425
3563.2542 | 671.4822
3564.2542 | 671.1983
3565.2542 | 669.4158
3566.2542 | 672.8422
3567.2542 | 675.3598
3568.2542 | 677.1797
3569.2542 | 676.1092
3570.2542 | 674.0747
3571.2542 | 675.7389
3572.2542 | 674.8783
3573.2542 | 671.0495
3574.2542 | 670.1655
3575.2542 | 668.1016
3576.2542 | 669.2736
3577.2542 | 670.8937
3578.2542 | 669.32
3579.2542 | 670.8402
3580.2542 | 670.5902
3581.2542 | 671.4457
3582.2542 | 675.8939
3583.2542 | 677.6937
3584.2542 | 677.242
3585.2542 | 670.9736
3586.2542 | 670.5935
3587.2542 | 670.327
3588.2542 | 666.5846
3589.2542 | 666.2929
3590.2542 | 668.949
3591.2542 | 672.4798
3592.2542 | 672.594
3593.2542 | 672.7637
3594.2542 | 672.9708
3595.2542 | 674.6821
3596.2542 | 677.0916
3597.2542 | 677.1106
3598.2542 | 679.1193
3599.2542 | 680.3641
3600.2542 | 679.8084
3601.2542 | 676.5869
3602.2542 | 676.0319
3603.2542 | 673.5687
3604.2542 | 672.6992
3605.2542 | 671.2787
3606.2542 | 672.7185
3607.2542 | 671.2012
3608.2542 | 672.4571
3609.2542 | 671.4552
3610.2542 | 672.4223
3611.2542 | 673.2258
3612.2542 | 672.8908
3613.2542 | 672.1789
3614.2542 | 671.935
3615.2542 | 672.6771
3616.2542 | 676.137
3617.2542 | 679.9598
3618.2542 | 678.7216
3619.2542 | 677.3117
3620.2542 | 676.761
3621.2542 | 676.7901
3622.2542 | 674.8478
3623.2542 | 672.9648
3624.2542 | 671.743
3625.2542 | 671.9568
3626.2542 | 671.3176
3627.2542 | 670.8324
3628.2542 | 670.7368
3629.2542 | 669.8687
3630.2542 | 667.7366
3631.2542 | 669.1778
3632.2542 | 670.0865
3633.2542 | 670.4122
3634.2542 | 669.0686
3635.2542 | 669.1749
3636.2542 | 669.8929
3637.2542 | 667.8119
3638.2542 | 664.492
3639.2542 | 664.2733
3640.2542 | 666.8032
3641.2542 | 667.9331
3642.2542 | 666.9655
3643.2542 | 666.3812
3644.2542 | 667.3362
3645.2542 | 665.9365
3646.2542 | 667.998
3647.2542 | 668.8951
3648.2542 | 670.3132
3649.2542 | 670.1305
3650.2542 | 670.747
3651.2542 | 671.5606
3652.2542 | 672.6924
3653.2542 | 671.6648
3654.2542 | 671.3905
3655.2542 | 671.2546
3656.2542 | 670.455
3657.2542 | 669.4794
3658.2542 | 667.7178
3659.2542 | 667.5083
3660.2542 | 667.2851
3661.2542 | 667.7347
3662.2542 | 668.5022
3663.2542 | 669.0525
3664.2542 | 669.1323
3665.2542 | 669.0426
3666.2542 | 672.9788
3667.2542 | 674.7515
3668.2542 | 679.4482
3669.2542 | 680.1297
3670.2542 | 681.0076
3671.2542 | 680.8922
3672.2542 | 683.4313
3673.2542 | 684.543
3674.2542 | 684.9264
3675.2542 | 683.2444
3676.2542 | 682.9252
3677.2542 | 681.5664
3678.2542 | 679.4137
3679.2542 | 679.2886
3680.2542 | 677.7624
3681.2542 | 676.8487
3682.2542 | 675.447
3683.2542 | 676.0118
3684.2542 | 674.4654
3685.2542 | 671.9055
3686.2542 | 671.5044
3687.2542 | 671.0307
3688.2542 | 671.521
3689.2542 | 672.7045
3690.2542 | 673.158
3691.2542 | 673.2045
3692.2542 | 675.5613
3693.2542 | 674.1806
3694.2542 | 671.4225
3695.2542 | 671.0726
3696.2542 | 672.0457
3697.2542 | 671.1074
3698.2542 | 673.1691
3699.2542 | 673.4327
3700.2542 | 671.5323
3701.2542 | 671.8237
3702.2542 | 672.5954
3703.2542 | 672.3703
3704.2542 | 672.4767
3705.2542 | 674.9594
3706.2542 | 676.8298
3707.2542 | 678.903
3708.2542 | 677.3108
3709.2542 | 681.1134
3710.2542 | 682.0775
3711.2542 | 679.9245
3712.2542 | 678.6362
3713.2542 | 678.8526
3714.2542 | 678.3715
3715.2542 | 678.6435
3716.2542 | 679.1829
3717.2542 | 678.4618
3718.2542 | 676.2484
3719.2542 | 674.6925
3720.2542 | 675.0251
3721.2542 | 673.851
3722.2542 | 673.171
3723.2542 | 670.3549
3724.2542 | 670.1265
3725.2542 | 672.3074
3726.2542 | 673.5551
3727.2542 | 672.9924
3728.2542 | 677.0234
3729.2542 | 678.6895
3730.2542 | 682.6437
3731.2542 | 685.3351
3732.2542 | 687.6661
3733.2542 | 685.6014
3734.2542 | 683.9397
3735.2542 | 681.5961
3736.2542 | 680.9717
3737.2542 | 679.4056
3738.2542 | 678.2384
3739.2542 | 676.3148
3740.2542 | 676.1732
3741.2542 | 676.4693
3742.2542 | 674.8769
3743.2542 | 673.772
3744.2542 | 673.5155
3745.2542 | 671.5777
3746.2542 | 670.9867
3747.2542 | 670.4054
3748.2542 | 669.351
3749.2542 | 671.1754
3750.2542 | 671.2917
3751.2542 | 672.1671
3752.2542 | 672.332
3753.2542 | 672.444
3754.2542 | 672.2197
3755.2542 | 673.2606
3756.2542 | 674.3782
3757.2542 | 674.0458
3758.2542 | 674.583
3759.2542 | 674.3373
3760.2542 | 675.3389
3761.2542 | 675.4944
3762.2542 | 676.7044
3763.2542 | 681.7522
3764.2542 | 681.0626
3765.2542 | 678.3721
3766.2542 | 676.8094
3767.2542 | 675.0346
3768.2542 | 677.8117
3769.2542 | 677.1572
3770.2542 | 678.2025
3771.2542 | 678.7252
3772.2542 | 677.8516
3773.2542 | 676.3821
3774.2542 | 674.3424
3775.2542 | 673.1901
3776.2542 | 673.9228
3777.2542 | 674.0291
3778.2542 | 674.1407
3779.2542 | 673.4225
3780.2542 | 673.1728
3781.2542 | 671.2361
3782.2542 | 671.7222
3783.2542 | 670.2164
3784.2542 | 669.5604
3785.2542 | 666.4297
3786.2542 | 664.4938
3787.2542 | 665.4574
3788.2542 | 665.8844
3789.2542 | 665.6403
3790.2542 | 666.9567
3791.2542 | 664.4112
3792.2542 | 665.0956
3793.2542 | 666.5257
3794.2542 | 668.8778
3795.2542 | 669.6265
3796.2542 | 665.5727
3797.2542 | 667.267
3798.2542 | 665.7865
3799.2542 | 666.7763
3800.2542 | 667.1744
3801.2542 | 667.2023
3802.2542 | 666.246
3803.2542 | 663.4542
3804.2542 | 663.565
3805.2542 | 661.761
3806.2542 | 663.588
3807.2542 | 663.8274
3808.2542 | 663.141
3809.2542 | 661.5785
3810.2542 | 661.2817
3811.2542 | 660.8137
3812.2542 | 662.1312
3813.2542 | 664.5733
3814.2542 | 666.8415
3815.2542 | 666.2661
3816.2542 | 667.8684
3817.2542 | 671.8562
3818.2542 | 675.6144
3819.2542 | 671.7315
3820.2542 | 671.8861
3821.2542 | 672.9643
3822.2542 | 672.723
3823.2542 | 671.5393
3824.2542 | 672.2159
3825.2542 | 670.9843
3826.2542 | 669.0013
3827.2542 | 673.4748
3828.2542 | 677.5529
3829.2542 | 679.9767
3830.2542 | 681.7025
3831.2542 | 681.3348
3832.2542 | 681.6051
3833.2542 | 680.9001
3834.2542 | 682.1238
3835.2542 | 680.8155
3836.2542 | 681.3534
3837.2542 | 680.8635
3838.2542 | 679.4028
3839.2542 | 679.6998
3840.2542 | 678.5768
3841.2542 | 677.5955
3842.2542 | 675.954
3843.2542 | 676.7539
3844.2542 | 679.7359
3845.2542 | 681.4621
3846.2542 | 681.4967
3847.2542 | 680.7715
3848.2542 | 680.3883
3849.2542 | 680.6586
3850.2542 | 679.1892
3851.2542 | 677.4627
3852.2542 | 677.3091
3853.2542 | 676.5851
3854.2542 | 676.8046
3855.2542 | 676.7695
3856.2542 | 677.0975
3857.2542 | 674.0619
3858.2542 | 671.5601
3859.2542 | 669.8866
3860.2542 | 670.0144
3861.2542 | 670.2126
3862.2542 | 671.1881
3863.2542 | 671.8259
3864.2542 | 672.9879
3865.2542 | 672.499
3866.2542 | 669.237
3867.2542 | 665.6756
3868.2542 | 662.8597
3869.2542 | 666.8403
3870.2542 | 667.165
3871.2542 | 667.1935
3872.2542 | 663.9055
3873.2542 | 665.7158
3874.2542 | 666.3955
3875.2542 | 666.49
3876.2542 | 665.518
3877.2542 | 665.866
3878.2542 | 667.9586
3879.2542 | 668.0863
3880.2542 | 669.1269
3881.2542 | 671.9616
3882.2542 | 672.1525
3883.2542 | 672.7522
3884.2542 | 672.827
3885.2542 | 674.073
3886.2542 | 675.2188
3887.2542 | 675.6868
3888.2542 | 675.5073
3889.2542 | 674.7409
3890.2542 | 672.564
3891.2542 | 673.0588
3892.2542 | 672.8778
3893.2542 | 672.4065
3894.2542 | 669.646
3895.2542 | 668.7645
3896.2542 | 674.3902
3897.2542 | 678.7499
3898.2542 | 679.4325
3899.2542 | 678.0659
3900.2542 | 676.1194
3901.2542 | 673.1321
3902.2542 | 674.9444
3903.2542 | 677.2724
3904.2542 | 675.3798
3905.2542 | 674.2721
3906.2542 | 674.8428
3907.2542 | 677.1997
3908.2542 | 675.8623
3909.2542 | 674.3753
3910.2542 | 672.8768
3911.2542 | 670.9777
3912.2542 | 671.5802
3913.2542 | 673.6566
3914.2542 | 675.0808
3915.2542 | 676.2774
3916.2542 | 675.1219
3917.2542 | 673.8406
3918.2542 | 675.5721
3919.2542 | 676.6797
3920.2542 | 675.0981
3921.2542 | 674.1377
3922.2542 | 674.1395
3923.2542 | 675.7833
3924.2542 | 673.7895
3925.2542 | 672.724
3926.2542 | 674.2381
3927.2542 | 673.6061
3928.2542 | 671.8201
3929.2542 | 673.328
3930.2542 | 669.5198
3931.2542 | 665.6963
3932.2542 | 668.9396
3933.2542 | 669.6678
3934.2542 | 668.8939
3935.2542 | 671.2938
3936.2542 | 672.4269
3937.2542 | 673.6817
3938.2542 | 674.8762
3939.2542 | 672.7587
3940.2542 | 674.2142
3941.2542 | 676.8195
3942.2542 | 678.7364
3943.2542 | 678.4636
3944.2542 | 680.1321
3945.2542 | 679.7631
3946.2542 | 680.9174
3947.2542 | 681.96
3948.2542 | 679.3167
3949.2542 | 679.5548
3950.2542 | 678.8744
3951.2542 | 679.3617
3952.2542 | 675.6645
3953.2542 | 675.1157
3954.2542 | 675.9969
3955.2542 | 675.9941
3956.2542 | 676.5854
3957.2542 | 673.3418
3958.2542 | 671.0913
3959.2542 | 671.0112
3960.2542 | 671.5591