## Test Conditions
DESIREE-FIRE Intermediate Scale Test 9 - Circuit Simulator Data Only
Test Date: | 2010-03-17
DCSim DAQ Start Time | 13:14
DCSim Time for Synchronization | 13:15
Heat Source Synchronization | 0:00 | hours:minutes:seconds
Heat Source DAQ Start Time | 13:14
Fire Time | 13:41
Offset | 0:27 | hours:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 1620 | seconds
Heat Source Offset | 0:26 | hours:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 1590 | seconds
Heat Source Stop Time | 14:36
Test Duration | 0:55 | hours:minutes:seconds
| 3300 | seconds
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
Intercable Configuration | EPR/CPE, 7c, 12AWG |  | Cable thermocouples were not used during this test. | There are three cable TCs monitoring air temperatures for the center of the tray in C Position. Channels 5, 6, and 7 are represented as "C Position - 3'", "C Position - Middle", and "C Position - 7'" in the raw temperature files.
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds.
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | Int-Cab_VT7-T1 | Int-Cab_VT7-T2 | Int-Cab_VT7-T3 | Int-Cab_VT7-T4 | Int-Cab_VT7-T5 | Int-Cab_VT7-T6 | Int-Cab_VT7-T7 | Int-Cab_VTU-S1+a | Int-Cab_VTU-S1+b | Int-Cab_VTU-S2+a | Int-Cab_VTU-S2+b | Int-Cab_VTU-S1-a | Int-Cab_VTU-S1-b | Int-Cab_VTU-S2-a | Int-Cab_VTU-S2-b | T1-V(Batt -) | T2 -V(Batt -) | T3 - V(Batt -) | T4 - V(Batt -) | T5 - V(Batt -) | T6 - V(Batt -) | T7 - V(Batt -) | {S1+a} - V(Batt - ) | {S1+b} - V(Batt - ) | {S2+a} - V(Batt - ) | {S2+b} - V(Batt - ) | {S1-a} - V(Batt -) | {S1-b} - V(Batt - ) | {S2-a} - V(Batt - ) | {S2-b} - V(Batt - ) | {S1+a} - {S1-a} | {S1+a} - {S2-a} | {S2+a} - {S1-a} | {S2+a} - {S2-a}
-0.6875 | 122.1451 | -61.0107 | 61.0153 | 0.089802 | -0.031363 | 0.042944 | -0.070802 | 0.040843 | 0.048956 | -0.12223 | 60.7359 | 60.744 | 60.7725 | 60.7307 | 60.9379 | 61.0946 | 60.7309 | 60.9186 | 0.10354 | -0.01763 | 0.056677 | -0.057069 | 0.054576 | 0.062689 | -0.1085 | 60.7496 | 60.7577 | 60.7862 | 60.7444 | 60.9517 | 61.1084 | 60.7446 | 60.9323 | -0.20208 | 0.004984 | -0.16548 | 0.041576
1.0469 | 122.1405 | -61.0794 | 60.9558 | 0.085224 | -0.026784 | 0.038365 | -0.07538 | 0.036265 | 0.053534 | -0.11308 | 60.7359 | 60.7485 | 60.777 | 60.7535 | 60.9334 | 61.09 | 60.7355 | 60.9094 | 0.098957 | -0.013051 | 0.052098 | -0.061647 | 0.049998 | 0.067267 | -0.099344 | 60.7496 | 60.7623 | 60.7908 | 60.7673 | 60.9471 | 61.1038 | 60.7492 | 60.9232 | -0.1975 | 0.000405 | -0.15633 | 0.041575
2.7812 | 122.1451 | -60.9833 | 61.0153 | 0.089802 | -0.031363 | 0.042944 | -0.07538 | 0.045421 | 0.058113 | -0.12681 | 60.7359 | 60.7485 | 60.7679 | 60.7169 | 60.9425 | 61.0946 | 60.74 | 60.914 | 0.10354 | -0.01763 | 0.056677 | -0.061647 | 0.059154 | 0.071846 | -0.11308 | 60.7496 | 60.7623 | 60.7816 | 60.7306 | 60.9563 | 61.1084 | 60.7538 | 60.9277 | -0.20665 | -0.004173 | -0.17464 | 0.027841
4.4375 | 122.168 | -61.0199 | 60.9924 | 0.089802 | -0.031363 | 0.038365 | -0.07538 | 0.036265 | 0.048956 | -0.11765 | 60.7267 | 60.7302 | 60.7633 | 60.7169 | 60.9334 | 61.0992 | 60.7309 | 60.9094 | 0.10354 | -0.01763 | 0.052098 | -0.061647 | 0.049998 | 0.062689 | -0.10392 | 60.7404 | 60.744 | 60.777 | 60.7306 | 60.9471 | 61.1129 | 60.7446 | 60.9232 | -0.20665 | -0.004173 | -0.17006 | 0.032419
6.1719 | 122.1268 | -61.0794 | 60.9558 | 0.089802 | -0.031363 | 0.029208 | -0.079959 | 0.040843 | 0.044377 | -0.12223 | 60.7313 | 60.744 | 60.7679 | 60.7307 | 60.9334 | 61.0855 | 60.7263 | 60.9094 | 0.10354 | -0.01763 | 0.042941 | -0.066226 | 0.054576 | 0.05811 | -0.1085 | 60.745 | 60.7577 | 60.7816 | 60.7444 | 60.9471 | 61.0992 | 60.74 | 60.9232 | -0.20208 | 0.004984 | -0.16548 | 0.041576
7.8906 | 122.1817 | -61.0382 | 60.9695 | 0.085224 | -0.022205 | 0.033786 | -0.07538 | 0.036265 | 0.048956 | -0.12223 | 60.7267 | 60.7485 | 60.777 | 60.7352 | 60.9288 | 61.09 | 60.7263 | 60.9094 | 0.098957 | -0.008472 | 0.047519 | -0.061647 | 0.049998 | 0.062689 | -0.1085 | 60.7404 | 60.7623 | 60.7908 | 60.749 | 60.9425 | 61.1038 | 60.74 | 60.9232 | -0.20208 | 0.000405 | -0.15175 | 0.050732
9.5625 | 122.1634 | -61.0428 | 60.9375 | 0.085224 | -0.035942 | 0.038365 | -0.079959 | 0.036265 | 0.048956 | -0.12223 | 60.7313 | 60.7485 | 60.777 | 60.7627 | 60.9196 | 61.09 | 60.7217 | 60.9048 | 0.098957 | -0.022209 | 0.052098 | -0.066226 | 0.049998 | 0.062689 | -0.1085 | 60.745 | 60.7623 | 60.7908 | 60.7764 | 60.9334 | 61.1038 | 60.7355 | 60.9186 | -0.18834 | 0.009563 | -0.14259 | 0.055311
11.2969 | 122.1222 | -61.0336 | 60.9558 | 0.080646 | -0.031363 | 0.038365 | -0.07538 | 0.045421 | 0.044377 | -0.12681 | 60.7313 | 60.7302 | 60.7725 | 60.7581 | 60.9288 | 61.0809 | 60.7309 | 60.9094 | 0.094379 | -0.01763 | 0.052098 | -0.061647 | 0.059154 | 0.05811 | -0.11308 | 60.745 | 60.744 | 60.7862 | 60.7719 | 60.9425 | 61.0946 | 60.7446 | 60.9232 | -0.1975 | 0.000406 | -0.15633 | 0.041576
13.0156 | 122.1176 | -60.9879 | 61.0153 | 0.085224 | -0.031363 | 0.038365 | -0.07538 | 0.045421 | 0.044377 | -0.12223 | 60.7267 | 60.7348 | 60.7633 | 60.7535 | 60.9288 | 61.0809 | 60.7217 | 60.9094 | 0.098957 | -0.01763 | 0.052098 | -0.061647 | 0.059154 | 0.05811 | -0.1085 | 60.7404 | 60.7485 | 60.777 | 60.7673 | 60.9425 | 61.0946 | 60.7355 | 60.9232 | -0.20208 | 0.004984 | -0.16549 | 0.041576
14.7344 | 122.113 | -61.0199 | 60.9238 | 0.080646 | -0.022205 | 0.042944 | -0.07538 | 0.036265 | 0.048956 | -0.11765 | 60.7267 | 60.7394 | 60.7679 | 60.749 | 60.9288 | 61.0855 | 60.7217 | 60.9094 | 0.094379 | -0.008472 | 0.056677 | -0.061647 | 0.049998 | 0.062689 | -0.10392 | 60.7404 | 60.7531 | 60.7816 | 60.7627 | 60.9425 | 61.0992 | 60.7355 | 60.9232 | -0.20208 | 0.004984 | -0.16091 | 0.046155
16.4062 | 122.2549 | -60.9467 | 60.9375 | 0.076067 | -0.026784 | 0.033786 | -0.079959 | 0.036265 | 0.044377 | -0.13139 | 60.7267 | 60.7348 | 60.7725 | 60.749 | 60.9242 | 61.09 | 60.7217 | 60.9048 | 0.0898 | -0.013051 | 0.047519 | -0.066226 | 0.049998 | 0.05811 | -0.11766 | 60.7404 | 60.7485 | 60.7862 | 60.7627 | 60.9379 | 61.1038 | 60.7355 | 60.9186 | -0.1975 | 0.004984 | -0.15175 | 0.050733
18.125 | 122.2 | -61.0062 | 60.91 | 0.080646 | -0.031363 | 0.038365 | -0.084537 | 0.040843 | 0.044377 | -0.12223 | 60.7221 | 60.7394 | 60.7633 | 60.7444 | 60.9242 | 61.0809 | 60.7263 | 60.9048 | 0.094379 | -0.01763 | 0.052098 | -0.070804 | 0.054576 | 0.05811 | -0.1085 | 60.7359 | 60.7531 | 60.777 | 60.7581 | 60.9379 | 61.0946 | 60.74 | 60.9186 | -0.20208 | -0.004173 | -0.16091 | 0.036997
19.8438 | 122.2183 | -60.9421 | 60.9741 | 0.080646 | -0.026784 | 0.033786 | -0.079959 | 0.045421 | 0.048956 | -0.12223 | 60.7267 | 60.7302 | 60.7633 | 60.749 | 60.9196 | 61.0855 | 60.7263 | 60.9048 | 0.094379 | -0.013051 | 0.047519 | -0.066226 | 0.059154 | 0.062689 | -0.1085 | 60.7404 | 60.744 | 60.777 | 60.7627 | 60.9334 | 61.0992 | 60.74 | 60.9186 | -0.19292 | 0.000405 | -0.15633 | 0.036997
21.5156 | 122.1817 | -60.9879 | 60.965 | 0.089802 | -0.026784 | 0.038365 | -0.070802 | 0.040843 | 0.053534 | -0.11765 | 60.7267 | 60.7257 | 60.7679 | 60.749 | 60.9242 | 61.09 | 60.7263 | 60.9003 | 0.10354 | -0.013051 | 0.052098 | -0.057069 | 0.054576 | 0.067267 | -0.10392 | 60.7404 | 60.7394 | 60.7816 | 60.7627 | 60.9379 | 61.1038 | 60.74 | 60.914 | -0.1975 | 0.000405 | -0.15633 | 0.041576
23.25 | 122.1085 | -61.0519 | 60.9467 | 0.080646 | -0.022205 | 0.038365 | -0.079959 | 0.040843 | 0.053534 | -0.13139 | 60.7267 | 60.7348 | 60.7679 | 60.7535 | 60.9196 | 61.09 | 60.7217 | 60.9003 | 0.094379 | -0.008472 | 0.052098 | -0.066226 | 0.054576 | 0.067267 | -0.11766 | 60.7404 | 60.7485 | 60.7816 | 60.7673 | 60.9334 | 61.1038 | 60.7355 | 60.914 | -0.19292 | 0.004984 | -0.15175 | 0.046155
24.9062 | 122.1451 | -61.0565 | 60.9146 | 0.071489 | -0.031363 | 0.038365 | -0.079959 | 0.040843 | 0.044377 | -0.12223 | 60.7221 | 60.7348 | 60.7587 | 60.7535 | 60.915 | 61.0809 | 60.7171 | 60.9048 | 0.085222 | -0.01763 | 0.052098 | -0.066226 | 0.054576 | 0.05811 | -0.1085 | 60.7359 | 60.7485 | 60.7725 | 60.7673 | 60.9288 | 61.0946 | 60.7309 | 60.9186 | -0.19292 | 0.004984 | -0.15633 | 0.041576
26.6406 | 122.1863 | -60.9879 | 60.9467 | 0.085224 | -0.035942 | 0.038365 | -0.07538 | 0.036265 | 0.048956 | -0.11765 | 60.7267 | 60.7257 | 60.7679 | 60.749 | 60.9196 | 61.0855 | 60.7171 | 60.9048 | 0.098957 | -0.022209 | 0.052098 | -0.061647 | 0.049998 | 0.062689 | -0.10392 | 60.7404 | 60.7394 | 60.7816 | 60.7627 | 60.9334 | 61.0992 | 60.7309 | 60.9186 | -0.19292 | 0.009562 | -0.15175 | 0.050733
28.375 | 122.113 | -60.9924 | 61.0199 | 0.085224 | -0.022205 | 0.038365 | -0.07538 | 0.040843 | 0.044377 | -0.11765 | 60.7175 | 60.7302 | 60.7587 | 60.7444 | 60.9242 | 61.0809 | 60.7126 | 60.8957 | 0.098957 | -0.008472 | 0.052098 | -0.061647 | 0.054576 | 0.05811 | -0.10392 | 60.7313 | 60.744 | 60.7725 | 60.7581 | 60.9379 | 61.0946 | 60.7263 | 60.9094 | -0.20666 | 0.004983 | -0.16549 | 0.046154
30.0312 | 122.2183 | -61.0153 | 60.8963 | 0.076067 | -0.031363 | 0.038365 | -0.079959 | 0.040843 | 0.048956 | -0.12681 | 60.7267 | 60.7348 | 60.7587 | 60.7444 | 60.9105 | 61.0763 | 60.7126 | 60.9003 | 0.0898 | -0.01763 | 0.052098 | -0.066226 | 0.054576 | 0.062689 | -0.11308 | 60.7404 | 60.7485 | 60.7725 | 60.7581 | 60.9242 | 61.09 | 60.7263 | 60.914 | -0.18376 | 0.01414 | -0.15175 | 0.046154
31.7656 | 122.2183 | -61.0016 | 60.8871 | 0.080646 | -0.026784 | 0.038365 | -0.079959 | 0.040843 | 0.058113 | -0.12681 | 60.7313 | 60.7302 | 60.7633 | 60.7444 | 60.9196 | 61.0809 | 60.7126 | 60.8957 | 0.094379 | -0.013051 | 0.052098 | -0.066226 | 0.054576 | 0.071846 | -0.11308 | 60.745 | 60.744 | 60.777 | 60.7581 | 60.9334 | 61.0946 | 60.7263 | 60.9094 | -0.18834 | 0.018719 | -0.15633 | 0.050732
33.4844 | 122.1634 | -61.0062 | 60.9604 | 0.085224 | -0.031363 | 0.038365 | -0.079959 | 0.036265 | 0.058113 | -0.11765 | 60.7175 | 60.7348 | 60.7587 | 60.749 | 60.9196 | 61.0809 | 60.7126 | 60.8957 | 0.098957 | -0.01763 | 0.052098 | -0.066226 | 0.049998 | 0.071846 | -0.10392 | 60.7313 | 60.7485 | 60.7725 | 60.7627 | 60.9334 | 61.0946 | 60.7263 | 60.9094 | -0.20208 | 0.004983 | -0.16091 | 0.046154
35.1562 | 122.113 | -61.0657 | 60.9375 | 0.080646 | -0.026784 | 0.038365 | -0.079959 | 0.045421 | 0.053534 | -0.11765 | 60.7221 | 60.7302 | 60.7587 | 60.7444 | 60.9105 | 61.0763 | 60.7126 | 60.9003 | 0.094379 | -0.013051 | 0.052098 | -0.066226 | 0.059154 | 0.067267 | -0.10392 | 60.7359 | 60.744 | 60.7725 | 60.7581 | 60.9242 | 61.09 | 60.7263 | 60.914 | -0.18834 | 0.009562 | -0.15175 | 0.046154
36.875 | 122.1359 | -61.0016 | 60.9833 | 0.080646 | -0.031363 | 0.038365 | -0.079959 | 0.045421 | 0.048956 | -0.13139 | 60.7175 | 60.7302 | 60.7633 | 60.749 | 60.9196 | 61.0809 | 60.708 | 60.8957 | 0.094379 | -0.01763 | 0.052098 | -0.066226 | 0.059154 | 0.062689 | -0.11766 | 60.7313 | 60.744 | 60.777 | 60.7627 | 60.9334 | 61.0946 | 60.7217 | 60.9094 | -0.20208 | 0.009562 | -0.15633 | 0.055311
38.5469 | 122.2183 | -60.9238 | 60.9741 | 0.080646 | -0.026784 | 0.042944 | -0.07538 | 0.036265 | 0.039799 | -0.12681 | 60.7221 | 60.7211 | 60.7679 | 60.7444 | 60.9196 | 61.0763 | 60.7217 | 60.8957 | 0.094379 | -0.013051 | 0.056677 | -0.061647 | 0.049998 | 0.053532 | -0.11308 | 60.7359 | 60.7348 | 60.7816 | 60.7581 | 60.9334 | 61.09 | 60.7355 | 60.9094 | -0.1975 | 0.000406 | -0.15175 | 0.046155
40.2812 | 122.2275 | -60.9741 | 60.9741 | 0.076067 | -0.022205 | 0.042944 | -0.079959 | 0.036265 | 0.039799 | -0.12223 | 60.7221 | 60.7165 | 60.7633 | 60.7398 | 60.915 | 61.0763 | 60.7171 | 60.8911 | 0.0898 | -0.008472 | 0.056677 | -0.066226 | 0.049998 | 0.053532 | -0.1085 | 60.7359 | 60.7302 | 60.777 | 60.7535 | 60.9288 | 61.09 | 60.7309 | 60.9048 | -0.19292 | 0.004984 | -0.15175 | 0.046154
42 | 122.1909 | -60.997 | 60.9055 | 0.071489 | -0.022205 | 0.042944 | -0.070802 | 0.045421 | 0.044377 | -0.12223 | 60.7038 | 60.7257 | 60.7587 | 60.7444 | 60.9105 | 61.0717 | 60.708 | 60.8957 | 0.085222 | -0.008472 | 0.056677 | -0.057069 | 0.059154 | 0.05811 | -0.1085 | 60.7175 | 60.7394 | 60.7725 | 60.7581 | 60.9242 | 61.0855 | 60.7217 | 60.9094 | -0.20666 | -0.004173 | -0.15175 | 0.050733
43.6562 | 122.2137 | -60.965 | 60.965 | 0.080646 | -0.026784 | 0.038365 | -0.07538 | 0.036265 | 0.044377 | -0.12681 | 60.7175 | 60.7257 | 60.7633 | 60.7352 | 60.915 | 61.0809 | 60.7126 | 60.8911 | 0.094379 | -0.013051 | 0.052098 | -0.061647 | 0.049998 | 0.05811 | -0.11308 | 60.7313 | 60.7394 | 60.777 | 60.749 | 60.9288 | 61.0946 | 60.7263 | 60.9048 | -0.1975 | 0.004983 | -0.15175 | 0.050732
45.375 | 122.0901 | -60.965 | 61.0199 | 0.080646 | -0.026784 | 0.038365 | -0.07538 | 0.031687 | 0.039799 | -0.12223 | 60.713 | 60.7257 | 60.7587 | 60.7444 | 60.9105 | 61.0763 | 60.7126 | 60.8957 | 0.094379 | -0.013051 | 0.052098 | -0.061647 | 0.04542 | 0.053532 | -0.1085 | 60.7267 | 60.7394 | 60.7725 | 60.7581 | 60.9242 | 61.09 | 60.7263 | 60.9094 | -0.1975 | 0.000405 | -0.15175 | 0.046154
47.0312 | 122.2137 | -60.9283 | 60.9375 | 0.085224 | -0.031363 | 0.033786 | -0.07538 | 0.031687 | 0.044377 | -0.12223 | 60.713 | 60.7211 | 60.7587 | 60.7398 | 60.9105 | 61.0763 | 60.708 | 60.8911 | 0.098957 | -0.01763 | 0.047519 | -0.061647 | 0.04542 | 0.05811 | -0.1085 | 60.7267 | 60.7348 | 60.7725 | 60.7535 | 60.9242 | 61.09 | 60.7217 | 60.9048 | -0.1975 | 0.004984 | -0.15175 | 0.050733
48.75 | 122.168 | -60.9695 | 60.9375 | 0.080646 | -0.022205 | 0.042944 | -0.07538 | 0.036265 | 0.048956 | -0.12681 | 60.713 | 60.7165 | 60.7541 | 60.7307 | 60.9059 | 61.0717 | 60.7171 | 60.8865 | 0.094379 | -0.008472 | 0.056677 | -0.061647 | 0.049998 | 0.062689 | -0.11308 | 60.7267 | 60.7302 | 60.7679 | 60.7444 | 60.9196 | 61.0855 | 60.7309 | 60.9003 | -0.19292 | -0.004173 | -0.15175 | 0.036998
50.4219 | 122.0901 | -61.0291 | 60.9055 | 0.080646 | -0.022205 | 0.038365 | -0.070802 | 0.045421 | 0.053534 | -0.12681 | 60.7084 | 60.7211 | 60.7541 | 60.7352 | 60.9059 | 61.0717 | 60.708 | 60.8911 | 0.094379 | -0.008472 | 0.052098 | -0.057069 | 0.059154 | 0.067267 | -0.11308 | 60.7221 | 60.7348 | 60.7679 | 60.749 | 60.9196 | 61.0855 | 60.7217 | 60.9048 | -0.1975 | 0.000405 | -0.15175 | 0.046155
52.0938 | 122.1405 | -61.0245 | 60.8871 | 0.085224 | -0.022205 | 0.042944 | -0.07538 | 0.045421 | 0.048956 | -0.12681 | 60.7084 | 60.7257 | 60.7587 | 60.7307 | 60.9013 | 61.0717 | 60.6988 | 60.8865 | 0.098957 | -0.008472 | 0.056677 | -0.061647 | 0.059154 | 0.062689 | -0.11308 | 60.7221 | 60.7394 | 60.7725 | 60.7444 | 60.915 | 61.0855 | 60.7126 | 60.9003 | -0.19292 | 0.009562 | -0.14259 | 0.05989
53.8281 | 122.1451 | -60.9741 | 60.9375 | 0.085224 | -0.031363 | 0.038365 | -0.070802 | 0.040843 | 0.053534 | -0.12223 | 60.7038 | 60.7165 | 60.7541 | 60.7352 | 60.9105 | 61.0672 | 60.7034 | 60.8865 | 0.098957 | -0.01763 | 0.052098 | -0.057069 | 0.054576 | 0.067267 | -0.1085 | 60.7175 | 60.7302 | 60.7679 | 60.749 | 60.9242 | 61.0809 | 60.7171 | 60.9003 | -0.20666 | 0.000405 | -0.15633 | 0.050733
55.4844 | 122.2092 | -60.9375 | 60.9375 | 0.080646 | -0.040521 | 0.038365 | -0.07538 | 0.036265 | 0.048956 | -0.12223 | 60.713 | 60.7257 | 60.7587 | 60.7352 | 60.9013 | 61.0672 | 60.6943 | 60.8911 | 0.094379 | -0.026788 | 0.052098 | -0.061647 | 0.049998 | 0.062689 | -0.1085 | 60.7267 | 60.7394 | 60.7725 | 60.749 | 60.915 | 61.0809 | 60.708 | 60.9048 | -0.18834 | 0.018719 | -0.14259 | 0.064468
57.2031 | 122.1771 | -60.9879 | 60.9421 | 0.085224 | -0.031363 | 0.033786 | -0.070802 | 0.031687 | 0.048956 | -0.12223 | 60.7175 | 60.7119 | 60.7496 | 60.7352 | 60.9013 | 61.0626 | 60.7034 | 60.8865 | 0.098957 | -0.01763 | 0.047519 | -0.057069 | 0.04542 | 0.062689 | -0.1085 | 60.7313 | 60.7256 | 60.7633 | 60.749 | 60.915 | 61.0763 | 60.7171 | 60.9003 | -0.18377 | 0.01414 | -0.15175 | 0.046154
58.9219 | 122.0993 | -61.0336 | 60.9375 | 0.085224 | -0.026784 | 0.038365 | -0.07538 | 0.040843 | 0.058113 | -0.12223 | 60.7084 | 60.7211 | 60.7587 | 60.7398 | 60.9013 | 61.0626 | 60.6988 | 60.882 | 0.098957 | -0.013051 | 0.052098 | -0.061647 | 0.054576 | 0.071846 | -0.1085 | 60.7221 | 60.7348 | 60.7725 | 60.7535 | 60.915 | 61.0763 | 60.7126 | 60.8957 | -0.19292 | 0.009562 | -0.14259 | 0.05989
60.6562 | 122.1909 | -60.997 | 60.9009 | 0.076067 | -0.035942 | 0.033786 | -0.07538 | 0.036265 | 0.053534 | -0.12223 | 60.7084 | 60.7165 | 60.7496 | 60.7352 | 60.9059 | 61.0626 | 60.6943 | 60.882 | 0.0898 | -0.022209 | 0.047519 | -0.061647 | 0.049998 | 0.067267 | -0.1085 | 60.7221 | 60.7302 | 60.7633 | 60.749 | 60.9196 | 61.0763 | 60.708 | 60.8957 | -0.1975 | 0.01414 | -0.15633 | 0.055311
62.3281 | 122.0993 | -60.9741 | 60.9924 | 0.085224 | -0.031363 | 0.038365 | -0.084537 | 0.036265 | 0.044377 | -0.11765 | 60.6992 | 60.7211 | 60.7496 | 60.7352 | 60.9013 | 61.0626 | 60.6988 | 60.8865 | 0.098957 | -0.01763 | 0.052098 | -0.070804 | 0.049998 | 0.05811 | -0.10392 | 60.713 | 60.7348 | 60.7633 | 60.749 | 60.915 | 61.0763 | 60.7126 | 60.9003 | -0.20208 | 0.000405 | -0.15175 | 0.050733
64.0469 | 122.168 | -60.9329 | 60.9558 | 0.071489 | -0.026784 | 0.038365 | -0.070802 | 0.036265 | 0.044377 | -0.12681 | 60.7038 | 60.7119 | 60.7496 | 60.7352 | 60.9105 | 61.0672 | 60.6988 | 60.882 | 0.085222 | -0.013051 | 0.052098 | -0.057069 | 0.049998 | 0.05811 | -0.11308 | 60.7175 | 60.7256 | 60.7633 | 60.749 | 60.9242 | 61.0809 | 60.7126 | 60.8957 | -0.20666 | 0.004984 | -0.16091 | 0.050733
65.7969 | 122.0535 | -61.0016 | 60.9192 | 0.076067 | -0.026784 | 0.047522 | -0.084537 | 0.045421 | 0.048956 | -0.12223 | 60.7038 | 60.7165 | 60.7496 | 60.7352 | 60.8967 | 61.0626 | 60.6943 | 60.8728 | 0.0898 | -0.013051 | 0.061255 | -0.070804 | 0.059154 | 0.062689 | -0.1085 | 60.7175 | 60.7302 | 60.7633 | 60.749 | 60.9105 | 61.0763 | 60.708 | 60.8865 | -0.19292 | 0.009562 | -0.14717 | 0.055311
67.4531 | 122.081 | -61.0016 | 60.9146 | 0.085224 | -0.026784 | 0.038365 | -0.07538 | 0.040843 | 0.048956 | -0.12223 | 60.7084 | 60.7211 | 60.745 | 60.7261 | 60.9105 | 61.0626 | 60.7034 | 60.8728 | 0.098957 | -0.013051 | 0.052098 | -0.061647 | 0.054576 | 0.062689 | -0.1085 | 60.7221 | 60.7348 | 60.7587 | 60.7398 | 60.9242 | 61.0763 | 60.7171 | 60.8865 | -0.20208 | 0.004983 | -0.16548 | 0.041576
69.1719 | 122.2092 | -60.9283 | 60.9467 | 0.085224 | -0.035942 | 0.042944 | -0.079959 | 0.040843 | 0.048956 | -0.11765 | 60.6992 | 60.7211 | 60.7496 | 60.7307 | 60.9105 | 61.058 | 60.7034 | 60.8865 | 0.098957 | -0.022209 | 0.056677 | -0.066226 | 0.054576 | 0.062689 | -0.10392 | 60.713 | 60.7348 | 60.7633 | 60.7444 | 60.9242 | 61.0717 | 60.7171 | 60.9003 | -0.21123 | -0.004174 | -0.16091 | 0.046154
70.8906 | 122.0535 | -61.0336 | 60.9238 | 0.080646 | -0.031363 | 0.038365 | -0.079959 | 0.049999 | 0.053534 | -0.13139 | 60.7038 | 60.7165 | 60.7496 | 60.7352 | 60.8876 | 61.058 | 60.6851 | 60.8774 | 0.094379 | -0.01763 | 0.052098 | -0.066226 | 0.063732 | 0.067267 | -0.11766 | 60.7175 | 60.7302 | 60.7633 | 60.749 | 60.9013 | 61.0717 | 60.6988 | 60.8911 | -0.18377 | 0.018719 | -0.13802 | 0.064468
72.6094 | 122.0718 | -61.0474 | 60.9192 | 0.085224 | -0.031363 | 0.038365 | -0.07538 | 0.036265 | 0.048956 | -0.12681 | 60.7038 | 60.7165 | 60.7541 | 60.7352 | 60.8922 | 61.058 | 60.6897 | 60.8774 | 0.098957 | -0.01763 | 0.052098 | -0.061647 | 0.049998 | 0.062689 | -0.11308 | 60.7175 | 60.7302 | 60.7679 | 60.749 | 60.9059 | 61.0717 | 60.7034 | 60.8911 | -0.18834 | 0.01414 | -0.13802 | 0.064468
74.2656 | 122.1405 | -60.9833 | 60.91 | 0.089802 | -0.026784 | 0.038365 | -0.07538 | 0.036265 | 0.053534 | -0.12681 | 60.6992 | 60.7119 | 60.7541 | 60.7307 | 60.8967 | 61.0626 | 60.6943 | 60.8774 | 0.10354 | -0.013051 | 0.052098 | -0.061647 | 0.049998 | 0.067267 | -0.11308 | 60.713 | 60.7256 | 60.7679 | 60.7444 | 60.9105 | 61.0763 | 60.708 | 60.8911 | -0.1975 | 0.004983 | -0.14259 | 0.05989
76 | 122.1909 | -60.8917 | 60.965 | 0.080646 | -0.035942 | 0.038365 | -0.066223 | 0.036265 | 0.044377 | -0.11765 | 60.7084 | 60.7073 | 60.7496 | 60.7215 | 60.8967 | 61.058 | 60.6943 | 60.882 | 0.094379 | -0.022209 | 0.052098 | -0.05249 | 0.049998 | 0.05811 | -0.10392 | 60.7221 | 60.7211 | 60.7633 | 60.7352 | 60.9105 | 61.0717 | 60.708 | 60.8957 | -0.18834 | 0.01414 | -0.14717 | 0.055311
77.7344 | 122.1863 | -60.9833 | 60.8231 | 0.076067 | -0.026784 | 0.038365 | -0.066223 | 0.045421 | 0.048956 | -0.11765 | 60.7038 | 60.7073 | 60.745 | 60.7261 | 60.8967 | 61.0626 | 60.6897 | 60.8682 | 0.0898 | -0.013051 | 0.052098 | -0.05249 | 0.059154 | 0.062689 | -0.10392 | 60.7175 | 60.7211 | 60.7587 | 60.7398 | 60.9105 | 61.0763 | 60.7034 | 60.882 | -0.19292 | 0.01414 | -0.15175 | 0.055311
79.3906 | 122.1817 | -61.0016 | 60.8688 | 0.080646 | -0.031363 | 0.033786 | -0.07538 | 0.036265 | 0.053534 | -0.11765 | 60.6901 | 60.7073 | 60.7404 | 60.7307 | 60.8922 | 61.0626 | 60.6988 | 60.8682 | 0.094379 | -0.01763 | 0.047519 | -0.061647 | 0.049998 | 0.067267 | -0.10392 | 60.7038 | 60.7211 | 60.7541 | 60.7444 | 60.9059 | 61.0763 | 60.7126 | 60.882 | -0.20208 | -0.008752 | -0.15175 | 0.041577
81.0625 | 122.1451 | -60.9787 | 60.9283 | 0.080646 | -0.035942 | 0.042944 | -0.07538 | 0.031687 | 0.048956 | -0.11765 | 60.7038 | 60.7073 | 60.745 | 60.7307 | 60.8922 | 61.0534 | 60.6943 | 60.8774 | 0.094379 | -0.022209 | 0.056677 | -0.061647 | 0.04542 | 0.062689 | -0.10392 | 60.7175 | 60.7211 | 60.7587 | 60.7444 | 60.9059 | 61.0672 | 60.708 | 60.8911 | -0.18834 | 0.009562 | -0.14717 | 0.050733
82.7812 | 122.1909 | -60.997 | 60.8688 | 0.080646 | -0.026784 | 0.033786 | -0.07538 | 0.045421 | 0.044377 | -0.12223 | 60.6947 | 60.7073 | 60.7404 | 60.7307 | 60.8876 | 61.058 | 60.6897 | 60.8636 | 0.094379 | -0.013051 | 0.047519 | -0.061647 | 0.059154 | 0.05811 | -0.1085 | 60.7084 | 60.7211 | 60.7541 | 60.7444 | 60.9013 | 61.0717 | 60.7034 | 60.8774 | -0.19292 | 0.004983 | -0.14717 | 0.050733
84.4375 | 122.1588 | -60.9375 | 60.9375 | 0.080646 | -0.031363 | 0.038365 | -0.079959 | 0.040843 | 0.048956 | -0.11765 | 60.6947 | 60.6982 | 60.745 | 60.7261 | 60.8922 | 61.058 | 60.6897 | 60.8682 | 0.094379 | -0.01763 | 0.052098 | -0.066226 | 0.054576 | 0.062689 | -0.10392 | 60.7084 | 60.7119 | 60.7587 | 60.7398 | 60.9059 | 61.0717 | 60.7034 | 60.882 | -0.1975 | 0.004983 | -0.14717 | 0.055311
86.1562 | 122.1954 | -60.9009 | 60.9283 | 0.076067 | -0.031363 | 0.033786 | -0.070802 | 0.036265 | 0.048956 | -0.12223 | 60.6947 | 60.7073 | 60.7404 | 60.7307 | 60.8967 | 61.0534 | 60.6943 | 60.8728 | 0.0898 | -0.01763 | 0.047519 | -0.057069 | 0.049998 | 0.062689 | -0.1085 | 60.7084 | 60.7211 | 60.7541 | 60.7444 | 60.9105 | 61.0672 | 60.708 | 60.8865 | -0.20208 | 0.000405 | -0.15633 | 0.046155
87.875 | 122.0947 | -61.0428 | 60.878 | 0.085224 | -0.035942 | 0.038365 | -0.070802 | 0.040843 | 0.044377 | -0.12223 | 60.7038 | 60.7119 | 60.7404 | 60.7215 | 60.8876 | 61.0534 | 60.6851 | 60.8636 | 0.098957 | -0.022209 | 0.052098 | -0.057069 | 0.054576 | 0.05811 | -0.1085 | 60.7175 | 60.7256 | 60.7541 | 60.7352 | 60.9013 | 61.0672 | 60.6988 | 60.8774 | -0.18377 | 0.018719 | -0.14717 | 0.055312
89.5469 | 122.168 | -61.0016 | 60.8826 | 0.085224 | -0.026784 | 0.038365 | -0.070802 | 0.040843 | 0.053534 | -0.12223 | 60.6992 | 60.7119 | 60.745 | 60.7261 | 60.8876 | 61.0488 | 60.6805 | 60.8728 | 0.098957 | -0.013051 | 0.052098 | -0.057069 | 0.054576 | 0.067267 | -0.1085 | 60.713 | 60.7256 | 60.7587 | 60.7398 | 60.9013 | 61.0626 | 60.6943 | 60.8865 | -0.18834 | 0.018718 | -0.1426 | 0.064468
91.2812 | 122.1542 | -60.9924 | 60.8505 | 0.085224 | -0.035942 | 0.029208 | -0.07538 | 0.040843 | 0.048956 | -0.11765 | 60.6947 | 60.7073 | 60.7404 | 60.7261 | 60.8967 | 61.0488 | 60.6897 | 60.8682 | 0.098957 | -0.022209 | 0.042941 | -0.061647 | 0.054576 | 0.062689 | -0.10392 | 60.7084 | 60.7211 | 60.7541 | 60.7398 | 60.9105 | 61.0626 | 60.7034 | 60.882 | -0.20208 | 0.004983 | -0.15633 | 0.050733
93 | 122.0718 | -61.0016 | 60.9055 | 0.080646 | -0.026784 | 0.042944 | -0.070802 | 0.040843 | 0.048956 | -0.11765 | 60.6901 | 60.7119 | 60.745 | 60.7215 | 60.8922 | 61.0443 | 60.6897 | 60.8591 | 0.094379 | -0.013051 | 0.056677 | -0.057069 | 0.054576 | 0.062689 | -0.10392 | 60.7038 | 60.7256 | 60.7587 | 60.7352 | 60.9059 | 61.058 | 60.7034 | 60.8728 | -0.20208 | 0.000404 | -0.14717 | 0.055311
94.7188 | 122.1725 | -60.9787 | 60.8597 | 0.085224 | -0.022205 | 0.042944 | -0.079959 | 0.036265 | 0.039799 | -0.11765 | 60.6992 | 60.7028 | 60.7404 | 60.7169 | 60.8876 | 61.0443 | 60.6805 | 60.8682 | 0.098957 | -0.008472 | 0.056677 | -0.066226 | 0.049998 | 0.053532 | -0.10392 | 60.713 | 60.7165 | 60.7541 | 60.7306 | 60.9013 | 61.058 | 60.6943 | 60.882 | -0.18834 | 0.018718 | -0.14717 | 0.05989
96.3906 | 122.0444 | -60.9695 | 60.965 | 0.080646 | -0.026784 | 0.038365 | -0.079959 | 0.045421 | 0.053534 | -0.12681 | 60.6947 | 60.7119 | 60.745 | 60.7261 | 60.8922 | 61.0488 | 60.6851 | 60.8682 | 0.094379 | -0.013051 | 0.052098 | -0.066226 | 0.059154 | 0.067267 | -0.11308 | 60.7084 | 60.7256 | 60.7587 | 60.7398 | 60.9059 | 61.0626 | 60.6988 | 60.882 | -0.1975 | 0.009562 | -0.14717 | 0.05989
98.1094 | 122.0901 | -60.9787 | 60.9238 | 0.089802 | -0.026784 | 0.042944 | -0.070802 | 0.036265 | 0.053534 | -0.12223 | 60.6992 | 60.7028 | 60.7404 | 60.7215 | 60.8922 | 61.0488 | 60.6805 | 60.8636 | 0.10354 | -0.013051 | 0.056677 | -0.057069 | 0.049998 | 0.067267 | -0.1085 | 60.713 | 60.7165 | 60.7541 | 60.7352 | 60.9059 | 61.0626 | 60.6943 | 60.8774 | -0.19292 | 0.018718 | -0.15175 | 0.05989
99.8281 | 122.0947 | -60.9558 | 60.9375 | 0.089802 | -0.031363 | 0.033786 | -0.070802 | 0.040843 | 0.048956 | -0.12681 | 60.6947 | 60.7028 | 60.7358 | 60.7169 | 60.8784 | 61.0488 | 60.6759 | 60.8636 | 0.10354 | -0.01763 | 0.047519 | -0.057069 | 0.054576 | 0.062689 | -0.11308 | 60.7084 | 60.7165 | 60.7496 | 60.7306 | 60.8922 | 61.0626 | 60.6897 | 60.8774 | -0.18377 | 0.018718 | -0.14259 | 0.05989
101.5 | 122.0901 | -60.9741 | 60.9695 | 0.080646 | -0.026784 | 0.038365 | -0.079959 | 0.045421 | 0.048956 | -0.12681 | 60.6901 | 60.6982 | 60.7404 | 60.7169 | 60.8922 | 61.0488 | 60.6805 | 60.8545 | 0.094379 | -0.013051 | 0.052098 | -0.066226 | 0.059154 | 0.062689 | -0.11308 | 60.7038 | 60.7119 | 60.7541 | 60.7306 | 60.9059 | 61.0626 | 60.6943 | 60.8682 | -0.20208 | 0.009561 | -0.15175 | 0.05989
103.2031 | 122.0901 | -60.9741 | 60.91 | 0.080646 | -0.031363 | 0.033786 | -0.070802 | 0.040843 | 0.044377 | -0.12223 | 60.6855 | 60.6982 | 60.7404 | 60.7261 | 60.883 | 61.0351 | 60.6805 | 60.8636 | 0.094379 | -0.01763 | 0.047519 | -0.057069 | 0.054576 | 0.05811 | -0.1085 | 60.6992 | 60.7119 | 60.7541 | 60.7398 | 60.8967 | 61.0488 | 60.6943 | 60.8774 | -0.1975 | 0.004983 | -0.14259 | 0.05989
104.9219 | 122.1725 | -60.9879 | 60.8459 | 0.085224 | -0.026784 | 0.033786 | -0.070802 | 0.040843 | 0.053534 | -0.12223 | 60.6901 | 60.6982 | 60.7404 | 60.7169 | 60.8876 | 61.0397 | 60.6759 | 60.8636 | 0.098957 | -0.013051 | 0.047519 | -0.057069 | 0.054576 | 0.067267 | -0.1085 | 60.7038 | 60.7119 | 60.7541 | 60.7306 | 60.9013 | 61.0534 | 60.6897 | 60.8774 | -0.1975 | 0.014139 | -0.14717 | 0.064468
106.6562 | 122.1725 | -60.9192 | 60.9238 | 0.076067 | -0.026784 | 0.033786 | -0.07538 | 0.045421 | 0.053534 | -0.11765 | 60.6901 | 60.7028 | 60.7313 | 60.7078 | 60.8876 | 61.0397 | 60.6851 | 60.8636 | 0.0898 | -0.013051 | 0.047519 | -0.061647 | 0.059154 | 0.067267 | -0.10392 | 60.7038 | 60.7165 | 60.745 | 60.7215 | 60.9013 | 61.0534 | 60.6988 | 60.8774 | -0.1975 | 0.004983 | -0.15633 | 0.046155
108.3906 | 122.1359 | -60.9055 | 60.9238 | 0.089802 | -0.031363 | 0.038365 | -0.079959 | 0.040843 | 0.039799 | -0.11765 | 60.6947 | 60.6982 | 60.7313 | 60.7123 | 60.8876 | 61.0488 | 60.6851 | 60.8636 | 0.10354 | -0.01763 | 0.052098 | -0.066226 | 0.054576 | 0.053532 | -0.10392 | 60.7084 | 60.7119 | 60.745 | 60.7261 | 60.9013 | 61.0626 | 60.6988 | 60.8774 | -0.19292 | 0.009562 | -0.15633 | 0.046155
110.0469 | 122.081 | -60.9421 | 60.9695 | 0.089802 | -0.031363 | 0.042944 | -0.079959 | 0.031687 | 0.044377 | -0.11765 | 60.6947 | 60.7028 | 60.7404 | 60.7169 | 60.8876 | 61.0443 | 60.6897 | 60.8636 | 0.10354 | -0.01763 | 0.056677 | -0.066226 | 0.04542 | 0.05811 | -0.10392 | 60.7084 | 60.7165 | 60.7541 | 60.7306 | 60.9013 | 61.058 | 60.7034 | 60.8774 | -0.19292 | 0.004983 | -0.14717 | 0.050733
111.7812 | 122.1359 | -60.9512 | 60.8643 | 0.085224 | -0.026784 | 0.038365 | -0.070802 | 0.040843 | 0.053534 | -0.12223 | 60.6855 | 60.6936 | 60.7267 | 60.7169 | 60.883 | 61.0351 | 60.6759 | 60.8545 | 0.098957 | -0.013051 | 0.052098 | -0.057069 | 0.054576 | 0.067267 | -0.1085 | 60.6992 | 60.7073 | 60.7404 | 60.7306 | 60.8967 | 61.0488 | 60.6897 | 60.8682 | -0.1975 | 0.009561 | -0.15633 | 0.050733
113.4531 | 122.1634 | -60.9192 | 60.9146 | 0.089802 | -0.031363 | 0.033786 | -0.07538 | 0.036265 | 0.044377 | -0.11765 | 60.6901 | 60.6936 | 60.7358 | 60.7123 | 60.883 | 61.0397 | 60.6851 | 60.8545 | 0.10354 | -0.01763 | 0.047519 | -0.061647 | 0.049998 | 0.05811 | -0.10392 | 60.7038 | 60.7073 | 60.7496 | 60.7261 | 60.8967 | 61.0534 | 60.6988 | 60.8682 | -0.19292 | 0.004983 | -0.14717 | 0.050734
115.1719 | 122.049 | -60.997 | 60.8734 | 0.094381 | -0.031363 | 0.038365 | -0.066223 | 0.036265 | 0.048956 | -0.11765 | 60.6901 | 60.7073 | 60.7313 | 60.7169 | 60.8876 | 61.0397 | 60.6805 | 60.8499 | 0.10811 | -0.01763 | 0.052098 | -0.05249 | 0.049998 | 0.062689 | -0.10392 | 60.7038 | 60.7211 | 60.745 | 60.7306 | 60.9013 | 61.0534 | 60.6943 | 60.8636 | -0.1975 | 0.009561 | -0.15633 | 0.050733
116.8906 | 122.1085 | -60.9558 | 60.9329 | 0.085224 | -0.035942 | 0.033786 | -0.079959 | 0.031687 | 0.048956 | -0.12681 | 60.6855 | 60.689 | 60.7404 | 60.7169 | 60.8784 | 61.0397 | 60.6805 | 60.8545 | 0.098957 | -0.022209 | 0.047519 | -0.066226 | 0.04542 | 0.062689 | -0.11308 | 60.6992 | 60.7028 | 60.7541 | 60.7306 | 60.8922 | 61.0534 | 60.6943 | 60.8682 | -0.19292 | 0.004983 | -0.13802 | 0.05989
118.6094 | 122.0993 | -60.9467 | 60.8871 | 0.089802 | -0.031363 | 0.033786 | -0.07538 | 0.031687 | 0.039799 | -0.12223 | 60.6901 | 60.6936 | 60.7358 | 60.7078 | 60.8784 | 61.0443 | 60.6805 | 60.8545 | 0.10354 | -0.01763 | 0.047519 | -0.061647 | 0.04542 | 0.053532 | -0.1085 | 60.7038 | 60.7073 | 60.7496 | 60.7215 | 60.8922 | 61.058 | 60.6943 | 60.8682 | -0.18834 | 0.009561 | -0.14259 | 0.055312
120.2656 | 122.0261 | -60.9192 | 60.9512 | 0.094381 | -0.035942 | 0.038365 | -0.07538 | 0.036265 | 0.044377 | -0.11765 | 60.6901 | 60.6936 | 60.7313 | 60.7169 | 60.8738 | 61.0397 | 60.6805 | 60.8545 | 0.10811 | -0.022209 | 0.052098 | -0.061647 | 0.049998 | 0.05811 | -0.10392 | 60.7038 | 60.7073 | 60.745 | 60.7306 | 60.8876 | 61.0534 | 60.6943 | 60.8682 | -0.18377 | 0.009561 | -0.1426 | 0.050733
121.9219 | 122.1085 | -60.9558 | 60.8688 | 0.085224 | -0.035942 | 0.029208 | -0.070802 | 0.040843 | 0.044377 | -0.12223 | 60.6901 | 60.6936 | 60.7313 | 60.7123 | 60.8738 | 61.0351 | 60.6714 | 60.8499 | 0.098957 | -0.022209 | 0.042941 | -0.057069 | 0.054576 | 0.05811 | -0.1085 | 60.7038 | 60.7073 | 60.745 | 60.7261 | 60.8876 | 61.0488 | 60.6851 | 60.8636 | -0.18377 | 0.018718 | -0.1426 | 0.05989
123.6406 | 122.1313 | -60.9375 | 60.9238 | 0.085224 | -0.031363 | 0.029208 | -0.079959 | 0.031687 | 0.044377 | -0.12681 | 60.6855 | 60.6982 | 60.7313 | 60.7169 | 60.883 | 61.0397 | 60.6805 | 60.8545 | 0.098957 | -0.01763 | 0.042941 | -0.066226 | 0.04542 | 0.05811 | -0.11308 | 60.6992 | 60.7119 | 60.745 | 60.7306 | 60.8967 | 61.0534 | 60.6943 | 60.8682 | -0.1975 | 0.004983 | -0.15175 | 0.050733
125.2969 | 122.1634 | -60.9924 | 60.8231 | 0.085224 | -0.031363 | 0.038365 | -0.061645 | 0.036265 | 0.039799 | -0.12223 | 60.6855 | 60.689 | 60.7267 | 60.7169 | 60.8738 | 61.0397 | 60.6759 | 60.8453 | 0.098957 | -0.01763 | 0.052098 | -0.047912 | 0.049998 | 0.053532 | -0.1085 | 60.6992 | 60.7028 | 60.7404 | 60.7306 | 60.8876 | 61.0534 | 60.6897 | 60.8591 | -0.18835 | 0.009561 | -0.14717 | 0.050733
127.0312 | 122.1634 | -60.8826 | 60.9329 | 0.094381 | -0.031363 | 0.038365 | -0.079959 | 0.040843 | 0.048956 | -0.12223 | 60.6763 | 60.6982 | 60.7313 | 60.7123 | 60.8738 | 61.0351 | 60.6805 | 60.8545 | 0.10811 | -0.01763 | 0.052098 | -0.066226 | 0.054576 | 0.062689 | -0.1085 | 60.6901 | 60.7119 | 60.745 | 60.7261 | 60.8876 | 61.0488 | 60.6943 | 60.8682 | -0.1975 | -0.004174 | -0.1426 | 0.050733
128.7656 | 122.1497 | -60.9558 | 60.8322 | 0.089802 | -0.026784 | 0.033786 | -0.070802 | 0.040843 | 0.048956 | -0.12223 | 60.6809 | 60.689 | 60.7313 | 60.7078 | 60.8738 | 61.0305 | 60.6805 | 60.8407 | 0.10354 | -0.013051 | 0.047519 | -0.057069 | 0.054576 | 0.062689 | -0.1085 | 60.6947 | 60.7028 | 60.745 | 60.7215 | 60.8876 | 61.0443 | 60.6943 | 60.8545 | -0.19292 | 0.000404 | -0.1426 | 0.050733
130.4375 | 122.1451 | -60.9238 | 60.8826 | 0.089802 | -0.022205 | 0.033786 | -0.070802 | 0.036265 | 0.039799 | -0.12223 | 60.6763 | 60.689 | 60.7313 | 60.7078 | 60.8784 | 61.0305 | 60.6714 | 60.8545 | 0.10354 | -0.008472 | 0.047519 | -0.057069 | 0.049998 | 0.053532 | -0.1085 | 60.6901 | 60.7028 | 60.745 | 60.7215 | 60.8922 | 61.0443 | 60.6851 | 60.8682 | -0.20208 | 0.004983 | -0.14717 | 0.05989
132.1719 | 122.1268 | -60.9192 | 60.8917 | 0.089802 | -0.022205 | 0.033786 | -0.070802 | 0.036265 | 0.048956 | -0.12681 | 60.6809 | 60.6844 | 60.7267 | 60.7032 | 60.8738 | 61.0443 | 60.6714 | 60.8545 | 0.10354 | -0.008472 | 0.047519 | -0.057069 | 0.049998 | 0.062689 | -0.11308 | 60.6947 | 60.6982 | 60.7404 | 60.7169 | 60.8876 | 61.058 | 60.6851 | 60.8682 | -0.19292 | 0.009561 | -0.14717 | 0.055312
133.8906 | 122.0856 | -60.9375 | 60.8871 | 0.089802 | -0.031363 | 0.033786 | -0.07538 | 0.036265 | 0.048956 | -0.11765 | 60.6809 | 60.6844 | 60.7221 | 60.7078 | 60.8693 | 61.0397 | 60.6668 | 60.8591 | 0.10354 | -0.01763 | 0.047519 | -0.061647 | 0.049998 | 0.062689 | -0.10392 | 60.6947 | 60.6982 | 60.7358 | 60.7215 | 60.883 | 61.0534 | 60.6805 | 60.8728 | -0.18835 | 0.014139 | -0.14717 | 0.055312
135.5625 | 122.0261 | -61.0062 | 60.8917 | 0.085224 | -0.031363 | 0.042944 | -0.07538 | 0.045421 | 0.044377 | -0.11765 | 60.6901 | 60.689 | 60.7267 | 60.7078 | 60.8647 | 61.0305 | 60.6576 | 60.8499 | 0.098957 | -0.01763 | 0.056677 | -0.061647 | 0.059154 | 0.05811 | -0.10392 | 60.7038 | 60.7028 | 60.7404 | 60.7215 | 60.8784 | 61.0443 | 60.6714 | 60.8636 | -0.17461 | 0.032453 | -0.13802 | 0.069047
137.2969 | 121.9986 | -60.9833 | 60.8597 | 0.080646 | -0.022205 | 0.038365 | -0.061645 | 0.045421 | 0.048956 | -0.11765 | 60.6763 | 60.689 | 60.7267 | 60.7078 | 60.8693 | 61.0351 | 60.6714 | 60.8545 | 0.094379 | -0.008472 | 0.052098 | -0.047912 | 0.059154 | 0.062689 | -0.10392 | 60.6901 | 60.7028 | 60.7404 | 60.7215 | 60.883 | 61.0488 | 60.6851 | 60.8682 | -0.19292 | 0.004983 | -0.1426 | 0.055312
139.0156 | 122.0306 | -60.9283 | 60.9512 | 0.094381 | -0.022205 | 0.038365 | -0.070802 | 0.036265 | 0.044377 | -0.12223 | 60.6718 | 60.6844 | 60.7221 | 60.7032 | 60.8738 | 61.0305 | 60.6622 | 60.8545 | 0.10811 | -0.008472 | 0.052098 | -0.057069 | 0.049998 | 0.05811 | -0.1085 | 60.6855 | 60.6982 | 60.7358 | 60.7169 | 60.8876 | 61.0443 | 60.6759 | 60.8682 | -0.20208 | 0.009561 | -0.15175 | 0.059891
140.75 | 122.0123 | -60.9879 | 60.8871 | 0.085224 | -0.026784 | 0.033786 | -0.070802 | 0.040843 | 0.053534 | -0.12223 | 60.6855 | 60.6844 | 60.7221 | 60.7032 | 60.8738 | 61.0305 | 60.6668 | 60.8407 | 0.098957 | -0.013051 | 0.047519 | -0.057069 | 0.054576 | 0.067267 | -0.1085 | 60.6992 | 60.6982 | 60.7358 | 60.7169 | 60.8876 | 61.0443 | 60.6805 | 60.8545 | -0.18835 | 0.018718 | -0.15175 | 0.055312
142.4219 | 122.0718 | -60.9192 | 60.9238 | 0.085224 | -0.031363 | 0.029208 | -0.07538 | 0.036265 | 0.048956 | -0.12223 | 60.6763 | 60.689 | 60.7221 | 60.7032 | 60.8693 | 61.0305 | 60.6622 | 60.8499 | 0.098957 | -0.01763 | 0.042941 | -0.061647 | 0.049998 | 0.062689 | -0.1085 | 60.6901 | 60.7028 | 60.7358 | 60.7169 | 60.883 | 61.0443 | 60.6759 | 60.8636 | -0.19292 | 0.01414 | -0.14717 | 0.059891
144.1406 | 122.1451 | -60.9283 | 60.8826 | 0.089802 | -0.031363 | 0.038365 | -0.070802 | 0.036265 | 0.044377 | -0.12681 | 60.6763 | 60.6844 | 60.7267 | 60.6986 | 60.8738 | 61.0259 | 60.6714 | 60.8499 | 0.10354 | -0.01763 | 0.052098 | -0.057069 | 0.049998 | 0.05811 | -0.11308 | 60.6901 | 60.6982 | 60.7404 | 60.7123 | 60.8876 | 61.0397 | 60.6851 | 60.8636 | -0.1975 | 0.004983 | -0.14717 | 0.055312
145.875 | 122.0627 | -61.0153 | 60.8414 | 0.094381 | -0.026784 | 0.033786 | -0.066223 | 0.036265 | 0.053534 | -0.12223 | 60.6763 | 60.6844 | 60.7267 | 60.7078 | 60.8738 | 61.0259 | 60.6576 | 60.8499 | 0.10811 | -0.013051 | 0.047519 | -0.05249 | 0.049998 | 0.067267 | -0.1085 | 60.6901 | 60.6982 | 60.7404 | 60.7215 | 60.8876 | 61.0397 | 60.6714 | 60.8636 | -0.1975 | 0.018718 | -0.14717 | 0.069047
147.5469 | 122.0627 | -60.9375 | 60.9055 | 0.089802 | -0.022205 | 0.033786 | -0.07538 | 0.040843 | 0.053534 | -0.12681 | 60.6855 | 60.689 | 60.7175 | 60.7078 | 60.8647 | 61.0214 | 60.6668 | 60.8453 | 0.10354 | -0.008472 | 0.047519 | -0.061647 | 0.054576 | 0.067267 | -0.11308 | 60.6992 | 60.7028 | 60.7312 | 60.7215 | 60.8784 | 61.0351 | 60.6805 | 60.8591 | -0.17919 | 0.018718 | -0.14717 | 0.050733
149.2656 | 122.1222 | -60.9512 | 60.8551 | 0.085224 | -0.026784 | 0.038365 | -0.070802 | 0.031687 | 0.053534 | -0.12223 | 60.6718 | 60.6844 | 60.7175 | 60.7078 | 60.8693 | 61.0305 | 60.6622 | 60.8316 | 0.098957 | -0.013051 | 0.052098 | -0.057069 | 0.04542 | 0.067267 | -0.1085 | 60.6855 | 60.6982 | 60.7312 | 60.7215 | 60.883 | 61.0443 | 60.6759 | 60.8453 | -0.1975 | 0.009561 | -0.15175 | 0.055312
151 | 122.0581 | -60.9558 | 60.9238 | 0.085224 | -0.022205 | 0.033786 | -0.066223 | 0.031687 | 0.053534 | -0.12223 | 60.6763 | 60.6844 | 60.7221 | 60.7032 | 60.8693 | 61.0214 | 60.6576 | 60.8362 | 0.098957 | -0.008472 | 0.047519 | -0.05249 | 0.04542 | 0.067267 | -0.1085 | 60.6901 | 60.6982 | 60.7358 | 60.7169 | 60.883 | 61.0351 | 60.6714 | 60.8499 | -0.19292 | 0.018718 | -0.14717 | 0.064469
152.7344 | 122.1405 | -60.8917 | 60.9055 | 0.089802 | -0.017627 | 0.029208 | -0.066223 | 0.040843 | 0.048956 | -0.12223 | 60.6763 | 60.6844 | 60.7175 | 60.7032 | 60.8647 | 61.0259 | 60.6576 | 60.8407 | 0.10354 | -0.003894 | 0.042941 | -0.05249 | 0.054576 | 0.062689 | -0.1085 | 60.6901 | 60.6982 | 60.7312 | 60.7169 | 60.8784 | 61.0397 | 60.6714 | 60.8545 | -0.18835 | 0.018718 | -0.14717 | 0.05989
154.3906 | 122.0901 | -60.9055 | 60.9283 | 0.089802 | -0.022205 | 0.038365 | -0.070802 | 0.036265 | 0.048956 | -0.12681 | 60.6718 | 60.689 | 60.7221 | 60.7032 | 60.8738 | 61.0259 | 60.6668 | 60.8407 | 0.10354 | -0.008472 | 0.052098 | -0.057069 | 0.049998 | 0.062689 | -0.11308 | 60.6855 | 60.7028 | 60.7358 | 60.7169 | 60.8876 | 61.0397 | 60.6805 | 60.8545 | -0.20208 | 0.004982 | -0.15175 | 0.055312
156.125 | 122.0627 | -60.9421 | 60.8963 | 0.085224 | -0.022205 | 0.038365 | -0.07538 | 0.036265 | 0.044377 | -0.12223 | 60.6763 | 60.6799 | 60.7129 | 60.7032 | 60.8647 | 61.0168 | 60.6622 | 60.8453 | 0.098957 | -0.008472 | 0.052098 | -0.061647 | 0.049998 | 0.05811 | -0.1085 | 60.6901 | 60.6936 | 60.7267 | 60.7169 | 60.8784 | 61.0305 | 60.6759 | 60.8591 | -0.18835 | 0.01414 | -0.15175 | 0.050734
157.8594 | 122.0215 | -60.965 | 60.8505 | 0.085224 | -0.022205 | 0.038365 | -0.070802 | 0.045421 | 0.044377 | -0.11765 | 60.6855 | 60.6799 | 60.7221 | 60.7032 | 60.8693 | 61.0214 | 60.6485 | 60.8362 | 0.098957 | -0.008472 | 0.052098 | -0.057069 | 0.059154 | 0.05811 | -0.10392 | 60.6992 | 60.6936 | 60.7358 | 60.7169 | 60.883 | 61.0351 | 60.6622 | 60.8499 | -0.18377 | 0.037032 | -0.14717 | 0.073626
159.5156 | 122.113 | -60.965 | 60.8276 | 0.080646 | -0.017627 | 0.029208 | -0.070802 | 0.036265 | 0.039799 | -0.11765 | 60.6763 | 60.6844 | 60.7267 | 60.6986 | 60.8647 | 61.0259 | 60.6439 | 60.8362 | 0.094379 | -0.003894 | 0.042941 | -0.057069 | 0.049998 | 0.053532 | -0.10392 | 60.6901 | 60.6982 | 60.7404 | 60.7123 | 60.8784 | 61.0397 | 60.6576 | 60.8499 | -0.18835 | 0.032453 | -0.13802 | 0.082782
161.2344 | 122.0306 | -60.9375 | 60.9009 | 0.085224 | -0.017627 | 0.042944 | -0.070802 | 0.036265 | 0.048956 | -0.12681 | 60.6763 | 60.6844 | 60.7221 | 60.7032 | 60.8693 | 61.0259 | 60.6576 | 60.8362 | 0.098957 | -0.003894 | 0.056677 | -0.057069 | 0.049998 | 0.062689 | -0.11308 | 60.6901 | 60.6982 | 60.7358 | 60.7169 | 60.883 | 61.0397 | 60.6714 | 60.8499 | -0.19292 | 0.018718 | -0.14717 | 0.064469
162.9531 | 122.0215 | -60.9375 | 60.9512 | 0.089802 | -0.022205 | 0.038365 | -0.066223 | 0.036265 | 0.044377 | -0.12223 | 60.6718 | 60.689 | 60.7129 | 60.7078 | 60.8647 | 61.0214 | 60.6576 | 60.8407 | 0.10354 | -0.008472 | 0.052098 | -0.05249 | 0.049998 | 0.05811 | -0.1085 | 60.6855 | 60.7028 | 60.7267 | 60.7215 | 60.8784 | 61.0351 | 60.6714 | 60.8545 | -0.19292 | 0.014139 | -0.15175 | 0.055312
164.6719 | 122.049 | -60.9146 | 60.9238 | 0.080646 | -0.013048 | 0.038365 | -0.066223 | 0.040843 | 0.044377 | -0.11308 | 60.6672 | 60.6844 | 60.7175 | 60.7078 | 60.8693 | 61.0168 | 60.653 | 60.8362 | 0.094379 | 0.000685 | 0.052098 | -0.05249 | 0.054576 | 0.05811 | -0.099344 | 60.6809 | 60.6982 | 60.7312 | 60.7215 | 60.883 | 61.0305 | 60.6668 | 60.8499 | -0.20208 | 0.014139 | -0.15175 | 0.064468
166.4219 | 122.0444 | -60.9329 | 60.9238 | 0.085224 | -0.022205 | 0.038365 | -0.070802 | 0.049999 | 0.053534 | -0.11765 | 60.6718 | 60.6799 | 60.7175 | 60.6986 | 60.8601 | 61.0168 | 60.6485 | 60.827 | 0.098957 | -0.008472 | 0.052098 | -0.057069 | 0.063732 | 0.067267 | -0.10392 | 60.6855 | 60.6936 | 60.7312 | 60.7123 | 60.8738 | 61.0305 | 60.6622 | 60.8407 | -0.18835 | 0.023296 | -0.1426 | 0.069047
168.1406 | 122.0947 | -60.9604 | 60.8459 | 0.089802 | -0.013048 | 0.029208 | -0.066223 | 0.040843 | 0.053534 | -0.11765 | 60.6672 | 60.6844 | 60.7175 | 60.694 | 60.8555 | 61.0122 | 60.653 | 60.8316 | 0.10354 | 0.000685 | 0.042941 | -0.05249 | 0.054576 | 0.067267 | -0.10392 | 60.6809 | 60.6982 | 60.7312 | 60.7078 | 60.8693 | 61.0259 | 60.6668 | 60.8453 | -0.18835 | 0.014139 | -0.13802 | 0.064468
169.7969 | 122.113 | -60.965 | 60.8139 | 0.089802 | -0.022205 | 0.042944 | -0.066223 | 0.040843 | 0.048956 | -0.12681 | 60.6626 | 60.6753 | 60.7175 | 60.6986 | 60.8601 | 61.0214 | 60.6622 | 60.8362 | 0.10354 | -0.008472 | 0.056677 | -0.05249 | 0.054576 | 0.062689 | -0.11308 | 60.6763 | 60.689 | 60.7312 | 60.7123 | 60.8738 | 61.0351 | 60.6759 | 60.8499 | -0.1975 | 0.000404 | -0.1426 | 0.055312
171.4531 | 122.1222 | -60.9055 | 60.8963 | 0.080646 | -0.022205 | 0.038365 | -0.070802 | 0.049999 | 0.048956 | -0.12681 | 60.6672 | 60.6707 | 60.7175 | 60.6986 | 60.8693 | 61.0168 | 60.653 | 60.8362 | 0.094379 | -0.008472 | 0.052098 | -0.057069 | 0.063732 | 0.062689 | -0.11308 | 60.6809 | 60.6844 | 60.7312 | 60.7123 | 60.883 | 61.0305 | 60.6668 | 60.8499 | -0.20208 | 0.014139 | -0.15175 | 0.064468
173.125 | 122.1039 | -60.8734 | 60.8871 | 0.089802 | -0.017627 | 0.038365 | -0.070802 | 0.036265 | 0.048956 | -0.12223 | 60.6718 | 60.6753 | 60.7175 | 60.6894 | 60.8601 | 61.0168 | 60.653 | 60.8407 | 0.10354 | -0.003894 | 0.052098 | -0.057069 | 0.049998 | 0.062689 | -0.1085 | 60.6855 | 60.689 | 60.7312 | 60.7032 | 60.8738 | 61.0305 | 60.6668 | 60.8545 | -0.18835 | 0.018717 | -0.1426 | 0.064468
174.7969 | 122.1039 | -60.8597 | 60.8871 | 0.080646 | -0.017627 | 0.033786 | -0.070802 | 0.040843 | 0.053534 | -0.12223 | 60.6626 | 60.6799 | 60.7129 | 60.6849 | 60.8601 | 61.0122 | 60.6439 | 60.827 | 0.094379 | -0.003894 | 0.047519 | -0.057069 | 0.054576 | 0.067267 | -0.1085 | 60.6763 | 60.6936 | 60.7267 | 60.6986 | 60.8738 | 61.0259 | 60.6576 | 60.8407 | -0.1975 | 0.018717 | -0.14717 | 0.069047
176.4844 | 121.9849 | -60.9055 | 60.965 | 0.085224 | -0.017627 | 0.042944 | -0.070802 | 0.040843 | 0.044377 | -0.11308 | 60.6763 | 60.6753 | 60.7175 | 60.694 | 60.8647 | 61.0259 | 60.6393 | 60.8316 | 0.098957 | -0.003894 | 0.056677 | -0.057069 | 0.054576 | 0.05811 | -0.099344 | 60.6901 | 60.689 | 60.7312 | 60.7078 | 60.8784 | 61.0397 | 60.653 | 60.8453 | -0.18835 | 0.037032 | -0.14717 | 0.078204
178.25 | 122.0673 | -60.8734 | 60.9238 | 0.085224 | -0.008469 | 0.038365 | -0.066223 | 0.040843 | 0.053534 | -0.13139 | 60.6626 | 60.6753 | 60.7129 | 60.6894 | 60.8601 | 61.0214 | 60.653 | 60.8316 | 0.098957 | 0.005264 | 0.052098 | -0.05249 | 0.054576 | 0.067267 | -0.11766 | 60.6763 | 60.689 | 60.7267 | 60.7032 | 60.8738 | 61.0351 | 60.6668 | 60.8453 | -0.1975 | 0.00956 | -0.14717 | 0.05989
179.9219 | 121.9711 | -60.9421 | 60.878 | 0.089802 | -0.013048 | 0.033786 | -0.061645 | 0.040843 | 0.048956 | -0.12681 | 60.6718 | 60.6799 | 60.7084 | 60.6986 | 60.8555 | 61.0214 | 60.6485 | 60.8224 | 0.10354 | 0.000685 | 0.047519 | -0.047912 | 0.054576 | 0.062689 | -0.11308 | 60.6855 | 60.6936 | 60.7221 | 60.7123 | 60.8693 | 61.0351 | 60.6622 | 60.8362 | -0.18377 | 0.023296 | -0.14717 | 0.059891
181.6094 | 122.0993 | -60.9329 | 60.8231 | 0.080646 | -0.017627 | 0.038365 | -0.061645 | 0.040843 | 0.044377 | -0.11765 | 60.6626 | 60.6844 | 60.7175 | 60.6894 | 60.851 | 61.0168 | 60.6439 | 60.8179 | 0.094379 | -0.003894 | 0.052098 | -0.047912 | 0.054576 | 0.05811 | -0.10392 | 60.6763 | 60.6982 | 60.7312 | 60.7032 | 60.8647 | 61.0305 | 60.6576 | 60.8316 | -0.18835 | 0.018717 | -0.13344 | 0.073625
183.2812 | 122.113 | -60.9009 | 60.91 | 0.085224 | -0.013048 | 0.033786 | -0.066223 | 0.036265 | 0.053534 | -0.12223 | 60.6672 | 60.6753 | 60.7129 | 60.6986 | 60.8555 | 61.0168 | 60.6485 | 60.827 | 0.098957 | 0.000685 | 0.047519 | -0.05249 | 0.049998 | 0.067267 | -0.1085 | 60.6809 | 60.689 | 60.7267 | 60.7123 | 60.8693 | 61.0305 | 60.6622 | 60.8407 | -0.18835 | 0.018718 | -0.1426 | 0.064469
184.9688 | 122.0764 | -60.9375 | 60.8551 | 0.094381 | -0.013048 | 0.038365 | -0.070802 | 0.036265 | 0.039799 | -0.12223 | 60.6672 | 60.6799 | 60.7175 | 60.6894 | 60.8555 | 61.0076 | 60.6485 | 60.827 | 0.10811 | 0.000685 | 0.052098 | -0.057069 | 0.049998 | 0.053532 | -0.1085 | 60.6809 | 60.6936 | 60.7312 | 60.7032 | 60.8693 | 61.0214 | 60.6622 | 60.8407 | -0.18835 | 0.018718 | -0.13802 | 0.069047
186.6406 | 122.0444 | -60.9146 | 60.8505 | 0.085224 | -0.017627 | 0.042944 | -0.066223 | 0.036265 | 0.048956 | -0.13139 | 60.658 | 60.6707 | 60.7038 | 60.6894 | 60.8555 | 61.0122 | 60.6485 | 60.8224 | 0.098957 | -0.003894 | 0.056677 | -0.05249 | 0.049998 | 0.062689 | -0.11766 | 60.6718 | 60.6844 | 60.7175 | 60.7032 | 60.8693 | 61.0259 | 60.6622 | 60.8362 | -0.1975 | 0.009561 | -0.15175 | 0.055313
188.3281 | 122.0947 | -60.9329 | 60.8093 | 0.089802 | -0.013048 | 0.038365 | -0.066223 | 0.031687 | 0.048956 | -0.12223 | 60.6626 | 60.6707 | 60.7038 | 60.6894 | 60.8418 | 61.0122 | 60.6439 | 60.8224 | 0.10354 | 0.000685 | 0.052098 | -0.05249 | 0.04542 | 0.062689 | -0.1085 | 60.6763 | 60.6844 | 60.7175 | 60.7032 | 60.8555 | 61.0259 | 60.6576 | 60.8362 | -0.17919 | 0.018717 | -0.13802 | 0.059891
189.9844 | 122.0535 | -60.9146 | 60.8643 | 0.089802 | -0.017627 | 0.038365 | -0.066223 | 0.036265 | 0.044377 | -0.12223 | 60.6626 | 60.6753 | 60.7084 | 60.6849 | 60.851 | 61.0076 | 60.6439 | 60.8224 | 0.10354 | -0.003894 | 0.052098 | -0.05249 | 0.049998 | 0.05811 | -0.1085 | 60.6763 | 60.689 | 60.7221 | 60.6986 | 60.8647 | 61.0214 | 60.6576 | 60.8362 | -0.18835 | 0.018717 | -0.1426 | 0.064469
191.6562 | 122.081 | -60.8688 | 60.9055 | 0.089802 | -0.022205 | 0.033786 | -0.066223 | 0.040843 | 0.048956 | -0.11765 | 60.6626 | 60.6753 | 60.7084 | 60.6894 | 60.8647 | 61.0122 | 60.6439 | 60.8224 | 0.10354 | -0.008472 | 0.047519 | -0.05249 | 0.054576 | 0.062689 | -0.10392 | 60.6763 | 60.689 | 60.7221 | 60.7032 | 60.8784 | 61.0259 | 60.6576 | 60.8362 | -0.20208 | 0.018717 | -0.15633 | 0.064469
193.3125 | 122.0535 | -60.9146 | 60.878 | 0.080646 | -0.017627 | 0.033786 | -0.066223 | 0.040843 | 0.048956 | -0.12223 | 60.6626 | 60.6707 | 60.7084 | 60.6894 | 60.851 | 61.0076 | 60.6439 | 60.8224 | 0.094379 | -0.003894 | 0.047519 | -0.05249 | 0.054576 | 0.062689 | -0.1085 | 60.6763 | 60.6844 | 60.7221 | 60.7032 | 60.8647 | 61.0214 | 60.6576 | 60.8362 | -0.18835 | 0.018717 | -0.1426 | 0.064469
195 | 122.0169 | -60.9146 | 60.9009 | 0.080646 | -0.022205 | 0.042944 | -0.070802 | 0.045421 | 0.048956 | -0.12223 | 60.6626 | 60.6753 | 60.7084 | 60.6849 | 60.8555 | 61.0122 | 60.6393 | 60.8179 | 0.094379 | -0.008472 | 0.056677 | -0.057069 | 0.059154 | 0.062689 | -0.1085 | 60.6763 | 60.689 | 60.7221 | 60.6986 | 60.8693 | 61.0259 | 60.653 | 60.8316 | -0.19292 | 0.023296 | -0.14717 | 0.069048
196.75 | 122.0169 | -60.9833 | 60.8231 | 0.085224 | -0.026784 | 0.038365 | -0.066223 | 0.031687 | 0.044377 | -0.12223 | 60.6672 | 60.6753 | 60.7038 | 60.6894 | 60.8418 | 61.0122 | 60.6302 | 60.8179 | 0.098957 | -0.013051 | 0.052098 | -0.05249 | 0.04542 | 0.05811 | -0.1085 | 60.6809 | 60.689 | 60.7175 | 60.7032 | 60.8555 | 61.0259 | 60.6439 | 60.8316 | -0.17461 | 0.037031 | -0.13802 | 0.073626
198.4062 | 122.0764 | -60.9375 | 60.8231 | 0.089802 | -0.026784 | 0.038365 | -0.061645 | 0.040843 | 0.048956 | -0.12223 | 60.6626 | 60.6707 | 60.6992 | 60.6849 | 60.8464 | 61.0122 | 60.6393 | 60.8179 | 0.10354 | -0.013051 | 0.052098 | -0.047912 | 0.054576 | 0.062689 | -0.1085 | 60.6763 | 60.6844 | 60.7129 | 60.6986 | 60.8601 | 61.0259 | 60.653 | 60.8316 | -0.18377 | 0.023296 | -0.14717 | 0.059891
200.0781 | 122.0947 | -60.878 | 60.9055 | 0.089802 | -0.031363 | 0.047522 | -0.07538 | 0.036265 | 0.048956 | -0.11765 | 60.6718 | 60.6661 | 60.7038 | 60.6894 | 60.8555 | 61.0031 | 60.6347 | 60.8133 | 0.10354 | -0.01763 | 0.061255 | -0.061647 | 0.049998 | 0.062689 | -0.10392 | 60.6855 | 60.6799 | 60.7175 | 60.7032 | 60.8693 | 61.0168 | 60.6485 | 60.827 | -0.18377 | 0.037031 | -0.15175 | 0.069048
201.7812 | 122.0993 | -60.8643 | 60.9055 | 0.080646 | -0.026784 | 0.033786 | -0.061645 | 0.040843 | 0.048956 | -0.12681 | 60.658 | 60.6753 | 60.7129 | 60.6757 | 60.851 | 61.0122 | 60.6393 | 60.8224 | 0.094379 | -0.013051 | 0.047519 | -0.047912 | 0.054576 | 0.062689 | -0.11308 | 60.6718 | 60.689 | 60.7267 | 60.6894 | 60.8647 | 61.0259 | 60.653 | 60.8362 | -0.19293 | 0.018718 | -0.13802 | 0.073626
203.4531 | 121.962 | -60.9787 | 60.8597 | 0.089802 | -0.017627 | 0.042944 | -0.061645 | 0.040843 | 0.044377 | -0.11765 | 60.6626 | 60.6753 | 60.7084 | 60.6803 | 60.8464 | 61.0122 | 60.6393 | 60.8133 | 0.10354 | -0.003894 | 0.056677 | -0.047912 | 0.054576 | 0.05811 | -0.10392 | 60.6763 | 60.689 | 60.7221 | 60.694 | 60.8601 | 61.0259 | 60.653 | 60.827 | -0.18377 | 0.023296 | -0.13802 | 0.069048
205.125 | 122.0901 | -60.9604 | 60.8185 | 0.089802 | -0.026784 | 0.038365 | -0.070802 | 0.040843 | 0.044377 | -0.11765 | 60.658 | 60.657 | 60.6992 | 60.6803 | 60.8418 | 61.0076 | 60.6302 | 60.8133 | 0.10354 | -0.013051 | 0.052098 | -0.057069 | 0.054576 | 0.05811 | -0.10392 | 60.6718 | 60.6707 | 60.7129 | 60.694 | 60.8555 | 61.0214 | 60.6439 | 60.827 | -0.18377 | 0.027874 | -0.1426 | 0.069047
206.8125 | 121.9574 | -60.8917 | 60.9741 | 0.089802 | -0.026784 | 0.038365 | -0.061645 | 0.036265 | 0.048956 | -0.11308 | 60.6626 | 60.6707 | 60.7084 | 60.6849 | 60.851 | 61.0076 | 60.6256 | 60.8179 | 0.10354 | -0.013051 | 0.052098 | -0.047912 | 0.049998 | 0.062689 | -0.099344 | 60.6763 | 60.6844 | 60.7221 | 60.6986 | 60.8647 | 61.0214 | 60.6393 | 60.8316 | -0.18835 | 0.037031 | -0.1426 | 0.082783
208.5312 | 121.9574 | -60.9146 | 60.9192 | 0.085224 | -0.022205 | 0.042944 | -0.070802 | 0.040843 | 0.048956 | -0.11308 | 60.6672 | 60.6707 | 60.7084 | 60.6803 | 60.851 | 61.0031 | 60.6393 | 60.8224 | 0.098957 | -0.008472 | 0.056677 | -0.057069 | 0.054576 | 0.062689 | -0.099344 | 60.6809 | 60.6844 | 60.7221 | 60.694 | 60.8647 | 61.0168 | 60.653 | 60.8362 | -0.18377 | 0.027875 | -0.1426 | 0.069048
210.2344 | 122.0718 | -60.8505 | 60.878 | 0.080646 | -0.022205 | 0.042944 | -0.070802 | 0.036265 | 0.044377 | -0.11308 | 60.6626 | 60.6753 | 60.7038 | 60.6803 | 60.851 | 61.0076 | 60.6347 | 60.827 | 0.094379 | -0.008472 | 0.056677 | -0.057069 | 0.049998 | 0.05811 | -0.099344 | 60.6763 | 60.689 | 60.7175 | 60.694 | 60.8647 | 61.0214 | 60.6485 | 60.8407 | -0.18835 | 0.027874 | -0.14717 | 0.069048
211.8906 | 121.9894 | -60.9329 | 60.9146 | 0.080646 | -0.022205 | 0.033786 | -0.066223 | 0.045421 | 0.044377 | -0.12223 | 60.658 | 60.6661 | 60.7038 | 60.6849 | 60.8464 | 61.0031 | 60.6302 | 60.8087 | 0.094379 | -0.008472 | 0.047519 | -0.05249 | 0.059154 | 0.05811 | -0.1085 | 60.6718 | 60.6799 | 60.7175 | 60.6986 | 60.8601 | 61.0168 | 60.6439 | 60.8224 | -0.18835 | 0.027874 | -0.1426 | 0.073626
213.5781 | 121.9986 | -60.9009 | 60.8963 | 0.085224 | -0.035942 | 0.038365 | -0.061645 | 0.040843 | 0.039799 | -0.11765 | 60.6626 | 60.6615 | 60.7038 | 60.6849 | 60.851 | 61.0031 | 60.6347 | 60.8133 | 0.098957 | -0.022209 | 0.052098 | -0.047912 | 0.054576 | 0.053532 | -0.10392 | 60.6763 | 60.6753 | 60.7175 | 60.6986 | 60.8647 | 61.0168 | 60.6485 | 60.827 | -0.18835 | 0.027874 | -0.14717 | 0.069048
215.3438 | 122.0444 | -60.9192 | 60.8231 | 0.085224 | -0.017627 | 0.038365 | -0.066223 | 0.040843 | 0.044377 | -0.12681 | 60.6534 | 60.6615 | 60.7038 | 60.6803 | 60.851 | 61.0076 | 60.621 | 60.8087 | 0.098957 | -0.003894 | 0.052098 | -0.05249 | 0.054576 | 0.05811 | -0.11308 | 60.6672 | 60.6753 | 60.7175 | 60.694 | 60.8647 | 61.0214 | 60.6347 | 60.8224 | -0.1975 | 0.032452 | -0.14717 | 0.082783
217.0156 | 122.0581 | -60.8734 | 60.9009 | 0.085224 | -0.022205 | 0.038365 | -0.066223 | 0.040843 | 0.039799 | -0.11765 | 60.6626 | 60.6615 | 60.69 | 60.6757 | 60.8418 | 61.0076 | 60.6302 | 60.8179 | 0.098957 | -0.008472 | 0.052098 | -0.05249 | 0.054576 | 0.053532 | -0.10392 | 60.6763 | 60.6753 | 60.7038 | 60.6894 | 60.8555 | 61.0214 | 60.6439 | 60.8316 | -0.17919 | 0.032452 | -0.15175 | 0.059891
218.75 | 122.0215 | -60.9421 | 60.8231 | 0.085224 | -0.022205 | 0.038365 | -0.070802 | 0.040843 | 0.044377 | -0.11765 | 60.658 | 60.6661 | 60.7038 | 60.6849 | 60.8418 | 60.9985 | 60.6027 | 60.8087 | 0.098957 | -0.008472 | 0.052098 | -0.057069 | 0.054576 | 0.05811 | -0.10392 | 60.6718 | 60.6799 | 60.7175 | 60.6986 | 60.8555 | 61.0122 | 60.6164 | 60.8224 | -0.18377 | 0.055345 | -0.13802 | 0.1011
220.4375 | 122.0947 | -60.8963 | 60.9009 | 0.080646 | -0.026784 | 0.029208 | -0.057066 | 0.031687 | 0.044377 | -0.12223 | 60.6534 | 60.6661 | 60.7084 | 60.6803 | 60.8418 | 61.0031 | 60.6347 | 60.8179 | 0.094379 | -0.013051 | 0.042941 | -0.043333 | 0.04542 | 0.05811 | -0.1085 | 60.6672 | 60.6799 | 60.7221 | 60.694 | 60.8555 | 61.0168 | 60.6485 | 60.8316 | -0.18835 | 0.018717 | -0.13344 | 0.073626
222.125 | 122.0123 | -60.8963 | 60.8643 | 0.085224 | -0.031363 | 0.038365 | -0.070802 | 0.045421 | 0.035221 | -0.12223 | 60.6489 | 60.6661 | 60.7038 | 60.6757 | 60.8418 | 61.0031 | 60.6302 | 60.8133 | 0.098957 | -0.01763 | 0.052098 | -0.057069 | 0.059154 | 0.048954 | -0.1085 | 60.6626 | 60.6799 | 60.7175 | 60.6894 | 60.8555 | 61.0168 | 60.6439 | 60.827 | -0.19293 | 0.018717 | -0.13802 | 0.073626
223.7969 | 121.962 | -60.9283 | 60.8551 | 0.089802 | -0.026784 | 0.033786 | -0.070802 | 0.036265 | 0.048956 | -0.12223 | 60.658 | 60.6661 | 60.7038 | 60.6711 | 60.8464 | 61.0031 | 60.6256 | 60.8041 | 0.10354 | -0.013051 | 0.047519 | -0.057069 | 0.049998 | 0.062689 | -0.1085 | 60.6718 | 60.6799 | 60.7175 | 60.6849 | 60.8601 | 61.0168 | 60.6393 | 60.8179 | -0.18835 | 0.032453 | -0.1426 | 0.078205
225.5 | 121.9711 | -60.8826 | 60.9238 | 0.094381 | -0.026784 | 0.042944 | -0.066223 | 0.036265 | 0.044377 | -0.11765 | 60.6626 | 60.6707 | 60.6992 | 60.6803 | 60.8464 | 60.9985 | 60.6164 | 60.8133 | 0.10811 | -0.013051 | 0.056677 | -0.05249 | 0.049998 | 0.05811 | -0.10392 | 60.6763 | 60.6844 | 60.7129 | 60.694 | 60.8601 | 61.0122 | 60.6302 | 60.827 | -0.18377 | 0.046188 | -0.14717 | 0.082783
227.1875 | 121.9391 | -60.9741 | 60.8597 | 0.085224 | -0.017627 | 0.038365 | -0.061645 | 0.040843 | 0.053534 | -0.11308 | 60.6534 | 60.6615 | 60.69 | 60.6711 | 60.8372 | 60.9939 | 60.6256 | 60.8087 | 0.098957 | -0.003894 | 0.052098 | -0.047912 | 0.054576 | 0.067267 | -0.099344 | 60.6672 | 60.6753 | 60.7038 | 60.6849 | 60.851 | 61.0076 | 60.6393 | 60.8224 | -0.18377 | 0.027874 | -0.14717 | 0.06447
228.8594 | 122.0215 | -60.9055 | 60.8643 | 0.085224 | -0.035942 | 0.038365 | -0.066223 | 0.040843 | 0.044377 | -0.12223 | 60.6626 | 60.6707 | 60.7038 | 60.6803 | 60.8418 | 61.0031 | 60.6302 | 60.8133 | 0.098957 | -0.022209 | 0.052098 | -0.05249 | 0.054576 | 0.05811 | -0.1085 | 60.6763 | 60.6844 | 60.7175 | 60.694 | 60.8555 | 61.0168 | 60.6439 | 60.827 | -0.17919 | 0.032452 | -0.13802 | 0.073626
230.5625 | 122.0627 | -60.8826 | 60.8917 | 0.089802 | -0.026784 | 0.038365 | -0.061645 | 0.036265 | 0.039799 | -0.11765 | 60.6626 | 60.6661 | 60.69 | 60.6711 | 60.8418 | 60.9985 | 60.6302 | 60.8087 | 0.10354 | -0.013051 | 0.052098 | -0.047912 | 0.049998 | 0.053532 | -0.10392 | 60.6763 | 60.6799 | 60.7038 | 60.6849 | 60.8555 | 61.0122 | 60.6439 | 60.8224 | -0.17919 | 0.032452 | -0.15175 | 0.059891
232.2344 | 122.0261 | -60.9467 | 60.7956 | 0.089802 | -0.031363 | 0.033786 | -0.066223 | 0.049999 | 0.048956 | -0.12223 | 60.6534 | 60.6615 | 60.7038 | 60.6849 | 60.8372 | 61.0031 | 60.6164 | 60.8041 | 0.10354 | -0.01763 | 0.047519 | -0.05249 | 0.063732 | 0.062689 | -0.1085 | 60.6672 | 60.6753 | 60.7175 | 60.6986 | 60.851 | 61.0168 | 60.6302 | 60.8179 | -0.18377 | 0.037031 | -0.13344 | 0.087362
233.8906 | 122.0627 | -60.9055 | 60.8002 | 0.085224 | -0.026784 | 0.042944 | -0.070802 | 0.036265 | 0.044377 | -0.11765 | 60.6534 | 60.657 | 60.6946 | 60.6757 | 60.8372 | 60.9939 | 60.6164 | 60.8041 | 0.098957 | -0.013051 | 0.056677 | -0.057069 | 0.049998 | 0.05811 | -0.10392 | 60.6672 | 60.6707 | 60.7084 | 60.6894 | 60.851 | 61.0076 | 60.6302 | 60.8179 | -0.18377 | 0.037031 | -0.1426 | 0.078205
235.5625 | 122.0215 | -60.9238 | 60.8688 | 0.076067 | -0.035942 | 0.038365 | -0.066223 | 0.040843 | 0.048956 | -0.12681 | 60.658 | 60.657 | 60.6992 | 60.6757 | 60.8418 | 60.9985 | 60.6302 | 60.8041 | 0.0898 | -0.022209 | 0.052098 | -0.05249 | 0.054576 | 0.062689 | -0.11308 | 60.6718 | 60.6707 | 60.7129 | 60.6894 | 60.8555 | 61.0122 | 60.6439 | 60.8179 | -0.18377 | 0.027874 | -0.1426 | 0.069047
237.2188 | 122.0352 | -60.9421 | 60.8276 | 0.080646 | -0.031363 | 0.033786 | -0.070802 | 0.036265 | 0.039799 | -0.1085 | 60.6534 | 60.6707 | 60.7038 | 60.6803 | 60.8418 | 60.9985 | 60.621 | 60.8041 | 0.094379 | -0.01763 | 0.047519 | -0.057069 | 0.049998 | 0.053532 | -0.094766 | 60.6672 | 60.6844 | 60.7175 | 60.694 | 60.8555 | 61.0122 | 60.6347 | 60.8179 | -0.18835 | 0.032452 | -0.13802 | 0.082783
238.9062 | 121.9391 | -60.9467 | 60.8643 | 0.089802 | -0.040521 | 0.038365 | -0.066223 | 0.045421 | 0.048956 | -0.11765 | 60.6626 | 60.657 | 60.69 | 60.6757 | 60.8372 | 60.9939 | 60.6164 | 60.8087 | 0.10354 | -0.026788 | 0.052098 | -0.05249 | 0.059154 | 0.062689 | -0.10392 | 60.6763 | 60.6707 | 60.7038 | 60.6894 | 60.851 | 61.0076 | 60.6302 | 60.8224 | -0.17461 | 0.046188 | -0.14717 | 0.073627
240.5781 | 121.9574 | -60.965 | 60.8551 | 0.089802 | -0.040521 | 0.038365 | -0.066223 | 0.040843 | 0.048956 | -0.11765 | 60.658 | 60.6615 | 60.6992 | 60.6803 | 60.8281 | 60.9985 | 60.5935 | 60.8087 | 0.10354 | -0.026788 | 0.052098 | -0.05249 | 0.054576 | 0.062689 | -0.10392 | 60.6718 | 60.6753 | 60.7129 | 60.694 | 60.8418 | 61.0122 | 60.6073 | 60.8224 | -0.17003 | 0.064501 | -0.12886 | 0.10567
242.25 | 121.9391 | -60.9329 | 60.8597 | 0.085224 | -0.0451 | 0.033786 | -0.061645 | 0.036265 | 0.048956 | -0.12223 | 60.6534 | 60.6661 | 60.6992 | 60.6803 | 60.8418 | 60.9985 | 60.5935 | 60.7995 | 0.098957 | -0.031367 | 0.047519 | -0.047912 | 0.049998 | 0.062689 | -0.1085 | 60.6672 | 60.6799 | 60.7129 | 60.694 | 60.8555 | 61.0122 | 60.6073 | 60.8133 | -0.18835 | 0.059922 | -0.1426 | 0.10567
243.9375 | 121.962 | -60.9238 | 60.8643 | 0.085224 | -0.040521 | 0.033786 | -0.066223 | 0.040843 | 0.048956 | -0.11308 | 60.6626 | 60.6661 | 60.6946 | 60.6757 | 60.8326 | 60.9985 | 60.5889 | 60.7995 | 0.098957 | -0.026788 | 0.047519 | -0.05249 | 0.054576 | 0.062689 | -0.099344 | 60.6763 | 60.6799 | 60.7084 | 60.6894 | 60.8464 | 61.0122 | 60.6027 | 60.8133 | -0.17003 | 0.073658 | -0.13802 | 0.10567
245.6094 | 122.0581 | -60.9238 | 60.7956 | 0.089802 | -0.0451 | 0.038365 | -0.066223 | 0.040843 | 0.044377 | -0.11765 | 60.6534 | 60.657 | 60.6992 | 60.6757 | 60.8326 | 60.9939 | 60.5661 | 60.8041 | 0.10354 | -0.031367 | 0.052098 | -0.05249 | 0.054576 | 0.05811 | -0.10392 | 60.6672 | 60.6707 | 60.7129 | 60.6894 | 60.8464 | 61.0076 | 60.5798 | 60.8179 | -0.17919 | 0.087393 | -0.13344 | 0.13314
247.2656 | 122.0261 | -60.9192 | 60.8185 | 0.089802 | -0.040521 | 0.033786 | -0.061645 | 0.036265 | 0.039799 | -0.11765 | 60.6534 | 60.6524 | 60.6946 | 60.6711 | 60.8281 | 60.9939 | 60.5706 | 60.7904 | 0.10354 | -0.026788 | 0.047519 | -0.047912 | 0.049998 | 0.053532 | -0.10392 | 60.6672 | 60.6661 | 60.7084 | 60.6849 | 60.8418 | 61.0076 | 60.5844 | 60.8041 | -0.17461 | 0.082814 | -0.13344 | 0.12399
248.9531 | 121.9711 | -60.965 | 60.8231 | 0.076067 | -0.031363 | 0.038365 | -0.061645 | 0.040843 | 0.044377 | -0.11308 | 60.6626 | 60.657 | 60.6946 | 60.6757 | 60.8281 | 60.9939 | 60.5981 | 60.8041 | 0.0898 | -0.01763 | 0.052098 | -0.047912 | 0.054576 | 0.05811 | -0.099344 | 60.6763 | 60.6707 | 60.7084 | 60.6894 | 60.8418 | 61.0076 | 60.6118 | 60.8179 | -0.16546 | 0.064501 | -0.13344 | 0.096518
250.6094 | 121.9666 | -60.878 | 60.91 | 0.085224 | -0.035942 | 0.033786 | -0.061645 | 0.036265 | 0.048956 | -0.11765 | 60.6534 | 60.657 | 60.6992 | 60.6711 | 60.8372 | 60.9939 | 60.5889 | 60.7995 | 0.098957 | -0.022209 | 0.047519 | -0.047912 | 0.049998 | 0.062689 | -0.10392 | 60.6672 | 60.6707 | 60.7129 | 60.6849 | 60.851 | 61.0076 | 60.6027 | 60.8133 | -0.18377 | 0.064501 | -0.13802 | 0.11025
252.2812 | 122.0581 | -60.8505 | 60.8505 | 0.085224 | -0.031363 | 0.033786 | -0.066223 | 0.036265 | 0.039799 | -0.13139 | 60.6489 | 60.6478 | 60.6946 | 60.6711 | 60.8326 | 60.9939 | 60.5706 | 60.7995 | 0.098957 | -0.01763 | 0.047519 | -0.05249 | 0.049998 | 0.053532 | -0.11766 | 60.6626 | 60.6615 | 60.7084 | 60.6849 | 60.8464 | 61.0076 | 60.5844 | 60.8133 | -0.18377 | 0.078236 | -0.13802 | 0.12399
253.9531 | 122.0535 | -60.8414 | 60.8551 | 0.080646 | -0.017627 | 0.033786 | -0.066223 | 0.036265 | 0.044377 | -0.11308 | 60.6534 | 60.657 | 60.6946 | 60.6665 | 60.8418 | 60.9893 | 60.5798 | 60.8041 | 0.094379 | -0.003894 | 0.047519 | -0.05249 | 0.049998 | 0.05811 | -0.099344 | 60.6672 | 60.6707 | 60.7084 | 60.6803 | 60.8555 | 61.0031 | 60.5935 | 60.8179 | -0.18835 | 0.073658 | -0.14717 | 0.11483
255.625 | 121.9711 | -60.8871 | 60.9146 | 0.080646 | -0.022205 | 0.038365 | -0.070802 | 0.045421 | 0.039799 | -0.12223 | 60.658 | 60.657 | 60.69 | 60.6757 | 60.8418 | 60.9939 | 60.5706 | 60.795 | 0.094379 | -0.008472 | 0.052098 | -0.057069 | 0.059154 | 0.053532 | -0.1085 | 60.6718 | 60.6707 | 60.7038 | 60.6894 | 60.8555 | 61.0076 | 60.5844 | 60.8087 | -0.18377 | 0.087393 | -0.15175 | 0.11941
257.2969 | 122.0581 | -60.8643 | 60.8963 | 0.080646 | -0.017627 | 0.038365 | -0.070802 | 0.036265 | 0.044377 | -0.11765 | 60.6534 | 60.6432 | 60.6946 | 60.6711 | 60.8372 | 60.9847 | 60.5798 | 60.795 | 0.094379 | -0.003894 | 0.052098 | -0.057069 | 0.049998 | 0.05811 | -0.10392 | 60.6672 | 60.657 | 60.7084 | 60.6849 | 60.851 | 60.9985 | 60.5935 | 60.8087 | -0.18377 | 0.073658 | -0.1426 | 0.11483
258.9844 | 122.0078 | -60.9009 | 60.8551 | 0.080646 | -0.017627 | 0.038365 | -0.066223 | 0.036265 | 0.044377 | -0.12681 | 60.6489 | 60.6615 | 60.6946 | 60.6665 | 60.8281 | 60.9847 | 60.5935 | 60.8041 | 0.094379 | -0.003894 | 0.052098 | -0.05249 | 0.049998 | 0.05811 | -0.11308 | 60.6626 | 60.6753 | 60.7084 | 60.6803 | 60.8418 | 60.9985 | 60.6073 | 60.8179 | -0.17919 | 0.055344 | -0.13344 | 0.1011
260.7188 | 122.0535 | -60.8505 | 60.8551 | 0.080646 | -0.022205 | 0.038365 | -0.070802 | 0.036265 | 0.048956 | -0.11765 | 60.658 | 60.657 | 60.69 | 60.6665 | 60.8372 | 60.9893 | 60.5752 | 60.7995 | 0.094379 | -0.008472 | 0.052098 | -0.057069 | 0.049998 | 0.062689 | -0.10392 | 60.6718 | 60.6707 | 60.7038 | 60.6803 | 60.851 | 61.0031 | 60.5889 | 60.8133 | -0.17919 | 0.082815 | -0.14717 | 0.11483
262.4531 | 122.0581 | -60.8505 | 60.8826 | 0.085224 | -0.017627 | 0.038365 | -0.061645 | 0.036265 | 0.044377 | -0.12223 | 60.6534 | 60.6524 | 60.6946 | 60.6665 | 60.8281 | 60.9847 | 60.5615 | 60.795 | 0.098957 | -0.003894 | 0.052098 | -0.047912 | 0.049998 | 0.05811 | -0.1085 | 60.6672 | 60.6661 | 60.7084 | 60.6803 | 60.8418 | 60.9985 | 60.5752 | 60.8087 | -0.17461 | 0.091971 | -0.13344 | 0.13314
264.1406 | 121.9116 | -60.9558 | 60.8276 | 0.085224 | -0.022205 | 0.042944 | -0.066223 | 0.040843 | 0.044377 | -0.11308 | 60.6489 | 60.6524 | 60.69 | 60.662 | 60.8281 | 60.9847 | 60.5615 | 60.795 | 0.098957 | -0.008472 | 0.056677 | -0.05249 | 0.054576 | 0.05811 | -0.099344 | 60.6626 | 60.6661 | 60.7038 | 60.6757 | 60.8418 | 60.9985 | 60.5752 | 60.8087 | -0.17919 | 0.087393 | -0.13802 | 0.12857
265.8438 | 122.0352 | -60.9329 | 60.7864 | 0.085224 | -0.017627 | 0.033786 | -0.061645 | 0.036265 | 0.048956 | -0.11765 | 60.658 | 60.6478 | 60.6946 | 60.6665 | 60.8189 | 60.9893 | 60.5386 | 60.7858 | 0.098957 | -0.003894 | 0.047519 | -0.047912 | 0.049998 | 0.062689 | -0.10392 | 60.6718 | 60.6615 | 60.7084 | 60.6803 | 60.8326 | 61.0031 | 60.5523 | 60.7995 | -0.16088 | 0.11944 | -0.12428 | 0.15604
267.5156 | 122.0673 | -60.8459 | 60.8734 | 0.080646 | -0.026784 | 0.038365 | -0.066223 | 0.036265 | 0.044377 | -0.11308 | 60.6534 | 60.6524 | 60.7038 | 60.662 | 60.8372 | 60.9893 | 60.5569 | 60.795 | 0.094379 | -0.013051 | 0.052098 | -0.05249 | 0.049998 | 0.05811 | -0.099344 | 60.6672 | 60.6661 | 60.7175 | 60.6757 | 60.851 | 61.0031 | 60.5706 | 60.8087 | -0.18377 | 0.09655 | -0.13344 | 0.14688
269.1875 | 121.9162 | -60.9787 | 60.8597 | 0.080646 | -0.026784 | 0.033786 | -0.070802 | 0.040843 | 0.048956 | -0.11765 | 60.6534 | 60.6524 | 60.6855 | 60.662 | 60.8189 | 60.9939 | 60.5889 | 60.7904 | 0.094379 | -0.013051 | 0.047519 | -0.057069 | 0.054576 | 0.062689 | -0.10392 | 60.6672 | 60.6661 | 60.6992 | 60.6757 | 60.8326 | 61.0076 | 60.6027 | 60.8041 | -0.16546 | 0.064501 | -0.13344 | 0.096518
270.9375 | 121.9574 | -60.8917 | 60.8734 | 0.076067 | -0.017627 | 0.038365 | -0.052488 | 0.045421 | 0.048956 | -0.11765 | 60.658 | 60.6524 | 60.69 | 60.6711 | 60.8189 | 60.9847 | 60.5889 | 60.7995 | 0.0898 | -0.003894 | 0.052098 | -0.038755 | 0.059154 | 0.062689 | -0.10392 | 60.6718 | 60.6661 | 60.7038 | 60.6849 | 60.8326 | 60.9985 | 60.6027 | 60.8133 | -0.16088 | 0.06908 | -0.12886 | 0.1011
272.6875 | 121.9391 | -60.8643 | 60.9329 | 0.080646 | -0.022205 | 0.033786 | -0.066223 | 0.036265 | 0.044377 | -0.11765 | 60.6534 | 60.6524 | 60.69 | 60.662 | 60.8281 | 60.9893 | 60.5661 | 60.795 | 0.094379 | -0.008472 | 0.047519 | -0.05249 | 0.049998 | 0.05811 | -0.10392 | 60.6672 | 60.6661 | 60.7038 | 60.6757 | 60.8418 | 61.0031 | 60.5798 | 60.8087 | -0.17461 | 0.087393 | -0.13802 | 0.12399
274.4375 | 122.0535 | -60.8414 | 60.8826 | 0.080646 | -0.026784 | 0.038365 | -0.057066 | 0.040843 | 0.044377 | -0.11308 | 60.6534 | 60.6524 | 60.6992 | 60.662 | 60.8235 | 60.9893 | 60.5981 | 60.7858 | 0.094379 | -0.013051 | 0.052098 | -0.043333 | 0.054576 | 0.05811 | -0.099344 | 60.6672 | 60.6661 | 60.7129 | 60.6757 | 60.8372 | 61.0031 | 60.6118 | 60.7995 | -0.17003 | 0.055344 | -0.12428 | 0.1011
276.1875 | 121.907 | -60.8414 | 60.91 | 0.076067 | -0.017627 | 0.042944 | -0.057066 | 0.036265 | 0.039799 | -0.11765 | 60.6534 | 60.6478 | 60.6855 | 60.662 | 60.8326 | 60.9802 | 60.5661 | 60.795 | 0.0898 | -0.003894 | 0.056677 | -0.043333 | 0.049998 | 0.053532 | -0.10392 | 60.6672 | 60.6615 | 60.6992 | 60.6757 | 60.8464 | 60.9939 | 60.5798 | 60.8087 | -0.17919 | 0.087393 | -0.14717 | 0.11941
277.875 | 121.9254 | -60.9283 | 60.8322 | 0.080646 | -0.022205 | 0.038365 | -0.066223 | 0.040843 | 0.039799 | -0.11765 | 60.6534 | 60.6524 | 60.6946 | 60.6665 | 60.8235 | 60.9847 | 60.5661 | 60.7812 | 0.094379 | -0.008472 | 0.052098 | -0.05249 | 0.054576 | 0.053532 | -0.10392 | 60.6672 | 60.6661 | 60.7084 | 60.6803 | 60.8372 | 60.9985 | 60.5798 | 60.795 | -0.17003 | 0.087393 | -0.12886 | 0.12857
279.6094 | 121.9254 | -60.8826 | 60.8963 | 0.076067 | -0.022205 | 0.038365 | -0.061645 | 0.040843 | 0.044377 | -0.11308 | 60.6534 | 60.6478 | 60.69 | 60.662 | 60.8281 | 60.9802 | 60.5798 | 60.7904 | 0.0898 | -0.008472 | 0.052098 | -0.047912 | 0.054576 | 0.05811 | -0.099344 | 60.6672 | 60.6615 | 60.7038 | 60.6757 | 60.8418 | 60.9939 | 60.5935 | 60.8041 | -0.17461 | 0.073658 | -0.13802 | 0.11025
281.3281 | 122.0352 | -60.8963 | 60.7773 | 0.080646 | -0.031363 | 0.038365 | -0.066223 | 0.040843 | 0.044377 | -0.11765 | 60.6489 | 60.6478 | 60.6855 | 60.6528 | 60.8281 | 60.9802 | 60.5615 | 60.7812 | 0.094379 | -0.01763 | 0.052098 | -0.05249 | 0.054576 | 0.05811 | -0.10392 | 60.6626 | 60.6615 | 60.6992 | 60.6665 | 60.8418 | 60.9939 | 60.5752 | 60.795 | -0.17919 | 0.087393 | -0.1426 | 0.12399
283 | 122.0078 | -60.9009 | 60.7681 | 0.085224 | -0.022205 | 0.029208 | -0.066223 | 0.045421 | 0.044377 | -0.11308 | 60.6489 | 60.6478 | 60.69 | 60.6711 | 60.8189 | 60.9802 | 60.5706 | 60.7858 | 0.098957 | -0.008472 | 0.042941 | -0.05249 | 0.059154 | 0.05811 | -0.099344 | 60.6626 | 60.6615 | 60.7038 | 60.6849 | 60.8326 | 60.9939 | 60.5844 | 60.7995 | -0.17004 | 0.078236 | -0.12886 | 0.11941
284.7344 | 121.9391 | -60.8917 | 60.8643 | 0.085224 | -0.026784 | 0.042944 | -0.070802 | 0.045421 | 0.039799 | -0.11308 | 60.6534 | 60.6524 | 60.69 | 60.6665 | 60.8281 | 60.9756 | 60.5706 | 60.7767 | 0.098957 | -0.013051 | 0.056677 | -0.057069 | 0.059154 | 0.053532 | -0.099344 | 60.6672 | 60.6661 | 60.7038 | 60.6803 | 60.8418 | 60.9893 | 60.5844 | 60.7904 | -0.17461 | 0.082814 | -0.13802 | 0.11941
286.4219 | 121.9437 | -60.8871 | 60.9009 | 0.080646 | -0.026784 | 0.042944 | -0.066223 | 0.040843 | 0.044377 | -0.12223 | 60.6534 | 60.6478 | 60.6855 | 60.6665 | 60.8235 | 60.9802 | 60.5752 | 60.7812 | 0.094379 | -0.013051 | 0.056677 | -0.05249 | 0.054576 | 0.05811 | -0.1085 | 60.6672 | 60.6615 | 60.6992 | 60.6803 | 60.8372 | 60.9939 | 60.5889 | 60.795 | -0.17003 | 0.078236 | -0.13802 | 0.11025
288.1562 | 121.907 | -60.8688 | 60.9055 | 0.080646 | -0.031363 | 0.038365 | -0.061645 | 0.036265 | 0.044377 | -0.1085 | 60.6534 | 60.6432 | 60.69 | 60.6574 | 60.8281 | 60.9756 | 60.5752 | 60.7858 | 0.094379 | -0.01763 | 0.052098 | -0.047912 | 0.049998 | 0.05811 | -0.094766 | 60.6672 | 60.657 | 60.7038 | 60.6711 | 60.8418 | 60.9893 | 60.5889 | 60.7995 | -0.17461 | 0.078236 | -0.13802 | 0.11483
289.8281 | 121.9345 | -60.878 | 60.9146 | 0.076067 | -0.031363 | 0.042944 | -0.061645 | 0.036265 | 0.044377 | -0.12223 | 60.6534 | 60.6524 | 60.6855 | 60.662 | 60.8235 | 60.9756 | 60.5386 | 60.7812 | 0.0898 | -0.01763 | 0.056677 | -0.047912 | 0.049998 | 0.05811 | -0.1085 | 60.6672 | 60.6661 | 60.6992 | 60.6757 | 60.8372 | 60.9893 | 60.5523 | 60.795 | -0.17003 | 0.11486 | -0.13802 | 0.14688
291.5625 | 121.9894 | -60.9055 | 60.8047 | 0.076067 | -0.026784 | 0.033786 | -0.061645 | 0.036265 | 0.039799 | -0.11765 | 60.6534 | 60.6478 | 60.6809 | 60.6528 | 60.8143 | 60.9802 | 60.5615 | 60.7812 | 0.0898 | -0.013051 | 0.047519 | -0.047912 | 0.049998 | 0.053532 | -0.10392 | 60.6672 | 60.6615 | 60.6946 | 60.6665 | 60.8281 | 60.9939 | 60.5752 | 60.795 | -0.16088 | 0.091971 | -0.13344 | 0.11941
293.2969 | 121.8796 | -60.9192 | 60.8505 | 0.080646 | -0.035942 | 0.033786 | -0.066223 | 0.036265 | 0.048956 | -0.12223 | 60.6489 | 60.6432 | 60.6946 | 60.662 | 60.8189 | 60.9756 | 60.5477 | 60.7858 | 0.094379 | -0.022209 | 0.047519 | -0.05249 | 0.049998 | 0.062689 | -0.1085 | 60.6626 | 60.657 | 60.7084 | 60.6757 | 60.8326 | 60.9893 | 60.5615 | 60.7995 | -0.17004 | 0.10113 | -0.12428 | 0.14688
294.9688 | 121.8979 | -60.8688 | 60.9192 | 0.071489 | -0.031363 | 0.038365 | -0.057066 | 0.045421 | 0.044377 | -0.11765 | 60.6489 | 60.6478 | 60.69 | 60.6574 | 60.8235 | 60.9756 | 60.5432 | 60.7812 | 0.085222 | -0.01763 | 0.052098 | -0.043333 | 0.059154 | 0.05811 | -0.10392 | 60.6626 | 60.6615 | 60.7038 | 60.6711 | 60.8372 | 60.9893 | 60.5569 | 60.795 | -0.17461 | 0.10571 | -0.13344 | 0.14688
296.7031 | 122.0398 | -60.8871 | 60.7819 | 0.085224 | -0.022205 | 0.042944 | -0.061645 | 0.040843 | 0.053534 | -0.12223 | 60.6443 | 60.6524 | 60.6855 | 60.662 | 60.8143 | 60.9847 | 60.5386 | 60.7767 | 0.098957 | -0.008472 | 0.056677 | -0.047912 | 0.054576 | 0.067267 | -0.1085 | 60.658 | 60.6661 | 60.6992 | 60.6757 | 60.8281 | 60.9985 | 60.5523 | 60.7904 | -0.17004 | 0.10571 | -0.12886 | 0.14688
298.4375 | 121.9711 | -60.9375 | 60.8185 | 0.076067 | -0.026784 | 0.042944 | -0.061645 | 0.040843 | 0.044377 | -0.11308 | 60.6489 | 60.6432 | 60.6855 | 60.662 | 60.8143 | 60.9802 | 60.5386 | 60.7767 | 0.0898 | -0.013051 | 0.056677 | -0.047912 | 0.054576 | 0.05811 | -0.099344 | 60.6626 | 60.657 | 60.6992 | 60.6757 | 60.8281 | 60.9939 | 60.5523 | 60.7904 | -0.16546 | 0.11028 | -0.12886 | 0.14688
300.1719 | 121.9849 | -60.8963 | 60.8551 | 0.076067 | -0.026784 | 0.038365 | -0.061645 | 0.040843 | 0.039799 | -0.11308 | 60.6351 | 60.6387 | 60.6763 | 60.6574 | 60.8189 | 60.9802 | 60.5661 | 60.7767 | 0.0898 | -0.013051 | 0.052098 | -0.047912 | 0.054576 | 0.053532 | -0.099344 | 60.6489 | 60.6524 | 60.69 | 60.6711 | 60.8326 | 60.9939 | 60.5798 | 60.7904 | -0.18377 | 0.069079 | -0.1426 | 0.11025
301.8594 | 121.9574 | -60.8551 | 60.9055 | 0.076067 | -0.031363 | 0.038365 | -0.057066 | 0.036265 | 0.039799 | -0.11765 | 60.6443 | 60.6387 | 60.69 | 60.6528 | 60.8281 | 60.9756 | 60.5615 | 60.7812 | 0.0898 | -0.01763 | 0.052098 | -0.043333 | 0.049998 | 0.053532 | -0.10392 | 60.658 | 60.6524 | 60.7038 | 60.6665 | 60.8418 | 60.9893 | 60.5752 | 60.795 | -0.18377 | 0.082814 | -0.13802 | 0.12857
303.6094 | 122.0032 | -60.8963 | 60.8139 | 0.076067 | -0.026784 | 0.038365 | -0.066223 | 0.040843 | 0.044377 | -0.11765 | 60.6397 | 60.6432 | 60.6946 | 60.662 | 60.8189 | 60.9756 | 60.5477 | 60.7858 | 0.0898 | -0.013051 | 0.052098 | -0.05249 | 0.054576 | 0.05811 | -0.10392 | 60.6534 | 60.657 | 60.7084 | 60.6757 | 60.8326 | 60.9893 | 60.5615 | 60.7995 | -0.17919 | 0.091971 | -0.12428 | 0.14688
305.2656 | 122.0306 | -60.8414 | 60.8597 | 0.080646 | -0.026784 | 0.038365 | -0.057066 | 0.040843 | 0.048956 | -0.11765 | 60.6489 | 60.6432 | 60.69 | 60.6528 | 60.8281 | 60.9756 | 60.534 | 60.7812 | 0.094379 | -0.013051 | 0.052098 | -0.043333 | 0.054576 | 0.062689 | -0.10392 | 60.6626 | 60.657 | 60.7038 | 60.6665 | 60.8418 | 60.9893 | 60.5477 | 60.795 | -0.17919 | 0.11486 | -0.13802 | 0.15604
307 | 121.8887 | -60.9421 | 60.8551 | 0.076067 | -0.035942 | 0.038365 | -0.066223 | 0.040843 | 0.039799 | -0.11308 | 60.6489 | 60.6478 | 60.69 | 60.6528 | 60.8189 | 60.9756 | 60.5569 | 60.7767 | 0.0898 | -0.022209 | 0.052098 | -0.05249 | 0.054576 | 0.053532 | -0.099344 | 60.6626 | 60.6615 | 60.7038 | 60.6665 | 60.8326 | 60.9893 | 60.5706 | 60.7904 | -0.17004 | 0.091972 | -0.12886 | 0.13315
308.75 | 122.0123 | -60.8963 | 60.7956 | 0.071489 | -0.026784 | 0.038365 | -0.070802 | 0.040843 | 0.039799 | -0.11765 | 60.6489 | 60.6432 | 60.69 | 60.6574 | 60.8143 | 60.971 | 60.534 | 60.7767 | 0.085222 | -0.013051 | 0.052098 | -0.057069 | 0.054576 | 0.053532 | -0.10392 | 60.6626 | 60.657 | 60.7038 | 60.6711 | 60.8281 | 60.9847 | 60.5477 | 60.7904 | -0.16546 | 0.11486 | -0.12428 | 0.15604
310.4219 | 122.0123 | -60.8688 | 60.7636 | 0.076067 | -0.026784 | 0.033786 | -0.066223 | 0.040843 | 0.039799 | -0.11765 | 60.6443 | 60.6387 | 60.69 | 60.6528 | 60.8143 | 60.971 | 60.5294 | 60.7767 | 0.0898 | -0.013051 | 0.047519 | -0.05249 | 0.054576 | 0.053532 | -0.10392 | 60.658 | 60.6524 | 60.7038 | 60.6665 | 60.8281 | 60.9847 | 60.5432 | 60.7904 | -0.17004 | 0.11486 | -0.12428 | 0.16062
312.1562 | 121.8979 | -60.878 | 60.9146 | 0.076067 | -0.031363 | 0.033786 | -0.057066 | 0.045421 | 0.044377 | -0.11765 | 60.6443 | 60.6478 | 60.69 | 60.6482 | 60.8235 | 60.9756 | 60.5432 | 60.7812 | 0.0898 | -0.01763 | 0.047519 | -0.043333 | 0.059154 | 0.05811 | -0.10392 | 60.658 | 60.6615 | 60.7038 | 60.662 | 60.8372 | 60.9893 | 60.5569 | 60.795 | -0.17919 | 0.10113 | -0.13344 | 0.14688
313.8906 | 121.9757 | -60.8917 | 60.8185 | 0.080646 | -0.031363 | 0.038365 | -0.066223 | 0.036265 | 0.044377 | -0.11765 | 60.6397 | 60.6432 | 60.6809 | 60.6528 | 60.8143 | 60.971 | 60.5569 | 60.7721 | 0.094379 | -0.01763 | 0.052098 | -0.05249 | 0.049998 | 0.05811 | -0.10392 | 60.6534 | 60.657 | 60.6946 | 60.6665 | 60.8281 | 60.9847 | 60.5706 | 60.7858 | -0.17461 | 0.082815 | -0.13344 | 0.12399
315.5781 | 122.0352 | -60.8414 | 60.8551 | 0.076067 | -0.0451 | 0.033786 | -0.061645 | 0.036265 | 0.039799 | -0.11308 | 60.6397 | 60.6341 | 60.6855 | 60.6574 | 60.8143 | 60.971 | 60.5386 | 60.7767 | 0.0898 | -0.031367 | 0.047519 | -0.047912 | 0.049998 | 0.053532 | -0.099344 | 60.6534 | 60.6478 | 60.6992 | 60.6711 | 60.8281 | 60.9847 | 60.5523 | 60.7904 | -0.17461 | 0.10113 | -0.12886 | 0.14688
317.2969 | 121.9803 | -60.8414 | 60.8414 | 0.076067 | -0.040521 | 0.033786 | -0.066223 | 0.036265 | 0.048956 | -0.11765 | 60.6397 | 60.6387 | 60.6809 | 60.6482 | 60.8143 | 60.971 | 60.534 | 60.7721 | 0.0898 | -0.026788 | 0.047519 | -0.05249 | 0.049998 | 0.062689 | -0.10392 | 60.6534 | 60.6524 | 60.6946 | 60.662 | 60.8281 | 60.9847 | 60.5477 | 60.7858 | -0.17461 | 0.10571 | -0.13344 | 0.14688
319.0312 | 121.9711 | -60.8734 | 60.8414 | 0.076067 | -0.031363 | 0.033786 | -0.057066 | 0.036265 | 0.044377 | -0.11765 | 60.6489 | 60.6387 | 60.6809 | 60.6528 | 60.8143 | 60.9756 | 60.5249 | 60.7721 | 0.0898 | -0.01763 | 0.047519 | -0.043333 | 0.049998 | 0.05811 | -0.10392 | 60.6626 | 60.6524 | 60.6946 | 60.6665 | 60.8281 | 60.9893 | 60.5386 | 60.7858 | -0.16546 | 0.12402 | -0.13344 | 0.15604
320.7031 | 121.9894 | -60.8826 | 60.7956 | 0.080646 | -0.035942 | 0.029208 | -0.061645 | 0.040843 | 0.048956 | -0.1085 | 60.6397 | 60.6387 | 60.6809 | 60.6437 | 60.8098 | 60.9756 | 60.5386 | 60.7721 | 0.094379 | -0.022209 | 0.042941 | -0.047912 | 0.054576 | 0.062689 | -0.094766 | 60.6534 | 60.6524 | 60.6946 | 60.6574 | 60.8235 | 60.9893 | 60.5523 | 60.7858 | -0.17004 | 0.10113 | -0.12886 | 0.1423
322.4375 | 122.0032 | -60.8505 | 60.8459 | 0.076067 | -0.040521 | 0.038365 | -0.061645 | 0.036265 | 0.044377 | -0.12223 | 60.6443 | 60.6341 | 60.6809 | 60.6574 | 60.8143 | 60.971 | 60.5386 | 60.7767 | 0.0898 | -0.026788 | 0.052098 | -0.047912 | 0.049998 | 0.05811 | -0.1085 | 60.658 | 60.6478 | 60.6946 | 60.6711 | 60.8281 | 60.9847 | 60.5523 | 60.7904 | -0.17004 | 0.10571 | -0.13344 | 0.1423
324.1094 | 121.9711 | -60.878 | 60.8139 | 0.080646 | -0.035942 | 0.038365 | -0.061645 | 0.040843 | 0.044377 | -0.11765 | 60.6397 | 60.6387 | 60.6809 | 60.6482 | 60.8143 | 60.971 | 60.5294 | 60.7767 | 0.094379 | -0.022209 | 0.052098 | -0.047912 | 0.054576 | 0.05811 | -0.10392 | 60.6534 | 60.6524 | 60.6946 | 60.662 | 60.8281 | 60.9847 | 60.5432 | 60.7904 | -0.17461 | 0.11029 | -0.13344 | 0.15146
325.8438 | 121.9391 | -60.8917 | 60.8322 | 0.080646 | -0.040521 | 0.033786 | -0.061645 | 0.040843 | 0.048956 | -0.11308 | 60.6397 | 60.6387 | 60.6855 | 60.6437 | 60.8143 | 60.971 | 60.5386 | 60.7629 | 0.094379 | -0.026788 | 0.047519 | -0.047912 | 0.054576 | 0.062689 | -0.099344 | 60.6534 | 60.6524 | 60.6992 | 60.6574 | 60.8281 | 60.9847 | 60.5523 | 60.7767 | -0.17461 | 0.10113 | -0.12886 | 0.14688
327.5156 | 122.0123 | -60.8231 | 60.8322 | 0.080646 | -0.035942 | 0.038365 | -0.061645 | 0.040843 | 0.048956 | -0.11308 | 60.6306 | 60.6387 | 60.6809 | 60.6528 | 60.8143 | 60.9664 | 60.5294 | 60.7767 | 0.094379 | -0.022209 | 0.052098 | -0.047912 | 0.054576 | 0.062689 | -0.099344 | 60.6443 | 60.6524 | 60.6946 | 60.6665 | 60.8281 | 60.9802 | 60.5432 | 60.7904 | -0.18377 | 0.10113 | -0.13344 | 0.15146
329.25 | 121.9254 | -60.8597 | 60.9055 | 0.076067 | -0.0451 | 0.033786 | -0.061645 | 0.036265 | 0.048956 | -0.11308 | 60.6443 | 60.6432 | 60.6809 | 60.6482 | 60.8143 | 60.971 | 60.5432 | 60.7721 | 0.0898 | -0.031367 | 0.047519 | -0.047912 | 0.049998 | 0.062689 | -0.099344 | 60.658 | 60.657 | 60.6946 | 60.662 | 60.8281 | 60.9847 | 60.5569 | 60.7858 | -0.17004 | 0.10113 | -0.13344 | 0.13772
330.9844 | 122.0261 | -60.8505 | 60.8505 | 0.076067 | -0.040521 | 0.038365 | -0.061645 | 0.031687 | 0.044377 | -0.11308 | 60.6306 | 60.6387 | 60.6717 | 60.6528 | 60.8189 | 60.971 | 60.5432 | 60.7721 | 0.0898 | -0.026788 | 0.052098 | -0.047912 | 0.04542 | 0.05811 | -0.099344 | 60.6443 | 60.6524 | 60.6855 | 60.6665 | 60.8326 | 60.9847 | 60.5569 | 60.7858 | -0.18835 | 0.087393 | -0.14717 | 0.12857
332.6562 | 121.8704 | -60.91 | 60.8231 | 0.085224 | -0.035942 | 0.038365 | -0.061645 | 0.040843 | 0.048956 | -0.11765 | 60.6306 | 60.6341 | 60.6809 | 60.6482 | 60.8052 | 60.9664 | 60.5386 | 60.7721 | 0.098957 | -0.022209 | 0.052098 | -0.047912 | 0.054576 | 0.062689 | -0.10392 | 60.6443 | 60.6478 | 60.6946 | 60.662 | 60.8189 | 60.9802 | 60.5523 | 60.7858 | -0.17461 | 0.091971 | -0.12428 | 0.1423
334.3906 | 121.9025 | -60.8688 | 60.8871 | 0.076067 | -0.031363 | 0.033786 | -0.061645 | 0.040843 | 0.048956 | -0.11308 | 60.6351 | 60.6387 | 60.6855 | 60.6528 | 60.8098 | 60.971 | 60.5203 | 60.7675 | 0.0898 | -0.01763 | 0.047519 | -0.047912 | 0.054576 | 0.062689 | -0.099344 | 60.6489 | 60.6524 | 60.6992 | 60.6665 | 60.8235 | 60.9847 | 60.534 | 60.7812 | -0.17461 | 0.11486 | -0.12428 | 0.16519
336.125 | 121.9254 | -60.8826 | 60.8597 | 0.076067 | -0.040521 | 0.038365 | -0.070802 | 0.036265 | 0.039799 | -0.10392 | 60.6306 | 60.6387 | 60.6855 | 60.6437 | 60.8143 | 60.9619 | 60.5249 | 60.7675 | 0.0898 | -0.026788 | 0.052098 | -0.057069 | 0.049998 | 0.053532 | -0.090188 | 60.6443 | 60.6524 | 60.6992 | 60.6574 | 60.8281 | 60.9756 | 60.5386 | 60.7812 | -0.18377 | 0.10571 | -0.12886 | 0.16061
337.8594 | 121.9254 | -60.9146 | 60.8002 | 0.076067 | -0.026784 | 0.038365 | -0.057066 | 0.045421 | 0.048956 | -0.11765 | 60.6397 | 60.6341 | 60.6855 | 60.6482 | 60.8052 | 60.971 | 60.5477 | 60.7721 | 0.0898 | -0.013051 | 0.052098 | -0.043333 | 0.059154 | 0.062689 | -0.10392 | 60.6534 | 60.6478 | 60.6992 | 60.662 | 60.8189 | 60.9847 | 60.5615 | 60.7858 | -0.16546 | 0.091971 | -0.1197 | 0.13772
339.5469 | 121.9986 | -60.8505 | 60.8368 | 0.080646 | -0.040521 | 0.029208 | -0.070802 | 0.031687 | 0.039799 | -0.11308 | 60.6351 | 60.6341 | 60.6763 | 60.6528 | 60.8189 | 60.9619 | 60.5386 | 60.7675 | 0.094379 | -0.026788 | 0.042941 | -0.057069 | 0.04542 | 0.053532 | -0.099344 | 60.6489 | 60.6478 | 60.69 | 60.6665 | 60.8326 | 60.9756 | 60.5523 | 60.7812 | -0.18377 | 0.096549 | -0.1426 | 0.13772
341.2812 | 121.9162 | -60.8688 | 60.8368 | 0.076067 | -0.040521 | 0.038365 | -0.061645 | 0.040843 | 0.039799 | -0.11308 | 60.6306 | 60.6295 | 60.6809 | 60.6482 | 60.8143 | 60.9664 | 60.5294 | 60.7721 | 0.0898 | -0.026788 | 0.052098 | -0.047912 | 0.054576 | 0.053532 | -0.099344 | 60.6443 | 60.6432 | 60.6946 | 60.662 | 60.8281 | 60.9802 | 60.5432 | 60.7858 | -0.18377 | 0.10113 | -0.13344 | 0.15146
342.9375 | 121.8796 | -60.8643 | 60.8963 | 0.085224 | -0.035942 | 0.042944 | -0.066223 | 0.040843 | 0.044377 | -0.12223 | 60.6351 | 60.6341 | 60.6763 | 60.6528 | 60.8143 | 60.9619 | 60.5386 | 60.7675 | 0.098957 | -0.022209 | 0.056677 | -0.05249 | 0.054576 | 0.05811 | -0.1085 | 60.6489 | 60.6478 | 60.69 | 60.6665 | 60.8281 | 60.9756 | 60.5523 | 60.7812 | -0.17919 | 0.096549 | -0.13802 | 0.13772
344.6719 | 121.8567 | -60.8688 | 60.8963 | 0.071489 | -0.040521 | 0.029208 | -0.070802 | 0.045421 | 0.039799 | -0.11765 | 60.6351 | 60.6387 | 60.6717 | 60.6482 | 60.8098 | 60.9573 | 60.5249 | 60.7675 | 0.085222 | -0.026788 | 0.042941 | -0.057069 | 0.059154 | 0.053532 | -0.10392 | 60.6489 | 60.6524 | 60.6855 | 60.662 | 60.8235 | 60.971 | 60.5386 | 60.7812 | -0.17461 | 0.11028 | -0.13802 | 0.14688
346.4062 | 121.9574 | -60.8734 | 60.8231 | 0.080646 | -0.031363 | 0.038365 | -0.070802 | 0.036265 | 0.044377 | -0.11308 | 60.6306 | 60.6341 | 60.6809 | 60.6482 | 60.8098 | 60.971 | 60.5294 | 60.7721 | 0.094379 | -0.01763 | 0.052098 | -0.057069 | 0.049998 | 0.05811 | -0.099344 | 60.6443 | 60.6478 | 60.6946 | 60.662 | 60.8235 | 60.9847 | 60.5432 | 60.7858 | -0.17919 | 0.10113 | -0.12886 | 0.15146
348.0781 | 121.9208 | -60.9238 | 60.8047 | 0.076067 | -0.035942 | 0.038365 | -0.066223 | 0.045421 | 0.048956 | -0.11308 | 60.6351 | 60.6341 | 60.6809 | 60.6528 | 60.8006 | 60.9664 | 60.534 | 60.7583 | 0.0898 | -0.022209 | 0.052098 | -0.05249 | 0.059154 | 0.062689 | -0.099344 | 60.6489 | 60.6478 | 60.6946 | 60.6665 | 60.8143 | 60.9802 | 60.5477 | 60.7721 | -0.16546 | 0.10113 | -0.1197 | 0.14688
349.8281 | 121.8887 | -60.9329 | 60.8002 | 0.085224 | -0.031363 | 0.033786 | -0.057066 | 0.045421 | 0.039799 | -0.11308 | 60.6351 | 60.6295 | 60.6763 | 60.6482 | 60.796 | 60.9573 | 60.5249 | 60.7629 | 0.098957 | -0.01763 | 0.047519 | -0.043333 | 0.059154 | 0.053532 | -0.099344 | 60.6489 | 60.6432 | 60.69 | 60.662 | 60.8097 | 60.971 | 60.5386 | 60.7767 | -0.16088 | 0.11028 | -0.11971 | 0.15146
351.5 | 121.8842 | -60.9192 | 60.7956 | 0.080646 | -0.026784 | 0.038365 | -0.070802 | 0.045421 | 0.044377 | -0.11308 | 60.6397 | 60.6295 | 60.6717 | 60.6391 | 60.8098 | 60.9619 | 60.5203 | 60.7538 | 0.094379 | -0.013051 | 0.052098 | -0.057069 | 0.059154 | 0.05811 | -0.099344 | 60.6534 | 60.6432 | 60.6855 | 60.6528 | 60.8235 | 60.9756 | 60.534 | 60.7675 | -0.17004 | 0.11944 | -0.13802 | 0.15146
353.2188 | 121.9803 | -60.9055 | 60.759 | 0.085224 | -0.022205 | 0.033786 | -0.057066 | 0.045421 | 0.044377 | -0.11308 | 60.6306 | 60.6341 | 60.6809 | 60.6437 | 60.8006 | 60.9664 | 60.5203 | 60.7629 | 0.098957 | -0.008472 | 0.047519 | -0.043333 | 0.059154 | 0.05811 | -0.099344 | 60.6443 | 60.6478 | 60.6946 | 60.6574 | 60.8143 | 60.9802 | 60.534 | 60.7767 | -0.17004 | 0.11028 | -0.1197 | 0.16062
354.9531 | 121.8567 | -60.8459 | 60.9055 | 0.076067 | -0.031363 | 0.038365 | -0.070802 | 0.036265 | 0.048956 | -0.11765 | 60.6306 | 60.6341 | 60.6855 | 60.6528 | 60.8143 | 60.9619 | 60.5111 | 60.7675 | 0.0898 | -0.01763 | 0.052098 | -0.057069 | 0.049998 | 0.062689 | -0.10392 | 60.6443 | 60.6478 | 60.6992 | 60.6665 | 60.8281 | 60.9756 | 60.5249 | 60.7812 | -0.18377 | 0.11944 | -0.12886 | 0.17435
356.6875 | 121.9437 | -60.8826 | 60.8002 | 0.080646 | -0.026784 | 0.038365 | -0.066223 | 0.040843 | 0.048956 | -0.11308 | 60.626 | 60.6295 | 60.6809 | 60.6437 | 60.8052 | 60.9619 | 60.5294 | 60.7675 | 0.094379 | -0.013051 | 0.052098 | -0.05249 | 0.054576 | 0.062689 | -0.099344 | 60.6397 | 60.6432 | 60.6946 | 60.6574 | 60.8189 | 60.9756 | 60.5432 | 60.7812 | -0.17919 | 0.096549 | -0.12428 | 0.15146
358.3594 | 122.0123 | -60.8826 | 60.7864 | 0.080646 | -0.031363 | 0.033786 | -0.057066 | 0.040843 | 0.039799 | -0.11308 | 60.626 | 60.6341 | 60.6763 | 60.6482 | 60.8006 | 60.9619 | 60.5294 | 60.7583 | 0.094379 | -0.01763 | 0.047519 | -0.043333 | 0.054576 | 0.053532 | -0.099344 | 60.6397 | 60.6478 | 60.69 | 60.662 | 60.8143 | 60.9756 | 60.5432 | 60.7721 | -0.17461 | 0.096549 | -0.12428 | 0.14688
360.1094 | 121.8658 | -60.9283 | 60.8231 | 0.085224 | -0.031363 | 0.033786 | -0.061645 | 0.036265 | 0.044377 | -0.11308 | 60.6351 | 60.6295 | 60.6763 | 60.6437 | 60.8006 | 60.9573 | 60.5203 | 60.7538 | 0.098957 | -0.01763 | 0.047519 | -0.047912 | 0.049998 | 0.05811 | -0.099344 | 60.6489 | 60.6432 | 60.69 | 60.6574 | 60.8143 | 60.971 | 60.534 | 60.7675 | -0.16546 | 0.11486 | -0.12428 | 0.15604
361.8438 | 121.9574 | -60.8597 | 60.8047 | 0.080646 | -0.026784 | 0.029208 | -0.061645 | 0.045421 | 0.039799 | -0.12223 | 60.6306 | 60.6295 | 60.6763 | 60.6391 | 60.8006 | 60.9573 | 60.5249 | 60.7629 | 0.094379 | -0.013051 | 0.042941 | -0.047912 | 0.059154 | 0.053532 | -0.1085 | 60.6443 | 60.6432 | 60.69 | 60.6528 | 60.8143 | 60.971 | 60.5386 | 60.7767 | -0.17004 | 0.10571 | -0.12428 | 0.15146
363.5938 | 121.8613 | -60.9192 | 60.8414 | 0.085224 | -0.031363 | 0.033786 | -0.061645 | 0.036265 | 0.044377 | -0.11308 | 60.6351 | 60.6341 | 60.6809 | 60.6574 | 60.8006 | 60.9573 | 60.5249 | 60.7583 | 0.098957 | -0.01763 | 0.047519 | -0.047912 | 0.049998 | 0.05811 | -0.099344 | 60.6489 | 60.6478 | 60.6946 | 60.6711 | 60.8143 | 60.971 | 60.5386 | 60.7721 | -0.16546 | 0.11028 | -0.1197 | 0.15604
365.2656 | 121.9162 | -60.8734 | 60.8597 | 0.080646 | -0.026784 | 0.038365 | -0.057066 | 0.040843 | 0.039799 | -0.12223 | 60.6351 | 60.6295 | 60.6717 | 60.6482 | 60.8006 | 60.9619 | 60.5249 | 60.7583 | 0.094379 | -0.013051 | 0.052098 | -0.043333 | 0.054576 | 0.053532 | -0.1085 | 60.6489 | 60.6432 | 60.6855 | 60.662 | 60.8143 | 60.9756 | 60.5386 | 60.7721 | -0.16546 | 0.11028 | -0.12886 | 0.14688
367 | 121.9849 | -60.8826 | 60.759 | 0.085224 | -0.026784 | 0.029208 | -0.061645 | 0.045421 | 0.039799 | -0.11765 | 60.6306 | 60.6295 | 60.6763 | 60.6437 | 60.8006 | 60.9573 | 60.5203 | 60.7583 | 0.098957 | -0.013051 | 0.042941 | -0.047912 | 0.059154 | 0.053532 | -0.10392 | 60.6443 | 60.6432 | 60.69 | 60.6574 | 60.8143 | 60.971 | 60.534 | 60.7721 | -0.17004 | 0.11028 | -0.12428 | 0.15604
368.7344 | 121.9574 | -60.8963 | 60.791 | 0.085224 | -0.026784 | 0.038365 | -0.070802 | 0.045421 | 0.039799 | -0.11308 | 60.6397 | 60.6295 | 60.6763 | 60.6391 | 60.8006 | 60.9573 | 60.5249 | 60.7538 | 0.098957 | -0.013051 | 0.052098 | -0.057069 | 0.059154 | 0.053532 | -0.099344 | 60.6534 | 60.6432 | 60.69 | 60.6528 | 60.8143 | 60.971 | 60.5386 | 60.7675 | -0.16088 | 0.11486 | -0.12428 | 0.15146
370.4062 | 121.8613 | -60.9283 | 60.8231 | 0.076067 | -0.031363 | 0.033786 | -0.057066 | 0.036265 | 0.039799 | -0.11308 | 60.626 | 60.6295 | 60.6717 | 60.6437 | 60.8006 | 60.9619 | 60.5203 | 60.7583 | 0.0898 | -0.01763 | 0.047519 | -0.043333 | 0.049998 | 0.053532 | -0.099344 | 60.6397 | 60.6432 | 60.6855 | 60.6574 | 60.8143 | 60.9756 | 60.534 | 60.7721 | -0.17461 | 0.10571 | -0.12886 | 0.15146
372.1406 | 121.9757 | -60.8322 | 60.8185 | 0.076067 | -0.031363 | 0.038365 | -0.066223 | 0.040843 | 0.044377 | -0.12223 | 60.6306 | 60.6295 | 60.6763 | 60.6391 | 60.8143 | 60.9573 | 60.5249 | 60.7583 | 0.0898 | -0.01763 | 0.052098 | -0.05249 | 0.054576 | 0.05811 | -0.1085 | 60.6443 | 60.6432 | 60.69 | 60.6528 | 60.8281 | 60.971 | 60.5386 | 60.7721 | -0.18377 | 0.10571 | -0.13802 | 0.15146
373.875 | 121.9803 | -60.8322 | 60.8368 | 0.080646 | -0.031363 | 0.033786 | -0.061645 | 0.031687 | 0.039799 | -0.11308 | 60.626 | 60.6203 | 60.6717 | 60.6345 | 60.8052 | 60.9527 | 60.5203 | 60.7583 | 0.094379 | -0.01763 | 0.047519 | -0.047912 | 0.04542 | 0.053532 | -0.099344 | 60.6397 | 60.6341 | 60.6855 | 60.6482 | 60.8189 | 60.9664 | 60.534 | 60.7721 | -0.17919 | 0.10571 | -0.13344 | 0.15146
375.5469 | 121.9849 | -60.9009 | 60.7773 | 0.085224 | -0.026784 | 0.033786 | -0.061645 | 0.045421 | 0.044377 | -0.12223 | 60.626 | 60.6341 | 60.6763 | 60.6391 | 60.8098 | 60.9573 | 60.5203 | 60.7492 | 0.098957 | -0.013051 | 0.047519 | -0.047912 | 0.059154 | 0.05811 | -0.1085 | 60.6397 | 60.6478 | 60.69 | 60.6528 | 60.8235 | 60.971 | 60.534 | 60.7629 | -0.18377 | 0.10571 | -0.13344 | 0.15604
377.2812 | 122.0032 | -60.9009 | 60.7407 | 0.076067 | -0.031363 | 0.033786 | -0.057066 | 0.040843 | 0.053534 | -0.11308 | 60.6306 | 60.6249 | 60.6763 | 60.6391 | 60.8006 | 60.9527 | 60.5157 | 60.7492 | 0.0898 | -0.01763 | 0.047519 | -0.043333 | 0.054576 | 0.067267 | -0.099344 | 60.6443 | 60.6387 | 60.69 | 60.6528 | 60.8143 | 60.9664 | 60.5294 | 60.7629 | -0.17004 | 0.11486 | -0.12428 | 0.16062
379.0156 | 121.8384 | -60.9192 | 60.8139 | 0.085224 | -0.040521 | 0.033786 | -0.052488 | 0.045421 | 0.039799 | -0.11308 | 60.6306 | 60.6203 | 60.6763 | 60.6345 | 60.796 | 60.9573 | 60.5203 | 60.7538 | 0.098957 | -0.026788 | 0.047519 | -0.038755 | 0.059154 | 0.053532 | -0.099344 | 60.6443 | 60.6341 | 60.69 | 60.6482 | 60.8097 | 60.971 | 60.534 | 60.7675 | -0.16546 | 0.11028 | -0.11971 | 0.15604
380.75 | 121.8475 | -60.9238 | 60.8276 | 0.080646 | -0.031363 | 0.033786 | -0.057066 | 0.040843 | 0.039799 | -0.11308 | 60.6306 | 60.6295 | 60.6717 | 60.6345 | 60.8006 | 60.9527 | 60.5157 | 60.7538 | 0.094379 | -0.01763 | 0.047519 | -0.043333 | 0.054576 | 0.053532 | -0.099344 | 60.6443 | 60.6432 | 60.6855 | 60.6482 | 60.8143 | 60.9664 | 60.5294 | 60.7675 | -0.17004 | 0.11486 | -0.12886 | 0.15604
382.4062 | 121.8613 | -60.8459 | 60.9009 | 0.080646 | -0.031363 | 0.038365 | -0.052488 | 0.031687 | 0.039799 | -0.11308 | 60.6306 | 60.6249 | 60.6717 | 60.6391 | 60.8052 | 60.9481 | 60.5203 | 60.7583 | 0.094379 | -0.01763 | 0.052098 | -0.038755 | 0.04542 | 0.053532 | -0.099344 | 60.6443 | 60.6387 | 60.6855 | 60.6528 | 60.8189 | 60.9619 | 60.534 | 60.7721 | -0.17461 | 0.11028 | -0.13344 | 0.15146
384.1562 | 121.8658 | -60.8688 | 60.8688 | 0.080646 | -0.035942 | 0.038365 | -0.066223 | 0.049999 | 0.044377 | -0.11765 | 60.626 | 60.6295 | 60.6717 | 60.6482 | 60.8052 | 60.9527 | 60.5203 | 60.7492 | 0.094379 | -0.022209 | 0.052098 | -0.05249 | 0.063732 | 0.05811 | -0.10392 | 60.6397 | 60.6432 | 60.6855 | 60.662 | 60.8189 | 60.9664 | 60.534 | 60.7629 | -0.17919 | 0.10571 | -0.13344 | 0.15146
385.9062 | 121.843 | -60.8368 | 60.8917 | 0.085224 | -0.035942 | 0.042944 | -0.057066 | 0.036265 | 0.044377 | -0.11765 | 60.6214 | 60.6249 | 60.6809 | 60.6391 | 60.8052 | 60.9481 | 60.534 | 60.7492 | 0.098957 | -0.022209 | 0.056677 | -0.043333 | 0.049998 | 0.05811 | -0.10392 | 60.6351 | 60.6387 | 60.6946 | 60.6528 | 60.8189 | 60.9619 | 60.5477 | 60.7629 | -0.18377 | 0.087392 | -0.12428 | 0.14688
387.5781 | 121.8475 | -60.8551 | 60.9055 | 0.080646 | -0.026784 | 0.042944 | -0.057066 | 0.045421 | 0.044377 | -0.11308 | 60.626 | 60.6249 | 60.6672 | 60.6345 | 60.8052 | 60.9481 | 60.5157 | 60.7538 | 0.094379 | -0.013051 | 0.056677 | -0.043333 | 0.059154 | 0.05811 | -0.099344 | 60.6397 | 60.6387 | 60.6809 | 60.6482 | 60.8189 | 60.9619 | 60.5294 | 60.7675 | -0.17919 | 0.11028 | -0.13802 | 0.15146
389.2969 | 121.8613 | -60.91 | 60.8093 | 0.071489 | -0.035942 | 0.029208 | -0.057066 | 0.049999 | 0.044377 | -0.11308 | 60.6306 | 60.6295 | 60.6672 | 60.6391 | 60.7914 | 60.9481 | 60.5294 | 60.7538 | 0.085222 | -0.022209 | 0.042941 | -0.043333 | 0.063732 | 0.05811 | -0.099344 | 60.6443 | 60.6432 | 60.6809 | 60.6528 | 60.8052 | 60.9619 | 60.5432 | 60.7675 | -0.16088 | 0.10113 | -0.12428 | 0.13772
391.0312 | 121.8475 | -60.91 | 60.8368 | 0.076067 | -0.026784 | 0.042944 | -0.061645 | 0.045421 | 0.048956 | -0.11765 | 60.626 | 60.6249 | 60.6717 | 60.6345 | 60.796 | 60.9527 | 60.5249 | 60.7446 | 0.0898 | -0.013051 | 0.056677 | -0.047912 | 0.059154 | 0.062689 | -0.10392 | 60.6397 | 60.6387 | 60.6855 | 60.6482 | 60.8097 | 60.9664 | 60.5386 | 60.7583 | -0.17004 | 0.10113 | -0.12428 | 0.14688
392.7656 | 121.875 | -60.9009 | 60.7773 | 0.080646 | -0.035942 | 0.029208 | -0.066223 | 0.040843 | 0.044377 | -0.11308 | 60.626 | 60.6203 | 60.6717 | 60.6345 | 60.7914 | 60.9481 | 60.5203 | 60.74 | 0.094379 | -0.022209 | 0.042941 | -0.05249 | 0.054576 | 0.05811 | -0.099344 | 60.6397 | 60.6341 | 60.6855 | 60.6482 | 60.8052 | 60.9619 | 60.534 | 60.7538 | -0.16546 | 0.10571 | -0.1197 | 0.15146
394.4375 | 121.9254 | -60.8231 | 60.8276 | 0.080646 | -0.035942 | 0.029208 | -0.057066 | 0.049999 | 0.048956 | -0.11765 | 60.6306 | 60.6249 | 60.6717 | 60.6299 | 60.796 | 60.9481 | 60.5203 | 60.7492 | 0.094379 | -0.022209 | 0.042941 | -0.043333 | 0.063732 | 0.062689 | -0.10392 | 60.6443 | 60.6387 | 60.6855 | 60.6436 | 60.8097 | 60.9619 | 60.534 | 60.7629 | -0.16546 | 0.11028 | -0.12428 | 0.15146
396.1875 | 121.9025 | -60.8734 | 60.8688 | 0.085224 | -0.035942 | 0.029208 | -0.066223 | 0.045421 | 0.044377 | -0.11765 | 60.6306 | 60.6203 | 60.6763 | 60.6391 | 60.8006 | 60.9481 | 60.5203 | 60.7446 | 0.098957 | -0.022209 | 0.042941 | -0.05249 | 0.059154 | 0.05811 | -0.10392 | 60.6443 | 60.6341 | 60.69 | 60.6528 | 60.8143 | 60.9619 | 60.534 | 60.7583 | -0.17004 | 0.11028 | -0.12428 | 0.15604
397.9375 | 121.8613 | -60.8459 | 60.9055 | 0.076067 | -0.031363 | 0.029208 | -0.052488 | 0.045421 | 0.044377 | -0.12223 | 60.626 | 60.6249 | 60.6763 | 60.6345 | 60.796 | 60.9527 | 60.5203 | 60.7583 | 0.0898 | -0.01763 | 0.042941 | -0.038755 | 0.059154 | 0.05811 | -0.1085 | 60.6397 | 60.6387 | 60.69 | 60.6482 | 60.8097 | 60.9664 | 60.534 | 60.7721 | -0.17004 | 0.10571 | -0.11971 | 0.15604
399.625 | 121.843 | -60.91 | 60.8139 | 0.076067 | -0.040521 | 0.029208 | -0.061645 | 0.045421 | 0.048956 | -0.12223 | 60.6306 | 60.6249 | 60.6672 | 60.6391 | 60.796 | 60.9527 | 60.5111 | 60.7538 | 0.0898 | -0.026788 | 0.042941 | -0.047912 | 0.059154 | 0.062689 | -0.1085 | 60.6443 | 60.6387 | 60.6809 | 60.6528 | 60.8097 | 60.9664 | 60.5249 | 60.7675 | -0.16546 | 0.11944 | -0.12886 | 0.15604
401.3594 | 121.9482 | -60.8414 | 60.7864 | 0.080646 | -0.031363 | 0.038365 | -0.070802 | 0.045421 | 0.048956 | -0.11308 | 60.6214 | 60.6158 | 60.6717 | 60.6299 | 60.796 | 60.9435 | 60.5157 | 60.7492 | 0.094379 | -0.01763 | 0.052098 | -0.057069 | 0.059154 | 0.062689 | -0.099344 | 60.6351 | 60.6295 | 60.6855 | 60.6436 | 60.8097 | 60.9573 | 60.5294 | 60.7629 | -0.17462 | 0.10571 | -0.12428 | 0.15604
403.0938 | 121.8292 | -60.8597 | 60.9009 | 0.089802 | -0.035942 | 0.038365 | -0.061645 | 0.049999 | 0.039799 | -0.11308 | 60.6214 | 60.6249 | 60.6672 | 60.6391 | 60.8006 | 60.9435 | 60.5065 | 60.74 | 0.10354 | -0.022209 | 0.052098 | -0.047912 | 0.063732 | 0.053532 | -0.099344 | 60.6351 | 60.6387 | 60.6809 | 60.6528 | 60.8143 | 60.9573 | 60.5203 | 60.7538 | -0.17919 | 0.11486 | -0.13344 | 0.16062
404.8281 | 121.8475 | -60.8505 | 60.8963 | 0.080646 | -0.0451 | 0.029208 | -0.057066 | 0.049999 | 0.039799 | -0.11765 | 60.6214 | 60.6203 | 60.6717 | 60.6299 | 60.8052 | 60.9481 | 60.5065 | 60.7492 | 0.094379 | -0.031367 | 0.042941 | -0.043333 | 0.063732 | 0.053532 | -0.10392 | 60.6351 | 60.6341 | 60.6855 | 60.6436 | 60.8189 | 60.9619 | 60.5203 | 60.7629 | -0.18377 | 0.11486 | -0.13344 | 0.1652
406.5 | 121.9208 | -60.8047 | 60.8597 | 0.080646 | -0.049678 | 0.038365 | -0.057066 | 0.036265 | 0.044377 | -0.11308 | 60.6214 | 60.6158 | 60.6626 | 60.6299 | 60.8052 | 60.9435 | 60.5249 | 60.7446 | 0.094379 | -0.035945 | 0.052098 | -0.043333 | 0.049998 | 0.05811 | -0.099344 | 60.6351 | 60.6295 | 60.6763 | 60.6436 | 60.8189 | 60.9573 | 60.5386 | 60.7583 | -0.18377 | 0.096549 | -0.1426 | 0.13772
408.2344 | 121.9803 | -60.8917 | 60.7452 | 0.085224 | -0.035942 | 0.033786 | -0.061645 | 0.036265 | 0.039799 | -0.12223 | 60.6306 | 60.6158 | 60.6672 | 60.6345 | 60.8006 | 60.9481 | 60.5157 | 60.7446 | 0.098957 | -0.022209 | 0.047519 | -0.047912 | 0.049998 | 0.053532 | -0.1085 | 60.6443 | 60.6295 | 60.6809 | 60.6482 | 60.8143 | 60.9619 | 60.5294 | 60.7583 | -0.17004 | 0.11486 | -0.13344 | 0.15146
409.9688 | 121.962 | -60.8047 | 60.8368 | 0.071489 | -0.0451 | 0.033786 | -0.061645 | 0.040843 | 0.044377 | -0.11765 | 60.626 | 60.6158 | 60.6672 | 60.6299 | 60.796 | 60.9435 | 60.5157 | 60.7446 | 0.085222 | -0.031367 | 0.047519 | -0.047912 | 0.054576 | 0.05811 | -0.10392 | 60.6397 | 60.6295 | 60.6809 | 60.6436 | 60.8097 | 60.9573 | 60.5294 | 60.7583 | -0.17004 | 0.11028 | -0.12886 | 0.15146
411.7031 | 121.9437 | -60.8734 | 60.759 | 0.080646 | -0.040521 | 0.038365 | -0.057066 | 0.049999 | 0.044377 | -0.11765 | 60.626 | 60.6203 | 60.6672 | 60.6253 | 60.796 | 60.9435 | 60.5157 | 60.7446 | 0.094379 | -0.026788 | 0.052098 | -0.043333 | 0.063732 | 0.05811 | -0.10392 | 60.6397 | 60.6341 | 60.6809 | 60.6391 | 60.8097 | 60.9573 | 60.5294 | 60.7583 | -0.17004 | 0.11028 | -0.12886 | 0.15146
413.375 | 121.843 | -60.9238 | 60.8139 | 0.080646 | -0.049678 | 0.033786 | -0.061645 | 0.049999 | 0.039799 | -0.11308 | 60.626 | 60.6158 | 60.658 | 60.6345 | 60.796 | 60.9481 | 60.5111 | 60.7355 | 0.094379 | -0.035945 | 0.047519 | -0.047912 | 0.063732 | 0.053532 | -0.099344 | 60.6397 | 60.6295 | 60.6717 | 60.6482 | 60.8097 | 60.9619 | 60.5249 | 60.7492 | -0.17004 | 0.11486 | -0.13802 | 0.14688
415.125 | 121.8658 | -60.8505 | 60.8871 | 0.080646 | -0.049678 | 0.038365 | -0.057066 | 0.040843 | 0.044377 | -0.12223 | 60.6168 | 60.6158 | 60.6672 | 60.6299 | 60.7914 | 60.939 | 60.502 | 60.74 | 0.094379 | -0.035945 | 0.052098 | -0.043333 | 0.054576 | 0.05811 | -0.1085 | 60.6306 | 60.6295 | 60.6809 | 60.6436 | 60.8052 | 60.9527 | 60.5157 | 60.7538 | -0.17462 | 0.11486 | -0.12428 | 0.16519
416.8594 | 121.9528 | -60.8414 | 60.8093 | 0.076067 | -0.049678 | 0.024629 | -0.061645 | 0.040843 | 0.039799 | -0.11308 | 60.626 | 60.6158 | 60.6672 | 60.6253 | 60.796 | 60.9481 | 60.5065 | 60.7446 | 0.0898 | -0.035945 | 0.038362 | -0.047912 | 0.054576 | 0.053532 | -0.099344 | 60.6397 | 60.6295 | 60.6809 | 60.6391 | 60.8097 | 60.9619 | 60.5203 | 60.7583 | -0.17004 | 0.11944 | -0.12886 | 0.16062
418.5312 | 121.9803 | -60.8185 | 60.8414 | 0.076067 | -0.049678 | 0.029208 | -0.066223 | 0.045421 | 0.053534 | -0.11308 | 60.6214 | 60.6203 | 60.6626 | 60.6299 | 60.8098 | 60.9435 | 60.5111 | 60.7492 | 0.0898 | -0.035945 | 0.042941 | -0.05249 | 0.059154 | 0.067267 | -0.099344 | 60.6351 | 60.6341 | 60.6763 | 60.6436 | 60.8235 | 60.9573 | 60.5249 | 60.7629 | -0.18835 | 0.11028 | -0.14717 | 0.15146
420.2656 | 121.9528 | -60.8322 | 60.8368 | 0.080646 | -0.040521 | 0.029208 | -0.061645 | 0.040843 | 0.048956 | -0.12223 | 60.6214 | 60.6158 | 60.6672 | 60.6299 | 60.796 | 60.9435 | 60.5111 | 60.74 | 0.094379 | -0.026788 | 0.042941 | -0.047912 | 0.054576 | 0.062689 | -0.1085 | 60.6351 | 60.6295 | 60.6809 | 60.6436 | 60.8097 | 60.9573 | 60.5249 | 60.7538 | -0.17462 | 0.11028 | -0.12886 | 0.15604
421.9531 | 121.843 | -60.9009 | 60.8047 | 0.076067 | -0.035942 | 0.029208 | -0.061645 | 0.045421 | 0.039799 | -0.11765 | 60.6168 | 60.6295 | 60.6672 | 60.6345 | 60.796 | 60.9344 | 60.4974 | 60.7446 | 0.0898 | -0.022209 | 0.042941 | -0.047912 | 0.059154 | 0.053532 | -0.10392 | 60.6306 | 60.6432 | 60.6809 | 60.6482 | 60.8097 | 60.9481 | 60.5111 | 60.7583 | -0.17919 | 0.11944 | -0.12886 | 0.16977
423.6875 | 121.9208 | -60.8734 | 60.7681 | 0.080646 | -0.035942 | 0.029208 | -0.061645 | 0.045421 | 0.044377 | -0.11308 | 60.626 | 60.6203 | 60.6626 | 60.6391 | 60.796 | 60.9435 | 60.5065 | 60.7355 | 0.094379 | -0.022209 | 0.042941 | -0.047912 | 0.059154 | 0.05811 | -0.099344 | 60.6397 | 60.6341 | 60.6763 | 60.6528 | 60.8097 | 60.9573 | 60.5203 | 60.7492 | -0.17004 | 0.11944 | -0.13344 | 0.15604
425.4219 | 121.8475 | -60.9009 | 60.8276 | 0.085224 | -0.049678 | 0.033786 | -0.061645 | 0.045421 | 0.044377 | -0.11765 | 60.6214 | 60.6249 | 60.6672 | 60.6299 | 60.796 | 60.9481 | 60.4974 | 60.7309 | 0.098957 | -0.035945 | 0.047519 | -0.047912 | 0.059154 | 0.05811 | -0.10392 | 60.6351 | 60.6387 | 60.6809 | 60.6436 | 60.8097 | 60.9619 | 60.5111 | 60.7446 | -0.17462 | 0.12402 | -0.12886 | 0.16977
427.1406 | 121.9528 | -60.8826 | 60.759 | 0.080646 | -0.035942 | 0.029208 | -0.061645 | 0.036265 | 0.039799 | -0.11765 | 60.6214 | 60.6158 | 60.6626 | 60.6345 | 60.7869 | 60.9298 | 60.502 | 60.7355 | 0.094379 | -0.022209 | 0.042941 | -0.047912 | 0.049998 | 0.053532 | -0.10392 | 60.6351 | 60.6295 | 60.6763 | 60.6482 | 60.8006 | 60.9435 | 60.5157 | 60.7492 | -0.16546 | 0.11944 | -0.12428 | 0.16062
428.875 | 121.9299 | -60.7956 | 60.8597 | 0.076067 | -0.0451 | 0.029208 | -0.066223 | 0.045421 | 0.039799 | -0.11765 | 60.6214 | 60.6249 | 60.6672 | 60.6299 | 60.796 | 60.9435 | 60.5065 | 60.7355 | 0.0898 | -0.031367 | 0.042941 | -0.05249 | 0.059154 | 0.053532 | -0.10392 | 60.6351 | 60.6387 | 60.6809 | 60.6436 | 60.8097 | 60.9573 | 60.5203 | 60.7492 | -0.17462 | 0.11486 | -0.12886 | 0.16062
430.5625 | 121.8521 | -60.91 | 60.8093 | 0.080646 | -0.0451 | 0.038365 | -0.061645 | 0.045421 | 0.048956 | -0.11765 | 60.626 | 60.6203 | 60.6672 | 60.6345 | 60.7914 | 60.939 | 60.4974 | 60.7309 | 0.094379 | -0.031367 | 0.052098 | -0.047912 | 0.059154 | 0.062689 | -0.10392 | 60.6397 | 60.6341 | 60.6809 | 60.6482 | 60.8052 | 60.9527 | 60.5111 | 60.7446 | -0.16546 | 0.1286 | -0.12428 | 0.16977
432.2969 | 121.9574 | -60.8643 | 60.7498 | 0.076067 | -0.035942 | 0.033786 | -0.061645 | 0.045421 | 0.048956 | -0.11308 | 60.6122 | 60.6295 | 60.6672 | 60.6391 | 60.7823 | 60.939 | 60.4974 | 60.74 | 0.0898 | -0.022209 | 0.047519 | -0.047912 | 0.059154 | 0.062689 | -0.099344 | 60.626 | 60.6432 | 60.6809 | 60.6528 | 60.796 | 60.9527 | 60.5111 | 60.7538 | -0.17004 | 0.11486 | -0.11513 | 0.16977
434.0312 | 121.8384 | -60.8276 | 60.91 | 0.076067 | -0.040521 | 0.029208 | -0.070802 | 0.045421 | 0.044377 | -0.11765 | 60.6214 | 60.6158 | 60.6672 | 60.6345 | 60.7914 | 60.939 | 60.502 | 60.74 | 0.0898 | -0.026788 | 0.042941 | -0.057069 | 0.059154 | 0.05811 | -0.10392 | 60.6351 | 60.6295 | 60.6809 | 60.6482 | 60.8052 | 60.9527 | 60.5157 | 60.7538 | -0.17004 | 0.11944 | -0.12428 | 0.16519
435.7812 | 121.8384 | -60.9055 | 60.791 | 0.085224 | -0.049678 | 0.033786 | -0.052488 | 0.045421 | 0.048956 | -0.11765 | 60.6168 | 60.6203 | 60.6626 | 60.6391 | 60.7914 | 60.939 | 60.502 | 60.7309 | 0.098957 | -0.035945 | 0.047519 | -0.038755 | 0.059154 | 0.062689 | -0.10392 | 60.6306 | 60.6341 | 60.6763 | 60.6528 | 60.8052 | 60.9527 | 60.5157 | 60.7446 | -0.17462 | 0.11486 | -0.12886 | 0.16062
437.4531 | 121.8658 | -60.8597 | 60.8185 | 0.085224 | -0.0451 | 0.029208 | -0.057066 | 0.045421 | 0.048956 | -0.1085 | 60.6168 | 60.6112 | 60.6672 | 60.6299 | 60.7914 | 60.939 | 60.502 | 60.7355 | 0.098957 | -0.031367 | 0.042941 | -0.043333 | 0.059154 | 0.062689 | -0.094766 | 60.6306 | 60.6249 | 60.6809 | 60.6436 | 60.8052 | 60.9527 | 60.5157 | 60.7492 | -0.17462 | 0.11486 | -0.12428 | 0.16519
439.1875 | 121.843 | -60.9009 | 60.8139 | 0.085224 | -0.0451 | 0.038365 | -0.061645 | 0.040843 | 0.035221 | -0.12223 | 60.6122 | 60.6158 | 60.6672 | 60.6299 | 60.7914 | 60.9435 | 60.502 | 60.74 | 0.098957 | -0.031367 | 0.052098 | -0.047912 | 0.054576 | 0.048954 | -0.1085 | 60.626 | 60.6295 | 60.6809 | 60.6436 | 60.8052 | 60.9573 | 60.5157 | 60.7538 | -0.17919 | 0.11028 | -0.12428 | 0.16519
440.9375 | 121.907 | -60.8459 | 60.7773 | 0.076067 | -0.054257 | 0.038365 | -0.061645 | 0.049999 | 0.048956 | -0.11308 | 60.6168 | 60.6158 | 60.6763 | 60.6345 | 60.7869 | 60.9344 | 60.5157 | 60.74 | 0.0898 | -0.040524 | 0.052098 | -0.047912 | 0.063732 | 0.062689 | -0.099344 | 60.6306 | 60.6295 | 60.69 | 60.6482 | 60.8006 | 60.9481 | 60.5294 | 60.7538 | -0.17004 | 0.10113 | -0.11055 | 0.16062
442.6094 | 121.8155 | -60.91 | 60.8231 | 0.080646 | -0.049678 | 0.033786 | -0.057066 | 0.040843 | 0.044377 | -0.1085 | 60.6214 | 60.6158 | 60.6672 | 60.6345 | 60.7869 | 60.9344 | 60.4974 | 60.7309 | 0.094379 | -0.035945 | 0.047519 | -0.043333 | 0.054576 | 0.05811 | -0.094766 | 60.6351 | 60.6295 | 60.6809 | 60.6482 | 60.8006 | 60.9481 | 60.5111 | 60.7446 | -0.16546 | 0.12402 | -0.11971 | 0.16977
444.3281 | 121.907 | -60.8551 | 60.7819 | 0.080646 | -0.049678 | 0.033786 | -0.066223 | 0.045421 | 0.039799 | -0.11765 | 60.6168 | 60.6158 | 60.6626 | 60.6299 | 60.7869 | 60.9344 | 60.5065 | 60.7355 | 0.094379 | -0.035945 | 0.047519 | -0.05249 | 0.059154 | 0.053532 | -0.10392 | 60.6306 | 60.6295 | 60.6763 | 60.6436 | 60.8006 | 60.9481 | 60.5203 | 60.7492 | -0.17004 | 0.11028 | -0.12428 | 0.15604
446.0625 | 121.8933 | -60.8368 | 60.8688 | 0.080646 | -0.058836 | 0.038365 | -0.061645 | 0.036265 | 0.044377 | -0.12223 | 60.6214 | 60.6203 | 60.6626 | 60.6253 | 60.796 | 60.939 | 60.5065 | 60.74 | 0.094379 | -0.045103 | 0.052098 | -0.047912 | 0.049998 | 0.05811 | -0.1085 | 60.6351 | 60.6341 | 60.6763 | 60.6391 | 60.8097 | 60.9527 | 60.5203 | 60.7538 | -0.17462 | 0.11486 | -0.13344 | 0.15604
447.7969 | 121.8063 | -60.8917 | 60.8139 | 0.076067 | -0.054257 | 0.038365 | -0.057066 | 0.040843 | 0.044377 | -0.10392 | 60.6168 | 60.6112 | 60.658 | 60.6208 | 60.7869 | 60.939 | 60.4974 | 60.7355 | 0.0898 | -0.040524 | 0.052098 | -0.043333 | 0.054576 | 0.05811 | -0.090188 | 60.6306 | 60.6249 | 60.6717 | 60.6345 | 60.8006 | 60.9527 | 60.5111 | 60.7492 | -0.17004 | 0.11944 | -0.12886 | 0.16062
449.4688 | 121.8384 | -60.8185 | 60.8688 | 0.080646 | -0.049678 | 0.033786 | -0.061645 | 0.036265 | 0.044377 | -0.11765 | 60.6214 | 60.6158 | 60.6717 | 60.6253 | 60.796 | 60.939 | 60.502 | 60.7355 | 0.094379 | -0.035945 | 0.047519 | -0.047912 | 0.049998 | 0.05811 | -0.10392 | 60.6351 | 60.6295 | 60.6855 | 60.6391 | 60.8097 | 60.9527 | 60.5157 | 60.7492 | -0.17462 | 0.11944 | -0.12428 | 0.16977
451.2031 | 121.8521 | -60.878 | 60.8002 | 0.076067 | -0.0451 | 0.042944 | -0.061645 | 0.045421 | 0.053534 | -0.11765 | 60.6168 | 60.6203 | 60.6626 | 60.6253 | 60.7869 | 60.9344 | 60.5065 | 60.7217 | 0.0898 | -0.031367 | 0.056677 | -0.047912 | 0.059154 | 0.067267 | -0.10392 | 60.6306 | 60.6341 | 60.6763 | 60.6391 | 60.8006 | 60.9481 | 60.5203 | 60.7355 | -0.17004 | 0.11028 | -0.12428 | 0.15604
452.9375 | 121.8933 | -60.8459 | 60.8368 | 0.080646 | -0.049678 | 0.038365 | -0.061645 | 0.045421 | 0.044377 | -0.11308 | 60.6122 | 60.6158 | 60.6672 | 60.6299 | 60.7869 | 60.939 | 60.4928 | 60.7355 | 0.094379 | -0.035945 | 0.052098 | -0.047912 | 0.059154 | 0.05811 | -0.099344 | 60.626 | 60.6295 | 60.6809 | 60.6436 | 60.8006 | 60.9527 | 60.5065 | 60.7492 | -0.17462 | 0.11944 | -0.11971 | 0.17435
454.6719 | 121.9437 | -60.791 | 60.8414 | 0.080646 | -0.058836 | 0.033786 | -0.066223 | 0.040843 | 0.044377 | -0.12223 | 60.6214 | 60.6158 | 60.6672 | 60.6208 | 60.796 | 60.9344 | 60.502 | 60.74 | 0.094379 | -0.045103 | 0.047519 | -0.05249 | 0.054576 | 0.05811 | -0.1085 | 60.6351 | 60.6295 | 60.6809 | 60.6345 | 60.8097 | 60.9481 | 60.5157 | 60.7538 | -0.17462 | 0.11944 | -0.12886 | 0.16519
456.3594 | 121.8704 | -60.8231 | 60.8643 | 0.080646 | -0.058836 | 0.038365 | -0.061645 | 0.045421 | 0.048956 | -0.1085 | 60.6168 | 60.6203 | 60.6626 | 60.6253 | 60.7914 | 60.9298 | 60.502 | 60.7355 | 0.094379 | -0.045103 | 0.052098 | -0.047912 | 0.059154 | 0.062689 | -0.094766 | 60.6306 | 60.6341 | 60.6763 | 60.6391 | 60.8052 | 60.9435 | 60.5157 | 60.7492 | -0.17462 | 0.11486 | -0.12886 | 0.16062
458.0938 | 121.8796 | -60.9009 | 60.7681 | 0.080646 | -0.058836 | 0.042944 | -0.061645 | 0.036265 | 0.039799 | -0.11308 | 60.6077 | 60.6158 | 60.6672 | 60.6299 | 60.7869 | 60.9344 | 60.4928 | 60.7263 | 0.094379 | -0.045103 | 0.056677 | -0.047912 | 0.049998 | 0.053532 | -0.099344 | 60.6214 | 60.6295 | 60.6809 | 60.6436 | 60.8006 | 60.9481 | 60.5065 | 60.74 | -0.17919 | 0.11486 | -0.11971 | 0.17435
459.8281 | 121.9116 | -60.8505 | 60.7636 | 0.080646 | -0.049678 | 0.038365 | -0.066223 | 0.036265 | 0.039799 | -0.12223 | 60.6168 | 60.6066 | 60.6626 | 60.6208 | 60.7869 | 60.939 | 60.502 | 60.7309 | 0.094379 | -0.035945 | 0.052098 | -0.05249 | 0.049998 | 0.053532 | -0.1085 | 60.6306 | 60.6203 | 60.6763 | 60.6345 | 60.8006 | 60.9527 | 60.5157 | 60.7446 | -0.17004 | 0.11486 | -0.12428 | 0.16062
461.5625 | 121.8109 | -60.91 | 60.7864 | 0.076067 | -0.049678 | 0.029208 | -0.057066 | 0.045421 | 0.053534 | -0.11308 | 60.6122 | 60.6158 | 60.6672 | 60.6299 | 60.7914 | 60.9298 | 60.502 | 60.7217 | 0.0898 | -0.035945 | 0.042941 | -0.043333 | 0.059154 | 0.067267 | -0.099344 | 60.626 | 60.6295 | 60.6809 | 60.6436 | 60.8052 | 60.9435 | 60.5157 | 60.7355 | -0.17919 | 0.11028 | -0.12428 | 0.16519
463.2969 | 121.9528 | -60.7956 | 60.8414 | 0.080646 | -0.054257 | 0.038365 | -0.061645 | 0.049999 | 0.035221 | -0.11765 | 60.6168 | 60.6066 | 60.6626 | 60.6253 | 60.7914 | 60.939 | 60.4882 | 60.7309 | 0.094379 | -0.040524 | 0.052098 | -0.047912 | 0.063732 | 0.048954 | -0.10392 | 60.6306 | 60.6203 | 60.6763 | 60.6391 | 60.8052 | 60.9527 | 60.502 | 60.7446 | -0.17462 | 0.1286 | -0.12886 | 0.17435
464.9688 | 121.962 | -60.791 | 60.8185 | 0.076067 | -0.054257 | 0.033786 | -0.061645 | 0.045421 | 0.044377 | -0.11308 | 60.6214 | 60.6112 | 60.6672 | 60.6208 | 60.7823 | 60.9252 | 60.5065 | 60.7309 | 0.0898 | -0.040524 | 0.047519 | -0.047912 | 0.059154 | 0.05811 | -0.099344 | 60.6351 | 60.6249 | 60.6809 | 60.6345 | 60.796 | 60.939 | 60.5203 | 60.7446 | -0.16088 | 0.11486 | -0.11513 | 0.16062
466.7188 | 121.8338 | -60.8368 | 60.8597 | 0.076067 | -0.054257 | 0.033786 | -0.057066 | 0.040843 | 0.048956 | -0.11308 | 60.6168 | 60.6112 | 60.6672 | 60.6253 | 60.7914 | 60.9344 | 60.5065 | 60.7309 | 0.0898 | -0.040524 | 0.047519 | -0.043333 | 0.054576 | 0.062689 | -0.099344 | 60.6306 | 60.6249 | 60.6809 | 60.6391 | 60.8052 | 60.9481 | 60.5203 | 60.7446 | -0.17462 | 0.11028 | -0.12428 | 0.16062
468.4531 | 121.9528 | -60.8002 | 60.8276 | 0.080646 | -0.049678 | 0.038365 | -0.066223 | 0.036265 | 0.044377 | -0.11765 | 60.6122 | 60.6066 | 60.6626 | 60.6208 | 60.7869 | 60.9344 | 60.4882 | 60.7263 | 0.094379 | -0.035945 | 0.052098 | -0.05249 | 0.049998 | 0.05811 | -0.10392 | 60.626 | 60.6203 | 60.6763 | 60.6345 | 60.8006 | 60.9481 | 60.502 | 60.74 | -0.17462 | 0.12402 | -0.12428 | 0.17435
470.125 | 121.8338 | -60.791 | 60.878 | 0.076067 | -0.058836 | 0.029208 | -0.057066 | 0.036265 | 0.048956 | -0.11765 | 60.6168 | 60.6158 | 60.658 | 60.6253 | 60.7914 | 60.9298 | 60.4974 | 60.7263 | 0.0898 | -0.045103 | 0.042941 | -0.043333 | 0.049998 | 0.062689 | -0.10392 | 60.6306 | 60.6295 | 60.6717 | 60.6391 | 60.8052 | 60.9435 | 60.5111 | 60.74 | -0.17462 | 0.11944 | -0.13344 | 0.16062
471.8594 | 121.8246 | -60.8917 | 60.7819 | 0.085224 | -0.054257 | 0.033786 | -0.061645 | 0.049999 | 0.044377 | -0.11308 | 60.6122 | 60.6158 | 60.658 | 60.6208 | 60.7823 | 60.9344 | 60.4928 | 60.7171 | 0.098957 | -0.040524 | 0.047519 | -0.047912 | 0.063732 | 0.05811 | -0.099344 | 60.626 | 60.6295 | 60.6717 | 60.6345 | 60.796 | 60.9481 | 60.5065 | 60.7309 | -0.17004 | 0.11944 | -0.12428 | 0.16519
473.6094 | 121.7926 | -60.878 | 60.8093 | 0.080646 | -0.058836 | 0.033786 | -0.052488 | 0.045421 | 0.044377 | -0.11308 | 60.6168 | 60.6112 | 60.658 | 60.6253 | 60.7869 | 60.9344 | 60.4974 | 60.7217 | 0.094379 | -0.045103 | 0.047519 | -0.038755 | 0.059154 | 0.05811 | -0.099344 | 60.6306 | 60.6249 | 60.6717 | 60.6391 | 60.8006 | 60.9481 | 60.5111 | 60.7355 | -0.17004 | 0.11944 | -0.12886 | 0.16062
475.2812 | 121.8521 | -60.8505 | 60.8276 | 0.080646 | -0.054257 | 0.033786 | -0.057066 | 0.040843 | 0.048956 | -0.11308 | 60.6122 | 60.6112 | 60.6534 | 60.6162 | 60.7869 | 60.9298 | 60.502 | 60.7217 | 0.094379 | -0.040524 | 0.047519 | -0.043333 | 0.054576 | 0.062689 | -0.099344 | 60.626 | 60.6249 | 60.6672 | 60.6299 | 60.8006 | 60.9435 | 60.5157 | 60.7355 | -0.17462 | 0.11028 | -0.13344 | 0.15146
477 | 121.8338 | -60.9192 | 60.7681 | 0.076067 | -0.049678 | 0.033786 | -0.057066 | 0.045421 | 0.053534 | -0.11765 | 60.6168 | 60.6112 | 60.658 | 60.6162 | 60.7823 | 60.9298 | 60.4928 | 60.7217 | 0.0898 | -0.035945 | 0.047519 | -0.043333 | 0.059154 | 0.067267 | -0.10392 | 60.6306 | 60.6249 | 60.6717 | 60.6299 | 60.796 | 60.9435 | 60.5065 | 60.7355 | -0.16546 | 0.12402 | -0.12428 | 0.16519
478.7344 | 121.9345 | -60.8551 | 60.7315 | 0.080646 | -0.054257 | 0.033786 | -0.057066 | 0.040843 | 0.044377 | -0.11765 | 60.6122 | 60.6158 | 60.6534 | 60.6253 | 60.7823 | 60.9344 | 60.4928 | 60.7217 | 0.094379 | -0.040524 | 0.047519 | -0.043333 | 0.054576 | 0.05811 | -0.10392 | 60.626 | 60.6295 | 60.6672 | 60.6391 | 60.796 | 60.9481 | 60.5065 | 60.7355 | -0.17004 | 0.11944 | -0.12886 | 0.16062
480.4062 | 121.8292 | -60.9283 | 60.8002 | 0.085224 | -0.058836 | 0.033786 | -0.061645 | 0.045421 | 0.048956 | -0.11765 | 60.6122 | 60.6112 | 60.6534 | 60.6208 | 60.7823 | 60.9344 | 60.4974 | 60.7263 | 0.098957 | -0.045103 | 0.047519 | -0.047912 | 0.059154 | 0.062689 | -0.10392 | 60.626 | 60.6249 | 60.6672 | 60.6345 | 60.796 | 60.9481 | 60.5111 | 60.74 | -0.17004 | 0.11486 | -0.12886 | 0.15604
482.1406 | 121.7972 | -60.8231 | 60.878 | 0.071489 | -0.058836 | 0.038365 | -0.052488 | 0.040843 | 0.044377 | -0.11765 | 60.6122 | 60.6066 | 60.6626 | 60.6162 | 60.7777 | 60.9344 | 60.502 | 60.7309 | 0.085222 | -0.045103 | 0.052098 | -0.038755 | 0.054576 | 0.05811 | -0.10392 | 60.626 | 60.6203 | 60.6763 | 60.6299 | 60.7914 | 60.9481 | 60.5157 | 60.7446 | -0.16546 | 0.11028 | -0.11513 | 0.16062
483.875 | 121.9116 | -60.8276 | 60.8047 | 0.071489 | -0.058836 | 0.024629 | -0.061645 | 0.045421 | 0.048956 | -0.11765 | 60.6077 | 60.602 | 60.6534 | 60.6253 | 60.7777 | 60.9207 | 60.4974 | 60.7263 | 0.085222 | -0.045103 | 0.038362 | -0.047912 | 0.059154 | 0.062689 | -0.10392 | 60.6214 | 60.6158 | 60.6672 | 60.6391 | 60.7914 | 60.9344 | 60.5111 | 60.74 | -0.17004 | 0.11028 | -0.12428 | 0.15604
485.6094 | 121.8384 | -60.878 | 60.8093 | 0.076067 | -0.063415 | 0.029208 | -0.061645 | 0.040843 | 0.044377 | -0.11308 | 60.6077 | 60.6112 | 60.6626 | 60.6162 | 60.7823 | 60.9298 | 60.4928 | 60.7217 | 0.0898 | -0.049682 | 0.042941 | -0.047912 | 0.054576 | 0.05811 | -0.099344 | 60.6214 | 60.6249 | 60.6763 | 60.6299 | 60.796 | 60.9435 | 60.5065 | 60.7355 | -0.17462 | 0.11486 | -0.11971 | 0.16977
487.2812 | 121.9208 | -60.7864 | 60.7956 | 0.080646 | -0.063415 | 0.033786 | -0.057066 | 0.045421 | 0.039799 | -0.11765 | 60.6168 | 60.6112 | 60.658 | 60.6253 | 60.7869 | 60.9344 | 60.4974 | 60.7309 | 0.094379 | -0.049682 | 0.047519 | -0.043333 | 0.059154 | 0.053532 | -0.10392 | 60.6306 | 60.6249 | 60.6717 | 60.6391 | 60.8006 | 60.9481 | 60.5111 | 60.7446 | -0.17004 | 0.11944 | -0.12886 | 0.16062
488.9531 | 121.9437 | -60.8551 | 60.7452 | 0.071489 | -0.054257 | 0.033786 | -0.066223 | 0.049999 | 0.048956 | -0.11308 | 60.6168 | 60.6158 | 60.6626 | 60.6162 | 60.7777 | 60.9298 | 60.4974 | 60.7217 | 0.085222 | -0.040524 | 0.047519 | -0.05249 | 0.063732 | 0.062689 | -0.099344 | 60.6306 | 60.6295 | 60.6763 | 60.6299 | 60.7914 | 60.9435 | 60.5111 | 60.7355 | -0.16088 | 0.11944 | -0.11513 | 0.1652
490.6875 | 121.8887 | -60.8459 | 60.8139 | 0.071489 | -0.058836 | 0.038365 | -0.061645 | 0.045421 | 0.044377 | -0.11765 | 60.6077 | 60.6158 | 60.6534 | 60.6253 | 60.7869 | 60.9298 | 60.4882 | 60.7126 | 0.085222 | -0.045103 | 0.052098 | -0.047912 | 0.059154 | 0.05811 | -0.10392 | 60.6214 | 60.6295 | 60.6672 | 60.6391 | 60.8006 | 60.9435 | 60.502 | 60.7263 | -0.17919 | 0.11944 | -0.13344 | 0.16519
492.4219 | 121.8155 | -60.8276 | 60.8459 | 0.085224 | -0.058836 | 0.038365 | -0.057066 | 0.040843 | 0.048956 | -0.1085 | 60.6077 | 60.6112 | 60.6534 | 60.6208 | 60.7823 | 60.9298 | 60.4928 | 60.7263 | 0.098957 | -0.045103 | 0.052098 | -0.043333 | 0.054576 | 0.062689 | -0.094766 | 60.6214 | 60.6249 | 60.6672 | 60.6345 | 60.796 | 60.9435 | 60.5065 | 60.74 | -0.17462 | 0.11486 | -0.12886 | 0.16062
494.0938 | 121.8018 | -60.8276 | 60.9009 | 0.076067 | -0.063415 | 0.033786 | -0.061645 | 0.040843 | 0.044377 | -0.11765 | 60.6031 | 60.6112 | 60.658 | 60.6208 | 60.7823 | 60.9298 | 60.4974 | 60.7217 | 0.0898 | -0.049682 | 0.047519 | -0.047912 | 0.054576 | 0.05811 | -0.10392 | 60.6168 | 60.6249 | 60.6717 | 60.6345 | 60.796 | 60.9435 | 60.5111 | 60.7355 | -0.17919 | 0.10571 | -0.12428 | 0.16062
495.8438 | 121.9345 | -60.7773 | 60.8185 | 0.089802 | -0.058836 | 0.038365 | -0.061645 | 0.049999 | 0.044377 | -0.11765 | 60.6077 | 60.6066 | 60.6626 | 60.6116 | 60.7823 | 60.9252 | 60.4928 | 60.7217 | 0.10354 | -0.045103 | 0.052098 | -0.047912 | 0.063732 | 0.05811 | -0.10392 | 60.6214 | 60.6203 | 60.6763 | 60.6253 | 60.796 | 60.939 | 60.5065 | 60.7355 | -0.17462 | 0.11486 | -0.11971 | 0.16977
497.5625 | 121.8155 | -60.8276 | 60.8597 | 0.089802 | -0.054257 | 0.029208 | -0.057066 | 0.049999 | 0.048956 | -0.11308 | 60.6077 | 60.602 | 60.6626 | 60.6208 | 60.7823 | 60.9344 | 60.4928 | 60.7217 | 0.10354 | -0.040524 | 0.042941 | -0.043333 | 0.063732 | 0.062689 | -0.099344 | 60.6214 | 60.6158 | 60.6763 | 60.6345 | 60.796 | 60.9481 | 60.5065 | 60.7355 | -0.17462 | 0.11486 | -0.11971 | 0.16977
499.2188 | 121.9299 | -60.7956 | 60.791 | 0.085224 | -0.058836 | 0.038365 | -0.052488 | 0.045421 | 0.048956 | -0.11308 | 60.6122 | 60.6158 | 60.658 | 60.6162 | 60.7777 | 60.9252 | 60.4928 | 60.7171 | 0.098957 | -0.045103 | 0.052098 | -0.038755 | 0.059154 | 0.062689 | -0.099344 | 60.626 | 60.6295 | 60.6717 | 60.6299 | 60.7914 | 60.939 | 60.5065 | 60.7309 | -0.16546 | 0.11944 | -0.11971 | 0.16519
500.9531 | 121.9254 | -60.8414 | 60.7315 | 0.089802 | -0.063415 | 0.033786 | -0.052488 | 0.049999 | 0.044377 | -0.12223 | 60.6122 | 60.6066 | 60.6626 | 60.6253 | 60.7777 | 60.9298 | 60.4882 | 60.7217 | 0.10354 | -0.049682 | 0.047519 | -0.038755 | 0.063732 | 0.05811 | -0.1085 | 60.626 | 60.6203 | 60.6763 | 60.6391 | 60.7914 | 60.9435 | 60.502 | 60.7355 | -0.16546 | 0.12402 | -0.11513 | 0.17435
502.6875 | 121.8338 | -60.8414 | 60.8047 | 0.085224 | -0.063415 | 0.029208 | -0.057066 | 0.045421 | 0.039799 | -0.10392 | 60.6122 | 60.6112 | 60.658 | 60.6253 | 60.7823 | 60.9252 | 60.4791 | 60.7171 | 0.098957 | -0.049682 | 0.042941 | -0.043333 | 0.059154 | 0.053532 | -0.090188 | 60.626 | 60.6249 | 60.6717 | 60.6391 | 60.796 | 60.939 | 60.4928 | 60.7309 | -0.17004 | 0.13318 | -0.12428 | 0.17893
504.4219 | 121.8246 | -60.8231 | 60.8643 | 0.076067 | -0.054257 | 0.029208 | -0.057066 | 0.040843 | 0.048956 | -0.11765 | 60.6077 | 60.6112 | 60.6534 | 60.6208 | 60.7869 | 60.9252 | 60.4974 | 60.7217 | 0.0898 | -0.040524 | 0.042941 | -0.043333 | 0.054576 | 0.062689 | -0.10392 | 60.6214 | 60.6249 | 60.6672 | 60.6345 | 60.8006 | 60.939 | 60.5111 | 60.7355 | -0.17919 | 0.11028 | -0.13344 | 0.15604
506.1719 | 121.8155 | -60.791 | 60.878 | 0.085224 | -0.058836 | 0.033786 | -0.057066 | 0.045421 | 0.048956 | -0.11308 | 60.6122 | 60.6112 | 60.6626 | 60.6253 | 60.7823 | 60.9207 | 60.4928 | 60.7263 | 0.098957 | -0.045103 | 0.047519 | -0.043333 | 0.059154 | 0.062689 | -0.099344 | 60.626 | 60.6249 | 60.6763 | 60.6391 | 60.796 | 60.9344 | 60.5065 | 60.74 | -0.17004 | 0.11944 | -0.11971 | 0.16977
507.8438 | 121.8063 | -60.8734 | 60.791 | 0.080646 | -0.058836 | 0.033786 | -0.052488 | 0.045421 | 0.044377 | -0.11308 | 60.6077 | 60.6112 | 60.6672 | 60.6116 | 60.7777 | 60.9252 | 60.4882 | 60.708 | 0.094379 | -0.045103 | 0.047519 | -0.038755 | 0.059154 | 0.05811 | -0.099344 | 60.6214 | 60.6249 | 60.6809 | 60.6253 | 60.7914 | 60.939 | 60.502 | 60.7217 | -0.17004 | 0.11944 | -0.11055 | 0.17893
509.5781 | 121.8292 | -60.8139 | 60.8734 | 0.085224 | -0.058836 | 0.029208 | -0.057066 | 0.049999 | 0.044377 | -0.11765 | 60.6077 | 60.6066 | 60.658 | 60.6162 | 60.7823 | 60.9207 | 60.4928 | 60.7171 | 0.098957 | -0.045103 | 0.042941 | -0.043333 | 0.063732 | 0.05811 | -0.10392 | 60.6214 | 60.6203 | 60.6717 | 60.6299 | 60.796 | 60.9344 | 60.5065 | 60.7309 | -0.17462 | 0.11486 | -0.12428 | 0.16519
511.3281 | 121.8155 | -60.9009 | 60.791 | 0.080646 | -0.054257 | 0.033786 | -0.057066 | 0.045421 | 0.048956 | -0.1085 | 60.6122 | 60.602 | 60.6534 | 60.6208 | 60.7777 | 60.9252 | 60.4836 | 60.7126 | 0.094379 | -0.040524 | 0.047519 | -0.043333 | 0.059154 | 0.062689 | -0.094766 | 60.626 | 60.6158 | 60.6672 | 60.6345 | 60.7914 | 60.939 | 60.4974 | 60.7263 | -0.16546 | 0.1286 | -0.12428 | 0.16977
513 | 121.9208 | -60.7819 | 60.8231 | 0.076067 | -0.058836 | 0.029208 | -0.057066 | 0.045421 | 0.044377 | -0.1085 | 60.6122 | 60.6158 | 60.6534 | 60.6162 | 60.7777 | 60.9207 | 60.4928 | 60.7171 | 0.0898 | -0.045103 | 0.042941 | -0.043333 | 0.059154 | 0.05811 | -0.094766 | 60.626 | 60.6295 | 60.6672 | 60.6299 | 60.7914 | 60.9344 | 60.5065 | 60.7309 | -0.16546 | 0.11944 | -0.12428 | 0.16062
514.7344 | 121.8842 | -60.8414 | 60.7773 | 0.076067 | -0.058836 | 0.029208 | -0.061645 | 0.049999 | 0.048956 | -0.11765 | 60.6077 | 60.5974 | 60.6488 | 60.6116 | 60.7777 | 60.9298 | 60.4836 | 60.7217 | 0.0898 | -0.045103 | 0.042941 | -0.047912 | 0.063732 | 0.062689 | -0.10392 | 60.6214 | 60.6112 | 60.6626 | 60.6253 | 60.7914 | 60.9435 | 60.4974 | 60.7355 | -0.17004 | 0.12402 | -0.12886 | 0.16519
516.4062 | 121.7926 | -60.8139 | 60.8734 | 0.080646 | -0.063415 | 0.029208 | -0.057066 | 0.040843 | 0.044377 | -0.11308 | 60.6031 | 60.6066 | 60.6534 | 60.6116 | 60.7777 | 60.9298 | 60.4882 | 60.7171 | 0.094379 | -0.049682 | 0.042941 | -0.043333 | 0.054576 | 0.05811 | -0.099344 | 60.6168 | 60.6203 | 60.6672 | 60.6253 | 60.7914 | 60.9435 | 60.502 | 60.7309 | -0.17462 | 0.11486 | -0.12428 | 0.16519
518.1406 | 121.9208 | -60.7681 | 60.7864 | 0.080646 | -0.067994 | 0.033786 | -0.057066 | 0.040843 | 0.053534 | -0.11765 | 60.6077 | 60.6066 | 60.6443 | 60.6162 | 60.7777 | 60.9252 | 60.4791 | 60.708 | 0.094379 | -0.054261 | 0.047519 | -0.043333 | 0.054576 | 0.067267 | -0.10392 | 60.6214 | 60.6203 | 60.658 | 60.6299 | 60.7914 | 60.939 | 60.4928 | 60.7217 | -0.17004 | 0.1286 | -0.13344 | 0.1652
519.875 | 121.7926 | -60.8643 | 60.8093 | 0.080646 | -0.058836 | 0.033786 | -0.057066 | 0.054577 | 0.044377 | -0.11308 | 60.6077 | 60.6066 | 60.658 | 60.6208 | 60.7777 | 60.9252 | 60.4791 | 60.7217 | 0.094379 | -0.045103 | 0.047519 | -0.043333 | 0.06831 | 0.05811 | -0.099344 | 60.6214 | 60.6203 | 60.6717 | 60.6345 | 60.7914 | 60.939 | 60.4928 | 60.7355 | -0.17004 | 0.1286 | -0.11971 | 0.17893
521.5469 | 121.7926 | -60.8688 | 60.791 | 0.076067 | -0.058836 | 0.033786 | -0.057066 | 0.049999 | 0.053534 | -0.11765 | 60.6122 | 60.6112 | 60.6534 | 60.6208 | 60.7731 | 60.9252 | 60.4836 | 60.708 | 0.0898 | -0.045103 | 0.047519 | -0.043333 | 0.063732 | 0.067267 | -0.10392 | 60.626 | 60.6249 | 60.6672 | 60.6345 | 60.7869 | 60.939 | 60.4974 | 60.7217 | -0.16088 | 0.1286 | -0.11971 | 0.16977
523.2812 | 121.8613 | -60.7681 | 60.8597 | 0.080646 | -0.067994 | 0.029208 | -0.057066 | 0.045421 | 0.053534 | -0.11308 | 60.6077 | 60.602 | 60.6488 | 60.6116 | 60.7823 | 60.9207 | 60.4882 | 60.7171 | 0.094379 | -0.054261 | 0.042941 | -0.043333 | 0.059154 | 0.067267 | -0.099344 | 60.6214 | 60.6158 | 60.6626 | 60.6253 | 60.796 | 60.9344 | 60.502 | 60.7309 | -0.17462 | 0.11944 | -0.13344 | 0.16062
525.0156 | 121.7926 | -60.8917 | 60.7956 | 0.085224 | -0.067994 | 0.033786 | -0.047909 | 0.045421 | 0.048956 | -0.1085 | 60.6077 | 60.6158 | 60.6534 | 60.6162 | 60.7777 | 60.9207 | 60.4836 | 60.7126 | 0.098957 | -0.054261 | 0.047519 | -0.034176 | 0.059154 | 0.062689 | -0.094766 | 60.6214 | 60.6295 | 60.6672 | 60.6299 | 60.7914 | 60.9344 | 60.4974 | 60.7263 | -0.17004 | 0.12402 | -0.12428 | 0.16977
526.7656 | 121.9025 | -60.8322 | 60.7727 | 0.080646 | -0.063415 | 0.029208 | -0.057066 | 0.040843 | 0.039799 | -0.10392 | 60.6077 | 60.602 | 60.6534 | 60.6162 | 60.7869 | 60.9252 | 60.4791 | 60.7126 | 0.094379 | -0.049682 | 0.042941 | -0.043333 | 0.054576 | 0.053532 | -0.090188 | 60.6214 | 60.6158 | 60.6672 | 60.6299 | 60.8006 | 60.939 | 60.4928 | 60.7263 | -0.17919 | 0.1286 | -0.13344 | 0.17435
528.5 | 121.7972 | -60.8917 | 60.7956 | 0.080646 | -0.054257 | 0.038365 | -0.057066 | 0.049999 | 0.058113 | -0.11308 | 60.6122 | 60.602 | 60.6488 | 60.6162 | 60.7823 | 60.9161 | 60.4791 | 60.7034 | 0.094379 | -0.040524 | 0.052098 | -0.043333 | 0.063732 | 0.071846 | -0.099344 | 60.626 | 60.6158 | 60.6626 | 60.6299 | 60.796 | 60.9298 | 60.4928 | 60.7171 | -0.17004 | 0.13318 | -0.13344 | 0.16977
530.1719 | 121.7789 | -60.8826 | 60.8139 | 0.085224 | -0.054257 | 0.038365 | -0.052488 | 0.045421 | 0.044377 | -0.11308 | 60.6077 | 60.6112 | 60.6534 | 60.6116 | 60.7777 | 60.9161 | 60.4699 | 60.7126 | 0.098957 | -0.040524 | 0.052098 | -0.038755 | 0.059154 | 0.05811 | -0.099344 | 60.6214 | 60.6249 | 60.6672 | 60.6253 | 60.7914 | 60.9298 | 60.4836 | 60.7263 | -0.17004 | 0.13775 | -0.12428 | 0.18351
531.9062 | 121.8155 | -60.8826 | 60.791 | 0.085224 | -0.063415 | 0.038365 | -0.052488 | 0.036265 | 0.048956 | -0.11765 | 60.6077 | 60.6112 | 60.6534 | 60.6208 | 60.7777 | 60.9252 | 60.4745 | 60.7034 | 0.098957 | -0.049682 | 0.052098 | -0.038755 | 0.049998 | 0.062689 | -0.10392 | 60.6214 | 60.6249 | 60.6672 | 60.6345 | 60.7914 | 60.939 | 60.4882 | 60.7171 | -0.17004 | 0.13318 | -0.12428 | 0.17893
533.5781 | 121.8933 | -60.8505 | 60.7498 | 0.080646 | -0.072572 | 0.029208 | -0.052488 | 0.049999 | 0.053534 | -0.11765 | 60.6077 | 60.6112 | 60.6488 | 60.6162 | 60.764 | 60.9252 | 60.4745 | 60.6942 | 0.094379 | -0.058839 | 0.042941 | -0.038755 | 0.063732 | 0.067267 | -0.10392 | 60.6214 | 60.6249 | 60.6626 | 60.6299 | 60.7777 | 60.939 | 60.4882 | 60.708 | -0.1563 | 0.13318 | -0.11513 | 0.17435
535.2969 | 121.9208 | -60.7864 | 60.7819 | 0.089802 | -0.058836 | 0.033786 | -0.052488 | 0.045421 | 0.048956 | -0.11308 | 60.5985 | 60.602 | 60.6443 | 60.6162 | 60.7777 | 60.9252 | 60.4928 | 60.7171 | 0.10354 | -0.045103 | 0.047519 | -0.038755 | 0.059154 | 0.062689 | -0.099344 | 60.6122 | 60.6158 | 60.658 | 60.6299 | 60.7914 | 60.939 | 60.5065 | 60.7309 | -0.17919 | 0.10571 | -0.13344 | 0.15146
537.0312 | 121.9162 | -60.7864 | 60.8047 | 0.085224 | -0.067994 | 0.033786 | -0.057066 | 0.040843 | 0.039799 | -0.11308 | 60.6031 | 60.602 | 60.6443 | 60.607 | 60.7731 | 60.9207 | 60.4836 | 60.7126 | 0.098957 | -0.054261 | 0.047519 | -0.043333 | 0.054576 | 0.053532 | -0.099344 | 60.6168 | 60.6158 | 60.658 | 60.6208 | 60.7869 | 60.9344 | 60.4974 | 60.7263 | -0.17004 | 0.11944 | -0.12886 | 0.16062
538.7812 | 121.7834 | -60.91 | 60.8047 | 0.085224 | -0.058836 | 0.042944 | -0.052488 | 0.049999 | 0.048956 | -0.11308 | 60.6031 | 60.5974 | 60.6534 | 60.6116 | 60.7685 | 60.9161 | 60.4745 | 60.708 | 0.098957 | -0.045103 | 0.056677 | -0.038755 | 0.063732 | 0.062689 | -0.099344 | 60.6168 | 60.6112 | 60.6672 | 60.6253 | 60.7823 | 60.9298 | 60.4882 | 60.7217 | -0.16546 | 0.1286 | -0.11513 | 0.17893
540.4531 | 121.7926 | -60.8231 | 60.8643 | 0.080646 | -0.067994 | 0.033786 | -0.057066 | 0.045421 | 0.053534 | -0.11765 | 60.6077 | 60.5974 | 60.658 | 60.6116 | 60.7777 | 60.9207 | 60.4791 | 60.708 | 0.094379 | -0.054261 | 0.047519 | -0.043333 | 0.059154 | 0.067267 | -0.10392 | 60.6214 | 60.6112 | 60.6717 | 60.6253 | 60.7914 | 60.9344 | 60.4928 | 60.7217 | -0.17004 | 0.1286 | -0.11971 | 0.17893
542.2031 | 121.7926 | -60.8917 | 60.7636 | 0.089802 | -0.063415 | 0.033786 | -0.061645 | 0.049999 | 0.048956 | -0.11765 | 60.6122 | 60.602 | 60.6488 | 60.6116 | 60.764 | 60.9115 | 60.4791 | 60.6988 | 0.10354 | -0.049682 | 0.047519 | -0.047912 | 0.063732 | 0.062689 | -0.10392 | 60.626 | 60.6158 | 60.6626 | 60.6253 | 60.7777 | 60.9252 | 60.4928 | 60.7126 | -0.15173 | 0.13318 | -0.11513 | 0.16977
543.9375 | 121.7789 | -60.8276 | 60.8597 | 0.080646 | -0.058836 | 0.033786 | -0.052488 | 0.045421 | 0.048956 | -0.11308 | 60.5985 | 60.602 | 60.6534 | 60.607 | 60.7731 | 60.9207 | 60.4653 | 60.7126 | 0.094379 | -0.045103 | 0.047519 | -0.038755 | 0.059154 | 0.062689 | -0.099344 | 60.6122 | 60.6158 | 60.6672 | 60.6208 | 60.7869 | 60.9344 | 60.4791 | 60.7263 | -0.17462 | 0.13318 | -0.11971 | 0.18809
545.6719 | 121.8796 | -60.8505 | 60.7269 | 0.080646 | -0.067994 | 0.024629 | -0.057066 | 0.045421 | 0.039799 | -0.12223 | 60.6077 | 60.602 | 60.6534 | 60.6162 | 60.7594 | 60.9161 | 60.4745 | 60.7034 | 0.094379 | -0.054261 | 0.038362 | -0.043333 | 0.059154 | 0.053532 | -0.1085 | 60.6214 | 60.6158 | 60.6672 | 60.6299 | 60.7731 | 60.9298 | 60.4882 | 60.7171 | -0.15173 | 0.13318 | -0.10597 | 0.17893
547.3438 | 121.9208 | -60.7636 | 60.8002 | 0.080646 | -0.063415 | 0.033786 | -0.057066 | 0.040843 | 0.039799 | -0.11308 | 60.6077 | 60.6066 | 60.6443 | 60.6116 | 60.7731 | 60.9161 | 60.4745 | 60.708 | 0.094379 | -0.049682 | 0.047519 | -0.043333 | 0.054576 | 0.053532 | -0.099344 | 60.6214 | 60.6203 | 60.658 | 60.6253 | 60.7869 | 60.9298 | 60.4882 | 60.7217 | -0.16546 | 0.13318 | -0.12886 | 0.16977
549.0781 | 121.843 | -60.791 | 60.8414 | 0.085224 | -0.058836 | 0.033786 | -0.057066 | 0.045421 | 0.044377 | -0.11308 | 60.6031 | 60.602 | 60.6397 | 60.6116 | 60.7777 | 60.9161 | 60.4699 | 60.7126 | 0.098957 | -0.045103 | 0.047519 | -0.043333 | 0.059154 | 0.05811 | -0.099344 | 60.6168 | 60.6158 | 60.6534 | 60.6253 | 60.7914 | 60.9298 | 60.4836 | 60.7263 | -0.17462 | 0.13318 | -0.13802 | 0.16977
550.8281 | 121.7651 | -60.8597 | 60.8002 | 0.080646 | -0.063415 | 0.042944 | -0.061645 | 0.049999 | 0.044377 | -0.11308 | 60.6031 | 60.602 | 60.6488 | 60.607 | 60.7685 | 60.9161 | 60.4699 | 60.708 | 0.094379 | -0.049682 | 0.056677 | -0.047912 | 0.063732 | 0.05811 | -0.099344 | 60.6168 | 60.6158 | 60.6626 | 60.6208 | 60.7823 | 60.9298 | 60.4836 | 60.7217 | -0.16546 | 0.13318 | -0.11971 | 0.17893
552.5 | 121.7926 | -60.8047 | 60.8414 | 0.085224 | -0.058836 | 0.033786 | -0.057066 | 0.036265 | 0.048956 | -0.11308 | 60.6031 | 60.602 | 60.6534 | 60.6116 | 60.7777 | 60.9161 | 60.4699 | 60.7034 | 0.098957 | -0.045103 | 0.047519 | -0.043333 | 0.049998 | 0.062689 | -0.099344 | 60.6168 | 60.6158 | 60.6672 | 60.6253 | 60.7914 | 60.9298 | 60.4836 | 60.7171 | -0.17462 | 0.13318 | -0.12428 | 0.18351
554.2344 | 121.7926 | -60.8826 | 60.7773 | 0.085224 | -0.077151 | 0.033786 | -0.052488 | 0.049999 | 0.048956 | -0.1085 | 60.6031 | 60.6066 | 60.6534 | 60.6116 | 60.7594 | 60.9115 | 60.4653 | 60.708 | 0.098957 | -0.063418 | 0.047519 | -0.038755 | 0.063732 | 0.062689 | -0.094766 | 60.6168 | 60.6203 | 60.6672 | 60.6253 | 60.7731 | 60.9252 | 60.4791 | 60.7217 | -0.1563 | 0.13775 | -0.10597 | 0.18809
555.9844 | 121.8796 | -60.8597 | 60.7269 | 0.085224 | -0.067994 | 0.029208 | -0.061645 | 0.045421 | 0.044377 | -0.11308 | 60.6077 | 60.5974 | 60.6488 | 60.6162 | 60.7685 | 60.9069 | 60.4562 | 60.708 | 0.098957 | -0.054261 | 0.042941 | -0.047912 | 0.059154 | 0.05811 | -0.099344 | 60.6214 | 60.6112 | 60.6626 | 60.6299 | 60.7823 | 60.9207 | 60.4699 | 60.7217 | -0.16088 | 0.15149 | -0.11971 | 0.19266
557.7188 | 121.7834 | -60.8643 | 60.7864 | 0.089802 | -0.067994 | 0.029208 | -0.052488 | 0.045421 | 0.053534 | -0.11765 | 60.5985 | 60.602 | 60.6443 | 60.6116 | 60.764 | 60.9207 | 60.4562 | 60.6988 | 0.10354 | -0.054261 | 0.042941 | -0.038755 | 0.059154 | 0.067267 | -0.10392 | 60.6122 | 60.6158 | 60.658 | 60.6253 | 60.7777 | 60.9344 | 60.4699 | 60.7126 | -0.16546 | 0.14233 | -0.11971 | 0.18809
559.375 | 121.9162 | -60.7727 | 60.8093 | 0.080646 | -0.072572 | 0.038365 | -0.052488 | 0.049999 | 0.039799 | -0.1085 | 60.6031 | 60.602 | 60.6488 | 60.6162 | 60.764 | 60.9115 | 60.4653 | 60.7034 | 0.094379 | -0.058839 | 0.052098 | -0.038755 | 0.063732 | 0.053532 | -0.094766 | 60.6168 | 60.6158 | 60.6626 | 60.6299 | 60.7777 | 60.9252 | 60.4791 | 60.7171 | -0.16088 | 0.13775 | -0.11513 | 0.18351
561.1094 | 121.8933 | -60.791 | 60.7956 | 0.076067 | -0.067994 | 0.029208 | -0.057066 | 0.045421 | 0.044377 | -0.1085 | 60.6031 | 60.6066 | 60.6397 | 60.6116 | 60.764 | 60.9115 | 60.4699 | 60.7034 | 0.0898 | -0.054261 | 0.042941 | -0.043333 | 0.059154 | 0.05811 | -0.094766 | 60.6168 | 60.6203 | 60.6534 | 60.6253 | 60.7777 | 60.9252 | 60.4836 | 60.7171 | -0.16088 | 0.13318 | -0.12428 | 0.16977
562.8281 | 121.7789 | -60.791 | 60.878 | 0.080646 | -0.072572 | 0.033786 | -0.052488 | 0.040843 | 0.053534 | -0.11765 | 60.6077 | 60.602 | 60.6488 | 60.6162 | 60.764 | 60.9161 | 60.4562 | 60.6988 | 0.094379 | -0.058839 | 0.047519 | -0.038755 | 0.054576 | 0.067267 | -0.10392 | 60.6214 | 60.6158 | 60.6626 | 60.6299 | 60.7777 | 60.9298 | 60.4699 | 60.7126 | -0.1563 | 0.15149 | -0.11513 | 0.19266
564.5 | 121.8842 | -60.7681 | 60.7864 | 0.085224 | -0.058836 | 0.029208 | -0.057066 | 0.036265 | 0.044377 | -0.11308 | 60.6077 | 60.5974 | 60.6397 | 60.607 | 60.7685 | 60.9161 | 60.4653 | 60.7126 | 0.098957 | -0.045103 | 0.042941 | -0.043333 | 0.049998 | 0.05811 | -0.099344 | 60.6214 | 60.6112 | 60.6534 | 60.6208 | 60.7823 | 60.9298 | 60.4791 | 60.7263 | -0.16088 | 0.14233 | -0.12886 | 0.17435
566.25 | 121.7606 | -60.8917 | 60.791 | 0.080646 | -0.063415 | 0.038365 | -0.052488 | 0.040843 | 0.039799 | -0.10392 | 60.6031 | 60.6066 | 60.658 | 60.607 | 60.7594 | 60.9115 | 60.447 | 60.6988 | 0.094379 | -0.049682 | 0.052098 | -0.038755 | 0.054576 | 0.053532 | -0.090188 | 60.6168 | 60.6203 | 60.6717 | 60.6208 | 60.7731 | 60.9252 | 60.4608 | 60.7126 | -0.1563 | 0.15607 | -0.10139 | 0.21098
567.9219 | 121.788 | -60.8093 | 60.8734 | 0.080646 | -0.067994 | 0.038365 | -0.057066 | 0.040843 | 0.044377 | -0.12223 | 60.6031 | 60.602 | 60.6351 | 60.6162 | 60.7594 | 60.9161 | 60.4562 | 60.7034 | 0.094379 | -0.054261 | 0.052098 | -0.043333 | 0.054576 | 0.05811 | -0.1085 | 60.6168 | 60.6158 | 60.6488 | 60.6299 | 60.7731 | 60.9298 | 60.4699 | 60.7171 | -0.1563 | 0.14691 | -0.12429 | 0.17893
569.6562 | 121.8109 | -60.8459 | 60.8185 | 0.089802 | -0.058836 | 0.033786 | -0.061645 | 0.045421 | 0.048956 | -0.11308 | 60.6122 | 60.602 | 60.6534 | 60.6162 | 60.764 | 60.9161 | 60.4379 | 60.6942 | 0.10354 | -0.045103 | 0.047519 | -0.047912 | 0.059154 | 0.062689 | -0.099344 | 60.626 | 60.6158 | 60.6672 | 60.6299 | 60.7777 | 60.9298 | 60.4516 | 60.708 | -0.15173 | 0.17438 | -0.11055 | 0.21556
571.4219 | 121.9208 | -60.7544 | 60.8002 | 0.089802 | -0.072572 | 0.029208 | -0.052488 | 0.049999 | 0.044377 | -0.11765 | 60.6077 | 60.5974 | 60.6534 | 60.6162 | 60.764 | 60.9069 | 60.4379 | 60.7034 | 0.10354 | -0.058839 | 0.042941 | -0.038755 | 0.063732 | 0.05811 | -0.10392 | 60.6214 | 60.6112 | 60.6672 | 60.6299 | 60.7777 | 60.9207 | 60.4516 | 60.7171 | -0.1563 | 0.1698 | -0.11055 | 0.21556
573.0938 | 121.8338 | -60.8231 | 60.8185 | 0.085224 | -0.067994 | 0.042944 | -0.052488 | 0.054577 | 0.044377 | -0.11308 | 60.6122 | 60.6112 | 60.6534 | 60.6208 | 60.7685 | 60.9115 | 60.4287 | 60.6942 | 0.098957 | -0.054261 | 0.056677 | -0.038755 | 0.06831 | 0.05811 | -0.099344 | 60.626 | 60.6249 | 60.6672 | 60.6345 | 60.7823 | 60.9252 | 60.4424 | 60.708 | -0.1563 | 0.18354 | -0.11513 | 0.22471
574.8281 | 121.8842 | -60.8093 | 60.7864 | 0.085224 | -0.067994 | 0.033786 | -0.057066 | 0.045421 | 0.044377 | -0.11308 | 60.6031 | 60.5929 | 60.6534 | 60.6116 | 60.7594 | 60.9161 | 60.4424 | 60.6988 | 0.098957 | -0.054261 | 0.047519 | -0.043333 | 0.059154 | 0.05811 | -0.099344 | 60.6168 | 60.6066 | 60.6672 | 60.6253 | 60.7731 | 60.9298 | 60.4562 | 60.7126 | -0.1563 | 0.16065 | -0.10597 | 0.21098
576.5 | 121.7743 | -60.8139 | 60.8459 | 0.080646 | -0.063415 | 0.033786 | -0.057066 | 0.045421 | 0.048956 | -0.11308 | 60.6031 | 60.5974 | 60.6488 | 60.6116 | 60.764 | 60.9069 | 60.4287 | 60.7034 | 0.094379 | -0.049682 | 0.047519 | -0.043333 | 0.059154 | 0.062689 | -0.099344 | 60.6168 | 60.6112 | 60.6626 | 60.6253 | 60.7777 | 60.9207 | 60.4424 | 60.7171 | -0.16088 | 0.17438 | -0.11513 | 0.22013
578.2344 | 121.8796 | -60.8139 | 60.8002 | 0.085224 | -0.063415 | 0.033786 | -0.061645 | 0.049999 | 0.039799 | -0.1085 | 60.6031 | 60.5883 | 60.6443 | 60.6116 | 60.7731 | 60.9069 | 60.4379 | 60.6897 | 0.098957 | -0.049682 | 0.047519 | -0.047912 | 0.063732 | 0.053532 | -0.094766 | 60.6168 | 60.602 | 60.658 | 60.6253 | 60.7869 | 60.9207 | 60.4516 | 60.7034 | -0.17004 | 0.16522 | -0.12886 | 0.2064
579.9062 | 121.875 | -60.8322 | 60.759 | 0.085224 | -0.054257 | 0.033786 | -0.057066 | 0.045421 | 0.044377 | -0.1085 | 60.6031 | 60.5974 | 60.6443 | 60.607 | 60.7594 | 60.9207 | 60.4333 | 60.708 | 0.098957 | -0.040524 | 0.047519 | -0.043333 | 0.059154 | 0.05811 | -0.094766 | 60.6168 | 60.6112 | 60.658 | 60.6208 | 60.7731 | 60.9344 | 60.447 | 60.7217 | -0.1563 | 0.1698 | -0.11513 | 0.21098
581.6406 | 121.8201 | -60.8276 | 60.7819 | 0.085224 | -0.063415 | 0.038365 | -0.052488 | 0.045421 | 0.048956 | -0.1085 | 60.6077 | 60.5929 | 60.6397 | 60.6116 | 60.7685 | 60.9161 | 60.4379 | 60.6988 | 0.098957 | -0.049682 | 0.052098 | -0.038755 | 0.059154 | 0.062689 | -0.094766 | 60.6214 | 60.6066 | 60.6534 | 60.6253 | 60.7823 | 60.9298 | 60.4516 | 60.7126 | -0.16088 | 0.1698 | -0.12886 | 0.20182
583.375 | 121.8658 | -60.8368 | 60.7498 | 0.085224 | -0.058836 | 0.033786 | -0.057066 | 0.036265 | 0.048956 | -0.1085 | 60.6031 | 60.5837 | 60.6305 | 60.5979 | 60.7685 | 60.9298 | 60.4424 | 60.7034 | 0.098957 | -0.045103 | 0.047519 | -0.043333 | 0.049998 | 0.062689 | -0.094766 | 60.6168 | 60.5974 | 60.6443 | 60.6116 | 60.7823 | 60.9435 | 60.4562 | 60.7171 | -0.16546 | 0.16065 | -0.13802 | 0.18809
585.0938 | 121.9254 | -60.791 | 60.7727 | 0.076067 | -0.058836 | 0.038365 | -0.061645 | 0.040843 | 0.048956 | -0.11308 | 60.5894 | 60.5791 | 60.6214 | 60.5841 | 60.7914 | 60.9252 | 60.447 | 60.7217 | 0.0898 | -0.045103 | 0.052098 | -0.047912 | 0.054576 | 0.062689 | -0.099344 | 60.6031 | 60.5929 | 60.6351 | 60.5979 | 60.8052 | 60.939 | 60.4608 | 60.7355 | -0.20209 | 0.14233 | -0.17007 | 0.17435
586.8438 | 121.8155 | -60.8643 | 60.7636 | 0.085224 | -0.058836 | 0.038365 | -0.052488 | 0.045421 | 0.044377 | -0.1085 | 60.5665 | 60.57 | 60.6122 | 60.575 | 60.796 | 60.939 | 60.4424 | 60.7309 | 0.098957 | -0.045103 | 0.052098 | -0.038755 | 0.059154 | 0.05811 | -0.094766 | 60.5802 | 60.5837 | 60.6259 | 60.5887 | 60.8097 | 60.9527 | 60.4562 | 60.7446 | -0.22956 | 0.12402 | -0.1838 | 0.16977
588.5156 | 121.8338 | -60.8734 | 60.7681 | 0.094381 | -0.058836 | 0.033786 | -0.057066 | 0.040843 | 0.053534 | -0.11765 | 60.5481 | 60.5517 | 60.5985 | 60.5612 | 60.8143 | 60.9573 | 60.4699 | 60.7492 | 0.10811 | -0.045103 | 0.047519 | -0.043333 | 0.054576 | 0.067267 | -0.10392 | 60.5619 | 60.5654 | 60.6122 | 60.575 | 60.8281 | 60.971 | 60.4836 | 60.7629 | -0.26618 | 0.078234 | -0.21585 | 0.12857
590.25 | 121.7651 | -60.9558 | 60.704 | 0.085224 | -0.067994 | 0.033786 | -0.057066 | 0.049999 | 0.044377 | -0.1085 | 60.5344 | 60.5288 | 60.5664 | 60.5429 | 60.8326 | 60.9756 | 60.4928 | 60.7721 | 0.098957 | -0.054261 | 0.047519 | -0.043333 | 0.063732 | 0.05811 | -0.094766 | 60.5481 | 60.5425 | 60.5802 | 60.5566 | 60.8464 | 60.9893 | 60.5065 | 60.7858 | -0.29823 | 0.041606 | -0.26621 | 0.073629
592 | 121.7743 | -60.9833 | 60.6903 | 0.076067 | -0.058836 | 0.033786 | -0.047909 | 0.045421 | 0.053534 | -0.11308 | 60.4978 | 60.4921 | 60.5344 | 60.5109 | 60.8555 | 61.0122 | 60.5249 | 60.7995 | 0.0898 | -0.045103 | 0.047519 | -0.034176 | 0.059154 | 0.067267 | -0.099344 | 60.5115 | 60.5059 | 60.5481 | 60.5246 | 60.8693 | 61.0259 | 60.5386 | 60.8133 | -0.35775 | -0.027071 | -0.32115 | 0.009532
593.75 | 121.7697 | -60.9879 | 60.64 | 0.076067 | -0.058836 | 0.029208 | -0.057066 | 0.045421 | 0.048956 | -0.1085 | 60.452 | 60.4418 | 60.4886 | 60.4605 | 60.9105 | 61.058 | 60.5523 | 60.8362 | 0.0898 | -0.045103 | 0.042941 | -0.043333 | 0.059154 | 0.062689 | -0.094766 | 60.4657 | 60.4555 | 60.5023 | 60.4742 | 60.9242 | 61.0717 | 60.5661 | 60.8499 | -0.45847 | -0.10033 | -0.42187 | -0.063721
595.4844 | 121.8475 | -61.0107 | 60.5804 | 0.085224 | -0.058836 | 0.038365 | -0.061645 | 0.040843 | 0.035221 | -0.1085 | 60.4016 | 60.4006 | 60.4428 | 60.4147 | 60.9608 | 61.1038 | 60.6164 | 60.9048 | 0.098957 | -0.045103 | 0.052098 | -0.047912 | 0.054576 | 0.048954 | -0.094766 | 60.4154 | 60.4143 | 60.4566 | 60.4284 | 60.9746 | 61.1175 | 60.6302 | 60.9186 | -0.5592 | -0.21479 | -0.51801 | -0.1736
597.1719 | 121.8613 | -61.0931 | 60.5072 | 0.085224 | -0.054257 | 0.038365 | -0.052488 | 0.045421 | 0.044377 | -0.11765 | 60.3421 | 60.3319 | 60.3879 | 60.3506 | 61.0112 | 61.1587 | 60.6759 | 60.9598 | 0.098957 | -0.040524 | 0.052098 | -0.038755 | 0.059154 | 0.05811 | -0.10392 | 60.3558 | 60.3456 | 60.4016 | 60.3643 | 61.0249 | 61.1724 | 60.6897 | 60.9735 | -0.66908 | -0.33383 | -0.62331 | -0.28806
598.9062 | 121.8201 | -61.1069 | 60.4889 | 0.080646 | -0.063415 | 0.029208 | -0.052488 | 0.040843 | 0.053534 | -0.11765 | 60.2597 | 60.2495 | 60.31 | 60.2727 | 61.1073 | 61.2503 | 60.7584 | 61.0376 | 0.094379 | -0.049682 | 0.042941 | -0.038755 | 0.054576 | 0.067267 | -0.10392 | 60.2734 | 60.2632 | 60.3238 | 60.2865 | 61.1211 | 61.264 | 60.7721 | 61.0513 | -0.84763 | -0.49865 | -0.79728 | -0.4483
600.5781 | 121.8384 | -61.2534 | 60.3241 | 0.089802 | -0.063415 | 0.033786 | -0.057066 | 0.049999 | 0.048956 | -0.11308 | 60.159 | 60.1487 | 60.191 | 60.1674 | 61.2126 | 61.351 | 60.8591 | 61.1429 | 0.10354 | -0.049682 | 0.047519 | -0.043333 | 0.063732 | 0.062689 | -0.099344 | 60.1727 | 60.1625 | 60.2047 | 60.1812 | 61.2264 | 61.3647 | 60.8728 | 61.1566 | -1.0537 | -0.7001 | -1.0216 | -0.66806
602.3281 | 121.9345 | -61.3495 | 60.228 | 0.085224 | -0.058836 | 0.033786 | -0.061645 | 0.045421 | 0.044377 | -0.11308 | 60.0262 | 60.0251 | 60.0628 | 60.0301 | 61.3408 | 61.4838 | 60.9964 | 61.2757 | 0.098957 | -0.045103 | 0.047519 | -0.047912 | 0.059154 | 0.05811 | -0.099344 | 60.0399 | 60.0388 | 60.0766 | 60.0438 | 61.3546 | 61.4975 | 61.0102 | 61.2894 | -1.3146 | -0.97023 | -1.278 | -0.93361
604.0625 | 121.7514 | -61.6104 | 60.0357 | 0.085224 | -0.058836 | 0.033786 | -0.047909 | 0.049999 | 0.048956 | -0.1085 | 59.8614 | 59.8603 | 59.9072 | 59.879 | 61.4919 | 61.6394 | 61.1521 | 61.4268 | 0.098957 | -0.045103 | 0.047519 | -0.034176 | 0.063732 | 0.062689 | -0.094766 | 59.8751 | 59.874 | 59.9209 | 59.8927 | 61.5056 | 61.6531 | 61.1658 | 61.4405 | -1.6305 | -1.2907 | -1.5847 | -1.2449
605.7969 | 121.9025 | -61.6882 | 59.8755 | 0.080646 | -0.054257 | 0.033786 | -0.057066 | 0.040843 | 0.048956 | -0.11308 | 59.692 | 59.6908 | 59.7286 | 59.6958 | 61.675 | 61.818 | 61.3261 | 61.6099 | 0.094379 | -0.040524 | 0.047519 | -0.043333 | 0.054576 | 0.062689 | -0.099344 | 59.7057 | 59.7046 | 59.7423 | 59.7095 | 61.6888 | 61.8317 | 61.3398 | 61.6236 | -1.9831 | -1.6341 | -1.9464 | -1.5975
607.4688 | 121.8475 | -61.9263 | 59.6329 | 0.076067 | -0.067994 | 0.033786 | -0.061645 | 0.036265 | 0.053534 | -0.11308 | 59.4905 | 59.4894 | 59.5226 | 59.4943 | 61.8719 | 62.0148 | 61.5275 | 61.8022 | 0.0898 | -0.054261 | 0.047519 | -0.047912 | 0.049998 | 0.067267 | -0.099344 | 59.5042 | 59.5031 | 59.5363 | 59.508 | 61.8856 | 62.0285 | 61.5413 | 61.8159 | -2.3814 | -2.037 | -2.3493 | -2.0049
609.2031 | 121.9116 | -62.1918 | 59.3903 | 0.076067 | -0.054257 | 0.033786 | -0.061645 | 0.045421 | 0.053534 | -0.1085 | 59.2112 | 59.2101 | 59.2479 | 59.2287 | 62.1512 | 62.3032 | 61.8022 | 62.0906 | 0.0898 | -0.040524 | 0.047519 | -0.047912 | 0.059154 | 0.067267 | -0.094766 | 59.225 | 59.2238 | 59.2616 | 59.2425 | 62.1649 | 62.317 | 61.816 | 62.1043 | -2.9399 | -2.591 | -2.9033 | -2.5543
610.9375 | 121.9025 | -62.4664 | 59.1064 | 0.094381 | -0.049678 | 0.033786 | -0.061645 | 0.045421 | 0.048956 | -0.11308 | 59.0006 | 58.9903 | 59.0281 | 59.0044 | 62.3663 | 62.5138 | 62.022 | 62.2966 | 0.10811 | -0.035945 | 0.047519 | -0.047912 | 0.059154 | 0.062689 | -0.099344 | 59.0143 | 59.004 | 59.0419 | 59.0181 | 62.3801 | 62.5276 | 62.0357 | 62.3103 | -3.3657 | -3.0214 | -3.3382 | -2.9939
612.6719 | 121.875 | -62.4115 | 59.1522 | 0.085224 | -0.058836 | 0.033786 | -0.052488 | 0.040843 | 0.039799 | -0.11308 | 59.5592 | 59.5855 | 59.6142 | 59.5859 | 61.8078 | 61.9553 | 61.4634 | 61.7289 | 0.098957 | -0.045103 | 0.047519 | -0.038755 | 0.054576 | 0.053532 | -0.099344 | 59.5729 | 59.5993 | 59.6279 | 59.5996 | 61.8215 | 61.969 | 61.4772 | 61.7426 | -2.2486 | -1.9042 | -2.1936 | -1.8493
614.4375 | 121.7697 | -48.0515 | 73.6908 | 0.080646 | -0.054257 | 0.038365 | -0.057066 | 0.040843 | 0.058113 | -0.11308 | 73.3862 | 73.4181 | 73.4818 | 73.4375 | 47.9176 | 48.0609 | 47.6504 | 47.8708 | 0.094379 | -0.040524 | 0.052098 | -0.043333 | 0.054576 | 0.071846 | -0.099344 | 73.4 | 73.4319 | 73.4955 | 73.4512 | 47.9313 | 48.0746 | 47.6642 | 47.8845 | 25.4686 | 25.7358 | 25.5641 | 25.8313
616.1562 | 121.8567 | -49.4568 | 72.1619 | 0.085224 | -0.054257 | 0.033786 | -0.052488 | 0.036265 | 0.039799 | -0.11308 | 72.0219 | 72.0536 | 72.122 | 72.0729 | 49.2911 | 49.4297 | 49.0056 | 49.2351 | 0.098957 | -0.040524 | 0.047519 | -0.038755 | 0.049998 | 0.053532 | -0.099344 | 72.0356 | 72.0674 | 72.1357 | 72.0866 | 49.3048 | 49.4434 | 49.0194 | 49.2488 | 22.7308 | 23.0162 | 22.8309 | 23.1164
617.8281 | 121.8475 | -60.2463 | 61.29 | 0.085224 | -0.035942 | 0.047522 | -0.043331 | 0.049999 | 0.053534 | -0.1085 | 58.8495 | 58.9262 | 58.9183 | 58.8853 | 62.6685 | 62.6512 | 62.2326 | 62.5667 | 0.098957 | -0.022209 | 0.061255 | -0.029598 | 0.063732 | 0.067267 | -0.094766 | 58.8633 | 58.9399 | 58.932 | 58.899 | 62.6822 | 62.6649 | 62.2463 | 62.5805 | -3.819 | -3.3831 | -3.7502 | -3.3143
619.5 | 121.7834 | -67.9138 | 53.6774 | 0.076067 | -0.049678 | 0.033786 | -0.066223 | 0.049999 | 0.048956 | -0.12223 | 54.2756 | 54.2878 | 54.3583 | 54.3154 | 67.0773 | 67.2155 | 66.7377 | 66.9938 | 0.0898 | -0.035945 | 0.047519 | -0.05249 | 0.063732 | 0.062689 | -0.1085 | 54.2893 | 54.3016 | 54.372 | 54.3292 | 67.091 | 67.2292 | 66.7515 | 67.0075 | -12.8017 | -12.4621 | -12.719 | -12.3794
621.2188 | 121.8979 | -71.7087 | 49.8688 | 0.080646 | -0.0451 | 0.033786 | -0.057066 | 0.045421 | 0.039799 | -0.11308 | 49.7246 | 49.7182 | 49.7617 | 49.7272 | 71.8111 | 71.7844 | 71.2703 | 71.5537 | 0.094379 | -0.031367 | 0.047519 | -0.043333 | 0.059154 | 0.053532 | -0.099344 | 49.7383 | 49.7319 | 49.7754 | 49.741 | 71.8248 | 71.7981 | 71.2841 | 71.5674 | -22.0865 | -21.5457 | -22.0494 | -21.5086
622.9531 | 121.9528 | -114.4318 | 7.0999 | 0.085224 | -0.0451 | 0.033786 | -0.057066 | 0.040843 | 0.044377 | -0.1085 | 7.0942 | 7.1764 | 7.1379 | 7.1606 | 114.4751 | 114.4566 | 114.1698 | 114.2955 | 0.098957 | -0.031367 | 0.047519 | -0.043333 | 0.054576 | 0.05811 | -0.094766 | 7.1079 | 7.1901 | 7.1516 | 7.1743 | 114.4888 | 114.4703 | 114.1836 | 114.3092 | -107.3809 | -107.0756 | -107.3372 | -107.0319
624.7031 | 121.8018 | -115.7181 | 5.928 | 0.076067 | -0.0451 | 0.038365 | -0.061645 | 0.045421 | 0.048956 | -0.11308 | 5.9359 | 6.0271 | 5.9338 | 6.0066 | 115.6334 | 115.6194 | 115.0306 | 115.4629 | 0.0898 | -0.031367 | 0.052098 | -0.047912 | 0.059154 | 0.062689 | -0.099344 | 5.9496 | 6.0408 | 5.9475 | 6.0204 | 115.6471 | 115.6331 | 115.0443 | 115.4767 | -109.6975 | -109.0947 | -109.6996 | -109.0967
626.3906 | 121.8842 | -116.4001 | 5.191 | 0.080646 | -0.040521 | 0.033786 | -0.057066 | 0.036265 | 0.053534 | -0.1085 | 5.391 | 5.4685 | 5.3798 | 5.4526 | 116.1919 | 116.1733 | 115.5891 | 116.0215 | 0.094379 | -0.026788 | 0.047519 | -0.043333 | 0.049998 | 0.067267 | -0.094766 | 5.4047 | 5.4822 | 5.3936 | 5.4663 | 116.2056 | 116.1871 | 115.6029 | 116.0352 | -110.8009 | -110.1981 | -110.8121 | -110.2093
628.0781 | 121.843 | -116.4505 | 5.127 | 0.080646 | -0.049678 | 0.033786 | -0.052488 | 0.040843 | 0.048956 | -0.11308 | 5.7619 | 5.8577 | 5.7781 | 5.8372 | 115.5922 | 115.7567 | 115.1816 | 115.6049 | 0.094379 | -0.035945 | 0.047519 | -0.038755 | 0.054576 | 0.062689 | -0.099344 | 5.7756 | 5.8714 | 5.7919 | 5.851 | 115.6059 | 115.7705 | 115.1954 | 115.6186 | -109.8303 | -109.4198 | -109.814 | -109.4035
629.7812 | 121.8292 | -118.3914 | 3.1082 | 0.076067 | -0.0451 | 0.033786 | -0.052488 | 0.045421 | 0.039799 | -0.11308 | 3.001 | 3.1012 | 2.9991 | 3.0761 | 118.307 | 118.4807 | 117.9058 | 118.3243 | 0.0898 | -0.031367 | 0.047519 | -0.038755 | 0.059154 | 0.053532 | -0.099344 | 3.0148 | 3.115 | 3.0129 | 3.0898 | 118.3208 | 118.4944 | 117.9195 | 118.338 | -115.306 | -114.9047 | -115.3079 | -114.9067
631.4688 | 121.7377 | -118.9178 | 2.6047 | 0.080646 | -0.0451 | 0.033786 | -0.061645 | 0.049999 | 0.048956 | -0.11308 | 2.4928 | 2.5884 | 2.4909 | 2.5632 | 118.7877 | 118.966 | 118.3865 | 118.6905 | 0.094379 | -0.031367 | 0.047519 | -0.047912 | 0.063732 | 0.062689 | -0.099344 | 2.5066 | 2.6021 | 2.5047 | 2.5769 | 118.8015 | 118.9797 | 118.4003 | 118.7043 | -116.2949 | -115.8937 | -116.2968 | -115.8956
633.2031 | 121.7056 | -118.9636 | 2.5772 | 0.080646 | -0.040521 | 0.038365 | -0.057066 | 0.036265 | 0.044377 | -0.11765 | 2.447 | 2.538 | 2.4406 | 2.522 | 118.8289 | 119.0072 | 118.4231 | 118.718 | 0.094379 | -0.026788 | 0.052098 | -0.043333 | 0.049998 | 0.05811 | -0.10392 | 2.4608 | 2.5518 | 2.4543 | 2.5357 | 118.8427 | 119.0209 | 118.4369 | 118.7317 | -116.3819 | -115.9761 | -116.3884 | -115.9826
634.9219 | 121.6461 | -119.1788 | 2.3666 | 0.080646 | -0.040521 | 0.029208 | -0.057066 | 0.036265 | 0.039799 | -0.12223 | 2.2227 | 2.3183 | 2.2162 | 2.2976 | 119.0441 | 119.2223 | 118.6246 | 118.9195 | 0.094379 | -0.026788 | 0.042941 | -0.043333 | 0.049998 | 0.053532 | -0.1085 | 2.2364 | 2.332 | 2.23 | 2.3114 | 119.0578 | 119.2361 | 118.6383 | 118.9332 | -116.8214 | -116.4019 | -116.8279 | -116.4083
636.6719 | 121.6278 | -118.959 | 2.5497 | 0.076067 | -0.040521 | 0.033786 | -0.047909 | 0.045421 | 0.044377 | -0.11308 | 2.2822 | 2.3824 | 2.2712 | 2.3526 | 119.1586 | 119.1445 | 118.7665 | 118.9927 | 0.0898 | -0.026788 | 0.047519 | -0.034176 | 0.059154 | 0.05811 | -0.099344 | 2.2959 | 2.3961 | 2.2849 | 2.3663 | 119.1723 | 119.1582 | 118.7803 | 119.0064 | -116.8764 | -116.4843 | -116.8874 | -116.4953
638.4219 | 121.7239 | -120.0577 | 1.4236 | 0.085224 | -0.040521 | 0.029208 | -0.057066 | 0.040843 | 0.048956 | -0.11308 | 1.3848 | 1.4803 | 1.4196 | 1.4551 | 120.0467 | 120.0326 | 119.7463 | 119.8809 | 0.098957 | -0.026788 | 0.042941 | -0.043333 | 0.054576 | 0.062689 | -0.099344 | 1.3986 | 1.4941 | 1.4334 | 1.4688 | 120.0605 | 120.0464 | 119.76 | 119.8946 | -118.6619 | -118.3615 | -118.6271 | -118.3267
640.1094 | 121.431 | -121.2616 | 0.15564 | 0.080646 | -0.040521 | 0.024629 | -0.061645 | 0.054577 | 0.048956 | -0.12223 | 2.7126 | 2.625 | 2.6832 | 2.6548 | 118.513 | 118.5493 | 118.2309 | 118.2694 | 0.094379 | -0.026788 | 0.038362 | -0.047912 | 0.06831 | 0.062689 | -0.1085 | 2.7263 | 2.6388 | 2.697 | 2.6685 | 118.5268 | 118.5631 | 118.2446 | 118.2831 | -115.8005 | -115.5183 | -115.8298 | -115.5476
641.8438 | 121.6141 | -121.4447 | 0.13275 | 0.085224 | -0.035942 | 0.038365 | -0.052488 | 0.040843 | 0.044377 | -0.11308 | -0.01619 | 0.079217 | 0.018672 | 0.063059 | 121.4797 | 121.4702 | 121.1839 | 121.3047 | 0.098957 | -0.022209 | 0.052098 | -0.038755 | 0.054576 | 0.05811 | -0.099344 | -0.002457 | 0.09295 | 0.032405 | 0.076792 | 121.4934 | 121.4839 | 121.1976 | 121.3184 | -121.4959 | -121.2001 | -121.461 | -121.1652
643.5156 | 121.7697 | -121.4218 | 0.09613 | 0.076067 | -0.040521 | 0.029208 | -0.057066 | 0.040843 | 0.039799 | -0.11765 | -0.020768 | 0.079217 | 0.004937 | 0.05848 | 121.5209 | 121.5068 | 120.9184 | 121.3459 | 0.0898 | -0.026788 | 0.042941 | -0.043333 | 0.054576 | 0.053532 | -0.10392 | -0.007035 | 0.09295 | 0.01867 | 0.072213 | 121.5346 | 121.5205 | 120.9321 | 121.3596 | -121.5417 | -120.9391 | -121.516 | -120.9134
645.25 | 121.6644 | -121.4493 | 0.14648 | 0.080646 | -0.0451 | 0.047522 | -0.057066 | 0.045421 | 0.044377 | -0.11308 | -0.029925 | 0.079217 | 0.000359 | 0.053901 | 121.5438 | 121.5388 | 120.9413 | 121.3734 | 0.094379 | -0.031367 | 0.061255 | -0.043333 | 0.059154 | 0.05811 | -0.099344 | -0.016192 | 0.09295 | 0.014092 | 0.067634 | 121.5575 | 121.5526 | 120.955 | 121.3871 | -121.5737 | -120.9712 | -121.5434 | -120.9409
646.9219 | 121.7468 | -121.4767 | 0.14648 | 0.085224 | -0.0451 | 0.029208 | -0.057066 | 0.040843 | 0.044377 | -0.11765 | -0.025347 | 0.079217 | -0.004219 | 0.05848 | 121.553 | 121.548 | 120.9596 | 121.3871 | 0.098957 | -0.031367 | 0.042941 | -0.043333 | 0.054576 | 0.05811 | -0.10392 | -0.011614 | 0.09295 | 0.009514 | 0.072213 | 121.5667 | 121.5617 | 120.9733 | 121.4008 | -121.5783 | -120.9849 | -121.5572 | -120.9638
648.6562 | 121.7422 | -121.4951 | 0.13275 | 0.076067 | -0.0451 | 0.029208 | -0.057066 | 0.040843 | 0.044377 | -0.11765 | -0.025347 | 0.079217 | 0.000359 | 0.053901 | 121.5713 | 121.5571 | 120.9596 | 121.3962 | 0.0898 | -0.031367 | 0.042941 | -0.043333 | 0.054576 | 0.05811 | -0.10392 | -0.011614 | 0.09295 | 0.014092 | 0.067634 | 121.585 | 121.5709 | 120.9733 | 121.41 | -121.5966 | -120.9849 | -121.5709 | -120.9592
650.3906 | 121.7972 | -121.4813 | 0.10529 | 0.085224 | -0.040521 | 0.029208 | -0.061645 | 0.045421 | 0.048956 | -0.11765 | -0.025347 | 0.074638 | 0.004937 | 0.053901 | 121.5804 | 121.5709 | 120.9687 | 121.2681 | 0.098957 | -0.026788 | 0.042941 | -0.047912 | 0.059154 | 0.062689 | -0.10392 | -0.011614 | 0.088371 | 0.01867 | 0.067634 | 121.5942 | 121.5846 | 120.9825 | 121.2818 | -121.6058 | -120.9941 | -121.5755 | -120.9638
652.1406 | 121.8063 | -121.4767 | 0.10986 | 0.080646 | -0.040521 | 0.024629 | -0.061645 | 0.040843 | 0.044377 | -0.11765 | -0.029925 | 0.079217 | 0.000359 | 0.049322 | 121.5804 | 121.5754 | 120.9779 | 121.2772 | 0.094379 | -0.026788 | 0.038362 | -0.047912 | 0.054576 | 0.05811 | -0.10392 | -0.016192 | 0.09295 | 0.014092 | 0.063055 | 121.5942 | 121.5892 | 120.9916 | 121.2909 | -121.6103 | -121.0078 | -121.5801 | -120.9775
653.875 | 121.8063 | -121.4859 | 0.10986 | 0.080646 | -0.040521 | 0.042944 | -0.057066 | 0.045421 | 0.048956 | -0.11765 | -0.020768 | 0.079217 | 0.000359 | 0.053901 | 121.585 | 121.5709 | 120.9825 | 121.2772 | 0.094379 | -0.026788 | 0.056677 | -0.043333 | 0.059154 | 0.062689 | -0.10392 | -0.007035 | 0.09295 | 0.014092 | 0.067634 | 121.5987 | 121.5846 | 120.9962 | 121.2909 | -121.6058 | -121.0032 | -121.5846 | -120.9821
655.5469 | 121.7422 | -121.5454 | 0.13733 | 0.080646 | -0.040521 | 0.024629 | -0.057066 | 0.045421 | 0.048956 | -0.1085 | -0.029925 | 0.07006 | -0.004219 | 0.053901 | 121.5896 | 121.5846 | 120.9825 | 121.2818 | 0.094379 | -0.026788 | 0.038362 | -0.043333 | 0.059154 | 0.062689 | -0.094766 | -0.016192 | 0.083793 | 0.009514 | 0.067634 | 121.6033 | 121.5983 | 120.9962 | 121.2955 | -121.6195 | -121.0124 | -121.5938 | -120.9867
657.2812 | 121.8155 | -121.5042 | 0.10071 | 0.080646 | -0.0451 | 0.038365 | -0.052488 | 0.040843 | 0.039799 | -0.11308 | -0.025347 | 0.079217 | -0.004219 | 0.044743 | 121.6033 | 121.5846 | 120.9916 | 121.2909 | 0.094379 | -0.031367 | 0.052098 | -0.038755 | 0.054576 | 0.053532 | -0.099344 | -0.011614 | 0.09295 | 0.009514 | 0.058476 | 121.617 | 121.5983 | 121.0054 | 121.3047 | -121.6287 | -121.017 | -121.6075 | -120.9958
659.0156 | 121.7697 | -121.5408 | 0.1236 | 0.089802 | -0.040521 | 0.033786 | -0.052488 | 0.040843 | 0.044377 | -0.1085 | -0.034504 | 0.074638 | -0.008798 | 0.049322 | 121.6079 | 121.5938 | 121.0054 | 121.3001 | 0.10354 | -0.026788 | 0.047519 | -0.038755 | 0.054576 | 0.05811 | -0.094766 | -0.020771 | 0.088371 | 0.004935 | 0.063055 | 121.6216 | 121.6075 | 121.0191 | 121.3138 | -121.6424 | -121.0399 | -121.6167 | -121.0142
660.75 | 121.7651 | -121.5454 | 0.11902 | 0.080646 | -0.054257 | 0.024629 | -0.057066 | 0.040843 | 0.039799 | -0.11308 | -0.034504 | 0.065481 | -0.008798 | 0.044743 | 121.6079 | 121.5938 | 121.0145 | 121.3001 | 0.094379 | -0.040524 | 0.038362 | -0.043333 | 0.054576 | 0.053532 | -0.099344 | -0.020771 | 0.079214 | 0.004935 | 0.058476 | 121.6216 | 121.6075 | 121.0282 | 121.3138 | -121.6424 | -121.049 | -121.6167 | -121.0233
662.4531 | 121.7102 | -121.5317 | 0.13733 | 0.085224 | -0.0451 | 0.033786 | -0.061645 | 0.045421 | 0.039799 | -0.1085 | -0.043661 | 0.079217 | -0.008798 | 0.053901 | 121.6125 | 121.5892 | 120.9962 | 121.3047 | 0.098957 | -0.031367 | 0.047519 | -0.047912 | 0.059154 | 0.053532 | -0.094766 | -0.029928 | 0.09295 | 0.004935 | 0.067634 | 121.6262 | 121.6029 | 121.0099 | 121.3184 | -121.6561 | -121.0399 | -121.6213 | -121.005
664.1719 | 121.8704 | -121.5225 | 0.09613 | 0.080646 | -0.040521 | 0.033786 | -0.052488 | 0.045421 | 0.039799 | -0.11308 | -0.034504 | 0.07006 | -0.004219 | 0.049322 | 121.6079 | 121.5892 | 121.0191 | 121.3047 | 0.094379 | -0.026788 | 0.047519 | -0.038755 | 0.059154 | 0.053532 | -0.099344 | -0.020771 | 0.083793 | 0.009514 | 0.063055 | 121.6216 | 121.6029 | 121.0328 | 121.3184 | -121.6424 | -121.0536 | -121.6121 | -121.0233
665.9062 | 121.7514 | -121.5546 | 0.13733 | 0.076067 | -0.035942 | 0.033786 | -0.057066 | 0.045421 | 0.044377 | -0.11308 | -0.025347 | 0.07006 | -0.004219 | 0.049322 | 121.6125 | 121.6029 | 121.0054 | 121.3047 | 0.0898 | -0.022209 | 0.047519 | -0.043333 | 0.059154 | 0.05811 | -0.099344 | -0.011614 | 0.083793 | 0.009514 | 0.063055 | 121.6262 | 121.6166 | 121.0191 | 121.3184 | -121.6378 | -121.0307 | -121.6167 | -121.0096
667.5938 | 121.7789 | -121.5683 | 0.11444 | 0.089802 | -0.0451 | 0.033786 | -0.052488 | 0.040843 | 0.044377 | -0.12223 | -0.029925 | 0.07006 | -0.004219 | 0.044743 | 121.6079 | 121.5983 | 121.0099 | 121.3047 | 0.10354 | -0.031367 | 0.047519 | -0.038755 | 0.054576 | 0.05811 | -0.1085 | -0.016192 | 0.083793 | 0.009514 | 0.058476 | 121.6216 | 121.6121 | 121.0237 | 121.3184 | -121.6378 | -121.0399 | -121.6121 | -121.0142
669.3281 | 121.7514 | -121.5775 | 0.11902 | 0.080646 | -0.040521 | 0.038365 | -0.047909 | 0.045421 | 0.039799 | -0.12223 | -0.034504 | 0.074638 | -0.004219 | 0.044743 | 121.6125 | 121.5938 | 121.0099 | 121.3093 | 0.094379 | -0.026788 | 0.052098 | -0.034176 | 0.059154 | 0.053532 | -0.1085 | -0.020771 | 0.088371 | 0.009514 | 0.058476 | 121.6262 | 121.6075 | 121.0237 | 121.323 | -121.647 | -121.0444 | -121.6167 | -121.0142
671.0625 | 121.8155 | -121.5271 | 0.1236 | 0.076067 | -0.040521 | 0.033786 | -0.052488 | 0.036265 | 0.044377 | -0.12223 | -0.025347 | 0.065481 | -0.004219 | 0.053901 | 121.6079 | 121.5938 | 121.0191 | 121.3047 | 0.0898 | -0.026788 | 0.047519 | -0.038755 | 0.049998 | 0.05811 | -0.1085 | -0.011614 | 0.079214 | 0.009514 | 0.067634 | 121.6216 | 121.6075 | 121.0328 | 121.3184 | -121.6332 | -121.0444 | -121.6121 | -121.0233
672.7969 | 121.8613 | -121.5363 | 0.11444 | 0.089802 | -0.0451 | 0.033786 | -0.057066 | 0.040843 | 0.035221 | -0.11765 | -0.034504 | 0.074638 | -0.013376 | 0.049322 | 121.6125 | 121.5983 | 121.0237 | 121.3047 | 0.10354 | -0.031367 | 0.047519 | -0.043333 | 0.054576 | 0.048954 | -0.10392 | -0.020771 | 0.088371 | 0.000357 | 0.063055 | 121.6262 | 121.6121 | 121.0374 | 121.3184 | -121.647 | -121.0582 | -121.6258 | -121.037
674.4688 | 121.8475 | -121.4905 | 0.10071 | 0.076067 | -0.0451 | 0.029208 | -0.061645 | 0.045421 | 0.039799 | -0.11308 | -0.039082 | 0.07006 | -0.004219 | 0.044743 | 121.617 | 121.5983 | 121.0099 | 121.3093 | 0.0898 | -0.031367 | 0.042941 | -0.047912 | 0.059154 | 0.053532 | -0.099344 | -0.025349 | 0.083793 | 0.009514 | 0.058476 | 121.6308 | 121.6121 | 121.0237 | 121.323 | -121.6561 | -121.049 | -121.6213 | -121.0142
676.2031 | 121.8979 | -121.5454 | 0.10529 | 0.076067 | -0.040521 | 0.024629 | -0.057066 | 0.040843 | 0.039799 | -0.11765 | -0.025347 | 0.074638 | -0.008798 | 0.040164 | 121.617 | 121.5938 | 121.0237 | 121.3093 | 0.0898 | -0.026788 | 0.038362 | -0.043333 | 0.054576 | 0.053532 | -0.10392 | -0.011614 | 0.088371 | 0.004935 | 0.053897 | 121.6308 | 121.6075 | 121.0374 | 121.323 | -121.6424 | -121.049 | -121.6258 | -121.0325
677.8906 | 121.7789 | -121.5591 | 0.11902 | 0.080646 | -0.0451 | 0.029208 | -0.052488 | 0.040843 | 0.048956 | -0.12223 | -0.039082 | 0.07006 | -0.008798 | 0.049322 | 121.6216 | 121.6029 | 121.0237 | 121.3001 | 0.094379 | -0.031367 | 0.042941 | -0.038755 | 0.054576 | 0.062689 | -0.1085 | -0.025349 | 0.083793 | 0.004935 | 0.063055 | 121.6354 | 121.6166 | 121.0374 | 121.3138 | -121.6607 | -121.0628 | -121.6304 | -121.0325
679.625 | 121.8567 | -121.5317 | 0.091553 | 0.080646 | -0.054257 | 0.033786 | -0.047909 | 0.049999 | 0.048956 | -0.11765 | -0.029925 | 0.07006 | -0.013376 | 0.040164 | 121.617 | 121.6075 | 121.0237 | 121.3093 | 0.094379 | -0.040524 | 0.047519 | -0.034176 | 0.063732 | 0.062689 | -0.10392 | -0.016192 | 0.083793 | 0.000357 | 0.053897 | 121.6308 | 121.6212 | 121.0374 | 121.323 | -121.647 | -121.0536 | -121.6304 | -121.037
681.3594 | 121.8796 | -121.5225 | 0.10529 | 0.085224 | -0.049678 | 0.033786 | -0.052488 | 0.036265 | 0.044377 | -0.11765 | -0.029925 | 0.065481 | -0.013376 | 0.044743 | 121.6125 | 121.5983 | 121.0237 | 121.3138 | 0.098957 | -0.035945 | 0.047519 | -0.038755 | 0.049998 | 0.05811 | -0.10392 | -0.016192 | 0.079214 | 0.000357 | 0.058476 | 121.6262 | 121.6121 | 121.0374 | 121.3276 | -121.6424 | -121.0536 | -121.6258 | -121.037
683.0625 | 121.8338 | -121.5179 | 0.11444 | 0.080646 | -0.040521 | 0.033786 | -0.057066 | 0.040843 | 0.035221 | -0.11765 | -0.029925 | 0.07006 | -0.008798 | 0.044743 | 121.6216 | 121.5983 | 121.0282 | 121.3001 | 0.094379 | -0.026788 | 0.047519 | -0.043333 | 0.054576 | 0.048954 | -0.10392 | -0.016192 | 0.083793 | 0.004935 | 0.058476 | 121.6354 | 121.6121 | 121.042 | 121.3138 | -121.6516 | -121.0582 | -121.6304 | -121.037
684.7656 | 121.8796 | -121.5317 | 0.082397 | 0.080646 | -0.040521 | 0.033786 | -0.052488 | 0.031687 | 0.044377 | -0.11765 | -0.034504 | 0.060902 | -0.008798 | 0.040164 | 121.617 | 121.6029 | 121.0191 | 121.3093 | 0.094379 | -0.026788 | 0.047519 | -0.038755 | 0.04542 | 0.05811 | -0.10392 | -0.020771 | 0.074635 | 0.004935 | 0.053897 | 121.6308 | 121.6166 | 121.0328 | 121.323 | -121.6516 | -121.0536 | -121.6258 | -121.0279
686.5 | 121.756 | -121.5454 | 0.12817 | 0.085224 | -0.040521 | 0.038365 | -0.047909 | 0.045421 | 0.039799 | -0.12223 | -0.034504 | 0.065481 | -0.013376 | 0.049322 | 121.6216 | 121.6029 | 121.0191 | 121.3093 | 0.098957 | -0.026788 | 0.052098 | -0.034176 | 0.059154 | 0.053532 | -0.1085 | -0.020771 | 0.079214 | 0.000357 | 0.063055 | 121.6354 | 121.6166 | 121.0328 | 121.323 | -121.6561 | -121.0536 | -121.635 | -121.0325
688.1719 | 121.8842 | -121.5225 | 0.091553 | 0.080646 | -0.040521 | 0.029208 | -0.052488 | 0.040843 | 0.039799 | -0.11765 | -0.034504 | 0.07006 | -0.013376 | 0.044743 | 121.6216 | 121.6029 | 121.0328 | 121.3184 | 0.094379 | -0.026788 | 0.042941 | -0.038755 | 0.054576 | 0.053532 | -0.10392 | -0.020771 | 0.083793 | 0.000357 | 0.058476 | 121.6354 | 121.6166 | 121.0466 | 121.3322 | -121.6561 | -121.0673 | -121.635 | -121.0462
689.9062 | 121.8842 | -121.5134 | 0.091553 | 0.076067 | -0.049678 | 0.038365 | -0.057066 | 0.045421 | 0.039799 | -0.11765 | -0.034504 | 0.065481 | -0.004219 | 0.044743 | 121.6216 | 121.6121 | 121.0237 | 121.3184 | 0.0898 | -0.035945 | 0.052098 | -0.043333 | 0.059154 | 0.053532 | -0.10392 | -0.020771 | 0.079214 | 0.009514 | 0.058476 | 121.6354 | 121.6258 | 121.0374 | 121.3322 | -121.6561 | -121.0582 | -121.6258 | -121.0279
691.6406 | 121.7514 | -121.5317 | 0.12817 | 0.076067 | -0.0451 | 0.038365 | -0.043331 | 0.045421 | 0.039799 | -0.11308 | -0.043661 | 0.07006 | -0.013376 | 0.049322 | 121.6216 | 121.6121 | 121.0191 | 121.3138 | 0.0898 | -0.031367 | 0.052098 | -0.029598 | 0.059154 | 0.053532 | -0.099344 | -0.029928 | 0.083793 | 0.000357 | 0.063055 | 121.6354 | 121.6258 | 121.0328 | 121.3276 | -121.6653 | -121.0628 | -121.635 | -121.0325
693.3281 | 121.756 | -121.582 | 0.11902 | 0.080646 | -0.040521 | 0.042944 | -0.052488 | 0.049999 | 0.048956 | -0.11765 | -0.034504 | 0.060902 | -0.008798 | 0.035585 | 121.6262 | 121.6075 | 121.0282 | 121.3093 | 0.094379 | -0.026788 | 0.056677 | -0.038755 | 0.063732 | 0.062689 | -0.10392 | -0.020771 | 0.074635 | 0.004935 | 0.049318 | 121.6399 | 121.6212 | 121.042 | 121.323 | -121.6607 | -121.0628 | -121.635 | -121.037
695.0625 | 121.8933 | -121.5225 | 0.09613 | 0.076067 | -0.054257 | 0.029208 | -0.052488 | 0.040843 | 0.039799 | -0.11765 | -0.039082 | 0.060902 | -0.013376 | 0.040164 | 121.6216 | 121.6029 | 121.0282 | 121.3093 | 0.0898 | -0.040524 | 0.042941 | -0.038755 | 0.054576 | 0.053532 | -0.10392 | -0.025349 | 0.074635 | 0.000357 | 0.053897 | 121.6354 | 121.6166 | 121.042 | 121.323 | -121.6607 | -121.0673 | -121.635 | -121.0416
696.7969 | 121.7468 | -121.5546 | 0.13733 | 0.076067 | -0.035942 | 0.033786 | -0.057066 | 0.049999 | 0.039799 | -0.11765 | -0.039082 | 0.065481 | -0.008798 | 0.044743 | 121.6262 | 121.6121 | 121.0282 | 121.3184 | 0.0898 | -0.022209 | 0.047519 | -0.043333 | 0.063732 | 0.053532 | -0.10392 | -0.025349 | 0.079214 | 0.004935 | 0.058476 | 121.6399 | 121.6258 | 121.042 | 121.3322 | -121.6653 | -121.0673 | -121.635 | -121.037
698.4844 | 121.8658 | -121.5317 | 0.086975 | 0.080646 | -0.049678 | 0.033786 | -0.052488 | 0.045421 | 0.048956 | -0.11765 | -0.039082 | 0.065481 | -0.004219 | 0.053901 | 121.617 | 121.6121 | 121.0374 | 121.323 | 0.094379 | -0.035945 | 0.047519 | -0.038755 | 0.059154 | 0.062689 | -0.10392 | -0.025349 | 0.079214 | 0.009514 | 0.067634 | 121.6308 | 121.6258 | 121.0511 | 121.3367 | -121.6561 | -121.0765 | -121.6213 | -121.0416
700.2344 | 121.8704 | -121.4859 | 0.082397 | 0.089802 | -0.0451 | 0.033786 | -0.061645 | 0.049999 | 0.035221 | -0.11765 | -0.034504 | 0.074638 | -0.013376 | 0.044743 | 121.617 | 121.6029 | 121.0237 | 121.3138 | 0.10354 | -0.031367 | 0.047519 | -0.047912 | 0.063732 | 0.048954 | -0.10392 | -0.020771 | 0.088371 | 0.000357 | 0.058476 | 121.6308 | 121.6166 | 121.0374 | 121.3276 | -121.6516 | -121.0582 | -121.6304 | -121.037
701.9688 | 121.8338 | -121.5454 | 0.09613 | 0.085224 | -0.0451 | 0.033786 | -0.057066 | 0.040843 | 0.044377 | -0.11765 | -0.029925 | 0.060902 | -0.008798 | 0.044743 | 121.6308 | 121.6029 | 121.0282 | 121.3138 | 0.098957 | -0.031367 | 0.047519 | -0.043333 | 0.054576 | 0.05811 | -0.10392 | -0.016192 | 0.074635 | 0.004935 | 0.058476 | 121.6445 | 121.6166 | 121.042 | 121.3276 | -121.6607 | -121.0582 | -121.6396 | -121.037
703.7188 | 121.7697 | -121.5866 | 0.10529 | 0.076067 | -0.0451 | 0.029208 | -0.052488 | 0.036265 | 0.039799 | -0.11308 | -0.052818 | 0.060902 | -0.017954 | 0.026427 | 121.6445 | 121.6121 | 121.042 | 121.323 | 0.0898 | -0.031367 | 0.042941 | -0.038755 | 0.049998 | 0.053532 | -0.099344 | -0.039085 | 0.074635 | -0.004221 | 0.04016 | 121.6582 | 121.6258 | 121.0557 | 121.3367 | -121.6973 | -121.0948 | -121.6625 | -121.0599
705.3906 | 121.875 | -121.5591 | 0.07782 | 0.076067 | -0.040521 | 0.024629 | -0.061645 | 0.045421 | 0.039799 | -0.11765 | -0.048239 | 0.060902 | -0.017954 | 0.035585 | 121.6354 | 121.6075 | 121.0374 | 121.3276 | 0.0898 | -0.026788 | 0.038362 | -0.047912 | 0.059154 | 0.053532 | -0.10392 | -0.034506 | 0.074635 | -0.004221 | 0.049318 | 121.6491 | 121.6212 | 121.0511 | 121.3413 | -121.6836 | -121.0856 | -121.6533 | -121.0554
707.0625 | 121.8292 | -121.5637 | 0.086975 | 0.085224 | -0.0451 | 0.033786 | -0.057066 | 0.040843 | 0.039799 | -0.11308 | -0.048239 | 0.042587 | -0.017954 | 0.031006 | 121.6445 | 121.6167 | 121.0328 | 121.323 | 0.098957 | -0.031367 | 0.047519 | -0.043333 | 0.054576 | 0.053532 | -0.099344 | -0.034506 | 0.05632 | -0.004221 | 0.044739 | 121.6582 | 121.6304 | 121.0466 | 121.3367 | -121.6928 | -121.0811 | -121.6625 | -121.0508
708.8125 | 121.8613 | -121.5317 | 0.086975 | 0.085224 | -0.035942 | 0.029208 | -0.057066 | 0.045421 | 0.039799 | -0.11765 | -0.052818 | 0.051744 | -0.017954 | 0.035585 | 121.6399 | 121.6167 | 121.042 | 121.3184 | 0.098957 | -0.022209 | 0.042941 | -0.043333 | 0.059154 | 0.053532 | -0.10392 | -0.039085 | 0.065477 | -0.004221 | 0.049318 | 121.6537 | 121.6304 | 121.0557 | 121.3322 | -121.6928 | -121.0948 | -121.6579 | -121.0599
710.4844 | 121.8292 | -121.5408 | 0.07782 | 0.080646 | -0.0451 | 0.033786 | -0.057066 | 0.036265 | 0.039799 | -0.12223 | -0.052818 | 0.056323 | -0.022532 | 0.035585 | 121.6445 | 121.6167 | 121.0374 | 121.3184 | 0.094379 | -0.031367 | 0.047519 | -0.043333 | 0.049998 | 0.053532 | -0.1085 | -0.039085 | 0.070056 | -0.008799 | 0.049318 | 121.6582 | 121.6304 | 121.0511 | 121.3322 | -121.6973 | -121.0902 | -121.667 | -121.0599
712.1562 | 121.8338 | -121.5088 | 0.10071 | 0.080646 | -0.0451 | 0.033786 | -0.061645 | 0.045421 | 0.044377 | -0.11765 | -0.048239 | 0.056323 | -0.017954 | 0.031006 | 121.6399 | 121.6121 | 121.042 | 121.3276 | 0.094379 | -0.031367 | 0.047519 | -0.047912 | 0.059154 | 0.05811 | -0.10392 | -0.034506 | 0.070056 | -0.004221 | 0.044739 | 121.6537 | 121.6258 | 121.0557 | 121.3413 | -121.6882 | -121.0902 | -121.6579 | -121.0599
713.8906 | 121.8704 | -121.5363 | 0.07782 | 0.080646 | -0.040521 | 0.038365 | -0.057066 | 0.040843 | 0.044377 | -0.1085 | -0.052818 | 0.056323 | -0.017954 | 0.031006 | 121.6354 | 121.6121 | 121.0374 | 121.3184 | 0.094379 | -0.026788 | 0.052098 | -0.043333 | 0.054576 | 0.05811 | -0.094766 | -0.039085 | 0.070056 | -0.004221 | 0.044739 | 121.6491 | 121.6258 | 121.0511 | 121.3322 | -121.6882 | -121.0902 | -121.6533 | -121.0554
715.625 | 121.756 | -121.5591 | 0.11444 | 0.076067 | -0.035942 | 0.038365 | -0.061645 | 0.045421 | 0.039799 | -0.11308 | -0.052818 | 0.060902 | -0.022532 | 0.026427 | 121.6354 | 121.6075 | 121.042 | 121.3276 | 0.0898 | -0.022209 | 0.052098 | -0.047912 | 0.059154 | 0.053532 | -0.099344 | -0.039085 | 0.074635 | -0.008799 | 0.04016 | 121.6491 | 121.6212 | 121.0557 | 121.3413 | -121.6882 | -121.0948 | -121.6579 | -121.0645
717.3594 | 121.843 | -121.55 | 0.07782 | 0.080646 | -0.040521 | 0.033786 | -0.052488 | 0.045421 | 0.044377 | -0.11308 | -0.052818 | 0.060902 | -0.027111 | 0.026427 | 121.6354 | 121.6121 | 121.0374 | 121.323 | 0.094379 | -0.026788 | 0.047519 | -0.038755 | 0.059154 | 0.05811 | -0.099344 | -0.039085 | 0.074635 | -0.013378 | 0.04016 | 121.6491 | 121.6258 | 121.0511 | 121.3367 | -121.6882 | -121.0902 | -121.6625 | -121.0645
719.0312 | 121.8567 | -121.5408 | 0.086975 | 0.076067 | -0.040521 | 0.029208 | -0.057066 | 0.045421 | 0.035221 | -0.11765 | -0.052818 | 0.056323 | -0.027111 | 0.031006 | 121.6399 | 121.6121 | 121.042 | 121.323 | 0.0898 | -0.026788 | 0.042941 | -0.043333 | 0.059154 | 0.048954 | -0.10392 | -0.039085 | 0.070056 | -0.013378 | 0.044739 | 121.6537 | 121.6258 | 121.0557 | 121.3367 | -121.6928 | -121.0948 | -121.667 | -121.0691
720.7656 | 121.7972 | -121.5546 | 0.10071 | 0.085224 | -0.040521 | 0.029208 | -0.057066 | 0.040843 | 0.044377 | -0.1085 | -0.048239 | 0.056323 | -0.013376 | 0.026427 | 121.6445 | 121.6167 | 121.042 | 121.3047 | 0.098957 | -0.026788 | 0.042941 | -0.043333 | 0.054576 | 0.05811 | -0.094766 | -0.034506 | 0.070056 | 0.000357 | 0.04016 | 121.6582 | 121.6304 | 121.0557 | 121.3184 | -121.6928 | -121.0902 | -121.6579 | -121.0554
722.5 | 121.7377 | -121.582 | 0.11444 | 0.080646 | -0.049678 | 0.038365 | -0.061645 | 0.045421 | 0.039799 | -0.11308 | -0.043661 | 0.056323 | -0.022532 | 0.026427 | 121.6445 | 121.6167 | 121.0511 | 121.3093 | 0.094379 | -0.035945 | 0.052098 | -0.047912 | 0.059154 | 0.053532 | -0.099344 | -0.029928 | 0.070056 | -0.008799 | 0.04016 | 121.6582 | 121.6304 | 121.0649 | 121.323 | -121.6882 | -121.0948 | -121.667 | -121.0737
724.1719 | 121.7789 | -121.55 | 0.11902 | 0.080646 | -0.035942 | 0.033786 | -0.057066 | 0.040843 | 0.048956 | -0.1085 | -0.052818 | 0.065481 | -0.022532 | 0.031006 | 121.6445 | 121.6167 | 121.0466 | 121.3093 | 0.094379 | -0.022209 | 0.047519 | -0.043333 | 0.054576 | 0.062689 | -0.094766 | -0.039085 | 0.079214 | -0.008799 | 0.044739 | 121.6582 | 121.6304 | 121.0603 | 121.323 | -121.6973 | -121.0994 | -121.667 | -121.0691
725.9062 | 121.8155 | -121.5225 | 0.10071 | 0.076067 | -0.0451 | 0.038365 | -0.057066 | 0.049999 | 0.039799 | -0.11765 | -0.052818 | 0.060902 | -0.013376 | 0.035585 | 121.6399 | 121.6212 | 121.0466 | 121.3001 | 0.0898 | -0.031367 | 0.052098 | -0.043333 | 0.063732 | 0.053532 | -0.10392 | -0.039085 | 0.074635 | 0.000357 | 0.049318 | 121.6537 | 121.635 | 121.0603 | 121.3138 | -121.6928 | -121.0994 | -121.6533 | -121.0599
727.6406 | 121.7422 | -121.5729 | 0.10529 | 0.085224 | -0.040521 | 0.038365 | -0.061645 | 0.045421 | 0.044377 | -0.1085 | -0.052818 | 0.056323 | -0.022532 | 0.031006 | 121.6445 | 121.6075 | 121.0328 | 121.3138 | 0.098957 | -0.026788 | 0.052098 | -0.047912 | 0.059154 | 0.05811 | -0.094766 | -0.039085 | 0.070056 | -0.008799 | 0.044739 | 121.6582 | 121.6212 | 121.0466 | 121.3276 | -121.6973 | -121.0856 | -121.667 | -121.0554
729.3125 | 121.8063 | -121.5317 | 0.11902 | 0.080646 | -0.035942 | 0.029208 | -0.057066 | 0.045421 | 0.035221 | -0.1085 | -0.020768 | 0.079217 | 0.000359 | 0.053901 | 121.5713 | 121.58 | 121.0603 | 121.2681 | 0.094379 | -0.022209 | 0.042941 | -0.043333 | 0.059154 | 0.048954 | -0.094766 | -0.007035 | 0.09295 | 0.014092 | 0.067634 | 121.585 | 121.5938 | 121.074 | 121.2818 | -121.592 | -121.0811 | -121.5709 | -121.0599
731 | 121.8704 | -121.5179 | 0.091553 | 0.080646 | -0.040521 | 0.038365 | -0.061645 | 0.040843 | 0.035221 | -0.11308 | -0.025347 | 0.088375 | 0.009515 | 0.053901 | 121.6125 | 121.5846 | 121.0054 | 121.2635 | 0.094379 | -0.026788 | 0.052098 | -0.047912 | 0.054576 | 0.048954 | -0.099344 | -0.011614 | 0.10211 | 0.023248 | 0.067634 | 121.6262 | 121.5983 | 121.0191 | 121.2772 | -121.6378 | -121.0307 | -121.603 | -120.9958
732.7344 | 121.8018 | -121.5363 | 0.14191 | 0.085224 | -0.040521 | 0.038365 | -0.057066 | 0.040843 | 0.048956 | -0.1085 | -0.025347 | 0.083796 | 0.009515 | 0.05848 | 121.6033 | 121.5754 | 121.0008 | 121.2726 | 0.098957 | -0.026788 | 0.052098 | -0.043333 | 0.054576 | 0.062689 | -0.094766 | -0.011614 | 0.097529 | 0.023248 | 0.072213 | 121.617 | 121.5892 | 121.0145 | 121.2864 | -121.6287 | -121.0261 | -121.5938 | -120.9913
734.4688 | 121.7834 | -121.5317 | 0.13275 | 0.085224 | -0.035942 | 0.033786 | -0.057066 | 0.045421 | 0.035221 | -0.1085 | -0.01619 | 0.079217 | 0.004937 | 0.063059 | 121.6033 | 121.5754 | 121.0008 | 121.2589 | 0.098957 | -0.022209 | 0.047519 | -0.043333 | 0.059154 | 0.048954 | -0.094766 | -0.002457 | 0.09295 | 0.01867 | 0.076792 | 121.617 | 121.5892 | 121.0145 | 121.2726 | -121.6195 | -121.017 | -121.5984 | -120.9958
736.1406 | 121.7468 | -121.5454 | 0.13733 | 0.085224 | -0.035942 | 0.029208 | -0.052488 | 0.040843 | 0.039799 | -0.12223 | -0.025347 | 0.079217 | 0.004937 | 0.053901 | 121.6079 | 121.5754 | 120.9916 | 121.2726 | 0.098957 | -0.022209 | 0.042941 | -0.038755 | 0.054576 | 0.053532 | -0.1085 | -0.011614 | 0.09295 | 0.01867 | 0.067634 | 121.6216 | 121.5892 | 121.0054 | 121.2864 | -121.6332 | -121.017 | -121.603 | -120.9867
737.875 | 121.7743 | -121.5271 | 0.14191 | 0.080646 | -0.049678 | 0.033786 | -0.057066 | 0.040843 | 0.039799 | -0.11308 | -0.034504 | 0.079217 | 0.004937 | 0.053901 | 121.6033 | 121.5754 | 121.0008 | 121.2406 | 0.094379 | -0.035945 | 0.047519 | -0.043333 | 0.054576 | 0.053532 | -0.099344 | -0.020771 | 0.09295 | 0.01867 | 0.067634 | 121.617 | 121.5892 | 121.0145 | 121.2543 | -121.6378 | -121.0353 | -121.5984 | -120.9958
739.5625 | 121.7834 | -121.5225 | 0.11902 | 0.080646 | -0.0451 | 0.024629 | -0.057066 | 0.045421 | 0.044377 | -0.11308 | -0.029925 | 0.083796 | 0.014094 | 0.063059 | 121.6033 | 121.5709 | 120.9962 | 121.236 | 0.094379 | -0.031367 | 0.038362 | -0.043333 | 0.059154 | 0.05811 | -0.099344 | -0.016192 | 0.097529 | 0.027827 | 0.076792 | 121.617 | 121.5846 | 121.0099 | 121.2497 | -121.6332 | -121.0261 | -121.5892 | -120.9821
741.2969 | 121.8842 | -121.4996 | 0.10986 | 0.076067 | -0.035942 | 0.024629 | -0.066223 | 0.045421 | 0.039799 | -0.11308 | -0.025347 | 0.083796 | 0.000359 | 0.063059 | 121.5987 | 121.5709 | 120.9962 | 121.236 | 0.0898 | -0.022209 | 0.038362 | -0.05249 | 0.059154 | 0.053532 | -0.099344 | -0.011614 | 0.097529 | 0.014092 | 0.076792 | 121.6125 | 121.5846 | 121.0099 | 121.2497 | -121.6241 | -121.0215 | -121.5984 | -120.9958
743.0312 | 121.7514 | -121.5408 | 0.11902 | 0.076067 | -0.040521 | 0.029208 | -0.052488 | 0.045421 | 0.035221 | -0.11308 | -0.01619 | 0.092954 | 0.000359 | 0.05848 | 121.5987 | 121.5663 | 120.9779 | 121.2314 | 0.0898 | -0.026788 | 0.042941 | -0.038755 | 0.059154 | 0.048954 | -0.099344 | -0.002457 | 0.10669 | 0.014092 | 0.072213 | 121.6125 | 121.58 | 120.9916 | 121.2452 | -121.6149 | -120.9941 | -121.5984 | -120.9775
744.7812 | 121.7697 | -121.5134 | 0.14191 | 0.080646 | -0.040521 | 0.029208 | -0.057066 | 0.049999 | 0.039799 | -0.11765 | -0.011611 | 0.097532 | 0.014094 | 0.067638 | 121.4385 | 121.548 | 121.0557 | 121.2497 | 0.094379 | -0.026788 | 0.042941 | -0.043333 | 0.063732 | 0.053532 | -0.10392 | 0.002122 | 0.11126 | 0.027827 | 0.081371 | 121.4522 | 121.5617 | 121.0695 | 121.2635 | -121.4501 | -121.0673 | -121.4244 | -121.0416
746.5312 | 121.7102 | -121.4813 | 0.17853 | 0.085224 | -0.0451 | 0.033786 | -0.057066 | 0.054577 | 0.039799 | -0.11765 | -0.007033 | 0.10211 | 0.018672 | 0.072217 | 121.4019 | 121.5571 | 120.9779 | 121.2223 | 0.098957 | -0.031367 | 0.047519 | -0.043333 | 0.06831 | 0.053532 | -0.10392 | 0.0067 | 0.11584 | 0.032405 | 0.08595 | 121.4156 | 121.5709 | 120.9916 | 121.236 | -121.4089 | -120.9849 | -121.3832 | -120.9592
748.2031 | 121.7377 | -121.4859 | 0.1236 | 0.071489 | -0.040521 | 0.029208 | -0.057066 | 0.045421 | 0.039799 | -0.11765 | -0.034504 | 0.074638 | -0.008798 | 0.040164 | 121.6033 | 121.58 | 120.9916 | 121.4329 | 0.085222 | -0.026788 | 0.042941 | -0.043333 | 0.059154 | 0.053532 | -0.10392 | -0.020771 | 0.088371 | 0.004935 | 0.053897 | 121.617 | 121.5938 | 121.0054 | 121.4466 | -121.6378 | -121.0261 | -121.6121 | -121.0004
749.9375 | 121.7743 | -121.4859 | 0.10529 | 0.076067 | -0.040521 | 0.033786 | -0.061645 | 0.049999 | 0.039799 | -0.12223 | -0.011611 | 0.092954 | 0.009515 | 0.067638 | 121.5804 | 121.548 | 121.1152 | 121.3962 | 0.0898 | -0.026788 | 0.047519 | -0.047912 | 0.063732 | 0.053532 | -0.1085 | 0.002122 | 0.10669 | 0.023248 | 0.081371 | 121.5942 | 121.5617 | 121.129 | 121.41 | -121.592 | -121.1268 | -121.5709 | -121.1057
751.9062 | 121.6919 | -120.5933 | 0.92468 | 0.080646 | -0.040521 | 0.029208 | -0.057066 | 0.049999 | 0.044377 | -0.11308 | 0.73468 | 0.84388 | 0.73288 | 0.81402 | 120.7014 | 120.701 | 120.3049 | 120.5539 | 0.094379 | -0.026788 | 0.042941 | -0.043333 | 0.063732 | 0.05811 | -0.099344 | 0.74842 | 0.85761 | 0.74662 | 0.82775 | 120.7151 | 120.7148 | 120.3186 | 120.5676 | -119.9667 | -119.5702 | -119.9685 | -119.572
755.4531 | 121.463 | -119.7418 | 1.4648 | 0.071489 | -0.040521 | 0.033786 | -0.066223 | 0.045421 | 0.039799 | -0.11308 | 1.3299 | 1.4437 | 1.3281 | 1.423 | 119.6484 | 119.8037 | 119.2198 | 119.4734 | 0.085222 | -0.026788 | 0.047519 | -0.05249 | 0.059154 | 0.053532 | -0.099344 | 1.3436 | 1.4574 | 1.3418 | 1.4368 | 119.6622 | 119.8175 | 119.2335 | 119.4871 | -118.3185 | -117.8899 | -118.3204 | -117.8917
759.0781 | 121.2982 | -119.7052 | 1.4557 | 0.085224 | -0.026784 | 0.038365 | -0.047909 | 0.059155 | 0.048956 | -0.11308 | 1.3253 | 1.4254 | 1.3601 | 1.391 | 119.7949 | 119.758 | 119.4716 | 119.6199 | 0.098957 | -0.013051 | 0.052098 | -0.034176 | 0.072888 | 0.062689 | -0.099344 | 1.339 | 1.4391 | 1.3738 | 1.4047 | 119.8087 | 119.7717 | 119.4853 | 119.6336 | -118.4696 | -118.1463 | -118.4348 | -118.1115
764.7344 | 121.7377 | -1.3138 | 120.1126 | 0.089802 | -0.022205 | 0.042944 | -0.043331 | 0.063733 | 0.076426 | -0.099343 | 119.9862 | 120.0305 | 120.1161 | 120.0749 | 1.3072 | 1.2913 | -0.038063 | 1.2833 | 0.10354 | -0.008472 | 0.056677 | -0.029598 | 0.077466 | 0.090159 | -0.08561 | 119.9999 | 120.0442 | 120.1299 | 120.0886 | 1.321 | 1.3051 | -0.02433 | 1.297 | 118.6789 | 120.0242 | 118.8089 | 120.1542
766.4844 | 121.6965 | -0.5127 | 120.8679 | 0.080646 | -0.022205 | 0.038365 | -0.047909 | 0.06831 | 0.067269 | -0.10392 | 120.4898 | 120.5616 | 120.6197 | 120.5832 | 0.90435 | 0.90679 | 0.83641 | 0.90789 | 0.094379 | -0.008472 | 0.052098 | -0.034176 | 0.082043 | 0.081002 | -0.090188 | 120.5035 | 120.5754 | 120.6335 | 120.5969 | 0.91809 | 0.92052 | 0.85014 | 0.92162 | 119.5855 | 119.6534 | 119.7154 | 119.7833
768.1719 | 121.6232 | -0.22888 | 119.4626 | 0.080646 | -0.013048 | 0.042944 | -0.043331 | 0.06831 | 0.048956 | -0.1085 | 120.9522 | 120.992 | 121.0364 | 121.0411 | 0.33666 | 0.31164 | 0.2458 | 0.32188 | 0.094379 | 0.000685 | 0.056677 | -0.029598 | 0.082043 | 0.062689 | -0.094766 | 120.966 | 121.0058 | 121.0501 | 121.0548 | 0.35039 | 0.32537 | 0.25953 | 0.33561 | 120.6156 | 120.7064 | 120.6997 | 120.7906
769.9062 | 121.7468 | -0.59052 | 120.5795 | 0.085224 | -0.017627 | 0.038365 | -0.057066 | 0.06831 | 0.048956 | -0.1085 | 121.0392 | 121.0699 | 121.105 | 121.1235 | 0.2863 | 0.26128 | 0.20001 | 0.26236 | 0.098957 | -0.003894 | 0.052098 | -0.043333 | 0.082043 | 0.062689 | -0.094766 | 121.053 | 121.0836 | 121.1188 | 121.1372 | 0.30003 | 0.27501 | 0.21375 | 0.27609 | 120.7529 | 120.8392 | 120.8187 | 120.905
771.6406 | 121.6324 | -0.29755 | 120.7169 | 0.089802 | -0.022205 | 0.033786 | -0.052488 | 0.072888 | 0.044377 | -0.1085 | 120.9797 | 121.0195 | 121.0959 | 121.064 | 0.26799 | 0.25212 | 0.18628 | 0.25321 | 0.10354 | -0.008472 | 0.047519 | -0.038755 | 0.086621 | 0.05811 | -0.094766 | 120.9934 | 121.0332 | 121.1096 | 121.0777 | 0.28172 | 0.26586 | 0.20001 | 0.26694 | 120.7117 | 120.7934 | 120.8279 | 120.9096
773.375 | 121.7743 | -0.1831 | 121.3028 | 0.076067 | -0.022205 | 0.038365 | -0.052488 | 0.077466 | 0.048956 | -0.099343 | 121.1216 | 121.1477 | 121.1874 | 121.1372 | 0.19474 | 0.17887 | 0.11302 | 0.17996 | 0.0898 | -0.008472 | 0.052098 | -0.038755 | 0.091199 | 0.062689 | -0.08561 | 121.1354 | 121.1615 | 121.2012 | 121.151 | 0.20847 | 0.19261 | 0.12676 | 0.19369 | 120.9269 | 121.0086 | 120.9927 | 121.0744
775.0469 | 121.7102 | -0.18768 | 121.3531 | 0.085224 | -0.022205 | 0.042944 | -0.047909 | 0.06831 | 0.053534 | -0.1085 | 121.1491 | 121.1752 | 121.2149 | 121.1693 | 0.18558 | 0.16514 | 0.10845 | 0.16622 | 0.098957 | -0.008472 | 0.056677 | -0.034176 | 0.082043 | 0.067267 | -0.094766 | 121.1628 | 121.1889 | 121.2286 | 121.183 | 0.19931 | 0.17887 | 0.12218 | 0.17995 | 120.9635 | 121.0407 | 121.0293 | 121.1065
776.7969 | 121.7331 | -0.1831 | 121.2891 | 0.089802 | -0.022205 | 0.042944 | -0.052488 | 0.059155 | 0.048956 | -0.099343 | 120.3753 | 120.3785 | 120.4366 | 120.3954 | 0.89062 | 0.87932 | 0.8181 | 0.88957 | 0.10354 | -0.008472 | 0.056677 | -0.038755 | 0.072888 | 0.062689 | -0.08561 | 120.3891 | 120.3922 | 120.4503 | 120.4092 | 0.90435 | 0.89305 | 0.83183 | 0.90331 | 119.4847 | 119.5572 | 119.546 | 119.6185
778.4688 | 121.5317 | -121.0556 | 0.21515 | 0.076067 | -0.040521 | 0.024629 | -0.061645 | 0.045421 | 0.030642 | -0.11765 | 0.10743 | 0.20284 | 0.14686 | 0.16838 | 121.1363 | 121.1131 | 120.8131 | 120.9567 | 0.0898 | -0.026788 | 0.038362 | -0.047912 | 0.059154 | 0.044375 | -0.10392 | 0.12116 | 0.21658 | 0.1606 | 0.18211 | 121.1501 | 121.1268 | 120.8268 | 120.9705 | -121.0289 | -120.7056 | -120.9895 | -120.6662
780.1406 | 121.5591 | -121.1975 | 0.19226 | 0.080646 | -0.035942 | 0.029208 | -0.061645 | 0.049999 | 0.039799 | -0.11765 | 0.057066 | 0.15248 | 0.091925 | 0.13174 | 121.2645 | 121.2367 | 120.9458 | 121.0804 | 0.094379 | -0.022209 | 0.042941 | -0.047912 | 0.063732 | 0.053532 | -0.10392 | 0.070799 | 0.16621 | 0.10566 | 0.14548 | 121.2783 | 121.2504 | 120.9596 | 121.0941 | -121.2075 | -120.8888 | -121.1726 | -120.8539
781.8906 | 121.701 | -121.2662 | 0.10986 | 0.080646 | -0.049678 | 0.024629 | -0.070802 | 0.045421 | 0.039799 | -0.12223 | 0.011281 | 0.11127 | 0.055298 | 0.085954 | 121.3378 | 121.3099 | 121.0191 | 121.1628 | 0.094379 | -0.035945 | 0.038362 | -0.057069 | 0.059154 | 0.053532 | -0.1085 | 0.025014 | 0.125 | 0.069031 | 0.099687 | 121.3515 | 121.3237 | 121.0328 | 121.1765 | -121.3265 | -121.0078 | -121.2825 | -120.9638
783.6406 | 121.7239 | -121.3394 | 0.086975 | 0.080646 | -0.035942 | 0.024629 | -0.07538 | 0.040843 | 0.039799 | -0.11765 | -0.007033 | 0.10211 | 0.018672 | 0.05848 | 121.3881 | 121.3603 | 121.0695 | 121.2085 | 0.094379 | -0.022209 | 0.038362 | -0.061647 | 0.054576 | 0.053532 | -0.10392 | 0.0067 | 0.11584 | 0.032405 | 0.072213 | 121.4019 | 121.374 | 121.0832 | 121.2223 | -121.3952 | -121.0765 | -121.3695 | -121.0508
785.375 | 121.5958 | -121.3989 | 0.11902 | 0.080646 | -0.040521 | 0.029208 | -0.061645 | 0.045421 | 0.048956 | -0.1085 | -0.034504 | 0.079217 | -0.004219 | 0.035585 | 121.4293 | 121.3969 | 121.1107 | 121.2452 | 0.094379 | -0.026788 | 0.042941 | -0.047912 | 0.059154 | 0.062689 | -0.094766 | -0.020771 | 0.09295 | 0.009514 | 0.049318 | 121.4431 | 121.4106 | 121.1244 | 121.2589 | -121.4638 | -121.1452 | -121.4336 | -121.1149
787.0469 | 121.6782 | -121.3989 | 0.10071 | 0.076067 | -0.0451 | 0.033786 | -0.061645 | 0.036265 | 0.044377 | -0.11765 | -0.034504 | 0.07006 | -0.008798 | 0.035585 | 121.4431 | 121.4152 | 121.1381 | 121.2726 | 0.0898 | -0.031367 | 0.047519 | -0.047912 | 0.049998 | 0.05811 | -0.10392 | -0.020771 | 0.083793 | 0.004935 | 0.049318 | 121.4568 | 121.4289 | 121.1519 | 121.2864 | -121.4776 | -121.1726 | -121.4519 | -121.1469
788.7812 | 121.6415 | -121.4264 | 0.10986 | 0.071489 | -0.040521 | 0.024629 | -0.066223 | 0.040843 | 0.035221 | -0.11765 | -0.039082 | 0.060902 | 0.000359 | 0.040164 | 121.4614 | 121.4335 | 121.1473 | 121.2772 | 0.085222 | -0.026788 | 0.038362 | -0.05249 | 0.054576 | 0.048954 | -0.10392 | -0.025349 | 0.074635 | 0.014092 | 0.053897 | 121.4751 | 121.4473 | 121.161 | 121.2909 | -121.5005 | -121.1864 | -121.461 | -121.1469
790.5312 | 121.7514 | -121.3669 | 0.086975 | 0.076067 | -0.035942 | 0.033786 | -0.057066 | 0.040843 | 0.039799 | -0.11765 | -0.039082 | 0.074638 | -0.013376 | 0.035585 | 121.4705 | 121.4473 | 121.1564 | 121.2955 | 0.0898 | -0.022209 | 0.047519 | -0.043333 | 0.054576 | 0.053532 | -0.10392 | -0.025349 | 0.088371 | 0.000357 | 0.049318 | 121.4843 | 121.461 | 121.1702 | 121.3093 | -121.5096 | -121.1955 | -121.4839 | -121.1698
792.2031 | 121.6187 | -121.4493 | 0.12817 | 0.080646 | -0.049678 | 0.024629 | -0.057066 | 0.045421 | 0.035221 | -0.1085 | -0.039082 | 0.07006 | -0.008798 | 0.035585 | 121.4797 | 121.4564 | 121.1656 | 121.3047 | 0.094379 | -0.035945 | 0.038362 | -0.043333 | 0.059154 | 0.048954 | -0.094766 | -0.025349 | 0.083793 | 0.004935 | 0.049318 | 121.4934 | 121.4702 | 121.1793 | 121.3184 | -121.5188 | -121.2047 | -121.4885 | -121.1744
793.9375 | 121.701 | -121.4081 | 0.091553 | 0.080646 | -0.040521 | 0.024629 | -0.070802 | 0.040843 | 0.039799 | -0.11765 | -0.048239 | 0.065481 | -0.008798 | 0.031006 | 121.4889 | 121.4518 | 120.8817 | 121.3093 | 0.094379 | -0.026788 | 0.038362 | -0.057069 | 0.054576 | 0.053532 | -0.10392 | -0.034506 | 0.079214 | 0.004935 | 0.044739 | 121.5026 | 121.4656 | 120.8955 | 121.323 | -121.5371 | -120.93 | -121.4977 | -120.8905
795.6719 | 121.669 | -121.4584 | 0.10986 | 0.080646 | -0.040521 | 0.024629 | -0.061645 | 0.040843 | 0.044377 | -0.11308 | -0.043661 | 0.07006 | -0.013376 | 0.031006 | 121.498 | 121.4702 | 120.8955 | 121.3184 | 0.094379 | -0.026788 | 0.038362 | -0.047912 | 0.054576 | 0.05811 | -0.099344 | -0.029928 | 0.083793 | 0.000357 | 0.044739 | 121.5117 | 121.4839 | 120.9092 | 121.3322 | -121.5417 | -120.9391 | -121.5114 | -120.9088
797.3438 | 121.7148 | -121.4218 | 0.086975 | 0.080646 | -0.035942 | 0.024629 | -0.061645 | 0.040843 | 0.039799 | -0.11765 | -0.043661 | 0.07006 | -0.013376 | 0.031006 | 121.5026 | 121.4656 | 120.8909 | 121.3184 | 0.094379 | -0.022209 | 0.038362 | -0.047912 | 0.054576 | 0.053532 | -0.10392 | -0.029928 | 0.083793 | 0.000357 | 0.044739 | 121.5163 | 121.4793 | 120.9046 | 121.3322 | -121.5463 | -120.9346 | -121.516 | -120.9043
799.0781 | 121.6141 | -121.463 | 0.11902 | 0.076067 | -0.040521 | 0.029208 | -0.057066 | 0.040843 | 0.039799 | -0.11308 | -0.048239 | 0.07006 | -0.013376 | 0.035585 | 121.5026 | 121.4747 | 120.8909 | 121.3367 | 0.0898 | -0.026788 | 0.042941 | -0.043333 | 0.054576 | 0.053532 | -0.099344 | -0.034506 | 0.083793 | 0.000357 | 0.049318 | 121.5163 | 121.4885 | 120.9046 | 121.3505 | -121.5508 | -120.9391 | -121.516 | -120.9043
800.8281 | 121.669 | -121.4447 | 0.11444 | 0.076067 | -0.035942 | 0.029208 | -0.070802 | 0.040843 | 0.039799 | -0.11308 | -0.034504 | 0.065481 | -0.017954 | 0.031006 | 121.5117 | 121.4839 | 120.9046 | 121.3322 | 0.0898 | -0.022209 | 0.042941 | -0.057069 | 0.054576 | 0.053532 | -0.099344 | -0.020771 | 0.079214 | -0.004221 | 0.044739 | 121.5255 | 121.4976 | 120.9184 | 121.3459 | -121.5463 | -120.9391 | -121.5297 | -120.9226
802.5 | 121.6141 | -121.463 | 0.10986 | 0.080646 | -0.040521 | 0.024629 | -0.061645 | 0.045421 | 0.044377 | -0.11308 | -0.043661 | 0.065481 | -0.013376 | 0.035585 | 121.5209 | 121.4793 | 120.9046 | 121.3367 | 0.094379 | -0.026788 | 0.038362 | -0.047912 | 0.059154 | 0.05811 | -0.099344 | -0.029928 | 0.079214 | 0.000357 | 0.049318 | 121.5346 | 121.493 | 120.9184 | 121.3505 | -121.5646 | -120.9483 | -121.5343 | -120.918
804.2344 | 121.756 | -121.3989 | 0.086975 | 0.080646 | -0.035942 | 0.024629 | -0.057066 | 0.031687 | 0.039799 | -0.11765 | -0.034504 | 0.065481 | -0.013376 | 0.035585 | 121.5255 | 121.4839 | 120.9046 | 121.3459 | 0.094379 | -0.022209 | 0.038362 | -0.043333 | 0.04542 | 0.053532 | -0.10392 | -0.020771 | 0.079214 | 0.000357 | 0.049318 | 121.5392 | 121.4976 | 120.9184 | 121.3596 | -121.56 | -120.9391 | -121.5389 | -120.918
805.9688 | 121.6461 | -121.4767 | 0.11444 | 0.080646 | -0.040521 | 0.033786 | -0.061645 | 0.036265 | 0.035221 | -0.1085 | -0.043661 | 0.060902 | -0.017954 | 0.035585 | 121.5255 | 121.493 | 120.9138 | 121.3413 | 0.094379 | -0.026788 | 0.047519 | -0.047912 | 0.049998 | 0.048954 | -0.094766 | -0.029928 | 0.074635 | -0.004221 | 0.049318 | 121.5392 | 121.5068 | 120.9275 | 121.355 | -121.5691 | -120.9574 | -121.5434 | -120.9317
807.7031 | 121.7148 | -121.431 | 0.09613 | 0.076067 | -0.040521 | 0.029208 | -0.066223 | 0.040843 | 0.035221 | -0.11765 | -0.043661 | 0.07006 | -0.027111 | 0.026427 | 121.5346 | 121.493 | 120.9184 | 121.3505 | 0.0898 | -0.026788 | 0.042941 | -0.05249 | 0.054576 | 0.048954 | -0.10392 | -0.029928 | 0.083793 | -0.013378 | 0.04016 | 121.5484 | 121.5068 | 120.9321 | 121.3642 | -121.5783 | -120.962 | -121.5618 | -120.9455
809.4375 | 121.7239 | -121.4355 | 0.086975 | 0.085224 | -0.035942 | 0.029208 | -0.061645 | 0.045421 | 0.039799 | -0.12223 | -0.039082 | 0.065481 | -0.013376 | 0.026427 | 121.5346 | 121.4976 | 120.9184 | 121.3459 | 0.098957 | -0.022209 | 0.042941 | -0.047912 | 0.059154 | 0.053532 | -0.1085 | -0.025349 | 0.079214 | 0.000357 | 0.04016 | 121.5484 | 121.5114 | 120.9321 | 121.3596 | -121.5737 | -120.9574 | -121.548 | -120.9317
811.1094 | 121.7148 | -121.4355 | 0.10071 | 0.071489 | -0.031363 | 0.024629 | -0.066223 | 0.045421 | 0.039799 | -0.12223 | -0.048239 | 0.065481 | -0.017954 | 0.026427 | 121.5438 | 121.4976 | 120.9229 | 121.355 | 0.085222 | -0.01763 | 0.038362 | -0.05249 | 0.059154 | 0.053532 | -0.1085 | -0.034506 | 0.079214 | -0.004221 | 0.04016 | 121.5575 | 121.5114 | 120.9367 | 121.3688 | -121.592 | -120.9712 | -121.5618 | -120.9409
812.8438 | 121.6507 | -121.4447 | 0.11902 | 0.071489 | -0.049678 | 0.029208 | -0.070802 | 0.040843 | 0.039799 | -0.11765 | -0.043661 | 0.065481 | -0.017954 | 0.031006 | 121.5346 | 121.5022 | 120.9367 | 121.3642 | 0.085222 | -0.035945 | 0.042941 | -0.057069 | 0.054576 | 0.053532 | -0.10392 | -0.029928 | 0.079214 | -0.004221 | 0.044739 | 121.5484 | 121.5159 | 120.9504 | 121.3779 | -121.5783 | -120.9803 | -121.5526 | -120.9546
814.5156 | 121.7789 | -121.4218 | 0.091553 | 0.080646 | -0.0451 | 0.029208 | -0.066223 | 0.040843 | 0.035221 | -0.11765 | -0.048239 | 0.056323 | -0.022532 | 0.035585 | 121.5484 | 121.5068 | 120.9275 | 121.3642 | 0.094379 | -0.031367 | 0.042941 | -0.05249 | 0.054576 | 0.048954 | -0.10392 | -0.034506 | 0.070056 | -0.008799 | 0.049318 | 121.5621 | 121.5205 | 120.9413 | 121.3779 | -121.5966 | -120.9758 | -121.5709 | -120.9501
816.25 | 121.6553 | -121.4996 | 0.09613 | 0.076067 | -0.035942 | 0.029208 | -0.061645 | 0.036265 | 0.039799 | -0.11765 | -0.043661 | 0.060902 | -0.027111 | 0.026427 | 121.5392 | 121.5159 | 120.9321 | 121.3688 | 0.0898 | -0.022209 | 0.042941 | -0.047912 | 0.049998 | 0.053532 | -0.10392 | -0.029928 | 0.074635 | -0.013378 | 0.04016 | 121.553 | 121.5297 | 120.9458 | 121.3825 | -121.5829 | -120.9758 | -121.5663 | -120.9592
817.9844 | 121.7239 | -121.4447 | 0.086975 | 0.071489 | -0.040521 | 0.029208 | -0.061645 | 0.040843 | 0.035221 | -0.12223 | -0.043661 | 0.056323 | -0.008798 | 0.035585 | 121.5484 | 121.5114 | 120.9367 | 121.3642 | 0.085222 | -0.026788 | 0.042941 | -0.047912 | 0.054576 | 0.048954 | -0.1085 | -0.029928 | 0.070056 | 0.004935 | 0.049318 | 121.5621 | 121.5251 | 120.9504 | 121.3779 | -121.592 | -120.9803 | -121.5572 | -120.9455
819.7188 | 121.756 | -121.4447 | 0.07782 | 0.071489 | -0.0451 | 0.029208 | -0.057066 | 0.045421 | 0.035221 | -0.11765 | -0.052818 | 0.065481 | -0.017954 | 0.040164 | 121.5484 | 121.5205 | 120.9321 | 121.3734 | 0.085222 | -0.031367 | 0.042941 | -0.043333 | 0.059154 | 0.048954 | -0.10392 | -0.039085 | 0.079214 | -0.004221 | 0.053897 | 121.5621 | 121.5342 | 120.9458 | 121.3871 | -121.6012 | -120.9849 | -121.5663 | -120.9501
821.3906 | 121.7743 | -121.4539 | 0.09613 | 0.076067 | -0.040521 | 0.029208 | -0.066223 | 0.036265 | 0.030642 | -0.12223 | -0.048239 | 0.060902 | -0.017954 | 0.035585 | 121.5575 | 121.5159 | 120.9413 | 121.3779 | 0.0898 | -0.026788 | 0.042941 | -0.05249 | 0.049998 | 0.044375 | -0.1085 | -0.034506 | 0.074635 | -0.004221 | 0.049318 | 121.5713 | 121.5297 | 120.955 | 121.3917 | -121.6058 | -120.9895 | -121.5755 | -120.9592
823.125 | 121.788 | -121.4493 | 0.10986 | 0.071489 | -0.040521 | 0.033786 | -0.061645 | 0.040843 | 0.039799 | -0.11765 | -0.043661 | 0.060902 | -0.017954 | 0.026427 | 121.5575 | 121.5251 | 120.9504 | 121.3779 | 0.085222 | -0.026788 | 0.047519 | -0.047912 | 0.054576 | 0.053532 | -0.10392 | -0.029928 | 0.074635 | -0.004221 | 0.04016 | 121.5713 | 121.5388 | 120.9641 | 121.3917 | -121.6012 | -120.9941 | -121.5755 | -120.9684
824.7969 | 121.7377 | -121.4722 | 0.091553 | 0.076067 | -0.040521 | 0.029208 | -0.066223 | 0.045421 | 0.039799 | -0.12223 | -0.048239 | 0.060902 | -0.017954 | 0.031006 | 121.5621 | 121.5297 | 120.9367 | 121.3779 | 0.0898 | -0.026788 | 0.042941 | -0.05249 | 0.059154 | 0.053532 | -0.1085 | -0.034506 | 0.074635 | -0.004221 | 0.044739 | 121.5758 | 121.5434 | 120.9504 | 121.3917 | -121.6103 | -120.9849 | -121.5801 | -120.9546
826.5469 | 121.7789 | -121.4401 | 0.082397 | 0.076067 | -0.035942 | 0.029208 | -0.061645 | 0.036265 | 0.039799 | -0.12223 | -0.048239 | 0.065481 | -0.013376 | 0.026427 | 121.5667 | 121.5251 | 120.9504 | 121.3825 | 0.0898 | -0.022209 | 0.042941 | -0.047912 | 0.049998 | 0.053532 | -0.1085 | -0.034506 | 0.079214 | 0.000357 | 0.04016 | 121.5804 | 121.5388 | 120.9641 | 121.3962 | -121.6149 | -120.9987 | -121.5801 | -120.9638
828.2969 | 121.7422 | -121.431 | 0.086975 | 0.076067 | -0.035942 | 0.033786 | -0.057066 | 0.040843 | 0.030642 | -0.11765 | -0.043661 | 0.060902 | -0.013376 | 0.035585 | 121.5621 | 121.5251 | 120.9504 | 121.3871 | 0.0898 | -0.022209 | 0.047519 | -0.043333 | 0.054576 | 0.044375 | -0.10392 | -0.029928 | 0.074635 | 0.000357 | 0.049318 | 121.5758 | 121.5388 | 120.9641 | 121.4008 | -121.6058 | -120.9941 | -121.5755 | -120.9638
830.0312 | 121.6507 | -121.4813 | 0.13275 | 0.076067 | -0.040521 | 0.029208 | -0.061645 | 0.031687 | 0.035221 | -0.12223 | -0.052818 | 0.065481 | -0.013376 | 0.035585 | 121.5667 | 121.5205 | 120.955 | 121.3871 | 0.0898 | -0.026788 | 0.042941 | -0.047912 | 0.04542 | 0.048954 | -0.1085 | -0.039085 | 0.079214 | 0.000357 | 0.049318 | 121.5804 | 121.5342 | 120.9687 | 121.4008 | -121.6195 | -121.0078 | -121.5801 | -120.9684
831.7656 | 121.6599 | -121.4859 | 0.13733 | 0.071489 | -0.040521 | 0.033786 | -0.066223 | 0.040843 | 0.039799 | -0.11308 | -0.052818 | 0.065481 | -0.017954 | 0.021847 | 121.5713 | 121.5342 | 120.955 | 121.3962 | 0.085222 | -0.026788 | 0.047519 | -0.05249 | 0.054576 | 0.053532 | -0.099344 | -0.039085 | 0.079214 | -0.004221 | 0.03558 | 121.585 | 121.548 | 120.9687 | 121.41 | -121.6241 | -121.0078 | -121.5892 | -120.9729
833.5 | 121.669 | -121.4722 | 0.11444 | 0.085224 | -0.040521 | 0.024629 | -0.057066 | 0.036265 | 0.035221 | -0.11308 | -0.043661 | 0.065481 | -0.013376 | 0.026427 | 121.5758 | 121.5251 | 120.9504 | 121.3871 | 0.098957 | -0.026788 | 0.038362 | -0.043333 | 0.049998 | 0.048954 | -0.099344 | -0.029928 | 0.079214 | 0.000357 | 0.04016 | 121.5896 | 121.5388 | 120.9641 | 121.4008 | -121.6195 | -120.9941 | -121.5892 | -120.9638
835.2344 | 121.7056 | -121.4859 | 0.10986 | 0.080646 | -0.0451 | 0.029208 | -0.061645 | 0.036265 | 0.039799 | -0.11765 | -0.048239 | 0.065481 | -0.022532 | 0.031006 | 121.5713 | 121.5297 | 120.9596 | 121.3962 | 0.094379 | -0.031367 | 0.042941 | -0.047912 | 0.049998 | 0.053532 | -0.10392 | -0.034506 | 0.079214 | -0.008799 | 0.044739 | 121.585 | 121.5434 | 120.9733 | 121.41 | -121.6195 | -121.0078 | -121.5938 | -120.9821
836.9062 | 121.7834 | -121.4584 | 0.10529 | 0.080646 | -0.0451 | 0.024629 | -0.061645 | 0.031687 | 0.030642 | -0.11308 | -0.043661 | 0.060902 | -0.013376 | 0.026427 | 121.5758 | 121.5342 | 120.9642 | 121.3962 | 0.094379 | -0.031367 | 0.038362 | -0.047912 | 0.04542 | 0.044375 | -0.099344 | -0.029928 | 0.074635 | 0.000357 | 0.04016 | 121.5896 | 121.548 | 120.9779 | 121.41 | -121.6195 | -121.0078 | -121.5892 | -120.9775
838.6562 | 121.7972 | -121.4493 | 0.082397 | 0.06691 | -0.035942 | 0.029208 | -0.070802 | 0.036265 | 0.035221 | -0.11765 | -0.048239 | 0.060902 | -0.013376 | 0.031006 | 121.5758 | 121.5434 | 120.9687 | 121.3962 | 0.080643 | -0.022209 | 0.042941 | -0.057069 | 0.049998 | 0.048954 | -0.10392 | -0.034506 | 0.074635 | 0.000357 | 0.044739 | 121.5896 | 121.5571 | 120.9825 | 121.41 | -121.6241 | -121.017 | -121.5892 | -120.9821
840.3906 | 121.6599 | -121.4996 | 0.1236 | 0.080646 | -0.040521 | 0.024629 | -0.057066 | 0.049999 | 0.035221 | -0.11765 | -0.043661 | 0.051744 | -0.017954 | 0.026427 | 121.5804 | 121.5388 | 120.9596 | 121.3962 | 0.094379 | -0.026788 | 0.038362 | -0.043333 | 0.063732 | 0.048954 | -0.10392 | -0.029928 | 0.065477 | -0.004221 | 0.04016 | 121.5942 | 121.5526 | 120.9733 | 121.41 | -121.6241 | -121.0032 | -121.5984 | -120.9775
842.125 | 121.6873 | -121.5042 | 0.13275 | 0.089802 | -0.031363 | 0.029208 | -0.057066 | 0.031687 | 0.044377 | -0.11765 | -0.048239 | 0.060902 | -0.017954 | 0.026427 | 121.5804 | 121.5388 | 120.9687 | 121.4008 | 0.10354 | -0.01763 | 0.042941 | -0.043333 | 0.04542 | 0.05811 | -0.10392 | -0.034506 | 0.074635 | -0.004221 | 0.04016 | 121.5942 | 121.5526 | 120.9825 | 121.4146 | -121.6287 | -121.017 | -121.5984 | -120.9867
843.8594 | 121.8018 | -121.4676 | 0.082397 | 0.076067 | -0.0451 | 0.024629 | -0.070802 | 0.036265 | 0.044377 | -0.1085 | -0.043661 | 0.060902 | -0.013376 | 0.035585 | 121.5804 | 121.5434 | 120.9642 | 121.4008 | 0.0898 | -0.031367 | 0.038362 | -0.057069 | 0.049998 | 0.05811 | -0.094766 | -0.029928 | 0.074635 | 0.000357 | 0.049318 | 121.5942 | 121.5571 | 120.9779 | 121.4146 | -121.6241 | -121.0078 | -121.5938 | -120.9775
845.6094 | 121.7239 | -121.4813 | 0.11444 | 0.076067 | -0.031363 | 0.020051 | -0.066223 | 0.040843 | 0.035221 | -0.11308 | -0.043661 | 0.07006 | -0.027111 | 0.035585 | 121.585 | 121.548 | 120.9642 | 121.41 | 0.0898 | -0.01763 | 0.033784 | -0.05249 | 0.054576 | 0.048954 | -0.099344 | -0.029928 | 0.083793 | -0.013378 | 0.049318 | 121.5987 | 121.5617 | 120.9779 | 121.4237 | -121.6287 | -121.0078 | -121.6121 | -120.9913
847.2812 | 121.7926 | -121.4539 | 0.068665 | 0.071489 | -0.040521 | 0.029208 | -0.070802 | 0.045421 | 0.044377 | -0.11308 | -0.057396 | 0.065481 | -0.022532 | 0.026427 | 121.585 | 121.5526 | 120.9642 | 121.4054 | 0.085222 | -0.026788 | 0.042941 | -0.057069 | 0.059154 | 0.05811 | -0.099344 | -0.043663 | 0.079214 | -0.008799 | 0.04016 | 121.5987 | 121.5663 | 120.9779 | 121.4191 | -121.6424 | -121.0215 | -121.6075 | -120.9867
849.0156 | 121.7194 | -121.4905 | 0.10529 | 0.071489 | -0.040521 | 0.020051 | -0.061645 | 0.040843 | 0.039799 | -0.11308 | -0.043661 | 0.060902 | -0.013376 | 0.021847 | 121.585 | 121.5434 | 120.9687 | 121.4146 | 0.085222 | -0.026788 | 0.033784 | -0.047912 | 0.054576 | 0.053532 | -0.099344 | -0.029928 | 0.074635 | 0.000357 | 0.03558 | 121.5987 | 121.5571 | 120.9825 | 121.4283 | -121.6287 | -121.0124 | -121.5984 | -120.9821
850.7656 | 121.788 | -121.463 | 0.091553 | 0.076067 | -0.035942 | 0.024629 | -0.061645 | 0.040843 | 0.035221 | -0.12223 | -0.043661 | 0.056323 | -0.013376 | 0.035585 | 121.5804 | 121.548 | 120.9687 | 121.41 | 0.0898 | -0.022209 | 0.038362 | -0.047912 | 0.054576 | 0.048954 | -0.1085 | -0.029928 | 0.070056 | 0.000357 | 0.049318 | 121.5942 | 121.5617 | 120.9825 | 121.4237 | -121.6241 | -121.0124 | -121.5938 | -120.9821
852.5 | 121.6644 | -121.5042 | 0.10986 | 0.080646 | -0.035942 | 0.024629 | -0.061645 | 0.045421 | 0.035221 | -0.11765 | -0.043661 | 0.056323 | -0.017954 | 0.026427 | 121.5896 | 121.5526 | 120.9642 | 121.41 | 0.094379 | -0.022209 | 0.038362 | -0.047912 | 0.059154 | 0.048954 | -0.10392 | -0.029928 | 0.070056 | -0.004221 | 0.04016 | 121.6033 | 121.5663 | 120.9779 | 121.4237 | -121.6332 | -121.0078 | -121.6075 | -120.9821
854.1719 | 121.7148 | -121.5363 | 0.10986 | 0.071489 | -0.040521 | 0.029208 | -0.070802 | 0.031687 | 0.039799 | -0.12223 | -0.048239 | 0.065481 | -0.013376 | 0.026427 | 121.5942 | 121.5617 | 120.9687 | 121.4191 | 0.085222 | -0.026788 | 0.042941 | -0.057069 | 0.04542 | 0.053532 | -0.1085 | -0.034506 | 0.079214 | 0.000357 | 0.04016 | 121.6079 | 121.5754 | 120.9825 | 121.4329 | -121.6424 | -121.017 | -121.6075 | -120.9821
855.9062 | 121.6827 | -121.5271 | 0.10986 | 0.071489 | -0.040521 | 0.029208 | -0.066223 | 0.040843 | 0.035221 | -0.11308 | -0.043661 | 0.056323 | -0.013376 | 0.031006 | 121.5987 | 121.5526 | 120.9779 | 121.41 | 0.085222 | -0.026788 | 0.042941 | -0.05249 | 0.054576 | 0.048954 | -0.099344 | -0.029928 | 0.070056 | 0.000357 | 0.044739 | 121.6125 | 121.5663 | 120.9916 | 121.4237 | -121.6424 | -121.0215 | -121.6121 | -120.9913
857.5781 | 121.8063 | -121.4859 | 0.09613 | 0.076067 | -0.040521 | 0.033786 | -0.061645 | 0.040843 | 0.035221 | -0.12223 | -0.043661 | 0.060902 | -0.022532 | 0.031006 | 121.5987 | 121.5571 | 120.987 | 121.4191 | 0.0898 | -0.026788 | 0.047519 | -0.047912 | 0.054576 | 0.048954 | -0.1085 | -0.029928 | 0.074635 | -0.008799 | 0.044739 | 121.6125 | 121.5709 | 121.0008 | 121.4329 | -121.6424 | -121.0307 | -121.6213 | -121.0096
859.3125 | 121.7422 | -121.5134 | 0.09613 | 0.076067 | -0.035942 | 0.024629 | -0.061645 | 0.040843 | 0.039799 | -0.12681 | -0.043661 | 0.051744 | -0.022532 | 0.031006 | 121.5942 | 121.5617 | 120.9779 | 121.4146 | 0.0898 | -0.022209 | 0.038362 | -0.047912 | 0.054576 | 0.053532 | -0.11308 | -0.029928 | 0.065477 | -0.008799 | 0.044739 | 121.6079 | 121.5754 | 120.9916 | 121.4283 | -121.6378 | -121.0215 | -121.6167 | -121.0004
861 | 121.7606 | -121.4996 | 0.10529 | 0.071489 | -0.0451 | 0.020051 | -0.057066 | 0.040843 | 0.035221 | -0.11765 | -0.043661 | 0.056323 | -0.017954 | 0.026427 | 121.5942 | 121.5571 | 120.9825 | 121.4191 | 0.085222 | -0.031367 | 0.033784 | -0.043333 | 0.054576 | 0.048954 | -0.10392 | -0.029928 | 0.070056 | -0.004221 | 0.04016 | 121.6079 | 121.5709 | 120.9962 | 121.4329 | -121.6378 | -121.0261 | -121.6121 | -121.0004
862.7344 | 121.8109 | -121.4813 | 0.082397 | 0.080646 | -0.031363 | 0.024629 | -0.061645 | 0.045421 | 0.035221 | -0.11308 | -0.043661 | 0.060902 | -0.022532 | 0.026427 | 121.5942 | 121.5663 | 120.987 | 121.2131 | 0.094379 | -0.01763 | 0.038362 | -0.047912 | 0.059154 | 0.048954 | -0.099344 | -0.029928 | 0.074635 | -0.008799 | 0.04016 | 121.6079 | 121.58 | 121.0008 | 121.2269 | -121.6378 | -121.0307 | -121.6167 | -121.0096
864.4062 | 121.6644 | -121.5363 | 0.12817 | 0.076067 | -0.0451 | 0.024629 | -0.052488 | 0.045421 | 0.030642 | -0.11308 | -0.043661 | 0.056323 | -0.022532 | 0.031006 | 121.5987 | 121.5663 | 120.987 | 121.2177 | 0.0898 | -0.031367 | 0.038362 | -0.038755 | 0.059154 | 0.044375 | -0.099344 | -0.029928 | 0.070056 | -0.008799 | 0.044739 | 121.6125 | 121.58 | 121.0008 | 121.2314 | -121.6424 | -121.0307 | -121.6213 | -121.0096
866.1562 | 121.6919 | -121.5363 | 0.10529 | 0.080646 | -0.040521 | 0.020051 | -0.057066 | 0.036265 | 0.039799 | -0.12223 | -0.048239 | 0.060902 | -0.022532 | 0.026427 | 121.5987 | 121.5709 | 120.987 | 121.2269 | 0.094379 | -0.026788 | 0.033784 | -0.043333 | 0.049998 | 0.053532 | -0.1085 | -0.034506 | 0.074635 | -0.008799 | 0.04016 | 121.6125 | 121.5846 | 121.0008 | 121.2406 | -121.647 | -121.0353 | -121.6213 | -121.0096
867.8906 | 121.8246 | -121.463 | 0.086975 | 0.076067 | -0.040521 | 0.024629 | -0.061645 | 0.036265 | 0.026064 | -0.11765 | -0.048239 | 0.056323 | -0.017954 | 0.026427 | 121.4202 | 121.58 | 120.9916 | 121.2223 | 0.0898 | -0.026788 | 0.038362 | -0.047912 | 0.049998 | 0.039797 | -0.10392 | -0.034506 | 0.070056 | -0.004221 | 0.04016 | 121.4339 | 121.5938 | 121.0054 | 121.236 | -121.4684 | -121.0399 | -121.4381 | -121.0096
869.5625 | 121.7789 | -121.5088 | 0.086975 | 0.076067 | -0.0451 | 0.024629 | -0.066223 | 0.036265 | 0.030642 | -0.12681 | -0.043661 | 0.051744 | -0.022532 | 0.035585 | 121.411 | 121.5754 | 120.9779 | 121.2269 | 0.0898 | -0.031367 | 0.038362 | -0.05249 | 0.049998 | 0.044375 | -0.11308 | -0.029928 | 0.065477 | -0.008799 | 0.049318 | 121.4248 | 121.5892 | 120.9916 | 121.2406 | -121.4547 | -121.0215 | -121.4336 | -121.0004
871.3125 | 121.8201 | -121.4859 | 0.073242 | 0.080646 | -0.040521 | 0.024629 | -0.057066 | 0.040843 | 0.035221 | -0.11765 | -0.043661 | 0.065481 | -0.022532 | 0.026427 | 121.411 | 121.5754 | 120.9916 | 121.2269 | 0.094379 | -0.026788 | 0.038362 | -0.043333 | 0.054576 | 0.048954 | -0.10392 | -0.029928 | 0.079214 | -0.008799 | 0.04016 | 121.4248 | 121.5892 | 121.0054 | 121.2406 | -121.4547 | -121.0353 | -121.4336 | -121.0142
873.0469 | 121.7422 | -121.5271 | 0.11444 | 0.076067 | -0.035942 | 0.024629 | -0.052488 | 0.036265 | 0.035221 | -0.11308 | -0.043661 | 0.051744 | -0.017954 | 0.031006 | 121.411 | 121.5754 | 120.9916 | 121.2314 | 0.0898 | -0.022209 | 0.038362 | -0.038755 | 0.049998 | 0.048954 | -0.099344 | -0.029928 | 0.065477 | -0.004221 | 0.044739 | 121.4248 | 121.5892 | 121.0054 | 121.2452 | -121.4547 | -121.0353 | -121.429 | -121.0096
874.7812 | 121.701 | -121.5408 | 0.10529 | 0.071489 | -0.035942 | 0.020051 | -0.052488 | 0.036265 | 0.035221 | -0.11765 | -0.043661 | 0.060902 | -0.017954 | 0.031006 | 121.4248 | 121.5754 | 120.9825 | 121.236 | 0.085222 | -0.022209 | 0.033784 | -0.038755 | 0.049998 | 0.048954 | -0.10392 | -0.029928 | 0.074635 | -0.004221 | 0.044739 | 121.4385 | 121.5892 | 120.9962 | 121.2497 | -121.4684 | -121.0261 | -121.4427 | -121.0004
876.4688 | 121.8475 | -121.5088 | 0.064087 | 0.076067 | -0.0451 | 0.020051 | -0.061645 | 0.031687 | 0.030642 | -0.12223 | -0.052818 | 0.060902 | -0.022532 | 0.026427 | 121.4248 | 121.58 | 120.9962 | 121.2269 | 0.0898 | -0.031367 | 0.033784 | -0.047912 | 0.04542 | 0.044375 | -0.1085 | -0.039085 | 0.074635 | -0.008799 | 0.04016 | 121.4385 | 121.5938 | 121.0099 | 121.2406 | -121.4776 | -121.049 | -121.4473 | -121.0187
878.1406 | 121.6965 | -121.5546 | 0.11444 | 0.06691 | -0.035942 | 0.020051 | -0.057066 | 0.027109 | 0.039799 | -0.12223 | -0.048239 | 0.056323 | -0.013376 | 0.026427 | 121.4248 | 121.5846 | 120.9962 | 121.2406 | 0.080643 | -0.022209 | 0.033784 | -0.043333 | 0.040842 | 0.053532 | -0.1085 | -0.034506 | 0.070056 | 0.000357 | 0.04016 | 121.4385 | 121.5983 | 121.0099 | 121.2543 | -121.473 | -121.0444 | -121.4381 | -121.0096
879.875 | 121.7422 | -121.5317 | 0.13275 | 0.076067 | -0.040521 | 0.024629 | -0.057066 | 0.036265 | 0.035221 | -0.12223 | -0.043661 | 0.060902 | -0.013376 | 0.035585 | 121.4248 | 121.58 | 121.0054 | 121.2406 | 0.0898 | -0.026788 | 0.038362 | -0.043333 | 0.049998 | 0.048954 | -0.1085 | -0.029928 | 0.074635 | 0.000357 | 0.049318 | 121.4385 | 121.5938 | 121.0191 | 121.2543 | -121.4684 | -121.049 | -121.4381 | -121.0187
881.5469 | 121.6782 | -121.5454 | 0.1236 | 0.080646 | -0.035942 | 0.015472 | -0.057066 | 0.045421 | 0.035221 | -0.11308 | -0.048239 | 0.060902 | -0.017954 | 0.026427 | 121.4202 | 121.5892 | 121.0008 | 121.2406 | 0.094379 | -0.022209 | 0.029205 | -0.043333 | 0.059154 | 0.048954 | -0.099344 | -0.034506 | 0.074635 | -0.004221 | 0.04016 | 121.4339 | 121.6029 | 121.0145 | 121.2543 | -121.4684 | -121.049 | -121.4381 | -121.0187
883.2812 | 121.7331 | -121.5271 | 0.11902 | 0.076067 | -0.040521 | 0.015472 | -0.061645 | 0.036265 | 0.035221 | -0.11765 | -0.043661 | 0.060902 | -0.013376 | 0.026427 | 121.4248 | 121.58 | 121.0099 | 121.236 | 0.0898 | -0.026788 | 0.029205 | -0.047912 | 0.049998 | 0.048954 | -0.10392 | -0.029928 | 0.074635 | 0.000357 | 0.04016 | 121.4385 | 121.5938 | 121.0237 | 121.2497 | -121.4684 | -121.0536 | -121.4381 | -121.0233
884.9531 | 121.701 | -121.5363 | 0.11444 | 0.076067 | -0.035942 | 0.024629 | -0.052488 | 0.036265 | 0.030642 | -0.11308 | -0.048239 | 0.051744 | -0.013376 | 0.031006 | 121.4248 | 121.5892 | 121.0099 | 121.2406 | 0.0898 | -0.022209 | 0.038362 | -0.038755 | 0.049998 | 0.044375 | -0.099344 | -0.034506 | 0.065477 | 0.000357 | 0.044739 | 121.4385 | 121.6029 | 121.0237 | 121.2543 | -121.473 | -121.0582 | -121.4381 | -121.0233
886.7031 | 121.8521 | -121.4859 | 0.068665 | 0.071489 | -0.040521 | 0.024629 | -0.057066 | 0.036265 | 0.021485 | -0.12223 | -0.039082 | 0.056323 | -0.022532 | 0.031006 | 121.4293 | 121.5892 | 121.0054 | 121.2452 | 0.085222 | -0.026788 | 0.038362 | -0.043333 | 0.049998 | 0.035218 | -0.1085 | -0.025349 | 0.070056 | -0.008799 | 0.044739 | 121.4431 | 121.6029 | 121.0191 | 121.2589 | -121.4684 | -121.0444 | -121.4519 | -121.0279
888.375 | 121.7377 | -121.5317 | 0.11444 | 0.080646 | -0.035942 | 0.024629 | -0.057066 | 0.040843 | 0.030642 | -0.11765 | -0.043661 | 0.051744 | -0.017954 | 0.026427 | 121.4248 | 121.5938 | 121.0099 | 121.2452 | 0.094379 | -0.022209 | 0.038362 | -0.043333 | 0.054576 | 0.044375 | -0.10392 | -0.029928 | 0.065477 | -0.004221 | 0.04016 | 121.4385 | 121.6075 | 121.0237 | 121.2589 | -121.4684 | -121.0536 | -121.4427 | -121.0279
890.0469 | 121.7285 | -121.5363 | 0.11902 | 0.06691 | -0.040521 | 0.020051 | -0.061645 | 0.031687 | 0.030642 | -0.11308 | -0.039082 | 0.065481 | -0.013376 | 0.031006 | 121.4339 | 121.5983 | 121.0099 | 121.2406 | 0.080643 | -0.026788 | 0.033784 | -0.047912 | 0.04542 | 0.044375 | -0.099344 | -0.025349 | 0.079214 | 0.000357 | 0.044739 | 121.4477 | 121.6121 | 121.0237 | 121.2543 | -121.473 | -121.049 | -121.4473 | -121.0233
891.7812 | 121.8338 | -121.4905 | 0.082397 | 0.080646 | -0.0451 | 0.029208 | -0.061645 | 0.027109 | 0.026064 | -0.11308 | -0.048239 | 0.056323 | -0.017954 | 0.031006 | 121.4293 | 121.5938 | 121.0099 | 121.2452 | 0.094379 | -0.031367 | 0.042941 | -0.047912 | 0.040842 | 0.039797 | -0.099344 | -0.034506 | 0.070056 | -0.004221 | 0.044739 | 121.4431 | 121.6075 | 121.0237 | 121.2589 | -121.4776 | -121.0582 | -121.4473 | -121.0279
893.4688 | 121.7377 | -121.5179 | 0.11902 | 0.076067 | -0.035942 | 0.020051 | -0.061645 | 0.040843 | 0.030642 | -0.11765 | -0.043661 | 0.060902 | -0.013376 | 0.026427 | 121.4293 | 121.6029 | 121.0054 | 121.2406 | 0.0898 | -0.022209 | 0.033784 | -0.047912 | 0.054576 | 0.044375 | -0.10392 | -0.029928 | 0.074635 | 0.000357 | 0.04016 | 121.4431 | 121.6166 | 121.0191 | 121.2543 | -121.473 | -121.049 | -121.4427 | -121.0187
895.2188 | 121.6873 | -121.5363 | 0.10529 | 0.080646 | -0.031363 | 0.020051 | -0.066223 | 0.040843 | 0.026064 | -0.11765 | -0.043661 | 0.060902 | -0.022532 | 0.026427 | 121.4339 | 121.5983 | 121.0099 | 121.2452 | 0.094379 | -0.01763 | 0.033784 | -0.05249 | 0.054576 | 0.039797 | -0.10392 | -0.029928 | 0.074635 | -0.008799 | 0.04016 | 121.4477 | 121.6121 | 121.0237 | 121.2589 | -121.4776 | -121.0536 | -121.4565 | -121.0325
896.9062 | 121.756 | -121.5408 | 0.086975 | 0.080646 | -0.0451 | 0.020051 | -0.066223 | 0.036265 | 0.030642 | -0.12223 | -0.057396 | 0.060902 | -0.017954 | 0.021847 | 121.4339 | 121.5938 | 121.0099 | 121.2406 | 0.094379 | -0.031367 | 0.033784 | -0.05249 | 0.049998 | 0.044375 | -0.1085 | -0.043663 | 0.074635 | -0.004221 | 0.03558 | 121.4477 | 121.6075 | 121.0237 | 121.2543 | -121.4913 | -121.0673 | -121.4519 | -121.0279
898.6562 | 121.7102 | -121.5134 | 0.10071 | 0.076067 | -0.0451 | 0.029208 | -0.061645 | 0.031687 | 0.039799 | -0.12223 | -0.052818 | 0.060902 | -0.017954 | 0.026427 | 121.4248 | 121.6075 | 121.0099 | 121.2497 | 0.0898 | -0.031367 | 0.042941 | -0.047912 | 0.04542 | 0.053532 | -0.1085 | -0.039085 | 0.074635 | -0.004221 | 0.04016 | 121.4385 | 121.6212 | 121.0237 | 121.2635 | -121.4776 | -121.0628 | -121.4427 | -121.0279
900.3438 | 121.7148 | -121.5317 | 0.11902 | 0.076067 | -0.035942 | 0.029208 | -0.061645 | 0.036265 | 0.035221 | -0.11308 | -0.057396 | 0.060902 | -0.017954 | 0.031006 | 121.4248 | 121.5938 | 121.0191 | 121.2543 | 0.0898 | -0.022209 | 0.042941 | -0.047912 | 0.049998 | 0.048954 | -0.099344 | -0.043663 | 0.074635 | -0.004221 | 0.044739 | 121.4385 | 121.6075 | 121.0328 | 121.2681 | -121.4822 | -121.0765 | -121.4427 | -121.037
902.1094 | 121.7697 | -121.5546 | 0.10071 | 0.080646 | -0.0451 | 0.020051 | -0.052488 | 0.036265 | 0.035221 | -0.12223 | -0.048239 | 0.060902 | -0.022532 | 0.026427 | 121.4339 | 121.6075 | 121.0145 | 121.2497 | 0.094379 | -0.031367 | 0.033784 | -0.038755 | 0.049998 | 0.048954 | -0.1085 | -0.034506 | 0.074635 | -0.008799 | 0.04016 | 121.4477 | 121.6212 | 121.0282 | 121.2635 | -121.4822 | -121.0628 | -121.4565 | -121.037
903.8438 | 121.7606 | -121.5225 | 0.11902 | 0.076067 | -0.040521 | 0.020051 | -0.066223 | 0.036265 | 0.030642 | -0.11765 | -0.048239 | 0.060902 | -0.013376 | 0.017268 | 121.4339 | 121.6029 | 121.0237 | 121.2452 | 0.0898 | -0.026788 | 0.033784 | -0.05249 | 0.049998 | 0.044375 | -0.10392 | -0.034506 | 0.074635 | 0.000357 | 0.031001 | 121.4477 | 121.6166 | 121.0374 | 121.2589 | -121.4822 | -121.0719 | -121.4473 | -121.037
905.5156 | 121.7285 | -121.5363 | 0.11902 | 0.080646 | -0.035942 | 0.020051 | -0.057066 | 0.040843 | 0.035221 | -0.11765 | -0.057396 | 0.065481 | -0.022532 | 0.026427 | 121.4293 | 121.6075 | 121.0099 | 121.2497 | 0.094379 | -0.022209 | 0.033784 | -0.043333 | 0.054576 | 0.048954 | -0.10392 | -0.043663 | 0.079214 | -0.008799 | 0.04016 | 121.4431 | 121.6212 | 121.0237 | 121.2635 | -121.4867 | -121.0673 | -121.4519 | -121.0325
907.25 | 121.6919 | -121.55 | 0.13275 | 0.076067 | -0.040521 | 0.020051 | -0.057066 | 0.036265 | 0.035221 | -0.12223 | -0.048239 | 0.060902 | -0.013376 | 0.035585 | 121.4385 | 121.6075 | 121.0145 | 121.2543 | 0.0898 | -0.026788 | 0.033784 | -0.043333 | 0.049998 | 0.048954 | -0.1085 | -0.034506 | 0.074635 | 0.000357 | 0.049318 | 121.4522 | 121.6212 | 121.0282 | 121.2681 | -121.4867 | -121.0628 | -121.4519 | -121.0279
908.9219 | 121.7148 | -121.5408 | 0.12817 | 0.071489 | -0.040521 | 0.024629 | -0.057066 | 0.031687 | 0.030642 | -0.12223 | -0.057396 | 0.060902 | -0.017954 | 0.026427 | 121.4293 | 121.6029 | 121.0191 | 121.2543 | 0.085222 | -0.026788 | 0.038362 | -0.043333 | 0.04542 | 0.044375 | -0.1085 | -0.043663 | 0.074635 | -0.004221 | 0.04016 | 121.4431 | 121.6166 | 121.0328 | 121.2681 | -121.4867 | -121.0765 | -121.4473 | -121.037
910.6562 | 121.8658 | -121.5408 | 0.07782 | 0.076067 | -0.0451 | 0.024629 | -0.066223 | 0.040843 | 0.030642 | -0.12223 | -0.057396 | 0.051744 | -0.022532 | 0.026427 | 121.4385 | 121.6121 | 121.0237 | 121.2543 | 0.0898 | -0.031367 | 0.038362 | -0.05249 | 0.054576 | 0.044375 | -0.1085 | -0.043663 | 0.065477 | -0.008799 | 0.04016 | 121.4522 | 121.6258 | 121.0374 | 121.2681 | -121.4959 | -121.0811 | -121.461 | -121.0462
912.3438 | 121.7697 | -121.55 | 0.12817 | 0.071489 | -0.0451 | 0.015472 | -0.061645 | 0.036265 | 0.039799 | -0.11308 | -0.048239 | 0.060902 | -0.017954 | 0.021847 | 121.4339 | 121.6121 | 121.0328 | 121.2635 | 0.085222 | -0.031367 | 0.029205 | -0.047912 | 0.049998 | 0.053532 | -0.099344 | -0.034506 | 0.074635 | -0.004221 | 0.03558 | 121.4477 | 121.6258 | 121.0466 | 121.2772 | -121.4822 | -121.0811 | -121.4519 | -121.0508
914.0156 | 121.7468 | -121.5546 | 0.12817 | 0.076067 | -0.040521 | 0.015472 | -0.057066 | 0.031687 | 0.035221 | -0.12223 | -0.052818 | 0.056323 | -0.022532 | 0.031006 | 121.4339 | 121.6121 | 121.0237 | 121.2589 | 0.0898 | -0.026788 | 0.029205 | -0.043333 | 0.04542 | 0.048954 | -0.1085 | -0.039085 | 0.070056 | -0.008799 | 0.044739 | 121.4477 | 121.6258 | 121.0374 | 121.2726 | -121.4867 | -121.0765 | -121.4565 | -121.0462
915.75 | 121.7285 | -121.5591 | 0.10986 | 0.071489 | -0.049678 | 0.024629 | -0.061645 | 0.040843 | 0.030642 | -0.12223 | -0.052818 | 0.056323 | -0.017954 | 0.031006 | 121.4431 | 121.6167 | 121.0237 | 121.2635 | 0.085222 | -0.035945 | 0.038362 | -0.047912 | 0.054576 | 0.044375 | -0.1085 | -0.039085 | 0.070056 | -0.004221 | 0.044739 | 121.4568 | 121.6304 | 121.0374 | 121.2772 | -121.4959 | -121.0765 | -121.461 | -121.0416
917.4219 | 121.7056 | -121.5363 | 0.11902 | 0.076067 | -0.0451 | 0.020051 | -0.066223 | 0.031687 | 0.039799 | -0.12223 | -0.048239 | 0.056323 | -0.022532 | 0.026427 | 121.4339 | 121.6121 | 121.0191 | 121.2589 | 0.0898 | -0.031367 | 0.033784 | -0.05249 | 0.04542 | 0.053532 | -0.1085 | -0.034506 | 0.070056 | -0.008799 | 0.04016 | 121.4477 | 121.6258 | 121.0328 | 121.2726 | -121.4822 | -121.0673 | -121.4565 | -121.0416
919.1562 | 121.788 | -121.5408 | 0.11444 | 0.071489 | -0.040521 | 0.029208 | -0.057066 | 0.031687 | 0.035221 | -0.12223 | -0.048239 | 0.056323 | -0.013376 | 0.026427 | 121.4339 | 121.6121 | 121.0237 | 121.2543 | 0.085222 | -0.026788 | 0.042941 | -0.043333 | 0.04542 | 0.048954 | -0.1085 | -0.034506 | 0.070056 | 0.000357 | 0.04016 | 121.4477 | 121.6258 | 121.0374 | 121.2681 | -121.4822 | -121.0719 | -121.4473 | -121.037
920.8906 | 121.7789 | -121.5408 | 0.10529 | 0.076067 | -0.049678 | 0.015472 | -0.061645 | 0.036265 | 0.026064 | -0.12223 | -0.048239 | 0.056323 | -0.013376 | 0.031006 | 121.4385 | 121.6075 | 121.0237 | 121.2589 | 0.0898 | -0.035945 | 0.029205 | -0.047912 | 0.049998 | 0.039797 | -0.1085 | -0.034506 | 0.070056 | 0.000357 | 0.044739 | 121.4522 | 121.6212 | 121.0374 | 121.2726 | -121.4867 | -121.0719 | -121.4519 | -121.037
922.5625 | 121.7972 | -121.5271 | 0.09613 | 0.080646 | -0.058836 | 0.010893 | -0.061645 | 0.031687 | 0.030642 | -0.12681 | -0.052818 | 0.056323 | -0.013376 | 0.026427 | 121.4385 | 121.6167 | 121.0282 | 121.2635 | 0.094379 | -0.045103 | 0.024626 | -0.047912 | 0.04542 | 0.044375 | -0.11308 | -0.039085 | 0.070056 | 0.000357 | 0.04016 | 121.4522 | 121.6304 | 121.042 | 121.2772 | -121.4913 | -121.0811 | -121.4519 | -121.0416
924.2969 | 121.8246 | -121.5454 | 0.086975 | 0.071489 | -0.049678 | 0.015472 | -0.061645 | 0.027109 | 0.030642 | -0.12223 | -0.048239 | 0.060902 | -0.008798 | 0.035585 | 121.4431 | 121.6167 | 121.0237 | 121.2589 | 0.085222 | -0.035945 | 0.029205 | -0.047912 | 0.040842 | 0.044375 | -0.1085 | -0.034506 | 0.074635 | 0.004935 | 0.049318 | 121.4568 | 121.6304 | 121.0374 | 121.2726 | -121.4913 | -121.0719 | -121.4519 | -121.0325
926.0312 | 121.7239 | -121.5637 | 0.13275 | 0.080646 | -0.054257 | 0.024629 | -0.070802 | 0.031687 | 0.030642 | -0.12223 | -0.048239 | 0.051744 | -0.022532 | 0.026427 | 121.4385 | 121.6258 | 121.0328 | 121.2681 | 0.094379 | -0.040524 | 0.038362 | -0.057069 | 0.04542 | 0.044375 | -0.1085 | -0.034506 | 0.065477 | -0.008799 | 0.04016 | 121.4522 | 121.6395 | 121.0466 | 121.2818 | -121.4867 | -121.0811 | -121.461 | -121.0554
927.7812 | 121.7651 | -121.5637 | 0.11444 | 0.071489 | -0.054257 | 0.024629 | -0.066223 | 0.027109 | 0.044377 | -0.12681 | -0.052818 | 0.060902 | -0.017954 | 0.026427 | 121.4477 | 121.6212 | 121.0328 | 121.2681 | 0.085222 | -0.040524 | 0.038362 | -0.05249 | 0.040842 | 0.05811 | -0.11308 | -0.039085 | 0.074635 | -0.004221 | 0.04016 | 121.4614 | 121.635 | 121.0466 | 121.2818 | -121.5005 | -121.0856 | -121.4656 | -121.0508
929.4531 | 121.756 | -121.5729 | 0.11444 | 0.080646 | -0.063415 | 0.020051 | -0.061645 | 0.031687 | 0.030642 | -0.11765 | -0.048239 | 0.051744 | -0.017954 | 0.026427 | 121.4477 | 121.6212 | 121.0374 | 121.2681 | 0.094379 | -0.049682 | 0.033784 | -0.047912 | 0.04542 | 0.044375 | -0.10392 | -0.034506 | 0.065477 | -0.004221 | 0.04016 | 121.4614 | 121.635 | 121.0511 | 121.2818 | -121.4959 | -121.0856 | -121.4656 | -121.0554
931.1875 | 121.8201 | -121.5179 | 0.082397 | 0.076067 | -0.054257 | 0.024629 | -0.061645 | 0.045421 | 0.030642 | -0.11765 | -0.052818 | 0.060902 | -0.013376 | 0.026427 | 121.4385 | 121.6258 | 121.0282 | 121.2681 | 0.0898 | -0.040524 | 0.038362 | -0.047912 | 0.059154 | 0.044375 | -0.10392 | -0.039085 | 0.074635 | 0.000357 | 0.04016 | 121.4522 | 121.6395 | 121.042 | 121.2818 | -121.4913 | -121.0811 | -121.4519 | -121.0416
932.9219 | 121.7789 | -121.5775 | 0.11902 | 0.080646 | -0.063415 | 0.015472 | -0.061645 | 0.031687 | 0.030642 | -0.12223 | -0.052818 | 0.047165 | -0.027111 | 0.031006 | 121.4522 | 121.6304 | 121.0328 | 121.2726 | 0.094379 | -0.049682 | 0.029205 | -0.047912 | 0.04542 | 0.044375 | -0.1085 | -0.039085 | 0.060898 | -0.013378 | 0.044739 | 121.466 | 121.6441 | 121.0466 | 121.2864 | -121.5051 | -121.0856 | -121.4793 | -121.0599
934.6562 | 121.8796 | -121.5134 | 0.082397 | 0.080646 | -0.067994 | 0.015472 | -0.061645 | 0.027109 | 0.026064 | -0.12681 | -0.048239 | 0.060902 | -0.013376 | 0.035585 | 121.4477 | 121.6167 | 121.042 | 121.2772 | 0.094379 | -0.054261 | 0.029205 | -0.047912 | 0.040842 | 0.039797 | -0.11308 | -0.034506 | 0.074635 | 0.000357 | 0.049318 | 121.4614 | 121.6304 | 121.0557 | 121.2909 | -121.4959 | -121.0902 | -121.461 | -121.0554
936.3906 | 121.7697 | -121.5637 | 0.11902 | 0.076067 | -0.067994 | 0.020051 | -0.061645 | 0.031687 | 0.030642 | -0.12223 | -0.043661 | 0.065481 | -0.013376 | 0.031006 | 121.4477 | 121.635 | 121.042 | 121.2635 | 0.0898 | -0.054261 | 0.033784 | -0.047912 | 0.04542 | 0.044375 | -0.1085 | -0.029928 | 0.079214 | 0.000357 | 0.044739 | 121.4614 | 121.6487 | 121.0557 | 121.2772 | -121.4913 | -121.0856 | -121.461 | -121.0554
938.125 | 121.8292 | -121.5454 | 0.086975 | 0.076067 | -0.072572 | 0.020051 | -0.070802 | 0.027109 | 0.035221 | -0.12681 | -0.048239 | 0.056323 | -0.013376 | 0.031006 | 121.4431 | 121.635 | 121.0374 | 121.2726 | 0.0898 | -0.058839 | 0.033784 | -0.057069 | 0.040842 | 0.048954 | -0.11308 | -0.034506 | 0.070056 | 0.000357 | 0.044739 | 121.4568 | 121.6487 | 121.0511 | 121.2864 | -121.4913 | -121.0856 | -121.4565 | -121.0508
939.8125 | 121.8246 | -121.5546 | 0.091553 | 0.071489 | -0.077151 | 0.010893 | -0.066223 | 0.031687 | 0.030642 | -0.12223 | -0.048239 | 0.060902 | -0.013376 | 0.035585 | 121.4385 | 121.635 | 121.042 | 121.2726 | 0.085222 | -0.063418 | 0.024626 | -0.05249 | 0.04542 | 0.044375 | -0.1085 | -0.034506 | 0.074635 | 0.000357 | 0.049318 | 121.4522 | 121.6487 | 121.0557 | 121.2864 | -121.4867 | -121.0902 | -121.4519 | -121.0554
941.5625 | 121.7834 | -121.5591 | 0.11902 | 0.080646 | -0.077151 | 0.015472 | -0.061645 | 0.031687 | 0.035221 | -0.12223 | -0.052818 | 0.060902 | -0.017954 | 0.026427 | 121.4477 | 121.6304 | 121.042 | 121.2772 | 0.094379 | -0.063418 | 0.029205 | -0.047912 | 0.04542 | 0.048954 | -0.1085 | -0.039085 | 0.074635 | -0.004221 | 0.04016 | 121.4614 | 121.6441 | 121.0557 | 121.2909 | -121.5005 | -121.0948 | -121.4656 | -121.0599
943.2969 | 121.8704 | -121.5179 | 0.091553 | 0.076067 | -0.072572 | 0.020051 | -0.061645 | 0.036265 | 0.030642 | -0.11308 | -0.048239 | 0.065481 | -0.017954 | 0.026427 | 121.4477 | 121.635 | 121.0328 | 121.2681 | 0.0898 | -0.058839 | 0.033784 | -0.047912 | 0.049998 | 0.044375 | -0.099344 | -0.034506 | 0.079214 | -0.004221 | 0.04016 | 121.4614 | 121.6487 | 121.0466 | 121.2818 | -121.4959 | -121.0811 | -121.4656 | -121.0508
944.9688 | 121.8704 | -121.5408 | 0.091553 | 0.080646 | -0.072572 | 0.020051 | -0.061645 | 0.027109 | 0.030642 | -0.11765 | -0.043661 | 0.056323 | -0.017954 | 0.035585 | 121.4431 | 121.635 | 121.042 | 121.2772 | 0.094379 | -0.058839 | 0.033784 | -0.047912 | 0.040842 | 0.044375 | -0.10392 | -0.029928 | 0.070056 | -0.004221 | 0.049318 | 121.4568 | 121.6487 | 121.0557 | 121.2909 | -121.4867 | -121.0856 | -121.461 | -121.0599
946.7031 | 121.8613 | -121.5271 | 0.091553 | 0.071489 | -0.086309 | 0.020051 | -0.066223 | 0.031687 | 0.026064 | -0.11765 | -0.052818 | 0.056323 | -0.022532 | 0.026427 | 121.4568 | 121.6304 | 121.0466 | 121.2818 | 0.085222 | -0.072576 | 0.033784 | -0.05249 | 0.04542 | 0.039797 | -0.10392 | -0.039085 | 0.070056 | -0.008799 | 0.04016 | 121.4705 | 121.6441 | 121.0603 | 121.2955 | -121.5096 | -121.0994 | -121.4793 | -121.0691
948.375 | 121.7422 | -121.5729 | 0.12817 | 0.076067 | -0.067994 | 0.015472 | -0.070802 | 0.036265 | 0.039799 | -0.12223 | -0.048239 | 0.060902 | -0.013376 | 0.026427 | 121.4568 | 121.6395 | 121.0466 | 121.2772 | 0.0898 | -0.054261 | 0.029205 | -0.057069 | 0.049998 | 0.053532 | -0.1085 | -0.034506 | 0.074635 | 0.000357 | 0.04016 | 121.4705 | 121.6533 | 121.0603 | 121.2909 | -121.505 | -121.0948 | -121.4702 | -121.0599
950.1094 | 121.7377 | -121.5958 | 0.10986 | 0.076067 | -0.08173 | 0.020051 | -0.066223 | 0.027109 | 0.021485 | -0.12223 | -0.048239 | 0.056323 | -0.017954 | 0.026427 | 121.4522 | 121.635 | 121.0511 | 121.2772 | 0.0898 | -0.067997 | 0.033784 | -0.05249 | 0.040842 | 0.035218 | -0.1085 | -0.034506 | 0.070056 | -0.004221 | 0.04016 | 121.466 | 121.6487 | 121.0649 | 121.2909 | -121.5005 | -121.0994 | -121.4702 | -121.0691
951.8438 | 121.7468 | -121.5775 | 0.11444 | 0.080646 | -0.077151 | 0.020051 | -0.066223 | 0.027109 | 0.026064 | -0.12681 | -0.048239 | 0.056323 | -0.017954 | 0.026427 | 121.4522 | 121.6441 | 121.0466 | 121.2772 | 0.094379 | -0.063418 | 0.033784 | -0.05249 | 0.040842 | 0.039797 | -0.11308 | -0.034506 | 0.070056 | -0.004221 | 0.04016 | 121.466 | 121.6579 | 121.0603 | 121.2909 | -121.5005 | -121.0948 | -121.4702 | -121.0645
953.5938 | 121.843 | -121.5454 | 0.07782 | 0.071489 | -0.077151 | 0.020051 | -0.066223 | 0.031687 | 0.030642 | -0.12681 | -0.052818 | 0.060902 | -0.022532 | 0.026427 | 121.4522 | 121.6395 | 121.0511 | 121.2818 | 0.085222 | -0.063418 | 0.033784 | -0.05249 | 0.04542 | 0.044375 | -0.11308 | -0.039085 | 0.074635 | -0.008799 | 0.04016 | 121.466 | 121.6533 | 121.0649 | 121.2955 | -121.5051 | -121.104 | -121.4748 | -121.0737
955.3438 | 121.8658 | -121.5546 | 0.091553 | 0.076067 | -0.08173 | 0.015472 | -0.061645 | 0.027109 | 0.021485 | -0.12223 | -0.048239 | 0.060902 | -0.017954 | 0.026427 | 121.4568 | 121.6441 | 121.0557 | 121.2818 | 0.0898 | -0.067997 | 0.029205 | -0.047912 | 0.040842 | 0.035218 | -0.1085 | -0.034506 | 0.074635 | -0.004221 | 0.04016 | 121.4705 | 121.6579 | 121.0695 | 121.2955 | -121.505 | -121.104 | -121.4748 | -121.0737
957.0312 | 121.875 | -121.5408 | 0.07782 | 0.076067 | -0.08173 | 0.020051 | -0.066223 | 0.027109 | 0.026064 | -0.12681 | -0.048239 | 0.056323 | -0.017954 | 0.021847 | 121.4568 | 121.6395 | 121.0603 | 121.2864 | 0.0898 | -0.067997 | 0.033784 | -0.05249 | 0.040842 | 0.039797 | -0.11308 | -0.034506 | 0.070056 | -0.004221 | 0.03558 | 121.4705 | 121.6533 | 121.074 | 121.3001 | -121.505 | -121.1085 | -121.4748 | -121.0782
958.7969 | 121.8338 | -121.5729 | 0.10071 | 0.076067 | -0.067994 | 0.020051 | -0.070802 | 0.027109 | 0.026064 | -0.12223 | -0.043661 | 0.060902 | -0.022532 | 0.026427 | 121.4522 | 121.6395 | 121.0557 | 121.2864 | 0.0898 | -0.054261 | 0.033784 | -0.057069 | 0.040842 | 0.039797 | -0.1085 | -0.029928 | 0.074635 | -0.008799 | 0.04016 | 121.466 | 121.6533 | 121.0695 | 121.3001 | -121.4959 | -121.0994 | -121.4748 | -121.0782
960.5469 | 121.8704 | -121.5454 | 0.082397 | 0.076067 | -0.054257 | 0.015472 | -0.07538 | 0.027109 | 0.026064 | -0.12681 | -0.048239 | 0.060902 | -0.022532 | 0.031006 | 121.4568 | 121.6441 | 121.0511 | 121.2864 | 0.0898 | -0.040524 | 0.029205 | -0.061647 | 0.040842 | 0.039797 | -0.11308 | -0.034506 | 0.074635 | -0.008799 | 0.044739 | 121.4705 | 121.6579 | 121.0649 | 121.3001 | -121.505 | -121.0994 | -121.4793 | -121.0737
962.2969 | 121.8796 | -121.4996 | 0.07782 | 0.080646 | -0.054257 | 0.020051 | -0.066223 | 0.027109 | 0.026064 | -0.13139 | -0.048239 | 0.056323 | -0.022532 | 0.026427 | 121.4568 | 121.6441 | 121.0603 | 121.2864 | 0.094379 | -0.040524 | 0.033784 | -0.05249 | 0.040842 | 0.039797 | -0.11766 | -0.034506 | 0.070056 | -0.008799 | 0.04016 | 121.4705 | 121.6579 | 121.074 | 121.3001 | -121.505 | -121.1085 | -121.4793 | -121.0828
963.9688 | 121.843 | -121.5454 | 0.091553 | 0.076067 | -0.049678 | 0.024629 | -0.07538 | 0.027109 | 0.026064 | -0.11765 | -0.039082 | 0.060902 | -0.017954 | 0.026427 | 121.4522 | 121.6395 | 121.0603 | 121.2864 | 0.0898 | -0.035945 | 0.038362 | -0.061647 | 0.040842 | 0.039797 | -0.10392 | -0.025349 | 0.074635 | -0.004221 | 0.04016 | 121.466 | 121.6533 | 121.074 | 121.3001 | -121.4913 | -121.0994 | -121.4702 | -121.0782
965.6562 | 121.7743 | -121.5637 | 0.10529 | 0.076067 | -0.049678 | 0.015472 | -0.070802 | 0.027109 | 0.030642 | -0.12681 | -0.048239 | 0.065481 | -0.017954 | 0.026427 | 121.4568 | 121.6441 | 121.0511 | 121.2864 | 0.0898 | -0.035945 | 0.029205 | -0.057069 | 0.040842 | 0.044375 | -0.11308 | -0.034506 | 0.079214 | -0.004221 | 0.04016 | 121.4705 | 121.6579 | 121.0649 | 121.3001 | -121.505 | -121.0994 | -121.4748 | -121.0691
967.4062 | 121.7972 | -121.5775 | 0.09613 | 0.076067 | -0.049678 | 0.015472 | -0.066223 | 0.036265 | 0.026064 | -0.12223 | -0.048239 | 0.065481 | -0.017954 | 0.031006 | 121.4568 | 121.6487 | 121.0466 | 121.2864 | 0.0898 | -0.035945 | 0.029205 | -0.05249 | 0.049998 | 0.039797 | -0.1085 | -0.034506 | 0.079214 | -0.004221 | 0.044739 | 121.4705 | 121.6624 | 121.0603 | 121.3001 | -121.505 | -121.0948 | -121.4748 | -121.0645
969.0781 | 121.7972 | -121.5591 | 0.11444 | 0.071489 | -0.049678 | 0.015472 | -0.079959 | 0.031687 | 0.030642 | -0.12681 | -0.057396 | 0.065481 | -0.022532 | 0.026427 | 121.4568 | 121.6487 | 121.0557 | 121.2864 | 0.085222 | -0.035945 | 0.029205 | -0.066226 | 0.04542 | 0.044375 | -0.11308 | -0.043663 | 0.079214 | -0.008799 | 0.04016 | 121.4705 | 121.6624 | 121.0695 | 121.3001 | -121.5142 | -121.1131 | -121.4793 | -121.0782
970.8125 | 121.8338 | -121.5729 | 0.086975 | 0.080646 | -0.049678 | 0.006315 | -0.070802 | 0.022531 | 0.021485 | -0.13139 | -0.048239 | 0.056323 | -0.022532 | 0.031006 | 121.4568 | 121.6395 | 121.0649 | 121.2864 | 0.094379 | -0.035945 | 0.020048 | -0.057069 | 0.036264 | 0.035218 | -0.11766 | -0.034506 | 0.070056 | -0.008799 | 0.044739 | 121.4705 | 121.6533 | 121.0786 | 121.3001 | -121.505 | -121.1131 | -121.4793 | -121.0874
972.5 | 121.8933 | -121.55 | 0.082397 | 0.076067 | -0.054257 | 0.006315 | -0.070802 | 0.022531 | 0.016907 | -0.13139 | -0.052818 | 0.060902 | -0.013376 | 0.031006 | 121.4614 | 121.6441 | 121.0649 | 121.2864 | 0.0898 | -0.040524 | 0.020048 | -0.057069 | 0.036264 | 0.03064 | -0.11766 | -0.039085 | 0.074635 | 0.000357 | 0.044739 | 121.4751 | 121.6579 | 121.0786 | 121.3001 | -121.5142 | -121.1177 | -121.4748 | -121.0782
974.1719 | 121.8613 | -121.5271 | 0.10986 | 0.071489 | -0.054257 | 0.010893 | -0.070802 | 0.022531 | 0.016907 | -0.13139 | -0.052818 | 0.051744 | -0.013376 | 0.035585 | 121.4568 | 121.6441 | 121.074 | 121.2864 | 0.085222 | -0.040524 | 0.024626 | -0.057069 | 0.036264 | 0.03064 | -0.11766 | -0.039085 | 0.065477 | 0.000357 | 0.049318 | 121.4705 | 121.6579 | 121.0878 | 121.3001 | -121.5096 | -121.1268 | -121.4702 | -121.0874
975.9062 | 121.8155 | -121.5591 | 0.091553 | 0.06691 | -0.054257 | 0.010893 | -0.070802 | 0.031687 | 0.016907 | -0.13139 | -0.039082 | 0.056323 | -0.008798 | 0.031006 | 121.4568 | 121.6487 | 121.0786 | 121.2864 | 0.080643 | -0.040524 | 0.024626 | -0.057069 | 0.04542 | 0.03064 | -0.11766 | -0.025349 | 0.070056 | 0.004935 | 0.044739 | 121.4705 | 121.6624 | 121.0923 | 121.3001 | -121.4959 | -121.1177 | -121.4656 | -121.0874
977.5781 | 121.7697 | -121.6049 | 0.13275 | 0.071489 | -0.049678 | 0.015472 | -0.07538 | 0.027109 | 0.016907 | -0.12681 | -0.048239 | 0.056323 | -0.013376 | 0.026427 | 121.4614 | 121.6533 | 121.0878 | 121.2909 | 0.085222 | -0.035945 | 0.029205 | -0.061647 | 0.040842 | 0.03064 | -0.11308 | -0.034506 | 0.070056 | 0.000357 | 0.04016 | 121.4751 | 121.667 | 121.1015 | 121.3047 | -121.5096 | -121.136 | -121.4748 | -121.1011
979.3125 | 121.8384 | -121.5546 | 0.082397 | 0.071489 | -0.054257 | 0.020051 | -0.070802 | 0.022531 | 0.026064 | -0.13139 | -0.057396 | 0.056323 | -0.022532 | 0.031006 | 121.4568 | 121.6533 | 121.074 | 121.2818 | 0.085222 | -0.040524 | 0.033784 | -0.057069 | 0.036264 | 0.039797 | -0.11766 | -0.043663 | 0.070056 | -0.008799 | 0.044739 | 121.4705 | 121.667 | 121.0878 | 121.2955 | -121.5142 | -121.1314 | -121.4793 | -121.0966
980.9844 | 121.8338 | -121.5591 | 0.09613 | 0.080646 | -0.054257 | 0.010893 | -0.07538 | 0.022531 | 0.026064 | -0.12681 | -0.061975 | 0.065481 | -0.017954 | 0.031006 | 121.4568 | 121.6487 | 121.0832 | 121.2909 | 0.094379 | -0.040524 | 0.024626 | -0.061647 | 0.036264 | 0.039797 | -0.11308 | -0.048242 | 0.079214 | -0.004221 | 0.044739 | 121.4705 | 121.6624 | 121.0969 | 121.3047 | -121.5188 | -121.1452 | -121.4748 | -121.1011
982.7344 | 121.8567 | -121.5637 | 0.10071 | 0.076067 | -0.049678 | 0.010893 | -0.070802 | 0.017953 | 0.030642 | -0.13139 | -0.048239 | 0.065481 | -0.013376 | 0.026427 | 121.466 | 121.6487 | 121.1015 | 121.2864 | 0.0898 | -0.035945 | 0.024626 | -0.057069 | 0.031686 | 0.044375 | -0.11766 | -0.034506 | 0.079214 | 0.000357 | 0.04016 | 121.4797 | 121.6624 | 121.1152 | 121.3001 | -121.5142 | -121.1497 | -121.4793 | -121.1149
984.4062 | 121.875 | -121.5363 | 0.086975 | 0.076067 | -0.049678 | 0.006315 | -0.070802 | 0.017953 | 0.026064 | -0.12681 | -0.048239 | 0.051744 | -0.022532 | 0.031006 | 121.466 | 121.6487 | 121.0923 | 121.2818 | 0.0898 | -0.035945 | 0.020048 | -0.057069 | 0.031686 | 0.039797 | -0.11308 | -0.034506 | 0.065477 | -0.008799 | 0.044739 | 121.4797 | 121.6624 | 121.1061 | 121.2955 | -121.5142 | -121.1406 | -121.4885 | -121.1149
986.1406 | 121.7926 | -121.5591 | 0.10986 | 0.06691 | -0.054257 | 0.015472 | -0.070802 | 0.027109 | 0.021485 | -0.12681 | -0.052818 | 0.060902 | -0.017954 | 0.021847 | 121.4614 | 121.6533 | 121.0832 | 121.2955 | 0.080643 | -0.040524 | 0.029205 | -0.057069 | 0.040842 | 0.035218 | -0.11308 | -0.039085 | 0.074635 | -0.004221 | 0.03558 | 121.4751 | 121.667 | 121.0969 | 121.3093 | -121.5142 | -121.136 | -121.4793 | -121.1011
987.8906 | 121.7789 | -121.5775 | 0.11444 | 0.071489 | -0.054257 | 0.010893 | -0.07538 | 0.027109 | 0.021485 | -0.12681 | -0.043661 | 0.051744 | -0.013376 | 0.031006 | 121.4705 | 121.6533 | 121.0878 | 121.2955 | 0.085222 | -0.040524 | 0.024626 | -0.061647 | 0.040842 | 0.035218 | -0.11308 | -0.029928 | 0.065477 | 0.000357 | 0.044739 | 121.4843 | 121.667 | 121.1015 | 121.3093 | -121.5142 | -121.1314 | -121.4839 | -121.1011
989.5781 | 121.7514 | -121.5729 | 0.1236 | 0.080646 | -0.049678 | 0.010893 | -0.079959 | 0.022531 | 0.026064 | -0.12223 | -0.048239 | 0.060902 | -0.022532 | 0.026427 | 121.466 | 121.6579 | 121.0786 | 121.3001 | 0.094379 | -0.035945 | 0.024626 | -0.066226 | 0.036264 | 0.039797 | -0.1085 | -0.034506 | 0.074635 | -0.008799 | 0.04016 | 121.4797 | 121.6716 | 121.0923 | 121.3138 | -121.5142 | -121.1268 | -121.4885 | -121.1011
991.3125 | 121.8613 | -121.5591 | 0.07782 | 0.076067 | -0.054257 | 0.015472 | -0.07538 | 0.017953 | 0.021485 | -0.13139 | -0.052818 | 0.056323 | -0.022532 | 0.026427 | 121.4751 | 121.6533 | 121.0786 | 121.2955 | 0.0898 | -0.040524 | 0.029205 | -0.061647 | 0.031686 | 0.035218 | -0.11766 | -0.039085 | 0.070056 | -0.008799 | 0.04016 | 121.4889 | 121.667 | 121.0923 | 121.3093 | -121.5279 | -121.1314 | -121.4977 | -121.1011
993 | 121.7651 | -121.582 | 0.11444 | 0.076067 | -0.054257 | 0.015472 | -0.07538 | 0.022531 | 0.021485 | -0.11765 | -0.057396 | 0.051744 | -0.017954 | 0.017268 | 121.4705 | 121.6579 | 121.0878 | 121.2955 | 0.0898 | -0.040524 | 0.029205 | -0.061647 | 0.036264 | 0.035218 | -0.10392 | -0.043663 | 0.065477 | -0.004221 | 0.031001 | 121.4843 | 121.6716 | 121.1015 | 121.3093 | -121.5279 | -121.1452 | -121.4885 | -121.1057
994.7344 | 121.8018 | -121.5775 | 0.091553 | 0.071489 | -0.063415 | 0.010893 | -0.07538 | 0.022531 | 0.021485 | -0.12681 | -0.052818 | 0.056323 | -0.008798 | 0.031006 | 121.466 | 121.6579 | 121.0923 | 121.3001 | 0.085222 | -0.049682 | 0.024626 | -0.061647 | 0.036264 | 0.035218 | -0.11308 | -0.039085 | 0.070056 | 0.004935 | 0.044739 | 121.4797 | 121.6716 | 121.1061 | 121.3138 | -121.5188 | -121.1452 | -121.4748 | -121.1011
996.4688 | 121.8521 | -121.5683 | 0.073242 | 0.071489 | -0.058836 | 0.024629 | -0.066223 | 0.031687 | 0.012329 | -0.13139 | -0.048239 | 0.060902 | -0.013376 | 0.031006 | 121.4705 | 121.6533 | 121.1015 | 121.2955 | 0.085222 | -0.045103 | 0.038362 | -0.05249 | 0.04542 | 0.026062 | -0.11766 | -0.034506 | 0.074635 | 0.000357 | 0.044739 | 121.4843 | 121.667 | 121.1152 | 121.3093 | -121.5188 | -121.1497 | -121.4839 | -121.1149
998.2188 | 121.7422 | -121.5866 | 0.11444 | 0.071489 | -0.058836 | 0.006315 | -0.07538 | 0.027109 | 0.016907 | -0.13139 | -0.052818 | 0.060902 | -0.017954 | 0.026427 | 121.4614 | 121.6579 | 121.0878 | 121.2909 | 0.085222 | -0.045103 | 0.020048 | -0.061647 | 0.040842 | 0.03064 | -0.11766 | -0.039085 | 0.074635 | -0.004221 | 0.04016 | 121.4751 | 121.6716 | 121.1015 | 121.3047 | -121.5142 | -121.1406 | -121.4793 | -121.1057
999.9531 | 121.7239 | -121.5866 | 0.1236 | 0.071489 | -0.063415 | 0.006315 | -0.07538 | 0.022531 | 0.016907 | -0.13139 | -0.048239 | 0.056323 | -0.017954 | 0.031006 | 121.4705 | 121.6579 | 121.0923 | 121.2955 | 0.085222 | -0.049682 | 0.020048 | -0.061647 | 0.036264 | 0.03064 | -0.11766 | -0.034506 | 0.070056 | -0.004221 | 0.044739 | 121.4843 | 121.6716 | 121.1061 | 121.3093 | -121.5188 | -121.1406 | -121.4885 | -121.1103
1001.625 | 121.8887 | -121.5546 | 0.082397 | 0.071489 | -0.067994 | 0.006315 | -0.079959 | 0.017953 | 0.016907 | -0.13597 | -0.052818 | 0.051744 | -0.022532 | 0.026427 | 121.4705 | 121.6579 | 121.0923 | 121.2955 | 0.085222 | -0.054261 | 0.020048 | -0.066226 | 0.031686 | 0.03064 | -0.12224 | -0.039085 | 0.065477 | -0.008799 | 0.04016 | 121.4843 | 121.6716 | 121.1061 | 121.3093 | -121.5234 | -121.1452 | -121.4931 | -121.1149
1003.375 | 121.7468 | -121.6003 | 0.10529 | 0.076067 | -0.063415 | 0.010893 | -0.079959 | 0.022531 | 0.016907 | -0.12223 | -0.052818 | 0.056323 | -0.017954 | 0.026427 | 121.466 | 121.6624 | 121.0878 | 121.2955 | 0.0898 | -0.049682 | 0.024626 | -0.066226 | 0.036264 | 0.03064 | -0.1085 | -0.039085 | 0.070056 | -0.004221 | 0.04016 | 121.4797 | 121.6762 | 121.1015 | 121.3093 | -121.5188 | -121.1406 | -121.4839 | -121.1057
1005.0469 | 121.7651 | -121.6049 | 0.11444 | 0.06691 | -0.067994 | 0.010893 | -0.070802 | 0.022531 | 0.021485 | -0.13139 | -0.057396 | 0.051744 | -0.017954 | 0.035585 | 121.4751 | 121.6624 | 121.1015 | 121.2955 | 0.080643 | -0.054261 | 0.024626 | -0.057069 | 0.036264 | 0.035218 | -0.11766 | -0.043663 | 0.065477 | -0.004221 | 0.049318 | 121.4889 | 121.6762 | 121.1152 | 121.3093 | -121.5325 | -121.1589 | -121.4931 | -121.1195
1006.7969 | 121.8887 | -121.5729 | 0.073242 | 0.080646 | -0.063415 | -0.002842 | -0.079959 | 0.017953 | 0.012329 | -0.13139 | -0.048239 | 0.060902 | -0.022532 | 0.026427 | 121.4705 | 121.6624 | 121.0923 | 121.3001 | 0.094379 | -0.049682 | 0.010891 | -0.066226 | 0.031686 | 0.026062 | -0.11766 | -0.034506 | 0.074635 | -0.008799 | 0.04016 | 121.4843 | 121.6762 | 121.1061 | 121.3138 | -121.5188 | -121.1406 | -121.4931 | -121.1149
1008.4688 | 121.7514 | -121.6003 | 0.12817 | 0.080646 | -0.063415 | 0.006315 | -0.07538 | 0.017953 | 0.012329 | -0.13139 | -0.043661 | 0.060902 | -0.031689 | 0.026427 | 121.4751 | 121.6579 | 121.1061 | 121.3093 | 0.094379 | -0.049682 | 0.020048 | -0.061647 | 0.031686 | 0.026062 | -0.11766 | -0.029928 | 0.074635 | -0.017956 | 0.04016 | 121.4889 | 121.6716 | 121.1198 | 121.323 | -121.5188 | -121.1497 | -121.5068 | -121.1378
1010.2031 | 121.8887 | -121.5546 | 0.082397 | 0.076067 | -0.067994 | 0.006315 | -0.07538 | 0.022531 | 0.016907 | -0.12223 | -0.048239 | 0.056323 | -0.017954 | 0.026427 | 121.4705 | 121.6624 | 121.1061 | 121.3093 | 0.0898 | -0.054261 | 0.020048 | -0.061647 | 0.036264 | 0.03064 | -0.1085 | -0.034506 | 0.070056 | -0.004221 | 0.04016 | 121.4843 | 121.6762 | 121.1198 | 121.323 | -121.5188 | -121.1543 | -121.4885 | -121.124
1011.875 | 121.7926 | -121.6278 | 0.10529 | 0.076067 | -0.067994 | 0.001736 | -0.079959 | 0.022531 | 0.021485 | -0.13139 | -0.052818 | 0.065481 | -0.017954 | 0.031006 | 121.4751 | 121.6624 | 121.0969 | 121.3001 | 0.0898 | -0.054261 | 0.015469 | -0.066226 | 0.036264 | 0.035218 | -0.11766 | -0.039085 | 0.079214 | -0.004221 | 0.044739 | 121.4889 | 121.6762 | 121.1107 | 121.3138 | -121.5279 | -121.1497 | -121.4931 | -121.1149
1013.6094 | 121.8979 | -121.5546 | 0.082397 | 0.071489 | -0.067994 | 0.001736 | -0.079959 | 0.017953 | 0.012329 | -0.13139 | -0.052818 | 0.056323 | -0.027111 | 0.035585 | 121.4797 | 121.6624 | 121.1244 | 121.3093 | 0.085222 | -0.054261 | 0.015469 | -0.066226 | 0.031686 | 0.026062 | -0.11766 | -0.039085 | 0.070056 | -0.013378 | 0.049318 | 121.4934 | 121.6762 | 121.1381 | 121.323 | -121.5325 | -121.1772 | -121.5068 | -121.1515
1015.3438 | 121.8704 | -121.5775 | 0.07782 | 0.071489 | -0.067994 | 0.006315 | -0.07538 | 0.017953 | 0.016907 | -0.12681 | -0.043661 | 0.060902 | -0.013376 | 0.031006 | 121.4705 | 121.667 | 121.129 | 121.3047 | 0.085222 | -0.054261 | 0.020048 | -0.061647 | 0.031686 | 0.03064 | -0.11308 | -0.029928 | 0.074635 | 0.000357 | 0.044739 | 121.4843 | 121.6807 | 121.1427 | 121.3184 | -121.5142 | -121.1726 | -121.4839 | -121.1423
1017.0156 | 121.8933 | -121.5546 | 0.086975 | 0.080646 | -0.072572 | 0.001736 | -0.07538 | 0.017953 | 0.00775 | -0.12681 | -0.052818 | 0.060902 | -0.008798 | 0.031006 | 121.4705 | 121.6624 | 121.1427 | 121.3001 | 0.094379 | -0.058839 | 0.015469 | -0.061647 | 0.031686 | 0.021483 | -0.11308 | -0.039085 | 0.074635 | 0.004935 | 0.044739 | 121.4843 | 121.6762 | 121.1564 | 121.3138 | -121.5234 | -121.1955 | -121.4793 | -121.1515
1018.75 | 121.8796 | -121.5591 | 0.082397 | 0.080646 | -0.072572 | 0.001736 | -0.079959 | 0.017953 | 0.012329 | -0.13139 | -0.052818 | 0.060902 | -0.022532 | 0.026427 | 121.4705 | 121.667 | 121.1061 | 121.3093 | 0.094379 | -0.058839 | 0.015469 | -0.066226 | 0.031686 | 0.026062 | -0.11766 | -0.039085 | 0.074635 | -0.008799 | 0.04016 | 121.4843 | 121.6807 | 121.1198 | 121.323 | -121.5234 | -121.1589 | -121.4931 | -121.1286
1020.4844 | 121.8063 | -121.582 | 0.11444 | 0.071489 | -0.067994 | 0.001736 | -0.07538 | 0.013375 | 0.016907 | -0.13139 | -0.052818 | 0.056323 | -0.017954 | 0.026427 | 121.4751 | 121.667 | 121.1198 | 121.3047 | 0.085222 | -0.054261 | 0.015469 | -0.061647 | 0.027108 | 0.03064 | -0.11766 | -0.039085 | 0.070056 | -0.004221 | 0.04016 | 121.4889 | 121.6807 | 121.1335 | 121.3184 | -121.5279 | -121.1726 | -121.4931 | -121.1378
1022.1719 | 121.8475 | -121.582 | 0.091553 | 0.076067 | -0.072572 | 0.001736 | -0.070802 | 0.017953 | 0.012329 | -0.13597 | -0.052818 | 0.060902 | -0.017954 | 0.035585 | 121.4797 | 121.6716 | 121.1198 | 121.3047 | 0.0898 | -0.058839 | 0.015469 | -0.057069 | 0.031686 | 0.026062 | -0.12224 | -0.039085 | 0.074635 | -0.004221 | 0.049318 | 121.4934 | 121.6853 | 121.1335 | 121.3184 | -121.5325 | -121.1726 | -121.4977 | -121.1378
1023.9062 | 121.875 | -121.5775 | 0.086975 | 0.071489 | -0.072572 | 0.006315 | -0.079959 | 0.008797 | 0.012329 | -0.13597 | -0.052818 | 0.060902 | -0.017954 | 0.026427 | 121.4797 | 121.667 | 121.1198 | 121.3047 | 0.085222 | -0.058839 | 0.020048 | -0.066226 | 0.02253 | 0.026062 | -0.12224 | -0.039085 | 0.074635 | -0.004221 | 0.04016 | 121.4934 | 121.6807 | 121.1335 | 121.3184 | -121.5325 | -121.1726 | -121.4977 | -121.1378
1025.5781 | 121.9025 | -121.5866 | 0.07782 | 0.076067 | -0.077151 | 0.006315 | -0.084537 | 0.017953 | 0.012329 | -0.14055 | -0.043661 | 0.056323 | -0.017954 | 0.031006 | 121.4797 | 121.6716 | 121.1381 | 121.3093 | 0.0898 | -0.063418 | 0.020048 | -0.070804 | 0.031686 | 0.026062 | -0.12681 | -0.029928 | 0.070056 | -0.004221 | 0.044739 | 121.4934 | 121.6853 | 121.1519 | 121.323 | -121.5234 | -121.1818 | -121.4977 | -121.1561
1027.3125 | 121.9025 | -121.5591 | 0.068665 | 0.076067 | -0.077151 | 0.001736 | -0.07538 | 0.008797 | 0.012329 | -0.13597 | -0.052818 | 0.056323 | -0.017954 | 0.035585 | 121.4751 | 121.6716 | 121.1335 | 121.3093 | 0.0898 | -0.063418 | 0.015469 | -0.061647 | 0.02253 | 0.026062 | -0.12224 | -0.039085 | 0.070056 | -0.004221 | 0.049318 | 121.4889 | 121.6853 | 121.1473 | 121.323 | -121.5279 | -121.1864 | -121.4931 | -121.1515
1029.0469 | 121.843 | -121.5775 | 0.073242 | 0.071489 | -0.08173 | -0.002842 | -0.084537 | 0.008797 | 0.012329 | -0.13139 | -0.052818 | 0.056323 | -0.017954 | 0.031006 | 121.4843 | 121.6716 | 121.129 | 121.3047 | 0.085222 | -0.067997 | 0.010891 | -0.070804 | 0.02253 | 0.026062 | -0.11766 | -0.039085 | 0.070056 | -0.004221 | 0.044739 | 121.498 | 121.6853 | 121.1427 | 121.3184 | -121.5371 | -121.1818 | -121.5022 | -121.1469
1030.7188 | 121.8842 | -121.582 | 0.07782 | 0.071489 | -0.08173 | 0.001736 | -0.079959 | 0.013375 | 0.012329 | -0.13597 | -0.052818 | 0.060902 | -0.017954 | 0.026427 | 121.4843 | 121.6716 | 121.1335 | 121.3138 | 0.085222 | -0.067997 | 0.015469 | -0.066226 | 0.027108 | 0.026062 | -0.12224 | -0.039085 | 0.074635 | -0.004221 | 0.04016 | 121.498 | 121.6853 | 121.1473 | 121.3276 | -121.5371 | -121.1864 | -121.5022 | -121.1515
1032.4531 | 121.8613 | -121.5729 | 0.07782 | 0.071489 | -0.086309 | 0.001736 | -0.07538 | 0.017953 | 0.016907 | -0.13597 | -0.048239 | 0.060902 | -0.022532 | 0.026427 | 121.4797 | 121.6716 | 121.1335 | 121.3047 | 0.085222 | -0.072576 | 0.015469 | -0.061647 | 0.031686 | 0.03064 | -0.12224 | -0.034506 | 0.074635 | -0.008799 | 0.04016 | 121.4934 | 121.6853 | 121.1473 | 121.3184 | -121.5279 | -121.1818 | -121.5022 | -121.1561
1034.125 | 121.8018 | -121.5912 | 0.10071 | 0.076067 | -0.077151 | 0.001736 | -0.084537 | 0.013375 | 0.012329 | -0.13139 | -0.052818 | 0.056323 | -0.008798 | 0.021847 | 121.4843 | 121.6762 | 121.1381 | 121.3138 | 0.0898 | -0.063418 | 0.015469 | -0.070804 | 0.027108 | 0.026062 | -0.11766 | -0.039085 | 0.070056 | 0.004935 | 0.03558 | 121.498 | 121.6899 | 121.1519 | 121.3276 | -121.5371 | -121.1909 | -121.4931 | -121.1469
1035.8438 | 121.8933 | -121.5454 | 0.068665 | 0.071489 | -0.077151 | -0.002842 | -0.07538 | 0.013375 | 0.00775 | -0.13597 | -0.048239 | 0.060902 | -0.017954 | 0.021847 | 121.4705 | 121.6762 | 121.129 | 121.3138 | 0.085222 | -0.063418 | 0.010891 | -0.061647 | 0.027108 | 0.021483 | -0.12224 | -0.034506 | 0.074635 | -0.004221 | 0.03558 | 121.4843 | 121.6899 | 121.1427 | 121.3276 | -121.5188 | -121.1772 | -121.4885 | -121.1469
1037.5156 | 121.8887 | -121.5637 | 0.082397 | 0.071489 | -0.08173 | 0.001736 | -0.079959 | 0.017953 | 0.012329 | -0.14055 | -0.043661 | 0.056323 | -0.022532 | 0.031006 | 121.4797 | 121.6716 | 121.1519 | 121.3184 | 0.085222 | -0.067997 | 0.015469 | -0.066226 | 0.031686 | 0.026062 | -0.12681 | -0.029928 | 0.070056 | -0.008799 | 0.044739 | 121.4934 | 121.6853 | 121.1656 | 121.3322 | -121.5234 | -121.1955 | -121.5022 | -121.1744
1039.25 | 121.8109 | -121.6141 | 0.10529 | 0.06691 | -0.086309 | 0.006315 | -0.084537 | 0.013375 | 0.00775 | -0.14055 | -0.048239 | 0.056323 | -0.027111 | 0.035585 | 121.4934 | 121.6762 | 121.1427 | 121.3093 | 0.080643 | -0.072576 | 0.020048 | -0.070804 | 0.027108 | 0.021483 | -0.12681 | -0.034506 | 0.070056 | -0.013378 | 0.049318 | 121.5072 | 121.6899 | 121.1564 | 121.323 | -121.5417 | -121.1909 | -121.5205 | -121.1698
1040.9844 | 121.8658 | -121.5591 | 0.07782 | 0.080646 | -0.08173 | -0.002842 | -0.084537 | 0.008797 | -0.005985 | -0.14512 | -0.048239 | 0.060902 | -0.022532 | 0.021847 | 121.4889 | 121.6762 | 121.1427 | 121.3184 | 0.094379 | -0.067997 | 0.010891 | -0.070804 | 0.02253 | 0.007748 | -0.13139 | -0.034506 | 0.074635 | -0.008799 | 0.03558 | 121.5026 | 121.6899 | 121.1564 | 121.3322 | -121.5371 | -121.1909 | -121.5114 | -121.1652
1042.7344 | 121.8658 | -121.582 | 0.09613 | 0.080646 | -0.086309 | -0.002842 | -0.084537 | 0.013375 | -0.001406 | -0.14055 | -0.048239 | 0.060902 | -0.017954 | 0.026427 | 121.4889 | 121.6853 | 121.1564 | 121.3138 | 0.094379 | -0.072576 | 0.010891 | -0.070804 | 0.027108 | 0.012327 | -0.12681 | -0.034506 | 0.074635 | -0.004221 | 0.04016 | 121.5026 | 121.6991 | 121.1702 | 121.3276 | -121.5371 | -121.2047 | -121.5068 | -121.1744
1044.4062 | 121.8842 | -121.5775 | 0.07782 | 0.06691 | -0.086309 | 0.001736 | -0.089116 | 0.013375 | 0.003172 | -0.14512 | -0.048239 | 0.060902 | -0.013376 | 0.026427 | 121.4843 | 121.6762 | 121.1564 | 121.3184 | 0.080643 | -0.072576 | 0.015469 | -0.075383 | 0.027108 | 0.016905 | -0.13139 | -0.034506 | 0.074635 | 0.000357 | 0.04016 | 121.498 | 121.6899 | 121.1702 | 121.3322 | -121.5325 | -121.2047 | -121.4977 | -121.1698
1046.1406 | 121.907 | -121.5546 | 0.082397 | 0.076067 | -0.086309 | -0.007421 | -0.089116 | 0.013375 | 0.00775 | -0.14055 | -0.048239 | 0.065481 | -0.017954 | 0.026427 | 121.4751 | 121.6716 | 121.1427 | 121.3047 | 0.0898 | -0.072576 | 0.006312 | -0.075383 | 0.027108 | 0.021483 | -0.12681 | -0.034506 | 0.079214 | -0.004221 | 0.04016 | 121.4889 | 121.6853 | 121.1564 | 121.3184 | -121.5234 | -121.1909 | -121.4931 | -121.1607
1047.8906 | 121.7697 | -121.6049 | 0.09613 | 0.076067 | -0.08173 | -0.002842 | -0.084537 | 0.013375 | 0.003172 | -0.13139 | -0.043661 | 0.060902 | -0.022532 | 0.017268 | 121.4843 | 121.6716 | 121.161 | 121.323 | 0.0898 | -0.067997 | 0.010891 | -0.070804 | 0.027108 | 0.016905 | -0.11766 | -0.029928 | 0.074635 | -0.008799 | 0.031001 | 121.498 | 121.6853 | 121.1748 | 121.3367 | -121.5279 | -121.2047 | -121.5068 | -121.1836
1049.625 | 121.8063 | -121.5912 | 0.10071 | 0.076067 | -0.077151 | -0.002842 | -0.079959 | 0.013375 | 0.003172 | -0.13597 | -0.052818 | 0.056323 | -0.022532 | 0.035585 | 121.4934 | 121.6716 | 121.1427 | 121.3184 | 0.0898 | -0.063418 | 0.010891 | -0.066226 | 0.027108 | 0.016905 | -0.12224 | -0.039085 | 0.070056 | -0.008799 | 0.049318 | 121.5072 | 121.6853 | 121.1564 | 121.3322 | -121.5463 | -121.1955 | -121.516 | -121.1652
1051.2969 | 121.8155 | -121.6049 | 0.11902 | 0.06691 | -0.08173 | -0.002842 | -0.084537 | 0.008797 | -0.001406 | -0.13597 | -0.052818 | 0.056323 | -0.027111 | 0.031006 | 121.4889 | 121.6716 | 121.161 | 121.3184 | 0.080643 | -0.067997 | 0.010891 | -0.070804 | 0.02253 | 0.012327 | -0.12224 | -0.039085 | 0.070056 | -0.013378 | 0.044739 | 121.5026 | 121.6853 | 121.1748 | 121.3322 | -121.5417 | -121.2138 | -121.516 | -121.1881
1053.0312 | 121.788 | -121.6049 | 0.11444 | 0.06691 | -0.090888 | -0.002842 | -0.089116 | 0.008797 | 0.003172 | -0.13597 | -0.057396 | 0.060902 | -0.013376 | 0.035585 | 121.4934 | 121.6716 | 121.161 | 121.3184 | 0.080643 | -0.077155 | 0.010891 | -0.075383 | 0.02253 | 0.016905 | -0.12224 | -0.043663 | 0.074635 | 0.000357 | 0.049318 | 121.5072 | 121.6853 | 121.1748 | 121.3322 | -121.5508 | -121.2184 | -121.5068 | -121.1744
1054.7812 | 121.8155 | -121.6095 | 0.082397 | 0.071489 | -0.086309 | -0.007421 | -0.079959 | 0.004219 | 0.016907 | -0.14055 | -0.048239 | 0.060902 | -0.022532 | 0.026427 | 121.4889 | 121.6762 | 121.1564 | 121.3184 | 0.085222 | -0.072576 | 0.006312 | -0.066226 | 0.017952 | 0.03064 | -0.12681 | -0.034506 | 0.074635 | -0.008799 | 0.04016 | 121.5026 | 121.6899 | 121.1702 | 121.3322 | -121.5371 | -121.2047 | -121.5114 | -121.179
1056.4531 | 121.7606 | -121.6141 | 0.10529 | 0.071489 | -0.086309 | -0.007421 | -0.089116 | 0.017953 | 0.012329 | -0.14055 | -0.043661 | 0.051744 | -0.013376 | 0.026427 | 121.4934 | 121.6716 | 121.161 | 121.3184 | 0.085222 | -0.072576 | 0.006312 | -0.075383 | 0.031686 | 0.026062 | -0.12681 | -0.029928 | 0.065477 | 0.000357 | 0.04016 | 121.5072 | 121.6853 | 121.1748 | 121.3322 | -121.5371 | -121.2047 | -121.5068 | -121.1744
1058.2031 | 121.8246 | -121.5912 | 0.11444 | 0.076067 | -0.086309 | -0.002842 | -0.079959 | 0.004219 | 0.00775 | -0.14055 | -0.048239 | 0.060902 | -0.013376 | 0.026427 | 121.4889 | 121.6807 | 121.1656 | 121.323 | 0.0898 | -0.072576 | 0.010891 | -0.066226 | 0.017952 | 0.021483 | -0.12681 | -0.034506 | 0.074635 | 0.000357 | 0.04016 | 121.5026 | 121.6945 | 121.1793 | 121.3367 | -121.5371 | -121.2138 | -121.5022 | -121.179
1059.9375 | 121.8246 | -121.5912 | 0.086975 | 0.06691 | -0.090888 | -0.012 | -0.093694 | -0.000359 | -0.001406 | -0.13597 | -0.043661 | 0.060902 | -0.017954 | 0.026427 | 121.498 | 121.6762 | 121.1656 | 121.323 | 0.080643 | -0.077155 | 0.001733 | -0.079961 | 0.013374 | 0.012327 | -0.12224 | -0.029928 | 0.074635 | -0.004221 | 0.04016 | 121.5117 | 121.6899 | 121.1793 | 121.3367 | -121.5417 | -121.2093 | -121.516 | -121.1836
1061.6719 | 121.7743 | -121.6324 | 0.11444 | 0.076067 | -0.086309 | -0.002842 | -0.084537 | 0.008797 | 0.003172 | -0.14055 | -0.039082 | 0.060902 | -0.013376 | 0.026427 | 121.498 | 121.6762 | 121.1748 | 121.323 | 0.0898 | -0.072576 | 0.010891 | -0.070804 | 0.02253 | 0.016905 | -0.12681 | -0.025349 | 0.074635 | 0.000357 | 0.04016 | 121.5117 | 121.6899 | 121.1885 | 121.3367 | -121.5371 | -121.2138 | -121.5114 | -121.1881
1063.3438 | 121.8933 | -121.5683 | 0.068665 | 0.080646 | -0.090888 | -0.007421 | -0.089116 | 0.013375 | -0.001406 | -0.14512 | -0.048239 | 0.07006 | -0.008798 | 0.035585 | 121.4934 | 121.6762 | 121.1656 | 121.3138 | 0.094379 | -0.077155 | 0.006312 | -0.075383 | 0.027108 | 0.012327 | -0.13139 | -0.034506 | 0.083793 | 0.004935 | 0.049318 | 121.5072 | 121.6899 | 121.1793 | 121.3276 | -121.5417 | -121.2138 | -121.5022 | -121.1744
1065.0781 | 121.8979 | -121.5683 | 0.082397 | 0.071489 | -0.090888 | -0.012 | -0.089116 | 0.008797 | -0.001406 | -0.14512 | -0.048239 | 0.051744 | -0.013376 | 0.026427 | 121.5026 | 121.6807 | 121.1335 | 121.3322 | 0.085222 | -0.077155 | 0.001733 | -0.075383 | 0.02253 | 0.012327 | -0.13139 | -0.034506 | 0.065477 | 0.000357 | 0.04016 | 121.5163 | 121.6945 | 121.1473 | 121.3459 | -121.5508 | -121.1818 | -121.516 | -121.1469
1066.8125 | 121.7972 | -121.6278 | 0.12817 | 0.076067 | -0.086309 | -0.012 | -0.089116 | -0.000359 | -0.005985 | -0.14055 | -0.052818 | 0.060902 | -0.017954 | 0.026427 | 121.4934 | 121.6807 | 121.1748 | 121.323 | 0.0898 | -0.072576 | 0.001733 | -0.075383 | 0.013374 | 0.007748 | -0.12681 | -0.039085 | 0.074635 | -0.004221 | 0.04016 | 121.5072 | 121.6945 | 121.1885 | 121.3367 | -121.5463 | -121.2276 | -121.5114 | -121.1927
1068.4844 | 121.7514 | -121.6049 | 0.10986 | 0.06691 | -0.095467 | -0.007421 | -0.098273 | 0.008797 | -0.001406 | -0.14055 | -0.057396 | 0.056323 | -0.013376 | 0.026427 | 121.4843 | 121.6762 | 121.1702 | 121.3276 | 0.080643 | -0.081734 | 0.006312 | -0.08454 | 0.02253 | 0.012327 | -0.12681 | -0.043663 | 0.070056 | 0.000357 | 0.04016 | 121.498 | 121.6899 | 121.1839 | 121.3413 | -121.5417 | -121.2276 | -121.4977 | -121.1836
1070.2188 | 121.9025 | -121.5775 | 0.064087 | 0.071489 | -0.090888 | -0.012 | -0.098273 | 0.004219 | -0.001406 | -0.14512 | -0.043661 | 0.065481 | -0.017954 | 0.026427 | 121.498 | 121.6853 | 121.1702 | 121.323 | 0.085222 | -0.077155 | 0.001733 | -0.08454 | 0.017952 | 0.012327 | -0.13139 | -0.029928 | 0.079214 | -0.004221 | 0.04016 | 121.5117 | 121.6991 | 121.1839 | 121.3367 | -121.5417 | -121.2138 | -121.516 | -121.1881
1071.9531 | 121.8933 | -121.5958 | 0.082397 | 0.076067 | -0.095467 | -0.016578 | -0.084537 | -0.000359 | -0.001406 | -0.14055 | -0.043661 | 0.065481 | -0.017954 | 0.031006 | 121.498 | 121.6807 | 121.1656 | 121.323 | 0.0898 | -0.081734 | -0.002845 | -0.070804 | 0.013374 | 0.012327 | -0.12681 | -0.029928 | 0.079214 | -0.004221 | 0.044739 | 121.5117 | 121.6945 | 121.1793 | 121.3367 | -121.5417 | -121.2093 | -121.516 | -121.1836
1073.6875 | 121.9208 | -121.5683 | 0.091553 | 0.071489 | -0.095467 | -0.007421 | -0.093694 | 0.004219 | -0.005985 | -0.1497 | -0.048239 | 0.060902 | -0.017954 | 0.021847 | 121.4934 | 121.6762 | 121.1748 | 121.323 | 0.085222 | -0.081734 | 0.006312 | -0.079961 | 0.017952 | 0.007748 | -0.13597 | -0.034506 | 0.074635 | -0.004221 | 0.03558 | 121.5072 | 121.6899 | 121.1885 | 121.3367 | -121.5417 | -121.223 | -121.5114 | -121.1927
1075.3594 | 121.8704 | -121.5775 | 0.10529 | 0.071489 | -0.090888 | -0.016578 | -0.098273 | 0.004219 | -0.005985 | -0.1497 | -0.048239 | 0.056323 | -0.013376 | 0.031006 | 121.4934 | 121.6807 | 121.1839 | 121.323 | 0.085222 | -0.077155 | -0.002845 | -0.08454 | 0.017952 | 0.007748 | -0.13597 | -0.034506 | 0.070056 | 0.000357 | 0.044739 | 121.5072 | 121.6945 | 121.1976 | 121.3367 | -121.5417 | -121.2322 | -121.5068 | -121.1973
1077.0938 | 121.8613 | -121.6049 | 0.09613 | 0.071489 | -0.095467 | -0.012 | -0.093694 | -0.004937 | -0.005985 | -0.14512 | -0.048239 | 0.060902 | -0.017954 | 0.021847 | 121.4889 | 121.6762 | 121.1748 | 121.3276 | 0.085222 | -0.081734 | 0.001733 | -0.079961 | 0.008796 | 0.007748 | -0.13139 | -0.034506 | 0.074635 | -0.004221 | 0.03558 | 121.5026 | 121.6899 | 121.1885 | 121.3413 | -121.5371 | -121.223 | -121.5068 | -121.1927
1078.7656 | 121.7834 | -121.6324 | 0.10071 | 0.076067 | -0.090888 | -0.012 | -0.098273 | 0.004219 | -0.005985 | -0.1497 | -0.043661 | 0.065481 | -0.013376 | 0.026427 | 121.4934 | 121.6762 | 121.1793 | 121.3322 | 0.0898 | -0.077155 | 0.001733 | -0.08454 | 0.017952 | 0.007748 | -0.13597 | -0.029928 | 0.079214 | 0.000357 | 0.04016 | 121.5072 | 121.6899 | 121.1931 | 121.3459 | -121.5371 | -121.223 | -121.5068 | -121.1927
1080.5 | 121.875 | -121.6003 | 0.09613 | 0.071489 | -0.090888 | -0.012 | -0.089116 | -0.000359 | -0.010563 | -0.1497 | -0.048239 | 0.065481 | -0.013376 | 0.017268 | 121.5026 | 121.6945 | 121.1656 | 121.3276 | 0.085222 | -0.077155 | 0.001733 | -0.075383 | 0.013374 | 0.00317 | -0.13597 | -0.034506 | 0.079214 | 0.000357 | 0.031001 | 121.5163 | 121.7082 | 121.1793 | 121.3413 | -121.5508 | -121.2138 | -121.516 | -121.179
1082.25 | 121.8658 | -121.582 | 0.086975 | 0.071489 | -0.095467 | -0.012 | -0.089116 | -0.004937 | -0.010563 | -0.13597 | -0.052818 | 0.065481 | -0.013376 | 0.026427 | 121.498 | 121.6762 | 121.1702 | 121.3184 | 0.085222 | -0.081734 | 0.001733 | -0.075383 | 0.008796 | 0.00317 | -0.12224 | -0.039085 | 0.079214 | 0.000357 | 0.04016 | 121.5117 | 121.6899 | 121.1839 | 121.3322 | -121.5508 | -121.223 | -121.5114 | -121.1836
1083.9375 | 121.7834 | -121.6232 | 0.09613 | 0.076067 | -0.090888 | -0.016578 | -0.093694 | 0.004219 | -0.005985 | -0.1497 | -0.039082 | 0.065481 | -0.013376 | 0.031006 | 121.5026 | 121.6899 | 121.1748 | 121.323 | 0.0898 | -0.077155 | -0.002845 | -0.079961 | 0.017952 | 0.007748 | -0.13597 | -0.025349 | 0.079214 | 0.000357 | 0.044739 | 121.5163 | 121.7036 | 121.1885 | 121.3367 | -121.5417 | -121.2138 | -121.516 | -121.1881
1085.6875 | 121.8704 | -121.5866 | 0.082397 | 0.076067 | -0.095467 | -0.012 | -0.089116 | -0.000359 | -0.001406 | -0.1497 | -0.048239 | 0.065481 | -0.017954 | 0.031006 | 121.5026 | 121.6899 | 121.1839 | 121.3276 | 0.0898 | -0.081734 | 0.001733 | -0.075383 | 0.013374 | 0.012327 | -0.13597 | -0.034506 | 0.079214 | -0.004221 | 0.044739 | 121.5163 | 121.7036 | 121.1976 | 121.3413 | -121.5508 | -121.2322 | -121.5205 | -121.2019
1087.4219 | 121.9345 | -121.5958 | 0.068665 | 0.076067 | -0.10004 | -0.016578 | -0.089116 | -0.000359 | -0.010563 | -0.1497 | -0.043661 | 0.07006 | -0.017954 | 0.026427 | 121.498 | 121.6899 | 121.1748 | 121.323 | 0.0898 | -0.086312 | -0.002845 | -0.075383 | 0.013374 | 0.00317 | -0.13597 | -0.029928 | 0.083793 | -0.004221 | 0.04016 | 121.5117 | 121.7036 | 121.1885 | 121.3367 | -121.5417 | -121.2184 | -121.516 | -121.1927
1089.1562 | 121.8384 | -121.6003 | 0.11902 | 0.080646 | -0.086309 | -0.016578 | -0.093694 | -0.000359 | -0.005985 | -0.15428 | -0.039082 | 0.060902 | -0.008798 | 0.035585 | 121.5026 | 121.6807 | 121.1748 | 121.3322 | 0.094379 | -0.072576 | -0.002845 | -0.079961 | 0.013374 | 0.007748 | -0.14055 | -0.025349 | 0.074635 | 0.004935 | 0.049318 | 121.5163 | 121.6945 | 121.1885 | 121.3459 | -121.5417 | -121.2138 | -121.5114 | -121.1836
1090.8906 | 121.9208 | -121.5866 | 0.086975 | 0.071489 | -0.10004 | -0.021157 | -0.084537 | -0.000359 | -0.010563 | -0.1497 | -0.043661 | 0.056323 | -0.013376 | 0.021847 | 121.5026 | 121.6853 | 121.1793 | 121.3276 | 0.085222 | -0.086312 | -0.007424 | -0.070804 | 0.013374 | 0.00317 | -0.13597 | -0.029928 | 0.070056 | 0.000357 | 0.03558 | 121.5163 | 121.6991 | 121.1931 | 121.3413 | -121.5463 | -121.223 | -121.516 | -121.1927
1092.5781 | 121.7926 | -121.637 | 0.10529 | 0.080646 | -0.086309 | -0.012 | -0.089116 | -0.004937 | -0.005985 | -0.1497 | -0.043661 | 0.060902 | -0.017954 | 0.031006 | 121.498 | 121.6899 | 121.1839 | 121.3276 | 0.094379 | -0.072576 | 0.001733 | -0.075383 | 0.008796 | 0.007748 | -0.13597 | -0.029928 | 0.074635 | -0.004221 | 0.044739 | 121.5117 | 121.7036 | 121.1976 | 121.3413 | -121.5417 | -121.2276 | -121.516 | -121.2019
1094.3125 | 121.8704 | -121.6095 | 0.091553 | 0.071489 | -0.095467 | -0.012 | -0.098273 | -0.004937 | -0.010563 | -0.1497 | -0.043661 | 0.065481 | -0.013376 | 0.031006 | 121.498 | 121.6899 | 121.1839 | 121.3367 | 0.085222 | -0.081734 | 0.001733 | -0.08454 | 0.008796 | 0.00317 | -0.13597 | -0.029928 | 0.079214 | 0.000357 | 0.044739 | 121.5117 | 121.7036 | 121.1976 | 121.3505 | -121.5417 | -121.2276 | -121.5114 | -121.1973
1095.9844 | 121.8018 | -121.6232 | 0.10986 | 0.076067 | -0.095467 | -0.016578 | -0.089116 | -0.000359 | -0.005985 | -0.14512 | -0.043661 | 0.060902 | -0.017954 | 0.031006 | 121.5026 | 121.6945 | 121.1793 | 121.3276 | 0.0898 | -0.081734 | -0.002845 | -0.075383 | 0.013374 | 0.007748 | -0.13139 | -0.029928 | 0.074635 | -0.004221 | 0.044739 | 121.5163 | 121.7082 | 121.1931 | 121.3413 | -121.5463 | -121.223 | -121.5205 | -121.1973
1097.7344 | 121.7651 | -121.6415 | 0.10986 | 0.076067 | -0.095467 | -0.021157 | -0.093694 | -0.000359 | -0.010563 | -0.1497 | -0.048239 | 0.060902 | -0.008798 | 0.031006 | 121.5026 | 121.6853 | 121.1748 | 121.3367 | 0.0898 | -0.081734 | -0.007424 | -0.079961 | 0.013374 | 0.00317 | -0.13597 | -0.034506 | 0.074635 | 0.004935 | 0.044739 | 121.5163 | 121.6991 | 121.1885 | 121.3505 | -121.5508 | -121.223 | -121.5114 | -121.1836
1099.4844 | 121.788 | -121.6187 | 0.11902 | 0.080646 | -0.10004 | -0.021157 | -0.093694 | -0.000359 | -0.005985 | -0.1497 | -0.048239 | 0.07006 | -0.013376 | 0.031006 | 121.5026 | 121.6899 | 121.1793 | 121.3276 | 0.094379 | -0.086312 | -0.007424 | -0.079961 | 0.013374 | 0.007748 | -0.13597 | -0.034506 | 0.083793 | 0.000357 | 0.044739 | 121.5163 | 121.7036 | 121.1931 | 121.3413 | -121.5508 | -121.2276 | -121.516 | -121.1927
1101.1562 | 121.788 | -121.6232 | 0.11902 | 0.080646 | -0.095467 | -0.021157 | -0.089116 | -0.000359 | -0.010563 | -0.15428 | -0.043661 | 0.065481 | -0.017954 | 0.035585 | 121.498 | 121.6853 | 121.1885 | 121.3322 | 0.094379 | -0.081734 | -0.007424 | -0.075383 | 0.013374 | 0.00317 | -0.14055 | -0.029928 | 0.079214 | -0.004221 | 0.049318 | 121.5117 | 121.6991 | 121.2022 | 121.3459 | -121.5417 | -121.2322 | -121.516 | -121.2064
1102.8906 | 121.8658 | -121.6003 | 0.091553 | 0.071489 | -0.10462 | -0.021157 | -0.098273 | -0.000359 | -0.015142 | -0.1497 | -0.043661 | 0.056323 | -0.013376 | 0.031006 | 121.498 | 121.6945 | 121.1793 | 121.3322 | 0.085222 | -0.090891 | -0.007424 | -0.08454 | 0.013374 | -0.001409 | -0.13597 | -0.029928 | 0.070056 | 0.000357 | 0.044739 | 121.5117 | 121.7082 | 121.1931 | 121.3459 | -121.5417 | -121.223 | -121.5114 | -121.1927
1104.6406 | 121.8109 | -121.6187 | 0.11902 | 0.080646 | -0.10462 | -0.021157 | -0.098273 | -0.009515 | -0.010563 | -0.14512 | -0.043661 | 0.056323 | -0.013376 | 0.031006 | 121.5072 | 121.6899 | 121.1931 | 121.3322 | 0.094379 | -0.090891 | -0.007424 | -0.08454 | 0.004218 | 0.00317 | -0.13139 | -0.029928 | 0.070056 | 0.000357 | 0.044739 | 121.5209 | 121.7036 | 121.2068 | 121.3459 | -121.5508 | -121.2367 | -121.5205 | -121.2064
1106.375 | 121.7972 | -121.6003 | 0.11444 | 0.06691 | -0.10462 | -0.021157 | -0.098273 | -0.004937 | -0.010563 | -0.15428 | -0.043661 | 0.060902 | -0.017954 | 0.021847 | 121.5026 | 121.6945 | 121.1885 | 121.3322 | 0.080643 | -0.090891 | -0.007424 | -0.08454 | 0.008796 | 0.00317 | -0.14055 | -0.029928 | 0.074635 | -0.004221 | 0.03558 | 121.5163 | 121.7082 | 121.2022 | 121.3459 | -121.5463 | -121.2322 | -121.5205 | -121.2064
1108.1094 | 121.7743 | -121.6461 | 0.1236 | 0.076067 | -0.10462 | -0.016578 | -0.10285 | -0.014093 | -0.015142 | -0.15428 | -0.043661 | 0.060902 | -0.013376 | 0.026427 | 121.5117 | 121.6991 | 121.1885 | 121.3367 | 0.0898 | -0.090891 | -0.002845 | -0.089118 | -0.00036 | -0.001409 | -0.14055 | -0.029928 | 0.074635 | 0.000357 | 0.04016 | 121.5255 | 121.7128 | 121.2022 | 121.3505 | -121.5554 | -121.2322 | -121.5251 | -121.2019
1109.7969 | 121.9254 | -121.5637 | 0.073242 | 0.076067 | -0.1092 | -0.016578 | -0.098273 | -0.000359 | -0.005985 | -0.1497 | -0.048239 | 0.060902 | -0.004219 | 0.026427 | 121.5026 | 121.6899 | 121.1885 | 121.3276 | 0.0898 | -0.09547 | -0.002845 | -0.08454 | 0.013374 | 0.007748 | -0.13597 | -0.034506 | 0.074635 | 0.009514 | 0.04016 | 121.5163 | 121.7036 | 121.2022 | 121.3413 | -121.5508 | -121.2367 | -121.5068 | -121.1927
1111.5312 | 121.7789 | -121.6415 | 0.1236 | 0.076067 | -0.11378 | -0.016578 | -0.093694 | -0.009515 | -0.01972 | -0.1497 | -0.043661 | 0.065481 | -0.017954 | 0.026427 | 121.5026 | 121.6991 | 121.1793 | 121.3367 | 0.0898 | -0.10005 | -0.002845 | -0.079961 | 0.004218 | -0.005987 | -0.13597 | -0.029928 | 0.079214 | -0.004221 | 0.04016 | 121.5163 | 121.7128 | 121.1931 | 121.3505 | -121.5463 | -121.223 | -121.5205 | -121.1973
1113.2656 | 121.9391 | -121.5866 | 0.086975 | 0.076067 | -0.10462 | -0.025735 | -0.10285 | -0.009515 | -0.015142 | -0.1497 | -0.043661 | 0.060902 | -0.008798 | 0.031006 | 121.5117 | 121.6991 | 121.1885 | 121.3322 | 0.0898 | -0.090891 | -0.012002 | -0.089118 | 0.004218 | -0.001409 | -0.13597 | -0.029928 | 0.074635 | 0.004935 | 0.044739 | 121.5255 | 121.7128 | 121.2022 | 121.3459 | -121.5554 | -121.2322 | -121.5205 | -121.1973
1114.9531 | 121.7926 | -121.6141 | 0.11902 | 0.080646 | -0.10462 | -0.021157 | -0.10743 | -0.000359 | -0.010563 | -0.1497 | -0.043661 | 0.065481 | -0.017954 | 0.026427 | 121.5072 | 121.7036 | 121.1885 | 121.3322 | 0.094379 | -0.090891 | -0.007424 | -0.093697 | 0.013374 | 0.00317 | -0.13597 | -0.029928 | 0.079214 | -0.004221 | 0.04016 | 121.5209 | 121.7174 | 121.2022 | 121.3459 | -121.5508 | -121.2322 | -121.5251 | -121.2064
1116.6875 | 121.9437 | -121.6003 | 0.091553 | 0.071489 | -0.11378 | -0.021157 | -0.10743 | -0.009515 | -0.01972 | -0.15428 | -0.043661 | 0.065481 | -0.008798 | 0.035585 | 121.5163 | 121.6991 | 121.1885 | 121.3367 | 0.085222 | -0.10005 | -0.007424 | -0.093697 | 0.004218 | -0.005987 | -0.14055 | -0.029928 | 0.079214 | 0.004935 | 0.049318 | 121.5301 | 121.7128 | 121.2022 | 121.3505 | -121.56 | -121.2322 | -121.5251 | -121.1973
1118.4375 | 121.9162 | -121.6095 | 0.086975 | 0.071489 | -0.10462 | -0.030314 | -0.098273 | -0.009515 | -0.024298 | -0.1497 | -0.048239 | 0.060902 | -0.008798 | 0.026427 | 121.5117 | 121.7036 | 121.1885 | 121.3367 | 0.085222 | -0.090891 | -0.016581 | -0.08454 | 0.004218 | -0.010565 | -0.13597 | -0.034506 | 0.074635 | 0.004935 | 0.04016 | 121.5255 | 121.7174 | 121.2022 | 121.3505 | -121.56 | -121.2367 | -121.5205 | -121.1973
1120.1719 | 121.8613 | -121.5866 | 0.086975 | 0.076067 | -0.11378 | -0.021157 | -0.098273 | -0.004937 | -0.01972 | -0.15886 | -0.048239 | 0.060902 | -0.008798 | 0.026427 | 121.5117 | 121.7082 | 121.1839 | 121.3459 | 0.0898 | -0.10005 | -0.007424 | -0.08454 | 0.008796 | -0.005987 | -0.14513 | -0.034506 | 0.074635 | 0.004935 | 0.04016 | 121.5255 | 121.7219 | 121.1976 | 121.3596 | -121.56 | -121.2322 | -121.5205 | -121.1927
1121.8438 | 121.8704 | -121.6141 | 0.086975 | 0.071489 | -0.10462 | -0.021157 | -0.10285 | -0.009515 | -0.01972 | -0.15428 | -0.048239 | 0.060902 | -0.017954 | 0.031006 | 121.5117 | 121.6991 | 121.1839 | 121.3505 | 0.085222 | -0.090891 | -0.007424 | -0.089118 | 0.004218 | -0.005987 | -0.14055 | -0.034506 | 0.074635 | -0.004221 | 0.044739 | 121.5255 | 121.7128 | 121.1976 | 121.3642 | -121.56 | -121.2322 | -121.5297 | -121.2019
1123.5781 | 121.8704 | -121.5958 | 0.10529 | 0.076067 | -0.11378 | -0.030314 | -0.098273 | -0.009515 | -0.015142 | -0.15428 | -0.039082 | 0.056323 | -0.008798 | 0.031006 | 121.5163 | 121.7036 | 121.1839 | 121.3367 | 0.0898 | -0.10005 | -0.016581 | -0.08454 | 0.004218 | -0.001409 | -0.14055 | -0.025349 | 0.070056 | 0.004935 | 0.044739 | 121.5301 | 121.7174 | 121.1976 | 121.3505 | -121.5554 | -121.223 | -121.5251 | -121.1927
1125.3125 | 121.8979 | -121.6141 | 0.086975 | 0.076067 | -0.11378 | -0.025735 | -0.098273 | -0.009515 | -0.01972 | -0.17259 | -0.043661 | 0.065481 | -0.013376 | 0.026427 | 121.5163 | 121.7082 | 121.1839 | 121.3367 | 0.0898 | -0.10005 | -0.012002 | -0.08454 | 0.004218 | -0.005987 | -0.15886 | -0.029928 | 0.079214 | 0.000357 | 0.04016 | 121.5301 | 121.7219 | 121.1976 | 121.3505 | -121.56 | -121.2276 | -121.5297 | -121.1973
1126.9844 | 121.8658 | -121.6049 | 0.073242 | 0.076067 | -0.11378 | -0.025735 | -0.10285 | -0.009515 | -0.015142 | -0.1497 | -0.048239 | 0.060902 | -0.013376 | 0.031006 | 121.5117 | 121.7036 | 121.1931 | 121.3322 | 0.0898 | -0.10005 | -0.012002 | -0.089118 | 0.004218 | -0.001409 | -0.13597 | -0.034506 | 0.074635 | 0.000357 | 0.044739 | 121.5255 | 121.7174 | 121.2068 | 121.3459 | -121.56 | -121.2413 | -121.5251 | -121.2064
1128.7344 | 121.9116 | -121.6141 | 0.07782 | 0.06691 | -0.1092 | -0.025735 | -0.10743 | -0.009515 | -0.01972 | -0.15428 | -0.043661 | 0.065481 | -0.008798 | 0.031006 | 121.5117 | 121.7036 | 121.1839 | 121.3367 | 0.080643 | -0.09547 | -0.012002 | -0.093697 | 0.004218 | -0.005987 | -0.14055 | -0.029928 | 0.079214 | 0.004935 | 0.044739 | 121.5255 | 121.7174 | 121.1976 | 121.3505 | -121.5554 | -121.2276 | -121.5205 | -121.1927
1130.4688 | 121.9345 | -121.582 | 0.082397 | 0.076067 | -0.11378 | -0.030314 | -0.10285 | -0.018671 | -0.010563 | -0.15886 | -0.043661 | 0.060902 | -0.013376 | 0.031006 | 121.5209 | 121.7036 | 121.1839 | 121.3459 | 0.0898 | -0.10005 | -0.016581 | -0.089118 | -0.004938 | 0.00317 | -0.14513 | -0.029928 | 0.074635 | 0.000357 | 0.044739 | 121.5346 | 121.7174 | 121.1976 | 121.3596 | -121.5646 | -121.2276 | -121.5343 | -121.1973
1132.2188 | 121.8842 | -121.582 | 0.07782 | 0.076067 | -0.11836 | -0.025735 | -0.10743 | -0.014093 | -0.015142 | -0.15886 | -0.043661 | 0.065481 | -0.013376 | 0.031006 | 121.5117 | 121.7036 | 121.1931 | 121.3367 | 0.0898 | -0.10463 | -0.012002 | -0.093697 | -0.00036 | -0.001409 | -0.14513 | -0.029928 | 0.079214 | 0.000357 | 0.044739 | 121.5255 | 121.7174 | 121.2068 | 121.3505 | -121.5554 | -121.2367 | -121.5251 | -121.2064
1133.9062 | 121.7972 | -121.6187 | 0.11444 | 0.071489 | -0.11378 | -0.030314 | -0.10743 | -0.014093 | -0.01972 | -0.1497 | -0.039082 | 0.07006 | -0.017954 | 0.031006 | 121.5163 | 121.6991 | 121.1931 | 121.3413 | 0.085222 | -0.10005 | -0.016581 | -0.093697 | -0.00036 | -0.005987 | -0.13597 | -0.025349 | 0.083793 | -0.004221 | 0.044739 | 121.5301 | 121.7128 | 121.2068 | 121.355 | -121.5554 | -121.2322 | -121.5343 | -121.211
1135.6406 | 121.9208 | -121.5866 | 0.07782 | 0.071489 | -0.11836 | -0.030314 | -0.10285 | -0.014093 | -0.01972 | -0.15428 | -0.043661 | 0.065481 | -0.013376 | 0.026427 | 121.5209 | 121.7036 | 121.2022 | 121.3505 | 0.085222 | -0.10463 | -0.016581 | -0.089118 | -0.00036 | -0.005987 | -0.14055 | -0.029928 | 0.079214 | 0.000357 | 0.04016 | 121.5346 | 121.7174 | 121.216 | 121.3642 | -121.5646 | -121.2459 | -121.5343 | -121.2156
1137.3125 | 121.8887 | -121.6187 | 0.09613 | 0.076067 | -0.1092 | -0.030314 | -0.11201 | -0.014093 | -0.01972 | -0.15428 | -0.039082 | 0.065481 | -0.013376 | 0.026427 | 121.5163 | 121.7128 | 121.1976 | 121.3459 | 0.0898 | -0.09547 | -0.016581 | -0.098275 | -0.00036 | -0.005987 | -0.14055 | -0.025349 | 0.079214 | 0.000357 | 0.04016 | 121.5301 | 121.7265 | 121.2114 | 121.3596 | -121.5554 | -121.2367 | -121.5297 | -121.211
1138.9844 | 121.8979 | -121.6141 | 0.09613 | 0.076067 | -0.11378 | -0.034893 | -0.10743 | -0.009515 | -0.024298 | -0.16801 | -0.039082 | 0.060902 | -0.017954 | 0.035585 | 121.5163 | 121.6991 | 121.1976 | 121.3459 | 0.0898 | -0.10005 | -0.02116 | -0.093697 | 0.004218 | -0.010565 | -0.15428 | -0.025349 | 0.074635 | -0.004221 | 0.049318 | 121.5301 | 121.7128 | 121.2114 | 121.3596 | -121.5554 | -121.2367 | -121.5343 | -121.2156
1140.7188 | 121.8292 | -121.6553 | 0.10529 | 0.076067 | -0.11378 | -0.030314 | -0.10743 | -0.018671 | -0.024298 | -0.15886 | -0.052818 | 0.056323 | -0.017954 | 0.035585 | 121.5072 | 121.7082 | 121.1885 | 121.3413 | 0.0898 | -0.10005 | -0.016581 | -0.093697 | -0.004938 | -0.010565 | -0.14513 | -0.039085 | 0.070056 | -0.004221 | 0.049318 | 121.5209 | 121.7219 | 121.2022 | 121.355 | -121.56 | -121.2413 | -121.5251 | -121.2064
1142.4531 | 121.8155 | -121.6644 | 0.10071 | 0.06691 | -0.11378 | -0.034893 | -0.11201 | -0.018671 | -0.015142 | -0.16344 | -0.048239 | 0.07006 | -0.008798 | 0.026427 | 121.5163 | 121.7036 | 121.1748 | 121.3459 | 0.080643 | -0.10005 | -0.02116 | -0.098275 | -0.004938 | -0.001409 | -0.1497 | -0.034506 | 0.083793 | 0.004935 | 0.04016 | 121.5301 | 121.7174 | 121.1885 | 121.3596 | -121.5646 | -121.223 | -121.5251 | -121.1836
1144.1875 | 121.8567 | -121.6187 | 0.073242 | 0.071489 | -0.11378 | -0.030314 | -0.10743 | -0.009515 | -0.024298 | -0.15886 | -0.039082 | 0.060902 | -0.013376 | 0.031006 | 121.5117 | 121.6991 | 121.2022 | 121.3459 | 0.085222 | -0.10005 | -0.016581 | -0.093697 | 0.004218 | -0.010565 | -0.14513 | -0.025349 | 0.074635 | 0.000357 | 0.044739 | 121.5255 | 121.7128 | 121.216 | 121.3596 | -121.5508 | -121.2413 | -121.5251 | -121.2156
1145.8594 | 121.8613 | -121.6141 | 0.091553 | 0.076067 | -0.11378 | -0.034893 | -0.10285 | -0.018671 | -0.015142 | -0.16344 | -0.048239 | 0.074638 | -0.017954 | 0.026427 | 121.5072 | 121.7036 | 121.1976 | 121.3413 | 0.0898 | -0.10005 | -0.02116 | -0.089118 | -0.004938 | -0.001409 | -0.1497 | -0.034506 | 0.088371 | -0.004221 | 0.04016 | 121.5209 | 121.7174 | 121.2114 | 121.355 | -121.5554 | -121.2459 | -121.5251 | -121.2156
1147.5938 | 121.9254 | -121.5958 | 0.086975 | 0.071489 | -0.1092 | -0.030314 | -0.11201 | -0.018671 | -0.028877 | -0.15886 | -0.034504 | 0.065481 | -0.013376 | 0.031006 | 121.5209 | 121.7128 | 121.2022 | 121.355 | 0.085222 | -0.09547 | -0.016581 | -0.098275 | -0.004938 | -0.015144 | -0.14513 | -0.020771 | 0.079214 | 0.000357 | 0.044739 | 121.5346 | 121.7265 | 121.216 | 121.3688 | -121.5554 | -121.2367 | -121.5343 | -121.2156
1149.3281 | 121.9437 | -121.5958 | 0.086975 | 0.080646 | -0.11836 | -0.039471 | -0.11201 | -0.014093 | -0.028877 | -0.15886 | -0.039082 | 0.07006 | -0.013376 | 0.031006 | 121.5255 | 121.7082 | 121.1931 | 121.3505 | 0.094379 | -0.10463 | -0.025738 | -0.098275 | -0.00036 | -0.015144 | -0.14513 | -0.025349 | 0.083793 | 0.000357 | 0.044739 | 121.5392 | 121.7219 | 121.2068 | 121.3642 | -121.5646 | -121.2322 | -121.5389 | -121.2064
1151.0625 | 121.8613 | -121.6187 | 0.10071 | 0.071489 | -0.12294 | -0.039471 | -0.11201 | -0.018671 | -0.01972 | -0.16344 | -0.048239 | 0.060902 | -0.004219 | 0.035585 | 121.5255 | 121.7128 | 121.2068 | 121.355 | 0.085222 | -0.10921 | -0.025738 | -0.098275 | -0.004938 | -0.005987 | -0.1497 | -0.034506 | 0.074635 | 0.009514 | 0.049318 | 121.5392 | 121.7265 | 121.2205 | 121.3688 | -121.5737 | -121.255 | -121.5297 | -121.211
1152.8125 | 121.843 | -121.637 | 0.11444 | 0.071489 | -0.1092 | -0.034893 | -0.11201 | -0.009515 | -0.033455 | -0.16344 | -0.052818 | 0.060902 | -0.008798 | 0.031006 | 121.5117 | 121.7174 | 121.2068 | 121.3459 | 0.085222 | -0.09547 | -0.02116 | -0.098275 | 0.004218 | -0.019722 | -0.1497 | -0.039085 | 0.074635 | 0.004935 | 0.044739 | 121.5255 | 121.7311 | 121.2205 | 121.3596 | -121.5646 | -121.2596 | -121.5205 | -121.2156
1154.5 | 121.8796 | -121.6187 | 0.091553 | 0.071489 | -0.11378 | -0.039471 | -0.11201 | -0.014093 | -0.01972 | -0.15886 | -0.039082 | 0.065481 | -0.017954 | 0.044743 | 121.5163 | 121.7082 | 121.1931 | 121.3505 | 0.085222 | -0.10005 | -0.025738 | -0.098275 | -0.00036 | -0.005987 | -0.14513 | -0.025349 | 0.079214 | -0.004221 | 0.058476 | 121.5301 | 121.7219 | 121.2068 | 121.3642 | -121.5554 | -121.2322 | -121.5343 | -121.211
1156.2344 | 121.8018 | -121.6324 | 0.10986 | 0.071489 | -0.1092 | -0.030314 | -0.12116 | -0.018671 | -0.024298 | -0.15886 | -0.043661 | 0.065481 | -0.013376 | 0.035585 | 121.5163 | 121.7082 | 121.2022 | 121.3459 | 0.085222 | -0.09547 | -0.016581 | -0.10743 | -0.004938 | -0.010565 | -0.14513 | -0.029928 | 0.079214 | 0.000357 | 0.049318 | 121.5301 | 121.7219 | 121.216 | 121.3596 | -121.56 | -121.2459 | -121.5297 | -121.2156
1157.9688 | 121.8887 | -121.6095 | 0.09613 | 0.071489 | -0.1092 | -0.030314 | -0.11201 | -0.018671 | -0.028877 | -0.16801 | -0.043661 | 0.065481 | -0.008798 | 0.031006 | 121.5209 | 121.7174 | 121.2022 | 121.3413 | 0.085222 | -0.09547 | -0.016581 | -0.098275 | -0.004938 | -0.015144 | -0.15428 | -0.029928 | 0.079214 | 0.004935 | 0.044739 | 121.5346 | 121.7311 | 121.216 | 121.355 | -121.5646 | -121.2459 | -121.5297 | -121.211
1159.7344 | 121.8796 | -121.6187 | 0.09613 | 0.071489 | -0.11378 | -0.034893 | -0.10743 | -0.023249 | -0.024298 | -0.16801 | -0.034504 | 0.07006 | -0.008798 | 0.035585 | 121.5209 | 121.7128 | 121.1976 | 121.3505 | 0.085222 | -0.10005 | -0.02116 | -0.093697 | -0.009516 | -0.010565 | -0.15428 | -0.020771 | 0.083793 | 0.004935 | 0.049318 | 121.5346 | 121.7265 | 121.2114 | 121.3642 | -121.5554 | -121.2322 | -121.5297 | -121.2064
1161.4219 | 121.9162 | -121.5912 | 0.068665 | 0.06691 | -0.11378 | -0.034893 | -0.11201 | -0.018671 | -0.024298 | -0.16344 | -0.043661 | 0.065481 | -0.008798 | 0.035585 | 121.5255 | 121.7174 | 121.2068 | 121.3505 | 0.080643 | -0.10005 | -0.02116 | -0.098275 | -0.004938 | -0.010565 | -0.1497 | -0.029928 | 0.079214 | 0.004935 | 0.049318 | 121.5392 | 121.7311 | 121.2205 | 121.3642 | -121.5691 | -121.2505 | -121.5343 | -121.2156
1163.1562 | 121.9345 | -121.6141 | 0.082397 | 0.071489 | -0.11836 | -0.034893 | -0.11201 | -0.023249 | -0.033455 | -0.16344 | -0.039082 | 0.065481 | -0.008798 | 0.031006 | 121.5209 | 121.7036 | 121.2022 | 121.3505 | 0.085222 | -0.10463 | -0.02116 | -0.098275 | -0.009516 | -0.019722 | -0.1497 | -0.025349 | 0.079214 | 0.004935 | 0.044739 | 121.5346 | 121.7174 | 121.216 | 121.3642 | -121.56 | -121.2413 | -121.5297 | -121.211
1164.9062 | 121.9162 | -121.6049 | 0.091553 | 0.071489 | -0.12294 | -0.039471 | -0.11659 | -0.009515 | -0.038034 | -0.16801 | -0.039082 | 0.060902 | -0.008798 | 0.035585 | 121.5209 | 121.7174 | 121.1931 | 121.3505 | 0.085222 | -0.10921 | -0.025738 | -0.10285 | 0.004218 | -0.024301 | -0.15428 | -0.025349 | 0.074635 | 0.004935 | 0.049318 | 121.5346 | 121.7311 | 121.2068 | 121.3642 | -121.56 | -121.2322 | -121.5297 | -121.2019
1166.5781 | 121.8475 | -121.6232 | 0.09613 | 0.071489 | -0.11836 | -0.04405 | -0.11659 | -0.018671 | -0.033455 | -0.16801 | -0.048239 | 0.060902 | -0.022532 | 0.026427 | 121.5209 | 121.7128 | 121.2022 | 121.3505 | 0.085222 | -0.10463 | -0.030317 | -0.10285 | -0.004938 | -0.019722 | -0.15428 | -0.034506 | 0.074635 | -0.008799 | 0.04016 | 121.5346 | 121.7265 | 121.216 | 121.3642 | -121.5691 | -121.2505 | -121.5434 | -121.2248
1168.2969 | 121.9391 | -121.5958 | 0.073242 | 0.071489 | -0.11836 | -0.04405 | -0.12116 | -0.018671 | -0.028877 | -0.17259 | -0.043661 | 0.07006 | -0.004219 | 0.035585 | 121.5163 | 121.7082 | 121.1885 | 121.355 | 0.085222 | -0.10463 | -0.030317 | -0.10743 | -0.004938 | -0.015144 | -0.15886 | -0.029928 | 0.083793 | 0.009514 | 0.049318 | 121.5301 | 121.7219 | 121.2022 | 121.3688 | -121.56 | -121.2322 | -121.5205 | -121.1927
1170.0469 | 121.8018 | -121.6507 | 0.13275 | 0.071489 | -0.12294 | -0.039471 | -0.11201 | -0.023249 | -0.033455 | -0.16801 | -0.048239 | 0.065481 | -0.004219 | 0.035585 | 121.5209 | 121.7082 | 121.2068 | 121.3596 | 0.085222 | -0.10921 | -0.025738 | -0.098275 | -0.009516 | -0.019722 | -0.15428 | -0.034506 | 0.079214 | 0.009514 | 0.049318 | 121.5346 | 121.7219 | 121.2205 | 121.3734 | -121.5691 | -121.255 | -121.5251 | -121.211
1171.7969 | 121.8567 | -121.6232 | 0.09613 | 0.06691 | -0.11836 | -0.04405 | -0.12116 | -0.018671 | -0.033455 | -0.15886 | -0.043661 | 0.065481 | -0.013376 | 0.021847 | 121.5255 | 121.7174 | 121.2114 | 121.3505 | 0.080643 | -0.10463 | -0.030317 | -0.10743 | -0.004938 | -0.019722 | -0.14513 | -0.029928 | 0.079214 | 0.000357 | 0.03558 | 121.5392 | 121.7311 | 121.2251 | 121.3642 | -121.5691 | -121.255 | -121.5389 | -121.2248
1173.4688 | 121.8292 | -121.6415 | 0.11902 | 0.076067 | -0.12294 | -0.039471 | -0.11659 | -0.023249 | -0.028877 | -0.17717 | -0.039082 | 0.07006 | -0.013376 | 0.031006 | 121.5255 | 121.7128 | 121.2068 | 121.3459 | 0.0898 | -0.10921 | -0.025738 | -0.10285 | -0.009516 | -0.015144 | -0.16344 | -0.025349 | 0.083793 | 0.000357 | 0.044739 | 121.5392 | 121.7265 | 121.2205 | 121.3596 | -121.5646 | -121.2459 | -121.5389 | -121.2202
1175.2031 | 121.843 | -121.6415 | 0.10529 | 0.06691 | -0.1321 | -0.039471 | -0.11201 | -0.023249 | -0.028877 | -0.17259 | -0.039082 | 0.060902 | -0.008798 | 0.031006 | 121.5209 | 121.7128 | 121.2068 | 121.3505 | 0.080643 | -0.11836 | -0.025738 | -0.098275 | -0.009516 | -0.015144 | -0.15886 | -0.025349 | 0.074635 | 0.004935 | 0.044739 | 121.5346 | 121.7265 | 121.2205 | 121.3642 | -121.56 | -121.2459 | -121.5297 | -121.2156
1176.9375 | 121.8063 | -121.6553 | 0.13733 | 0.080646 | -0.11836 | -0.04405 | -0.11659 | -0.018671 | -0.028877 | -0.17259 | -0.043661 | 0.060902 | -0.013376 | 0.035585 | 121.5209 | 121.7036 | 121.2022 | 121.355 | 0.094379 | -0.10463 | -0.030317 | -0.10285 | -0.004938 | -0.015144 | -0.15886 | -0.029928 | 0.074635 | 0.000357 | 0.049318 | 121.5346 | 121.7174 | 121.216 | 121.3688 | -121.5646 | -121.2459 | -121.5343 | -121.2156
1178.6719 | 121.8933 | -121.6141 | 0.086975 | 0.071489 | -0.12752 | -0.048628 | -0.11659 | -0.032405 | -0.033455 | -0.16801 | -0.034504 | 0.07006 | -0.013376 | 0.035585 | 121.5209 | 121.7174 | 121.2022 | 121.3505 | 0.085222 | -0.11378 | -0.034895 | -0.10285 | -0.018672 | -0.019722 | -0.15428 | -0.020771 | 0.083793 | 0.000357 | 0.049318 | 121.5346 | 121.7311 | 121.216 | 121.3642 | -121.5554 | -121.2367 | -121.5343 | -121.2156
1180.3594 | 121.9299 | -121.6003 | 0.064087 | 0.06691 | -0.12294 | -0.048628 | -0.12116 | -0.023249 | -0.028877 | -0.16801 | -0.034504 | 0.07006 | -0.004219 | 0.031006 | 121.5163 | 121.7174 | 121.2022 | 121.3413 | 0.080643 | -0.10921 | -0.034895 | -0.10743 | -0.009516 | -0.015144 | -0.15428 | -0.020771 | 0.083793 | 0.009514 | 0.044739 | 121.5301 | 121.7311 | 121.216 | 121.355 | -121.5508 | -121.2367 | -121.5205 | -121.2064
1182.0938 | 121.8246 | -121.6415 | 0.12817 | 0.076067 | -0.12294 | -0.04405 | -0.12574 | -0.027827 | -0.042612 | -0.17259 | -0.039082 | 0.060902 | -0.017954 | 0.035585 | 121.5255 | 121.7128 | 121.2022 | 121.355 | 0.0898 | -0.10921 | -0.030317 | -0.11201 | -0.014094 | -0.028879 | -0.15886 | -0.025349 | 0.074635 | -0.004221 | 0.049318 | 121.5392 | 121.7265 | 121.216 | 121.3688 | -121.5646 | -121.2413 | -121.5434 | -121.2202
1183.8281 | 121.8384 | -121.6278 | 0.1236 | 0.080646 | -0.1321 | -0.048628 | -0.12116 | -0.023249 | -0.033455 | -0.16801 | -0.039082 | 0.065481 | -0.008798 | 0.035585 | 121.5209 | 121.7128 | 121.2068 | 121.3505 | 0.094379 | -0.11836 | -0.034895 | -0.10743 | -0.009516 | -0.019722 | -0.15428 | -0.025349 | 0.079214 | 0.004935 | 0.049318 | 121.5346 | 121.7265 | 121.2205 | 121.3642 | -121.56 | -121.2459 | -121.5297 | -121.2156
1185.5 | 121.8933 | -121.6095 | 0.10071 | 0.076067 | -0.1321 | -0.04405 | -0.11659 | -0.027827 | -0.033455 | -0.17259 | -0.039082 | 0.074638 | -0.004219 | 0.035585 | 121.5209 | 121.7219 | 121.2068 | 121.355 | 0.0898 | -0.11836 | -0.030317 | -0.10285 | -0.014094 | -0.019722 | -0.15886 | -0.025349 | 0.088371 | 0.009514 | 0.049318 | 121.5346 | 121.7357 | 121.2205 | 121.3688 | -121.56 | -121.2459 | -121.5251 | -121.211
1187.2344 | 121.9574 | -121.6324 | 0.082397 | 0.080646 | -0.1321 | -0.048628 | -0.12116 | -0.027827 | -0.033455 | -0.17717 | -0.039082 | 0.07006 | -0.008798 | 0.035585 | 121.5255 | 121.7174 | 121.2022 | 121.3596 | 0.094379 | -0.11836 | -0.034895 | -0.10743 | -0.014094 | -0.019722 | -0.16344 | -0.025349 | 0.083793 | 0.004935 | 0.049318 | 121.5392 | 121.7311 | 121.216 | 121.3734 | -121.5646 | -121.2413 | -121.5343 | -121.211
1188.9688 | 121.907 | -121.5958 | 0.068665 | 0.076067 | -0.1321 | -0.048628 | -0.1349 | -0.032405 | -0.033455 | -0.17259 | -0.039082 | 0.065481 | -0.008798 | 0.031006 | 121.5163 | 121.7174 | 121.1976 | 121.3505 | 0.0898 | -0.11836 | -0.034895 | -0.12117 | -0.018672 | -0.019722 | -0.15886 | -0.025349 | 0.079214 | 0.004935 | 0.044739 | 121.5301 | 121.7311 | 121.2114 | 121.3642 | -121.5554 | -121.2367 | -121.5251 | -121.2064
1190.7188 | 121.8567 | -121.6049 | 0.10529 | 0.080646 | -0.12752 | -0.04405 | -0.13032 | -0.023249 | -0.042612 | -0.17717 | -0.039082 | 0.07006 | -0.004219 | 0.040164 | 121.5255 | 121.7128 | 121.2068 | 121.355 | 0.094379 | -0.11378 | -0.030317 | -0.11659 | -0.009516 | -0.028879 | -0.16344 | -0.025349 | 0.083793 | 0.009514 | 0.053897 | 121.5392 | 121.7265 | 121.2205 | 121.3688 | -121.5646 | -121.2459 | -121.5297 | -121.211
1192.4062 | 121.8246 | -121.6507 | 0.10071 | 0.080646 | -0.1321 | -0.048628 | -0.12574 | -0.032405 | -0.038034 | -0.17259 | -0.039082 | 0.065481 | -0.004219 | 0.035585 | 121.5163 | 121.7128 | 121.2022 | 121.3505 | 0.094379 | -0.11836 | -0.034895 | -0.11201 | -0.018672 | -0.024301 | -0.15886 | -0.025349 | 0.079214 | 0.009514 | 0.049318 | 121.5301 | 121.7265 | 121.216 | 121.3642 | -121.5554 | -121.2413 | -121.5205 | -121.2064
1194.1406 | 121.8109 | -121.6553 | 0.1236 | 0.076067 | -0.1321 | -0.057786 | -0.12116 | -0.032405 | -0.042612 | -0.17717 | -0.043661 | 0.07006 | -0.004219 | 0.040164 | 121.5255 | 121.7174 | 121.2114 | 121.355 | 0.0898 | -0.11836 | -0.044053 | -0.10743 | -0.018672 | -0.028879 | -0.16344 | -0.029928 | 0.083793 | 0.009514 | 0.053897 | 121.5392 | 121.7311 | 121.2251 | 121.3688 | -121.5691 | -121.255 | -121.5297 | -121.2156
1195.875 | 121.7972 | -121.6507 | 0.11444 | 0.071489 | -0.1321 | -0.062364 | -0.12116 | -0.032405 | -0.033455 | -0.17259 | -0.034504 | 0.065481 | -0.004219 | 0.031006 | 121.5209 | 121.7128 | 121.2022 | 121.3459 | 0.085222 | -0.11836 | -0.048631 | -0.10743 | -0.018672 | -0.019722 | -0.15886 | -0.020771 | 0.079214 | 0.009514 | 0.044739 | 121.5346 | 121.7265 | 121.216 | 121.3596 | -121.5554 | -121.2367 | -121.5251 | -121.2064
1197.5469 | 121.8246 | -121.6415 | 0.091553 | 0.076067 | -0.12294 | -0.04405 | -0.12116 | -0.032405 | -0.042612 | -0.17259 | -0.034504 | 0.074638 | -0.004219 | 0.035585 | 121.5209 | 121.7174 | 121.1976 | 121.355 | 0.0898 | -0.10921 | -0.030317 | -0.10743 | -0.018672 | -0.028879 | -0.15886 | -0.020771 | 0.088371 | 0.009514 | 0.049318 | 121.5346 | 121.7311 | 121.2114 | 121.3688 | -121.5554 | -121.2322 | -121.5251 | -121.2019
1199.2812 | 121.9299 | -121.582 | 0.07782 | 0.071489 | -0.13668 | -0.053207 | -0.12116 | -0.027827 | -0.038034 | -0.16801 | -0.034504 | 0.07006 | -0.008798 | 0.035585 | 121.5117 | 121.7082 | 121.2068 | 121.3505 | 0.085222 | -0.12294 | -0.039474 | -0.10743 | -0.014094 | -0.024301 | -0.15428 | -0.020771 | 0.083793 | 0.004935 | 0.049318 | 121.5255 | 121.7219 | 121.2205 | 121.3642 | -121.5463 | -121.2413 | -121.5205 | -121.2156
1201.0312 | 121.9116 | -121.6003 | 0.082397 | 0.080646 | -0.12752 | -0.048628 | -0.13032 | -0.032405 | -0.038034 | -0.18175 | -0.034504 | 0.079217 | -0.004219 | 0.040164 | 121.5117 | 121.7128 | 121.1976 | 121.3459 | 0.094379 | -0.11378 | -0.034895 | -0.11659 | -0.018672 | -0.024301 | -0.16802 | -0.020771 | 0.09295 | 0.009514 | 0.053897 | 121.5255 | 121.7265 | 121.2114 | 121.3596 | -121.5463 | -121.2322 | -121.516 | -121.2019
1202.7812 | 121.9254 | -121.582 | 0.10529 | 0.076067 | -0.12294 | -0.048628 | -0.12574 | -0.036983 | -0.04719 | -0.17717 | -0.039082 | 0.065481 | -0.013376 | 0.040164 | 121.5209 | 121.7128 | 121.1976 | 121.3505 | 0.0898 | -0.10921 | -0.034895 | -0.11201 | -0.02325 | -0.033457 | -0.16344 | -0.025349 | 0.079214 | 0.000357 | 0.053897 | 121.5346 | 121.7265 | 121.2114 | 121.3642 | -121.56 | -121.2367 | -121.5343 | -121.211
1204.5312 | 121.9116 | -121.6003 | 0.082397 | 0.076067 | -0.1321 | -0.057786 | -0.13032 | -0.041561 | -0.038034 | -0.18175 | -0.039082 | 0.074638 | -0.008798 | 0.035585 | 121.5209 | 121.7128 | 121.2022 | 121.355 | 0.0898 | -0.11836 | -0.044053 | -0.11659 | -0.027828 | -0.024301 | -0.16802 | -0.025349 | 0.088371 | 0.004935 | 0.049318 | 121.5346 | 121.7265 | 121.216 | 121.3688 | -121.56 | -121.2413 | -121.5297 | -121.211
1206.2188 | 121.8567 | -121.6187 | 0.09613 | 0.076067 | -0.1321 | -0.057786 | -0.13032 | -0.032405 | -0.042612 | -0.18633 | -0.039082 | 0.079217 | -0.004219 | 0.035585 | 121.5209 | 121.7128 | 121.2022 | 121.3505 | 0.0898 | -0.11836 | -0.044053 | -0.11659 | -0.018672 | -0.028879 | -0.17259 | -0.025349 | 0.09295 | 0.009514 | 0.049318 | 121.5346 | 121.7265 | 121.216 | 121.3642 | -121.56 | -121.2413 | -121.5251 | -121.2064
1207.9062 | 121.843 | -121.6553 | 0.12817 | 0.071489 | -0.1321 | -0.053207 | -0.13032 | -0.036983 | -0.042612 | -0.18175 | -0.034504 | 0.079217 | 0.000359 | 0.040164 | 121.5209 | 121.7174 | 121.2022 | 121.3505 | 0.085222 | -0.11836 | -0.039474 | -0.11659 | -0.02325 | -0.028879 | -0.16802 | -0.020771 | 0.09295 | 0.014092 | 0.053897 | 121.5346 | 121.7311 | 121.216 | 121.3642 | -121.5554 | -121.2367 | -121.5205 | -121.2019
1209.6406 | 121.8567 | -121.637 | 0.11444 | 0.071489 | -0.13668 | -0.053207 | -0.12574 | -0.036983 | -0.042612 | -0.17717 | -0.029925 | 0.079217 | -0.004219 | 0.040164 | 121.5163 | 121.7128 | 121.2068 | 121.3505 | 0.085222 | -0.12294 | -0.039474 | -0.11201 | -0.02325 | -0.028879 | -0.16344 | -0.016192 | 0.09295 | 0.009514 | 0.053897 | 121.5301 | 121.7265 | 121.2205 | 121.3642 | -121.5463 | -121.2367 | -121.5205 | -121.211
1211.375 | 121.9162 | -121.6095 | 0.10529 | 0.071489 | -0.14125 | -0.062364 | -0.1349 | -0.032405 | -0.042612 | -0.18633 | -0.034504 | 0.083796 | -0.008798 | 0.040164 | 121.5163 | 121.7082 | 121.2068 | 121.3459 | 0.085222 | -0.12752 | -0.048631 | -0.12117 | -0.018672 | -0.028879 | -0.17259 | -0.020771 | 0.097529 | 0.004935 | 0.053897 | 121.5301 | 121.7219 | 121.2205 | 121.3596 | -121.5508 | -121.2413 | -121.5251 | -121.2156
1213.1094 | 121.8613 | -121.6278 | 0.10986 | 0.076067 | -0.1321 | -0.062364 | -0.1349 | -0.036983 | -0.04719 | -0.18175 | -0.029925 | 0.074638 | 0.000359 | 0.031006 | 121.5209 | 121.7128 | 121.1976 | 121.3459 | 0.0898 | -0.11836 | -0.048631 | -0.12117 | -0.02325 | -0.033457 | -0.16802 | -0.016192 | 0.088371 | 0.014092 | 0.044739 | 121.5346 | 121.7265 | 121.2114 | 121.3596 | -121.5508 | -121.2276 | -121.5205 | -121.1973
1214.8594 | 121.9299 | -121.582 | 0.09613 | 0.080646 | -0.14125 | -0.062364 | -0.13032 | -0.036983 | -0.051769 | -0.19091 | -0.029925 | 0.079217 | -0.013376 | 0.035585 | 121.5209 | 121.6991 | 121.1976 | 121.3459 | 0.094379 | -0.12752 | -0.048631 | -0.11659 | -0.02325 | -0.038036 | -0.17717 | -0.016192 | 0.09295 | 0.000357 | 0.049318 | 121.5346 | 121.7128 | 121.2114 | 121.3596 | -121.5508 | -121.2276 | -121.5343 | -121.211
1216.5938 | 121.8109 | -121.6461 | 0.12817 | 0.080646 | -0.12752 | -0.057786 | -0.1349 | -0.036983 | -0.042612 | -0.17259 | -0.029925 | 0.074638 | -0.004219 | 0.044743 | 121.5117 | 121.7082 | 121.1931 | 121.3459 | 0.094379 | -0.11378 | -0.044053 | -0.12117 | -0.02325 | -0.028879 | -0.15886 | -0.016192 | 0.088371 | 0.009514 | 0.058476 | 121.5255 | 121.7219 | 121.2068 | 121.3596 | -121.5417 | -121.223 | -121.516 | -121.1973
1218.2656 | 121.8155 | -121.6324 | 0.13733 | 0.080646 | -0.13668 | -0.057786 | -0.1349 | -0.041561 | -0.04719 | -0.18633 | -0.029925 | 0.083796 | 0.000359 | 0.040164 | 121.5117 | 121.7082 | 121.1931 | 121.3413 | 0.094379 | -0.12294 | -0.044053 | -0.12117 | -0.027828 | -0.033457 | -0.17259 | -0.016192 | 0.097529 | 0.014092 | 0.053897 | 121.5255 | 121.7219 | 121.2068 | 121.355 | -121.5417 | -121.223 | -121.5114 | -121.1927
1219.9531 | 121.8979 | -121.5958 | 0.091553 | 0.071489 | -0.1321 | -0.062364 | -0.13032 | -0.036983 | -0.051769 | -0.19091 | -0.029925 | 0.083796 | -0.004219 | 0.035585 | 121.5072 | 121.7082 | 121.2022 | 121.3459 | 0.085222 | -0.11836 | -0.048631 | -0.11659 | -0.02325 | -0.038036 | -0.17717 | -0.016192 | 0.097529 | 0.009514 | 0.049318 | 121.5209 | 121.7219 | 121.216 | 121.3596 | -121.5371 | -121.2322 | -121.5114 | -121.2064
1221.7031 | 121.7972 | -121.6003 | 0.12817 | 0.076067 | -0.14125 | -0.062364 | -0.13032 | -0.041561 | -0.04719 | -0.18633 | -0.039082 | 0.074638 | 0.000359 | 0.049322 | 121.5163 | 121.6991 | 121.1976 | 121.3413 | 0.0898 | -0.12752 | -0.048631 | -0.11659 | -0.027828 | -0.033457 | -0.17259 | -0.025349 | 0.088371 | 0.014092 | 0.063055 | 121.5301 | 121.7128 | 121.2114 | 121.355 | -121.5554 | -121.2367 | -121.516 | -121.1973
1223.4375 | 121.9437 | -121.5912 | 0.09613 | 0.076067 | -0.1321 | -0.066943 | -0.1349 | -0.046138 | -0.04719 | -0.19091 | -0.029925 | 0.07006 | 0.000359 | 0.044743 | 121.5117 | 121.7128 | 121.2022 | 121.3459 | 0.0898 | -0.11836 | -0.05321 | -0.12117 | -0.032405 | -0.033457 | -0.17717 | -0.016192 | 0.083793 | 0.014092 | 0.058476 | 121.5255 | 121.7265 | 121.216 | 121.3596 | -121.5417 | -121.2322 | -121.5114 | -121.2019
1225.1875 | 121.8887 | -121.6095 | 0.10529 | 0.076067 | -0.13668 | -0.066943 | -0.14406 | -0.041561 | -0.051769 | -0.18175 | -0.034504 | 0.088375 | 0.000359 | 0.049322 | 121.5117 | 121.7082 | 121.1931 | 121.3367 | 0.0898 | -0.12294 | -0.05321 | -0.13032 | -0.027828 | -0.038036 | -0.16802 | -0.020771 | 0.10211 | 0.014092 | 0.063055 | 121.5255 | 121.7219 | 121.2068 | 121.3505 | -121.5463 | -121.2276 | -121.5114 | -121.1927
1226.9219 | 121.8155 | -121.637 | 0.13733 | 0.076067 | -0.13668 | -0.066943 | -0.14406 | -0.041561 | -0.056347 | -0.19091 | -0.029925 | 0.079217 | 0.000359 | 0.044743 | 121.5072 | 121.6945 | 121.1839 | 121.3413 | 0.0898 | -0.12294 | -0.05321 | -0.13032 | -0.027828 | -0.042614 | -0.17717 | -0.016192 | 0.09295 | 0.014092 | 0.058476 | 121.5209 | 121.7082 | 121.1976 | 121.355 | -121.5371 | -121.2138 | -121.5068 | -121.1836
1228.6562 | 121.7972 | -121.637 | 0.11902 | 0.071489 | -0.14125 | -0.071521 | -0.14406 | -0.046138 | -0.060926 | -0.19548 | -0.029925 | 0.083796 | 0.000359 | 0.044743 | 121.5117 | 121.6991 | 121.1931 | 121.3367 | 0.085222 | -0.12752 | -0.057788 | -0.13032 | -0.032405 | -0.047193 | -0.18175 | -0.016192 | 0.097529 | 0.014092 | 0.058476 | 121.5255 | 121.7128 | 121.2068 | 121.3505 | -121.5417 | -121.223 | -121.5114 | -121.1927
1230.4062 | 121.8155 | -121.6324 | 0.14191 | 0.076067 | -0.14125 | -0.0761 | -0.14406 | -0.046138 | -0.060926 | -0.19548 | -0.029925 | 0.079217 | 0.009515 | 0.040164 | 121.5117 | 121.7036 | 121.1885 | 121.3413 | 0.0898 | -0.12752 | -0.062367 | -0.13032 | -0.032405 | -0.047193 | -0.18175 | -0.016192 | 0.09295 | 0.023248 | 0.053897 | 121.5255 | 121.7174 | 121.2022 | 121.355 | -121.5417 | -121.2184 | -121.5022 | -121.179
1232.0938 | 121.8796 | -121.5958 | 0.10071 | 0.080646 | -0.13668 | -0.071521 | -0.13948 | -0.050716 | -0.060926 | -0.19548 | -0.020768 | 0.088375 | -0.004219 | 0.049322 | 121.5117 | 121.7036 | 121.1793 | 121.3276 | 0.094379 | -0.12294 | -0.057788 | -0.12575 | -0.036983 | -0.047193 | -0.18175 | -0.007035 | 0.10211 | 0.009514 | 0.063055 | 121.5255 | 121.7174 | 121.1931 | 121.3413 | -121.5325 | -121.2001 | -121.516 | -121.1836
1233.8281 | 121.8842 | -121.5775 | 0.10986 | 0.071489 | -0.14125 | -0.071521 | -0.13948 | -0.055294 | -0.056347 | -0.20464 | -0.025347 | 0.092954 | 0.000359 | 0.044743 | 121.5072 | 121.7036 | 121.1793 | 121.3322 | 0.085222 | -0.12752 | -0.057788 | -0.12575 | -0.041561 | -0.042614 | -0.19091 | -0.011614 | 0.10669 | 0.014092 | 0.058476 | 121.5209 | 121.7174 | 121.1931 | 121.3459 | -121.5325 | -121.2047 | -121.5068 | -121.179
1235.5625 | 121.8933 | -121.5912 | 0.10529 | 0.071489 | -0.13668 | -0.080679 | -0.14406 | -0.055294 | -0.056347 | -0.20006 | -0.025347 | 0.083796 | 0.000359 | 0.049322 | 121.5026 | 121.6899 | 121.1885 | 121.3413 | 0.085222 | -0.12294 | -0.066946 | -0.13032 | -0.041561 | -0.042614 | -0.18633 | -0.011614 | 0.097529 | 0.014092 | 0.063055 | 121.5163 | 121.7036 | 121.2022 | 121.355 | -121.5279 | -121.2138 | -121.5022 | -121.1881
1237.2344 | 121.8704 | -121.5866 | 0.10986 | 0.06691 | -0.14583 | -0.0761 | -0.14864 | -0.050716 | -0.056347 | -0.20464 | -0.020768 | 0.083796 | 0.000359 | 0.053901 | 121.498 | 121.6853 | 121.1748 | 121.3276 | 0.080643 | -0.1321 | -0.062367 | -0.1349 | -0.036983 | -0.042614 | -0.19091 | -0.007035 | 0.097529 | 0.014092 | 0.067634 | 121.5117 | 121.6991 | 121.1885 | 121.3413 | -121.5188 | -121.1955 | -121.4977 | -121.1744
1238.9219 | 121.9299 | -121.5683 | 0.086975 | 0.071489 | -0.14125 | -0.0761 | -0.14406 | -0.046138 | -0.065504 | -0.19548 | -0.020768 | 0.079217 | 0.000359 | 0.044743 | 121.5026 | 121.6899 | 121.1839 | 121.3322 | 0.085222 | -0.12752 | -0.062367 | -0.13032 | -0.032405 | -0.051771 | -0.18175 | -0.007035 | 0.09295 | 0.014092 | 0.058476 | 121.5163 | 121.7036 | 121.1976 | 121.3459 | -121.5234 | -121.2047 | -121.5022 | -121.1836
1240.6719 | 121.843 | -121.5912 | 0.1236 | 0.071489 | -0.14125 | -0.0761 | -0.14864 | -0.046138 | -0.060926 | -0.20006 | -0.029925 | 0.088375 | 0.004937 | 0.049322 | 121.498 | 121.6853 | 121.1839 | 121.3322 | 0.085222 | -0.12752 | -0.062367 | -0.1349 | -0.032405 | -0.047193 | -0.18633 | -0.016192 | 0.10211 | 0.01867 | 0.063055 | 121.5117 | 121.6991 | 121.1976 | 121.3459 | -121.5279 | -121.2138 | -121.4931 | -121.179
1242.3438 | 121.8063 | -121.6278 | 0.12817 | 0.080646 | -0.14583 | -0.0761 | -0.15321 | -0.050716 | -0.070082 | -0.19091 | -0.020768 | 0.088375 | 0.004937 | 0.053901 | 121.4889 | 121.6853 | 121.1793 | 121.3184 | 0.094379 | -0.1321 | -0.062367 | -0.13948 | -0.036983 | -0.056349 | -0.17717 | -0.007035 | 0.10211 | 0.01867 | 0.067634 | 121.5026 | 121.6991 | 121.1931 | 121.3322 | -121.5096 | -121.2001 | -121.4839 | -121.1744
1244.0781 | 121.8842 | -121.5683 | 0.091553 | 0.076067 | -0.14125 | -0.0761 | -0.14864 | -0.050716 | -0.070082 | -0.20006 | -0.025347 | 0.088375 | 0.000359 | 0.053901 | 121.4934 | 121.6853 | 121.1793 | 121.3276 | 0.0898 | -0.12752 | -0.062367 | -0.1349 | -0.036983 | -0.056349 | -0.18633 | -0.011614 | 0.10211 | 0.014092 | 0.067634 | 121.5072 | 121.6991 | 121.1931 | 121.3413 | -121.5188 | -121.2047 | -121.4931 | -121.179
1245.8281 | 121.8384 | -121.582 | 0.1236 | 0.080646 | -0.14583 | -0.0761 | -0.15321 | -0.055294 | -0.065504 | -0.20464 | -0.025347 | 0.088375 | 0.014094 | 0.053901 | 121.4889 | 121.6899 | 121.1793 | 121.3276 | 0.094379 | -0.1321 | -0.062367 | -0.13948 | -0.041561 | -0.051771 | -0.19091 | -0.011614 | 0.10211 | 0.027827 | 0.067634 | 121.5026 | 121.7036 | 121.1931 | 121.3413 | -121.5142 | -121.2047 | -121.4748 | -121.1652
1247.5625 | 121.8933 | -121.582 | 0.10071 | 0.071489 | -0.14125 | -0.080679 | -0.14864 | -0.050716 | -0.065504 | -0.20464 | -0.025347 | 0.088375 | 0.004937 | 0.049322 | 121.4934 | 121.6762 | 121.1748 | 121.3184 | 0.085222 | -0.12752 | -0.066946 | -0.1349 | -0.036983 | -0.051771 | -0.19091 | -0.011614 | 0.10211 | 0.01867 | 0.063055 | 121.5072 | 121.6899 | 121.1885 | 121.3322 | -121.5188 | -121.2001 | -121.4885 | -121.1698
1249.2344 | 121.7834 | -121.637 | 0.13733 | 0.071489 | -0.14125 | -0.0761 | -0.14864 | -0.055294 | -0.060926 | -0.20006 | -0.025347 | 0.092954 | 0.009515 | 0.049322 | 121.4934 | 121.6853 | 121.1656 | 121.3184 | 0.085222 | -0.12752 | -0.062367 | -0.1349 | -0.041561 | -0.047193 | -0.18633 | -0.011614 | 0.10669 | 0.023248 | 0.063055 | 121.5072 | 121.6991 | 121.1793 | 121.3322 | -121.5188 | -121.1909 | -121.4839 | -121.1561
1250.9219 | 121.8613 | -121.582 | 0.091553 | 0.076067 | -0.14583 | -0.089836 | -0.15321 | -0.050716 | -0.065504 | -0.20464 | -0.020768 | 0.092954 | 0.009515 | 0.053901 | 121.4889 | 121.6807 | 121.1702 | 121.3184 | 0.0898 | -0.1321 | -0.076103 | -0.13948 | -0.036983 | -0.051771 | -0.19091 | -0.007035 | 0.10669 | 0.023248 | 0.067634 | 121.5026 | 121.6945 | 121.1839 | 121.3322 | -121.5096 | -121.1909 | -121.4793 | -121.1607
1252.6719 | 121.7926 | -121.5591 | 0.14191 | 0.076067 | -0.14583 | -0.085257 | -0.15779 | -0.055294 | -0.070082 | -0.20006 | -0.011611 | 0.10669 | 0.02325 | 0.063059 | 121.466 | 121.6579 | 121.1427 | 121.2864 | 0.0898 | -0.1321 | -0.071524 | -0.14406 | -0.041561 | -0.056349 | -0.18633 | 0.002122 | 0.12042 | 0.036983 | 0.076792 | 121.4797 | 121.6716 | 121.1564 | 121.3001 | -121.4776 | -121.1543 | -121.4427 | -121.1195
1254.3438 | 121.8155 | -121.5958 | 0.14191 | 0.071489 | -0.14125 | -0.080679 | -0.15321 | -0.059872 | -0.065504 | -0.20006 | 0.002124 | 0.11127 | 0.027829 | 0.067638 | 121.4568 | 121.6533 | 121.1427 | 121.2864 | 0.085222 | -0.12752 | -0.066946 | -0.13948 | -0.046139 | -0.051771 | -0.18633 | 0.015857 | 0.125 | 0.041562 | 0.081371 | 121.4705 | 121.667 | 121.1564 | 121.3001 | -121.4547 | -121.1406 | -121.429 | -121.1149
1256.0312 | 121.8338 | -121.5546 | 0.13275 | 0.071489 | -0.14583 | -0.085257 | -0.15779 | -0.055294 | -0.070082 | -0.19548 | -0.002454 | 0.11127 | 0.027829 | 0.076796 | 121.4568 | 121.6533 | 121.1427 | 121.2864 | 0.085222 | -0.1321 | -0.071524 | -0.14406 | -0.041561 | -0.056349 | -0.18175 | 0.011279 | 0.125 | 0.041562 | 0.090529 | 121.4705 | 121.667 | 121.1564 | 121.3001 | -121.4593 | -121.1452 | -121.429 | -121.1149
1257.7812 | 121.8063 | -121.5546 | 0.15106 | 0.071489 | -0.14125 | -0.080679 | -0.15321 | -0.055294 | -0.065504 | -0.20922 | -0.002454 | 0.10669 | 0.02325 | 0.067638 | 121.4477 | 121.6395 | 121.1335 | 121.2726 | 0.085222 | -0.12752 | -0.066946 | -0.13948 | -0.041561 | -0.051771 | -0.19549 | 0.011279 | 0.12042 | 0.036983 | 0.081371 | 121.4614 | 121.6533 | 121.1473 | 121.2864 | -121.4501 | -121.136 | -121.4244 | -121.1103
1259.5156 | 121.7102 | -121.5591 | 0.15106 | 0.076067 | -0.14125 | -0.080679 | -0.16237 | -0.055294 | -0.065504 | -0.20922 | -0.002454 | 0.11585 | 0.027829 | 0.076796 | 121.4477 | 121.6441 | 121.1335 | 121.2726 | 0.0898 | -0.12752 | -0.066946 | -0.14864 | -0.041561 | -0.051771 | -0.19549 | 0.011279 | 0.12958 | 0.041562 | 0.090529 | 121.4614 | 121.6579 | 121.1473 | 121.2864 | -121.4501 | -121.136 | -121.4198 | -121.1057
1261.2031 | 121.7834 | -121.5591 | 0.15564 | 0.076067 | -0.14125 | -0.089836 | -0.15321 | -0.059872 | -0.065504 | -0.20922 | 0.002124 | 0.11127 | 0.027829 | 0.076796 | 121.4477 | 121.635 | 121.1198 | 121.2681 | 0.0898 | -0.12752 | -0.076103 | -0.13948 | -0.046139 | -0.051771 | -0.19549 | 0.015857 | 0.125 | 0.041562 | 0.090529 | 121.4614 | 121.6487 | 121.1335 | 121.2818 | -121.4455 | -121.1177 | -121.4198 | -121.092
1262.9531 | 121.8246 | -121.5637 | 0.15106 | 0.071489 | -0.14583 | -0.089836 | -0.15779 | -0.059872 | -0.074661 | -0.2138 | -0.002454 | 0.11585 | 0.027829 | 0.072217 | 121.4339 | 121.635 | 121.129 | 121.2772 | 0.085222 | -0.1321 | -0.076103 | -0.14406 | -0.046139 | -0.060928 | -0.20006 | 0.011279 | 0.12958 | 0.041562 | 0.08595 | 121.4477 | 121.6487 | 121.1427 | 121.2909 | -121.4364 | -121.1314 | -121.4061 | -121.1011
1264.6406 | 121.7514 | -121.55 | 0.17395 | 0.06691 | -0.15499 | -0.089836 | -0.15321 | -0.06445 | -0.074661 | -0.20464 | 0.002124 | 0.11127 | 0.02325 | 0.072217 | 121.4339 | 121.6304 | 121.1198 | 121.2681 | 0.080643 | -0.14126 | -0.076103 | -0.13948 | -0.050717 | -0.060928 | -0.19091 | 0.015857 | 0.125 | 0.036983 | 0.08595 | 121.4477 | 121.6441 | 121.1335 | 121.2818 | -121.4318 | -121.1177 | -121.4107 | -121.0966
1266.375 | 121.7651 | -121.5454 | 0.15564 | 0.071489 | -0.14583 | -0.094414 | -0.15779 | -0.055294 | -0.070082 | -0.20464 | 0.002124 | 0.11585 | 0.032407 | 0.081375 | 121.4339 | 121.6258 | 121.1198 | 121.2589 | 0.085222 | -0.1321 | -0.080681 | -0.14406 | -0.041561 | -0.056349 | -0.19091 | 0.015857 | 0.12958 | 0.04614 | 0.095108 | 121.4477 | 121.6395 | 121.1335 | 121.2726 | -121.4318 | -121.1177 | -121.4015 | -121.0874
1268.1094 | 121.7743 | -121.5317 | 0.17395 | 0.071489 | -0.15041 | -0.085257 | -0.16237 | -0.06445 | -0.074661 | -0.20922 | 0.006703 | 0.11127 | 0.027829 | 0.076796 | 121.4248 | 121.6258 | 121.1107 | 121.2589 | 0.085222 | -0.13668 | -0.071524 | -0.14864 | -0.050717 | -0.060928 | -0.19549 | 0.020436 | 0.125 | 0.041562 | 0.090529 | 121.4385 | 121.6395 | 121.1244 | 121.2726 | -121.4181 | -121.104 | -121.3969 | -121.0828
1269.8438 | 121.8796 | -121.5225 | 0.14648 | 0.071489 | -0.15041 | -0.098993 | -0.15779 | -0.069028 | -0.074661 | -0.20922 | 0.006703 | 0.12501 | 0.027829 | 0.081375 | 121.4248 | 121.6121 | 121.1107 | 121.2543 | 0.085222 | -0.13668 | -0.08526 | -0.14406 | -0.055295 | -0.060928 | -0.19549 | 0.020436 | 0.13874 | 0.041562 | 0.095108 | 121.4385 | 121.6258 | 121.1244 | 121.2681 | -121.4181 | -121.104 | -121.3969 | -121.0828
1271.5312 | 121.7468 | -121.5042 | 0.17853 | 0.071489 | -0.15499 | -0.085257 | -0.16237 | -0.06445 | -0.079239 | -0.20922 | 0.020438 | 0.13416 | 0.041563 | 0.090533 | 121.411 | 121.5983 | 121.0923 | 121.236 | 0.085222 | -0.14126 | -0.071524 | -0.14864 | -0.050717 | -0.065506 | -0.19549 | 0.034171 | 0.1479 | 0.055296 | 0.10427 | 121.4248 | 121.6121 | 121.1061 | 121.2497 | -121.3906 | -121.0719 | -121.3695 | -121.0508
1273.2656 | 121.7789 | -121.4951 | 0.18768 | 0.076067 | -0.14583 | -0.089836 | -0.16237 | -0.055294 | -0.079239 | -0.2138 | 0.020438 | 0.13416 | 0.046142 | 0.090533 | 121.4019 | 121.5938 | 121.0878 | 121.2269 | 0.0898 | -0.1321 | -0.076103 | -0.14864 | -0.041561 | -0.065506 | -0.20006 | 0.034171 | 0.1479 | 0.059875 | 0.10427 | 121.4156 | 121.6075 | 121.1015 | 121.2406 | -121.3814 | -121.0673 | -121.3557 | -121.0416
1275.0156 | 121.8704 | -121.463 | 0.15106 | 0.071489 | -0.15499 | -0.094414 | -0.17153 | -0.06445 | -0.079239 | -0.2138 | 0.025017 | 0.12958 | 0.05072 | 0.090533 | 121.3881 | 121.58 | 121.0695 | 121.2223 | 0.085222 | -0.14126 | -0.080681 | -0.1578 | -0.050717 | -0.065506 | -0.20006 | 0.03875 | 0.14332 | 0.064453 | 0.10427 | 121.4019 | 121.5938 | 121.0832 | 121.236 | -121.3631 | -121.0444 | -121.3374 | -121.0187
1276.7656 | 121.8475 | -121.463 | 0.12817 | 0.071489 | -0.15041 | -0.089836 | -0.16695 | -0.073606 | -0.079239 | -0.21838 | 0.020438 | 0.13416 | 0.046142 | 0.095112 | 121.379 | 121.58 | 121.0695 | 121.2177 | 0.085222 | -0.13668 | -0.076103 | -0.15322 | -0.059873 | -0.065506 | -0.20464 | 0.034171 | 0.1479 | 0.059875 | 0.10884 | 121.3927 | 121.5938 | 121.0832 | 121.2314 | -121.3585 | -121.049 | -121.3328 | -121.0233
1278.4375 | 121.6965 | -121.4905 | 0.19684 | 0.080646 | -0.15041 | -0.098993 | -0.16695 | -0.06445 | -0.079239 | -0.2138 | 0.057066 | 0.17537 | 0.087346 | 0.13632 | 121.5301 | 121.5342 | 121.2389 | 121.3734 | 0.094379 | -0.13668 | -0.08526 | -0.15322 | -0.050717 | -0.065506 | -0.20006 | 0.070799 | 0.1891 | 0.10108 | 0.15006 | 121.5438 | 121.548 | 121.2526 | 121.3871 | -121.473 | -121.1818 | -121.4427 | -121.1515
1280.1719 | 121.5591 | -121.3074 | 0.11444 | 0.076067 | -0.14583 | -0.089836 | -0.16237 | -0.055294 | -0.074661 | -0.2138 | 1.133 | 1.2193 | 1.1724 | 1.1849 | 120.1108 | 120.1059 | 119.8241 | 119.9312 | 0.0898 | -0.1321 | -0.076103 | -0.14864 | -0.041561 | -0.060928 | -0.20006 | 1.1467 | 1.2331 | 1.1861 | 1.1987 | 120.1246 | 120.1196 | 119.8379 | 119.945 | -118.9778 | -118.6911 | -118.9384 | -118.6517
1281.9062 | 121.6873 | -121.5317 | 0.11444 | 0.071489 | -0.15041 | -0.098993 | -0.17153 | -0.073606 | -0.079239 | -0.20922 | -0.043661 | 0.07006 | -0.013376 | 0.026427 | 121.6079 | 121.5938 | 121.3213 | 121.4466 | 0.085222 | -0.13668 | -0.08526 | -0.1578 | -0.059873 | -0.065506 | -0.19549 | -0.029928 | 0.083793 | 0.000357 | 0.04016 | 121.6216 | 121.6075 | 121.335 | 121.4603 | -121.6516 | -121.3649 | -121.6213 | -121.3346
1283.5781 | 121.7239 | -121.55 | 0.13733 | 0.071489 | -0.15041 | -0.098993 | -0.16695 | -0.069028 | -0.079239 | -0.20922 | -0.034504 | 0.065481 | -0.008798 | 0.031006 | 121.6308 | 121.6212 | 121.1198 | 121.4695 | 0.085222 | -0.13668 | -0.08526 | -0.15322 | -0.055295 | -0.065506 | -0.19549 | -0.020771 | 0.079214 | 0.004935 | 0.044739 | 121.6445 | 121.635 | 121.1335 | 121.4832 | -121.6653 | -121.1543 | -121.6396 | -121.1286
1285.3125 | 121.7285 | -121.5729 | 0.11902 | 0.076067 | -0.15041 | -0.098993 | -0.17153 | -0.073606 | -0.088396 | -0.22295 | -0.039082 | 0.065481 | -0.004219 | 0.026427 | 121.4522 | 121.6487 | 121.1244 | 121.4878 | 0.0898 | -0.13668 | -0.08526 | -0.1578 | -0.059873 | -0.074663 | -0.20922 | -0.025349 | 0.079214 | 0.009514 | 0.04016 | 121.466 | 121.6624 | 121.1381 | 121.5015 | -121.4913 | -121.1635 | -121.4565 | -121.1286
1287.0469 | 121.8796 | -121.5317 | 0.086975 | 0.06691 | -0.15041 | -0.094414 | -0.16695 | -0.073606 | -0.088396 | -0.21838 | -0.039082 | 0.065481 | -0.004219 | 0.035585 | 121.4568 | 121.6487 | 121.1427 | 121.497 | 0.080643 | -0.13668 | -0.080681 | -0.15322 | -0.059873 | -0.074663 | -0.20464 | -0.025349 | 0.079214 | 0.009514 | 0.049318 | 121.4705 | 121.6624 | 121.1564 | 121.5107 | -121.4959 | -121.1818 | -121.461 | -121.1469
1288.7969 | 121.8246 | -121.5775 | 0.091553 | 0.071489 | -0.15041 | -0.098993 | -0.17153 | -0.069028 | -0.079239 | -0.22295 | -0.039082 | 0.074638 | -0.008798 | 0.026427 | 121.4751 | 121.6624 | 121.161 | 121.5015 | 0.085222 | -0.13668 | -0.08526 | -0.1578 | -0.055295 | -0.065506 | -0.20922 | -0.025349 | 0.088371 | 0.004935 | 0.04016 | 121.4889 | 121.6762 | 121.1748 | 121.5153 | -121.5142 | -121.2001 | -121.4839 | -121.1698
1290.4688 | 121.8018 | -121.5775 | 0.10529 | 0.06691 | -0.15499 | -0.10815 | -0.16695 | -0.073606 | -0.079239 | -0.21838 | -0.043661 | 0.065481 | -0.004219 | 0.031006 | 121.4751 | 121.6716 | 121.161 | 121.5153 | 0.080643 | -0.14126 | -0.094417 | -0.15322 | -0.059873 | -0.065506 | -0.20464 | -0.029928 | 0.079214 | 0.009514 | 0.044739 | 121.4889 | 121.6853 | 121.1748 | 121.529 | -121.5188 | -121.2047 | -121.4793 | -121.1652
1292.2031 | 121.8201 | -121.5866 | 0.10529 | 0.071489 | -0.15499 | -0.098993 | -0.17153 | -0.073606 | -0.083817 | -0.22295 | -0.034504 | 0.07006 | -0.004219 | 0.021847 | 121.4843 | 121.6807 | 121.1702 | 121.5244 | 0.085222 | -0.14126 | -0.08526 | -0.1578 | -0.059873 | -0.070084 | -0.20922 | -0.020771 | 0.083793 | 0.009514 | 0.03558 | 121.498 | 121.6945 | 121.1839 | 121.5382 | -121.5188 | -121.2047 | -121.4885 | -121.1744
1293.9375 | 121.9116 | -121.5637 | 0.09613 | 0.071489 | -0.15499 | -0.098993 | -0.17153 | -0.073606 | -0.083817 | -0.22295 | -0.043661 | 0.07006 | -0.008798 | 0.026427 | 121.4934 | 121.6853 | 121.1748 | 121.3093 | 0.085222 | -0.14126 | -0.08526 | -0.1578 | -0.059873 | -0.070084 | -0.20922 | -0.029928 | 0.083793 | 0.004935 | 0.04016 | 121.5072 | 121.6991 | 121.1885 | 121.323 | -121.5371 | -121.2184 | -121.5022 | -121.1836
1295.6875 | 121.8842 | -121.5866 | 0.09613 | 0.06691 | -0.15041 | -0.10815 | -0.17153 | -0.082762 | -0.088396 | -0.22753 | -0.039082 | 0.060902 | -0.008798 | 0.026427 | 121.498 | 121.6945 | 121.1793 | 121.3322 | 0.080643 | -0.13668 | -0.094417 | -0.1578 | -0.069029 | -0.074663 | -0.2138 | -0.025349 | 0.074635 | 0.004935 | 0.04016 | 121.5117 | 121.7082 | 121.1931 | 121.3459 | -121.5371 | -121.2184 | -121.5068 | -121.1881
1297.375 | 121.9116 | -121.582 | 0.082397 | 0.076067 | -0.15957 | -0.10815 | -0.17611 | -0.073606 | -0.092974 | -0.22753 | -0.043661 | 0.074638 | 0.000359 | 0.040164 | 121.5026 | 121.6945 | 121.1793 | 121.3322 | 0.0898 | -0.14584 | -0.094417 | -0.16237 | -0.059873 | -0.079241 | -0.2138 | -0.029928 | 0.088371 | 0.014092 | 0.053897 | 121.5163 | 121.7082 | 121.1931 | 121.3459 | -121.5463 | -121.223 | -121.5022 | -121.179
1299.125 | 121.9116 | -121.5866 | 0.082397 | 0.062332 | -0.16415 | -0.10815 | -0.17611 | -0.078184 | -0.088396 | -0.23211 | -0.043661 | 0.07006 | -0.008798 | 0.031006 | 121.5072 | 121.7082 | 121.1839 | 121.3367 | 0.076065 | -0.15042 | -0.094417 | -0.16237 | -0.064451 | -0.074663 | -0.21838 | -0.029928 | 0.083793 | 0.004935 | 0.044739 | 121.5209 | 121.7219 | 121.1976 | 121.3505 | -121.5508 | -121.2276 | -121.516 | -121.1927
1300.875 | 121.8704 | -121.6003 | 0.082397 | 0.071489 | -0.16415 | -0.11273 | -0.17611 | -0.073606 | -0.092974 | -0.22753 | -0.034504 | 0.07006 | -0.013376 | 0.031006 | 121.5072 | 121.7082 | 121.1976 | 121.3367 | 0.085222 | -0.15042 | -0.098996 | -0.16237 | -0.059873 | -0.079241 | -0.2138 | -0.020771 | 0.083793 | 0.000357 | 0.044739 | 121.5209 | 121.7219 | 121.2114 | 121.3505 | -121.5417 | -121.2322 | -121.5205 | -121.211
1302.5625 | 121.9162 | -121.5958 | 0.091553 | 0.062332 | -0.16415 | -0.11731 | -0.18069 | -0.082762 | -0.092974 | -0.22753 | -0.039082 | 0.074638 | -0.004219 | 0.035585 | 121.5255 | 121.7128 | 121.2022 | 121.3505 | 0.076065 | -0.15042 | -0.10357 | -0.16695 | -0.069029 | -0.079241 | -0.2138 | -0.025349 | 0.088371 | 0.009514 | 0.049318 | 121.5392 | 121.7265 | 121.216 | 121.3642 | -121.5646 | -121.2413 | -121.5297 | -121.2064
1304.2969 | 121.8246 | -121.6187 | 0.10071 | 0.076067 | -0.15957 | -0.11273 | -0.17611 | -0.078184 | -0.092974 | -0.23211 | -0.043661 | 0.079217 | -0.004219 | 0.026427 | 121.5163 | 121.7174 | 121.1976 | 121.3459 | 0.0898 | -0.14584 | -0.098996 | -0.16237 | -0.064451 | -0.079241 | -0.21838 | -0.029928 | 0.09295 | 0.009514 | 0.04016 | 121.5301 | 121.7311 | 121.2114 | 121.3596 | -121.56 | -121.2413 | -121.5205 | -121.2019
1305.9688 | 121.8979 | -121.6187 | 0.10986 | 0.071489 | -0.16415 | -0.11731 | -0.17153 | -0.082762 | -0.097553 | -0.23211 | -0.043661 | 0.07006 | 0.000359 | 0.031006 | 121.5301 | 121.7219 | 121.216 | 121.3596 | 0.085222 | -0.15042 | -0.10357 | -0.1578 | -0.069029 | -0.08382 | -0.21838 | -0.029928 | 0.083793 | 0.014092 | 0.044739 | 121.5438 | 121.7357 | 121.2297 | 121.3734 | -121.5737 | -121.2596 | -121.5297 | -121.2156
1307.6562 | 121.8155 | -121.6644 | 0.11902 | 0.071489 | -0.16873 | -0.10815 | -0.18069 | -0.078184 | -0.097553 | -0.23211 | -0.034504 | 0.074638 | -0.004219 | 0.026427 | 121.5255 | 121.7219 | 121.216 | 121.355 | 0.085222 | -0.15499 | -0.094417 | -0.16695 | -0.064451 | -0.08382 | -0.21838 | -0.020771 | 0.088371 | 0.009514 | 0.04016 | 121.5392 | 121.7357 | 121.2297 | 121.3688 | -121.56 | -121.2505 | -121.5297 | -121.2202
1309.3906 | 121.9208 | -121.6187 | 0.091553 | 0.06691 | -0.15957 | -0.10815 | -0.18069 | -0.091918 | -0.088396 | -0.23211 | -0.039082 | 0.07006 | -0.008798 | 0.031006 | 121.5346 | 121.7219 | 121.2205 | 121.3642 | 0.080643 | -0.14584 | -0.094417 | -0.16695 | -0.078185 | -0.074663 | -0.21838 | -0.025349 | 0.083793 | 0.004935 | 0.044739 | 121.5484 | 121.7357 | 121.2343 | 121.3779 | -121.5737 | -121.2596 | -121.5434 | -121.2293
1311.125 | 121.843 | -121.6553 | 0.11902 | 0.06691 | -0.16873 | -0.11731 | -0.18526 | -0.082762 | -0.092974 | -0.22753 | -0.039082 | 0.065481 | -0.013376 | 0.031006 | 121.5346 | 121.7265 | 121.2205 | 121.3642 | 0.080643 | -0.15499 | -0.10357 | -0.17153 | -0.069029 | -0.079241 | -0.2138 | -0.025349 | 0.079214 | 0.000357 | 0.044739 | 121.5484 | 121.7403 | 121.2343 | 121.3779 | -121.5737 | -121.2596 | -121.548 | -121.2339
1312.8594 | 121.8201 | -121.6461 | 0.10986 | 0.06691 | -0.17331 | -0.12189 | -0.18069 | -0.08734 | -0.088396 | -0.23211 | -0.039082 | 0.065481 | -0.008798 | 0.035585 | 121.5438 | 121.7311 | 121.2251 | 121.3734 | 0.080643 | -0.15957 | -0.10815 | -0.16695 | -0.073607 | -0.074663 | -0.21838 | -0.025349 | 0.079214 | 0.004935 | 0.049318 | 121.5575 | 121.7448 | 121.2389 | 121.3871 | -121.5829 | -121.2642 | -121.5526 | -121.2339
1314.5938 | 121.8613 | -121.669 | 0.11902 | 0.071489 | -0.16873 | -0.10815 | -0.18069 | -0.073606 | -0.097553 | -0.24127 | -0.043661 | 0.065481 | -0.008798 | 0.026427 | 121.5392 | 121.7357 | 121.216 | 121.3734 | 0.085222 | -0.15499 | -0.094417 | -0.16695 | -0.059873 | -0.08382 | -0.22753 | -0.029928 | 0.079214 | 0.004935 | 0.04016 | 121.553 | 121.7494 | 121.2297 | 121.3871 | -121.5829 | -121.2596 | -121.548 | -121.2248
1316.3281 | 121.8384 | -121.6736 | 0.09613 | 0.076067 | -0.16415 | -0.11731 | -0.18069 | -0.08734 | -0.10213 | -0.23669 | -0.039082 | 0.074638 | -0.008798 | 0.031006 | 121.5438 | 121.7357 | 121.2251 | 121.3688 | 0.0898 | -0.15042 | -0.10357 | -0.16695 | -0.073607 | -0.088398 | -0.22296 | -0.025349 | 0.088371 | 0.004935 | 0.044739 | 121.5575 | 121.7494 | 121.2389 | 121.3825 | -121.5829 | -121.2642 | -121.5526 | -121.2339
1318 | 121.9437 | -121.6324 | 0.07782 | 0.06691 | -0.17331 | -0.11731 | -0.18526 | -0.08734 | -0.10213 | -0.23669 | -0.039082 | 0.07006 | -0.008798 | 0.035585 | 121.5438 | 121.7403 | 121.2251 | 121.3688 | 0.080643 | -0.15957 | -0.10357 | -0.17153 | -0.073607 | -0.088398 | -0.22296 | -0.025349 | 0.083793 | 0.004935 | 0.049318 | 121.5575 | 121.754 | 121.2389 | 121.3825 | -121.5829 | -121.2642 | -121.5526 | -121.2339
1319.75 | 121.9803 | -121.6324 | 0.082397 | 0.06691 | -0.16873 | -0.11731 | -0.18984 | -0.078184 | -0.10671 | -0.23669 | -0.039082 | 0.074638 | -0.013376 | 0.031006 | 121.553 | 121.7403 | 121.2389 | 121.3825 | 0.080643 | -0.15499 | -0.10357 | -0.17611 | -0.064451 | -0.092976 | -0.22296 | -0.025349 | 0.088371 | 0.000357 | 0.044739 | 121.5667 | 121.754 | 121.2526 | 121.3962 | -121.592 | -121.2779 | -121.5663 | -121.2522
1321.5 | 121.8475 | -121.6599 | 0.10986 | 0.076067 | -0.15957 | -0.12189 | -0.18526 | -0.08734 | -0.10213 | -0.23669 | -0.034504 | 0.07006 | -0.013376 | 0.035585 | 121.553 | 121.7357 | 121.2434 | 121.3825 | 0.0898 | -0.14584 | -0.10815 | -0.17153 | -0.073607 | -0.088398 | -0.22296 | -0.020771 | 0.083793 | 0.000357 | 0.049318 | 121.5667 | 121.7494 | 121.2572 | 121.3962 | -121.5875 | -121.2779 | -121.5663 | -121.2568
1323.1875 | 121.9757 | -121.6278 | 0.09613 | 0.06691 | -0.16415 | -0.12189 | -0.18984 | -0.082762 | -0.10671 | -0.24127 | -0.034504 | 0.074638 | -0.004219 | 0.035585 | 121.5484 | 121.7448 | 121.2389 | 121.3825 | 0.080643 | -0.15042 | -0.10815 | -0.17611 | -0.069029 | -0.092976 | -0.22753 | -0.020771 | 0.088371 | 0.009514 | 0.049318 | 121.5621 | 121.7586 | 121.2526 | 121.3962 | -121.5829 | -121.2734 | -121.5526 | -121.2431
1324.9375 | 121.9162 | -121.6507 | 0.091553 | 0.062332 | -0.16415 | -0.12189 | -0.18984 | -0.091918 | -0.11129 | -0.22753 | -0.048239 | 0.065481 | -0.008798 | 0.031006 | 121.5575 | 121.7494 | 121.2389 | 121.3871 | 0.076065 | -0.15042 | -0.10815 | -0.17611 | -0.078185 | -0.097555 | -0.2138 | -0.034506 | 0.079214 | 0.004935 | 0.044739 | 121.5713 | 121.7631 | 121.2526 | 121.4008 | -121.6058 | -121.2871 | -121.5663 | -121.2477
1326.6875 | 121.8384 | -121.6965 | 0.1236 | 0.057754 | -0.16415 | -0.12189 | -0.18984 | -0.091918 | -0.10671 | -0.24127 | -0.039082 | 0.074638 | -0.008798 | 0.035585 | 121.553 | 121.7448 | 121.2389 | 121.3734 | 0.071487 | -0.15042 | -0.10815 | -0.17611 | -0.078185 | -0.092976 | -0.22753 | -0.025349 | 0.088371 | 0.004935 | 0.049318 | 121.5667 | 121.7586 | 121.2526 | 121.3871 | -121.592 | -121.2779 | -121.5618 | -121.2477
1328.3594 | 121.8613 | -121.6827 | 0.11902 | 0.076067 | -0.16873 | -0.12646 | -0.18984 | -0.096496 | -0.10213 | -0.24127 | -0.039082 | 0.074638 | -0.004219 | 0.031006 | 121.5484 | 121.7494 | 121.2434 | 121.3825 | 0.0898 | -0.15499 | -0.11273 | -0.17611 | -0.082763 | -0.088398 | -0.22753 | -0.025349 | 0.088371 | 0.009514 | 0.044739 | 121.5621 | 121.7631 | 121.2572 | 121.3962 | -121.5875 | -121.2825 | -121.5526 | -121.2477
1330.0938 | 121.8796 | -121.6827 | 0.13275 | 0.062332 | -0.17331 | -0.13104 | -0.18984 | -0.096496 | -0.11129 | -0.24127 | -0.034504 | 0.07006 | -0.008798 | 0.021847 | 121.5621 | 121.754 | 121.2434 | 121.3962 | 0.076065 | -0.15957 | -0.11731 | -0.17611 | -0.082763 | -0.097555 | -0.22753 | -0.020771 | 0.083793 | 0.004935 | 0.03558 | 121.5758 | 121.7677 | 121.2572 | 121.41 | -121.5966 | -121.2779 | -121.5709 | -121.2522
1331.7812 | 121.8567 | -121.7056 | 0.10986 | 0.06691 | -0.16415 | -0.12646 | -0.18984 | -0.091918 | -0.10671 | -0.24127 | -0.039082 | 0.07006 | -0.004219 | 0.031006 | 121.5621 | 121.754 | 121.248 | 121.3917 | 0.080643 | -0.15042 | -0.11273 | -0.17611 | -0.078185 | -0.092976 | -0.22753 | -0.025349 | 0.083793 | 0.009514 | 0.044739 | 121.5758 | 121.7677 | 121.2617 | 121.4054 | -121.6012 | -121.2871 | -121.5663 | -121.2522
1333.5156 | 121.8384 | -121.701 | 0.10071 | 0.062332 | -0.17331 | -0.12646 | -0.19442 | -0.10107 | -0.10213 | -0.23669 | -0.034504 | 0.074638 | -0.004219 | 0.031006 | 121.5621 | 121.7494 | 121.248 | 121.3962 | 0.076065 | -0.15957 | -0.11273 | -0.18069 | -0.087341 | -0.088398 | -0.22296 | -0.020771 | 0.088371 | 0.009514 | 0.044739 | 121.5758 | 121.7631 | 121.2617 | 121.41 | -121.5966 | -121.2825 | -121.5663 | -121.2522
1335.25 | 121.8246 | -121.6736 | 0.11902 | 0.071489 | -0.16873 | -0.12189 | -0.19442 | -0.10107 | -0.11129 | -0.23669 | -0.039082 | 0.074638 | -0.013376 | 0.031006 | 121.5621 | 121.7494 | 121.2389 | 121.3917 | 0.085222 | -0.15499 | -0.10815 | -0.18069 | -0.087341 | -0.097555 | -0.22296 | -0.025349 | 0.088371 | 0.000357 | 0.044739 | 121.5758 | 121.7631 | 121.2526 | 121.4054 | -121.6012 | -121.2779 | -121.5755 | -121.2522
1336.9375 | 121.962 | -121.6553 | 0.068665 | 0.062332 | -0.17788 | -0.1402 | -0.19442 | -0.096496 | -0.11129 | -0.25042 | -0.043661 | 0.07006 | -0.008798 | 0.021847 | 121.5667 | 121.7586 | 121.2572 | 121.3962 | 0.076065 | -0.16415 | -0.12647 | -0.18069 | -0.082763 | -0.097555 | -0.23669 | -0.029928 | 0.083793 | 0.004935 | 0.03558 | 121.5804 | 121.7723 | 121.2709 | 121.41 | -121.6103 | -121.3008 | -121.5755 | -121.266
1338.6719 | 121.8613 | -121.6782 | 0.11444 | 0.06691 | -0.17331 | -0.13104 | -0.19442 | -0.096496 | -0.10213 | -0.25042 | -0.039082 | 0.07006 | -0.013376 | 0.026427 | 121.5621 | 121.754 | 121.2389 | 121.3962 | 0.080643 | -0.15957 | -0.11731 | -0.18069 | -0.082763 | -0.088398 | -0.23669 | -0.025349 | 0.083793 | 0.000357 | 0.04016 | 121.5758 | 121.7677 | 121.2526 | 121.41 | -121.6012 | -121.2779 | -121.5755 | -121.2522
1340.4062 | 121.9574 | -121.6324 | 0.086975 | 0.06691 | -0.17331 | -0.13104 | -0.199 | -0.10565 | -0.11587 | -0.25042 | -0.034504 | 0.060902 | -0.004219 | 0.031006 | 121.5667 | 121.7631 | 121.248 | 121.4054 | 0.080643 | -0.15957 | -0.11731 | -0.18527 | -0.091919 | -0.10213 | -0.23669 | -0.020771 | 0.074635 | 0.009514 | 0.044739 | 121.5804 | 121.7769 | 121.2617 | 121.4191 | -121.6012 | -121.2825 | -121.5709 | -121.2522
1342.0781 | 121.8521 | -121.6827 | 0.1236 | 0.06691 | -0.17331 | -0.13562 | -0.199 | -0.10107 | -0.10671 | -0.24584 | -0.039082 | 0.074638 | -0.013376 | 0.026427 | 121.5758 | 121.7586 | 121.2617 | 121.4054 | 0.080643 | -0.15957 | -0.12189 | -0.18527 | -0.087341 | -0.092976 | -0.23211 | -0.025349 | 0.088371 | 0.000357 | 0.04016 | 121.5896 | 121.7723 | 121.2755 | 121.4191 | -121.6149 | -121.3008 | -121.5892 | -121.2751
1343.8125 | 121.9849 | -121.6324 | 0.091553 | 0.06691 | -0.17788 | -0.13562 | -0.199 | -0.10107 | -0.11587 | -0.24584 | -0.034504 | 0.074638 | -0.008798 | 0.031006 | 121.5804 | 121.7631 | 121.2572 | 121.41 | 0.080643 | -0.16415 | -0.12189 | -0.18527 | -0.087341 | -0.10213 | -0.23211 | -0.020771 | 0.088371 | 0.004935 | 0.044739 | 121.5942 | 121.7769 | 121.2709 | 121.4237 | -121.6149 | -121.2917 | -121.5892 | -121.266
1345.4844 | 121.8475 | -121.6919 | 0.12817 | 0.062332 | -0.17788 | -0.1402 | -0.20816 | -0.10107 | -0.11129 | -0.25042 | -0.039082 | 0.07006 | -0.004219 | 0.035585 | 121.585 | 121.7586 | 121.2572 | 121.41 | 0.076065 | -0.16415 | -0.12647 | -0.19442 | -0.087341 | -0.097555 | -0.23669 | -0.025349 | 0.083793 | 0.009514 | 0.049318 | 121.5987 | 121.7723 | 121.2709 | 121.4237 | -121.6241 | -121.2962 | -121.5892 | -121.2614
1347.2188 | 121.9437 | -121.6599 | 0.10986 | 0.06691 | -0.18246 | -0.1402 | -0.199 | -0.10107 | -0.10671 | -0.25042 | -0.039082 | 0.079217 | -0.004219 | 0.031006 | 121.585 | 121.7677 | 121.2572 | 121.4054 | 0.080643 | -0.16873 | -0.12647 | -0.18527 | -0.087341 | -0.092976 | -0.23669 | -0.025349 | 0.09295 | 0.009514 | 0.044739 | 121.5987 | 121.7815 | 121.2709 | 121.4191 | -121.6241 | -121.2962 | -121.5892 | -121.2614
1348.9531 | 121.8521 | -121.6873 | 0.11444 | 0.062332 | -0.18246 | -0.13104 | -0.199 | -0.10565 | -0.11587 | -0.255 | -0.043661 | 0.074638 | -0.008798 | 0.026427 | 121.5758 | 121.7677 | 121.2526 | 121.4054 | 0.076065 | -0.16873 | -0.11731 | -0.18527 | -0.091919 | -0.10213 | -0.24127 | -0.029928 | 0.088371 | 0.004935 | 0.04016 | 121.5896 | 121.7815 | 121.2663 | 121.4191 | -121.6195 | -121.2962 | -121.5846 | -121.2614
1350.6875 | 121.9574 | -121.6553 | 0.091553 | 0.06691 | -0.18246 | -0.1402 | -0.199 | -0.10565 | -0.11587 | -0.25042 | -0.034504 | 0.07006 | -0.008798 | 0.031006 | 121.5758 | 121.7723 | 121.2572 | 121.4054 | 0.080643 | -0.16873 | -0.12647 | -0.18527 | -0.091919 | -0.10213 | -0.23669 | -0.020771 | 0.083793 | 0.004935 | 0.044739 | 121.5896 | 121.786 | 121.2709 | 121.4191 | -121.6103 | -121.2917 | -121.5846 | -121.266
1352.375 | 121.9711 | -121.6553 | 0.09613 | 0.071489 | -0.18704 | -0.1402 | -0.21274 | -0.11481 | -0.11587 | -0.25042 | -0.043661 | 0.074638 | -0.004219 | 0.026427 | 121.5804 | 121.7723 | 121.2663 | 121.41 | 0.085222 | -0.17331 | -0.12647 | -0.199 | -0.10107 | -0.10213 | -0.23669 | -0.029928 | 0.088371 | 0.009514 | 0.04016 | 121.5942 | 121.786 | 121.2801 | 121.4237 | -121.6241 | -121.31 | -121.5846 | -121.2705
1354.1094 | 122.0032 | -121.6415 | 0.086975 | 0.071489 | -0.18704 | -0.14478 | -0.20816 | -0.10107 | -0.11587 | -0.255 | -0.034504 | 0.065481 | -0.004219 | 0.021847 | 121.5804 | 121.7631 | 121.2663 | 121.4054 | 0.085222 | -0.17331 | -0.13105 | -0.19442 | -0.087341 | -0.10213 | -0.24127 | -0.020771 | 0.079214 | 0.009514 | 0.03558 | 121.5942 | 121.7769 | 121.2801 | 121.4191 | -121.6149 | -121.3008 | -121.5846 | -121.2705
1355.8438 | 121.9711 | -121.6461 | 0.073242 | 0.06691 | -0.18704 | -0.14478 | -0.20358 | -0.11023 | -0.12044 | -0.25042 | -0.039082 | 0.079217 | -0.013376 | 0.035585 | 121.5804 | 121.7723 | 121.2617 | 121.41 | 0.080643 | -0.17331 | -0.13105 | -0.18985 | -0.096497 | -0.10671 | -0.23669 | -0.025349 | 0.09295 | 0.000357 | 0.049318 | 121.5942 | 121.786 | 121.2755 | 121.4237 | -121.6195 | -121.3008 | -121.5938 | -121.2751
1357.5156 | 121.8521 | -121.6965 | 0.12817 | 0.062332 | -0.1962 | -0.1402 | -0.20816 | -0.11023 | -0.12502 | -0.255 | -0.043661 | 0.074638 | -0.004219 | 0.031006 | 121.5896 | 121.7769 | 121.2663 | 121.4146 | 0.076065 | -0.18247 | -0.12647 | -0.19442 | -0.096497 | -0.11129 | -0.24127 | -0.029928 | 0.088371 | 0.009514 | 0.044739 | 121.6033 | 121.7906 | 121.2801 | 121.4283 | -121.6332 | -121.31 | -121.5938 | -121.2705
1359.25 | 122.0215 | -121.6507 | 0.068665 | 0.057754 | -0.18704 | -0.14936 | -0.20358 | -0.11023 | -0.1296 | -0.25958 | -0.034504 | 0.079217 | -0.004219 | 0.035585 | 121.585 | 121.7723 | 121.2617 | 121.4146 | 0.071487 | -0.17331 | -0.13562 | -0.18985 | -0.096497 | -0.11587 | -0.24585 | -0.020771 | 0.09295 | 0.009514 | 0.049318 | 121.5987 | 121.786 | 121.2755 | 121.4283 | -121.6195 | -121.2962 | -121.5892 | -121.266
1360.9844 | 121.8658 | -121.7056 | 0.13275 | 0.071489 | -0.19162 | -0.15394 | -0.20816 | -0.12396 | -0.12044 | -0.25958 | -0.034504 | 0.07006 | -0.004219 | 0.035585 | 121.585 | 121.7723 | 121.2617 | 121.41 | 0.085222 | -0.17789 | -0.1402 | -0.19442 | -0.11023 | -0.10671 | -0.24585 | -0.020771 | 0.083793 | 0.009514 | 0.049318 | 121.5987 | 121.786 | 121.2755 | 121.4237 | -121.6195 | -121.2962 | -121.5892 | -121.266
1362.7344 | 121.8704 | -121.7056 | 0.10071 | 0.062332 | -0.20078 | -0.14936 | -0.21731 | -0.11481 | -0.12502 | -0.25958 | -0.039082 | 0.07006 | -0.008798 | 0.026427 | 121.5896 | 121.7723 | 121.2617 | 121.41 | 0.076065 | -0.18705 | -0.13562 | -0.20358 | -0.10107 | -0.11129 | -0.24585 | -0.025349 | 0.083793 | 0.004935 | 0.04016 | 121.6033 | 121.786 | 121.2755 | 121.4237 | -121.6287 | -121.3008 | -121.5984 | -121.2705
1364.4062 | 121.9894 | -121.6553 | 0.082397 | 0.06691 | -0.19162 | -0.15394 | -0.20816 | -0.11481 | -0.13418 | -0.25958 | -0.034504 | 0.07006 | -0.008798 | 0.031006 | 121.5896 | 121.7815 | 121.2663 | 121.4191 | 0.080643 | -0.17789 | -0.1402 | -0.19442 | -0.10107 | -0.12045 | -0.24585 | -0.020771 | 0.083793 | 0.004935 | 0.044739 | 121.6033 | 121.7952 | 121.2801 | 121.4329 | -121.6241 | -121.3008 | -121.5984 | -121.2751
1366.1406 | 122.0032 | -121.6553 | 0.068665 | 0.062332 | -0.1962 | -0.15394 | -0.21731 | -0.11023 | -0.1296 | -0.25958 | -0.043661 | 0.074638 | -0.004219 | 0.026427 | 121.5804 | 121.7677 | 121.2709 | 121.41 | 0.076065 | -0.18247 | -0.1402 | -0.20358 | -0.096497 | -0.11587 | -0.24585 | -0.029928 | 0.088371 | 0.009514 | 0.04016 | 121.5942 | 121.7815 | 121.2846 | 121.4237 | -121.6241 | -121.3146 | -121.5846 | -121.2751
1367.8906 | 121.962 | -121.6553 | 0.086975 | 0.062332 | -0.20078 | -0.15394 | -0.21731 | -0.11939 | -0.14791 | -0.26874 | -0.034504 | 0.07006 | -0.008798 | 0.031006 | 121.585 | 121.7815 | 121.2617 | 121.4237 | 0.076065 | -0.18705 | -0.1402 | -0.20358 | -0.10565 | -0.13418 | -0.255 | -0.020771 | 0.083793 | 0.004935 | 0.044739 | 121.5987 | 121.7952 | 121.2755 | 121.4374 | -121.6195 | -121.2962 | -121.5938 | -121.2705
1369.5625 | 121.9986 | -121.6507 | 0.091553 | 0.06691 | -0.20536 | -0.15394 | -0.22189 | -0.11939 | -0.13418 | -0.26416 | -0.043661 | 0.07006 | -0.008798 | 0.026427 | 121.5942 | 121.7815 | 121.2755 | 121.4283 | 0.080643 | -0.19163 | -0.1402 | -0.20816 | -0.10565 | -0.12045 | -0.25042 | -0.029928 | 0.083793 | 0.004935 | 0.04016 | 121.6079 | 121.7952 | 121.2892 | 121.442 | -121.6378 | -121.3191 | -121.603 | -121.2843
1371.2969 | 121.8704 | -121.6965 | 0.14191 | 0.06691 | -0.20078 | -0.15851 | -0.21731 | -0.12854 | -0.1296 | -0.27331 | -0.034504 | 0.07006 | -0.008798 | 0.031006 | 121.5896 | 121.786 | 121.2755 | 121.4146 | 0.080643 | -0.18705 | -0.14478 | -0.20358 | -0.11481 | -0.11587 | -0.25958 | -0.020771 | 0.083793 | 0.004935 | 0.044739 | 121.6033 | 121.7998 | 121.2892 | 121.4283 | -121.6241 | -121.31 | -121.5984 | -121.2843
1372.9844 | 122.0078 | -121.6782 | 0.091553 | 0.06691 | -0.20994 | -0.15851 | -0.21274 | -0.12396 | -0.13876 | -0.27331 | -0.039082 | 0.074638 | -0.008798 | 0.031006 | 121.5942 | 121.7769 | 121.2709 | 121.4283 | 0.080643 | -0.1962 | -0.14478 | -0.199 | -0.11023 | -0.12502 | -0.25958 | -0.025349 | 0.088371 | 0.004935 | 0.044739 | 121.6079 | 121.7906 | 121.2846 | 121.442 | -121.6332 | -121.31 | -121.603 | -121.2797
1374.7188 | 122.0078 | -121.669 | 0.059509 | 0.062332 | -0.20536 | -0.16309 | -0.22189 | -0.12396 | -0.13418 | -0.27331 | -0.043661 | 0.07006 | -0.004219 | 0.031006 | 121.5987 | 121.786 | 121.2801 | 121.4237 | 0.076065 | -0.19163 | -0.14936 | -0.20816 | -0.11023 | -0.12045 | -0.25958 | -0.029928 | 0.083793 | 0.009514 | 0.044739 | 121.6125 | 121.7998 | 121.2938 | 121.4374 | -121.6424 | -121.3237 | -121.603 | -121.2843
1376.4531 | 121.994 | -121.6599 | 0.068665 | 0.062332 | -0.21452 | -0.16309 | -0.22189 | -0.12396 | -0.13418 | -0.26874 | -0.034504 | 0.074638 | -0.013376 | 0.026427 | 121.5942 | 121.786 | 121.2709 | 121.4237 | 0.076065 | -0.20078 | -0.14936 | -0.20816 | -0.11023 | -0.12045 | -0.255 | -0.020771 | 0.088371 | 0.000357 | 0.04016 | 121.6079 | 121.7998 | 121.2846 | 121.4374 | -121.6287 | -121.3054 | -121.6075 | -121.2843
1378.1406 | 121.8567 | -121.7239 | 0.11444 | 0.06691 | -0.20994 | -0.16767 | -0.21731 | -0.11939 | -0.13418 | -0.27331 | -0.039082 | 0.07006 | -0.013376 | 0.026427 | 121.5987 | 121.7815 | 121.2755 | 121.4283 | 0.080643 | -0.1962 | -0.15394 | -0.20358 | -0.10565 | -0.12045 | -0.25958 | -0.025349 | 0.083793 | 0.000357 | 0.04016 | 121.6125 | 121.7952 | 121.2892 | 121.442 | -121.6378 | -121.3146 | -121.6121 | -121.2889
1379.875 | 121.9986 | -121.6599 | 0.086975 | 0.062332 | -0.22367 | -0.16767 | -0.23105 | -0.12854 | -0.13418 | -0.26874 | -0.039082 | 0.07006 | -0.004219 | 0.026427 | 121.5987 | 121.7815 | 121.2755 | 121.4283 | 0.076065 | -0.20994 | -0.15394 | -0.21732 | -0.11481 | -0.12045 | -0.255 | -0.025349 | 0.083793 | 0.009514 | 0.04016 | 121.6125 | 121.7952 | 121.2892 | 121.442 | -121.6378 | -121.3146 | -121.603 | -121.2797
1381.5625 | 121.8842 | -121.7194 | 0.10529 | 0.06691 | -0.2191 | -0.15851 | -0.22189 | -0.12854 | -0.13876 | -0.27331 | -0.039082 | 0.07006 | -0.008798 | 0.031006 | 121.6079 | 121.7815 | 121.2755 | 121.4375 | 0.080643 | -0.20536 | -0.14478 | -0.20816 | -0.11481 | -0.12502 | -0.25958 | -0.025349 | 0.083793 | 0.004935 | 0.044739 | 121.6216 | 121.7952 | 121.2892 | 121.4512 | -121.647 | -121.3146 | -121.6167 | -121.2843
1383.3125 | 122.0215 | -121.6736 | 0.082397 | 0.071489 | -0.22367 | -0.16767 | -0.22647 | -0.13312 | -0.13418 | -0.27789 | -0.039082 | 0.07006 | 0.000359 | 0.035585 | 121.5942 | 121.786 | 121.2755 | 121.4283 | 0.085222 | -0.20994 | -0.15394 | -0.21274 | -0.11939 | -0.12045 | -0.26416 | -0.025349 | 0.083793 | 0.014092 | 0.049318 | 121.6079 | 121.7998 | 121.2892 | 121.442 | -121.6332 | -121.3146 | -121.5938 | -121.2751
1385.0469 | 121.9986 | -121.669 | 0.059509 | 0.06691 | -0.22825 | -0.16767 | -0.23105 | -0.12854 | -0.13876 | -0.27789 | -0.034504 | 0.07006 | -0.008798 | 0.021847 | 121.6033 | 121.7906 | 121.2801 | 121.4283 | 0.080643 | -0.21452 | -0.15394 | -0.21732 | -0.11481 | -0.12502 | -0.26416 | -0.020771 | 0.083793 | 0.004935 | 0.03558 | 121.617 | 121.8043 | 121.2938 | 121.442 | -121.6378 | -121.3146 | -121.6121 | -121.2889
1386.7969 | 122.0078 | -121.6736 | 0.068665 | 0.071489 | -0.22825 | -0.16767 | -0.23105 | -0.12854 | -0.14334 | -0.27789 | -0.034504 | 0.07006 | -0.004219 | 0.026427 | 121.6033 | 121.7906 | 121.2755 | 121.4283 | 0.085222 | -0.21452 | -0.15394 | -0.21732 | -0.11481 | -0.1296 | -0.26416 | -0.020771 | 0.083793 | 0.009514 | 0.04016 | 121.617 | 121.8043 | 121.2892 | 121.442 | -121.6378 | -121.31 | -121.6075 | -121.2797
1388.4688 | 121.9757 | -121.6736 | 0.091553 | 0.062332 | -0.22367 | -0.16767 | -0.23105 | -0.1377 | -0.14334 | -0.28705 | -0.039082 | 0.07006 | -0.004219 | 0.031006 | 121.5942 | 121.7906 | 121.2892 | 121.4329 | 0.076065 | -0.20994 | -0.15394 | -0.21732 | -0.12396 | -0.1296 | -0.27332 | -0.025349 | 0.083793 | 0.009514 | 0.044739 | 121.6079 | 121.8043 | 121.3029 | 121.4466 | -121.6332 | -121.3283 | -121.5984 | -121.2934
1390.2188 | 122.0032 | -121.669 | 0.09613 | 0.06691 | -0.22367 | -0.17683 | -0.23105 | -0.13312 | -0.14334 | -0.28705 | -0.039082 | 0.074638 | -0.013376 | 0.026427 | 121.6079 | 121.7952 | 121.2892 | 121.4329 | 0.080643 | -0.20994 | -0.1631 | -0.21732 | -0.11939 | -0.1296 | -0.27332 | -0.025349 | 0.088371 | 0.000357 | 0.04016 | 121.6216 | 121.8089 | 121.3029 | 121.4466 | -121.647 | -121.3283 | -121.6213 | -121.3026
1391.9531 | 121.875 | -121.7422 | 0.12817 | 0.062332 | -0.22825 | -0.16767 | -0.23105 | -0.1377 | -0.14791 | -0.27789 | -0.029925 | 0.07006 | -0.004219 | 0.031006 | 121.617 | 121.7906 | 121.2892 | 121.4375 | 0.076065 | -0.21452 | -0.15394 | -0.21732 | -0.12396 | -0.13418 | -0.26416 | -0.016192 | 0.083793 | 0.009514 | 0.044739 | 121.6308 | 121.8043 | 121.3029 | 121.4512 | -121.647 | -121.3191 | -121.6213 | -121.2934
1393.625 | 121.9391 | -121.7102 | 0.10529 | 0.06691 | -0.23283 | -0.16767 | -0.23105 | -0.13312 | -0.14791 | -0.28705 | -0.039082 | 0.074638 | 0.000359 | 0.031006 | 121.6033 | 121.7952 | 121.2892 | 121.4375 | 0.080643 | -0.2191 | -0.15394 | -0.21732 | -0.11939 | -0.13418 | -0.27332 | -0.025349 | 0.088371 | 0.014092 | 0.044739 | 121.617 | 121.8089 | 121.3029 | 121.4512 | -121.6424 | -121.3283 | -121.603 | -121.2889
1395.3594 | 121.907 | -121.7148 | 0.10986 | 0.071489 | -0.22825 | -0.17683 | -0.24021 | -0.1377 | -0.14791 | -0.28247 | -0.029925 | 0.07006 | -0.013376 | 0.026427 | 121.6125 | 121.7906 | 121.2801 | 121.4283 | 0.085222 | -0.21452 | -0.1631 | -0.22647 | -0.12396 | -0.13418 | -0.26874 | -0.016192 | 0.083793 | 0.000357 | 0.04016 | 121.6262 | 121.8043 | 121.2938 | 121.442 | -121.6424 | -121.31 | -121.6258 | -121.2934
1397.0781 | 121.9025 | -121.7194 | 0.10529 | 0.06691 | -0.22825 | -0.17683 | -0.23563 | -0.1377 | -0.14791 | -0.28247 | -0.039082 | 0.07006 | 0.000359 | 0.035585 | 121.6125 | 121.7952 | 121.2846 | 121.4466 | 0.080643 | -0.21452 | -0.1631 | -0.2219 | -0.12396 | -0.13418 | -0.26874 | -0.025349 | 0.083793 | 0.014092 | 0.049318 | 121.6262 | 121.8089 | 121.2984 | 121.4603 | -121.6516 | -121.3237 | -121.6121 | -121.2843
1398.7656 | 121.9803 | -121.6736 | 0.10529 | 0.06691 | -0.23741 | -0.18599 | -0.24021 | -0.1377 | -0.15249 | -0.28705 | -0.029925 | 0.065481 | -0.008798 | 0.031006 | 121.6125 | 121.7952 | 121.2892 | 121.4375 | 0.080643 | -0.22368 | -0.17225 | -0.22647 | -0.12396 | -0.13876 | -0.27332 | -0.016192 | 0.079214 | 0.004935 | 0.044739 | 121.6262 | 121.8089 | 121.3029 | 121.4512 | -121.6424 | -121.3191 | -121.6213 | -121.298
1400.5 | 121.8842 | -121.7102 | 0.10529 | 0.062332 | -0.23283 | -0.18141 | -0.24021 | -0.13312 | -0.14791 | -0.28705 | -0.039082 | 0.074638 | -0.004219 | 0.035585 | 121.6079 | 121.7998 | 121.2801 | 121.442 | 0.076065 | -0.2191 | -0.16768 | -0.22647 | -0.11939 | -0.13418 | -0.27332 | -0.025349 | 0.088371 | 0.009514 | 0.049318 | 121.6216 | 121.8135 | 121.2938 | 121.4558 | -121.647 | -121.3191 | -121.6121 | -121.2843
1402.25 | 121.875 | -121.7468 | 0.11444 | 0.06691 | -0.22825 | -0.19057 | -0.24936 | -0.14685 | -0.15707 | -0.29163 | -0.034504 | 0.07006 | -0.013376 | 0.035585 | 121.6216 | 121.7906 | 121.2892 | 121.4375 | 0.080643 | -0.21452 | -0.17683 | -0.23563 | -0.13312 | -0.14334 | -0.27789 | -0.020771 | 0.083793 | 0.000357 | 0.049318 | 121.6354 | 121.8043 | 121.3029 | 121.4512 | -121.6561 | -121.3237 | -121.635 | -121.3026
1403.9375 | 121.875 | -121.7285 | 0.11444 | 0.06691 | -0.23741 | -0.18599 | -0.24021 | -0.14685 | -0.15707 | -0.29163 | -0.039082 | 0.07006 | -0.004219 | 0.040164 | 121.617 | 121.7998 | 121.2892 | 121.4375 | 0.080643 | -0.22368 | -0.17225 | -0.22647 | -0.13312 | -0.14334 | -0.27789 | -0.025349 | 0.083793 | 0.009514 | 0.053897 | 121.6308 | 121.8135 | 121.3029 | 121.4512 | -121.6561 | -121.3283 | -121.6213 | -121.2934
1405.6719 | 121.9803 | -121.6873 | 0.10529 | 0.062332 | -0.23741 | -0.19057 | -0.24021 | -0.14228 | -0.15707 | -0.30078 | -0.034504 | 0.065481 | -0.008798 | 0.035585 | 121.6216 | 121.8089 | 121.2938 | 121.4466 | 0.076065 | -0.22368 | -0.17683 | -0.22647 | -0.12854 | -0.14334 | -0.28705 | -0.020771 | 0.079214 | 0.004935 | 0.049318 | 121.6354 | 121.8227 | 121.3075 | 121.4603 | -121.6561 | -121.3283 | -121.6304 | -121.3026
1407.4062 | 121.8933 | -121.7422 | 0.10529 | 0.062332 | -0.23741 | -0.18599 | -0.25852 | -0.15601 | -0.15707 | -0.2962 | -0.029925 | 0.074638 | -0.008798 | 0.035585 | 121.617 | 121.7952 | 121.2938 | 121.442 | 0.076065 | -0.22368 | -0.17225 | -0.24479 | -0.14228 | -0.14334 | -0.28247 | -0.016192 | 0.088371 | 0.004935 | 0.049318 | 121.6308 | 121.8089 | 121.3075 | 121.4558 | -121.647 | -121.3237 | -121.6258 | -121.3026
1409.1406 | 122.0032 | -121.7056 | 0.09613 | 0.062332 | -0.24199 | -0.19057 | -0.24479 | -0.15601 | -0.15707 | -0.30078 | -0.034504 | 0.07006 | -0.008798 | 0.031006 | 121.6125 | 121.7952 | 121.2846 | 121.4466 | 0.076065 | -0.22826 | -0.17683 | -0.23105 | -0.14228 | -0.14334 | -0.28705 | -0.020771 | 0.083793 | 0.004935 | 0.044739 | 121.6262 | 121.8089 | 121.2984 | 121.4603 | -121.647 | -121.3191 | -121.6213 | -121.2934
1410.875 | 121.8796 | -121.7194 | 0.10071 | 0.06691 | -0.24657 | -0.18599 | -0.24936 | -0.14685 | -0.16623 | -0.2962 | -0.034504 | 0.07006 | -0.004219 | 0.035585 | 121.6125 | 121.8089 | 121.2938 | 121.4558 | 0.080643 | -0.23283 | -0.17225 | -0.23563 | -0.13312 | -0.15249 | -0.28247 | -0.020771 | 0.083793 | 0.009514 | 0.049318 | 121.6262 | 121.8227 | 121.3075 | 121.4695 | -121.647 | -121.3283 | -121.6167 | -121.298
1412.5625 | 121.962 | -121.6919 | 0.07782 | 0.053175 | -0.25115 | -0.19057 | -0.24936 | -0.16059 | -0.16623 | -0.30078 | -0.025347 | 0.07006 | -0.008798 | 0.035585 | 121.617 | 121.8044 | 121.2984 | 121.4466 | 0.066908 | -0.23741 | -0.17683 | -0.23563 | -0.14685 | -0.15249 | -0.28705 | -0.011614 | 0.083793 | 0.004935 | 0.049318 | 121.6308 | 121.8181 | 121.3121 | 121.4603 | -121.6424 | -121.3237 | -121.6258 | -121.3072
1414.3125 | 122.0078 | -121.6827 | 0.091553 | 0.062332 | -0.24657 | -0.19514 | -0.24936 | -0.15601 | -0.15707 | -0.30078 | -0.029925 | 0.074638 | -0.008798 | 0.035585 | 121.6079 | 121.8089 | 121.2938 | 121.4466 | 0.076065 | -0.23283 | -0.18141 | -0.23563 | -0.14228 | -0.14334 | -0.28705 | -0.016192 | 0.088371 | 0.004935 | 0.049318 | 121.6216 | 121.8227 | 121.3075 | 121.4603 | -121.6378 | -121.3237 | -121.6167 | -121.3026
1416.0625 | 121.9803 | -121.701 | 0.086975 | 0.06691 | -0.24657 | -0.19057 | -0.24479 | -0.15143 | -0.16623 | -0.30536 | -0.034504 | 0.07006 | 0.000359 | 0.026427 | 121.617 | 121.8089 | 121.2938 | 121.4512 | 0.080643 | -0.23283 | -0.17683 | -0.23105 | -0.1377 | -0.15249 | -0.29163 | -0.020771 | 0.083793 | 0.014092 | 0.04016 | 121.6308 | 121.8227 | 121.3075 | 121.4649 | -121.6516 | -121.3283 | -121.6167 | -121.2934
1417.7656 | 121.9894 | -121.6827 | 0.082397 | 0.071489 | -0.24657 | -0.19972 | -0.25394 | -0.15601 | -0.16623 | -0.30536 | -0.034504 | 0.07006 | -0.008798 | 0.026427 | 121.617 | 121.8044 | 121.2984 | 121.442 | 0.085222 | -0.23283 | -0.18599 | -0.24021 | -0.14228 | -0.15249 | -0.29163 | -0.020771 | 0.083793 | 0.004935 | 0.04016 | 121.6308 | 121.8181 | 121.3121 | 121.4558 | -121.6516 | -121.3329 | -121.6258 | -121.3072
1419.5 | 121.9986 | -121.6965 | 0.086975 | 0.057754 | -0.24657 | -0.19057 | -0.2631 | -0.16059 | -0.17081 | -0.30536 | -0.039082 | 0.07006 | -0.013376 | 0.035585 | 121.6262 | 121.7998 | 121.303 | 121.4512 | 0.071487 | -0.23283 | -0.17683 | -0.24937 | -0.14685 | -0.15707 | -0.29163 | -0.025349 | 0.083793 | 0.000357 | 0.049318 | 121.6399 | 121.8135 | 121.3167 | 121.4649 | -121.6653 | -121.342 | -121.6396 | -121.3163
1421.25 | 121.9894 | -121.7102 | 0.091553 | 0.06691 | -0.25572 | -0.19514 | -0.25394 | -0.15143 | -0.17081 | -0.30536 | -0.034504 | 0.07006 | 0.000359 | 0.026427 | 121.617 | 121.8135 | 121.2892 | 121.442 | 0.080643 | -0.24199 | -0.18141 | -0.24021 | -0.1377 | -0.15707 | -0.29163 | -0.020771 | 0.083793 | 0.014092 | 0.04016 | 121.6308 | 121.8272 | 121.3029 | 121.4558 | -121.6516 | -121.3237 | -121.6167 | -121.2889
1422.9375 | 122.0123 | -121.7056 | 0.086975 | 0.06691 | -0.25572 | -0.19972 | -0.2631 | -0.16059 | -0.17539 | -0.31452 | -0.034504 | 0.074638 | -0.008798 | 0.031006 | 121.6216 | 121.8044 | 121.303 | 121.4558 | 0.080643 | -0.24199 | -0.18599 | -0.24937 | -0.14685 | -0.16165 | -0.30078 | -0.020771 | 0.088371 | 0.004935 | 0.044739 | 121.6354 | 121.8181 | 121.3167 | 121.4695 | -121.6561 | -121.3375 | -121.6304 | -121.3117
1424.6719 | 122.0215 | -121.6873 | 0.07782 | 0.071489 | -0.25115 | -0.19972 | -0.2631 | -0.16059 | -0.17539 | -0.30994 | -0.034504 | 0.07006 | -0.013376 | 0.026427 | 121.617 | 121.8089 | 121.303 | 121.4466 | 0.085222 | -0.23741 | -0.18599 | -0.24937 | -0.14685 | -0.16165 | -0.29621 | -0.020771 | 0.083793 | 0.000357 | 0.04016 | 121.6308 | 121.8227 | 121.3167 | 121.4603 | -121.6516 | -121.3375 | -121.6304 | -121.3163
1426.4062 | 121.907 | -121.7148 | 0.12817 | 0.057754 | -0.25572 | -0.2043 | -0.26768 | -0.16059 | -0.17539 | -0.30994 | -0.034504 | 0.079217 | -0.004219 | 0.031006 | 121.6308 | 121.8044 | 121.303 | 121.4558 | 0.071487 | -0.24199 | -0.19057 | -0.25394 | -0.14685 | -0.16165 | -0.29621 | -0.020771 | 0.09295 | 0.009514 | 0.044739 | 121.6445 | 121.8181 | 121.3167 | 121.4695 | -121.6653 | -121.3375 | -121.635 | -121.3072
1428.1562 | 121.9116 | -121.7239 | 0.11444 | 0.062332 | -0.25572 | -0.19514 | -0.25852 | -0.16517 | -0.17996 | -0.31452 | -0.034504 | 0.074638 | -0.008798 | 0.026427 | 121.6216 | 121.8135 | 121.303 | 121.4512 | 0.076065 | -0.24199 | -0.18141 | -0.24479 | -0.15143 | -0.16623 | -0.30078 | -0.020771 | 0.088371 | 0.004935 | 0.04016 | 121.6354 | 121.8272 | 121.3167 | 121.4649 | -121.6561 | -121.3375 | -121.6304 | -121.3117
1429.8906 | 121.9025 | -121.7285 | 0.10071 | 0.062332 | -0.26488 | -0.2043 | -0.2631 | -0.16974 | -0.17539 | -0.30994 | -0.025347 | 0.074638 | 0.000359 | 0.035585 | 121.6308 | 121.8089 | 121.3075 | 121.4603 | 0.076065 | -0.25115 | -0.19057 | -0.24937 | -0.15601 | -0.16165 | -0.29621 | -0.011614 | 0.088371 | 0.014092 | 0.049318 | 121.6445 | 121.8227 | 121.3213 | 121.4741 | -121.6561 | -121.3329 | -121.6304 | -121.3072
1431.5781 | 121.9528 | -121.7468 | 0.11902 | 0.062332 | -0.2603 | -0.21804 | -0.27226 | -0.16059 | -0.17996 | -0.30994 | -0.039082 | 0.065481 | -0.004219 | 0.035585 | 121.6308 | 121.8089 | 121.3075 | 121.4512 | 0.076065 | -0.24657 | -0.2043 | -0.25852 | -0.14685 | -0.16623 | -0.29621 | -0.025349 | 0.079214 | 0.009514 | 0.049318 | 121.6445 | 121.8227 | 121.3213 | 121.4649 | -121.6699 | -121.3466 | -121.635 | -121.3117
1433.3125 | 121.9757 | -121.701 | 0.11444 | 0.057754 | -0.2603 | -0.20888 | -0.26768 | -0.16974 | -0.18912 | -0.32367 | -0.039082 | 0.074638 | -0.013376 | 0.026427 | 121.6308 | 121.8135 | 121.303 | 121.4558 | 0.071487 | -0.24657 | -0.19515 | -0.25394 | -0.15601 | -0.17539 | -0.30994 | -0.025349 | 0.088371 | 0.000357 | 0.04016 | 121.6445 | 121.8272 | 121.3167 | 121.4695 | -121.6699 | -121.342 | -121.6442 | -121.3163
1434.9844 | 121.9894 | -121.7056 | 0.086975 | 0.06691 | -0.25572 | -0.21346 | -0.27226 | -0.16974 | -0.17539 | -0.32367 | -0.034504 | 0.074638 | -0.004219 | 0.035585 | 121.6308 | 121.8227 | 121.2984 | 121.4558 | 0.080643 | -0.24199 | -0.19973 | -0.25852 | -0.15601 | -0.16165 | -0.30994 | -0.020771 | 0.088371 | 0.009514 | 0.049318 | 121.6445 | 121.8364 | 121.3121 | 121.4695 | -121.6653 | -121.3329 | -121.635 | -121.3026
1436.7344 | 122.0123 | -121.6644 | 0.07782 | 0.057754 | -0.2603 | -0.21346 | -0.26768 | -0.16517 | -0.18454 | -0.3191 | -0.034504 | 0.079217 | 0.000359 | 0.026427 | 121.6262 | 121.8135 | 121.303 | 121.4558 | 0.071487 | -0.24657 | -0.19973 | -0.25394 | -0.15143 | -0.17081 | -0.30536 | -0.020771 | 0.09295 | 0.014092 | 0.04016 | 121.6399 | 121.8272 | 121.3167 | 121.4695 | -121.6607 | -121.3375 | -121.6258 | -121.3026
1438.4844 | 121.9345 | -121.7239 | 0.091553 | 0.062332 | -0.26488 | -0.21804 | -0.27226 | -0.16059 | -0.18912 | -0.32367 | -0.043661 | 0.074638 | -0.004219 | 0.040164 | 121.617 | 121.8181 | 121.3075 | 121.4603 | 0.076065 | -0.25115 | -0.2043 | -0.25852 | -0.14685 | -0.17539 | -0.30994 | -0.029928 | 0.088371 | 0.009514 | 0.053897 | 121.6308 | 121.8318 | 121.3213 | 121.4741 | -121.6607 | -121.3512 | -121.6213 | -121.3117
1440.2344 | 122.0398 | -121.6827 | 0.10071 | 0.062332 | -0.26488 | -0.21346 | -0.27683 | -0.16974 | -0.18454 | -0.32367 | -0.039082 | 0.07006 | -0.004219 | 0.031006 | 121.6262 | 121.8227 | 121.3075 | 121.4603 | 0.076065 | -0.25115 | -0.19973 | -0.2631 | -0.15601 | -0.17081 | -0.30994 | -0.025349 | 0.083793 | 0.009514 | 0.044739 | 121.6399 | 121.8364 | 121.3213 | 121.4741 | -121.6653 | -121.3466 | -121.6304 | -121.3117
1441.9219 | 122.0169 | -121.7148 | 0.07782 | 0.071489 | -0.27404 | -0.22262 | -0.27683 | -0.16517 | -0.18454 | -0.32825 | -0.034504 | 0.065481 | 0.000359 | 0.031006 | 121.6262 | 121.8181 | 121.303 | 121.4512 | 0.085222 | -0.26031 | -0.20888 | -0.2631 | -0.15143 | -0.17081 | -0.31452 | -0.020771 | 0.079214 | 0.014092 | 0.044739 | 121.6399 | 121.8318 | 121.3167 | 121.4649 | -121.6607 | -121.3375 | -121.6258 | -121.3026
1443.6719 | 122.0352 | -121.701 | 0.091553 | 0.062332 | -0.26946 | -0.21804 | -0.27226 | -0.17432 | -0.18454 | -0.3191 | -0.034504 | 0.074638 | -0.008798 | 0.031006 | 121.6262 | 121.8135 | 121.3121 | 121.4512 | 0.076065 | -0.25573 | -0.2043 | -0.25852 | -0.16059 | -0.17081 | -0.30536 | -0.020771 | 0.088371 | 0.004935 | 0.044739 | 121.6399 | 121.8272 | 121.3258 | 121.4649 | -121.6607 | -121.3466 | -121.635 | -121.3209
1445.4219 | 121.9757 | -121.7285 | 0.086975 | 0.062332 | -0.27404 | -0.21804 | -0.28141 | -0.16974 | -0.18912 | -0.32367 | -0.039082 | 0.074638 | 0.000359 | 0.026427 | 121.6308 | 121.8181 | 121.3121 | 121.4512 | 0.076065 | -0.26031 | -0.2043 | -0.26768 | -0.15601 | -0.17539 | -0.30994 | -0.025349 | 0.088371 | 0.014092 | 0.04016 | 121.6445 | 121.8318 | 121.3258 | 121.4649 | -121.6699 | -121.3512 | -121.6304 | -121.3117
1447.0938 | 122.0215 | -121.701 | 0.073242 | 0.057754 | -0.26946 | -0.22719 | -0.27683 | -0.1789 | -0.1937 | -0.32367 | -0.034504 | 0.074638 | -0.004219 | 0.031006 | 121.6308 | 121.8181 | 121.3121 | 121.4558 | 0.071487 | -0.25573 | -0.21346 | -0.2631 | -0.16517 | -0.17997 | -0.30994 | -0.020771 | 0.088371 | 0.009514 | 0.044739 | 121.6445 | 121.8318 | 121.3258 | 121.4695 | -121.6653 | -121.3466 | -121.635 | -121.3163
1448.8438 | 122.0169 | -121.7148 | 0.073242 | 0.062332 | -0.27862 | -0.22719 | -0.28141 | -0.1789 | -0.18912 | -0.33283 | -0.034504 | 0.074638 | 0.000359 | 0.040164 | 121.6354 | 121.8181 | 121.3075 | 121.4558 | 0.076065 | -0.26489 | -0.21346 | -0.26768 | -0.16517 | -0.17539 | -0.3191 | -0.020771 | 0.088371 | 0.014092 | 0.053897 | 121.6491 | 121.8318 | 121.3213 | 121.4695 | -121.6699 | -121.342 | -121.635 | -121.3072
1450.5781 | 122.0123 | -121.6827 | 0.086975 | 0.062332 | -0.27404 | -0.22719 | -0.28141 | -0.17432 | -0.1937 | -0.32367 | -0.034504 | 0.079217 | 0.000359 | 0.040164 | 121.6354 | 121.8227 | 121.3075 | 121.4558 | 0.076065 | -0.26031 | -0.21346 | -0.26768 | -0.16059 | -0.17997 | -0.30994 | -0.020771 | 0.09295 | 0.014092 | 0.053897 | 121.6491 | 121.8364 | 121.3213 | 121.4695 | -121.6699 | -121.342 | -121.635 | -121.3072
1452.3125 | 122.0261 | -121.7468 | 0.091553 | 0.06691 | -0.2832 | -0.22262 | -0.27683 | -0.17432 | -0.1937 | -0.33283 | -0.029925 | 0.060902 | 0.000359 | 0.040164 | 121.6308 | 121.8227 | 121.3121 | 121.4695 | 0.080643 | -0.26947 | -0.20888 | -0.2631 | -0.16059 | -0.17997 | -0.3191 | -0.016192 | 0.074635 | 0.014092 | 0.053897 | 121.6445 | 121.8364 | 121.3258 | 121.4832 | -121.6607 | -121.342 | -121.6304 | -121.3117
1453.9844 | 121.9574 | -121.7148 | 0.11902 | 0.06691 | -0.27862 | -0.22719 | -0.28599 | -0.18348 | -0.1937 | -0.33283 | -0.029925 | 0.07006 | -0.004219 | 0.035585 | 121.6354 | 121.8227 | 121.3167 | 121.4649 | 0.080643 | -0.26489 | -0.21346 | -0.27226 | -0.16974 | -0.17997 | -0.3191 | -0.016192 | 0.083793 | 0.009514 | 0.049318 | 121.6491 | 121.8364 | 121.3304 | 121.4787 | -121.6653 | -121.3466 | -121.6396 | -121.3209
1455.7188 | 121.962 | -121.7514 | 0.10986 | 0.06691 | -0.27862 | -0.23177 | -0.28599 | -0.1789 | -0.20286 | -0.32825 | -0.034504 | 0.079217 | -0.004219 | 0.031006 | 121.6399 | 121.8181 | 121.3121 | 121.4649 | 0.080643 | -0.26489 | -0.21804 | -0.27226 | -0.16517 | -0.18912 | -0.31452 | -0.020771 | 0.09295 | 0.009514 | 0.044739 | 121.6537 | 121.8318 | 121.3258 | 121.4787 | -121.6744 | -121.3466 | -121.6442 | -121.3163
1457.4531 | 121.907 | -121.7606 | 0.11902 | 0.057754 | -0.28778 | -0.22719 | -0.29057 | -0.1789 | -0.19828 | -0.33741 | -0.034504 | 0.074638 | 0.000359 | 0.035585 | 121.6399 | 121.8181 | 121.3167 | 121.4695 | 0.071487 | -0.27404 | -0.21346 | -0.27684 | -0.16517 | -0.18454 | -0.32367 | -0.020771 | 0.088371 | 0.014092 | 0.049318 | 121.6537 | 121.8318 | 121.3304 | 121.4832 | -121.6744 | -121.3512 | -121.6396 | -121.3163
1459.1875 | 121.9025 | -121.7697 | 0.13733 | 0.06691 | -0.27862 | -0.22262 | -0.28599 | -0.18805 | -0.19828 | -0.33741 | -0.029925 | 0.07006 | -0.004219 | 0.026427 | 121.6399 | 121.8227 | 121.3167 | 121.4649 | 0.080643 | -0.26489 | -0.20888 | -0.27226 | -0.17432 | -0.18454 | -0.32367 | -0.016192 | 0.083793 | 0.009514 | 0.04016 | 121.6537 | 121.8364 | 121.3304 | 121.4787 | -121.6699 | -121.3466 | -121.6442 | -121.3209
1460.8594 | 121.9254 | -121.7422 | 0.1236 | 0.053175 | -0.27862 | -0.23635 | -0.28599 | -0.1789 | -0.20286 | -0.33283 | -0.025347 | 0.079217 | 0.000359 | 0.031006 | 121.6354 | 121.8272 | 121.3121 | 121.4649 | 0.066908 | -0.26489 | -0.22262 | -0.27226 | -0.16517 | -0.18912 | -0.3191 | -0.011614 | 0.09295 | 0.014092 | 0.044739 | 121.6491 | 121.841 | 121.3258 | 121.4787 | -121.6607 | -121.3375 | -121.635 | -121.3117
1462.6094 | 121.9574 | -121.7743 | 0.12817 | 0.062332 | -0.28778 | -0.24093 | -0.29057 | -0.19263 | -0.19828 | -0.33283 | -0.034504 | 0.074638 | 0.000359 | 0.035585 | 121.6399 | 121.8227 | 121.3213 | 121.4695 | 0.076065 | -0.27404 | -0.2272 | -0.27684 | -0.1789 | -0.18454 | -0.3191 | -0.020771 | 0.088371 | 0.014092 | 0.049318 | 121.6537 | 121.8364 | 121.335 | 121.4832 | -121.6744 | -121.3558 | -121.6396 | -121.3209
1464.3438 | 121.9208 | -121.7377 | 0.13733 | 0.06691 | -0.28778 | -0.24093 | -0.29515 | -0.18348 | -0.20286 | -0.34199 | -0.029925 | 0.07006 | -0.004219 | 0.035585 | 121.6354 | 121.8318 | 121.3167 | 121.4649 | 0.080643 | -0.27404 | -0.2272 | -0.28142 | -0.16974 | -0.18912 | -0.32825 | -0.016192 | 0.083793 | 0.009514 | 0.049318 | 121.6491 | 121.8456 | 121.3304 | 121.4787 | -121.6653 | -121.3466 | -121.6396 | -121.3209
1466.0156 | 122.0398 | -121.701 | 0.086975 | 0.071489 | -0.28778 | -0.24093 | -0.29057 | -0.19263 | -0.20743 | -0.34656 | -0.034504 | 0.074638 | -0.008798 | 0.026427 | 121.6354 | 121.8227 | 121.3167 | 121.4649 | 0.085222 | -0.27404 | -0.2272 | -0.27684 | -0.1789 | -0.1937 | -0.33283 | -0.020771 | 0.088371 | 0.004935 | 0.04016 | 121.6491 | 121.8364 | 121.3304 | 121.4787 | -121.6699 | -121.3512 | -121.6442 | -121.3255
1467.75 | 121.907 | -121.7606 | 0.11902 | 0.062332 | -0.29236 | -0.24093 | -0.3043 | -0.19721 | -0.20743 | -0.34199 | -0.025347 | 0.074638 | 0.004937 | 0.035585 | 121.6491 | 121.8364 | 121.3258 | 121.4649 | 0.076065 | -0.27862 | -0.2272 | -0.29057 | -0.18348 | -0.1937 | -0.32825 | -0.011614 | 0.088371 | 0.01867 | 0.049318 | 121.6628 | 121.8501 | 121.3396 | 121.4787 | -121.6744 | -121.3512 | -121.6442 | -121.3209
1469.4844 | 121.9986 | -121.7331 | 0.091553 | 0.06691 | -0.29693 | -0.24551 | -0.29973 | -0.19721 | -0.21201 | -0.34656 | -0.034504 | 0.074638 | 0.004937 | 0.035585 | 121.6445 | 121.8318 | 121.3258 | 121.4787 | 0.080643 | -0.2832 | -0.23178 | -0.28599 | -0.18348 | -0.19828 | -0.33283 | -0.020771 | 0.088371 | 0.01867 | 0.049318 | 121.6582 | 121.8456 | 121.3396 | 121.4924 | -121.679 | -121.3603 | -121.6396 | -121.3209
1471.2188 | 121.9437 | -121.7606 | 0.11444 | 0.06691 | -0.29236 | -0.24551 | -0.3043 | -0.19721 | -0.21201 | -0.34656 | -0.034504 | 0.065481 | -0.004219 | 0.031006 | 121.6491 | 121.8272 | 121.3213 | 121.4695 | 0.080643 | -0.27862 | -0.23178 | -0.29057 | -0.18348 | -0.19828 | -0.33283 | -0.020771 | 0.079214 | 0.009514 | 0.044739 | 121.6628 | 121.841 | 121.335 | 121.4832 | -121.6836 | -121.3558 | -121.6533 | -121.3255
1472.9062 | 122.0444 | -121.6827 | 0.064087 | 0.062332 | -0.29236 | -0.25009 | -0.3043 | -0.19721 | -0.21659 | -0.35114 | -0.029925 | 0.074638 | -0.008798 | 0.035585 | 121.6354 | 121.8227 | 121.3213 | 121.4695 | 0.076065 | -0.27862 | -0.23635 | -0.29057 | -0.18348 | -0.20286 | -0.33741 | -0.016192 | 0.088371 | 0.004935 | 0.049318 | 121.6491 | 121.8364 | 121.335 | 121.4832 | -121.6653 | -121.3512 | -121.6442 | -121.3301
1474.6406 | 121.9025 | -121.7834 | 0.12817 | 0.062332 | -0.29693 | -0.23635 | -0.29973 | -0.20179 | -0.21659 | -0.35114 | -0.025347 | 0.065481 | -0.004219 | 0.035585 | 121.6445 | 121.8364 | 121.3304 | 121.4695 | 0.076065 | -0.2832 | -0.22262 | -0.28599 | -0.18806 | -0.20286 | -0.33741 | -0.011614 | 0.079214 | 0.009514 | 0.049318 | 121.6582 | 121.8501 | 121.3442 | 121.4832 | -121.6699 | -121.3558 | -121.6487 | -121.3346
1476.3125 | 121.9208 | -121.756 | 0.1236 | 0.06691 | -0.30151 | -0.24551 | -0.29973 | -0.20637 | -0.22575 | -0.35114 | -0.034504 | 0.07006 | -0.004219 | 0.031006 | 121.6399 | 121.8272 | 121.3167 | 121.4695 | 0.080643 | -0.28778 | -0.23178 | -0.28599 | -0.19263 | -0.21201 | -0.33741 | -0.020771 | 0.083793 | 0.009514 | 0.044739 | 121.6537 | 121.841 | 121.3304 | 121.4832 | -121.6744 | -121.3512 | -121.6442 | -121.3209
1478.0625 | 121.9711 | -121.7377 | 0.091553 | 0.06691 | -0.30609 | -0.25009 | -0.3043 | -0.20637 | -0.22117 | -0.35114 | -0.039082 | 0.07006 | -0.004219 | 0.035585 | 121.6399 | 121.8364 | 121.3213 | 121.4741 | 0.080643 | -0.29236 | -0.23635 | -0.29057 | -0.19263 | -0.20744 | -0.33741 | -0.025349 | 0.083793 | 0.009514 | 0.049318 | 121.6537 | 121.8501 | 121.335 | 121.4878 | -121.679 | -121.3603 | -121.6442 | -121.3255
1479.8125 | 122.0123 | -121.7148 | 0.091553 | 0.057754 | -0.30609 | -0.25009 | -0.3043 | -0.20179 | -0.22575 | -0.3603 | -0.025347 | 0.079217 | -0.008798 | 0.031006 | 121.6399 | 121.8364 | 121.3258 | 121.4695 | 0.071487 | -0.29236 | -0.23635 | -0.29057 | -0.18806 | -0.21201 | -0.34657 | -0.011614 | 0.09295 | 0.004935 | 0.044739 | 121.6537 | 121.8501 | 121.3396 | 121.4832 | -121.6653 | -121.3512 | -121.6487 | -121.3346
1481.5 | 121.9391 | -121.7606 | 0.1236 | 0.06691 | -0.30609 | -0.24551 | -0.31346 | -0.19721 | -0.22575 | -0.3603 | -0.029925 | 0.079217 | -0.008798 | 0.035585 | 121.6491 | 121.841 | 121.3258 | 121.4832 | 0.080643 | -0.29236 | -0.23178 | -0.29973 | -0.18348 | -0.21201 | -0.34657 | -0.016192 | 0.09295 | 0.004935 | 0.049318 | 121.6628 | 121.8547 | 121.3396 | 121.497 | -121.679 | -121.3558 | -121.6579 | -121.3346
1483.25 | 121.9345 | -121.7606 | 0.11444 | 0.06691 | -0.30151 | -0.25924 | -0.31804 | -0.21094 | -0.23033 | -0.3603 | -0.025347 | 0.079217 | 0.000359 | 0.031006 | 121.6537 | 121.841 | 121.3258 | 121.4787 | 0.080643 | -0.28778 | -0.24551 | -0.30431 | -0.19721 | -0.21659 | -0.34657 | -0.011614 | 0.09295 | 0.014092 | 0.044739 | 121.6674 | 121.8547 | 121.3396 | 121.4924 | -121.679 | -121.3512 | -121.6533 | -121.3255
1484.9375 | 121.9757 | -121.7697 | 0.10071 | 0.06691 | -0.30151 | -0.25467 | -0.31804 | -0.21094 | -0.23033 | -0.36488 | -0.029925 | 0.079217 | 0.004937 | 0.031006 | 121.6399 | 121.8364 | 121.3304 | 121.4695 | 0.080643 | -0.28778 | -0.24093 | -0.30431 | -0.19721 | -0.21659 | -0.35114 | -0.016192 | 0.09295 | 0.01867 | 0.044739 | 121.6537 | 121.8501 | 121.3442 | 121.4832 | -121.6699 | -121.3603 | -121.635 | -121.3255
1486.6875 | 121.994 | -121.7148 | 0.091553 | 0.062332 | -0.31067 | -0.26382 | -0.3272 | -0.21094 | -0.22117 | -0.3603 | -0.029925 | 0.079217 | 0.000359 | 0.035585 | 121.6399 | 121.8364 | 121.3258 | 121.4695 | 0.076065 | -0.29694 | -0.25009 | -0.31346 | -0.19721 | -0.20744 | -0.34657 | -0.016192 | 0.09295 | 0.014092 | 0.049318 | 121.6537 | 121.8501 | 121.3396 | 121.4832 | -121.6699 | -121.3558 | -121.6396 | -121.3255
1488.4219 | 122.0673 | -121.701 | 0.086975 | 0.062332 | -0.31983 | -0.2684 | -0.30888 | -0.21094 | -0.23033 | -0.36945 | -0.029925 | 0.07006 | -0.004219 | 0.040164 | 121.6537 | 121.8318 | 121.3258 | 121.4787 | 0.076065 | -0.3061 | -0.25467 | -0.29515 | -0.19721 | -0.21659 | -0.35572 | -0.016192 | 0.083793 | 0.009514 | 0.053897 | 121.6674 | 121.8456 | 121.3396 | 121.4924 | -121.6836 | -121.3558 | -121.6579 | -121.3301
1490.0938 | 121.9025 | -121.7606 | 0.11902 | 0.062332 | -0.31067 | -0.26382 | -0.31346 | -0.20637 | -0.23033 | -0.36945 | -0.020768 | 0.07006 | 0.000359 | 0.035585 | 121.6445 | 121.8364 | 121.3304 | 121.4741 | 0.076065 | -0.29694 | -0.25009 | -0.29973 | -0.19263 | -0.21659 | -0.35572 | -0.007035 | 0.083793 | 0.014092 | 0.049318 | 121.6582 | 121.8501 | 121.3442 | 121.4878 | -121.6653 | -121.3512 | -121.6442 | -121.3301
1491.8281 | 121.9391 | -121.7514 | 0.10986 | 0.06691 | -0.31525 | -0.25924 | -0.32262 | -0.21552 | -0.2349 | -0.36945 | -0.025347 | 0.074638 | 0.000359 | 0.035585 | 121.6537 | 121.8456 | 121.335 | 121.4741 | 0.080643 | -0.30152 | -0.24551 | -0.30889 | -0.20179 | -0.22117 | -0.35572 | -0.011614 | 0.088371 | 0.014092 | 0.049318 | 121.6674 | 121.8593 | 121.3487 | 121.4878 | -121.679 | -121.3603 | -121.6533 | -121.3346
1493.5625 | 121.9757 | -121.7102 | 0.10986 | 0.057754 | -0.31067 | -0.27298 | -0.3272 | -0.2201 | -0.23948 | -0.37403 | -0.025347 | 0.074638 | -0.008798 | 0.026427 | 121.6537 | 121.841 | 121.335 | 121.4741 | 0.071487 | -0.29694 | -0.25925 | -0.31346 | -0.20637 | -0.22575 | -0.3603 | -0.011614 | 0.088371 | 0.004935 | 0.04016 | 121.6674 | 121.8547 | 121.3487 | 121.4878 | -121.679 | -121.3603 | -121.6625 | -121.3438
1495.2969 | 122.0673 | -121.7468 | 0.073242 | 0.06691 | -0.31983 | -0.27756 | -0.33178 | -0.22468 | -0.23948 | -0.37403 | -0.029925 | 0.074638 | -0.004219 | 0.040164 | 121.6537 | 121.8456 | 121.335 | 121.4832 | 0.080643 | -0.3061 | -0.26383 | -0.31804 | -0.21095 | -0.22575 | -0.3603 | -0.016192 | 0.088371 | 0.009514 | 0.053897 | 121.6674 | 121.8593 | 121.3487 | 121.497 | -121.6836 | -121.3649 | -121.6579 | -121.3392
1496.9844 | 122.0352 | -121.7468 | 0.10071 | 0.06691 | -0.32899 | -0.27298 | -0.3272 | -0.22468 | -0.24864 | -0.38319 | -0.029925 | 0.074638 | 0.000359 | 0.035585 | 121.6583 | 121.8364 | 121.3258 | 121.4787 | 0.080643 | -0.31525 | -0.25925 | -0.31346 | -0.21095 | -0.23491 | -0.36946 | -0.016192 | 0.088371 | 0.014092 | 0.049318 | 121.672 | 121.8501 | 121.3396 | 121.4924 | -121.6882 | -121.3558 | -121.6579 | -121.3255
1498.7344 | 122.081 | -121.7239 | 0.091553 | 0.062332 | -0.32441 | -0.27756 | -0.33178 | -0.22926 | -0.24406 | -0.37403 | -0.025347 | 0.079217 | 0.000359 | 0.040164 | 121.6628 | 121.841 | 121.3258 | 121.4787 | 0.076065 | -0.31067 | -0.26383 | -0.31804 | -0.21552 | -0.23033 | -0.3603 | -0.011614 | 0.09295 | 0.014092 | 0.053897 | 121.6766 | 121.8547 | 121.3396 | 121.4924 | -121.6882 | -121.3512 | -121.6625 | -121.3255
1500.4844 | 122.0581 | -121.7148 | 0.10071 | 0.062332 | -0.32899 | -0.27756 | -0.34093 | -0.22926 | -0.24864 | -0.38319 | -0.025347 | 0.079217 | 0.000359 | 0.031006 | 121.6491 | 121.8456 | 121.3304 | 121.4787 | 0.076065 | -0.31525 | -0.26383 | -0.3272 | -0.21552 | -0.23491 | -0.36946 | -0.011614 | 0.09295 | 0.014092 | 0.044739 | 121.6628 | 121.8593 | 121.3442 | 121.4924 | -121.6744 | -121.3558 | -121.6487 | -121.3301
1502.2344 | 122.0032 | -121.7514 | 0.09613 | 0.06691 | -0.32899 | -0.27298 | -0.33636 | -0.23383 | -0.24406 | -0.38777 | -0.034504 | 0.079217 | -0.008798 | 0.040164 | 121.6537 | 121.841 | 121.3304 | 121.4878 | 0.080643 | -0.31525 | -0.25925 | -0.32262 | -0.2201 | -0.23033 | -0.37404 | -0.020771 | 0.09295 | 0.004935 | 0.053897 | 121.6674 | 121.8547 | 121.3442 | 121.5015 | -121.6882 | -121.3649 | -121.6625 | -121.3392
1503.9219 | 121.9254 | -121.7651 | 0.1236 | 0.06691 | -0.33357 | -0.28214 | -0.33178 | -0.23841 | -0.24864 | -0.38319 | -0.025347 | 0.074638 | 0.000359 | 0.035585 | 121.6583 | 121.8456 | 121.3304 | 121.4878 | 0.080643 | -0.31983 | -0.2684 | -0.31804 | -0.22468 | -0.23491 | -0.36946 | -0.011614 | 0.088371 | 0.014092 | 0.049318 | 121.672 | 121.8593 | 121.3442 | 121.5015 | -121.6836 | -121.3558 | -121.6579 | -121.3301
1505.6719 | 121.9299 | -121.7743 | 0.14191 | 0.053175 | -0.33814 | -0.28672 | -0.33636 | -0.23841 | -0.25322 | -0.39235 | -0.020768 | 0.079217 | 0.000359 | 0.031006 | 121.6583 | 121.8501 | 121.335 | 121.4832 | 0.066908 | -0.32441 | -0.27298 | -0.32262 | -0.22468 | -0.23949 | -0.37861 | -0.007035 | 0.09295 | 0.014092 | 0.044739 | 121.672 | 121.8639 | 121.3487 | 121.497 | -121.679 | -121.3558 | -121.6579 | -121.3346
1507.4219 | 121.9528 | -121.7789 | 0.11444 | 0.06691 | -0.32899 | -0.28214 | -0.34093 | -0.23383 | -0.2578 | -0.39692 | -0.029925 | 0.079217 | 0.000359 | 0.035585 | 121.6537 | 121.8364 | 121.335 | 121.4878 | 0.080643 | -0.31525 | -0.2684 | -0.3272 | -0.2201 | -0.24406 | -0.38319 | -0.016192 | 0.09295 | 0.014092 | 0.049318 | 121.6674 | 121.8501 | 121.3487 | 121.5015 | -121.6836 | -121.3649 | -121.6533 | -121.3346
1509.1094 | 121.9116 | -121.7285 | 0.12817 | 0.062332 | -0.33814 | -0.28672 | -0.34551 | -0.23841 | -0.25322 | -0.38777 | -0.029925 | 0.074638 | 0.004937 | 0.035585 | 121.6583 | 121.841 | 121.335 | 121.4832 | 0.076065 | -0.32441 | -0.27298 | -0.33178 | -0.22468 | -0.23949 | -0.37404 | -0.016192 | 0.088371 | 0.01867 | 0.049318 | 121.672 | 121.8547 | 121.3487 | 121.497 | -121.6882 | -121.3649 | -121.6533 | -121.3301
1510.8438 | 121.9528 | -121.7468 | 0.11444 | 0.057754 | -0.33814 | -0.29587 | -0.34551 | -0.23383 | -0.2578 | -0.39235 | -0.029925 | 0.083796 | 0.004937 | 0.035585 | 121.6491 | 121.841 | 121.335 | 121.4878 | 0.071487 | -0.32441 | -0.28214 | -0.33178 | -0.2201 | -0.24406 | -0.37861 | -0.016192 | 0.097529 | 0.01867 | 0.049318 | 121.6628 | 121.8547 | 121.3487 | 121.5015 | -121.679 | -121.3649 | -121.6442 | -121.3301
1512.5781 | 122.0535 | -121.7239 | 0.07782 | 0.062332 | -0.34272 | -0.29587 | -0.34551 | -0.24299 | -0.26695 | -0.4015 | -0.029925 | 0.088375 | 0.000359 | 0.040164 | 121.6628 | 121.8456 | 121.335 | 121.4924 | 0.076065 | -0.32899 | -0.28214 | -0.33178 | -0.22926 | -0.25322 | -0.38777 | -0.016192 | 0.10211 | 0.014092 | 0.053897 | 121.6766 | 121.8593 | 121.3487 | 121.5061 | -121.6928 | -121.3649 | -121.6625 | -121.3346
1514.3281 | 121.9666 | -121.7422 | 0.13275 | 0.06691 | -0.33814 | -0.29129 | -0.35009 | -0.24757 | -0.27153 | -0.4015 | -0.025347 | 0.083796 | 0.004937 | 0.031006 | 121.6674 | 121.8456 | 121.3442 | 121.4787 | 0.080643 | -0.32441 | -0.27756 | -0.33636 | -0.23384 | -0.2578 | -0.38777 | -0.011614 | 0.097529 | 0.01867 | 0.044739 | 121.6811 | 121.8593 | 121.3579 | 121.4924 | -121.6928 | -121.3695 | -121.6625 | -121.3392
1516 | 121.9528 | -121.7697 | 0.10071 | 0.06691 | -0.3473 | -0.29587 | -0.35467 | -0.24299 | -0.26238 | -0.38319 | -0.029925 | 0.079217 | -0.004219 | 0.040164 | 121.6583 | 121.8456 | 121.3258 | 121.4832 | 0.080643 | -0.33357 | -0.28214 | -0.34094 | -0.22926 | -0.24864 | -0.36946 | -0.016192 | 0.09295 | 0.009514 | 0.053897 | 121.672 | 121.8593 | 121.3396 | 121.497 | -121.6882 | -121.3558 | -121.6625 | -121.3301
1517.75 | 121.9254 | -121.7651 | 0.13733 | 0.062332 | -0.34272 | -0.30045 | -0.35925 | -0.24757 | -0.26695 | -0.39692 | -0.025347 | 0.079217 | -0.004219 | 0.035585 | 121.6583 | 121.841 | 121.3258 | 121.4787 | 0.076065 | -0.32899 | -0.28672 | -0.34551 | -0.23384 | -0.25322 | -0.38319 | -0.011614 | 0.09295 | 0.009514 | 0.049318 | 121.672 | 121.8547 | 121.3396 | 121.4924 | -121.6836 | -121.3512 | -121.6625 | -121.3301
1519.5 | 122.0352 | -121.7285 | 0.091553 | 0.06691 | -0.34272 | -0.30503 | -0.36383 | -0.24757 | -0.27153 | -0.4015 | -0.020768 | 0.079217 | 0.000359 | 0.035585 | 121.6537 | 121.8364 | 121.3258 | 121.4832 | 0.080643 | -0.32899 | -0.2913 | -0.35009 | -0.23384 | -0.2578 | -0.38777 | -0.007035 | 0.09295 | 0.014092 | 0.049318 | 121.6674 | 121.8501 | 121.3396 | 121.497 | -121.6744 | -121.3466 | -121.6533 | -121.3255
1521.1719 | 122.0581 | -121.7056 | 0.073242 | 0.062332 | -0.35188 | -0.30961 | -0.35925 | -0.25672 | -0.27611 | -0.4015 | -0.034504 | 0.079217 | 0.004937 | 0.035585 | 121.6537 | 121.8456 | 121.3304 | 121.4832 | 0.076065 | -0.33815 | -0.29588 | -0.34551 | -0.24299 | -0.26238 | -0.38777 | -0.020771 | 0.09295 | 0.01867 | 0.049318 | 121.6674 | 121.8593 | 121.3442 | 121.497 | -121.6882 | -121.3649 | -121.6487 | -121.3255
1522.9062 | 121.9162 | -121.7468 | 0.13275 | 0.06691 | -0.35188 | -0.30961 | -0.35925 | -0.25215 | -0.26695 | -0.40608 | -0.025347 | 0.079217 | 0.004937 | 0.040164 | 121.6583 | 121.8456 | 121.3213 | 121.4832 | 0.080643 | -0.33815 | -0.29588 | -0.34551 | -0.23841 | -0.25322 | -0.39235 | -0.011614 | 0.09295 | 0.01867 | 0.053897 | 121.672 | 121.8593 | 121.335 | 121.497 | -121.6836 | -121.3466 | -121.6533 | -121.3163
1524.6406 | 122.0627 | -121.7377 | 0.07782 | 0.062332 | -0.36104 | -0.30961 | -0.3684 | -0.25672 | -0.27611 | -0.41066 | -0.025347 | 0.079217 | 0.004937 | 0.035585 | 121.6491 | 121.8456 | 121.3258 | 121.4787 | 0.076065 | -0.34731 | -0.29588 | -0.35467 | -0.24299 | -0.26238 | -0.39693 | -0.011614 | 0.09295 | 0.01867 | 0.049318 | 121.6628 | 121.8593 | 121.3396 | 121.4924 | -121.6744 | -121.3512 | -121.6442 | -121.3209
1526.375 | 122.049 | -121.7102 | 0.10071 | 0.062332 | -0.36104 | -0.32334 | -0.3684 | -0.25215 | -0.27611 | -0.40608 | -0.025347 | 0.083796 | 0.000359 | 0.044743 | 121.6583 | 121.8456 | 121.3258 | 121.4787 | 0.076065 | -0.34731 | -0.30961 | -0.35467 | -0.23841 | -0.26238 | -0.39235 | -0.011614 | 0.097529 | 0.014092 | 0.058476 | 121.672 | 121.8593 | 121.3396 | 121.4924 | -121.6836 | -121.3512 | -121.6579 | -121.3255
1528.0469 | 121.9894 | -121.7239 | 0.086975 | 0.06691 | -0.36104 | -0.30503 | -0.3684 | -0.2613 | -0.28069 | -0.40608 | -0.025347 | 0.083796 | 0.009515 | 0.040164 | 121.6537 | 121.841 | 121.3304 | 121.4787 | 0.080643 | -0.34731 | -0.2913 | -0.35467 | -0.24757 | -0.26695 | -0.39235 | -0.011614 | 0.097529 | 0.023248 | 0.053897 | 121.6674 | 121.8547 | 121.3442 | 121.4924 | -121.679 | -121.3558 | -121.6442 | -121.3209
1529.7969 | 122.0398 | -121.7285 | 0.10071 | 0.057754 | -0.36104 | -0.31877 | -0.3684 | -0.26588 | -0.27611 | -0.42439 | -0.025347 | 0.079217 | 0.000359 | 0.040164 | 121.6491 | 121.8456 | 121.3258 | 121.4741 | 0.071487 | -0.34731 | -0.30503 | -0.35467 | -0.25215 | -0.26238 | -0.41066 | -0.011614 | 0.09295 | 0.014092 | 0.053897 | 121.6628 | 121.8593 | 121.3396 | 121.4878 | -121.6744 | -121.3512 | -121.6487 | -121.3255
1531.4688 | 121.9254 | -121.7514 | 0.11902 | 0.071489 | -0.36562 | -0.32334 | -0.37298 | -0.25672 | -0.28069 | -0.41524 | -0.025347 | 0.088375 | 0.009515 | 0.044743 | 121.6537 | 121.841 | 121.3304 | 121.4832 | 0.085222 | -0.35188 | -0.30961 | -0.35925 | -0.24299 | -0.26695 | -0.4015 | -0.011614 | 0.10211 | 0.023248 | 0.058476 | 121.6674 | 121.8547 | 121.3442 | 121.497 | -121.679 | -121.3558 | -121.6442 | -121.3209
1533.2031 | 121.9757 | -121.7377 | 0.13733 | 0.071489 | -0.36104 | -0.31877 | -0.37756 | -0.27504 | -0.28069 | -0.41524 | -0.020768 | 0.083796 | 0.009515 | 0.044743 | 121.6583 | 121.8364 | 121.3304 | 121.4787 | 0.085222 | -0.34731 | -0.30503 | -0.36383 | -0.2613 | -0.26695 | -0.4015 | -0.007035 | 0.097529 | 0.023248 | 0.058476 | 121.672 | 121.8501 | 121.3442 | 121.4924 | -121.679 | -121.3512 | -121.6487 | -121.3209
1534.9531 | 122.0581 | -121.701 | 0.073242 | 0.071489 | -0.3702 | -0.31877 | -0.37298 | -0.27046 | -0.28985 | -0.41066 | -0.020768 | 0.083796 | 0.004937 | 0.040164 | 121.6491 | 121.841 | 121.3304 | 121.4787 | 0.085222 | -0.35646 | -0.30503 | -0.35925 | -0.25672 | -0.27611 | -0.39693 | -0.007035 | 0.097529 | 0.01867 | 0.053897 | 121.6628 | 121.8547 | 121.3442 | 121.4924 | -121.6699 | -121.3512 | -121.6442 | -121.3255
1536.6875 | 121.9299 | -121.7606 | 0.1236 | 0.062332 | -0.37477 | -0.32334 | -0.37298 | -0.27046 | -0.28985 | -0.42897 | -0.01619 | 0.088375 | 0.009515 | 0.044743 | 121.6491 | 121.8364 | 121.3213 | 121.4741 | 0.076065 | -0.36104 | -0.30961 | -0.35925 | -0.25672 | -0.27611 | -0.41524 | -0.002457 | 0.10211 | 0.023248 | 0.058476 | 121.6628 | 121.8501 | 121.335 | 121.4878 | -121.6653 | -121.3375 | -121.6396 | -121.3117
1538.4219 | 121.9254 | -121.756 | 0.10529 | 0.062332 | -0.3702 | -0.3325 | -0.37298 | -0.27046 | -0.29442 | -0.42439 | -0.020768 | 0.088375 | 0.004937 | 0.040164 | 121.6491 | 121.8272 | 121.3213 | 121.4695 | 0.076065 | -0.35646 | -0.31877 | -0.35925 | -0.25672 | -0.28069 | -0.41066 | -0.007035 | 0.10211 | 0.01867 | 0.053897 | 121.6628 | 121.841 | 121.335 | 121.4832 | -121.6699 | -121.342 | -121.6442 | -121.3163
1540.1094 | 122.049 | -121.7102 | 0.09613 | 0.062332 | -0.37477 | -0.3325 | -0.37756 | -0.26588 | -0.29442 | -0.43355 | -0.020768 | 0.083796 | 0.014094 | 0.044743 | 121.6537 | 121.8364 | 121.3258 | 121.4832 | 0.076065 | -0.36104 | -0.31877 | -0.36383 | -0.25215 | -0.28069 | -0.41982 | -0.007035 | 0.097529 | 0.027827 | 0.058476 | 121.6674 | 121.8501 | 121.3396 | 121.497 | -121.6744 | -121.3466 | -121.6396 | -121.3117
1541.8438 | 121.9757 | -121.7377 | 0.10529 | 0.062332 | -0.38851 | -0.3325 | -0.38214 | -0.27961 | -0.299 | -0.42897 | -0.01619 | 0.088375 | 0.009515 | 0.049322 | 121.6537 | 121.8318 | 121.3213 | 121.4787 | 0.076065 | -0.37478 | -0.31877 | -0.36841 | -0.26588 | -0.28527 | -0.41524 | -0.002457 | 0.10211 | 0.023248 | 0.063055 | 121.6674 | 121.8456 | 121.335 | 121.4924 | -121.6699 | -121.3375 | -121.6442 | -121.3117
1543.5938 | 122.0535 | -121.7102 | 0.10986 | 0.057754 | -0.38393 | -0.3325 | -0.3913 | -0.27961 | -0.30358 | -0.43813 | -0.020768 | 0.092954 | 0.009515 | 0.049322 | 121.6491 | 121.8272 | 121.3213 | 121.4787 | 0.071487 | -0.3702 | -0.31877 | -0.37756 | -0.26588 | -0.28985 | -0.4244 | -0.007035 | 0.10669 | 0.023248 | 0.063055 | 121.6628 | 121.841 | 121.335 | 121.4924 | -121.6699 | -121.342 | -121.6396 | -121.3117
1545.2812 | 121.962 | -121.7468 | 0.13275 | 0.057754 | -0.38393 | -0.34166 | -0.38672 | -0.28419 | -0.299 | -0.43355 | -0.011611 | 0.088375 | 0.014094 | 0.044743 | 121.6399 | 121.8227 | 121.3167 | 121.4741 | 0.071487 | -0.3702 | -0.32793 | -0.37299 | -0.27046 | -0.28527 | -0.41982 | 0.002122 | 0.10211 | 0.027827 | 0.058476 | 121.6537 | 121.8364 | 121.3304 | 121.4878 | -121.6515 | -121.3283 | -121.6258 | -121.3026
1546.9688 | 122.0581 | -121.6965 | 0.10529 | 0.062332 | -0.38393 | -0.34166 | -0.40045 | -0.27961 | -0.30358 | -0.43813 | -0.011611 | 0.097532 | 0.014094 | 0.044743 | 121.6399 | 121.8318 | 121.303 | 121.4695 | 0.076065 | -0.3702 | -0.32793 | -0.38672 | -0.26588 | -0.28985 | -0.4244 | 0.002122 | 0.11126 | 0.027827 | 0.058476 | 121.6537 | 121.8456 | 121.3167 | 121.4832 | -121.6515 | -121.3146 | -121.6258 | -121.2889
1548.7188 | 122.0398 | -121.7285 | 0.10529 | 0.062332 | -0.39309 | -0.34166 | -0.40961 | -0.29335 | -0.30816 | -0.43813 | -0.01619 | 0.079217 | 0.014094 | 0.044743 | 121.6445 | 121.8227 | 121.3121 | 121.4695 | 0.076065 | -0.37936 | -0.32793 | -0.39588 | -0.27962 | -0.29442 | -0.4244 | -0.002457 | 0.09295 | 0.027827 | 0.058476 | 121.6582 | 121.8364 | 121.3258 | 121.4832 | -121.6607 | -121.3283 | -121.6304 | -121.298
1550.4688 | 121.9711 | -121.7285 | 0.13275 | 0.071489 | -0.39309 | -0.35082 | -0.40503 | -0.29793 | -0.30816 | -0.44271 | -0.011611 | 0.097532 | 0.014094 | 0.05848 | 121.6354 | 121.8272 | 121.3075 | 121.4741 | 0.085222 | -0.37936 | -0.33708 | -0.3913 | -0.28419 | -0.29442 | -0.42897 | 0.002122 | 0.11126 | 0.027827 | 0.072213 | 121.6491 | 121.841 | 121.3213 | 121.4878 | -121.647 | -121.3191 | -121.6213 | -121.2934
1552.1406 | 122.0306 | -121.6644 | 0.11902 | 0.057754 | -0.39309 | -0.34624 | -0.40045 | -0.28877 | -0.30816 | -0.44728 | 0.002124 | 0.10669 | 0.036985 | 0.067638 | 121.617 | 121.7952 | 121.2892 | 121.442 | 0.071487 | -0.37936 | -0.3325 | -0.38672 | -0.27504 | -0.29442 | -0.43355 | 0.015857 | 0.12042 | 0.050718 | 0.081371 | 121.6308 | 121.8089 | 121.3029 | 121.4558 | -121.6149 | -121.2871 | -121.5801 | -121.2522
1553.8906 | 122.0444 | -121.6782 | 0.10529 | 0.062332 | -0.40225 | -0.35082 | -0.40503 | -0.29335 | -0.31732 | -0.44271 | 0.002124 | 0.11585 | 0.032407 | 0.05848 | 121.6125 | 121.7906 | 121.2801 | 121.442 | 0.076065 | -0.38851 | -0.33708 | -0.3913 | -0.27962 | -0.30358 | -0.42897 | 0.015857 | 0.12958 | 0.04614 | 0.072213 | 121.6262 | 121.8043 | 121.2938 | 121.4558 | -121.6103 | -121.2779 | -121.5801 | -121.2477
1555.625 | 121.8796 | -121.7102 | 0.15106 | 0.071489 | -0.40683 | -0.35082 | -0.40045 | -0.29335 | -0.31274 | -0.45186 | 0.002124 | 0.11127 | 0.032407 | 0.072217 | 121.5942 | 121.7906 | 121.2709 | 121.4237 | 0.085222 | -0.39309 | -0.33708 | -0.38672 | -0.27962 | -0.299 | -0.43813 | 0.015857 | 0.125 | 0.04614 | 0.08595 | 121.6079 | 121.8043 | 121.2846 | 121.4374 | -121.592 | -121.2688 | -121.5617 | -121.2385
1557.2969 | 121.8979 | -121.6873 | 0.13733 | 0.057754 | -0.40225 | -0.3554 | -0.40961 | -0.30708 | -0.32189 | -0.45186 | 0.006703 | 0.12043 | 0.027829 | 0.076796 | 121.5942 | 121.786 | 121.2663 | 121.4191 | 0.071487 | -0.38851 | -0.34166 | -0.39588 | -0.29335 | -0.30816 | -0.43813 | 0.020436 | 0.13416 | 0.041562 | 0.090529 | 121.6079 | 121.7998 | 121.2801 | 121.4329 | -121.5875 | -121.2596 | -121.5663 | -121.2385
1558.9844 | 121.9986 | -121.6599 | 0.12817 | 0.062332 | -0.39767 | -0.35997 | -0.40961 | -0.30708 | -0.32647 | -0.46102 | 0.006703 | 0.11127 | 0.036985 | 0.067638 | 121.5896 | 121.7769 | 121.2663 | 121.4191 | 0.076065 | -0.38394 | -0.34624 | -0.39588 | -0.29335 | -0.31274 | -0.44728 | 0.020436 | 0.125 | 0.050718 | 0.081371 | 121.6033 | 121.7906 | 121.2801 | 121.4329 | -121.5829 | -121.2596 | -121.5526 | -121.2293
1560.7188 | 122.0078 | -121.6507 | 0.12817 | 0.057754 | -0.40683 | -0.35997 | -0.41419 | -0.31166 | -0.32189 | -0.46102 | 0.011281 | 0.12043 | 0.036985 | 0.076796 | 121.5896 | 121.7723 | 121.2617 | 121.4191 | 0.071487 | -0.39309 | -0.34624 | -0.40046 | -0.29793 | -0.30816 | -0.44728 | 0.025014 | 0.13416 | 0.050718 | 0.090529 | 121.6033 | 121.786 | 121.2755 | 121.4329 | -121.5783 | -121.2505 | -121.5526 | -121.2248
1562.4531 | 121.9299 | -121.6599 | 0.15564 | 0.062332 | -0.41141 | -0.36913 | -0.41419 | -0.31624 | -0.32647 | -0.46102 | 0.002124 | 0.11585 | 0.036985 | 0.067638 | 121.585 | 121.7631 | 121.2526 | 121.4054 | 0.076065 | -0.39767 | -0.3554 | -0.40046 | -0.30251 | -0.31274 | -0.44728 | 0.015857 | 0.12958 | 0.050718 | 0.081371 | 121.5987 | 121.7769 | 121.2663 | 121.4191 | -121.5829 | -121.2505 | -121.548 | -121.2156
1564.125 | 121.994 | -121.669 | 0.1236 | 0.06691 | -0.41598 | -0.35997 | -0.42792 | -0.31624 | -0.33563 | -0.46102 | 0.011281 | 0.12501 | 0.036985 | 0.076796 | 121.5758 | 121.7631 | 121.2389 | 121.4008 | 0.080643 | -0.40225 | -0.34624 | -0.41419 | -0.30251 | -0.3219 | -0.44728 | 0.025014 | 0.13874 | 0.050718 | 0.090529 | 121.5896 | 121.7769 | 121.2526 | 121.4146 | -121.5646 | -121.2276 | -121.5389 | -121.2019
1565.8594 | 121.8933 | -121.6782 | 0.16022 | 0.062332 | -0.42056 | -0.36913 | -0.42335 | -0.31624 | -0.33563 | -0.4656 | 0.01586 | 0.12043 | 0.032407 | 0.072217 | 121.5713 | 121.754 | 121.248 | 121.4054 | 0.076065 | -0.40683 | -0.3554 | -0.40961 | -0.30251 | -0.3219 | -0.45186 | 0.029593 | 0.13416 | 0.04614 | 0.08595 | 121.585 | 121.7677 | 121.2617 | 121.4191 | -121.5554 | -121.2321 | -121.5389 | -121.2156
1567.6094 | 121.9391 | -121.637 | 0.13733 | 0.057754 | -0.42514 | -0.37829 | -0.4325 | -0.31624 | -0.33563 | -0.47018 | 0.01586 | 0.12958 | 0.036985 | 0.081375 | 121.5621 | 121.7494 | 121.2297 | 121.3917 | 0.071487 | -0.41141 | -0.36456 | -0.41877 | -0.30251 | -0.3219 | -0.45644 | 0.029593 | 0.14332 | 0.050718 | 0.095108 | 121.5758 | 121.7631 | 121.2434 | 121.4054 | -121.5462 | -121.2138 | -121.5251 | -121.1927
1569.2969 | 121.8979 | -121.6782 | 0.16022 | 0.06691 | -0.42056 | -0.37829 | -0.4325 | -0.32539 | -0.34479 | -0.47018 | 0.020438 | 0.12958 | 0.041563 | 0.076796 | 121.5667 | 121.7403 | 121.2343 | 121.3917 | 0.080643 | -0.40683 | -0.36456 | -0.41877 | -0.31166 | -0.33105 | -0.45644 | 0.034171 | 0.14332 | 0.055296 | 0.090529 | 121.5804 | 121.754 | 121.248 | 121.4054 | -121.5463 | -121.2138 | -121.5251 | -121.1927
1570.9844 | 121.8979 | -121.6599 | 0.16479 | 0.06691 | -0.42972 | -0.37829 | -0.42792 | -0.31166 | -0.34479 | -0.47475 | 0.025017 | 0.12501 | 0.05072 | 0.076796 | 121.5575 | 121.7403 | 121.2297 | 121.3871 | 0.080643 | -0.41599 | -0.36456 | -0.41419 | -0.29793 | -0.33105 | -0.46102 | 0.03875 | 0.13874 | 0.064453 | 0.090529 | 121.5713 | 121.754 | 121.2434 | 121.4008 | -121.5325 | -121.2047 | -121.5068 | -121.179
1572.6562 | 121.9116 | -121.637 | 0.17395 | 0.062332 | -0.4343 | -0.37829 | -0.43708 | -0.32539 | -0.35394 | -0.47475 | 0.025017 | 0.12501 | 0.046142 | 0.085954 | 121.5575 | 121.7357 | 121.2297 | 121.3779 | 0.076065 | -0.42057 | -0.36456 | -0.42335 | -0.31166 | -0.34021 | -0.46102 | 0.03875 | 0.13874 | 0.059875 | 0.099687 | 121.5713 | 121.7494 | 121.2434 | 121.3917 | -121.5325 | -121.2047 | -121.5114 | -121.1836
1574.3438 | 121.9986 | -121.6187 | 0.15106 | 0.057754 | -0.4343 | -0.38744 | -0.43708 | -0.32997 | -0.34936 | -0.48391 | 0.025017 | 0.13874 | 0.041563 | 0.095112 | 121.5484 | 121.7219 | 121.216 | 121.3734 | 0.071487 | -0.42057 | -0.37371 | -0.42335 | -0.31624 | -0.33563 | -0.47018 | 0.03875 | 0.15247 | 0.055296 | 0.10884 | 121.5621 | 121.7357 | 121.2297 | 121.3871 | -121.5234 | -121.1909 | -121.5068 | -121.1744
1576.0312 | 121.8521 | -121.637 | 0.16937 | 0.071489 | -0.4343 | -0.39202 | -0.43708 | -0.32082 | -0.34936 | -0.48391 | 0.034174 | 0.13874 | 0.05072 | 0.090533 | 121.5392 | 121.7219 | 121.2022 | 121.3688 | 0.085222 | -0.42057 | -0.37829 | -0.42335 | -0.30708 | -0.33563 | -0.47018 | 0.047907 | 0.15247 | 0.064453 | 0.10427 | 121.553 | 121.7357 | 121.216 | 121.3825 | -121.505 | -121.1681 | -121.4885 | -121.1515
1577.7656 | 121.9803 | -121.6003 | 0.15106 | 0.06691 | -0.43888 | -0.39202 | -0.44624 | -0.33455 | -0.35394 | -0.49307 | 0.029595 | 0.13416 | 0.055298 | 0.095112 | 121.5346 | 121.7174 | 121.1976 | 121.355 | 0.080643 | -0.42514 | -0.37829 | -0.43251 | -0.32082 | -0.34021 | -0.47933 | 0.043328 | 0.1479 | 0.069031 | 0.10884 | 121.5484 | 121.7311 | 121.2114 | 121.3688 | -121.505 | -121.1681 | -121.4793 | -121.1424
1579.5 | 121.9528 | -121.6278 | 0.14648 | 0.06691 | -0.43888 | -0.40118 | -0.44166 | -0.33913 | -0.35394 | -0.48391 | 0.029595 | 0.13874 | 0.05072 | 0.095112 | 121.7223 | 121.6991 | 121.422 | 121.5519 | 0.080643 | -0.42514 | -0.38745 | -0.42793 | -0.32539 | -0.34021 | -0.47018 | 0.043328 | 0.15247 | 0.064453 | 0.10884 | 121.7361 | 121.7128 | 121.4357 | 121.5656 | -121.6928 | -121.3924 | -121.6716 | -121.3713
1581.1719 | 121.8704 | -121.6599 | 0.10986 | 0.071489 | -0.43888 | -0.39202 | -0.44166 | -0.33913 | -0.34479 | -0.49307 | 0.006703 | 0.10669 | 0.027829 | 0.05848 | 121.7361 | 121.7174 | 121.4403 | 121.5656 | 0.085222 | -0.42514 | -0.37829 | -0.42793 | -0.32539 | -0.33105 | -0.47933 | 0.020436 | 0.12042 | 0.041562 | 0.072213 | 121.7498 | 121.7311 | 121.454 | 121.5794 | -121.7294 | -121.4336 | -121.7083 | -121.4125
1582.9062 | 121.9208 | -121.6553 | 0.09613 | 0.062332 | -0.43888 | -0.40118 | -0.44166 | -0.33455 | -0.3631 | -0.48849 | -0.01619 | 0.097532 | 0.014094 | 0.040164 | 121.5896 | 121.7677 | 121.248 | 121.4146 | 0.076065 | -0.42514 | -0.38745 | -0.42793 | -0.32082 | -0.34937 | -0.47475 | -0.002457 | 0.11126 | 0.027827 | 0.053897 | 121.6033 | 121.7815 | 121.2617 | 121.4283 | -121.6058 | -121.2642 | -121.5755 | -121.2339
1584.6406 | 121.9803 | -121.6553 | 0.07782 | 0.06691 | -0.44346 | -0.3966 | -0.45539 | -0.33913 | -0.35852 | -0.49764 | -0.007033 | 0.092954 | 0.018672 | 0.049322 | 121.5942 | 121.7769 | 121.2572 | 121.4146 | 0.080643 | -0.42972 | -0.38287 | -0.44166 | -0.32539 | -0.34479 | -0.48391 | 0.0067 | 0.10669 | 0.032405 | 0.063055 | 121.6079 | 121.7906 | 121.2709 | 121.4283 | -121.6012 | -121.2642 | -121.5755 | -121.2385
1586.375 | 122.0078 | -121.6461 | 0.1236 | 0.062332 | -0.45261 | -0.41034 | -0.45997 | -0.35286 | -0.3631 | -0.49307 | -0.011611 | 0.092954 | 0.009515 | 0.044743 | 121.6033 | 121.7769 | 121.2663 | 121.4237 | 0.076065 | -0.43888 | -0.3966 | -0.44624 | -0.33913 | -0.34937 | -0.47933 | 0.002122 | 0.10669 | 0.023248 | 0.058476 | 121.617 | 121.7906 | 121.2801 | 121.4374 | -121.6149 | -121.2779 | -121.5938 | -121.2568
1588.0938 | 121.875 | -121.6919 | 0.12817 | 0.071489 | -0.44346 | -0.40118 | -0.45997 | -0.34371 | -0.37226 | -0.50222 | -0.002454 | 0.097532 | 0.014094 | 0.044743 | 121.5987 | 121.7769 | 121.2663 | 121.4191 | 0.085222 | -0.42972 | -0.38745 | -0.44624 | -0.32997 | -0.35852 | -0.48849 | 0.011279 | 0.11126 | 0.027827 | 0.058476 | 121.6125 | 121.7906 | 121.2801 | 121.4329 | -121.6012 | -121.2688 | -121.5846 | -121.2522
1589.7812 | 121.9208 | -121.6782 | 0.13733 | 0.071489 | -0.46177 | -0.41034 | -0.45539 | -0.34371 | -0.37226 | -0.5068 | -0.007033 | 0.10211 | 0.009515 | 0.044743 | 121.6033 | 121.786 | 121.2709 | 121.4237 | 0.085222 | -0.44804 | -0.3966 | -0.44166 | -0.32997 | -0.35852 | -0.49307 | 0.0067 | 0.11584 | 0.023248 | 0.058476 | 121.617 | 121.7998 | 121.2846 | 121.4374 | -121.6103 | -121.2779 | -121.5938 | -121.2614
1591.5156 | 122.0352 | -121.6599 | 0.10071 | 0.062332 | -0.45719 | -0.41034 | -0.46913 | -0.34828 | -0.36768 | -0.50222 | -0.007033 | 0.10211 | 0.02325 | 0.053901 | 121.5987 | 121.786 | 121.2663 | 121.4283 | 0.076065 | -0.44346 | -0.3966 | -0.4554 | -0.33455 | -0.35395 | -0.48849 | 0.0067 | 0.11584 | 0.036983 | 0.067634 | 121.6125 | 121.7998 | 121.2801 | 121.442 | -121.6058 | -121.2734 | -121.5755 | -121.2431
1593.2031 | 121.8842 | -121.7056 | 0.13275 | 0.06691 | -0.46635 | -0.41492 | -0.46455 | -0.35286 | -0.37683 | -0.51138 | -0.002454 | 0.097532 | 0.02325 | 0.05848 | 121.6033 | 121.7815 | 121.2617 | 121.4237 | 0.080643 | -0.45262 | -0.40118 | -0.45082 | -0.33913 | -0.3631 | -0.49765 | 0.011279 | 0.11126 | 0.036983 | 0.072213 | 121.617 | 121.7952 | 121.2755 | 121.4374 | -121.6058 | -121.2642 | -121.5801 | -121.2385
1594.9531 | 121.9116 | -121.6736 | 0.15106 | 0.06691 | -0.46177 | -0.42407 | -0.47371 | -0.35744 | -0.37683 | -0.5068 | 0.006703 | 0.097532 | 0.018672 | 0.05848 | 121.5987 | 121.7769 | 121.2663 | 121.4237 | 0.080643 | -0.44804 | -0.41034 | -0.45998 | -0.34371 | -0.3631 | -0.49307 | 0.020436 | 0.11126 | 0.032405 | 0.072213 | 121.6125 | 121.7906 | 121.2801 | 121.4374 | -121.592 | -121.2596 | -121.5801 | -121.2477
1596.7031 | 121.962 | -121.6644 | 0.11444 | 0.06691 | -0.47093 | -0.4195 | -0.47829 | -0.36202 | -0.38599 | -0.51138 | 0.002124 | 0.10669 | 0.027829 | 0.05848 | 121.6079 | 121.7815 | 121.2617 | 121.4283 | 0.080643 | -0.4572 | -0.40576 | -0.46455 | -0.34829 | -0.37226 | -0.49765 | 0.015857 | 0.12042 | 0.041562 | 0.072213 | 121.6216 | 121.7952 | 121.2755 | 121.442 | -121.6058 | -121.2596 | -121.5801 | -121.2339
1598.3906 | 121.8842 | -121.701 | 0.16479 | 0.071489 | -0.46635 | -0.42407 | -0.47829 | -0.36202 | -0.37683 | -0.51138 | 0.002124 | 0.10669 | 0.032407 | 0.05848 | 121.5896 | 121.7769 | 121.2617 | 121.41 | 0.085222 | -0.45262 | -0.41034 | -0.46455 | -0.34829 | -0.3631 | -0.49765 | 0.015857 | 0.12042 | 0.04614 | 0.072213 | 121.6033 | 121.7906 | 121.2755 | 121.4237 | -121.5875 | -121.2596 | -121.5572 | -121.2293
1600.1562 | 121.875 | -121.6873 | 0.15106 | 0.062332 | -0.47551 | -0.42865 | -0.47829 | -0.36202 | -0.38141 | -0.51596 | 0.006703 | 0.11585 | 0.032407 | 0.072217 | 121.585 | 121.7723 | 121.248 | 121.41 | 0.076065 | -0.46177 | -0.41492 | -0.46455 | -0.34829 | -0.36768 | -0.50222 | 0.020436 | 0.12958 | 0.04614 | 0.08595 | 121.5987 | 121.786 | 121.2617 | 121.4237 | -121.5783 | -121.2413 | -121.5526 | -121.2156
1601.8906 | 121.2296 | -46.4996 | 74.2218 | 0.10812 | 0.005267 | 0.084151 | 0.011611 | 0.12325 | 0.099318 | -0.044405 | 66.9901 | 67.5618 | 67.2187 | 67.3016 | 53.4389 | 53.3165 | 53.1216 | 53.479 | 0.12185 | 0.019 | 0.097884 | 0.025344 | 0.13698 | 0.11305 | -0.030672 | 67.0038 | 67.5756 | 67.2324 | 67.3153 | 53.4526 | 53.3302 | 53.1353 | 53.4928 | 13.5512 | 13.8685 | 13.7798 | 14.0971
1603.5625 | 121.3669 | -31.6132 | 79.0329 | 0.11727 | 0.046477 | 0.13452 | 0.057396 | 0.17818 | 0.1451 | 0.015112 | 74.1051 | 74.4575 | 74.1639 | 74.248 | 47.0478 | 47.0308 | 46.7851 | 47.0604 | 0.13101 | 0.06021 | 0.14825 | 0.071129 | 0.19191 | 0.15884 | 0.028845 | 74.1188 | 74.4713 | 74.1777 | 74.2617 | 47.0615 | 47.0445 | 46.7988 | 47.0742 | 27.0573 | 27.32 | 27.1162 | 27.3788
1605.2969 | 120.6848 | -0.51727 | 112.1887 | 0.11727 | 0.28458 | 0.39092 | 0.30006 | 0.40708 | 0.38318 | 0.2486 | 120.3845 | 120.4288 | 120.4732 | 120.4138 | 0.66629 | 0.79691 | 0.48387 | 0.64693 | 0.13101 | 0.29831 | 0.40465 | 0.31379 | 0.42081 | 0.39691 | 0.26233 | 120.3982 | 120.4426 | 120.487 | 120.4275 | 0.68002 | 0.81065 | 0.49761 | 0.66066 | 119.7182 | 119.9006 | 119.8069 | 119.9894
1607.0312 | 121.3852 | -0.76446 | 120.0165 | 0.11727 | 0.28 | 0.39092 | 0.29548 | 0.40708 | 0.3786 | 0.23944 | 120.4578 | 120.493 | 120.5511 | 120.487 | 0.65713 | 0.78776 | 0.47472 | 0.63777 | 0.13101 | 0.29373 | 0.40465 | 0.30921 | 0.42081 | 0.39233 | 0.25317 | 120.4715 | 120.5067 | 120.5648 | 120.5008 | 0.67087 | 0.80149 | 0.48845 | 0.65151 | 119.8006 | 119.983 | 119.8939 | 120.0763
1608.7812 | 121.6232 | -0.79193 | 120.4697 | 0.12643 | 0.28458 | 0.39092 | 0.29548 | 0.39792 | 0.36944 | 0.23944 | 120.499 | 120.525 | 120.5923 | 120.5282 | 0.67544 | 0.79691 | 0.48387 | 0.64693 | 0.14016 | 0.29831 | 0.40465 | 0.30921 | 0.41166 | 0.38318 | 0.25317 | 120.5127 | 120.5387 | 120.606 | 120.542 | 0.68918 | 0.81065 | 0.49761 | 0.66066 | 119.8235 | 120.0151 | 119.9168 | 120.1084
1610.4688 | 121.669 | -0.80109 | 120.7535 | 0.11269 | 0.28 | 0.39092 | 0.2909 | 0.39792 | 0.37402 | 0.24402 | 120.499 | 120.5387 | 120.6014 | 120.542 | 0.6846 | 0.81522 | 0.49761 | 0.66066 | 0.12643 | 0.29373 | 0.40465 | 0.30463 | 0.41166 | 0.38775 | 0.25775 | 120.5127 | 120.5525 | 120.6152 | 120.5557 | 0.69834 | 0.82896 | 0.51134 | 0.6744 | 119.8144 | 120.0014 | 119.9168 | 120.1038
1612.2031 | 121.5866 | -0.83771 | 120.8176 | 0.11727 | 0.28 | 0.40008 | 0.29548 | 0.40708 | 0.3786 | 0.2486 | 120.5127 | 120.5525 | 120.606 | 120.5465 | 0.68918 | 0.82438 | 0.50219 | 0.6744 | 0.13101 | 0.29373 | 0.41381 | 0.30921 | 0.42081 | 0.39233 | 0.26233 | 120.5264 | 120.5662 | 120.6197 | 120.5603 | 0.70291 | 0.83811 | 0.51592 | 0.68813 | 119.8235 | 120.0105 | 119.9168 | 120.1038
1613.875 | 121.6965 | -0.84228 | 120.7855 | 0.11269 | 0.28 | 0.39092 | 0.2909 | 0.39792 | 0.38318 | 0.2486 | 120.5127 | 120.5479 | 120.6106 | 120.5511 | 0.71207 | 0.83812 | 0.52508 | 0.68813 | 0.12643 | 0.29373 | 0.40465 | 0.30463 | 0.41166 | 0.39691 | 0.26233 | 120.5264 | 120.5616 | 120.6243 | 120.5649 | 0.7258 | 0.85185 | 0.53881 | 0.70186 | 119.8006 | 119.9876 | 119.8985 | 120.0855
1615.625 | 121.7148 | -0.85144 | 120.7809 | 0.11727 | 0.28 | 0.40008 | 0.28174 | 0.4025 | 0.36944 | 0.24402 | 120.5127 | 120.5525 | 120.6197 | 120.5511 | 0.73496 | 0.86101 | 0.53424 | 0.72018 | 0.13101 | 0.29373 | 0.41381 | 0.29547 | 0.41623 | 0.38318 | 0.25775 | 120.5264 | 120.5662 | 120.6335 | 120.5649 | 0.74869 | 0.87474 | 0.54797 | 0.73391 | 119.7777 | 119.9785 | 119.8848 | 120.0855
1617.3594 | 121.7239 | -0.90179 | 120.7672 | 0.11269 | 0.28915 | 0.39092 | 0.28632 | 0.4025 | 0.38776 | 0.2486 | 120.5081 | 120.5342 | 120.5968 | 120.5328 | 0.75785 | 0.87932 | 0.56171 | 0.73391 | 0.12643 | 0.30289 | 0.40465 | 0.30005 | 0.41623 | 0.40149 | 0.26233 | 120.5219 | 120.5479 | 120.6106 | 120.5465 | 0.77158 | 0.89305 | 0.57544 | 0.74765 | 119.7503 | 119.9464 | 119.839 | 120.0351
1619.0938 | 121.6415 | -0.96588 | 120.7626 | 0.11727 | 0.28915 | 0.39092 | 0.29548 | 0.4025 | 0.38776 | 0.2486 | 120.4898 | 120.5296 | 120.5877 | 120.5237 | 0.77616 | 0.89763 | 0.59376 | 0.76138 | 0.13101 | 0.30289 | 0.40465 | 0.30921 | 0.41623 | 0.40149 | 0.26233 | 120.5035 | 120.5433 | 120.6014 | 120.5374 | 0.7899 | 0.91136 | 0.60749 | 0.77512 | 119.7136 | 119.896 | 119.8115 | 119.9939
1620.8438 | 121.6599 | -0.98877 | 120.7718 | 0.11269 | 0.29373 | 0.40008 | 0.30463 | 0.41166 | 0.39233 | 0.25318 | 120.4852 | 120.5067 | 120.574 | 120.5145 | 0.80821 | 0.92968 | 0.61207 | 0.78885 | 0.12643 | 0.30747 | 0.41381 | 0.31837 | 0.42539 | 0.40607 | 0.26691 | 120.499 | 120.5204 | 120.5877 | 120.5282 | 0.82195 | 0.94341 | 0.6258 | 0.80258 | 119.677 | 119.8732 | 119.7657 | 119.9619
1622.5781 | 121.7148 | -0.98419 | 120.7214 | 0.10812 | 0.29831 | 0.40465 | 0.30463 | 0.4025 | 0.38776 | 0.25318 | 120.4669 | 120.4975 | 120.5602 | 120.4962 | 0.82652 | 0.96172 | 0.64412 | 0.81632 | 0.12185 | 0.31205 | 0.41839 | 0.31837 | 0.41623 | 0.40149 | 0.26691 | 120.4806 | 120.5113 | 120.574 | 120.5099 | 0.84026 | 0.97546 | 0.65785 | 0.83005 | 119.6404 | 119.8228 | 119.7337 | 119.9161
1624.25 | 121.7285 | -1.0071 | 120.7123 | 0.11727 | 0.29831 | 0.40465 | 0.30006 | 0.41166 | 0.38776 | 0.25776 | 120.4486 | 120.4746 | 120.5373 | 120.4779 | 0.86315 | 0.98461 | 0.67159 | 0.84379 | 0.13101 | 0.31205 | 0.41839 | 0.31379 | 0.42539 | 0.40149 | 0.27149 | 120.4623 | 120.4884 | 120.5511 | 120.4916 | 0.87688 | 0.99835 | 0.68532 | 0.85752 | 119.5854 | 119.777 | 119.6742 | 119.8657
1626 | 121.701 | -1.0757 | 120.6894 | 0.11269 | 0.30289 | 0.40923 | 0.30463 | 0.42081 | 0.38318 | 0.25318 | 120.4074 | 120.438 | 120.5099 | 120.4412 | 0.8952 | 1.0258 | 0.70821 | 0.88042 | 0.12643 | 0.31662 | 0.42296 | 0.31837 | 0.43455 | 0.39691 | 0.26691 | 120.4211 | 120.4517 | 120.5236 | 120.455 | 0.90893 | 1.0395 | 0.72195 | 0.89415 | 119.5122 | 119.6992 | 119.6147 | 119.8016
1627.75 | 121.8063 | -1.062 | 120.607 | 0.11269 | 0.30289 | 0.40923 | 0.31379 | 0.41624 | 0.39233 | 0.25776 | 120.3845 | 120.4105 | 120.4732 | 120.4 | 0.94556 | 1.067 | 0.74942 | 0.9262 | 0.12643 | 0.31662 | 0.42296 | 0.32753 | 0.42997 | 0.40607 | 0.27149 | 120.3982 | 120.4243 | 120.487 | 120.4138 | 0.95929 | 1.0808 | 0.76315 | 0.93993 | 119.4389 | 119.6351 | 119.5277 | 119.7238
1629.5 | 121.7102 | -1.1673 | 120.6482 | 0.11269 | 0.30747 | 0.41381 | 0.31837 | 0.42539 | 0.39233 | 0.26233 | 120.3387 | 120.3693 | 120.4274 | 120.3634 | 0.98676 | 1.1174 | 0.79978 | 0.9674 | 0.12643 | 0.3212 | 0.42754 | 0.3321 | 0.43912 | 0.40607 | 0.27607 | 120.3524 | 120.3831 | 120.4412 | 120.3771 | 1.0005 | 1.1311 | 0.81351 | 0.98113 | 119.352 | 119.5389 | 119.4407 | 119.6277
1631.1719 | 121.8155 | -1.1856 | 120.5154 | 0.11269 | 0.30747 | 0.40465 | 0.30463 | 0.41624 | 0.39233 | 0.26233 | 120.2838 | 120.3006 | 120.3542 | 120.2993 | 1.0554 | 1.1815 | 0.8593 | 1.0315 | 0.12643 | 0.3212 | 0.41839 | 0.31837 | 0.42997 | 0.40607 | 0.27607 | 120.2975 | 120.3144 | 120.3679 | 120.313 | 1.0692 | 1.1952 | 0.87303 | 1.0452 | 119.2283 | 119.4245 | 119.2988 | 119.4949
1632.9062 | 121.7468 | -1.2726 | 120.52 | 0.12185 | 0.30747 | 0.40923 | 0.31837 | 0.42081 | 0.40149 | 0.26691 | 120.238 | 120.264 | 120.3267 | 120.2672 | 1.0966 | 1.2273 | 0.90509 | 1.0819 | 0.13558 | 0.3212 | 0.42296 | 0.3321 | 0.43455 | 0.41523 | 0.28064 | 120.2517 | 120.2777 | 120.3405 | 120.281 | 1.1104 | 1.241 | 0.91882 | 1.0956 | 119.1414 | 119.3329 | 119.2301 | 119.4216
1634.6562 | 121.8063 | -1.2863 | 120.4468 | 0.11727 | 0.30747 | 0.41381 | 0.31379 | 0.42081 | 0.40607 | 0.26691 | 120.2105 | 120.232 | 120.2947 | 120.226 | 1.1378 | 1.2685 | 0.95087 | 1.1231 | 0.13101 | 0.3212 | 0.42754 | 0.32753 | 0.43455 | 0.4198 | 0.28064 | 120.2242 | 120.2457 | 120.3084 | 120.2397 | 1.1516 | 1.2822 | 0.9646 | 1.1368 | 119.0727 | 119.2596 | 119.1568 | 119.3438
1636.3438 | 121.8704 | -1.2863 | 120.4239 | 0.11727 | 0.31663 | 0.41381 | 0.31379 | 0.42539 | 0.40149 | 0.27149 | 120.1876 | 120.2136 | 120.2626 | 120.2123 | 1.1699 | 1.3005 | 0.97834 | 1.1551 | 0.13101 | 0.33036 | 0.42754 | 0.32753 | 0.43912 | 0.41523 | 0.28522 | 120.2014 | 120.2274 | 120.2764 | 120.226 | 1.1836 | 1.3142 | 0.99207 | 1.1688 | 119.0177 | 119.2093 | 119.0927 | 119.2843
1638.0781 | 121.8521 | -1.7578 | 119.9661 | 0.12185 | 0.31205 | 0.41839 | 0.31837 | 0.42997 | 0.40607 | 0.26691 | 120.0365 | 120.0625 | 120.1115 | 120.0612 | 1.321 | 1.4516 | 1.134 | 1.3153 | 0.13558 | 0.32578 | 0.43212 | 0.3321 | 0.4437 | 0.4198 | 0.28064 | 120.0503 | 120.0763 | 120.1253 | 120.0749 | 1.3347 | 1.4653 | 1.1477 | 1.3291 | 118.7156 | 118.9025 | 118.7906 | 118.9775
1639.8281 | 121.8613 | -1.9547 | 119.7464 | 0.11269 | 0.31205 | 0.41381 | 0.30921 | 0.42997 | 0.40149 | 0.26233 | 119.5375 | 119.5635 | 119.6263 | 119.5575 | 1.82 | 1.9414 | 1.6239 | 1.8098 | 0.12643 | 0.32578 | 0.42754 | 0.32295 | 0.4437 | 0.41523 | 0.27607 | 119.5512 | 119.5772 | 119.64 | 119.5712 | 1.8337 | 1.9552 | 1.6376 | 1.8235 | 117.7175 | 117.9136 | 117.8063 | 118.0024
1641.5781 | 121.8292 | -2.005 | 119.6915 | 0.11269 | 0.32121 | 0.42755 | 0.30463 | 0.42081 | 0.39691 | 0.27149 | 119.4917 | 119.5222 | 119.5713 | 119.5117 | 1.8658 | 1.9964 | 1.6743 | 1.851 | 0.12643 | 0.33494 | 0.44128 | 0.31837 | 0.43455 | 0.41065 | 0.28522 | 119.5054 | 119.536 | 119.585 | 119.5254 | 1.8795 | 2.0101 | 1.688 | 1.8647 | 117.6259 | 117.8174 | 117.7055 | 117.8971
1643.25 | 121.8384 | -2.0187 | 119.7098 | 0.11727 | 0.32121 | 0.42297 | 0.32753 | 0.42997 | 0.40607 | 0.27149 | 119.478 | 119.4948 | 119.553 | 119.4979 | 1.8932 | 2.0193 | 1.6971 | 1.8739 | 0.13101 | 0.33494 | 0.4367 | 0.34126 | 0.4437 | 0.4198 | 0.28522 | 119.4917 | 119.5085 | 119.5667 | 119.5117 | 1.907 | 2.033 | 1.7109 | 1.8876 | 117.5847 | 117.7808 | 117.6598 | 117.8559
1644.9375 | 121.7377 | -2.0874 | 119.7281 | 0.12643 | 0.32121 | 0.42755 | 0.32753 | 0.42997 | 0.41065 | 0.27607 | 119.4505 | 119.4902 | 119.5301 | 119.4796 | 1.9024 | 2.0376 | 1.7155 | 1.8922 | 0.14016 | 0.33494 | 0.44128 | 0.34126 | 0.4437 | 0.42438 | 0.2898 | 119.4642 | 119.5039 | 119.5438 | 119.4934 | 1.9161 | 2.0513 | 1.7292 | 1.9059 | 117.5481 | 117.735 | 117.6277 | 117.8146
1646.6719 | 121.8063 | -2.0737 | 119.6777 | 0.11269 | 0.33036 | 0.42755 | 0.32295 | 0.43912 | 0.41065 | 0.28522 | 119.4368 | 119.4627 | 119.5164 | 119.4567 | 1.9299 | 2.0605 | 1.7429 | 1.9151 | 0.12643 | 0.3441 | 0.44128 | 0.33668 | 0.45286 | 0.42438 | 0.29896 | 119.4505 | 119.4765 | 119.5301 | 119.4705 | 1.9436 | 2.0742 | 1.7567 | 1.9288 | 117.5069 | 117.6938 | 117.5865 | 117.7734
1648.4062 | 121.8155 | -2.1103 | 119.6915 | 0.11727 | 0.32578 | 0.43212 | 0.32753 | 0.4437 | 0.41523 | 0.28065 | 119.4368 | 119.4627 | 119.5118 | 119.4567 | 1.9344 | 2.0696 | 1.7429 | 1.9242 | 0.13101 | 0.33952 | 0.44586 | 0.34126 | 0.45744 | 0.42896 | 0.29438 | 119.4505 | 119.4765 | 119.5255 | 119.4705 | 1.9482 | 2.0833 | 1.7567 | 1.938 | 117.5023 | 117.6938 | 117.5774 | 117.7689
1650.1562 | 121.8521 | -2.1103 | 119.6228 | 0.11727 | 0.31663 | 0.4367 | 0.33211 | 0.43912 | 0.42438 | 0.28522 | 119.4093 | 119.449 | 119.4981 | 119.4384 | 1.9573 | 2.0788 | 1.7612 | 1.9426 | 0.13101 | 0.33036 | 0.45044 | 0.34584 | 0.45286 | 0.43812 | 0.29896 | 119.423 | 119.4627 | 119.5118 | 119.4522 | 1.9711 | 2.0925 | 1.775 | 1.9563 | 117.4519 | 117.648 | 117.5407 | 117.7368
1651.8906 | 121.7514 | -2.1103 | 119.7052 | 0.11727 | 0.33036 | 0.4367 | 0.33668 | 0.4437 | 0.42438 | 0.29438 | 119.4459 | 119.4765 | 119.521 | 119.4567 | 1.939 | 2.0742 | 1.7429 | 1.9242 | 0.13101 | 0.3441 | 0.45044 | 0.35042 | 0.45744 | 0.43812 | 0.30811 | 119.4596 | 119.4902 | 119.5347 | 119.4705 | 1.9528 | 2.0879 | 1.7567 | 1.938 | 117.5069 | 117.703 | 117.5819 | 117.778
1653.5625 | 121.8201 | -2.0325 | 119.7052 | 0.11727 | 0.33036 | 0.4367 | 0.33211 | 0.43455 | 0.42438 | 0.2898 | 119.4734 | 119.5131 | 119.5576 | 119.4979 | 1.9116 | 2.0284 | 1.7109 | 1.8922 | 0.13101 | 0.3441 | 0.45044 | 0.34584 | 0.44828 | 0.43812 | 0.30353 | 119.4871 | 119.5268 | 119.5713 | 119.5117 | 1.9253 | 2.0421 | 1.7246 | 1.9059 | 117.5618 | 117.7625 | 117.646 | 117.8467
1655.3125 | 121.788 | -2.0599 | 119.7464 | 0.10812 | 0.33494 | 0.4367 | 0.33668 | 0.43455 | 0.42438 | 0.28522 | 119.4871 | 119.5177 | 119.5667 | 119.5117 | 1.8932 | 2.0284 | 1.7063 | 1.8876 | 0.12185 | 0.34868 | 0.45044 | 0.35042 | 0.44828 | 0.43812 | 0.29896 | 119.5008 | 119.5314 | 119.5805 | 119.5254 | 1.907 | 2.0421 | 1.72 | 1.9013 | 117.5939 | 117.7808 | 117.6735 | 117.8604
1656.9844 | 121.8887 | -2.0325 | 119.7144 | 0.12185 | 0.33036 | 0.44128 | 0.33211 | 0.44828 | 0.42438 | 0.29438 | 119.4871 | 119.5177 | 119.5622 | 119.5071 | 1.8932 | 2.0238 | 1.7109 | 1.883 | 0.13558 | 0.3441 | 0.45502 | 0.34584 | 0.46201 | 0.43812 | 0.30811 | 119.5008 | 119.5314 | 119.5759 | 119.5208 | 1.907 | 2.0376 | 1.7246 | 1.8968 | 117.5939 | 117.7762 | 117.6689 | 117.8513
1658.7188 | 121.8475 | -2.0325 | 119.7235 | 0.11269 | 0.33952 | 0.44128 | 0.33668 | 0.45286 | 0.42896 | 0.29896 | 119.4963 | 119.5314 | 119.5805 | 119.53 | 1.8887 | 2.0284 | 1.6926 | 1.8785 | 0.12643 | 0.35325 | 0.45502 | 0.35042 | 0.46659 | 0.4427 | 0.31269 | 119.51 | 119.5451 | 119.5942 | 119.5437 | 1.9024 | 2.0421 | 1.7063 | 1.8922 | 117.6076 | 117.8037 | 117.6918 | 117.8879
1660.4688 | 121.8933 | -1.9913 | 119.7418 | 0.11269 | 0.3441 | 0.44128 | 0.33668 | 0.44828 | 0.42438 | 0.29896 | 119.5375 | 119.5772 | 119.6171 | 119.5621 | 1.8475 | 1.9781 | 1.6559 | 1.8281 | 0.12643 | 0.35783 | 0.45502 | 0.35042 | 0.46201 | 0.43812 | 0.31269 | 119.5512 | 119.5909 | 119.6308 | 119.5758 | 1.8612 | 1.9918 | 1.6697 | 1.8418 | 117.69 | 117.8815 | 117.7696 | 117.9612
1662.1406 | 121.8521 | -1.9684 | 119.7922 | 0.11727 | 0.3441 | 0.45502 | 0.34584 | 0.4437 | 0.43812 | 0.29438 | 119.5466 | 119.5909 | 119.6354 | 119.5758 | 1.8337 | 1.9689 | 1.6605 | 1.8281 | 0.13101 | 0.35783 | 0.46875 | 0.35957 | 0.45744 | 0.45185 | 0.30811 | 119.5604 | 119.6047 | 119.6491 | 119.5895 | 1.8475 | 1.9826 | 1.6743 | 1.8418 | 117.7129 | 117.8861 | 117.8017 | 117.9749
1663.875 | 121.7697 | -1.9547 | 119.8563 | 0.12185 | 0.34868 | 0.45502 | 0.35042 | 0.46202 | 0.43354 | 0.29438 | 119.5833 | 119.6138 | 119.6583 | 119.6078 | 1.8108 | 1.9506 | 1.6193 | 1.796 | 0.13558 | 0.36241 | 0.46875 | 0.36415 | 0.47575 | 0.44727 | 0.30811 | 119.597 | 119.6276 | 119.672 | 119.6216 | 1.8246 | 1.9643 | 1.633 | 1.8098 | 117.7724 | 117.9639 | 117.8475 | 118.039
1665.625 | 121.8933 | -1.9501 | 119.838 | 0.11727 | 0.34868 | 0.45044 | 0.34584 | 0.45744 | 0.42896 | 0.30354 | 119.5878 | 119.6276 | 119.672 | 119.6124 | 1.8017 | 1.9369 | 1.6193 | 1.8006 | 0.13101 | 0.36241 | 0.46417 | 0.35957 | 0.47117 | 0.4427 | 0.31727 | 119.6016 | 119.6413 | 119.6858 | 119.6262 | 1.8154 | 1.9506 | 1.633 | 1.8144 | 117.7862 | 117.9685 | 117.8704 | 118.0527
1667.2969 | 121.8521 | -1.7532 | 119.9982 | 0.12185 | 0.35326 | 0.46418 | 0.35042 | 0.47117 | 0.43354 | 0.30354 | 119.7893 | 119.8153 | 119.8643 | 119.8047 | 1.614 | 1.74 | 1.4316 | 1.6083 | 0.13558 | 0.36699 | 0.47791 | 0.36415 | 0.4849 | 0.44727 | 0.31727 | 119.803 | 119.829 | 119.8781 | 119.8185 | 1.6277 | 1.7537 | 1.4453 | 1.6221 | 118.1753 | 118.3577 | 118.2504 | 118.4327
1669.0469 | 121.7972 | -1.5656 | 120.2728 | 0.12643 | 0.36699 | 0.46418 | 0.35958 | 0.47117 | 0.44728 | 0.31727 | 119.9175 | 119.9572 | 119.9971 | 119.933 | 1.4904 | 1.6164 | 1.3126 | 1.4802 | 0.14016 | 0.38073 | 0.47791 | 0.37331 | 0.4849 | 0.46101 | 0.331 | 119.9312 | 119.971 | 120.0108 | 119.9467 | 1.5041 | 1.6301 | 1.3263 | 1.4939 | 118.4271 | 118.6049 | 118.5067 | 118.6845
1670.7969 | 121.907 | -1.7258 | 119.9982 | 0.11727 | 0.36241 | 0.46875 | 0.355 | 0.46202 | 0.45185 | 0.31269 | 119.7252 | 119.7466 | 119.8002 | 119.7452 | 1.6918 | 1.8178 | 1.4957 | 1.6724 | 0.13101 | 0.37615 | 0.48249 | 0.36873 | 0.47575 | 0.46559 | 0.32643 | 119.7389 | 119.7603 | 119.814 | 119.7589 | 1.7055 | 1.8316 | 1.5094 | 1.6862 | 118.0334 | 118.2295 | 118.1084 | 118.3045
1672.5469 | 121.7743 | -1.5884 | 120.2682 | 0.11727 | 0.36699 | 0.46875 | 0.37331 | 0.47575 | 0.45643 | 0.31727 | 120.0594 | 120.0946 | 120.1482 | 120.0841 | 1.353 | 1.4745 | 1.1752 | 1.3474 | 0.13101 | 0.38073 | 0.48249 | 0.38704 | 0.48948 | 0.47016 | 0.331 | 120.0732 | 120.1083 | 120.1619 | 120.0978 | 1.3667 | 1.4882 | 1.1889 | 1.3611 | 118.7064 | 118.8842 | 118.7952 | 118.973
1674.2188 | 121.8887 | -1.5198 | 120.2637 | 0.12643 | 0.37157 | 0.47333 | 0.36873 | 0.4849 | 0.45185 | 0.32185 | 119.9358 | 119.9847 | 120.02 | 119.9559 | 1.472 | 1.6118 | 1.2805 | 1.4664 | 0.14016 | 0.38531 | 0.48706 | 0.38247 | 0.49864 | 0.46559 | 0.33558 | 119.9495 | 119.9984 | 120.0337 | 119.9696 | 1.4858 | 1.6255 | 1.2942 | 1.4802 | 118.4638 | 118.6553 | 118.5479 | 118.7395
1675.9062 | 121.8567 | -1.4832 | 120.3461 | 0.12185 | 0.36699 | 0.47791 | 0.37789 | 0.4849 | 0.46101 | 0.33101 | 120.2517 | 120.2732 | 120.3267 | 120.2718 | 1.1836 | 1.3005 | 1.0012 | 1.1688 | 0.13558 | 0.38073 | 0.49164 | 0.39162 | 0.49864 | 0.47474 | 0.34474 | 120.2655 | 120.2869 | 120.3405 | 120.2855 | 1.1974 | 1.3142 | 1.015 | 1.1826 | 119.0681 | 119.2505 | 119.1431 | 119.3255
1677.6562 | 121.9162 | -0.93384 | 120.8267 | 0.11727 | 0.38073 | 0.48249 | 0.38705 | 0.48948 | 0.47475 | 0.33558 | 120.5585 | 120.6074 | 120.6518 | 120.5969 | 0.84942 | 0.98004 | 0.66701 | 0.83921 | 0.13101 | 0.39446 | 0.49622 | 0.40078 | 0.50322 | 0.48848 | 0.34932 | 120.5722 | 120.6212 | 120.6655 | 120.6106 | 0.86315 | 0.99377 | 0.68074 | 0.85294 | 119.7091 | 119.8915 | 119.8024 | 119.9848
1679.3906 | 121.8979 | -0.87433 | 120.8862 | 0.12185 | 0.38989 | 0.48707 | 0.38247 | 0.49406 | 0.47475 | 0.33101 | 120.7004 | 120.7356 | 120.7846 | 120.7251 | 0.72123 | 0.84269 | 0.53881 | 0.71102 | 0.13558 | 0.40362 | 0.5008 | 0.3962 | 0.50779 | 0.48848 | 0.34474 | 120.7141 | 120.7494 | 120.7983 | 120.7389 | 0.73496 | 0.85643 | 0.55255 | 0.72476 | 119.9792 | 120.1616 | 120.0633 | 120.2457
1681.0625 | 121.9162 | -0.97504 | 120.7855 | 0.11727 | 0.38531 | 0.49165 | 0.38705 | 0.49864 | 0.47475 | 0.33558 | 120.4532 | 120.4975 | 120.5419 | 120.4687 | 0.96845 | 1.0945 | 0.80436 | 0.9674 | 0.13101 | 0.39904 | 0.50538 | 0.40078 | 0.51237 | 0.48848 | 0.34932 | 120.4669 | 120.5113 | 120.5556 | 120.4824 | 0.98218 | 1.1082 | 0.81809 | 0.98113 | 119.4847 | 119.6488 | 119.5735 | 119.7375
1682.8125 | 121.9254 | -0.98419 | 120.8038 | 0.11727 | 0.38531 | 0.48707 | 0.39163 | 0.50322 | 0.47932 | 0.34474 | 120.6317 | 120.6715 | 120.725 | 120.6519 | 0.79906 | 0.92052 | 0.60291 | 0.78885 | 0.13101 | 0.39904 | 0.5008 | 0.40536 | 0.51695 | 0.49306 | 0.35847 | 120.6455 | 120.6853 | 120.7388 | 120.6656 | 0.81279 | 0.93425 | 0.61664 | 0.80258 | 119.8327 | 120.0288 | 119.926 | 120.1221
1684.4844 | 121.843 | -0.90637 | 120.9412 | 0.11727 | 0.39447 | 0.5008 | 0.40078 | 0.50779 | 0.4839 | 0.34932 | 120.7416 | 120.7723 | 120.8166 | 120.7572 | 0.68918 | 0.81522 | 0.50677 | 0.68355 | 0.13101 | 0.4082 | 0.51454 | 0.41452 | 0.52153 | 0.49764 | 0.36305 | 120.7554 | 120.786 | 120.8303 | 120.7709 | 0.70291 | 0.82896 | 0.5205 | 0.69729 | 120.0524 | 120.2349 | 120.1274 | 120.3098
1686.2188 | 121.8292 | -0.66376 | 121.1792 | 0.11727 | 0.39905 | 0.50538 | 0.40994 | 0.51237 | 0.49764 | 0.3539 | 120.9064 | 120.9417 | 120.9952 | 120.922 | 0.52894 | 0.65957 | 0.34652 | 0.5279 | 0.13101 | 0.41278 | 0.51911 | 0.42367 | 0.52611 | 0.51137 | 0.36763 | 120.9202 | 120.9554 | 121.0089 | 120.9358 | 0.54268 | 0.6733 | 0.36025 | 0.54163 | 120.3775 | 120.5599 | 120.4662 | 120.6486
1687.9531 | 121.8246 | -0.92468 | 120.9457 | 0.12643 | 0.41278 | 0.51454 | 0.40078 | 0.52153 | 0.49306 | 0.34932 | 120.8744 | 120.9096 | 120.9585 | 120.8854 | 0.56099 | 0.69162 | 0.38315 | 0.55994 | 0.14016 | 0.42651 | 0.52827 | 0.41452 | 0.53526 | 0.50679 | 0.36305 | 120.8881 | 120.9234 | 120.9723 | 120.8991 | 0.57472 | 0.70535 | 0.39688 | 0.57368 | 120.3134 | 120.4912 | 120.3975 | 120.5754
1689.6875 | 121.788 | -0.83313 | 121.0327 | 0.11727 | 0.4082 | 0.51454 | 0.40536 | 0.52153 | 0.48848 | 0.36305 | 120.8698 | 120.9096 | 120.9585 | 120.89 | 0.56557 | 0.6962 | 0.38315 | 0.55536 | 0.13101 | 0.42194 | 0.52827 | 0.41909 | 0.53526 | 0.50221 | 0.37679 | 120.8836 | 120.9234 | 120.9723 | 120.9037 | 0.5793 | 0.70993 | 0.39688 | 0.5691 | 120.3043 | 120.4867 | 120.393 | 120.5754
1691.4219 | 121.7926 | -0.73242 | 121.0922 | 0.12185 | 0.41736 | 0.51912 | 0.4191 | 0.52611 | 0.50222 | 0.36305 | 120.8744 | 120.9188 | 120.9677 | 120.9037 | 0.55183 | 0.67331 | 0.37399 | 0.55994 | 0.13558 | 0.43109 | 0.53285 | 0.43283 | 0.53984 | 0.51595 | 0.37679 | 120.8881 | 120.9325 | 120.9814 | 120.9174 | 0.56557 | 0.68704 | 0.38772 | 0.57368 | 120.3226 | 120.5004 | 120.4159 | 120.5937
1693.1562 | 121.8567 | -0.74616 | 121.0464 | 0.12643 | 0.41278 | 0.51912 | 0.41452 | 0.53068 | 0.50679 | 0.36305 | 120.8332 | 120.873 | 120.9173 | 120.8579 | 0.58846 | 0.7374 | 0.41978 | 0.59657 | 0.14016 | 0.42651 | 0.53285 | 0.42825 | 0.54442 | 0.52053 | 0.37679 | 120.8469 | 120.8867 | 120.9311 | 120.8717 | 0.60219 | 0.75113 | 0.43351 | 0.6103 | 120.2447 | 120.4134 | 120.3289 | 120.4976
1694.8438 | 121.9208 | -1.1124 | 120.6802 | 0.11727 | 0.41278 | 0.53285 | 0.4191 | 0.52611 | 0.49306 | 0.36763 | 120.6088 | 120.6441 | 120.6793 | 120.6152 | 0.84484 | 0.9663 | 0.66243 | 0.83463 | 0.13101 | 0.42651 | 0.54659 | 0.43283 | 0.53984 | 0.50679 | 0.38136 | 120.6226 | 120.6578 | 120.693 | 120.629 | 0.85857 | 0.98003 | 0.67616 | 0.84837 | 119.764 | 119.9464 | 119.8344 | 120.0168
1696.5938 | 121.8658 | -0.60883 | 121.225 | 0.11727 | 0.42194 | 0.53743 | 0.42368 | 0.53984 | 0.51137 | 0.38137 | 120.9248 | 120.96 | 121.0043 | 120.9495 | 0.52437 | 0.64584 | 0.34194 | 0.51874 | 0.13101 | 0.43567 | 0.55117 | 0.43741 | 0.55357 | 0.52511 | 0.3951 | 120.9385 | 120.9737 | 121.018 | 120.9632 | 0.5381 | 0.65957 | 0.35568 | 0.53247 | 120.4004 | 120.5828 | 120.4799 | 120.6624
1698.3281 | 121.8796 | -0.9201 | 120.9183 | 0.13101 | 0.41736 | 0.53743 | 0.42825 | 0.53526 | 0.51137 | 0.38594 | 120.7096 | 120.7539 | 120.7983 | 120.7251 | 0.73038 | 0.85185 | 0.55255 | 0.7156 | 0.14474 | 0.43109 | 0.55117 | 0.44199 | 0.549 | 0.52511 | 0.39968 | 120.7233 | 120.7677 | 120.812 | 120.7389 | 0.74412 | 0.86558 | 0.56628 | 0.72933 | 119.9792 | 120.157 | 120.0679 | 120.2457
1700.0625 | 121.8796 | -0.60883 | 121.2021 | 0.12643 | 0.42652 | 0.54201 | 0.43283 | 0.54442 | 0.51595 | 0.38137 | 120.966 | 121.0195 | 121.0547 | 120.9953 | 0.47401 | 0.60006 | 0.29616 | 0.47754 | 0.14016 | 0.44025 | 0.55574 | 0.44657 | 0.55815 | 0.52968 | 0.3951 | 120.9797 | 121.0332 | 121.0684 | 121.009 | 0.48774 | 0.61379 | 0.30989 | 0.49127 | 120.492 | 120.6698 | 120.5807 | 120.7585
1701.8125 | 121.9254 | -0.68207 | 121.1197 | 0.12185 | 0.44026 | 0.54201 | 0.43283 | 0.54442 | 0.52053 | 0.38594 | 120.9614 | 121.0058 | 121.0455 | 120.9816 | 0.48774 | 0.60921 | 0.32363 | 0.48669 | 0.13558 | 0.45399 | 0.55574 | 0.44657 | 0.55815 | 0.53426 | 0.39968 | 120.9751 | 121.0195 | 121.0593 | 120.9953 | 0.50147 | 0.62294 | 0.33736 | 0.50043 | 120.4736 | 120.6378 | 120.5578 | 120.7219
1703.5 | 121.7926 | -0.62256 | 121.2982 | 0.12643 | 0.44026 | 0.54659 | 0.44199 | 0.55815 | 0.52511 | 0.39052 | 121.0163 | 121.047 | 121.0867 | 121.0319 | 0.44196 | 0.57259 | 0.27327 | 0.45007 | 0.14016 | 0.45399 | 0.56032 | 0.45572 | 0.57188 | 0.53884 | 0.40425 | 121.0301 | 121.0607 | 121.1005 | 121.0457 | 0.45569 | 0.58632 | 0.287 | 0.4638 | 120.5744 | 120.7431 | 120.6448 | 120.8135
1705.2344 | 121.8842 | -0.59967 | 121.2296 | 0.13101 | 0.43568 | 0.54659 | 0.44199 | 0.55357 | 0.52969 | 0.39968 | 120.9934 | 121.0287 | 121.073 | 120.9999 | 0.46027 | 0.58174 | 0.29158 | 0.45922 | 0.14474 | 0.44941 | 0.56032 | 0.45572 | 0.56731 | 0.54342 | 0.41341 | 121.0072 | 121.0424 | 121.0867 | 121.0136 | 0.474 | 0.59548 | 0.30531 | 0.47296 | 120.5332 | 120.7019 | 120.6127 | 120.7814
1706.9062 | 121.8109 | -0.6134 | 121.2662 | 0.12643 | 0.44483 | 0.56033 | 0.4603 | 0.56273 | 0.52969 | 0.3951 | 121.0301 | 121.0653 | 121.1096 | 121.0502 | 0.42822 | 0.5497 | 0.26411 | 0.42718 | 0.14016 | 0.45857 | 0.57406 | 0.47404 | 0.57646 | 0.54342 | 0.40883 | 121.0438 | 121.079 | 121.1233 | 121.064 | 0.44196 | 0.56343 | 0.27784 | 0.44091 | 120.6018 | 120.766 | 120.6814 | 120.8455
1708.6406 | 121.9482 | -0.75531 | 121.051 | 0.12643 | 0.44941 | 0.55575 | 0.44657 | 0.56273 | 0.53426 | 0.3951 | 120.8607 | 120.9005 | 120.9494 | 120.8762 | 0.58846 | 0.71909 | 0.4152 | 0.58283 | 0.14016 | 0.46315 | 0.56948 | 0.4603 | 0.57646 | 0.548 | 0.40883 | 120.8744 | 120.9142 | 120.9631 | 120.89 | 0.60219 | 0.73282 | 0.42893 | 0.59657 | 120.2722 | 120.4455 | 120.3609 | 120.5342
1710.375 | 121.8155 | -0.67291 | 121.1792 | 0.11727 | 0.44483 | 0.56033 | 0.46488 | 0.56731 | 0.548 | 0.40884 | 120.9202 | 120.9691 | 121.0135 | 120.9449 | 0.52894 | 0.65957 | 0.3511 | 0.5279 | 0.13101 | 0.45857 | 0.57406 | 0.47862 | 0.58104 | 0.56173 | 0.42257 | 120.9339 | 120.9829 | 121.0272 | 120.9587 | 0.54268 | 0.6733 | 0.36483 | 0.54163 | 120.3912 | 120.5691 | 120.4845 | 120.6624
1712.0625 | 121.9345 | -0.58594 | 121.1838 | 0.13101 | 0.45399 | 0.5649 | 0.4603 | 0.56731 | 0.55258 | 0.41341 | 120.9797 | 121.0195 | 121.0593 | 120.9999 | 0.46943 | 0.60006 | 0.30532 | 0.46838 | 0.14474 | 0.46773 | 0.57864 | 0.47404 | 0.58104 | 0.56631 | 0.42715 | 120.9934 | 121.0332 | 121.073 | 121.0136 | 0.48316 | 0.61379 | 0.31905 | 0.48211 | 120.5103 | 120.6744 | 120.5898 | 120.7539
1713.7969 | 121.8567 | -0.56305 | 121.2845 | 0.12643 | 0.45399 | 0.5649 | 0.47404 | 0.58104 | 0.55716 | 0.41341 | 121.0118 | 121.0653 | 121.1005 | 121.0411 | 0.43738 | 0.56801 | 0.26869 | 0.44549 | 0.14016 | 0.46773 | 0.57864 | 0.48777 | 0.59477 | 0.57089 | 0.42715 | 121.0255 | 121.079 | 121.1142 | 121.0548 | 0.45111 | 0.58174 | 0.28242 | 0.45922 | 120.5744 | 120.7431 | 120.6631 | 120.8318
1715.5312 | 121.8842 | -0.6134 | 121.2067 | 0.11727 | 0.45399 | 0.57406 | 0.46488 | 0.57189 | 0.548 | 0.41341 | 120.9751 | 121.0149 | 121.0501 | 120.9861 | 0.49232 | 0.61379 | 0.30989 | 0.47754 | 0.13101 | 0.46773 | 0.58779 | 0.47862 | 0.58562 | 0.56173 | 0.42715 | 120.9889 | 121.0287 | 121.0638 | 120.9999 | 0.50605 | 0.62752 | 0.32363 | 0.49127 | 120.4828 | 120.6652 | 120.5578 | 120.7402
1717.2031 | 121.9391 | -0.52643 | 121.2616 | 0.12185 | 0.45857 | 0.57864 | 0.47404 | 0.58104 | 0.55258 | 0.42257 | 121.0026 | 121.0378 | 121.0867 | 121.0136 | 0.45569 | 0.5909 | 0.29616 | 0.47296 | 0.13558 | 0.4723 | 0.59237 | 0.48777 | 0.59477 | 0.56631 | 0.4363 | 121.0163 | 121.0516 | 121.1005 | 121.0273 | 0.46943 | 0.60463 | 0.30989 | 0.48669 | 120.5469 | 120.7064 | 120.631 | 120.7906
1718.8906 | 121.8567 | -0.5722 | 121.2799 | 0.12643 | 0.45857 | 0.57864 | 0.47862 | 0.58562 | 0.56173 | 0.43173 | 121.0392 | 121.0836 | 121.1233 | 121.0594 | 0.41907 | 0.55428 | 0.25495 | 0.42718 | 0.14016 | 0.4723 | 0.59237 | 0.49235 | 0.59935 | 0.57547 | 0.44546 | 121.053 | 121.0974 | 121.1371 | 121.0731 | 0.4328 | 0.56801 | 0.26869 | 0.44091 | 120.6202 | 120.7843 | 120.7043 | 120.8684
1720.6406 | 121.9437 | -0.52185 | 121.257 | 0.13559 | 0.46773 | 0.5878 | 0.4832 | 0.59478 | 0.56631 | 0.42715 | 121.0667 | 121.1065 | 121.16 | 121.0869 | 0.3916 | 0.51765 | 0.24122 | 0.39971 | 0.14932 | 0.48146 | 0.60153 | 0.49693 | 0.60851 | 0.58005 | 0.44088 | 121.0804 | 121.1202 | 121.1737 | 121.1006 | 0.40533 | 0.53138 | 0.25495 | 0.41344 | 120.6751 | 120.8255 | 120.7684 | 120.9188
1722.3281 | 121.9528 | -0.88348 | 120.9183 | 0.13101 | 0.46773 | 0.58322 | 0.47862 | 0.5902 | 0.56173 | 0.42715 | 120.8469 | 120.8822 | 120.9311 | 120.8625 | 0.61593 | 0.74198 | 0.46098 | 0.62404 | 0.14474 | 0.48146 | 0.59695 | 0.49235 | 0.60393 | 0.57547 | 0.44088 | 120.8607 | 120.8959 | 120.9448 | 120.8762 | 0.62966 | 0.75571 | 0.47471 | 0.63777 | 120.231 | 120.3859 | 120.3151 | 120.4701
1724.0781 | 121.9345 | -0.53558 | 121.3074 | 0.13101 | 0.46315 | 0.5878 | 0.49235 | 0.5902 | 0.57089 | 0.42715 | 121.0575 | 121.0974 | 121.1371 | 121.0823 | 0.40533 | 0.54054 | 0.25038 | 0.41802 | 0.14474 | 0.47688 | 0.60153 | 0.50609 | 0.60393 | 0.58462 | 0.44088 | 121.0713 | 121.1111 | 121.1508 | 121.096 | 0.41907 | 0.55427 | 0.26411 | 0.43175 | 120.6522 | 120.8072 | 120.7318 | 120.8867
1725.8281 | 121.8292 | -0.53558 | 121.3715 | 0.13559 | 0.46773 | 0.5878 | 0.49693 | 0.59935 | 0.58005 | 0.4363 | 121.1354 | 121.1706 | 121.2195 | 121.151 | 0.34582 | 0.46729 | 0.20459 | 0.3585 | 0.14932 | 0.48146 | 0.60153 | 0.51067 | 0.61309 | 0.59378 | 0.45004 | 121.1491 | 121.1843 | 121.2332 | 121.1647 | 0.35955 | 0.48102 | 0.21832 | 0.37224 | 120.7896 | 120.9308 | 120.8737 | 121.0149
1727.5156 | 121.9391 | -0.49896 | 121.3074 | 0.13101 | 0.47689 | 0.59696 | 0.49693 | 0.59935 | 0.58005 | 0.43173 | 121.1354 | 121.1752 | 121.2149 | 121.1556 | 0.3504 | 0.46271 | 0.20001 | 0.36308 | 0.14474 | 0.49062 | 0.61069 | 0.51067 | 0.61309 | 0.59378 | 0.44546 | 121.1491 | 121.1889 | 121.2286 | 121.1693 | 0.36413 | 0.47645 | 0.21375 | 0.37682 | 120.785 | 120.9354 | 120.8645 | 121.0149
1729.2656 | 121.9391 | -0.60883 | 121.1884 | 0.13101 | 0.48146 | 0.59696 | 0.49693 | 0.59935 | 0.58005 | 0.44546 | 121.0667 | 121.1019 | 121.1462 | 121.0777 | 0.40991 | 0.53596 | 0.25495 | 0.4226 | 0.14474 | 0.4952 | 0.61069 | 0.51067 | 0.61309 | 0.59378 | 0.45919 | 121.0804 | 121.1157 | 121.16 | 121.0914 | 0.42364 | 0.5497 | 0.26869 | 0.43633 | 120.6568 | 120.8117 | 120.7363 | 120.8913
1730.9531 | 121.9254 | -0.53101 | 121.2616 | 0.13101 | 0.49062 | 0.60153 | 0.50609 | 0.60851 | 0.58463 | 0.44088 | 121.0026 | 121.0378 | 121.0913 | 121.0182 | 0.46485 | 0.59548 | 0.29616 | 0.46838 | 0.14474 | 0.50435 | 0.61527 | 0.51982 | 0.62224 | 0.59836 | 0.45461 | 121.0163 | 121.0516 | 121.105 | 121.0319 | 0.47858 | 0.60921 | 0.30989 | 0.48211 | 120.5377 | 120.7064 | 120.6265 | 120.7951
1732.6875 | 121.9025 | -0.51727 | 121.3303 | 0.12643 | 0.48604 | 0.61069 | 0.51067 | 0.61309 | 0.58463 | 0.45004 | 121.1125 | 121.1615 | 121.2058 | 121.1372 | 0.35955 | 0.49018 | 0.21375 | 0.36766 | 0.14016 | 0.49978 | 0.62442 | 0.5244 | 0.62682 | 0.59836 | 0.46377 | 121.1262 | 121.1752 | 121.2195 | 121.151 | 0.37328 | 0.50392 | 0.22748 | 0.38139 | 120.7529 | 120.8987 | 120.8462 | 120.992
1734.4375 | 121.8246 | -0.55389 | 121.3623 | 0.13101 | 0.49062 | 0.61527 | 0.51067 | 0.62224 | 0.59836 | 0.45919 | 121.0942 | 121.134 | 121.1737 | 121.1143 | 0.38702 | 0.51765 | 0.23206 | 0.39971 | 0.14474 | 0.50435 | 0.629 | 0.5244 | 0.63598 | 0.61209 | 0.47293 | 121.1079 | 121.1477 | 121.1874 | 121.1281 | 0.40075 | 0.53138 | 0.24579 | 0.41344 | 120.7071 | 120.8621 | 120.7867 | 120.9416
1736.125 | 121.9391 | -0.53558 | 121.2753 | 0.13559 | 0.49978 | 0.61069 | 0.51525 | 0.62682 | 0.60294 | 0.46377 | 121.085 | 121.1202 | 121.1646 | 121.1052 | 0.38244 | 0.52223 | 0.23206 | 0.40886 | 0.14932 | 0.51351 | 0.62442 | 0.52898 | 0.64055 | 0.61667 | 0.47751 | 121.0987 | 121.134 | 121.1783 | 121.1189 | 0.39617 | 0.53596 | 0.24579 | 0.4226 | 120.7026 | 120.8529 | 120.7821 | 120.9325
1737.8125 | 121.8018 | -0.56305 | 121.3257 | 0.13101 | 0.50436 | 0.61985 | 0.51982 | 0.62682 | 0.60752 | 0.46835 | 121.0942 | 121.1294 | 121.1783 | 121.1052 | 0.38702 | 0.51765 | 0.23206 | 0.39971 | 0.14474 | 0.51809 | 0.63358 | 0.53356 | 0.64055 | 0.62125 | 0.48208 | 121.1079 | 121.1431 | 121.192 | 121.1189 | 0.40075 | 0.53138 | 0.24579 | 0.41344 | 120.7071 | 120.8621 | 120.7913 | 120.9462
1739.5469 | 121.8338 | -0.62256 | 121.2433 | 0.13101 | 0.49978 | 0.62443 | 0.52898 | 0.64055 | 0.6121 | 0.46377 | 121.0759 | 121.1157 | 121.1554 | 121.096 | 0.40533 | 0.52681 | 0.2458 | 0.40429 | 0.14474 | 0.51351 | 0.63816 | 0.54271 | 0.65429 | 0.62583 | 0.47751 | 121.0896 | 121.1294 | 121.1691 | 121.1098 | 0.41907 | 0.54054 | 0.25953 | 0.41802 | 120.6705 | 120.8301 | 120.7501 | 120.9096
1741.2969 | 121.907 | -0.53558 | 121.2936 | 0.12643 | 0.50436 | 0.62443 | 0.51982 | 0.6314 | 0.60752 | 0.46835 | 121.0942 | 121.1248 | 121.1829 | 121.1098 | 0.3916 | 0.5085 | 0.23664 | 0.39971 | 0.14016 | 0.51809 | 0.63816 | 0.53356 | 0.64513 | 0.62125 | 0.48208 | 121.1079 | 121.1386 | 121.1966 | 121.1235 | 0.40533 | 0.52223 | 0.25037 | 0.41344 | 120.7026 | 120.8575 | 120.7913 | 120.9462
1742.9844 | 121.9162 | -0.59967 | 121.2158 | 0.13559 | 0.51352 | 0.63816 | 0.52898 | 0.64055 | 0.6121 | 0.47751 | 120.9797 | 121.0104 | 121.0638 | 120.9907 | 0.50605 | 0.6321 | 0.32821 | 0.50043 | 0.14932 | 0.52725 | 0.6519 | 0.54271 | 0.65429 | 0.62583 | 0.49124 | 120.9934 | 121.0241 | 121.0776 | 121.0044 | 0.51979 | 0.64584 | 0.34194 | 0.51416 | 120.4737 | 120.6515 | 120.5578 | 120.7356
1744.7344 | 121.9482 | -1.6983 | 120.1904 | 0.12185 | 0.50436 | 0.62901 | 0.52898 | 0.6314 | 0.6121 | 0.46835 | 120.325 | 120.351 | 120.4 | 120.3451 | 1.1745 | 1.2913 | 1.0608 | 1.1734 | 0.13558 | 0.51809 | 0.64274 | 0.54271 | 0.64513 | 0.62583 | 0.48208 | 120.3387 | 120.3647 | 120.4137 | 120.3588 | 1.1882 | 1.3051 | 1.0745 | 1.1872 | 119.1505 | 119.2642 | 119.2255 | 119.3392
1746.4219 | 121.8475 | -0.86517 | 120.9869 | 0.13101 | 0.52267 | 0.63358 | 0.53356 | 0.64513 | 0.63041 | 0.47751 | 120.6363 | 120.6715 | 120.7205 | 120.6519 | 0.84484 | 0.97546 | 0.68074 | 0.83921 | 0.14474 | 0.53641 | 0.64732 | 0.54729 | 0.65887 | 0.64414 | 0.49124 | 120.65 | 120.6853 | 120.7342 | 120.6656 | 0.85857 | 0.98919 | 0.69448 | 0.85294 | 119.7915 | 119.9556 | 119.8756 | 120.0397
1748.1562 | 121.8613 | -0.62256 | 121.2936 | 0.13559 | 0.52267 | 0.6519 | 0.55645 | 0.64971 | 0.63499 | 0.49582 | 121.0072 | 121.0424 | 121.0959 | 121.0273 | 0.47858 | 0.61379 | 0.31905 | 0.47296 | 0.14932 | 0.53641 | 0.66563 | 0.57018 | 0.66344 | 0.64872 | 0.50955 | 121.0209 | 121.0561 | 121.1096 | 121.0411 | 0.49232 | 0.62752 | 0.33278 | 0.48669 | 120.5286 | 120.6881 | 120.6173 | 120.7768
1749.8438 | 121.8704 | -0.68665 | 121.1929 | 0.13559 | 0.52725 | 0.6519 | 0.55187 | 0.65887 | 0.63499 | 0.5004 | 120.9156 | 120.9371 | 120.986 | 120.922 | 0.58388 | 0.71451 | 0.40604 | 0.57826 | 0.14932 | 0.54099 | 0.66563 | 0.56561 | 0.6726 | 0.64872 | 0.51413 | 120.9293 | 120.9508 | 120.9997 | 120.9358 | 0.59762 | 0.72824 | 0.41977 | 0.59199 | 120.3317 | 120.5096 | 120.4021 | 120.58
1751.5938 | 121.907 | -0.78278 | 121.051 | 0.13101 | 0.52725 | 0.65648 | 0.55187 | 0.65887 | 0.63041 | 0.49124 | 120.8286 | 120.8501 | 120.9173 | 120.8533 | 0.65713 | 0.78776 | 0.48845 | 0.66066 | 0.14474 | 0.54099 | 0.67021 | 0.56561 | 0.6726 | 0.64414 | 0.50498 | 120.8423 | 120.8638 | 120.9311 | 120.8671 | 0.67087 | 0.80149 | 0.50218 | 0.6744 | 120.1715 | 120.3402 | 120.2602 | 120.4289
1753.3281 | 121.843 | -0.95673 | 120.9549 | 0.12643 | 0.53183 | 0.66563 | 0.54272 | 0.66802 | 0.63499 | 0.49582 | 120.7462 | 120.7768 | 120.8303 | 120.7572 | 0.75327 | 0.87932 | 0.56628 | 0.73849 | 0.14016 | 0.54556 | 0.67937 | 0.55645 | 0.68176 | 0.64872 | 0.50955 | 120.7599 | 120.7906 | 120.8441 | 120.7709 | 0.76701 | 0.89305 | 0.58002 | 0.75223 | 119.9929 | 120.1799 | 120.0771 | 120.2641
1755.0625 | 121.8979 | -0.64545 | 121.2296 | 0.13101 | 0.54099 | 0.67021 | 0.57019 | 0.6726 | 0.6533 | 0.50498 | 121.0621 | 121.0836 | 121.1417 | 121.0731 | 0.44196 | 0.56343 | 0.27785 | 0.43633 | 0.14474 | 0.55472 | 0.68395 | 0.58392 | 0.68633 | 0.66704 | 0.51871 | 121.0758 | 121.0974 | 121.1554 | 121.0869 | 0.45569 | 0.57717 | 0.29158 | 0.45007 | 120.6202 | 120.7843 | 120.6997 | 120.8638
1756.8125 | 121.875 | -0.62714 | 121.2387 | 0.13559 | 0.55015 | 0.67021 | 0.57019 | 0.68176 | 0.6533 | 0.51871 | 120.9339 | 120.96 | 121.0089 | 120.9449 | 0.56099 | 0.70077 | 0.38773 | 0.5691 | 0.14932 | 0.56388 | 0.68395 | 0.58392 | 0.69549 | 0.66704 | 0.53244 | 120.9477 | 120.9737 | 121.0226 | 120.9587 | 0.57472 | 0.71451 | 0.40146 | 0.58283 | 120.3729 | 120.5462 | 120.4479 | 120.6212
1758.5469 | 121.9986 | -0.5127 | 121.3211 | 0.13101 | 0.55015 | 0.67937 | 0.58392 | 0.68634 | 0.6533 | 0.51871 | 121.0987 | 121.1294 | 121.1737 | 121.1098 | 0.39618 | 0.52223 | 0.25038 | 0.41802 | 0.14474 | 0.56388 | 0.6931 | 0.59766 | 0.70007 | 0.66704 | 0.53244 | 121.1125 | 121.1431 | 121.1874 | 121.1235 | 0.40991 | 0.53596 | 0.26411 | 0.43175 | 120.7026 | 120.8484 | 120.7775 | 120.9233
1760.2812 | 121.8338 | -0.56305 | 121.3486 | 0.13101 | 0.56846 | 0.68395 | 0.58392 | 0.69549 | 0.66704 | 0.53244 | 121.1399 | 121.1706 | 121.2149 | 121.1464 | 0.36413 | 0.49018 | 0.21833 | 0.37682 | 0.14474 | 0.5822 | 0.69768 | 0.59766 | 0.70922 | 0.68077 | 0.54618 | 121.1537 | 121.1843 | 121.2286 | 121.1601 | 0.37786 | 0.50392 | 0.23206 | 0.39055 | 120.7758 | 120.9216 | 120.8508 | 120.9966
1761.9688 | 121.962 | -0.53101 | 121.2936 | 0.13101 | 0.56846 | 0.68395 | 0.59308 | 0.69549 | 0.67619 | 0.53244 | 121.0987 | 121.1248 | 121.1691 | 121.1143 | 0.40075 | 0.52681 | 0.24122 | 0.40886 | 0.14474 | 0.5822 | 0.69768 | 0.60681 | 0.70922 | 0.68993 | 0.54618 | 121.1125 | 121.1386 | 121.1829 | 121.1281 | 0.41449 | 0.54054 | 0.25495 | 0.4226 | 120.698 | 120.8575 | 120.7684 | 120.9279
1763.7188 | 121.8475 | -0.77362 | 121.1563 | 0.13559 | 0.57762 | 0.6931 | 0.59766 | 0.70007 | 0.67162 | 0.5416 | 120.9705 | 121.0012 | 121.0547 | 120.9907 | 0.52437 | 0.66415 | 0.35568 | 0.52332 | 0.14932 | 0.59135 | 0.70684 | 0.61139 | 0.7138 | 0.68535 | 0.55534 | 120.9843 | 121.0149 | 121.0684 | 121.0044 | 0.5381 | 0.67788 | 0.36941 | 0.53705 | 120.4462 | 120.6149 | 120.5303 | 120.699
1765.4688 | 121.843 | -0.74158 | 121.1609 | 0.13559 | 0.57304 | 0.69768 | 0.61139 | 0.70465 | 0.68077 | 0.5416 | 120.9705 | 120.9966 | 121.0409 | 120.9816 | 0.52894 | 0.66873 | 0.35568 | 0.53705 | 0.14932 | 0.58677 | 0.71142 | 0.62513 | 0.71838 | 0.69451 | 0.55534 | 120.9843 | 121.0104 | 121.0547 | 120.9953 | 0.54268 | 0.68246 | 0.36941 | 0.55079 | 120.4416 | 120.6149 | 120.512 | 120.6853
1767.1406 | 121.962 | -0.70038 | 121.138 | 0.14017 | 0.58678 | 0.70684 | 0.60224 | 0.70922 | 0.68993 | 0.55076 | 120.9248 | 120.9508 | 121.0043 | 120.9358 | 0.57473 | 0.70993 | 0.39688 | 0.5691 | 0.1539 | 0.60051 | 0.72057 | 0.61597 | 0.72296 | 0.70366 | 0.56449 | 120.9385 | 120.9646 | 121.018 | 120.9495 | 0.58846 | 0.72366 | 0.41062 | 0.58283 | 120.35 | 120.5279 | 120.4296 | 120.6074
1768.875 | 121.9666 | -0.58136 | 121.2616 | 0.14017 | 0.59136 | 0.71142 | 0.61597 | 0.7138 | 0.69451 | 0.55991 | 121.0667 | 121.0928 | 121.1417 | 121.0731 | 0.4328 | 0.55885 | 0.26869 | 0.44549 | 0.1539 | 0.60509 | 0.72515 | 0.6297 | 0.72754 | 0.70824 | 0.57365 | 121.0804 | 121.1065 | 121.1554 | 121.0869 | 0.44654 | 0.57259 | 0.28242 | 0.45922 | 120.6339 | 120.798 | 120.7089 | 120.873
1770.625 | 121.8246 | -0.56305 | 121.3303 | 0.13559 | 0.60509 | 0.72058 | 0.61139 | 0.72296 | 0.70366 | 0.56907 | 121.0987 | 121.1248 | 121.1829 | 121.1052 | 0.40075 | 0.53596 | 0.2458 | 0.41802 | 0.14932 | 0.61883 | 0.73431 | 0.62513 | 0.73669 | 0.7174 | 0.5828 | 121.1125 | 121.1386 | 121.1966 | 121.1189 | 0.41449 | 0.5497 | 0.25953 | 0.43175 | 120.698 | 120.8529 | 120.7821 | 120.9371
1772.375 | 121.9849 | -0.5127 | 121.2799 | 0.14017 | 0.60967 | 0.72515 | 0.62055 | 0.72754 | 0.70824 | 0.56449 | 121.0987 | 121.1248 | 121.1829 | 121.1098 | 0.40533 | 0.53596 | 0.2458 | 0.41802 | 0.1539 | 0.6234 | 0.73889 | 0.63428 | 0.74127 | 0.72198 | 0.57822 | 121.1125 | 121.1386 | 121.1966 | 121.1235 | 0.41907 | 0.5497 | 0.25953 | 0.43175 | 120.6934 | 120.8529 | 120.7775 | 120.9371
1774.0625 | 121.9757 | -0.59509 | 121.225 | 0.14017 | 0.60967 | 0.72973 | 0.62055 | 0.73211 | 0.70824 | 0.56907 | 121.0621 | 121.0882 | 121.1417 | 121.0686 | 0.44654 | 0.58632 | 0.28242 | 0.45922 | 0.1539 | 0.6234 | 0.74347 | 0.63428 | 0.74585 | 0.72198 | 0.5828 | 121.0758 | 121.1019 | 121.1554 | 121.0823 | 0.46027 | 0.60006 | 0.29616 | 0.47296 | 120.6156 | 120.7797 | 120.6951 | 120.8592
1775.8125 | 121.9528 | -0.56763 | 121.2982 | 0.14017 | 0.62799 | 0.73889 | 0.62971 | 0.74127 | 0.70824 | 0.57823 | 121.0987 | 121.134 | 121.1829 | 121.1098 | 0.40075 | 0.53138 | 0.25038 | 0.4226 | 0.1539 | 0.64172 | 0.75262 | 0.64344 | 0.755 | 0.72198 | 0.59196 | 121.1125 | 121.1477 | 121.1966 | 121.1235 | 0.41449 | 0.54512 | 0.26411 | 0.43633 | 120.698 | 120.8484 | 120.7821 | 120.9325
1777.5625 | 121.843 | -0.69122 | 121.225 | 0.14474 | 0.62799 | 0.74347 | 0.63429 | 0.74585 | 0.72656 | 0.58738 | 120.9614 | 120.9966 | 121.0501 | 120.9678 | 0.5381 | 0.66873 | 0.36484 | 0.54163 | 0.15848 | 0.64172 | 0.7572 | 0.64802 | 0.75958 | 0.74029 | 0.60112 | 120.9751 | 121.0104 | 121.0638 | 120.9815 | 0.55183 | 0.68246 | 0.37857 | 0.55536 | 120.4233 | 120.5966 | 120.512 | 120.6853
1779.2188 | 121.8567 | -0.55389 | 121.3669 | 0.14932 | 0.63257 | 0.74805 | 0.64802 | 0.75043 | 0.73571 | 0.59196 | 121.1491 | 121.1844 | 121.2332 | 121.1601 | 0.36871 | 0.49018 | 0.22748 | 0.37682 | 0.16305 | 0.6463 | 0.76178 | 0.66175 | 0.76416 | 0.74945 | 0.60569 | 121.1628 | 121.1981 | 121.247 | 121.1739 | 0.38244 | 0.50392 | 0.24122 | 0.39055 | 120.7804 | 120.9216 | 120.8645 | 121.0057
1780.9062 | 121.8658 | -0.52185 | 121.3623 | 0.14932 | 0.63714 | 0.75263 | 0.64802 | 0.755 | 0.73114 | 0.59196 | 121.1262 | 121.1523 | 121.1966 | 121.1327 | 0.38702 | 0.52223 | 0.24122 | 0.40886 | 0.16305 | 0.65088 | 0.76636 | 0.66175 | 0.76874 | 0.74487 | 0.60569 | 121.1399 | 121.166 | 121.2103 | 121.1464 | 0.40075 | 0.53596 | 0.25495 | 0.4226 | 120.7392 | 120.885 | 120.8096 | 120.9554
1782.6562 | 121.9391 | -0.54016 | 121.3257 | 0.14017 | 0.64172 | 0.75263 | 0.6526 | 0.76416 | 0.74029 | 0.59654 | 121.0667 | 121.0974 | 121.1417 | 121.0823 | 0.43738 | 0.56801 | 0.27785 | 0.45465 | 0.1539 | 0.65546 | 0.76636 | 0.66633 | 0.77789 | 0.75402 | 0.61027 | 121.0804 | 121.1111 | 121.1554 | 121.096 | 0.45111 | 0.58174 | 0.29158 | 0.46838 | 120.6293 | 120.7888 | 120.7043 | 120.8638
1784.3906 | 121.9986 | -0.51727 | 121.3303 | 0.14474 | 0.64172 | 0.75721 | 0.65718 | 0.76416 | 0.74487 | 0.6057 | 121.0896 | 121.1157 | 121.1737 | 121.096 | 0.42365 | 0.55428 | 0.27785 | 0.43175 | 0.15848 | 0.65546 | 0.77094 | 0.67091 | 0.77789 | 0.7586 | 0.61943 | 121.1033 | 121.1294 | 121.1874 | 121.1098 | 0.43738 | 0.56801 | 0.29158 | 0.44549 | 120.6659 | 120.8117 | 120.7501 | 120.8959
1786.0781 | 121.9482 | -0.52643 | 121.2982 | 0.14932 | 0.65088 | 0.76178 | 0.66176 | 0.76416 | 0.74487 | 0.61027 | 121.1583 | 121.1889 | 121.2378 | 121.1739 | 0.35955 | 0.48103 | 0.21833 | 0.38139 | 0.16305 | 0.66461 | 0.77552 | 0.67549 | 0.77789 | 0.7586 | 0.62401 | 121.172 | 121.2027 | 121.2515 | 121.1876 | 0.37328 | 0.49476 | 0.23206 | 0.39513 | 120.7987 | 120.9399 | 120.8783 | 121.0195
1787.8438 | 121.9574 | -0.54474 | 121.3028 | 0.14474 | 0.65088 | 0.76636 | 0.66176 | 0.76874 | 0.74945 | 0.61027 | 121.0163 | 121.047 | 121.0959 | 121.0273 | 0.48774 | 0.62295 | 0.32821 | 0.49585 | 0.15848 | 0.66461 | 0.7801 | 0.67549 | 0.78247 | 0.76318 | 0.62401 | 121.0301 | 121.0607 | 121.1096 | 121.0411 | 0.50147 | 0.63668 | 0.34194 | 0.50958 | 120.5286 | 120.6881 | 120.6081 | 120.7677
1789.5312 | 121.9299 | -0.52643 | 121.3623 | 0.14017 | 0.65546 | 0.77552 | 0.67091 | 0.78247 | 0.75861 | 0.61943 | 121.1445 | 121.1798 | 121.2286 | 121.1601 | 0.36871 | 0.49934 | 0.22748 | 0.38597 | 0.1539 | 0.66919 | 0.78925 | 0.68465 | 0.7962 | 0.77234 | 0.63316 | 121.1583 | 121.1935 | 121.2424 | 121.1739 | 0.38244 | 0.51307 | 0.24122 | 0.39971 | 120.7758 | 120.917 | 120.8599 | 121.0012
1791.2656 | 121.9162 | -0.54474 | 121.3074 | 0.14017 | 0.6692 | 0.77552 | 0.67549 | 0.78247 | 0.76318 | 0.62859 | 121.1125 | 121.1431 | 121.1966 | 121.1189 | 0.40075 | 0.53596 | 0.24122 | 0.41344 | 0.1539 | 0.68293 | 0.78925 | 0.68923 | 0.7962 | 0.77692 | 0.64232 | 121.1262 | 121.1569 | 121.2103 | 121.1327 | 0.41449 | 0.5497 | 0.25495 | 0.42717 | 120.7117 | 120.8713 | 120.7958 | 120.9554
1793 | 121.962 | -0.5127 | 121.3669 | 0.14932 | 0.6692 | 0.78926 | 0.69381 | 0.78705 | 0.76318 | 0.62859 | 121.1399 | 121.166 | 121.2149 | 121.1464 | 0.38702 | 0.51307 | 0.23664 | 0.39971 | 0.16305 | 0.68293 | 0.80299 | 0.70754 | 0.80078 | 0.77692 | 0.64232 | 121.1537 | 121.1798 | 121.2286 | 121.1601 | 0.40075 | 0.52681 | 0.25037 | 0.41344 | 120.7529 | 120.9033 | 120.8279 | 120.9783
1794.75 | 121.962 | -0.49896 | 121.3531 | 0.14474 | 0.67378 | 0.79383 | 0.68465 | 0.80078 | 0.76776 | 0.63774 | 121.1674 | 121.1935 | 121.2515 | 121.1693 | 0.35497 | 0.48561 | 0.21833 | 0.37682 | 0.15848 | 0.68751 | 0.80757 | 0.69838 | 0.81452 | 0.7815 | 0.65148 | 121.1812 | 121.2072 | 121.2653 | 121.183 | 0.36871 | 0.49934 | 0.23206 | 0.39055 | 120.8124 | 120.9491 | 120.8966 | 121.0332
1796.4375 | 121.843 | -0.58594 | 121.3303 | 0.14017 | 0.68751 | 0.80299 | 0.69381 | 0.79621 | 0.77692 | 0.6469 | 121.1308 | 121.1615 | 121.2103 | 121.1327 | 0.3916 | 0.52681 | 0.23664 | 0.40429 | 0.1539 | 0.70124 | 0.81673 | 0.70754 | 0.80994 | 0.79065 | 0.66063 | 121.1445 | 121.1752 | 121.2241 | 121.1464 | 0.40533 | 0.54054 | 0.25037 | 0.41802 | 120.7392 | 120.8942 | 120.8187 | 120.9737
1798.1875 | 121.8796 | -0.53101 | 121.4218 | 0.1539 | 0.69209 | 0.79841 | 0.70296 | 0.80994 | 0.77692 | 0.65148 | 121.2132 | 121.2393 | 121.2927 | 121.2151 | 0.3275 | 0.43525 | 0.18628 | 0.33561 | 0.16763 | 0.70582 | 0.81215 | 0.7167 | 0.82367 | 0.79065 | 0.66521 | 121.2269 | 121.253 | 121.3065 | 121.2288 | 0.34124 | 0.44898 | 0.20001 | 0.34935 | 120.8857 | 121.0269 | 120.9652 | 121.1065
1799.9219 | 121.9254 | -0.46234 | 121.4081 | 0.14017 | 0.68293 | 0.80757 | 0.70296 | 0.80994 | 0.79065 | 0.65148 | 121.2086 | 121.2439 | 121.2973 | 121.2197 | 0.31835 | 0.43067 | 0.18628 | 0.34019 | 0.1539 | 0.69666 | 0.8213 | 0.7167 | 0.82367 | 0.80439 | 0.66521 | 121.2224 | 121.2576 | 121.3111 | 121.2334 | 0.33208 | 0.4444 | 0.20001 | 0.35392 | 120.8903 | 121.0223 | 120.979 | 121.111
1801.5938 | 121.8979 | -0.49896 | 121.4264 | 0.14932 | 0.70125 | 0.81673 | 0.71212 | 0.8191 | 0.80439 | 0.65606 | 121.2086 | 121.2393 | 121.2882 | 121.2151 | 0.33208 | 0.44898 | 0.1817 | 0.34477 | 0.16305 | 0.71498 | 0.83046 | 0.72585 | 0.83283 | 0.81812 | 0.66979 | 121.2224 | 121.253 | 121.3019 | 121.2288 | 0.34581 | 0.46271 | 0.19543 | 0.3585 | 120.8765 | 121.0269 | 120.9561 | 121.1065
1803.3438 | 121.9208 | -0.48523 | 121.3715 | 0.14474 | 0.70125 | 0.81215 | 0.7167 | 0.8191 | 0.79065 | 0.65606 | 121.1903 | 121.2256 | 121.279 | 121.1968 | 0.33666 | 0.44898 | 0.19543 | 0.34935 | 0.15848 | 0.71498 | 0.82588 | 0.73043 | 0.83283 | 0.80439 | 0.66979 | 121.204 | 121.2393 | 121.2927 | 121.2105 | 0.35039 | 0.46271 | 0.20917 | 0.36308 | 120.8537 | 120.9949 | 120.9423 | 121.0836
1805.0312 | 121.9803 | -0.40283 | 121.4172 | 0.14932 | 0.70583 | 0.82131 | 0.72586 | 0.83283 | 0.80439 | 0.66979 | 121.2453 | 121.2759 | 121.334 | 121.2609 | 0.29088 | 0.40778 | 0.15881 | 0.30357 | 0.16305 | 0.71956 | 0.83504 | 0.73959 | 0.84656 | 0.81812 | 0.68352 | 121.259 | 121.2897 | 121.3477 | 121.2746 | 0.30461 | 0.42151 | 0.17254 | 0.3173 | 120.9544 | 121.0864 | 121.0431 | 121.1751
1806.7812 | 121.9025 | -0.44403 | 121.4401 | 0.14474 | 0.7104 | 0.83046 | 0.73501 | 0.83283 | 0.80897 | 0.67437 | 121.2544 | 121.2851 | 121.3385 | 121.2563 | 0.29546 | 0.40778 | 0.15881 | 0.31272 | 0.15848 | 0.72414 | 0.8442 | 0.74875 | 0.84656 | 0.8227 | 0.6881 | 121.2681 | 121.2988 | 121.3523 | 121.27 | 0.30919 | 0.42151 | 0.17254 | 0.32645 | 120.959 | 121.0956 | 121.0431 | 121.1797
1808.4531 | 121.8796 | -0.45319 | 121.4584 | 0.14932 | 0.71956 | 0.83504 | 0.73043 | 0.83741 | 0.81812 | 0.68353 | 121.2498 | 121.2805 | 121.3431 | 121.2563 | 0.29546 | 0.39862 | 0.15423 | 0.30357 | 0.16305 | 0.7333 | 0.84877 | 0.74417 | 0.85114 | 0.83186 | 0.69726 | 121.2636 | 121.2942 | 121.3568 | 121.27 | 0.30919 | 0.41235 | 0.16796 | 0.3173 | 120.9544 | 121.0956 | 121.0476 | 121.1889
1810.1875 | 121.8842 | -0.46234 | 121.4401 | 0.14932 | 0.71956 | 0.8442 | 0.73959 | 0.84656 | 0.8227 | 0.68353 | 121.2361 | 121.2668 | 121.3202 | 121.2426 | 0.30461 | 0.40778 | 0.16339 | 0.3173 | 0.16305 | 0.7333 | 0.85793 | 0.75333 | 0.8603 | 0.83644 | 0.69726 | 121.2498 | 121.2805 | 121.3339 | 121.2563 | 0.31835 | 0.42151 | 0.17712 | 0.33103 | 120.9315 | 121.0727 | 121.0156 | 121.1568
1811.875 | 121.9803 | -1.4328 | 120.401 | 0.1539 | 0.70583 | 0.82588 | 0.72586 | 0.83741 | 0.80439 | 0.66979 | 120.1693 | 120.1907 | 120.2397 | 120.1711 | 1.353 | 1.4836 | 1.1844 | 1.352 | 0.16763 | 0.71956 | 0.83962 | 0.73959 | 0.85114 | 0.81812 | 0.68352 | 120.183 | 120.2045 | 120.2535 | 120.1848 | 1.3667 | 1.4974 | 1.1981 | 1.3657 | 118.8163 | 118.9849 | 118.8867 | 119.0554
1813.6094 | 121.9711 | -1.9821 | 119.8837 | 0.14474 | 0.71956 | 0.83046 | 0.73501 | 0.82825 | 0.80897 | 0.66979 | 120.0457 | 120.0717 | 120.1253 | 120.0474 | 1.4766 | 1.5935 | 1.2897 | 1.4802 | 0.15848 | 0.7333 | 0.8442 | 0.74875 | 0.84198 | 0.8227 | 0.68352 | 120.0594 | 120.0854 | 120.139 | 120.0612 | 1.4904 | 1.6072 | 1.3034 | 1.4939 | 118.5691 | 118.756 | 118.6487 | 118.8356
1815.2812 | 121.9345 | -1.7395 | 120.0943 | 0.14932 | 0.71498 | 0.83046 | 0.73501 | 0.83741 | 0.8227 | 0.66979 | 119.9816 | 120.003 | 120.0566 | 119.9787 | 1.5453 | 1.6851 | 1.3583 | 1.5351 | 0.16305 | 0.72872 | 0.8442 | 0.74875 | 0.85114 | 0.83644 | 0.68352 | 119.9953 | 120.0168 | 120.0703 | 119.9925 | 1.559 | 1.6988 | 1.3721 | 1.5488 | 118.4363 | 118.6232 | 118.5113 | 118.6983
1817.0312 | 121.9391 | -1.8539 | 119.9982 | 0.15848 | 0.72414 | 0.83504 | 0.74417 | 0.84656 | 0.81812 | 0.67895 | 119.8305 | 119.8519 | 119.9101 | 119.8231 | 1.6964 | 1.827 | 1.514 | 1.6862 | 0.17221 | 0.73787 | 0.84877 | 0.7579 | 0.8603 | 0.83186 | 0.69268 | 119.8442 | 119.8657 | 119.9238 | 119.8368 | 1.7101 | 1.8407 | 1.5277 | 1.6999 | 118.1341 | 118.3165 | 118.2137 | 118.3961
1818.7812 | 121.9528 | -2.0325 | 119.8151 | 0.14932 | 0.72414 | 0.83962 | 0.73959 | 0.84656 | 0.82728 | 0.68353 | 119.7252 | 119.7466 | 119.8048 | 119.7269 | 1.7879 | 1.9231 | 1.601 | 1.7869 | 0.16305 | 0.73787 | 0.85335 | 0.75333 | 0.8603 | 0.84101 | 0.69726 | 119.7389 | 119.7603 | 119.8185 | 119.7406 | 1.8017 | 1.9368 | 1.6147 | 1.8006 | 117.9373 | 118.1242 | 118.0169 | 118.2038
1820.4688 | 121.9116 | -1.918 | 119.9844 | 0.1539 | 0.72872 | 0.8442 | 0.75333 | 0.8603 | 0.82728 | 0.69726 | 119.7801 | 119.797 | 119.8552 | 119.7818 | 1.7513 | 1.8865 | 1.5644 | 1.7365 | 0.16763 | 0.74245 | 0.85793 | 0.76706 | 0.87403 | 0.84101 | 0.71099 | 119.7939 | 119.8107 | 119.8689 | 119.7956 | 1.765 | 1.9002 | 1.5781 | 1.7503 | 118.0288 | 118.2158 | 118.1038 | 118.2908
1822.2031 | 121.9757 | -1.6891 | 120.1126 | 0.14932 | 0.7333 | 0.85336 | 0.75791 | 0.86487 | 0.83644 | 0.70184 | 119.9404 | 119.9664 | 120.0154 | 119.9467 | 1.5819 | 1.7171 | 1.395 | 1.5717 | 0.16305 | 0.74703 | 0.86709 | 0.77164 | 0.87861 | 0.85017 | 0.71557 | 119.9541 | 119.9801 | 120.0291 | 119.9604 | 1.5957 | 1.7308 | 1.4087 | 1.5855 | 118.3585 | 118.5454 | 118.4335 | 118.6204
1823.9375 | 121.843 | -1.7807 | 120.1584 | 0.15848 | 0.74246 | 0.85794 | 0.77164 | 0.87403 | 0.84559 | 0.70642 | 119.9404 | 119.9572 | 120.02 | 119.9375 | 1.5865 | 1.7217 | 1.3996 | 1.5809 | 0.17221 | 0.75619 | 0.87167 | 0.78537 | 0.88776 | 0.85933 | 0.72015 | 119.9541 | 119.971 | 120.0337 | 119.9513 | 1.6002 | 1.7354 | 1.4133 | 1.5946 | 118.3539 | 118.5408 | 118.4335 | 118.6204
1825.6875 | 121.8475 | -1.8631 | 120.0668 | 0.1539 | 0.74246 | 0.86709 | 0.75791 | 0.86487 | 0.84559 | 0.70642 | 119.8534 | 119.884 | 119.9467 | 119.8597 | 1.6689 | 1.7949 | 1.4774 | 1.6633 | 0.16763 | 0.75619 | 0.88082 | 0.77164 | 0.87861 | 0.85933 | 0.72015 | 119.8671 | 119.8977 | 119.9605 | 119.8734 | 1.6826 | 1.8087 | 1.4911 | 1.677 | 118.1845 | 118.376 | 118.2778 | 118.4693
1827.375 | 121.875 | -1.8173 | 120.1126 | 0.14474 | 0.74704 | 0.86709 | 0.77622 | 0.86945 | 0.85475 | 0.71557 | 119.8671 | 119.8931 | 119.9605 | 119.8688 | 1.6552 | 1.7858 | 1.4774 | 1.6495 | 0.15848 | 0.76077 | 0.88082 | 0.78995 | 0.88319 | 0.86848 | 0.7293 | 119.8809 | 119.9069 | 119.9742 | 119.8826 | 1.6689 | 1.7995 | 1.4911 | 1.6633 | 118.212 | 118.3897 | 118.3053 | 118.4831
1829.1094 | 121.9711 | -1.7487 | 120.0851 | 0.1539 | 0.76077 | 0.87167 | 0.7808 | 0.87861 | 0.86391 | 0.72473 | 119.8809 | 119.9114 | 119.965 | 119.8917 | 1.646 | 1.7812 | 1.4682 | 1.6404 | 0.16763 | 0.7745 | 0.8854 | 0.79453 | 0.89234 | 0.87764 | 0.73846 | 119.8946 | 119.9252 | 119.9788 | 119.9055 | 1.6598 | 1.7949 | 1.482 | 1.6541 | 118.2348 | 118.4126 | 118.319 | 118.4968
1830.8438 | 121.994 | -1.68 | 120.1401 | 0.15848 | 0.76535 | 0.88083 | 0.78538 | 0.89234 | 0.86391 | 0.72015 | 119.9038 | 119.9389 | 119.9879 | 119.9192 | 1.6094 | 1.7492 | 1.4316 | 1.6129 | 0.17221 | 0.77908 | 0.89456 | 0.79911 | 0.90608 | 0.87764 | 0.73388 | 119.9175 | 119.9526 | 120.0017 | 119.933 | 1.6231 | 1.7629 | 1.4453 | 1.6267 | 118.2944 | 118.4722 | 118.3785 | 118.5563
1832.5312 | 121.907 | -1.6113 | 120.282 | 0.16306 | 0.77451 | 0.89456 | 0.79453 | 0.9015 | 0.88222 | 0.73846 | 120.064 | 120.0809 | 120.139 | 120.0657 | 1.4675 | 1.6072 | 1.2897 | 1.4573 | 0.17679 | 0.78824 | 0.9083 | 0.80827 | 0.91523 | 0.89595 | 0.7522 | 120.0777 | 120.0946 | 120.1528 | 120.0795 | 1.4812 | 1.621 | 1.3034 | 1.471 | 118.5965 | 118.7743 | 118.6716 | 118.8493
1834.2812 | 121.8384 | -1.8448 | 120.108 | 0.1539 | 0.77451 | 0.88999 | 0.80369 | 0.90608 | 0.88222 | 0.74304 | 119.8717 | 119.8885 | 119.9559 | 119.878 | 1.646 | 1.7949 | 1.4682 | 1.6495 | 0.16763 | 0.78824 | 0.90372 | 0.81742 | 0.91981 | 0.89595 | 0.75677 | 119.8854 | 119.9023 | 119.9696 | 119.8917 | 1.6598 | 1.8087 | 1.482 | 1.6633 | 118.2257 | 118.4035 | 118.3099 | 118.4877
1835.9688 | 121.9482 | -1.7258 | 120.1126 | 0.14932 | 0.77909 | 0.90372 | 0.80369 | 0.91065 | 0.8868 | 0.7522 | 119.9038 | 119.9252 | 119.9879 | 119.9055 | 1.614 | 1.7629 | 1.4408 | 1.6129 | 0.16305 | 0.79282 | 0.91745 | 0.81742 | 0.92439 | 0.90053 | 0.76593 | 119.9175 | 119.9389 | 120.0017 | 119.9192 | 1.6277 | 1.7766 | 1.4545 | 1.6267 | 118.2898 | 118.463 | 118.374 | 118.5472
1837.7344 | 121.9254 | -1.7441 | 120.1492 | 0.1539 | 0.79282 | 0.91746 | 0.81743 | 0.92439 | 0.89138 | 0.76135 | 119.9679 | 119.9801 | 120.0475 | 119.9604 | 1.5636 | 1.6942 | 1.3812 | 1.558 | 0.16763 | 0.80656 | 0.93119 | 0.83116 | 0.93812 | 0.90511 | 0.77509 | 119.9816 | 119.9939 | 120.0612 | 119.9742 | 1.5773 | 1.7079 | 1.395 | 1.5717 | 118.4042 | 118.5866 | 118.4838 | 118.6662
1839.4062 | 121.9391 | -1.6846 | 120.2133 | 0.1539 | 0.80198 | 0.93119 | 0.822 | 0.92897 | 0.90511 | 0.77051 | 119.9999 | 120.0168 | 120.0795 | 119.9971 | 1.527 | 1.6622 | 1.3492 | 1.5305 | 0.16763 | 0.81571 | 0.94493 | 0.83574 | 0.9427 | 0.91885 | 0.78424 | 120.0136 | 120.0305 | 120.0932 | 120.0108 | 1.5407 | 1.6759 | 1.3629 | 1.5442 | 118.4729 | 118.6507 | 118.5525 | 118.7303
1841.1406 | 121.8704 | -1.6846 | 120.2316 | 0.15848 | 0.81114 | 0.92661 | 0.83574 | 0.93812 | 0.90511 | 0.78424 | 120.0228 | 120.0488 | 120.1115 | 120.0291 | 1.4949 | 1.6347 | 1.3171 | 1.503 | 0.17221 | 0.82487 | 0.94035 | 0.84947 | 0.95186 | 0.91885 | 0.79798 | 120.0365 | 120.0625 | 120.1253 | 120.0428 | 1.5087 | 1.6484 | 1.3309 | 1.5168 | 118.5279 | 118.7057 | 118.6166 | 118.7944
1842.8906 | 121.962 | -1.5976 | 120.2362 | 0.1539 | 0.81114 | 0.93119 | 0.84032 | 0.93812 | 0.91885 | 0.77967 | 120.064 | 120.0946 | 120.1436 | 120.0749 | 1.4583 | 1.5981 | 1.2805 | 1.4527 | 0.16763 | 0.82487 | 0.94493 | 0.85405 | 0.95186 | 0.93258 | 0.7934 | 120.0777 | 120.1083 | 120.1573 | 120.0886 | 1.472 | 1.6118 | 1.2942 | 1.4664 | 118.6057 | 118.7835 | 118.6853 | 118.8631
1844.5625 | 121.9986 | -1.5381 | 120.3003 | 0.15848 | 0.82946 | 0.93577 | 0.8449 | 0.95643 | 0.92343 | 0.7934 | 120.1556 | 120.1816 | 120.2306 | 120.1619 | 1.3805 | 1.5065 | 1.1889 | 1.3749 | 0.17221 | 0.84319 | 0.9495 | 0.85863 | 0.97017 | 0.93716 | 0.80713 | 120.1693 | 120.1953 | 120.2443 | 120.1756 | 1.3942 | 1.5202 | 1.2027 | 1.3886 | 118.7751 | 118.9666 | 118.8501 | 119.0416
1846.2969 | 121.9345 | -1.5244 | 120.3552 | 0.15848 | 0.83403 | 0.96324 | 0.84948 | 0.96101 | 0.93258 | 0.7934 | 120.1693 | 120.1862 | 120.2443 | 120.1711 | 1.353 | 1.4882 | 1.1798 | 1.3611 | 0.17221 | 0.84777 | 0.97698 | 0.86321 | 0.97474 | 0.94632 | 0.80713 | 120.183 | 120.1999 | 120.2581 | 120.1848 | 1.3667 | 1.5019 | 1.1935 | 1.3749 | 118.8163 | 118.9895 | 118.8913 | 119.0645
1847.9844 | 121.8384 | -1.4511 | 120.5063 | 0.15848 | 0.84319 | 0.9724 | 0.86779 | 0.97475 | 0.95548 | 0.81629 | 120.2471 | 120.2686 | 120.3313 | 120.2535 | 1.2889 | 1.4195 | 1.102 | 1.2787 | 0.17221 | 0.85692 | 0.98613 | 0.88152 | 0.98848 | 0.96921 | 0.83003 | 120.2609 | 120.2823 | 120.345 | 120.2672 | 1.3027 | 1.4333 | 1.1157 | 1.2925 | 118.9582 | 119.1452 | 119.0424 | 119.2293
1849.7188 | 121.8796 | -1.5701 | 120.3827 | 0.16306 | 0.85235 | 0.96782 | 0.87237 | 0.97932 | 0.9509 | 0.81629 | 120.1281 | 120.1587 | 120.2168 | 120.1344 | 1.408 | 1.5386 | 1.221 | 1.3932 | 0.17679 | 0.86608 | 0.98155 | 0.8861 | 0.99306 | 0.96463 | 0.83003 | 120.1418 | 120.1724 | 120.2306 | 120.1482 | 1.4217 | 1.5523 | 1.2347 | 1.4069 | 118.7201 | 118.9071 | 118.8089 | 118.9959
1851.4531 | 121.8567 | -1.6434 | 120.2637 | 0.16764 | 0.85235 | 0.97698 | 0.8861 | 0.9839 | 0.95548 | 0.82545 | 120.1006 | 120.1175 | 120.1802 | 120.1024 | 1.4354 | 1.5569 | 1.2485 | 1.4344 | 0.18137 | 0.86608 | 0.99071 | 0.89984 | 0.99764 | 0.96921 | 0.83918 | 120.1144 | 120.1312 | 120.194 | 120.1161 | 1.4492 | 1.5706 | 1.2622 | 1.4481 | 118.6652 | 118.8522 | 118.7448 | 118.9318
1853.1875 | 121.8567 | -1.5701 | 120.3415 | 0.15848 | 0.86608 | 0.99071 | 0.87695 | 0.99764 | 0.97379 | 0.83003 | 120.1373 | 120.1633 | 120.2168 | 120.139 | 1.4034 | 1.5294 | 1.2118 | 1.3977 | 0.17221 | 0.87982 | 1.0044 | 0.89068 | 1.0114 | 0.98752 | 0.84376 | 120.151 | 120.177 | 120.2306 | 120.1527 | 1.4171 | 1.5431 | 1.2256 | 1.4115 | 118.7339 | 118.9254 | 118.8135 | 119.005
1854.8594 | 121.8384 | -1.8814 | 120.0302 | 0.16764 | 0.87524 | 0.98614 | 0.8861 | 1.0022 | 0.97837 | 0.83461 | 119.8763 | 119.8977 | 119.9605 | 119.8643 | 1.6598 | 1.7995 | 1.4682 | 1.6587 | 0.18137 | 0.88898 | 0.99987 | 0.89984 | 1.0159 | 0.9921 | 0.84834 | 119.89 | 119.9114 | 119.9742 | 119.878 | 1.6735 | 1.8132 | 1.482 | 1.6724 | 118.2165 | 118.4081 | 118.3007 | 118.4922
1856.5938 | 121.8475 | -1.7807 | 120.1492 | 0.18137 | 0.87982 | 0.99529 | 0.89984 | 1.0114 | 0.97837 | 0.83918 | 119.8488 | 119.8794 | 119.9376 | 119.8643 | 1.6781 | 1.8041 | 1.4911 | 1.6724 | 0.1951 | 0.89355 | 1.009 | 0.91357 | 1.0251 | 0.9921 | 0.85292 | 119.8625 | 119.8931 | 119.9513 | 119.878 | 1.6918 | 1.8178 | 1.5049 | 1.6862 | 118.1707 | 118.3577 | 118.2595 | 118.4465
1858.2812 | 121.9666 | -1.5793 | 120.2957 | 0.17221 | 0.8844 | 1.0136 | 0.91358 | 1.0159 | 0.9921 | 0.85292 | 120.0823 | 120.0992 | 120.1619 | 120.0795 | 1.4537 | 1.5889 | 1.2714 | 1.4573 | 0.18595 | 0.89813 | 1.0273 | 0.92731 | 1.0297 | 1.0058 | 0.86665 | 120.0961 | 120.1129 | 120.1756 | 120.0932 | 1.4675 | 1.6027 | 1.2851 | 1.471 | 118.6286 | 118.811 | 118.7082 | 118.8906
1860.0156 | 121.9711 | -1.4648 | 120.4102 | 0.17221 | 0.89356 | 1.0182 | 0.91815 | 1.0251 | 1.0058 | 0.86665 | 120.238 | 120.2594 | 120.3221 | 120.2352 | 1.2935 | 1.4287 | 1.1203 | 1.297 | 0.18595 | 0.90729 | 1.0319 | 0.93189 | 1.0388 | 1.0196 | 0.88038 | 120.2517 | 120.2732 | 120.3359 | 120.2489 | 1.3072 | 1.4424 | 1.134 | 1.3108 | 118.9445 | 119.1177 | 119.0287 | 119.2019
1861.75 | 121.9849 | -1.4877 | 120.3644 | 0.17679 | 0.90272 | 1.0273 | 0.92731 | 1.0251 | 1.0104 | 0.87123 | 120.1189 | 120.1358 | 120.2031 | 120.1115 | 1.4217 | 1.5523 | 1.2439 | 1.4252 | 0.19052 | 0.91645 | 1.0411 | 0.94104 | 1.0388 | 1.0241 | 0.88496 | 120.1327 | 120.1495 | 120.2168 | 120.1253 | 1.4354 | 1.566 | 1.2576 | 1.439 | 118.6973 | 118.8751 | 118.7814 | 118.9592
1863.5 | 121.8613 | -1.3229 | 120.6116 | 0.17679 | 0.92561 | 1.0457 | 0.94105 | 1.048 | 1.0196 | 0.88497 | 120.3341 | 120.3464 | 120.4137 | 120.3313 | 1.2019 | 1.3325 | 1.0241 | 1.2009 | 0.19052 | 0.93934 | 1.0594 | 0.95478 | 1.0617 | 1.0333 | 0.8987 | 120.3479 | 120.3602 | 120.4274 | 120.3451 | 1.2157 | 1.3463 | 1.0379 | 1.2146 | 119.1322 | 119.31 | 119.2118 | 119.3896
1865.1875 | 121.994 | -1.799 | 120.0485 | 0.17221 | 0.92103 | 1.0411 | 0.94105 | 1.0434 | 1.0242 | 0.88954 | 119.8305 | 119.8428 | 119.9055 | 119.8231 | 1.7238 | 1.8499 | 1.5369 | 1.7045 | 0.18595 | 0.93476 | 1.0548 | 0.95478 | 1.0571 | 1.0379 | 0.90328 | 119.8442 | 119.8565 | 119.9193 | 119.8368 | 1.7376 | 1.8636 | 1.5506 | 1.7182 | 118.1067 | 118.2936 | 118.1817 | 118.3686
1866.9375 | 121.9116 | -1.8723 | 120.0073 | 0.17679 | 0.93019 | 1.0411 | 0.95478 | 1.0572 | 1.0287 | 0.90328 | 119.8442 | 119.8519 | 119.9193 | 119.8368 | 1.701 | 1.8316 | 1.5232 | 1.6953 | 0.19052 | 0.94392 | 1.0548 | 0.96851 | 1.0709 | 1.0425 | 0.91701 | 119.858 | 119.8657 | 119.933 | 119.8505 | 1.7147 | 1.8453 | 1.5369 | 1.7091 | 118.1433 | 118.3211 | 118.2183 | 118.3961
1868.625 | 121.8658 | -1.7761 | 120.163 | 0.17221 | 0.9485 | 1.064 | 0.96394 | 1.0755 | 1.0425 | 0.90328 | 119.9495 | 119.971 | 120.0383 | 119.9513 | 1.5819 | 1.7263 | 1.4041 | 1.5855 | 0.18595 | 0.96224 | 1.0777 | 0.97767 | 1.0892 | 1.0562 | 0.91701 | 119.9633 | 119.9847 | 120.052 | 119.965 | 1.5957 | 1.74 | 1.4179 | 1.5992 | 118.3676 | 118.5454 | 118.4564 | 118.6342
1870.3594 | 121.8521 | -1.6479 | 120.2682 | 0.17221 | 0.95308 | 1.0686 | 0.9731 | 1.0755 | 1.0562 | 0.91701 | 120.0045 | 120.0213 | 120.0932 | 120.0062 | 1.5316 | 1.6622 | 1.3538 | 1.5214 | 0.18595 | 0.96682 | 1.0823 | 0.98683 | 1.0892 | 1.0699 | 0.93075 | 120.0182 | 120.0351 | 120.107 | 120.02 | 1.5453 | 1.6759 | 1.3675 | 1.5351 | 118.4729 | 118.6507 | 118.5617 | 118.7395
1872.0312 | 121.9803 | -1.8677 | 119.989 | 0.17679 | 0.95766 | 1.0777 | 0.97767 | 1.0892 | 1.0516 | 0.92617 | 119.8854 | 119.9023 | 119.9696 | 119.8872 | 1.6414 | 1.7766 | 1.4636 | 1.6358 | 0.19052 | 0.97139 | 1.0914 | 0.99141 | 1.1029 | 1.0654 | 0.9399 | 119.8992 | 119.916 | 119.9834 | 119.9009 | 1.6552 | 1.7904 | 1.4774 | 1.6495 | 118.244 | 118.4218 | 118.3282 | 118.506
1873.7656 | 121.9345 | -1.8585 | 120.0256 | 0.17679 | 0.9714 | 1.0823 | 0.98225 | 1.0984 | 1.0608 | 0.93075 | 119.8351 | 119.8519 | 119.9193 | 119.8322 | 1.701 | 1.8316 | 1.514 | 1.7091 | 0.19052 | 0.98513 | 1.096 | 0.99599 | 1.1121 | 1.0745 | 0.94448 | 119.8488 | 119.8657 | 119.933 | 119.846 | 1.7147 | 1.8453 | 1.5277 | 1.7228 | 118.1341 | 118.3211 | 118.2183 | 118.4053
1875.5 | 121.9437 | -1.886 | 119.9661 | 0.18137 | 0.9714 | 1.0914 | 1.0051 | 1.1029 | 1.0745 | 0.93075 | 119.803 | 119.8153 | 119.8781 | 119.7864 | 1.7376 | 1.8773 | 1.5598 | 1.7365 | 0.1951 | 0.98513 | 1.1052 | 1.0189 | 1.1167 | 1.0882 | 0.94448 | 119.8168 | 119.829 | 119.8918 | 119.8002 | 1.7513 | 1.8911 | 1.5735 | 1.7503 | 118.0654 | 118.2432 | 118.1405 | 118.3183
1877.1719 | 121.9986 | -1.8082 | 119.9982 | 0.17679 | 0.98971 | 1.1098 | 1.0051 | 1.1029 | 1.0837 | 0.94448 | 119.858 | 119.8657 | 119.9376 | 119.8505 | 1.6781 | 1.8178 | 1.4957 | 1.6816 | 0.19052 | 1.0034 | 1.1235 | 1.0189 | 1.1167 | 1.0974 | 0.95821 | 119.8717 | 119.8794 | 119.9513 | 119.8643 | 1.6918 | 1.8316 | 1.5094 | 1.6953 | 118.1799 | 118.3623 | 118.2595 | 118.4419
1878.9219 | 121.9894 | -1.8448 | 120.0119 | 0.18595 | 1.0034 | 1.1143 | 1.0143 | 1.1258 | 1.0974 | 0.95822 | 119.8946 | 119.9023 | 119.9696 | 119.8917 | 1.6506 | 1.7766 | 1.4591 | 1.645 | 0.19968 | 1.0172 | 1.1281 | 1.028 | 1.1396 | 1.1111 | 0.97195 | 119.9083 | 119.916 | 119.9834 | 119.9055 | 1.6643 | 1.7904 | 1.4728 | 1.6587 | 118.244 | 118.4355 | 118.319 | 118.5106
1880.5938 | 121.8384 | -1.9272 | 119.9936 | 0.17679 | 1.008 | 1.1235 | 1.0235 | 1.135 | 1.0974 | 0.96737 | 119.8122 | 119.8336 | 119.8964 | 119.8047 | 1.7147 | 1.8636 | 1.5415 | 1.7136 | 0.19052 | 1.0218 | 1.1372 | 1.0372 | 1.1487 | 1.1111 | 0.98111 | 119.8259 | 119.8473 | 119.9101 | 119.8185 | 1.7284 | 1.8773 | 1.5552 | 1.7274 | 118.0975 | 118.2707 | 118.1817 | 118.3549
1882.3281 | 121.907 | -1.7899 | 120.1309 | 0.18595 | 1.0218 | 1.1372 | 1.0326 | 1.1441 | 1.1157 | 0.98111 | 119.9266 | 119.9481 | 120.0154 | 119.9238 | 1.614 | 1.7492 | 1.4224 | 1.6083 | 0.19968 | 1.0355 | 1.151 | 1.0463 | 1.1579 | 1.1295 | 0.99484 | 119.9404 | 119.9618 | 120.0291 | 119.9375 | 1.6277 | 1.7629 | 1.4362 | 1.6221 | 118.3127 | 118.5042 | 118.4014 | 118.593
1884.0625 | 121.8338 | -1.8585 | 120.0851 | 0.18595 | 1.0263 | 1.1418 | 1.0464 | 1.1579 | 1.1295 | 0.98568 | 119.9038 | 119.9206 | 119.9879 | 119.8963 | 1.6323 | 1.7766 | 1.4499 | 1.6312 | 0.19968 | 1.0401 | 1.1555 | 1.0601 | 1.1716 | 1.1432 | 0.99942 | 119.9175 | 119.9343 | 120.0017 | 119.9101 | 1.646 | 1.7904 | 1.4636 | 1.645 | 118.2715 | 118.4538 | 118.3557 | 118.538
1885.8125 | 121.9894 | -1.7395 | 120.1218 | 0.18595 | 1.0355 | 1.151 | 1.0509 | 1.1533 | 1.1386 | 0.99484 | 119.9129 | 119.9343 | 119.9971 | 119.9101 | 1.6185 | 1.7583 | 1.4408 | 1.6221 | 0.19968 | 1.0492 | 1.1647 | 1.0647 | 1.167 | 1.1523 | 1.0086 | 119.9266 | 119.9481 | 120.0108 | 119.9238 | 1.6323 | 1.772 | 1.4545 | 1.6358 | 118.2944 | 118.4722 | 118.3785 | 118.5563
1887.5625 | 121.9666 | -1.799 | 120.0668 | 0.19511 | 1.0355 | 1.1647 | 1.0692 | 1.167 | 1.1478 | 1.0132 | 119.9312 | 119.9389 | 120.0062 | 119.9238 | 1.6094 | 1.7446 | 1.427 | 1.6083 | 0.20884 | 1.0492 | 1.1784 | 1.083 | 1.1808 | 1.1615 | 1.0269 | 119.945 | 119.9526 | 120.02 | 119.9375 | 1.6231 | 1.7583 | 1.4408 | 1.6221 | 118.3218 | 118.5042 | 118.3969 | 118.5792
1889.25 | 121.9757 | -1.7029 | 120.0989 | 0.19053 | 1.063 | 1.1739 | 1.0784 | 1.1808 | 1.1615 | 1.0223 | 119.9953 | 120.0076 | 120.0658 | 119.9787 | 1.5499 | 1.6805 | 1.3675 | 1.5443 | 0.20426 | 1.0767 | 1.1876 | 1.0921 | 1.1945 | 1.1752 | 1.036 | 120.0091 | 120.0213 | 120.0795 | 119.9925 | 1.5636 | 1.6942 | 1.3812 | 1.558 | 118.4455 | 118.6278 | 118.5159 | 118.6983
1890.9844 | 121.9849 | -1.5289 | 120.2866 | 0.19053 | 1.0676 | 1.183 | 1.0876 | 1.1945 | 1.1707 | 1.036 | 120.1189 | 120.1312 | 120.2031 | 120.1115 | 1.4217 | 1.5523 | 1.2393 | 1.4206 | 0.20426 | 1.0813 | 1.1967 | 1.1013 | 1.2082 | 1.1844 | 1.0498 | 120.1327 | 120.145 | 120.2168 | 120.1253 | 1.4354 | 1.566 | 1.253 | 1.4344 | 118.6973 | 118.8796 | 118.7814 | 118.9638
1892.7344 | 121.9025 | -1.5152 | 120.3644 | 0.19968 | 1.0813 | 1.1968 | 1.1059 | 1.2036 | 1.1844 | 1.0406 | 120.1647 | 120.1816 | 120.2352 | 120.1482 | 1.3759 | 1.5202 | 1.1981 | 1.3794 | 0.21342 | 1.095 | 1.2105 | 1.1196 | 1.2174 | 1.1981 | 1.0544 | 120.1785 | 120.1953 | 120.2489 | 120.1619 | 1.3896 | 1.534 | 1.2118 | 1.3932 | 118.7888 | 118.9666 | 118.8593 | 119.0371
1894.4219 | 121.8979 | -1.3962 | 120.488 | 0.19968 | 1.1042 | 1.2059 | 1.1242 | 1.2174 | 1.2027 | 1.0635 | 120.2792 | 120.3052 | 120.3542 | 120.2718 | 1.2706 | 1.4012 | 1.0882 | 1.265 | 0.21342 | 1.1179 | 1.2196 | 1.1379 | 1.2311 | 1.2164 | 1.0772 | 120.2929 | 120.319 | 120.3679 | 120.2855 | 1.2843 | 1.415 | 1.102 | 1.2787 | 119.0086 | 119.191 | 119.0836 | 119.266
1896.1719 | 121.9391 | -1.474 | 120.4056 | 0.19968 | 1.1042 | 1.2196 | 1.1196 | 1.2265 | 1.2027 | 1.0727 | 120.2563 | 120.2732 | 120.3313 | 120.2443 | 1.2798 | 1.4241 | 1.1065 | 1.2833 | 0.21342 | 1.1179 | 1.2334 | 1.1333 | 1.2403 | 1.2164 | 1.0864 | 120.27 | 120.2869 | 120.345 | 120.2581 | 1.2935 | 1.4378 | 1.1203 | 1.297 | 118.9765 | 119.1498 | 119.0515 | 119.2248
1897.9062 | 121.9666 | -1.4191 | 120.4697 | 0.19511 | 1.1133 | 1.2242 | 1.1333 | 1.2357 | 1.2073 | 1.0772 | 120.2471 | 120.264 | 120.3221 | 120.2398 | 1.2935 | 1.4333 | 1.1111 | 1.2925 | 0.20884 | 1.1271 | 1.238 | 1.1471 | 1.2494 | 1.221 | 1.091 | 120.2609 | 120.2777 | 120.3359 | 120.2535 | 1.3072 | 1.447 | 1.1248 | 1.3062 | 118.9536 | 119.136 | 119.0287 | 119.211
1899.6094 | 121.9849 | -1.4511 | 120.3873 | 0.20426 | 1.1179 | 1.238 | 1.1425 | 1.2494 | 1.2256 | 1.0864 | 120.2426 | 120.2457 | 120.313 | 120.2306 | 1.2981 | 1.4424 | 1.1248 | 1.3016 | 0.21799 | 1.1317 | 1.2517 | 1.1562 | 1.2632 | 1.2393 | 1.1001 | 120.2563 | 120.2594 | 120.3267 | 120.2443 | 1.3118 | 1.4562 | 1.1386 | 1.3153 | 118.9445 | 119.1177 | 119.0149 | 119.1881
1901.3594 | 121.9254 | -1.4236 | 120.4605 | 0.20426 | 1.1225 | 1.238 | 1.1562 | 1.254 | 1.2256 | 1.0956 | 120.238 | 120.2686 | 120.3176 | 120.2398 | 1.3027 | 1.4333 | 1.1203 | 1.2925 | 0.21799 | 1.1362 | 1.2517 | 1.17 | 1.2677 | 1.2393 | 1.1093 | 120.2517 | 120.2823 | 120.3313 | 120.2535 | 1.3164 | 1.447 | 1.134 | 1.3062 | 118.9353 | 119.1177 | 119.0149 | 119.1973
1903.0469 | 121.8933 | -1.5289 | 120.3918 | 0.19968 | 1.15 | 1.2609 | 1.1608 | 1.2677 | 1.2485 | 1.1185 | 120.2197 | 120.2228 | 120.2809 | 120.1985 | 1.3301 | 1.4699 | 1.1523 | 1.3245 | 0.21342 | 1.1637 | 1.2746 | 1.1745 | 1.2815 | 1.2622 | 1.1322 | 120.2334 | 120.2365 | 120.2947 | 120.2123 | 1.3439 | 1.4836 | 1.1661 | 1.3382 | 118.8895 | 119.0674 | 118.9508 | 119.1286
1904.7812 | 121.8292 | -1.4694 | 120.4559 | 0.20426 | 1.1546 | 1.2654 | 1.17 | 1.2769 | 1.2485 | 1.1185 | 120.2609 | 120.2869 | 120.3359 | 120.2535 | 1.2798 | 1.4104 | 1.0928 | 1.2787 | 0.21799 | 1.1683 | 1.2792 | 1.1837 | 1.2906 | 1.2622 | 1.1322 | 120.2746 | 120.3006 | 120.3496 | 120.2672 | 1.2935 | 1.4241 | 1.1065 | 1.2925 | 118.9811 | 119.1681 | 119.0561 | 119.2431
1906.4531 | 121.9711 | -1.4145 | 120.4559 | 0.20884 | 1.1637 | 1.2837 | 1.1837 | 1.2906 | 1.2668 | 1.1322 | 120.2792 | 120.2961 | 120.3542 | 120.2718 | 1.2569 | 1.3966 | 1.0699 | 1.2558 | 0.22257 | 1.1774 | 1.2975 | 1.1974 | 1.3044 | 1.2805 | 1.1459 | 120.2929 | 120.3098 | 120.3679 | 120.2855 | 1.2706 | 1.4104 | 1.0836 | 1.2696 | 119.0223 | 119.2093 | 119.0973 | 119.2843
1908.1875 | 121.9528 | -1.3412 | 120.5292 | 0.21342 | 1.1774 | 1.2837 | 1.202 | 1.3089 | 1.276 | 1.1413 | 120.3524 | 120.3647 | 120.4229 | 120.3359 | 1.1928 | 1.328 | 1.0104 | 1.1917 | 0.22715 | 1.1912 | 1.2975 | 1.2158 | 1.3227 | 1.2897 | 1.1551 | 120.3662 | 120.3785 | 120.4366 | 120.3496 | 1.2065 | 1.3417 | 1.0241 | 1.2055 | 119.1597 | 119.3421 | 119.2301 | 119.4125
1909.9219 | 121.9666 | -1.2772 | 120.5475 | 0.218 | 1.1958 | 1.3158 | 1.2112 | 1.3181 | 1.2897 | 1.1597 | 120.3891 | 120.4014 | 120.4595 | 120.3725 | 1.1607 | 1.2913 | 0.97834 | 1.1597 | 0.23173 | 1.2095 | 1.3295 | 1.2249 | 1.3318 | 1.3034 | 1.1734 | 120.4028 | 120.4151 | 120.4732 | 120.3863 | 1.1745 | 1.3051 | 0.99207 | 1.1734 | 119.2283 | 119.4107 | 119.2988 | 119.4812
1911.5938 | 121.9849 | -1.3092 | 120.5841 | 0.20426 | 1.1958 | 1.3204 | 1.2203 | 1.3272 | 1.3034 | 1.1642 | 120.4165 | 120.4288 | 120.4915 | 120.4 | 1.1241 | 1.2593 | 0.95545 | 1.1322 | 0.21799 | 1.2095 | 1.3341 | 1.2341 | 1.341 | 1.3172 | 1.178 | 120.4303 | 120.4426 | 120.5053 | 120.4138 | 1.1378 | 1.273 | 0.96918 | 1.1459 | 119.2924 | 119.4611 | 119.3674 | 119.5361
1913.3281 | 121.8521 | -1.3367 | 120.5841 | 0.218 | 1.2095 | 1.3341 | 1.2341 | 1.3318 | 1.3172 | 1.1825 | 120.4074 | 120.4243 | 120.4824 | 120.3954 | 1.147 | 1.2822 | 0.9646 | 1.1414 | 0.23173 | 1.2232 | 1.3478 | 1.2478 | 1.3456 | 1.3309 | 1.1963 | 120.4211 | 120.438 | 120.4961 | 120.4092 | 1.1607 | 1.2959 | 0.97834 | 1.1551 | 119.2604 | 119.4428 | 119.3354 | 119.5178
1915.0625 | 121.9299 | -1.268 | 120.6162 | 0.218 | 1.2232 | 1.3478 | 1.2432 | 1.3456 | 1.3263 | 1.1917 | 120.4074 | 120.4334 | 120.4824 | 120.4046 | 1.1287 | 1.2639 | 0.94629 | 1.1276 | 0.23173 | 1.237 | 1.3616 | 1.257 | 1.3593 | 1.3401 | 1.2054 | 120.4211 | 120.4472 | 120.4961 | 120.4183 | 1.1424 | 1.2776 | 0.96002 | 1.1414 | 119.2787 | 119.4611 | 119.3537 | 119.5361
1916.7969 | 121.9803 | -1.2634 | 120.5612 | 0.21342 | 1.2324 | 1.3524 | 1.2524 | 1.3547 | 1.3446 | 1.2054 | 120.4028 | 120.4288 | 120.4824 | 120.3863 | 1.1333 | 1.273 | 0.95545 | 1.1322 | 0.22715 | 1.2461 | 1.3662 | 1.2661 | 1.3684 | 1.3584 | 1.2192 | 120.4165 | 120.4426 | 120.4961 | 120.4 | 1.147 | 1.2868 | 0.96918 | 1.1459 | 119.2695 | 119.4474 | 119.3491 | 119.5269
1918.4844 | 121.8704 | -2.2659 | 119.5862 | 0.218 | 1.1774 | 1.2975 | 1.2112 | 1.3044 | 1.2851 | 1.1459 | 117.3581 | 117.4068 | 117.4195 | 117.3641 | 4.2785 | 4.2717 | 4.1054 | 4.2408 | 0.23173 | 1.1912 | 1.3112 | 1.2249 | 1.3181 | 1.2989 | 1.1597 | 117.3718 | 117.4206 | 117.4333 | 117.3779 | 4.2922 | 4.2854 | 4.1191 | 4.2545 | 113.0796 | 113.2527 | 113.1411 | 113.3141
1920.2344 | 119.7235 | -72.5052 | 46.8842 | 0.030283 | -0.19162 | -0.1402 | -0.18984 | -0.096496 | -0.12044 | -0.22295 | 64.5406 | 63.9537 | 64.5953 | 64.316 | 55.7646 | 55.5826 | 55.333 | 55.379 | 0.044016 | -0.17789 | -0.12647 | -0.17611 | -0.082763 | -0.10671 | -0.20922 | 64.5543 | 63.9674 | 64.6091 | 64.3298 | 55.7783 | 55.5964 | 55.3467 | 55.3927 | 8.776 | 9.2076 | 8.8307 | 9.2624
1921.9844 | 121.5546 | -0.37994 | 121.257 | 0.22715 | 1.2965 | 1.4119 | 1.3165 | 1.4188 | 1.3996 | 1.2695 | 121.0575 | 121.0882 | 121.1371 | 121.0502 | 0.22678 | 0.32537 | 0.09471 | 0.23489 | 0.24089 | 1.3102 | 1.4257 | 1.3302 | 1.4325 | 1.4133 | 1.2833 | 121.0713 | 121.1019 | 121.1508 | 121.064 | 0.24052 | 0.3391 | 0.10844 | 0.24863 | 120.8308 | 120.9628 | 120.9103 | 121.0424
1923.7344 | 121.6644 | -0.33875 | 121.3303 | 0.23631 | 1.2965 | 1.4257 | 1.3211 | 1.4234 | 1.4087 | 1.2695 | 121.1399 | 121.1523 | 121.2103 | 121.1281 | 0.21763 | 0.31164 | 0.099289 | 0.23031 | 0.25004 | 1.3102 | 1.4394 | 1.3348 | 1.4371 | 1.4225 | 1.2833 | 121.1537 | 121.166 | 121.2241 | 121.1418 | 0.23136 | 0.32537 | 0.11302 | 0.24405 | 120.9223 | 121.0407 | 120.9927 | 121.111
1925.4062 | 121.6187 | -0.35706 | 121.4035 | 0.23631 | 1.3148 | 1.4348 | 1.3394 | 1.4371 | 1.4133 | 1.2741 | 121.1766 | 121.2072 | 121.2607 | 121.183 | 0.20389 | 0.29333 | 0.09471 | 0.22116 | 0.25004 | 1.3285 | 1.4486 | 1.3531 | 1.4509 | 1.427 | 1.2878 | 121.1903 | 121.221 | 121.2744 | 121.1968 | 0.21763 | 0.30706 | 0.10844 | 0.23489 | 120.9727 | 121.0819 | 121.0568 | 121.166
1927.1406 | 121.7377 | -0.29755 | 121.3806 | 0.24089 | 1.324 | 1.444 | 1.3531 | 1.4554 | 1.4316 | 1.297 | 121.2178 | 121.2393 | 121.2927 | 121.2151 | 0.20389 | 0.28417 | 0.090132 | 0.20742 | 0.25462 | 1.3377 | 1.4577 | 1.3668 | 1.4692 | 1.4454 | 1.3107 | 121.2315 | 121.253 | 121.3065 | 121.2288 | 0.21763 | 0.2979 | 0.10386 | 0.22116 | 121.0139 | 121.1277 | 121.0889 | 121.2026
1928.8906 | 121.701 | -0.32044 | 121.4584 | 0.23631 | 1.3377 | 1.4577 | 1.3623 | 1.4646 | 1.4454 | 1.3062 | 121.2453 | 121.2576 | 121.3111 | 121.2288 | 0.20847 | 0.28875 | 0.099289 | 0.20285 | 0.25004 | 1.3514 | 1.4715 | 1.376 | 1.4783 | 1.4591 | 1.3199 | 121.259 | 121.2713 | 121.3248 | 121.2426 | 0.2222 | 0.30248 | 0.11302 | 0.21658 | 121.0368 | 121.146 | 121.1026 | 121.2118
1930.5625 | 121.788 | -0.27466 | 121.4081 | 0.24089 | 1.3469 | 1.4623 | 1.3668 | 1.4783 | 1.4454 | 1.3153 | 121.2544 | 121.2805 | 121.334 | 121.2471 | 0.19474 | 0.27959 | 0.099289 | 0.20285 | 0.25462 | 1.3606 | 1.476 | 1.3806 | 1.4921 | 1.4591 | 1.329 | 121.2681 | 121.2942 | 121.3477 | 121.2609 | 0.20847 | 0.29333 | 0.11302 | 0.21658 | 121.0597 | 121.1551 | 121.1392 | 121.2347
1932.2969 | 121.8201 | -0.28839 | 121.4447 | 0.24547 | 1.3606 | 1.4852 | 1.3806 | 1.4875 | 1.4728 | 1.3336 | 121.2681 | 121.2851 | 121.3385 | 121.2655 | 0.19474 | 0.27959 | 0.09471 | 0.20285 | 0.2592 | 1.3743 | 1.4989 | 1.3943 | 1.5012 | 1.4866 | 1.3474 | 121.2819 | 121.2988 | 121.3523 | 121.2792 | 0.20847 | 0.29333 | 0.10844 | 0.21658 | 121.0734 | 121.1734 | 121.1438 | 121.2438
1933.9844 | 121.138 | -0.23346 | 120.9457 | 0.25005 | 1.3652 | 1.4852 | 1.3897 | 1.4921 | 1.4728 | 1.3336 | 120.0823 | 120.1541 | 120.1482 | 120.0886 | 0.69834 | 0.68704 | 0.60749 | 0.6744 | 0.26378 | 1.3789 | 1.4989 | 1.4035 | 1.5058 | 1.4866 | 1.3474 | 120.0961 | 120.1679 | 120.1619 | 120.1024 | 0.71207 | 0.70077 | 0.62122 | 0.68813 | 119.384 | 119.4748 | 119.4498 | 119.5407
1935.75 | 121.4676 | -0.20142 | 121.17 | 0.25005 | 1.3789 | 1.5081 | 1.4081 | 1.5149 | 1.482 | 1.3565 | 121.0163 | 121.0378 | 121.0913 | 121.009 | 0.21305 | 0.18345 | 0.016878 | 0.16622 | 0.26378 | 1.3926 | 1.5218 | 1.4218 | 1.5287 | 1.4957 | 1.3702 | 121.0301 | 121.0516 | 121.105 | 121.0228 | 0.22678 | 0.19718 | 0.030611 | 0.17995 | 120.8033 | 120.9995 | 120.8783 | 121.0744
1937.4375 | 121.4813 | -0.21973 | 121.2524 | 0.25462 | 1.3972 | 1.5173 | 1.4264 | 1.5287 | 1.5095 | 1.3657 | 121.085 | 121.1065 | 121.1508 | 121.0731 | 0.21763 | 0.18345 | 0.026035 | 0.1708 | 0.26836 | 1.411 | 1.531 | 1.4401 | 1.5424 | 1.5232 | 1.3794 | 121.0987 | 121.1202 | 121.1646 | 121.0869 | 0.23136 | 0.19718 | 0.039768 | 0.18453 | 120.8674 | 121.059 | 120.9332 | 121.1248
1939.1875 | 121.4584 | -0.21515 | 121.312 | 0.25005 | 1.411 | 1.531 | 1.4355 | 1.5333 | 1.5186 | 1.3794 | 121.1171 | 121.134 | 121.1966 | 121.1098 | 0.21763 | 0.17887 | 0.026035 | 0.1708 | 0.26378 | 1.4247 | 1.5447 | 1.4493 | 1.547 | 1.5324 | 1.3931 | 121.1308 | 121.1477 | 121.2103 | 121.1235 | 0.23136 | 0.19261 | 0.039768 | 0.18453 | 120.8994 | 121.091 | 120.979 | 121.1706
1940.9375 | 121.6141 | -0.18768 | 121.3074 | 0.2592 | 1.411 | 1.5447 | 1.4447 | 1.5516 | 1.5278 | 1.3886 | 121.1537 | 121.1615 | 121.2286 | 121.1464 | 0.21763 | 0.18803 | 0.030613 | 0.16622 | 0.27294 | 1.4247 | 1.5585 | 1.4584 | 1.5653 | 1.5415 | 1.4023 | 121.1674 | 121.1752 | 121.2424 | 121.1601 | 0.23136 | 0.20176 | 0.044346 | 0.17995 | 120.9361 | 121.1231 | 121.011 | 121.198
1942.6094 | 121.5454 | -0.23804 | 121.3623 | 0.26378 | 1.4293 | 1.5493 | 1.4584 | 1.5653 | 1.5415 | 1.4115 | 121.172 | 121.1935 | 121.2515 | 121.1647 | 0.21763 | 0.17887 | 0.030613 | 0.12044 | 0.27751 | 1.443 | 1.563 | 1.4721 | 1.579 | 1.5552 | 1.4252 | 121.1857 | 121.2072 | 121.2653 | 121.1784 | 0.23136 | 0.19261 | 0.044346 | 0.13417 | 120.9544 | 121.1414 | 121.0339 | 121.2209
1944.3594 | 121.6324 | -0.19226 | 121.3165 | 0.26378 | 1.4522 | 1.5676 | 1.4676 | 1.579 | 1.5461 | 1.4206 | 121.1903 | 121.2118 | 121.2653 | 121.183 | 0.21763 | 0.17887 | 0.026035 | 0.12044 | 0.27751 | 1.4659 | 1.5814 | 1.4813 | 1.5928 | 1.5598 | 1.4343 | 121.204 | 121.2256 | 121.279 | 121.1968 | 0.23136 | 0.19261 | 0.039768 | 0.13417 | 120.9727 | 121.1643 | 121.0476 | 121.2392
1946.0938 | 121.55 | -0.24261 | 121.3898 | 0.26836 | 1.4613 | 1.5768 | 1.4859 | 1.5928 | 1.569 | 1.4298 | 121.2086 | 121.2256 | 121.2836 | 121.1968 | 0.21305 | 0.1743 | 0.026035 | 0.11586 | 0.28209 | 1.4751 | 1.5905 | 1.4996 | 1.6065 | 1.5827 | 1.4435 | 121.2224 | 121.2393 | 121.2973 | 121.2105 | 0.22678 | 0.18803 | 0.039768 | 0.12959 | 120.9956 | 121.1826 | 121.0705 | 121.2576
1947.7812 | 121.5729 | -0.22888 | 121.4127 | 0.26378 | 1.4796 | 1.5905 | 1.5042 | 1.5973 | 1.5736 | 1.4389 | 121.2269 | 121.2347 | 121.3019 | 121.2105 | 0.22221 | 0.18345 | 0.035191 | 0.12959 | 0.27751 | 1.4934 | 1.6042 | 1.5179 | 1.6111 | 1.5873 | 1.4527 | 121.2407 | 121.2485 | 121.3156 | 121.2242 | 0.23594 | 0.19718 | 0.048924 | 0.14333 | 121.0047 | 121.1917 | 121.0797 | 121.2667
1949.5312 | 121.6461 | -0.21057 | 121.3989 | 0.26836 | 1.4796 | 1.6042 | 1.5088 | 1.6202 | 1.5873 | 1.4572 | 121.2361 | 121.2576 | 121.3065 | 121.2197 | 0.21763 | 0.18803 | 0.026035 | 0.13417 | 0.28209 | 1.4934 | 1.618 | 1.5225 | 1.634 | 1.601 | 1.471 | 121.2498 | 121.2713 | 121.3202 | 121.2334 | 0.23136 | 0.20176 | 0.039768 | 0.14791 | 121.0185 | 121.2101 | 121.0889 | 121.2804
1951.2031 | 121.6873 | -0.19684 | 121.3943 | 0.27294 | 1.498 | 1.6271 | 1.5271 | 1.634 | 1.6148 | 1.4801 | 121.2407 | 121.2622 | 121.3156 | 121.238 | 0.21305 | 0.18345 | 0.030613 | 0.12044 | 0.28667 | 1.5117 | 1.6409 | 1.5408 | 1.6477 | 1.6285 | 1.4939 | 121.2544 | 121.2759 | 121.3294 | 121.2517 | 0.22678 | 0.19718 | 0.044346 | 0.13417 | 121.0276 | 121.2101 | 121.1026 | 121.285
1952.9375 | 121.7239 | -0.19684 | 121.4081 | 0.27752 | 1.5209 | 1.6363 | 1.5546 | 1.6431 | 1.6193 | 1.4847 | 121.2544 | 121.2714 | 121.3202 | 121.238 | 0.21763 | 0.18803 | 0.030613 | 0.13417 | 0.29125 | 1.5346 | 1.65 | 1.5683 | 1.6569 | 1.6331 | 1.4984 | 121.2681 | 121.2851 | 121.3339 | 121.2517 | 0.23136 | 0.20176 | 0.044346 | 0.14791 | 121.0368 | 121.2238 | 121.1026 | 121.2896
1954.6875 | 121.7148 | -0.21057 | 121.4447 | 0.27752 | 1.53 | 1.6455 | 1.5591 | 1.6614 | 1.6377 | 1.5076 | 121.2636 | 121.2851 | 121.3385 | 121.2471 | 0.22678 | 0.18803 | 0.026035 | 0.13417 | 0.29125 | 1.5437 | 1.6592 | 1.5729 | 1.6752 | 1.6514 | 1.5213 | 121.2773 | 121.2988 | 121.3523 | 121.2609 | 0.24052 | 0.20176 | 0.039768 | 0.14791 | 121.0368 | 121.2375 | 121.1117 | 121.3125
1956.3594 | 121.669 | -0.25635 | 121.4493 | 0.28667 | 1.5437 | 1.6729 | 1.5729 | 1.6752 | 1.656 | 1.5213 | 121.2727 | 121.2897 | 121.3431 | 121.2563 | 0.22221 | 0.18803 | 0.026035 | 0.12959 | 0.30041 | 1.5575 | 1.6867 | 1.5866 | 1.6889 | 1.6697 | 1.5351 | 121.2865 | 121.3034 | 121.3568 | 121.27 | 0.23594 | 0.20176 | 0.039768 | 0.14333 | 121.0505 | 121.2467 | 121.1209 | 121.3171
1958.1094 | 121.6278 | -0.25635 | 121.4539 | 0.28667 | 1.5666 | 1.6775 | 1.582 | 1.6889 | 1.6605 | 1.5442 | 121.2773 | 121.2942 | 121.3477 | 121.27 | 0.22221 | 0.18803 | 0.026035 | 0.12959 | 0.30041 | 1.5804 | 1.6912 | 1.5958 | 1.7026 | 1.6743 | 1.558 | 121.291 | 121.308 | 121.3614 | 121.2838 | 0.23594 | 0.20176 | 0.039768 | 0.14333 | 121.0551 | 121.2513 | 121.1255 | 121.3217
1959.8594 | 121.6461 | -0.22888 | 121.4767 | 0.29125 | 1.5712 | 1.7004 | 1.6003 | 1.7072 | 1.6743 | 1.5442 | 121.2819 | 121.308 | 121.3614 | 121.2792 | 0.21763 | 0.19261 | 0.030613 | 0.12959 | 0.30498 | 1.585 | 1.7141 | 1.6141 | 1.721 | 1.688 | 1.558 | 121.2956 | 121.3217 | 121.3752 | 121.2929 | 0.23136 | 0.20634 | 0.044346 | 0.14333 | 121.0643 | 121.2513 | 121.1438 | 121.3308
1961.5469 | 121.6278 | -0.25177 | 121.4767 | 0.29125 | 1.5895 | 1.7096 | 1.6187 | 1.7255 | 1.6972 | 1.558 | 121.291 | 121.3126 | 121.3706 | 121.2838 | 0.22221 | 0.17887 | 0.026035 | 0.13417 | 0.30498 | 1.6033 | 1.7233 | 1.6324 | 1.7393 | 1.7109 | 1.5717 | 121.3048 | 121.3263 | 121.3843 | 121.2975 | 0.23594 | 0.19261 | 0.039768 | 0.14791 | 121.0688 | 121.265 | 121.1484 | 121.3445
1963.2812 | 121.6553 | -0.24719 | 121.4676 | 0.29125 | 1.6079 | 1.7279 | 1.6278 | 1.7393 | 1.7063 | 1.5763 | 121.3002 | 121.3171 | 121.3752 | 121.2838 | 0.22678 | 0.18803 | 0.030613 | 0.13417 | 0.30498 | 1.6216 | 1.7416 | 1.6416 | 1.753 | 1.7201 | 1.59 | 121.3139 | 121.3309 | 121.3889 | 121.2975 | 0.24052 | 0.20176 | 0.044346 | 0.14791 | 121.0734 | 121.2696 | 121.1484 | 121.3445
1965.0312 | 121.669 | -0.24261 | 121.4813 | 0.30499 | 1.6216 | 1.7416 | 1.6507 | 1.7576 | 1.7246 | 1.5946 | 121.3002 | 121.3171 | 121.3752 | 121.3021 | 0.22678 | 0.18803 | 0.035191 | 0.13417 | 0.31872 | 1.6353 | 1.7553 | 1.6644 | 1.7713 | 1.7384 | 1.6083 | 121.3139 | 121.3309 | 121.3889 | 121.3158 | 0.24052 | 0.20176 | 0.048924 | 0.14791 | 121.0734 | 121.265 | 121.1484 | 121.34
1966.7812 | 121.701 | -0.24719 | 121.4951 | 0.30499 | 1.6353 | 1.7599 | 1.6644 | 1.7667 | 1.7292 | 1.6037 | 121.3002 | 121.3309 | 121.3706 | 121.2883 | 0.22678 | 0.19719 | 0.030613 | 0.12959 | 0.31872 | 1.6491 | 1.7737 | 1.6782 | 1.7805 | 1.743 | 1.6175 | 121.3139 | 121.3446 | 121.3843 | 121.3021 | 0.24052 | 0.21092 | 0.044346 | 0.14333 | 121.0734 | 121.2696 | 121.1438 | 121.34
1968.4688 | 121.5729 | -0.21515 | 121.3898 | 0.30041 | 1.6582 | 1.7737 | 1.6782 | 1.7759 | 1.7567 | 1.6266 | 121.1995 | 121.2164 | 121.2653 | 121.1876 | 0.20847 | 0.16972 | 0.09471 | 0.16164 | 0.31414 | 1.672 | 1.7874 | 1.6919 | 1.7896 | 1.7704 | 1.6404 | 121.2132 | 121.2301 | 121.279 | 121.2013 | 0.2222 | 0.18345 | 0.10844 | 0.17538 | 120.991 | 121.1048 | 121.0568 | 121.1706
1970.2031 | 121.6644 | -0.21973 | 121.4539 | 0.30499 | 1.6674 | 1.792 | 1.6965 | 1.7942 | 1.7704 | 1.6358 | 121.2636 | 121.2942 | 121.3385 | 121.2655 | 0.20847 | 0.1743 | 0.016878 | 0.14791 | 0.31872 | 1.6811 | 1.8057 | 1.7102 | 1.8079 | 1.7842 | 1.6495 | 121.2773 | 121.308 | 121.3523 | 121.2792 | 0.2222 | 0.18803 | 0.030611 | 0.16164 | 121.0551 | 121.2467 | 121.1301 | 121.3216
1971.9375 | 121.7651 | -0.20599 | 121.4401 | 0.30956 | 1.6857 | 1.7965 | 1.7057 | 1.8079 | 1.7842 | 1.6541 | 121.2865 | 121.308 | 121.3614 | 121.2838 | 0.19474 | 0.16972 | 0.016878 | 0.15706 | 0.3233 | 1.6994 | 1.8103 | 1.7194 | 1.8217 | 1.7979 | 1.6678 | 121.3002 | 121.3217 | 121.3752 | 121.2975 | 0.20847 | 0.18345 | 0.030611 | 0.1708 | 121.0917 | 121.2696 | 121.1667 | 121.3445
1973.6719 | 121.7285 | -0.1831 | 121.4722 | 0.31872 | 1.6994 | 1.8194 | 1.724 | 1.8262 | 1.8025 | 1.6724 | 121.3048 | 121.3263 | 121.3752 | 121.3021 | 0.20847 | 0.16056 | 0.016878 | 0.16164 | 0.33246 | 1.7132 | 1.8332 | 1.7377 | 1.84 | 1.8162 | 1.6861 | 121.3185 | 121.34 | 121.3889 | 121.3158 | 0.2222 | 0.1743 | 0.030611 | 0.17538 | 121.0963 | 121.2879 | 121.1667 | 121.3583
1975.3594 | 121.7926 | -0.16937 | 121.4493 | 0.30956 | 1.7177 | 1.8378 | 1.7469 | 1.8446 | 1.8162 | 1.6907 | 121.3139 | 121.3355 | 121.3889 | 121.3067 | 0.20389 | 0.16514 | 0.016878 | 0.16164 | 0.3233 | 1.7315 | 1.8515 | 1.7606 | 1.8583 | 1.8299 | 1.7045 | 121.3277 | 121.3492 | 121.4026 | 121.3204 | 0.21763 | 0.17887 | 0.030611 | 0.17538 | 121.11 | 121.2971 | 121.185 | 121.372
1977.0938 | 121.7697 | -0.20142 | 121.4676 | 0.3233 | 1.7269 | 1.8515 | 1.756 | 1.8537 | 1.8391 | 1.6953 | 121.3277 | 121.3538 | 121.4026 | 121.3112 | 0.20389 | 0.16972 | 0.026035 | 0.15249 | 0.33703 | 1.7406 | 1.8652 | 1.7698 | 1.8674 | 1.8528 | 1.709 | 121.3414 | 121.3675 | 121.4164 | 121.325 | 0.21763 | 0.18345 | 0.039768 | 0.16622 | 121.1238 | 121.3016 | 121.1987 | 121.3766
1978.8281 | 121.7377 | -0.19226 | 121.4951 | 0.32788 | 1.7452 | 1.8652 | 1.7698 | 1.8674 | 1.8483 | 1.7228 | 121.3322 | 121.3446 | 121.4026 | 121.3158 | 0.20847 | 0.1743 | 0.012299 | 0.11586 | 0.34161 | 1.759 | 1.879 | 1.7835 | 1.8812 | 1.862 | 1.7365 | 121.346 | 121.3583 | 121.4164 | 121.3296 | 0.2222 | 0.18803 | 0.026032 | 0.12959 | 121.1238 | 121.3199 | 121.1942 | 121.3903
1980.5156 | 121.7285 | -0.20142 | 121.4996 | 0.32788 | 1.759 | 1.879 | 1.7926 | 1.8903 | 1.8712 | 1.7365 | 121.3322 | 121.3629 | 121.4072 | 121.3204 | 0.21305 | 0.16972 | 0.016878 | 0.12502 | 0.34161 | 1.7727 | 1.8927 | 1.8064 | 1.9041 | 1.8849 | 1.7502 | 121.346 | 121.3767 | 121.4209 | 121.3341 | 0.22678 | 0.18345 | 0.030611 | 0.13875 | 121.1192 | 121.3154 | 121.1942 | 121.3903
1982.25 | 121.6919 | -0.25177 | 121.5179 | 0.33246 | 1.7818 | 1.9064 | 1.8064 | 1.9178 | 1.8849 | 1.7548 | 121.3414 | 121.3538 | 121.4072 | 121.3296 | 0.22221 | 0.18345 | 0.021456 | 0.12502 | 0.34619 | 1.7956 | 1.9202 | 1.8201 | 1.9315 | 1.8986 | 1.7686 | 121.3551 | 121.3675 | 121.4209 | 121.3433 | 0.23594 | 0.19718 | 0.035189 | 0.13875 | 121.1192 | 121.3199 | 121.185 | 121.3857
1983.9375 | 121.6827 | -0.25635 | 121.5317 | 0.34161 | 1.7956 | 1.9156 | 1.8247 | 1.9224 | 1.9032 | 1.764 | 121.346 | 121.3629 | 121.4118 | 121.325 | 0.21763 | 0.16972 | 0.021456 | 0.12044 | 0.35535 | 1.8093 | 1.9293 | 1.8384 | 1.9361 | 1.9169 | 1.7777 | 121.3597 | 121.3767 | 121.4255 | 121.3387 | 0.23136 | 0.18345 | 0.035189 | 0.13417 | 121.1284 | 121.3245 | 121.1942 | 121.3903
1985.6875 | 121.756 | -0.2243 | 121.4859 | 0.34161 | 1.8139 | 1.9385 | 1.8339 | 1.9453 | 1.9169 | 1.7914 | 121.3414 | 121.3675 | 121.4164 | 121.3341 | 0.22221 | 0.18345 | 0.021456 | 0.12959 | 0.35535 | 1.8276 | 1.9522 | 1.8476 | 1.959 | 1.9307 | 1.8052 | 121.3551 | 121.3812 | 121.4301 | 121.3479 | 0.23594 | 0.19718 | 0.035189 | 0.14333 | 121.1192 | 121.3199 | 121.1942 | 121.3949
1987.4375 | 121.756 | -0.22888 | 121.5225 | 0.34619 | 1.8276 | 1.9476 | 1.8522 | 1.9544 | 1.9307 | 1.8006 | 121.346 | 121.3721 | 121.4209 | 121.3387 | 0.21763 | 0.17887 | 0.026035 | 0.12959 | 0.35992 | 1.8414 | 1.9614 | 1.8659 | 1.9682 | 1.9444 | 1.8143 | 121.3597 | 121.3858 | 121.4347 | 121.3525 | 0.23136 | 0.19261 | 0.039768 | 0.14333 | 121.1284 | 121.3199 | 121.2033 | 121.3949
1989.1875 | 121.7743 | -0.19684 | 121.4767 | 0.35077 | 1.8414 | 1.9614 | 1.8705 | 1.9636 | 1.9444 | 1.8098 | 121.346 | 121.3629 | 121.4301 | 121.3387 | 0.21763 | 0.19261 | 0.016878 | 0.12502 | 0.3645 | 1.8551 | 1.9751 | 1.8842 | 1.9773 | 1.9581 | 1.8235 | 121.3597 | 121.3767 | 121.4438 | 121.3525 | 0.23136 | 0.20634 | 0.030611 | 0.13875 | 121.1284 | 121.3291 | 121.2125 | 121.4132
1990.8594 | 121.6827 | -0.24719 | 121.5591 | 0.35535 | 1.846 | 1.9797 | 1.8842 | 1.9911 | 1.9627 | 1.8235 | 121.3551 | 121.3721 | 121.4255 | 121.3479 | 0.21305 | 0.17887 | 0.021456 | 0.12502 | 0.36908 | 1.8597 | 1.9934 | 1.8979 | 2.0048 | 1.9765 | 1.8372 | 121.3689 | 121.3858 | 121.4392 | 121.3616 | 0.22678 | 0.19261 | 0.035189 | 0.13875 | 121.1421 | 121.3337 | 121.2125 | 121.4041
1992.6094 | 121.8018 | -0.20142 | 121.5088 | 0.35993 | 1.8688 | 1.9889 | 1.898 | 2.0048 | 1.9627 | 1.8418 | 121.3597 | 121.3767 | 121.4438 | 121.3525 | 0.21305 | 0.18345 | 0.026035 | 0.12044 | 0.37366 | 1.8826 | 2.0026 | 1.9117 | 2.0185 | 1.9765 | 1.8555 | 121.3735 | 121.3904 | 121.4576 | 121.3662 | 0.22678 | 0.19718 | 0.039768 | 0.13417 | 121.1467 | 121.3337 | 121.2308 | 121.4178
1994.2969 | 121.8384 | -0.18768 | 121.5134 | 0.35993 | 1.878 | 2.0026 | 1.9071 | 2.0139 | 1.9856 | 1.8555 | 121.3551 | 121.3721 | 121.4347 | 121.3479 | 0.22221 | 0.19261 | 0.030613 | 0.12959 | 0.37366 | 1.8917 | 2.0163 | 1.9208 | 2.0277 | 1.9993 | 1.8693 | 121.3689 | 121.3858 | 121.4484 | 121.3616 | 0.23594 | 0.20634 | 0.044346 | 0.14333 | 121.1329 | 121.3245 | 121.2125 | 121.4041
1996.0312 | 121.8246 | -0.20142 | 121.4996 | 0.36451 | 1.9055 | 2.0209 | 1.93 | 2.0323 | 2.0039 | 1.8693 | 121.3643 | 121.3812 | 121.4301 | 121.3479 | 0.21763 | 0.18803 | 0.030613 | 0.12959 | 0.37824 | 1.9192 | 2.0346 | 1.9437 | 2.046 | 2.0177 | 1.883 | 121.378 | 121.395 | 121.4438 | 121.3616 | 0.23136 | 0.20176 | 0.044346 | 0.14333 | 121.1467 | 121.3337 | 121.2125 | 121.3995
1997.8125 | 121.7651 | -0.23804 | 121.5454 | 0.37366 | 1.9238 | 2.0346 | 1.9483 | 2.0506 | 2.0177 | 1.8922 | 121.3643 | 121.3812 | 121.4393 | 121.3479 | 0.24052 | 0.20176 | 0.035191 | 0.13417 | 0.38739 | 1.9375 | 2.0484 | 1.962 | 2.0643 | 2.0314 | 1.9059 | 121.378 | 121.395 | 121.453 | 121.3616 | 0.25425 | 0.2155 | 0.048924 | 0.14791 | 121.1238 | 121.3291 | 121.1987 | 121.4041
1999.5469 | 121.7285 | -0.25635 | 121.5546 | 0.36908 | 1.9329 | 2.053 | 1.9666 | 2.0597 | 2.036 | 1.9105 | 121.3689 | 121.3858 | 121.4347 | 121.357 | 0.23136 | 0.19719 | 0.03977 | 0.13875 | 0.38282 | 1.9467 | 2.0667 | 1.9804 | 2.0735 | 2.0497 | 1.9242 | 121.3826 | 121.3996 | 121.4484 | 121.3708 | 0.2451 | 0.21092 | 0.053503 | 0.15248 | 121.1375 | 121.3291 | 121.2033 | 121.3949
2001.2812 | 121.8109 | -0.21973 | 121.4951 | 0.37824 | 1.9604 | 2.0758 | 1.9804 | 2.0826 | 2.0589 | 1.9334 | 121.3597 | 121.3904 | 121.4484 | 121.357 | 0.23136 | 0.19719 | 0.030613 | 0.13417 | 0.39197 | 1.9742 | 2.0896 | 1.9941 | 2.0963 | 2.0726 | 1.9471 | 121.3735 | 121.4041 | 121.4621 | 121.3708 | 0.2451 | 0.21092 | 0.044346 | 0.14791 | 121.1284 | 121.3291 | 121.217 | 121.4178
2002.9531 | 121.8155 | -0.2243 | 121.5225 | 0.3874 | 1.9742 | 2.085 | 1.9941 | 2.1009 | 2.0772 | 1.9471 | 121.3643 | 121.3904 | 121.4484 | 121.357 | 0.23136 | 0.18803 | 0.030613 | 0.13417 | 0.40113 | 1.9879 | 2.0987 | 2.0078 | 2.1147 | 2.0909 | 1.9608 | 121.378 | 121.4041 | 121.4621 | 121.3708 | 0.2451 | 0.20176 | 0.044346 | 0.14791 | 121.1329 | 121.3337 | 121.217 | 121.4178
2004.7031 | 121.8292 | -0.22888 | 121.5134 | 0.3874 | 1.9879 | 2.1125 | 2.0124 | 2.1192 | 2.0909 | 1.9608 | 121.3368 | 121.3538 | 121.4072 | 121.3158 | 0.27714 | 0.23381 | 0.080975 | 0.17996 | 0.40113 | 2.0016 | 2.1262 | 2.0261 | 2.133 | 2.1047 | 1.9746 | 121.3506 | 121.3675 | 121.4209 | 121.3296 | 0.29088 | 0.24754 | 0.094708 | 0.19369 | 121.0597 | 121.2559 | 121.1301 | 121.3262
2006.4531 | 121.788 | -0.25177 | 121.5363 | 0.39198 | 2.0108 | 2.1262 | 2.0353 | 2.1421 | 2.1184 | 1.9929 | 121.3735 | 121.3904 | 121.453 | 121.3662 | 0.23136 | 0.20634 | 0.035191 | 0.13875 | 0.40571 | 2.0245 | 2.1399 | 2.049 | 2.1559 | 2.1321 | 2.0066 | 121.3872 | 121.4041 | 121.4667 | 121.3799 | 0.2451 | 0.22008 | 0.048924 | 0.15248 | 121.1421 | 121.3383 | 121.2216 | 121.4178
2008.125 | 121.8658 | -0.25177 | 121.4218 | 0.39655 | 2.0337 | 2.1491 | 2.049 | 2.1559 | 2.1275 | 1.9929 | 121.346 | 121.3675 | 121.4209 | 121.3341 | 0.25883 | 0.22465 | 0.058083 | 0.15706 | 0.41029 | 2.0474 | 2.1628 | 2.0628 | 2.1696 | 2.1413 | 2.0066 | 121.3597 | 121.3812 | 121.4347 | 121.3479 | 0.27257 | 0.23839 | 0.071816 | 0.1708 | 121.0872 | 121.2879 | 121.1621 | 121.3629
2009.8125 | 117.5766 | -27.4841 | 89.6439 | 0.19968 | 0.80198 | 0.92204 | 0.83574 | 0.93354 | 0.91427 | 0.77051 | 87.6849 | 87.7132 | 87.7523 | 87.6691 | 29.6644 | 29.6342 | 29.4284 | 29.5672 | 0.21342 | 0.81571 | 0.93577 | 0.84947 | 0.94728 | 0.928 | 0.78424 | 87.6986 | 87.7269 | 87.766 | 87.6828 | 29.6782 | 29.6479 | 29.4422 | 29.581 | 58.0204 | 58.2564 | 58.0878 | 58.3238
2011.5625 | 120.8908 | -0.19226 | 120.8176 | 0.41487 | 2.0612 | 2.1857 | 2.0902 | 2.1971 | 2.1687 | 2.0432 | 120.5722 | 120.5845 | 120.6426 | 120.5649 | 0.20847 | 0.1743 | 0.044348 | 0.12044 | 0.4286 | 2.0749 | 2.1995 | 2.104 | 2.2108 | 2.1825 | 2.057 | 120.5859 | 120.5983 | 120.6564 | 120.5786 | 0.2222 | 0.18803 | 0.058081 | 0.13417 | 120.3637 | 120.5279 | 120.4342 | 120.5983
2013.2344 | 121.0464 | -0.17853 | 120.9183 | 0.41945 | 2.0886 | 2.204 | 2.1131 | 2.2245 | 2.1916 | 2.0616 | 120.7416 | 120.7585 | 120.812 | 120.7297 | 0.181 | 0.13309 | 0.003143 | 0.083814 | 0.43318 | 2.1024 | 2.2178 | 2.1269 | 2.2383 | 2.2054 | 2.0753 | 120.7554 | 120.7723 | 120.8258 | 120.7434 | 0.19474 | 0.14683 | 0.016876 | 0.097547 | 120.5606 | 120.7385 | 120.631 | 120.8089
2014.9219 | 121.1655 | -0.13275 | 120.9778 | 0.41945 | 2.1115 | 2.2407 | 2.1498 | 2.2428 | 2.21 | 2.089 | 120.8057 | 120.8226 | 120.8899 | 120.7938 | 0.181 | 0.12851 | 0.003143 | 0.088392 | 0.43318 | 2.1253 | 2.2544 | 2.1635 | 2.2566 | 2.2237 | 2.1028 | 120.8195 | 120.8364 | 120.9036 | 120.8075 | 0.19474 | 0.14225 | 0.016876 | 0.10212 | 120.6247 | 120.8026 | 120.7089 | 120.8867
2016.6562 | 121.2753 | -0.16479 | 120.9915 | 0.43318 | 2.139 | 2.2453 | 2.1589 | 2.2566 | 2.2283 | 2.1028 | 120.8515 | 120.8638 | 120.9265 | 120.8396 | 0.181 | 0.13767 | -0.001436 | 0.09297 | 0.44691 | 2.1527 | 2.259 | 2.1727 | 2.2703 | 2.242 | 2.1165 | 120.8652 | 120.8776 | 120.9402 | 120.8533 | 0.19474 | 0.1514 | 0.012297 | 0.1067 | 120.6705 | 120.8529 | 120.7455 | 120.9279
2018.4062 | 121.257 | -0.14648 | 121.0373 | 0.43776 | 2.1527 | 2.2681 | 2.1772 | 2.2795 | 2.2557 | 2.1302 | 120.8836 | 120.8867 | 120.9631 | 120.8625 | 0.181 | 0.14225 | -0.001436 | 0.09297 | 0.45149 | 2.1665 | 2.2819 | 2.191 | 2.2932 | 2.2695 | 2.144 | 120.8973 | 120.9005 | 120.9768 | 120.8762 | 0.19474 | 0.15598 | 0.012297 | 0.1067 | 120.7026 | 120.885 | 120.7821 | 120.9645
2020.0938 | 121.2753 | -0.16479 | 121.0602 | 0.44234 | 2.1619 | 2.2865 | 2.1864 | 2.2932 | 2.2649 | 2.1394 | 120.8836 | 120.9005 | 120.9631 | 120.8762 | 0.19016 | 0.16514 | 0.021456 | 0.11128 | 0.45607 | 2.1756 | 2.3002 | 2.2001 | 2.3069 | 2.2786 | 2.1531 | 120.8973 | 120.9142 | 120.9768 | 120.89 | 0.20389 | 0.17887 | 0.035189 | 0.12502 | 120.6934 | 120.8621 | 120.773 | 120.9417
2021.8438 | 118.0115 | -12.5839 | 104.7821 | 0.30956 | 1.3102 | 1.3936 | 1.3211 | 1.4463 | 1.4133 | 1.2833 | 96.3428 | 96.4954 | 96.3777 | 96.3647 | 21.0163 | 21.032 | 20.8302 | 20.9786 | 0.3233 | 1.324 | 1.4074 | 1.3348 | 1.46 | 1.427 | 1.297 | 96.3566 | 96.5091 | 96.3915 | 96.3784 | 21.03 | 21.0457 | 20.844 | 20.9923 | 75.3266 | 75.5126 | 75.3615 | 75.5475
2023.5938 | 120.5658 | -0.17853 | 120.4422 | 0.44692 | 2.1985 | 2.3094 | 2.223 | 2.3298 | 2.3061 | 2.176 | 120.2471 | 120.264 | 120.3267 | 120.2352 | 0.098596 | 0.14225 | -0.006014 | 0.10213 | 0.46065 | 2.2123 | 2.3231 | 2.2368 | 2.3436 | 2.3198 | 2.1897 | 120.2609 | 120.2777 | 120.3405 | 120.2489 | 0.11233 | 0.15598 | 0.007719 | 0.11586 | 120.1485 | 120.2532 | 120.2281 | 120.3327
2025.2812 | 120.6573 | -0.19226 | 120.5292 | 0.46065 | 2.2168 | 2.3322 | 2.2505 | 2.3481 | 2.3153 | 2.1897 | 120.3708 | 120.3922 | 120.4503 | 120.3588 | 0.094017 | 0.14225 | 0.003143 | 0.09297 | 0.47439 | 2.2306 | 2.346 | 2.2642 | 2.3619 | 2.329 | 2.2035 | 120.3845 | 120.406 | 120.4641 | 120.3725 | 0.10775 | 0.15598 | 0.016876 | 0.1067 | 120.2767 | 120.3676 | 120.3563 | 120.4472
2026.9688 | 120.8542 | -0.16937 | 120.6116 | 0.46523 | 2.2397 | 2.3551 | 2.2688 | 2.3664 | 2.3427 | 2.2126 | 120.444 | 120.4609 | 120.5144 | 120.4229 | 0.080283 | 0.14225 | -0.001436 | 0.097548 | 0.47896 | 2.2535 | 2.3689 | 2.2825 | 2.3802 | 2.3565 | 2.2264 | 120.4578 | 120.4746 | 120.5282 | 120.4366 | 0.094016 | 0.15598 | 0.012297 | 0.11128 | 120.3637 | 120.4455 | 120.4342 | 120.5159
2028.7031 | 115.4297 | -37.8525 | 77.3941 | 0.14932 | 0.46773 | 0.53285 | 0.47862 | 0.5902 | 0.548 | 0.42715 | 75.8769 | 75.909 | 75.9403 | 75.8598 | 39.5121 | 39.4816 | 39.2491 | 39.4012 | 0.16305 | 0.48146 | 0.54659 | 0.49235 | 0.60393 | 0.56173 | 0.44088 | 75.8907 | 75.9227 | 75.954 | 75.8735 | 39.5258 | 39.4953 | 39.2628 | 39.4149 | 36.3649 | 36.6279 | 36.4282 | 36.6912
2030.4531 | 120.0302 | -0.20599 | 119.9066 | 0.47439 | 2.2764 | 2.3872 | 2.2917 | 2.4076 | 2.3748 | 2.2401 | 119.6703 | 119.6779 | 119.7361 | 119.6536 | 0.23594 | 0.19719 | 0.053505 | 0.20285 | 0.48812 | 2.2901 | 2.4009 | 2.3054 | 2.4214 | 2.3885 | 2.2538 | 119.684 | 119.6917 | 119.7499 | 119.6674 | 0.24967 | 0.21092 | 0.067238 | 0.21658 | 119.4343 | 119.6167 | 119.5002 | 119.6826
2032.1875 | 120.2362 | -0.3067 | 119.9844 | 0.47439 | 2.2809 | 2.4009 | 2.3192 | 2.4076 | 2.3839 | 2.2538 | 119.858 | 119.8748 | 119.9422 | 119.8414 | 0.2451 | 0.22008 | 0.085554 | 0.15706 | 0.48812 | 2.2947 | 2.4147 | 2.3329 | 2.4214 | 2.3977 | 2.2676 | 119.8717 | 119.8885 | 119.9559 | 119.8551 | 0.25883 | 0.23381 | 0.099287 | 0.1708 | 119.6129 | 119.7724 | 119.6971 | 119.8566
2033.9219 | 120.4376 | -0.46692 | 119.8334 | 0.47896 | 2.2855 | 2.4009 | 2.31 | 2.4168 | 2.3885 | 2.2584 | 119.7481 | 119.7558 | 119.8185 | 119.7361 | 0.4328 | 0.38489 | 0.25953 | 0.38139 | 0.4927 | 2.2993 | 2.4147 | 2.3237 | 2.4305 | 2.4022 | 2.2722 | 119.7618 | 119.7695 | 119.8323 | 119.7498 | 0.44654 | 0.39862 | 0.27326 | 0.39513 | 119.3153 | 119.4886 | 119.3857 | 119.559
2035.6719 | 120.3461 | -0.26093 | 120.2362 | 0.4927 | 2.3221 | 2.4421 | 2.3558 | 2.4488 | 2.4251 | 2.295 | 120.0228 | 120.0396 | 120.0978 | 120.0154 | 0.22678 | 0.19719 | 0.06724 | 0.15249 | 0.50643 | 2.3359 | 2.4559 | 2.3695 | 2.4626 | 2.4389 | 2.3088 | 120.0365 | 120.0534 | 120.1115 | 120.0291 | 0.24052 | 0.21092 | 0.080973 | 0.16622 | 119.796 | 119.9556 | 119.871 | 120.0306
2037.3438 | 119.6732 | -2.7054 | 116.9678 | 0.44234 | 2.0154 | 2.1354 | 2.0536 | 2.1559 | 2.1275 | 1.9883 | 111.6579 | 111.7703 | 111.7287 | 111.6632 | 7.0986 | 7.0918 | 6.9898 | 7.0655 | 0.45607 | 2.0291 | 2.1491 | 2.0674 | 2.1696 | 2.1413 | 2.002 | 111.6716 | 111.784 | 111.7425 | 111.677 | 7.1124 | 7.1055 | 7.0035 | 7.0793 | 104.5593 | 104.6681 | 104.6301 | 104.739
2039.0781 | 120.2637 | -0.18768 | 120.0806 | 0.51559 | 2.3634 | 2.4833 | 2.4016 | 2.4946 | 2.4663 | 2.3408 | 119.8854 | 119.9069 | 119.9605 | 119.878 | 0.181 | 0.13767 | 0.003143 | 0.14333 | 0.52933 | 2.3771 | 2.4971 | 2.4153 | 2.5084 | 2.4801 | 2.3546 | 119.8992 | 119.9206 | 119.9742 | 119.8917 | 0.19474 | 0.1514 | 0.016876 | 0.15706 | 119.7044 | 119.8823 | 119.7795 | 119.9573
2040.8281 | 120.2728 | -0.21515 | 120.1859 | 0.51559 | 2.3863 | 2.5108 | 2.4245 | 2.5313 | 2.4984 | 2.3683 | 120.0045 | 120.0305 | 120.0841 | 119.9971 | 0.17185 | 0.13309 | -0.001436 | 0.088392 | 0.52933 | 2.4 | 2.5245 | 2.4382 | 2.545 | 2.5121 | 2.382 | 120.0182 | 120.0442 | 120.0978 | 120.0108 | 0.18558 | 0.14683 | 0.012297 | 0.10212 | 119.8326 | 120.0059 | 119.9122 | 120.0855
2042.5156 | 120.3506 | -0.20142 | 120.2728 | 0.52475 | 2.4229 | 2.5429 | 2.4519 | 2.5541 | 2.5213 | 2.3958 | 120.064 | 120.0763 | 120.1436 | 120.0566 | 0.16727 | 0.13309 | -0.006014 | 0.097548 | 0.53848 | 2.4366 | 2.5566 | 2.4657 | 2.5679 | 2.535 | 2.4095 | 120.0777 | 120.09 | 120.1573 | 120.0703 | 0.181 | 0.14683 | 0.007719 | 0.11128 | 119.8967 | 120.07 | 119.9763 | 120.1496
2044.25 | 120.4559 | -0.1831 | 120.2637 | 0.52933 | 2.4275 | 2.5566 | 2.4657 | 2.5633 | 2.535 | 2.4049 | 120.0915 | 120.1221 | 120.1711 | 120.0886 | 0.181 | 0.13767 | 0.003143 | 0.088392 | 0.54306 | 2.4412 | 2.5703 | 2.4794 | 2.577 | 2.5488 | 2.4187 | 120.1052 | 120.1358 | 120.1848 | 120.1024 | 0.19474 | 0.1514 | 0.016876 | 0.10212 | 119.9105 | 120.0883 | 119.9901 | 120.1679
2045.9844 | 120.4468 | -0.17395 | 120.2362 | 0.53391 | 2.4504 | 2.5658 | 2.4794 | 2.5816 | 2.5488 | 2.4278 | 120.0686 | 120.0809 | 120.1436 | 120.0612 | 0.17642 | 0.14683 | 0.044348 | 0.13875 | 0.54764 | 2.4641 | 2.5795 | 2.4932 | 2.5953 | 2.5625 | 2.4415 | 120.0823 | 120.0946 | 120.1573 | 120.0749 | 0.19016 | 0.16056 | 0.058081 | 0.15248 | 119.8922 | 120.0242 | 119.9672 | 120.0992
2047.7188 | 120.5429 | -0.14191 | 120.2682 | 0.53391 | 2.4641 | 2.5932 | 2.5069 | 2.6137 | 2.5762 | 2.4507 | 120.1327 | 120.1495 | 120.2123 | 120.1253 | 0.181 | 0.13767 | 0.012299 | 0.13875 | 0.54764 | 2.4778 | 2.607 | 2.5206 | 2.6274 | 2.59 | 2.4644 | 120.1464 | 120.1633 | 120.226 | 120.139 | 0.19474 | 0.1514 | 0.026032 | 0.15248 | 119.9517 | 120.1204 | 120.0313 | 120.2
2049.4062 | 120.4742 | -0.19226 | 120.3186 | 0.54764 | 2.487 | 2.6161 | 2.5435 | 2.632 | 2.5991 | 2.4782 | 120.1785 | 120.1953 | 120.2489 | 120.1573 | 0.16269 | 0.13767 | -0.001436 | 0.088392 | 0.56137 | 2.5007 | 2.6299 | 2.5573 | 2.6457 | 2.6129 | 2.4919 | 120.1922 | 120.2091 | 120.2626 | 120.1711 | 0.17642 | 0.1514 | 0.012297 | 0.10212 | 120.0158 | 120.1799 | 120.0862 | 120.2503
2051.1562 | 120.4834 | -0.21057 | 120.3506 | 0.56138 | 2.5145 | 2.639 | 2.5527 | 2.6594 | 2.6174 | 2.5056 | 120.2014 | 120.2182 | 120.2764 | 120.194 | 0.16727 | 0.13767 | -0.006014 | 0.083814 | 0.57511 | 2.5282 | 2.6527 | 2.5664 | 2.6732 | 2.6312 | 2.5194 | 120.2151 | 120.232 | 120.2901 | 120.2077 | 0.181 | 0.1514 | 0.007719 | 0.097547 | 120.0341 | 120.2074 | 120.1091 | 120.2824
2052.8906 | 120.5154 | -0.1831 | 120.3827 | 0.56595 | 2.5282 | 2.6527 | 2.571 | 2.6686 | 2.6357 | 2.5148 | 120.2197 | 120.2365 | 120.2947 | 120.2123 | 0.17642 | 0.13767 | 0.007721 | 0.11586 | 0.57969 | 2.5419 | 2.6665 | 2.5847 | 2.6823 | 2.6495 | 2.5285 | 120.2334 | 120.2503 | 120.3084 | 120.226 | 0.19016 | 0.1514 | 0.021454 | 0.12959 | 120.0432 | 120.212 | 120.1183 | 120.287
2054.5781 | 120.6482 | -0.14648 | 120.3735 | 0.56595 | 2.5465 | 2.6756 | 2.5801 | 2.6915 | 2.6586 | 2.5331 | 120.238 | 120.2594 | 120.3221 | 120.2398 | 0.16727 | 0.13309 | -0.001436 | 0.088392 | 0.57969 | 2.5602 | 2.6894 | 2.5939 | 2.7052 | 2.6724 | 2.5468 | 120.2517 | 120.2732 | 120.3359 | 120.2535 | 0.181 | 0.14683 | 0.012297 | 0.10212 | 120.0707 | 120.2394 | 120.1549 | 120.3236
2056.3281 | 120.6665 | -0.13275 | 120.3781 | 0.57511 | 2.574 | 2.7123 | 2.6122 | 2.7144 | 2.677 | 2.5606 | 120.2471 | 120.264 | 120.3221 | 120.2398 | 0.181 | 0.15141 | 0.012299 | 0.097548 | 0.58884 | 2.5877 | 2.726 | 2.6259 | 2.7281 | 2.6907 | 2.5743 | 120.2609 | 120.2777 | 120.3359 | 120.2535 | 0.19474 | 0.16514 | 0.026032 | 0.11128 | 120.0661 | 120.2348 | 120.1411 | 120.3099
2058.0156 | 120.6573 | -0.16022 | 120.4239 | 0.58427 | 2.5923 | 2.7123 | 2.6259 | 2.7235 | 2.6953 | 2.5697 | 120.2838 | 120.3006 | 120.3588 | 120.2718 | 0.181 | 0.14225 | 0.003143 | 0.088392 | 0.598 | 2.606 | 2.726 | 2.6397 | 2.7373 | 2.709 | 2.5835 | 120.2975 | 120.3144 | 120.3725 | 120.2855 | 0.19474 | 0.15598 | 0.016876 | 0.10212 | 120.1028 | 120.2806 | 120.1778 | 120.3556
2059.7656 | 120.6573 | -0.16937 | 120.4514 | 0.58885 | 2.6152 | 2.7352 | 2.6488 | 2.7464 | 2.7136 | 2.588 | 120.3021 | 120.3144 | 120.3588 | 120.2901 | 0.181 | 0.13767 | 0.012299 | 0.10213 | 0.60258 | 2.6289 | 2.7489 | 2.6626 | 2.7601 | 2.7273 | 2.6018 | 120.3158 | 120.3281 | 120.3725 | 120.3039 | 0.19474 | 0.1514 | 0.026032 | 0.11586 | 120.1211 | 120.2898 | 120.1778 | 120.3465
2061.4531 | 120.7077 | -0.14191 | 120.4651 | 0.59342 | 2.6335 | 2.7489 | 2.6626 | 2.7739 | 2.7365 | 2.6109 | 120.3158 | 120.3419 | 120.3908 | 120.3084 | 0.181 | 0.13767 | -0.001436 | 0.12959 | 0.60716 | 2.6472 | 2.7626 | 2.6763 | 2.7876 | 2.7502 | 2.6247 | 120.3296 | 120.3556 | 120.4046 | 120.3222 | 0.19474 | 0.1514 | 0.012297 | 0.14333 | 120.1348 | 120.3173 | 120.2098 | 120.3923
2063.1875 | 120.7123 | -0.16022 | 120.488 | 0.61632 | 2.6656 | 2.7901 | 2.6992 | 2.7968 | 2.7731 | 2.6384 | 120.325 | 120.3464 | 120.4 | 120.313 | 0.089439 | 0.13309 | 0.012299 | 0.097548 | 0.63005 | 2.6793 | 2.8038 | 2.7129 | 2.8105 | 2.7868 | 2.6521 | 120.3387 | 120.3602 | 120.4137 | 120.3267 | 0.10317 | 0.14683 | 0.026032 | 0.11128 | 120.2355 | 120.3127 | 120.3105 | 120.3877
2064.9219 | 120.7626 | -0.13275 | 120.4971 | 0.61632 | 2.693 | 2.8084 | 2.7267 | 2.8242 | 2.7914 | 2.6705 | 120.3524 | 120.3739 | 120.432 | 120.3496 | 0.17642 | 0.13309 | -0.001436 | 0.088392 | 0.63005 | 2.7068 | 2.8222 | 2.7404 | 2.838 | 2.8051 | 2.6842 | 120.3662 | 120.3876 | 120.4458 | 120.3634 | 0.19016 | 0.14683 | 0.012297 | 0.10212 | 120.176 | 120.3539 | 120.2556 | 120.4335
2066.6719 | 120.6757 | -0.17853 | 120.5154 | 0.63463 | 2.7068 | 2.8405 | 2.7496 | 2.8517 | 2.8143 | 2.7025 | 120.3387 | 120.3647 | 120.4229 | 120.3359 | 0.17642 | 0.13767 | 0.003143 | 0.088392 | 0.64836 | 2.7205 | 2.8542 | 2.7633 | 2.8654 | 2.828 | 2.7162 | 120.3524 | 120.3785 | 120.4366 | 120.3496 | 0.19016 | 0.1514 | 0.016876 | 0.10212 | 120.1623 | 120.3356 | 120.2464 | 120.4197
2068.4219 | 120.7077 | -0.19226 | 120.5658 | 0.63921 | 2.7342 | 2.8588 | 2.7724 | 2.87 | 2.8418 | 2.7162 | 120.3753 | 120.3968 | 120.4458 | 120.368 | 0.17185 | 0.13309 | 0.003143 | 0.12502 | 0.65294 | 2.748 | 2.8725 | 2.7862 | 2.8838 | 2.8555 | 2.73 | 120.3891 | 120.4105 | 120.4595 | 120.3817 | 0.18558 | 0.14683 | 0.016876 | 0.13875 | 120.2035 | 120.3722 | 120.2739 | 120.4426
2070.1094 | 120.694 | -0.17853 | 120.5383 | 0.64379 | 2.7526 | 2.8725 | 2.7908 | 2.8883 | 2.8555 | 2.7391 | 120.3845 | 120.4014 | 120.4595 | 120.3817 | 0.17642 | 0.13309 | 0.003143 | 0.10213 | 0.65752 | 2.7663 | 2.8863 | 2.8045 | 2.9021 | 2.8692 | 2.7529 | 120.3982 | 120.4151 | 120.4732 | 120.3954 | 0.19016 | 0.14683 | 0.016876 | 0.11586 | 120.2081 | 120.3814 | 120.2831 | 120.4564
2071.875 | 120.7031 | -0.20142 | 120.5475 | 0.65294 | 2.7709 | 2.8817 | 2.8045 | 2.9066 | 2.8692 | 2.7437 | 120.3937 | 120.4105 | 120.4732 | 120.3863 | 0.18558 | 0.14225 | 0.003143 | 0.10213 | 0.66668 | 2.7846 | 2.8954 | 2.8182 | 2.9204 | 2.883 | 2.7574 | 120.4074 | 120.4243 | 120.487 | 120.4 | 0.19931 | 0.15598 | 0.016876 | 0.11586 | 120.2081 | 120.3905 | 120.2877 | 120.4701
2073.5469 | 120.3094 | -0.19226 | 120.2087 | 0.65752 | 2.7846 | 2.8725 | 2.8136 | 2.9204 | 2.883 | 2.7666 | 118.9194 | 119.0186 | 118.9899 | 118.9347 | 1.0463 | 1.0533 | 0.9646 | 1.0361 | 0.67126 | 2.7983 | 2.8863 | 2.8274 | 2.9341 | 2.8967 | 2.7803 | 118.9331 | 119.0323 | 119.0036 | 118.9485 | 1.06 | 1.067 | 0.97834 | 1.0498 | 117.8731 | 117.9548 | 117.9436 | 118.0253
2075.2969 | 120.7214 | -0.14191 | 120.4559 | 0.67126 | 2.8075 | 2.9366 | 2.8457 | 2.9387 | 2.9104 | 2.7849 | 120.3341 | 120.3556 | 120.4091 | 120.3359 | 0.17185 | 0.13309 | 0.003143 | 0.12502 | 0.68499 | 2.8212 | 2.9504 | 2.8594 | 2.9524 | 2.9242 | 2.7986 | 120.3479 | 120.3693 | 120.4229 | 120.3496 | 0.18558 | 0.14683 | 0.016876 | 0.13875 | 120.1623 | 120.331 | 120.2373 | 120.406
2076.9844 | 120.7443 | -0.16479 | 120.5338 | 0.68041 | 2.8396 | 2.9549 | 2.8686 | 2.9662 | 2.9288 | 2.8124 | 120.3845 | 120.4014 | 120.4595 | 120.3771 | 0.17642 | 0.13767 | -0.006014 | 0.12959 | 0.69415 | 2.8533 | 2.9687 | 2.8823 | 2.9799 | 2.9425 | 2.8261 | 120.3982 | 120.4151 | 120.4732 | 120.3909 | 0.19016 | 0.1514 | 0.007719 | 0.14333 | 120.2081 | 120.3905 | 120.2831 | 120.4655
2078.7188 | 120.7993 | -0.14648 | 120.5338 | 0.68957 | 2.8579 | 2.9778 | 2.9006 | 2.989 | 2.9517 | 2.8307 | 120.3982 | 120.4105 | 120.4732 | 120.3909 | 0.19016 | 0.13767 | 0.007721 | 0.083814 | 0.7033 | 2.8716 | 2.9916 | 2.9144 | 3.0028 | 2.9654 | 2.8444 | 120.412 | 120.4243 | 120.487 | 120.4046 | 0.20389 | 0.1514 | 0.021454 | 0.097547 | 120.2081 | 120.3905 | 120.2831 | 120.4655
2080.4062 | 120.6848 | -0.20599 | 120.5841 | 0.68957 | 2.8716 | 2.987 | 2.9006 | 3.0028 | 2.9745 | 2.849 | 120.4257 | 120.4472 | 120.5053 | 120.4275 | 0.181 | 0.13767 | -0.006014 | 0.088392 | 0.7033 | 2.8853 | 3.0007 | 2.9144 | 3.0165 | 2.9883 | 2.8627 | 120.4394 | 120.4609 | 120.519 | 120.4412 | 0.19474 | 0.1514 | 0.007719 | 0.10212 | 120.2447 | 120.4317 | 120.3243 | 120.5113
2082.1562 | 120.7214 | -0.21515 | 120.6207 | 0.70788 | 2.8853 | 3.0053 | 2.919 | 3.0119 | 2.9883 | 2.8582 | 120.4211 | 120.4426 | 120.4915 | 120.4229 | 0.18558 | 0.14225 | 0.007721 | 0.097548 | 0.72162 | 2.8991 | 3.019 | 2.9327 | 3.0257 | 3.002 | 2.8719 | 120.4349 | 120.4563 | 120.5053 | 120.4366 | 0.19931 | 0.15598 | 0.021454 | 0.11128 | 120.2355 | 120.4134 | 120.306 | 120.4838
2083.8906 | 120.7672 | -0.15106 | 120.575 | 0.71704 | 2.9082 | 3.0328 | 2.951 | 3.0486 | 3.0158 | 2.8948 | 120.4532 | 120.4746 | 120.5328 | 120.4504 | 0.181 | 0.13767 | 0.003143 | 0.088392 | 0.73077 | 2.922 | 3.0465 | 2.9647 | 3.0623 | 3.0295 | 2.9085 | 120.4669 | 120.4884 | 120.5465 | 120.4641 | 0.19474 | 0.1514 | 0.016876 | 0.10212 | 120.2722 | 120.45 | 120.3517 | 120.5296
2085.5781 | 120.7718 | -0.19226 | 120.6299 | 0.73078 | 2.9357 | 3.0511 | 2.9693 | 3.0715 | 3.0341 | 2.9177 | 120.4761 | 120.4884 | 120.5373 | 120.4687 | 0.17185 | 0.13767 | -0.001436 | 0.088392 | 0.74451 | 2.9494 | 3.0648 | 2.9831 | 3.0852 | 3.0478 | 2.9314 | 120.4898 | 120.5021 | 120.5511 | 120.4824 | 0.18558 | 0.1514 | 0.012297 | 0.10212 | 120.3042 | 120.4775 | 120.3655 | 120.5388
2087.3281 | 120.7718 | -0.17853 | 120.639 | 0.73993 | 2.9678 | 3.0969 | 3.0105 | 3.1081 | 3.0707 | 2.9451 | 120.4898 | 120.5067 | 120.5602 | 120.4824 | 0.16727 | 0.13309 | -0.001436 | 0.083814 | 0.75367 | 2.9815 | 3.1106 | 3.0243 | 3.1218 | 3.0844 | 2.9589 | 120.5035 | 120.5204 | 120.574 | 120.4962 | 0.181 | 0.14683 | 0.012297 | 0.097547 | 120.3225 | 120.4912 | 120.393 | 120.5617
2089.0156 | 120.7672 | -0.20599 | 120.6665 | 0.74909 | 2.9998 | 3.1198 | 3.0334 | 3.1264 | 3.0982 | 2.9772 | 120.4944 | 120.5067 | 120.5648 | 120.4916 | 0.17185 | 0.13767 | 0.007721 | 0.083814 | 0.76282 | 3.0135 | 3.1335 | 3.0472 | 3.1401 | 3.1119 | 2.9909 | 120.5081 | 120.5204 | 120.5785 | 120.5053 | 0.18558 | 0.1514 | 0.021454 | 0.097547 | 120.3225 | 120.4867 | 120.393 | 120.5571
2090.7656 | 120.7809 | -0.21057 | 120.6848 | 0.75825 | 3.0319 | 3.1381 | 3.0655 | 3.1584 | 3.1211 | 3.0001 | 120.5035 | 120.5158 | 120.5831 | 120.5053 | 0.181 | 0.14225 | 0.003143 | 0.10213 | 0.77198 | 3.0456 | 3.1518 | 3.0792 | 3.1722 | 3.1348 | 3.0138 | 120.5173 | 120.5296 | 120.5968 | 120.5191 | 0.19474 | 0.15598 | 0.016876 | 0.11586 | 120.3225 | 120.5004 | 120.4021 | 120.58
2092.4375 | 120.7993 | -0.20599 | 120.6985 | 0.7674 | 3.0548 | 3.1701 | 3.0884 | 3.1859 | 3.1439 | 3.0321 | 120.5127 | 120.5387 | 120.5923 | 120.5145 | 0.17642 | 0.13309 | -0.006014 | 0.083814 | 0.78114 | 3.0685 | 3.1839 | 3.1021 | 3.1996 | 3.1577 | 3.0459 | 120.5264 | 120.5525 | 120.606 | 120.5282 | 0.19016 | 0.14683 | 0.007719 | 0.097547 | 120.3363 | 120.5187 | 120.4158 | 120.5983
2094.1719 | 120.8542 | -0.21057 | 120.6985 | 0.78572 | 3.0639 | 3.1884 | 3.1113 | 3.2042 | 3.1714 | 3.0596 | 120.5127 | 120.525 | 120.5785 | 120.5099 | 0.18558 | 0.15141 | 0.044348 | 0.11128 | 0.79945 | 3.0777 | 3.2022 | 3.125 | 3.2179 | 3.1851 | 3.0733 | 120.5264 | 120.5387 | 120.5923 | 120.5236 | 0.19931 | 0.16514 | 0.058081 | 0.12502 | 120.3271 | 120.4683 | 120.393 | 120.5342
2095.9062 | 120.8908 | -0.17853 | 120.694 | 0.7903 | 3.0914 | 3.2113 | 3.125 | 3.2225 | 3.1989 | 3.0733 | 120.5539 | 120.5662 | 120.6243 | 120.542 | 0.17642 | 0.14225 | 0.007721 | 0.09297 | 0.80403 | 3.1051 | 3.2251 | 3.1387 | 3.2363 | 3.2126 | 3.0871 | 120.5676 | 120.5799 | 120.638 | 120.5557 | 0.19016 | 0.15598 | 0.021454 | 0.1067 | 120.3775 | 120.5462 | 120.4479 | 120.6166
2097.5781 | 120.932 | -0.16479 | 120.6985 | 0.80403 | 3.1051 | 3.2342 | 3.1433 | 3.2408 | 3.2035 | 3.0916 | 120.5585 | 120.5662 | 120.6243 | 120.542 | 0.17642 | 0.13767 | 0.007721 | 0.09297 | 0.81776 | 3.1189 | 3.248 | 3.157 | 3.2546 | 3.2172 | 3.1054 | 120.5722 | 120.5799 | 120.638 | 120.5557 | 0.19016 | 0.1514 | 0.021454 | 0.1067 | 120.3821 | 120.5508 | 120.4479 | 120.6166
2099.3125 | 118.1122 | -23.1949 | 94.3771 | 0.74451 | 2.9769 | 3.0877 | 3.0105 | 3.1035 | 3.0707 | 2.9543 | 118.3516 | 118.286 | 118.4634 | 118.3211 | 2.232 | 2.1291 | 2.0176 | 2.0982 | 0.75824 | 2.9907 | 3.1014 | 3.0243 | 3.1172 | 3.0844 | 2.968 | 118.3654 | 118.2997 | 118.4771 | 118.3349 | 2.2458 | 2.1429 | 2.0314 | 2.1119 | 116.1196 | 116.334 | 116.2313 | 116.4457
2101.0469 | 120.9137 | -0.16479 | 120.639 | 0.81777 | 3.1509 | 3.2663 | 3.1845 | 3.282 | 3.2538 | 3.1328 | 120.531 | 120.5387 | 120.5968 | 120.5237 | 0.17185 | 0.13767 | -0.006014 | 0.088392 | 0.8315 | 3.1646 | 3.28 | 3.1982 | 3.2958 | 3.2676 | 3.1466 | 120.5447 | 120.5525 | 120.6106 | 120.5374 | 0.18558 | 0.1514 | 0.007719 | 0.10212 | 120.3592 | 120.537 | 120.425 | 120.6029
2102.7812 | 120.9137 | -0.15106 | 120.6985 | 0.83608 | 3.1784 | 3.3075 | 3.2211 | 3.3141 | 3.2859 | 3.1557 | 120.5631 | 120.5708 | 120.6335 | 120.5557 | 0.17185 | 0.13767 | -0.006014 | 0.09297 | 0.84981 | 3.1921 | 3.3212 | 3.2349 | 3.3278 | 3.2996 | 3.1695 | 120.5768 | 120.5845 | 120.6472 | 120.5694 | 0.18558 | 0.1514 | 0.007719 | 0.1067 | 120.3912 | 120.5691 | 120.4616 | 120.6395
2104.4531 | 120.845 | -0.21057 | 120.7306 | 0.84066 | 3.2013 | 3.3304 | 3.2486 | 3.337 | 3.3133 | 3.1878 | 120.5768 | 120.5937 | 120.6518 | 120.5694 | 0.17185 | 0.13309 | 0.003143 | 0.083814 | 0.85439 | 3.215 | 3.3441 | 3.2623 | 3.3507 | 3.3271 | 3.2015 | 120.5905 | 120.6074 | 120.6655 | 120.5832 | 0.18558 | 0.14683 | 0.016876 | 0.097547 | 120.4049 | 120.5737 | 120.4799 | 120.6486
2106.2031 | 120.8496 | -0.19226 | 120.7626 | 0.86813 | 3.2288 | 3.3441 | 3.2669 | 3.369 | 3.3317 | 3.2153 | 120.5905 | 120.6028 | 120.6609 | 120.5786 | 0.17185 | 0.13767 | -0.006014 | 0.09297 | 0.88186 | 3.2425 | 3.3578 | 3.2807 | 3.3828 | 3.3454 | 3.229 | 120.6043 | 120.6166 | 120.6747 | 120.5923 | 0.18558 | 0.1514 | 0.007719 | 0.1067 | 120.4187 | 120.5965 | 120.4891 | 120.667
2107.9531 | 120.8679 | -0.18768 | 120.7626 | 0.87728 | 3.2562 | 3.3853 | 3.299 | 3.4056 | 3.3683 | 3.2427 | 120.6043 | 120.6166 | 120.6747 | 120.5878 | 0.17185 | 0.13309 | -0.006014 | 0.097548 | 0.89102 | 3.27 | 3.3991 | 3.3127 | 3.4194 | 3.382 | 3.2565 | 120.618 | 120.6303 | 120.6884 | 120.6015 | 0.18558 | 0.14683 | 0.007719 | 0.11128 | 120.4324 | 120.6103 | 120.5028 | 120.6807
2109.6406 | 120.9137 | -0.19684 | 120.7993 | 0.88644 | 3.2791 | 3.4036 | 3.3219 | 3.4148 | 3.3866 | 3.261 | 120.6226 | 120.6166 | 120.6884 | 120.6061 | 0.17642 | 0.13767 | -0.001436 | 0.083814 | 0.90017 | 3.2929 | 3.4174 | 3.3356 | 3.4285 | 3.4003 | 3.2748 | 120.6363 | 120.6303 | 120.7021 | 120.6198 | 0.19016 | 0.1514 | 0.012297 | 0.097547 | 120.4462 | 120.624 | 120.512 | 120.6898
2111.375 | 120.9549 | -0.16937 | 120.7672 | 0.8956 | 3.2974 | 3.4265 | 3.3448 | 3.4423 | 3.4049 | 3.2839 | 120.6272 | 120.6441 | 120.6976 | 120.6198 | 0.16727 | 0.13309 | -0.001436 | 0.09297 | 0.90933 | 3.3112 | 3.4403 | 3.3585 | 3.456 | 3.4186 | 3.2977 | 120.6409 | 120.6578 | 120.7113 | 120.6335 | 0.181 | 0.14683 | 0.012297 | 0.1067 | 120.4599 | 120.6286 | 120.5303 | 120.699
2113.1094 | 120.9091 | -0.20599 | 120.7901 | 0.91391 | 3.3386 | 3.4586 | 3.3722 | 3.4697 | 3.437 | 3.3251 | 120.6272 | 120.6349 | 120.693 | 120.6152 | 0.18558 | 0.14225 | 0.016878 | 0.10213 | 0.92764 | 3.3524 | 3.4723 | 3.386 | 3.4835 | 3.4507 | 3.3389 | 120.6409 | 120.6486 | 120.7067 | 120.629 | 0.19931 | 0.15598 | 0.030611 | 0.11586 | 120.4416 | 120.6103 | 120.5074 | 120.6761
2114.8594 | 121.0327 | -0.15106 | 120.7809 | 0.92307 | 3.3524 | 3.4815 | 3.386 | 3.4926 | 3.4644 | 3.3343 | 120.6501 | 120.6578 | 120.7205 | 120.6427 | 0.17185 | 0.13767 | -0.001436 | 0.088392 | 0.9368 | 3.3661 | 3.4952 | 3.3997 | 3.5064 | 3.4782 | 3.348 | 120.6638 | 120.6715 | 120.7342 | 120.6564 | 0.18558 | 0.1514 | 0.012297 | 0.10212 | 120.4782 | 120.6515 | 120.5486 | 120.7219
2116.5469 | 121.0464 | -0.15106 | 120.7764 | 0.94138 | 3.3753 | 3.5044 | 3.4272 | 3.5155 | 3.4827 | 3.3709 | 120.6546 | 120.6715 | 120.7296 | 120.6564 | 0.17642 | 0.14225 | 0.003143 | 0.09297 | 0.95512 | 3.389 | 3.5181 | 3.4409 | 3.5292 | 3.4965 | 3.3846 | 120.6684 | 120.6853 | 120.7434 | 120.6702 | 0.19016 | 0.15598 | 0.016876 | 0.1067 | 120.4782 | 120.6515 | 120.5532 | 120.7265
2118.2812 | 121.0648 | -0.15564 | 120.7809 | 0.95054 | 3.3982 | 3.5227 | 3.4455 | 3.5384 | 3.5011 | 3.3755 | 120.6684 | 120.6807 | 120.7388 | 120.661 | 0.181 | 0.12851 | -0.006014 | 0.088392 | 0.96427 | 3.4119 | 3.5364 | 3.4592 | 3.5521 | 3.5148 | 3.3892 | 120.6821 | 120.6944 | 120.7525 | 120.6748 | 0.19474 | 0.14225 | 0.007719 | 0.10212 | 120.4874 | 120.6744 | 120.5578 | 120.7448
2120.0156 | 121.0373 | -0.14648 | 120.8176 | 0.96885 | 3.4302 | 3.5639 | 3.4775 | 3.5704 | 3.5285 | 3.4167 | 120.6821 | 120.6944 | 120.7479 | 120.6748 | 0.17185 | 0.14225 | -0.001436 | 0.088392 | 0.98259 | 3.444 | 3.5776 | 3.4913 | 3.5842 | 3.5423 | 3.4304 | 120.6958 | 120.7082 | 120.7617 | 120.6885 | 0.18558 | 0.15598 | 0.012297 | 0.10212 | 120.5103 | 120.6835 | 120.5761 | 120.7494
2121.7031 | 121.1014 | -0.13275 | 120.8176 | 0.98259 | 3.4531 | 3.5776 | 3.4958 | 3.5933 | 3.5606 | 3.4487 | 120.6775 | 120.6944 | 120.7571 | 120.6793 | 0.16727 | 0.13309 | 0.003143 | 0.088392 | 0.99632 | 3.4669 | 3.5914 | 3.5096 | 3.6071 | 3.5743 | 3.4625 | 120.6913 | 120.7082 | 120.7708 | 120.6931 | 0.181 | 0.14683 | 0.016876 | 0.10212 | 120.5103 | 120.6744 | 120.5898 | 120.7539
2123.4375 | 120.9595 | -0.18768 | 120.8588 | 1.0055 | 3.4897 | 3.6188 | 3.5371 | 3.6345 | 3.5972 | 3.4808 | 120.6913 | 120.7173 | 120.7662 | 120.6931 | 0.17642 | 0.13309 | 0.003143 | 0.09297 | 1.0192 | 3.5035 | 3.6326 | 3.5508 | 3.6483 | 3.6109 | 3.4945 | 120.705 | 120.731 | 120.78 | 120.7068 | 0.19016 | 0.14683 | 0.016876 | 0.1067 | 120.5148 | 120.6881 | 120.5898 | 120.7631
2125.1719 | 120.9686 | -0.21057 | 120.8588 | 1.0146 | 3.5264 | 3.6509 | 3.5737 | 3.6712 | 3.6247 | 3.5174 | 120.7096 | 120.7265 | 120.7708 | 120.6977 | 0.17185 | 0.14225 | 0.007721 | 0.083814 | 1.0284 | 3.5401 | 3.6646 | 3.5874 | 3.6849 | 3.6384 | 3.5311 | 120.7233 | 120.7402 | 120.7846 | 120.7114 | 0.18558 | 0.15598 | 0.021454 | 0.097547 | 120.5377 | 120.7019 | 120.599 | 120.7631
2126.9219 | 120.9915 | -0.19684 | 120.8954 | 1.033 | 3.5539 | 3.6829 | 3.6057 | 3.6986 | 3.6659 | 3.5449 | 120.7187 | 120.7265 | 120.7846 | 120.7022 | 0.17642 | 0.14225 | 0.003143 | 0.088392 | 1.0467 | 3.5676 | 3.6967 | 3.6195 | 3.7124 | 3.6796 | 3.5586 | 120.7325 | 120.7402 | 120.7983 | 120.716 | 0.19016 | 0.15598 | 0.016876 | 0.10212 | 120.5423 | 120.7156 | 120.6081 | 120.7814
2128.6094 | 121.1288 | -0.15106 | 120.845 | 1.0513 | 3.5905 | 3.7287 | 3.6424 | 3.7444 | 3.7025 | 3.5861 | 120.7187 | 120.7356 | 120.7846 | 120.716 | 0.17642 | 0.13309 | 0.012299 | 0.09297 | 1.065 | 3.6042 | 3.7425 | 3.6561 | 3.7581 | 3.7162 | 3.5998 | 120.7325 | 120.7494 | 120.7983 | 120.7297 | 0.19016 | 0.14683 | 0.026032 | 0.1067 | 120.5423 | 120.7064 | 120.6081 | 120.7723
2130.3594 | 121.0144 | -0.22888 | 120.8862 | 1.0742 | 3.6225 | 3.7516 | 3.6698 | 3.7673 | 3.73 | 3.609 | 120.737 | 120.7448 | 120.8074 | 120.7205 | 0.17185 | 0.14225 | -0.001436 | 0.097548 | 1.0879 | 3.6363 | 3.7653 | 3.6836 | 3.781 | 3.7437 | 3.6227 | 120.7508 | 120.7585 | 120.8212 | 120.7343 | 0.18558 | 0.15598 | 0.012297 | 0.11128 | 120.5652 | 120.7385 | 120.6356 | 120.8089
2132.1094 | 121.1517 | -0.14648 | 120.8725 | 1.0925 | 3.6454 | 3.7745 | 3.7019 | 3.7993 | 3.7574 | 3.641 | 120.7416 | 120.7494 | 120.8212 | 120.7297 | 0.17642 | 0.14225 | -0.001436 | 0.09297 | 1.1062 | 3.6592 | 3.7882 | 3.7156 | 3.8131 | 3.7712 | 3.6548 | 120.7554 | 120.7631 | 120.8349 | 120.7434 | 0.19016 | 0.15598 | 0.012297 | 0.1067 | 120.5652 | 120.7431 | 120.6448 | 120.8226
2133.8594 | 121.0373 | -0.20142 | 120.9045 | 1.1062 | 3.6775 | 3.8111 | 3.7293 | 3.8222 | 3.7849 | 3.6685 | 120.7508 | 120.7631 | 120.8212 | 120.7389 | 0.17642 | 0.13309 | -0.001436 | 0.083814 | 1.1199 | 3.6912 | 3.8249 | 3.7431 | 3.836 | 3.7987 | 3.6822 | 120.7645 | 120.7768 | 120.8349 | 120.7526 | 0.19016 | 0.14683 | 0.012297 | 0.097547 | 120.5744 | 120.7522 | 120.6448 | 120.8226
2135.6094 | 121.1243 | -0.15564 | 120.8771 | 1.1199 | 3.705 | 3.8386 | 3.7568 | 3.8451 | 3.817 | 3.7051 | 120.7554 | 120.7723 | 120.8258 | 120.748 | 0.17642 | 0.13767 | -0.001436 | 0.097548 | 1.1337 | 3.7187 | 3.8523 | 3.7706 | 3.8589 | 3.8307 | 3.7189 | 120.7691 | 120.786 | 120.8395 | 120.7618 | 0.19016 | 0.1514 | 0.012297 | 0.11128 | 120.5789 | 120.7568 | 120.6493 | 120.8272
2137.2969 | 121.0556 | -0.20599 | 120.9137 | 1.1337 | 3.7416 | 3.8752 | 3.7889 | 3.8863 | 3.8444 | 3.728 | 120.7737 | 120.7814 | 120.8349 | 120.7572 | 0.17642 | 0.13767 | 0.003143 | 0.088392 | 1.1474 | 3.7553 | 3.889 | 3.8026 | 3.9001 | 3.8582 | 3.7417 | 120.7874 | 120.7952 | 120.8487 | 120.7709 | 0.19016 | 0.1514 | 0.016876 | 0.10212 | 120.5972 | 120.7705 | 120.6585 | 120.8318
2139.0312 | 121.1609 | -0.16479 | 120.9045 | 1.1566 | 3.7553 | 3.8844 | 3.8118 | 3.9001 | 3.8719 | 3.7417 | 120.7691 | 120.7814 | 120.8395 | 120.7663 | 0.17642 | 0.14683 | -0.001436 | 0.09297 | 1.1703 | 3.7691 | 3.8981 | 3.8255 | 3.9138 | 3.8856 | 3.7555 | 120.7828 | 120.7952 | 120.8532 | 120.7801 | 0.19016 | 0.16056 | 0.012297 | 0.1067 | 120.5927 | 120.7705 | 120.6631 | 120.8409
2140.7969 | 121.138 | -0.16937 | 120.9183 | 1.1657 | 3.7782 | 3.9073 | 3.8255 | 3.9184 | 3.8856 | 3.7601 | 120.7874 | 120.7997 | 120.8532 | 120.7663 | 0.17185 | 0.14683 | -0.006014 | 0.09297 | 1.1795 | 3.7919 | 3.921 | 3.8392 | 3.9321 | 3.8994 | 3.7738 | 120.8011 | 120.8135 | 120.867 | 120.7801 | 0.18558 | 0.16056 | 0.007719 | 0.1067 | 120.6156 | 120.7934 | 120.6814 | 120.8592
2142.4844 | 117.9474 | -22.4075 | 95.2744 | 0.60258 | 1.8643 | 1.9568 | 1.8842 | 2.0002 | 1.9581 | 1.8418 | 94.7037 | 94.7096 | 94.7708 | 94.6842 | 22.9803 | 22.9456 | 22.7577 | 22.8969 | 0.61631 | 1.878 | 1.9705 | 1.8979 | 2.0139 | 1.9719 | 1.8555 | 94.7175 | 94.7234 | 94.7845 | 94.6979 | 22.994 | 22.9593 | 22.7715 | 22.9106 | 71.7234 | 71.946 | 71.7905 | 72.013
2144.2188 | 120.8542 | -0.19684 | 120.7031 | 1.2024 | 3.8148 | 3.9393 | 3.8667 | 3.9642 | 3.9268 | 3.8104 | 120.5402 | 120.5525 | 120.6106 | 120.5328 | 0.18558 | 0.13767 | 0.003143 | 0.09297 | 1.2161 | 3.8286 | 3.9531 | 3.8804 | 3.9779 | 3.9406 | 3.8242 | 120.5539 | 120.5662 | 120.6243 | 120.5465 | 0.19931 | 0.1514 | 0.016876 | 0.1067 | 120.3546 | 120.537 | 120.425 | 120.6074
2145.9688 | 120.9869 | -0.17395 | 120.7626 | 1.2207 | 3.8606 | 3.9851 | 3.9079 | 4.0008 | 3.9681 | 3.847 | 120.6134 | 120.6303 | 120.6884 | 120.6015 | 0.17642 | 0.14683 | 0.007721 | 0.09297 | 1.2344 | 3.8744 | 3.9989 | 3.9216 | 4.0145 | 3.9818 | 3.8608 | 120.6272 | 120.644 | 120.7021 | 120.6152 | 0.19016 | 0.16056 | 0.021454 | 0.1067 | 120.437 | 120.6057 | 120.512 | 120.6807
2147.6562 | 121.0007 | -0.17853 | 120.7809 | 1.239 | 3.8835 | 4.0034 | 3.9308 | 4.0191 | 3.9864 | 3.8699 | 120.6455 | 120.6624 | 120.7205 | 120.6381 | 0.17642 | 0.14683 | -0.001436 | 0.09297 | 1.2527 | 3.8973 | 4.0172 | 3.9445 | 4.0328 | 4.0001 | 3.8837 | 120.6592 | 120.6761 | 120.7342 | 120.6519 | 0.19016 | 0.16056 | 0.012297 | 0.1067 | 120.469 | 120.6469 | 120.544 | 120.7219
2149.3906 | 121.0648 | -0.15564 | 120.813 | 1.2573 | 3.911 | 4.0401 | 3.9629 | 4.0557 | 4.0093 | 3.9066 | 120.6821 | 120.6944 | 120.7434 | 120.661 | 0.181 | 0.14225 | 0.003143 | 0.097548 | 1.271 | 3.9247 | 4.0538 | 3.9766 | 4.0694 | 4.023 | 3.9203 | 120.6958 | 120.7082 | 120.7571 | 120.6748 | 0.19474 | 0.15598 | 0.016876 | 0.11128 | 120.5011 | 120.679 | 120.5623 | 120.7402
2151.125 | 121.0144 | -0.20599 | 120.8817 | 1.2802 | 3.9293 | 4.063 | 3.9857 | 4.0832 | 4.0413 | 3.9249 | 120.7004 | 120.7127 | 120.7754 | 120.6885 | 0.181 | 0.14225 | 0.003143 | 0.09297 | 1.2939 | 3.943 | 4.0767 | 3.9995 | 4.0969 | 4.055 | 3.9386 | 120.7141 | 120.7265 | 120.7891 | 120.7022 | 0.19474 | 0.15598 | 0.016876 | 0.1067 | 120.5194 | 120.6973 | 120.5944 | 120.7723
2152.875 | 121.0373 | -0.20142 | 120.8817 | 1.3031 | 3.9614 | 4.0904 | 4.0132 | 4.1061 | 4.0734 | 3.9615 | 120.7142 | 120.7265 | 120.7846 | 120.7022 | 0.18558 | 0.14225 | 0.003143 | 0.097548 | 1.3168 | 3.9751 | 4.1042 | 4.0269 | 4.1198 | 4.0871 | 3.9752 | 120.7279 | 120.7402 | 120.7983 | 120.716 | 0.19931 | 0.15598 | 0.016876 | 0.11128 | 120.5286 | 120.711 | 120.599 | 120.7814
2154.5625 | 121.0785 | -0.19226 | 120.8679 | 1.3168 | 3.998 | 4.1271 | 4.0498 | 4.1335 | 4.1146 | 3.9935 | 120.7233 | 120.7402 | 120.7937 | 120.7114 | 0.19016 | 0.15141 | 0.007721 | 0.097548 | 1.3305 | 4.0117 | 4.1408 | 4.0636 | 4.1473 | 4.1283 | 4.0073 | 120.737 | 120.7539 | 120.8074 | 120.7251 | 0.20389 | 0.16514 | 0.021454 | 0.11128 | 120.5331 | 120.7156 | 120.6036 | 120.786
2156.3125 | 120.6024 | -1.7761 | 118.84 | 1.2893 | 3.8698 | 3.9943 | 3.9262 | 4.0054 | 3.9772 | 3.8699 | 118.924 | 118.9224 | 118.9944 | 118.9027 | 1.7284 | 1.6896 | 1.6056 | 1.677 | 1.3031 | 3.8835 | 4.008 | 3.94 | 4.0191 | 3.9909 | 3.8837 | 118.9377 | 118.9361 | 119.0082 | 118.9164 | 1.7422 | 1.7034 | 1.6193 | 1.6908 | 117.1955 | 117.3184 | 117.266 | 117.3889
2158.0469 | 120.6894 | -0.16022 | 120.369 | 1.358 | 4.0255 | 4.1728 | 4.0911 | 4.1839 | 4.1466 | 4.0347 | 120.2746 | 120.232 | 120.2901 | 120.2031 | 0.20847 | 0.1743 | 0.030613 | 0.16622 | 1.3717 | 4.0392 | 4.1866 | 4.1048 | 4.1976 | 4.1603 | 4.0485 | 120.2883 | 120.2457 | 120.3038 | 120.2169 | 0.2222 | 0.18803 | 0.044346 | 0.17995 | 120.0661 | 120.244 | 120.0816 | 120.2595
2159.7969 | 120.7031 | -0.20142 | 120.5612 | 1.3672 | 4.0713 | 4.2141 | 4.1277 | 4.2205 | 4.1878 | 4.0714 | 120.412 | 120.4334 | 120.4824 | 120.4 | 0.181 | 0.14225 | 0.012299 | 0.088392 | 1.3809 | 4.085 | 4.2278 | 4.1414 | 4.2343 | 4.2016 | 4.0851 | 120.4257 | 120.4472 | 120.4961 | 120.4138 | 0.19474 | 0.15598 | 0.026032 | 0.10212 | 120.231 | 120.3997 | 120.3014 | 120.4701
2161.4844 | 120.8038 | -0.20142 | 120.6116 | 1.3946 | 4.0987 | 4.2324 | 4.1506 | 4.2434 | 4.2107 | 4.0943 | 120.4761 | 120.4792 | 120.5373 | 120.455 | 0.18558 | 0.14683 | 0.003143 | 0.10213 | 1.4084 | 4.1125 | 4.2461 | 4.1643 | 4.2571 | 4.2244 | 4.108 | 120.4898 | 120.4929 | 120.5511 | 120.4687 | 0.19931 | 0.16056 | 0.016876 | 0.11586 | 120.2905 | 120.4729 | 120.3517 | 120.5342
2163.2188 | 120.8679 | -0.19226 | 120.6802 | 1.413 | 4.117 | 4.2461 | 4.1735 | 4.2663 | 4.229 | 4.1126 | 120.5264 | 120.5433 | 120.5968 | 120.5099 | 0.17642 | 0.13767 | 0.003143 | 0.088392 | 1.4267 | 4.1308 | 4.2598 | 4.1872 | 4.28 | 4.2428 | 4.1263 | 120.5402 | 120.5571 | 120.6106 | 120.5236 | 0.19016 | 0.1514 | 0.016876 | 0.10212 | 120.35 | 120.5233 | 120.4204 | 120.5937
2164.9531 | 120.8862 | -0.17853 | 120.7031 | 1.4267 | 4.1491 | 4.2873 | 4.2101 | 4.3029 | 4.2611 | 4.1446 | 120.5585 | 120.5754 | 120.6289 | 120.5465 | 0.17642 | 0.14225 | 0.003143 | 0.09297 | 1.4404 | 4.1628 | 4.301 | 4.2238 | 4.3167 | 4.2748 | 4.1584 | 120.5722 | 120.5891 | 120.6426 | 120.5603 | 0.19016 | 0.15598 | 0.016876 | 0.1067 | 120.3821 | 120.5553 | 120.4525 | 120.6258
2166.7031 | 120.8588 | -0.20599 | 120.7581 | 1.4633 | 4.1949 | 4.3239 | 4.2421 | 4.335 | 4.3023 | 4.1812 | 120.586 | 120.5937 | 120.6564 | 120.5694 | 0.17642 | 0.14225 | -0.001436 | 0.09297 | 1.4771 | 4.2086 | 4.3377 | 4.2559 | 4.3487 | 4.316 | 4.195 | 120.5997 | 120.6074 | 120.6701 | 120.5832 | 0.19016 | 0.15598 | 0.012297 | 0.1067 | 120.4095 | 120.5874 | 120.4799 | 120.6578
2168.4531 | 120.8954 | -0.20599 | 120.7672 | 1.4725 | 4.2132 | 4.3423 | 4.2696 | 4.3624 | 4.3252 | 4.2087 | 120.5997 | 120.6166 | 120.6701 | 120.5786 | 0.18558 | 0.15141 | 0.012299 | 0.097548 | 1.4862 | 4.2269 | 4.356 | 4.2833 | 4.3762 | 4.3389 | 4.2225 | 120.6134 | 120.6303 | 120.6838 | 120.5923 | 0.19931 | 0.16514 | 0.026032 | 0.11128 | 120.4141 | 120.5874 | 120.4845 | 120.6578
2170.125 | 121.0236 | -0.15564 | 120.7581 | 1.5045 | 4.2544 | 4.3926 | 4.3108 | 4.3991 | 4.3572 | 4.2499 | 120.6272 | 120.6395 | 120.693 | 120.6152 | 0.18558 | 0.14683 | 0.003143 | 0.09297 | 1.5183 | 4.2681 | 4.4063 | 4.3246 | 4.4128 | 4.371 | 4.2637 | 120.6409 | 120.6532 | 120.7067 | 120.629 | 0.19931 | 0.16056 | 0.016876 | 0.1067 | 120.4416 | 120.624 | 120.5074 | 120.6898
2171.875 | 120.9549 | -0.21057 | 120.8084 | 1.532 | 4.3002 | 4.4384 | 4.352 | 4.454 | 4.4122 | 4.2957 | 120.6455 | 120.6669 | 120.7113 | 120.6381 | 0.19016 | 0.14683 | 0.003143 | 0.097548 | 1.5457 | 4.3139 | 4.4521 | 4.3658 | 4.4677 | 4.4259 | 4.3094 | 120.6592 | 120.6807 | 120.725 | 120.6519 | 0.20389 | 0.16056 | 0.016876 | 0.11128 | 120.4553 | 120.6423 | 120.5211 | 120.7082
2173.5469 | 120.932 | -0.21973 | 120.813 | 1.5549 | 4.3368 | 4.4659 | 4.3887 | 4.486 | 4.4396 | 4.3369 | 120.6638 | 120.6715 | 120.725 | 120.6519 | 0.18558 | 0.14683 | 0.007721 | 0.097548 | 1.5686 | 4.3506 | 4.4796 | 4.4024 | 4.4998 | 4.4534 | 4.3506 | 120.6775 | 120.6853 | 120.7388 | 120.6656 | 0.19931 | 0.16056 | 0.021454 | 0.11128 | 120.4782 | 120.6561 | 120.5395 | 120.7173
2175.2812 | 121.0739 | -0.16022 | 120.8038 | 1.5778 | 4.3735 | 4.5162 | 4.4344 | 4.5318 | 4.49 | 4.3735 | 120.6729 | 120.6898 | 120.7388 | 120.6656 | 0.17185 | 0.13767 | 0.007721 | 0.088392 | 1.5915 | 4.3872 | 4.53 | 4.4482 | 4.5456 | 4.5037 | 4.3873 | 120.6867 | 120.7036 | 120.7525 | 120.6793 | 0.18558 | 0.1514 | 0.021454 | 0.10212 | 120.5011 | 120.6652 | 120.5669 | 120.7311
2177.0312 | 121.1243 | -0.16479 | 120.8176 | 1.6007 | 4.4009 | 4.5391 | 4.4573 | 4.5456 | 4.5175 | 4.3964 | 120.6821 | 120.699 | 120.7434 | 120.6793 | 0.18558 | 0.14683 | -0.006014 | 0.10213 | 1.6144 | 4.4147 | 4.5529 | 4.4711 | 4.5593 | 4.5312 | 4.4102 | 120.6958 | 120.7127 | 120.7571 | 120.6931 | 0.19931 | 0.16056 | 0.007719 | 0.11586 | 120.4965 | 120.6881 | 120.5578 | 120.7494
2178.7812 | 121.0739 | -0.1831 | 120.8084 | 1.6236 | 4.4376 | 4.5758 | 4.494 | 4.5913 | 4.5495 | 4.4376 | 120.7004 | 120.7127 | 120.7617 | 120.6839 | 0.19016 | 0.15141 | 0.016878 | 0.10213 | 1.6373 | 4.4513 | 4.5895 | 4.5077 | 4.6051 | 4.5632 | 4.4514 | 120.7141 | 120.7265 | 120.7754 | 120.6976 | 0.20389 | 0.16514 | 0.030611 | 0.11586 | 120.5103 | 120.6835 | 120.5715 | 120.7448
2180.4688 | 120.9824 | -0.21973 | 120.8771 | 1.6602 | 4.4788 | 4.6032 | 4.5306 | 4.6325 | 4.5953 | 4.4743 | 120.6958 | 120.7082 | 120.7571 | 120.6839 | 0.19931 | 0.15598 | 0.016878 | 0.11586 | 1.6739 | 4.4925 | 4.617 | 4.5443 | 4.6463 | 4.609 | 4.488 | 120.7096 | 120.7219 | 120.7708 | 120.6976 | 0.21305 | 0.16972 | 0.030611 | 0.12959 | 120.4965 | 120.679 | 120.5578 | 120.7402
2182.2188 | 120.9869 | -0.21515 | 120.8633 | 1.6831 | 4.5108 | 4.6536 | 4.5764 | 4.6646 | 4.6319 | 4.52 | 120.7187 | 120.7402 | 120.7937 | 120.7068 | 0.18558 | 0.16056 | 0.007721 | 0.10213 | 1.6968 | 4.5246 | 4.6673 | 4.5901 | 4.6783 | 4.6457 | 4.5338 | 120.7325 | 120.7539 | 120.8074 | 120.7205 | 0.19931 | 0.1743 | 0.021454 | 0.11586 | 120.5331 | 120.711 | 120.6081 | 120.786
2183.9688 | 121.0464 | -0.1831 | 120.9183 | 1.6968 | 4.5291 | 4.6673 | 4.5901 | 4.6875 | 4.6457 | 4.5338 | 120.7096 | 120.7219 | 120.78 | 120.6977 | 0.19016 | 0.16514 | 0.021456 | 0.11586 | 1.7105 | 4.5429 | 4.6811 | 4.6038 | 4.7012 | 4.6594 | 4.5475 | 120.7233 | 120.7356 | 120.7937 | 120.7114 | 0.20389 | 0.17887 | 0.035189 | 0.12959 | 120.5194 | 120.6881 | 120.5898 | 120.7585
2185.7188 | 121.0876 | -0.17853 | 120.8862 | 1.7197 | 4.5566 | 4.6994 | 4.6176 | 4.7104 | 4.6731 | 4.5521 | 120.7325 | 120.7494 | 120.7937 | 120.716 | 0.16269 | 0.15141 | 0.035191 | 0.11586 | 1.7334 | 4.5703 | 4.7131 | 4.6313 | 4.7241 | 4.6869 | 4.5658 | 120.7462 | 120.7631 | 120.8074 | 120.7297 | 0.17642 | 0.16514 | 0.048924 | 0.12959 | 120.5698 | 120.6973 | 120.631 | 120.7585
2187.4062 | 120.5795 | -0.21057 | 120.4788 | 1.7106 | 4.5978 | 4.7269 | 4.6542 | 4.747 | 4.7052 | 4.6024 | 120.2151 | 120.232 | 120.2764 | 120.1985 | 0.22678 | 0.19719 | 0.044348 | 0.14791 | 1.7243 | 4.6116 | 4.7406 | 4.6679 | 4.7607 | 4.7189 | 4.6162 | 120.2288 | 120.2457 | 120.2901 | 120.2123 | 0.24052 | 0.21092 | 0.058081 | 0.16164 | 119.9883 | 120.1707 | 120.0496 | 120.232
2189.1406 | 120.9183 | -0.16479 | 120.6528 | 1.7334 | 4.6207 | 4.7589 | 4.6908 | 4.779 | 4.7418 | 4.6345 | 120.4486 | 120.4655 | 120.5144 | 120.4412 | 0.19931 | 0.19719 | 0.085554 | 0.1708 | 1.7472 | 4.6344 | 4.7726 | 4.7046 | 4.7928 | 4.7555 | 4.6482 | 120.4623 | 120.4792 | 120.5282 | 120.455 | 0.21305 | 0.21092 | 0.099287 | 0.18453 | 120.2493 | 120.363 | 120.3151 | 120.4289
2190.875 | 120.8405 | -0.16479 | 120.6024 | 1.7472 | 4.6207 | 4.7543 | 4.6817 | 4.7745 | 4.7372 | 4.6253 | 120.0457 | 120.0854 | 120.1115 | 120.0383 | 0.50148 | 0.47645 | 0.40146 | 0.4638 | 1.7609 | 4.6344 | 4.7681 | 4.6954 | 4.7882 | 4.751 | 4.6391 | 120.0594 | 120.0992 | 120.1253 | 120.052 | 0.51521 | 0.49018 | 0.41519 | 0.47753 | 119.5442 | 119.6442 | 119.6101 | 119.7101
2192.5469 | 120.8588 | -0.20599 | 120.7489 | 1.7792 | 4.6986 | 4.8322 | 4.7504 | 4.8477 | 4.8105 | 4.7032 | 120.5814 | 120.5983 | 120.6472 | 120.5694 | 0.18558 | 0.14225 | 0.007721 | 0.14333 | 1.793 | 4.7123 | 4.8459 | 4.7641 | 4.8614 | 4.8242 | 4.7169 | 120.5951 | 120.612 | 120.6609 | 120.5832 | 0.19931 | 0.15598 | 0.021454 | 0.15706 | 120.3958 | 120.5737 | 120.4616 | 120.6395
2194.2812 | 120.9045 | -0.21057 | 120.7855 | 1.8067 | 4.7169 | 4.8642 | 4.7778 | 4.8706 | 4.8334 | 4.7306 | 120.618 | 120.6303 | 120.6838 | 120.6015 | 0.18558 | 0.14683 | 0.012299 | 0.10213 | 1.8204 | 4.7306 | 4.8779 | 4.7916 | 4.8843 | 4.8471 | 4.7444 | 120.6317 | 120.644 | 120.6976 | 120.6152 | 0.19931 | 0.16056 | 0.026032 | 0.11586 | 120.4324 | 120.6057 | 120.4983 | 120.6715
2195.9531 | 120.9961 | -0.17853 | 120.7901 | 1.8433 | 4.7627 | 4.9008 | 4.8145 | 4.9118 | 4.8746 | 4.7627 | 120.6455 | 120.6578 | 120.7159 | 120.629 | 0.18558 | 0.14683 | 0.007721 | 0.097548 | 1.8571 | 4.7764 | 4.9146 | 4.8282 | 4.9255 | 4.8883 | 4.7764 | 120.6592 | 120.6715 | 120.7296 | 120.6427 | 0.19931 | 0.16056 | 0.021454 | 0.11128 | 120.4599 | 120.6378 | 120.5303 | 120.7082
2197.7031 | 120.9732 | -0.19684 | 120.8542 | 1.8616 | 4.8039 | 4.942 | 4.8648 | 4.953 | 4.9158 | 4.813 | 120.6684 | 120.6715 | 120.7296 | 120.6564 | 0.18558 | 0.14225 | 0.007721 | 0.097548 | 1.8754 | 4.8176 | 4.9558 | 4.8785 | 4.9667 | 4.9295 | 4.8268 | 120.6821 | 120.6853 | 120.7434 | 120.6702 | 0.19931 | 0.15598 | 0.021454 | 0.11128 | 120.4828 | 120.6606 | 120.544 | 120.7219
2199.4531 | 120.9686 | -0.21515 | 120.8359 | 1.8891 | 4.8359 | 4.9741 | 4.9014 | 4.9896 | 4.9524 | 4.8451 | 120.6913 | 120.699 | 120.7479 | 120.6748 | 0.18558 | 0.15141 | 0.012299 | 0.10213 | 1.9028 | 4.8497 | 4.9878 | 4.9152 | 5.0033 | 4.9661 | 4.8588 | 120.705 | 120.7127 | 120.7617 | 120.6885 | 0.19931 | 0.16514 | 0.026032 | 0.11586 | 120.5057 | 120.679 | 120.5623 | 120.7356
2201.1875 | 121.0464 | -0.16937 | 120.8588 | 1.9212 | 4.8634 | 5.0016 | 4.9243 | 5.0171 | 4.9753 | 4.8634 | 120.7004 | 120.7127 | 120.7571 | 120.6839 | 0.18558 | 0.14683 | 0.007721 | 0.1067 | 1.9349 | 4.8771 | 5.0153 | 4.9381 | 5.0308 | 4.989 | 4.8771 | 120.7141 | 120.7265 | 120.7708 | 120.6976 | 0.19931 | 0.16056 | 0.021454 | 0.12044 | 120.5148 | 120.6927 | 120.5715 | 120.7494
2202.875 | 121.0419 | -0.20599 | 120.8588 | 1.9395 | 4.8817 | 5.0245 | 4.9381 | 5.04 | 4.9982 | 4.8863 | 120.7142 | 120.731 | 120.78 | 120.7114 | 0.18558 | 0.15141 | 0.007721 | 0.097548 | 1.9532 | 4.8954 | 5.0382 | 4.9518 | 5.0537 | 5.0119 | 4.9 | 120.7279 | 120.7448 | 120.7937 | 120.7251 | 0.19931 | 0.16514 | 0.021454 | 0.11128 | 120.5286 | 120.7064 | 120.5944 | 120.7723
2204.6094 | 121.0602 | -0.20142 | 120.9091 | 1.9578 | 4.9092 | 5.0474 | 4.961 | 5.0583 | 5.0211 | 4.9092 | 120.7325 | 120.7402 | 120.7891 | 120.716 | 0.181 | 0.15598 | 0.003143 | 0.09297 | 1.9715 | 4.9229 | 5.0611 | 4.9747 | 5.072 | 5.0348 | 4.9229 | 120.7462 | 120.7539 | 120.8029 | 120.7297 | 0.19474 | 0.16972 | 0.016876 | 0.1067 | 120.5515 | 120.7293 | 120.6081 | 120.786
2206.3438 | 121.0648 | -0.19226 | 120.845 | 1.9898 | 4.9504 | 5.0931 | 5.0113 | 5.1041 | 5.0623 | 4.9504 | 120.7416 | 120.7494 | 120.8074 | 120.7343 | 0.181 | 0.15141 | 0.003143 | 0.10213 | 2.0036 | 4.9641 | 5.1069 | 5.0251 | 5.1178 | 5.076 | 4.9641 | 120.7554 | 120.7631 | 120.8212 | 120.748 | 0.19474 | 0.16514 | 0.016876 | 0.11586 | 120.5606 | 120.7385 | 120.6264 | 120.8043
2208.0938 | 121.0098 | -0.20599 | 120.9183 | 2.0265 | 4.9824 | 5.1252 | 5.0434 | 5.1407 | 5.0898 | 4.987 | 120.7462 | 120.7631 | 120.8166 | 120.7434 | 0.19016 | 0.14683 | 0.012299 | 0.10213 | 2.0402 | 4.9962 | 5.1389 | 5.0571 | 5.1544 | 5.1035 | 5.0007 | 120.7599 | 120.7768 | 120.8303 | 120.7572 | 0.20389 | 0.16056 | 0.026032 | 0.11586 | 120.556 | 120.7339 | 120.6264 | 120.8043
2209.7812 | 121.0556 | -0.19684 | 120.9137 | 2.0494 | 5.0374 | 5.1801 | 5.0892 | 5.1865 | 5.1447 | 5.0419 | 120.7645 | 120.7768 | 120.8258 | 120.7434 | 0.18558 | 0.14683 | 0.003143 | 0.097548 | 2.0631 | 5.0511 | 5.1939 | 5.1029 | 5.2002 | 5.1584 | 5.0557 | 120.7782 | 120.7906 | 120.8395 | 120.7572 | 0.19931 | 0.16056 | 0.016876 | 0.11128 | 120.5789 | 120.7614 | 120.6402 | 120.8226
2211.5312 | 121.1655 | -0.16937 | 120.8817 | 2.0722 | 5.0557 | 5.1985 | 5.1121 | 5.2048 | 5.1768 | 5.0648 | 120.7737 | 120.786 | 120.8349 | 120.7618 | 0.17642 | 0.14683 | 0.007721 | 0.097548 | 2.086 | 5.0694 | 5.2122 | 5.1258 | 5.2185 | 5.1905 | 5.0786 | 120.7874 | 120.7997 | 120.8487 | 120.7755 | 0.19016 | 0.16056 | 0.021454 | 0.11128 | 120.5972 | 120.7659 | 120.6585 | 120.8272
2213.2812 | 121.1426 | -0.16937 | 120.9045 | 2.0997 | 5.0832 | 5.2305 | 5.1395 | 5.2368 | 5.2042 | 5.0969 | 120.7828 | 120.7952 | 120.8487 | 120.7755 | 0.181 | 0.14683 | 0.003143 | 0.097548 | 2.1134 | 5.0969 | 5.2442 | 5.1533 | 5.2506 | 5.218 | 5.1106 | 120.7966 | 120.8089 | 120.8624 | 120.7892 | 0.19474 | 0.16056 | 0.016876 | 0.11128 | 120.6018 | 120.7797 | 120.6676 | 120.8455
2214.9531 | 121.1426 | -0.19226 | 120.932 | 2.1318 | 5.1152 | 5.2534 | 5.1807 | 5.2643 | 5.2271 | 5.1198 | 120.792 | 120.8043 | 120.8578 | 120.7801 | 0.181 | 0.14225 | 0.003143 | 0.09297 | 2.1455 | 5.129 | 5.2671 | 5.1945 | 5.278 | 5.2408 | 5.1335 | 120.8057 | 120.818 | 120.8715 | 120.7938 | 0.19474 | 0.15598 | 0.016876 | 0.1067 | 120.611 | 120.7888 | 120.6768 | 120.8547
2216.7031 | 121.0831 | -0.21973 | 120.9549 | 2.1592 | 5.1564 | 5.2946 | 5.2174 | 5.3147 | 5.2729 | 5.161 | 120.8011 | 120.8089 | 120.867 | 120.7892 | 0.181 | 0.14225 | 0.003143 | 0.097548 | 2.173 | 5.1702 | 5.3083 | 5.2311 | 5.3284 | 5.2866 | 5.1747 | 120.8149 | 120.8226 | 120.8807 | 120.803 | 0.19474 | 0.15598 | 0.016876 | 0.11128 | 120.6201 | 120.798 | 120.686 | 120.8638
2218.3906 | 121.1609 | -0.1831 | 120.9503 | 2.1959 | 5.2022 | 5.345 | 5.2723 | 5.3559 | 5.3187 | 5.2113 | 120.8057 | 120.8272 | 120.8761 | 120.7938 | 0.181 | 0.14225 | 0.007721 | 0.10213 | 2.2096 | 5.216 | 5.3587 | 5.286 | 5.3696 | 5.3324 | 5.2251 | 120.8195 | 120.8409 | 120.8899 | 120.8075 | 0.19474 | 0.15598 | 0.021454 | 0.11586 | 120.6247 | 120.798 | 120.6951 | 120.8684
2220.125 | 121.2067 | -0.15106 | 120.9549 | 2.2188 | 5.2343 | 5.3816 | 5.2998 | 5.3925 | 5.3416 | 5.2434 | 120.8195 | 120.8318 | 120.8807 | 120.7984 | 0.18558 | 0.14683 | 0.007721 | 0.083814 | 2.2325 | 5.248 | 5.3953 | 5.3135 | 5.4062 | 5.3553 | 5.2571 | 120.8332 | 120.8455 | 120.8944 | 120.8121 | 0.19931 | 0.16056 | 0.021454 | 0.097547 | 120.6339 | 120.8117 | 120.6951 | 120.873
2221.8594 | 121.2021 | -0.19684 | 120.9503 | 2.2508 | 5.2755 | 5.4182 | 5.3364 | 5.4291 | 5.3874 | 5.28 | 120.824 | 120.8364 | 120.8899 | 120.8076 | 0.181 | 0.15141 | 0.003143 | 0.097548 | 2.2645 | 5.2892 | 5.432 | 5.3501 | 5.4428 | 5.4011 | 5.2937 | 120.8378 | 120.8501 | 120.9036 | 120.8213 | 0.19474 | 0.16514 | 0.016876 | 0.11128 | 120.643 | 120.8209 | 120.7089 | 120.8867
2223.5938 | 121.2433 | -0.15106 | 120.9457 | 2.2645 | 5.2892 | 5.4228 | 5.3456 | 5.4337 | 5.3919 | 5.2937 | 120.824 | 120.8409 | 120.8853 | 120.8167 | 0.18558 | 0.14683 | 0.003143 | 0.10213 | 2.2783 | 5.303 | 5.4365 | 5.3593 | 5.4474 | 5.4057 | 5.3075 | 120.8378 | 120.8547 | 120.899 | 120.8304 | 0.19931 | 0.16056 | 0.016876 | 0.11586 | 120.6385 | 120.8209 | 120.6997 | 120.8821
2225.2656 | 121.2479 | -0.17853 | 120.9412 | 2.2874 | 5.3121 | 5.4503 | 5.3776 | 5.4657 | 5.424 | 5.3212 | 120.8423 | 120.8501 | 120.899 | 120.8213 | 0.18558 | 0.14225 | 0.012299 | 0.10213 | 2.3012 | 5.3258 | 5.464 | 5.3913 | 5.4795 | 5.4377 | 5.3349 | 120.8561 | 120.8638 | 120.9127 | 120.835 | 0.19931 | 0.15598 | 0.026032 | 0.11586 | 120.6568 | 120.83 | 120.7134 | 120.8867
2227 | 121.2067 | -0.17853 | 120.9641 | 2.3195 | 5.3442 | 5.4777 | 5.3959 | 5.4978 | 5.4515 | 5.3487 | 120.8469 | 120.8638 | 120.9082 | 120.8304 | 0.19016 | 0.14683 | 0.003143 | 0.097548 | 2.3332 | 5.3579 | 5.4915 | 5.4097 | 5.5115 | 5.4652 | 5.3624 | 120.8607 | 120.8776 | 120.9219 | 120.8442 | 0.20389 | 0.16056 | 0.016876 | 0.11128 | 120.6568 | 120.8438 | 120.718 | 120.905
2228.6875 | 121.1792 | -0.20142 | 120.9915 | 2.3607 | 5.3716 | 5.5052 | 5.428 | 5.5207 | 5.4789 | 5.3853 | 120.8607 | 120.8684 | 120.9219 | 120.8533 | 0.18558 | 0.14225 | -0.006014 | 0.088392 | 2.3744 | 5.3854 | 5.5189 | 5.4417 | 5.5344 | 5.4927 | 5.399 | 120.8744 | 120.8821 | 120.9356 | 120.8671 | 0.19931 | 0.15598 | 0.007719 | 0.10212 | 120.6751 | 120.8667 | 120.7363 | 120.9279
2230.4375 | 121.1472 | -0.18768 | 121.019 | 2.379 | 5.3945 | 5.5418 | 5.4554 | 5.5481 | 5.511 | 5.4036 | 120.8652 | 120.8776 | 120.9265 | 120.8488 | 0.181 | 0.14683 | 0.003143 | 0.088392 | 2.3927 | 5.4083 | 5.5556 | 5.4692 | 5.5619 | 5.5247 | 5.4174 | 120.879 | 120.8913 | 120.9402 | 120.8625 | 0.19474 | 0.16056 | 0.016876 | 0.10212 | 120.6842 | 120.8621 | 120.7455 | 120.9233
2232.1875 | 121.2296 | -0.15564 | 120.9961 | 2.4156 | 5.4312 | 5.5739 | 5.5012 | 5.5893 | 5.5384 | 5.4357 | 120.8698 | 120.8913 | 120.9402 | 120.8625 | 0.17185 | 0.14225 | 0.007721 | 0.09297 | 2.4294 | 5.4449 | 5.5876 | 5.515 | 5.6031 | 5.5522 | 5.4494 | 120.8836 | 120.905 | 120.954 | 120.8762 | 0.18558 | 0.15598 | 0.021454 | 0.1067 | 120.698 | 120.8621 | 120.7684 | 120.9325
2233.875 | 121.1472 | -0.21057 | 121.0236 | 2.4339 | 5.4586 | 5.5922 | 5.5241 | 5.6168 | 5.5751 | 5.4631 | 120.8881 | 120.9005 | 120.9494 | 120.8717 | 0.17642 | 0.14683 | 0.007721 | 0.097548 | 2.4477 | 5.4724 | 5.6059 | 5.5379 | 5.6305 | 5.5888 | 5.4769 | 120.9019 | 120.9142 | 120.9631 | 120.8854 | 0.19016 | 0.16056 | 0.021454 | 0.11128 | 120.7117 | 120.8804 | 120.773 | 120.9417
2235.6094 | 121.3028 | -0.16022 | 121.0327 | 2.4614 | 5.4953 | 5.638 | 5.5562 | 5.6488 | 5.6071 | 5.4998 | 120.8881 | 120.905 | 120.9494 | 120.8717 | 0.181 | 0.13767 | 0.007721 | 0.09297 | 2.4751 | 5.509 | 5.6517 | 5.5699 | 5.6626 | 5.6209 | 5.5135 | 120.9019 | 120.9188 | 120.9631 | 120.8854 | 0.19474 | 0.1514 | 0.021454 | 0.1067 | 120.7071 | 120.8804 | 120.7684 | 120.9417
2237.2969 | 121.2936 | -0.14191 | 121.019 | 2.4843 | 5.5182 | 5.6517 | 5.5836 | 5.6717 | 5.6254 | 5.5227 | 120.9019 | 120.9142 | 120.9631 | 120.8808 | 0.17642 | 0.13767 | 0.003143 | 0.097548 | 2.498 | 5.5319 | 5.6655 | 5.5974 | 5.6855 | 5.6392 | 5.5364 | 120.9156 | 120.9279 | 120.9768 | 120.8945 | 0.19016 | 0.1514 | 0.016876 | 0.11128 | 120.7254 | 120.8987 | 120.7867 | 120.96
2239.0469 | 121.2708 | -0.16479 | 121.019 | 2.5301 | 5.564 | 5.7067 | 5.6294 | 5.7129 | 5.6804 | 5.5684 | 120.9064 | 120.9188 | 120.9631 | 120.89 | 0.17642 | 0.15598 | 0.007721 | 0.10213 | 2.5438 | 5.5777 | 5.7204 | 5.6432 | 5.7267 | 5.6941 | 5.5822 | 120.9202 | 120.9325 | 120.9768 | 120.9037 | 0.19016 | 0.16972 | 0.021454 | 0.11586 | 120.73 | 120.8987 | 120.7867 | 120.9554
2240.7969 | 121.2158 | -0.1831 | 121.051 | 2.553 | 5.5731 | 5.7204 | 5.6432 | 5.7358 | 5.6987 | 5.5959 | 120.9202 | 120.9371 | 120.9768 | 120.9037 | 0.17642 | 0.14225 | -0.001436 | 0.097548 | 2.5667 | 5.5868 | 5.7341 | 5.6569 | 5.7496 | 5.7124 | 5.6096 | 120.9339 | 120.9508 | 120.9906 | 120.9174 | 0.19016 | 0.15598 | 0.012297 | 0.11128 | 120.7438 | 120.9216 | 120.8004 | 120.9783
2242.5469 | 121.3486 | -0.15564 | 121.0281 | 2.5804 | 5.6418 | 5.7799 | 5.7027 | 5.7862 | 5.7445 | 5.6417 | 120.9248 | 120.9325 | 120.9768 | 120.9083 | 0.181 | 0.13767 | 0.003143 | 0.088392 | 2.5942 | 5.6555 | 5.7937 | 5.7164 | 5.7999 | 5.7582 | 5.6554 | 120.9385 | 120.9463 | 120.9906 | 120.922 | 0.19474 | 0.1514 | 0.016876 | 0.10212 | 120.7438 | 120.9216 | 120.7958 | 120.9737
2244.2969 | 121.2296 | -0.20142 | 121.0968 | 2.6262 | 5.6693 | 5.8074 | 5.7393 | 5.8182 | 5.7811 | 5.6783 | 120.9293 | 120.9371 | 120.9997 | 120.9174 | 0.181 | 0.14683 | 0.003143 | 0.09297 | 2.64 | 5.683 | 5.8211 | 5.753 | 5.832 | 5.7948 | 5.692 | 120.9431 | 120.9508 | 121.0135 | 120.9312 | 0.19474 | 0.16056 | 0.016876 | 0.1067 | 120.7483 | 120.9262 | 120.8187 | 120.9966
2245.9844 | 121.3257 | -0.15564 | 121.0419 | 2.6583 | 5.7105 | 5.8532 | 5.7759 | 5.864 | 5.8269 | 5.7241 | 120.9385 | 120.9508 | 120.9906 | 120.9266 | 0.181 | 0.14683 | 0.007721 | 0.097548 | 2.672 | 5.7242 | 5.8669 | 5.7897 | 5.8777 | 5.8406 | 5.7378 | 120.9522 | 120.9646 | 121.0043 | 120.9403 | 0.19474 | 0.16056 | 0.021454 | 0.11128 | 120.7575 | 120.9308 | 120.8096 | 120.9829
2247.7344 | 121.1838 | -0.20599 | 121.1151 | 2.6812 | 5.7288 | 5.8623 | 5.7851 | 5.8732 | 5.8315 | 5.7332 | 120.9385 | 120.9554 | 121.0043 | 120.9266 | 0.17642 | 0.14225 | 0.003143 | 0.09297 | 2.6949 | 5.7425 | 5.8761 | 5.7988 | 5.8869 | 5.8452 | 5.747 | 120.9522 | 120.9691 | 121.018 | 120.9403 | 0.19016 | 0.15598 | 0.016876 | 0.1067 | 120.7621 | 120.9354 | 120.8279 | 121.0012
2249.4062 | 121.3211 | -0.16022 | 121.0419 | 2.7041 | 5.7379 | 5.8807 | 5.808 | 5.8823 | 5.8452 | 5.7424 | 120.9477 | 120.96 | 121.0089 | 120.9358 | 0.19016 | 0.15141 | 0.003143 | 0.097548 | 2.7178 | 5.7517 | 5.8944 | 5.8217 | 5.8961 | 5.8589 | 5.7561 | 120.9614 | 120.9737 | 121.0226 | 120.9495 | 0.20389 | 0.16514 | 0.016876 | 0.11128 | 120.7575 | 120.9445 | 120.8187 | 121.0057
2251.1406 | 121.2067 | -0.19684 | 121.0922 | 2.7407 | 5.7929 | 5.9356 | 5.8538 | 5.951 | 5.9093 | 5.8065 | 120.9522 | 120.9646 | 121.0089 | 120.9449 | 0.17642 | 0.15141 | 0.021456 | 0.097548 | 2.7544 | 5.8066 | 5.9493 | 5.8675 | 5.9647 | 5.923 | 5.8202 | 120.966 | 120.9783 | 121.0226 | 120.9587 | 0.19016 | 0.16514 | 0.035189 | 0.11128 | 120.7758 | 120.9308 | 120.8325 | 120.9874
2252.8281 | 121.2982 | -0.16479 | 121.0876 | 2.7636 | 5.8295 | 5.9631 | 5.8904 | 5.9785 | 5.9368 | 5.8385 | 120.9614 | 120.9691 | 121.0226 | 120.9449 | 0.181 | 0.14225 | -0.001436 | 0.088392 | 2.7773 | 5.8433 | 5.9768 | 5.9041 | 5.9922 | 5.9505 | 5.8523 | 120.9751 | 120.9829 | 121.0364 | 120.9587 | 0.19474 | 0.15598 | 0.012297 | 0.10212 | 120.7804 | 120.9628 | 120.8416 | 121.0241
2254.5781 | 121.2433 | -0.19226 | 121.1105 | 2.8185 | 5.889 | 6.0272 | 5.9499 | 6.0425 | 6.0009 | 5.8843 | 120.9705 | 120.9783 | 121.0226 | 120.9495 | 0.19016 | 0.15141 | 0.012299 | 0.097548 | 2.8323 | 5.9028 | 6.0409 | 5.9637 | 6.0563 | 6.0146 | 5.8981 | 120.9843 | 120.992 | 121.0364 | 120.9632 | 0.20389 | 0.16514 | 0.026032 | 0.11128 | 120.7804 | 120.9582 | 120.8325 | 121.0103
2256.3125 | 121.2799 | -0.18768 | 121.1014 | 2.8414 | 5.8982 | 6.0501 | 5.9682 | 6.0654 | 6.0238 | 5.9118 | 120.9797 | 120.9875 | 121.0409 | 120.9632 | 0.18558 | 0.14225 | -0.001436 | 0.097548 | 2.8551 | 5.9119 | 6.0638 | 5.982 | 6.0792 | 6.0375 | 5.9255 | 120.9934 | 121.0012 | 121.0547 | 120.977 | 0.19931 | 0.15598 | 0.012297 | 0.11128 | 120.7941 | 120.9811 | 120.8554 | 121.0424
2258 | 121.2296 | -0.21057 | 121.1197 | 2.8277 | 5.8707 | 5.9997 | 5.927 | 6.0105 | 5.9734 | 5.8706 | 120.9751 | 120.992 | 121.0364 | 120.9678 | 0.181 | 0.14225 | 0.003143 | 0.09297 | 2.8414 | 5.8845 | 6.0134 | 5.9408 | 6.0242 | 5.9871 | 5.8843 | 120.9889 | 121.0058 | 121.0501 | 120.9815 | 0.19474 | 0.15598 | 0.016876 | 0.1067 | 120.7941 | 120.972 | 120.8554 | 121.0332
2259.75 | 121.3806 | -0.14191 | 121.0831 | 2.846 | 5.8662 | 5.9997 | 5.927 | 6.0242 | 5.978 | 5.8843 | 120.9843 | 120.9875 | 121.0364 | 120.9678 | 0.19016 | 0.14683 | 0.012299 | 0.097548 | 2.8597 | 5.8799 | 6.0134 | 5.9408 | 6.038 | 5.9917 | 5.8981 | 120.998 | 121.0012 | 121.0501 | 120.9815 | 0.20389 | 0.16056 | 0.026032 | 0.11128 | 120.7941 | 120.972 | 120.8462 | 121.0241
2261.5 | 121.3715 | -0.15564 | 121.1014 | 2.8826 | 5.9074 | 6.0501 | 5.9774 | 6.07 | 6.0238 | 5.9164 | 120.9889 | 121.0012 | 121.0547 | 120.977 | 0.19016 | 0.14225 | -0.001436 | 0.09297 | 2.8964 | 5.9211 | 6.0638 | 5.9911 | 6.0837 | 6.0375 | 5.9301 | 121.0026 | 121.0149 | 121.0684 | 120.9907 | 0.20389 | 0.15598 | 0.012297 | 0.1067 | 120.7987 | 120.9903 | 120.8645 | 121.0561
2263.25 | 121.2616 | -0.21515 | 121.1609 | 2.933 | 5.9623 | 6.0959 | 6.0278 | 6.1112 | 6.0741 | 5.9622 | 120.998 | 121.0149 | 121.0593 | 120.9907 | 0.17642 | 0.15141 | 0.007721 | 0.097548 | 2.9467 | 5.976 | 6.1096 | 6.0415 | 6.1249 | 6.0878 | 5.9759 | 121.0118 | 121.0287 | 121.073 | 121.0044 | 0.19016 | 0.16514 | 0.021454 | 0.11128 | 120.8216 | 120.9903 | 120.8828 | 121.0515
2264.9219 | 121.3852 | -0.15564 | 121.1334 | 2.9513 | 5.9669 | 6.1004 | 6.0323 | 6.1204 | 6.0787 | 5.9713 | 120.998 | 121.0104 | 121.0638 | 120.9861 | 0.181 | 0.14683 | 0.003143 | 0.09297 | 2.965 | 5.9806 | 6.1142 | 6.0461 | 6.1341 | 6.0924 | 5.985 | 121.0118 | 121.0241 | 121.0776 | 120.9999 | 0.19474 | 0.16056 | 0.016876 | 0.1067 | 120.817 | 120.9949 | 120.8828 | 121.0607
2266.6562 | 121.3806 | -0.16022 | 121.0968 | 2.9879 | 6.0173 | 6.1508 | 6.0781 | 6.1662 | 6.1153 | 6.0217 | 120.998 | 121.0149 | 121.0593 | 120.9861 | 0.18558 | 0.15598 | 0.03977 | 0.11128 | 3.0017 | 6.031 | 6.1645 | 6.0918 | 6.1799 | 6.1291 | 6.0354 | 121.0118 | 121.0287 | 121.073 | 120.9999 | 0.19931 | 0.16972 | 0.053503 | 0.12502 | 120.8124 | 120.9582 | 120.8737 | 121.0195
2268.3438 | 121.3074 | -0.19684 | 121.1517 | 3.02 | 6.0539 | 6.1966 | 6.1193 | 6.2119 | 6.1703 | 6.0629 | 121.0163 | 121.0333 | 121.0638 | 121.0044 | 0.181 | 0.14225 | 0.007721 | 0.09297 | 3.0337 | 6.0676 | 6.2103 | 6.1331 | 6.2257 | 6.184 | 6.0766 | 121.0301 | 121.047 | 121.0776 | 121.0182 | 0.19474 | 0.15598 | 0.021454 | 0.1067 | 120.8353 | 121.0086 | 120.8828 | 121.0561
2270.0781 | 121.3531 | -0.16937 | 121.1563 | 3.0658 | 6.1088 | 6.2332 | 6.1651 | 6.2623 | 6.216 | 6.1087 | 121.0209 | 121.0333 | 121.0821 | 121.0044 | 0.181 | 0.14683 | -0.001436 | 0.097548 | 3.0795 | 6.1226 | 6.2469 | 6.1788 | 6.276 | 6.2298 | 6.1224 | 121.0346 | 121.047 | 121.0959 | 121.0182 | 0.19474 | 0.16056 | 0.012297 | 0.11128 | 120.8399 | 121.0223 | 120.9011 | 121.0836
2271.8281 | 121.4172 | -0.17395 | 121.1472 | 3.0841 | 6.1226 | 6.2561 | 6.1743 | 6.2714 | 6.2298 | 6.127 | 121.0255 | 121.0333 | 121.0913 | 121.0136 | 0.17642 | 0.14225 | -0.001436 | 0.097548 | 3.0978 | 6.1363 | 6.2698 | 6.188 | 6.2852 | 6.2435 | 6.1407 | 121.0392 | 121.047 | 121.105 | 121.0273 | 0.19016 | 0.15598 | 0.012297 | 0.11128 | 120.8491 | 121.0269 | 120.9149 | 121.0927
2273.5156 | 121.3028 | -0.20142 | 121.1929 | 3.1253 | 6.1821 | 6.3202 | 6.2429 | 6.331 | 6.2939 | 6.1865 | 121.0346 | 121.0424 | 121.0959 | 121.0182 | 0.17642 | 0.14225 | 0.003143 | 0.10213 | 3.139 | 6.1958 | 6.3339 | 6.2567 | 6.3447 | 6.3076 | 6.2002 | 121.0484 | 121.0561 | 121.1096 | 121.0319 | 0.19016 | 0.15598 | 0.016876 | 0.11586 | 120.8582 | 121.0315 | 120.9195 | 121.0927
2275.2656 | 121.2799 | -0.21057 | 121.1929 | 3.1619 | 6.2096 | 6.3523 | 6.2704 | 6.3676 | 6.3305 | 6.2094 | 121.0392 | 121.0516 | 121.105 | 121.0182 | 0.18558 | 0.14683 | 0.003143 | 0.09297 | 3.1756 | 6.2233 | 6.366 | 6.2841 | 6.3813 | 6.3442 | 6.2231 | 121.053 | 121.0653 | 121.1188 | 121.0319 | 0.19931 | 0.16056 | 0.016876 | 0.1067 | 120.8536 | 121.0361 | 120.9195 | 121.1019
2276.9531 | 121.3303 | -0.19684 | 121.1838 | 3.1848 | 6.2233 | 6.3614 | 6.2841 | 6.3767 | 6.3397 | 6.2231 | 121.053 | 121.0561 | 121.105 | 121.0319 | 0.17642 | 0.15141 | 0.003143 | 0.088392 | 3.1985 | 6.237 | 6.3751 | 6.2979 | 6.3905 | 6.3534 | 6.2368 | 121.0667 | 121.0699 | 121.1188 | 121.0457 | 0.19016 | 0.16514 | 0.016876 | 0.10212 | 120.8765 | 121.0498 | 120.9286 | 121.1019
2278.6875 | 121.3577 | -0.17395 | 121.2021 | 3.2306 | 6.2782 | 6.4164 | 6.3528 | 6.4271 | 6.3809 | 6.2918 | 121.053 | 121.0561 | 121.105 | 121.0365 | 0.17185 | 0.14225 | 0.003143 | 0.097548 | 3.2443 | 6.292 | 6.4301 | 6.3666 | 6.4408 | 6.3946 | 6.3055 | 121.0667 | 121.0699 | 121.1188 | 121.0502 | 0.18558 | 0.15598 | 0.016876 | 0.11128 | 120.8811 | 121.0498 | 120.9332 | 121.1019
2280.4219 | 121.3394 | -0.2243 | 121.2204 | 3.2672 | 6.3378 | 6.4667 | 6.3986 | 6.4912 | 6.445 | 6.3421 | 121.0621 | 121.0653 | 121.1096 | 121.0365 | 0.17642 | 0.15598 | -0.001436 | 0.097548 | 3.2809 | 6.3515 | 6.4805 | 6.4123 | 6.5049 | 6.4587 | 6.3559 | 121.0758 | 121.079 | 121.1233 | 121.0502 | 0.19016 | 0.16972 | 0.012297 | 0.11128 | 120.8857 | 121.0636 | 120.9332 | 121.111
2282.1094 | 121.4722 | -0.15106 | 121.1792 | 3.3084 | 6.3698 | 6.5125 | 6.4398 | 6.5232 | 6.4862 | 6.3834 | 121.0667 | 121.0699 | 121.1188 | 121.0457 | 0.17642 | 0.14683 | 0.003143 | 0.09297 | 3.3221 | 6.3836 | 6.5262 | 6.4536 | 6.537 | 6.4999 | 6.3971 | 121.0804 | 121.0836 | 121.1325 | 121.0594 | 0.19016 | 0.16056 | 0.016876 | 0.1067 | 120.8903 | 121.0636 | 120.9423 | 121.1156
2283.8594 | 121.3577 | -0.19226 | 121.1929 | 3.345 | 6.411 | 6.5491 | 6.4764 | 6.569 | 6.5274 | 6.4154 | 121.0667 | 121.0745 | 121.1233 | 121.0548 | 0.18558 | 0.15141 | -0.001436 | 0.09297 | 3.3588 | 6.4248 | 6.5629 | 6.4902 | 6.5827 | 6.5411 | 6.4291 | 121.0804 | 121.0882 | 121.1371 | 121.0686 | 0.19931 | 0.16514 | 0.012297 | 0.1067 | 120.8811 | 121.0681 | 120.9378 | 121.1248
2285.5938 | 121.3211 | -0.20599 | 121.2341 | 3.3679 | 6.4202 | 6.5583 | 6.4856 | 6.5873 | 6.5365 | 6.4337 | 121.0713 | 121.0836 | 121.1371 | 121.0594 | 0.181 | 0.14225 | 0.003143 | 0.097548 | 3.3817 | 6.4339 | 6.572 | 6.4993 | 6.6011 | 6.5503 | 6.4474 | 121.085 | 121.0974 | 121.1508 | 121.0731 | 0.19474 | 0.15598 | 0.016876 | 0.11128 | 120.8903 | 121.0681 | 120.9561 | 121.1339
2287.2656 | 121.4676 | -0.15564 | 121.1655 | 3.3862 | 6.4522 | 6.5949 | 6.5085 | 6.6056 | 6.5548 | 6.452 | 121.0713 | 121.0836 | 121.1371 | 121.064 | 0.18558 | 0.14683 | -0.001436 | 0.09297 | 3.4 | 6.466 | 6.6087 | 6.5222 | 6.6194 | 6.5686 | 6.4658 | 121.085 | 121.0974 | 121.1508 | 121.0777 | 0.19931 | 0.16056 | 0.012297 | 0.1067 | 120.8857 | 121.0727 | 120.9515 | 121.1385
2289.0156 | 121.4767 | -0.16479 | 121.2067 | 3.4274 | 6.4935 | 6.627 | 6.5451 | 6.6468 | 6.5915 | 6.5024 | 121.085 | 121.0928 | 121.1325 | 121.0686 | 0.181 | 0.14683 | 0.003143 | 0.09297 | 3.4412 | 6.5072 | 6.6407 | 6.5589 | 6.6606 | 6.6052 | 6.5161 | 121.0987 | 121.1065 | 121.1462 | 121.0823 | 0.19474 | 0.16056 | 0.016876 | 0.1067 | 120.904 | 121.0819 | 120.9515 | 121.1294
2290.7656 | 121.3486 | -0.19684 | 121.2204 | 3.4687 | 6.5392 | 6.6819 | 6.6046 | 6.7063 | 6.6556 | 6.5619 | 121.0896 | 121.1019 | 121.1462 | 121.0823 | 0.18558 | 0.14225 | 0.007721 | 0.097548 | 3.4824 | 6.553 | 6.6957 | 6.6184 | 6.7201 | 6.6693 | 6.5756 | 121.1033 | 121.1157 | 121.16 | 121.096 | 0.19931 | 0.15598 | 0.021454 | 0.11128 | 120.904 | 121.0819 | 120.9607 | 121.1385
2292.5156 | 121.3531 | -0.2243 | 121.2341 | 3.5053 | 6.5667 | 6.7094 | 6.6275 | 6.7201 | 6.6739 | 6.5848 | 121.0942 | 121.1019 | 121.1554 | 121.0731 | 0.19016 | 0.14225 | 0.007721 | 0.09297 | 3.519 | 6.5804 | 6.7231 | 6.6413 | 6.7338 | 6.6876 | 6.5985 | 121.1079 | 121.1157 | 121.1691 | 121.0869 | 0.20389 | 0.15598 | 0.021454 | 0.1067 | 120.904 | 121.0864 | 120.9652 | 121.1477
2294.2656 | 121.3989 | -0.18768 | 121.2296 | 3.5328 | 6.585 | 6.7277 | 6.6596 | 6.7476 | 6.7059 | 6.5985 | 121.0942 | 121.1065 | 121.1508 | 121.0777 | 0.18558 | 0.14225 | 0.007721 | 0.09297 | 3.5465 | 6.5988 | 6.7414 | 6.6733 | 6.7613 | 6.7197 | 6.6123 | 121.1079 | 121.1202 | 121.1646 | 121.0914 | 0.19931 | 0.15598 | 0.021454 | 0.1067 | 120.9086 | 121.0864 | 120.9652 | 121.1431
2295.9375 | 121.4447 | -0.18768 | 121.225 | 3.5831 | 6.6491 | 6.7964 | 6.7145 | 6.8116 | 6.7655 | 6.658 | 121.1033 | 121.1111 | 121.16 | 121.0915 | 0.19016 | 0.15598 | -0.001436 | 0.097548 | 3.5968 | 6.6629 | 6.8101 | 6.7283 | 6.8254 | 6.7792 | 6.6718 | 121.1171 | 121.1248 | 121.1737 | 121.1052 | 0.20389 | 0.16972 | 0.012297 | 0.11128 | 120.9132 | 121.1048 | 120.9698 | 121.1614
2297.6719 | 121.4859 | -0.15564 | 121.225 | 3.6152 | 6.7041 | 6.8422 | 6.7695 | 6.8666 | 6.8158 | 6.7176 | 121.1079 | 121.1111 | 121.1646 | 121.096 | 0.18558 | 0.14683 | 0.003143 | 0.09297 | 3.6289 | 6.7178 | 6.8559 | 6.7832 | 6.8803 | 6.8295 | 6.7313 | 121.1216 | 121.1248 | 121.1783 | 121.1098 | 0.19931 | 0.16056 | 0.016876 | 0.1067 | 120.9223 | 121.1048 | 120.979 | 121.1614
2299.4219 | 121.5134 | -0.14191 | 121.2433 | 3.6655 | 6.7682 | 6.9154 | 6.829 | 6.9215 | 6.8845 | 6.7771 | 121.1079 | 121.1202 | 121.1737 | 121.096 | 0.18558 | 0.15141 | -0.006014 | 0.097548 | 3.6793 | 6.7819 | 6.9292 | 6.8427 | 6.9352 | 6.8982 | 6.7908 | 121.1216 | 121.134 | 121.1874 | 121.1098 | 0.19931 | 0.16514 | 0.007719 | 0.11128 | 120.9223 | 121.1139 | 120.9881 | 121.1797
2301.0938 | 121.4172 | -0.21057 | 121.257 | 3.7067 | 6.8048 | 6.9337 | 6.861 | 6.9536 | 6.9028 | 6.8091 | 121.1216 | 121.1294 | 121.1829 | 121.1098 | 0.181 | 0.15141 | 0.003143 | 0.09297 | 3.7205 | 6.8185 | 6.9475 | 6.8748 | 6.9673 | 6.9165 | 6.8229 | 121.1354 | 121.1431 | 121.1966 | 121.1235 | 0.19474 | 0.16514 | 0.016876 | 0.1067 | 120.9406 | 121.1185 | 121.0019 | 121.1797
2302.7812 | 121.5042 | -0.15106 | 121.225 | 3.7388 | 6.8414 | 6.9887 | 6.9022 | 6.9948 | 6.9532 | 6.8549 | 121.1216 | 121.1248 | 121.1737 | 121.1052 | 0.181 | 0.14683 | 0.003143 | 0.09297 | 3.7525 | 6.8552 | 7.0024 | 6.916 | 7.0085 | 6.9669 | 6.8686 | 121.1354 | 121.1386 | 121.1874 | 121.1189 | 0.19474 | 0.16056 | 0.016876 | 0.1067 | 120.9406 | 121.1185 | 120.9927 | 121.1706
2304.5312 | 121.3669 | -0.21973 | 121.2708 | 3.7754 | 6.8872 | 7.0299 | 6.9435 | 7.0405 | 6.9944 | 6.9007 | 121.1216 | 121.1431 | 121.1874 | 121.1143 | 0.18558 | 0.14683 | 0.003143 | 0.09297 | 3.7891 | 6.901 | 7.0436 | 6.9572 | 7.0543 | 7.0081 | 6.9144 | 121.1354 | 121.1569 | 121.2012 | 121.1281 | 0.19931 | 0.16056 | 0.016876 | 0.1067 | 120.9361 | 121.1185 | 121.0019 | 121.1843
2306.2031 | 117.8558 | -25.1404 | 92.4408 | 1.3214 | 2.1985 | 2.2956 | 2.2413 | 2.3436 | 2.2786 | 2.1852 | 88.7746 | 88.7984 | 88.8236 | 88.7589 | 28.6343 | 28.6041 | 28.3846 | 28.528 | 1.3351 | 2.2123 | 2.3093 | 2.2551 | 2.3573 | 2.2924 | 2.1989 | 88.7883 | 88.8121 | 88.8373 | 88.7726 | 28.6481 | 28.6178 | 28.3983 | 28.5417 | 60.1402 | 60.39 | 60.1892 | 60.439
2307.9375 | 115.3336 | -37.6053 | 77.1286 | 0.79487 | 1.2232 | 1.2929 | 1.2478 | 1.341 | 1.3217 | 1.2009 | 81.3528 | 81.3166 | 81.4113 | 81.2997 | 34.618 | 34.5601 | 34.3502 | 34.4842 | 0.80861 | 1.237 | 1.3066 | 1.2615 | 1.3547 | 1.3355 | 1.2146 | 81.3666 | 81.3303 | 81.4251 | 81.3134 | 34.6318 | 34.5739 | 34.3639 | 34.4979 | 46.7348 | 47.0026 | 46.7933 | 47.0611
2309.6875 | 120.1538 | -0.3479 | 119.902 | 3.8944 | 6.9513 | 7.0528 | 7.0076 | 7.1092 | 7.0585 | 6.951 | 119.7801 | 119.797 | 119.8369 | 119.759 | 0.17185 | 0.23381 | 0.080975 | 0.1708 | 3.9082 | 6.9651 | 7.0665 | 7.0213 | 7.1229 | 7.0722 | 6.9648 | 119.7939 | 119.8107 | 119.8506 | 119.7727 | 0.18558 | 0.24754 | 0.094708 | 0.18453 | 119.6083 | 119.6992 | 119.665 | 119.7559
2311.375 | 120.3186 | -0.21057 | 120.2362 | 3.899 | 6.9513 | 7.0619 | 7.0259 | 7.1138 | 7.0676 | 6.9739 | 120.0503 | 120.0763 | 120.1161 | 120.0429 | 0.17642 | 0.14683 | 0.012299 | 0.10213 | 3.9128 | 6.9651 | 7.0757 | 7.0396 | 7.1275 | 7.0814 | 6.9877 | 120.064 | 120.09 | 120.1299 | 120.0566 | 0.19016 | 0.16056 | 0.026032 | 0.11586 | 119.8738 | 120.038 | 119.9397 | 120.1038
2313.125 | 120.4147 | -0.20142 | 120.3186 | 3.9356 | 6.9834 | 7.0803 | 7.0488 | 7.1321 | 7.0951 | 6.9922 | 120.151 | 120.1587 | 120.1985 | 120.1299 | 0.181 | 0.15141 | 0.007721 | 0.10213 | 3.9494 | 6.9971 | 7.094 | 7.0625 | 7.1458 | 7.1088 | 7.006 | 120.1647 | 120.1724 | 120.2123 | 120.1436 | 0.19474 | 0.16514 | 0.021454 | 0.11586 | 119.97 | 120.1433 | 120.0175 | 120.1908
2314.875 | 120.5795 | -0.16479 | 120.3049 | 3.9677 | 7.0338 | 7.1306 | 7.0991 | 7.1916 | 7.1455 | 7.0426 | 120.2014 | 120.2182 | 120.2626 | 120.1848 | 0.19016 | 0.15141 | 0.007721 | 0.10213 | 3.9814 | 7.0475 | 7.1444 | 7.1129 | 7.2053 | 7.1592 | 7.0563 | 120.2151 | 120.232 | 120.2764 | 120.1985 | 0.20389 | 0.16514 | 0.021454 | 0.11586 | 120.0112 | 120.1936 | 120.0725 | 120.2549
2316.5469 | 120.6162 | -0.15106 | 120.3827 | 3.9997 | 7.0521 | 7.1444 | 7.1174 | 7.2099 | 7.1592 | 7.0563 | 120.2471 | 120.264 | 120.3038 | 120.2352 | 0.181 | 0.15141 | 0.007721 | 0.10213 | 4.0135 | 7.0658 | 7.1581 | 7.1312 | 7.2237 | 7.1729 | 7.0701 | 120.2609 | 120.2777 | 120.3176 | 120.2489 | 0.19474 | 0.16514 | 0.021454 | 0.11586 | 120.0661 | 120.2394 | 120.1228 | 120.2961
2318.2812 | 120.6436 | -0.16022 | 120.401 | 4.041 | 7.1162 | 7.2085 | 7.177 | 7.2649 | 7.2233 | 7.1159 | 120.2883 | 120.2961 | 120.345 | 120.281 | 0.19016 | 0.14683 | 0.003143 | 0.10213 | 4.0547 | 7.1299 | 7.2222 | 7.1907 | 7.2786 | 7.237 | 7.1296 | 120.3021 | 120.3098 | 120.3588 | 120.2947 | 0.20389 | 0.16056 | 0.016876 | 0.11586 | 120.0982 | 120.2852 | 120.1549 | 120.3419
2319.9844 | 120.607 | -0.19226 | 120.4422 | 4.0776 | 7.1482 | 7.2451 | 7.2227 | 7.3015 | 7.2645 | 7.1616 | 120.3158 | 120.3281 | 120.3771 | 120.3039 | 0.18558 | 0.14683 | 0.012299 | 0.088392 | 4.0913 | 7.162 | 7.2588 | 7.2365 | 7.3152 | 7.2782 | 7.1754 | 120.3296 | 120.3418 | 120.3908 | 120.3176 | 0.19931 | 0.16056 | 0.026032 | 0.10212 | 120.1302 | 120.3035 | 120.1915 | 120.3648
2321.7344 | 120.6848 | -0.1831 | 120.4971 | 4.1463 | 7.1986 | 7.3092 | 7.2685 | 7.361 | 7.3194 | 7.2166 | 120.3524 | 120.3647 | 120.4046 | 120.3313 | 0.181 | 0.14225 | -0.001436 | 0.097548 | 4.16 | 7.2123 | 7.3229 | 7.2823 | 7.3747 | 7.3332 | 7.2303 | 120.3662 | 120.3785 | 120.4183 | 120.3451 | 0.19474 | 0.15598 | 0.012297 | 0.11128 | 120.1714 | 120.3539 | 120.2236 | 120.406
2323.5 | 116.1255 | -37.0743 | 78.891 | 1.0833 | 1.8643 | 1.8652 | 1.8888 | 1.9132 | 1.8849 | 1.8372 | 86.3709 | 86.0465 | 86.4566 | 86.2588 | 30.8365 | 30.6642 | 30.4677 | 30.5882 | 1.097 | 1.878 | 1.879 | 1.9025 | 1.927 | 1.8986 | 1.851 | 86.3846 | 86.0602 | 86.4703 | 86.2725 | 30.8502 | 30.6779 | 30.4815 | 30.6019 | 55.5344 | 55.9031 | 55.6202 | 55.9889
2325.25 | 115.4114 | -38.9969 | 76.149 | 0.69415 | 0.96224 | 1.0457 | 0.99599 | 1.0892 | 1.0333 | 0.9399 | 79.0865 | 79.0592 | 79.1451 | 79.0422 | 36.5363 | 36.4829 | 36.264 | 36.4025 | 0.70788 | 0.97597 | 1.0594 | 1.0097 | 1.1029 | 1.047 | 0.95364 | 79.1002 | 79.073 | 79.1588 | 79.0559 | 36.55 | 36.4967 | 36.2777 | 36.4162 | 42.5502 | 42.8225 | 42.6088 | 42.8811
2326.9375 | 119.8791 | -0.16022 | 119.6274 | 4.3065 | 7.3176 | 7.4649 | 7.3921 | 7.4754 | 7.4293 | 7.3219 | 119.4825 | 119.4948 | 119.5301 | 119.4613 | 0.20389 | 0.16514 | 0.012299 | 0.11128 | 4.3202 | 7.3314 | 7.4786 | 7.4059 | 7.4892 | 7.4431 | 7.3356 | 119.4963 | 119.5085 | 119.5438 | 119.475 | 0.21763 | 0.17887 | 0.026032 | 0.12502 | 119.2786 | 119.4702 | 119.3262 | 119.5178
2328.6875 | 119.9661 | -0.21057 | 119.87 | 4.3385 | 7.3543 | 7.4923 | 7.4196 | 7.5075 | 7.4659 | 7.3585 | 119.6977 | 119.7054 | 119.7453 | 119.6811 | 0.19016 | 0.15141 | 0.012299 | 0.097548 | 4.3523 | 7.368 | 7.5061 | 7.4333 | 7.5212 | 7.4797 | 7.3722 | 119.7115 | 119.7191 | 119.759 | 119.6948 | 0.20389 | 0.16514 | 0.026032 | 0.11128 | 119.5076 | 119.6854 | 119.5551 | 119.733
2330.4219 | 120.0531 | -0.20599 | 119.9478 | 4.3706 | 7.3863 | 7.5198 | 7.4471 | 7.535 | 7.4934 | 7.3951 | 119.7893 | 119.797 | 119.846 | 119.7818 | 0.18558 | 0.14225 | 0.012299 | 0.09297 | 4.3843 | 7.4001 | 7.5335 | 7.4608 | 7.5487 | 7.5071 | 7.4089 | 119.803 | 119.8107 | 119.8597 | 119.7956 | 0.19931 | 0.15598 | 0.026032 | 0.1067 | 119.6037 | 119.777 | 119.6604 | 119.8337
2332.1719 | 120.2133 | -0.16937 | 119.9799 | 4.4118 | 7.4275 | 7.5702 | 7.4929 | 7.5807 | 7.5438 | 7.4363 | 119.858 | 119.8611 | 119.9193 | 119.8414 | 0.181 | 0.15141 | 0.007721 | 0.097548 | 4.4255 | 7.4413 | 7.5839 | 7.5066 | 7.5945 | 7.5575 | 7.4501 | 119.8717 | 119.8748 | 119.933 | 119.8551 | 0.19474 | 0.16514 | 0.021454 | 0.11128 | 119.677 | 119.8503 | 119.7383 | 119.9115
2333.8594 | 119.8563 | -0.20599 | 119.7418 | 4.4622 | 7.5145 | 7.648 | 7.5753 | 7.6723 | 7.6216 | 7.5187 | 119.5237 | 119.5268 | 119.5759 | 119.5163 | 0.11691 | 0.17887 | 0.035191 | 0.12959 | 4.4759 | 7.5283 | 7.6617 | 7.589 | 7.686 | 7.6353 | 7.5325 | 119.5375 | 119.5406 | 119.5896 | 119.53 | 0.13064 | 0.19261 | 0.048924 | 0.14333 | 119.4068 | 119.4886 | 119.459 | 119.5407
2335.5938 | 120.0668 | -0.19226 | 119.9432 | 4.4942 | 7.5741 | 7.7213 | 7.6348 | 7.7318 | 7.6903 | 7.5966 | 119.8076 | 119.8153 | 119.8643 | 119.7818 | 0.094017 | 0.14683 | 0.007721 | 0.09297 | 4.5079 | 7.5878 | 7.735 | 7.6485 | 7.7455 | 7.704 | 7.6103 | 119.8213 | 119.829 | 119.8781 | 119.7956 | 0.10775 | 0.16056 | 0.021454 | 0.1067 | 119.7136 | 119.7999 | 119.7703 | 119.8566
2337.3281 | 116.391 | -27.5208 | 88.6414 | 2.0265 | 3.2562 | 3.367 | 3.2944 | 3.3919 | 3.3591 | 3.2427 | 92.7579 | 92.7728 | 92.8204 | 92.7289 | 23.9509 | 23.9116 | 23.7283 | 23.8583 | 2.0402 | 3.27 | 3.3807 | 3.3081 | 3.4056 | 3.3729 | 3.2565 | 92.7716 | 92.7865 | 92.8342 | 92.7427 | 23.9646 | 23.9253 | 23.7421 | 23.872 | 68.807 | 69.0295 | 68.8695 | 69.0921
2339.0156 | 119.7968 | -0.17853 | 119.6091 | 4.5904 | 7.6656 | 7.7716 | 7.731 | 7.8234 | 7.7819 | 7.679 | 119.4596 | 119.4627 | 119.5164 | 119.4522 | 0.094017 | 0.14225 | 0.003143 | 0.09297 | 4.6041 | 7.6794 | 7.7854 | 7.7447 | 7.8371 | 7.7956 | 7.6927 | 119.4734 | 119.4765 | 119.5301 | 119.4659 | 0.10775 | 0.15598 | 0.016876 | 0.1067 | 119.3656 | 119.4565 | 119.4224 | 119.5132
2340.75 | 120.0119 | -0.16022 | 119.7464 | 4.6407 | 7.7023 | 7.8128 | 7.7767 | 7.86 | 7.8276 | 7.7293 | 119.6382 | 119.6367 | 119.6903 | 119.617 | 0.084861 | 0.14225 | 0.003143 | 0.09297 | 4.6545 | 7.716 | 7.8266 | 7.7905 | 7.8737 | 7.8414 | 7.7431 | 119.6519 | 119.6504 | 119.7041 | 119.6307 | 0.098594 | 0.15598 | 0.016876 | 0.1067 | 119.5533 | 119.6351 | 119.6055 | 119.6872
2342.5 | 120.0531 | -0.17395 | 119.8288 | 4.6773 | 7.7389 | 7.8449 | 7.8134 | 7.9058 | 7.8551 | 7.7614 | 119.7115 | 119.7237 | 119.7728 | 119.6994 | 0.089439 | 0.14683 | 0.007721 | 0.09297 | 4.6911 | 7.7526 | 7.8586 | 7.8271 | 7.9195 | 7.8688 | 7.7751 | 119.7252 | 119.7374 | 119.7865 | 119.7132 | 0.10317 | 0.16056 | 0.021454 | 0.1067 | 119.622 | 119.7037 | 119.6833 | 119.765
2344.25 | 120.0577 | -0.18768 | 119.9112 | 4.7231 | 7.7984 | 7.909 | 7.8637 | 7.9607 | 7.91 | 7.8117 | 119.7801 | 119.7878 | 119.8277 | 119.7544 | 0.084861 | 0.14225 | 0.007721 | 0.097548 | 4.7369 | 7.8121 | 7.9227 | 7.8775 | 7.9744 | 7.9238 | 7.8255 | 119.7939 | 119.8015 | 119.8414 | 119.7681 | 0.098594 | 0.15598 | 0.021454 | 0.11128 | 119.6953 | 119.7724 | 119.7428 | 119.82
2345.9219 | 120.0943 | -0.19684 | 119.9524 | 4.7598 | 7.8488 | 7.9502 | 7.9095 | 8.0019 | 7.9604 | 7.8667 | 119.8168 | 119.829 | 119.8735 | 119.8093 | 0.094017 | 0.15141 | 0.012299 | 0.097548 | 4.7735 | 7.8625 | 7.9639 | 7.9232 | 8.0156 | 7.9741 | 7.8804 | 119.8305 | 119.8428 | 119.8872 | 119.8231 | 0.10775 | 0.16514 | 0.026032 | 0.11128 | 119.7227 | 119.8045 | 119.7795 | 119.8612
2347.6719 | 120.1492 | -0.20142 | 120.0073 | 4.8193 | 7.8991 | 8.0006 | 7.9645 | 8.0614 | 8.0108 | 7.9125 | 119.858 | 119.8702 | 119.9193 | 119.846 | 0.094017 | 0.15141 | 0.007721 | 0.09297 | 4.833 | 7.9129 | 8.0143 | 7.9782 | 8.0752 | 8.0245 | 7.9262 | 119.8717 | 119.884 | 119.933 | 119.8597 | 0.10775 | 0.16514 | 0.021454 | 0.1067 | 119.764 | 119.8503 | 119.8252 | 119.9115
2349.4375 | 120.2545 | -0.16479 | 120.0073 | 4.8559 | 7.9449 | 8.0418 | 8.0102 | 8.1072 | 8.0611 | 7.9582 | 119.8946 | 119.9023 | 119.9559 | 119.8826 | 0.084861 | 0.14683 | -0.001436 | 0.09297 | 4.8696 | 7.9587 | 8.0555 | 8.024 | 8.1209 | 8.0749 | 7.972 | 119.9083 | 119.916 | 119.9696 | 119.8963 | 0.098594 | 0.16056 | 0.012297 | 0.1067 | 119.8097 | 119.896 | 119.871 | 119.9573
2351.1094 | 120.1996 | -0.21515 | 120.0668 | 4.9108 | 7.9861 | 8.0967 | 8.0514 | 8.153 | 8.1069 | 8.0086 | 119.9266 | 119.9389 | 119.9879 | 119.9101 | 0.094017 | 0.14683 | 0.003143 | 0.1067 | 4.9246 | 7.9999 | 8.1104 | 8.0652 | 8.1667 | 8.1207 | 8.0223 | 119.9404 | 119.9526 | 120.0017 | 119.9238 | 0.10775 | 0.16056 | 0.016876 | 0.12044 | 119.8326 | 119.9235 | 119.8939 | 119.9848
2352.8438 | 120.2408 | -0.20599 | 120.0897 | 4.9475 | 8.0319 | 8.1425 | 8.0972 | 8.1942 | 8.1435 | 8.0452 | 119.9587 | 119.9664 | 120.02 | 119.9467 | 0.089439 | 0.15141 | 0.003143 | 0.09297 | 4.9612 | 8.0457 | 8.1562 | 8.111 | 8.2079 | 8.1573 | 8.059 | 119.9724 | 119.9801 | 120.0337 | 119.9604 | 0.10317 | 0.16514 | 0.016876 | 0.1067 | 119.8693 | 119.9556 | 119.9305 | 120.0168
2354.5938 | 120.369 | -0.16479 | 120.0943 | 5.0116 | 8.0915 | 8.2112 | 8.1659 | 8.2537 | 8.2122 | 8.1093 | 119.9816 | 119.9939 | 120.0475 | 119.9833 | 0.084861 | 0.15141 | 0.003143 | 0.09297 | 5.0253 | 8.1052 | 8.2249 | 8.1796 | 8.2674 | 8.226 | 8.1231 | 119.9953 | 120.0076 | 120.0612 | 119.9971 | 0.098594 | 0.16514 | 0.016876 | 0.1067 | 119.8967 | 119.9784 | 119.9626 | 120.0443
2356.3281 | 120.2728 | -0.22888 | 120.1401 | 5.0757 | 8.1556 | 8.257 | 8.2163 | 8.3132 | 8.2626 | 8.1688 | 120.0228 | 120.0305 | 120.0841 | 120.0108 | 0.084861 | 0.14225 | -0.001436 | 0.097548 | 5.0894 | 8.1693 | 8.2707 | 8.23 | 8.3269 | 8.2763 | 8.1826 | 120.0365 | 120.0442 | 120.0978 | 120.0245 | 0.098594 | 0.15598 | 0.012297 | 0.11128 | 119.9379 | 120.0242 | 119.9992 | 120.0855
2358.0156 | 120.282 | -0.21057 | 120.1859 | 5.126 | 8.2197 | 8.3302 | 8.2895 | 8.3865 | 8.3358 | 8.2421 | 120.0411 | 120.0534 | 120.0978 | 120.0291 | 0.094017 | 0.14225 | 0.003143 | 0.097548 | 5.1398 | 8.2334 | 8.3439 | 8.3033 | 8.4002 | 8.3496 | 8.2558 | 120.0548 | 120.0671 | 120.1115 | 120.0428 | 0.10775 | 0.15598 | 0.016876 | 0.11128 | 119.9471 | 120.038 | 120.0038 | 120.0947
2359.7656 | 120.3186 | -0.20142 | 120.2133 | 5.1672 | 8.2563 | 8.3714 | 8.3262 | 8.4185 | 8.3725 | 8.2696 | 120.0732 | 120.0763 | 120.1253 | 120.0566 | 0.084861 | 0.15141 | -0.001436 | 0.097548 | 5.181 | 8.27 | 8.3852 | 8.3399 | 8.4322 | 8.3862 | 8.2833 | 120.0869 | 120.09 | 120.139 | 120.0703 | 0.098594 | 0.16514 | 0.012297 | 0.11128 | 119.9883 | 120.0746 | 120.0404 | 120.1267
2361.5 | 120.3964 | -0.20142 | 120.2362 | 5.2222 | 8.3067 | 8.4172 | 8.3765 | 8.478 | 8.4228 | 8.3382 | 120.0915 | 120.1038 | 120.1528 | 120.0886 | 0.089439 | 0.15141 | 0.007721 | 0.088392 | 5.2359 | 8.3204 | 8.4309 | 8.3903 | 8.4918 | 8.4366 | 8.352 | 120.1052 | 120.1175 | 120.1665 | 120.1024 | 0.10317 | 0.16514 | 0.021454 | 0.10212 | 120.002 | 120.0838 | 120.0633 | 120.145
2363.2344 | 120.3644 | -0.22888 | 120.2454 | 5.268 | 8.3525 | 8.463 | 8.4223 | 8.5101 | 8.4686 | 8.3703 | 120.1189 | 120.1358 | 120.1665 | 120.1161 | 0.084861 | 0.13767 | 0.007721 | 0.09297 | 5.2817 | 8.3662 | 8.4767 | 8.436 | 8.5238 | 8.4823 | 8.384 | 120.1327 | 120.1495 | 120.1802 | 120.1299 | 0.098594 | 0.1514 | 0.021454 | 0.1067 | 120.0341 | 120.1112 | 120.0816 | 120.1588
2364.9062 | 120.4926 | -0.16022 | 120.2637 | 5.3229 | 8.3982 | 8.5042 | 8.4681 | 8.565 | 8.5144 | 8.4115 | 120.151 | 120.1495 | 120.2031 | 120.1299 | 0.084861 | 0.14225 | 0.003143 | 0.09297 | 5.3366 | 8.412 | 8.5179 | 8.4818 | 8.5787 | 8.5281 | 8.4252 | 120.1647 | 120.1633 | 120.2168 | 120.1436 | 0.098594 | 0.15598 | 0.016876 | 0.1067 | 120.0661 | 120.1479 | 120.1183 | 120.2
2366.6406 | 120.5566 | -0.15106 | 120.2728 | 5.3778 | 8.4807 | 8.5775 | 8.5459 | 8.6382 | 8.5922 | 8.4939 | 120.1739 | 120.1679 | 120.2214 | 120.1573 | 0.084861 | 0.14683 | -0.006014 | 0.09297 | 5.3916 | 8.4944 | 8.5912 | 8.5597 | 8.652 | 8.606 | 8.5076 | 120.1876 | 120.1816 | 120.2352 | 120.1711 | 0.098594 | 0.16056 | 0.007719 | 0.1067 | 120.089 | 120.1799 | 120.1366 | 120.2274
2368.3125 | 120.5612 | -0.19684 | 120.3186 | 5.4328 | 8.5036 | 8.6095 | 8.5642 | 8.6611 | 8.6243 | 8.5168 | 120.1968 | 120.1953 | 120.2489 | 120.1756 | 0.089439 | 0.15598 | -0.001436 | 0.09297 | 5.4465 | 8.5173 | 8.6232 | 8.578 | 8.6749 | 8.638 | 8.5305 | 120.2105 | 120.2091 | 120.2626 | 120.1894 | 0.10317 | 0.16972 | 0.012297 | 0.1067 | 120.1073 | 120.1982 | 120.1595 | 120.2503
2369.9844 | 118.483 | -26.4542 | 91.6534 | 5.3549 | 8.3479 | 8.4584 | 8.4131 | 8.5009 | 8.4549 | 8.3611 | 120.0823 | 120.0854 | 120.1344 | 120.0657 | 0.31835 | 0.27501 | 0.16339 | 0.26694 | 5.3687 | 8.3616 | 8.4721 | 8.4269 | 8.5146 | 8.4686 | 8.3749 | 120.0961 | 120.0992 | 120.1482 | 120.0795 | 0.33208 | 0.28875 | 0.17712 | 0.28067 | 119.764 | 119.9189 | 119.8161 | 119.9711
2371.7344 | 115.9882 | -33.7189 | 81.9443 | 1.4587 | 2.052 | 2.1674 | 2.0902 | 2.2016 | 2.1733 | 2.0387 | 84.0084 | 84.0547 | 84.0347 | 83.9784 | 31.8253 | 31.7996 | 31.594 | 31.7281 | 1.4725 | 2.0657 | 2.1811 | 2.104 | 2.2154 | 2.1871 | 2.0524 | 84.0221 | 84.0685 | 84.0484 | 83.9921 | 31.8391 | 31.8133 | 31.6078 | 31.7419 | 52.183 | 52.4143 | 52.2094 | 52.4407
2373.4844 | 119.7784 | -2.8427 | 117.0502 | 5.1627 | 7.9633 | 8.0601 | 8.024 | 8.1164 | 8.0749 | 7.9674 | 116.9048 | 116.9123 | 116.9525 | 116.8787 | 2.8043 | 2.7792 | 2.4388 | 2.7575 | 5.1764 | 7.977 | 8.0738 | 8.0377 | 8.1301 | 8.0886 | 7.9811 | 116.9186 | 116.9261 | 116.9663 | 116.8925 | 2.818 | 2.7929 | 2.4526 | 2.7712 | 114.1005 | 114.466 | 114.1482 | 114.5137
2375.2344 | 119.9112 | -1.8082 | 118.2312 | 5.2771 | 8.096 | 8.2112 | 8.1613 | 8.272 | 8.2214 | 8.1047 | 117.4039 | 117.4572 | 117.4424 | 117.3962 | 2.4243 | 2.413 | 2.3198 | 2.3866 | 5.2908 | 8.1098 | 8.2249 | 8.1751 | 8.2857 | 8.2351 | 8.1185 | 117.4176 | 117.4709 | 117.4561 | 117.4099 | 2.438 | 2.4267 | 2.3335 | 2.4004 | 114.9796 | 115.0841 | 115.0181 | 115.1226
2376.9219 | 119.8746 | -0.99792 | 118.8446 | 5.4831 | 8.4074 | 8.5088 | 8.4635 | 8.5604 | 8.5144 | 8.4115 | 118.6905 | 118.6981 | 118.7426 | 118.6737 | 0.84484 | 0.98004 | 0.66243 | 0.84837 | 5.4969 | 8.4211 | 8.5225 | 8.4772 | 8.5742 | 8.5281 | 8.4252 | 118.7042 | 118.7118 | 118.7564 | 118.6875 | 0.85857 | 0.99377 | 0.67616 | 0.8621 | 117.8456 | 118.028 | 117.8978 | 118.0802
2378.6562 | 120.0302 | -1.0025 | 119.0186 | 5.5289 | 8.4532 | 8.5546 | 8.5047 | 8.6062 | 8.5602 | 8.4618 | 118.869 | 118.8812 | 118.9258 | 118.8615 | 0.8311 | 0.97088 | 0.6487 | 0.83463 | 5.5427 | 8.4669 | 8.5683 | 8.5185 | 8.6199 | 8.5739 | 8.4756 | 118.8827 | 118.8949 | 118.9395 | 118.8752 | 0.84484 | 0.98461 | 0.66243 | 0.84837 | 118.0379 | 118.2203 | 118.0947 | 118.2771
2380.4062 | 120.0256 | -1.1536 | 118.9453 | 5.5518 | 8.4944 | 8.5775 | 8.5413 | 8.6337 | 8.5968 | 8.4893 | 118.8187 | 118.8263 | 118.8708 | 118.8111 | 0.95929 | 1.1036 | 0.78147 | 0.94909 | 5.5656 | 8.5081 | 8.5912 | 8.5551 | 8.6474 | 8.6105 | 8.503 | 118.8324 | 118.84 | 118.8846 | 118.8248 | 0.97303 | 1.1174 | 0.7952 | 0.96282 | 117.8594 | 118.0372 | 117.9115 | 118.0894
2382.0781 | 117.6178 | -48.3902 | 69.223 | -0.80298 | -1.5195 | -1.3856 | -1.481 | -1.3371 | -1.3795 | -1.5369 | 66.1614 | 66.3393 | 66.1931 | 66.1751 | 50.6325 | 50.6383 | 50.3837 | 50.5719 | -0.78925 | -1.5057 | -1.3718 | -1.4672 | -1.3234 | -1.3658 | -1.5232 | 66.1751 | 66.353 | 66.2069 | 66.1889 | 50.6462 | 50.6521 | 50.3975 | 50.5856 | 15.5289 | 15.7777 | 15.5607 | 15.8094
2383.8125 | 119.9203 | -4.3716 | 115.4709 | 5.2909 | 7.9266 | 8.0143 | 7.9782 | 8.0614 | 8.0199 | 7.9262 | 115.3344 | 115.3464 | 115.3913 | 115.3173 | 4.4341 | 4.3953 | 4.2931 | 4.369 | 5.3046 | 7.9404 | 8.028 | 7.9919 | 8.0752 | 8.0337 | 7.9399 | 115.3482 | 115.3601 | 115.4051 | 115.331 | 4.4479 | 4.409 | 4.3068 | 4.3827 | 110.9003 | 111.0413 | 110.9572 | 111.0982
2385.5625 | 120.0119 | -4.2068 | 115.8417 | 5.3641 | 8.009 | 8.0967 | 8.0606 | 8.1576 | 8.1115 | 8.0086 | 115.687 | 115.6898 | 115.7256 | 115.6516 | 4.2144 | 4.1801 | 3.8444 | 4.163 | 5.3778 | 8.0228 | 8.1104 | 8.0743 | 8.1713 | 8.1252 | 8.0223 | 115.7007 | 115.7035 | 115.7393 | 115.6653 | 4.2281 | 4.1938 | 3.8581 | 4.1767 | 111.4726 | 111.8426 | 111.5112 | 111.8811
2387.3125 | 119.8929 | -3.891 | 116.0568 | 5.419 | 8.1189 | 8.2157 | 8.1796 | 8.2674 | 8.2168 | 8.1322 | 115.8838 | 115.8912 | 115.9224 | 115.8668 | 3.9305 | 3.9008 | 3.7574 | 3.8654 | 5.4328 | 8.1327 | 8.2295 | 8.1934 | 8.2812 | 8.2305 | 8.1459 | 115.8976 | 115.905 | 115.9362 | 115.8805 | 3.9443 | 3.9146 | 3.7712 | 3.8791 | 111.9533 | 112.1264 | 111.9919 | 112.165
2388.9844 | 120.0806 | -4.216 | 115.8005 | 5.4236 | 8.1235 | 8.2066 | 8.1659 | 8.2674 | 8.2214 | 8.1276 | 115.893 | 115.9004 | 115.9453 | 115.8714 | 4.0312 | 3.9924 | 3.6567 | 3.8471 | 5.4374 | 8.1372 | 8.2203 | 8.1796 | 8.2812 | 8.2351 | 8.1414 | 115.9067 | 115.9141 | 115.959 | 115.8851 | 4.045 | 4.0061 | 3.6704 | 3.8608 | 111.8617 | 112.2363 | 111.9141 | 112.2886
2390.7344 | 120.1859 | -3.8315 | 116.2354 | 5.4877 | 8.1785 | 8.2753 | 8.2346 | 8.3178 | 8.2855 | 8.1872 | 116.1402 | 116.1477 | 116.1834 | 116.1186 | 3.8481 | 3.8093 | 3.4827 | 3.6639 | 5.5015 | 8.1922 | 8.289 | 8.2483 | 8.3315 | 8.2992 | 8.2009 | 116.154 | 116.1614 | 116.1971 | 116.1324 | 3.8619 | 3.823 | 3.4965 | 3.6777 | 112.2921 | 112.6575 | 112.3353 | 112.7007
2392.4844 | 119.7601 | -73.114 | 46.2662 | -3.8797 | -6.0296 | -5.9779 | -6.0045 | -5.9197 | -5.9899 | -6.0647 | 46.0481 | 46.0139 | 46.0441 | 45.9724 | 73.2899 | 73.2952 | 73.0101 | 73.124 | -3.8659 | -6.0159 | -5.9642 | -5.9908 | -5.9059 | -5.9762 | -6.051 | 46.0618 | 46.0276 | 46.0579 | 45.9862 | 73.3036 | 73.3089 | 73.0238 | 73.1377 | -27.2418 | -26.9621 | -27.2457 | -26.966
2394.1562 | 120.0302 | -5.7724 | 114.3356 | 5.4374 | 8.0182 | 8.1104 | 8.0789 | 8.1713 | 8.1207 | 8.0178 | 114.4737 | 114.4901 | 114.5306 | 114.4564 | 5.4413 | 5.4391 | 5.108 | 5.335 | 5.4511 | 8.0319 | 8.1242 | 8.0927 | 8.185 | 8.1344 | 8.0315 | 114.4874 | 114.5039 | 114.5444 | 114.4702 | 5.4551 | 5.4528 | 5.1218 | 5.3487 | 109.0323 | 109.3656 | 109.0893 | 109.4226
2395.9062 | 120.0897 | -2.9343 | 117.2699 | 5.8265 | 8.5539 | 8.6416 | 8.6009 | 8.7023 | 8.6609 | 8.5397 | 117.0834 | 117.0909 | 117.1265 | 117.0665 | 2.9554 | 2.912 | 2.5854 | 2.8948 | 5.8403 | 8.5677 | 8.6553 | 8.6146 | 8.7161 | 8.6746 | 8.5534 | 117.0971 | 117.1046 | 117.1402 | 117.0802 | 2.9691 | 2.9257 | 2.5991 | 2.9085 | 114.128 | 114.4981 | 114.1711 | 114.5412
2397.5938 | 120.2499 | -2.3895 | 117.7597 | 5.9456 | 8.6775 | 8.7652 | 8.7336 | 8.8259 | 8.7937 | 8.6862 | 117.6054 | 117.6129 | 117.6622 | 117.5885 | 2.4609 | 2.4313 | 2.0955 | 2.2859 | 5.9593 | 8.6913 | 8.7789 | 8.7474 | 8.8397 | 8.8074 | 8.6999 | 117.6191 | 117.6266 | 117.6759 | 117.6022 | 2.4747 | 2.445 | 2.1092 | 2.2996 | 115.1444 | 115.5099 | 115.2012 | 115.5667
2399.3281 | 120.2499 | -1.9501 | 118.2541 | 6.0554 | 8.8378 | 8.93 | 8.8893 | 8.9816 | 8.9493 | 8.8327 | 118.1319 | 118.1394 | 118.1795 | 118.1105 | 1.9711 | 1.9414 | 1.6102 | 1.8052 | 6.0692 | 8.8515 | 8.9437 | 8.903 | 8.9953 | 8.9631 | 8.8464 | 118.1456 | 118.1532 | 118.1932 | 118.1242 | 1.9848 | 1.9552 | 1.6239 | 1.8189 | 116.1608 | 116.5217 | 116.2084 | 116.5694
2401.0781 | 117.009 | -53.9612 | 63.0981 | 1.8296 | 2.8991 | 2.7581 | 2.8686 | 2.7876 | 2.7456 | 2.8078 | 89.4842 | 88.8854 | 89.6477 | 89.2992 | 29.7743 | 29.4373 | 29.2361 | 29.3475 | 1.8433 | 2.9128 | 2.7718 | 2.8823 | 2.8014 | 2.7594 | 2.8215 | 89.498 | 88.8991 | 89.6614 | 89.313 | 29.788 | 29.451 | 29.2499 | 29.3612 | 59.7099 | 60.2481 | 59.8734 | 60.4115
2402.8281 | 120.1218 | -2.4078 | 117.5812 | 6.0966 | 8.8378 | 8.9346 | 8.8985 | 8.9953 | 8.9356 | 8.8464 | 117.4268 | 117.4435 | 117.4836 | 117.4053 | 2.4701 | 2.4267 | 2.1046 | 2.2951 | 6.1104 | 8.8515 | 8.9483 | 8.9122 | 9.0091 | 8.9493 | 8.8601 | 117.4405 | 117.4572 | 117.4973 | 117.4191 | 2.4838 | 2.4404 | 2.1184 | 2.3088 | 114.9567 | 115.3222 | 115.0135 | 115.379
2404.5156 | 120.1263 | -2.2751 | 117.9108 | 6.2706 | 9.108 | 9.1956 | 9.164 | 9.2563 | 9.2012 | 9.1074 | 117.761 | 117.7731 | 117.8133 | 117.7442 | 2.2778 | 2.239 | 1.9032 | 2.0891 | 6.2844 | 9.1217 | 9.2093 | 9.1778 | 9.27 | 9.2149 | 9.1211 | 117.7748 | 117.7869 | 117.827 | 117.7579 | 2.2915 | 2.2527 | 1.9169 | 2.1028 | 115.4832 | 115.8578 | 115.5354 | 115.9101
2406.25 | 120.1904 | -2.5452 | 117.7277 | 6.1379 | 8.8744 | 8.9804 | 8.9351 | 9.0274 | 8.986 | 8.8785 | 117.5687 | 117.5717 | 117.6164 | 117.5473 | 2.5433 | 2.5228 | 2.1825 | 2.3729 | 6.1516 | 8.8882 | 8.9941 | 8.9488 | 9.0411 | 8.9997 | 8.8922 | 117.5825 | 117.5854 | 117.6301 | 117.561 | 2.5571 | 2.5366 | 2.1962 | 2.3866 | 115.0254 | 115.3863 | 115.073 | 115.4339
2407.9219 | 117.9565 | -63.2629 | 54.6204 | 2.9833 | 4.5978 | 4.4796 | 4.5718 | 4.4998 | 4.4488 | 4.52 | 97.3364 | 96.7976 | 97.5589 | 97.1752 | 22.5408 | 22.1811 | 22.1534 | 22.1872 | 2.9971 | 4.6116 | 4.4933 | 4.5855 | 4.5135 | 4.4625 | 4.5338 | 97.3501 | 96.8113 | 97.5727 | 97.1889 | 22.5545 | 22.1948 | 22.1671 | 22.201 | 74.7956 | 75.183 | 75.0181 | 75.4056
2409.6562 | 120.0119 | -8.0978 | 111.0992 | 5.5243 | 7.8808 | 7.9731 | 7.9324 | 8.0248 | 7.9833 | 7.8804 | 111.9509 | 111.9672 | 111.9988 | 111.9197 | 7.9227 | 7.8929 | 7.6628 | 7.8667 | 5.5381 | 7.8946 | 7.9868 | 7.9461 | 8.0385 | 7.997 | 7.8941 | 111.9646 | 111.9809 | 112.0126 | 111.9334 | 7.9364 | 7.9066 | 7.6765 | 7.8804 | 104.0282 | 104.2881 | 104.0761 | 104.3361
2411.3906 | 120.1904 | -7.2922 | 112.0148 | 5.6022 | 7.9861 | 8.0784 | 8.056 | 8.1347 | 8.084 | 7.9903 | 112.5003 | 112.5029 | 112.5482 | 112.4737 | 7.3413 | 7.4534 | 7.15 | 7.3219 | 5.6159 | 7.9999 | 8.0921 | 8.0698 | 8.1484 | 8.0978 | 8.004 | 112.5141 | 112.5166 | 112.562 | 112.4874 | 7.355 | 7.4672 | 7.1637 | 7.3356 | 105.1591 | 105.3503 | 105.207 | 105.3982
2413.0625 | 116.1758 | -41.9678 | 78.0029 | -2.0163 | -3.1724 | -3.0751 | -3.143 | -3.0218 | -3.0552 | -3.1942 | 60.0766 | 60.2082 | 60.1819 | 60.0942 | 59.9445 | 59.8723 | 59.6641 | 59.8381 | -2.0025 | -3.1587 | -3.0614 | -3.1292 | -3.0081 | -3.0415 | -3.1805 | 60.0903 | 60.222 | 60.1956 | 60.1079 | 59.9582 | 59.886 | 59.6778 | 59.8519 | 0.13208 | 0.41244 | 0.23738 | 0.51774
2414.8125 | 119.8608 | -31.8008 | 87.7762 | 2.0677 | 2.7205 | 2.8542 | 2.7541 | 2.87 | 2.828 | 2.7071 | 87.1813 | 87.1775 | 87.18 | 87.0967 | 32.773 | 32.7427 | 32.4685 | 32.685 | 2.0814 | 2.7342 | 2.8679 | 2.7679 | 2.8838 | 2.8418 | 2.7208 | 87.195 | 87.1912 | 87.1937 | 87.1105 | 32.7868 | 32.7564 | 32.4822 | 32.6987 | 54.4082 | 54.7128 | 54.407 | 54.7115
2416.5469 | 119.8105 | -35.376 | 83.7021 | 1.2161 | 1.4934 | 1.5859 | 1.5362 | 1.6431 | 1.6148 | 1.4801 | 81.4764 | 81.4906 | 81.4709 | 81.4004 | 38.157 | 38.131 | 37.8893 | 38.0552 | 1.2298 | 1.5071 | 1.5997 | 1.55 | 1.6569 | 1.6285 | 1.4939 | 81.4902 | 81.5043 | 81.4846 | 81.4141 | 38.1707 | 38.1448 | 37.903 | 38.0689 | 43.3195 | 43.5871 | 43.3139 | 43.5816
2418.2812 | 119.458 | -2.7008 | 99.9619 | 6.5545 | 9.2178 | 9.3467 | 9.2739 | 9.3616 | 9.3202 | 9.2218 | 116.8087 | 116.8024 | 116.8518 | 116.7872 | 3.2072 | 3.3148 | 3.002 | 3.2015 | 6.5682 | 9.2316 | 9.3604 | 9.2876 | 9.3753 | 9.3339 | 9.2356 | 116.8224 | 116.8162 | 116.8655 | 116.8009 | 3.2209 | 3.3286 | 3.0157 | 3.2153 | 113.6015 | 113.8067 | 113.6446 | 113.8498
2419.9688 | 120.4971 | -51.0635 | 68.9621 | -0.46418 | -0.69529 | -0.70337 | -0.69806 | -0.65958 | -0.69274 | -0.7586 | 72.4614 | 72.246 | 72.5066 | 72.3568 | 47.8444 | 47.7496 | 47.4902 | 47.6098 | -0.45045 | -0.68156 | -0.68964 | -0.68432 | -0.64585 | -0.67901 | -0.74487 | 72.4751 | 72.2597 | 72.5203 | 72.3705 | 47.8581 | 47.7633 | 47.5039 | 47.6236 | 24.617 | 24.9712 | 24.6622 | 25.0164
2421.7031 | 119.8654 | -119.4031 | 0.24719 | -11.1456 | -16.0389 | -16.0554 | -16.0314 | -15.9729 | -16.0715 | -16.0772 | 3.3902 | 3.2981 | 3.3562 | 3.2546 | 115.876 | 115.9124 | 115.58 | 115.6323 | -11.1318 | -16.0252 | -16.0417 | -16.0177 | -15.9591 | -16.0578 | -16.0634 | 3.4039 | 3.3119 | 3.37 | 3.2684 | 115.8898 | 115.9261 | 115.5937 | 115.6461 | -112.4858 | -112.1898 | -112.5198 | -112.2237
2423.3906 | 120.4102 | -119.8608 | 0.19226 | -11.5805 | -16.7807 | -16.7559 | -16.764 | -16.6595 | -16.7537 | -16.828 | 0.19442 | 0.26237 | 0.2018 | 0.1638 | 119.9826 | 119.9731 | 119.673 | 119.7893 | -11.5668 | -16.7669 | -16.7422 | -16.7503 | -16.6458 | -16.74 | -16.8143 | 0.20815 | 0.2761 | 0.21554 | 0.17753 | 119.9964 | 119.9869 | 119.6868 | 119.803 | -119.7882 | -119.4786 | -119.7808 | -119.4712
2425.0781 | 120.4239 | -120.0027 | 0.20142 | -11.5714 | -16.7898 | -16.7468 | -16.7594 | -16.6687 | -16.7537 | -16.828 | 0.17611 | 0.25779 | 0.19265 | 0.15922 | 120.0696 | 120.0647 | 119.7692 | 119.89 | -11.5576 | -16.7761 | -16.7331 | -16.7457 | -16.655 | -16.74 | -16.8143 | 0.18984 | 0.27152 | 0.20638 | 0.17295 | 120.0834 | 120.0784 | 119.7829 | 119.9038 | -119.8935 | -119.5931 | -119.877 | -119.5765
2426.8125 | 120.5383 | -120.0394 | 0.18768 | -11.64 | -16.8631 | -16.82 | -16.8373 | -16.7282 | -16.827 | -16.8967 | 0.18526 | 0.25321 | 0.1606 | 0.15922 | 120.1291 | 120.1196 | 119.5861 | 119.945 | -11.6263 | -16.8494 | -16.8063 | -16.8235 | -16.7145 | -16.8132 | -16.8829 | 0.199 | 0.26694 | 0.17433 | 0.17295 | 120.1429 | 120.1334 | 119.5998 | 119.9587 | -119.9439 | -119.4008 | -119.9685 | -119.4255
2428.5625 | 119.989 | -119.4534 | 0.27008 | -11.402 | -16.4235 | -16.4217 | -16.4069 | -16.3391 | -16.4424 | -16.4617 | 1.9022 | 1.8375 | 1.8637 | 1.7802 | 117.5837 | 117.62 | 117.2785 | 117.3446 | -11.3882 | -16.4098 | -16.408 | -16.3931 | -16.3254 | -16.4287 | -16.448 | 1.9159 | 1.8512 | 1.8775 | 1.7939 | 117.5974 | 117.6337 | 117.2923 | 117.3583 | -115.6815 | -115.3763 | -115.72 | -115.4148
2430.25 | 120.3827 | -119.9524 | 0.20142 | -11.7774 | -17.0005 | -16.9528 | -16.97 | -16.8701 | -16.9552 | -17.0248 | 0.17611 | 0.25779 | 0.16518 | 0.15464 | 120.033 | 120.0235 | 119.7234 | 119.858 | -11.7636 | -16.9867 | -16.9391 | -16.9563 | -16.8564 | -16.9414 | -17.0111 | 0.18984 | 0.27152 | 0.17891 | 0.16837 | 120.0467 | 120.0372 | 119.7371 | 119.8717 | -119.8569 | -119.5473 | -119.8678 | -119.5582
2431.9219 | 120.4056 | -120.0668 | 0.2243 | -11.8232 | -17.0325 | -16.9849 | -17.0021 | -16.893 | -16.9964 | -17.0615 | 0.18984 | 0.27611 | 0.17433 | 0.085954 | 120.0879 | 120.0784 | 119.5723 | 119.9038 | -11.8094 | -17.0188 | -16.9711 | -16.9883 | -16.8793 | -16.9826 | -17.0477 | 0.20358 | 0.28984 | 0.18807 | 0.099687 | 120.1017 | 120.0922 | 119.5861 | 119.9175 | -119.8981 | -119.3825 | -119.9136 | -119.398
2433.6562 | 116.0477 | -87.4512 | 29.2419 | -10.7015 | -15.5032 | -15.3778 | -15.45 | -15.2999 | -15.3848 | -15.5003 | 6.5219 | 6.7368 | 6.5153 | 6.6065 | 112.6713 | 112.6528 | 112.3339 | 112.5695 | -10.6877 | -15.4895 | -15.3641 | -15.4362 | -15.2862 | -15.3711 | -15.4866 | 6.5356 | 6.7506 | 6.529 | 6.6202 | 112.685 | 112.6665 | 112.3476 | 112.5833 | -106.1494 | -105.812 | -106.156 | -105.8186
2435.4062 | 120.3552 | -119.8654 | 0.20142 | -12.0017 | -17.1653 | -17.1177 | -17.1349 | -17.0258 | -17.1246 | -17.1988 | 0.17611 | 0.25321 | 0.17891 | 0.1638 | 120.0055 | 119.9869 | 119.6914 | 119.8076 | -11.988 | -17.1516 | -17.1039 | -17.1211 | -17.0121 | -17.1108 | -17.1851 | 0.18984 | 0.26694 | 0.19264 | 0.17753 | 120.0193 | 120.0006 | 119.7051 | 119.8214 | -119.8294 | -119.5153 | -119.8266 | -119.5124
2437.1562 | 120.4651 | -119.9844 | 0.21057 | -12.0658 | -17.2111 | -17.1589 | -17.1806 | -17.0761 | -17.1749 | -17.24 | 0.17611 | 0.25779 | 0.14229 | 0.085954 | 120.1017 | 120.1013 | 119.554 | 119.9312 | -12.0521 | -17.1974 | -17.1451 | -17.1669 | -17.0624 | -17.1612 | -17.2263 | 0.18984 | 0.27152 | 0.15602 | 0.099687 | 120.1154 | 120.115 | 119.5677 | 119.945 | -119.9256 | -119.3779 | -119.9594 | -119.4117
2438.8438 | 119.8837 | -119.4992 | 0.11444 | -12.0246 | -16.9959 | -16.9803 | -16.9746 | -16.8884 | -16.9872 | -17.0294 | 1.1147 | 1.114 | 1.0854 | 1.0476 | 118.4764 | 118.499 | 118.1805 | 118.2648 | -12.0109 | -16.9821 | -16.9666 | -16.9609 | -16.8747 | -16.9735 | -17.0157 | 1.1284 | 1.1278 | 1.0991 | 1.0613 | 118.4902 | 118.5127 | 118.1942 | 118.2785 | -117.3617 | -117.0658 | -117.391 | -117.0951
2440.6094 | 119.902 | -119.4305 | 0.18768 | -12.2032 | -17.2569 | -17.2184 | -17.2356 | -17.1357 | -17.2161 | -17.2858 | 0.24936 | 0.33105 | 0.2659 | 0.23706 | 119.4241 | 119.4192 | 119.1236 | 119.2353 | -12.1894 | -17.2431 | -17.2047 | -17.2218 | -17.1219 | -17.2024 | -17.2721 | 0.2631 | 0.34479 | 0.27963 | 0.25079 | 119.4378 | 119.4329 | 119.1374 | 119.2491 | -119.1747 | -118.8743 | -119.1582 | -118.8577
2442.3594 | 120.2133 | -119.7876 | 0.22888 | -12.3085 | -17.3851 | -17.3466 | -17.3638 | -17.2547 | -17.3489 | -17.414 | 0.16237 | 0.23948 | 0.14686 | 0.15006 | 119.9002 | 119.8953 | 119.5906 | 119.7161 | -12.2947 | -17.3713 | -17.3329 | -17.35 | -17.241 | -17.3352 | -17.4003 | 0.1761 | 0.25321 | 0.1606 | 0.16379 | 119.914 | 119.909 | 119.6044 | 119.7298 | -119.7379 | -119.4283 | -119.7534 | -119.4438
2444.0312 | 120.2499 | -119.9295 | 0.2243 | -12.4092 | -17.4767 | -17.429 | -17.4462 | -17.3371 | -17.4313 | -17.501 | 0.15779 | 0.23948 | 0.14686 | 0.053901 | 119.8132 | 119.9869 | 119.4441 | 119.8214 | -12.3955 | -17.4629 | -17.4153 | -17.4325 | -17.3234 | -17.4176 | -17.4872 | 0.17153 | 0.25321 | 0.1606 | 0.067634 | 119.827 | 120.0006 | 119.4579 | 119.8351 | -119.6555 | -119.2863 | -119.6664 | -119.2973
2445.7812 | 120.4285 | -119.9707 | 0.20599 | -12.5282 | -17.5865 | -17.5389 | -17.5652 | -17.4607 | -17.5458 | -17.6154 | 0.16237 | 0.24405 | 0.14229 | 0.063059 | 119.8545 | 120.0555 | 119.5128 | 119.8855 | -12.5145 | -17.5728 | -17.5252 | -17.5515 | -17.447 | -17.5321 | -17.6017 | 0.1761 | 0.25779 | 0.15602 | 0.076792 | 119.8682 | 120.0693 | 119.5265 | 119.8992 | -119.6921 | -119.3504 | -119.7122 | -119.3705
2447.5312 | 120.369 | -120.0531 | 0.2243 | -12.5878 | -17.6186 | -17.5618 | -17.5881 | -17.4836 | -17.5687 | -17.6475 | 0.16237 | 0.24863 | 0.14229 | 0.05848 | 119.9094 | 120.1059 | 119.5677 | 119.9358 | -12.574 | -17.6049 | -17.548 | -17.5744 | -17.4699 | -17.5549 | -17.6337 | 0.1761 | 0.26237 | 0.15602 | 0.072213 | 119.9231 | 120.1196 | 119.5815 | 119.9495 | -119.747 | -119.4054 | -119.7671 | -119.4255
2449.2188 | 120.3873 | -120.0943 | 0.2243 | -12.7022 | -17.7193 | -17.6762 | -17.6889 | -17.5843 | -17.6694 | -17.7482 | 0.16237 | 0.24405 | 0.14686 | 0.063059 | 119.946 | 120.1471 | 119.5998 | 119.977 | -12.6885 | -17.7056 | -17.6625 | -17.6751 | -17.5706 | -17.6557 | -17.7345 | 0.1761 | 0.25779 | 0.1606 | 0.076792 | 119.9597 | 120.1608 | 119.6135 | 119.9907 | -119.7836 | -119.4374 | -119.7992 | -119.4529
2450.9062 | 120.3964 | -120.1492 | 0.23804 | -12.7663 | -17.7651 | -17.7175 | -17.7392 | -17.6347 | -17.7198 | -17.794 | 0.15779 | 0.23948 | 0.14229 | 0.063059 | 119.9826 | 120.1883 | 119.6456 | 120.0091 | -12.7526 | -17.7514 | -17.7037 | -17.7255 | -17.6209 | -17.706 | -17.7802 | 0.17153 | 0.25321 | 0.15602 | 0.076792 | 119.9964 | 120.202 | 119.6593 | 120.0228 | -119.8248 | -119.4878 | -119.8404 | -119.5033
2452.6562 | 120.1355 | -120.1447 | 0.23804 | -12.8304 | -17.8201 | -17.7632 | -17.7896 | -17.685 | -17.7656 | -17.8398 | 0.18069 | 0.27153 | 0.16975 | 0.081375 | 119.9872 | 120.1883 | 119.6502 | 119.7985 | -12.8167 | -17.8063 | -17.7495 | -17.7758 | -17.6713 | -17.7518 | -17.826 | 0.19442 | 0.28526 | 0.18349 | 0.095108 | 120.001 | 120.202 | 119.6639 | 119.8122 | -119.8065 | -119.4695 | -119.8175 | -119.4804
2454.4062 | 120.3598 | -120.1401 | 0.28381 | -12.9403 | -17.9116 | -17.8594 | -17.8811 | -17.7766 | -17.8617 | -17.9313 | 0.20358 | 0.28526 | 0.17891 | 0.095112 | 120.0101 | 120.2112 | 119.6685 | 119.8168 | -12.9266 | -17.8979 | -17.8457 | -17.8674 | -17.7628 | -17.848 | -17.9176 | 0.21731 | 0.299 | 0.19264 | 0.10884 | 120.0238 | 120.2249 | 119.6822 | 119.8305 | -119.8065 | -119.4649 | -119.8312 | -119.4896
2456.0938 | 120.607 | -120.1126 | 0.24719 | -13.0364 | -17.9941 | -17.9372 | -17.9636 | -17.859 | -17.935 | -18.0183 | 0.199 | 0.28526 | 0.17891 | 0.095112 | 120.0238 | 120.2249 | 119.6776 | 119.8305 | -13.0227 | -17.9803 | -17.9235 | -17.9498 | -17.8452 | -17.9212 | -18.0046 | 0.21273 | 0.299 | 0.19264 | 0.10884 | 120.0376 | 120.2387 | 119.6914 | 119.8442 | -119.8248 | -119.4786 | -119.8449 | -119.4987
2457.8281 | 120.1996 | -120.076 | 0.28839 | -13.1463 | -18.0902 | -18.0425 | -18.0597 | -17.9505 | -18.0357 | -18.119 | 0.20816 | 0.28984 | 0.18807 | 0.10427 | 120.0467 | 120.2478 | 119.7143 | 119.858 | -13.1326 | -18.0765 | -18.0288 | -18.046 | -17.9368 | -18.0219 | -18.1053 | 0.22189 | 0.30358 | 0.2018 | 0.118 | 120.0605 | 120.2615 | 119.728 | 119.8717 | -119.8386 | -119.5061 | -119.8587 | -119.5262
2459.5156 | 120.6345 | -120.1584 | 0.27466 | -13.2333 | -18.136 | -18.0929 | -18.1101 | -18.0009 | -18.086 | -18.1694 | 0.20358 | 0.28526 | 0.18349 | 0.099691 | 120.0696 | 120.2707 | 119.728 | 119.8717 | -13.2196 | -18.1223 | -18.0792 | -18.0963 | -17.9872 | -18.0723 | -18.1557 | 0.21731 | 0.299 | 0.19722 | 0.11342 | 120.0834 | 120.2844 | 119.7417 | 119.8854 | -119.866 | -119.5244 | -119.8861 | -119.5445
2461.2656 | 120.1172 | -119.9203 | 0.2655 | -13.3615 | -18.2505 | -18.2028 | -18.22 | -18.1153 | -18.1913 | -18.2747 | 0.21274 | 0.299 | 0.19265 | 0.099691 | 120.0834 | 120.2936 | 119.76 | 119.89 | -13.3478 | -18.2367 | -18.1891 | -18.2062 | -18.1016 | -18.1776 | -18.261 | 0.22647 | 0.31273 | 0.20638 | 0.11342 | 120.0971 | 120.3073 | 119.7738 | 119.9038 | -119.8706 | -119.5473 | -119.8907 | -119.5674
2462.9375 | 120.6619 | -120.2408 | 0.25635 | -13.4485 | -18.3237 | -18.2715 | -18.2932 | -18.184 | -18.2646 | -18.3479 | 0.199 | 0.28526 | 0.18349 | 0.10427 | 120.1154 | 120.3211 | 119.7738 | 119.9221 | -13.4348 | -18.31 | -18.2577 | -18.2795 | -18.1703 | -18.2509 | -18.3342 | 0.21273 | 0.299 | 0.19722 | 0.118 | 120.1291 | 120.3348 | 119.7875 | 119.9358 | -119.9164 | -119.5748 | -119.9319 | -119.5903
2464.6875 | 120.7535 | -120.2362 | 0.25177 | -13.5584 | -18.4336 | -18.3859 | -18.4031 | -18.2939 | -18.3882 | -18.4624 | 0.20358 | 0.28984 | 0.18349 | 0.090533 | 120.1475 | 120.3439 | 119.8058 | 119.9541 | -13.5446 | -18.4199 | -18.3722 | -18.3894 | -18.2801 | -18.3745 | -18.4487 | 0.21731 | 0.30358 | 0.19722 | 0.10427 | 120.1612 | 120.3577 | 119.8196 | 119.9679 | -119.9439 | -119.6022 | -119.964 | -119.6223
2466.4375 | 120.6024 | -120.2591 | 0.28839 | -13.6454 | -18.4977 | -18.4546 | -18.4809 | -18.3717 | -18.4523 | -18.5311 | 0.20358 | 0.28984 | 0.19265 | 0.095112 | 120.1658 | 120.3668 | 119.8241 | 119.9724 | -13.6316 | -18.484 | -18.4409 | -18.4672 | -18.358 | -18.4386 | -18.5173 | 0.21731 | 0.30358 | 0.20638 | 0.10884 | 120.1795 | 120.3806 | 119.8379 | 119.9862 | -119.9622 | -119.6206 | -119.9731 | -119.6315
2468.1094 | 120.7855 | -120.2499 | 0.26093 | -13.7095 | -18.5298 | -18.4775 | -18.4992 | -18.39 | -18.4752 | -18.5585 | 0.21274 | 0.299 | 0.19723 | 0.10427 | 120.1795 | 120.3806 | 119.8424 | 119.9862 | -13.6957 | -18.5161 | -18.4638 | -18.4855 | -18.3763 | -18.4615 | -18.5448 | 0.22647 | 0.31273 | 0.21096 | 0.118 | 120.1932 | 120.3943 | 119.8562 | 119.9999 | -119.9668 | -119.6297 | -119.9823 | -119.6452
2469.8594 | 120.639 | -120.2637 | 0.27466 | -13.7827 | -18.5756 | -18.5279 | -18.545 | -18.4404 | -18.5301 | -18.6043 | 0.21274 | 0.30358 | 0.19265 | 0.10427 | 120.207 | 120.4035 | 119.8562 | 120.0091 | -13.769 | -18.5618 | -18.5141 | -18.5313 | -18.4266 | -18.5164 | -18.5906 | 0.22647 | 0.31731 | 0.20638 | 0.118 | 120.2207 | 120.4172 | 119.8699 | 120.0228 | -119.9942 | -119.6434 | -120.0143 | -119.6635
2471.5312 | 120.7077 | -120.3461 | 0.29755 | -13.8514 | -18.6122 | -18.5599 | -18.5725 | -18.4724 | -18.553 | -18.6318 | 0.21731 | 0.299 | 0.19265 | 0.11343 | 120.2207 | 120.4172 | 119.8837 | 120.0274 | -13.8377 | -18.5985 | -18.5462 | -18.5588 | -18.4587 | -18.5393 | -18.6181 | 0.23105 | 0.31273 | 0.20638 | 0.12716 | 120.2344 | 120.4309 | 119.8974 | 120.0411 | -120.0034 | -119.6663 | -120.0281 | -119.691
2473.2812 | 120.694 | -120.2454 | 0.28381 | -13.9613 | -18.7038 | -18.6515 | -18.6778 | -18.5731 | -18.6492 | -18.7279 | 0.22189 | 0.30816 | 0.2018 | 0.10885 | 120.2299 | 120.4355 | 119.8928 | 120.0457 | -13.9475 | -18.69 | -18.6378 | -18.6641 | -18.5594 | -18.6354 | -18.7142 | 0.23563 | 0.32189 | 0.21554 | 0.12258 | 120.2436 | 120.4492 | 119.9065 | 120.0594 | -120.008 | -119.6709 | -120.0281 | -119.691
2474.9688 | 120.8405 | -120.3323 | 0.27466 | -14.0528 | -18.7587 | -18.7156 | -18.7419 | -18.6327 | -18.7041 | -18.7874 | 0.21731 | 0.30358 | 0.21096 | 0.10427 | 120.2482 | 120.4538 | 119.902 | 120.0457 | -14.0391 | -18.745 | -18.7019 | -18.7282 | -18.6189 | -18.6904 | -18.7737 | 0.23105 | 0.31731 | 0.22469 | 0.118 | 120.2619 | 120.4676 | 119.9157 | 120.0594 | -120.0309 | -119.6847 | -120.0372 | -119.691
2476.7188 | 120.845 | -120.3415 | 0.27008 | -14.1352 | -18.8228 | -18.7751 | -18.7923 | -18.6876 | -18.7636 | -18.8424 | 0.22647 | 0.31274 | 0.20638 | 0.12259 | 120.2665 | 120.463 | 119.9294 | 120.0777 | -14.1215 | -18.8091 | -18.7614 | -18.7785 | -18.6739 | -18.7499 | -18.8287 | 0.2402 | 0.32647 | 0.22012 | 0.13632 | 120.2802 | 120.4767 | 119.9432 | 120.0915 | -120.04 | -119.703 | -120.0601 | -119.7231
2478.4531 | 120.8679 | -120.3598 | 0.27466 | -14.1078 | -18.7129 | -18.6652 | -18.6824 | -18.5823 | -18.6629 | -18.7325 | 0.23105 | 0.31274 | 0.2018 | 0.11801 | 120.2802 | 120.4767 | 119.9386 | 120.0915 | -14.094 | -18.6992 | -18.6515 | -18.6687 | -18.5686 | -18.6492 | -18.7188 | 0.24478 | 0.32647 | 0.21554 | 0.13174 | 120.294 | 120.4904 | 119.9523 | 120.1052 | -120.0492 | -119.7075 | -120.0784 | -119.7368
2480.125 | 120.8359 | -120.3918 | 0.29755 | -14.1352 | -18.6946 | -18.6515 | -18.6686 | -18.564 | -18.6446 | -18.7188 | 0.23105 | 0.32189 | 0.21096 | 0.12259 | 120.2985 | 120.495 | 119.9661 | 120.1006 | -14.1215 | -18.6809 | -18.6378 | -18.6549 | -18.5502 | -18.6309 | -18.705 | 0.24478 | 0.33563 | 0.22469 | 0.13632 | 120.3123 | 120.5088 | 119.9798 | 120.1144 | -120.0675 | -119.735 | -120.0876 | -119.7551
2481.875 | 120.9091 | -120.3827 | 0.28839 | -14.2131 | -18.745 | -18.6973 | -18.719 | -18.6098 | -18.695 | -18.7737 | 0.22647 | 0.32189 | 0.21096 | 0.11343 | 120.3077 | 120.5133 | 119.9752 | 120.1189 | -14.1993 | -18.7313 | -18.6835 | -18.7053 | -18.596 | -18.6812 | -18.76 | 0.2402 | 0.33563 | 0.22469 | 0.12716 | 120.3214 | 120.5271 | 119.989 | 120.1327 | -120.0812 | -119.7487 | -120.0967 | -119.7643
2483.5469 | 120.9366 | -120.4102 | 0.28839 | -14.2314 | -18.7313 | -18.679 | -18.7007 | -18.5869 | -18.6767 | -18.76 | 0.24021 | 0.31732 | 0.21096 | 0.12259 | 120.326 | 120.5179 | 119.9935 | 120.1372 | -14.2177 | -18.7175 | -18.6652 | -18.687 | -18.5731 | -18.6629 | -18.7462 | 0.25394 | 0.33105 | 0.22469 | 0.13632 | 120.3397 | 120.5316 | 120.0073 | 120.151 | -120.0858 | -119.7533 | -120.115 | -119.7826
2485.2812 | 120.9137 | -120.4376 | 0.28381 | -14.2863 | -18.7496 | -18.7064 | -18.7099 | -18.6098 | -18.6858 | -18.7646 | 0.23105 | 0.31732 | 0.21096 | 0.12259 | 120.3397 | 120.55 | 120.0027 | 120.1556 | -14.2726 | -18.7358 | -18.6927 | -18.6961 | -18.596 | -18.6721 | -18.7508 | 0.24478 | 0.33105 | 0.22469 | 0.13632 | 120.3535 | 120.5637 | 120.0164 | 120.1693 | -120.1087 | -119.7716 | -120.1288 | -119.7917
2487.0312 | 120.8633 | -120.4926 | 0.31128 | -14.3687 | -18.7954 | -18.7385 | -18.7602 | -18.6555 | -18.7362 | -18.8195 | 0.22647 | 0.32647 | 0.21096 | 0.12259 | 120.3626 | 120.5637 | 120.0164 | 120.1693 | -14.355 | -18.7816 | -18.7248 | -18.7465 | -18.6418 | -18.7224 | -18.8058 | 0.2402 | 0.34021 | 0.22469 | 0.13632 | 120.3764 | 120.5774 | 120.0302 | 120.183 | -120.1362 | -119.79 | -120.1517 | -119.8055
2488.7812 | 121.0098 | -120.4605 | 0.28839 | -14.181 | -18.5069 | -18.4546 | -18.4718 | -18.3626 | -18.4477 | -18.5402 | 0.23563 | 0.32189 | 0.21554 | 0.12717 | 120.3764 | 120.582 | 120.0393 | 120.1876 | -14.1673 | -18.4932 | -18.4409 | -18.458 | -18.3488 | -18.434 | -18.5265 | 0.24936 | 0.33563 | 0.22927 | 0.1409 | 120.3901 | 120.5957 | 120.053 | 120.2013 | -120.1407 | -119.8037 | -120.1608 | -119.8238
2490.5312 | 121.0327 | -120.4651 | 0.27924 | -14.2268 | -18.4977 | -18.4455 | -18.4718 | -18.3534 | -18.4386 | -18.5311 | 0.23105 | 0.31274 | 0.21554 | 0.12259 | 120.3993 | 120.5957 | 120.0576 | 120.2059 | -14.2131 | -18.484 | -18.4317 | -18.458 | -18.3397 | -18.4248 | -18.5173 | 0.24478 | 0.32647 | 0.22927 | 0.13632 | 120.413 | 120.6095 | 120.0714 | 120.2197 | -120.1682 | -119.8266 | -120.1837 | -119.8421
2492.2188 | 120.8954 | -120.5383 | 0.31128 | -14.2451 | -18.4611 | -18.4088 | -18.4214 | -18.3122 | -18.3974 | -18.4761 | 0.23105 | 0.31732 | 0.22012 | 0.13174 | 120.413 | 120.6141 | 120.0759 | 120.2151 | -14.2314 | -18.4474 | -18.3951 | -18.4077 | -18.2985 | -18.3836 | -18.4624 | 0.24478 | 0.33105 | 0.23385 | 0.14548 | 120.4267 | 120.6278 | 120.0897 | 120.2288 | -120.1819 | -119.8449 | -120.1929 | -119.8558
2493.9531 | 121.0327 | -120.5109 | 0.3067 | -14.3001 | -18.4932 | -18.4409 | -18.4626 | -18.3488 | -18.4294 | -18.5173 | 0.24021 | 0.32647 | 0.2247 | 0.13174 | 120.4267 | 120.6232 | 120.0805 | 120.2334 | -14.2863 | -18.4794 | -18.4271 | -18.4489 | -18.3351 | -18.4157 | -18.5036 | 0.25394 | 0.34021 | 0.23843 | 0.14548 | 120.4405 | 120.6369 | 120.0943 | 120.2471 | -120.1865 | -119.8403 | -120.202 | -119.8558
2495.7031 | 120.9686 | -120.52 | 0.3067 | -14.3642 | -18.5115 | -18.4638 | -18.4764 | -18.3717 | -18.4615 | -18.5356 | 0.24021 | 0.32647 | 0.22012 | 0.13632 | 120.4313 | 120.6324 | 120.0943 | 120.2471 | -14.3504 | -18.4977 | -18.45 | -18.4626 | -18.358 | -18.4477 | -18.5219 | 0.25394 | 0.34021 | 0.23385 | 0.15006 | 120.445 | 120.6461 | 120.108 | 120.2609 | -120.1911 | -119.8541 | -120.2112 | -119.8741
2497.3906 | 121.0144 | -120.52 | 0.30212 | -14.7259 | -18.9236 | -18.8804 | -18.8838 | -18.7791 | -18.8644 | -18.9431 | 0.23563 | 0.33105 | 0.22012 | 0.13174 | 120.4405 | 120.6415 | 120.1034 | 120.2517 | -14.7121 | -18.9098 | -18.8667 | -18.8701 | -18.7654 | -18.8506 | -18.9294 | 0.24936 | 0.34479 | 0.23385 | 0.14548 | 120.4542 | 120.6553 | 120.1171 | 120.2654 | -120.2048 | -119.8678 | -120.2203 | -119.8833
2499.125 | 121.0693 | -120.5429 | 0.28381 | -14.7991 | -18.9556 | -18.9033 | -18.925 | -18.8112 | -18.8964 | -18.9706 | 0.24479 | 0.32647 | 0.22012 | 0.13174 | 120.4542 | 120.669 | 120.1171 | 120.2563 | -14.7854 | -18.9419 | -18.8896 | -18.9113 | -18.7975 | -18.8827 | -18.9568 | 0.25852 | 0.34021 | 0.23385 | 0.14548 | 120.4679 | 120.6827 | 120.1309 | 120.27 | -120.2094 | -119.8724 | -120.2341 | -119.897
2500.875 | 121.0968 | -120.5566 | 0.31128 | -14.4237 | -18.4382 | -18.3905 | -18.4077 | -18.2985 | -18.3699 | -18.4624 | 0.24479 | 0.33105 | 0.22012 | 0.1409 | 120.4771 | 120.6736 | 120.1355 | 120.2838 | -14.41 | -18.4245 | -18.3768 | -18.3939 | -18.2847 | -18.3562 | -18.4487 | 0.25852 | 0.34479 | 0.23385 | 0.15463 | 120.4908 | 120.6873 | 120.1492 | 120.2975 | -120.2323 | -119.8907 | -120.257 | -119.9153
2502.5625 | 121.0602 | -120.5566 | 0.31586 | -14.4695 | -18.4474 | -18.3859 | -18.4077 | -18.2985 | -18.3836 | -18.4578 | 0.24936 | 0.34479 | 0.23385 | 0.13632 | 120.4862 | 120.6781 | 120.1584 | 120.2929 | -14.4557 | -18.4336 | -18.3722 | -18.3939 | -18.2847 | -18.3699 | -18.4441 | 0.2631 | 0.35852 | 0.24758 | 0.15006 | 120.5 | 120.6919 | 120.1721 | 120.3066 | -120.2369 | -119.909 | -120.2524 | -119.9245
2504.3125 | 121.0602 | -120.5933 | 0.29755 | -14.5427 | -18.4703 | -18.4134 | -18.4443 | -18.3259 | -18.4111 | -18.4899 | 0.25394 | 0.34021 | 0.23385 | 0.13632 | 120.4954 | 120.6919 | 120.1492 | 120.2975 | -14.529 | -18.4565 | -18.3997 | -18.4306 | -18.3122 | -18.3974 | -18.4761 | 0.26767 | 0.35394 | 0.24758 | 0.15006 | 120.5091 | 120.7056 | 120.1629 | 120.3112 | -120.2415 | -119.8953 | -120.2615 | -119.9153
2506 | 120.9869 | -120.6116 | 0.32501 | -14.6206 | -18.5115 | -18.4592 | -18.4809 | -18.3717 | -18.4569 | -18.5356 | 0.25852 | 0.34937 | 0.22927 | 0.13632 | 120.5046 | 120.7056 | 120.1675 | 120.3158 | -14.6068 | -18.4977 | -18.4455 | -18.4672 | -18.358 | -18.4432 | -18.5219 | 0.27225 | 0.3631 | 0.24301 | 0.15006 | 120.5183 | 120.7193 | 120.1812 | 120.3295 | -120.246 | -119.909 | -120.2753 | -119.9382
2507.7344 | 121.0098 | -120.6345 | 0.32959 | -14.6663 | -18.5252 | -18.4729 | -18.4947 | -18.3854 | -18.4706 | -18.5494 | 0.25394 | 0.34021 | 0.23385 | 0.14548 | 120.5229 | 120.7194 | 120.1812 | 120.325 | -14.6526 | -18.5115 | -18.4592 | -18.4809 | -18.3717 | -18.4569 | -18.5356 | 0.26767 | 0.35394 | 0.24758 | 0.15921 | 120.5366 | 120.7331 | 120.195 | 120.3387 | -120.2689 | -119.9273 | -120.289 | -119.9474
2509.4688 | 121.1288 | -120.6116 | 0.29755 | -14.7442 | -18.5802 | -18.537 | -18.545 | -18.4404 | -18.5301 | -18.6043 | 0.25852 | 0.34021 | 0.23385 | 0.13632 | 120.5274 | 120.7285 | 120.1812 | 120.3341 | -14.7304 | -18.5664 | -18.5233 | -18.5313 | -18.4266 | -18.5164 | -18.5906 | 0.27225 | 0.35394 | 0.24758 | 0.15006 | 120.5412 | 120.7422 | 120.195 | 120.3478 | -120.2689 | -119.9227 | -120.2936 | -119.9474
2511.1562 | 121.1609 | -120.607 | 0.3067 | -14.8357 | -18.6443 | -18.6011 | -18.6137 | -18.5045 | -18.5897 | -18.6684 | 0.2631 | 0.34937 | 0.24301 | 0.1409 | 120.5412 | 120.7377 | 120.1996 | 120.3478 | -14.822 | -18.6305 | -18.5874 | -18.6 | -18.4907 | -18.5759 | -18.6547 | 0.27683 | 0.3631 | 0.25674 | 0.15463 | 120.5549 | 120.7514 | 120.2133 | 120.3616 | -120.2781 | -119.9365 | -120.2982 | -119.9566
2512.8906 | 121.1746 | -120.6116 | 0.29297 | -14.9044 | -18.6809 | -18.6423 | -18.6549 | -18.5411 | -18.6263 | -18.7142 | 0.26768 | 0.34479 | 0.24301 | 0.15006 | 120.5503 | 120.7422 | 120.2179 | 120.3616 | -14.8907 | -18.6672 | -18.6286 | -18.6412 | -18.5274 | -18.6126 | -18.7005 | 0.28141 | 0.35852 | 0.25674 | 0.16379 | 120.5641 | 120.756 | 120.2316 | 120.3753 | -120.2827 | -119.9502 | -120.3073 | -119.9749
2514.5781 | 121.1792 | -120.6116 | 0.33875 | -14.941 | -18.6855 | -18.6378 | -18.6503 | -18.5457 | -18.6309 | -18.7142 | 0.2631 | 0.34937 | 0.24301 | 0.1409 | 120.5595 | 120.7606 | 120.2225 | 120.3707 | -14.9273 | -18.6717 | -18.624 | -18.6366 | -18.5319 | -18.6171 | -18.7005 | 0.27683 | 0.3631 | 0.25674 | 0.15463 | 120.5732 | 120.7743 | 120.2362 | 120.3845 | -120.2964 | -119.9594 | -120.3165 | -119.9794
2516.3281 | 121.1517 | -120.6711 | 0.33417 | -15.028 | -18.7541 | -18.711 | -18.7327 | -18.6098 | -18.6904 | -18.7737 | 0.24479 | 0.34937 | 0.23385 | 0.1409 | 120.5824 | 120.7834 | 120.2408 | 120.3845 | -15.0143 | -18.7404 | -18.6973 | -18.719 | -18.596 | -18.6767 | -18.76 | 0.25852 | 0.3631 | 0.24758 | 0.15463 | 120.5961 | 120.7972 | 120.2545 | 120.3982 | -120.3376 | -119.996 | -120.3485 | -120.0069
2518.0156 | 121.0831 | -120.6985 | 0.33417 | -15.0647 | -18.7633 | -18.7156 | -18.7282 | -18.6189 | -18.7041 | -18.7829 | 0.25394 | 0.33563 | 0.22927 | 0.13632 | 120.5915 | 120.7972 | 120.2545 | 120.4028 | -15.0509 | -18.7496 | -18.7019 | -18.7144 | -18.6052 | -18.6904 | -18.7691 | 0.26767 | 0.34936 | 0.24301 | 0.15006 | 120.6053 | 120.8109 | 120.2682 | 120.4165 | -120.3376 | -120.0006 | -120.3623 | -120.0252
2519.7656 | 121.2341 | -120.6802 | 0.29297 | -15.1242 | -18.7679 | -18.7293 | -18.7419 | -18.6281 | -18.7179 | -18.7966 | 0.25394 | 0.34937 | 0.23385 | 0.1409 | 120.6098 | 120.8018 | 120.2637 | 120.4211 | -15.1104 | -18.7542 | -18.7156 | -18.7282 | -18.6143 | -18.7041 | -18.7829 | 0.26767 | 0.3631 | 0.24758 | 0.15463 | 120.6236 | 120.8155 | 120.2774 | 120.4348 | -120.3559 | -120.0097 | -120.376 | -120.0298
2521.5156 | 121.225 | -120.7031 | 0.31586 | -15.2157 | -18.8457 | -18.798 | -18.8197 | -18.7105 | -18.782 | -18.8744 | 0.25852 | 0.34937 | 0.22927 | 0.14548 | 120.619 | 120.8155 | 120.2911 | 120.4348 | -15.202 | -18.832 | -18.7843 | -18.806 | -18.6967 | -18.7682 | -18.8607 | 0.27225 | 0.3631 | 0.24301 | 0.15921 | 120.6327 | 120.8292 | 120.3049 | 120.4486 | -120.3605 | -120.0326 | -120.3897 | -120.0619
2523.25 | 121.1517 | -120.7397 | 0.34332 | -15.2707 | -18.864 | -18.8209 | -18.8426 | -18.7288 | -18.814 | -18.9065 | 0.25852 | 0.34479 | 0.24301 | 0.15006 | 120.6236 | 120.8201 | 120.3003 | 120.444 | -15.257 | -18.8503 | -18.8072 | -18.8289 | -18.7151 | -18.8003 | -18.8927 | 0.27225 | 0.35852 | 0.25674 | 0.16379 | 120.6373 | 120.8338 | 120.314 | 120.4577 | -120.3651 | -120.0418 | -120.3806 | -120.0573
2524.9219 | 121.1472 | -120.7581 | 0.32044 | -15.3348 | -18.9236 | -18.8758 | -18.893 | -18.77 | -18.8598 | -18.9339 | 0.25852 | 0.34479 | 0.23843 | 0.14548 | 120.6373 | 120.8384 | 120.3003 | 120.444 | -15.3211 | -18.9098 | -18.8621 | -18.8793 | -18.7563 | -18.8461 | -18.9202 | 0.27225 | 0.35852 | 0.25216 | 0.15921 | 120.6511 | 120.8521 | 120.314 | 120.4577 | -120.3788 | -120.0418 | -120.3989 | -120.0619
2526.6875 | 121.2708 | -120.7214 | 0.30212 | -15.4035 | -18.9602 | -18.8987 | -18.9205 | -18.8066 | -18.8918 | -18.9752 | 0.25394 | 0.35395 | 0.24301 | 0.14548 | 120.6511 | 120.8475 | 120.314 | 120.4577 | -15.3897 | -18.9465 | -18.885 | -18.9067 | -18.7929 | -18.8781 | -18.9614 | 0.26767 | 0.36768 | 0.25674 | 0.15921 | 120.6648 | 120.8613 | 120.3278 | 120.4715 | -120.3971 | -120.0601 | -120.408 | -120.071
2528.4219 | 121.2296 | -120.7535 | 0.32501 | -15.463 | -18.9877 | -18.9537 | -18.9571 | -18.8524 | -18.9376 | -19.0118 | 0.31346 | 0.40889 | 0.30252 | 0.19127 | 120.8021 | 120.788 | 120.3964 | 120.6225 | -15.4492 | -18.9739 | -18.9399 | -18.9434 | -18.8387 | -18.9239 | -18.998 | 0.3272 | 0.42262 | 0.31626 | 0.205 | 120.8159 | 120.8018 | 120.4102 | 120.6363 | -120.4887 | -120.083 | -120.4996 | -120.0939
2530.1094 | 121.1655 | -120.7672 | 0.35248 | -15.5225 | -19.0197 | -18.9766 | -18.9891 | -18.8707 | -18.9559 | -19.0347 | 0.2631 | 0.35395 | 0.24759 | 0.14548 | 120.6694 | 120.8658 | 120.3232 | 120.476 | -15.5088 | -19.006 | -18.9628 | -18.9754 | -18.857 | -18.9422 | -19.0209 | 0.27683 | 0.36768 | 0.26132 | 0.15921 | 120.6831 | 120.8796 | 120.3369 | 120.4898 | -120.4063 | -120.0601 | -120.4218 | -120.0756
2531.8594 | 121.2524 | -120.7581 | 0.32501 | -15.5912 | -19.0655 | -19.0178 | -19.0212 | -18.9165 | -18.9971 | -19.0896 | 0.26768 | 0.35852 | 0.24759 | 0.15006 | 120.6785 | 120.8704 | 120.3323 | 120.4852 | -15.5774 | -19.0518 | -19.004 | -19.0075 | -18.9028 | -18.9834 | -19.0759 | 0.28141 | 0.37226 | 0.26132 | 0.16379 | 120.6923 | 120.8842 | 120.3461 | 120.4989 | -120.4108 | -120.0647 | -120.4309 | -120.0847
2533.6094 | 121.1884 | -120.7764 | 0.33875 | -15.6507 | -19.093 | -19.0407 | -19.0578 | -18.9394 | -19.0338 | -19.1079 | 0.26768 | 0.36768 | 0.26132 | 0.15464 | 120.8388 | 120.8658 | 120.4102 | 120.7004 | -15.637 | -19.0792 | -19.0269 | -19.0441 | -18.9256 | -19.02 | -19.0942 | 0.28141 | 0.38142 | 0.27505 | 0.16837 | 120.8525 | 120.8796 | 120.4239 | 120.7141 | -120.5711 | -120.1425 | -120.5774 | -120.1488
2535.3438 | 121.2158 | -120.7718 | 0.32044 | -15.7011 | -19.1205 | -19.0681 | -19.0899 | -18.9714 | -19.0567 | -19.1445 | 0.2631 | 0.35852 | 0.25674 | 0.15464 | 120.738 | 120.8887 | 120.3873 | 120.531 | -15.6873 | -19.1067 | -19.0544 | -19.0761 | -18.9577 | -19.0429 | -19.1308 | 0.27683 | 0.37226 | 0.27048 | 0.16837 | 120.7518 | 120.9025 | 120.401 | 120.5447 | -120.4749 | -120.1242 | -120.4813 | -120.1305
2537.0312 | 121.344 | -120.7581 | 0.31128 | -15.8109 | -19.2212 | -19.1735 | -19.1814 | -19.0721 | -19.1528 | -19.2315 | 0.27226 | 0.35852 | 0.26132 | 0.15006 | 120.7106 | 120.8979 | 120.3644 | 120.5127 | -15.7972 | -19.2075 | -19.1597 | -19.1677 | -19.0584 | -19.1391 | -19.2178 | 0.28599 | 0.37226 | 0.27505 | 0.16379 | 120.7243 | 120.9116 | 120.3781 | 120.5264 | -120.4383 | -120.0921 | -120.4492 | -120.1031
2538.7188 | 121.2204 | -120.8221 | 0.37079 | -15.843 | -19.2303 | -19.1735 | -19.1952 | -19.0813 | -19.1665 | -19.2407 | 0.26768 | 0.3631 | 0.24759 | 0.15006 | 120.7243 | 120.907 | 120.3735 | 120.5218 | -15.8293 | -19.2166 | -19.1597 | -19.1814 | -19.0676 | -19.1528 | -19.227 | 0.28141 | 0.37684 | 0.26132 | 0.16379 | 120.738 | 120.9208 | 120.3873 | 120.5356 | -120.4566 | -120.1059 | -120.4767 | -120.126
2540.4688 | 121.2067 | -120.6802 | 0.27008 | -15.93 | -19.2807 | -19.2376 | -19.2547 | -19.1408 | -19.2261 | -19.3048 | 0.21731 | 0.30816 | 0.22927 | 0.21875 | 120.8159 | 120.7972 | 120.5017 | 120.6317 | -15.9162 | -19.267 | -19.2238 | -19.241 | -19.1271 | -19.2123 | -19.291 | 0.23105 | 0.32189 | 0.24301 | 0.23248 | 120.8296 | 120.8109 | 120.5155 | 120.6454 | -120.5986 | -120.2844 | -120.5866 | -120.2725
2542.1562 | 120.7901 | -120.2911 | 0.28839 | -15.875 | -19.1388 | -19.0727 | -19.1173 | -19.0126 | -19.107 | -19.172 | 0.68432 | 0.72483 | 0.67794 | 0.64917 | 119.9414 | 119.9411 | 119.641 | 119.7481 | -15.8613 | -19.125 | -19.059 | -19.1036 | -18.9989 | -19.0933 | -19.1583 | 0.69805 | 0.73856 | 0.69168 | 0.66291 | 119.9552 | 119.9548 | 119.6547 | 119.7618 | -119.2571 | -118.9567 | -119.2635 | -118.9631
2543.9062 | 121.0373 | -120.4559 | 0.29755 | -16.0536 | -19.3219 | -19.2788 | -19.2867 | -19.182 | -19.2627 | -19.3551 | 0.23105 | 0.31732 | 0.24301 | 0.21417 | 120.6236 | 120.6049 | 120.3094 | 120.4348 | -16.0399 | -19.3082 | -19.265 | -19.273 | -19.1683 | -19.249 | -19.3414 | 0.24478 | 0.33105 | 0.25674 | 0.2279 | 120.6373 | 120.6186 | 120.3232 | 120.4486 | -120.3925 | -120.0784 | -120.3806 | -120.0664
2545.5781 | 120.7993 | -120.3323 | 0.18768 | -16.104 | -19.3769 | -19.3383 | -19.3463 | -19.2369 | -19.3222 | -19.4055 | 0.34093 | 0.39973 | 0.34373 | 0.32864 | 120.2848 | 120.2661 | 119.9569 | 120.0823 | -16.0902 | -19.3631 | -19.3245 | -19.3325 | -19.2232 | -19.3085 | -19.3918 | 0.35467 | 0.41347 | 0.35746 | 0.34238 | 120.2985 | 120.2799 | 119.9706 | 120.096 | -119.9439 | -119.616 | -119.9411 | -119.6132
2547.3281 | 120.9183 | -120.3827 | 0.28381 | -16.104 | -19.3448 | -19.3017 | -19.3142 | -19.2003 | -19.2947 | -19.378 | 0.35467 | 0.43179 | 0.36662 | 0.35154 | 120.4176 | 120.408 | 120.1034 | 120.2288 | -16.0902 | -19.3311 | -19.2879 | -19.3005 | -19.1866 | -19.281 | -19.3643 | 0.3684 | 0.44552 | 0.38035 | 0.36527 | 120.4313 | 120.4218 | 120.1171 | 120.2425 | -120.0629 | -119.7487 | -120.0509 | -119.7368
2549.0625 | 121.0098 | -120.5841 | 0.31586 | -16.1864 | -19.4318 | -19.3886 | -19.4012 | -19.2873 | -19.3726 | -19.4604 | 0.25852 | 0.34021 | 0.27506 | 0.2508 | 120.6556 | 120.6415 | 120.3415 | 120.476 | -16.1726 | -19.4181 | -19.3749 | -19.3875 | -19.2736 | -19.3588 | -19.4467 | 0.27225 | 0.35394 | 0.28879 | 0.26453 | 120.6694 | 120.6553 | 120.3552 | 120.4898 | -120.3971 | -120.083 | -120.3806 | -120.0664
2550.7969 | 120.9824 | -120.4514 | 0.29755 | -16.2413 | -19.4455 | -19.4024 | -19.4241 | -19.3102 | -19.3955 | -19.4788 | 0.31346 | 0.40889 | 0.33915 | 0.31949 | 120.4771 | 120.463 | 120.1538 | 120.2929 | -16.2276 | -19.4318 | -19.3886 | -19.4104 | -19.2965 | -19.3817 | -19.465 | 0.3272 | 0.42262 | 0.35289 | 0.33322 | 120.4908 | 120.4767 | 120.1675 | 120.3066 | -120.1636 | -119.8403 | -120.1379 | -119.8146
2552.4844 | 121.0464 | -120.4147 | 0.29297 | -16.3695 | -19.5921 | -19.5397 | -19.5569 | -19.4384 | -19.5282 | -19.6115 | 0.22189 | 0.31274 | 0.24301 | 0.2279 | 120.6282 | 120.6141 | 120.3094 | 120.4394 | -16.3558 | -19.5783 | -19.526 | -19.5431 | -19.4246 | -19.5145 | -19.5978 | 0.23563 | 0.32647 | 0.25674 | 0.24164 | 120.6419 | 120.6278 | 120.3232 | 120.4531 | -120.4063 | -120.0875 | -120.3852 | -120.0664
2554.2344 | 120.6848 | -119.7922 | 0.43488 | -13.0044 | -15.4299 | -15.4923 | -15.4362 | -15.4006 | -15.4809 | -15.4957 | 14.1817 | 14.0355 | 14.1793 | 14.0245 | 105.5751 | 105.5705 | 105.2786 | 105.3269 | -12.9907 | -15.4162 | -15.4785 | -15.4225 | -15.3869 | -15.4672 | -15.482 | 14.1955 | 14.0492 | 14.193 | 14.0383 | 105.5889 | 105.5843 | 105.2923 | 105.3406 | -91.3934 | -91.0969 | -91.3958 | -91.0993
2555.9219 | 120.4788 | -119.9203 | 0.25635 | -12.7755 | -15.1003 | -15.2175 | -15.1203 | -15.1168 | -15.2017 | -15.1798 | 15.3172 | 15.0794 | 15.2964 | 15.1143 | 104.2703 | 104.2841 | 103.9829 | 103.9671 | -12.7617 | -15.0865 | -15.2038 | -15.1066 | -15.103 | -15.1879 | -15.1661 | 15.3309 | 15.0932 | 15.3101 | 15.1281 | 104.2841 | 104.2978 | 103.9966 | 103.9809 | -88.9532 | -88.6657 | -88.974 | -88.6865
2557.6562 | 116.7252 | -71.8506 | 44.8196 | -5.0563 | -6.4005 | -6.1473 | -6.3204 | -6.0753 | -6.1593 | -6.3852 | 43.5299 | 43.9534 | 43.668 | 43.715 | 74.0636 | 73.9178 | 73.6877 | 74.035 | -5.0426 | -6.3868 | -6.1336 | -6.3067 | -6.0616 | -6.1456 | -6.3714 | 43.5436 | 43.9672 | 43.6817 | 43.7287 | 74.0773 | 73.9315 | 73.7015 | 74.0488 | -30.5337 | -30.1578 | -30.3956 | -30.0197
2559.4062 | 120.7443 | -120.3873 | 0.25635 | -16.6717 | -19.8073 | -19.7641 | -19.7675 | -19.6627 | -19.7343 | -19.8175 | 0.19442 | 0.28069 | 0.21096 | 0.19127 | 120.4679 | 120.4584 | 120.1675 | 120.2838 | -16.6579 | -19.7935 | -19.7504 | -19.7538 | -19.649 | -19.7205 | -19.8038 | 0.20815 | 0.29442 | 0.22469 | 0.205 | 120.4817 | 120.4721 | 120.1812 | 120.2975 | -120.2735 | -119.9731 | -120.257 | -119.9565
2561.0781 | 120.9595 | -120.4559 | 0.24261 | -16.7037 | -19.8073 | -19.7687 | -19.7858 | -19.6673 | -19.7526 | -19.8313 | 0.18984 | 0.28069 | 0.18349 | 0.099691 | 120.5915 | 120.5729 | 120.0347 | 120.4074 | -16.69 | -19.7935 | -19.7549 | -19.7721 | -19.6535 | -19.7388 | -19.8175 | 0.20358 | 0.29442 | 0.19722 | 0.11342 | 120.6053 | 120.5866 | 120.0485 | 120.4211 | -120.4017 | -119.8449 | -120.408 | -119.8512
2562.8281 | 120.9961 | -120.52 | 0.24719 | -16.69 | -19.7661 | -19.7275 | -19.7354 | -19.6169 | -19.7022 | -19.7901 | 0.20358 | 0.28069 | 0.17891 | 0.090533 | 120.4313 | 120.6415 | 120.0851 | 120.4623 | -16.6763 | -19.7523 | -19.7137 | -19.7217 | -19.6032 | -19.6885 | -19.7763 | 0.21731 | 0.29442 | 0.19264 | 0.10427 | 120.445 | 120.6553 | 120.0988 | 120.476 | -120.2277 | -119.8815 | -120.2524 | -119.9062
2564.5781 | 121.051 | -120.5795 | 0.24261 | -16.7953 | -19.8622 | -19.8145 | -19.827 | -19.713 | -19.8029 | -19.8862 | 0.199 | 0.28069 | 0.19265 | 0.095112 | 120.4771 | 120.6781 | 120.14 | 120.5035 | -16.7816 | -19.8485 | -19.8007 | -19.8133 | -19.6993 | -19.7892 | -19.8725 | 0.21273 | 0.29442 | 0.20638 | 0.10884 | 120.4908 | 120.6919 | 120.1538 | 120.5172 | -120.2781 | -119.941 | -120.2844 | -119.9474
2566.3125 | 121.0968 | -120.5841 | 0.24719 | -17.0105 | -20.0774 | -20.0251 | -20.0422 | -19.9236 | -20.009 | -20.0968 | 0.19442 | 0.28069 | 0.17891 | 0.095112 | 120.5046 | 120.701 | 120.1584 | 120.5356 | -16.9967 | -20.0637 | -20.0113 | -20.0285 | -19.9099 | -19.9952 | -20.0831 | 0.20815 | 0.29442 | 0.19264 | 0.10884 | 120.5183 | 120.7148 | 120.1721 | 120.5493 | -120.3101 | -119.9639 | -120.3256 | -119.9794
2568 | 121.1105 | -120.5978 | 0.25177 | -16.9052 | -19.9126 | -19.8694 | -19.882 | -19.768 | -19.8487 | -19.9411 | 0.19442 | 0.27611 | 0.18349 | 0.099691 | 120.5274 | 120.7422 | 120.1812 | 120.3524 | -16.8914 | -19.8989 | -19.8557 | -19.8682 | -19.7543 | -19.835 | -19.9274 | 0.20815 | 0.28984 | 0.19722 | 0.11342 | 120.5412 | 120.756 | 120.195 | 120.3662 | -120.333 | -119.9868 | -120.344 | -119.9978
2569.75 | 121.0785 | -120.6299 | 0.27466 | -16.9464 | -19.9355 | -19.8969 | -19.9048 | -19.7955 | -19.8716 | -19.9686 | 0.19442 | 0.28984 | 0.17891 | 0.099691 | 120.5549 | 120.756 | 120.2133 | 120.357 | -16.9326 | -19.9217 | -19.8831 | -19.8911 | -19.7817 | -19.8579 | -19.9549 | 0.20815 | 0.30358 | 0.19264 | 0.11342 | 120.5686 | 120.7697 | 120.227 | 120.3707 | -120.3605 | -120.0189 | -120.376 | -120.0344
2571.5 | 120.2316 | -120.2408 | 0.27924 | -17.0013 | -19.9584 | -19.9198 | -19.9232 | -19.8229 | -19.8991 | -19.9869 | 0.18984 | 0.28526 | 0.19265 | 0.095112 | 120.5778 | 120.7697 | 120.2362 | 120.3799 | -16.9876 | -19.9446 | -19.906 | -19.9094 | -19.8092 | -19.8853 | -19.9732 | 0.20358 | 0.299 | 0.20638 | 0.10884 | 120.5915 | 120.7834 | 120.2499 | 120.3936 | -120.388 | -120.0463 | -120.3852 | -120.0435
2573.2344 | 120.2362 | -120.1767 | 0.28381 | -17.0471 | -19.9996 | -19.9472 | -19.9506 | -19.8458 | -19.9265 | -20.019 | 0.18984 | 0.29442 | 0.18349 | 0.099691 | 120.6007 | 120.7972 | 120.2545 | 120.4028 | -17.0334 | -19.9859 | -19.9335 | -19.9369 | -19.8321 | -19.9128 | -20.0052 | 0.20358 | 0.30816 | 0.19722 | 0.11342 | 120.6144 | 120.8109 | 120.2682 | 120.4165 | -120.4109 | -120.0647 | -120.4172 | -120.071
2574.9844 | 121.1563 | -120.6757 | 0.25177 | -17.1249 | -20.05 | -20.0068 | -20.0147 | -19.9007 | -19.9769 | -20.0648 | 0.19442 | 0.28984 | 0.18807 | 0.095112 | 120.6007 | 120.8063 | 120.2728 | 120.4119 | -17.1112 | -20.0362 | -19.993 | -20.001 | -19.887 | -19.9632 | -20.051 | 0.20815 | 0.30358 | 0.2018 | 0.10884 | 120.6144 | 120.8201 | 120.2865 | 120.4257 | -120.4063 | -120.0784 | -120.4126 | -120.0847
2576.75 | 121.0876 | -120.6528 | 0.25635 | -17.1478 | -20.0408 | -19.9839 | -19.9964 | -19.8916 | -19.9678 | -20.0602 | 0.20358 | 0.29442 | 0.18807 | 0.10885 | 120.6236 | 120.8246 | 120.2865 | 120.4303 | -17.1341 | -20.0271 | -19.9701 | -19.9827 | -19.8779 | -19.954 | -20.0464 | 0.21731 | 0.30816 | 0.2018 | 0.12258 | 120.6373 | 120.8384 | 120.3003 | 120.444 | -120.42 | -120.083 | -120.4355 | -120.0985
2578.4375 | 121.2479 | -120.7214 | 0.25177 | -17.2028 | -20.0728 | -20.0297 | -20.0376 | -19.9191 | -20.0044 | -20.1014 | 0.199 | 0.28984 | 0.17891 | 0.10427 | 120.6465 | 120.8475 | 120.3094 | 120.4531 | -17.189 | -20.0591 | -20.0159 | -20.0239 | -19.9053 | -19.9907 | -20.0876 | 0.21273 | 0.30358 | 0.19264 | 0.118 | 120.6602 | 120.8613 | 120.3232 | 120.4669 | -120.4475 | -120.1104 | -120.4676 | -120.1305
2580.1875 | 121.2341 | -120.7443 | 0.2655 | -17.2302 | -20.0728 | -20.0297 | -20.0376 | -19.9328 | -20.0044 | -20.0968 | 0.19442 | 0.28984 | 0.19265 | 0.10427 | 120.6602 | 120.8658 | 120.3232 | 120.4715 | -17.2165 | -20.0591 | -20.0159 | -20.0239 | -19.9191 | -19.9907 | -20.0831 | 0.20815 | 0.30358 | 0.20638 | 0.118 | 120.6739 | 120.8796 | 120.3369 | 120.4852 | -120.4658 | -120.1288 | -120.4676 | -120.1305
2581.8906 | 121.2524 | -120.7077 | 0.25177 | -17.3264 | -20.1598 | -20.1166 | -20.1155 | -20.0106 | -20.0914 | -20.1746 | 0.20816 | 0.299 | 0.18807 | 0.10427 | 120.6785 | 120.8658 | 120.3369 | 120.4715 | -17.3127 | -20.1461 | -20.1029 | -20.1017 | -19.9969 | -20.0776 | -20.1609 | 0.22189 | 0.31273 | 0.2018 | 0.118 | 120.6923 | 120.8796 | 120.3506 | 120.4852 | -120.4704 | -120.1288 | -120.4905 | -120.1488
2583.6406 | 120.9915 | -120.6802 | 0.33417 | -17.363 | -20.1736 | -20.1304 | -20.1383 | -20.0335 | -20.1051 | -20.2067 | 0.21731 | 0.30358 | 0.20638 | 0.11801 | 120.6831 | 120.8704 | 120.3323 | 120.4852 | -17.3493 | -20.1598 | -20.1166 | -20.1246 | -20.0198 | -20.0914 | -20.1929 | 0.23105 | 0.31731 | 0.22012 | 0.13174 | 120.6968 | 120.8842 | 120.3461 | 120.4989 | -120.4658 | -120.115 | -120.4767 | -120.1259
2585.3906 | 121.1929 | -120.7535 | 0.31128 | -17.4363 | -20.2285 | -20.1762 | -20.1841 | -20.0747 | -20.1463 | -20.2525 | 0.22647 | 0.31732 | 0.21554 | 0.13174 | 120.6785 | 120.875 | 120.3415 | 120.4943 | -17.4225 | -20.2148 | -20.1624 | -20.1704 | -20.061 | -20.1326 | -20.2387 | 0.2402 | 0.33105 | 0.22927 | 0.14548 | 120.6923 | 120.8887 | 120.3552 | 120.5081 | -120.4521 | -120.115 | -120.463 | -120.126
2587.1406 | 121.2753 | -120.7214 | 0.28839 | -17.5782 | -20.3567 | -20.3089 | -20.3123 | -20.2029 | -20.2882 | -20.3806 | 0.23563 | 0.31274 | 0.21096 | 0.11801 | 120.6785 | 120.8887 | 120.3369 | 120.4898 | -17.5645 | -20.343 | -20.2952 | -20.2986 | -20.1892 | -20.2745 | -20.3669 | 0.24936 | 0.32647 | 0.22469 | 0.13174 | 120.6923 | 120.9025 | 120.3506 | 120.5035 | -120.4429 | -120.1013 | -120.4676 | -120.126
2588.8281 | 121.2616 | -120.7764 | 0.3067 | -17.624 | -20.3842 | -20.3364 | -20.3444 | -20.2258 | -20.3066 | -20.4081 | 0.23563 | 0.31732 | 0.21096 | 0.13174 | 120.7014 | 120.8887 | 120.3598 | 120.4989 | -17.6102 | -20.3705 | -20.3227 | -20.3306 | -20.212 | -20.2928 | -20.3944 | 0.24936 | 0.33105 | 0.22469 | 0.14548 | 120.7151 | 120.9025 | 120.3735 | 120.5127 | -120.4658 | -120.1242 | -120.4905 | -120.1488
2590.5781 | 121.1014 | -120.5841 | 0.32044 | -17.6789 | -20.4254 | -20.3776 | -20.3947 | -20.2807 | -20.3478 | -20.4493 | 0.23563 | 0.32647 | 0.22012 | 0.12717 | 120.7014 | 120.9025 | 120.369 | 120.5035 | -17.6652 | -20.4117 | -20.3639 | -20.381 | -20.267 | -20.334 | -20.4356 | 0.24936 | 0.34021 | 0.23385 | 0.1409 | 120.7151 | 120.9162 | 120.3827 | 120.5172 | -120.4658 | -120.1333 | -120.4813 | -120.1488
2592.3281 | 121.3074 | -120.7718 | 0.3067 | -17.8621 | -20.6086 | -20.5562 | -20.5687 | -20.4547 | -20.5263 | -20.6324 | 0.23563 | 0.32647 | 0.2247 | 0.13632 | 120.7151 | 120.9116 | 120.3735 | 120.531 | -17.8483 | -20.5948 | -20.5425 | -20.555 | -20.4409 | -20.5126 | -20.6187 | 0.24936 | 0.34021 | 0.23843 | 0.15006 | 120.7289 | 120.9254 | 120.3873 | 120.5447 | -120.4795 | -120.1379 | -120.4905 | -120.1488
2594.0156 | 121.0098 | -120.5429 | 0.30212 | -17.8025 | -20.4987 | -20.4509 | -20.4497 | -20.354 | -20.421 | -20.518 | 0.22189 | 0.31732 | 0.24759 | 0.2279 | 120.7243 | 120.7056 | 120.4056 | 120.531 | -17.7888 | -20.4849 | -20.4371 | -20.436 | -20.3402 | -20.4073 | -20.5043 | 0.23563 | 0.33105 | 0.26132 | 0.24164 | 120.738 | 120.7193 | 120.4193 | 120.5447 | -120.5024 | -120.1837 | -120.4767 | -120.158
2595.7656 | 121.17 | -120.694 | 0.31586 | -17.8575 | -20.5445 | -20.4967 | -20.5 | -20.3997 | -20.476 | -20.5684 | 0.22647 | 0.31732 | 0.20638 | 0.13632 | 120.6648 | 120.8109 | 120.2728 | 120.6454 | -17.8437 | -20.5307 | -20.4829 | -20.4863 | -20.386 | -20.4622 | -20.5546 | 0.2402 | 0.33105 | 0.22012 | 0.15006 | 120.6785 | 120.8246 | 120.2865 | 120.6592 | -120.4383 | -120.0463 | -120.4584 | -120.0664
2597.4688 | 121.2296 | -120.7214 | 0.28839 | -17.9857 | -20.6452 | -20.6066 | -20.6145 | -20.5005 | -20.5813 | -20.6737 | 0.22647 | 0.31732 | 0.21554 | 0.12717 | 120.6419 | 120.8475 | 120.3003 | 120.6866 | -17.9719 | -20.6315 | -20.5928 | -20.6008 | -20.4867 | -20.5675 | -20.6599 | 0.2402 | 0.33105 | 0.22927 | 0.1409 | 120.6556 | 120.8613 | 120.314 | 120.7004 | -120.4154 | -120.0738 | -120.4264 | -120.0847
2599.2031 | 121.1563 | -120.7352 | 0.3067 | -17.9399 | -20.5719 | -20.5287 | -20.5321 | -20.4226 | -20.5034 | -20.5912 | 0.22647 | 0.33105 | 0.22012 | 0.12717 | 120.6739 | 120.8658 | 120.3232 | 120.5172 | -17.9262 | -20.5582 | -20.515 | -20.5184 | -20.4089 | -20.4897 | -20.5775 | 0.2402 | 0.34479 | 0.23385 | 0.1409 | 120.6877 | 120.8796 | 120.3369 | 120.531 | -120.4475 | -120.0967 | -120.4538 | -120.1031
2600.8906 | 121.3028 | -120.7855 | 0.29755 | -17.9399 | -20.5536 | -20.515 | -20.5138 | -20.4043 | -20.4805 | -20.5775 | 0.23563 | 0.33105 | 0.22012 | 0.13174 | 120.6831 | 120.8933 | 120.3461 | 120.4943 | -17.9262 | -20.5399 | -20.5012 | -20.5001 | -20.3906 | -20.4668 | -20.5638 | 0.24936 | 0.34479 | 0.23385 | 0.14548 | 120.6968 | 120.907 | 120.3598 | 120.5081 | -120.4475 | -120.1104 | -120.463 | -120.126
2602.6406 | 121.1792 | -120.8221 | 0.32501 | -18.0223 | -20.6086 | -20.5653 | -20.5687 | -20.4593 | -20.5401 | -20.6324 | 0.24021 | 0.32647 | 0.21096 | 0.12717 | 120.7014 | 120.9025 | 120.3644 | 120.5127 | -18.0086 | -20.5948 | -20.5516 | -20.555 | -20.4455 | -20.5263 | -20.6187 | 0.25394 | 0.34021 | 0.22469 | 0.1409 | 120.7151 | 120.9162 | 120.3781 | 120.5264 | -120.4612 | -120.1242 | -120.4905 | -120.1534
2604.3906 | 120.9869 | -119.5221 | 1.3916 | -18.0223 | -20.5903 | -20.547 | -20.5458 | -20.4364 | -20.5263 | -20.6096 | 0.29973 | 0.386 | 0.27048 | 0.17296 | 120.6923 | 120.8521 | 120.3415 | 120.4852 | -18.0086 | -20.5765 | -20.5333 | -20.5321 | -20.4226 | -20.5126 | -20.5958 | 0.31346 | 0.39973 | 0.28421 | 0.18669 | 120.706 | 120.8658 | 120.3552 | 120.4989 | -120.3925 | -120.0418 | -120.4218 | -120.071
2606.1406 | 118.2587 | -86.2015 | 31.6498 | -9.9048 | -11.5746 | -11.3349 | -11.4804 | -11.2759 | -11.3741 | -11.5539 | 27.4502 | 27.7811 | 27.557 | 27.5876 | 91.2592 | 91.1771 | 90.9025 | 91.194 | -9.8911 | -11.5608 | -11.3212 | -11.4667 | -11.2621 | -11.3604 | -11.5402 | 27.4639 | 27.7948 | 27.5708 | 27.6014 | 91.2729 | 91.1908 | 90.9162 | 91.2078 | -63.809 | -63.4523 | -63.7022 | -63.3454
2607.8906 | 121.0556 | -120.5338 | 0.27924 | -18.1001 | -20.6086 | -20.5608 | -20.5687 | -20.4547 | -20.5309 | -20.637 | 0.22647 | 0.32189 | 0.24301 | 0.23706 | 120.7151 | 120.6965 | 120.3964 | 120.5264 | -18.0864 | -20.5948 | -20.547 | -20.555 | -20.4409 | -20.5172 | -20.6233 | 0.2402 | 0.33563 | 0.25674 | 0.25079 | 120.7289 | 120.7102 | 120.4102 | 120.5401 | -120.4887 | -120.17 | -120.4721 | -120.1534
2609.6406 | 121.0785 | -120.6528 | 0.31128 | -18.1825 | -20.6864 | -20.634 | -20.642 | -20.5325 | -20.6042 | -20.7103 | 0.24021 | 0.32647 | 0.22012 | 0.13174 | 120.793 | 120.7743 | 120.2362 | 120.6042 | -18.1688 | -20.6727 | -20.6203 | -20.6282 | -20.5188 | -20.5904 | -20.6965 | 0.25394 | 0.34021 | 0.23385 | 0.14548 | 120.8067 | 120.788 | 120.2499 | 120.618 | -120.5528 | -119.996 | -120.5729 | -120.0161
2611.3906 | 120.845 | -120.3323 | 0.39825 | -18.1093 | -20.5674 | -20.4784 | -20.5275 | -20.4135 | -20.4943 | -20.5958 | 0.31346 | 0.40431 | 0.32999 | 0.31491 | 120.4588 | 120.4447 | 120.1446 | 120.2838 | -18.0956 | -20.5536 | -20.4646 | -20.5138 | -20.3997 | -20.4805 | -20.5821 | 0.3272 | 0.41805 | 0.34373 | 0.32864 | 120.4725 | 120.4584 | 120.1584 | 120.2975 | -120.1453 | -119.8312 | -120.1288 | -119.8146
2613.0781 | 121.0785 | -120.5154 | 0.31128 | -18.1047 | -20.5445 | -20.4509 | -20.5 | -20.386 | -20.4714 | -20.5638 | 0.24479 | 0.34021 | 0.23385 | 0.1409 | 120.6648 | 120.6415 | 120.1034 | 120.4806 | -18.091 | -20.5307 | -20.4371 | -20.4863 | -20.3723 | -20.4576 | -20.55 | 0.25852 | 0.35394 | 0.24758 | 0.15463 | 120.6785 | 120.6553 | 120.1171 | 120.4943 | -120.42 | -119.8586 | -120.4309 | -119.8696
2614.8281 | 120.9869 | -120.6253 | 0.33875 | -18.2604 | -20.6773 | -20.602 | -20.6328 | -20.5279 | -20.6087 | -20.7057 | 0.25394 | 0.34021 | 0.22927 | 0.14548 | 120.5046 | 120.701 | 120.1675 | 120.531 | -18.2466 | -20.6635 | -20.5882 | -20.6191 | -20.5142 | -20.595 | -20.692 | 0.26767 | 0.35394 | 0.24301 | 0.15921 | 120.5183 | 120.7148 | 120.1812 | 120.5447 | -120.2506 | -119.9136 | -120.2753 | -119.9382
2616.5 | 121.1517 | -120.5933 | 0.28381 | -18.2695 | -20.6956 | -20.5974 | -20.6374 | -20.5279 | -20.6042 | -20.7011 | 0.24936 | 0.34937 | 0.23385 | 0.1409 | 120.5366 | 120.7377 | 120.1904 | 120.5676 | -18.2558 | -20.6818 | -20.5837 | -20.6237 | -20.5142 | -20.5904 | -20.6874 | 0.2631 | 0.3631 | 0.24758 | 0.15463 | 120.5503 | 120.7514 | 120.2041 | 120.5813 | -120.2872 | -119.941 | -120.3027 | -119.9566
2618.25 | 121.1105 | -120.6802 | 0.33417 | -18.3062 | -20.691 | -20.6066 | -20.642 | -20.5325 | -20.6179 | -20.7149 | 0.25852 | 0.34479 | 0.23385 | 0.14548 | 120.5686 | 120.7651 | 120.2225 | 120.3845 | -18.2924 | -20.6773 | -20.5928 | -20.6282 | -20.5188 | -20.6042 | -20.7011 | 0.27225 | 0.35852 | 0.24758 | 0.15921 | 120.5824 | 120.7789 | 120.2362 | 120.3982 | -120.3101 | -119.9639 | -120.3348 | -119.9886
2619.9531 | 121.1975 | -120.6482 | 0.33417 | -18.3245 | -20.6773 | -20.5974 | -20.6374 | -20.5233 | -20.6087 | -20.7011 | 0.25852 | 0.34479 | 0.23385 | 0.15006 | 120.5915 | 120.7743 | 120.2453 | 120.4028 | -18.3107 | -20.6635 | -20.5837 | -20.6237 | -20.5096 | -20.595 | -20.6874 | 0.27225 | 0.35852 | 0.24758 | 0.16379 | 120.6053 | 120.788 | 120.2591 | 120.4165 | -120.333 | -119.9868 | -120.3577 | -120.0115
2621.7031 | 121.0327 | -118.7393 | 2.4261 | -18.1597 | -20.4804 | -20.3914 | -20.4451 | -20.3265 | -20.4027 | -20.5043 | 0.83083 | 0.93546 | 0.80614 | 0.69954 | 120.1291 | 120.1746 | 119.7326 | 119.8946 | -18.1459 | -20.4666 | -20.3776 | -20.4314 | -20.3128 | -20.389 | -20.4905 | 0.84457 | 0.94919 | 0.81987 | 0.71328 | 120.1429 | 120.1883 | 119.7463 | 119.9083 | -119.2983 | -118.9017 | -119.323 | -118.9264
2623.4531 | 121.0373 | -120.3415 | 0.48065 | -18.3199 | -20.6315 | -20.5516 | -20.587 | -20.4821 | -20.5584 | -20.6508 | 0.41419 | 0.50963 | 0.43072 | 0.41107 | 120.5183 | 120.4859 | 120.2041 | 120.3295 | -18.3062 | -20.6177 | -20.5379 | -20.5733 | -20.4684 | -20.5446 | -20.637 | 0.42792 | 0.52336 | 0.44445 | 0.4248 | 120.532 | 120.4996 | 120.2179 | 120.3433 | -120.1041 | -119.7899 | -120.0876 | -119.7734
2625.125 | 121.0556 | -120.2866 | 0.60425 | -18.3382 | -20.6269 | -20.5287 | -20.5916 | -20.4776 | -20.5446 | -20.6462 | 0.52865 | 0.61952 | 0.49481 | 0.35612 | 120.239 | 120.4126 | 119.8928 | 120.2471 | -18.3245 | -20.6132 | -20.515 | -20.5779 | -20.4638 | -20.5309 | -20.6325 | 0.54238 | 0.63325 | 0.50855 | 0.36985 | 120.2528 | 120.4264 | 119.9065 | 120.2609 | -119.7104 | -119.3642 | -119.7442 | -119.398
2626.875 | 120.9915 | -119.9753 | 0.88348 | -18.297 | -20.5582 | -20.4829 | -20.5229 | -20.4089 | -20.4897 | -20.5821 | 0.84915 | 0.94003 | 0.81987 | 0.67207 | 120.0879 | 120.0693 | 119.7646 | 119.9038 | -18.2833 | -20.5445 | -20.4692 | -20.5092 | -20.3952 | -20.476 | -20.5684 | 0.86288 | 0.95377 | 0.8336 | 0.6858 | 120.1017 | 120.083 | 119.7783 | 119.9175 | -119.2388 | -118.9155 | -119.2681 | -118.9447
2628.6406 | 120.7031 | -119.5358 | 1.0345 | -18.2329 | -20.4529 | -20.3685 | -20.4131 | -20.3036 | -20.3752 | -20.4722 | 0.90867 | 0.99498 | 0.92517 | 0.91018 | 119.7125 | 119.6939 | 119.4075 | 119.5284 | -18.2192 | -20.4392 | -20.3547 | -20.3993 | -20.2899 | -20.3615 | -20.4585 | 0.9224 | 1.0087 | 0.9389 | 0.92391 | 119.7263 | 119.7076 | 119.4212 | 119.5421 | -118.8039 | -118.4988 | -118.7874 | -118.4823
2630.3281 | 120.7901 | -119.0781 | 1.4465 | -18.0956 | -20.2789 | -20.1991 | -20.2391 | -20.1205 | -20.2013 | -20.3074 | 1.3803 | 1.4758 | 1.351 | 1.2124 | 119.2639 | 119.2361 | 118.7299 | 119.0751 | -18.0818 | -20.2652 | -20.1853 | -20.2253 | -20.1068 | -20.1875 | -20.2937 | 1.394 | 1.4895 | 1.3647 | 1.2261 | 119.2776 | 119.2498 | 118.7436 | 119.0888 | -117.8836 | -117.3496 | -117.9129 | -117.3789
2632.0781 | 120.6619 | -118.5562 | 1.9409 | -17.9903 | -20.1324 | -20.0525 | -20.0926 | -19.974 | -20.0593 | -20.1563 | 1.9342 | 2.0252 | 1.9095 | 1.7665 | 118.481 | 118.6134 | 118.0981 | 118.4479 | -17.9765 | -20.1186 | -20.0388 | -20.0788 | -19.9603 | -20.0456 | -20.1426 | 1.948 | 2.0389 | 1.9232 | 1.7802 | 118.4947 | 118.6272 | 118.1118 | 118.4616 | -116.5468 | -116.1638 | -116.5715 | -116.1886
2633.8281 | 120.7031 | -116.8671 | 3.3096 | -17.6423 | -19.7157 | -19.6359 | -19.6805 | -19.5711 | -19.6564 | -19.7443 | 2.9919 | 3.0692 | 2.9946 | 2.9799 | 117.3685 | 117.3407 | 117.0405 | 117.1752 | -17.6286 | -19.702 | -19.6222 | -19.6668 | -19.5574 | -19.6427 | -19.7306 | 3.0056 | 3.0829 | 3.0083 | 2.9936 | 117.3822 | 117.3545 | 117.0542 | 117.1889 | -114.3766 | -114.0486 | -114.3739 | -114.0459
2635.5625 | 120.3827 | -116.7252 | 3.4195 | -17.3218 | -19.3357 | -19.2604 | -19.3005 | -19.1957 | -19.281 | -19.3643 | 3.8938 | 3.9712 | 3.869 | 3.7675 | 116.2423 | 116.2557 | 115.8455 | 116.0856 | -17.3081 | -19.3219 | -19.2467 | -19.2867 | -19.182 | -19.2673 | -19.3506 | 3.9076 | 3.9849 | 3.8827 | 3.7812 | 116.256 | 116.2695 | 115.8592 | 116.0993 | -112.3484 | -111.9517 | -112.3733 | -111.9765
2637.2344 | 119.7739 | -110.4584 | 9.0271 | -16.0765 | -17.9574 | -17.8731 | -17.9269 | -17.8132 | -17.8983 | -17.9863 | 7.8771 | 7.9731 | 7.8521 | 7.7558 | 111.774 | 111.7647 | 111.3724 | 111.6081 | -16.0628 | -17.9437 | -17.8594 | -17.9132 | -17.7995 | -17.8846 | -17.9725 | 7.8909 | 7.9868 | 7.8658 | 7.7696 | 111.7877 | 111.7784 | 111.3862 | 111.6218 | -103.8968 | -103.4953 | -103.9219 | -103.5203
2638.9219 | 120.8267 | -120.314 | 0.23804 | -18.5671 | -20.6773 | -20.5928 | -20.642 | -20.5233 | -20.5996 | -20.6965 | 0.18526 | 0.27611 | 0.17891 | 0.090533 | 120.294 | 120.4813 | 119.9523 | 120.325 | -18.5534 | -20.6635 | -20.5791 | -20.6282 | -20.5096 | -20.5858 | -20.6828 | 0.199 | 0.28984 | 0.19264 | 0.10427 | 120.3077 | 120.495 | 119.9661 | 120.3387 | -120.1087 | -119.7671 | -120.115 | -119.7734
2640.6562 | 120.9686 | -120.4468 | 0.23804 | -18.6404 | -20.7505 | -20.6615 | -20.7152 | -20.6012 | -20.6728 | -20.779 | 0.18526 | 0.27611 | 0.17433 | 0.099691 | 120.3901 | 120.5729 | 120.0531 | 120.1968 | -18.6266 | -20.7368 | -20.6478 | -20.7015 | -20.5874 | -20.6591 | -20.7652 | 0.199 | 0.28984 | 0.18807 | 0.11342 | 120.4038 | 120.5866 | 120.0668 | 120.2105 | -120.2048 | -119.8678 | -120.2158 | -119.8787
2642.4062 | 117.4393 | -90.8981 | 26.6327 | -11.7636 | -13.3328 | -13.0656 | -13.2386 | -13.0063 | -13.0956 | -13.3074 | 21.0632 | 21.444 | 21.1566 | 21.2502 | 97.2657 | 97.1469 | 96.9047 | 97.2143 | -11.7499 | -13.3191 | -13.0519 | -13.2248 | -12.9926 | -13.0819 | -13.2936 | 21.0769 | 21.4577 | 21.1703 | 21.264 | 97.2795 | 97.1606 | 96.9185 | 97.2281 | -76.2025 | -75.8415 | -76.1092 | -75.7481
2644.0938 | 120.7581 | -120.2087 | 0.22888 | -18.6266 | -20.6773 | -20.602 | -20.642 | -20.5325 | -20.6133 | -20.7057 | 0.18526 | 0.27611 | 0.2018 | 0.18211 | 120.3947 | 120.3714 | 120.0897 | 120.2105 | -18.6129 | -20.6635 | -20.5882 | -20.6282 | -20.5188 | -20.5996 | -20.692 | 0.199 | 0.28984 | 0.21554 | 0.19585 | 120.4084 | 120.3851 | 120.1034 | 120.2242 | -120.2094 | -119.9044 | -120.1929 | -119.8879
2645.8281 | 120.7764 | -120.3461 | 0.27008 | -18.677 | -20.7139 | -20.6432 | -20.6832 | -20.5691 | -20.6408 | -20.7469 | 0.18984 | 0.28526 | 0.17433 | 0.11343 | 120.5046 | 120.463 | 119.9432 | 120.3066 | -18.6633 | -20.7001 | -20.6295 | -20.6695 | -20.5554 | -20.627 | -20.7332 | 0.20358 | 0.299 | 0.18807 | 0.12716 | 120.5183 | 120.4767 | 119.9569 | 120.3204 | -120.3147 | -119.7533 | -120.3302 | -119.7688
2647.5938 | 119.4031 | -116.8076 | 3.3508 | -18.6999 | -20.7093 | -20.634 | -20.674 | -20.5691 | -20.6454 | -20.7423 | 0.21731 | 0.30358 | 0.22927 | 0.21417 | 120.1887 | 120.1608 | 119.8699 | 119.9999 | -18.6862 | -20.6956 | -20.6203 | -20.6603 | -20.5554 | -20.6316 | -20.7286 | 0.23105 | 0.31731 | 0.24301 | 0.2279 | 120.2024 | 120.1746 | 119.8836 | 120.0136 | -119.9713 | -119.6526 | -119.9594 | -119.6406
2649.2812 | 116.6382 | -86.6592 | 29.7867 | -10.6923 | -12.1423 | -11.8385 | -12.0527 | -11.7932 | -11.8915 | -12.1079 | 24.204 | 24.6171 | 24.3156 | 24.3915 | 93.7589 | 93.6126 | 93.3839 | 93.7166 | -10.6786 | -12.1286 | -11.8248 | -12.039 | -11.7794 | -11.8777 | -12.0942 | 24.2178 | 24.6308 | 24.3293 | 24.4052 | 93.7726 | 93.6264 | 93.3977 | 93.7303 | -69.5548 | -69.1799 | -69.4433 | -69.0683
2651.0312 | 119.5953 | -119.1238 | 0.22888 | -11.4615 | -12.8154 | -12.681 | -12.7761 | -12.6264 | -12.711 | -12.8496 | 22.4688 | 22.6528 | 22.553 | 22.5141 | 95.4848 | 95.366 | 95.142 | 95.3281 | -11.4477 | -12.8017 | -12.6673 | -12.7624 | -12.6126 | -12.6973 | -12.8358 | 22.4825 | 22.6665 | 22.5667 | 22.5278 | 95.4986 | 95.3798 | 95.1558 | 95.3419 | -73.016 | -72.6732 | -72.9319 | -72.5891
2652.7969 | 120.5658 | -120.1721 | 0.24261 | -18.9105 | -20.8879 | -20.8446 | -20.8389 | -20.7339 | -20.8148 | -20.9117 | 0.15321 | 0.25779 | 0.18349 | 0.16838 | 120.3214 | 120.2799 | 119.9981 | 120.1281 | -18.8968 | -20.8741 | -20.8309 | -20.8251 | -20.7202 | -20.801 | -20.898 | 0.16695 | 0.27152 | 0.19722 | 0.18211 | 120.3352 | 120.2936 | 120.0118 | 120.1418 | -120.1682 | -119.8449 | -120.1379 | -119.8146
2654.4844 | 120.7626 | -120.1447 | 0.32959 | -18.8693 | -20.8192 | -20.776 | -20.7885 | -20.6698 | -20.7507 | -20.8476 | 0.23105 | 0.33105 | 0.2247 | 0.13632 | 120.3489 | 120.3119 | 119.8333 | 120.1556 | -18.8556 | -20.8055 | -20.7622 | -20.7748 | -20.6561 | -20.7369 | -20.8339 | 0.24478 | 0.34479 | 0.23843 | 0.15006 | 120.3626 | 120.3256 | 119.847 | 120.1693 | -120.1178 | -119.6022 | -120.1242 | -119.6086
2656.2344 | 120.6528 | -120.2682 | 0.24719 | -18.9197 | -20.8604 | -20.8126 | -20.8205 | -20.711 | -20.7827 | -20.8842 | 0.16695 | 0.24863 | 0.18807 | 0.16838 | 120.3947 | 120.3714 | 120.0805 | 120.2151 | -18.9059 | -20.8467 | -20.7989 | -20.8068 | -20.6973 | -20.769 | -20.8705 | 0.18068 | 0.26237 | 0.2018 | 0.18211 | 120.4084 | 120.3851 | 120.0943 | 120.2288 | -120.2277 | -119.9136 | -120.2066 | -119.8925
2657.9688 | 120.726 | -120.3552 | 0.25635 | -18.9288 | -20.8375 | -20.7943 | -20.8068 | -20.6927 | -20.7644 | -20.8659 | 0.18069 | 0.27611 | 0.16518 | 0.081375 | 120.4084 | 120.4401 | 119.902 | 120.2838 | -18.9151 | -20.8238 | -20.7805 | -20.7931 | -20.679 | -20.7507 | -20.8522 | 0.19442 | 0.28984 | 0.17891 | 0.095108 | 120.4221 | 120.4538 | 119.9157 | 120.2975 | -120.2277 | -119.7213 | -120.2432 | -119.7368
2659.7031 | 120.639 | -120.1355 | 0.21515 | -18.9288 | -20.8192 | -20.7714 | -20.7839 | -20.679 | -20.7461 | -20.8476 | 0.17153 | 0.26695 | 0.19723 | 0.18211 | 120.2756 | 120.2387 | 119.9615 | 120.0869 | -18.9151 | -20.8055 | -20.7577 | -20.7702 | -20.6653 | -20.7323 | -20.8339 | 0.18526 | 0.28068 | 0.21096 | 0.19585 | 120.2894 | 120.2524 | 119.9752 | 120.1006 | -120.1041 | -119.79 | -120.0784 | -119.7643
2661.3906 | 120.7077 | -120.314 | 0.24261 | -18.9334 | -20.8055 | -20.7531 | -20.761 | -20.6607 | -20.7232 | -20.8293 | 0.18069 | 0.26695 | 0.16518 | 0.090533 | 120.4359 | 120.4035 | 119.8699 | 120.238 | -18.9197 | -20.7917 | -20.7393 | -20.7473 | -20.647 | -20.7095 | -20.8156 | 0.19442 | 0.28068 | 0.17891 | 0.10427 | 120.4496 | 120.4172 | 119.8836 | 120.2517 | -120.2552 | -119.6892 | -120.2707 | -119.7047
2663.1406 | 120.694 | -120.3873 | 0.24719 | -18.9517 | -20.8146 | -20.7668 | -20.7564 | -20.6561 | -20.7369 | -20.8293 | 0.18069 | 0.27611 | 0.16975 | 0.090533 | 120.2711 | 120.463 | 119.934 | 120.3021 | -18.938 | -20.8009 | -20.7531 | -20.7427 | -20.6424 | -20.7232 | -20.8156 | 0.19442 | 0.28984 | 0.18349 | 0.10427 | 120.2848 | 120.4767 | 119.9477 | 120.3158 | -120.0904 | -119.7533 | -120.1013 | -119.7643
2664.8281 | 120.8679 | -120.3598 | 0.21515 | -18.9334 | -20.778 | -20.7348 | -20.7381 | -20.6195 | -20.7003 | -20.7973 | 0.18526 | 0.27153 | 0.16975 | 0.090533 | 120.3077 | 120.5042 | 119.9661 | 120.3341 | -18.9197 | -20.7643 | -20.721 | -20.7244 | -20.6058 | -20.6866 | -20.7835 | 0.199 | 0.28526 | 0.18349 | 0.10427 | 120.3214 | 120.5179 | 119.9798 | 120.3478 | -120.1224 | -119.7808 | -120.1379 | -119.7963
2666.5625 | 120.5338 | -120.1813 | 0.24261 | -18.851 | -20.6544 | -20.5745 | -20.6008 | -20.5096 | -20.5767 | -20.6737 | 0.17153 | 0.25779 | 0.18349 | 0.16838 | 120.2985 | 120.2615 | 119.9844 | 120.1006 | -18.8373 | -20.6406 | -20.5608 | -20.587 | -20.4959 | -20.5629 | -20.6599 | 0.18526 | 0.27152 | 0.19722 | 0.18211 | 120.3123 | 120.2753 | 119.9981 | 120.1144 | -120.127 | -119.8128 | -120.115 | -119.8009
2668.25 | 120.6985 | -120.3186 | 0.2655 | -18.9334 | -20.7185 | -20.634 | -20.674 | -20.5645 | -20.6408 | -20.7286 | 0.15779 | 0.26695 | 0.15602 | 0.17296 | 120.4405 | 120.408 | 120.0668 | 120.2563 | -18.9197 | -20.7047 | -20.6203 | -20.6603 | -20.5508 | -20.627 | -20.7149 | 0.17153 | 0.28068 | 0.16975 | 0.18669 | 120.4542 | 120.4218 | 120.0805 | 120.27 | -120.2827 | -119.909 | -120.2844 | -119.9108
2669.9844 | 120.7397 | -120.4102 | 0.2655 | -18.9746 | -20.7459 | -20.6661 | -20.7061 | -20.6012 | -20.6682 | -20.7652 | 0.16695 | 0.25321 | 0.16518 | 0.081375 | 120.5137 | 120.4813 | 119.9477 | 120.3158 | -18.9609 | -20.7322 | -20.6523 | -20.6923 | -20.5874 | -20.6545 | -20.7515 | 0.18068 | 0.26694 | 0.17891 | 0.095108 | 120.5274 | 120.495 | 119.9615 | 120.3295 | -120.3468 | -119.7808 | -120.3485 | -119.7826
2671.7344 | 120.6253 | -120.4193 | 0.25635 | -18.9929 | -20.7414 | -20.6661 | -20.7015 | -20.5829 | -20.6637 | -20.7606 | 0.17153 | 0.25779 | 0.15602 | 0.085954 | 120.3306 | 120.5271 | 119.9981 | 120.3707 | -18.9792 | -20.7276 | -20.6523 | -20.6878 | -20.5691 | -20.6499 | -20.7469 | 0.18526 | 0.27152 | 0.16975 | 0.099687 | 120.3443 | 120.5408 | 120.0118 | 120.3845 | -120.1591 | -119.8266 | -120.1746 | -119.8421
2673.4844 | 120.9045 | -120.4651 | 0.21973 | -18.9838 | -20.7139 | -20.634 | -20.674 | -20.5691 | -20.6454 | -20.7423 | 0.17153 | 0.26237 | 0.1606 | 0.085954 | 120.3672 | 120.5545 | 120.021 | 120.3982 | -18.97 | -20.7001 | -20.6203 | -20.6603 | -20.5554 | -20.6316 | -20.7286 | 0.18526 | 0.2761 | 0.17433 | 0.099687 | 120.3809 | 120.5683 | 120.0347 | 120.4119 | -120.1957 | -119.8495 | -120.2066 | -119.8604
2675.1562 | 120.369 | -120.4056 | 0.25177 | -18.9883 | -20.7139 | -20.6294 | -20.6695 | -20.5508 | -20.6362 | -20.7194 | 0.17611 | 0.26237 | 0.1606 | 0.081375 | 120.3993 | 120.5866 | 120.0531 | 120.4211 | -18.9746 | -20.7001 | -20.6157 | -20.6557 | -20.5371 | -20.6225 | -20.7057 | 0.18984 | 0.2761 | 0.17433 | 0.095108 | 120.413 | 120.6003 | 120.0668 | 120.4348 | -120.2231 | -119.8769 | -120.2387 | -119.8925
2676.9062 | 119.783 | -119.2978 | 0.20142 | -14.9502 | -16.1671 | -16.2431 | -16.1688 | -16.1697 | -16.2684 | -16.242 | 12.4968 | 12.3413 | 12.4899 | 12.344 | 105.9734 | 105.978 | 105.6723 | 105.6977 | -14.9365 | -16.1534 | -16.2294 | -16.1551 | -16.156 | -16.2547 | -16.2282 | 12.5106 | 12.355 | 12.5036 | 12.3578 | 105.9872 | 105.9917 | 105.6861 | 105.7114 | -93.4766 | -93.1755 | -93.4835 | -93.1824
2678.6562 | 120.1813 | -119.7693 | 0.091553 | -18.9426 | -20.5628 | -20.5425 | -20.5229 | -20.4318 | -20.5126 | -20.5821 | 0.44624 | 0.50505 | 0.45361 | 0.42938 | 119.5248 | 119.5062 | 119.2198 | 119.3315 | -18.9288 | -20.549 | -20.5287 | -20.5092 | -20.4181 | -20.4989 | -20.5684 | 0.45997 | 0.51878 | 0.46734 | 0.44311 | 119.5386 | 119.5199 | 119.2335 | 119.3452 | -119.0786 | -118.7735 | -119.0712 | -118.7662
2680.3438 | 120.5658 | -120.0714 | 0.21515 | -19.0387 | -20.6956 | -20.6523 | -20.6649 | -20.5462 | -20.627 | -20.7194 | 0.17153 | 0.26237 | 0.15602 | 0.17296 | 120.2207 | 120.1837 | 119.8974 | 120.0274 | -19.025 | -20.6818 | -20.6386 | -20.6511 | -20.5325 | -20.6133 | -20.7057 | 0.18526 | 0.2761 | 0.16975 | 0.18669 | 120.2344 | 120.1974 | 119.9111 | 120.0411 | -120.0492 | -119.7259 | -120.0647 | -119.7414
2682.0312 | 120.5841 | -120.1767 | 0.22888 | -19.0204 | -20.6727 | -20.6157 | -20.6282 | -20.5142 | -20.5904 | -20.6874 | 0.17153 | 0.27153 | 0.15602 | 0.081375 | 120.3031 | 120.2707 | 119.7417 | 120.1189 | -19.0067 | -20.6589 | -20.602 | -20.6145 | -20.5005 | -20.5767 | -20.6737 | 0.18526 | 0.28526 | 0.16975 | 0.095108 | 120.3168 | 120.2844 | 119.7555 | 120.1327 | -120.1316 | -119.5702 | -120.1471 | -119.5857
2683.7812 | 120.6665 | -120.195 | 0.23804 | -19.0112 | -20.6406 | -20.602 | -20.6008 | -20.4959 | -20.5675 | -20.6599 | 0.17153 | 0.26237 | 0.15602 | 0.17753 | 120.1703 | 120.3302 | 119.8104 | 120.1785 | -18.9975 | -20.6269 | -20.5882 | -20.587 | -20.4821 | -20.5538 | -20.6462 | 0.18526 | 0.2761 | 0.16975 | 0.19127 | 120.1841 | 120.3439 | 119.8241 | 120.1922 | -119.9988 | -119.6389 | -120.0143 | -119.6544
2685.5312 | 120.4376 | -119.9524 | 0.25635 | -19.0341 | -20.6452 | -20.602 | -20.6099 | -20.505 | -20.5675 | -20.6645 | 0.18069 | 0.27153 | 0.1606 | 0.085954 | 120.1978 | 120.3852 | 119.8516 | 120.2151 | -19.0204 | -20.6315 | -20.5882 | -20.5962 | -20.4913 | -20.5538 | -20.6508 | 0.19442 | 0.28526 | 0.17433 | 0.099687 | 120.2115 | 120.3989 | 119.8653 | 120.2288 | -120.0171 | -119.6709 | -120.0372 | -119.691
2687.2031 | 120.1813 | -119.9615 | 0.2655 | -19.0799 | -20.6773 | -20.6386 | -20.6328 | -20.5371 | -20.5996 | -20.7011 | 0.18526 | 0.27153 | 0.16975 | 0.085954 | 120.239 | 120.4218 | 119.8974 | 120.27 | -19.0662 | -20.6635 | -20.6249 | -20.6191 | -20.5233 | -20.5858 | -20.6874 | 0.199 | 0.28526 | 0.18349 | 0.099687 | 120.2528 | 120.4355 | 119.9111 | 120.2837 | -120.0538 | -119.7121 | -120.0693 | -119.7276
2688.9531 | 120.3827 | -120.3094 | 0.26093 | -19.0845 | -20.6681 | -20.6294 | -20.6328 | -20.5279 | -20.5996 | -20.6874 | 0.18984 | 0.26695 | 0.16975 | 0.090533 | 120.2756 | 120.463 | 119.9203 | 120.1098 | -19.0708 | -20.6544 | -20.6157 | -20.6191 | -20.5142 | -20.5858 | -20.6737 | 0.20358 | 0.28068 | 0.18349 | 0.10427 | 120.2894 | 120.4767 | 119.934 | 120.1235 | -120.0858 | -119.7304 | -120.1059 | -119.7505
2690.6875 | 120.8267 | -120.401 | 0.22888 | -19.1257 | -20.6956 | -20.6569 | -20.6603 | -20.5554 | -20.627 | -20.7194 | 0.18069 | 0.28069 | 0.17433 | 0.095112 | 120.3123 | 120.495 | 119.9615 | 120.1189 | -19.112 | -20.6818 | -20.6432 | -20.6466 | -20.5417 | -20.6133 | -20.7057 | 0.19442 | 0.29442 | 0.18807 | 0.10884 | 120.326 | 120.5088 | 119.9752 | 120.1327 | -120.1316 | -119.7808 | -120.1379 | -119.7871
2692.4375 | 120.5338 | -120.0302 | 0.12817 | -19.0753 | -20.6223 | -20.5745 | -20.5825 | -20.4684 | -20.5446 | -20.6324 | 0.21731 | 0.299 | 0.23385 | 0.20959 | 120.1566 | 120.1334 | 119.8424 | 119.9724 | -19.0616 | -20.6086 | -20.5608 | -20.5687 | -20.4547 | -20.5309 | -20.6187 | 0.23105 | 0.31273 | 0.24758 | 0.22332 | 120.1703 | 120.1471 | 119.8562 | 119.9862 | -119.9393 | -119.6251 | -119.9228 | -119.6086
2694.125 | 120.4102 | -119.9066 | 0.2243 | -19.025 | -20.549 | -20.4692 | -20.5046 | -20.3997 | -20.4714 | -20.5592 | 0.34093 | 0.43637 | 0.36204 | 0.34696 | 119.9277 | 119.8999 | 119.6044 | 119.7389 | -19.0112 | -20.5353 | -20.4555 | -20.4909 | -20.386 | -20.4576 | -20.5455 | 0.35467 | 0.4501 | 0.37578 | 0.36069 | 119.9414 | 119.9136 | 119.6181 | 119.7527 | -119.5868 | -119.2634 | -119.5657 | -119.2423
2695.8594 | 120.4285 | -119.1925 | 1.0025 | -18.8647 | -20.3705 | -20.2861 | -20.3306 | -20.2212 | -20.2928 | -20.3852 | 0.76673 | 0.8622 | 0.78324 | 0.77281 | 119.566 | 119.5382 | 119.2427 | 119.3864 | -18.851 | -20.3567 | -20.2723 | -20.3169 | -20.2075 | -20.2791 | -20.3715 | 0.78047 | 0.87593 | 0.79698 | 0.78654 | 119.5798 | 119.5519 | 119.2564 | 119.4002 | -118.7993 | -118.4759 | -118.7828 | -118.4594
2697.5469 | 120.4468 | -120.1263 | 0.13275 | -18.59 | -20.0271 | -19.9701 | -19.9918 | -19.9099 | -19.9861 | -20.0464 | 1.6595 | 1.7001 | 1.644 | 1.5787 | 118.4993 | 118.4853 | 118.1301 | 118.3014 | -18.5763 | -20.0133 | -19.9564 | -19.9781 | -19.8962 | -19.9723 | -20.0327 | 1.6733 | 1.7139 | 1.6577 | 1.5925 | 118.513 | 118.499 | 118.1439 | 118.3151 | -116.8398 | -116.4706 | -116.8553 | -116.4862
2699.2812 | 120.7443 | -120.3323 | 0.10986 | -19.1394 | -20.6269 | -20.5653 | -20.6054 | -20.4959 | -20.5629 | -20.6553 | 0.057066 | 0.15706 | 0.055298 | -0.08347 | 120.3031 | 120.4859 | 119.9523 | 120.3341 | -19.1257 | -20.6132 | -20.5516 | -20.5916 | -20.4821 | -20.5492 | -20.6416 | 0.070799 | 0.17079 | 0.069031 | -0.069737 | 120.3168 | 120.4996 | 119.9661 | 120.3478 | -120.246 | -119.8953 | -120.2478 | -119.897
2701.0312 | 120.7535 | -120.4605 | 0.11444 | -19.1394 | -20.6131 | -20.5287 | -20.5733 | -20.4593 | -20.5355 | -20.6324 | 0.057066 | 0.15248 | 0.05072 | -0.097207 | 120.3672 | 120.5545 | 120.0256 | 120.4028 | -19.1257 | -20.5994 | -20.515 | -20.5596 | -20.4455 | -20.5217 | -20.6187 | 0.070799 | 0.16621 | 0.064453 | -0.083474 | 120.3809 | 120.5683 | 120.0393 | 120.4165 | -120.3101 | -119.9685 | -120.3165 | -119.9749
2702.7812 | 120.7077 | -120.2591 | 0.12817 | -19.1394 | -20.5903 | -20.515 | -20.5596 | -20.4455 | -20.5217 | -20.6096 | 0.061645 | 0.15248 | 0.073611 | 0.072217 | 120.4817 | 120.4447 | 120.1492 | 120.2883 | -19.1257 | -20.5765 | -20.5012 | -20.5458 | -20.4318 | -20.508 | -20.5958 | 0.075378 | 0.16621 | 0.087344 | 0.08595 | 120.4954 | 120.4584 | 120.1629 | 120.3021 | -120.42 | -120.0876 | -120.408 | -120.0756
2704.4844 | 120.7031 | -120.4559 | 0.13733 | -19.1623 | -20.6086 | -20.5287 | -20.5733 | -20.4593 | -20.5309 | -20.6187 | 0.057066 | 0.16164 | 0.046142 | 0.072217 | 120.6007 | 120.5683 | 120.1721 | 120.4119 | -19.1486 | -20.5948 | -20.515 | -20.5596 | -20.4455 | -20.5172 | -20.605 | 0.070799 | 0.17537 | 0.059875 | 0.08595 | 120.6144 | 120.582 | 120.1858 | 120.4257 | -120.5436 | -120.115 | -120.5546 | -120.1259
2706.2188 | 120.3232 | -120.0851 | 0.10986 | -19.0799 | -20.4895 | -20.4188 | -20.4588 | -20.3494 | -20.4256 | -20.5134 | 0.093694 | 0.17537 | 0.11024 | 0.090533 | 120.1383 | 120.1105 | 119.8058 | 119.9495 | -19.0662 | -20.4758 | -20.4051 | -20.4451 | -20.3357 | -20.4119 | -20.4997 | 0.10743 | 0.1891 | 0.12397 | 0.10427 | 120.152 | 120.1242 | 119.8196 | 119.9633 | -120.0446 | -119.7121 | -120.0281 | -119.6956
2707.8906 | 120.4468 | -120.0394 | 0.12817 | -19.1028 | -20.5078 | -20.4326 | -20.4726 | -20.3585 | -20.4302 | -20.5272 | 0.057066 | 0.15248 | 0.07819 | 0.063059 | 120.2344 | 120.202 | 119.9111 | 120.0548 | -19.0891 | -20.4941 | -20.4188 | -20.4588 | -20.3448 | -20.4164 | -20.5134 | 0.070799 | 0.16621 | 0.091923 | 0.076792 | 120.2482 | 120.2158 | 119.9249 | 120.0686 | -120.1774 | -119.8541 | -120.1562 | -119.8329
2709.6406 | 120.6528 | -120.2637 | 0.12817 | -19.0936 | -20.4804 | -20.4051 | -20.4359 | -20.3311 | -20.4119 | -20.4997 | 0.061645 | 0.14332 | 0.046142 | -0.069733 | 120.4267 | 120.3897 | 119.8699 | 120.238 | -19.0799 | -20.4666 | -20.3914 | -20.4222 | -20.3173 | -20.3981 | -20.486 | 0.075378 | 0.15705 | 0.059875 | -0.056 | 120.4405 | 120.4035 | 119.8836 | 120.2517 | -120.3651 | -119.8083 | -120.3806 | -119.8238
2711.375 | 120.7535 | -120.3278 | 0.1236 | -19.0753 | -20.4529 | -20.373 | -20.4176 | -20.3036 | -20.3798 | -20.4676 | 0.052488 | 0.1479 | 0.059877 | -0.08347 | 120.2894 | 120.4767 | 119.9386 | 120.3158 | -19.0616 | -20.4392 | -20.3593 | -20.4039 | -20.2899 | -20.3661 | -20.4539 | 0.066221 | 0.16163 | 0.07361 | -0.069737 | 120.3031 | 120.4904 | 119.9523 | 120.3295 | -120.2369 | -119.8861 | -120.2295 | -119.8787
2713.0469 | 120.3461 | -119.3115 | -3.1677 | -18.8693 | -20.2194 | -20.1304 | -20.1841 | -20.061 | -20.1326 | -20.2296 | 0.71637 | 0.82099 | 0.73288 | 0.72702 | 119.479 | 119.4421 | 119.1465 | 119.2949 | -18.8556 | -20.2056 | -20.1166 | -20.1704 | -20.0472 | -20.1188 | -20.2158 | 0.7301 | 0.83472 | 0.74662 | 0.74075 | 119.4928 | 119.4558 | 119.1603 | 119.3086 | -118.7627 | -118.4302 | -118.7462 | -118.4136
2714.8125 | 120.3781 | -120.0348 | 0.11902 | -19.0845 | -20.4392 | -20.4005 | -20.4085 | -20.2899 | -20.3707 | -20.4585 | 0.066223 | 0.15248 | 0.07819 | 0.05848 | 120.1841 | 120.1517 | 119.8516 | 119.9907 | -19.0708 | -20.4254 | -20.3868 | -20.3947 | -20.2761 | -20.3569 | -20.4447 | 0.079956 | 0.16621 | 0.091923 | 0.072213 | 120.1978 | 120.1654 | 119.8653 | 120.0045 | -120.1179 | -119.7854 | -120.1059 | -119.7734
2716.5625 | 120.4742 | -120.3049 | 0.14648 | -19.1211 | -20.4666 | -20.428 | -20.4405 | -20.3265 | -20.3981 | -20.4859 | 0.052488 | 0.1479 | 0.05072 | -0.092628 | 120.3855 | 120.3531 | 120.0576 | 120.1968 | -19.1074 | -20.4529 | -20.4143 | -20.4268 | -20.3128 | -20.3844 | -20.4722 | 0.066221 | 0.16163 | 0.064453 | -0.078895 | 120.3993 | 120.3668 | 120.0714 | 120.2105 | -120.333 | -120.0051 | -120.3348 | -120.0069
2718.2344 | 120.4147 | -120.3552 | 0.13733 | -19.1806 | -20.5078 | -20.4692 | -20.4909 | -20.3723 | -20.4439 | -20.5272 | 0.052488 | 0.1479 | 0.05072 | -0.092628 | 120.4771 | 120.4355 | 119.9157 | 120.2838 | -19.1669 | -20.4941 | -20.4555 | -20.4772 | -20.3585 | -20.4302 | -20.5134 | 0.066221 | 0.16163 | 0.064453 | -0.078895 | 120.4908 | 120.4492 | 119.9294 | 120.2975 | -120.4246 | -119.8632 | -120.4264 | -119.865
2719.9219 | 120.3415 | -120.4193 | 0.15564 | -19.1394 | -20.4483 | -20.4143 | -20.4222 | -20.3082 | -20.3798 | -20.4722 | 0.052488 | 0.1479 | 0.05072 | -0.10179 | 120.3214 | 120.4996 | 119.9752 | 120.3478 | -19.1257 | -20.4346 | -20.4005 | -20.4085 | -20.2945 | -20.3661 | -20.4585 | 0.066221 | 0.16163 | 0.064453 | -0.088053 | 120.3352 | 120.5133 | 119.989 | 120.3616 | -120.2689 | -119.9227 | -120.2707 | -119.9245
2721.6719 | 120.369 | -120.4697 | 0.14191 | -19.1165 | -20.4208 | -20.3822 | -20.3993 | -20.2807 | -20.3478 | -20.4356 | 0.066223 | 0.1479 | 0.05072 | -0.092628 | 120.3718 | 120.5545 | 120.0256 | 120.4028 | -19.1028 | -20.4071 | -20.3685 | -20.3856 | -20.267 | -20.334 | -20.4219 | 0.079956 | 0.16163 | 0.064453 | -0.078895 | 120.3855 | 120.5683 | 120.0393 | 120.4165 | -120.3056 | -119.9594 | -120.3211 | -119.9749
2723.4219 | 120.0668 | -120.0302 | 0.14648 | -19.1532 | -20.4529 | -20.4097 | -20.4268 | -20.3173 | -20.3844 | -20.4722 | 0.057066 | 0.1479 | 0.05072 | -0.092628 | 120.4084 | 120.5912 | 120.0668 | 120.4394 | -19.1394 | -20.4392 | -20.3959 | -20.4131 | -20.3036 | -20.3707 | -20.4585 | 0.070799 | 0.16163 | 0.064453 | -0.078895 | 120.4221 | 120.6049 | 120.0805 | 120.4531 | -120.3513 | -120.0097 | -120.3577 | -120.0161
2725.1562 | 120.5658 | -120.4926 | 0.1236 | -19.2081 | -20.4895 | -20.4463 | -20.4634 | -20.3448 | -20.421 | -20.5043 | 0.057066 | 0.1479 | 0.055298 | -0.051417 | 120.4496 | 120.6278 | 120.0943 | 120.4715 | -19.1944 | -20.4758 | -20.4326 | -20.4497 | -20.3311 | -20.4073 | -20.4905 | 0.070799 | 0.16163 | 0.069031 | -0.037684 | 120.4633 | 120.6415 | 120.108 | 120.4852 | -120.3925 | -120.0372 | -120.3943 | -120.039
2726.8906 | 117.9657 | -89.4333 | 28.1754 | -14.2726 | -15.5169 | -15.2175 | -15.4088 | -15.1488 | -15.22 | -15.4545 | 13.1699 | 13.5821 | 13.2407 | 13.3102 | 106.184 | 106.1703 | 105.7822 | 106.1372 | -14.2589 | -15.5032 | -15.2038 | -15.395 | -15.1351 | -15.2062 | -15.4408 | 13.1836 | 13.5959 | 13.2545 | 13.3239 | 106.1978 | 106.184 | 105.7959 | 106.1509 | -93.0141 | -92.6123 | -92.9433 | -92.5415
2728.5781 | 120.7397 | -120.3094 | 0.10529 | -19.1852 | -20.4529 | -20.4188 | -20.4268 | -20.3173 | -20.3844 | -20.4676 | 0.057066 | 0.15248 | 0.073611 | 0.063059 | 120.4908 | 120.4676 | 120.1721 | 120.3021 | -19.1715 | -20.4392 | -20.4051 | -20.4131 | -20.3036 | -20.3707 | -20.4539 | 0.070799 | 0.16621 | 0.087344 | 0.076792 | 120.5046 | 120.4813 | 120.1858 | 120.3158 | -120.4338 | -120.115 | -120.4172 | -120.0985
2730.3281 | 118.0435 | -94.7159 | 22.5815 | -9.8087 | -10.526 | -10.497 | -10.5006 | -10.4244 | -10.5134 | -10.5422 | 25.9576 | 25.9678 | 25.9913 | 25.9117 | 91.3599 | 91.3144 | 91.0169 | 91.1574 | -9.7949 | -10.5123 | -10.4833 | -10.4869 | -10.4106 | -10.4997 | -10.5284 | 25.9713 | 25.9816 | 26.005 | 25.9254 | 91.3736 | 91.3282 | 91.0306 | 91.1711 | -65.4023 | -65.0593 | -65.3686 | -65.0257
2732.0781 | 120.7306 | -120.2545 | 0.10529 | -19.1806 | -20.4208 | -20.3914 | -20.4131 | -20.2899 | -20.3615 | -20.4493 | 0.052488 | 0.14332 | 0.055298 | 0.067638 | 120.4817 | 120.4355 | 119.989 | 120.2838 | -19.1669 | -20.4071 | -20.3776 | -20.3993 | -20.2761 | -20.3478 | -20.4356 | 0.066221 | 0.15705 | 0.069031 | 0.081371 | 120.4954 | 120.4492 | 120.0027 | 120.2975 | -120.4292 | -119.9365 | -120.4264 | -119.9337
2733.8281 | 120.8313 | -120.3918 | 0.11444 | -19.2127 | -20.4575 | -20.4188 | -20.4359 | -20.3173 | -20.389 | -20.4768 | 0.061645 | 0.1479 | 0.041563 | -0.097207 | 120.3626 | 120.55 | 120.0118 | 120.3936 | -19.1989 | -20.4437 | -20.4051 | -20.4222 | -20.3036 | -20.3752 | -20.4631 | 0.075378 | 0.16163 | 0.055296 | -0.083474 | 120.3764 | 120.5637 | 120.0256 | 120.4074 | -120.301 | -119.9502 | -120.3211 | -119.9703
2735.5625 | 120.8176 | -120.5017 | 0.09613 | -19.2768 | -20.5033 | -20.4692 | -20.4772 | -20.3631 | -20.4393 | -20.518 | 0.057066 | 0.1479 | 0.055298 | -0.092628 | 120.4176 | 120.6003 | 120.0759 | 120.4531 | -19.263 | -20.4895 | -20.4555 | -20.4634 | -20.3494 | -20.4256 | -20.5043 | 0.070799 | 0.16163 | 0.069031 | -0.078895 | 120.4313 | 120.6141 | 120.0897 | 120.4669 | -120.3605 | -120.0189 | -120.3623 | -120.0206
2737.3125 | 120.8817 | -120.5521 | 0.1236 | -19.2493 | -20.4849 | -20.4555 | -20.4634 | -20.354 | -20.421 | -20.5088 | 0.047909 | 0.14332 | 0.046142 | -0.092628 | 120.4679 | 120.6507 | 120.1263 | 120.4623 | -19.2356 | -20.4712 | -20.4417 | -20.4497 | -20.3402 | -20.4073 | -20.4951 | 0.061642 | 0.15705 | 0.059875 | -0.078895 | 120.4817 | 120.6644 | 120.14 | 120.476 | -120.42 | -120.0784 | -120.4218 | -120.0802
2739 | 120.9412 | -120.5704 | 0.11444 | -19.3271 | -20.5536 | -20.5196 | -20.5275 | -20.4089 | -20.4805 | -20.5775 | 0.057066 | 0.14332 | 0.05072 | -0.069733 | 120.5046 | 120.6873 | 120.1584 | 120.3158 | -19.3134 | -20.5399 | -20.5058 | -20.5138 | -20.3952 | -20.4668 | -20.5638 | 0.070799 | 0.15705 | 0.064453 | -0.056 | 120.5183 | 120.701 | 120.1721 | 120.3295 | -120.4475 | -120.1013 | -120.4538 | -120.1076
2740.75 | 120.9274 | -120.6024 | 0.10071 | -19.3546 | -20.5948 | -20.5516 | -20.5596 | -20.4455 | -20.5126 | -20.6004 | 0.047909 | 0.14332 | 0.055298 | -0.092628 | 120.5274 | 120.7239 | 120.195 | 120.3478 | -19.3409 | -20.5811 | -20.5379 | -20.5458 | -20.4318 | -20.4989 | -20.5867 | 0.061642 | 0.15705 | 0.069031 | -0.078895 | 120.5412 | 120.7377 | 120.2087 | 120.3616 | -120.4795 | -120.1471 | -120.4721 | -120.1397
2742.4219 | 120.8588 | -120.6848 | 0.16022 | -19.3912 | -20.6131 | -20.5653 | -20.587 | -20.4638 | -20.5401 | -20.6233 | 0.052488 | 0.1479 | 0.059877 | -0.092628 | 120.5686 | 120.7468 | 120.2225 | 120.3799 | -19.3775 | -20.5994 | -20.5516 | -20.5733 | -20.4501 | -20.5263 | -20.6096 | 0.066221 | 0.16163 | 0.07361 | -0.078895 | 120.5824 | 120.7606 | 120.2362 | 120.3936 | -120.5162 | -120.17 | -120.5088 | -120.1626
2744.1719 | 121.0281 | -120.6482 | 0.11444 | -19.3821 | -20.604 | -20.5562 | -20.5687 | -20.4501 | -20.5263 | -20.605 | 0.052488 | 0.15248 | 0.055298 | -0.078891 | 120.5961 | 120.7743 | 120.2453 | 120.4028 | -19.3683 | -20.5903 | -20.5425 | -20.555 | -20.4364 | -20.5126 | -20.5912 | 0.066221 | 0.16621 | 0.069031 | -0.065158 | 120.6098 | 120.788 | 120.2591 | 120.4165 | -120.5436 | -120.1929 | -120.5408 | -120.19
2745.9062 | 120.9778 | -120.6802 | 0.11902 | -19.3821 | -20.5948 | -20.5516 | -20.555 | -20.4501 | -20.5172 | -20.605 | 0.052488 | 0.1479 | 0.059877 | -0.097207 | 120.6144 | 120.7972 | 120.2682 | 120.4211 | -19.3683 | -20.5811 | -20.5379 | -20.5413 | -20.4364 | -20.5034 | -20.5912 | 0.066221 | 0.16163 | 0.07361 | -0.083474 | 120.6282 | 120.8109 | 120.282 | 120.4348 | -120.5619 | -120.2157 | -120.5546 | -120.2084
2747.6094 | 121.0419 | -120.7031 | 0.091553 | -19.4279 | -20.6269 | -20.5837 | -20.5962 | -20.4776 | -20.5492 | -20.6279 | 0.052488 | 0.14332 | 0.05072 | -0.092628 | 120.6556 | 120.8246 | 120.2957 | 120.4531 | -19.4141 | -20.6132 | -20.5699 | -20.5825 | -20.4638 | -20.5355 | -20.6141 | 0.066221 | 0.15705 | 0.064453 | -0.078895 | 120.6694 | 120.8384 | 120.3094 | 120.4669 | -120.6031 | -120.2432 | -120.6049 | -120.245
2749.375 | 121.0785 | -120.7214 | 0.11444 | -19.3775 | -20.5811 | -20.5333 | -20.5458 | -20.4226 | -20.4943 | -20.5775 | 0.047909 | 0.14332 | 0.05072 | -0.092628 | 120.6602 | 120.8475 | 120.3186 | 120.476 | -19.3638 | -20.5674 | -20.5196 | -20.5321 | -20.4089 | -20.4805 | -20.5638 | 0.061642 | 0.15705 | 0.064453 | -0.078895 | 120.6739 | 120.8613 | 120.3323 | 120.4898 | -120.6123 | -120.2707 | -120.6095 | -120.2679
2751.0625 | 120.8679 | -120.813 | 0.15564 | -19.3592 | -20.5445 | -20.5012 | -20.5046 | -20.3997 | -20.4668 | -20.55 | 0.052488 | 0.14332 | 0.046142 | -0.078891 | 120.6968 | 120.875 | 120.3506 | 120.4989 | -19.3455 | -20.5307 | -20.4875 | -20.4909 | -20.386 | -20.4531 | -20.5363 | 0.066221 | 0.15705 | 0.059875 | -0.065158 | 120.7106 | 120.8887 | 120.3644 | 120.5127 | -120.6443 | -120.2982 | -120.6507 | -120.3045
2752.8125 | 121.0373 | -120.7993 | 0.11902 | -19.3867 | -20.5765 | -20.5241 | -20.5458 | -20.4226 | -20.4897 | -20.5821 | 0.057066 | 0.1479 | 0.05072 | -0.088049 | 120.7243 | 120.8887 | 120.369 | 120.5218 | -19.3729 | -20.5628 | -20.5104 | -20.5321 | -20.4089 | -20.476 | -20.5684 | 0.070799 | 0.16163 | 0.064453 | -0.074316 | 120.738 | 120.9025 | 120.3827 | 120.5356 | -120.6672 | -120.3119 | -120.6736 | -120.3182
2754.5156 | 120.9274 | -120.8084 | 0.16022 | -19.3867 | -20.5582 | -20.515 | -20.5275 | -20.4181 | -20.4851 | -20.5638 | 0.052488 | 0.1479 | 0.05072 | -0.092628 | 120.7335 | 120.9162 | 120.3873 | 120.5447 | -19.3729 | -20.5445 | -20.5012 | -20.5138 | -20.4043 | -20.4714 | -20.55 | 0.066221 | 0.16163 | 0.064453 | -0.078895 | 120.7472 | 120.9299 | 120.401 | 120.5584 | -120.681 | -120.3348 | -120.6827 | -120.3366
2756.2656 | 121.1655 | -120.7993 | 0.11444 | -19.3821 | -20.5536 | -20.5058 | -20.5229 | -20.4043 | -20.476 | -20.5592 | 0.057066 | 0.1479 | 0.055298 | -0.088049 | 120.7564 | 120.9345 | 120.4056 | 120.5584 | -19.3683 | -20.5399 | -20.4921 | -20.5092 | -20.3906 | -20.4622 | -20.5455 | 0.070799 | 0.16163 | 0.069031 | -0.074316 | 120.7701 | 120.9483 | 120.4193 | 120.5722 | -120.6993 | -120.3485 | -120.7011 | -120.3503
2758.0156 | 121.138 | -120.8267 | 0.11902 | -19.4782 | -20.6544 | -20.602 | -20.6191 | -20.5005 | -20.5721 | -20.6553 | 0.057066 | 0.13874 | 0.05072 | -0.092628 | 120.7747 | 120.9574 | 120.4193 | 120.5813 | -19.4645 | -20.6406 | -20.5882 | -20.6054 | -20.4867 | -20.5584 | -20.6416 | 0.070799 | 0.15247 | 0.064453 | -0.078895 | 120.7884 | 120.9711 | 120.4331 | 120.5951 | -120.7176 | -120.3623 | -120.7239 | -120.3686
2759.7812 | 120.9915 | -120.726 | 0.14648 | -19.405 | -20.5719 | -20.5241 | -20.5367 | -20.4226 | -20.4988 | -20.5775 | 0.052488 | 0.14332 | 0.055298 | -0.092628 | 120.7884 | 120.9666 | 120.4376 | 120.5951 | -19.3912 | -20.5582 | -20.5104 | -20.5229 | -20.4089 | -20.4851 | -20.5638 | 0.066221 | 0.15705 | 0.069031 | -0.078895 | 120.8021 | 120.9803 | 120.4514 | 120.6088 | -120.7359 | -120.3851 | -120.7331 | -120.3823
2761.4531 | 121.2112 | -120.8725 | 0.12817 | -19.3455 | -20.5078 | -20.4555 | -20.4726 | -20.3631 | -20.4302 | -20.5134 | 0.061645 | 0.14332 | 0.059877 | -0.097207 | 120.8067 | 120.994 | 120.4605 | 120.6134 | -19.3317 | -20.4941 | -20.4417 | -20.4588 | -20.3494 | -20.4164 | -20.4997 | 0.075378 | 0.15705 | 0.07361 | -0.083474 | 120.8204 | 121.0078 | 120.4743 | 120.6271 | -120.7451 | -120.3989 | -120.7468 | -120.4006
2763.125 | 121.0236 | -120.607 | 0.12817 | -19.3867 | -20.549 | -20.4967 | -20.5184 | -20.3997 | -20.4668 | -20.55 | 0.057066 | 0.1479 | 0.046142 | -0.08347 | 120.825 | 121.0078 | 120.4926 | 120.6363 | -19.3729 | -20.5353 | -20.4829 | -20.5046 | -20.386 | -20.4531 | -20.5363 | 0.070799 | 0.16163 | 0.059875 | -0.069737 | 120.8388 | 121.0215 | 120.5063 | 120.65 | -120.768 | -120.4355 | -120.7789 | -120.4464
2764.875 | 91.4658 | -108.9569 | 0.36621 | -18.5259 | -19.5554 | -19.5489 | -19.534 | -19.4475 | -19.5282 | -19.5749 | 2.4745 | 2.4877 | 2.4589 | 2.4213 | 117.8538 | 117.8306 | 117.5258 | 117.6376 | -18.5122 | -19.5417 | -19.5352 | -19.5203 | -19.4338 | -19.5145 | -19.5612 | 2.4882 | 2.5014 | 2.4726 | 2.435 | 117.8675 | 117.8443 | 117.5395 | 117.6513 | -115.3793 | -115.0513 | -115.3949 | -115.0669
2766.625 | 120.8496 | -120.3964 | 0.10529 | -19.3409 | -20.462 | -20.4234 | -20.4314 | -20.3128 | -20.3935 | -20.4768 | 0.061645 | 0.1479 | 0.073611 | 0.067638 | 120.587 | 120.5454 | 120.2591 | 120.3936 | -19.3271 | -20.4483 | -20.4097 | -20.4176 | -20.299 | -20.3798 | -20.4631 | 0.075378 | 0.16163 | 0.087344 | 0.081371 | 120.6007 | 120.5591 | 120.2728 | 120.4074 | -120.5253 | -120.1974 | -120.5133 | -120.1855
2768.3125 | 120.9549 | -120.6299 | 0.1236 | -19.4141 | -20.5536 | -20.5058 | -20.5229 | -20.4043 | -20.4805 | -20.5592 | 0.052488 | 0.15248 | 0.055298 | 0.053901 | 120.7884 | 120.7514 | 120.4651 | 120.5951 | -19.4004 | -20.5399 | -20.4921 | -20.5092 | -20.3906 | -20.4668 | -20.5455 | 0.066221 | 0.16621 | 0.069031 | 0.067634 | 120.8021 | 120.7651 | 120.4788 | 120.6088 | -120.7359 | -120.4126 | -120.7331 | -120.4098
2770 | 121.0556 | -120.6894 | 0.1236 | -19.3912 | -20.5261 | -20.4829 | -20.5046 | -20.3769 | -20.4531 | -20.5363 | 0.052488 | 0.14332 | 0.046142 | -0.092628 | 120.8571 | 120.8155 | 120.2957 | 120.6683 | -19.3775 | -20.5124 | -20.4692 | -20.4909 | -20.3631 | -20.4393 | -20.5226 | 0.066221 | 0.15705 | 0.059875 | -0.078895 | 120.8708 | 120.8292 | 120.3094 | 120.6821 | -120.8046 | -120.2432 | -120.8109 | -120.2496
2771.75 | 121.0693 | -120.7809 | 0.10986 | -19.4141 | -20.5536 | -20.5058 | -20.5184 | -20.4043 | -20.4851 | -20.5638 | 0.057066 | 0.15248 | 0.059877 | -0.088049 | 120.6785 | 120.8658 | 120.3461 | 120.7141 | -19.4004 | -20.5399 | -20.4921 | -20.5046 | -20.3906 | -20.4714 | -20.55 | 0.070799 | 0.16621 | 0.07361 | -0.074316 | 120.6923 | 120.8796 | 120.3598 | 120.7278 | -120.6215 | -120.289 | -120.6186 | -120.2862
2773.4375 | 120.726 | -120.4514 | 0.12817 | -19.4004 | -20.5307 | -20.4417 | -20.5 | -20.3814 | -20.4622 | -20.5363 | 0.061645 | 0.15248 | 0.07819 | 0.05848 | 120.5961 | 120.5637 | 120.2728 | 120.4119 | -19.3867 | -20.517 | -20.428 | -20.4863 | -20.3677 | -20.4485 | -20.5226 | 0.075378 | 0.16621 | 0.091923 | 0.072213 | 120.6098 | 120.5774 | 120.2865 | 120.4257 | -120.5345 | -120.2112 | -120.5179 | -120.1946
2775.1875 | 120.8908 | -120.6528 | 0.14648 | -19.437 | -20.5857 | -20.4921 | -20.5458 | -20.4272 | -20.5034 | -20.5867 | 0.052488 | 0.1479 | 0.059877 | -0.078891 | 120.7838 | 120.7468 | 120.2225 | 120.5951 | -19.4233 | -20.5719 | -20.4784 | -20.5321 | -20.4135 | -20.4897 | -20.5729 | 0.066221 | 0.16163 | 0.07361 | -0.065158 | 120.7976 | 120.7606 | 120.2362 | 120.6088 | -120.7313 | -120.17 | -120.7239 | -120.1626
2776.875 | 121.0052 | -120.7169 | 0.12817 | -19.5332 | -20.6727 | -20.5837 | -20.6466 | -20.5188 | -20.595 | -20.6828 | 0.057066 | 0.15248 | 0.05072 | -0.092628 | 120.6327 | 120.8201 | 120.2728 | 120.6592 | -19.5194 | -20.6589 | -20.5699 | -20.6328 | -20.505 | -20.5813 | -20.6691 | 0.070799 | 0.16621 | 0.064453 | -0.078895 | 120.6465 | 120.8338 | 120.2865 | 120.6729 | -120.5757 | -120.2157 | -120.582 | -120.2221
2778.625 | 121.0876 | -120.7123 | 0.11902 | -19.5973 | -20.7459 | -20.6615 | -20.7152 | -20.592 | -20.6774 | -20.7469 | 0.057066 | 0.14332 | 0.055298 | -0.097207 | 120.6785 | 120.8613 | 120.3232 | 120.7095 | -19.5835 | -20.7322 | -20.6478 | -20.7015 | -20.5783 | -20.6637 | -20.7332 | 0.070799 | 0.15705 | 0.069031 | -0.083474 | 120.6923 | 120.875 | 120.3369 | 120.7233 | -120.6215 | -120.2661 | -120.6232 | -120.2679
2780.375 | 121.1655 | -120.7764 | 0.11902 | -19.5744 | -20.7093 | -20.6157 | -20.6695 | -20.5645 | -20.6362 | -20.7103 | 0.057066 | 0.14332 | 0.05072 | -0.08347 | 120.7197 | 120.8979 | 120.3644 | 120.5264 | -19.5606 | -20.6956 | -20.602 | -20.6557 | -20.5508 | -20.6225 | -20.6965 | 0.070799 | 0.15705 | 0.064453 | -0.069737 | 120.7335 | 120.9116 | 120.3781 | 120.5401 | -120.6627 | -120.3073 | -120.669 | -120.3137
2782.1094 | 121.019 | -120.6894 | 0.13733 | -14.7533 | -15.6039 | -15.5701 | -15.6011 | -15.4693 | -15.545 | -15.5965 | 0.047909 | 0.13874 | 0.082768 | 0.044743 | 120.9486 | 120.9116 | 3.1119 | 3.2702 | -14.7396 | -15.5902 | -15.5564 | -15.5873 | -15.4555 | -15.5313 | -15.5827 | 0.061642 | 0.15247 | 0.096501 | 0.058476 | 120.9624 | 120.9254 | 3.1256 | 3.284 | -120.9007 | -3.064 | -120.8659 | -3.0291
2783.7969 | 120.9915 | -120.8588 | 0.14191 | -14.7533 | -15.6268 | -15.6021 | -15.6285 | -15.4922 | -15.5679 | -15.6056 | 0.043331 | 0.1479 | 0.05072 | 0.05848 | 120.8388 | 120.9574 | 3.9589 | 4.1172 | -14.7396 | -15.6131 | -15.5884 | -15.6148 | -15.4784 | -15.5542 | -15.5919 | 0.057064 | 0.16163 | 0.064453 | 0.072213 | 120.8525 | 120.9711 | 3.9726 | 4.1309 | -120.7954 | -3.9155 | -120.788 | -3.9082
2785.5469 | 121.1929 | -120.8313 | 0.10529 | -14.8083 | -15.6772 | -15.6525 | -15.6743 | -15.5517 | -15.6091 | -15.6697 | 0.043331 | 0.1479 | 0.041563 | -0.092628 | 120.7976 | 120.9803 | 4.9203 | 5.0786 | -14.7945 | -15.6634 | -15.6388 | -15.6606 | -15.538 | -15.5954 | -15.656 | 0.057064 | 0.16163 | 0.055296 | -0.078895 | 120.8113 | 120.994 | 4.9341 | 5.0923 | -120.7542 | -4.877 | -120.756 | -4.8788
2787.2969 | 121.2341 | -120.8771 | 0.10071 | -14.7213 | -15.5719 | -15.5609 | -15.5782 | -15.451 | -15.5176 | -15.5781 | 0.047909 | 0.1479 | 0.046142 | -0.092628 | 120.8204 | 121.0123 | 2.9104 | 3.0596 | -14.7075 | -15.5581 | -15.5472 | -15.5644 | -15.4372 | -15.5038 | -15.5644 | 0.061642 | 0.16163 | 0.059875 | -0.078895 | 120.8342 | 121.0261 | 2.9242 | 3.0734 | -120.7725 | -2.8625 | -120.7743 | -2.8643
2788.9688 | 120.9778 | -120.8633 | 0.10986 | -14.6572 | -15.5032 | -15.4923 | -15.5095 | -15.3823 | -15.4535 | -15.5003 | 0.052488 | 0.14332 | 0.046142 | -0.097207 | 120.8388 | 121.0307 | 1.3446 | 1.503 | -14.6435 | -15.4895 | -15.4785 | -15.4958 | -15.3686 | -15.4397 | -15.4866 | 0.066221 | 0.15705 | 0.059875 | -0.083474 | 120.8525 | 121.0444 | 1.3583 | 1.5168 | -120.7863 | -1.2921 | -120.7926 | -1.2985
2790.7188 | 121.2799 | -120.9091 | 0.09613 | -14.616 | -15.4711 | -15.4556 | -15.4774 | -15.3503 | -15.4214 | -15.4683 | 0.047909 | 0.13874 | 0.041563 | -0.092628 | 120.8571 | 121.049 | 0.48845 | 0.65609 | -14.6022 | -15.4574 | -15.4419 | -15.4637 | -15.3365 | -15.4077 | -15.4545 | 0.061642 | 0.15247 | 0.055296 | -0.078895 | 120.8708 | 121.0627 | 0.50218 | 0.66982 | -120.8092 | -0.44054 | -120.8155 | -0.44689
2792.4062 | 121.1746 | -120.9 | 0.10529 | -14.6251 | -15.462 | -15.4419 | -15.4683 | -15.3457 | -15.4168 | -15.4545 | 0.052488 | 0.14332 | 0.046142 | -0.092628 | 120.8754 | 121.0673 | 0.20459 | 0.34935 | -14.6114 | -15.4482 | -15.4282 | -15.4545 | -15.3319 | -15.4031 | -15.4408 | 0.066221 | 0.15705 | 0.059875 | -0.078895 | 120.8891 | 121.081 | 0.21832 | 0.36308 | -120.8229 | -0.1521 | -120.8292 | -0.15845
2794.0781 | 121.2891 | -120.9549 | 0.11444 | -14.6389 | -15.4757 | -15.4556 | -15.4866 | -15.3548 | -15.426 | -15.4728 | 0.047909 | 0.1479 | 0.05072 | -0.092628 | 120.8983 | 121.0856 | 0.15881 | 0.28068 | -14.6251 | -15.462 | -15.4419 | -15.4729 | -15.3411 | -15.4123 | -15.4591 | 0.061642 | 0.16163 | 0.064453 | -0.078895 | 120.912 | 121.0993 | 0.17254 | 0.29441 | -120.8504 | -0.1109 | -120.8476 | -0.10809
2795.8281 | 120.9457 | -120.8862 | 0.15564 | -14.6434 | -15.4803 | -15.4602 | -15.4912 | -15.3548 | -15.426 | -15.4728 | 0.047909 | 0.13874 | 0.05072 | -0.092628 | 120.9303 | 121.1039 | 0.27785 | 0.42718 | -14.6297 | -15.4666 | -15.4465 | -15.4774 | -15.3411 | -15.4123 | -15.4591 | 0.061642 | 0.15247 | 0.064453 | -0.078895 | 120.9441 | 121.1176 | 0.29158 | 0.44091 | -120.8824 | -0.22994 | -120.8796 | -0.22713
2797.5781 | 121.3531 | -120.9824 | 0.10986 | -14.9227 | -15.7642 | -15.7441 | -15.7705 | -15.6478 | -15.719 | -15.7704 | 0.052488 | 0.14332 | 0.041563 | -0.092628 | 120.9395 | 121.1222 | 5.4697 | 5.6142 | -14.909 | -15.7504 | -15.7303 | -15.7567 | -15.6341 | -15.7053 | -15.7567 | 0.066221 | 0.15705 | 0.055296 | -0.078895 | 120.9532 | 121.136 | 5.4835 | 5.628 | -120.887 | -5.4173 | -120.8979 | -5.4282
2799.2656 | 120.8862 | -120.6619 | 0.15564 | -14.79 | -15.6222 | -15.6113 | -15.6423 | -15.5151 | -15.5817 | -15.6239 | 0.047909 | 0.13874 | 0.041563 | -0.097207 | 120.9578 | 121.1314 | 0.42435 | 0.58741 | -14.7762 | -15.6085 | -15.5976 | -15.6285 | -15.5013 | -15.5679 | -15.6102 | 0.061642 | 0.15247 | 0.055296 | -0.083474 | 120.9715 | 121.1451 | 0.43809 | 0.60115 | -120.9099 | -0.37645 | -120.9162 | -0.38279
2800.9531 | 121.1975 | -121.0373 | 0.14191 | -14.8312 | -15.6634 | -15.6342 | -15.6652 | -15.538 | -15.6137 | -15.6606 | 0.047909 | 0.14332 | 0.041563 | -0.092628 | 120.9715 | 121.1543 | 0.13592 | 0.26236 | -14.8174 | -15.6497 | -15.6205 | -15.6514 | -15.5242 | -15.6 | -15.6468 | 0.061642 | 0.15705 | 0.055296 | -0.078895 | 120.9853 | 121.168 | 0.14965 | 0.27609 | -120.9236 | -0.088007 | -120.93 | -0.094353
2802.7188 | 120.7993 | -120.3415 | 0.1236 | -14.8541 | -15.7001 | -15.6846 | -15.7201 | -15.5883 | -15.6549 | -15.7018 | 0.057066 | 0.14332 | 0.046142 | -0.092628 | 120.9898 | 121.1726 | 0.099289 | 0.212 | -14.8403 | -15.6863 | -15.6708 | -15.7064 | -15.5746 | -15.6412 | -15.688 | 0.070799 | 0.15705 | 0.059875 | -0.078895 | 121.0036 | 121.1863 | 0.11302 | 0.22573 | -120.9328 | -0.042223 | -120.9437 | -0.053147
2804.4062 | 121.225 | -121.0281 | 0.16022 | -14.8998 | -15.7275 | -15.7166 | -15.7521 | -15.6204 | -15.6915 | -15.7201 | 0.047909 | 0.1479 | 0.046142 | -0.097207 | 121.0082 | 121.1863 | 0.10845 | 0.212 | -14.8861 | -15.7138 | -15.7029 | -15.7384 | -15.6066 | -15.6778 | -15.7063 | 0.061642 | 0.16163 | 0.059875 | -0.083474 | 121.0219 | 121.2 | 0.12218 | 0.22573 | -120.9602 | -0.060537 | -120.962 | -0.062304
2806.0938 | 121.3852 | -121.0602 | 0.10986 | -14.9227 | -15.7367 | -15.7212 | -15.7613 | -15.6341 | -15.6915 | -15.7338 | 0.043331 | 0.1479 | 0.041563 | -0.097207 | 121.0127 | 121.1955 | 0.12676 | 0.23947 | -14.909 | -15.723 | -15.7075 | -15.7476 | -15.6204 | -15.6778 | -15.7201 | 0.057064 | 0.16163 | 0.055296 | -0.083474 | 121.0265 | 121.2092 | 0.14049 | 0.2532 | -120.9694 | -0.083428 | -120.9712 | -0.085196
2807.8438 | 121.376 | -121.1197 | 0.11444 | -14.9502 | -15.7871 | -15.7715 | -15.8208 | -15.6936 | -15.7556 | -15.7887 | 0.047909 | 0.1479 | 0.041563 | -0.092628 | 121.031 | 121.2092 | 0.88219 | 1.0269 | -14.9365 | -15.7733 | -15.7578 | -15.8071 | -15.6799 | -15.7419 | -15.775 | 0.061642 | 0.16163 | 0.055296 | -0.078895 | 121.0448 | 121.2229 | 0.89593 | 1.0407 | -120.9831 | -0.83428 | -120.9895 | -0.84063
2809.6094 | 121.3989 | -121.0922 | 0.11444 | -14.9868 | -15.8008 | -15.7944 | -15.8483 | -15.7211 | -15.7694 | -15.8071 | 0.043331 | 0.1479 | 0.041563 | -0.088049 | 121.0494 | 121.2229 | 0.33737 | 0.50501 | -14.9731 | -15.7871 | -15.7807 | -15.8346 | -15.7073 | -15.7556 | -15.7933 | 0.057064 | 0.16163 | 0.055296 | -0.074316 | 121.0631 | 121.2367 | 0.3511 | 0.51874 | -121.006 | -0.29403 | -121.0078 | -0.2958
2811.2969 | 121.2936 | -120.9732 | 0.14648 | -15.0097 | -15.8145 | -15.8082 | -15.862 | -15.7348 | -15.7785 | -15.8254 | 0.047909 | 0.13416 | 0.046142 | -0.088049 | 121.0448 | 121.2367 | 0.12218 | 0.23947 | -14.996 | -15.8008 | -15.7944 | -15.8483 | -15.7211 | -15.7648 | -15.8116 | 0.061642 | 0.1479 | 0.059875 | -0.074316 | 121.0585 | 121.2504 | 0.13591 | 0.2532 | -120.9969 | -0.074272 | -120.9986 | -0.076039
2813.0469 | 121.4264 | -121.1472 | 0.12817 | -15.0601 | -15.8695 | -15.8494 | -15.8987 | -15.776 | -15.8289 | -15.8666 | 0.052488 | 0.14332 | 0.041563 | -0.092628 | 121.0677 | 121.255 | 0.11302 | 0.22574 | -15.0464 | -15.8558 | -15.8357 | -15.8849 | -15.7623 | -15.8152 | -15.8528 | 0.066221 | 0.15705 | 0.055296 | -0.078895 | 121.0814 | 121.2687 | 0.12676 | 0.23947 | -121.0152 | -0.060536 | -121.0261 | -0.071461
2814.8125 | 121.3486 | -121.0098 | 0.13275 | -14.9594 | -15.7459 | -15.7258 | -15.7796 | -15.6524 | -15.7144 | -15.743 | 0.052488 | 0.13874 | 0.046142 | -0.097207 | 121.0814 | 121.2641 | 0.1176 | 0.22574 | -14.9456 | -15.7321 | -15.712 | -15.7659 | -15.6387 | -15.7007 | -15.7292 | 0.066221 | 0.15247 | 0.059875 | -0.083474 | 121.0951 | 121.2779 | 0.13134 | 0.23947 | -121.0289 | -0.065114 | -121.0353 | -0.07146
2816.4844 | 121.4813 | -121.138 | 0.10529 | -14.9823 | -15.7504 | -15.7441 | -15.7979 | -15.657 | -15.7282 | -15.7567 | 0.047909 | 0.14332 | 0.046142 | -0.097207 | 121.0951 | 121.2825 | 0.1176 | 0.23489 | -14.9685 | -15.7367 | -15.7303 | -15.7842 | -15.6432 | -15.7144 | -15.743 | 0.061642 | 0.15705 | 0.059875 | -0.083474 | 121.1089 | 121.2962 | 0.13134 | 0.24863 | -121.0472 | -0.069693 | -121.049 | -0.07146
2818.2344 | 121.4218 | -121.1563 | 0.14191 | -15.0097 | -15.7825 | -15.767 | -15.8117 | -15.689 | -15.7465 | -15.7796 | 0.043331 | 0.1479 | 0.036985 | -0.092628 | 121.1089 | 121.287 | 0.13134 | 0.23489 | -14.996 | -15.7688 | -15.7532 | -15.7979 | -15.6753 | -15.7327 | -15.7659 | 0.057064 | 0.16163 | 0.050718 | -0.078895 | 121.1226 | 121.3008 | 0.14507 | 0.24863 | -121.0655 | -0.088006 | -121.0719 | -0.094352
2819.9375 | 121.3806 | -121.2021 | 0.15564 | -15.0051 | -15.7642 | -15.767 | -15.8071 | -15.6799 | -15.7419 | -15.775 | 0.052488 | 0.1479 | 0.05072 | -0.097207 | 121.1134 | 121.3008 | 0.13134 | 0.24863 | -14.9914 | -15.7504 | -15.7532 | -15.7934 | -15.6661 | -15.7282 | -15.7613 | 0.066221 | 0.16163 | 0.064453 | -0.083474 | 121.1272 | 121.3145 | 0.14507 | 0.26236 | -121.061 | -0.078849 | -121.0627 | -0.080617
2821.6719 | 121.3898 | -121.2433 | 0.14648 | -15.0418 | -15.8054 | -15.799 | -15.8483 | -15.7119 | -15.774 | -15.8116 | 0.047909 | 0.14332 | 0.05072 | -0.10179 | 121.1272 | 121.3099 | 0.13592 | 0.26236 | -15.028 | -15.7917 | -15.7853 | -15.8346 | -15.6982 | -15.7602 | -15.7979 | 0.061642 | 0.15705 | 0.064453 | -0.088053 | 121.1409 | 121.3237 | 0.14965 | 0.27609 | -121.0793 | -0.088007 | -121.0765 | -0.085196
2823.3438 | 121.4172 | -121.1929 | 0.14648 | -15.0692 | -15.8329 | -15.8265 | -15.8803 | -15.7394 | -15.8014 | -15.8345 | 0.047909 | 0.14332 | 0.046142 | -0.10179 | 121.1318 | 121.3191 | 0.14507 | 0.26694 | -15.0555 | -15.8191 | -15.8128 | -15.8666 | -15.7256 | -15.7877 | -15.8208 | 0.061642 | 0.15705 | 0.059875 | -0.088053 | 121.1455 | 121.3328 | 0.15881 | 0.28067 | -121.0839 | -0.097164 | -121.0856 | -0.098931
2825.0312 | 121.5683 | -121.1975 | 0.11902 | -15.0647 | -15.8191 | -15.8128 | -15.862 | -15.7302 | -15.7877 | -15.8208 | 0.043331 | 0.14332 | 0.05072 | -0.08347 | 121.1501 | 121.3328 | 0.17712 | 0.30357 | -15.0509 | -15.8054 | -15.799 | -15.8483 | -15.7165 | -15.774 | -15.8071 | 0.057064 | 0.15705 | 0.064453 | -0.069737 | 121.1638 | 121.3465 | 0.19085 | 0.3173 | -121.1067 | -0.13379 | -121.0994 | -0.1264
2826.7812 | 121.4676 | -121.2204 | 0.14648 | -15.0647 | -15.8191 | -15.8128 | -15.862 | -15.7348 | -15.7923 | -15.8208 | 0.052488 | 0.13874 | 0.046142 | -0.10179 | 121.1684 | 121.3465 | 0.17254 | 0.3173 | -15.0509 | -15.8054 | -15.799 | -15.8483 | -15.7211 | -15.7785 | -15.8071 | 0.066221 | 0.15247 | 0.059875 | -0.088053 | 121.1821 | 121.3603 | 0.18628 | 0.33103 | -121.1159 | -0.12005 | -121.1222 | -0.1264
2828.5156 | 121.55 | -121.2204 | 0.1236 | -15.1059 | -15.8466 | -15.8402 | -15.8941 | -15.7623 | -15.8197 | -15.8574 | 0.052488 | 0.13874 | 0.046142 | -0.097207 | 121.173 | 121.3511 | -0.028906 | 0.019719 | -15.0921 | -15.8329 | -15.8265 | -15.8803 | -15.7485 | -15.806 | -15.8437 | 0.066221 | 0.15247 | 0.059875 | -0.083474 | 121.1867 | 121.3649 | -0.015173 | 0.033452 | -121.1205 | 0.081394 | -121.1268 | 0.075048
2830.2656 | 121.2387 | -121.0373 | 0.15106 | -15.0921 | -15.8466 | -15.8448 | -15.8895 | -15.7531 | -15.8243 | -15.8483 | 0.052488 | 0.15248 | 0.073611 | 0.05848 | 121.173 | 121.136 | -0.024328 | 0.033454 | -15.0784 | -15.8329 | -15.8311 | -15.8758 | -15.7394 | -15.8106 | -15.8345 | 0.066221 | 0.16621 | 0.087344 | 0.072213 | 121.1867 | 121.1497 | -0.010595 | 0.047187 | -121.1205 | 0.076816 | -121.0994 | 0.097939
2831.9375 | 121.5042 | -121.1197 | 0.10071 | -15.1837 | -15.9107 | -15.9043 | -15.9536 | -15.8309 | -15.8793 | -15.9261 | 0.052488 | 0.14332 | 0.036985 | 0.05848 | 121.3103 | 121.2825 | 0.016878 | 0.097548 | -15.17 | -15.897 | -15.8906 | -15.9399 | -15.8172 | -15.8655 | -15.9124 | 0.066221 | 0.15705 | 0.050718 | 0.072213 | 121.324 | 121.2962 | 0.030611 | 0.11128 | -121.2578 | 0.03561 | -121.2733 | 0.020107
2833.625 | 121.2936 | -120.8908 | 0.11444 | -15.1929 | -15.9107 | -15.9181 | -15.9582 | -15.8309 | -15.8793 | -15.9215 | 0.061645 | 0.15248 | 0.07819 | 0.063059 | 121.118 | 121.0764 | -0.006014 | 0.060923 | -15.1791 | -15.897 | -15.9043 | -15.9444 | -15.8172 | -15.8655 | -15.9078 | 0.075378 | 0.16621 | 0.091923 | 0.076792 | 121.1318 | 121.0902 | 0.007719 | 0.074656 | -121.0564 | 0.067659 | -121.0398 | 0.084204
2835.375 | 121.1563 | -120.8633 | 0.12817 | -15.2341 | -15.9473 | -15.941 | -15.9948 | -15.8584 | -15.9159 | -15.949 | 0.052488 | 0.1479 | 0.073611 | 0.053901 | 121.0356 | 120.9895 | -0.042641 | 0.028875 | -15.2203 | -15.9336 | -15.9272 | -15.9811 | -15.8447 | -15.9021 | -15.9352 | 0.066221 | 0.16163 | 0.087344 | 0.067634 | 121.0494 | 121.0032 | -0.028908 | 0.042608 | -120.9831 | 0.095129 | -120.962 | 0.11625
2837.0469 | 121.2982 | -120.9869 | 0.11902 | -15.3119 | -16.0297 | -16.0234 | -16.0543 | -15.9317 | -15.9754 | -16.0222 | 0.052488 | 0.14332 | 0.05072 | -0.10179 | 121.1455 | 121.1039 | -0.04722 | 0.010563 | -15.2982 | -16.016 | -16.0096 | -16.0406 | -15.9179 | -15.9617 | -16.0085 | 0.066221 | 0.15705 | 0.064453 | -0.088053 | 121.1592 | 121.1176 | -0.033487 | 0.024296 | -121.093 | 0.099708 | -121.0948 | 0.09794
2838.7969 | 120.9778 | -120.7214 | 0.13733 | -15.3623 | -16.0755 | -16.0646 | -16.1047 | -15.9729 | -16.0258 | -16.0634 | 0.066223 | 0.15706 | 0.07819 | 0.076796 | 120.8616 | 120.8292 | -0.051798 | 0.005985 | -15.3485 | -16.0618 | -16.0508 | -16.091 | -15.9591 | -16.012 | -16.0497 | 0.079956 | 0.17079 | 0.091923 | 0.090529 | 120.8754 | 120.843 | -0.038065 | 0.019718 | -120.7954 | 0.11802 | -120.7835 | 0.12999
2840.5469 | 120.9137 | -120.6802 | 0.12817 | -15.3256 | -16.016 | -16.0234 | -16.0497 | -15.9271 | -15.9846 | -16.0039 | 0.1349 | 0.22116 | 0.15144 | 0.1409 | 120.6831 | 120.6598 | -0.056376 | 0.010563 | -15.3119 | -16.0023 | -16.0096 | -16.036 | -15.9133 | -15.9708 | -15.9902 | 0.14863 | 0.23489 | 0.16517 | 0.15463 | 120.6968 | 120.6736 | -0.042643 | 0.024296 | -120.5482 | 0.19128 | -120.5317 | 0.20782
2842.25 | 121.2433 | -120.8862 | 0.10529 | -15.3806 | -16.071 | -16.0692 | -16.1001 | -15.9683 | -16.0258 | -16.068 | 0.052488 | 0.1479 | 0.05072 | 0.053901 | 121.0494 | 121.0169 | -0.070112 | -0.012328 | -15.3668 | -16.0572 | -16.0554 | -16.0864 | -15.9545 | -16.012 | -16.0543 | 0.066221 | 0.16163 | 0.064453 | 0.067634 | 121.0631 | 121.0307 | -0.056379 | 0.001405 | -120.9969 | 0.1226 | -120.9986 | 0.12083
2844 | 121.1838 | -120.9961 | 0.11902 | -15.3806 | -16.0664 | -16.0737 | -16.1138 | -15.9729 | -16.0303 | -16.0634 | 0.047909 | 0.14332 | 0.046142 | -0.092628 | 120.9166 | 121.081 | -0.07469 | -0.016906 | -15.3668 | -16.0526 | -16.06 | -16.1001 | -15.9591 | -16.0166 | -16.0497 | 0.061642 | 0.15705 | 0.059875 | -0.078895 | 120.9303 | 121.0948 | -0.060957 | -0.003173 | -120.8687 | 0.1226 | -120.8704 | 0.12083
2845.6875 | 121.312 | -121.0144 | 0.082397 | -15.3714 | -16.071 | -16.06 | -16.1001 | -15.9545 | -16.0166 | -16.0543 | 0.047909 | 0.14332 | 0.055298 | -0.092628 | 120.9349 | 121.1131 | -0.070112 | -0.012328 | -15.3577 | -16.0572 | -16.0463 | -16.0864 | -15.9408 | -16.0029 | -16.0405 | 0.061642 | 0.15705 | 0.069031 | -0.078895 | 120.9486 | 121.1268 | -0.056379 | 0.001405 | -120.887 | 0.11802 | -120.8796 | 0.12541
2847.4219 | 121.2662 | -121.0648 | 0.13275 | -15.3668 | -16.0435 | -16.0417 | -16.0864 | -15.95 | -15.9983 | -16.0405 | 0.052488 | 0.14332 | 0.041563 | -0.10179 | 120.9761 | 121.1497 | -0.065533 | -0.00775 | -15.3531 | -16.0298 | -16.028 | -16.0726 | -15.9362 | -15.9846 | -16.0268 | 0.066221 | 0.15705 | 0.055296 | -0.088053 | 120.9898 | 121.1634 | -0.0518 | 0.005983 | -120.9236 | 0.11802 | -120.9345 | 0.1071
2849.1562 | 121.2662 | -121.0739 | 0.11902 | -15.2249 | -15.9107 | -15.8997 | -15.9353 | -15.8126 | -15.8564 | -15.8986 | 0.047909 | 0.1479 | 0.046142 | -0.092628 | 121.0951 | 121.1726 | -0.065533 | -0.016906 | -15.2112 | -15.897 | -15.886 | -15.9216 | -15.7989 | -15.8426 | -15.8849 | 0.061642 | 0.16163 | 0.059875 | -0.078895 | 121.1089 | 121.1863 | -0.0518 | -0.003173 | -121.0472 | 0.11344 | -121.049 | 0.11167
2850.9062 | 121.4127 | -121.0602 | 0.091553 | -15.0784 | -15.7321 | -15.7395 | -15.775 | -15.6387 | -15.687 | -15.7201 | 0.047909 | 0.1479 | 0.05072 | -0.097207 | 121.0814 | 121.2046 | -0.070112 | -0.00775 | -15.0647 | -15.7184 | -15.7258 | -15.7613 | -15.6249 | -15.6732 | -15.7063 | 0.061642 | 0.16163 | 0.064453 | -0.083474 | 121.0951 | 121.2184 | -0.056379 | 0.005983 | -121.0335 | 0.11802 | -121.0307 | 0.12083
2852.6562 | 121.3303 | -121.1014 | 0.13275 | -14.909 | -15.5581 | -15.5701 | -15.6011 | -15.4601 | -15.513 | -15.5461 | 0.057066 | 0.15706 | 0.059877 | -0.069733 | 121.1684 | 121.2046 | -0.065533 | -0.012328 | -14.8953 | -15.5444 | -15.5564 | -15.5873 | -15.4464 | -15.4993 | -15.5324 | 0.070799 | 0.17079 | 0.07361 | -0.056 | 121.1821 | 121.2184 | -0.0518 | 0.001405 | -121.1113 | 0.1226 | -121.1085 | 0.12541
2854.3438 | 121.3715 | -121.0327 | 0.11444 | -14.8357 | -15.4803 | -15.5014 | -15.5186 | -15.3823 | -15.4352 | -15.4728 | 0.052488 | 0.14332 | 0.041563 | 0.053901 | 121.173 | 121.1268 | -0.065533 | -0.00775 | -14.822 | -15.4666 | -15.4877 | -15.5049 | -15.3686 | -15.4214 | -15.4591 | 0.066221 | 0.15705 | 0.055296 | 0.067634 | 121.1867 | 121.1405 | -0.0518 | 0.005983 | -121.1205 | 0.11802 | -121.1314 | 0.1071
2856.0938 | 121.2936 | -121.0922 | 0.15106 | -14.6801 | -15.32 | -15.3274 | -15.3584 | -15.2129 | -15.2658 | -15.3126 | 0.047909 | 0.15248 | 0.046142 | -0.092628 | 121.0036 | 121.1909 | -0.070112 | -0.012328 | -14.6663 | -15.3063 | -15.3137 | -15.3447 | -15.1992 | -15.252 | -15.2989 | 0.061642 | 0.16621 | 0.059875 | -0.078895 | 121.0173 | 121.2046 | -0.056379 | 0.001405 | -120.9557 | 0.11802 | -120.9574 | 0.11625
2857.8438 | 121.3165 | -121.1655 | 0.14648 | -14.5519 | -15.1872 | -15.1855 | -15.2165 | -15.0802 | -15.133 | -15.1753 | 0.052488 | 0.13416 | 0.055298 | -0.097207 | 121.0539 | 121.2229 | -0.065533 | -0.00775 | -14.5381 | -15.1735 | -15.1718 | -15.2027 | -15.0664 | -15.1192 | -15.1615 | 0.066221 | 0.1479 | 0.069031 | -0.083474 | 121.0677 | 121.2367 | -0.0518 | 0.005983 | -121.0014 | 0.11802 | -120.9986 | 0.12083
2859.5156 | 121.4218 | -121.1197 | 0.11444 | -14.3046 | -14.9308 | -14.9245 | -14.9601 | -14.8238 | -14.872 | -14.9189 | 0.047909 | 0.13874 | 0.046142 | -0.092628 | 121.0585 | 121.2367 | -0.065533 | -0.012328 | -14.2909 | -14.9171 | -14.9108 | -14.9463 | -14.8101 | -14.8583 | -14.9052 | 0.061642 | 0.15247 | 0.059875 | -0.078895 | 121.0722 | 121.2504 | -0.0518 | 0.001405 | -121.0106 | 0.11344 | -121.0124 | 0.11167
2861.2656 | 121.3577 | -121.17 | 0.15564 | -14.0483 | -14.6424 | -14.6452 | -14.6808 | -14.54 | -14.6065 | -14.6259 | 0.047909 | 0.13416 | 0.046142 | -0.097207 | 121.0768 | 121.2596 | -0.065533 | -0.016906 | -14.0345 | -14.6286 | -14.6315 | -14.667 | -14.5262 | -14.5927 | -14.6122 | 0.061642 | 0.1479 | 0.059875 | -0.083474 | 121.0906 | 121.2733 | -0.0518 | -0.003173 | -121.0289 | 0.11344 | -121.0307 | 0.11167
2863 | 121.4859 | -121.1563 | 0.10529 | -13.9292 | -14.5279 | -14.5124 | -14.5617 | -14.4209 | -14.4874 | -14.5206 | 0.038752 | 0.13874 | 0.05072 | -0.10637 | 121.0906 | 121.2825 | -0.060955 | -0.016906 | -13.9155 | -14.5142 | -14.4987 | -14.548 | -14.4072 | -14.4737 | -14.5069 | 0.052485 | 0.15247 | 0.064453 | -0.092632 | 121.1043 | 121.2962 | -0.047222 | -0.003173 | -121.0518 | 0.099707 | -121.0398 | 0.11167
2864.75 | 121.4539 | -121.1792 | 0.11902 | -13.9613 | -14.5462 | -14.5445 | -14.5801 | -14.4484 | -14.5103 | -14.5389 | 0.047909 | 0.14332 | 0.041563 | -0.092628 | 121.1089 | 121.2962 | -0.065533 | -0.021484 | -13.9475 | -14.5325 | -14.5308 | -14.5663 | -14.4347 | -14.4966 | -14.5252 | 0.061642 | 0.15705 | 0.055296 | -0.078895 | 121.1226 | 121.3099 | -0.0518 | -0.007751 | -121.061 | 0.11344 | -121.0673 | 0.1071
2866.4375 | 121.4081 | -121.2204 | 0.1236 | -14.062 | -14.6469 | -14.6406 | -14.6716 | -14.5445 | -14.5927 | -14.6259 | 0.047909 | 0.14332 | 0.041563 | -0.088049 | 121.1272 | 121.3053 | -0.070112 | -0.00775 | -14.0483 | -14.6332 | -14.6269 | -14.6579 | -14.5308 | -14.579 | -14.6122 | 0.061642 | 0.15705 | 0.055296 | -0.074316 | 121.1409 | 121.3191 | -0.056379 | 0.005983 | -121.0793 | 0.11802 | -121.0856 | 0.11167
2868.1875 | 121.3943 | -121.2387 | 0.15564 | -14.0299 | -14.6241 | -14.6132 | -14.6487 | -14.5079 | -14.5698 | -14.603 | 0.052488 | 0.1479 | 0.041563 | -0.097207 | 121.1455 | 121.3282 | -0.065533 | -0.021484 | -14.0162 | -14.6103 | -14.5994 | -14.635 | -14.4942 | -14.5561 | -14.5893 | 0.066221 | 0.16163 | 0.055296 | -0.083474 | 121.1592 | 121.342 | -0.0518 | -0.007751 | -121.093 | 0.11802 | -121.1039 | 0.1071
2869.9219 | 121.4584 | -121.225 | 0.1236 | -14.0986 | -14.6744 | -14.6727 | -14.7128 | -14.5812 | -14.6339 | -14.6671 | 0.047909 | 0.1479 | 0.05072 | -0.097207 | 121.1547 | 121.3328 | -0.065533 | -0.012328 | -14.0849 | -14.6607 | -14.659 | -14.6991 | -14.5674 | -14.6202 | -14.6534 | 0.061642 | 0.16163 | 0.064453 | -0.083474 | 121.1684 | 121.3465 | -0.0518 | 0.001405 | -121.1067 | 0.11344 | -121.1039 | 0.11625
2871.6719 | 121.5591 | -121.2158 | 0.11444 | -14.0391 | -14.6149 | -14.6086 | -14.6487 | -14.5171 | -14.5744 | -14.5984 | 0.052488 | 0.1479 | 0.046142 | -0.097207 | 121.1638 | 121.3511 | -0.070112 | -0.012328 | -14.0254 | -14.6012 | -14.5949 | -14.635 | -14.5033 | -14.5607 | -14.5847 | 0.066221 | 0.16163 | 0.059875 | -0.083474 | 121.1775 | 121.3649 | -0.056379 | 0.001405 | -121.1113 | 0.1226 | -121.1177 | 0.11625
2873.3438 | 121.4401 | -121.2524 | 0.12817 | -14.0299 | -14.5966 | -14.5948 | -14.635 | -14.4988 | -14.5515 | -14.5847 | 0.047909 | 0.15248 | 0.046142 | -0.097207 | 121.1821 | 121.3649 | -0.070112 | -0.00775 | -14.0162 | -14.5828 | -14.5811 | -14.6213 | -14.485 | -14.5378 | -14.5709 | 0.061642 | 0.16621 | 0.059875 | -0.083474 | 121.1959 | 121.3786 | -0.056379 | 0.005983 | -121.1342 | 0.11802 | -121.136 | 0.11625
2875.0781 | 121.5271 | -121.2662 | 0.13733 | -14.0528 | -14.6241 | -14.6132 | -14.6579 | -14.5216 | -14.579 | -14.603 | 0.052488 | 0.1479 | 0.046142 | -0.097207 | 121.1959 | 121.3694 | -0.065533 | -0.00775 | -14.0391 | -14.6103 | -14.5994 | -14.6442 | -14.5079 | -14.5653 | -14.5893 | 0.066221 | 0.16163 | 0.059875 | -0.083474 | 121.2096 | 121.3832 | -0.0518 | 0.005983 | -121.1434 | 0.11802 | -121.1497 | 0.11167
2876.8281 | 121.6324 | -121.225 | 0.10071 | -14.094 | -14.6515 | -14.6498 | -14.6854 | -14.5491 | -14.611 | -14.6442 | 0.047909 | 0.1479 | 0.05072 | -0.092628 | 121.2096 | 121.3969 | -0.070112 | -0.00775 | -14.0803 | -14.6378 | -14.6361 | -14.6716 | -14.5354 | -14.5973 | -14.6305 | 0.061642 | 0.16163 | 0.064453 | -0.078895 | 121.2233 | 121.4106 | -0.056379 | 0.005983 | -121.1617 | 0.11802 | -121.1589 | 0.12083
2878.5156 | 121.6095 | -121.2616 | 0.086975 | -14.062 | -14.6149 | -14.6086 | -14.6533 | -14.5171 | -14.5607 | -14.603 | 0.043331 | 0.13416 | 0.046142 | -0.097207 | 121.2187 | 121.4015 | -0.065533 | -0.012328 | -14.0483 | -14.6012 | -14.5949 | -14.6396 | -14.5033 | -14.5469 | -14.5893 | 0.057064 | 0.1479 | 0.059875 | -0.083474 | 121.2325 | 121.4152 | -0.0518 | 0.001405 | -121.1754 | 0.10886 | -121.1726 | 0.11167
2880.25 | 121.5775 | -121.2708 | 0.1236 | -14.062 | -14.6195 | -14.6132 | -14.6533 | -14.5125 | -14.5698 | -14.5984 | 0.052488 | 0.15248 | 0.041563 | -0.092628 | 121.2233 | 121.4106 | -0.065533 | -0.012328 | -14.0483 | -14.6057 | -14.5994 | -14.6396 | -14.4988 | -14.5561 | -14.5847 | 0.066221 | 0.16621 | 0.055296 | -0.078895 | 121.2371 | 121.4244 | -0.0518 | 0.001405 | -121.1708 | 0.11802 | -121.1818 | 0.1071
2881.9531 | 121.4996 | -121.3165 | 0.16022 | -14.0483 | -14.5874 | -14.5811 | -14.6213 | -14.4896 | -14.5424 | -14.5801 | 0.038752 | 0.1479 | 0.05072 | -0.092628 | 121.2371 | 121.4244 | -0.065533 | -0.012328 | -14.0345 | -14.5737 | -14.5674 | -14.6075 | -14.4759 | -14.5286 | -14.5664 | 0.052485 | 0.16163 | 0.064453 | -0.078895 | 121.2508 | 121.4381 | -0.0518 | 0.001405 | -121.1983 | 0.10428 | -121.1863 | 0.11625
2883.7031 | 121.6095 | -121.312 | 0.11444 | -14.0437 | -14.5783 | -14.5765 | -14.6121 | -14.4804 | -14.5286 | -14.5755 | 0.052488 | 0.15248 | 0.05072 | -0.097207 | 121.2508 | 121.4335 | -0.065533 | -0.016906 | -14.0299 | -14.5645 | -14.5628 | -14.5984 | -14.4667 | -14.5149 | -14.5618 | 0.066221 | 0.16621 | 0.064453 | -0.083474 | 121.2645 | 121.4473 | -0.0518 | -0.003173 | -121.1983 | 0.11802 | -121.2001 | 0.11625
2885.4375 | 121.6095 | -121.344 | 0.10986 | -13.8972 | -14.4775 | -14.4712 | -14.5114 | -14.3751 | -14.4371 | -14.4748 | 0.052488 | 0.14332 | 0.05072 | -0.088049 | 121.26 | 121.4473 | -0.060955 | -0.00775 | -13.8834 | -14.4638 | -14.4575 | -14.4976 | -14.3614 | -14.4233 | -14.4611 | 0.066221 | 0.15705 | 0.064453 | -0.074316 | 121.2737 | 121.461 | -0.047222 | 0.005983 | -121.2075 | 0.11344 | -121.2092 | 0.11167
2887.1875 | 121.5546 | -121.3531 | 0.14648 | -13.9246 | -14.4867 | -14.485 | -14.5205 | -14.3935 | -14.4462 | -14.4885 | 0.057066 | 0.13874 | 0.059877 | -0.097207 | 121.2737 | 121.4518 | -0.065533 | -0.012328 | -13.9109 | -14.473 | -14.4712 | -14.5068 | -14.3797 | -14.4325 | -14.4748 | 0.070799 | 0.15247 | 0.07361 | -0.083474 | 121.2874 | 121.4656 | -0.0518 | 0.001405 | -121.2166 | 0.1226 | -121.2138 | 0.12541
2888.9375 | 121.5775 | -121.3806 | 0.14191 | -13.9933 | -14.5416 | -14.5307 | -14.5801 | -14.4438 | -14.5103 | -14.5343 | 0.057066 | 0.14332 | 0.041563 | -0.10179 | 121.2828 | 121.461 | -0.070112 | -0.012328 | -13.9796 | -14.5279 | -14.517 | -14.5663 | -14.4301 | -14.4966 | -14.5206 | 0.070799 | 0.15705 | 0.055296 | -0.088053 | 121.2966 | 121.4747 | -0.056379 | 0.001405 | -121.2258 | 0.12718 | -121.2413 | 0.11167
2890.7031 | 121.6782 | -121.3394 | 0.09613 | -13.9887 | -14.5233 | -14.517 | -14.5526 | -14.4164 | -14.4783 | -14.5114 | 0.047909 | 0.14332 | 0.055298 | -0.092628 | 121.292 | 121.4656 | -0.060955 | -0.003172 | -13.975 | -14.5096 | -14.5033 | -14.5388 | -14.4026 | -14.4645 | -14.4977 | 0.061642 | 0.15705 | 0.069031 | -0.078895 | 121.3057 | 121.4793 | -0.047222 | 0.010561 | -121.2441 | 0.10886 | -121.2367 | 0.11625
2892.3906 | 121.5729 | -121.3806 | 0.14191 | -13.9567 | -14.4913 | -14.4758 | -14.5068 | -14.3797 | -14.4325 | -14.4748 | 0.052488 | 0.1479 | 0.046142 | -0.092628 | 121.2966 | 121.4747 | -0.070112 | -0.00775 | -13.943 | -14.4775 | -14.4621 | -14.4931 | -14.366 | -14.4188 | -14.4611 | 0.066221 | 0.16163 | 0.059875 | -0.078895 | 121.3103 | 121.4885 | -0.056379 | 0.005983 | -121.2441 | 0.1226 | -121.2504 | 0.11625
2894.1406 | 121.701 | -121.344 | 0.11444 | -14.0025 | -14.5187 | -14.5124 | -14.5434 | -14.4072 | -14.46 | -14.5023 | 0.034174 | 0.1479 | 0.05072 | -0.092628 | 121.3149 | 121.4976 | -0.060955 | -0.012328 | -13.9887 | -14.505 | -14.4987 | -14.5297 | -14.3935 | -14.4462 | -14.4885 | 0.047907 | 0.16163 | 0.064453 | -0.078895 | 121.3286 | 121.5114 | -0.047222 | 0.001405 | -121.2807 | 0.095129 | -121.2642 | 0.11167
2895.8906 | 121.6278 | -121.3943 | 0.14648 | -14.0437 | -14.5416 | -14.5353 | -14.5663 | -14.4438 | -14.492 | -14.5389 | 0.029595 | 0.15248 | 0.05072 | -0.10179 | 121.3195 | 121.5022 | -0.070112 | -0.00775 | -14.0299 | -14.5279 | -14.5216 | -14.5526 | -14.4301 | -14.4783 | -14.5252 | 0.043328 | 0.16621 | 0.064453 | -0.088053 | 121.3332 | 121.5159 | -0.056379 | 0.005983 | -121.2899 | 0.099707 | -121.2687 | 0.12083
2897.5781 | 121.6049 | -121.4355 | 0.13733 | -14.0757 | -14.5737 | -14.5674 | -14.6029 | -14.4576 | -14.5149 | -14.5572 | 0.029595 | 0.1479 | 0.05072 | -0.088049 | 121.3378 | 121.5068 | -0.07469 | -0.00775 | -14.062 | -14.56 | -14.5536 | -14.5892 | -14.4438 | -14.5012 | -14.5435 | 0.043328 | 0.16163 | 0.064453 | -0.074316 | 121.3515 | 121.5205 | -0.060957 | 0.005983 | -121.3082 | 0.10429 | -121.2871 | 0.12541
2899.3281 | 121.6507 | -121.4264 | 0.12817 | -14.094 | -14.5783 | -14.572 | -14.6029 | -14.4713 | -14.5195 | -14.5664 | 0.034174 | 0.14332 | 0.046142 | -0.10179 | 121.3424 | 121.5205 | -0.065533 | -0.021484 | -14.0803 | -14.5645 | -14.5582 | -14.5892 | -14.4576 | -14.5057 | -14.5526 | 0.047907 | 0.15705 | 0.059875 | -0.088053 | 121.3561 | 121.5342 | -0.0518 | -0.007751 | -121.3082 | 0.099707 | -121.2962 | 0.11167
2901.0156 | 121.6599 | -121.4172 | 0.12817 | -14.0757 | -14.5508 | -14.5399 | -14.5801 | -14.4438 | -14.4966 | -14.5343 | 0.029595 | 0.15248 | 0.05072 | -0.10179 | 121.3515 | 121.5251 | -0.070112 | -0.012328 | -14.062 | -14.5371 | -14.5262 | -14.5663 | -14.4301 | -14.4828 | -14.5206 | 0.043328 | 0.16621 | 0.064453 | -0.088053 | 121.3652 | 121.5388 | -0.056379 | 0.001405 | -121.3219 | 0.099707 | -121.3008 | 0.12083
2902.7656 | 121.6324 | -121.4355 | 0.13733 | -14.1261 | -14.5966 | -14.5765 | -14.6258 | -14.4896 | -14.5424 | -14.5801 | 0.034174 | 0.1479 | 0.046142 | -0.092628 | 121.3515 | 121.5342 | -0.056376 | -0.012328 | -14.1124 | -14.5828 | -14.5628 | -14.6121 | -14.4759 | -14.5286 | -14.5664 | 0.047907 | 0.16163 | 0.059875 | -0.078895 | 121.3652 | 121.548 | -0.042643 | 0.001405 | -121.3173 | 0.09055 | -121.3054 | 0.10252
2904.5156 | 121.6965 | -121.4218 | 0.10529 | -14.1078 | -14.5783 | -14.5628 | -14.6075 | -14.4667 | -14.5149 | -14.5664 | 0.034174 | 0.13874 | 0.055298 | -0.088049 | 121.3652 | 121.548 | -0.070112 | -0.016906 | -14.094 | -14.5645 | -14.5491 | -14.5938 | -14.453 | -14.5012 | -14.5526 | 0.047907 | 0.15247 | 0.069031 | -0.074316 | 121.379 | 121.5617 | -0.056379 | -0.003173 | -121.3311 | 0.10429 | -121.31 | 0.12541
2906.2812 | 121.7194 | -121.4218 | 0.11444 | -14.1169 | -14.5828 | -14.5628 | -14.5984 | -14.4667 | -14.5195 | -14.5618 | 0.029595 | 0.14332 | 0.046142 | -0.088049 | 121.3698 | 121.548 | -0.070112 | -0.012328 | -14.1032 | -14.5691 | -14.5491 | -14.5846 | -14.453 | -14.5057 | -14.5481 | 0.043328 | 0.15705 | 0.059875 | -0.074316 | 121.3836 | 121.5617 | -0.056379 | 0.001405 | -121.3402 | 0.099707 | -121.3237 | 0.11625
2907.9688 | 121.7468 | -121.4264 | 0.11902 | -14.149 | -14.5966 | -14.5811 | -14.6213 | -14.4804 | -14.5424 | -14.5847 | 0.038752 | 0.1479 | 0.046142 | -0.092628 | 121.3881 | 121.5571 | -0.065533 | -0.00775 | -14.1353 | -14.5828 | -14.5674 | -14.6075 | -14.4667 | -14.5286 | -14.5709 | 0.052485 | 0.16163 | 0.059875 | -0.078895 | 121.4019 | 121.5709 | -0.0518 | 0.005983 | -121.3494 | 0.10428 | -121.342 | 0.11167
2909.6719 | 121.8018 | -121.4447 | 0.11902 | -14.1856 | -14.6424 | -14.6223 | -14.6487 | -14.5216 | -14.579 | -14.6213 | 0.025017 | 0.1479 | 0.046142 | -0.10179 | 121.3836 | 121.5617 | -0.065533 | -0.016906 | -14.1719 | -14.6286 | -14.6086 | -14.635 | -14.5079 | -14.5653 | -14.6076 | 0.03875 | 0.16163 | 0.059875 | -0.088053 | 121.3973 | 121.5754 | -0.0518 | -0.003173 | -121.3585 | 0.09055 | -121.3374 | 0.11167
2911.4219 | 121.7743 | -121.4493 | 0.09613 | -14.2039 | -14.6424 | -14.6269 | -14.6625 | -14.5308 | -14.579 | -14.6122 | 0.034174 | 0.15248 | 0.05072 | -0.092628 | 121.3927 | 121.5709 | -0.070112 | -0.012328 | -14.1902 | -14.6286 | -14.6132 | -14.6487 | -14.5171 | -14.5653 | -14.5984 | 0.047907 | 0.16621 | 0.064453 | -0.078895 | 121.4065 | 121.5846 | -0.056379 | 0.001405 | -121.3585 | 0.10429 | -121.342 | 0.12083
2913.1719 | 121.7651 | -121.4172 | 0.1236 | -14.1948 | -14.6195 | -14.6132 | -14.6396 | -14.5033 | -14.5653 | -14.6167 | 0.034174 | 0.15248 | 0.055298 | -0.10179 | 121.411 | 121.58 | -0.060955 | -0.012328 | -14.181 | -14.6057 | -14.5994 | -14.6258 | -14.4896 | -14.5515 | -14.603 | 0.047907 | 0.16621 | 0.069031 | -0.088053 | 121.4248 | 121.5938 | -0.047222 | 0.001405 | -121.3769 | 0.095129 | -121.3557 | 0.11625
2914.9219 | 121.6782 | -121.5042 | 0.13733 | -14.1581 | -14.5828 | -14.5674 | -14.6029 | -14.4667 | -14.5195 | -14.5709 | 0.034174 | 0.15248 | 0.055298 | -0.10179 | 121.4202 | 121.58 | -0.070112 | -0.00775 | -14.1444 | -14.5691 | -14.5536 | -14.5892 | -14.453 | -14.5057 | -14.5572 | 0.047907 | 0.16621 | 0.069031 | -0.088053 | 121.4339 | 121.5938 | -0.056379 | 0.005983 | -121.386 | 0.10429 | -121.3649 | 0.12541
2916.6094 | 121.6736 | -121.4905 | 0.14191 | -14.1948 | -14.6012 | -14.5948 | -14.6213 | -14.4942 | -14.5469 | -14.5893 | 0.038752 | 0.15248 | 0.05072 | -0.088049 | 121.4248 | 121.5983 | -0.065533 | -0.016906 | -14.181 | -14.5874 | -14.5811 | -14.6075 | -14.4804 | -14.5332 | -14.5755 | 0.052485 | 0.16621 | 0.064453 | -0.074316 | 121.4385 | 121.6121 | -0.0518 | -0.003173 | -121.386 | 0.10428 | -121.374 | 0.11625
2918.3594 | 121.7468 | -121.4951 | 0.13275 | -14.2222 | -14.6332 | -14.6086 | -14.6487 | -14.5171 | -14.5698 | -14.6122 | 0.034174 | 0.15248 | 0.05072 | -0.092628 | 121.4339 | 121.6029 | -0.065533 | -0.00775 | -14.2085 | -14.6195 | -14.5949 | -14.635 | -14.5033 | -14.5561 | -14.5984 | 0.047907 | 0.16621 | 0.064453 | -0.078895 | 121.4477 | 121.6166 | -0.0518 | 0.005983 | -121.3997 | 0.099707 | -121.3832 | 0.11625
2920.0469 | 121.6873 | -121.5271 | 0.16937 | -14.2039 | -14.6103 | -14.5994 | -14.6213 | -14.4896 | -14.5515 | -14.5984 | 0.043331 | 0.1479 | 0.055298 | -0.097207 | 121.4248 | 121.6075 | -0.07469 | -0.00775 | -14.1902 | -14.5966 | -14.5857 | -14.6075 | -14.4759 | -14.5378 | -14.5847 | 0.057064 | 0.16163 | 0.069031 | -0.083474 | 121.4385 | 121.6212 | -0.060957 | 0.005983 | -121.3814 | 0.11802 | -121.3695 | 0.12999
2921.8125 | 121.7926 | -121.4951 | 0.13275 | -14.1948 | -14.6012 | -14.5811 | -14.6121 | -14.4896 | -14.5424 | -14.5893 | 0.029595 | 0.1479 | 0.046142 | -0.092628 | 121.4385 | 121.6167 | -0.065533 | -0.016906 | -14.181 | -14.5874 | -14.5674 | -14.5984 | -14.4759 | -14.5286 | -14.5755 | 0.043328 | 0.16163 | 0.059875 | -0.078895 | 121.4522 | 121.6304 | -0.0518 | -0.003173 | -121.4089 | 0.095128 | -121.3924 | 0.11167
2923.4844 | 121.7468 | -121.5317 | 0.12817 | -14.2039 | -14.6195 | -14.5857 | -14.6258 | -14.5033 | -14.5515 | -14.5984 | 0.038752 | 0.1479 | 0.05072 | -0.078891 | 121.4522 | 121.635 | -0.065533 | -0.00775 | -14.1902 | -14.6057 | -14.572 | -14.6121 | -14.4896 | -14.5378 | -14.5847 | 0.052485 | 0.16163 | 0.064453 | -0.065158 | 121.466 | 121.6487 | -0.0518 | 0.005983 | -121.4135 | 0.10428 | -121.4015 | 0.11625
2925.2188 | 121.7651 | -121.5408 | 0.13275 | -14.2451 | -14.6424 | -14.6223 | -14.6533 | -14.5308 | -14.5836 | -14.6167 | 0.038752 | 0.14332 | 0.055298 | -0.092628 | 121.4614 | 121.635 | -0.070112 | -0.016906 | -14.2314 | -14.6286 | -14.6086 | -14.6396 | -14.5171 | -14.5698 | -14.603 | 0.052485 | 0.15705 | 0.069031 | -0.078895 | 121.4751 | 121.6487 | -0.056379 | -0.003173 | -121.4226 | 0.10886 | -121.4061 | 0.12541
2926.9062 | 121.7331 | -121.5317 | 0.12817 | -14.2177 | -14.6103 | -14.5903 | -14.6258 | -14.5033 | -14.5515 | -14.5984 | 0.034174 | 0.1479 | 0.055298 | -0.10179 | 121.466 | 121.635 | -0.070112 | -0.012328 | -14.2039 | -14.5966 | -14.5765 | -14.6121 | -14.4896 | -14.5378 | -14.5847 | 0.047907 | 0.16163 | 0.069031 | -0.088053 | 121.4797 | 121.6487 | -0.056379 | 0.001405 | -121.4318 | 0.10429 | -121.4107 | 0.12541
2928.6562 | 121.8658 | -121.5317 | 0.11444 | -14.1856 | -14.5874 | -14.5628 | -14.5892 | -14.4759 | -14.5378 | -14.5755 | 0.038752 | 0.1479 | 0.05072 | -0.092628 | 121.4751 | 121.6487 | -0.065533 | -0.00775 | -14.1719 | -14.5737 | -14.5491 | -14.5755 | -14.4621 | -14.5241 | -14.5618 | 0.052485 | 0.16163 | 0.064453 | -0.078895 | 121.4889 | 121.6624 | -0.0518 | 0.005983 | -121.4364 | 0.10428 | -121.4244 | 0.11625
2930.4062 | 121.8521 | -121.5408 | 0.11444 | -14.2085 | -14.6012 | -14.5857 | -14.6121 | -14.4759 | -14.5424 | -14.5847 | 0.029595 | 0.15248 | 0.05072 | -0.097207 | 121.4705 | 121.6533 | -0.065533 | -0.00775 | -14.1948 | -14.5874 | -14.572 | -14.5984 | -14.4621 | -14.5286 | -14.5709 | 0.043328 | 0.16621 | 0.064453 | -0.083474 | 121.4843 | 121.667 | -0.0518 | 0.005983 | -121.441 | 0.095128 | -121.4198 | 0.11625
2932.1562 | 121.3028 | -121.1609 | 0.11902 | -14.1215 | -14.5187 | -14.4941 | -14.5205 | -14.4026 | -14.46 | -14.4977 | 0.079959 | 0.17079 | 0.10566 | 0.090533 | 121.205 | 121.168 | -0.065533 | -0.021484 | -14.1078 | -14.505 | -14.4804 | -14.5068 | -14.3889 | -14.4462 | -14.484 | 0.093692 | 0.18453 | 0.11939 | 0.10427 | 121.2187 | 121.1817 | -0.0518 | -0.007751 | -121.1251 | 0.14549 | -121.0994 | 0.17119
2933.9062 | 121.5454 | -121.3531 | 0.13275 | -14.1307 | -14.5325 | -14.517 | -14.5388 | -14.4072 | -14.4645 | -14.516 | 0.052488 | 0.1479 | 0.055298 | -0.028522 | 121.4843 | 121.4427 | -0.065533 | -0.016906 | -14.1169 | -14.5187 | -14.5033 | -14.5251 | -14.3935 | -14.4508 | -14.5023 | 0.066221 | 0.16163 | 0.069031 | -0.014789 | 121.498 | 121.4564 | -0.0518 | -0.003173 | -121.4318 | 0.11802 | -121.429 | 0.12083
2935.5781 | 121.6919 | -121.3623 | 0.10529 | -14.149 | -14.5508 | -14.5307 | -14.5526 | -14.4255 | -14.4874 | -14.5343 | 0.057066 | 0.1479 | 0.05072 | -0.097207 | 121.3149 | 121.4885 | -0.065533 | -0.012328 | -14.1353 | -14.5371 | -14.517 | -14.5388 | -14.4118 | -14.4737 | -14.5206 | 0.070799 | 0.16163 | 0.064453 | -0.083474 | 121.3286 | 121.5022 | -0.0518 | 0.001405 | -121.2578 | 0.1226 | -121.2642 | 0.11625
2937.3281 | 121.6141 | -121.4401 | 0.14648 | -14.1627 | -14.5554 | -14.5262 | -14.5572 | -14.4255 | -14.5012 | -14.5389 | 0.047909 | 0.15248 | 0.046142 | -0.097207 | 121.3515 | 121.5159 | -0.065533 | -0.00775 | -14.149 | -14.5416 | -14.5124 | -14.5434 | -14.4118 | -14.4874 | -14.5252 | 0.061642 | 0.16621 | 0.059875 | -0.083474 | 121.3652 | 121.5297 | -0.0518 | 0.005983 | -121.3036 | 0.11344 | -121.3054 | 0.11167
2939.0625 | 120.8817 | -120.5933 | 0.10986 | -12.8167 | -13.2641 | -13.1343 | -13.2248 | -13.0338 | -13.0864 | -13.2021 | 2.7721 | 2.973 | 2.8068 | 2.87 | 116.9473 | 116.8875 | -0.033484 | 0.019719 | -12.8029 | -13.2504 | -13.1205 | -13.2111 | -13.0201 | -13.0727 | -13.1883 | 2.7858 | 2.9868 | 2.8206 | 2.8837 | 116.961 | 116.9012 | -0.019751 | 0.033452 | -114.1752 | 2.8056 | -114.1405 | 2.8403
2940.7969 | 120.9091 | -120.5933 | 0.11902 | 0.95054 | 0.86608 | 0.88083 | 0.88153 | 0.92897 | 0.89596 | 0.84376 | 4.4707 | 4.3055 | 4.4047 | 4.2987 | 0.40075 | 0.32995 | -0.065533 | 0.005985 | 0.96427 | 0.87982 | 0.89456 | 0.89526 | 0.9427 | 0.90969 | 0.85749 | 4.4845 | 4.3192 | 4.4184 | 4.3124 | 0.41449 | 0.34368 | -0.0518 | 0.019718 | 4.07 | 4.5363 | 4.0039 | 4.4702
2942.5625 | 121.4035 | -121.138 | 0.10986 | 0.089802 | -0.077151 | 0.015472 | -0.047909 | 0.054577 | 0.030642 | -0.090186 | 0.043331 | 0.13874 | 0.055298 | 0.044743 | 0.29546 | 0.38489 | -0.065533 | -0.016906 | 0.10354 | -0.063418 | 0.029205 | -0.034176 | 0.06831 | 0.044375 | -0.076453 | 0.057064 | 0.15247 | 0.069031 | 0.058476 | 0.30919 | 0.39862 | -0.0518 | -0.003173 | -0.25213 | 0.10886 | -0.24016 | 0.12083
2944.25 | 121.3989 | -121.2662 | 0.1236 | 0.094381 | -0.077151 | 0.015472 | -0.043331 | 0.049999 | 0.035221 | -0.08103 | 0.034174 | 0.13416 | 0.041563 | -0.097207 | 0.25883 | 0.33911 | -0.065533 | -0.021484 | 0.10811 | -0.063418 | 0.029205 | -0.029598 | 0.063732 | 0.048954 | -0.067297 | 0.047907 | 0.1479 | 0.055296 | -0.083474 | 0.27257 | 0.35284 | -0.0518 | -0.007751 | -0.22466 | 0.099707 | -0.21727 | 0.1071
2946 | 121.4767 | -121.2982 | 0.13733 | 0.094381 | -0.077151 | 0.010893 | -0.038752 | 0.049999 | 0.035221 | -0.071874 | 0.038752 | 0.13416 | 0.036985 | -0.088049 | 0.23594 | 0.31164 | -0.070112 | -0.012328 | 0.10811 | -0.063418 | 0.024626 | -0.025019 | 0.063732 | 0.048954 | -0.058141 | 0.052485 | 0.1479 | 0.050718 | -0.074316 | 0.24967 | 0.32537 | -0.056379 | 0.001405 | -0.19719 | 0.10886 | -0.19896 | 0.1071
2947.7812 | 121.1655 | -120.8084 | 0.11902 | 0.10812 | -0.063415 | 0.033786 | -0.020438 | 0.086622 | 0.053534 | -0.058139 | 0.13032 | 0.21658 | 0.13771 | 0.12717 | 0.22221 | 0.28417 | -0.065533 | -0.00775 | 0.12185 | -0.049682 | 0.047519 | -0.006705 | 0.10035 | 0.067267 | -0.044406 | 0.14405 | 0.23031 | 0.15144 | 0.1409 | 0.23594 | 0.2979 | -0.0518 | 0.005983 | -0.091884 | 0.19586 | -0.084499 | 0.20324
2949.4688 | 121.3074 | -121.0876 | 0.11902 | 0.098959 | -0.067994 | 0.020051 | -0.038752 | 0.063733 | 0.030642 | -0.08103 | 0.038752 | 0.13874 | 0.041563 | 0.040164 | 0.20847 | 0.27501 | -0.070112 | -0.00775 | 0.11269 | -0.054261 | 0.033784 | -0.025019 | 0.077466 | 0.044375 | -0.067297 | 0.052485 | 0.15247 | 0.055296 | 0.053897 | 0.2222 | 0.28875 | -0.056379 | 0.005983 | -0.16972 | 0.10886 | -0.16691 | 0.11167
2951.2188 | 121.4676 | -121.1426 | 0.07782 | 0.094381 | -0.077151 | 0.029208 | -0.043331 | 0.054577 | 0.035221 | -0.076452 | 0.043331 | 0.12043 | 0.036985 | -0.097207 | 0.19931 | 0.26586 | -0.060955 | -0.003172 | 0.10811 | -0.063418 | 0.042941 | -0.029598 | 0.06831 | 0.048954 | -0.062719 | 0.057064 | 0.13416 | 0.050718 | -0.083474 | 0.21305 | 0.27959 | -0.047222 | 0.010561 | -0.15598 | 0.10429 | -0.16233 | 0.09794
2952.9688 | 118.3456 | -85.4507 | 32.0663 | 6.44 | 6.2462 | 6.4713 | 6.3208 | 6.5141 | 6.4495 | 6.2872 | 28.1278 | 28.4862 | 28.2346 | 28.2607 | -0.6156 | -0.75047 | -0.056376 | 0.001406 | 6.4538 | 6.2599 | 6.485 | 6.3345 | 6.5278 | 6.4633 | 6.3009 | 28.1416 | 28.4999 | 28.2483 | 28.2745 | -0.60187 | -0.73674 | -0.042643 | 0.015139 | 28.7434 | 28.1842 | 28.8502 | 28.291
2954.7188 | 121.3028 | -121.0007 | 0.09613 | 0.089802 | -0.08173 | 0.020051 | -0.047909 | 0.054577 | 0.026064 | -0.090186 | 0.043331 | 0.12958 | 0.041563 | 0.049322 | 0.18558 | 0.2567 | -0.065533 | -0.012328 | 0.10354 | -0.067997 | 0.033784 | -0.034176 | 0.06831 | 0.039797 | -0.076453 | 0.057064 | 0.14332 | 0.055296 | 0.063055 | 0.19931 | 0.27043 | -0.0518 | 0.001405 | -0.14225 | 0.10886 | -0.14402 | 0.1071
2956.3906 | 121.3348 | -121.1334 | 0.10986 | 0.098959 | -0.072572 | 0.020051 | -0.038752 | 0.059155 | 0.030642 | -0.076452 | 0.038752 | 0.13874 | 0.046142 | -0.10179 | 0.18558 | 0.2567 | -0.060955 | -0.012328 | 0.11269 | -0.058839 | 0.033784 | -0.025019 | 0.072888 | 0.044375 | -0.062719 | 0.052485 | 0.15247 | 0.059875 | -0.088053 | 0.19931 | 0.27043 | -0.047222 | 0.001405 | -0.14683 | 0.099707 | -0.13944 | 0.1071
2958.1406 | 121.4722 | -121.138 | 0.091553 | 0.098959 | -0.067994 | 0.024629 | -0.038752 | 0.059155 | 0.035221 | -0.067295 | 0.034174 | 0.13416 | 0.032407 | -0.092628 | 0.16727 | 0.22465 | -0.07469 | -0.00775 | 0.11269 | -0.054261 | 0.038362 | -0.025019 | 0.072888 | 0.048954 | -0.053562 | 0.047907 | 0.1479 | 0.04614 | -0.078895 | 0.181 | 0.23839 | -0.060957 | 0.005983 | -0.13309 | 0.10886 | -0.13486 | 0.1071
2959.875 | 121.4127 | -121.225 | 0.12817 | 0.10354 | -0.063415 | 0.020051 | -0.034174 | 0.063733 | 0.030642 | -0.071874 | 0.029595 | 0.13874 | 0.032407 | -0.097207 | 0.15353 | 0.20176 | -0.070112 | -0.012328 | 0.11727 | -0.049682 | 0.033784 | -0.020441 | 0.077466 | 0.044375 | -0.058141 | 0.043328 | 0.15247 | 0.04614 | -0.083474 | 0.16727 | 0.2155 | -0.056379 | 0.001405 | -0.12394 | 0.099707 | -0.12113 | 0.10252
2961.5625 | 121.3898 | -121.2433 | 0.10529 | 0.098959 | -0.063415 | 0.033786 | -0.029595 | 0.059155 | 0.035221 | -0.08103 | 0.034174 | 0.12958 | 0.036985 | -0.10179 | 0.11691 | 0.1743 | -0.060955 | -0.016906 | 0.11269 | -0.049682 | 0.047519 | -0.015862 | 0.072888 | 0.048954 | -0.067297 | 0.047907 | 0.14332 | 0.050718 | -0.088053 | 0.13064 | 0.18803 | -0.047222 | -0.003173 | -0.082734 | 0.095129 | -0.079923 | 0.09794
2963.2969 | 121.4905 | -121.2067 | 0.11902 | 0.10812 | -0.049678 | 0.024629 | -0.025017 | 0.06831 | 0.039799 | -0.062717 | 0.038752 | 0.14332 | 0.036985 | -0.097207 | 0.075705 | 0.12851 | -0.070112 | -0.016906 | 0.12185 | -0.035945 | 0.038362 | -0.011284 | 0.082043 | 0.053532 | -0.048984 | 0.052485 | 0.15705 | 0.050718 | -0.083474 | 0.089438 | 0.14225 | -0.056379 | -0.003173 | -0.036953 | 0.10886 | -0.03872 | 0.1071
2965.0469 | 121.5271 | -121.2524 | 0.11444 | 0.10812 | -0.063415 | 0.024629 | -0.034174 | 0.06831 | 0.039799 | -0.067295 | 0.043331 | 0.13416 | 0.041563 | -0.092628 | 0.06197 | 0.087313 | -0.065533 | -0.016906 | 0.12185 | -0.049682 | 0.038362 | -0.020441 | 0.082043 | 0.053532 | -0.053562 | 0.057064 | 0.1479 | 0.055296 | -0.078895 | 0.075703 | 0.10105 | -0.0518 | -0.003173 | -0.018639 | 0.10886 | -0.020407 | 0.1071
2966.8125 | 121.1243 | -120.813 | 0.10071 | 0.11727 | -0.049678 | 0.029208 | -0.029595 | 0.086622 | 0.048956 | -0.062717 | 0.043331 | 0.1479 | 0.073611 | 0.053901 | 0.13522 | 0.087313 | -0.060955 | -0.012328 | 0.13101 | -0.035945 | 0.042941 | -0.015862 | 0.10035 | 0.062689 | -0.048984 | 0.057064 | 0.16163 | 0.087344 | 0.067634 | 0.14895 | 0.10105 | -0.047222 | 0.001405 | -0.09189 | 0.10429 | -0.06161 | 0.13457
2968.5 | 121.2296 | -121.0419 | 0.13275 | 0.11269 | -0.063415 | 0.038365 | -0.020438 | 0.072888 | 0.044377 | -0.067295 | 0.029595 | 0.13416 | 0.032407 | -0.001048 | 0.048236 | 0.082735 | -0.056376 | -0.012328 | 0.12643 | -0.049682 | 0.052098 | -0.006705 | 0.086621 | 0.05811 | -0.053562 | 0.043328 | 0.1479 | 0.04614 | 0.012685 | 0.061969 | 0.096468 | -0.042643 | 0.001405 | -0.018641 | 0.085971 | -0.015829 | 0.088783
2970.2344 | 121.2845 | -121.138 | 0.11444 | 0.11727 | -0.058836 | 0.038365 | -0.029595 | 0.063733 | 0.044377 | -0.067295 | 0.034174 | 0.12958 | 0.036985 | -0.097207 | 0.048236 | 0.082735 | -0.065533 | -0.012328 | 0.13101 | -0.045103 | 0.052098 | -0.015862 | 0.077466 | 0.05811 | -0.053562 | 0.047907 | 0.14332 | 0.050718 | -0.083474 | 0.061969 | 0.096468 | -0.0518 | 0.001405 | -0.014062 | 0.099707 | -0.011251 | 0.10252
2971.9844 | 121.4355 | -121.1288 | 0.09613 | 0.11727 | -0.058836 | 0.038365 | -0.025017 | 0.077466 | 0.053534 | -0.058139 | 0.061645 | 0.16164 | 0.064455 | -0.069733 | 0.052814 | 0.082735 | -0.070112 | -0.012328 | 0.13101 | -0.045103 | 0.052098 | -0.011284 | 0.091199 | 0.067267 | -0.044406 | 0.075378 | 0.17537 | 0.078188 | -0.056 | 0.066547 | 0.096468 | -0.056379 | 0.001405 | 0.008831 | 0.13176 | 0.011641 | 0.13457
2973.7344 | 121.0693 | -120.8313 | 0.10071 | 0.10354 | -0.058836 | 0.033786 | -0.029595 | 0.086622 | 0.039799 | -0.058139 | 0.043331 | 0.13416 | 0.059877 | 0.053901 | 0.12607 | 0.082735 | -0.070112 | -0.00775 | 0.11727 | -0.045103 | 0.047519 | -0.015862 | 0.10035 | 0.053532 | -0.044406 | 0.057064 | 0.1479 | 0.07361 | 0.067634 | 0.1398 | 0.096468 | -0.056379 | 0.005983 | -0.082734 | 0.11344 | -0.066188 | 0.12999
2975.4219 | 121.1929 | -121.0144 | 0.13733 | 0.10812 | -0.058836 | 0.033786 | -0.020438 | 0.06831 | 0.039799 | -0.076452 | 0.038752 | 0.12501 | 0.036985 | 0.044743 | 0.043657 | 0.073579 | -0.060955 | -0.00775 | 0.12185 | -0.045103 | 0.047519 | -0.006705 | 0.082043 | 0.053532 | -0.062719 | 0.052485 | 0.13874 | 0.050718 | 0.058476 | 0.05739 | 0.087312 | -0.047222 | 0.005983 | -0.004905 | 0.099707 | -0.006672 | 0.09794
2977.1562 | 121.257 | -121.0693 | 0.12817 | 0.11727 | -0.067994 | 0.020051 | -0.029595 | 0.072888 | 0.044377 | -0.076452 | 0.034174 | 0.13416 | 0.036985 | -0.10179 | 0.048236 | 0.073579 | -0.070112 | -0.003172 | 0.13101 | -0.054261 | 0.033784 | -0.015862 | 0.086621 | 0.05811 | -0.062719 | 0.047907 | 0.1479 | 0.050718 | -0.088053 | 0.061969 | 0.087312 | -0.056379 | 0.010561 | -0.014062 | 0.10429 | -0.011251 | 0.1071
2978.8438 | 121.4127 | -121.0831 | 0.091553 | 0.10812 | -0.067994 | 0.033786 | -0.029595 | 0.072888 | 0.039799 | -0.067295 | 0.034174 | 0.12501 | 0.041563 | -0.10179 | 0.048236 | 0.073579 | -0.07469 | -0.012328 | 0.12185 | -0.054261 | 0.047519 | -0.015862 | 0.086621 | 0.053532 | -0.053562 | 0.047907 | 0.13874 | 0.055296 | -0.088053 | 0.061969 | 0.087312 | -0.060957 | 0.001405 | -0.014062 | 0.10886 | -0.006673 | 0.11625
2980.5938 | 120.9366 | -120.6299 | 0.10071 | 0.10812 | -0.063415 | 0.029208 | -0.025017 | 0.082044 | 0.039799 | -0.071874 | 0.047909 | 0.13416 | 0.069033 | 0.049322 | 0.048236 | 0.078157 | -0.060955 | -0.00775 | 0.12185 | -0.049682 | 0.042941 | -0.011284 | 0.095777 | 0.053532 | -0.058141 | 0.061642 | 0.1479 | 0.082766 | 0.063055 | 0.061969 | 0.09189 | -0.047222 | 0.005983 | -0.000327 | 0.10886 | 0.020797 | 0.12999
2982.3438 | 121.1334 | -120.9183 | 0.11902 | 0.10354 | -0.067994 | 0.020051 | -0.029595 | 0.063733 | 0.039799 | -0.067295 | 0.034174 | 0.13874 | 0.036985 | 0.035585 | 0.043657 | 0.073579 | -0.070112 | -0.016906 | 0.11727 | -0.054261 | 0.033784 | -0.015862 | 0.077466 | 0.053532 | -0.053562 | 0.047907 | 0.15247 | 0.050718 | 0.049318 | 0.05739 | 0.087312 | -0.056379 | -0.003173 | -0.009483 | 0.10429 | -0.006672 | 0.1071
2984.0938 | 121.2891 | -120.9641 | 0.064087 | 0.10812 | -0.072572 | 0.033786 | -0.029595 | 0.063733 | 0.030642 | -0.071874 | 0.038752 | 0.12501 | 0.032407 | -0.10179 | 0.034501 | 0.073579 | -0.065533 | -0.00775 | 0.12185 | -0.058839 | 0.047519 | -0.015862 | 0.077466 | 0.044375 | -0.058141 | 0.052485 | 0.13874 | 0.04614 | -0.088053 | 0.048234 | 0.087312 | -0.0518 | 0.005983 | 0.004251 | 0.10428 | -0.002094 | 0.09794
2985.8281 | 121.2158 | -121.0693 | 0.11444 | 0.10354 | -0.067994 | 0.020051 | -0.029595 | 0.06831 | 0.035221 | -0.067295 | 0.029595 | 0.12958 | 0.032407 | -0.092628 | 0.048236 | 0.073579 | -0.065533 | -0.016906 | 0.11727 | -0.054261 | 0.033784 | -0.015862 | 0.082043 | 0.048954 | -0.053562 | 0.043328 | 0.14332 | 0.04614 | -0.078895 | 0.061969 | 0.087312 | -0.0518 | -0.003173 | -0.018641 | 0.095128 | -0.015829 | 0.09794
2987.5156 | 121.3531 | -121.0556 | 0.1236 | 0.11269 | -0.067994 | 0.029208 | -0.034174 | 0.063733 | 0.044377 | -0.062717 | 0.038752 | 0.13874 | 0.041563 | -0.097207 | 0.043657 | 0.073579 | -0.065533 | -0.012328 | 0.12643 | -0.054261 | 0.042941 | -0.020441 | 0.077466 | 0.05811 | -0.048984 | 0.052485 | 0.15247 | 0.055296 | -0.083474 | 0.05739 | 0.087312 | -0.0518 | 0.001405 | -0.004905 | 0.10428 | -0.002094 | 0.1071
2989.2656 | 121.1563 | -120.8771 | 0.073242 | 0.10812 | -0.067994 | 0.024629 | -0.034174 | 0.06831 | 0.039799 | -0.067295 | 0.034174 | 0.13416 | 0.046142 | 0.044743 | 0.043657 | 0.082735 | -0.065533 | -0.012328 | 0.12185 | -0.054261 | 0.038362 | -0.020441 | 0.082043 | 0.053532 | -0.053562 | 0.047907 | 0.1479 | 0.059875 | 0.058476 | 0.05739 | 0.096468 | -0.0518 | 0.001405 | -0.009483 | 0.099707 | 0.002485 | 0.11167
2990.9531 | 121.2112 | -120.9732 | 0.11444 | 0.10354 | -0.063415 | 0.029208 | -0.029595 | 0.06831 | 0.035221 | -0.071874 | 0.038752 | 0.13416 | 0.032407 | -0.097207 | 0.039079 | 0.069001 | -0.07469 | -0.016906 | 0.11727 | -0.049682 | 0.042941 | -0.015862 | 0.082043 | 0.048954 | -0.058141 | 0.052485 | 0.1479 | 0.04614 | -0.083474 | 0.052812 | 0.082734 | -0.060957 | -0.003173 | -0.000327 | 0.11344 | -0.006672 | 0.1071
2992.7031 | 121.0373 | -120.8176 | 0.1236 | 0.10354 | -0.077151 | 0.020051 | -0.029595 | 0.063733 | 0.026064 | -0.071874 | 0.029595 | 0.13416 | 0.055298 | 0.044743 | 0.034501 | 0.073579 | -0.070112 | -0.016906 | 0.11727 | -0.063418 | 0.033784 | -0.015862 | 0.077466 | 0.039797 | -0.058141 | 0.043328 | 0.1479 | 0.069031 | 0.058476 | 0.048234 | 0.087312 | -0.056379 | -0.003173 | -0.004906 | 0.099707 | 0.020797 | 0.12541
2994.4375 | 121.1197 | -120.9366 | 0.12817 | 0.10354 | -0.072572 | 0.020051 | -0.029595 | 0.06831 | 0.035221 | -0.071874 | 0.029595 | 0.12958 | 0.036985 | -0.097207 | 0.034501 | 0.069001 | -0.065533 | -0.016906 | 0.11727 | -0.058839 | 0.033784 | -0.015862 | 0.082043 | 0.048954 | -0.058141 | 0.043328 | 0.14332 | 0.050718 | -0.083474 | 0.048234 | 0.082734 | -0.0518 | -0.003173 | -0.004906 | 0.095128 | 0.002484 | 0.10252
2996.125 | 121.1563 | -121.0052 | 0.11444 | 0.10812 | -0.072572 | 0.020051 | -0.034174 | 0.059155 | 0.026064 | -0.071874 | 0.029595 | 0.12958 | 0.036985 | -0.10179 | 0.043657 | 0.069001 | -0.065533 | -0.00775 | 0.12185 | -0.058839 | 0.033784 | -0.020441 | 0.072888 | 0.039797 | -0.058141 | 0.043328 | 0.14332 | 0.050718 | -0.088053 | 0.05739 | 0.082734 | -0.0518 | 0.005983 | -0.014062 | 0.095128 | -0.006672 | 0.10252
2997.8906 | 121.2662 | -121.0144 | 0.10071 | 0.098959 | -0.072572 | 0.020051 | -0.025017 | 0.063733 | 0.030642 | -0.076452 | 0.034174 | 0.12958 | 0.032407 | -0.10179 | 0.034501 | 0.064423 | -0.065533 | -0.021484 | 0.11269 | -0.058839 | 0.033784 | -0.011284 | 0.077466 | 0.044375 | -0.062719 | 0.047907 | 0.14332 | 0.04614 | -0.088053 | 0.048234 | 0.078156 | -0.0518 | -0.007751 | -0.000327 | 0.099707 | -0.002094 | 0.09794
2999.6406 | 121.312 | -121.0419 | 0.10529 | 0.098959 | -0.08173 | 0.024629 | -0.043331 | 0.054577 | 0.021485 | -0.071874 | 0.029595 | 0.12501 | 0.032407 | -0.10179 | 0.029923 | 0.069001 | -0.060955 | -0.012328 | 0.11269 | -0.067997 | 0.038362 | -0.029598 | 0.06831 | 0.035218 | -0.058141 | 0.043328 | 0.13874 | 0.04614 | -0.088053 | 0.043656 | 0.082734 | -0.047222 | 0.001405 | -0.000328 | 0.09055 | 0.002484 | 0.093362
3001.3906 | 121.3165 | -121.1014 | 0.12817 | 0.098959 | -0.072572 | 0.024629 | -0.038752 | 0.063733 | 0.030642 | -0.076452 | 0.029595 | 0.12958 | 0.032407 | -0.097207 | 0.039079 | 0.064423 | -0.070112 | -0.00775 | 0.11269 | -0.058839 | 0.038362 | -0.025019 | 0.077466 | 0.044375 | -0.062719 | 0.043328 | 0.14332 | 0.04614 | -0.083474 | 0.052812 | 0.078156 | -0.056379 | 0.005983 | -0.009484 | 0.099707 | -0.006672 | 0.10252
3003.125 | 120.7809 | -120.4056 | 0.10071 | 0.56138 | 0.44483 | 0.48249 | 0.47862 | 0.53526 | 0.50222 | 0.44546 | 2.4013 | 2.3183 | 2.3582 | 2.2885 | 0.034501 | 0.069001 | -0.060955 | -0.003172 | 0.57511 | 0.45857 | 0.49622 | 0.49235 | 0.549 | 0.51595 | 0.45919 | 2.415 | 2.332 | 2.3719 | 2.3022 | 0.048234 | 0.082734 | -0.047222 | 0.010561 | 2.3668 | 2.4622 | 2.3237 | 2.4191
3004.8125 | 121.1838 | -120.8908 | 0.10071 | 0.10354 | -0.08173 | 0.020051 | -0.029595 | 0.059155 | 0.030642 | -0.076452 | 0.029595 | 0.12958 | 0.036985 | 0.040164 | 0.039079 | 0.069001 | -0.065533 | -0.00775 | 0.11727 | -0.067997 | 0.033784 | -0.015862 | 0.072888 | 0.044375 | -0.062719 | 0.043328 | 0.14332 | 0.050718 | 0.053897 | 0.052812 | 0.082734 | -0.0518 | 0.005983 | -0.009484 | 0.095128 | -0.002094 | 0.10252
3006.5469 | 121.2616 | -120.9778 | 0.10071 | 0.10354 | -0.08173 | 0.024629 | -0.034174 | 0.063733 | 0.030642 | -0.071874 | 0.038752 | 0.12958 | 0.036985 | -0.10179 | 0.039079 | 0.073579 | -0.060955 | -0.012328 | 0.11727 | -0.067997 | 0.038362 | -0.020441 | 0.077466 | 0.044375 | -0.058141 | 0.052485 | 0.14332 | 0.050718 | -0.088053 | 0.052812 | 0.087312 | -0.047222 | 0.001405 | -0.000327 | 0.099707 | -0.002094 | 0.09794
3008.2969 | 117.6178 | -92.6102 | 24.7971 | 7.6396 | 7.4825 | 7.6617 | 7.557 | 7.6952 | 7.6308 | 7.5142 | 32.688 | 32.891 | 32.7808 | 32.7528 | -0.011281 | -0.045451 | -0.04722 | 0.001406 | 7.6533 | 7.4962 | 7.6755 | 7.5707 | 7.7089 | 7.6445 | 7.5279 | 32.7017 | 32.9048 | 32.7946 | 32.7665 | 0.002452 | -0.031718 | -0.033487 | 0.015139 | 32.6993 | 32.7352 | 32.7921 | 32.8281
3010.0469 | 121.1472 | -120.8038 | 0.10071 | 0.098959 | -0.086309 | 0.020051 | -0.038752 | 0.059155 | 0.026064 | -0.08103 | 0.038752 | 0.13416 | 0.064455 | 0.044743 | 0.034501 | 0.064423 | -0.070112 | -0.00775 | 0.11269 | -0.072576 | 0.033784 | -0.025019 | 0.072888 | 0.039797 | -0.067297 | 0.052485 | 0.1479 | 0.078188 | 0.058476 | 0.048234 | 0.078156 | -0.056379 | 0.005983 | 0.004251 | 0.10886 | 0.029954 | 0.13457
3011.7969 | 121.2296 | -120.8862 | 0.086975 | 0.098959 | -0.086309 | 0.015472 | -0.038752 | 0.054577 | 0.030642 | -0.076452 | 0.038752 | 0.13416 | 0.036985 | -0.092628 | 0.039079 | 0.059844 | -0.060955 | -0.016906 | 0.11269 | -0.072576 | 0.029205 | -0.025019 | 0.06831 | 0.044375 | -0.062719 | 0.052485 | 0.1479 | 0.050718 | -0.078895 | 0.052812 | 0.073577 | -0.047222 | -0.003173 | -0.000327 | 0.099707 | -0.002094 | 0.09794
3013.5 | 121.2112 | -120.9778 | 0.10986 | 0.094381 | -0.086309 | 0.020051 | -0.043331 | 0.06831 | 0.030642 | -0.071874 | 0.025017 | 0.12501 | 0.036985 | -0.092628 | 0.029923 | 0.069001 | -0.070112 | -0.012328 | 0.10811 | -0.072576 | 0.033784 | -0.029598 | 0.082043 | 0.044375 | -0.058141 | 0.03875 | 0.13874 | 0.050718 | -0.078895 | 0.043656 | 0.082734 | -0.056379 | 0.001405 | -0.004906 | 0.095129 | 0.007062 | 0.1071
3015.25 | 121.3211 | -121.0281 | 0.07782 | 0.098959 | -0.08173 | 0.015472 | -0.034174 | 0.059155 | 0.026064 | -0.085608 | 0.038752 | 0.12958 | 0.036985 | -0.10179 | 0.025345 | 0.069001 | -0.060955 | -0.016906 | 0.11269 | -0.067997 | 0.029205 | -0.020441 | 0.072888 | 0.039797 | -0.071875 | 0.052485 | 0.14332 | 0.050718 | -0.088053 | 0.039078 | 0.082734 | -0.047222 | -0.003173 | 0.013407 | 0.099707 | 0.01164 | 0.09794
3016.9219 | 121.2204 | -121.0739 | 0.11444 | 0.098959 | -0.086309 | 0.015472 | -0.034174 | 0.054577 | 0.035221 | -0.076452 | 0.034174 | 0.12501 | 0.036985 | -0.097207 | 0.020767 | 0.055266 | -0.065533 | -0.012328 | 0.11269 | -0.072576 | 0.029205 | -0.020441 | 0.06831 | 0.048954 | -0.062719 | 0.047907 | 0.13874 | 0.050718 | -0.083474 | 0.0345 | 0.068999 | -0.0518 | 0.001405 | 0.013407 | 0.099707 | 0.016218 | 0.10252
3018.6719 | 121.2845 | -121.106 | 0.1236 | 0.089802 | -0.086309 | 0.020051 | -0.029595 | 0.059155 | 0.030642 | -0.076452 | 0.029595 | 0.13874 | 0.036985 | -0.11094 | 0.034501 | 0.059844 | -0.070112 | -0.016906 | 0.10354 | -0.072576 | 0.033784 | -0.015862 | 0.072888 | 0.044375 | -0.062719 | 0.043328 | 0.15247 | 0.050718 | -0.097211 | 0.048234 | 0.073577 | -0.056379 | -0.003173 | -0.004906 | 0.099707 | 0.002484 | 0.1071
3020.4219 | 121.3257 | -121.1014 | 0.10071 | 0.085224 | -0.08173 | 0.024629 | -0.043331 | 0.049999 | 0.021485 | -0.08103 | 0.029595 | 0.13416 | 0.036985 | -0.10637 | 0.029923 | 0.055266 | -0.065533 | -0.00775 | 0.098957 | -0.067997 | 0.038362 | -0.029598 | 0.063732 | 0.035218 | -0.067297 | 0.043328 | 0.1479 | 0.050718 | -0.092632 | 0.043656 | 0.068999 | -0.0518 | 0.005983 | -0.000328 | 0.095128 | 0.007062 | 0.10252
3022.1094 | 121.3028 | -121.1472 | 0.10986 | 0.076067 | -0.08173 | 0.015472 | -0.038752 | 0.049999 | 0.030642 | -0.076452 | 0.038752 | 0.12958 | 0.032407 | -0.10179 | 0.020767 | 0.050688 | -0.065533 | -0.012328 | 0.0898 | -0.067997 | 0.029205 | -0.025019 | 0.063732 | 0.044375 | -0.062719 | 0.052485 | 0.14332 | 0.04614 | -0.088053 | 0.0345 | 0.064421 | -0.0518 | 0.001405 | 0.017985 | 0.10428 | 0.01164 | 0.09794
3023.8594 | 121.4355 | -121.1288 | 0.07782 | 0.085224 | -0.095467 | 0.010893 | -0.043331 | 0.049999 | 0.021485 | -0.085608 | 0.025017 | 0.13416 | 0.036985 | -0.10179 | 0.025345 | 0.041532 | -0.07469 | -0.012328 | 0.098957 | -0.081734 | 0.024626 | -0.029598 | 0.063732 | 0.035218 | -0.071875 | 0.03875 | 0.1479 | 0.050718 | -0.088053 | 0.039078 | 0.055265 | -0.060957 | 0.001405 | -0.000328 | 0.099707 | 0.01164 | 0.11167
3025.5469 | 121.4172 | -121.1426 | 0.10986 | 0.071489 | -0.086309 | 0.010893 | -0.047909 | 0.059155 | 0.026064 | -0.085608 | 0.034174 | 0.12501 | 0.032407 | -0.10637 | 0.020767 | 0.050688 | -0.065533 | -0.016906 | 0.085222 | -0.072576 | 0.024626 | -0.034176 | 0.072888 | 0.039797 | -0.071875 | 0.047907 | 0.13874 | 0.04614 | -0.092632 | 0.0345 | 0.064421 | -0.0518 | -0.003173 | 0.013407 | 0.099707 | 0.01164 | 0.09794
3027.2812 | 121.4813 | -121.1472 | 0.10986 | 0.076067 | -0.090888 | 0.015472 | -0.047909 | 0.049999 | 0.026064 | -0.076452 | 0.029595 | 0.12958 | 0.032407 | -0.10179 | 0.029923 | 0.050688 | -0.060955 | -0.016906 | 0.0898 | -0.077155 | 0.029205 | -0.034176 | 0.063732 | 0.039797 | -0.062719 | 0.043328 | 0.14332 | 0.04614 | -0.088053 | 0.043656 | 0.064421 | -0.047222 | -0.003173 | -0.000328 | 0.09055 | 0.002484 | 0.093362
3029.0312 | 121.4676 | -121.1838 | 0.09613 | 0.071489 | -0.08173 | 0.010893 | -0.043331 | 0.049999 | 0.021485 | -0.085608 | 0.029595 | 0.12958 | 0.032407 | -0.10637 | 0.025345 | 0.050688 | -0.065533 | -0.012328 | 0.085222 | -0.067997 | 0.024626 | -0.029598 | 0.063732 | 0.035218 | -0.071875 | 0.043328 | 0.14332 | 0.04614 | -0.092632 | 0.039078 | 0.064421 | -0.0518 | 0.001405 | 0.00425 | 0.095128 | 0.007062 | 0.09794
3030.7812 | 121.4172 | -121.2433 | 0.13733 | 0.071489 | -0.090888 | 0.015472 | -0.038752 | 0.059155 | 0.021485 | -0.08103 | 0.034174 | 0.12958 | 0.032407 | -0.10179 | 0.020767 | 0.050688 | -0.065533 | -0.012328 | 0.085222 | -0.077155 | 0.029205 | -0.025019 | 0.072888 | 0.035218 | -0.067297 | 0.047907 | 0.14332 | 0.04614 | -0.088053 | 0.0345 | 0.064421 | -0.0518 | 0.001405 | 0.013407 | 0.099707 | 0.01164 | 0.09794
3032.4688 | 121.5134 | -121.1975 | 0.10986 | 0.071489 | -0.095467 | 0.010893 | -0.043331 | 0.054577 | 0.021485 | -0.085608 | 0.038752 | 0.13874 | 0.032407 | -0.097207 | 0.025345 | 0.04611 | -0.065533 | -0.012328 | 0.085222 | -0.081734 | 0.024626 | -0.029598 | 0.06831 | 0.035218 | -0.071875 | 0.052485 | 0.15247 | 0.04614 | -0.083474 | 0.039078 | 0.059843 | -0.0518 | 0.001405 | 0.013407 | 0.10428 | 0.007062 | 0.09794
3034.2188 | 121.4172 | -121.2662 | 0.10529 | 0.071489 | -0.090888 | 0.024629 | -0.043331 | 0.063733 | 0.026064 | -0.08103 | 0.029595 | 0.12501 | 0.036985 | -0.10179 | 0.020767 | 0.055266 | -0.070112 | -0.012328 | 0.085222 | -0.077155 | 0.038362 | -0.029598 | 0.077466 | 0.039797 | -0.067297 | 0.043328 | 0.13874 | 0.050718 | -0.088053 | 0.0345 | 0.068999 | -0.056379 | 0.001405 | 0.008828 | 0.099707 | 0.016218 | 0.1071
3035.9688 | 121.4218 | -121.2662 | 0.10986 | 0.06691 | -0.095467 | 0.010893 | -0.043331 | 0.045421 | 0.016907 | -0.08103 | 0.034174 | 0.13416 | 0.036985 | -0.10637 | 0.025345 | 0.04611 | -0.070112 | -0.016906 | 0.080643 | -0.081734 | 0.024626 | -0.029598 | 0.059154 | 0.03064 | -0.067297 | 0.047907 | 0.1479 | 0.050718 | -0.092632 | 0.039078 | 0.059843 | -0.056379 | -0.003173 | 0.008829 | 0.10429 | 0.01164 | 0.1071
3037.7344 | 121.5683 | -121.2204 | 0.09613 | 0.06691 | -0.086309 | 0.015472 | -0.043331 | 0.054577 | 0.016907 | -0.085608 | 0.034174 | 0.12501 | 0.036985 | -0.10179 | 0.025345 | 0.050688 | -0.065533 | -0.00775 | 0.080643 | -0.072576 | 0.029205 | -0.029598 | 0.06831 | 0.03064 | -0.071875 | 0.047907 | 0.13874 | 0.050718 | -0.088053 | 0.039078 | 0.064421 | -0.0518 | 0.005983 | 0.008829 | 0.099707 | 0.01164 | 0.10252
3039.4219 | 121.5042 | -121.2799 | 0.11444 | 0.06691 | -0.086309 | 0.015472 | -0.038752 | 0.063733 | 0.026064 | -0.076452 | 0.034174 | 0.1479 | 0.041563 | -0.088049 | 0.025345 | 0.055266 | -0.065533 | -0.00775 | 0.080643 | -0.072576 | 0.029205 | -0.025019 | 0.077466 | 0.039797 | -0.062719 | 0.047907 | 0.16163 | 0.055296 | -0.074316 | 0.039078 | 0.068999 | -0.0518 | 0.005983 | 0.008829 | 0.099707 | 0.016218 | 0.1071
3041.1562 | 121.2708 | -121.0876 | 0.11902 | 0.06691 | -0.086309 | 0.010893 | -0.043331 | 0.054577 | 0.021485 | -0.08103 | 0.029595 | 0.13416 | 0.055298 | 0.040164 | 0.029923 | 0.055266 | -0.065533 | -0.00775 | 0.080643 | -0.072576 | 0.024626 | -0.029598 | 0.06831 | 0.035218 | -0.067297 | 0.043328 | 0.1479 | 0.069031 | 0.053897 | 0.043656 | 0.068999 | -0.0518 | 0.005983 | -0.000328 | 0.095128 | 0.025375 | 0.12083
3042.9062 | 121.4127 | -121.1563 | 0.12817 | 0.06691 | -0.095467 | 0.015472 | -0.047909 | 0.054577 | 0.016907 | -0.090186 | 0.029595 | 0.13416 | 0.036985 | -0.10637 | 0.029923 | 0.050688 | -0.060955 | -0.00775 | 0.080643 | -0.081734 | 0.029205 | -0.034176 | 0.06831 | 0.03064 | -0.076453 | 0.043328 | 0.1479 | 0.050718 | -0.092632 | 0.043656 | 0.064421 | -0.047222 | 0.005983 | -0.000328 | 0.09055 | 0.007062 | 0.09794
3044.5938 | 121.4859 | -121.1884 | 0.10986 | 0.062332 | -0.10004 | 0.006315 | -0.047909 | 0.049999 | 0.021485 | -0.085608 | 0.029595 | 0.13416 | 0.036985 | -0.10637 | 0.029923 | 0.055266 | -0.065533 | -0.016906 | 0.076065 | -0.086312 | 0.020048 | -0.034176 | 0.063732 | 0.035218 | -0.071875 | 0.043328 | 0.1479 | 0.050718 | -0.092632 | 0.043656 | 0.068999 | -0.0518 | -0.003173 | -0.000328 | 0.095128 | 0.007062 | 0.10252
3046.3438 | 121.4172 | -121.257 | 0.13733 | 0.057754 | -0.086309 | 0.010893 | -0.052488 | 0.054577 | 0.021485 | -0.090186 | 0.047909 | 0.13416 | 0.036985 | -0.10637 | 0.025345 | 0.050688 | -0.065533 | -0.00775 | 0.071487 | -0.072576 | 0.024626 | -0.038755 | 0.06831 | 0.035218 | -0.076453 | 0.061642 | 0.1479 | 0.050718 | -0.092632 | 0.039078 | 0.064421 | -0.0518 | 0.005983 | 0.022564 | 0.11344 | 0.01164 | 0.10252
3048.0938 | 121.4493 | -121.2524 | 0.10529 | 0.057754 | -0.095467 | 0.010893 | -0.047909 | 0.045421 | 0.016907 | -0.094765 | 0.029595 | 0.13874 | 0.036985 | -0.10179 | 0.025345 | 0.059844 | -0.060955 | -0.016906 | 0.071487 | -0.081734 | 0.024626 | -0.034176 | 0.059154 | 0.03064 | -0.081032 | 0.043328 | 0.15247 | 0.050718 | -0.088053 | 0.039078 | 0.073577 | -0.047222 | -0.003173 | 0.00425 | 0.09055 | 0.01164 | 0.09794
3049.8438 | 121.5591 | -121.2524 | 0.10529 | 0.057754 | -0.10004 | -0.002842 | -0.052488 | 0.045421 | 0.016907 | -0.090186 | 0.038752 | 0.12958 | 0.041563 | -0.10179 | 0.025345 | 0.064423 | -0.065533 | -0.00775 | 0.071487 | -0.086312 | 0.010891 | -0.038755 | 0.059154 | 0.03064 | -0.076453 | 0.052485 | 0.14332 | 0.055296 | -0.088053 | 0.039078 | 0.078156 | -0.0518 | 0.005983 | 0.013407 | 0.10428 | 0.016218 | 0.1071
3051.5156 | 121.5088 | -121.2799 | 0.12817 | 0.062332 | -0.095467 | 0.006315 | -0.052488 | 0.040843 | 0.012329 | -0.094765 | 0.029595 | 0.12501 | 0.036985 | -0.10637 | 0.034501 | 0.041532 | -0.060955 | -0.00775 | 0.076065 | -0.081734 | 0.020048 | -0.038755 | 0.054576 | 0.026062 | -0.081032 | 0.043328 | 0.13874 | 0.050718 | -0.092632 | 0.048234 | 0.055265 | -0.047222 | 0.005983 | -0.004906 | 0.09055 | 0.002484 | 0.09794
3053.2656 | 121.4813 | -121.3348 | 0.10986 | 0.057754 | -0.090888 | -0.002842 | -0.052488 | 0.045421 | 0.016907 | -0.085608 | 0.034174 | 0.13416 | 0.041563 | -0.10179 | 0.020767 | 0.055266 | -0.070112 | -0.012328 | 0.071487 | -0.077155 | 0.010891 | -0.038755 | 0.059154 | 0.03064 | -0.071875 | 0.047907 | 0.1479 | 0.055296 | -0.088053 | 0.0345 | 0.068999 | -0.056379 | 0.001405 | 0.013407 | 0.10429 | 0.020796 | 0.11167
3054.9688 | 121.6232 | -121.2753 | 0.082397 | 0.057754 | -0.095467 | 0.001736 | -0.061645 | 0.045421 | 0.012329 | -0.090186 | 0.034174 | 0.13874 | 0.036985 | -0.10179 | 0.020767 | 0.055266 | -0.065533 | -0.00775 | 0.071487 | -0.081734 | 0.015469 | -0.047912 | 0.059154 | 0.026062 | -0.076453 | 0.047907 | 0.15247 | 0.050718 | -0.088053 | 0.0345 | 0.068999 | -0.0518 | 0.005983 | 0.013407 | 0.099707 | 0.016218 | 0.10252
3056.7188 | 121.6232 | -121.3348 | 0.10529 | 0.057754 | -0.090888 | 0.001736 | -0.052488 | 0.045421 | 0.012329 | -0.094765 | 0.034174 | 0.12958 | 0.032407 | -0.10637 | 0.025345 | 0.055266 | -0.070112 | -0.012328 | 0.071487 | -0.077155 | 0.015469 | -0.038755 | 0.059154 | 0.026062 | -0.081032 | 0.047907 | 0.14332 | 0.04614 | -0.092632 | 0.039078 | 0.068999 | -0.056379 | 0.001405 | 0.008829 | 0.10429 | 0.007062 | 0.10252
3058.4688 | 121.6599 | -121.3165 | 0.10986 | 0.062332 | -0.10004 | 0.006315 | -0.052488 | 0.040843 | 0.012329 | -0.094765 | 0.038752 | 0.13874 | 0.032407 | -0.11094 | 0.029923 | 0.059844 | -0.060955 | -0.012328 | 0.076065 | -0.086312 | 0.020048 | -0.038755 | 0.054576 | 0.026062 | -0.081032 | 0.052485 | 0.15247 | 0.04614 | -0.097211 | 0.043656 | 0.073577 | -0.047222 | 0.001405 | 0.008829 | 0.099707 | 0.002484 | 0.093362
3060.1406 | 121.5317 | -121.376 | 0.12817 | 0.06691 | -0.10004 | 0.001736 | -0.052488 | 0.045421 | 0.012329 | -0.094765 | 0.034174 | 0.12958 | 0.036985 | -0.10179 | 0.020767 | 0.04611 | -0.065533 | -0.00775 | 0.080643 | -0.086312 | 0.015469 | -0.038755 | 0.059154 | 0.026062 | -0.081032 | 0.047907 | 0.14332 | 0.050718 | -0.088053 | 0.0345 | 0.059843 | -0.0518 | 0.005983 | 0.013407 | 0.099707 | 0.016218 | 0.10252
3061.8906 | 121.6187 | -121.3623 | 0.11902 | 0.062332 | -0.10004 | -0.007421 | -0.057066 | 0.045421 | 0.00775 | -0.094765 | 0.038752 | 0.13416 | 0.032407 | -0.10179 | 0.029923 | 0.059844 | -0.065533 | -0.016906 | 0.076065 | -0.086312 | 0.006312 | -0.043333 | 0.059154 | 0.021483 | -0.081032 | 0.052485 | 0.1479 | 0.04614 | -0.088053 | 0.043656 | 0.073577 | -0.0518 | -0.003173 | 0.008829 | 0.10428 | 0.002484 | 0.09794
3063.625 | 121.5317 | -121.3852 | 0.11902 | 0.071489 | -0.10004 | -0.002842 | -0.052488 | 0.045421 | 0.012329 | -0.085608 | 0.038752 | 0.13416 | 0.046142 | -0.10179 | 0.029923 | 0.050688 | -0.07469 | -0.012328 | 0.085222 | -0.086312 | 0.010891 | -0.038755 | 0.059154 | 0.026062 | -0.071875 | 0.052485 | 0.1479 | 0.059875 | -0.088053 | 0.043656 | 0.064421 | -0.060957 | 0.001405 | 0.008829 | 0.11344 | 0.016219 | 0.12083
3065.375 | 121.669 | -121.376 | 0.086975 | 0.057754 | -0.10004 | -0.002842 | -0.047909 | 0.040843 | 0.00775 | -0.094765 | 0.038752 | 0.13416 | 0.036985 | -0.097207 | 0.034501 | 0.055266 | -0.070112 | -0.012328 | 0.071487 | -0.086312 | 0.010891 | -0.034176 | 0.054576 | 0.021483 | -0.081032 | 0.052485 | 0.1479 | 0.050718 | -0.083474 | 0.048234 | 0.068999 | -0.056379 | 0.001405 | 0.004251 | 0.10886 | 0.002484 | 0.1071
3067.0625 | 121.5729 | -121.431 | 0.12817 | 0.057754 | -0.10004 | -0.007421 | -0.047909 | 0.036265 | 0.003172 | -0.094765 | 0.034174 | 0.13416 | 0.041563 | -0.10637 | 0.025345 | 0.055266 | -0.070112 | -0.012328 | 0.071487 | -0.086312 | 0.006312 | -0.034176 | 0.049998 | 0.016905 | -0.081032 | 0.047907 | 0.1479 | 0.055296 | -0.092632 | 0.039078 | 0.068999 | -0.056379 | 0.001405 | 0.008829 | 0.10429 | 0.016218 | 0.11167
3068.8281 | 121.7148 | -121.3852 | 0.082397 | 0.057754 | -0.10462 | 0.001736 | -0.061645 | 0.040843 | 0.003172 | -0.10392 | 0.038752 | 0.13874 | 0.032407 | -0.092628 | 0.025345 | 0.050688 | -0.065533 | -0.016906 | 0.071487 | -0.090891 | 0.015469 | -0.047912 | 0.054576 | 0.016905 | -0.090188 | 0.052485 | 0.15247 | 0.04614 | -0.078895 | 0.039078 | 0.064421 | -0.0518 | -0.003173 | 0.013407 | 0.10428 | 0.007062 | 0.09794
3070.5156 | 121.6324 | -121.4447 | 0.13275 | 0.053175 | -0.10004 | -0.007421 | -0.052488 | 0.040843 | 0.012329 | -0.10392 | 0.034174 | 0.13874 | 0.036985 | -0.10179 | 0.025345 | 0.055266 | -0.065533 | -0.00775 | 0.066908 | -0.086312 | 0.006312 | -0.038755 | 0.054576 | 0.026062 | -0.090188 | 0.047907 | 0.15247 | 0.050718 | -0.088053 | 0.039078 | 0.068999 | -0.0518 | 0.005983 | 0.008829 | 0.099707 | 0.01164 | 0.10252
3072.2656 | 121.6599 | -121.431 | 0.12817 | 0.053175 | -0.10462 | -0.007421 | -0.061645 | 0.040843 | 0.00775 | -0.094765 | 0.034174 | 0.12958 | 0.041563 | -0.097207 | 0.020767 | 0.055266 | -0.070112 | -0.012328 | 0.066908 | -0.090891 | 0.006312 | -0.047912 | 0.054576 | 0.021483 | -0.081032 | 0.047907 | 0.14332 | 0.055296 | -0.083474 | 0.0345 | 0.068999 | -0.056379 | 0.001405 | 0.013407 | 0.10429 | 0.020796 | 0.11167
3073.9688 | 121.6049 | -121.463 | 0.13275 | 0.057754 | -0.1092 | -0.007421 | -0.066223 | 0.031687 | 0.012329 | -0.099343 | 0.034174 | 0.13416 | 0.032407 | -0.10179 | 0.039079 | 0.050688 | -0.070112 | -0.016906 | 0.071487 | -0.09547 | 0.006312 | -0.05249 | 0.04542 | 0.026062 | -0.08561 | 0.047907 | 0.1479 | 0.04614 | -0.088053 | 0.052812 | 0.064421 | -0.056379 | -0.003173 | -0.004905 | 0.10429 | -0.006672 | 0.10252
3075.7188 | 121.637 | -121.4722 | 0.11902 | 0.057754 | -0.11378 | -0.012 | -0.066223 | 0.031687 | 0.00775 | -0.099343 | 0.034174 | 0.13416 | 0.036985 | -0.10179 | 0.025345 | 0.041532 | -0.070112 | -0.016906 | 0.071487 | -0.10005 | 0.001733 | -0.05249 | 0.04542 | 0.021483 | -0.08561 | 0.047907 | 0.1479 | 0.050718 | -0.088053 | 0.039078 | 0.055265 | -0.056379 | -0.003173 | 0.008829 | 0.10429 | 0.01164 | 0.1071
3077.4688 | 121.7651 | -121.4172 | 0.10071 | 0.053175 | -0.1092 | -0.012 | -0.066223 | 0.036265 | 0.003172 | -0.099343 | 0.038752 | 0.13416 | 0.041563 | -0.10179 | 0.020767 | 0.055266 | -0.070112 | -0.016906 | 0.066908 | -0.09547 | 0.001733 | -0.05249 | 0.049998 | 0.016905 | -0.08561 | 0.052485 | 0.1479 | 0.055296 | -0.088053 | 0.0345 | 0.068999 | -0.056379 | -0.003173 | 0.017985 | 0.10886 | 0.020796 | 0.11167
3079.1562 | 121.7102 | -121.4767 | 0.11444 | 0.048597 | -0.1092 | -0.007421 | -0.066223 | 0.040843 | 0.003172 | -0.10392 | 0.038752 | 0.13416 | 0.032407 | -0.097207 | 0.025345 | 0.050688 | -0.070112 | -0.012328 | 0.06233 | -0.09547 | 0.006312 | -0.05249 | 0.054576 | 0.016905 | -0.090188 | 0.052485 | 0.1479 | 0.04614 | -0.083474 | 0.039078 | 0.064421 | -0.056379 | 0.001405 | 0.013407 | 0.10886 | 0.007062 | 0.10252
3080.9062 | 121.6553 | -121.5042 | 0.11902 | 0.057754 | -0.1092 | -0.021157 | -0.061645 | 0.031687 | -0.001406 | -0.1085 | 0.029595 | 0.13874 | 0.036985 | -0.10179 | 0.020767 | 0.04611 | -0.065533 | -0.012328 | 0.071487 | -0.09547 | -0.007424 | -0.047912 | 0.04542 | 0.012327 | -0.094766 | 0.043328 | 0.15247 | 0.050718 | -0.088053 | 0.0345 | 0.059843 | -0.0518 | 0.001405 | 0.008828 | 0.095128 | 0.016218 | 0.10252
3082.5938 | 121.6873 | -121.4996 | 0.13733 | 0.048597 | -0.11378 | -0.012 | -0.066223 | 0.027109 | 0.003172 | -0.11308 | 0.043331 | 0.13416 | 0.041563 | -0.10179 | 0.016188 | 0.04611 | -0.060955 | -0.00775 | 0.06233 | -0.10005 | 0.001733 | -0.05249 | 0.040842 | 0.016905 | -0.099344 | 0.057064 | 0.1479 | 0.055296 | -0.088053 | 0.029921 | 0.059843 | -0.047222 | 0.005983 | 0.027143 | 0.10429 | 0.025375 | 0.10252
3084.3438 | 121.7972 | -121.4767 | 0.082397 | 0.048597 | -0.11836 | -0.007421 | -0.061645 | 0.031687 | -0.005985 | -0.1085 | 0.043331 | 0.13874 | 0.036985 | -0.097207 | 0.016188 | 0.041532 | -0.060955 | -0.00775 | 0.06233 | -0.10463 | 0.006312 | -0.047912 | 0.04542 | 0.007748 | -0.094766 | 0.057064 | 0.15247 | 0.050718 | -0.083474 | 0.029921 | 0.055265 | -0.047222 | 0.005983 | 0.027143 | 0.10429 | 0.020797 | 0.09794
3086.0156 | 121.669 | -121.5042 | 0.12817 | 0.048597 | -0.11836 | -0.012 | -0.07538 | 0.027109 | -0.005985 | -0.1085 | 0.038752 | 0.13416 | 0.036985 | -0.097207 | 0.025345 | 0.059844 | -0.070112 | -0.00775 | 0.06233 | -0.10463 | 0.001733 | -0.061647 | 0.040842 | 0.007748 | -0.094766 | 0.052485 | 0.1479 | 0.050718 | -0.083474 | 0.039078 | 0.073577 | -0.056379 | 0.005983 | 0.013407 | 0.10886 | 0.01164 | 0.1071
3087.7812 | 121.7789 | -121.4905 | 0.09613 | 0.048597 | -0.11836 | -0.016578 | -0.07538 | 0.040843 | -0.001406 | -0.1085 | 0.043331 | 0.13416 | 0.041563 | -0.11094 | 0.016188 | 0.032376 | -0.070112 | -0.012328 | 0.06233 | -0.10463 | -0.002845 | -0.061647 | 0.054576 | 0.012327 | -0.094766 | 0.057064 | 0.1479 | 0.055296 | -0.097211 | 0.029921 | 0.046109 | -0.056379 | 0.001405 | 0.027143 | 0.11344 | 0.025375 | 0.11167
3089.5312 | 121.701 | -121.5363 | 0.1236 | 0.053175 | -0.12294 | -0.012 | -0.066223 | 0.027109 | -0.001406 | -0.1085 | 0.034174 | 0.12958 | 0.036985 | -0.092628 | 0.016188 | 0.032376 | -0.070112 | -0.012328 | 0.066908 | -0.10921 | 0.001733 | -0.05249 | 0.040842 | 0.012327 | -0.094766 | 0.047907 | 0.14332 | 0.050718 | -0.078895 | 0.029921 | 0.046109 | -0.056379 | 0.001405 | 0.017986 | 0.10429 | 0.020797 | 0.1071
3091.2031 | 121.7926 | -121.5317 | 0.10529 | 0.044018 | -0.11836 | -0.021157 | -0.061645 | 0.031687 | -0.001406 | -0.11308 | 0.034174 | 0.13874 | 0.041563 | -0.11094 | 0.016188 | 0.036954 | -0.065533 | -0.016906 | 0.057751 | -0.10463 | -0.007424 | -0.047912 | 0.04542 | 0.012327 | -0.099344 | 0.047907 | 0.15247 | 0.055296 | -0.097211 | 0.029921 | 0.050687 | -0.0518 | -0.003173 | 0.017986 | 0.099707 | 0.025375 | 0.1071
3092.9531 | 121.7789 | -121.5591 | 0.11444 | 0.03944 | -0.12294 | -0.012 | -0.070802 | 0.022531 | -0.001406 | -0.1085 | 0.038752 | 0.12958 | 0.041563 | -0.10179 | 0.007032 | 0.041532 | -0.070112 | -0.012328 | 0.053173 | -0.10921 | 0.001733 | -0.057069 | 0.036264 | 0.012327 | -0.094766 | 0.052485 | 0.14332 | 0.055296 | -0.088053 | 0.020765 | 0.055265 | -0.056379 | 0.001405 | 0.03172 | 0.10886 | 0.034531 | 0.11167
3094.6406 | 121.8613 | -121.5134 | 0.10986 | 0.03944 | -0.12294 | -0.016578 | -0.066223 | 0.027109 | -0.005985 | -0.10392 | 0.038752 | 0.13416 | 0.036985 | -0.10179 | 0.020767 | 0.036954 | -0.07469 | -0.012328 | 0.053173 | -0.10921 | -0.002845 | -0.05249 | 0.040842 | 0.007748 | -0.090188 | 0.052485 | 0.1479 | 0.050718 | -0.088053 | 0.0345 | 0.050687 | -0.060957 | 0.001405 | 0.017985 | 0.11344 | 0.016218 | 0.11167
3096.375 | 121.7422 | -121.5546 | 0.12817 | 0.044018 | -0.11378 | -0.016578 | -0.07538 | 0.031687 | -0.010563 | -0.11765 | 0.034174 | 0.13874 | 0.041563 | -0.092628 | 0.016188 | 0.032376 | -0.060955 | -0.012328 | 0.057751 | -0.10005 | -0.002845 | -0.061647 | 0.04542 | 0.00317 | -0.10392 | 0.047907 | 0.15247 | 0.055296 | -0.078895 | 0.029921 | 0.046109 | -0.047222 | 0.001405 | 0.017986 | 0.095129 | 0.025375 | 0.10252
3098.0625 | 121.7285 | -121.5683 | 0.12817 | 0.034862 | -0.12294 | -0.030314 | -0.07538 | 0.027109 | -0.010563 | -0.11308 | 0.034174 | 0.13874 | 0.041563 | -0.10179 | 0.016188 | 0.036954 | -0.070112 | -0.00775 | 0.048595 | -0.10921 | -0.016581 | -0.061647 | 0.040842 | 0.00317 | -0.099344 | 0.047907 | 0.15247 | 0.055296 | -0.088053 | 0.029921 | 0.050687 | -0.056379 | 0.005983 | 0.017986 | 0.10429 | 0.025375 | 0.11167
3099.8281 | 121.7834 | -121.5866 | 0.11444 | 0.034862 | -0.11836 | -0.021157 | -0.070802 | 0.027109 | 0.003172 | -0.1085 | 0.038752 | 0.13874 | 0.036985 | -0.097207 | 0.025345 | 0.04611 | -0.07469 | -0.021484 | 0.048595 | -0.10463 | -0.007424 | -0.057069 | 0.040842 | 0.016905 | -0.094766 | 0.052485 | 0.15247 | 0.050718 | -0.083474 | 0.039078 | 0.059843 | -0.060957 | -0.007751 | 0.013407 | 0.11344 | 0.01164 | 0.11167
3101.5156 | 121.8018 | -121.5683 | 0.10529 | 0.03944 | -0.11836 | -0.016578 | -0.070802 | 0.027109 | -0.005985 | -0.12223 | 0.038752 | 0.13874 | 0.041563 | -0.10179 | 0.01161 | 0.041532 | -0.070112 | -0.012328 | 0.053173 | -0.10463 | -0.002845 | -0.057069 | 0.040842 | 0.007748 | -0.1085 | 0.052485 | 0.15247 | 0.055296 | -0.088053 | 0.025343 | 0.055265 | -0.056379 | 0.001405 | 0.027142 | 0.10886 | 0.029953 | 0.11167
3103.2656 | 121.8979 | -121.5775 | 0.073242 | 0.044018 | -0.12752 | -0.025735 | -0.070802 | 0.027109 | -0.010563 | -0.11765 | 0.043331 | 0.12958 | 0.032407 | -0.097207 | 0.020767 | 0.04611 | -0.065533 | -0.00775 | 0.057751 | -0.11378 | -0.012002 | -0.057069 | 0.040842 | 0.00317 | -0.10392 | 0.057064 | 0.14332 | 0.04614 | -0.083474 | 0.0345 | 0.059843 | -0.0518 | 0.005983 | 0.022564 | 0.10886 | 0.01164 | 0.09794
3104.9688 | 121.8201 | -121.6049 | 0.10529 | 0.030283 | -0.12294 | -0.025735 | -0.07538 | 0.013375 | -0.010563 | -0.1085 | 0.034174 | 0.12958 | 0.041563 | -0.10179 | 0.020767 | 0.04611 | -0.065533 | -0.003172 | 0.044016 | -0.10921 | -0.012002 | -0.061647 | 0.027108 | 0.00317 | -0.094766 | 0.047907 | 0.14332 | 0.055296 | -0.088053 | 0.0345 | 0.059843 | -0.0518 | 0.010561 | 0.013407 | 0.099707 | 0.020796 | 0.1071
3106.7031 | 121.8201 | -121.6278 | 0.11444 | 0.030283 | -0.11836 | -0.025735 | -0.07538 | 0.027109 | -0.005985 | -0.11765 | 0.034174 | 0.13416 | 0.046142 | -0.10179 | 0.029923 | 0.050688 | -0.065533 | -0.012328 | 0.044016 | -0.10463 | -0.012002 | -0.061647 | 0.040842 | 0.007748 | -0.10392 | 0.047907 | 0.1479 | 0.059875 | -0.088053 | 0.043656 | 0.064421 | -0.0518 | 0.001405 | 0.004251 | 0.099707 | 0.016219 | 0.11167
3108.4375 | 121.8796 | -121.6095 | 0.09613 | 0.021127 | -0.1321 | -0.030314 | -0.070802 | 0.017953 | -0.015142 | -0.12223 | 0.043331 | 0.12043 | 0.041563 | -0.097207 | 0.025345 | 0.055266 | -0.070112 | -0.012328 | 0.03486 | -0.11836 | -0.016581 | -0.057069 | 0.031686 | -0.001409 | -0.1085 | 0.057064 | 0.13416 | 0.055296 | -0.083474 | 0.039078 | 0.068999 | -0.056379 | 0.001405 | 0.017986 | 0.11344 | 0.016218 | 0.11167
3110.125 | 121.9208 | -121.5866 | 0.086975 | 0.034862 | -0.1321 | -0.021157 | -0.070802 | 0.022531 | -0.015142 | -0.11765 | 0.034174 | 0.12043 | 0.046142 | -0.10179 | 0.01161 | 0.04611 | -0.065533 | -0.012328 | 0.048595 | -0.11836 | -0.007424 | -0.057069 | 0.036264 | -0.001409 | -0.10392 | 0.047907 | 0.13416 | 0.059875 | -0.088053 | 0.025343 | 0.059843 | -0.0518 | 0.001405 | 0.022564 | 0.099707 | 0.034532 | 0.11167
3111.8594 | 121.8018 | -121.6461 | 0.10529 | 0.030283 | -0.12294 | -0.030314 | -0.07538 | 0.017953 | -0.005985 | -0.11765 | 0.038752 | 0.13874 | 0.036985 | -0.10179 | 0.020767 | 0.041532 | -0.065533 | -0.00775 | 0.044016 | -0.10921 | -0.016581 | -0.061647 | 0.031686 | 0.007748 | -0.10392 | 0.052485 | 0.15247 | 0.050718 | -0.088053 | 0.0345 | 0.055265 | -0.0518 | 0.005983 | 0.017985 | 0.10428 | 0.016218 | 0.10252
3113.5469 | 121.9208 | -121.582 | 0.07782 | 0.025705 | -0.12294 | -0.030314 | -0.079959 | 0.013375 | -0.015142 | -0.12223 | 0.034174 | 0.13416 | 0.041563 | -0.088049 | 0.016188 | 0.041532 | -0.060955 | -0.016906 | 0.039438 | -0.10921 | -0.016581 | -0.066226 | 0.027108 | -0.001409 | -0.1085 | 0.047907 | 0.1479 | 0.055296 | -0.074316 | 0.029921 | 0.055265 | -0.047222 | -0.003173 | 0.017986 | 0.095129 | 0.025375 | 0.10252
3115.2969 | 121.7972 | -121.6736 | 0.1236 | 0.021127 | -0.12752 | -0.025735 | -0.079959 | 0.008797 | -0.015142 | -0.12223 | 0.034174 | 0.13416 | 0.036985 | -0.097207 | 0.016188 | 0.050688 | -0.060955 | -0.016906 | 0.03486 | -0.11378 | -0.012002 | -0.066226 | 0.02253 | -0.001409 | -0.1085 | 0.047907 | 0.1479 | 0.050718 | -0.083474 | 0.029921 | 0.064421 | -0.047222 | -0.003173 | 0.017986 | 0.095129 | 0.020797 | 0.09794
3116.9844 | 121.9345 | -121.6003 | 0.10071 | 0.016548 | -0.1321 | -0.030314 | -0.079959 | 0.017953 | -0.005985 | -0.12223 | 0.034174 | 0.12958 | 0.032407 | -0.10179 | 0.020767 | 0.041532 | -0.070112 | -0.012328 | 0.030281 | -0.11836 | -0.016581 | -0.066226 | 0.031686 | 0.007748 | -0.1085 | 0.047907 | 0.14332 | 0.04614 | -0.088053 | 0.0345 | 0.055265 | -0.056379 | 0.001405 | 0.013407 | 0.10429 | 0.01164 | 0.10252
3118.75 | 121.9528 | -121.6049 | 0.09613 | 0.030283 | -0.12294 | -0.025735 | -0.079959 | 0.017953 | -0.015142 | -0.12223 | 0.038752 | 0.12501 | 0.036985 | -0.088049 | 0.020767 | 0.04611 | -0.065533 | -0.012328 | 0.044016 | -0.10921 | -0.012002 | -0.066226 | 0.031686 | -0.001409 | -0.1085 | 0.052485 | 0.13874 | 0.050718 | -0.074316 | 0.0345 | 0.059843 | -0.0518 | 0.001405 | 0.017985 | 0.10428 | 0.016218 | 0.10252
3120.5 | 121.9162 | -121.6461 | 0.091553 | 0.016548 | -0.1321 | -0.025735 | -0.07538 | 0.017953 | -0.015142 | -0.12681 | 0.043331 | 0.12958 | 0.036985 | -0.10637 | 0.025345 | 0.041532 | -0.070112 | -0.016906 | 0.030281 | -0.11836 | -0.012002 | -0.061647 | 0.031686 | -0.001409 | -0.11308 | 0.057064 | 0.14332 | 0.050718 | -0.092632 | 0.039078 | 0.055265 | -0.056379 | -0.003173 | 0.017986 | 0.11344 | 0.01164 | 0.1071
3122.25 | 121.8979 | -121.6782 | 0.10986 | 0.016548 | -0.12294 | -0.025735 | -0.070802 | 0.013375 | -0.015142 | -0.12681 | 0.038752 | 0.13416 | 0.046142 | -0.10179 | 0.01161 | 0.032376 | -0.056376 | -0.012328 | 0.030281 | -0.10921 | -0.012002 | -0.057069 | 0.027108 | -0.001409 | -0.11308 | 0.052485 | 0.1479 | 0.059875 | -0.088053 | 0.025343 | 0.046109 | -0.042643 | 0.001405 | 0.027142 | 0.095128 | 0.034532 | 0.10252
3123.9375 | 121.8201 | -121.7056 | 0.12817 | 0.021127 | -0.12752 | -0.034893 | -0.079959 | 0.017953 | -0.015142 | -0.12681 | 0.038752 | 0.13416 | 0.036985 | -0.10637 | 0.016188 | 0.041532 | -0.07469 | -0.016906 | 0.03486 | -0.11378 | -0.02116 | -0.066226 | 0.031686 | -0.001409 | -0.11308 | 0.052485 | 0.1479 | 0.050718 | -0.092632 | 0.029921 | 0.055265 | -0.060957 | -0.003173 | 0.022564 | 0.11344 | 0.020797 | 0.11167
3125.6719 | 121.9437 | -121.6644 | 0.10529 | 0.007391 | -0.12752 | -0.025735 | -0.084537 | 0.008797 | -0.015142 | -0.12681 | 0.043331 | 0.13874 | 0.041563 | -0.10179 | 0.01161 | 0.041532 | -0.065533 | -0.016906 | 0.021124 | -0.11378 | -0.012002 | -0.070804 | 0.02253 | -0.001409 | -0.11308 | 0.057064 | 0.15247 | 0.055296 | -0.088053 | 0.025343 | 0.055265 | -0.0518 | -0.003173 | 0.031721 | 0.10886 | 0.029953 | 0.1071
3127.3594 | 121.9254 | -121.6873 | 0.10071 | 0.01197 | -0.12752 | -0.030314 | -0.084537 | 0.013375 | -0.01972 | -0.12681 | 0.038752 | 0.12958 | 0.041563 | -0.10179 | 0.016188 | 0.041532 | -0.070112 | -0.012328 | 0.025703 | -0.11378 | -0.016581 | -0.070804 | 0.027108 | -0.005987 | -0.11308 | 0.052485 | 0.14332 | 0.055296 | -0.088053 | 0.029921 | 0.055265 | -0.056379 | 0.001405 | 0.022564 | 0.10886 | 0.025375 | 0.11167
3129.1094 | 121.994 | -121.6461 | 0.068665 | 0.002813 | -0.1321 | -0.025735 | -0.079959 | 0.013375 | -0.015142 | -0.11765 | 0.038752 | 0.13416 | 0.036985 | -0.097207 | 0.01161 | 0.041532 | -0.065533 | -0.016906 | 0.016546 | -0.11836 | -0.012002 | -0.066226 | 0.027108 | -0.001409 | -0.10392 | 0.052485 | 0.1479 | 0.050718 | -0.083474 | 0.025343 | 0.055265 | -0.0518 | -0.003173 | 0.027142 | 0.10428 | 0.025375 | 0.10252
3130.8438 | 121.9025 | -121.7148 | 0.11444 | 0.01197 | -0.1321 | -0.034893 | -0.079959 | 0.008797 | -0.015142 | -0.12681 | 0.029595 | 0.13874 | 0.032407 | -0.10637 | 0.025345 | 0.04611 | -0.070112 | -0.00775 | 0.025703 | -0.11836 | -0.02116 | -0.066226 | 0.02253 | -0.001409 | -0.11308 | 0.043328 | 0.15247 | 0.04614 | -0.092632 | 0.039078 | 0.059843 | -0.056379 | 0.005983 | 0.00425 | 0.099707 | 0.007062 | 0.10252
3132.5312 | 122.0078 | -121.6736 | 0.09613 | 0.002813 | -0.1321 | -0.025735 | -0.084537 | 0.008797 | -0.015142 | -0.12223 | 0.034174 | 0.13416 | 0.036985 | -0.10179 | 0.01161 | 0.036954 | -0.065533 | -0.012328 | 0.016546 | -0.11836 | -0.012002 | -0.070804 | 0.02253 | -0.001409 | -0.1085 | 0.047907 | 0.1479 | 0.050718 | -0.088053 | 0.025343 | 0.050687 | -0.0518 | 0.001405 | 0.022564 | 0.099707 | 0.025375 | 0.10252
3134.2812 | 121.9482 | -121.7056 | 0.11444 | 0.002813 | -0.12752 | -0.034893 | -0.079959 | 0.017953 | -0.015142 | -0.13139 | 0.038752 | 0.13874 | 0.041563 | -0.097207 | 0.016188 | 0.050688 | -0.07469 | -0.00775 | 0.016546 | -0.11378 | -0.02116 | -0.066226 | 0.031686 | -0.001409 | -0.11766 | 0.052485 | 0.15247 | 0.055296 | -0.083474 | 0.029921 | 0.064421 | -0.060957 | 0.005983 | 0.022564 | 0.11344 | 0.025375 | 0.11625
3136.0156 | 121.9299 | -121.7056 | 0.12817 | 0.002813 | -0.12752 | -0.030314 | -0.084537 | 0.013375 | -0.015142 | -0.12681 | 0.029595 | 0.13416 | 0.036985 | -0.097207 | 0.016188 | 0.036954 | -0.065533 | -0.012328 | 0.016546 | -0.11378 | -0.016581 | -0.070804 | 0.027108 | -0.001409 | -0.11308 | 0.043328 | 0.1479 | 0.050718 | -0.083474 | 0.029921 | 0.050687 | -0.0518 | 0.001405 | 0.013407 | 0.095128 | 0.020797 | 0.10252
3137.7812 | 121.9482 | -121.7056 | 0.10986 | -0.001765 | -0.12752 | -0.034893 | -0.07538 | 0.013375 | -0.015142 | -0.12681 | 0.043331 | 0.13874 | 0.036985 | -0.097207 | 0.01161 | 0.04611 | -0.070112 | -0.021484 | 0.011968 | -0.11378 | -0.02116 | -0.061647 | 0.027108 | -0.001409 | -0.11308 | 0.057064 | 0.15247 | 0.050718 | -0.083474 | 0.025343 | 0.059843 | -0.056379 | -0.007751 | 0.031721 | 0.11344 | 0.025375 | 0.1071
3139.4844 | 121.994 | -121.7056 | 0.10529 | 0.002813 | -0.12294 | -0.030314 | -0.084537 | 0.008797 | -0.01972 | -0.12681 | 0.038752 | 0.13874 | 0.041563 | -0.097207 | 0.020767 | 0.036954 | -0.065533 | -0.016906 | 0.016546 | -0.10921 | -0.016581 | -0.070804 | 0.02253 | -0.005987 | -0.11308 | 0.052485 | 0.15247 | 0.055296 | -0.083474 | 0.0345 | 0.050687 | -0.0518 | -0.003173 | 0.017985 | 0.10428 | 0.020796 | 0.1071
3141.1719 | 121.9116 | -121.7743 | 0.086975 | -0.001765 | -0.1321 | -0.030314 | -0.084537 | 0.013375 | -0.015142 | -0.12223 | 0.038752 | 0.13874 | 0.046142 | -0.10637 | 0.020767 | 0.04611 | -0.07469 | -0.012328 | 0.011968 | -0.11836 | -0.016581 | -0.070804 | 0.027108 | -0.001409 | -0.1085 | 0.052485 | 0.15247 | 0.059875 | -0.092632 | 0.0345 | 0.059843 | -0.060957 | 0.001405 | 0.017985 | 0.11344 | 0.025375 | 0.12083
3142.9062 | 122.0078 | -121.7239 | 0.091553 | -0.006344 | -0.12752 | -0.034893 | -0.07538 | 0.008797 | -0.01972 | -0.12681 | 0.038752 | 0.12958 | 0.041563 | -0.097207 | 0.016188 | 0.04611 | -0.070112 | -0.021484 | 0.007389 | -0.11378 | -0.02116 | -0.061647 | 0.02253 | -0.005987 | -0.11308 | 0.052485 | 0.14332 | 0.055296 | -0.083474 | 0.029921 | 0.059843 | -0.056379 | -0.007751 | 0.022564 | 0.10886 | 0.025375 | 0.11167
3144.5938 | 121.9986 | -121.7606 | 0.10529 | -0.006344 | -0.12294 | -0.039471 | -0.084537 | 0.008797 | -0.01972 | -0.13139 | 0.034174 | 0.13416 | 0.046142 | -0.088049 | 0.016188 | 0.036954 | -0.065533 | -0.00775 | 0.007389 | -0.10921 | -0.025738 | -0.070804 | 0.02253 | -0.005987 | -0.11766 | 0.047907 | 0.1479 | 0.059875 | -0.074316 | 0.029921 | 0.050687 | -0.0518 | 0.005983 | 0.017986 | 0.099707 | 0.029954 | 0.11167
3146.3438 | 121.9208 | -121.7697 | 0.11902 | 0.002813 | -0.11836 | -0.039471 | -0.079959 | 0.008797 | -0.015142 | -0.12681 | 0.034174 | 0.12958 | 0.036985 | -0.10179 | 0.020767 | 0.041532 | -0.065533 | -0.016906 | 0.016546 | -0.10463 | -0.025738 | -0.066226 | 0.02253 | -0.001409 | -0.11308 | 0.047907 | 0.14332 | 0.050718 | -0.088053 | 0.0345 | 0.055265 | -0.0518 | -0.003173 | 0.013407 | 0.099707 | 0.016218 | 0.10252
3148.0312 | 122.0352 | -121.7331 | 0.07782 | -0.001765 | -0.13668 | -0.034893 | -0.089116 | 0.008797 | -0.01972 | -0.12681 | 0.038752 | 0.13874 | 0.036985 | -0.11094 | 0.016188 | 0.036954 | -0.065533 | -0.00775 | 0.011968 | -0.12294 | -0.02116 | -0.075383 | 0.02253 | -0.005987 | -0.11308 | 0.052485 | 0.15247 | 0.050718 | -0.097211 | 0.029921 | 0.050687 | -0.0518 | 0.005983 | 0.022564 | 0.10428 | 0.020797 | 0.10252
3149.7969 | 121.9208 | -121.7789 | 0.11902 | -0.010922 | -0.13668 | -0.030314 | -0.084537 | 0.008797 | -0.015142 | -0.13139 | 0.034174 | 0.13874 | 0.036985 | -0.10179 | 0.01161 | 0.036954 | -0.070112 | -0.012328 | 0.002811 | -0.12294 | -0.016581 | -0.070804 | 0.02253 | -0.001409 | -0.11766 | 0.047907 | 0.15247 | 0.050718 | -0.088053 | 0.025343 | 0.050687 | -0.056379 | 0.001405 | 0.022564 | 0.10429 | 0.025375 | 0.1071
3151.4844 | 122.0123 | -121.7651 | 0.09613 | -0.001765 | -0.1321 | -0.034893 | -0.089116 | 0.004219 | -0.024298 | -0.13139 | 0.034174 | 0.13416 | 0.036985 | -0.10179 | 0.002454 | 0.041532 | -0.065533 | -0.012328 | 0.011968 | -0.11836 | -0.02116 | -0.075383 | 0.017952 | -0.010565 | -0.11766 | 0.047907 | 0.1479 | 0.050718 | -0.088053 | 0.016187 | 0.055265 | -0.0518 | 0.001405 | 0.03172 | 0.099707 | 0.034531 | 0.10252
3153.2344 | 121.9437 | -121.7789 | 0.11444 | -0.006344 | -0.12752 | -0.04405 | -0.079959 | 0.004219 | -0.024298 | -0.12681 | 0.029595 | 0.13416 | 0.046142 | -0.088049 | 0.020767 | 0.032376 | -0.07469 | -0.00775 | 0.007389 | -0.11378 | -0.030317 | -0.066226 | 0.017952 | -0.010565 | -0.11308 | 0.043328 | 0.1479 | 0.059875 | -0.074316 | 0.0345 | 0.046109 | -0.060957 | 0.005983 | 0.008828 | 0.10429 | 0.025375 | 0.12083
3154.9219 | 121.9528 | -121.7926 | 0.12817 | -0.001765 | -0.1321 | -0.039471 | -0.084537 | 0.013375 | -0.01972 | -0.13139 | 0.038752 | 0.13874 | 0.032407 | -0.10179 | 0.01161 | 0.036954 | -0.065533 | -0.012328 | 0.011968 | -0.11836 | -0.025738 | -0.070804 | 0.027108 | -0.005987 | -0.11766 | 0.052485 | 0.15247 | 0.04614 | -0.088053 | 0.025343 | 0.050687 | -0.0518 | 0.001405 | 0.027142 | 0.10428 | 0.020797 | 0.09794
3156.6719 | 122.0947 | -121.7422 | 0.082397 | -0.006344 | -0.12752 | -0.039471 | -0.084537 | 0.004219 | -0.028877 | -0.12681 | 0.043331 | 0.13874 | 0.036985 | -0.097207 | 0.01161 | 0.04611 | -0.065533 | -0.012328 | 0.007389 | -0.11378 | -0.025738 | -0.070804 | 0.017952 | -0.015144 | -0.11308 | 0.057064 | 0.15247 | 0.050718 | -0.083474 | 0.025343 | 0.059843 | -0.0518 | 0.001405 | 0.031721 | 0.10886 | 0.025375 | 0.10252
3158.3594 | 122.0673 | -121.7697 | 0.10529 | -0.006344 | -0.1321 | -0.04405 | -0.084537 | 0.013375 | -0.015142 | -0.13139 | 0.038752 | 0.13416 | 0.041563 | -0.092628 | 0.01161 | 0.032376 | -0.065533 | -0.016906 | 0.007389 | -0.11836 | -0.030317 | -0.070804 | 0.027108 | -0.001409 | -0.11766 | 0.052485 | 0.1479 | 0.055296 | -0.078895 | 0.025343 | 0.046109 | -0.0518 | -0.003173 | 0.027142 | 0.10428 | 0.029953 | 0.1071
3160.1094 | 121.9803 | -121.788 | 0.11902 | -0.006344 | -0.12752 | -0.04405 | -0.079959 | -0.000359 | -0.028877 | -0.12223 | 0.034174 | 0.13416 | 0.041563 | -0.10179 | 0.016188 | 0.041532 | -0.060955 | -0.012328 | 0.007389 | -0.11378 | -0.030317 | -0.066226 | 0.013374 | -0.015144 | -0.1085 | 0.047907 | 0.1479 | 0.055296 | -0.088053 | 0.029921 | 0.055265 | -0.047222 | 0.001405 | 0.017986 | 0.095129 | 0.025375 | 0.10252
3161.8594 | 122.1039 | -121.7697 | 0.086975 | -0.015501 | -0.14125 | -0.04405 | -0.084537 | 0.004219 | -0.024298 | -0.13139 | 0.043331 | 0.12958 | 0.036985 | -0.11094 | 0.016188 | 0.036954 | -0.065533 | -0.012328 | -0.001768 | -0.12752 | -0.030317 | -0.070804 | 0.017952 | -0.010565 | -0.11766 | 0.057064 | 0.14332 | 0.050718 | -0.097211 | 0.029921 | 0.050687 | -0.0518 | 0.001405 | 0.027143 | 0.10886 | 0.020797 | 0.10252
3163.5312 | 121.9574 | -121.8155 | 0.11444 | -0.015501 | -0.13668 | -0.04405 | -0.079959 | -0.000359 | -0.024298 | -0.13139 | 0.034174 | 0.13874 | 0.027829 | -0.10179 | 0.01161 | 0.032376 | -0.060955 | -0.00775 | -0.001768 | -0.12294 | -0.030317 | -0.066226 | 0.013374 | -0.010565 | -0.11766 | 0.047907 | 0.15247 | 0.041562 | -0.088053 | 0.025343 | 0.046109 | -0.047222 | 0.005983 | 0.022564 | 0.095129 | 0.016219 | 0.088784
3165.2656 | 122.0032 | -121.8521 | 0.11902 | -0.006344 | -0.12752 | -0.034893 | -0.089116 | 0.008797 | -0.024298 | -0.13139 | 0.038752 | 0.12958 | 0.032407 | -0.10179 | 0.016188 | 0.036954 | -0.070112 | -0.00775 | 0.007389 | -0.11378 | -0.02116 | -0.075383 | 0.02253 | -0.010565 | -0.11766 | 0.052485 | 0.14332 | 0.04614 | -0.088053 | 0.029921 | 0.050687 | -0.056379 | 0.005983 | 0.022564 | 0.10886 | 0.016219 | 0.10252
3166.9531 | 122.0673 | -121.8109 | 0.10071 | -0.015501 | -0.1321 | -0.048628 | -0.089116 | -0.000359 | -0.028877 | -0.13139 | 0.034174 | 0.12958 | 0.036985 | -0.10179 | 0.016188 | 0.041532 | -0.060955 | -0.016906 | -0.001768 | -0.11836 | -0.034895 | -0.075383 | 0.013374 | -0.015144 | -0.11766 | 0.047907 | 0.14332 | 0.050718 | -0.088053 | 0.029921 | 0.055265 | -0.047222 | -0.003173 | 0.017986 | 0.095129 | 0.020797 | 0.09794
3168.7031 | 122.1085 | -121.8018 | 0.091553 | -0.010922 | -0.14125 | -0.04405 | -0.089116 | 0.004219 | -0.024298 | -0.13597 | 0.043331 | 0.12958 | 0.041563 | -0.10179 | 0.007032 | 0.036954 | -0.065533 | -0.00775 | 0.002811 | -0.12752 | -0.030317 | -0.075383 | 0.017952 | -0.010565 | -0.12224 | 0.057064 | 0.14332 | 0.055296 | -0.088053 | 0.020765 | 0.050687 | -0.0518 | 0.005983 | 0.036299 | 0.10886 | 0.034531 | 0.1071
3170.4531 | 122.1085 | -121.7651 | 0.091553 | -0.006344 | -0.14125 | -0.04405 | -0.084537 | 0.004219 | -0.033455 | -0.13597 | 0.047909 | 0.13874 | 0.027829 | -0.097207 | 0.016188 | 0.032376 | -0.070112 | -0.012328 | 0.007389 | -0.12752 | -0.030317 | -0.070804 | 0.017952 | -0.019722 | -0.12224 | 0.061642 | 0.15247 | 0.041562 | -0.083474 | 0.029921 | 0.046109 | -0.056379 | 0.001405 | 0.031721 | 0.11802 | 0.011641 | 0.097941
3172.1875 | 122.1176 | -121.8109 | 0.086975 | -0.001765 | -0.13668 | -0.04405 | -0.093694 | -0.000359 | -0.024298 | -0.14055 | 0.038752 | 0.12958 | 0.041563 | -0.11094 | 0.016188 | 0.032376 | -0.065533 | -0.012328 | 0.011968 | -0.12294 | -0.030317 | -0.079961 | 0.013374 | -0.010565 | -0.12681 | 0.052485 | 0.14332 | 0.055296 | -0.097211 | 0.029921 | 0.046109 | -0.0518 | 0.001405 | 0.022564 | 0.10428 | 0.025375 | 0.1071
3173.875 | 122.0078 | -121.8658 | 0.12817 | -0.006344 | -0.13668 | -0.039471 | -0.089116 | -0.000359 | -0.024298 | -0.13139 | 0.034174 | 0.12958 | 0.041563 | -0.097207 | 0.01161 | 0.032376 | -0.065533 | -0.00775 | 0.007389 | -0.12294 | -0.025738 | -0.075383 | 0.013374 | -0.010565 | -0.11766 | 0.047907 | 0.14332 | 0.055296 | -0.083474 | 0.025343 | 0.046109 | -0.0518 | 0.005983 | 0.022564 | 0.099707 | 0.029953 | 0.1071
3175.6406 | 122.049 | -121.8567 | 0.11902 | -0.010922 | -0.1321 | -0.039471 | -0.093694 | -0.000359 | -0.024298 | -0.13597 | 0.038752 | 0.13416 | 0.036985 | -0.097207 | 0.016188 | 0.036954 | -0.07469 | -0.016906 | 0.002811 | -0.11836 | -0.025738 | -0.079961 | 0.013374 | -0.010565 | -0.12224 | 0.052485 | 0.1479 | 0.050718 | -0.083474 | 0.029921 | 0.050687 | -0.060957 | -0.003173 | 0.022564 | 0.11344 | 0.020797 | 0.11167
3177.3906 | 122.0123 | -121.8384 | 0.14191 | -0.010922 | -0.12752 | -0.048628 | -0.089116 | -0.000359 | -0.028877 | -0.13597 | 0.038752 | 0.13416 | 0.036985 | -0.10179 | 0.016188 | 0.036954 | -0.070112 | -0.00775 | 0.002811 | -0.11378 | -0.034895 | -0.075383 | 0.013374 | -0.015144 | -0.12224 | 0.052485 | 0.1479 | 0.050718 | -0.088053 | 0.029921 | 0.050687 | -0.056379 | 0.005983 | 0.022564 | 0.10886 | 0.020797 | 0.1071
3179.125 | 122.1451 | -121.8155 | 0.07782 | -0.006344 | -0.13668 | -0.048628 | -0.089116 | 0.004219 | -0.024298 | -0.13139 | 0.025017 | 0.13874 | 0.041563 | -0.10637 | 0.01161 | 0.036954 | -0.070112 | -0.00775 | 0.007389 | -0.12294 | -0.034895 | -0.075383 | 0.017952 | -0.010565 | -0.11766 | 0.03875 | 0.15247 | 0.055296 | -0.092632 | 0.025343 | 0.050687 | -0.056379 | 0.005983 | 0.013407 | 0.095129 | 0.029953 | 0.11167
3180.875 | 122.1313 | -121.7926 | 0.082397 | -0.001765 | -0.13668 | -0.04405 | -0.093694 | 0.004219 | -0.024298 | -0.12681 | 0.029595 | 0.12958 | 0.036985 | -0.097207 | 0.01161 | 0.036954 | -0.079268 | -0.016906 | 0.011968 | -0.12294 | -0.030317 | -0.079961 | 0.017952 | -0.010565 | -0.11308 | 0.043328 | 0.14332 | 0.050718 | -0.083474 | 0.025343 | 0.050687 | -0.065535 | -0.003173 | 0.017985 | 0.10886 | 0.025375 | 0.11625
3182.5625 | 122.168 | -121.8109 | 0.07782 | -0.006344 | -0.1321 | -0.039471 | -0.093694 | 0.004219 | -0.028877 | -0.13139 | 0.034174 | 0.12958 | 0.032407 | -0.10637 | 0.01161 | 0.036954 | -0.07469 | -0.016906 | 0.007389 | -0.11836 | -0.025738 | -0.079961 | 0.017952 | -0.015144 | -0.11766 | 0.047907 | 0.14332 | 0.04614 | -0.092632 | 0.025343 | 0.050687 | -0.060957 | -0.003173 | 0.022564 | 0.10886 | 0.020797 | 0.1071
3184.2969 | 122.0215 | -121.8796 | 0.13275 | -0.010922 | -0.14583 | -0.034893 | -0.093694 | -0.000359 | -0.024298 | -0.14055 | 0.034174 | 0.13874 | 0.046142 | -0.10179 | 0.01161 | 0.036954 | -0.070112 | -0.016906 | 0.002811 | -0.1321 | -0.02116 | -0.079961 | 0.013374 | -0.010565 | -0.12681 | 0.047907 | 0.15247 | 0.059875 | -0.088053 | 0.025343 | 0.050687 | -0.056379 | -0.003173 | 0.022564 | 0.10429 | 0.034532 | 0.11625
3185.9844 | 122.1542 | -121.8201 | 0.07782 | -0.010922 | -0.14583 | -0.04405 | -0.089116 | 0.004219 | -0.024298 | -0.13597 | 0.034174 | 0.14332 | 0.036985 | -0.10637 | 0.007032 | 0.04611 | -0.070112 | -0.016906 | 0.002811 | -0.1321 | -0.030317 | -0.075383 | 0.017952 | -0.010565 | -0.12224 | 0.047907 | 0.15705 | 0.050718 | -0.092632 | 0.020765 | 0.059843 | -0.056379 | -0.003173 | 0.027142 | 0.10429 | 0.029953 | 0.1071
3187.7344 | 122.0718 | -121.8704 | 0.10529 | -0.010922 | -0.1321 | -0.04405 | -0.089116 | 0.004219 | -0.024298 | -0.12681 | 0.029595 | 0.13874 | 0.032407 | -0.10637 | 0.01161 | 0.036954 | -0.070112 | -0.012328 | 0.002811 | -0.11836 | -0.030317 | -0.075383 | 0.017952 | -0.010565 | -0.11308 | 0.043328 | 0.15247 | 0.04614 | -0.092632 | 0.025343 | 0.050687 | -0.056379 | 0.001405 | 0.017985 | 0.099707 | 0.020797 | 0.10252
3189.4844 | 122.1268 | -121.8567 | 0.09613 | -0.010922 | -0.1321 | -0.04405 | -0.089116 | -0.000359 | -0.024298 | -0.13597 | 0.038752 | 0.13416 | 0.032407 | -0.10179 | 0.01161 | 0.041532 | -0.065533 | -0.00775 | 0.002811 | -0.11836 | -0.030317 | -0.075383 | 0.013374 | -0.010565 | -0.12224 | 0.052485 | 0.1479 | 0.04614 | -0.088053 | 0.025343 | 0.055265 | -0.0518 | 0.005983 | 0.027142 | 0.10428 | 0.020797 | 0.09794
3191.1719 | 122.1359 | -121.8704 | 0.10071 | -0.010922 | -0.1321 | -0.04405 | -0.093694 | -0.000359 | -0.028877 | -0.14055 | 0.034174 | 0.13874 | 0.041563 | -0.097207 | 0.01161 | 0.036954 | -0.065533 | -0.00775 | 0.002811 | -0.11836 | -0.030317 | -0.079961 | 0.013374 | -0.015144 | -0.12681 | 0.047907 | 0.15247 | 0.055296 | -0.083474 | 0.025343 | 0.050687 | -0.0518 | 0.005983 | 0.022564 | 0.099707 | 0.029953 | 0.1071
3192.9062 | 122.1497 | -121.8338 | 0.091553 | -0.010922 | -0.13668 | -0.04405 | -0.084537 | -0.009515 | -0.028877 | -0.13139 | 0.029595 | 0.13874 | 0.046142 | -0.10179 | 0.016188 | 0.04611 | -0.065533 | -0.012328 | 0.002811 | -0.12294 | -0.030317 | -0.070804 | 0.004218 | -0.015144 | -0.11766 | 0.043328 | 0.15247 | 0.059875 | -0.088053 | 0.029921 | 0.059843 | -0.0518 | 0.001405 | 0.013407 | 0.095128 | 0.029954 | 0.11167
3194.6562 | 122.0718 | -121.907 | 0.11444 | -0.001765 | -0.14583 | -0.04405 | -0.093694 | 0.008797 | -0.028877 | -0.14512 | 0.038752 | 0.13416 | 0.041563 | -0.10179 | 0.016188 | 0.032376 | -0.070112 | -0.012328 | 0.011968 | -0.1321 | -0.030317 | -0.079961 | 0.02253 | -0.015144 | -0.13139 | 0.052485 | 0.1479 | 0.055296 | -0.088053 | 0.029921 | 0.046109 | -0.056379 | 0.001405 | 0.022564 | 0.10886 | 0.025375 | 0.11167
3196.3438 | 122.0673 | -121.9162 | 0.11444 | -0.001765 | -0.13668 | -0.039471 | -0.093694 | 0.004219 | -0.01972 | -0.13139 | 0.038752 | 0.13416 | 0.041563 | -0.10637 | 0.01161 | 0.036954 | -0.070112 | -0.00775 | 0.011968 | -0.12294 | -0.025738 | -0.079961 | 0.017952 | -0.005987 | -0.11766 | 0.052485 | 0.1479 | 0.055296 | -0.092632 | 0.025343 | 0.050687 | -0.056379 | 0.005983 | 0.027142 | 0.10886 | 0.029953 | 0.11167
3198.0312 | 122.1085 | -121.9208 | 0.10529 | -0.010922 | -0.1321 | -0.039471 | -0.089116 | -0.000359 | -0.028877 | -0.14055 | 0.034174 | 0.13874 | 0.032407 | -0.10179 | 0.016188 | 0.032376 | -0.070112 | -0.016906 | 0.002811 | -0.11836 | -0.025738 | -0.075383 | 0.013374 | -0.015144 | -0.12681 | 0.047907 | 0.15247 | 0.04614 | -0.088053 | 0.029921 | 0.046109 | -0.056379 | -0.003173 | 0.017986 | 0.10429 | 0.016219 | 0.10252
3199.7812 | 122.1909 | -121.8658 | 0.10071 | -0.001765 | -0.14125 | -0.039471 | -0.089116 | -0.009515 | -0.033455 | -0.14055 | 0.034174 | 0.12958 | 0.036985 | -0.10179 | 0.01161 | 0.036954 | -0.070112 | -0.012328 | 0.011968 | -0.12752 | -0.025738 | -0.075383 | 0.004218 | -0.019722 | -0.12681 | 0.047907 | 0.14332 | 0.050718 | -0.088053 | 0.025343 | 0.050687 | -0.056379 | 0.001405 | 0.022564 | 0.10429 | 0.025375 | 0.1071
3201.5312 | 122.2046 | -121.8613 | 0.091553 | -0.015501 | -0.14125 | -0.04405 | -0.089116 | -0.000359 | -0.033455 | -0.14512 | 0.034174 | 0.13416 | 0.041563 | -0.10637 | 0.016188 | 0.036954 | -0.065533 | -0.003172 | -0.001768 | -0.12752 | -0.030317 | -0.075383 | 0.013374 | -0.019722 | -0.13139 | 0.047907 | 0.1479 | 0.055296 | -0.092632 | 0.029921 | 0.050687 | -0.0518 | 0.010561 | 0.017986 | 0.099707 | 0.025375 | 0.1071
3203.2656 | 122.113 | -121.9116 | 0.12817 | -0.010922 | -0.14125 | -0.039471 | -0.084537 | 0.004219 | -0.028877 | -0.13139 | 0.034174 | 0.14332 | 0.032407 | -0.10179 | 0.016188 | 0.032376 | -0.065533 | -0.012328 | 0.002811 | -0.12752 | -0.025738 | -0.070804 | 0.017952 | -0.015144 | -0.11766 | 0.047907 | 0.15705 | 0.04614 | -0.088053 | 0.029921 | 0.046109 | -0.0518 | 0.001405 | 0.017986 | 0.099707 | 0.016219 | 0.09794
3204.9688 | 122.2092 | -121.8567 | 0.10071 | -0.015501 | -0.1321 | -0.04405 | -0.093694 | -0.000359 | -0.033455 | -0.13597 | 0.034174 | 0.13416 | 0.036985 | -0.10179 | 0.01161 | 0.036954 | -0.070112 | -0.012328 | -0.001768 | -0.11836 | -0.030317 | -0.079961 | 0.013374 | -0.019722 | -0.12224 | 0.047907 | 0.1479 | 0.050718 | -0.088053 | 0.025343 | 0.050687 | -0.056379 | 0.001405 | 0.022564 | 0.10429 | 0.025375 | 0.1071
3206.7188 | 122.1725 | -121.8567 | 0.10071 | 0.002813 | -0.14125 | -0.048628 | -0.089116 | 0.004219 | -0.024298 | -0.13139 | 0.029595 | 0.13416 | 0.036985 | -0.10179 | 0.016188 | 0.036954 | -0.060955 | -0.021484 | 0.016546 | -0.12752 | -0.034895 | -0.075383 | 0.017952 | -0.010565 | -0.11766 | 0.043328 | 0.1479 | 0.050718 | -0.088053 | 0.029921 | 0.050687 | -0.047222 | -0.007751 | 0.013407 | 0.09055 | 0.020797 | 0.09794
3208.4062 | 122.1039 | -121.9299 | 0.1236 | 0.002813 | -0.1321 | -0.053207 | -0.089116 | 0.004219 | -0.028877 | -0.13139 | 0.034174 | 0.13416 | 0.041563 | -0.10179 | 0.01161 | 0.041532 | -0.060955 | -0.012328 | 0.016546 | -0.11836 | -0.039474 | -0.075383 | 0.017952 | -0.015144 | -0.11766 | 0.047907 | 0.1479 | 0.055296 | -0.088053 | 0.025343 | 0.055265 | -0.047222 | 0.001405 | 0.022564 | 0.095129 | 0.029953 | 0.10252
3210.1094 | 122.1497 | -121.9208 | 0.10986 | 0.002813 | -0.14125 | -0.053207 | -0.089116 | 0.008797 | -0.033455 | -0.13139 | 0.034174 | 0.12958 | 0.032407 | -0.10637 | 0.01161 | 0.036954 | -0.065533 | -0.016906 | 0.016546 | -0.12752 | -0.039474 | -0.075383 | 0.02253 | -0.019722 | -0.11766 | 0.047907 | 0.14332 | 0.04614 | -0.092632 | 0.025343 | 0.050687 | -0.0518 | -0.003173 | 0.022564 | 0.099707 | 0.020797 | 0.09794
3211.8594 | 122.1817 | -121.8979 | 0.086975 | -0.006344 | -0.14125 | -0.048628 | -0.098273 | 0.004219 | -0.024298 | -0.13597 | 0.029595 | 0.13874 | 0.036985 | -0.092628 | 0.020767 | 0.036954 | -0.07469 | -0.016906 | 0.007389 | -0.12752 | -0.034895 | -0.08454 | 0.017952 | -0.010565 | -0.12224 | 0.043328 | 0.15247 | 0.050718 | -0.078895 | 0.0345 | 0.050687 | -0.060957 | -0.003173 | 0.008828 | 0.10429 | 0.016218 | 0.11167
3213.6094 | 122.1405 | -121.9299 | 0.13733 | 0.002813 | -0.14125 | -0.048628 | -0.089116 | -0.000359 | -0.024298 | -0.13139 | 0.034174 | 0.13416 | 0.036985 | -0.10179 | 0.01161 | 0.027798 | -0.070112 | -0.012328 | 0.016546 | -0.12752 | -0.034895 | -0.075383 | 0.013374 | -0.010565 | -0.11766 | 0.047907 | 0.1479 | 0.050718 | -0.088053 | 0.025343 | 0.041531 | -0.056379 | 0.001405 | 0.022564 | 0.10429 | 0.025375 | 0.1071
3215.2969 | 122.2183 | -121.9162 | 0.091553 | -0.001765 | -0.13668 | -0.048628 | -0.093694 | 0.004219 | -0.028877 | -0.12681 | 0.038752 | 0.12958 | 0.041563 | -0.092628 | 0.01161 | 0.036954 | -0.060955 | -0.012328 | 0.011968 | -0.12294 | -0.034895 | -0.079961 | 0.017952 | -0.015144 | -0.11308 | 0.052485 | 0.14332 | 0.055296 | -0.078895 | 0.025343 | 0.050687 | -0.047222 | 0.001405 | 0.027142 | 0.099707 | 0.029953 | 0.10252
3216.9688 | 122.2549 | -121.9025 | 0.07782 | 0.007391 | -0.1321 | -0.062364 | -0.089116 | 0.008797 | -0.024298 | -0.12681 | 0.034174 | 0.13874 | 0.032407 | -0.10179 | 0.007032 | 0.032376 | -0.060955 | -0.012328 | 0.021124 | -0.11836 | -0.048631 | -0.075383 | 0.02253 | -0.010565 | -0.11308 | 0.047907 | 0.15247 | 0.04614 | -0.088053 | 0.020765 | 0.046109 | -0.047222 | 0.001405 | 0.027142 | 0.095129 | 0.025375 | 0.093362
3218.7188 | 122.1085 | -121.962 | 0.11902 | -0.001765 | -0.14125 | -0.039471 | -0.093694 | 0.004219 | -0.028877 | -0.13139 | 0.038752 | 0.13874 | 0.036985 | -0.11094 | 0.020767 | 0.041532 | -0.060955 | -0.016906 | 0.011968 | -0.12752 | -0.025738 | -0.079961 | 0.017952 | -0.015144 | -0.11766 | 0.052485 | 0.15247 | 0.050718 | -0.097211 | 0.0345 | 0.055265 | -0.047222 | -0.003173 | 0.017985 | 0.099707 | 0.016218 | 0.09794
3220.4062 | 122.2458 | -121.9391 | 0.09613 | -0.001765 | -0.14583 | -0.04405 | -0.098273 | -0.000359 | -0.01972 | -0.13597 | 0.043331 | 0.13416 | 0.036985 | -0.097207 | 0.020767 | 0.036954 | -0.07469 | -0.016906 | 0.011968 | -0.1321 | -0.030317 | -0.08454 | 0.013374 | -0.005987 | -0.12224 | 0.057064 | 0.1479 | 0.050718 | -0.083474 | 0.0345 | 0.050687 | -0.060957 | -0.003173 | 0.022564 | 0.11802 | 0.016218 | 0.11167
3222.1562 | 122.2458 | -121.907 | 0.091553 | 0.007391 | -0.14125 | -0.04405 | -0.084537 | -0.000359 | -0.028877 | -0.13139 | 0.038752 | 0.13416 | 0.041563 | -0.10179 | 0.007032 | 0.041532 | -0.065533 | -0.00775 | 0.021124 | -0.12752 | -0.030317 | -0.070804 | 0.013374 | -0.015144 | -0.11766 | 0.052485 | 0.1479 | 0.055296 | -0.088053 | 0.020765 | 0.055265 | -0.0518 | 0.005983 | 0.03172 | 0.10428 | 0.034531 | 0.1071
3223.8438 | 122.2046 | -121.9574 | 0.10529 | 0.002813 | -0.13668 | -0.04405 | -0.084537 | 0.004219 | -0.01972 | -0.14055 | 0.038752 | 0.13416 | 0.036985 | -0.10179 | 0.01161 | 0.036954 | -0.065533 | -0.00775 | 0.016546 | -0.12294 | -0.030317 | -0.070804 | 0.017952 | -0.005987 | -0.12681 | 0.052485 | 0.1479 | 0.050718 | -0.088053 | 0.025343 | 0.050687 | -0.0518 | 0.005983 | 0.027142 | 0.10428 | 0.025375 | 0.10252
3225.5938 | 122.2 | -121.9391 | 0.10529 | 0.002813 | -0.1321 | -0.04405 | -0.084537 | 0.004219 | -0.01972 | -0.12681 | 0.043331 | 0.13874 | 0.036985 | -0.097207 | 0.01161 | 0.036954 | -0.070112 | -0.012328 | 0.016546 | -0.11836 | -0.030317 | -0.070804 | 0.017952 | -0.005987 | -0.11308 | 0.057064 | 0.15247 | 0.050718 | -0.083474 | 0.025343 | 0.050687 | -0.056379 | 0.001405 | 0.031721 | 0.11344 | 0.025375 | 0.1071
3227.2656 | 122.1771 | -121.9666 | 0.11902 | 0.007391 | -0.13668 | -0.034893 | -0.084537 | 0.013375 | -0.010563 | -0.12681 | 0.043331 | 0.13874 | 0.041563 | -0.10637 | 0.01161 | 0.036954 | -0.056376 | -0.012328 | 0.021124 | -0.12294 | -0.02116 | -0.070804 | 0.027108 | 0.00317 | -0.11308 | 0.057064 | 0.15247 | 0.055296 | -0.092632 | 0.025343 | 0.050687 | -0.042643 | 0.001405 | 0.031721 | 0.099707 | 0.029953 | 0.097939
3229 | 122.2641 | -121.9299 | 0.091553 | 0.007391 | -0.13668 | -0.034893 | -0.089116 | 0.017953 | -0.01972 | -0.12681 | 0.025017 | 0.13416 | 0.036985 | -0.10179 | 0.007032 | 0.032376 | -0.060955 | -0.016906 | 0.021124 | -0.12294 | -0.02116 | -0.075383 | 0.031686 | -0.005987 | -0.11308 | 0.03875 | 0.1479 | 0.050718 | -0.088053 | 0.020765 | 0.046109 | -0.047222 | -0.003173 | 0.017985 | 0.085972 | 0.029953 | 0.09794
3230.7656 | 122.2321 | -121.9437 | 0.091553 | 0.01197 | -0.13668 | -0.039471 | -0.079959 | 0.017953 | -0.015142 | -0.13139 | 0.043331 | 0.14332 | 0.041563 | -0.11094 | 0.01161 | 0.032376 | -0.065533 | -0.00775 | 0.025703 | -0.12294 | -0.025738 | -0.066226 | 0.031686 | -0.001409 | -0.11766 | 0.057064 | 0.15705 | 0.055296 | -0.097211 | 0.025343 | 0.046109 | -0.0518 | 0.005983 | 0.031721 | 0.10886 | 0.029953 | 0.1071
3232.4531 | 122.1909 | -121.9574 | 0.1236 | 0.01197 | -0.12752 | -0.034893 | -0.084537 | 0.017953 | -0.015142 | -0.12681 | 0.034174 | 0.13416 | 0.041563 | -0.10179 | 0.01161 | 0.032376 | -0.070112 | -0.016906 | 0.025703 | -0.11378 | -0.02116 | -0.070804 | 0.031686 | -0.001409 | -0.11308 | 0.047907 | 0.1479 | 0.055296 | -0.088053 | 0.025343 | 0.046109 | -0.056379 | -0.003173 | 0.022564 | 0.10429 | 0.029953 | 0.11167
3234.2031 | 122.1497 | -121.9803 | 0.10986 | 0.021127 | -0.12294 | -0.025735 | -0.070802 | 0.013375 | -0.010563 | -0.12681 | 0.034174 | 0.13416 | 0.036985 | -0.10637 | 0.01161 | 0.032376 | -0.065533 | -0.00775 | 0.03486 | -0.10921 | -0.012002 | -0.057069 | 0.027108 | 0.00317 | -0.11308 | 0.047907 | 0.1479 | 0.050718 | -0.092632 | 0.025343 | 0.046109 | -0.0518 | 0.005983 | 0.022564 | 0.099707 | 0.025375 | 0.10252
3235.9531 | 122.2275 | -121.9574 | 0.11444 | 0.01197 | -0.12294 | -0.039471 | -0.079959 | 0.008797 | -0.015142 | -0.12681 | 0.034174 | 0.13874 | 0.041563 | -0.10179 | 0.016188 | 0.036954 | -0.065533 | -0.003172 | 0.025703 | -0.10921 | -0.025738 | -0.066226 | 0.02253 | -0.001409 | -0.11308 | 0.047907 | 0.15247 | 0.055296 | -0.088053 | 0.029921 | 0.050687 | -0.0518 | 0.010561 | 0.017986 | 0.099707 | 0.025375 | 0.1071
3237.7031 | 122.1725 | -122.0078 | 0.13275 | 0.025705 | -0.11836 | -0.025735 | -0.066223 | 0.022531 | -0.005985 | -0.12681 | 0.034174 | 0.13416 | 0.036985 | -0.10179 | 0.016188 | 0.032376 | -0.070112 | -0.012328 | 0.039438 | -0.10463 | -0.012002 | -0.05249 | 0.036264 | 0.007748 | -0.11308 | 0.047907 | 0.1479 | 0.050718 | -0.088053 | 0.029921 | 0.046109 | -0.056379 | 0.001405 | 0.017986 | 0.10429 | 0.020797 | 0.1071
3239.3906 | 122.2321 | -121.962 | 0.091553 | 0.025705 | -0.11836 | -0.030314 | -0.07538 | 0.017953 | -0.015142 | -0.11765 | 0.038752 | 0.13416 | 0.036985 | -0.11094 | 0.016188 | 0.032376 | -0.065533 | -0.003172 | 0.039438 | -0.10463 | -0.016581 | -0.061647 | 0.031686 | -0.001409 | -0.10392 | 0.052485 | 0.1479 | 0.050718 | -0.097211 | 0.029921 | 0.046109 | -0.0518 | 0.010561 | 0.022564 | 0.10428 | 0.020797 | 0.10252
3241.125 | 122.1542 | -122.0261 | 0.12817 | 0.021127 | -0.11836 | -0.030314 | -0.070802 | 0.013375 | -0.001406 | -0.12681 | 0.038752 | 0.13416 | 0.036985 | -0.092628 | 0.016188 | 0.036954 | -0.070112 | -0.016906 | 0.03486 | -0.10463 | -0.016581 | -0.057069 | 0.027108 | 0.012327 | -0.11308 | 0.052485 | 0.1479 | 0.050718 | -0.078895 | 0.029921 | 0.050687 | -0.056379 | -0.003173 | 0.022564 | 0.10886 | 0.020797 | 0.1071
3242.875 | 122.2275 | -121.994 | 0.11444 | 0.025705 | -0.12294 | -0.025735 | -0.079959 | 0.017953 | -0.001406 | -0.11308 | 0.034174 | 0.14332 | 0.041563 | -0.10179 | 0.020767 | 0.027798 | -0.070112 | -0.016906 | 0.039438 | -0.10921 | -0.012002 | -0.066226 | 0.031686 | 0.012327 | -0.099344 | 0.047907 | 0.15705 | 0.055296 | -0.088053 | 0.0345 | 0.041531 | -0.056379 | -0.003173 | 0.013407 | 0.10429 | 0.020796 | 0.11167
3244.5625 | 122.2183 | -122.0032 | 0.11444 | 0.021127 | -0.11836 | -0.021157 | -0.070802 | 0.013375 | -0.005985 | -0.11765 | 0.038752 | 0.14332 | 0.032407 | -0.10179 | 0.01161 | 0.027798 | -0.070112 | -0.00775 | 0.03486 | -0.10463 | -0.007424 | -0.057069 | 0.027108 | 0.007748 | -0.10392 | 0.052485 | 0.15705 | 0.04614 | -0.088053 | 0.025343 | 0.041531 | -0.056379 | 0.005983 | 0.027142 | 0.10886 | 0.020797 | 0.10252
3246.2969 | 122.2275 | -122.0078 | 0.11902 | 0.021127 | -0.11378 | -0.021157 | -0.070802 | 0.027109 | 0.003172 | -0.11308 | 0.038752 | 0.12958 | 0.041563 | -0.10179 | 0.01161 | 0.036954 | -0.070112 | -0.016906 | 0.03486 | -0.10005 | -0.007424 | -0.057069 | 0.040842 | 0.016905 | -0.099344 | 0.052485 | 0.14332 | 0.055296 | -0.088053 | 0.025343 | 0.050687 | -0.056379 | -0.003173 | 0.027142 | 0.10886 | 0.029953 | 0.11167
3248.0312 | 122.2549 | -122.0032 | 0.09613 | 0.025705 | -0.11378 | -0.025735 | -0.070802 | 0.036265 | 0.003172 | -0.11765 | 0.029595 | 0.13874 | 0.036985 | -0.10179 | 0.007032 | 0.027798 | -0.065533 | -0.00775 | 0.039438 | -0.10005 | -0.012002 | -0.057069 | 0.049998 | 0.016905 | -0.10392 | 0.043328 | 0.15247 | 0.050718 | -0.088053 | 0.020765 | 0.041531 | -0.0518 | 0.005983 | 0.022563 | 0.095128 | 0.029953 | 0.10252
3249.7188 | 122.2275 | -122.0261 | 0.11444 | 0.030283 | -0.11378 | -0.021157 | -0.066223 | 0.022531 | -0.001406 | -0.1085 | 0.034174 | 0.13416 | 0.046142 | -0.10179 | 0.002454 | 0.036954 | -0.065533 | -0.00775 | 0.044016 | -0.10005 | -0.007424 | -0.05249 | 0.036264 | 0.012327 | -0.094766 | 0.047907 | 0.1479 | 0.059875 | -0.088053 | 0.016187 | 0.050687 | -0.0518 | 0.005983 | 0.03172 | 0.099707 | 0.043688 | 0.11167
3251.4531 | 122.2961 | -121.9803 | 0.091553 | 0.030283 | -0.11378 | -0.016578 | -0.079959 | 0.027109 | 0.003172 | -0.11308 | 0.034174 | 0.13874 | 0.032407 | -0.10179 | 0.016188 | 0.032376 | -0.070112 | -0.021484 | 0.044016 | -0.10005 | -0.002845 | -0.066226 | 0.040842 | 0.016905 | -0.099344 | 0.047907 | 0.15247 | 0.04614 | -0.088053 | 0.029921 | 0.046109 | -0.056379 | -0.007751 | 0.017986 | 0.10429 | 0.016219 | 0.10252
3253.1875 | 122.3099 | -121.9803 | 0.086975 | 0.03944 | -0.11378 | -0.016578 | -0.079959 | 0.027109 | -0.001406 | -0.10392 | 0.038752 | 0.13416 | 0.032407 | -0.10637 | 0.002454 | 0.027798 | -0.070112 | -0.012328 | 0.053173 | -0.10005 | -0.002845 | -0.066226 | 0.040842 | 0.012327 | -0.090188 | 0.052485 | 0.1479 | 0.04614 | -0.092632 | 0.016187 | 0.041531 | -0.056379 | 0.001405 | 0.036298 | 0.10886 | 0.029953 | 0.10252
3254.875 | 122.2641 | -121.9757 | 0.10071 | 0.030283 | -0.10004 | -0.016578 | -0.07538 | 0.022531 | -0.001406 | -0.10392 | 0.034174 | 0.12958 | 0.036985 | -0.10637 | -0.002124 | 0.032376 | -0.065533 | -0.012328 | 0.044016 | -0.086312 | -0.002845 | -0.061647 | 0.036264 | 0.012327 | -0.090188 | 0.047907 | 0.14332 | 0.050718 | -0.092632 | 0.011609 | 0.046109 | -0.0518 | 0.001405 | 0.036298 | 0.099707 | 0.039109 | 0.10252
3256.625 | 122.2092 | -122.0306 | 0.12817 | 0.034862 | -0.10462 | -0.016578 | -0.066223 | 0.031687 | 0.012329 | -0.1085 | 0.038752 | 0.13416 | 0.036985 | -0.10179 | 0.007032 | 0.036954 | -0.070112 | -0.00775 | 0.048595 | -0.090891 | -0.002845 | -0.05249 | 0.04542 | 0.026062 | -0.094766 | 0.052485 | 0.1479 | 0.050718 | -0.088053 | 0.020765 | 0.050687 | -0.056379 | 0.005983 | 0.03172 | 0.10886 | 0.029953 | 0.1071
3258.375 | 122.2458 | -122.0032 | 0.10071 | 0.044018 | -0.10462 | -0.016578 | -0.070802 | 0.036265 | 0.00775 | -0.1085 | 0.029595 | 0.12958 | 0.046142 | -0.10179 | 0.007032 | 0.041532 | -0.065533 | -0.012328 | 0.057751 | -0.090891 | -0.002845 | -0.057069 | 0.049998 | 0.021483 | -0.094766 | 0.043328 | 0.14332 | 0.059875 | -0.088053 | 0.020765 | 0.055265 | -0.0518 | 0.001405 | 0.022563 | 0.095128 | 0.03911 | 0.11167
3260.1406 | 122.2046 | -122.0306 | 0.10986 | 0.034862 | -0.10462 | -0.016578 | -0.066223 | 0.031687 | 0.003172 | -0.10392 | 0.029595 | 0.13874 | 0.036985 | -0.10637 | 0.007032 | 0.032376 | -0.065533 | -0.016906 | 0.048595 | -0.090891 | -0.002845 | -0.05249 | 0.04542 | 0.016905 | -0.090188 | 0.043328 | 0.15247 | 0.050718 | -0.092632 | 0.020765 | 0.046109 | -0.0518 | -0.003173 | 0.022563 | 0.095128 | 0.029953 | 0.10252
3261.8906 | 122.2916 | -122.0261 | 0.10071 | 0.034862 | -0.095467 | -0.016578 | -0.066223 | 0.031687 | 0.012329 | -0.10392 | 0.038752 | 0.14332 | 0.041563 | -0.10637 | 0.01161 | 0.032376 | -0.060955 | -0.021484 | 0.048595 | -0.081734 | -0.002845 | -0.05249 | 0.04542 | 0.026062 | -0.090188 | 0.052485 | 0.15705 | 0.055296 | -0.092632 | 0.025343 | 0.046109 | -0.047222 | -0.007751 | 0.027142 | 0.099707 | 0.029953 | 0.10252
3263.5781 | 122.2321 | -122.0261 | 0.13733 | 0.044018 | -0.10462 | -0.012 | -0.061645 | 0.036265 | 0.012329 | -0.10392 | 0.034174 | 0.13874 | 0.041563 | -0.10637 | 0.016188 | 0.036954 | -0.065533 | -0.021484 | 0.057751 | -0.090891 | 0.001733 | -0.047912 | 0.049998 | 0.026062 | -0.090188 | 0.047907 | 0.15247 | 0.055296 | -0.092632 | 0.029921 | 0.050687 | -0.0518 | -0.007751 | 0.017986 | 0.099707 | 0.025375 | 0.1071
3265.3281 | 122.2412 | -122.049 | 0.11902 | 0.044018 | -0.10004 | -0.012 | -0.066223 | 0.031687 | 0.012329 | -0.099343 | 0.034174 | 0.13416 | 0.041563 | -0.10637 | 0.016188 | 0.036954 | -0.070112 | -0.016906 | 0.057751 | -0.086312 | 0.001733 | -0.05249 | 0.04542 | 0.026062 | -0.08561 | 0.047907 | 0.1479 | 0.055296 | -0.092632 | 0.029921 | 0.050687 | -0.056379 | -0.003173 | 0.017986 | 0.10429 | 0.025375 | 0.11167
3267.0156 | 122.3328 | -121.9986 | 0.09613 | 0.044018 | -0.095467 | -0.021157 | -0.066223 | 0.031687 | 0.016907 | -0.094765 | 0.034174 | 0.13416 | 0.036985 | -0.097207 | 0.007032 | 0.032376 | -0.070112 | -0.016906 | 0.057751 | -0.081734 | -0.007424 | -0.05249 | 0.04542 | 0.03064 | -0.081032 | 0.047907 | 0.1479 | 0.050718 | -0.083474 | 0.020765 | 0.046109 | -0.056379 | -0.003173 | 0.027142 | 0.10429 | 0.029953 | 0.1071
3268.75 | 122.2778 | -122.0398 | 0.10071 | 0.057754 | -0.095467 | -0.002842 | -0.061645 | 0.036265 | 0.016907 | -0.090186 | 0.038752 | 0.13874 | 0.036985 | -0.10637 | 0.01161 | 0.036954 | -0.065533 | -0.00775 | 0.071487 | -0.081734 | 0.010891 | -0.047912 | 0.049998 | 0.03064 | -0.076453 | 0.052485 | 0.15247 | 0.050718 | -0.092632 | 0.025343 | 0.050687 | -0.0518 | 0.005983 | 0.027142 | 0.10428 | 0.025375 | 0.10252
3270.5156 | 122.2046 | -122.0764 | 0.12817 | 0.048597 | -0.095467 | -0.007421 | -0.052488 | 0.040843 | 0.016907 | -0.094765 | 0.038752 | 0.13416 | 0.041563 | -0.10637 | 0.01161 | 0.027798 | -0.065533 | -0.012328 | 0.06233 | -0.081734 | 0.006312 | -0.038755 | 0.054576 | 0.03064 | -0.081032 | 0.052485 | 0.1479 | 0.055296 | -0.092632 | 0.025343 | 0.041531 | -0.0518 | 0.001405 | 0.027142 | 0.10428 | 0.029953 | 0.1071
3272.2656 | 122.3007 | -122.0398 | 0.09613 | 0.053175 | -0.095467 | 0.001736 | -0.047909 | 0.045421 | 0.012329 | -0.085608 | 0.043331 | 0.13874 | 0.036985 | -0.11094 | 0.01161 | 0.036954 | -0.070112 | -0.012328 | 0.066908 | -0.081734 | 0.015469 | -0.034176 | 0.059154 | 0.026062 | -0.071875 | 0.057064 | 0.15247 | 0.050718 | -0.097211 | 0.025343 | 0.050687 | -0.056379 | 0.001405 | 0.031721 | 0.11344 | 0.025375 | 0.1071
3273.9375 | 122.2321 | -122.0627 | 0.11444 | 0.053175 | -0.095467 | 0.010893 | -0.057066 | 0.031687 | 0.012329 | -0.090186 | 0.034174 | 0.13874 | 0.036985 | -0.097207 | 0.01161 | 0.036954 | -0.070112 | -0.00775 | 0.066908 | -0.081734 | 0.024626 | -0.043333 | 0.04542 | 0.026062 | -0.076453 | 0.047907 | 0.15247 | 0.050718 | -0.083474 | 0.025343 | 0.050687 | -0.056379 | 0.005983 | 0.022564 | 0.10429 | 0.025375 | 0.1071
3275.6719 | 122.3053 | -122.0398 | 0.07782 | 0.053175 | -0.095467 | -0.002842 | -0.047909 | 0.045421 | 0.012329 | -0.085608 | 0.029595 | 0.12958 | 0.036985 | -0.10179 | 0.01161 | 0.036954 | -0.07469 | -0.016906 | 0.066908 | -0.081734 | 0.010891 | -0.034176 | 0.059154 | 0.026062 | -0.071875 | 0.043328 | 0.14332 | 0.050718 | -0.088053 | 0.025343 | 0.050687 | -0.060957 | -0.003173 | 0.017985 | 0.10429 | 0.025375 | 0.11167
3277.375 | 122.3511 | -122.0215 | 0.091553 | 0.053175 | -0.090888 | -0.002842 | -0.052488 | 0.045421 | 0.012329 | -0.08103 | 0.029595 | 0.13874 | 0.036985 | -0.10179 | 0.002454 | 0.032376 | -0.060955 | -0.012328 | 0.066908 | -0.077155 | 0.010891 | -0.038755 | 0.059154 | 0.026062 | -0.067297 | 0.043328 | 0.15247 | 0.050718 | -0.088053 | 0.016187 | 0.046109 | -0.047222 | 0.001405 | 0.027141 | 0.09055 | 0.034531 | 0.09794
3279.0625 | 122.2366 | -122.081 | 0.11902 | 0.057754 | -0.095467 | 0.010893 | -0.047909 | 0.049999 | 0.016907 | -0.090186 | 0.034174 | 0.13416 | 0.041563 | -0.097207 | 0.01161 | 0.027798 | -0.060955 | -0.012328 | 0.071487 | -0.081734 | 0.024626 | -0.034176 | 0.063732 | 0.03064 | -0.076453 | 0.047907 | 0.1479 | 0.055296 | -0.083474 | 0.025343 | 0.041531 | -0.047222 | 0.001405 | 0.022564 | 0.095129 | 0.029953 | 0.10252
3280.8281 | 122.3831 | -122.0398 | 0.082397 | 0.062332 | -0.090888 | -0.002842 | -0.052488 | 0.045421 | 0.012329 | -0.085608 | 0.043331 | 0.12958 | 0.046142 | -0.10637 | 0.002454 | 0.027798 | -0.065533 | -0.016906 | 0.076065 | -0.077155 | 0.010891 | -0.038755 | 0.059154 | 0.026062 | -0.071875 | 0.057064 | 0.14332 | 0.059875 | -0.092632 | 0.016187 | 0.041531 | -0.0518 | -0.003173 | 0.040877 | 0.10886 | 0.043688 | 0.11167
3282.5938 | 122.319 | -122.0581 | 0.091553 | 0.062332 | -0.086309 | 0.010893 | -0.047909 | 0.045421 | 0.016907 | -0.090186 | 0.034174 | 0.13874 | 0.036985 | -0.10637 | 0.016188 | 0.036954 | -0.070112 | -0.012328 | 0.076065 | -0.072576 | 0.024626 | -0.034176 | 0.059154 | 0.03064 | -0.076453 | 0.047907 | 0.15247 | 0.050718 | -0.092632 | 0.029921 | 0.050687 | -0.056379 | 0.001405 | 0.017986 | 0.10429 | 0.020797 | 0.1071
3284.3438 | 122.287 | -122.081 | 0.11444 | 0.06691 | -0.090888 | 0.001736 | -0.038752 | 0.049999 | 0.030642 | -0.076452 | 0.038752 | 0.13874 | 0.041563 | -0.10179 | 0.002454 | 0.027798 | -0.070112 | -0.00775 | 0.080643 | -0.077155 | 0.015469 | -0.025019 | 0.063732 | 0.044375 | -0.062719 | 0.052485 | 0.15247 | 0.055296 | -0.088053 | 0.016187 | 0.041531 | -0.056379 | 0.005983 | 0.036298 | 0.10886 | 0.039109 | 0.11167
3286.0312 | 122.2549 | -122.0901 | 0.11902 | 0.062332 | -0.095467 | 0.006315 | -0.043331 | 0.054577 | 0.026064 | -0.090186 | 0.034174 | 0.13874 | 0.036985 | -0.10179 | 0.007032 | 0.027798 | -0.065533 | -0.00775 | 0.076065 | -0.081734 | 0.020048 | -0.029598 | 0.06831 | 0.039797 | -0.076453 | 0.047907 | 0.15247 | 0.050718 | -0.088053 | 0.020765 | 0.041531 | -0.0518 | 0.005983 | 0.027142 | 0.099707 | 0.029953 | 0.10252
3287.7969 | 122.2549 | -122.0947 | 0.13275 | 0.062332 | -0.095467 | 0.010893 | -0.047909 | 0.045421 | 0.016907 | -0.08103 | 0.038752 | 0.13874 | 0.036985 | -0.10179 | 0.007032 | 0.027798 | -0.065533 | -0.012328 | 0.076065 | -0.081734 | 0.024626 | -0.034176 | 0.059154 | 0.03064 | -0.067297 | 0.052485 | 0.15247 | 0.050718 | -0.088053 | 0.020765 | 0.041531 | -0.0518 | 0.001405 | 0.03172 | 0.10428 | 0.029953 | 0.10252
3289.4688 | 122.2549 | -122.0993 | 0.13733 | 0.062332 | -0.090888 | 0.010893 | -0.038752 | 0.049999 | 0.016907 | -0.076452 | 0.029595 | 0.13874 | 0.041563 | -0.10637 | 0.007032 | 0.032376 | -0.070112 | -0.012328 | 0.076065 | -0.077155 | 0.024626 | -0.025019 | 0.063732 | 0.03064 | -0.062719 | 0.043328 | 0.15247 | 0.055296 | -0.092632 | 0.020765 | 0.046109 | -0.056379 | 0.001405 | 0.022563 | 0.099707 | 0.034531 | 0.11167
3291.2188 | 122.2778 | -122.1039 | 0.09613 | 0.062332 | -0.090888 | 0.006315 | -0.047909 | 0.049999 | 0.026064 | -0.071874 | 0.034174 | 0.13874 | 0.041563 | -0.097207 | 0.01161 | 0.036954 | -0.065533 | -0.012328 | 0.076065 | -0.077155 | 0.020048 | -0.034176 | 0.063732 | 0.039797 | -0.058141 | 0.047907 | 0.15247 | 0.055296 | -0.083474 | 0.025343 | 0.050687 | -0.0518 | 0.001405 | 0.022564 | 0.099707 | 0.029953 | 0.1071
3292.9062 | 122.2641 | -122.1268 | 0.11444 | 0.062332 | -0.090888 | 0.006315 | -0.047909 | 0.049999 | 0.021485 | -0.076452 | 0.043331 | 0.14332 | 0.036985 | -0.097207 | 0.01161 | 0.027798 | -0.065533 | -0.012328 | 0.076065 | -0.077155 | 0.020048 | -0.034176 | 0.063732 | 0.035218 | -0.062719 | 0.057064 | 0.15705 | 0.050718 | -0.083474 | 0.025343 | 0.041531 | -0.0518 | 0.001405 | 0.031721 | 0.10886 | 0.025375 | 0.10252
3294.6562 | 122.4106 | -122.0673 | 0.068665 | 0.06691 | -0.090888 | 0.006315 | -0.047909 | 0.049999 | 0.021485 | -0.085608 | 0.034174 | 0.13874 | 0.041563 | -0.10637 | 0.01161 | 0.018642 | -0.070112 | -0.012328 | 0.080643 | -0.077155 | 0.020048 | -0.034176 | 0.063732 | 0.035218 | -0.071875 | 0.047907 | 0.15247 | 0.055296 | -0.092632 | 0.025343 | 0.032375 | -0.056379 | 0.001405 | 0.022564 | 0.10429 | 0.029953 | 0.11167
3296.3438 | 122.3923 | -122.0581 | 0.064087 | 0.06691 | -0.086309 | 0.006315 | -0.043331 | 0.049999 | 0.021485 | -0.076452 | 0.038752 | 0.12958 | 0.032407 | -0.10179 | 0.007032 | 0.036954 | -0.070112 | -0.012328 | 0.080643 | -0.072576 | 0.020048 | -0.029598 | 0.063732 | 0.035218 | -0.062719 | 0.052485 | 0.14332 | 0.04614 | -0.088053 | 0.020765 | 0.050687 | -0.056379 | 0.001405 | 0.03172 | 0.10886 | 0.025375 | 0.10252
3298.0938 | 122.2687 | -122.0993 | 0.1236 | 0.071489 | -0.086309 | 0.006315 | -0.038752 | 0.059155 | 0.021485 | -0.076452 | 0.034174 | 0.13416 | 0.041563 | -0.10637 | 0.016188 | 0.032376 | -0.060955 | -0.00775 | 0.085222 | -0.072576 | 0.020048 | -0.025019 | 0.072888 | 0.035218 | -0.062719 | 0.047907 | 0.1479 | 0.055296 | -0.092632 | 0.029921 | 0.046109 | -0.047222 | 0.005983 | 0.017986 | 0.095129 | 0.025375 | 0.10252
3299.8438 | 122.3602 | -122.0947 | 0.082397 | 0.06691 | -0.086309 | 0.010893 | -0.052488 | 0.059155 | 0.026064 | -0.071874 | 0.038752 | 0.13874 | 0.036985 | -0.10637 | 0.01161 | 0.032376 | -0.060955 | -0.012328 | 0.080643 | -0.072576 | 0.024626 | -0.038755 | 0.072888 | 0.039797 | -0.058141 | 0.052485 | 0.15247 | 0.050718 | -0.092632 | 0.025343 | 0.046109 | -0.047222 | 0.001405 | 0.027142 | 0.099707 | 0.025375 | 0.09794
3301.5312 | 122.4106 | -122.0627 | 0.091553 | 0.062332 | -0.086309 | 0.010893 | -0.043331 | 0.054577 | 0.026064 | -0.076452 | 0.043331 | 0.13874 | 0.041563 | -0.10179 | 0.01161 | 0.027798 | -0.065533 | -0.003172 | 0.076065 | -0.072576 | 0.024626 | -0.029598 | 0.06831 | 0.039797 | -0.062719 | 0.057064 | 0.15247 | 0.055296 | -0.088053 | 0.025343 | 0.041531 | -0.0518 | 0.010561 | 0.031721 | 0.10886 | 0.029953 | 0.1071

## Thermal Data
Fire Time | C Position - 3' | C Position - Middle | C Position - 7'
-0.6833 | 10.9222 | 10.7177 | 10.1373
0.3167 | 10.9176 | 10.7265 | 10.1477
1.3167 | 10.9202 | 10.7316 | 10.1579
2.3167 | 10.9156 | 10.74 | 10.1661
3.3167 | 10.9067 | 10.7445 | 10.1645
4.3167 | 10.9079 | 10.7705 | 10.1892
5.3167 | 10.918 | 10.7988 | 10.2208
6.3167 | 10.9342 | 10.9336 | 10.2515
7.3167 | 11.1599 | 11.2736 | 10.5027
8.3167 | 11.2505 | 11.4009 | 11.032
9.3167 | 11.5216 | 12.355 | 11.1866
10.3167 | 11.8808 | 13.5265 | 11.6462
11.3167 | 12.6253 | 15.0324 | 12.0206
12.3167 | 13.9396 | 16.6256 | 12.6332
13.3167 | 15.2356 | 17.9116 | 14.2911
14.3167 | 16.5346 | 19.8966 | 16.8731
15.3167 | 18.7665 | 23.3686 | 18.999
16.3167 | 20.9652 | 25.7677 | 21.5628
17.3167 | 23.5431 | 28.6198 | 23.492
18.3167 | 25.3789 | 31.3018 | 25.5306
19.3167 | 27.4782 | 35.8272 | 28.8618
20.3167 | 29.3733 | 38.8325 | 31.5459
21.3167 | 32.8078 | 41.4694 | 34.2896
22.3167 | 35.6043 | 43.6149 | 37.2355
23.3167 | 38.709 | 45.4054 | 38.9202
24.3167 | 42.2465 | 47.8748 | 42.5747
25.3167 | 45.3244 | 51.2831 | 45.6101
26.3167 | 47.6303 | 54.6903 | 48.1481
27.3167 | 49.5409 | 58.0233 | 50.9939
28.3167 | 52.2664 | 59.9894 | 53.1935
29.3167 | 53.9043 | 61.7314 | 56.0586
30.3167 | 56.865 | 64.5163 | 59.0267
31.3167 | 59.9413 | 67.039 | 62.033
32.3167 | 61.5474 | 70.0348 | 63.9831
33.3167 | 64.1074 | 73.4523 | 65.8911
34.3167 | 65.8836 | 74.8405 | 69.4747
35.3167 | 66.5691 | 77.2898 | 71.8204
36.3167 | 68.5584 | 79.406 | 73.5777
37.3167 | 70.9006 | 81.8051 | 75.5858
38.3167 | 71.8886 | 83.524 | 77.6461
39.3167 | 73.6763 | 84.6174 | 80.1008
40.3167 | 75.9452 | 86.3793 | 81.6609
41.3167 | 77.9316 | 88.0833 | 83.5041
42.3167 | 80.1775 | 89.6225 | 84.4918
43.3167 | 82.3986 | 91.4731 | 85.6379
44.3167 | 84.2666 | 92.3018 | 86.9313
45.3167 | 85.0719 | 93.6059 | 88.7338
46.3167 | 85.741 | 95.0318 | 90.7423
47.3167 | 86.6943 | 96.0617 | 91.8014
48.3167 | 87.6945 | 96.7954 | 92.9043
49.3167 | 88.046 | 97.7919 | 93.2948
50.3167 | 89.3909 | 98.7672 | 93.732
51.3167 | 89.871 | 99.6801 | 94.5142
52.3167 | 90.5577 | 100.676 | 95.0475
53.3167 | 91.6206 | 101.9077 | 95.8333
54.3167 | 92.2602 | 103.2997 | 96.4065
55.3167 | 93.3132 | 105.214 | 96.9294
56.3167 | 94.7829 | 105.6787 | 98.3682
57.3167 | 94.8042 | 106.279 | 99.1448
58.3167 | 96.5987 | 108.0555 | 100.4853
59.3167 | 98.7231 | 109.021 | 101.6316
60.3167 | 100.5441 | 109.9879 | 102.2462
61.3167 | 102.2858 | 111.6101 | 103.0067
62.3167 | 103.4837 | 112.9666 | 104.5936
63.3167 | 104.5991 | 114.0297 | 104.9127
64.3167 | 106.0062 | 115.1098 | 105.9248
65.3167 | 107.8103 | 116.7281 | 107.2829
66.3167 | 109.5958 | 118.7791 | 107.8775
67.3167 | 110.2253 | 119.8727 | 108.4762
68.3167 | 110.2079 | 120.5201 | 108.8463
69.3167 | 110.5855 | 120.9945 | 109.8433
70.3167 | 112.0173 | 121.6935 | 110.2474
71.3167 | 112.8019 | 123.4321 | 111.7009
72.3167 | 113.8541 | 123.8782 | 112.1023
73.3167 | 114.4685 | 124.7659 | 112.6343
74.3167 | 115.1281 | 125.2181 | 112.8824
75.3167 | 115.7423 | 125.3687 | 112.9562
76.3167 | 115.7698 | 125.5715 | 113.0377
77.3167 | 115.8843 | 126.7197 | 113.2024
78.3167 | 116.162 | 127.827 | 113.4665
79.3167 | 117.0684 | 127.9264 | 114.2364
80.3167 | 117.0111 | 129.0043 | 114.7393
81.3167 | 117.2007 | 130.0782 | 115.2456
82.3167 | 118.2254 | 130.6315 | 115.1362
83.3323 | 118.9959 | 131.6929 | 115.7472
84.3167 | 119.56 | 132.2525 | 115.5279
85.3167 | 120.0164 | 132.454 | 115.5807
86.3167 | 121.0437 | 132.4646 | 115.765
87.3167 | 121.5515 | 132.9253 | 116.0889
88.3167 | 121.467 | 133.6702 | 116.4516
89.3167 | 121.8913 | 133.6092 | 117.0914
90.3167 | 122.3879 | 134.0878 | 117.399
91.3167 | 122.9154 | 134.6181 | 117.9998
92.3167 | 123.574 | 134.8721 | 118.1318
93.3167 | 124.7135 | 135.6834 | 118.4067
94.3167 | 126.0898 | 136.3511 | 118.1357
95.3167 | 126.3153 | 136.4359 | 119.4019
96.3167 | 126.9416 | 136.9316 | 119.544
97.3167 | 127.0241 | 137.4836 | 120.3317
98.3167 | 127.2033 | 138.046 | 120.7394
99.3167 | 127.8921 | 138.2927 | 122.0288
100.3167 | 127.8846 | 138.5274 | 123.1497
101.3167 | 128.0632 | 138.8513 | 123.8464
102.3167 | 128.8561 | 139.2231 | 124.559
103.3167 | 128.9606 | 140.477 | 125.2745
104.3167 | 128.6675 | 140.4895 | 125.7314
105.3167 | 129.4359 | 140.6175 | 125.9714
106.3167 | 129.5176 | 140.1577 | 125.9802
107.3167 | 129.4067 | 139.8476 | 126.1578
108.3167 | 129.5441 | 139.9035 | 126.1419
109.3167 | 129.3749 | 139.5375 | 126.7603
110.3167 | 128.7595 | 139.3341 | 127.029
111.3167 | 128.309 | 139.6811 | 127.2254
112.3167 | 128.5462 | 139.2935 | 127.7736
113.3167 | 128.3567 | 139.3396 | 127.8625
114.3167 | 128.5027 | 139.2865 | 127.705
115.3167 | 128.046 | 139.6249 | 127.4935
116.3167 | 127.7978 | 139.499 | 128.1859
117.3167 | 127.898 | 139.2735 | 127.7458
118.3167 | 128.2436 | 139.5007 | 127.9781
119.3167 | 128.6064 | 139.3224 | 127.6578
120.3167 | 128.7816 | 139.3887 | 127.2387
121.3167 | 128.739 | 139.576 | 127.0971
122.3167 | 129.0874 | 139.703 | 127.172
123.3167 | 129.441 | 139.7287 | 127.5888
124.3167 | 129.1431 | 139.3194 | 127.4374
125.3167 | 128.8568 | 139.4975 | 127.4868
126.3167 | 129.292 | 139.3928 | 127.2133
127.3167 | 129.3812 | 138.8692 | 127.2387
128.3167 | 129.2141 | 138.2821 | 127.0028
129.3167 | 128.8541 | 137.8213 | 126.8637
130.3167 | 128.8155 | 137.6212 | 126.6863
131.3167 | 128.5186 | 137.7104 | 126.2965
132.3167 | 127.9878 | 137.1356 | 126.5833
133.3167 | 127.6838 | 136.8209 | 126.3721
134.3167 | 127.603 | 136.6697 | 126.3107
135.3167 | 127.3377 | 136.3721 | 126.0592
136.3167 | 127.7257 | 136.9789 | 126.3819
137.3167 | 127.7268 | 137.2784 | 126.8013
138.3167 | 128.9148 | 137.6566 | 127.6691
139.3167 | 129.6289 | 138.1661 | 128.0458
140.3167 | 130.0813 | 138.7798 | 128.0429
141.3167 | 130.4344 | 139.7174 | 128.1231
142.3167 | 130.7626 | 140.5025 | 128.8115
143.3167 | 130.7067 | 141.2324 | 128.566
144.3167 | 131.2437 | 141.5098 | 129.0281
145.3167 | 131.2992 | 141.528 | 129.0687
146.3167 | 131.6909 | 142.0348 | 129.2171
147.3167 | 131.3128 | 142.1728 | 129.6056
148.3167 | 131.3655 | 142.244 | 130.1631
149.3167 | 131.7933 | 143.1508 | 130.7892
150.3167 | 132.0566 | 143.0061 | 130.9614
151.3167 | 132.7376 | 143.377 | 131.0744
152.3167 | 133.2142 | 143.391 | 130.8595
153.3167 | 134.1018 | 143.676 | 131.1492
154.3167 | 134.139 | 143.9543 | 131.0776
155.3167 | 134.716 | 144.1819 | 131.0716
156.3167 | 134.7168 | 145.0021 | 131.5874
157.3167 | 134.9295 | 145.6305 | 132.3168
158.3167 | 135.482 | 145.9675 | 132.8012
159.3167 | 135.5549 | 145.9968 | 133.0622
160.3167 | 136.1413 | 146.4135 | 133.3547
161.3167 | 136.1821 | 146.0574 | 133.4647
162.3167 | 136.4904 | 145.7213 | 133.6145
163.3167 | 137.5137 | 145.6248 | 133.3673
164.3167 | 137.1493 | 145.4513 | 132.9405
165.3167 | 137.416 | 145.7478 | 132.9154
166.3167 | 137.7551 | 146.6549 | 133.1226
167.3167 | 137.9628 | 147.4072 | 133.9441
168.3167 | 137.5073 | 148.1109 | 134.3925
169.3167 | 137.9372 | 148.5192 | 134.9194
170.3167 | 138.2243 | 148.5936 | 135.0855
171.3167 | 137.8162 | 149.4804 | 135.4096
172.3167 | 137.4142 | 149.2568 | 135.2007
173.3167 | 136.9987 | 149.365 | 136.0934
174.3167 | 136.6797 | 150.0184 | 136.3802
175.3167 | 137.0567 | 150.0013 | 136.6198
176.3167 | 137.6475 | 149.9845 | 137.0364
177.3167 | 138.2475 | 150.0883 | 137.2197
178.3167 | 138.2905 | 149.5863 | 136.7527
179.3167 | 137.8071 | 149.3839 | 136.2929
180.3167 | 137.5918 | 149.1306 | 135.8043
181.3167 | 137.2123 | 149.4517 | 135.3806
182.3167 | 137.9959 | 149.7071 | 134.8136
183.3167 | 138.6729 | 149.7746 | 134.6923
184.3167 | 140.093 | 150.0924 | 134.2939
185.3167 | 140.588 | 149.9815 | 134.2706
186.3167 | 141.2749 | 150.4264 | 134.8048
187.3167 | 142.1362 | 150.2663 | 135.3227
188.3167 | 143.1591 | 150.1912 | 135.6654
189.3167 | 143.7562 | 150.6819 | 135.7423
190.3167 | 143.8099 | 151.2017 | 135.6957
191.3167 | 143.1623 | 151.4293 | 135.3226
192.3167 | 143.0707 | 151.823 | 135.459
193.3167 | 143.8641 | 152.1488 | 136.5777
194.3167 | 144.3758 | 152.3662 | 136.4534
195.3167 | 145.9671 | 153.3735 | 136.8219
196.3167 | 146.4097 | 154.1358 | 138.4829
197.3167 | 147.557 | 154.667 | 139.4655
198.3167 | 148.7681 | 155.7306 | 139.5065
199.3167 | 148.3984 | 156.1865 | 139.9403
200.3167 | 148.7319 | 157.1885 | 140.5011
201.3167 | 149.4418 | 157.7781 | 141.3581
202.3167 | 149.8865 | 158.5945 | 142.1861
203.3167 | 150.6729 | 158.677 | 142.7051
204.3167 | 151.147 | 158.7165 | 142.9561
205.3167 | 151.4608 | 158.8993 | 143.355
206.3167 | 151.4953 | 158.6923 | 143.3302
207.3167 | 152.6442 | 158.6819 | 143.4887
208.3167 | 152.7465 | 158.807 | 144.1899
209.3167 | 152.1703 | 158.8834 | 144.3708
210.3167 | 151.5869 | 158.8321 | 144.4228
211.3167 | 151.7822 | 159.3629 | 145.8565
212.3167 | 151.3811 | 159.48 | 145.4254
213.3167 | 151.0236 | 159.2815 | 145.711
214.3167 | 151.0565 | 159.0671 | 145.8311
215.3167 | 151.1743 | 159.3 | 146.1793
216.3167 | 151.5826 | 159.7441 | 145.845
217.3167 | 152.1304 | 159.5964 | 145.7606
218.3167 | 152.6567 | 159.8149 | 145.9597
219.3167 | 153.5625 | 160.1417 | 146.1407
220.3167 | 154.4446 | 160.1892 | 146.1728
221.3167 | 155.6314 | 160.4554 | 146.0138
222.3167 | 155.6705 | 160.9523 | 146.7901
223.3167 | 155.9743 | 161.3555 | 147.1122
224.3167 | 156.7129 | 162.4108 | 147.2814
225.3167 | 157.0733 | 163.0846 | 147.4905
226.3167 | 157.9553 | 163.9349 | 148.5042
227.3167 | 157.8872 | 164.1808 | 149.1198
228.3167 | 157.7596 | 165.45 | 149.2065
229.3167 | 157.9921 | 166.691 | 149.8735
230.3167 | 159.3302 | 166.7776 | 150.7767
231.3167 | 159.9741 | 167.127 | 150.7094
232.3167 | 159.7136 | 168.3237 | 151.9734
233.3167 | 159.712 | 168.3915 | 152.2011
234.3167 | 160.5276 | 169.658 | 153.0441
235.3167 | 160.2515 | 170.8763 | 153.713
236.3167 | 161.0274 | 171.7683 | 154.6146
237.3167 | 161.4193 | 172.0955 | 155.4079
238.3167 | 163.1707 | 172.7821 | 155.6582
239.3167 | 163.7901 | 173.2205 | 156.1151
240.3167 | 163.4829 | 173.3328 | 156.4868
241.3167 | 163.7771 | 173.6959 | 156.7609
242.3167 | 164.4513 | 175.5044 | 157.3421
243.3167 | 163.9433 | 176.1449 | 158.2096
244.3167 | 164.4796 | 176.8155 | 158.0329
245.3167 | 165.2461 | 177.3 | 158.4398
246.3167 | 165.9106 | 177.65 | 158.5246
247.3167 | 166.5202 | 177.3532 | 158.4671
248.3167 | 166.513 | 177.2517 | 158.9651
249.3167 | 167.6341 | 177.1349 | 159.1399
250.3167 | 166.7127 | 176.6998 | 159.4384
251.3167 | 166.6225 | 177.055 | 159.6809
252.3167 | 166.347 | 177.4865 | 160.8231
253.3167 | 166.1197 | 178.4214 | 161.1836
254.3167 | 166.2919 | 178.9181 | 161.2433
255.3167 | 166.5579 | 179.665 | 162.3093
256.3167 | 166.2502 | 179.7371 | 162.7749
257.3167 | 166.8769 | 180.1095 | 162.9982
258.3167 | 166.2269 | 180.0321 | 162.9524
259.3167 | 166.2237 | 179.7843 | 163.2053
260.3167 | 165.8448 | 179.7104 | 163.305
261.3167 | 165.5418 | 180.1273 | 163.2888
262.3167 | 165.6536 | 180.5023 | 163.8581
263.3167 | 165.8031 | 180.265 | 164.9646
264.3167 | 166.2886 | 180.1626 | 165.7231
265.3167 | 166.7142 | 180.3245 | 165.7454
266.3167 | 166.8553 | 180.3024 | 165.6283
267.3167 | 166.2421 | 180.4008 | 166.1471
268.3167 | 166.0405 | 180.1618 | 166.0306
269.3167 | 165.4286 | 180.1451 | 166.0968
270.3167 | 166.2511 | 180.6238 | 167.1489
271.3167 | 166.9642 | 180.4385 | 167.1405
272.3167 | 166.61 | 180.918 | 167.7058
273.3167 | 166.676 | 181.2688 | 167.7958
274.3167 | 166.4289 | 181.7504 | 168.5644
275.3167 | 166.3966 | 182.6913 | 168.6777
276.3167 | 166.5955 | 183.2723 | 168.8038
277.3167 | 167.5808 | 183.2996 | 168.7731
278.3167 | 167.9828 | 183.2482 | 169.5041
279.3167 | 168.5895 | 183.6773 | 169.943
280.3167 | 168.6932 | 183.6778 | 169.5722
281.3167 | 168.9702 | 184.8624 | 169.2625
282.3167 | 169.5306 | 184.5807 | 169.5041
283.3167 | 169.4344 | 184.1563 | 169.391
284.3167 | 168.4987 | 183.9085 | 169.0803
285.3167 | 168.035 | 183.8587 | 169.4617
286.3167 | 168.6209 | 183.9901 | 170.0053
287.3167 | 169.2289 | 184.8431 | 169.9207
288.3167 | 170.0183 | 185.0972 | 169.5915
289.3167 | 170.3331 | 185.8561 | 170.4642
290.3167 | 170.8945 | 186.298 | 170.7671
291.3167 | 171.9908 | 186.9122 | 170.6489
292.3167 | 172.6703 | 186.7819 | 170.3641
293.3167 | 173.2356 | 187.8556 | 172.0312
294.3167 | 172.7406 | 187.6908 | 172.0293
295.3167 | 172.494 | 187.4837 | 172.1721
296.3167 | 173.4057 | 187.7923 | 173.064
297.3167 | 174.5348 | 187.9814 | 172.957
298.3167 | 174.906 | 188.0118 | 173.3279
299.3167 | 174.8215 | 188.0708 | 173.0468
300.3167 | 175.2442 | 188.6258 | 173.4861
301.3167 | 175.0895 | 188.3233 | 173.7147
302.3167 | 175.8262 | 188.5829 | 173.9569
303.3167 | 176.2093 | 188.1901 | 173.8146
304.3167 | 176.6421 | 187.9595 | 173.8871
305.3167 | 176.4129 | 187.6954 | 173.7789
306.3167 | 176.5264 | 187.9638 | 173.9297
307.3167 | 176.144 | 188.2795 | 173.8307
308.3167 | 176.3986 | 188.0696 | 174.096
309.3167 | 176.4561 | 188.5427 | 174.254
310.3167 | 176.5038 | 188.3789 | 173.9617
311.3167 | 175.9126 | 188.5404 | 174.3435
312.3167 | 175.1343 | 188.3508 | 174.1843
313.3167 | 174.3155 | 188.2761 | 173.7083
314.3167 | 175.1148 | 188.2771 | 173.4556
315.3167 | 174.7332 | 188.5937 | 173.2301
316.3167 | 174.5348 | 188.5921 | 173.0156
317.3167 | 175.4272 | 189.2479 | 173.2165
318.3167 | 175.3647 | 189.8438 | 173.7687
319.3167 | 175.9298 | 190.1355 | 174.0866
320.3167 | 176.6186 | 190.3714 | 174.2881
321.3167 | 177.5966 | 190.7125 | 174.4907
322.3167 | 178.6671 | 190.654 | 174.4698
323.3167 | 178.4934 | 190.4417 | 175.2056
324.3167 | 178.039 | 190.5968 | 175.4356
325.3167 | 177.5157 | 191.3547 | 175.6914
326.3167 | 177.5004 | 191.5778 | 176.6774
327.3167 | 178.1747 | 191.9058 | 176.7338
328.3167 | 179.0052 | 191.6677 | 177.5584
329.3167 | 178.9737 | 191.7298 | 178.4376
330.3167 | 179.0826 | 192.1128 | 179.3378
331.3167 | 179.2282 | 192.1379 | 178.8566
332.3167 | 177.9859 | 192.0253 | 178.1845
333.3167 | 177.4476 | 191.8699 | 178.1823
334.3167 | 177.584 | 192.2621 | 177.945
335.3167 | 177.9341 | 191.7523 | 177.6954
336.3167 | 177.7498 | 191.9365 | 177.6839
337.3167 | 177.8613 | 191.8528 | 177.5249
338.3167 | 177.6005 | 192.1783 | 178.0872
339.3167 | 177.4464 | 191.9207 | 178.1697
340.3167 | 177.942 | 192.4155 | 178.337
341.3167 | 178.8344 | 192.6266 | 178.769
342.3167 | 178.8314 | 192.9463 | 179.1507
343.3167 | 178.9383 | 192.8021 | 178.6724
344.3167 | 180.8868 | 193.5183 | 178.5316
345.3167 | 181.2629 | 193.9969 | 178.4511
346.3167 | 180.8372 | 194.8866 | 178.3838
347.3167 | 180.8452 | 195.1494 | 178.689
348.3167 | 181.3162 | 195.4202 | 179.15
349.3167 | 180.8005 | 195.8759 | 179.451
350.3167 | 180.9047 | 195.6876 | 179.9947
351.3167 | 181.2154 | 196.7226 | 180.6012
352.3167 | 181.7941 | 197.0754 | 180.7079
353.3167 | 181.6814 | 197.9679 | 181.2684
354.3167 | 181.4169 | 198.1453 | 182.3924
355.3167 | 180.9331 | 198.1755 | 182.7119
356.3167 | 181.5509 | 197.8327 | 182.6001
357.3167 | 182.8313 | 197.9308 | 182.4744
358.3167 | 182.6658 | 197.8096 | 182.8662
359.3167 | 182.567 | 198.2909 | 183.3106
360.3167 | 182.2031 | 198.4299 | 183.7538
361.3167 | 181.7429 | 198.2993 | 183.8479
362.3167 | 182.6356 | 198.9511 | 183.4682
363.3167 | 181.9541 | 198.671 | 183.1671
364.3167 | 181.9746 | 198.7992 | 183.4511
365.3167 | 181.6738 | 198.8964 | 184.4819
366.3167 | 181.3749 | 199.1594 | 184.9029
367.3167 | 181.9779 | 199.2056 | 184.9683
368.3167 | 181.8912 | 199.6688 | 184.9384
369.3167 | 182.0461 | 199.9018 | 184.7771
370.3167 | 182.7975 | 199.6906 | 184.8609
371.3167 | 182.932 | 199.7569 | 185.3349
372.3167 | 183.1759 | 199.5962 | 185.5513
373.3167 | 183.0732 | 199.8307 | 185.5474
374.3167 | 182.6989 | 199.7428 | 186.1501
375.3167 | 182.2011 | 200.8842 | 185.99
376.3167 | 182.181 | 201.5344 | 186.0663
377.3167 | 182.1749 | 201.319 | 185.8965
378.3167 | 182.4944 | 201.1139 | 186.2403
379.3167 | 182.4476 | 200.735 | 186.5405
380.3167 | 182.0511 | 200.9062 | 186.314
381.3167 | 181.3018 | 201.037 | 186.28
382.3167 | 181.5085 | 201.0656 | 186.1241
383.3167 | 182.4179 | 201.2129 | 186.3752
384.3167 | 182.0249 | 201.4592 | 186.9134
385.3167 | 181.7264 | 201.6116 | 187.4632
386.3167 | 182.2313 | 202.1033 | 187.5118
387.3167 | 181.7553 | 202.2209 | 187.5176
388.3167 | 181.6142 | 202.6887 | 187.3228
389.3167 | 181.7286 | 203.3911 | 187.3141
390.3167 | 181.9662 | 203.9018 | 187.0368
391.3167 | 182.8105 | 204.4502 | 187.4386
392.3167 | 182.3465 | 204.5079 | 187.4452
393.3167 | 183.2989 | 205.1145 | 187.5413
394.3167 | 184.2542 | 205.0261 | 187.671
395.3167 | 184.9114 | 204.713 | 187.2832
396.3167 | 185.1986 | 205.6941 | 187.3398
397.3167 | 186.552 | 205.6021 | 187.8757
398.3167 | 186.6153 | 205.5478 | 188.3068
399.3167 | 186.5284 | 206.4415 | 188.1395
400.3167 | 186.5123 | 207.042 | 188.0298
401.3167 | 187.4238 | 208.0071 | 188.6919
402.3167 | 187.4945 | 208.3068 | 188.7223
403.3167 | 187.975 | 208.4836 | 188.489
404.3167 | 188.3456 | 208.4399 | 188.5431
405.3167 | 188.0184 | 208.7271 | 188.9833
406.3167 | 188.3858 | 209.0526 | 189.0094
407.3167 | 187.7577 | 208.8413 | 189.1878
408.3167 | 187.395 | 208.956 | 189.5355
409.3167 | 188.5297 | 209.296 | 190.5336
410.3167 | 188.4432 | 210.1722 | 190.798
411.3167 | 189.7721 | 209.8955 | 191.3141
412.3167 | 189.4221 | 209.4095 | 191.2609
413.3167 | 188.9262 | 209.3001 | 191.1719
414.3167 | 188.8326 | 209.3886 | 191.4141
415.3167 | 188.8299 | 209.101 | 191.4978
416.3167 | 188.4751 | 209.2076 | 191.5441
417.3167 | 188.8597 | 209.6562 | 192.3132
418.3167 | 188.6323 | 210.4435 | 193.4874
419.3167 | 189.3661 | 211.1239 | 194.383
420.3167 | 188.9721 | 210.9891 | 195.5408
421.3167 | 188.9 | 211.3527 | 195.7854
422.3167 | 188.3962 | 211.2743 | 196.6135
423.3167 | 188.5828 | 211.6372 | 197.0692
424.3167 | 188.18 | 212.3572 | 197.2076
425.3167 | 187.6815 | 213.6724 | 197.4194
426.3167 | 187.9958 | 213.7704 | 197.5852
427.3167 | 188.818 | 213.6212 | 198.6976
428.3167 | 188.9027 | 214.1986 | 199.0521
429.3167 | 190.0103 | 214.3929 | 198.7351
430.3167 | 189.9013 | 214.5097 | 198.7912
431.3167 | 190.062 | 214.5261 | 198.6579
432.3167 | 190.3964 | 215.1794 | 198.9369
433.3167 | 190.3633 | 215.0733 | 199.4319
434.3167 | 190.1758 | 215.2007 | 199.4251
435.3167 | 190.1329 | 214.7341 | 199.2898
436.3167 | 189.972 | 214.3719 | 198.9503
437.3167 | 189.4496 | 214.4586 | 198.8706
438.3167 | 188.8194 | 214.3522 | 198.5054
439.3167 | 188.6649 | 213.9931 | 198.3182
440.3167 | 188.8532 | 213.8741 | 198.0033
441.3167 | 188.9794 | 213.6776 | 197.9283
442.3167 | 189.5002 | 213.5643 | 198.4516
443.3167 | 189.5345 | 214.2695 | 198.3826
444.3167 | 189.183 | 214.2315 | 198.1519
445.3167 | 188.7013 | 214.2977 | 198.2684
446.3167 | 188.8069 | 213.9605 | 198.57
447.3167 | 189.644 | 213.9127 | 198.5325
448.3167 | 190.1288 | 214.0512 | 198.6116
449.3167 | 190.0806 | 214.4524 | 198.5389
450.3167 | 189.7818 | 214.2182 | 198.7167
451.3167 | 189.3313 | 214.2924 | 198.7978
452.3167 | 189.6986 | 214.0465 | 198.7509
453.3167 | 190.9553 | 214.2632 | 198.924
454.3167 | 192.084 | 214.393 | 199.4789
455.3167 | 191.4386 | 214.4784 | 199.3874
456.3167 | 191.4216 | 214.6923 | 199.4875
457.3167 | 193.6189 | 215.083 | 199.5094
458.3167 | 192.8862 | 214.9176 | 199.6938
459.3167 | 193.8915 | 215.3537 | 199.7793
460.3167 | 193.991 | 215.7082 | 199.5004
461.3167 | 193.686 | 215.8562 | 199.5602
462.3167 | 193.5501 | 216.1963 | 199.3965
463.3167 | 193.0483 | 215.8338 | 199.6151
464.3167 | 193.2527 | 215.6078 | 200.2742
465.3167 | 193.0631 | 216.0226 | 200.404
466.3167 | 193.348 | 215.9463 | 200.3394
467.3167 | 193.6606 | 215.8773 | 200.4645
468.3167 | 193.0513 | 215.9713 | 200.5108
469.3167 | 193.9752 | 216.3931 | 200.6125
470.3167 | 193.6458 | 216.8444 | 200.9095
471.3167 | 193.7285 | 217.064 | 200.815
472.3167 | 195.2642 | 217.2655 | 200.9619
473.3167 | 195.0302 | 218.0904 | 201.2903
474.3167 | 195.3378 | 219.0981 | 201.7894
475.3167 | 195.3145 | 219.4233 | 201.6481
476.3167 | 195.5684 | 220.1054 | 201.9301
477.3167 | 195.2712 | 219.919 | 202.1593
478.3167 | 194.9579 | 219.5602 | 202.0077
479.3167 | 194.8212 | 219.6759 | 201.8798
480.3167 | 194.5663 | 219.504 | 201.9086
481.3167 | 193.9518 | 219.0807 | 201.7326
482.3167 | 193.9755 | 218.7672 | 201.8933
483.3167 | 193.9277 | 218.4811 | 201.5934
484.3167 | 193.689 | 218.3388 | 201.5788
485.3167 | 194.099 | 218.3692 | 201.2294
486.3167 | 194.5172 | 218.2964 | 200.8437
487.3167 | 194.5814 | 218.4701 | 200.7607
488.3167 | 194.387 | 218.2898 | 200.7575
489.3167 | 194.3531 | 218.0077 | 200.6397
490.3167 | 194.1614 | 218.1941 | 201.0349
491.3167 | 194.6445 | 218.3145 | 201.3132
492.3167 | 195.5231 | 218.7509 | 202.0102
493.3167 | 196.1374 | 218.7445 | 202.2145
494.3167 | 196.4151 | 219.5214 | 202.5143
495.3167 | 196.8295 | 219.9347 | 202.4584
496.3167 | 196.686 | 220.1765 | 202.4345
497.3167 | 197.3049 | 220.3093 | 202.4607
498.3167 | 197.2416 | 220.1396 | 202.7847
499.3167 | 196.9416 | 220.0306 | 202.6316
500.3167 | 197.3852 | 220.2895 | 202.7789
501.3167 | 197.9874 | 220.5349 | 202.7201
502.3167 | 197.3703 | 221.5538 | 203.7548
503.3167 | 197.5103 | 222.0824 | 204.9276
504.3167 | 197.4294 | 223.5409 | 205.2235
505.3167 | 198.1794 | 223.7142 | 205.301
506.3167 | 199.2288 | 224.8623 | 205.2126
507.3167 | 199.0967 | 224.6573 | 205.2323
508.3167 | 199.4603 | 224.6921 | 205.3793
509.3167 | 200.0866 | 225.4115 | 205.855
510.3167 | 200.0079 | 225.859 | 206.5893
511.3167 | 199.9532 | 225.9827 | 207.0509
512.3167 | 199.7043 | 225.5314 | 207.2217
513.3167 | 199.5662 | 225.0235 | 207.0091
514.3167 | 200.4052 | 225.2774 | 207.4457
515.3167 | 199.9001 | 224.8184 | 207.0127
516.3167 | 200.2557 | 225.3007 | 206.7222
517.3167 | 200.1527 | 224.7933 | 207.1142
518.3167 | 199.8411 | 224.8889 | 207.1614
519.3167 | 199.4784 | 224.9048 | 207.1386
520.3167 | 199.2757 | 224.4074 | 207.442
521.3167 | 199.4819 | 224.0082 | 207.7057
522.3167 | 199.4129 | 223.4194 | 207.6818
523.3167 | 198.859 | 223.155 | 207.5332
524.3167 | 198.6367 | 222.8789 | 207.6787
525.3167 | 198.2328 | 222.6171 | 207.553
526.3167 | 198.2795 | 222.6162 | 207.5999
527.3167 | 198.395 | 222.4699 | 207.9594
528.3167 | 199.5033 | 222.1655 | 208.0084
529.3167 | 199.0573 | 221.8449 | 208.2223
530.3167 | 199.7497 | 221.7915 | 208.444
531.3167 | 200.5729 | 222.066 | 208.2083
532.3167 | 200.907 | 222.0162 | 208.6331
533.3167 | 201.2899 | 221.9148 | 208.4674
534.3167 | 202.3227 | 221.831 | 208.6346
535.3167 | 201.2537 | 222.1976 | 208.7214
536.3167 | 201.017 | 222.1166 | 208.9426
537.3167 | 200.588 | 222.4341 | 209.2725
538.3167 | 200.7777 | 222.3721 | 209.3136
539.3167 | 200.4244 | 222.4844 | 209.4185
540.3167 | 200.4909 | 222.5225 | 209.4576
541.3167 | 200.4265 | 222.4355 | 209.1426
542.3167 | 199.881 | 222.1893 | 208.8022
543.3167 | 199.883 | 221.9964 | 208.6826
544.3167 | 200.2868 | 222.003 | 208.5661
545.3167 | 200.122 | 222.0284 | 208.1162
546.3167 | 200.022 | 221.822 | 208.1605
547.3167 | 199.9947 | 221.8644 | 208.3368
548.3167 | 199.7157 | 221.8362 | 209.1729
549.3167 | 199.4522 | 222.052 | 209.0971
550.3167 | 199.3968 | 222.4461 | 209.3802
551.3167 | 199.3938 | 222.5684 | 209.8318
552.3167 | 199.3577 | 222.9602 | 210.0737
553.3167 | 199.8841 | 223.1455 | 210.0727
554.3167 | 200.9563 | 223.0289 | 210.426
555.3167 | 200.9074 | 223.2633 | 210.6334
556.3167 | 200.7938 | 223.4556 | 210.3169
557.3167 | 200.7385 | 223.4881 | 210.0388
558.3167 | 200.9617 | 223.6616 | 210.2108
559.3167 | 201.1238 | 223.6362 | 210.0903
560.3167 | 200.8392 | 223.6525 | 210.1212
561.3167 | 200.729 | 223.6432 | 210.5142
562.3167 | 200.5022 | 223.7024 | 210.8782
563.3167 | 200.4738 | 223.4602 | 210.8351
564.3167 | 200.0637 | 223.0255 | 210.9389
565.3167 | 200.4717 | 223.1962 | 211.078
566.3167 | 200.9423 | 222.9097 | 211.1193
567.3167 | 201.2046 | 222.6121 | 211.1838
568.3167 | 201.3777 | 222.4764 | 211.3459
569.3167 | 201.7104 | 222.2941 | 211.4168
570.3167 | 201.7392 | 222.5837 | 211.4383
571.3167 | 201.886 | 222.8731 | 211.9251
572.3167 | 202.0213 | 223.0972 | 212.3556
573.3167 | 202.5257 | 223.1373 | 212.3329
574.3167 | 202.9766 | 222.9388 | 212.3843
575.3167 | 203.5593 | 223.2798 | 212.2273
576.3167 | 203.7873 | 222.9066 | 212.1109
577.3167 | 204.173 | 222.9706 | 212.0379
578.3167 | 204.7212 | 223.134 | 212.7545
579.3167 | 205.4356 | 223.468 | 213.1144
580.3167 | 205.425 | 223.7916 | 213.6668
581.3167 | 205.5877 | 224.0224 | 213.6582
582.3167 | 205.4009 | 224.576 | 213.4423
583.3167 | 205.4748 | 224.8274 | 213.7053
584.3167 | 205.0985 | 224.9643 | 214.1189
585.3167 | 204.8838 | 225.2777 | 214.4559
586.3167 | 204.9614 | 226.2467 | 213.811
587.3167 | 204.7975 | 226.5113 | 213.9494
588.3167 | 204.7423 | 226.8114 | 213.9393
589.3167 | 205.3801 | 226.9128 | 214.356
590.3167 | 205.1694 | 227.118 | 214.2954
591.3167 | 205.0627 | 227.4767 | 214.1844
592.3167 | 204.7593 | 227.3903 | 214.2096
593.3167 | 204.711 | 228.1183 | 213.8162
594.3167 | 204.8964 | 228.0835 | 214.1077
595.3167 | 204.5131 | 227.6845 | 214.9616
596.3167 | 204.3445 | 227.5021 | 215.1727
597.3167 | 204.1099 | 227.6701 | 215.0245
598.3167 | 204.1276 | 227.4609 | 214.6985
599.3167 | 203.8572 | 227.0309 | 214.6702
600.3167 | 204.0387 | 226.221 | 214.7608
601.3167 | 203.8859 | 225.7805 | 214.5239
602.3167 | 203.8026 | 225.509 | 214.1922
603.3167 | 204.088 | 225.4184 | 213.7181
604.3167 | 204.4118 | 225.4704 | 214.0271
605.3167 | 204.4416 | 225.5178 | 213.9871
606.3167 | 204.4505 | 226.0543 | 214.491
607.3167 | 204.2067 | 226.0654 | 214.43
608.3167 | 204.3727 | 226.2844 | 214.4113
609.3167 | 204.6721 | 225.9138 | 214.6253
610.3167 | 204.1467 | 226.0227 | 215.2155
611.3167 | 203.9158 | 226.9409 | 215.4006
612.3167 | 203.8814 | 226.8995 | 215.5904
613.3167 | 203.8643 | 226.5978 | 215.6277
614.3167 | 203.6918 | 226.5925 | 215.7519
615.3167 | 203.6551 | 226.7686 | 215.7356
616.3167 | 205.026 | 226.77 | 215.4952
617.3167 | 205.1175 | 226.7542 | 215.1904
618.3167 | 204.7496 | 226.5946 | 214.8734
619.3167 | 204.4931 | 226.605 | 214.5098
620.3167 | 205.4482 | 226.0954 | 214.4679
621.3167 | 206.4357 | 225.751 | 214.325
622.3167 | 206.1429 | 225.6217 | 214.5104
623.3167 | 206.2932 | 225.5539 | 214.4695
624.3167 | 206.0825 | 225.3968 | 214.2315
625.3167 | 206.2888 | 225.2684 | 213.9679
626.3167 | 206.0289 | 225.5079 | 213.6715
627.3167 | 205.9545 | 225.5755 | 213.9671
628.3167 | 206.1886 | 225.9071 | 214.0324
629.3167 | 206.3298 | 226.655 | 214.4345
630.3167 | 206.5023 | 226.7291 | 214.5352
631.3167 | 206.4545 | 226.5768 | 214.6728
632.3167 | 206.6562 | 226.5376 | 214.588
633.3167 | 206.7037 | 227.0434 | 214.5442
634.3167 | 206.6158 | 226.9172 | 214.6198
635.3167 | 206.4773 | 226.8487 | 214.4991
636.3167 | 206.5761 | 227.0182 | 214.4656
637.3167 | 207.0158 | 226.7932 | 214.5333
638.3167 | 206.9656 | 226.5977 | 214.9319
639.3167 | 207.1836 | 226.3936 | 215.6528
640.3167 | 207.4719 | 226.9575 | 216.6193
641.3167 | 207.2231 | 226.7493 | 217.2424
642.3167 | 207.1355 | 226.7633 | 217.2914
643.3167 | 207.417 | 227.1671 | 217.9689
644.3167 | 208.3508 | 227.1565 | 218.3462
645.3167 | 208.2857 | 227.267 | 218.5565
646.3167 | 207.9633 | 227.9442 | 218.9041
647.3167 | 208.0147 | 228.3428 | 219.5989
648.3167 | 208.3545 | 228.7864 | 219.9019
649.3167 | 208.4097 | 228.9004 | 219.8449
650.3167 | 208.5703 | 228.9873 | 220.0422
651.3167 | 209.1047 | 229.2308 | 219.8226
652.3167 | 210.4407 | 229.9721 | 220.0181
653.3167 | 210.2093 | 229.9406 | 219.8114
654.3167 | 210.561 | 230.0129 | 219.799
655.3167 | 210.8486 | 229.9191 | 219.88
656.3167 | 211.2532 | 230.3639 | 220.2158
657.3167 | 211.0637 | 230.6289 | 220.2278
658.3167 | 210.8357 | 231.2366 | 220.6975
659.3167 | 210.2581 | 231.0691 | 221.2111
660.3167 | 209.9364 | 230.9304 | 221.2202
661.3167 | 211.5358 | 230.9409 | 221.1202
662.3167 | 211.3752 | 231.7223 | 221.2206
663.3167 | 211.3511 | 232.0536 | 221.6019
664.3167 | 211.7736 | 232.2997 | 221.7427
665.3167 | 211.8651 | 232.6159 | 221.6871
666.3167 | 212.5619 | 232.6064 | 221.9476
667.3167 | 213.094 | 233.5082 | 222.266
668.3167 | 213.6041 | 233.2728 | 222.2118
669.3167 | 213.3443 | 234.1568 | 222.9926
670.3167 | 213.7526 | 233.8756 | 222.8992
671.3167 | 213.0302 | 233.9089 | 222.9972
672.3167 | 212.857 | 234.3435 | 222.7264
673.3167 | 212.7557 | 235.6337 | 222.8106
674.3167 | 212.6348 | 235.9857 | 222.724
675.3167 | 212.6188 | 235.9025 | 222.8742
676.3167 | 212.5966 | 235.6799 | 222.8625
677.3167 | 212.4373 | 235.2314 | 222.9878
678.3167 | 212.6146 | 235.2497 | 222.8279
679.3167 | 213.011 | 234.8708 | 222.6687
680.3167 | 212.5468 | 234.555 | 222.7724
681.3167 | 213.0491 | 234.611 | 223.423
682.3167 | 213.271 | 235.2555 | 224.0358
683.3167 | 213.5551 | 235.4053 | 223.7627
684.3167 | 213.7248 | 235.4983 | 223.8844
685.3167 | 213.3578 | 235.731 | 223.7932
686.3167 | 212.8363 | 236.0642 | 223.7503
687.3167 | 212.6005 | 235.8167 | 223.7619
688.3167 | 212.2855 | 235.4127 | 223.7493
689.3167 | 212.4418 | 235.2787 | 223.8441
690.3167 | 212.3254 | 235.0728 | 223.5833
691.3167 | 212.9941 | 234.7435 | 223.2817
692.3167 | 213.1244 | 234.6 | 223.1297
693.3167 | 212.9214 | 234.1659 | 222.6187
694.3167 | 212.6697 | 234.0909 | 222.3565
695.3167 | 212.3535 | 233.8019 | 222.3202
696.3167 | 212.2605 | 233.211 | 222.0575
697.3167 | 212.276 | 232.8832 | 221.9591
698.3167 | 212.7857 | 233.8811 | 221.8919
699.3167 | 212.8158 | 233.8917 | 221.7014
700.3167 | 212.9619 | 233.5264 | 221.9179
701.3167 | 212.9738 | 233.5888 | 221.9011
702.3167 | 213.1728 | 233.3577 | 221.8873
703.3167 | 213.0621 | 233.6507 | 221.647
704.3167 | 213.2754 | 233.8376 | 221.6922
705.3167 | 213.1987 | 233.7638 | 221.6664
706.3167 | 213.911 | 233.3612 | 221.6805
707.3167 | 213.9118 | 233.857 | 221.8478
708.3167 | 213.8151 | 234.108 | 222.0942
709.3167 | 213.4256 | 234.296 | 222.0893
710.3167 | 213.9308 | 234.2862 | 222.339
711.3167 | 214.1699 | 234.3276 | 222.3287
712.3167 | 214.4814 | 234.6546 | 222.4023
713.3167 | 215.1405 | 234.4555 | 222.4097
714.3167 | 214.9543 | 234.7108 | 222.9693
715.3167 | 214.8075 | 234.8453 | 223.0792
716.3167 | 215.8637 | 235.0865 | 223.4071
717.3167 | 216.2403 | 235.2312 | 223.4734
718.3167 | 216.0218 | 235.4078 | 223.6702
719.3167 | 215.8737 | 235.3906 | 223.6705
720.3167 | 215.5999 | 235.7665 | 223.9262
721.3167 | 215.5316 | 235.9337 | 224.3969
722.3167 | 215.3983 | 236.3525 | 224.5043
723.3167 | 215.9272 | 236.6581 | 225.1143
724.3167 | 215.8481 | 236.8444 | 225.9135
725.3167 | 215.9603 | 237.0851 | 226.0243
726.3167 | 216.1061 | 237.2965 | 226.0511
727.3167 | 216.2998 | 237.1784 | 225.7883
728.3167 | 216.1392 | 237.0377 | 225.8083
729.3167 | 216.7692 | 237.0531 | 225.8536
730.3167 | 217.7282 | 237.2586 | 225.7323
731.3167 | 217.7893 | 237.3134 | 225.3223
732.3167 | 218.7279 | 237.3546 | 225.0125
733.3167 | 218.5296 | 236.9987 | 224.9253
734.3167 | 218.9458 | 236.7945 | 224.9402
735.3167 | 218.7782 | 236.3506 | 225.2851
736.3167 | 218.1128 | 235.8033 | 225.247
737.3167 | 217.9493 | 235.5862 | 225.8186
738.3167 | 217.8845 | 235.3668 | 225.9674
739.3167 | 218.1914 | 234.8997 | 225.8573
740.3167 | 218.7335 | 236.1509 | 225.5974
741.3167 | 219.6312 | 235.8865 | 225.3682
742.3167 | 219.3804 | 235.7531 | 225.41
743.3167 | 219.6888 | 235.6181 | 225.6611
744.3167 | 219.8235 | 235.319 | 226.0012
745.3167 | 219.7646 | 234.963 | 226.6454
746.3167 | 219.4227 | 234.7159 | 226.7566
747.3167 | 219.6023 | 234.614 | 227.3201
748.3167 | 220.1934 | 235.2877 | 227.8125
749.3167 | 220.5585 | 235.2248 | 228.771
750.3167 | 219.9111 | 235.7322 | 229.1675
751.3167 | 220.5644 | 236.9891 | 229.66
752.3167 | 220.3148 | 237.2392 | 229.9512
753.3167 | 220.9007 | 237.2028 | 230.551
754.3167 | 221.3262 | 237.557 | 230.7314
755.3167 | 221.4745 | 237.654 | 230.7856
756.3167 | 221.1868 | 238.8918 | 231.2199
757.3167 | 221.4043 | 239.4852 | 230.7787
758.3167 | 221.8649 | 239.5921 | 231.3811
759.3167 | 222.9574 | 239.6966 | 231.7828
760.3167 | 223.277 | 239.7252 | 232.8811
761.3167 | 222.8484 | 241.0648 | 233.2021
762.3167 | 222.7684 | 241.2319 | 233.2505
763.3167 | 222.4987 | 241.8239 | 233.3116
764.3167 | 222.3593 | 241.8811 | 233.612
765.3167 | 222.4522 | 241.866 | 233.4918
766.3167 | 221.9931 | 242.2034 | 233.6541
767.3167 | 221.9827 | 242.1535 | 233.726
768.3167 | 221.5226 | 243.2573 | 233.9053
769.3167 | 221.5869 | 243.4126 | 233.6191
770.3167 | 222.2781 | 243.4755 | 233.8351
771.3167 | 222.1395 | 243.5477 | 233.6797
772.3167 | 222.0973 | 243.3702 | 233.6734
773.3167 | 221.5739 | 243.4773 | 233.3585
774.3167 | 222.5876 | 243.8691 | 233.0332
775.3167 | 222.8609 | 245.0676 | 233.5636
776.3167 | 222.6706 | 244.7911 | 233.3642
777.3167 | 222.7691 | 244.8415 | 233.3048
778.3167 | 222.9049 | 244.739 | 233.2625
779.3167 | 222.705 | 244.3684 | 232.8231
780.3167 | 223.2018 | 244.1787 | 232.1797
781.3167 | 224.2208 | 244.3346 | 231.8909
782.3167 | 224.7338 | 243.9167 | 231.8049
783.3167 | 224.5235 | 243.7334 | 231.7942
784.3167 | 224.7258 | 243.3096 | 231.7238
785.3167 | 224.4889 | 243.1056 | 231.7022
786.3167 | 224.5805 | 243.1822 | 231.7085
787.3167 | 224.1089 | 243.3718 | 231.663
788.3167 | 223.762 | 243.293 | 231.5452
789.3167 | 223.5526 | 243.1869 | 231.4804
790.3167 | 223.5909 | 243.4776 | 231.4339
791.3167 | 223.6077 | 243.4635 | 231.8517
792.3167 | 223.4504 | 243.3896 | 231.8517
793.3167 | 223.352 | 243.3134 | 232.0803
794.3167 | 223.2346 | 243.0774 | 232.2544
795.3167 | 224.0126 | 242.9846 | 232.218
796.3167 | 223.8264 | 242.669 | 232.1186
797.3167 | 223.9339 | 242.5825 | 232.3285
798.3167 | 224.6556 | 242.4497 | 232.9523
799.3167 | 224.8613 | 242.7956 | 233.1993
800.3167 | 225.056 | 243.1277 | 234.2316
801.3167 | 226.0713 | 243.1339 | 234.5184
802.3167 | 227.0615 | 244.6276 | 234.9686
803.3167 | 227.5013 | 244.0098 | 235.7656
804.3167 | 227.6814 | 243.8695 | 236.2295
805.3167 | 227.6542 | 243.703 | 236.0566
806.3167 | 227.6175 | 243.7619 | 236.047
807.3167 | 227.9402 | 243.981 | 236.0573
808.3167 | 227.8997 | 243.6086 | 235.8548
809.3167 | 227.622 | 243.6184 | 235.8628
810.3167 | 227.3342 | 243.2386 | 235.6002
811.3167 | 226.6628 | 242.8742 | 235.3022
812.3167 | 226.1566 | 242.5848 | 235.4959
813.3167 | 226.1521 | 243.1845 | 235.6559
814.3167 | 226.2221 | 243.7204 | 236.4588
815.3167 | 225.9862 | 244.6085 | 236.4982
816.3167 | 226.2023 | 244.7995 | 236.4211
817.3167 | 226.3953 | 245.2397 | 236.4442
818.3167 | 226.456 | 245.2454 | 236.5495
819.3167 | 226.5009 | 245.9785 | 236.3008
820.3167 | 226.1533 | 246.0573 | 236.0954
821.3167 | 226.2047 | 246.1769 | 236.1789
822.3167 | 226.0112 | 246.1811 | 235.8989
823.3167 | 225.8008 | 246.0277 | 235.8055
824.3167 | 225.5812 | 245.8165 | 235.618
825.3167 | 225.4403 | 245.8083 | 235.3978
826.3167 | 224.9516 | 245.7831 | 235.3758
827.3167 | 224.9401 | 245.4547 | 235.4871
828.3167 | 224.5141 | 245.1286 | 236.1049
829.3167 | 225.1207 | 245.3708 | 236.2291
830.3167 | 224.8812 | 245.9854 | 236.197
831.3167 | 224.6806 | 245.2742 | 235.8247
832.3167 | 224.4679 | 244.9375 | 235.5016
833.3167 | 224.5803 | 244.4851 | 235.2719
834.3167 | 224.3328 | 243.9998 | 234.8025
835.3167 | 224 | 243.3828 | 234.6082
836.3167 | 223.7287 | 242.7989 | 234.302
837.3167 | 223.863 | 242.5877 | 233.7859
838.3167 | 224.094 | 242.0909 | 233.3313
839.3167 | 223.9159 | 241.6883 | 233.0837
840.3167 | 223.9362 | 241.1859 | 233.1104
841.3167 | 223.832 | 240.7513 | 232.8948
842.3167 | 224.1124 | 240.938 | 232.9068
843.3167 | 224.4345 | 240.5588 | 232.5328
844.3167 | 223.7452 | 240.4758 | 232.2653
845.3167 | 224.0515 | 240.5907 | 232.5525
846.3167 | 223.6869 | 240.1804 | 232.5915
847.3167 | 223.6179 | 240.0337 | 232.7193
848.3167 | 223.4736 | 239.9274 | 232.9509
849.3167 | 223.45 | 240.0351 | 232.7795
850.3167 | 223.1903 | 240.0442 | 232.9471
851.3167 | 222.869 | 239.8719 | 232.775
852.3167 | 222.81 | 239.8031 | 232.7911
853.3167 | 222.4846 | 239.7936 | 232.7896
854.3167 | 222.1641 | 239.6124 | 232.2874
855.3167 | 222.273 | 239.6332 | 232.178
856.3167 | 222.0557 | 239.3046 | 232.4072
857.3167 | 221.5595 | 239.4794 | 232.5702
858.3167 | 221.7139 | 239.5197 | 233.0141
859.3167 | 221.7968 | 239.4889 | 233.2385
860.3167 | 222.3339 | 239.5446 | 234.5912
861.3167 | 222.9898 | 240.9533 | 234.9963
862.3167 | 223.1399 | 242.3132 | 236.1711
863.3167 | 223.5335 | 242.3301 | 236.5833
864.3167 | 223.5394 | 242.1705 | 236.5626
865.3167 | 223.5024 | 244.332 | 237.0773
866.3167 | 224.2515 | 244.1123 | 237.4289
867.3167 | 224.2878 | 244.0529 | 238.4946
868.3167 | 224.5604 | 245.0377 | 239.2184
869.3167 | 224.2404 | 245.1405 | 239.3165
870.3167 | 224.8295 | 244.886 | 239.567
871.3167 | 225.2561 | 244.7831 | 239.9366
872.3167 | 225.0845 | 244.8782 | 239.8786
873.3167 | 224.9726 | 245.0305 | 239.9884
874.3167 | 224.9489 | 245.0905 | 240.3056
875.3167 | 225.1347 | 245.3673 | 240.7179
876.3167 | 224.888 | 246.0234 | 241.1208
877.3167 | 225.703 | 246.8964 | 241.0005
878.3167 | 225.5335 | 247.0526 | 241.4407
879.3167 | 226.0284 | 247.0408 | 242.4601
880.3167 | 226.1367 | 247.8603 | 242.2204
881.3167 | 226.2141 | 247.7204 | 242.1441
882.3167 | 226.6348 | 247.4045 | 242.206
883.3167 | 226.699 | 247.3699 | 242.4538
884.3167 | 226.8465 | 247.4794 | 242.6554
885.3167 | 226.76 | 248.1177 | 242.7292
886.3167 | 226.7534 | 248.6248 | 242.6373
887.3167 | 226.9158 | 249.4647 | 242.712
888.3167 | 226.3107 | 249.4312 | 243.0068
889.3167 | 226.1094 | 249.5549 | 242.7518
890.3167 | 225.8597 | 249.8031 | 242.5957
891.3167 | 225.5229 | 249.5749 | 242.3901
892.3167 | 225.5241 | 249.4372 | 242.0837
893.3167 | 226.2821 | 249.2044 | 241.9154
894.3167 | 225.9717 | 249.0255 | 241.8219
895.3167 | 226.4476 | 248.995 | 241.6103
896.3167 | 226.5052 | 249.0611 | 241.8914
897.3167 | 226.0444 | 249.2672 | 241.7976
898.3167 | 225.9671 | 249.349 | 241.8505
899.3167 | 226.2255 | 249.4702 | 242.8305
900.3167 | 226.2693 | 248.9843 | 243.5161
901.3167 | 226.4612 | 248.5835 | 243.9603
902.3167 | 226.6962 | 248.8788 | 244.1626
903.3167 | 227.0824 | 249.1465 | 244.9171
904.3167 | 228.0246 | 249.4291 | 245.2848
905.3167 | 228.3322 | 250.1459 | 245.609
906.3167 | 228.1308 | 250.5288 | 246.175
907.3167 | 228.5803 | 250.444 | 246.5387
908.3167 | 228.8313 | 249.8169 | 247.5887
909.3167 | 229.3173 | 249.7442 | 247.9905
910.3167 | 230.4527 | 250.368 | 248.5683
911.3167 | 230.8487 | 249.8435 | 248.8437
912.3167 | 231.1934 | 249.8293 | 248.8649
913.3167 | 231.3308 | 249.861 | 248.9347
914.3167 | 231.6919 | 250.5002 | 249.3895
915.3167 | 232.2159 | 252.3599 | 250.1819
916.3167 | 232.2395 | 252.7702 | 250.0276
917.3167 | 232.5095 | 252.7251 | 249.7168
918.3167 | 232.587 | 254.1315 | 249.3424
919.3167 | 232.6838 | 254.3545 | 248.6719
920.3167 | 232.1694 | 254.0418 | 248.8332
921.3167 | 233.1515 | 254.2841 | 249.2398
922.3167 | 233.497 | 254.4289 | 249.5348
923.3167 | 234.3475 | 255.2001 | 250.324
924.3167 | 235.1118 | 255.4732 | 250.8072
925.3167 | 235.9255 | 257.8873 | 251.0992
926.3167 | 236.4004 | 258.3971 | 251.8647
927.3167 | 236.5912 | 258.5224 | 252.5296
928.3167 | 237.0632 | 258.9477 | 252.5663
929.3167 | 236.579 | 258.9776 | 252.3769
930.3167 | 236.8218 | 258.6304 | 252.2186
931.3167 | 237.7394 | 259.8616 | 252.5756
932.3167 | 237.5011 | 259.5205 | 252.5904
933.3167 | 237.8491 | 259.7774 | 252.7812
934.3167 | 238.6889 | 259.8971 | 253.7689
935.3167 | 239.7192 | 259.9252 | 254.0252
936.3167 | 240.9103 | 260.6072 | 254.6012
937.3167 | 242.0211 | 261.0003 | 254.936
938.3167 | 242.7187 | 261.4347 | 255.4893
939.3167 | 241.9141 | 262.577 | 256.1724
940.3167 | 242.4111 | 262.2047 | 256.7976
941.3167 | 243.2462 | 262.2519 | 257.6001
942.3167 | 244.0525 | 263.2753 | 258.6853
943.3167 | 244.6928 | 263.2654 | 259.359
944.3167 | 245.5302 | 263.613 | 259.8631
945.3167 | 245.1668 | 264.2318 | 259.7585
946.3167 | 245.8102 | 264.1913 | 259.784
947.3167 | 246.2511 | 264.7962 | 260.3671
948.3167 | 247.8458 | 265.9102 | 260.1952
949.3167 | 249.647 | 266.4871 | 260.5022
950.3167 | 249.8871 | 267.69 | 260.8501
951.3167 | 249.8145 | 270.042 | 262.279
952.3167 | 250.062 | 270.3902 | 262.6034
953.3167 | 249.9041 | 271.1165 | 262.4566
954.3167 | 249.1522 | 270.8053 | 262.4154
955.3167 | 248.7345 | 270.7731 | 262.1234
956.3167 | 247.7333 | 270.8043 | 261.8229
957.3167 | 247.5433 | 270.5715 | 262.4614
958.3167 | 247.1264 | 270.5111 | 262.0061
959.3167 | 247.44 | 271.1056 | 261.609
960.3167 | 247.5252 | 271.218 | 261.7711
961.3167 | 248.7658 | 271.5946 | 261.8157
962.3167 | 248.8242 | 272.5296 | 262.2756
963.3167 | 248.2486 | 271.9595 | 262.3372
964.3167 | 248.0269 | 271.8281 | 262.1375
965.3167 | 247.6702 | 271.3106 | 262.0857
966.3167 | 247.9993 | 271.0013 | 261.3745
967.3167 | 248.1637 | 270.6691 | 261.1582
968.3167 | 247.81 | 270.1531 | 260.7753
969.3167 | 247.2233 | 270.2676 | 260.0348
970.3167 | 246.302 | 269.6165 | 260.2012
971.3167 | 245.945 | 269.0159 | 260.0677
972.3167 | 246.28 | 269.029 | 259.9486
973.3167 | 245.7264 | 270.2647 | 261.9247
974.3167 | 245.4895 | 269.4423 | 261.7841
975.3167 | 245.2121 | 269.0183 | 261.9728
976.3167 | 245.1153 | 268.5758 | 262.0686
977.3167 | 245.1033 | 269.1854 | 262.9179
978.3167 | 244.9454 | 268.5987 | 262.4064
979.3167 | 244.8423 | 268.8971 | 261.8551
980.3167 | 244.8461 | 268.1079 | 261.5105
981.3167 | 244.7522 | 268.0456 | 261.7036
982.3167 | 244.4707 | 267.7532 | 261.6174
983.3167 | 244.3949 | 267.5911 | 261.3254
984.3167 | 244.4695 | 267.5682 | 261.0847
985.3167 | 244.776 | 267.3359 | 261.0767
986.3167 | 244.4255 | 267.3975 | 260.8451
987.3167 | 244.019 | 267.1041 | 260.7568
988.3167 | 243.72 | 267.4221 | 260.824
989.3167 | 243.4936 | 267.9282 | 261.1683
990.3167 | 243.2536 | 268.2921 | 261.5671
991.3167 | 243.2464 | 267.8796 | 261.2631
992.3167 | 243.0893 | 267.5172 | 261.3185
993.3167 | 242.7956 | 268.36 | 261.2144
994.3167 | 242.69 | 267.9242 | 261.158
995.3167 | 242.4405 | 267.5834 | 260.6554
996.3167 | 241.8141 | 267.1343 | 260.3424
997.3167 | 241.6902 | 267.3428 | 260.1531
998.3167 | 241.7105 | 267.6278 | 260.4717
999.3167 | 241.6581 | 268.2878 | 260.8176
1000.3167 | 241.8193 | 268.4897 | 261.1043
1001.3167 | 241.9414 | 268.492 | 260.8993
1002.3167 | 242.3033 | 268.1272 | 260.8945
1003.3167 | 241.5422 | 267.8029 | 260.1628
1004.3167 | 241.1897 | 267.4784 | 260.3903
1005.3167 | 241.0173 | 267.6488 | 261.0234
1006.3167 | 241.4549 | 267.4772 | 261.4035
1007.3167 | 241.7594 | 267.7817 | 261.9677
1008.3167 | 241.7805 | 269.3015 | 262.5835
1009.3167 | 242.4575 | 270.5422 | 262.9408
1010.3167 | 242.5762 | 270.1605 | 262.6708
1011.3167 | 242.8031 | 270.1784 | 262.6787
1012.3167 | 243.3643 | 270.2338 | 262.3578
1013.3167 | 244.2023 | 269.9815 | 262.0316
1014.3167 | 244.4441 | 269.6443 | 262.5722
1015.3167 | 244.1946 | 269.0683 | 263.6394
1016.3167 | 244.7387 | 268.915 | 263.9632
1017.3167 | 245.8657 | 269.1456 | 264.1896
1018.3167 | 246.233 | 269.2768 | 264.1336
1019.3167 | 247.0552 | 269.7798 | 265.3155
1020.3167 | 247.0288 | 269.4985 | 265.2241
1021.3167 | 247.2413 | 270.58 | 265.283
1022.3167 | 247.8674 | 270.5395 | 265.1117
1023.3167 | 248.5379 | 270.8986 | 265.4147
1024.3167 | 249.2471 | 271.298 | 265.9955
1025.3167 | 249.5634 | 272.0776 | 266.131
1026.3167 | 250.456 | 272.1925 | 266.1076
1027.3167 | 250.6947 | 272.3671 | 266.1494
1028.3167 | 251.4114 | 271.558 | 266.519
1029.3167 | 252.0896 | 271.2553 | 266.6966
1030.3167 | 251.5365 | 271.6899 | 266.5648
1031.3167 | 251.3798 | 271.1643 | 266.2652
1032.3167 | 251.4321 | 271.2355 | 266.3237
1033.3167 | 251.9387 | 271.1215 | 266.4177
1034.3167 | 253.0441 | 271.1437 | 266.2905
1035.3167 | 252.6226 | 272.0511 | 266.4121
1036.3167 | 253.3156 | 272.0851 | 266.4783
1037.3167 | 254.4739 | 272.5668 | 267.4132
1038.3167 | 254.8241 | 272.6164 | 268.1595
1039.3167 | 254.7319 | 272.6924 | 269.2949
1040.3167 | 254.7178 | 272.96 | 269.2039
1041.3167 | 254.4441 | 273.1527 | 269.3791
1042.3167 | 254.1625 | 273.2161 | 269.1534
1043.3167 | 254.074 | 274.1749 | 268.908
1044.3167 | 253.5074 | 274.7489 | 268.2188
1045.3167 | 253.5742 | 274.7295 | 267.7154
1046.3167 | 253.5309 | 274.7337 | 267.3188
1047.3167 | 254.0763 | 275.1703 | 266.9711
1048.3167 | 255.2366 | 274.7552 | 266.9381
1049.3167 | 254.873 | 275.2923 | 267.1733
1050.3167 | 255.3077 | 275.4723 | 267.3935
1051.3167 | 256.5915 | 275.1355 | 267.7959
1052.3167 | 256.5696 | 275.6899 | 267.6402
1053.3167 | 256.8113 | 275.6391 | 267.7226
1054.3167 | 257.6473 | 275.2851 | 267.7313
1055.3167 | 258.4112 | 275.559 | 268.2997
1056.3167 | 259.5442 | 275.9644 | 267.923
1057.3167 | 259.7371 | 275.5502 | 268.3989
1058.3167 | 259.7521 | 275.2106 | 268.3643
1059.3167 | 259.8936 | 275.1592 | 268.1445
1060.3167 | 260.0446 | 274.8554 | 268.3319
1061.3167 | 259.5326 | 274.6194 | 268.4629
1062.3167 | 258.9559 | 274.8403 | 268.3272
1063.3167 | 259.7648 | 275.4513 | 268.6236
1064.3167 | 259.7023 | 275.2897 | 268.3819
1065.3167 | 260.1018 | 275.3469 | 268.9403
1066.3167 | 259.3802 | 275.2513 | 268.3778
1067.3167 | 260.0075 | 274.952 | 268.311
1068.3167 | 259.8438 | 275.3132 | 268.5677
1069.3167 | 259.6558 | 275.392 | 268.5262
1070.3167 | 259.4757 | 274.9061 | 268.3783
1071.3167 | 260.1581 | 274.5542 | 268.4531
1072.3167 | 260.3089 | 274.0951 | 268.1007
1073.3167 | 260.4572 | 274.154 | 268.0588
1074.3167 | 260.4865 | 275.0369 | 268.5094
1075.3167 | 261.5354 | 275.389 | 268.6934
1076.3167 | 261.8014 | 275.6376 | 268.7813
1077.3167 | 262.7552 | 275.9087 | 269.1054
1078.3167 | 263.2799 | 275.714 | 268.8539
1079.3167 | 263.543 | 275.2483 | 268.71
1080.3167 | 264.0276 | 275.7058 | 268.7848
1081.3167 | 264.1284 | 275.8614 | 268.5285
1082.3167 | 264.0709 | 275.7688 | 269.0927
1083.3167 | 262.9189 | 275.216 | 269.7638
1084.3167 | 263.9137 | 276.1792 | 270.6526
1085.3167 | 263.1229 | 275.9353 | 270.4763
1086.3167 | 263.0653 | 276.3655 | 270.525
1087.3167 | 263.0839 | 276.2933 | 271.0866
1088.3167 | 262.923 | 276.0726 | 271.0695
1089.3167 | 262.4932 | 276.7677 | 270.4988
1090.3167 | 262.8566 | 276.9331 | 270.2035
1091.3167 | 263.2286 | 277.3507 | 270.5273
1092.3167 | 262.063 | 277.1538 | 270.3246
1093.3167 | 261.805 | 276.8434 | 270.5574
1094.3167 | 261.8166 | 276.8726 | 270.6536
1095.3167 | 262.3144 | 277.7216 | 270.9541
1096.3167 | 262.6115 | 277.6185 | 271.4179
1097.3167 | 263.5269 | 277.9167 | 271.1453
1098.3167 | 263.9287 | 278.7541 | 271.6754
1099.3167 | 263.8138 | 278.9977 | 271.8751
1100.3167 | 264.5094 | 279.1865 | 272.6429
1101.3167 | 265.1764 | 279.5071 | 272.1763
1102.3167 | 265.5531 | 279.4847 | 272.201
1103.3167 | 266.6587 | 279.3459 | 272.3978
1104.3167 | 266.3307 | 280.1714 | 272.1221
1105.3167 | 265.6515 | 279.7915 | 272.7121
1106.3167 | 264.8298 | 279.1425 | 273.2038
1107.3167 | 264.4342 | 279.4892 | 273.3204
1108.3167 | 264.4268 | 279.3362 | 273.2441
1109.3167 | 264.5676 | 279.6734 | 272.7921
1110.3167 | 264.81 | 279.6293 | 272.6724
1111.3167 | 264.6692 | 279.814 | 273.1676
1112.3167 | 264.9058 | 279.0837 | 272.9267
1113.3167 | 264.845 | 278.4531 | 272.5435
1114.3167 | 264.2457 | 278.2589 | 271.9536
1115.3167 | 264.8919 | 278.4688 | 271.41
1116.3167 | 265.3115 | 278.809 | 271.6052
1117.3167 | 265.3383 | 278.3468 | 271.9667
1118.3167 | 265.4198 | 277.5262 | 271.7297
1119.3167 | 265.2579 | 277.6121 | 271.4005
1120.3167 | 264.7478 | 277.9757 | 271.9102
1121.3167 | 265.159 | 277.9998 | 271.3897
1122.3167 | 265.5785 | 278.3453 | 271.6778
1123.3167 | 265.3983 | 278.7294 | 271.6325
1124.3167 | 265.7436 | 278.4706 | 271.7559
1125.3167 | 265.6791 | 278.6002 | 271.9126
1126.3167 | 266.2793 | 277.9831 | 271.2805
1127.3167 | 265.7611 | 277.4727 | 271.707
1128.3167 | 265.622 | 277.1087 | 270.9393
1129.3167 | 265.1401 | 277.1809 | 271.2263
1130.3167 | 265.8296 | 277.2712 | 270.7371
1131.3167 | 265.5311 | 277.1564 | 270.4088
1132.3167 | 265.1431 | 277.2115 | 270.3687
1133.3167 | 264.4976 | 277.0838 | 270.6341
1134.3167 | 264.5455 | 276.7026 | 270.443
1135.3167 | 264.5252 | 276.7059 | 269.8576
1136.3167 | 264.8692 | 276.7887 | 269.8346
1137.3167 | 265.2438 | 277.2203 | 269.665
1138.3167 | 265.2334 | 276.9876 | 269.7596
1139.3167 | 266.0563 | 277.1448 | 269.926
1140.3167 | 266.1097 | 277.1124 | 269.6985
1141.3167 | 266.5602 | 277.2514 | 270.0788
1142.3167 | 266.8393 | 277.0923 | 270.1395
1143.3167 | 266.6751 | 277.1295 | 270.0919
1144.3167 | 266.5976 | 276.9543 | 270.1113
1145.3167 | 266.493 | 276.4138 | 269.8871
1146.3167 | 266.3123 | 275.8415 | 269.8507
1147.3167 | 266.4052 | 276.2721 | 269.8757
1148.3167 | 265.5896 | 276.2513 | 270.129
1149.3167 | 265.0781 | 276.4177 | 270.25
1150.3167 | 264.9225 | 276.5294 | 270.1448
1151.3167 | 264.1256 | 276.1432 | 270.1846
1152.3167 | 264.7797 | 276.6942 | 269.9982
1153.3167 | 264.7989 | 276.4834 | 269.3375
1154.3167 | 265.1881 | 276.2268 | 269.9291
1155.3167 | 265.1254 | 276.7918 | 270.4564
1156.3167 | 265.1985 | 276.9958 | 270.9033
1157.3167 | 265.4455 | 277.1991 | 270.489
1158.3167 | 265.3943 | 277.5008 | 270.8799
1159.3167 | 265.2754 | 277.3301 | 270.819
1160.3167 | 264.7341 | 277.0579 | 271.4352
1161.3167 | 265.016 | 277.118 | 271.3018
1162.3167 | 265.2475 | 276.8776 | 271.3882
1163.3167 | 264.8731 | 277.0455 | 271.6353
1164.3167 | 265.0048 | 277.4113 | 271.2478
1165.3167 | 264.8215 | 277.3118 | 270.5953
1166.3167 | 264.0112 | 276.6588 | 270.6116
1167.3167 | 264.0606 | 275.9776 | 270.5713
1168.3167 | 264.4772 | 276.2817 | 270.6479
1169.3167 | 264.4971 | 276.0908 | 269.9856
1170.3167 | 264.4575 | 275.7784 | 269.5679
1171.3167 | 264.6141 | 276.0403 | 269.3623
1172.3167 | 264.6713 | 277.0282 | 269.7701
1173.3167 | 264.798 | 276.6163 | 269.7883
1174.3167 | 264.1219 | 276.2945 | 270.0595
1175.3167 | 263.8846 | 276.2777 | 269.9204
1176.3167 | 264.2451 | 276.9148 | 269.6257
1177.3167 | 264.7824 | 276.7641 | 270.0299
1178.3167 | 265.6207 | 277.3113 | 269.6926
1179.3167 | 265.8815 | 277.0205 | 269.4954
1180.3167 | 265.8714 | 277.5519 | 269.4091
1181.3167 | 265.7463 | 277.9458 | 269.9984
1182.3167 | 265.8273 | 277.6671 | 269.6476
1183.3167 | 265.7944 | 277.9225 | 270.0929
1184.3167 | 265.1449 | 278.2427 | 270.0334
1185.3167 | 265.0797 | 278.3366 | 270.3574
1186.3167 | 265.0279 | 278.3723 | 270.169
1187.3167 | 265.4432 | 278.2008 | 269.7322
1188.3167 | 265.5815 | 277.9912 | 269.6553
1189.3167 | 265.5868 | 277.3863 | 269.7886
1190.3167 | 265.9849 | 277.1155 | 269.933
1191.3167 | 265.7872 | 276.7537 | 270.2296
1192.3167 | 266.2231 | 277.2798 | 270.2991
1193.3167 | 266.5269 | 277.0655 | 270.7043
1194.3167 | 266.2962 | 277.3537 | 270.4392
1195.3167 | 265.8854 | 277.5443 | 270.6273
1196.3167 | 265.9215 | 277.7612 | 270.7635
1197.3167 | 266.282 | 277.7882 | 271.1108
1198.3167 | 266.5056 | 277.933 | 270.4522
1199.3167 | 267.2123 | 277.7336 | 270.4989
1200.3167 | 268.1922 | 278.5081 | 271.2459
1201.3167 | 268.556 | 278.439 | 271.0257
1202.3167 | 268.4829 | 278.2278 | 271.0219
1203.3167 | 267.507 | 277.6882 | 270.8172
1204.3167 | 267.2941 | 277.7228 | 270.7987
1205.3167 | 267.1842 | 277.8691 | 270.4039
1206.3167 | 267.6832 | 277.448 | 270.316
1207.3167 | 268.1278 | 278.0427 | 270.745
1208.3167 | 267.9051 | 278.1064 | 270.7184
1209.3167 | 267.0075 | 277.6758 | 270.6574
1210.3167 | 266.7931 | 277.6498 | 270.9586
1211.3167 | 266.2517 | 277.4123 | 270.366
1212.3167 | 265.1385 | 277.2979 | 270.4856
1213.3167 | 264.4598 | 276.9846 | 270.5174
1214.3167 | 264.6861 | 276.7521 | 270.1014
1215.3167 | 264.069 | 276.6901 | 269.6627
1216.3167 | 264.1097 | 276.5807 | 269.6667
1217.3167 | 263.974 | 276.7728 | 269.9984
1218.3167 | 263.7639 | 277.6735 | 270.1761
1219.3167 | 263.786 | 277.9544 | 270.3053
1220.3167 | 263.9327 | 277.9849 | 270.4785
1221.3167 | 264.295 | 277.9049 | 270.6763
1222.3167 | 264.6575 | 278.8583 | 270.6936
1223.3167 | 264.5628 | 278.2557 | 270.8742
1224.3167 | 264.6874 | 278.3427 | 271.3008
1225.3167 | 264.6102 | 277.6435 | 271.2561
1226.3167 | 264.1616 | 277.0503 | 271.533
1227.3167 | 264.5855 | 277.4201 | 270.9131
1228.3167 | 264.7595 | 277.4262 | 271.4238
1229.3167 | 265.2381 | 277.1623 | 271.3924
1230.3167 | 265.3885 | 276.8947 | 271.7159
1231.3167 | 265.5195 | 277.039 | 271.6126
1232.3167 | 265.3869 | 277.1506 | 271.2966
1233.3167 | 265.1907 | 276.681 | 270.9947
1234.3167 | 264.6502 | 276.2614 | 271.5598
1235.3167 | 264.6745 | 276.3295 | 271.8389
1236.3167 | 265.275 | 276.3078 | 271.6203
1237.3167 | 266.2697 | 276.6553 | 271.5836
1238.3167 | 265.8751 | 276.9483 | 272.0219
1239.3167 | 266.1573 | 276.8412 | 271.7316
1240.3167 | 266.2389 | 276.392 | 272.1726
1241.3167 | 266.2894 | 276.5515 | 272.2978
1242.3167 | 265.5606 | 277.2594 | 272.5148
1243.3167 | 265.4034 | 276.9748 | 272.0538
1244.3167 | 265.3133 | 277.1451 | 272.2633
1245.3167 | 265.5343 | 277.4591 | 272.3862
1246.3167 | 265.8203 | 277.7188 | 272.6594
1247.3167 | 265.9056 | 277.4992 | 272.7159
1248.3167 | 265.8395 | 276.8717 | 272.555
1249.3167 | 265.2412 | 277.4395 | 272.9712
1250.3167 | 264.8248 | 277.1063 | 272.6674
1251.3167 | 265.2387 | 276.3912 | 272.739
1252.3167 | 265.9639 | 277.1703 | 272.928
1253.3167 | 266.5631 | 278.9004 | 274.1256
1254.3167 | 266.2901 | 279.9038 | 274.568
1255.3167 | 266.1172 | 280.617 | 276.5049
1256.3167 | 266.248 | 281.6105 | 276.7782
1257.3167 | 265.9084 | 281.5901 | 276.9376
1258.3167 | 265.6114 | 281.7385 | 276.6582
1259.3167 | 265.1996 | 282.0293 | 276.4491
1260.3167 | 264.8526 | 281.7267 | 276.2618
1261.3167 | 264.8059 | 281.5114 | 275.8195
1262.3167 | 264.4734 | 281.612 | 275.2906
1263.3167 | 264.0702 | 281.6548 | 275.1324
1264.3167 | 264.2126 | 282.1676 | 275.3126
1265.3167 | 264.1274 | 281.9504 | 275.558
1266.3167 | 263.6714 | 281.7381 | 275.2941
1267.3167 | 263.4122 | 281.4997 | 275.4811
1268.3167 | 263.213 | 281.6536 | 275.2742
1269.3167 | 263.2666 | 281.4571 | 274.8353
1270.3167 | 263.3362 | 281.6974 | 274.7495
1271.3167 | 263.0507 | 281.5975 | 274.6484
1272.3167 | 262.9537 | 281.7362 | 274.6461
1273.3167 | 262.7636 | 281.3441 | 274.4691
1274.3167 | 263.0567 | 282.2135 | 274.7808
1275.3167 | 263.2054 | 282.0001 | 274.8056
1276.3167 | 263.3832 | 281.6114 | 274.9564
1277.3167 | 262.9865 | 281.6578 | 274.9089
1278.3167 | 263.6436 | 281.2209 | 274.6046
1279.3167 | 263.7614 | 281.1436 | 274.5016
1280.3167 | 263.8422 | 280.8853 | 274.1354
1281.3167 | 264.1761 | 281.1235 | 273.8828
1282.3167 | 264.0079 | 281.1698 | 273.84
1283.3167 | 263.8751 | 281.6146 | 273.7099
1284.3167 | 263.842 | 281.767 | 273.5025
1285.3167 | 264.0319 | 280.9457 | 273.1599
1286.3167 | 264.3076 | 280.2487 | 272.9045
1287.3167 | 264.2566 | 280.5475 | 273.1089
1288.3167 | 264.8846 | 280.8711 | 272.6717
1289.3167 | 265.6719 | 280.5901 | 273.1719
1290.3167 | 266.3834 | 280.47 | 273.6691
1291.3167 | 266.7465 | 280.6411 | 274.1373
1292.3167 | 266.2342 | 280.5876 | 274.0697
1293.3167 | 266.8666 | 280.4905 | 274.3545
1294.3167 | 266.6337 | 280.2527 | 274.6832
1295.3167 | 267.1455 | 279.5826 | 274.161
1296.3167 | 267.3819 | 279.7865 | 273.9251
1297.3167 | 266.7347 | 279.8688 | 273.9833
1298.3167 | 266.4043 | 280.3741 | 274.1378
1299.3167 | 266.1186 | 280.1795 | 274.2631
1300.3167 | 265.7377 | 279.9304 | 274.2084
1301.3167 | 265.4265 | 279.8412 | 273.9997
1302.3167 | 265.5923 | 280.4393 | 274.0195
1303.3167 | 265.9183 | 281.1279 | 273.908
1304.3167 | 266.2765 | 281.7717 | 274.6038
1305.3167 | 266.9782 | 282.2527 | 274.7372
1306.3167 | 266.7727 | 282.1364 | 274.6789
1307.3167 | 266.9625 | 281.8453 | 274.6578
1308.3167 | 267.8081 | 282.0733 | 275.005
1309.3167 | 268.3152 | 281.9708 | 274.6492
1310.3167 | 268.1287 | 282.5153 | 274.5879
1311.3167 | 268.1257 | 282.2312 | 274.5042
1312.3167 | 268.7666 | 283.0851 | 274.8807
1313.3167 | 268.8166 | 283.3217 | 274.6644
1314.3167 | 269.4296 | 283.0931 | 274.9907
1315.3167 | 269.9922 | 283.2739 | 275.1752
1316.3167 | 270.5697 | 282.9256 | 275.0143
1317.3167 | 270.6887 | 283.0813 | 274.7293
1318.3167 | 270.1867 | 282.6369 | 274.5466
1319.3167 | 270.0999 | 283.166 | 274.2578
1320.3167 | 269.9348 | 282.5687 | 274.3373
1321.3167 | 269.9281 | 282.3265 | 274.0608
1322.3167 | 270.1735 | 282.8764 | 273.7025
1323.3167 | 269.8684 | 282.8454 | 273.4222
1324.3167 | 269.9043 | 282.7931 | 273.3498
1325.3167 | 269.8559 | 283.2595 | 273.6929
1326.3167 | 270.1869 | 282.7882 | 273.8634
1327.3167 | 270.4694 | 282.9871 | 274.1166
1328.3167 | 270.2098 | 282.8066 | 274.5931
1329.3167 | 270.8555 | 282.7595 | 275.0473
1330.3167 | 270.8968 | 282.5907 | 274.7783
1331.3167 | 270.6989 | 282.3741 | 275.1001
1332.3167 | 271.208 | 282.5128 | 274.9561
1333.3167 | 271.2136 | 282.3627 | 274.6709
1334.3167 | 270.2159 | 281.7734 | 274.7825
1335.3167 | 270.3857 | 281.1175 | 275.1424
1336.3167 | 270.4651 | 280.7747 | 275.0258
1337.3167 | 270.8456 | 281.0721 | 274.9957
1338.3167 | 271.0092 | 281.3726 | 275.3819
1339.3167 | 271.2561 | 281.1099 | 275.1983
1340.3167 | 271.2071 | 281.8151 | 275.3618
1341.3167 | 271.364 | 281.6877 | 275.5252
1342.3167 | 271.3501 | 281.5276 | 274.946
1343.3167 | 271.5241 | 281.5876 | 274.9179
1344.3167 | 271.135 | 281.3053 | 275.2847
1345.3167 | 270.7227 | 281.6976 | 275.2218
1346.3167 | 270.9349 | 281.5464 | 275.5512
1347.3167 | 270.2104 | 281.4586 | 276.1986
1348.3167 | 270.1711 | 281.9097 | 275.9752
1349.3167 | 270.4271 | 282.4758 | 275.8716
1350.3167 | 269.9163 | 282.5888 | 275.9274
1351.3167 | 269.8901 | 283.3031 | 276.1501
1352.3167 | 269.9086 | 283.3906 | 275.8074
1353.3167 | 270.331 | 283.7482 | 275.3187
1354.3167 | 270.8563 | 283.7714 | 275.5191
1355.3167 | 271.13 | 283.5686 | 276.184
1356.3167 | 272.0481 | 284.5946 | 276.5584
1357.3167 | 272.6262 | 285.2162 | 276.962
1358.3167 | 272.614 | 286.0932 | 278.5421
1359.3167 | 272.5972 | 286.6509 | 279.3787
1360.3167 | 272.5461 | 286.8888 | 279.3111
1361.3167 | 272.7278 | 287.3405 | 279.529
1362.3167 | 273.249 | 287.3244 | 279.571
1363.3167 | 273.1791 | 287.1766 | 279.1837
1364.3167 | 273.1079 | 287.7251 | 279.0564
1365.3167 | 273.1789 | 287.2351 | 278.5487
1366.3167 | 273.0638 | 287.4381 | 278.4464
1367.3167 | 273.3186 | 287.1261 | 278.2347
1368.3167 | 273.2521 | 287.0686 | 278.0956
1369.3167 | 273.379 | 287.4431 | 278.7585
1370.3167 | 273.1809 | 287.3304 | 278.8361
1371.3167 | 273.2749 | 286.9381 | 278.8367
1372.3167 | 273.0933 | 286.1784 | 278.4589
1373.3167 | 272.7484 | 286.445 | 278.9257
1374.3167 | 272.3937 | 285.9166 | 278.614
1375.3167 | 273.4764 | 286.2956 | 279.1934
1376.3167 | 274.4086 | 286.8938 | 279.331
1377.3167 | 274.5536 | 286.7705 | 278.8679
1378.3167 | 274.6931 | 286.7554 | 278.8792
1379.3167 | 274.5434 | 287.0096 | 278.8262
1380.3167 | 274.6459 | 286.8572 | 278.7218
1381.3167 | 274.3101 | 287.3962 | 279.6249
1382.3167 | 274.5715 | 287.4151 | 279.5737
1383.3167 | 274.188 | 287.8988 | 279.5589
1384.3167 | 273.6494 | 287.5029 | 279.7653
1385.3167 | 273.817 | 287.1037 | 279.4372
1386.3167 | 273.1213 | 286.6372 | 279.1875
1387.3167 | 273.2657 | 286.5124 | 279.5124
1388.3167 | 273.2521 | 286.6428 | 278.6404
1389.3167 | 273.2592 | 286.319 | 278.0425
1390.3167 | 273.7301 | 285.7222 | 277.4089
1391.3167 | 273.4528 | 285.5552 | 277.0361
1392.3167 | 273.454 | 285.4053 | 277.3268
1393.3167 | 273.8156 | 285.9851 | 277.4178
1394.3167 | 273.5331 | 285.7957 | 277.0395
1395.3167 | 273.8435 | 285.2633 | 276.5028
1396.3167 | 273.9169 | 285.4048 | 276.0053
1397.3167 | 273.1818 | 284.9755 | 275.7348
1398.3167 | 272.7754 | 285.077 | 276.3103
1399.3167 | 272.5353 | 284.717 | 276.6559
1400.3167 | 271.9538 | 284.8317 | 276.7747
1401.3167 | 272.0801 | 284.8139 | 276.7294
1402.3167 | 272.2717 | 285.1458 | 277.5735
1403.3167 | 272.2726 | 285.0984 | 277.4801
1404.3167 | 271.864 | 285.2824 | 277.4739
1405.3167 | 272.5453 | 285.5005 | 277.457
1406.3167 | 273.1469 | 285.92 | 277.3476
1407.3167 | 273.6 | 286.2674 | 277.6282
1408.3167 | 273.9317 | 285.9129 | 277.1968
1409.3167 | 274.1491 | 285.8009 | 277.2189
1410.3167 | 274.9084 | 286.4583 | 277.7198
1411.3167 | 274.6956 | 286.6371 | 277.464
1412.3167 | 274.5381 | 286.9027 | 277.489
1413.3167 | 275.2245 | 286.6894 | 277.6859
1414.3167 | 275.3951 | 286.8409 | 277.3043
1415.3167 | 275.6493 | 286.7659 | 277.363
1416.3167 | 275.9807 | 287.0729 | 277.3236
1417.3167 | 275.85 | 286.9887 | 276.9265
1418.3167 | 275.9412 | 287.0276 | 276.8478
1419.3167 | 275.804 | 286.7013 | 277.0448
1420.3167 | 275.7904 | 286.1935 | 276.9716
1421.3167 | 275.8626 | 286.114 | 276.6706
1422.3167 | 275.4189 | 285.7976 | 275.8858
1423.3167 | 275.1659 | 285.6821 | 275.8696
1424.3167 | 274.5948 | 284.9759 | 275.9081
1425.3167 | 274.3359 | 284.7366 | 275.6668
1426.3167 | 274.4232 | 284.5627 | 275.6554
1427.3167 | 274.4993 | 284.1016 | 275.2559
1428.3167 | 274.588 | 284.1162 | 275.11
1429.3167 | 274.4926 | 284.4781 | 274.7055
1430.3167 | 274.8776 | 284.6736 | 275.1413
1431.3167 | 275.13 | 284.8114 | 275.053
1432.3167 | 275.147 | 284.7035 | 275.1185
1433.3167 | 274.9713 | 284.7271 | 274.9869
1434.3167 | 274.9934 | 284.7854 | 274.8637
1435.3167 | 274.9275 | 284.2897 | 274.4676
1436.3167 | 275.1976 | 283.6891 | 274.48
1437.3167 | 274.739 | 283.6306 | 274.3769
1438.3167 | 274.457 | 283.9554 | 274.2554
1439.3167 | 274.0624 | 283.6597 | 274.6058
1440.3167 | 273.4436 | 283.4249 | 275.0543
1441.3167 | 272.9818 | 283.2815 | 274.8105
1442.3167 | 272.7772 | 282.9976 | 274.5695
1443.3167 | 273.1249 | 283.5025 | 274.3978
1444.3167 | 273.5014 | 283.4924 | 274.241
1445.3167 | 273.741 | 284.3349 | 274.5218
1446.3167 | 274.0763 | 284.2097 | 274.4133
1447.3167 | 274.3985 | 284.6127 | 274.3536
1448.3167 | 274.2682 | 285.1074 | 274.0076
1449.3167 | 274.7602 | 284.7971 | 274.671
1450.3167 | 274.7031 | 284.8302 | 275.0366
1451.3167 | 274.3252 | 285.5991 | 275.7046
1452.3167 | 274.537 | 285.6658 | 276.7232
1453.3167 | 274.3935 | 286.2318 | 276.4748
1454.3167 | 274.0868 | 286.621 | 276.5306
1455.3167 | 274.3389 | 286.7389 | 277.1039
1456.3167 | 275.1202 | 287.1578 | 277.5059
1457.3167 | 275.2632 | 288.2338 | 277.9209
1458.3167 | 275.2323 | 288.594 | 278.3918
1459.3167 | 275.1165 | 288.4421 | 278.4511
1460.3167 | 275.192 | 288.4958 | 278.9045
1461.3167 | 275.682 | 288.8364 | 278.8827
1462.3167 | 275.4433 | 288.6555 | 278.871
1463.3167 | 275.5627 | 289.0534 | 279.0861
1464.3167 | 276.1335 | 289.8032 | 279.6356
1465.3167 | 276.6232 | 289.3675 | 279.5131
1466.3167 | 276.7647 | 289.6171 | 279.5221
1467.3167 | 276.8097 | 289.3273 | 279.233
1468.3167 | 276.6679 | 289.788 | 279.8352
1469.3167 | 276.9794 | 289.6864 | 279.544
1470.3167 | 277.0849 | 289.9192 | 279.6612
1471.3167 | 276.7398 | 289.6241 | 279.9065
1472.3167 | 276.727 | 289.9169 | 279.6308
1473.3167 | 276.8636 | 289.5901 | 279.9755
1474.3167 | 276.8498 | 289.6594 | 280.3938
1475.3167 | 276.1732 | 288.9139 | 280.4156
1476.3167 | 276.0165 | 288.9467 | 281.0682
1477.3167 | 276.0652 | 289.1592 | 281.3532
1478.3167 | 276.126 | 288.793 | 281.7927
1479.3167 | 276.2648 | 288.6951 | 281.8029
1480.3167 | 276.8807 | 289.3482 | 281.6337
1481.3167 | 276.8068 | 289.047 | 281.2278
1482.3167 | 276.6595 | 289.0165 | 281.2141
1483.3167 | 276.7342 | 289.0015 | 281.2729
1484.3167 | 277.0315 | 288.6313 | 281.5221
1485.3167 | 277.0673 | 288.8948 | 281.1201
1486.3167 | 277.1305 | 288.356 | 281.1186
1487.3167 | 277.4891 | 288.8564 | 281.4188
1488.3167 | 277.3448 | 288.8864 | 281.1188
1489.3167 | 277.7669 | 288.3567 | 281.2577
1490.3167 | 278.0919 | 288.5049 | 280.9881
1491.3167 | 278.0696 | 288.2884 | 281.1084
1492.3167 | 278.1055 | 288.2157 | 281.686
1493.3167 | 277.5264 | 288.6379 | 281.8456
1494.3167 | 277.5356 | 288.1514 | 282.1034
1495.3167 | 278.0541 | 287.8536 | 282.5171
1496.3167 | 277.2424 | 287.6208 | 282.5191
1497.3167 | 277.609 | 287.9429 | 282.4913
1498.3167 | 278.2433 | 287.5834 | 282.2113
1499.3167 | 277.7999 | 287.551 | 281.9789
1500.3167 | 277.8031 | 288.1152 | 281.863
1501.3167 | 278.1552 | 288.0504 | 281.9761
1502.3167 | 278.3177 | 287.6049 | 281.7372
1503.3167 | 278.6439 | 288.9282 | 281.8744
1504.3167 | 278.3647 | 289.464 | 282.5251
1505.3167 | 279.4075 | 289.5994 | 282.9951
1506.3167 | 279.6749 | 291.9034 | 282.9965
1507.3167 | 279.7339 | 292.3209 | 284.2872
1508.3167 | 279.8474 | 292.4578 | 285.091
1509.3167 | 279.455 | 292.6307 | 284.8508
1510.3167 | 278.9938 | 292.6268 | 284.5639
1511.3167 | 278.4086 | 292.4439 | 284.2223
1512.3167 | 278.5262 | 292.2621 | 284.1351
1513.3167 | 277.8728 | 292.4981 | 283.7457
1514.3167 | 277.3472 | 292.1537 | 283.2772
1515.3167 | 277.0812 | 292.2591 | 284.0623
1516.3167 | 276.7712 | 291.9459 | 283.7715
1517.3167 | 276.627 | 291.6443 | 284.7021
1518.3167 | 276.8949 | 291.4425 | 284.447
1519.3167 | 276.597 | 291.451 | 284.3545
1520.3167 | 276.7713 | 291.9052 | 284.6967
1521.3167 | 276.8225 | 291.742 | 284.6619
1522.3167 | 276.7444 | 291.9384 | 284.6743
1523.3167 | 277.4995 | 292.336 | 284.8367
1524.3167 | 278.0825 | 292.4554 | 285.3025
1525.3167 | 278.3152 | 291.865 | 284.9504
1526.3167 | 278.57 | 292.1354 | 284.6323
1527.3167 | 278.478 | 292.4335 | 284.6894
1528.3167 | 278.5542 | 292.4076 | 284.4244
1529.3167 | 278.9555 | 291.8507 | 285.0722
1530.3167 | 279.1301 | 291.1425 | 284.9001
1531.3167 | 279.4058 | 290.9564 | 284.5954
1532.3167 | 279.593 | 290.5039 | 284.514
1533.3167 | 279.7942 | 289.8433 | 284.0174
1534.3167 | 280.0909 | 289.2361 | 283.6808
1535.3167 | 280.4223 | 290.7063 | 284.1087
1536.3167 | 280.8962 | 291.7349 | 284.0365
1537.3167 | 281.2677 | 292.5201 | 284.2544
1538.3167 | 282.0442 | 293.1132 | 284.6772
1539.3167 | 281.569 | 293.0643 | 285.289
1540.3167 | 281.1982 | 293.2433 | 285.7586
1541.3167 | 281.5015 | 294.681 | 286.068
1542.3167 | 281.1869 | 294.6509 | 286.499
1543.3167 | 280.9421 | 294.7818 | 286.7203
1544.3167 | 280.5687 | 294.896 | 286.9684
1545.3167 | 280.5138 | 295.4082 | 287.0392
1546.3167 | 280.1091 | 295.6657 | 286.7578
1547.3167 | 280.1366 | 295.9932 | 286.7658
1548.3167 | 280.1293 | 295.8197 | 286.8286
1549.3167 | 280.7647 | 295.8422 | 286.5857
1550.3167 | 281.6318 | 295.5022 | 286.8304
1551.3167 | 281.8056 | 295.3249 | 286.7325
1552.3167 | 282.1919 | 295.3196 | 287.0693
1553.3167 | 282.3975 | 296.503 | 288.2088
1554.3167 | 282.1577 | 296.5459 | 288.8151
1555.3167 | 281.8757 | 296.4622 | 288.9074
1556.3167 | 281.2158 | 296.3665 | 288.704
1557.3167 | 280.9687 | 296.2311 | 288.9973
1558.3167 | 280.6815 | 296.2523 | 288.8802
1559.3167 | 280.1536 | 296.3058 | 288.8851
1560.3167 | 279.9044 | 296.3123 | 288.7103
1561.3167 | 279.473 | 296.3359 | 288.8606
1562.3167 | 279.6956 | 296.1707 | 288.7927
1563.3167 | 279.1689 | 296.2208 | 288.8422
1564.3167 | 279.1832 | 296.0882 | 288.7693
1565.3167 | 279.1942 | 295.7795 | 288.2186
1566.3167 | 278.9068 | 296.139 | 287.8262
1567.3167 | 278.8227 | 295.7938 | 287.6725
1568.3167 | 278.6442 | 295.9088 | 287.4797
1569.3167 | 278.86 | 295.3363 | 287.3614
1570.3167 | 278.3613 | 294.6418 | 287.1
1571.3167 | 278.0953 | 294.3697 | 287.7163
1572.3167 | 277.907 | 294.0399 | 287.7497
1573.3167 | 277.7196 | 293.8103 | 287.5887
1574.3167 | 277.356 | 293.8802 | 287.6673
1575.3167 | 278.2404 | 293.6956 | 287.752
1576.3167 | 278.5165 | 293.7075 | 287.6991
1577.3167 | 278.2505 | 293.739 | 287.5889
1578.3167 | 278.953 | 293.2794 | 287.2628
1579.3167 | 278.2056 | 293.4516 | 287.2882
1580.3167 | 278.188 | 293.3175 | 287.6844
1581.3167 | 278.3272 | 293.8208 | 287.3137
1582.3167 | 278.9174 | 293.3782 | 287.1559
1583.3167 | 279.6707 | 293.5758 | 287.0105
1584.3167 | 279.6955 | 294.0704 | 287.4427
1585.3167 | 280.2178 | 294.2403 | 287.485
1586.3167 | 280.8842 | 294.8982 | 287.6272
1587.3167 | 281.4095 | 294.8422 | 287.9506
1588.3167 | 281.7438 | 294.9212 | 287.7882
1589.3167 | 282.059 | 294.9445 | 288.2478
1590.3167 | 282.3938 | 295.1966 | 288.671
1591.3167 | 282.4237 | 295.4864 | 289.3317
1592.3167 | 282.3914 | 295.476 | 289.0549
1593.3167 | 282.5697 | 296.3982 | 289.3828
1594.3167 | 282.3413 | 296.1871 | 289.3793
1595.3167 | 282.8436 | 295.9416 | 289.4217
1596.3167 | 282.839 | 297.1119 | 289.5224
1597.3167 | 282.5524 | 297.0013 | 288.922
1598.3167 | 282.8651 | 297.438 | 288.7532
1599.3167 | 282.1798 | 297.7887 | 288.4963
1600.3167 | 282.4847 | 297.8 | 288.317
1601.3167 | 282.8501 | 297.7625 | 288.1084
1602.3167 | 281.5387 | 297.6221 | 287.7533
1603.3167 | 281.5137 | 297.8132 | 288.2249
1604.3167 | 281.4472 | 297.8714 | 288.4779
1605.3167 | 281.3586 | 298.385 | 288.8882
1606.3167 | 281.4961 | 298.4716 | 289.7957
1607.3167 | 281.3631 | 298.8575 | 289.9562
1608.3167 | 281.205 | 298.7909 | 290.2822
1609.3167 | 281.2211 | 298.9247 | 290.5278
1610.3167 | 281.0434 | 298.6367 | 290.9213
1611.3167 | 281.0168 | 298.3005 | 291.0385
1612.3167 | 280.7885 | 298.0401 | 290.6282
1613.3167 | 280.3882 | 297.6508 | 290.4016
1614.3167 | 280.1493 | 297.2948 | 290.291
1615.3167 | 279.8513 | 296.8051 | 289.8802
1616.3167 | 279.6996 | 296.4684 | 289.5137
1617.3167 | 279.471 | 296.0405 | 289.2261
1618.3167 | 279.1614 | 295.9887 | 289.0207
1619.3167 | 279.2993 | 295.9803 | 289.3721
1620.3167 | 279.072 | 296.208 | 289.6181
1621.3167 | 278.9497 | 296.0336 | 289.5975
1622.3167 | 278.8214 | 295.9602 | 289.6299
1623.3167 | 279.0256 | 296.0846 | 290.0515
1624.3167 | 278.9979 | 295.9361 | 290.3437
1625.3167 | 278.833 | 295.8585 | 290.1792
1626.3167 | 278.8577 | 295.9244 | 290.1912
1627.3167 | 279.122 | 295.7874 | 290.5196
1628.3167 | 279.0468 | 295.6936 | 290.3867
1629.3167 | 279.3969 | 295.8386 | 290.4375
1630.3167 | 280.4765 | 295.8489 | 290.3232
1631.3167 | 280.2717 | 296.1841 | 290.1633
1632.3167 | 280.5789 | 295.8912 | 291.0287
1633.3167 | 280.1777 | 295.5518 | 290.8574
1634.3167 | 279.9027 | 295.2873 | 290.586
1635.3167 | 279.6498 | 295.1078 | 290.1211
1636.3167 | 279.3296 | 294.9269 | 290.233
1637.3167 | 279.6831 | 294.6478 | 290.1276
1638.3167 | 280.2372 | 294.8228 | 289.6067
1639.3167 | 280.5156 | 296.1211 | 289.9364
1640.3167 | 281.082 | 296.3187 | 290.5659
1641.3167 | 281.5618 | 296.5408 | 290.5158
1642.3167 | 282.2322 | 296.6872 | 290.497
1643.3167 | 282.2078 | 296.7979 | 290.9127
1644.3167 | 282.8605 | 296.9685 | 291.2017
1645.3167 | 283.1722 | 296.7934 | 291.3079
1646.3167 | 283.7554 | 296.8455 | 291.3086
1647.3167 | 283.8488 | 297.2702 | 291.3725
1648.3167 | 283.5477 | 297.0319 | 291.5844
1649.3167 | 283.8026 | 296.8971 | 291.3576
1650.3167 | 283.9451 | 297.4848 | 291.7978
1651.3167 | 284.2976 | 297.2649 | 291.6938
1652.3167 | 284.0302 | 296.6535 | 291.2939
1653.3167 | 284.2556 | 296.7855 | 291.3069
1654.3167 | 284.3149 | 296.8723 | 291.0869
1655.3167 | 284.3688 | 296.8749 | 290.664
1656.3167 | 284.6216 | 297.1345 | 290.9106
1657.3167 | 284.919 | 297.3571 | 290.7507
1658.3167 | 284.9436 | 297.2785 | 290.301
1659.3167 | 285.115 | 297.2682 | 290.4081
1660.3167 | 285.4273 | 297.3726 | 290.6438
1661.3167 | 286.0341 | 297.3122 | 290.8693
1662.3167 | 286.3213 | 297.9065 | 291.0447
1663.3167 | 286.1716 | 297.9908 | 291.3112
1664.3167 | 286.0017 | 298.2877 | 291.5236
1665.3167 | 285.7987 | 298.6094 | 291.9864
1666.3167 | 285.9194 | 298.6545 | 292.2452
1667.3167 | 286.3006 | 298.7155 | 291.9164
1668.3167 | 286.5377 | 299.1775 | 291.3344
1669.3167 | 286.6911 | 299.3235 | 291.4204
1670.3167 | 287.0472 | 299.2797 | 291.477
1671.3167 | 287.1269 | 299.0497 | 291.4704
1672.3167 | 287.0225 | 299.2957 | 291.7076
1673.3167 | 287.1421 | 299.5995 | 291.5845
1674.3167 | 287.3163 | 299.7465 | 292.129
1675.3167 | 287.0317 | 300.1662 | 294.3043
1676.3167 | 286.9523 | 300.0524 | 294.5341
1677.3167 | 286.5674 | 300.5042 | 294.7024
1678.3167 | 286.1977 | 301.0881 | 294.6302
1679.3167 | 286.1022 | 301.4226 | 294.662
1680.3167 | 286.1531 | 301.4312 | 294.6241
1681.3167 | 286.5885 | 301.6837 | 294.6723
1682.3167 | 286.4696 | 301.8246 | 294.6133
1683.3167 | 286.1342 | 301.6195 | 294.3808
1684.3167 | 285.848 | 301.7538 | 294.5073
1685.3167 | 285.76 | 302.0577 | 294.3958
1686.3167 | 285.6232 | 302.2215 | 294.4388
1687.3167 | 285.2908 | 301.697 | 294.6119
1688.3167 | 285.6542 | 301.2826 | 294.5975
1689.3167 | 285.245 | 301.1028 | 294.313
1690.3167 | 285.1641 | 301.5464 | 294.9043
1691.3167 | 284.838 | 301.6271 | 295.6033
1692.3167 | 284.7363 | 301.4752 | 295.5302
1693.3167 | 284.9384 | 301.9125 | 295.0276
1694.3167 | 285.0156 | 301.8634 | 295.0054
1695.3167 | 285.0746 | 301.8542 | 294.9058
1696.3167 | 285.4216 | 301.4936 | 295.0228
1697.3167 | 285.5674 | 301.05 | 294.7882
1698.3167 | 285.9376 | 301.0818 | 294.4163
1699.3167 | 286.1358 | 301.1233 | 294.46
1700.3167 | 286.24 | 300.9736 | 294.4586
1701.3167 | 286.7693 | 301.6605 | 294.3634
1702.3167 | 286.8173 | 301.9656 | 294.8198
1703.3167 | 286.513 | 301.6753 | 294.8509
1704.3167 | 286.1849 | 301.6129 | 295.0844
1705.3167 | 286.2828 | 301.8701 | 294.9128
1706.3167 | 286.7866 | 302.0521 | 294.5357
1707.3167 | 287.2909 | 301.8471 | 294.5561
1708.3167 | 287.2608 | 301.2306 | 294.4514
1709.3167 | 287.189 | 300.946 | 294.71
1710.3167 | 287.6755 | 301.2986 | 294.4322
1711.3167 | 287.804 | 301.7334 | 293.994
1712.3167 | 288.3661 | 301.3752 | 293.7915
1713.3167 | 288.6668 | 301.1617 | 294.1385
1714.3167 | 289.1646 | 301.6407 | 294.1158
1715.3167 | 289.5799 | 301.5793 | 294.5626
1716.3167 | 290.0127 | 301.838 | 294.5007
1717.3167 | 290.9258 | 302.311 | 295.2882
1718.3167 | 291.4447 | 302.4201 | 295.0504
1719.3167 | 291.7793 | 302.5923 | 295.1615
1720.3167 | 291.9755 | 302.5461 | 295.6061
1721.3167 | 292.0099 | 302.562 | 295.7491
1722.3167 | 292.1769 | 302.9311 | 296.0363
1723.3167 | 292.624 | 303.5273 | 296.0935
1724.3167 | 293.0059 | 303.8003 | 296.6514
1725.3167 | 293.2282 | 304.2368 | 297.0301
1726.3167 | 294.6448 | 306.2473 | 297.7823
1727.3167 | 295.1976 | 306.8091 | 298.5454
1728.3167 | 295.9005 | 307.6739 | 299.6006
1729.3167 | 295.7176 | 308.1476 | 299.8393
1730.3167 | 295.6687 | 308.2212 | 300.3033
1731.3167 | 295.8715 | 309.6773 | 301.4551
1732.3167 | 296.1407 | 310.2408 | 302.0616
1733.3167 | 295.8202 | 310.8673 | 302.3629
1734.3167 | 295.7603 | 311.7866 | 302.6419
1735.3167 | 295.7264 | 312.0034 | 302.5962
1736.3167 | 296.2953 | 312.0153 | 302.8146
1737.3167 | 296.2079 | 313.102 | 303.188
1738.3167 | 296.0573 | 313.0771 | 303.2333
1739.3167 | 296.1092 | 314.1003 | 303.49
1740.3167 | 296.077 | 314.4438 | 303.6947
1741.3167 | 296.3185 | 314.3882 | 304.5818
1742.3167 | 296.132 | 314.8211 | 304.942
1743.3167 | 296.5288 | 315.7685 | 305.1822
1744.3167 | 296.9592 | 315.8721 | 305.2918
1745.3167 | 297.7987 | 315.8954 | 305.1813
1746.3167 | 298.5913 | 316.3028 | 305.8839
1747.3167 | 299.1325 | 316.2453 | 306.1433
1748.3167 | 299.368 | 316.0074 | 306.3149
1749.3167 | 299.6075 | 315.8713 | 306.9357
1750.3167 | 299.3852 | 315.9549 | 307.3288
1751.3167 | 300.1359 | 316.2724 | 308.0068
1752.3167 | 300.4249 | 317.2587 | 309.032
1753.3167 | 300.75 | 317.8788 | 309.3736
1754.3167 | 301.5901 | 318.0389 | 308.9732
1755.3167 | 301.9143 | 317.9094 | 308.7214
1756.3167 | 302.1327 | 317.5687 | 308.7427
1757.3167 | 302.1513 | 317.5612 | 309.1481
1758.3167 | 302.8687 | 317.7068 | 309.196
1759.3167 | 303.1967 | 318.0552 | 309.1726
1760.3167 | 303.2402 | 319.1443 | 309.0207
1761.3167 | 303.461 | 318.9652 | 309.4922
1762.3167 | 304.0766 | 318.9051 | 309.4465
1763.3167 | 303.9328 | 319.2446 | 309.8337
1764.3167 | 304.8763 | 319.4201 | 309.6002
1765.3167 | 305.1274 | 319.1976 | 310.2901
1766.3167 | 305.7718 | 319.465 | 311.1672
1767.3167 | 306.5891 | 319.432 | 310.823
1768.3167 | 306.6248 | 319.5985 | 310.8533
1769.3167 | 307.2119 | 320.4607 | 310.4002
1770.3167 | 307.5324 | 321.2916 | 310.6094
1771.3167 | 307.4763 | 321.1192 | 310.4973
1772.3167 | 307.6721 | 320.9503 | 310.3514
1773.3167 | 308.218 | 321.6769 | 310.7021
1774.3167 | 307.6688 | 321.683 | 311.3124
1775.3167 | 307.3801 | 321.5395 | 311.5968
1776.3167 | 306.8246 | 321.9587 | 311.7038
1777.3167 | 306.5927 | 322.0897 | 311.3527
1778.3167 | 306.2333 | 322.1485 | 311.317
1779.3167 | 306.8845 | 322.3874 | 311.4038
1780.3167 | 307.3213 | 322.6083 | 310.8246
1781.3167 | 307.8547 | 322.5313 | 311.4087
1782.3167 | 308.0545 | 322.7541 | 311.8227
1783.3167 | 307.9087 | 323.3727 | 312.5393
1784.3167 | 307.4962 | 323.7724 | 312.841
1785.3167 | 307.7437 | 324.9903 | 312.8896
1786.3167 | 308.2768 | 325.6102 | 313.2769
1787.3167 | 308.1808 | 326.5259 | 313.5695
1788.3167 | 308.3855 | 327.2018 | 313.4416
1789.3167 | 309.1032 | 326.7834 | 313.5156
1790.3167 | 308.7955 | 326.3795 | 313.4772
1791.3167 | 309.307 | 326.2055 | 312.9869
1792.3167 | 309.3644 | 326.8833 | 312.4529
1793.3167 | 309.8372 | 326.3278 | 312.1139
1794.3167 | 310.2594 | 326.0915 | 311.8148
1795.3167 | 310.8074 | 326.0591 | 312.4639
1796.3167 | 310.3577 | 326.3458 | 312.118
1797.3167 | 310.2351 | 325.8255 | 312.2398
1798.3167 | 310.0151 | 325.9579 | 312.2427
1799.3167 | 310.7888 | 326.0508 | 312.8836
1800.3167 | 310.8563 | 326.1475 | 313.3754
1801.3167 | 311.237 | 326.1949 | 313.2988
1802.3167 | 311.3977 | 326.0646 | 313.287
1803.3167 | 311.3524 | 325.8761 | 313.2974
1804.3167 | 311.794 | 326.1799 | 313.2952
1805.3167 | 312.7683 | 326.3792 | 313.4198
1806.3167 | 313.2559 | 326.6547 | 313.5091
1807.3167 | 312.8131 | 326.8237 | 313.7194
1808.3167 | 312.845 | 326.8674 | 314.3058
1809.3167 | 313.3458 | 327.0799 | 314.4657
1810.3167 | 313.4896 | 327.6967 | 314.2539
1811.3167 | 313.9892 | 328.0155 | 314.2866
1812.3167 | 315.1628 | 328.9317 | 314.478
1813.3167 | 315.3267 | 329.3109 | 314.5855
1814.3167 | 315.5809 | 331.3016 | 315.1093
1815.3167 | 315.9236 | 331.4858 | 315.1507
1816.3167 | 316.2171 | 331.5322 | 315.7297
1817.3167 | 316.7502 | 331.1621 | 315.8101
1818.3167 | 316.8728 | 331 | 316.1542
1819.3167 | 316.7317 | 330.9777 | 317.0848
1820.3167 | 316.2461 | 331.1512 | 317.1665
1821.3167 | 315.778 | 331.7001 | 318.1299
1822.3167 | 315.4369 | 331.4472 | 318.1215
1823.3167 | 315.2023 | 331.4782 | 319.44
1824.3167 | 314.9309 | 332.0181 | 319.4782
1825.3167 | 315.2629 | 333.2365 | 319.658
1826.3167 | 314.9483 | 333.4835 | 319.8402
1827.3167 | 315.1594 | 333.1978 | 319.5773
1828.3167 | 315.2517 | 333.0469 | 319.312
1829.3167 | 315.2061 | 332.4419 | 318.6071
1830.3167 | 315.0791 | 332.7428 | 318.4187
1831.3167 | 314.4889 | 332.6243 | 318.141
1832.3167 | 314.1804 | 332.6393 | 317.9435
1833.3167 | 314.0304 | 332.3502 | 317.7584
1834.3167 | 314.7887 | 332.5172 | 318.2783
1835.3167 | 315.6449 | 332.0886 | 318.0438
1836.3167 | 315.9206 | 332.6402 | 318.4522
1837.3167 | 315.7753 | 332.8305 | 318.8033
1838.3167 | 315.9236 | 332.9794 | 318.9393
1839.3167 | 316.4771 | 332.9864 | 319.4118
1840.3167 | 317.0564 | 333.5552 | 319.8693
1841.3167 | 317.898 | 333.8016 | 320.9575
1842.3167 | 318.3012 | 334.1267 | 321.4961
1843.3167 | 319.2077 | 335.8175 | 322.3825
1844.3167 | 319.614 | 337.4356 | 323.5529
1845.3167 | 320.1119 | 337.9254 | 323.5081
1848.4729 | 321.1733 | 338.2873 | 324.1912
1849.3167 | 321.4696 | 338.9276 | 324.6509
1850.3167 | 322.1557 | 338.7571 | 324.6112
1851.3167 | 322.428 | 338.9667 | 325.7042
1854.4729 | 321.6956 | 338.2897 | 325.4565
1855.3167 | 322.1878 | 338.9466 | 325.8519
1856.3167 | 322.1781 | 339.3634 | 326.2127
1860.4885 | 322.2479 | 343.0426 | 328.804
1861.3167 | 322.5801 | 343.3113 | 329.8415
1862.3167 | 322.5621 | 343.4948 | 330.0044
1863.3167 | 323.0719 | 344.1158 | 329.7513
1864.3167 | 323.1481 | 344.5464 | 329.4104
1865.3167 | 323.3627 | 344.3781 | 328.6364
1869.4729 | 325.62 | 342.8879 | 328.1281
1870.3167 | 325.8742 | 343.1399 | 328.5363
1871.3167 | 327.0243 | 343.5876 | 328.9581
1872.3167 | 327.4235 | 344.7031 | 329.3865
1873.3167 | 327.5592 | 345.388 | 330.3211
1874.3167 | 327.4075 | 345.229 | 332.014
1875.3167 | 327.2265 | 345.64 | 332.2163
1876.3167 | 327.5647 | 345.7734 | 331.7674
1877.3167 | 327.5672 | 344.8882 | 331.4567
1878.3167 | 327.9382 | 345.9926 | 331.7644
1879.3167 | 328.726 | 346.095 | 331.7512
1880.3167 | 328.9195 | 345.7856 | 331.6267
1881.3167 | 329.055 | 345.5597 | 331.2225
1882.3167 | 328.916 | 344.8222 | 330.8865
1883.3167 | 329.4393 | 344.1382 | 330.8318
1884.3167 | 329.2748 | 343.4654 | 330.4423
1885.3167 | 329.7373 | 344.4217 | 330.3342
1889.4729 | 329.9616 | 346.5929 | 333.1462
1890.3167 | 329.6032 | 346.5699 | 333.6212
1891.3167 | 329.3316 | 346.8778 | 334.2241
1895.4885 | 330.8095 | 347.5641 | 334.0383
1896.3167 | 331.1492 | 347.1319 | 333.762
1897.3167 | 331.9979 | 346.5196 | 333.8944
1898.3167 | 332.4564 | 346.9817 | 335.7422
1899.3167 | 332.7936 | 348.5703 | 336.3265
1900.3167 | 333.361 | 348.6828 | 336.858
1901.3167 | 333.6091 | 349.7476 | 336.6687
1902.3167 | 333.6027 | 350.6651 | 336.6422
1903.3167 | 334.1325 | 350.3267 | 336.652
1904.3167 | 334.1399 | 351.2192 | 336.0789
1905.3167 | 334.9694 | 352.2281 | 336.1992
1906.3167 | 334.9316 | 352.9988 | 336.2946
1907.3167 | 335.0593 | 353.2599 | 336.4144
1908.3167 | 335.1856 | 352.6234 | 336.1002
1909.3167 | 334.6359 | 352.1119 | 335.9486
1910.3167 | 334.9739 | 351.7613 | 335.83
1911.3167 | 335.1219 | 351.358 | 335.5875
1912.3167 | 335.2915 | 350.3753 | 334.6817
1913.3167 | 335.2146 | 350.3897 | 335.1829
1914.3167 | 335.8419 | 349.957 | 335.5175
1915.3167 | 336.3019 | 350.9403 | 335.5074
1916.3167 | 336.7134 | 351.2288 | 335.9856
1917.3167 | 336.5366 | 351.07 | 336.2134
1918.3167 | 337.1455 | 351.1965 | 336.1396
1919.3167 | 337.6883 | 352.0103 | 336.3212
1920.3167 | 338.0831 | 352.289 | 336.5773
1921.3167 | 338.9003 | 351.6808 | 336.4595
1922.3167 | 339.203 | 351.5184 | 336.4568
1923.3167 | 339.1731 | 351.685 | 336.2971
1924.3167 | 338.9997 | 351.1581 | 336.2866
1925.3167 | 338.9281 | 351.0469 | 336.1357
1926.3167 | 339.3031 | 351.0605 | 336.3359
1927.3167 | 339.644 | 350.8487 | 336.5947
1928.3167 | 340.1214 | 350.252 | 336.4691
1929.3167 | 340.2982 | 349.9536 | 337.3682
1930.3167 | 340.6346 | 350.3989 | 337.7304
1931.3167 | 340.7365 | 350.4162 | 337.9744
1932.3167 | 341.3527 | 351.1112 | 338.3534
1933.3167 | 341.5146 | 351.0971 | 338.2634
1934.3167 | 342.314 | 351.1801 | 338.0791
1935.3167 | 343.1228 | 351.3298 | 337.5352
1936.3167 | 342.8428 | 351.5678 | 337.7773
1937.3167 | 342.4423 | 351.7813 | 337.6556
1938.3167 | 342.5283 | 352.3458 | 337.6488
1939.3167 | 342.19 | 352.5619 | 338.0766
1940.3167 | 342.569 | 352.193 | 338.2325
1941.3167 | 342.337 | 352.0906 | 338.385
1942.3167 | 342.0453 | 352.1444 | 338.5947
1943.3167 | 341.8832 | 352.5608 | 338.5318
1944.3167 | 342.0418 | 352.5011 | 338.7973
1945.3167 | 341.9039 | 353.7587 | 339.6502
1946.3167 | 342.1916 | 355.2628 | 340.8763
1947.3167 | 342.3462 | 356.0867 | 342.0045
1948.3167 | 342.2474 | 356.5439 | 342.2762
1949.3167 | 342.6086 | 357.2416 | 342.5332
1950.3167 | 342.1913 | 357.3137 | 342.7605
1951.3167 | 342.0518 | 356.9654 | 342.5269
1952.3167 | 343.0126 | 356.7318 | 342.124
1953.3167 | 343.2893 | 355.9785 | 341.5639
1954.3167 | 343.5639 | 355.5977 | 341.8536
1955.3167 | 344.0545 | 355.6076 | 341.7235
1956.3167 | 344.8359 | 356.0468 | 342.4043
1957.3167 | 345.0043 | 357.0022 | 342.805
1958.3167 | 345.2635 | 358.3471 | 343.5342
1959.3167 | 344.7558 | 359.0273 | 343.9599
1960.3167 | 345.0671 | 359.7691 | 344.7409
1961.3167 | 345.081 | 360.6402 | 344.7297
1962.3167 | 345.5797 | 360.2368 | 344.6194
1963.3167 | 345.6392 | 359.9618 | 343.9581
1964.3167 | 346.3227 | 359.6711 | 343.826
1965.3167 | 346.3116 | 359.3988 | 343.217
1966.3167 | 346.5743 | 359.3526 | 342.9944
1967.3167 | 346.825 | 359.4191 | 343.0581
1968.3167 | 346.7149 | 359.1087 | 343.6583
1969.3167 | 347.1584 | 359.1499 | 343.7629
1970.3167 | 347.7472 | 359.3733 | 344.1172
1971.3167 | 348.9057 | 359.3327 | 343.9215
1972.3167 | 349.1666 | 360.6109 | 344.3764
1973.3167 | 349.1164 | 360.739 | 344.9959
1974.3167 | 348.819 | 360.9154 | 345.2759
1975.3167 | 349.5352 | 360.871 | 345.6556
1976.3167 | 349.6564 | 360.4656 | 345.1887
1977.3167 | 349.7167 | 360.2708 | 345.7153
1978.3167 | 350.3326 | 360.7432 | 345.6671
1979.3167 | 350.6795 | 361.0282 | 346.3335
1980.3167 | 350.9083 | 361.6077 | 346.4336
1981.3167 | 350.9876 | 361.9541 | 346.8056
1982.3167 | 350.9131 | 361.9082 | 346.4842
1983.3167 | 351.0938 | 362.7757 | 347.5118
1984.3167 | 351.81 | 362.5439 | 348.093
1985.3167 | 352.0273 | 362.5965 | 348.5351
1986.3167 | 352.4607 | 362.5442 | 348.2937
1987.3167 | 352.4517 | 362.7257 | 348.224
1988.3167 | 352.787 | 362.9688 | 347.9253
1989.3167 | 352.9592 | 363.4227 | 347.8644
1990.3167 | 353.1859 | 363.8596 | 348.1676
1991.3167 | 353.1924 | 363.6404 | 348.045
1992.3167 | 353.0989 | 363.9064 | 348.4367
1993.3167 | 352.8799 | 364.0776 | 348.474
1994.3167 | 353.4927 | 364.157 | 348.7063
1995.3167 | 353.3026 | 364.9088 | 349.149
1996.3167 | 353.6547 | 365.1869 | 349.3186
1997.3167 | 353.7747 | 365.4829 | 349.5848
1998.3167 | 353.8094 | 365.5106 | 349.564
1999.3167 | 353.6496 | 365.9353 | 349.4142
2000.3167 | 354.2595 | 365.8746 | 349.5263
2001.3167 | 354.0202 | 366.1602 | 349.6751
2002.3167 | 354.1754 | 367.3304 | 349.5644
2003.3167 | 354.7149 | 367.0156 | 349.9033
2004.3167 | 354.8486 | 366.3742 | 350.1771
2005.3167 | 355.0936 | 366.7125 | 350.8266
2006.3167 | 355.7399 | 366.8069 | 351.389
2007.3167 | 355.0458 | 367.4749 | 352.2506
2008.3167 | 355.2371 | 368.2321 | 352.2192
2009.3167 | 354.9542 | 368.1593 | 351.9838
2010.3167 | 355.4853 | 367.8934 | 352.1105
2011.3167 | 354.8675 | 367.8637 | 352.2453
2012.3167 | 355.9071 | 368.7319 | 352.134
2013.3167 | 355.8967 | 368.5431 | 352.2854
2014.3167 | 356.272 | 369.3456 | 352.6551
2015.3167 | 356.8187 | 368.9474 | 352.4293
2016.3167 | 357.29 | 368.7004 | 352.1386
2017.3167 | 357.8901 | 368.4659 | 351.9768
2018.3167 | 358.0254 | 369.5163 | 351.9335
2019.3167 | 358.4427 | 369.924 | 351.7656
2020.3167 | 358.8101 | 369.6542 | 351.5452
2021.3167 | 358.9304 | 369.4819 | 351.7679
2022.3167 | 358.8886 | 369.1316 | 352.6429
2023.3167 | 358.5747 | 368.7036 | 353.304
2024.3167 | 359.4351 | 369.1875 | 353.4543
2025.3167 | 360.1178 | 368.9554 | 353.4973
2026.3167 | 360.416 | 369.2642 | 354.0509
2027.3167 | 360.1628 | 369.6143 | 354.5648
2028.3167 | 360.9348 | 370.2707 | 355.2709
2029.3167 | 361.1324 | 370.4396 | 355.6697
2030.3167 | 361.6793 | 370.1885 | 355.5868
2031.3167 | 361.8695 | 370.6966 | 355.713
2032.3167 | 362.1779 | 371.1342 | 355.893
2033.3167 | 362.2202 | 370.9074 | 355.8391
2034.3167 | 362.6522 | 370.6744 | 356.2631
2035.3167 | 362.7914 | 370.7288 | 355.875
2036.3167 | 362.7453 | 370.6682 | 355.8007
2037.3167 | 363.3977 | 371.0421 | 355.3346
2038.3167 | 363.5148 | 371.1248 | 354.8881
2039.3167 | 363.7211 | 371.6994 | 355.0187
2040.3167 | 363.9205 | 371.8887 | 355.3051
2041.3167 | 364.0152 | 372.2731 | 355.3758
2042.3167 | 364.1869 | 372.4854 | 355.3322
2043.3167 | 364.3678 | 372.9819 | 355.6341
2044.3167 | 364.5114 | 373.0223 | 355.5062
2045.3167 | 364.5715 | 373.4469 | 355.8752
2046.3167 | 364.7083 | 373.4439 | 355.6303
2047.3167 | 364.7675 | 373.4824 | 355.6125
2048.3167 | 364.8838 | 373.4547 | 355.8739
2049.3167 | 365.5265 | 373.6134 | 355.9927
2050.3167 | 365.6612 | 374.3403 | 357.2707
2051.3167 | 365.6043 | 374.2651 | 357.932
2052.3167 | 365.6556 | 374.5045 | 357.5065
2053.3167 | 365.9874 | 375.5494 | 357.6094
2054.3167 | 365.9843 | 375.2742 | 357.3192
2055.3167 | 365.7951 | 374.9802 | 357.4111
2056.3167 | 366.1905 | 375.1686 | 358.173
2057.3167 | 366.4804 | 375.2663 | 357.9059
2058.3167 | 366.7991 | 375.3861 | 358.9701
2059.3167 | 366.5638 | 375.7756 | 359.3909
2060.3167 | 366.2791 | 375.7408 | 359.5174
2061.3167 | 366.4045 | 375.6059 | 359.3679
2062.3167 | 366.5813 | 375.5286 | 358.8008
2063.3167 | 366.2026 | 376.5313 | 358.4907
2064.3167 | 366.4432 | 376.2937 | 359.29
2065.3167 | 366.7425 | 376.4829 | 358.9871
2066.3167 | 366.4882 | 376.5407 | 358.7701
2067.3167 | 366.2937 | 376.8415 | 359.2438
2068.3167 | 366.0145 | 377.7105 | 359.4373
2069.3167 | 366.5628 | 378.6327 | 359.5742
2070.3167 | 367.0577 | 378.914 | 360.1863
2071.3167 | 366.9655 | 380.0857 | 361.3285
2072.3167 | 366.5428 | 380.6465 | 362.3931
2073.3167 | 366.6198 | 380.5024 | 362.5617
2074.3167 | 366.884 | 380.9126 | 362.7557
2075.3167 | 366.8698 | 381.0525 | 362.6513
2076.3167 | 366.7807 | 381.1391 | 363.3611
2077.3167 | 366.7002 | 381.3645 | 363.3195
2078.3167 | 366.7771 | 381.0004 | 363.1341
2079.3167 | 367.0613 | 381.0014 | 362.7696
2080.3167 | 367.5974 | 380.5304 | 362.4705
2081.3167 | 367.9527 | 381.2255 | 362.5605
2082.3167 | 367.9002 | 381.274 | 362.9913
2083.3167 | 367.9713 | 380.7613 | 363.1156
2084.3167 | 368.6204 | 381.0675 | 363.452
2085.3167 | 368.66 | 381.1411 | 363.8972
2086.3167 | 369.3612 | 381.2437 | 364.3451
2087.3167 | 369.9521 | 381.7608 | 365.0937
2088.801 | 369.7822 | 380.7507 | 365.3672
2089.3792 | 370.1174 | 380.5137 | 365.4983
2090.3948 | 371.1642 | 380.2314 | 365.3978
2091.426 | 371.7629 | 380.5347 | 365.1223
2092.4104 | 372.3443 | 381.0012 | 365.2368
2093.3167 | 372.0831 | 381.6408 | 365.4659
2095.1604 | 372.1969 | 381.6506 | 365.4053
2095.6448 | 372.2885 | 382.2329 | 365.5122
2096.3167 | 372.3365 | 382.4654 | 365.8113
2097.3167 | 372.3038 | 382.4986 | 366.0491
2098.3167 | 371.8545 | 382.2116 | 366.1515
2099.3167 | 372.1363 | 381.8861 | 366.4134
2100.3167 | 372.4939 | 382.2449 | 367.1241
2101.3167 | 372.7117 | 382.7623 | 366.93
2102.3167 | 372.9151 | 383.2769 | 367.493
2103.3167 | 372.9731 | 383.4884 | 368.0191
2104.3167 | 373.504 | 383.5819 | 368.4534
2105.3167 | 373.2566 | 383.6667 | 368.7976
2106.3167 | 373.2124 | 383.4606 | 368.6517
2107.3167 | 373.2933 | 383.8988 | 368.6091
2108.3167 | 373.6702 | 384.3323 | 368.5871
2109.3167 | 374.0933 | 385.0692 | 368.865
2110.3167 | 375.0099 | 385.5619 | 368.9981
2111.3167 | 375.8732 | 385.4953 | 369.4001
2112.3167 | 375.7826 | 385.8331 | 369.6497
2113.3167 | 376.164 | 385.8712 | 369.541
2114.3167 | 376.0798 | 386.3071 | 371.1873
2115.3167 | 376.4672 | 386.7427 | 371.3915
2116.3167 | 376.4886 | 387.9969 | 371.5624
2117.3167 | 376.3816 | 388.7644 | 372.654
2118.3167 | 377.1048 | 389.0603 | 372.7402
2119.3167 | 377.124 | 388.9219 | 373.1825
2120.3167 | 377.4417 | 388.963 | 373.7287
2121.3167 | 377.8311 | 389.4956 | 374.4934
2122.3167 | 378.1673 | 390.0438 | 374.2067
2123.3167 | 378.5537 | 389.5782 | 374.4355
2124.3167 | 378.3959 | 389.7781 | 374.8409
2125.3167 | 379.0311 | 389.6986 | 374.9627
2126.3323 | 380.1742 | 389.9678 | 375.5969
2127.3167 | 380.5689 | 390.8264 | 375.483
2128.3323 | 380.8859 | 391.6089 | 375.8896
2129.3167 | 380.9379 | 392.0042 | 375.7052
2130.3167 | 381.4967 | 392.0262 | 375.6226
2131.3167 | 381.4091 | 392.7134 | 376.543
2132.3323 | 381.0621 | 392.7753 | 376.1955
2133.3167 | 380.8286 | 392.4931 | 376.2072
2134.3167 | 380.5576 | 392.5605 | 376.4825
2135.3167 | 380.4502 | 392.1513 | 376.2753
2136.3167 | 380.8845 | 392.3509 | 376.2039
2137.3167 | 380.9573 | 392.5338 | 376.2929
2138.3167 | 381.3301 | 392.7029 | 376.8265
2139.3167 | 381.585 | 392.5238 | 376.955
2140.3167 | 381.9442 | 392.3154 | 377.1513
2141.3167 | 381.4629 | 392.0864 | 377.1778
2142.3167 | 382.0635 | 391.7034 | 377.1411
2143.3167 | 382.3847 | 391.7082 | 377.2219
2144.3167 | 382.6995 | 391.7025 | 376.745
2145.3167 | 382.6198 | 391.6784 | 377.0501
2146.3167 | 382.6942 | 391.8043 | 377.1742
2147.3167 | 383.3471 | 392.9264 | 376.8034
2148.3167 | 384.0255 | 393.6763 | 376.8643
2149.3167 | 385.2809 | 393.1861 | 376.8114
2150.3167 | 385.5621 | 392.9871 | 377.0609
2151.3167 | 385.255 | 392.9395 | 377.1131
2152.3167 | 385.4169 | 393.1581 | 377.2048
2153.3167 | 385.8377 | 393.961 | 377.0442
2154.3167 | 385.4141 | 393.1841 | 377.0429
2155.3167 | 385.8457 | 393.1819 | 376.6792
2156.3167 | 385.7364 | 394.5155 | 376.4843
2157.3167 | 385.7095 | 394.4504 | 376.5494
2158.3167 | 385.5627 | 393.9339 | 376.8898
2159.3167 | 386.1709 | 394.4757 | 377.4328
2160.3167 | 386.4144 | 394.8131 | 377.8722
2161.3167 | 386.5067 | 395.5977 | 379.193
2162.3479 | 387.063 | 396.0174 | 379.3601
2163.3167 | 386.9959 | 396.3079 | 379.2088
2164.3167 | 386.8802 | 396.0619 | 379.7708
2165.3167 | 386.9443 | 395.7594 | 379.6865
2166.3323 | 386.8198 | 395.5962 | 379.4927
2167.3167 | 386.8193 | 395.8383 | 379.4891
2168.3167 | 386.6313 | 396.3482 | 379.6806
2169.3167 | 386.8167 | 396.5269 | 379.7621
2170.3167 | 386.6792 | 396.0313 | 379.8652
2171.3167 | 386.5675 | 395.8671 | 380.0675
2172.3167 | 386.3956 | 395.6387 | 379.6886
2173.3167 | 386.2561 | 395.2693 | 380.307
2174.3167 | 386.1543 | 395.8718 | 379.9812
2175.3167 | 385.823 | 395.4722 | 380.2358
2176.3167 | 386.4494 | 395.3854 | 380.7701
2177.3167 | 386.448 | 395.5337 | 381.3442
2178.3167 | 386.2297 | 394.9863 | 381.3473
2179.3167 | 386.0463 | 394.9563 | 381.5973
2180.3167 | 385.9524 | 395.2992 | 381.879
2181.3167 | 385.9788 | 395.3616 | 381.7426
2182.3167 | 386.3347 | 395.1549 | 381.7271
2183.3167 | 386.01 | 394.8262 | 381.6297
2184.3167 | 385.8782 | 395.3371 | 381.3839
2185.3167 | 386.0141 | 395.0182 | 380.9843
2186.3167 | 386.9646 | 394.7686 | 380.6725
2187.3167 | 387.2984 | 394.7335 | 380.5107
2188.3167 | 387.2347 | 394.4333 | 380.6615
2189.3167 | 387.7624 | 394.7226 | 380.8984
2190.3167 | 388.0469 | 394.5781 | 380.6346
2191.3167 | 388.8371 | 394.3052 | 380.7589
2192.3167 | 388.7417 | 394.2331 | 380.7487
2193.3167 | 388.644 | 394.0866 | 380.7066
2194.3167 | 388.886 | 395.1587 | 381.095
2195.3167 | 388.7683 | 395.5556 | 381.3375
2196.3167 | 388.5201 | 395.9443 | 381.5573
2197.3167 | 388.1772 | 395.6725 | 381.3343
2198.3167 | 388.3337 | 395.8824 | 381.3218
2199.3167 | 388.6035 | 395.5831 | 381.1044
2200.3167 | 388.6464 | 395.6158 | 380.9092
2201.3167 | 388.7964 | 396.1615 | 380.7728
2202.3167 | 389.1048 | 396.2703 | 380.7908
2203.3167 | 389.4658 | 396.5206 | 381.0916
2204.3167 | 389.5909 | 396.7278 | 381.5072
2205.3167 | 389.4463 | 396.2264 | 381.6403
2206.3167 | 389.5744 | 397.3342 | 381.7518
2207.3167 | 389.6376 | 397.3254 | 382.2725
2208.3167 | 389.7505 | 398.2736 | 382.7115
2209.3167 | 390.3134 | 398.5914 | 383.7532
2210.3167 | 391.1971 | 399.2567 | 384.0676
2211.3167 | 391.2866 | 399.5415 | 384.5985
2212.3167 | 391.2441 | 400.8718 | 385.0097
2213.3167 | 391.4123 | 400.445 | 385.7108
2214.3167 | 391.4534 | 400.4545 | 385.6576
2215.3167 | 391.9301 | 399.8826 | 385.396
2216.3167 | 392.0967 | 400.1712 | 385.4597
2217.3167 | 392.7403 | 400.9719 | 385.17
2218.3167 | 393.4106 | 400.9837 | 385.491
2219.3167 | 393.6868 | 401.1973 | 385.4698
2220.3167 | 394.8724 | 401.61 | 385.2616
2221.3167 | 395.2867 | 401.856 | 385.3493
2222.3323 | 395.5295 | 401.7224 | 385.1723
2223.3167 | 395.4214 | 401.6527 | 386.2062
2224.3167 | 396.1792 | 401.6747 | 386.1489
2225.3167 | 396.0164 | 401.9247 | 387.2826
2226.3167 | 395.8725 | 401.6764 | 387.4195
2227.3167 | 396.2386 | 401.8636 | 388.0359
2228.3167 | 396.4315 | 402.5556 | 388.0562
2229.3167 | 397.0556 | 402.6256 | 387.5856
2230.3167 | 397.1971 | 402.5567 | 387.4526
2231.3167 | 397.1963 | 402.7799 | 387.6331
2232.3167 | 397.7216 | 402.8766 | 387.728
2233.3167 | 397.0731 | 403.1876 | 387.2381
2234.3167 | 396.6583 | 403.8867 | 387.3598
2235.3167 | 396.5391 | 403.6623 | 387.2419
2236.3167 | 396.5984 | 403.3654 | 387.3549
2237.3167 | 396.66 | 403.2121 | 387.6267
2238.3167 | 396.6327 | 404.4916 | 387.6727
2239.3167 | 396.7997 | 404.5766 | 387.424
2240.3167 | 397.1395 | 403.8632 | 387.3741
2241.3167 | 397.5062 | 403.167 | 387.5912
2242.3167 | 397.7523 | 403.239 | 387.6639
2243.3167 | 397.8013 | 404.2484 | 387.7537
2244.3167 | 398.0438 | 404.2901 | 387.5852
2245.3167 | 398.5327 | 404.7675 | 387.547
2246.3167 | 399.1421 | 405.2003 | 387.0876
2247.3167 | 398.8953 | 405.1549 | 386.7428
2248.3167 | 399.3317 | 405.1004 | 386.9165
2249.3167 | 399.2717 | 405.0395 | 387.0185
2250.3167 | 399.6532 | 404.5547 | 386.6909
2251.3167 | 399.62 | 404.8489 | 386.7703
2252.3167 | 399.2906 | 405.162 | 386.8726
2253.3167 | 399.3737 | 406.0277 | 387.4288
2254.3167 | 399.1431 | 406.5748 | 387.6133
2255.3167 | 399.3883 | 407.3404 | 387.9112
2256.3167 | 399.402 | 407.3839 | 388.0367
2257.3167 | 399.7127 | 407.801 | 388.5339
2258.3167 | 399.6831 | 407.1973 | 388.4391
2259.3167 | 399.8319 | 406.6936 | 388.4473
2260.3167 | 399.9072 | 407.3813 | 388.6286
2261.3167 | 400.1813 | 406.9793 | 388.4667
2262.3167 | 399.698 | 407.0847 | 388.2064
2263.3167 | 399.3396 | 406.5131 | 388.5055
2264.3167 | 399.0776 | 405.7878 | 388.5671
2265.3167 | 399.2282 | 405.7578 | 388.4334
2266.3167 | 399.7628 | 405.9403 | 388.2358
2267.3167 | 400.1895 | 405.2736 | 388.0492
2268.3167 | 400.3119 | 405.571 | 388.0909
2269.3167 | 400.2006 | 405.3108 | 387.7847
2270.3167 | 399.9536 | 405.7985 | 387.8664
2271.3167 | 400.1676 | 405.5826 | 387.5525
2272.3167 | 399.9292 | 405.8673 | 387.5462
2273.3167 | 400.316 | 405.4664 | 387.851
2274.3167 | 400.1665 | 405.5995 | 387.7069
2275.3167 | 400.5205 | 405.5264 | 387.5439
2276.3167 | 400.6647 | 406.4612 | 388.2487
2277.3167 | 400.6808 | 406.3783 | 388.2476
2278.3167 | 401.4491 | 407.1646 | 388.5075
2279.3167 | 401.7443 | 407.3362 | 388.5716
2280.3167 | 401.6475 | 408.0217 | 388.468
2281.3167 | 401.8869 | 408.1861 | 388.2689
2282.3167 | 401.7623 | 407.7852 | 389.0398
2283.3167 | 401.3184 | 407.8891 | 389.9544
2284.3167 | 401.5613 | 407.8709 | 390.3584
2285.3167 | 401.5462 | 408.2401 | 391.2427
2286.3167 | 401.9551 | 410.5165 | 392.4912
2287.3167 | 402.7751 | 412.9426 | 393.727
2288.3167 | 403.8743 | 414.647 | 395.4887
2289.3167 | 404.7559 | 414.4788 | 396.2959
2290.3167 | 405.1761 | 415.0452 | 396.8677
2291.3167 | 405.2802 | 415.8519 | 396.9362
2292.3167 | 405.2324 | 415.4873 | 397.0762
2293.3167 | 405.3439 | 415.5257 | 397.0872
2294.3167 | 406.2648 | 416.0892 | 397.1077
2295.3167 | 406.9645 | 416.9019 | 397.4877
2296.3167 | 407.7993 | 418.9547 | 398.0269
2297.3167 | 408.6455 | 419.3926 | 399.0936
2298.3167 | 409.5364 | 420.3094 | 399.5662
2299.3167 | 409.5337 | 420.1044 | 399.6874
2300.3167 | 410.2371 | 420.4362 | 399.8237
2301.3167 | 411.287 | 420.8276 | 400.1439
2302.3167 | 411.3162 | 421.6047 | 400.7431
2303.3167 | 411.4863 | 421.168 | 401.1296
2304.3167 | 411.9626 | 421.2584 | 401.403
2305.3167 | 412.1798 | 422.1375 | 401.7023
2306.3167 | 412.5071 | 422.8249 | 401.9324
2307.3167 | 413.1361 | 423.0348 | 402.312
2308.3167 | 413.7419 | 423.2046 | 402.4071
2309.3167 | 413.5477 | 423.0304 | 402.777
2310.3167 | 414.4509 | 423.386 | 403.4599
2311.3167 | 414.5206 | 423.778 | 403.7695
2312.3167 | 414.8983 | 424.3977 | 404.2881
2313.3167 | 415.4816 | 424.1661 | 404.396
2314.3167 | 416.0895 | 423.9181 | 404.7235
2315.3167 | 416.0847 | 424.1323 | 404.6729
2316.3167 | 415.9073 | 423.9419 | 404.5503
2317.3167 | 416.1213 | 423.5129 | 404.4731
2318.3167 | 416.2139 | 424.3721 | 404.5907
2319.3167 | 416.3758 | 424.4424 | 404.7039
2320.3167 | 416.9411 | 425.0403 | 405.3365
2321.3167 | 417.0213 | 425.197 | 405.5999
2322.3167 | 417.295 | 426.0081 | 406.9991
2323.3167 | 417.5679 | 426.4971 | 407.9099
2324.3167 | 417.9091 | 427.1042 | 407.7645
2325.3167 | 418.1865 | 427.2671 | 407.6201
2326.3167 | 418.6622 | 428.0377 | 408.7881
2327.3167 | 418.5722 | 428.1676 | 409.0895
2328.3167 | 419.4028 | 429.1602 | 409.1777
2329.3167 | 419.3032 | 429.0257 | 409.1978
2330.3167 | 419.371 | 429.2436 | 410.151
2331.3167 | 419.4098 | 429.301 | 411.0702
2332.3167 | 419.0357 | 430.6196 | 412.1046
2333.3167 | 418.4955 | 431.0603 | 412.0421
2334.3167 | 418.4196 | 430.7539 | 412.1139
2335.3167 | 418.5138 | 430.2304 | 412.6613
2336.3167 | 418.927 | 430.1089 | 412.675
2337.3167 | 418.9922 | 430.9252 | 412.6101
2338.3167 | 418.7001 | 430.8725 | 412.5636
2339.3167 | 418.4336 | 430.2188 | 412.6538
2340.3167 | 419.2105 | 430.713 | 413.0001
2341.3167 | 419.5239 | 430.8523 | 412.8878
2342.3167 | 419.886 | 430.6669 | 413.1757
2343.3167 | 420.256 | 431.4243 | 413.3131
2344.3167 | 421.3369 | 431.7912 | 413.665
2345.3167 | 421.4519 | 431.8385 | 415.0252
2346.3167 | 421.4604 | 432.5957 | 416.3707
2347.3167 | 421.4994 | 433.9192 | 417.5665
2348.3167 | 421.9491 | 434.3536 | 418.5761
2349.3167 | 422.6968 | 436.2786 | 419.8007
2350.3167 | 422.4658 | 435.9297 | 419.9519
2351.3167 | 422.8774 | 436.1805 | 420.1029
2352.3167 | 423.4526 | 436.2486 | 420.4867
2353.3167 | 423.809 | 436.5319 | 420.9928
2354.3167 | 424.7973 | 437.0489 | 421.7049
2355.3167 | 424.6434 | 437.9519 | 422.1627
2356.3167 | 424.4348 | 438.5485 | 423.0389
2357.3167 | 424.9745 | 438.5372 | 423.3284
2358.3167 | 425.2841 | 438.5003 | 423.0679
2359.3167 | 424.752 | 438.5459 | 422.8412
2360.3167 | 425.7879 | 439.1579 | 422.6881
2361.3167 | 425.8748 | 440.1612 | 423.094
2362.3167 | 425.6802 | 440.8473 | 423.7445
2363.3167 | 425.743 | 440.3289 | 423.4417
2364.3167 | 426.2673 | 439.8984 | 423.376
2365.3167 | 426.483 | 440.7476 | 424.1278
2366.3167 | 426.9352 | 442.52 | 424.7947
2367.3167 | 427.0293 | 442.3459 | 425.3646
2368.3167 | 427.7557 | 442.2887 | 425.6102
2369.3167 | 428.2535 | 441.9837 | 426.0888
2370.3167 | 428.6238 | 442.5412 | 426.6321
2371.3167 | 428.9612 | 443.6632 | 426.6402
2372.3167 | 429.3116 | 445.8113 | 427.3509
2373.3167 | 429.2174 | 444.9657 | 427.4013
2374.3167 | 429.7879 | 445.4428 | 427.513
2375.3167 | 430.0861 | 445.9925 | 427.9355
2376.3167 | 431.0045 | 446.3394 | 428.7042
2377.3167 | 431.3323 | 446.5908 | 428.978
2378.3167 | 431.736 | 446.4818 | 429.5412
2379.3167 | 432.0668 | 447.0305 | 429.5437
2380.3167 | 432.1978 | 447.2855 | 429.5887
2381.3167 | 432.2066 | 446.9437 | 429.5951
2382.3167 | 432.3158 | 447.0389 | 429.6348
2383.3167 | 432.7508 | 446.416 | 430.1952
2384.3167 | 433.0766 | 446.046 | 430.5688
2385.3167 | 433.3551 | 446.3057 | 430.1853
2386.3167 | 433.7254 | 446.1573 | 430.7024
2387.3167 | 434.1422 | 446.0298 | 430.5757
2388.3167 | 434.3448 | 446.2243 | 431.1417
2389.3167 | 434.0451 | 446.5419 | 431.4944
2390.3167 | 434.1283 | 447.0911 | 431.1008
2391.3167 | 434.2575 | 447.3998 | 431.0467
2392.3167 | 433.9661 | 447.0456 | 431.4255
2393.3167 | 433.8516 | 447.8539 | 431.7226
2394.3167 | 433.6929 | 448.6908 | 431.594
2395.3167 | 434.2781 | 448.2328 | 432.3457
2396.3167 | 434.6289 | 448.8765 | 432.8008
2397.3167 | 434.8101 | 448.5861 | 434.5301
2398.3167 | 434.7766 | 450.1937 | 434.9547
2399.3167 | 434.6673 | 450.2826 | 436.2557
2400.3167 | 434.7061 | 450.4244 | 436.7366
2401.3167 | 434.2679 | 451.3164 | 436.7858
2402.3167 | 434.6147 | 451.8782 | 436.2285
2403.3167 | 434.5289 | 450.5172 | 436.0911
2404.3167 | 435.2358 | 451.0777 | 436.4303
2405.3167 | 434.9723 | 451.4651 | 436.7055
2406.3167 | 434.8559 | 451.3343 | 436.9407
2407.3167 | 434.8323 | 450.3566 | 436.9613
2408.3167 | 434.4034 | 450.5253 | 436.882
2409.3167 | 434.4823 | 451.7944 | 436.6799
2410.3167 | 434.761 | 450.6998 | 437.0991
2411.3167 | 435.004 | 450.8461 | 437.2089
2412.3167 | 434.9537 | 450.7824 | 437.4668
2413.3167 | 434.9859 | 452.5204 | 438.4059
2414.3167 | 435.5203 | 453.2572 | 438.3393
2415.3167 | 435.9114 | 452.4089 | 438.5926
2416.3167 | 436.3315 | 453.6124 | 439.6878
2417.3167 | 436.971 | 454.2171 | 439.7766
2418.3167 | 436.8717 | 454.5994 | 440.0504
2419.3167 | 437.3916 | 454.9544 | 440.4773
2420.3167 | 437.9012 | 455.9865 | 440.9631
2421.3167 | 437.7626 | 458.617 | 441.8101
2422.3167 | 437.6543 | 458.9351 | 441.7535
2423.3167 | 437.3223 | 459.1676 | 442.2128
2424.3167 | 437.0339 | 460.9372 | 442.7414
2425.3167 | 437.1715 | 462.2633 | 443.8721
2426.3167 | 436.8307 | 463.7264 | 444.9377
2427.3167 | 436.4939 | 464.122 | 444.8145
2428.3167 | 436.6073 | 465.0192 | 445.2862
2429.3167 | 437.1762 | 465.1386 | 445.4686
2430.3167 | 437.1285 | 465.4323 | 446.1069
2431.3167 | 436.8687 | 464.6715 | 446.442
2432.3167 | 437.2348 | 465.0063 | 446.2023
2433.3167 | 437.9052 | 467.692 | 446.4412
2434.3167 | 436.5726 | 469.4717 | 446.8909
2435.3167 | 438.3953 | 468.6155 | 447.3489
2436.3167 | 438.1808 | 468.2103 | 448.1144
2437.3167 | 437.9391 | 467.9833 | 447.7987
2438.3167 | 438.1544 | 468.0286 | 447.7342
2439.3167 | 438.1756 | 468.1578 | 448.1726
2440.3167 | 438.5097 | 469.0692 | 448.1923
2441.3167 | 438.8536 | 468.4579 | 447.7412
2442.3167 | 439.1226 | 468.6458 | 447.2882
2443.3167 | 439.631 | 467.4367 | 446.5858
2444.3167 | 440.2976 | 467.1884 | 446.3219
2445.3167 | 440.6756 | 467.7155 | 446.4685
2446.3167 | 441.068 | 467.1625 | 446.9531
2447.3167 | 441.4377 | 467.0543 | 446.8938
2448.3167 | 442.5826 | 469.3103 | 447.9478
2449.3167 | 443.3298 | 470.7905 | 448.4663
2450.3167 | 443.8415 | 470.1887 | 448.6581
2451.3167 | 444.2146 | 470.6676 | 449.4297
2452.3167 | 444.4966 | 469.8131 | 449.7912
2453.3167 | 444.7077 | 469.8328 | 450.0705
2454.3167 | 444.4292 | 468.9971 | 450.547
2455.3167 | 444.7991 | 468.9989 | 450.4094
2456.3167 | 445.2583 | 468.8085 | 450.3544
2457.3167 | 445.3451 | 468.6335 | 449.9608
2458.3167 | 445.6336 | 468.9612 | 449.7336
2459.3167 | 445.8142 | 469.4216 | 449.7706
2460.3167 | 445.6441 | 469.9705 | 450.8748
2461.3167 | 445.4543 | 470.5305 | 451.458
2462.3167 | 445.7468 | 470.3275 | 451.3906
2463.3167 | 445.9235 | 469.417 | 450.919
2464.3167 | 445.6212 | 469.5619 | 451.1092
2465.3167 | 446.1706 | 469.7263 | 451.4748
2466.3167 | 446.0551 | 469.5476 | 451.9068
2467.3167 | 446.3509 | 469.4119 | 451.6586
2468.3167 | 446.4922 | 468.5658 | 451.2617
2469.3167 | 446.2427 | 468.4083 | 450.9895
2470.3167 | 446.7831 | 468.2831 | 450.8844
2471.3167 | 447.0335 | 468.1043 | 450.8863
2472.3167 | 447.7332 | 469.0819 | 451.4357
2473.3167 | 448.8986 | 469.3663 | 452.5371
2474.3167 | 448.9888 | 468.9738 | 452.4373
2475.3167 | 449.0406 | 467.9003 | 452.7807
2476.3167 | 449.1839 | 467.1448 | 452.6033
2477.3167 | 449.7629 | 467.57 | 452.4683
2478.3167 | 450.0632 | 467.3553 | 452.4483
2479.3167 | 450.6119 | 467.2853 | 452.1097
2480.3167 | 451.4847 | 467.3469 | 452.1345
2481.3167 | 451.838 | 467.0926 | 452.5582
2482.3167 | 452.3677 | 467.1977 | 452.668
2483.3167 | 452.6784 | 467.0056 | 452.4712
2484.3167 | 453.0328 | 466.8634 | 452.4983
2485.3167 | 452.7861 | 466.347 | 452.163
2486.3167 | 452.9505 | 466.6857 | 452.0855
2487.3167 | 453.4126 | 467.6481 | 452.2496
2488.3167 | 454.0973 | 468.445 | 452.9006
2489.3167 | 454.4484 | 469.957 | 453.9461
2490.3167 | 454.8048 | 471.0099 | 454.5716
2491.3167 | 454.5713 | 471.2851 | 455.709
2492.3167 | 454.0945 | 470.8056 | 456.2756
2493.3167 | 453.8246 | 471.7753 | 457.2156
2494.3167 | 453.3376 | 471.9274 | 457.2276
2495.3167 | 452.884 | 471.3228 | 457.2909
2496.3167 | 452.49 | 471.1629 | 457.2361
2497.3167 | 453.1546 | 471.1985 | 456.8456
2498.3167 | 453.3033 | 471.6539 | 456.3276
2499.3167 | 453.0468 | 470.5886 | 455.7238
2500.3167 | 453.9654 | 469.8803 | 455.0845
2501.3167 | 454.6134 | 469.7299 | 454.9575
2502.3167 | 455.4369 | 470.3764 | 454.9033
2503.3167 | 456.5534 | 472.0555 | 455.9342
2504.3167 | 456.6051 | 471.8549 | 456.3173
2505.3167 | 456.8624 | 471.7937 | 456.5489
2506.3167 | 457.4721 | 471.6763 | 456.6061
2507.3167 | 458.7851 | 471.9312 | 457.0684
2508.3167 | 459.4467 | 472.5425 | 457.379
2509.3167 | 459.4739 | 472.109 | 457.2429
2510.3167 | 459.7279 | 471.7678 | 457.091
2511.3167 | 459.7594 | 472.4295 | 457.6581
2512.3167 | 460.1224 | 473.0597 | 457.3256
2513.3167 | 460.8448 | 473.5061 | 457.7658
2514.3167 | 461.0792 | 473.3635 | 457.5251
2515.3167 | 461.1245 | 473.4513 | 457.3819
2516.3167 | 461.3878 | 472.9184 | 456.9227
2517.3167 | 461.2583 | 472.604 | 456.843
2518.3167 | 461.3809 | 472.7441 | 456.8967
2519.3167 | 461.3575 | 472.2993 | 456.8935
2520.3167 | 461.2687 | 471.7492 | 457.1927
2521.3167 | 461.4891 | 471.6429 | 457.1084
2522.3167 | 461.2884 | 472.8651 | 458.6109
2523.3167 | 462.0185 | 473.5812 | 459.1788
2524.3167 | 463.0377 | 473.6617 | 459.5092
2525.3167 | 463.0805 | 473.6201 | 460.3287
2526.3167 | 463.2196 | 473.3714 | 460.2955
2527.3167 | 463.6596 | 473.0749 | 460.4011
2528.3167 | 464.2152 | 473.9577 | 460.5096
2529.3167 | 465.0675 | 474.3587 | 460.998
2530.3167 | 465.1977 | 474.0764 | 461.3152
2531.3167 | 464.7799 | 473.9323 | 460.9717
2532.3167 | 464.6421 | 474.3513 | 460.911
2533.3167 | 465.2915 | 475.3411 | 461.1389
2534.3167 | 465.3964 | 475.6256 | 461.0252
2535.3167 | 465.7117 | 475.7634 | 460.7441
2536.3167 | 465.6257 | 475.2372 | 460.4657
2537.3167 | 465.4217 | 475.0486 | 460.2177
2538.3167 | 465.6195 | 474.9301 | 460.0365
2539.3167 | 465.9405 | 475.952 | 460.1411
2540.3167 | 466.0736 | 475.9831 | 460.1415
2541.3167 | 466.5049 | 476.7377 | 460.6658
2542.3167 | 467.059 | 476.1068 | 461.1027
2543.3167 | 467.026 | 476.0797 | 461.3827
2544.3167 | 467.6571 | 475.8718 | 461.2188
2545.3167 | 467.9305 | 475.2914 | 461.3117
2546.3167 | 467.97 | 475.6191 | 461.858
2547.3167 | 468.4545 | 476.3212 | 462.2698
2548.3167 | 468.984 | 476.9818 | 462.6357
2549.3167 | 469.5 | 476.3229 | 462.5465
2550.3167 | 469.5062 | 475.6904 | 462.2853
2551.3167 | 469.7544 | 475.1645 | 462.012
2552.3167 | 469.7718 | 474.7835 | 461.806
2553.3167 | 469.8669 | 474.7496 | 461.5933
2554.3167 | 469.9943 | 475.4279 | 462.2787
2555.3167 | 470.0606 | 475.1422 | 462.5078
2556.3167 | 470.6583 | 476.1256 | 462.6976
2557.3167 | 470.7024 | 476.3131 | 463.126
2558.3167 | 471.3813 | 475.1864 | 463.0224
2559.3167 | 471.5221 | 476.4572 | 462.8748
2560.3167 | 471.8644 | 477.6423 | 463.0394
2561.3167 | 472.1371 | 478.8672 | 463.4951
2562.3167 | 472.2626 | 478.6679 | 463.5923
2563.3167 | 472.3293 | 478.8325 | 463.5865
2564.3167 | 472.3425 | 479.0261 | 463.5153
2565.3167 | 472.0763 | 479.1728 | 463.6384
2566.3167 | 471.4923 | 478.3797 | 463.5618
2567.3167 | 471.3437 | 478.7319 | 463.7149
2568.3167 | 471.5773 | 478.9017 | 463.6245
2569.3167 | 472.062 | 479.0324 | 464.1197
2570.3167 | 472.0767 | 479.1468 | 464.1102
2571.3167 | 472.5696 | 478.7097 | 464.4223
2572.3167 | 472.8742 | 477.9671 | 463.9694
2573.3167 | 473.5777 | 478.1652 | 463.9544
2574.3167 | 474.4447 | 479.1627 | 464.4707
2575.3167 | 474.9651 | 479.3888 | 464.5332
2576.3167 | 475.5489 | 478.9728 | 465.0441
2577.3167 | 476.2495 | 478.5737 | 465.0191
2578.3167 | 475.8236 | 479.5084 | 464.7941
2579.3167 | 475.7472 | 480.0087 | 464.9736
2580.3167 | 476.1434 | 479.8191 | 465.4338
2581.3167 | 476.6192 | 481.1045 | 466.5172
2582.3167 | 476.8658 | 481.5237 | 467.1325
2583.3167 | 476.8803 | 482.1462 | 467.5857
2584.3167 | 476.6717 | 481.4493 | 468.0516
2585.3167 | 476.9999 | 480.6725 | 467.6338
2586.3167 | 477.6431 | 479.9192 | 467.5464
2587.3167 | 477.8109 | 480.214 | 467.2915
2588.3167 | 477.6613 | 479.6364 | 467.018
2589.3167 | 477.4314 | 479.3145 | 466.5261
2590.3167 | 477.2355 | 478.8094 | 466.9306
2591.3167 | 478.2576 | 479.7842 | 467.5717
2592.3167 | 478.7523 | 481.8765 | 468.0919
2593.3167 | 478.5305 | 483.3039 | 468.5873
2594.3167 | 479.7717 | 483.7408 | 469.7564
2595.3167 | 479.7307 | 483.6435 | 469.6339
2596.3167 | 480.2039 | 483.3525 | 469.2925
2597.3167 | 481.1839 | 482.7112 | 469.1255
2598.3167 | 481.8876 | 482.9985 | 468.9579
2599.3167 | 481.9359 | 482.869 | 468.9222
2600.3167 | 482.0956 | 482.6768 | 468.7596
2601.3167 | 483.0184 | 482.3254 | 468.2988
2602.3167 | 482.9963 | 482.4079 | 468.2751
2603.3167 | 483.5111 | 482.5709 | 468.5456
2604.3167 | 484.1959 | 482.5565 | 468.8413
2605.3167 | 484.8713 | 484.2857 | 469.6789
2606.3167 | 485.2887 | 485.0663 | 470.5259
2607.3167 | 485.1736 | 484.3286 | 470.318
2608.3167 | 484.9586 | 483.8033 | 470.4223
2609.3167 | 485.3403 | 482.9417 | 470.4466
2610.3167 | 485.6309 | 482.8212 | 470.2767
2611.3167 | 486.5434 | 483.017 | 470.4406
2612.3167 | 486.602 | 483.0581 | 470.5049
2613.3167 | 487.1894 | 483.5547 | 471.1988
2614.3167 | 487.2348 | 484.424 | 471.4761
2615.3167 | 487.8169 | 484.6959 | 471.8081
2616.3167 | 487.5057 | 483.9256 | 471.7732
2617.3167 | 487.7133 | 483.8202 | 471.4523
2618.3167 | 487.6027 | 483.3457 | 471.1284
2619.3167 | 487.6198 | 483.4126 | 471.3094
2620.3167 | 488.2435 | 486.5499 | 471.504
2621.3167 | 488.6392 | 486.7233 | 471.4915
2622.3167 | 489.4112 | 487.4334 | 471.8123
2623.3167 | 489.5125 | 486.7688 | 471.7117
2624.3167 | 489.3428 | 486.4282 | 471.4146
2625.3167 | 489.3105 | 485.6307 | 471.2704
2626.3167 | 488.9699 | 485.4376 | 471.0107
2627.3167 | 489.2585 | 485.2189 | 471.2579
2628.3167 | 489.5594 | 484.3077 | 471.7032
2629.3167 | 489.3615 | 485.699 | 471.6983
2630.3167 | 489.2566 | 486.1986 | 472.1483
2631.3167 | 489.4267 | 485.8981 | 472.6512
2632.3167 | 489.3599 | 485.0663 | 473.4431
2633.3167 | 488.323 | 483.7246 | 473.5974
2634.3167 | 488.6309 | 484.4279 | 473.3582
2635.3167 | 488.8139 | 484.1681 | 474.294
2636.3167 | 488.7665 | 484.5118 | 474.5108
2637.3167 | 489.1776 | 485.0809 | 474.5572
2638.3167 | 489.7531 | 485.5958 | 474.676
2639.3167 | 489.122 | 485.7085 | 474.1391
2640.3167 | 489.0033 | 486.8115 | 473.9929
2641.3167 | 489.3911 | 486.9996 | 474.2641
2642.3167 | 489.7593 | 487.2682 | 474.4265
2643.3167 | 490.3227 | 487.193 | 474.2121
2644.3167 | 490.6632 | 487.516 | 473.77
2645.3167 | 491.1635 | 487.1316 | 473.7291
2646.3167 | 491.1101 | 488.2471 | 473.8274
2647.3167 | 492.3199 | 488.8601 | 474.1345
2648.3167 | 493.3619 | 489.1282 | 474.1937
2649.3167 | 494.2365 | 489.1128 | 474.3129
2650.3167 | 494.3158 | 488.9617 | 474.0826
2651.3167 | 495.4455 | 489.7809 | 474.7253
2652.3167 | 495.9909 | 490.1385 | 475.5835
2653.3167 | 496.006 | 491.0381 | 475.9511
2654.3167 | 496.0687 | 490.6968 | 476.2885
2655.3167 | 495.6297 | 488.739 | 476.8054
2656.3167 | 496.6625 | 490.0623 | 476.7857
2657.3167 | 497.3156 | 489.3844 | 476.5923
2658.3167 | 498.1464 | 489.463 | 476.4768
2659.3167 | 497.8602 | 488.5684 | 476.02
2660.3167 | 497.6654 | 488.9746 | 475.8203
2661.3167 | 498.3903 | 489.9442 | 476.246
2662.3167 | 498.6273 | 491.7332 | 476.6447
2663.3167 | 498.6013 | 492.5018 | 477.1281
2664.3167 | 498.9436 | 493.1389 | 477.5031
2665.3167 | 499.1123 | 493.1339 | 477.9447
2666.3167 | 498.1119 | 493.4547 | 477.5952
2667.3167 | 497.9676 | 494.2296 | 478.2053
2668.3167 | 498.101 | 495.6866 | 479.6253
2669.3167 | 498.7687 | 495.6276 | 479.8103
2670.3167 | 498.6319 | 495.3563 | 479.7506
2671.3167 | 498.278 | 494.4187 | 479.4151
2672.3167 | 498.3383 | 493.1358 | 478.9655
2673.3167 | 498.1407 | 491.4795 | 478.6565
2674.3167 | 498.2346 | 491.29 | 478.5996
2675.3167 | 498.2004 | 490.4974 | 478.0732
2676.3167 | 498.3904 | 486.2342 | 477.8589
2677.3167 | 498.2464 | 489.7464 | 477.8756
2678.3167 | 497.6518 | 489.3862 | 478.2225
2679.3167 | 498.3892 | 489.3055 | 478.7275
2680.3167 | 499.2553 | 489.2704 | 478.6299
2681.3167 | 498.5239 | 488.8177 | 478.3218
2682.3167 | 498.9916 | 488.3796 | 478.3799
2683.3167 | 499.2559 | 488.6657 | 478.7002
2684.3167 | 500.3577 | 490.3095 | 479.7244
2685.3167 | 501.6599 | 490.733 | 480.5184
2686.3167 | 501.9438 | 490.8064 | 480.7135
2687.3167 | 501.9852 | 491.0702 | 480.822
2688.3167 | 501.3256 | 490.8979 | 480.2843
2689.3167 | 500.2635 | 490.7023 | 479.8
2690.3167 | 500.0181 | 490.1544 | 479.9029
2691.3167 | 499.5408 | 489.8908 | 479.6288
2692.3167 | 499.6828 | 486.8093 | 479.4965
2693.3167 | 500.1545 | 490.5925 | 480.2514
2694.3167 | 500.9163 | 490.3555 | 481.7811
2695.3167 | 500.6588 | 490.8688 | 482.6682
2696.3167 | 500.6472 | 493.3558 | 482.9537
2697.3167 | 500.8501 | 493.5434 | 483.2229
2698.3167 | 501.6576 | 493.2005 | 483.1876
2699.3167 | 502.2981 | 493.4821 | 483.3003
2700.3167 | 502.2601 | 493.3065 | 484.0037
2701.3167 | 501.8442 | 494.2442 | 484.0731
2702.3167 | 502.458 | 494.3586 | 483.7155
2703.3167 | 502.0459 | 494.3386 | 483.7791
2704.3167 | 502.8545 | 495.2603 | 484.699
2705.3167 | 503.8201 | 495.8309 | 485.8558
2706.3167 | 505.0022 | 494.1734 | 487.7664
2707.3167 | 505.1945 | 494.0601 | 488.6
2708.3167 | 504.7626 | 499.4532 | 488.9414
2709.3167 | 504.1051 | 499.9725 | 489.0008
2710.3167 | 503.605 | 499.9583 | 489.0417
2711.3167 | 503.0741 | 499.3222 | 488.7238
2712.3167 | 503.5755 | 498.9013 | 488.3436
2713.3167 | 504.224 | 497.6317 | 488.7238
2714.3167 | 503.943 | 497.8055 | 488.8826
2715.3167 | 504.6081 | 501.0056 | 488.99
2716.3167 | 503.7842 | 500.5644 | 488.7391
2717.3167 | 504.009 | 500.6762 | 488.9155
2718.3167 | 503.7833 | 500.9278 | 489.391
2719.3167 | 503.9582 | 502.2679 | 489.6138
2720.3167 | 504.3977 | 502.3294 | 489.8755
2721.3167 | 504.0876 | 502.2653 | 489.4877
2722.3167 | 503.409 | 501.8751 | 488.9416
2723.3167 | 502.7484 | 501.4311 | 488.2624
2724.3167 | 503.6593 | 501.0884 | 488.1118
2725.3167 | 503.7967 | 501.1964 | 487.9409
2726.3167 | 503.739 | 501.1414 | 487.7286
2727.3167 | 503.3831 | 500.4862 | 487.1861
2728.3167 | 502.9576 | 498.8781 | 486.5129
2729.3167 | 503.3021 | 499.0729 | 485.9241
2730.3167 | 503.7099 | 499.4048 | 486.0474
2731.3167 | 503.8712 | 498.7549 | 486.0755
2732.3167 | 503.2387 | 497.8652 | 485.8193
2733.3167 | 504.7492 | 497.3002 | 485.7768
2734.3167 | 505.124 | 498.5717 | 486.087
2735.3167 | 505.492 | 498.4333 | 486.5754
2736.3167 | 505.0788 | 498.0678 | 486.5029
2737.3167 | 505.4897 | 498.1529 | 486.5928
2738.3167 | 506.4414 | 498.5373 | 486.7459
2739.3167 | 506.5707 | 499.3492 | 486.7301
2740.3167 | 506.6815 | 499.0441 | 486.2803
2741.3167 | 505.9077 | 499.333 | 486.017
2742.3167 | 505.0662 | 499.097 | 485.8881
2743.3167 | 503.7183 | 499.0579 | 485.9725
2744.3167 | 502.9469 | 498.3825 | 486.1327
2745.3167 | 502.8676 | 497.6489 | 486.4214
2746.3167 | 502.8048 | 497.3782 | 486.6413
2747.3167 | 503.3053 | 498.182 | 487.174
2748.3167 | 504.1199 | 499.7251 | 487.4615
2749.3167 | 504.0016 | 502.7286 | 487.91
2750.3167 | 504.0237 | 505.7364 | 488.8533
2751.3167 | 503.929 | 506.2522 | 488.965
2752.3167 | 504.2636 | 506.0352 | 488.8905
2753.3167 | 504.4422 | 506.0315 | 489.0673
2754.3167 | 503.9471 | 506.0455 | 489.1929
2755.3167 | 503.5944 | 505.8913 | 489.0283
2756.3167 | 503.6086 | 505.4032 | 488.8695
2757.3167 | 503.8699 | 505.6753 | 489.1508
2758.3167 | 503.4207 | 505.2324 | 488.7992
2759.3167 | 502.3551 | 504.9703 | 488.0389
2760.3167 | 501.5104 | 504.3948 | 488.271
2761.3167 | 501.5199 | 505.1696 | 488.8078
2762.3167 | 502.2666 | 505.8024 | 488.7778
2763.3167 | 502.7658 | 506.7456 | 489.3473
2764.3167 | 503.658 | 505.8788 | 489.7627
2765.3167 | 504.5781 | 502.5742 | 489.7578
2766.3167 | 505.8283 | 502.2596 | 490.5199
2767.3167 | 506.2564 | 504.1553 | 491.3581
2768.3167 | 505.3838 | 503.5204 | 491.4451
2769.3167 | 506.1223 | 502.8159 | 491.7818
2770.3167 | 506.5761 | 502.6336 | 492.2049
2771.3167 | 506.3906 | 502.211 | 492.2041
2772.3167 | 506.415 | 501.4509 | 492.4046
2773.3167 | 506.8391 | 497.3219 | 492.3118
2774.3167 | 506.7578 | 500.2864 | 491.9897
2775.3167 | 506.7352 | 499.7892 | 491.5717
2776.3167 | 506.9196 | 499.396 | 491.5343
2777.3167 | 506.3137 | 499.4695 | 491.7841
2778.3167 | 506.5522 | 500.3626 | 492.4835
2779.3167 | 506.1633 | 500.8355 | 493.0568
2780.3167 | 505.993 | 501.0852 | 493.4969
2781.3167 | 506.3252 | 500.4643 | 493.2905
2782.3167 | 505.9995 | 499.4288 | 493.0747
2783.3167 | 504.8699 | 498.2189 | 493.2734
2784.3167 | 505.0835 | 498.1663 | 493.4299
2785.3167 | 505.3534 | 498.0667 | 492.8215
2786.3167 | 504.9702 | 497.706 | 492.3648
2787.3167 | 505.3101 | 497.0895 | 492.4748
2788.3167 | 504.7937 | 497.6428 | 492.6749
2789.3167 | 504.4482 | 497.7698 | 492.6448
2790.3167 | 502.8666 | 497.6215 | 492.3892
2791.3167 | 502.5979 | 497.4408 | 492.4996
2792.3167 | 502.7355 | 497.1555 | 492.475
2793.3167 | 503.4136 | 497.3577 | 492.48
2794.3167 | 504.2427 | 497.0346 | 492.1951
2795.3167 | 502.8581 | 496.9245 | 492.1265
2796.3167 | 503.0629 | 497.2128 | 492.0982
2797.3167 | 502.872 | 497.4332 | 491.9028
2798.3167 | 502.4894 | 497.4986 | 491.6338
2799.3167 | 501.7805 | 497.4081 | 491.246
2800.3167 | 502.3348 | 497.3461 | 491.0178
2801.3167 | 501.5609 | 496.4757 | 490.9407
2802.3167 | 500.5043 | 496.2958 | 491.0478
2803.3167 | 500.7928 | 496.3885 | 490.6889
2804.3167 | 501.0207 | 496.6742 | 490.7707
2805.3167 | 499.9443 | 497.6491 | 490.9909
2806.3167 | 500.5052 | 497.4341 | 491.0961
2807.3167 | 499.9005 | 497.5953 | 491.0762
2808.3167 | 500.0133 | 498.5389 | 491.683
2809.3167 | 499.9877 | 498.1814 | 491.8139
2810.3167 | 499.4891 | 498.0199 | 492.3983
2811.3167 | 499.8526 | 498.3151 | 492.2715
2812.3167 | 499.9857 | 499.0475 | 492.3035
2813.3167 | 500.4667 | 498.8821 | 492.5014
2814.3167 | 500.5343 | 498.8895 | 492.4175
2815.3167 | 499.6361 | 499.9912 | 492.2487
2816.3167 | 499.1241 | 499.9691 | 491.9254
2817.3167 | 498.3289 | 499.401 | 491.7385
2818.3167 | 498.3654 | 498.5179 | 491.9382
2819.3167 | 498.0473 | 498.4336 | 492.9249
2820.3167 | 497.8178 | 498.575 | 493.3187
2821.3167 | 498.2344 | 498.7039 | 493.4062
2822.3167 | 499.1091 | 498.6239 | 493.9483
2823.3167 | 499.0281 | 499.1239 | 493.849
2824.3167 | 497.1911 | 499.5724 | 493.787
2825.3167 | 497.2252 | 499.5454 | 493.4649
2826.3167 | 497.1938 | 499.3148 | 492.9643
2827.3167 | 498.0109 | 499.9458 | 493.1213
2828.3167 | 497.8659 | 500.0146 | 493.3537
2829.3167 | 498.0556 | 500.0243 | 492.8919
2830.3167 | 497.7125 | 496.5557 | 492.7022
2831.3167 | 497.9374 | 499.4341 | 492.8586
2832.3167 | 498.9314 | 499.4474 | 492.8462
2833.3167 | 499.9342 | 500.459 | 493.2855
2834.3167 | 500.0578 | 501.7417 | 493.7988
2835.3167 | 499.9584 | 502.3947 | 493.892
2836.3167 | 499.9682 | 502.4074 | 493.6948
2837.3167 | 499.5744 | 502.5023 | 493.2305
2838.3167 | 499.6882 | 501.969 | 492.7269
2839.3167 | 499.43 | 501.6146 | 492.3652
2840.3167 | 499.7897 | 501.5792 | 492.4911
2841.3167 | 499.9505 | 502.9238 | 493.2362
2842.3167 | 499.995 | 504.3663 | 493.4371
2843.3167 | 499.7848 | 503.8735 | 493.3062
2844.3167 | 499.472 | 503.2577 | 493.4777
2845.3167 | 501.0375 | 503.8254 | 494.2183
2846.3167 | 501.6108 | 504.7273 | 495.5651
2847.3167 | 502.6516 | 506.0754 | 495.7478
2848.3167 | 503.3058 | 506.1958 | 495.5721
2849.3167 | 502.3243 | 506.7812 | 495.4498
2850.3167 | 501.6373 | 507.7088 | 495.7799
2851.3167 | 501.8103 | 507.7201 | 495.6979
2852.3167 | 501.5451 | 507.7982 | 496.1677
2853.3167 | 502.2234 | 507.8964 | 496.7027
2854.3167 | 502.111 | 507.4861 | 496.9561
2855.3167 | 500.7586 | 506.8253 | 497.2297
2856.3167 | 501.7473 | 506.4351 | 497.9293
2857.3167 | 502.2777 | 506.2323 | 498.5717
2858.3167 | 501.6319 | 505.5289 | 498.3039
2859.3167 | 499.4738 | 505.1115 | 497.8641
2860.3167 | 499.9082 | 504.6317 | 497.6362
2861.3167 | 500.0852 | 504.6446 | 498.4903
2862.3167 | 500.7757 | 504.7094 | 498.7192
2863.3167 | 500.9546 | 504.7836 | 499.0976
2864.3167 | 501.8071 | 505.2474 | 499.5088
2865.3167 | 501.227 | 505.2576 | 499.5341
2866.3167 | 501.477 | 504.785 | 498.9393
2867.3167 | 501.2255 | 503.5175 | 498.3462
2868.3167 | 500.9603 | 502.7354 | 498.0983
2869.3167 | 501.0157 | 502.3834 | 497.9277
2870.3167 | 500.0723 | 502.2936 | 497.7292
2871.3167 | 500.1384 | 502.8834 | 497.3383
2872.3167 | 500.8764 | 503.848 | 497.5741
2873.3167 | 502.2733 | 505.4586 | 497.92
2874.3167 | 503.1122 | 506.0716 | 498.0949
2875.3167 | 502.6638 | 506.5754 | 498.2298
2876.3167 | 501.4021 | 507.5658 | 498.0371
2877.3167 | 501.7596 | 506.461 | 498.5176
2878.3167 | 501.6305 | 505.6736 | 498.2757
2879.3167 | 501.3071 | 505.4101 | 498.9087
2880.3167 | 501.2139 | 505.8604 | 500.2599
2881.3167 | 500.9773 | 506.8811 | 500.6794
2882.3167 | 500.7059 | 507.4007 | 501.0717
2883.3167 | 501.1159 | 508.5522 | 501.0646
2884.3167 | 501.0686 | 508.3035 | 500.9722
2885.3167 | 501.7581 | 507.3582 | 500.9683
2886.3167 | 501.9913 | 505.9782 | 500.8102
2887.3167 | 501.4106 | 505.137 | 500.1918
2888.3167 | 500.4261 | 505.6756 | 500.0235
2889.3167 | 500.0081 | 505.9455 | 499.9189
2890.3167 | 500.0767 | 506.1836 | 500.2489
2891.3167 | 501.1579 | 507.1207 | 500.5993
2892.3167 | 501.7152 | 508.2727 | 501.2249
2893.3167 | 501.7986 | 508.4636 | 501.3142
2894.3167 | 502.2582 | 508.0778 | 501.318
2895.3167 | 502.2514 | 507.0935 | 500.8686
2896.3167 | 502.265 | 506.7076 | 500.3843
2897.3167 | 500.9885 | 507.8754 | 500.0877
2898.3167 | 501.3509 | 507.9234 | 499.8488
2899.3167 | 501.4308 | 507.5317 | 499.2726
2900.3167 | 501.8018 | 507.2138 | 499.1051
2901.3167 | 500.9121 | 506.9164 | 499.6587
2902.3167 | 501.1436 | 506.2905 | 500.0346
2903.3167 | 500.9703 | 506.2654 | 500.224
2904.3167 | 501.0447 | 506.2092 | 501.1317
2905.3167 | 501.2836 | 506.9432 | 502.2923
2906.3167 | 501.3317 | 507.1038 | 502.4461
2907.3167 | 501.446 | 507.0271 | 502.4926
2908.3167 | 501.7598 | 507.8343 | 502.525
2909.3167 | 501.2037 | 508.2047 | 502.7289
2910.3167 | 500.7626 | 507.7923 | 503.2495
2911.3167 | 500.9987 | 506.7782 | 502.5833
2912.3167 | 500.5487 | 505.9297 | 502.5025
2913.3167 | 500.6143 | 506.1938 | 502.9555
2914.3167 | 500.4388 | 506.6464 | 503.6274
2915.3167 | 500.042 | 507.6907 | 503.4107
2916.3167 | 499.8228 | 507.9751 | 503.6129
2917.3167 | 500.5301 | 507.8141 | 503.9823
2918.3167 | 500.6845 | 507.0129 | 504.3367
2919.3167 | 500.444 | 506.218 | 504.3137
2920.3167 | 500.229 | 505.8365 | 503.8637
2921.3167 | 500.0396 | 507.7569 | 504.1688
2922.3167 | 500.8507 | 508.2337 | 504.223
2923.3167 | 499.5593 | 507.5457 | 504.3138
2924.3167 | 498.7618 | 508.1948 | 504.2474
2925.3167 | 498.7476 | 509.0048 | 503.476
2926.3167 | 498.6206 | 510.8006 | 503.6593
2927.3167 | 498.7905 | 511.7726 | 503.6223
2928.3167 | 498.8713 | 511.8464 | 503.1628
2929.3167 | 499.4297 | 511.3658 | 502.634
2930.3167 | 498.9737 | 511.3738 | 502.8702
2931.3167 | 498.7043 | 511.6393 | 503.1851
2932.3167 | 496.536 | 508.2031 | 503.341
2933.3167 | 498.263 | 510.7099 | 503.0971
2934.3167 | 498.1346 | 510.7386 | 502.7999
2935.3167 | 498.1006 | 512.1655 | 502.5939
2936.3167 | 497.8899 | 512.2986 | 502.9528
2937.3167 | 497.7639 | 512.3052 | 502.4788
2938.3167 | 497.8956 | 510.8716 | 502.3947
2939.3167 | 497.7747 | 509.4184 | 502.3993
2940.3167 | 496.8056 | 508.9156 | 502.3007
2941.3167 | 493.3452 | 505.9762 | 502.3616
2942.3167 | 495.0849 | 507.7124 | 502.5625
2943.3167 | 495.2498 | 507.2952 | 502.7806
2944.3167 | 495.3432 | 506.7679 | 502.5964
2945.3167 | 495.5323 | 506.9287 | 502.2424
2946.3167 | 495.4228 | 507.2905 | 502.1676
2947.3167 | 495.6229 | 507.419 | 502.201
2948.3167 | 496.3952 | 508.7926 | 501.7647
2949.3167 | 496.4438 | 508.5625 | 501.9077
2950.3167 | 496.2085 | 507.3751 | 502.0408
2951.3167 | 496.0798 | 506.2034 | 500.9319
2952.3167 | 495.5154 | 505.3698 | 500.4602
2953.3167 | 494.715 | 505.3777 | 500.2889
2954.3167 | 494.4476 | 504.9599 | 500.314
2955.3167 | 493.9271 | 504.8902 | 500.7514
2956.3167 | 493.3712 | 504.4314 | 500.3429
2957.3167 | 493.5316 | 504.96 | 501.1814
2958.3167 | 493.9534 | 505.7904 | 501.6676
2959.3167 | 493.6067 | 505.8427 | 501.4991
2960.3167 | 493.7474 | 505.0924 | 501.7711
2961.3167 | 493.3399 | 504.3129 | 501.9181
2962.3167 | 492.8833 | 503.6595 | 501.854
2963.3167 | 492.3825 | 503.4268 | 502.1608
2964.3167 | 491.8825 | 503.5866 | 502.6122
2965.3167 | 491.9552 | 503.4976 | 502.8252
2966.3167 | 491.3903 | 504.3422 | 502.8893
2967.3167 | 491.0261 | 504.4338 | 502.6771
2968.3167 | 490.8174 | 505.9643 | 502.7604
2969.3167 | 490.7611 | 506.5772 | 502.8784
2970.3167 | 491.02 | 505.8985 | 502.157
2971.3167 | 490.9856 | 505.182 | 501.5132
2972.3167 | 490.5695 | 505.1201 | 501.779
2973.3167 | 490.5838 | 506.0542 | 501.9569
2974.3167 | 490.7658 | 506.347 | 502.9197
2975.3167 | 490.6739 | 506.4843 | 503.5402
2976.3167 | 490.894 | 505.6954 | 503.1943
2977.3167 | 490.8152 | 504.6618 | 502.7781
2978.3167 | 490.2632 | 504.3178 | 503.5436
2979.3167 | 490.102 | 504.2593 | 503.1936
2980.3167 | 490.3201 | 503.919 | 502.8423
2981.3167 | 491.2528 | 504.2786 | 503.0832
2982.3167 | 491.7491 | 504.115 | 502.8924
2983.3167 | 492.0329 | 504.403 | 502.6938
2984.3167 | 492.0125 | 503.9066 | 502.2299
2985.3167 | 491.6435 | 508.2071 | 502.3355
2986.3167 | 491.5632 | 507.7602 | 502.4145
2987.3167 | 491.8291 | 509.0206 | 502.7019
2988.3167 | 492.2755 | 511.5143 | 504.2246
2989.3167 | 493.705 | 513.3469 | 505.0241
2990.3167 | 494.2334 | 514.0471 | 505.0146
2991.3167 | 494.3112 | 512.5614 | 504.0602
2992.3167 | 493.9075 | 512.0192 | 503.1578
2993.3167 | 493.9612 | 512.2548 | 503.4261
2994.3167 | 493.699 | 512.5074 | 503.5647
2995.3167 | 494.2416 | 511.6569 | 504.225
2996.3167 | 494.4976 | 510.7001 | 504.1181
2997.3167 | 494.953 | 511.1395 | 504.0142
2998.3167 | 494.9455 | 510.882 | 503.8229
2999.3167 | 494.9212 | 510.5085 | 503.8046
3000.3167 | 495.2291 | 510.2516 | 504.0959
3001.3167 | 495.835 | 510.5416 | 504.3967
3002.3167 | 496.152 | 509.5873 | 504.9763
3003.3167 | 496.2806 | 510.7603 | 505.0844
3004.3167 | 496.3796 | 511.0558 | 505.3076
3005.3167 | 496.2038 | 513.0226 | 504.2799
3006.3167 | 496.189 | 513.2635 | 503.9841
3007.3167 | 496.0351 | 512.6267 | 505.6163
3008.3167 | 496.37 | 513.2108 | 506.1913
3009.3167 | 496.3457 | 512.0492 | 506.335
3010.3167 | 496.6727 | 512.0688 | 506.4466
3011.3167 | 496.4939 | 511.4123 | 505.6989
3012.3167 | 496.3015 | 511.0656 | 505.0891
3013.3167 | 495.437 | 509.7546 | 504.9801
3014.3167 | 495.4638 | 508.866 | 504.8815
3015.3167 | 495.4659 | 508.5264 | 505.4573
3016.3167 | 495.5541 | 508.7357 | 505.1403
3017.3167 | 495.4504 | 509.6325 | 504.8602
3018.3167 | 495.0343 | 510.2078 | 504.3476
3019.3167 | 494.7941 | 510.8131 | 503.7995
3020.3167 | 494.6779 | 510.6393 | 504.443
3021.3167 | 494.7493 | 511.1113 | 505.5146
3022.3167 | 494.9006 | 511.3736 | 506.0106
3023.3167 | 494.5501 | 510.8509 | 505.46
3024.3167 | 494.4609 | 510.5847 | 505.2811
3025.3167 | 494.5021 | 511.1643 | 504.7301
3026.3167 | 494.0805 | 511.5919 | 505.2561
3027.3167 | 493.875 | 510.8808 | 505.0219
3028.3167 | 494.2646 | 509.5447 | 505.8467
3029.3167 | 494.3916 | 508.8127 | 505.3463
3030.3167 | 494.6046 | 509.3593 | 505.7369
3031.3167 | 494.5986 | 509.6659 | 506.3411
3032.3167 | 494.68 | 510.0266 | 506.7759
3033.3167 | 494.6075 | 509.7872 | 506.4657
3034.3167 | 494.2509 | 509.5184 | 506.8869
3035.3167 | 493.9159 | 509.5335 | 506.9085
3036.3167 | 493.9751 | 509.2811 | 506.8936
3037.3167 | 493.7406 | 508.3135 | 505.953
3038.3167 | 493.7424 | 508.4174 | 506.2747
3039.3167 | 494.2638 | 508.4969 | 506.1295
3040.3167 | 494.3784 | 508.6326 | 505.6731
3041.3167 | 494.7031 | 507.7899 | 505.2462
3042.3167 | 495.0678 | 508.5488 | 505.2604
3043.3167 | 495.1023 | 509.8989 | 505.9072
3044.3167 | 494.7637 | 509.4601 | 505.4824
3045.3167 | 494.7802 | 509.902 | 504.706
3046.3167 | 494.6183 | 509.8004 | 504.693
3047.3167 | 494.3034 | 509.3611 | 504.6524
3048.3167 | 494.3381 | 508.8233 | 504.5997
3049.3167 | 494.2841 | 509.897 | 504.9036
3050.3167 | 494.1313 | 510.945 | 505.2522
3051.3167 | 493.8459 | 510.4872 | 505.2693
3052.3167 | 493.8826 | 509.8152 | 505.1052
3053.3167 | 493.8507 | 509.1899 | 504.7371
3054.3167 | 493.3656 | 507.9832 | 504.7734
3055.3167 | 493.0661 | 508.2349 | 504.8033
3056.3167 | 493.0026 | 509.9834 | 504.8485
3057.3167 | 493.0472 | 509.4074 | 504.9728
3058.3167 | 493.0693 | 509.7456 | 504.9485
3059.3167 | 492.8652 | 509.727 | 505.0898
3060.3167 | 493.2144 | 509.4979 | 505.2815
3061.3167 | 493.0434 | 508.8211 | 505.433
3062.3167 | 492.743 | 508.5165 | 505.1052
3063.3167 | 492.6838 | 507.4248 | 504.5757
3064.3167 | 492.6179 | 507.6245 | 504.0396
3065.3167 | 492.4383 | 507.7614 | 503.823
3066.3167 | 492.0966 | 508.4954 | 503.7789
3067.3167 | 491.9738 | 508.1283 | 503.7879
3068.3167 | 491.9651 | 507.7779 | 503.6326
3069.3167 | 492.0781 | 507.6782 | 503.4457
3070.3167 | 492.4049 | 507.4059 | 503.4146
3071.3167 | 492.5636 | 506.9741 | 503.486
3072.3167 | 492.4586 | 506.9927 | 503.7294
3073.3167 | 492.1311 | 506.2334 | 503.2804
3074.3167 | 492.0818 | 505.8067 | 503.3729
3075.3167 | 492.0608 | 506.0028 | 503.2064
3076.3167 | 492.3035 | 505.3573 | 502.7921
3077.3167 | 492.1808 | 504.4114 | 502.8428
3078.3167 | 492.0443 | 504.3595 | 503.7195
3079.3167 | 492.2694 | 504.6323 | 503.7588
3080.3167 | 492.036 | 505.1121 | 503.9688
3081.3167 | 491.7119 | 505.2798 | 504.5646
3082.3167 | 491.9514 | 506.2911 | 506.3767
3083.3167 | 492.3391 | 506.222 | 505.8004
3084.3167 | 492.0641 | 505.7182 | 505.2267
3085.3167 | 491.6701 | 506.1483 | 504.3777
3086.3167 | 491.0145 | 506.3093 | 503.7215
3087.3167 | 490.9145 | 506.1859 | 503.3263
3088.3167 | 491.1806 | 505.9403 | 503.6095
3089.3167 | 491.7113 | 506.116 | 504.5013
3090.3167 | 492.4838 | 505.1835 | 506.9876
3091.3167 | 492.3544 | 505.3086 | 507.7704
3092.3167 | 492.3561 | 506.6381 | 508.1738
3093.3323 | 492.7884 | 507.5287 | 508.3853
3094.3167 | 493.0545 | 508.0765 | 508.2921
3095.3167 | 493.2065 | 507.7267 | 507.2443
3096.3167 | 493.1075 | 507.4652 | 506.698
3097.3167 | 493.4649 | 508.5108 | 506.465
3098.3167 | 493.3295 | 509.221 | 505.9276
3099.3167 | 493.6587 | 508.8595 | 505.7532
3100.3167 | 494.1339 | 509.3447 | 505.2144
3101.3167 | 495.1611 | 509.1604 | 504.8693
3102.3167 | 495.9056 | 509.842 | 504.9345
3103.3167 | 496.5995 | 509.8335 | 506.2865
3104.3167 | 497.0203 | 509.4803 | 505.6617
3105.3167 | 497.5379 | 509.5825 | 505.3228
3106.3167 | 498.01 | 509.4181 | 506.2966
3107.3167 | 497.6369 | 508.5275 | 505.6676
3108.3167 | 496.9578 | 508.5398 | 504.4256
3109.3167 | 497.0133 | 509.1741 | 503.9312
3110.3167 | 497.2214 | 510.0629 | 503.9914
3111.3167 | 497.2771 | 510.1759 | 505.5214
3112.3167 | 497.4975 | 511.4242 | 506.0221
3113.3167 | 497.2551 | 510.8652 | 506.451
3114.3167 | 496.9335 | 510.9372 | 506.1249
3115.3167 | 496.8157 | 510.6555 | 506.1152
3116.3167 | 497.0209 | 510.6956 | 505.395
3117.3167 | 496.7842 | 509.1519 | 504.6614
3118.3167 | 496.5663 | 508.3995 | 504.3862
3119.3167 | 496.2786 | 508.8767 | 504.0214
3120.3167 | 495.929 | 508.615 | 504.2938
3121.3167 | 495.5953 | 508.5766 | 504.1825
3122.3167 | 495.413 | 508.812 | 503.8078
3123.3323 | 495.5375 | 508.3115 | 505.1406
3124.3167 | 495.2487 | 508.0457 | 505.4883
3125.3167 | 495.1637 | 507.8318 | 504.5389
3126.3167 | 495.4145 | 508.9959 | 504.5592
3127.3167 | 495.718 | 509.5052 | 505.8954
3128.3167 | 495.4007 | 509.2056 | 505.5776
3129.3167 | 495.1486 | 509.3833 | 504.8716
3130.3167 | 494.5129 | 507.7712 | 505.1224
3131.3167 | 494.4117 | 507.2529 | 506.1392
3132.3167 | 494.6593 | 509.0222 | 506.47
3133.3167 | 495.1173 | 509.3879 | 506.0937
3134.3167 | 495.129 | 508.6482 | 505.4525
3135.3167 | 494.9263 | 508.6879 | 505.0843
3136.3167 | 494.8357 | 510.3273 | 506.0789
3137.3167 | 494.5492 | 511.0237 | 505.7612
3138.3167 | 494.3622 | 511.2475 | 505.3554
3139.3167 | 494.4594 | 511.2896 | 505.3704
3140.3167 | 495.039 | 511.4502 | 506.043
3141.3167 | 495.252 | 511.4965 | 506.4487
3142.3167 | 495.4422 | 512.008 | 505.9777
3143.3167 | 495.3149 | 514.5624 | 506.3806
3144.3167 | 495.0517 | 515.0223 | 507.0371
3145.3167 | 494.4255 | 514.3399 | 507.724
3146.3167 | 493.8843 | 513.6342 | 506.8512
3147.3167 | 493.486 | 513.1861 | 505.8986
3148.3167 | 493.4268 | 512.2969 | 506.7302
3149.3167 | 493.4242 | 511.233 | 506.6431
3150.3167 | 493.0731 | 510.68 | 506.3483
3151.3167 | 493.0174 | 509.7491 | 506.0131
3152.3167 | 493.151 | 510.2676 | 506.8245
3153.3167 | 493.5896 | 510.4913 | 509.7487
3154.3167 | 493.9563 | 511.6115 | 509.0374
3155.3167 | 493.8267 | 513.1455 | 508.5741
3156.3167 | 493.4318 | 513.0341 | 508.914
3157.3167 | 493.1031 | 511.5522 | 508.9661
3158.3167 | 492.9844 | 510.9811 | 508.3952
3159.3167 | 493.0718 | 510.1932 | 508.7453
3160.3167 | 492.9046 | 509.1849 | 508.5991
3161.3167 | 492.5728 | 509.122 | 507.2315
3162.3167 | 492.2719 | 508.828 | 506.424
3163.3167 | 492.2456 | 508.6032 | 506.5751
3164.3167 | 492.5669 | 508.1101 | 506.0842
3165.3167 | 492.7815 | 507.0856 | 505.489
3166.3167 | 492.5823 | 507.4659 | 506.0492
3167.3167 | 492.4975 | 507.2128 | 506.328
3168.3167 | 492.441 | 506.5032 | 506.2914
3169.3167 | 492.252 | 506.3362 | 506.7446
3170.3167 | 491.8733 | 505.8496 | 506.1009
3171.3167 | 491.5488 | 506.2327 | 506.7629
3172.3167 | 491.3577 | 506.8205 | 507.6133
3173.3167 | 491.174 | 507.3595 | 507.3869
3174.3167 | 491.0916 | 506.5497 | 506.7892
3175.3167 | 491.7363 | 506.2172 | 506.2782
3176.3167 | 491.9683 | 506.2777 | 506.9116
3177.3167 | 492.2061 | 505.4063 | 507.0423
3178.3167 | 492.5117 | 504.8212 | 506.0613
3179.3167 | 493.0742 | 505.8431 | 506.2902
3180.3167 | 494.2008 | 505.9881 | 506.4916
3181.3167 | 494.3836 | 505.2813 | 506.4477
3182.3167 | 494.7602 | 505.047 | 506.6652
3183.3167 | 495.4631 | 506.0343 | 507.5401
3184.3167 | 495.7563 | 507.0933 | 507.2002
3185.3167 | 495.6826 | 507.5798 | 507.7398
3186.3167 | 495.4729 | 508.8312 | 508.2727
3187.3167 | 495.2807 | 510.1895 | 507.5402
3188.3167 | 495.0951 | 510.5523 | 509.0396
3189.3167 | 495.17 | 510.0194 | 508.6493
3190.3167 | 494.9631 | 509.8705 | 508.9386
3191.3167 | 495.0859 | 510.3065 | 509.278
3192.3167 | 495.3186 | 513.3562 | 510.7893
3193.3167 | 495.9061 | 516.6535 | 511.0007
3194.3167 | 496.2224 | 518.1376 | 511.9624
3195.3167 | 496.1741 | 516.6396 | 512.3765
3196.3167 | 495.7854 | 516.6028 | 511.1865
3197.3167 | 495.5452 | 516.6824 | 510.2421
3198.3167 | 495.7651 | 516.6389 | 511.0081
3199.3167 | 496.4402 | 516.6257 | 510.735
3200.3167 | 496.9575 | 516.2134 | 510.4074
3201.3167 | 497.1113 | 515.5728 | 511.4519
3202.3167 | 497.0838 | 517.7685 | 512.6358
3203.3167 | 496.9909 | 518.253 | 512.2057
3204.3167 | 497.1855 | 516.1829 | 512.1353
3205.3167 | 497.0195 | 514.157 | 512.2505
3206.3167 | 496.7691 | 512.7594 | 511.4338
3207.3167 | 496.6469 | 512.1829 | 511.1985
3208.3167 | 497.0859 | 513.081 | 510.1248
3209.3167 | 496.825 | 512.0421 | 509.355
3210.3167 | 496.7399 | 511.3468 | 508.9387
3211.3167 | 497.1248 | 511.867 | 508.9498
3212.3167 | 497.3538 | 514.106 | 509.074
3213.3167 | 497.4829 | 516.0134 | 509.1245
3214.3167 | 497.4027 | 515.0735 | 508.3583
3215.3167 | 497.5728 | 514.6229 | 507.8766
3216.3167 | 497.543 | 515.5198 | 507.7541
3217.3167 | 497.1947 | 516.2298 | 507.1185
3218.3167 | 496.6855 | 517.5223 | 506.3159
3219.3167 | 496.538 | 517.1596 | 505.6065
3220.3167 | 496.1026 | 517.1477 | 505.6515
3221.3167 | 495.6114 | 516.1204 | 506.3387
3222.3167 | 494.9478 | 514.6331 | 506.2093
3223.3167 | 494.692 | 513.9895 | 506.1305
3224.3167 | 495.2641 | 514.3352 | 505.9477
3225.3167 | 495.8761 | 514.8755 | 505.7807
3226.3167 | 496.4069 | 515.5991 | 505.1439
3227.3167 | 496.5285 | 515.9312 | 504.6527
3228.3167 | 496.2935 | 516.4705 | 504.8366
3229.3167 | 496.5972 | 519.2726 | 506.0394
3230.3167 | 496.8247 | 519.557 | 506.0171
3231.3167 | 496.9663 | 521.577 | 508.208
3232.3167 | 496.8996 | 522.1974 | 508.1037
3233.3167 | 497.0258 | 521.4005 | 508.1554
3234.3167 | 497.1198 | 521.4305 | 509.5126
3235.3167 | 497.1676 | 520.5931 | 510.4689
3236.3167 | 497.1593 | 520.0596 | 509.6355
3237.3167 | 496.959 | 520.6002 | 509.9302
3238.3167 | 496.6646 | 519.351 | 510.1069
3239.3167 | 496.3678 | 517.539 | 509.6409
3240.3167 | 496.2664 | 515.6471 | 509.9953
3241.3167 | 496.731 | 514.6171 | 510.6104
3242.3167 | 497.4346 | 516.1753 | 510.255
3243.3167 | 497.9747 | 516.7768 | 511.0288
3244.3167 | 498.0146 | 515.1449 | 512.996
3245.3167 | 498.321 | 515.1895 | 512.7008
3246.3167 | 498.595 | 516.7974 | 512.4653
3247.3167 | 498.6845 | 516.6299 | 512.6098
3248.3167 | 498.7299 | 516.1421 | 512.0608
3249.3167 | 498.5413 | 514.8954 | 511.2776
3250.3167 | 498.3146 | 512.7237 | 510.0242
3251.3167 | 498.1308 | 512.3652 | 509.5412
3252.3167 | 498.2638 | 512.2424 | 509.4659
3253.3167 | 498.5859 | 513.0756 | 508.3557
3254.3167 | 498.6658 | 512.1585 | 507.2325
3255.3167 | 498.4294 | 511.8654 | 507.322
3256.3167 | 498.0402 | 510.5892 | 507.4858
3257.3167 | 498.0313 | 511.2891 | 506.8522
3258.3167 | 498.2701 | 510.9411 | 506.6003
3259.3167 | 498.5515 | 509.9203 | 506.8847
3260.3167 | 498.3589 | 509.3201 | 506.3581
3261.3167 | 498.2045 | 509.507 | 505.8983
3262.3167 | 498.0885 | 509.3749 | 504.8603
3263.3167 | 498.1974 | 510.4837 | 505.2971
3264.3167 | 498.2276 | 510.5543 | 506.4488
3265.3167 | 498.319 | 511.6854 | 506.6467
3266.3167 | 498.2929 | 510.7539 | 505.6763
3267.3167 | 498.2238 | 510.564 | 505.1996
3268.3167 | 498.9719 | 509.1379 | 505.7234
3269.3167 | 499.2996 | 509.3151 | 505.9173
3270.3167 | 499.4658 | 508.2004 | 505.6388
3271.3167 | 499.5473 | 507.2563 | 505.689
3272.3167 | 499.7822 | 508.9806 | 505.5046
3273.3167 | 499.9446 | 509.063 | 504.655
3274.3167 | 500.1212 | 508.4658 | 504.7774
3275.3167 | 500.2436 | 510.2324 | 505.3883
3276.3167 | 500.1682 | 510.0059 | 505.4406
3277.3167 | 500.2024 | 509.7768 | 505.0784
3278.3167 | 499.9776 | 508.7845 | 504.4879
3279.3167 | 499.653 | 508.8192 | 503.9513
3280.3167 | 499.9479 | 509.4557 | 503.8604
3281.3167 | 500.3026 | 510.5025 | 503.8595
3282.3167 | 500.4918 | 510.1712 | 504.1631
3283.3167 | 500.4481 | 510.7722 | 506.4444
3284.3167 | 500.4003 | 511.1801 | 505.8226
3285.3167 | 500.2315 | 512.0862 | 506.9371
3286.3167 | 500.1433 | 511.1282 | 506.8368
3287.3167 | 500.2821 | 512.579 | 505.7789
3288.3167 | 500.129 | 513.3283 | 507.024
3289.3167 | 499.9363 | 514.5525 | 506.4324
3290.3167 | 499.5954 | 513.5423 | 505.9553
3291.3167 | 499.9294 | 513.3803 | 505.8232
3292.3167 | 499.7544 | 513.9772 | 504.6309
3293.3167 | 499.2482 | 513.5969 | 503.2135
3294.3167 | 499.0139 | 512.4119 | 502.8946
3295.3167 | 499.2145 | 511.7295 | 503.4833
3296.3167 | 499.5734 | 511.0329 | 503.7179
3297.3167 | 499.8785 | 510.7345 | 504.6195
3298.3167 | 500.0454 | 512.432 | 505.6206
3299.3167 | 499.9842 | 511.9252 | 505.0329
3300.3167 | 499.6767 | 510.4197 | 505.6309