## Test Conditions
DESIREE-FIRE Intermediate Scale Test 8 - Circuit Data Only
Test Date: | 2009-11-17
DCSim DAQ Start Time | 10:35
DCSim Time for Synchronization | 10:38
Heat Source Synchronization | 0:03 | hours:minutes:seconds
Heat Source DAQ Start Time | 10:35
Fire Time | 11:34
Offset | 0:59 | hours:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 3565 | seconds
Heat Source Offset | 0:59 | hours:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 3568 | seconds
Heat Source Stop Time | 12:16
Test Duration | 0:42 | hours:minutes:seconds
| 2495 | seconds
CT500 turns | 2 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 turns | 5 | 1 or 5
Pre-Test Baseline: | Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
1" Solenoid Valve | PE/PVC, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 0 which is defined as "A Position - Middle" in the Temperature Data File respresents the temperature in the center of the cable tray.
Large Coil | PE/PVC, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 0 which is defined as "A Position - Middle" in the Temperature Data File respresents the temperature in the center of the cable tray.
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | 1"Coil_CT500 | 1"Coil_CT35_1_P | 1"Coil_CT35_2_G | 1"Coil_CT35_3_R | 1"Coil_CT35_4_N2 | 1"Coil_CT35_5_S | 1"Coil_CT35_6_N1 | LgCoil_CT500 | LgCoil_CT35_1_P | LgCoil_CT35_2_G | LgCoil_CT35_3_N2 | LgCoil_CT35_4_S | LgCoil_CT35_5_N1 | 1"Coil_VT7_1_G | 1"Coil_VT7_2_R | 1"Coil_VT7_3_SP | 1"Coil_VT7_4_S | 1"Coil_VTU_1_P | 1"Coil_VTU_2_N2 | 1"Coil_VTU_3_N1 | LgCoil_VT7_1_R | LgCoil_VT7_2_SP | LgCoil_VT7_3_S | LgCoil_VTU_1_P | LgCoil_VTU_2_G | LgCoil_VTU_3_N2 | LgCoil_VTU_4_N1 | {1"Valve} V(N2) - V(Batt -) | {1"Valve} V(N1) - V(Batt -) | {1"Valve} V(P) - V(Batt +) | {1"Valve} V(R) - V(Batt -) | {1"Valve} V(S) - V(Batt -) | {1"Valve} V(S) - V(N1) | {1"Valve} V(G) - V(Batt +) | {LgCoil} V(N2) - V(Batt -) | {LgCoil} V(N1) - V(Batt -) | {LgCoil} V(P) - V(Batt +) | {LgCoil} V(R) - V(Batt -) | {LgCoil} V(S) - V(Batt -) | {LgCoil} V(S) - V(N1) | {LgCoil} V(G) - V(Batt +) | {1"Valve} V(P) - V(Batt -) | {1"Valve} V(G) - V(Batt -) | {1"Valve} V(SP) - V(Batt -) | {1"Valve} V(N1) - V(Batt +) | {LgCoil} V(P) - V(Batt -) | {LgCoil} V(G) - V(Batt -) | {LgCoil} V(SP) - V(Batt -) | {LgCoil} V(N1) - V(Batt +)
-1.5156 | 121.7834 | -61.7889 | 59.8022 | -0.16907 | 0.0051825 | 0.063162 | 0.065849 | 0.12802 | -0.00088448 | -0.0022707 | -0.069428 | -0.0066436 | 0.05936 | 0.068274 | 0.0014164 | -0.0045053 | 59.9716 | 59.9121 | 0.10986 | -61.8668 | 59.642 | -61.7661 | -61.6699 | -61.5875 | 0.11444 | -62.1094 | 59.642 | 59.6741 | -61.5326 | -61.7661 | 0.022888 | 0.11902 | -0.16022 | 121.701 | -0.07782 | -0.19684 | 0.16937 | 0.25635 | 0.022888 | -0.16022 | 0.20142 | -0.32044 | -0.34332 | -0.12817 | 121.431 | 121.7606 | 61.8988 | -121.4722 | 121.431 | 121.463 | 61.9034 | -121.5683
0.23438 | 121.8613 | -61.7935 | 59.7427 | 0.090332 | 0.0056097 | 0.063162 | 0.06414 | 0.12952 | -0.00067088 | -0.0031253 | 0.1976 | -0.0060028 | 0.057651 | 0.069128 | 0.0031254 | -0.0055735 | 59.8984 | 59.816 | -0.082397 | -61.9629 | 59.5505 | -61.8576 | -61.7752 | -61.6379 | -0.10071 | -62.1872 | 59.5505 | 59.5871 | -61.6058 | -61.8393 | -0.064087 | 0.01831 | -0.19226 | 121.6095 | -0.16937 | -0.18768 | 0.15564 | 0.18768 | -0.045776 | -0.19226 | 0.15564 | -0.39368 | -0.3479 | -0.15564 | 121.344 | 121.6919 | 61.7111 | -121.5179 | 121.344 | 121.3806 | 61.6928 | -121.582
1.9844 | 121.8979 | -61.6882 | 59.8434 | -0.092773 | 0.0062505 | 0.062735 | 0.06649 | 0.12717 | -0.0072931 | -0.0054751 | 0.052643 | -0.0085662 | 0.059787 | 0.066779 | -7.9008e-05 | -0.0053599 | 60.0906 | 60.0861 | 0.24719 | -61.7615 | 59.6237 | -61.7203 | -61.6058 | -61.4136 | 0.2655 | -61.9263 | 59.6237 | 59.6741 | -61.4548 | -61.6745 | -0.032044 | 0.082397 | -0.21973 | 121.7743 | -0.073243 | -0.15564 | 0.24719 | 0.23346 | 0.013732 | -0.21973 | 0.27466 | -0.23804 | -0.25177 | -0.16937 | 121.3119 | 121.7789 | 61.9354 | -121.4493 | 121.3119 | 121.3623 | 61.9537 | -121.5179
3.6562 | 121.8567 | -61.7889 | 59.7427 | 0.097962 | 0.0051825 | 0.064444 | 0.060509 | 0.1261 | 0.00082452 | -0.0026981 | 0.13657 | -0.0096344 | 0.055301 | 0.067847 | 0.0041934 | -0.0057871 | 59.8892 | 59.816 | -0.10986 | -61.9537 | 59.5779 | -61.8622 | -61.7798 | -61.6425 | -0.10529 | -62.1964 | 59.5596 | 59.5871 | -61.6333 | -61.8439 | -0.073243 | 0.009155 | -0.16479 | 121.6049 | -0.1648 | -0.17395 | 0.14648 | 0.15564 | -0.054932 | -0.18311 | 0.14648 | -0.40741 | -0.35248 | -0.15564 | 121.3669 | 121.6782 | 61.6791 | -121.5225 | 121.3486 | 121.376 | 61.6837 | -121.5866
5.3906 | 121.8704 | -61.7661 | 59.7244 | 0.12848 | 0.0049689 | 0.063375 | 0.06414 | 0.12631 | -2.988e-05 | -0.0037661 | 0.21286 | -0.0062164 | 0.059573 | 0.069769 | 0.004407 | -0.0051463 | 59.903 | 59.8389 | -0.086975 | -61.9675 | 59.5413 | -61.8622 | -61.7661 | -61.6196 | -0.082397 | -62.1689 | 59.5322 | 59.5596 | -61.6104 | -61.8439 | -0.096131 | 0 | -0.1831 | 121.6049 | -0.20142 | -0.20142 | 0.17853 | 0.15564 | -0.07782 | -0.19226 | 0.14648 | -0.40283 | -0.32501 | -0.16479 | 121.3074 | 121.669 | 61.6791 | -121.4905 | 121.2982 | 121.3257 | 61.6837 | -121.5683
7.125 | 121.8796 | -61.7615 | 59.761 | 0.159 | 0.0039007 | 0.062948 | 0.06179 | 0.1293 | -0.0019525 | -0.0037661 | 0.2739 | -0.009848 | 0.058078 | 0.066565 | 0.0035526 | -0.0055735 | 59.9854 | 59.9625 | 0.022888 | -61.8622 | 59.5276 | -61.8164 | -61.7203 | -61.5601 | 0.009155 | -62.0728 | 59.5093 | 59.5367 | -61.5921 | -61.8118 | -0.054931 | 0.041199 | -0.23346 | 121.7239 | -0.10071 | -0.14191 | 0.22431 | 0.16937 | -0.050354 | -0.25177 | 0.20142 | -0.31128 | -0.26093 | -0.2243 | 121.2891 | 121.7468 | 61.7844 | -121.4813 | 121.2708 | 121.2982 | 61.7706 | -121.5729
8.875 | 121.7743 | -61.8073 | 59.7519 | -0.069885 | 0.0086005 | 0.063589 | 0.064568 | 0.12845 | 0.00061092 | -0.0020571 | -0.031281 | -0.0074982 | 0.057437 | 0.067633 | 0.0022708 | -0.0045053 | 59.967 | 59.935 | 0.07782 | -61.908 | 59.5963 | -61.8164 | -61.7203 | -61.5738 | 0.068665 | -62.114 | 59.5871 | 59.6054 | -61.5601 | -61.7981 | -0.009155 | 0.086975 | -0.15564 | 121.7422 | -0.10071 | -0.18768 | 0.21515 | 0.24719 | 0.009155 | -0.16479 | 0.23346 | -0.3067 | -0.31586 | -0.14648 | 121.4035 | 121.7743 | 61.8851 | -121.4722 | 121.3943 | 121.4127 | 61.8759 | -121.55
10.5469 | 121.8842 | -61.6745 | 59.8251 | 0.044556 | 0.0047553 | 0.064871 | 0.063713 | 0.12802 | -0.0081477 | -0.0046207 | 0.08316 | -0.0094208 | 0.058078 | 0.064429 | 0.00056179 | -0.0042917 | 59.9899 | 60.0128 | 0.10986 | -61.8301 | 59.6054 | -61.7386 | -61.6241 | -61.5189 | 0.10529 | -62.027 | 59.6237 | 59.6558 | -61.5051 | -61.7203 | -0.064086 | 0.050354 | -0.21973 | 121.6873 | -0.15564 | -0.20599 | 0.16479 | 0.16937 | -0.045776 | -0.20142 | 0.15564 | -0.35248 | -0.3067 | -0.16937 | 121.2799 | 121.6644 | 61.7844 | -121.4493 | 121.2982 | 121.3303 | 61.7798 | -121.5454
12.2812 | 121.8796 | -61.7111 | 59.8251 | 0.021668 | 0.0030463 | 0.06423 | 0.06179 | 0.12866 | -0.0053705 | -0.0076113 | 0.11368 | -0.010275 | 0.058932 | 0.06571 | -0.00093361 | -0.0049325 | 59.9991 | 59.9899 | 0.10986 | -61.8256 | 59.6146 | -61.734 | -61.6379 | -61.496 | 0.13733 | -61.9995 | 59.6146 | 59.6283 | -61.4868 | -61.702 | -0.022888 | 0.073243 | -0.21057 | 121.701 | -0.11444 | -0.18768 | 0.17395 | 0.22431 | 0.009156 | -0.21057 | 0.21515 | -0.28839 | -0.29755 | -0.19684 | 121.3257 | 121.7102 | 61.821 | -121.463 | 121.3257 | 121.3394 | 61.8484 | -121.5271
14.0312 | 121.7514 | -61.7294 | 59.8709 | -0.15381 | 0.0047553 | 0.063162 | 0.065208 | 0.12802 | -0.0025935 | -0.0059023 | -0.092316 | -0.0085662 | 0.060214 | 0.067847 | -0.00093361 | -0.0064279 | 60.0906 | 60.0632 | 0.2655 | -61.7615 | 59.6466 | -61.7065 | -61.615 | -61.4822 | 0.23346 | -62.0132 | 59.6695 | 59.6878 | -61.441 | -61.6653 | 0.022888 | 0.11444 | -0.22431 | 121.7926 | -0.032044 | -0.14648 | 0.21973 | 0.28839 | 0.064087 | -0.20142 | 0.24719 | -0.28381 | -0.3479 | -0.18311 | 121.376 | 121.8201 | 61.9949 | -121.4859 | 121.3989 | 121.4172 | 61.9629 | -121.5363
15.7812 | 121.8338 | -61.734 | 59.7977 | 0.097962 | 0.0032599 | 0.062521 | 0.059654 | 0.12653 | -0.00088448 | -0.0063297 | 0.22049 | -0.0085662 | 0.056582 | 0.06571 | 0.0035526 | -0.0042917 | 60.0037 | 59.9899 | 0.059509 | -61.8576 | 59.5367 | -61.7798 | -61.6837 | -61.5143 | 0.054932 | -62.0453 | 59.5871 | 59.5917 | -61.5234 | -61.734 | -0.045776 | 0.050354 | -0.26093 | 121.7239 | -0.1236 | -0.17395 | 0.20599 | 0.21057 | 0 | -0.21057 | 0.21973 | -0.31128 | -0.31128 | -0.20599 | 121.2708 | 121.7377 | 61.7935 | -121.4813 | 121.3211 | 121.3257 | 61.7889 | -121.5317
17.4688 | 121.7468 | -61.8347 | 59.7519 | -0.062256 | 0.0066779 | 0.062307 | 0.062431 | 0.12482 | 0.0046697 | -0.0035525 | -0.03891 | -0.0060028 | 0.056582 | 0.066992 | 0.003339 | -0.0072825 | 59.9945 | 59.9213 | 0.064087 | -61.8896 | 59.5963 | -61.8301 | -61.7157 | -61.5738 | 0.050354 | -62.1185 | 59.5825 | 59.61 | -61.5738 | -61.8164 | 0.004578 | 0.11902 | -0.15564 | 121.756 | -0.054931 | -0.17395 | 0.24262 | 0.26093 | 0.018311 | -0.16937 | 0.26093 | -0.28381 | -0.30212 | -0.14191 | 121.431 | 121.8292 | 61.8988 | -121.4676 | 121.4172 | 121.4447 | 61.8851 | -121.5683
19.2188 | 121.875 | -61.6699 | 59.8526 | -0.062256 | 0.0049689 | 0.063803 | 0.065636 | 0.12738 | -0.0066523 | -0.0056887 | -0.00076274 | -0.010275 | 0.058719 | 0.06806 | -0.0013608 | -0.0057871 | 60.0952 | 60.0861 | 0.24261 | -61.7432 | 59.6283 | -61.7111 | -61.6013 | -61.4182 | 0.24719 | -61.9354 | 59.6329 | 59.6558 | -61.4456 | -61.6699 | -0.041199 | 0.068665 | -0.2243 | 121.756 | -0.073242 | -0.14191 | 0.24262 | 0.2243 | 0 | -0.21973 | 0.25177 | -0.2655 | -0.2655 | -0.19684 | 121.2982 | 121.7651 | 61.9125 | -121.4539 | 121.3028 | 121.3257 | 61.9171 | -121.5225
20.8906 | 121.7697 | -61.821 | 59.7427 | -0.031738 | 0.0086005 | 0.063375 | 0.062859 | 0.1308 | 0.0046697 | -0.0031253 | -0.054169 | -0.0072846 | 0.057651 | 0.070196 | 0.0046206 | -0.0072825 | 59.9899 | 59.9167 | 0.07782 | -61.8942 | 59.5871 | -61.8118 | -61.7203 | -61.5601 | 0.073242 | -62.114 | 59.61 | 59.5917 | -61.5692 | -61.7752 | 0.009155 | 0.10071 | -0.15564 | 121.7377 | -0.073242 | -0.17395 | 0.24719 | 0.25177 | 0.045776 | -0.13275 | 0.26093 | -0.29297 | -0.33875 | -0.15106 | 121.4081 | 121.8109 | 61.8988 | -121.463 | 121.431 | 121.4127 | 61.8942 | -121.5179
22.6406 | 121.756 | -61.8439 | 59.7565 | 0.059815 | 0.0051825 | 0.062948 | 0.063286 | 0.12802 | 0.0025335 | -0.00013452 | 0.08316 | -0.0072846 | 0.057864 | 0.069556 | 0.003339 | -0.0040781 | 59.8846 | 59.7931 | -0.07782 | -61.9583 | 59.5688 | -61.8622 | -61.7523 | -61.6974 | -0.10071 | -62.2559 | 59.5825 | 59.5825 | -61.6013 | -61.8484 | -0.018311 | 0.091553 | -0.18768 | 121.637 | -0.11444 | -0.20599 | 0.12817 | 0.24262 | -0.004578 | -0.17395 | 0.14648 | -0.41199 | -0.40741 | -0.17395 | 121.4127 | 121.7285 | 61.7661 | -121.5088 | 121.4264 | 121.4264 | 61.7432 | -121.6049
24.3906 | 121.8475 | -61.6608 | 59.8434 | -0.13092 | 0.0066779 | 0.064444 | 0.067345 | 0.1246 | -0.0051569 | -0.0061161 | -0.031281 | -0.0072846 | 0.057437 | 0.06571 | -0.0020016 | -0.0062143 | 60.1135 | 60.1227 | 0.29297 | -61.7432 | 59.642 | -61.6837 | -61.5829 | -61.3998 | 0.31586 | -61.9263 | 59.6283 | 59.6878 | -61.4456 | -61.6653 | -0.022888 | 0.07782 | -0.20142 | 121.7834 | -0.082397 | -0.16022 | 0.27008 | 0.21515 | -0.004577 | -0.21515 | 0.26093 | -0.2655 | -0.26093 | -0.15564 | 121.3028 | 121.7743 | 61.9537 | -121.4264 | 121.2891 | 121.3486 | 61.9766 | -121.5088
26.0625 | 121.8475 | -61.6882 | 59.8434 | -0.10803 | 0.0051825 | 0.062307 | 0.063713 | 0.12759 | -0.0043023 | -0.0052615 | -0.03891 | -0.011343 | 0.06 | 0.067633 | -0.001788 | -0.0053599 | 60.0952 | 60.1135 | 0.27008 | -61.7386 | 59.642 | -61.7065 | -61.5875 | -61.409 | 0.31586 | -61.9354 | 59.642 | 59.6786 | -61.4456 | -61.6608 | -0.018311 | 0.10071 | -0.20142 | 121.8018 | -0.050354 | -0.15106 | 0.25177 | 0.24261 | 0.027465 | -0.20142 | 0.27923 | -0.24719 | -0.27466 | -0.1648 | 121.3303 | 121.7834 | 61.9583 | -121.431 | 121.3303 | 121.3669 | 62.0041 | -121.5042
27.8125 | 121.875 | -61.7569 | 59.7336 | 0.15137 | 0.0036871 | 0.062948 | 0.057091 | 0.12674 | -0.00088448 | -0.0020571 | 0.22049 | -0.0089936 | 0.056796 | 0.065924 | 0.003339 | -0.0060007 | 59.9854 | 59.9579 | 0.018311 | -61.8759 | 59.5276 | -61.8118 | -61.7294 | -61.5417 | 0 | -62.0773 | 59.4864 | 59.5322 | -61.5738 | -61.7935 | -0.054932 | 0.027466 | -0.20599 | 121.7148 | -0.11902 | -0.14648 | 0.25177 | 0.18311 | -0.036621 | -0.24719 | 0.21515 | -0.32043 | -0.28381 | -0.20142 | 121.2845 | 121.7422 | 61.7752 | -121.463 | 121.2433 | 121.2891 | 61.7569 | -121.5271
29.5625 | 121.8384 | -61.7432 | 59.7427 | 0.16663 | 0.0041143 | 0.062735 | 0.061577 | 0.12888 | 0.00039732 | -0.0041933 | 0.24338 | -0.010275 | 0.058078 | 0.066565 | 0.0029116 | -0.0064279 | 59.9762 | 59.9533 | 0.022888 | -61.8896 | 59.5139 | -61.8164 | -61.7569 | -61.5234 | 0.032043 | -62.0636 | 59.5322 | 59.5276 | -61.5829 | -61.7981 | -0.073242 | -0.013733 | -0.22888 | 121.6965 | -0.14648 | -0.13275 | 0.23346 | 0.16022 | -0.054932 | -0.21057 | 0.21973 | -0.32044 | -0.2655 | -0.21515 | 121.257 | 121.7194 | 61.7661 | -121.4996 | 121.2753 | 121.2708 | 61.7752 | -121.5408
31.25 | 121.8887 | -61.6653 | 59.8526 | -0.031738 | 0.0051825 | 0.063589 | 0.065422 | 0.13037 | -0.0053705 | -0.0041933 | 0.037384 | -0.0092072 | 0.058719 | 0.068915 | -0.00071981 | -0.0072825 | 60.0632 | 60.0449 | 0.18768 | -61.7752 | 59.6237 | -61.7111 | -61.6196 | -61.4136 | 0.24261 | -61.9263 | 59.6695 | 59.6878 | -61.4273 | -61.6974 | -0.045777 | 0.045776 | -0.22888 | 121.7102 | -0.10986 | -0.15564 | 0.21057 | 0.23804 | -0.032044 | -0.18311 | 0.25177 | -0.26093 | -0.22888 | -0.1648 | 121.2891 | 121.7285 | 61.853 | -121.4722 | 121.3348 | 121.3531 | 61.908 | -121.55
33 | 121.788 | -61.8256 | 59.7061 | 0.13611 | 0.0062505 | 0.061026 | 0.063713 | 0.12802 | 0.0018927 | -0.0014163 | 0.13657 | -0.0077118 | 0.059146 | 0.069128 | 0.0048344 | -0.0072825 | 59.8709 | 59.7977 | -0.12817 | -61.9904 | 59.5413 | -61.8759 | -61.7889 | -61.6516 | -0.11902 | -62.2055 | 59.5734 | 59.5779 | -61.6196 | -61.8576 | -0.050354 | 0.036622 | -0.16479 | 121.6232 | -0.16479 | -0.20142 | 0.16479 | 0.20599 | -0.032043 | -0.13275 | 0.17395 | -0.37994 | -0.3479 | -0.12817 | 121.3669 | 121.6965 | 61.6974 | -121.4951 | 121.3989 | 121.4035 | 61.7065 | -121.5637
34.6719 | 121.7697 | -61.6974 | 59.8755 | -0.16144 | 0.0071051 | 0.063803 | 0.063927 | 0.1293 | -0.0043023 | -0.0037661 | -0.031281 | -0.009848 | 0.056796 | 0.063788 | 0.00034819 | -0.0051463 | 60.0998 | 60.0906 | 0.27466 | -61.7661 | 59.6237 | -61.7065 | -61.6287 | -61.441 | 0.28381 | -61.9583 | 59.6283 | 59.6512 | -61.4777 | -61.6882 | -0.009155 | 0.068665 | -0.25177 | 121.788 | -0.068664 | -0.13733 | 0.2243 | 0.21973 | 0.009156 | -0.24719 | 0.25635 | -0.26093 | -0.27008 | -0.2243 | 121.3211 | 121.7972 | 61.972 | -121.5042 | 121.3257 | 121.3486 | 61.9812 | -121.5637
36.4219 | 121.7377 | -61.7111 | 59.8755 | -0.1767 | 0.0075323 | 0.063589 | 0.06414 | 0.12845 | -0.0017389 | -0.0065433 | -0.099945 | -0.0092072 | 0.06 | 0.069769 | 0.00077539 | -0.0083505 | 60.0311 | 59.967 | 0.16937 | -61.8301 | 59.6558 | -61.7203 | -61.6241 | -61.5372 | 0.16022 | -62.0636 | 59.6512 | 59.697 | -61.4868 | -61.7157 | -0.009155 | 0.086975 | -0.21973 | 121.6782 | -0.11902 | -0.20599 | 0.15564 | 0.22431 | -0.004577 | -0.2243 | 0.17395 | -0.35248 | -0.3479 | -0.17853 | 121.3669 | 121.7422 | 61.8805 | -121.4996 | 121.3623 | 121.4081 | 61.8713 | -121.5912
38.1719 | 121.8658 | -61.6745 | 59.8389 | -0.077515 | 0.0051825 | 0.064016 | 0.065422 | 0.12781 | -0.0057977 | -0.0048343 | -0.00076274 | -0.010062 | 0.058291 | 0.066565 | -0.00071981 | -0.0047189 | 60.1181 | 60.1044 | 0.26093 | -61.7477 | 59.6283 | -61.6928 | -61.6013 | -61.4044 | 0.29297 | -61.9263 | 59.6375 | 59.6695 | -61.4319 | -61.6745 | -0.01831 | 0.073243 | -0.21057 | 121.7789 | -0.073242 | -0.14649 | 0.27924 | 0.24262 | 0 | -0.20142 | 0.27008 | -0.25177 | -0.25177 | -0.16937 | 121.3028 | 121.7926 | 61.9354 | -121.4401 | 121.312 | 121.344 | 61.9675 | -121.5134
39.9062 | 121.7514 | -61.7477 | 59.8389 | -0.1767 | 0.0060369 | 0.063162 | 0.06649 | 0.12546 | 0.0012519 | -0.0061161 | -0.14572 | -0.0079254 | 0.056369 | 0.069128 | 0.00077539 | -0.0072825 | 60.0037 | 59.9579 | 0.14648 | -61.8668 | 59.6603 | -61.7294 | -61.6653 | -61.528 | 0.16022 | -62.0911 | 59.7061 | 59.7336 | -61.4822 | -61.7111 | 0.018311 | 0.082398 | -0.17853 | 121.7056 | -0.11902 | -0.20142 | 0.16479 | 0.2655 | 0.036621 | -0.13275 | 0.21973 | -0.34332 | -0.37994 | -0.10529 | 121.4081 | 121.7514 | 61.8942 | -121.5042 | 121.4539 | 121.4813 | 61.908 | -121.55
41.5938 | 121.8292 | -61.7386 | 59.761 | 0.14374 | 0.0049689 | 0.062307 | 0.059013 | 0.12524 | -0.0021661 | -0.0041933 | 0.18234 | -0.008139 | 0.056582 | 0.067847 | 0.003339 | -0.0070689 | 59.9945 | 59.9854 | 0.041199 | -61.8622 | 59.5367 | -61.8027 | -61.7065 | -61.5143 | 0.041199 | -62.0361 | 59.5413 | 59.5596 | -61.5326 | -61.7615 | -0.064087 | 0.032043 | -0.2243 | 121.7239 | -0.1236 | -0.15564 | 0.23346 | 0.20599 | -0.022889 | -0.21973 | 0.2243 | -0.29755 | -0.27466 | -0.20142 | 121.2753 | 121.7331 | 61.7798 | -121.4676 | 121.2799 | 121.2982 | 61.7798 | -121.5225
43.3438 | 121.7789 | -61.7844 | 59.7794 | -0.13092 | 0.0081733 | 0.063375 | 0.063286 | 0.12695 | 0.00082452 | -0.0026981 | -0.13046 | -0.00643 | 0.057864 | 0.067206 | 0.0037662 | -0.0055735 | 59.9762 | 59.9213 | 0.10986 | -61.853 | 59.6237 | -61.7798 | -61.6745 | -61.5646 | 0.11444 | -62.114 | 59.6329 | 59.6237 | -61.5601 | -61.7752 | 0.004578 | 0.10986 | -0.15564 | 121.7056 | -0.068664 | -0.17853 | 0.19684 | 0.2243 | 0.009155 | -0.14648 | 0.21973 | -0.32959 | -0.33875 | -0.15564 | 121.4081 | 121.7606 | 61.8942 | -121.4539 | 121.4172 | 121.4081 | 61.8988 | -121.5546
45.0781 | 121.7239 | -61.8256 | 59.7519 | -0.046997 | 0.0056097 | 0.061453 | 0.062004 | 0.12759 | 0.0027471 | -0.0024845 | -0.00076274 | -0.0051484 | 0.057437 | 0.06806 | 0.0041934 | -0.0053599 | 59.9625 | 59.9304 | 0.045776 | -61.8851 | 59.5688 | -61.8256 | -61.734 | -61.5829 | 0.032043 | -62.1414 | 59.5779 | 59.5963 | -61.5646 | -61.8118 | 0 | 0.091553 | -0.1831 | 121.756 | -0.059509 | -0.15106 | 0.21057 | 0.26093 | 0.013733 | -0.17395 | 0.24262 | -0.31586 | -0.32959 | -0.15564 | 121.3943 | 121.788 | 61.8713 | -121.4859 | 121.4035 | 121.4218 | 61.8576 | -121.5637
46.75 | 121.8201 | -61.7477 | 59.7839 | 0.11322 | 0.0032599 | 0.063589 | 0.059868 | 0.12802 | -0.0043023 | -0.0029117 | 0.20523 | -0.010489 | 0.056369 | 0.067847 | 0.0029116 | -0.0036509 | 59.9808 | 59.9716 | 0.054932 | -61.8576 | 59.5322 | -61.7706 | -61.6882 | -61.528 | 0.054932 | -62.0453 | 59.5322 | 59.5642 | -61.5463 | -61.7706 | -0.022888 | 0.05951 | -0.25177 | 121.7194 | -0.10986 | -0.16937 | 0.19684 | 0.20142 | -0.022888 | -0.25177 | 0.21973 | -0.29755 | -0.27466 | -0.21973 | 121.2799 | 121.7285 | 61.8027 | -121.4722 | 121.2799 | 121.312 | 61.8027 | -121.5546
48.5 | 121.7514 | -61.8164 | 59.7336 | -0.046997 | 0.0086005 | 0.062094 | 0.067345 | 0.12589 | 0.0012519 | -0.0033389 | -0.054169 | -0.0092072 | 0.05936 | 0.067847 | 0.0020572 | -0.0077097 | 59.967 | 59.9167 | 0.068665 | -61.8805 | 59.5825 | -61.8073 | -61.7111 | -61.5692 | 0.07782 | -62.1231 | 59.5734 | 59.5825 | -61.5692 | -61.7889 | 0.009155 | 0.10529 | -0.15106 | 121.7331 | -0.064087 | -0.16937 | 0.23346 | 0.24719 | 0.027466 | -0.16022 | 0.24719 | -0.3067 | -0.33417 | -0.15106 | 121.3989 | 121.7834 | 61.8851 | -121.4447 | 121.3898 | 121.3989 | 61.8942 | -121.5225
50.2344 | 121.875 | -61.7752 | 59.7153 | 0.18188 | 0.0026191 | 0.059958 | 0.06414 | 0.12866 | -0.0015253 | -0.0039797 | 0.22049 | -0.00878 | 0.057651 | 0.068487 | 0.00163 | -0.0042917 | 59.9716 | 59.9396 | 0 | -61.8759 | 59.5093 | -61.8118 | -61.7157 | -61.5372 | 0.009155 | -62.0682 | 59.5093 | 59.5505 | -61.5463 | -61.7844 | -0.036621 | 0.05951 | -0.20599 | 121.7148 | -0.10071 | -0.16022 | 0.25635 | 0.22888 | -0.009155 | -0.20599 | 0.23804 | -0.29297 | -0.28381 | -0.16479 | 121.2845 | 121.7468 | 61.7752 | -121.431 | 121.2845 | 121.3257 | 61.7844 | -121.4996
51.9844 | 121.7606 | -61.6928 | 59.8526 | -0.16144 | 0.0066779 | 0.065725 | 0.064781 | 0.12909 | -0.0055841 | -0.0035525 | -0.0083922 | -0.01113 | 0.057864 | 0.068915 | -0.00029261 | -0.0047189 | 60.0861 | 60.0906 | 0.27008 | -61.7661 | 59.6191 | -61.6745 | -61.6058 | -61.4502 | 0.27466 | -61.9629 | 59.6466 | 59.7061 | -61.4502 | -61.702 | 0.01831 | 0.086975 | -0.23346 | 121.7834 | -0.073242 | -0.16022 | 0.23346 | 0.24262 | -0.009155 | -0.20599 | 0.24262 | -0.27008 | -0.26093 | -0.14648 | 121.312 | 121.7789 | 61.9629 | -121.4584 | 121.3394 | 121.3989 | 61.9675 | -121.5546
53.6875 | 121.7468 | -61.7065 | 59.8892 | -0.16144 | 0.0068915 | 0.064016 | 0.064354 | 0.1293 | -0.0036615 | -0.0039797 | -0.13809 | -0.0092072 | 0.057223 | 0.067206 | 0.0020572 | -0.0064279 | 60.0815 | 60.0677 | 0.25635 | -61.7523 | 59.6558 | -61.6928 | -61.615 | -61.4914 | 0.24719 | -61.9949 | 59.6741 | 59.6741 | -61.4548 | -61.7065 | 0.013733 | 0.091553 | -0.23346 | 121.7743 | -0.045776 | -0.13733 | 0.19226 | 0.25177 | 0 | -0.21515 | 0.21515 | -0.28839 | -0.28839 | -0.21515 | 121.3623 | 121.788 | 61.9629 | -121.5042 | 121.3806 | 121.3806 | 61.9537 | -121.5958
55.4531 | 121.8613 | -61.7706 | 59.6924 | 0.18951 | 0.0047553 | 0.062948 | 0.06115 | 0.12781 | 0.0012519 | -0.0029117 | 0.17471 | -0.0083526 | 0.056582 | 0.06571 | 0.0031254 | -0.0049325 | 59.903 | 59.8526 | -0.068665 | -61.94 | 59.5505 | -61.8256 | -61.7523 | -61.5738 | -0.036621 | -62.1094 | 59.5276 | 59.523 | -61.5921 | -61.7981 | -0.054932 | 0.018311 | -0.14191 | 121.6232 | -0.16937 | -0.18768 | 0.21057 | 0.17853 | -0.027466 | -0.16479 | 0.19684 | -0.33875 | -0.31128 | -0.16937 | 121.3211 | 121.6736 | 61.702 | -121.4447 | 121.2982 | 121.2936 | 61.734 | -121.4905
57.1406 | 121.7834 | -61.7477 | 59.8022 | -0.13092 | 0.0039007 | 0.065939 | 0.064354 | 0.12567 | 0.00061092 | -0.0056887 | -0.13046 | -0.0092072 | 0.056369 | 0.066138 | 0.0020572 | -0.0055735 | 59.967 | 59.9304 | 0.1236 | -61.8484 | 59.6466 | -61.7661 | -61.6791 | -61.5829 | 0.11444 | -62.1048 | 59.6603 | 59.6786 | -61.5143 | -61.7477 | -0.01831 | 0.068665 | -0.15564 | 121.6782 | -0.10071 | -0.16937 | 0.1648 | 0.23346 | 0 | -0.14191 | 0.1648 | -0.35705 | -0.35705 | -0.1236 | 121.3943 | 121.7148 | 61.8713 | -121.4813 | 121.4081 | 121.4264 | 61.8622 | -121.55
58.8906 | 121.7972 | -61.6928 | 59.8709 | -0.16144 | 0.0064643 | 0.063803 | 0.065849 | 0.12589 | -0.0060113 | -0.0029117 | -0.046539 | -0.0096344 | 0.057223 | 0.06571 | -0.0013608 | -0.0049325 | 60.0906 | 60.1089 | 0.31586 | -61.7294 | 59.6237 | -61.6745 | -61.5829 | -61.4227 | 0.29297 | -61.9354 | 59.6558 | 59.6512 | -61.4548 | -61.6837 | 0.01831 | 0.10986 | -0.24719 | 121.8018 | -0.036621 | -0.14648 | 0.21973 | 0.23804 | 0.009155 | -0.21515 | 0.27008 | -0.24262 | -0.25177 | -0.21973 | 121.3165 | 121.7834 | 62.0087 | -121.4539 | 121.3486 | 121.344 | 61.9858 | -121.5546
60.625 | 121.843 | -61.6791 | 59.8343 | -0.077515 | 0.0064643 | 0.063589 | 0.063499 | 0.12717 | -0.0038751 | -0.0044071 | -0.0083922 | -0.0092072 | 0.058078 | 0.066992 | -0.00071981 | -0.0060007 | 60.0952 | 60.1273 | 0.27008 | -61.7477 | 59.6283 | -61.6882 | -61.5875 | -61.409 | 0.28839 | -61.908 | 59.6603 | 59.6741 | -61.4365 | -61.6562 | -0.009155 | 0.091553 | -0.20599 | 121.8063 | -0.068665 | -0.16022 | 0.26093 | 0.24262 | 0.022888 | -0.17395 | 0.27008 | -0.22888 | -0.25177 | -0.16022 | 121.3074 | 121.7743 | 61.9492 | -121.4218 | 121.3394 | 121.3531 | 61.9675 | -121.4905
62.3594 | 121.7377 | -61.702 | 59.8801 | -0.12329 | 0.0077459 | 0.064871 | 0.064354 | 0.12909 | -0.0023797 | -0.0046207 | -0.077057 | -0.009848 | 0.058932 | 0.064001 | 0.00034819 | -0.0051463 | 60.0815 | 60.0769 | 0.25635 | -61.7523 | 59.6191 | -61.6974 | -61.5967 | -61.4456 | 0.28381 | -61.9537 | 59.6558 | 59.6786 | -61.4685 | -61.6837 | 0.004577 | 0.10529 | -0.26093 | 121.7789 | -0.050354 | -0.15564 | 0.20142 | 0.23346 | 0.01831 | -0.2243 | 0.25635 | -0.25177 | -0.27008 | -0.20142 | 121.3211 | 121.7834 | 61.9583 | -121.4767 | 121.3577 | 121.3806 | 61.9858 | -121.5637
64.1094 | 121.843 | -61.7798 | 59.6924 | 0.12848 | 0.0041143 | 0.061666 | 0.06115 | 0.12567 | -0.0015253 | -0.0046207 | 0.18234 | -0.010703 | 0.05936 | 0.067419 | 0.0029116 | -0.0062143 | 59.8938 | 59.8389 | -0.086975 | -61.9492 | 59.5551 | -61.8439 | -61.7569 | -61.5967 | -0.082397 | -62.1506 | 59.5551 | 59.5413 | -61.5875 | -61.821 | -0.064087 | 0.022888 | -0.13733 | 121.6187 | -0.16937 | -0.19226 | 0.20142 | 0.19226 | -0.041199 | -0.13733 | 0.1831 | -0.37079 | -0.32959 | -0.15106 | 121.3348 | 121.6736 | 61.6928 | -121.4493 | 121.3348 | 121.3211 | 61.6974 | -121.5134
65.7969 | 121.8063 | -61.7203 | 59.8068 | 0.090332 | 0.0041143 | 0.064657 | 0.063927 | 0.12268 | -0.0045161 | -0.0052615 | 0.16708 | -0.0074982 | 0.06 | 0.067847 | 0.00098899 | -0.0055735 | 59.9808 | 59.9716 | 0.073242 | -61.8484 | 59.5505 | -61.7569 | -61.6608 | -61.5097 | 0.050354 | -62.0316 | 59.5871 | 59.5963 | -61.5051 | -61.7615 | -0.036621 | 0.059509 | -0.25635 | 121.6919 | -0.12817 | -0.18768 | 0.17395 | 0.21515 | -0.041199 | -0.21973 | 0.21057 | -0.31128 | -0.27008 | -0.21057 | 121.2708 | 121.701 | 61.7935 | -121.4676 | 121.3074 | 121.3165 | 61.7706 | -121.5683
67.5469 | 121.7102 | -61.821 | 59.7427 | -0.024109 | 0.0079595 | 0.061026 | 0.065208 | 0.12567 | 0.0031745 | -0.0024845 | 0.014496 | -0.0085662 | 0.058505 | 0.069769 | 0.0035526 | -0.0072825 | 59.9533 | 59.8892 | 0.022888 | -61.9125 | 59.5642 | -61.8256 | -61.7386 | -61.6333 | -0.027466 | -62.2101 | 59.5688 | 59.5825 | -61.5875 | -61.8301 | -0.004578 | 0.082398 | -0.17853 | 121.7102 | -0.091553 | -0.17395 | 0.21057 | 0.23346 | -0.009155 | -0.17395 | 0.18768 | -0.3891 | -0.37994 | -0.16022 | 121.3852 | 121.7743 | 61.8439 | -121.4813 | 121.3898 | 121.4035 | 61.7935 | -121.5729
69.2969 | 121.8109 | -61.6974 | 59.7931 | 0.12085 | 0.0032599 | 0.063375 | 0.063286 | 0.12546 | -0.0034479 | -0.0041933 | 0.21286 | -0.009848 | 0.056369 | 0.068915 | 0.00163 | -0.0062143 | 59.9716 | 59.9808 | 0.059509 | -61.8393 | 59.523 | -61.7935 | -61.6791 | -61.5005 | 0.045776 | -62.0453 | 59.5596 | 59.5551 | -61.5417 | -61.7706 | -0.09613 | 0.018311 | -0.27008 | 121.6782 | -0.14191 | -0.16022 | 0.17853 | 0.15564 | -0.073242 | -0.23346 | 0.19684 | -0.3479 | -0.27466 | -0.23804 | 121.2204 | 121.669 | 61.7569 | -121.4722 | 121.257 | 121.2524 | 61.7432 | -121.5637
71.0469 | 121.8475 | -61.6653 | 59.8389 | -0.1004 | 0.0053961 | 0.064657 | 0.066063 | 0.12695 | -0.0036615 | -0.0037661 | -0.031281 | -0.010916 | 0.057223 | 0.067847 | -0.0026426 | -0.0040781 | 60.0952 | 60.1135 | 0.2655 | -61.7569 | 59.6191 | -61.6745 | -61.5921 | -61.4044 | 0.28381 | -61.9171 | 59.6558 | 59.6695 | -61.4273 | -61.6791 | -0.009156 | 0.073242 | -0.21973 | 121.7789 | -0.091553 | -0.1648 | 0.25635 | 0.23804 | -0.013733 | -0.1831 | 0.26093 | -0.25177 | -0.23804 | -0.16937 | 121.2845 | 121.7606 | 61.9308 | -121.431 | 121.3211 | 121.3348 | 61.9492 | -121.5179
72.7188 | 121.7239 | -61.7203 | 59.8572 | -0.20721 | 0.0056097 | 0.063162 | 0.06414 | 0.12738 | -0.00067088 | -0.0041933 | -0.13046 | -0.00878 | 0.05936 | 0.069342 | 0.00098899 | -0.0064279 | 60.0494 | 60.0311 | 0.23346 | -61.7981 | 59.6375 | -61.7111 | -61.6104 | -61.5097 | 0.1831 | -62.0453 | 59.6786 | 59.6832 | -61.4777 | -61.6745 | 0.009155 | 0.10986 | -0.21973 | 121.7514 | -0.07782 | -0.18768 | 0.19226 | 0.24262 | 0.045776 | -0.17853 | 0.21057 | -0.32501 | -0.37079 | -0.17395 | 121.3577 | 121.7697 | 61.9537 | -121.4676 | 121.3989 | 121.4035 | 61.9034 | -121.5317
74.4688 | 121.7056 | -61.8347 | 59.761 | -0.024109 | 0.0066779 | 0.063589 | 0.063286 | 0.12567 | 0.0036017 | -0.0037661 | 0.029755 | -0.0079254 | 0.058505 | 0.069342 | 0.0054752 | -0.0085641 | 59.9304 | 59.8663 | 0.004578 | -61.9125 | 59.5596 | -61.821 | -61.7386 | -61.647 | -0.041199 | -62.1918 | 59.5551 | 59.5917 | -61.6013 | -61.8301 | 0.013733 | 0.096131 | -0.20142 | 121.701 | -0.07782 | -0.17395 | 0.16937 | 0.23346 | 0.004578 | -0.20599 | 0.18768 | -0.35706 | -0.36163 | -0.16937 | 121.3943 | 121.7651 | 61.8393 | -121.4996 | 121.3898 | 121.4264 | 61.7935 | -121.5912
76.2031 | 121.8246 | -61.734 | 59.7565 | 0.14374 | 0.0032599 | 0.063803 | 0.060509 | 0.12845 | -0.0043023 | -0.0039797 | 0.18234 | -0.0072846 | 0.055942 | 0.067419 | 0.00163 | -0.0034373 | 59.9762 | 59.9808 | 0.041199 | -61.8759 | 59.5093 | -61.8073 | -61.6974 | -61.5051 | 0.054932 | -62.0224 | 59.5276 | 59.5551 | -61.5372 | -61.7706 | -0.073242 | 0.036621 | -0.24719 | 121.7148 | -0.14191 | -0.17853 | 0.21973 | 0.19684 | -0.036621 | -0.22888 | 0.22888 | -0.28839 | -0.25177 | -0.20142 | 121.2433 | 121.7102 | 61.7752 | -121.4539 | 121.2616 | 121.2891 | 61.7889 | -121.5271
77.9688 | 121.8796 | -61.6562 | 59.8206 | -0.0088499 | 0.0056097 | 0.065939 | 0.063927 | 0.12717 | -0.0034479 | -0.0054751 | 0.13657 | -0.008139 | 0.057223 | 0.065924 | 0.0020572 | -0.0060007 | 60.0037 | 59.9762 | 0.10986 | -61.8118 | 59.6008 | -61.7386 | -61.6516 | -61.496 | 0.14191 | -62.0087 | 59.6146 | 59.642 | -61.4777 | -61.6882 | -0.082397 | 0.004578 | -0.21973 | 121.6324 | -0.15564 | -0.16022 | 0.1831 | 0.17853 | -0.032043 | -0.20599 | 0.16022 | -0.35248 | -0.32044 | -0.17853 | 121.257 | 121.6599 | 61.7661 | -121.4722 | 121.2708 | 121.2982 | 61.7981 | -121.5088
79.6562 | 121.8155 | -61.7111 | 59.8206 | 0.12848 | 0.0021917 | 0.062948 | 0.060082 | 0.12759 | -0.0015253 | -0.0050479 | 0.20523 | -0.0085662 | 0.057651 | 0.065497 | 0.0014164 | -0.0057871 | 59.9762 | 59.967 | 0.059509 | -61.8713 | 59.5505 | -61.7706 | -61.6745 | -61.5097 | 0.064087 | -62.0361 | 59.5825 | 59.5779 | -61.5189 | -61.7386 | -0.059509 | 0.036621 | -0.27008 | 121.6782 | -0.16022 | -0.19684 | 0.15564 | 0.19226 | -0.027465 | -0.23804 | 0.20142 | -0.32501 | -0.29755 | -0.24262 | 121.2616 | 121.6873 | 61.7706 | -121.4951 | 121.2936 | 121.2891 | 61.7752 | -121.5591
81.3906 | 121.8201 | -61.7065 | 59.8206 | 0.044556 | 0.0036871 | 0.064016 | 0.064995 | 0.12738 | -0.0047297 | -0.0065433 | 0.11368 | -0.012411 | 0.057651 | 0.065497 | 0.00163 | -0.0055735 | 59.9899 | 59.9716 | 0.073242 | -61.8439 | 59.5871 | -61.7386 | -61.647 | -61.5005 | 0.09613 | -62.0178 | 59.6191 | 59.61 | -61.4868 | -61.7203 | -0.032043 | 0.059509 | -0.23346 | 121.6782 | -0.13733 | -0.19684 | 0.16937 | 0.21973 | -0.013733 | -0.20142 | 0.20599 | -0.31128 | -0.29755 | -0.21057 | 121.2936 | 121.6965 | 61.7798 | -121.4676 | 121.3257 | 121.3165 | 61.8027 | -121.5408
83.1406 | 121.7285 | -61.8347 | 59.7382 | 0.059815 | 0.0062505 | 0.062307 | 0.062645 | 0.1293 | 0.0042425 | -0.0033389 | 0.060272 | -0.0072846 | 0.058505 | 0.067847 | 0.0052616 | -0.0072825 | 59.8709 | 59.7931 | -0.082397 | -61.9537 | 59.5917 | -61.8713 | -61.7432 | -61.6837 | -0.10529 | -62.2375 | 59.5825 | 59.5688 | -61.5875 | -61.8439 | -0.036621 | 0.091553 | -0.14648 | 121.6278 | -0.11902 | -0.21057 | 0.13275 | 0.24719 | -0.009155 | -0.15564 | 0.15106 | -0.40283 | -0.39368 | -0.16937 | 121.4264 | 121.7056 | 61.7523 | -121.4813 | 121.4172 | 121.4035 | 61.7294 | -121.582
84.8906 | 121.7331 | -61.7203 | 59.848 | -0.15381 | 0.0060369 | 0.064016 | 0.06414 | 0.12717 | -0.0025935 | -0.0033389 | -0.13046 | -0.0096344 | 0.055514 | 0.069983 | -0.00029261 | -0.0057871 | 60.0723 | 60.0723 | 0.2655 | -61.7615 | 59.6146 | -61.7065 | -61.5967 | -61.4594 | 0.25635 | -61.9904 | 59.6741 | 59.6603 | -61.4639 | -61.6974 | 0.013733 | 0.1236 | -0.23346 | 121.7926 | -0.041199 | -0.16479 | 0.22431 | 0.25635 | 0.022888 | -0.17395 | 0.26093 | -0.27008 | -0.29297 | -0.18768 | 121.3348 | 121.7926 | 61.9858 | -121.4447 | 121.3943 | 121.3806 | 61.9766 | -121.5454
86.5781 | 121.8063 | -61.7432 | 59.761 | 0.18951 | 0.0041143 | 0.064871 | 0.059227 | 0.12866 | -0.0040887 | -0.0037661 | 0.16708 | -0.010489 | 0.056369 | 0.06806 | 0.0018436 | -0.0051463 | 59.9808 | 59.9899 | 0.041199 | -61.8668 | 59.5001 | -61.7661 | -61.6791 | -61.4914 | 0.059509 | -62.0407 | 59.5505 | 59.5459 | -61.5326 | -61.7615 | -0.022888 | 0.064087 | -0.26093 | 121.7331 | -0.1236 | -0.18768 | 0.21973 | 0.21057 | -0.018311 | -0.21057 | 0.25177 | -0.29755 | -0.27923 | -0.21515 | 121.2433 | 121.7239 | 61.7844 | -121.4401 | 121.2936 | 121.2891 | 61.8027 | -121.5225
88.3281 | 121.7331 | -61.7432 | 59.8434 | -0.11566 | 0.0045417 | 0.064657 | 0.066704 | 0.12717 | -0.0010981 | -0.0054751 | -0.15335 | -0.00878 | 0.057864 | 0.070196 | 0.002698 | -0.0051463 | 59.9899 | 59.9579 | 0.15106 | -61.8393 | 59.6558 | -61.734 | -61.6608 | -61.5326 | 0.15564 | -62.059 | 59.6832 | 59.7107 | -61.4914 | -61.7203 | 0.009155 | 0.082397 | -0.18768 | 121.7011 | -0.09613 | -0.17853 | 0.14648 | 0.25177 | 0.022888 | -0.16022 | 0.21057 | -0.31586 | -0.33875 | -0.13275 | 121.3989 | 121.7331 | 61.8942 | -121.5042 | 121.4264 | 121.4539 | 61.8988 | -121.5637
90.0781 | 121.8704 | -61.7569 | 59.7061 | 0.17426 | 0.0071051 | 0.060812 | 0.062431 | 0.12695 | 0.0010381 | -0.0046207 | 0.21286 | -0.0085662 | 0.056369 | 0.067633 | 0.0024844 | -0.0070689 | 59.9533 | 59.8984 | -0.009155 | -61.8851 | 59.5047 | -61.821 | -61.7203 | -61.5463 | 0.027466 | -62.0773 | 59.523 | 59.5413 | -61.5555 | -61.7798 | -0.064087 | 0.036621 | -0.20142 | 121.6553 | -0.12817 | -0.1648 | 0.24719 | 0.20142 | -0.022888 | -0.18311 | 0.21057 | -0.32043 | -0.29755 | -0.16479 | 121.2616 | 121.7102 | 61.7477 | -121.4264 | 121.2799 | 121.2982 | 61.7844 | -121.4859
91.75 | 121.843 | -61.6333 | 59.8343 | 0.021668 | 0.00026912 | 0.06423 | 0.062431 | 0.12909 | -0.0043023 | -0.0059023 | 0.1442 | -0.0083526 | 0.055301 | 0.068915 | 0.00034819 | -0.0049325 | 60.0037 | 59.9716 | 0.10071 | -61.821 | 59.6008 | -61.7157 | -61.6699 | -61.496 | 0.10986 | -62.027 | 59.61 | 59.6375 | -61.4868 | -61.7203 | -0.082397 | -0.036621 | -0.23346 | 121.6049 | -0.18768 | -0.15106 | 0.16937 | 0.14649 | -0.086975 | -0.22431 | 0.13733 | -0.39368 | -0.3067 | -0.19684 | 121.2341 | 121.637 | 61.734 | -121.5042 | 121.2433 | 121.2708 | 61.7432 | -121.5546
93.5 | 121.6965 | -61.8439 | 59.7336 | -0.016479 | 0.0060369 | 0.062521 | 0.063499 | 0.1246 | 0.0044561 | -0.0026981 | -0.054169 | -0.0079254 | 0.057437 | 0.06806 | 0.0059024 | -0.0062143 | 59.9396 | 59.8801 | 0.004578 | -61.9125 | 59.5779 | -61.821 | -61.7477 | -61.647 | -0.045776 | -62.2009 | 59.5596 | 59.5779 | -61.6333 | -61.8439 | 0.022888 | 0.09613 | -0.15564 | 121.7239 | -0.068665 | -0.16479 | 0.20599 | 0.21057 | 0 | -0.17395 | 0.19684 | -0.35706 | -0.35706 | -0.15564 | 121.4218 | 121.7834 | 61.8484 | -121.4813 | 121.4035 | 121.4218 | 61.7981 | -121.5775
95.25 | 121.8613 | -61.6562 | 59.8434 | -0.10803 | 0.0053961 | 0.066793 | 0.065636 | 0.12546 | -0.0040887 | -0.0039797 | 0.014496 | -0.010916 | 0.05701 | 0.06571 | -7.9008e-05 | -0.0055735 | 60.0906 | 60.0906 | 0.24719 | -61.7386 | 59.642 | -61.702 | -61.5692 | -61.3861 | 0.27924 | -61.9171 | 59.5963 | 59.6466 | -61.441 | -61.6791 | -0.045776 | 0.086975 | -0.20142 | 121.7468 | -0.082397 | -0.16937 | 0.24719 | 0.21515 | -0.022888 | -0.24719 | 0.27008 | -0.26093 | -0.23804 | -0.19684 | 121.2982 | 121.7468 | 61.9034 | -121.4127 | 121.2524 | 121.3028 | 61.9354 | -121.5225
97 | 121.7743 | -61.7569 | 59.8022 | -0.16907 | 0.0073187 | 0.063589 | 0.064995 | 0.12888 | 0.0016791 | -0.0037661 | -0.13046 | -0.0066436 | 0.059146 | 0.066992 | 0.0018436 | -0.0055735 | 59.9854 | 59.9258 | 0.10986 | -61.8393 | 59.6786 | -61.734 | -61.6882 | -61.5738 | 0.1236 | -62.0911 | 59.6466 | 59.6603 | -61.5234 | -61.734 | 0.022888 | 0.068665 | -0.1236 | 121.6827 | -0.082397 | -0.15106 | 0.18311 | 0.23346 | 0.022888 | -0.15564 | 0.18311 | -0.33417 | -0.35706 | -0.14191 | 121.4355 | 121.7422 | 61.8668 | -121.4905 | 121.4035 | 121.4172 | 61.8805 | -121.5363
98.75 | 121.8567 | -61.7844 | 59.7015 | 0.159 | 0.0088141 | 0.062307 | 0.063072 | 0.12695 | -0.0017389 | -0.0037661 | 0.18234 | -0.0085662 | 0.056155 | 0.069128 | 0.0037662 | -0.0053599 | 59.8846 | 59.8572 | -0.07782 | -61.9354 | 59.5276 | -61.8576 | -61.7294 | -61.5601 | -0.018311 | -62.0956 | 59.5047 | 59.5459 | -61.6013 | -61.7981 | -0.073242 | 0.054932 | -0.17395 | 121.6415 | -0.15106 | -0.20599 | 0.18311 | 0.18311 | -0.013733 | -0.19684 | 0.2243 | -0.31128 | -0.29755 | -0.15564 | 121.312 | 121.669 | 61.7065 | -121.431 | 121.2891 | 121.3303 | 61.7661 | -121.4996
100.4531 | 121.875 | -61.6379 | 59.8343 | -0.016479 | 0.0053961 | 0.064016 | 0.064354 | 0.12674 | -0.0051569 | -0.0033389 | -0.15335 | -0.0079254 | 0.057651 | 0.066138 | -0.0020016 | -0.0055735 | 60.022 | 60.0311 | 0.16937 | -61.7844 | 59.6146 | -61.7249 | -61.6058 | -61.4182 | 0.23804 | -61.9263 | 59.6466 | 59.6695 | -61.4273 | -61.6699 | -0.086976 | 0.032043 | -0.21973 | 121.669 | -0.14648 | -0.17853 | 0.18768 | 0.21057 | -0.032044 | -0.18768 | 0.21973 | -0.28839 | -0.25635 | -0.1648 | 121.2524 | 121.6599 | 61.8073 | -121.4401 | 121.2845 | 121.3074 | 61.8759 | -121.5042
102.1875 | 121.7606 | -61.7569 | 59.7794 | -0.16144 | 0.0098821 | 0.064444 | 0.067131 | 0.12909 | 0.00061092 | -0.0037661 | -0.12283 | -0.007071 | 0.058505 | 0.066565 | 0.0014164 | -0.0079233 | 59.9716 | 59.9167 | 0.11902 | -61.8576 | 59.6603 | -61.7523 | -61.6562 | -61.5646 | 0.13275 | -62.114 | 59.6512 | 59.6786 | -61.5005 | -61.7477 | 0.004578 | 0.10071 | -0.11902 | 121.6736 | -0.10071 | -0.20142 | 0.19226 | 0.25635 | 0.009155 | -0.12817 | 0.19226 | -0.35706 | -0.36621 | -0.10071 | 121.4172 | 121.7285 | 61.8759 | -121.4355 | 121.4081 | 121.4355 | 61.8896 | -121.5271
103.9375 | 121.7606 | -61.7889 | 59.7656 | -0.077515 | 0.01095 | 0.062521 | 0.064781 | 0.12631 | 0.0033881 | -0.00077552 | -0.054169 | -0.0083526 | 0.058719 | 0.068915 | 0.0039798 | -0.0077097 | 59.967 | 59.9213 | 0.086975 | -61.8622 | 59.5825 | -61.7935 | -61.6928 | -61.5555 | 0.09613 | -62.1048 | 59.5871 | 59.5825 | -61.5601 | -61.7935 | -0.004578 | 0.09613 | -0.1831 | 121.7102 | -0.073243 | -0.16937 | 0.20142 | 0.22888 | -0.004578 | -0.17853 | 0.23346 | -0.31586 | -0.31128 | -0.1831 | 121.3715 | 121.756 | 61.8759 | -121.4584 | 121.376 | 121.3715 | 61.8851 | -121.5591
105.6875 | 121.7834 | -61.7844 | 59.7336 | 0.16663 | 0.0064643 | 0.06188 | 0.062004 | 0.12781 | -0.00045708 | -0.0033389 | 0.13657 | -0.0083526 | 0.058078 | 0.069128 | 0.0037662 | -0.0055735 | 59.8389 | 59.8022 | -0.11902 | -61.9766 | 59.5413 | -61.8576 | -61.7798 | -61.6516 | -0.1236 | -62.1872 | 59.5642 | 59.5734 | -61.5921 | -61.8118 | -0.073242 | 0.004578 | -0.19226 | 121.5866 | -0.19226 | -0.19684 | 0.10529 | 0.19226 | -0.027466 | -0.16937 | 0.13275 | -0.40283 | -0.37537 | -0.16022 | 121.3257 | 121.6232 | 61.6653 | -121.5134 | 121.3486 | 121.3577 | 61.6608 | -121.5454
107.375 | 121.8292 | -61.6608 | 59.8343 | -0.10803 | 0.0032599 | 0.062735 | 0.067345 | 0.12759 | -0.0068659 | -0.0031253 | 0.052643 | -0.010062 | 0.05701 | 0.06806 | -0.00071981 | -0.0034373 | 60.0769 | 60.1089 | 0.24261 | -61.7432 | 59.6008 | -61.6974 | -61.5967 | -61.3953 | 0.28839 | -61.8896 | 59.6329 | 59.6512 | -61.4227 | -61.6608 | -0.036621 | 0.064087 | -0.23346 | 121.7697 | -0.082397 | -0.14648 | 0.24261 | 0.23804 | 0 | -0.20142 | 0.2655 | -0.22888 | -0.22888 | -0.18311 | 121.2616 | 121.7377 | 61.9034 | -121.431 | 121.2936 | 121.312 | 61.9492 | -121.4951
109.125 | 121.7743 | -61.7477 | 59.7931 | -0.16907 | 0.0077459 | 0.062094 | 0.065208 | 0.12695 | 0.0018927 | -0.0052615 | -0.10757 | -0.00643 | 0.058719 | 0.069769 | 0.0014164 | -0.0081369 | 59.9716 | 59.9304 | 0.11902 | -61.8393 | 59.6512 | -61.7523 | -61.647 | -61.5738 | 0.12817 | -62.1048 | 59.6741 | 59.6878 | -61.5051 | -61.7477 | -0.004577 | 0.10071 | -0.14191 | 121.6782 | -0.091552 | -0.19226 | 0.17853 | 0.24262 | 0 | -0.11902 | 0.17395 | -0.35705 | -0.35705 | -0.10529 | 121.3989 | 121.7194 | 61.8668 | -121.4401 | 121.4218 | 121.4355 | 61.8759 | -121.5408
110.7969 | 121.8475 | -61.6241 | 59.8434 | -0.031738 | 0.0051825 | 0.064016 | 0.063072 | 0.12631 | -0.0060113 | -0.0063297 | 0.029755 | -0.010275 | 0.055942 | 0.065924 | 0.00013459 | -0.0049325 | 60.0632 | 60.0723 | 0.21057 | -61.7615 | 59.6329 | -61.702 | -61.6058 | -61.3998 | 0.24719 | -61.8988 | 59.6375 | 59.6512 | -61.4548 | -61.6425 | -0.077819 | 0.018311 | -0.21057 | 121.6965 | -0.13733 | -0.15564 | 0.21973 | 0.16937 | -0.01831 | -0.20599 | 0.22431 | -0.27466 | -0.25635 | -0.19226 | 121.257 | 121.6873 | 61.8347 | -121.4493 | 121.2616 | 121.2753 | 61.8713 | -121.4859
112.5469 | 121.7377 | -61.7432 | 59.8663 | -0.13092 | 0.0058233 | 0.063162 | 0.065636 | 0.12866 | -0.0032343 | -0.0061161 | -0.10757 | -0.0074982 | 0.05936 | 0.069983 | 0.0018436 | -0.0062143 | 59.9991 | 59.967 | 0.16937 | -61.8393 | 59.6466 | -61.734 | -61.6241 | -61.528 | 0.15564 | -62.0544 | 59.6878 | 59.697 | -61.4822 | -61.6928 | 0.009155 | 0.11902 | -0.21973 | 121.7102 | -0.09613 | -0.21515 | 0.13275 | 0.26093 | 0.050354 | -0.17853 | 0.21515 | -0.31128 | -0.36163 | -0.16937 | 121.3898 | 121.7422 | 61.9125 | -121.4905 | 121.431 | 121.4401 | 61.8988 | -121.5591
114.2969 | 121.843 | -61.7432 | 59.7336 | 0.16663 | 0.0043279 | 0.058889 | 0.060936 | 0.12866 | 0.00061092 | -0.0024845 | 0.1976 | -0.0072846 | 0.056582 | 0.068915 | 0.0041934 | -0.0057871 | 59.9396 | 59.9075 | -0.018311 | -61.8668 | 59.523 | -61.8164 | -61.7249 | -61.528 | 0.018311 | -62.0865 | 59.523 | 59.5459 | -61.5601 | -61.7661 | -0.073242 | 0.01831 | -0.21057 | 121.6507 | -0.1236 | -0.14191 | 0.20599 | 0.1831 | -0.022888 | -0.21057 | 0.21515 | -0.34332 | -0.32043 | -0.18768 | 121.2662 | 121.6827 | 61.7249 | -121.4584 | 121.2662 | 121.2891 | 61.7615 | -121.4996
116.0312 | 121.8384 | -61.7844 | 59.6878 | 0.15137 | 0.0049689 | 0.063589 | 0.060295 | 0.12695 | -0.00067088 | -0.0022707 | 0.18997 | -0.0079254 | 0.058932 | 0.066565 | 0.0054752 | -0.0049325 | 59.8846 | 59.8343 | -0.09613 | -61.9537 | 59.5505 | -61.821 | -61.7706 | -61.5784 | -0.050354 | -62.1231 | 59.5367 | 59.5139 | -61.5967 | -61.8164 | -0.036621 | 0.013733 | -0.13733 | 121.6187 | -0.16937 | -0.18311 | 0.19684 | 0.18768 | -0.032043 | -0.15106 | 0.20599 | -0.33875 | -0.3067 | -0.17395 | 121.3348 | 121.669 | 61.6882 | -121.4584 | 121.3211 | 121.2982 | 61.734 | -121.5042
117.7188 | 121.7056 | -61.8301 | 59.7565 | -0.039368 | 0.0071051 | 0.061239 | 0.062859 | 0.12653 | 0.0012519 | -0.0031253 | 0.022125 | -0.0057892 | 0.058719 | 0.069128 | 0.003339 | -0.0081369 | 59.9533 | 59.8938 | 0.032043 | -61.8759 | 59.5642 | -61.7935 | -61.7432 | -61.615 | -0.004578 | -62.1552 | 59.5642 | 59.5825 | -61.6013 | -61.821 | 0.036621 | 0.086975 | -0.19226 | 121.7239 | -0.045777 | -0.13275 | 0.19684 | 0.22888 | 0.009155 | -0.19226 | 0.21515 | -0.32501 | -0.33417 | -0.17395 | 121.3943 | 121.7834 | 61.8622 | -121.4996 | 121.3943 | 121.4127 | 61.8256 | -121.5775
119.4688 | 121.7422 | -61.7065 | 59.8526 | -0.13855 | 0.0068915 | 0.063589 | 0.064354 | 0.12738 | -0.0064387 | -0.0035525 | -0.046539 | -0.0094208 | 0.059787 | 0.067419 | 0.00056179 | -0.0060007 | 60.054 | 60.0723 | 0.26093 | -61.7386 | 59.6054 | -61.6791 | -61.6058 | -61.4731 | 0.27466 | -61.9492 | 59.6649 | 59.6832 | -61.4685 | -61.6837 | 0.027466 | 0.10071 | -0.24719 | 121.7789 | -0.032043 | -0.13275 | 0.20142 | 0.23804 | 0.022888 | -0.18768 | 0.23346 | -0.24261 | -0.2655 | -0.16937 | 121.312 | 121.7606 | 61.9675 | -121.4584 | 121.3715 | 121.3898 | 61.9812 | -121.5363
121.2188 | 121.7651 | -61.7981 | 59.761 | -0.1004 | 0.0086005 | 0.060812 | 0.061577 | 0.1261 | 0.0021063 | -0.0014163 | -0.077057 | -0.009848 | 0.056155 | 0.067847 | 0.0037662 | -0.0055735 | 59.9533 | 59.9121 | 0.091553 | -61.853 | 59.5963 | -61.7706 | -61.6882 | -61.5692 | 0.09613 | -62.0865 | 59.6146 | 59.6237 | -61.5509 | -61.7706 | 0.027466 | 0.10986 | -0.16479 | 121.7102 | -0.054931 | -0.16479 | 0.19226 | 0.24719 | 0.027466 | -0.14648 | 0.22888 | -0.28839 | -0.31586 | -0.13733 | 121.3943 | 121.7514 | 61.8896 | -121.4493 | 121.4127 | 121.4218 | 61.8942 | -121.5317
122.9844 | 121.8521 | -61.6562 | 59.8022 | 0.029297 | 0.0036871 | 0.06423 | 0.065636 | 0.12653 | -0.0068659 | -0.0029117 | 0.12894 | -0.009848 | 0.05701 | 0.066779 | -0.00029261 | -0.0040781 | 59.9762 | 59.967 | 0.10529 | -61.8118 | 59.5917 | -61.734 | -61.6333 | -61.4914 | 0.10986 | -62.0132 | 59.6146 | 59.6146 | -61.4868 | -61.7203 | -0.07782 | 0.022888 | -0.21057 | 121.6232 | -0.15564 | -0.17853 | 0.17395 | 0.16937 | -0.064087 | -0.18768 | 0.16479 | -0.35706 | -0.29297 | -0.18768 | 121.2479 | 121.6324 | 61.7615 | -121.4355 | 121.2708 | 121.2708 | 61.7661 | -121.5225
124.7344 | 121.8475 | -61.7661 | 59.7198 | 0.12085 | 0.0053961 | 0.062094 | 0.063713 | 0.12845 | -0.0010981 | -0.0059023 | 0.24338 | -0.0094208 | 0.057864 | 0.067206 | 0.00098899 | -0.0064279 | 59.9762 | 59.9396 | 0.022888 | -61.8484 | 59.5093 | -61.7935 | -61.7386 | -61.5372 | 0.022888 | -62.0636 | 59.5139 | 59.523 | -61.5646 | -61.7889 | -0.027466 | 0.027466 | -0.21057 | 121.7056 | -0.082398 | -0.10986 | 0.25635 | 0.20142 | -0.022888 | -0.20599 | 0.22888 | -0.29755 | -0.27466 | -0.19684 | 121.2753 | 121.7422 | 61.7889 | -121.4584 | 121.2799 | 121.2891 | 61.7889 | -121.5088
126.4062 | 121.7102 | -61.7157 | 59.8434 | -0.1767 | 0.0077459 | 0.063375 | 0.066063 | 0.12631 | -0.0023797 | -0.0046207 | -0.084686 | -0.0085662 | 0.058505 | 0.06507 | -0.00050621 | -0.0070689 | 59.9945 | 59.9716 | 0.17395 | -61.821 | 59.642 | -61.7065 | -61.6425 | -61.5372 | 0.16479 | -62.0544 | 59.6741 | 59.7107 | -61.4868 | -61.702 | 0.009155 | 0.073242 | -0.20142 | 121.6873 | -0.10529 | -0.17853 | 0.15106 | 0.22888 | 0.013733 | -0.16937 | 0.17853 | -0.33874 | -0.35248 | -0.13275 | 121.3577 | 121.7102 | 61.8896 | -121.4859 | 121.3898 | 121.4264 | 61.8805 | -121.5454
128.1562 | 121.8155 | -61.7157 | 59.7839 | 0.15137 | 0.0053961 | 0.062521 | 0.062431 | 0.12738 | -0.0017389 | -0.0050479 | 0.18997 | -0.010916 | 0.056582 | 0.067419 | 0.0022708 | -0.0060007 | 59.9808 | 59.967 | 0.059509 | -61.8668 | 59.5184 | -61.7798 | -61.702 | -61.496 | 0.059509 | -62.0407 | 59.5322 | 59.5505 | -61.5555 | -61.7569 | -0.064087 | 0.013733 | -0.2655 | 121.6827 | -0.15106 | -0.16479 | 0.19684 | 0.16022 | -0.041199 | -0.25177 | 0.21973 | -0.32501 | -0.28381 | -0.23346 | 121.2341 | 121.6965 | 61.7752 | -121.4859 | 121.2479 | 121.2662 | 61.7752 | -121.5408
129.9219 | 121.8521 | -61.7661 | 59.6924 | 0.14374 | 0.0049689 | 0.061026 | 0.063499 | 0.12738 | -0.00045708 | -0.0059023 | 0.1976 | -0.008139 | 0.058719 | 0.07041 | 0.0029116 | -0.0077097 | 59.8938 | 59.8206 | -0.07782 | -61.9446 | 59.5596 | -61.8622 | -61.7432 | -61.5875 | -0.082397 | -62.1323 | 59.5367 | 59.5551 | -61.5601 | -61.7981 | -0.096131 | 0.022888 | -0.13275 | 121.5866 | -0.17853 | -0.20142 | 0.20142 | 0.20599 | -0.032044 | -0.15564 | 0.17853 | -0.36621 | -0.33417 | -0.13733 | 121.3257 | 121.6599 | 61.6882 | -121.4355 | 121.3028 | 121.3211 | 61.6837 | -121.4905
131.6094 | 121.7056 | -61.8393 | 59.7427 | -0.062256 | 0.0075323 | 0.061453 | 0.065849 | 0.12631 | 0.0014655 | -0.0046207 | -0.031281 | -0.0074982 | 0.055301 | 0.067206 | 0.0041934 | -0.0081369 | 59.9716 | 59.8846 | 0.050354 | -61.8805 | 59.5596 | -61.8027 | -61.7203 | -61.5875 | 0.032043 | -62.1185 | 59.5871 | 59.6191 | -61.5601 | -61.7889 | 0.036621 | 0.11902 | -0.18311 | 121.7239 | -0.041199 | -0.16022 | 0.22888 | 0.27923 | 0.050354 | -0.15564 | 0.25177 | -0.27924 | -0.32959 | -0.1236 | 121.3989 | 121.8109 | 61.8896 | -121.463 | 121.4264 | 121.4584 | 61.8713 | -121.5317
133.3594 | 121.7972 | -61.7203 | 59.7931 | 0.159 | 0.0088141 | 0.062094 | 0.06179 | 0.1246 | -0.0047297 | -0.0033389 | 0.22812 | -0.009848 | 0.05701 | 0.067847 | 0.00163 | -0.0068551 | 59.9716 | 59.967 | 0.045776 | -61.8576 | 59.5139 | -61.7889 | -61.6882 | -61.5051 | 0.045776 | -62.0361 | 59.523 | 59.5779 | -61.5509 | -61.7844 | -0.068664 | 0.032044 | -0.27924 | 121.6873 | -0.13733 | -0.16937 | 0.17853 | 0.16937 | -0.064087 | -0.27008 | 0.21515 | -0.31586 | -0.25177 | -0.21515 | 121.2341 | 121.6919 | 61.7661 | -121.4813 | 121.2433 | 121.2982 | 61.7661 | -121.5775
135.1094 | 121.7056 | -61.7844 | 59.7519 | -0.016479 | 0.0068915 | 0.060385 | 0.064781 | 0.12695 | 0.0016791 | -0.0024845 | -0.0083922 | -0.00643 | 0.058078 | 0.068487 | 0.0052616 | -0.0051463 | 59.9533 | 59.8938 | 0.032043 | -61.8805 | 59.5871 | -61.7935 | -61.7157 | -61.6013 | 0.018311 | -62.1643 | 59.5551 | 59.6008 | -61.5784 | -61.8393 | -0.009155 | 0.068665 | -0.16479 | 121.6782 | -0.09613 | -0.16479 | 0.20142 | 0.20599 | -0.054931 | -0.19684 | 0.18311 | -0.37994 | -0.32501 | -0.15106 | 121.3715 | 121.7377 | 61.8164 | -121.4676 | 121.3394 | 121.3852 | 61.8027 | -121.5912
136.7812 | 121.8063 | -61.7065 | 59.7977 | 0.12085 | 0.0039007 | 0.063589 | 0.062218 | 0.12439 | -0.0051569 | -0.0037661 | 0.24338 | -0.010489 | 0.056796 | 0.067419 | 0.00013459 | -0.0030099 | 59.967 | 59.9625 | 0.064087 | -61.8759 | 59.5276 | -61.7798 | -61.6837 | -61.5005 | 0.073242 | -62.0224 | 59.5642 | 59.5917 | -61.4914 | -61.7386 | -0.073242 | 0.022888 | -0.27008 | 121.669 | -0.16937 | -0.19226 | 0.16937 | 0.21515 | -0.032043 | -0.23346 | 0.20599 | -0.31586 | -0.28381 | -0.20599 | 121.2341 | 121.6736 | 61.7706 | -121.4813 | 121.2708 | 121.2982 | 61.7798 | -121.5363
138.5312 | 121.8384 | -61.6653 | 59.848 | -0.1004 | 0.0062505 | 0.065512 | 0.066704 | 0.1261 | -0.0040887 | -0.0067569 | -0.0083922 | -0.0094208 | 0.059787 | 0.065924 | -0.0011472 | -0.0060007 | 60.0861 | 60.0906 | 0.25635 | -61.7386 | 59.6283 | -61.6837 | -61.6196 | -61.3815 | 0.29297 | -61.8851 | 59.642 | 59.6466 | -61.4456 | -61.6653 | -0.018311 | 0.045776 | -0.21973 | 121.756 | -0.073242 | -0.11902 | 0.23804 | 0.21973 | 0 | -0.20599 | 0.28381 | -0.21973 | -0.21973 | -0.20142 | 121.2936 | 121.7514 | 61.9217 | -121.4676 | 121.3074 | 121.3119 | 61.9583 | -121.5134
140.2812 | 121.8384 | -61.7706 | 59.7198 | 0.11322 | 0.0060369 | 0.061026 | 0.064354 | 0.12866 | -0.0015253 | -0.0029117 | 0.18997 | -0.0057892 | 0.056796 | 0.07041 | 0.0029116 | -0.0070689 | 59.8984 | 59.8206 | -0.091553 | -61.9537 | 59.5367 | -61.8393 | -61.734 | -61.5829 | -0.059509 | -62.1368 | 59.5551 | 59.5505 | -61.5829 | -61.8073 | -0.068664 | 0.036621 | -0.18311 | 121.5912 | -0.18311 | -0.21973 | 0.17853 | 0.18768 | -0.036621 | -0.1648 | 0.18768 | -0.36621 | -0.32959 | -0.16937 | 121.3074 | 121.669 | 61.6791 | -121.4539 | 121.3257 | 121.3211 | 61.7111 | -121.5271
142.0156 | 121.7468 | -61.7889 | 59.7473 | 0.075073 | 0.0075323 | 0.062094 | 0.062004 | 0.12738 | 0.0016791 | -0.0026981 | 0.11368 | -0.0062164 | 0.06 | 0.069556 | 0.0041934 | -0.0070689 | 59.8434 | 59.7839 | -0.10986 | -61.9629 | 59.5642 | -61.853 | -61.7569 | -61.6745 | -0.11902 | -62.233 | 59.5551 | 59.5688 | -61.6013 | -61.8439 | -0.064087 | 0.032043 | -0.18311 | 121.5729 | -0.17395 | -0.20599 | 0.096131 | 0.18768 | -0.054932 | -0.19226 | 0.11444 | -0.44403 | -0.3891 | -0.17853 | 121.3531 | 121.6324 | 61.6791 | -121.5042 | 121.344 | 121.3577 | 61.6699 | -121.5912
143.75 | 121.8338 | -61.7523 | 59.7382 | 0.15137 | 0.0034735 | 0.062307 | 0.059227 | 0.12674 | -0.0032343 | -0.0039797 | 0.22812 | -0.0085662 | 0.056582 | 0.067633 | 0.00034819 | -0.0049325 | 59.9533 | 59.9487 | 0.013733 | -61.8484 | 59.5001 | -61.7981 | -61.6928 | -61.5372 | 0.027466 | -62.0407 | 59.5139 | 59.5551 | -61.5692 | -61.7569 | -0.045777 | 0.059509 | -0.23804 | 121.701 | -0.096131 | -0.15564 | 0.21515 | 0.1831 | -0.004578 | -0.2243 | 0.21515 | -0.28839 | -0.28381 | -0.18311 | 121.2524 | 121.7056 | 61.7661 | -121.431 | 121.2662 | 121.3074 | 61.7798 | -121.4951
145.5156 | 121.7148 | -61.7294 | 59.8206 | -0.21484 | 0.0043279 | 0.063589 | 0.064781 | 0.12717 | -0.0030207 | -0.0041933 | -0.10757 | -0.009848 | 0.055514 | 0.066779 | -7.9008e-05 | -0.0068551 | 59.9762 | 59.9442 | 0.16022 | -61.8439 | 59.6466 | -61.7203 | -61.6516 | -61.5326 | 0.15564 | -62.0499 | 59.6832 | 59.7107 | -61.4731 | -61.7065 | 0.009155 | 0.07782 | -0.17395 | 121.6736 | -0.11444 | -0.19226 | 0.15564 | 0.25635 | 0.022888 | -0.13733 | 0.19684 | -0.32044 | -0.34332 | -0.10986 | 121.376 | 121.7056 | 61.8896 | -121.4722 | 121.4127 | 121.4401 | 61.8851 | -121.5271
147.2031 | 121.8155 | -61.7569 | 59.7198 | 0.16663 | 0.0039007 | 0.063803 | 0.06179 | 0.12653 | -0.0036615 | -0.0024845 | 0.24338 | -0.01113 | 0.05701 | 0.066779 | 0.0031254 | -0.0053599 | 59.9625 | 59.9396 | 0.022888 | -61.8713 | 59.4864 | -61.8027 | -61.7294 | -61.5189 | 0.032043 | -62.0544 | 59.5184 | 59.5367 | -61.5326 | -61.7935 | -0.045776 | 0.027466 | -0.23346 | 121.6965 | -0.11444 | -0.14191 | 0.24261 | 0.2243 | -0.036621 | -0.20142 | 0.23804 | -0.29755 | -0.26093 | -0.18311 | 121.2433 | 121.7194 | 61.7798 | -121.4493 | 121.2753 | 121.2936 | 61.7889 | -121.5134
148.9375 | 121.7285 | -61.7111 | 59.8663 | -0.20721 | 0.0068915 | 0.064871 | 0.066917 | 0.12994 | -0.0017389 | -0.0039797 | -0.099945 | -0.0089936 | 0.059787 | 0.066992 | 0.00098899 | -0.0038645 | 60.0494 | 60.0037 | 0.2243 | -61.7981 | 59.6512 | -61.7065 | -61.6104 | -61.5097 | 0.17853 | -62.0316 | 59.6924 | 59.697 | -61.4868 | -61.702 | 0.004578 | 0.10071 | -0.21515 | 121.7148 | -0.086975 | -0.18768 | 0.18311 | 0.22431 | 0.009156 | -0.17395 | 0.20142 | -0.32043 | -0.32959 | -0.16937 | 121.3623 | 121.7606 | 61.9354 | -121.4767 | 121.4035 | 121.4081 | 61.8896 | -121.5683
150.625 | 121.8613 | -61.7935 | 59.6924 | 0.18951 | 0.0064643 | 0.064657 | 0.061577 | 0.12631 | 0.00061092 | -0.0033389 | 0.16708 | -0.008139 | 0.055942 | 0.068274 | 0.0054752 | -0.0070689 | 59.8892 | 59.8297 | -0.07782 | -61.9217 | 59.5322 | -61.8027 | -61.7386 | -61.5738 | -0.009155 | -62.1002 | 59.5367 | 59.5367 | -61.5875 | -61.8073 | -0.009155 | 0.054932 | -0.16022 | 121.6232 | -0.12817 | -0.18311 | 0.19684 | 0.20599 | -0.013733 | -0.15564 | 0.21973 | -0.3067 | -0.29297 | -0.15564 | 121.3257 | 121.6827 | 61.7157 | -121.431 | 121.3303 | 121.3303 | 61.7844 | -121.4996
152.375 | 121.7514 | -61.8256 | 59.7107 | 0.14374 | 0.0077459 | 0.064657 | 0.062004 | 0.12503 | 0.0010381 | -0.0018435 | 0.13657 | -0.0079254 | 0.058505 | 0.067847 | 0.0024844 | -0.0064279 | 59.8297 | 59.761 | -0.13275 | -61.9766 | 59.5276 | -61.853 | -61.7661 | -61.647 | -0.1236 | -62.1918 | 59.5505 | 59.5459 | -61.5967 | -61.8439 | -0.027465 | 0.05951 | -0.1831 | 121.5866 | -0.15106 | -0.21057 | 0.11902 | 0.22888 | -0.01831 | -0.16022 | 0.17853 | -0.36621 | -0.3479 | -0.16479 | 121.3531 | 121.6553 | 61.6928 | -121.4767 | 121.376 | 121.3715 | 61.702 | -121.5546
154.125 | 121.701 | -61.853 | 59.7107 | 0.0064086 | 0.0071051 | 0.05953 | 0.063713 | 0.12802 | 0.0014655 | -0.0024845 | 0.075531 | -0.0072846 | 0.058932 | 0.06806 | 0.0022708 | -0.0053599 | 59.9075 | 59.8434 | -0.009155 | -61.9171 | 59.5413 | -61.8073 | -61.7615 | -61.6425 | -0.068665 | -62.2055 | 59.5551 | 59.5779 | -61.5967 | -61.8347 | 0.045776 | 0.091552 | -0.16937 | 121.6965 | -0.064087 | -0.15564 | 0.19684 | 0.25635 | 0.01831 | -0.15564 | 0.21057 | -0.35248 | -0.37079 | -0.13275 | 121.3943 | 121.7606 | 61.8439 | -121.4722 | 121.4081 | 121.431 | 61.7844 | -121.5454
155.8125 | 121.788 | -61.6562 | 59.848 | -0.16907 | 0.0066779 | 0.063589 | 0.067345 | 0.12888 | -0.0064387 | -0.0050479 | -0.023651 | -0.0085662 | 0.05936 | 0.066351 | -0.0020016 | -0.0047189 | 60.0998 | 60.1044 | 0.29297 | -61.7249 | 59.6329 | -61.6699 | -61.5829 | -61.4319 | 0.29297 | -61.9171 | 59.6191 | 59.6832 | -61.4182 | -61.6837 | -0.013733 | 0.073242 | -0.21515 | 121.7606 | -0.068665 | -0.14191 | 0.25177 | 0.23804 | -0.027466 | -0.22888 | 0.2243 | -0.26093 | -0.23346 | -0.16479 | 121.2891 | 121.756 | 61.9492 | -121.431 | 121.2753 | 121.3394 | 61.9492 | -121.5317
157.5625 | 121.7194 | -61.7386 | 59.8434 | -0.1767 | 0.0077459 | 0.062735 | 0.064568 | 0.12781 | -0.0032343 | -0.0054751 | -0.13809 | -0.0074982 | 0.057223 | 0.069342 | 0.00163 | -0.0066415 | 59.9808 | 59.9396 | 0.15564 | -61.8439 | 59.6649 | -61.7386 | -61.6287 | -61.5372 | 0.15106 | -62.0499 | 59.6832 | 59.7153 | -61.4731 | -61.6974 | 0 | 0.10986 | -0.17853 | 121.6782 | -0.10529 | -0.21515 | 0.13733 | 0.2655 | 0.041198 | -0.16022 | 0.20142 | -0.31128 | -0.35248 | -0.12817 | 121.4035 | 121.7194 | 61.8942 | -121.4722 | 121.4218 | 121.4539 | 61.8896 | -121.5408
159.2969 | 121.7194 | -61.8393 | 59.7153 | 0.059815 | 0.0058233 | 0.062521 | 0.059441 | 0.1293 | 0.0016791 | -0.0031253 | 0.022125 | -0.007071 | 0.05701 | 0.068487 | 0.0059024 | -0.0081369 | 59.8663 | 59.7839 | -0.082397 | -61.9537 | 59.5734 | -61.8301 | -61.7615 | -61.6699 | -0.09613 | -62.2055 | 59.5642 | 59.5871 | -61.6104 | -61.8164 | 0.009155 | 0.077819 | -0.14191 | 121.6232 | -0.11444 | -0.19226 | 0.15106 | 0.22888 | 0.022888 | -0.15106 | 0.16937 | -0.36621 | -0.3891 | -0.12817 | 121.4127 | 121.7056 | 61.7569 | -121.4767 | 121.4035 | 121.4264 | 61.7432 | -121.5317
161.0312 | 121.8109 | -61.7432 | 59.7794 | 0.16663 | 0.0047553 | 0.062948 | 0.058373 | 0.12717 | -0.0034479 | -0.0024845 | 0.23575 | -0.009848 | 0.057223 | 0.066779 | 0.0022708 | -0.0053599 | 59.9442 | 59.9533 | 0.032043 | -61.853 | 59.4955 | -61.7935 | -61.6837 | -61.5051 | 0.036621 | -62.0316 | 59.4955 | 59.5505 | -61.5555 | -61.7844 | -0.050354 | 0.059509 | -0.28381 | 121.6965 | -0.10986 | -0.16937 | 0.16479 | 0.18768 | -0.041199 | -0.28381 | 0.23804 | -0.28839 | -0.24719 | -0.22888 | 121.2387 | 121.6873 | 61.7752 | -121.463 | 121.2387 | 121.2936 | 61.7798 | -121.5637
162.7812 | 121.7926 | -61.7249 | 59.7794 | 0.14374 | 0.0047553 | 0.063162 | 0.06115 | 0.12717 | -0.0040887 | -0.0065433 | 0.20523 | -0.0083526 | 0.056369 | 0.066992 | -7.9008e-05 | -0.0051463 | 59.967 | 59.9533 | 0.036621 | -61.853 | 59.5093 | -61.7798 | -61.6882 | -61.5051 | 0.045776 | -62.027 | 59.5322 | 59.5642 | -61.5417 | -61.7798 | -0.054931 | 0.036622 | -0.27008 | 121.6782 | -0.12817 | -0.16479 | 0.18768 | 0.18311 | -0.054931 | -0.24719 | 0.21973 | -0.30212 | -0.24719 | -0.21515 | 121.2341 | 121.6919 | 61.7615 | -121.4676 | 121.257 | 121.2891 | 61.7706 | -121.5591
164.5312 | 121.8384 | -61.6379 | 59.8343 | -0.1004 | 0.0056097 | 0.063162 | 0.064781 | 0.12631 | -0.0057977 | -0.0061161 | -0.077057 | -0.011557 | 0.05936 | 0.066992 | -0.001788 | -0.0062143 | 60.1044 | 60.1044 | 0.27466 | -61.7157 | 59.6329 | -61.6882 | -61.5738 | -61.3907 | 0.29755 | -61.8942 | 59.6466 | 59.6695 | -61.4365 | -61.6425 | -0.050354 | 0.064086 | -0.20142 | 121.7422 | -0.07782 | -0.14191 | 0.27008 | 0.20142 | -0.004578 | -0.18768 | 0.24719 | -0.25635 | -0.25177 | -0.1648 | 121.2708 | 121.7422 | 61.9125 | -121.4081 | 121.2845 | 121.3074 | 61.9354 | -121.4767
166.2812 | 121.7468 | -61.7752 | 59.7656 | -0.1004 | 0.0066779 | 0.05953 | 0.062218 | 0.12695 | 0.0036017 | -0.0063297 | -0.061798 | -0.0068572 | 0.057864 | 0.06806 | 0.0041934 | -0.0077097 | 59.9487 | 59.9167 | 0.082397 | -61.8393 | 59.6054 | -61.7981 | -61.6837 | -61.5601 | 0.086975 | -62.0865 | 59.6054 | 59.5963 | -61.5372 | -61.7706 | -0.022888 | 0.091553 | -0.16022 | 121.6919 | -0.064086 | -0.15564 | 0.1831 | 0.23804 | 0.004578 | -0.16022 | 0.21515 | -0.31128 | -0.31586 | -0.16937 | 121.3806 | 121.7239 | 61.8576 | -121.4493 | 121.3806 | 121.3715 | 61.8622 | -121.5363
167.9688 | 121.7422 | -61.7523 | 59.7656 | -0.13855 | 0.0075323 | 0.06423 | 0.064568 | 0.12802 | 0.0016791 | -0.0018435 | -0.099945 | -0.00878 | 0.060214 | 0.069128 | 0.00163 | -0.0072825 | 59.9533 | 59.9121 | 0.11902 | -61.8393 | 59.6466 | -61.7706 | -61.6699 | -61.5784 | 0.091553 | -62.0911 | 59.6054 | 59.6329 | -61.5738 | -61.7798 | -0.018311 | 0.082397 | -0.11902 | 121.6644 | -0.086975 | -0.16937 | 0.18768 | 0.17853 | -0.027466 | -0.16022 | 0.17395 | -0.33875 | -0.31128 | -0.13275 | 121.3989 | 121.7056 | 61.8713 | -121.4355 | 121.3577 | 121.3852 | 61.8439 | -121.5454
169.7188 | 121.7789 | -61.7569 | 59.7931 | -0.16907 | 0.0071051 | 0.064444 | 0.064568 | 0.12717 | -0.0010981 | -0.0063297 | -0.092316 | -0.0068572 | 0.056796 | 0.068915 | 0.00163 | -0.0068551 | 59.9487 | 59.9075 | 0.10529 | -61.8347 | 59.6603 | -61.7294 | -61.6745 | -61.5692 | 0.13275 | -62.0819 | 59.6329 | 59.6741 | -61.5097 | -61.7477 | 0.027466 | 0.082397 | -0.13275 | 121.6644 | -0.07782 | -0.16022 | 0.15564 | 0.24719 | 0.009155 | -0.16022 | 0.18768 | -0.32501 | -0.33417 | -0.11902 | 121.4172 | 121.7056 | 61.8622 | -121.4676 | 121.3898 | 121.431 | 61.8896 | -121.5408
171.4844 | 121.8338 | -61.6333 | 59.8297 | -0.092773 | 0.0066779 | 0.065725 | 0.065849 | 0.12759 | -0.0043023 | -0.0054751 | 0.037384 | -0.0085662 | 0.058505 | 0.068274 | -0.0022152 | -0.0051463 | 60.0586 | 60.0906 | 0.23804 | -61.7432 | 59.6237 | -61.6928 | -61.5829 | -61.3953 | 0.2655 | -61.8988 | 59.5871 | 59.6558 | -61.4319 | -61.6562 | -0.059509 | 0.050354 | -0.20599 | 121.7239 | -0.10986 | -0.16022 | 0.22888 | 0.20142 | -0.022888 | -0.24262 | 0.23804 | -0.2655 | -0.24262 | -0.17395 | 121.257 | 121.6919 | 61.8713 | -121.4127 | 121.2204 | 121.2891 | 61.8988 | -121.4859
173.2344 | 121.7102 | -61.7065 | 59.848 | -0.15381 | 0.0051825 | 0.064016 | 0.065636 | 0.12781 | -0.0028071 | -0.0059023 | -0.084686 | -0.0083526 | 0.057864 | 0.067206 | -0.00050621 | -0.0068551 | 60.0403 | 60.0266 | 0.25635 | -61.7477 | 59.6375 | -61.6791 | -61.6058 | -61.4914 | 0.2243 | -61.9858 | 59.6649 | 59.6924 | -61.4594 | -61.6882 | 0.027466 | 0.10071 | -0.21057 | 121.7331 | -0.041199 | -0.14191 | 0.19226 | 0.24719 | 0.018311 | -0.1831 | 0.21515 | -0.27924 | -0.29755 | -0.15564 | 121.344 | 121.7468 | 61.9629 | -121.4539 | 121.3715 | 121.3989 | 61.9308 | -121.5363
175 | 121.6919 | -61.8118 | 59.7244 | -0.016479 | 0.0083869 | 0.059958 | 0.062645 | 0.12631 | 0.0027471 | -0.0035525 | 0.045013 | -0.0092072 | 0.059787 | 0.071478 | 0.004407 | -0.0062143 | 59.9304 | 59.8755 | 0.022888 | -61.8988 | 59.5551 | -61.821 | -61.7249 | -61.6379 | -0.032043 | -62.1735 | 59.5596 | 59.5459 | -61.5692 | -61.821 | -0.009155 | 0.086975 | -0.16937 | 121.6873 | -0.086975 | -0.17395 | 0.20599 | 0.24262 | -0.009155 | -0.16479 | 0.17395 | -0.36163 | -0.35248 | -0.17853 | 121.3669 | 121.7422 | 61.8347 | -121.4493 | 121.3715 | 121.3577 | 61.7798 | -121.5454
176.6719 | 121.8521 | -61.6379 | 59.8251 | -0.031738 | 0.0034735 | 0.065939 | 0.064781 | 0.12695 | -0.0087885 | -0.0059023 | 0.029755 | -0.010275 | 0.057437 | 0.06507 | 0.00077539 | -0.0036509 | 60.0128 | 60.0449 | 0.17395 | -61.7706 | 59.6283 | -61.6837 | -61.6013 | -61.4182 | 0.23804 | -61.9263 | 59.6375 | 59.6695 | -61.4639 | -61.6837 | -0.045777 | 0.036621 | -0.19684 | 121.6827 | -0.13275 | -0.16937 | 0.18768 | 0.17395 | -0.045777 | -0.18768 | 0.21973 | -0.28839 | -0.24262 | -0.15564 | 121.2662 | 121.6507 | 61.8118 | -121.4264 | 121.2753 | 121.3074 | 61.8759 | -121.5088
178.4219 | 121.8155 | -61.7615 | 59.6786 | 0.11322 | 0.0041143 | 0.059744 | 0.06115 | 0.12546 | 0.00082452 | -0.0041933 | 0.1976 | -0.008139 | 0.056796 | 0.069128 | 0.004407 | -0.0072825 | 59.8663 | 59.8389 | -0.082397 | -61.9446 | 59.5642 | -61.8164 | -61.7386 | -61.5967 | -0.07782 | -62.1414 | 59.5551 | 59.5367 | -61.6013 | -61.8164 | -0.054931 | 0.022889 | -0.11444 | 121.6003 | -0.18311 | -0.20599 | 0.18768 | 0.16022 | -0.054931 | -0.1236 | 0.16479 | -0.37994 | -0.32501 | -0.14191 | 121.3257 | 121.6278 | 61.6791 | -121.4172 | 121.3165 | 121.2982 | 61.6837 | -121.4951
180.1094 | 121.7651 | -61.7661 | 59.7794 | -0.16144 | 0.0056097 | 0.063375 | 0.063713 | 0.1246 | -0.0010981 | -0.0044071 | -0.099945 | -0.0083526 | 0.054446 | 0.06806 | 0.0046206 | -0.0047189 | 59.9625 | 59.903 | 0.11902 | -61.8301 | 59.6558 | -61.7432 | -61.6745 | -61.5417 | 0.13275 | -62.0911 | 59.6375 | 59.6695 | -61.496 | -61.7203 | 0.022888 | 0.091552 | -0.1236 | 121.669 | -0.064087 | -0.15564 | 0.1831 | 0.27008 | 0.045776 | -0.14191 | 0.2243 | -0.32501 | -0.37079 | -0.10986 | 121.4218 | 121.7285 | 61.8851 | -121.4539 | 121.4035 | 121.4355 | 61.8988 | -121.4996
181.8438 | 121.843 | -61.6699 | 59.816 | 0.021668 | 0.0032599 | 0.064871 | 0.062218 | 0.12375 | -0.0068659 | -0.0054751 | 0.13657 | -0.0096344 | 0.055942 | 0.06571 | 0.0012028 | -0.0051463 | 59.9533 | 59.9808 | 0.10529 | -61.8027 | 59.6146 | -61.7294 | -61.615 | -61.5051 | 0.13275 | -62.0087 | 59.5917 | 59.6237 | -61.5005 | -61.7157 | -0.059509 | 0.054932 | -0.20142 | 121.6507 | -0.13275 | -0.18768 | 0.13733 | 0.16937 | -0.045776 | -0.2243 | 0.16479 | -0.33875 | -0.29297 | -0.19226 | 121.2845 | 121.6232 | 61.7752 | -121.431 | 121.2616 | 121.2936 | 61.8027 | -121.5317
183.5781 | 121.8796 | -61.6562 | 59.8343 | -0.016479 | 0.0075323 | 0.063162 | 0.06414 | 0.12503 | -0.0034479 | -0.0056887 | 0.060272 | -0.011771 | 0.057223 | 0.066565 | 0.0012028 | -0.0049325 | 60.0266 | 60.0266 | 0.16479 | -61.7706 | 59.6146 | -61.6882 | -61.5921 | -61.409 | 0.23346 | -61.9308 | 59.6283 | 59.6558 | -61.4548 | -61.6699 | -0.032043 | 0.064087 | -0.21973 | 121.6827 | -0.11444 | -0.17853 | 0.19226 | 0.20142 | -0.013733 | -0.20599 | 0.24719 | -0.27466 | -0.26093 | -0.17853 | 121.2708 | 121.6827 | 61.821 | -121.4264 | 121.2845 | 121.312 | 61.8896 | -121.5042
185.2656 | 121.7194 | -61.7203 | 59.8343 | -0.12329 | 0.01031 | 0.063162 | 0.063499 | 0.12567 | -0.0017389 | -0.0080387 | -0.13809 | -0.0096344 | 0.055942 | 0.066138 | 0.0014164 | -0.0060007 | 59.9762 | 59.9487 | 0.14648 | -61.8256 | 59.6649 | -61.7294 | -61.6241 | -61.5463 | 0.16022 | -62.0544 | 59.6786 | 59.6832 | -61.5051 | -61.7111 | -0.009155 | 0.09613 | -0.16937 | 121.669 | -0.10529 | -0.20142 | 0.14191 | 0.21515 | 0.009155 | -0.15564 | 0.17395 | -0.33417 | -0.34332 | -0.15106 | 121.3852 | 121.6965 | 61.8668 | -121.4584 | 121.3989 | 121.4035 | 61.8805 | -121.5454
187 | 121.6965 | -61.8118 | 59.7244 | 0.044556 | 0.0098821 | 0.059744 | 0.060295 | 0.12546 | 0.0036017 | -0.0054751 | 0.075531 | -0.0083526 | 0.058719 | 0.069556 | 0.00163 | -0.0064279 | 59.8663 | 59.7931 | -0.064087 | -61.9446 | 59.5459 | -61.8484 | -61.7569 | -61.6653 | -0.082397 | -62.2147 | 59.5642 | 59.5642 | -61.6058 | -61.8347 | -0.036621 | 0.054932 | -0.17853 | 121.6049 | -0.13275 | -0.18768 | 0.14191 | 0.20599 | -0.022888 | -0.16022 | 0.14649 | -0.40283 | -0.37994 | -0.16022 | 121.3577 | 121.6782 | 61.7477 | -121.4813 | 121.376 | 121.376 | 61.7294 | -121.5591
188.7344 | 121.7102 | -61.8073 | 59.7382 | 0.090332 | 0.0056097 | 0.062307 | 0.060295 | 0.12674 | 0.0044561 | -0.0026981 | 0.075531 | -0.0057892 | 0.055942 | 0.067206 | 0.0046206 | -0.0074961 | 59.8572 | 59.8206 | -0.059509 | -61.94 | 59.5505 | -61.8301 | -61.7523 | -61.6745 | -0.082397 | -62.2101 | 59.5551 | 59.5825 | -61.6104 | -61.8393 | -0.022888 | 0.054932 | -0.18768 | 121.6278 | -0.13275 | -0.18768 | 0.11902 | 0.19684 | -0.032043 | -0.18311 | 0.13275 | -0.40283 | -0.37079 | -0.15564 | 121.3577 | 121.6644 | 61.7477 | -121.4905 | 121.3623 | 121.3898 | 61.7249 | -121.5775
190.5 | 121.8521 | -61.6333 | 59.816 | -0.039368 | 0.0039007 | 0.066366 | 0.063713 | 0.1308 | -0.0072931 | -0.0031253 | 0.014496 | -0.011984 | 0.056582 | 0.066351 | 0.0012028 | -0.0055735 | 60.054 | 60.0906 | 0.23346 | -61.7569 | 59.5963 | -61.6974 | -61.5829 | -61.3907 | 0.25635 | -61.8988 | 59.5963 | 59.6329 | -61.4548 | -61.6791 | -0.064087 | 0.050354 | -0.21973 | 121.7239 | -0.1236 | -0.17395 | 0.23804 | 0.17853 | -0.045776 | -0.21973 | 0.24262 | -0.2655 | -0.21973 | -0.1831 | 121.2296 | 121.6873 | 61.8668 | -121.3989 | 121.2296 | 121.2662 | 61.8896 | -121.4951
192.1719 | 121.8201 | -61.7706 | 59.7153 | 0.15137 | 0.0071051 | 0.064016 | 0.06179 | 0.12866 | -0.0010981 | -0.0029117 | 0.22812 | -0.008139 | 0.057437 | 0.069128 | 0.002698 | -0.0070689 | 59.9533 | 59.9304 | 0 | -61.8484 | 59.5093 | -61.7981 | -61.7065 | -61.5234 | 0.013733 | -62.059 | 59.5001 | 59.5367 | -61.5601 | -61.7706 | -0.027466 | 0.064087 | -0.20599 | 121.701 | -0.07782 | -0.14191 | 0.23804 | 0.21057 | 0 | -0.21515 | 0.24719 | -0.28839 | -0.28839 | -0.17853 | 121.2799 | 121.7239 | 61.7706 | -121.4218 | 121.2708 | 121.3074 | 61.7844 | -121.4859
193.9219 | 121.8384 | -61.6562 | 59.8206 | -0.054626 | 0.0066779 | 0.064016 | 0.065849 | 0.12482 | -0.0066523 | -0.0044071 | 0.0068663 | -0.0077118 | 0.057223 | 0.067419 | -0.0020016 | -0.0047189 | 60.0494 | 60.0403 | 0.20142 | -61.7432 | 59.6146 | -61.6791 | -61.5967 | -61.4044 | 0.24261 | -61.9034 | 59.642 | 59.6329 | -61.4273 | -61.6653 | -0.022888 | 0.059509 | -0.20599 | 121.6965 | -0.086975 | -0.14648 | 0.22888 | 0.22888 | -0.009155 | -0.17853 | 0.25177 | -0.24719 | -0.23804 | -0.18768 | 121.2708 | 121.7056 | 61.8576 | -121.4172 | 121.2982 | 121.2891 | 61.8988 | -121.4859
195.6719 | 121.7972 | -61.7706 | 59.7015 | 0.12848 | 0.0066779 | 0.063162 | 0.062645 | 0.12781 | 0.0046697 | -0.0044071 | 0.11368 | -0.0074982 | 0.058719 | 0.068487 | 0.0035526 | -0.0068551 | 59.8572 | 59.8022 | -0.10529 | -61.9492 | 59.5459 | -61.8301 | -61.7432 | -61.615 | -0.10071 | -62.1872 | 59.5551 | 59.5688 | -61.5967 | -61.8347 | -0.059509 | 0.027466 | -0.15564 | 121.5729 | -0.17853 | -0.20599 | 0.15564 | 0.17395 | -0.064087 | -0.14648 | 0.15564 | -0.41657 | -0.35248 | -0.13275 | 121.3165 | 121.6278 | 61.6653 | -121.4447 | 121.3257 | 121.3394 | 61.6699 | -121.5363
197.3594 | 121.7056 | -61.702 | 59.8343 | -0.19196 | 0.0081733 | 0.06423 | 0.066917 | 0.12759 | -0.0040887 | -0.0048343 | -0.099945 | -0.01113 | 0.058291 | 0.066779 | 0.00034819 | -0.0057871 | 60.054 | 60.0174 | 0.24719 | -61.7615 | 59.6237 | -61.6974 | -61.6013 | -61.4822 | 0.21973 | -62.0132 | 59.6786 | 59.7107 | -61.4777 | -61.6837 | 0.004577 | 0.10071 | -0.21057 | 121.7194 | -0.05951 | -0.16022 | 0.21973 | 0.2243 | 0.01831 | -0.15564 | 0.21973 | -0.31128 | -0.32959 | -0.1236 | 121.3257 | 121.756 | 61.9492 | -121.4355 | 121.3806 | 121.4127 | 61.9217 | -121.5179
199.1094 | 121.7834 | -61.647 | 59.8663 | -0.13855 | 0.0073187 | 0.063803 | 0.064781 | 0.12695 | -0.0032343 | -0.0037661 | -0.061798 | -0.00878 | 0.057864 | 0.066779 | -0.00050621 | -0.0081369 | 60.0952 | 60.0906 | 0.28839 | -61.7203 | 59.6466 | -61.6745 | -61.5784 | -61.409 | 0.31128 | -61.9125 | 59.642 | 59.6558 | -61.4273 | -61.6425 | -0.027466 | 0.068665 | -0.21973 | 121.7377 | -0.073242 | -0.14191 | 0.22888 | 0.21973 | 0.004578 | -0.2243 | 0.23804 | -0.2655 | -0.27008 | -0.21057 | 121.2936 | 121.7422 | 61.9354 | -121.4447 | 121.2891 | 121.3028 | 61.9583 | -121.5088
200.8594 | 121.8246 | -61.6425 | 59.8297 | 0.036926 | 0.0056097 | 0.065512 | 0.062218 | 0.12631 | -0.0062249 | -0.0065433 | 0.10605 | -0.010703 | 0.05701 | 0.067206 | 0.0039798 | -0.0055735 | 59.967 | 59.9716 | 0.09613 | -61.821 | 59.6237 | -61.7157 | -61.6196 | -61.4777 | 0.11902 | -61.9995 | 59.6146 | 59.6237 | -61.4685 | -61.7111 | -0.073242 | 0.022888 | -0.20599 | 121.6141 | -0.17853 | -0.20142 | 0.13733 | 0.17395 | -0.068665 | -0.21515 | 0.1648 | -0.35706 | -0.28839 | -0.20599 | 121.2662 | 121.6095 | 61.7386 | -121.4493 | 121.257 | 121.2662 | 61.7615 | -121.5408
202.6094 | 121.7422 | -61.7615 | 59.7427 | -0.22247 | 0.0066779 | 0.063803 | 0.064354 | 0.12866 | 0.0012519 | -0.0029117 | -0.15335 | -0.008139 | 0.058505 | 0.06806 | 0.00163 | -0.0070689 | 59.967 | 59.9075 | 0.11902 | -61.8256 | 59.6695 | -61.7294 | -61.6379 | -61.5463 | 0.1236 | -62.0728 | 59.6832 | 59.6603 | -61.5189 | -61.7432 | 0.032044 | 0.1236 | -0.073242 | 121.669 | -0.064087 | -0.18768 | 0.2243 | 0.24262 | 0.018311 | -0.059509 | 0.21515 | -0.31128 | -0.32959 | -0.082398 | 121.431 | 121.7285 | 61.8805 | -121.3806 | 121.4447 | 121.4218 | 61.8851 | -121.4859
204.3594 | 121.8155 | -61.647 | 59.8068 | -0.069885 | 0.0053961 | 0.064657 | 0.064781 | 0.12375 | -0.0025935 | -0.0059023 | 0.029755 | -0.0083526 | 0.056796 | 0.066992 | -7.9008e-05 | -0.0055735 | 60.0632 | 60.0723 | 0.21973 | -61.7294 | 59.6329 | -61.6791 | -61.5875 | -61.3815 | 0.24719 | -61.908 | 59.6146 | 59.6283 | -61.4502 | -61.6562 | -0.032043 | 0.05951 | -0.17395 | 121.7194 | -0.082397 | -0.14191 | 0.25635 | 0.19684 | -0.009155 | -0.19226 | 0.2655 | -0.26093 | -0.25177 | -0.17853 | 121.2799 | 121.7102 | 61.8668 | -121.3943 | 121.2616 | 121.2753 | 61.8942 | -121.463
206.0469 | 121.7285 | -61.8073 | 59.6924 | 0.097962 | 0.0056097 | 0.062948 | 0.059868 | 0.12546 | 0.0044561 | -0.0048343 | 0.098419 | -0.0079254 | 0.056582 | 0.068701 | 0.0039798 | -0.0070689 | 59.8343 | 59.761 | -0.09613 | -61.9675 | 59.5459 | -61.8484 | -61.7615 | -61.6379 | -0.1236 | -62.2192 | 59.5459 | 59.5551 | -61.6013 | -61.821 | -0.041199 | 0.045776 | -0.14648 | 121.5683 | -0.16022 | -0.20599 | 0.14191 | 0.20599 | -0.013733 | -0.14648 | 0.16937 | -0.41199 | -0.39825 | -0.13733 | 121.3531 | 121.6415 | 61.7111 | -121.4539 | 121.3531 | 121.3623 | 61.6837 | -121.5134
207.7969 | 121.8384 | -61.7523 | 59.6924 | 0.16663 | 0.0032599 | 0.063803 | 0.062645 | 0.12524 | 0.00082452 | -0.0029117 | 0.1976 | -0.0074982 | 0.056369 | 0.068701 | 0.0046206 | -0.0066415 | 59.9075 | 59.9121 | -0.013733 | -61.8713 | 59.5139 | -61.8118 | -61.702 | -61.528 | 0 | -62.0636 | 59.5184 | 59.5139 | -61.5555 | -61.7798 | -0.05951 | 0.050354 | -0.17853 | 121.6644 | -0.11902 | -0.16937 | 0.21515 | 0.19684 | -0.027466 | -0.17395 | 0.2243 | -0.31128 | -0.28381 | -0.17853 | 121.2662 | 121.6599 | 61.7386 | -121.3943 | 121.2708 | 121.2662 | 61.7523 | -121.4722
209.4844 | 121.7285 | -61.8027 | 59.7061 | 0.082703 | 0.0064643 | 0.062307 | 0.062218 | 0.12503 | 0.0025335 | -0.0035525 | 0.1442 | -0.0062164 | 0.057651 | 0.066565 | 0.0029116 | -0.0060007 | 59.8251 | 59.7656 | -0.10071 | -61.9629 | 59.523 | -61.8301 | -61.7569 | -61.6608 | -0.12817 | -62.1826 | 59.5276 | 59.5596 | -61.6013 | -61.8301 | -0.027466 | 0.045776 | -0.18311 | 121.5683 | -0.16022 | -0.20599 | 0.11902 | 0.20142 | -0.027466 | -0.17853 | 0.14191 | -0.37994 | -0.35248 | -0.14648 | 121.3257 | 121.6278 | 61.702 | -121.463 | 121.3303 | 121.3623 | 61.6745 | -121.5363
211.2344 | 121.7102 | -61.6882 | 59.8434 | -0.13855 | 0.0081733 | 0.062094 | 0.064995 | 0.12674 | -0.0036615 | -0.0029117 | -0.054169 | -0.0094208 | 0.057437 | 0.068487 | -0.0022152 | -0.0064279 | 60.054 | 60.0586 | 0.25635 | -61.7569 | 59.6191 | -61.6928 | -61.6013 | -61.4273 | 0.27924 | -61.9583 | 59.6329 | 59.6603 | -61.441 | -61.6699 | -0.004578 | 0.086975 | -0.2243 | 121.7468 | -0.068665 | -0.15564 | 0.21057 | 0.24719 | 0.01831 | -0.21057 | 0.26093 | -0.27008 | -0.28839 | -0.18311 | 121.3074 | 121.7422 | 61.9446 | -121.4447 | 121.3211 | 121.3486 | 61.9675 | -121.5134
212.9844 | 121.8155 | -61.734 | 59.7107 | 0.097962 | 0.0058233 | 0.063162 | 0.06179 | 0.12589 | -0.00067088 | -0.0035525 | 0.22049 | -0.009848 | 0.055301 | 0.067419 | 0.0041934 | -0.0053599 | 59.9442 | 59.9258 | 0.022888 | -61.8576 | 59.5047 | -61.8118 | -61.6791 | -61.5372 | 0.009155 | -62.0865 | 59.523 | 59.5093 | -61.5601 | -61.7981 | -0.07782 | 0.054932 | -0.20599 | 121.6599 | -0.1236 | -0.17853 | 0.23346 | 0.17395 | -0.064087 | -0.18768 | 0.19684 | -0.35248 | -0.28839 | -0.20142 | 121.2387 | 121.6782 | 61.7569 | -121.3898 | 121.257 | 121.2433 | 61.7432 | -121.5088
214.6719 | 121.701 | -61.8073 | 59.729 | 0.036926 | 0.0083869 | 0.063162 | 0.062431 | 0.12866 | 0.0038153 | -0.0026981 | 0.09079 | -0.0062164 | 0.056155 | 0.066992 | 0.003339 | -0.0079233 | 59.8663 | 59.8068 | -0.064087 | -61.94 | 59.5459 | -61.8393 | -61.7386 | -61.6608 | -0.073242 | -62.2009 | 59.5551 | 59.5596 | -61.5921 | -61.8393 | -0.032043 | 0.068665 | -0.18311 | 121.6141 | -0.13275 | -0.20142 | 0.13733 | 0.21515 | -0.032043 | -0.17395 | 0.14648 | -0.39368 | -0.36163 | -0.16937 | 121.3531 | 121.6736 | 61.7432 | -121.4676 | 121.3623 | 121.3669 | 61.734 | -121.5683
216.4219 | 121.7056 | -61.8073 | 59.7198 | -0.039368 | 0.010096 | 0.063162 | 0.064568 | 0.12888 | 0.0025335 | -0.0018435 | -0.054169 | -0.0085662 | 0.05936 | 0.06806 | 0.0018436 | -0.0072825 | 59.9625 | 59.9075 | 0.050354 | -61.8713 | 59.5413 | -61.7889 | -61.7249 | -61.5784 | 0.045776 | -62.1048 | 59.5825 | 59.6146 | -61.5555 | -61.7844 | 0.018311 | 0.082397 | -0.17853 | 121.7148 | -0.064087 | -0.14648 | 0.24261 | 0.25177 | 0.022888 | -0.13733 | 0.22888 | -0.29755 | -0.32043 | -0.10529 | 121.3486 | 121.7697 | 61.8576 | -121.4447 | 121.3898 | 121.4218 | 61.853 | -121.5042
218.1094 | 121.7972 | -61.6608 | 59.848 | -0.10803 | 0.0068915 | 0.062521 | 0.066277 | 0.12781 | -0.0068659 | -0.0056887 | -0.03891 | -0.010916 | 0.057223 | 0.066351 | -0.0011472 | -0.0051463 | 60.0632 | 60.0906 | 0.27924 | -61.7294 | 59.61 | -61.6653 | -61.5875 | -61.3953 | 0.30212 | -61.9034 | 59.6283 | 59.6695 | -61.4044 | -61.6516 | -0.004577 | 0.073243 | -0.23804 | 121.7514 | -0.068664 | -0.14191 | 0.21515 | 0.25635 | 0.009156 | -0.21973 | 0.2655 | -0.24261 | -0.25177 | -0.17853 | 121.2708 | 121.7239 | 61.94 | -121.4355 | 121.2891 | 121.3303 | 61.9629 | -121.4996
219.8594 | 121.7239 | -61.702 | 59.8114 | -0.16144 | 0.0043279 | 0.062307 | 0.06414 | 0.12418 | -0.0015253 | -0.0050479 | -0.14572 | -0.010275 | 0.058932 | 0.069983 | 0.00013459 | -0.0051463 | 59.9625 | 59.9442 | 0.15106 | -61.8301 | 59.6786 | -61.7249 | -61.6379 | -61.5234 | 0.14648 | -62.059 | 59.6832 | 59.6924 | -61.5097 | -61.6882 | -0.022889 | 0.064087 | -0.13275 | 121.6461 | -0.12817 | -0.19226 | 0.15106 | 0.19226 | 0.013733 | -0.12817 | 0.17853 | -0.35706 | -0.37079 | -0.11902 | 121.3806 | 121.6644 | 61.853 | -121.4493 | 121.3852 | 121.3943 | 61.8484 | -121.4996
221.5469 | 121.8246 | -61.615 | 59.8251 | -0.085144 | 0.0041143 | 0.063375 | 0.065636 | 0.12759 | -0.0072931 | -0.0056887 | 0.022125 | -0.007071 | 0.05701 | 0.066992 | -0.00093361 | -0.0062143 | 60.0494 | 60.0632 | 0.25177 | -61.7432 | 59.6054 | -61.6928 | -61.5829 | -61.3724 | 0.25635 | -61.8942 | 59.6191 | 59.6512 | -61.4044 | -61.6653 | -0.07782 | 0.032043 | -0.21973 | 121.6782 | -0.12817 | -0.16022 | 0.2243 | 0.21057 | -0.050354 | -0.20599 | 0.24262 | -0.27924 | -0.22888 | -0.17395 | 121.2204 | 121.6644 | 61.8668 | -121.4081 | 121.2341 | 121.2662 | 61.8713 | -121.4905
223.2812 | 121.7194 | -61.7477 | 59.8251 | -0.16907 | 0.0088141 | 0.062094 | 0.066063 | 0.12589 | 0.00082452 | -0.0056887 | -0.16098 | -0.010062 | 0.059146 | 0.068274 | 0.00163 | -0.0055735 | 59.9716 | 59.9213 | 0.15564 | -61.821 | 59.6741 | -61.7157 | -61.6104 | -61.528 | 0.14648 | -62.059 | 59.6695 | 59.7015 | -61.4639 | -61.7111 | 0.032044 | 0.13733 | -0.15106 | 121.669 | -0.073242 | -0.21057 | 0.14648 | 0.28381 | 0.036621 | -0.15564 | 0.21973 | -0.31128 | -0.3479 | -0.1236 | 121.4218 | 121.7194 | 61.9034 | -121.4355 | 121.4172 | 121.4493 | 61.8942 | -121.5363
225.0312 | 121.7789 | -61.6653 | 59.816 | -0.14618 | 0.0043279 | 0.064444 | 0.064995 | 0.12631 | -0.0028071 | -0.0061161 | -0.054169 | -0.0089936 | 0.057437 | 0.066992 | 0.00098899 | -0.0062143 | 60.0769 | 60.0815 | 0.27924 | -61.7386 | 59.6512 | -61.6608 | -61.5875 | -61.409 | 0.29297 | -61.9263 | 59.6283 | 59.6558 | -61.4502 | -61.6608 | 0.004577 | 0.07782 | -0.16479 | 121.7468 | -0.073242 | -0.15106 | 0.26093 | 0.21515 | 0.004577 | -0.18768 | 0.25635 | -0.26093 | -0.2655 | -0.16022 | 121.3165 | 121.7422 | 61.9446 | -121.4035 | 121.2936 | 121.3211 | 61.9583 | -121.4767
226.7031 | 121.7468 | -61.8073 | 59.6924 | 0.097962 | 0.0060369 | 0.060812 | 0.059868 | 0.12781 | 0.00039732 | -0.0046207 | 0.1442 | -0.0085662 | 0.05701 | 0.067847 | 0.005048 | -0.0053599 | 59.8297 | 59.761 | -0.13733 | -61.9629 | 59.5459 | -61.853 | -61.7661 | -61.6608 | -0.1236 | -62.1918 | 59.5642 | 59.5551 | -61.6241 | -61.8439 | -0.045776 | 0.041199 | -0.14648 | 121.5683 | -0.15564 | -0.19684 | 0.13733 | 0.1831 | -0.036621 | -0.12817 | 0.14648 | -0.38452 | -0.3479 | -0.13733 | 121.3531 | 121.637 | 61.6699 | -121.4584 | 121.3715 | 121.3623 | 61.6837 | -121.5363
228.4531 | 121.7743 | -61.6653 | 59.816 | -0.13855 | 0.0073187 | 0.06423 | 0.064995 | 0.12717 | -0.0047297 | -0.0041933 | -0.069428 | -0.011557 | 0.056796 | 0.065497 | 0.0022708 | -0.0027963 | 60.054 | 60.0952 | 0.29297 | -61.7249 | 59.642 | -61.6653 | -61.6013 | -61.409 | 0.28839 | -61.9217 | 59.6329 | 59.6512 | -61.4639 | -61.6745 | 0 | 0.064087 | -0.17395 | 121.7606 | -0.05951 | -0.1236 | 0.23804 | 0.20142 | -0.009156 | -0.1831 | 0.25635 | -0.25635 | -0.24719 | -0.16479 | 121.3074 | 121.7194 | 61.9583 | -121.4172 | 121.2982 | 121.3165 | 61.9537 | -121.4905
230.125 | 121.7377 | -61.7889 | 59.697 | 0.12085 | 0.0071051 | 0.061666 | 0.062431 | 0.12589 | 0.0021063 | -0.0037661 | 0.12131 | -0.0089936 | 0.058505 | 0.069983 | 0.0039798 | -0.0060007 | 59.8297 | 59.7748 | -0.1236 | -61.9492 | 59.5505 | -61.8439 | -61.7477 | -61.647 | -0.1236 | -62.1964 | 59.5413 | 59.5505 | -61.5784 | -61.8484 | -0.054932 | 0.041198 | -0.14648 | 121.5637 | -0.16022 | -0.20142 | 0.13275 | 0.21057 | -0.05951 | -0.15564 | 0.14191 | -0.40741 | -0.3479 | -0.14648 | 121.3394 | 121.6187 | 61.6653 | -121.4447 | 121.3303 | 121.3394 | 61.6653 | -121.5454
231.8594 | 121.7834 | -61.6974 | 59.7656 | 0.12848 | 0.0045417 | 0.063162 | 0.061363 | 0.1293 | -0.0032343 | -0.0020571 | 0.1976 | -0.008139 | 0.056796 | 0.068274 | 0.0018436 | -0.0051463 | 59.9442 | 59.967 | 0.045776 | -61.853 | 59.5047 | -61.7569 | -61.7065 | -61.4868 | 0.041199 | -62.0178 | 59.5367 | 59.5596 | -61.528 | -61.734 | -0.059509 | -0.009155 | -0.26093 | 121.6644 | -0.15564 | -0.14648 | 0.17853 | 0.16937 | -0.036621 | -0.22888 | 0.21057 | -0.32043 | -0.28381 | -0.20599 | 121.2021 | 121.6415 | 61.7432 | -121.4722 | 121.2341 | 121.257 | 61.7386 | -121.4996
233.5938 | 121.788 | -61.6837 | 59.7839 | 0.029297 | 0.0041143 | 0.065084 | 0.061363 | 0.12717 | -0.0028071 | -0.0067569 | 0.15945 | -0.0096344 | 0.055301 | 0.066138 | 0.0012028 | -0.0038645 | 59.9579 | 59.9533 | 0.059509 | -61.8301 | 59.5688 | -61.7203 | -61.6516 | -61.5005 | 0.086975 | -62.0041 | 59.5779 | 59.6191 | -61.4685 | -61.7065 | -0.036621 | 0.032044 | -0.21515 | 121.637 | -0.14648 | -0.17853 | 0.17395 | 0.21515 | -0.022888 | -0.20599 | 0.18311 | -0.32043 | -0.29755 | -0.16479 | 121.2524 | 121.6415 | 61.7432 | -121.4355 | 121.2616 | 121.3028 | 61.7706 | -121.4905
235.3438 | 121.7468 | -61.7615 | 59.7427 | -0.13855 | 0.0051825 | 0.061239 | 0.061577 | 0.12888 | 0.0018927 | -0.0041933 | -0.084686 | -0.00878 | 0.057223 | 0.068915 | 0.0048344 | -0.0079233 | 59.9442 | 59.9075 | 0.09613 | -61.8393 | 59.6008 | -61.7661 | -61.6837 | -61.5509 | 0.09613 | -62.0865 | 59.61 | 59.6237 | -61.5555 | -61.7706 | -0.004577 | 0.07782 | -0.14191 | 121.669 | -0.077819 | -0.15564 | 0.20142 | 0.20599 | -0.009155 | -0.13275 | 0.21057 | -0.32501 | -0.31586 | -0.11902 | 121.3623 | 121.7056 | 61.8576 | -121.4264 | 121.3715 | 121.3852 | 61.8576 | -121.5134
237.0469 | 121.6782 | -61.8256 | 59.729 | 0.075073 | 0.0064643 | 0.059958 | 0.062218 | 0.12824 | 0.0027471 | -0.0012027 | 0.098419 | -0.0066436 | 0.057223 | 0.067847 | 0.0041934 | -0.0066415 | 59.848 | 59.7794 | -0.054932 | -61.9308 | 59.5276 | -61.8256 | -61.7569 | -61.647 | -0.07782 | -62.2009 | 59.5688 | 59.5917 | -61.5784 | -61.8439 | 0 | 0.068665 | -0.20142 | 121.6049 | -0.10529 | -0.17395 | 0.11902 | 0.24719 | -0.01831 | -0.16022 | 0.17853 | -0.37537 | -0.35706 | -0.13733 | 121.3531 | 121.6736 | 61.7706 | -121.4859 | 121.3943 | 121.4172 | 61.7477 | -121.5729
238.7969 | 121.7285 | -61.7981 | 59.7015 | 0.052185 | 0.0068915 | 0.062307 | 0.063072 | 0.12738 | 0.0014655 | -0.0031253 | 0.13657 | -0.0096344 | 0.057651 | 0.066565 | 0.0029116 | -0.0072825 | 59.8114 | 59.7519 | -0.11444 | -61.9629 | 59.5276 | -61.821 | -61.7569 | -61.6653 | -0.11902 | -62.2055 | 59.5413 | 59.5505 | -61.6104 | -61.8484 | -0.022888 | 0.041199 | -0.17395 | 121.55 | -0.16479 | -0.20599 | 0.10986 | 0.18768 | -0.050354 | -0.16022 | 0.13275 | -0.40741 | -0.35706 | -0.15106 | 121.3257 | 121.6095 | 61.6837 | -121.4584 | 121.3394 | 121.3486 | 61.6791 | -121.55
240.5469 | 121.8292 | -61.6516 | 59.8343 | 0.0064086 | 0.0034735 | 0.063803 | 0.063713 | 0.12695 | -0.0077203 | -0.0035525 | 0.15945 | -0.0096344 | 0.056796 | 0.063147 | -0.0011472 | -0.0045053 | 59.9533 | 59.9762 | 0.10529 | -61.8118 | 59.6054 | -61.7157 | -61.6562 | -61.496 | 0.11444 | -61.9995 | 59.6146 | 59.6146 | -61.4868 | -61.7111 | -0.064087 | -0.004578 | -0.22888 | 121.6278 | -0.16022 | -0.15564 | 0.11902 | 0.1648 | -0.05951 | -0.21973 | 0.15564 | -0.3479 | -0.28839 | -0.21973 | 121.257 | 121.6049 | 61.7569 | -121.4905 | 121.2662 | 121.2662 | 61.7661 | -121.5454
242.2344 | 121.8246 | -61.7432 | 59.7107 | 0.11322 | 0.0064643 | 0.061666 | 0.063072 | 0.12717 | -0.0017389 | -0.0039797 | 0.22812 | -0.009848 | 0.056369 | 0.066992 | 0.0018436 | -0.0053599 | 59.9487 | 59.9213 | 0 | -61.8439 | 59.5001 | -61.7752 | -61.7065 | -61.5326 | -0.004578 | -62.0682 | 59.5047 | 59.5322 | -61.5692 | -61.7752 | -0.032044 | 0.036621 | -0.21057 | 121.6644 | -0.10071 | -0.13733 | 0.23804 | 0.17395 | -0.032044 | -0.20599 | 0.21057 | -0.32501 | -0.29297 | -0.17853 | 121.2433 | 121.6919 | 61.7432 | -121.4172 | 121.2479 | 121.2753 | 61.7386 | -121.4859
243.9844 | 121.7056 | -61.7065 | 59.8297 | -0.15381 | 0.0096685 | 0.063162 | 0.066704 | 0.12738 | -0.0021661 | -0.0037661 | -0.069428 | -0.010275 | 0.059787 | 0.065497 | -0.0015744 | -0.0081369 | 60.0266 | 60.0266 | 0.2655 | -61.7386 | 59.6237 | -61.6837 | -61.5829 | -61.4731 | 0.23804 | -61.9812 | 59.6466 | 59.6649 | -61.4319 | -61.6974 | 0.022888 | 0.1236 | -0.20599 | 121.7331 | -0.032043 | -0.15564 | 0.19684 | 0.27466 | 0.009155 | -0.18311 | 0.23346 | -0.27466 | -0.28381 | -0.16479 | 121.3303 | 121.7331 | 61.972 | -121.4127 | 121.3531 | 121.3715 | 61.9446 | -121.5271
245.7344 | 121.7056 | -61.8118 | 59.7427 | -0.046997 | 0.0058233 | 0.061453 | 0.062218 | 0.12695 | 0.0029607 | -0.0026981 | -0.031281 | -0.0055756 | 0.057651 | 0.067633 | 0.0035526 | -0.0081369 | 59.9442 | 59.8984 | 0.086975 | -61.8622 | 59.5688 | -61.7981 | -61.7249 | -61.5646 | 0.050354 | -62.0956 | 59.5734 | 59.5871 | -61.5234 | -61.7935 | 0.013733 | 0.086975 | -0.17395 | 121.7102 | -0.050354 | -0.13733 | 0.20142 | 0.28839 | 0.018311 | -0.16937 | 0.24719 | -0.28381 | -0.30212 | -0.15564 | 121.3806 | 121.756 | 61.8988 | -121.4676 | 121.3852 | 121.3989 | 61.8622 | -121.5363
247.4219 | 121.7148 | -61.8256 | 59.7198 | -0.031738 | 0.011805 | 0.061453 | 0.06414 | 0.12375 | 0.0010381 | -0.0029117 | -0.031281 | -0.007071 | 0.058078 | 0.068487 | 0.0024844 | -0.0079233 | 59.9533 | 59.8938 | 0.064087 | -61.8713 | 59.5779 | -61.7798 | -61.6928 | -61.5646 | 0.054932 | -62.0865 | 59.5734 | 59.6008 | -61.5509 | -61.7798 | 0.045777 | 0.13275 | -0.14191 | 121.7194 | -0.045776 | -0.17853 | 0.23346 | 0.27466 | 0.045777 | -0.14649 | 0.26093 | -0.26093 | -0.3067 | -0.11902 | 121.4035 | 121.7789 | 61.8896 | -121.4127 | 121.3989 | 121.4264 | 61.8805 | -121.4996
249.1562 | 121.6965 | -61.8439 | 59.729 | 0.0064086 | 0.0064643 | 0.063162 | 0.060082 | 0.12589 | 0.0016791 | -0.0012027 | 0.045013 | -0.008139 | 0.057864 | 0.067419 | 0.0039798 | -0.0049325 | 59.8526 | 59.8206 | -0.032043 | -61.9354 | 59.5276 | -61.821 | -61.734 | -61.6333 | -0.064087 | -62.1918 | 59.5505 | 59.5871 | -61.5829 | -61.821 | 0.022888 | 0.10986 | -0.20142 | 121.6644 | -0.091553 | -0.20142 | 0.1236 | 0.26093 | 0.022888 | -0.17853 | 0.21057 | -0.3479 | -0.37079 | -0.14191 | 121.3715 | 121.6965 | 61.8118 | -121.463 | 121.3943 | 121.431 | 61.7798 | -121.55
250.8438 | 121.8475 | -61.6425 | 59.8022 | -0.0088499 | 0.0058233 | 0.063803 | 0.068626 | 0.12845 | -0.0077203 | -0.0037661 | 0.09079 | -0.0089936 | 0.058719 | 0.068274 | -0.0020016 | -0.0057871 | 59.9716 | 60.0082 | 0.16479 | -61.7844 | 59.5963 | -61.6837 | -61.6058 | -61.4319 | 0.21973 | -61.9217 | 59.6512 | 59.6237 | -61.4456 | -61.6608 | -0.041199 | 0.036621 | -0.20599 | 121.6507 | -0.14191 | -0.17853 | 0.16937 | 0.19684 | -0.018311 | -0.15106 | 0.21057 | -0.27924 | -0.26093 | -0.17853 | 121.2387 | 121.6141 | 61.8073 | -121.4081 | 121.2936 | 121.2662 | 61.8622 | -121.463
252.5938 | 121.7056 | -61.8073 | 59.7153 | 0.014038 | 0.010096 | 0.059958 | 0.062218 | 0.12482 | 0.0033881 | -0.0050479 | 0.060272 | -0.0074982 | 0.061496 | 0.067633 | 0.002698 | -0.0064279 | 59.8434 | 59.7794 | -0.068665 | -61.9354 | 59.5322 | -61.7981 | -61.7523 | -61.6516 | -0.086975 | -62.2009 | 59.5688 | 59.5963 | -61.6104 | -61.8347 | 0.009155 | 0.054932 | -0.18311 | 121.5866 | -0.12817 | -0.18311 | 0.12817 | 0.19684 | -0.027466 | -0.14648 | 0.15564 | -0.39368 | -0.36621 | -0.11902 | 121.3394 | 121.6507 | 61.7386 | -121.4676 | 121.376 | 121.4035 | 61.7203 | -121.55
254.3281 | 121.8292 | -61.7523 | 59.7107 | 0.10559 | 0.0045417 | 0.061666 | 0.06179 | 0.12589 | 0.00018372 | -0.0039797 | 0.22812 | -0.0066436 | 0.057864 | 0.068274 | 0.0037662 | -0.0051463 | 59.8572 | 59.8068 | -0.086975 | -61.94 | 59.5413 | -61.8118 | -61.7569 | -61.5921 | -0.09613 | -62.1506 | 59.5367 | 59.5596 | -61.5967 | -61.821 | -0.05951 | -0.004578 | -0.16937 | 121.5591 | -0.18768 | -0.1831 | 0.14648 | 0.15564 | -0.068665 | -0.17395 | 0.16022 | -0.39825 | -0.32959 | -0.15106 | 121.2936 | 121.6095 | 61.6653 | -121.4676 | 121.2891 | 121.3119 | 61.6562 | -121.5317
256 | 121.8384 | -61.6379 | 59.8297 | -0.031738 | -0.00058528 | 0.065084 | 0.06179 | 0.12738 | -0.0087885 | -0.0054751 | 0.052643 | -0.011984 | 0.056369 | 0.066992 | -7.9008e-05 | -0.0062143 | 59.9945 | 60.0311 | 0.19226 | -61.7523 | 59.5963 | -61.6653 | -61.615 | -61.4273 | 0.22888 | -61.9171 | 59.6191 | 59.642 | -61.441 | -61.6608 | -0.027466 | 0.022888 | -0.23346 | 121.669 | -0.11444 | -0.13733 | 0.16479 | 0.19684 | -0.022889 | -0.21057 | 0.21057 | -0.27924 | -0.25635 | -0.18768 | 121.2341 | 121.6324 | 61.8301 | -121.4447 | 121.257 | 121.2799 | 61.8668 | -121.4905
257.7344 | 121.6919 | -61.6974 | 59.8526 | -0.19958 | 0.0079595 | 0.064444 | 0.066277 | 0.12866 | -0.0010981 | -0.0052615 | -0.069428 | -0.0094208 | 0.05936 | 0.068701 | -0.0015744 | -0.0072825 | 60.0128 | 59.9945 | 0.2243 | -61.7661 | 59.6146 | -61.6837 | -61.6333 | -61.5326 | 0.20142 | -62.0132 | 59.6832 | 59.6832 | -61.4639 | -61.7065 | 0.013733 | 0.064087 | -0.23804 | 121.6919 | -0.068664 | -0.13275 | 0.16022 | 0.23346 | -0.009155 | -0.16937 | 0.16479 | -0.31586 | -0.3067 | -0.16937 | 121.312 | 121.7102 | 61.9217 | -121.4859 | 121.3806 | 121.3806 | 61.8988 | -121.5591
259.4844 | 121.7743 | -61.6882 | 59.7565 | 0.15137 | 0.0045417 | 0.061453 | 0.059868 | 0.12546 | -0.0025935 | -0.0050479 | 0.20523 | -0.0089936 | 0.056796 | 0.067206 | 0.0022708 | -0.0064279 | 59.9579 | 59.9579 | 0.036621 | -61.8439 | 59.5322 | -61.7661 | -61.6608 | -61.4868 | 0.041199 | -62.0178 | 59.5459 | 59.5413 | -61.5555 | -61.7477 | -0.07782 | 0.027465 | -0.2243 | 121.6461 | -0.15564 | -0.1831 | 0.20142 | 0.13275 | -0.05951 | -0.21057 | 0.20142 | -0.32959 | -0.27008 | -0.21515 | 121.2204 | 121.6461 | 61.7249 | -121.4172 | 121.2341 | 121.2296 | 61.7294 | -121.5042
261.1719 | 121.8246 | -61.7523 | 59.7107 | 0.11322 | 0.0060369 | 0.062307 | 0.063713 | 0.12439 | 0.0016791 | -0.0052615 | 0.17471 | -0.00878 | 0.057864 | 0.068915 | 0.0046206 | -0.0062143 | 59.8755 | 59.8068 | -0.086975 | -61.9263 | 59.523 | -61.821 | -61.7294 | -61.6104 | -0.11444 | -62.1414 | 59.5322 | 59.5642 | -61.6104 | -61.7935 | -0.068665 | 0.022888 | -0.18768 | 121.5591 | -0.17395 | -0.19684 | 0.16479 | 0.14191 | -0.041199 | -0.17853 | 0.14191 | -0.3891 | -0.3479 | -0.14648 | 121.2753 | 121.6278 | 61.6653 | -121.4401 | 121.2845 | 121.3165 | 61.6379 | -121.5042
262.9219 | 121.6873 | -61.7157 | 59.8434 | -0.1767 | 0.0068915 | 0.062307 | 0.067558 | 0.12781 | -0.00088448 | -0.0031253 | -0.046539 | -0.010489 | 0.055942 | 0.067847 | 0.00034819 | -0.0060007 | 59.9991 | 59.9716 | 0.19226 | -61.7935 | 59.6512 | -61.702 | -61.6013 | -61.5143 | 0.16022 | -62.0453 | 59.6466 | 59.7061 | -61.4731 | -61.6974 | 0.013733 | 0.11444 | -0.19226 | 121.6873 | -0.07782 | -0.19226 | 0.15564 | 0.24262 | 0.01831 | -0.19684 | 0.20142 | -0.32959 | -0.3479 | -0.13733 | 121.3669 | 121.7148 | 61.908 | -121.4447 | 121.3623 | 121.4218 | 61.8759 | -121.5408
264.6719 | 121.6919 | -61.6699 | 59.8389 | -0.21484 | 0.0094549 | 0.062735 | 0.065849 | 0.12439 | -0.0013117 | -0.0039797 | -0.12283 | -0.010275 | 0.056796 | 0.068274 | 0.0014164 | -0.0072825 | 60.0266 | 60.0266 | 0.23804 | -61.7477 | 59.6283 | -61.6882 | -61.6104 | -61.4822 | 0.21057 | -62.0087 | 59.6649 | 59.697 | -61.4822 | -61.6974 | -0.01831 | 0.059509 | -0.21057 | 121.6965 | -0.07782 | -0.13733 | 0.18768 | 0.18768 | -0.027466 | -0.17395 | 0.18768 | -0.33875 | -0.31128 | -0.14191 | 121.2982 | 121.6965 | 61.908 | -121.4493 | 121.3348 | 121.3669 | 61.8805 | -121.5363
266.3594 | 121.7743 | -61.7111 | 59.7702 | 0.097962 | 0.0062505 | 0.06188 | 0.063499 | 0.12695 | -0.0062249 | -0.0052615 | 0.17471 | -0.010916 | 0.058505 | 0.066779 | 0.00163 | -0.0072825 | 59.9716 | 59.9487 | 0.086975 | -61.8347 | 59.5551 | -61.7386 | -61.6562 | -61.5005 | 0.059509 | -62.027 | 59.5642 | 59.5642 | -61.496 | -61.7249 | -0.027465 | 0.054932 | -0.21515 | 121.6599 | -0.1236 | -0.17853 | 0.20142 | 0.21515 | -0.013733 | -0.20599 | 0.21057 | -0.31586 | -0.30212 | -0.20599 | 121.2662 | 121.6827 | 61.7981 | -121.4264 | 121.2753 | 121.2753 | 61.7706 | -121.4951
268.1094 | 121.7743 | -61.6974 | 59.761 | 0.082703 | 0.0073187 | 0.063589 | 0.063499 | 0.12354 | -0.00045708 | -0.0041933 | 0.1976 | -0.0079254 | 0.05701 | 0.066992 | 0.0029116 | -0.0051463 | 59.9625 | 59.9487 | 0.064087 | -61.8484 | 59.5184 | -61.7661 | -61.6745 | -61.496 | 0.059509 | -62.0178 | 59.5413 | 59.5367 | -61.496 | -61.7432 | -0.068664 | 0.022888 | -0.24261 | 121.6461 | -0.15106 | -0.17395 | 0.20142 | 0.20142 | -0.045776 | -0.21973 | 0.20142 | -0.32043 | -0.27466 | -0.2243 | 121.2158 | 121.6599 | 61.7615 | -121.4355 | 121.2387 | 121.2341 | 61.7569 | -121.5042
269.7969 | 121.8384 | -61.6516 | 59.8114 | 0.021668 | 0.0071051 | 0.062307 | 0.06414 | 0.12567 | -0.0045161 | -0.0052615 | 0.08316 | -0.010275 | 0.056155 | 0.067206 | 0.00098899 | -0.0068551 | 59.9762 | 59.9487 | 0.10529 | -61.8027 | 59.5963 | -61.7111 | -61.6425 | -61.4731 | 0.11444 | -61.9766 | 59.5917 | 59.6329 | -61.4639 | -61.6974 | -0.05951 | 0.009155 | -0.21515 | 121.6003 | -0.15106 | -0.16022 | 0.1648 | 0.18768 | -0.045777 | -0.21973 | 0.17853 | -0.32501 | -0.27924 | -0.17853 | 121.2479 | 121.6278 | 61.7569 | -121.4539 | 121.2433 | 121.2845 | 61.7661 | -121.5088
271.5469 | 121.8109 | -61.6562 | 59.8206 | -0.10803 | 0.0043279 | 0.064444 | 0.064354 | 0.12781 | -0.0019525 | -0.0069705 | -0.03891 | -0.010062 | 0.055514 | 0.06571 | 0.0020572 | -0.0068551 | 60.0723 | 60.0861 | 0.25177 | -61.734 | 59.6146 | -61.6653 | -61.5692 | -61.3678 | 0.27924 | -61.8988 | 59.6283 | 59.6375 | -61.4365 | -61.647 | -0.009155 | 0.086975 | -0.20599 | 121.7422 | -0.07782 | -0.16479 | 0.25177 | 0.21973 | 0.009155 | -0.19226 | 0.28839 | -0.24262 | -0.25177 | -0.18311 | 121.2708 | 121.7285 | 61.908 | -121.3898 | 121.2845 | 121.2936 | 61.9354 | -121.4676
273.2812 | 121.7834 | -61.7157 | 59.7656 | 0.17426 | 0.0039007 | 0.064871 | 0.060936 | 0.12738 | -2.988e-05 | -0.0035525 | 0.20523 | -0.0094208 | 0.056582 | 0.066779 | 0.0039798 | -0.0081369 | 59.9579 | 59.9304 | 0.032043 | -61.8576 | 59.4955 | -61.8073 | -61.6837 | -61.5051 | 0.027466 | -62.0407 | 59.5184 | 59.523 | -61.5326 | -61.7706 | -0.091553 | 0.032043 | -0.27008 | 121.6461 | -0.14191 | -0.17395 | 0.19226 | 0.18311 | -0.054932 | -0.24719 | 0.21057 | -0.32501 | -0.27008 | -0.24262 | 121.2112 | 121.6736 | 61.7477 | -121.4493 | 121.2341 | 121.2387 | 61.7432 | -121.5363
275.0312 | 121.843 | -61.6516 | 59.8114 | -0.024109 | 0.0043279 | 0.063162 | 0.064781 | 0.12546 | -0.0051569 | -0.0059023 | -0.03891 | -0.011557 | 0.057223 | 0.066138 | -0.00093361 | -0.0060007 | 60.0266 | 60.0311 | 0.1831 | -61.7477 | 59.6283 | -61.6837 | -61.6058 | -61.3907 | 0.2243 | -61.9263 | 59.6329 | 59.6237 | -61.4502 | -61.6608 | -0.032044 | 0.045776 | -0.1831 | 121.6827 | -0.096131 | -0.14191 | 0.21515 | 0.20142 | -0.009156 | -0.17853 | 0.26093 | -0.27466 | -0.2655 | -0.18768 | 121.2799 | 121.6782 | 61.8347 | -121.4172 | 121.2845 | 121.2753 | 61.8759 | -121.4722
276.7812 | 121.7972 | -61.7752 | 59.6832 | 0.11322 | 0.0051825 | 0.06188 | 0.061363 | 0.12824 | 0.0044561 | -0.0029117 | 0.10605 | -0.0085662 | 0.054233 | 0.067633 | 0.0039798 | -0.0068551 | 59.8801 | 59.8022 | -0.09613 | -61.9446 | 59.5688 | -61.8256 | -61.7523 | -61.5967 | -0.11444 | -62.1597 | 59.5734 | 59.5779 | -61.5967 | -61.8164 | -0.050354 | 0.022889 | -0.11444 | 121.5775 | -0.16937 | -0.19226 | 0.19684 | 0.17853 | -0.041198 | -0.10986 | 0.17853 | -0.38452 | -0.34332 | -0.10529 | 121.344 | 121.6553 | 61.6791 | -121.4355 | 121.3486 | 121.3531 | 61.6608 | -121.4996
278.4531 | 121.7377 | -61.7249 | 59.7931 | -0.15381 | 0.0088141 | 0.065084 | 0.068626 | 0.12888 | 0.0016791 | -0.0059023 | -0.10757 | -0.0077118 | 0.060428 | 0.067847 | 0.00163 | -0.0053599 | 59.9579 | 59.9121 | 0.13275 | -61.8347 | 59.6191 | -61.7111 | -61.6745 | -61.5509 | 0.13275 | -62.0773 | 59.6466 | 59.6466 | -61.496 | -61.7523 | 0.013733 | 0.050354 | -0.17395 | 121.637 | -0.10986 | -0.16022 | 0.1648 | 0.22888 | -0.027465 | -0.14648 | 0.17395 | -0.35248 | -0.32501 | -0.14648 | 121.344 | 121.6827 | 61.8576 | -121.4676 | 121.3715 | 121.3715 | 61.8576 | -121.5454
280.1875 | 121.7056 | -61.702 | 59.8297 | -0.19196 | 0.0088141 | 0.064444 | 0.063927 | 0.12888 | -0.0023797 | -0.0039797 | -0.084686 | -0.0092072 | 0.057651 | 0.068487 | 0.0022708 | -0.0070689 | 59.9762 | 59.9487 | 0.1831 | -61.8027 | 59.6466 | -61.6882 | -61.6241 | -61.5097 | 0.16937 | -62.0361 | 59.6329 | 59.7061 | -61.4914 | -61.7111 | 0.013733 | 0.077819 | -0.18311 | 121.6507 | -0.10071 | -0.17853 | 0.14648 | 0.21057 | -0.009156 | -0.19684 | 0.19226 | -0.33417 | -0.32501 | -0.1236 | 121.3486 | 121.6782 | 61.8851 | -121.4539 | 121.3348 | 121.4081 | 61.8713 | -121.5408
281.9375 | 121.6919 | -61.702 | 59.816 | -0.18433 | 0.0071051 | 0.065084 | 0.066917 | 0.1261 | -0.0028071 | -0.0035525 | -0.15335 | -0.0085662 | 0.057223 | 0.069128 | -0.00093361 | -0.0051463 | 59.9899 | 59.967 | 0.19226 | -61.7889 | 59.6329 | -61.6837 | -61.6058 | -61.5097 | 0.17395 | -62.027 | 59.6649 | 59.6649 | -61.4914 | -61.7157 | 0.01831 | 0.09613 | -0.1831 | 121.669 | -0.086975 | -0.1831 | 0.17395 | 0.21057 | -0.013733 | -0.15106 | 0.19226 | -0.32501 | -0.31128 | -0.15106 | 121.3348 | 121.6919 | 61.8942 | -121.4218 | 121.3669 | 121.3669 | 61.8759 | -121.5317
283.6875 | 121.701 | -61.7981 | 59.7198 | -0.054626 | 0.0071051 | 0.061453 | 0.057945 | 0.12695 | 0.0014655 | -0.0020571 | -0.023651 | -0.0074982 | 0.056796 | 0.068701 | 0.0073978 | -0.0072825 | 59.9442 | 59.9167 | 0.059509 | -61.8759 | 59.5642 | -61.7752 | -61.6974 | -61.5463 | 0.068665 | -62.0819 | 59.5825 | 59.5779 | -61.5601 | -61.7981 | 0.022888 | 0.10071 | -0.15564 | 121.7148 | -0.07782 | -0.17853 | 0.2243 | 0.23804 | 0 | -0.13733 | 0.25177 | -0.28381 | -0.28381 | -0.14191 | 121.3623 | 121.7422 | 61.8576 | -121.4172 | 121.3806 | 121.376 | 61.8668 | -121.5179
285.375 | 121.7697 | -61.702 | 59.7702 | 0.18188 | 0.0051825 | 0.061453 | 0.06179 | 0.12567 | -0.0030207 | -0.0029117 | 0.18997 | -0.00878 | 0.05701 | 0.067633 | 0.0024844 | -0.0049325 | 59.935 | 59.9396 | 0.022888 | -61.8484 | 59.491 | -61.7935 | -61.702 | -61.5005 | 0.027466 | -62.0178 | 59.5047 | 59.5184 | -61.5234 | -61.7661 | -0.091553 | 0 | -0.27924 | 121.6415 | -0.14648 | -0.14648 | 0.16479 | 0.17853 | -0.064087 | -0.2655 | 0.20142 | -0.31586 | -0.25177 | -0.25177 | 121.1929 | 121.637 | 61.7249 | -121.4722 | 121.2067 | 121.2204 | 61.7294 | -121.5363
287.1406 | 121.7651 | -61.7889 | 59.7153 | 0.15137 | 0.0049689 | 0.064016 | 0.063713 | 0.12653 | 0.0010381 | -0.0020571 | 0.09079 | -0.0079254 | 0.058078 | 0.06806 | 0.0037662 | -0.0066415 | 59.8251 | 59.7885 | -0.10529 | -61.9446 | 59.5413 | -61.8301 | -61.7432 | -61.615 | -0.10529 | -62.1597 | 59.5596 | 59.5596 | -61.5692 | -61.8256 | -0.041199 | 0.045776 | -0.17395 | 121.5775 | -0.15564 | -0.20142 | 0.10986 | 0.21973 | -0.036622 | -0.15564 | 0.17395 | -0.37079 | -0.33417 | -0.15564 | 121.3303 | 121.6141 | 61.6837 | -121.4584 | 121.3486 | 121.3486 | 61.6837 | -121.5408
288.8281 | 121.7148 | -61.7294 | 59.8114 | -0.16907 | 0.0077459 | 0.061239 | 0.06649 | 0.12845 | -0.0023797 | -0.0067569 | -0.15335 | -0.008139 | 0.055942 | 0.069128 | 0.00034819 | -0.0053599 | 59.9304 | 59.935 | 0.15106 | -61.8118 | 59.6558 | -61.734 | -61.6104 | -61.5326 | 0.16022 | -62.0361 | 59.6695 | 59.7198 | -61.4914 | -61.6974 | -0.004578 | 0.11902 | -0.15564 | 121.6644 | -0.082398 | -0.20142 | 0.11902 | 0.23804 | 0.032043 | -0.14191 | 0.19684 | -0.3067 | -0.33875 | -0.091552 | 121.3852 | 121.6599 | 61.8805 | -121.4218 | 121.3989 | 121.4493 | 61.8896 | -121.5088
290.5781 | 121.7789 | -61.7065 | 59.7519 | 0.16663 | 0.0053961 | 0.061666 | 0.061577 | 0.12631 | -0.0025935 | -0.0031253 | 0.22049 | -0.009848 | 0.056582 | 0.06806 | 0.00163 | -0.0070689 | 59.9442 | 59.935 | 0.022888 | -61.8484 | 59.4727 | -61.7661 | -61.7111 | -61.5143 | 0.027466 | -62.0224 | 59.5047 | 59.5413 | -61.5463 | -61.7523 | -0.059509 | -0.004578 | -0.27924 | 121.6415 | -0.14191 | -0.13733 | 0.19226 | 0.16022 | -0.045776 | -0.24719 | 0.19226 | -0.31586 | -0.27008 | -0.21057 | 121.1792 | 121.6507 | 61.7294 | -121.463 | 121.2112 | 121.2479 | 61.734 | -121.5042
292.3281 | 121.7697 | -61.702 | 59.7702 | 0.075073 | 0.0032599 | 0.063589 | 0.063499 | 0.12738 | -0.0040887 | -0.0039797 | 0.15945 | -0.010062 | 0.058078 | 0.066779 | 0.00098899 | -0.0068551 | 59.9533 | 59.935 | 0.064087 | -61.8301 | 59.5734 | -61.7294 | -61.647 | -61.5005 | 0.07782 | -62.0087 | 59.5917 | 59.5963 | -61.4914 | -61.6928 | -0.027466 | 0.054931 | -0.19684 | 121.637 | -0.12817 | -0.18311 | 0.1831 | 0.21057 | 0.009155 | -0.17853 | 0.20142 | -0.3067 | -0.31586 | -0.17395 | 121.2753 | 121.6553 | 61.7661 | -121.4172 | 121.2936 | 121.2982 | 61.7798 | -121.463
294 | 121.6827 | -61.7111 | 59.8389 | -0.19958 | 0.0092413 | 0.061453 | 0.066063 | 0.13037 | -0.0021661 | -0.0052615 | -0.03891 | -0.010062 | 0.059787 | 0.067419 | -0.00050621 | -0.0068551 | 60.0082 | 59.9716 | 0.19684 | -61.7615 | 59.6512 | -61.6791 | -61.6058 | -61.5005 | 0.17853 | -62.0224 | 59.6649 | 59.6741 | -61.4777 | -61.7065 | 0.032044 | 0.10529 | -0.18768 | 121.6827 | -0.050354 | -0.15564 | 0.16937 | 0.23346 | 0.004578 | -0.17395 | 0.21057 | -0.31128 | -0.31586 | -0.16479 | 121.3623 | 121.7194 | 61.908 | -121.4447 | 121.376 | 121.3852 | 61.8896 | -121.5454
295.7344 | 121.7239 | -61.7111 | 59.7656 | -0.19196 | 0.0092413 | 0.062307 | 0.063286 | 0.12845 | 0.00061092 | -0.0044071 | -0.13809 | -0.0072846 | 0.058505 | 0.069769 | 0.00077539 | -0.0074961 | 59.9579 | 59.9167 | 0.14648 | -61.8164 | 59.6741 | -61.7249 | -61.6516 | -61.5463 | 0.13275 | -62.0819 | 59.6466 | 59.6558 | -61.5097 | -61.7157 | -0.013733 | 0.05951 | -0.091553 | 121.6278 | -0.10529 | -0.16479 | 0.19226 | 0.20142 | -0.004577 | -0.11902 | 0.16479 | -0.37079 | -0.36621 | -0.10986 | 121.3852 | 121.669 | 61.8576 | -121.4172 | 121.3577 | 121.3669 | 61.8439 | -121.4813
297.4219 | 121.6827 | -61.702 | 59.848 | -0.1767 | 0.0068915 | 0.064016 | 0.064781 | 0.12653 | -0.0028071 | -0.0031253 | -0.061798 | -0.0079254 | 0.057437 | 0.069128 | 0.0029116 | -0.0051463 | 60.0037 | 59.9762 | 0.21057 | -61.7798 | 59.6375 | -61.6882 | -61.615 | -61.5051 | 0.1831 | -62.0361 | 59.6649 | 59.6878 | -61.4731 | -61.7111 | 0.013733 | 0.086975 | -0.21057 | 121.6782 | -0.07782 | -0.16479 | 0.15564 | 0.22888 | -0.009156 | -0.1831 | 0.19684 | -0.33417 | -0.32501 | -0.16022 | 121.3394 | 121.7056 | 61.9125 | -121.463 | 121.3669 | 121.3898 | 61.8851 | -121.5591
299.1562 | 121.7285 | -61.7294 | 59.7656 | -0.19958 | 0.0077459 | 0.063162 | 0.064354 | 0.12631 | -0.00024348 | -0.0031253 | -0.17624 | -0.0083526 | 0.057864 | 0.067847 | 0.0018436 | -0.0070689 | 59.9442 | 59.903 | 0.13275 | -61.8118 | 59.6695 | -61.7157 | -61.6379 | -61.5372 | 0.11902 | -62.059 | 59.6558 | 59.6649 | -61.4777 | -61.7157 | 0.013733 | 0.091553 | -0.09613 | 121.6324 | -0.082398 | -0.17395 | 0.17853 | 0.25177 | 0.013733 | -0.10986 | 0.19226 | -0.32959 | -0.34332 | -0.10071 | 121.3989 | 121.6736 | 61.8622 | -121.4035 | 121.3852 | 121.3943 | 61.8484 | -121.4813
300.9062 | 121.7743 | -61.6699 | 59.7794 | 0.052185 | 0.0047553 | 0.063589 | 0.062645 | 0.12695 | -0.0043023 | -0.0044071 | 0.15945 | -0.01113 | 0.057223 | 0.066779 | 0.0012028 | -0.0057871 | 59.9487 | 59.9487 | 0.073242 | -61.8256 | 59.5642 | -61.7157 | -61.6333 | -61.5005 | 0.064087 | -62.0132 | 59.5596 | 59.5871 | -61.5143 | -61.7386 | -0.045776 | 0.036621 | -0.21515 | 121.6187 | -0.15564 | -0.19226 | 0.16937 | 0.15564 | -0.068664 | -0.21973 | 0.16937 | -0.34332 | -0.27466 | -0.19226 | 121.2341 | 121.6187 | 61.7432 | -121.4127 | 121.2296 | 121.257 | 61.734 | -121.5179
302.5938 | 121.7651 | -61.6974 | 59.7702 | 0.13611 | 0.0047553 | 0.061239 | 0.060936 | 0.12631 | -0.0040887 | -0.0039797 | 0.18234 | -0.0094208 | 0.055942 | 0.066138 | 0.0022708 | -0.0042917 | 59.935 | 59.9442 | 0.054932 | -61.8301 | 59.5276 | -61.7477 | -61.6653 | -61.4914 | 0.054932 | -62.027 | 59.5642 | 59.5917 | -61.5143 | -61.7386 | -0.050354 | 0.032044 | -0.24262 | 121.6415 | -0.13275 | -0.1648 | 0.16479 | 0.18311 | -0.041198 | -0.20599 | 0.20599 | -0.32959 | -0.28839 | -0.17853 | 121.225 | 121.6324 | 61.7523 | -121.4355 | 121.2616 | 121.2891 | 61.7523 | -121.5088
304.3438 | 121.8201 | -61.6287 | 59.816 | -0.046997 | 0.0062505 | 0.060385 | 0.065849 | 0.12567 | -0.0028071 | -0.0056887 | 0.045013 | -0.0092072 | 0.058291 | 0.066779 | -0.00050621 | -0.0060007 | 60.0266 | 60.0403 | 0.18768 | -61.7386 | 59.6191 | -61.6653 | -61.5692 | -61.409 | 0.23804 | -61.8988 | 59.6512 | 59.6466 | -61.4136 | -61.6699 | -0.036621 | 0.059509 | -0.19684 | 121.669 | -0.10986 | -0.16937 | 0.21057 | 0.21515 | -0.041199 | -0.16479 | 0.21973 | -0.27008 | -0.22888 | -0.16937 | 121.2479 | 121.6553 | 61.8164 | -121.3852 | 121.2799 | 121.2753 | 61.8668 | -121.4859
306.0312 | 121.8109 | -61.7386 | 59.6878 | 0.067444 | 0.0051825 | 0.062094 | 0.059013 | 0.12674 | 0.00018372 | -0.0048343 | 0.18997 | -0.0068572 | 0.054019 | 0.069128 | 0.0046206 | -0.0085641 | 59.9396 | 59.9121 | 0.009155 | -61.8439 | 59.5093 | -61.7935 | -61.6928 | -61.5097 | 0.004578 | -62.059 | 59.4818 | 59.5459 | -61.5692 | -61.7935 | -0.054932 | 0.045776 | -0.17853 | 121.6507 | -0.10529 | -0.15106 | 0.25177 | 0.16937 | -0.054932 | -0.20599 | 0.22888 | -0.32044 | -0.2655 | -0.14191 | 121.2479 | 121.6782 | 61.7477 | -121.3806 | 121.2204 | 121.2845 | 61.7432 | -121.4813
307.7812 | 121.7239 | -61.702 | 59.8068 | -0.19196 | 0.0096685 | 0.063162 | 0.063713 | 0.1229 | 0.00061092 | -0.0061161 | -0.16861 | -0.00878 | 0.058078 | 0.067206 | 0.00163 | -0.0066415 | 59.9716 | 59.9213 | 0.16937 | -61.8256 | 59.6603 | -61.7157 | -61.6287 | -61.528 | 0.13275 | -62.0407 | 59.6649 | 59.6878 | -61.4777 | -61.702 | -0.013733 | 0.073242 | -0.14648 | 121.6232 | -0.1236 | -0.19684 | 0.16479 | 0.2243 | 0 | -0.14191 | 0.17395 | -0.33874 | -0.33874 | -0.11902 | 121.3623 | 121.6736 | 61.8713 | -121.4355 | 121.3669 | 121.3898 | 61.8347 | -121.5088
309.4688 | 121.8201 | -61.6425 | 59.7839 | 0.021668 | 0.0056097 | 0.064657 | 0.062859 | 0.12396 | -0.0047297 | -0.0037661 | 0.060272 | -0.0089936 | 0.057223 | 0.065924 | 0.00098899 | -0.0072825 | 59.9854 | 59.9716 | 0.10529 | -61.7935 | 59.6008 | -61.7111 | -61.6241 | -61.4548 | 0.15564 | -61.9492 | 59.61 | 59.6329 | -61.4685 | -61.702 | -0.068665 | 0.01831 | -0.18311 | 121.6141 | -0.15106 | -0.16937 | 0.20142 | 0.17395 | -0.059509 | -0.17395 | 0.18768 | -0.3067 | -0.24719 | -0.15106 | 121.2433 | 121.6278 | 61.7477 | -121.4081 | 121.2524 | 121.2753 | 61.7981 | -121.4859
311.2188 | 121.7056 | -61.8073 | 59.7107 | 0.090332 | 0.0060369 | 0.061666 | 0.059013 | 0.12589 | 0.0050971 | -0.0031253 | 0.08316 | -0.007071 | 0.056582 | 0.068915 | 0.0048344 | -0.0070689 | 59.8434 | 59.7839 | -0.073242 | -61.9354 | 59.5367 | -61.8301 | -61.7386 | -61.6653 | -0.1236 | -62.2192 | 59.5596 | 59.5459 | -61.6058 | -61.8301 | -0.022888 | 0.068665 | -0.17395 | 121.5912 | -0.12817 | -0.19684 | 0.13275 | 0.20142 | -0.022888 | -0.15106 | 0.14191 | -0.41199 | -0.3891 | -0.16479 | 121.344 | 121.6507 | 61.734 | -121.4493 | 121.3669 | 121.3531 | 61.6837 | -121.5408
312.9062 | 121.7285 | -61.7615 | 59.761 | -0.11566 | 0.0096685 | 0.060598 | 0.067772 | 0.12888 | 0.00061092 | -0.0012027 | -0.15335 | -0.0089936 | 0.058078 | 0.067847 | 0.0041934 | -0.0087777 | 59.9396 | 59.8892 | 0.12817 | -61.8164 | 59.6329 | -61.7569 | -61.6608 | -61.5463 | 0.11902 | -62.0728 | 59.6512 | 59.6283 | -61.5143 | -61.734 | 0.004578 | 0.10071 | -0.12817 | 121.6507 | -0.054931 | -0.15564 | 0.17853 | 0.24719 | 0.027466 | -0.10986 | 0.21515 | -0.31128 | -0.33875 | -0.13275 | 121.3943 | 121.701 | 61.8896 | -121.4218 | 121.4127 | 121.3898 | 61.8805 | -121.4951
314.6562 | 121.8201 | -61.7432 | 59.697 | 0.15137 | 0.0071051 | 0.062094 | 0.063713 | 0.12866 | -0.00045708 | -0.0033389 | 0.1976 | -0.0094208 | 0.05466 | 0.067419 | -0.00029261 | -0.0070689 | 59.9167 | 59.8984 | 0 | -61.8484 | 59.5093 | -61.7798 | -61.7294 | -61.5143 | 0.009155 | -62.0407 | 59.5139 | 59.5413 | -61.5509 | -61.7569 | -0.036621 | 0.013733 | -0.18768 | 121.6415 | -0.10529 | -0.11902 | 0.21973 | 0.19226 | -0.013733 | -0.1831 | 0.22888 | -0.29755 | -0.28381 | -0.15564 | 121.2524 | 121.6599 | 61.7432 | -121.4264 | 121.257 | 121.2845 | 61.7523 | -121.4539
316.3438 | 121.7743 | -61.6425 | 59.8251 | -0.15381 | 0.0086005 | 0.06423 | 0.06649 | 0.12845 | -0.0051569 | -0.0050479 | -0.03891 | -0.0094208 | 0.057223 | 0.068701 | 0.00013459 | -0.0064279 | 60.0769 | 60.0769 | 0.27924 | -61.7203 | 59.6237 | -61.6562 | -61.5738 | -61.4044 | 0.30212 | -61.9034 | 59.642 | 59.6512 | -61.4502 | -61.6653 | -0.013733 | 0.068664 | -0.20142 | 121.7194 | -0.07782 | -0.14648 | 0.25177 | 0.19226 | -0.022888 | -0.1831 | 0.23804 | -0.26093 | -0.23804 | -0.17395 | 121.2662 | 121.7194 | 61.9217 | -121.3989 | 121.2845 | 121.2936 | 61.9446 | -121.4905
318.0938 | 121.6827 | -61.8118 | 59.729 | 0.097962 | 0.0081733 | 0.060598 | 0.063713 | 0.12589 | 0.0021063 | -0.0014163 | 0.08316 | -0.0085662 | 0.056155 | 0.067633 | 0.0037662 | -0.0081369 | 59.848 | 59.7702 | -0.073242 | -61.9354 | 59.5596 | -61.8256 | -61.7523 | -61.6608 | -0.091553 | -62.1872 | 59.5505 | 59.5825 | -61.5875 | -61.8347 | -0.013733 | 0.05951 | -0.16937 | 121.582 | -0.1236 | -0.18311 | 0.11902 | 0.22431 | -0.022888 | -0.17853 | 0.15106 | -0.37537 | -0.35248 | -0.14648 | 121.3715 | 121.6599 | 61.7386 | -121.4813 | 121.3623 | 121.3943 | 61.7203 | -121.5637
319.7812 | 121.7056 | -61.702 | 59.8572 | -0.12329 | 0.0086005 | 0.063375 | 0.063499 | 0.12824 | -0.0062249 | -0.0039797 | -0.069428 | -0.0079254 | 0.05701 | 0.065283 | 0.0020572 | -0.0070689 | 60.0266 | 60.0449 | 0.25635 | -61.7386 | 59.5917 | -61.6791 | -61.5967 | -61.4365 | 0.27008 | -61.9263 | 59.642 | 59.6695 | -61.4456 | -61.6699 | 0.022888 | 0.10529 | -0.2655 | 121.7468 | -0.036621 | -0.14191 | 0.16937 | 0.25635 | 0.032043 | -0.21515 | 0.2655 | -0.22431 | -0.25635 | -0.18768 | 121.2936 | 121.7285 | 61.9583 | -121.4539 | 121.344 | 121.3715 | 61.972 | -121.5271
321.5156 | 121.7697 | -61.7065 | 59.7565 | 0.075073 | 0.0036871 | 0.06423 | 0.061363 | 0.12674 | -0.0047297 | -0.0061161 | 0.13657 | -0.01113 | 0.056796 | 0.06571 | 0.0022708 | -0.0049325 | 59.9487 | 59.9396 | 0.068665 | -61.821 | 59.5367 | -61.7157 | -61.6333 | -61.496 | 0.054932 | -62.0224 | 59.5688 | 59.5871 | -61.496 | -61.7477 | -0.009155 | 0.073242 | -0.21973 | 121.6461 | -0.11444 | -0.18768 | 0.19226 | 0.21057 | -0.041199 | -0.18768 | 0.21057 | -0.31586 | -0.27466 | -0.16937 | 121.2433 | 121.6553 | 61.7752 | -121.3898 | 121.2753 | 121.2936 | 61.7615 | -121.5042
323.2656 | 121.701 | -61.6882 | 59.8297 | -0.13092 | 0.0077459 | 0.06423 | 0.065636 | 0.12888 | -0.0038751 | -0.0050479 | -0.1152 | -0.010062 | 0.05701 | 0.068274 | 0.0020572 | -0.0066415 | 60.0586 | 60.0311 | 0.24261 | -61.7386 | 59.6283 | -61.6653 | -61.5967 | -61.4227 | 0.2655 | -61.9354 | 59.642 | 59.6786 | -61.4365 | -61.647 | 0.022888 | 0.091552 | -0.20142 | 121.7194 | -0.050354 | -0.14191 | 0.22888 | 0.25177 | 0.041198 | -0.18768 | 0.2655 | -0.24719 | -0.28839 | -0.15106 | 121.3165 | 121.7468 | 61.9308 | -121.4264 | 121.3303 | 121.3669 | 61.9537 | -121.4767
325.0156 | 121.7056 | -61.7935 | 59.729 | -0.062256 | 0.0068915 | 0.061453 | 0.063286 | 0.12503 | 0.0031745 | -0.0054751 | -0.046539 | -0.0074982 | 0.056155 | 0.067633 | 0.0046206 | -0.0070689 | 59.9533 | 59.8892 | 0.07782 | -61.8576 | 59.5825 | -61.7889 | -61.6974 | -61.5555 | 0.073242 | -62.0911 | 59.5734 | 59.6054 | -61.5326 | -61.7706 | 0.004578 | 0.09613 | -0.14648 | 121.6827 | -0.064087 | -0.16022 | 0.2243 | 0.26093 | 0.022888 | -0.15564 | 0.23804 | -0.29755 | -0.32043 | -0.1236 | 121.376 | 121.7468 | 61.8713 | -121.4264 | 121.3669 | 121.3989 | 61.8668 | -121.4996
326.7656 | 121.8155 | -61.7706 | 59.7153 | 0.17426 | 0.0047553 | 0.063589 | 0.059013 | 0.12546 | -0.0017389 | -0.0029117 | 0.29678 | -0.0089936 | 0.055728 | 0.066779 | 0.0048344 | -0.0057871 | 59.8892 | 59.8846 | -0.027466 | -61.8942 | 59.523 | -61.8118 | -61.7203 | -61.5143 | -0.009155 | -62.0544 | 59.523 | 59.5047 | -61.5738 | -61.7935 | -0.041199 | 0.050354 | -0.19226 | 121.6553 | -0.1236 | -0.17395 | 0.17395 | 0.19684 | -0.022888 | -0.19226 | 0.25635 | -0.28381 | -0.26093 | -0.21057 | 121.2936 | 121.6599 | 61.7432 | -121.4355 | 121.2936 | 121.2753 | 61.7615 | -121.5088
328.4531 | 121.6736 | -61.821 | 59.6832 | 0.044556 | 0.0075323 | 0.062307 | 0.063072 | 0.12824 | 0.0055243 | -0.0026981 | 0.045013 | -0.0068572 | 0.059146 | 0.069342 | 0.0041934 | -0.0085641 | 59.8618 | 59.8114 | -0.013733 | -61.9263 | 59.5322 | -61.8393 | -61.7386 | -61.6333 | -0.059509 | -62.1918 | 59.5551 | 59.5688 | -61.6013 | -61.8256 | -0.01831 | 0.082398 | -0.15106 | 121.6324 | -0.10529 | -0.18768 | 0.17853 | 0.21973 | -0.004578 | -0.12817 | 0.18768 | -0.37079 | -0.36621 | -0.11444 | 121.3531 | 121.6827 | 61.8073 | -121.4218 | 121.376 | 121.3898 | 61.7615 | -121.5088
330.2188 | 121.6644 | -61.8301 | 59.6878 | 0.052185 | 0.0053961 | 0.062521 | 0.060722 | 0.12589 | -2.988e-05 | -0.0024845 | 0.09079 | -0.0062164 | 0.055942 | 0.067633 | 0.0035526 | -0.0042917 | 59.8297 | 59.8114 | -0.064087 | -61.9354 | 59.5413 | -61.8256 | -61.7294 | -61.647 | -0.064087 | -62.178 | 59.5551 | 59.5642 | -61.615 | -61.8164 | 0.004577 | 0.10071 | -0.14648 | 121.6415 | -0.10529 | -0.20599 | 0.14191 | 0.21515 | 0.013733 | -0.13275 | 0.18311 | -0.3479 | -0.36163 | -0.1236 | 121.3715 | 121.6599 | 61.7661 | -121.4172 | 121.3852 | 121.3943 | 61.7661 | -121.5042
331.9844 | 121.7377 | -61.7569 | 59.7656 | -0.13092 | 0.0077459 | 0.061239 | 0.064354 | 0.12674 | -0.0010981 | -0.0024845 | -0.069428 | -0.010489 | 0.057651 | 0.066992 | 0.0014164 | -0.0066415 | 59.9167 | 59.903 | 0.10529 | -61.8439 | 59.5871 | -61.7569 | -61.6745 | -61.5417 | 0.10986 | -62.0682 | 59.6237 | 59.61 | -61.5234 | -61.7706 | 0 | 0.082397 | -0.17853 | 121.6599 | -0.086975 | -0.16937 | 0.15106 | 0.23346 | -0.013733 | -0.14191 | 0.21515 | -0.31128 | -0.29755 | -0.15564 | 121.344 | 121.6736 | 61.8622 | -121.4401 | 121.3806 | 121.3669 | 61.8668 | -121.5363
333.6719 | 121.6919 | -61.702 | 59.8297 | -0.13855 | 0.0081733 | 0.063589 | 0.066917 | 0.12738 | -0.0057977 | -0.0048343 | -0.069428 | -0.011343 | 0.059573 | 0.066992 | -0.00093361 | -0.0047189 | 60.0082 | 60.0494 | 0.27008 | -61.7432 | 59.5779 | -61.6791 | -61.5967 | -61.4456 | 0.27466 | -61.9492 | 59.642 | 59.6649 | -61.4548 | -61.6562 | 0.022888 | 0.10529 | -0.25177 | 121.7514 | -0.041199 | -0.14648 | 0.17853 | 0.24719 | 0.045776 | -0.18768 | 0.25635 | -0.24719 | -0.29297 | -0.16479 | 121.2799 | 121.7102 | 61.972 | -121.4264 | 121.344 | 121.3669 | 61.9766 | -121.4859
335.4219 | 121.7148 | -61.8027 | 59.729 | 0.082703 | 0.0047553 | 0.062735 | 0.059441 | 0.12674 | -0.00067088 | -0.0031253 | 0.11368 | -0.0094208 | 0.057864 | 0.066992 | 0.0039798 | -0.0057871 | 59.8114 | 59.7656 | -0.09613 | -61.94 | 59.5505 | -61.8484 | -61.7477 | -61.647 | -0.11444 | -62.178 | 59.5596 | 59.5642 | -61.6013 | -61.8439 | -0.045777 | 0.054931 | -0.17853 | 121.5683 | -0.13733 | -0.19226 | 0.082397 | 0.20142 | -0.041199 | -0.16937 | 0.15564 | -0.37537 | -0.33417 | -0.1648 | 121.3531 | 121.6141 | 61.7065 | -121.4767 | 121.3623 | 121.3669 | 61.6882 | -121.5729
337.125 | 121.6782 | -61.8118 | 59.7153 | 0.075073 | 0.0049689 | 0.060385 | 0.060722 | 0.12759 | 0.0012519 | -0.00077552 | 0.11368 | -0.0077118 | 0.05701 | 0.069342 | 0.003339 | -0.0068551 | 59.8251 | 59.761 | -0.091553 | -61.9354 | 59.5459 | -61.8073 | -61.7386 | -61.6745 | -0.10071 | -62.2009 | 59.5276 | 59.5642 | -61.6196 | -61.8393 | 0.004578 | 0.073243 | -0.16937 | 121.5729 | -0.1236 | -0.19684 | 0.10986 | 0.19226 | -0.027465 | -0.18768 | 0.13733 | -0.3891 | -0.36163 | -0.15106 | 121.3577 | 121.637 | 61.7203 | -121.4539 | 121.3394 | 121.376 | 61.7111 | -121.5546
338.8594 | 121.7834 | -61.7111 | 59.7427 | 0.17426 | 0.0036871 | 0.062094 | 0.060936 | 0.12589 | -0.0051569 | -0.0037661 | 0.28152 | -0.012198 | 0.055087 | 0.065924 | 0.00163 | -0.0045053 | 59.9121 | 59.9304 | 0.013733 | -61.8439 | 59.491 | -61.7798 | -61.6837 | -61.5143 | 0.022888 | -62.0224 | 59.5093 | 59.5276 | -61.5417 | -61.7752 | -0.068664 | 0.027466 | -0.25177 | 121.6415 | -0.13275 | -0.16022 | 0.16937 | 0.16937 | -0.064087 | -0.23346 | 0.19684 | -0.31128 | -0.24719 | -0.21515 | 121.2021 | 121.6232 | 61.7249 | -121.4264 | 121.2204 | 121.2387 | 61.734 | -121.5179
340.5938 | 121.7651 | -61.7752 | 59.6832 | 0.13611 | 0.0066779 | 0.06188 | 0.065849 | 0.12845 | 0.00061092 | -0.0037661 | 0.15182 | -0.0085662 | 0.058719 | 0.067419 | 0.0022708 | -0.0066415 | 59.816 | 59.7839 | -0.10529 | -61.9492 | 59.5367 | -61.8439 | -61.7569 | -61.6241 | -0.10529 | -62.1597 | 59.5276 | 59.5642 | -61.5875 | -61.8164 | -0.068664 | 0.018311 | -0.14648 | 121.5591 | -0.17395 | -0.19226 | 0.13275 | 0.18768 | -0.041198 | -0.15564 | 0.15106 | -0.38452 | -0.34332 | -0.11902 | 121.312 | 121.5912 | 61.6699 | -121.4401 | 121.3028 | 121.3394 | 61.6699 | -121.4996
342.3438 | 121.7697 | -61.6928 | 59.7748 | 0.044556 | 0.0066779 | 0.062521 | 0.066063 | 0.12674 | -0.0066523 | -0.0048343 | 0.17471 | -0.0096344 | 0.056796 | 0.067419 | -0.00050621 | -0.0057871 | 59.9396 | 59.9396 | 0.07782 | -61.8256 | 59.5642 | -61.702 | -61.6196 | -61.5005 | 0.073242 | -62.0132 | 59.6054 | 59.6191 | -61.4548 | -61.7065 | -0.009155 | 0.073242 | -0.21057 | 121.6324 | -0.13275 | -0.20599 | 0.16479 | 0.23804 | -0.013733 | -0.16937 | 0.19226 | -0.32043 | -0.3067 | -0.15564 | 121.257 | 121.6324 | 61.7706 | -121.3943 | 121.2982 | 121.312 | 61.7661 | -121.4813
344.0781 | 121.7651 | -61.7157 | 59.761 | 0.13611 | 0.0036871 | 0.063162 | 0.060936 | 0.12759 | -0.0017389 | -0.0048343 | 0.23575 | -0.011771 | 0.055514 | 0.069128 | 0.0024844 | -0.0062143 | 59.9442 | 59.9487 | 0.050354 | -61.8347 | 59.5001 | -61.734 | -61.6562 | -61.4868 | 0.018311 | -62.0178 | 59.5184 | 59.5505 | -61.5143 | -61.7661 | -0.018311 | 0.059509 | -0.26093 | 121.6644 | -0.11902 | -0.17853 | 0.18311 | 0.20142 | -0.050354 | -0.24261 | 0.22888 | -0.30212 | -0.25177 | -0.21057 | 121.2158 | 121.6599 | 61.7661 | -121.4172 | 121.2341 | 121.2662 | 61.734 | -121.5271
345.8281 | 121.8246 | -61.6516 | 59.7794 | -0.0012209 | 0.0068915 | 0.064444 | 0.066063 | 0.12674 | -0.0051569 | -0.0048343 | 0.09079 | -0.010703 | 0.058078 | 0.067633 | -0.0015744 | -0.0062143 | 59.967 | 59.967 | 0.11902 | -61.7844 | 59.5963 | -61.7065 | -61.5875 | -61.441 | 0.15106 | -61.9492 | 59.61 | 59.6466 | -61.4502 | -61.6745 | -0.054932 | 0.064087 | -0.18311 | 121.6187 | -0.13275 | -0.19684 | 0.18768 | 0.20142 | -0.022889 | -0.16937 | 0.21057 | -0.29755 | -0.27466 | -0.13275 | 121.2479 | 121.6187 | 61.7706 | -121.3669 | 121.2616 | 121.2982 | 61.8027 | -121.4539
347.5312 | 121.7377 | -61.7065 | 59.7473 | -0.13092 | 0.0090277 | 0.060598 | 0.063499 | 0.12717 | 0.0010381 | -0.0048343 | -0.13809 | -0.009848 | 0.057437 | 0.066779 | 0.0024844 | -0.0094187 | 59.9579 | 59.8755 | 0.1236 | -61.821 | 59.6558 | -61.7249 | -61.6379 | -61.5417 | 0.1236 | -62.0636 | 59.6466 | 59.6558 | -61.5097 | -61.7203 | -0.018311 | 0.068665 | -0.091552 | 121.582 | -0.11444 | -0.18311 | 0.21057 | 0.19684 | -0.013733 | -0.10071 | 0.1648 | -0.35706 | -0.34332 | -0.091552 | 121.3623 | 121.6644 | 61.8301 | -121.3852 | 121.3531 | 121.3623 | 61.8301 | -121.4676
349.2656 | 121.8109 | -61.6333 | 59.8114 | -0.1004 | 0.0079595 | 0.063162 | 0.064781 | 0.1246 | -0.0053705 | -0.0067569 | 0.029755 | -0.011771 | 0.058719 | 0.066779 | 0.00034819 | -0.0060007 | 60.0723 | 60.0632 | 0.23804 | -61.7203 | 59.61 | -61.6837 | -61.5646 | -61.3815 | 0.25635 | -61.8805 | 59.6191 | 59.6512 | -61.4227 | -61.6287 | -0.050354 | 0.068665 | -0.20142 | 121.6965 | -0.086975 | -0.15564 | 0.26093 | 0.21057 | 0.004578 | -0.19226 | 0.25177 | -0.24719 | -0.25177 | -0.16022 | 121.2433 | 121.7056 | 61.8713 | -121.376 | 121.2524 | 121.2845 | 61.8896 | -121.4401
351.0156 | 121.7377 | -61.7615 | 59.761 | -0.11566 | 0.0064643 | 0.062735 | 0.062645 | 0.12717 | 0.0031745 | -0.0046207 | -0.077057 | -0.00878 | 0.056796 | 0.068274 | 0.0035526 | -0.0081369 | 59.9487 | 59.8984 | 0.09613 | -61.8347 | 59.5917 | -61.7706 | -61.6928 | -61.5234 | 0.082397 | -62.0819 | 59.5917 | 59.6191 | -61.5463 | -61.7661 | -0.009155 | 0.068665 | -0.16937 | 121.6599 | -0.073242 | -0.14191 | 0.18768 | 0.21515 | -0.004577 | -0.16937 | 0.23804 | -0.32043 | -0.31586 | -0.14191 | 121.3531 | 121.7102 | 61.8576 | -121.4539 | 121.3531 | 121.3806 | 61.8439 | -121.5271
352.7188 | 121.7377 | -61.7981 | 59.6878 | 0.12848 | 0.01031 | 0.062307 | 0.060295 | 0.12866 | 0.0018927 | -0.0029117 | 0.12894 | -0.0079254 | 0.056155 | 0.068915 | 0.004407 | -0.0045053 | 59.8297 | 59.761 | -0.11444 | -61.9537 | 59.5505 | -61.8393 | -61.7569 | -61.6333 | -0.1236 | -62.178 | 59.5551 | 59.5596 | -61.5967 | -61.8484 | -0.041198 | 0.041199 | -0.13733 | 121.5591 | -0.15564 | -0.19684 | 0.14191 | 0.20142 | -0.050354 | -0.13275 | 0.16479 | -0.37994 | -0.32959 | -0.12817 | 121.3486 | 121.6278 | 61.6837 | -121.4447 | 121.3531 | 121.3577 | 61.6745 | -121.5363
354.4688 | 121.6965 | -61.8256 | 59.7107 | 0.097962 | 0.0066779 | 0.063162 | 0.062431 | 0.12695 | 0.0012519 | -0.0024845 | 0.13657 | -0.0066436 | 0.057864 | 0.068701 | 0.002698 | -0.0066415 | 59.8114 | 59.7382 | -0.07782 | -61.9446 | 59.5184 | -61.8118 | -61.7477 | -61.6608 | -0.12817 | -62.2101 | 59.5276 | 59.5551 | -61.5921 | -61.8439 | 0.013733 | 0.07782 | -0.19226 | 121.5637 | -0.11902 | -0.19684 | 0.10071 | 0.23346 | -0.01831 | -0.1831 | 0.16479 | -0.38452 | -0.36621 | -0.15564 | 121.344 | 121.637 | 61.7477 | -121.4584 | 121.3531 | 121.3806 | 61.6974 | -121.5546
356.2188 | 121.8018 | -61.6013 | 59.8068 | -0.16144 | 0.0049689 | 0.063589 | 0.067131 | 0.12717 | -0.0068659 | -0.0067569 | 0.067902 | -0.011343 | 0.057864 | 0.066351 | -0.0032834 | -0.0047189 | 60.0357 | 60.054 | 0.2243 | -61.7203 | 59.6054 | -61.6837 | -61.5784 | -61.3907 | 0.24261 | -61.908 | 59.6054 | 59.642 | -61.441 | -61.6699 | -0.082398 | 0.022888 | -0.20142 | 121.6553 | -0.11902 | -0.14191 | 0.22888 | 0.16022 | -0.068665 | -0.20142 | 0.21057 | -0.3067 | -0.23804 | -0.16479 | 121.2067 | 121.637 | 61.8256 | -121.3852 | 121.2067 | 121.2433 | 61.8439 | -121.4767
357.9062 | 121.7468 | -61.6928 | 59.7473 | 0.10559 | 0.0060369 | 0.063589 | 0.062218 | 0.12695 | -0.0047297 | -0.0048343 | 0.22812 | -0.010062 | 0.054873 | 0.067847 | 0.0031254 | -0.0055735 | 59.9442 | 59.9625 | 0.059509 | -61.8393 | 59.5139 | -61.7386 | -61.6791 | -61.4868 | 0.045776 | -62.0087 | 59.5505 | 59.5596 | -61.5326 | -61.7249 | -0.045776 | 0.013733 | -0.23346 | 121.6553 | -0.14648 | -0.16022 | 0.19684 | 0.16022 | -0.032044 | -0.19684 | 0.20599 | -0.31586 | -0.28381 | -0.18768 | 121.2067 | 121.637 | 61.7523 | -121.4264 | 121.2433 | 121.2524 | 61.7386 | -121.4722
359.6562 | 121.843 | -61.6425 | 59.8114 | 0.0064086 | 0.0058233 | 0.064444 | 0.064781 | 0.12546 | -0.0049433 | -0.0044071 | 0.037384 | -0.009848 | 0.06 | 0.065497 | 0.00013459 | -0.0077097 | 59.9899 | 59.9991 | 0.14648 | -61.7569 | 59.6008 | -61.6928 | -61.6333 | -61.4227 | 0.20142 | -61.9125 | 59.6283 | 59.6054 | -61.441 | -61.6745 | -0.050354 | 0.009155 | -0.21057 | 121.6415 | -0.11444 | -0.1236 | 0.17853 | 0.20142 | -0.032044 | -0.1831 | 0.21973 | -0.27008 | -0.23804 | -0.20599 | 121.2433 | 121.6324 | 61.7889 | -121.4447 | 121.2708 | 121.2479 | 61.8439 | -121.4859
361.3438 | 121.7148 | -61.702 | 59.7977 | -0.19196 | 0.0079595 | 0.063162 | 0.065208 | 0.1261 | -0.00045708 | -0.0048343 | -0.15335 | -0.00878 | 0.057864 | 0.066779 | 0.0012028 | -0.0096323 | 59.9533 | 59.9304 | 0.14648 | -61.8073 | 59.6649 | -61.6974 | -61.6287 | -61.5097 | 0.13275 | -62.0544 | 59.6649 | 59.6878 | -61.5051 | -61.702 | 0.004577 | 0.073242 | -0.13275 | 121.6324 | -0.10529 | -0.17853 | 0.15564 | 0.19684 | 0 | -0.13275 | 0.19226 | -0.35248 | -0.35248 | -0.10986 | 121.3669 | 121.6553 | 61.8484 | -121.4264 | 121.3669 | 121.3898 | 61.8347 | -121.4996
363.0938 | 121.669 | -61.6745 | 59.8526 | -0.19958 | 0.0079595 | 0.060812 | 0.065208 | 0.12824 | -0.0036615 | -0.0059023 | -0.12283 | -0.007071 | 0.057651 | 0.068701 | 0.00056179 | -0.0064279 | 60.0174 | 60.0037 | 0.23804 | -61.7523 | 59.6375 | -61.6699 | -61.6013 | -61.4914 | 0.20599 | -62.0041 | 59.6512 | 59.6924 | -61.4548 | -61.6699 | 0.004578 | 0.073243 | -0.21515 | 121.6782 | -0.077819 | -0.15106 | 0.16479 | 0.21973 | 0.004578 | -0.20142 | 0.18311 | -0.32959 | -0.33417 | -0.16022 | 121.312 | 121.6919 | 61.9125 | -121.4539 | 121.3257 | 121.3669 | 61.8805 | -121.5225
364.7812 | 121.7926 | -61.6699 | 59.7794 | 0.036926 | 0.0049689 | 0.064016 | 0.062431 | 0.12332 | -0.0030207 | -0.0067569 | 0.12894 | -0.0085662 | 0.055301 | 0.066565 | 0.00163 | -0.0064279 | 59.9396 | 59.9579 | 0.082397 | -61.8027 | 59.6008 | -61.7157 | -61.6241 | -61.4731 | 0.091553 | -62.0041 | 59.6008 | 59.6191 | -61.4639 | -61.6974 | -0.045776 | 0.045776 | -0.17853 | 121.6278 | -0.13275 | -0.17853 | 0.16022 | 0.20599 | -0.027466 | -0.17853 | 0.19684 | -0.33417 | -0.3067 | -0.16022 | 121.2708 | 121.6095 | 61.7523 | -121.4035 | 121.2708 | 121.2891 | 61.7615 | -121.4767
366.5156 | 121.8155 | -61.6516 | 59.8114 | 0.044556 | 0.0047553 | 0.06423 | 0.060295 | 0.12695 | -0.0051569 | -0.0044071 | 0.098419 | -0.010275 | 0.05701 | 0.066992 | 0.0024844 | -0.0053599 | 59.9396 | 59.9533 | 0.082397 | -61.8027 | 59.5825 | -61.7157 | -61.6379 | -61.4731 | 0.091553 | -61.9949 | 59.61 | 59.6283 | -61.4914 | -61.702 | -0.064087 | 0.013733 | -0.22888 | 121.6049 | -0.15106 | -0.16479 | 0.12817 | 0.16022 | -0.050354 | -0.20142 | 0.17853 | -0.34332 | -0.29297 | -0.1831 | 121.2341 | 121.5912 | 61.734 | -121.4493 | 121.2616 | 121.2799 | 61.7432 | -121.5134
368.2031 | 121.6736 | -61.6882 | 59.8572 | -0.19196 | 0.0088141 | 0.065939 | 0.064354 | 0.1261 | -0.0013117 | -0.0065433 | -0.10757 | -0.0089936 | 0.056796 | 0.067847 | 0.00098899 | -0.0077097 | 60.0128 | 60.0266 | 0.2243 | -61.7432 | 59.642 | -61.6837 | -61.5829 | -61.4868 | 0.17395 | -62.0132 | 59.6558 | 59.6466 | -61.4685 | -61.6974 | 0.004577 | 0.10529 | -0.21515 | 121.7148 | -0.054932 | -0.16022 | 0.15564 | 0.21973 | -0.009156 | -0.20142 | 0.20142 | -0.32501 | -0.31586 | -0.21057 | 121.3303 | 121.701 | 61.9125 | -121.4401 | 121.344 | 121.3348 | 61.8622 | -121.5546
369.9375 | 121.8063 | -61.6241 | 59.8251 | -0.062256 | 0.0051825 | 0.062521 | 0.063927 | 0.12824 | -0.0040887 | -0.0065433 | -0.0083922 | -0.010062 | 0.055087 | 0.067206 | 0.0024844 | -0.0070689 | 60.0449 | 60.0586 | 0.21973 | -61.734 | 59.6329 | -61.6745 | -61.5692 | -61.3815 | 0.24261 | -61.8988 | 59.6054 | 59.61 | -61.4502 | -61.6745 | -0.050354 | 0.054932 | -0.19226 | 121.6827 | -0.10986 | -0.16479 | 0.21973 | 0.17395 | -0.050354 | -0.21973 | 0.24262 | -0.27466 | -0.2243 | -0.21515 | 121.257 | 121.669 | 61.8439 | -121.3943 | 121.2296 | 121.2341 | 61.8668 | -121.4996
371.6719 | 121.8018 | -61.6241 | 59.8068 | -0.13092 | 0.0034735 | 0.062735 | 0.063927 | 0.12802 | -0.0025935 | -0.0065433 | -0.016022 | -0.011343 | 0.055087 | 0.068487 | -0.0020016 | -0.0066415 | 60.0677 | 60.0723 | 0.23346 | -61.7157 | 59.6283 | -61.6699 | -61.5967 | -61.3724 | 0.26093 | -61.8759 | 59.61 | 59.6329 | -61.4227 | -61.6653 | -0.045776 | 0.027466 | -0.17853 | 121.6965 | -0.091552 | -0.11902 | 0.26093 | 0.20142 | -0.041198 | -0.19684 | 0.25177 | -0.25177 | -0.21057 | -0.17395 | 121.2524 | 121.6919 | 61.8576 | -121.4035 | 121.2341 | 121.257 | 61.8851 | -121.4722
373.3594 | 121.7972 | -61.6287 | 59.816 | -0.062256 | 0.0071051 | 0.063589 | 0.062859 | 0.12589 | -0.0036615 | -0.0067569 | -0.031281 | -0.010062 | 0.05701 | 0.067206 | 0.0020572 | -0.0083505 | 60.0494 | 60.0403 | 0.19226 | -61.7386 | 59.6283 | -61.6653 | -61.5601 | -61.3678 | 0.23804 | -61.9125 | 59.6329 | 59.6237 | -61.4639 | -61.6653 | -0.036621 | 0.068664 | -0.18768 | 121.669 | -0.10986 | -0.17853 | 0.23346 | 0.16479 | -0.036621 | -0.1831 | 0.26093 | -0.28381 | -0.24719 | -0.19226 | 121.257 | 121.6782 | 61.821 | -121.376 | 121.2616 | 121.2524 | 61.8668 | -121.4813
375.1094 | 121.8338 | -61.615 | 59.7977 | -0.031738 | 0.0081733 | 0.063162 | 0.062645 | 0.12546 | -0.0023797 | -0.0054751 | -0.13046 | -0.010489 | 0.057437 | 0.066992 | 0.0012028 | -0.0074961 | 59.9854 | 59.9899 | 0.14648 | -61.7661 | 59.61 | -61.702 | -61.5921 | -61.3907 | 0.18768 | -61.9263 | 59.6283 | 59.6054 | -61.4548 | -61.6882 | -0.086975 | 0.022888 | -0.18768 | 121.6049 | -0.15106 | -0.17395 | 0.18768 | 0.16022 | -0.073242 | -0.16937 | 0.2243 | -0.31128 | -0.23804 | -0.19226 | 121.225 | 121.6003 | 61.7615 | -121.3898 | 121.2433 | 121.2204 | 61.8027 | -121.4859
376.7969 | 121.701 | -61.7111 | 59.8206 | -0.20721 | 0.0077459 | 0.063162 | 0.062859 | 0.12802 | 0.00018372 | -0.0031253 | -0.17624 | -0.0083526 | 0.057864 | 0.067633 | 0.00034819 | -0.0092051 | 59.9625 | 59.9304 | 0.14191 | -61.7981 | 59.642 | -61.7294 | -61.6333 | -61.4868 | 0.16022 | -62.0453 | 59.6786 | 59.6512 | -61.4777 | -61.6882 | -0.01831 | 0.07782 | -0.17853 | 121.6415 | -0.086975 | -0.16479 | 0.14191 | 0.23346 | 0.022889 | -0.14191 | 0.22431 | -0.33417 | -0.35706 | -0.16937 | 121.3531 | 121.6736 | 61.853 | -121.4539 | 121.3898 | 121.3623 | 61.8713 | -121.5088
378.5469 | 121.7697 | -61.7523 | 59.7015 | 0.15137 | 0.0075323 | 0.061026 | 0.059441 | 0.12567 | 0.0027471 | -0.0046207 | 0.09079 | -0.0077118 | 0.057864 | 0.069128 | 0.0052616 | -0.0070689 | 59.8389 | 59.7839 | -0.11902 | -61.9263 | 59.5688 | -61.8256 | -61.7477 | -61.6013 | -0.09613 | -62.1597 | 59.5505 | 59.5505 | -61.5829 | -61.8118 | -0.073243 | 0.004577 | -0.13275 | 121.5363 | -0.17395 | -0.17853 | 0.13733 | 0.16937 | -0.05951 | -0.15106 | 0.15106 | -0.40741 | -0.3479 | -0.15106 | 121.3211 | 121.5912 | 61.6333 | -121.4493 | 121.3028 | 121.3028 | 61.6562 | -121.5134
380.2812 | 121.7606 | -61.6974 | 59.7702 | 0.082703 | 0.0049689 | 0.062948 | 0.060082 | 0.12824 | -0.0025935 | -0.0046207 | 0.13657 | -0.011771 | 0.055728 | 0.066351 | 0.0022708 | -0.0051463 | 59.9442 | 59.9487 | 0.068665 | -61.8393 | 59.5596 | -61.7065 | -61.6425 | -61.4639 | 0.068665 | -62.0224 | 59.5734 | 59.6008 | -61.4777 | -61.6837 | -0.009155 | 0.054932 | -0.21057 | 121.6461 | -0.14191 | -0.19684 | 0.17395 | 0.21973 | 0.013733 | -0.19684 | 0.23346 | -0.32501 | -0.33874 | -0.16937 | 121.257 | 121.6415 | 61.7661 | -121.4127 | 121.2708 | 121.2982 | 61.7661 | -121.4539
382.0156 | 121.7926 | -61.6333 | 59.8297 | -0.039368 | 0.0064643 | 0.062521 | 0.061577 | 0.12567 | -0.0045161 | -0.0059023 | -0.054169 | -0.011343 | 0.056796 | 0.064642 | 0.00034819 | -0.0066415 | 60.0082 | 60.0449 | 0.1831 | -61.7294 | 59.6237 | -61.6653 | -61.6058 | -61.3861 | 0.22888 | -61.908 | 59.61 | 59.61 | -61.4502 | -61.6745 | -0.032043 | 0.027466 | -0.20599 | 121.6782 | -0.09613 | -0.1236 | 0.17853 | 0.18311 | -0.041199 | -0.21973 | 0.24719 | -0.27466 | -0.23346 | -0.21973 | 121.257 | 121.6415 | 61.8164 | -121.4355 | 121.2433 | 121.2433 | 61.8622 | -121.5042
383.7031 | 121.6461 | -61.7889 | 59.729 | -0.016479 | 0.0068915 | 0.06188 | 0.060722 | 0.12674 | 0.0029607 | -0.0035525 | 0.029755 | -0.008139 | 0.055728 | 0.068487 | 0.0041934 | -0.0055735 | 59.8892 | 59.8618 | 0.013733 | -61.8942 | 59.5688 | -61.8027 | -61.7065 | -61.6241 | -0.027466 | -62.1689 | 59.5367 | 59.5276 | -61.6104 | -61.8301 | -0.013733 | 0.082397 | -0.16022 | 121.6507 | -0.10529 | -0.18768 | 0.16022 | 0.17853 | -0.041199 | -0.19226 | 0.16479 | -0.37994 | -0.33874 | -0.20142 | 121.3577 | 121.6782 | 61.8027 | -121.4355 | 121.3257 | 121.3165 | 61.7615 | -121.5591
385.4688 | 121.701 | -61.7065 | 59.8297 | -0.1767 | 0.0071051 | 0.063803 | 0.065849 | 0.12674 | -0.0013117 | -0.0056887 | -0.16861 | -0.0085662 | 0.05701 | 0.068915 | 0.00013459 | -0.0047189 | 59.9487 | 59.9442 | 0.13733 | -61.8118 | 59.6603 | -61.7065 | -61.615 | -61.5234 | 0.16479 | -62.0499 | 59.6649 | 59.6786 | -61.4777 | -61.702 | 0 | 0.091553 | -0.16937 | 121.6507 | -0.10529 | -0.19684 | 0.11902 | 0.22888 | 0.004578 | -0.16479 | 0.18311 | -0.34332 | -0.3479 | -0.15106 | 121.3669 | 121.6553 | 61.8439 | -121.4447 | 121.3715 | 121.3852 | 61.8713 | -121.5317
387.1562 | 121.7651 | -61.6791 | 59.761 | 0.11322 | 0.0081733 | 0.062735 | 0.064995 | 0.12503 | -0.0049433 | -0.0050479 | 0.15945 | -0.008139 | 0.056582 | 0.06507 | -0.00029261 | -0.0055735 | 59.9396 | 59.9579 | 0.059509 | -61.8164 | 59.5596 | -61.7523 | -61.6333 | -61.4914 | 0.059509 | -61.9995 | 59.5779 | 59.5642 | -61.496 | -61.7386 | -0.073242 | 0.045776 | -0.20142 | 121.637 | -0.13733 | -0.1831 | 0.17853 | 0.1831 | -0.059509 | -0.1831 | 0.18768 | -0.32044 | -0.26093 | -0.19684 | 121.2387 | 121.6187 | 61.7386 | -121.3943 | 121.257 | 121.2433 | 61.7386 | -121.4996
388.9062 | 121.6827 | -61.6837 | 59.8206 | -0.18433 | 0.0098821 | 0.062948 | 0.06649 | 0.12909 | -0.00045708 | -0.0052615 | -0.13809 | -0.010489 | 0.058291 | 0.067847 | 0.0012028 | -0.0077097 | 59.9991 | 60.0311 | 0.24719 | -61.7477 | 59.6237 | -61.6791 | -61.5875 | -61.4777 | 0.21515 | -61.9812 | 59.6741 | 59.6512 | -61.4914 | -61.6974 | 0.004578 | 0.096131 | -0.19684 | 121.7148 | -0.064087 | -0.16022 | 0.17853 | 0.19226 | -0.013733 | -0.14648 | 0.20599 | -0.29755 | -0.28381 | -0.16937 | 121.3074 | 121.6827 | 61.9308 | -121.4081 | 121.3577 | 121.3348 | 61.8988 | -121.5179
390.6406 | 121.6507 | -61.7935 | 59.6924 | -0.016479 | 0.0083869 | 0.061026 | 0.060722 | 0.12717 | 0.0036017 | -0.0026981 | 0.022125 | -0.0089936 | 0.057437 | 0.066992 | 0.0063296 | -0.0083505 | 59.8846 | 59.8434 | 0.009155 | -61.8851 | 59.5413 | -61.8118 | -61.7065 | -61.6333 | -0.054932 | -62.1735 | 59.5413 | 59.523 | -61.5921 | -61.8118 | -0.018311 | 0.086975 | -0.15106 | 121.637 | -0.091553 | -0.17853 | 0.19226 | 0.20142 | -0.018311 | -0.15106 | 0.16022 | -0.37994 | -0.36163 | -0.16937 | 121.3348 | 121.6782 | 61.8027 | -121.3989 | 121.3348 | 121.3165 | 61.7386 | -121.5042
392.3281 | 121.7102 | -61.6562 | 59.8297 | -0.14618 | 0.0083869 | 0.065725 | 0.063927 | 0.12653 | -0.0040887 | -0.0039797 | -0.054169 | -0.01113 | 0.056582 | 0.068274 | 0.0014164 | -0.0062143 | 60.0357 | 60.0815 | 0.27008 | -61.7203 | 59.6008 | -61.6653 | -61.5784 | -61.4227 | 0.28839 | -61.9171 | 59.6237 | 59.5825 | -61.4456 | -61.6745 | -0.009155 | 0.07782 | -0.22888 | 121.7377 | -0.064087 | -0.14191 | 0.20599 | 0.21057 | -0.018311 | -0.20599 | 0.23346 | -0.26093 | -0.24261 | -0.24719 | 121.257 | 121.6919 | 61.9263 | -121.4081 | 121.2799 | 121.2387 | 61.9446 | -121.5042
394.0781 | 121.669 | -61.8118 | 59.697 | 0.014038 | 0.012873 | 0.05953 | 0.064568 | 0.12653 | 0.0038153 | -0.0020571 | 0.045013 | -0.007071 | 0.057651 | 0.067419 | 0.0035526 | -0.0068551 | 59.8572 | 59.8022 | -0.022888 | -61.908 | 59.5367 | -61.8164 | -61.7203 | -61.6425 | -0.059509 | -62.178 | 59.5642 | 59.5459 | -61.5829 | -61.8164 | -0.004577 | 0.091553 | -0.16022 | 121.6141 | -0.09613 | -0.18768 | 0.16022 | 0.22888 | -0.004577 | -0.13275 | 0.16937 | -0.36621 | -0.36163 | -0.15106 | 121.3486 | 121.669 | 61.7889 | -121.4172 | 121.376 | 121.3577 | 61.7523 | -121.5134
395.8125 | 121.7468 | -61.7111 | 59.7244 | 0.16663 | 0.0051825 | 0.062094 | 0.062004 | 0.12866 | -0.0032343 | -0.0044071 | 0.22812 | -0.009848 | 0.056155 | 0.068274 | 0.0012028 | -0.0064279 | 59.9213 | 59.935 | 0.027466 | -61.8484 | 59.4772 | -61.7889 | -61.6974 | -61.496 | 0.054932 | -62.0041 | 59.5139 | 59.5001 | -61.5463 | -61.7615 | -0.077819 | 0.013733 | -0.24719 | 121.6461 | -0.13733 | -0.15106 | 0.19684 | 0.16479 | -0.050354 | -0.21057 | 0.21515 | -0.29297 | -0.24261 | -0.2243 | 121.1884 | 121.6324 | 61.7386 | -121.4218 | 121.225 | 121.2112 | 61.7661 | -121.4859
397.5625 | 121.6965 | -61.702 | 59.8022 | -0.16144 | 0.0086005 | 0.063589 | 0.065208 | 0.12653 | -0.0040887 | -0.0037661 | -0.14572 | -0.0085662 | 0.05701 | 0.068274 | 0.00056179 | -0.0036509 | 59.9396 | 59.9258 | 0.15106 | -61.8073 | 59.6466 | -61.6974 | -61.6013 | -61.5143 | 0.16937 | -62.027 | 59.7015 | 59.697 | -61.4639 | -61.7294 | 0.004577 | 0.10071 | -0.15564 | 121.6278 | -0.10529 | -0.20599 | 0.13733 | 0.23804 | -0.027466 | -0.10071 | 0.18768 | -0.32501 | -0.29755 | -0.10529 | 121.3486 | 121.6415 | 61.853 | -121.4035 | 121.4035 | 121.3989 | 61.8713 | -121.5317
399.2656 | 121.8063 | -61.6287 | 59.7885 | -0.085144 | 0.0071051 | 0.06423 | 0.066917 | 0.12695 | -0.0062249 | -0.0039797 | 0.014496 | -0.011984 | 0.056155 | 0.068487 | -0.0013608 | -0.0051463 | 60.0403 | 60.0769 | 0.22888 | -61.7294 | 59.5917 | -61.6425 | -61.5601 | -61.3678 | 0.27924 | -61.8759 | 59.6054 | 59.6283 | -61.4044 | -61.6699 | -0.013733 | 0.068664 | -0.19684 | 121.7056 | -0.10071 | -0.16937 | 0.25177 | 0.2243 | -0.041199 | -0.18311 | 0.26093 | -0.24719 | -0.20599 | -0.16022 | 121.2204 | 121.669 | 61.8576 | -121.3486 | 121.2341 | 121.257 | 61.908 | -121.4584
401.0156 | 121.7422 | -61.7569 | 59.697 | 0.12085 | 0.0079595 | 0.062521 | 0.059013 | 0.12589 | 0.0027471 | -0.0033389 | 0.11368 | -0.0072846 | 0.055301 | 0.069342 | 0.0048344 | -0.0074961 | 59.8251 | 59.7794 | -0.1236 | -61.9354 | 59.5184 | -61.8301 | -61.7111 | -61.6241 | -0.10986 | -62.1552 | 59.5642 | 59.5596 | -61.6058 | -61.8256 | -0.073242 | 0.045776 | -0.17853 | 121.5363 | -0.17853 | -0.2243 | 0.12817 | 0.15106 | -0.068665 | -0.13275 | 0.13275 | -0.39825 | -0.32959 | -0.13733 | 121.2753 | 121.582 | 61.6333 | -121.4081 | 121.3211 | 121.3165 | 61.647 | -121.5225
402.6875 | 121.6965 | -61.8073 | 59.7244 | 0.10559 | 0.011164 | 0.061026 | 0.063499 | 0.1246 | 0.00018372 | -0.0029117 | 0.1442 | -0.007071 | 0.057864 | 0.069556 | 0.0037662 | -0.0072825 | 59.7931 | 59.7656 | -0.086975 | -61.9308 | 59.5459 | -61.8073 | -61.7615 | -61.6241 | -0.1236 | -62.1872 | 59.5093 | 59.5505 | -61.6013 | -61.8393 | 0 | 0.045776 | -0.17853 | 121.5729 | -0.1236 | -0.16937 | 0.068665 | 0.20599 | -0.032043 | -0.21515 | 0.1831 | -0.37994 | -0.3479 | -0.17395 | 121.3531 | 121.6003 | 61.7203 | -121.4859 | 121.3165 | 121.3577 | 61.6837 | -121.5637
404.4375 | 121.7972 | -61.7523 | 59.6603 | 0.18951 | 0.0083869 | 0.061239 | 0.062004 | 0.12439 | -0.0010981 | -0.0035525 | 0.1976 | -0.0072846 | 0.056796 | 0.069556 | 0.003339 | -0.0055735 | 59.8572 | 59.848 | -0.073242 | -61.9034 | 59.5184 | -61.8073 | -61.7203 | -61.5372 | -0.009155 | -62.0865 | 59.5047 | 59.5276 | -61.5875 | -61.7935 | -0.054932 | 0.032043 | -0.14191 | 121.6003 | -0.15106 | -0.18311 | 0.19684 | 0.16479 | -0.041199 | -0.15564 | 0.21515 | -0.33417 | -0.29297 | -0.13275 | 121.2708 | 121.6095 | 61.6791 | -121.3806 | 121.257 | 121.2799 | 61.7432 | -121.4539
406.1875 | 121.8018 | -61.7386 | 59.7153 | 0.052185 | 0.0075323 | 0.061026 | 0.063499 | 0.12503 | -0.0017389 | -0.0029117 | 0.22049 | -0.0092072 | 0.056582 | 0.067633 | 0.0029116 | -0.0055735 | 59.9258 | 59.9075 | 0.013733 | -61.8439 | 59.5184 | -61.7935 | -61.6974 | -61.5005 | 0.009155 | -62.0453 | 59.4955 | 59.5139 | -61.5372 | -61.7798 | -0.054932 | 0.041198 | -0.19684 | 121.6461 | -0.10529 | -0.14648 | 0.21057 | 0.20142 | -0.041199 | -0.21973 | 0.23804 | -0.3067 | -0.2655 | -0.20142 | 121.257 | 121.6644 | 61.7523 | -121.4127 | 121.2341 | 121.2524 | 61.7477 | -121.4951
407.8906 | 121.6599 | -61.8118 | 59.7427 | -0.031738 | 0.0039007 | 0.062521 | 0.061363 | 0.12845 | 0.0012519 | -0.0044071 | 0.022125 | -0.0085662 | 0.055087 | 0.070196 | 0.0031254 | -0.0057871 | 59.9121 | 59.8846 | 0.050354 | -61.8713 | 59.5413 | -61.7661 | -61.6928 | -61.5875 | -0.009155 | -62.1277 | 59.5505 | 59.5734 | -61.5738 | -61.7935 | 0.045777 | 0.11902 | -0.20142 | 121.6965 | -0.059509 | -0.17853 | 0.16937 | 0.23804 | 0.018311 | -0.19226 | 0.22431 | -0.31586 | -0.33417 | -0.16937 | 121.3531 | 121.7239 | 61.8622 | -121.4355 | 121.3623 | 121.3852 | 61.8027 | -121.5363
409.625 | 121.6553 | -61.8027 | 59.7107 | -0.0012209 | 0.010523 | 0.062307 | 0.063713 | 0.12994 | 0.0036017 | -0.0014163 | 0.16708 | -0.0094208 | 0.058932 | 0.069769 | 0.0020572 | -0.0051463 | 59.8846 | 59.8389 | 0.027466 | -61.8713 | 59.5459 | -61.7706 | -61.7111 | -61.6333 | -0.036621 | -62.1506 | 59.5413 | 59.5642 | -61.5829 | -61.8256 | 0.032043 | 0.091552 | -0.16479 | 121.6415 | -0.068665 | -0.16022 | 0.17395 | 0.21973 | -0.022889 | -0.16937 | 0.16937 | -0.3479 | -0.32501 | -0.14648 | 121.3486 | 121.6873 | 61.8301 | -121.4218 | 121.344 | 121.3669 | 61.7661 | -121.5363
411.3125 | 121.8201 | -61.6379 | 59.8251 | -0.024109 | 0.0073187 | 0.062735 | 0.066704 | 0.12631 | -0.0083613 | -0.0048343 | 0.09079 | -0.012839 | 0.057651 | 0.069342 | -0.0020016 | -0.0057871 | 59.9579 | 59.9854 | 0.15564 | -61.7569 | 59.5917 | -61.6745 | -61.5921 | -61.409 | 0.20599 | -61.8988 | 59.6054 | 59.6237 | -61.4639 | -61.6791 | -0.036622 | 0.045776 | -0.23346 | 121.6232 | -0.11902 | -0.1648 | 0.13275 | 0.17395 | -0.041199 | -0.21973 | 0.22888 | -0.26093 | -0.21973 | -0.20142 | 121.2296 | 121.5958 | 61.7935 | -121.4172 | 121.2433 | 121.2616 | 61.8439 | -121.5042
413.0625 | 121.7972 | -61.7294 | 59.7107 | 0.22003 | 0.0058233 | 0.061026 | 0.060936 | 0.12866 | -0.0025935 | -0.0041933 | 0.21286 | -0.009848 | 0.055301 | 0.071265 | 0.0035526 | -0.0062143 | 59.9258 | 59.903 | 0.013733 | -61.8347 | 59.5139 | -61.7889 | -61.6974 | -61.5234 | 0.004578 | -62.0499 | 59.5001 | 59.5322 | -61.5463 | -61.7706 | -0.059509 | 0.032043 | -0.19684 | 121.6324 | -0.10529 | -0.13733 | 0.21515 | 0.1831 | -0.041199 | -0.21057 | 0.20599 | -0.32044 | -0.27924 | -0.17853 | 121.2433 | 121.6553 | 61.7432 | -121.4081 | 121.2296 | 121.2616 | 61.734 | -121.4813
414.8125 | 121.6827 | -61.8347 | 59.7198 | 0.097962 | 0.0092413 | 0.061453 | 0.061363 | 0.12695 | 0.00039732 | -0.0046207 | 0.09079 | -0.00643 | 0.057223 | 0.069556 | 0.0056888 | -0.0077097 | 59.8343 | 59.7748 | -0.059509 | -61.9171 | 59.5459 | -61.8118 | -61.7523 | -61.6516 | -0.07782 | -62.1872 | 59.5779 | 59.5779 | -61.5921 | -61.8027 | 0.022888 | 0.082398 | -0.17395 | 121.6095 | -0.082397 | -0.16479 | 0.11444 | 0.24262 | 0.032044 | -0.14191 | 0.18311 | -0.35248 | -0.38452 | -0.14191 | 121.3806 | 121.669 | 61.7752 | -121.4722 | 121.4127 | 121.4127 | 61.7569 | -121.5225
416.5469 | 121.7468 | -61.6653 | 59.7702 | 0.12085 | 0.0039007 | 0.061026 | 0.063713 | 0.12439 | -0.0051569 | -0.0052615 | 0.22812 | -0.010275 | 0.056796 | 0.067206 | 0.0022708 | -0.0047189 | 59.9213 | 59.9487 | 0.050354 | -61.8301 | 59.5322 | -61.7294 | -61.6425 | -61.496 | 0.050354 | -62.0041 | 59.5871 | 59.5825 | -61.5005 | -61.7249 | -0.064087 | 0.022888 | -0.23804 | 121.6141 | -0.1648 | -0.18768 | 0.15106 | 0.16479 | -0.05951 | -0.18311 | 0.16937 | -0.33875 | -0.27923 | -0.18768 | 121.1975 | 121.5866 | 61.7157 | -121.4127 | 121.2524 | 121.2479 | 61.7157 | -121.4951
418.2344 | 121.8201 | -61.615 | 59.8206 | -0.1004 | 0.0060369 | 0.06188 | 0.066917 | 0.1261 | -0.0060113 | -0.0059023 | 0.0068663 | -0.011771 | 0.057223 | 0.067206 | -0.00071981 | -0.0051463 | 60.0449 | 60.0586 | 0.23346 | -61.7249 | 59.6146 | -61.6837 | -61.5829 | -61.3907 | 0.28381 | -61.8805 | 59.6191 | 59.6375 | -61.4319 | -61.6699 | -0.068665 | 0.032043 | -0.20599 | 121.6736 | -0.10986 | -0.14191 | 0.2243 | 0.1831 | -0.054932 | -0.20142 | 0.2243 | -0.2655 | -0.21057 | -0.18311 | 121.2296 | 121.6599 | 61.8484 | -121.4035 | 121.2341 | 121.2524 | 61.8988 | -121.4905
419.9844 | 121.7102 | -61.7249 | 59.7473 | -0.12329 | 0.0064643 | 0.060385 | 0.065636 | 0.12802 | 0.0016791 | -0.0050479 | -0.16098 | -0.009848 | 0.056369 | 0.068701 | 0.002698 | -0.0096323 | 59.9396 | 59.8755 | 0.10986 | -61.8118 | 59.6329 | -61.734 | -61.6333 | -61.5555 | 0.11444 | -62.0544 | 59.6512 | 59.6375 | -61.5051 | -61.734 | -0.009155 | 0.091553 | -0.11444 | 121.6003 | -0.086975 | -0.17853 | 0.19226 | 0.21973 | -0.009155 | -0.09613 | 0.16937 | -0.32959 | -0.32043 | -0.10986 | 121.3577 | 121.6644 | 61.8347 | -121.3806 | 121.376 | 121.3623 | 61.8393 | -121.4813
421.7344 | 121.6553 | -61.8256 | 59.7336 | -0.016479 | 0.0083869 | 0.062307 | 0.060936 | 0.12546 | 0.0027471 | -0.00098912 | 0.037384 | -0.0094208 | 0.055514 | 0.069342 | 0.0056888 | -0.0062143 | 59.9075 | 59.848 | 0.041199 | -61.8759 | 59.5551 | -61.7889 | -61.7157 | -61.6104 | -0.036621 | -62.1597 | 59.5322 | 59.5505 | -61.5738 | -61.8164 | 0.036622 | 0.10986 | -0.17853 | 121.6736 | -0.050354 | -0.16022 | 0.17395 | 0.25177 | 0.009156 | -0.20142 | 0.21515 | -0.33417 | -0.34332 | -0.18311 | 121.3806 | 121.7331 | 61.8668 | -121.4493 | 121.3577 | 121.376 | 61.7889 | -121.55
423.4375 | 121.6736 | -61.7706 | 59.729 | -0.054626 | 0.0077459 | 0.062735 | 0.063927 | 0.12503 | 0.0025335 | -0.0012027 | -0.00076274 | -0.009848 | 0.056155 | 0.066992 | 0.0018436 | -0.0074961 | 59.903 | 59.8846 | 0.054932 | -61.853 | 59.5642 | -61.7523 | -61.6837 | -61.5784 | 0.027466 | -62.1185 | 59.5642 | 59.5825 | -61.5555 | -61.8164 | 0.018311 | 0.086975 | -0.1648 | 121.6553 | -0.082397 | -0.16937 | 0.17395 | 0.21515 | -0.045776 | -0.1648 | 0.19226 | -0.3479 | -0.30212 | -0.14648 | 121.3348 | 121.6736 | 61.8256 | -121.4127 | 121.3348 | 121.3531 | 61.7981 | -121.5454
425.1875 | 121.8063 | -61.615 | 59.8068 | -0.092773 | 0.0049689 | 0.063162 | 0.062004 | 0.1261 | -0.0092157 | -0.0050479 | 0.022125 | -0.010703 | 0.058505 | 0.066992 | 0.00056179 | -0.0045053 | 60.0311 | 60.0494 | 0.21973 | -61.7249 | 59.6283 | -61.6699 | -61.5921 | -61.3861 | 0.24261 | -61.8713 | 59.5963 | 59.6237 | -61.4456 | -61.6608 | -0.054932 | 0.022888 | -0.17853 | 121.6644 | -0.10986 | -0.13275 | 0.2243 | 0.16937 | -0.045777 | -0.21057 | 0.22888 | -0.25635 | -0.21057 | -0.18311 | 121.2433 | 121.6461 | 61.8347 | -121.3989 | 121.2112 | 121.2387 | 61.8576 | -121.4676
426.9219 | 121.7285 | -61.7477 | 59.729 | -0.16144 | 0.0092413 | 0.060385 | 0.06115 | 0.12888 | 0.0021063 | -0.0041933 | -0.092316 | -0.0068572 | 0.058932 | 0.069983 | 0.00056179 | -0.0098459 | 59.935 | 59.8846 | 0.10986 | -61.821 | 59.6329 | -61.7569 | -61.6745 | -61.5509 | 0.091553 | -62.059 | 59.61 | 59.6375 | -61.5372 | -61.7523 | -0.009155 | 0.073242 | -0.09613 | 121.6324 | -0.073242 | -0.14648 | 0.20599 | 0.21057 | -0.004577 | -0.11902 | 0.19684 | -0.31128 | -0.3067 | -0.091553 | 121.3806 | 121.6827 | 61.8576 | -121.4035 | 121.3577 | 121.3852 | 61.8393 | -121.4813
428.6719 | 121.756 | -61.6425 | 59.8251 | -0.15381 | 0.0058233 | 0.062948 | 0.063713 | 0.12439 | -0.0060113 | -0.0044071 | -0.023651 | -0.010703 | 0.057651 | 0.064215 | -7.9008e-05 | -0.0068551 | 60.0494 | 60.0906 | 0.27466 | -61.7203 | 59.6054 | -61.647 | -61.5875 | -61.4136 | 0.29755 | -61.8896 | 59.6237 | 59.6329 | -61.4365 | -61.647 | -0.004578 | 0.054932 | -0.21973 | 121.7331 | -0.07782 | -0.13275 | 0.2243 | 0.20599 | -0.004578 | -0.20142 | 0.22888 | -0.24719 | -0.24261 | -0.19226 | 121.2479 | 121.6919 | 61.9171 | -121.4127 | 121.2662 | 121.2753 | 61.94 | -121.4722
430.4219 | 121.6782 | -61.7706 | 59.7153 | -0.046997 | 0.0079595 | 0.060171 | 0.059868 | 0.12567 | 0.0029607 | -0.0048343 | -0.046539 | -0.009848 | 0.055942 | 0.067847 | 0.0046206 | -0.0087777 | 59.9258 | 59.8892 | 0.068665 | -61.8622 | 59.5505 | -61.7752 | -61.6974 | -61.5555 | 0.068665 | -62.0773 | 59.5642 | 59.5688 | -61.5463 | -61.7615 | -0.004578 | 0.073242 | -0.16479 | 121.6599 | -0.091553 | -0.1648 | 0.21057 | 0.2243 | 0.009155 | -0.15106 | 0.21515 | -0.3067 | -0.31586 | -0.14648 | 121.3211 | 121.6965 | 61.8393 | -121.4127 | 121.3348 | 121.3394 | 61.8393 | -121.4767
432.1094 | 121.8246 | -61.6013 | 59.7885 | -0.024109 | 0.0090277 | 0.065939 | 0.062645 | 0.12674 | -0.0055841 | -0.0056887 | 0.029755 | -0.01113 | 0.056369 | 0.067633 | -0.00093361 | -0.0051463 | 59.9945 | 60.0266 | 0.17395 | -61.7386 | 59.6191 | -61.6837 | -61.5829 | -61.3953 | 0.22888 | -61.8988 | 59.6237 | 59.6191 | -61.4594 | -61.6653 | -0.082398 | 0.01831 | -0.16937 | 121.6278 | -0.13733 | -0.15564 | 0.20599 | 0.14191 | -0.064087 | -0.1648 | 0.20599 | -0.29755 | -0.23346 | -0.16937 | 121.2204 | 121.5958 | 61.7752 | -121.3715 | 121.225 | 121.2204 | 61.8301 | -121.4539
433.8594 | 121.6873 | -61.7935 | 59.729 | -0.062256 | 0.0090277 | 0.062521 | 0.064354 | 0.12546 | 0.0042425 | -0.0031253 | -0.031281 | -0.0079254 | 0.057437 | 0.067847 | 0.004407 | -0.0077097 | 59.9304 | 59.8938 | 0.082397 | -61.8484 | 59.5779 | -61.7752 | -61.702 | -61.5509 | 0.068665 | -62.0819 | 59.5917 | 59.6283 | -61.5326 | -61.7798 | 0.01831 | 0.091553 | -0.15106 | 121.6873 | -0.054932 | -0.14648 | 0.20142 | 0.26093 | 0.013733 | -0.13733 | 0.24262 | -0.28839 | -0.30212 | -0.10071 | 121.3715 | 121.7239 | 61.8759 | -121.431 | 121.3852 | 121.4218 | 61.8622 | -121.5088
435.6094 | 121.7102 | -61.6837 | 59.8251 | -0.19196 | 0.0075323 | 0.06423 | 0.065208 | 0.12631 | -0.0038751 | -0.0048343 | -0.023651 | -0.010916 | 0.05701 | 0.068274 | -0.0015744 | -0.0062143 | 60.0174 | 60.0449 | 0.2655 | -61.7294 | 59.5963 | -61.6745 | -61.5738 | -61.4136 | 0.2655 | -61.9171 | 59.6146 | 59.6466 | -61.4365 | -61.6425 | 0.009155 | 0.10986 | -0.22888 | 121.7285 | -0.045776 | -0.15564 | 0.19226 | 0.24719 | 0.041199 | -0.21057 | 0.27008 | -0.23346 | -0.27466 | -0.17853 | 121.2799 | 121.7011 | 61.9492 | -121.3989 | 121.2982 | 121.3303 | 61.9492 | -121.4676
437.2969 | 121.788 | -61.6745 | 59.8068 | -0.054626 | 0.0068915 | 0.065725 | 0.062645 | 0.12567 | -0.0055841 | -0.0056887 | 0.0068663 | -0.01113 | 0.055514 | 0.066779 | 0.00013459 | -0.0060007 | 60.0403 | 60.0586 | 0.24719 | -61.7203 | 59.6054 | -61.6745 | -61.5738 | -61.3632 | 0.2655 | -61.8576 | 59.6054 | 59.6375 | -61.4502 | -61.6699 | 0 | 0.10071 | -0.20142 | 121.7331 | -0.045776 | -0.14648 | 0.23346 | 0.22431 | 0.004578 | -0.20142 | 0.31128 | -0.1831 | -0.18768 | -0.16937 | 121.2799 | 121.7148 | 61.9217 | -121.3806 | 121.2799 | 121.312 | 61.94 | -121.4767
439.0469 | 121.6873 | -61.8164 | 59.7015 | 0.067444 | 0.0064643 | 0.060598 | 0.061577 | 0.12653 | 0.0018927 | -0.0046207 | 0.052643 | -0.0077118 | 0.056796 | 0.068915 | 0.0052616 | -0.0074961 | 59.8251 | 59.7702 | -0.050354 | -61.9125 | 59.5413 | -61.8027 | -61.7157 | -61.6608 | -0.11444 | -62.2055 | 59.5734 | 59.5367 | -61.6013 | -61.8393 | 0.013733 | 0.10071 | -0.16022 | 121.5866 | -0.096131 | -0.19684 | 0.1236 | 0.21515 | -0.022888 | -0.12817 | 0.15564 | -0.3891 | -0.36621 | -0.16479 | 121.3577 | 121.6415 | 61.7661 | -121.4172 | 121.3898 | 121.3531 | 61.702 | -121.5408
440.7812 | 121.7606 | -61.6974 | 59.7473 | 0.14374 | 0.0053961 | 0.060812 | 0.06179 | 0.12802 | -0.0040887 | -0.0048343 | 0.1976 | -0.010062 | 0.055942 | 0.065924 | 0.0041934 | -0.0066415 | 59.9213 | 59.9487 | 0.041199 | -61.8301 | 59.5093 | -61.7432 | -61.6882 | -61.4914 | 0.041199 | -62.0087 | 59.5322 | 59.5642 | -61.5646 | -61.7569 | -0.045776 | 0.009156 | -0.23804 | 121.6461 | -0.13275 | -0.14191 | 0.17395 | 0.13275 | -0.059509 | -0.21515 | 0.20599 | -0.31128 | -0.25177 | -0.18311 | 121.2067 | 121.6187 | 61.7386 | -121.4355 | 121.2296 | 121.2616 | 61.7386 | -121.5042
442.4688 | 121.7651 | -61.6653 | 59.7656 | 0.059815 | 0.0045417 | 0.064871 | 0.063499 | 0.12802 | -0.0049433 | -0.0039797 | 0.17471 | -0.011343 | 0.054019 | 0.066779 | 0.0014164 | -0.0066415 | 59.935 | 59.9396 | 0.068665 | -61.821 | 59.5825 | -61.7111 | -61.6287 | -61.496 | 0.050354 | -62.0087 | 59.5871 | 59.6054 | -61.5051 | -61.7294 | -0.045777 | 0.036621 | -0.1831 | 121.6049 | -0.15564 | -0.19226 | 0.16937 | 0.16022 | -0.064087 | -0.17853 | 0.16937 | -0.34332 | -0.27924 | -0.16022 | 121.2479 | 121.6003 | 61.734 | -121.3943 | 121.2524 | 121.2708 | 61.7157 | -121.4951
444.2188 | 121.8018 | -61.6745 | 59.7931 | 0.021668 | 0.0053961 | 0.063162 | 0.062431 | 0.12973 | -0.0047297 | -0.0071841 | 0.075531 | -0.012198 | 0.057864 | 0.067206 | 0.00056179 | -0.0066415 | 59.9533 | 59.9579 | 0.11902 | -61.7798 | 59.6237 | -61.7111 | -61.6104 | -61.4548 | 0.15106 | -61.9446 | 59.6008 | 59.6237 | -61.4594 | -61.6653 | -0.036621 | 0.064087 | -0.16937 | 121.6324 | -0.10528 | -0.16937 | 0.16022 | 0.21515 | 0.009156 | -0.19226 | 0.21973 | -0.27008 | -0.27924 | -0.16937 | 121.2982 | 121.6278 | 61.7935 | -121.4035 | 121.2753 | 121.2982 | 61.8256 | -121.4584
445.9062 | 121.7239 | -61.7157 | 59.7794 | -0.16907 | 0.0071051 | 0.065084 | 0.064568 | 0.12653 | -0.00024348 | -0.0041933 | -0.13046 | -0.0092072 | 0.056582 | 0.066779 | -7.9008e-05 | -0.0083505 | 59.9533 | 59.8892 | 0.12817 | -61.8027 | 59.6603 | -61.7157 | -61.6333 | -61.5463 | 0.11444 | -62.0682 | 59.6558 | 59.6695 | -61.5097 | -61.6928 | 0 | 0.082397 | -0.11902 | 121.6049 | -0.086975 | -0.16937 | 0.17395 | 0.20599 | 0.022888 | -0.1236 | 0.16937 | -0.35248 | -0.37537 | -0.10986 | 121.376 | 121.669 | 61.8439 | -121.4127 | 121.3715 | 121.3852 | 61.8301 | -121.4722
447.6406 | 121.701 | -61.6837 | 59.8297 | -0.15381 | 0.0083869 | 0.062735 | 0.063927 | 0.12482 | -0.0021661 | -0.0044071 | -0.054169 | -0.0092072 | 0.055942 | 0.067847 | -0.00029261 | -0.0079233 | 60.0403 | 60.054 | 0.25635 | -61.7294 | 59.6054 | -61.6791 | -61.5921 | -61.4182 | 0.27008 | -61.9171 | 59.6191 | 59.6375 | -61.4365 | -61.6562 | 0.004578 | 0.091553 | -0.2243 | 121.7377 | -0.045776 | -0.13733 | 0.21057 | 0.24719 | 0.027466 | -0.21057 | 0.2655 | -0.23346 | -0.26093 | -0.19226 | 121.2891 | 121.7239 | 61.94 | -121.4218 | 121.3028 | 121.3211 | 61.9537 | -121.4859
449.3281 | 121.8246 | -61.6379 | 59.7931 | -0.0088499 | 0.0068915 | 0.063162 | 0.065422 | 0.1261 | -0.0047297 | -0.0037661 | 0.08316 | -0.012411 | 0.05701 | 0.066565 | 0.00056179 | -0.0072825 | 59.9808 | 59.9854 | 0.14648 | -61.7477 | 59.6008 | -61.6608 | -61.6013 | -61.3998 | 0.21515 | -61.908 | 59.6054 | 59.6283 | -61.4227 | -61.6699 | -0.022889 | 0.036621 | -0.19226 | 121.6232 | -0.10986 | -0.14649 | 0.18768 | 0.21515 | -0.032044 | -0.18768 | 0.23804 | -0.27008 | -0.23804 | -0.16479 | 121.2387 | 121.6187 | 61.7844 | -121.3943 | 121.2433 | 121.2662 | 61.853 | -121.463
451.0781 | 121.7194 | -61.7477 | 59.7519 | -0.11566 | 0.0086005 | 0.060598 | 0.064781 | 0.12845 | 0.0025335 | -0.0037661 | -0.092316 | -0.008139 | 0.057223 | 0.068701 | 0.0048344 | -0.0092051 | 59.9533 | 59.9121 | 0.11902 | -61.8256 | 59.6054 | -61.7523 | -61.6745 | -61.5189 | 0.09613 | -62.059 | 59.5825 | 59.5779 | -61.5326 | -61.7569 | -0.004577 | 0.073242 | -0.14648 | 121.6599 | -0.07782 | -0.15106 | 0.20142 | 0.21515 | -0.009155 | -0.16937 | 0.22888 | -0.31128 | -0.30212 | -0.17395 | 121.3531 | 121.7011 | 61.8668 | -121.4264 | 121.3303 | 121.3257 | 61.8439 | -121.5088
452.8125 | 121.7697 | -61.7203 | 59.7015 | 0.17426 | 0.0064643 | 0.05953 | 0.060509 | 0.12653 | -0.0019525 | -0.0020571 | 0.23575 | -0.010062 | 0.057437 | 0.069556 | 0.0041934 | -0.0060007 | 59.9258 | 59.935 | 0.018311 | -61.8347 | 59.4864 | -61.7661 | -61.7065 | -61.4914 | 0.032043 | -62.0224 | 59.4772 | 59.5047 | -61.5921 | -61.7523 | -0.045776 | 0.013733 | -0.21515 | 121.6553 | -0.11444 | -0.12817 | 0.2243 | 0.12817 | -0.032043 | -0.2243 | 0.22888 | -0.30212 | -0.27008 | -0.19684 | 121.2067 | 121.6461 | 61.7386 | -121.4081 | 121.1975 | 121.225 | 61.7523 | -121.4539
454.5625 | 121.7194 | -61.7523 | 59.7336 | -0.12329 | 0.010096 | 0.061026 | 0.066277 | 0.12524 | 0.0012519 | -0.0031253 | -0.15335 | -0.007071 | 0.055301 | 0.066565 | 0.0031254 | -0.0087777 | 59.9121 | 59.8938 | 0.11902 | -61.8027 | 59.6466 | -61.7249 | -61.6333 | -61.5417 | 0.1236 | -62.059 | 59.6558 | 59.6329 | -61.528 | -61.7477 | 0.027465 | 0.11902 | -0.086976 | 121.6461 | -0.050354 | -0.16937 | 0.17853 | 0.2243 | 0.004577 | -0.07782 | 0.21057 | -0.3067 | -0.31128 | -0.10071 | 121.3989 | 121.6644 | 61.8713 | -121.3669 | 121.4081 | 121.3852 | 61.8759 | -121.4813
456.2344 | 121.7514 | -61.6699 | 59.7748 | 0.090332 | 0.0062505 | 0.064657 | 0.062004 | 0.12524 | -0.0077203 | -0.0056887 | 0.18234 | -0.012198 | 0.054873 | 0.066779 | 0.0018436 | -0.0045053 | 59.935 | 59.9579 | 0.059509 | -61.8118 | 59.5459 | -61.7203 | -61.6379 | -61.4822 | 0.068665 | -62.0087 | 59.5551 | 59.5779 | -61.496 | -61.7386 | -0.050354 | 0.032044 | -0.22888 | 121.6278 | -0.14191 | -0.17395 | 0.16022 | 0.17395 | -0.068664 | -0.21973 | 0.18768 | -0.33875 | -0.27008 | -0.19684 | 121.2158 | 121.6049 | 61.7294 | -121.4127 | 121.225 | 121.2479 | 61.7386 | -121.5134
457.9844 | 121.7148 | -61.7203 | 59.7794 | -0.19196 | 0.0088141 | 0.065298 | 0.067986 | 0.1293 | -0.00024348 | -0.0054751 | -0.16098 | -0.009848 | 0.057651 | 0.067847 | 0.0024844 | -0.0070689 | 59.9487 | 59.9075 | 0.15106 | -61.821 | 59.6649 | -61.7157 | -61.6196 | -61.5463 | 0.14191 | -62.0499 | 59.6603 | 59.6832 | -61.4639 | -61.702 | 0.004578 | 0.10071 | -0.11444 | 121.6278 | -0.10071 | -0.20142 | 0.16937 | 0.25635 | 0.018311 | -0.11902 | 0.17395 | -0.32959 | -0.3479 | -0.09613 | 121.3852 | 121.669 | 61.8713 | -121.3989 | 121.3806 | 121.4035 | 61.8622 | -121.4813
459.75 | 121.7606 | -61.6333 | 59.8297 | -0.13855 | 0.0081733 | 0.061666 | 0.063713 | 0.1261 | -0.0053705 | -0.0065433 | -0.077057 | -0.010062 | 0.056369 | 0.065924 | 0.0012028 | -0.0072825 | 60.0677 | 60.0815 | 0.28839 | -61.7065 | 59.6146 | -61.647 | -61.5509 | -61.3907 | 0.29297 | -61.8942 | 59.6329 | 59.6466 | -61.4136 | -61.6425 | -0.013733 | 0.082398 | -0.21515 | 121.7148 | -0.073242 | -0.15564 | 0.23804 | 0.21973 | -0.009155 | -0.19684 | 0.24262 | -0.26093 | -0.25177 | -0.18311 | 121.2479 | 121.7011 | 61.9217 | -121.3806 | 121.2662 | 121.2799 | 61.9263 | -121.4722
461.4375 | 121.7514 | -61.7157 | 59.7748 | 0.067444 | 0.0051825 | 0.06423 | 0.062431 | 0.12738 | -0.0051569 | -0.0050479 | 0.13657 | -0.011557 | 0.05701 | 0.067419 | 0.002698 | -0.0053599 | 59.9396 | 59.9258 | 0.054932 | -61.8256 | 59.5825 | -61.7111 | -61.6196 | -61.5005 | 0.068665 | -62.0087 | 59.5779 | 59.6146 | -61.496 | -61.7111 | 0.004577 | 0.09613 | -0.19226 | 121.6415 | -0.10986 | -0.20599 | 0.16479 | 0.21973 | 0.004577 | -0.19684 | 0.21515 | -0.29297 | -0.29755 | -0.16022 | 121.2982 | 121.6553 | 61.7706 | -121.3943 | 121.2936 | 121.3303 | 61.7844 | -121.4859
463.1875 | 121.6644 | -61.7065 | 59.816 | -0.3064 | 0.0077459 | 0.063589 | 0.062218 | 0.12674 | -0.00024348 | -0.0039797 | -0.15335 | -0.0089936 | 0.056369 | 0.065924 | 0.0012028 | -0.0092051 | 59.9533 | 59.9213 | 0.16479 | -61.8073 | 59.6237 | -61.7065 | -61.5967 | -61.5143 | 0.15564 | -62.0224 | 59.6924 | 59.6878 | -61.4685 | -61.6928 | 0 | 0.10986 | -0.19226 | 121.6278 | -0.10071 | -0.21057 | 0.13733 | 0.23804 | 0.013733 | -0.1236 | 0.19226 | -0.31586 | -0.32959 | -0.12817 | 121.3303 | 121.6599 | 61.8713 | -121.4127 | 121.3989 | 121.3943 | 61.8622 | -121.5088
464.9531 | 121.7194 | -61.734 | 59.7656 | -0.1767 | 0.0047553 | 0.063162 | 0.064568 | 0.12653 | 0.0012519 | -0.0061161 | -0.13046 | -0.008139 | 0.05701 | 0.06806 | 0.0039798 | -0.0077097 | 59.9396 | 59.8984 | 0.1236 | -61.8164 | 59.6695 | -61.6974 | -61.615 | -61.5601 | 0.1236 | -62.0636 | 59.6512 | 59.6649 | -61.496 | -61.7386 | 0.036621 | 0.11902 | -0.09613 | 121.6324 | -0.082397 | -0.20142 | 0.17395 | 0.23804 | -0.004577 | -0.11444 | 0.17395 | -0.32959 | -0.32501 | -0.10071 | 121.4035 | 121.6736 | 61.8576 | -121.3806 | 121.3852 | 121.3989 | 61.8576 | -121.5042
466.6406 | 121.8155 | -61.6425 | 59.8022 | 0.029297 | 0.0041143 | 0.062948 | 0.061363 | 0.12589 | -0.0064387 | -0.0050479 | 0.067902 | -0.011557 | 0.056369 | 0.066351 | -7.9008e-05 | -0.0047189 | 59.9258 | 59.9442 | 0.11902 | -61.7935 | 59.5688 | -61.6928 | -61.6333 | -61.4594 | 0.12817 | -61.9583 | 59.5825 | 59.61 | -61.4502 | -61.6882 | -0.050354 | 0.009155 | -0.23346 | 121.5866 | -0.15106 | -0.16022 | 0.1236 | 0.19226 | -0.045776 | -0.21973 | 0.18311 | -0.31586 | -0.27008 | -0.19226 | 121.2112 | 121.5683 | 61.7615 | -121.4355 | 121.225 | 121.2524 | 61.7706 | -121.4905
468.375 | 121.7789 | -61.6196 | 59.816 | -0.1004 | 0.0056097 | 0.06423 | 0.063927 | 0.12674 | -0.0036615 | -0.0067569 | -0.016022 | -0.012839 | 0.056796 | 0.067633 | 0.00013459 | -0.0068551 | 60.0494 | 60.0586 | 0.22888 | -61.7157 | 59.6008 | -61.6562 | -61.5829 | -61.3495 | 0.27466 | -61.8622 | 59.6329 | 59.6237 | -61.4594 | -61.6516 | -0.036621 | 0.036621 | -0.21515 | 121.6782 | -0.09613 | -0.13275 | 0.23346 | 0.16022 | -0.032043 | -0.1831 | 0.27008 | -0.24262 | -0.21057 | -0.19226 | 121.2204 | 121.669 | 61.8484 | -121.3989 | 121.2524 | 121.2433 | 61.8942 | -121.4676
470.125 | 121.701 | -61.8027 | 59.7061 | 0.082703 | 0.0096685 | 0.061026 | 0.062218 | 0.12524 | 0.0021063 | -0.0037661 | 0.12894 | -0.0074982 | 0.056582 | 0.069983 | 0.004407 | -0.0081369 | 59.8114 | 59.7244 | -0.086975 | -61.94 | 59.5551 | -61.8118 | -61.7294 | -61.6333 | -0.1236 | -62.1918 | 59.5642 | 59.5505 | -61.5967 | -61.8301 | -0.009156 | 0.073242 | -0.15106 | 121.5271 | -0.13733 | -0.21057 | 0.10528 | 0.20599 | -0.027466 | -0.14191 | 0.16937 | -0.3891 | -0.36163 | -0.15564 | 121.3577 | 121.6141 | 61.7157 | -121.4355 | 121.3669 | 121.3531 | 61.6791 | -121.5363
471.875 | 121.6919 | -61.7661 | 59.7107 | 0.059815 | 0.0068915 | 0.063375 | 0.063072 | 0.1246 | 0.0023199 | -0.0029117 | 0.098419 | -0.010916 | 0.057437 | 0.068701 | 0.0035526 | -0.0068551 | 59.8297 | 59.761 | -0.073242 | -61.9217 | 59.5551 | -61.8164 | -61.7569 | -61.6379 | -0.10986 | -62.1872 | 59.5413 | 59.5734 | -61.6104 | -61.8073 | -0.050354 | 0.009155 | -0.15564 | 121.5271 | -0.15564 | -0.16479 | 0.11902 | 0.15564 | -0.041199 | -0.16937 | 0.12817 | -0.42114 | -0.37994 | -0.13733 | 121.3211 | 121.5958 | 61.6928 | -121.4676 | 121.3074 | 121.3394 | 61.6562 | -121.5179
473.625 | 121.6919 | -61.7569 | 59.697 | -0.077515 | 0.013514 | 0.060385 | 0.06649 | 0.12631 | 0.0027471 | -0.0018435 | -0.061798 | -0.0079254 | 0.058291 | 0.069342 | 0.00034819 | -0.0068551 | 59.9258 | 59.8938 | 0.082397 | -61.8484 | 59.5779 | -61.7523 | -61.6974 | -61.5189 | 0.086975 | -62.0728 | 59.5688 | 59.5963 | -61.5555 | -61.7523 | 0.004578 | 0.059509 | -0.11902 | 121.6507 | -0.091553 | -0.15106 | 0.22888 | 0.20142 | 0.004578 | -0.12817 | 0.23804 | -0.31586 | -0.32044 | -0.10071 | 121.3348 | 121.6827 | 61.8393 | -121.3943 | 121.3257 | 121.3531 | 61.8439 | -121.4493
475.3125 | 121.7422 | -61.7615 | 59.6832 | 0.12848 | 0.0075323 | 0.061453 | 0.059227 | 0.12717 | -0.0030207 | -0.0020571 | 0.12131 | -0.0089936 | 0.056582 | 0.069769 | 0.0046206 | -0.0049325 | 59.8022 | 59.7565 | -0.11444 | -61.9308 | 59.523 | -61.8393 | -61.734 | -61.6333 | -0.10529 | -62.146 | 59.5688 | 59.5688 | -61.5967 | -61.8118 | -0.077819 | 0.027466 | -0.16022 | 121.5179 | -0.16937 | -0.19684 | 0.11902 | 0.16479 | -0.050354 | -0.11444 | 0.12817 | -0.38452 | -0.33417 | -0.11444 | 121.2845 | 121.5637 | 61.647 | -121.4172 | 121.3303 | 121.3303 | 61.6562 | -121.4951
477.0469 | 121.6553 | -61.821 | 59.6924 | 0.014038 | 0.01095 | 0.064016 | 0.063286 | 0.12845 | 0.00061092 | -0.0020571 | 0.09079 | -0.00878 | 0.057437 | 0.068487 | 0.0035526 | -0.0038645 | 59.8343 | 59.8022 | -0.032043 | -61.9125 | 59.523 | -61.8073 | -61.734 | -61.6562 | -0.07782 | -62.1643 | 59.5551 | 59.5688 | -61.5875 | -61.821 | 0.013733 | 0.086975 | -0.16937 | 121.6232 | -0.091553 | -0.17853 | 0.14191 | 0.23346 | 0 | -0.13733 | 0.1648 | -0.34332 | -0.34332 | -0.1236 | 121.344 | 121.6553 | 61.7889 | -121.4264 | 121.376 | 121.3898 | 61.7432 | -121.5134
478.7969 | 121.7697 | -61.6608 | 59.7794 | 0.067444 | 0.0064643 | 0.065084 | 0.064354 | 0.12589 | -0.0081477 | -0.0048343 | 0.18234 | -0.010489 | 0.055942 | 0.064856 | -0.00071981 | -0.0049325 | 59.9167 | 59.935 | 0.07782 | -61.7935 | 59.5734 | -61.702 | -61.615 | -61.5051 | 0.082397 | -61.9812 | 59.5963 | 59.61 | -61.4868 | -61.6974 | -0.041198 | 0.045777 | -0.20599 | 121.5958 | -0.13275 | -0.17853 | 0.13733 | 0.17395 | -0.036621 | -0.18311 | 0.15564 | -0.32043 | -0.28381 | -0.16937 | 121.2341 | 121.5775 | 61.7386 | -121.3943 | 121.257 | 121.2708 | 61.7432 | -121.4767
480.5469 | 121.6782 | -61.7661 | 59.7107 | -0.024109 | 0.0094549 | 0.061026 | 0.06179 | 0.12546 | 0.00061092 | -0.0026981 | 0.022125 | -0.0089936 | 0.057223 | 0.068915 | 0.0052616 | -0.0087777 | 59.903 | 59.8709 | 0.045776 | -61.853 | 59.5505 | -61.7798 | -61.6928 | -61.6104 | -0.018311 | -62.1323 | 59.5596 | 59.5779 | -61.5738 | -61.8027 | -0.013733 | 0.073242 | -0.16022 | 121.637 | -0.086975 | -0.16022 | 0.19226 | 0.19226 | -0.036621 | -0.15106 | 0.15564 | -0.36621 | -0.32959 | -0.13275 | 121.3165 | 121.669 | 61.8118 | -121.4035 | 121.3257 | 121.344 | 61.7477 | -121.5134
482.2188 | 121.8018 | -61.5784 | 59.7977 | -0.046997 | 0.0071051 | 0.064444 | 0.064995 | 0.12653 | -0.0060113 | -0.0082523 | 0.037384 | -0.011343 | 0.056369 | 0.067419 | 0.00077539 | -0.0057871 | 60.0174 | 60.054 | 0.19684 | -61.7111 | 59.6237 | -61.6333 | -61.5829 | -61.3907 | 0.25177 | -61.8759 | 59.6008 | 59.6237 | -61.4456 | -61.6699 | -0.054932 | -0.004578 | -0.17395 | 121.6324 | -0.13275 | -0.12817 | 0.21973 | 0.13275 | -0.091553 | -0.19684 | 0.18768 | -0.29755 | -0.20599 | -0.17395 | 121.2021 | 121.5958 | 61.7752 | -121.3806 | 121.1792 | 121.2021 | 61.8301 | -121.4676
483.9688 | 121.7514 | -61.7065 | 59.7107 | 0.18188 | 0.0053961 | 0.061239 | 0.060722 | 0.12695 | -0.00045708 | -0.0048343 | 0.24338 | -0.0092072 | 0.055087 | 0.067206 | 0.0022708 | -0.0087777 | 59.9213 | 59.903 | 0.022888 | -61.853 | 59.4635 | -61.7889 | -61.6791 | -61.528 | 0.013733 | -62.0132 | 59.5184 | 59.5139 | -61.5509 | -61.7615 | -0.082397 | 0.027466 | -0.24719 | 121.6095 | -0.14648 | -0.17395 | 0.21057 | 0.15564 | -0.054932 | -0.19226 | 0.17853 | -0.3067 | -0.25177 | -0.19684 | 121.17 | 121.6278 | 61.7294 | -121.3898 | 121.225 | 121.2204 | 61.7203 | -121.4722
485.7188 | 121.701 | -61.734 | 59.7198 | -0.085144 | 0.0068915 | 0.061666 | 0.061577 | 0.12482 | 0.0010381 | -0.0031253 | -0.061798 | -0.0072846 | 0.053592 | 0.067206 | 0.0048344 | -0.0064279 | 59.935 | 59.8984 | 0.082397 | -61.8393 | 59.5734 | -61.7615 | -61.6837 | -61.5555 | 0.073242 | -62.0544 | 59.5963 | 59.5825 | -61.5692 | -61.7661 | -0.027466 | 0.050354 | -0.14649 | 121.6324 | -0.10529 | -0.15564 | 0.21515 | 0.16479 | -0.032043 | -0.1236 | 0.17853 | -0.32043 | -0.28839 | -0.13733 | 121.3074 | 121.669 | 61.8164 | -121.4035 | 121.3303 | 121.3165 | 61.8073 | -121.4859
487.4062 | 121.8063 | -61.5967 | 59.8206 | -0.031738 | 0.0075323 | 0.064871 | 0.06414 | 0.12631 | -0.0070795 | -0.0059023 | 0.09079 | -0.010703 | 0.056796 | 0.063147 | -0.00029261 | -0.0040781 | 60.0174 | 60.0357 | 0.18768 | -61.7157 | 59.6054 | -61.6745 | -61.5784 | -61.409 | 0.21973 | -61.8896 | 59.6329 | 59.6375 | -61.4502 | -61.6608 | -0.07782 | 0.018311 | -0.21515 | 121.6324 | -0.11902 | -0.13733 | 0.19684 | 0.14648 | -0.064087 | -0.18768 | 0.18768 | -0.29297 | -0.22888 | -0.18311 | 121.2021 | 121.6141 | 61.7844 | -121.3989 | 121.2296 | 121.2341 | 61.8164 | -121.4813
489.1562 | 121.7148 | -61.734 | 59.7382 | -0.13092 | 0.0090277 | 0.062307 | 0.062859 | 0.12589 | 0.0023199 | -0.0041933 | -0.12283 | -0.0089936 | 0.055514 | 0.070196 | 0.003339 | -0.0064279 | 59.9304 | 59.8846 | 0.10529 | -61.7981 | 59.6375 | -61.7432 | -61.6699 | -61.5509 | 0.10529 | -62.059 | 59.5825 | 59.61 | -61.5005 | -61.7386 | -0.009155 | 0.064087 | -0.10071 | 121.6187 | -0.064087 | -0.12817 | 0.19226 | 0.23346 | -0.004577 | -0.15564 | 0.18311 | -0.32501 | -0.32044 | -0.12817 | 121.3715 | 121.6644 | 61.8393 | -121.4081 | 121.3165 | 121.344 | 61.8393 | -121.4767
490.9062 | 121.7194 | -61.7294 | 59.7656 | -0.13855 | 0.012232 | 0.061026 | 0.066063 | 0.12674 | 0.0018927 | -0.0039797 | -0.099945 | -0.010062 | 0.056369 | 0.067419 | 0.0031254 | -0.0089915 | 59.9075 | 59.8846 | 0.1236 | -61.8164 | 59.6329 | -61.7432 | -61.6333 | -61.5372 | 0.11902 | -62.0499 | 59.6512 | 59.6649 | -61.5234 | -61.7249 | -0.013733 | 0.09613 | -0.13275 | 121.6141 | -0.086975 | -0.1831 | 0.14191 | 0.20599 | 0.004577 | -0.11444 | 0.19226 | -0.32044 | -0.32501 | -0.10071 | 121.3623 | 121.637 | 61.853 | -121.3989 | 121.3806 | 121.3943 | 61.8484 | -121.4905
492.5938 | 121.7422 | -61.6882 | 59.7519 | 0.12848 | 0.0066779 | 0.065512 | 0.059441 | 0.12717 | -0.0032343 | -0.0044071 | 0.22049 | -0.010489 | 0.05701 | 0.067206 | 0.0018436 | -0.0049325 | 59.9213 | 59.9487 | 0.041199 | -61.8301 | 59.5139 | -61.7432 | -61.6653 | -61.496 | 0.022888 | -62.0041 | 59.5551 | 59.5322 | -61.5326 | -61.7706 | -0.054932 | 0.022888 | -0.23804 | 121.637 | -0.14191 | -0.1648 | 0.16937 | 0.15564 | -0.082398 | -0.19684 | 0.19226 | -0.31586 | -0.23346 | -0.21973 | 121.2021 | 121.6095 | 61.7294 | -121.4172 | 121.2433 | 121.2204 | 61.7111 | -121.5225
494.3438 | 121.6736 | -61.8073 | 59.6924 | 0.090332 | 0.0083869 | 0.061453 | 0.061363 | 0.12418 | 0.0038153 | -0.0020571 | 0.060272 | -0.010062 | 0.058291 | 0.067847 | 0.002698 | -0.0066415 | 59.8206 | 59.7794 | -0.068665 | -61.908 | 59.5505 | -61.8118 | -61.7477 | -61.6379 | -0.11444 | -62.2055 | 59.5505 | 59.5642 | -61.5967 | -61.8256 | -0.004578 | 0.059509 | -0.14191 | 121.5866 | -0.10071 | -0.16022 | 0.12817 | 0.21057 | -0.018311 | -0.14191 | 0.16937 | -0.39825 | -0.37994 | -0.12817 | 121.3577 | 121.6278 | 61.7386 | -121.4401 | 121.3577 | 121.3715 | 61.6928 | -121.5179
496.0938 | 121.7926 | -61.7569 | 59.6649 | 0.16663 | 0.0066779 | 0.061239 | 0.063072 | 0.12396 | -2.988e-05 | -0.0022707 | 0.18997 | -0.011343 | 0.054446 | 0.068274 | 0.0035526 | -0.0034373 | 59.8526 | 59.8572 | -0.045776 | -61.8805 | 59.5276 | -61.7935 | -61.7065 | -61.5417 | -0.027466 | -62.059 | 59.5001 | 59.523 | -61.5692 | -61.7798 | -0.036621 | 0.050354 | -0.13733 | 121.6141 | -0.1236 | -0.17395 | 0.18768 | 0.18768 | -0.022888 | -0.1648 | 0.21515 | -0.30212 | -0.27924 | -0.14191 | 121.2845 | 121.6095 | 61.7111 | -121.3715 | 121.257 | 121.2799 | 61.7294 | -121.4447
497.7812 | 121.7972 | -61.6287 | 59.8022 | -0.046997 | 0.0062505 | 0.06423 | 0.066277 | 0.12375 | -0.0057977 | -0.0052615 | 0.045013 | -0.012411 | 0.055514 | 0.06806 | -0.0015744 | -0.0049325 | 60.0082 | 60.054 | 0.18768 | -61.7294 | 59.6054 | -61.6516 | -61.5829 | -61.409 | 0.2243 | -61.8942 | 59.6008 | 59.6329 | -61.4365 | -61.6745 | -0.022888 | 0.045776 | -0.19684 | 121.6827 | -0.10071 | -0.14648 | 0.20599 | 0.19226 | -0.045777 | -0.20142 | 0.21973 | -0.2655 | -0.21973 | -0.16937 | 121.2341 | 121.637 | 61.8164 | -121.3852 | 121.2296 | 121.2616 | 61.853 | -121.4767
499.5312 | 121.6873 | -61.7935 | 59.7153 | 0.075073 | 0.0079595 | 0.059958 | 0.062859 | 0.12695 | 0.0033881 | -0.0035525 | 0.12894 | -0.00643 | 0.057437 | 0.069769 | 0.0056888 | -0.0070689 | 59.8114 | 59.7015 | -0.11902 | -61.9354 | 59.5322 | -61.8118 | -61.7432 | -61.6516 | -0.12817 | -62.1735 | 59.5505 | 59.5551 | -61.5875 | -61.8301 | -0.018311 | 0.050354 | -0.18311 | 121.4951 | -0.14191 | -0.19226 | 0.09613 | 0.20599 | -0.036621 | -0.16479 | 0.14191 | -0.37994 | -0.34332 | -0.16022 | 121.3257 | 121.6049 | 61.6745 | -121.4584 | 121.344 | 121.3486 | 61.6653 | -121.5454
501.2812 | 121.8246 | -61.6287 | 59.7656 | 0.014038 | 0.0081733 | 0.062948 | 0.066277 | 0.12482 | -0.0068659 | -0.0054751 | 0.10605 | -0.010703 | 0.056582 | 0.068915 | -0.00071981 | -0.0060007 | 59.9396 | 59.9533 | 0.11444 | -61.7935 | 59.5871 | -61.7111 | -61.6058 | -61.4685 | 0.12817 | -61.9629 | 59.5871 | 59.6237 | -61.4731 | -61.6882 | -0.082398 | 0.022888 | -0.17853 | 121.582 | -0.16479 | -0.18768 | 0.17395 | 0.15564 | -0.059509 | -0.17853 | 0.16022 | -0.33417 | -0.27466 | -0.14191 | 121.2158 | 121.5683 | 61.7432 | -121.3715 | 121.2158 | 121.2524 | 61.7569 | -121.4539
503.0312 | 121.7331 | -61.734 | 59.7473 | -0.13092 | 0.0092413 | 0.060812 | 0.063927 | 0.12717 | 0.0018927 | -0.0037661 | -0.10757 | -0.0072846 | 0.05701 | 0.070196 | 0.00098899 | -0.010059 | 59.935 | 59.8846 | 0.11444 | -61.7981 | 59.6375 | -61.7203 | -61.6379 | -61.5509 | 0.10071 | -62.0636 | 59.6146 | 59.6146 | -61.5005 | -61.7615 | 0.013733 | 0.096131 | -0.10986 | 121.6187 | -0.064087 | -0.16022 | 0.18768 | 0.23346 | -0.027466 | -0.13275 | 0.18311 | -0.32959 | -0.30212 | -0.13275 | 121.3715 | 121.669 | 61.8484 | -121.3852 | 121.3486 | 121.3486 | 61.8347 | -121.5088
504.7031 | 121.7239 | -61.7294 | 59.7702 | -0.21484 | 0.0096685 | 0.06188 | 0.064781 | 0.1261 | -0.00088448 | -0.0067569 | -0.1152 | -0.0092072 | 0.06 | 0.068701 | 0.00077539 | -0.0060007 | 59.9442 | 59.8938 | 0.1236 | -61.8073 | 59.6329 | -61.702 | -61.6333 | -61.5372 | 0.11902 | -62.0544 | 59.6603 | 59.6832 | -61.5143 | -61.7294 | 0.027466 | 0.09613 | -0.13733 | 121.6232 | -0.07782 | -0.17395 | 0.17395 | 0.21515 | 0 | -0.10986 | 0.19226 | -0.32501 | -0.32501 | -0.086975 | 121.3623 | 121.6736 | 61.853 | -121.4035 | 121.3898 | 121.4127 | 61.8484 | -121.4996
506.4531 | 121.7926 | -61.6104 | 59.8297 | -0.12329 | 0.0060369 | 0.064657 | 0.063927 | 0.1229 | -0.0077203 | -0.0069705 | 0.037384 | -0.010275 | 0.055942 | 0.067419 | -0.00050621 | -0.0057871 | 60.0174 | 60.0632 | 0.21973 | -61.7294 | 59.6237 | -61.6882 | -61.5738 | -61.3861 | 0.23804 | -61.8713 | 59.6054 | 59.6191 | -61.4594 | -61.6699 | -0.077819 | 0.036621 | -0.20599 | 121.6736 | -0.11902 | -0.15564 | 0.18768 | 0.15106 | -0.059509 | -0.2243 | 0.22431 | -0.26093 | -0.20142 | -0.21057 | 121.2341 | 121.6278 | 61.8301 | -121.4035 | 121.2158 | 121.2296 | 61.8484 | -121.4996
508.1406 | 121.788 | -61.7294 | 59.6649 | 0.10559 | 0.0086005 | 0.059744 | 0.061363 | 0.12781 | 0.0023199 | -0.0061161 | 0.1442 | -0.0089936 | 0.055087 | 0.071051 | 0.0052616 | -0.0077097 | 59.8297 | 59.7794 | -0.091553 | -61.9034 | 59.5551 | -61.8256 | -61.7065 | -61.6058 | -0.11444 | -62.146 | 59.5139 | 59.5688 | -61.5829 | -61.8073 | -0.096131 | 0.022888 | -0.10986 | 121.5088 | -0.17395 | -0.19684 | 0.16479 | 0.14648 | -0.07782 | -0.15106 | 0.1236 | -0.41656 | -0.33874 | -0.09613 | 121.2845 | 121.5591 | 61.6379 | -121.3715 | 121.2433 | 121.2982 | 61.615 | -121.4722
509.8906 | 121.701 | -61.7111 | 59.7794 | -0.19958 | 0.0086005 | 0.063375 | 0.066277 | 0.12973 | -0.0010981 | -0.0061161 | -0.13809 | -0.009848 | 0.057651 | 0.067206 | 0.00163 | -0.0060007 | 59.9304 | 59.9258 | 0.16022 | -61.7935 | 59.6603 | -61.702 | -61.6333 | -61.5372 | 0.14191 | -62.0361 | 59.6741 | 59.6741 | -61.5189 | -61.6882 | 0.009156 | 0.07782 | -0.11902 | 121.637 | -0.082397 | -0.16022 | 0.15106 | 0.19226 | 0.022889 | -0.10529 | 0.17395 | -0.32501 | -0.3479 | -0.10529 | 121.3715 | 121.6415 | 61.8713 | -121.4127 | 121.3852 | 121.3852 | 61.853 | -121.4676
511.5781 | 121.756 | -61.7111 | 59.7519 | 0.059815 | 0.0075323 | 0.062094 | 0.062431 | 0.12589 | -0.0021661 | -0.0039797 | 0.23575 | -0.012198 | 0.055728 | 0.066351 | 0.0031254 | -0.0066415 | 59.8984 | 59.903 | 0.022888 | -61.8301 | 59.4818 | -61.7523 | -61.702 | -61.5097 | 0.027466 | -62.0178 | 59.491 | 59.5322 | -61.5692 | -61.7752 | -0.041198 | 0.009156 | -0.27008 | 121.6141 | -0.11902 | -0.12817 | 0.14648 | 0.14191 | -0.064087 | -0.26093 | 0.20142 | -0.3067 | -0.24261 | -0.21973 | 121.1929 | 121.6095 | 61.734 | -121.4539 | 121.2021 | 121.2433 | 61.7386 | -121.5271
513.3281 | 121.6736 | -61.7111 | 59.8251 | -0.13855 | 0.0071051 | 0.062735 | 0.06414 | 0.12546 | -0.0040887 | -0.0041933 | -0.099945 | -0.01113 | 0.05701 | 0.06806 | -0.00029261 | -0.0079233 | 60.0266 | 60.0357 | 0.23346 | -61.7249 | 59.6054 | -61.6562 | -61.5646 | -61.4319 | 0.25177 | -61.9354 | 59.6512 | 59.6695 | -61.441 | -61.6653 | 0.054932 | 0.14648 | -0.21973 | 121.7468 | -0.013733 | -0.16022 | 0.20142 | 0.27008 | 0.045777 | -0.17395 | 0.27924 | -0.2243 | -0.27008 | -0.15564 | 121.3165 | 121.7377 | 61.9446 | -121.3898 | 121.3623 | 121.3806 | 61.9629 | -121.4905
515.0781 | 121.7834 | -61.734 | 59.6786 | 0.097962 | 0.0079595 | 0.062307 | 0.059227 | 0.12567 | 0.00061092 | -0.0052615 | 0.18997 | -0.0077118 | 0.055514 | 0.070196 | 0.0039798 | -0.0047189 | 59.9213 | 59.9121 | 0.013733 | -61.8301 | 59.5093 | -61.7569 | -61.7157 | -61.5097 | 0.009155 | -62.0316 | 59.4955 | 59.5367 | -61.5326 | -61.7752 | -0.022888 | 0.018311 | -0.16937 | 121.6461 | -0.09613 | -0.11444 | 0.24262 | 0.20142 | -0.041199 | -0.18311 | 0.2243 | -0.29755 | -0.25635 | -0.14191 | 121.2433 | 121.6553 | 61.7477 | -121.3943 | 121.2296 | 121.2708 | 61.7432 | -121.4539
516.7656 | 121.7148 | -61.7065 | 59.7748 | -0.15381 | 0.0092413 | 0.064016 | 0.065636 | 0.12781 | 0.0012519 | -0.0052615 | -0.13809 | -0.0077118 | 0.057651 | 0.06806 | 0.00098899 | -0.0077097 | 59.9396 | 59.8938 | 0.10529 | -61.8073 | 59.6375 | -61.7294 | -61.6425 | -61.5326 | 0.1236 | -62.0544 | 59.6329 | 59.6466 | -61.5005 | -61.7386 | -0.022888 | 0.064087 | -0.13733 | 121.6003 | -0.10071 | -0.16479 | 0.16479 | 0.20599 | -0.032043 | -0.14191 | 0.17395 | -0.3479 | -0.31586 | -0.12817 | 121.344 | 121.6461 | 61.8118 | -121.4172 | 121.3394 | 121.3531 | 61.8301 | -121.5134
518.5 | 121.669 | -61.7752 | 59.7153 | 0.067444 | 0.0068915 | 0.060385 | 0.061363 | 0.12674 | 0.00061092 | -0.0022707 | 0.08316 | -0.008139 | 0.056155 | 0.068915 | 0.0020572 | -0.0072825 | 59.816 | 59.7473 | -0.068665 | -61.9263 | 59.5688 | -61.7935 | -61.734 | -61.6241 | -0.10071 | -62.178 | 59.5551 | 59.5459 | -61.5967 | -61.8164 | -0.01831 | 0.041199 | -0.14648 | 121.5225 | -0.15106 | -0.19226 | 0.10071 | 0.17853 | -0.041198 | -0.16022 | 0.15106 | -0.40283 | -0.36163 | -0.16937 | 121.344 | 121.5912 | 61.7065 | -121.4493 | 121.3303 | 121.3211 | 61.6745 | -121.5317
520.2031 | 121.7926 | -61.6241 | 59.8068 | -0.0088499 | 0.0045417 | 0.062735 | 0.065208 | 0.12695 | -0.0060113 | -0.0039797 | 0.052643 | -0.0096344 | 0.056796 | 0.067633 | 0.00013459 | -0.0038645 | 59.9808 | 60.0082 | 0.15564 | -61.7294 | 59.6146 | -61.6745 | -61.5784 | -61.4182 | 0.22888 | -61.9034 | 59.6054 | 59.6512 | -61.4502 | -61.6791 | -0.050354 | 0.045777 | -0.19226 | 121.6324 | -0.10528 | -0.15106 | 0.17395 | 0.17395 | -0.054931 | -0.20142 | 0.20599 | -0.27923 | -0.2243 | -0.15564 | 121.2387 | 121.6049 | 61.7798 | -121.3852 | 121.2296 | 121.2753 | 61.853 | -121.4859
521.9375 | 121.8063 | -61.6058 | 59.8251 | -0.054626 | 0.0043279 | 0.062735 | 0.062218 | 0.12781 | -0.0064387 | -0.0052615 | 0.022125 | -0.013266 | 0.056796 | 0.065497 | -0.00029261 | -0.0064279 | 60.0037 | 60.022 | 0.16479 | -61.7249 | 59.6146 | -61.6882 | -61.5875 | -61.3953 | 0.21515 | -61.908 | 59.5963 | 59.6237 | -61.4502 | -61.6653 | -0.082397 | 0.018311 | -0.21057 | 121.6278 | -0.11902 | -0.13733 | 0.17853 | 0.15564 | -0.059509 | -0.22888 | 0.21057 | -0.30212 | -0.24262 | -0.20142 | 121.2204 | 121.6095 | 61.7706 | -121.4127 | 121.2021 | 121.2296 | 61.821 | -121.4905
523.6875 | 121.7056 | -61.7157 | 59.7931 | -0.20721 | 0.0066779 | 0.063375 | 0.059654 | 0.12802 | -0.0023797 | -0.0035525 | -0.15335 | -0.0079254 | 0.056369 | 0.067419 | 0.005048 | -0.0070689 | 59.935 | 59.9258 | 0.13275 | -61.7935 | 59.6512 | -61.6882 | -61.6379 | -61.5326 | 0.13733 | -62.0407 | 59.6741 | 59.6924 | -61.4868 | -61.702 | 0.027466 | 0.07782 | -0.14191 | 121.6415 | -0.07782 | -0.15564 | 0.14191 | 0.22888 | 0.013733 | -0.11902 | 0.18311 | -0.32501 | -0.33874 | -0.10071 | 121.3669 | 121.6507 | 61.8484 | -121.431 | 121.3898 | 121.4081 | 61.853 | -121.4951
525.4531 | 121.7834 | -61.734 | 59.6924 | 0.17426 | 0.0068915 | 0.063589 | 0.06179 | 0.12546 | -0.0010981 | -0.0029117 | 0.20523 | -0.009848 | 0.055087 | 0.067206 | 0.002698 | -0.0074961 | 59.9075 | 59.8938 | 0.004578 | -61.8393 | 59.523 | -61.7752 | -61.7111 | -61.5189 | -0.009155 | -62.0316 | 59.5139 | 59.5322 | -61.5555 | -61.7752 | -0.041199 | 0.022888 | -0.16937 | 121.6278 | -0.10529 | -0.12817 | 0.21515 | 0.17853 | -0.041199 | -0.17853 | 0.21515 | -0.29755 | -0.25635 | -0.16022 | 121.257 | 121.6415 | 61.7386 | -121.4035 | 121.2479 | 121.2662 | 61.7249 | -121.4676
527.1406 | 121.7148 | -61.7523 | 59.7748 | -0.14618 | 0.0086005 | 0.062094 | 0.065636 | 0.12973 | -0.00024348 | -0.0050479 | -0.1152 | -0.0096344 | 0.058078 | 0.06806 | -0.00029261 | -0.0072825 | 59.9304 | 59.8709 | 0.11902 | -61.8027 | 59.6375 | -61.7065 | -61.6379 | -61.5646 | 0.13275 | -62.0499 | 59.6329 | 59.6649 | -61.5097 | -61.7477 | 0.045776 | 0.11444 | -0.13733 | 121.6232 | -0.050354 | -0.16479 | 0.15564 | 0.24261 | 0.004577 | -0.14191 | 0.18768 | -0.29755 | -0.30212 | -0.10986 | 121.3898 | 121.6827 | 61.8713 | -121.4127 | 121.3852 | 121.4172 | 61.8851 | -121.5225
528.875 | 121.6782 | -61.6837 | 59.8297 | -0.10803 | 0.0079595 | 0.064657 | 0.066917 | 0.12759 | -0.0036615 | -0.0029117 | -0.069428 | -0.010062 | 0.057223 | 0.069128 | 0.00056179 | -0.0064279 | 60.0311 | 60.0128 | 0.25177 | -61.7249 | 59.6008 | -61.6562 | -61.5829 | -61.441 | 0.27008 | -61.9171 | 59.6375 | 59.6649 | -61.441 | -61.6745 | 0.027466 | 0.10071 | -0.22888 | 121.6965 | -0.041199 | -0.14191 | 0.20142 | 0.24262 | 0.009155 | -0.19226 | 0.24262 | -0.23346 | -0.24261 | -0.16479 | 121.2845 | 121.7148 | 61.9354 | -121.4127 | 121.3211 | 121.3486 | 61.9537 | -121.5042
530.625 | 121.6599 | -61.6608 | 59.8343 | -0.16907 | 0.0090277 | 0.062094 | 0.065422 | 0.12866 | -0.0034479 | -0.0046207 | -0.10757 | -0.010062 | 0.057437 | 0.066779 | 0.0020572 | -0.0068551 | 60.022 | 60.0311 | 0.2243 | -61.7111 | 59.6375 | -61.6562 | -61.5784 | -61.4685 | 0.23804 | -61.9675 | 59.6466 | 59.6558 | -61.4594 | -61.6699 | 0.004578 | 0.082398 | -0.19684 | 121.6919 | -0.050354 | -0.13275 | 0.18768 | 0.20142 | -0.009155 | -0.18768 | 0.19226 | -0.3067 | -0.29755 | -0.17853 | 121.2982 | 121.6827 | 61.8851 | -121.4127 | 121.3074 | 121.3165 | 61.8988 | -121.5042
532.3281 | 121.7056 | -61.7249 | 59.7336 | -0.11566 | 0.0086005 | 0.062735 | 0.058586 | 0.12653 | 0.00039732 | -0.0035525 | -0.077057 | -0.0083526 | 0.054446 | 0.067419 | 0.0041934 | -0.0077097 | 59.9304 | 59.8938 | 0.10529 | -61.8164 | 59.6054 | -61.7386 | -61.6653 | -61.5372 | 0.10986 | -62.0499 | 59.6054 | 59.6191 | -61.5372 | -61.7569 | -0.013732 | 0.05951 | -0.12817 | 121.6187 | -0.091552 | -0.15106 | 0.19684 | 0.18768 | -0.032043 | -0.12817 | 0.18768 | -0.32501 | -0.29297 | -0.11444 | 121.3303 | 121.6553 | 61.8301 | -121.3989 | 121.3303 | 121.344 | 61.8347 | -121.4905
534.0625 | 121.6278 | -61.7798 | 59.7244 | -0.016479 | 0.012873 | 0.05953 | 0.067131 | 0.12759 | 0.0016791 | -0.0044071 | 0.037384 | -0.007071 | 0.058078 | 0.071478 | 0.0020572 | -0.0077097 | 59.9167 | 59.8572 | 0.059509 | -61.8622 | 59.5871 | -61.7798 | -61.7065 | -61.6104 | -0.022888 | -62.1368 | 59.5642 | 59.5779 | -61.5967 | -61.8164 | 0 | 0.073242 | -0.13733 | 121.637 | -0.082398 | -0.15564 | 0.19226 | 0.1831 | -0.036621 | -0.16022 | 0.16937 | -0.35706 | -0.32043 | -0.14648 | 121.3669 | 121.6965 | 61.8393 | -121.431 | 121.344 | 121.3577 | 61.7569 | -121.5408
535.75 | 121.7239 | -61.7294 | 59.7565 | -0.16144 | 0.0098821 | 0.062735 | 0.062218 | 0.12759 | -0.0015253 | -0.0026981 | -0.1152 | -0.009848 | 0.058078 | 0.068274 | 0.00013459 | -0.0081369 | 59.9167 | 59.8892 | 0.11444 | -61.8027 | 59.6466 | -61.7203 | -61.6562 | -61.5463 | 0.1236 | -62.0453 | 59.6375 | 59.6786 | -61.5005 | -61.7203 | 0.009155 | 0.073242 | -0.10986 | 121.6187 | -0.073242 | -0.14648 | 0.16022 | 0.22888 | 0.009155 | -0.11902 | 0.1831 | -0.31586 | -0.32501 | -0.07782 | 121.376 | 121.6461 | 61.8439 | -121.4127 | 121.3669 | 121.4081 | 61.853 | -121.4767
537.5 | 121.756 | -61.6974 | 59.729 | 0.12848 | 0.0060369 | 0.060171 | 0.059868 | 0.12375 | -0.0040887 | -0.0041933 | 0.23575 | -0.0089936 | 0.055728 | 0.069128 | 0.0022708 | -0.0055735 | 59.9167 | 59.9304 | 0.045776 | -61.8301 | 59.5184 | -61.7706 | -61.6699 | -61.4914 | 0.032043 | -61.9858 | 59.5184 | 59.5596 | -61.5326 | -61.7615 | -0.073242 | 0.027466 | -0.21057 | 121.6278 | -0.13275 | -0.16022 | 0.18768 | 0.16479 | -0.064087 | -0.21057 | 0.20599 | -0.28839 | -0.2243 | -0.16937 | 121.2158 | 121.6141 | 61.7432 | -121.3989 | 121.2158 | 121.257 | 61.7294 | -121.4905
539.25 | 121.788 | -61.6379 | 59.8114 | -0.1004 | 0.0068915 | 0.063375 | 0.064568 | 0.12631 | -0.0062249 | -0.0071841 | 0.037384 | -0.010703 | 0.056582 | 0.069769 | -0.00050621 | -0.0057871 | 60.0403 | 60.054 | 0.21973 | -61.7203 | 59.5871 | -61.6562 | -61.5921 | -61.377 | 0.27466 | -61.8576 | 59.642 | 59.6695 | -61.4548 | -61.6745 | -0.018311 | 0.045776 | -0.2243 | 121.6919 | -0.082398 | -0.12817 | 0.22888 | 0.1831 | -0.036622 | -0.16937 | 0.26093 | -0.21973 | -0.1831 | -0.14191 | 121.225 | 121.6782 | 61.8576 | -121.4035 | 121.2799 | 121.3074 | 61.9125 | -121.4859
540.9375 | 121.7743 | -61.615 | 59.7931 | -0.1004 | 0.0083869 | 0.065725 | 0.064354 | 0.12717 | -0.0038751 | -0.0076113 | -0.023651 | -0.010062 | 0.057437 | 0.066779 | -7.9008e-05 | -0.0064279 | 60.0586 | 60.0861 | 0.24261 | -61.6974 | 59.6237 | -61.6653 | -61.5555 | -61.3953 | 0.27924 | -61.8759 | 59.6283 | 59.6695 | -61.4594 | -61.647 | -0.050354 | 0.059509 | -0.16937 | 121.7011 | -0.082398 | -0.14191 | 0.2655 | 0.15564 | -0.032044 | -0.16479 | 0.21973 | -0.26093 | -0.22888 | -0.1236 | 121.2387 | 121.6736 | 61.8576 | -121.3486 | 121.2433 | 121.2845 | 61.8942 | -121.4401
542.6875 | 121.788 | -61.7111 | 59.7198 | 0.14374 | 0.0098821 | 0.06188 | 0.060722 | 0.12717 | -0.00024348 | -0.0037661 | 0.21286 | -0.0092072 | 0.058932 | 0.068274 | 0.0037662 | -0.0074961 | 59.935 | 59.9213 | 0.022888 | -61.8164 | 59.5139 | -61.7752 | -61.6837 | -61.5051 | 0 | -62.0224 | 59.5093 | 59.5367 | -61.5692 | -61.7798 | -0.064087 | 0.027466 | -0.20599 | 121.6324 | -0.10529 | -0.13275 | 0.21515 | 0.14191 | -0.068664 | -0.21057 | 0.20599 | -0.31128 | -0.24262 | -0.18311 | 121.225 | 121.6461 | 61.734 | -121.4035 | 121.2204 | 121.2479 | 61.7111 | -121.4996
544.4531 | 121.7926 | -61.7249 | 59.7244 | 0.2124 | 0.0062505 | 0.062948 | 0.060936 | 0.12695 | -0.00024348 | -0.0024845 | 0.20523 | -0.0092072 | 0.054446 | 0.067847 | 0.0048344 | -0.0083505 | 59.9304 | 59.903 | 0.027466 | -61.8118 | 59.5184 | -61.7615 | -61.6653 | -61.5097 | 0.009155 | -62.027 | 59.5001 | 59.523 | -61.5646 | -61.7844 | -0.036621 | 0.05951 | -0.20599 | 121.6278 | -0.086975 | -0.14649 | 0.20599 | 0.16022 | -0.059509 | -0.2243 | 0.21515 | -0.30212 | -0.24262 | -0.20142 | 121.2433 | 121.6553 | 61.7523 | -121.3898 | 121.225 | 121.2479 | 61.734 | -121.5088
546.1406 | 121.7468 | -61.6791 | 59.761 | 0.12848 | 0.0041143 | 0.060598 | 0.06179 | 0.12759 | -0.0036615 | -0.0029117 | 0.18997 | -0.011771 | 0.055514 | 0.066351 | 0.0031254 | -0.0049325 | 59.9487 | 59.9487 | 0.050354 | -61.8118 | 59.5001 | -61.7523 | -61.6516 | -61.4731 | 0.027466 | -61.9904 | 59.523 | 59.5596 | -61.5417 | -61.7844 | -0.073242 | 0.027466 | -0.26093 | 121.6278 | -0.13275 | -0.16022 | 0.18768 | 0.13733 | -0.10529 | -0.23804 | 0.20599 | -0.31128 | -0.20599 | -0.20142 | 121.1792 | 121.6278 | 61.7294 | -121.4127 | 121.2021 | 121.2387 | 61.7065 | -121.5454
547.875 | 121.701 | -61.7065 | 59.7382 | -0.10803 | 0.0064643 | 0.063375 | 0.061363 | 0.12589 | 0.0014655 | -0.0033389 | -0.10757 | -0.010489 | 0.055301 | 0.068274 | 0.0052616 | -0.0083505 | 59.935 | 59.9075 | 0.10071 | -61.8118 | 59.61 | -61.734 | -61.6379 | -61.5326 | 0.10986 | -62.0499 | 59.6283 | 59.6237 | -61.5417 | -61.7432 | -0.027466 | 0.068665 | -0.12817 | 121.6141 | -0.10529 | -0.17395 | 0.19684 | 0.1648 | -0.036621 | -0.10986 | 0.17395 | -0.34332 | -0.3067 | -0.11444 | 121.3165 | 121.6415 | 61.8073 | -121.376 | 121.3348 | 121.3303 | 61.8164 | -121.4813
549.625 | 121.7697 | -61.7203 | 59.7015 | 0.16663 | 0.011164 | 0.060598 | 0.066704 | 0.12759 | -0.0017389 | -0.0065433 | 0.22812 | -0.011771 | 0.057223 | 0.068274 | 0.00098899 | -0.0068551 | 59.9167 | 59.9213 | 0.027466 | -61.821 | 59.4864 | -61.7706 | -61.6745 | -61.4914 | 0.022888 | -61.9949 | 59.4864 | 59.5367 | -61.5463 | -61.7523 | -0.050354 | 0.045776 | -0.21515 | 121.6415 | -0.10071 | -0.14648 | 0.21515 | 0.17395 | -0.032043 | -0.21515 | 0.22888 | -0.27466 | -0.24262 | -0.16479 | 121.2067 | 121.637 | 61.7477 | -121.376 | 121.2067 | 121.257 | 61.7432 | -121.4539
551.3594 | 121.756 | -61.6745 | 59.7748 | 0.11322 | 0.0060369 | 0.065084 | 0.06179 | 0.12653 | -0.0045161 | -0.0067569 | 0.21286 | -0.010703 | 0.056369 | 0.067847 | 0.0031254 | -0.0064279 | 59.935 | 59.9487 | 0.059509 | -61.8118 | 59.5322 | -61.7065 | -61.6196 | -61.4777 | 0.050354 | -61.972 | 59.5825 | 59.5871 | -61.5005 | -61.7157 | -0.032043 | 0.054932 | -0.24261 | 121.6232 | -0.13733 | -0.19226 | 0.16022 | 0.17395 | -0.041198 | -0.19226 | 0.19684 | -0.29755 | -0.25635 | -0.18768 | 121.2067 | 121.6095 | 61.734 | -121.3943 | 121.257 | 121.2616 | 61.7249 | -121.4905
553.0938 | 121.756 | -61.6745 | 59.7931 | 0.082703 | 0.0062505 | 0.060598 | 0.061577 | 0.12439 | -0.0038751 | -0.0061161 | 0.11368 | -0.012198 | 0.057223 | 0.066779 | 0.0018436 | -0.0066415 | 59.9304 | 59.9442 | 0.059509 | -61.8073 | 59.5917 | -61.6974 | -61.6287 | -61.4822 | 0.054932 | -61.9858 | 59.6008 | 59.6008 | -61.4594 | -61.7065 | -0.022888 | 0.045777 | -0.20142 | 121.6187 | -0.13275 | -0.17853 | 0.13733 | 0.21515 | -0.032043 | -0.19226 | 0.19226 | -0.31128 | -0.27924 | -0.19226 | 121.2662 | 121.6049 | 61.734 | -121.4218 | 121.2753 | 121.2753 | 61.7294 | -121.4996
554.8438 | 121.7422 | -61.6699 | 59.7977 | 0.067444 | 0.0062505 | 0.061026 | 0.064354 | 0.12589 | -0.0036615 | -0.0065433 | 0.1442 | -0.009848 | 0.056796 | 0.067633 | 0.0014164 | -0.0070689 | 59.9487 | 59.9304 | 0.050354 | -61.7889 | 59.5825 | -61.6974 | -61.6241 | -61.4868 | 0.054932 | -61.9858 | 59.5734 | 59.6191 | -61.441 | -61.7111 | -0.027466 | 0.045776 | -0.21515 | 121.6003 | -0.11902 | -0.16479 | 0.15106 | 0.22888 | -0.041199 | -0.2243 | 0.18311 | -0.31586 | -0.27466 | -0.17853 | 121.2524 | 121.6187 | 61.7203 | -121.4218 | 121.2433 | 121.2891 | 61.7249 | -121.5088
556.5312 | 121.701 | -61.7661 | 59.7061 | 0.12848 | 0.0058233 | 0.062735 | 0.062431 | 0.1246 | 0.0033881 | -0.0041933 | 0.10605 | -0.0083526 | 0.05466 | 0.067633 | 0.0035526 | -0.0092051 | 59.8526 | 59.7702 | -0.086975 | -61.9217 | 59.5779 | -61.8164 | -61.7477 | -61.6241 | -0.12817 | -62.1597 | 59.5825 | 59.5917 | -61.5829 | -61.8164 | -0.050354 | 0.01831 | -0.12817 | 121.5363 | -0.15564 | -0.17395 | 0.14648 | 0.18311 | -0.050354 | -0.1236 | 0.14191 | -0.39368 | -0.34332 | -0.11444 | 121.344 | 121.6187 | 61.6791 | -121.4539 | 121.3486 | 121.3577 | 61.6379 | -121.5225
558.2812 | 121.7972 | -61.7249 | 59.7015 | 0.159 | 0.0058233 | 0.063375 | 0.059227 | 0.12567 | 0.00061092 | -0.0033389 | 0.1442 | -0.0096344 | 0.054019 | 0.064642 | 0.0035526 | -0.0079233 | 59.9304 | 59.9075 | 0.009155 | -61.8027 | 59.5184 | -61.7523 | -61.6653 | -61.5189 | 0.009155 | -62.0132 | 59.5367 | 59.5367 | -61.528 | -61.7432 | -0.027465 | 0.05951 | -0.1831 | 121.6324 | -0.077819 | -0.13733 | 0.22888 | 0.19684 | -0.01831 | -0.16479 | 0.20599 | -0.28839 | -0.27008 | -0.16479 | 121.2433 | 121.6553 | 61.734 | -121.3669 | 121.2616 | 121.2616 | 61.734 | -121.4447
560.0312 | 121.701 | -61.7065 | 59.7839 | -0.16907 | 0.01031 | 0.064657 | 0.061577 | 0.12738 | 0.0010381 | -0.0033389 | -0.10757 | -0.008139 | 0.056582 | 0.066779 | 0.002698 | -0.0068551 | 59.9579 | 59.8892 | 0.11444 | -61.7752 | 59.642 | -61.7065 | -61.6425 | -61.528 | 0.14191 | -62.0224 | 59.6741 | 59.6786 | -61.5143 | -61.7065 | 0 | 0.064087 | -0.14191 | 121.5958 | -0.068665 | -0.13275 | 0.17395 | 0.19226 | 0 | -0.10986 | 0.17853 | -0.31586 | -0.31586 | -0.10529 | 121.3486 | 121.6644 | 61.821 | -121.4264 | 121.3806 | 121.3852 | 61.8485 | -121.4905
561.7812 | 121.6736 | -61.7798 | 59.7473 | 0.067444 | 0.0068915 | 0.06188 | 0.060936 | 0.12503 | 0.0023199 | -0.0026981 | 0.098419 | -0.0074982 | 0.056582 | 0.068487 | 0.0035526 | -0.0055735 | 59.8343 | 59.7794 | -0.068665 | -61.8988 | 59.5688 | -61.7889 | -61.7157 | -61.6608 | -0.091553 | -62.1597 | 59.5917 | 59.5779 | -61.5967 | -61.7935 | -0.009155 | 0.064087 | -0.17853 | 121.5591 | -0.11902 | -0.18311 | 0.086976 | 0.1831 | -0.013733 | -0.15564 | 0.11902 | -0.37994 | -0.36621 | -0.16937 | 121.3486 | 121.6141 | 61.7111 | -121.463 | 121.3715 | 121.3577 | 61.6882 | -121.5408
563.4688 | 121.756 | -61.6562 | 59.7931 | 0.052185 | 0.0066779 | 0.063375 | 0.066063 | 0.12332 | -0.0066523 | -0.0044071 | 0.15945 | -0.0096344 | 0.055514 | 0.06806 | -0.00029261 | -0.0074961 | 59.935 | 59.9487 | 0.086975 | -61.7798 | 59.5871 | -61.6791 | -61.5967 | -61.496 | 0.07782 | -61.972 | 59.5963 | 59.6375 | -61.4639 | -61.6882 | -0.022888 | 0.059509 | -0.20599 | 121.6049 | -0.1236 | -0.1831 | 0.14191 | 0.19226 | -0.032043 | -0.19684 | 0.16022 | -0.31586 | -0.28381 | -0.15564 | 121.2433 | 121.5912 | 61.7432 | -121.3898 | 121.2524 | 121.2936 | 61.734 | -121.4813
565.2344 | 121.7926 | -61.5967 | 59.8206 | -0.1004 | 0.0056097 | 0.06423 | 0.065422 | 0.12738 | -0.0062249 | -0.0086795 | -0.0083922 | -0.012411 | 0.055301 | 0.068487 | -0.001788 | -0.0079233 | 60.0723 | 60.0815 | 0.21057 | -61.6837 | 59.642 | -61.6287 | -61.5738 | -61.3449 | 0.27466 | -61.8393 | 59.6466 | 59.7061 | -61.4227 | -61.6241 | -0.032043 | 0.022888 | -0.17853 | 121.6782 | -0.086975 | -0.10986 | 0.25177 | 0.17395 | -0.027466 | -0.17395 | 0.25177 | -0.24261 | -0.21515 | -0.11444 | 121.2387 | 121.669 | 61.8073 | -121.3943 | 121.2433 | 121.3028 | 61.8713 | -121.4447
566.9219 | 121.7194 | -61.6974 | 59.7656 | -0.13855 | 0.01095 | 0.063162 | 0.063713 | 0.12781 | 0.0033881 | -0.0050479 | -0.13809 | -0.00878 | 0.056369 | 0.068274 | 0.0035526 | -0.0092051 | 59.9716 | 59.9121 | 0.10071 | -61.7615 | 59.6786 | -61.6837 | -61.6241 | -61.5189 | 0.11902 | -62.0224 | 59.6466 | 59.6466 | -61.496 | -61.7111 | 0.013733 | 0.073242 | -0.086975 | 121.6095 | -0.064087 | -0.13733 | 0.20599 | 0.20142 | -0.013733 | -0.11902 | 0.17853 | -0.32501 | -0.31128 | -0.11902 | 121.376 | 121.669 | 61.7981 | -121.3898 | 121.344 | 121.344 | 61.8164 | -121.4767
568.6719 | 121.7743 | -61.6928 | 59.7244 | 0.14374 | 0.0071051 | 0.063162 | 0.060936 | 0.12631 | -0.00045708 | -0.0039797 | 0.22812 | -0.010489 | 0.053378 | 0.069128 | 0.0022708 | -0.0062143 | 59.9625 | 59.9442 | 0.027466 | -61.7844 | 59.523 | -61.7386 | -61.6699 | -61.4822 | 0.013733 | -61.9949 | 59.5184 | 59.5551 | -61.5555 | -61.7569 | -0.045776 | 0.022888 | -0.20142 | 121.637 | -0.091553 | -0.11444 | 0.23804 | 0.13733 | -0.064087 | -0.20599 | 0.21057 | -0.30212 | -0.23804 | -0.16937 | 121.2158 | 121.6553 | 61.7203 | -121.3943 | 121.2112 | 121.2479 | 61.7065 | -121.4813
570.4375 | 121.6919 | -61.6745 | 59.8251 | -0.16907 | 0.0056097 | 0.062948 | 0.065849 | 0.12909 | -0.0034479 | -0.0046207 | -0.13809 | -0.0077118 | 0.056155 | 0.067633 | -0.00050621 | -0.0085641 | 59.9716 | 59.9396 | 0.14648 | -61.7706 | 59.6741 | -61.6699 | -61.5829 | -61.496 | 0.14191 | -62.0087 | 59.7061 | 59.7427 | -61.4365 | -61.6562 | 0.004578 | 0.091553 | -0.15106 | 121.6141 | -0.09613 | -0.18768 | 0.14648 | 0.23804 | 0.018311 | -0.11902 | 0.17853 | -0.33417 | -0.35248 | -0.082397 | 121.3486 | 121.6461 | 61.821 | -121.4081 | 121.3806 | 121.4172 | 61.8164 | -121.4813
572.125 | 121.756 | -61.6653 | 59.7382 | 0.17426 | 0.0039007 | 0.060171 | 0.061577 | 0.12738 | -0.0023797 | -0.0041933 | 0.21286 | -0.010916 | 0.055087 | 0.068274 | 0.0046206 | -0.0077097 | 59.9442 | 59.935 | 0.036621 | -61.7981 | 59.5276 | -61.7477 | -61.6333 | -61.4685 | 0.018311 | -61.972 | 59.5551 | 59.5596 | -61.5189 | -61.7477 | -0.082398 | 0.032043 | -0.21057 | 121.6003 | -0.13275 | -0.16479 | 0.20599 | 0.14648 | -0.082398 | -0.18311 | 0.19684 | -0.3067 | -0.2243 | -0.17853 | 121.1929 | 121.6095 | 61.702 | -121.3715 | 121.2204 | 121.225 | 61.6837 | -121.4859
573.8594 | 121.7789 | -61.6104 | 59.8297 | -0.10803 | 0.0086005 | 0.064444 | 0.065636 | 0.12717 | -0.0060113 | -0.0054751 | -0.00076274 | -0.012198 | 0.056155 | 0.066351 | 0.00013459 | -0.0079233 | 60.0677 | 60.0906 | 0.23346 | -61.6745 | 59.6375 | -61.6425 | -61.528 | -61.3403 | 0.2655 | -61.8164 | 59.642 | 59.6512 | -61.4182 | -61.6058 | -0.032043 | 0.082398 | -0.19226 | 121.7011 | -0.064087 | -0.14648 | 0.23804 | 0.19226 | 0.004578 | -0.18768 | 0.27008 | -0.20599 | -0.21057 | -0.17853 | 121.2479 | 121.6782 | 61.8439 | -121.3577 | 121.2524 | 121.2616 | 61.8759 | -121.4355
575.5938 | 121.701 | -61.734 | 59.761 | -0.077515 | 0.010096 | 0.062735 | 0.066277 | 0.12524 | 0.0042425 | -0.0035525 | -0.046539 | -0.010062 | 0.055514 | 0.068487 | 0.0024844 | -0.0083505 | 59.9716 | 59.9304 | 0.1236 | -61.8027 | 59.6329 | -61.7065 | -61.6516 | -61.496 | 0.09613 | -62.0316 | 59.6146 | 59.6375 | -61.5097 | -61.7386 | 0.027466 | 0.082398 | -0.12817 | 121.6644 | -0.068664 | -0.15106 | 0.21057 | 0.2243 | -0.004577 | -0.14648 | 0.23804 | -0.29755 | -0.29297 | -0.1236 | 121.3669 | 121.7056 | 61.8576 | -121.4127 | 121.3486 | 121.3715 | 61.8301 | -121.4996
577.3281 | 121.6736 | -61.7386 | 59.7519 | 0.0064086 | 0.011378 | 0.061239 | 0.060722 | 0.1246 | 0.0023199 | -0.0014163 | 0.12131 | -0.0083526 | 0.055942 | 0.069128 | 0.0048344 | -0.0074961 | 59.903 | 59.8343 | -0.022888 | -61.8576 | 59.6054 | -61.7706 | -61.6837 | -61.5875 | -0.045776 | -62.114 | 59.5963 | 59.5779 | -61.5417 | -61.7798 | -0.032044 | 0.054931 | -0.14648 | 121.5729 | -0.11902 | -0.17395 | 0.15106 | 0.19684 | -0.041199 | -0.15564 | 0.15106 | -0.37537 | -0.33417 | -0.17395 | 121.344 | 121.6415 | 61.7157 | -121.4355 | 121.3348 | 121.3165 | 61.6928 | -121.5317
579.0781 | 121.6644 | -61.7432 | 59.7519 | 0.052185 | 0.0081733 | 0.065084 | 0.063499 | 0.12674 | 0.00082452 | -0.0022707 | 0.13657 | -0.0092072 | 0.057651 | 0.067847 | 0.002698 | -0.0051463 | 59.8343 | 59.7931 | -0.10071 | -61.8759 | 59.5734 | -61.7798 | -61.6974 | -61.6058 | -0.11902 | -62.1414 | 59.5779 | 59.5779 | -61.5601 | -61.7615 | -0.036621 | 0.045776 | -0.17853 | 121.5363 | -0.13275 | -0.17853 | 0.082398 | 0.1831 | -0.018311 | -0.17395 | 0.13733 | -0.39825 | -0.37994 | -0.17395 | 121.3165 | 121.5775 | 61.6425 | -121.4493 | 121.3211 | 121.3211 | 61.6241 | -121.5134
580.7656 | 121.7468 | -61.6608 | 59.7702 | 0.13611 | 0.0053961 | 0.064657 | 0.060295 | 0.12759 | -0.0034479 | -0.0041933 | 0.23575 | -0.0096344 | 0.055514 | 0.068915 | 0.0014164 | -0.0074961 | 59.9533 | 59.9625 | 0.050354 | -61.7889 | 59.5367 | -61.6974 | -61.6287 | -61.4548 | 0.045776 | -61.9583 | 59.5505 | 59.5825 | -61.5051 | -61.7203 | -0.036621 | 0.032044 | -0.23346 | 121.6232 | -0.12817 | -0.16022 | 0.1831 | 0.15564 | -0.059509 | -0.21973 | 0.20599 | -0.29755 | -0.23804 | -0.18768 | 121.1975 | 121.6141 | 61.7111 | -121.3989 | 121.2112 | 121.2433 | 61.7065 | -121.4905
582.5156 | 121.8018 | -61.5875 | 59.8343 | -0.0088499 | 0.0083869 | 0.063162 | 0.067986 | 0.12738 | -0.0057977 | -0.0073977 | 0.11368 | -0.011557 | 0.057651 | 0.06571 | -0.0022152 | -0.0062143 | 59.9579 | 59.9854 | 0.09613 | -61.7432 | 59.6191 | -61.6562 | -61.5646 | -61.4136 | 0.13733 | -61.9034 | 59.6283 | 59.6375 | -61.4227 | -61.6333 | -0.068665 | 0.022888 | -0.21515 | 121.5729 | -0.15564 | -0.17853 | 0.1236 | 0.1648 | -0.045777 | -0.20599 | 0.17395 | -0.31586 | -0.27008 | -0.19684 | 121.2067 | 121.5454 | 61.6837 | -121.3989 | 121.2158 | 121.225 | 61.7249 | -121.4676
584.2656 | 121.6782 | -61.7386 | 59.7656 | 0.090332 | 0.0086005 | 0.059744 | 0.064568 | 0.12717 | 0.0040289 | -0.0039797 | 0.09079 | -0.009848 | 0.057223 | 0.07041 | 0.0039798 | -0.0068551 | 59.8755 | 59.8068 | -0.064087 | -61.8576 | 59.6054 | -61.7752 | -61.6974 | -61.615 | -0.10986 | -62.1597 | 59.6008 | 59.6054 | -61.5326 | -61.7706 | -0.036622 | 0.041198 | -0.16022 | 121.5454 | -0.11902 | -0.16022 | 0.10986 | 0.20599 | -0.032044 | -0.16479 | 0.1236 | -0.42114 | -0.3891 | -0.16022 | 121.344 | 121.6141 | 61.6745 | -121.463 | 121.3394 | 121.344 | 61.6287 | -121.5363
585.9531 | 121.7102 | -61.6653 | 59.8114 | -0.13855 | 0.0041143 | 0.061453 | 0.060722 | 0.1293 | -2.988e-05 | -0.0065433 | -0.13046 | -0.010275 | 0.055942 | 0.068701 | -0.00029261 | -0.0057871 | 59.9762 | 59.9258 | 0.082397 | -61.7615 | 59.6924 | -61.6699 | -61.5967 | -61.4914 | 0.14191 | -62.0087 | 59.6924 | 59.7244 | -61.4456 | -61.6516 | -0.004578 | 0.068664 | -0.11902 | 121.5912 | -0.096131 | -0.16479 | 0.1648 | 0.21973 | 0.013733 | -0.11902 | 0.17395 | -0.34332 | -0.35706 | -0.086975 | 121.3577 | 121.6415 | 61.7477 | -121.4081 | 121.3577 | 121.3898 | 61.8073 | -121.463
587.7031 | 121.6461 | -61.7111 | 59.7519 | -0.0012209 | 0.0092413 | 0.06658 | 0.059654 | 0.12759 | 0.0027471 | -0.0041933 | 0.029755 | -0.0072846 | 0.056155 | 0.068274 | 0.006116 | -0.0066415 | 59.9213 | 59.8663 | -0.004578 | -61.821 | 59.6008 | -61.7386 | -61.6425 | -61.5646 | -0.064087 | -62.0956 | 59.5871 | 59.6191 | -61.5417 | -61.7523 | -0.027465 | 0.068665 | -0.15106 | 121.5775 | -0.10986 | -0.17853 | 0.16937 | 0.16937 | -0.041198 | -0.16479 | 0.14648 | -0.38452 | -0.34332 | -0.13275 | 121.312 | 121.6324 | 61.7065 | -121.3943 | 121.2982 | 121.3303 | 61.647 | -121.5042
589.4688 | 121.6965 | -61.6928 | 59.7656 | -0.054626 | 0.0081733 | 0.063162 | 0.060509 | 0.12524 | 0.00018372 | -0.0029117 | -0.046539 | -0.0079254 | 0.056369 | 0.069128 | 0.004407 | -0.0062143 | 59.9854 | 59.9487 | 0.07782 | -61.7615 | 59.6283 | -61.7065 | -61.6241 | -61.4914 | 0.10071 | -61.9995 | 59.6283 | 59.6832 | -61.496 | -61.6974 | -0.013733 | 0.068664 | -0.13733 | 121.6415 | -0.068665 | -0.13733 | 0.21973 | 0.19684 | -0.004578 | -0.13733 | 0.20142 | -0.3067 | -0.30212 | -0.082397 | 121.3211 | 121.6782 | 61.7706 | -121.3898 | 121.3211 | 121.376 | 61.7935 | -121.463
591.1562 | 121.7056 | -61.6516 | 59.8434 | -0.19196 | 0.010096 | 0.063589 | 0.065636 | 0.12524 | -0.0032343 | -0.0037661 | -0.13046 | -0.010062 | 0.058291 | 0.070624 | 0.00013459 | -0.0062143 | 59.9808 | 59.9487 | 0.11444 | -61.7386 | 59.7015 | -61.6425 | -61.5555 | -61.496 | 0.14191 | -61.972 | 59.7153 | 59.7473 | -61.4456 | -61.6562 | 0.009155 | 0.09613 | -0.14191 | 121.6003 | -0.086975 | -0.1831 | 0.13733 | 0.20599 | -0.004578 | -0.12817 | 0.15564 | -0.32043 | -0.31586 | -0.096131 | 121.3531 | 121.6324 | 61.7661 | -121.3989 | 121.3669 | 121.3989 | 61.7935 | -121.4996
592.9219 | 121.7148 | -61.6791 | 59.8068 | -0.13092 | 0.0053961 | 0.060598 | 0.063499 | 0.12759 | 0.00061092 | -0.0039797 | -0.077057 | -0.010703 | 0.056582 | 0.068274 | 0.0031254 | -0.0081369 | 59.9716 | 59.9304 | 0.086975 | -61.7386 | 59.6649 | -61.6653 | -61.615 | -61.4822 | 0.10529 | -61.9858 | 59.6649 | 59.6512 | -61.4777 | -61.6791 | 0.013733 | 0.064087 | -0.14191 | 121.6095 | -0.059509 | -0.1236 | 0.16479 | 0.20142 | 0 | -0.14191 | 0.19684 | -0.3067 | -0.3067 | -0.15564 | 121.344 | 121.6507 | 61.7661 | -121.4218 | 121.344 | 121.3303 | 61.7844 | -121.4859
594.6719 | 121.6736 | -61.7294 | 59.7839 | 0.075073 | 0.0068915 | 0.062094 | 0.060722 | 0.12717 | -0.0010981 | -0.0033389 | 0.11368 | -0.01113 | 0.056796 | 0.066992 | 0.0054752 | -0.0057871 | 59.8572 | 59.8251 | -0.11444 | -61.853 | 59.6191 | -61.7249 | -61.6425 | -61.6104 | -0.1236 | -62.1185 | 59.6237 | 59.6375 | -61.5463 | -61.7569 | 0.004577 | 0.086975 | -0.16479 | 121.5546 | -0.1236 | -0.21057 | 0.073242 | 0.1831 | -0.027466 | -0.16022 | 0.11902 | -0.3891 | -0.36163 | -0.14648 | 121.3486 | 121.5866 | 61.615 | -121.4264 | 121.3531 | 121.3669 | 61.6058 | -121.5408
596.3594 | 121.7194 | -61.7111 | 59.7702 | 0.13611 | 0.0094549 | 0.062094 | 0.063286 | 0.12589 | 0.0010381 | -0.0026981 | 0.18997 | -0.0074982 | 0.056582 | 0.070196 | 0.0022708 | -0.0060007 | 59.8755 | 59.8114 | -0.15564 | -61.8576 | 59.61 | -61.734 | -61.647 | -61.5738 | -0.11902 | -62.0819 | 59.6191 | 59.6558 | -61.5189 | -61.7523 | -0.022888 | 0.064087 | -0.16022 | 121.5225 | -0.14648 | -0.21057 | 0.10528 | 0.19226 | -0.041198 | -0.15106 | 0.13733 | -0.37079 | -0.32959 | -0.11444 | 121.3211 | 121.5866 | 61.5555 | -121.4172 | 121.3303 | 121.3669 | 61.5921 | -121.5225
598.1094 | 121.7697 | -61.647 | 59.7839 | 0.15137 | 0.0062505 | 0.062307 | 0.066063 | 0.12802 | -0.0032343 | -0.0026981 | 0.22049 | -0.011557 | 0.057651 | 0.07041 | 0.00163 | -0.0081369 | 59.9762 | 59.9533 | -0.036621 | -61.7523 | 59.5779 | -61.6745 | -61.5875 | -61.4365 | -0.004578 | -61.9537 | 59.6008 | 59.61 | -61.4731 | -61.702 | -0.027466 | 0.05951 | -0.20599 | 121.6003 | -0.10529 | -0.16479 | 0.19226 | 0.17395 | -0.054931 | -0.18311 | 0.21057 | -0.3067 | -0.25177 | -0.17395 | 121.225 | 121.6232 | 61.6104 | -121.3715 | 121.2479 | 121.257 | 61.6425 | -121.4859
599.8594 | 121.7514 | -61.6379 | 59.848 | 0.16663 | 0.0036871 | 0.062521 | 0.062004 | 0.12567 | -0.0060113 | -0.0039797 | 0.24338 | -0.010703 | 0.05466 | 0.069128 | 0.0012028 | -0.0055735 | 59.9991 | 59.9991 | -0.050354 | -61.7477 | 59.5779 | -61.6745 | -61.5875 | -61.3953 | 0.027466 | -61.908 | 59.6008 | 59.6237 | -61.4502 | -61.6745 | -0.036622 | 0.050354 | -0.27008 | 121.637 | -0.10986 | -0.16022 | 0.15106 | 0.18768 | -0.036622 | -0.24719 | 0.24261 | -0.27008 | -0.23346 | -0.2243 | 121.2158 | 121.637 | 61.5875 | -121.4355 | 121.2387 | 121.2616 | 61.6653 | -121.5225
601.5625 | 121.8018 | -61.5372 | 59.8801 | 0.021668 | 0.0053961 | 0.064657 | 0.06649 | 0.12311 | -0.0060113 | -0.0059023 | 0.13657 | -0.012839 | 0.057864 | 0.066992 | -0.001788 | -0.0066415 | 60.0082 | 60.0357 | -0.004578 | -61.6882 | 59.6695 | -61.5921 | -61.5189 | -61.3861 | 0.11902 | -61.8713 | 59.6741 | 59.697 | -61.3998 | -61.6196 | -0.054932 | 0.01831 | -0.21057 | 121.5729 | -0.15106 | -0.16937 | 0.12817 | 0.13733 | -0.082398 | -0.20599 | 0.15106 | -0.33417 | -0.25177 | -0.18311 | 121.2067 | 121.5454 | 61.5326 | -121.3989 | 121.2112 | 121.2341 | 61.6562 | -121.4996
603.3281 | 121.7148 | -61.6196 | 59.8709 | -0.16144 | 0.0088141 | 0.06188 | 0.064354 | 0.12674 | -0.00067088 | -0.0054751 | -0.13046 | -0.010275 | 0.056796 | 0.067847 | 0.004407 | -0.0085641 | 60.0174 | 59.9899 | 0.022888 | -61.702 | 59.7473 | -61.6104 | -61.5234 | -61.4365 | 0.12817 | -61.94 | 59.7794 | 59.761 | -61.409 | -61.6196 | 0.009155 | 0.096131 | -0.1236 | 121.6095 | -0.082397 | -0.17853 | 0.14648 | 0.21057 | 0 | -0.091553 | 0.18311 | -0.32043 | -0.32043 | -0.10986 | 121.3669 | 121.637 | 61.6425 | -121.3943 | 121.3989 | 121.3806 | 61.7477 | -121.4905
605 | 121.756 | -61.6013 | 59.7794 | 0.15137 | 0.0062505 | 0.062307 | 0.059654 | 0.12482 | -0.0010981 | -0.0065433 | 0.24338 | -0.012411 | 0.054233 | 0.067847 | 0.0041934 | -0.0064279 | 60.0311 | 60.0128 | -0.068665 | -61.7203 | 59.6054 | -61.6516 | -61.5967 | -61.3998 | 0.013733 | -61.9125 | 59.6191 | 59.6283 | -61.4685 | -61.6837 | -0.050354 | 0.004577 | -0.17395 | 121.6141 | -0.11902 | -0.1236 | 0.25177 | 0.13275 | -0.082398 | -0.16022 | 0.20142 | -0.31128 | -0.22888 | -0.15106 | 121.2067 | 121.6324 | 61.5326 | -121.376 | 121.2204 | 121.2296 | 61.615 | -121.463
606.75 | 121.6782 | -61.5692 | 59.9533 | -0.14618 | 0.01095 | 0.061026 | 0.064995 | 0.12845 | -0.0010981 | -0.0046207 | -0.069428 | -0.012411 | 0.058291 | 0.066779 | 0.00077539 | -0.0064279 | 60.1135 | 60.1501 | 0.10529 | -61.6013 | 59.7198 | -61.5509 | -61.4502 | -61.3083 | 0.25635 | -61.821 | 59.7565 | 59.7748 | -61.3449 | -61.5555 | 0.018311 | 0.11902 | -0.23346 | 121.7194 | -0.032043 | -0.15106 | 0.16022 | 0.2243 | 0.013733 | -0.19684 | 0.26093 | -0.25177 | -0.2655 | -0.17853 | 121.2891 | 121.6827 | 61.6745 | -121.4035 | 121.3257 | 121.344 | 61.8256 | -121.5088
608.5 | 121.7697 | -61.6104 | 59.7977 | 0.14374 | 0.0066779 | 0.061666 | 0.060295 | 0.12674 | -0.00088448 | -0.0031253 | 0.1976 | -0.0077118 | 0.057651 | 0.067633 | 0.0046206 | -0.0057871 | 59.9625 | 59.9258 | -0.1831 | -61.7752 | 59.6283 | -61.6837 | -61.6058 | -61.4227 | -0.082397 | -61.9629 | 59.6649 | 59.6695 | -61.4365 | -61.6699 | -0.073242 | 0.004578 | -0.16937 | 121.5363 | -0.16479 | -0.16937 | 0.16479 | 0.17395 | -0.059509 | -0.13275 | 0.18768 | -0.35248 | -0.29297 | -0.12817 | 121.2387 | 121.5729 | 61.4273 | -121.4035 | 121.2753 | 121.2799 | 61.528 | -121.4676
610.2344 | 121.6919 | -61.5326 | 59.9854 | -0.16144 | 0.0073187 | 0.063162 | 0.065636 | 0.1246 | -0.0036615 | -0.0052615 | -0.031281 | -0.013052 | 0.058078 | 0.065497 | 0.0014164 | -0.0074961 | 60.1501 | 60.173 | 0.1236 | -61.5875 | 59.7565 | -61.5189 | -61.4685 | -61.2854 | 0.27008 | -61.7798 | 59.7473 | 59.7885 | -61.3037 | -61.5463 | 0.013733 | 0.064087 | -0.22888 | 121.7056 | -0.054931 | -0.11902 | 0.16479 | 0.22888 | -0.013733 | -0.23804 | 0.24719 | -0.24719 | -0.23346 | -0.19684 | 121.2891 | 121.6827 | 61.6562 | -121.4539 | 121.2799 | 121.3211 | 61.8027 | -121.5317
611.9219 | 121.7331 | -61.5005 | 59.9716 | -0.14618 | 0.0075323 | 0.06188 | 0.064568 | 0.12418 | -0.0030207 | -0.0059023 | -0.061798 | -0.01113 | 0.058291 | 0.068487 | 0.0014164 | -0.0098459 | 60.1776 | 60.2097 | 0.14191 | -61.5646 | 59.7565 | -61.5097 | -61.4273 | -61.2579 | 0.27008 | -61.7661 | 59.7794 | 59.761 | -61.3403 | -61.5326 | -0.009156 | 0.073242 | -0.21515 | 121.7102 | -0.064087 | -0.13733 | 0.20599 | 0.16022 | -0.032044 | -0.19226 | 0.24261 | -0.2655 | -0.23346 | -0.21057 | 121.257 | 121.6782 | 61.6425 | -121.3989 | 121.2799 | 121.2616 | 61.7706 | -121.5042
613.6562 | 121.6873 | -61.5143 | 59.9579 | -0.18433 | 0.010523 | 0.063162 | 0.065422 | 0.12631 | -0.0034479 | -0.0056887 | -0.054169 | -0.00878 | 0.05701 | 0.069342 | 0.00163 | -0.0083505 | 60.1273 | 60.1044 | 0.050354 | -61.615 | 59.7885 | -61.5555 | -61.441 | -61.3312 | 0.16937 | -61.8668 | 59.8343 | 59.8068 | -61.3266 | -61.5555 | -0.041199 | 0.073242 | -0.16937 | 121.6187 | -0.10071 | -0.17395 | 0.16937 | 0.18768 | -0.041199 | -0.1236 | 0.18311 | -0.35248 | -0.31128 | -0.15106 | 121.3028 | 121.6415 | 61.5646 | -121.3989 | 121.3486 | 121.3211 | 61.6837 | -121.5134
615.3438 | 121.7468 | -61.5509 | 59.9167 | 0.12848 | 0.0073187 | 0.06423 | 0.063927 | 0.12695 | -0.0047297 | -0.0048343 | 0.18997 | -0.009848 | 0.056155 | 0.067847 | 0.0014164 | -0.0081369 | 60.0769 | 60.0677 | -0.068665 | -61.6837 | 59.6695 | -61.5967 | -61.5005 | -61.322 | 0.032043 | -61.8668 | 59.7061 | 59.7153 | -61.3632 | -61.5829 | -0.045777 | 0.050354 | -0.24719 | 121.6187 | -0.13275 | -0.18311 | 0.16022 | 0.18768 | -0.032044 | -0.21057 | 0.22888 | -0.31586 | -0.28381 | -0.20142 | 121.2204 | 121.6278 | 61.4822 | -121.4172 | 121.257 | 121.2662 | 61.5829 | -121.4996
617.0938 | 121.788 | -61.5829 | 59.8297 | 0.12085 | 0.0047553 | 0.062948 | 0.061363 | 0.12631 | 0.0021063 | -0.0063297 | 0.15182 | -0.0074982 | 0.055087 | 0.069128 | 0.0056888 | -0.0087777 | 59.9808 | 59.9487 | -0.17853 | -61.7477 | 59.7198 | -61.6516 | -61.5738 | -61.4273 | -0.10986 | -61.9812 | 59.6695 | 59.6786 | -61.4548 | -61.6791 | -0.068664 | 0.009155 | -0.10986 | 121.5317 | -0.1648 | -0.17395 | 0.15106 | 0.12817 | -0.09613 | -0.16022 | 0.15564 | -0.39825 | -0.30212 | -0.15106 | 121.3028 | 121.5637 | 61.4044 | -121.4035 | 121.2524 | 121.2616 | 61.4731 | -121.5088
618.7812 | 121.6644 | -61.5326 | 59.9716 | -0.14618 | 0.0083869 | 0.062307 | 0.064995 | 0.12824 | -0.0013117 | -0.0050479 | -0.14572 | -0.01113 | 0.057651 | 0.069769 | 0.00013459 | -0.0079233 | 60.0723 | 60.0723 | 0.041199 | -61.6425 | 59.8022 | -61.528 | -61.4594 | -61.3495 | 0.16022 | -61.8576 | 59.8343 | 59.848 | -61.322 | -61.5417 | 0.004578 | 0.073242 | -0.16937 | 121.6049 | -0.10986 | -0.18311 | 0.10071 | 0.21057 | -0.009155 | -0.13733 | 0.18311 | -0.32501 | -0.31586 | -0.1236 | 121.3348 | 121.6049 | 61.5738 | -121.431 | 121.3669 | 121.3806 | 61.6928 | -121.5134
620.5312 | 121.6507 | -61.6241 | 59.9121 | -0.039368 | 0.012232 | 0.063589 | 0.065208 | 0.1261 | 0.0029607 | -0.0026981 | -0.0083922 | -0.0072846 | 0.059573 | 0.068701 | 0.0020572 | -0.0077097 | 60.0906 | 60.0403 | -0.018311 | -61.6745 | 59.729 | -61.5784 | -61.496 | -61.3861 | 0.027466 | -61.9217 | 59.7244 | 59.7565 | -61.4044 | -61.6196 | 0.045777 | 0.12817 | -0.1831 | 121.6644 | -0.050354 | -0.17853 | 0.17853 | 0.21973 | 0.004578 | -0.18768 | 0.23804 | -0.29755 | -0.30212 | -0.15564 | 121.3531 | 121.7148 | 61.6058 | -121.4081 | 121.3486 | 121.3806 | 61.6516 | -121.5317
622.2812 | 121.7789 | -61.4594 | 59.9487 | -0.092773 | 0.0071051 | 0.062521 | 0.065849 | 0.12759 | -0.0072931 | -0.0059023 | 0.029755 | -0.011771 | 0.055942 | 0.067633 | -7.9008e-05 | -0.0042917 | 60.1776 | 60.2188 | 0.11902 | -61.5417 | 59.7748 | -61.4777 | -61.4227 | -61.2076 | 0.25635 | -61.7065 | 59.7748 | 59.761 | -61.2625 | -61.4914 | -0.01831 | 0.036622 | -0.17395 | 121.6782 | -0.082397 | -0.11902 | 0.22888 | 0.19684 | -0.032043 | -0.17395 | 0.25177 | -0.24719 | -0.21515 | -0.18768 | 121.2341 | 121.637 | 61.5784 | -121.3715 | 121.2341 | 121.2204 | 61.7157 | -121.4401
623.9688 | 121.7239 | -61.6058 | 59.8618 | 0.12085 | 0.0071051 | 0.062948 | 0.060722 | 0.12781 | 0.00061092 | -0.0059023 | 0.12894 | -0.0066436 | 0.054873 | 0.069769 | 0.0037662 | -0.0064279 | 59.9762 | 59.9121 | -0.15564 | -61.7477 | 59.7244 | -61.6745 | -61.5601 | -61.4456 | -0.12817 | -61.9766 | 59.7336 | 59.7473 | -61.441 | -61.6562 | -0.068665 | 0.045776 | -0.13733 | 121.5179 | -0.14191 | -0.18768 | 0.11444 | 0.16479 | -0.050354 | -0.12817 | 0.16022 | -0.37079 | -0.32044 | -0.11444 | 121.3303 | 121.582 | 61.4502 | -121.4218 | 121.3394 | 121.3531 | 61.4777 | -121.5179
625.7188 | 121.788 | -61.4502 | 59.967 | -0.1004 | 0.0058233 | 0.064016 | 0.063072 | 0.1261 | -0.0055841 | -0.0050479 | -0.00076274 | -0.012411 | 0.055514 | 0.064856 | 0.0022708 | -0.0062143 | 60.1913 | 60.2325 | 0.14648 | -61.5463 | 59.7702 | -61.4868 | -61.3861 | -61.1847 | 0.24719 | -61.6791 | 59.7977 | 59.8343 | -61.2671 | -61.4731 | -0.036621 | 0.064087 | -0.19684 | 121.6827 | -0.096131 | -0.16022 | 0.2243 | 0.1831 | -0.022888 | -0.16937 | 0.2655 | -0.22888 | -0.20599 | -0.13275 | 121.2204 | 121.6415 | 61.5967 | -121.3531 | 121.2479 | 121.2845 | 61.6974 | -121.4401
627.4844 | 121.6507 | -61.6013 | 59.9121 | -0.016479 | 0.0088141 | 0.062094 | 0.062645 | 0.12653 | 0.0029607 | -0.0020571 | 0.014496 | -0.00878 | 0.05701 | 0.069769 | 0.0052616 | -0.0085641 | 60.0861 | 60.054 | -0.041199 | -61.6653 | 59.7336 | -61.5829 | -61.5234 | -61.4136 | -0.050354 | -61.9583 | 59.7473 | 59.7427 | -61.3998 | -61.6333 | 0.01831 | 0.07782 | -0.17853 | 121.6553 | -0.064087 | -0.14191 | 0.17395 | 0.20142 | -0.032044 | -0.16479 | 0.18768 | -0.35706 | -0.32501 | -0.16937 | 121.3348 | 121.6873 | 61.5601 | -121.4355 | 121.3486 | 121.344 | 61.5509 | -121.5454
629.1719 | 121.6736 | -61.496 | 60.0174 | -0.22247 | 0.010096 | 0.062521 | 0.066704 | 0.12589 | -0.0047297 | -0.0063297 | -0.099945 | -0.0083526 | 0.058719 | 0.069556 | 0.00013459 | -0.0057871 | 60.1135 | 60.1547 | 0.082397 | -61.5921 | 59.8114 | -61.4914 | -61.4227 | -61.2991 | 0.13733 | -61.8301 | 59.8618 | 59.8755 | -61.3037 | -61.5234 | 0.004578 | 0.073243 | -0.20599 | 121.6507 | -0.09613 | -0.16937 | 0.09613 | 0.19226 | -0.027465 | -0.15564 | 0.19684 | -0.33417 | -0.3067 | -0.14191 | 121.3074 | 121.6095 | 61.5784 | -121.4401 | 121.3577 | 121.3715 | 61.6333 | -121.5408
630.9219 | 121.7697 | -61.528 | 59.8984 | 0.11322 | 0.0073187 | 0.063375 | 0.062218 | 0.1261 | -0.0010981 | -0.0033389 | 0.22049 | -0.010703 | 0.055301 | 0.068274 | 0.0020572 | -0.0072825 | 60.1044 | 60.0998 | -0.013733 | -61.6287 | 59.7107 | -61.5875 | -61.4777 | -61.3083 | -0.013733 | -61.8301 | 59.7061 | 59.729 | -61.3632 | -61.5372 | -0.059509 | 0.050354 | -0.18768 | 121.6278 | -0.10071 | -0.15106 | 0.20599 | 0.1648 | -0.009155 | -0.19226 | 0.21973 | -0.30212 | -0.29297 | -0.16937 | 121.2387 | 121.6324 | 61.5143 | -121.376 | 121.2341 | 121.257 | 61.5143 | -121.4355
632.6719 | 121.7834 | -61.4868 | 59.8938 | 0.159 | 0.0060369 | 0.062948 | 0.058586 | 0.12631 | -0.0019525 | -0.0048343 | 0.1976 | -0.011984 | 0.054873 | 0.065924 | 0.002698 | -0.0081369 | 60.0998 | 60.1044 | -0.027466 | -61.615 | 59.6878 | -61.5738 | -61.4822 | -61.3037 | -0.018311 | -61.8347 | 59.6832 | 59.6924 | -61.3586 | -61.5829 | -0.086976 | 0.004577 | -0.20599 | 121.5912 | -0.12817 | -0.13275 | 0.20599 | 0.12817 | -0.096131 | -0.21057 | 0.1831 | -0.3479 | -0.25177 | -0.20142 | 121.1746 | 121.5866 | 61.4594 | -121.376 | 121.17 | 121.1792 | 61.4685 | -121.4767
634.3594 | 121.7056 | -61.5967 | 59.8984 | 0.097962 | 0.0090277 | 0.061453 | 0.062431 | 0.12631 | 0.0014655 | -0.0039797 | 0.13657 | -0.0079254 | 0.05466 | 0.069342 | 0.0020572 | -0.0077097 | 59.9991 | 59.9304 | -0.11444 | -61.7157 | 59.7427 | -61.6196 | -61.528 | -61.4273 | -0.14191 | -61.9675 | 59.7336 | 59.761 | -61.3998 | -61.6333 | -0.022888 | 0.068665 | -0.15564 | 121.5271 | -0.11902 | -0.18768 | 0.10071 | 0.19684 | -0.036621 | -0.16479 | 0.16937 | -0.37079 | -0.33417 | -0.13733 | 121.3394 | 121.5958 | 61.4822 | -121.4264 | 121.3303 | 121.3577 | 61.4548 | -121.5317
636.1094 | 121.7743 | -61.4319 | 59.9808 | -0.077515 | 0.0066779 | 0.063803 | 0.065849 | 0.12866 | -0.0068659 | -0.0063297 | 0.0068663 | -0.011771 | 0.056582 | 0.067419 | -0.0013608 | -0.0053599 | 60.2234 | 60.2509 | 0.17395 | -61.5051 | 59.7931 | -61.4731 | -61.3861 | -61.171 | 0.24261 | -61.6653 | 59.8297 | 59.8343 | -61.2488 | -61.4319 | -0.041198 | 0.045777 | -0.18768 | 121.6827 | -0.073242 | -0.11902 | 0.24262 | 0.18311 | 0 | -0.15106 | 0.26093 | -0.23346 | -0.23346 | -0.14648 | 121.225 | 121.6553 | 61.6058 | -121.3669 | 121.2616 | 121.2662 | 61.6745 | -121.4127
637.8594 | 121.7194 | -61.5784 | 59.8892 | 0.15137 | 0.0086005 | 0.060598 | 0.062859 | 0.1261 | 0.0012519 | -0.0018435 | 0.12894 | -0.0094208 | 0.055087 | 0.070624 | 0.003339 | -0.0087777 | 60.0174 | 59.9487 | -0.13733 | -61.7111 | 59.7427 | -61.6013 | -61.5097 | -61.3998 | -0.15564 | -61.9354 | 59.761 | 59.7839 | -61.3861 | -61.6104 | -0.022888 | 0.068664 | -0.14648 | 121.5271 | -0.13275 | -0.20142 | 0.12817 | 0.19226 | -0.032044 | -0.12817 | 0.17853 | -0.35706 | -0.32501 | -0.10529 | 121.3211 | 121.5958 | 61.441 | -121.3989 | 121.3394 | 121.3623 | 61.4227 | -121.4996
639.5469 | 121.6599 | -61.4594 | 60.054 | -0.15381 | 0.0077459 | 0.062094 | 0.06649 | 0.12802 | -0.0038751 | -0.0046207 | -0.1152 | -0.0092072 | 0.059146 | 0.069128 | 0.00034819 | -0.0060007 | 60.2325 | 60.2417 | 0.15564 | -61.4868 | 59.8297 | -61.4548 | -61.3586 | -61.2213 | 0.19684 | -61.7111 | 59.8434 | 59.903 | -61.2213 | -61.4685 | 0.004578 | 0.10071 | -0.2243 | 121.701 | -0.027465 | -0.12817 | 0.17853 | 0.23804 | -0.009155 | -0.21057 | 0.23804 | -0.25177 | -0.24262 | -0.15106 | 121.2891 | 121.6919 | 61.615 | -121.4127 | 121.3028 | 121.3623 | 61.6562 | -121.5225
641.3125 | 121.6644 | -61.441 | 60.0677 | -0.14618 | 0.0090277 | 0.062307 | 0.065422 | 0.12759 | -0.0021661 | -0.0065433 | -0.16861 | -0.00878 | 0.058932 | 0.06806 | 0.0014164 | -0.010059 | 60.2417 | 60.2554 | 0.13275 | -61.4914 | 59.848 | -61.4365 | -61.3449 | -61.2076 | 0.17853 | -61.7157 | 59.8663 | 59.9121 | -61.2534 | -61.4594 | 0.004578 | 0.09613 | -0.21973 | 121.6965 | -0.050354 | -0.14648 | 0.17395 | 0.18768 | -0.018311 | -0.20142 | 0.23346 | -0.27466 | -0.25635 | -0.15564 | 121.2891 | 121.6827 | 61.5738 | -121.4127 | 121.3074 | 121.3531 | 61.6196 | -121.5271
643.0625 | 121.669 | -61.5738 | 59.9396 | 0.059815 | 0.0071051 | 0.061453 | 0.059227 | 0.12759 | 0.0044561 | -0.0035525 | 0.060272 | -0.0077118 | 0.054233 | 0.070837 | 0.0086796 | -0.0074961 | 60.0586 | 59.9808 | -0.14191 | -61.6791 | 59.7794 | -61.5738 | -61.5051 | -61.4136 | -0.15106 | -61.9537 | 59.7519 | 59.8022 | -61.3541 | -61.6058 | 0 | 0.068665 | -0.16022 | 121.5546 | -0.10529 | -0.17395 | 0.11902 | 0.21973 | -0.032043 | -0.18768 | 0.16022 | -0.37994 | -0.3479 | -0.13733 | 121.3531 | 121.6324 | 61.4319 | -121.4447 | 121.3257 | 121.376 | 61.4227 | -121.5454
644.7344 | 121.788 | -61.3861 | 60.0174 | -0.11566 | 0.0053961 | 0.066153 | 0.064354 | 0.12524 | -0.0062249 | -0.0065433 | 0.014496 | -0.011984 | 0.057223 | 0.068487 | -0.00093361 | -0.0060007 | 60.2371 | 60.26 | 0.14648 | -61.4868 | 59.8297 | -61.4502 | -61.3632 | -61.1435 | 0.18768 | -61.6516 | 59.8297 | 59.8526 | -61.2442 | -61.4685 | -0.064087 | 0.022888 | -0.18768 | 121.6461 | -0.10071 | -0.1236 | 0.21973 | 0.14191 | -0.082398 | -0.18768 | 0.24261 | -0.2655 | -0.18311 | -0.16479 | 121.2158 | 121.6232 | 61.5326 | -121.3806 | 121.2158 | 121.2387 | 61.5738 | -121.4859
646.5 | 121.7514 | -61.4594 | 59.9396 | 0.15137 | 0.0049689 | 0.061026 | 0.0588 | 0.12653 | -0.0019525 | -0.0067569 | 0.1976 | -0.012625 | 0.055301 | 0.068487 | 0.00056179 | -0.0089915 | 60.1593 | 60.1456 | -0.036621 | -61.6013 | 59.761 | -61.5189 | -61.4319 | -61.2305 | 0.004578 | -61.7706 | 59.7565 | 59.7702 | -61.2991 | -61.528 | -0.059509 | 0.027466 | -0.17853 | 121.6049 | -0.14191 | -0.16937 | 0.21973 | 0.16022 | -0.068664 | -0.1831 | 0.22888 | -0.31128 | -0.24261 | -0.16937 | 121.2204 | 121.6187 | 61.4227 | -121.3715 | 121.2158 | 121.2296 | 61.4639 | -121.4676
648.1875 | 121.669 | -61.4273 | 60.1089 | -0.19958 | 0.0073187 | 0.062948 | 0.063713 | 0.12653 | -0.0038751 | -0.0063297 | -0.12283 | -0.0096344 | 0.058932 | 0.068487 | 0.0014164 | -0.0072825 | 60.2509 | 60.2417 | 0.11902 | -61.4868 | 59.8755 | -61.4456 | -61.3449 | -61.2167 | 0.16479 | -61.7294 | 59.9167 | 59.9167 | -61.2167 | -61.4502 | -0.018311 | 0.082397 | -0.23346 | 121.669 | -0.059509 | -0.14191 | 0.14191 | 0.21057 | -0.022888 | -0.19226 | 0.21057 | -0.30212 | -0.27924 | -0.19226 | 121.3028 | 121.6782 | 61.5463 | -121.4539 | 121.344 | 121.344 | 61.5921 | -121.5591
649.9375 | 121.6324 | -61.5417 | 59.9762 | -0.039368 | 0.0086005 | 0.063375 | 0.06115 | 0.12653 | 0.0061651 | -0.0037661 | -0.016022 | -0.00878 | 0.055514 | 0.069342 | 0.006116 | -0.0096323 | 60.1501 | 60.1135 | -0.036621 | -61.6013 | 59.816 | -61.5143 | -61.4548 | -61.3083 | -0.009155 | -61.8622 | 59.7885 | 59.8022 | -61.3724 | -61.5555 | 0.027466 | 0.086975 | -0.16022 | 121.6553 | -0.059509 | -0.14648 | 0.17395 | 0.16937 | -0.013733 | -0.18768 | 0.23346 | -0.32044 | -0.3067 | -0.17395 | 121.3577 | 121.6919 | 61.5051 | -121.431 | 121.3303 | 121.344 | 61.5326 | -121.5317
652.1094 | 121.788 | -61.4639 | 59.9304 | 0.159 | 0.0075323 | 0.058462 | 0.061577 | 0.12674 | -0.0019525 | -0.0037661 | 0.12131 | -0.011984 | 0.055728 | 0.070196 | 0.0018436 | -0.0057871 | 60.1273 | 60.1181 | -0.064087 | -61.615 | 59.7565 | -61.5326 | -61.4731 | -61.2396 | -0.018311 | -61.7935 | 59.7519 | 59.7839 | -61.322 | -61.5692 | -0.068665 | -0.009155 | -0.17395 | 121.582 | -0.15106 | -0.14191 | 0.19684 | 0.14191 | -0.10529 | -0.17853 | 0.2243 | -0.32959 | -0.2243 | -0.14648 | 121.2204 | 121.5912 | 61.3998 | -121.4035 | 121.2158 | 121.2479 | 61.4456 | -121.4996
654 | 121.6644 | -61.4456 | 60.054 | -0.19196 | 0.0079595 | 0.064016 | 0.063927 | 0.12546 | -0.0038751 | -0.0048343 | -0.099945 | -0.00878 | 0.056582 | 0.067633 | 0.0012028 | -0.0057871 | 60.1776 | 60.173 | 0.091553 | -61.5234 | 59.8846 | -61.441 | -61.3678 | -61.2488 | 0.10529 | -61.7569 | 59.9213 | 59.8846 | -61.2625 | -61.4548 | 0.004578 | 0.07782 | -0.16937 | 121.6187 | -0.077819 | -0.15564 | 0.1236 | 0.18311 | -0.009155 | -0.13275 | 0.19684 | -0.31128 | -0.30212 | -0.16937 | 121.3303 | 121.6232 | 61.5372 | -121.4218 | 121.3669 | 121.3303 | 61.5509 | -121.5088
655.7031 | 121.7972 | -61.377 | 60.0311 | 0.044556 | 0.0053961 | 0.062948 | 0.064568 | 0.12482 | -0.0040887 | -0.0067569 | 0.12131 | -0.012198 | 0.057651 | 0.068701 | 0.00098899 | -0.0053599 | 60.1501 | 60.2097 | 0 | -61.5234 | 59.848 | -61.4273 | -61.3495 | -61.2076 | 0.07782 | -61.7111 | 59.8572 | 59.8755 | -61.2213 | -61.4548 | -0.050354 | 0.027466 | -0.18311 | 121.5866 | -0.14648 | -0.17395 | 0.11902 | 0.15564 | -0.07782 | -0.17395 | 0.16937 | -0.33417 | -0.25635 | -0.15564 | 121.225 | 121.5271 | 61.377 | -121.3806 | 121.2341 | 121.2524 | 61.4548 | -121.4859
657.4062 | 121.7606 | -61.4639 | 59.9167 | 0.10559 | 0.0066779 | 0.063375 | 0.060295 | 0.12482 | 0.0018927 | -0.0063297 | 0.16708 | -0.0077118 | 0.056582 | 0.069128 | 0.004407 | -0.0047189 | 60.0906 | 60.0586 | -0.15106 | -61.6379 | 59.816 | -61.5372 | -61.4548 | -61.3174 | -0.15106 | -61.8668 | 59.7977 | 59.7977 | -61.3129 | -61.5601 | -0.073242 | 0.009155 | -0.10071 | 121.5225 | -0.17395 | -0.1831 | 0.17395 | 0.15106 | -0.096131 | -0.11902 | 0.14648 | -0.40283 | -0.3067 | -0.11902 | 121.2799 | 121.5546 | 61.3129 | -121.3715 | 121.2616 | 121.2616 | 61.3129 | -121.4767
659.2344 | 121.8201 | -61.3541 | 60.1135 | -0.0088499 | 0.0071051 | 0.066153 | 0.06179 | 0.12674 | -0.0057977 | -0.0054751 | 0.060272 | -0.012839 | 0.056582 | 0.066138 | 0.0012028 | -0.0072825 | 60.228 | 60.2692 | 0.068665 | -61.4594 | 59.8572 | -61.4182 | -61.2946 | -61.1114 | 0.11902 | -61.615 | 59.8938 | 59.9075 | -61.1755 | -61.3998 | -0.064087 | 0.059509 | -0.25635 | 121.6232 | -0.10529 | -0.16479 | 0.11444 | 0.17853 | -0.045776 | -0.21973 | 0.24262 | -0.26093 | -0.21515 | -0.20599 | 121.2112 | 121.582 | 61.4227 | -121.4081 | 121.2479 | 121.2616 | 61.4731 | -121.5134
660.9688 | 121.6782 | -61.3724 | 60.0906 | -0.13855 | 0.0086005 | 0.061666 | 0.066277 | 0.12909 | -0.0028071 | -0.0044071 | -0.046539 | -0.0096344 | 0.058932 | 0.068274 | -0.00071981 | -0.010059 | 60.2966 | 60.3149 | 0.11902 | -61.4319 | 59.8801 | -61.3907 | -61.3266 | -61.1298 | 0.26093 | -61.6608 | 59.8984 | 59.9075 | -61.1755 | -61.4273 | -0.018311 | 0.045776 | -0.21057 | 121.6873 | -0.05951 | -0.10529 | 0.20599 | 0.19684 | -0.054932 | -0.19226 | 0.24261 | -0.28839 | -0.23346 | -0.1831 | 121.2524 | 121.669 | 61.4914 | -121.4172 | 121.2708 | 121.2799 | 61.6333 | -121.5179
662.6562 | 121.788 | -61.4319 | 59.967 | 0.17426 | 0.0073187 | 0.062094 | 0.060295 | 0.1246 | 0.0018927 | -0.0046207 | 0.16708 | -0.010062 | 0.054019 | 0.071265 | 0.0039798 | -0.0083505 | 60.1685 | 60.1318 | -0.14191 | -61.5784 | 59.816 | -61.4822 | -61.3907 | -61.2167 | -0.032043 | -61.7569 | 59.7931 | 59.7977 | -61.2671 | -61.5143 | -0.050354 | 0.041199 | -0.15106 | 121.5637 | -0.14648 | -0.18768 | 0.20142 | 0.16479 | -0.082397 | -0.17395 | 0.21515 | -0.32501 | -0.24262 | -0.16937 | 121.2479 | 121.6003 | 61.29 | -121.3577 | 121.225 | 121.2296 | 61.3998 | -121.4813
664.3594 | 121.7056 | -61.4502 | 60.0174 | -0.1004 | 0.011164 | 0.062521 | 0.067986 | 0.12653 | 0.0023199 | -0.0031253 | -0.084686 | -0.0094208 | 0.057864 | 0.069128 | 0.003339 | -0.0092051 | 60.2325 | 60.1959 | -0.045776 | -61.5051 | 59.8846 | -61.441 | -61.3586 | -61.2213 | 0.086975 | -61.7661 | 59.8984 | 59.8938 | -61.2442 | -61.4822 | 0.009155 | 0.091552 | -0.13275 | 121.6461 | -0.054932 | -0.14648 | 0.21515 | 0.20599 | -0.032044 | -0.11902 | 0.22888 | -0.31586 | -0.28381 | -0.1236 | 121.3348 | 121.6827 | 61.4044 | -121.376 | 121.3486 | 121.344 | 61.5372 | -121.4996
666.1094 | 121.7377 | -61.3815 | 60.0494 | 0.097962 | 0.0081733 | 0.063162 | 0.060936 | 0.12738 | -0.0055841 | -0.0052615 | 0.24338 | -0.009848 | 0.057437 | 0.06806 | -0.00029261 | -0.0057871 | 60.228 | 60.228 | 0 | -61.5234 | 59.8114 | -61.4548 | -61.3861 | -61.171 | -0.013733 | -61.6974 | 59.8526 | 59.8892 | -61.2259 | -61.4639 | -0.073242 | -0.004577 | -0.23804 | 121.6095 | -0.14191 | -0.13733 | 0.17853 | 0.15564 | -0.082397 | -0.19684 | 0.21057 | -0.31586 | -0.23346 | -0.16022 | 121.1929 | 121.6095 | 61.3815 | -121.4355 | 121.2341 | 121.2708 | 61.3678 | -121.5134
667.8125 | 121.7834 | -61.3358 | 60.0952 | -0.077515 | 0.0049689 | 0.06423 | 0.064568 | 0.12482 | -0.0051569 | -0.0052615 | -0.00076274 | -0.00878 | 0.055728 | 0.066565 | -0.001788 | -0.0068551 | 60.3241 | 60.3424 | 0.21057 | -61.4136 | 59.8801 | -61.3678 | -61.2808 | -61.0565 | 0.1236 | -61.5692 | 59.9167 | 59.935 | -61.1481 | -61.3907 | -0.032044 | 0.054931 | -0.21515 | 121.6782 | -0.07782 | -0.13275 | 0.22888 | 0.18768 | -0.054932 | -0.17853 | 0.27923 | -0.23346 | -0.17853 | -0.16022 | 121.2158 | 121.6599 | 61.5463 | -121.376 | 121.2524 | 121.2708 | 61.4594 | -121.4859
669.5156 | 121.7148 | -61.3861 | 60.0677 | -0.13855 | 0.0092413 | 0.062735 | 0.060295 | 0.12653 | 0.0016791 | -0.0067569 | -0.13809 | -0.0094208 | 0.055942 | 0.069983 | 0.005048 | -0.0089915 | 60.2371 | 60.2051 | 0.022888 | -61.4777 | 59.9762 | -61.3815 | -61.29 | -61.1938 | -0.018311 | -61.7249 | 59.9579 | 59.9762 | -61.1984 | -61.3998 | 0.004577 | 0.09613 | -0.091553 | 121.5912 | -0.091553 | -0.18768 | 0.16937 | 0.18768 | -0.013733 | -0.10986 | 0.19226 | -0.33875 | -0.32501 | -0.091553 | 121.3623 | 121.6232 | 61.409 | -121.3577 | 121.344 | 121.3623 | 61.3678 | -121.4676
671.2031 | 121.6553 | -61.3861 | 60.141 | -0.11566 | 0.0094549 | 0.063162 | 0.067558 | 0.12781 | -0.00045708 | -0.0033389 | -0.13809 | -0.010489 | 0.058505 | 0.068274 | 0.00163 | -0.0070689 | 60.2692 | 60.2371 | 0.050354 | -61.4548 | 59.9854 | -61.3724 | -61.2946 | -61.1526 | 0.059509 | -61.6928 | 59.9762 | 59.9945 | -61.1618 | -61.3632 | 0.013733 | 0.091552 | -0.15564 | 121.6232 | -0.068665 | -0.16022 | 0.12817 | 0.2243 | 0.022888 | -0.16479 | 0.23346 | -0.3067 | -0.32959 | -0.14648 | 121.3715 | 121.6553 | 61.4365 | -121.4355 | 121.3623 | 121.3806 | 61.4456 | -121.5042
672.9375 | 121.7148 | -61.3678 | 60.0998 | -0.13855 | 0.0090277 | 0.060598 | 0.065422 | 0.12759 | 0.00082452 | -0.0018435 | -0.12283 | -0.0089936 | 0.058078 | 0.068701 | 0.0012028 | -0.0079233 | 60.2646 | 60.2509 | 0.050354 | -61.441 | 59.9899 | -61.377 | -61.2991 | -61.1572 | 0.018311 | -61.6745 | 59.9716 | 59.9854 | -61.171 | -61.409 | -0.009155 | 0.068665 | -0.10986 | 121.6187 | -0.073242 | -0.14191 | 0.16479 | 0.19684 | -0.041199 | -0.12817 | 0.21057 | -0.3067 | -0.2655 | -0.11444 | 121.3577 | 121.6324 | 61.4182 | -121.3989 | 121.3394 | 121.3531 | 61.3861 | -121.5088
674.625 | 121.7697 | -61.3632 | 60.0494 | 0.16663 | 0.0092413 | 0.063162 | 0.059654 | 0.12674 | -0.00088448 | -0.0018435 | 0.21286 | -0.012198 | 0.055301 | 0.068915 | 0.0041934 | -0.0072825 | 60.26 | 60.26 | 0.15106 | -61.4639 | 59.8389 | -61.4044 | -61.3266 | -61.1298 | -0.082397 | -61.6699 | 59.8572 | 59.8618 | -61.1938 | -61.4502 | -0.041199 | 0.036621 | -0.21057 | 121.6232 | -0.10071 | -0.13733 | 0.21057 | 0.16937 | -0.086975 | -0.19226 | 0.23346 | -0.3067 | -0.21973 | -0.18768 | 121.2021 | 121.6232 | 61.5143 | -121.376 | 121.2204 | 121.225 | 61.2808 | -121.4996
676.3438 | 121.7789 | -61.377 | 60.0266 | 0.11322 | 0.0083869 | 0.062094 | 0.063072 | 0.12674 | 0.0010381 | -0.0044071 | 0.18997 | -0.0092072 | 0.056582 | 0.069556 | 0.0035526 | -0.0068551 | 60.173 | 60.1593 | 0.20142 | -61.5463 | 59.8846 | -61.4365 | -61.3632 | -61.1893 | -0.19226 | -61.7523 | 59.8663 | 59.9167 | -61.2534 | -61.4639 | -0.059509 | 0.013733 | -0.14191 | 121.5363 | -0.16937 | -0.18311 | 0.14648 | 0.1236 | -0.086975 | -0.16022 | 0.18768 | -0.37537 | -0.28839 | -0.10986 | 121.2616 | 121.55 | 61.5784 | -121.3898 | 121.2433 | 121.2936 | 61.1847 | -121.4905
678.0312 | 121.7972 | -61.2442 | 60.1547 | -0.0088499 | 0.0073187 | 0.063162 | 0.065208 | 0.13187 | -0.0070795 | -0.0054751 | 0.10605 | -0.0094208 | 0.057437 | 0.068915 | -0.00093361 | -0.0064279 | 60.3149 | 60.3241 | 0.39368 | -61.3724 | 59.967 | -61.2991 | -61.2122 | -61.0428 | 0.050354 | -61.5555 | 59.9808 | 59.9991 | -61.0886 | -61.2808 | -0.054931 | 0.032044 | -0.18768 | 121.5683 | -0.12817 | -0.16022 | 0.16022 | 0.15564 | -0.036621 | -0.17395 | 0.20142 | -0.31128 | -0.27466 | -0.15564 | 121.2112 | 121.5591 | 61.6379 | -121.3669 | 121.225 | 121.2433 | 61.2946 | -121.4355
679.7188 | 121.6507 | -61.3998 | 60.0723 | -0.031738 | 0.0090277 | 0.061239 | 0.06115 | 0.12524 | 0.0033881 | -0.0052615 | -0.0083922 | -0.0072846 | 0.055728 | 0.06806 | 0.0056888 | -0.0083505 | 60.2783 | 60.2234 | 0.44861 | -61.4777 | 59.9167 | -61.3998 | -61.3174 | -61.1664 | -0.064087 | -61.7294 | 59.935 | 59.9533 | -61.1984 | -61.4502 | 0 | 0.082397 | -0.15564 | 121.6232 | -0.07782 | -0.16022 | 0.20599 | 0.20142 | -0.050354 | -0.13733 | 0.23346 | -0.32959 | -0.27924 | -0.11902 | 121.3165 | 121.6782 | 61.8484 | -121.3898 | 121.3348 | 121.3531 | 61.3358 | -121.5225
681.4531 | 121.6873 | -61.2854 | 60.2097 | -0.15381 | 0.0081733 | 0.06423 | 0.064995 | 0.12589 | -0.0051569 | -0.0037661 | -0.016022 | -0.011984 | 0.058505 | 0.067419 | 0.0012028 | -0.0077097 | 60.379 | 60.4202 | 0.71411 | -61.3358 | 59.9808 | -61.2671 | -61.203 | -61.0062 | 0.16937 | -61.5097 | 60.0082 | 59.9991 | -61.0611 | -61.2991 | 0.01831 | 0.082397 | -0.22888 | 121.7056 | -0.050354 | -0.13275 | 0.16937 | 0.2243 | -0.013733 | -0.20142 | 0.27923 | -0.2243 | -0.21057 | -0.21057 | 121.2662 | 121.6644 | 61.9995 | -121.4127 | 121.2936 | 121.2845 | 61.4548 | -121.5088
683.2031 | 121.701 | -61.3266 | 60.1776 | -0.19958 | 0.0075323 | 0.063375 | 0.064568 | 0.12866 | 0.00061092 | -0.0033389 | -0.13046 | -0.010489 | 0.057437 | 0.066992 | 0.00163 | -0.0085641 | 60.3195 | 60.2921 | 0.58594 | -61.3861 | 60.0677 | -61.3037 | -61.2213 | -61.116 | 0.09613 | -61.6379 | 60.0632 | 60.0494 | -61.1252 | -61.322 | 0.022888 | 0.10529 | -0.10986 | 121.6187 | -0.059509 | -0.16479 | 0.14191 | 0.20142 | 0.004578 | -0.11444 | 0.21057 | -0.31128 | -0.31586 | -0.12817 | 121.3943 | 121.6461 | 61.9125 | -121.3989 | 121.3898 | 121.376 | 61.4227 | -121.4996
684.9688 | 121.7834 | -61.2213 | 60.1959 | -0.11566 | 0.0045417 | 0.063375 | 0.063927 | 0.12781 | -0.0075067 | -0.0054751 | 0.022125 | -0.011343 | 0.055514 | 0.067847 | 0.00098899 | -0.0074961 | 60.4019 | 60.4385 | 0.66376 | -61.3266 | 60.0082 | -61.2488 | -61.1938 | -60.9604 | 0.25635 | -61.4685 | 59.9899 | 60.022 | -61.0565 | -61.2808 | -0.027466 | 0.027465 | -0.18768 | 121.6599 | -0.10529 | -0.13275 | 0.20599 | 0.16479 | -0.05951 | -0.20599 | 0.26093 | -0.24719 | -0.18768 | -0.17395 | 121.2296 | 121.6232 | 61.8851 | -121.3898 | 121.2112 | 121.2433 | 61.4777 | -121.4767
686.7188 | 121.6736 | -61.4319 | 60.0677 | 0.082703 | 0.011164 | 0.06188 | 0.064781 | 0.12973 | 0.0018927 | -0.0056887 | 0.060272 | -0.0096344 | 0.058291 | 0.067847 | 0.0037662 | -0.0083505 | 60.1913 | 60.1227 | 0.40283 | -61.528 | 59.9213 | -61.441 | -61.3586 | -61.2579 | -0.059509 | -61.8164 | 59.9487 | 59.9487 | -61.2259 | -61.441 | -0.009155 | 0.073242 | -0.14648 | 121.5546 | -0.09613 | -0.16937 | 0.1236 | 0.20599 | -0.009155 | -0.11902 | 0.17395 | -0.38452 | -0.37537 | -0.11902 | 121.3531 | 121.6232 | 61.8347 | -121.4264 | 121.3806 | 121.3806 | 61.3724 | -121.5088
688.4688 | 121.6736 | -61.4136 | 60.0769 | -0.039368 | 0.0064643 | 0.063589 | 0.062645 | 0.12482 | 0.0031745 | -0.0014163 | -0.016022 | -0.0089936 | 0.056796 | 0.068915 | 0.0048344 | -0.0068551 | 60.3104 | 60.26 | 0.42114 | -61.4502 | 59.9487 | -61.3724 | -61.2991 | -61.1206 | 0.09613 | -61.6928 | 59.967 | 59.9899 | -61.171 | -61.3861 | 0.041199 | 0.11444 | -0.12817 | 121.6736 | -0.036621 | -0.15106 | 0.23346 | 0.24261 | 0.027466 | -0.10986 | 0.29297 | -0.27924 | -0.3067 | -0.086975 | 121.3623 | 121.7239 | 61.8347 | -121.376 | 121.3806 | 121.4035 | 61.5097 | -121.463
690.2344 | 121.7972 | -61.171 | 60.2554 | 0.11322 | 0.0064643 | 0.062735 | 0.062645 | 0.12653 | 0.00018372 | -0.0035525 | 0.22049 | -0.010062 | 0.054233 | 0.069983 | 0.0024844 | -0.0055735 | 60.4156 | 60.3516 | 0.24261 | -61.322 | 60.0906 | -61.2167 | -61.1298 | -60.9833 | -0.004578 | -61.5234 | 60.1044 | 60.1227 | -61.0016 | -61.203 | -0.045777 | 0.041198 | -0.16479 | 121.5225 | -0.15106 | -0.19226 | 0.16022 | 0.16937 | -0.032044 | -0.15106 | 0.18768 | -0.35248 | -0.32043 | -0.13275 | 121.2616 | 121.5866 | 61.4136 | -121.3852 | 121.2753 | 121.2936 | 61.1664 | -121.4584
691.9844 | 121.6782 | -61.0336 | 60.4843 | -0.19958 | 0.0090277 | 0.062948 | 0.062218 | 0.12503 | -0.00088448 | -0.0020571 | -0.1152 | -0.012411 | 0.057864 | 0.066992 | 0.0022708 | -0.0066415 | 60.5576 | 60.553 | 0.31128 | -61.1618 | 60.2921 | -61.0428 | -60.9604 | -60.8322 | 0.23804 | -61.377 | 60.3195 | 60.3653 | -60.8368 | -61.0474 | -0.009156 | 0.073242 | -0.19226 | 121.5866 | -0.12817 | -0.20142 | 0.073242 | 0.19684 | -0.013733 | -0.16479 | 0.20142 | -0.34332 | -0.32959 | -0.11902 | 121.3257 | 121.5912 | 61.3449 | -121.4447 | 121.3531 | 121.3989 | 61.2717 | -121.5317
693.7344 | 121.6644 | -61.1023 | 60.3882 | -0.069885 | 0.0077459 | 0.061239 | 0.06179 | 0.12888 | -0.00067088 | -0.0037661 | -0.00076274 | -0.007071 | 0.056796 | 0.068487 | 0.005048 | -0.0085641 | 60.5759 | 60.5667 | 0.28839 | -61.1481 | 60.2463 | -61.0703 | -60.9695 | -60.8368 | 0.20142 | -61.3861 | 60.2875 | 60.2646 | -60.8917 | -61.0977 | 0.032044 | 0.13275 | -0.14191 | 121.669 | -0.045776 | -0.17853 | 0.18768 | 0.21057 | 0.004578 | -0.10071 | 0.2655 | -0.28381 | -0.28839 | -0.1236 | 121.3486 | 121.6782 | 61.3907 | -121.3577 | 121.3898 | 121.3669 | 61.3037 | -121.4859
695.4219 | 121.788 | -60.965 | 60.4752 | 0.036926 | 0.0053961 | 0.062735 | 0.063927 | 0.12418 | -0.0068659 | -0.0044071 | 0.17471 | -0.010703 | 0.054446 | 0.065497 | 0.00056179 | -0.0042917 | 60.5804 | 60.6262 | 0.32044 | -61.1023 | 60.2646 | -61.0153 | -60.9146 | -60.791 | 0.24261 | -61.2854 | 60.2509 | 60.3012 | -60.8322 | -61.0245 | -0.050354 | 0.050354 | -0.21057 | 121.5912 | -0.13733 | -0.18768 | 0.10529 | 0.13275 | -0.059509 | -0.22431 | 0.17395 | -0.32043 | -0.26093 | -0.17395 | 121.2296 | 121.5454 | 61.2854 | -121.3898 | 121.2158 | 121.2662 | 61.2076 | -121.4996
697.1719 | 121.7514 | -61.0794 | 60.3882 | 0.12848 | 0.0083869 | 0.062948 | 0.064781 | 0.1261 | 0.00082452 | -0.0033389 | 0.1442 | -0.0077118 | 0.056582 | 0.069983 | 0.002698 | -0.0094187 | 60.4843 | 60.4477 | 0.10529 | -61.2396 | 60.2234 | -61.1343 | -61.0336 | -60.8963 | 0.082397 | -61.4548 | 60.2188 | 60.2325 | -60.9192 | -61.1389 | -0.054931 | 0.045777 | -0.1648 | 121.5271 | -0.16022 | -0.20599 | 0.09613 | 0.16022 | -0.059509 | -0.16937 | 0.18311 | -0.37537 | -0.31586 | -0.15564 | 121.3028 | 121.5637 | 61.1847 | -121.4218 | 121.2982 | 121.312 | 61.1618 | -121.5271
698.9219 | 121.6553 | -61.0519 | 60.4706 | -0.1767 | 0.0098821 | 0.062521 | 0.068626 | 0.12695 | -0.0015253 | -0.0054751 | -0.084686 | -0.010916 | 0.059146 | 0.069556 | -7.9008e-05 | -0.0072825 | 60.64 | 60.6216 | 0.36163 | -61.0886 | 60.26 | -60.9879 | -60.9421 | -60.8002 | 0.37994 | -61.3312 | 60.26 | 60.3149 | -60.8185 | -61.0291 | 0.064087 | 0.10986 | -0.21057 | 121.6736 | -0.036621 | -0.14648 | 0.16937 | 0.23346 | 0.022888 | -0.21057 | 0.25177 | -0.27924 | -0.30212 | -0.15564 | 121.312 | 121.6919 | 61.4136 | -121.4127 | 121.312 | 121.3669 | 61.4319 | -121.4996
700.6094 | 121.7377 | -61.116 | 60.3012 | 0.11322 | 0.0058233 | 0.06188 | 0.062218 | 0.12332 | -0.0023797 | -0.0059023 | 0.1976 | -0.0092072 | 0.054873 | 0.066138 | 0.0029116 | -0.0068551 | 60.4843 | 60.4843 | 0.16022 | -61.2488 | 60.0861 | -61.1755 | -61.0657 | -60.878 | 0.19684 | -61.4273 | 60.1273 | 60.1593 | -60.9558 | -61.1389 | -0.059509 | 0.050354 | -0.21515 | 121.6003 | -0.13275 | -0.1831 | 0.18311 | 0.16022 | -0.022888 | -0.17395 | 0.23804 | -0.31128 | -0.28839 | -0.14191 | 121.2021 | 121.6003 | 61.2762 | -121.3669 | 121.2433 | 121.2753 | 61.3129 | -121.4401
702.3906 | 121.788 | -61.1618 | 60.2646 | 0.12085 | 0.0068915 | 0.061453 | 0.063713 | 0.12631 | 0.00039732 | -0.0054751 | 0.18234 | -0.00878 | 0.05466 | 0.068701 | 0.0039798 | -0.0074961 | 60.434 | 60.3561 | -0.022888 | -61.3266 | 60.1044 | -61.203 | -61.1481 | -60.9467 | 0.10986 | -61.5051 | 60.1135 | 60.141 | -60.9787 | -61.2305 | -0.041199 | 0.013733 | -0.16022 | 121.5179 | -0.1648 | -0.17853 | 0.16937 | 0.1831 | -0.068665 | -0.15106 | 0.21515 | -0.34332 | -0.27466 | -0.1236 | 121.2662 | 121.5958 | 61.1389 | -121.4127 | 121.2753 | 121.3028 | 61.2717 | -121.4951
704.0781 | 121.6507 | -61.0886 | 60.3836 | 0.075073 | 0.010737 | 0.062094 | 0.068199 | 0.1261 | 0.00082452 | -0.0041933 | 0.10605 | -0.0092072 | 0.058291 | 0.071051 | 0.0029116 | -0.0077097 | 60.4752 | 60.4019 | -0.064087 | -61.2396 | 60.228 | -61.116 | -61.0519 | -60.9375 | 0.036621 | -61.5143 | 60.2097 | 60.2325 | -60.9467 | -61.1847 | -0.027466 | 0.036621 | -0.15564 | 121.4905 | -0.15106 | -0.18768 | 0.091553 | 0.14191 | -0.09613 | -0.17395 | 0.15106 | -0.42572 | -0.32959 | -0.15106 | 121.3165 | 121.5637 | 61.0245 | -121.4355 | 121.2982 | 121.3211 | 61.1252 | -121.5683
705.8125 | 121.6736 | -61.0657 | 60.4156 | 0.075073 | 0.0088141 | 0.06188 | 0.059227 | 0.12396 | 0.0014655 | -0.0026981 | 0.13657 | -0.0083526 | 0.054233 | 0.068915 | 0.0039798 | -0.0066415 | 60.4889 | 60.4431 | -0.11444 | -61.2167 | 60.2463 | -61.084 | -61.0245 | -60.878 | 0.027466 | -61.4548 | 60.2554 | 60.2875 | -60.8871 | -61.1298 | -0.01831 | 0.041199 | -0.16937 | 121.5088 | -0.15106 | -0.19226 | 0.073243 | 0.17853 | -0.064087 | -0.16022 | 0.18768 | -0.3891 | -0.32501 | -0.12817 | 121.312 | 121.5546 | 60.9512 | -121.4401 | 121.3211 | 121.3531 | 61.0931 | -121.5454
707.5625 | 121.6507 | -60.8826 | 60.6308 | -0.22247 | 0.0079595 | 0.063589 | 0.065849 | 0.12674 | -0.0047297 | -0.0067569 | -0.077057 | -0.011771 | 0.055087 | 0.065283 | 0.00077539 | -0.0047189 | 60.7819 | 60.8002 | 0.14191 | -60.9329 | 60.434 | -60.8643 | -60.7773 | -60.6216 | 0.35706 | -61.171 | 60.4797 | 60.4706 | -60.6903 | -60.8963 | 0.01831 | 0.10529 | -0.19684 | 121.6827 | -0.050354 | -0.15564 | 0.15106 | 0.19226 | -0.013733 | -0.15106 | 0.26093 | -0.28839 | -0.27466 | -0.16022 | 121.3165 | 121.6644 | 61.0245 | -121.4081 | 121.3623 | 121.3531 | 61.2396 | -121.5271
709.25 | 121.7651 | -60.7452 | 60.6308 | 0.097962 | 0.0073187 | 0.064016 | 0.062859 | 0.12674 | -0.0062249 | -0.0052615 | 0.18234 | -0.01348 | 0.056155 | 0.066779 | 0.0012028 | -0.0062143 | 60.759 | 60.7773 | 0.022888 | -60.9421 | 60.3928 | -60.8551 | -60.8002 | -60.5942 | 0.21973 | -61.1298 | 60.4065 | 60.4568 | -60.6674 | -60.9009 | -0.10986 | -0.054932 | -0.23804 | 121.5225 | -0.19684 | -0.14191 | 0.12817 | 0.07782 | -0.15564 | -0.2243 | 0.15106 | -0.38452 | -0.22888 | -0.17395 | 121.138 | 121.5042 | 60.7681 | -121.431 | 121.1517 | 121.2021 | 60.965 | -121.5317
711 | 121.6827 | -6.7383 | 114.917 | 0.036926 | 0.0088141 | 0.065298 | 0.063286 | 0.12247 | -0.0053705 | 0.019732 | 0.26627 | -0.011771 | 0.056796 | 0.067206 | 0.0018436 | -0.0055735 | 114.949 | 114.9261 | 0.79651 | -6.6971 | 114.6652 | -6.5781 | -6.6055 | -6.6055 | 1.1032 | -6.8161 | 114.6698 | 114.679 | -6.601 | -6.6559 | 0.16022 | 0.13275 | -0.25177 | 121.6644 | 0.041198 | -0.091553 | 0.032044 | 0.13733 | 0.082397 | -0.24719 | 0.13275 | -0.07782 | -0.16022 | -0.23804 | 121.4035 | 121.6873 | 7.5348 | -121.5225 | 121.4081 | 121.4172 | 7.8415 | -121.5729
712.7656 | 121.6141 | -5.603 | 116.1209 | -0.12329 | 0.01031 | 0.062521 | 0.065849 | 0.12802 | -0.0028071 | 0.02016 | 0.014496 | -0.010916 | 0.056796 | 0.067206 | -0.001788 | -0.0092051 | 116.1667 | 116.1255 | 0.94757 | -5.484 | 115.7822 | -5.4337 | -5.4749 | -5.4245 | 1.2131 | -5.603 | 115.7959 | 115.8234 | -5.4565 | -5.5069 | 0.16937 | 0.12817 | -0.33875 | 121.7285 | 0.11902 | -0.009155 | 0.045776 | 0.14648 | 0.09613 | -0.32501 | 0.17853 | 0 | -0.09613 | -0.29755 | 121.3852 | 121.7697 | 6.5506 | -121.5958 | 121.3989 | 121.4264 | 6.8161 | -121.6278
714.4688 | 121.6553 | -5.0079 | 116.6702 | -0.1767 | 0.0098821 | 0.061666 | 0.06414 | 0.12781 | -0.00045708 | 0.02315 | -0.12283 | -0.0085662 | 0.054233 | 0.070196 | 0.0024844 | -0.0098459 | 116.6885 | 116.6061 | 0.82855 | -4.9576 | 116.4551 | -4.8614 | -4.9484 | -4.9118 | 1.0986 | -5.1041 | 116.4505 | 116.478 | -4.866 | -4.9255 | 0.14649 | 0.05951 | -0.21515 | 121.6141 | 0.050354 | -0.009156 | 0.018311 | 0.14191 | 0.082398 | -0.21973 | 0.096131 | -0.09613 | -0.17853 | -0.19226 | 121.463 | 121.6965 | 5.8365 | -121.6187 | 121.4584 | 121.4859 | 6.1066 | -121.5958
716.2344 | 121.7422 | -4.9438 | 116.6565 | -0.039368 | 0.0075323 | 0.062521 | 0.063499 | 0.12674 | -0.0051569 | 0.022723 | -0.00076274 | -0.011771 | 0.056155 | 0.066992 | 0.00034819 | -0.0057871 | 116.7343 | 116.7252 | 0.87433 | -4.9026 | 116.4185 | -4.8294 | -4.8569 | -4.7882 | 1.0941 | -4.9667 | 116.3956 | 116.423 | -4.8431 | -4.8981 | 0.11444 | 0.086975 | -0.23804 | 121.669 | 0.041199 | -0.045776 | 0.07782 | 0.10071 | 0.045777 | -0.26093 | 0.15564 | -0.022888 | -0.068665 | -0.23346 | 121.3623 | 121.6782 | 5.8182 | -121.5134 | 121.3394 | 121.3669 | 6.0379 | -121.5546
717.9844 | 121.7422 | -5.2597 | 116.3406 | 0.159 | 0.0071051 | 0.063803 | 0.057732 | 0.12524 | 0.0014655 | 0.026141 | 0.12894 | -0.01113 | 0.052951 | 0.065924 | 0.0052616 | -0.0070689 | 116.4093 | 116.3086 | 0.72327 | -5.2597 | 116.1072 | -5.1727 | -5.191 | -5.1086 | 0.90179 | -5.3513 | 116.1118 | 116.1072 | -5.1636 | -5.2185 | 0.086976 | 0.068665 | -0.23346 | 121.5683 | 0 | -0.068665 | 0.068665 | 0.096131 | 0.041199 | -0.22888 | 0.15106 | -0.091552 | -0.13275 | -0.23346 | 121.3669 | 121.669 | 5.983 | -121.5317 | 121.3715 | 121.3669 | 6.1615 | -121.5591
719.6719 | 121.6324 | -4.2618 | 117.4438 | -0.20721 | 0.0079595 | 0.063375 | 0.068626 | 0.12802 | -0.0025935 | 0.021869 | -0.16861 | -0.01113 | 0.053378 | 0.067633 | 0.0012028 | -0.0081369 | 117.4713 | 117.4393 | 0.96588 | -4.1656 | 117.1326 | -4.129 | -4.1885 | -4.1428 | 1.0529 | -4.2984 | 117.1921 | 117.2058 | -4.1336 | -4.184 | 0.13275 | 0.073242 | -0.31128 | 121.701 | 0.096131 | 0.022889 | 0.027465 | 0.12817 | 0.07782 | -0.25177 | 0.11902 | -0.036621 | -0.11444 | -0.23804 | 121.3943 | 121.7331 | 5.2277 | -121.6324 | 121.4539 | 121.4676 | 5.3146 | -121.6278
721.4375 | 121.6644 | -4.3854 | 117.2562 | -0.16907 | 0.01031 | 0.065298 | 0.060722 | 0.12888 | 0.0012519 | 0.023791 | -0.18387 | -0.0094208 | 0.056155 | 0.067633 | 0.0022708 | -0.0092051 | 117.2607 | 117.1692 | 0.97046 | -4.3716 | 117.0273 | -4.3076 | -4.3671 | -4.3259 | 1.0574 | -4.5136 | 117.009 | 117.0364 | -4.2892 | -4.3533 | 0.07782 | 0.018311 | -0.22888 | 121.5546 | 0.013733 | -0.004578 | 0.004577 | 0.09613 | 0.032043 | -0.24719 | 0.059509 | -0.12817 | -0.16022 | -0.21973 | 121.4127 | 121.6461 | 5.3558 | -121.6232 | 121.3943 | 121.4218 | 5.4428 | -121.6095
723.1875 | 121.7422 | -4.0329 | 117.5491 | 0.036926 | 0.0071051 | 0.064016 | 0.064354 | 0.12759 | -0.0055841 | 0.022937 | 0.060272 | -0.012198 | 0.056796 | 0.067419 | 0.00077539 | -0.0060007 | 117.6132 | 117.5949 | 1.149 | -3.978 | 117.3386 | -3.9322 | -3.9734 | -3.9185 | 1.0803 | -4.0695 | 117.3386 | 117.3615 | -3.9322 | -3.9917 | 0.10071 | 0.059509 | -0.21057 | 121.6278 | 0.054932 | -0.004577 | 0.064087 | 0.10071 | 0.041199 | -0.21057 | 0.11444 | -0.036621 | -0.07782 | -0.18768 | 121.3715 | 121.6461 | 5.1819 | -121.5225 | 121.3715 | 121.3943 | 5.1132 | -121.5408
724.9375 | 121.6415 | -4.747 | 116.9128 | -0.11566 | 0.0094549 | 0.062094 | 0.066277 | 0.12695 | -0.0023797 | 0.022723 | -0.1915 | -0.0092072 | 0.056582 | 0.06806 | 0.00056179 | -0.0089915 | 116.8991 | 116.8533 | 1.6205 | -4.7424 | 116.6702 | -4.6509 | -4.7241 | -4.6829 | 1.181 | -4.8706 | 116.6565 | 116.6748 | -4.6829 | -4.7287 | 0.09613 | 0.022888 | -0.24262 | 121.6003 | 0.004577 | -0.018311 | -0.013733 | 0.064087 | 0.01831 | -0.25635 | 0.064087 | -0.1236 | -0.14191 | -0.23804 | 121.4172 | 121.6461 | 6.3675 | -121.637 | 121.4035 | 121.4218 | 5.928 | -121.6415
726.6875 | 121.7102 | -4.6326 | 116.9769 | -0.12329 | 0.0096685 | 0.064657 | 0.06649 | 0.12418 | -0.0049433 | 0.021014 | -0.18387 | -0.010703 | 0.056369 | 0.065497 | 0.00056179 | -0.0064279 | 117.0959 | 117.1005 | 1.9592 | -4.5319 | 116.7618 | -4.5319 | -4.5593 | -4.4495 | 1.1536 | -4.6783 | 116.6885 | 116.7389 | -4.541 | -4.5914 | 0.10071 | 0.073242 | -0.21515 | 121.7331 | 0.10071 | 0.027466 | 0.11902 | 0.091552 | 0.041198 | -0.28839 | 0.18311 | -0.045777 | -0.086975 | -0.23804 | 121.3943 | 121.7285 | 6.5918 | -121.5363 | 121.3211 | 121.3715 | 5.7861 | -121.5683
728.375 | 121.6461 | -4.7287 | 116.9083 | -0.19196 | 0.01031 | 0.065298 | 0.062431 | 0.12781 | -0.0021661 | 0.022509 | -0.17624 | -0.011343 | 0.057864 | 0.068701 | 0.0022708 | -0.0066415 | 117.0593 | 117.009 | 1.8448 | -4.5639 | 116.7618 | -4.5364 | -4.5456 | -4.5685 | 1.0529 | -4.7653 | 116.7252 | 116.7526 | -4.5593 | -4.6188 | 0.19226 | 0.18311 | -0.14648 | 121.7377 | 0.16479 | -0.018311 | 0.15106 | 0.16937 | 0.10986 | -0.1831 | 0.16022 | -0.036621 | -0.14649 | -0.15564 | 121.4905 | 121.788 | 6.5735 | -121.4539 | 121.4539 | 121.4813 | 5.7816 | -121.5271
730.125 | 121.6461 | -4.2068 | 117.4438 | -0.069885 | 0.01031 | 0.062735 | 0.063072 | 0.12717 | 0.0029607 | 0.024005 | -0.13809 | -0.008139 | 0.056155 | 0.067847 | 0.0046206 | -0.010487 | 117.5171 | 117.4438 | 1.7899 | -4.1245 | 117.2516 | -4.1061 | -4.1428 | -4.0604 | 1.0666 | -4.2801 | 117.2195 | 117.2241 | -4.0833 | -4.1519 | 0.10071 | 0.064087 | -0.19226 | 121.6507 | 0.082397 | 0.01831 | 0.073242 | 0.1236 | 0.054931 | -0.22431 | 0.14648 | -0.073242 | -0.12817 | -0.21973 | 121.4584 | 121.7239 | 5.9967 | -121.5866 | 121.4264 | 121.431 | 5.2734 | -121.5958
731.8125 | 121.7194 | -4.4586 | 117.1051 | 0.18951 | 0.0090277 | 0.064444 | 0.062859 | 0.1246 | -0.0021661 | 0.024218 | 0.1442 | -0.011557 | 0.057651 | 0.066779 | 0.00163 | -0.0087777 | 117.215 | 117.1921 | 1.7807 | -4.3945 | 116.8854 | -4.3579 | -4.39 | -4.303 | 1.0849 | -4.4952 | 116.8671 | 116.8762 | -4.3762 | -4.4266 | 0.10071 | 0.068664 | -0.21973 | 121.6507 | 0.064087 | -0.004577 | 0.10986 | 0.082397 | 0.032043 | -0.23804 | 0.15564 | -0.036621 | -0.068664 | -0.22888 | 121.344 | 121.6736 | 6.2393 | -121.4951 | 121.3257 | 121.3348 | 5.5435 | -121.5317
733.5625 | 121.6965 | -4.5181 | 117.1143 | -0.16144 | 0.012232 | 0.060598 | 0.064781 | 0.12503 | 0.0014655 | 0.026568 | -0.17624 | -0.0083526 | 0.056155 | 0.06806 | 0.002698 | -0.0087777 | 117.1738 | 117.1005 | 1.8448 | -4.4586 | 116.9266 | -4.4128 | -4.4586 | -4.3945 | 1.1856 | -4.6005 | 116.9037 | 116.9449 | -4.39 | -4.4678 | 0.10528 | 0.059509 | -0.18768 | 121.6187 | 0.059509 | 0 | 0.059509 | 0.12817 | 0.050354 | -0.21057 | 0.1236 | -0.082398 | -0.13275 | -0.16937 | 121.4447 | 121.6919 | 6.3629 | -121.5729 | 121.4218 | 121.463 | 5.7037 | -121.582
735.2969 | 121.6965 | -4.2252 | 117.3981 | -0.1004 | 0.010523 | 0.062521 | 0.065208 | 0.12759 | 0.00082452 | 0.025073 | -0.13046 | -0.009848 | 0.05701 | 0.068487 | 0.0029116 | -0.0079233 | 117.4622 | 117.3935 | 1.6983 | -4.1702 | 117.1738 | -4.129 | -4.2068 | -4.1199 | 1.2131 | -4.3167 | 117.1646 | 117.2058 | -4.1336 | -4.2068 | 0.096131 | 0.018311 | -0.2243 | 121.6187 | 0.054932 | 0.036621 | 0.064087 | 0.091553 | 0.018311 | -0.23346 | 0.10529 | -0.091552 | -0.10986 | -0.19226 | 121.3989 | 121.6873 | 5.9235 | -121.6049 | 121.3898 | 121.431 | 5.4382 | -121.6049
737.0469 | 121.8887 | -58.8135 | 62.4115 | -0.024109 | 0.0066779 | 0.062948 | 0.063286 | 0.12631 | -0.0070795 | -0.0041933 | -0.12283 | -0.011771 | 0.057223 | 0.069342 | -0.00050621 | -0.0057871 | 62.4481 | 62.471 | -1.2405 | -59.0057 | 62.3932 | -58.6761 | -58.1955 | -58.7128 | -0.737 | -59.2896 | 62.4161 | 62.4481 | -58.6212 | -58.7585 | 0.13733 | 0.61798 | -0.018311 | 121.2845 | -0.19226 | -0.81024 | 0.036621 | 0.19226 | 0.054932 | 0.004578 | 0.10071 | -0.47607 | -0.53101 | 0.036621 | 121.2067 | 121.2616 | 57.5729 | -120.607 | 121.2296 | 121.2616 | 58.0765 | -121.17
738.8125 | 121.7239 | -5.0812 | 116.5558 | 0.14374 | 0.0081733 | 0.061666 | 0.059227 | 0.12589 | 0.0012519 | 0.024005 | 0.22812 | -0.010275 | 0.056369 | 0.069769 | 0.0018436 | -0.0074961 | 116.6565 | 116.629 | 1.4557 | -4.9667 | 116.3361 | -4.9026 | -4.9713 | -4.8752 | 1.1993 | -5.0674 | 116.3177 | 116.3132 | -4.921 | -4.985 | 0.17853 | 0.10986 | -0.21973 | 121.7102 | 0.11444 | 0.004577 | 0.10071 | 0.16022 | 0.096131 | -0.23804 | 0.20599 | 0.013733 | -0.082398 | -0.24262 | 121.4172 | 121.7377 | 6.5369 | -121.5271 | 121.3989 | 121.3943 | 6.2805 | -121.5408
740.5 | 121.7148 | -59.2804 | 62.1231 | -0.13855 | 0.0086005 | 0.063589 | 0.066277 | 0.1261 | -0.0025935 | -0.0035525 | -0.26779 | -0.0083526 | 0.054873 | 0.067419 | 0.00013459 | -0.0068551 | 62.233 | 62.2284 | -0.054932 | -59.4543 | 61.9858 | -59.4131 | -59.3216 | -59.0973 | 0.28839 | -59.6741 | 62.0316 | 62.027 | -59.1614 | -59.3719 | -0.13275 | -0.041198 | -0.13733 | 121.5088 | -0.17395 | -0.13275 | 0.10986 | 0.11902 | -0.091552 | -0.091553 | 0.18311 | -0.39368 | -0.30212 | -0.09613 | 121.2662 | 121.5134 | 59.2255 | -121.4447 | 121.312 | 121.3074 | 59.5688 | -121.4951
742.25 | 121.7972 | -58.4518 | 62.9059 | 0.097962 | 0.0077459 | 0.059958 | 0.060082 | 0.12439 | 0.0021063 | -0.00098912 | 0.075531 | -0.0085662 | 0.055942 | 0.069556 | 0.0031254 | -0.0055735 | 63.0478 | 62.9974 | -0.018311 | -58.6945 | 62.7777 | -58.6212 | -58.5434 | -58.3466 | -0.013733 | -58.9096 | 62.7457 | 62.7731 | -58.3923 | -58.6121 | -0.16937 | -0.091553 | -0.12817 | 121.4493 | -0.24262 | -0.15106 | 0.14191 | 0.059509 | -0.16022 | -0.16022 | 0.10528 | -0.45776 | -0.29755 | -0.13275 | 121.2296 | 121.4996 | 58.4335 | -121.4493 | 121.1975 | 121.225 | 58.4381 | -121.5179
744 | 121.8063 | -57.8796 | 63.5284 | -0.085144 | 0.0073187 | 0.062948 | 0.064354 | 0.12866 | -0.0047297 | -0.0026981 | -0.046539 | -0.010489 | 0.058078 | 0.068915 | -0.001788 | -0.0064279 | 63.7619 | 63.7939 | 0.35706 | -57.962 | 63.3408 | -57.9208 | -57.8613 | -57.6462 | 0.33417 | -58.1406 | 63.3636 | 63.3591 | -57.7194 | -57.9391 | -0.041198 | 0.018311 | -0.18768 | 121.6736 | -0.082397 | -0.10071 | 0.23346 | 0.16022 | -0.059509 | -0.16479 | 0.23346 | -0.26093 | -0.20142 | -0.16937 | 121.2204 | 121.6415 | 58.2367 | -121.3898 | 121.2433 | 121.2387 | 58.2138 | -121.4676
745.6875 | 121.8292 | -57.399 | 64.0228 | 0.0064086 | 0.0045417 | 0.066153 | 0.063286 | 0.12631 | -0.0051569 | -0.0050479 | 0.060272 | -0.012198 | 0.055301 | 0.065283 | 0.00056179 | -0.0079233 | 64.1647 | 64.2151 | 0.29755 | -57.5363 | 63.8351 | -57.431 | -57.3944 | -57.1884 | 0.22888 | -57.6645 | 63.8672 | 63.858 | -57.225 | -57.431 | -0.032043 | 0.004578 | -0.18768 | 121.6141 | -0.13733 | -0.14191 | 0.14191 | 0.17395 | -0.032043 | -0.15564 | 0.21057 | -0.2655 | -0.23346 | -0.1648 | 121.2341 | 121.5637 | 57.6965 | -121.4172 | 121.2662 | 121.257 | 57.6279 | -121.4539
747.4219 | 121.1014 | -7.0496 | 114.7018 | -0.20721 | 0.0086005 | 0.063162 | 0.064354 | 0.12354 | -0.00024348 | 0.021655 | -0.092316 | -0.010703 | 0.057651 | 0.066138 | 0.00056179 | -0.0094187 | 114.6469 | 114.6286 | 2.2568 | -6.9901 | 114.418 | -6.871 | -6.9397 | -6.9351 | 1.6479 | -7.1457 | 114.418 | 114.4318 | -6.8802 | -6.9397 | 0.17853 | 0.10986 | -0.28381 | 121.6782 | 0.05951 | -0.050354 | -0.054931 | 0.16937 | 0.10986 | -0.28381 | 0.11444 | -0.09613 | -0.20599 | -0.27008 | 121.4676 | 121.6965 | 9.3063 | -121.6415 | 121.4676 | 121.4813 | 8.6975 | -121.6415
749.1719 | 121.6232 | -5.3833 | 116.3498 | -0.13092 | 0.0073187 | 0.062948 | 0.063286 | 0.12546 | -0.0025935 | 0.021655 | 0.022125 | -0.01113 | 0.055301 | 0.068274 | 0.002698 | -0.0087777 | 116.3818 | 116.3956 | 2.4124 | -5.246 | 116.0614 | -5.1865 | -5.2277 | -5.1636 | 1.4832 | -5.3558 | 116.0797 | 116.0843 | -5.1773 | -5.2414 | 0.19684 | 0.15564 | -0.28839 | 121.7789 | 0.13733 | -0.018311 | 0.032044 | 0.20599 | 0.14191 | -0.27008 | 0.21973 | 0.027466 | -0.11444 | -0.2655 | 121.4447 | 121.7651 | 7.7957 | -121.5775 | 121.463 | 121.4676 | 6.8665 | -121.5912
750.9219 | 121.7239 | -5.127 | 116.5009 | 0.14374 | 0.0096685 | 0.062094 | 0.057732 | 0.12653 | 0.0012519 | 0.024218 | 0.20523 | -0.010062 | 0.056796 | 0.065924 | 0.004407 | -0.0087777 | 116.5237 | 116.4551 | 2.179 | -5.1315 | 116.2811 | -5.04 | -5.0903 | -4.9942 | 1.0712 | -5.2139 | 116.2354 | 116.2262 | -5.0079 | -5.072 | 0.086975 | 0.036621 | -0.21973 | 121.582 | -0.004578 | -0.041199 | 0.022889 | 0.11902 | 0.054932 | -0.2655 | 0.13275 | -0.086975 | -0.14191 | -0.27466 | 121.4081 | 121.6507 | 7.3059 | -121.5912 | 121.3623 | 121.3531 | 6.1981 | -121.5729
752.625 | 121.6324 | -4.9484 | 116.7709 | -0.19958 | 0.0094549 | 0.065725 | 0.064354 | 0.12695 | -0.0036615 | 0.022937 | -0.061798 | -0.0089936 | 0.054233 | 0.066992 | 0.003339 | -0.0092051 | 116.7709 | 116.7389 | 2.3621 | -4.8569 | 116.4963 | -4.7882 | -4.866 | -4.834 | 1.2314 | -5.0125 | 116.5009 | 116.51 | -4.8157 | -4.866 | 0.16022 | 0.082397 | -0.27466 | 121.6873 | 0.091552 | 0.009155 | 0 | 0.13275 | 0.082397 | -0.27008 | 0.11444 | -0.064087 | -0.14648 | -0.26093 | 121.4447 | 121.7194 | 7.3105 | -121.637 | 121.4493 | 121.4584 | 6.1798 | -121.637
754.3594 | 121.6278 | -4.9393 | 116.7389 | 0.052185 | 0.055811 | 0.061026 | 0.018639 | 0.12631 | 0.0025335 | 0.026782 | 0.037384 | -0.0072846 | 0.056582 | 0.069342 | 0.0037662 | -0.0064279 | 116.716 | 116.6428 | 2.3026 | -4.9118 | 116.5192 | -4.8248 | -4.8798 | -4.8752 | 1.0757 | -5.0903 | 116.5009 | 116.5329 | -4.8157 | -4.866 | 0.11444 | 0.059509 | -0.21973 | 121.582 | 0.027466 | -0.032043 | -0.022889 | 0.1236 | 0.073242 | -0.23804 | 0.064087 | -0.15106 | -0.2243 | -0.20599 | 121.4584 | 121.6553 | 7.2418 | -121.6187 | 121.4401 | 121.4722 | 6.015 | -121.6049
756.0938 | 121.7514 | -4.6097 | 116.9678 | 0.17426 | 0.053889 | 0.062521 | 0.017143 | 0.12589 | -0.0021661 | 0.026141 | 0.15945 | -0.0096344 | 0.055514 | 0.067633 | 0.0035526 | -0.0087777 | 117.041 | 116.9952 | 3.0579 | -4.6051 | 116.7572 | -4.5273 | -4.5822 | -4.4907 | 1.062 | -4.6967 | 116.7297 | 116.8076 | -4.5136 | -4.5822 | 0.082397 | 0.027466 | -0.21057 | 121.6049 | 0.004577 | -0.022889 | 0.073243 | 0.09613 | 0.027466 | -0.23804 | 0.11902 | -0.086975 | -0.11444 | -0.16022 | 121.3669 | 121.6507 | 7.6675 | -121.55 | 121.3394 | 121.4172 | 5.6717 | -121.55
757.7812 | 121.6965 | -4.8248 | 116.8121 | 0.10559 | 0.051752 | 0.061453 | 0.019066 | 0.12375 | 0.0012519 | 0.023364 | 0.11368 | -0.010275 | 0.058505 | 0.069128 | 0.002698 | -0.0085641 | 116.9357 | 116.8625 | 3.3829 | -4.6875 | 116.7343 | -4.6005 | -4.6463 | -4.6371 | 0.97046 | -4.8523 | 116.7206 | 116.7526 | -4.5868 | -4.6646 | 0.2243 | 0.17853 | -0.07782 | 121.6873 | 0.13733 | -0.041199 | 0.1236 | 0.23804 | 0.16022 | -0.091553 | 0.18768 | -0.027466 | -0.18768 | -0.059509 | 121.5591 | 121.7606 | 8.2077 | -121.4584 | 121.5454 | 121.5775 | 5.7953 | -121.4767
759.5312 | 121.7697 | -4.8294 | 116.7526 | 0.16663 | 0.053034 | 0.063162 | 0.016502 | 0.12354 | -0.00067088 | 0.022937 | 0.08316 | -0.010916 | 0.055514 | 0.066351 | 0.0031254 | -0.0070689 | 116.835 | 116.803 | 4.3076 | -4.7882 | 116.5512 | -4.7195 | -4.8065 | -4.6967 | 1.03 | -4.8981 | 116.5237 | 116.5375 | -4.7241 | -4.7836 | 0.10986 | 0.022888 | -0.20142 | 121.6324 | 0.041199 | 0.018311 | 0.082397 | 0.10529 | 0.045777 | -0.22888 | 0.13275 | -0.068664 | -0.11444 | -0.21515 | 121.3806 | 121.6644 | 9.137 | -121.5591 | 121.3531 | 121.3669 | 5.8594 | -121.5363
761.2188 | 121.637 | -5.8182 | 115.8417 | 0.12848 | 0.053461 | 0.062521 | 0.018211 | 0.12503 | 0.0010381 | 0.02315 | 0.08316 | -0.0079254 | 0.055514 | 0.066138 | 0.005048 | -0.0070689 | 115.8646 | 115.7776 | 4.3259 | -5.777 | 115.6448 | -5.6808 | -5.722 | -5.7037 | 0.97046 | -5.9235 | 115.6403 | 115.6769 | -5.6717 | -5.722 | 0.13733 | 0.09613 | -0.19684 | 121.5958 | 0.041198 | -0.054932 | 0.022888 | 0.14648 | 0.09613 | -0.20142 | 0.11444 | -0.10529 | -0.20142 | -0.16479 | 121.463 | 121.6827 | 10.144 | -121.5637 | 121.4584 | 121.4951 | 6.7886 | -121.5637
762.9844 | 121.5912 | -5.3055 | 116.3956 | -0.054626 | 0.054743 | 0.061026 | 0.01992 | 0.12524 | 0.00082452 | 0.024218 | -0.054169 | -0.0079254 | 0.056155 | 0.066992 | 0.002698 | -0.0070689 | 116.3864 | 116.304 | 4.509 | -5.2826 | 116.0706 | -5.2185 | -5.278 | -5.2322 | 1.0529 | -5.4291 | 116.0934 | 116.1209 | -5.2185 | -5.278 | 0.086975 | 0.027466 | -0.32501 | 121.6095 | 0.022888 | -0.004578 | -0.009155 | 0.086975 | 0.027466 | -0.30212 | 0.073242 | -0.1236 | -0.15106 | -0.27466 | 121.376 | 121.6919 | 9.8145 | -121.6736 | 121.3989 | 121.4264 | 6.3583 | -121.6736
764.6719 | 121.6095 | -5.0079 | 116.7114 | -0.19958 | 0.052393 | 0.065084 | 0.021202 | 0.12738 | -0.0057977 | 0.022509 | -0.14572 | -0.0092072 | 0.058719 | 0.066138 | -0.00071981 | -0.0092051 | 116.7068 | 116.6931 | 4.6875 | -4.9164 | 116.423 | -4.8706 | -4.9118 | -4.8935 | 1.3092 | -5.0491 | 116.4322 | 116.478 | -4.8798 | -4.9164 | 0.13733 | 0.096131 | -0.28839 | 121.7011 | 0.091553 | -0.004578 | -0.004578 | 0.12817 | 0.091553 | -0.27924 | 0.11444 | -0.041198 | -0.13275 | -0.23346 | 121.431 | 121.7148 | 9.6954 | -121.6232 | 121.4401 | 121.4859 | 6.3171 | -121.6278
766.4219 | 121.7194 | -8.6792 | 112.9349 | 0.17426 | 0.053461 | 0.062094 | 0.01928 | 0.12653 | -0.0040887 | 0.019946 | 0.15945 | -0.010916 | 0.056155 | 0.067847 | -7.9008e-05 | -0.0062143 | 113.0173 | 112.9807 | 4.8614 | -8.6792 | 112.6877 | -8.5648 | -8.606 | -8.5464 | 1.1032 | -8.7799 | 112.6602 | 112.706 | -8.5464 | -8.6197 | 0.11444 | 0.073242 | -0.24719 | 121.6599 | 0 | -0.073242 | 0.082398 | 0.13275 | 0.059509 | -0.27466 | 0.13275 | -0.10071 | -0.16022 | -0.22888 | 121.3669 | 121.6965 | 13.5406 | -121.5408 | 121.3394 | 121.3852 | 9.7824 | -121.5546
768.1719 | 121.669 | -6.9305 | 114.7339 | -0.20721 | 0.05517 | 0.064871 | 0.018425 | 0.12589 | -0.00088448 | 0.022723 | -0.19913 | -0.010916 | 0.057651 | 0.06806 | 0.0014164 | -0.0089915 | 114.6881 | 114.6286 | 4.9393 | -6.9397 | 114.4913 | -6.8436 | -6.8848 | -6.9077 | 1.4053 | -7.1182 | 114.5233 | 114.5325 | -6.8436 | -6.8893 | 0.086975 | 0.045776 | -0.24262 | 121.5591 | -0.009155 | -0.054931 | -0.045777 | 0.086975 | 0.041199 | -0.21057 | 0.022888 | -0.18768 | -0.22888 | -0.20142 | 121.4218 | 121.6187 | 11.8698 | -121.6187 | 121.4539 | 121.463 | 8.3359 | -121.6232
769.9219 | 121.669 | -6.6742 | 114.9673 | 0.075073 | 0.051539 | 0.063803 | 0.017143 | 0.12311 | -0.00024348 | 0.023577 | 0.060272 | -0.009848 | 0.057651 | 0.068915 | 0.0037662 | -0.0079233 | 114.949 | 114.8712 | 3.8864 | -6.6925 | 114.7705 | -6.5598 | -6.6101 | -6.6147 | 1.4145 | -6.8436 | 114.7614 | 114.7842 | -6.5689 | -6.6101 | 0.11444 | 0.064087 | -0.19684 | 121.5454 | -0.018311 | -0.082398 | -0.01831 | 0.10529 | 0.064087 | -0.20599 | 0.059509 | -0.16937 | -0.23346 | -0.18311 | 121.4447 | 121.6232 | 10.5606 | -121.5775 | 121.4355 | 121.4584 | 8.0887 | -121.5775
771.625 | 121.701 | -6.4682 | 115.1276 | 0.097962 | 0.051752 | 0.062307 | 0.020561 | 0.1246 | -0.0049433 | 0.023364 | 0.12131 | -0.010916 | 0.058719 | 0.065924 | -0.0030698 | -0.0060007 | 115.1825 | 115.1596 | 3.8681 | -6.459 | 114.8758 | -6.3492 | -6.427 | -6.395 | 1.6434 | -6.5735 | 114.8438 | 114.9124 | -6.3721 | -6.4453 | 0.11902 | 0.041199 | -0.25177 | 121.6278 | 0.009156 | -0.032043 | 0.054932 | 0.096131 | 0.022889 | -0.28381 | 0.073243 | -0.10529 | -0.12817 | -0.21515 | 121.344 | 121.6507 | 10.3363 | -121.5546 | 121.312 | 121.3806 | 8.1116 | -121.5729
773.3906 | 121.7514 | -6.1707 | 115.3839 | 0.17426 | 0.053889 | 0.064016 | 0.019066 | 0.12631 | -0.00067088 | 0.024005 | 0.13657 | -0.0083526 | 0.055514 | 0.069342 | 0.0022708 | -0.0098459 | 115.4755 | 115.3931 | 4.0146 | -6.189 | 115.2008 | -6.0883 | -6.134 | -6.0654 | 1.6983 | -6.2714 | 115.1916 | 115.1825 | -6.0928 | -6.1249 | 0.082397 | 0.036621 | -0.1831 | 121.5637 | -0.018311 | -0.054932 | 0.091553 | 0.07782 | 0.045776 | -0.19226 | 0.10529 | -0.10071 | -0.14648 | -0.20142 | 121.3715 | 121.6461 | 10.1852 | -121.5179 | 121.3623 | 121.3531 | 7.869 | -121.5088
775.1406 | 121.7514 | -5.777 | 115.8005 | 0.044556 | 0.052821 | 0.062735 | 0.020561 | 0.12482 | -0.0051569 | 0.02016 | 0.067902 | -0.011343 | 0.056796 | 0.067419 | -0.0022152 | -0.0057871 | 115.8417 | 115.8142 | 4.7974 | -5.7587 | 115.567 | -5.6854 | -5.7404 | -5.7175 | 1.9409 | -5.8868 | 115.5624 | 115.5945 | -5.6763 | -5.7266 | 0.091553 | 0.036622 | -0.23346 | 121.5912 | 0.018311 | -0.018311 | 0.041199 | 0.10071 | 0.050354 | -0.23804 | 0.05951 | -0.10986 | -0.16022 | -0.20599 | 121.344 | 121.6187 | 10.5743 | -121.5408 | 121.3394 | 121.3715 | 7.7179 | -121.5271
776.8438 | 121.7194 | -6.0425 | 115.5441 | 0.16663 | 0.05453 | 0.063162 | 0.017998 | 0.1246 | -0.00088448 | 0.021869 | 0.15182 | -0.0092072 | 0.056369 | 0.067847 | 0.0020572 | -0.0074961 | 115.6815 | 115.6357 | 4.6738 | -5.9692 | 115.2969 | -5.896 | -5.9463 | -5.8594 | 2.092 | -6.0699 | 115.3198 | 115.3152 | -5.9143 | -5.9601 | 0.14648 | 0.09613 | -0.24719 | 121.6782 | 0.073242 | -0.022888 | 0.13733 | 0.12817 | 0.082397 | -0.2243 | 0.18311 | -0.027466 | -0.10986 | -0.22888 | 121.3394 | 121.7239 | 10.7162 | -121.4905 | 121.3623 | 121.3577 | 8.1345 | -121.5042
778.5938 | 121.6599 | -5.9921 | 115.6677 | -0.13855 | 0.053248 | 0.063375 | 0.018852 | 0.12824 | -0.0043023 | 0.022937 | -0.13046 | -0.010916 | 0.056155 | 0.066779 | 0.00056179 | -0.010059 | 115.7272 | 115.7181 | 4.5731 | -5.9143 | 115.3885 | -5.8685 | -5.9143 | -5.8456 | 2.4811 | -6.0379 | 115.3793 | 115.4022 | -5.864 | -5.9189 | 0.1236 | 0.077819 | -0.27924 | 121.7102 | 0.077819 | 0 | 0.059509 | 0.12817 | 0.073242 | -0.28839 | 0.14648 | -0.045777 | -0.11902 | -0.2655 | 121.3806 | 121.7194 | 10.5652 | -121.582 | 121.3715 | 121.3943 | 8.4732 | -121.5866
780.3594 | 121.7697 | -5.7632 | 115.8096 | 0.12085 | 0.053461 | 0.061666 | 0.01458 | 0.1261 | -0.0010981 | 0.022723 | 0.13657 | -0.0096344 | 0.055301 | 0.066565 | 0.0056888 | -0.0096323 | 115.8646 | 115.8051 | 4.6738 | -5.7724 | 115.6265 | -5.6854 | -5.7495 | -5.6717 | 2.5497 | -5.8777 | 115.6311 | 115.6082 | -5.658 | -5.7312 | 0.07782 | 0.013733 | -0.1831 | 121.5683 | -0.009155 | -0.022888 | 0.054932 | 0.10529 | 0.032044 | -0.17853 | 0.091553 | -0.11444 | -0.14648 | -0.20142 | 121.3898 | 121.6278 | 10.437 | -121.5591 | 121.3943 | 121.3715 | 8.313 | -121.5408
782.0469 | 121.6919 | -5.8273 | 115.7776 | -0.13092 | 0.059016 | 0.064016 | 0.021843 | 0.12503 | 0.0016791 | 0.024218 | -0.14572 | -0.0096344 | 0.058719 | 0.067419 | 0.0012028 | -0.0092051 | 115.8279 | 115.7684 | 4.4037 | -5.7999 | 115.6128 | -5.7495 | -5.7861 | -5.7587 | 2.7969 | -5.9463 | 115.5899 | 115.5991 | -5.7358 | -5.7953 | 0.07782 | 0.041199 | -0.16479 | 121.5958 | 0.027466 | -0.013733 | 0.050354 | 0.091553 | 0.032044 | -0.18768 | 0.068665 | -0.11902 | -0.15106 | -0.17853 | 121.4401 | 121.6553 | 10.231 | -121.5637 | 121.4172 | 121.4264 | 8.6243 | -121.5729
783.7969 | 121.7285 | -6.015 | 115.5762 | 0.11322 | 0.053034 | 0.062521 | 0.015862 | 0.12759 | -0.0038751 | 0.022937 | 0.15182 | -0.010916 | 0.055087 | 0.068274 | 0.0024844 | -0.0049325 | 115.6815 | 115.6952 | 4.9301 | -5.9647 | 115.3519 | -5.9006 | -5.928 | -5.8502 | 3.1998 | -6.0608 | 115.3381 | 115.3931 | -5.8914 | -5.9509 | 0.11444 | 0.086975 | -0.2243 | 121.7102 | 0.050354 | -0.036621 | 0.10529 | 0.1236 | 0.064087 | -0.23804 | 0.16479 | -0.045776 | -0.10986 | -0.18311 | 121.3669 | 121.6965 | 10.9451 | -121.5042 | 121.3531 | 121.4081 | 9.2148 | -121.5271
785.4844 | 121.637 | -5.7037 | 115.9515 | -0.069885 | 0.054957 | 0.062948 | 0.016716 | 0.12418 | 0.0010381 | 0.022937 | -0.092316 | -0.0083526 | 0.055514 | 0.068915 | 0.0065432 | -0.0089915 | 116.011 | 115.9424 | 4.9484 | -5.6488 | 115.7181 | -5.5847 | -5.6351 | -5.5801 | 3.5339 | -5.809 | 115.6952 | 115.741 | -5.5847 | -5.6442 | 0.11902 | 0.068664 | -0.23346 | 121.6461 | 0.054931 | -0.013733 | 0.059509 | 0.11902 | 0.059509 | -0.25635 | 0.1236 | -0.10529 | -0.1648 | -0.21057 | 121.4218 | 121.7148 | 10.6522 | -121.5866 | 121.3989 | 121.4447 | 9.2377 | -121.5958
787.2344 | 121.7331 | -5.6854 | 115.9332 | 0.097962 | 0.051112 | 0.063589 | 0.018425 | 0.12695 | -0.0068659 | 0.024859 | 0.15945 | -0.010062 | 0.055301 | 0.065497 | 0.00163 | -0.0062143 | 116.0248 | 116.0202 | 5.1544 | -5.6213 | 115.6815 | -5.5344 | -5.5939 | -5.5023 | 3.8269 | -5.7083 | 115.7181 | 115.7364 | -5.5389 | -5.5984 | 0.15106 | 0.091553 | -0.25177 | 121.7056 | 0.064087 | -0.027466 | 0.091552 | 0.14649 | 0.086975 | -0.21515 | 0.18311 | -0.022888 | -0.10986 | -0.19684 | 121.3669 | 121.7102 | 10.8398 | -121.5271 | 121.4035 | 121.4218 | 9.5123 | -121.5317
789 | 121.6461 | -5.658 | 116.0477 | -0.19196 | 0.052393 | 0.063803 | 0.019707 | 0.12631 | -0.00045708 | 0.022509 | -0.17624 | -0.011771 | 0.05701 | 0.068487 | 0.0012028 | -0.0079233 | 116.0614 | 116.0156 | 5.6717 | -5.5618 | 115.7822 | -5.4886 | -5.5618 | -5.5527 | 4.2755 | -5.7312 | 115.773 | 115.8096 | -5.5161 | -5.5664 | 0.16937 | 0.09613 | -0.2655 | 121.6736 | 0.09613 | 0 | 0.013733 | 0.14191 | 0.091553 | -0.27466 | 0.10529 | -0.073242 | -0.1648 | -0.23804 | 121.4401 | 121.7194 | 11.3297 | -121.6095 | 121.431 | 121.4676 | 9.9335 | -121.6141
790.75 | 121.8018 | -5.4611 | 116.1163 | -0.031738 | 0.052607 | 0.063162 | 0.021202 | 0.12354 | -0.0055841 | 0.023791 | -0.023651 | -0.012411 | 0.056582 | 0.066992 | -0.001788 | -0.0089915 | 116.2079 | 116.1942 | 5.6763 | -5.4062 | 115.9103 | -5.3421 | -5.3925 | -5.2963 | 4.6005 | -5.4703 | 115.9195 | 115.9287 | -5.3513 | -5.4062 | 0.11902 | 0.068665 | -0.20599 | 121.6553 | 0.054932 | -0.013733 | 0.091553 | 0.10986 | 0.054932 | -0.19684 | 0.1648 | -0.009155 | -0.064087 | -0.18768 | 121.3715 | 121.669 | 11.1374 | -121.5088 | 121.3806 | 121.3898 | 10.0616 | -121.5225
792.5 | 121.6782 | -5.7953 | 115.8188 | -0.092773 | 0.055811 | 0.062521 | 0.017784 | 0.12738 | 0.0023199 | 0.023577 | -0.12283 | -0.0094208 | 0.053592 | 0.069128 | 0.0039798 | -0.010273 | 115.8783 | 115.7913 | 5.9647 | -5.777 | 115.6036 | -5.722 | -5.7816 | -5.6854 | 4.628 | -5.928 | 115.6128 | 115.6357 | -5.7175 | -5.7632 | 0.073242 | 0.013733 | -0.21515 | 121.5866 | 0.01831 | 0.004577 | 0.059509 | 0.07782 | 0.032043 | -0.20599 | 0.10986 | -0.13275 | -0.16479 | -0.18311 | 121.3989 | 121.6736 | 11.7599 | -121.6003 | 121.4081 | 121.431 | 10.4233 | -121.582
794.2031 | 121.7834 | -5.6396 | 115.9195 | 0.14374 | 0.053675 | 0.062307 | 0.016502 | 0.12524 | -0.00024348 | 0.022509 | 0.11368 | -0.0096344 | 0.057651 | 0.069128 | 0.0037662 | -0.0085641 | 115.9973 | 115.9103 | 6.4774 | -5.6442 | 115.7501 | -5.5618 | -5.5984 | -5.5298 | 4.7287 | -5.7587 | 115.7593 | 115.7822 | -5.5435 | -5.5847 | 0.077819 | 0.041198 | -0.16937 | 121.55 | -0.004578 | -0.045776 | 0.077819 | 0.09613 | 0.054931 | -0.16022 | 0.10986 | -0.11902 | -0.17395 | -0.13733 | 121.3898 | 121.637 | 12.117 | -121.5179 | 121.3989 | 121.4218 | 10.3683 | -121.5042
795.9531 | 121.7285 | -5.7678 | 115.8325 | -0.13855 | 0.052821 | 0.063589 | 0.021202 | 0.12524 | -0.0053705 | 0.022723 | -0.092316 | -0.011984 | 0.058505 | 0.067419 | -7.9008e-05 | -0.0064279 | 115.9012 | 115.8875 | 6.4316 | -5.7358 | 115.5487 | -5.6992 | -5.7541 | -5.6442 | 5.809 | -5.8273 | 115.5624 | 115.6082 | -5.6717 | -5.7312 | 0.068664 | 0.013733 | -0.28381 | 121.6553 | 0.032043 | 0.01831 | 0.068664 | 0.09613 | 0.036621 | -0.27008 | 0.1236 | -0.05951 | -0.096131 | -0.22431 | 121.3165 | 121.669 | 12.1994 | -121.5866 | 121.3303 | 121.376 | 11.5768 | -121.5637
797.6406 | 121.7743 | -5.6808 | 115.8875 | 0.11322 | 0.056452 | 0.06188 | 0.016075 | 0.12695 | 0.0014655 | 0.022937 | 0.15945 | -0.009848 | 0.056369 | 0.068701 | 0.0052616 | -0.0079233 | 115.9332 | 115.8966 | 6.5414 | -5.6808 | 115.7227 | -5.6168 | -5.6625 | -5.5847 | 5.7724 | -5.7999 | 115.6769 | 115.7227 | -5.5939 | -5.6534 | 0.064087 | 0.01831 | -0.16479 | 121.5775 | 0 | -0.01831 | 0.045777 | 0.086975 | 0.027466 | -0.21057 | 0.09613 | -0.11902 | -0.14648 | -0.16479 | 121.4035 | 121.6141 | 12.2223 | -121.55 | 121.3577 | 121.4035 | 11.4532 | -121.5408
799.4062 | 121.6324 | -5.6213 | 116.0248 | -0.016479 | 0.05517 | 0.063375 | 0.016502 | 0.12631 | 0.0031745 | 0.024646 | -0.016022 | -0.0094208 | 0.056369 | 0.068915 | 0.0054752 | -0.0083505 | 116.0797 | 116.011 | 6.3217 | -5.5664 | 115.8234 | -5.4977 | -5.5618 | -5.5069 | 5.8777 | -5.7358 | 115.8188 | 115.8417 | -5.484 | -5.5435 | 0.1236 | 0.059509 | -0.20142 | 121.6324 | 0.054932 | -0.004577 | 0.054932 | 0.13733 | 0.07782 | -0.20599 | 0.11444 | -0.11444 | -0.19226 | -0.18311 | 121.4447 | 121.701 | 11.9431 | -121.5866 | 121.4401 | 121.463 | 11.499 | -121.5683
801.0938 | 121.7743 | -5.5206 | 116.0843 | 0.036926 | 0.054743 | 0.062521 | 0.022057 | 0.12439 | -0.0064387 | 0.023791 | 0.09079 | -0.012625 | 0.057223 | 0.067633 | -0.00050621 | -0.0060007 | 116.1026 | 116.0797 | 5.9463 | -5.4886 | 115.86 | -5.4016 | -5.4749 | -5.4016 | 7.0221 | -5.603 | 115.8371 | 115.8966 | -5.4062 | -5.452 | 0.11902 | 0.045776 | -0.22431 | 121.6003 | 0.032044 | -0.013732 | 0.01831 | 0.11444 | 0.068665 | -0.24719 | 0.11902 | -0.082397 | -0.15106 | -0.18768 | 121.3806 | 121.6232 | 11.467 | -121.5591 | 121.3577 | 121.4172 | 12.5427 | -121.5363
802.8438 | 121.637 | -5.159 | 116.5237 | -0.0012209 | 0.055384 | 0.062735 | 0.016716 | 0.12589 | 0.0044561 | 0.025286 | -0.016022 | -0.0089936 | 0.057223 | 0.068487 | 0.0041934 | -0.010059 | 116.5375 | 116.4642 | 5.9692 | -5.1041 | 116.2903 | -5.0079 | -5.0903 | -5.0583 | 6.926 | -5.2917 | 116.2949 | 116.3132 | -5.0446 | -5.0812 | 0.15106 | 0.068665 | -0.23346 | 121.6232 | 0.054932 | -0.013733 | 0.013733 | 0.11444 | 0.07782 | -0.22888 | 0.10071 | -0.13275 | -0.21057 | -0.21057 | 121.4493 | 121.6965 | 11.1282 | -121.6141 | 121.4539 | 121.4722 | 12.085 | -121.6049
804.5938 | 121.788 | -5.2597 | 116.3315 | 0.159 | 0.054957 | 0.06188 | 0.016289 | 0.12482 | -0.0025935 | 0.022296 | 0.098419 | -0.009848 | 0.055514 | 0.068274 | 0.0048344 | -0.0072825 | 116.4276 | 116.3773 | 5.7816 | -5.1865 | 116.1255 | -5.1178 | -5.2048 | -5.1132 | 6.4957 | -5.3055 | 116.098 | 116.1255 | -5.1544 | -5.191 | 0.14191 | 0.054932 | -0.20599 | 121.637 | 0.073243 | 0.018311 | 0.09613 | 0.10529 | 0.068665 | -0.23346 | 0.14649 | -0.045776 | -0.11444 | -0.20599 | 121.3852 | 121.6873 | 11.0413 | -121.5363 | 121.3577 | 121.3852 | 11.7554 | -121.5225
806.3438 | 121.6873 | -5.2872 | 116.3864 | -0.092773 | 0.056238 | 0.061453 | 0.020561 | 0.12418 | 0.00082452 | 0.025927 | -0.099945 | -0.008139 | 0.058719 | 0.068701 | 0.0024844 | -0.0077097 | 116.4047 | 116.3681 | 6.7337 | -5.2094 | 116.1575 | -5.1773 | -5.2185 | -5.1498 | 5.896 | -5.3558 | 116.1346 | 116.1575 | -5.1453 | -5.2094 | 0.10986 | 0.068664 | -0.22888 | 121.6553 | 0.077819 | 0.009155 | 0.01831 | 0.14191 | 0.077819 | -0.25177 | 0.13733 | -0.068665 | -0.14648 | -0.22888 | 121.4447 | 121.6919 | 12.0209 | -121.6049 | 121.4218 | 121.4447 | 11.1832 | -121.5958
808.0156 | 121.8109 | -5.3192 | 116.2491 | -0.039368 | 0.051752 | 0.064444 | 0.019066 | 0.12375 | -0.0085749 | 0.023577 | -0.084686 | -0.013693 | 0.056369 | 0.065924 | -0.0011472 | -0.0064279 | 116.3269 | 116.3406 | 8.0246 | -5.2826 | 116.0522 | -5.2139 | -5.2734 | -5.1819 | 6.0379 | -5.365 | 116.0248 | 116.0477 | -5.2094 | -5.2734 | 0.10529 | 0.045777 | -0.19684 | 121.6599 | 0.036621 | -0.009156 | 0.07782 | 0.10986 | 0.045777 | -0.2243 | 0.13733 | -0.045776 | -0.091553 | -0.20142 | 121.3715 | 121.6461 | 13.3438 | -121.5225 | 121.344 | 121.3669 | 11.3571 | -121.5225
809.7656 | 121.7377 | -5.2322 | 116.3315 | 0.12848 | 0.050257 | 0.062094 | 0.016716 | 0.12759 | -0.0036615 | 0.021869 | 0.1442 | -0.010275 | 0.053164 | 0.068701 | 0.002698 | -0.0072825 | 116.4688 | 116.4413 | 7.9788 | -5.159 | 116.1758 | -5.1224 | -5.1727 | -5.0629 | 5.6854 | -5.2597 | 116.1118 | 116.153 | -5.0949 | -5.1682 | 0.10986 | 0.05951 | -0.15564 | 121.6736 | 0.073242 | 0.013732 | 0.13733 | 0.13733 | 0.064087 | -0.21973 | 0.16937 | -0.027466 | -0.091553 | -0.17853 | 121.4081 | 121.7011 | 13.2111 | -121.5042 | 121.344 | 121.3852 | 10.9177 | -121.4996
811.5156 | 121.6461 | -5.3329 | 116.3086 | -0.13092 | 0.056238 | 0.062521 | 0.01992 | 0.12781 | -0.0045161 | 0.021441 | -0.1152 | -0.010703 | 0.057651 | 0.066992 | 0.00034819 | -0.0092051 | 116.3818 | 116.3727 | 7.2372 | -5.2231 | 116.0843 | -5.191 | -5.2368 | -5.1819 | 5.3238 | -5.3467 | 116.0797 | 116.0934 | -5.1773 | -5.2505 | 0.14191 | 0.096131 | -0.2243 | 121.7056 | 0.10986 | 0.013733 | 0.073242 | 0.15564 | 0.082398 | -0.22888 | 0.15106 | -0.013733 | -0.096131 | -0.21515 | 121.4172 | 121.7148 | 12.5702 | -121.5454 | 121.4127 | 121.4264 | 10.6567 | -121.5591
813.2656 | 121.6782 | -5.2963 | 116.3544 | -0.13855 | 0.056238 | 0.062307 | 0.020775 | 0.12631 | -0.0023797 | 0.021869 | -0.1152 | -0.012625 | 0.055514 | 0.068274 | 0.00077539 | -0.010059 | 116.4368 | 116.4001 | 6.7017 | -5.191 | 116.1163 | -5.1636 | -5.1956 | -5.1086 | 5.4337 | -5.3009 | 116.1163 | 116.1438 | -5.1407 | -5.1865 | 0.13275 | 0.10071 | -0.23804 | 121.6965 | 0.10529 | 0.004578 | 0.082398 | 0.15564 | 0.10986 | -0.23804 | 0.18768 | -0.004577 | -0.11444 | -0.21057 | 121.4127 | 121.7331 | 11.998 | -121.55 | 121.4127 | 121.4401 | 10.73 | -121.5408
815.0156 | 121.7697 | -4.7699 | 116.803 | 0.029297 | 0.051325 | 0.065084 | 0.015648 | 0.12759 | -0.0047297 | 0.0208 | 0.060272 | -0.010062 | 0.05701 | 0.066351 | -0.0013608 | -0.0085641 | 116.8808 | 116.8533 | 6.4865 | -4.7104 | 116.6428 | -4.6692 | -4.7058 | -4.6326 | 5.0537 | -4.8294 | 116.6016 | 116.6199 | -4.6509 | -4.7104 | 0.10071 | 0.064086 | -0.16022 | 121.6232 | 0.059509 | -0.004577 | 0.077819 | 0.11902 | 0.059509 | -0.20142 | 0.13733 | -0.05951 | -0.11902 | -0.18311 | 121.4127 | 121.6507 | 11.2564 | -121.5088 | 121.3715 | 121.3898 | 9.8236 | -121.5134
816.7031 | 121.7422 | -5.2689 | 116.3177 | -0.14618 | 0.054102 | 0.063375 | 0.018852 | 0.12738 | -0.0045161 | 0.0208 | -0.15335 | -0.010489 | 0.056155 | 0.068487 | 0.0012028 | -0.0094187 | 116.4642 | 116.4276 | 5.9967 | -5.1727 | 116.0934 | -5.1544 | -5.2231 | -5.0858 | 5.0812 | -5.278 | 116.0934 | 116.1392 | -5.1361 | -5.2048 | 0.11444 | 0.045777 | -0.2243 | 121.6965 | 0.096131 | 0.050354 | 0.14648 | 0.13275 | 0.064087 | -0.2243 | 0.18311 | -0.009155 | -0.073242 | -0.17853 | 121.3623 | 121.7331 | 11.2656 | -121.5408 | 121.3623 | 121.4081 | 10.35 | -121.5225
818.4375 | 121.7056 | -5.2917 | 116.3589 | -0.1004 | 0.057947 | 0.062948 | 0.019707 | 0.12759 | 0.0042425 | 0.021869 | -0.16098 | -0.010489 | 0.058719 | 0.066992 | 0.004407 | -0.0087777 | 116.4001 | 116.3223 | 6.2668 | -5.2277 | 116.1713 | -5.1727 | -5.2505 | -5.1773 | 5.0583 | -5.365 | 116.153 | 116.1484 | -5.1682 | -5.2185 | 0.11902 | 0.041199 | -0.18768 | 121.6141 | 0.064087 | 0.022888 | 0.041198 | 0.1236 | 0.073242 | -0.20599 | 0.11444 | -0.073242 | -0.14648 | -0.21057 | 121.463 | 121.6919 | 11.5585 | -121.6095 | 121.4447 | 121.4401 | 10.35 | -121.5775
820.1875 | 121.669 | -5.0903 | 116.5512 | -0.054626 | 0.05453 | 0.062094 | 0.019066 | 0.12759 | 0.0036017 | 0.025073 | -0.12283 | -0.0083526 | 0.056155 | 0.067847 | 0.0054752 | -0.0079233 | 116.6061 | 116.5512 | 6.1203 | -5.0262 | 116.3635 | -4.9622 | -5.0262 | -4.9484 | 4.9759 | -5.159 | 116.3177 | 116.3635 | -4.9667 | -5.0262 | 0.12817 | 0.064087 | -0.18768 | 121.6415 | 0.064087 | 0 | 0.054932 | 0.1236 | 0.064087 | -0.23346 | 0.14191 | -0.068665 | -0.13275 | -0.18768 | 121.4539 | 121.6965 | 11.2106 | -121.5775 | 121.4081 | 121.4539 | 10.0662 | -121.5775
821.9375 | 121.7239 | -5.3192 | 116.2994 | 0.090332 | 0.050043 | 0.062521 | 0.020348 | 0.12717 | -0.0062249 | 0.022296 | 0.15945 | -0.010489 | 0.057651 | 0.06507 | 0.0022708 | -0.0045053 | 116.3635 | 116.3544 | 6.1157 | -5.2597 | 116.0294 | -5.1956 | -5.2505 | -5.159 | 4.9805 | -5.3696 | 116.0294 | 116.0706 | -5.2002 | -5.2689 | 0.1236 | 0.068665 | -0.27008 | 121.6736 | 0.059509 | -0.009156 | 0.064087 | 0.11902 | 0.050354 | -0.27008 | 0.16022 | -0.050354 | -0.10071 | -0.22888 | 121.3486 | 121.6827 | 11.4349 | -121.55 | 121.3486 | 121.3898 | 10.2997 | -121.5683
823.6406 | 121.6415 | -5.2734 | 116.3818 | -0.11566 | 0.054316 | 0.065084 | 0.02227 | 0.12567 | -0.0030207 | 0.022296 | -0.16098 | -0.009848 | 0.05701 | 0.067206 | 0.00098899 | -0.0047189 | 116.3727 | 116.3452 | 5.9006 | -5.2368 | 116.153 | -5.1498 | -5.2231 | -5.191 | 5.2231 | -5.3879 | 116.1942 | 116.1758 | -5.1636 | -5.2368 | 0.1236 | 0.050354 | -0.22888 | 121.6187 | 0.036621 | -0.013733 | -0.009155 | 0.10986 | 0.036621 | -0.18768 | 0.082397 | -0.11444 | -0.15106 | -0.20599 | 121.4264 | 121.6461 | 11.174 | -121.6049 | 121.4676 | 121.4493 | 10.4965 | -121.6187
825.375 | 121.6553 | -5.2963 | 116.3498 | 0.059815 | 0.054316 | 0.06188 | 0.01693 | 0.12695 | 0.0016791 | 0.023364 | 0.052643 | -0.0094208 | 0.056369 | 0.067206 | 0.003339 | -0.0077097 | 116.3544 | 116.2628 | 5.1224 | -5.2643 | 116.1621 | -5.1636 | -5.2277 | -5.2185 | 4.9759 | -5.4611 | 116.1621 | 116.1713 | -5.159 | -5.2368 | 0.13275 | 0.068665 | -0.18768 | 121.5591 | 0.032044 | -0.036621 | 0.004578 | 0.13733 | 0.05951 | -0.18768 | 0.07782 | -0.1648 | -0.22431 | -0.17853 | 121.4584 | 121.6507 | 10.4187 | -121.5775 | 121.4584 | 121.4676 | 10.2722 | -121.5866
827.125 | 121.7972 | -5.2185 | 116.3589 | 0.0064086 | 0.055384 | 0.06423 | 0.023338 | 0.12781 | -0.0060113 | 0.020373 | 0.022125 | -0.010916 | 0.058078 | 0.066992 | -7.9008e-05 | -0.0079233 | 116.4322 | 116.4368 | 5.3787 | -5.1544 | 116.1667 | -5.1086 | -5.1544 | -5.0629 | 5.1956 | -5.2551 | 116.1575 | 116.1804 | -5.0903 | -5.1407 | 0.10986 | 0.064087 | -0.19226 | 121.6553 | 0.064087 | 0 | 0.073242 | 0.12817 | 0.07782 | -0.20142 | 0.15564 | -0.036621 | -0.11444 | -0.17853 | 121.3852 | 121.6507 | 10.5972 | -121.5134 | 121.376 | 121.3989 | 10.4141 | -121.4996
828.8281 | 121.7789 | -4.8065 | 116.7801 | -0.077515 | 0.053889 | 0.064657 | 0.020348 | 0.12631 | -0.0062249 | 0.018878 | -0.061798 | -0.011343 | 0.057437 | 0.066138 | 0.00034819 | -0.0098459 | 116.9037 | 116.9037 | 5.4932 | -4.6875 | 116.5878 | -4.6692 | -4.7241 | -4.5868 | 5.9006 | -4.7653 | 116.5695 | 116.5695 | -4.6555 | -4.715 | 0.13733 | 0.082398 | -0.19226 | 121.7102 | 0.11902 | 0.036621 | 0.1236 | 0.15106 | 0.091553 | -0.21057 | 0.21973 | 0.041199 | -0.050354 | -0.21057 | 121.3943 | 121.7102 | 10.2997 | -121.5042 | 121.376 | 121.376 | 10.7071 | -121.4951
830.5781 | 121.7697 | -5.0171 | 116.5192 | -0.40558 | 0.056879 | 0.062735 | 0.020134 | 0.12546 | -0.0049433 | 0.020373 | -0.054169 | -0.011771 | 0.058078 | 0.06571 | 0.00056179 | -0.0092051 | 116.6428 | 116.6428 | 5.2643 | -4.9438 | 116.3589 | -4.9301 | -4.9805 | -4.8523 | 5.6213 | -5.0262 | 116.3361 | 116.3498 | -4.9164 | -4.9622 | 0.086975 | 0.036621 | -0.16022 | 121.6599 | 0.073242 | 0.036621 | 0.1236 | 0.10071 | 0.054932 | -0.1831 | 0.16479 | -0.009155 | -0.064087 | -0.16937 | 121.376 | 121.6599 | 10.2814 | -121.4996 | 121.3531 | 121.3669 | 10.6384 | -121.4813
832.3281 | 121.6507 | -4.953 | 116.7389 | -0.19958 | 0.055598 | 0.063589 | 0.022697 | 0.12866 | 0.00018372 | 0.021869 | -0.17624 | -0.013052 | 0.056796 | 0.069342 | 0.0024844 | -0.0098459 | 116.7709 | 116.7297 | 5.0308 | -4.8386 | 116.4963 | -4.8019 | -4.8477 | -4.8065 | 5.2414 | -5.0034 | 116.5009 | 116.5329 | -4.8111 | -4.8752 | 0.15106 | 0.10529 | -0.24262 | 121.6827 | 0.11444 | 0.009155 | 0.032043 | 0.14191 | 0.07782 | -0.23804 | 0.14648 | -0.050354 | -0.12817 | -0.20599 | 121.4493 | 121.7239 | 9.9838 | -121.5866 | 121.4539 | 121.4859 | 10.1944 | -121.6141
834.0938 | 121.7834 | -5.0446 | 116.5466 | 0.044556 | 0.05218 | 0.065512 | 0.017571 | 0.12888 | -0.0062249 | 0.021014 | -0.046539 | -0.011343 | 0.055301 | 0.067847 | 0.0018436 | -0.0092051 | 116.6931 | 116.6748 | 5.1361 | -4.921 | 116.3956 | -4.8935 | -4.9393 | -4.8111 | 4.7974 | -4.9942 | 116.3727 | 116.3864 | -4.8798 | -4.953 | 0.15106 | 0.10529 | -0.15106 | 121.7194 | 0.1236 | 0.018311 | 0.14648 | 0.16479 | 0.091553 | -0.17395 | 0.23346 | 0.050354 | -0.041199 | -0.16022 | 121.4401 | 121.7377 | 10.1807 | -121.4859 | 121.4172 | 121.431 | 9.8419 | -121.4996
835.7812 | 121.6827 | -4.9667 | 116.6611 | -0.16144 | 0.055384 | 0.063589 | 0.016075 | 0.13101 | 0.0033881 | 0.020373 | -0.20676 | -0.007071 | 0.053592 | 0.066992 | 0.006757 | -0.0083505 | 116.7389 | 116.6473 | 5.0583 | -4.8614 | 116.4825 | -4.8431 | -4.8843 | -4.834 | 4.747 | -5.0537 | 116.4917 | 116.5009 | -4.8569 | -4.8981 | 0.1236 | 0.082398 | -0.17853 | 121.6141 | 0.10529 | 0.022888 | 0.07782 | 0.10986 | 0.068665 | -0.16937 | 0.13275 | -0.086975 | -0.15564 | -0.16022 | 121.4493 | 121.7056 | 10.025 | -121.5454 | 121.4584 | 121.4676 | 9.7137 | -121.5591
837.5312 | 121.7834 | -4.921 | 116.6565 | 0.15137 | 0.053248 | 0.061239 | 0.015221 | 0.13123 | 0.00061092 | 0.021869 | 0.11368 | -0.010275 | 0.054873 | 0.067633 | 0.0052616 | -0.0072825 | 116.7252 | 116.6519 | 5.0171 | -4.8981 | 116.478 | -4.7974 | -4.8889 | -4.7699 | 5.0766 | -5.0217 | 116.4642 | 116.4963 | -4.8157 | -4.8843 | 0.1236 | 0.032043 | -0.17853 | 121.5729 | 0.022888 | -0.009155 | 0.068665 | 0.10529 | 0.036621 | -0.19226 | 0.15106 | -0.10071 | -0.13733 | -0.16022 | 121.3989 | 121.6461 | 9.938 | -121.5454 | 121.3852 | 121.4172 | 9.9976 | -121.5408
839.2188 | 121.7606 | -4.9484 | 116.6382 | -0.10803 | 0.053889 | 0.062735 | 0.023338 | 0.12994 | -0.0049433 | 0.019305 | -0.092316 | -0.009848 | 0.057864 | 0.065924 | 0.00013459 | -0.0074961 | 116.7892 | 116.7801 | 5.0537 | -4.8203 | 116.4093 | -4.8203 | -4.8752 | -4.7516 | 5.3558 | -4.9438 | 116.4139 | 116.4597 | -4.7928 | -4.8752 | 0.12817 | 0.073242 | -0.22888 | 121.7285 | 0.12817 | 0.054932 | 0.15106 | 0.15564 | 0.073242 | -0.22431 | 0.19684 | 0.004577 | -0.068665 | -0.17853 | 121.3577 | 121.7377 | 10.0021 | -121.5134 | 121.3623 | 121.4081 | 10.3043 | -121.5134
840.9688 | 121.7239 | -4.8111 | 116.7572 | 0.159 | 0.054316 | 0.062735 | 0.017357 | 0.13059 | -0.0019525 | 0.019946 | 0.15945 | -0.011984 | 0.052737 | 0.066779 | 0.003339 | -0.0092051 | 116.8854 | 116.8396 | 4.5456 | -4.7104 | 116.5329 | -4.7058 | -4.747 | -4.6326 | 5.4428 | -4.8523 | 116.5421 | 116.5604 | -4.6967 | -4.7562 | 0.10529 | 0.064087 | -0.2243 | 121.6507 | 0.10071 | 0.036621 | 0.12817 | 0.11444 | 0.054931 | -0.21515 | 0.17853 | -0.041199 | -0.09613 | -0.19684 | 121.344 | 121.6965 | 9.3567 | -121.5042 | 121.3531 | 121.3715 | 10.2539 | -121.5134
842.6562 | 121.6553 | -4.7287 | 116.954 | 0.059815 | 0.056879 | 0.062521 | 0.018425 | 0.1308 | 0.0029607 | 0.021441 | 0.029755 | -0.0085662 | 0.056369 | 0.070196 | 0.005048 | -0.0096323 | 116.9174 | 116.7984 | 4.2343 | -4.6646 | 116.7389 | -4.6143 | -4.6829 | -4.6371 | 5.1086 | -4.8752 | 116.716 | 116.7435 | -4.5959 | -4.6692 | 0.11444 | 0.045777 | -0.21515 | 121.5271 | 0.064087 | 0.01831 | -0.036622 | 0.13275 | 0.05951 | -0.23804 | 0.091553 | -0.14648 | -0.20599 | -0.21057 | 121.4676 | 121.6461 | 8.963 | -121.637 | 121.4447 | 121.4722 | 9.8373 | -121.6232
844.4062 | 121.6553 | -4.8523 | 116.7984 | -0.069885 | 0.055384 | 0.063162 | 0.018425 | 0.13123 | 0.0029607 | 0.021228 | -0.099945 | -0.0089936 | 0.053592 | 0.06806 | 0.004407 | -0.0085641 | 116.8671 | 116.7847 | 4.1107 | -4.7241 | 116.6199 | -4.7241 | -4.7791 | -4.6875 | 4.715 | -4.9026 | 116.5695 | 116.6199 | -4.7333 | -4.7791 | 0.12817 | 0.073242 | -0.17853 | 121.637 | 0.12817 | 0.054932 | 0.068664 | 0.11902 | 0.073242 | -0.22888 | 0.16479 | -0.050354 | -0.1236 | -0.17853 | 121.4722 | 121.7194 | 8.963 | -121.5775 | 121.4218 | 121.4722 | 9.5673 | -121.5775
846.1406 | 121.7651 | -4.7424 | 116.7984 | 0.18188 | 0.053034 | 0.061666 | 0.016502 | 0.13251 | -0.0015253 | 0.019091 | 0.12894 | -0.0094208 | 0.055728 | 0.06806 | 0.0024844 | -0.0064279 | 116.8579 | 116.7984 | 3.8406 | -4.6875 | 116.6245 | -4.6783 | -4.7379 | -4.6097 | 4.8889 | -4.8294 | 116.6061 | 116.6565 | -4.6555 | -4.715 | 0.064087 | 0.004578 | -0.17395 | 121.5408 | 0.054932 | 0.050354 | 0.059509 | 0.086975 | 0.027466 | -0.19226 | 0.13275 | -0.086975 | -0.11444 | -0.14191 | 121.3669 | 121.6003 | 8.5831 | -121.5363 | 121.3486 | 121.3989 | 9.6313 | -121.5134
847.8906 | 121.7102 | -4.5547 | 117.0456 | 0.14374 | 0.051752 | 0.063162 | 0.020348 | 0.13422 | -0.0030207 | 0.015887 | 0.15182 | -0.010062 | 0.056369 | 0.066992 | 0.00077539 | -0.0068551 | 117.1463 | 117.1326 | 3.1311 | -4.3945 | 116.8304 | -4.4037 | -4.4632 | -4.3396 | 4.8798 | -4.5456 | 116.803 | 116.8671 | -4.4312 | -4.4724 | 0.15106 | 0.091553 | -0.21515 | 121.6873 | 0.16022 | 0.068665 | 0.10071 | 0.1236 | 0.082398 | -0.24261 | 0.21515 | 0.009156 | -0.073242 | -0.17853 | 121.3852 | 121.701 | 7.6859 | -121.5088 | 121.3577 | 121.4218 | 9.4345 | -121.5179
849.5781 | 121.7194 | -4.5364 | 117.0639 | 0.11322 | 0.050898 | 0.062307 | 0.015648 | 0.13251 | -0.0036615 | 0.017382 | 0.17471 | -0.010703 | 0.057437 | 0.06806 | 0.003339 | -0.0068551 | 117.1738 | 117.1692 | 2.9892 | -4.3991 | 116.8488 | -4.3854 | -4.4266 | -4.3259 | 5.0354 | -4.541 | 116.835 | 116.8762 | -4.4037 | -4.4678 | 0.15106 | 0.10986 | -0.21515 | 121.7056 | 0.13733 | 0.027466 | 0.10986 | 0.13275 | 0.068665 | -0.22888 | 0.21057 | -0.004578 | -0.073243 | -0.18768 | 121.3852 | 121.7102 | 7.5256 | -121.4905 | 121.3715 | 121.4127 | 9.5718 | -121.5317
851.3281 | 121.7102 | -3.8956 | 117.7368 | 0.12085 | 0.050471 | 0.064444 | 0.015648 | 0.13507 | -0.0025935 | 0.013537 | 0.10605 | -0.012411 | 0.055728 | 0.067206 | 0.0018436 | -0.0060007 | 117.7689 | 117.7368 | 3.1586 | -3.8177 | 117.4667 | -3.7811 | -3.8452 | -3.7445 | 5.0308 | -3.9322 | 117.5079 | 117.5262 | -3.8086 | -3.9825 | 0.11444 | 0.050354 | -0.27008 | 121.6324 | 0.07782 | 0.027466 | 0.032044 | 0.086975 | -0.086975 | -0.22888 | 0.15106 | -0.036621 | 0.050354 | -0.21057 | 121.3623 | 121.6644 | 7.0541 | -121.582 | 121.4035 | 121.4218 | 8.9264 | -121.7194
853.0156 | 121.6644 | -6.6971 | 114.9399 | -0.046997 | 0.055811 | 0.06188 | 0.018852 | 0.1355 | 0.0025335 | 0.013751 | -0.13046 | -0.0085662 | 0.056155 | 0.067419 | 0.0024844 | -0.012409 | 118.364 | 118.2678 | 3.3279 | -3.3005 | 118.071 | -3.2318 | -3.3005 | -3.1906 | 5.1132 | -3.4058 | 118.071 | 118.103 | -3.241 | -3.3005 | 3.4653 | 3.3966 | 3.1311 | 124.9649 | 3.3966 | 0 | 3.4241 | 3.4561 | 3.3966 | 3.1311 | 3.5065 | 3.2913 | -0.10529 | 3.1631 | 124.7681 | 125.061 | 10.025 | -118.2404 | 124.7681 | 124.8001 | 11.8103 | -118.2404
854.7812 | 121.7651 | -2.1378 | 119.4992 | -0.1004 | 0.053889 | 0.064444 | 0.023552 | 0.1355 | -0.0068659 | 0.015887 | -0.061798 | -0.011771 | 0.05936 | 0.066565 | -0.0015744 | -0.0062143 | 119.6136 | 119.5816 | 3.4195 | -1.9409 | 119.252 | -2.0142 | -2.0645 | -1.9455 | 5.5435 | -2.0645 | 119.2383 | 119.2978 | -2.0279 | -2.0554 | 0.1236 | 0.073242 | -0.24719 | 121.7194 | 0.19684 | 0.1236 | 0.11444 | 0.10986 | 0.082397 | -0.26093 | 0.19226 | 0.073242 | -0.009155 | -0.20142 | 121.3898 | 121.7514 | 5.5573 | -121.5637 | 121.376 | 121.4355 | 7.6813 | -121.5546
856.4688 | 121.7606 | -5.7632 | 116.6656 | -0.11566 | 0.053248 | 0.062735 | 0.025688 | 0.17886 | -0.0036615 | -0.0029117 | -0.16098 | -0.009848 | 0.056369 | 0.065283 | -0.00071981 | -0.0066415 | 117.4988 | 117.4164 | 4.5639 | -5.2322 | 116.4688 | -5.1178 | -5.0034 | -4.1931 | 6.8024 | -4.4998 | 116.4688 | 116.6565 | -4.921 | -4.8477 | 0.64545 | 0.75989 | -0.19684 | 123.1796 | 0.53101 | -0.22888 | 0.83313 | 0.84229 | 0.91553 | -0.19684 | 1.5701 | 1.2634 | 0.3479 | -0.009155 | 122.2321 | 123.262 | 10.3271 | -121.669 | 122.2321 | 122.4197 | 12.5656 | -121.5134
858.2188 | 121.6553 | -1.2543 | 120.4559 | 0.097962 | 0.05453 | 0.062307 | 0.01693 | 0.13422 | 0.0025335 | 0.01781 | 0.060272 | -0.00878 | 0.054446 | 0.069556 | 0.0046206 | -0.0077097 | 120.4102 | 120.3323 | 3.2593 | -1.0895 | 120.2682 | -1.1078 | -1.149 | -1.1032 | 5.658 | -1.2909 | 120.2545 | 120.2728 | -1.1032 | -1.1719 | 0.14648 | 0.10529 | -0.18768 | 121.5866 | 0.16479 | 0.059509 | -0.045777 | 0.15106 | 0.082397 | -0.20142 | 0.15106 | -0.036622 | -0.11902 | -0.18311 | 121.5225 | 121.6644 | 4.5135 | -121.6049 | 121.5088 | 121.5271 | 6.9122 | -121.6278
859.9688 | 121.6827 | -37.1658 | 84.8511 | -0.16144 | 0.20748 | 0.063375 | 0.11626 | 0.13614 | 0.051026 | 0.19661 | -0.16098 | -0.0092072 | 0.059787 | 0.06806 | 0.00163 | -0.0085641 | 86.4578 | 86.8469 | 1.6113 | -25.0259 | 86.4899 | -34.3643 | -34.2957 | -35.9207 | 1.4877 | -36.0535 | 85.4782 | 85.6201 | -35.5133 | -35.4584 | 2.8015 | 2.8702 | 1.6388 | 124.0128 | 12.1399 | 9.2697 | 1.6068 | 1.6525 | 1.7075 | 0.62714 | 1.2451 | 1.1124 | -0.59509 | 0.76904 | 123.6557 | 123.6237 | 38.7772 | -119.1467 | 122.644 | 122.7859 | 38.6536 | -120.3094
861.6562 | 121.6278 | -0.89264 | 120.7993 | -0.16907 | 0.058161 | 0.064657 | 0.021416 | 0.13165 | 0.00082452 | 0.022296 | -0.15335 | -0.0094208 | 0.057437 | 0.067633 | 0.0029116 | -0.0079233 | 120.7718 | 120.7169 | 3.1494 | -0.80566 | 120.6253 | -0.74158 | -0.80566 | -0.75989 | 5.7587 | -0.89722 | 120.5978 | 120.607 | -0.74616 | -0.80109 | 0.15106 | 0.086975 | -0.17395 | 121.6095 | 0.086975 | 0 | -0.027465 | 0.14648 | 0.091553 | -0.20142 | 0.13275 | -0.004578 | -0.096131 | -0.19226 | 121.5179 | 121.6644 | 4.0421 | -121.6049 | 121.4905 | 121.4996 | 6.6513 | -121.6003
863.4062 | 121.7468 | -0.82398 | 120.7901 | 0.0064086 | 0.05752 | 0.066366 | 0.020134 | 0.13016 | -0.0053705 | 0.021869 | 0.045013 | -0.011343 | 0.057437 | 0.066351 | -7.9008e-05 | -0.0072825 | 120.8496 | 120.8359 | 3.6255 | -0.59509 | 120.6162 | -0.69122 | -0.75531 | -0.63629 | 6.2164 | -0.77362 | 120.5658 | 120.6116 | -0.70953 | -0.72784 | 0.13275 | 0.068665 | -0.17395 | 121.6599 | 0.22888 | 0.16022 | 0.059509 | 0.11444 | 0.096131 | -0.2243 | 0.18768 | 0.050354 | -0.045777 | -0.17853 | 121.4401 | 121.6736 | 4.4495 | -121.5454 | 121.3898 | 121.4355 | 7.0404 | -121.5179
865.1719 | 121.7422 | -1.1444 | 120.4468 | 0.159 | 0.054316 | 0.064016 | 0.015862 | 0.13635 | 0.0014655 | 0.019946 | 0.12131 | -0.0096344 | 0.057437 | 0.067206 | 0.0041934 | -0.0070689 | 120.5063 | 120.4376 | 3.2959 | -0.90637 | 120.282 | -1.0391 | -1.0895 | -0.97961 | 6.0333 | -1.149 | 120.2454 | 120.2774 | -1.0437 | -1.0757 | 0.10529 | 0.054931 | -0.16479 | 121.582 | 0.23804 | 0.18311 | 0.05951 | 0.10071 | 0.068664 | -0.20142 | 0.1648 | -0.004578 | -0.073242 | -0.16937 | 121.4264 | 121.6507 | 4.4403 | -121.5363 | 121.3898 | 121.4218 | 7.1777 | -121.5225
866.9219 | 121.6782 | -1.181 | 120.4926 | -0.16144 | 0.059229 | 0.062094 | 0.020561 | 0.13358 | 0.0012519 | 0.020373 | -0.12283 | -0.0092072 | 0.058291 | 0.068487 | 0.002698 | -0.0092051 | 120.5154 | 120.4193 | 3.0899 | -0.92926 | 120.282 | -1.0712 | -1.149 | -1.03 | 6.0196 | -1.1856 | 120.2682 | 120.3049 | -1.0757 | -1.0986 | 0.10986 | 0.032043 | -0.21057 | 121.6003 | 0.25177 | 0.21973 | 0.022888 | 0.10529 | 0.082397 | -0.2243 | 0.15106 | -0.004578 | -0.086975 | -0.18768 | 121.463 | 121.6965 | 4.2709 | -121.6415 | 121.4493 | 121.4859 | 7.2006 | -121.5912
868.6094 | 121.7285 | -1.2451 | 120.3644 | 0.0064086 | 0.055598 | 0.065725 | 0.020988 | 0.13593 | -0.0049433 | 0.018451 | 0.098419 | -0.012625 | 0.055942 | 0.066138 | -0.0011472 | -0.0077097 | 120.3918 | 120.3598 | 3.0853 | -0.97961 | 120.163 | -1.1307 | -1.1948 | -1.1032 | 6.2256 | -1.2405 | 120.1355 | 120.1721 | -1.1444 | -1.1902 | 0.11444 | 0.050354 | -0.20142 | 121.6049 | 0.2655 | 0.21515 | 0.027466 | 0.10071 | 0.054931 | -0.22888 | 0.14191 | 0.004577 | -0.050354 | -0.19226 | 121.4081 | 121.637 | 4.3304 | -121.5591 | 121.3806 | 121.4172 | 7.4707 | -121.5546
870.3594 | 121.6827 | -0.78278 | 120.8817 | 0.12085 | 0.056452 | 0.061453 | 0.017357 | 0.134 | 0.0012519 | 0.023577 | 0.10605 | -0.0083526 | 0.056369 | 0.068701 | 0.0052616 | -0.0094187 | 120.8817 | 120.7901 | 2.7786 | -0.58594 | 120.7169 | -0.6546 | -0.71869 | -0.65002 | 6.3446 | -0.81482 | 120.694 | 120.7123 | -0.67749 | -0.71411 | 0.12817 | 0.064087 | -0.16479 | 121.5729 | 0.19684 | 0.13275 | 0 | 0.10529 | 0.068665 | -0.18768 | 0.13275 | -0.032043 | -0.10071 | -0.16937 | 121.4996 | 121.6644 | 3.5614 | -121.6003 | 121.4767 | 121.4951 | 7.1274 | -121.5958
872.1094 | 121.701 | -0.50354 | 121.138 | 0.11322 | 0.056025 | 0.065084 | 0.018639 | 0.13101 | -0.0032343 | 0.022937 | 0.13657 | -0.011557 | 0.057864 | 0.065497 | 0.0031254 | -0.0070689 | 121.1838 | 121.1655 | 2.774 | -0.3067 | 120.8908 | -0.37079 | -0.43488 | -0.3067 | 6.3492 | -0.46234 | 120.9045 | 120.9229 | -0.37994 | -0.42114 | 0.13275 | 0.068665 | -0.24719 | 121.669 | 0.19684 | 0.12817 | 0.045777 | 0.1236 | 0.082397 | -0.23346 | 0.19684 | 0.041199 | -0.041198 | -0.21515 | 121.3943 | 121.6873 | 3.2776 | -121.5729 | 121.4081 | 121.4264 | 6.8527 | -121.5591
873.7969 | 121.7377 | -0.66834 | 120.9412 | 0.11322 | 0.056452 | 0.064016 | 0.017143 | 0.13486 | 0.00061092 | 0.0208 | 0.075531 | -0.009848 | 0.057223 | 0.068487 | 0.0052616 | -0.0068551 | 120.9778 | 120.8771 | 2.5818 | -0.5127 | 120.7855 | -0.58594 | -0.65002 | -0.55389 | 6.3629 | -0.72784 | 120.7809 | 120.7626 | -0.58594 | -0.64545 | 0.082398 | 0.018311 | -0.15564 | 121.5454 | 0.15564 | 0.13733 | 0.036621 | 0.082398 | 0.022888 | -0.16022 | 0.11444 | -0.059509 | -0.082397 | -0.17853 | 121.4539 | 121.6461 | 3.2501 | -121.5912 | 121.4493 | 121.431 | 7.0312 | -121.5866
875.5469 | 121.6827 | -0.77362 | 120.9229 | -0.19196 | 0.060297 | 0.06423 | 0.023125 | 0.13529 | 0.0012519 | 0.0208 | -0.18387 | -0.008139 | 0.05701 | 0.068487 | 0.0022708 | -0.0087777 | 120.8954 | 120.8176 | 2.6642 | -0.56763 | 120.7123 | -0.65002 | -0.71869 | -0.64545 | 6.6467 | -0.78735 | 120.726 | 120.7581 | -0.65918 | -0.68665 | 0.1236 | 0.054932 | -0.21057 | 121.5912 | 0.20599 | 0.15106 | -0.027466 | 0.11444 | 0.086975 | -0.19684 | 0.12817 | -0.013733 | -0.10071 | -0.1648 | 121.4859 | 121.669 | 3.4378 | -121.6415 | 121.4996 | 121.5317 | 7.4204 | -121.6095
877.2969 | 121.7834 | -0.59052 | 121.0007 | -0.016479 | 0.055598 | 0.062307 | 0.020348 | 0.13486 | -0.0051569 | 0.021441 | 0.0068663 | -0.010916 | 0.057864 | 0.066992 | -0.00029261 | -0.0060007 | 121.0739 | 121.0602 | 2.6413 | -0.37994 | 120.8267 | -0.46692 | -0.5127 | -0.40741 | 7.3654 | -0.53101 | 120.7993 | 120.8405 | -0.44403 | -0.51727 | 0.1236 | 0.07782 | -0.17395 | 121.6507 | 0.21057 | 0.13275 | 0.073243 | 0.14648 | 0.073242 | -0.20142 | 0.18311 | 0.059509 | -0.013733 | -0.16022 | 121.4172 | 121.6644 | 3.2318 | -121.5134 | 121.3898 | 121.431 | 7.9559 | -121.5179
879.0469 | 121.669 | -0.59052 | 121.106 | -0.062256 | 0.059016 | 0.058676 | 0.020134 | 0.13635 | 0.0016791 | 0.026568 | -0.12283 | -0.0068572 | 0.056369 | 0.068701 | 0.0054752 | -0.0089915 | 121.1426 | 121.0648 | 2.4307 | -0.35248 | 120.9091 | -0.43945 | -0.53101 | -0.39368 | 7.37 | -0.56305 | 120.8817 | 120.9229 | -0.43488 | -0.49439 | 0.15106 | 0.059509 | -0.19684 | 121.6553 | 0.23804 | 0.17853 | 0.036621 | 0.15564 | 0.09613 | -0.2243 | 0.19684 | 0.027466 | -0.068664 | -0.1831 | 121.4996 | 121.7331 | 3.0212 | -121.637 | 121.4722 | 121.5134 | 7.9605 | -121.6003
880.75 | 121.6415 | -0.5722 | 121.1288 | 0.067444 | 0.057093 | 0.063589 | 0.018211 | 0.134 | 0.0016791 | 0.024432 | 0.052643 | -0.0094208 | 0.057223 | 0.06806 | 0.0059024 | -0.0070689 | 121.0922 | 120.9869 | 2.3529 | -0.40741 | 120.9137 | -0.43945 | -0.48981 | -0.4303 | 7.0496 | -0.60883 | 120.9091 | 120.9641 | -0.43488 | -0.48981 | 0.13275 | 0.082398 | -0.21515 | 121.5591 | 0.16479 | 0.082397 | -0.036621 | 0.13733 | 0.082398 | -0.21973 | 0.14191 | -0.036621 | -0.11902 | -0.16479 | 121.4859 | 121.6644 | 2.9251 | -121.6187 | 121.4813 | 121.5363 | 7.6218 | -121.6187
882.5 | 121.7102 | -0.48065 | 121.17 | 0.097962 | 0.052607 | 0.065084 | 0.019493 | 0.13123 | 0.0023199 | 0.018451 | 0.15945 | -0.010703 | 0.056582 | 0.067206 | 0.0014164 | -0.0051463 | 121.2433 | 121.2021 | 2.6413 | -3.4424 | 120.932 | -0.33417 | -0.40283 | -0.27924 | 7.3059 | -0.41657 | 120.9366 | 120.9824 | -0.3479 | -0.3891 | 0.14649 | 0.07782 | -0.23804 | 121.6827 | -2.9617 | -3.0396 | 0.073242 | 0.13275 | 0.091553 | -0.23346 | 0.20142 | 0.064087 | -0.027466 | -0.18768 | 121.4127 | 121.7239 | 3.1219 | -121.5729 | 121.4172 | 121.463 | 7.7866 | -121.5591
884.1719 | 121.6919 | -0.63629 | 121.0327 | -0.1004 | 0.061152 | 0.061666 | 0.026115 | 0.13422 | 0.0018927 | 0.023577 | -0.10757 | -0.0068572 | 0.058291 | 0.06806 | 0.0022708 | -0.010273 | 121.0602 | 120.9732 | 2.4078 | -0.46234 | 120.8267 | -0.52185 | -0.59967 | -0.48981 | 7.1777 | -0.737 | 120.7718 | 120.7993 | -0.5722 | -0.59052 | 0.11444 | 0.036622 | -0.20599 | 121.6095 | 0.17395 | 0.13733 | 0.027466 | 0.064087 | 0.045777 | -0.26093 | 0.14648 | -0.10071 | -0.14648 | -0.23346 | 121.463 | 121.6965 | 3.0441 | -121.6324 | 121.4081 | 121.4355 | 7.814 | -121.6232
885.9219 | 121.7056 | -1.0162 | 120.639 | -0.15381 | 0.063502 | 0.064657 | 0.025261 | 0.14468 | -0.0034479 | 0.022723 | -0.10757 | -0.010703 | 0.056369 | 0.067847 | -0.0013608 | -0.0079233 | 120.7123 | 120.6894 | 2.536 | -0.63629 | 120.433 | -0.86517 | -0.95673 | -0.85602 | 7.196 | -0.93842 | 120.3827 | 120.4514 | -0.88806 | -0.92468 | 0.15106 | 0.059509 | -0.20599 | 121.7056 | 0.37994 | 0.32043 | 0.073242 | 0.12817 | 0.091552 | -0.25635 | 0.16022 | 0.077819 | -0.013733 | -0.18768 | 121.4493 | 121.7285 | 3.5522 | -121.5958 | 121.3989 | 121.4676 | 8.2123 | -121.5637
887.6094 | 121.7194 | -0.46234 | 121.1792 | -0.13092 | 0.060938 | 0.064444 | 0.02227 | 0.13464 | -0.00088448 | 0.024859 | -0.10757 | -0.013907 | 0.058291 | 0.06507 | 0.0022708 | -0.0096323 | 121.2753 | 121.2616 | 2.3712 | -1.181 | 120.9778 | -0.31586 | -0.38452 | -0.2655 | 7.8506 | -0.37079 | 120.9503 | 120.9595 | -0.33417 | -0.36621 | 0.14648 | 0.07782 | -0.20142 | 121.7239 | -0.71869 | -0.79651 | 0.096131 | 0.12817 | 0.09613 | -0.22888 | 0.19684 | 0.091552 | -0.004578 | -0.21973 | 121.4401 | 121.7377 | 2.8336 | -121.5637 | 121.4127 | 121.4218 | 8.313 | -121.5454
889.3594 | 121.6278 | -0.64545 | 121.0556 | -0.046997 | 0.062861 | 0.060171 | 0.02227 | 0.13742 | 0.0040289 | 0.027209 | -0.077057 | -0.0092072 | 0.060641 | 0.069342 | 0.0041934 | -0.0096323 | 121.0693 | 121.0098 | 2.2018 | -0.42114 | 120.8359 | -0.51727 | -0.5722 | -0.48981 | 7.402 | -0.65002 | 120.8221 | 120.8359 | -0.53101 | -0.56763 | 0.12817 | 0.073242 | -0.21973 | 121.6553 | 0.2243 | 0.15106 | 0.013733 | 0.11444 | 0.07782 | -0.23346 | 0.15564 | -0.004577 | -0.082397 | -0.21973 | 121.4813 | 121.7148 | 2.8473 | -121.6278 | 121.4676 | 121.4813 | 8.0475 | -121.6232
891.1094 | 121.6827 | -0.74616 | 120.8908 | -0.1767 | 0.071192 | 0.061666 | 0.031456 | 0.14063 | 0.00061092 | 0.038745 | -0.099945 | -0.011343 | 0.058719 | 0.066992 | 0.00077539 | -0.0087777 | 120.9549 | 121.0144 | 2.1011 | -0.24261 | 120.6802 | -0.6134 | -0.66376 | -0.51727 | 7.5943 | -0.68665 | 120.6436 | 120.6665 | -0.62714 | -0.66834 | 0.13275 | 0.082398 | -0.21057 | 121.7606 | 0.50354 | 0.42114 | 0.064087 | 0.11902 | 0.07782 | -0.24719 | 0.22888 | 0.059509 | -0.018311 | -0.2243 | 121.4264 | 121.701 | 2.8473 | -121.5546 | 121.3898 | 121.4127 | 8.3405 | -121.5591
892.8125 | 121.637 | -0.76446 | 120.9183 | -0.21484 | 0.072047 | 0.065298 | 0.029747 | 0.14404 | -0.0010981 | 0.047503 | -0.15335 | -0.010275 | 0.060641 | 0.067847 | 0.00056179 | -0.0079233 | 120.8862 | 120.8405 | 1.8539 | -0.14191 | 120.6345 | -0.6546 | -0.73242 | -0.70953 | 7.3105 | -0.85602 | 120.6573 | 120.6299 | -0.69122 | -0.74158 | 0.10986 | 0.032043 | -0.28381 | 121.6049 | 0.62256 | 0.59052 | -0.032044 | 0.073242 | 0.022888 | -0.26093 | 0.054931 | -0.091553 | -0.11444 | -0.28839 | 121.3989 | 121.6507 | 2.6184 | -121.6507 | 121.4218 | 121.3943 | 8.075 | -121.6599
894.5625 | 121.7377 | -0.86517 | 120.7306 | 0.014038 | 0.05752 | 0.064016 | 0.020775 | 0.13742 | -0.0030207 | 0.065875 | 0.060272 | -0.011343 | 0.097598 | 0.066779 | 0.00034819 | -0.0081369 | 120.7169 | 120.7123 | 1.6846 | -0.43488 | 120.5429 | -0.75531 | -0.81482 | -0.74616 | 8.139 | -0.86517 | 120.5109 | 120.5338 | -0.76904 | -0.82398 | 0.10986 | 0.050354 | -0.18768 | 121.5775 | 0.4303 | 0.37994 | -0.013733 | 0.09613 | 0.041198 | -0.21973 | 0.11902 | 0 | -0.041198 | -0.19684 | 121.4081 | 121.582 | 2.5497 | -121.5454 | 121.376 | 121.3989 | 9.0042 | -121.5546
896.25 | 121.6827 | -0.55847 | 121.0327 | 0.059815 | 0.059443 | 0.067007 | 0.018425 | 0.13699 | 0.0025335 | 0.034045 | 0.029755 | -0.0096344 | 0.059146 | 0.067419 | 0.00163 | -0.0087777 | 121.1014 | 121.1151 | 1.5793 | 1.7395 | 120.8725 | -0.43488 | -0.49896 | -0.36163 | 8.1299 | -0.53558 | 120.8084 | 120.7993 | -0.48523 | -0.54016 | 0.1236 | 0.05951 | -0.16022 | 121.6736 | 2.298 | 2.2385 | 0.068664 | 0.073243 | 0.018311 | -0.2243 | 0.19684 | 0.022889 | 0.004578 | -0.23346 | 121.431 | 121.6599 | 2.1378 | -121.5317 | 121.3669 | 121.3577 | 8.6884 | -121.5729
897.9844 | 121.6095 | -3.2547 | 118.3456 | -0.19958 | 0.50506 | 0.062948 | 0.2846 | 0.2515 | 0.15741 | 0.4442 | -0.23727 | -0.01113 | 0.064059 | 0.067206 | 0.0022708 | -0.010059 | 118.2495 | 118.19 | 1.3504 | 37.8479 | 117.9794 | -3.186 | -3.2364 | -3.2181 | 8.2626 | -3.4058 | 118.071 | 118.0618 | -3.2135 | -3.2822 | 0.068665 | 0.018311 | -0.36621 | 121.4447 | 41.1026 | 41.0843 | -0.09613 | 0.041199 | -0.027466 | -0.27466 | 0.036621 | -0.15106 | -0.1236 | -0.28381 | 121.2341 | 121.5042 | 4.6051 | -121.582 | 121.3257 | 121.3165 | 11.5173 | -121.6278
899.6875 | 121.6919 | -98.8403 | 22.4854 | -0.092773 | -0.036688 | -0.0037021 | 0.034233 | -0.014251 | 0.0010381 | 0.0045651 | -0.12283 | -0.010062 | 0.092471 | 0.073187 | 0.0054752 | -0.0081369 | 0.045776 | -0.022888 | -0.16937 | -0.004578 | -0.022888 | 0.10529 | 0.004578 | -97.9797 | -8.7479 | -98.9365 | 22.5769 | 22.6044 | -98.5565 | -98.822 | 98.9456 | 98.8449 | -22.5082 | 98.8174 | 98.8358 | -0.009156 | -22.4396 | 0.28381 | 0.018311 | 0.091552 | 0.8606 | -0.09613 | -0.11444 | 0.11902 | 98.8174 | 98.8861 | 98.671 | -22.4808 | 121.4172 | 121.4447 | 90.0925 | -121.3074
901.4531 | 121.701 | -109.758 | 11.7004 | -0.14618 | -0.038397 | -0.0011385 | 0.034233 | -0.012115 | -0.0057977 | 0.0071287 | -0.10757 | -0.011771 | 0.096744 | 0.071265 | 0.0052616 | -0.0068551 | 0.059509 | 0.064087 | -0.12817 | 0.068665 | -0.041199 | 0.11902 | 0.009155 | -108.9798 | -9.8053 | -109.9136 | 11.5677 | 11.5952 | -109.5657 | -109.8358 | 109.877 | 109.7672 | -11.7416 | 109.8221 | 109.8267 | 0.05951 | -11.6409 | 0.19226 | -0.077819 | -0.13275 | 0.7782 | -0.15564 | -0.07782 | -0.10528 | 109.7168 | 109.8175 | 109.6298 | -11.6913 | 121.3257 | 121.3531 | 99.9527 | -121.5363
903.2031 | 121.669 | -110.8475 | 10.6155 | -0.039368 | -0.037328 | -0.0049837 | 0.029106 | -0.012969 | 0.0018927 | 0.0079831 | -0.077057 | -0.010062 | 0.093326 | 0.071905 | 0.0071842 | -0.0070689 | 0.054932 | -0.009155 | -0.16479 | 0.022888 | -0.036621 | 0.10071 | 0.013733 | -110.0922 | -9.8419 | -111.1038 | 10.524 | 10.5423 | -110.6186 | -110.9619 | 110.9482 | 110.8612 | -10.6522 | 110.8383 | 110.8704 | 0.009155 | -10.5606 | 0.22888 | -0.11444 | -0.091553 | 0.75531 | -0.25635 | -0.14191 | -0.073243 | 110.8109 | 110.9024 | 110.6827 | -10.6018 | 121.3715 | 121.3898 | 101.0056 | -121.5775
904.9688 | 121.8063 | -111.3281 | 10.1028 | 0.021668 | -0.042883 | -0.0032749 | 0.033379 | -0.014678 | -0.0070795 | 0.0056333 | 0.075531 | -0.012198 | 0.095675 | 0.070624 | 0.0020572 | -0.0045053 | 0.022888 | 0 | -0.086975 | 0.036621 | -0.045776 | 0.12817 | 0.022888 | -110.6094 | -8.7433 | -111.5433 | 9.9792 | 10.0159 | -111.1359 | -111.4563 | 111.4563 | 111.351 | -10.1486 | 111.3281 | 111.3647 | 0.013733 | -10.08 | 0.19226 | -0.12817 | -0.1236 | 0.71869 | -0.21515 | -0.086975 | -0.086975 | 111.2823 | 111.351 | 111.2412 | -10.08 | 121.3074 | 121.344 | 102.5848 | -121.5591
906.6562 | 121.8475 | -111.6394 | 9.7916 | -0.024109 | -0.039037 | -0.0051975 | 0.033592 | -0.014037 | -0.0051569 | 0.0047787 | 0.0068663 | -0.010916 | 0.096103 | 0.073187 | 0.0035526 | -0.0085641 | 0.041199 | 0.018311 | -0.064087 | 0.041199 | -0.064087 | 0.10529 | 0.027466 | -110.7971 | -8.9813 | -111.8042 | 9.7137 | 9.7412 | -111.3968 | -111.7355 | 111.7447 | 111.6669 | -9.8557 | 111.6577 | 111.6806 | 0.013733 | -9.7504 | 0.24261 | -0.096131 | -0.07782 | 0.84229 | -0.16479 | -0.068664 | -0.050354 | 111.5753 | 111.6806 | 111.5753 | -9.7641 | 121.3531 | 121.3806 | 102.6581 | -121.5271
908.4062 | 121.7239 | -111.8042 | 9.7137 | -0.14618 | -0.038397 | -0.0034885 | 0.034233 | -0.016387 | -0.0053705 | 0.0054197 | -0.092316 | -0.011343 | 0.097171 | 0.071478 | 0.0031254 | -0.0074961 | 0.091553 | 0.07782 | 0 | 0.068665 | -0.064087 | 0.1236 | 0.036621 | -110.9665 | -9.2102 | -111.9415 | 9.5581 | 9.6039 | -111.5067 | -111.8546 | 111.9278 | 111.8408 | -9.7778 | 111.882 | 111.8729 | 0.032044 | -9.6222 | 0.29755 | -0.050354 | -0.15564 | 0.83771 | -0.13733 | -0.086975 | -0.10986 | 111.7401 | 111.8958 | 111.8042 | -9.6771 | 121.3623 | 121.4081 | 102.594 | -121.5683
910.0938 | 121.7468 | -111.9919 | 9.4666 | -0.10803 | -0.033697 | -0.0054111 | 0.033379 | -0.014464 | 0.00082452 | 0.0067013 | -0.13046 | -0.011771 | 0.097598 | 0.071478 | 0.0052616 | -0.0089915 | 0.059509 | -0.036621 | -0.064087 | 0.032043 | -0.022888 | 0.07782 | -0.013733 | -111.2366 | -8.931 | -112.2208 | 9.3842 | 9.4299 | -111.7447 | -112.056 | 112.0697 | 111.9781 | -9.4894 | 111.9553 | 112.0239 | 0.045776 | -9.407 | 0.24719 | -0.064087 | -0.082398 | 0.75531 | -0.22888 | -0.16479 | -0.036621 | 111.969 | 112.0514 | 111.9278 | -9.4803 | 121.376 | 121.4218 | 103.0609 | -121.5225
911.8438 | 121.6827 | -111.9415 | 9.581 | -0.046997 | -0.035192 | -0.0054111 | 0.034447 | -0.012115 | 0.00082452 | 0.0090513 | -0.084686 | -0.011771 | 0.097384 | 0.072333 | 0.005048 | -0.010487 | 0.068665 | -0.004578 | -0.036621 | 0.036621 | -0.027466 | 0.10986 | -0.018311 | -111.1404 | -8.4641 | -112.1475 | 9.4711 | 9.5123 | -111.6394 | -111.9827 | 112.0514 | 111.9232 | -9.6085 | 111.937 | 111.9781 | 0.054932 | -9.5123 | 0.30212 | -0.041199 | -0.10986 | 0.80109 | -0.20599 | -0.16479 | -0.068665 | 111.9141 | 112.0102 | 111.9049 | -9.5993 | 121.4127 | 121.4539 | 103.4775 | -121.5637
913.5938 | 121.7834 | -112.0148 | 9.4437 | 0.18188 | -0.037328 | -0.0028475 | 0.033165 | -0.01361 | -0.0040887 | 0.0088377 | 0.16708 | -0.011984 | 0.09653 | 0.068701 | 0.0052616 | -0.0064279 | 0.086975 | 0.059509 | 0.013733 | 0.073242 | -0.082397 | 0.14191 | 0.041199 | -111.1816 | -8.4915 | -112.1567 | 9.3201 | 9.3384 | -111.7172 | -112.056 | 112.1567 | 112.056 | -9.5261 | 112.0743 | 112.088 | 0.032043 | -9.3567 | 0.29755 | -0.041198 | -0.1236 | 0.83313 | -0.14191 | -0.10071 | -0.10529 | 111.9324 | 112.1017 | 112.0285 | -9.4025 | 121.3348 | 121.3531 | 103.5233 | -121.4996
915.3438 | 121.7285 | -111.9049 | 9.5856 | -0.14618 | -0.036688 | -0.0062655 | 0.035301 | -0.01361 | -0.0019525 | 0.0062741 | -0.19913 | -0.01113 | 0.098453 | 0.072119 | 0.0031254 | -0.0064279 | -0.018311 | -0.050354 | -0.10071 | 0.004578 | -0.004578 | 0.09613 | -0.009155 | -111.2091 | -8.8028 | -112.2025 | 9.4345 | 9.462 | -111.7172 | -112.0331 | 112.001 | 111.8958 | -9.5901 | 111.8546 | 111.9095 | 0.013733 | -9.6039 | 0.18768 | -0.12817 | -0.15106 | 0.6958 | -0.29755 | -0.16937 | -0.1236 | 111.9003 | 111.8866 | 111.8042 | -9.5947 | 121.3394 | 121.3669 | 103.1021 | -121.6187
917.0938 | 121.701 | -111.9324 | 9.5901 | 0.090332 | -0.037969 | -0.0051975 | 0.029961 | -0.015319 | -0.0023797 | 0.0071287 | 0.075531 | -0.010062 | 0.095675 | 0.071478 | 0.005048 | -0.0077097 | -0.009155 | -0.07782 | -0.082397 | -0.013733 | -0.022888 | 0.09613 | -0.013733 | -111.1633 | -8.6609 | -112.1979 | 9.4894 | 9.5078 | -111.6348 | -111.9827 | 112.0285 | 111.9186 | -9.613 | 111.8546 | 111.9186 | 0 | -9.5993 | 0.29755 | -0.050354 | -0.10071 | 0.76904 | -0.2655 | -0.21515 | -0.082398 | 111.9095 | 111.9232 | 111.85 | -9.6039 | 121.4218 | 121.4401 | 103.2715 | -121.5729
918.8438 | 121.6827 | -111.8729 | 9.668 | -0.016479 | -0.032629 | -0.0056247 | 0.034019 | -0.013824 | -0.00088448 | 0.0062741 | -0.031281 | -0.0092072 | 0.09888 | 0.068274 | 0.004407 | -0.0066415 | 0.045776 | -0.027466 | -0.013733 | 0.027466 | -0.050354 | 0.10071 | -0.013733 | -111.0718 | -8.4137 | -112.1017 | 9.5673 | 9.5901 | -111.5936 | -111.9095 | 111.9736 | 111.8591 | -9.7183 | 111.8454 | 111.9003 | 0.041199 | -9.6222 | 0.27924 | -0.036621 | -0.10071 | 0.80109 | -0.22888 | -0.19226 | -0.07782 | 111.8225 | 111.9186 | 111.8591 | -9.6817 | 121.4401 | 121.463 | 103.4592 | -121.5775
920.5469 | 121.8155 | -111.6852 | 9.7595 | 0.097962 | -0.036901 | -0.0041293 | 0.032311 | -0.011901 | -0.0040887 | 0.0086239 | 0.18997 | -0.013266 | 0.09653 | 0.068701 | 0.0024844 | -0.0042917 | 0.068665 | 0.064087 | 0.068665 | 0.086975 | -0.059509 | 0.1236 | 0.036621 | -110.8429 | -7.6218 | -111.882 | 9.6176 | 9.6451 | -111.438 | -111.7767 | 111.8088 | 111.7218 | -9.819 | 111.7493 | 111.7722 | 0.050354 | -9.6909 | 0.24719 | -0.091552 | -0.14191 | 0.84229 | -0.19684 | -0.10529 | -0.11444 | 111.6257 | 111.7538 | 111.7538 | -9.7229 | 121.3028 | 121.3303 | 104.0634 | -121.5363
922.2969 | 121.7789 | -111.6852 | 9.7961 | 0.029297 | -0.037969 | -0.0030611 | 0.037437 | -0.012969 | -0.0077203 | 0.0052061 | 0.12894 | -0.013907 | 0.095889 | 0.071478 | 0.00034819 | -0.0070689 | 0.036621 | 0.027466 | 0.07782 | 0.041199 | -0.059509 | 0.13733 | 0.032043 | -110.8063 | -7.6584 | -111.8546 | 9.6909 | 9.7229 | -111.4014 | -111.7401 | 111.8225 | 111.7172 | -9.8557 | 111.7126 | 111.7264 | 0.009156 | -9.7595 | 0.28381 | -0.054931 | -0.10529 | 0.87891 | -0.16937 | -0.11444 | -0.073243 | 111.6257 | 111.7218 | 111.763 | -9.7641 | 121.376 | 121.4081 | 104.0268 | -121.5363
923.9844 | 121.6736 | -111.9965 | 9.5535 | -0.039368 | -0.03626 | -0.0054111 | 0.033379 | -0.013183 | 0.0021063 | 0.0096921 | -0.069428 | -0.010275 | 0.097598 | 0.071692 | 0.005048 | -0.0094187 | 0.059509 | -0.004578 | 0.027466 | 0.041199 | -0.045776 | 0.10071 | -0.009155 | -111.113 | -8.345 | -112.2025 | 9.4162 | 9.4711 | -111.7035 | -112.0148 | 112.0972 | 111.9873 | -9.5993 | 111.9919 | 112.0377 | 0.050354 | -9.494 | 0.29297 | -0.018311 | -0.13733 | 0.88348 | -0.20599 | -0.18768 | -0.082398 | 111.9507 | 112.056 | 112.0239 | -9.5627 | 121.4127 | 121.4676 | 103.6514 | -121.5683
925.7344 | 121.701 | -112.1979 | 9.3384 | -0.13092 | -0.036688 | -0.0041293 | 0.037224 | -0.011474 | -0.0068659 | 0.0067013 | -0.12283 | -0.01412 | 0.099093 | 0.073401 | 0.00098899 | -0.0062143 | 0.082397 | 0.073242 | 0.12817 | 0.073242 | -0.059509 | 0.13275 | 0.027466 | -111.2228 | -8.6334 | -112.3352 | 9.1965 | 9.2285 | -111.9186 | -112.2162 | 112.3306 | 112.2253 | -9.3979 | 112.2711 | 112.2711 | 0.045776 | -9.256 | 0.27924 | -0.018311 | -0.14191 | 0.97504 | -0.13733 | -0.11902 | -0.10986 | 112.1384 | 112.2803 | 112.326 | -9.3109 | 121.3943 | 121.4264 | 103.5645 | -121.5546
927.4844 | 121.6873 | -112.3123 | 9.2011 | 0.044556 | -0.03626 | -0.0041293 | 0.030388 | -0.014464 | 0.0014655 | 0.0081967 | 0.0068663 | -0.0096344 | 0.099521 | 0.072333 | 0.006757 | -0.0083505 | 0.018311 | -0.073242 | -0.013733 | 0.004578 | -0.036621 | 0.07782 | -0.018311 | -111.4197 | -8.7433 | -112.5732 | 9.1095 | 9.1461 | -112.0148 | -112.381 | 112.3901 | 112.294 | -9.2377 | 112.2391 | 112.3169 | 0.022889 | -9.1827 | 0.29755 | -0.068664 | -0.091553 | 0.89264 | -0.26093 | -0.19226 | -0.054932 | 112.2757 | 112.3306 | 112.2986 | -9.2194 | 121.4218 | 121.4584 | 103.569 | -121.582
929.2344 | 121.6644 | -112.4222 | 9.1324 | -0.024109 | -0.034124 | -0.0060519 | 0.03701 | -0.015746 | 0.00018372 | 0.0086239 | -0.023651 | -0.0096344 | 0.10059 | 0.072333 | 0.0039798 | -0.0068551 | 0.027466 | -0.009155 | 0.036621 | 0.018311 | -0.018311 | 0.086975 | -0.018311 | -111.4838 | -8.432 | -112.6373 | 8.9951 | 9.0637 | -112.1338 | -112.4588 | 112.5092 | 112.4039 | -9.1507 | 112.413 | 112.4405 | 0.036622 | -9.1049 | 0.28839 | -0.036621 | -0.13733 | 0.93841 | -0.21515 | -0.17853 | -0.068664 | 112.4039 | 112.4496 | 112.4588 | -9.1507 | 121.4172 | 121.4859 | 103.9902 | -121.5912
930.9844 | 121.8109 | -112.2345 | 9.2331 | 0.15137 | -0.040746 | -0.0041293 | 0.031883 | -0.016814 | -0.0038751 | 0.0092649 | 0.18234 | -0.010703 | 0.097384 | 0.069342 | 0.0080386 | -0.0074961 | 0.064087 | 0.013733 | 0.082397 | 0.059509 | -0.041199 | 0.13733 | 0.027466 | -111.2778 | -5.0766 | -112.4542 | 9.0958 | 9.1232 | -112.0102 | -112.3077 | 112.3718 | 112.262 | -9.2743 | 112.2482 | 112.294 | 0.032043 | -9.169 | 0.2243 | -0.073242 | -0.13733 | 0.95673 | -0.21973 | -0.14648 | -0.10986 | 112.1933 | 112.2986 | 112.3169 | -9.2056 | 121.3303 | 121.3577 | 107.1579 | -121.5408
932.6719 | 121.7468 | -111.5616 | 9.9792 | -0.1004 | -0.038824 | -0.0060519 | 0.034447 | -0.01361 | -0.0010981 | 0.0094785 | -0.1152 | -0.01113 | 0.098025 | 0.073187 | 0.006757 | -0.0070689 | 0.050354 | -0.009155 | 0.045776 | 0.032043 | -0.018311 | 0.10071 | -0.022888 | -110.527 | -4.8111 | -111.7218 | 9.8602 | 9.9152 | -111.2595 | -111.5845 | 111.6623 | 111.5387 | -9.9976 | 111.5524 | 111.5936 | 0.054931 | -9.9289 | 0.30212 | -0.022889 | -0.11902 | 1.0345 | -0.16022 | -0.13733 | -0.064087 | 111.5433 | 111.6119 | 111.6074 | -10.0021 | 121.4218 | 121.4767 | 106.7505 | -121.5637
934.4219 | 121.7834 | -111.2366 | 10.2722 | 0.13611 | -0.039892 | -0.0032749 | 0.032738 | -0.014678 | -0.0060113 | 0.0086239 | 0.15945 | -0.009848 | 0.09888 | 0.073401 | 0.0046206 | -0.0049325 | 0.091553 | 0.07782 | 0.14191 | 0.07782 | -0.064087 | 0.13275 | 0.036621 | -110.1105 | -5.2094 | -111.3419 | 10.1715 | 10.2036 | -110.9161 | -111.2412 | 111.3693 | 111.2732 | -10.3363 | 111.3144 | 111.3144 | 0.041199 | -10.1807 | 0.32043 | -0.004578 | -0.10071 | 1.1261 | -0.10529 | -0.10071 | -0.068665 | 111.1725 | 111.3281 | 111.3785 | -10.2356 | 121.4081 | 121.4401 | 106.0272 | -121.5134
936.1719 | 121.7972 | -110.9894 | 10.5194 | -0.11566 | -0.039678 | -0.0037021 | 0.033806 | -0.014251 | -0.0077203 | 0.0045651 | -0.12283 | -0.013052 | 0.098239 | 0.071051 | 0.0039798 | -0.0085641 | 0.082397 | 0.10986 | 0.15106 | 0.07782 | -0.059509 | 0.13733 | 0.013733 | -109.8358 | -4.7928 | -111.0992 | 10.3821 | 10.4187 | -110.6964 | -111.0535 | 111.1267 | 111.0031 | -10.5789 | 111.0992 | 111.0672 | 0.064087 | -10.437 | 0.29297 | -0.064087 | -0.13733 | 1.1536 | -0.10986 | -0.045776 | -0.10071 | 110.9299 | 111.0718 | 111.1404 | -10.5057 | 121.3715 | 121.4081 | 106.1966 | -121.5729
937.8594 | 121.7422 | -111.6028 | 9.9243 | -0.1767 | -0.035619 | -0.0032749 | 0.036797 | -0.010406 | -0.0017389 | 0.0047787 | -0.20676 | -0.011557 | 0.10123 | 0.072119 | 0.00163 | -0.0087777 | 0.004578 | -0.054932 | 0.018311 | -0.004578 | 0.013733 | 0.091553 | -0.009155 | -110.4355 | -5.4977 | -111.7996 | 9.8282 | 9.8694 | -111.3602 | -111.676 | 111.6943 | 111.5936 | -9.9106 | 111.5479 | 111.5982 | 0.004577 | -9.9197 | 0.24262 | -0.073242 | -0.09613 | 1.1673 | -0.19684 | -0.1236 | -0.054931 | 111.6165 | 111.6074 | 111.6211 | -9.9335 | 121.431 | 121.4722 | 106.105 | -121.6003
939.5938 | 121.6187 | -83.931 | 37.3215 | 0.10559 | -0.033483 | -0.0062655 | 0.033592 | -0.013183 | -0.00024348 | 0.0071287 | -0.20676 | -0.010703 | 1.954 | 0.11228 | 1.8275 | -0.0094187 | 0.07782 | 0 | 0.073242 | 0.059509 | 0.004578 | 0.10986 | 0.009155 | -8.1848 | -3.9185 | -22.0367 | 36.9919 | 36.9553 | -83.9401 | -84.3109 | 84.0408 | 83.9401 | -37.3169 | 83.931 | 83.9905 | 0.050354 | -37.2437 | -0.009156 | -0.37994 | -0.32959 | 75.7462 | 61.8942 | 62.2742 | -0.36621 | 83.9355 | 84.0088 | 84.0042 | -37.3123 | 120.9229 | 120.8862 | 80.0125 | -121.6324
941.3438 | 121.582 | -96.7163 | 24.5087 | -0.19196 | -0.03391 | -0.0041293 | 0.035515 | -0.01361 | -0.0043023 | 0.0088377 | -0.18387 | -0.010062 | 2.353 | 0.11762 | 2.1951 | -0.0079233 | 0.036621 | -0.036621 | 0.059509 | 0.041199 | 0.009155 | 0.12817 | 0.027466 | -6.8069 | -4.8431 | -25.5844 | 24.9298 | 25.0076 | -95.5444 | -95.842 | 96.8445 | 96.7438 | -24.4995 | 96.6797 | 96.7575 | 0.013733 | -24.472 | 1.1719 | 0.87433 | 0.42114 | 89.9094 | 71.1319 | 70.2576 | 0.49896 | 96.7255 | 96.7529 | 96.7758 | -24.4812 | 121.6461 | 121.7239 | 91.8732 | -120.3506
943.0312 | 121.4722 | -113.9832 | 7.0404 | 0.12848 | -0.037542 | -0.0019931 | 0.032738 | -0.013824 | -0.0034479 | 0.0088377 | 0.17471 | -0.01113 | 3.5544 | 0.12766 | 3.3771 | -0.0057871 | 0.073242 | 0.022888 | 0.09613 | 0.054932 | 0.027466 | 0.16022 | 0.050354 | -6.2805 | -6.9305 | -4.2572 | 6.7566 | 6.7474 | -113.5666 | -113.8779 | 114.1434 | 114.0335 | -7.0129 | 114.006 | 114.0381 | 0.004578 | -6.9672 | 0.41657 | 0.10528 | -0.28381 | 107.7026 | 109.726 | 109.6207 | -0.29297 | 114.0106 | 114.0564 | 114.0793 | -6.9901 | 120.7397 | 120.7306 | 107.0526 | -120.9183
944.7812 | 121.4172 | -114.8666 | 6.1981 | 0.159 | -0.038183 | -0.0062655 | 0.033592 | -0.01361 | -0.0034479 | 0.0084103 | 0.16708 | -0.013266 | 3.5914 | 0.12681 | 3.4106 | -0.0064279 | 0.10986 | 0.091553 | 0.16022 | 0.11902 | -0.013733 | 0.19226 | 0.064087 | -5.8411 | -7.7683 | -3.8773 | 5.8456 | 5.8228 | -114.3402 | -114.6561 | 115.0589 | 114.9307 | -6.2119 | 114.9582 | 114.9857 | 0.054932 | -6.0883 | 0.52643 | 0.21057 | -0.35248 | 109.0256 | 110.9894 | 110.7788 | -0.37537 | 114.8529 | 114.9765 | 115.0269 | -6.134 | 120.7123 | 120.6894 | 107.0984 | -120.8542
946.5312 | 121.2296 | -115.2283 | 5.8319 | 0.021668 | -0.034979 | -0.0043429 | 0.035942 | -0.011687 | -0.00024348 | 0.0081967 | 0.045013 | -0.0083526 | 3.6053 | 0.13065 | 3.4226 | -0.0066415 | 0.032043 | -0.027466 | 0.054932 | 0.054932 | 0.004578 | 0.14191 | 0.013733 | -5.7358 | -7.869 | -3.9551 | 5.5023 | 5.5069 | -114.7156 | -115.0635 | 115.3702 | 115.242 | -5.8273 | 115.2008 | 115.2832 | 0.041199 | -5.7999 | 0.5127 | 0.16479 | -0.32959 | 109.4925 | 111.2732 | 111.1084 | -0.32501 | 115.2328 | 115.2603 | 115.2832 | -5.8182 | 120.7306 | 120.7352 | 107.3593 | -120.8954
948.2344 | 121.2433 | -115.3839 | 5.658 | -0.14618 | -0.03327 | -0.0054111 | 0.037651 | -0.012755 | -0.0019525 | 0.0081967 | -0.16861 | -0.013266 | 3.6115 | 0.12916 | 3.4269 | -0.0066415 | 0.022888 | -0.009155 | 0.073242 | 0.045776 | 0.009155 | 0.12817 | 0.032043 | -5.5801 | -7.6447 | -3.8223 | 5.3146 | 5.3055 | -114.8895 | -115.1916 | 115.5121 | 115.416 | -5.6488 | 115.3748 | 115.4297 | 0.013733 | -5.6351 | 0.49438 | 0.19226 | -0.34332 | 109.8038 | 111.5616 | 111.3693 | -0.35248 | 115.3931 | 115.4068 | 115.4572 | -5.6259 | 120.6985 | 120.6894 | 107.7393 | -120.8496
949.9844 | 121.2524 | -115.5167 | 5.4611 | 0.12848 | -0.039251 | -0.0051975 | 0.031242 | -0.014251 | -0.0057977 | 0.0054197 | 0.17471 | -0.012198 | 3.6153 | 0.12958 | 3.4343 | -0.0060007 | 0.09613 | 0.10986 | 0.1831 | 0.086975 | -0.027466 | 0.16479 | 0.064087 | -5.3558 | -7.5119 | -3.6713 | 5.1086 | 5.0812 | -114.9857 | -115.3244 | 115.6815 | 115.5807 | -5.4886 | 115.6265 | 115.6036 | 0.022888 | -5.365 | 0.53101 | 0.19226 | -0.35248 | 110.1608 | 111.8454 | 111.6531 | -0.37994 | 115.4892 | 115.6128 | 115.6998 | -5.397 | 120.6253 | 120.5978 | 108.0048 | -120.7855
951.6875 | 121.1609 | -115.7181 | 5.3009 | -0.14618 | -0.039678 | -0.0034885 | 0.035515 | -0.013183 | -0.0053705 | 0.0056333 | -0.16098 | -0.012411 | 3.6228 | 0.12852 | 3.4369 | -0.0055735 | 0.09613 | 0.091553 | 0.15106 | 0.10986 | -0.032043 | 0.14648 | 0.041199 | -5.4611 | -7.3563 | -3.6484 | 4.9484 | 4.9484 | -115.1276 | -115.4755 | 115.8646 | 115.7593 | -5.3329 | 115.8096 | 115.8279 | 0.068664 | -5.2048 | 0.59052 | 0.24262 | -0.35248 | 110.257 | 112.0697 | 111.8271 | -0.35248 | 115.686 | 115.8142 | 115.8691 | -5.2597 | 120.6665 | 120.6665 | 108.3618 | -120.7764
953.4375 | 121.1563 | -115.7318 | 5.2048 | -0.13855 | -0.035833 | -0.0043429 | 0.034233 | -0.014678 | -2.988e-05 | 0.0069151 | -0.17624 | -0.009848 | 3.6232 | 0.12766 | 3.4433 | -0.0092051 | 0.032043 | -0.027466 | 0.068665 | 0.054932 | -0.013733 | 0.12817 | 0.009155 | -5.4291 | -7.4615 | -3.6118 | 4.9026 | 4.8752 | -115.2328 | -115.5624 | 115.86 | 115.741 | -5.2185 | 115.7043 | 115.7867 | 0.045777 | -5.1727 | 0.49896 | 0.16937 | -0.30212 | 110.3027 | 112.1201 | 111.9507 | -0.32959 | 115.7181 | 115.7639 | 115.8005 | -5.1956 | 120.6345 | 120.607 | 108.2703 | -120.7672
955.1875 | 121.1792 | -115.773 | 5.0858 | 0.159 | -0.040319 | -0.0054111 | 0.031029 | -0.014464 | -0.0068659 | 0.0064877 | 0.13657 | -0.010703 | 3.6256 | 0.12531 | 3.4452 | -0.0055735 | 0.10529 | 0.10986 | 0.1831 | 0.086975 | -0.059509 | 0.15564 | 0.045776 | -5.3375 | -7.2418 | -3.5019 | 4.7607 | 4.7104 | -115.274 | -115.5899 | 115.9287 | 115.8188 | -5.1453 | 115.8829 | 115.86 | 0.041199 | -4.9805 | 0.49896 | 0.1831 | -0.32501 | 110.4355 | 112.2711 | 112.088 | -0.37537 | 115.7135 | 115.8783 | 115.9561 | -5.04 | 120.5338 | 120.4834 | 108.5312 | -120.6757
956.9531 | 121.1838 | -115.7776 | 5.0812 | 0.17426 | -0.037115 | -0.0019931 | 0.034019 | -0.013183 | -0.0036615 | 0.0073423 | 0.16708 | -0.012411 | 3.6249 | 0.12766 | 3.4465 | -0.0070689 | 0.11902 | 0.091553 | 0.16479 | 0.10986 | -0.036621 | 0.16479 | 0.054932 | -5.2002 | -7.4203 | -3.4973 | 4.7333 | 4.7195 | -115.2603 | -115.5991 | 115.9424 | 115.8325 | -5.1178 | 115.8691 | 115.8875 | 0.054931 | -4.9622 | 0.51727 | 0.17853 | -0.3479 | 110.5774 | 112.2803 | 112.1017 | -0.36163 | 115.741 | 115.8966 | 115.9424 | -5.0262 | 120.5109 | 120.4971 | 108.3572 | -120.6802
958.6562 | 121.0281 | -115.892 | 5.0262 | -0.19958 | -0.035833 | -0.0037021 | 0.03936 | -0.013824 | -0.0047297 | 0.0069151 | -0.099945 | -0.011984 | 3.6343 | 0.12766 | 3.4469 | -0.0070689 | 0.068665 | 0.022888 | 0.11444 | 0.054932 | -0.022888 | 0.1236 | 0.009155 | -5.5023 | -7.4524 | -3.5065 | 4.6875 | 4.6783 | -115.3198 | -115.6815 | 116.0156 | 115.9012 | -5.0491 | 115.9149 | 115.947 | 0.045777 | -4.9576 | 0.5722 | 0.21057 | -0.33875 | 110.3897 | 112.3856 | 112.175 | -0.3479 | 115.8691 | 115.9607 | 116.0065 | -5.0171 | 120.5795 | 120.5704 | 108.4396 | -120.7077
960.4219 | 121.0327 | -115.8188 | 5.0674 | -0.13855 | -0.038397 | -0.0026339 | 0.034447 | -0.012115 | -0.0045161 | 0.0075559 | -0.10757 | -0.014975 | 3.6286 | 0.1298 | 3.4476 | -0.0081369 | 0.09613 | 0.10529 | 0.16937 | 0.09613 | -0.045776 | 0.15564 | 0.050354 | -5.397 | -6.9031 | -3.3279 | 4.6967 | 4.6692 | -115.2786 | -115.6082 | 115.9744 | 115.8691 | -5.1132 | 115.9241 | 115.9149 | 0.045776 | -4.9713 | 0.54016 | 0.21057 | -0.37079 | 110.4218 | 112.4908 | 112.2803 | -0.39825 | 115.773 | 115.9149 | 115.9882 | -5.0171 | 120.5154 | 120.488 | 108.9157 | -120.6757
962.1094 | 120.9915 | -115.9103 | 4.9347 | -0.16907 | -0.03626 | -0.0019931 | 0.036156 | -0.013396 | -0.0040887 | 0.0081967 | -0.15335 | -0.012625 | 3.6365 | 0.12745 | 3.4495 | -0.0087777 | 0.018311 | 0.004578 | 0.059509 | 0.022888 | -0.022888 | 0.10529 | 0.004578 | -5.4382 | -7.2006 | -3.3829 | 4.6188 | 4.5914 | -115.3793 | -115.7043 | 116.0156 | 115.9149 | -4.9576 | 115.9149 | 115.9332 | 0.01831 | -4.9164 | 0.53101 | 0.20599 | -0.31586 | 110.4721 | 112.5275 | 112.3215 | -0.34332 | 115.8875 | 115.9286 | 115.9698 | -4.9301 | 120.5292 | 120.5017 | 108.7097 | -120.639
963.8594 | 120.9686 | -115.9103 | 4.9393 | 0.082703 | -0.035406 | -0.0054111 | 0.031883 | -0.014251 | 0.0023199 | 0.0081967 | 0.0068663 | -0.0092072 | 3.6369 | 0.12958 | 3.4561 | -0.0081369 | 0.018311 | -0.07782 | -0.004578 | 0 | -0.013733 | 0.086975 | -0.004578 | -5.3467 | -7.2693 | -3.3371 | 4.5868 | 4.6005 | -115.3702 | -115.7181 | 115.9973 | 115.9058 | -4.953 | 115.8325 | 115.9103 | 0.004578 | -4.921 | 0.54016 | 0.19226 | -0.35248 | 110.5637 | 112.5732 | 112.381 | -0.33874 | 115.8966 | 115.9286 | 115.9058 | -4.9438 | 120.4971 | 120.5109 | 108.6411 | -120.6573
965.5469 | 120.9503 | -115.7776 | 5.0354 | 0.075073 | -0.032629 | -0.0064791 | 0.036369 | -0.013183 | -0.0013117 | 0.0073423 | 0.045013 | -0.010275 | 3.6363 | 0.13172 | 3.4497 | -0.0092051 | -0.018311 | -0.073242 | 0.013733 | 0.004578 | -0.009155 | 0.11444 | 0.018311 | -5.3421 | -7.132 | -3.273 | 4.7241 | 4.6829 | -115.2466 | -115.5716 | 115.892 | 115.7959 | -5.0446 | 115.7043 | 115.7822 | -0.013733 | -5.0537 | 0.53101 | 0.20599 | -0.31128 | 110.4355 | 112.5046 | 112.2986 | -0.35248 | 115.7684 | 115.7593 | 115.7913 | -5.0171 | 120.5017 | 120.4605 | 108.6456 | -120.607
967.2969 | 121.0236 | -115.8508 | 4.8706 | 0.15137 | -0.039465 | -0.0047701 | 0.032097 | -0.011901 | -0.0055841 | 0.0079831 | 0.18234 | -0.012198 | 3.6367 | 0.1283 | 3.4551 | -0.0064279 | 0.10529 | 0.086975 | 0.15106 | 0.10529 | -0.064087 | 0.14191 | 0.041199 | -4.834 | -7.0129 | -3.0304 | 4.5136 | 4.5227 | -115.3107 | -115.6265 | 115.9927 | 115.892 | -4.9347 | 115.9378 | 115.9561 | 0.064087 | -4.7653 | 0.54016 | 0.2243 | -0.35705 | 111.0168 | 112.8204 | 112.5961 | -0.3479 | 115.7867 | 115.9561 | 116.0019 | -4.8294 | 120.3644 | 120.3735 | 108.8379 | -120.4971
969.0469 | 120.9686 | -115.8417 | 4.8294 | 0.14374 | -0.039892 | -0.0045565 | 0.030388 | -0.014464 | -0.0045161 | 0.0088377 | 0.1442 | -0.011984 | 3.6367 | 0.12766 | 3.4576 | -0.0051463 | 0.10529 | 0.09613 | 0.13733 | 0.086975 | -0.068665 | 0.16479 | 0.054932 | -4.6738 | -6.9901 | -2.9663 | 4.4861 | 4.4724 | -115.3702 | -115.6586 | 116.0065 | 115.8966 | -4.8981 | 115.9378 | 115.9286 | 0.032043 | -4.7241 | 0.4715 | 0.18311 | -0.34332 | 111.1679 | 112.8754 | 112.6923 | -0.35706 | 115.773 | 115.947 | 115.979 | -4.7745 | 120.3278 | 120.314 | 108.8516 | -120.488
970.8125 | 120.932 | -115.8417 | 4.8614 | 0.13611 | -0.039251 | -0.0034885 | 0.032738 | -0.015319 | -0.0010981 | 0.0092649 | 0.075531 | -0.0085662 | 3.6403 | 0.13065 | 3.4593 | -0.0085641 | 0.013733 | -0.068665 | -0.018311 | 0.004578 | -0.004578 | 0.10529 | 0 | -4.9896 | -6.6559 | -3.067 | 4.541 | 4.5364 | -115.3656 | -115.6815 | 115.947 | 115.8417 | -4.866 | 115.773 | 115.8463 | 0.004578 | -4.8477 | 0.47607 | 0.16022 | -0.32043 | 110.8521 | 112.7747 | 112.6144 | -0.32501 | 115.8371 | 115.8554 | 115.8234 | -4.8614 | 120.3827 | 120.3781 | 109.1858 | -120.5429
972.5 | 120.8771 | -115.8508 | 4.8843 | 0.059815 | -0.036047 | -0.0045565 | 0.032951 | -0.014678 | 0.00061092 | 0.0088377 | 0.037384 | -0.010275 | 3.6395 | 0.12873 | 3.4595 | -0.0074961 | 0 | -0.073242 | 0 | -0.004578 | -0.009155 | 0.10071 | -0.022888 | -4.9255 | -6.4224 | -3.0853 | 4.5593 | 4.541 | -115.3519 | -115.654 | 115.9515 | 115.8279 | -4.8935 | 115.7776 | 115.8463 | 0.01831 | -4.8843 | 0.49896 | 0.19684 | -0.32501 | 110.9253 | 112.7655 | 112.5687 | -0.34332 | 115.8417 | 115.8508 | 115.8508 | -4.9072 | 120.4102 | 120.3918 | 109.4284 | -120.5383
974.25 | 120.8954 | -115.8829 | 4.8065 | -0.14618 | -0.033056 | -0.0051975 | 0.039787 | -0.014251 | -0.00024348 | 0.0099057 | -0.14572 | -0.011771 | 3.6435 | 0.13151 | 3.4572 | -0.0074961 | 0.022888 | -0.013733 | 0.045776 | 0.027466 | -0.013733 | 0.1236 | -0.009155 | -4.7195 | -5.6351 | -2.9846 | 4.5044 | 4.4632 | -115.3931 | -115.7043 | 116.0065 | 115.8737 | -4.8203 | 115.8691 | 115.9103 | 0.036621 | -4.7836 | 0.48981 | 0.17853 | -0.30212 | 111.1633 | 112.8983 | 112.7197 | -0.34332 | 115.8691 | 115.9058 | 115.9287 | -4.8157 | 120.3873 | 120.3461 | 110.2478 | -120.5109
976 | 120.9412 | -115.8096 | 4.8203 | -0.10803 | -0.037756 | -0.0019931 | 0.03466 | -0.01361 | -0.01007 | 0.0060605 | -0.031281 | -0.011984 | 3.6371 | 0.12916 | 3.4512 | -0.0045053 | 0.07782 | 0.11902 | 0.17395 | 0.10071 | -0.059509 | 0.1236 | 0.032043 | -4.8157 | -5.571 | -2.8473 | 4.4632 | 4.454 | -115.2924 | -115.6082 | 115.9332 | 115.8417 | -4.8798 | 115.9286 | 115.9103 | 0.068665 | -4.7424 | 0.51727 | 0.20142 | -0.35705 | 110.994 | 112.9623 | 112.7609 | -0.36621 | 115.7501 | 115.8875 | 115.9836 | -4.7882 | 120.2728 | 120.2637 | 110.2386 | -120.4285
977.7656 | 120.8633 | -115.7043 | 4.9347 | 0.12085 | -0.037969 | -0.0030611 | 0.03167 | -0.014892 | -0.00045708 | 0.0075559 | 0.067902 | -0.01113 | 3.6371 | 0.13044 | 3.4544 | -0.0077097 | 0.009155 | -0.045776 | -0.013733 | 0.018311 | -0.018311 | 0.11444 | -0.004578 | -5.0949 | -5.2094 | -2.9938 | 4.6188 | 4.6005 | -115.2145 | -115.5396 | 115.8188 | 115.6998 | -4.953 | 115.6586 | 115.7227 | 0.022889 | -4.9255 | 0.48981 | 0.16479 | -0.31586 | 110.6094 | 112.7106 | 112.5458 | -0.33417 | 115.686 | 115.7135 | 115.6906 | -4.9393 | 120.3232 | 120.3049 | 110.495 | -120.4742
979.5312 | 120.9045 | -115.8691 | 4.6921 | 0.067444 | -0.039892 | -0.0047701 | 0.032524 | -0.014037 | -0.0030207 | 0.0056333 | 0.17471 | -0.010703 | 3.6386 | 0.13044 | 3.4542 | -0.0083505 | 0.10529 | 0.073242 | 0.10986 | 0.091553 | -0.054932 | 0.14648 | 0.050354 | -4.6921 | -5.7129 | -2.8656 | 4.3533 | 4.3442 | -115.3976 | -115.6998 | 116.0156 | 115.9195 | -4.747 | 115.9424 | 115.9607 | 0.041199 | -4.5868 | 0.4715 | 0.16937 | -0.33875 | 111.1771 | 113.0035 | 112.8342 | -0.3479 | 115.8142 | 115.9744 | 115.979 | -4.6417 | 120.2225 | 120.2133 | 110.1562 | -120.3918
981.2188 | 120.8954 | -115.7501 | 4.7836 | 0.159 | -0.036901 | -0.0066927 | 0.035515 | -0.014892 | -0.0023797 | 0.0092649 | 0.1442 | -0.009848 | 3.638 | 0.13407 | 3.4527 | -0.0083505 | 0.036621 | -0.018311 | 0.045776 | 0.018311 | -0.036621 | 0.11444 | 0.013733 | -4.8065 | -4.5547 | -2.8656 | 4.4632 | 4.454 | -115.2786 | -115.5899 | 115.8646 | 115.7639 | -4.8203 | 115.7318 | 115.7684 | 0.004578 | -4.747 | 0.4715 | 0.16022 | -0.32043 | 110.9436 | 112.8845 | 112.7243 | -0.32959 | 115.7135 | 115.7867 | 115.7959 | -4.7699 | 120.2133 | 120.2042 | 111.1954 | -120.3735
982.9062 | 120.7352 | -115.7867 | 4.8386 | 0.036926 | -0.037328 | -0.0037021 | 0.031029 | -0.015533 | 0.00018372 | 0.0084103 | 0.045013 | -0.0094208 | 3.6367 | 0.13065 | 3.4538 | -0.0087777 | 0.041199 | -0.050354 | 0.004578 | 0.013733 | -0.022888 | 0.10986 | 0.004578 | -4.9301 | -4.8019 | -2.9755 | 4.5181 | 4.509 | -115.2649 | -115.5853 | 115.8966 | 115.7913 | -4.8614 | 115.7364 | 115.8005 | 0.009155 | -4.7974 | 0.52185 | 0.20142 | -0.32043 | 110.8566 | 112.8113 | 112.6099 | -0.32959 | 115.7639 | 115.8279 | 115.7913 | -4.834 | 120.3049 | 120.2957 | 110.9848 | -120.4239
984.6406 | 120.8496 | -115.7089 | 4.8111 | 0.029297 | -0.041601 | -7.0528e-05 | 0.031242 | -0.014892 | -0.0085749 | 0.0060605 | 0.09079 | -0.012411 | 3.6354 | 0.12873 | 3.445 | -0.0049325 | 0.027466 | 0.013733 | 0.07782 | 0.050354 | -0.036621 | 0.13275 | 0.022888 | -4.66 | -4.7516 | -2.8839 | 4.4769 | 4.4815 | -115.2328 | -115.5304 | 115.8417 | 115.7318 | -4.8477 | 115.7227 | 115.7593 | 0.027466 | -4.7836 | 0.47607 | 0.17853 | -0.33417 | 111.0489 | 112.825 | 112.6465 | -0.32959 | 115.6723 | 115.7364 | 115.7867 | -4.7882 | 120.1859 | 120.1904 | 110.9573 | -120.3415
986.4062 | 120.7123 | -115.9058 | 4.6692 | -0.13855 | -0.034765 | -0.0034885 | 0.035515 | -0.015105 | -0.0057977 | 0.0041379 | -0.16861 | -0.012411 | 3.638 | 0.12852 | 3.4501 | -0.0083505 | 0.09613 | 0.073242 | 0.11902 | 0.07782 | -0.045776 | 0.13733 | 0.032043 | -4.6829 | -3.8864 | -2.8839 | 4.3304 | 4.3167 | -115.3885 | -115.6677 | 116.0431 | 115.9378 | -4.715 | 115.979 | 115.9836 | 0.045777 | -4.5731 | 0.51727 | 0.23804 | -0.33875 | 111.2228 | 113.0219 | 112.7838 | -0.35248 | 115.86 | 116.0019 | 116.0248 | -4.6371 | 120.2362 | 120.2225 | 112.0193 | -120.3369
988.1562 | 120.8313 | -115.6769 | 4.7974 | 0.17426 | -0.036474 | -0.0062655 | 0.032311 | -0.013396 | -0.0019525 | 0.0088377 | 0.067902 | -0.009848 | 3.6303 | 0.13044 | 3.4467 | -0.0068551 | 0.10986 | 0.045776 | 0.10071 | 0.068665 | -0.045776 | 0.15564 | 0.032043 | -4.5639 | -3.4607 | -2.8519 | 4.4861 | 4.4769 | -115.1642 | -115.48 | 115.8325 | 115.7089 | -4.8431 | 115.7227 | 115.7455 | 0.036622 | -4.6875 | 0.51269 | 0.19684 | -0.31128 | 111.113 | 112.825 | 112.6282 | -0.32043 | 115.6311 | 115.7867 | 115.7776 | -4.7653 | 120.163 | 120.1538 | 112.2162 | -120.2774
989.8438 | 120.7077 | -115.8463 | 4.7012 | -0.1767 | -0.036047 | -0.0047701 | 0.037224 | -0.014892 | -0.0032343 | 0.0086239 | -0.21439 | -0.010275 | 3.6331 | 0.13343 | 3.4461 | -0.0094187 | 0.013733 | -0.036621 | 0.004578 | 0.004578 | -0.022888 | 0.09613 | -0.022888 | -4.8981 | -3.1311 | -2.9755 | 4.3625 | 4.3716 | -115.3564 | -115.6677 | 115.9424 | 115.8234 | -4.7241 | 115.8096 | 115.8508 | 0.027466 | -4.6875 | 0.48981 | 0.17853 | -0.33875 | 110.9482 | 112.8708 | 112.6923 | -0.32959 | 115.8234 | 115.86 | 115.8508 | -4.7241 | 120.2087 | 120.2179 | 112.7151 | -120.369
991.6094 | 120.6619 | -115.686 | 4.8706 | -0.19958 | -0.037542 | -0.0045565 | 0.037437 | -0.012328 | -0.0043023 | 0.0060605 | -0.14572 | -0.012198 | 3.6288 | 0.13044 | 3.4427 | -0.0055735 | 0.07782 | 0.045776 | 0.091553 | 0.054932 | -0.022888 | 0.1236 | 0.009155 | -4.7607 | -2.8198 | -2.9297 | 4.5136 | 4.4907 | -115.1367 | -115.4846 | 115.8096 | 115.6952 | -4.8935 | 115.7318 | 115.741 | 0.045777 | -4.7928 | 0.54932 | 0.20142 | -0.35705 | 110.9253 | 112.7563 | 112.5549 | -0.37994 | 115.6631 | 115.7639 | 115.7776 | -4.8615 | 120.1996 | 120.1767 | 112.8662 | -120.3552
993.3594 | 120.7214 | -115.8691 | 4.6005 | 0.13611 | -0.036688 | -0.0081881 | 0.031029 | -0.016387 | -0.00024348 | 0.0084103 | 0.052643 | -0.008139 | 3.6346 | 0.13108 | 3.4514 | -0.0062143 | 0.036621 | -0.054932 | -0.022888 | -0.009155 | -0.013733 | 0.09613 | -0.004578 | -4.8019 | -2.9755 | -2.9617 | 4.2801 | 4.2709 | -115.3931 | -115.7272 | 115.9653 | 115.8646 | -4.6143 | 115.8142 | 115.86 | -0.004577 | -4.5639 | 0.47607 | 0.14191 | -0.32043 | 111.0672 | 112.9074 | 112.7655 | -0.32959 | 115.8554 | 115.9058 | 115.8463 | -4.6051 | 120.1492 | 120.1401 | 112.8937 | -120.3278
995.1094 | 120.7489 | -115.9744 | 4.4586 | -0.069885 | -0.034979 | -0.0032749 | 0.037224 | -0.015319 | -0.0083613 | 0.0073423 | -0.092316 | -0.013693 | 3.6393 | 0.13044 | 3.4484 | -0.0060007 | 0.10529 | 0.12817 | 0.17853 | 0.10071 | -0.054932 | 0.13733 | 0.022888 | -4.541 | -2.6962 | -2.8015 | 4.1061 | 4.097 | -115.48 | -115.8096 | 116.1118 | 115.9973 | -4.5136 | 116.1026 | 116.0751 | 0.07782 | -4.3533 | 0.49438 | 0.16479 | -0.35248 | 111.4334 | 113.1729 | 113.0081 | -0.36163 | 115.9195 | 116.0797 | 116.153 | -4.4357 | 120.0806 | 120.0714 | 113.2782 | -120.2682
996.8125 | 120.6619 | -116.0202 | 4.4403 | -0.14618 | -0.036688 | -0.0043429 | 0.034874 | -0.014251 | 0.00039732 | 0.0073423 | -0.19913 | -0.009848 | 3.6386 | 0.1345 | 3.4512 | -0.0083505 | 0.022888 | -0.036621 | 0.004578 | 0.036621 | -0.013733 | 0.10071 | -0.004578 | -4.8477 | -2.7512 | -2.9388 | 4.1107 | 4.1061 | -115.5304 | -115.8417 | 116.1209 | 116.0156 | -4.454 | 115.9836 | 116.0568 | 0.041199 | -4.4174 | 0.48981 | 0.17853 | -0.32959 | 111.1725 | 113.0814 | 112.9028 | -0.33417 | 116.0065 | 116.0431 | 116.0248 | -4.4449 | 120.1309 | 120.1263 | 113.269 | -120.282
998.5625 | 120.5841 | -116.0294 | 4.4083 | -0.0088499 | -0.034765 | -0.0071201 | 0.033165 | -0.012969 | -0.0010981 | 0.0094785 | -0.016022 | -0.009848 | 3.6709 | 0.16099 | 3.4499 | -0.0074961 | 0.059509 | -0.009155 | 0.027466 | 0.041199 | -0.036621 | 0.11444 | -0.004578 | -4.8614 | -2.5131 | -2.9617 | 4.0604 | 4.0924 | -115.5487 | -115.8691 | 116.1438 | 116.0248 | -4.4449 | 116.0202 | 116.0706 | 0.045777 | -4.3488 | 0.48065 | 0.16022 | -0.3479 | 111.1679 | 113.0676 | 112.9074 | -0.31586 | 115.9927 | 116.0889 | 116.0568 | -4.4128 | 120.0897 | 120.1218 | 113.5162 | -120.2774
1000.25 | 120.5795 | -115.8829 | 4.5776 | -0.1767 | -0.035619 | -0.0045565 | 0.037651 | -0.016601 | -0.0057977 | 0.0062741 | -0.17624 | -0.010703 | 3.7236 | 0.21482 | 3.445 | -0.0036509 | 0.013733 | 0 | 0.041199 | 0.027466 | -0.032043 | 0.091553 | 0 | -4.8798 | -2.4033 | -2.9205 | 4.2435 | 4.216 | -115.3381 | -115.6723 | 115.9744 | 115.8829 | -4.6097 | 115.8829 | 115.9103 | 0.027466 | -4.5639 | 0.54474 | 0.21057 | -0.33417 | 111.0031 | 112.9623 | 112.7518 | -0.36163 | 115.8508 | 115.8966 | 115.9241 | -4.5776 | 120.1263 | 120.0989 | 113.4796 | -120.2499
1002.0156 | 120.6207 | -115.9607 | 4.4632 | -0.14618 | -0.03391 | -0.0045565 | 0.035088 | -0.011901 | -0.0010981 | 0.0069151 | -0.18387 | -0.011557 | 3.641 | 0.13535 | 3.4493 | -0.0085641 | 0.022888 | -0.032043 | 0.013733 | 0.032043 | -0.032043 | 0.09613 | 0.004578 | -4.8203 | -2.417 | -2.9205 | 4.1382 | 4.1016 | -115.4434 | -115.7822 | 116.0568 | 115.9653 | -4.4952 | 115.9287 | 115.9927 | 0.027465 | -4.4403 | 0.51727 | 0.17853 | -0.32501 | 111.1404 | 113.0402 | 112.8616 | -0.36163 | 115.9287 | 115.9836 | 115.9744 | -4.4586 | 120.0989 | 120.0623 | 113.5437 | -120.2454
1003.7656 | 120.6848 | -115.9698 | 4.3808 | -0.11566 | -0.036901 | -0.0043429 | 0.035515 | -0.013396 | -0.010284 | 0.0064877 | -0.031281 | -0.013266 | 3.644 | 0.13087 | 3.4446 | -0.0060007 | 0.086975 | 0.10986 | 0.15106 | 0.086975 | -0.036621 | 0.1236 | 0.027466 | -4.6188 | -1.8677 | -2.8061 | 4.0237 | 4.0146 | -115.4755 | -115.8096 | 116.0934 | 115.9973 | -4.4174 | 116.0797 | 116.0568 | 0.059509 | -4.2938 | 0.49438 | 0.16022 | -0.35706 | 111.351 | 113.1638 | 113.0035 | -0.36621 | 115.9332 | 116.0568 | 116.1209 | -4.3533 | 119.9936 | 119.9844 | 114.1022 | -120.1904
1005.4531 | 120.6573 | -115.8829 | 4.4449 | 0.082703 | -0.036474 | -0.0071201 | 0.031456 | -0.01361 | -0.0013117 | 0.0075559 | 0.12131 | -0.011557 | 3.6341 | 0.13428 | 3.4448 | -0.0077097 | 0.027466 | -0.041199 | 0.036621 | 0.022888 | -0.022888 | 0.10529 | 0.004578 | -4.6051 | -1.9318 | -3.067 | 4.1656 | 4.1245 | -115.3976 | -115.741 | 115.9882 | 115.8875 | -4.4678 | 115.8417 | 115.9058 | 0.01831 | -4.4174 | 0.48523 | 0.14191 | -0.27924 | 111.2778 | 112.8159 | 112.6739 | -0.32043 | 115.86 | 115.9103 | 115.9195 | -4.4403 | 120.0485 | 120.0073 | 113.9511 | -120.1859
1007.2188 | 120.5612 | -115.8234 | 4.5319 | 0.10559 | -0.038397 | -0.0028475 | 0.029106 | -0.015319 | 0.0010381 | 0.0090513 | 0.098419 | -0.00878 | 3.6333 | 0.13236 | 3.4425 | -0.0051463 | 0 | -0.045776 | 0.009155 | 0.009155 | -0.027466 | 0.1236 | 0.009155 | -4.6875 | -3.0212 | -3.0762 | 4.216 | 4.2114 | -115.3336 | -115.6723 | 115.947 | 115.8325 | -4.5593 | 115.7776 | 115.8325 | 0 | -4.5319 | 0.48981 | 0.15106 | -0.31586 | 111.1359 | 112.7472 | 112.5961 | -0.32043 | 115.7959 | 115.8234 | 115.8325 | -4.5227 | 120.0394 | 120.0348 | 112.8021 | -120.2042
1008.9688 | 120.52 | -115.8966 | 4.4861 | 0.036926 | -0.034979 | -0.0056247 | 0.029747 | -0.014037 | -0.0028071 | 0.0079831 | 0.029755 | -0.0096344 | 3.6337 | 0.13407 | 3.4422 | -0.0062143 | 0.004578 | -0.050354 | 0.009155 | 0.018311 | -0.032043 | 0.086975 | -0.018311 | -4.9484 | -2.2797 | -3.1494 | 4.1382 | 4.1336 | -115.3931 | -115.7455 | 115.9836 | 115.8783 | -4.5181 | 115.8463 | 115.9149 | 0.036622 | -4.4815 | 0.50354 | 0.15106 | -0.3479 | 110.9482 | 112.7472 | 112.5961 | -0.35248 | 115.8646 | 115.9012 | 115.9058 | -4.5044 | 120.0348 | 120.0302 | 113.6169 | -120.2316
1010.6562 | 120.5063 | -115.947 | 4.422 | 0.052185 | -0.037756 | -0.0049837 | 0.033592 | -0.014464 | -0.0023797 | 0.012042 | 0.067902 | -0.010489 | 3.6384 | 0.13578 | 3.4427 | -0.0068551 | -0.027466 | -0.07782 | 0.009155 | 0 | 0.004578 | 0.10986 | 0.009155 | -4.8065 | -2.0874 | -3.0899 | 4.0649 | 4.0741 | -115.4572 | -115.7593 | 116.0568 | 115.9561 | -4.4174 | 115.8691 | 115.947 | -0.009155 | -4.4495 | 0.48981 | 0.18768 | -0.35706 | 111.1404 | 112.8571 | 112.6694 | -0.3479 | 115.9515 | 115.9195 | 115.9561 | -4.4128 | 120.0119 | 120.0211 | 113.8596 | -120.1813
1012.4062 | 120.6116 | -115.9744 | 4.2938 | 0.13611 | -0.038397 | -0.0037021 | 0.033165 | -0.013183 | -0.0034479 | 0.0075559 | 0.18234 | -0.0094208 | 3.6354 | 0.13236 | 3.4437 | -0.0070689 | 0.036621 | -0.018311 | 0.045776 | 0.018311 | -0.027466 | 0.10529 | 0.013733 | -4.7424 | -1.7441 | -3.0212 | 3.9734 | 3.9734 | -115.4938 | -115.8188 | 116.0797 | 115.9882 | -4.3213 | 115.9561 | 115.9927 | 0.004578 | -4.2572 | 0.48065 | 0.15564 | -0.32043 | 111.232 | 112.9532 | 112.7975 | -0.32043 | 115.947 | 116.011 | 116.0202 | -4.2801 | 119.9478 | 119.9478 | 114.2303 | -120.1126
1014.1562 | 120.5933 | -115.9287 | 4.3213 | 0.12848 | -0.037542 | -0.0047701 | 0.032524 | -0.01361 | -0.0030207 | 0.0071287 | 0.17471 | -0.0089936 | 3.6634 | 0.15864 | 3.4437 | -0.0051463 | 0.050354 | -0.032043 | 0.041199 | 0.018311 | -0.041199 | 0.11902 | -0.004578 | -4.4357 | -1.5656 | -2.948 | 3.9963 | 3.978 | -115.4663 | -115.7867 | 116.0477 | 115.9241 | -4.3625 | 115.8966 | 115.947 | 0.022889 | -4.2709 | 0.46234 | 0.14191 | -0.32501 | 111.4929 | 112.9807 | 112.8387 | -0.34332 | 115.8875 | 115.979 | 115.9698 | -4.3259 | 119.9249 | 119.9066 | 114.3631 | -120.108
1015.9062 | 120.4376 | -115.8279 | 4.4724 | -0.0088499 | -0.03327 | -0.0049837 | 0.036369 | -0.01361 | -0.0015253 | 0.0099057 | -0.016022 | -0.010275 | 3.7431 | 0.23832 | 3.441 | -0.0062143 | 0.050354 | -0.004578 | 0.059509 | 0.041199 | -0.050354 | 0.086975 | -0.018311 | -4.5547 | -1.3962 | -2.9388 | 4.1245 | 4.1336 | -115.3107 | -115.6448 | 115.9149 | 115.8096 | -4.5227 | 115.8234 | 115.8691 | 0.05951 | -4.422 | 0.51727 | 0.18311 | -0.3479 | 111.2732 | 112.8891 | 112.706 | -0.33874 | 115.7776 | 115.8783 | 115.8875 | -4.4907 | 119.9524 | 119.9615 | 114.4318 | -120.1172
1017.5938 | 120.4788 | -115.9195 | 4.3671 | -0.069885 | -0.036901 | -0.0047701 | 0.034019 | -0.014037 | 0.00039732 | 0.0081967 | -0.077057 | -0.0092072 | 3.6429 | 0.13642 | 3.4422 | -0.0070689 | 0.064087 | 0 | 0.064087 | 0.050354 | -0.022888 | 0.09613 | -0.013733 | -4.4861 | -1.2131 | -2.9068 | 4.0237 | 4.0329 | -115.4205 | -115.7272 | 116.0156 | 115.9058 | -4.39 | 115.9195 | 115.9698 | 0.064087 | -4.303 | 0.49896 | 0.19226 | -0.34332 | 111.4334 | 113.0127 | 112.8204 | -0.33417 | 115.8966 | 115.9836 | 115.9836 | -4.3808 | 119.9432 | 119.9524 | 114.7064 | -120.0943
1019.3438 | 120.575 | -115.9058 | 4.303 | 0.014038 | -0.037542 | -0.0037021 | 0.03466 | -0.014251 | -0.01007 | 0.0052061 | 0.045013 | -0.01412 | 3.6463 | 0.13813 | 3.436 | -0.0040781 | 0.041199 | 0.027466 | 0.11444 | 0.059509 | -0.059509 | 0.13733 | 0.027466 | -4.3304 | -1.0483 | -2.8427 | 3.9825 | 3.9642 | -115.4343 | -115.7639 | 116.0431 | 115.9332 | -4.3625 | 115.9332 | 115.9653 | 0.032043 | -4.2618 | 0.4715 | 0.14191 | -0.32043 | 111.5753 | 113.063 | 112.9211 | -0.33875 | 115.8463 | 115.947 | 116.0202 | -4.2755 | 119.8883 | 119.87 | 114.8575 | -120.0668
1021.0312 | 120.4193 | -115.86 | 4.4037 | 0.082703 | -0.036688 | -0.0041293 | 0.029533 | -0.015105 | -2.988e-05 | 0.0075559 | 0.022125 | -0.0092072 | 3.6435 | 0.13898 | 3.4401 | -0.0081369 | 0 | -0.082397 | -0.018311 | 0.009155 | -0.022888 | 0.086975 | -0.009155 | -4.5044 | -0.9613 | -3.0029 | 4.0833 | 4.0649 | -115.3473 | -115.686 | 115.947 | 115.8508 | -4.4266 | 115.7776 | 115.8691 | 0.01831 | -4.4037 | 0.51269 | 0.17395 | -0.32043 | 111.3556 | 112.8571 | 112.6831 | -0.33875 | 115.8371 | 115.86 | 115.8417 | -4.4128 | 119.9432 | 119.9249 | 114.8987 | -120.0897
1022.7812 | 120.4468 | -115.8646 | 4.3533 | -0.14618 | -0.034338 | -0.0030611 | 0.037437 | -0.012328 | -0.0081477 | 0.0062741 | -0.077057 | -0.013052 | 3.645 | 0.14133 | 3.4346 | -0.0040781 | 0.091553 | 0.086975 | 0.14648 | 0.086975 | -0.068665 | 0.13733 | 0.004578 | -4.3488 | -0.56763 | -2.8839 | 3.9917 | 3.9963 | -115.3748 | -115.686 | 116.0019 | 115.8691 | -4.422 | 115.9515 | 115.9515 | 0.082397 | -4.2618 | 0.48981 | 0.17853 | -0.36163 | 111.5158 | 112.9807 | 112.8021 | -0.35706 | 115.7959 | 115.9561 | 116.011 | -4.3488 | 119.8563 | 119.8608 | 115.2969 | -120.0394
1024.4688 | 120.3918 | -115.9332 | 4.3304 | -0.16144 | -0.036688 | -0.0034885 | 0.032311 | -0.016814 | -0.0053705 | 0.0043515 | -0.14572 | -0.013052 | 3.6501 | 0.14261 | 3.4373 | -0.0023691 | 0.018311 | -0.027466 | 0.041199 | 0 | -0.045776 | 0.07782 | -0.032043 | -4.3991 | -0.6546 | -2.9434 | 3.9963 | 3.9642 | -115.4663 | -115.7684 | 116.011 | 115.9012 | -4.3762 | 115.9058 | 115.9332 | 0.032043 | -4.3121 | 0.46692 | 0.16479 | -0.33417 | 111.5341 | 112.9898 | 112.825 | -0.36621 | 115.8875 | 115.9515 | 115.9744 | -4.3625 | 119.9295 | 119.8975 | 115.2786 | -120.0989
1026.2031 | 120.3873 | -115.8554 | 4.39 | 0.067444 | -0.036047 | -0.0075473 | 0.031242 | -0.013824 | -0.00088448 | 0.0067013 | 0.060272 | -0.011343 | 3.6508 | 0.14924 | 3.435 | -0.0030099 | -0.013733 | -0.10986 | -0.018311 | -0.009155 | -0.041199 | 0.068665 | -0.036621 | -4.6326 | -0.72327 | -2.9663 | 4.0649 | 4.0466 | -115.3427 | -115.6906 | 115.9241 | 115.8188 | -4.4312 | 115.7455 | 115.8463 | 0.027466 | -4.4037 | 0.5127 | 0.16479 | -0.32501 | 111.2228 | 112.8891 | 112.7243 | -0.34332 | 115.8142 | 115.8417 | 115.8371 | -4.4266 | 119.9203 | 119.902 | 115.1321 | -120.0806
1027.9531 | 120.369 | -115.7639 | 4.4907 | 0.11322 | -0.037115 | -0.0047701 | 0.032524 | -0.013396 | -2.988e-05 | 0.0058469 | 0.045013 | -0.010275 | 3.6478 | 0.14625 | 3.4335 | -0.0019419 | -0.013733 | -0.1236 | -0.036621 | -0.027466 | -0.050354 | 0.054932 | -0.045776 | -4.5502 | -1.0025 | -2.9709 | 4.1428 | 4.1656 | -115.2557 | -115.5624 | 115.8188 | 115.7181 | -4.541 | 115.6403 | 115.7364 | 0.01831 | -4.5044 | 0.50812 | 0.20142 | -0.3479 | 111.2137 | 112.793 | 112.5916 | -0.32501 | 115.7135 | 115.7501 | 115.7272 | -4.5364 | 119.9066 | 119.9295 | 114.7614 | -120.0531
1029.7031 | 120.3964 | -115.7043 | 4.4815 | -0.024109 | -0.032415 | -0.0077609 | 0.037651 | -0.0012198 | -0.0028071 | -0.0059023 | -0.12283 | -0.0094208 | 3.7023 | 0.15372 | 3.4279 | 0.046337 | -0.13275 | -0.18768 | -0.24261 | -0.15106 | -0.21973 | -0.17395 | -0.27924 | -4.7287 | -1.3367 | -2.861 | 4.1382 | 4.1245 | -115.2191 | -115.535 | 115.5304 | 115.4251 | -4.7012 | 115.5167 | 115.5533 | 0.12817 | -4.6143 | 0.48523 | 0.16937 | -0.34332 | 110.9756 | 112.8433 | 112.6739 | -0.35706 | 115.4846 | 115.5716 | 115.4617 | -4.7607 | 119.8425 | 119.8288 | 114.3677 | -120.0165
1031.3906 | 120.3232 | -115.892 | 4.3167 | -0.19196 | -0.038397 | -0.0028475 | 0.03466 | -0.012755 | -0.0064387 | 0.0062741 | -0.13809 | -0.011343 | 3.6572 | 0.15607 | 3.4294 | -0.0057871 | 0.050354 | 0.054932 | 0.10529 | 0.059509 | -0.054932 | 0.10986 | -0.022888 | -4.0741 | -0.52185 | -2.9022 | 3.978 | 3.9688 | -115.361 | -115.6815 | 116.0019 | 115.8691 | -4.3716 | 115.947 | 115.9515 | 0.082397 | -4.2664 | 0.53101 | 0.21057 | -0.33874 | 111.8179 | 112.9898 | 112.7792 | -0.3479 | 115.8371 | 115.9424 | 115.9973 | -4.3396 | 119.87 | 119.8608 | 115.3702 | -119.9982
1033.1406 | 120.401 | -115.6586 | 4.4724 | 0.15137 | -0.042669 | -0.0049837 | 0.031029 | -0.017455 | -0.0072931 | 0.0073423 | 0.17471 | -0.011984 | 3.6519 | 0.15073 | 3.4307 | -0.0042917 | 0.073242 | 0.073242 | 0.13733 | 0.064087 | -0.073242 | 0.13275 | 0.027466 | -4.1428 | -0.49896 | -2.7924 | 4.1245 | 4.1016 | -115.1916 | -115.48 | 115.7913 | 115.686 | -4.5456 | 115.7318 | 115.7227 | 0.036621 | -4.3991 | 0.46692 | 0.17853 | -0.3479 | 111.5158 | 112.8662 | 112.6877 | -0.37079 | 115.5853 | 115.7318 | 115.7959 | -4.4449 | 119.783 | 119.7601 | 115.1596 | -119.9524
1034.8906 | 120.401 | -115.741 | 4.4128 | 0.10559 | -0.040106 | -0.0034885 | 0.032951 | -0.016387 | -0.0053705 | 0.0060605 | 0.1442 | -0.012411 | 3.6698 | 0.1674 | 3.429 | -0.0023691 | 0.050354 | 0.050354 | 0.10529 | 0.045776 | -0.073242 | 0.10986 | 0.018311 | -4.1016 | -0.49896 | -2.8931 | 4.0833 | 4.0512 | -115.1413 | -115.5212 | 115.8508 | 115.7593 | -4.4861 | 115.7913 | 115.7867 | 0.027465 | -4.3625 | 0.59967 | 0.21973 | -0.32959 | 111.6394 | 112.8479 | 112.6282 | -0.36163 | 115.6677 | 115.7913 | 115.8463 | -4.3945 | 119.8242 | 119.7922 | 115.242 | -119.9341
1036.5938 | 120.3323 | -115.6219 | 4.5044 | -0.21484 | -0.036901 | -0.0058383 | 0.033379 | -0.01596 | -0.00024348 | 0.0060605 | -0.13809 | -0.011343 | 3.6854 | 0.18555 | 3.4243 | -0.0038645 | -0.004578 | -0.068665 | 0 | 0.004578 | -0.032043 | 0.07782 | -0.036621 | -4.2252 | -2.2659 | -2.9892 | 4.2023 | 4.1611 | -115.1688 | -115.48 | 115.6998 | 115.5853 | -4.5364 | 115.5533 | 115.6265 | 0.041199 | -4.509 | 0.45319 | 0.14191 | -0.30212 | 111.3968 | 112.6328 | 112.4908 | -0.34332 | 115.5899 | 115.6174 | 115.6219 | -4.541 | 119.8242 | 119.783 | 113.356 | -119.9844
1038.3438 | 120.3735 | -115.6265 | 4.4586 | 0.17426 | -0.036474 | -0.0056247 | 0.03167 | -0.01596 | -0.0028071 | 0.0056333 | 0.15182 | -0.013693 | 3.6805 | 0.1832 | 3.4239 | 0.0016897 | 0.091553 | 0.064087 | 0.12817 | 0.073242 | -0.10071 | 0.10986 | 0.013733 | -4.0466 | -2.179 | -2.8931 | 4.1016 | 4.1061 | -115.1276 | -115.4297 | 115.7364 | 115.6403 | -4.5593 | 115.6906 | 115.6998 | 0.059509 | -4.3671 | 0.49896 | 0.19684 | -0.35706 | 111.5799 | 112.7335 | 112.5366 | -0.35248 | 115.5258 | 115.7181 | 115.7547 | -4.4449 | 119.7281 | 119.7327 | 113.4476 | -119.8883
1040.0781 | 120.3049 | -115.6357 | 4.5273 | -0.10803 | -0.034765 | -0.0049837 | 0.032524 | -0.014678 | -0.0047297 | 0.0058469 | -0.20676 | -0.010062 | 3.7168 | 0.19901 | 3.4234 | -0.0021555 | -0.027466 | -0.050354 | 0.004578 | -0.022888 | -0.086975 | 0.068665 | -0.054932 | -4.1153 | -3.1952 | -2.9617 | 4.2023 | 4.1931 | -115.1596 | -115.4434 | 115.7043 | 115.5807 | -4.6143 | 115.5853 | 115.6128 | 0.032044 | -4.5547 | 0.47607 | 0.19226 | -0.32501 | 111.5204 | 112.674 | 112.4817 | -0.33417 | 115.5487 | 115.6082 | 115.6403 | -4.5822 | 119.838 | 119.8288 | 112.4405 | -119.9707
1041.8438 | 120.3186 | -115.7455 | 4.4174 | -0.16144 | -0.038183 | -0.0015659 | 0.032524 | -0.0097646 | -0.0023797 | 0.0041379 | -0.18387 | -0.011771 | 3.6807 | 0.17295 | 3.4284 | 0.01643 | -0.009155 | -0.064087 | 0 | -0.004578 | -0.07782 | 0.045776 | -0.068665 | -4.3304 | -2.6825 | -2.9251 | 4.0878 | 4.0558 | -115.2374 | -115.5624 | 115.7913 | 115.6769 | -4.4952 | 115.6815 | 115.741 | 0.064087 | -4.4266 | 0.50812 | 0.1831 | -0.32959 | 111.4151 | 112.8204 | 112.6373 | -0.36163 | 115.6677 | 115.7364 | 115.7455 | -4.4861 | 119.8334 | 119.8013 | 113.063 | -119.9799
1043.5312 | 120.3827 | -115.6815 | 4.3991 | -0.10803 | -0.037969 | -0.00092493 | 0.035942 | -0.012969 | -0.0068659 | 0.0058469 | -0.14572 | -0.013693 | 3.6559 | 0.14475 | 3.4245 | -1.9284e-05 | 0.091553 | 0.082397 | 0.13733 | 0.073242 | -0.09613 | 0.11444 | 0.027466 | -4.129 | -4.2618 | -2.6962 | 4.0192 | 4.0329 | -115.1871 | -115.5029 | 115.7959 | 115.7089 | -4.4952 | 115.7639 | 115.7547 | 0.045776 | -4.3076 | 0.49439 | 0.17853 | -0.37994 | 111.5524 | 112.9852 | 112.8067 | -0.36621 | 115.5853 | 115.773 | 115.8188 | -4.3716 | 119.7006 | 119.7144 | 111.4197 | -119.902
1045.2656 | 120.2774 | -115.7135 | 4.4128 | -0.046997 | -0.033483 | -0.0041293 | 0.031242 | -0.012328 | 0.00039732 | 0.0081967 | -0.13046 | -0.010275 | 3.6702 | 0.16312 | 3.4309 | -0.0036509 | 0.073242 | 0.018311 | 0.064087 | 0.041199 | -0.041199 | 0.10071 | 0 | -4.0054 | -0.33417 | -2.774 | 4.0741 | 4.0512 | -115.2054 | -115.5258 | 115.8142 | 115.7135 | -4.454 | 115.7318 | 115.7547 | 0.041199 | -4.3396 | 0.50812 | 0.18768 | -0.33875 | 111.7081 | 112.9395 | 112.7518 | -0.36163 | 115.6723 | 115.7867 | 115.7776 | -4.4128 | 119.7876 | 119.7647 | 115.3793 | -119.9387
1047.0312 | 120.2728 | -115.6174 | 4.4769 | -0.13092 | -0.037542 | -0.0034885 | 0.034447 | -0.015105 | -0.0075067 | 0.0090513 | -0.10757 | -0.011557 | 3.6495 | 0.14304 | 3.4247 | -0.0019419 | 0.10071 | 0.10071 | 0.15564 | 0.10071 | -0.073242 | 0.1236 | 0.032043 | -3.9871 | 0.14191 | -2.6962 | 4.1382 | 4.1199 | -115.1047 | -115.3885 | 115.741 | 115.6494 | -4.5502 | 115.7181 | 115.7181 | 0.068665 | -4.3762 | 0.5127 | 0.22888 | -0.33875 | 111.6302 | 112.9211 | 112.6923 | -0.35706 | 115.5441 | 115.7181 | 115.773 | -4.4449 | 119.7556 | 119.7372 | 115.7593 | -119.8654
1048.7031 | 120.369 | -115.6357 | 4.39 | 0.16663 | -0.037756 | -0.0026339 | 0.028252 | -0.011901 | -0.0010981 | 0.0073423 | 0.12894 | -0.012625 | 3.6469 | 0.1424 | 3.4273 | -0.0040781 | 0.073242 | 0.009155 | 0.086975 | 0.036621 | -0.050354 | 0.13275 | 0.022888 | -3.9642 | -0.27008 | -2.7283 | 4.0695 | 4.0695 | -115.1505 | -115.4434 | 115.7684 | 115.6586 | -4.4403 | 115.6448 | 115.6723 | 0.013733 | -4.3167 | 0.48523 | 0.19226 | -0.32044 | 111.6714 | 112.9074 | 112.7151 | -0.32044 | 115.5853 | 115.7089 | 115.7227 | -4.3671 | 119.7052 | 119.7052 | 115.3656 | -119.8334
1050.4531 | 120.2271 | -115.7593 | 4.3533 | -0.024109 | -0.037542 | -0.0062655 | 0.036156 | -0.014464 | 0.0012519 | 0.0052061 | -0.092316 | -0.01113 | 3.6724 | 0.16996 | 3.429 | 0.0019033 | 0.064087 | 0 | 0.07782 | 0.036621 | -0.045776 | 0.10986 | -0.018311 | -4.1519 | -0.33875 | -2.7557 | 4.01 | 4.01 | -115.2649 | -115.5807 | 115.8691 | 115.741 | -4.3991 | 115.7593 | 115.7959 | 0.054932 | -4.2892 | 0.49438 | 0.17853 | -0.34332 | 111.6074 | 113.0035 | 112.825 | -0.34332 | 115.7135 | 115.8234 | 115.8371 | -4.3716 | 119.7693 | 119.7693 | 115.4205 | -119.9341
1052.2031 | 120.2728 | -115.4022 | 4.5959 | 0.12085 | -0.038183 | -0.0032749 | 0.031883 | -0.011687 | -0.0019525 | 0.0064877 | 0.098419 | -0.011343 | 3.8815 | 0.1486 | 3.4209 | -0.00087368 | -0.054932 | -0.11444 | -0.059509 | -0.027466 | -0.091553 | 0.054932 | -0.059509 | -4.184 | -0.40283 | -2.7237 | 4.2755 | 4.2343 | -114.9719 | -115.2649 | 115.4572 | 115.3427 | -4.6875 | 115.2878 | 115.3748 | 0.032043 | -4.6509 | 0.4303 | 0.13733 | -0.32043 | 111.2183 | 112.6785 | 112.5412 | -0.36163 | 115.3107 | 115.3473 | 115.3427 | -4.6555 | 119.6777 | 119.6365 | 114.9994 | -119.8608
1053.9531 | 120.2499 | -115.6906 | 4.39 | -0.13092 | -0.038397 | -0.0017795 | 0.033165 | -0.005065 | -0.0068659 | -0.0029117 | -0.084686 | -0.011984 | 3.7798 | 0.14582 | 3.4252 | 0.040569 | -0.054932 | -0.022888 | -0.009155 | 0.018311 | -0.1831 | -0.013733 | -0.11902 | -4.1611 | -0.60883 | -2.5681 | 4.0375 | 4.0375 | -115.1642 | -115.4663 | 115.6769 | 115.5716 | -4.5731 | 115.6677 | 115.7089 | 0.13733 | -4.4449 | 0.52643 | 0.2243 | -0.35248 | 111.5295 | 113.1226 | 112.8983 | -0.35248 | 115.5075 | 115.6357 | 115.6815 | -4.509 | 119.7281 | 119.7281 | 115.0818 | -119.8563
1055.6406 | 120.2957 | -115.6815 | 4.335 | 0.13611 | -0.041387 | -0.0045565 | 0.03167 | -0.014464 | -0.0051569 | 0.0069151 | 0.15182 | -0.016257 | 3.7491 | 0.1597 | 3.4296 | 0.00083532 | 0.068665 | 0.082397 | 0.13275 | 0.068665 | -0.086975 | 0.11444 | -0.009155 | -4.3076 | -0.66376 | -2.5452 | 4.01 | 3.9917 | -115.1688 | -115.4617 | 115.7959 | 115.6723 | -4.422 | 115.7639 | 115.7501 | 0.07782 | -4.2664 | 0.5127 | 0.21973 | -0.32501 | 111.3739 | 113.1363 | 112.9166 | -0.34332 | 115.5945 | 115.7501 | 115.8142 | -4.3442 | 119.6915 | 119.6732 | 115.0177 | -119.7968
1057.3906 | 120.1492 | -115.6952 | 4.39 | 0.059815 | -0.038183 | 0.0014249 | 0.029533 | -0.012542 | 0.00061092 | 0.0049923 | -0.03891 | -0.0094208 | 3.8245 | 0.1691 | 3.4313 | 0.0019033 | -0.091553 | -0.18768 | -0.15106 | -0.041199 | -0.13275 | -0.027466 | -0.12817 | -4.3808 | -0.737 | -2.6733 | 4.0375 | 3.9963 | -115.2145 | -115.4434 | 115.6677 | 115.567 | -4.5227 | 115.5075 | 115.654 | 0.086975 | -4.4815 | 0.48065 | 0.25177 | -0.35248 | 111.3144 | 113.0219 | 112.7701 | -0.39368 | 115.5624 | 115.6036 | 115.5441 | -4.5181 | 119.7327 | 119.6915 | 114.9582 | -119.8334
1059.1406 | 120.2957 | -115.7501 | 4.2938 | -0.13092 | -0.036474 | -0.0022067 | 0.034019 | -0.014037 | -0.0090021 | 0.0069151 | -0.099945 | -0.013907 | 3.7431 | 0.14838 | 3.4266 | 0.00083532 | 0.073242 | 0.068665 | 0.12817 | 0.064087 | -0.082397 | 0.10529 | 0.004578 | -4.0146 | -0.37994 | -2.4948 | 3.923 | 3.9322 | -115.2512 | -115.5396 | 115.8554 | 115.7547 | -4.3762 | 115.8188 | 115.8142 | 0.059509 | -4.2206 | 0.49896 | 0.21057 | -0.37079 | 111.7355 | 113.2553 | 113.0447 | -0.36163 | 115.6677 | 115.8234 | 115.8783 | -4.2892 | 119.6732 | 119.6823 | 115.3702 | -119.8334
1060.8906 | 120.3094 | -115.7364 | 4.2114 | 0.082703 | -0.039037 | -0.0058383 | 0.030602 | -0.012542 | -0.0017389 | 0.0054197 | 0.12131 | -0.011557 | 3.7651 | 0.17145 | 3.4316 | 0.0072439 | 0.032043 | 0.018311 | 0.086975 | 0.045776 | -0.11444 | 0.091553 | -0.027466 | -4.1382 | -1.4877 | -2.5314 | 3.8727 | 3.8544 | -115.3107 | -115.5991 | 115.8279 | 115.7089 | -4.3259 | 115.7547 | 115.7822 | 0.073242 | -4.1794 | 0.42572 | 0.13733 | -0.33875 | 111.5982 | 113.205 | 113.0676 | -0.35706 | 115.6219 | 115.7684 | 115.8234 | -4.2389 | 119.6091 | 119.5908 | 114.2487 | -119.8105
1062.5781 | 118.2083 | -67.6392 | 50.5096 | -0.15381 | -0.054205 | 0.03475 | 0.021416 | -0.010833 | -0.0055841 | -0.0018435 | -0.12283 | -0.0094208 | 7.0265 | 7.0025 | 2.2754 | 0.018139 | -0.50354 | -0.50354 | -0.26093 | -0.47607 | -0.60883 | -0.1831 | -0.27466 | -2.6276 | 27.8412 | -1.7944 | 46.3989 | 46.0236 | -61.4044 | -62.1094 | 67.4561 | 67.3645 | -51.1185 | 67.1356 | 67.1631 | -0.20142 | -51.0132 | 6.2347 | 5.5298 | -4.1107 | 65.0116 | 65.8447 | 60.3149 | -4.4861 | 67.0303 | 67.1356 | 67.3782 | -50.7843 | 114.0381 | 113.6627 | 95.4803 | -112.619
1064.3281 | 116.2766 | -63.8626 | 52.5101 | 0.036926 | -1.2385 | 2.0537 | -0.86961 | -0.22766 | -0.058563 | 0.25685 | 0.022125 | -0.012198 | 7.0265 | 7.0025 | 1.7145 | 1.1159 | -11.911 | -11.5494 | -4.1611 | -10.9085 | -9.3475 | -3.1769 | -3.273 | 13.5269 | 3.685 | -2.2934 | 45.4376 | 44.6686 | -55.632 | -56.369 | 60.6857 | 60.5896 | -61.8576 | 52.3132 | 52.9541 | -7.6355 | -64.4211 | 8.2306 | 7.4936 | -7.0724 | 77.3895 | 61.5692 | 54.0756 | -7.8415 | 54.5151 | 51.9516 | 59.7015 | -55.7831 | 109.3002 | 108.5312 | 67.5476 | -108.8791
1066.0625 | 120.2637 | -118.689 | 1.1948 | 0.14374 | -0.037969 | 0.0044157 | 0.0090256 | -0.010406 | -0.0019525 | -0.0037661 | 0.075531 | 0.016855 | 0.13477 | 0.025977 | 0.017224 | 0.025188 | 0.027466 | -0.068665 | -0.004578 | 0.004578 | -0.032043 | 0.086975 | -0.027466 | 0.027466 | 0.045776 | -0.082397 | 1.1307 | 1.1353 | 0.13275 | 0.059509 | 118.7759 | 118.6615 | -1.2268 | 118.6203 | 118.6935 | 0.032044 | -1.1673 | 118.8217 | 118.7485 | -0.064087 | 118.7164 | 118.6066 | -0.14191 | -0.059509 | 118.6569 | 118.7164 | 118.6844 | -1.2222 | 119.8196 | 119.8242 | 118.7347 | -1.1353
1067.7656 | 120.401 | -119.5908 | 0.3891 | 0.16663 | -0.039465 | 0.0093289 | 0.011375 | -0.013396 | -0.0021661 | -0.0037661 | 0.13657 | 0.016214 | 0.13541 | 0.026617 | 0.017224 | 0.024334 | 0.054932 | -0.027466 | 0.054932 | 0.013733 | -0.050354 | 0.11444 | 0.013733 | 0.10071 | 0.1236 | -0.013733 | 0.3067 | 0.32501 | 0.11902 | 0.059509 | 119.7052 | 119.6045 | -0.43945 | 119.5633 | 119.6045 | 0 | -0.33417 | 119.7098 | 119.6503 | -0.082397 | 119.6915 | 119.577 | -0.073242 | -0.064087 | 119.5404 | 119.6457 | 119.6457 | -0.37537 | 119.8975 | 119.9158 | 119.7144 | -0.32959
1069.5156 | 120.369 | -119.7189 | 0.43945 | 0.075073 | -0.037328 | 0.0059109 | 0.008812 | -0.010192 | 0.00039732 | -0.0012027 | 0.052643 | 0.016855 | 0.13477 | 0.028967 | 0.017865 | 0.023693 | -0.013733 | -0.091553 | -0.013733 | -0.018311 | -0.050354 | 0.09613 | -0.022888 | 0.027466 | 0.009155 | -0.11902 | 0.35706 | 0.37994 | 0.09613 | 0.018311 | 119.8151 | 119.696 | -0.48981 | 119.6274 | 119.7006 | 0.004577 | -0.45319 | 119.8151 | 119.7372 | -0.082397 | 119.7464 | 119.5999 | -0.13733 | -0.059509 | 119.6686 | 119.7052 | 119.7052 | -0.46234 | 120.076 | 120.0989 | 119.7281 | -0.42114
1071.2031 | 120.433 | -119.8059 | 0.42114 | -0.13092 | -0.038397 | 0.0089017 | 0.013725 | -0.012115 | -0.0015253 | -0.0041933 | -0.20676 | 0.020273 | 0.13776 | 0.029181 | 0.015302 | 0.022411 | -0.004578 | -0.054932 | 0.004578 | 0.018311 | -0.041199 | 0.07782 | -0.004578 | 0.032043 | 0.082397 | -0.082397 | 0.33875 | 0.3479 | 0.10071 | 0.036621 | 119.8837 | 119.8013 | -0.46234 | 119.751 | 119.8242 | 0.022889 | -0.42572 | 119.9066 | 119.8425 | -0.082398 | 119.838 | 119.7235 | -0.11902 | -0.073243 | 119.7647 | 119.8013 | 119.8105 | -0.42572 | 120.1447 | 120.1538 | 119.8883 | -0.38452
1072.9688 | 120.5246 | -119.8013 | 0.43488 | 0.014038 | -0.042242 | 0.0091153 | 0.0092392 | -0.012328 | -0.0081477 | -0.0041933 | 0.10605 | 0.022409 | 0.1305 | 0.025763 | 0.012952 | 0.025402 | 0.032043 | 0.013733 | 0.082397 | 0.045776 | -0.07782 | 0.10986 | 0.013733 | 0.064087 | 0.1236 | -0.018311 | 0.35706 | 0.38452 | 0.13275 | 0.054932 | 119.9112 | 119.8151 | -0.5127 | 119.8151 | 119.8471 | 0.032043 | -0.40283 | 119.9341 | 119.8563 | -0.077819 | 119.8654 | 119.783 | -0.073243 | -0.050354 | 119.7235 | 119.8334 | 119.8837 | -0.42114 | 120.1584 | 120.1859 | 119.9249 | -0.37994
1074.7188 | 120.4742 | -119.902 | 0.42572 | -0.19958 | -0.041814 | 0.011679 | 0.010521 | -0.011474 | -0.0030207 | -0.0065433 | -0.1915 | 0.019846 | 0.1337 | 0.027685 | 0.014661 | 0.021557 | 0 | -0.064087 | 0.013733 | -0.004578 | -0.036621 | 0.068665 | -0.018311 | 0.018311 | 0.059509 | -0.10529 | 0.35248 | 0.36163 | 0.091553 | 0.013733 | 119.9707 | 119.8837 | -0.46234 | 119.838 | 119.8975 | 0.013733 | -0.42572 | 119.9936 | 119.9158 | -0.073242 | 119.9203 | 119.7968 | -0.11902 | -0.064087 | 119.8654 | 119.902 | 119.9158 | -0.44403 | 120.2545 | 120.2637 | 119.9615 | -0.41199
1076.4062 | 120.5063 | -119.8791 | 0.4303 | -0.16907 | -0.040319 | 0.011892 | 0.012871 | -0.009551 | -0.0051569 | -0.0031253 | -0.099945 | 0.017709 | 0.13434 | 0.025977 | 0.014661 | 0.020702 | 0.082397 | 0.082397 | 0.14191 | 0.073242 | -0.068665 | 0.10986 | 0.018311 | 0.1236 | 0.20142 | 0.027466 | 0.33417 | 0.35248 | 0.13733 | 0.032043 | 119.989 | 119.8975 | -0.49896 | 119.9615 | 119.9524 | 0.054931 | -0.3479 | 120.0165 | 119.9112 | -0.096131 | 120.0027 | 119.9066 | -0.004577 | -0.07782 | 119.8105 | 119.9615 | 120.0211 | -0.41199 | 120.2133 | 120.2316 | 120.0806 | -0.39826
1078.1562 | 120.575 | -119.8791 | 0.44861 | 0.16663 | -0.044164 | 0.0065519 | 0.0090256 | -0.011046 | -0.0030207 | -0.0024845 | 0.18997 | 0.019418 | 0.13562 | 0.027685 | 0.015515 | 0.021984 | 0.10986 | 0.059509 | 0.1236 | 0.07782 | -0.082397 | 0.11444 | 0.018311 | 0.15564 | 0.16937 | 0.032043 | 0.35706 | 0.37994 | 0.13275 | 0.068665 | 119.9936 | 119.8975 | -0.531 | 119.9387 | 119.957 | 0.059509 | -0.33875 | 120.0119 | 119.9478 | -0.091552 | 120.0348 | 119.9112 | -0.036622 | -0.068664 | 119.7968 | 119.989 | 120.0027 | -0.4303 | 120.2362 | 120.2591 | 120.0485 | -0.37994
1079.8906 | 120.6345 | -119.838 | 0.48523 | -0.092773 | -0.042242 | 0.0086881 | 0.014793 | -0.011046 | -0.0072931 | -0.0063297 | -0.023651 | 0.018991 | 0.13712 | 0.027472 | 0.0097476 | 0.022839 | 0.10071 | 0.07782 | 0.14191 | 0.073242 | -0.10071 | 0.12817 | 0.004578 | 0.16937 | 0.19684 | 0.073242 | 0.37537 | 0.39825 | 0.14191 | 0.054932 | 119.9661 | 119.8425 | -0.58594 | 119.9158 | 119.9112 | 0.068664 | -0.38452 | 119.9799 | 119.8929 | -0.10986 | 120.0073 | 119.9112 | 0.01831 | -0.086975 | 119.7372 | 119.9387 | 119.9799 | -0.48065 | 120.2133 | 120.2362 | 120.0348 | -0.4303
1081.6406 | 120.6299 | -119.8425 | 0.53558 | 0.159 | -0.040746 | 0.0093289 | 0.0064622 | -0.01126 | -0.0023797 | -0.0041933 | 0.12131 | 0.020486 | 0.14075 | 0.027258 | 0.017011 | 0.023052 | 0.11902 | 0.07782 | 0.13275 | 0.059509 | -0.10071 | 0.11902 | 0.027466 | 0.14648 | 0.16937 | 0.018311 | 0.44861 | 0.45776 | 0.1236 | 0.068665 | 119.9615 | 119.87 | -0.63629 | 119.9203 | 119.902 | 0.032043 | -0.41656 | 119.9661 | 119.9112 | -0.086975 | 119.989 | 119.8608 | -0.050354 | -0.077819 | 119.7418 | 119.9615 | 119.9753 | -0.50812 | 120.2911 | 120.3003 | 120.0119 | -0.46692
1083.3906 | 120.6024 | -119.8425 | 0.5722 | -0.13092 | -0.039251 | 0.0099699 | 0.011803 | -0.010833 | 0.0010381 | -0.0048343 | -0.1915 | 0.0207 | 0.14588 | 0.027472 | 0.018079 | 0.023693 | 0.022888 | -0.064087 | 0.004578 | 0.009155 | -0.054932 | 0.086975 | -0.041199 | 0.022888 | 0.091553 | -0.082397 | 0.52185 | 0.51727 | 0.10071 | 0.036621 | 119.9295 | 119.8013 | -0.62714 | 119.7784 | 119.8517 | 0.050354 | -0.54932 | 119.9432 | 119.8791 | -0.050354 | 119.8654 | 119.7601 | -0.11902 | -0.054932 | 119.7876 | 119.8654 | 119.8471 | -0.6134 | 120.3644 | 120.3598 | 119.9341 | -0.53558
1085.0781 | 120.5841 | -119.8746 | 0.59967 | -0.14618 | -0.037969 | 0.0082609 | 0.01458 | -0.009551 | -0.0028071 | -0.0035525 | -0.19913 | 0.022836 | 0.15143 | 0.027258 | 0.013593 | 0.02412 | -0.004578 | -0.041199 | 0.009155 | -0.013733 | -0.045776 | 0.07782 | -0.009155 | 0.013733 | 0.09613 | -0.10986 | 0.52643 | 0.52185 | 0.10071 | 0.018311 | 119.9524 | 119.8654 | -0.64545 | 119.8334 | 119.8608 | -0.004578 | -0.60425 | 119.9753 | 119.8929 | -0.073242 | 119.8883 | 119.7647 | -0.12817 | -0.077819 | 119.8288 | 119.87 | 119.8837 | -0.60883 | 120.401 | 120.3964 | 119.9707 | -0.58136
1086.8281 | 120.7123 | -119.8013 | 0.60883 | 0.15137 | -0.039465 | 0.0080473 | 0.005394 | -0.011901 | -0.0030207 | -0.0020571 | 0.12894 | 0.020059 | 0.15058 | 0.025763 | 0.017224 | 0.023693 | 0.086975 | 0.045776 | 0.10071 | 0.068665 | -0.064087 | 0.10986 | 0.009155 | 0.14191 | 0.16937 | 0.018311 | 0.50354 | 0.5127 | 0.16022 | 0.09613 | 119.9112 | 119.8105 | -0.67291 | 119.8471 | 119.87 | 0.05951 | -0.52185 | 119.9615 | 119.8975 | -0.10529 | 119.9432 | 119.8196 | -0.077819 | -0.096131 | 119.7372 | 119.8883 | 119.902 | -0.59967 | 120.3049 | 120.314 | 119.9707 | -0.5127
1088.5938 | 120.6162 | -119.8059 | 0.70496 | 0.082703 | -0.040106 | 0.0067655 | 0.0094528 | -0.010406 | 0.0014655 | -0.0020571 | 0.045013 | 0.023264 | 0.16019 | 0.025763 | 0.017224 | 0.023479 | -0.013733 | -0.10529 | -0.027466 | -0.013733 | -0.041199 | 0.068665 | -0.032043 | 0.013733 | 0.054932 | -0.1236 | 0.60425 | 0.61798 | 0.11444 | 0.054932 | 119.8746 | 119.7739 | -0.74616 | 119.7006 | 119.7922 | 0.01831 | -0.71869 | 119.9203 | 119.8608 | -0.10071 | 119.8196 | 119.6823 | -0.17853 | -0.086975 | 119.7647 | 119.7922 | 119.7784 | -0.737 | 120.4102 | 120.4239 | 119.8608 | -0.65002
1090.3438 | 120.6894 | -119.751 | 0.66834 | 0.18951 | -0.041174 | 0.0086881 | 0.0083848 | -0.0091238 | -0.0032343 | -0.0016299 | 0.17471 | 0.022195 | 0.16532 | 0.024481 | 0.014875 | 0.025616 | 0.10529 | 0.073242 | 0.14648 | 0.059509 | -0.091553 | 0.11902 | 0.027466 | 0.15106 | 0.20599 | 0.041199 | 0.56763 | 0.60425 | 0.16022 | 0.10986 | 119.87 | 119.7784 | -0.75989 | 119.8242 | 119.8105 | 0.032043 | -0.56305 | 119.9112 | 119.8608 | -0.10071 | 119.902 | 119.7922 | -0.068664 | -0.064087 | 119.6594 | 119.8563 | 119.8975 | -0.64087 | 120.3186 | 120.3552 | 119.957 | -0.55847
1092.0938 | 120.639 | -119.7922 | 0.72784 | -0.15381 | -0.041174 | 0.0089017 | 0.013512 | -0.0089102 | -0.0070795 | -0.0048343 | -0.16098 | 0.021127 | 0.17002 | 0.027258 | 0.015515 | 0.025188 | 0.064087 | 0.073242 | 0.10986 | 0.068665 | -0.073242 | 0.091553 | 0.004578 | 0.07782 | 0.1831 | -0.027466 | 0.6134 | 0.60883 | 0.15564 | 0.07782 | 119.8837 | 119.7968 | -0.80109 | 119.8654 | 119.8608 | 0.064087 | -0.66376 | 119.9478 | 119.87 | -0.11444 | 119.87 | 119.7647 | -0.10529 | -0.11902 | 119.7189 | 119.8563 | 119.902 | -0.72327 | 120.4056 | 120.401 | 119.9753 | -0.65002
1093.8438 | 120.7489 | -119.7968 | 0.68207 | 0.090332 | -0.040746 | 0.0056973 | 0.010735 | -0.011046 | -0.0013117 | -0.0035525 | 0.09079 | 0.022836 | 0.17343 | 0.025763 | 0.016797 | 0.024761 | 0.018311 | -0.064087 | -0.018311 | 0.009155 | -0.050354 | 0.082397 | -0.018311 | 0.054932 | 0.082397 | -0.086975 | 0.64087 | 0.62714 | 0.13733 | 0.068665 | 119.8791 | 119.7784 | -0.73242 | 119.7327 | 119.8059 | 0.027466 | -0.66376 | 119.9341 | 119.8654 | -0.041199 | 119.8517 | 119.7098 | -0.15564 | -0.054932 | 119.7464 | 119.8151 | 119.7784 | -0.70038 | 120.4376 | 120.4239 | 119.8791 | -0.6134
1095.5312 | 120.7077 | -119.8654 | 0.70038 | -0.18433 | -0.036901 | 0.0054837 | 0.015648 | -0.0091238 | -0.00067088 | -0.0059023 | -0.16098 | 0.022836 | 0.17621 | 0.027258 | 0.012097 | 0.025402 | 0 | -0.073242 | 0.004578 | -0.013733 | -0.045776 | 0.073242 | -0.036621 | 0.032043 | 0.10071 | -0.07782 | 0.59967 | 0.62256 | 0.1236 | 0.054932 | 119.9387 | 119.8288 | -0.74615 | 119.7922 | 119.8517 | 0.022888 | -0.70038 | 119.989 | 119.9203 | -0.10071 | 119.8975 | 119.7876 | -0.13275 | -0.077819 | 119.8196 | 119.8654 | 119.87 | -0.737 | 120.4651 | 120.488 | 119.9661 | -0.64545
1097.2656 | 120.7718 | -119.8196 | 0.66376 | 0.12848 | -0.039037 | 0.0059109 | 0.0092392 | -0.009551 | -0.0017389 | -0.0041933 | 0.09079 | 0.023691 | 0.17707 | 0.027258 | 0.013806 | 0.023479 | 0.022888 | -0.064087 | -0.009155 | 0.004578 | -0.032043 | 0.07782 | -0.018311 | 0.068665 | 0.073242 | -0.091553 | 0.60883 | 0.60883 | 0.15106 | 0.07782 | 119.8975 | 119.8013 | -0.6958 | 119.7556 | 119.8242 | 0.022889 | -0.64087 | 119.9707 | 119.8975 | -0.054931 | 119.8883 | 119.7281 | -0.16937 | -0.054931 | 119.7876 | 119.8425 | 119.8105 | -0.68207 | 120.4285 | 120.4285 | 119.8929 | -0.58594
1099.0312 | 120.7764 | -119.9158 | 0.62256 | 0.10559 | -0.042028 | 0.0080473 | 0.010521 | -0.0089102 | -0.0075067 | -0.0044071 | 0.17471 | 0.022195 | 0.17792 | 0.02619 | 0.013593 | 0.027111 | 0.09613 | 0.059509 | 0.11902 | 0.068665 | -0.09613 | 0.10986 | 0.004578 | 0.16022 | 0.1831 | 0.018311 | 0.52185 | 0.54932 | 0.14648 | 0.091553 | 120.0256 | 119.9203 | -0.71869 | 119.9753 | 119.9844 | 0.064087 | -0.52643 | 120.0623 | 120.0073 | -0.10071 | 120.076 | 119.9341 | -0.073242 | -0.073243 | 119.8196 | 120.0119 | 120.0348 | -0.61798 | 120.4376 | 120.4651 | 120.0989 | -0.53101
1100.7188 | 120.8176 | -119.8608 | 0.59052 | 0.12085 | -0.041387 | 0.0069791 | 0.0085984 | -0.0080558 | -0.0028071 | -0.0046207 | 0.11368 | 0.020059 | 0.17877 | 0.025336 | 0.014447 | 0.024334 | 0.086975 | 0.032043 | 0.10986 | 0.073242 | -0.082397 | 0.10529 | 0.009155 | 0.16022 | 0.1831 | 0.004578 | 0.5127 | 0.53558 | 0.16937 | 0.11444 | 119.9661 | 119.87 | -0.67291 | 119.8929 | 119.9341 | 0.064087 | -0.50354 | 120.0302 | 119.9753 | -0.07782 | 120.0211 | 119.8654 | -0.10986 | -0.054932 | 119.7784 | 119.9478 | 119.9707 | -0.58136 | 120.3735 | 120.3964 | 120.0439 | -0.47607
1102.4688 | 116.3315 | -95.4666 | 20.7275 | -0.13855 | 0.045344 | -0.13679 | 0.072899 | 0.013093 | 0.0018927 | -0.02641 | -0.13046 | 0.35951 | 7.0265 | -0.40255 | -0.12163 | 0.57463 | 1.03 | 0.93384 | 0.74158 | 0.97046 | 0.91095 | 0.70496 | 0.59967 | 6.1752 | 4.8798 | 0.027466 | 19.5374 | 19.4138 | 4.7058 | 4.6463 | 96.1716 | 96.0663 | -19.8166 | 96.4005 | 96.4371 | 0.37079 | -19.6976 | 100.1724 | 100.1129 | -1.1902 | 101.6418 | 95.4941 | -4.6188 | -1.3138 | 96.3776 | 96.4966 | 96.2082 | -20.1279 | 115.004 | 114.8804 | 100.3464 | -16.0812
1104.2344 | 116.0065 | -94.3222 | 21.4188 | -0.046997 | 0.033167 | -0.11884 | 0.067131 | 0.0090342 | -0.0087885 | -0.024488 | -0.077057 | 0.064066 | 7.0265 | -0.38781 | -0.098132 | 0.49644 | 0.8194 | 0.74616 | 0.6134 | 0.737 | 0.70953 | 0.6134 | 0.50354 | 7.3288 | 3.4195 | 0.082397 | 20.4254 | 20.4483 | 3.8635 | 3.7903 | 94.9356 | 94.8257 | -20.7092 | 95.0684 | 95.0592 | 0.23346 | -20.5994 | 98.1857 | 98.1125 | -0.99335 | 101.651 | 94.4046 | -3.7079 | -0.97046 | 95.0317 | 95.1416 | 94.9356 | -20.9152 | 114.7476 | 114.7705 | 97.7417 | -17.6285
1106 | 115.7181 | -93.1 | 22.3434 | 0.090332 | 0.013728 | -0.091501 | 0.055382 | 0.010529 | -0.00088448 | -0.028547 | 0.10605 | 0.23966 | 7.0186 | -0.30728 | -0.11138 | 0.45991 | 0.90179 | 0.82398 | 0.66376 | 0.79193 | 0.71411 | 0.63629 | 0.50812 | 8.8074 | 4.3304 | -0.88806 | 21.3409 | 21.6934 | 4.3076 | 4.2572 | 93.7363 | 93.6081 | -21.6293 | 93.924 | 93.8919 | 0.28381 | -21.4417 | 97.4075 | 97.3572 | -1.0025 | 101.9073 | 92.2119 | -5.1453 | -0.65002 | 93.8141 | 94.0018 | 93.7637 | -21.8353 | 114.4409 | 114.7934 | 97.4304 | -18.0862
1107.6875 | 115.4388 | -93.4204 | 21.9086 | -0.20721 | 0.0064643 | -0.071634 | 0.042778 | 0.016084 | -0.00088448 | -0.035596 | -0.19913 | 0.37681 | 7.0265 | -0.29061 | -0.10646 | 0.4488 | 0.89722 | 0.82398 | 0.64545 | 0.83313 | 0.74158 | 0.62714 | 0.52185 | 7.2693 | 4.1611 | -0.013733 | 21.2585 | 21.2036 | 4.0192 | 3.9825 | 94.0475 | 93.9423 | -21.167 | 94.2444 | 94.2535 | 0.31128 | -21.0114 | 97.4396 | 97.403 | -0.65002 | 100.6897 | 93.4067 | -3.9963 | -0.70496 | 94.162 | 94.3176 | 94.0659 | -21.3867 | 114.679 | 114.624 | 97.5815 | -17.926
1109.4375 | 115.3931 | -94.0109 | 20.993 | -0.1004 | -0.030492 | -0.0047701 | 0.014793 | 0.033601 | -0.0025935 | -0.052472 | -0.2449 | 0.35801 | 7.0265 | -0.34188 | -0.13445 | 0.51268 | 1.2634 | 1.236 | 0.95673 | 1.2543 | 1.0757 | 0.85602 | 0.75531 | 7.9926 | 5.2597 | 0.35706 | 20.2286 | 20.1691 | 4.9759 | 4.921 | 94.8669 | 94.7662 | -19.9173 | 95.2469 | 95.2652 | 0.49896 | -19.7296 | 98.9868 | 98.9319 | -0.76446 | 102.0035 | 94.368 | -4.5639 | -0.82398 | 95.0867 | 95.2744 | 94.9677 | -20.2377 | 114.2395 | 114.18 | 99.2706 | -16.0721
1111.1875 | 115.21 | -94.0292 | 20.9335 | -0.14618 | -0.27167 | 0.38531 | -0.1591 | 0.078675 | 0.0087287 | -0.11421 | -0.1152 | 0.37083 | 7.0265 | -0.29788 | -0.13957 | 0.48704 | 2.742 | 2.6733 | 1.8723 | 3.4698 | 2.5543 | 1.9089 | 1.7899 | 8.0933 | 5.5389 | 0.16022 | 19.9768 | 19.8578 | 5.2322 | 5.1773 | 95.9381 | 95.8191 | -18.3792 | 96.7026 | 97.4991 | 1.68 | -18.1915 | 99.2615 | 99.2065 | -0.95673 | 102.1225 | 94.1895 | -5.0171 | -1.0757 | 96.5836 | 96.7712 | 95.9015 | -19.1437 | 114.006 | 113.887 | 99.5682 | -15.7562
1112.9375 | 115.1505 | -94.455 | 20.3247 | -0.11566 | -0.52482 | 0.8572 | -0.35777 | 0.15686 | 0.015137 | -0.1956 | -0.069428 | 0.3234 | 7.0265 | -0.1838 | -0.14171 | 0.37339 | 3.891 | 4.0741 | 2.7054 | 5.9784 | 3.8589 | 2.742 | 2.6276 | 7.8552 | 5.4062 | 0.13733 | 19.2673 | 19.0933 | 5.1956 | 5.1544 | 97.197 | 97.0825 | -16.4658 | 98.5291 | 100.4333 | 3.3508 | -16.4337 | 99.6506 | 99.6094 | -1.0574 | 102.3102 | 94.5923 | -5.0171 | -1.2314 | 98.3139 | 98.3459 | 97.1603 | -17.6971 | 113.7222 | 113.5483 | 99.8611 | -15.1703
1114.625 | 115.0269 | -94.5557 | 20.137 | -0.10803 | -0.51243 | 0.82601 | -0.34666 | 0.15472 | 0.021119 | -0.19368 | -0.15335 | 0.6808 | 7.0265 | -0.1947 | -0.14769 | 0.39155 | 3.7994 | 3.9413 | 2.5955 | 6.3492 | 3.7125 | 2.5131 | 2.4124 | 7.8644 | 5.6534 | 0.07782 | 18.9514 | 18.8782 | 5.4428 | 5.4016 | 97.0688 | 96.9681 | -16.4246 | 98.497 | 100.9048 | 3.9368 | -16.3376 | 99.9985 | 99.9573 | -1.1856 | 102.42 | 94.6335 | -5.3238 | -1.2588 | 98.2681 | 98.3551 | 97.1512 | -17.7246 | 113.5071 | 113.4338 | 100.209 | -14.7354
1116.3594 | 114.83 | -94.043 | 20.6955 | 0.014038 | -0.39921 | 0.66088 | -0.26142 | 0.11478 | 0.026459 | -0.1548 | -0.21439 | 0.053598 | 7.0265 | -0.16287 | -0.10454 | 0.32255 | 2.8885 | 2.8976 | 1.7624 | 4.5914 | 2.7924 | 1.8539 | 1.7624 | 7.2052 | 4.3396 | -0.013733 | 19.7708 | 19.7342 | 4.3625 | 4.3213 | 95.8969 | 95.8054 | -17.9031 | 96.9406 | 98.6343 | 2.829 | -17.807 | 98.4055 | 98.3643 | -0.92468 | 101.2482 | 94.0292 | -4.335 | -0.9613 | 96.8353 | 96.9315 | 95.8054 | -18.9331 | 113.8138 | 113.7772 | 98.3826 | -16.3742
1118.1094 | 114.8117 | -96.6568 | 17.8894 | -0.1767 | -0.35755 | 0.56731 | -0.23215 | 0.12204 | 0.016633 | -0.15886 | -0.22202 | 0.13563 | 7.0265 | -0.37179 | -0.18935 | 0.61628 | 3.0624 | 3.1265 | 2.0233 | 4.9759 | 3.1082 | 2.0782 | 1.9638 | 7.8873 | 7.0724 | -0.013733 | 16.246 | 16.1087 | 6.8436 | 6.8024 | 98.735 | 98.6206 | -14.7812 | 99.7833 | 101.6327 | 3.0121 | -14.827 | 103.5004 | 103.4592 | -1.6434 | 104.5441 | 96.6431 | -6.8161 | -1.7807 | 99.765 | 99.7192 | 98.6801 | -15.9256 | 112.9028 | 112.7655 | 103.7292 | -11.087
1119.7969 | 114.8987 | -95.9518 | 18.5806 | -0.28351 | -0.40348 | 0.51241 | -0.2595 | 0.10965 | 0.014069 | -0.16334 | 0.18997 | 0.59214 | 7.0265 | -0.28549 | -0.1603 | 0.48042 | 3.0624 | 3.3096 | 2.0782 | 5.4382 | 3.0487 | 2.1423 | 2.0233 | 10.3867 | 5.9097 | 0.082397 | 17.1936 | 17.07 | 6.1478 | 6.0745 | 98.0942 | 97.9752 | -15.5319 | 99.2615 | 101.3901 | 3.4149 | -15.5182 | 102.0996 | 102.0264 | -1.387 | 106.3385 | 96.0342 | -5.9921 | -1.5106 | 99.0005 | 99.0143 | 98.0301 | -16.5573 | 113.1454 | 113.0219 | 101.8616 | -12.5061
1121.5469 | 114.8117 | -97.8561 | 16.6306 | -0.0012209 | -0.29838 | 0.46477 | -0.18559 | 0.09192 | 0.011506 | -0.12596 | 0.037384 | 2.703 | 7.0265 | -0.34957 | -0.17375 | 0.57484 | 2.6505 | 2.7283 | 1.8036 | 4.2526 | 2.623 | 1.918 | 1.7944 | 7.9422 | 6.5094 | 0.073242 | 14.6896 | 14.5248 | 6.2988 | 6.2439 | 99.7742 | 99.6506 | -14.0076 | 100.5844 | 102.1088 | 2.4582 | -13.9801 | 104.155 | 104.1 | -1.9409 | 105.7983 | 97.9294 | -6.1707 | -2.1057 | 100.4791 | 100.5066 | 99.6597 | -14.8361 | 112.5458 | 112.381 | 104.3655 | -10.3867
1123.2969 | 114.7934 | -98.3414 | 16.0584 | 0.159 | -0.29645 | 0.45089 | -0.18922 | 0.095551 | 0.016419 | -0.12596 | 0.12894 | 4.4064 | 7.0265 | -0.32073 | -0.1635 | 0.53169 | 2.6367 | 2.6733 | 1.8402 | 4.129 | 2.5131 | 1.8814 | 1.7715 | 7.6813 | 6.189 | 0.12817 | 14.0762 | 13.9435 | 5.9509 | 5.9097 | 100.2228 | 100.1129 | -13.5452 | 101.0147 | 102.4704 | 2.3575 | -13.4216 | 104.2923 | 104.2511 | -1.9821 | 106.0226 | 98.4695 | -5.7816 | -2.1149 | 100.8545 | 100.9781 | 100.1816 | -14.2868 | 112.4176 | 112.2849 | 104.5303 | -10.1486
1124.9844 | 114.7705 | -95.0958 | 19.455 | 0.090332 | -0.54319 | 0.86403 | -0.35285 | 0.13892 | 0.026246 | -0.18364 | 0.08316 | 1.0452 | 7.0265 | 0.044989 | -0.069293 | 0.086498 | 3.2043 | 3.1265 | 2.1973 | 6.2027 | 3.2913 | 2.298 | 2.1835 | 13.2523 | 2.7512 | 0.14648 | 18.6264 | 18.512 | 2.8702 | 2.8015 | 97.3938 | 97.2794 | -16.1636 | 98.2224 | 101.2985 | 4.0192 | -16.2506 | 97.966 | 97.8973 | -0.82855 | 108.3481 | 95.2423 | -2.655 | -0.94299 | 98.3871 | 98.3002 | 97.2931 | -17.2714 | 113.7222 | 113.6078 | 97.847 | -16.6534
1126.7344 | 114.8117 | -97.4945 | 16.9464 | -0.092773 | -0.36417 | 0.56518 | -0.22746 | 0.11862 | 0.013001 | -0.14796 | -0.069428 | 3.9443 | 7.0265 | -0.31689 | -0.17461 | 0.54301 | 2.7832 | 2.8976 | 2.0737 | 4.9713 | 2.7512 | 2.0599 | 1.9363 | 8.3954 | 6.7795 | 0.14648 | 15.4129 | 15.3168 | 6.3766 | 6.3446 | 99.5544 | 99.4308 | -14.1953 | 100.3922 | 102.4658 | 3.035 | -14.1632 | 103.8712 | 103.8391 | -1.5335 | 105.8899 | 97.641 | -6.1981 | -1.6296 | 100.2457 | 100.2777 | 99.5682 | -15.0101 | 112.9074 | 112.8113 | 104.274 | -10.6018
1128.4844 | 114.8438 | -95.7413 | 18.75 | 0.014038 | -0.53336 | 0.86382 | -0.35926 | 0.15579 | 0.020051 | -0.19688 | 0.08316 | 1.6647 | 7.0265 | 0.0099548 | -0.085742 | 0.13221 | 3.3234 | 3.4882 | 2.3712 | 6.1523 | 3.3783 | 2.3666 | 2.2705 | 11.8195 | 3.5477 | 0.009155 | 17.7612 | 17.6834 | 3.4973 | 3.4515 | 98.1079 | 98.0118 | -15.3717 | 99.2294 | 101.8936 | 3.8818 | -15.4266 | 99.2386 | 99.1928 | -0.98877 | 107.5607 | 95.7504 | -3.4424 | -1.0666 | 99.1196 | 99.0646 | 98.1125 | -16.4795 | 113.5025 | 113.4247 | 99.2889 | -15.2985
1130.2344 | 114.8483 | -95.668 | 18.8004 | -0.13092 | -0.53443 | 0.86553 | -0.35307 | 0.17075 | 0.019196 | -0.21547 | -0.016022 | 2.1505 | 7.0265 | 0.11143 | -0.05968 | -0.0019419 | 3.3371 | 3.5248 | 2.3941 | 5.6305 | 3.3783 | 2.3438 | 2.2202 | 12.6434 | 3.598 | 0 | 17.8162 | 17.8345 | 3.2364 | 3.1998 | 98.0118 | 97.8882 | -15.4221 | 99.1928 | 101.2985 | 3.4103 | -15.4633 | 98.9044 | 98.8678 | -0.98419 | 108.3115 | 95.668 | -3.1998 | -0.96588 | 99.0463 | 99.0051 | 98.0621 | -16.5802 | 113.4842 | 113.5025 | 99.2661 | -15.6006
1132 | 114.7202 | -97.9614 | 16.5207 | 0.12085 | -0.48658 | 0.78884 | -0.33085 | 0.16583 | 0.026246 | -0.20137 | 0.052643 | 5.2824 | 7.0265 | -0.048578 | -0.1462 | 0.25206 | 3.2593 | 3.3463 | 2.2614 | 5.5161 | 3.3691 | 2.3529 | 2.243 | 8.1985 | 5.5389 | -0.036621 | 14.8453 | 14.7308 | 5.5069 | 5.4474 | 100.3143 | 100.2045 | -13.1516 | 101.3077 | 103.4775 | 3.273 | -13.2614 | 103.4683 | 103.4088 | -1.6754 | 106.16 | 97.9248 | -5.484 | -1.7899 | 101.3306 | 101.2207 | 100.2228 | -14.2776 | 112.8067 | 112.6923 | 103.5004 | -11.0733
1133.7031 | 114.7018 | -99.5636 | 14.8956 | -0.15381 | -0.39493 | 0.63119 | -0.25651 | 0.17288 | 0.010438 | -0.20436 | -0.12283 | 6.9882 | 7.0265 | -0.017389 | -0.13423 | 0.1995 | 2.7832 | 2.916 | 1.9958 | 4.4266 | 2.7237 | 2.0142 | 1.9043 | 6.4499 | 5.0766 | 0.1236 | 12.7487 | 12.6389 | 4.9301 | 4.8752 | 101.5778 | 101.4679 | -12.1719 | 102.4796 | 103.9902 | 2.5223 | -12.1124 | 104.4937 | 104.4388 | -2.1469 | 106.0135 | 99.6872 | -4.7516 | -2.2568 | 102.2873 | 102.3468 | 101.5594 | -12.9913 | 112.3123 | 112.2025 | 104.6402 | -10.0204
1135.4531 | 114.7568 | -99.9207 | 14.5157 | 0.11322 | -0.38212 | 0.60042 | -0.24967 | 0.15109 | 0.010865 | -0.18214 | 0.1442 | 6.9882 | 7.0265 | -0.013544 | -0.1259 | 0.19117 | 2.6825 | 2.7878 | 1.918 | 4.2068 | 2.5955 | 1.9089 | 1.799 | 6.3721 | 4.9301 | 0.13275 | 12.3459 | 12.236 | 4.834 | 4.7607 | 101.8295 | 101.7197 | -11.9202 | 102.7084 | 104.1275 | 2.4078 | -11.8332 | 104.7546 | 104.6814 | -2.1698 | 106.2927 | 100.0534 | -4.628 | -2.2797 | 102.5162 | 102.6031 | 101.8387 | -12.7167 | 112.2665 | 112.1567 | 104.8508 | -9.7549
1137.2031 | 118.0984 | -117.7231 | 0.032043 | 0.14374 | -0.042883 | 0.01296 | 0.0049668 | -0.012542 | -0.0053705 | -0.0054751 | 0.060272 | 0.02775 | 0.056796 | 0.022345 | 0.016156 | 0.01878 | 0.073242 | 0.041199 | 0.082397 | 0.050354 | -0.09613 | 0.10986 | 0.032043 | 0.10071 | 0.091553 | -0.013733 | -0.045776 | -0.045776 | 0.10529 | 0.041199 | 117.8329 | 117.7551 | -0.12817 | 117.7643 | 117.7734 | 0.018311 | 0.041199 | 117.8284 | 117.7643 | -0.077819 | 117.8238 | 117.7094 | -0.054932 | -0.077819 | 117.627 | 117.7963 | 117.8055 | 0 | 117.6773 | 117.6773 | 117.8146 | 0.009156
1138.9531 | 118.3456 | -117.9932 | 0.045776 | -0.12329 | -0.041601 | 0.011038 | 0.011589 | -0.011687 | -0.0038751 | -0.0071841 | -0.14572 | 0.026254 | 0.06235 | 0.024054 | 0.012097 | 0.017071 | 0.10071 | 0.073242 | 0.13733 | 0.073242 | -0.07782 | 0.10529 | 0 | 0.14191 | 0.16479 | 0.041199 | -0.059509 | -0.054932 | 0.091553 | 0.022888 | 118.0984 | 117.9932 | -0.1236 | 118.0664 | 118.0664 | 0.073242 | 0.054932 | 118.0847 | 118.0161 | -0.10528 | 118.1351 | 118.0344 | 0.018311 | -0.10071 | 117.9153 | 118.0939 | 118.1305 | -0.045776 | 117.9337 | 117.9382 | 118.158 | -0.022888
1140.6406 | 118.5013 | -118.1305 | 0.018311 | -0.0088499 | -0.046514 | 0.01232 | 0.0083848 | -0.0069876 | -0.0075067 | -0.010816 | -0.0083922 | 0.027963 | 0.05936 | 0.022131 | 0.014234 | 0.018352 | 0.045776 | 0.022888 | 0.091553 | 0.054932 | -0.064087 | 0.10071 | 0 | 0.10986 | 0.1236 | 0.027466 | -0.059509 | -0.041199 | 0.09613 | 0.045776 | 118.2312 | 118.1305 | -0.082398 | 118.1534 | 118.1854 | 0.054932 | 0.027465 | 118.2266 | 118.1763 | -0.07782 | 118.2404 | 118.158 | -0.01831 | -0.05951 | 118.0664 | 118.1763 | 118.222 | -0.018311 | 118.071 | 118.0893 | 118.2541 | 0.027465
1142.375 | 118.5242 | -118.2953 | 0.059509 | -0.1767 | -0.037542 | 0.011038 | 0.010735 | -0.006774 | 0.00039732 | -0.0086795 | -0.21439 | 0.03074 | 0.062137 | 0.023199 | 0.014447 | 0.014934 | 0.009155 | -0.068665 | -0.004578 | 0 | -0.041199 | 0.073242 | -0.050354 | 0.022888 | 0.036621 | -0.10071 | -0.022888 | -0.018311 | 0.064087 | 0.004578 | 118.3685 | 118.2449 | -0.10071 | 118.2266 | 118.2953 | 0.050354 | -0.050354 | 118.3594 | 118.2999 | -0.082397 | 118.3182 | 118.1946 | -0.10529 | -0.07782 | 118.2541 | 118.3044 | 118.2907 | -0.10986 | 118.2724 | 118.277 | 118.3319 | -0.054931
1144.125 | 118.6111 | -118.3914 | 0.041199 | -0.085144 | -0.039251 | 0.010397 | 0.0090256 | -0.0063468 | 0.0016791 | -0.0061161 | -0.14572 | 0.028391 | 0.061709 | 0.023627 | 0.017865 | 0.017071 | 0.059509 | 0.018311 | 0.064087 | 0.036621 | -0.045776 | 0.07782 | -0.018311 | 0.07782 | 0.09613 | -0.050354 | -0.050354 | -0.022888 | 0.073242 | -0.009155 | 118.4692 | 118.3731 | -0.086975 | 118.4097 | 118.428 | 0.054932 | 0.01831 | 118.4647 | 118.3823 | -0.091553 | 118.4692 | 118.3411 | -0.041199 | -0.064087 | 118.3456 | 118.4509 | 118.4555 | -0.05951 | 118.3411 | 118.3685 | 118.4875 | -0.050354
1145.875 | 118.7347 | -118.4555 | 0.022888 | 0.12848 | -0.042028 | 0.010611 | 0.0077438 | -0.009551 | 0.00018372 | -0.0069705 | 0.045013 | 0.028177 | 0.060641 | 0.025977 | 0.014447 | 0.018993 | 0 | -0.064087 | -0.009155 | -0.009155 | -0.045776 | 0.091553 | -0.036621 | 0.054932 | 0.004578 | -0.10071 | -0.018311 | -0.022888 | 0.068665 | 0.004578 | 118.5471 | 118.4189 | -0.068664 | 118.3914 | 118.4463 | 0.027466 | -0.022888 | 118.5242 | 118.4601 | -0.041199 | 118.5104 | 118.3548 | -0.10529 | -0.045776 | 118.4097 | 118.4555 | 118.4463 | -0.059509 | 118.4372 | 118.4326 | 118.4601 | -0.01831
1147.625 | 118.7668 | -118.5791 | 0.032043 | -0.069885 | -0.040106 | 0.011038 | 0.008812 | -0.010833 | -0.00024348 | -0.0063297 | -0.099945 | 0.029886 | 0.060641 | 0.024481 | 0.017652 | 0.018139 | 0.045776 | 0 | 0.050354 | 0.027466 | -0.073242 | 0.086975 | -0.036621 | 0.082397 | 0.086975 | -0.032043 | -0.041199 | -0.022888 | 0.082397 | 0.004578 | 118.6661 | 118.5425 | -0.10529 | 118.5791 | 118.6066 | 0.064087 | 0.013733 | 118.6615 | 118.5837 | -0.073242 | 118.6615 | 118.5471 | -0.036621 | -0.054931 | 118.5059 | 118.6249 | 118.6295 | -0.068664 | 118.5379 | 118.5562 | 118.6661 | -0.027465
1149.3281 | 118.9362 | -118.6157 | 0.009155 | 0.15137 | -0.042669 | 0.0091153 | 0.0073166 | -0.0074148 | -0.0034479 | -0.0059023 | 0.12131 | 0.028604 | 0.061496 | 0.024054 | 0.015302 | 0.020702 | 0.054932 | 0.013733 | 0.073242 | 0.059509 | -0.09613 | 0.10071 | -0.009155 | 0.11902 | 0.11902 | 0.022888 | -0.073242 | -0.050354 | 0.091553 | 0.041199 | 118.7164 | 118.6066 | -0.10528 | 118.6295 | 118.6752 | 0.068664 | 0.045777 | 118.7073 | 118.6569 | -0.082397 | 118.7347 | 118.6386 | -0.018311 | -0.059509 | 118.5196 | 118.6707 | 118.689 | -0.01831 | 118.5425 | 118.5654 | 118.7347 | 0.032044
1151.0781 | 118.9545 | -118.7622 | 0.004578 | 0.059815 | -0.0020807 | -0.06373 | 0.024834 | -0.012328 | -0.0075067 | -0.0041933 | 0.098419 | 0.015146 | 0.022616 | 0.023413 | 0.012097 | 0.020916 | 0.041199 | 0.036621 | 0.10071 | 0.018311 | -0.073242 | 0.13275 | 0.004578 | 0.082397 | 0.10071 | 0 | -0.07782 | -0.064087 | 0.10986 | 0.022888 | 118.895 | 118.7668 | -0.07782 | 118.7988 | 118.7805 | 0.013733 | 0.036621 | 118.8721 | 118.7851 | -0.082398 | 118.8446 | 118.7622 | -0.022888 | -0.068665 | 118.689 | 118.8034 | 118.8629 | 0 | 118.6844 | 118.6981 | 118.8629 | 0.01831
1152.7656 | 119.0689 | -118.8217 | -0.009155 | 0.10559 | -0.0035761 | -0.060099 | 0.021843 | -0.011687 | -0.0021661 | -0.0041933 | 0.13657 | 0.015146 | 0.018558 | 0.024908 | 0.015302 | 0.017712 | 0.036621 | -0.041199 | 0.027466 | 0 | -0.054932 | 0.10529 | -0.013733 | 0.064087 | 0.032043 | -0.054932 | -0.068665 | -0.050354 | 0.10529 | 0 | 118.927 | 118.808 | -0.045777 | 118.7805 | 118.8217 | 0.013733 | 0.045776 | 118.927 | 118.8217 | -0.05951 | 118.8858 | 118.7668 | -0.054932 | -0.041199 | 118.7668 | 118.8583 | 118.8492 | -0.004578 | 118.7531 | 118.7714 | 118.8538 | 0.009155
1154.5312 | 119.1696 | -118.8721 | -0.018311 | -0.0012209 | -0.0033625 | -0.059458 | 0.025261 | -0.011474 | -0.0092157 | -0.0065433 | 0.037384 | 0.010233 | 0.019198 | 0.022345 | 0.012738 | 0.019634 | 0.027466 | 0.027466 | 0.10071 | 0.032043 | -0.07782 | 0.1236 | 0.018311 | 0.07782 | 0.11444 | 0.018311 | -0.073242 | -0.054932 | 0.10071 | 0.022888 | 118.9957 | 118.8904 | -0.059509 | 118.8995 | 118.9041 | 0.013732 | 0.045777 | 118.9728 | 118.895 | -0.054931 | 118.9499 | 118.8904 | -0.004577 | -0.036621 | 118.7942 | 118.8995 | 118.9728 | 0.036622 | 118.7988 | 118.8171 | 118.9865 | 0.041199
1156.2812 | 119.1101 | -118.9911 | 0.045776 | 0.097962 | -0.0016535 | -0.063089 | 0.024406 | -0.013396 | 0.0021063 | -0.0018435 | -0.0083922 | 0.016428 | 0.021121 | 0.025977 | 0.015088 | 0.017071 | 0.009155 | -0.068665 | 0.009155 | -0.004578 | -0.059509 | 0.091553 | -0.009155 | -0.009155 | 0 | -0.11902 | -0.036621 | -0.045776 | 0.082397 | -0.009155 | 119.0826 | 118.9819 | -0.10528 | 118.9224 | 118.9865 | 0.004577 | -0.036621 | 119.0735 | 118.9819 | -0.082397 | 118.9819 | 118.8721 | -0.10986 | -0.091552 | 118.9316 | 119.0002 | 119.0002 | -0.054931 | 118.9545 | 118.9453 | 118.9911 | -0.054931
1158.0156 | 119.2474 | -119.0094 | -0.009155 | 0.12085 | -0.0035761 | -0.065012 | 0.020348 | -0.010833 | -0.0013117 | -0.0016299 | 0.08316 | 0.014291 | 0.017917 | 0.025763 | 0.016584 | 0.019421 | -0.004578 | -0.064087 | -0.004578 | -0.018311 | -0.041199 | 0.09613 | -0.004578 | 0.004578 | 0 | -0.086975 | -0.045776 | -0.032043 | 0.064087 | 0.022888 | 119.1055 | 119.0048 | -0.032044 | 118.9453 | 118.9911 | -0.013733 | 0.004577 | 119.0735 | 119.0323 | -0.036621 | 119.014 | 118.9224 | -0.10986 | -0.022888 | 118.9682 | 119.0048 | 119.0048 | 0.004577 | 118.9636 | 118.9774 | 119.0094 | 0.032043
1159.7656 | 119.2474 | -119.101 | 0.036621 | 0.029297 | -0.00079888 | -0.065226 | 0.021843 | -0.010833 | -0.0013117 | -0.0041933 | 0.022125 | 0.014505 | 0.021975 | 0.02384 | 0.016797 | 0.017712 | -0.013733 | -0.064087 | 0.022888 | -0.013733 | -0.050354 | 0.10071 | -0.009155 | -0.018311 | -0.018311 | -0.12817 | -0.054932 | -0.036621 | 0.073242 | 0.004578 | 119.2017 | 119.0918 | -0.086975 | 119.0369 | 119.0872 | -0.004578 | -0.050354 | 119.1742 | 119.1055 | -0.091553 | 119.0826 | 118.9728 | -0.13275 | -0.073242 | 119.0506 | 119.0872 | 119.1238 | -0.045776 | 119.046 | 119.0643 | 119.0826 | -0.032043
1161.4531 | 119.3573 | -119.1834 | 0.018311 | -0.11566 | -0.0010125 | -0.063517 | 0.024406 | -0.01126 | -0.0036615 | -0.0041933 | -0.16098 | 0.016428 | 0.018771 | 0.023627 | 0.013379 | 0.018139 | 0 | -0.059509 | 0.032043 | 0.022888 | -0.032043 | 0.091553 | -0.018311 | 0.022888 | 0.059509 | -0.059509 | -0.032043 | -0.027466 | 0.07782 | 0.018311 | 119.2749 | 119.165 | -0.050354 | 119.1238 | 119.2062 | 0.041199 | -0.018311 | 119.2612 | 119.2017 | -0.050354 | 119.2062 | 119.1238 | -0.07782 | -0.045777 | 119.1513 | 119.1834 | 119.2154 | -0.036622 | 119.1513 | 119.1559 | 119.2429 | 0
1163.2188 | 119.3756 | -119.2474 | 0.018311 | -0.18433 | -0.0018671 | -0.060953 | 0.026115 | -0.012542 | -0.0085749 | -0.0018435 | -0.13046 | 0.014719 | 0.019839 | 0.025122 | 0.011243 | 0.01878 | 0 | -0.013733 | 0.041199 | 0.018311 | -0.064087 | 0.091553 | -0.013733 | 0.004578 | 0.050354 | -0.07782 | -0.073242 | -0.022888 | 0.064087 | 0.004578 | 119.339 | 119.2337 | -0.082398 | 119.2337 | 119.2657 | 0.032044 | -0.018311 | 119.3115 | 119.252 | -0.091553 | 119.252 | 119.1696 | -0.082398 | -0.041199 | 119.1834 | 119.2474 | 119.2886 | -0.032044 | 119.1742 | 119.2245 | 119.2978 | -0.013733
1164.9062 | 119.5587 | -119.2657 | 0.018311 | -0.1004 | -0.0029351 | -0.060099 | 0.025261 | -0.011474 | -0.0085749 | -0.0035525 | -0.061798 | 0.011728 | 0.019839 | 0.022345 | 0.011884 | 0.017071 | 0.09613 | 0.10529 | 0.16479 | 0.082397 | -0.073242 | 0.13275 | 0.018311 | 0.1236 | 0.16479 | 0.064087 | -0.073242 | -0.068665 | 0.10986 | 0.032043 | 119.3985 | 119.2841 | -0.091553 | 119.371 | 119.3481 | 0.064086 | 0.077819 | 119.3756 | 119.2978 | -0.091553 | 119.3893 | 119.3298 | 0.032044 | -0.086976 | 119.1925 | 119.3619 | 119.4305 | 0 | 119.1925 | 119.1971 | 119.4305 | 0.013732
1166.6562 | 119.5267 | -119.3481 | 0.022888 | 0.082703 | -0.0042169 | -0.066294 | 0.023125 | -0.011687 | 0.0025335 | -0.0056887 | 0.075531 | 0.016214 | 0.019839 | 0.024054 | 0.016797 | 0.017498 | -0.027466 | -0.10986 | 0 | -0.032043 | -0.032043 | 0.086975 | -0.013733 | -0.004578 | -0.013733 | -0.10986 | -0.041199 | -0.027466 | 0.050354 | 0 | 119.4351 | 119.3344 | -0.054931 | 119.2383 | 119.3161 | -0.01831 | -0.050354 | 119.3985 | 119.3481 | -0.064087 | 119.3436 | 119.2383 | -0.10986 | -0.050354 | 119.3161 | 119.3207 | 119.3481 | -0.036621 | 119.3069 | 119.3207 | 119.3344 | -0.022888
1168.4062 | 119.5862 | -119.4122 | 0.032043 | -0.15381 | 0.00048272 | -0.061808 | 0.02462 | -0.011046 | -0.0060113 | -0.0046207 | -0.21439 | 0.016214 | 0.022189 | 0.024695 | 0.013593 | 0.018352 | -0.018311 | -0.036621 | 0.032043 | -0.013733 | -0.045776 | 0.091553 | -0.004578 | -0.013733 | 0.022888 | -0.073242 | -0.036621 | -0.004578 | 0.054932 | 0.013733 | 119.5038 | 119.4077 | -0.077819 | 119.3756 | 119.3985 | -0.009155 | -0.050354 | 119.4672 | 119.426 | -0.068664 | 119.3985 | 119.339 | -0.086975 | -0.036621 | 119.3665 | 119.3939 | 119.4443 | -0.036621 | 119.3756 | 119.4077 | 119.4351 | -0.01831
1170.1562 | 119.6045 | -119.4992 | 0.036621 | 0.12085 | -0.0020807 | -0.064157 | 0.020988 | -0.011901 | -2.988e-05 | -0.0033389 | 0.014496 | 0.01301 | 0.019198 | 0.024268 | 0.018293 | 0.018139 | 0.009155 | -0.059509 | 0.027466 | -0.004578 | -0.032043 | 0.082397 | -0.013733 | -0.013733 | -0.013733 | -0.1236 | -0.032043 | -0.027466 | 0.064087 | -0.009155 | 119.5816 | 119.4855 | -0.068664 | 119.4397 | 119.4946 | 0.009155 | -0.027466 | 119.5633 | 119.4901 | -0.068664 | 119.4855 | 119.3756 | -0.11444 | -0.064087 | 119.4672 | 119.5084 | 119.5267 | -0.050354 | 119.4672 | 119.4717 | 119.4855 | -0.045776
1171.8438 | 119.7006 | -119.5129 | 0.027466 | -0.046997 | 0.00091012 | -0.063517 | 0.026756 | -0.010406 | -0.00088448 | -0.0024845 | -0.1152 | 0.016428 | 0.020053 | 0.024481 | 0.015515 | 0.017284 | 0.036621 | 0.009155 | 0.073242 | 0.027466 | -0.059509 | 0.10529 | 0 | 0.073242 | 0.07782 | -0.045776 | -0.064087 | -0.045776 | 0.068665 | 0.013733 | 119.6182 | 119.5129 | -0.086975 | 119.5221 | 119.5404 | 0.027466 | 0.009155 | 119.5816 | 119.5267 | -0.091553 | 119.5862 | 119.4672 | -0.059509 | -0.073242 | 119.4534 | 119.5496 | 119.5862 | -0.027466 | 119.4489 | 119.4672 | 119.5908 | -0.013733
1173.5938 | 119.8242 | -119.545 | 0.009155 | -0.12329 | -0.0048579 | -0.060953 | 0.023766 | -0.012328 | -0.0090021 | -0.0041933 | -0.077057 | 0.015146 | 0.017062 | 0.022559 | 0.011243 | 0.017925 | 0.07782 | 0.09613 | 0.15564 | 0.073242 | -0.082397 | 0.1236 | 0.013733 | 0.1236 | 0.17395 | 0.059509 | -0.086975 | -0.073242 | 0.09613 | 0.027466 | 119.6686 | 119.5587 | -0.091552 | 119.6411 | 119.6182 | 0.059509 | 0.068665 | 119.6411 | 119.5724 | -0.09613 | 119.6686 | 119.6045 | 0.032043 | -0.082397 | 119.4626 | 119.6228 | 119.7006 | 0.004578 | 119.458 | 119.4717 | 119.7189 | 0.018311
1175.3438 | 119.8105 | -119.6228 | 0.013733 | -0.046997 | -0.00015808 | -0.063517 | 0.020134 | -0.010833 | 0.00039732 | -0.0022707 | -0.1152 | 0.016428 | 0.017276 | 0.022559 | 0.019361 | 0.016216 | 0.068665 | -0.009155 | 0.059509 | 0.022888 | -0.050354 | 0.09613 | -0.009155 | 0.045776 | 0.07782 | -0.041199 | -0.054932 | -0.050354 | 0.082397 | 0.022888 | 119.7189 | 119.6136 | -0.064087 | 119.6136 | 119.6457 | 0.032043 | 0.054932 | 119.7052 | 119.6457 | -0.068665 | 119.6686 | 119.5816 | -0.064087 | -0.064087 | 119.5724 | 119.6915 | 119.6823 | -0.022888 | 119.5679 | 119.5724 | 119.7006 | 0.009155
1177.1094 | 119.8517 | -119.6457 | 0.018311 | -0.085144 | -0.0042169 | -0.063517 | 0.021843 | -0.011046 | -0.0010981 | -0.0035525 | -0.077057 | 0.015787 | 0.018344 | 0.02384 | 0.017865 | 0.018566 | 0.054932 | -0.013733 | 0.068665 | 0.032043 | -0.045776 | 0.09613 | -0.018311 | 0.054932 | 0.07782 | -0.050354 | -0.050354 | -0.041199 | 0.082397 | 0.027466 | 119.7418 | 119.6274 | -0.064087 | 119.632 | 119.6777 | 0.050354 | 0.036621 | 119.7281 | 119.6732 | -0.068665 | 119.7006 | 119.5953 | -0.07782 | -0.05951 | 119.5999 | 119.7006 | 119.7144 | -0.036622 | 119.5953 | 119.6045 | 119.7235 | 0.009155
1178.8594 | 119.9112 | -119.7098 | 0 | -0.12329 | 0.0015509 | -0.062448 | 0.026329 | -0.011474 | -0.0017389 | -0.0037661 | -0.12283 | 0.014719 | 0.019839 | 0.025336 | 0.014234 | 0.020489 | 0.032043 | -0.036621 | 0.059509 | 0.041199 | -0.050354 | 0.086975 | -0.018311 | 0.032043 | 0.068665 | -0.050354 | -0.050354 | -0.027466 | 0.091553 | 0.004578 | 119.7968 | 119.6915 | -0.050354 | 119.6732 | 119.751 | 0.05951 | 0.032043 | 119.8013 | 119.7144 | -0.050354 | 119.7418 | 119.6594 | -0.054932 | -0.027466 | 119.6594 | 119.7418 | 119.7693 | -0.018311 | 119.6594 | 119.6823 | 119.7784 | 0.004578
1180.5469 | 119.9615 | -119.751 | 0.032043 | -0.11566 | 5.5518e-05 | -0.063517 | 0.026543 | -0.011046 | -0.0021661 | -0.0016299 | -0.13046 | 0.01536 | 0.02048 | 0.02384 | 0.01637 | 0.017071 | 0.009155 | -0.022888 | 0.068665 | 0.045776 | -0.050354 | 0.082397 | -0.022888 | 0.041199 | 0.068665 | -0.059509 | -0.032043 | -0.032043 | 0.082397 | 0 | 119.8334 | 119.7281 | -0.082397 | 119.7281 | 119.7968 | 0.068664 | -0.022888 | 119.8334 | 119.751 | -0.064086 | 119.7922 | 119.6915 | -0.059509 | -0.064086 | 119.7006 | 119.7601 | 119.8196 | -0.054931 | 119.7189 | 119.7189 | 119.8196 | -0.032043
1182.2969 | 120.0531 | -119.7693 | 0.009155 | 0.10559 | -0.0035761 | -0.062448 | 0.022911 | -0.011687 | -0.0015253 | -0.0024845 | 0.12131 | 0.013864 | 0.020907 | 0.025549 | 0.015088 | 0.017498 | -0.004578 | -0.050354 | 0.013733 | 0.004578 | -0.050354 | 0.086975 | -0.013733 | 0.022888 | 0.018311 | -0.064087 | -0.036621 | -0.027466 | 0.064087 | 0.013733 | 119.8563 | 119.7556 | -0.059509 | 119.7189 | 119.7739 | 0.018311 | -0.013733 | 119.8334 | 119.783 | -0.045776 | 119.7922 | 119.7052 | -0.07782 | -0.036621 | 119.7189 | 119.7647 | 119.783 | -0.022888 | 119.7327 | 119.7418 | 119.7876 | 0.004578
1183.9844 | 120.0897 | -119.8105 | 0.009155 | 0.17426 | -0.0031489 | -0.065012 | 0.021202 | -0.012115 | -0.0079339 | -0.0035525 | 0.1976 | 0.014719 | 0.018771 | 0.025122 | 0.012311 | 0.017498 | 0.07782 | 0.064087 | 0.15106 | 0.086975 | -0.082397 | 0.1236 | 0.041199 | 0.13275 | 0.13733 | 0.045776 | -0.09613 | -0.086975 | 0.11444 | 0.032043 | 119.9341 | 119.8517 | -0.091552 | 119.8746 | 119.8975 | 0.045776 | 0.068665 | 119.9249 | 119.8425 | -0.10528 | 119.9432 | 119.8563 | 0.013733 | -0.09613 | 119.7281 | 119.8883 | 119.9615 | 0.032044 | 119.7144 | 119.7235 | 119.9478 | 0.022888
1185.7344 | 120.1218 | -119.8791 | 0.022888 | 0.067444 | -0.0031489 | -0.061167 | 0.023766 | -0.010406 | -0.0077203 | -0.0031253 | 0.098419 | 0.013864 | 0.020053 | 0.024268 | 0.012738 | 0.018993 | 0.027466 | 0.013733 | 0.086975 | 0.045776 | -0.073242 | 0.13733 | 0.013733 | 0.068665 | 0.068665 | -0.022888 | -0.054932 | -0.045776 | 0.086975 | 0.032043 | 120.0165 | 119.8929 | -0.09613 | 119.8929 | 119.9249 | 0.032043 | 0.004578 | 119.9661 | 119.9112 | -0.07782 | 119.9478 | 119.8563 | -0.054931 | -0.068664 | 119.8059 | 119.9066 | 119.9661 | -0.009155 | 119.8242 | 119.8334 | 119.9478 | 0.009155
1187.4219 | 120.1996 | -119.8975 | 0.004578 | 0.18951 | -0.0044305 | -0.062662 | 0.022484 | -0.010619 | -0.0034479 | -0.0033389 | 0.15182 | 0.012796 | 0.015994 | 0.023199 | 0.018079 | 0.017498 | 0.086975 | 0.07782 | 0.12817 | 0.07782 | -0.082397 | 0.13275 | 0.027466 | 0.1236 | 0.1236 | 0.032043 | -0.09613 | -0.082397 | 0.11444 | 0.032043 | 120.0302 | 119.9249 | -0.086975 | 119.9753 | 119.9753 | 0.050354 | 0.082397 | 120.0119 | 119.9295 | -0.10071 | 120.0211 | 119.9295 | 0 | -0.086975 | 119.8151 | 119.9844 | 120.0256 | 0.022888 | 119.8013 | 119.8151 | 120.0211 | 0.027465
1189.1719 | 120.2316 | -119.9249 | 0.009155 | 0.0064086 | -0.0057123 | -0.060099 | 0.025261 | -0.012755 | -0.0066523 | -0.0031253 | 0.045013 | 0.011087 | 0.018344 | 0.024695 | 0.014234 | 0.019421 | 0.018311 | 0.018311 | 0.10071 | 0.045776 | -0.059509 | 0.10986 | 0.018311 | 0.073242 | 0.073242 | -0.009155 | -0.064087 | -0.045776 | 0.10986 | 0.018311 | 120.0348 | 119.9432 | -0.068664 | 119.9432 | 119.9707 | 0.027465 | 0.009156 | 120.0348 | 119.9432 | -0.073242 | 119.9982 | 119.9158 | -0.027466 | -0.054931 | 119.8654 | 119.9432 | 120.0256 | 0.009156 | 119.8608 | 119.8792 | 119.9982 | 0.009156
1190.9219 | 120.2728 | -119.9615 | 0 | 0.097962 | -0.0035761 | -0.061167 | 0.020348 | -0.011046 | -0.0013117 | -0.0054751 | 0.12894 | 0.013223 | 0.017062 | 0.024695 | 0.017224 | 0.017498 | 0.091553 | 0.054932 | 0.11902 | 0.082397 | -0.086975 | 0.1236 | 0.018311 | 0.11902 | 0.10986 | 0.027466 | -0.10071 | -0.068665 | 0.11444 | 0.032043 | 120.0851 | 119.9799 | -0.086975 | 120.0165 | 120.0439 | 0.064086 | 0.091553 | 120.076 | 119.9936 | -0.10071 | 120.0806 | 119.989 | -0.004577 | -0.068665 | 119.8746 | 120.0531 | 120.0806 | 0.018311 | 119.8608 | 119.8929 | 120.0714 | 0.032043
1192.6094 | 120.2728 | -120.0256 | 0.018311 | 0.12848 | -0.0048579 | -0.061808 | 0.023766 | -0.014464 | -0.0051569 | -0.0071841 | 0.12894 | 0.014078 | 0.017276 | 0.023199 | 0.012097 | 0.016857 | 0.086975 | 0.068665 | 0.13275 | 0.045776 | -0.09613 | 0.11444 | 0.027466 | 0.09613 | 0.082397 | -0.004578 | -0.073242 | -0.068665 | 0.10071 | 0.036621 | 120.1401 | 120.0531 | -0.11444 | 120.0943 | 120.0714 | 0.01831 | 0.068664 | 120.1263 | 120.0623 | -0.091553 | 120.1218 | 120.0211 | -0.041199 | -0.086976 | 119.9295 | 120.1126 | 120.1584 | 0.009155 | 119.9524 | 119.957 | 120.108 | 0.01831
1194.3594 | 120.2499 | -120.0668 | 0.009155 | 0.090332 | -0.0025079 | -0.063303 | 0.021843 | -0.010406 | 0.0018927 | -0.0050479 | 0.067902 | 0.015573 | 0.018771 | 0.024481 | 0.01637 | 0.015575 | 0.004578 | -0.091553 | 0.004578 | 0.004578 | -0.032043 | 0.091553 | -0.018311 | 0.018311 | -0.027466 | -0.11902 | -0.054932 | -0.013733 | 0.086975 | 0.004578 | 120.1584 | 120.0485 | -0.041198 | 119.9753 | 120.0714 | 0.022889 | -0.004577 | 120.1538 | 120.0714 | -0.064087 | 120.0851 | 119.9478 | -0.1236 | -0.022888 | 120.0348 | 120.0714 | 120.0714 | -0.027466 | 120.0119 | 120.0531 | 120.0394 | -0.004577
1196.125 | 120.2957 | -120.108 | 0.059509 | -0.13855 | -0.0012263 | -0.061594 | 0.025902 | -0.010406 | -0.0066523 | -0.0031253 | -0.1152 | 0.011942 | 0.019412 | 0.024268 | 0.012525 | 0.015362 | 0.091553 | 0.07782 | 0.14648 | 0.068665 | -0.07782 | 0.11902 | 0.004578 | 0.10529 | 0.13275 | 0.027466 | -0.086975 | -0.041199 | 0.09613 | 0.045776 | 120.2271 | 120.1126 | -0.13733 | 120.1859 | 120.1767 | 0.064087 | 0.032044 | 120.2042 | 120.1538 | -0.14648 | 120.2133 | 120.1355 | -0.01831 | -0.10071 | 120.0302 | 120.1996 | 120.2545 | -0.054931 | 120.0211 | 120.0668 | 120.2408 | -0.013733
1197.8281 | 120.4422 | -120.1126 | 0.009155 | -0.0012209 | -0.0037897 | -0.06074 | 0.022911 | -0.013183 | -0.0066523 | -0.0056887 | -0.016022 | 0.011087 | 0.019839 | 0.022986 | 0.010175 | 0.017712 | 0.032043 | 0.032043 | 0.10071 | 0.045776 | -0.073242 | 0.10529 | 0.018311 | 0.11444 | 0.11444 | 0.013733 | -0.086975 | -0.054932 | 0.10986 | 0.027466 | 120.2179 | 120.1309 | -0.082397 | 120.1447 | 120.1584 | 0.027465 | 0.022888 | 120.2225 | 120.1401 | -0.09613 | 120.2271 | 120.1263 | -0.013733 | -0.064087 | 120.0394 | 120.1447 | 120.2133 | 0.009156 | 120.0256 | 120.0577 | 120.2271 | 0.018311
1199.7188 | 120.4742 | -120.1401 | 0 | 0.16663 | -0.0031489 | -0.06138 | 0.020134 | -0.015105 | -0.0015253 | -0.0041933 | -0.00076274 | 0.016214 | 0.016849 | 0.024481 | 0.016156 | 0.015575 | 0.07782 | 0.013733 | 0.10529 | 0.054932 | -0.068665 | 0.11444 | 0.022888 | 0.13275 | 0.10986 | 0.018311 | -0.086975 | -0.064087 | 0.10529 | 0.050354 | 120.2545 | 120.163 | -0.068665 | 120.1538 | 120.195 | 0.032044 | 0.07782 | 120.2454 | 120.1904 | -0.086975 | 120.2728 | 120.1584 | -0.032043 | -0.064087 | 120.0714 | 120.2179 | 120.2454 | 0.022888 | 120.0531 | 120.076 | 120.2499 | 0.050354
1201.4688 | 120.4926 | -120.1767 | -0.009155 | -0.0012209 | -0.0061395 | -0.059885 | 0.021629 | -0.015533 | -0.0053705 | -0.0046207 | 0.022125 | 0.011301 | 0.016208 | 0.021277 | 0.013593 | 0.016857 | 0.036621 | 0.022888 | 0.10986 | 0.054932 | -0.073242 | 0.13275 | 0.009155 | 0.10529 | 0.10529 | 0.013733 | -0.07782 | -0.059509 | 0.11444 | 0.027466 | 120.3094 | 120.1859 | -0.064087 | 120.1996 | 120.2316 | 0.045777 | 0.045776 | 120.2911 | 120.2042 | -0.068665 | 120.282 | 120.1904 | -0.013733 | -0.050354 | 120.1035 | 120.2133 | 120.2866 | 0.01831 | 120.0989 | 120.1172 | 120.282 | 0.036621
1203.2188 | 120.3873 | -120.2637 | 0.027466 | -0.18433 | 0.00048272 | -0.06074 | 0.025475 | -0.010406 | -0.0030207 | -0.0039797 | -0.16861 | 0.014932 | 0.022403 | 0.023199 | 0.014661 | 0.017498 | 0.018311 | -0.032043 | 0.041199 | 0.009155 | -0.059509 | 0.07782 | -0.018311 | 0.009155 | 0.050354 | -0.082397 | -0.032043 | -0.018311 | 0.073242 | -0.018311 | 120.3415 | 120.2454 | -0.086975 | 120.2316 | 120.2728 | 0.027466 | -0.009155 | 120.3369 | 120.2454 | -0.059509 | 120.2728 | 120.1813 | -0.064086 | -0.045777 | 120.2042 | 120.282 | 120.3049 | -0.045777 | 120.2316 | 120.2454 | 120.314 | -0.045777
1204.9688 | 120.4559 | -120.2591 | 0.041199 | -0.1767 | -0.0012263 | -0.062021 | 0.026329 | -0.015105 | -2.988e-05 | -0.0026981 | -0.1915 | 0.015573 | 0.019412 | 0.024695 | 0.013806 | 0.013439 | 0.013733 | -0.054932 | 0.022888 | 0.004578 | -0.022888 | 0.10071 | -0.018311 | 0.022888 | 0.041199 | -0.086975 | -0.022888 | -0.027466 | 0.064087 | 0.004578 | 120.3598 | 120.2408 | -0.064087 | 120.2042 | 120.2637 | 0.022889 | -0.027466 | 120.3232 | 120.2637 | -0.064087 | 120.282 | 120.1721 | -0.091553 | -0.068665 | 120.2362 | 120.2728 | 120.282 | -0.05951 | 120.2362 | 120.2316 | 120.3003 | -0.036621
1206.7188 | 120.575 | -120.2682 | 0 | 0.029297 | -0.0022943 | -0.062021 | 0.024406 | -0.014251 | -0.0070795 | -0.0046207 | 0.045013 | 0.011728 | 0.018558 | 0.024268 | 0.01402 | 0.017925 | 0.018311 | 0.018311 | 0.10529 | 0.045776 | -0.082397 | 0.10986 | 0.022888 | 0.082397 | 0.086975 | 0 | -0.073242 | -0.045776 | 0.09613 | 0.018311 | 120.3781 | 120.2911 | -0.082397 | 120.2866 | 120.314 | 0.022888 | 0.018311 | 120.3644 | 120.2866 | -0.073242 | 120.3506 | 120.2682 | -0.018311 | -0.045776 | 120.1859 | 120.2866 | 120.3735 | 0.022888 | 120.195 | 120.2225 | 120.3552 | 0.018311
1208.4688 | 120.4559 | -120.3278 | 0.018311 | -0.0088499 | -0.00037168 | -0.06373 | 0.02227 | -0.013396 | 0.00082452 | -0.0046207 | -0.031281 | 0.016 | 0.017703 | 0.025549 | 0.016797 | 0.015575 | 0.045776 | -0.004578 | 0.041199 | 0.032043 | -0.036621 | 0.10986 | -0.009155 | 0.041199 | 0.022888 | -0.09613 | -0.059509 | -0.036621 | 0.068665 | 0.013733 | 120.4376 | 120.3186 | -0.054932 | 120.3232 | 120.3598 | 0.041198 | 0.027465 | 120.3964 | 120.3415 | -0.07782 | 120.369 | 120.2316 | -0.10986 | -0.054932 | 120.2911 | 120.3735 | 120.369 | -0.027466 | 120.2682 | 120.2911 | 120.3506 | -0.004578
1210.1562 | 120.5795 | -120.3415 | -0.013733 | 0.12848 | -0.0050715 | -0.063303 | 0.021416 | -0.013183 | -0.0062249 | -0.0012027 | 0.1442 | 0.012155 | 0.014926 | 0.024054 | 0.014875 | 0.018993 | 0.10071 | 0.064087 | 0.14648 | 0.07782 | -0.10071 | 0.14648 | 0.022888 | 0.13275 | 0.12817 | 0.027466 | -0.082397 | -0.059509 | 0.10529 | 0.050354 | 120.488 | 120.3644 | -0.086975 | 120.4056 | 120.4193 | 0.054932 | 0.11444 | 120.4468 | 120.3918 | -0.068664 | 120.4742 | 120.369 | -0.022888 | -0.045776 | 120.2408 | 120.4422 | 120.488 | 0.036621 | 120.2591 | 120.282 | 120.4697 | 0.064087
1211.9062 | 120.5292 | -120.4285 | 0.032043 | -0.1767 | -0.00079888 | -0.062876 | 0.025902 | -0.012542 | -0.0045161 | -0.0026981 | -0.10757 | 0.014719 | 0.020907 | 0.024908 | 0.014447 | 0.017712 | 0.041199 | 0.018311 | 0.073242 | 0.036621 | -0.045776 | 0.09613 | -0.004578 | 0.027466 | 0.050354 | -0.059509 | -0.07782 | -0.036621 | 0.073242 | 0.004578 | 120.5246 | 120.4239 | -0.077819 | 120.4468 | 120.4651 | 0.041199 | 0.009156 | 120.5017 | 120.433 | -0.10986 | 120.4559 | 120.369 | -0.064087 | -0.068664 | 120.3827 | 120.4697 | 120.5017 | -0.036621 | 120.3506 | 120.3918 | 120.4788 | -0.027465
1213.6562 | 120.6573 | -120.3873 | -0.004578 | 0.159 | -0.0050715 | -0.060099 | 0.018425 | -0.0097646 | -0.0023797 | -0.0046207 | 0.1442 | 0.014505 | 0.01578 | 0.023627 | 0.017438 | 0.016216 | 0.10986 | 0.064087 | 0.14191 | 0.082397 | -0.082397 | 0.12817 | 0.022888 | 0.14648 | 0.1236 | 0.027466 | -0.10071 | -0.07782 | 0.11444 | 0.045776 | 120.5154 | 120.4102 | -0.077819 | 120.4514 | 120.4697 | 0.059509 | 0.11444 | 120.5017 | 120.433 | -0.09613 | 120.5338 | 120.4147 | -0.01831 | -0.073242 | 120.3049 | 120.4971 | 120.5292 | 0.027466 | 120.2866 | 120.3094 | 120.5109 | 0.050354
1215.3594 | 120.6665 | -120.4193 | 0.004578 | 0.052185 | -0.0069941 | -0.061167 | 0.021843 | -0.016387 | -0.0060113 | -0.0031253 | 0.060272 | 0.012369 | 0.017276 | 0.022559 | 0.014447 | 0.01878 | 0.027466 | 0.018311 | 0.10529 | 0.041199 | -0.068665 | 0.11444 | 0.013733 | 0.082397 | 0.09613 | -0.013733 | -0.07782 | -0.064087 | 0.091553 | 0.022888 | 120.5338 | 120.433 | -0.073243 | 120.4376 | 120.4605 | 0.027466 | 0.022888 | 120.5109 | 120.4422 | -0.082398 | 120.5017 | 120.4056 | -0.036621 | -0.068665 | 120.3506 | 120.4468 | 120.5246 | 0.009155 | 120.3415 | 120.3552 | 120.5154 | 0.01831
1217.1094 | 120.694 | -120.4514 | 0.004578 | 0.052185 | -0.0065667 | -0.059244 | 0.022911 | -0.012328 | -0.0049433 | -0.00077552 | 0.10605 | 0.012582 | 0.017917 | 0.022986 | 0.013806 | 0.01643 | 0.059509 | 0.045776 | 0.091553 | 0.036621 | -0.086975 | 0.11444 | 0.036621 | 0.09613 | 0.086975 | -0.009155 | -0.082397 | -0.064087 | 0.10529 | 0.041199 | 120.5658 | 120.488 | -0.091553 | 120.4971 | 120.488 | 0 | 0.054931 | 120.5566 | 120.4926 | -0.086975 | 120.5475 | 120.4422 | -0.050354 | -0.068665 | 120.3644 | 120.5109 | 120.5429 | 0.032043 | 120.369 | 120.3873 | 120.5383 | 0.036621
1218.7969 | 120.726 | -120.4605 | 0.004578 | 0.17426 | -0.0048579 | -0.062876 | 0.01928 | -0.013183 | -0.0021661 | -0.0012027 | 0.13657 | 0.012155 | 0.01578 | 0.023627 | 0.019147 | 0.016857 | 0.1236 | 0.059509 | 0.15564 | 0.09613 | -0.09613 | 0.13275 | 0.009155 | 0.12817 | 0.12817 | 0.032043 | -0.07782 | -0.068665 | 0.10986 | 0.041199 | 120.5933 | 120.4697 | -0.10071 | 120.52 | 120.5566 | 0.086975 | 0.11902 | 120.5704 | 120.5017 | -0.082398 | 120.5887 | 120.4926 | -0.009156 | -0.073243 | 120.3644 | 120.5841 | 120.6162 | 0.004577 | 120.3827 | 120.3918 | 120.5887 | 0.036621
1220.5469 | 120.6894 | -120.52 | 0.013733 | 0.097962 | -0.0031489 | -0.063944 | 0.020348 | -0.012755 | 0.0029607 | -0.0018435 | 0.052643 | 0.016855 | 0.018344 | 0.024054 | 0.018293 | 0.016857 | 0.013733 | -0.086975 | 0 | 0.004578 | -0.064087 | 0.10529 | -0.013733 | 0.013733 | -0.022888 | -0.10986 | -0.036621 | -0.032043 | 0.068665 | 0.022888 | 120.6253 | 120.5063 | -0.07782 | 120.433 | 120.5246 | 0.018311 | 0 | 120.5887 | 120.5429 | -0.050354 | 120.5338 | 120.4102 | -0.13275 | -0.045776 | 120.4559 | 120.5338 | 120.52 | -0.027466 | 120.4834 | 120.488 | 120.4971 | 0.009155
1222.25 | 120.7397 | -120.5063 | 0.004578 | 0.13611 | -0.0012263 | -0.062876 | 0.023979 | -0.012542 | 0.00061092 | -0.0012027 | 0.060272 | 0.014719 | 0.018558 | 0.023413 | 0.015515 | 0.01643 | 0.022888 | -0.064087 | 0.004578 | -0.009155 | -0.041199 | 0.091553 | -0.018311 | 0.027466 | 0.009155 | -0.091553 | -0.036621 | -0.022888 | 0.086975 | 0.013733 | 120.5978 | 120.488 | -0.045777 | 120.4422 | 120.4971 | 0.009156 | 0.01831 | 120.5933 | 120.52 | -0.041199 | 120.5338 | 120.4147 | -0.10529 | -0.027466 | 120.4651 | 120.5292 | 120.5109 | -0.022889 | 120.4697 | 120.4834 | 120.5154 | 0.009155
1224 | 120.7214 | -120.5795 | 0.018311 | -0.1767 | -0.0012263 | -0.061167 | 0.025475 | -0.012115 | -0.0038751 | -0.0037661 | -0.16861 | 0.014078 | 0.016635 | 0.022345 | 0.013379 | 0.017284 | 0.009155 | -0.036621 | 0.050354 | 0.004578 | -0.032043 | 0.091553 | -0.009155 | 0.004578 | 0.041199 | -0.07782 | -0.036621 | -0.041199 | 0.07782 | 0.004578 | 120.6711 | 120.5704 | -0.050354 | 120.5429 | 120.5841 | 0.013733 | -0.009156 | 120.6573 | 120.5841 | -0.054932 | 120.5841 | 120.5017 | -0.082398 | -0.05951 | 120.5475 | 120.5887 | 120.6299 | -0.027466 | 120.5429 | 120.5383 | 120.6207 | -0.013733
1225.75 | 120.8542 | -120.5429 | -0.013733 | 0.014038 | -0.0022943 | -0.062876 | 0.023125 | -0.011687 | -0.0081477 | -0.0029117 | 0.022125 | 0.012796 | 0.019412 | 0.024908 | 0.010816 | 0.017925 | 0.018311 | 0.018311 | 0.086975 | 0.045776 | -0.073242 | 0.10986 | 0.013733 | 0.082397 | 0.10529 | 0.018311 | -0.082397 | -0.045776 | 0.11902 | 0.036621 | 120.6528 | 120.5566 | -0.059509 | 120.5612 | 120.5887 | 0.032043 | 0.032044 | 120.6619 | 120.5795 | -0.068664 | 120.6253 | 120.5612 | -0.01831 | -0.032043 | 120.4697 | 120.5612 | 120.6299 | 0.027466 | 120.4605 | 120.4971 | 120.6482 | 0.050354
1227.5 | 120.726 | -120.6024 | 0.036621 | -0.031738 | -0.0012263 | -0.063303 | 0.020775 | -0.014251 | 0.0023199 | -0.0031253 | -0.069428 | 0.015573 | 0.017917 | 0.024695 | 0.018293 | 0.017498 | 0.068665 | -0.009155 | 0.059509 | 0.027466 | -0.050354 | 0.10529 | -0.018311 | 0.045776 | 0.032043 | -0.07782 | -0.064087 | -0.050354 | 0.073242 | -0.009155 | 120.7077 | 120.5841 | -0.086975 | 120.5933 | 120.6299 | 0.045777 | 0.032044 | 120.6757 | 120.5933 | -0.10071 | 120.6482 | 120.5246 | -0.068665 | -0.086975 | 120.5521 | 120.6711 | 120.6619 | -0.054932 | 120.5383 | 120.5521 | 120.6345 | -0.045776
1229.2031 | 120.8359 | -120.6299 | 0.032043 | -0.16144 | -0.0029351 | -0.061594 | 0.025688 | -0.011901 | -0.0077203 | -0.0046207 | -0.13046 | 0.011728 | 0.018558 | 0.021918 | 0.011457 | 0.018139 | 0.07782 | 0.10071 | 0.15106 | 0.082397 | -0.082397 | 0.1236 | 0.009155 | 0.10986 | 0.16479 | 0.041199 | -0.086975 | -0.068665 | 0.09613 | 0.027466 | 120.7535 | 120.639 | -0.11444 | 120.7306 | 120.7123 | 0.073242 | 0.045777 | 120.726 | 120.6573 | -0.11902 | 120.7397 | 120.6711 | 0.013733 | -0.10071 | 120.5475 | 120.7077 | 120.7809 | -0.022888 | 120.5429 | 120.5612 | 120.7947 | -0.004577
1230.9375 | 120.7672 | -120.6253 | 0.022888 | -0.0088499 | -0.00058528 | -0.06373 | 0.020775 | -0.015105 | 0.0021063 | -0.0024845 | -0.023651 | 0.016428 | 0.01813 | 0.024054 | 0.01872 | 0.015789 | 0.050354 | -0.013733 | 0.041199 | 0.018311 | -0.064087 | 0.09613 | -0.013733 | 0.018311 | 0.022888 | -0.091553 | -0.041199 | -0.045776 | 0.091553 | 0.027466 | 120.7214 | 120.6116 | -0.086975 | 120.6116 | 120.6436 | 0.032044 | 0.027466 | 120.7169 | 120.6528 | -0.064087 | 120.6436 | 120.5338 | -0.11902 | -0.068664 | 120.5612 | 120.6757 | 120.6665 | -0.036621 | 120.5841 | 120.5795 | 120.6482 | 0.004578
1232.6875 | 120.8954 | -120.6345 | 0.009155 | 0.052185 | -0.0012263 | -0.059885 | 0.02227 | -0.012542 | -0.0079339 | -0.0012027 | 0.075531 | 0.013437 | 0.017917 | 0.021918 | 0.01167 | 0.018566 | 0.045776 | 0.013733 | 0.091553 | 0.036621 | -0.082397 | 0.11444 | 0.009155 | 0.07782 | 0.09613 | -0.013733 | -0.073242 | -0.059509 | 0.10529 | 0.018311 | 120.7489 | 120.6436 | -0.091552 | 120.6482 | 120.6711 | 0.027466 | 0.036621 | 120.7397 | 120.6528 | -0.082397 | 120.7123 | 120.6207 | -0.032044 | -0.068664 | 120.5521 | 120.6802 | 120.726 | 0 | 120.5612 | 120.575 | 120.7306 | 0.009156
1234.4531 | 120.8633 | -120.694 | 0.036621 | -0.16144 | -0.0050715 | -0.062662 | 0.023979 | -0.011046 | -0.0053705 | -0.0046207 | -0.10757 | 0.014291 | 0.018344 | 0.023413 | 0.015088 | 0.01643 | 0.10529 | 0.073242 | 0.14191 | 0.086975 | -0.086975 | 0.11902 | 0.032043 | 0.10986 | 0.17395 | 0.032043 | -0.086975 | -0.073242 | 0.10529 | 0.032043 | 120.813 | 120.726 | -0.1236 | 120.7672 | 120.7809 | 0.054932 | 0.068665 | 120.7993 | 120.726 | -0.1236 | 120.8038 | 120.726 | 0 | -0.10986 | 120.607 | 120.7993 | 120.8359 | -0.004578 | 120.607 | 120.6207 | 120.8679 | -0.004578
1236.1406 | 120.9045 | -120.7031 | 0.018311 | -0.14618 | -0.00058528 | -0.063303 | 0.024834 | -0.01361 | -2.988e-05 | -0.00077552 | -0.21439 | 0.014291 | 0.019198 | 0.025763 | 0.015515 | 0.015362 | 0.022888 | -0.050354 | 0.032043 | 0.022888 | -0.050354 | 0.07782 | -0.009155 | 0.032043 | 0.073242 | -0.073242 | -0.041199 | -0.036621 | 0.045776 | 0.004578 | 120.7809 | 120.694 | -0.068665 | 120.6528 | 120.726 | 0.032043 | 0.004577 | 120.7489 | 120.7077 | -0.05951 | 120.7352 | 120.6299 | -0.07782 | -0.054932 | 120.6528 | 120.726 | 120.7352 | -0.027466 | 120.6619 | 120.6665 | 120.7764 | -0.013733
1237.8906 | 120.8862 | -120.7443 | 0.018311 | -0.15381 | -0.0042169 | -0.059885 | 0.023766 | -0.010192 | -0.0053705 | -0.0044071 | -0.1915 | 0.013864 | 0.017276 | 0.024695 | 0.012952 | 0.018352 | 0.064087 | 0.054932 | 0.13733 | 0.059509 | -0.082397 | 0.1236 | 0.027466 | 0.064087 | 0.1236 | -0.009155 | -0.068665 | -0.032043 | 0.086975 | 0.022888 | 120.8679 | 120.7718 | -0.10071 | 120.7993 | 120.8038 | 0.032043 | 0.045776 | 120.8313 | 120.7672 | -0.086976 | 120.8084 | 120.7352 | -0.032043 | -0.050354 | 120.6619 | 120.8084 | 120.8817 | 0.009155 | 120.6757 | 120.7123 | 120.8679 | 0.004577
1239.6562 | 120.9 | -120.7306 | 0.036621 | 0.029297 | -0.00058528 | -0.061594 | 0.021629 | -0.011474 | 0.00061092 | -0.0026981 | -0.00076274 | 0.016428 | 0.020053 | 0.025763 | 0.019361 | 0.01643 | 0.022888 | -0.059509 | 0.022888 | 0.009155 | -0.059509 | 0.09613 | -0.027466 | -0.004578 | -0.009155 | -0.11444 | -0.045776 | -0.041199 | 0.059509 | -0.004578 | 120.8267 | 120.7031 | -0.09613 | 120.6711 | 120.7397 | 0.036621 | -0.013733 | 120.7901 | 120.726 | -0.082397 | 120.726 | 120.6162 | -0.10986 | -0.07782 | 120.6711 | 120.7535 | 120.7535 | -0.064087 | 120.6848 | 120.6894 | 120.7214 | -0.041199
1241.3438 | 120.9229 | -120.7855 | 0.036621 | -0.13092 | -0.0010125 | -0.06138 | 0.026543 | -0.011046 | -0.0085749 | -0.0026981 | -0.15335 | 0.013437 | 0.01813 | 0.025336 | 0.011457 | 0.017284 | 0.054932 | 0.07782 | 0.14191 | 0.068665 | -0.082397 | 0.11902 | 0.004578 | 0.07782 | 0.14191 | 0 | -0.07782 | -0.054932 | 0.086975 | 0.018311 | 120.9045 | 120.7901 | -0.11902 | 120.8633 | 120.8542 | 0.064087 | 0.018311 | 120.8725 | 120.8038 | -0.11444 | 120.8633 | 120.7855 | -0.018311 | -0.091553 | 120.7031 | 120.8405 | 120.9274 | -0.032043 | 120.7077 | 120.7306 | 120.9274 | -0.01831
1243.0938 | 120.9824 | -120.7947 | 0.022888 | -0.15381 | -0.0031489 | -0.063944 | 0.023552 | -0.012755 | -0.0015253 | -0.0048343 | -0.1915 | 0.01536 | 0.017276 | 0.024268 | 0.018506 | 0.016857 | 0.018311 | -0.036621 | 0.027466 | 0.022888 | -0.041199 | 0.086975 | -0.013733 | 0.032043 | 0.054932 | -0.068665 | -0.054932 | -0.022888 | 0.073242 | 0.004578 | 120.8817 | 120.7809 | -0.064087 | 120.7581 | 120.8176 | 0.036621 | -0.004577 | 120.8679 | 120.7993 | -0.07782 | 120.8267 | 120.726 | -0.073243 | -0.045776 | 120.7535 | 120.813 | 120.8221 | -0.036621 | 120.7397 | 120.7718 | 120.8496 | -0.01831
1245.4688 | 121.0464 | -120.7718 | 0.018311 | -0.12329 | -0.0040033 | -0.058176 | 0.021843 | -0.013396 | -0.0083613 | -0.0037661 | -0.1152 | 0.011514 | 0.015994 | 0.022559 | 0.015515 | 0.020489 | 0.091553 | 0.10529 | 0.15564 | 0.07782 | -0.086975 | 0.10529 | 0.022888 | 0.1236 | 0.17853 | 0.064087 | -0.064087 | -0.07782 | 0.11444 | 0.036621 | 120.8771 | 120.7947 | -0.10529 | 120.8771 | 120.8496 | 0.054932 | 0.073242 | 120.8862 | 120.8084 | -0.082398 | 120.8954 | 120.8359 | 0.027466 | -0.096131 | 120.6848 | 120.8633 | 120.9274 | 0.004577 | 120.7077 | 120.694 | 120.9503 | 0.01831
1248.7812 | 121.0648 | -120.8038 | 0 | 0.12085 | -0.0035761 | -0.061167 | 0.01992 | -0.012542 | -0.00024348 | -0.0033389 | 0.067902 | 0.018137 | 0.018771 | 0.024054 | 0.017011 | 0.015362 | 0.027466 | -0.050354 | 0.018311 | -0.013733 | -0.036621 | 0.10529 | -0.022888 | 0.036621 | 0.009155 | -0.073242 | -0.050354 | -0.027466 | 0.086975 | 0.013733 | 120.9091 | 120.7809 | -0.036621 | 120.7535 | 120.7901 | 0.009155 | 0.027466 | 120.8908 | 120.8176 | -0.050354 | 120.8405 | 120.7306 | -0.086975 | -0.027466 | 120.7672 | 120.8313 | 120.8221 | -0.022888 | 120.7535 | 120.7764 | 120.813 | 0.013733
1252.2656 | 121.1014 | -120.8405 | 0.009155 | 0.159 | -0.0031489 | -0.06074 | 0.022697 | -0.012542 | -0.0047297 | -0.00098912 | 0.13657 | 0.017282 | 0.032657 | 0.025336 | 0.014234 | 0.016216 | 0.11444 | 0.073242 | 0.15106 | 0.07782 | -0.09613 | 0.12817 | 0.027466 | 0.13733 | 0.14191 | 0.045776 | -0.073242 | -0.064087 | 0.13275 | 0.036621 | 120.9686 | 120.8679 | -0.10528 | 120.9137 | 120.9183 | 0.050354 | 0.10529 | 120.9732 | 120.8771 | -0.082397 | 120.9778 | 120.8862 | 0.009155 | -0.073242 | 120.7443 | 120.9549 | 120.9915 | 0.018311 | 120.7672 | 120.7764 | 120.9824 | 0.027466
1257.8594 | 121.1243 | -120.9045 | 0.022888 | -0.16144 | -0.0035761 | -0.062235 | 0.022911 | -0.012542 | -0.0025935 | -0.0012027 | -0.1915 | 0.017709 | 0.030948 | 0.02384 | 0.013379 | 0.015362 | 0.013733 | -0.054932 | 0.027466 | 0.018311 | -0.036621 | 0.10071 | -0.022888 | 0.009155 | 0.041199 | -0.073242 | -0.032043 | -0.004578 | 0.07782 | 0.004578 | 121.0052 | 120.8817 | -0.059509 | 120.8496 | 120.9229 | 0.041199 | -0.009155 | 120.9824 | 120.9091 | -0.054931 | 120.9137 | 120.8313 | -0.07782 | -0.027466 | 120.8679 | 120.9183 | 120.932 | -0.045776 | 120.8725 | 120.9 | 120.9457 | -0.01831
1259.6406 | 121.1334 | -120.9229 | 0.054932 | -0.19196 | -0.0016535 | -0.062021 | 0.025688 | -0.012115 | -0.00088448 | -0.0048343 | -0.18387 | 0.017709 | 0.030734 | 0.024695 | 0.01402 | 0.016216 | -0.013733 | -0.045776 | 0.013733 | 0.009155 | -0.050354 | 0.086975 | -0.018311 | 0.009155 | 0.027466 | -0.09613 | -0.036621 | -0.022888 | 0.082397 | 0.009155 | 121.0098 | 120.9045 | -0.10529 | 120.8771 | 120.932 | 0.027466 | -0.068665 | 121.0052 | 120.932 | -0.091553 | 120.932 | 120.8267 | -0.10528 | -0.07782 | 120.8725 | 120.9091 | 120.9366 | -0.073243 | 120.8862 | 120.9 | 120.9503 | -0.045777
1261.3438 | 121.1334 | -120.9366 | 0.027466 | 0.082703 | -0.0025079 | -0.061808 | 0.023766 | -0.012755 | -0.00045708 | -0.00098912 | 0.09079 | 0.020914 | 0.031375 | 0.025977 | 0.015088 | 0.016643 | 0.009155 | -0.091553 | 0.013733 | 0 | -0.045776 | 0.11444 | -0.009155 | 0.027466 | -0.018311 | -0.09613 | -0.045776 | -0.013733 | 0.082397 | 0.009155 | 121.051 | 120.9274 | -0.073242 | 120.845 | 120.9366 | 0.009155 | -0.018311 | 121.019 | 120.9457 | -0.073242 | 120.9641 | 120.8405 | -0.10528 | -0.041199 | 120.8908 | 120.9457 | 120.9503 | -0.036621 | 120.8908 | 120.9229 | 120.9183 | -0.018311
1263.0469 | 121.0922 | -120.9641 | 0.032043 | 0.029297 | -0.0022943 | -0.063089 | 0.022057 | -0.010192 | 0.00039732 | -0.0020571 | 0.045013 | 0.021982 | 0.033298 | 0.023199 | 0.016156 | 0.018139 | 0.022888 | -0.041199 | 0.032043 | 0 | -0.064087 | 0.10071 | 0 | 0.009155 | 0.018311 | -0.09613 | -0.059509 | -0.022888 | 0.07782 | 0.027466 | 121.0648 | 120.9641 | -0.09613 | 120.9229 | 120.9641 | 0 | -0.009155 | 121.0419 | 120.9915 | -0.091552 | 120.9732 | 120.8679 | -0.1236 | -0.054931 | 120.9 | 120.9869 | 120.9961 | -0.032043 | 120.9045 | 120.9412 | 120.9824 | -0.004577
1264.7969 | 121.225 | -120.9412 | 0 | -0.13092 | -0.0031489 | -0.060312 | 0.025047 | -0.012328 | -0.0077203 | -0.0031253 | -0.084686 | 0.016641 | 0.029452 | 0.023199 | 0.011884 | 0.016857 | 0.07782 | 0.12817 | 0.16937 | 0.082397 | -0.086975 | 0.14191 | 0.022888 | 0.11444 | 0.19226 | 0.050354 | -0.082397 | -0.045776 | 0.086975 | 0.050354 | 121.0831 | 120.9641 | -0.086975 | 121.0693 | 121.0236 | 0.059509 | 0.07782 | 121.0281 | 120.9915 | -0.082397 | 121.0556 | 120.9915 | 0 | -0.045776 | 120.8542 | 121.019 | 121.1105 | 0.022888 | 120.8588 | 120.8954 | 121.1334 | 0.050354
1266.5625 | 121.1838 | -120.9778 | 0.018311 | -0.1004 | -0.0029351 | -0.061167 | 0.022697 | -0.010833 | -0.00067088 | -0.0029117 | -0.12283 | 0.018137 | 0.03052 | 0.023627 | 0.016584 | 0.018139 | 0.050354 | 0.004578 | 0.073242 | 0.045776 | -0.041199 | 0.09613 | 0 | 0.068665 | 0.07782 | -0.041199 | -0.041199 | -0.050354 | 0.086975 | 0.018311 | 121.0739 | 120.9778 | -0.05951 | 120.9824 | 121.0236 | 0.045776 | 0.032043 | 121.0648 | 120.9961 | -0.05951 | 121.0464 | 120.9366 | -0.05951 | -0.068665 | 120.9366 | 121.0281 | 121.051 | -0.018311 | 120.9366 | 120.9274 | 121.0556 | 0
1268.25 | 121.1609 | -121.0007 | 0.022888 | -0.062256 | -0.0012263 | -0.060099 | 0.025261 | -0.013824 | -0.0010981 | -0.0022707 | -0.084686 | 0.020914 | 0.032016 | 0.022986 | 0.015729 | 0.017925 | 0.050354 | 0.013733 | 0.073242 | 0.036621 | -0.050354 | 0.091553 | 0.013733 | 0.07782 | 0.082397 | -0.050354 | -0.050354 | -0.045776 | 0.086975 | 0.013733 | 121.0922 | 121.0144 | -0.073242 | 121.0144 | 121.0373 | 0.022888 | 0.027466 | 121.0876 | 121.0144 | -0.073242 | 121.0785 | 120.9503 | -0.064087 | -0.068664 | 120.9503 | 121.051 | 121.0739 | -0.009155 | 120.9503 | 120.9549 | 121.0831 | -0.009155
1270 | 121.1975 | -121.0327 | 0.027466 | 0.075073 | -0.0035761 | -0.062021 | 0.020561 | -0.012328 | -0.0043023 | 0.0011471 | 0.10605 | 0.020914 | 0.030948 | 0.022559 | 0.016156 | 0.018566 | 0 | -0.054932 | 0.004578 | 0 | -0.045776 | 0.082397 | -0.027466 | 0.013733 | -0.013733 | -0.11444 | -0.032043 | -0.004578 | 0.091553 | 0.013733 | 121.1151 | 121.0052 | -0.073242 | 120.9778 | 121.0327 | 0.027466 | -0.027466 | 121.1243 | 121.0464 | -0.059509 | 121.0464 | 120.9183 | -0.12817 | -0.032044 | 120.9869 | 121.0327 | 121.0373 | -0.054932 | 121.0007 | 121.0281 | 121.019 | -0.013733
1271.75 | 121.1838 | -121.0419 | 0.045776 | -0.054626 | 0.00026912 | -0.062662 | 0.022911 | -0.013824 | -0.0019525 | -0.0016299 | -0.054169 | 0.020059 | 0.031589 | 0.021918 | 0.017652 | 0.01643 | 0.054932 | 0.022888 | 0.082397 | 0.041199 | -0.059509 | 0.10071 | 0.004578 | 0.050354 | 0.086975 | -0.045776 | -0.054932 | -0.027466 | 0.068665 | 0.013733 | 121.1426 | 121.0464 | -0.10528 | 121.0648 | 121.0831 | 0.036621 | 0.009156 | 121.1105 | 121.0556 | -0.10071 | 121.0922 | 120.9961 | -0.059509 | -0.073242 | 120.9824 | 121.0968 | 121.1243 | -0.041198 | 120.9869 | 121.0144 | 121.1288 | -0.032043
1273.4375 | 121.2158 | -121.0419 | 0.018311 | -0.069885 | 0.0011237 | -0.062021 | 0.023338 | -0.01126 | -0.00088448 | -0.0016299 | -0.092316 | 0.0207 | 0.032016 | 0.027472 | 0.015729 | 0.018139 | 0.050354 | 0.013733 | 0.073242 | 0.041199 | -0.059509 | 0.10071 | -0.004578 | 0.050354 | 0.082397 | -0.027466 | -0.041199 | -0.027466 | 0.10529 | 0.009155 | 121.1426 | 121.0373 | -0.07782 | 121.0556 | 121.0831 | 0.045777 | 0.032043 | 121.1472 | 121.051 | -0.05951 | 121.0922 | 121.0144 | -0.036621 | -0.045777 | 120.9824 | 121.0922 | 121.1151 | -0.022889 | 121.0007 | 121.0144 | 121.1243 | -0.009156
1275.1094 | 121.257 | -121.0648 | 0.041199 | -0.14618 | -0.0022943 | -0.059244 | 0.02697 | -0.01361 | -0.0098565 | -0.0039797 | -0.092316 | 0.016 | 0.03287 | 0.024054 | 0.010602 | 0.018139 | 0.07782 | 0.082397 | 0.16479 | 0.086975 | -0.086975 | 0.13275 | 0.022888 | 0.086975 | 0.16479 | 0.032043 | -0.086975 | -0.050354 | 0.10986 | 0.050354 | 121.1975 | 121.0876 | -0.12817 | 121.1472 | 121.1517 | 0.064087 | 0.036621 | 121.1746 | 121.1151 | -0.12817 | 121.1517 | 121.0968 | -0.018311 | -0.091553 | 120.9778 | 121.1426 | 121.2296 | -0.018311 | 120.9778 | 121.0144 | 121.2296 | 0.009155
1276.7969 | 121.225 | -121.0876 | 0.027466 | -0.16907 | 0.00091012 | -0.060526 | 0.025475 | -0.011474 | -0.0060113 | -0.0044071 | -0.15335 | 0.01835 | 0.033298 | 0.023627 | 0.011884 | 0.01643 | 0 | -0.013733 | 0.045776 | 0.022888 | -0.064087 | 0.10071 | -0.013733 | 0.004578 | 0.032043 | -0.068665 | -0.027466 | -0.018311 | 0.07782 | 0.004578 | 121.1884 | 121.0739 | -0.091553 | 121.0739 | 121.1105 | 0.036621 | -0.027466 | 121.1655 | 121.0922 | -0.054932 | 121.0922 | 121.019 | -0.073243 | -0.045777 | 121.0236 | 121.0876 | 121.1334 | -0.041199 | 121.0602 | 121.0693 | 121.1197 | -0.022888
1278.4844 | 121.3257 | -121.0327 | 0.022888 | 0.075073 | -0.0057123 | -0.061167 | 0.022697 | -0.015319 | -0.0070795 | -0.0059023 | 0.09079 | 0.017923 | 0.03052 | 0.022772 | 0.012738 | 0.017925 | 0.036621 | 0.032043 | 0.10986 | 0.045776 | -0.073242 | 0.14191 | 0.032043 | 0.073242 | 0.07782 | -0.004578 | -0.054932 | -0.050354 | 0.10071 | 0.036621 | 121.1746 | 121.0648 | -0.09613 | 121.0648 | 121.0785 | 0.013733 | 0.013733 | 121.1334 | 121.0693 | -0.07782 | 121.106 | 121.0281 | -0.041199 | -0.073242 | 120.9595 | 121.0693 | 121.1426 | 0.009155 | 120.9778 | 120.9824 | 121.1105 | 0.013733
1280.1875 | 121.4081 | -121.0693 | 0.004578 | -0.0088499 | -0.0031489 | -0.060526 | 0.024406 | -0.01361 | -0.0064387 | -0.0029117 | -0.054169 | 0.017923 | 0.030734 | 0.022559 | 0.012952 | 0.018566 | 0.068665 | 0.054932 | 0.13275 | 0.064087 | -0.086975 | 0.13275 | 0.018311 | 0.1236 | 0.13733 | 0.041199 | -0.068665 | -0.032043 | 0.11444 | 0.036621 | 121.2021 | 121.0876 | -0.091553 | 121.1243 | 121.1334 | 0.045776 | 0.064087 | 121.1838 | 121.106 | -0.073243 | 121.1929 | 121.1105 | 0.004578 | -0.036621 | 120.9824 | 121.138 | 121.2021 | 0.013733 | 121.0007 | 121.0373 | 121.2067 | 0.032043
1281.8906 | 121.376 | -121.0693 | 0.009155 | -0.039368 | -0.0018671 | -0.060953 | 0.024193 | -0.01361 | -0.0055841 | -0.0056887 | -0.077057 | 0.017068 | 0.030948 | 0.024054 | 0.013166 | 0.016857 | 0.10986 | 0.10071 | 0.16937 | 0.082397 | -0.082397 | 0.13733 | 0.022888 | 0.16479 | 0.17395 | 0.064087 | -0.082397 | -0.073242 | 0.10986 | 0.036621 | 121.2067 | 121.0922 | -0.091552 | 121.17 | 121.1517 | 0.059509 | 0.10071 | 121.1792 | 121.106 | -0.091552 | 121.2341 | 121.1334 | 0.027466 | -0.082397 | 120.9869 | 121.1792 | 121.2387 | 0.013733 | 120.9869 | 120.9961 | 121.2433 | 0.027466
1283.5781 | 121.4218 | -121.0739 | 0.013733 | -0.0088499 | -0.0082757 | -0.060312 | 0.017571 | -0.012328 | -0.0064387 | -0.0065433 | -0.046539 | 0.016428 | 0.024539 | 0.023199 | 0.016584 | 0.017071 | 0.059509 | 0.045776 | 0.11902 | 0.059509 | -0.068665 | 0.11444 | 0.009155 | 0.1236 | 0.1236 | 0.027466 | -0.064087 | -0.050354 | 0.10986 | 0.059509 | 121.1884 | 121.0831 | -0.082398 | 121.1197 | 121.1334 | 0.050354 | 0.045776 | 121.1838 | 121.1334 | -0.07782 | 121.1975 | 121.1014 | -0.032043 | -0.064087 | 121.0052 | 121.1334 | 121.1929 | -0.004578 | 121.0098 | 121.0236 | 121.1975 | 0.045776
1285.3125 | 121.3257 | -121.1105 | 0.027466 | -0.15381 | -0.0022943 | -0.059458 | 0.025261 | -0.010833 | 0.0016791 | -0.0024845 | -0.20676 | 0.019418 | 0.031375 | 0.024695 | 0.015302 | 0.014721 | 0.022888 | -0.050354 | 0.009155 | 0.004578 | -0.041199 | 0.09613 | -0.022888 | 0.022888 | 0.041199 | -0.07782 | -0.018311 | -0.032043 | 0.064087 | 0.018311 | 121.2067 | 121.0876 | -0.068665 | 121.0602 | 121.1151 | 0.027466 | -0.004578 | 121.1746 | 121.1288 | -0.045777 | 121.1334 | 121.0327 | -0.096131 | -0.059509 | 121.0693 | 121.1334 | 121.1197 | -0.050354 | 121.0922 | 121.0785 | 121.1517 | -0.009155
1287.0156 | 121.4035 | -121.106 | 0.009155 | 0.097962 | -0.0025079 | -0.061167 | 0.019707 | -0.012328 | -0.0015253 | -0.0035525 | 0.08316 | 0.021127 | 0.02753 | 0.024268 | 0.017652 | 0.017284 | 0.032043 | -0.045776 | 0.022888 | 0.009155 | -0.032043 | 0.10071 | 0 | 0.059509 | 0.022888 | -0.068665 | -0.041199 | -0.032043 | 0.07782 | 0.027466 | 121.2067 | 121.106 | -0.041198 | 121.0602 | 121.1151 | 0.009155 | 0.022888 | 121.1838 | 121.1334 | -0.050354 | 121.1655 | 121.0373 | -0.096131 | -0.041198 | 121.0739 | 121.138 | 121.1288 | -0.009155 | 121.0648 | 121.0739 | 121.1288 | 0.018311
1288.7656 | 121.344 | -121.1563 | 0.032043 | -0.13855 | 0.00048272 | -0.060312 | 0.027184 | -0.012969 | -0.0017389 | -0.0046207 | -0.1915 | 0.020059 | 0.031802 | 0.023199 | 0.014447 | 0.01643 | 0.013733 | -0.036621 | 0.032043 | 0.018311 | -0.045776 | 0.091553 | 0.004578 | 0.050354 | 0.045776 | -0.091553 | -0.041199 | -0.018311 | 0.068665 | 0.009155 | 121.2479 | 121.1609 | -0.077819 | 121.1197 | 121.1746 | 0.013733 | -0.01831 | 121.225 | 121.1655 | -0.073242 | 121.2067 | 121.0648 | -0.10071 | -0.050354 | 121.1105 | 121.17 | 121.1884 | -0.027465 | 121.1151 | 121.138 | 121.2021 | -0.022888
1290.5156 | 121.3165 | -121.1792 | 0.041199 | -0.16144 | 0.0019781 | -0.062876 | 0.026543 | -0.012328 | -0.0028071 | -0.0041933 | -0.18387 | 0.020059 | 0.031589 | 0.023413 | 0.012738 | 0.018352 | -0.004578 | -0.032043 | 0.045776 | 0.004578 | -0.050354 | 0.09613 | -0.009155 | 0.018311 | 0.036621 | -0.091553 | -0.027466 | -0.018311 | 0.07782 | -0.013733 | 121.2753 | 121.17 | -0.091553 | 121.1472 | 121.1838 | 0.013733 | -0.045777 | 121.257 | 121.1655 | -0.068665 | 121.1975 | 121.0876 | -0.07782 | -0.05951 | 121.1288 | 121.1746 | 121.225 | -0.050354 | 121.1517 | 121.1609 | 121.2158 | -0.054932
1292.2188 | 121.4172 | -121.1517 | -0.004578 | 0.159 | -0.0040033 | -0.061594 | 0.018852 | -0.014464 | -0.0038751 | -0.0020571 | 0.18234 | 0.019418 | 0.029025 | 0.022131 | 0.017438 | 0.017071 | 0.10529 | 0.068665 | 0.15564 | 0.086975 | -0.07782 | 0.15564 | 0.045776 | 0.15564 | 0.12817 | 0.032043 | -0.073242 | -0.054932 | 0.13275 | 0.050354 | 121.3074 | 121.1975 | -0.073242 | 121.2204 | 121.2387 | 0.041199 | 0.10986 | 121.2845 | 121.2021 | -0.068664 | 121.3074 | 121.1838 | -0.018311 | -0.050354 | 121.0739 | 121.257 | 121.3074 | 0.050354 | 121.0785 | 121.0968 | 121.2799 | 0.054932
1293.9688 | 121.3577 | -121.17 | 0.041199 | 0.067444 | 0.00026912 | -0.063303 | 0.020134 | -0.014892 | 0.00061092 | -0.0016299 | 0.0068663 | 0.021127 | 0.030734 | 0.025336 | 0.01637 | 0.017284 | 0.004578 | -0.068665 | 0.013733 | -0.004578 | -0.032043 | 0.09613 | -0.009155 | -0.018311 | -0.009155 | -0.13275 | -0.022888 | -0.022888 | 0.07782 | -0.004578 | 121.2662 | 121.1609 | -0.073242 | 121.1014 | 121.1655 | 0.004577 | -0.036621 | 121.2479 | 121.1655 | -0.064087 | 121.1517 | 121.0373 | -0.12817 | -0.064087 | 121.138 | 121.1746 | 121.1838 | -0.050354 | 121.1472 | 121.1472 | 121.1609 | -0.045777
1295.6562 | 121.3623 | -121.2067 | 0.036621 | 0.044556 | -0.00037168 | -0.064371 | 0.023125 | -0.012755 | -0.0015253 | -0.0018435 | 0.0068663 | 0.021127 | 0.028598 | 0.025763 | 0.015302 | 0.016857 | -0.009155 | -0.082397 | 0.013733 | -0.004578 | -0.022888 | 0.10071 | 0.009155 | -0.009155 | -0.004578 | -0.12817 | -0.036621 | -0.004578 | 0.082397 | 0.009155 | 121.3074 | 121.2158 | -0.059509 | 121.1243 | 121.2021 | -0.013733 | -0.045776 | 121.2891 | 121.2158 | -0.073242 | 121.1975 | 121.0785 | -0.13733 | -0.041199 | 121.1838 | 121.1975 | 121.2204 | -0.027466 | 121.17 | 121.2021 | 121.2021 | -0.027466
1297.4062 | 121.3623 | -121.1975 | 0.054932 | -0.15381 | -0.0029351 | -0.060312 | 0.027611 | -0.010192 | -0.0062249 | -0.0024845 | -0.16098 | 0.017709 | 0.027102 | 0.022559 | 0.011884 | 0.018352 | 0.068665 | 0.064087 | 0.13733 | 0.086975 | -0.068665 | 0.10529 | 0.022888 | 0.082397 | 0.13275 | 0.004578 | -0.073242 | -0.036621 | 0.09613 | 0.032043 | 121.3028 | 121.2204 | -0.1236 | 121.2616 | 121.2845 | 0.064087 | 0.013733 | 121.2936 | 121.2296 | -0.12817 | 121.2799 | 121.2021 | -0.027465 | -0.091553 | 121.1288 | 121.2662 | 121.3348 | -0.032044 | 121.1243 | 121.1609 | 121.3303 | -0.022889
1299.1719 | 121.4996 | -121.1655 | 0.009155 | -0.039368 | -0.0040033 | -0.061594 | 0.021843 | -0.011046 | -0.0087885 | -0.0035525 | -0.03891 | 0.015787 | 0.029452 | 0.025549 | 0.012097 | 0.017712 | 0.064087 | 0.073242 | 0.12817 | 0.086975 | -0.073242 | 0.1236 | 0.036621 | 0.13275 | 0.15564 | 0.059509 | -0.068665 | -0.064087 | 0.1236 | 0.050354 | 121.2891 | 121.2021 | -0.082397 | 121.2387 | 121.2524 | 0.050354 | 0.054932 | 121.2891 | 121.2158 | -0.07782 | 121.2982 | 121.225 | 0.009155 | -0.073242 | 121.0922 | 121.2296 | 121.2936 | 0.027466 | 121.0968 | 121.1014 | 121.3211 | 0.041199
1300.9219 | 121.5088 | -121.1975 | 0 | 0.159 | -0.0035761 | -0.062448 | 0.021202 | -0.012115 | -0.0023797 | -0.0035525 | 0.09079 | 0.019205 | 0.026462 | 0.022986 | 0.01872 | 0.013866 | 0.09613 | 0.018311 | 0.11902 | 0.068665 | -0.068665 | 0.10986 | 0.032043 | 0.12817 | 0.1236 | 0.018311 | -0.082397 | -0.050354 | 0.12817 | 0.073242 | 121.3074 | 121.2296 | -0.068665 | 121.2158 | 121.2662 | 0.036622 | 0.09613 | 121.3257 | 121.2708 | -0.082397 | 121.3257 | 121.2158 | -0.054931 | -0.050354 | 121.1288 | 121.2936 | 121.3165 | 0.032043 | 121.1151 | 121.1472 | 121.3211 | 0.073242
1302.625 | 121.4722 | -121.2021 | 0.013733 | 0.159 | -0.0042169 | -0.064157 | 0.023125 | -0.015319 | -0.0043023 | -0.0037661 | 0.15945 | 0.019205 | 0.029239 | 0.02085 | 0.014661 | 0.016857 | 0.11902 | 0.068665 | 0.15106 | 0.086975 | -0.09613 | 0.13733 | 0.054932 | 0.15106 | 0.13733 | 0.027466 | -0.09613 | -0.068665 | 0.11444 | 0.036621 | 121.3394 | 121.257 | -0.10986 | 121.2708 | 121.2891 | 0.032043 | 0.10529 | 121.3165 | 121.2387 | -0.10986 | 121.3531 | 121.2296 | -0.009155 | -0.082398 | 121.106 | 121.3211 | 121.3531 | 0.041199 | 121.106 | 121.1334 | 121.3394 | 0.022888
1304.375 | 121.5271 | -121.2158 | 0.004578 | -0.11566 | -0.0040033 | -0.06074 | 0.023766 | -0.014037 | -0.0060113 | -0.0054751 | -0.054169 | 0.017068 | 0.030734 | 0.02149 | 0.013379 | 0.017071 | 0.10529 | 0.086975 | 0.16937 | 0.086975 | -0.073242 | 0.1236 | 0.036621 | 0.15106 | 0.17395 | 0.059509 | -0.086975 | -0.068665 | 0.10986 | 0.050354 | 121.3394 | 121.2524 | -0.07782 | 121.3028 | 121.3028 | 0.050354 | 0.10071 | 121.3257 | 121.2662 | -0.091553 | 121.3669 | 121.2753 | 0.009155 | -0.073243 | 121.1426 | 121.3211 | 121.3852 | 0.032043 | 121.1288 | 121.1472 | 121.3898 | 0.045776
1306.1406 | 121.5454 | -121.2158 | 0.018311 | 0.029297 | -0.0029351 | -0.060953 | 0.024834 | -0.010833 | -0.0053705 | -0.0059023 | 0.037384 | 0.019418 | 0.032016 | 0.023627 | 0.012525 | 0.017071 | 0.045776 | 0.027466 | 0.10529 | 0.054932 | -0.07782 | 0.11444 | 0.018311 | 0.086975 | 0.082397 | -0.018311 | -0.068665 | -0.059509 | 0.10071 | 0.013733 | 121.3303 | 121.2341 | -0.096131 | 121.2433 | 121.2708 | 0.036621 | 0.027465 | 121.3165 | 121.2296 | -0.086976 | 121.3028 | 121.1975 | -0.032044 | -0.07782 | 121.138 | 121.2616 | 121.3211 | 0 | 121.1472 | 121.1563 | 121.2982 | -0.004578
1307.8281 | 121.5134 | -121.2204 | 0.018311 | 0.13611 | -0.0029351 | -0.06138 | 0.020561 | -0.012328 | 0.00018372 | -0.0035525 | 0.029755 | 0.020486 | 0.029239 | 0.025977 | 0.017865 | 0.016216 | 0.022888 | -0.068665 | 0.009155 | -0.009155 | -0.041199 | 0.091553 | 0 | 0.050354 | -0.004578 | -0.091553 | -0.032043 | -0.009155 | 0.07782 | 0.004578 | 121.312 | 121.2204 | -0.05951 | 121.1517 | 121.2112 | -0.009155 | 0.004577 | 121.2982 | 121.225 | -0.050354 | 121.2708 | 121.1288 | -0.096131 | -0.027466 | 121.1792 | 121.2433 | 121.2296 | -0.018311 | 121.1884 | 121.2112 | 121.2158 | -0.013733
1309.5625 | 121.5225 | -121.257 | 0.018311 | 0.052185 | -0.0046441 | -0.061594 | 0.022911 | -0.015105 | -0.0064387 | -0.0048343 | 0.060272 | 0.016641 | 0.031375 | 0.022986 | 0.014661 | 0.017925 | 0.045776 | 0.018311 | 0.10986 | 0.045776 | -0.09613 | 0.1236 | 0.022888 | 0.082397 | 0.082397 | -0.022888 | -0.073242 | -0.041199 | 0.11444 | 0.018311 | 121.3806 | 121.2799 | -0.11444 | 121.2753 | 121.3028 | 0.022888 | 0.027465 | 121.3715 | 121.2753 | -0.091553 | 121.3394 | 121.2341 | -0.041199 | -0.05951 | 121.1609 | 121.3028 | 121.3669 | 0.004577 | 121.1838 | 121.2158 | 121.3394 | 0
1311.3281 | 121.5637 | -121.2479 | 0.004578 | 0.021668 | -0.0025079 | -0.061808 | 0.025475 | -0.010833 | -0.0047297 | -0.0048343 | 0.022125 | 0.022623 | 0.029666 | 0.022772 | 0.012952 | 0.01643 | 0.036621 | 0.009155 | 0.091553 | 0.045776 | -0.073242 | 0.11444 | 0.013733 | 0.086975 | 0.086975 | -0.013733 | -0.068665 | -0.050354 | 0.09613 | 0.032043 | 121.3623 | 121.2616 | -0.07782 | 121.257 | 121.2936 | 0.032043 | 0.032043 | 121.344 | 121.2799 | -0.073243 | 121.3348 | 121.2341 | -0.045776 | -0.054932 | 121.1746 | 121.2845 | 121.3394 | 0.009155 | 121.1792 | 121.1975 | 121.3348 | 0.027465
1313.0781 | 121.5683 | -121.2387 | -0.004578 | 0.10559 | -0.0029351 | -0.064371 | 0.017571 | -0.014464 | -0.00024348 | -0.0048343 | 0.098419 | 0.021982 | 0.027957 | 0.025122 | 0.015302 | 0.017925 | 0.041199 | -0.041199 | 0.041199 | 0 | -0.032043 | 0.10986 | 0.004578 | 0.086975 | 0.036621 | -0.059509 | -0.059509 | -0.041199 | 0.086975 | 0.022888 | 121.3486 | 121.2433 | -0.027465 | 121.1975 | 121.2387 | -0.004578 | 0.045777 | 121.3257 | 121.2616 | -0.054931 | 121.3257 | 121.1792 | -0.082397 | -0.036621 | 121.2067 | 121.2799 | 121.2799 | 0.009156 | 121.1792 | 121.1975 | 121.2753 | 0.027466
1314.7656 | 121.5637 | -121.2891 | -0.009155 | 0.12085 | -0.0033625 | -0.061167 | 0.019493 | -0.014251 | -0.0019525 | -0.0044071 | 0.12894 | 0.020273 | 0.026889 | 0.021704 | 0.01872 | 0.016857 | 0.027466 | -0.032043 | 0.018311 | 0.018311 | -0.050354 | 0.086975 | -0.013733 | 0.082397 | 0.036621 | -0.064087 | -0.050354 | -0.036621 | 0.091553 | 0.013733 | 121.376 | 121.2753 | -0.041199 | 121.257 | 121.3074 | 0.032044 | 0.036621 | 121.3806 | 121.3028 | -0.041199 | 121.3715 | 121.225 | -0.07782 | -0.027466 | 121.2387 | 121.3165 | 121.3074 | -0.004578 | 121.2387 | 121.2524 | 121.3257 | 0.022888
1316.5156 | 121.5591 | -121.2845 | 0.018311 | 0.18188 | -0.0057123 | -0.062876 | 0.021629 | -0.0086966 | -0.0036615 | -0.0039797 | 0.1442 | 0.018564 | 0.02753 | 0.022986 | 0.015302 | 0.018352 | 0.10529 | 0.068665 | 0.15564 | 0.07782 | -0.086975 | 0.13733 | 0.045776 | 0.13733 | 0.11902 | 0.045776 | -0.082397 | -0.064087 | 0.10529 | 0.041199 | 121.4218 | 121.3303 | -0.10529 | 121.3531 | 121.3623 | 0.032044 | 0.086975 | 121.3898 | 121.3257 | -0.10071 | 121.4218 | 121.3303 | 0.004577 | -0.082398 | 121.1975 | 121.3898 | 121.4401 | 0.027465 | 121.2021 | 121.2204 | 121.4035 | 0.022888
1318.2656 | 121.5408 | -121.3257 | 0.018311 | -0.1767 | -0.0029351 | -0.062448 | 0.030174 | -0.011474 | -0.0053705 | -0.0048343 | -0.099945 | 0.019632 | 0.028598 | 0.022345 | 0.013593 | 0.017498 | 0.10986 | 0.09613 | 0.16937 | 0.082397 | -0.086975 | 0.1236 | 0.004578 | 0.1236 | 0.16937 | 0.032043 | -0.082397 | -0.059509 | 0.10071 | 0.045776 | 121.4493 | 121.3303 | -0.10529 | 121.4218 | 121.4081 | 0.077819 | 0.091552 | 121.4264 | 121.3715 | -0.10071 | 121.4493 | 121.3577 | -0.013733 | -0.07782 | 121.2387 | 121.4355 | 121.4951 | -0.013733 | 121.2433 | 121.2662 | 121.4951 | 0.027465
1320.0156 | 121.4767 | -121.3577 | 0.045776 | -0.19196 | -0.0027215 | -0.060953 | 0.024834 | -0.012542 | -0.0010981 | -0.0046207 | -0.1915 | 0.018991 | 0.029239 | 0.022131 | 0.011884 | 0.015362 | 0.036621 | 0.036621 | 0.082397 | 0.036621 | -0.064087 | 0.086975 | -0.004578 | 0.027466 | 0.054932 | -0.059509 | -0.050354 | -0.027466 | 0.073242 | 0.022888 | 121.4447 | 121.3531 | -0.10986 | 121.3943 | 121.3943 | 0.041199 | -0.009155 | 121.431 | 121.3806 | -0.09613 | 121.3852 | 121.2982 | -0.082397 | -0.073242 | 121.2936 | 121.3943 | 121.4401 | -0.050354 | 121.3074 | 121.3303 | 121.4127 | -0.022888
1321.7188 | 121.5225 | -121.3257 | 0.009155 | -0.069885 | -0.00058528 | -0.063303 | 0.020988 | -0.012755 | -2.988e-05 | -0.0016299 | -0.14572 | 0.0207 | 0.027316 | 0.024481 | 0.01637 | 0.016857 | 0.050354 | 0.018311 | 0.082397 | 0.041199 | -0.064087 | 0.11444 | -0.004578 | 0.082397 | 0.073242 | -0.045776 | -0.050354 | -0.041199 | 0.082397 | 0.013733 | 121.4401 | 121.3211 | -0.073242 | 121.344 | 121.3669 | 0.045777 | 0.041199 | 121.4081 | 121.3394 | -0.059509 | 121.4081 | 121.2799 | -0.059509 | -0.050354 | 121.2616 | 121.376 | 121.4081 | -0.013733 | 121.2753 | 121.2845 | 121.3989 | 0.004578
1323.4844 | 121.6049 | -121.344 | 0.018311 | -0.13855 | -0.0044305 | -0.060312 | 0.024834 | -0.0076284 | -0.0062249 | -0.0026981 | -0.12283 | 0.018991 | 0.028811 | 0.022559 | 0.013379 | 0.018139 | 0.086975 | 0.1236 | 0.17395 | 0.086975 | -0.082397 | 0.12817 | 0.027466 | 0.14648 | 0.17853 | 0.054932 | -0.07782 | -0.07782 | 0.10529 | 0.045776 | 121.4722 | 121.3715 | -0.10071 | 121.4676 | 121.431 | 0.059509 | 0.068664 | 121.4493 | 121.3898 | -0.096131 | 121.4905 | 121.3989 | 0.009156 | -0.096131 | 121.2616 | 121.431 | 121.5179 | 0.009155 | 121.2662 | 121.2662 | 121.5225 | 0.027465
1325.1719 | 121.6232 | -121.344 | 0 | 0.10559 | -0.0031489 | -0.06074 | 0.018852 | -0.011474 | -0.0023797 | -0.0012027 | 0.052643 | 0.023904 | 0.026462 | 0.024481 | 0.016797 | 0.017071 | 0.009155 | -0.032043 | 0.027466 | 0 | -0.050354 | 0.091553 | -0.009155 | 0.045776 | 0.013733 | -0.07782 | -0.064087 | -0.032043 | 0.073242 | 0.022888 | 121.4355 | 121.3348 | -0.050354 | 121.312 | 121.344 | 0.009155 | 0.009155 | 121.4172 | 121.3669 | -0.064087 | 121.3898 | 121.2662 | -0.10071 | -0.032043 | 121.2936 | 121.3531 | 121.3715 | -0.009155 | 121.2799 | 121.312 | 121.3577 | 0.022888
1326.9375 | 121.5958 | -121.3531 | 0.009155 | 0.12848 | -0.0044305 | -0.061594 | 0.020775 | -0.010619 | -0.0075067 | -0.0033389 | 0.10605 | 0.021127 | 0.026034 | 0.022131 | 0.014661 | 0.018566 | 0.07782 | 0.068665 | 0.12817 | 0.059509 | -0.091553 | 0.13275 | 0.032043 | 0.10071 | 0.091553 | 0.013733 | -0.073242 | -0.068665 | 0.1236 | 0.050354 | 121.4859 | 121.3852 | -0.10071 | 121.4218 | 121.4127 | 0.027466 | 0.068665 | 121.4767 | 121.4035 | -0.082397 | 121.4539 | 121.3669 | -0.036621 | -0.07782 | 121.2616 | 121.431 | 121.4813 | 0.022888 | 121.2799 | 121.2845 | 121.4447 | 0.041199
1328.6875 | 121.5363 | -121.3989 | 0.045776 | -0.16907 | -0.0016535 | -0.060526 | 0.024834 | -0.011474 | -0.0021661 | -0.0024845 | -0.22964 | 0.0254 | 0.026462 | 0.024908 | 0.015302 | 0.016216 | 0.004578 | -0.036621 | 0.027466 | 0.004578 | -0.045776 | 0.082397 | 0 | 0.018311 | 0.022888 | -0.091553 | -0.036621 | -0.032043 | 0.07782 | 0.013733 | 121.4813 | 121.3989 | -0.091552 | 121.3623 | 121.4035 | 0.004578 | -0.041198 | 121.4767 | 121.4127 | -0.082397 | 121.4172 | 121.3074 | -0.10529 | -0.077819 | 121.3531 | 121.4035 | 121.4264 | -0.045776 | 121.3623 | 121.3669 | 121.4218 | -0.032043
1330.375 | 121.6507 | -121.3623 | 0.018311 | -0.10803 | -0.0027215 | -0.060526 | 0.023766 | -0.011901 | -0.0068659 | -0.0067569 | -0.12283 | 0.020059 | 0.026248 | 0.022986 | 0.01167 | 0.014934 | 0.10529 | 0.10986 | 0.16479 | 0.091553 | -0.073242 | 0.11902 | 0.018311 | 0.13733 | 0.18768 | 0.054932 | -0.07782 | -0.045776 | 0.10986 | 0.036621 | 121.4813 | 121.3806 | -0.091553 | 121.4722 | 121.4539 | 0.073242 | 0.086975 | 121.4722 | 121.3989 | -0.096131 | 121.4996 | 121.4172 | 0.018311 | -0.064087 | 121.2891 | 121.4676 | 121.5271 | 0 | 121.2845 | 121.3165 | 121.55 | 0.01831
1332.125 | 121.5454 | -121.4172 | 0.041199 | -0.19196 | -0.0018671 | -0.059458 | 0.022057 | -0.01361 | -0.0040887 | -0.0052615 | -0.17624 | 0.02305 | 0.026034 | 0.022772 | 0.01402 | 0.014934 | 0.07782 | 0.073242 | 0.11444 | 0.059509 | -0.073242 | 0.11444 | 0.013733 | 0.068665 | 0.09613 | -0.036621 | -0.064087 | -0.041199 | 0.082397 | 0.018311 | 121.5317 | 121.431 | -0.11444 | 121.4905 | 121.4767 | 0.045776 | 0.036621 | 121.4996 | 121.4355 | -0.10529 | 121.4859 | 121.3806 | -0.054932 | -0.082398 | 121.344 | 121.4951 | 121.5317 | -0.027466 | 121.3531 | 121.376 | 121.5134 | -0.022888
1333.875 | 121.6599 | -121.376 | 0.004578 | 0.12848 | -0.0037897 | -0.060526 | 0.01992 | -0.013396 | 0.0010381 | -0.0035525 | 0.037384 | 0.023691 | 0.024753 | 0.022772 | 0.017438 | 0.015148 | 0.018311 | -0.050354 | 0.032043 | -0.004578 | -0.036621 | 0.10986 | -0.009155 | 0.050354 | 0.009155 | -0.07782 | -0.050354 | -0.022888 | 0.07782 | 0 | 121.4859 | 121.3669 | -0.041199 | 121.3257 | 121.3715 | 0.004577 | 0.013733 | 121.4539 | 121.376 | -0.054932 | 121.4264 | 121.2982 | -0.07782 | -0.027466 | 121.3394 | 121.3943 | 121.4081 | -0.013733 | 121.3257 | 121.3531 | 121.3852 | -0.004578
1335.5625 | 121.5729 | -121.4264 | 0.036621 | 0.067444 | -0.0029351 | -0.059031 | 0.021416 | -0.014678 | 0.0016791 | -0.0016299 | -0.0083922 | 0.026041 | 0.024966 | 0.022986 | 0.018079 | 0.01643 | 0.009155 | -0.07782 | -0.004578 | 0.009155 | -0.054932 | 0.10986 | -0.004578 | -0.009155 | -0.018311 | -0.13275 | -0.036621 | -0.022888 | 0.07782 | -0.004578 | 121.5363 | 121.4218 | -0.091553 | 121.3486 | 121.4355 | 0.013733 | -0.027466 | 121.5042 | 121.4218 | -0.073242 | 121.4172 | 121.2936 | -0.12817 | -0.059509 | 121.3715 | 121.4355 | 121.4218 | -0.041199 | 121.3898 | 121.4035 | 121.4081 | -0.041199
1337.3125 | 121.6141 | -121.4172 | 0.036621 | -0.13855 | 0.00091012 | -0.060526 | 0.025475 | -0.011474 | -0.0015253 | -0.0026981 | -0.13809 | 0.023904 | 0.026248 | 0.023413 | 0.01402 | 0.017284 | 0.041199 | -0.013733 | 0.041199 | 0.045776 | -0.045776 | 0.091553 | 0.004578 | 0.045776 | 0.082397 | -0.059509 | -0.050354 | -0.032043 | 0.086975 | 0.013733 | 121.5088 | 121.4218 | -0.082397 | 121.4035 | 121.463 | 0.041198 | 0.004578 | 121.5042 | 121.431 | -0.086975 | 121.463 | 121.3577 | -0.073242 | -0.068664 | 121.3715 | 121.4584 | 121.4584 | -0.032043 | 121.3669 | 121.3852 | 121.4996 | -0.022888
1339.0625 | 121.6599 | -121.4172 | 0.013733 | 0.052185 | -0.0040033 | -0.059885 | 0.020775 | -0.01361 | -0.0087885 | -0.0039797 | 0.098419 | 0.0254 | 0.024112 | 0.022131 | 0.011457 | 0.019634 | 0.050354 | 0.032043 | 0.10986 | 0.041199 | -0.07782 | 0.13733 | 0.018311 | 0.086975 | 0.086975 | 0 | -0.082397 | -0.050354 | 0.11902 | 0.032043 | 121.5546 | 121.4355 | -0.091553 | 121.4493 | 121.4584 | 0.022888 | 0.036621 | 121.5363 | 121.4493 | -0.09613 | 121.5042 | 121.4172 | -0.032043 | -0.064087 | 121.3394 | 121.4676 | 121.5271 | 0.004578 | 121.3348 | 121.3669 | 121.5042 | 0.01831
1340.8125 | 121.6187 | -121.431 | 0.032043 | -0.13855 | -0.0012263 | -0.058176 | 0.020775 | -0.012542 | -0.00045708 | -0.0039797 | -0.1915 | 0.025186 | 0.026462 | 0.024268 | 0.014234 | 0.016857 | 0.022888 | -0.045776 | 0.022888 | 0.013733 | -0.054932 | 0.091553 | -0.013733 | 0.013733 | 0.045776 | -0.059509 | -0.045776 | -0.050354 | 0.082397 | 0.004578 | 121.5225 | 121.4172 | -0.086975 | 121.3852 | 121.4447 | 0.027466 | -0.009155 | 121.5134 | 121.4355 | -0.077819 | 121.4447 | 121.3715 | -0.064087 | -0.082397 | 121.376 | 121.4539 | 121.4539 | -0.045776 | 121.3852 | 121.3806 | 121.4767 | -0.027465
1342.5625 | 121.637 | -121.4355 | 0.022888 | -0.13092 | -0.00037168 | -0.060953 | 0.021843 | -0.013396 | -0.0013117 | -0.0046207 | -0.10757 | 0.022409 | 0.026889 | 0.027045 | 0.014447 | 0.015789 | 0.054932 | -0.013733 | 0.045776 | 0.045776 | -0.045776 | 0.086975 | -0.022888 | 0.045776 | 0.091553 | -0.041199 | -0.059509 | -0.045776 | 0.082397 | 0.022888 | 121.5225 | 121.4127 | -0.068664 | 121.4218 | 121.4813 | 0.068664 | 0.032044 | 121.5179 | 121.4584 | -0.082397 | 121.4813 | 121.3943 | -0.064087 | -0.068664 | 121.3898 | 121.4905 | 121.4813 | -0.045776 | 121.376 | 121.3898 | 121.5271 | 0
1344.3125 | 121.6415 | -121.4493 | 0.022888 | -0.13092 | -0.0027215 | -0.060953 | 0.021629 | -0.010833 | -0.0023797 | -0.00077552 | -0.1152 | 0.023477 | 0.026675 | 0.024054 | 0.013379 | 0.017071 | 0.027466 | -0.018311 | 0.045776 | 0.041199 | -0.036621 | 0.10071 | -0.009155 | 0.041199 | 0.07782 | -0.036621 | -0.045776 | -0.036621 | 0.082397 | 0.018311 | 121.55 | 121.4401 | -0.059509 | 121.431 | 121.4905 | 0.050354 | 0.004578 | 121.5317 | 121.4676 | -0.068664 | 121.4905 | 121.4127 | -0.054932 | -0.059509 | 121.4127 | 121.4767 | 121.4951 | -0.032043 | 121.4035 | 121.4127 | 121.5271 | -0.004577
1346 | 121.7285 | -121.4355 | 0.022888 | -0.1004 | -0.0050715 | -0.06074 | 0.025047 | -0.013183 | -0.011138 | -0.0044071 | -0.016022 | 0.022195 | 0.024966 | 0.022986 | 0.012738 | 0.018139 | 0.082397 | 0.11444 | 0.16937 | 0.09613 | -0.082397 | 0.15564 | 0.018311 | 0.14648 | 0.18768 | 0.082397 | -0.091553 | -0.082397 | 0.11444 | 0.045776 | 121.5912 | 121.4539 | -0.10528 | 121.55 | 121.5317 | 0.077819 | 0.059509 | 121.55 | 121.4813 | -0.11444 | 121.582 | 121.5179 | 0.036621 | -0.10528 | 121.3531 | 121.5179 | 121.6049 | -0.004577 | 121.344 | 121.3531 | 121.6232 | 0.022888
1347.75 | 121.701 | -121.463 | 0.013733 | 0.036926 | -0.0087031 | -0.059458 | 0.021629 | -0.012115 | -0.0060113 | -0.0041933 | 0.067902 | 0.021982 | 0.026034 | 0.022986 | 0.013806 | 0.018139 | 0.045776 | 0.022888 | 0.10529 | 0.045776 | -0.068665 | 0.12817 | 0.018311 | 0.07782 | 0.086975 | -0.013733 | -0.068665 | -0.045776 | 0.10071 | 0.036621 | 121.5912 | 121.4813 | -0.082398 | 121.4859 | 121.5088 | 0.027465 | 0.032043 | 121.5637 | 121.4996 | -0.082398 | 121.5408 | 121.4493 | -0.050354 | -0.059509 | 121.3943 | 121.5088 | 121.5683 | 0.004578 | 121.3943 | 121.4172 | 121.55 | 0.022888
1349.4375 | 121.6232 | -121.4676 | 0.041199 | 0.067444 | -0.0020807 | -0.06138 | 0.016716 | -0.011901 | 0.00018372 | -0.0037661 | 0.037384 | 0.024332 | 0.024753 | 0.025549 | 0.019361 | 0.01643 | 0.018311 | -0.064087 | 0.004578 | 0.004578 | -0.050354 | 0.091553 | -0.009155 | 0.009155 | 0.004578 | -0.11444 | -0.045776 | -0.041199 | 0.059509 | 0.009155 | 121.5591 | 121.4584 | -0.091553 | 121.4035 | 121.4722 | 0.013733 | -0.022888 | 121.5271 | 121.4767 | -0.086975 | 121.4767 | 121.3531 | -0.1236 | -0.082398 | 121.4172 | 121.4859 | 121.4722 | -0.050354 | 121.4218 | 121.4264 | 121.4722 | -0.032044
1351.2031 | 121.6415 | -121.5042 | 0.045776 | -0.12329 | -0.0022943 | -0.060526 | 0.025475 | -0.010833 | -0.0057977 | -0.0044071 | -0.16861 | 0.021341 | 0.026889 | 0.021277 | 0.013379 | 0.015148 | 0.068665 | 0.086975 | 0.11444 | 0.073242 | -0.086975 | 0.10986 | 0.018311 | 0.064087 | 0.1236 | 0.004578 | -0.054932 | -0.036621 | 0.09613 | 0.018311 | 121.6141 | 121.5225 | -0.13275 | 121.5912 | 121.5775 | 0.054931 | 0.022889 | 121.6003 | 121.5225 | -0.10071 | 121.5683 | 121.5088 | -0.013733 | -0.082397 | 121.4172 | 121.5729 | 121.6187 | -0.027465 | 121.4493 | 121.4676 | 121.6278 | -0.027465
1352.9688 | 121.6965 | -121.4722 | 0.013733 | 0.13611 | -0.0052851 | -0.063303 | 0.017357 | -0.01126 | -0.0015253 | -0.0044071 | 0.060272 | 0.022836 | 0.024966 | 0.024268 | 0.01872 | 0.015148 | 0.018311 | -0.07782 | 0.009155 | -0.009155 | -0.036621 | 0.086975 | 0.009155 | 0.022888 | -0.004578 | -0.10071 | -0.041199 | -0.032043 | 0.086975 | 0.013733 | 121.5591 | 121.4813 | -0.050354 | 121.3943 | 121.463 | -0.01831 | 0.004578 | 121.5591 | 121.4859 | -0.054932 | 121.4951 | 121.3715 | -0.11444 | -0.045776 | 121.4355 | 121.4905 | 121.4813 | -0.004578 | 121.431 | 121.4401 | 121.4676 | 0
1354.7188 | 121.6461 | -121.5134 | 0.032043 | -0.092773 | -0.0040033 | -0.06074 | 0.025047 | -0.011687 | -0.0047297 | -0.0039797 | -0.19913 | 0.022623 | 0.026675 | 0.024908 | 0.012311 | 0.016216 | 0.004578 | -0.036621 | 0.036621 | 0 | -0.036621 | 0.091553 | -0.009155 | 0 | 0.032043 | -0.07782 | -0.022888 | -0.018311 | 0.068665 | 0.013733 | 121.6049 | 121.5042 | -0.068664 | 121.4767 | 121.5134 | 0.009155 | -0.027465 | 121.582 | 121.5271 | -0.054931 | 121.5134 | 121.4355 | -0.091553 | -0.050354 | 121.4767 | 121.5179 | 121.55 | -0.041198 | 121.4905 | 121.4951 | 121.5454 | -0.01831
1356.4062 | 121.6507 | -121.5454 | 0.022888 | -0.19958 | -0.0035761 | -0.06138 | 0.022697 | -0.01126 | -0.0049433 | -0.0059023 | -0.16861 | 0.022836 | 0.026462 | 0.022131 | 0.013806 | 0.017925 | 0.059509 | 0.054932 | 0.10071 | 0.045776 | -0.064087 | 0.10529 | -0.009155 | 0.041199 | 0.086975 | -0.022888 | -0.064087 | -0.032043 | 0.086975 | 0.009155 | 121.6507 | 121.5363 | -0.086975 | 121.6003 | 121.5912 | 0.054931 | 0.036621 | 121.6324 | 121.5546 | -0.086975 | 121.5866 | 121.5225 | -0.032043 | -0.054931 | 121.4813 | 121.6049 | 121.6461 | -0.032043 | 121.4813 | 121.5134 | 121.6324 | -0.013733
1358.1562 | 121.6599 | -121.5637 | 0.032043 | -0.19958 | -0.0031489 | -0.059671 | 0.02227 | -0.012115 | -0.0072931 | -0.0046207 | -0.10757 | 0.025827 | 0.026462 | 0.024268 | 0.01402 | 0.017712 | 0.050354 | -0.004578 | 0.086975 | 0.045776 | -0.059509 | 0.11902 | -0.004578 | 0.027466 | 0.045776 | -0.054932 | -0.045776 | -0.018311 | 0.07782 | 0 | 121.6827 | 121.5591 | -0.091552 | 121.5591 | 121.6095 | 0.050354 | 0.018311 | 121.6415 | 121.5637 | -0.077819 | 121.5912 | 121.5088 | -0.054932 | -0.050354 | 121.5042 | 121.6141 | 121.6507 | -0.036621 | 121.5179 | 121.5454 | 121.6095 | -0.032043
1359.8438 | 121.7926 | -121.4951 | 0 | 0.159 | -0.0029351 | -0.059885 | 0.018852 | -0.0082694 | -0.0017389 | -0.0052615 | 0.12894 | 0.024973 | 0.025821 | 0.023413 | 0.01637 | 0.018352 | 0.068665 | -0.013733 | 0.050354 | 0.013733 | -0.064087 | 0.11902 | 0.004578 | 0.10071 | 0.07782 | -0.004578 | -0.082397 | -0.054932 | 0.11444 | 0.022888 | 121.6141 | 121.4996 | -0.064087 | 121.4813 | 121.5088 | 0.009155 | 0.068665 | 121.6095 | 121.5179 | -0.082397 | 121.5958 | 121.4905 | -0.027466 | -0.054932 | 121.431 | 121.5637 | 121.5454 | 0.004578 | 121.4127 | 121.4401 | 121.5729 | 0.022888
1361.5938 | 121.7194 | -121.55 | 0.032043 | -0.14618 | 0.0013373 | -0.060526 | 0.022911 | -0.013183 | -0.0015253 | -0.0022707 | -0.1915 | 0.025827 | 0.024753 | 0.024695 | 0.016156 | 0.01643 | 0.004578 | -0.032043 | 0.054932 | 0.032043 | -0.032043 | 0.086975 | -0.004578 | 0.050354 | 0.050354 | -0.059509 | -0.054932 | -0.036621 | 0.086975 | 0 | 121.637 | 121.5454 | -0.064086 | 121.5179 | 121.582 | 0.036621 | -0.027465 | 121.637 | 121.55 | -0.086975 | 121.6003 | 121.4905 | -0.059509 | -0.068664 | 121.5179 | 121.5546 | 121.6049 | -0.036621 | 121.4951 | 121.5134 | 121.6003 | -0.032043
1363.3438 | 121.7377 | -121.5271 | 0.032043 | -0.13092 | -0.00037168 | -0.062235 | 0.025475 | -0.012755 | -0.0021661 | -0.0024845 | -0.12283 | 0.025827 | 0.024966 | 0.023413 | 0.017865 | 0.017284 | 0.036621 | -0.022888 | 0.054932 | 0.045776 | -0.054932 | 0.086975 | -0.013733 | 0.041199 | 0.073242 | -0.059509 | -0.036621 | -0.018311 | 0.082397 | 0.009155 | 121.6141 | 121.5134 | -0.086975 | 121.5042 | 121.5729 | 0.059509 | 0.004578 | 121.6095 | 121.5363 | -0.068664 | 121.5683 | 121.4676 | -0.068664 | -0.050354 | 121.4722 | 121.5637 | 121.582 | -0.045776 | 121.4905 | 121.5088 | 121.6003 | -0.022888
1365.0312 | 121.7422 | -121.5408 | 0.027466 | -0.1767 | -0.0027215 | -0.062021 | 0.026756 | -0.012328 | -0.0021661 | -0.0039797 | -0.15335 | 0.025186 | 0.027316 | 0.024908 | 0.013166 | 0.018139 | 0.004578 | -0.054932 | 0.009155 | 0.009155 | -0.036621 | 0.10071 | -0.013733 | 0.009155 | 0.032043 | -0.082397 | -0.041199 | -0.027466 | 0.064087 | 0.004578 | 121.6415 | 121.5271 | -0.064087 | 121.4859 | 121.55 | 0.022888 | -0.022888 | 121.6049 | 121.5454 | -0.068665 | 121.55 | 121.4584 | -0.086975 | -0.054932 | 121.5042 | 121.5454 | 121.55 | -0.041199 | 121.4996 | 121.5134 | 121.5729 | -0.022888
1366.7812 | 121.7606 | -121.5225 | 0.004578 | 0.10559 | -0.0046441 | -0.059885 | 0.018639 | -0.012115 | -0.0019525 | -0.0020571 | 0.09079 | 0.025613 | 0.023257 | 0.024268 | 0.016584 | 0.017712 | -0.004578 | -0.064087 | 0.009155 | 0 | -0.045776 | 0.086975 | -0.018311 | 0.032043 | -0.009155 | -0.10071 | -0.045776 | -0.022888 | 0.07782 | 0.004578 | 121.6095 | 121.5042 | -0.050354 | 121.4584 | 121.5225 | 0.018311 | -0.009156 | 121.6003 | 121.5271 | -0.050354 | 121.5546 | 121.4218 | -0.10529 | -0.027466 | 121.4767 | 121.5179 | 121.5317 | -0.022889 | 121.4767 | 121.4996 | 121.5134 | 0
1368.4688 | 121.7743 | -121.5454 | 0.013733 | 0.14374 | -0.0018671 | -0.061808 | 0.022484 | -0.012755 | -0.0021661 | -0.0029117 | 0.08316 | 0.024545 | 0.024966 | 0.023413 | 0.01637 | 0.017712 | 0.004578 | -0.073242 | 0.004578 | 0.004578 | -0.050354 | 0.086975 | -0.009155 | 0.022888 | 0 | -0.086975 | -0.054932 | -0.018311 | 0.07782 | 0.009155 | 121.6324 | 121.5363 | -0.064087 | 121.4722 | 121.55 | 0.013733 | -0.009155 | 121.6232 | 121.5546 | -0.068665 | 121.5683 | 121.4584 | -0.09613 | -0.032044 | 121.4951 | 121.55 | 121.55 | -0.022888 | 121.4905 | 121.5271 | 121.5454 | -0.004578
1370.2188 | 121.7514 | -121.5454 | 0.036621 | -0.13092 | -0.0012263 | -0.060312 | 0.026756 | -0.011474 | -0.0038751 | -0.0016299 | -0.15335 | 0.024973 | 0.02518 | 0.022986 | 0.015088 | 0.015148 | 0 | -0.059509 | 0.045776 | 0.009155 | -0.041199 | 0.09613 | -0.022888 | 0.022888 | 0.050354 | -0.07782 | -0.054932 | -0.027466 | 0.073242 | -0.009155 | 121.6415 | 121.5225 | -0.07782 | 121.4859 | 121.5546 | 0.032043 | -0.036621 | 121.6187 | 121.5363 | -0.091553 | 121.5683 | 121.4676 | -0.068665 | -0.064087 | 121.5042 | 121.5454 | 121.5912 | -0.059509 | 121.4905 | 121.5179 | 121.5958 | -0.045776
1371.9688 | 121.8384 | -121.5546 | -0.009155 | 0.014038 | -0.0035761 | -0.060312 | 0.023125 | -0.014678 | -0.0090021 | -0.0041933 | 0.11368 | 0.024118 | 0.024112 | 0.021704 | 0.012097 | 0.017284 | 0.009155 | 0.009155 | 0.10071 | 0.054932 | -0.068665 | 0.12817 | 0.004578 | 0.07782 | 0.07782 | -0.009155 | -0.073242 | -0.050354 | 0.09613 | 0.041199 | 121.6827 | 121.5591 | -0.05951 | 121.5637 | 121.6095 | 0.050354 | 0.01831 | 121.6507 | 121.5958 | -0.064087 | 121.6324 | 121.5454 | -0.050354 | -0.041199 | 121.4859 | 121.5637 | 121.6553 | 0.013733 | 121.4813 | 121.5042 | 121.6324 | 0.050354
1373.7344 | 121.7972 | -121.5591 | 0.009155 | 0.12848 | -0.0035761 | -0.061808 | 0.022697 | -0.01126 | -0.0070795 | -0.0052615 | 0.17471 | 0.023264 | 0.024966 | 0.024695 | 0.01167 | 0.017925 | 0.082397 | 0.064087 | 0.14191 | 0.064087 | -0.086975 | 0.11902 | 0.022888 | 0.10071 | 0.082397 | 0.018311 | -0.068665 | -0.054932 | 0.10071 | 0.027466 | 121.6782 | 121.582 | -0.09613 | 121.6232 | 121.6232 | 0.041199 | 0.073242 | 121.6599 | 121.5866 | -0.07782 | 121.6599 | 121.5775 | -0.009155 | -0.064087 | 121.4722 | 121.6415 | 121.7011 | 0.013733 | 121.4905 | 121.5042 | 121.6415 | 0.018311
1375.4219 | 121.8658 | -121.5408 | 0 | 0.17426 | -0.0042169 | -0.059885 | 0.017357 | -0.012115 | -0.00088448 | -0.0046207 | 0.052643 | 0.025827 | 0.023898 | 0.025977 | 0.018079 | 0.015362 | 0.059509 | 0 | 0.10071 | 0.045776 | -0.073242 | 0.13275 | 0.027466 | 0.10986 | 0.1236 | 0.022888 | -0.086975 | -0.068665 | 0.11444 | 0.059509 | 121.6736 | 121.5683 | -0.073242 | 121.5408 | 121.5866 | 0.01831 | 0.059509 | 121.6553 | 121.6003 | -0.086975 | 121.6507 | 121.5637 | -0.036621 | -0.068665 | 121.4676 | 121.6003 | 121.6415 | 0.027466 | 121.4539 | 121.4722 | 121.6644 | 0.059509
1377.1719 | 121.7148 | -121.582 | 0.045776 | -0.062256 | -0.00058528 | -0.064585 | 0.021202 | -0.011474 | 0.00061092 | -0.0035525 | -0.061798 | 0.025827 | 0.024112 | 0.025336 | 0.015943 | 0.014721 | 0.073242 | 0 | 0.073242 | 0.032043 | -0.041199 | 0.091553 | 0.004578 | 0.054932 | 0.064087 | -0.068665 | -0.041199 | -0.027466 | 0.09613 | 0 | 121.6736 | 121.5866 | -0.086975 | 121.582 | 121.6141 | 0.027465 | 0.027466 | 121.6782 | 121.582 | -0.086975 | 121.637 | 121.5134 | -0.068665 | -0.073242 | 121.5408 | 121.6553 | 121.6553 | -0.041198 | 121.5408 | 121.5546 | 121.6461 | -0.045776
1378.9219 | 121.7331 | -121.5958 | 0.036621 | -0.19196 | -0.0035761 | -0.059244 | 0.025902 | -0.012969 | -0.0064387 | -0.0037661 | -0.17624 | 0.021127 | 0.026675 | 0.024908 | 0.012097 | 0.018352 | 0.054932 | 0.032043 | 0.091553 | 0.045776 | -0.059509 | 0.10529 | -0.022888 | 0.009155 | 0.086975 | -0.054932 | -0.054932 | -0.041199 | 0.064087 | 0.022888 | 121.7011 | 121.5729 | -0.09613 | 121.6278 | 121.6415 | 0.068664 | 0.018311 | 121.6599 | 121.6187 | -0.091553 | 121.6049 | 121.5408 | -0.07782 | -0.07782 | 121.5363 | 121.6507 | 121.6873 | -0.059509 | 121.5408 | 121.5546 | 121.6827 | -0.013733
1380.625 | 121.8613 | -121.5683 | -0.013733 | -0.069885 | -0.0029351 | -0.059885 | 0.024406 | -0.01126 | -0.0072931 | -0.0033389 | -0.046539 | 0.02305 | 0.02518 | 0.024268 | 0.013379 | 0.017071 | 0.086975 | 0.082397 | 0.15106 | 0.082397 | -0.073242 | 0.11902 | 0.027466 | 0.13733 | 0.14648 | 0.068665 | -0.07782 | -0.054932 | 0.10529 | 0.041199 | 121.6873 | 121.5958 | -0.059509 | 121.6507 | 121.6507 | 0.054931 | 0.10071 | 121.6736 | 121.6095 | -0.064087 | 121.7056 | 121.637 | 0.027466 | -0.041199 | 121.4951 | 121.6553 | 121.7194 | 0.041199 | 121.4905 | 121.5134 | 121.7148 | 0.054932
1382.3906 | 121.8292 | -121.6049 | 0 | 0.067444 | -0.0033625 | -0.060953 | 0.02227 | -0.012969 | -0.0055841 | -0.0050479 | 0.09079 | 0.023691 | 0.026462 | 0.024481 | 0.012525 | 0.016003 | 0.064087 | 0.041199 | 0.10529 | 0.045776 | -0.073242 | 0.11902 | 0.045776 | 0.09613 | 0.082397 | -0.009155 | -0.086975 | -0.068665 | 0.10986 | 0.022888 | 121.7239 | 121.6507 | -0.073242 | 121.6461 | 121.6507 | 0 | 0.064087 | 121.7148 | 121.6278 | -0.086975 | 121.701 | 121.5958 | -0.032043 | -0.068665 | 121.5317 | 121.669 | 121.7102 | 0.045776 | 121.5179 | 121.5363 | 121.6873 | 0.022888
1384.1406 | 121.8063 | -121.6095 | 0.027466 | -0.13855 | 0.0019781 | -0.060099 | 0.023766 | -0.012755 | 0.00018372 | -0.0035525 | -0.1915 | 0.025613 | 0.025821 | 0.026404 | 0.017438 | 0.013225 | 0.013733 | -0.045776 | 0.036621 | 0.018311 | -0.050354 | 0.086975 | -0.022888 | 0.027466 | 0.045776 | -0.064087 | -0.041199 | -0.036621 | 0.050354 | 0.013733 | 121.6965 | 121.5866 | -0.07782 | 121.5637 | 121.6278 | 0.041199 | -0.013733 | 121.6599 | 121.6232 | -0.068665 | 121.637 | 121.5454 | -0.07782 | -0.064087 | 121.5591 | 121.6232 | 121.6461 | -0.050354 | 121.5683 | 121.5729 | 121.6553 | -0.013733
1385.875 | 121.8613 | -121.5775 | -0.004578 | 0.159 | -0.0046441 | -0.062876 | 0.020348 | -0.011474 | -0.0025935 | -0.0022707 | 0.18234 | 0.022623 | 0.025821 | 0.022986 | 0.015943 | 0.018352 | 0.09613 | 0.082397 | 0.15564 | 0.082397 | -0.10529 | 0.13275 | 0.036621 | 0.15106 | 0.12817 | 0.036621 | -0.082397 | -0.073242 | 0.1236 | 0.036621 | 121.7102 | 121.6141 | -0.10071 | 121.6599 | 121.6599 | 0.045776 | 0.10071 | 121.7011 | 121.6141 | -0.077819 | 121.7285 | 121.6141 | 0 | -0.068664 | 121.4722 | 121.6736 | 121.7331 | 0.041199 | 121.4951 | 121.5042 | 121.7056 | 0.041199
1387.5625 | 121.8796 | -121.5729 | -0.004578 | -0.11566 | -0.0040033 | -0.059885 | 0.021629 | -0.010406 | -0.0083613 | -0.0052615 | -0.092316 | 0.021982 | 0.024112 | 0.023413 | 0.01167 | 0.017071 | 0.10529 | 0.10986 | 0.14648 | 0.091553 | -0.07782 | 0.12817 | 0.022888 | 0.13733 | 0.17395 | 0.059509 | -0.068665 | -0.068665 | 0.10986 | 0.036621 | 121.701 | 121.5958 | -0.073242 | 121.6827 | 121.6644 | 0.068665 | 0.10986 | 121.6827 | 121.6095 | -0.064087 | 121.7102 | 121.6324 | 0.022888 | -0.064087 | 121.4951 | 121.6782 | 121.7194 | 0.027466 | 121.5042 | 121.5042 | 121.7468 | 0.041199
1389.3281 | 121.7926 | -121.637 | 0.018311 | -0.19958 | -0.0027215 | -0.060312 | 0.023552 | -0.01126 | -0.0010981 | -0.0054751 | -0.17624 | 0.025613 | 0.024753 | 0.023199 | 0.017011 | 0.016857 | 0.018311 | -0.050354 | 0.022888 | 0.009155 | -0.054932 | 0.082397 | -0.018311 | 0.022888 | 0.022888 | -0.082397 | -0.041199 | -0.036621 | 0.064087 | -0.004578 | 121.7194 | 121.6187 | -0.073243 | 121.5866 | 121.6461 | 0.027466 | 0 | 121.701 | 121.6324 | -0.05951 | 121.6599 | 121.5546 | -0.077819 | -0.054932 | 121.582 | 121.6553 | 121.6599 | -0.036622 | 121.5958 | 121.6003 | 121.6599 | -0.022889
1391.0781 | 121.8658 | -121.6095 | 0.027466 | 0.097962 | -0.0072077 | -0.060953 | 0.01992 | -0.010833 | -0.0068659 | -0.0031253 | 0.16708 | 0.024118 | 0.023471 | 0.022986 | 0.018293 | 0.016643 | 0.10986 | 0.07782 | 0.15564 | 0.059509 | -0.086975 | 0.13733 | 0.032043 | 0.13733 | 0.1236 | 0.036621 | -0.068665 | -0.045776 | 0.11444 | 0.045776 | 121.7468 | 121.6415 | -0.11444 | 121.6873 | 121.669 | 0.027466 | 0.082397 | 121.7239 | 121.6553 | -0.096131 | 121.7468 | 121.6461 | -0.009155 | -0.073242 | 121.5225 | 121.7194 | 121.7651 | 0.004577 | 121.5408 | 121.5637 | 121.7331 | 0.01831
1392.7812 | 121.7697 | -121.6553 | 0.054932 | -0.19196 | -0.0014399 | -0.061594 | 0.024193 | -0.013183 | -0.0025935 | -0.0059023 | -0.092316 | 0.024545 | 0.023471 | 0.024481 | 0.015088 | 0.01643 | 0.036621 | 0 | 0.07782 | 0.036621 | -0.068665 | 0.10529 | -0.032043 | 0.022888 | 0.036621 | -0.068665 | -0.032043 | -0.027466 | 0.082397 | -0.004578 | 121.7606 | 121.6232 | -0.1236 | 121.6553 | 121.6919 | 0.068664 | -0.018311 | 121.7377 | 121.6507 | -0.086975 | 121.6782 | 121.5866 | -0.064087 | -0.082398 | 121.5866 | 121.6919 | 121.7331 | -0.086975 | 121.6232 | 121.6278 | 121.6919 | -0.05951
1394.5312 | 121.8018 | -121.637 | 0.018311 | -0.046997 | -0.00015808 | -0.063089 | 0.021843 | -0.01361 | 0.00039732 | -0.0039797 | -0.13046 | 0.026041 | 0.024325 | 0.025763 | 0.015088 | 0.015362 | 0.073242 | -0.004578 | 0.073242 | 0.041199 | -0.045776 | 0.11902 | -0.013733 | 0.082397 | 0.082397 | -0.027466 | -0.054932 | -0.045776 | 0.07782 | 0.013733 | 121.756 | 121.6232 | -0.064087 | 121.6324 | 121.6782 | 0.054932 | 0.054931 | 121.7148 | 121.6507 | -0.073243 | 121.7194 | 121.6095 | -0.041199 | -0.064087 | 121.5912 | 121.7102 | 121.7102 | -0.032044 | 121.582 | 121.5912 | 121.7194 | -0.004578
1396.2969 | 121.8384 | -121.6461 | 0.018311 | -0.11566 | -0.0016535 | -0.062876 | 0.024834 | -0.011687 | -0.00024348 | 0.00029268 | -0.12283 | 0.024759 | 0.024539 | 0.024054 | 0.017438 | 0.016857 | 0.045776 | 0.004578 | 0.064087 | 0.045776 | -0.045776 | 0.091553 | -0.009155 | 0.064087 | 0.082397 | -0.036621 | -0.050354 | -0.050354 | 0.082397 | 0.018311 | 121.7377 | 121.637 | -0.064087 | 121.6507 | 121.6919 | 0.054931 | 0.027465 | 121.7285 | 121.6644 | -0.068665 | 121.7102 | 121.6095 | -0.054932 | -0.068665 | 121.6003 | 121.6919 | 121.7102 | -0.027466 | 121.5958 | 121.5958 | 121.7285 | 0
1398 | 121.7926 | -121.6827 | 0.036621 | -0.054626 | -0.0010125 | -0.06373 | 0.023125 | -0.011474 | -0.0010981 | -0.0014163 | -0.061798 | 0.027109 | 0.023471 | 0.024695 | 0.017438 | 0.01643 | 0.045776 | -0.004578 | 0.059509 | 0.054932 | -0.064087 | 0.10986 | -0.009155 | 0.041199 | 0.059509 | -0.068665 | -0.068665 | -0.022888 | 0.082397 | 0.013733 | 121.7926 | 121.6736 | -0.10071 | 121.6782 | 121.7377 | 0.064087 | 0.009155 | 121.7651 | 121.6965 | -0.10529 | 121.7239 | 121.6141 | -0.082398 | -0.059509 | 121.6187 | 121.7285 | 121.7422 | -0.045776 | 121.6141 | 121.6599 | 121.7422 | -0.022888
1399.75 | 121.9391 | -121.6324 | -0.013733 | -0.062256 | -0.0057123 | -0.06074 | 0.024834 | -0.01126 | -0.0087885 | -0.0073977 | -0.03891 | 0.023691 | 0.021762 | 0.023199 | 0.012952 | 0.01878 | 0.068665 | 0.07782 | 0.12817 | 0.068665 | -0.082397 | 0.13733 | 0.018311 | 0.12817 | 0.16022 | 0.059509 | -0.073242 | -0.059509 | 0.11902 | 0.045776 | 121.7697 | 121.6507 | -0.068664 | 121.7102 | 121.701 | 0.050354 | 0.082398 | 121.7514 | 121.6782 | -0.059509 | 121.7606 | 121.6919 | 0.013733 | -0.045776 | 121.55 | 121.701 | 121.7606 | 0.032044 | 121.5591 | 121.5729 | 121.7926 | 0.059509
1401.5 | 121.907 | -121.6507 | 0.022888 | 0.10559 | -0.0057123 | -0.060312 | 0.021202 | -0.010192 | -0.0057977 | -0.0039797 | 0.10605 | 0.023904 | 0.023684 | 0.022559 | 0.01402 | 0.017284 | 0.059509 | 0.041199 | 0.13275 | 0.050354 | -0.086975 | 0.11444 | 0.022888 | 0.10986 | 0.091553 | 0.004578 | -0.086975 | -0.064087 | 0.10529 | 0.050354 | 121.7651 | 121.6736 | -0.10986 | 121.6919 | 121.701 | 0.027466 | 0.036621 | 121.756 | 121.701 | -0.10986 | 121.7606 | 121.6553 | -0.045776 | -0.086975 | 121.5637 | 121.7102 | 121.7834 | 0 | 121.5637 | 121.5866 | 121.7422 | 0.027466
1403.25 | 121.9299 | -121.6553 | 0.009155 | -0.10803 | -0.0046441 | -0.061167 | 0.024834 | -0.012755 | -0.0060113 | -0.0056887 | -0.061798 | 0.021555 | 0.024966 | 0.022772 | 0.011457 | 0.014721 | 0.10529 | 0.10986 | 0.17395 | 0.086975 | -0.07782 | 0.10986 | 0.027466 | 0.16022 | 0.17395 | 0.07782 | -0.091553 | -0.068665 | 0.10529 | 0.032043 | 121.7651 | 121.6827 | -0.086975 | 121.7651 | 121.7422 | 0.059509 | 0.096131 | 121.7606 | 121.6873 | -0.10071 | 121.8155 | 121.7331 | 0.045777 | -0.07782 | 121.5775 | 121.7606 | 121.8292 | 0.018311 | 121.5637 | 121.5866 | 121.8292 | 0.022888
1404.9375 | 121.8796 | -121.669 | 0.041199 | -0.20721 | -0.0016535 | -0.058817 | 0.025902 | -0.012542 | -0.0019525 | -0.0048343 | -0.20676 | 0.024759 | 0.025393 | 0.02384 | 0.015302 | 0.015148 | 0.009155 | -0.050354 | 0.022888 | 0 | -0.036621 | 0.091553 | -0.009155 | 0.013733 | 0.022888 | -0.09613 | -0.050354 | -0.004578 | 0.07782 | 0.018311 | 121.7606 | 121.6599 | -0.07782 | 121.6187 | 121.669 | 0.009155 | -0.032044 | 121.7468 | 121.6873 | -0.091553 | 121.6827 | 121.5729 | -0.11444 | -0.045777 | 121.6324 | 121.6782 | 121.6919 | -0.050354 | 121.6187 | 121.6644 | 121.6919 | -0.022888
1406.6875 | 121.8292 | -121.6736 | 0.032043 | 0.059815 | -0.0020807 | -0.064798 | 0.018211 | -0.012328 | 0.0010381 | -0.0039797 | 0.0068663 | 0.024332 | 0.024539 | 0.026404 | 0.019788 | 0.015148 | 0.009155 | -0.07782 | 0 | -0.009155 | -0.032043 | 0.091553 | -0.018311 | -0.009155 | -0.013733 | -0.13275 | -0.036621 | -0.022888 | 0.086975 | 0.027466 | 121.7651 | 121.6553 | -0.064086 | 121.5958 | 121.6644 | 0.009156 | -0.022888 | 121.7606 | 121.7011 | -0.068664 | 121.6644 | 121.5408 | -0.16022 | -0.054931 | 121.6415 | 121.6827 | 121.6736 | -0.050354 | 121.637 | 121.6507 | 121.6599 | -0.004577
1408.4375 | 121.8521 | -121.6873 | 0.027466 | -0.13855 | -0.00037168 | -0.060526 | 0.028679 | -0.010192 | -0.0019525 | -0.0059023 | -0.20676 | 0.026682 | 0.026248 | 0.024054 | 0.012952 | 0.018352 | -0.013733 | -0.054932 | 0.018311 | -0.004578 | -0.054932 | 0.073242 | -0.022888 | 0.009155 | 0.032043 | -0.082397 | -0.041199 | -0.022888 | 0.068665 | 0.009155 | 121.7606 | 121.6644 | -0.082398 | 121.6324 | 121.6827 | 0.01831 | -0.041199 | 121.756 | 121.6965 | -0.068665 | 121.6965 | 121.6049 | -0.091552 | -0.050354 | 121.6324 | 121.6736 | 121.7056 | -0.050354 | 121.6461 | 121.6644 | 121.7194 | -0.018311
1410.1875 | 121.962 | -121.669 | -0.009155 | -0.054626 | -0.0037897 | -0.060099 | 0.022484 | -0.011046 | -0.0072931 | -0.0035525 | -0.077057 | 0.023264 | 0.024325 | 0.022772 | 0.013593 | 0.018352 | 0.059509 | 0.073242 | 0.13733 | 0.07782 | -0.07782 | 0.10986 | 0.013733 | 0.13733 | 0.15106 | 0.068665 | -0.082397 | -0.073242 | 0.09613 | 0.032043 | 121.7789 | 121.6827 | -0.068665 | 121.7422 | 121.7468 | 0.064087 | 0.068664 | 121.7651 | 121.701 | -0.073242 | 121.8063 | 121.7377 | 0.036622 | -0.064087 | 121.5912 | 121.7285 | 121.8063 | 0.022888 | 121.5866 | 121.5958 | 121.8201 | 0.041198
1411.875 | 121.9482 | -121.6507 | 0.018311 | 0.12085 | -0.00079888 | -0.062021 | 0.018639 | -0.013824 | -0.0013117 | -0.0050479 | 0.12894 | 0.023904 | 0.021548 | 0.02384 | 0.01872 | 0.016003 | 0.032043 | -0.036621 | 0.009155 | -0.013733 | -0.050354 | 0.1236 | -0.004578 | 0.07782 | 0.045776 | -0.032043 | -0.064087 | -0.050354 | 0.10529 | 0.022888 | 121.7743 | 121.6461 | -0.068665 | 121.6141 | 121.637 | -0.009155 | 0.013732 | 121.756 | 121.6736 | -0.082398 | 121.7285 | 121.6187 | -0.054931 | -0.068665 | 121.6003 | 121.6827 | 121.6599 | -0.022889 | 121.5866 | 121.6003 | 121.6965 | 0.004577
1413.625 | 121.843 | -121.7056 | 0.032043 | -0.21484 | 0.0015509 | -0.060526 | 0.027824 | -0.011901 | -0.0040887 | -0.0061161 | -0.16861 | 0.024332 | 0.025821 | 0.024695 | 0.012952 | 0.016643 | 0.036621 | 0.041199 | 0.073242 | 0.041199 | -0.07782 | 0.091553 | -0.013733 | 0.022888 | 0.082397 | -0.059509 | -0.045776 | -0.032043 | 0.09613 | 0.013733 | 121.7972 | 121.6919 | -0.10986 | 121.7468 | 121.7468 | 0.054932 | 0.004578 | 121.8018 | 121.7194 | -0.077819 | 121.7285 | 121.6461 | -0.073242 | -0.064086 | 121.6278 | 121.7422 | 121.7789 | -0.045776 | 121.6599 | 121.6736 | 121.788 | -0.01831
1415.375 | 121.8338 | -121.7056 | 0.032043 | 0.0064086 | -0.00079888 | -0.062662 | 0.022484 | -0.012969 | 0.0012519 | -0.0048343 | 0.0068663 | 0.023264 | 0.024112 | 0.025763 | 0.017865 | 0.01643 | 0.027466 | -0.018311 | 0.036621 | 0.018311 | -0.050354 | 0.11444 | -0.018311 | 0.018311 | 0.004578 | -0.091553 | -0.045776 | -0.032043 | 0.082397 | 0.009155 | 121.8201 | 121.6873 | -0.082397 | 121.6873 | 121.7239 | 0.036622 | -0.004577 | 121.788 | 121.7148 | -0.077819 | 121.7239 | 121.6141 | -0.10071 | -0.064086 | 121.6553 | 121.7331 | 121.7422 | -0.050354 | 121.6599 | 121.6736 | 121.7102 | -0.022888
1417.0625 | 121.9162 | -121.701 | 0.032043 | -0.085144 | 0.00026912 | -0.063303 | 0.024193 | -0.011901 | -0.0010981 | -0.0046207 | -0.17624 | 0.026041 | 0.024325 | 0.024054 | 0.017652 | 0.017498 | 0.018311 | -0.018311 | 0.045776 | 0.022888 | -0.054932 | 0.086975 | -0.032043 | 0.045776 | 0.050354 | -0.050354 | -0.059509 | -0.045776 | 0.068665 | 0.009155 | 121.788 | 121.669 | -0.086975 | 121.6827 | 121.7239 | 0.054931 | -0.013732 | 121.7697 | 121.7102 | -0.091552 | 121.7468 | 121.6507 | -0.059509 | -0.077819 | 121.6461 | 121.7194 | 121.7468 | -0.064086 | 121.6415 | 121.6553 | 121.7514 | -0.022888
1418.8125 | 121.8704 | -121.7148 | 0.054932 | -0.046997 | 0.0011237 | -0.062021 | 0.025902 | -0.013824 | -0.00024348 | -0.0014163 | -0.10757 | 0.026254 | 0.026889 | 0.025336 | 0.016156 | 0.017498 | 0.050354 | 0.004578 | 0.064087 | 0.036621 | -0.054932 | 0.11444 | -0.032043 | 0.07782 | 0.082397 | -0.045776 | -0.050354 | -0.032043 | 0.082397 | 0.018311 | 121.8292 | 121.6827 | -0.10986 | 121.7194 | 121.7514 | 0.068664 | -0.004578 | 121.7972 | 121.7331 | -0.10529 | 121.7926 | 121.669 | -0.064087 | -0.086975 | 121.6599 | 121.7651 | 121.7789 | -0.086975 | 121.6644 | 121.6827 | 121.7972 | -0.036621
1420.5 | 121.907 | -121.701 | 0.018311 | -0.13092 | 0.0011237 | -0.06138 | 0.024193 | -0.012755 | -0.0021661 | -0.0029117 | -0.13809 | 0.025186 | 0.027743 | 0.023199 | 0.014661 | 0.016857 | 0 | -0.004578 | 0.054932 | 0.032043 | -0.086975 | 0.091553 | -0.018311 | 0.041199 | 0.073242 | -0.050354 | -0.045776 | -0.036621 | 0.091553 | 0.022888 | 121.7926 | 121.6827 | -0.10529 | 121.6965 | 121.7331 | 0.050354 | -0.018311 | 121.7926 | 121.7239 | -0.064087 | 121.7422 | 121.6507 | -0.073242 | -0.054932 | 121.6141 | 121.701 | 121.756 | -0.036622 | 121.6553 | 121.6644 | 121.7743 | 0.004577
1422.25 | 121.9528 | -121.7056 | 0.018311 | 0.14374 | -0.0022943 | -0.061594 | 0.020348 | -0.013396 | -0.0064387 | -0.0056887 | 0.17471 | 0.022195 | 0.023471 | 0.022345 | 0.013593 | 0.019421 | 0.068665 | 0.064087 | 0.12817 | 0.059509 | -0.07782 | 0.1236 | 0.009155 | 0.10529 | 0.11902 | 0.009155 | -0.07782 | -0.054932 | 0.10071 | 0.045776 | 121.8292 | 121.7148 | -0.096131 | 121.7697 | 121.7651 | 0.050354 | 0.050354 | 121.8063 | 121.7514 | -0.096131 | 121.8109 | 121.7148 | -0.036621 | -0.073243 | 121.6278 | 121.7743 | 121.8338 | -0.009156 | 121.6278 | 121.6507 | 121.8246 | 0.027465
1424 | 122.0169 | -121.7056 | -0.018311 | 0.10559 | -0.0027215 | -0.062876 | 0.021629 | -0.012969 | -0.0010981 | -0.0031253 | 0.17471 | 0.027322 | 0.02283 | 0.023413 | 0.018079 | 0.016216 | -0.009155 | -0.050354 | 0.032043 | 0.009155 | -0.054932 | 0.09613 | -0.013733 | 0.064087 | 0.045776 | -0.036621 | -0.054932 | -0.050354 | 0.086975 | 0.032043 | 121.8018 | 121.6919 | -0.036621 | 121.6553 | 121.7148 | 0.022888 | 0.009156 | 121.7926 | 121.7377 | -0.036621 | 121.7697 | 121.669 | -0.068664 | -0.032043 | 121.6507 | 121.6965 | 121.7377 | 0.004578 | 121.6507 | 121.6553 | 121.7514 | 0.050354
1425.6875 | 121.9025 | -121.7514 | 0.036621 | -0.069885 | 0.0011237 | -0.061594 | 0.020775 | -0.012328 | -0.00024348 | -0.0039797 | -0.084686 | 0.0254 | 0.024753 | 0.02384 | 0.016797 | 0.016216 | 0.050354 | -0.009155 | 0.064087 | 0.022888 | -0.07782 | 0.082397 | -0.013733 | 0.059509 | 0.086975 | -0.036621 | -0.050354 | -0.036621 | 0.10071 | 0.022888 | 121.8338 | 121.7377 | -0.11444 | 121.7422 | 121.7743 | 0.036621 | 0.013733 | 121.8521 | 121.7743 | -0.086975 | 121.8109 | 121.7148 | -0.059509 | -0.073242 | 121.6736 | 121.8018 | 121.8155 | -0.050354 | 121.701 | 121.7148 | 121.8384 | -0.013733
1427.4375 | 121.9757 | -121.7285 | 0 | 0.159 | -0.0031489 | -0.060099 | 0.022911 | -0.015746 | -0.0053705 | -0.0037661 | 0.15945 | 0.023691 | 0.023898 | 0.022986 | 0.014234 | 0.018352 | 0.086975 | 0.07782 | 0.13733 | 0.068665 | -0.091553 | 0.1236 | 0.022888 | 0.13733 | 0.11902 | 0.054932 | -0.07782 | -0.068665 | 0.11444 | 0.059509 | 121.8521 | 121.7514 | -0.091553 | 121.8063 | 121.7972 | 0.045777 | 0.086975 | 121.843 | 121.788 | -0.07782 | 121.8658 | 121.7834 | -0.004577 | -0.068665 | 121.637 | 121.8155 | 121.8658 | 0.022888 | 121.6507 | 121.6599 | 121.8475 | 0.059509
1429.2031 | 121.9116 | -121.7422 | 0.009155 | -0.062256 | -0.0010125 | -0.062021 | 0.023979 | -0.011687 | 0.0018927 | -0.0024845 | -0.12283 | 0.023904 | 0.02518 | 0.022986 | 0.018506 | 0.015575 | 0.050354 | 0.009155 | 0.059509 | 0.032043 | -0.059509 | 0.10071 | 0 | 0.073242 | 0.091553 | -0.027466 | -0.050354 | -0.027466 | 0.082397 | 0.027466 | 121.843 | 121.7422 | -0.068664 | 121.7514 | 121.7743 | 0.032043 | 0.041199 | 121.8246 | 121.7697 | -0.059509 | 121.8155 | 121.7148 | -0.054932 | -0.036621 | 121.6827 | 121.7926 | 121.8018 | -0.009155 | 121.6919 | 121.7148 | 121.8338 | 0.018311
1430.8906 | 121.9299 | -121.7606 | 0.036621 | -0.19196 | -0.00079888 | -0.060953 | 0.023125 | -0.011046 | -0.0047297 | -0.0026981 | -0.17624 | 0.023904 | 0.024966 | 0.023627 | 0.012097 | 0.015789 | -0.018311 | -0.036621 | 0.018311 | -0.004578 | -0.045776 | 0.086975 | -0.022888 | 0 | 0.041199 | -0.091553 | -0.027466 | -0.036621 | 0.073242 | 0 | 121.8475 | 121.7377 | -0.082397 | 121.7239 | 121.756 | 0.01831 | -0.054932 | 121.8338 | 121.7606 | -0.064087 | 121.7606 | 121.669 | -0.091553 | -0.073242 | 121.7148 | 121.7422 | 121.7789 | -0.059509 | 121.7331 | 121.7239 | 121.8018 | -0.036621
1432.6406 | 121.8887 | -121.8155 | 0.032043 | -0.016479 | 0.0019781 | -0.064798 | 0.021416 | -0.010619 | 0.00061092 | -0.0037661 | -0.016022 | 0.026468 | 0.024112 | 0.026617 | 0.018293 | 0.017925 | 0.045776 | -0.013733 | 0.050354 | 0.032043 | -0.054932 | 0.09613 | -0.013733 | 0.027466 | 0.022888 | -0.07782 | -0.045776 | -0.036621 | 0.086975 | 0.027466 | 121.9116 | 121.8018 | -0.086975 | 121.8018 | 121.8475 | 0.045776 | 0.013733 | 121.9025 | 121.843 | -0.077819 | 121.843 | 121.7377 | -0.10529 | -0.068664 | 121.7606 | 121.8613 | 121.8658 | -0.045776 | 121.7697 | 121.7789 | 121.8384 | -0.004577
1434.3594 | 122.0261 | -121.7468 | 0.009155 | -0.11566 | -0.0029351 | -0.059885 | 0.025902 | -0.011687 | -0.0092157 | -0.0031253 | -0.084686 | 0.020059 | 0.023684 | 0.020422 | 0.013593 | 0.018993 | 0.10529 | 0.10529 | 0.17395 | 0.086975 | -0.09613 | 0.11902 | 0.013733 | 0.11444 | 0.16479 | 0.054932 | -0.091553 | -0.054932 | 0.11902 | 0.054932 | 121.8658 | 121.7606 | -0.10528 | 121.8521 | 121.8338 | 0.073242 | 0.096131 | 121.8658 | 121.8018 | -0.10071 | 121.8613 | 121.8018 | 0 | -0.064087 | 121.6507 | 121.8521 | 121.9208 | 0.004578 | 121.6553 | 121.6919 | 121.9116 | 0.045777
1436.1094 | 122.0123 | -121.7606 | 0.013733 | 0.059815 | -0.0063531 | -0.06074 | 0.020988 | -0.013183 | -0.0070795 | -0.0071841 | 0.075531 | 0.021127 | 0.023684 | 0.024268 | 0.013379 | 0.016216 | 0.027466 | 0.027466 | 0.10529 | 0.054932 | -0.064087 | 0.11902 | 0.018311 | 0.073242 | 0.073242 | -0.013733 | -0.073242 | -0.050354 | 0.10071 | 0.027466 | 121.8796 | 121.7789 | -0.07782 | 121.788 | 121.8155 | 0.036621 | 0.013733 | 121.8613 | 121.788 | -0.086975 | 121.8338 | 121.7468 | -0.041199 | -0.064087 | 121.6965 | 121.788 | 121.8658 | 0.004578 | 121.6873 | 121.7102 | 121.8338 | 0.013733
1437.8594 | 121.9986 | -121.756 | 0.022888 | 0.059815 | -0.0042169 | -0.059885 | 0.021629 | -0.014892 | -0.0043023 | -0.0056887 | 0.075531 | 0.022409 | 0.02283 | 0.022986 | 0.015729 | 0.014721 | 0.059509 | 0.022888 | 0.086975 | 0.036621 | -0.073242 | 0.11902 | 0.022888 | 0.082397 | 0.073242 | 0.009155 | -0.068665 | -0.045776 | 0.10071 | 0.045776 | 121.875 | 121.7789 | -0.09613 | 121.7789 | 121.7926 | 0.013733 | 0.036621 | 121.8567 | 121.8018 | -0.091553 | 121.8384 | 121.7651 | -0.036621 | -0.068664 | 121.6827 | 121.8155 | 121.843 | 0 | 121.6873 | 121.7102 | 121.8292 | 0.022888
1439.5469 | 122.0032 | -121.7377 | 0.027466 | 0.11322 | -0.0020807 | -0.062662 | 0.022057 | -0.011474 | 0.00039732 | -0.0059023 | 0.045013 | 0.024973 | 0.02518 | 0.024908 | 0.019147 | 0.013866 | 0.018311 | -0.064087 | -0.009155 | 0 | -0.041199 | 0.09613 | 0.004578 | 0.032043 | -0.004578 | -0.086975 | -0.054932 | -0.027466 | 0.082397 | 0.027466 | 121.8338 | 121.7422 | -0.068665 | 121.6736 | 121.7377 | -0.004578 | -0.009155 | 121.8201 | 121.7651 | -0.082398 | 121.7697 | 121.6507 | -0.11444 | -0.054932 | 121.6965 | 121.756 | 121.7285 | -0.022888 | 121.6827 | 121.7102 | 121.7331 | 0
1441.3125 | 121.9482 | -121.7697 | 0.041199 | -0.16907 | -0.0040033 | -0.059244 | 0.021843 | -0.011901 | -0.0025935 | -0.0063297 | -0.21439 | 0.024759 | 0.023684 | 0.023413 | 0.01402 | 0.016643 | 0.004578 | -0.068665 | 0.018311 | 0.004578 | -0.054932 | 0.082397 | -0.013733 | 0.004578 | 0.013733 | -0.086975 | -0.032043 | -0.018311 | 0.064087 | 0.004578 | 121.8521 | 121.756 | -0.096131 | 121.701 | 121.7743 | 0.018311 | -0.036621 | 121.8338 | 121.7743 | -0.073242 | 121.7743 | 121.6827 | -0.091553 | -0.05951 | 121.7148 | 121.7743 | 121.788 | -0.054932 | 121.7377 | 121.7514 | 121.7834 | -0.036621
1443.0625 | 121.9345 | -121.7972 | 0.041199 | -0.18433 | -0.0029351 | -0.06074 | 0.023552 | -0.014037 | -0.0060113 | -0.0056887 | -0.17624 | 0.021982 | 0.02518 | 0.022345 | 0.013806 | 0.01643 | 0.064087 | 0.032043 | 0.09613 | 0.054932 | -0.059509 | 0.11444 | -0.004578 | 0.041199 | 0.086975 | -0.032043 | -0.054932 | -0.041199 | 0.09613 | 0.013733 | 121.9116 | 121.7926 | -0.10071 | 121.8292 | 121.8521 | 0.05951 | 0.022888 | 121.8933 | 121.8109 | -0.096131 | 121.8384 | 121.7651 | -0.045776 | -0.082398 | 121.7377 | 121.8613 | 121.8933 | -0.045777 | 121.7422 | 121.756 | 121.8842 | -0.027466
1444.8125 | 122.0535 | -121.7606 | 0 | -0.092773 | -0.0042169 | -0.060099 | 0.025902 | -0.012542 | -0.0070795 | -0.0071841 | -0.084686 | 0.022195 | 0.023684 | 0.023199 | 0.011884 | 0.017284 | 0.10529 | 0.091553 | 0.16022 | 0.082397 | -0.091553 | 0.14648 | 0.013733 | 0.16022 | 0.16479 | 0.068665 | -0.073242 | -0.068665 | 0.11902 | 0.054932 | 121.907 | 121.7743 | -0.091553 | 121.8521 | 121.843 | 0.068664 | 0.10529 | 121.8796 | 121.8155 | -0.073242 | 121.9208 | 121.8292 | 0.013733 | -0.068665 | 121.669 | 121.8658 | 121.9208 | 0.013733 | 121.6873 | 121.6919 | 121.9254 | 0.054932
1446.5156 | 121.9254 | -121.8018 | 0.027466 | -0.0088499 | -0.0025079 | -0.064157 | 0.019707 | -0.013396 | 0.0040289 | -0.0033389 | 0.014496 | 0.023477 | 0.023684 | 0.025977 | 0.020642 | 0.014721 | 0.041199 | -0.036621 | 0.022888 | 0 | -0.050354 | 0.086975 | -0.013733 | 0.022888 | 0 | -0.10986 | -0.041199 | -0.027466 | 0.082397 | 0.013733 | 121.8887 | 121.788 | -0.07782 | 121.7651 | 121.8018 | 0.013733 | 0.013733 | 121.8842 | 121.8155 | -0.068665 | 121.8246 | 121.6919 | -0.1236 | -0.054932 | 121.7514 | 121.843 | 121.8246 | -0.041199 | 121.7606 | 121.7743 | 121.8018 | -0.013733
1448.2812 | 122.0398 | -121.7651 | 0.022888 | 0.11322 | -0.0014399 | -0.060312 | 0.020134 | -0.011901 | -0.00088448 | -0.0033389 | 0.052643 | 0.021341 | 0.023684 | 0.024481 | 0.016156 | 0.017071 | 0.018311 | -0.054932 | 0.004578 | 0.009155 | -0.036621 | 0.10071 | -0.009155 | 0.036621 | 0.009155 | -0.091553 | -0.032043 | -0.036621 | 0.091553 | 0.022888 | 121.8658 | 121.756 | -0.059509 | 121.7102 | 121.7743 | 0.01831 | -0.004577 | 121.8567 | 121.788 | -0.054931 | 121.8018 | 121.6736 | -0.11444 | -0.059509 | 121.7285 | 121.7834 | 121.7697 | -0.032043 | 121.7331 | 121.7285 | 121.7743 | 0
1450.0312 | 122.0718 | -121.7697 | 0.009155 | 0.029297 | -0.0065667 | -0.060099 | 0.024406 | -0.015105 | -0.0090021 | -0.0048343 | 0.067902 | 0.020914 | 0.024753 | 0.022131 | 0.011884 | 0.018993 | 0.022888 | 0.013733 | 0.10529 | 0.036621 | -0.10529 | 0.1236 | 0.022888 | 0.086975 | 0.086975 | 0.009155 | -0.064087 | -0.059509 | 0.091553 | 0.027466 | 121.8933 | 121.7926 | -0.11444 | 121.7834 | 121.8063 | 0.013733 | 0.013733 | 121.8613 | 121.7972 | -0.073242 | 121.8567 | 121.7789 | -0.018311 | -0.068664 | 121.6644 | 121.7926 | 121.875 | 0.013733 | 121.7056 | 121.7102 | 121.8567 | 0.018311
1451.7812 | 121.9803 | -121.7972 | 0.013733 | 0.090332 | -0.0027215 | -0.06074 | 0.01992 | -0.012969 | -0.00067088 | -0.0054751 | 0.075531 | 0.023264 | 0.021975 | 0.022986 | 0.018506 | 0.016216 | 0 | -0.082397 | -0.004578 | 0.004578 | -0.041199 | 0.086975 | -0.018311 | 0.013733 | -0.022888 | -0.10529 | -0.045776 | -0.032043 | 0.07782 | 0.004578 | 121.8842 | 121.7789 | -0.054932 | 121.7148 | 121.8018 | 0.022889 | -0.013733 | 121.875 | 121.8018 | -0.059509 | 121.8109 | 121.6919 | -0.10986 | -0.045776 | 121.756 | 121.7972 | 121.7926 | -0.032044 | 121.7514 | 121.7651 | 121.7743 | -0.009155
1453.4844 | 122.0306 | -121.7789 | 0.009155 | 0.097962 | -0.0050715 | -0.057962 | 0.023125 | -0.01361 | -0.0068659 | -0.0067569 | 0.11368 | 0.02305 | 0.025821 | 0.022772 | 0.013379 | 0.017925 | 0.045776 | 0.032043 | 0.10529 | 0.045776 | -0.086975 | 0.12817 | 0.009155 | 0.086975 | 0.082397 | 0 | -0.086975 | -0.073242 | 0.11902 | 0.045776 | 121.907 | 121.788 | -0.09613 | 121.8109 | 121.8246 | 0.036621 | 0.036621 | 121.8979 | 121.8246 | -0.09613 | 121.8658 | 121.7789 | -0.045776 | -0.082397 | 121.6919 | 121.8246 | 121.8842 | 0 | 121.6919 | 121.7056 | 121.8613 | 0.036621
1455.2344 | 121.9528 | -121.8246 | 0.027466 | -0.19958 | -0.0020807 | -0.059885 | 0.02697 | -0.01126 | -0.0025935 | -0.0054751 | -0.18387 | 0.021555 | 0.024753 | 0.021918 | 0.015088 | 0.014507 | 0.050354 | 0.018311 | 0.10071 | 0.050354 | -0.059509 | 0.086975 | 0 | 0.022888 | 0.073242 | -0.059509 | -0.050354 | -0.022888 | 0.07782 | 0.004578 | 121.9116 | 121.8246 | -0.086975 | 121.843 | 121.875 | 0.050354 | 0.022888 | 121.9025 | 121.8292 | -0.07782 | 121.8475 | 121.7651 | -0.064087 | -0.050354 | 121.7651 | 121.875 | 121.9254 | -0.027466 | 121.7743 | 121.8018 | 121.8979 | -0.022888
1456.9844 | 122.0123 | -121.8155 | 0.032043 | -0.22247 | 0.0011237 | -0.06138 | 0.028038 | -0.015319 | -0.00067088 | -0.0048343 | -0.1915 | 0.023264 | 0.026248 | 0.025122 | 0.014875 | 0.014934 | -0.004578 | -0.054932 | 0.013733 | 0.009155 | -0.036621 | 0.07782 | -0.022888 | 0.013733 | 0.013733 | -0.082397 | -0.036621 | -0.027466 | 0.07782 | 0.009155 | 121.8933 | 121.7926 | -0.068664 | 121.7606 | 121.8246 | 0.032043 | -0.036621 | 121.8933 | 121.8246 | -0.068664 | 121.8292 | 121.7331 | -0.091552 | -0.059509 | 121.7789 | 121.8109 | 121.8292 | -0.054931 | 121.7789 | 121.788 | 121.8292 | -0.022888
1458.6719 | 121.9894 | -121.8338 | 0.027466 | -0.077515 | -0.00058528 | -0.061167 | 0.02227 | -0.010619 | 0.00039732 | -0.0033389 | -0.1152 | 0.024759 | 0.02518 | 0.024695 | 0.017652 | 0.015362 | 0.050354 | 0.018311 | 0.068665 | 0.032043 | -0.054932 | 0.091553 | 0 | 0.07782 | 0.07782 | -0.027466 | -0.045776 | -0.041199 | 0.10071 | 0.022888 | 121.9254 | 121.8338 | -0.082398 | 121.8521 | 121.8658 | 0.032043 | 0.022888 | 121.9345 | 121.8567 | -0.073242 | 121.9116 | 121.8063 | -0.050354 | -0.068665 | 121.7789 | 121.8842 | 121.9025 | -0.027466 | 121.788 | 121.7926 | 121.9116 | -0.004578
1460.4219 | 122.0352 | -121.8567 | 0.022888 | -0.16907 | -0.0040033 | -0.060312 | 0.023552 | -0.010833 | -0.0077203 | -0.0046207 | -0.099945 | 0.021127 | 0.024112 | 0.022986 | 0.012525 | 0.018139 | 0.082397 | 0.10529 | 0.16022 | 0.09613 | -0.091553 | 0.11444 | 0.009155 | 0.10986 | 0.16479 | 0.050354 | -0.064087 | -0.07782 | 0.10986 | 0.050354 | 121.9711 | 121.8658 | -0.11444 | 121.962 | 121.9528 | 0.086975 | 0.059509 | 121.9666 | 121.907 | -0.086975 | 121.9666 | 121.907 | 0 | -0.10071 | 121.7651 | 121.9391 | 122.0169 | -0.013733 | 121.7926 | 121.7789 | 122.0215 | 0.027466
1462.1875 | 122.0535 | -121.8109 | -0.022888 | 0.159 | -0.0035761 | -0.062235 | 0.020775 | -0.012755 | -0.0040887 | -0.0048343 | 0.1442 | 0.0207 | 0.022189 | 0.02384 | 0.015515 | 0.01643 | 0.10071 | 0.082397 | 0.15564 | 0.091553 | -0.07782 | 0.12817 | 0.032043 | 0.13275 | 0.13733 | 0.036621 | -0.068665 | -0.07782 | 0.11902 | 0.041199 | 121.9391 | 121.843 | -0.054932 | 121.8933 | 121.9025 | 0.05951 | 0.1236 | 121.9299 | 121.8521 | -0.045777 | 121.9437 | 121.8475 | -0.004578 | -0.054932 | 121.7331 | 121.9116 | 121.9666 | 0.054931 | 121.7422 | 121.7331 | 121.9482 | 0.064087
1463.8906 | 121.9849 | -121.8567 | 0.036621 | -0.21484 | -0.0018671 | -0.059244 | 0.024406 | -0.011046 | -0.0043023 | -0.0073977 | -0.1915 | 0.022409 | 0.024966 | 0.02149 | 0.014234 | 0.017925 | 0.059509 | 0.050354 | 0.10071 | 0.064087 | -0.07782 | 0.10986 | 0.018311 | 0.050354 | 0.073242 | -0.027466 | -0.050354 | -0.036621 | 0.082397 | 0.022888 | 121.9666 | 121.875 | -0.11444 | 121.907 | 121.9208 | 0.045776 | 0.022888 | 121.9391 | 121.8796 | -0.086975 | 121.907 | 121.8292 | -0.050354 | -0.073242 | 121.7789 | 121.9162 | 121.9574 | -0.01831 | 121.8063 | 121.8201 | 121.9299 | -0.013733
1465.6406 | 122.0673 | -121.8063 | -0.013733 | 0.15137 | -0.0050715 | -0.059885 | 0.018852 | -0.014251 | -0.0040887 | -0.0022707 | 0.13657 | 0.022195 | 0.024112 | 0.024695 | 0.016584 | 0.017712 | 0.10529 | 0.091553 | 0.15106 | 0.07782 | -0.068665 | 0.1236 | 0.018311 | 0.13733 | 0.10986 | 0.036621 | -0.07782 | -0.050354 | 0.11902 | 0.050354 | 121.9299 | 121.8246 | -0.054932 | 121.8979 | 121.8842 | 0.059509 | 0.11902 | 121.9254 | 121.8567 | -0.064087 | 121.9437 | 121.843 | -0.013733 | -0.036621 | 121.7377 | 121.9116 | 121.9574 | 0.032044 | 121.7285 | 121.756 | 121.9162 | 0.064087
1467.3281 | 122.0718 | -121.8384 | 0 | 0.12085 | -0.0040033 | -0.059671 | 0.01928 | -0.013183 | -0.0034479 | -0.0044071 | 0.11368 | 0.02305 | 0.023898 | 0.022131 | 0.017438 | 0.016216 | 0.10986 | 0.082397 | 0.14191 | 0.064087 | -0.09613 | 0.14191 | 0.013733 | 0.13733 | 0.11902 | 0.027466 | -0.086975 | -0.068665 | 0.11444 | 0.059509 | 121.9803 | 121.8521 | -0.09613 | 121.9208 | 121.9025 | 0.050354 | 0.10986 | 121.9528 | 121.8979 | -0.086975 | 121.9757 | 121.8658 | -0.032043 | -0.068665 | 121.7422 | 121.9482 | 121.9803 | 0.013733 | 121.7514 | 121.7697 | 121.9574 | 0.059509
1469.0781 | 122.0673 | -121.843 | 0.018311 | 0.12848 | -0.0052851 | -0.057108 | 0.020561 | -0.014892 | -0.0051569 | -0.0063297 | 0.10605 | 0.022836 | 0.023898 | 0.021277 | 0.016156 | 0.015575 | 0.091553 | 0.054932 | 0.13275 | 0.050354 | -0.07782 | 0.13733 | 0.018311 | 0.10529 | 0.086975 | 0 | -0.086975 | -0.064087 | 0.10986 | 0.041199 | 121.9803 | 121.8613 | -0.096131 | 121.8979 | 121.8933 | 0.032043 | 0.073242 | 121.9528 | 121.8842 | -0.10529 | 121.9482 | 121.843 | -0.041199 | -0.082398 | 121.7651 | 121.9345 | 121.9757 | 0 | 121.756 | 121.7789 | 121.9299 | 0.022888
1470.7656 | 122.1268 | -121.8246 | 0.013733 | 0.021668 | -0.0065667 | -0.060953 | 0.022484 | -0.01126 | -0.0068659 | -0.0069705 | 0.029755 | 0.020486 | 0.02283 | 0.021918 | 0.013379 | 0.017284 | 0.054932 | 0.013733 | 0.086975 | 0.041199 | -0.054932 | 0.10986 | 0.022888 | 0.086975 | 0.07782 | -0.004578 | -0.064087 | -0.064087 | 0.11444 | 0.022888 | 121.9345 | 121.8475 | -0.068665 | 121.8384 | 121.8658 | 0.018311 | 0.041199 | 121.9391 | 121.8475 | -0.07782 | 121.9116 | 121.8201 | -0.027466 | -0.07782 | 121.7697 | 121.8796 | 121.9116 | 0.009155 | 121.7606 | 121.7606 | 121.9025 | 0.009155
1472.5312 | 122.0993 | -121.8063 | 0.009155 | 0.13611 | -0.0063531 | -0.061167 | 0.020988 | -0.012755 | -0.00088448 | -0.0035525 | 0.15182 | 0.023691 | 0.022403 | 0.022772 | 0.01872 | 0.015575 | 0.12817 | 0.068665 | 0.13733 | 0.091553 | -0.09613 | 0.11902 | 0.036621 | 0.15106 | 0.11444 | 0.032043 | -0.073242 | -0.059509 | 0.10986 | 0.050354 | 121.9254 | 121.843 | -0.10528 | 121.875 | 121.8979 | 0.054932 | 0.11902 | 121.9162 | 121.8567 | -0.082397 | 121.9574 | 121.8384 | -0.018311 | -0.068664 | 121.7102 | 121.9345 | 121.9437 | 0.027466 | 121.7331 | 121.7468 | 121.9208 | 0.041199
1474.2188 | 121.994 | -121.8704 | 0.027466 | -0.15381 | -0.0025079 | -0.059244 | 0.023766 | -0.011687 | -0.0047297 | -0.0037661 | -0.14572 | 0.021768 | 0.024112 | 0.021918 | 0.013593 | 0.016216 | 0.10071 | 0.07782 | 0.14191 | 0.073242 | -0.082397 | 0.10986 | 0.009155 | 0.10071 | 0.13275 | 0.022888 | -0.07782 | -0.064087 | 0.10071 | 0.045776 | 121.9803 | 121.8796 | -0.10986 | 121.9482 | 121.9437 | 0.064087 | 0.073242 | 121.9711 | 121.9162 | -0.10529 | 121.9711 | 121.8933 | -0.022888 | -0.091553 | 121.788 | 121.9711 | 122.0123 | -0.018311 | 121.7926 | 121.8063 | 122.0032 | 0.01831
1475.9688 | 122.0627 | -121.8292 | 0.013733 | -0.10803 | -0.00058528 | -0.062235 | 0.022697 | -0.014037 | 0.0010381 | -0.0029117 | -0.15335 | 0.021341 | 0.026675 | 0.024695 | 0.01637 | 0.014934 | 0.064087 | -0.022888 | 0.059509 | 0.041199 | -0.036621 | 0.091553 | -0.032043 | 0.073242 | 0.082397 | -0.036621 | -0.045776 | -0.027466 | 0.091553 | 0.027466 | 121.9208 | 121.7972 | -0.050354 | 121.8063 | 121.8704 | 0.073242 | 0.050354 | 121.9208 | 121.8567 | -0.059509 | 121.9025 | 121.7926 | -0.064087 | -0.041199 | 121.7926 | 121.8933 | 121.8887 | -0.045776 | 121.7834 | 121.8018 | 121.9116 | 0.013733
1477.7188 | 122.049 | -121.8658 | 0.022888 | -0.16907 | -0.0016535 | -0.059671 | 0.024406 | -0.013824 | -0.0040887 | -0.0033389 | -0.10757 | 0.019846 | 0.026248 | 0.023627 | 0.01402 | 0.018139 | 0.086975 | 0.086975 | 0.15106 | 0.082397 | -0.091553 | 0.12817 | 0.009155 | 0.11902 | 0.15564 | 0.036621 | -0.10071 | -0.073242 | 0.10071 | 0.050354 | 121.994 | 121.875 | -0.11444 | 121.9528 | 121.9482 | 0.073242 | 0.064087 | 121.9666 | 121.9162 | -0.1236 | 121.9849 | 121.9025 | -0.013733 | -0.09613 | 121.7743 | 121.9528 | 122.0169 | -0.013733 | 121.7651 | 121.7926 | 122.0215 | 0.027466
1479.4219 | 122.1634 | -121.8475 | -0.004578 | 0.014038 | -0.00058528 | -0.061594 | 0.023125 | -0.015746 | -0.0068659 | -0.0052615 | 0.037384 | 0.020059 | 0.02518 | 0.023627 | 0.012311 | 0.017284 | 0.036621 | 0.018311 | 0.09613 | 0.041199 | -0.064087 | 0.11902 | 0.018311 | 0.082397 | 0.09613 | -0.004578 | -0.068665 | -0.050354 | 0.10986 | 0.032043 | 121.9666 | 121.8658 | -0.059509 | 121.8658 | 121.8887 | 0.022888 | 0.041199 | 121.9574 | 121.8796 | -0.064087 | 121.9299 | 121.843 | -0.036621 | -0.045776 | 121.7834 | 121.8842 | 121.9437 | 0.022889 | 121.7789 | 121.7972 | 121.9437 | 0.036621
1481.1875 | 122.049 | -121.8613 | 0.009155 | -0.14618 | -0.0022943 | -0.059458 | 0.021629 | -0.012969 | -0.0038751 | -0.0046207 | -0.12283 | 0.022409 | 0.023684 | 0.022772 | 0.012952 | 0.017071 | 0.10529 | 0.10071 | 0.15564 | 0.082397 | -0.07782 | 0.11902 | 0.013733 | 0.1236 | 0.15106 | 0.036621 | -0.073242 | -0.054932 | 0.10529 | 0.059509 | 121.9803 | 121.875 | -0.086975 | 121.962 | 121.9437 | 0.068664 | 0.096131 | 121.9666 | 121.9208 | -0.082397 | 121.9849 | 121.8979 | -0.022888 | -0.064087 | 121.7834 | 121.9666 | 122.0169 | 0.004578 | 121.788 | 121.8063 | 122.0123 | 0.050354
1482.9375 | 122.0993 | -121.8796 | -0.004578 | 0.090332 | -0.0033625 | -0.059885 | 0.021416 | -0.0097646 | -0.0038751 | -0.0063297 | 0.12131 | 0.019632 | 0.024325 | 0.022559 | 0.015302 | 0.017925 | 0.086975 | 0.082397 | 0.15106 | 0.064087 | -0.07782 | 0.1236 | 0.009155 | 0.13733 | 0.10529 | 0.009155 | -0.10529 | -0.054932 | 0.10986 | 0.041199 | 122.0032 | 121.8887 | -0.073242 | 121.962 | 121.9437 | 0.054932 | 0.091553 | 121.9894 | 121.9208 | -0.10071 | 122.0169 | 121.8887 | -0.032044 | -0.050354 | 121.8018 | 121.9666 | 122.0306 | 0.013733 | 121.7743 | 121.8246 | 121.9849 | 0.045777
1484.6406 | 122.1863 | -121.8613 | -0.013733 | -0.031738 | -0.0010125 | -0.060526 | 0.023125 | -0.014464 | -0.0045161 | -0.0041933 | -0.15335 | 0.021982 | 0.026248 | 0.023199 | 0.012952 | 0.016643 | 0.059509 | 0.054932 | 0.10986 | 0.059509 | -0.064087 | 0.13733 | 0.013733 | 0.15564 | 0.14648 | 0.045776 | -0.073242 | -0.068665 | 0.10071 | 0.041199 | 121.9986 | 121.875 | -0.050354 | 121.9162 | 121.9208 | 0.045776 | 0.073242 | 121.962 | 121.9025 | -0.059509 | 122.0169 | 121.907 | 0.004577 | -0.054932 | 121.7972 | 121.9208 | 121.9711 | 0.027466 | 121.788 | 121.7926 | 122.0078 | 0.054932
1486.4062 | 122.0856 | -121.9116 | 0.022888 | -0.12329 | -0.0012263 | -0.060312 | 0.020348 | -0.012542 | 0.0014655 | -0.0026981 | -0.20676 | 0.024545 | 0.024753 | 0.022559 | 0.016584 | 0.014721 | 0.032043 | -0.032043 | 0.036621 | 0.018311 | -0.045776 | 0.073242 | -0.013733 | 0.050354 | 0.050354 | -0.054932 | -0.064087 | -0.045776 | 0.07782 | 0.004578 | 121.9849 | 121.8979 | -0.068664 | 121.8796 | 121.9299 | 0.032044 | 0.009155 | 121.9894 | 121.9162 | -0.086975 | 121.962 | 121.8567 | -0.05951 | -0.068664 | 121.8658 | 121.9437 | 121.9482 | -0.036621 | 121.8475 | 121.8658 | 121.962 | -0.01831
1488.1562 | 122.1405 | -121.8475 | -0.009155 | 0.15137 | -0.0052851 | -0.060953 | 0.016716 | -0.013824 | -0.0034479 | -0.0026981 | 0.13657 | 0.022623 | 0.02283 | 0.02085 | 0.017865 | 0.016003 | 0.10529 | 0.064087 | 0.13275 | 0.082397 | -0.082397 | 0.13275 | 0.013733 | 0.16022 | 0.12817 | 0.022888 | -0.082397 | -0.059509 | 0.091553 | 0.064087 | 121.9803 | 121.8613 | -0.073242 | 121.9116 | 121.9299 | 0.068664 | 0.11444 | 121.9391 | 121.9116 | -0.073242 | 122.0078 | 121.8704 | -0.041199 | -0.050354 | 121.7651 | 121.9528 | 121.9803 | 0.022888 | 121.7651 | 121.788 | 121.9757 | 0.073242
1489.9062 | 122.1451 | -121.8521 | 0.009155 | 0.10559 | -0.0040033 | -0.06074 | 0.01992 | -0.014464 | -0.00088448 | -0.0048343 | 0.12894 | 0.020914 | 0.023471 | 0.024695 | 0.017438 | 0.016003 | 0.018311 | -0.036621 | 0.041199 | 0.022888 | -0.064087 | 0.09613 | -0.013733 | 0.07782 | 0.041199 | -0.036621 | -0.050354 | -0.041199 | 0.086975 | 0.027466 | 121.9482 | 121.8384 | -0.073242 | 121.8155 | 121.875 | 0.036621 | 0.009156 | 121.9391 | 121.8796 | -0.059509 | 121.9299 | 121.8155 | -0.064087 | -0.050354 | 121.788 | 121.8704 | 121.8933 | -0.022888 | 121.8018 | 121.8109 | 121.8933 | 0.018311
1491.5938 | 122.1634 | -121.8521 | -0.018311 | 0.17426 | -0.0020807 | -0.06138 | 0.020988 | -0.013183 | 0.00018372 | -0.0046207 | 0.10605 | 0.02305 | 0.021121 | 0.022345 | 0.015943 | 0.018139 | 0.050354 | -0.004578 | 0.07782 | 0.027466 | -0.050354 | 0.11444 | 0.004578 | 0.10986 | 0.10071 | -0.018311 | -0.068665 | -0.064087 | 0.10986 | 0.041199 | 121.9666 | 121.8567 | -0.032043 | 121.8475 | 121.8796 | 0.022888 | 0.068665 | 121.962 | 121.8933 | -0.050354 | 121.962 | 121.8338 | -0.05951 | -0.045776 | 121.8018 | 121.9025 | 121.9299 | 0.022889 | 121.7834 | 121.788 | 121.9528 | 0.05951
1493.2812 | 122.1359 | -121.8704 | -0.009155 | 0.18188 | -0.0061395 | -0.062876 | 0.023552 | -0.014037 | -0.0047297 | -0.0046207 | 0.15182 | 0.020486 | 0.023471 | 0.023199 | 0.016156 | 0.016216 | 0.10529 | 0.073242 | 0.14191 | 0.073242 | -0.09613 | 0.12817 | 0.022888 | 0.15564 | 0.13733 | 0.027466 | -0.082397 | -0.07782 | 0.11444 | 0.041199 | 121.9986 | 121.8933 | -0.086975 | 121.9437 | 121.9437 | 0.050354 | 0.11444 | 121.9849 | 121.9116 | -0.073242 | 122.0261 | 121.8979 | -0.013733 | -0.068665 | 121.7743 | 121.9757 | 122.0123 | 0.032043 | 121.788 | 121.7926 | 122.0078 | 0.050354
1495.0469 | 122.0398 | -121.9299 | 0.036621 | -0.18433 | -0.0022943 | -0.062021 | 0.026756 | -0.010192 | -0.0034479 | -0.0048343 | -0.092316 | 0.020273 | 0.026889 | 0.022559 | 0.012525 | 0.018139 | 0.059509 | 0.018311 | 0.082397 | 0.050354 | -0.068665 | 0.10529 | -0.009155 | 0.045776 | 0.050354 | -0.068665 | -0.054932 | -0.036621 | 0.07782 | 0 | 122.0352 | 121.9208 | -0.10529 | 121.9482 | 121.9803 | 0.059509 | 0.022888 | 122.0078 | 121.9299 | -0.091553 | 121.9757 | 121.8613 | -0.068665 | -0.073242 | 121.8613 | 121.9894 | 122.0123 | -0.045776 | 121.875 | 121.8933 | 121.9803 | -0.036621
1496.7969 | 122.1863 | -121.8842 | 0 | 0.021668 | -0.0052851 | -0.061594 | 0.01928 | -0.012328 | -0.0081477 | -0.0056887 | 0.052643 | 0.018991 | 0.021548 | 0.023627 | 0.01402 | 0.017712 | 0.022888 | 0.022888 | 0.091553 | 0.045776 | -0.073242 | 0.10529 | 0 | 0.09613 | 0.09613 | 0.009155 | -0.068665 | -0.064087 | 0.09613 | 0.050354 | 121.9894 | 121.8842 | -0.073242 | 121.907 | 121.9299 | 0.045776 | 0.022888 | 121.9803 | 121.9345 | -0.068665 | 121.9803 | 121.8933 | -0.041199 | -0.064087 | 121.8109 | 121.907 | 121.9757 | 0 | 121.8155 | 121.8201 | 121.9803 | 0.050354
1498.4844 | 122.1359 | -121.8933 | 0.004578 | 0.12085 | -0.0020807 | -0.061167 | 0.019066 | -0.01361 | -0.00088448 | -0.0041933 | 0.060272 | 0.021982 | 0.023684 | 0.022559 | 0.01637 | 0.015362 | 0.036621 | -0.073242 | 0.018311 | 0.009155 | -0.041199 | 0.07782 | -0.013733 | 0.050354 | 0.004578 | -0.086975 | -0.050354 | -0.045776 | 0.10071 | 0.032043 | 121.9711 | 121.8796 | -0.045777 | 121.8201 | 121.9025 | 0.022888 | 0.032043 | 121.994 | 121.9254 | -0.054932 | 121.9437 | 121.8063 | -0.11902 | -0.050354 | 121.8521 | 121.9299 | 121.9116 | -0.018311 | 121.843 | 121.8475 | 121.8979 | 0.027465
1500.25 | 122.1909 | -121.8933 | 0.009155 | 0.18188 | -0.0027215 | -0.06074 | 0.018425 | -0.012115 | 0.00082452 | -0.0054751 | 0.11368 | 0.022623 | 0.023044 | 0.021918 | 0.014661 | 0.016857 | 0.068665 | 0 | 0.068665 | 0.036621 | -0.064087 | 0.10071 | 0.009155 | 0.1236 | 0.07782 | 0 | -0.068665 | -0.068665 | 0.11444 | 0.045776 | 121.994 | 121.9025 | -0.073242 | 121.8933 | 121.9299 | 0.027466 | 0.05951 | 122.0078 | 121.9391 | -0.07782 | 122.0169 | 121.8933 | -0.045776 | -0.07782 | 121.8292 | 121.962 | 121.962 | 0 | 121.8246 | 121.8246 | 121.9711 | 0.036621
1502 | 122.113 | -121.9254 | 0.022888 | -0.16144 | 0.0011237 | -0.06138 | 0.023125 | -0.011901 | -0.0019525 | -0.0052615 | -0.17624 | 0.022836 | 0.02518 | 0.024054 | 0.015088 | 0.016216 | 0.013733 | -0.059509 | 0.018311 | 0.018311 | -0.032043 | 0.09613 | -0.018311 | 0.013733 | 0.036621 | -0.07782 | -0.059509 | -0.032043 | 0.086975 | 0.009155 | 122.0215 | 121.907 | -0.054931 | 121.8658 | 121.9437 | 0.036622 | -0.009155 | 122.0123 | 121.9345 | -0.082397 | 121.9391 | 121.8475 | -0.086975 | -0.054931 | 121.8933 | 121.9391 | 121.9437 | -0.041199 | 121.8658 | 121.8933 | 121.962 | -0.013733
1503.7031 | 122.0581 | -121.9254 | 0.036621 | 0.15137 | -0.00058528 | -0.061808 | 0.022057 | -0.011046 | 0.00082452 | -0.0026981 | 0.014496 | 0.020273 | 0.024753 | 0.024054 | 0.017224 | 0.01643 | 0.022888 | -0.064087 | 0.022888 | 0.004578 | -0.059509 | 0.091553 | -0.018311 | 0 | 0.009155 | -0.10071 | -0.041199 | -0.022888 | 0.068665 | 0.004578 | 122.0169 | 121.907 | -0.09613 | 121.8613 | 121.9299 | 0.022889 | -0.013733 | 121.994 | 121.9299 | -0.07782 | 121.9254 | 121.8246 | -0.10529 | -0.059509 | 121.8658 | 121.9482 | 121.9482 | -0.054932 | 121.8842 | 121.9025 | 121.9345 | -0.032043
1505.4688 | 122.1497 | -121.9025 | 0 | 0.11322 | -0.0027215 | -0.059671 | 0.020561 | -0.01361 | -0.0013117 | -0.0024845 | 0.08316 | 0.019846 | 0.024112 | 0.022772 | 0.01637 | 0.017284 | 0.013733 | -0.073242 | 0.013733 | 0 | -0.041199 | 0.086975 | -0.036621 | 0.054932 | 0.009155 | -0.073242 | -0.054932 | -0.036621 | 0.091553 | 0.013733 | 121.9894 | 121.8658 | -0.041199 | 121.8292 | 121.9025 | 0.036621 | 0.013733 | 121.994 | 121.9162 | -0.054932 | 121.9574 | 121.8292 | -0.086975 | -0.036621 | 121.8613 | 121.9162 | 121.9162 | -0.036621 | 121.8475 | 121.8658 | 121.9116 | 0.013733
1507.1719 | 122.2137 | -121.8979 | -0.009155 | 0.15137 | -0.0037897 | -0.062021 | 0.021416 | -0.0093374 | -0.0055841 | -0.0033389 | 0.13657 | 0.0207 | 0.025607 | 0.022131 | 0.015088 | 0.017071 | 0.07782 | 0.041199 | 0.1236 | 0.086975 | -0.07782 | 0.12817 | 0.004578 | 0.1236 | 0.13275 | 0.027466 | -0.091553 | -0.073242 | 0.11444 | 0.036621 | 122.0261 | 121.9025 | -0.068665 | 121.9391 | 121.9849 | 0.082397 | 0.086975 | 122.0123 | 121.9345 | -0.082398 | 122.0215 | 121.9254 | -0.009155 | -0.064087 | 121.8201 | 121.9757 | 122.0215 | 0.013733 | 121.8063 | 121.8246 | 122.0306 | 0.045776
1508.9375 | 122.1588 | -121.9116 | 0.022888 | 0.11322 | -0.0035761 | -0.061167 | 0.024193 | -0.014251 | -0.0049433 | -0.0059023 | 0.15945 | 0.021127 | 0.023684 | 0.024054 | 0.012097 | 0.01643 | 0.10529 | 0.050354 | 0.13733 | 0.073242 | -0.082397 | 0.13733 | 0.009155 | 0.13275 | 0.11902 | 0.032043 | -0.07782 | -0.054932 | 0.1236 | 0.050354 | 122.0489 | 121.9208 | -0.10528 | 121.962 | 121.9849 | 0.064087 | 0.082398 | 122.0352 | 121.962 | -0.10071 | 122.0444 | 121.9437 | -0.018311 | -0.07782 | 121.8292 | 122.0169 | 122.0489 | -0.013733 | 121.8338 | 121.8567 | 122.0306 | 0.027466
1510.625 | 122.2275 | -121.8933 | -0.009155 | 0.159 | -0.0035761 | -0.062235 | 0.01992 | -0.015105 | -0.0023797 | -0.0048343 | 0.13657 | 0.021341 | 0.024112 | 0.022986 | 0.017652 | 0.013225 | 0.07782 | 0.018311 | 0.10071 | 0.041199 | -0.082397 | 0.11902 | 0.018311 | 0.11902 | 0.10071 | 0.018311 | -0.068665 | -0.059509 | 0.10986 | 0.036621 | 122.0123 | 121.9116 | -0.073242 | 121.9116 | 121.9345 | 0.022888 | 0.086975 | 122.0032 | 121.9299 | -0.05951 | 122.0123 | 121.9116 | -0.01831 | -0.050354 | 121.8109 | 121.9711 | 121.994 | 0.027466 | 121.8246 | 121.8338 | 121.994 | 0.045776
1512.3906 | 122.1954 | -121.8933 | -0.004578 | 0.15137 | -0.0018671 | -0.063303 | 0.023766 | -0.013824 | -0.0040887 | -0.0020571 | 0.17471 | 0.020273 | 0.026462 | 0.023199 | 0.015729 | 0.014934 | 0.10529 | 0.059509 | 0.15564 | 0.10529 | -0.10986 | 0.13275 | 0.013733 | 0.14191 | 0.11902 | 0.022888 | -0.09613 | -0.07782 | 0.11444 | 0.045776 | 122.0261 | 121.907 | -0.10529 | 121.9528 | 121.9986 | 0.091553 | 0.10986 | 122.0078 | 121.9391 | -0.091552 | 122.0352 | 121.9162 | -0.022888 | -0.073242 | 121.7834 | 121.9986 | 122.049 | 0.018311 | 121.7972 | 121.8155 | 122.0123 | 0.050354
1514.0781 | 122.2321 | -121.9254 | -0.018311 | 0.021668 | -0.0076349 | -0.060312 | 0.022911 | -0.010833 | -0.0083613 | -0.0063297 | 0.022125 | 0.021768 | 0.023471 | 0.024268 | 0.013593 | 0.015575 | 0.050354 | 0.022888 | 0.10071 | 0.050354 | -0.07782 | 0.1236 | 0.004578 | 0.10071 | 0.11902 | 0.036621 | -0.082397 | -0.064087 | 0.10071 | 0.022888 | 122.049 | 121.9299 | -0.059509 | 121.9482 | 121.9757 | 0.045776 | 0.068665 | 122.0261 | 121.9482 | -0.064086 | 122.0261 | 121.962 | 0.013733 | -0.045776 | 121.8475 | 121.9757 | 122.0261 | 0.022889 | 121.843 | 121.8613 | 122.0444 | 0.041199
1515.8281 | 122.1176 | -121.9437 | 0.027466 | 0.059815 | -0.0020807 | -0.062448 | 0.020134 | -0.013183 | 0.0029607 | -0.0044071 | 0.052643 | 0.020914 | 0.026675 | 0.024054 | 0.016797 | 0.016003 | 0.004578 | -0.10529 | -0.018311 | -0.022888 | -0.036621 | 0.091553 | -0.022888 | 0.013733 | -0.022888 | -0.10071 | -0.036621 | -0.050354 | 0.091553 | 0.018311 | 122.0352 | 121.9208 | -0.064087 | 121.8384 | 121.9208 | 0 | -0.022888 | 122.0352 | 121.962 | -0.064087 | 121.9574 | 121.843 | -0.11902 | -0.07782 | 121.907 | 121.9482 | 121.9254 | -0.050354 | 121.907 | 121.8933 | 121.9208 | -0.009155
1517.5156 | 122.0856 | -121.9437 | 0.032043 | -0.18433 | -0.0018671 | -0.060099 | 0.02697 | -0.010833 | -0.0032343 | -0.0054751 | -0.13046 | 0.020486 | 0.02518 | 0.022131 | 0.014447 | 0.016857 | 0.018311 | -0.032043 | 0.032043 | 0.013733 | -0.045776 | 0.1236 | 0.018311 | 0.027466 | 0.032043 | -0.068665 | -0.036621 | -0.022888 | 0.091553 | 0.027466 | 122.0673 | 121.962 | -0.077819 | 121.9116 | 121.9574 | -0.004578 | -0.013732 | 122.0352 | 121.9711 | -0.068664 | 121.9711 | 121.875 | -0.096131 | -0.054931 | 121.8979 | 121.962 | 121.9757 | -0.013732 | 121.907 | 121.9208 | 121.9757 | -0.004577
1519.2812 | 122.1039 | -121.9757 | 0.045776 | 0.059815 | -0.0027215 | -0.062662 | 0.018852 | -0.012328 | 0.0012519 | -0.0024845 | -0.0083922 | 0.023904 | 0.025607 | 0.024908 | 0.017652 | 0.014934 | 0.013733 | -0.064087 | 0.013733 | 0.004578 | -0.064087 | 0.091553 | -0.022888 | 0.004578 | -0.018311 | -0.13275 | -0.041199 | -0.045776 | 0.07782 | -0.004578 | 122.0673 | 121.9528 | -0.10986 | 121.9116 | 121.9803 | 0.027466 | -0.032043 | 122.0535 | 121.9711 | -0.086975 | 121.9803 | 121.843 | -0.12817 | -0.091552 | 121.9116 | 121.9894 | 121.9894 | -0.068664 | 121.9345 | 121.9299 | 121.9574 | -0.050354
1521.0312 | 122.0947 | -121.9849 | 0.036621 | -0.19196 | -0.0022943 | -0.060526 | 0.025902 | -0.010619 | -0.0051569 | -0.0048343 | -0.14572 | 0.022195 | 0.025393 | 0.022986 | 0.01167 | 0.015789 | 0.036621 | 0.032043 | 0.082397 | 0.045776 | -0.064087 | 0.10071 | -0.004578 | 0.032043 | 0.041199 | -0.041199 | -0.045776 | -0.027466 | 0.082397 | 0.022888 | 122.0856 | 121.9803 | -0.10071 | 122.0169 | 122.0306 | 0.050354 | 0 | 122.0673 | 122.0078 | -0.082397 | 122.0169 | 121.9437 | -0.064087 | -0.064087 | 121.9208 | 122.0215 | 122.0673 | -0.041199 | 121.9391 | 121.9574 | 122.0261 | -0.013733
1522.7188 | 122.2366 | -121.9254 | -0.004578 | 0.014038 | -0.0046441 | -0.06138 | 0.023766 | -0.01126 | -0.0081477 | -0.0061161 | 0.067902 | 0.01835 | 0.023471 | 0.024481 | 0.010816 | 0.017071 | 0.013733 | 0.009155 | 0.086975 | 0.054932 | -0.073242 | 0.10529 | 0.009155 | 0.086975 | 0.09613 | 0.004578 | -0.073242 | -0.050354 | 0.10071 | 0.050354 | 122.0306 | 121.9345 | -0.068664 | 121.9345 | 121.9803 | 0.045777 | 0.018311 | 122.0261 | 121.9757 | -0.068664 | 122.0123 | 121.9299 | -0.045776 | -0.045776 | 121.8521 | 121.9391 | 122.0123 | 0.013733 | 121.8521 | 121.875 | 122.0215 | 0.054932
1524.4688 | 122.2366 | -121.9162 | 0.018311 | -0.077515 | -0.0037897 | -0.059885 | 0.021843 | -0.011687 | -0.0085749 | -0.0080387 | -0.077057 | 0.020914 | 0.023471 | 0.023627 | 0.012952 | 0.017071 | 0.091553 | 0.086975 | 0.14648 | 0.07782 | -0.068665 | 0.1236 | 0.032043 | 0.15106 | 0.16937 | 0.064087 | -0.086975 | -0.068665 | 0.11444 | 0.041199 | 122.0398 | 121.9482 | -0.086976 | 122.0032 | 121.994 | 0.045777 | 0.073242 | 122.0306 | 121.9574 | -0.10529 | 122.0673 | 121.9803 | 0.022888 | -0.086976 | 121.8475 | 122.0078 | 122.0627 | 0.013732 | 121.8292 | 121.8475 | 122.0856 | 0.022888
1526.2188 | 122.1359 | -121.9666 | 0.036621 | -0.077515 | -0.0018671 | -0.061167 | 0.020775 | -0.0097646 | -2.988e-05 | -0.0046207 | -0.15335 | 0.021127 | 0.023257 | 0.022131 | 0.018079 | 0.014721 | 0.073242 | -0.004578 | 0.064087 | 0.036621 | -0.036621 | 0.10986 | -0.022888 | 0.07782 | 0.059509 | -0.027466 | -0.059509 | -0.036621 | 0.086975 | 0.013733 | 122.0764 | 121.9437 | -0.073242 | 121.962 | 122.0032 | 0.059509 | 0.036621 | 122.0535 | 121.9803 | -0.09613 | 122.0444 | 121.9391 | -0.041199 | -0.073242 | 121.9299 | 122.0398 | 122.0306 | -0.059509 | 121.907 | 121.9299 | 122.0261 | -0.022888
1527.9062 | 122.1954 | -121.9757 | 0.013733 | -0.16907 | -0.00079888 | -0.061594 | 0.02462 | -0.012328 | -0.0043023 | -0.0041933 | -0.12283 | 0.020059 | 0.024539 | 0.021704 | 0.013593 | 0.013439 | 0.086975 | 0.09613 | 0.15564 | 0.091553 | -0.07782 | 0.11444 | 0.018311 | 0.13275 | 0.16937 | 0.045776 | -0.082397 | -0.07782 | 0.10071 | 0.059509 | 122.0901 | 121.994 | -0.091553 | 122.0718 | 122.0673 | 0.073242 | 0.073242 | 122.0764 | 122.0352 | -0.09613 | 122.1085 | 122.0215 | -0.013733 | -0.091553 | 121.8979 | 122.0627 | 122.1313 | 0.004578 | 121.8933 | 121.8979 | 122.1451 | 0.045776
1529.6562 | 122.1954 | -121.9666 | 0.004578 | 0.097962 | -0.0050715 | -0.061167 | 0.017784 | -0.012542 | -0.0053705 | -0.0050479 | 0.13657 | 0.017923 | 0.023471 | 0.023413 | 0.015943 | 0.017712 | 0.07782 | 0.082397 | 0.15106 | 0.059509 | -0.07782 | 0.13733 | 0.018311 | 0.13275 | 0.10529 | 0.018311 | -0.068665 | -0.059509 | 0.10529 | 0.045776 | 122.1039 | 121.9849 | -0.082398 | 122.049 | 122.0261 | 0.041198 | 0.073242 | 122.0718 | 122.0123 | -0.073243 | 122.0993 | 121.9849 | -0.027465 | -0.064087 | 121.8887 | 122.0444 | 122.1176 | 0.013733 | 121.8979 | 121.907 | 122.0718 | 0.041198
1531.4062 | 122.1634 | -121.9757 | 0.032043 | -0.21484 | -0.0016535 | -0.058817 | 0.021202 | -0.014251 | -0.0043023 | -0.0048343 | -0.19913 | 0.022623 | 0.023684 | 0.024481 | 0.01637 | 0.014507 | 0 | -0.041199 | 0.009155 | -0.004578 | -0.032043 | 0.07782 | -0.018311 | 0.004578 | 0.018311 | -0.10071 | -0.045776 | -0.022888 | 0.07782 | 0.027466 | 122.0535 | 121.9574 | -0.064086 | 121.9345 | 121.9711 | 0.013733 | -0.032043 | 122.0535 | 122.0032 | -0.077819 | 121.9803 | 121.875 | -0.12817 | -0.054931 | 121.9437 | 121.9757 | 121.9849 | -0.050354 | 121.9299 | 121.9528 | 121.994 | -0.004577
1533.0938 | 122.1313 | -121.9803 | 0.045776 | -0.16907 | -0.00037168 | -0.059671 | 0.025261 | -0.01126 | -0.0036615 | -0.0056887 | -0.19913 | 0.020273 | 0.026034 | 0.022559 | 0.012525 | 0.016216 | 0.073242 | 0.064087 | 0.11444 | 0.073242 | -0.068665 | 0.10986 | 0.009155 | 0.059509 | 0.086975 | -0.018311 | -0.07782 | -0.064087 | 0.082397 | 0.013733 | 122.0901 | 121.9894 | -0.11444 | 122.0444 | 122.0535 | 0.064087 | 0.027466 | 122.0627 | 121.994 | -0.1236 | 122.0398 | 121.962 | -0.032044 | -0.10986 | 121.9116 | 122.0535 | 122.0947 | -0.036621 | 121.9025 | 121.9162 | 122.0673 | -0.032043
1534.8438 | 122.2458 | -121.9437 | -0.018311 | 0.17426 | -0.0025079 | -0.060953 | 0.017784 | -0.014037 | -0.0019525 | -0.0037661 | 0.12131 | 0.022195 | 0.023257 | 0.022345 | 0.017224 | 0.014507 | 0.068665 | 0.009155 | 0.086975 | 0.041199 | -0.073242 | 0.11902 | 0.004578 | 0.11902 | 0.086975 | 0.004578 | -0.091553 | -0.050354 | 0.10529 | 0.045776 | 122.0627 | 121.9482 | -0.054931 | 121.9528 | 121.9849 | 0.036621 | 0.086976 | 122.049 | 121.9894 | -0.073242 | 122.0627 | 121.9482 | -0.041198 | -0.032043 | 121.8704 | 122.0123 | 122.0306 | 0.022889 | 121.8521 | 121.8933 | 122.0306 | 0.064087
1536.5938 | 122.2275 | -121.9528 | 0.009155 | 0.036926 | -0.0037897 | -0.060953 | 0.023979 | -0.012755 | -0.0083613 | -0.0048343 | 0.052643 | 0.021127 | 0.02283 | 0.021918 | 0.014447 | 0.018352 | 0.036621 | 0.022888 | 0.10071 | 0.041199 | -0.07782 | 0.11444 | 0.018311 | 0.068665 | 0.082397 | -0.009155 | -0.082397 | -0.064087 | 0.10986 | 0.032043 | 122.0673 | 121.9711 | -0.086975 | 121.9757 | 121.994 | 0.022888 | 0.027466 | 122.0627 | 121.9849 | -0.091552 | 122.0215 | 121.9437 | -0.041198 | -0.073242 | 121.875 | 121.9894 | 122.0535 | 0.009156 | 121.8704 | 121.8887 | 122.0352 | 0.022888
1538.3594 | 122.2092 | -121.9666 | 0.009155 | 0.11322 | -0.0048579 | -0.06138 | 0.023979 | -0.014464 | -0.0043023 | -0.0054751 | 0.09079 | 0.019846 | 0.026034 | 0.024268 | 0.013166 | 0.014934 | 0.073242 | 0.045776 | 0.11902 | 0.050354 | -0.086975 | 0.11902 | 0.032043 | 0.10071 | 0.082397 | 0 | -0.064087 | -0.054932 | 0.11902 | 0.045776 | 122.0856 | 121.9986 | -0.09613 | 122.0123 | 122.0169 | 0.018311 | 0.064087 | 122.0856 | 122.0123 | -0.073242 | 122.0673 | 121.9666 | -0.045776 | -0.064087 | 121.8796 | 122.0398 | 122.0856 | 0.022888 | 121.9025 | 121.9116 | 122.049 | 0.036621
1540.0625 | 122.1451 | -122.0215 | 0.013733 | 0.052185 | 0.0041143 | -0.062235 | 0.019493 | -0.014892 | 0.0023199 | -0.0039797 | -0.031281 | 0.0207 | 0.025821 | 0.024695 | 0.016797 | 0.014294 | 0.009155 | -0.09613 | 0 | 0 | -0.045776 | 0.091553 | -0.036621 | 0.004578 | -0.027466 | -0.11444 | -0.036621 | -0.032043 | 0.073242 | 0.018311 | 122.113 | 121.9849 | -0.059509 | 121.9254 | 122.0215 | 0.036621 | -0.004578 | 122.0947 | 122.0398 | -0.050354 | 122.0261 | 121.907 | -0.13275 | -0.045776 | 121.9757 | 122.0306 | 122.0215 | -0.050354 | 121.9849 | 121.9894 | 121.994 | 0.004578
1541.7969 | 122.2687 | -121.9574 | 0 | 0.159 | -0.0022943 | -0.060526 | 0.019066 | -0.012115 | -0.0015253 | -0.0054751 | 0.075531 | 0.021127 | 0.02048 | 0.022772 | 0.017652 | 0.016216 | 0.068665 | 0.009155 | 0.09613 | 0.036621 | -0.064087 | 0.11444 | 0.018311 | 0.12817 | 0.1236 | 0.018311 | -0.064087 | -0.068665 | 0.11444 | 0.041199 | 122.0718 | 121.9757 | -0.064087 | 121.9666 | 121.994 | 0.01831 | 0.068665 | 122.0718 | 121.9986 | -0.064087 | 122.0856 | 121.9757 | -0.022888 | -0.068665 | 121.8933 | 122.0261 | 122.0535 | 0.018311 | 121.8933 | 121.8887 | 122.081 | 0.041199
1543.5625 | 122.1542 | -122.0078 | 0.041199 | -0.10803 | -0.0016535 | -0.060099 | 0.025047 | -0.012969 | -0.0038751 | -0.0061161 | -0.18387 | 0.021341 | 0.024753 | 0.023627 | 0.012311 | 0.015148 | 0 | -0.045776 | 0.032043 | 0 | -0.059509 | 0.10071 | -0.032043 | 0.013733 | 0.032043 | -0.068665 | -0.041199 | -0.013733 | 0.068665 | 0.013733 | 122.1085 | 121.9757 | -0.10071 | 121.962 | 122.0078 | 0.032043 | -0.041199 | 122.0764 | 122.0215 | -0.082398 | 122.0215 | 121.9391 | -0.082398 | -0.054932 | 121.9482 | 122.0078 | 122.0398 | -0.073242 | 121.9666 | 121.994 | 122.0398 | -0.027466
1545.25 | 122.1542 | -122.0123 | 0.013733 | -0.031738 | 0.0021917 | -0.063944 | 0.023338 | -0.010192 | 0.0025335 | -0.0035525 | -0.084686 | 0.023264 | 0.026675 | 0.025336 | 0.014661 | 0.014934 | 0.07782 | 0.004578 | 0.07782 | 0.045776 | -0.059509 | 0.10071 | -0.004578 | 0.068665 | 0.073242 | -0.045776 | -0.059509 | -0.032043 | 0.07782 | 0.022888 | 122.113 | 122.0078 | -0.073242 | 122.0169 | 122.0581 | 0.050354 | 0.064087 | 122.0901 | 122.0352 | -0.073242 | 122.081 | 121.9666 | -0.068664 | -0.045776 | 121.9528 | 122.0901 | 122.0901 | -0.018311 | 121.9528 | 121.9803 | 122.0856 | 0.009155
1546.9844 | 122.2778 | -121.9757 | -0.004578 | 0.0064086 | -0.0046441 | -0.062021 | 0.020988 | -0.012542 | -0.010284 | -0.0054751 | 0.067902 | 0.020059 | 0.023044 | 0.023199 | 0.012311 | 0.019207 | 0.032043 | 0.022888 | 0.10071 | 0.045776 | -0.068665 | 0.10529 | 0.004578 | 0.09613 | 0.10071 | 0.004578 | -0.091553 | -0.064087 | 0.11902 | 0.036621 | 122.081 | 121.9803 | -0.064087 | 121.9986 | 122.0215 | 0.041198 | 0.036621 | 122.0947 | 122.0123 | -0.086975 | 122.0718 | 121.9803 | -0.032043 | -0.059509 | 121.907 | 122.0078 | 122.0764 | 0.009156 | 121.8842 | 121.9116 | 122.0764 | 0.041199
1548.6719 | 122.2366 | -121.9757 | 0.004578 | 0.067444 | -0.0044305 | -0.060099 | 0.018639 | -0.013824 | -0.0055841 | -0.0054751 | 0.098419 | 0.018137 | 0.023471 | 0.021918 | 0.014447 | 0.017712 | 0.068665 | 0.027466 | 0.10529 | 0.045776 | -0.059509 | 0.13275 | 0.009155 | 0.09613 | 0.086975 | 0.004578 | -0.07782 | -0.045776 | 0.10529 | 0.032043 | 122.1085 | 121.9849 | -0.064087 | 122.0032 | 122.0215 | 0.036621 | 0.064087 | 122.081 | 122.0078 | -0.082398 | 122.0718 | 121.9803 | -0.027465 | -0.050354 | 121.9162 | 122.0444 | 122.081 | 0.004577 | 121.8979 | 121.9299 | 122.0627 | 0.027465
1550.3594 | 122.1588 | -122.0444 | 0.009155 | -0.16144 | -0.00079888 | -0.061808 | 0.023338 | -0.012115 | -0.0062249 | -0.0065433 | -0.13809 | 0.020486 | 0.024325 | 0.021063 | 0.013806 | 0.015575 | 0.086975 | 0.059509 | 0.14191 | 0.07782 | -0.09613 | 0.10986 | 0.022888 | 0.10529 | 0.14648 | 0.027466 | -0.082397 | -0.054932 | 0.10071 | 0.045776 | 122.1542 | 122.0673 | -0.10528 | 122.1039 | 122.1222 | 0.054932 | 0.07782 | 122.1451 | 122.0901 | -0.091552 | 122.1497 | 122.0718 | -0.01831 | -0.064087 | 121.9482 | 122.1313 | 122.1863 | 0.013733 | 121.962 | 121.9894 | 122.1909 | 0.036621
1552.1094 | 122.2824 | -121.9711 | -0.004578 | 0.14374 | -0.0040033 | -0.065653 | 0.020561 | -0.01361 | 0.0016791 | -0.0050479 | 0.09079 | 0.0207 | 0.026034 | 0.025122 | 0.015088 | 0.016003 | 0.036621 | -0.041199 | 0.032043 | 0.004578 | -0.054932 | 0.091553 | -0.009155 | 0.086975 | 0.054932 | -0.041199 | -0.068665 | -0.059509 | 0.10071 | 0.009155 | 122.0627 | 121.962 | -0.050354 | 121.9299 | 121.9757 | 0.013733 | 0.041199 | 122.0718 | 121.9803 | -0.064087 | 122.0581 | 121.9299 | -0.050354 | -0.054931 | 121.9162 | 122.0078 | 122.0032 | -0.004577 | 121.9025 | 121.9116 | 122.0261 | 0.013733
1553.7969 | 122.2687 | -121.9803 | 0.009155 | 0.097962 | -0.00037168 | -0.05839 | 0.020775 | -0.0086966 | 0.00061092 | -0.0041933 | 0.075531 | 0.020914 | 0.022403 | 0.024268 | 0.018079 | 0.015789 | 0.027466 | -0.059509 | 0.009155 | 0.009155 | -0.050354 | 0.091553 | -0.013733 | 0.050354 | 0.013733 | -0.07782 | -0.036621 | -0.018311 | 0.082397 | 0.027466 | 122.0718 | 121.9666 | -0.059509 | 121.9208 | 121.9894 | 0.022888 | 0.018311 | 122.0627 | 122.0078 | -0.045776 | 122.0306 | 121.9025 | -0.10529 | -0.027466 | 121.9299 | 122.0078 | 121.9894 | -0.022888 | 121.9437 | 121.962 | 121.994 | 0.018311
1555.5469 | 122.1725 | -122.0215 | 0.018311 | 0.082703 | -0.0018671 | -0.06074 | 0.01992 | -0.011046 | -0.00088448 | -0.0054751 | 0.060272 | 0.023477 | 0.02283 | 0.025763 | 0.01872 | 0.017712 | -0.004578 | -0.10529 | -0.018311 | -0.009155 | -0.041199 | 0.086975 | -0.036621 | 0.018311 | -0.022888 | -0.10529 | -0.050354 | -0.027466 | 0.07782 | 0.022888 | 122.1085 | 121.9849 | -0.05951 | 121.9162 | 122.0123 | 0.027466 | -0.022889 | 122.0993 | 122.0444 | -0.068665 | 122.0398 | 121.9162 | -0.12817 | -0.045777 | 121.9803 | 122.0169 | 122.0032 | -0.054932 | 121.9711 | 121.994 | 121.9986 | 0.004577
1557.2344 | 122.1634 | -122.0169 | 0.041199 | -0.20721 | -0.0014399 | -0.06138 | 0.025688 | -0.011901 | -0.0060113 | -0.0059023 | -0.13046 | 0.020914 | 0.02518 | 0.024268 | 0.013593 | 0.017071 | 0.032043 | 0.022888 | 0.068665 | 0.041199 | -0.068665 | 0.09613 | 0 | 0.018311 | 0.064087 | -0.054932 | -0.050354 | -0.036621 | 0.068665 | 0.013733 | 122.113 | 122.0169 | -0.10986 | 122.0398 | 122.0581 | 0.041199 | -0.009156 | 122.0856 | 122.0306 | -0.091553 | 122.0352 | 121.962 | -0.068665 | -0.07782 | 121.9482 | 122.049 | 122.0856 | -0.041199 | 121.9666 | 121.9803 | 122.081 | -0.027466
1559 | 122.1634 | -122.0398 | 0.027466 | -0.19196 | -0.0033625 | -0.059031 | 0.023766 | -0.012328 | -0.0043023 | -0.0059023 | -0.30594 | 0.021341 | 0.025607 | 0.025336 | 0.011884 | 0.016216 | 0.022888 | -0.004578 | 0.059509 | 0.027466 | -0.064087 | 0.11444 | -0.018311 | 0.045776 | 0.041199 | -0.064087 | -0.050354 | -0.041199 | 0.086975 | -0.004578 | 122.1542 | 122.0215 | -0.091553 | 122.0352 | 122.0673 | 0.045777 | -0.004578 | 122.1268 | 122.0352 | -0.07782 | 122.0856 | 121.9757 | -0.059509 | -0.068665 | 121.9757 | 122.0627 | 122.0993 | -0.045777 | 121.9894 | 121.9986 | 122.081 | -0.032044
1560.7656 | 122.287 | -121.9986 | 0 | 0.021668 | -0.0027215 | -0.060526 | 0.023552 | -0.014892 | -0.0068659 | -0.0056887 | 0.075531 | 0.017923 | 0.026248 | 0.022559 | 0.012525 | 0.016857 | 0.022888 | 0.022888 | 0.091553 | 0.041199 | -0.086975 | 0.1236 | 0.009155 | 0.073242 | 0.068665 | -0.004578 | -0.082397 | -0.050354 | 0.09613 | 0.027466 | 122.1222 | 122.0078 | -0.086975 | 122.0215 | 122.0398 | 0.032044 | 0.022888 | 122.0947 | 122.0261 | -0.082397 | 122.0718 | 121.994 | -0.032044 | -0.050354 | 121.9116 | 122.0215 | 122.0901 | 0.009155 | 121.9162 | 121.9482 | 122.0673 | 0.027466
1562.4688 | 122.2229 | -122.0398 | 0.036621 | -0.14618 | -0.0022943 | -0.062021 | 0.020775 | -0.010406 | 0.00061092 | -0.0041933 | -0.20676 | 0.021768 | 0.02283 | 0.025336 | 0.017011 | 0.014294 | 0.013733 | -0.054932 | 0.027466 | 0.022888 | -0.054932 | 0.091553 | -0.032043 | 0.013733 | 0.041199 | -0.064087 | -0.050354 | -0.036621 | 0.082397 | 0.036621 | 122.1313 | 122.0078 | -0.091553 | 121.9849 | 122.0627 | 0.054931 | -0.022888 | 122.1222 | 122.0764 | -0.086975 | 122.0535 | 121.9757 | -0.10071 | -0.073242 | 121.9849 | 122.0535 | 122.0673 | -0.068664 | 121.9894 | 122.0032 | 122.081 | 0
1564.2188 | 122.2641 | -122.0169 | -0.013733 | 0.052185 | -0.0069941 | -0.058603 | 0.021202 | -0.014251 | -0.0064387 | -0.0035525 | 0.067902 | 0.019418 | 0.02283 | 0.021918 | 0.01402 | 0.017925 | 0.045776 | 0.041199 | 0.10071 | 0.032043 | -0.091553 | 0.1236 | 0.013733 | 0.07782 | 0.073242 | -0.013733 | -0.07782 | -0.045776 | 0.09613 | 0.032043 | 122.1405 | 122.0306 | -0.07782 | 122.0581 | 122.049 | 0.01831 | 0.059509 | 122.113 | 122.049 | -0.064087 | 122.0947 | 122.0032 | -0.045776 | -0.032043 | 121.9254 | 122.0627 | 122.1176 | 0.027466 | 121.9391 | 121.9711 | 122.0901 | 0.045776
1565.9062 | 122.1725 | -122.0673 | 0.036621 | -0.16144 | -0.0033625 | -0.058817 | 0.023552 | -0.013396 | -0.0032343 | -0.0063297 | -0.19913 | 0.021555 | 0.026462 | 0.022131 | 0.014447 | 0.017712 | 0 | 0.004578 | 0.041199 | -0.004578 | -0.050354 | 0.073242 | -0.013733 | 0.013733 | 0.032043 | -0.064087 | -0.054932 | -0.027466 | 0.068665 | 0.004578 | 122.1405 | 122.0535 | -0.086975 | 122.0718 | 122.0627 | 0.009155 | -0.036621 | 122.1359 | 122.0718 | -0.091553 | 122.081 | 122.0032 | -0.068665 | -0.064087 | 122.0169 | 122.0673 | 122.1085 | -0.050354 | 122.0123 | 122.0398 | 122.0993 | -0.032043
1567.6562 | 122.2504 | -121.9894 | 0.027466 | 0.13611 | -0.0033625 | -0.060099 | 0.019707 | -0.01361 | -2.988e-05 | -0.0048343 | 0.037384 | 0.020059 | 0.023044 | 0.023627 | 0.018506 | 0.016643 | 0.022888 | -0.068665 | -0.004578 | 0 | -0.036621 | 0.07782 | -0.027466 | 0.036621 | -0.004578 | -0.10071 | -0.050354 | -0.041199 | 0.073242 | -0.004578 | 122.0673 | 121.962 | -0.064087 | 121.9208 | 121.9894 | 0.027466 | -0.004578 | 122.0627 | 121.9849 | -0.07782 | 122.0261 | 121.8887 | -0.09613 | -0.068665 | 121.9528 | 122.0123 | 121.9849 | -0.054932 | 121.9391 | 121.9482 | 121.9849 | -0.032044
1569.4219 | 122.2595 | -122.0352 | -0.004578 | 0.11322 | 0.0019781 | -0.060953 | 0.021629 | -0.010619 | -0.00045708 | -0.0039797 | 0.067902 | 0.020486 | 0.026675 | 0.023627 | 0.015943 | 0.015362 | 0.009155 | -0.059509 | 0.009155 | -0.013733 | -0.041199 | 0.10529 | -0.013733 | 0.036621 | 0 | -0.07782 | -0.045776 | -0.041199 | 0.091553 | 0.032043 | 122.1405 | 122.0215 | -0.036621 | 121.9757 | 122.0215 | 0 | 0.013733 | 122.1268 | 122.0673 | -0.041198 | 122.0718 | 121.9574 | -0.10986 | -0.036621 | 121.994 | 122.0444 | 122.0444 | -0.009155 | 121.9894 | 121.994 | 122.0352 | 0.036621
1571.1719 | 122.3053 | -122.0261 | -0.004578 | -0.085144 | -0.0020807 | -0.059031 | 0.02462 | -0.011046 | -0.0083613 | -0.0056887 | -0.084686 | 0.017709 | 0.024539 | 0.024268 | 0.011243 | 0.017498 | 0.068665 | 0.12817 | 0.16937 | 0.086975 | -0.07782 | 0.13733 | 0.018311 | 0.13275 | 0.17395 | 0.059509 | -0.09613 | -0.064087 | 0.13275 | 0.045776 | 122.1634 | 122.0444 | -0.073242 | 122.1542 | 122.113 | 0.068664 | 0.073243 | 122.1588 | 122.0718 | -0.091552 | 122.1588 | 122.0856 | 0.013733 | -0.059509 | 121.9482 | 122.0947 | 122.1954 | 0.022889 | 121.9299 | 121.962 | 122.2 | 0.050354
1572.9219 | 122.319 | -122.0306 | 0.013733 | -0.077515 | -0.0042169 | -0.057535 | 0.023766 | -0.01126 | -0.0077203 | -0.0071841 | -0.061798 | 0.017496 | 0.024112 | 0.022345 | 0.01402 | 0.015362 | 0.082397 | 0.11902 | 0.15564 | 0.07782 | -0.073242 | 0.13275 | -0.004578 | 0.15106 | 0.16479 | 0.086975 | -0.082397 | -0.068665 | 0.11444 | 0.036621 | 122.1634 | 122.0261 | -0.086975 | 122.1497 | 122.1085 | 0.082398 | 0.068664 | 122.1451 | 122.0673 | -0.09613 | 122.1817 | 122.1176 | 0.050354 | -0.082398 | 121.9574 | 122.113 | 122.1863 | -0.018311 | 121.9482 | 121.962 | 122.1954 | 0.022888
1574.6719 | 122.2275 | -122.0627 | 0.027466 | -0.1767 | -0.0029351 | -0.058817 | 0.023766 | -0.012969 | -0.0055841 | -0.0050479 | -0.10757 | 0.018991 | 0.025607 | 0.022772 | 0.015729 | 0.015362 | 0.086975 | 0.082397 | 0.15106 | 0.068665 | -0.073242 | 0.1236 | 0.013733 | 0.11444 | 0.16479 | 0.027466 | -0.086975 | -0.054932 | 0.09613 | 0.036621 | 122.1863 | 122.0764 | -0.10071 | 122.1451 | 122.1313 | 0.054932 | 0.059509 | 122.1588 | 122.0993 | -0.11444 | 122.1771 | 122.0901 | -0.009155 | -0.082398 | 121.9894 | 122.1497 | 122.2137 | -0.013733 | 121.9757 | 122.0078 | 122.2275 | 0.009155
1576.3594 | 122.319 | -122.0123 | 0 | -0.11566 | -0.0050715 | -0.058817 | 0.02227 | -0.011474 | -0.0070795 | -0.0052615 | -0.069428 | 0.018777 | 0.020694 | 0.023413 | 0.01402 | 0.015575 | 0.07782 | 0.073242 | 0.13733 | 0.091553 | -0.064087 | 0.10986 | 0.022888 | 0.16022 | 0.16022 | 0.059509 | -0.082397 | -0.07782 | 0.10529 | 0.045776 | 122.1222 | 122.0352 | -0.064087 | 122.0856 | 122.1039 | 0.068665 | 0.07782 | 122.1176 | 122.0581 | -0.082397 | 122.1725 | 122.0718 | 0.013733 | -0.07782 | 121.9482 | 122.0901 | 122.1497 | 0.022888 | 121.9299 | 121.9345 | 122.1725 | 0.045776
1578.0938 | 122.1817 | -122.0673 | 0.032043 | -0.0088499 | 5.5518e-05 | -0.062662 | 0.021202 | -0.011474 | 0.0018927 | -0.0026981 | -0.03891 | 0.021341 | 0.025393 | 0.02384 | 0.017011 | 0.014507 | 0.032043 | -0.009155 | 0.032043 | 0.004578 | -0.050354 | 0.068665 | 0.004578 | 0.032043 | 0.004578 | -0.10529 | -0.045776 | -0.036621 | 0.09613 | 0.004578 | 122.1359 | 122.0718 | -0.082397 | 122.0581 | 122.0718 | 0 | 0 | 122.1634 | 122.0718 | -0.077819 | 122.0993 | 121.962 | -0.10986 | -0.068664 | 122.0169 | 122.0993 | 122.0993 | -0.027465 | 122.0215 | 122.0306 | 122.0718 | -0.027465
1579.8594 | 122.3236 | -122.0215 | 0.004578 | 0.11322 | -0.0035761 | -0.062448 | 0.020134 | -0.01126 | -0.0013117 | -0.0048343 | 0.13657 | 0.019846 | 0.022189 | 0.024481 | 0.017438 | 0.014934 | 0.022888 | -0.013733 | 0.045776 | 0.027466 | -0.032043 | 0.10071 | 0 | 0.086975 | 0.036621 | -0.022888 | -0.059509 | -0.054932 | 0.07782 | 0.036621 | 122.1222 | 122.0215 | -0.036621 | 122.0078 | 122.049 | 0.027466 | 0.01831 | 122.0993 | 122.0581 | -0.064087 | 122.1085 | 121.9986 | -0.059509 | -0.05951 | 121.9894 | 122.0444 | 122.0673 | -0.004578 | 121.962 | 121.9666 | 122.0581 | 0.032043
1581.5469 | 122.3007 | -122.0444 | 0.009155 | 0.12085 | -0.0020807 | -0.059031 | 0.021416 | -0.01126 | 0.00018372 | -0.0020571 | 0.067902 | 0.017923 | 0.020053 | 0.024268 | 0.018293 | 0.01643 | 0.004578 | -0.054932 | 0.013733 | 0 | -0.036621 | 0.086975 | -0.022888 | 0.032043 | -0.009155 | -0.082397 | -0.032043 | -0.036621 | 0.091553 | 0.004578 | 122.1313 | 122.0215 | -0.045776 | 121.9894 | 122.0444 | 0.022888 | -0.004577 | 122.1359 | 122.049 | -0.041198 | 122.0764 | 121.962 | -0.086975 | -0.045776 | 122.0078 | 122.049 | 122.0581 | -0.032043 | 122.0123 | 122.0078 | 122.0352 | -0.004577
1583.2969 | 122.3053 | -122.0352 | -0.004578 | 0.097962 | -0.0044305 | -0.057962 | 0.021416 | -0.01361 | -0.0013117 | -0.0044071 | 0.11368 | 0.019846 | 0.018344 | 0.023199 | 0.01637 | 0.016216 | 0.004578 | -0.054932 | 0.009155 | 0.009155 | -0.036621 | 0.09613 | -0.027466 | 0.045776 | 0 | -0.064087 | -0.041199 | -0.027466 | 0.10529 | 0.027466 | 122.1313 | 122.0078 | -0.032043 | 121.9803 | 122.0444 | 0.036621 | 0.009156 | 122.1405 | 122.0627 | -0.036621 | 122.081 | 121.9711 | -0.091553 | -0.022888 | 121.9986 | 122.0398 | 122.0444 | -0.022888 | 121.994 | 122.0078 | 122.0352 | 0.032044
1585 | 122.2137 | -122.0993 | 0.027466 | -0.15381 | -0.0014399 | -0.06074 | 0.024834 | -0.012755 | -0.0064387 | -0.0050479 | -0.12283 | 0.015146 | 0.019412 | 0.023413 | 0.014661 | 0.01643 | 0.082397 | 0.07782 | 0.15106 | 0.082397 | -0.07782 | 0.11902 | 0.004578 | 0.082397 | 0.13733 | 0.018311 | -0.086975 | -0.059509 | 0.10986 | 0.050354 | 122.2183 | 122.1039 | -0.10529 | 122.1771 | 122.1817 | 0.077819 | 0.054931 | 122.2092 | 122.1497 | -0.11444 | 122.1817 | 122.1176 | -0.032043 | -0.086975 | 122.0215 | 122.1817 | 122.2504 | -0.022888 | 122.0123 | 122.0398 | 122.2366 | 0.022888
1586.7656 | 122.3007 | -122.049 | 0.004578 | 0.14374 | -0.0012263 | -0.062021 | 0.021416 | -0.014678 | -0.0028071 | -0.0041933 | 0.16708 | 0.014932 | 0.017703 | 0.021063 | 0.015515 | 0.015148 | 0.10529 | 0.059509 | 0.15106 | 0.086975 | -0.086975 | 0.13275 | 0.041199 | 0.12817 | 0.13733 | 0.032043 | -0.086975 | -0.082397 | 0.11902 | 0.041199 | 122.1817 | 122.0901 | -0.091553 | 122.1085 | 122.1359 | 0.045776 | 0.10071 | 122.168 | 122.0901 | -0.091553 | 122.1771 | 122.081 | -0.009156 | -0.086975 | 121.962 | 122.1542 | 122.2 | 0.036621 | 121.962 | 121.9666 | 122.1863 | 0.036621
1588.5156 | 122.2 | -122.0947 | 0.018311 | -0.024109 | 0.0013373 | -0.064157 | 0.022697 | -0.011901 | 0.0029607 | -0.0046207 | 0.0068663 | 0.018564 | 0.021548 | 0.024481 | 0.018079 | 0.014934 | 0.041199 | -0.027466 | 0.041199 | 0.022888 | -0.045776 | 0.091553 | -0.004578 | 0.032043 | -0.004578 | -0.10071 | -0.054932 | -0.041199 | 0.054932 | 0.009155 | 122.1863 | 122.0901 | -0.064087 | 122.0673 | 122.1176 | 0.027466 | 0.022888 | 122.1497 | 122.1039 | -0.073243 | 122.1268 | 121.994 | -0.10986 | -0.05951 | 122.049 | 122.1359 | 122.1359 | -0.022889 | 122.0398 | 122.0535 | 122.0901 | -0.009156
1590.2656 | 122.2549 | -122.0581 | 0.018311 | -0.077515 | 0.00069632 | -0.064371 | 0.022911 | -0.013396 | 0.00039732 | -0.0033389 | -0.10757 | 0.017282 | 0.020053 | 0.024695 | 0.012952 | 0.014721 | 0.068665 | -0.009155 | 0.059509 | 0.036621 | -0.050354 | 0.10529 | -0.009155 | 0.064087 | 0.073242 | -0.045776 | -0.054932 | -0.041199 | 0.10986 | 0.036621 | 122.1634 | 122.0489 | -0.068665 | 122.0489 | 122.0947 | 0.045776 | 0.050354 | 122.168 | 122.0947 | -0.073243 | 122.1222 | 122.0123 | -0.082397 | -0.05951 | 122.0078 | 122.1268 | 122.1176 | -0.027466 | 122.0032 | 122.0169 | 122.1313 | 0.01831
1592.0156 | 122.3099 | -122.0581 | -0.009155 | 0.159 | -0.0031489 | -0.062235 | 0.020775 | -0.010192 | -0.0070795 | -0.0039797 | 0.17471 | 0.014932 | 0.020053 | 0.020636 | 0.014447 | 0.015362 | 0.09613 | 0.073242 | 0.14191 | 0.073242 | -0.091553 | 0.11902 | 0.018311 | 0.14191 | 0.13733 | 0.036621 | -0.09613 | -0.073242 | 0.13275 | 0.064087 | 122.1771 | 122.0764 | -0.082398 | 122.1313 | 122.1313 | 0.054931 | 0.10528 | 122.1909 | 122.1222 | -0.086975 | 122.2 | 122.0947 | -0.027466 | -0.064087 | 121.9666 | 122.1542 | 122.2 | 0.027466 | 121.962 | 121.9849 | 122.1954 | 0.073242
1593.7188 | 122.2916 | -122.0581 | 0 | 0.075073 | -0.0016535 | -0.061167 | 0.025475 | -0.01361 | -0.0079339 | -0.0080387 | 0.1442 | 0.014078 | 0.021975 | 0.02149 | 0.011457 | 0.015148 | 0.059509 | 0.036621 | 0.10529 | 0.041199 | -0.091553 | 0.11902 | 0.041199 | 0.09613 | 0.082397 | -0.009155 | -0.082397 | -0.050354 | 0.10986 | 0.027466 | 122.1771 | 122.0993 | -0.091553 | 122.0947 | 122.0993 | 0 | 0.059509 | 122.168 | 122.0856 | -0.082397 | 122.1542 | 122.0489 | -0.036621 | -0.050354 | 121.9666 | 122.1176 | 122.1634 | 0.041199 | 121.9757 | 122.0078 | 122.1405 | 0.027466
1595.4844 | 122.3648 | -122.0581 | 0 | -0.0012209 | -0.0042169 | -0.062021 | 0.019707 | -0.010406 | -0.0072931 | -0.0046207 | 0.022125 | 0.013437 | 0.018771 | 0.024054 | 0.013806 | 0.015575 | 0.050354 | 0.009155 | 0.09613 | 0.064087 | -0.064087 | 0.1236 | 0.013733 | 0.086975 | 0.10529 | 0.013733 | -0.073242 | -0.059509 | 0.10529 | 0.041199 | 122.1817 | 122.0718 | -0.064087 | 122.0673 | 122.1222 | 0.050354 | 0.050354 | 122.1634 | 122.0993 | -0.073242 | 122.1451 | 122.0718 | -0.027466 | -0.059509 | 121.994 | 122.1085 | 122.1542 | 0.013733 | 121.9849 | 121.9986 | 122.1634 | 0.041199
1597.2344 | 122.2275 | -122.081 | 0.032043 | 0.036926 | 0.00048272 | -0.065012 | 0.01992 | -0.012115 | 0.0036017 | -0.0037661 | 0.0068663 | 0.016855 | 0.021975 | 0.025122 | 0.019147 | 0.015575 | 0.032043 | -0.068665 | 0.013733 | 0.004578 | -0.054932 | 0.09613 | -0.032043 | 0.013733 | -0.018311 | -0.11902 | -0.032043 | -0.041199 | 0.082397 | 0.004578 | 122.1771 | 122.049 | -0.086975 | 122.0123 | 122.0856 | 0.036621 | 0 | 122.1634 | 122.0856 | -0.064086 | 122.0947 | 121.962 | -0.1236 | -0.073242 | 122.0261 | 122.113 | 122.0947 | -0.064086 | 122.049 | 122.0398 | 122.0627 | -0.027465
1599 | 122.3465 | -122.0398 | -0.013733 | 0.14374 | -0.0012263 | -0.061167 | 0.019707 | -0.012969 | -0.0025935 | -0.0029117 | 0.12131 | 0.017282 | 0.017917 | 0.023627 | 0.015729 | 0.013225 | 0.045776 | -0.004578 | 0.073242 | 0.036621 | -0.064087 | 0.11444 | 0 | 0.1236 | 0.07782 | 0.009155 | -0.07782 | -0.068665 | 0.10071 | 0.036621 | 122.1542 | 122.0398 | -0.050354 | 122.0352 | 122.0764 | 0.036621 | 0.059509 | 122.1405 | 122.0764 | -0.064087 | 122.1634 | 122.049 | -0.027466 | -0.054932 | 121.9757 | 122.0856 | 122.113 | 0.013733 | 121.962 | 121.9711 | 122.1176 | 0.050354
1600.6875 | 122.3373 | -122.0535 | -0.009155 | 0.159 | -0.0025079 | -0.061167 | 0.019066 | -0.011046 | -0.0032343 | -0.0033389 | 0.17471 | 0.014078 | 0.017489 | 0.022772 | 0.017224 | 0.016857 | 0.07782 | 0.022888 | 0.10986 | 0.059509 | -0.068665 | 0.12817 | 0.009155 | 0.13275 | 0.10529 | 0.018311 | -0.07782 | -0.064087 | 0.13275 | 0.036621 | 122.1817 | 122.0627 | -0.05951 | 122.0764 | 122.113 | 0.050354 | 0.086975 | 122.1863 | 122.0901 | -0.068665 | 122.1863 | 122.0718 | -0.01831 | -0.054932 | 121.9849 | 122.1313 | 122.1634 | 0.01831 | 121.9757 | 121.9894 | 122.1588 | 0.045776
1602.4531 | 122.3511 | -122.0673 | 0.013733 | -0.031738 | -0.0040033 | -0.060099 | 0.025047 | -0.0091238 | -0.0079339 | -0.0052615 | -0.054169 | 0.014932 | 0.018985 | 0.022131 | 0.01167 | 0.016857 | 0.068665 | 0.050354 | 0.1236 | 0.07782 | -0.082397 | 0.10986 | 0.009155 | 0.13275 | 0.13733 | 0.059509 | -0.073242 | -0.068665 | 0.11444 | 0.036621 | 122.1771 | 122.0764 | -0.09613 | 122.1176 | 122.1451 | 0.068665 | 0.054932 | 122.1817 | 122.1039 | -0.086975 | 122.2 | 122.1268 | 0.022888 | -0.082398 | 121.9849 | 122.1359 | 122.1909 | -0.004578 | 121.994 | 121.9986 | 122.2046 | 0.022888
1604.2031 | 122.2412 | -122.1405 | 0.027466 | -0.0012209 | 0.00048272 | -0.059671 | 0.021416 | -0.013396 | 0.0018927 | -0.0069705 | 0.045013 | 0.017709 | 0.022189 | 0.02384 | 0.016797 | 0.015575 | 0.027466 | -0.050354 | 0.036621 | 0.009155 | -0.068665 | 0.10071 | -0.022888 | 0.018311 | -0.009155 | -0.10529 | -0.054932 | -0.036621 | 0.082397 | -0.009155 | 122.2412 | 122.1176 | -0.096131 | 122.0901 | 122.1497 | 0.032043 | 0 | 122.2229 | 122.1313 | -0.082398 | 122.1588 | 122.0352 | -0.096131 | -0.064087 | 122.0718 | 122.168 | 122.1771 | -0.050354 | 122.0856 | 122.1039 | 122.1313 | -0.036621
1605.9531 | 122.2595 | -122.0901 | 0.027466 | 0.075073 | -0.00015808 | -0.061808 | 0.019066 | -0.01126 | 0.00039732 | -0.0037661 | 0.037384 | 0.019205 | 0.019839 | 0.024268 | 0.01637 | 0.017712 | -0.009155 | -0.10529 | -0.013733 | 0 | -0.041199 | 0.10986 | -0.004578 | 0 | -0.022888 | -0.10986 | -0.045776 | -0.027466 | 0.07782 | 0.009155 | 122.2 | 122.0856 | -0.068665 | 121.9849 | 122.0901 | 0.004578 | -0.036621 | 122.168 | 122.0993 | -0.073242 | 122.0901 | 121.9803 | -0.11902 | -0.054932 | 122.0489 | 122.081 | 122.0764 | -0.032044 | 122.0444 | 122.0627 | 122.0673 | -0.018311
1607.7031 | 122.2595 | -122.1268 | 0.027466 | -0.13092 | -0.0046441 | -0.06138 | 0.02462 | -0.013183 | -0.0066523 | -0.0048343 | -0.13046 | 0.014932 | 0.020267 | 0.02085 | 0.011884 | 0.015148 | 0.073242 | 0.064087 | 0.14191 | 0.07782 | -0.091553 | 0.12817 | 0 | 0.082397 | 0.13733 | 0.018311 | -0.086975 | -0.050354 | 0.10986 | 0.036621 | 122.2549 | 122.1268 | -0.11902 | 122.1909 | 122.2046 | 0.07782 | 0.045776 | 122.2366 | 122.1634 | -0.11444 | 122.2092 | 122.1451 | -0.01831 | -0.07782 | 122.0352 | 122.2 | 122.2687 | -0.027466 | 122.0398 | 122.0764 | 122.2641 | 0.009155
1609.4688 | 122.3145 | -122.113 | 0.009155 | -0.13092 | -0.00058528 | -0.060953 | 0.025261 | -0.011046 | -0.0064387 | -0.0063297 | -0.12283 | 0.012582 | 0.02048 | 0.022772 | 0.012097 | 0.016857 | 0.082397 | 0.086975 | 0.15106 | 0.082397 | -0.068665 | 0.11902 | 0.013733 | 0.11902 | 0.17395 | 0.059509 | -0.082397 | -0.068665 | 0.1236 | 0.050354 | 122.2321 | 122.1268 | -0.07782 | 122.2 | 122.1954 | 0.068664 | 0.073242 | 122.2366 | 122.1634 | -0.091552 | 122.2321 | 122.1725 | 0.009155 | -0.07782 | 122.0444 | 122.1954 | 122.2641 | 0.004578 | 122.0306 | 122.0444 | 122.287 | 0.041199
1611.1719 | 122.2916 | -122.0993 | 0.013733 | -0.085144 | -0.0010125 | -0.061594 | 0.020348 | -0.010406 | 0.0014655 | -0.0033389 | -0.13046 | 0.015787 | 0.018985 | 0.022131 | 0.017011 | 0.013225 | 0.059509 | 0 | 0.068665 | 0.036621 | -0.041199 | 0.086975 | -0.004578 | 0.073242 | 0.068665 | -0.041199 | -0.064087 | -0.032043 | 0.086975 | 0.018311 | 122.1863 | 122.0947 | -0.054932 | 122.0993 | 122.1359 | 0.041199 | 0.045776 | 122.1863 | 122.1176 | -0.07782 | 122.1725 | 122.0581 | -0.05951 | -0.045776 | 122.0581 | 122.1588 | 122.168 | -0.018311 | 122.0352 | 122.0673 | 122.168 | 0.004578
1612.9375 | 122.3511 | -122.0993 | 0.018311 | -0.14618 | -0.0035761 | -0.06074 | 0.025902 | -0.010406 | -0.0075067 | -0.0033389 | -0.10757 | 0.012796 | 0.020694 | 0.022345 | 0.010389 | 0.016857 | 0.086975 | 0.10529 | 0.15106 | 0.09613 | -0.07782 | 0.10529 | 0.036621 | 0.11444 | 0.17395 | 0.054932 | -0.091553 | -0.07782 | 0.10529 | 0.036621 | 122.2046 | 122.1359 | -0.096131 | 122.2046 | 122.1954 | 0.059509 | 0.068664 | 122.2046 | 122.1359 | -0.10986 | 122.2137 | 122.1542 | 0.018311 | -0.096131 | 122.0215 | 122.1863 | 122.2504 | 0.01831 | 122.0078 | 122.0215 | 122.2733 | 0.01831
1614.6406 | 122.2961 | -122.1176 | 0.041199 | -0.19196 | -0.00058528 | -0.062021 | 0.024834 | -0.012328 | -0.0036615 | -0.0061161 | -0.20676 | 0.016641 | 0.021121 | 0.025336 | 0.012311 | 0.017284 | -0.004578 | -0.041199 | 0.013733 | -0.013733 | -0.036621 | 0.073242 | -0.022888 | 0.009155 | 0.022888 | -0.09613 | -0.045776 | -0.027466 | 0.064087 | -0.018311 | 122.1909 | 122.0947 | -0.07782 | 122.0764 | 122.1039 | 0.009155 | -0.045777 | 122.1817 | 122.0993 | -0.086975 | 122.1268 | 122.0215 | -0.077819 | -0.068665 | 122.081 | 122.113 | 122.1313 | -0.064087 | 122.0718 | 122.0901 | 122.1405 | -0.05951
1616.4062 | 122.3419 | -122.0901 | -0.009155 | 0.15137 | -0.0033625 | -0.059885 | 0.017998 | -0.013824 | -0.0034479 | -0.0012027 | 0.15182 | 0.015787 | 0.020053 | 0.022345 | 0.015088 | 0.016643 | 0.082397 | 0.082397 | 0.13733 | 0.073242 | -0.091553 | 0.12817 | 0.032043 | 0.13275 | 0.13733 | 0.045776 | -0.09613 | -0.059509 | 0.10986 | 0.036621 | 122.2183 | 122.1222 | -0.082398 | 122.1725 | 122.1634 | 0.041199 | 0.091552 | 122.2 | 122.1268 | -0.086975 | 122.2229 | 122.1359 | 0.009155 | -0.050354 | 121.9986 | 122.1725 | 122.2275 | 0.041198 | 121.994 | 122.0306 | 122.2275 | 0.045776
1618.0938 | 122.3831 | -122.0673 | -0.022888 | 0.11322 | -0.0027215 | -0.062235 | 0.019707 | -0.01126 | 0.00061092 | -0.0037661 | 0.12131 | 0.017709 | 0.019198 | 0.022131 | 0.01872 | 0.016003 | 0.032043 | -0.041199 | 0.018311 | 0.009155 | -0.032043 | 0.086975 | 0.009155 | 0.064087 | 0.022888 | -0.045776 | -0.054932 | -0.041199 | 0.10071 | 0.036621 | 122.1542 | 122.0764 | -0.009155 | 122.0261 | 122.0764 | 0 | 0.054931 | 122.168 | 122.1039 | -0.032044 | 122.1313 | 122.0215 | -0.082397 | -0.018311 | 122.0352 | 122.0993 | 122.0856 | 0.032043 | 122.0123 | 122.0261 | 122.0901 | 0.059509
1619.8438 | 122.3694 | -122.0901 | -0.013733 | 0.097962 | -0.0016535 | -0.062021 | 0.019066 | -0.014464 | -0.0023797 | -0.0037661 | 0.098419 | 0.017282 | 0.017703 | 0.024481 | 0.016156 | 0.017712 | 0.009155 | -0.045776 | 0.018311 | 0.004578 | -0.036621 | 0.086975 | -0.009155 | 0.059509 | 0.004578 | -0.07782 | -0.068665 | -0.045776 | 0.082397 | 0.022888 | 122.1771 | 122.081 | -0.022888 | 122.0444 | 122.0947 | 0.013733 | 0.022888 | 122.1725 | 122.113 | -0.054932 | 122.1497 | 122.0123 | -0.10071 | -0.032043 | 122.0535 | 122.0993 | 122.1085 | 0.004578 | 122.0215 | 122.0444 | 122.0947 | 0.036621
1621.6094 | 122.3602 | -122.1039 | 0.009155 | 0.036926 | -0.0035761 | -0.06074 | 0.022057 | -0.014678 | -0.0066523 | -0.0052615 | 0.067902 | 0.014719 | 0.018344 | 0.022345 | 0.012952 | 0.01643 | 0.032043 | 0 | 0.10071 | 0.050354 | -0.07782 | 0.11444 | -0.013733 | 0.073242 | 0.07782 | -0.013733 | -0.073242 | -0.054932 | 0.09613 | 0.041199 | 122.2183 | 122.0901 | -0.086975 | 122.1039 | 122.1542 | 0.064087 | 0.022888 | 122.2 | 122.1451 | -0.082397 | 122.1771 | 122.0901 | -0.054932 | -0.064087 | 122.0261 | 122.1359 | 122.2046 | -0.022888 | 122.0306 | 122.049 | 122.1817 | 0.032044
1623.3594 | 122.2778 | -122.1405 | 0.018311 | -0.19958 | -0.0035761 | -0.060312 | 0.022057 | -0.013183 | -0.0021661 | -0.0039797 | -0.14572 | 0.014291 | 0.017917 | 0.024695 | 0.014661 | 0.015575 | 0.004578 | -0.018311 | 0.036621 | 0 | -0.041199 | 0.09613 | -0.022888 | 0.004578 | 0.041199 | -0.07782 | -0.041199 | -0.041199 | 0.07782 | 0.022888 | 122.2366 | 122.1176 | -0.05951 | 122.1222 | 122.1405 | 0.022888 | -0.013733 | 122.2183 | 122.1634 | -0.05951 | 122.1451 | 122.0627 | -0.10071 | -0.05951 | 122.0993 | 122.1451 | 122.1771 | -0.041199 | 122.0993 | 122.0993 | 122.1817 | 0.004577
1625.0469 | 122.2778 | -122.113 | 0.045776 | -0.031738 | 5.5518e-05 | -0.063303 | 0.025047 | -0.012328 | 0.0016791 | -0.0050479 | -0.12283 | 0.014291 | 0.022403 | 0.022345 | 0.019147 | 0.013653 | 0.073242 | 0.013733 | 0.068665 | 0.041199 | -0.054932 | 0.082397 | 0 | 0.086975 | 0.07782 | -0.041199 | -0.045776 | -0.036621 | 0.09613 | 0.022888 | 122.1954 | 122.113 | -0.10071 | 122.1268 | 122.1542 | 0.041199 | 0.027466 | 122.2092 | 122.1359 | -0.091552 | 122.2 | 122.0718 | -0.064087 | -0.082397 | 122.0581 | 122.1863 | 122.1817 | -0.045776 | 122.0673 | 122.0764 | 122.1909 | -0.022888
1626.7969 | 122.3145 | -122.1313 | 0.022888 | -0.16907 | 0.0026191 | -0.059885 | 0.021416 | -0.010619 | -0.00067088 | -0.0048343 | -0.16098 | 0.016855 | 0.021121 | 0.023413 | 0.016584 | 0.017071 | 0.018311 | -0.027466 | 0.045776 | 0.027466 | -0.050354 | 0.091553 | -0.032043 | 0.036621 | 0.07782 | -0.045776 | -0.059509 | -0.041199 | 0.07782 | 0.018311 | 122.2229 | 122.0993 | -0.073242 | 122.1039 | 122.1588 | 0.059509 | -0.004577 | 122.2092 | 122.1497 | -0.082397 | 122.168 | 122.0856 | -0.064087 | -0.064087 | 122.081 | 122.1497 | 122.1771 | -0.054931 | 122.0718 | 122.0901 | 122.2092 | -0.004577
1628.5469 | 122.3877 | -122.113 | -0.004578 | 0.159 | -0.0010125 | -0.061167 | 0.020134 | -0.012755 | -0.0036615 | -0.0039797 | 0.1976 | 0.015146 | 0.020053 | 0.023627 | 0.016156 | 0.016643 | 0.091553 | 0.07782 | 0.15106 | 0.082397 | -0.082397 | 0.11902 | 0.004578 | 0.13275 | 0.12817 | 0.041199 | -0.09613 | -0.068665 | 0.12817 | 0.050354 | 122.2321 | 122.1176 | -0.077819 | 122.1909 | 122.1954 | 0.077819 | 0.096131 | 122.2412 | 122.1634 | -0.091552 | 122.2458 | 122.1542 | -0.009155 | -0.064087 | 122.0306 | 122.2046 | 122.2641 | 0.009156 | 122.0169 | 122.0444 | 122.2412 | 0.054932
1630.3125 | 122.3236 | -122.1222 | 0.022888 | -0.062256 | 0.00091012 | -0.060099 | 0.020775 | -0.013396 | -0.0025935 | -0.0037661 | -0.12283 | 0.016855 | 0.017276 | 0.02384 | 0.017224 | 0.016643 | 0.050354 | 0.004578 | 0.054932 | 0.036621 | -0.045776 | 0.073242 | -0.022888 | 0.059509 | 0.073242 | -0.050354 | -0.045776 | -0.045776 | 0.09613 | 0.032043 | 122.1954 | 122.0993 | -0.068664 | 122.1268 | 122.1588 | 0.059509 | 0.027466 | 122.2183 | 122.1542 | -0.068664 | 122.1817 | 122.0718 | -0.082397 | -0.068664 | 122.0764 | 122.1725 | 122.1771 | -0.045776 | 122.0764 | 122.0764 | 122.1954 | 0.009155
1632.0625 | 122.3648 | -122.1176 | 0 | 0.17426 | -0.0025079 | -0.062876 | 0.018852 | -0.010833 | -0.0045161 | -0.0039797 | 0.17471 | 0.014719 | 0.017489 | 0.022131 | 0.015943 | 0.017284 | 0.091553 | 0.082397 | 0.15564 | 0.07782 | -0.09613 | 0.13275 | 0.013733 | 0.13275 | 0.13275 | 0.045776 | -0.091553 | -0.068665 | 0.10986 | 0.050354 | 122.2504 | 122.1313 | -0.09613 | 122.2 | 122.1954 | 0.064087 | 0.091553 | 122.2275 | 122.168 | -0.091553 | 122.2504 | 122.1634 | -0.004578 | -0.068665 | 122.0215 | 122.2092 | 122.2733 | 0.013733 | 122.0261 | 122.049 | 122.2504 | 0.050354
1633.75 | 122.2916 | -122.1497 | 0.013733 | 0.075073 | -0.00037168 | -0.06074 | 0.01992 | -0.013183 | 0.00039732 | -0.0020571 | 0.037384 | 0.017496 | 0.019412 | 0.022345 | 0.017011 | 0.017071 | -0.013733 | -0.09613 | 0 | -0.018311 | -0.032043 | 0.086975 | -0.027466 | 0.004578 | -0.004578 | -0.11902 | -0.059509 | -0.036621 | 0.068665 | 0.004578 | 122.2366 | 122.1222 | -0.045776 | 122.0535 | 122.1313 | 0.009155 | -0.027466 | 122.2183 | 122.1542 | -0.073242 | 122.1542 | 122.0306 | -0.1236 | -0.050354 | 122.1176 | 122.1359 | 122.1497 | -0.041199 | 122.0901 | 122.113 | 122.1451 | -0.009155
1635.5156 | 122.287 | -122.1359 | 0.027466 | 0.082703 | -0.0020807 | -0.063089 | 0.021843 | -0.014892 | -0.0013117 | -0.0018435 | 0.0068663 | 0.016 | 0.019412 | 0.022772 | 0.017011 | 0.015789 | -0.018311 | -0.082397 | -0.004578 | -0.009155 | -0.045776 | 0.09613 | -0.022888 | -0.027466 | -0.036621 | -0.12817 | -0.022888 | -0.022888 | 0.07782 | 0.004578 | 122.2321 | 122.113 | -0.073242 | 122.0535 | 122.1268 | 0.013733 | -0.045777 | 122.2137 | 122.1405 | -0.050354 | 122.1085 | 122.0078 | -0.13275 | -0.050354 | 122.0901 | 122.1176 | 122.1313 | -0.050354 | 122.113 | 122.113 | 122.0993 | -0.022888
1637.2656 | 122.3282 | -122.1359 | 0.004578 | -0.21484 | 0.00048272 | -0.059885 | 0.022697 | -0.011046 | -0.0049433 | -0.0031253 | -0.16861 | 0.01536 | 0.018985 | 0.025122 | 0.01402 | 0.017284 | -0.018311 | -0.050354 | 0.013733 | 0.009155 | -0.032043 | 0.09613 | -0.036621 | -0.004578 | 0.013733 | -0.091553 | -0.036621 | -0.018311 | 0.073242 | 0.004578 | 122.2321 | 122.0993 | -0.036621 | 122.0856 | 122.1451 | 0.045776 | -0.022889 | 122.2092 | 122.1405 | -0.041199 | 122.1313 | 122.0444 | -0.096131 | -0.022889 | 122.1039 | 122.1176 | 122.1497 | -0.041199 | 122.0993 | 122.1176 | 122.1497 | 0
1639.0156 | 122.4106 | -122.1222 | -0.027466 | 0.15137 | -0.0020807 | -0.059671 | 0.01928 | -0.012328 | -0.0030207 | -0.0022707 | 0.18997 | 0.016428 | 0.017062 | 0.02384 | 0.015515 | 0.01643 | 0.073242 | 0.036621 | 0.10529 | 0.054932 | -0.07782 | 0.12817 | 0.018311 | 0.11902 | 0.1236 | 0.013733 | -0.07782 | -0.07782 | 0.10071 | 0.045776 | 122.2504 | 122.1405 | -0.050354 | 122.1588 | 122.1771 | 0.036621 | 0.10071 | 122.2229 | 122.168 | -0.050354 | 122.2412 | 122.1359 | -0.032043 | -0.050354 | 122.0444 | 122.1954 | 122.2275 | 0.045777 | 122.0444 | 122.0444 | 122.2458 | 0.073242
1640.7031 | 122.3877 | -122.1313 | 0.004578 | 0.082703 | -0.00037168 | -0.062021 | 0.023338 | -0.013396 | -0.0019525 | -0.0039797 | 0.098419 | 0.015146 | 0.018771 | 0.025336 | 0.015943 | 0.016857 | -0.009155 | -0.073242 | 0.013733 | 0 | -0.032043 | 0.09613 | -0.027466 | 0.036621 | -0.009155 | -0.068665 | -0.041199 | -0.041199 | 0.086975 | 0.004578 | 122.2275 | 122.1039 | -0.036621 | 122.0581 | 122.1313 | 0.027466 | -0.013733 | 122.2183 | 122.1359 | -0.045777 | 122.168 | 122.0627 | -0.073243 | -0.045777 | 122.0993 | 122.1222 | 122.1451 | -0.032044 | 122.0901 | 122.0901 | 122.1222 | 0
1642.4531 | 122.3145 | -122.1588 | 0.009155 | -0.1004 | -0.00037168 | -0.062448 | 0.022484 | -0.012969 | -0.00067088 | -0.0029117 | -0.077057 | 0.015146 | 0.017489 | 0.025763 | 0.01637 | 0.014294 | 0.054932 | -0.022888 | 0.054932 | 0.032043 | -0.050354 | 0.073242 | -0.027466 | 0.068665 | 0.073242 | -0.045776 | -0.054932 | -0.027466 | 0.10071 | 0.013733 | 122.2321 | 122.1313 | -0.059509 | 122.1359 | 122.1909 | 0.059509 | 0.045777 | 122.2595 | 122.1725 | -0.064087 | 122.2275 | 122.113 | -0.059509 | -0.036621 | 122.1085 | 122.2137 | 122.2137 | -0.036621 | 122.1039 | 122.1313 | 122.2321 | 0.004578
1644.2031 | 122.374 | -122.1405 | 0 | 0.067444 | -0.0020807 | -0.061167 | 0.022911 | -0.014464 | -0.0072931 | -0.0039797 | 0.067902 | 0.012155 | 0.020907 | 0.022772 | 0.011243 | 0.017925 | 0.036621 | 0.027466 | 0.09613 | 0.050354 | -0.082397 | 0.12817 | 0.009155 | 0.073242 | 0.064087 | 0.009155 | -0.073242 | -0.059509 | 0.11902 | 0.036621 | 122.2687 | 122.1497 | -0.082397 | 122.168 | 122.1909 | 0.041199 | 0.036621 | 122.2595 | 122.1771 | -0.073242 | 122.2137 | 122.1497 | -0.027466 | -0.059509 | 122.0581 | 122.1771 | 122.2366 | 0.009155 | 122.0673 | 122.081 | 122.2046 | 0.036621
1645.9062 | 122.374 | -122.1451 | 0 | 0.10559 | -0.0018671 | -0.060099 | 0.021843 | -0.014251 | -0.0055841 | -0.0029117 | 0.18997 | 0.014291 | 0.020907 | 0.022345 | 0.012738 | 0.015789 | 0.082397 | 0.068665 | 0.12817 | 0.07782 | -0.082397 | 0.11444 | 0.009155 | 0.11444 | 0.10986 | 0.027466 | -0.073242 | -0.054932 | 0.11444 | 0.032043 | 122.2595 | 122.1542 | -0.082397 | 122.2137 | 122.2229 | 0.068665 | 0.082397 | 122.2595 | 122.1771 | -0.073242 | 122.2595 | 122.1725 | -0.004577 | -0.054932 | 122.0627 | 122.2275 | 122.2733 | 0.009155 | 122.0718 | 122.0901 | 122.2549 | 0.032043
1647.6562 | 122.3236 | -122.1542 | 0.013733 | 0.082703 | -0.0031489 | -0.061808 | 0.018211 | -0.012542 | -0.00088448 | -0.0046207 | 0.10605 | 0.016214 | 0.016208 | 0.024481 | 0.019788 | 0.015575 | 0.004578 | -0.091553 | 0 | 0.004578 | -0.041199 | 0.091553 | -0.041199 | 0.009155 | -0.018311 | -0.1236 | -0.054932 | -0.027466 | 0.073242 | 0.013733 | 122.2458 | 122.113 | -0.054932 | 122.0627 | 122.1588 | 0.045777 | -0.009155 | 122.2275 | 122.168 | -0.068665 | 122.1634 | 122.0306 | -0.13733 | -0.041199 | 122.113 | 122.1588 | 122.1542 | -0.054932 | 122.0993 | 122.1268 | 122.1359 | 0
1649.4219 | 122.3785 | -122.1176 | 0 | 0.15137 | -0.0022943 | -0.062876 | 0.020134 | -0.014464 | -0.0051569 | -0.0044071 | 0.15182 | 0.013223 | 0.018344 | 0.023413 | 0.017652 | 0.01878 | 0.10986 | 0.07782 | 0.14191 | 0.082397 | -0.09613 | 0.1236 | 0.013733 | 0.13275 | 0.11902 | 0.032043 | -0.082397 | -0.07782 | 0.11902 | 0.050354 | 122.2412 | 122.1313 | -0.09613 | 122.1954 | 122.2 | 0.068664 | 0.10986 | 122.2366 | 122.168 | -0.082397 | 122.2504 | 122.1497 | -0.018311 | -0.07782 | 122.0215 | 122.2275 | 122.2595 | 0.013733 | 122.0352 | 122.0398 | 122.2366 | 0.050354
1651.1719 | 122.3145 | -122.1725 | 0.022888 | 0.075073 | -0.0020807 | -0.062235 | 0.01693 | -0.011901 | 0.00061092 | -0.0035525 | -0.00076274 | 0.013864 | 0.016635 | 0.023199 | 0.017652 | 0.017284 | -0.018311 | -0.09613 | -0.013733 | -0.013733 | -0.045776 | 0.09613 | -0.036621 | -0.013733 | -0.032043 | -0.1236 | -0.050354 | -0.004578 | 0.07782 | 0 | 122.2687 | 122.1359 | -0.068664 | 122.0764 | 122.1588 | 0.022888 | -0.041199 | 122.2504 | 122.1725 | -0.073242 | 122.1588 | 122.0489 | -0.1236 | -0.027466 | 122.1268 | 122.1542 | 122.1588 | -0.059509 | 122.1222 | 122.168 | 122.1405 | -0.022888
1652.9219 | 122.3099 | -122.1863 | 0.027466 | -0.19196 | 0.00069632 | -0.060312 | 0.025475 | -0.012542 | -0.0057977 | -0.0052615 | -0.18387 | 0.014291 | 0.019839 | 0.022772 | 0.011029 | 0.01643 | -0.009155 | -0.050354 | 0.032043 | -0.022888 | -0.041199 | 0.082397 | -0.022888 | 0.004578 | 0.036621 | -0.091553 | -0.022888 | -0.036621 | 0.064087 | 0.009155 | 122.2687 | 122.1634 | -0.068665 | 122.1359 | 122.1634 | 0 | -0.036621 | 122.2504 | 122.1954 | -0.050354 | 122.1909 | 122.0947 | -0.10071 | -0.064087 | 122.1451 | 122.1771 | 122.2183 | -0.050354 | 122.1634 | 122.1497 | 122.2229 | -0.018311
1654.6094 | 122.4014 | -122.1359 | -0.013733 | 0.159 | -0.0025079 | -0.062448 | 0.01928 | -0.014678 | -0.0049433 | -0.0035525 | 0.20523 | 0.011087 | 0.017917 | 0.022772 | 0.015943 | 0.017712 | 0.086975 | 0.073242 | 0.15564 | 0.086975 | -0.091553 | 0.11444 | 0.022888 | 0.13275 | 0.1236 | 0.045776 | -0.082397 | -0.086975 | 0.11902 | 0.041199 | 122.2504 | 122.1588 | -0.07782 | 122.2092 | 122.2229 | 0.064087 | 0.10071 | 122.2549 | 122.1771 | -0.068664 | 122.2687 | 122.1817 | 0.004577 | -0.073242 | 122.0444 | 122.2229 | 122.2916 | 0.036621 | 122.0535 | 122.049 | 122.2595 | 0.054932
1656.375 | 122.3923 | -122.1588 | 0.004578 | 0.044556 | -0.0014399 | -0.060099 | 0.023979 | -0.014251 | -0.0083613 | -0.0071841 | 0.067902 | 0.011942 | 0.016421 | 0.022772 | 0.013379 | 0.016857 | 0.036621 | 0.022888 | 0.086975 | 0.041199 | -0.068665 | 0.11902 | 0.009155 | 0.082397 | 0.07782 | -0.013733 | -0.073242 | -0.054932 | 0.091553 | 0.022888 | 122.2778 | 122.168 | -0.073243 | 122.1817 | 122.2 | 0.032044 | 0.032043 | 122.2504 | 122.1817 | -0.07782 | 122.2412 | 122.1451 | -0.036621 | -0.05951 | 122.0901 | 122.1954 | 122.2458 | 0.004577 | 122.0856 | 122.1039 | 122.2366 | 0.01831
1658.0625 | 122.3831 | -122.1451 | -0.009155 | 0.18951 | -0.0027215 | -0.060526 | 0.020134 | -0.013824 | -0.0025935 | -0.0065433 | 0.15945 | 0.012155 | 0.014499 | 0.021063 | 0.01637 | 0.015789 | 0.11902 | 0.059509 | 0.13275 | 0.068665 | -0.082397 | 0.1236 | 0.022888 | 0.15564 | 0.1236 | 0.022888 | -0.091553 | -0.068665 | 0.1236 | 0.045776 | 122.2687 | 122.168 | -0.073242 | 122.2046 | 122.2137 | 0.045777 | 0.12817 | 122.2687 | 122.1909 | -0.082398 | 122.3007 | 122.168 | -0.022888 | -0.05951 | 122.0627 | 122.2641 | 122.2778 | 0.032043 | 122.0535 | 122.0764 | 122.2687 | 0.054931
1659.7969 | 122.3877 | -122.1588 | 0 | 0.12848 | -0.0042169 | -0.057749 | 0.020775 | -0.011901 | -0.0062249 | -0.0039797 | 0.1442 | 0.013864 | 0.016208 | 0.024481 | 0.015088 | 0.01643 | 0.10529 | 0.059509 | 0.13275 | 0.059509 | -0.07782 | 0.13275 | 0.036621 | 0.13275 | 0.10986 | 0.032043 | -0.082397 | -0.073242 | 0.10986 | 0.036621 | 122.2916 | 122.1954 | -0.07782 | 122.2183 | 122.2183 | 0.022888 | 0.10529 | 122.2687 | 122.1954 | -0.082397 | 122.2916 | 122.1909 | -0.004578 | -0.073242 | 122.081 | 122.2641 | 122.2916 | 0.036621 | 122.0764 | 122.0856 | 122.2687 | 0.036621
1661.5469 | 122.3373 | -122.1863 | 0.009155 | 0.090332 | -0.0014399 | -0.060099 | 0.019493 | -0.013824 | 0.00039732 | -0.0035525 | 0.08316 | 0.015146 | 0.014071 | 0.024481 | 0.016797 | 0.013866 | 0.018311 | -0.091553 | 0.009155 | -0.009155 | -0.041199 | 0.10071 | -0.027466 | 0.036621 | -0.022888 | -0.11902 | -0.036621 | -0.022888 | 0.064087 | 0.013733 | 122.287 | 122.1588 | -0.050354 | 122.0947 | 122.1771 | 0.018311 | 0.009156 | 122.2504 | 122.2 | -0.045776 | 122.2229 | 122.0673 | -0.13275 | -0.032043 | 122.1451 | 122.2046 | 122.1954 | -0.036621 | 122.1497 | 122.1634 | 122.1634 | 0.004578
1663.2969 | 122.438 | -122.1405 | 0 | -0.062256 | -0.0014399 | -0.060312 | 0.025261 | -0.013396 | -0.0079339 | -0.0050479 | -0.054169 | 0.011301 | 0.017489 | 0.022559 | 0.01167 | 0.015575 | 0.073242 | 0.086975 | 0.13733 | 0.068665 | -0.082397 | 0.10071 | 0.004578 | 0.13733 | 0.15564 | 0.073242 | -0.086975 | -0.059509 | 0.11902 | 0.054932 | 122.2412 | 122.1451 | -0.082397 | 122.2275 | 122.2092 | 0.064087 | 0.073242 | 122.2595 | 122.1954 | -0.086975 | 122.2778 | 122.2137 | 0.01831 | -0.059509 | 122.0581 | 122.2137 | 122.2778 | 0.004578 | 122.0535 | 122.081 | 122.2961 | 0.054932
1665.0469 | 122.319 | -122.2 | 0.022888 | 0.036926 | -0.00079888 | -0.062662 | 0.017784 | -0.010833 | 0.0014655 | -0.0022707 | -0.00076274 | 0.013864 | 0.015994 | 0.024695 | 0.017438 | 0.016216 | 0.004578 | -0.09613 | -0.004578 | -0.009155 | -0.059509 | 0.086975 | -0.027466 | -0.009155 | -0.032043 | -0.11444 | -0.064087 | -0.041199 | 0.073242 | 0.009155 | 122.287 | 122.1725 | -0.082397 | 122.1039 | 122.1909 | 0.018311 | -0.01831 | 122.2733 | 122.2092 | -0.086975 | 122.1909 | 122.0856 | -0.1236 | -0.064087 | 122.1405 | 122.2046 | 122.1954 | -0.050354 | 122.1359 | 122.1588 | 122.168 | -0.013733
1666.7344 | 122.374 | -122.1634 | 0.009155 | 0.11322 | -0.0061395 | -0.057749 | 0.019493 | -0.012969 | -0.0064387 | -0.0050479 | 0.15182 | 0.012582 | 0.014499 | 0.022131 | 0.014661 | 0.017071 | 0.10071 | 0.054932 | 0.11902 | 0.045776 | -0.086975 | 0.11444 | -0.004578 | 0.10986 | 0.10071 | 0.009155 | -0.09613 | -0.068665 | 0.091553 | 0.018311 | 122.2778 | 122.1588 | -0.09613 | 122.2183 | 122.2092 | 0.050354 | 0.091553 | 122.2549 | 122.1817 | -0.10528 | 122.2733 | 122.1725 | -0.009156 | -0.07782 | 122.0764 | 122.2641 | 122.2824 | -0.013733 | 122.0673 | 122.0947 | 122.2641 | 0.009156
1668.4844 | 122.319 | -122.1909 | 0.032043 | -0.10803 | -0.00058528 | -0.059458 | 0.025902 | -0.012755 | -0.0030207 | -0.0054751 | -0.17624 | 0.014505 | 0.018558 | 0.023199 | 0.013806 | 0.015789 | 0.013733 | -0.045776 | 0.022888 | -0.004578 | -0.059509 | 0.086975 | -0.022888 | 0.013733 | 0.032043 | -0.07782 | -0.045776 | -0.027466 | 0.082397 | 0.004578 | 122.2778 | 122.168 | -0.091552 | 122.1451 | 122.1863 | 0.01831 | -0.01831 | 122.2733 | 122.1954 | -0.077819 | 122.2046 | 122.113 | -0.082398 | -0.059509 | 122.1313 | 122.2046 | 122.2137 | -0.054931 | 122.1451 | 122.1634 | 122.2229 | -0.027465
1670.2344 | 122.4518 | -122.1588 | -0.004578 | 0.14374 | -0.0037897 | -0.061167 | 0.019493 | -0.011901 | -0.0017389 | -0.0016299 | 0.09079 | 0.014505 | 0.013858 | 0.023413 | 0.015515 | 0.01408 | 0.091553 | 0.036621 | 0.11444 | 0.07782 | -0.068665 | 0.11444 | 0.013733 | 0.11902 | 0.10986 | 0.027466 | -0.073242 | -0.064087 | 0.1236 | 0.050354 | 122.2733 | 122.1725 | -0.064087 | 122.1954 | 122.2366 | 0.064087 | 0.096131 | 122.2824 | 122.2092 | -0.068664 | 122.2778 | 122.1863 | -0.022888 | -0.059509 | 122.0901 | 122.2504 | 122.2733 | 0.018311 | 122.0856 | 122.0947 | 122.2687 | 0.054932
1672 | 122.3419 | -122.2137 | 0.041199 | -0.13855 | -0.0012263 | -0.060526 | 0.024834 | -0.010619 | -0.0032343 | -0.0039797 | -0.1915 | 0.012155 | 0.017703 | 0.022131 | 0.012097 | 0.016216 | 0.073242 | 0.054932 | 0.12817 | 0.082397 | -0.059509 | 0.10071 | 0.009155 | 0.068665 | 0.10986 | -0.022888 | -0.073242 | -0.045776 | 0.09613 | 0.022888 | 122.3145 | 122.2229 | -0.10071 | 122.2687 | 122.2961 | 0.073242 | 0.032043 | 122.3099 | 122.2366 | -0.11444 | 122.2824 | 122.1909 | -0.045776 | -0.086975 | 122.1542 | 122.287 | 122.3419 | -0.032044 | 122.1405 | 122.168 | 122.3236 | -0.018311
1673.7656 | 122.4564 | -122.1451 | -0.013733 | 0.014038 | -0.0040033 | -0.061594 | 0.023979 | -0.012542 | -0.0090021 | -0.0078249 | -0.016022 | 0.010446 | 0.018558 | 0.023627 | 0.012311 | 0.015789 | 0.032043 | 0.032043 | 0.086975 | 0.054932 | -0.07782 | 0.10529 | 0 | 0.10071 | 0.10986 | 0.018311 | -0.07782 | -0.059509 | 0.10071 | 0.027466 | 122.2504 | 122.1451 | -0.064087 | 122.1771 | 122.2 | 0.054932 | 0.045776 | 122.2458 | 122.1725 | -0.064087 | 122.2458 | 122.1634 | -0.009155 | -0.045776 | 122.0673 | 122.1771 | 122.2321 | 0.013733 | 122.0673 | 122.0856 | 122.2549 | 0.041199
1675.4531 | 122.4747 | -122.1451 | 0 | 0.0064086 | -0.0035761 | -0.059885 | 0.023766 | -0.011474 | -0.0049433 | -0.0063297 | -0.023651 | 0.011514 | 0.016635 | 0.022559 | 0.012097 | 0.014721 | 0.059509 | 0.036621 | 0.10071 | 0.050354 | -0.068665 | 0.10529 | 0.022888 | 0.1236 | 0.13275 | 0.041199 | -0.082397 | -0.064087 | 0.11444 | 0.050354 | 122.2504 | 122.168 | -0.068665 | 122.1817 | 122.1954 | 0.027466 | 0.059509 | 122.2595 | 122.1954 | -0.082397 | 122.2687 | 122.1863 | -0.009155 | -0.064087 | 122.0764 | 122.2046 | 122.2458 | 0.022888 | 122.0627 | 122.081 | 122.2778 | 0.050354
1677.2188 | 122.3785 | -122.2 | 0.027466 | -0.20721 | -0.0029351 | -0.060526 | 0.020775 | -0.01361 | -0.0010981 | -0.0071841 | -0.20676 | 0.013864 | 0.020053 | 0.025763 | 0.017224 | 0.013866 | 0.004578 | -0.054932 | 0.013733 | 0.004578 | -0.045776 | 0.073242 | -0.036621 | 0.018311 | 0.013733 | -0.091553 | -0.036621 | -0.013733 | 0.064087 | -0.018311 | 122.2733 | 122.1634 | -0.073242 | 122.1451 | 122.2046 | 0.041199 | -0.022888 | 122.2641 | 122.1817 | -0.064087 | 122.2183 | 122.1085 | -0.073242 | -0.041199 | 122.1542 | 122.2046 | 122.2137 | -0.064087 | 122.1634 | 122.1863 | 122.2137 | -0.045777
1678.9688 | 122.4335 | -122.2046 | 0 | -0.13092 | -0.0063531 | -0.05839 | 0.020134 | -0.014251 | -0.0053705 | -0.0059023 | -0.15335 | 0.010019 | 0.01578 | 0.022131 | 0.014661 | 0.017498 | 0.086975 | 0.11902 | 0.14648 | 0.07782 | -0.086975 | 0.10071 | 0.013733 | 0.14191 | 0.16937 | 0.045776 | -0.091553 | -0.082397 | 0.10986 | 0.041199 | 122.3053 | 122.2183 | -0.086975 | 122.3236 | 122.2824 | 0.064087 | 0.086975 | 122.3145 | 122.2458 | -0.091553 | 122.3465 | 122.2504 | 0.004577 | -0.082397 | 122.1176 | 122.2916 | 122.3511 | 0.013733 | 122.113 | 122.1222 | 122.374 | 0.041199
1680.6562 | 122.4747 | -122.1588 | -0.004578 | 0.0064086 | -0.0018671 | -0.060312 | 0.020561 | -0.0082694 | -0.0057977 | -0.0048343 | -0.023651 | 0.011942 | 0.015567 | 0.021063 | 0.013166 | 0.016857 | 0.054932 | 0.050354 | 0.11444 | 0.054932 | -0.068665 | 0.11902 | 0.009155 | 0.10986 | 0.13275 | 0.036621 | -0.091553 | -0.064087 | 0.11444 | 0.041199 | 122.2778 | 122.168 | -0.064087 | 122.2092 | 122.2137 | 0.045777 | 0.05951 | 122.2733 | 122.2 | -0.086975 | 122.2687 | 122.1954 | -0.004578 | -0.059509 | 122.0901 | 122.2137 | 122.2733 | 0.013733 | 122.0673 | 122.0947 | 122.2916 | 0.045777
1682.4062 | 122.4197 | -122.1909 | 0.004578 | -0.16907 | -0.0029351 | -0.059671 | 0.021843 | -0.014037 | -0.0047297 | -0.0073977 | -0.12283 | 0.012369 | 0.01578 | 0.021277 | 0.013593 | 0.015362 | 0.1236 | 0.09613 | 0.14648 | 0.068665 | -0.07782 | 0.11444 | 0.018311 | 0.12817 | 0.16022 | 0.050354 | -0.091553 | -0.068665 | 0.10986 | 0.036621 | 122.3053 | 122.2092 | -0.082398 | 122.287 | 122.2595 | 0.050354 | 0.11902 | 122.3007 | 122.2275 | -0.096131 | 122.319 | 122.2412 | 0.013733 | -0.073243 | 122.113 | 122.3145 | 122.3373 | 0.013733 | 122.0993 | 122.1222 | 122.3511 | 0.032043
1684.1562 | 122.4609 | -122.168 | -0.018311 | 0.082703 | -0.0035761 | -0.061167 | 0.020561 | -0.012542 | 0.00082452 | -0.0044071 | 0.10605 | 0.012155 | 0.016849 | 0.022559 | 0.017865 | 0.015362 | 0.036621 | -0.059509 | 0.013733 | -0.009155 | -0.045776 | 0.086975 | -0.009155 | 0.059509 | 0.032043 | -0.068665 | -0.045776 | -0.050354 | 0.091553 | 0.036621 | 122.2549 | 122.1588 | -0.027465 | 122.1085 | 122.1588 | 0 | 0.054932 | 122.2595 | 122.2046 | -0.027465 | 122.2275 | 122.0993 | -0.10529 | -0.032043 | 122.1222 | 122.2046 | 122.1817 | 0.009156 | 122.1222 | 122.1176 | 122.2 | 0.054932
1685.9219 | 122.3831 | -122.2 | 0.009155 | -0.077515 | 0.00069632 | -0.060099 | 0.018211 | -0.01596 | 0.0027471 | -0.0048343 | -0.14572 | 0.014291 | 0.01813 | 0.021704 | 0.017652 | 0.015362 | 0.059509 | 0 | 0.059509 | 0.041199 | -0.054932 | 0.082397 | -0.032043 | 0.073242 | 0.068665 | -0.036621 | -0.07782 | -0.027466 | 0.086975 | 0.027466 | 122.2824 | 122.168 | -0.064087 | 122.2 | 122.2412 | 0.073242 | 0.050354 | 122.287 | 122.2275 | -0.086975 | 122.2733 | 122.1634 | -0.064087 | -0.036621 | 122.1451 | 122.2595 | 122.2595 | -0.041198 | 122.1222 | 122.1725 | 122.2687 | 0.018311
1687.6094 | 122.3282 | -122.2046 | 0.027466 | 0.0064086 | -0.0012263 | -0.06138 | 0.01992 | -0.011046 | 0.00039732 | -0.0044071 | -0.031281 | 0.016428 | 0.017062 | 0.022772 | 0.019361 | 0.015362 | 0.013733 | -0.032043 | 0.004578 | 0.013733 | -0.068665 | 0.086975 | -0.022888 | 0.009155 | 0.004578 | -0.10529 | -0.032043 | -0.045776 | 0.082397 | -0.009155 | 122.2916 | 122.1817 | -0.096131 | 122.1725 | 122.2183 | 0.036621 | -0.013733 | 122.287 | 122.1954 | -0.059509 | 122.2137 | 122.0993 | -0.096131 | -0.073242 | 122.1359 | 122.2183 | 122.2092 | -0.050354 | 122.1725 | 122.1588 | 122.2092 | -0.036621
1689.375 | 122.4609 | -122.1863 | -0.027466 | 0.13611 | -0.0018671 | -0.062021 | 0.021202 | -0.015319 | -0.0038751 | -0.0029117 | 0.15182 | 0.016 | 0.016421 | 0.02149 | 0.01637 | 0.017498 | 0.027466 | -0.036621 | 0.032043 | 0.004578 | -0.054932 | 0.10529 | -0.018311 | 0.07782 | 0.068665 | -0.045776 | -0.07782 | -0.050354 | 0.09613 | 0.027466 | 122.2916 | 122.168 | -0.027466 | 122.1497 | 122.1909 | 0.022889 | 0.054932 | 122.2824 | 122.2137 | -0.050354 | 122.2641 | 122.1405 | -0.073242 | -0.022888 | 122.1313 | 122.2137 | 122.2183 | 0.009155 | 122.1085 | 122.1359 | 122.2549 | 0.054932
1691.0781 | 122.493 | -122.168 | -0.013733 | -0.0012209 | -0.0037897 | -0.059458 | 0.023125 | -0.011901 | -0.0068659 | -0.0061161 | 0.037384 | 0.011728 | 0.018344 | 0.02149 | 0.011029 | 0.016003 | 0.032043 | 0.036621 | 0.10986 | 0.050354 | -0.09613 | 0.1236 | 0.018311 | 0.091553 | 0.12817 | 0.036621 | -0.09613 | -0.045776 | 0.10529 | 0.045776 | 122.2916 | 122.1863 | -0.082397 | 122.2046 | 122.2183 | 0.032043 | 0.045776 | 122.2733 | 122.2137 | -0.082397 | 122.2595 | 122.2046 | -0.009155 | -0.032043 | 122.0718 | 122.2 | 122.2778 | 0.032044 | 122.0718 | 122.1222 | 122.2961 | 0.059509
1692.8281 | 122.3419 | -122.2183 | 0.018311 | 0.021668 | -0.00058528 | -0.06074 | 0.020561 | -0.01361 | 0.0016791 | -0.0016299 | -0.03891 | 0.014932 | 0.016635 | 0.024695 | 0.018293 | 0.014721 | 0.036621 | -0.036621 | 0.027466 | 0.013733 | -0.045776 | 0.073242 | -0.013733 | 0.013733 | 0.018311 | -0.10529 | -0.032043 | -0.027466 | 0.082397 | 0.004578 | 122.2916 | 122.2046 | -0.064087 | 122.1817 | 122.2321 | 0.027466 | 0.01831 | 122.3007 | 122.2229 | -0.050354 | 122.2321 | 122.113 | -0.10986 | -0.045777 | 122.1725 | 122.2549 | 122.2458 | -0.032044 | 122.1863 | 122.1909 | 122.2366 | -0.013733
1694.5781 | 122.3419 | -122.2092 | 0.032043 | -0.069885 | 5.5518e-05 | -0.062448 | 0.01992 | -0.013396 | -0.00088448 | -0.0022707 | -0.084686 | 0.013864 | 0.016421 | 0.023413 | 0.015729 | 0.015575 | 0.073242 | 0.013733 | 0.064087 | 0.045776 | -0.054932 | 0.09613 | 0.004578 | 0.054932 | 0.073242 | -0.036621 | -0.045776 | -0.027466 | 0.082397 | 0.022888 | 122.3053 | 122.2137 | -0.086975 | 122.2229 | 122.2549 | 0.041198 | 0.041199 | 122.2916 | 122.2321 | -0.077819 | 122.2641 | 122.1725 | -0.059509 | -0.059509 | 122.1542 | 122.2824 | 122.2733 | -0.027465 | 122.1634 | 122.1817 | 122.2824 | -0.009155
1696.2656 | 122.4655 | -122.1725 | -0.022888 | 0.090332 | -0.0010125 | -0.060099 | 0.02227 | -0.012115 | -0.0036615 | -0.0037661 | 0.15182 | 0.012582 | 0.017703 | 0.024054 | 0.014447 | 0.017284 | 0.013733 | -0.045776 | 0.004578 | -0.009155 | -0.045776 | 0.10071 | -0.018311 | 0.064087 | 0.036621 | -0.059509 | -0.064087 | -0.059509 | 0.086975 | 0.022888 | 122.2733 | 122.1542 | -0.022888 | 122.1268 | 122.1634 | 0.009156 | 0.036621 | 122.2595 | 122.1954 | -0.041199 | 122.2366 | 122.113 | -0.082397 | -0.036621 | 122.1268 | 122.1863 | 122.1771 | 0.004577 | 122.1085 | 122.113 | 122.2092 | 0.045776
1698 | 122.4335 | -122.1771 | 0.004578 | 0.15137 | -0.010412 | -0.058817 | 0.017571 | -0.013183 | -0.0064387 | -0.0037661 | 0.15182 | 0.012582 | 0.014285 | 0.022559 | 0.015088 | 0.018993 | 0.082397 | 0.086975 | 0.14191 | 0.064087 | -0.09613 | 0.12817 | 0.013733 | 0.12817 | 0.14191 | 0.022888 | -0.086975 | -0.073242 | 0.11444 | 0.050354 | 122.3053 | 122.1909 | -0.10071 | 122.2641 | 122.2412 | 0.050354 | 0.077819 | 122.2916 | 122.2275 | -0.091553 | 122.3053 | 122.2 | -0.027466 | -0.07782 | 122.081 | 122.2595 | 122.319 | 0.009155 | 122.0901 | 122.1039 | 122.319 | 0.045776
1699.6875 | 122.3511 | -122.2321 | 0.027466 | -0.16144 | 0.0017645 | -0.060953 | 0.027397 | -0.014251 | -0.0045161 | -0.0065433 | -0.18387 | 0.016428 | 0.018344 | 0.024054 | 0.010602 | 0.015148 | 0.004578 | -0.054932 | 0.022888 | 0.009155 | -0.054932 | 0.091553 | -0.050354 | 0.022888 | 0.032043 | -0.082397 | -0.041199 | 0 | 0.073242 | -0.004578 | 122.3236 | 122.1817 | -0.082398 | 122.1771 | 122.2412 | 0.059509 | -0.022888 | 122.3053 | 122.2275 | -0.068665 | 122.2549 | 122.1497 | -0.077819 | -0.027466 | 122.1771 | 122.2366 | 122.2549 | -0.07782 | 122.1909 | 122.2321 | 122.2641 | -0.032044
1701.4531 | 122.3877 | -122.2229 | 0.009155 | -0.069885 | -0.0016535 | -0.062662 | 0.019707 | -0.01361 | -2.988e-05 | -0.0054751 | -0.084686 | 0.014291 | 0.019412 | 0.025549 | 0.016797 | 0.013866 | 0.054932 | 0.004578 | 0.050354 | 0.036621 | -0.054932 | 0.10529 | -0.022888 | 0.068665 | 0.073242 | -0.041199 | -0.054932 | -0.036621 | 0.064087 | 0.009155 | 122.3282 | 122.2 | -0.064087 | 122.2275 | 122.2595 | 0.059509 | 0.045777 | 122.287 | 122.2321 | -0.064087 | 122.2916 | 122.1817 | -0.050354 | -0.045776 | 122.168 | 122.2778 | 122.2733 | -0.032043 | 122.168 | 122.1863 | 122.2961 | 0
1703.1406 | 122.4014 | -122.2137 | 0.022888 | -0.16144 | -0.00015808 | -0.060099 | 0.023552 | -0.01126 | -0.0015253 | -0.0014163 | -0.14572 | 0.012369 | 0.019412 | 0.025122 | 0.012738 | 0.014507 | 0.013733 | -0.032043 | 0.032043 | 0.041199 | -0.045776 | 0.07782 | -0.045776 | 0.032043 | 0.068665 | -0.054932 | -0.050354 | -0.032043 | 0.07782 | 0.018311 | 122.2916 | 122.168 | -0.068664 | 122.1817 | 122.2549 | 0.086975 | -0.009155 | 122.2916 | 122.2321 | -0.073242 | 122.2458 | 122.1588 | -0.073243 | -0.054931 | 122.168 | 122.2275 | 122.2458 | -0.068664 | 122.1634 | 122.1817 | 122.2824 | -0.004577
1704.8906 | 122.4701 | -122.2 | -0.009155 | 0.13611 | -0.0025079 | -0.063089 | 0.021629 | -0.014251 | -0.0021661 | -0.0037661 | 0.1442 | 0.012582 | 0.017917 | 0.025977 | 0.01637 | 0.016643 | 0.013733 | -0.036621 | 0.032043 | 0.018311 | -0.050354 | 0.10986 | -0.009155 | 0.073242 | 0.073242 | -0.009155 | -0.073242 | -0.050354 | 0.09613 | 0.050354 | 122.3099 | 122.1909 | -0.041199 | 122.1634 | 122.2183 | 0.027466 | 0.022888 | 122.2961 | 122.2504 | -0.064087 | 122.2733 | 122.1909 | -0.059509 | -0.041199 | 122.1497 | 122.2137 | 122.2321 | 0 | 122.1268 | 122.1497 | 122.2733 | 0.059509
1706.6562 | 122.4701 | -122.1954 | -0.004578 | 0.090332 | -0.0014399 | -0.063303 | 0.021843 | -0.012542 | -0.0019525 | -0.0031253 | 0.15945 | 0.014291 | 0.018344 | 0.025336 | 0.015729 | 0.016216 | 0.009155 | -0.054932 | 0.022888 | 0 | -0.059509 | 0.086975 | -0.022888 | 0.054932 | 0.027466 | -0.045776 | -0.054932 | -0.041199 | 0.086975 | 0.022888 | 122.2824 | 122.1725 | -0.054931 | 122.1405 | 122.1954 | 0.022888 | 0.013733 | 122.2824 | 122.2183 | -0.050354 | 122.2504 | 122.1497 | -0.068664 | -0.036621 | 122.1359 | 122.2046 | 122.2183 | -0.01831 | 122.1405 | 122.1542 | 122.2229 | 0.027466
1708.4062 | 122.4106 | -122.2229 | 0.018311 | -0.16144 | 0.0013373 | -0.059458 | 0.024193 | -0.01361 | -0.0032343 | -0.0052615 | -0.15335 | 0.014291 | 0.017489 | 0.022986 | 0.01402 | 0.01408 | -0.018311 | -0.045776 | 0.004578 | 0.009155 | -0.036621 | 0.068665 | -0.032043 | 0.004578 | 0.050354 | -0.07782 | -0.032043 | -0.027466 | 0.082397 | 0 | 122.2916 | 122.1909 | -0.054932 | 122.1771 | 122.2321 | 0.041198 | -0.036622 | 122.3053 | 122.2229 | -0.050354 | 122.2275 | 122.1451 | -0.07782 | -0.045777 | 122.1863 | 122.2046 | 122.2275 | -0.050354 | 122.1909 | 122.1954 | 122.2733 | -0.018311
1710.0938 | 122.3831 | -122.2275 | 0.032043 | -0.062256 | -0.00058528 | -0.063517 | 0.021629 | -0.010833 | -0.0017389 | -0.0041933 | -0.084686 | 0.014291 | 0.019626 | 0.025549 | 0.015515 | 0.016643 | 0.050354 | 0.013733 | 0.073242 | 0.036621 | -0.054932 | 0.10529 | -0.004578 | 0.059509 | 0.086975 | -0.032043 | -0.059509 | -0.050354 | 0.09613 | 0.004578 | 122.3328 | 122.2229 | -0.086975 | 122.2412 | 122.2641 | 0.041199 | 0.018311 | 122.3236 | 122.2321 | -0.091552 | 122.287 | 122.1954 | -0.036621 | -0.082397 | 122.1725 | 122.2778 | 122.3007 | -0.036621 | 122.168 | 122.1771 | 122.3145 | -0.027465
1711.8438 | 122.3602 | -122.2412 | 0.018311 | -0.2301 | -0.0037897 | -0.060312 | 0.022911 | -0.0080558 | -0.0066523 | -0.0044071 | -0.054169 | 0.014719 | 0.016208 | 0.025549 | 0.012525 | 0.01878 | 0.004578 | 0 | 0.045776 | 0.018311 | -0.064087 | 0.09613 | -0.022888 | 0.004578 | 0.050354 | -0.068665 | -0.032043 | -0.027466 | 0.073242 | 0 | 122.3373 | 122.2183 | -0.082398 | 122.2412 | 122.2595 | 0.041199 | -0.013733 | 122.3145 | 122.2412 | -0.050354 | 122.2458 | 122.1725 | -0.068665 | -0.045777 | 122.1771 | 122.2458 | 122.287 | -0.041199 | 122.2092 | 122.2137 | 122.2916 | -0.018311
1713.5938 | 122.4838 | -122.2 | -0.022888 | 0.10559 | -0.0033625 | -0.062448 | 0.018425 | -0.014678 | -0.0032343 | -0.0046207 | 0.11368 | 0.016 | 0.01578 | 0.02149 | 0.017652 | 0.014294 | -0.004578 | -0.064087 | 0.013733 | 0 | -0.045776 | 0.082397 | -0.018311 | 0.050354 | 0.022888 | -0.064087 | -0.054932 | -0.032043 | 0.091553 | 0.027466 | 122.2824 | 122.1817 | -0.022888 | 122.1359 | 122.2 | 0.018311 | 0.01831 | 122.2916 | 122.2275 | -0.032044 | 122.2504 | 122.1359 | -0.091553 | -0.009155 | 122.1542 | 122.1954 | 122.2137 | 0.004577 | 122.1451 | 122.168 | 122.2229 | 0.050354
1715.3594 | 122.3877 | -122.2412 | 0.041199 | 0.075073 | -0.0010125 | -0.06074 | 0.021202 | -0.014251 | -0.00088448 | -0.0037661 | 0.075531 | 0.014932 | 0.018985 | 0.021704 | 0.01872 | 0.014934 | -0.032043 | -0.091553 | 0 | -0.013733 | -0.041199 | 0.091553 | -0.027466 | 0.009155 | -0.027466 | -0.11444 | -0.041199 | -0.041199 | 0.082397 | -0.009155 | 122.3328 | 122.2137 | -0.082398 | 122.1497 | 122.2275 | 0.013733 | -0.073242 | 122.3236 | 122.2321 | -0.082398 | 122.2504 | 122.1268 | -0.10529 | -0.082398 | 122.2 | 122.2092 | 122.2412 | -0.068665 | 122.2 | 122.2 | 122.2137 | -0.050354
1717.125 | 122.4838 | -122.2229 | 0 | 0.044556 | -0.0057123 | -0.061167 | 0.021416 | -0.013824 | -0.010497 | -0.0046207 | 0.12131 | 0.015573 | 0.01514 | 0.021063 | 0.013166 | 0.017925 | 0.018311 | 0.018311 | 0.068665 | 0.027466 | -0.073242 | 0.10071 | 0.022888 | 0.073242 | 0.07782 | 0 | -0.086975 | -0.064087 | 0.12817 | 0.041199 | 122.3236 | 122.2458 | -0.073242 | 122.2412 | 122.2504 | 0.004578 | 0.018311 | 122.3511 | 122.2641 | -0.086975 | 122.2961 | 122.2229 | -0.041199 | -0.064087 | 122.1497 | 122.2412 | 122.2916 | 0.022888 | 122.1359 | 122.1588 | 122.3007 | 0.041199
1718.875 | 122.4152 | -122.2458 | 0.018311 | 0.11322 | -0.0018671 | -0.06074 | 0.020988 | -0.014464 | -0.00024348 | -0.0033389 | 0.098419 | 0.016214 | 0.017703 | 0.022772 | 0.016584 | 0.016216 | -0.004578 | -0.09613 | -0.009155 | -0.004578 | -0.041199 | 0.09613 | -0.022888 | 0.004578 | -0.018311 | -0.09613 | -0.041199 | -0.036621 | 0.068665 | 0.009155 | 122.3419 | 122.2229 | -0.05951 | 122.1497 | 122.2412 | 0.01831 | -0.022889 | 122.3145 | 122.2549 | -0.05951 | 122.2504 | 122.1497 | -0.10528 | -0.054932 | 122.2046 | 122.2412 | 122.2366 | -0.041199 | 122.2046 | 122.2092 | 122.2275 | -0.009156
1720.5781 | 122.3785 | -122.2366 | 0.022888 | -0.069885 | -0.00015808 | -0.061167 | 0.021416 | -0.014678 | -0.00024348 | -0.0046207 | -0.061798 | 0.012796 | 0.017276 | 0.025549 | 0.017438 | 0.014721 | 0.073242 | 0.018311 | 0.050354 | 0.032043 | -0.045776 | 0.07782 | -0.013733 | 0.059509 | 0.073242 | -0.059509 | -0.045776 | -0.050354 | 0.086975 | 0.027466 | 122.3145 | 122.2229 | -0.068664 | 122.2549 | 122.2687 | 0.045776 | 0.050354 | 122.3236 | 122.2641 | -0.068664 | 122.2961 | 122.1771 | -0.086975 | -0.073242 | 122.1909 | 122.3099 | 122.287 | -0.036621 | 122.1909 | 122.1863 | 122.3099 | 0.004578
1722.3281 | 122.4106 | -122.2275 | 0.009155 | -0.16907 | -0.00015808 | -0.06074 | 0.024834 | -0.011901 | -0.0034479 | -0.0078249 | -0.13046 | 0.012582 | 0.018985 | 0.024695 | 0.013166 | 0.014934 | -0.018311 | -0.064087 | 0.009155 | 0.018311 | -0.045776 | 0.054932 | -0.045776 | -0.004578 | 0.032043 | -0.082397 | -0.045776 | -0.009155 | 0.082397 | 0.018311 | 122.2824 | 122.1817 | -0.054931 | 122.1634 | 122.2458 | 0.064087 | -0.027466 | 122.3099 | 122.2458 | -0.054931 | 122.2229 | 122.1451 | -0.10071 | -0.01831 | 122.1817 | 122.2092 | 122.2366 | -0.054931 | 122.1817 | 122.2183 | 122.2595 | 0.009156
1724.0781 | 122.4792 | -122.2275 | 0 | 0.17426 | -0.0044305 | -0.060526 | 0.018852 | -0.011901 | -0.0047297 | -0.0050479 | 0.17471 | 0.016214 | 0.017276 | 0.023413 | 0.01637 | 0.01643 | 0.082397 | 0.064087 | 0.14191 | 0.068665 | -0.091553 | 0.12817 | 0.022888 | 0.1236 | 0.12817 | 0.050354 | -0.091553 | -0.07782 | 0.10529 | 0.036621 | 122.3557 | 122.2504 | -0.091553 | 122.2916 | 122.2961 | 0.045777 | 0.082397 | 122.3328 | 122.2641 | -0.091553 | 122.3511 | 122.2778 | 0.013733 | -0.07782 | 122.1359 | 122.3099 | 122.3694 | 0.022888 | 122.1359 | 122.1497 | 122.3557 | 0.036621
1725.7656 | 122.3877 | -122.2458 | 0.032043 | 0.075073 | -0.00058528 | -0.06138 | 0.01992 | -0.013824 | -2.988e-05 | -0.0046207 | 0.060272 | 0.014932 | 0.017917 | 0.023627 | 0.018506 | 0.015148 | -0.009155 | -0.10071 | -0.018311 | -0.018311 | -0.045776 | 0.064087 | -0.032043 | -0.004578 | -0.027466 | -0.10529 | -0.045776 | -0.027466 | 0.07782 | 0.004578 | 122.3099 | 122.2137 | -0.077819 | 122.1451 | 122.2275 | 0.013732 | -0.041198 | 122.3236 | 122.2504 | -0.077819 | 122.2412 | 122.1405 | -0.10986 | -0.059509 | 122.2 | 122.2366 | 122.2275 | -0.064086 | 122.2 | 122.2183 | 122.2183 | -0.027465
1727.5469 | 122.5159 | -122.2137 | 0.004578 | -0.046997 | -0.0033625 | -0.059458 | 0.025688 | -0.012755 | -0.010711 | -0.0065433 | -0.0083922 | 0.01301 | 0.020053 | 0.023413 | 0.011243 | 0.014934 | 0.050354 | 0.054932 | 0.12817 | 0.059509 | -0.073242 | 0.10986 | -0.009155 | 0.1236 | 0.16022 | 0.059509 | -0.082397 | -0.041199 | 0.10529 | 0.045776 | 122.3236 | 122.2046 | -0.07782 | 122.2687 | 122.2733 | 0.068664 | 0.045776 | 122.319 | 122.2595 | -0.086975 | 122.3373 | 122.2733 | 0.013733 | -0.045777 | 122.1405 | 122.2641 | 122.3419 | -0.013733 | 122.1313 | 122.1725 | 122.374 | 0.041198
1729.3125 | 122.4838 | -122.2275 | -0.004578 | 0.067444 | -0.0020807 | -0.061808 | 0.02462 | -0.014678 | -0.0064387 | -0.0078249 | 0.08316 | 0.014078 | 0.019626 | 0.023199 | 0.013166 | 0.015362 | 0.041199 | 0.004578 | 0.10071 | 0.032043 | -0.091553 | 0.1236 | 0.009155 | 0.068665 | 0.07782 | -0.009155 | -0.082397 | -0.068665 | 0.10986 | 0.036621 | 122.3511 | 122.2366 | -0.086975 | 122.2321 | 122.2595 | 0.022888 | 0.045777 | 122.3373 | 122.2641 | -0.077819 | 122.2961 | 122.2183 | -0.045776 | -0.064087 | 122.1359 | 122.2687 | 122.3282 | 0.013733 | 122.1451 | 122.1588 | 122.3053 | 0.041199
1731.0156 | 122.4792 | -122.2183 | -0.013733 | 0.17426 | -0.0029351 | -0.060099 | 0.020561 | -0.012328 | -0.0043023 | -0.0063297 | 0.12894 | 0.013651 | 0.017276 | 0.022986 | 0.017224 | 0.013225 | 0.11444 | 0.082397 | 0.14191 | 0.07782 | -0.086975 | 0.12817 | 0.018311 | 0.13733 | 0.11444 | 0.036621 | -0.073242 | -0.073242 | 0.10529 | 0.050354 | 122.3465 | 122.2366 | -0.073242 | 122.3007 | 122.2961 | 0.059509 | 0.12817 | 122.3236 | 122.2687 | -0.059509 | 122.3557 | 122.2549 | -0.013733 | -0.059509 | 122.1313 | 122.3328 | 122.3602 | 0.032044 | 122.1451 | 122.1451 | 122.3328 | 0.064087
1732.7031 | 122.4838 | -122.2458 | 0.009155 | 0.067444 | -0.0052851 | -0.060312 | 0.020348 | -0.012969 | -0.0057977 | -0.0052615 | 0.067902 | 0.011942 | 0.01514 | 0.022772 | 0.014875 | 0.016216 | 0.045776 | 0.027466 | 0.10071 | 0.050354 | -0.07782 | 0.10986 | 0.009155 | 0.086975 | 0.073242 | -0.004578 | -0.073242 | -0.050354 | 0.11902 | 0.032043 | 122.3557 | 122.2549 | -0.086975 | 122.2733 | 122.2961 | 0.041199 | 0.036621 | 122.3648 | 122.2778 | -0.082397 | 122.3328 | 122.2412 | -0.036621 | -0.059509 | 122.168 | 122.2916 | 122.3465 | 0 | 122.1725 | 122.1954 | 122.319 | 0.022888
1734.4688 | 122.4106 | -122.2595 | 0.032043 | 0.067444 | -0.00058528 | -0.062235 | 0.01992 | -0.014251 | 0.0038153 | -0.0039797 | -0.00076274 | 0.016855 | 0.018558 | 0.024695 | 0.019147 | 0.013866 | 0 | -0.082397 | -0.013733 | -0.009155 | -0.041199 | 0.086975 | -0.027466 | -0.009155 | -0.036621 | -0.15564 | -0.045776 | -0.036621 | 0.068665 | 0.022888 | 122.3465 | 122.2321 | -0.073242 | 122.1771 | 122.2504 | 0.018311 | -0.032043 | 122.3282 | 122.2824 | -0.077819 | 122.2504 | 122.1039 | -0.17853 | -0.068664 | 122.2183 | 122.2595 | 122.2458 | -0.059509 | 122.2137 | 122.2229 | 122.2229 | -0.009155
1736.1562 | 122.4106 | -122.2687 | 0.027466 | -0.062256 | -0.00058528 | -0.062448 | 0.022697 | -0.013183 | -0.0019525 | -0.0048343 | -0.1152 | 0.014505 | 0.017062 | 0.022986 | 0.015515 | 0.011516 | 0.068665 | 0.018311 | 0.054932 | 0.036621 | -0.041199 | 0.07782 | -0.009155 | 0.07782 | 0.073242 | -0.054932 | -0.068665 | -0.041199 | 0.073242 | 0.004578 | 122.3465 | 122.2595 | -0.068665 | 122.287 | 122.3053 | 0.045776 | 0.041199 | 122.3419 | 122.2733 | -0.096131 | 122.3465 | 122.2137 | -0.05951 | -0.068665 | 122.2275 | 122.3373 | 122.3236 | -0.036621 | 122.2 | 122.2275 | 122.3419 | -0.022888
1737.9375 | 122.4838 | -122.2 | -0.009155 | 0.13611 | -0.0048579 | -0.060526 | 0.020561 | -0.013396 | -0.0036615 | -0.0063297 | 0.18234 | 0.013223 | 0.017489 | 0.022131 | 0.016584 | 0.016003 | 0.09613 | 0.073242 | 0.13733 | 0.07782 | -0.10529 | 0.12817 | 0.004578 | 0.13275 | 0.12817 | 0.041199 | -0.10529 | -0.07782 | 0.1236 | 0.045776 | 122.3282 | 122.2046 | -0.096131 | 122.2733 | 122.2778 | 0.073242 | 0.10528 | 122.3236 | 122.2458 | -0.096131 | 122.3328 | 122.2412 | -0.004577 | -0.068665 | 122.0947 | 122.2961 | 122.3373 | 0.013733 | 122.0947 | 122.1222 | 122.3282 | 0.054931
1739.6875 | 122.3923 | -122.2961 | 0.036621 | 0.10559 | -0.0016535 | -0.060099 | 0.018211 | -0.01361 | -2.988e-05 | -0.0039797 | 0.014496 | 0.016428 | 0.018344 | 0.02384 | 0.018079 | 0.016003 | 0.004578 | -0.07782 | -0.004578 | -0.022888 | -0.059509 | 0.086975 | -0.013733 | -0.013733 | -0.013733 | -0.12817 | -0.027466 | -0.041199 | 0.073242 | -0.027466 | 122.3831 | 122.2824 | -0.09613 | 122.2183 | 122.2733 | -0.009155 | -0.032043 | 122.3694 | 122.2687 | -0.064087 | 122.2824 | 122.168 | -0.10071 | -0.07782 | 122.2366 | 122.3007 | 122.2916 | -0.050354 | 122.2687 | 122.2549 | 122.2824 | -0.064087
1741.3906 | 122.525 | -122.2137 | -0.027466 | 0.15137 | -0.0018671 | -0.061167 | 0.021202 | -0.013824 | -0.0023797 | -0.0037661 | 0.10605 | 0.016 | 0.017276 | 0.022345 | 0.015088 | 0.015575 | 0.064087 | 0.022888 | 0.10529 | 0.050354 | -0.07782 | 0.11444 | 0.013733 | 0.12817 | 0.11444 | 0.018311 | -0.086975 | -0.064087 | 0.10986 | 0.054932 | 122.3282 | 122.2275 | -0.050354 | 122.2366 | 122.2641 | 0.036621 | 0.091553 | 122.3236 | 122.2687 | -0.059509 | 122.3419 | 122.2321 | -0.036621 | -0.036621 | 122.1359 | 122.2778 | 122.319 | 0.041199 | 122.1268 | 122.1497 | 122.3282 | 0.082398
1743.1719 | 122.374 | -122.2733 | 0.013733 | -0.016479 | -0.00058528 | -0.060312 | 0.020775 | -0.012542 | 0.00061092 | -0.0024845 | 0.022125 | 0.017282 | 0.020053 | 0.023199 | 0.018506 | 0.017071 | 0.018311 | -0.018311 | 0.027466 | 0.018311 | -0.041199 | 0.09613 | -0.013733 | 0.022888 | 0.009155 | -0.10529 | -0.050354 | -0.027466 | 0.091553 | -0.004578 | 122.3694 | 122.2595 | -0.054932 | 122.2549 | 122.2916 | 0.032044 | 0.004578 | 122.3648 | 122.2687 | -0.064087 | 122.2961 | 122.168 | -0.10071 | -0.041199 | 122.2321 | 122.2916 | 122.3007 | -0.027466 | 122.2229 | 122.2458 | 122.2824 | -0.018311
1744.875 | 122.4289 | -122.3145 | -0.013733 | 0.13611 | -0.0022943 | -0.059244 | 0.01992 | -0.013824 | -0.0013117 | -0.0035525 | 0.11368 | 0.024759 | 0.026248 | 0.023413 | 0.015943 | 0.017071 | -0.022888 | -0.086975 | 0.004578 | -0.004578 | -0.036621 | 0.07782 | -0.013733 | 0.009155 | -0.013733 | -0.091553 | -0.036621 | -0.027466 | 0.068665 | 0.009155 | 122.3923 | 122.3007 | -0.022888 | 122.2275 | 122.3099 | 0.009155 | -0.009155 | 122.3831 | 122.3236 | -0.022888 | 122.3236 | 122.2229 | -0.10071 | -0.013733 | 122.2778 | 122.2916 | 122.319 | 0 | 122.2778 | 122.287 | 122.3007 | 0.022888
1746.625 | 122.3877 | -122.3373 | 0.018311 | -0.21484 | -0.00058528 | -0.059244 | 0.026756 | -0.014037 | -0.0062249 | -0.0048343 | -0.13046 | 0.023904 | 0.025821 | 0.022345 | 0.010389 | 0.016643 | -0.018311 | -0.036621 | 0.018311 | -0.009155 | -0.068665 | 0.10071 | -0.027466 | -0.004578 | 0.018311 | -0.07782 | -0.036621 | -0.022888 | 0.068665 | 0 | 122.438 | 122.3099 | -0.086976 | 122.3007 | 122.3282 | 0.018311 | -0.036622 | 122.406 | 122.3373 | -0.054932 | 122.3328 | 122.2595 | -0.07782 | -0.041199 | 122.2687 | 122.319 | 122.3557 | -0.045777 | 122.3007 | 122.3145 | 122.3557 | -0.018311
1748.375 | 122.3923 | -122.2778 | 0.027466 | -0.1767 | -0.0012263 | -0.062021 | 0.025047 | -0.012969 | -0.0032343 | -0.0063297 | -0.1152 | 0.021341 | 0.026675 | 0.021704 | 0.01167 | 0.017498 | 0 | -0.009155 | 0.050354 | 0 | -0.041199 | 0.086975 | -0.032043 | 0.009155 | 0.041199 | -0.073242 | -0.050354 | -0.022888 | 0.064087 | 0.022888 | 122.3648 | 122.2458 | -0.068665 | 122.2687 | 122.2778 | 0.032043 | -0.027466 | 122.3419 | 122.3007 | -0.07782 | 122.287 | 122.2046 | -0.09613 | -0.050354 | 122.2366 | 122.2778 | 122.3282 | -0.059509 | 122.2275 | 122.2549 | 122.319 | -0.004578
1750.0625 | 122.5388 | -122.2275 | 0.009155 | -0.069885 | -0.0044305 | -0.061167 | 0.021202 | -0.014251 | -0.0075067 | -0.0067569 | -0.03891 | 0.020486 | 0.025393 | 0.022772 | 0.010389 | 0.015575 | 0.054932 | 0.064087 | 0.1236 | 0.068665 | -0.086975 | 0.11444 | 0.018311 | 0.14648 | 0.14648 | 0.054932 | -0.091553 | -0.073242 | 0.10529 | 0.054932 | 122.3419 | 122.2458 | -0.09613 | 122.2916 | 122.2961 | 0.050354 | 0.045777 | 122.3328 | 122.2824 | -0.10071 | 122.374 | 122.2824 | 0 | -0.082397 | 122.1405 | 122.2824 | 122.3511 | 0.009156 | 122.1359 | 122.1542 | 122.374 | 0.045777
1751.8125 | 122.5204 | -122.2366 | -0.009155 | 0.15137 | 0.00026912 | -0.063517 | 0.023979 | -0.012755 | -0.00045708 | -0.0048343 | 0.12894 | 0.022195 | 0.027102 | 0.023627 | 0.015302 | 0.015789 | 0.050354 | -0.013733 | 0.054932 | 0.022888 | -0.07782 | 0.09613 | 0 | 0.10529 | 0.11444 | 0.013733 | -0.086975 | -0.073242 | 0.10529 | 0.036621 | 122.3328 | 122.2366 | -0.068665 | 122.2229 | 122.2595 | 0.022888 | 0.059509 | 122.3419 | 122.2733 | -0.07782 | 122.3419 | 122.2504 | -0.022888 | -0.064087 | 122.1588 | 122.287 | 122.2916 | 0.009155 | 122.1497 | 122.1634 | 122.3511 | 0.045776
1753.5625 | 122.3923 | -122.2549 | 0.022888 | -0.016479 | 0.00069632 | -0.061808 | 0.018425 | -0.011687 | 0.00061092 | -0.0037661 | -0.016022 | 0.026468 | 0.025607 | 0.024908 | 0.017438 | 0.01408 | 0.050354 | -0.022888 | 0.036621 | 0.027466 | -0.036621 | 0.086975 | -0.013733 | 0.022888 | 0.018311 | -0.086975 | -0.059509 | -0.032043 | 0.07782 | 0.004578 | 122.3419 | 122.2412 | -0.059509 | 122.2321 | 122.2824 | 0.041199 | 0.027466 | 122.3328 | 122.2595 | -0.082397 | 122.2778 | 122.168 | -0.091553 | -0.054931 | 122.2183 | 122.3053 | 122.2916 | -0.036621 | 122.1954 | 122.2229 | 122.2733 | -0.01831
1755.25 | 122.4014 | -122.2733 | 0.018311 | 0.029297 | -0.00058528 | -0.062662 | 0.022057 | -0.012328 | -2.988e-05 | -0.0031253 | 0.029755 | 0.025827 | 0.029025 | 0.023199 | 0.017011 | 0.014721 | 0.004578 | -0.054932 | 0.013733 | 0.027466 | -0.054932 | 0.082397 | -0.018311 | 0.018311 | 0 | -0.10529 | -0.041199 | -0.018311 | 0.07782 | 0.013733 | 122.3557 | 122.2549 | -0.073243 | 122.2183 | 122.3007 | 0.045777 | -0.013733 | 122.3511 | 122.287 | -0.05951 | 122.2916 | 122.168 | -0.11902 | -0.036622 | 122.2183 | 122.2778 | 122.287 | -0.036622 | 122.2321 | 122.2549 | 122.2733 | -0.004578
1757.0156 | 122.5021 | -122.2458 | -0.018311 | 0.13611 | -0.00058528 | -0.060099 | 0.023552 | -0.011474 | -0.0077203 | -0.0044071 | 0.15182 | 0.023264 | 0.025821 | 0.023627 | 0.013166 | 0.018352 | 0.082397 | 0.082397 | 0.14648 | 0.073242 | -0.091553 | 0.11902 | 0.018311 | 0.12817 | 0.11902 | 0.027466 | -0.086975 | -0.064087 | 0.1236 | 0.022888 | 122.3648 | 122.2641 | -0.073242 | 122.3282 | 122.319 | 0.054931 | 0.10071 | 122.3694 | 122.2687 | -0.068664 | 122.374 | 122.2733 | 0.004578 | -0.045776 | 122.1542 | 122.3282 | 122.3923 | 0.036622 | 122.1588 | 122.1817 | 122.3648 | 0.041199
1758.7188 | 122.4243 | -122.2641 | 0.022888 | -0.046997 | -0.0022943 | -0.06138 | 0.021202 | -0.014251 | -0.00045708 | -0.0041933 | -0.077057 | 0.023691 | 0.023257 | 0.024908 | 0.016797 | 0.013866 | 0.082397 | -0.004578 | 0.064087 | 0.041199 | -0.045776 | 0.091553 | -0.022888 | 0.07782 | 0.050354 | -0.045776 | -0.054932 | -0.036621 | 0.082397 | 0.013733 | 122.3557 | 122.2412 | -0.068664 | 122.2595 | 122.3053 | 0.064087 | 0.059509 | 122.3465 | 122.2778 | -0.07782 | 122.3419 | 122.2183 | -0.059509 | -0.059509 | 122.2183 | 122.3465 | 122.3282 | -0.045776 | 122.2092 | 122.2275 | 122.3145 | -0.009155
1760.5156 | 122.4564 | -122.2504 | 0.018311 | -0.092773 | 0.0019781 | -0.062662 | 0.026756 | -0.010406 | -0.0023797 | -0.0026981 | -0.084686 | 0.022409 | 0.027743 | 0.022345 | 0.014234 | 0.015362 | 0.041199 | -0.013733 | 0.054932 | 0.045776 | -0.036621 | 0.10071 | -0.036621 | 0.068665 | 0.07782 | -0.041199 | -0.045776 | -0.036621 | 0.07782 | 0.018311 | 122.3511 | 122.2137 | -0.054932 | 122.2366 | 122.2961 | 0.082397 | 0.022888 | 122.3282 | 122.2687 | -0.064087 | 122.319 | 122.2092 | -0.05951 | -0.054932 | 122.2137 | 122.2916 | 122.3053 | -0.054932 | 122.2046 | 122.2137 | 122.3282 | 0
1762.2031 | 122.5433 | -122.2137 | -0.027466 | 0.159 | -0.0025079 | -0.060099 | 0.018211 | -0.011046 | -0.0045161 | -0.0041933 | 0.12131 | 0.023477 | 0.024966 | 0.024054 | 0.018079 | 0.015148 | 0.050354 | 0.022888 | 0.091553 | 0.059509 | -0.07782 | 0.1236 | 0.013733 | 0.10529 | 0.10986 | 0.018311 | -0.09613 | -0.059509 | 0.10986 | 0.027466 | 122.3373 | 122.2275 | -0.050354 | 122.2366 | 122.2733 | 0.045776 | 0.07782 | 122.3236 | 122.2412 | -0.068664 | 122.319 | 122.2321 | -0.009155 | -0.032043 | 122.1359 | 122.2641 | 122.3053 | 0.041199 | 122.1176 | 122.1542 | 122.3236 | 0.054932
1763.9375 | 122.5067 | -122.2549 | 0.022888 | 0.082703 | -0.0057123 | -0.060953 | 0.020348 | -0.014037 | -0.0094293 | -0.0084659 | 0.098419 | 0.021127 | 0.023684 | 0.022559 | 0.012525 | 0.01878 | 0.018311 | 0.027466 | 0.082397 | 0.050354 | -0.086975 | 0.11444 | 0.013733 | 0.07782 | 0.082397 | -0.004578 | -0.07782 | -0.059509 | 0.09613 | 0.041199 | 122.3694 | 122.2687 | -0.10986 | 122.2824 | 122.3053 | 0.036621 | -0.004577 | 122.3511 | 122.2961 | -0.10071 | 122.3328 | 122.2504 | -0.045777 | -0.082397 | 122.168 | 122.2733 | 122.3373 | -0.009155 | 122.1771 | 122.1954 | 122.3373 | 0.018311
1765.625 | 122.525 | -122.2504 | 0 | 0.029297 | -0.0061395 | -0.060526 | 0.022484 | -0.013824 | -0.0060113 | -0.0080387 | 0.075531 | 0.022623 | 0.023471 | 0.021704 | 0.012311 | 0.016857 | 0.050354 | 0.013733 | 0.091553 | 0.041199 | -0.07782 | 0.11902 | 0.013733 | 0.07782 | 0.07782 | -0.009155 | -0.059509 | -0.068665 | 0.09613 | 0.018311 | 122.3694 | 122.2641 | -0.07782 | 122.2641 | 122.2916 | 0.027466 | 0.050354 | 122.3465 | 122.2687 | -0.059509 | 122.3282 | 122.2412 | -0.027466 | -0.068665 | 122.1725 | 122.3007 | 122.3419 | 0.013733 | 122.1909 | 122.1817 | 122.3282 | 0.018311
1767.3125 | 122.4655 | -122.2733 | 0.032043 | -0.1004 | -0.0035761 | -0.060953 | 0.017357 | -0.012755 | -0.00045708 | -0.0050479 | -0.13046 | 0.024545 | 0.023898 | 0.026831 | 0.017224 | 0.013225 | 0.068665 | -0.004578 | 0.045776 | 0.032043 | -0.041199 | 0.091553 | -0.018311 | 0.059509 | 0.064087 | -0.045776 | -0.059509 | -0.050354 | 0.07782 | 0.013733 | 122.3648 | 122.2549 | -0.073242 | 122.2687 | 122.3053 | 0.050354 | 0.036622 | 122.3511 | 122.287 | -0.091552 | 122.3328 | 122.2275 | -0.059509 | -0.082397 | 122.2321 | 122.3419 | 122.319 | -0.050354 | 122.2137 | 122.2229 | 122.3373 | -0.01831
1769 | 122.5571 | -122.2275 | 0.004578 | -0.024109 | -0.0016535 | -0.060526 | 0.023552 | -0.012969 | -0.0077203 | -0.0048343 | -0.069428 | 0.020273 | 0.02518 | 0.021063 | 0.011457 | 0.012798 | 0.054932 | 0.064087 | 0.13275 | 0.073242 | -0.091553 | 0.10071 | 0.018311 | 0.1236 | 0.15106 | 0.059509 | -0.059509 | -0.064087 | 0.10529 | 0.041199 | 122.3282 | 122.2458 | -0.096131 | 122.2916 | 122.3007 | 0.054931 | 0.050354 | 122.3328 | 122.2687 | -0.064087 | 122.3511 | 122.287 | 0.01831 | -0.068665 | 122.1359 | 122.2824 | 122.3602 | 0.013733 | 122.168 | 122.1634 | 122.3785 | 0.036621
1770.6875 | 122.5388 | -122.2458 | -0.004578 | -0.11566 | -0.0012263 | -0.062235 | 0.024834 | -0.011901 | -0.0064387 | -0.0059023 | -0.13046 | 0.019632 | 0.02518 | 0.024908 | 0.013593 | 0.014934 | 0.11444 | 0.10071 | 0.15106 | 0.082397 | -0.086975 | 0.10986 | 0.022888 | 0.12817 | 0.16479 | 0.054932 | -0.091553 | -0.059509 | 0.10529 | 0.045776 | 122.3557 | 122.2687 | -0.082397 | 122.3465 | 122.3282 | 0.059509 | 0.11902 | 122.3511 | 122.2916 | -0.086975 | 122.374 | 122.3007 | 0.009156 | -0.054931 | 122.1588 | 122.3602 | 122.3969 | 0.027466 | 122.1542 | 122.1863 | 122.4106 | 0.050354
1772.375 | 122.5067 | -122.2549 | -0.004578 | 0.11322 | -0.0061395 | -0.060099 | 0.019066 | -0.014037 | -0.0053705 | -0.0061161 | 0.13657 | 0.022836 | 0.023471 | 0.022131 | 0.015729 | 0.015148 | 0.09613 | 0.050354 | 0.11444 | 0.059509 | -0.082397 | 0.10529 | 0 | 0.10071 | 0.091553 | 0.009155 | -0.09613 | -0.068665 | 0.11902 | 0.041199 | 122.3602 | 122.2549 | -0.077819 | 122.3053 | 122.3145 | 0.059509 | 0.10071 | 122.374 | 122.2961 | -0.091552 | 122.3557 | 122.2641 | -0.032044 | -0.064087 | 122.1725 | 122.3511 | 122.3694 | 0.004578 | 122.1588 | 122.1863 | 122.3465 | 0.045777
1774.0625 | 122.4609 | -122.2687 | 0 | 0.11322 | -0.0022943 | -0.059885 | 0.016716 | -0.015533 | 0.0021063 | -0.0063297 | 0.060272 | 0.024118 | 0.024539 | 0.023413 | 0.019147 | 0.01408 | 0.027466 | -0.091553 | -0.009155 | 0 | -0.045776 | 0.082397 | -0.022888 | 0.022888 | -0.018311 | -0.11444 | -0.041199 | -0.018311 | 0.082397 | 0.009155 | 122.3511 | 122.2458 | -0.045776 | 122.1771 | 122.2687 | 0.022888 | 0.027466 | 122.3511 | 122.2778 | -0.041199 | 122.2916 | 122.1542 | -0.1236 | -0.018311 | 122.2229 | 122.2961 | 122.2595 | -0.022888 | 122.2275 | 122.2504 | 122.2504 | 0.009155
1775.75 | 122.438 | -122.3099 | 0.036621 | 0.059815 | -0.0022943 | -0.061594 | 0.019707 | -0.011901 | 0.0012519 | -0.0037661 | 0.0068663 | 0.023264 | 0.024966 | 0.021918 | 0.019361 | 0.015362 | -0.018311 | -0.082397 | -0.018311 | -0.018311 | -0.050354 | 0.091553 | -0.022888 | 0.004578 | -0.022888 | -0.13733 | -0.036621 | -0.036621 | 0.068665 | 0.004578 | 122.4014 | 122.287 | -0.086975 | 122.2275 | 122.2916 | 0.004577 | -0.054932 | 122.3785 | 122.3145 | -0.073242 | 122.3145 | 122.1725 | -0.14191 | -0.073242 | 122.2595 | 122.2916 | 122.2916 | -0.059509 | 122.2733 | 122.2733 | 122.287 | -0.032043
1777.4375 | 122.4701 | -122.2961 | 0.013733 | -0.15381 | -0.00015808 | -0.059244 | 0.023338 | -0.011901 | -0.0030207 | -0.0039797 | -0.16098 | 0.022836 | 0.025607 | 0.024054 | 0.014661 | 0.013653 | 0.022888 | -0.032043 | 0.022888 | 0.032043 | -0.064087 | 0.073242 | -0.032043 | 0.050354 | 0.064087 | -0.059509 | -0.059509 | -0.032043 | 0.068665 | -0.004578 | 122.3694 | 122.2641 | -0.07782 | 122.2641 | 122.3282 | 0.064086 | 0.009155 | 122.3648 | 122.2916 | -0.073242 | 122.3465 | 122.2366 | -0.054931 | -0.045776 | 122.2321 | 122.319 | 122.319 | -0.045776 | 122.2366 | 122.2641 | 122.3602 | -0.018311
1779.1406 | 122.4884 | -122.2733 | 0.032043 | -0.085144 | -0.0037897 | -0.062662 | 0.021843 | -0.012755 | 0.0012519 | -0.0035525 | -0.12283 | 0.022836 | 0.023684 | 0.024481 | 0.015515 | 0.015575 | 0.036621 | 0.013733 | 0.050354 | 0.027466 | -0.054932 | 0.068665 | -0.018311 | 0.064087 | 0.07782 | -0.041199 | -0.050354 | -0.032043 | 0.073242 | 0.018311 | 122.3419 | 122.2549 | -0.086975 | 122.287 | 122.3007 | 0.045777 | 0.004578 | 122.3465 | 122.2916 | -0.082397 | 122.3373 | 122.2321 | -0.05951 | -0.064086 | 122.2183 | 122.3099 | 122.3236 | -0.050354 | 122.2229 | 122.2412 | 122.3511 | -0.013732
1780.8438 | 122.4655 | -122.3053 | 0.027466 | 0.059815 | -0.0040033 | -0.059458 | 0.019066 | -0.012328 | -0.00088448 | -0.0029117 | 0.075531 | 0.024545 | 0.023257 | 0.023627 | 0.018933 | 0.014934 | -0.032043 | -0.10071 | -0.009155 | -0.004578 | -0.041199 | 0.068665 | -0.036621 | 0 | -0.013733 | -0.10986 | -0.059509 | -0.013733 | 0.064087 | 0.009155 | 122.374 | 122.2687 | -0.068665 | 122.2046 | 122.3007 | 0.032043 | -0.059509 | 122.3694 | 122.3145 | -0.086975 | 122.3053 | 122.1954 | -0.11902 | -0.041199 | 122.2641 | 122.2733 | 122.2961 | -0.064087 | 122.2458 | 122.2916 | 122.2916 | -0.018311
1782.5469 | 122.5479 | -122.2549 | -0.018311 | 0.14374 | -0.0020807 | -0.059885 | 0.022057 | -0.013183 | -0.0034479 | -0.0041933 | 0.15945 | 0.023477 | 0.025393 | 0.022131 | 0.017438 | 0.014507 | -0.009155 | -0.050354 | 0.036621 | 0.009155 | -0.036621 | 0.10071 | -0.018311 | 0.068665 | 0.059509 | -0.036621 | -0.054932 | -0.054932 | 0.10071 | 0.027466 | 122.3557 | 122.2366 | -0.01831 | 122.2046 | 122.2641 | 0.027466 | 0.009156 | 122.3557 | 122.2824 | -0.036621 | 122.3236 | 122.2183 | -0.064087 | -0.036621 | 122.2183 | 122.2458 | 122.2916 | 0 | 122.2 | 122.2 | 122.3145 | 0.045777
1784.2656 | 122.4792 | -122.3007 | 0.009155 | -0.13092 | -0.00079888 | -0.06074 | 0.025688 | -0.013183 | -0.0038751 | -0.0044071 | -0.16861 | 0.023904 | 0.028598 | 0.025336 | 0.013806 | 0.015148 | -0.009155 | -0.050354 | 0.022888 | 0.009155 | -0.068665 | 0.086975 | -0.027466 | 0.009155 | 0.045776 | -0.073242 | -0.059509 | -0.027466 | 0.068665 | 0.004578 | 122.3877 | 122.2733 | -0.07782 | 122.2504 | 122.3099 | 0.036621 | -0.01831 | 122.3694 | 122.3053 | -0.068664 | 122.3099 | 122.2275 | -0.07782 | -0.036621 | 122.2321 | 122.2916 | 122.3236 | -0.036621 | 122.2412 | 122.2733 | 122.3465 | -0.004577
1785.9844 | 122.5296 | -122.2778 | 0 | 0.18188 | -0.0065667 | -0.06138 | 0.020561 | -0.014251 | -0.0064387 | -0.0046207 | 0.18234 | 0.020273 | 0.023257 | 0.021063 | 0.015515 | 0.016003 | 0.091553 | 0.07782 | 0.14191 | 0.082397 | -0.091553 | 0.1236 | 0.004578 | 0.13275 | 0.13733 | 0.045776 | -0.086975 | -0.073242 | 0.10986 | 0.032043 | 122.4014 | 122.2824 | -0.091553 | 122.3557 | 122.3602 | 0.077819 | 0.091553 | 122.3877 | 122.3099 | -0.086975 | 122.4106 | 122.3236 | 0.013733 | -0.073242 | 122.1863 | 122.3694 | 122.4197 | 0.004578 | 122.1909 | 122.2046 | 122.4152 | 0.032043
1787.6719 | 122.4655 | -122.3053 | 0.009155 | -0.1004 | -0.0016535 | -0.063944 | 0.022484 | -0.013824 | -0.00067088 | -0.0039797 | -0.077057 | 0.025186 | 0.024966 | 0.024054 | 0.015302 | 0.014294 | 0.054932 | -0.009155 | 0.064087 | 0.036621 | -0.045776 | 0.091553 | -0.022888 | 0.073242 | 0.073242 | -0.041199 | -0.054932 | -0.045776 | 0.07782 | 0.027466 | 122.3969 | 122.2824 | -0.054931 | 122.2961 | 122.3419 | 0.059509 | 0.045777 | 122.3831 | 122.3328 | -0.064087 | 122.3785 | 122.2641 | -0.068665 | -0.054931 | 122.2595 | 122.3602 | 122.3694 | -0.032043 | 122.2504 | 122.2595 | 122.3785 | 0.018311
1789.4219 | 122.5204 | -122.3053 | 0.009155 | -0.1767 | -0.0027215 | -0.060953 | 0.027611 | -0.012115 | -0.0077203 | -0.0059023 | -0.092316 | 0.01835 | 0.027102 | 0.024054 | 0.012738 | 0.017071 | 0.086975 | 0.091553 | 0.15106 | 0.073242 | -0.082397 | 0.11444 | 0.004578 | 0.10986 | 0.16479 | 0.041199 | -0.091553 | -0.068665 | 0.09613 | 0.027466 | 122.4197 | 122.3099 | -0.091552 | 122.3969 | 122.3785 | 0.068664 | 0.07782 | 122.4014 | 122.3328 | -0.10071 | 122.4152 | 122.3465 | 0.013733 | -0.07782 | 122.2229 | 122.3923 | 122.4564 | -0.004577 | 122.2137 | 122.2366 | 122.4701 | 0.018311
1791.1094 | 122.5708 | -122.2733 | -0.009155 | -0.0012209 | -0.0078485 | -0.060099 | 0.024834 | -0.01361 | -0.0068659 | -0.0084659 | 0.037384 | 0.020486 | 0.026889 | 0.02149 | 0.012738 | 0.015789 | 0.022888 | 0.018311 | 0.082397 | 0.045776 | -0.064087 | 0.11902 | 0.013733 | 0.082397 | 0.10071 | 0.018311 | -0.082397 | -0.054932 | 0.10986 | 0.022888 | 122.3923 | 122.287 | -0.054932 | 122.2916 | 122.319 | 0.032043 | 0.032043 | 122.3831 | 122.2961 | -0.073242 | 122.3557 | 122.2916 | -0.004577 | -0.045777 | 122.2092 | 122.2961 | 122.3557 | 0.022888 | 122.1909 | 122.2183 | 122.374 | 0.032043
1792.8438 | 122.5708 | -122.2687 | 0 | 0.12848 | -0.0042169 | -0.06138 | 0.021202 | -0.010406 | -2.988e-05 | -0.0044071 | 0.15945 | 0.02305 | 0.02518 | 0.025336 | 0.015515 | 0.014294 | 0.022888 | -0.064087 | 0.022888 | 0.004578 | -0.022888 | 0.09613 | -0.022888 | 0.073242 | 0.032043 | -0.041199 | -0.059509 | -0.045776 | 0.10529 | 0.027466 | 122.3648 | 122.2458 | -0.022888 | 122.2046 | 122.2733 | 0.027466 | 0.022888 | 122.374 | 122.2961 | -0.059509 | 122.3419 | 122.2275 | -0.068665 | -0.045776 | 122.2458 | 122.2916 | 122.2916 | -0.022888 | 122.2092 | 122.2229 | 122.3007 | 0.027466
1794.5469 | 122.5708 | -122.2778 | -0.018311 | 0.14374 | -0.0048579 | -0.060312 | 0.01992 | -0.012969 | -0.0045161 | -0.0029117 | 0.1442 | 0.023264 | 0.024753 | 0.022345 | 0.017438 | 0.014934 | 0.086975 | 0.059509 | 0.10986 | 0.07782 | -0.082397 | 0.1236 | 0.036621 | 0.1236 | 0.11444 | 0.022888 | -0.091553 | -0.07782 | 0.12817 | 0.050354 | 122.4014 | 122.3145 | -0.064086 | 122.3373 | 122.3557 | 0.041199 | 0.10529 | 122.406 | 122.3282 | -0.073242 | 122.4014 | 122.3007 | -0.027466 | -0.059509 | 122.1954 | 122.3648 | 122.3877 | 0.054932 | 122.1863 | 122.2 | 122.3923 | 0.068665
1796.2812 | 122.5388 | -122.2687 | 0.009155 | 0.067444 | -0.0048579 | -0.059458 | 0.022057 | -0.014251 | -0.0066523 | -0.0063297 | 0.11368 | 0.021768 | 0.024966 | 0.022345 | 0.014447 | 0.01643 | 0.059509 | 0.022888 | 0.10071 | 0.041199 | -0.082397 | 0.10986 | 0.009155 | 0.082397 | 0.07782 | -0.004578 | -0.064087 | -0.045776 | 0.11444 | 0.022888 | 122.3785 | 122.2778 | -0.091552 | 122.2916 | 122.3099 | 0.032044 | 0.050354 | 122.3831 | 122.2916 | -0.073242 | 122.3511 | 122.2641 | -0.027466 | -0.054931 | 122.1863 | 122.3282 | 122.3694 | 0 | 122.2046 | 122.2229 | 122.3465 | 0.013733
1797.9844 | 122.5891 | -122.2733 | 0 | -0.0088499 | -0.0067805 | -0.060312 | 0.022697 | -0.014037 | -0.0064387 | -0.0061161 | 0.014496 | 0.022623 | 0.028598 | 0.022986 | 0.011243 | 0.012371 | 0.054932 | 0.018311 | 0.09613 | 0.045776 | -0.07782 | 0.12817 | 0 | 0.11444 | 0.10529 | 0.036621 | -0.068665 | -0.064087 | 0.11902 | 0.032043 | 122.4014 | 122.2733 | -0.07782 | 122.2916 | 122.319 | 0.045776 | 0.054932 | 122.3923 | 122.3053 | -0.068665 | 122.3877 | 122.3099 | 0.004578 | -0.064087 | 122.1954 | 122.3282 | 122.3694 | 0 | 122.2046 | 122.2092 | 122.3785 | 0.032043
1799.6875 | 122.5433 | -122.3007 | 0.004578 | -0.16144 | -0.0012263 | -0.063303 | 0.024193 | -0.013396 | -0.0053705 | -0.0082523 | -0.13046 | 0.023477 | 0.027102 | 0.021704 | 0.012952 | 0.014934 | 0.10071 | 0.10529 | 0.15564 | 0.086975 | -0.086975 | 0.10529 | 0.009155 | 0.11444 | 0.16479 | 0.041199 | -0.07782 | -0.054932 | 0.10529 | 0.041199 | 122.406 | 122.3099 | -0.091553 | 122.406 | 122.3877 | 0.07782 | 0.09613 | 122.406 | 122.3419 | -0.082398 | 122.4152 | 122.3419 | 0 | -0.05951 | 122.2137 | 122.4014 | 122.4564 | 0.004577 | 122.2229 | 122.2458 | 122.4655 | 0.036621
1801.375 | 122.4655 | -122.3511 | 0.032043 | -0.19196 | -0.0012263 | -0.06074 | 0.025261 | -0.012969 | -0.0051569 | -0.0050479 | -0.20676 | 0.023264 | 0.028811 | 0.024695 | 0.015729 | 0.014721 | 0.068665 | 0.059509 | 0.10529 | 0.068665 | -0.082397 | 0.09613 | -0.009155 | 0.064087 | 0.091553 | -0.027466 | -0.059509 | -0.050354 | 0.082397 | -0.004578 | 122.4472 | 122.3419 | -0.11444 | 122.4106 | 122.4197 | 0.07782 | 0.036622 | 122.4335 | 122.3465 | -0.091552 | 122.4152 | 122.3236 | -0.022888 | -0.082397 | 122.2687 | 122.4197 | 122.4564 | -0.041198 | 122.2916 | 122.3007 | 122.4426 | -0.036621
1803.0625 | 122.5571 | -122.3007 | 0.009155 | 0.036926 | -0.0037897 | -0.060099 | 0.018639 | -0.012115 | -0.0062249 | -0.0052615 | 0.037384 | 0.021127 | 0.025821 | 0.022559 | 0.013806 | 0.015148 | 0.041199 | 0.036621 | 0.082397 | 0.032043 | -0.068665 | 0.10986 | 0.004578 | 0.091553 | 0.068665 | -0.018311 | -0.073242 | -0.059509 | 0.10986 | 0.022888 | 122.4106 | 122.3053 | -0.07782 | 122.3373 | 122.3328 | 0.027465 | 0.032044 | 122.4106 | 122.3236 | -0.082397 | 122.3923 | 122.2824 | -0.041199 | -0.068664 | 122.2321 | 122.3419 | 122.3831 | -0.004577 | 122.2275 | 122.2412 | 122.3694 | 0.013733
1804.7656 | 122.4792 | -122.3236 | 0.013733 | 0.097962 | -0.0020807 | -0.062876 | 0.01992 | -0.015746 | 0.00082452 | -0.0063297 | 0.060272 | 0.023477 | 0.024112 | 0.025336 | 0.020856 | 0.011944 | 0 | -0.073242 | -0.004578 | 0 | -0.032043 | 0.10986 | -0.022888 | 0.032043 | -0.032043 | -0.1236 | -0.036621 | -0.036621 | 0.064087 | 0.004578 | 122.4335 | 122.3007 | -0.045776 | 122.2504 | 122.3236 | 0.022888 | -0.013733 | 122.3877 | 122.3282 | -0.050354 | 122.3557 | 122.2 | -0.12817 | -0.050354 | 122.2916 | 122.3236 | 122.319 | -0.036621 | 122.287 | 122.287 | 122.2916 | -0.009155
1806.4844 | 122.4518 | -122.3236 | 0.013733 | 0.036926 | -0.0031489 | -0.060953 | 0.020134 | -0.014251 | -0.00024348 | -0.0020571 | -0.00076274 | 0.023904 | 0.025393 | 0.023413 | 0.01872 | 0.015575 | 0.018311 | -0.041199 | 0.018311 | -0.009155 | -0.036621 | 0.086975 | -0.018311 | 0.022888 | 0 | -0.1236 | -0.041199 | -0.027466 | 0.054932 | 0.018311 | 122.4106 | 122.3053 | -0.050354 | 122.2824 | 122.3145 | 0.009156 | 0.004578 | 122.3785 | 122.3419 | -0.054932 | 122.3465 | 122.2 | -0.14191 | -0.041199 | 122.287 | 122.3419 | 122.3419 | -0.032044 | 122.2824 | 122.2961 | 122.3236 | 0.004578
1808.1719 | 122.5937 | -122.3007 | -0.004578 | 0.0064086 | -0.0067805 | -0.05839 | 0.021416 | -0.010619 | -0.0081477 | -0.0054751 | 0.075531 | 0.020273 | 0.024966 | 0.021277 | 0.012097 | 0.015789 | 0.013733 | 0.018311 | 0.082397 | 0.050354 | -0.064087 | 0.10529 | -0.004578 | 0.07782 | 0.086975 | 0.009155 | -0.068665 | -0.068665 | 0.10071 | 0.041199 | 122.406 | 122.2961 | -0.059509 | 122.319 | 122.3511 | 0.054932 | 0.018311 | 122.4014 | 122.3419 | -0.064087 | 122.3785 | 122.3099 | -0.032044 | -0.064087 | 122.2366 | 122.3145 | 122.3831 | 0 | 122.2321 | 122.2321 | 122.3877 | 0.045777
1809.875 | 122.493 | -122.3236 | 0.018311 | -0.092773 | -0.0022943 | -0.061167 | 0.023552 | -0.014464 | 0.0023199 | -0.0020571 | -0.10757 | 0.024545 | 0.024112 | 0.023199 | 0.01637 | 0.013439 | 0.054932 | 0.009155 | 0.050354 | 0.041199 | -0.032043 | 0.073242 | -0.027466 | 0.064087 | 0.073242 | -0.036621 | -0.050354 | -0.032043 | 0.082397 | 0.022888 | 122.3968 | 122.2961 | -0.050354 | 122.3328 | 122.3648 | 0.068665 | 0.036621 | 122.406 | 122.3465 | -0.068665 | 122.3877 | 122.287 | -0.059509 | -0.050354 | 122.2916 | 122.3785 | 122.374 | -0.045777 | 122.2733 | 122.2916 | 122.3968 | 0.004577
1811.5781 | 122.4609 | -122.3373 | 0.009155 | -0.077515 | 0.00026912 | -0.063517 | 0.021416 | -0.01361 | 0.00061092 | -0.0041933 | -0.084686 | 0.024545 | 0.023684 | 0.025122 | 0.017224 | 0.013653 | 0.059509 | 0.022888 | 0.064087 | 0.032043 | -0.045776 | 0.082397 | -0.004578 | 0.073242 | 0.073242 | -0.050354 | -0.073242 | -0.045776 | 0.082397 | 0.022888 | 122.4197 | 122.3328 | -0.054931 | 122.3602 | 122.3694 | 0.036621 | 0.050354 | 122.4197 | 122.3602 | -0.082397 | 122.4106 | 122.287 | -0.073242 | -0.054931 | 122.2916 | 122.3969 | 122.4014 | -0.013733 | 122.2641 | 122.2916 | 122.4106 | 0.013733
1813.2969 | 122.4609 | -122.3602 | 0.036621 | -0.20721 | -0.0020807 | -0.060099 | 0.023125 | -0.015105 | -0.0077203 | -0.0050479 | -0.084686 | 0.023691 | 0.024966 | 0.022772 | 0.012952 | 0.016216 | 0.009155 | 0.018311 | 0.054932 | 0.032043 | -0.059509 | 0.091553 | -0.036621 | 0.022888 | 0.059509 | -0.068665 | -0.050354 | -0.018311 | 0.082397 | 0.018311 | 122.4518 | 122.3236 | -0.09613 | 122.3785 | 122.3923 | 0.068664 | -0.027466 | 122.4426 | 122.3785 | -0.086975 | 122.3831 | 122.2916 | -0.086976 | -0.054932 | 122.3007 | 122.3694 | 122.4152 | -0.073242 | 122.3099 | 122.3419 | 122.4197 | -0.01831
1815 | 122.5983 | -122.2824 | -0.004578 | -0.077515 | -0.0048579 | -0.059458 | 0.025261 | -0.011901 | -0.0079339 | -0.0056887 | -0.046539 | 0.021768 | 0.026034 | 0.021918 | 0.01167 | 0.014721 | 0.059509 | 0.086975 | 0.12817 | 0.068665 | -0.064087 | 0.1236 | 0.009155 | 0.13275 | 0.16022 | 0.073242 | -0.082397 | -0.064087 | 0.10986 | 0.050354 | 122.406 | 122.2916 | -0.059509 | 122.3694 | 122.3511 | 0.05951 | 0.064087 | 122.3923 | 122.3328 | -0.077819 | 122.4152 | 122.3557 | 0.022888 | -0.059509 | 122.2183 | 122.3419 | 122.4106 | 0.013733 | 122.2 | 122.2183 | 122.4426 | 0.054932
1816.7188 | 122.5845 | -122.3145 | 0.009155 | -0.1004 | -0.0020807 | -0.06138 | 0.025688 | -0.012328 | -0.0055841 | -0.0063297 | -0.1152 | 0.017709 | 0.02518 | 0.023199 | 0.011029 | 0.013225 | 0.10071 | 0.11902 | 0.17395 | 0.09613 | -0.073242 | 0.12817 | 0.004578 | 0.13275 | 0.1831 | 0.059509 | -0.09613 | -0.073242 | 0.10529 | 0.036621 | 122.4426 | 122.319 | -0.082397 | 122.4335 | 122.4106 | 0.091552 | 0.091553 | 122.4197 | 122.3511 | -0.10528 | 122.4472 | 122.374 | 0.022888 | -0.082397 | 122.2412 | 122.4152 | 122.4884 | -0.004577 | 122.2183 | 122.2412 | 122.4976 | 0.027466
1818.4688 | 122.4747 | -122.3373 | 0.036621 | 0.0064086 | -0.0031489 | -0.062876 | 0.021202 | -0.01361 | 0.0042425 | -0.0037661 | 0.037384 | 0.024545 | 0.025607 | 0.022559 | 0.018933 | 0.012798 | 0.027466 | -0.027466 | 0.009155 | 0.018311 | -0.054932 | 0.086975 | -0.013733 | 0.004578 | 0.009155 | -0.10071 | -0.050354 | -0.027466 | 0.068665 | 0.022888 | 122.4243 | 122.3236 | -0.091553 | 122.3099 | 122.3557 | 0.032044 | -0.009155 | 122.406 | 122.3602 | -0.086975 | 122.3419 | 122.2366 | -0.1236 | -0.064087 | 122.2824 | 122.3648 | 122.3465 | -0.050354 | 122.287 | 122.3099 | 122.3465 | -0.013733
1820.1719 | 122.4792 | -122.3282 | 0.032043 | -0.15381 | -0.0037897 | -0.059458 | 0.022697 | -0.011046 | -0.0068659 | -0.0026981 | -0.1152 | 0.01835 | 0.023898 | 0.021704 | 0.015515 | 0.014721 | 0.068665 | 0.086975 | 0.11902 | 0.073242 | -0.086975 | 0.10529 | 0 | 0.09613 | 0.15564 | 0.013733 | -0.059509 | -0.045776 | 0.11444 | 0.036621 | 122.4335 | 122.3282 | -0.11902 | 122.4152 | 122.4014 | 0.073242 | 0.036622 | 122.4426 | 122.3648 | -0.091552 | 122.4243 | 122.3419 | -0.022888 | -0.077819 | 122.2412 | 122.3969 | 122.4472 | -0.032043 | 122.2687 | 122.2824 | 122.4838 | 0.004578
1821.8594 | 122.525 | -122.319 | 0.013733 | -0.16144 | -0.0035761 | -0.062448 | 0.024406 | -0.0099784 | -0.0010981 | -0.0061161 | -0.17624 | 0.025613 | 0.026034 | 0.025336 | 0.016797 | 0.012798 | 0 | -0.050354 | 0.041199 | 0.009155 | -0.032043 | 0.07782 | -0.022888 | 0.018311 | 0.054932 | -0.045776 | -0.054932 | -0.041199 | 0.07782 | 0.018311 | 122.3969 | 122.2961 | -0.045776 | 122.2687 | 122.3282 | 0.032043 | -0.013733 | 122.3969 | 122.3373 | -0.068665 | 122.3373 | 122.2733 | -0.064087 | -0.054932 | 122.287 | 122.319 | 122.3602 | -0.036621 | 122.2641 | 122.2778 | 122.374 | 0.004578
1823.6562 | 122.4792 | -122.3328 | 0.032043 | -0.062256 | -0.0022943 | -0.062235 | 0.022484 | -0.009551 | -2.988e-05 | -0.0056887 | -0.084686 | 0.023904 | 0.024966 | 0.025977 | 0.017438 | 0.014721 | 0.054932 | 0.018311 | 0.064087 | 0.045776 | -0.045776 | 0.091553 | -0.009155 | 0.07782 | 0.07782 | -0.054932 | -0.050354 | -0.045776 | 0.086975 | 0.009155 | 122.4243 | 122.3236 | -0.077819 | 122.3511 | 122.3785 | 0.054931 | 0.022889 | 122.4197 | 122.3419 | -0.082397 | 122.4106 | 122.2778 | -0.064087 | -0.077819 | 122.287 | 122.3877 | 122.3969 | -0.041198 | 122.2824 | 122.287 | 122.4106 | -0.022888
1825.375 | 122.5525 | -122.3145 | 0 | 0.10559 | -0.0050715 | -0.059671 | 0.020561 | -0.012542 | -0.0068659 | -0.0056887 | 0.1442 | 0.022409 | 0.024539 | 0.019995 | 0.013806 | 0.017071 | 0.064087 | 0.07782 | 0.11902 | 0.054932 | -0.086975 | 0.11902 | 0.018311 | 0.09613 | 0.10529 | 0.013733 | -0.091553 | -0.059509 | 0.10529 | 0.036621 | 122.4335 | 122.3328 | -0.086975 | 122.3923 | 122.3694 | 0.036621 | 0.064087 | 122.4197 | 122.3511 | -0.091553 | 122.4106 | 122.3282 | -0.022888 | -0.059509 | 122.2275 | 122.3785 | 122.4335 | 0.018311 | 122.2229 | 122.2549 | 122.4197 | 0.036621
1827.0625 | 122.5159 | -122.3328 | 0.027466 | -0.069885 | -0.0025079 | -0.063944 | 0.023125 | -0.010192 | -0.0013117 | -0.0052615 | -0.12283 | 0.023691 | 0.028811 | 0.022986 | 0.015515 | 0.014507 | 0.050354 | 0.004578 | 0.054932 | 0.041199 | -0.050354 | 0.082397 | -0.018311 | 0.064087 | 0.073242 | -0.045776 | -0.050354 | -0.009155 | 0.07782 | 0.009155 | 122.4152 | 122.3145 | -0.07782 | 122.3373 | 122.374 | 0.05951 | 0.022888 | 122.4106 | 122.3419 | -0.07782 | 122.3969 | 122.287 | -0.054931 | -0.036621 | 122.2824 | 122.3831 | 122.3877 | -0.045777 | 122.2824 | 122.3236 | 122.406 | -0.018311
1828.75 | 122.5159 | -122.3236 | 0.013733 | -0.18433 | -0.0014399 | -0.060953 | 0.024834 | -0.015319 | -0.0023797 | -0.0063297 | -0.17624 | 0.024118 | 0.027743 | 0.022345 | 0.013379 | 0.015148 | -0.022888 | -0.068665 | 0.013733 | 0.013733 | -0.045776 | 0.082397 | -0.036621 | 0.004578 | 0.032043 | -0.07782 | -0.059509 | -0.009155 | 0.045776 | 0 | 122.406 | 122.287 | -0.059509 | 122.2549 | 122.3373 | 0.050354 | -0.036621 | 122.3694 | 122.3236 | -0.073242 | 122.3282 | 122.2458 | -0.07782 | -0.022888 | 122.2778 | 122.3007 | 122.3373 | -0.050354 | 122.2641 | 122.3145 | 122.3557 | -0.013733
1830.4531 | 122.5113 | -122.3282 | 0.036621 | -0.1767 | -0.0046441 | -0.061167 | 0.023979 | -0.012328 | -0.0034479 | -0.0039797 | -0.16098 | 0.02305 | 0.028384 | 0.025122 | 0.013379 | 0.014721 | -0.013733 | -0.050354 | 0 | 0.013733 | -0.036621 | 0.068665 | -0.027466 | 0 | 0.022888 | -0.082397 | -0.054932 | -0.027466 | 0.073242 | 0.009155 | 122.3969 | 122.3007 | -0.073242 | 122.2778 | 122.3419 | 0.041199 | -0.050354 | 122.4014 | 122.3373 | -0.091553 | 122.3282 | 122.2458 | -0.091552 | -0.064087 | 122.2916 | 122.3145 | 122.3282 | -0.064087 | 122.2733 | 122.3007 | 122.3511 | -0.027466
1832.1719 | 122.4609 | -122.3419 | 0.036621 | -0.024109 | -0.0018671 | -0.062876 | 0.01992 | -0.011901 | 0.00018372 | -0.0033389 | -0.077057 | 0.022623 | 0.024325 | 0.025763 | 0.017652 | 0.015362 | 0.045776 | 0.018311 | 0.059509 | 0.032043 | -0.054932 | 0.091553 | -0.009155 | 0.041199 | 0.054932 | -0.045776 | -0.059509 | -0.032043 | 0.064087 | -0.004578 | 122.4335 | 122.3328 | -0.091553 | 122.3602 | 122.374 | 0.041198 | 0.009155 | 122.406 | 122.3373 | -0.09613 | 122.3831 | 122.2961 | -0.041198 | -0.068664 | 122.287 | 122.3877 | 122.4014 | -0.045776 | 122.2824 | 122.3099 | 122.3969 | -0.041199
1833.9219 | 122.5662 | -122.319 | -0.009155 | 0.17426 | -0.0063531 | -0.059031 | 0.020134 | -0.01361 | -0.0034479 | -0.0044071 | 0.18234 | 0.021555 | 0.024539 | 0.022559 | 0.016584 | 0.015148 | 0.082397 | 0.082397 | 0.13275 | 0.07782 | -0.10071 | 0.12817 | 0.009155 | 0.14191 | 0.13733 | 0.027466 | -0.082397 | -0.064087 | 0.10986 | 0.045776 | 122.4472 | 122.3282 | -0.091553 | 122.4014 | 122.3969 | 0.068665 | 0.091552 | 122.4289 | 122.3648 | -0.073242 | 122.4609 | 122.3465 | -0.01831 | -0.054932 | 122.2183 | 122.4014 | 122.4518 | 0.01831 | 122.2366 | 122.2549 | 122.4564 | 0.054931
1835.6094 | 122.525 | -122.3465 | 0.045776 | -0.19196 | -0.0022943 | -0.059885 | 0.026115 | -0.010833 | -0.0051569 | -0.0050479 | -0.19913 | 0.023904 | 0.027957 | 0.021704 | 0.014234 | 0.015148 | -0.022888 | -0.059509 | 0.009155 | 0 | -0.027466 | 0.086975 | -0.032043 | 0 | 0.013733 | -0.082397 | -0.045776 | -0.018311 | 0.059509 | 0.009155 | 122.4335 | 122.3145 | -0.073242 | 122.287 | 122.3465 | 0.032043 | -0.068664 | 122.406 | 122.3557 | -0.091552 | 122.3465 | 122.2641 | -0.091552 | -0.064087 | 122.319 | 122.3236 | 122.3557 | -0.077819 | 122.3007 | 122.3282 | 122.3602 | -0.036621
1837.3125 | 122.4792 | -122.3419 | 0.022888 | 0.021668 | -0.0020807 | -0.059458 | 0.01992 | -0.012328 | -0.0015253 | -0.0073977 | 0.022125 | 0.023264 | 0.024325 | 0.02384 | 0.018079 | 0.014507 | -0.018311 | -0.059509 | 0.004578 | -0.009155 | -0.050354 | 0.07782 | -0.022888 | -0.022888 | -0.027466 | -0.10071 | -0.032043 | -0.013733 | 0.07782 | -0.004578 | 122.4197 | 122.319 | -0.073242 | 122.2824 | 122.3328 | 0.013733 | -0.041199 | 122.4197 | 122.3373 | -0.054931 | 122.319 | 122.2412 | -0.09613 | -0.036621 | 122.2916 | 122.3236 | 122.3465 | -0.045776 | 122.3099 | 122.3282 | 122.3145 | -0.027466
1839.0156 | 122.5754 | -122.3328 | -0.004578 | 0.12085 | -0.0037897 | -0.059458 | 0.025047 | -0.015105 | -0.0092157 | -0.0069705 | 0.12894 | 0.020273 | 0.027316 | 0.02149 | 0.011884 | 0.017284 | 0.041199 | 0.059509 | 0.11444 | 0.036621 | -0.07782 | 0.12817 | 0.004578 | 0.10071 | 0.086975 | 0.009155 | -0.068665 | -0.064087 | 0.1236 | 0.041199 | 122.4609 | 122.3373 | -0.073242 | 122.3923 | 122.3694 | 0.032043 | 0.045777 | 122.4564 | 122.374 | -0.064087 | 122.4335 | 122.3419 | -0.032044 | -0.059509 | 122.2549 | 122.374 | 122.4472 | 0.009156 | 122.2641 | 122.2687 | 122.4197 | 0.045777
1840.7031 | 122.5571 | -122.3328 | 0.022888 | 0.12848 | -0.0037897 | -0.059885 | 0.021843 | -0.0097646 | -0.00067088 | -0.0061161 | 0.08316 | 0.023477 | 0.023898 | 0.024908 | 0.017652 | 0.016003 | 0.004578 | -0.07782 | -0.004578 | -0.004578 | -0.041199 | 0.086975 | -0.013733 | 0.013733 | -0.004578 | -0.086975 | -0.032043 | -0.027466 | 0.073242 | 0 | 122.4197 | 122.319 | -0.064087 | 122.2549 | 122.3282 | 0.009155 | -0.01831 | 122.406 | 122.3328 | -0.054931 | 122.3465 | 122.2458 | -0.086975 | -0.050354 | 122.2916 | 122.3373 | 122.3282 | -0.036621 | 122.3007 | 122.3053 | 122.3282 | -0.022888
1842.4219 | 122.6212 | -122.3099 | -0.018311 | -0.10803 | -0.0067805 | -0.05839 | 0.023125 | -0.011901 | -0.0090021 | -0.0063297 | -0.031281 | 0.021555 | 0.025393 | 0.020422 | 0.012097 | 0.017071 | 0.059509 | 0.07782 | 0.13275 | 0.068665 | -0.068665 | 0.09613 | 0.013733 | 0.1236 | 0.16937 | 0.068665 | -0.082397 | -0.059509 | 0.10986 | 0.041199 | 122.406 | 122.3236 | -0.050354 | 122.3877 | 122.3785 | 0.054932 | 0.07782 | 122.4197 | 122.3511 | -0.064086 | 122.4335 | 122.3785 | 0.027466 | -0.041198 | 122.2412 | 122.3694 | 122.4426 | 0.032044 | 122.2275 | 122.2504 | 122.4792 | 0.05951
1844.125 | 122.4838 | -122.3602 | 0.027466 | -0.16907 | -0.0037897 | -0.060526 | 0.023766 | -0.011687 | -0.0062249 | -0.0080387 | -0.19913 | 0.022195 | 0.027102 | 0.025549 | 0.012952 | 0.014507 | -0.004578 | -0.036621 | 0.032043 | 0 | -0.041199 | 0.082397 | -0.018311 | 0.004578 | 0.027466 | -0.068665 | -0.041199 | -0.027466 | 0.068665 | 0 | 122.4426 | 122.3419 | -0.068665 | 122.3236 | 122.3602 | 0.018311 | -0.032044 | 122.4289 | 122.3602 | -0.068665 | 122.3648 | 122.2916 | -0.068665 | -0.054932 | 122.319 | 122.3557 | 122.3923 | -0.045777 | 122.319 | 122.3328 | 122.3877 | -0.027466
1845.8594 | 122.5296 | -122.3465 | 0.018311 | -0.16907 | -0.0050715 | -0.059671 | 0.021843 | -0.011687 | 0.00018372 | -0.0026981 | -0.16098 | 0.021555 | 0.024325 | 0.02619 | 0.015729 | 0.013866 | 0.022888 | -0.018311 | 0.022888 | 0.032043 | -0.022888 | 0.068665 | -0.036621 | 0.041199 | 0.050354 | -0.064087 | -0.054932 | -0.027466 | 0.068665 | 0.018311 | 122.4152 | 122.3099 | -0.041199 | 122.3282 | 122.3785 | 0.068664 | 0.004577 | 122.4152 | 122.3648 | -0.073243 | 122.3877 | 122.2824 | -0.082398 | -0.045777 | 122.3236 | 122.3694 | 122.3694 | -0.054932 | 122.2916 | 122.319 | 122.3969 | 0
1847.5625 | 122.493 | -122.3373 | 0.036621 | -0.085144 | -0.00079888 | -0.062021 | 0.021202 | -0.015746 | -0.00088448 | -0.0046207 | -0.092316 | 0.022623 | 0.023257 | 0.023627 | 0.019574 | 0.014721 | 0.059509 | 0.004578 | 0.07782 | 0.041199 | -0.050354 | 0.09613 | -0.004578 | 0.050354 | 0.059509 | -0.054932 | -0.036621 | -0.045776 | 0.07782 | 0.022888 | 122.4335 | 122.3328 | -0.086975 | 122.3419 | 122.3785 | 0.045777 | 0.022888 | 122.4152 | 122.3602 | -0.073242 | 122.3877 | 122.2824 | -0.07782 | -0.082397 | 122.287 | 122.3969 | 122.4152 | -0.041199 | 122.3007 | 122.2916 | 122.3969 | -0.013733
1849.2812 | 122.6074 | -122.3053 | 0.004578 | 0.12848 | -0.0059259 | -0.059244 | 0.020988 | -0.011901 | -0.0038751 | -0.0044071 | 0.15945 | 0.022623 | 0.024539 | 0.024268 | 0.014234 | 0.016643 | 0.10071 | 0.054932 | 0.14191 | 0.091553 | -0.082397 | 0.11902 | 0.004578 | 0.12817 | 0.11902 | 0.032043 | -0.091553 | -0.068665 | 0.10986 | 0.054932 | 122.4243 | 122.3099 | -0.086975 | 122.3602 | 122.3969 | 0.086975 | 0.09613 | 122.4152 | 122.3602 | -0.096131 | 122.4335 | 122.3373 | -0.022889 | -0.073243 | 122.2229 | 122.406 | 122.4472 | 0 | 122.2137 | 122.2366 | 122.4243 | 0.050354
1851 | 122.5708 | -122.3419 | -0.009155 | 0.090332 | -0.0061395 | -0.059671 | 0.023552 | -0.011901 | -0.0077203 | -0.0046207 | 0.12894 | 0.021555 | 0.026889 | 0.023627 | 0.013593 | 0.017712 | 0.073242 | 0.045776 | 0.10986 | 0.045776 | -0.091553 | 0.11902 | 0.018311 | 0.086975 | 0.082397 | 0.004578 | -0.07782 | -0.032043 | 0.12817 | 0.027466 | 122.4609 | 122.3602 | -0.082398 | 122.3877 | 122.3877 | 0.027465 | 0.082397 | 122.4701 | 122.3694 | -0.068665 | 122.4289 | 122.3465 | -0.022888 | -0.022888 | 122.2504 | 122.4152 | 122.4518 | 0.027466 | 122.2641 | 122.3099 | 122.4243 | 0.036621
1852.6875 | 122.6395 | -122.3236 | -0.004578 | 0.17426 | -0.0044305 | -0.061167 | 0.019707 | -0.013396 | -0.0021661 | -0.0080387 | 0.12894 | 0.024118 | 0.024112 | 0.02384 | 0.017865 | 0.013012 | 0.045776 | -0.009155 | 0.064087 | 0.032043 | -0.054932 | 0.11444 | 0 | 0.086975 | 0.09613 | 0.013733 | -0.091553 | -0.054932 | 0.07782 | 0.050354 | 122.438 | 122.3236 | -0.050354 | 122.3145 | 122.3557 | 0.032043 | 0.050354 | 122.4014 | 122.374 | -0.086975 | 122.4106 | 122.3373 | -0.036621 | -0.050354 | 122.2687 | 122.3694 | 122.3877 | 0.004578 | 122.2321 | 122.2687 | 122.4197 | 0.054932
1854.4062 | 122.58 | -122.3419 | 0.018311 | 0.059815 | -0.0061395 | -0.057535 | 0.022057 | -0.011474 | -0.0087885 | -0.0088931 | 0.08316 | 0.018991 | 0.023684 | 0.023413 | 0.012525 | 0.016003 | 0.054932 | 0.022888 | 0.10529 | 0.045776 | -0.086975 | 0.10986 | 0.013733 | 0.07782 | 0.064087 | -0.004578 | -0.09613 | -0.050354 | 0.09613 | 0.018311 | 122.4518 | 122.3557 | -0.10529 | 122.3648 | 122.3877 | 0.032043 | 0.036621 | 122.438 | 122.3602 | -0.11444 | 122.4197 | 122.3373 | -0.022889 | -0.068665 | 122.2549 | 122.3969 | 122.4472 | -0.004578 | 122.2458 | 122.2916 | 122.406 | 0
1856.0938 | 122.6028 | -122.3557 | 0.027466 | 0.044556 | -0.0091303 | -0.058176 | 0.020561 | -0.014251 | -0.0064387 | -0.0067569 | 0.052643 | 0.022836 | 0.021762 | 0.019568 | 0.016797 | 0.015575 | 0.045776 | 0.009155 | 0.07782 | 0.054932 | -0.064087 | 0.10986 | 0.018311 | 0.073242 | 0.068665 | -0.004578 | -0.07782 | -0.054932 | 0.10986 | 0.032043 | 122.4655 | 122.374 | -0.091553 | 122.3648 | 122.4106 | 0.036621 | 0.01831 | 122.4655 | 122.3877 | -0.10529 | 122.4289 | 122.3511 | -0.036621 | -0.082398 | 122.2916 | 122.4014 | 122.4335 | -0.009155 | 122.2778 | 122.3007 | 122.4243 | 0.004577
1857.7969 | 122.5433 | -122.3648 | 0.027466 | -0.22247 | -0.0016535 | -0.060526 | 0.02462 | -0.01126 | -0.0015253 | -0.0061161 | -0.21439 | 0.02305 | 0.025393 | 0.024268 | 0.012738 | 0.013866 | 0.009155 | -0.07782 | 0.009155 | -0.013733 | -0.032043 | 0.068665 | -0.045776 | 0.004578 | 0.013733 | -0.091553 | -0.018311 | -0.022888 | 0.073242 | 0.004578 | 122.4335 | 122.319 | -0.059509 | 122.287 | 122.3511 | 0.032043 | -0.018311 | 122.438 | 122.3694 | -0.045777 | 122.3694 | 122.2733 | -0.096131 | -0.050354 | 122.3328 | 122.374 | 122.374 | -0.073242 | 122.3465 | 122.3419 | 122.3785 | -0.022888
1859.5 | 122.5113 | -122.3602 | 0.032043 | 0.075073 | -0.0029351 | -0.060953 | 0.020134 | -0.012542 | 0.0010381 | -0.0041933 | 0.060272 | 0.022836 | 0.026034 | 0.024054 | 0.01872 | 0.015789 | -0.004578 | -0.10529 | -0.022888 | -0.022888 | -0.027466 | 0.073242 | -0.004578 | 0.013733 | -0.032043 | -0.12817 | -0.032043 | -0.041199 | 0.073242 | 0.009155 | 122.4335 | 122.3557 | -0.059509 | 122.2549 | 122.3373 | -0.01831 | -0.036621 | 122.4335 | 122.3694 | -0.064086 | 122.374 | 122.2321 | -0.13733 | -0.073242 | 122.3328 | 122.3557 | 122.3373 | -0.036621 | 122.3282 | 122.319 | 122.3282 | -0.022888
1861.1875 | 122.6349 | -122.3236 | -0.004578 | 0.12848 | -0.0044305 | -0.058817 | 0.021202 | -0.012115 | -0.0025935 | -0.0052615 | 0.1442 | 0.021555 | 0.025607 | 0.022986 | 0.017438 | 0.015575 | 0.027466 | -0.022888 | 0.050354 | 0.027466 | -0.059509 | 0.09613 | -0.013733 | 0.068665 | 0.059509 | -0.022888 | -0.068665 | -0.059509 | 0.10986 | 0.013733 | 122.4197 | 122.3099 | -0.054931 | 122.3007 | 122.3511 | 0.041199 | 0.032044 | 122.4335 | 122.3373 | -0.064087 | 122.3923 | 122.3007 | -0.036621 | -0.054931 | 122.2641 | 122.3511 | 122.374 | -0.009155 | 122.2549 | 122.2641 | 122.3831 | 0.018311
1862.9375 | 122.5891 | -122.3465 | 0 | 0.14374 | -0.0027215 | -0.060953 | 0.01928 | -0.011901 | -0.0045161 | -0.0035525 | 0.067902 | 0.021127 | 0.021335 | 0.024268 | 0.017438 | 0.014294 | 0.022888 | -0.054932 | 0.004578 | 0.004578 | -0.027466 | 0.082397 | -0.045776 | 0.022888 | -0.018311 | -0.082397 | -0.059509 | -0.022888 | 0.07782 | 0.009155 | 122.4289 | 122.3007 | -0.027466 | 122.2916 | 122.3511 | 0.050354 | 0.022888 | 122.4243 | 122.3557 | -0.059509 | 122.3694 | 122.2641 | -0.091552 | -0.022888 | 122.319 | 122.3694 | 122.3511 | -0.045776 | 122.287 | 122.3236 | 122.3282 | 0.009155
1864.625 | 122.5845 | -122.3557 | 0.004578 | 0.097962 | -0.0082757 | -0.059458 | 0.020561 | -0.015319 | -0.0081477 | -0.0052615 | 0.098419 | 0.021341 | 0.021335 | 0.021277 | 0.01167 | 0.015789 | 0.054932 | 0.036621 | 0.10071 | 0.036621 | -0.07782 | 0.10529 | 0.018311 | 0.086975 | 0.073242 | -0.009155 | -0.086975 | -0.073242 | 0.10071 | 0.036621 | 122.4609 | 122.374 | -0.082398 | 122.3923 | 122.3923 | 0.01831 | 0.050354 | 122.4564 | 122.3923 | -0.091553 | 122.4426 | 122.3465 | -0.045776 | -0.07782 | 122.2778 | 122.4106 | 122.4564 | 0.013733 | 122.2687 | 122.2824 | 122.4289 | 0.032043
1866.3125 | 122.5525 | -122.374 | 0.032043 | -0.069885 | -0.0046441 | -0.061167 | 0.021629 | -0.014037 | 0.0012519 | -0.0052615 | -0.12283 | 0.023904 | 0.023684 | 0.025122 | 0.014875 | 0.01408 | 0.059509 | -0.009155 | 0.054932 | 0.032043 | -0.064087 | 0.073242 | -0.022888 | 0.059509 | 0.054932 | -0.059509 | -0.054932 | -0.045776 | 0.073242 | 0.004578 | 122.4472 | 122.3511 | -0.09613 | 122.3648 | 122.406 | 0.054931 | 0.027466 | 122.4472 | 122.3785 | -0.086975 | 122.4335 | 122.3145 | -0.064087 | -0.077819 | 122.3099 | 122.4335 | 122.4289 | -0.054931 | 122.319 | 122.3282 | 122.4289 | -0.027465
1868.0156 | 122.6715 | -122.3419 | 0.004578 | -0.024109 | -0.0044305 | -0.058176 | 0.026756 | -0.011687 | -0.0079339 | -0.0037661 | -0.10757 | 0.018991 | 0.024753 | 0.021063 | 0.010816 | 0.014934 | 0.045776 | 0.036621 | 0.1236 | 0.068665 | -0.07782 | 0.11444 | 0.004578 | 0.10986 | 0.12817 | 0.045776 | -0.082397 | -0.064087 | 0.10071 | 0.036621 | 122.4564 | 122.3465 | -0.082398 | 122.3785 | 122.4106 | 0.064087 | 0.041198 | 122.4426 | 122.3785 | -0.086975 | 122.4518 | 122.3877 | 0.009155 | -0.068665 | 122.2641 | 122.3877 | 122.4655 | 0 | 122.2595 | 122.2778 | 122.4701 | 0.032043
1869.7656 | 122.6486 | -122.319 | -0.009155 | -0.039368 | -0.0022943 | -0.061167 | 0.022057 | -0.014464 | -0.0066523 | -0.0061161 | -0.031281 | 0.018777 | 0.024325 | 0.022345 | 0.01167 | 0.012798 | 0.082397 | 0.07782 | 0.11902 | 0.064087 | -0.082397 | 0.10071 | 0.009155 | 0.1236 | 0.14191 | 0.050354 | -0.086975 | -0.082397 | 0.11444 | 0.041199 | 122.4197 | 122.3282 | -0.073242 | 122.3969 | 122.3831 | 0.054932 | 0.091552 | 122.4335 | 122.3602 | -0.07782 | 122.4426 | 122.3694 | 0.009155 | -0.073242 | 122.2366 | 122.4014 | 122.438 | 0.01831 | 122.2321 | 122.2366 | 122.4609 | 0.050354
1871.5312 | 122.6166 | -122.3557 | 0.022888 | 0.029297 | -0.0025079 | -0.058603 | 0.022697 | -0.011687 | -0.0062249 | -0.0056887 | 0.060272 | 0.020914 | 0.023684 | 0.023199 | 0.013166 | 0.015148 | 0.027466 | 0.027466 | 0.082397 | 0.032043 | -0.068665 | 0.10986 | 0.004578 | 0.059509 | 0.073242 | -0.013733 | -0.068665 | -0.064087 | 0.10529 | 0.027466 | 122.4655 | 122.3602 | -0.091553 | 122.3831 | 122.3877 | 0.027465 | 0.004578 | 122.4609 | 122.3831 | -0.091553 | 122.4152 | 122.3419 | -0.041199 | -0.086975 | 122.287 | 122.3831 | 122.438 | -0.01831 | 122.287 | 122.2916 | 122.4289 | 0.004578
1873.25 | 122.6532 | -122.3511 | -0.013733 | -0.016479 | -0.0042169 | -0.06138 | 0.023766 | -0.01361 | -0.0057977 | -0.0080387 | 0.014496 | 0.019846 | 0.025607 | 0.024054 | 0.012952 | 0.012585 | 0.059509 | 0.054932 | 0.10986 | 0.059509 | -0.068665 | 0.11444 | 0.009155 | 0.13275 | 0.12817 | 0.032043 | -0.082397 | -0.036621 | 0.10986 | 0.032043 | 122.4655 | 122.3602 | -0.054932 | 122.406 | 122.4106 | 0.050354 | 0.073242 | 122.4609 | 122.3831 | -0.068664 | 122.4838 | 122.3831 | 0 | -0.022888 | 122.2824 | 122.4106 | 122.4609 | 0.022888 | 122.2687 | 122.3145 | 122.4792 | 0.045776
1875 | 122.5571 | -122.3831 | 0.027466 | -0.16144 | -0.0048579 | -0.060099 | 0.023766 | -0.012542 | -0.0040887 | -0.0063297 | -0.13809 | 0.020273 | 0.024112 | 0.022345 | 0.01402 | 0.013439 | 0.10986 | 0.091553 | 0.14648 | 0.086975 | -0.091553 | 0.11444 | 0.013733 | 0.1236 | 0.13733 | 0.027466 | -0.091553 | -0.045776 | 0.11444 | 0.045776 | 122.4976 | 122.3969 | -0.11902 | 122.4747 | 122.4701 | 0.073242 | 0.082397 | 122.4976 | 122.4289 | -0.11902 | 122.5067 | 122.4106 | -0.01831 | -0.073242 | 122.2916 | 122.493 | 122.5296 | -0.013733 | 122.2916 | 122.3373 | 122.5204 | 0.01831
1876.7031 | 122.4976 | -122.4106 | 0.022888 | -0.1767 | -0.0025079 | -0.059671 | 0.023125 | -0.012542 | -0.0047297 | -0.0061161 | -0.16861 | 0.020273 | 0.02518 | 0.022131 | 0.014447 | 0.013225 | 0.068665 | 0.068665 | 0.10071 | 0.068665 | -0.059509 | 0.09613 | -0.018311 | 0.059509 | 0.091553 | -0.041199 | -0.064087 | -0.050354 | 0.07782 | 0.018311 | 122.5067 | 122.3923 | -0.082397 | 122.4792 | 122.4792 | 0.086976 | 0.045777 | 122.4884 | 122.4289 | -0.086975 | 122.4701 | 122.3694 | -0.05951 | -0.073242 | 122.3511 | 122.4792 | 122.5113 | -0.041199 | 122.3465 | 122.3602 | 122.5021 | -0.004577
1878.4844 | 122.5983 | -122.3373 | 0.004578 | 0.11322 | -0.0057123 | -0.060526 | 0.019066 | -0.012115 | -0.0032343 | -0.0063297 | 0.060272 | 0.023264 | 0.023898 | 0.022772 | 0.01637 | 0.014507 | 0.086975 | 0.064087 | 0.11444 | 0.054932 | -0.082397 | 0.11444 | 0.004578 | 0.10986 | 0.073242 | -0.009155 | -0.10071 | -0.073242 | 0.10071 | 0.032043 | 122.4518 | 122.3419 | -0.086975 | 122.4014 | 122.3923 | 0.050354 | 0.082397 | 122.438 | 122.3694 | -0.10529 | 122.4472 | 122.3282 | -0.041198 | -0.07782 | 122.2549 | 122.4243 | 122.4518 | 0 | 122.2366 | 122.2641 | 122.4106 | 0.027465
1880.1875 | 122.612 | -122.374 | 0.004578 | -0.1004 | -0.0037897 | -0.060099 | 0.02462 | -0.013183 | -0.0045161 | -0.0073977 | -0.15335 | 0.021555 | 0.021975 | 0.020422 | 0.013806 | 0.013225 | 0.12817 | 0.15106 | 0.15564 | 0.091553 | -0.07782 | 0.11902 | 0.013733 | 0.14648 | 0.16479 | 0.064087 | -0.086975 | -0.073242 | 0.1236 | 0.045776 | 122.493 | 122.3877 | -0.082398 | 122.525 | 122.4655 | 0.07782 | 0.1236 | 122.4976 | 122.4197 | -0.091553 | 122.5204 | 122.438 | 0.018311 | -0.07782 | 122.2961 | 122.5021 | 122.5296 | 0.009155 | 122.287 | 122.3007 | 122.5388 | 0.041198
1881.9219 | 122.6532 | -122.3373 | 0.009155 | 0.14374 | -0.0012263 | -0.063517 | 0.021843 | -0.012542 | 0.0021063 | -0.0050479 | 0.12131 | 0.022195 | 0.023471 | 0.025336 | 0.015088 | 0.014507 | 0.041199 | -0.027466 | 0.036621 | 0.018311 | -0.064087 | 0.09613 | -0.032043 | 0.091553 | 0.041199 | -0.036621 | -0.086975 | -0.054932 | 0.091553 | 0.032043 | 122.4335 | 122.3053 | -0.073242 | 122.3099 | 122.3557 | 0.050354 | 0.032044 | 122.4289 | 122.3694 | -0.09613 | 122.4289 | 122.3007 | -0.068664 | -0.064087 | 122.2733 | 122.3785 | 122.374 | -0.041198 | 122.2504 | 122.2824 | 122.3785 | 0.022888
1883.625 | 122.6257 | -122.3602 | -0.004578 | -0.092773 | -0.0033625 | -0.060953 | 0.022484 | -0.012328 | -0.0047297 | -0.0063297 | -0.1152 | 0.017923 | 0.02283 | 0.024054 | 0.013593 | 0.014721 | 0.1236 | 0.13275 | 0.15564 | 0.091553 | -0.073242 | 0.12817 | -0.004578 | 0.15106 | 0.18768 | 0.045776 | -0.073242 | -0.068665 | 0.13275 | 0.036621 | 122.4884 | 122.3557 | -0.068664 | 122.493 | 122.4518 | 0.096131 | 0.12817 | 122.493 | 122.3969 | -0.068664 | 122.5113 | 122.406 | 0.009155 | -0.064087 | 122.287 | 122.4838 | 122.5159 | 0 | 122.287 | 122.2916 | 122.5479 | 0.041199
1885.3594 | 122.6074 | -122.3602 | 0.004578 | 0.12085 | -0.0040033 | -0.062021 | 0.017357 | -0.01361 | 0.0033881 | -0.0065433 | 0.037384 | 0.023691 | 0.022189 | 0.022986 | 0.017224 | 0.012798 | 0 | -0.050354 | -0.009155 | 0 | -0.036621 | 0.07782 | -0.027466 | 0.050354 | 0.004578 | -0.10986 | -0.050354 | -0.027466 | 0.059509 | -0.009155 | 122.438 | 122.3328 | -0.041199 | 122.3099 | 122.3602 | 0.027466 | -0.004578 | 122.4197 | 122.3511 | -0.054932 | 122.4106 | 122.2504 | -0.10071 | -0.032044 | 122.3236 | 122.3602 | 122.3511 | -0.032044 | 122.3099 | 122.3328 | 122.3648 | -0.013733
1887.0469 | 122.525 | -122.438 | 0.027466 | -0.10803 | -0.0050715 | -0.059031 | 0.023125 | -0.012115 | -0.0047297 | -0.0076113 | -0.15335 | 0.022836 | 0.023684 | 0.022131 | 0.014234 | 0.013653 | 0.07782 | 0.091553 | 0.13275 | 0.073242 | -0.073242 | 0.11444 | 0 | 0.10071 | 0.14191 | 0.004578 | -0.082397 | -0.073242 | 0.09613 | 0.032043 | 122.5525 | 122.438 | -0.10071 | 122.5296 | 122.5113 | 0.073242 | 0.050354 | 122.5342 | 122.4701 | -0.10986 | 122.5388 | 122.4426 | -0.027465 | -0.10071 | 122.3648 | 122.5159 | 122.5708 | -0.027466 | 122.3557 | 122.3648 | 122.58 | 0.004577
1888.7188 | 122.5159 | -122.3785 | 0.022888 | -0.069885 | 0.0013373 | -0.059885 | 0.018639 | -0.011046 | 0.0027471 | -0.0022707 | -0.12283 | 0.02305 | 0.022403 | 0.023413 | 0.018506 | 0.013225 | 0.091553 | 0.022888 | 0.064087 | 0.050354 | -0.045776 | 0.086975 | -0.013733 | 0.07782 | 0.082397 | -0.050354 | -0.059509 | -0.032043 | 0.082397 | 0.013733 | 122.4655 | 122.3648 | -0.068664 | 122.4014 | 122.4289 | 0.064087 | 0.068665 | 122.4609 | 122.3923 | -0.082397 | 122.4564 | 122.3282 | -0.064087 | -0.054931 | 122.3328 | 122.4701 | 122.4426 | -0.036621 | 122.319 | 122.3465 | 122.4609 | -0.009155
1890.4062 | 122.6486 | -122.3419 | 0 | -0.10803 | -0.0040033 | -0.059671 | 0.021843 | -0.011687 | -0.0075067 | -0.0069705 | -0.046539 | 0.018991 | 0.022616 | 0.020636 | 0.01402 | 0.017712 | 0.10071 | 0.12817 | 0.14648 | 0.086975 | -0.082397 | 0.1236 | 0.036621 | 0.15564 | 0.17853 | 0.07782 | -0.086975 | -0.068665 | 0.1236 | 0.050354 | 122.4655 | 122.3785 | -0.082397 | 122.4701 | 122.4289 | 0.050354 | 0.10071 | 122.4655 | 122.3923 | -0.086975 | 122.4976 | 122.4197 | 0.027466 | -0.068665 | 122.2595 | 122.4426 | 122.4884 | 0.036621 | 122.2549 | 122.2733 | 122.5204 | 0.050354
1892.1094 | 122.5479 | -122.3923 | 0.027466 | 0.067444 | -0.0022943 | -0.06074 | 0.020134 | -0.012542 | 0.0016791 | -0.0044071 | 0.037384 | 0.023477 | 0.023257 | 0.024268 | 0.017865 | 0.016643 | -0.013733 | -0.07782 | -0.009155 | -0.022888 | -0.036621 | 0.07782 | -0.032043 | 0 | -0.013733 | -0.11444 | -0.041199 | -0.018311 | 0.068665 | 0.018311 | 122.4701 | 122.3602 | -0.064087 | 122.3145 | 122.3694 | 0.009155 | -0.041199 | 122.4609 | 122.4106 | -0.068665 | 122.3923 | 122.2778 | -0.13275 | -0.045777 | 122.3557 | 122.3785 | 122.3831 | -0.059509 | 122.3511 | 122.374 | 122.3785 | -0.009155
1893.8906 | 122.6624 | -122.3465 | 0.004578 | 0.052185 | -0.0050715 | -0.060312 | 0.02462 | -0.012115 | -0.0064387 | -0.0061161 | 0.0068663 | 0.020914 | 0.024539 | 0.023627 | 0.010602 | 0.016643 | 0.050354 | 0.041199 | 0.1236 | 0.050354 | -0.054932 | 0.091553 | 0.013733 | 0.10071 | 0.11902 | 0.027466 | -0.07782 | -0.059509 | 0.10529 | 0.032043 | 122.4381 | 122.3602 | -0.05951 | 122.3877 | 122.3969 | 0.036621 | 0.045776 | 122.4518 | 122.3785 | -0.082398 | 122.4472 | 122.374 | -0.004577 | -0.064087 | 122.2916 | 122.3969 | 122.4701 | 0.009155 | 122.2687 | 122.287 | 122.4655 | 0.027465
1895.5781 | 122.5296 | -122.406 | 0.036621 | 0.090332 | -0.0020807 | -0.06138 | 0.018639 | -0.012755 | 0.0012519 | -0.0018435 | -0.00076274 | 0.023477 | 0.023044 | 0.021918 | 0.018293 | 0.015148 | -0.018311 | -0.064087 | -0.004578 | 0.004578 | -0.045776 | 0.082397 | -0.032043 | -0.022888 | -0.009155 | -0.12817 | -0.036621 | -0.036621 | 0.073242 | -0.009155 | 122.4884 | 122.374 | -0.082397 | 122.3419 | 122.4106 | 0.036621 | -0.054932 | 122.4792 | 122.3969 | -0.073242 | 122.3831 | 122.2778 | -0.11902 | -0.073242 | 122.3602 | 122.3877 | 122.4014 | -0.068664 | 122.3694 | 122.3694 | 122.3969 | -0.045776
1897.2969 | 122.5113 | -122.4243 | 0.018311 | -0.031738 | -0.0029351 | -0.061167 | 0.020775 | -0.014251 | -0.00024348 | -0.0029117 | -0.054169 | 0.022195 | 0.023044 | 0.023199 | 0.020002 | 0.014294 | 0.050354 | 0 | 0.041199 | 0.027466 | -0.054932 | 0.07782 | -0.018311 | 0.041199 | 0.032043 | -0.091553 | -0.041199 | -0.045776 | 0.082397 | 0.018311 | 122.5021 | 122.406 | -0.073243 | 122.4243 | 122.4518 | 0.045777 | 0.032043 | 122.5067 | 122.4426 | -0.05951 | 122.4655 | 122.3328 | -0.10986 | -0.064087 | 122.3694 | 122.4747 | 122.4655 | -0.036622 | 122.3831 | 122.3785 | 122.4564 | 0
1899 | 122.5662 | -122.3923 | 0.018311 | 0.11322 | -0.0048579 | -0.059671 | 0.024193 | -0.01126 | -0.00045708 | -0.0026981 | 0.09079 | 0.022409 | 0.024966 | 0.024695 | 0.014875 | 0.016857 | -0.004578 | -0.073242 | -0.009155 | -0.004578 | -0.059509 | 0.082397 | -0.027466 | 0 | -0.013733 | -0.082397 | -0.050354 | -0.022888 | 0.073242 | 0.013733 | 122.4747 | 122.3648 | -0.07782 | 122.319 | 122.3877 | 0.022888 | -0.022889 | 122.4655 | 122.406 | -0.068665 | 122.3923 | 122.3099 | -0.09613 | -0.041199 | 122.3328 | 122.3877 | 122.3831 | -0.045777 | 122.3419 | 122.3694 | 122.3785 | -0.004578
1900.6719 | 122.6669 | -122.3557 | 0.004578 | -0.054626 | -0.0054987 | -0.059458 | 0.025475 | -0.014678 | -0.0092157 | -0.0044071 | -0.023651 | 0.01835 | 0.022403 | 0.02085 | 0.011243 | 0.016216 | 0.059509 | 0.086975 | 0.14191 | 0.082397 | -0.068665 | 0.11444 | 0.013733 | 0.11902 | 0.16479 | 0.045776 | -0.073242 | -0.064087 | 0.09613 | 0.050354 | 122.4701 | 122.3694 | -0.073243 | 122.4426 | 122.438 | 0.068664 | 0.054931 | 122.4518 | 122.406 | -0.07782 | 122.4747 | 122.4014 | -0.004578 | -0.068665 | 122.287 | 122.4152 | 122.4976 | 0.009155 | 122.2824 | 122.2916 | 122.5204 | 0.045776
1902.375 | 122.5296 | -122.406 | 0.009155 | -0.054626 | -0.0031489 | -0.06074 | 0.024834 | -0.013824 | -0.00045708 | -0.0056887 | -0.099945 | 0.021555 | 0.024966 | 0.024054 | 0.014447 | 0.014934 | 0.068665 | 0.027466 | 0.054932 | 0.041199 | -0.045776 | 0.10071 | -0.027466 | 0.054932 | 0.082397 | -0.036621 | -0.068665 | -0.054932 | 0.07782 | 0.022888 | 122.5067 | 122.3785 | -0.054931 | 122.4335 | 122.4472 | 0.068665 | 0.05951 | 122.4838 | 122.4289 | -0.07782 | 122.4609 | 122.3694 | -0.059509 | -0.064087 | 122.3602 | 122.4747 | 122.4609 | -0.036621 | 122.3373 | 122.3511 | 122.4884 | 0.013733
1904.0781 | 122.5845 | -122.374 | 0.004578 | -0.11566 | 0.0011237 | -0.062662 | 0.023766 | -0.013396 | -0.00067088 | -0.0052615 | -0.13809 | 0.022836 | 0.026675 | 0.025977 | 0.014447 | 0.014507 | 0.036621 | -0.027466 | 0.050354 | 0.041199 | -0.032043 | 0.091553 | -0.018311 | 0.054932 | 0.064087 | -0.045776 | -0.045776 | -0.022888 | 0.091553 | 0.013733 | 122.4655 | 122.3557 | -0.036621 | 122.3465 | 122.4152 | 0.05951 | 0.032043 | 122.4655 | 122.3877 | -0.050354 | 122.4289 | 122.3282 | -0.059509 | -0.027466 | 122.3419 | 122.4106 | 122.4243 | -0.022889 | 122.3282 | 122.3511 | 122.438 | 0.009155
1905.75 | 122.5433 | -122.4152 | 0.027466 | 0.029297 | -0.0022943 | -0.059244 | 0.019493 | -0.013396 | 0.00039732 | -0.0046207 | 0.067902 | 0.023477 | 0.023471 | 0.024481 | 0.017652 | 0.015575 | -0.032043 | -0.091553 | -0.022888 | -0.013733 | -0.045776 | 0.082397 | -0.022888 | 0.004578 | -0.018311 | -0.10986 | -0.045776 | -0.027466 | 0.07782 | -0.013733 | 122.4976 | 122.3923 | -0.073242 | 122.3236 | 122.4014 | 0.009155 | -0.059509 | 122.493 | 122.4014 | -0.073242 | 122.4197 | 122.3053 | -0.09613 | -0.054932 | 122.3694 | 122.3831 | 122.3923 | -0.050354 | 122.3694 | 122.3877 | 122.3969 | -0.041199
1907.4219 | 122.6486 | -122.374 | 0.009155 | -0.092773 | -0.0042169 | -0.059458 | 0.023766 | -0.014464 | -0.010284 | -0.0035525 | -0.084686 | 0.018777 | 0.023044 | 0.020422 | 0.0099612 | 0.015148 | 0.10071 | 0.1236 | 0.16937 | 0.09613 | -0.082397 | 0.10986 | -0.004578 | 0.11902 | 0.17853 | 0.064087 | -0.073242 | -0.050354 | 0.10071 | 0.036621 | 122.4838 | 122.3694 | -0.091552 | 122.4976 | 122.4701 | 0.10071 | 0.091553 | 122.4747 | 122.4106 | -0.082397 | 122.493 | 122.438 | 0.027466 | -0.059509 | 122.2916 | 122.4747 | 122.5433 | -0.013733 | 122.3007 | 122.3236 | 122.5525 | 0.027466
1909.0938 | 122.5845 | -122.4289 | 0.013733 | -0.085144 | -0.00079888 | -0.06074 | 0.020988 | -0.012542 | -0.0010981 | -0.0031253 | -0.10757 | 0.022195 | 0.024753 | 0.023199 | 0.017865 | 0.012585 | 0.045776 | 0.004578 | 0.045776 | 0.036621 | -0.022888 | 0.091553 | -0.032043 | 0.050354 | 0.064087 | -0.032043 | -0.059509 | -0.027466 | 0.073242 | 0.018311 | 122.5204 | 122.3969 | -0.036621 | 122.4335 | 122.4655 | 0.068664 | 0.032043 | 122.5021 | 122.4472 | -0.073242 | 122.4792 | 122.3969 | -0.050354 | -0.041199 | 122.406 | 122.4747 | 122.4747 | -0.045776 | 122.3694 | 122.4014 | 122.493 | 0.004578
1910.7812 | 122.6532 | -122.3419 | -0.009155 | 0.159 | -0.0040033 | -0.063089 | 0.020348 | -0.014678 | -0.0030207 | -0.0037661 | 0.15182 | 0.021768 | 0.023471 | 0.022131 | 0.017224 | 0.014294 | 0.086975 | 0.059509 | 0.10986 | 0.068665 | -0.07782 | 0.10986 | 0 | 0.11444 | 0.11902 | 0.032043 | -0.10071 | -0.073242 | 0.11444 | 0.050354 | 122.4518 | 122.3419 | -0.068665 | 122.4014 | 122.4106 | 0.068665 | 0.09613 | 122.4564 | 122.3923 | -0.091553 | 122.4564 | 122.374 | -0.018311 | -0.064087 | 122.2641 | 122.4289 | 122.4518 | 0.009155 | 122.2412 | 122.2687 | 122.4609 | 0.059509
1912.4688 | 122.5433 | -122.4243 | 0.027466 | -0.069885 | -0.00037168 | -0.06138 | 0.023979 | -0.013183 | 0.00039732 | -0.0037661 | -0.069428 | 0.021768 | 0.023684 | 0.021277 | 0.016584 | 0.01408 | 0.059509 | 0.013733 | 0.064087 | 0.036621 | -0.059509 | 0.086975 | -0.013733 | 0.054932 | 0.059509 | -0.045776 | -0.059509 | -0.050354 | 0.068665 | 0.013733 | 122.5113 | 122.4106 | -0.086975 | 122.438 | 122.4609 | 0.050354 | 0.032043 | 122.493 | 122.438 | -0.086975 | 122.4792 | 122.3785 | -0.059509 | -0.07782 | 122.3648 | 122.4838 | 122.4884 | -0.041199 | 122.3648 | 122.374 | 122.4838 | -0.013733
1914.1562 | 122.6074 | -122.3785 | -0.004578 | 0.16663 | -0.0084893 | -0.059885 | 0.021843 | -0.014037 | -0.0075067 | -0.0031253 | 0.1976 | 0.019632 | 0.021548 | 0.020636 | 0.015729 | 0.017284 | 0.082397 | 0.09613 | 0.13275 | 0.086975 | -0.082397 | 0.13275 | 0.027466 | 0.12817 | 0.12817 | 0.064087 | -0.091553 | -0.054932 | 0.10529 | 0.036621 | 122.5113 | 122.406 | -0.077819 | 122.4747 | 122.4655 | 0.059509 | 0.086975 | 122.4838 | 122.4152 | -0.086975 | 122.5067 | 122.4426 | 0.027466 | -0.050354 | 122.2961 | 122.4609 | 122.5113 | 0.032044 | 122.287 | 122.3236 | 122.5067 | 0.041199
1915.9219 | 122.6349 | -122.3877 | -0.004578 | 0.021668 | -0.0063531 | -0.056467 | 0.021629 | -0.016387 | -0.0075067 | -0.0076113 | 0.098419 | 0.019418 | 0.020267 | 0.022345 | 0.013166 | 0.01878 | 0.036621 | 0.027466 | 0.086975 | 0.045776 | -0.073242 | 0.11444 | 0.013733 | 0.050354 | 0.064087 | -0.022888 | -0.07782 | -0.068665 | 0.10986 | 0.036621 | 122.5021 | 122.4014 | -0.068664 | 122.4152 | 122.4335 | 0.032043 | 0.041199 | 122.4976 | 122.4243 | -0.073242 | 122.438 | 122.3648 | -0.059509 | -0.064087 | 122.3145 | 122.4243 | 122.4747 | 0.018311 | 122.3099 | 122.319 | 122.4518 | 0.041199
1917.625 | 122.5571 | -122.4106 | 0.032043 | 0.067444 | -0.0037897 | -0.063303 | 0.019493 | -0.015319 | 0.00061092 | -0.0063297 | 0.045013 | 0.0207 | 0.023684 | 0.024481 | 0.018293 | 0.014294 | -0.022888 | -0.086975 | -0.022888 | -0.009155 | -0.050354 | 0.07782 | -0.027466 | 0.013733 | -0.036621 | -0.11902 | -0.022888 | -0.036621 | 0.086975 | 0.013733 | 122.4884 | 122.3831 | -0.082397 | 122.3236 | 122.4014 | 0.018311 | -0.054931 | 122.4976 | 122.4243 | -0.054931 | 122.4243 | 122.2916 | -0.13275 | -0.068664 | 122.3602 | 122.3877 | 122.3877 | -0.059509 | 122.3877 | 122.374 | 122.374 | -0.01831
1919.3438 | 122.5479 | -122.4106 | 0.022888 | 0.059815 | -0.0031489 | -0.057535 | 0.017784 | -0.014464 | 0.00018372 | -0.0067569 | -0.016022 | 0.022409 | 0.021762 | 0.022559 | 0.017865 | 0.015148 | -0.018311 | -0.059509 | -0.004578 | -0.004578 | -0.054932 | 0.073242 | -0.041199 | -0.032043 | -0.018311 | -0.13275 | -0.041199 | -0.027466 | 0.064087 | 0.013733 | 122.4838 | 122.3694 | -0.07782 | 122.3511 | 122.406 | 0.036621 | -0.041199 | 122.4747 | 122.4243 | -0.064087 | 122.3785 | 122.2778 | -0.14648 | -0.050354 | 122.3557 | 122.3923 | 122.406 | -0.064087 | 122.3694 | 122.3831 | 122.3923 | -0.009155
1921.0781 | 122.5937 | -122.4197 | 0.018311 | -0.15381 | -0.00037168 | -0.060099 | 0.023552 | -0.012542 | -0.0019525 | -0.0035525 | -0.15335 | 0.021982 | 0.024325 | 0.023413 | 0.014447 | 0.013653 | -0.009155 | -0.054932 | 0.032043 | 0.027466 | -0.027466 | 0.082397 | -0.032043 | 0.022888 | 0.050354 | -0.064087 | -0.054932 | -0.032043 | 0.059509 | 0.004578 | 122.5021 | 122.3877 | -0.045777 | 122.3648 | 122.4472 | 0.059509 | -0.027466 | 122.4792 | 122.4243 | -0.073243 | 122.4426 | 122.3557 | -0.068665 | -0.050354 | 122.3923 | 122.4106 | 122.4518 | -0.050354 | 122.3648 | 122.3877 | 122.4701 | -0.013733
1922.75 | 122.6578 | -122.3831 | 0.004578 | 0.029297 | -0.0099847 | -0.057749 | 0.01928 | -0.013824 | -0.011565 | -0.0046207 | 0.09079 | 0.018777 | 0.02283 | 0.02384 | 0.012952 | 0.017925 | 0.022888 | 0.032043 | 0.082397 | 0.022888 | -0.073242 | 0.10529 | -0.004578 | 0.064087 | 0.059509 | -0.004578 | -0.07782 | -0.054932 | 0.091553 | 0.036621 | 122.4884 | 122.3785 | -0.07782 | 122.4152 | 122.406 | 0.027466 | 0.01831 | 122.4747 | 122.4197 | -0.082398 | 122.4472 | 122.3785 | -0.041199 | -0.05951 | 122.3099 | 122.406 | 122.4655 | -0.009156 | 122.3053 | 122.3282 | 122.4426 | 0.032043
1924.4688 | 122.6028 | -122.3877 | -0.004578 | -0.1767 | -0.0052851 | -0.059031 | 0.023338 | -0.012542 | -0.0075067 | -0.0073977 | -0.10757 | 0.017923 | 0.022189 | 0.023199 | 0.011029 | 0.014294 | 0.091553 | 0.091553 | 0.16937 | 0.082397 | -0.086975 | 0.11902 | 0.013733 | 0.091553 | 0.16022 | 0.041199 | -0.086975 | -0.068665 | 0.10986 | 0.036621 | 122.5067 | 122.4014 | -0.082397 | 122.4792 | 122.4701 | 0.068664 | 0.096131 | 122.4976 | 122.4243 | -0.082397 | 122.4792 | 122.4289 | 0.004578 | -0.064087 | 122.3007 | 122.4792 | 122.5571 | 0.018311 | 122.3007 | 122.319 | 122.5479 | 0.041199
1926.1719 | 122.6074 | -122.3877 | 0.045776 | -0.13855 | -0.0046441 | -0.062448 | 0.021629 | -0.014037 | 0.00082452 | -0.0056887 | -0.14572 | 0.021768 | 0.023044 | 0.024695 | 0.015515 | 0.012798 | 0.045776 | -0.022888 | 0.036621 | 0.032043 | -0.050354 | 0.073242 | -0.032043 | 0.036621 | 0.059509 | -0.045776 | -0.054932 | -0.018311 | 0.073242 | 0.013733 | 122.4609 | 122.3557 | -0.09613 | 122.3648 | 122.4197 | 0.064086 | 0 | 122.4609 | 122.4014 | -0.10071 | 122.4243 | 122.3419 | -0.059509 | -0.064087 | 122.3373 | 122.4335 | 122.4243 | -0.077819 | 122.3328 | 122.3694 | 122.4472 | -0.032043
1927.9219 | 122.6028 | -122.4014 | 0.013733 | -0.11566 | -0.0027215 | -0.06138 | 0.02227 | -0.011474 | -0.0010981 | -0.0046207 | -0.13046 | 0.021768 | 0.023684 | 0.02384 | 0.015729 | 0.013225 | 0.032043 | -0.009155 | 0.041199 | 0.022888 | -0.054932 | 0.073242 | -0.018311 | 0.041199 | 0.064087 | -0.045776 | -0.041199 | -0.032043 | 0.068665 | 0.009155 | 122.4747 | 122.3831 | -0.068665 | 122.3923 | 122.4243 | 0.041199 | 0.01831 | 122.4701 | 122.4106 | -0.054932 | 122.4426 | 122.3557 | -0.054931 | -0.045776 | 122.3465 | 122.4335 | 122.4426 | -0.032044 | 122.3602 | 122.3694 | 122.4655 | -0.004578
1929.6094 | 122.5845 | -122.4152 | 0 | 0.11322 | -0.0054987 | -0.059031 | 0.018639 | -0.015105 | -0.0013117 | -0.0048343 | 0.11368 | 0.020273 | 0.023471 | 0.022772 | 0.017224 | 0.015362 | -0.013733 | -0.068665 | -0.013733 | -0.004578 | -0.050354 | 0.086975 | -0.022888 | 0.004578 | -0.009155 | -0.09613 | -0.045776 | -0.022888 | 0.073242 | 0.004578 | 122.5021 | 122.3923 | -0.050354 | 122.3465 | 122.4106 | 0.01831 | -0.013733 | 122.4884 | 122.4197 | -0.045776 | 122.4197 | 122.319 | -0.10071 | -0.022888 | 122.3648 | 122.4014 | 122.4014 | -0.022888 | 122.3694 | 122.3923 | 122.406 | 0.004578
1931.2969 | 122.5479 | -122.438 | 0.018311 | 0.0064086 | -0.0025079 | -0.06074 | 0.021202 | -0.012969 | -0.00045708 | -0.0039797 | 0.014496 | 0.021768 | 0.024753 | 0.022772 | 0.017224 | 0.015789 | 0.004578 | -0.032043 | 0.009155 | -0.004578 | -0.064087 | 0.086975 | -0.018311 | -0.009155 | -0.009155 | -0.1236 | -0.036621 | -0.041199 | 0.050354 | 0.022888 | 122.525 | 122.4197 | -0.082398 | 122.406 | 122.4335 | 0.013733 | -0.013733 | 122.4884 | 122.4609 | -0.054932 | 122.4289 | 122.3145 | -0.14648 | -0.05951 | 122.374 | 122.4426 | 122.4472 | -0.036622 | 122.4014 | 122.3969 | 122.4289 | 0.004577
1933 | 122.5754 | -122.4289 | 0.018311 | 0.082703 | -0.0046441 | -0.059885 | 0.019066 | -0.01361 | -0.00045708 | -0.0020571 | 0.10605 | 0.0207 | 0.024112 | 0.023199 | 0.017438 | 0.016857 | -0.050354 | -0.091553 | -0.018311 | -0.018311 | -0.059509 | 0.064087 | -0.027466 | 0.004578 | -0.018311 | -0.11444 | -0.059509 | -0.032043 | 0.07782 | 0.009155 | 122.493 | 122.4014 | -0.07782 | 122.3373 | 122.4106 | 0.009155 | -0.068665 | 122.5067 | 122.438 | -0.07782 | 122.4335 | 122.3145 | -0.1236 | -0.050354 | 122.3694 | 122.3785 | 122.4106 | -0.045777 | 122.3694 | 122.3969 | 122.4106 | -0.009156
1934.6875 | 122.6212 | -122.3969 | -0.004578 | 0.13611 | -0.0087031 | -0.05839 | 0.021629 | -0.014678 | -0.0081477 | -0.0050479 | 0.17471 | 0.020486 | 0.02283 | 0.02149 | 0.013166 | 0.016857 | 0.054932 | 0.068665 | 0.11902 | 0.064087 | -0.086975 | 0.10071 | 0.004578 | 0.073242 | 0.086975 | 0.004578 | -0.091553 | -0.050354 | 0.10986 | 0.041199 | 122.4976 | 122.4014 | -0.082397 | 122.4655 | 122.4609 | 0.059509 | 0.05951 | 122.5067 | 122.4381 | -0.086975 | 122.4701 | 122.4014 | -0.036621 | -0.045776 | 122.3099 | 122.4518 | 122.5159 | 0.009156 | 122.3053 | 122.3465 | 122.4838 | 0.045777
1936.4062 | 122.5342 | -122.4152 | 0.036621 | -0.046997 | -0.0057123 | -0.06074 | 0.02227 | -0.013824 | 0.0014655 | -0.0048343 | -0.054169 | 0.023691 | 0.023684 | 0.026404 | 0.015943 | 0.015575 | 0.054932 | 0 | 0.059509 | 0.036621 | -0.059509 | 0.091553 | -0.027466 | 0.036621 | 0.059509 | -0.059509 | -0.050354 | -0.032043 | 0.086975 | 0.009155 | 122.5067 | 122.3877 | -0.09613 | 122.4152 | 122.4518 | 0.064087 | 0.018311 | 122.5021 | 122.4243 | -0.086975 | 122.4518 | 122.3557 | -0.068664 | -0.068664 | 122.3557 | 122.4701 | 122.4747 | -0.064087 | 122.3648 | 122.3831 | 122.4747 | -0.027466
1938.1406 | 122.6486 | -122.4014 | 0.004578 | 0.16663 | -0.0042169 | -0.060312 | 0.021202 | -0.015105 | -0.0081477 | -0.0039797 | 0.16708 | 0.019632 | 0.021548 | 0.021063 | 0.012738 | 0.016003 | 0.10529 | 0.086975 | 0.15564 | 0.068665 | -0.082397 | 0.13275 | 0.018311 | 0.12817 | 0.11902 | 0.050354 | -0.091553 | -0.059509 | 0.10529 | 0.036621 | 122.5342 | 122.4197 | -0.086975 | 122.4884 | 122.4701 | 0.050354 | 0.10071 | 122.5067 | 122.438 | -0.096131 | 122.5296 | 122.4518 | 0.013733 | -0.064087 | 122.319 | 122.5067 | 122.5571 | 0.013733 | 122.3099 | 122.3419 | 122.5204 | 0.032043
1939.8281 | 122.5754 | -122.438 | 0.027466 | 0.082703 | -0.0044305 | -0.059244 | 0.02227 | -0.014251 | -0.00067088 | -0.0041933 | 0.08316 | 0.023691 | 0.024966 | 0.022131 | 0.017438 | 0.012157 | 0 | -0.082397 | -0.004578 | -0.009155 | -0.045776 | 0.073242 | -0.022888 | 0.004578 | -0.036621 | -0.10986 | -0.050354 | -0.027466 | 0.068665 | 0.013733 | 122.5113 | 122.4152 | -0.073242 | 122.3557 | 122.4289 | 0.013733 | -0.027466 | 122.5067 | 122.4518 | -0.07782 | 122.4426 | 122.3282 | -0.1236 | -0.054932 | 122.3923 | 122.438 | 122.4335 | -0.050354 | 122.3877 | 122.4106 | 122.4014 | -0.013733
1941.5312 | 122.7127 | -122.3923 | 0 | -0.0012209 | -0.0052851 | -0.061808 | 0.026115 | -0.012755 | -0.01242 | -0.0048343 | 0.022125 | 0.019418 | 0.024966 | 0.022131 | 0.010389 | 0.016643 | 0.036621 | 0.022888 | 0.10529 | 0.041199 | -0.073242 | 0.11444 | 0 | 0.09613 | 0.13733 | 0.032043 | -0.07782 | -0.059509 | 0.10986 | 0.041199 | 122.5067 | 122.3923 | -0.073242 | 122.4152 | 122.4335 | 0.041199 | 0.036621 | 122.5021 | 122.4335 | -0.07782 | 122.4884 | 122.4243 | -0.009156 | -0.059509 | 122.319 | 122.4289 | 122.4976 | 0 | 122.3145 | 122.3328 | 122.5296 | 0.041199
1943.2344 | 122.644 | -122.3923 | 0.022888 | 0.15137 | -0.0080621 | -0.059031 | 0.020775 | -0.012969 | -0.0049433 | -0.0084659 | 0.12894 | 0.01835 | 0.023257 | 0.021063 | 0.01402 | 0.013012 | 0.091553 | 0.064087 | 0.11444 | 0.045776 | -0.064087 | 0.10986 | 0.009155 | 0.10071 | 0.07782 | 0.004578 | -0.086975 | -0.068665 | 0.1236 | 0.041199 | 122.5021 | 122.4014 | -0.086975 | 122.4564 | 122.438 | 0.036621 | 0.068665 | 122.5159 | 122.4335 | -0.10986 | 122.493 | 122.3969 | -0.036621 | -0.091553 | 122.3282 | 122.4838 | 122.5067 | -0.013733 | 122.3053 | 122.3236 | 122.4701 | 0.018311
1945.0156 | 122.6807 | -122.4152 | 0.004578 | 0.0064086 | -0.0061395 | -0.060099 | 0.019707 | -0.01361 | -0.0066523 | -0.0078249 | 0.075531 | 0.019632 | 0.023044 | 0.022345 | 0.012952 | 0.014507 | 0.036621 | 0.032043 | 0.082397 | 0.027466 | -0.07782 | 0.10071 | 0 | 0.064087 | 0.07782 | -0.013733 | -0.054932 | -0.064087 | 0.07782 | 0.027466 | 122.5159 | 122.4152 | -0.082398 | 122.4472 | 122.4426 | 0.027466 | 0.032043 | 122.493 | 122.4426 | -0.05951 | 122.4792 | 122.4014 | -0.041199 | -0.068665 | 122.3373 | 122.4518 | 122.4976 | -0.004578 | 122.3602 | 122.3511 | 122.493 | 0.022888
1946.6875 | 122.644 | -122.4014 | 0.022888 | -0.16907 | -0.0052851 | -0.060312 | 0.021416 | -0.011046 | -0.0034479 | -0.0078249 | -0.1152 | 0.019846 | 0.023257 | 0.021704 | 0.013593 | 0.012585 | 0.10986 | 0.091553 | 0.14191 | 0.086975 | -0.082397 | 0.10529 | 0 | 0.10986 | 0.15106 | 0.041199 | -0.068665 | -0.059509 | 0.09613 | 0.036621 | 122.5067 | 122.4014 | -0.10528 | 122.493 | 122.4884 | 0.086975 | 0.086975 | 122.4976 | 122.438 | -0.091553 | 122.5113 | 122.4426 | 0.004578 | -0.082397 | 122.319 | 122.5113 | 122.5433 | -0.022888 | 122.3328 | 122.3419 | 122.5525 | 0.013733
1948.4062 | 122.6852 | -122.3969 | 0.036621 | -0.10803 | -0.0054987 | -0.059031 | 0.022911 | -0.012969 | -0.0062249 | -0.0067569 | -0.084686 | 0.020273 | 0.023898 | 0.02384 | 0.014234 | 0.014294 | 0.1236 | 0.1236 | 0.15106 | 0.091553 | -0.082397 | 0.11902 | 0.013733 | 0.15564 | 0.17395 | 0.073242 | -0.086975 | -0.068665 | 0.086975 | 0.045776 | 122.5159 | 122.4106 | -0.11902 | 122.5204 | 122.4884 | 0.07782 | 0.086975 | 122.4838 | 122.4426 | -0.1236 | 122.5525 | 122.4701 | 0.027466 | -0.10529 | 122.3145 | 122.5204 | 122.5479 | -0.022888 | 122.3099 | 122.3282 | 122.5708 | 0.009155
1950.0938 | 122.7036 | -122.3969 | 0.027466 | -0.092773 | -0.0065667 | -0.058603 | 0.022484 | -0.011901 | -0.0049433 | -0.0078249 | -0.092316 | 0.019418 | 0.021975 | 0.021277 | 0.014875 | 0.015148 | 0.10071 | 0.10529 | 0.13733 | 0.07782 | -0.07782 | 0.09613 | 0.018311 | 0.15106 | 0.15564 | 0.059509 | -0.073242 | -0.059509 | 0.11902 | 0.041199 | 122.493 | 122.4152 | -0.10529 | 122.5021 | 122.4747 | 0.059509 | 0.073242 | 122.5159 | 122.4381 | -0.10071 | 122.5479 | 122.4564 | 0.01831 | -0.086975 | 122.319 | 122.4976 | 122.5342 | -0.009155 | 122.3236 | 122.3373 | 122.5525 | 0.013733
1951.7812 | 122.6532 | -122.406 | 0.013733 | -0.15381 | -0.0025079 | -0.059885 | 0.023338 | -0.012969 | -0.0049433 | -0.0061161 | -0.16861 | 0.017709 | 0.024753 | 0.022345 | 0.014661 | 0.012371 | 0.11444 | 0.10071 | 0.13733 | 0.082397 | -0.082397 | 0.11444 | -0.004578 | 0.13275 | 0.16022 | 0.036621 | -0.082397 | -0.064087 | 0.09613 | 0.032043 | 122.5204 | 122.4014 | -0.09613 | 122.5067 | 122.4884 | 0.086975 | 0.10071 | 122.5021 | 122.438 | -0.09613 | 122.5388 | 122.4426 | 0.004578 | -0.07782 | 122.3236 | 122.5204 | 122.5433 | -0.018311 | 122.3236 | 122.3419 | 122.5662 | 0.01831
1953.4688 | 122.5845 | -122.4243 | 0.013733 | -0.085144 | -0.0054987 | -0.060953 | 0.017571 | -0.01126 | 0.0027471 | -0.0046207 | -0.16098 | 0.021341 | 0.02283 | 0.02384 | 0.01872 | 0.012371 | 0.068665 | 0.018311 | 0.059509 | 0.027466 | -0.045776 | 0.073242 | -0.032043 | 0.086975 | 0.073242 | -0.059509 | -0.050354 | -0.045776 | 0.07782 | 0.013733 | 122.4976 | 122.3923 | -0.059509 | 122.4426 | 122.4518 | 0.059509 | 0.054932 | 122.5021 | 122.438 | -0.064087 | 122.5113 | 122.3648 | -0.073242 | -0.059509 | 122.3785 | 122.493 | 122.4838 | -0.045776 | 122.374 | 122.3785 | 122.4976 | 0
1955.1719 | 122.644 | -122.4152 | 0.018311 | -0.13855 | -0.0018671 | -0.060953 | 0.023552 | -0.010192 | -0.0062249 | -0.0059023 | -0.14572 | 0.0207 | 0.024753 | 0.022559 | 0.013166 | 0.015148 | 0.10071 | 0.11444 | 0.15564 | 0.086975 | -0.07782 | 0.10986 | 0.009155 | 0.12817 | 0.16937 | 0.036621 | -0.073242 | -0.068665 | 0.086975 | 0.032043 | 122.525 | 122.4243 | -0.096131 | 122.5296 | 122.5021 | 0.07782 | 0.082397 | 122.5021 | 122.4472 | -0.091553 | 122.5433 | 122.4518 | 0.004578 | -0.086976 | 122.3373 | 122.5159 | 122.5708 | -0.009156 | 122.3419 | 122.3465 | 122.5845 | 0.013732
1956.8906 | 122.5616 | -122.4152 | 0.036621 | -0.1767 | -0.0012263 | -0.060099 | 0.02227 | -0.012542 | -0.0023797 | -0.0071841 | -0.18387 | 0.020273 | 0.025393 | 0.023413 | 0.013379 | 0.014721 | 0.013733 | 0.004578 | 0.036621 | 0.009155 | -0.041199 | 0.073242 | -0.022888 | 0.036621 | 0.045776 | -0.07782 | -0.032043 | -0.022888 | 0.059509 | 0 | 122.4884 | 122.3923 | -0.07782 | 122.4197 | 122.4243 | 0.032043 | -0.022888 | 122.4747 | 122.4152 | -0.068664 | 122.4518 | 122.3373 | -0.07782 | -0.059509 | 122.374 | 122.4289 | 122.4518 | -0.059509 | 122.3831 | 122.3923 | 122.4609 | -0.036621
1958.5625 | 122.6852 | -122.4014 | -0.009155 | 0.10559 | -0.0065667 | -0.062662 | 0.018211 | -0.01361 | -0.0013117 | -0.0048343 | 0.014496 | 0.021127 | 0.021121 | 0.024481 | 0.019361 | 0.013439 | 0 | -0.036621 | 0.004578 | 0 | -0.045776 | 0.082397 | -0.027466 | 0.054932 | 0.004578 | -0.086975 | -0.050354 | -0.041199 | 0.091553 | 0.009155 | 122.4838 | 122.374 | -0.036621 | 122.3648 | 122.4014 | 0.027466 | 0.009155 | 122.493 | 122.4106 | -0.041199 | 122.4564 | 122.3145 | -0.09613 | -0.032044 | 122.3557 | 122.4014 | 122.406 | -0.018311 | 122.3511 | 122.3602 | 122.406 | 0.01831
1960.25 | 122.5616 | -122.4564 | 0.032043 | -0.21484 | -0.0020807 | -0.060312 | 0.022911 | -0.014037 | -0.0047297 | -0.0046207 | -0.099945 | 0.022195 | 0.024112 | 0.022986 | 0.014234 | 0.016857 | 0.036621 | 0.032043 | 0.064087 | 0.050354 | -0.054932 | 0.07782 | -0.032043 | 0.013733 | 0.036621 | -0.064087 | -0.050354 | -0.045776 | 0.059509 | 0.013733 | 122.5342 | 122.4243 | -0.086975 | 122.4884 | 122.5067 | 0.082397 | 0.004578 | 122.5159 | 122.4701 | -0.082397 | 122.4701 | 122.3923 | -0.07782 | -0.077819 | 122.4014 | 122.493 | 122.5204 | -0.064086 | 122.406 | 122.4106 | 122.493 | -0.01831
1961.9219 | 122.5983 | -122.4564 | 0.036621 | -0.19196 | -0.0037897 | -0.060526 | 0.025261 | -0.012328 | -2.988e-05 | -0.0056887 | -0.22964 | 0.021341 | 0.023898 | 0.022772 | 0.014447 | 0.014721 | -0.018311 | -0.041199 | 0.018311 | -0.013733 | -0.036621 | 0.082397 | -0.032043 | 0 | 0.032043 | -0.086975 | -0.036621 | -0.013733 | 0.050354 | 0 | 122.5388 | 122.4243 | -0.073242 | 122.4152 | 122.4426 | 0.01831 | -0.054932 | 122.5067 | 122.4564 | -0.073242 | 122.4564 | 122.3694 | -0.086975 | -0.050354 | 122.4197 | 122.438 | 122.4747 | -0.068664 | 122.4197 | 122.4426 | 122.4884 | -0.036621
1963.6094 | 122.58 | -122.4335 | 0.032043 | -0.16907 | -0.00079888 | -0.063517 | 0.023766 | -0.013183 | -0.0049433 | -0.0067569 | -0.19913 | 0.019846 | 0.024112 | 0.021704 | 0.013379 | 0.015362 | 0.068665 | 0.07782 | 0.1236 | 0.068665 | -0.073242 | 0.091553 | 0.004578 | 0.068665 | 0.11902 | -0.013733 | -0.07782 | -0.036621 | 0.10529 | 0.009155 | 122.525 | 122.438 | -0.10529 | 122.5113 | 122.5021 | 0.064087 | 0.036622 | 122.5388 | 122.4426 | -0.10986 | 122.5021 | 122.4197 | -0.022888 | -0.068664 | 122.3602 | 122.5021 | 122.5571 | -0.027465 | 122.3557 | 122.3969 | 122.5525 | -0.022888
1965.2812 | 122.7127 | -122.3923 | -0.013733 | 0.159 | -0.0035761 | -0.061594 | 0.018211 | -0.012755 | -0.0036615 | -0.0026981 | 0.098419 | 0.021127 | 0.023044 | 0.019354 | 0.01872 | 0.013866 | 0.09613 | 0.07782 | 0.11444 | 0.068665 | -0.073242 | 0.09613 | 0 | 0.13275 | 0.11444 | 0.036621 | -0.086975 | -0.064087 | 0.11902 | 0.027466 | 122.4884 | 122.3923 | -0.059509 | 122.4701 | 122.4609 | 0.068665 | 0.10986 | 122.5113 | 122.4197 | -0.073242 | 122.525 | 122.4289 | 0.009155 | -0.050354 | 122.319 | 122.4884 | 122.5067 | 0.013733 | 122.3053 | 122.3282 | 122.5067 | 0.041199
1967.0156 | 122.6578 | -122.4335 | -0.004578 | 0.082703 | -0.0027215 | -0.060312 | 0.024193 | -0.015319 | -0.0075067 | -0.0056887 | 0.09079 | 0.021768 | 0.025607 | 0.019995 | 0.016156 | 0.015789 | 0.054932 | 0.059509 | 0.09613 | 0.054932 | -0.082397 | 0.10986 | 0.022888 | 0.086975 | 0.086975 | -0.004578 | -0.064087 | -0.064087 | 0.10071 | 0.013733 | 122.5433 | 122.4564 | -0.077819 | 122.493 | 122.4884 | 0.032044 | 0.05951 | 122.5342 | 122.4472 | -0.059509 | 122.5204 | 122.4289 | -0.018311 | -0.059509 | 122.3511 | 122.4884 | 122.5296 | 0.027466 | 122.3694 | 122.3694 | 122.5204 | 0.018311
1968.7031 | 122.6303 | -122.4472 | 0.018311 | -0.085144 | 0.00048272 | -0.059244 | 0.020348 | -0.01126 | 0.0038153 | -0.0041933 | -0.17624 | 0.020486 | 0.023257 | 0.025549 | 0.01637 | 0.014294 | 0.054932 | 0 | 0.059509 | 0.036621 | -0.059509 | 0.07782 | -0.022888 | 0.059509 | 0.068665 | -0.036621 | -0.036621 | -0.027466 | 0.07782 | 0 | 122.525 | 122.4243 | -0.07782 | 122.4472 | 122.4838 | 0.059509 | 0.036621 | 122.525 | 122.4472 | -0.054932 | 122.5067 | 122.4106 | -0.036621 | -0.045777 | 122.3877 | 122.5021 | 122.5067 | -0.041199 | 122.4106 | 122.4197 | 122.5159 | -0.018311
1970.4062 | 122.699 | -122.3969 | -0.009155 | 0.10559 | -0.0027215 | -0.06074 | 0.020134 | -0.013183 | -0.0025935 | -0.0029117 | 0.13657 | 0.021555 | 0.023257 | 0.024481 | 0.018079 | 0.015362 | 0.013733 | -0.027466 | 0.022888 | 0 | -0.041199 | 0.10071 | -0.018311 | 0.082397 | 0.045776 | -0.036621 | -0.054932 | -0.041199 | 0.073242 | 0.027466 | 122.4976 | 122.3785 | -0.032044 | 122.3694 | 122.3969 | 0.018311 | 0.022888 | 122.4701 | 122.4243 | -0.045777 | 122.4792 | 122.3602 | -0.064087 | -0.032044 | 122.3557 | 122.4106 | 122.4197 | -0.009156 | 122.3419 | 122.3557 | 122.4426 | 0.036621
1972.1094 | 122.5983 | -122.4564 | 0.013733 | 0.075073 | -0.0031489 | -0.060312 | 0.021629 | -0.018737 | 0.00018372 | -0.0033389 | 0.098419 | 0.024332 | 0.024112 | 0.024054 | 0.017224 | 0.017712 | -0.009155 | -0.068665 | 0.004578 | 0 | -0.041199 | 0.07782 | -0.013733 | 0.018311 | -0.013733 | -0.091553 | -0.036621 | -0.041199 | 0.073242 | -0.013733 | 122.5342 | 122.4426 | -0.054932 | 122.3877 | 122.4564 | 0.013733 | -0.022888 | 122.5296 | 122.4426 | -0.050354 | 122.4747 | 122.3648 | -0.07782 | -0.054932 | 122.4152 | 122.4472 | 122.4609 | -0.027466 | 122.4197 | 122.4152 | 122.4426 | -0.027466
1973.7812 | 122.6624 | -122.4518 | 0.004578 | 0.097962 | -0.0052851 | -0.060099 | 0.019493 | -0.014678 | -0.0068659 | -0.0041933 | 0.17471 | 0.020059 | 0.021762 | 0.02149 | 0.014447 | 0.017071 | 0.07782 | 0.10071 | 0.13275 | 0.059509 | -0.086975 | 0.13733 | 0.018311 | 0.10529 | 0.1236 | 0.032043 | -0.073242 | -0.068665 | 0.09613 | 0.036621 | 122.5891 | 122.4701 | -0.091553 | 122.5525 | 122.5113 | 0.041198 | 0.073242 | 122.5479 | 122.4884 | -0.07782 | 122.5571 | 122.4838 | -0.004578 | -0.073243 | 122.3648 | 122.5296 | 122.5845 | 0.013733 | 122.3785 | 122.3831 | 122.5754 | 0.032043
1975.4688 | 122.5571 | -122.4335 | 0.022888 | -0.0012209 | -0.00079888 | -0.060312 | 0.021202 | -0.014251 | 0.00082452 | -0.0046207 | -0.0083922 | 0.022623 | 0.021975 | 0.023627 | 0.019361 | 0.015575 | 0.036621 | -0.013733 | 0.022888 | 0.027466 | -0.064087 | 0.091553 | -0.018311 | 0.013733 | 0.009155 | -0.09613 | -0.045776 | -0.032043 | 0.07782 | 0 | 122.525 | 122.4152 | -0.086975 | 122.4197 | 122.4609 | 0.045777 | 0.013733 | 122.5113 | 122.4335 | -0.068664 | 122.4472 | 122.3373 | -0.09613 | -0.054931 | 122.3694 | 122.4701 | 122.4564 | -0.041199 | 122.3877 | 122.4014 | 122.4426 | -0.022888
1977.1562 | 122.6715 | -122.438 | 0.018311 | -0.14618 | -0.0031489 | -0.06074 | 0.026543 | -0.013183 | -0.0096429 | -0.0039797 | -0.099945 | 0.019418 | 0.024539 | 0.020422 | 0.010602 | 0.016643 | 0.09613 | 0.086975 | 0.16022 | 0.07782 | -0.091553 | 0.10071 | 0.022888 | 0.10529 | 0.16937 | 0.054932 | -0.086975 | -0.068665 | 0.10986 | 0.050354 | 122.5388 | 122.4609 | -0.10986 | 122.525 | 122.5159 | 0.054932 | 0.077819 | 122.5479 | 122.4884 | -0.10529 | 122.5433 | 122.493 | 0.004578 | -0.086976 | 122.3465 | 122.5342 | 122.5983 | 0.004577 | 122.3511 | 122.3694 | 122.6074 | 0.032043
1978.8594 | 122.5845 | -122.4701 | 0.009155 | 0.052185 | -0.0022943 | -0.059671 | 0.020775 | -0.010192 | 0.00082452 | -0.0031253 | 0.0068663 | 0.02305 | 0.023684 | 0.022772 | 0.016797 | 0.014721 | -0.013733 | -0.082397 | -0.013733 | -0.013733 | -0.041199 | 0.068665 | -0.027466 | -0.018311 | -0.018311 | -0.13275 | -0.036621 | -0.036621 | 0.082397 | 0.013733 | 122.5388 | 122.4426 | -0.050354 | 122.3877 | 122.4564 | 0.013733 | -0.022888 | 122.5525 | 122.4838 | -0.045776 | 122.4518 | 122.3373 | -0.14648 | -0.045776 | 122.4289 | 122.4564 | 122.4564 | -0.036621 | 122.4335 | 122.4335 | 122.4518 | 0.004578
1980.5469 | 122.6578 | -122.4472 | 0.004578 | 0.12848 | -0.00079888 | -0.060953 | 0.018639 | -0.0099784 | -0.0028071 | -0.0039797 | 0.09079 | 0.022836 | 0.024112 | 0.023199 | 0.015943 | 0.016857 | 0 | -0.064087 | -0.013733 | 0 | -0.022888 | 0.086975 | -0.022888 | 0.013733 | 0.004578 | -0.091553 | -0.041199 | -0.036621 | 0.07782 | 0.009155 | 122.5342 | 122.4243 | -0.027466 | 122.3831 | 122.4472 | 0.022888 | -0.004578 | 122.525 | 122.4564 | -0.045777 | 122.4609 | 122.3557 | -0.10071 | -0.041199 | 122.4243 | 122.4472 | 122.4335 | -0.027466 | 122.406 | 122.4106 | 122.4518 | 0.004577
1982.2188 | 122.731 | -122.406 | -0.004578 | 0.029297 | -0.0061395 | -0.059244 | 0.023125 | -0.015319 | -0.0090021 | -0.0063297 | 0.060272 | 0.022623 | 0.027316 | 0.020209 | 0.01167 | 0.01643 | 0.022888 | 0.027466 | 0.091553 | 0.045776 | -0.068665 | 0.091553 | -0.009155 | 0.073242 | 0.10071 | 0.018311 | -0.068665 | -0.054932 | 0.09613 | 0.036621 | 122.4976 | 122.3969 | -0.064087 | 122.4335 | 122.4518 | 0.054931 | 0.027466 | 122.5021 | 122.4426 | -0.064087 | 122.4792 | 122.4243 | -0.01831 | -0.050354 | 122.3373 | 122.4289 | 122.4976 | -0.004577 | 122.3373 | 122.3511 | 122.5067 | 0.041199
1983.8906 | 122.6257 | -122.4518 | 0.022888 | -0.16144 | -0.0025079 | -0.064157 | 0.024406 | -0.013824 | -0.0057977 | -0.0067569 | -0.092316 | 0.022836 | 0.024112 | 0.022345 | 0.012097 | 0.013225 | 0.10071 | 0.09613 | 0.14191 | 0.086975 | -0.082397 | 0.10986 | 0 | 0.09613 | 0.14648 | 0.036621 | -0.091553 | -0.050354 | 0.091553 | 0.032043 | 122.5616 | 122.4518 | -0.10528 | 122.5479 | 122.5388 | 0.086975 | 0.07782 | 122.5433 | 122.4838 | -0.11444 | 122.5479 | 122.4884 | 0.004578 | -0.073242 | 122.3694 | 122.5525 | 122.5937 | -0.022888 | 122.3602 | 122.4014 | 122.5983 | 0.009155
1985.6094 | 122.6807 | -122.4014 | -0.004578 | 0.14374 | -0.0044305 | -0.060953 | 0.018425 | -0.011474 | -0.0047297 | -0.0050479 | 0.16708 | 0.019632 | 0.024325 | 0.025122 | 0.01402 | 0.012371 | 0.10986 | 0.091553 | 0.13275 | 0.082397 | -0.091553 | 0.13275 | 0.013733 | 0.13733 | 0.12817 | 0.036621 | -0.082397 | -0.068665 | 0.10986 | 0.050354 | 122.5342 | 122.4152 | -0.086975 | 122.493 | 122.4838 | 0.068664 | 0.11444 | 122.5113 | 122.4518 | -0.077819 | 122.5388 | 122.438 | -0.013733 | -0.064087 | 122.3099 | 122.5113 | 122.5342 | 0.018311 | 122.319 | 122.3328 | 122.5296 | 0.054932
1987.2969 | 122.7127 | -122.438 | -0.004578 | -0.039368 | -0.0048579 | -0.061167 | 0.023338 | -0.014037 | -0.0077203 | -0.0078249 | -0.099945 | 0.019846 | 0.023684 | 0.024908 | 0.011243 | 0.015789 | 0.073242 | 0.054932 | 0.11444 | 0.064087 | -0.07782 | 0.11444 | -0.004578 | 0.14648 | 0.14648 | 0.050354 | -0.091553 | -0.054932 | 0.09613 | 0.050354 | 122.5525 | 122.4335 | -0.073242 | 122.493 | 122.5021 | 0.068665 | 0.07782 | 122.5342 | 122.4884 | -0.086975 | 122.5845 | 122.4884 | 0 | -0.050354 | 122.3602 | 122.5113 | 122.5525 | 0 | 122.3465 | 122.3831 | 122.5845 | 0.054932
1989 | 122.5708 | -122.4472 | 0.027466 | -0.0088499 | -0.00079888 | -0.063517 | 0.021629 | -0.012328 | 0.0021063 | -0.0050479 | -0.054169 | 0.024759 | 0.027102 | 0.024695 | 0.018933 | 0.014294 | 0.050354 | -0.013733 | 0.036621 | 0.009155 | -0.054932 | 0.091553 | -0.032043 | 0.032043 | 0.009155 | -0.086975 | -0.036621 | -0.027466 | 0.091553 | -0.004578 | 122.5388 | 122.4152 | -0.082398 | 122.4335 | 122.4564 | 0.041198 | 0.022888 | 122.5388 | 122.4426 | -0.064087 | 122.4792 | 122.3602 | -0.082397 | -0.054932 | 122.3923 | 122.4976 | 122.4838 | -0.059509 | 122.4106 | 122.4197 | 122.4564 | -0.032044
1990.7188 | 122.5937 | -122.4747 | 0.032043 | -0.20721 | -0.00079888 | -0.060099 | 0.022911 | -0.011687 | -0.0028071 | -0.0031253 | -0.1152 | 0.020273 | 0.02518 | 0.022345 | 0.012952 | 0.014294 | 0.027466 | 0.022888 | 0.068665 | 0.027466 | -0.041199 | 0.07782 | -0.032043 | 0.027466 | 0.045776 | -0.064087 | -0.050354 | -0.027466 | 0.064087 | 0 | 122.5525 | 122.4426 | -0.073242 | 122.4976 | 122.5021 | 0.059509 | -0.004577 | 122.5388 | 122.4747 | -0.082397 | 122.5021 | 122.4106 | -0.064087 | -0.059509 | 122.4335 | 122.5021 | 122.5433 | -0.064086 | 122.4243 | 122.4472 | 122.5204 | -0.032043
1992.4062 | 122.6669 | -122.4426 | 0 | 0.159 | -0.0046441 | -0.060953 | 0.018639 | -0.014037 | -0.0030207 | -0.0076113 | 0.12894 | 0.021341 | 0.022403 | 0.020636 | 0.016584 | 0.015362 | 0.09613 | 0.10071 | 0.13733 | 0.064087 | -0.07782 | 0.13275 | 0.027466 | 0.13733 | 0.1236 | 0.045776 | -0.086975 | -0.07782 | 0.10529 | 0.041199 | 122.5754 | 122.4701 | -0.07782 | 122.5433 | 122.5067 | 0.036621 | 0.09613 | 122.5479 | 122.4838 | -0.086975 | 122.58 | 122.4884 | 0.004577 | -0.07782 | 122.3648 | 122.5388 | 122.58 | 0.027466 | 122.3557 | 122.3648 | 122.5662 | 0.041199
1994.0781 | 122.644 | -122.4518 | 0.022888 | -0.16907 | -0.0016535 | -0.060099 | 0.024834 | -0.012115 | -0.0013117 | -0.0052615 | -0.21439 | 0.021982 | 0.023684 | 0.023413 | 0.013806 | 0.012585 | 0.009155 | -0.032043 | 0.009155 | 0.018311 | -0.041199 | 0.082397 | -0.050354 | 0.013733 | 0.045776 | -0.068665 | -0.032043 | -0.018311 | 0.07782 | 0.004578 | 122.5342 | 122.4014 | -0.064087 | 122.4197 | 122.4701 | 0.068665 | -0.013733 | 122.5296 | 122.4564 | -0.054931 | 122.4655 | 122.3831 | -0.073243 | -0.041199 | 122.4106 | 122.4609 | 122.4609 | -0.073242 | 122.4197 | 122.4335 | 122.4976 | -0.01831
1995.7656 | 122.7219 | -122.4289 | 0.004578 | 0.17426 | -0.0033625 | -0.061167 | 0.019493 | -0.011046 | -0.00045708 | -0.0048343 | 0.12131 | 0.022836 | 0.023684 | 0.024054 | 0.017438 | 0.014294 | 0.027466 | 0 | 0.045776 | 0.032043 | -0.045776 | 0.09613 | -0.009155 | 0.10071 | 0.068665 | 0 | -0.064087 | -0.054932 | 0.10529 | 0.036621 | 122.525 | 122.4197 | -0.050354 | 122.4289 | 122.4609 | 0.041198 | 0.022888 | 122.5342 | 122.4655 | -0.068665 | 122.5296 | 122.4289 | -0.036621 | -0.05951 | 122.3831 | 122.4564 | 122.4747 | -0.013733 | 122.3648 | 122.374 | 122.4976 | 0.032043
1997.4531 | 122.6486 | -122.4701 | 0.018311 | -0.18433 | -0.0048579 | -0.062235 | 0.022911 | -0.012328 | -0.00067088 | -0.0063297 | -0.16098 | 0.021982 | 0.024112 | 0.022559 | 0.013166 | 0.013225 | 0 | -0.036621 | 0 | -0.004578 | -0.032043 | 0.059509 | -0.050354 | 0.009155 | 0.032043 | -0.091553 | -0.041199 | -0.036621 | 0.068665 | -0.013733 | 122.5296 | 122.4197 | -0.050354 | 122.4335 | 122.4655 | 0.045776 | -0.018311 | 122.5388 | 122.4564 | -0.05951 | 122.4792 | 122.3785 | -0.07782 | -0.054932 | 122.4381 | 122.4701 | 122.4701 | -0.068665 | 122.4289 | 122.4335 | 122.5021 | -0.032044
1999.1406 | 122.7264 | -122.4335 | -0.018311 | 0.159 | -0.0044305 | -0.062235 | 0.019066 | -0.015319 | -0.0019525 | -0.0054751 | 0.09079 | 0.02305 | 0.020694 | 0.02384 | 0.017865 | 0.014934 | 0.054932 | 0.022888 | 0.082397 | 0.045776 | -0.064087 | 0.10071 | -0.013733 | 0.11902 | 0.10071 | 0.022888 | -0.082397 | -0.045776 | 0.10529 | 0.036621 | 122.5342 | 122.4197 | -0.045776 | 122.4564 | 122.4792 | 0.059509 | 0.073243 | 122.5388 | 122.4701 | -0.064086 | 122.5525 | 122.4564 | -0.013733 | -0.027465 | 122.3694 | 122.4884 | 122.5159 | 0.004578 | 122.3511 | 122.3877 | 122.5342 | 0.054932
2000.8594 | 122.7448 | -122.4518 | 0 | -0.024109 | -0.0072077 | -0.059244 | 0.020348 | -0.014037 | -0.0081477 | -0.0061161 | 0.029755 | 0.019632 | 0.022403 | 0.02149 | 0.013166 | 0.015575 | 0.045776 | 0.045776 | 0.10529 | 0.054932 | -0.064087 | 0.10529 | 0 | 0.10071 | 0.12817 | 0.045776 | -0.059509 | -0.054932 | 0.10986 | 0.027466 | 122.5571 | 122.4518 | -0.064087 | 122.4976 | 122.5067 | 0.054932 | 0.045776 | 122.5616 | 122.4792 | -0.059509 | 122.5525 | 122.4976 | 0.01831 | -0.054932 | 122.3877 | 122.4976 | 122.5571 | 0 | 122.3923 | 122.3969 | 122.58 | 0.027466
2002.5469 | 122.6349 | -122.4655 | 0.009155 | 0.097962 | -0.0042169 | -0.061167 | 0.01928 | -0.01361 | -0.00024348 | -0.0046207 | 0.067902 | 0.02305 | 0.022189 | 0.023199 | 0.017865 | 0.012585 | 0.018311 | -0.086975 | -0.004578 | -0.004578 | -0.032043 | 0.082397 | -0.036621 | 0.013733 | -0.022888 | -0.11444 | -0.045776 | -0.032043 | 0.064087 | 0.004578 | 122.5479 | 122.4289 | -0.041198 | 122.3785 | 122.4609 | 0.032043 | 0.009156 | 122.5296 | 122.4701 | -0.054931 | 122.4792 | 122.3511 | -0.11902 | -0.041198 | 122.4335 | 122.4838 | 122.4609 | -0.045776 | 122.4197 | 122.4335 | 122.4426 | -0.004577
2004.2344 | 122.6761 | -122.4564 | 0.009155 | 0.12848 | -0.0050715 | -0.060953 | 0.022057 | -0.013824 | -0.0077203 | -0.0056887 | 0.17471 | 0.01835 | 0.023898 | 0.02149 | 0.014661 | 0.01643 | 0.09613 | 0.059509 | 0.1236 | 0.059509 | -0.073242 | 0.12817 | 0.004578 | 0.11444 | 0.10071 | 0.013733 | -0.073242 | -0.054932 | 0.11444 | 0.045776 | 122.5845 | 122.4609 | -0.082397 | 122.5159 | 122.5159 | 0.054931 | 0.086975 | 122.5708 | 122.5021 | -0.082397 | 122.5708 | 122.4701 | -0.032043 | -0.064087 | 122.3831 | 122.5525 | 122.58 | -0.004577 | 122.3831 | 122.4014 | 122.5571 | 0.036621
2005.9844 | 122.7081 | -122.4243 | 0.009155 | 0.021668 | -0.0040033 | -0.060526 | 0.023552 | -0.014464 | -0.0062249 | -0.0076113 | 0.075531 | 0.021555 | 0.023684 | 0.024054 | 0.01167 | 0.014507 | 0.050354 | 0.022888 | 0.082397 | 0.036621 | -0.082397 | 0.1236 | -0.004578 | 0.068665 | 0.073242 | -0.013733 | -0.059509 | -0.036621 | 0.09613 | 0.041199 | 122.5479 | 122.4197 | -0.091552 | 122.4472 | 122.4609 | 0.041199 | 0.041199 | 122.5204 | 122.4655 | -0.068664 | 122.493 | 122.4106 | -0.054932 | -0.045776 | 122.3419 | 122.4747 | 122.5067 | -0.013733 | 122.3648 | 122.3877 | 122.4976 | 0.032044
2007.6719 | 122.644 | -122.4747 | 0.036621 | -0.20721 | -0.0031489 | -0.059244 | 0.020134 | -0.0080558 | -0.0017389 | -0.0061161 | -0.19913 | 0.02305 | 0.025393 | 0.021704 | 0.015729 | 0.013225 | 0.018311 | -0.041199 | 0.009155 | 0.009155 | -0.027466 | 0.064087 | -0.032043 | -0.004578 | 0.013733 | -0.086975 | -0.041199 | -0.018311 | 0.07782 | -0.004578 | 122.5388 | 122.4426 | -0.064087 | 122.4335 | 122.4838 | 0.041198 | -0.01831 | 122.5525 | 122.4701 | -0.07782 | 122.4701 | 122.3877 | -0.082397 | -0.054932 | 122.4472 | 122.493 | 122.4838 | -0.068664 | 122.4335 | 122.4564 | 122.4884 | -0.041199
2009.375 | 122.6761 | -122.4426 | 0.004578 | 0.13611 | -0.0065667 | -0.060526 | 0.017998 | -0.015533 | -0.0057977 | -0.0050479 | 0.13657 | 0.020273 | 0.024112 | 0.020636 | 0.015943 | 0.01643 | 0.09613 | 0.091553 | 0.12817 | 0.073242 | -0.07782 | 0.1236 | 0 | 0.13275 | 0.11444 | 0.036621 | -0.086975 | -0.068665 | 0.086975 | 0.036621 | 122.5662 | 122.4426 | -0.082398 | 122.5342 | 122.5159 | 0.073242 | 0.091552 | 122.5296 | 122.4792 | -0.091553 | 122.5754 | 122.4792 | 0 | -0.073243 | 122.3648 | 122.5388 | 122.5708 | -0.004578 | 122.3557 | 122.374 | 122.5571 | 0.032043
2011.1094 | 122.6761 | -122.438 | 0.018311 | 0.097962 | -0.0052851 | -0.058603 | 0.020348 | -0.012542 | -0.0055841 | -0.0050479 | 0.13657 | 0.021555 | 0.025393 | 0.024054 | 0.015943 | 0.016216 | 0.10529 | 0.09613 | 0.12817 | 0.07782 | -0.059509 | 0.11444 | 0.013733 | 0.13275 | 0.10529 | 0.032043 | -0.086975 | -0.064087 | 0.10986 | 0.027466 | 122.5525 | 122.4518 | -0.07782 | 122.5342 | 122.5159 | 0.064087 | 0.086975 | 122.5479 | 122.4655 | -0.10529 | 122.5708 | 122.4701 | 0.004577 | -0.082398 | 122.3785 | 122.5433 | 122.5662 | -0.004578 | 122.3511 | 122.374 | 122.5433 | 0.009155
2012.8125 | 122.5983 | -122.4838 | 0.022888 | -0.039368 | 0.0032599 | -0.060526 | 0.027184 | -0.014464 | 0.0042425 | -0.0056887 | -0.046539 | 0.024759 | 0.027316 | 0.02384 | 0.016797 | 0.013866 | 0.059509 | 0 | 0.045776 | 0.022888 | -0.036621 | 0.091553 | -0.027466 | 0.022888 | 0.013733 | -0.091553 | -0.054932 | -0.027466 | 0.07782 | 0.013733 | 122.5754 | 122.4564 | -0.059509 | 122.4838 | 122.5067 | 0.050354 | 0.036621 | 122.5616 | 122.4976 | -0.07782 | 122.5067 | 122.3923 | -0.10529 | -0.050354 | 122.4472 | 122.5433 | 122.5296 | -0.050354 | 122.4289 | 122.4564 | 122.4976 | -0.009155
2014.5469 | 122.7264 | -122.4289 | -0.009155 | 0.10559 | -0.0020807 | -0.059458 | 0.019707 | -0.015319 | -0.00024348 | -0.0037661 | 0.12131 | 0.02305 | 0.023898 | 0.023199 | 0.015729 | 0.012798 | 0.022888 | -0.032043 | 0.018311 | 0.004578 | -0.032043 | 0.091553 | -0.013733 | 0.09613 | 0.045776 | -0.054932 | -0.068665 | -0.036621 | 0.082397 | 0.013733 | 122.5204 | 122.4152 | -0.022888 | 122.3969 | 122.4335 | 0.018311 | 0.032043 | 122.5113 | 122.4426 | -0.05951 | 122.525 | 122.374 | -0.068665 | -0.027466 | 122.3969 | 122.4518 | 122.4472 | -0.004578 | 122.3602 | 122.3923 | 122.4747 | 0.022888
2016.2344 | 122.7081 | -122.4426 | 0.009155 | 0.036926 | -0.0042169 | -0.057535 | 0.01992 | -0.012542 | -0.0087885 | -0.0039797 | 0.08316 | 0.018991 | 0.023257 | 0.021918 | 0.011884 | 0.016857 | 0.027466 | 0.036621 | 0.091553 | 0.027466 | -0.073242 | 0.10986 | 0.004578 | 0.07782 | 0.073242 | -0.004578 | -0.082397 | -0.059509 | 0.11902 | 0.041199 | 122.5525 | 122.4472 | -0.082397 | 122.4792 | 122.4701 | 0.022888 | 0.018311 | 122.5616 | 122.4838 | -0.091552 | 122.5204 | 122.438 | -0.045777 | -0.068664 | 122.3694 | 122.4701 | 122.5342 | -0.004577 | 122.3602 | 122.3831 | 122.5159 | 0.032044
2018 | 122.6074 | -122.4976 | 0.013733 | 0.067444 | -0.0018671 | -0.060953 | 0.017357 | -0.013183 | 0.0016791 | -0.0056887 | 0.052643 | 0.022409 | 0.024539 | 0.022345 | 0.017865 | 0.014721 | -0.009155 | -0.10529 | -0.022888 | 0 | -0.032043 | 0.086975 | -0.018311 | 0.009155 | -0.013733 | -0.10986 | -0.050354 | -0.032043 | 0.064087 | 0.004578 | 122.5845 | 122.4792 | -0.045776 | 122.3923 | 122.4976 | 0.018311 | -0.022888 | 122.5616 | 122.5021 | -0.064087 | 122.5067 | 122.3877 | -0.11444 | -0.045776 | 122.4655 | 122.4884 | 122.4747 | -0.032044 | 122.4472 | 122.4655 | 122.4838 | -0.009155
2019.6875 | 122.6532 | -122.4792 | 0.004578 | -0.14618 | -0.00058528 | -0.06074 | 0.023766 | -0.013396 | -0.0023797 | -0.0046207 | -0.17624 | 0.024332 | 0.027743 | 0.023199 | 0.015088 | 0.013866 | 0 | -0.036621 | 0.009155 | 0.009155 | -0.036621 | 0.07782 | -0.045776 | 0.027466 | 0.036621 | -0.073242 | -0.032043 | -0.036621 | 0.064087 | -0.004578 | 122.5571 | 122.4335 | -0.041199 | 122.4426 | 122.4884 | 0.054931 | -0.004578 | 122.5433 | 122.4747 | -0.036621 | 122.5067 | 122.406 | -0.068664 | -0.041199 | 122.4426 | 122.4792 | 122.4884 | -0.050354 | 122.4472 | 122.4426 | 122.5159 | -0.009156
2021.3906 | 122.7219 | -122.4289 | -0.009155 | 0.12085 | -0.0044305 | -0.061167 | 0.022911 | -0.012542 | -0.0010981 | -0.0031253 | 0.075531 | 0.024759 | 0.027743 | 0.023199 | 0.017652 | 0.013866 | 0.009155 | -0.050354 | 0.004578 | -0.013733 | -0.027466 | 0.07782 | -0.022888 | 0.032043 | 0.004578 | -0.082397 | -0.045776 | -0.050354 | 0.073242 | 0.009155 | 122.5067 | 122.406 | -0.018311 | 122.3785 | 122.4152 | 0.009155 | 0.01831 | 122.5021 | 122.438 | -0.036621 | 122.4609 | 122.3465 | -0.091552 | -0.041199 | 122.4014 | 122.438 | 122.4335 | -0.013733 | 122.3831 | 122.3785 | 122.4335 | 0.01831
2023.125 | 122.7402 | -122.4335 | 0.018311 | 0.15137 | -0.00079888 | -0.060526 | 0.024193 | -0.01361 | -0.0045161 | -0.0044071 | 0.1442 | 0.022836 | 0.026889 | 0.024054 | 0.015302 | 0.013653 | 0.032043 | -0.009155 | 0.068665 | 0.013733 | -0.041199 | 0.10071 | 0 | 0.09613 | 0.086975 | 0.009155 | -0.068665 | -0.07782 | 0.10529 | 0.022888 | 122.5342 | 122.4335 | -0.05951 | 122.4243 | 122.4472 | 0.013733 | 0.013732 | 122.5388 | 122.4564 | -0.086976 | 122.5296 | 122.4426 | -0.013733 | -0.096131 | 122.3923 | 122.4655 | 122.5021 | -0.018311 | 122.3648 | 122.3557 | 122.5204 | 0.004577
2024.8125 | 122.6074 | -122.4976 | 0.036621 | -0.062256 | -0.0035761 | -0.059885 | 0.018639 | -0.010833 | -0.0019525 | -0.0026981 | -0.069428 | 0.022836 | 0.023471 | 0.026404 | 0.01872 | 0.016003 | 0.050354 | 0.032043 | 0.059509 | 0.022888 | -0.059509 | 0.091553 | -0.032043 | 0.059509 | 0.073242 | -0.050354 | -0.041199 | -0.032043 | 0.07782 | 0.018311 | 122.5891 | 122.4655 | -0.09613 | 122.5296 | 122.5204 | 0.054931 | 0.013733 | 122.5754 | 122.5159 | -0.07782 | 122.5571 | 122.4472 | -0.068665 | -0.068664 | 122.438 | 122.5479 | 122.5571 | -0.068664 | 122.4564 | 122.4655 | 122.5708 | -0.01831
2026.5156 | 122.6898 | -122.4518 | 0.013733 | 0.159 | -0.0065667 | -0.061167 | 0.021629 | -0.014037 | -0.0075067 | -0.0041933 | 0.15182 | 0.02305 | 0.022616 | 0.022559 | 0.015302 | 0.01643 | 0.09613 | 0.086975 | 0.13733 | 0.073242 | -0.09613 | 0.12817 | 0.018311 | 0.12817 | 0.1236 | 0.036621 | -0.07782 | -0.073242 | 0.10071 | 0.050354 | 122.58 | 122.4701 | -0.10986 | 122.5388 | 122.525 | 0.054931 | 0.082397 | 122.5525 | 122.5021 | -0.091553 | 122.58 | 122.4884 | -0.013733 | -0.086975 | 122.3557 | 122.5479 | 122.5891 | 0.004578 | 122.374 | 122.3785 | 122.5754 | 0.036621
2028.2188 | 122.7676 | -122.4609 | 0.004578 | -0.016479 | -0.0042169 | -0.05839 | 0.020775 | -0.011901 | -0.01007 | -0.0082523 | 0.014496 | 0.020059 | 0.025393 | 0.020209 | 0.013593 | 0.016643 | 0.050354 | 0.045776 | 0.11444 | 0.054932 | -0.064087 | 0.11444 | 0.004578 | 0.10529 | 0.14191 | 0.036621 | -0.068665 | -0.050354 | 0.10071 | 0.032043 | 122.5754 | 122.4655 | -0.068665 | 122.5067 | 122.5159 | 0.050354 | 0.045776 | 122.5616 | 122.493 | -0.073243 | 122.5662 | 122.4976 | 0.004578 | -0.054932 | 122.3969 | 122.5113 | 122.5754 | 0 | 122.3923 | 122.4106 | 122.6028 | 0.027465
2029.9531 | 122.7356 | -122.4472 | 0.004578 | 0.11322 | -0.0029351 | -0.059885 | 0.018852 | -0.013183 | -0.0010981 | -0.0063297 | 0.08316 | 0.024545 | 0.022403 | 0.02149 | 0.01872 | 0.017071 | 0.022888 | -0.054932 | 0.009155 | 0.004578 | -0.050354 | 0.10529 | -0.036621 | 0.032043 | 0 | -0.073242 | -0.059509 | -0.041199 | 0.073242 | 0.013733 | 122.5525 | 122.4106 | -0.054932 | 122.3923 | 122.4518 | 0.041199 | 0.01831 | 122.5204 | 122.4609 | -0.064087 | 122.4792 | 122.374 | -0.086975 | -0.045777 | 122.3969 | 122.4701 | 122.4564 | -0.041199 | 122.3877 | 122.406 | 122.4472 | 0.009155
2031.6406 | 122.7036 | -122.4838 | 0.036621 | 0.052185 | -0.0035761 | -0.06074 | 0.026543 | -0.015319 | -0.0083613 | -0.0048343 | 0.098419 | 0.022836 | 0.023044 | 0.019568 | 0.012952 | 0.015575 | 0.068665 | 0.027466 | 0.10071 | 0.041199 | -0.091553 | 0.1236 | 0.004578 | 0.086975 | 0.07782 | 0.004578 | -0.07782 | -0.054932 | 0.086975 | 0.032043 | 122.6074 | 122.4884 | -0.12817 | 122.5113 | 122.525 | 0.036621 | 0.032044 | 122.5708 | 122.5159 | -0.11444 | 122.5708 | 122.4884 | -0.027465 | -0.091553 | 122.3923 | 122.5525 | 122.5845 | -0.032043 | 122.406 | 122.4289 | 122.5616 | -0.004578
2033.3594 | 122.6944 | -122.4335 | 0.022888 | 0.11322 | -0.0063531 | -0.062448 | 0.021629 | -0.012755 | -0.0047297 | -0.0069705 | 0.098419 | 0.021982 | 0.024966 | 0.024268 | 0.013806 | 0.015148 | 0.07782 | 0.045776 | 0.11902 | 0.041199 | -0.082397 | 0.13275 | 0.013733 | 0.09613 | 0.086975 | 0.004578 | -0.082397 | -0.064087 | 0.10071 | 0.018311 | 122.5662 | 122.4472 | -0.10528 | 122.4792 | 122.4747 | 0.027466 | 0.054932 | 122.5342 | 122.4518 | -0.10528 | 122.5296 | 122.438 | -0.013733 | -0.086975 | 122.3511 | 122.5113 | 122.5525 | -0.009155 | 122.3511 | 122.3694 | 122.5204 | -0.004577
2035.0469 | 122.644 | -122.4792 | 0.013733 | 0.082703 | -0.00037168 | -0.062876 | 0.020775 | -0.015746 | 0.00018372 | -0.0061161 | 0.014496 | 0.022409 | 0.023684 | 0.022131 | 0.018079 | 0.01173 | 0.004578 | -0.091553 | -0.018311 | -0.004578 | -0.041199 | 0.07782 | -0.027466 | -0.009155 | -0.041199 | -0.15564 | -0.045776 | -0.018311 | 0.059509 | 0.013733 | 122.5571 | 122.4518 | -0.054932 | 122.3877 | 122.4747 | 0.022888 | -0.009155 | 122.5388 | 122.493 | -0.059509 | 122.4701 | 122.3236 | -0.16937 | -0.032044 | 122.438 | 122.4838 | 122.4609 | -0.041199 | 122.4335 | 122.4609 | 122.438 | 0
2036.7188 | 122.731 | -122.4472 | 0.004578 | -0.1004 | -0.0033625 | -0.059885 | 0.023338 | -0.013824 | -0.0064387 | -0.0069705 | -0.084686 | 0.019418 | 0.022616 | 0.021704 | 0.013166 | 0.01408 | 0.10071 | 0.11444 | 0.16479 | 0.091553 | -0.082397 | 0.10986 | 0.004578 | 0.13733 | 0.1831 | 0.054932 | -0.082397 | -0.045776 | 0.09613 | 0.041199 | 122.5571 | 122.4518 | -0.086975 | 122.5616 | 122.5388 | 0.086975 | 0.09613 | 122.5433 | 122.4884 | -0.086975 | 122.5845 | 122.5021 | 0.013733 | -0.050354 | 122.3648 | 122.5479 | 122.612 | 0 | 122.3648 | 122.4014 | 122.6303 | 0.036621
2038.4688 | 122.7585 | -122.4701 | 0.009155 | 0.044556 | -0.0059259 | -0.059031 | 0.01992 | -0.015533 | -0.0036615 | -0.0063297 | 0.029755 | 0.019846 | 0.023684 | 0.021704 | 0.014661 | 0.013653 | 0.032043 | 0.022888 | 0.07782 | 0.050354 | -0.054932 | 0.11902 | -0.009155 | 0.086975 | 0.07782 | 0 | -0.054932 | -0.059509 | 0.091553 | 0.027466 | 122.5891 | 122.4609 | -0.064087 | 122.493 | 122.5204 | 0.059509 | 0.022888 | 122.5616 | 122.4976 | -0.064087 | 122.5571 | 122.4701 | -0.027466 | -0.068664 | 122.4152 | 122.5021 | 122.5479 | -0.01831 | 122.4152 | 122.4106 | 122.5479 | 0.018311
2040.25 | 122.7402 | -122.4564 | 0.013733 | -0.092773 | -0.0027215 | -0.061808 | 0.023338 | -0.014037 | -0.0057977 | -0.0076113 | -0.10757 | 0.020273 | 0.024325 | 0.020636 | 0.011884 | 0.013866 | 0.11902 | 0.11444 | 0.16937 | 0.086975 | -0.082397 | 0.10071 | 0.013733 | 0.15106 | 0.16479 | 0.045776 | -0.086975 | -0.068665 | 0.07782 | 0.027466 | 122.5571 | 122.4701 | -0.09613 | 122.5708 | 122.5433 | 0.073242 | 0.10529 | 122.5342 | 122.4838 | -0.10071 | 122.6074 | 122.5021 | 0.01831 | -0.082398 | 122.374 | 122.5754 | 122.6257 | 0 | 122.3694 | 122.3877 | 122.6212 | 0.013733
2041.9531 | 122.6761 | -122.4838 | 0.022888 | -0.11566 | -0.0012263 | -0.062235 | 0.01928 | -0.009551 | 0.00082452 | -0.0073977 | -0.15335 | 0.021768 | 0.02283 | 0.02384 | 0.018933 | 0.010876 | 0.050354 | 0.004578 | 0.036621 | 0.041199 | -0.041199 | 0.082397 | -0.036621 | 0.059509 | 0.054932 | -0.064087 | -0.032043 | -0.032043 | 0.073242 | 0.018311 | 122.5662 | 122.4472 | -0.064087 | 122.4884 | 122.525 | 0.07782 | 0.027466 | 122.5571 | 122.5021 | -0.054931 | 122.5433 | 122.4197 | -0.082398 | -0.054931 | 122.4426 | 122.5342 | 122.5204 | -0.059509 | 122.4518 | 122.4518 | 122.5388 | -0.004577
2043.7031 | 122.6166 | -122.5159 | 0.027466 | 0.067444 | -0.0018671 | -0.06074 | 0.020134 | -0.014892 | 0.0014655 | -0.0056887 | -0.00076274 | 0.021341 | 0.022616 | 0.023199 | 0.019361 | 0.016643 | 0.018311 | -0.036621 | 0.013733 | 0.018311 | -0.045776 | 0.086975 | -0.018311 | 0.009155 | -0.004578 | -0.11444 | -0.050354 | -0.027466 | 0.064087 | 0.004578 | 122.6028 | 122.4976 | -0.073242 | 122.4792 | 122.5342 | 0.036622 | -0.009155 | 122.58 | 122.5204 | -0.07782 | 122.525 | 122.4014 | -0.11902 | -0.054932 | 122.4701 | 122.5342 | 122.5296 | -0.045777 | 122.4655 | 122.4884 | 122.5113 | -0.022888
2045.4531 | 122.6944 | -122.4701 | -0.009155 | 0.11322 | -0.0067805 | -0.059671 | 0.021416 | -0.014892 | -0.0072931 | -0.0054751 | 0.1442 | 0.01835 | 0.023684 | 0.022131 | 0.013166 | 0.01643 | 0.07782 | 0.091553 | 0.13733 | 0.068665 | -0.09613 | 0.13275 | 0.013733 | 0.13275 | 0.10986 | 0.013733 | -0.086975 | -0.054932 | 0.10986 | 0.045776 | 122.6028 | 122.4838 | -0.086975 | 122.5616 | 122.5388 | 0.054932 | 0.086975 | 122.58 | 122.5159 | -0.07782 | 122.6028 | 122.4838 | -0.032043 | -0.045777 | 122.374 | 122.5479 | 122.6074 | 0.022888 | 122.3831 | 122.4152 | 122.58 | 0.054931
2047.1406 | 122.7493 | -122.4655 | 0.013733 | -0.0012209 | -0.0074213 | -0.05604 | 0.021843 | -0.014892 | -0.0060113 | -0.0063297 | 0.045013 | 0.017709 | 0.021548 | 0.021063 | 0.014234 | 0.016216 | 0.013733 | 0.022888 | 0.082397 | 0.041199 | -0.059509 | 0.10529 | 0 | 0.086975 | 0.10071 | 0.009155 | -0.07782 | -0.054932 | 0.10529 | 0.022888 | 122.5708 | 122.4655 | -0.073242 | 122.4884 | 122.5067 | 0.041199 | 0 | 122.5708 | 122.4884 | -0.091553 | 122.5525 | 122.4747 | -0.013733 | -0.068665 | 122.406 | 122.4792 | 122.5479 | -0.013733 | 122.3877 | 122.4106 | 122.5662 | 0.009155
2048.875 | 122.6212 | -122.5204 | 0.027466 | -0.15381 | -0.0025079 | -0.06074 | 0.025261 | -0.011901 | -0.0045161 | -0.0061161 | -0.13809 | 0.020486 | 0.024112 | 0.022131 | 0.011457 | 0.014934 | 0.086975 | 0.091553 | 0.15564 | 0.07782 | -0.09613 | 0.10529 | -0.013733 | 0.10529 | 0.14191 | 0.013733 | -0.064087 | -0.054932 | 0.10986 | 0.027466 | 122.6257 | 122.5067 | -0.1236 | 122.612 | 122.5983 | 0.091553 | 0.059509 | 122.6303 | 122.5479 | -0.091553 | 122.6257 | 122.5342 | -0.013733 | -0.082398 | 122.4243 | 122.6074 | 122.6761 | -0.041199 | 122.4564 | 122.4655 | 122.6624 | 0
2050.625 | 122.6578 | -122.4701 | 0.013733 | 0.097962 | -0.0029351 | -0.060099 | 0.017998 | -0.016387 | -0.0025935 | -0.0046207 | 0.052643 | 0.020914 | 0.023471 | 0.023627 | 0.01872 | 0.013012 | 0.013733 | -0.045776 | -0.018311 | 0 | -0.022888 | 0.073242 | -0.032043 | 0.027466 | -0.018311 | -0.10529 | -0.045776 | -0.022888 | 0.064087 | -0.013733 | 122.5433 | 122.4381 | -0.036621 | 122.4243 | 122.4701 | 0.032043 | 0 | 122.5342 | 122.4564 | -0.059509 | 122.4976 | 122.3648 | -0.091553 | -0.036621 | 122.4472 | 122.4838 | 122.4518 | -0.045776 | 122.4243 | 122.4472 | 122.4518 | -0.027466
2052.375 | 122.6166 | -122.525 | 0.032043 | -0.19958 | -0.0012263 | -0.06074 | 0.024193 | -0.01361 | -0.0034479 | -0.0067569 | -0.077057 | 0.020486 | 0.024966 | 0.021704 | 0.014234 | 0.014294 | 0.018311 | 0.013733 | 0.054932 | 0.018311 | -0.050354 | 0.082397 | -0.027466 | 0.041199 | 0.050354 | -0.064087 | -0.027466 | -0.027466 | 0.059509 | 0 | 122.6074 | 122.4976 | -0.082397 | 122.5388 | 122.5433 | 0.045777 | -0.013732 | 122.5845 | 122.525 | -0.059509 | 122.5662 | 122.4609 | -0.064087 | -0.059509 | 122.4747 | 122.5433 | 122.58 | -0.059509 | 122.4976 | 122.4976 | 122.5754 | -0.032043
2054.0469 | 122.6166 | -122.5067 | 0.036621 | -0.016479 | -0.0010125 | -0.06074 | 0.017571 | -0.012755 | 0.0018927 | -0.0029117 | -0.03891 | 0.024332 | 0.024539 | 0.024481 | 0.019147 | 0.012798 | 0.032043 | 0 | 0.027466 | 0.009155 | -0.036621 | 0.07782 | -0.036621 | 0.022888 | 0.018311 | -0.11444 | -0.064087 | -0.032043 | 0.07782 | 0 | 122.5845 | 122.4701 | -0.073242 | 122.5067 | 122.5159 | 0.045776 | -0.004578 | 122.5845 | 122.5067 | -0.10071 | 122.5296 | 122.3923 | -0.11444 | -0.068664 | 122.4701 | 122.5388 | 122.5342 | -0.073242 | 122.4426 | 122.4747 | 122.525 | -0.036621
2055.7812 | 122.6212 | -122.5113 | 0.041199 | 0.029297 | -0.0025079 | -0.06138 | 0.019707 | -0.015105 | -0.0015253 | -0.0035525 | 0.029755 | 0.023264 | 0.025393 | 0.022986 | 0.017011 | 0.01408 | 0.013733 | -0.036621 | 0.013733 | 0.018311 | -0.045776 | 0.086975 | -0.013733 | 0.004578 | 0 | -0.11902 | -0.050354 | -0.013733 | 0.07782 | -0.022888 | 122.5983 | 122.4976 | -0.086975 | 122.4747 | 122.5296 | 0.032044 | -0.027466 | 122.5891 | 122.4884 | -0.091553 | 122.5159 | 122.3923 | -0.096131 | -0.054932 | 122.4655 | 122.525 | 122.525 | -0.054932 | 122.4609 | 122.4976 | 122.5113 | -0.064087
2057.5312 | 122.6852 | -122.4564 | 0.009155 | 0.12085 | -0.0027215 | -0.060312 | 0.018211 | -0.012755 | -0.0013117 | -0.0041933 | 0.098419 | 0.024332 | 0.025821 | 0.024268 | 0.017224 | 0.014934 | 0 | -0.064087 | -0.004578 | -0.004578 | -0.045776 | 0.086975 | -0.041199 | 0.027466 | -0.004578 | -0.086975 | -0.041199 | -0.032043 | 0.064087 | 0.004578 | 122.5433 | 122.4152 | -0.054931 | 122.3923 | 122.4518 | 0.036621 | -0.009155 | 122.5204 | 122.4609 | -0.050354 | 122.4838 | 122.3694 | -0.091553 | -0.041198 | 122.4106 | 122.4564 | 122.4518 | -0.050354 | 122.4152 | 122.4243 | 122.4518 | -0.004577
2059.2188 | 122.6898 | -122.4701 | 0.027466 | -0.1767 | -0.0029351 | -0.060312 | 0.026115 | -0.013183 | -0.0096429 | -0.0061161 | -0.10757 | 0.024759 | 0.023684 | 0.02149 | 0.012097 | 0.016857 | 0.07782 | 0.10529 | 0.14648 | 0.086975 | -0.082397 | 0.11444 | 0.004578 | 0.11444 | 0.17853 | 0.032043 | -0.10986 | -0.068665 | 0.10071 | 0.045776 | 122.5845 | 122.4747 | -0.10986 | 122.5754 | 122.5571 | 0.082397 | 0.050354 | 122.5708 | 122.5159 | -0.13733 | 122.5845 | 122.5021 | -0.013733 | -0.096131 | 122.3877 | 122.5479 | 122.6166 | -0.022888 | 122.3602 | 122.4014 | 122.6486 | 0.01831
2060.9688 | 122.612 | -122.5021 | 0.022888 | -0.046997 | -0.00058528 | -0.059885 | 0.020348 | -0.012542 | -0.00088448 | -0.0054751 | -0.03891 | 0.0254 | 0.026675 | 0.023413 | 0.017865 | 0.012371 | 0.041199 | 0 | 0.045776 | 0.027466 | -0.054932 | 0.07782 | -0.027466 | 0.032043 | 0.032043 | -0.073242 | -0.045776 | -0.027466 | 0.073242 | 0.004578 | 122.58 | 122.4747 | -0.07782 | 122.5021 | 122.5296 | 0.054932 | 0.018311 | 122.5754 | 122.5067 | -0.068664 | 122.5342 | 122.4289 | -0.07782 | -0.050354 | 122.4472 | 122.5433 | 122.5479 | -0.050354 | 122.4564 | 122.4747 | 122.5342 | -0.01831
2062.7188 | 122.644 | -122.5021 | 0.045776 | -0.13092 | -0.0022943 | -0.060312 | 0.024193 | -0.011901 | -0.0047297 | -0.0069705 | -0.16861 | 0.022623 | 0.026889 | 0.024908 | 0.013593 | 0.015362 | -0.004578 | -0.036621 | 0.022888 | -0.013733 | -0.027466 | 0.068665 | -0.045776 | 0 | 0.027466 | -0.07782 | -0.041199 | -0.013733 | 0.073242 | -0.004578 | 122.5708 | 122.4564 | -0.073242 | 122.4655 | 122.4884 | 0.032043 | -0.050354 | 122.5754 | 122.4976 | -0.086975 | 122.5021 | 122.4243 | -0.073242 | -0.059509 | 122.4747 | 122.4976 | 122.525 | -0.091552 | 122.4609 | 122.4884 | 122.5296 | -0.050354
2064.4688 | 122.6166 | -122.4976 | 0.036621 | -0.069885 | 0.0032599 | -0.062448 | 0.025047 | -0.014678 | -0.00067088 | -0.0035525 | -0.046539 | 0.023477 | 0.027316 | 0.023627 | 0.015302 | 0.014721 | 0.059509 | -0.013733 | 0.054932 | 0.036621 | -0.045776 | 0.10529 | -0.022888 | 0.036621 | 0.050354 | -0.073242 | -0.041199 | -0.041199 | 0.064087 | 0.013733 | 122.6028 | 122.4747 | -0.082397 | 122.4838 | 122.5342 | 0.059509 | 0.022888 | 122.5616 | 122.5113 | -0.07782 | 122.5342 | 122.4243 | -0.086975 | -0.07782 | 122.4518 | 122.5571 | 122.5525 | -0.059509 | 122.4564 | 122.4564 | 122.5479 | -0.022888
2066.1406 | 122.7631 | -122.4609 | 0.009155 | -0.024109 | -0.0059259 | -0.06074 | 0.021629 | -0.014251 | -0.0085749 | -0.0073977 | -0.046539 | 0.022623 | 0.023898 | 0.022131 | 0.012525 | 0.016003 | 0.045776 | 0.068665 | 0.10986 | 0.068665 | -0.059509 | 0.10986 | 0.027466 | 0.12817 | 0.16022 | 0.059509 | -0.059509 | -0.050354 | 0.10529 | 0.036621 | 122.5708 | 122.4884 | -0.068664 | 122.5296 | 122.5296 | 0.041199 | 0.036621 | 122.5662 | 122.4976 | -0.068664 | 122.5891 | 122.5204 | 0.022888 | -0.059509 | 122.4014 | 122.5067 | 122.5708 | 0.018311 | 122.4014 | 122.4106 | 122.6212 | 0.027466
2067.875 | 122.6395 | -122.5021 | 0.041199 | -0.21484 | -0.00037168 | -0.059671 | 0.020561 | -0.013396 | -0.0040887 | -0.0059023 | -0.18387 | 0.020486 | 0.024966 | 0.021704 | 0.014447 | 0.013225 | 0.045776 | 0.050354 | 0.091553 | 0.059509 | -0.068665 | 0.10071 | -0.009155 | 0.041199 | 0.068665 | -0.050354 | -0.041199 | -0.036621 | 0.064087 | 0.013733 | 122.6028 | 122.493 | -0.10986 | 122.5525 | 122.5616 | 0.068664 | 0.004577 | 122.5662 | 122.5159 | -0.082398 | 122.5433 | 122.4518 | -0.064087 | -0.07782 | 122.4335 | 122.5479 | 122.5937 | -0.050354 | 122.4609 | 122.4655 | 122.5708 | -0.027466
2069.625 | 122.6349 | -122.5159 | 0.032043 | 0.052185 | -0.00015808 | -0.059885 | 0.016502 | -0.011046 | 0.0012519 | -0.0050479 | 0.060272 | 0.022195 | 0.026034 | 0.022772 | 0.018293 | 0.015148 | -0.013733 | -0.07782 | -0.022888 | -0.004578 | -0.022888 | 0.068665 | -0.027466 | 0.013733 | -0.022888 | -0.10071 | -0.036621 | -0.022888 | 0.07782 | 0 | 122.5845 | 122.4884 | -0.054931 | 122.438 | 122.5113 | 0.022888 | -0.045776 | 122.5937 | 122.5159 | -0.068664 | 122.5296 | 122.4152 | -0.10071 | -0.054931 | 122.493 | 122.5021 | 122.493 | -0.059509 | 122.4792 | 122.493 | 122.493 | -0.032043
2071.3125 | 122.6761 | -122.4701 | 0.032043 | -0.092773 | -0.00079888 | -0.059885 | 0.022911 | -0.012328 | 0.00018372 | -0.0061161 | -0.13046 | 0.024545 | 0.025393 | 0.022772 | 0.016156 | 0.011516 | 0.045776 | -0.009155 | 0.045776 | 0.050354 | -0.032043 | 0.082397 | -0.032043 | 0.064087 | 0.068665 | -0.050354 | -0.050354 | -0.032043 | 0.059509 | 0 | 122.5525 | 122.4381 | -0.064086 | 122.4609 | 122.5204 | 0.082397 | 0.013733 | 122.5296 | 122.4701 | -0.082397 | 122.5342 | 122.4197 | -0.050354 | -0.064086 | 122.4381 | 122.5159 | 122.5159 | -0.064086 | 122.4197 | 122.4381 | 122.5388 | -0.032043
2073.125 | 122.7173 | -122.4472 | -0.013733 | 0.159 | -0.0027215 | -0.06074 | 0.020775 | -0.010619 | -0.0019525 | -0.0033389 | 0.1976 | 0.020486 | 0.023684 | 0.022772 | 0.014875 | 0.015148 | 0.082397 | 0.073242 | 0.14191 | 0.086975 | -0.07782 | 0.1236 | 0.022888 | 0.13733 | 0.14191 | 0.045776 | -0.07782 | -0.064087 | 0.11444 | 0.036621 | 122.5708 | 122.4701 | -0.064087 | 122.5204 | 122.5342 | 0.064087 | 0.09613 | 122.5616 | 122.4838 | -0.064087 | 122.5845 | 122.493 | 0.009155 | -0.050354 | 122.3694 | 122.5296 | 122.5891 | 0.036621 | 122.3694 | 122.3831 | 122.5891 | 0.050354
2074.8281 | 122.7859 | -122.4792 | 0.013733 | 0.021668 | -0.0057123 | -0.059885 | 0.023338 | -0.011901 | -0.0077203 | -0.0084659 | 0.060272 | 0.021982 | 0.022189 | 0.02149 | 0.012097 | 0.015148 | 0.018311 | 0.027466 | 0.07782 | 0.050354 | -0.073242 | 0.09613 | 0 | 0.091553 | 0.10529 | 0.004578 | -0.07782 | -0.054932 | 0.10986 | 0.032043 | 122.5754 | 122.4792 | -0.086975 | 122.5067 | 122.5296 | 0.050354 | 0.004578 | 122.5891 | 122.5113 | -0.091553 | 122.5708 | 122.4838 | -0.027465 | -0.068665 | 122.406 | 122.4976 | 122.5571 | -0.013733 | 122.4014 | 122.4243 | 122.5845 | 0.01831
2076.5469 | 122.6486 | -122.5021 | 0.032043 | 0.036926 | -0.0014399 | -0.061594 | 0.016289 | -0.014251 | 0.0016791 | -0.0065433 | -0.016022 | 0.021341 | 0.025393 | 0.025549 | 0.017011 | 0.013012 | 0.013733 | -0.059509 | 0.009155 | 0.018311 | -0.036621 | 0.082397 | -0.018311 | -0.009155 | -0.022888 | -0.10986 | -0.032043 | -0.009155 | 0.054932 | -0.009155 | 122.5845 | 122.4838 | -0.068664 | 122.4426 | 122.5204 | 0.036622 | -0.01831 | 122.5571 | 122.493 | -0.064086 | 122.493 | 122.3923 | -0.10071 | -0.041198 | 122.4655 | 122.5159 | 122.5113 | -0.050354 | 122.4701 | 122.493 | 122.4792 | -0.041198
2078.2344 | 122.7676 | -122.4518 | 0 | 0.159 | -0.0050715 | -0.059885 | 0.01992 | -0.015319 | -0.00067088 | -0.0029117 | 0.11368 | 0.019632 | 0.022616 | 0.023413 | 0.020215 | 0.015148 | 0.045776 | 0.022888 | 0.073242 | 0.041199 | -0.054932 | 0.1236 | -0.032043 | 0.10986 | 0.086975 | 0.013733 | -0.10071 | -0.054932 | 0.086975 | 0.036621 | 122.5754 | 122.4197 | -0.054932 | 122.4747 | 122.493 | 0.073242 | 0.045776 | 122.5388 | 122.4884 | -0.10071 | 122.5616 | 122.4655 | -0.022888 | -0.054932 | 122.3969 | 122.4976 | 122.525 | -0.032043 | 122.3511 | 122.3969 | 122.5388 | 0.036621
2079.9062 | 122.7493 | -122.4564 | 0.013733 | 0.029297 | -0.0037897 | -0.059671 | 0.020348 | -0.012969 | -0.0092157 | -0.0067569 | 0.098419 | 0.019846 | 0.024539 | 0.022131 | 0.012311 | 0.015789 | 0.027466 | 0.041199 | 0.091553 | 0.041199 | -0.082397 | 0.09613 | -0.004578 | 0.073242 | 0.068665 | 0.009155 | -0.064087 | -0.054932 | 0.091553 | 0.027466 | 122.5525 | 122.4518 | -0.09613 | 122.4976 | 122.4976 | 0.045777 | 0.013733 | 122.5479 | 122.4838 | -0.07782 | 122.5296 | 122.4655 | -0.018311 | -0.068665 | 122.374 | 122.4838 | 122.5479 | -0.018311 | 122.3923 | 122.4014 | 122.525 | 0.013733
2081.5938 | 122.6807 | -122.493 | 0 | -0.1004 | -0.0020807 | -0.061167 | 0.01992 | -0.012542 | 0.00039732 | -0.0063297 | -0.12283 | 0.0254 | 0.026462 | 0.021277 | 0.017011 | 0.012798 | 0.045776 | 0.004578 | 0.050354 | 0.036621 | -0.041199 | 0.068665 | -0.032043 | 0.064087 | 0.064087 | -0.041199 | -0.027466 | -0.032043 | 0.073242 | 0.018311 | 122.5616 | 122.4609 | -0.041199 | 122.4976 | 122.5296 | 0.068664 | 0.045776 | 122.5662 | 122.5113 | -0.027466 | 122.5571 | 122.4518 | -0.05951 | -0.032043 | 122.4518 | 122.5388 | 122.5433 | -0.032043 | 122.4655 | 122.4609 | 122.5571 | 0.018311
2083.2812 | 122.7036 | -122.4838 | 0.018311 | -0.11566 | -0.0042169 | -0.06074 | 0.020775 | -0.013396 | -0.00067088 | -0.0029117 | -0.10757 | 0.023691 | 0.026034 | 0.021918 | 0.01637 | 0.01408 | 0.036621 | 0.009155 | 0.041199 | 0.022888 | -0.050354 | 0.064087 | -0.018311 | 0.050354 | 0.064087 | -0.050354 | -0.045776 | -0.045776 | 0.068665 | -0.004578 | 122.5479 | 122.4655 | -0.068665 | 122.493 | 122.5067 | 0.041199 | 0.01831 | 122.5525 | 122.4792 | -0.064087 | 122.5342 | 122.4335 | -0.045776 | -0.064087 | 122.4335 | 122.5204 | 122.525 | -0.036622 | 122.438 | 122.438 | 122.5479 | -0.022889
2085 | 122.6807 | -122.4976 | 0.009155 | 0.11322 | -0.0040033 | -0.060099 | 0.020348 | -0.014464 | -0.00088448 | -0.0061161 | 0.10605 | 0.024973 | 0.026248 | 0.023413 | 0.017438 | 0.014721 | -0.027466 | -0.073242 | -0.009155 | -0.013733 | -0.022888 | 0.07782 | -0.036621 | 0.018311 | -0.022888 | -0.10529 | -0.032043 | -0.022888 | 0.068665 | 0.013733 | 122.5754 | 122.4609 | -0.032043 | 122.4243 | 122.4838 | 0.022888 | -0.036621 | 122.5662 | 122.5113 | -0.041198 | 122.5159 | 122.3923 | -0.11902 | -0.032043 | 122.4747 | 122.4701 | 122.4884 | -0.045776 | 122.4655 | 122.4747 | 122.4747 | 0.004578
2086.7031 | 122.7768 | -122.4472 | -0.004578 | 0.12085 | -0.0022943 | -0.059671 | 0.016502 | -0.011046 | -0.0047297 | -0.0054751 | 0.18234 | 0.023264 | 0.026034 | 0.021918 | 0.016584 | 0.014507 | 0.027466 | -0.027466 | 0.041199 | 0.009155 | -0.050354 | 0.091553 | -0.022888 | 0.064087 | 0.050354 | -0.027466 | -0.073242 | -0.059509 | 0.10071 | 0.027466 | 122.5388 | 122.4243 | -0.045776 | 122.4197 | 122.4564 | 0.032043 | 0.032044 | 122.5479 | 122.4747 | -0.068664 | 122.5113 | 122.4197 | -0.054932 | -0.054931 | 122.3969 | 122.4747 | 122.4884 | -0.01831 | 122.374 | 122.3877 | 122.4976 | 0.032044
2088.4531 | 122.6807 | -122.5113 | 0.018311 | -0.10803 | -0.0020807 | -0.06138 | 0.01992 | -0.013183 | -0.00067088 | -0.0050479 | -0.092316 | 0.023264 | 0.025821 | 0.022772 | 0.017011 | 0.015575 | 0.041199 | 0.013733 | 0.050354 | 0.041199 | -0.041199 | 0.073242 | -0.009155 | 0.064087 | 0.07782 | -0.041199 | -0.054932 | -0.036621 | 0.086975 | 0.022888 | 122.5845 | 122.5021 | -0.05951 | 122.525 | 122.5525 | 0.050354 | 0.022888 | 122.5983 | 122.5342 | -0.073243 | 122.5754 | 122.4701 | -0.064087 | -0.054932 | 122.4701 | 122.5525 | 122.5616 | -0.027466 | 122.4564 | 122.4747 | 122.5891 | 0.004577
2090.1562 | 122.7493 | -122.4976 | -0.013733 | 0.15137 | -0.0022943 | -0.060953 | 0.020561 | -0.012755 | -0.0068659 | -0.0026981 | 0.1976 | 0.023904 | 0.02518 | 0.019781 | 0.013593 | 0.014507 | 0.082397 | 0.086975 | 0.15564 | 0.086975 | -0.082397 | 0.11444 | 0.013733 | 0.1236 | 0.12817 | 0.045776 | -0.091553 | -0.073242 | 0.09613 | 0.041199 | 122.612 | 122.5113 | -0.068664 | 122.5845 | 122.5845 | 0.073242 | 0.09613 | 122.5937 | 122.5388 | -0.07782 | 122.6212 | 122.5433 | 0.004577 | -0.059509 | 122.4152 | 122.58 | 122.6532 | 0.027466 | 122.406 | 122.4243 | 122.6257 | 0.054932
2091.8594 | 122.7539 | -122.4792 | 0.022888 | 0.029297 | -0.0052851 | -0.058817 | 0.02227 | -0.01361 | -0.0079339 | -0.0073977 | 0.09079 | 0.021982 | 0.02753 | 0.023413 | 0.012952 | 0.014721 | 0.027466 | 0.032043 | 0.082397 | 0.041199 | -0.07782 | 0.10986 | 0.013733 | 0.059509 | 0.059509 | -0.009155 | -0.073242 | -0.068665 | 0.082397 | 0.036621 | 122.5891 | 122.493 | -0.10071 | 122.5113 | 122.5204 | 0.027466 | 0.004578 | 122.5616 | 122.5159 | -0.09613 | 122.5388 | 122.4701 | -0.045776 | -0.091553 | 122.4014 | 122.5067 | 122.5616 | -0.009155 | 122.406 | 122.4106 | 122.5388 | 0.013733
2093.5625 | 122.7859 | -122.4655 | 0.009155 | -0.085144 | -0.0044305 | -0.06074 | 0.024406 | -0.011687 | -0.0068659 | -0.0056887 | -0.092316 | 0.019205 | 0.02518 | 0.022772 | 0.011243 | 0.013439 | 0.11902 | 0.11444 | 0.16022 | 0.082397 | -0.068665 | 0.12817 | 0.009155 | 0.1236 | 0.16479 | 0.050354 | -0.064087 | -0.064087 | 0.10986 | 0.036621 | 122.5937 | 122.4747 | -0.07782 | 122.58 | 122.5479 | 0.073242 | 0.10986 | 122.5754 | 122.5021 | -0.073242 | 122.5891 | 122.5159 | 0.013733 | -0.073242 | 122.3969 | 122.5845 | 122.6257 | 0 | 122.4014 | 122.4014 | 122.6303 | 0.027466
2095.25 | 122.699 | -122.5113 | 0.032043 | -0.16907 | -0.0029351 | -0.059244 | 0.022484 | -0.010192 | 0.00039732 | -0.0078249 | -0.13809 | 0.024545 | 0.024753 | 0.023199 | 0.015729 | 0.012585 | 0.018311 | -0.059509 | 0.013733 | 0.027466 | -0.027466 | 0.068665 | -0.050354 | 0.009155 | 0.032043 | -0.091553 | -0.036621 | -0.036621 | 0.059509 | -0.009155 | 122.58 | 122.4609 | -0.059509 | 122.4518 | 122.5388 | 0.07782 | -0.013732 | 122.5708 | 122.5021 | -0.068664 | 122.5204 | 122.4197 | -0.082398 | -0.068664 | 122.4838 | 122.5296 | 122.525 | -0.082397 | 122.4747 | 122.4747 | 122.5433 | -0.041198
2096.9375 | 122.7722 | -122.4655 | 0 | 0.18951 | -0.0025079 | -0.059244 | 0.01928 | -0.014037 | -0.0025935 | -0.0071841 | 0.13657 | 0.022195 | 0.024753 | 0.022986 | 0.016156 | 0.014721 | 0.09613 | 0.064087 | 0.1236 | 0.082397 | -0.068665 | 0.11444 | 0 | 0.13275 | 0.1236 | 0.032043 | -0.091553 | -0.07782 | 0.11902 | 0.045776 | 122.58 | 122.4655 | -0.068665 | 122.5296 | 122.5479 | 0.082397 | 0.09613 | 122.5845 | 122.5113 | -0.091553 | 122.5983 | 122.4976 | -0.013733 | -0.07782 | 122.3969 | 122.5616 | 122.5891 | 0 | 122.374 | 122.3877 | 122.5891 | 0.045776
2098.625 | 122.7493 | -122.4609 | -0.009155 | 0.13611 | -0.0050715 | -0.059885 | 0.019493 | -0.015105 | -0.0032343 | -0.0061161 | 0.15945 | 0.022836 | 0.023044 | 0.024268 | 0.016156 | 0.012585 | 0.10529 | 0.091553 | 0.11444 | 0.07782 | -0.086975 | 0.11444 | 0.004578 | 0.14648 | 0.11444 | 0.041199 | -0.091553 | -0.082397 | 0.10986 | 0.050354 | 122.5754 | 122.4655 | -0.07782 | 122.5525 | 122.5388 | 0.073242 | 0.11444 | 122.5708 | 122.5113 | -0.082398 | 122.6074 | 122.5021 | -0.009155 | -0.073242 | 122.374 | 122.5662 | 122.5754 | 0.013733 | 122.3694 | 122.3785 | 122.5754 | 0.059509
2100.2969 | 122.7081 | -122.493 | 0.036621 | -0.16144 | -0.0046441 | -0.059031 | 0.022484 | -0.012328 | -0.0045161 | -0.0050479 | -0.092316 | 0.021341 | 0.024325 | 0.022131 | 0.012097 | 0.013866 | 0.10071 | 0.10071 | 0.13733 | 0.082397 | -0.07782 | 0.09613 | 0.009155 | 0.11902 | 0.16022 | 0.041199 | -0.086975 | -0.045776 | 0.10071 | 0.022888 | 122.5891 | 122.5021 | -0.11444 | 122.5937 | 122.5754 | 0.073242 | 0.064087 | 122.5937 | 122.5159 | -0.1236 | 122.612 | 122.5342 | 0.018311 | -0.082397 | 122.4152 | 122.5937 | 122.6303 | -0.027466 | 122.406 | 122.4472 | 122.6532 | -0.013733
2102.0156 | 122.7448 | -122.4884 | 0.004578 | 0.052185 | -0.0054987 | -0.059031 | 0.020775 | -0.012328 | -0.0068659 | -0.0046207 | 0.10605 | 0.020059 | 0.023044 | 0.022986 | 0.012738 | 0.014721 | 0.073242 | 0.032043 | 0.10071 | 0.045776 | -0.068665 | 0.11444 | 0.022888 | 0.091553 | 0.082397 | -0.004578 | -0.082397 | -0.054932 | 0.086975 | 0.036621 | 122.6028 | 122.5113 | -0.073243 | 122.5204 | 122.5342 | 0.022888 | 0.068664 | 122.5754 | 122.525 | -0.086975 | 122.58 | 122.4838 | -0.041199 | -0.05951 | 122.4197 | 122.5616 | 122.5891 | 0.01831 | 122.406 | 122.4335 | 122.5708 | 0.032043
2103.75 | 122.6715 | -122.5159 | 0.032043 | 0.075073 | -0.00058528 | -0.063303 | 0.020561 | -0.016173 | 0.0025335 | -0.0063297 | -0.0083922 | 0.024332 | 0.024539 | 0.02619 | 0.01637 | 0.012798 | 0.004578 | -0.091553 | -0.013733 | 0.009155 | -0.022888 | 0.073242 | -0.032043 | 0.013733 | -0.018311 | -0.10986 | -0.036621 | -0.027466 | 0.068665 | 0 | 122.5891 | 122.4838 | -0.054931 | 122.4243 | 122.525 | 0.041198 | -0.027465 | 122.5845 | 122.5159 | -0.068664 | 122.5296 | 122.406 | -0.10986 | -0.059509 | 122.493 | 122.5204 | 122.5021 | -0.064086 | 122.4792 | 122.4884 | 122.4976 | -0.032043
2105.4375 | 122.7448 | -122.4792 | 0.022888 | -0.19958 | -0.0031489 | -0.061808 | 0.023979 | -0.011046 | -0.0045161 | -0.0067569 | -0.13046 | 0.020486 | 0.026034 | 0.024054 | 0.011243 | 0.016643 | 0.10986 | 0.091553 | 0.15106 | 0.091553 | -0.064087 | 0.10986 | 0.004578 | 0.13733 | 0.16479 | 0.041199 | -0.086975 | -0.050354 | 0.086975 | 0.036621 | 122.5891 | 122.4838 | -0.086975 | 122.5708 | 122.5708 | 0.086975 | 0.086975 | 122.5662 | 122.5159 | -0.10986 | 122.6166 | 122.5204 | 0.004578 | -0.073242 | 122.4152 | 122.5891 | 122.6303 | -0.01831 | 122.3923 | 122.4289 | 122.644 | 0.013733
2107.1406 | 122.7631 | -122.4426 | 0.009155 | 0.11322 | -0.0037897 | -0.062876 | 0.022484 | -0.011901 | -0.00067088 | -0.0035525 | 0.12131 | 0.022195 | 0.025821 | 0.022559 | 0.017011 | 0.012798 | 0.091553 | 0.064087 | 0.12817 | 0.086975 | -0.073242 | 0.10986 | -0.004578 | 0.14648 | 0.1236 | 0.022888 | -0.082397 | -0.082397 | 0.10071 | 0.050354 | 122.5525 | 122.438 | -0.082397 | 122.5067 | 122.5296 | 0.091553 | 0.082398 | 122.5433 | 122.493 | -0.091552 | 122.5891 | 122.4655 | -0.027466 | -0.091552 | 122.3694 | 122.5342 | 122.5708 | -0.013733 | 122.3602 | 122.3602 | 122.5662 | 0.041199
2108.8906 | 122.6761 | -122.5388 | 0.032043 | -0.16907 | -0.00037168 | -0.060526 | 0.023125 | -0.009551 | -0.0021661 | -0.0054751 | -0.23727 | 0.022836 | 0.025393 | 0.024908 | 0.015515 | 0.013439 | -0.004578 | -0.036621 | 0.009155 | -0.004578 | -0.036621 | 0.064087 | -0.041199 | 0.009155 | 0.032043 | -0.086975 | -0.041199 | -0.032043 | 0.059509 | 0.004578 | 122.6028 | 122.4976 | -0.068664 | 122.5021 | 122.5342 | 0.036621 | -0.036621 | 122.5983 | 122.5433 | -0.073242 | 122.5479 | 122.4518 | -0.091553 | -0.064086 | 122.5021 | 122.5342 | 122.5479 | -0.073242 | 122.4976 | 122.5067 | 122.5708 | -0.027465
2110.5625 | 122.7356 | -122.5113 | 0.004578 | 0.12085 | -0.0059259 | -0.058817 | 0.017571 | -0.012755 | -0.0055841 | -0.0048343 | 0.13657 | 0.022836 | 0.024539 | 0.021704 | 0.015515 | 0.015789 | 0.068665 | 0.082397 | 0.1236 | 0.045776 | -0.068665 | 0.10986 | 0.009155 | 0.1236 | 0.082397 | -0.004578 | -0.086975 | -0.059509 | 0.09613 | 0.032043 | 122.6212 | 122.5204 | -0.073243 | 122.5937 | 122.5571 | 0.036621 | 0.064087 | 122.6074 | 122.5433 | -0.091553 | 122.6349 | 122.5067 | -0.036621 | -0.064087 | 122.4426 | 122.58 | 122.6349 | 0.004577 | 122.4243 | 122.4518 | 122.5937 | 0.027465
2112.2812 | 122.7402 | -122.4976 | 0.022888 | 0.097962 | -0.0054987 | -0.061594 | 0.01992 | -0.014251 | -0.0045161 | -0.0073977 | 0.11368 | 0.024118 | 0.023044 | 0.022772 | 0.015515 | 0.012585 | 0.082397 | 0.064087 | 0.10986 | 0.050354 | -0.07782 | 0.10071 | 0 | 0.11902 | 0.09613 | 0.009155 | -0.082397 | -0.064087 | 0.10986 | 0.022888 | 122.5983 | 122.4976 | -0.10071 | 122.5616 | 122.5479 | 0.050354 | 0.059509 | 122.6074 | 122.5204 | -0.10528 | 122.6166 | 122.5067 | -0.013733 | -0.086975 | 122.4197 | 122.58 | 122.6074 | -0.022888 | 122.4152 | 122.4335 | 122.5937 | 0
2113.9688 | 122.7036 | -122.5296 | 0.032043 | -0.14618 | 0.0015509 | -0.062448 | 0.021843 | -0.015105 | -0.00067088 | -0.0044071 | -0.20676 | 0.023904 | 0.027316 | 0.025122 | 0.016797 | 0.010448 | 0.027466 | -0.036621 | 0.022888 | 0.004578 | -0.032043 | 0.073242 | -0.054932 | 0.050354 | 0.068665 | -0.073242 | -0.041199 | -0.032043 | 0.07782 | -0.004578 | 122.6028 | 122.4747 | -0.064086 | 122.493 | 122.5342 | 0.05951 | -0.004577 | 122.6074 | 122.525 | -0.073242 | 122.58 | 122.4564 | -0.068664 | -0.064086 | 122.4976 | 122.5571 | 122.5525 | -0.086975 | 122.4884 | 122.4976 | 122.5983 | -0.036621
2115.7031 | 122.7859 | -122.4747 | 0.018311 | 0.18188 | -0.0033625 | -0.060953 | 0.019493 | -0.01596 | -0.0019525 | -0.0037661 | 0.067902 | 0.023691 | 0.025821 | 0.021704 | 0.015729 | 0.012798 | 0.09613 | 0.054932 | 0.1236 | 0.082397 | -0.054932 | 0.13275 | 0.009155 | 0.14191 | 0.11444 | 0.027466 | -0.091553 | -0.059509 | 0.1236 | 0.050354 | 122.6074 | 122.4838 | -0.073243 | 122.5296 | 122.5571 | 0.073242 | 0.077819 | 122.5983 | 122.525 | -0.10986 | 122.6166 | 122.5021 | -0.022888 | -0.07782 | 122.4197 | 122.5708 | 122.5983 | -0.009156 | 122.3831 | 122.4152 | 122.5891 | 0.032043
2117.4062 | 122.7356 | -122.493 | 0.009155 | 0.11322 | -0.0052851 | -0.060312 | 0.020988 | -0.012969 | -0.0055841 | -0.0063297 | 0.11368 | 0.020914 | 0.022616 | 0.024054 | 0.016584 | 0.016003 | 0.09613 | 0.086975 | 0.15106 | 0.073242 | -0.07782 | 0.10986 | 0.013733 | 0.14191 | 0.13275 | 0.027466 | -0.07782 | -0.054932 | 0.091553 | 0.045776 | 122.6028 | 122.5067 | -0.086975 | 122.58 | 122.5662 | 0.059509 | 0.086975 | 122.5845 | 122.5388 | -0.086975 | 122.6349 | 122.5204 | -0.01831 | -0.064087 | 122.4152 | 122.5891 | 122.644 | 0.004578 | 122.4152 | 122.438 | 122.6257 | 0.036621
2119.0938 | 122.7768 | -122.493 | -0.009155 | 0.159 | -0.0057123 | -0.06074 | 0.018211 | -0.014464 | -0.0013117 | -0.0078249 | 0.067902 | 0.026041 | 0.022616 | 0.022559 | 0.018933 | 0.013439 | 0.073242 | 0.009155 | 0.068665 | 0.050354 | -0.054932 | 0.11444 | -0.018311 | 0.13733 | 0.10071 | 0 | -0.07782 | -0.054932 | 0.11902 | 0.027466 | 122.6074 | 122.4747 | -0.045777 | 122.5021 | 122.5433 | 0.068665 | 0.082397 | 122.612 | 122.5204 | -0.068665 | 122.6303 | 122.493 | -0.027466 | -0.045777 | 122.438 | 122.5662 | 122.5616 | -0.009156 | 122.4152 | 122.438 | 122.5937 | 0.036621
2120.7812 | 122.7448 | -122.4976 | 0.018311 | 0.067444 | -0.0057123 | -0.06074 | 0.020988 | -0.015105 | -0.0072931 | -0.0061161 | 0.098419 | 0.024332 | 0.023471 | 0.021277 | 0.013593 | 0.015789 | 0.059509 | 0.036621 | 0.091553 | 0.041199 | -0.073242 | 0.10071 | 0.013733 | 0.082397 | 0.091553 | -0.004578 | -0.064087 | -0.054932 | 0.091553 | 0.036621 | 122.5983 | 122.5113 | -0.091553 | 122.5342 | 122.5388 | 0.027466 | 0.041198 | 122.5891 | 122.5342 | -0.082398 | 122.58 | 122.493 | -0.041199 | -0.073243 | 122.4243 | 122.5571 | 122.5891 | -0.004578 | 122.4335 | 122.4426 | 122.5891 | 0.01831
2122.4688 | 122.7219 | -122.5113 | 0.004578 | 0.082703 | -0.0063531 | -0.058817 | 0.017998 | -0.015105 | -0.0053705 | -0.0076113 | 0.1442 | 0.022623 | 0.023898 | 0.022345 | 0.013166 | 0.012585 | 0.10529 | 0.068665 | 0.12817 | 0.059509 | -0.086975 | 0.10529 | 0.004578 | 0.12817 | 0.10986 | 0.022888 | -0.068665 | -0.050354 | 0.10986 | 0.041199 | 122.6166 | 122.5159 | -0.091553 | 122.58 | 122.5708 | 0.054931 | 0.10071 | 122.6212 | 122.5525 | -0.073243 | 122.6395 | 122.5342 | -0.018311 | -0.054932 | 122.4243 | 122.6166 | 122.6395 | 0 | 122.4426 | 122.4609 | 122.6212 | 0.036621
2124.1406 | 122.699 | -122.5204 | 0.022888 | 0.090332 | -0.0016535 | -0.060312 | 0.018852 | -0.013824 | 0.0021063 | -0.0048343 | 0.037384 | 0.020273 | 0.024325 | 0.025122 | 0.016584 | 0.014294 | 0.032043 | -0.091553 | -0.009155 | -0.009155 | -0.045776 | 0.073242 | -0.032043 | 0.027466 | -0.013733 | -0.091553 | -0.032043 | -0.036621 | 0.073242 | 0 | 122.5937 | 122.4884 | -0.068664 | 122.4289 | 122.5113 | 0.022888 | 0.009155 | 122.5937 | 122.5204 | -0.054931 | 122.5479 | 122.4289 | -0.091553 | -0.059509 | 122.4747 | 122.5525 | 122.5113 | -0.054931 | 122.4884 | 122.4838 | 122.5067 | -0.022888
2125.875 | 122.7264 | -122.5159 | 0.045776 | -0.15381 | -0.00058528 | -0.062021 | 0.025047 | -0.014678 | -0.0017389 | -0.0039797 | -0.18387 | 0.021982 | 0.024753 | 0.024268 | 0.016156 | 0.01408 | -0.004578 | -0.045776 | 0.009155 | 0.009155 | -0.036621 | 0.073242 | -0.050354 | 0.013733 | 0.041199 | -0.091553 | -0.022888 | -0.013733 | 0.050354 | -0.004578 | 122.5891 | 122.4655 | -0.082397 | 122.4701 | 122.525 | 0.059509 | -0.050354 | 122.5662 | 122.5113 | -0.068664 | 122.5296 | 122.4243 | -0.086975 | -0.059509 | 122.4792 | 122.5113 | 122.525 | -0.09613 | 122.493 | 122.5021 | 122.5571 | -0.050354
2127.5625 | 122.7631 | -122.4976 | 0.013733 | 0.029297 | -0.0040033 | -0.06074 | 0.023766 | -0.01361 | -0.0068659 | -0.0065433 | 0.060272 | 0.017282 | 0.026462 | 0.022345 | 0.012525 | 0.014294 | 0.027466 | 0.032043 | 0.082397 | 0.036621 | -0.073242 | 0.10071 | -0.009155 | 0.082397 | 0.073242 | -0.009155 | -0.059509 | -0.054932 | 0.09613 | 0.032043 | 122.5983 | 122.4884 | -0.086975 | 122.5296 | 122.5342 | 0.045776 | 0.013733 | 122.5937 | 122.5296 | -0.073242 | 122.58 | 122.4884 | -0.041198 | -0.068665 | 122.4243 | 122.525 | 122.58 | -0.022888 | 122.438 | 122.4426 | 122.5708 | 0.01831
2129.25 | 122.6624 | -122.5342 | 0.041199 | -0.046997 | -0.0040033 | -0.062021 | 0.018425 | -0.012115 | 0.0023199 | -0.0059023 | -0.061798 | 0.023691 | 0.024112 | 0.024054 | 0.018079 | 0.011516 | 0.073242 | 0.009155 | 0.050354 | 0.032043 | -0.036621 | 0.09613 | -0.009155 | 0.045776 | 0.041199 | -0.068665 | -0.059509 | -0.022888 | 0.073242 | -0.004578 | 122.6303 | 122.525 | -0.07782 | 122.5433 | 122.5662 | 0.041198 | 0.032043 | 122.6074 | 122.5296 | -0.10071 | 122.58 | 122.4655 | -0.064087 | -0.064087 | 122.4976 | 122.6074 | 122.5845 | -0.050354 | 122.4747 | 122.5113 | 122.5754 | -0.045777
2130.9844 | 122.7631 | -122.5113 | 0.004578 | 0.044556 | -0.0072077 | -0.058176 | 0.019707 | -0.016601 | -0.0077203 | -0.0033389 | 0.067902 | 0.021768 | 0.024112 | 0.02149 | 0.015515 | 0.015148 | 0.041199 | 0.036621 | 0.082397 | 0.050354 | -0.068665 | 0.10529 | 0.004578 | 0.10071 | 0.09613 | -0.004578 | -0.082397 | -0.050354 | 0.09613 | 0.036621 | 122.6166 | 122.5159 | -0.073243 | 122.5479 | 122.5616 | 0.045776 | 0.036621 | 122.6074 | 122.5479 | -0.086975 | 122.612 | 122.5067 | -0.041199 | -0.054932 | 122.4426 | 122.5525 | 122.5937 | 0 | 122.4289 | 122.4609 | 122.6074 | 0.032043
2132.6719 | 122.6532 | -122.5342 | 0.036621 | -0.069885 | -0.00079888 | -0.060526 | 0.020561 | -0.014464 | 0.0029607 | -0.0061161 | -0.1152 | 0.023264 | 0.026034 | 0.024054 | 0.016584 | 0.012798 | 0.082397 | 0.022888 | 0.045776 | 0.022888 | -0.041199 | 0.09613 | -0.041199 | 0.068665 | 0.054932 | -0.045776 | -0.059509 | -0.032043 | 0.082397 | 0.009155 | 122.6303 | 122.493 | -0.07782 | 122.5571 | 122.5571 | 0.064087 | 0.045776 | 122.6166 | 122.5433 | -0.09613 | 122.6028 | 122.4884 | -0.054931 | -0.068664 | 122.493 | 122.6166 | 122.58 | -0.07782 | 122.4747 | 122.5021 | 122.5891 | -0.027466
2134.4062 | 122.7539 | -122.5113 | 0.018311 | 0.18188 | -0.0067805 | -0.060953 | 0.019493 | -0.013396 | -0.0051569 | -0.0054751 | 0.1442 | 0.02305 | 0.023471 | 0.02085 | 0.016156 | 0.015362 | 0.09613 | 0.086975 | 0.14191 | 0.068665 | -0.07782 | 0.12817 | 0.009155 | 0.14648 | 0.12817 | 0.045776 | -0.086975 | -0.064087 | 0.10071 | 0.041199 | 122.6395 | 122.5204 | -0.096131 | 122.5983 | 122.58 | 0.05951 | 0.077819 | 122.612 | 122.5525 | -0.10529 | 122.6578 | 122.5571 | 0.004577 | -0.082398 | 122.4335 | 122.6074 | 122.6532 | -0.009156 | 122.4243 | 122.4472 | 122.6395 | 0.022888
2136.1094 | 122.7814 | -122.5159 | -0.004578 | 0.10559 | -0.0029351 | -0.060953 | 0.018639 | -0.011901 | -0.00067088 | -0.0044071 | 0.075531 | 0.024545 | 0.023471 | 0.022345 | 0.01637 | 0.014721 | 0.027466 | -0.050354 | -0.004578 | -0.009155 | -0.036621 | 0.068665 | -0.022888 | 0.045776 | 0.004578 | -0.068665 | -0.041199 | -0.032043 | 0.07782 | 0 | 122.5845 | 122.493 | -0.032043 | 122.4655 | 122.5067 | 0.013733 | 0.032044 | 122.5937 | 122.5159 | -0.036621 | 122.5616 | 122.4472 | -0.068665 | -0.027465 | 122.4792 | 122.5433 | 122.5113 | -0.01831 | 122.4747 | 122.4838 | 122.5204 | 0.004578
2137.7969 | 122.7539 | -122.5067 | 0.013733 | 0.16663 | -0.0054987 | -0.060953 | 0.018639 | -0.013824 | -0.0043023 | -0.0052615 | 0.1442 | 0.02305 | 0.024753 | 0.021704 | 0.014447 | 0.016003 | 0.10071 | 0.10071 | 0.15106 | 0.073242 | -0.073242 | 0.12817 | 0.009155 | 0.14191 | 0.13275 | 0.054932 | -0.07782 | -0.059509 | 0.11444 | 0.041199 | 122.6349 | 122.5159 | -0.086975 | 122.6074 | 122.58 | 0.064087 | 0.086975 | 122.6212 | 122.5479 | -0.091553 | 122.6486 | 122.5616 | 0.013733 | -0.073242 | 122.4335 | 122.6074 | 122.6578 | -0.004578 | 122.4289 | 122.4472 | 122.6395 | 0.027466
2139.4844 | 122.7081 | -122.525 | 0.018311 | -0.085144 | -0.0033625 | -0.059885 | 0.01928 | -0.014464 | 0.00018372 | -0.0046207 | -0.1152 | 0.023691 | 0.02283 | 0.021918 | 0.018293 | 0.011516 | 0.068665 | 0.022888 | 0.054932 | 0.041199 | -0.036621 | 0.082397 | -0.045776 | 0.059509 | 0.07782 | -0.045776 | -0.068665 | -0.054932 | 0.07782 | 0.009155 | 122.6074 | 122.4792 | -0.054932 | 122.5479 | 122.5662 | 0.086975 | 0.050354 | 122.6028 | 122.5342 | -0.086976 | 122.5845 | 122.4792 | -0.054931 | -0.073243 | 122.4884 | 122.5937 | 122.58 | -0.064087 | 122.4564 | 122.4701 | 122.6028 | -0.009156
2141.1719 | 122.6761 | -122.5662 | 0.022888 | -0.18433 | -0.0012263 | -0.059458 | 0.025047 | -0.013183 | -0.0060113 | -0.0067569 | -0.16861 | 0.022195 | 0.026675 | 0.022559 | 0.011243 | 0.015575 | 0.059509 | 0.041199 | 0.10529 | 0.054932 | -0.07782 | 0.086975 | -0.018311 | 0.054932 | 0.07782 | -0.050354 | -0.041199 | -0.027466 | 0.068665 | 0.009155 | 122.6532 | 122.5479 | -0.10071 | 122.6074 | 122.6212 | 0.073243 | 0.036621 | 122.6349 | 122.5754 | -0.064087 | 122.6212 | 122.5159 | -0.059509 | -0.050354 | 122.4884 | 122.6257 | 122.6715 | -0.041199 | 122.525 | 122.5388 | 122.644 | -0.013733
2142.8594 | 122.6761 | -122.5433 | 0.032043 | -0.18433 | -0.0020807 | -0.057749 | 0.023552 | -0.012542 | -0.0055841 | -0.0061161 | -0.36697 | 0.022195 | 0.02518 | 0.023413 | 0.012311 | 0.016857 | 0.022888 | 0.013733 | 0.059509 | 0.022888 | -0.050354 | 0.091553 | -0.036621 | 0.027466 | 0.050354 | -0.064087 | -0.027466 | -0.009155 | 0.073242 | -0.004578 | 122.6349 | 122.5067 | -0.082397 | 122.5571 | 122.5662 | 0.059509 | -0.009155 | 122.6166 | 122.5388 | -0.059509 | 122.5708 | 122.4792 | -0.059509 | -0.041198 | 122.493 | 122.5662 | 122.6028 | -0.068664 | 122.5159 | 122.5342 | 122.5937 | -0.036621
2144.5469 | 122.7219 | -122.5296 | 0.018311 | -0.16144 | -0.0029351 | -0.06138 | 0.022484 | -0.01126 | -0.0010981 | -0.0071841 | -0.16098 | 0.024759 | 0.028384 | 0.023199 | 0.014447 | 0.014294 | -0.004578 | -0.045776 | 0.013733 | -0.004578 | -0.018311 | 0.086975 | -0.050354 | 0.013733 | 0.045776 | -0.07782 | -0.032043 | -0.022888 | 0.07782 | 0 | 122.6166 | 122.4792 | -0.036622 | 122.4838 | 122.525 | 0.045776 | -0.022889 | 122.6074 | 122.5296 | -0.050354 | 122.5433 | 122.4518 | -0.07782 | -0.041199 | 122.5113 | 122.525 | 122.5433 | -0.068665 | 122.4976 | 122.5067 | 122.5754 | -0.018311
2146.25 | 122.8043 | -122.4976 | 0.009155 | -0.077515 | -0.0033625 | -0.059458 | 0.020988 | -0.014037 | -0.01007 | -0.0071841 | -0.069428 | 0.021341 | 0.024112 | 0.020636 | 0.012311 | 0.014507 | 0.073242 | 0.13733 | 0.16022 | 0.091553 | -0.068665 | 0.12817 | 0 | 0.12817 | 0.17395 | 0.050354 | -0.10071 | -0.050354 | 0.10071 | 0.027466 | 122.6257 | 122.4976 | -0.07782 | 122.6349 | 122.5891 | 0.091553 | 0.064087 | 122.5983 | 122.525 | -0.10986 | 122.6257 | 122.5479 | 0.022888 | -0.059509 | 122.4289 | 122.5708 | 122.6578 | -0.009155 | 122.3969 | 122.4472 | 122.6715 | 0.018311
2147.9844 | 122.6898 | -122.5433 | 0.036621 | -0.15381 | -0.0029351 | -0.060099 | 0.023979 | -0.013824 | -0.0049433 | -0.0069705 | -0.13046 | 0.02305 | 0.026889 | 0.022986 | 0.013806 | 0.012371 | 0.086975 | 0.07782 | 0.14191 | 0.068665 | -0.082397 | 0.10986 | 0 | 0.09613 | 0.15564 | 0.027466 | -0.064087 | -0.050354 | 0.082397 | 0.027466 | 122.6532 | 122.5433 | -0.11902 | 122.6212 | 122.612 | 0.068665 | 0.050354 | 122.6257 | 122.5708 | -0.10071 | 122.6395 | 122.5708 | 0 | -0.086975 | 122.4609 | 122.6303 | 122.6852 | -0.036621 | 122.4792 | 122.493 | 122.699 | -0.009155
2149.6875 | 122.6898 | -122.5433 | 0.018311 | -0.062256 | 0.00026912 | -0.060526 | 0.017998 | -0.015105 | 0.0010381 | -0.0044071 | -0.15335 | 0.026468 | 0.026034 | 0.023199 | 0.01872 | 0.01173 | 0.064087 | 0.022888 | 0.064087 | 0.032043 | -0.032043 | 0.082397 | -0.018311 | 0.073242 | 0.073242 | -0.032043 | -0.045776 | -0.027466 | 0.091553 | 0.018311 | 122.6257 | 122.525 | -0.050354 | 122.5662 | 122.5754 | 0.050354 | 0.045776 | 122.6349 | 122.5616 | -0.064087 | 122.6166 | 122.5113 | -0.050354 | -0.045777 | 122.5113 | 122.6074 | 122.6074 | -0.036622 | 122.4976 | 122.5159 | 122.6166 | 0
2151.375 | 122.699 | -122.5616 | 0.022888 | -0.14618 | -0.0054987 | -0.06074 | 0.021416 | -0.012969 | -0.0062249 | -0.0059023 | -0.14572 | 0.021555 | 0.026034 | 0.02085 | 0.012525 | 0.013653 | 0.068665 | 0.082397 | 0.12817 | 0.064087 | -0.07782 | 0.10986 | 0.009155 | 0.09613 | 0.12817 | 0.032043 | -0.064087 | -0.059509 | 0.10071 | 0.032043 | 122.6715 | 122.5708 | -0.10071 | 122.644 | 122.6257 | 0.054932 | 0.045777 | 122.6624 | 122.5937 | -0.086975 | 122.6578 | 122.5937 | 0 | -0.082397 | 122.4838 | 122.6303 | 122.6898 | -0.013733 | 122.4976 | 122.5021 | 122.6898 | 0.009155
2153.0781 | 122.7676 | -122.5021 | 0.013733 | -0.14618 | -0.0022943 | -0.059671 | 0.024406 | -0.0091238 | -0.0068659 | -0.0041933 | -0.13809 | 0.023264 | 0.02753 | 0.021704 | 0.011884 | 0.013653 | 0.086975 | 0.1236 | 0.14648 | 0.091553 | -0.068665 | 0.11902 | 0.009155 | 0.12817 | 0.1831 | 0.064087 | -0.073242 | -0.068665 | 0.10986 | 0.022888 | 122.6212 | 122.5113 | -0.082398 | 122.6257 | 122.5937 | 0.082398 | 0.073242 | 122.612 | 122.525 | -0.086975 | 122.6303 | 122.5662 | 0.041199 | -0.082398 | 122.4335 | 122.5891 | 122.6486 | -0.004578 | 122.4289 | 122.4335 | 122.6852 | 0.009155
2154.7656 | 122.7173 | -122.5433 | 0.032043 | -0.19958 | -0.0022943 | -0.062021 | 0.020561 | -0.012115 | -0.0015253 | -0.0059023 | -0.1915 | 0.021768 | 0.027743 | 0.025122 | 0.01637 | 0.012157 | 0 | -0.032043 | 0.018311 | 0.004578 | -0.041199 | 0.082397 | -0.054932 | 0.018311 | 0.032043 | -0.082397 | -0.041199 | -0.018311 | 0.068665 | 0.013733 | 122.6257 | 122.4884 | -0.073242 | 122.5113 | 122.5479 | 0.05951 | -0.032043 | 122.612 | 122.5571 | -0.073242 | 122.5616 | 122.4609 | -0.09613 | -0.050354 | 122.5021 | 122.5433 | 122.5616 | -0.086975 | 122.5021 | 122.525 | 122.5754 | -0.01831
2156.4531 | 122.8043 | -122.5067 | 0.004578 | 0.029297 | -0.0059259 | -0.05839 | 0.020348 | -0.013183 | -0.0062249 | -0.0069705 | 0.037384 | 0.022195 | 0.025821 | 0.022345 | 0.014234 | 0.014721 | 0.013733 | 0.045776 | 0.082397 | 0.036621 | -0.064087 | 0.10529 | -0.009155 | 0.07782 | 0.10529 | -0.004578 | -0.068665 | -0.059509 | 0.10071 | 0.018311 | 122.612 | 122.4976 | -0.068665 | 122.5525 | 122.5433 | 0.045776 | 0.009155 | 122.6074 | 122.525 | -0.073243 | 122.5845 | 122.5021 | -0.022889 | -0.064087 | 122.4426 | 122.5204 | 122.5891 | -0.013733 | 122.438 | 122.4472 | 122.612 | 0.013733
2158.1406 | 122.7814 | -122.5159 | 0.009155 | -0.13855 | -0.0035761 | -0.05839 | 0.020561 | -0.014892 | -0.0057977 | -0.0097475 | -0.13046 | 0.021341 | 0.025607 | 0.022345 | 0.012952 | 0.013012 | 0.10529 | 0.10071 | 0.13733 | 0.082397 | -0.082397 | 0.10986 | -0.009155 | 0.12817 | 0.16479 | 0.054932 | -0.086975 | -0.054932 | 0.10071 | 0.041199 | 122.6257 | 122.5067 | -0.091552 | 122.6166 | 122.5983 | 0.091552 | 0.096131 | 122.6166 | 122.5571 | -0.09613 | 122.644 | 122.5708 | 0.013733 | -0.064087 | 122.4335 | 122.6212 | 122.6532 | -0.01831 | 122.4289 | 122.4609 | 122.6807 | 0.032044
2159.8438 | 122.8134 | -122.5296 | 0.004578 | 0.014038 | -0.0031489 | -0.059885 | 0.019707 | -0.01361 | -0.0062249 | -0.0069705 | 0.029755 | 0.021768 | 0.023471 | 0.022559 | 0.013806 | 0.013439 | 0.027466 | 0.013733 | 0.082397 | 0.041199 | -0.050354 | 0.10529 | 0.009155 | 0.09613 | 0.086975 | -0.004578 | -0.064087 | -0.068665 | 0.091553 | 0.022888 | 122.6349 | 122.5388 | -0.054932 | 122.5433 | 122.5708 | 0.032044 | 0.022888 | 122.6212 | 122.5525 | -0.068665 | 122.6257 | 122.525 | -0.027466 | -0.073243 | 122.4792 | 122.5571 | 122.612 | 0.004577 | 122.4655 | 122.4609 | 122.6166 | 0.01831
2161.5312 | 122.7493 | -122.5113 | 0.004578 | 0.15137 | -0.0042169 | -0.059885 | 0.017357 | -0.010833 | -0.00067088 | -0.0039797 | 0.12131 | 0.020914 | 0.021335 | 0.019995 | 0.01637 | 0.013439 | 0.10529 | 0.086975 | 0.13733 | 0.086975 | -0.068665 | 0.10986 | 0.009155 | 0.14648 | 0.12817 | 0.032043 | -0.09613 | -0.068665 | 0.10986 | 0.041199 | 122.6212 | 122.5204 | -0.073243 | 122.5983 | 122.5983 | 0.07782 | 0.10071 | 122.6212 | 122.5525 | -0.10071 | 122.6578 | 122.5433 | -0.009156 | -0.073243 | 122.4426 | 122.6166 | 122.6486 | 0.004577 | 122.4152 | 122.4426 | 122.6395 | 0.036621
2163.2344 | 122.818 | -122.5021 | 0 | 0.18188 | -0.0042169 | -0.061167 | 0.018425 | -0.012328 | 0.00018372 | -0.0069705 | 0.10605 | 0.021127 | 0.020907 | 0.023199 | 0.018079 | 0.012798 | 0.064087 | 0.004578 | 0.068665 | 0.022888 | -0.059509 | 0.11902 | 0 | 0.091553 | 0.091553 | -0.009155 | -0.082397 | -0.064087 | 0.091553 | 0.032043 | 122.6212 | 122.5021 | -0.059509 | 122.5067 | 122.525 | 0.022888 | 0.064087 | 122.5937 | 122.5342 | -0.082397 | 122.5937 | 122.493 | -0.041198 | -0.064087 | 122.4426 | 122.5662 | 122.5708 | 0 | 122.4197 | 122.438 | 122.5937 | 0.032043
2164.9531 | 122.6944 | -122.5296 | 0.022888 | 0.059815 | -0.0037897 | -0.061594 | 0.01928 | -0.011474 | 0.0012519 | -0.0054751 | 0.052643 | 0.024332 | 0.022403 | 0.024268 | 0.019788 | 0.014294 | 0.009155 | -0.073242 | -0.018311 | -0.022888 | -0.027466 | 0.073242 | -0.022888 | 0.032043 | -0.022888 | -0.11902 | -0.036621 | -0.022888 | 0.054932 | -0.004578 | 122.6028 | 122.5067 | -0.050354 | 122.4564 | 122.5067 | 0 | -0.013733 | 122.5845 | 122.525 | -0.059509 | 122.5616 | 122.4106 | -0.11444 | -0.045776 | 122.5021 | 122.5388 | 122.5113 | -0.045776 | 122.493 | 122.5067 | 122.5067 | -0.027466
2166.6406 | 122.7264 | -122.525 | 0.032043 | -0.1004 | -0.0020807 | -0.059458 | 0.022911 | -0.013396 | 0.00039732 | -0.0048343 | -0.1152 | 0.023691 | 0.028384 | 0.022131 | 0.016156 | 0.013225 | 0.059509 | 0.013733 | 0.059509 | 0.027466 | -0.027466 | 0.073242 | -0.041199 | 0.068665 | 0.064087 | -0.041199 | -0.054932 | -0.032043 | 0.073242 | 0.004578 | 122.5983 | 122.4838 | -0.059509 | 122.5388 | 122.5525 | 0.068665 | 0.027466 | 122.5983 | 122.5296 | -0.086975 | 122.5937 | 122.4838 | -0.045777 | -0.064086 | 122.4976 | 122.5845 | 122.5845 | -0.073242 | 122.4701 | 122.493 | 122.5891 | -0.027465
2168.3594 | 122.7951 | -122.4838 | -0.013733 | 0.33447 | -0.0033625 | -0.058817 | 0.01992 | -0.014678 | -0.0053705 | -0.0033389 | 0.15945 | 0.022409 | 0.024753 | 0.021063 | 0.017011 | 0.017498 | 0.091553 | 0.073242 | 0.11444 | 0.07782 | -0.073242 | 0.11444 | -0.009155 | 0.14648 | 0.1236 | 0.022888 | -0.073242 | -0.07782 | 0.10529 | 0.041199 | 122.5983 | 122.4747 | -0.059509 | 122.5571 | 122.5616 | 0.086975 | 0.10529 | 122.5891 | 122.525 | -0.059509 | 122.6303 | 122.5067 | -0.018311 | -0.064087 | 122.4106 | 122.5754 | 122.5983 | 0.004578 | 122.4106 | 122.406 | 122.6074 | 0.054932
2170.0625 | 122.7997 | -122.4884 | -0.009155 | 0.11322 | -0.0044305 | -0.05839 | 0.020988 | -0.01126 | -0.0030207 | -0.0039797 | 0.18234 | 0.0207 | 0.023471 | 0.02384 | 0.016156 | 0.014294 | 0.10986 | 0.082397 | 0.13275 | 0.091553 | -0.073242 | 0.10071 | 0.022888 | 0.13733 | 0.14648 | 0.036621 | -0.07782 | -0.07782 | 0.09613 | 0.022888 | 122.5891 | 122.5113 | -0.064087 | 122.5708 | 122.58 | 0.068665 | 0.11902 | 122.5845 | 122.5113 | -0.068665 | 122.6257 | 122.525 | 0.013733 | -0.068665 | 122.4152 | 122.5983 | 122.6212 | 0.032043 | 122.4106 | 122.4106 | 122.6349 | 0.032043
2171.75 | 122.8134 | -122.5159 | 0.004578 | -0.12329 | -0.0027215 | -0.060312 | 0.025047 | -0.014464 | -0.0081477 | -0.0046207 | -0.084686 | 0.021555 | 0.027957 | 0.021918 | 0.012311 | 0.012371 | 0.10986 | 0.1236 | 0.16022 | 0.11444 | -0.064087 | 0.10529 | 0.018311 | 0.13275 | 0.16937 | 0.054932 | -0.073242 | -0.068665 | 0.10529 | 0.032043 | 122.6212 | 122.5342 | -0.068665 | 122.6395 | 122.6303 | 0.09613 | 0.10529 | 122.6212 | 122.5479 | -0.07782 | 122.6486 | 122.5708 | 0.022889 | -0.073243 | 122.4518 | 122.6257 | 122.6761 | 0.013733 | 122.4426 | 122.4472 | 122.6852 | 0.027465
2173.4844 | 122.8134 | -122.5067 | -0.009155 | 0.18951 | -0.0029351 | -0.060526 | 0.019066 | -0.012755 | -0.0019525 | -0.0069705 | 0.12131 | 0.023477 | 0.024539 | 0.024054 | 0.016156 | 0.012585 | 0.064087 | 0.032043 | 0.082397 | 0.050354 | -0.07782 | 0.12817 | 0 | 0.12817 | 0.10986 | 0.009155 | -0.073242 | -0.059509 | 0.10071 | 0.050354 | 122.6349 | 122.5067 | -0.068665 | 122.5388 | 122.5571 | 0.050354 | 0.073242 | 122.6074 | 122.5571 | -0.064087 | 122.6349 | 122.5159 | -0.041199 | -0.050354 | 122.4289 | 122.5708 | 122.5891 | 0.009155 | 122.4335 | 122.4472 | 122.6166 | 0.059509
2175.1719 | 122.7127 | -122.5571 | 0.041199 | -0.16907 | -0.0033625 | -0.060312 | 0.023766 | -0.014464 | -0.0051569 | -0.0069705 | -0.22202 | 0.026682 | 0.025393 | 0.024054 | 0.015302 | 0.012371 | 0 | -0.041199 | 0.013733 | -0.004578 | -0.027466 | 0.073242 | -0.045776 | 0.013733 | 0.027466 | -0.086975 | -0.041199 | -0.022888 | 0.059509 | -0.004578 | 122.6303 | 122.5113 | -0.068665 | 122.5159 | 122.5525 | 0.041198 | -0.041199 | 122.6166 | 122.5525 | -0.082398 | 122.5708 | 122.4701 | -0.082397 | -0.064087 | 122.5296 | 122.5571 | 122.5708 | -0.086975 | 122.5159 | 122.5342 | 122.5845 | -0.045777
2176.9219 | 122.731 | -122.5525 | 0.018311 | -0.19196 | -0.0035761 | -0.059885 | 0.01992 | -0.011474 | -0.0010981 | -0.0063297 | -0.17624 | 0.023264 | 0.027743 | 0.022131 | 0.015515 | 0.014294 | 0.004578 | -0.036621 | -0.009155 | 0.009155 | -0.027466 | 0.064087 | -0.050354 | 0.004578 | 0.022888 | -0.086975 | -0.036621 | -0.032043 | 0.068665 | -0.004578 | 122.6166 | 122.5021 | -0.045777 | 122.5159 | 122.5616 | 0.059509 | -0.013733 | 122.6212 | 122.5479 | -0.054932 | 122.5571 | 122.4655 | -0.082397 | -0.050354 | 122.525 | 122.5571 | 122.5433 | -0.068665 | 122.5159 | 122.5204 | 122.5754 | -0.022889
2178.625 | 122.6624 | -122.5388 | 0.032043 | -0.046997 | -0.0037897 | -0.062876 | 0.019707 | -0.010833 | 0.00061092 | -0.0022707 | -0.069428 | 0.024973 | 0.026034 | 0.025122 | 0.017224 | 0.013012 | 0.07782 | 0.027466 | 0.059509 | 0.027466 | -0.054932 | 0.082397 | -0.013733 | 0.068665 | 0.064087 | -0.059509 | -0.054932 | -0.022888 | 0.07782 | 0.004578 | 122.6212 | 122.525 | -0.086975 | 122.5662 | 122.5662 | 0.041199 | 0.045777 | 122.6166 | 122.5433 | -0.086975 | 122.6074 | 122.4792 | -0.064087 | -0.054931 | 122.4838 | 122.6166 | 122.5983 | -0.045776 | 122.4838 | 122.5159 | 122.6028 | -0.027465
2180.3125 | 122.7448 | -122.5525 | 0.018311 | -0.10803 | 0.0015509 | -0.060312 | 0.023979 | -0.011901 | -0.00088448 | -0.0054751 | -0.13809 | 0.023904 | 0.026889 | 0.022986 | 0.016156 | 0.014507 | 0.022888 | -0.004578 | 0.054932 | 0.045776 | -0.045776 | 0.082397 | -0.045776 | 0.050354 | 0.073242 | -0.050354 | -0.036621 | -0.027466 | 0.082397 | 0.009155 | 122.6349 | 122.5067 | -0.064087 | 122.5479 | 122.5983 | 0.091552 | 0.004577 | 122.6349 | 122.5616 | -0.054932 | 122.6028 | 122.5021 | -0.059509 | -0.045777 | 122.5067 | 122.5754 | 122.6074 | -0.064087 | 122.5159 | 122.525 | 122.6257 | -0.009156
2182.0156 | 122.7814 | -122.525 | 0.004578 | 0.036926 | -0.0048579 | -0.060953 | 0.022057 | -0.010192 | -0.0094293 | -0.0052615 | 0.10605 | 0.023477 | 0.026675 | 0.024268 | 0.012738 | 0.017712 | 0.013733 | 0.059509 | 0.09613 | 0.045776 | -0.073242 | 0.10986 | -0.009155 | 0.07782 | 0.07782 | -0.018311 | -0.068665 | -0.045776 | 0.082397 | 0.032043 | 122.6349 | 122.5159 | -0.07782 | 122.5845 | 122.5708 | 0.054931 | 0.009155 | 122.6074 | 122.5571 | -0.073243 | 122.6028 | 122.5067 | -0.050354 | -0.050354 | 122.4518 | 122.5388 | 122.6212 | -0.013733 | 122.4564 | 122.4792 | 122.6028 | 0.027465
2183.7188 | 122.7402 | -122.5388 | 0.013733 | -0.1004 | -0.0035761 | -0.058176 | 0.018639 | -0.013396 | -0.00067088 | -0.0046207 | -0.14572 | 0.026682 | 0.026248 | 0.025977 | 0.017652 | 0.01408 | 0.045776 | 0.004578 | 0.032043 | 0.045776 | -0.041199 | 0.073242 | -0.036621 | 0.050354 | 0.073242 | -0.041199 | -0.036621 | -0.027466 | 0.07782 | -0.013733 | 122.612 | 122.5021 | -0.054932 | 122.5433 | 122.5845 | 0.082397 | 0.032043 | 122.6166 | 122.525 | -0.050354 | 122.5891 | 122.4976 | -0.027466 | -0.041199 | 122.4976 | 122.5845 | 122.5708 | -0.050354 | 122.5021 | 122.5113 | 122.612 | -0.027466
2185.4531 | 122.7768 | -122.5159 | 0.004578 | 0.15137 | -0.0061395 | -0.060526 | 0.018639 | -0.014037 | -0.0055841 | -0.0063297 | 0.15182 | 0.024332 | 0.026889 | 0.02149 | 0.014447 | 0.015789 | 0.086975 | 0.10986 | 0.14648 | 0.064087 | -0.082397 | 0.11902 | 0.013733 | 0.1236 | 0.13275 | 0.032043 | -0.07782 | -0.059509 | 0.086975 | 0.036621 | 122.6349 | 122.5296 | -0.086975 | 122.6257 | 122.58 | 0.050354 | 0.082397 | 122.6028 | 122.5525 | -0.082398 | 122.6395 | 122.5479 | -0.004578 | -0.064087 | 122.4335 | 122.6028 | 122.6624 | 0.009155 | 122.438 | 122.4564 | 122.6486 | 0.032043
2187.1719 | 122.7219 | -122.5571 | 0.018311 | 0.082703 | -0.0010125 | -0.059458 | 0.018639 | -0.013396 | -0.0028071 | -0.0050479 | 0.09079 | 0.027109 | 0.024753 | 0.023413 | 0.016797 | 0.012157 | 0.004578 | -0.068665 | -0.018311 | -0.013733 | -0.022888 | 0.073242 | -0.022888 | 0.018311 | -0.018311 | -0.10529 | -0.045776 | 0 | 0.059509 | 0.004578 | 122.6303 | 122.5342 | -0.041199 | 122.4884 | 122.5433 | 0.009155 | -0.013733 | 122.6166 | 122.5616 | -0.064087 | 122.5754 | 122.4518 | -0.10986 | -0.018311 | 122.5342 | 122.5616 | 122.5388 | -0.041199 | 122.5113 | 122.5571 | 122.5388 | -0.013733
2188.9375 | 122.7036 | -122.5525 | 0.036621 | 0.059815 | -0.00058528 | -0.060312 | 0.021202 | -0.014251 | 0.0012519 | -0.0052615 | 0.022125 | 0.027109 | 0.028598 | 0.02384 | 0.016797 | 0.014934 | 0.009155 | -0.059509 | -0.004578 | -0.009155 | -0.054932 | 0.086975 | -0.032043 | -0.027466 | -0.041199 | -0.11902 | -0.045776 | -0.004578 | 0.054932 | -0.013733 | 122.6395 | 122.5204 | -0.091553 | 122.493 | 122.5433 | 0.022888 | -0.027466 | 122.6074 | 122.5388 | -0.082397 | 122.525 | 122.4335 | -0.10529 | -0.041199 | 122.4976 | 122.5616 | 122.5479 | -0.068664 | 122.5067 | 122.5479 | 122.5113 | -0.050354
2190.7031 | 122.8226 | -122.5021 | -0.004578 | -0.1004 | -0.0057123 | -0.058603 | 0.021843 | -0.013824 | -0.0092157 | -0.0080387 | -0.054169 | 0.021768 | 0.027316 | 0.02085 | 0.01167 | 0.014721 | 0.09613 | 0.11444 | 0.16937 | 0.10529 | -0.07782 | 0.10529 | -0.009155 | 0.12817 | 0.16937 | 0.059509 | -0.082397 | -0.054932 | 0.10529 | 0.022888 | 122.6074 | 122.493 | -0.073242 | 122.6166 | 122.6074 | 0.11444 | 0.10071 | 122.6074 | 122.525 | -0.077819 | 122.6303 | 122.5616 | 0.036621 | -0.050354 | 122.4243 | 122.5983 | 122.6715 | -0.004577 | 122.4197 | 122.4472 | 122.6715 | 0.027466
2192.5 | 122.8317 | -122.525 | 0.004578 | 0.17426 | -0.0046441 | -0.059244 | 0.017571 | -0.012969 | -0.0032343 | -0.0039797 | 0.13657 | 0.024759 | 0.023684 | 0.022559 | 0.017652 | 0.013653 | 0.054932 | -0.009155 | 0.064087 | 0.041199 | -0.059509 | 0.10071 | -0.009155 | 0.11444 | 0.07782 | 0 | -0.068665 | -0.059509 | 0.09613 | 0.054932 | 122.6257 | 122.5159 | -0.064087 | 122.5159 | 122.5662 | 0.050354 | 0.050354 | 122.6212 | 122.58 | -0.073243 | 122.6395 | 122.525 | -0.054932 | -0.064087 | 122.4655 | 122.58 | 122.5891 | -0.013733 | 122.4564 | 122.4655 | 122.6028 | 0.050354
2194.2344 | 122.8043 | -122.5342 | 0.022888 | -0.12329 | -0.0025079 | -0.059458 | 0.024193 | -0.014464 | -0.0077203 | -0.0071841 | -0.13046 | 0.022623 | 0.027102 | 0.022559 | 0.01167 | 0.015789 | 0.10071 | 0.11902 | 0.16022 | 0.091553 | -0.073242 | 0.10529 | -0.018311 | 0.11902 | 0.16479 | 0.054932 | -0.082397 | -0.064087 | 0.10071 | 0.013733 | 122.6395 | 122.5159 | -0.09613 | 122.6532 | 122.6257 | 0.10986 | 0.07782 | 122.6349 | 122.5479 | -0.10528 | 122.6532 | 122.5891 | 0.041199 | -0.086975 | 122.4609 | 122.6349 | 122.6944 | -0.041199 | 122.4518 | 122.4701 | 122.699 | -0.009155
2195.9688 | 122.8363 | -122.5342 | 0.009155 | -0.031738 | -0.0048579 | -0.060099 | 0.021202 | -0.013183 | -0.0068659 | -0.0095339 | -0.00076274 | 0.023477 | 0.028384 | 0.021704 | 0.011457 | 0.013653 | 0.059509 | 0.045776 | 0.10986 | 0.045776 | -0.054932 | 0.091553 | 0.004578 | 0.10071 | 0.12817 | 0.041199 | -0.068665 | -0.059509 | 0.09613 | 0.027466 | 122.6257 | 122.5388 | -0.064087 | 122.58 | 122.58 | 0.041198 | 0.050354 | 122.6303 | 122.5616 | -0.07782 | 122.6349 | 122.5754 | 0.013733 | -0.068664 | 122.4792 | 122.5937 | 122.644 | -0.004577 | 122.4655 | 122.4747 | 122.6624 | 0.018311
2197.6875 | 122.7814 | -122.5204 | -0.004578 | 0.15137 | -0.0061395 | -0.06074 | 0.017784 | -0.014464 | 0.00082452 | -0.0065433 | 0.1442 | 0.023691 | 0.025821 | 0.021063 | 0.017865 | 0.013866 | 0.1236 | 0.07782 | 0.13733 | 0.073242 | -0.082397 | 0.11444 | 0.009155 | 0.16022 | 0.12817 | 0.022888 | -0.086975 | -0.068665 | 0.11902 | 0.032043 | 122.6349 | 122.5296 | -0.077819 | 122.5983 | 122.5937 | 0.064087 | 0.12817 | 122.6395 | 122.5525 | -0.082397 | 122.6807 | 122.5433 | -0.009155 | -0.064087 | 122.4381 | 122.644 | 122.6578 | 0.013733 | 122.4335 | 122.4518 | 122.6486 | 0.036621
2199.375 | 122.6944 | -122.5708 | 0.013733 | -0.054626 | -0.0027215 | -0.058603 | 0.01693 | -0.01361 | 0.0027471 | -0.0050479 | -0.10757 | 0.026468 | 0.026462 | 0.024908 | 0.018506 | 0.011516 | 0.091553 | 0.009155 | 0.050354 | 0.027466 | -0.041199 | 0.082397 | -0.027466 | 0.086975 | 0.054932 | -0.050354 | -0.050354 | -0.022888 | 0.068665 | 0.018311 | 122.6532 | 122.5433 | -0.054932 | 122.58 | 122.5983 | 0.054932 | 0.07782 | 122.6395 | 122.5891 | -0.064087 | 122.6578 | 122.5204 | -0.068665 | -0.036621 | 122.5296 | 122.6624 | 122.6212 | -0.041199 | 122.5204 | 122.5479 | 122.6257 | 0.004578
2201.0938 | 122.7127 | -122.5708 | 0.027466 | 0.052185 | -0.0020807 | -0.06074 | 0.020775 | -0.011474 | -0.00024348 | -0.0048343 | 0.067902 | 0.024973 | 0.028598 | 0.025977 | 0.01637 | 0.014721 | 0 | -0.10071 | -0.032043 | -0.013733 | -0.041199 | 0.086975 | -0.041199 | 0.004578 | -0.022888 | -0.11902 | -0.054932 | -0.018311 | 0.059509 | 0.009155 | 122.6578 | 122.5296 | -0.068665 | 122.4701 | 122.5571 | 0.027466 | -0.027466 | 122.6303 | 122.58 | -0.082398 | 122.5754 | 122.4518 | -0.12817 | -0.045777 | 122.5296 | 122.5708 | 122.5388 | -0.068665 | 122.5159 | 122.5525 | 122.5479 | -0.018311
2202.8125 | 122.7814 | -122.5296 | 0.018311 | 0.12085 | -0.0059259 | -0.060953 | 0.023552 | -0.012755 | -0.0068659 | -0.0052615 | 0.1442 | 0.022836 | 0.028171 | 0.022345 | 0.012738 | 0.017498 | 0.10529 | 0.068665 | 0.14191 | 0.068665 | -0.09613 | 0.10529 | 0.018311 | 0.14191 | 0.10986 | 0.022888 | -0.073242 | -0.073242 | 0.082397 | 0.045776 | 122.6349 | 122.5479 | -0.11444 | 122.5983 | 122.5983 | 0.050354 | 0.086975 | 122.612 | 122.5754 | -0.091553 | 122.6715 | 122.5525 | -0.022888 | -0.091553 | 122.4335 | 122.6349 | 122.6715 | 0 | 122.4564 | 122.4564 | 122.6395 | 0.027465
2204.5312 | 122.8317 | -122.5113 | 0 | 0.029297 | -0.0035761 | -0.058176 | 0.020775 | -0.01831 | -0.0068659 | -0.0080387 | 0.075531 | 0.023904 | 0.02753 | 0.022772 | 0.01402 | 0.014721 | 0.045776 | 0.027466 | 0.086975 | 0.041199 | -0.064087 | 0.11444 | -0.009155 | 0.068665 | 0.073242 | 0.018311 | -0.064087 | -0.041199 | 0.082397 | 0.022888 | 122.6257 | 122.5021 | -0.064087 | 122.5388 | 122.5525 | 0.050354 | 0.045776 | 122.5937 | 122.5342 | -0.064087 | 122.58 | 122.5296 | -0.004577 | -0.041199 | 122.4472 | 122.5571 | 122.5983 | -0.009155 | 122.4472 | 122.4701 | 122.5845 | 0.022888
2206.2344 | 122.7539 | -122.5571 | 0.018311 | -0.13855 | -0.0025079 | -0.060526 | 0.021629 | -0.01361 | -2.988e-05 | -0.0071841 | -0.20676 | 0.024332 | 0.028384 | 0.025122 | 0.018079 | 0.0093801 | 0.027466 | -0.050354 | 0.022888 | 0.022888 | -0.050354 | 0.086975 | -0.036621 | 0.045776 | 0.068665 | -0.068665 | -0.032043 | -0.018311 | 0.073242 | -0.009155 | 122.644 | 122.5204 | -0.068665 | 122.5067 | 122.58 | 0.059509 | 0.009155 | 122.6303 | 122.5479 | -0.050354 | 122.6028 | 122.4884 | -0.05951 | -0.036622 | 122.5067 | 122.5845 | 122.58 | -0.054932 | 122.525 | 122.5388 | 122.6257 | -0.027466
2207.9844 | 122.7814 | -122.5433 | 0.027466 | 0.052185 | -0.0074213 | -0.05839 | 0.017998 | -0.015746 | -0.0070795 | -0.0065433 | 0.075531 | 0.023904 | 0.027316 | 0.02384 | 0.014234 | 0.014294 | 0.041199 | 0.027466 | 0.082397 | 0.036621 | -0.064087 | 0.10071 | 0.013733 | 0.07782 | 0.086975 | -0.013733 | -0.073242 | -0.032043 | 0.082397 | 0.027466 | 122.644 | 122.5571 | -0.091553 | 122.5708 | 122.58 | 0.022888 | 0.013733 | 122.6257 | 122.5708 | -0.10071 | 122.6212 | 122.5296 | -0.041199 | -0.059509 | 122.4792 | 122.5845 | 122.6257 | -0.013733 | 122.4701 | 122.5113 | 122.6303 | 0
2209.6719 | 122.7814 | -122.5525 | 0.013733 | -0.15381 | -0.0031489 | -0.059244 | 0.023552 | -0.014037 | -0.0055841 | -0.0073977 | -0.13046 | 0.023691 | 0.025607 | 0.019995 | 0.01402 | 0.013439 | 0.11444 | 0.09613 | 0.14648 | 0.07782 | -0.082397 | 0.10529 | 0 | 0.13275 | 0.16022 | 0.059509 | -0.073242 | -0.068665 | 0.11902 | 0.054932 | 122.6578 | 122.5525 | -0.09613 | 122.6486 | 122.6303 | 0.07782 | 0.10071 | 122.6715 | 122.6074 | -0.086975 | 122.6852 | 122.612 | 0.004577 | -0.082398 | 122.4701 | 122.6669 | 122.699 | -0.013733 | 122.4792 | 122.4838 | 122.7127 | 0.041199
2211.375 | 122.7493 | -122.5616 | 0 | 0.13611 | -0.0029351 | -0.060526 | 0.018852 | -0.014678 | 0.0016791 | -0.0067569 | 0.075531 | 0.026468 | 0.026675 | 0.024054 | 0.017865 | 0.012157 | 0.004578 | -0.059509 | 0.004578 | -0.004578 | -0.032043 | 0.082397 | -0.036621 | 0.022888 | -0.027466 | -0.10071 | -0.036621 | -0.022888 | 0.068665 | 0.013733 | 122.644 | 122.525 | -0.032043 | 122.5021 | 122.5571 | 0.032043 | 0.004578 | 122.6303 | 122.5754 | -0.036621 | 122.5845 | 122.4609 | -0.11444 | -0.022888 | 122.5296 | 122.5662 | 122.5662 | -0.036621 | 122.525 | 122.5388 | 122.5342 | 0.013733
2213.1094 | 122.7173 | -122.5525 | 0.036621 | -0.085144 | -0.0025079 | -0.061167 | 0.019066 | -0.014037 | 0.00018372 | -0.0048343 | -0.10757 | 0.024332 | 0.025821 | 0.023199 | 0.018506 | 0.012585 | 0.050354 | 0.027466 | 0.064087 | 0.045776 | -0.032043 | 0.073242 | -0.027466 | 0.068665 | 0.07782 | -0.032043 | -0.054932 | -0.045776 | 0.09613 | 0.004578 | 122.6257 | 122.525 | -0.068664 | 122.58 | 122.5983 | 0.073242 | 0.013733 | 122.6486 | 122.5571 | -0.091553 | 122.6212 | 122.5204 | -0.036621 | -0.082397 | 122.5204 | 122.6028 | 122.6166 | -0.064087 | 122.4976 | 122.5067 | 122.6303 | -0.032043
2214.8125 | 122.7905 | -122.5616 | 0.004578 | 0.16663 | -0.0050715 | -0.058603 | 0.021202 | -0.011474 | -0.0034479 | -0.0059023 | 0.16708 | 0.021555 | 0.025393 | 0.019995 | 0.012952 | 0.01408 | 0.07782 | 0.091553 | 0.15106 | 0.086975 | -0.086975 | 0.13275 | 0.013733 | 0.13733 | 0.14191 | 0.036621 | -0.10071 | -0.068665 | 0.09613 | 0.022888 | 122.6944 | 122.5754 | -0.091553 | 122.6532 | 122.6486 | 0.073242 | 0.073242 | 122.6578 | 122.5845 | -0.10529 | 122.699 | 122.5983 | 0.013733 | -0.073243 | 122.4747 | 122.6395 | 122.7127 | 0.009155 | 122.4609 | 122.493 | 122.7036 | 0.01831
2216.5156 | 122.7539 | -122.5525 | 0.022888 | -0.13092 | 0.00091012 | -0.060953 | 0.027184 | -0.013396 | -0.00067088 | -0.0065433 | -0.22202 | 0.023264 | 0.028598 | 0.023413 | 0.014447 | 0.011089 | 0.013733 | -0.045776 | 0.018311 | 0.018311 | -0.041199 | 0.082397 | -0.045776 | 0.013733 | 0.045776 | -0.073242 | -0.032043 | -0.018311 | 0.086975 | 0.009155 | 122.6349 | 122.5067 | -0.064087 | 122.5067 | 122.5708 | 0.064087 | -0.009155 | 122.6395 | 122.5616 | -0.054931 | 122.5662 | 122.4792 | -0.082397 | -0.041199 | 122.5113 | 122.5662 | 122.5708 | -0.068664 | 122.5204 | 122.5342 | 122.5983 | -0.013733
2218.2031 | 122.7127 | -122.5708 | 0.032043 | 0.059815 | -0.0027215 | -0.060953 | 0.017784 | -0.011046 | 0.00039732 | -0.0039797 | 0.045013 | 0.024545 | 0.025393 | 0.022986 | 0.015943 | 0.014721 | -0.013733 | -0.073242 | -0.009155 | -0.009155 | -0.045776 | 0.07782 | -0.032043 | 0.009155 | -0.009155 | -0.10986 | -0.041199 | -0.018311 | 0.068665 | 0 | 122.6486 | 122.5388 | -0.077819 | 122.4976 | 122.5616 | 0.022888 | -0.045776 | 122.6395 | 122.5708 | -0.073242 | 122.58 | 122.4609 | -0.10986 | -0.050354 | 122.525 | 122.5571 | 122.5616 | -0.064086 | 122.5296 | 122.5525 | 122.5616 | -0.032043
2219.9531 | 122.7081 | -122.5525 | 0.041199 | -0.19196 | -0.0065667 | -0.061808 | 0.025261 | -0.012542 | -0.0075067 | -0.0052615 | -0.16098 | 0.022409 | 0.028171 | 0.024054 | 0.015088 | 0.013439 | 0.059509 | 0.086975 | 0.10529 | 0.064087 | -0.073242 | 0.082397 | -0.013733 | 0.054932 | 0.10071 | -0.022888 | -0.068665 | -0.027466 | 0.086975 | 0.004578 | 122.6349 | 122.5388 | -0.11444 | 122.6395 | 122.6166 | 0.07782 | 0.01831 | 122.6395 | 122.5571 | -0.10986 | 122.6074 | 122.5296 | -0.027466 | -0.068665 | 122.4792 | 122.612 | 122.6578 | -0.054932 | 122.4838 | 122.525 | 122.6532 | -0.036621
2221.6562 | 122.8317 | -122.5204 | -0.004578 | 0.097962 | -0.0033625 | -0.059031 | 0.017357 | -0.014251 | -0.0015253 | -0.0048343 | 0.12894 | 0.024973 | 0.025821 | 0.024268 | 0.016156 | 0.013653 | 0.013733 | -0.022888 | 0.018311 | 0.004578 | -0.036621 | 0.082397 | -0.054932 | 0.064087 | 0.018311 | -0.050354 | -0.041199 | -0.041199 | 0.07782 | 0 | 122.6028 | 122.4655 | -0.032043 | 122.4976 | 122.525 | 0.05951 | 0.018311 | 122.5983 | 122.5204 | -0.036621 | 122.5845 | 122.4701 | -0.050354 | -0.036621 | 122.4838 | 122.5342 | 122.5388 | -0.050354 | 122.4792 | 122.4792 | 122.5388 | 0.004578
2223.3438 | 122.8409 | -122.5113 | 0.009155 | 0.15137 | -0.0037897 | -0.061594 | 0.01928 | -0.011687 | -0.0021661 | -0.0050479 | 0.15945 | 0.025613 | 0.026248 | 0.022986 | 0.018079 | 0.014294 | 0.032043 | -0.018311 | 0.036621 | 0.013733 | -0.054932 | 0.086975 | -0.018311 | 0.086975 | 0.068665 | -0.013733 | -0.068665 | -0.036621 | 0.10071 | 0.027466 | 122.5983 | 122.493 | -0.064087 | 122.493 | 122.525 | 0.032044 | 0.022888 | 122.612 | 122.5388 | -0.07782 | 122.5983 | 122.4976 | -0.041199 | -0.045776 | 122.4564 | 122.5433 | 122.5479 | -0.027466 | 122.4426 | 122.4747 | 122.58 | 0.018311
2225.0625 | 122.7585 | -122.5525 | 0.009155 | -0.12329 | -0.0018671 | -0.060099 | 0.021629 | -0.014037 | -0.0038751 | -0.0039797 | -0.16861 | 0.023477 | 0.026462 | 0.023413 | 0.015088 | 0.014721 | 0.013733 | -0.009155 | 0.027466 | 0.027466 | -0.050354 | 0.082397 | -0.036621 | 0.045776 | 0.054932 | -0.041199 | -0.036621 | -0.022888 | 0.073242 | 0.009155 | 122.6349 | 122.5159 | -0.059509 | 122.5433 | 122.58 | 0.064087 | 0.004578 | 122.6257 | 122.5616 | -0.045776 | 122.5983 | 122.5113 | -0.050354 | -0.032043 | 122.5021 | 122.5662 | 122.58 | -0.045776 | 122.5159 | 122.5296 | 122.6074 | 0
2226.7656 | 122.8043 | -122.5433 | -0.004578 | 0.097962 | -0.0025079 | -0.05839 | 0.018425 | -0.013183 | -0.00067088 | -0.0067569 | 0.08316 | 0.022409 | 0.024966 | 0.023627 | 0.017652 | 0.012798 | -0.009155 | -0.041199 | 0.013733 | 0.009155 | -0.027466 | 0.086975 | -0.054932 | 0.045776 | 0.009155 | -0.082397 | -0.050354 | -0.041199 | 0.064087 | 0 | 122.6303 | 122.4884 | -0.022888 | 122.5021 | 122.5525 | 0.064087 | -0.004577 | 122.6074 | 122.5433 | -0.045776 | 122.5891 | 122.4609 | -0.082397 | -0.036621 | 122.5159 | 122.5342 | 122.5571 | -0.050354 | 122.493 | 122.5021 | 122.5525 | 0.004578
2228.5156 | 122.7356 | -122.58 | 0.045776 | -0.18433 | -0.0014399 | -0.056467 | 0.024193 | -0.012542 | -0.0043023 | -0.0071841 | -0.18387 | 0.023477 | 0.02753 | 0.022131 | 0.014234 | 0.014934 | -0.022888 | -0.027466 | 0.032043 | -0.022888 | -0.036621 | 0.073242 | -0.036621 | -0.013733 | 0.032043 | -0.091553 | -0.032043 | -0.018311 | 0.064087 | 0.004578 | 122.6532 | 122.5433 | -0.082397 | 122.5525 | 122.5571 | 0.013733 | -0.068664 | 122.644 | 122.5845 | -0.077819 | 122.5662 | 122.4884 | -0.096131 | -0.064087 | 122.5433 | 122.5571 | 122.612 | -0.082397 | 122.5479 | 122.5616 | 122.612 | -0.041198
2230.2188 | 122.7905 | -122.5342 | -0.022888 | 0.18188 | -0.0046441 | -0.057322 | 0.022484 | -0.011046 | -0.0055841 | -0.0080387 | 0.18997 | 0.0207 | 0.026462 | 0.02149 | 0.014234 | 0.014294 | 0.09613 | 0.068665 | 0.14648 | 0.07782 | -0.068665 | 0.1236 | 0.009155 | 0.12817 | 0.13733 | 0.050354 | -0.073242 | -0.068665 | 0.10071 | 0.041199 | 122.6578 | 122.5433 | -0.045777 | 122.6028 | 122.612 | 0.068665 | 0.11902 | 122.6349 | 122.5754 | -0.050354 | 122.6624 | 122.5845 | 0.009155 | -0.045777 | 122.4655 | 122.6303 | 122.6807 | 0.032043 | 122.4609 | 122.4655 | 122.6715 | 0.064087
2231.9688 | 122.8592 | -122.5296 | 0.013733 | -0.016479 | -0.0050715 | -0.059244 | 0.023766 | -0.015533 | -0.0079339 | -0.0067569 | 0.0068663 | 0.020059 | 0.027743 | 0.022345 | 0.012311 | 0.013653 | 0.041199 | 0.036621 | 0.10986 | 0.050354 | -0.059509 | 0.10071 | 0.004578 | 0.10986 | 0.13275 | 0.036621 | -0.050354 | -0.050354 | 0.09613 | 0.036621 | 122.6303 | 122.5342 | -0.073242 | 122.5662 | 122.58 | 0.045776 | 0.027466 | 122.6257 | 122.5662 | -0.064087 | 122.6395 | 122.5662 | 0 | -0.064087 | 122.4701 | 122.5708 | 122.6395 | -0.009155 | 122.4792 | 122.4792 | 122.6624 | 0.022888
2233.7031 | 122.818 | -122.525 | 0.004578 | 0.10559 | -0.0044305 | -0.061594 | 0.015434 | -0.011901 | -2.988e-05 | -0.0044071 | 0.09079 | 0.023904 | 0.024112 | 0.02384 | 0.017224 | 0.013012 | 0.027466 | -0.041199 | -0.004578 | 0.009155 | -0.041199 | 0.07782 | -0.022888 | 0.036621 | 0 | -0.091553 | -0.036621 | -0.032043 | 0.059509 | 0.018311 | 122.6028 | 122.5021 | -0.045777 | 122.4838 | 122.5342 | 0.032043 | 0.022888 | 122.5845 | 122.5433 | -0.041199 | 122.5616 | 122.4335 | -0.10986 | -0.036621 | 122.4838 | 122.5525 | 122.5204 | -0.027466 | 122.4884 | 122.493 | 122.525 | 0.013733
2235.5 | 122.85 | -122.525 | 0.004578 | -0.0012209 | -0.0042169 | -0.057108 | 0.023552 | -0.011901 | -0.0087885 | -0.0061161 | 0.029755 | 0.0207 | 0.025821 | 0.021063 | 0.010816 | 0.01173 | 0.045776 | 0.036621 | 0.091553 | 0.064087 | -0.068665 | 0.11444 | -0.004578 | 0.091553 | 0.09613 | 0.018311 | -0.07782 | -0.054932 | 0.10986 | 0.041199 | 122.6395 | 122.5204 | -0.073243 | 122.5616 | 122.5891 | 0.068665 | 0.041198 | 122.6349 | 122.5662 | -0.082398 | 122.6166 | 122.5433 | -0.022888 | -0.05951 | 122.4564 | 122.5708 | 122.6166 | -0.009156 | 122.4472 | 122.4701 | 122.6212 | 0.036621
2237.2031 | 122.7081 | -122.6028 | 0.032043 | 0.014038 | -0.0018671 | -0.061594 | 0.01992 | -0.011474 | 0.00082452 | -0.0046207 | 0.014496 | 0.024545 | 0.026034 | 0.024695 | 0.018506 | 0.011089 | 0.032043 | -0.059509 | -0.004578 | -0.004578 | -0.041199 | 0.082397 | -0.036621 | -0.009155 | -0.013733 | -0.1236 | -0.036621 | -0.027466 | 0.054932 | 0.004578 | 122.6852 | 122.5662 | -0.073242 | 122.5433 | 122.5983 | 0.032043 | 0 | 122.6578 | 122.6074 | -0.068664 | 122.5937 | 122.4792 | -0.12817 | -0.059509 | 122.5616 | 122.6349 | 122.5983 | -0.068664 | 122.5662 | 122.5754 | 122.5891 | -0.027465
2238.9688 | 122.7539 | -122.5616 | 0.027466 | -0.11566 | -0.0048579 | -0.059885 | 0.020775 | -0.012542 | -0.0010981 | -0.0063297 | -0.17624 | 0.022623 | 0.021762 | 0.023413 | 0.015088 | 0.012157 | 0 | -0.036621 | 0.009155 | 0.027466 | -0.050354 | 0.064087 | -0.041199 | 0.018311 | 0.064087 | -0.07782 | -0.054932 | -0.027466 | 0.073242 | -0.013733 | 122.6257 | 122.5204 | -0.07782 | 122.525 | 122.5891 | 0.068665 | -0.027466 | 122.6349 | 122.5479 | -0.082398 | 122.58 | 122.4838 | -0.064087 | -0.054932 | 122.5113 | 122.5616 | 122.5708 | -0.068665 | 122.5067 | 122.5342 | 122.6257 | -0.041199
2240.7031 | 122.8363 | -122.5433 | -0.004578 | 0.17426 | -0.0029351 | -0.061167 | 0.020775 | -0.014464 | -0.0036615 | -0.0076113 | 0.09079 | 0.022195 | 0.024753 | 0.020422 | 0.014875 | 0.012798 | 0.07782 | 0.068665 | 0.10071 | 0.064087 | -0.054932 | 0.10071 | 0 | 0.11444 | 0.10986 | 0.027466 | -0.073242 | -0.064087 | 0.10986 | 0.050354 | 122.644 | 122.5433 | -0.050354 | 122.612 | 122.6074 | 0.064087 | 0.082398 | 122.6532 | 122.5937 | -0.068664 | 122.6578 | 122.5708 | -0.022888 | -0.059509 | 122.4884 | 122.6212 | 122.644 | 0.004578 | 122.4701 | 122.4792 | 122.6532 | 0.054932
2242.4062 | 122.7631 | -122.5754 | 0.032043 | -0.1767 | -0.0057123 | -0.060099 | 0.023125 | -0.01361 | -0.0087885 | -0.0065433 | -0.084686 | 0.020486 | 0.023044 | 0.021704 | 0.012952 | 0.01408 | 0.10071 | 0.086975 | 0.15106 | 0.091553 | -0.07782 | 0.12817 | -0.004578 | 0.10529 | 0.14191 | 0.041199 | -0.07782 | -0.050354 | 0.09613 | 0.036621 | 122.7036 | 122.5708 | -0.10986 | 122.6624 | 122.6669 | 0.096131 | 0.068665 | 122.6715 | 122.612 | -0.10986 | 122.6807 | 122.6166 | 0.004578 | -0.082397 | 122.4976 | 122.6761 | 122.7264 | -0.036621 | 122.4976 | 122.525 | 122.7173 | 0.004578
2244.1094 | 122.731 | -122.5754 | 0.018311 | -0.077515 | -0.0020807 | -0.062662 | 0.021843 | -0.010619 | 0.00039732 | -0.0048343 | -0.12283 | 0.023904 | 0.024539 | 0.025549 | 0.017865 | 0.011303 | 0.073242 | 0.004578 | 0.059509 | 0.045776 | -0.059509 | 0.059509 | -0.027466 | 0.086975 | 0.073242 | -0.036621 | -0.054932 | -0.045776 | 0.086975 | 0.013733 | 122.6349 | 122.5479 | -0.07782 | 122.58 | 122.6212 | 0.073242 | 0.054931 | 122.6624 | 122.5891 | -0.073243 | 122.6624 | 122.5388 | -0.050354 | -0.064087 | 122.5159 | 122.6486 | 122.6349 | -0.045777 | 122.5204 | 122.5296 | 122.6486 | -0.004578
2245.8438 | 122.7081 | -122.6074 | 0.054932 | -0.16144 | -0.0018671 | -0.058817 | 0.021416 | -0.012328 | -0.0057977 | -0.0084659 | -0.084686 | 0.021768 | 0.026462 | 0.024481 | 0.01167 | 0.017071 | 0.009155 | -0.004578 | 0.045776 | 0.022888 | -0.041199 | 0.073242 | -0.045776 | 0.022888 | 0.041199 | -0.073242 | -0.032043 | -0.009155 | 0.050354 | 0.004578 | 122.6807 | 122.5616 | -0.096131 | 122.6028 | 122.6303 | 0.068664 | -0.045777 | 122.6578 | 122.612 | -0.086975 | 122.6303 | 122.5342 | -0.07782 | -0.064087 | 122.5662 | 122.6166 | 122.6532 | -0.10071 | 122.5754 | 122.5983 | 122.6486 | -0.050354
2247.5469 | 122.8043 | -122.5388 | 0.004578 | 0.11322 | -0.0040033 | -0.060953 | 0.018211 | -0.013824 | -0.0023797 | -0.0052615 | 0.08316 | 0.024545 | 0.023898 | 0.023627 | 0.017438 | 0.012157 | 0.009155 | -0.059509 | -0.004578 | 0.004578 | -0.041199 | 0.073242 | -0.027466 | 0.036621 | -0.009155 | -0.086975 | -0.045776 | -0.013733 | 0.068665 | -0.004578 | 122.612 | 122.5113 | -0.045777 | 122.4792 | 122.5433 | 0.032044 | 0.004577 | 122.6074 | 122.5342 | -0.050354 | 122.5754 | 122.4518 | -0.082397 | -0.018311 | 122.4976 | 122.5479 | 122.5342 | -0.032044 | 122.493 | 122.525 | 122.5296 | -0.009156
2249.25 | 122.7081 | -122.6074 | 0.032043 | -0.16907 | -0.0020807 | -0.059885 | 0.024406 | -0.012542 | -0.0064387 | -0.0084659 | -0.16098 | 0.024759 | 0.027316 | 0.024268 | 0.011243 | 0.014507 | 0.027466 | -0.013733 | 0.036621 | 0.013733 | -0.050354 | 0.07782 | -0.032043 | 0.013733 | 0.036621 | -0.07782 | -0.036621 | -0.018311 | 0.07782 | -0.004578 | 122.6852 | 122.5754 | -0.082397 | 122.5937 | 122.6212 | 0.045776 | -0.004577 | 122.6852 | 122.6028 | -0.068664 | 122.6212 | 122.5296 | -0.073242 | -0.050354 | 122.5571 | 122.6349 | 122.644 | -0.064086 | 122.5708 | 122.5891 | 122.644 | -0.036621
2251 | 122.818 | -122.5571 | 0.009155 | 0.097962 | -0.0035761 | -0.060099 | 0.017357 | -0.013183 | 0.00061092 | -0.0039797 | 0.10605 | 0.02305 | 0.025393 | 0.025122 | 0.018079 | 0.012585 | 0.004578 | -0.050354 | 0.018311 | -0.004578 | -0.032043 | 0.091553 | -0.018311 | 0.059509 | 0.018311 | -0.045776 | -0.059509 | -0.032043 | 0.073242 | 0.018311 | 122.6486 | 122.5388 | -0.041198 | 122.5067 | 122.5525 | 0.013733 | -0.004577 | 122.6303 | 122.5754 | -0.068664 | 122.6166 | 122.5113 | -0.064087 | -0.041198 | 122.525 | 122.5616 | 122.5754 | -0.027466 | 122.4976 | 122.525 | 122.5754 | 0.009156
2252.7188 | 122.85 | -122.58 | 0 | -0.13855 | -0.0048579 | -0.06138 | 0.023125 | -0.014037 | -0.0070795 | -0.0061161 | -0.046539 | 0.021341 | 0.02518 | 0.021704 | 0.011457 | 0.01643 | 0.086975 | 0.09613 | 0.13733 | 0.086975 | -0.068665 | 0.10529 | 0.004578 | 0.15106 | 0.16479 | 0.082397 | -0.059509 | -0.054932 | 0.10071 | 0.045776 | 122.6852 | 122.5845 | -0.068665 | 122.6761 | 122.6669 | 0.082397 | 0.086975 | 122.6807 | 122.6257 | -0.059509 | 122.731 | 122.6624 | 0.036621 | -0.054932 | 122.5113 | 122.6669 | 122.7173 | 0.004578 | 122.5204 | 122.525 | 122.7448 | 0.045776
2254.4219 | 122.8546 | -122.5296 | -0.013733 | 0.021668 | -0.0033625 | -0.057962 | 0.020775 | -0.013183 | -0.0077203 | -0.0086795 | -0.00076274 | 0.020914 | 0.02518 | 0.021277 | 0.011884 | 0.013225 | 0.036621 | 0.041199 | 0.086975 | 0.050354 | -0.064087 | 0.091553 | -0.009155 | 0.10529 | 0.10529 | 0.022888 | -0.064087 | -0.059509 | 0.082397 | 0.059509 | 122.6212 | 122.5204 | -0.050354 | 122.5708 | 122.58 | 0.059509 | 0.050354 | 122.612 | 122.5891 | -0.050354 | 122.6349 | 122.5525 | -0.036621 | -0.045776 | 122.4655 | 122.5662 | 122.6166 | 0.004578 | 122.4655 | 122.4701 | 122.6349 | 0.073242
2256.1562 | 122.7997 | -122.5708 | -0.009155 | 0.18188 | -0.0048579 | -0.059244 | 0.018425 | -0.013824 | -0.0064387 | -0.0071841 | 0.12131 | 0.023691 | 0.024539 | 0.023199 | 0.015088 | 0.013012 | 0.10529 | 0.082397 | 0.12817 | 0.07782 | -0.073242 | 0.11902 | 0.004578 | 0.14191 | 0.13275 | 0.036621 | -0.091553 | -0.050354 | 0.11444 | 0.045776 | 122.6898 | 122.5754 | -0.064087 | 122.6532 | 122.6486 | 0.073242 | 0.11444 | 122.6852 | 122.6166 | -0.082398 | 122.7127 | 122.6074 | -0.009155 | -0.041199 | 122.4976 | 122.6761 | 122.699 | 0.013733 | 122.4792 | 122.5204 | 122.7036 | 0.054931
2257.9062 | 122.7951 | -122.5662 | 0 | 0.15137 | -0.0052851 | -0.059244 | 0.01992 | -0.012969 | -0.0013117 | -0.0059023 | 0.13657 | 0.021768 | 0.024112 | 0.020422 | 0.014661 | 0.012371 | 0.11902 | 0.086975 | 0.14648 | 0.082397 | -0.086975 | 0.13733 | 0.004578 | 0.13733 | 0.1236 | 0.022888 | -0.07782 | -0.068665 | 0.086975 | 0.045776 | 122.7036 | 122.5708 | -0.086975 | 122.6532 | 122.6486 | 0.077819 | 0.11902 | 122.6532 | 122.612 | -0.07782 | 122.7036 | 122.5891 | -0.022888 | -0.068665 | 122.4792 | 122.6852 | 122.7127 | 0.004578 | 122.4884 | 122.4976 | 122.6898 | 0.045776
2259.6406 | 122.7814 | -122.5754 | 0.009155 | -0.14618 | -0.0048579 | -0.060312 | 0.021629 | -0.011046 | -0.00024348 | -0.0056887 | -0.21439 | 0.021341 | 0.027316 | 0.022986 | 0.017011 | 0.014507 | 0.009155 | -0.045776 | 0.013733 | 0.018311 | -0.022888 | 0.07782 | -0.041199 | 0.036621 | 0.022888 | -0.07782 | -0.036621 | -0.027466 | 0.059509 | -0.009155 | 122.6532 | 122.5342 | -0.032043 | 122.5296 | 122.5937 | 0.05951 | 0 | 122.6349 | 122.5662 | -0.045776 | 122.612 | 122.4976 | -0.068665 | -0.036621 | 122.5525 | 122.5845 | 122.5891 | -0.050354 | 122.5388 | 122.5479 | 122.5983 | -0.01831
2261.3438 | 122.8455 | -122.5525 | 0 | -0.046997 | -0.0040033 | -0.059031 | 0.021202 | -0.015319 | -0.0070795 | -0.0065433 | -0.077057 | 0.018137 | 0.024325 | 0.022131 | 0.013166 | 0.013225 | 0.09613 | 0.10529 | 0.14191 | 0.082397 | -0.07782 | 0.11902 | -0.004578 | 0.14648 | 0.14648 | 0.073242 | -0.082397 | -0.059509 | 0.10071 | 0.022888 | 122.6715 | 122.5479 | -0.07782 | 122.6578 | 122.6349 | 0.086975 | 0.09613 | 122.6532 | 122.5754 | -0.082397 | 122.699 | 122.6257 | 0.050354 | -0.059509 | 122.4747 | 122.6486 | 122.6944 | -0.004578 | 122.4701 | 122.493 | 122.699 | 0.022888
2263.0781 | 122.7814 | -122.5708 | 0.009155 | 0.14374 | -0.0016535 | -0.061167 | 0.017357 | -0.013396 | 0.0012519 | -0.0048343 | 0.075531 | 0.023477 | 0.023471 | 0.022559 | 0.018079 | 0.013866 | 0.018311 | -0.064087 | -0.009155 | -0.009155 | -0.045776 | 0.073242 | -0.041199 | 0.032043 | -0.022888 | -0.091553 | -0.054932 | -0.027466 | 0.073242 | -0.004578 | 122.644 | 122.5296 | -0.054931 | 122.5067 | 122.5616 | 0.032044 | 0.009156 | 122.644 | 122.5662 | -0.064087 | 122.6028 | 122.4792 | -0.086975 | -0.036621 | 122.525 | 122.5891 | 122.5616 | -0.050354 | 122.5159 | 122.5433 | 122.5479 | -0.013733
2264.8281 | 122.7173 | -122.6074 | 0.032043 | -0.21484 | -0.0027215 | -0.058176 | 0.023125 | -0.014251 | -0.0043023 | -0.0071841 | -0.17624 | 0.019846 | 0.02283 | 0.02149 | 0.015943 | 0.015575 | 0.045776 | 0.032043 | 0.07782 | 0.050354 | -0.059509 | 0.086975 | -0.004578 | 0.027466 | 0.091553 | -0.050354 | -0.045776 | -0.018311 | 0.064087 | 0.018311 | 122.6944 | 122.6028 | -0.091552 | 122.6395 | 122.6578 | 0.054932 | 0.013733 | 122.6715 | 122.6257 | -0.077819 | 122.6349 | 122.5571 | -0.068665 | -0.050354 | 122.5479 | 122.6532 | 122.6852 | -0.036621 | 122.5616 | 122.5891 | 122.699 | -0.013732
2266.5312 | 122.7905 | -122.5433 | 0.004578 | 0.11322 | -0.0052851 | -0.059885 | 0.022057 | -0.014678 | -0.0066523 | -0.0052615 | 0.098419 | 0.019418 | 0.023898 | 0.02149 | 0.013379 | 0.015575 | 0.07782 | 0.064087 | 0.11444 | 0.041199 | -0.086975 | 0.11902 | 0.009155 | 0.09613 | 0.091553 | 0 | -0.082397 | -0.073242 | 0.091553 | 0.027466 | 122.6624 | 122.5525 | -0.091553 | 122.6074 | 122.5845 | 0.032044 | 0.073242 | 122.6349 | 122.5708 | -0.086975 | 122.6395 | 122.5433 | -0.027466 | -0.07782 | 122.4564 | 122.6212 | 122.6578 | 0.004577 | 122.4609 | 122.4701 | 122.6349 | 0.022888
2268.2344 | 122.731 | -122.6074 | 0.050354 | -0.1767 | -0.0037897 | -0.060312 | 0.021202 | -0.013183 | -0.0030207 | -0.0073977 | -0.15335 | 0.019846 | 0.023898 | 0.02384 | 0.01402 | 0.012585 | 0.004578 | 0 | 0.041199 | 0.013733 | -0.036621 | 0.07782 | -0.045776 | 0.013733 | 0.032043 | -0.07782 | -0.027466 | -0.013733 | 0.050354 | -0.018311 | 122.6852 | 122.5616 | -0.086975 | 122.6074 | 122.6212 | 0.059509 | -0.045776 | 122.6578 | 122.5891 | -0.07782 | 122.6212 | 122.5296 | -0.059509 | -0.064087 | 122.5708 | 122.612 | 122.6486 | -0.09613 | 122.58 | 122.5937 | 122.6395 | -0.068665
2270 | 122.7219 | -122.6028 | 0.041199 | -0.062256 | -0.0025079 | -0.061594 | 0.020348 | -0.012115 | 0.00018372 | -0.0065433 | -0.13046 | 0.023264 | 0.026889 | 0.024908 | 0.017224 | 0.011303 | 0.086975 | 0.013733 | 0.059509 | 0.041199 | -0.041199 | 0.09613 | -0.027466 | 0.054932 | 0.064087 | -0.064087 | -0.045776 | -0.036621 | 0.073242 | 0.018311 | 122.699 | 122.5754 | -0.082398 | 122.6166 | 122.644 | 0.068665 | 0.045776 | 122.6761 | 122.6212 | -0.086975 | 122.6578 | 122.5388 | -0.082398 | -0.07782 | 122.5616 | 122.6898 | 122.6624 | -0.068665 | 122.5571 | 122.5662 | 122.6669 | -0.022888
2271.7031 | 122.8683 | -122.5342 | 0 | -0.031738 | -0.0027215 | -0.05839 | 0.020561 | -0.014037 | -0.0096429 | -0.0071841 | -0.00076274 | 0.018991 | 0.022403 | 0.022131 | 0.014234 | 0.014507 | 0.054932 | 0.059509 | 0.09613 | 0.059509 | -0.050354 | 0.11444 | 0 | 0.10071 | 0.12817 | 0.045776 | -0.068665 | -0.050354 | 0.10529 | 0.018311 | 122.6486 | 122.5342 | -0.050354 | 122.5937 | 122.5937 | 0.059509 | 0.054932 | 122.6395 | 122.5525 | -0.068665 | 122.6349 | 122.58 | 0.027465 | -0.050354 | 122.4838 | 122.5891 | 122.6303 | 0 | 122.4655 | 122.4838 | 122.6624 | 0.018311
2273.4062 | 122.7356 | -122.5616 | 0.013733 | 0.082703 | -0.0050715 | -0.060312 | 0.016716 | -0.015105 | 0.0023199 | -0.0076113 | 0.045013 | 0.023691 | 0.02283 | 0.022772 | 0.017011 | 0.014934 | 0.009155 | -0.073242 | -0.009155 | 0.013733 | -0.041199 | 0.07782 | -0.027466 | 0.022888 | -0.013733 | -0.11902 | -0.032043 | -0.022888 | 0.064087 | 0 | 122.6395 | 122.5342 | -0.054932 | 122.4884 | 122.5754 | 0.041199 | -0.004578 | 122.6257 | 122.5616 | -0.045776 | 122.5845 | 122.4426 | -0.11902 | -0.036621 | 122.5204 | 122.5708 | 122.5525 | -0.041199 | 122.5296 | 122.5388 | 122.5479 | -0.013733
2275.1094 | 122.731 | -122.58 | 0.054932 | -0.19196 | -0.0029351 | -0.059885 | 0.025688 | -0.014037 | -0.0057977 | -0.0056887 | -0.19913 | 0.020273 | 0.024966 | 0.022345 | 0.011884 | 0.013225 | 0.013733 | 0.004578 | 0.059509 | 0.009155 | -0.045776 | 0.091553 | -0.022888 | 0.022888 | 0.041199 | -0.073242 | -0.041199 | -0.032043 | 0.07782 | -0.004578 | 122.6715 | 122.5571 | -0.10071 | 122.5845 | 122.5891 | 0.032043 | -0.041199 | 122.6578 | 122.5754 | -0.096131 | 122.6028 | 122.5067 | -0.068664 | -0.086975 | 122.5342 | 122.5937 | 122.6395 | -0.07782 | 122.5388 | 122.5479 | 122.6212 | -0.05951
2276.8594 | 122.85 | -122.5754 | 0.009155 | -0.046997 | -0.0078485 | -0.058176 | 0.022057 | -0.014892 | -0.0081477 | -0.0061161 | -0.069428 | 0.017709 | 0.024325 | 0.02085 | 0.014661 | 0.015148 | 0.073242 | 0.082397 | 0.1236 | 0.07782 | -0.064087 | 0.10071 | 0.009155 | 0.13733 | 0.15106 | 0.054932 | -0.082397 | -0.050354 | 0.086975 | 0.013733 | 122.6761 | 122.5845 | -0.073242 | 122.6578 | 122.6532 | 0.068665 | 0.064087 | 122.6624 | 122.5891 | -0.091552 | 122.7127 | 122.6303 | 0.041199 | -0.059509 | 122.5113 | 122.6486 | 122.699 | 0 | 122.493 | 122.525 | 122.7264 | 0.004578
2278.5469 | 122.7264 | -122.6028 | 0.045776 | -0.085144 | 0.00026912 | -0.060953 | 0.021629 | -0.012969 | 0.0010381 | -0.0052615 | -0.099945 | 0.024332 | 0.022189 | 0.02384 | 0.017224 | 0.013225 | 0.086975 | 0.018311 | 0.050354 | 0.050354 | -0.036621 | 0.086975 | -0.032043 | 0.064087 | 0.054932 | -0.041199 | -0.041199 | -0.050354 | 0.07782 | -0.009155 | 122.6898 | 122.5708 | -0.082397 | 122.6212 | 122.6532 | 0.082397 | 0.041199 | 122.6807 | 122.5937 | -0.086975 | 122.6669 | 122.5616 | -0.032044 | -0.09613 | 122.5662 | 122.6898 | 122.6532 | -0.077819 | 122.5616 | 122.5525 | 122.6578 | -0.054931
2280.2812 | 122.7722 | -122.5845 | 0.032043 | -0.18433 | -0.0014399 | -0.057749 | 0.022911 | -0.01361 | -0.00045708 | -0.0054751 | -0.18387 | 0.020914 | 0.02518 | 0.022131 | 0.016156 | 0.01408 | -0.009155 | -0.036621 | 0 | 0.009155 | -0.036621 | 0.073242 | -0.041199 | 0.013733 | 0.036621 | -0.07782 | -0.045776 | -0.018311 | 0.050354 | 0 | 122.6578 | 122.5433 | -0.068664 | 122.5479 | 122.5937 | 0.050354 | -0.041198 | 122.6349 | 122.5845 | -0.077819 | 122.5983 | 122.5067 | -0.07782 | -0.050354 | 122.5479 | 122.5754 | 122.5845 | -0.073242 | 122.5388 | 122.5662 | 122.6212 | -0.032043
2282.0312 | 122.8409 | -122.5708 | -0.009155 | -0.085144 | -0.0065667 | -0.058176 | 0.022697 | -0.013824 | -0.0075067 | -0.0054751 | -0.084686 | 0.01835 | 0.023044 | 0.02085 | 0.012097 | 0.014507 | 0.086975 | 0.12817 | 0.16937 | 0.09613 | -0.064087 | 0.10529 | 0.013733 | 0.11902 | 0.16937 | 0.064087 | -0.091553 | -0.073242 | 0.091553 | 0.036621 | 122.6761 | 122.5845 | -0.054932 | 122.699 | 122.6669 | 0.082397 | 0.09613 | 122.6624 | 122.6074 | -0.082398 | 122.6898 | 122.6349 | 0.027466 | -0.064087 | 122.5067 | 122.6578 | 122.7402 | 0.022888 | 122.4792 | 122.4976 | 122.7402 | 0.045776
2283.75 | 122.7402 | -122.6166 | 0.041199 | -0.18433 | -0.0048579 | -0.058603 | 0.021202 | -0.013824 | -0.0034479 | -0.0073977 | -0.18387 | 0.020914 | 0.024539 | 0.023199 | 0.014447 | 0.01408 | 0 | -0.041199 | 0.013733 | -0.022888 | -0.036621 | 0.082397 | -0.045776 | 0 | 0.022888 | -0.073242 | -0.036621 | -0.032043 | 0.054932 | -0.013733 | 122.699 | 122.5708 | -0.07782 | 122.5754 | 122.5937 | 0.022888 | -0.041199 | 122.6715 | 122.6028 | -0.07782 | 122.6166 | 122.5433 | -0.059509 | -0.073242 | 122.58 | 122.6166 | 122.6303 | -0.086975 | 122.58 | 122.5845 | 122.6395 | -0.054932
2285.4531 | 122.7997 | -122.5616 | 0.022888 | 0.10559 | -0.0063531 | -0.058817 | 0.018425 | -0.014892 | -0.0060113 | -0.0052615 | 0.075531 | 0.017709 | 0.020907 | 0.020422 | 0.015302 | 0.014934 | 0.045776 | 0.054932 | 0.09613 | 0.036621 | -0.068665 | 0.1236 | 0.009155 | 0.086975 | 0.07782 | -0.004578 | -0.073242 | -0.073242 | 0.09613 | 0.032043 | 122.6852 | 122.5708 | -0.091553 | 122.6166 | 122.5983 | 0.027466 | 0.022888 | 122.6578 | 122.5937 | -0.09613 | 122.6486 | 122.5571 | -0.036621 | -0.09613 | 122.493 | 122.6074 | 122.6578 | -0.013733 | 122.4884 | 122.4884 | 122.6395 | 0.009155
2287.1562 | 122.7676 | -122.5937 | 0.032043 | -0.092773 | -0.0042169 | -0.059885 | 0.020775 | -0.013183 | 0.0012519 | -0.0059023 | -0.14572 | 0.024332 | 0.024112 | 0.02384 | 0.016797 | 0.014507 | 0.064087 | 0.013733 | 0.045776 | 0.036621 | -0.050354 | 0.091553 | -0.041199 | 0.073242 | 0.073242 | -0.036621 | -0.045776 | -0.032043 | 0.086975 | 0.018311 | 122.6852 | 122.5525 | -0.082397 | 122.6074 | 122.6303 | 0.07782 | 0.032044 | 122.6807 | 122.612 | -0.077819 | 122.6669 | 122.5571 | -0.054932 | -0.064086 | 122.5433 | 122.6578 | 122.6395 | -0.073242 | 122.5479 | 122.5616 | 122.6669 | -0.013732
2288.875 | 122.7264 | -122.5983 | 0.027466 | -0.039368 | -0.0042169 | -0.06074 | 0.020134 | -0.014892 | -0.0010981 | -0.0054751 | -0.099945 | 0.024759 | 0.023471 | 0.022559 | 0.018293 | 0.01643 | 0.068665 | 0.022888 | 0.054932 | 0.041199 | -0.050354 | 0.091553 | -0.022888 | 0.050354 | 0.064087 | -0.050354 | -0.054932 | -0.032043 | 0.07782 | 0 | 122.6898 | 122.5754 | -0.07782 | 122.6212 | 122.6395 | 0.064087 | 0.041199 | 122.6761 | 122.5983 | -0.082398 | 122.6486 | 122.5479 | -0.050354 | -0.059509 | 122.5479 | 122.6669 | 122.6532 | -0.050354 | 122.5433 | 122.5662 | 122.6624 | -0.027466
2290.5781 | 122.8226 | -122.5891 | 0.004578 | 0.10559 | -0.0046441 | -0.057108 | 0.020988 | -0.014251 | -0.0081477 | -0.0054751 | 0.11368 | 0.019846 | 0.024112 | 0.021063 | 0.013166 | 0.01643 | 0.045776 | 0.064087 | 0.1236 | 0.050354 | -0.082397 | 0.10071 | 0.004578 | 0.091553 | 0.086975 | -0.004578 | -0.086975 | -0.068665 | 0.091553 | 0 | 122.6898 | 122.5937 | -0.086975 | 122.6532 | 122.6395 | 0.045776 | 0.041198 | 122.6807 | 122.5891 | -0.091553 | 122.6807 | 122.5845 | -0.004578 | -0.073243 | 122.5067 | 122.6349 | 122.7127 | 0 | 122.5021 | 122.5204 | 122.6761 | -0.004578
2292.2969 | 122.7036 | -122.6212 | 0.018311 | -0.016479 | -0.00079888 | -0.060526 | 0.020561 | -0.011901 | -0.00045708 | -0.0041933 | 0.0068663 | 0.025613 | 0.025821 | 0.023413 | 0.01872 | 0.013225 | 0.027466 | -0.009155 | 0.027466 | 0.018311 | -0.041199 | 0.091553 | -0.027466 | 0.009155 | -0.004578 | -0.10529 | -0.050354 | -0.022888 | 0.054932 | -0.004578 | 122.7127 | 122.5937 | -0.05951 | 122.612 | 122.6395 | 0.045777 | 0.009155 | 122.6761 | 122.6166 | -0.068665 | 122.6303 | 122.5159 | -0.10071 | -0.041199 | 122.58 | 122.6486 | 122.6486 | -0.045777 | 122.5708 | 122.5983 | 122.6166 | -0.022889
2293.9844 | 122.8867 | -122.5662 | 0 | 0.036926 | -0.0052851 | -0.058603 | 0.022057 | -0.016387 | -0.0085749 | -0.0069705 | 0.052643 | 0.019418 | 0.024325 | 0.02149 | 0.014661 | 0.016643 | 0.013733 | 0.032043 | 0.068665 | 0.032043 | -0.07782 | 0.091553 | -0.009155 | 0.07782 | 0.07782 | 0.013733 | -0.073242 | -0.050354 | 0.09613 | 0.018311 | 122.6578 | 122.5571 | -0.07782 | 122.5983 | 122.5983 | 0.041198 | 0.013733 | 122.6624 | 122.5845 | -0.073242 | 122.644 | 122.58 | -0.004578 | -0.050354 | 122.4884 | 122.58 | 122.6349 | -0.009155 | 122.493 | 122.5159 | 122.644 | 0.018311
2295.7812 | 122.85 | -122.5525 | 0.013733 | 0.17426 | -0.0048579 | -0.060526 | 0.018639 | -0.01361 | -0.0015253 | -0.0063297 | 0.060272 | 0.021127 | 0.023471 | 0.022345 | 0.017011 | 0.013866 | 0.064087 | 0.004578 | 0.082397 | 0.054932 | -0.059509 | 0.091553 | -0.013733 | 0.10986 | 0.10529 | 0.009155 | -0.07782 | -0.059509 | 0.10071 | 0.032043 | 122.644 | 122.5388 | -0.073242 | 122.5571 | 122.6074 | 0.068665 | 0.050354 | 122.6532 | 122.5845 | -0.091553 | 122.6624 | 122.5616 | -0.022888 | -0.073242 | 122.493 | 122.6166 | 122.6349 | -0.027466 | 122.4747 | 122.493 | 122.6578 | 0.01831
2297.4844 | 122.8638 | -122.5708 | 0 | 0.17426 | -0.0037897 | -0.058603 | 0.018211 | -0.014678 | -0.0021661 | -0.0039797 | 0.15945 | 0.020486 | 0.023044 | 0.022131 | 0.014447 | 0.013653 | 0.059509 | 0.004578 | 0.07782 | 0.041199 | -0.050354 | 0.091553 | 0 | 0.10529 | 0.09613 | 0.004578 | -0.086975 | -0.059509 | 0.10529 | 0.041199 | 122.6624 | 122.5708 | -0.050354 | 122.5754 | 122.612 | 0.041199 | 0.059509 | 122.6761 | 122.612 | -0.086975 | 122.6761 | 122.5754 | -0.036621 | -0.059509 | 122.5204 | 122.6303 | 122.6486 | 0 | 122.4838 | 122.5113 | 122.6669 | 0.041199
2299.1875 | 122.8775 | -122.5525 | 0.013733 | -0.031738 | -0.0057123 | -0.059244 | 0.021202 | -0.014678 | -0.0070795 | -0.0065433 | 0.0068663 | 0.020059 | 0.024539 | 0.022986 | 0.012738 | 0.015148 | 0.064087 | 0.036621 | 0.10529 | 0.050354 | -0.064087 | 0.10071 | -0.018311 | 0.11902 | 0.11902 | 0.036621 | -0.068665 | -0.045776 | 0.10529 | 0.022888 | 122.6532 | 122.5342 | -0.07782 | 122.5891 | 122.6028 | 0.068665 | 0.050354 | 122.6578 | 122.5754 | -0.082398 | 122.6715 | 122.5891 | 0.013733 | -0.059509 | 122.4884 | 122.6166 | 122.6578 | -0.032044 | 122.4838 | 122.5067 | 122.6715 | 0.009155
2300.875 | 122.7768 | -122.5891 | 0.027466 | -0.13855 | -0.0010125 | -0.061167 | 0.025902 | -0.011901 | 0.00039732 | -0.0039797 | -0.19913 | 0.021341 | 0.026462 | 0.023199 | 0.015302 | 0.012585 | 0.018311 | -0.032043 | 0.027466 | 0.018311 | -0.036621 | 0.07782 | -0.027466 | 0.027466 | 0.045776 | -0.059509 | -0.032043 | -0.032043 | 0.068665 | 0.004578 | 122.6669 | 122.5616 | -0.064087 | 122.5571 | 122.6074 | 0.045777 | -0.009155 | 122.6578 | 122.5937 | -0.059509 | 122.6166 | 122.5296 | -0.064087 | -0.059509 | 122.5525 | 122.6074 | 122.6166 | -0.054932 | 122.5571 | 122.5571 | 122.6349 | -0.022888
2302.5781 | 122.8592 | -122.5845 | 0.013733 | 0.014038 | -0.0048579 | -0.057962 | 0.022484 | -0.016387 | -0.0085749 | -0.0069705 | 0.075531 | 0.021555 | 0.025393 | 0.020209 | 0.013166 | 0.015148 | 0.032043 | 0.018311 | 0.091553 | 0.041199 | -0.059509 | 0.11444 | -0.004578 | 0.07782 | 0.068665 | -0.018311 | -0.07782 | -0.036621 | 0.086975 | 0.032043 | 122.699 | 122.58 | -0.073242 | 122.6028 | 122.6257 | 0.045777 | 0.01831 | 122.6715 | 122.6166 | -0.091553 | 122.6624 | 122.5662 | -0.050354 | -0.050354 | 122.525 | 122.6166 | 122.6761 | -0.018311 | 122.5067 | 122.5479 | 122.6532 | 0.01831
2304.2969 | 122.7264 | -122.6074 | 0.036621 | 0.067444 | -0.0010125 | -0.060099 | 0.01992 | -0.016173 | 0.0036017 | -0.0024845 | -0.0083922 | 0.024545 | 0.026248 | 0.021918 | 0.017224 | 0.012157 | 0.004578 | -0.073242 | 0.004578 | -0.004578 | -0.064087 | 0.068665 | -0.022888 | 0.009155 | -0.027466 | -0.13275 | -0.022888 | -0.022888 | 0.068665 | -0.004578 | 122.6761 | 122.5845 | -0.10071 | 122.5342 | 122.6028 | 0.01831 | -0.032043 | 122.6761 | 122.6028 | -0.059509 | 122.6166 | 122.4747 | -0.12817 | -0.059509 | 122.5433 | 122.612 | 122.612 | -0.059509 | 122.5845 | 122.5845 | 122.58 | -0.041199
2306.0156 | 122.85 | -122.5616 | 0 | -0.1004 | -0.0048579 | -0.062235 | 0.026115 | -0.015746 | -0.0068659 | -0.0050479 | -0.046539 | 0.021555 | 0.028171 | 0.022131 | 0.012311 | 0.013653 | 0.10986 | 0.11444 | 0.15564 | 0.10529 | -0.068665 | 0.10071 | -0.009155 | 0.15106 | 0.1831 | 0.082397 | -0.082397 | -0.050354 | 0.091553 | 0.041199 | 122.6624 | 122.5525 | -0.068665 | 122.6761 | 122.6669 | 0.11444 | 0.10986 | 122.6532 | 122.6028 | -0.082397 | 122.7127 | 122.644 | 0.041198 | -0.050354 | 122.493 | 122.6715 | 122.7173 | -0.009155 | 122.4792 | 122.5113 | 122.7448 | 0.041199
2307.7188 | 122.7676 | -122.6028 | 0.022888 | -0.19196 | -0.0025079 | -0.059244 | 0.021416 | -0.012328 | -0.00088448 | -0.0073977 | -0.1915 | 0.021768 | 0.026889 | 0.024054 | 0.015515 | 0.013225 | 0.004578 | -0.036621 | -0.013733 | 0 | -0.032043 | 0.07782 | -0.036621 | 0.018311 | 0.013733 | -0.091553 | -0.032043 | -0.013733 | 0.054932 | -0.013733 | 122.6807 | 122.5662 | -0.054931 | 122.5662 | 122.6028 | 0.036621 | -0.01831 | 122.6578 | 122.5891 | -0.054931 | 122.6212 | 122.5113 | -0.07782 | -0.036621 | 122.5708 | 122.6074 | 122.5891 | -0.059509 | 122.5708 | 122.5891 | 122.6166 | -0.036621
2309.4531 | 122.7402 | -122.612 | 0.027466 | -0.16144 | -0.0031489 | -0.060099 | 0.023338 | -0.014892 | -0.0038751 | -0.0069705 | -0.19913 | 0.022409 | 0.026889 | 0.022345 | 0.01402 | 0.014934 | 0.07782 | 0.07782 | 0.11444 | 0.073242 | -0.068665 | 0.091553 | -0.013733 | 0.064087 | 0.09613 | 0 | -0.064087 | -0.036621 | 0.082397 | 0.032043 | 122.7036 | 122.5983 | -0.096131 | 122.6898 | 122.6852 | 0.086975 | 0.050354 | 122.6944 | 122.644 | -0.091553 | 122.6761 | 122.612 | -0.032043 | -0.064087 | 122.5433 | 122.6898 | 122.7264 | -0.041199 | 122.5479 | 122.5754 | 122.7081 | 0.004577
2311.1719 | 122.8729 | -122.5708 | -0.009155 | -0.069885 | -0.0027215 | -0.059244 | 0.022911 | -0.013183 | -0.0066523 | -0.0048343 | -0.061798 | 0.020486 | 0.024112 | 0.022131 | 0.012952 | 0.013653 | 0.082397 | 0.086975 | 0.13275 | 0.073242 | -0.068665 | 0.10529 | 0.009155 | 0.14648 | 0.16937 | 0.054932 | -0.054932 | -0.059509 | 0.09613 | 0.027466 | 122.6761 | 122.58 | -0.05951 | 122.6578 | 122.644 | 0.064087 | 0.091552 | 122.6669 | 122.5983 | -0.045777 | 122.7173 | 122.6257 | 0.027466 | -0.050354 | 122.5021 | 122.6532 | 122.7036 | 0.01831 | 122.5159 | 122.5113 | 122.7402 | 0.036621
2312.9219 | 122.8134 | -122.5616 | -0.004578 | 0.11322 | -0.0037897 | -0.06074 | 0.017998 | -0.014464 | 0.0031745 | -0.0056887 | 0.045013 | 0.025827 | 0.027102 | 0.022986 | 0.018079 | 0.013012 | 0.022888 | -0.045776 | -0.009155 | -0.004578 | -0.032043 | 0.073242 | -0.027466 | 0.045776 | -0.004578 | -0.086975 | -0.022888 | -0.041199 | 0.059509 | -0.004578 | 122.6349 | 122.5342 | -0.027465 | 122.5159 | 122.5571 | 0.022888 | 0.027466 | 122.6212 | 122.5571 | -0.01831 | 122.6074 | 122.4747 | -0.082397 | -0.036621 | 122.5296 | 122.5845 | 122.5525 | -0.022888 | 122.5388 | 122.5204 | 122.5571 | 0
2314.625 | 122.7631 | -122.5983 | 0.041199 | -0.19958 | -0.0027215 | -0.059671 | 0.025047 | -0.013183 | -0.0032343 | -0.0065433 | -0.22202 | 0.026254 | 0.029239 | 0.021277 | 0.015088 | 0.012157 | -0.004578 | -0.036621 | 0.018311 | -0.009155 | -0.027466 | 0.068665 | -0.050354 | 0.018311 | 0.018311 | -0.11444 | -0.050354 | -0.018311 | 0.082397 | -0.018311 | 122.6669 | 122.5479 | -0.068665 | 122.5616 | 122.5891 | 0.041199 | -0.045777 | 122.6807 | 122.58 | -0.091553 | 122.6166 | 122.4838 | -0.09613 | -0.05951 | 122.5708 | 122.5937 | 122.6166 | -0.091553 | 122.5479 | 122.58 | 122.6166 | -0.05951
2316.3438 | 122.8363 | -122.5937 | -0.013733 | 0.159 | -0.0048579 | -0.061167 | 0.019066 | -0.016387 | -0.0055841 | -0.0031253 | 0.17471 | 0.021768 | 0.027743 | 0.019568 | 0.015515 | 0.013653 | 0.10529 | 0.09613 | 0.14191 | 0.082397 | -0.07782 | 0.10529 | 0.004578 | 0.14191 | 0.11902 | 0.036621 | -0.082397 | -0.07782 | 0.09613 | 0.032043 | 122.699 | 122.5983 | -0.064087 | 122.6898 | 122.6761 | 0.077819 | 0.11902 | 122.6898 | 122.6257 | -0.068664 | 122.7356 | 122.6303 | 0.004578 | -0.064087 | 122.5159 | 122.699 | 122.7356 | 0.018311 | 122.5113 | 122.5159 | 122.7127 | 0.045776
2318.0625 | 122.8317 | -122.5937 | 0.013733 | 0.052185 | -0.0044305 | -0.058603 | 0.021843 | -0.014037 | -0.0070795 | -0.0061161 | 0.067902 | 0.024759 | 0.026675 | 0.019568 | 0.012952 | 0.015362 | 0.036621 | 0.018311 | 0.10071 | 0.045776 | -0.050354 | 0.10071 | -0.009155 | 0.068665 | 0.073242 | -0.013733 | -0.068665 | -0.054932 | 0.091553 | 0.018311 | 122.6944 | 122.5845 | -0.064087 | 122.612 | 122.6395 | 0.054931 | 0.022888 | 122.6852 | 122.612 | -0.082398 | 122.6624 | 122.58 | -0.032044 | -0.068665 | 122.5433 | 122.6303 | 122.6944 | -0.022888 | 122.525 | 122.5388 | 122.6669 | 0.004578
2319.75 | 122.8043 | -122.5754 | 0.022888 | 0.052185 | -0.0078485 | -0.058817 | 0.020348 | -0.013183 | -0.0062249 | -0.0071841 | 0.098419 | 0.021341 | 0.026675 | 0.021918 | 0.015088 | 0.012585 | 0.059509 | 0.041199 | 0.10071 | 0.041199 | -0.068665 | 0.1236 | -0.004578 | 0.09613 | 0.073242 | -0.004578 | -0.073242 | -0.050354 | 0.091553 | 0.032043 | 122.699 | 122.5708 | -0.091553 | 122.6166 | 122.6166 | 0.045777 | 0.036621 | 122.6669 | 122.6074 | -0.09613 | 122.6715 | 122.5708 | -0.036621 | -0.073242 | 122.5067 | 122.6349 | 122.6761 | -0.027466 | 122.5021 | 122.525 | 122.6486 | 0.009155
2321.4531 | 122.7768 | -122.5891 | 0.027466 | -0.16907 | -0.0014399 | -0.060099 | 0.024193 | -0.012115 | 0.00061092 | -0.0050479 | -0.20676 | 0.025613 | 0.028598 | 0.022986 | 0.014661 | 0.010662 | 0.032043 | -0.064087 | -0.004578 | 0.022888 | -0.022888 | 0.073242 | -0.022888 | 0.022888 | 0.032043 | -0.082397 | -0.022888 | -0.018311 | 0.064087 | -0.004578 | 122.6624 | 122.5662 | -0.050354 | 122.525 | 122.612 | 0.045776 | 0.004577 | 122.6532 | 122.5845 | -0.050354 | 122.612 | 122.5067 | -0.077819 | -0.045777 | 122.5662 | 122.6212 | 122.5845 | -0.050354 | 122.5662 | 122.5708 | 122.6212 | -0.032044
2323.1719 | 122.8409 | -122.58 | 0.004578 | 0.10559 | -0.0037897 | -0.062021 | 0.017571 | -0.013183 | 0.00061092 | -0.0022707 | 0.052643 | 0.024332 | 0.026889 | 0.021918 | 0.020215 | 0.013012 | 0.009155 | -0.064087 | 0.004578 | -0.004578 | -0.027466 | 0.082397 | -0.045776 | 0.041199 | 0 | -0.064087 | -0.045776 | -0.022888 | 0.068665 | 0 | 122.6624 | 122.5342 | -0.032044 | 122.5159 | 122.5754 | 0.041198 | 0.004577 | 122.6486 | 122.58 | -0.050354 | 122.6212 | 122.5159 | -0.064087 | -0.027466 | 122.5525 | 122.5891 | 122.5845 | -0.050354 | 122.5342 | 122.5571 | 122.58 | -0.004578
2324.9375 | 122.7402 | -122.612 | 0.036621 | -0.024109 | -0.0027215 | -0.059671 | 0.020348 | -0.015105 | 0.00039732 | -0.0041933 | -0.061798 | 0.025613 | 0.026034 | 0.024268 | 0.017011 | 0.013439 | 0.059509 | 0.004578 | 0.054932 | 0.036621 | -0.050354 | 0.086975 | -0.027466 | 0.041199 | 0.041199 | -0.064087 | -0.045776 | -0.013733 | 0.086975 | 0.018311 | 122.699 | 122.5845 | -0.086975 | 122.6166 | 122.6486 | 0.064087 | 0.022888 | 122.699 | 122.6303 | -0.082397 | 122.6532 | 122.5479 | -0.082398 | -0.050354 | 122.5616 | 122.6715 | 122.6669 | -0.064087 | 122.5662 | 122.5983 | 122.6532 | -0.01831
2326.625 | 122.8729 | -122.5525 | 0.009155 | 0.17426 | -0.0033625 | -0.060099 | 0.019493 | -0.01596 | -0.0036615 | -0.0059023 | 0.30441 | 0.023264 | 0.024325 | 0.023413 | 0.015943 | 0.01173 | 0.059509 | 0.036621 | 0.091553 | 0.050354 | -0.054932 | 0.11444 | -0.004578 | 0.11902 | 0.11444 | 0.022888 | -0.082397 | -0.064087 | 0.091553 | 0.013733 | 122.6669 | 122.5479 | -0.064087 | 122.5891 | 122.6028 | 0.054932 | 0.050354 | 122.644 | 122.5662 | -0.091552 | 122.6715 | 122.5754 | 0.009155 | -0.073242 | 122.4976 | 122.612 | 122.644 | -0.013733 | 122.4701 | 122.4884 | 122.6669 | 0.004578
2328.3281 | 122.7402 | -122.5983 | 0.045776 | -0.19196 | -0.0048579 | -0.058817 | 0.025261 | -0.014464 | -0.0055841 | -0.0071841 | -0.17624 | 0.021127 | 0.026034 | 0.021277 | 0.012097 | 0.014294 | 0.045776 | 0.050354 | 0.10529 | 0.064087 | -0.059509 | 0.091553 | -0.013733 | 0.041199 | 0.068665 | -0.032043 | -0.059509 | -0.045776 | 0.050354 | 0.004578 | 122.6898 | 122.5845 | -0.10528 | 122.6486 | 122.6624 | 0.07782 | 0 | 122.6486 | 122.6028 | -0.10528 | 122.6395 | 122.5662 | -0.036621 | -0.091552 | 122.5388 | 122.644 | 122.7036 | -0.059509 | 122.5388 | 122.5525 | 122.6669 | -0.041198
2330.0312 | 122.8088 | -122.58 | 0.041199 | -0.13855 | -0.0014399 | -0.060953 | 0.023125 | -0.012969 | 0.00039732 | -0.0050479 | -0.13046 | 0.023691 | 0.027743 | 0.025763 | 0.015088 | 0.010876 | 0.041199 | -0.013733 | 0.032043 | 0.027466 | -0.032043 | 0.073242 | -0.045776 | 0.041199 | 0.050354 | -0.059509 | -0.041199 | -0.027466 | 0.07782 | 0 | 122.6532 | 122.5342 | -0.073242 | 122.5662 | 122.6074 | 0.073242 | 0 | 122.6578 | 122.58 | -0.082398 | 122.6212 | 122.5204 | -0.059509 | -0.068665 | 122.5479 | 122.6212 | 122.612 | -0.086975 | 122.5388 | 122.5525 | 122.6303 | -0.041199
2331.7344 | 122.7768 | -122.5937 | 0.018311 | 0.082703 | -0.0020807 | -0.058603 | 0.018211 | -0.013183 | -0.00045708 | -0.0037661 | 0.09079 | 0.025613 | 0.026034 | 0.023627 | 0.017652 | 0.015789 | -0.009155 | -0.07782 | -0.018311 | 0 | -0.032043 | 0.086975 | -0.022888 | 0.013733 | -0.013733 | -0.09613 | -0.059509 | -0.022888 | 0.073242 | 0.004578 | 122.6807 | 122.5708 | -0.050354 | 122.5159 | 122.5937 | 0.022888 | -0.027466 | 122.6669 | 122.5983 | -0.07782 | 122.6074 | 122.4976 | -0.10071 | -0.041199 | 122.5616 | 122.5845 | 122.5754 | -0.041199 | 122.5342 | 122.5708 | 122.58 | -0.013733
2333.4375 | 122.8409 | -122.5754 | -0.009155 | 0.15137 | -0.0046441 | -0.058817 | 0.020134 | -0.015533 | -0.0060113 | -0.0044071 | 0.18997 | 0.02305 | 0.025393 | 0.021918 | 0.015943 | 0.014507 | 0.09613 | 0.086975 | 0.15106 | 0.082397 | -0.07782 | 0.1236 | 0 | 0.12817 | 0.14191 | 0.050354 | -0.073242 | -0.064087 | 0.09613 | 0.045776 | 122.699 | 122.5754 | -0.068665 | 122.6624 | 122.6578 | 0.082397 | 0.10528 | 122.6715 | 122.6212 | -0.064087 | 122.7036 | 122.6257 | 0.004578 | -0.054932 | 122.4976 | 122.6715 | 122.7264 | 0.009155 | 122.5021 | 122.5113 | 122.7173 | 0.054931
2335.1406 | 122.8729 | -122.5296 | -0.009155 | 0.159 | -0.0031489 | -0.060526 | 0.018639 | -0.015319 | -0.00045708 | -0.0039797 | 0.12894 | 0.022195 | 0.026034 | 0.022772 | 0.017224 | 0.015148 | 0.041199 | -0.004578 | 0.054932 | 0.036621 | -0.045776 | 0.11444 | -0.009155 | 0.10986 | 0.086975 | -0.004578 | -0.082397 | -0.050354 | 0.09613 | 0.032043 | 122.644 | 122.5204 | -0.036621 | 122.525 | 122.5662 | 0.045776 | 0.050354 | 122.6257 | 122.5616 | -0.073242 | 122.6395 | 122.525 | -0.036621 | -0.041199 | 122.4838 | 122.5708 | 122.5845 | 0 | 122.4472 | 122.4792 | 122.6166 | 0.041198
2336.9531 | 122.7356 | -122.612 | 0.018311 | -0.19196 | -0.00015808 | -0.060526 | 0.025475 | -0.01361 | -0.0051569 | -0.0065433 | -0.13809 | 0.023904 | 0.028598 | 0.023199 | 0.012097 | 0.013225 | -0.013733 | 0 | 0.041199 | 0.018311 | -0.036621 | 0.064087 | -0.036621 | 0.022888 | 0.022888 | -0.068665 | -0.041199 | -0.022888 | 0.064087 | 0.004578 | 122.6761 | 122.5754 | -0.054932 | 122.612 | 122.6303 | 0.054932 | -0.032044 | 122.6761 | 122.6166 | -0.05951 | 122.6349 | 122.5433 | -0.073243 | -0.041199 | 122.5754 | 122.5983 | 122.6532 | -0.054932 | 122.5708 | 122.5891 | 122.6349 | -0.013733
2338.6875 | 122.8409 | -122.5891 | 0.022888 | 0.029297 | -0.0040033 | -0.060953 | 0.020348 | -0.016173 | -0.0077203 | -0.0071841 | 0.075531 | 0.023264 | 0.028811 | 0.022772 | 0.010816 | 0.013225 | 0.041199 | 0.036621 | 0.082397 | 0.032043 | -0.068665 | 0.10529 | -0.004578 | 0.064087 | 0.073242 | -0.009155 | -0.050354 | -0.036621 | 0.082397 | 0.022888 | 122.6944 | 122.5845 | -0.091553 | 122.6257 | 122.6212 | 0.036621 | 0.018311 | 122.6715 | 122.612 | -0.073242 | 122.6532 | 122.58 | -0.032043 | -0.059509 | 122.5204 | 122.6303 | 122.6715 | -0.027466 | 122.5388 | 122.5525 | 122.6624 | 0
2340.4219 | 122.7814 | -122.5891 | 0.045776 | -0.092773 | 0.00048272 | -0.061594 | 0.021629 | -0.012328 | -2.988e-05 | -0.0059023 | -0.14572 | 0.026041 | 0.027743 | 0.022986 | 0.015943 | 0.013653 | 0.068665 | 0.009155 | 0.059509 | 0.050354 | -0.027466 | 0.073242 | -0.050354 | 0.059509 | 0.064087 | -0.032043 | -0.050354 | -0.041199 | 0.064087 | 0.004578 | 122.6624 | 122.5388 | -0.073242 | 122.5983 | 122.6395 | 0.10071 | 0.022889 | 122.6532 | 122.5937 | -0.09613 | 122.6486 | 122.5571 | -0.036621 | -0.086975 | 122.5616 | 122.6578 | 122.6486 | -0.09613 | 122.5388 | 122.5479 | 122.6532 | -0.041198
2342.125 | 122.8363 | -122.5845 | -0.004578 | 0.14374 | -0.0057123 | -0.060526 | 0.018211 | -0.01361 | -0.0045161 | -0.0061161 | 0.1442 | 0.022836 | 0.024539 | 0.022986 | 0.014234 | 0.012798 | 0.086975 | 0.091553 | 0.13733 | 0.07782 | -0.068665 | 0.11902 | 0.004578 | 0.12817 | 0.13275 | 0.027466 | -0.082397 | -0.059509 | 0.091553 | 0.045776 | 122.7036 | 122.5891 | -0.064087 | 122.6761 | 122.6624 | 0.073242 | 0.091553 | 122.6761 | 122.6303 | -0.077819 | 122.7127 | 122.612 | -0.01831 | -0.054931 | 122.5159 | 122.6715 | 122.7219 | 0.009156 | 122.5021 | 122.525 | 122.7173 | 0.050354
2343.9062 | 122.9004 | -122.5616 | 0.013733 | -0.039368 | -0.0033625 | -0.060312 | 0.022697 | -0.012542 | -0.0075067 | -0.0071841 | -0.046539 | 0.022409 | 0.028598 | 0.019568 | 0.01167 | 0.014721 | 0.054932 | 0.07782 | 0.10986 | 0.059509 | -0.059509 | 0.10986 | -0.009155 | 0.13275 | 0.14191 | 0.045776 | -0.059509 | -0.068665 | 0.10986 | 0.032043 | 122.6715 | 122.5525 | -0.073242 | 122.6395 | 122.6212 | 0.068664 | 0.041199 | 122.6715 | 122.5937 | -0.073242 | 122.6944 | 122.6074 | 0.013733 | -0.082398 | 122.5021 | 122.6166 | 122.6715 | -0.022888 | 122.5021 | 122.493 | 122.7036 | 0.01831
2345.625 | 122.8363 | -122.5891 | 0.004578 | 0.059815 | -0.0022943 | -0.060312 | 0.024834 | -0.016387 | -0.0068659 | -0.0048343 | 0.08316 | 0.021982 | 0.029239 | 0.021918 | 0.012952 | 0.014294 | 0.054932 | 0.032043 | 0.10071 | 0.041199 | -0.073242 | 0.11444 | -0.004578 | 0.086975 | 0.068665 | -0.018311 | -0.068665 | -0.054932 | 0.086975 | 0.018311 | 122.7036 | 122.5845 | -0.07782 | 122.6212 | 122.6303 | 0.045777 | 0.050354 | 122.6761 | 122.6074 | -0.073243 | 122.6761 | 122.5708 | -0.036622 | -0.05951 | 122.5159 | 122.644 | 122.6898 | -0.009156 | 122.5204 | 122.5342 | 122.6578 | 0.013733
2347.3594 | 122.8409 | -122.5891 | 0.009155 | 0.014038 | -0.0063531 | -0.061167 | 0.020348 | -0.014892 | -0.0043023 | -0.0082523 | 0.067902 | 0.023477 | 0.028171 | 0.022345 | 0.014234 | 0.015148 | 0.036621 | 0.036621 | 0.082397 | 0.050354 | -0.064087 | 0.07782 | -0.009155 | 0.07782 | 0.068665 | -0.022888 | -0.059509 | -0.064087 | 0.073242 | 0.018311 | 122.6669 | 122.58 | -0.073242 | 122.6257 | 122.6395 | 0.059509 | 0.027466 | 122.6624 | 122.6074 | -0.068664 | 122.6669 | 122.5662 | -0.041199 | -0.073242 | 122.525 | 122.6257 | 122.6715 | -0.01831 | 122.5296 | 122.525 | 122.6578 | 0.009156
2349.0781 | 122.8317 | -122.58 | -0.004578 | 0.15137 | -0.0063531 | -0.059885 | 0.017357 | -0.015746 | -0.0036615 | -0.0050479 | 0.15182 | 0.025613 | 0.027316 | 0.02149 | 0.017865 | 0.011944 | 0.11902 | 0.07782 | 0.13733 | 0.07782 | -0.07782 | 0.10986 | 0.004578 | 0.15564 | 0.1236 | 0.036621 | -0.073242 | -0.064087 | 0.091553 | 0.036621 | 122.6898 | 122.5845 | -0.073242 | 122.6578 | 122.6578 | 0.073242 | 0.1236 | 122.6715 | 122.6166 | -0.068664 | 122.7356 | 122.6166 | 0 | -0.059509 | 122.5021 | 122.699 | 122.7173 | 0.009156 | 122.5067 | 122.5159 | 122.7036 | 0.041199
2350.7812 | 122.8455 | -122.58 | -0.004578 | 0.13611 | -0.0080621 | -0.060312 | 0.020988 | -0.017455 | -0.0045161 | -0.0046207 | 0.10605 | 0.022836 | 0.023898 | 0.023627 | 0.014875 | 0.013012 | 0.10529 | 0.091553 | 0.13733 | 0.068665 | -0.068665 | 0.10529 | -0.004578 | 0.14191 | 0.10986 | 0.018311 | -0.073242 | -0.059509 | 0.091553 | 0.036621 | 122.6852 | 122.5754 | -0.064087 | 122.6715 | 122.6486 | 0.073243 | 0.10986 | 122.6715 | 122.6166 | -0.068664 | 122.7219 | 122.5983 | -0.01831 | -0.054931 | 122.5113 | 122.6852 | 122.7173 | 0 | 122.5067 | 122.5204 | 122.6898 | 0.041199
2352.5625 | 122.8409 | -122.6074 | 0.013733 | 0.067444 | -0.0063531 | -0.060526 | 0.021202 | -0.015319 | -0.0060113 | -0.0065433 | 0.037384 | 0.023691 | 0.02518 | 0.021704 | 0.015302 | 0.013225 | 0.050354 | 0.041199 | 0.091553 | 0.045776 | -0.050354 | 0.10529 | 0.009155 | 0.086975 | 0.064087 | -0.013733 | -0.07782 | -0.054932 | 0.082397 | 0.036621 | 122.7127 | 122.6166 | -0.064087 | 122.6486 | 122.6532 | 0.036621 | 0.036621 | 122.6898 | 122.644 | -0.091553 | 122.6944 | 122.5937 | -0.050354 | -0.068665 | 122.5571 | 122.6578 | 122.699 | -0.004578 | 122.5296 | 122.5525 | 122.6715 | 0.022888
2354.2812 | 122.7585 | -122.6074 | 0.032043 | -0.2301 | -0.0046441 | -0.059244 | 0.023766 | -0.01596 | 0.0018927 | -0.0069705 | -0.2449 | 0.023691 | 0.024539 | 0.027045 | 0.015088 | 0.011089 | 0.004578 | -0.036621 | 0.009155 | 0 | -0.013733 | 0.073242 | -0.050354 | 0.022888 | 0.022888 | -0.091553 | -0.022888 | -0.032043 | 0.068665 | -0.004578 | 122.6807 | 122.5571 | -0.045776 | 122.5708 | 122.6074 | 0.050354 | -0.027465 | 122.6761 | 122.6028 | -0.054931 | 122.6303 | 122.5159 | -0.086975 | -0.064086 | 122.5937 | 122.612 | 122.6166 | -0.082397 | 122.5845 | 122.5754 | 122.6303 | -0.036621
2356 | 122.8043 | -122.5983 | 0.018311 | -0.16144 | -0.0020807 | -0.057535 | 0.02227 | -0.015105 | -0.0049433 | -0.0046207 | -0.13809 | 0.020914 | 0.024112 | 0.020422 | 0.015302 | 0.011516 | 0.082397 | 0.091553 | 0.15564 | 0.09613 | -0.07782 | 0.10986 | -0.004578 | 0.11902 | 0.15564 | 0.045776 | -0.082397 | -0.045776 | 0.09613 | 0.032043 | 122.7081 | 122.5937 | -0.096131 | 122.6898 | 122.6944 | 0.10071 | 0.064086 | 122.6944 | 122.6303 | -0.10071 | 122.7173 | 122.644 | 0.013733 | -0.064087 | 122.5204 | 122.6807 | 122.7539 | -0.022889 | 122.5159 | 122.5525 | 122.7539 | 0.013732
2357.6875 | 122.7905 | -122.6074 | 0.032043 | -0.1004 | -0.0029351 | -0.059031 | 0.021843 | -0.014251 | 0.0016791 | -0.0065433 | -0.14572 | 0.024332 | 0.027957 | 0.02384 | 0.016584 | 0.0095937 | 0.073242 | 0.013733 | 0.059509 | 0.036621 | -0.041199 | 0.073242 | -0.022888 | 0.07782 | 0.073242 | -0.045776 | -0.045776 | -0.054932 | 0.054932 | 0.004578 | 122.6807 | 122.5845 | -0.073242 | 122.6212 | 122.644 | 0.059509 | 0.041199 | 122.6624 | 122.612 | -0.077819 | 122.6852 | 122.5616 | -0.050354 | -0.086975 | 122.5662 | 122.6807 | 122.6669 | -0.054931 | 122.5616 | 122.5525 | 122.6807 | -0.027465
2359.375 | 122.7905 | -122.5754 | 0.013733 | 0.13611 | -0.0057123 | -0.057322 | 0.017784 | -0.013824 | -0.00045708 | -0.0056887 | 0.060272 | 0.022623 | 0.024112 | 0.024268 | 0.017438 | 0.012371 | -0.004578 | -0.050354 | -0.009155 | -0.004578 | -0.022888 | 0.059509 | -0.036621 | 0.032043 | -0.004578 | -0.086975 | -0.050354 | -0.027466 | 0.07782 | -0.004578 | 122.6349 | 122.5388 | -0.036621 | 122.525 | 122.5708 | 0.032043 | -0.018311 | 122.6532 | 122.5708 | -0.064087 | 122.6074 | 122.4884 | -0.082397 | -0.041199 | 122.5525 | 122.5708 | 122.5662 | -0.050354 | 122.525 | 122.5479 | 122.5708 | -0.018311
2361.0781 | 122.8363 | -122.58 | 0.009155 | -0.13855 | -0.0046441 | -0.057535 | 0.023125 | -0.01361 | -0.0090021 | -0.0067569 | -0.10757 | 0.024545 | 0.027102 | 0.022559 | 0.012311 | 0.014721 | 0.091553 | 0.11444 | 0.15106 | 0.086975 | -0.059509 | 0.10071 | -0.004578 | 0.11444 | 0.17395 | 0.041199 | -0.059509 | -0.050354 | 0.10529 | 0.041199 | 122.6807 | 122.5754 | -0.068664 | 122.6944 | 122.6669 | 0.091553 | 0.082398 | 122.6852 | 122.6212 | -0.068664 | 122.6944 | 122.6212 | 0 | -0.059509 | 122.5204 | 122.6715 | 122.731 | -0.013733 | 122.5204 | 122.5296 | 122.7539 | 0.032044
2362.7656 | 122.8867 | -122.5616 | 0.018311 | -0.046997 | -0.0063531 | -0.058176 | 0.021629 | -0.014678 | -0.0060113 | -0.0063297 | -0.069428 | 0.022623 | 0.02518 | 0.023413 | 0.012097 | 0.012157 | 0.073242 | 0.073242 | 0.1236 | 0.064087 | -0.050354 | 0.11444 | -0.013733 | 0.13733 | 0.15564 | 0.068665 | -0.091553 | -0.041199 | 0.091553 | 0.022888 | 122.6761 | 122.5479 | -0.068665 | 122.6349 | 122.6257 | 0.07782 | 0.054931 | 122.6532 | 122.5845 | -0.10986 | 122.699 | 122.6303 | 0.045777 | -0.05951 | 122.5113 | 122.6349 | 122.6852 | -0.032044 | 122.4701 | 122.5204 | 122.7173 | 0.004577
2364.4531 | 122.8683 | -122.5525 | 0 | 0.0064086 | -0.0020807 | -0.057749 | 0.022057 | -0.014892 | -0.0068659 | -0.0061161 | 0.060272 | 0.024545 | 0.025607 | 0.023627 | 0.015088 | 0.013653 | 0.018311 | 0.013733 | 0.07782 | 0.050354 | -0.064087 | 0.10071 | -0.013733 | 0.086975 | 0.07782 | 0.009155 | -0.054932 | -0.036621 | 0.09613 | 0.032043 | 122.6532 | 122.5388 | -0.064087 | 122.5662 | 122.6028 | 0.064087 | 0.018311 | 122.6486 | 122.5845 | -0.054932 | 122.6395 | 122.5616 | -0.022888 | -0.036621 | 122.4884 | 122.5708 | 122.6303 | -0.013733 | 122.4976 | 122.5159 | 122.6303 | 0.032043
2366.1562 | 122.7402 | -122.6212 | 0.027466 | -0.19196 | -0.0020807 | -0.059244 | 0.023338 | -0.013396 | -0.0021661 | -0.0071841 | -0.20676 | 0.025186 | 0.024966 | 0.023627 | 0.014661 | 0.01173 | 0.086975 | 0.054932 | 0.086975 | 0.059509 | -0.068665 | 0.086975 | -0.022888 | 0.045776 | 0.07782 | -0.041199 | -0.041199 | -0.036621 | 0.064087 | 0.004578 | 122.7081 | 122.5983 | -0.096131 | 122.6761 | 122.6807 | 0.082397 | 0.059509 | 122.6852 | 122.6257 | -0.068665 | 122.6669 | 122.58 | -0.045777 | -0.064087 | 122.5525 | 122.7081 | 122.7081 | -0.050354 | 122.58 | 122.5845 | 122.699 | -0.022888
2367.8906 | 122.8317 | -122.5845 | 0 | 0.159 | -0.0065667 | -0.060312 | 0.018639 | -0.016173 | -0.0036615 | -0.0076113 | 0.1442 | 0.025827 | 0.024112 | 0.021704 | 0.016584 | 0.011516 | 0.11444 | 0.073242 | 0.14191 | 0.073242 | -0.07782 | 0.10071 | 0.013733 | 0.13733 | 0.1236 | 0.013733 | -0.068665 | -0.068665 | 0.09613 | 0.018311 | 122.6852 | 122.5983 | -0.07782 | 122.6578 | 122.6578 | 0.059509 | 0.11444 | 122.6807 | 122.6028 | -0.068665 | 122.7219 | 122.5983 | -0.004578 | -0.068665 | 122.5067 | 122.699 | 122.7264 | 0.013733 | 122.5159 | 122.5159 | 122.7081 | 0.018311
2369.5938 | 122.8546 | -122.5983 | 0.009155 | -0.10803 | -0.0050715 | -0.058817 | 0.024406 | -0.013396 | -0.0047297 | -0.0061161 | -0.13046 | 0.024332 | 0.026462 | 0.022345 | 0.01402 | 0.010876 | 0.11444 | 0.10071 | 0.16022 | 0.082397 | -0.073242 | 0.10071 | 0.009155 | 0.14191 | 0.17853 | 0.064087 | -0.064087 | -0.059509 | 0.091553 | 0.027466 | 122.699 | 122.6074 | -0.082397 | 122.699 | 122.6807 | 0.073242 | 0.10529 | 122.6898 | 122.6257 | -0.073242 | 122.7402 | 122.6624 | 0.036621 | -0.068664 | 122.525 | 122.7127 | 122.7585 | 0 | 122.5342 | 122.5388 | 122.7768 | 0.018311
2371.2969 | 122.7631 | -122.5983 | 0.036621 | -0.069885 | -0.0012263 | -0.059244 | 0.017998 | -0.015533 | 0.0023199 | -0.0067569 | -0.16098 | 0.026254 | 0.024539 | 0.023413 | 0.018506 | 0.011516 | 0.091553 | 0.013733 | 0.045776 | 0.027466 | -0.036621 | 0.082397 | -0.013733 | 0.10071 | 0.082397 | -0.045776 | -0.041199 | -0.032043 | 0.068665 | -0.004578 | 122.6807 | 122.5845 | -0.073242 | 122.612 | 122.6257 | 0.041199 | 0.054932 | 122.6669 | 122.5937 | -0.07782 | 122.699 | 122.5525 | -0.041198 | -0.068664 | 122.5616 | 122.6898 | 122.644 | -0.050354 | 122.5571 | 122.5662 | 122.6807 | -0.041199
2373.0156 | 122.7448 | -122.644 | 0.022888 | 0.059815 | -0.0016535 | -0.059671 | 0.018211 | -0.013824 | 0.0023199 | -0.0065433 | 0.014496 | 0.025827 | 0.023684 | 0.022772 | 0.017438 | 0.01408 | 0.013733 | -0.059509 | -0.009155 | 0 | -0.018311 | 0.082397 | -0.032043 | 0 | -0.013733 | -0.1236 | -0.027466 | -0.009155 | 0.045776 | -0.004578 | 122.7264 | 122.612 | -0.041199 | 122.5845 | 122.644 | 0.032043 | -0.009155 | 122.6898 | 122.6395 | -0.050354 | 122.644 | 122.5204 | -0.11902 | -0.032043 | 122.6257 | 122.6578 | 122.6349 | -0.054931 | 122.6166 | 122.6349 | 122.6303 | -0.027466
2374.7031 | 122.7676 | -122.6257 | 0.018311 | -0.031738 | -0.00058528 | -0.059244 | 0.022057 | -0.015105 | 0.00061092 | -0.0041933 | -0.10757 | 0.024545 | 0.026248 | 0.022345 | 0.017224 | 0.013439 | 0.054932 | 0.022888 | 0.059509 | 0.045776 | -0.054932 | 0.07782 | -0.036621 | 0.073242 | 0.082397 | -0.027466 | -0.045776 | -0.041199 | 0.068665 | 0.013733 | 122.7036 | 122.5891 | -0.073243 | 122.6486 | 122.6715 | 0.082397 | 0.036621 | 122.6944 | 122.6395 | -0.064087 | 122.699 | 122.5983 | -0.041199 | -0.05951 | 122.5708 | 122.6807 | 122.6852 | -0.054932 | 122.58 | 122.5845 | 122.7081 | -0.004578
2376.4062 | 122.8271 | -122.5983 | 0.013733 | 0.090332 | -0.0044305 | -0.058817 | 0.020348 | -0.015319 | -0.0049433 | -0.0052615 | 0.16708 | 0.0254 | 0.025821 | 0.021918 | 0.013379 | 0.015789 | 0.068665 | 0.10071 | 0.1236 | 0.073242 | -0.07782 | 0.10071 | 0.004578 | 0.10529 | 0.10529 | 0.009155 | -0.07782 | -0.045776 | 0.09613 | 0.018311 | 122.699 | 122.6028 | -0.091553 | 122.699 | 122.6715 | 0.068664 | 0.054932 | 122.6944 | 122.6166 | -0.091553 | 122.7036 | 122.6074 | -0.009156 | -0.059509 | 122.5204 | 122.6669 | 122.7219 | -0.009155 | 122.5204 | 122.5525 | 122.7036 | 0.004578
2378.1094 | 122.7997 | -122.5891 | 0.045776 | -0.19196 | -0.0025079 | -0.058603 | 0.022484 | -0.014037 | -0.0030207 | -0.0061161 | -0.16861 | 0.024973 | 0.025393 | 0.02085 | 0.015515 | 0.0095937 | 0.013733 | -0.041199 | 0.004578 | 0.013733 | -0.032043 | 0.054932 | -0.050354 | 0.004578 | 0.018311 | -0.091553 | -0.036621 | -0.004578 | 0.050354 | 0.013733 | 122.644 | 122.5388 | -0.077819 | 122.5479 | 122.6028 | 0.064087 | -0.032043 | 122.6395 | 122.6028 | -0.082397 | 122.5937 | 122.4976 | -0.10529 | -0.050354 | 122.5571 | 122.6028 | 122.5937 | -0.09613 | 122.5525 | 122.5845 | 122.6074 | -0.032043
2379.8125 | 122.7814 | -122.612 | 0.013733 | -0.19958 | -0.0016535 | -0.059244 | 0.023125 | -0.014037 | -0.0036615 | -0.0078249 | -0.20676 | 0.024759 | 0.026462 | 0.023413 | 0.012097 | 0.012585 | -0.013733 | -0.036621 | 0.009155 | -0.013733 | -0.009155 | 0.07782 | -0.036621 | 0.009155 | 0.027466 | -0.091553 | -0.027466 | -0.027466 | 0.068665 | 0 | 122.6898 | 122.5754 | -0.022888 | 122.5754 | 122.5983 | 0.022888 | -0.027466 | 122.6807 | 122.612 | -0.041199 | 122.6212 | 122.5204 | -0.091553 | -0.041199 | 122.6028 | 122.5983 | 122.6212 | -0.050354 | 122.5845 | 122.5845 | 122.6395 | -0.013733
2381.5156 | 122.7905 | -122.5845 | 0.022888 | -0.15381 | -0.0018671 | -0.060312 | 0.02227 | -0.012755 | -0.0038751 | -0.0046207 | -0.16861 | 0.027109 | 0.028384 | 0.026831 | 0.013806 | 0.010662 | -0.004578 | -0.054932 | 0.018311 | 0 | -0.027466 | 0.068665 | -0.036621 | 0.004578 | 0.036621 | -0.082397 | -0.027466 | -0.022888 | 0.059509 | -0.027466 | 122.6532 | 122.5479 | -0.050354 | 122.5296 | 122.5845 | 0.036621 | -0.027466 | 122.644 | 122.5571 | -0.050354 | 122.5891 | 122.5021 | -0.054931 | -0.045776 | 122.5571 | 122.58 | 122.6028 | -0.059509 | 122.5571 | 122.5616 | 122.6212 | -0.050354
2383.2188 | 122.7951 | -122.612 | 0.018311 | -0.14618 | 5.5518e-05 | -0.060099 | 0.023338 | -0.011901 | -2.988e-05 | -0.0044071 | -0.17624 | 0.026041 | 0.02988 | 0.022772 | 0.014234 | 0.010876 | 0.004578 | -0.022888 | 0.032043 | 0.022888 | -0.041199 | 0.07782 | -0.022888 | 0.027466 | 0.045776 | -0.041199 | -0.041199 | -0.018311 | 0.07782 | 0.004578 | 122.6898 | 122.5891 | -0.05951 | 122.5891 | 122.6349 | 0.045776 | -0.013733 | 122.6898 | 122.6166 | -0.05951 | 122.6395 | 122.5708 | -0.045777 | -0.036622 | 122.5708 | 122.6166 | 122.644 | -0.041199 | 122.5708 | 122.5937 | 122.6578 | -0.013733
2384.9688 | 122.7585 | -122.6349 | 0.027466 | 0.067444 | -0.0042169 | -0.059458 | 0.019707 | -0.017028 | -0.00067088 | -0.0031253 | 0.075531 | 0.028391 | 0.026034 | 0.022772 | 0.017011 | 0.013866 | -0.018311 | -0.073242 | -0.022888 | -0.009155 | -0.018311 | 0.07782 | -0.041199 | -0.004578 | -0.004578 | -0.10529 | -0.041199 | -0.027466 | 0.054932 | 0.004578 | 122.7127 | 122.5937 | -0.045777 | 122.5616 | 122.6257 | 0.032044 | -0.045777 | 122.6898 | 122.6395 | -0.068665 | 122.6303 | 122.5296 | -0.10986 | -0.054932 | 122.6166 | 122.6166 | 122.612 | -0.068665 | 122.5937 | 122.6074 | 122.6303 | -0.022888
2386.6719 | 122.8043 | -122.5983 | 0.013733 | 0.13611 | -0.0052851 | -0.058176 | 0.017998 | -0.017455 | -0.0021661 | -0.0031253 | 0.09079 | 0.026254 | 0.028171 | 0.021918 | 0.017224 | 0.014507 | -0.022888 | -0.054932 | -0.004578 | -0.009155 | -0.032043 | 0.068665 | -0.041199 | 0.027466 | -0.013733 | -0.073242 | -0.054932 | -0.036621 | 0.068665 | -0.004578 | 122.6669 | 122.5571 | -0.045776 | 122.5433 | 122.5891 | 0.032044 | -0.036621 | 122.6669 | 122.5937 | -0.068665 | 122.6257 | 122.525 | -0.068664 | -0.050354 | 122.5662 | 122.5754 | 122.5937 | -0.054932 | 122.5433 | 122.5616 | 122.5845 | -0.018311
2388.375 | 122.7539 | -122.6166 | 0.027466 | 0.036926 | -0.0035761 | -0.060099 | 0.021843 | -0.015105 | -0.0019525 | -0.0046207 | 0.037384 | 0.0254 | 0.028598 | 0.022559 | 0.016156 | 0.012585 | 0.004578 | -0.045776 | 0.027466 | 0.004578 | -0.036621 | 0.068665 | -0.027466 | -0.013733 | -0.018311 | -0.11444 | -0.032043 | -0.041199 | 0.045776 | 0.004578 | 122.6852 | 122.5891 | -0.064087 | 122.5708 | 122.6212 | 0.032044 | -0.022888 | 122.6624 | 122.6212 | -0.059509 | 122.6028 | 122.5021 | -0.11902 | -0.068665 | 122.58 | 122.6212 | 122.644 | -0.054932 | 122.5845 | 122.5754 | 122.5983 | -0.022888
2390.0625 | 122.8043 | -122.6028 | 0.036621 | -0.13855 | -0.0027215 | -0.060099 | 0.022484 | -0.016601 | -0.0032343 | -0.0065433 | -0.15335 | 0.026682 | 0.027102 | 0.022345 | 0.013806 | 0.012157 | -0.009155 | -0.022888 | 0.009155 | 0.018311 | -0.027466 | 0.068665 | -0.050354 | -0.009155 | 0.036621 | -0.068665 | -0.041199 | -0.022888 | 0.082397 | 0.009155 | 122.6715 | 122.5525 | -0.064087 | 122.58 | 122.6212 | 0.068665 | -0.045776 | 122.6852 | 122.612 | -0.07782 | 122.5937 | 122.5342 | -0.07782 | -0.059509 | 122.5754 | 122.5937 | 122.612 | -0.086975 | 122.5616 | 122.58 | 122.6395 | -0.027466
2391.75 | 122.7722 | -122.6532 | 0.045776 | -0.16144 | -0.0016535 | -0.057322 | 0.026115 | -0.017455 | -0.0057977 | -0.0054751 | -0.22202 | 0.024973 | 0.02988 | 0.023413 | 0.009534 | 0.013653 | 0 | 0 | 0.073242 | 0.018311 | -0.050354 | 0.068665 | -0.045776 | -0.009155 | 0.045776 | -0.064087 | -0.022888 | -0.013733 | 0.064087 | -0.009155 | 122.7219 | 122.6074 | -0.09613 | 122.6532 | 122.6715 | 0.064087 | -0.045776 | 122.7173 | 122.644 | -0.068664 | 122.644 | 122.5891 | -0.054932 | -0.059509 | 122.6028 | 122.6532 | 122.7264 | -0.091552 | 122.6303 | 122.6395 | 122.699 | -0.054931
2393.4375 | 122.7585 | -122.612 | 0.036621 | -0.069885 | -0.0010125 | -0.061167 | 0.020561 | -0.013396 | -0.00088448 | -0.0048343 | -0.054169 | 0.026254 | 0.028598 | 0.022345 | 0.017652 | 0.01408 | 0.054932 | 0.022888 | 0.050354 | 0.032043 | -0.041199 | 0.07782 | -0.041199 | 0.054932 | 0.054932 | -0.036621 | -0.041199 | -0.018311 | 0.073242 | 0.004578 | 122.6898 | 122.5708 | -0.07782 | 122.6349 | 122.644 | 0.073242 | 0.018311 | 122.6852 | 122.6166 | -0.07782 | 122.6669 | 122.5754 | -0.041199 | -0.054932 | 122.5708 | 122.6669 | 122.6624 | -0.07782 | 122.5708 | 122.5937 | 122.6669 | -0.032043
2395.125 | 122.7585 | -122.612 | 0.054932 | 0.17426 | -0.0037897 | -0.061167 | 0.020561 | -0.015105 | 0.00082452 | -0.0039797 | 0.029755 | 0.026468 | 0.026675 | 0.021277 | 0.01872 | 0.012585 | -0.018311 | -0.022888 | 0 | 0.004578 | -0.032043 | 0.07782 | -0.036621 | -0.018311 | -0.009155 | -0.11444 | -0.064087 | -0.018311 | 0.054932 | -0.004578 | 122.6898 | 122.5754 | -0.086975 | 122.5891 | 122.6166 | 0.041199 | -0.073243 | 122.6669 | 122.6074 | -0.11902 | 122.5937 | 122.4976 | -0.10986 | -0.073243 | 122.58 | 122.5937 | 122.612 | -0.091553 | 122.5479 | 122.5937 | 122.6028 | -0.05951
2396.8125 | 122.7905 | -122.5937 | 0.032043 | 0.10559 | -0.0037897 | -0.058817 | 0.018211 | -0.017028 | -0.0038751 | -0.0050479 | 0.098419 | 0.026468 | 0.026889 | 0.023199 | 0.018079 | 0.013439 | -0.022888 | -0.07782 | -0.013733 | 0 | -0.018311 | 0.073242 | -0.022888 | 0.009155 | -0.032043 | -0.09613 | -0.027466 | -0.022888 | 0.07782 | -0.004578 | 122.6669 | 122.5708 | -0.050354 | 122.5159 | 122.5937 | 0.022888 | -0.054931 | 122.6715 | 122.5891 | -0.059509 | 122.6028 | 122.4976 | -0.091552 | -0.054931 | 122.5754 | 122.5708 | 122.58 | -0.054931 | 122.5662 | 122.5708 | 122.5616 | -0.036621
2398.5 | 122.7722 | -122.5891 | 0.032043 | -0.031738 | -0.0046441 | -0.059244 | 0.019066 | -0.016173 | -0.0030207 | -0.0046207 | -0.092316 | 0.023904 | 0.027102 | 0.023199 | 0.014234 | 0.013012 | 0.041199 | 0.032043 | 0.054932 | 0.036621 | -0.041199 | 0.10529 | -0.036621 | 0.064087 | 0.068665 | -0.032043 | -0.050354 | -0.018311 | 0.073242 | 0.009155 | 122.6944 | 122.5525 | -0.073242 | 122.6212 | 122.6257 | 0.073242 | 0.009156 | 122.6624 | 122.5983 | -0.082397 | 122.6532 | 122.5571 | -0.041198 | -0.050354 | 122.5479 | 122.6303 | 122.644 | -0.068664 | 122.5388 | 122.5708 | 122.6578 | -0.022888
2400.2188 | 122.8317 | -122.5845 | 0.009155 | 0.059815 | -0.0069941 | -0.05839 | 0.018639 | -0.014892 | -0.011565 | -0.0071841 | 0.13657 | 0.022836 | 0.026248 | 0.020422 | 0.012952 | 0.016003 | 0.036621 | 0.041199 | 0.10071 | 0.032043 | -0.073242 | 0.10071 | 0.013733 | 0.064087 | 0.068665 | -0.004578 | -0.07782 | -0.045776 | 0.10529 | 0.022888 | 122.6852 | 122.5983 | -0.082397 | 122.6257 | 122.6166 | 0.01831 | 0.027466 | 122.6898 | 122.6074 | -0.086975 | 122.6486 | 122.58 | -0.027466 | -0.054931 | 122.5113 | 122.6212 | 122.6852 | 0.004578 | 122.5067 | 122.5388 | 122.6532 | 0.013733
2401.9531 | 122.7997 | -122.612 | 0.036621 | -0.18433 | -0.0016535 | -0.058176 | 0.025261 | -0.012755 | -0.0025935 | -0.0052615 | -0.16098 | 0.027322 | 0.031161 | 0.021277 | 0.014661 | 0.011303 | 0 | -0.036621 | 0.009155 | 0 | -0.018311 | 0.082397 | -0.041199 | -0.004578 | 0.027466 | -0.082397 | -0.022888 | -0.013733 | 0.064087 | 0.004578 | 122.6944 | 122.5708 | -0.054932 | 122.5754 | 122.612 | 0.041199 | -0.036621 | 122.6761 | 122.6166 | -0.059509 | 122.6074 | 122.5296 | -0.086975 | -0.050354 | 122.5937 | 122.612 | 122.6212 | -0.07782 | 122.5891 | 122.5983 | 122.6395 | -0.032043
2403.6562 | 122.7356 | -122.6303 | 0.041199 | -0.024109 | -0.0014399 | -0.059244 | 0.020775 | -0.016601 | -0.00067088 | -0.0054751 | -0.046539 | 0.027322 | 0.027102 | 0.021704 | 0.018293 | 0.01173 | 0.027466 | -0.013733 | 0.027466 | -0.022888 | -0.022888 | 0.082397 | -0.036621 | 0.018311 | -0.009155 | -0.086975 | -0.036621 | -0.018311 | 0.059509 | 0 | 122.7127 | 122.5937 | -0.064087 | 122.6166 | 122.6074 | 0.013733 | -0.013733 | 122.6898 | 122.6303 | -0.07782 | 122.6486 | 122.5433 | -0.086975 | -0.05951 | 122.6074 | 122.6578 | 122.6578 | -0.07782 | 122.5937 | 122.612 | 122.6212 | -0.041199
2405.3438 | 122.8912 | -122.5708 | 0 | 0.14374 | -0.0040033 | -0.059671 | 0.016502 | -0.016173 | -0.0043023 | -0.0031253 | 0.12131 | 0.027536 | 0.024966 | 0.02149 | 0.015729 | 0.012585 | 0.045776 | -0.018311 | 0.045776 | 0.032043 | -0.059509 | 0.091553 | -0.022888 | 0.082397 | 0.068665 | -0.009155 | -0.064087 | -0.054932 | 0.09613 | 0.018311 | 122.6624 | 122.5479 | -0.059509 | 122.5525 | 122.6028 | 0.054931 | 0.045776 | 122.6669 | 122.5891 | -0.064087 | 122.6532 | 122.5616 | -0.027466 | -0.054932 | 122.5113 | 122.6166 | 122.6166 | -0.022888 | 122.5067 | 122.5159 | 122.6395 | 0.018311
2407.0469 | 122.8958 | -122.5937 | -0.009155 | 0.029297 | -0.0054987 | -0.054758 | 0.023125 | -0.013824 | -0.010925 | -0.0056887 | 0.075531 | 0.025613 | 0.027743 | 0.022131 | 0.012097 | 0.013866 | 0.009155 | 0 | 0.07782 | 0.050354 | -0.059509 | 0.091553 | -0.009155 | 0.07782 | 0.07782 | 0.004578 | -0.068665 | -0.073242 | 0.086975 | 0.009155 | 122.6852 | 122.5845 | -0.050354 | 122.5937 | 122.644 | 0.059509 | 0.01831 | 122.6807 | 122.6028 | -0.05951 | 122.6715 | 122.5983 | -0.004577 | -0.064087 | 122.5342 | 122.6028 | 122.6715 | 0 | 122.525 | 122.5204 | 122.6715 | 0.01831
2408.7344 | 122.8958 | -122.58 | 0.009155 | -0.062256 | -0.0050715 | -0.058603 | 0.024193 | -0.016601 | -0.0075067 | -0.0086795 | -0.054169 | 0.024545 | 0.029025 | 0.019141 | 0.012097 | 0.012798 | 0.09613 | 0.064087 | 0.13733 | 0.073242 | -0.082397 | 0.10529 | -0.004578 | 0.13275 | 0.15106 | 0.064087 | -0.068665 | -0.036621 | 0.11444 | 0.045776 | 122.6852 | 122.5754 | -0.091552 | 122.644 | 122.6532 | 0.07782 | 0.086975 | 122.6944 | 122.6257 | -0.07782 | 122.7127 | 122.644 | 0.018311 | -0.045776 | 122.4976 | 122.6761 | 122.7173 | -0.013733 | 122.5113 | 122.5433 | 122.731 | 0.036621
2410.4375 | 122.7585 | -122.644 | 0.045776 | -0.21484 | -0.0042169 | -0.059031 | 0.022911 | -0.01361 | -0.0023797 | -0.0076113 | -0.19913 | 0.028177 | 0.027957 | 0.019781 | 0.015729 | 0.010235 | 0 | -0.045776 | 0.022888 | -0.009155 | -0.027466 | 0.064087 | -0.045776 | 0.009155 | 0.027466 | -0.086975 | -0.050354 | -0.009155 | 0.054932 | -0.009155 | 122.7081 | 122.5983 | -0.073242 | 122.5983 | 122.6349 | 0.036621 | -0.045776 | 122.699 | 122.6349 | -0.09613 | 122.6532 | 122.5571 | -0.07782 | -0.054931 | 122.6166 | 122.644 | 122.6669 | -0.091552 | 122.5937 | 122.6349 | 122.6715 | -0.054931
2412.1406 | 122.8592 | -122.5754 | 0.004578 | 0.15137 | -0.0031489 | -0.059458 | 0.016716 | -0.014037 | -0.0021661 | -0.0073977 | 0.15182 | 0.025827 | 0.026248 | 0.022772 | 0.018293 | 0.014721 | 0.10071 | 0.07782 | 0.12817 | 0.10071 | -0.086975 | 0.1236 | 0.009155 | 0.1236 | 0.1236 | 0.032043 | -0.10071 | -0.068665 | 0.10071 | 0.041199 | 122.699 | 122.5845 | -0.091553 | 122.6532 | 122.6761 | 0.091553 | 0.09613 | 122.6761 | 122.6166 | -0.10529 | 122.699 | 122.6074 | -0.009156 | -0.073243 | 122.4884 | 122.6761 | 122.7036 | 0.004577 | 122.4747 | 122.5067 | 122.699 | 0.036621
2413.8906 | 122.7493 | -122.6395 | 0.036621 | -0.21484 | -0.0022943 | -0.057108 | 0.023766 | -0.01361 | -0.0051569 | -0.0056887 | -0.1915 | 0.025613 | 0.028171 | 0.021277 | 0.012952 | 0.013012 | 0.054932 | 0.045776 | 0.091553 | 0.050354 | -0.050354 | 0.082397 | -0.036621 | 0.041199 | 0.036621 | -0.054932 | -0.050354 | -0.027466 | 0.082397 | -0.004578 | 122.7219 | 122.6028 | -0.086975 | 122.6852 | 122.6898 | 0.086975 | 0.018311 | 122.7219 | 122.6349 | -0.086975 | 122.6807 | 122.5845 | -0.050354 | -0.064087 | 122.5891 | 122.6944 | 122.731 | -0.073242 | 122.5891 | 122.612 | 122.6761 | -0.041199
2415.5781 | 122.7493 | -122.6212 | 0.032043 | -0.039368 | -0.0010125 | -0.060099 | 0.01928 | -0.014892 | 0.0029607 | -0.0073977 | -0.1152 | 0.028604 | 0.02988 | 0.022986 | 0.015729 | 0.01173 | 0.073242 | 0.027466 | 0.07782 | 0.032043 | -0.045776 | 0.082397 | -0.022888 | 0.064087 | 0.059509 | -0.054932 | -0.045776 | -0.032043 | 0.073242 | 0 | 122.7036 | 122.5983 | -0.077819 | 122.6486 | 122.6532 | 0.054931 | 0.041199 | 122.6944 | 122.6212 | -0.077819 | 122.6852 | 122.5662 | -0.054932 | -0.064086 | 122.5754 | 122.6944 | 122.699 | -0.054931 | 122.5754 | 122.5891 | 122.6807 | -0.032043
2417.2656 | 122.8958 | -122.5845 | -0.009155 | 0.14374 | -0.0052851 | -0.06138 | 0.016075 | -0.012328 | -0.0030207 | -0.0041933 | 0.25101 | 0.030099 | 0.02988 | 0.02085 | 0.016797 | 0.015148 | 0.064087 | 0.022888 | 0.091553 | 0.041199 | -0.068665 | 0.1236 | -0.004578 | 0.11444 | 0.11902 | 0.004578 | -0.064087 | -0.059509 | 0.09613 | 0.045776 | 122.7081 | 122.58 | -0.05951 | 122.6074 | 122.6257 | 0.045777 | 0.073242 | 122.6807 | 122.6303 | -0.054932 | 122.699 | 122.5891 | -0.041198 | -0.050354 | 122.5159 | 122.6486 | 122.6761 | 0.004577 | 122.5204 | 122.525 | 122.7036 | 0.054931
2418.9844 | 122.8821 | -122.58 | -0.004578 | 0.021668 | -0.0057123 | -0.058603 | 0.019707 | -0.015105 | -0.0096429 | -0.0056887 | 0.037384 | 0.03074 | 0.032443 | 0.022559 | 0.012952 | 0.015575 | 0.009155 | 0.032043 | 0.07782 | 0.045776 | -0.054932 | 0.09613 | -0.009155 | 0.068665 | 0.073242 | 0 | -0.064087 | -0.041199 | 0.086975 | 0.022888 | 122.6761 | 122.5708 | -0.050354 | 122.612 | 122.6257 | 0.054931 | 0.013733 | 122.6669 | 122.6028 | -0.059509 | 122.6486 | 122.58 | -0.022888 | -0.036621 | 122.525 | 122.5891 | 122.6578 | -0.004577 | 122.5159 | 122.5388 | 122.6532 | 0.027466
2420.6719 | 122.7631 | -122.6166 | 0.050354 | -0.13855 | -0.0014399 | -0.056467 | 0.023766 | -0.015746 | -0.0049433 | -0.0067569 | -0.13809 | 0.034372 | 0.034793 | 0.020422 | 0.012525 | 0.012157 | 0.086975 | 0.082397 | 0.12817 | 0.082397 | -0.082397 | 0.11902 | -0.013733 | 0.10071 | 0.13733 | -0.004578 | -0.059509 | -0.054932 | 0.10986 | 0.027466 | 122.7356 | 122.6028 | -0.13275 | 122.699 | 122.699 | 0.09613 | 0.036621 | 122.7264 | 122.644 | -0.10986 | 122.7173 | 122.612 | -0.032044 | -0.10529 | 122.5342 | 122.7036 | 122.7448 | -0.064087 | 122.5571 | 122.5616 | 122.7539 | -0.022888
2422.3906 | 122.8043 | -122.6028 | 0.032043 | -0.12329 | 0.00048272 | -0.057962 | 0.02227 | -0.011687 | 0.00061092 | -0.0048343 | -0.19913 | 0.036508 | 0.036502 | 0.022772 | 0.016797 | 0.010662 | 0.022888 | -0.054932 | 0.018311 | 0.032043 | -0.027466 | 0.073242 | -0.041199 | 0.036621 | 0.036621 | -0.068665 | -0.032043 | -0.022888 | 0.054932 | 0.004578 | 122.6761 | 122.5616 | -0.059509 | 122.5479 | 122.6349 | 0.073242 | -0.009155 | 122.6578 | 122.6074 | -0.064086 | 122.6395 | 122.5342 | -0.073243 | -0.054931 | 122.5754 | 122.6257 | 122.6212 | -0.073242 | 122.5708 | 122.58 | 122.6395 | -0.027465
2424.0781 | 122.8683 | -122.5845 | 0.009155 | 0.082703 | -0.0010125 | -0.059244 | 0.019493 | -0.015319 | -0.00024348 | -0.0052615 | 0.10605 | 0.038004 | 0.03757 | 0.022772 | 0.017438 | 0.011516 | 0.022888 | -0.050354 | 0.018311 | 0 | -0.022888 | 0.068665 | -0.027466 | 0.050354 | 0.022888 | -0.064087 | -0.050354 | -0.027466 | 0.073242 | 0.009155 | 122.6532 | 122.5571 | -0.032043 | 122.5342 | 122.5845 | 0.027466 | 0.013733 | 122.6578 | 122.5937 | -0.059509 | 122.6349 | 122.5204 | -0.073242 | -0.036621 | 122.5616 | 122.6074 | 122.6028 | -0.036621 | 122.5342 | 122.5571 | 122.6074 | 0
2425.7656 | 122.8683 | -122.5616 | 0.013733 | 0.067444 | -0.0052851 | -0.058176 | 0.017571 | -0.014251 | -0.0043023 | -0.0050479 | 0.16708 | 0.03779 | 0.03522 | 0.021918 | 0.017652 | 0.013866 | 0.091553 | 0.07782 | 0.10986 | 0.073242 | -0.068665 | 0.11444 | 0.009155 | 0.14191 | 0.11444 | 0.022888 | -0.07782 | -0.059509 | 0.10986 | 0.041199 | 122.6761 | 122.5708 | -0.082398 | 122.6395 | 122.6349 | 0.064087 | 0.07782 | 122.6715 | 122.6028 | -0.091553 | 122.7036 | 122.5845 | -0.018311 | -0.073242 | 122.493 | 122.6532 | 122.6715 | -0.004578 | 122.4838 | 122.5021 | 122.6761 | 0.027466
2427.4688 | 122.7951 | -122.58 | 0.036621 | -0.13855 | -0.0031489 | -0.059031 | 0.020775 | -0.016387 | -0.0023797 | -0.0063297 | -0.17624 | 0.037149 | 0.03757 | 0.023413 | 0.01637 | 0.013012 | 0.013733 | -0.041199 | 0.013733 | 0.004578 | -0.041199 | 0.07782 | -0.032043 | 0.013733 | 0.045776 | -0.073242 | -0.027466 | -0.013733 | 0.054932 | 0 | 122.6578 | 122.5479 | -0.07782 | 122.5388 | 122.5845 | 0.036621 | -0.022888 | 122.6349 | 122.58 | -0.064087 | 122.5937 | 122.5067 | -0.073242 | -0.050354 | 122.5388 | 122.5937 | 122.5937 | -0.068664 | 122.5525 | 122.5662 | 122.6257 | -0.036621
2429.1719 | 122.7264 | -122.6074 | 0.022888 | -0.024109 | -0.0040033 | -0.059885 | 0.016716 | -0.015105 | 0.00082452 | -0.0050479 | -0.023651 | 0.039713 | 0.036288 | 0.021704 | 0.018079 | 0.010235 | 0.045776 | 0.018311 | 0.032043 | 0.018311 | -0.018311 | 0.068665 | -0.032043 | 0.032043 | 0.018311 | -0.073242 | -0.036621 | -0.018311 | 0.086975 | -0.018311 | 122.6761 | 122.5754 | -0.041199 | 122.6257 | 122.6257 | 0.050354 | 0.022888 | 122.6944 | 122.5891 | -0.059509 | 122.6395 | 122.5342 | -0.054931 | -0.041199 | 122.5891 | 122.6532 | 122.6395 | -0.054931 | 122.5708 | 122.5891 | 122.6257 | -0.041199
2430.9219 | 122.7448 | -122.612 | 0.032043 | -0.13855 | -0.00058528 | -0.059031 | 0.024834 | -0.015746 | -0.0087885 | -0.0039797 | -0.15335 | 0.039499 | 0.041202 | 0.022986 | 0.011029 | 0.012585 | 0.050354 | 0.082397 | 0.12817 | 0.07782 | -0.054932 | 0.09613 | -0.032043 | 0.059509 | 0.091553 | -0.022888 | -0.045776 | -0.032043 | 0.091553 | 0.018311 | 122.7081 | 122.58 | -0.086975 | 122.6944 | 122.6898 | 0.10986 | 0.018311 | 122.7036 | 122.6303 | -0.077819 | 122.6715 | 122.5891 | -0.041199 | -0.064086 | 122.5571 | 122.6624 | 122.7402 | -0.064086 | 122.5662 | 122.58 | 122.7036 | -0.013732
2432.6094 | 122.8226 | -122.6028 | 0.013733 | 0.14374 | -0.0037897 | -0.061594 | 0.016716 | -0.012755 | -0.0025935 | -0.0046207 | 0.08316 | 0.03779 | 0.034366 | 0.02384 | 0.01637 | 0.010235 | -0.004578 | -0.064087 | -0.013733 | 0 | -0.032043 | 0.086975 | -0.032043 | 0.032043 | -0.013733 | -0.086975 | -0.045776 | 0 | 0.073242 | 0.009155 | 122.6898 | 122.5708 | -0.045776 | 122.5388 | 122.6028 | 0.032043 | -0.018311 | 122.6761 | 122.612 | -0.059509 | 122.6349 | 122.5159 | -0.09613 | -0.013733 | 122.5708 | 122.5983 | 122.5891 | -0.045776 | 122.5571 | 122.6028 | 122.5891 | -0.004578
2434.3281 | 122.8958 | -122.5708 | 0.004578 | -0.0012209 | -0.0037897 | -0.057749 | 0.021202 | -0.015319 | -0.010497 | -0.0076113 | 0.022125 | 0.035654 | 0.036715 | 0.021277 | 0.01167 | 0.013439 | 0.027466 | 0.050354 | 0.10529 | 0.045776 | -0.054932 | 0.09613 | -0.013733 | 0.10529 | 0.13733 | 0.027466 | -0.073242 | -0.045776 | 0.10529 | 0.027466 | 122.6669 | 122.5571 | -0.05951 | 122.6212 | 122.6166 | 0.059509 | 0.022888 | 122.6761 | 122.5983 | -0.07782 | 122.6761 | 122.5983 | 0 | -0.050354 | 122.5159 | 122.5983 | 122.6761 | -0.018311 | 122.4976 | 122.525 | 122.7081 | 0.022888
2436.0469 | 122.7493 | -122.612 | 0.050354 | -0.22247 | -0.0010125 | -0.059031 | 0.023125 | -0.015746 | -0.0040887 | -0.0056887 | -0.17624 | 0.041208 | 0.039065 | 0.021277 | 0.013593 | 0.010662 | -0.009155 | -0.009155 | 0.004578 | 0 | -0.022888 | 0.086975 | -0.041199 | 0.018311 | 0.022888 | -0.073242 | -0.022888 | 0 | 0.054932 | -0.009155 | 122.699 | 122.5708 | -0.073242 | 122.6028 | 122.612 | 0.041199 | -0.059509 | 122.6669 | 122.6028 | -0.073242 | 122.6303 | 122.5388 | -0.064087 | -0.050354 | 122.5891 | 122.6028 | 122.6166 | -0.091553 | 122.5891 | 122.612 | 122.6349 | -0.059509
2437.7656 | 122.7676 | -122.6212 | 0.032043 | 0.075073 | -0.0029351 | -0.059671 | 0.018639 | -0.014251 | 0.00039732 | -0.0052615 | 0.075531 | 0.040781 | 0.037356 | 0.021063 | 0.017865 | 0.013866 | -0.004578 | -0.07782 | -0.018311 | -0.004578 | -0.018311 | 0.064087 | -0.045776 | 0.022888 | -0.022888 | -0.11444 | -0.041199 | 0 | 0.059509 | -0.018311 | 122.6852 | 122.5754 | -0.050354 | 122.5433 | 122.6166 | 0.041198 | -0.036621 | 122.6807 | 122.6028 | -0.073242 | 122.644 | 122.5067 | -0.09613 | -0.032043 | 122.6028 | 122.6166 | 122.6028 | -0.077819 | 122.58 | 122.6212 | 122.5983 | -0.050354
2439.4844 | 122.8592 | -122.5708 | 0.032043 | -0.1004 | -0.0042169 | -0.057108 | 0.023766 | -0.017028 | -0.0092157 | -0.0050479 | -0.084686 | 0.038004 | 0.039493 | 0.019354 | 0.012097 | 0.013439 | 0.10529 | 0.1236 | 0.16479 | 0.091553 | -0.059509 | 0.10986 | -0.013733 | 0.10986 | 0.17395 | 0.064087 | -0.054932 | -0.041199 | 0.10071 | 0.036621 | 122.6807 | 122.5571 | -0.091552 | 122.6944 | 122.6624 | 0.10529 | 0.073243 | 122.6715 | 122.6074 | -0.086975 | 122.6807 | 122.6349 | 0.027466 | -0.073242 | 122.5113 | 122.6761 | 122.7356 | -0.045776 | 122.5159 | 122.5296 | 122.7448 | 0.004578
2441.1719 | 122.7768 | -122.5845 | 0.027466 | -0.092773 | -0.0025079 | -0.058817 | 0.018425 | -0.014037 | 0.00082452 | -0.0061161 | -0.1152 | 0.04313 | 0.03992 | 0.021277 | 0.01637 | 0.010021 | 0.07782 | 0.018311 | 0.045776 | 0.045776 | -0.041199 | 0.068665 | -0.045776 | 0.082397 | 0.059509 | -0.041199 | -0.036621 | -0.018311 | 0.073242 | -0.018311 | 122.6532 | 122.5388 | -0.068665 | 122.6028 | 122.6303 | 0.091552 | 0.050354 | 122.6578 | 122.5662 | -0.064087 | 122.6669 | 122.5433 | -0.022888 | -0.045777 | 122.5433 | 122.6624 | 122.6303 | -0.073242 | 122.5479 | 122.5662 | 122.644 | -0.045777
2442.9219 | 122.7539 | -122.612 | 0.041199 | -0.13092 | -0.0018671 | -0.058817 | 0.024834 | -0.013183 | -0.0068659 | -0.0044071 | -0.12283 | 0.038858 | 0.040774 | 0.02149 | 0.012738 | 0.01173 | 0.07782 | 0.082397 | 0.12817 | 0.082397 | -0.064087 | 0.091553 | -0.018311 | 0.086975 | 0.1236 | 0.004578 | -0.054932 | -0.059509 | 0.091553 | 0.018311 | 122.7036 | 122.5937 | -0.10529 | 122.6944 | 122.6944 | 0.10071 | 0.036621 | 122.7036 | 122.6303 | -0.096131 | 122.699 | 122.6166 | -0.013733 | -0.10071 | 122.5479 | 122.6898 | 122.7402 | -0.05951 | 122.5571 | 122.5525 | 122.7356 | -0.022888
2444.6094 | 122.7814 | -122.5983 | 0.032043 | -0.19196 | 0.0011237 | -0.061594 | 0.023552 | -0.014037 | -0.0010981 | -0.0061161 | -0.18387 | 0.041849 | 0.040988 | 0.024054 | 0.015302 | 0.010662 | 0.013733 | -0.041199 | 0 | 0.009155 | -0.036621 | 0.073242 | -0.036621 | 0.018311 | 0.032043 | -0.082397 | -0.036621 | -0.027466 | 0.068665 | -0.004578 | 122.6715 | 122.5616 | -0.068664 | 122.5571 | 122.6074 | 0.045776 | -0.01831 | 122.6669 | 122.5937 | -0.068664 | 122.6166 | 122.5159 | -0.077819 | -0.059509 | 122.5616 | 122.612 | 122.5983 | -0.068664 | 122.5616 | 122.5708 | 122.6303 | -0.036621
2446.3281 | 122.8821 | -122.5479 | 0.013733 | 0.014038 | -0.0027215 | -0.057535 | 0.01928 | -0.014464 | -0.0064387 | -0.0071841 | 0.0068663 | 0.04014 | 0.040561 | 0.02085 | 0.010816 | 0.014721 | 0.041199 | 0.045776 | 0.091553 | 0.045776 | -0.059509 | 0.10071 | -0.027466 | 0.09613 | 0.11902 | 0.032043 | -0.059509 | -0.041199 | 0.09613 | 0.018311 | 122.6486 | 122.5204 | -0.073242 | 122.5937 | 122.5937 | 0.073242 | 0.027466 | 122.644 | 122.5662 | -0.073242 | 122.644 | 122.58 | 0.013732 | -0.054932 | 122.4884 | 122.5891 | 122.6395 | -0.041199 | 122.4884 | 122.5067 | 122.6669 | 0.004578
2448.0312 | 122.7676 | -122.5845 | 0.045776 | -0.13855 | -0.0012263 | -0.059671 | 0.019066 | -0.015533 | -0.00088448 | -0.0052615 | -0.17624 | 0.041635 | 0.040988 | 0.022986 | 0.015943 | 0.011303 | 0.018311 | -0.036621 | 0.022888 | 0.027466 | -0.032043 | 0.07782 | -0.041199 | 0.036621 | 0.050354 | -0.068665 | -0.027466 | -0.013733 | 0.059509 | 0 | 122.6624 | 122.5433 | -0.077819 | 122.5479 | 122.612 | 0.068665 | -0.027465 | 122.644 | 122.5845 | -0.073242 | 122.6212 | 122.5159 | -0.068665 | -0.059509 | 122.5525 | 122.6028 | 122.6074 | -0.086975 | 122.5571 | 122.5708 | 122.6349 | -0.045776
2449.7344 | 122.7631 | -122.6166 | 0.050354 | 0.067444 | -0.0025079 | -0.057108 | 0.013512 | -0.015319 | -2.988e-05 | -0.0052615 | 0.067902 | 0.04313 | 0.043338 | 0.023627 | 0.018506 | 0.012585 | -0.004578 | -0.054932 | -0.009155 | 0.004578 | -0.032043 | 0.082397 | -0.032043 | 0.018311 | -0.018311 | -0.10529 | -0.050354 | -0.018311 | 0.068665 | 0.004578 | 122.699 | 122.5845 | -0.082397 | 122.5616 | 122.6212 | 0.036621 | -0.054932 | 122.6852 | 122.6212 | -0.10071 | 122.6349 | 122.5113 | -0.10986 | -0.068665 | 122.5845 | 122.612 | 122.6074 | -0.082397 | 122.5662 | 122.5983 | 122.5983 | -0.045776
2451.4219 | 122.7127 | -122.5983 | 0.045776 | -0.016479 | -0.00058528 | -0.060526 | 0.019066 | -0.01361 | -0.0017389 | -0.0033389 | -0.0083922 | 0.045694 | 0.042911 | 0.02085 | 0.016797 | 0.013225 | 0.018311 | 0 | 0.036621 | 0.027466 | -0.022888 | 0.082397 | -0.027466 | 0.018311 | 0.009155 | -0.086975 | -0.032043 | -0.032043 | 0.082397 | -0.004578 | 122.6807 | 122.5708 | -0.068664 | 122.5983 | 122.6257 | 0.054932 | -0.027465 | 122.6807 | 122.5937 | -0.077819 | 122.6166 | 122.5113 | -0.082397 | -0.077819 | 122.5754 | 122.6166 | 122.6349 | -0.073242 | 122.5662 | 122.5662 | 122.6074 | -0.050354
2453.125 | 122.8455 | -122.5708 | 0.022888 | 0.021668 | -0.0033625 | -0.059671 | 0.022697 | -0.016387 | -0.0083613 | -0.0046207 | 0.10605 | 0.043558 | 0.044406 | 0.021063 | 0.010389 | 0.015148 | 0.032043 | 0.018311 | 0.09613 | 0.036621 | -0.059509 | 0.10071 | -0.004578 | 0.059509 | 0.07782 | -0.018311 | -0.045776 | -0.041199 | 0.09613 | 0.009155 | 122.6715 | 122.5662 | -0.082397 | 122.5891 | 122.6074 | 0.041199 | 0.009155 | 122.6669 | 122.58 | -0.068664 | 122.6303 | 122.5525 | -0.027466 | -0.064087 | 122.5113 | 122.6028 | 122.6669 | -0.027466 | 122.525 | 122.5296 | 122.6486 | -0.013733
2454.8281 | 122.7356 | -122.6166 | 0.045776 | -0.19196 | -0.0025079 | -0.060312 | 0.021843 | -0.014464 | -0.0064387 | -0.0080387 | -0.16098 | 0.045267 | 0.045474 | 0.021918 | 0.013379 | 0.011944 | 0.073242 | 0.07782 | 0.11444 | 0.064087 | -0.064087 | 0.10071 | 0 | 0.07782 | 0.13275 | 0.009155 | -0.068665 | -0.032043 | 0.07782 | 0.027466 | 122.7173 | 122.6166 | -0.10986 | 122.6944 | 122.6807 | 0.064087 | 0.027466 | 122.6944 | 122.644 | -0.11444 | 122.6944 | 122.6257 | -0.018311 | -0.077819 | 122.5525 | 122.6898 | 122.731 | -0.045776 | 122.5479 | 122.5845 | 122.7493 | -0.01831
2456.5312 | 122.7768 | -122.6074 | 0.027466 | -0.1004 | 0.00026912 | -0.059458 | 0.020134 | -0.012542 | 0.00039732 | -0.0059023 | -0.10757 | 0.046976 | 0.045047 | 0.02149 | 0.016584 | 0.0091665 | 0.07782 | 0.013733 | 0.050354 | 0.032043 | -0.036621 | 0.07782 | -0.041199 | 0.054932 | 0.073242 | -0.032043 | -0.041199 | -0.018311 | 0.073242 | 0.009155 | 122.6852 | 122.5662 | -0.064087 | 122.6212 | 122.6395 | 0.073242 | 0.050354 | 122.6807 | 122.6166 | -0.068665 | 122.6624 | 122.5754 | -0.041198 | -0.045777 | 122.5708 | 122.6852 | 122.6578 | -0.068665 | 122.5662 | 122.5891 | 122.6807 | -0.018311
2458.2344 | 122.7951 | -122.5891 | 0.041199 | -0.13855 | -0.0048579 | -0.060312 | 0.01928 | -0.014892 | -0.0038751 | -0.0059023 | -0.18387 | 0.048257 | 0.049106 | 0.02085 | 0.016584 | 0.010662 | 0 | -0.022888 | 0.018311 | 0.022888 | -0.036621 | 0.054932 | -0.036621 | 0.041199 | 0.050354 | -0.059509 | -0.027466 | -0.027466 | 0.068665 | -0.004578 | 122.644 | 122.5525 | -0.07782 | 122.5662 | 122.612 | 0.059509 | -0.041199 | 122.6578 | 122.5845 | -0.068665 | 122.6303 | 122.5296 | -0.054931 | -0.068665 | 122.5525 | 122.5891 | 122.6074 | -0.07782 | 122.5616 | 122.5616 | 122.6395 | -0.045777
2459.9844 | 122.7722 | -122.5983 | 0.050354 | -0.19196 | -0.0027215 | -0.056253 | 0.022697 | -0.013396 | -0.0055841 | -0.0078249 | -0.15335 | 0.048471 | 0.048465 | 0.024054 | 0.014447 | 0.012371 | -0.013733 | -0.041199 | -0.004578 | 0 | -0.027466 | 0.07782 | -0.041199 | -0.009155 | 0.022888 | -0.086975 | -0.041199 | -0.022888 | 0.059509 | -0.004578 | 122.6761 | 122.5571 | -0.07782 | 122.5571 | 122.5983 | 0.041199 | -0.064087 | 122.6578 | 122.5937 | -0.091553 | 122.5891 | 122.5113 | -0.082397 | -0.073242 | 122.5708 | 122.5845 | 122.5937 | -0.091553 | 122.5571 | 122.5754 | 122.6212 | -0.054932
2461.6875 | 122.8226 | -122.5433 | 0.009155 | 0.159 | -0.0054987 | -0.059671 | 0.019066 | -0.014678 | -0.0064387 | -0.0037661 | 0.1976 | 0.048685 | 0.047824 | 0.022345 | 0.018079 | 0.014294 | 0.091553 | 0.086975 | 0.1236 | 0.086975 | -0.091553 | 0.12817 | -0.004578 | 0.14191 | 0.13275 | 0.041199 | -0.082397 | -0.050354 | 0.10071 | 0.027466 | 122.6715 | 122.5388 | -0.10071 | 122.6303 | 122.6303 | 0.091553 | 0.082398 | 122.644 | 122.5708 | -0.091552 | 122.6852 | 122.5845 | 0.013733 | -0.059509 | 122.4518 | 122.6349 | 122.6669 | -0.013733 | 122.4609 | 122.493 | 122.6761 | 0.018311
2463.3906 | 122.8638 | -122.5571 | 0.027466 | -0.031738 | -0.0031489 | -0.05839 | 0.021629 | -0.01831 | -0.0079339 | -0.0073977 | -0.069428 | 0.050607 | 0.050815 | 0.022345 | 0.012525 | 0.01408 | 0.036621 | 0.050354 | 0.13275 | 0.068665 | -0.050354 | 0.10071 | -0.004578 | 0.11902 | 0.14648 | 0.059509 | -0.07782 | -0.036621 | 0.07782 | 0.018311 | 122.6578 | 122.5525 | -0.07782 | 122.6074 | 122.6257 | 0.073243 | 0.009155 | 122.6349 | 122.5754 | -0.10529 | 122.6761 | 122.6166 | 0.041198 | -0.064087 | 122.5067 | 122.5937 | 122.6898 | -0.032044 | 122.4792 | 122.5204 | 122.7036 | -0.009155
2465.0938 | 122.7448 | -122.5845 | 0.041199 | 0.090332 | -0.00015808 | -0.059031 | 0.016075 | -0.016387 | 0.0023199 | -0.0054751 | 0.08316 | 0.051462 | 0.050815 | 0.025549 | 0.019788 | 0.012157 | 0.004578 | -0.059509 | -0.018311 | -0.004578 | -0.022888 | 0.07782 | -0.022888 | 0.022888 | -0.022888 | -0.10529 | -0.036621 | -0.004578 | 0.064087 | 0.004578 | 122.6624 | 122.5616 | -0.064087 | 122.525 | 122.58 | 0.01831 | -0.036621 | 122.6486 | 122.5891 | -0.07782 | 122.6074 | 122.4792 | -0.10986 | -0.045777 | 122.5616 | 122.5891 | 122.5662 | -0.064087 | 122.5479 | 122.58 | 122.5616 | -0.036621
2466.7969 | 122.8546 | -122.5021 | 0.022888 | 0.159 | -0.0025079 | -0.059458 | 0.017998 | -0.013396 | -0.0017389 | -0.0044071 | 0.15182 | 0.05488 | 0.04996 | 0.02149 | 0.017011 | 0.013866 | 0.050354 | 0.013733 | 0.068665 | 0.036621 | -0.054932 | 0.11444 | -0.009155 | 0.10529 | 0.09613 | 0.009155 | -0.073242 | -0.032043 | 0.10071 | 0.036621 | 122.6166 | 122.493 | -0.07782 | 122.5159 | 122.5388 | 0.045776 | 0.027466 | 122.6028 | 122.5388 | -0.09613 | 122.6074 | 122.5113 | -0.027466 | -0.054931 | 122.4472 | 122.5525 | 122.5708 | -0.032043 | 122.4289 | 122.4701 | 122.5983 | 0.013733
2468.5781 | 122.7493 | -122.5708 | 0.054932 | -0.21484 | -0.0018671 | -0.058817 | 0.021416 | -0.015533 | -0.0034479 | -0.0073977 | -0.1915 | 0.053384 | 0.052524 | 0.02384 | 0.013593 | 0.012371 | 0.004578 | -0.059509 | 0.013733 | -0.013733 | -0.027466 | 0.064087 | -0.054932 | -0.009155 | 0.013733 | -0.082397 | 0 | 0.013733 | 0.050354 | -0.009155 | 122.6349 | 122.5159 | -0.082398 | 122.5113 | 122.5571 | 0.041199 | -0.050354 | 122.6212 | 122.5616 | -0.054932 | 122.5616 | 122.4884 | -0.073242 | -0.041199 | 122.5433 | 122.5754 | 122.5845 | -0.10986 | 122.5708 | 122.5845 | 122.5845 | -0.064087
2470.3594 | 122.7951 | -122.5433 | 0.027466 | 0.075073 | -0.0050715 | -0.057962 | 0.018425 | -0.014892 | -0.0083613 | -0.0054751 | 0.12131 | 0.056589 | 0.055301 | 0.020209 | 0.014234 | 0.014294 | 0.045776 | 0.032043 | 0.09613 | 0.054932 | -0.073242 | 0.10529 | 0.013733 | 0.091553 | 0.068665 | -0.004578 | -0.064087 | -0.036621 | 0.082397 | 0.022888 | 122.6486 | 122.5571 | -0.10071 | 122.5754 | 122.5983 | 0.041199 | 0.01831 | 122.6257 | 122.5662 | -0.091553 | 122.6349 | 122.5388 | -0.027466 | -0.064087 | 122.4701 | 122.5891 | 122.6395 | -0.013733 | 122.4792 | 122.5067 | 122.612 | -0.004578
2472.125 | 122.8043 | -122.5479 | 0.022888 | 0.12848 | -0.0057123 | -0.059671 | 0.018639 | -0.015319 | -0.0043023 | -0.0052615 | 0.13657 | 0.066843 | 0.064273 | 0.019995 | 0.015302 | 0.012585 | 0.082397 | 0.086975 | 0.14191 | 0.064087 | -0.068665 | 0.10071 | 0.018311 | 0.1236 | 0.10986 | 0.036621 | -0.064087 | -0.027466 | 0.10529 | 0.027466 | 122.6486 | 122.5662 | -0.091553 | 122.6349 | 122.612 | 0.045776 | 0.059509 | 122.6532 | 122.5754 | -0.086975 | 122.6715 | 122.5845 | 0.009155 | -0.050354 | 122.4792 | 122.6303 | 122.6898 | -0.004577 | 122.4838 | 122.5204 | 122.6578 | 0.004578
2473.8281 | 122.7905 | -122.525 | 0.064087 | -0.13092 | -0.0018671 | -0.057749 | 0.020988 | -0.01361 | -0.0047297 | -0.0046207 | -0.13809 | 0.07261 | 0.071536 | 0.021704 | 0.012311 | 0.011303 | 0.10071 | 0.10071 | 0.16022 | 0.07782 | -0.059509 | 0.10529 | -0.009155 | 0.11902 | 0.16937 | 0.054932 | -0.059509 | -0.045776 | 0.10529 | 0.032043 | 122.6303 | 122.5159 | -0.1236 | 122.6257 | 122.6028 | 0.086975 | 0.036621 | 122.6303 | 122.5571 | -0.1236 | 122.644 | 122.58 | 0.022889 | -0.10986 | 122.4655 | 122.6257 | 122.6852 | -0.073242 | 122.4655 | 122.4792 | 122.6944 | -0.032044
2475.5781 | 122.8134 | -122.5021 | 0.013733 | 0.052185 | -0.0065667 | -0.060312 | 0.018852 | -0.014251 | -0.0057977 | -0.0080387 | 0.0068663 | 0.04014 | 0.039279 | 0.022772 | 0.01402 | 0.011303 | 0.027466 | 0.027466 | 0.086975 | 0.050354 | -0.045776 | 0.09613 | 0.004578 | 0.07782 | 0.10529 | 0.013733 | -0.059509 | -0.027466 | 0.086975 | 0.032043 | 122.5983 | 122.5067 | -0.059509 | 122.5296 | 122.5525 | 0.045776 | 0.013733 | 122.5891 | 122.5342 | -0.073242 | 122.58 | 122.5159 | -0.01831 | -0.041199 | 122.4564 | 122.5296 | 122.5891 | -0.009155 | 122.4426 | 122.4747 | 122.6074 | 0.01831
2477.2812 | 122.5937 | -122.4335 | 0.041199 | -0.069885 | 0.0021917 | -0.061594 | 0.020561 | -0.012969 | 0.0021063 | -0.0050479 | -0.13809 | 0.056589 | 0.052951 | 0.02384 | 0.017865 | 0.010662 | 0.091553 | 0.004578 | 0.068665 | 0.050354 | -0.045776 | 0.07782 | -0.018311 | 0.082397 | 0.064087 | -0.045776 | -0.045776 | -0.022888 | 0.073242 | 0.022888 | 122.5113 | 122.4152 | -0.086975 | 122.438 | 122.4838 | 0.068665 | 0.050354 | 122.5067 | 122.4564 | -0.086975 | 122.5159 | 122.3877 | -0.068664 | -0.064087 | 122.3877 | 122.525 | 122.5021 | -0.05951 | 122.3877 | 122.4106 | 122.4976 | -0.018311
2479.0469 | 122.6578 | -122.4792 | 0.064087 | -0.077515 | -0.0022943 | -0.06074 | 0.01992 | -0.015105 | -0.00045708 | -0.0033389 | -0.13046 | 0.076883 | 0.073245 | 0.024054 | 0.017224 | 0.0095937 | 0.064087 | 0.013733 | 0.068665 | 0.045776 | -0.036621 | 0.07782 | -0.045776 | 0.091553 | 0.086975 | -0.050354 | -0.018311 | -0.027466 | 0.054932 | 0.004578 | 122.5571 | 122.4335 | -0.10071 | 122.493 | 122.525 | 0.091552 | 0 | 122.5342 | 122.4838 | -0.082398 | 122.5708 | 122.4289 | -0.054932 | -0.091553 | 122.4426 | 122.5433 | 122.5479 | -0.10986 | 122.4609 | 122.4518 | 122.5662 | -0.059509
2480.75 | 122.7539 | -122.4472 | 0.018311 | 0.14374 | -0.0042169 | -0.057749 | 0.017998 | -0.014037 | -0.0021661 | -0.0059023 | 0.098419 | 0.063211 | 0.060641 | 0.023199 | 0.015943 | 0.013225 | 0 | -0.041199 | 0.009155 | -0.013733 | -0.022888 | 0.07782 | -0.036621 | 0.041199 | 0 | -0.064087 | -0.050354 | -0.022888 | 0.07782 | 0.013733 | 122.525 | 122.4106 | -0.041199 | 122.406 | 122.4335 | 0.022888 | -0.018311 | 122.525 | 122.4609 | -0.068665 | 122.4884 | 122.3831 | -0.07782 | -0.041199 | 122.4243 | 122.4472 | 122.4564 | -0.054932 | 122.3969 | 122.4243 | 122.4472 | -0.004578
2482.5156 | 122.8592 | -122.493 | 0.018311 | 0.11322 | -0.0076349 | -0.057535 | 0.022057 | -0.012755 | -0.0077203 | -0.0044071 | 0.12131 | 0.046548 | 0.044406 | 0.022772 | 0.012738 | 0.014507 | 0.054932 | 0.059509 | 0.10986 | 0.045776 | -0.064087 | 0.09613 | 0.013733 | 0.10071 | 0.07782 | 0.013733 | -0.064087 | -0.059509 | 0.09613 | 0.027466 | 122.5891 | 122.5067 | -0.082398 | 122.5525 | 122.5388 | 0.032043 | 0.036621 | 122.5891 | 122.5204 | -0.082398 | 122.5937 | 122.5067 | -0.013733 | -0.07782 | 122.4289 | 122.5479 | 122.6028 | -0.004578 | 122.4289 | 122.4335 | 122.5708 | 0.009155
2484.2656 | 122.7127 | -122.4655 | 0.050354 | 0.097962 | -0.0046441 | -0.060526 | 0.018852 | -0.01361 | -0.0062249 | -0.0048343 | 0.15182 | 0.089273 | 0.087131 | 0.023413 | 0.015302 | 0.014294 | 0.082397 | 0.086975 | 0.13733 | 0.07782 | -0.068665 | 0.10071 | -0.004578 | 0.12817 | 0.10071 | 0.027466 | -0.054932 | -0.050354 | 0.10071 | 0.032043 | 122.5662 | 122.4609 | -0.11902 | 122.5525 | 122.5433 | 0.082398 | 0.032043 | 122.5662 | 122.4976 | -0.10529 | 122.5937 | 122.493 | -0.004577 | -0.10071 | 122.3969 | 122.5479 | 122.6028 | -0.054932 | 122.4106 | 122.4152 | 122.5662 | -0.018311
2486.0156 | 122.6669 | -122.493 | 0.059509 | -0.19958 | -0.0027215 | -0.05839 | 0.021202 | -0.013824 | -0.0017389 | -0.0061161 | -0.18387 | 0.060648 | 0.060214 | 0.022559 | 0.01402 | 0.0093801 | 0 | -0.032043 | 0 | -0.004578 | -0.027466 | 0.073242 | -0.045776 | 0.013733 | 0.013733 | -0.10071 | -0.027466 | 0.004578 | 0.064087 | -0.018311 | 122.5662 | 122.4472 | -0.086975 | 122.4609 | 122.4884 | 0.041198 | -0.059509 | 122.5571 | 122.4747 | -0.086975 | 122.5067 | 122.3923 | -0.082397 | -0.054931 | 122.4655 | 122.493 | 122.493 | -0.10528 | 122.4655 | 122.4976 | 122.5067 | -0.07782
2487.7188 | 122.6807 | -122.4838 | 0.050354 | -0.1767 | -0.0035761 | -0.057108 | 0.021416 | -0.014037 | -0.0062249 | -0.0067569 | -0.099945 | 0.070901 | 0.0694 | 0.021277 | 0.014875 | 0.014294 | 0.09613 | 0.11902 | 0.14191 | 0.07782 | -0.059509 | 0.091553 | 0.004578 | 0.10529 | 0.16022 | 0.041199 | -0.059509 | -0.045776 | 0.091553 | 0.036621 | 122.5754 | 122.4884 | -0.10986 | 122.6028 | 122.5616 | 0.073242 | 0.045776 | 122.5754 | 122.5204 | -0.10986 | 122.5891 | 122.525 | 0.004578 | -0.09613 | 122.4243 | 122.58 | 122.6257 | -0.045776 | 122.4243 | 122.438 | 122.644 | -0.013733
2489.4844 | 122.5571 | -122.3831 | 0.11902 | -0.16907 | 0.00048272 | -0.061594 | 0.021202 | -0.013396 | -0.0032343 | -0.0086795 | -0.17624 | 0.22364 | 0.20655 | 0.021063 | 0.013166 | 0.012798 | 0 | -0.018311 | 0.041199 | 0 | -0.036621 | 0.073242 | -0.045776 | 0.032043 | 0.041199 | -0.07782 | 0.018311 | 0.027466 | 0.064087 | 0 | 122.4564 | 122.3373 | -0.15564 | 122.3648 | 122.3831 | 0.045776 | -0.11902 | 122.4472 | 122.3831 | -0.10071 | 122.4152 | 122.3053 | -0.07782 | -0.091553 | 122.3465 | 122.3831 | 122.4243 | -0.16479 | 122.4014 | 122.4106 | 122.4243 | -0.11902
2491.1875 | 122.3328 | -121.9574 | 0.31586 | -0.031738 | -0.00058528 | -0.059458 | 0.017143 | -0.015533 | 0.0027471 | -0.0039797 | -0.0083922 | 0.71092 | 0.64041 | 0.017645 | 0.020215 | 0.016216 | 0.068665 | 0.022888 | 0.045776 | 0.036621 | -0.018311 | 0.10529 | -0.027466 | 0.064087 | 0.045776 | -0.068665 | 0.13275 | 0.16022 | 0.073242 | 0.013733 | 122.0627 | 121.9299 | -0.33417 | 121.9803 | 121.994 | 0.064087 | -0.24719 | 122.0306 | 121.9711 | -0.18311 | 122.0215 | 121.8887 | -0.082398 | -0.15564 | 121.9391 | 122.0261 | 122.0032 | -0.34332 | 122.0901 | 122.1176 | 122.0032 | -0.30212
2492.9531 | 122.5113 | -122.3007 | 0.004578 | -0.19196 | -0.0052851 | -0.057108 | 0.020134 | -0.016173 | -0.0068659 | -0.0041933 | -0.092316 | 0.019418 | 0.023471 | 0.020636 | 0.014447 | 0.012798 | 0.086975 | 0.10986 | 0.15564 | 0.091553 | -0.059509 | 0.09613 | -0.013733 | 0.10986 | 0.15106 | 0.045776 | -0.086975 | -0.059509 | 0.086975 | 0.022888 | 122.3969 | 122.287 | -0.064087 | 122.4106 | 122.3923 | 0.10529 | 0.082397 | 122.3877 | 122.3236 | -0.091553 | 122.4106 | 122.3465 | 0.022888 | -0.064087 | 122.2412 | 122.3877 | 122.4564 | -0.018311 | 122.2137 | 122.2412 | 122.4518 | 0.01831
2494.7031 | 122.6303 | -122.374 | 0.022888 | 0.036926 | -0.0054987 | -0.058817 | 0.01928 | -0.013183 | -0.0055841 | -0.0046207 | 0.060272 | 0.019418 | 0.022189 | 0.024054 | 0.014661 | 0.013225 | 0.032043 | 0.018311 | 0.10071 | 0.041199 | -0.068665 | 0.091553 | -0.018311 | 0.073242 | 0.07782 | -0.009155 | -0.073242 | -0.054932 | 0.086975 | 0.013733 | 122.4655 | 122.3557 | -0.091553 | 122.3923 | 122.4152 | 0.05951 | 0.009155 | 122.4609 | 122.3877 | -0.09613 | 122.4472 | 122.3648 | -0.022888 | -0.07782 | 122.3053 | 122.406 | 122.4747 | -0.041199 | 122.3007 | 122.319 | 122.4518 | -0.009155
2496.4062 | 122.5891 | -122.438 | 0.041199 | -0.10803 | -0.0016535 | -0.059244 | 0.022057 | -0.015746 | -0.0023797 | -0.0050479 | -0.19913 | 0.0207 | 0.026675 | 0.025122 | 0.012097 | 0.012157 | 0.018311 | -0.036621 | 0.018311 | 0.009155 | -0.032043 | 0.059509 | -0.041199 | 0.013733 | 0.018311 | -0.07782 | -0.050354 | -0.032043 | 0.064087 | 0 | 122.4976 | 122.3969 | -0.073242 | 122.4014 | 122.4472 | 0.050354 | -0.022888 | 122.5021 | 122.438 | -0.091553 | 122.4518 | 122.3602 | -0.07782 | -0.073242 | 122.406 | 122.4564 | 122.4564 | -0.082398 | 122.3877 | 122.406 | 122.4564 | -0.041199

## Thermal Data
Fire Time | A Position - Middle
-0.0115 | 14.3882
0.9885 | 15.7546
1.9885 | 17.1176
2.9885 | 18.5299
3.9885 | 22.1659
4.9885 | 26.108
5.9885 | 30.7716
6.9885 | 34.5481
7.9885 | 38.3323
8.9885 | 41.159
9.9885 | 43.3338
10.9885 | 47.4701
11.9885 | 51.2885
12.9885 | 54.5182
13.9885 | 57.5085
14.9885 | 61.2242
15.9885 | 64.3916
16.9885 | 68.0072
17.9885 | 71.5582
18.9885 | 76.8949
19.9885 | 80.9865
20.9885 | 84.2908
21.9885 | 87.957
22.9885 | 89.8068
23.9885 | 91.8901
24.9885 | 92.7914
25.9885 | 93.4893
26.9885 | 94.8782
27.9885 | 97.0945
28.9885 | 99.4971
29.9885 | 103.2254
30.9885 | 106.629
31.9885 | 108.4187
32.9885 | 111.3789
33.9885 | 112.8953
34.9885 | 114.8258
35.9885 | 115.5648
36.9885 | 115.5223
37.9885 | 115.5914
38.9885 | 115.5891
39.9885 | 116.0614
40.9885 | 115.913
41.9885 | 116.201
42.9885 | 116.2362
43.9885 | 115.8508
44.9885 | 116.8535
45.9885 | 117.2071
46.9885 | 117.0441
47.9885 | 117.8264
48.9885 | 118.13
49.9885 | 119.8949
50.9885 | 121.3921
51.9885 | 122.5267
52.9885 | 123.9934
53.9885 | 124.7469
54.9885 | 125.7384
55.9885 | 127.7705
56.9885 | 129.1996
57.9885 | 132.4602
58.9885 | 133.6144
59.9885 | 136.0397
60.9885 | 136.1493
61.9885 | 135.8884
62.9885 | 135.5148
63.9885 | 136.5296
64.9885 | 137.2046
65.9885 | 138.1894
66.9885 | 139.836
67.9885 | 140.5032
68.9885 | 140.2597
69.9885 | 139.5907
70.9885 | 139.2297
71.9885 | 139.4321
72.9885 | 138.8572
73.9885 | 140.8459
74.9885 | 142.9308
75.9885 | 143.8341
76.9885 | 145.0962
77.9885 | 146.729
78.9885 | 146.3405
79.9885 | 146.5211
80.9885 | 146.566
81.9885 | 145.5591
82.9885 | 146.8785
83.9885 | 147.8977
84.9885 | 148.5361
85.9885 | 147.9591
86.9885 | 150.7459
87.9885 | 152.8113
88.9885 | 154.2124
89.9885 | 153.3517
90.9885 | 155.1736
91.9885 | 156.9091
92.9885 | 157.6626
93.9885 | 159.2855
94.9885 | 162.9172
95.9885 | 165.2007
96.9885 | 165.8505
97.9885 | 166.452
98.9885 | 168.0213
99.9885 | 170.5635
100.9885 | 171.5883
101.9885 | 174.543
102.9885 | 177.8073
103.9885 | 180.3553
104.9885 | 180.0631
105.9885 | 183.0756
106.9885 | 184.3864
107.9885 | 185.9773
108.9885 | 187.4808
109.9885 | 187.7062
110.9885 | 186.3393
111.9885 | 187.8176
112.9885 | 189.6016
113.9885 | 188.9843
114.9885 | 188.9462
115.9885 | 189.0166
116.9885 | 189.1964
117.9885 | 189.3628
118.9885 | 188.2897
119.9885 | 188.6473
120.9885 | 187.4534
121.9885 | 187.7154
122.9885 | 186.061
123.9885 | 186.9125
124.9885 | 187.0698
125.9885 | 186.7987
126.9885 | 186.2154
127.9885 | 185.6278
128.9885 | 185.5246
129.9885 | 185.778
130.9885 | 186.3094
131.9885 | 185.5223
132.9885 | 185.4889
133.9885 | 183.6962
134.9885 | 183.8173
135.9885 | 184.6762
136.9885 | 184.4271
137.9885 | 185.8831
138.9885 | 185.2684
139.9885 | 184.9713
140.9885 | 184.3508
141.9885 | 185.8851
142.9885 | 186.8055
143.9885 | 188.1269
144.9885 | 190.4662
145.9885 | 192.1735
146.9885 | 192.7073
147.9885 | 194.9527
148.9885 | 193.9874
149.9885 | 193.0527
150.9885 | 192.9911
151.9885 | 193.1708
152.9885 | 193.7579
153.9885 | 192.3142
154.9885 | 193.9109
155.9885 | 194.0447
156.9885 | 196.2558
157.9885 | 195.1233
158.9885 | 194.9533
159.9885 | 195.9118
160.9885 | 196.9117
161.9885 | 196.478
162.9885 | 197.2395
163.9885 | 197.7478
164.9885 | 197.9015
165.9885 | 198.3581
166.9885 | 196.6221
167.9885 | 199.7941
168.9885 | 200.2184
169.9885 | 199.7774
170.9885 | 198.2569
171.9885 | 198.0992
172.9885 | 198.2838
173.9885 | 197.6295
174.9885 | 197.326
175.9885 | 197.1084
176.9885 | 198.1388
177.9885 | 197.76
178.9885 | 198.3681
179.9885 | 199.1905
180.9885 | 200.7158
181.9885 | 201.5385
182.9885 | 204.1945
183.9885 | 206.4704
184.9885 | 206.9179
185.9885 | 206.4932
186.9885 | 205.0975
187.9885 | 204.372
188.9885 | 203.4787
189.9885 | 204.7392
190.9885 | 204.076
191.9885 | 203.5405
192.9885 | 202.9251
193.9885 | 201.0373
194.9885 | 201.3083
195.9885 | 201.1045
196.9885 | 201.161
197.9885 | 200.6071
198.9885 | 200.754
199.9885 | 199.8958
200.9885 | 200.6199
201.9885 | 199.8635
202.9885 | 200.2136
203.9885 | 199.5064
204.9885 | 199.4877
205.9885 | 200.961
206.9885 | 199.9113
207.9885 | 198.7314
208.9885 | 198.8564
209.9885 | 200.4735
210.9885 | 198.1893
211.9885 | 198.6324
212.9885 | 199.2049
213.9885 | 198.8643
214.9885 | 199.5054
215.9885 | 199.8685
216.9885 | 198.2496
217.9885 | 196.8023
218.9885 | 195.0332
219.9885 | 194.0942
220.9885 | 194.6375
221.9885 | 195.4002
222.9885 | 195.0433
223.9885 | 195.422
224.9885 | 197.009
225.9885 | 197.8017
226.9885 | 198.8013
227.9885 | 199.5276
228.9885 | 201.5812
229.9885 | 201.2872
230.9885 | 200.4261
231.9885 | 202.1301
232.9885 | 204.1732
233.9885 | 206.0655
234.9885 | 206.5666
235.9885 | 207.18
236.9885 | 207.7724
237.9885 | 208.3239
238.9885 | 207.8839
239.9885 | 208.5882
240.9885 | 208.8175
241.9885 | 207.959
242.9885 | 208.5502
243.9885 | 208.5841
244.9885 | 209.6494
245.9885 | 210.5123
246.9885 | 212.419
247.9885 | 212.4741
248.9885 | 214.3084
249.9885 | 215.6265
250.9885 | 215.7589
251.9885 | 216.7861
252.9885 | 218.7459
253.9885 | 220.4027
254.9885 | 220.3849
255.9885 | 221.0106
256.9885 | 220.9764
257.9885 | 220.4766
258.9885 | 220.9648
259.9885 | 221.2624
260.9885 | 221.4856
261.9885 | 222.7228
262.9885 | 220.5614
263.9885 | 219.2652
264.9885 | 220.3408
265.9885 | 220.115
266.9885 | 220.1247
267.9885 | 221.2205
268.9885 | 222.6563
269.9885 | 223.3375
270.9885 | 226.3064
271.9885 | 227.8108
272.9885 | 230.0535
273.9885 | 232.5899
274.9885 | 232.895
275.9885 | 232.2217
276.9885 | 233.3686
277.9885 | 231.7267
278.9885 | 235.4472
279.9885 | 236.4791
280.9885 | 237.2088
281.9885 | 237.717
282.9885 | 240.6201
283.9885 | 239.1515
284.9885 | 243.3553
285.9885 | 243.9762
286.9885 | 246.974
287.9885 | 249.4776
288.9885 | 252.4071
289.9885 | 253.6185
290.9885 | 256.1404
291.9885 | 256.1294
292.9885 | 255.097
293.9885 | 256.7574
294.9885 | 256.6482
295.9885 | 257.5153
296.9885 | 273.7505
297.9885 | 288.6446
298.9885 | 297.6854
299.9885 | 296.335
300.9885 | 297.5058
301.9885 | 296.1728
302.9885 | 295.8779
303.9885 | 296.2883
304.9885 | 297.1311
305.9885 | 297.5145
306.9885 | 316.3197
307.9885 | 313.282
308.9885 | 311.2478
309.9885 | 311.3099
310.9885 | 308.2628
311.9885 | 309.416
312.9885 | 308.3583
313.9885 | 306.949
314.9885 | 308.7163
315.9885 | 308.8873
316.9885 | 309.0887
317.9885 | 310.7092
318.9885 | 309.2369
319.9885 | 313.258
320.9885 | 314.712
321.9885 | 316.7881
322.9885 | 318.0895
323.9885 | 317.677
324.9885 | 320.1649
325.9885 | 323.9931
326.9885 | 324.8942
327.9885 | 322.4458
328.9885 | 322.5465
329.9885 | 320.2062
330.9885 | 320.6593
331.9885 | 321.7497
332.9885 | 324.3875
333.9885 | 326.8393
334.9885 | 332.0503
335.9885 | 334.634
336.9885 | 357.2708
337.9885 | 369.5878
338.9885 | 375.1844
339.9885 | 411.6388
340.9885 | 437.7987
341.9885 | 452.2412
342.9885 | 464.6511
343.9885 | 483.9421
344.9885 | 478.3682
345.9885 | 473.3161
346.9885 | 470.5982
347.9885 | 487.942
348.9885 | 489.8593
349.9885 | 484.0014
350.9885 | 477.1669
351.9885 | 471.2899
352.9885 | 464.3695
353.9885 | 462.1087
354.9885 | 454.8943
355.9885 | 450.9224
356.9885 | 455.3707
357.9885 | 450.8933
358.9885 | 447.8558
359.9885 | 442.3072
360.9885 | 436.3271
361.9885 | 434.2347
362.9885 | 431.9915
363.9885 | 428.5091
364.9885 | 426.3772
365.9885 | 427.9156
366.9885 | 426.0717
367.9885 | 422.3327
368.9885 | 421.2784
369.9885 | 420.4016
370.9885 | 421.2949
371.9885 | 419.7245
372.9885 | 423.2063
373.9885 | 423.0247
374.9885 | 424.4666
375.9885 | 425.7271
376.9885 | 427.0939
377.9885 | 425.3134
378.9885 | 425.8092
379.9885 | 426.8008
380.9885 | 426.953
381.9885 | 426.547
382.9885 | 427.3405
383.9885 | 427.3091
384.9885 | 427.9189
385.9885 | 430.8602
386.9885 | 433.9572
387.9885 | 435.6979
388.9885 | 439.8072
389.9885 | 446.606
390.9885 | 449.1955
391.9885 | 451.7227
392.9885 | 455.8504
393.9885 | 461.2094
394.9885 | 463.0455
395.9885 | 463.9579
396.9885 | 464.6034
397.9885 | 465.1399
398.9885 | 472.1267
399.9885 | 473.5135
400.9885 | 474.4483
401.9885 | 478.5373
402.9885 | 482.3987
403.9885 | 484.3836
404.9885 | 484.343
405.9885 | 484.6111
406.9885 | 488.0014
407.9885 | 493.2442
408.9885 | 498.418
409.9885 | 501.1432
410.9885 | 511.4801
411.9885 | 514.2493
412.9885 | 522.0577
413.9885 | 521.0423
414.9885 | 522.0416
415.9885 | 524.1771
416.9885 | 530.422
417.9885 | 544.0491
418.9885 | 568.0145
419.9885 | 567.9243
420.9885 | 565.5619
421.9885 | 570.3543
422.9885 | 570.4482
423.9885 | 569.19
424.9885 | 572.7513
425.9885 | 572.9268
426.9885 | 571.1283
427.9885 | 588.4649
428.9885 | 598.1019
429.9885 | 597.9608
430.9885 | 598.852
431.9885 | 595.1874
432.9885 | 601.4147
433.9885 | 600.459
434.9885 | 605.6903
435.9885 | 603.1864
436.9885 | 596.6018
437.9885 | 593.9502
438.9885 | 592.8664
439.9885 | 598.2846
440.9885 | 606.7365
441.9885 | 604.0945
442.9885 | 601.2005
443.9885 | 599.3189
444.9885 | 596.5668
445.9885 | 595.651
446.9885 | 599.0211
447.9885 | 600.1927
448.9885 | 609.5423
449.9885 | 614.3616
450.9885 | 617.2313
451.9885 | 616.8323
452.9885 | 614.2087
453.9885 | 612.7648
454.9885 | 608.9928
455.9885 | 610.0138
456.9885 | 611.1174
457.9885 | 606.3233
458.9885 | 607.6854
459.9885 | 605.5196
460.9885 | 601.0222
461.9885 | 607.0907
462.9885 | 604.6053
463.9885 | 600.9029
464.9885 | 612.0958
465.9885 | 620.4011
466.9885 | 616.3433
467.9885 | 617.5856
468.9885 | 616.6502
469.9885 | 618.0759
470.9885 | 613.2188
471.9885 | 609.9602
472.9885 | 610.9795
473.9885 | 609.0423
474.9885 | 608.313
475.9885 | 620.0991
476.9885 | 625.1409
477.9885 | 617.8323
478.9885 | 628.0686
479.9885 | 623.6603
480.9885 | 646.2055
481.9885 | 640.9986
482.9885 | 636.9986
483.9885 | 635.2547
484.9885 | 636.743
485.9885 | 637.2707
486.9885 | 639.4283
487.9885 | 637.6548
488.9885 | 637.7137
489.9885 | 632.4029
490.9885 | 643.2575
491.9885 | 643.3994
492.9885 | 641.1547
493.9885 | 640.352
494.9885 | 647.8073
495.9885 | 639.4889
496.9885 | 637.1863
497.9885 | 650.9503
498.9885 | 663.6558
499.9885 | 659.472
500.9885 | 654.3892
501.9885 | 661.1328
502.9885 | 663.4594
503.9885 | 657.7352
504.9885 | 657.4878
505.9885 | 666.793
506.9885 | 664.0782
507.9885 | 662.5541
508.9885 | 659.7093
509.9885 | 670.5354
510.9885 | 673.8352
511.9885 | 679.1859
512.9885 | 677.5311
513.9885 | 685.5665
514.9885 | 683.8864
515.9885 | 682.0257
516.9885 | 681.0992
517.9885 | 673.2499
518.9885 | 672.6764
519.9885 | 675.7019
520.9885 | 688.3959
521.9885 | 679.5305
522.9885 | 672.1633
523.9885 | 666.4124
524.9885 | 671.3103
525.9885 | 668.8302
526.9885 | 666.2017
527.9885 | 674.6551
528.9885 | 673.0816
529.9885 | 676.1473
530.9885 | 678.0224
531.9885 | 685.3518
532.9885 | 682.6359
533.9885 | 678.8287
534.9885 | 681.5759
535.9885 | 685.6644
536.9885 | 677.8567
537.9885 | 674.6309
538.9885 | 675.1244
539.9885 | 679.7059
540.9885 | 684.5948
541.9885 | 685.0836
542.9885 | 682.2539
543.9885 | 677.2515
544.9885 | 682.5617
545.9885 | 679.6482
546.9885 | 678.6506
547.9885 | 679.8376
548.9885 | 675.1148
549.9885 | 672.3733
550.9885 | 675.0397
551.9885 | 677.4736
552.9885 | 684.7072
553.9885 | 700.4551
554.9885 | 706.5814
555.9885 | 712.0765
556.9885 | 706.9956
557.9885 | 706.0798
558.9885 | 710.1323
559.9885 | 711.0524
560.9885 | 710.1204
561.9885 | 710.3923
562.9885 | 717.6189
563.9885 | 720.2036
564.9885 | 724.7057
565.9885 | 721.5384
566.9885 | 729.0187
567.9885 | 731.3171
568.9885 | 726.8472
569.9885 | 723.4712
570.9885 | 726.8459
571.9885 | 734.8876
572.9885 | 732.5859
573.9885 | 731.2225
574.9885 | 723.3362
575.9885 | 722.8161
576.9885 | 718.9425
577.9885 | 716.4333
578.9885 | 718.389
579.9885 | 716.8782
580.9885 | 712.2076
581.9885 | 713.8578
582.9885 | 709.9184
583.9885 | 715.7554
584.9885 | 720.7311
585.9885 | 712.3169
586.9885 | 726.7488
587.9885 | 731.8553
588.9885 | 731.4721
589.9885 | 737.0783
590.9885 | 739.1074
591.9885 | 736.6705
592.9885 | 749.487
593.9885 | 746.8532
594.9885 | 743.6789
595.9885 | 744.9457
596.9885 | 746.4908
597.9885 | 746.1717
598.9885 | 742.0362
599.9885 | 744.315
600.9885 | 752.0049
601.9885 | 755.0186
602.9885 | 752.3057
603.9885 | 754.8099
604.9885 | 753.1588
605.9885 | 751.5533
606.9885 | 747.9974
607.9885 | 745.7911
608.9885 | 743.7778
609.9885 | 745.2636
610.9885 | 741.7714
611.9885 | 743.1095
612.9885 | 750.9418
613.9885 | 754.2176
614.9885 | 756.6337
615.9885 | 761.2272
616.9885 | 763.5025
617.9885 | 763.1482
618.9885 | 765.7298
619.9885 | 759.2749
620.9885 | 767.1406
621.9885 | 765.6877
622.9885 | 769.7077
623.9885 | 765.6902
624.9885 | 765.786
625.9885 | 767.8038
626.9885 | 763.3911
627.9885 | 769.9086
628.9885 | 766.4001
629.9885 | 762.0699
630.9885 | 760.3992
631.9885 | 759.355
632.9885 | 761.5663
633.9885 | 765.8787
634.9885 | 758.739
635.9885 | 762.5095
636.9885 | 762.8207
637.9885 | 760.7643
638.9885 | 765.5838
639.9885 | 763.0336
640.9885 | 764.2337
641.9885 | 764.0004
642.9885 | 759.8963
643.9885 | 761.0452
644.9885 | 758.7046
645.9885 | 760.8847
646.9885 | 762.153
647.9885 | 765.3099
648.9885 | 770.6496
649.9885 | 769.064
650.9885 | 770.0592
651.9885 | 766.6115
652.9885 | 765.0851
653.9885 | 763.6438
654.9885 | 759.6528
655.9885 | 761.4436
656.9885 | 764.8529
657.9885 | 763.5619
658.9885 | 763.3463
659.9885 | 763.9889
660.9885 | 759.9972
661.9885 | 761.6689
662.9885 | 765.4326
663.9885 | 759.205
664.9885 | 754.4934
665.9885 | 751.6253
666.9885 | 757.4106
667.9885 | 761.359
668.9885 | 762.7943
669.9885 | 763.7905
670.9885 | 765.6189
671.9885 | 763.8895
672.9885 | 763.5756
673.9885 | 761.3107
674.9885 | 758.7471
675.9885 | 757.1821
676.9885 | 760.3996
677.9885 | 757.4291
678.9885 | 755.3151
679.9885 | 756.9573
680.9885 | 753.9975
681.9885 | 753.2958
682.9885 | 757.2733
683.9885 | 757.8362
684.9885 | 758.6325
685.9885 | 763.1117
686.9885 | 767.7241
687.9885 | 764.0941
688.9885 | 759.432
689.9885 | 758.0003
690.9885 | 757.7909
691.9885 | 760.5334
692.9885 | 758.2555
693.9885 | 760.8964
694.9885 | 763.4936
695.9885 | 760.0684
696.9885 | 760.0873
697.9885 | 762.1548
698.9885 | 767.9086
699.9885 | 764.6575
700.9885 | 770.3512
701.9885 | 769.9999
702.9885 | 768.4717
703.9885 | 764.999
704.9885 | 767.7181
705.9885 | 766.8792
706.9885 | 762.2558
707.9885 | 757.3661
708.9885 | 758.6715
709.9885 | 762.4634
710.9885 | 761.6611
711.9885 | 762.3834
712.9885 | 759.8748
713.9885 | 761.2777
714.9885 | 754.1353
715.9885 | 759.4672
716.9885 | 763.219
717.9885 | 764.0915
718.9885 | 762.2367
719.9885 | 761.2742
720.9885 | 758.0951
721.9885 | 754.3862
722.9885 | 752.2608
723.9885 | 752.5481
724.9885 | 751.9818
725.9885 | 750.1284
726.9885 | 754.1376
727.9885 | 751.206
728.9885 | 752.5171
729.9885 | 756.3829
730.9885 | 757.6409
731.9885 | 757.6369
732.9885 | 755.2544
733.9885 | 755.1257
734.9885 | 748.9267
735.9885 | 748.7335
736.9885 | 749.9577
737.9885 | 753.8119
738.9885 | 758.0081
739.9885 | 762.5926
740.9885 | 768.2149
741.9885 | 767.3654
742.9885 | 768.7012
743.9885 | 773.0602
744.9885 | 769.2655
745.9885 | 767.8003
746.9885 | 764.5103
747.9885 | 764.4528
748.9885 | 763.7978
749.9885 | 767.0217
750.9885 | 768.6633
751.9885 | 768.8376
752.9885 | 776.4298
753.9885 | 777.4295
754.9885 | 779.872
755.9885 | 786.4968
756.9885 | 783.2838
757.9885 | 781.3122
758.9885 | 786.9898
759.9885 | 787.6287
760.9885 | 794.2772
761.9885 | 795.3088
762.9885 | 789.1884
763.9885 | 794.8325
764.9885 | 796.6879
765.9885 | 794.8625
766.9885 | 792.1087
767.9885 | 794.5659
768.9885 | 790.1561
769.9885 | 790.0413
770.9885 | 783.3439
771.9885 | 782.6467
772.9885 | 782.9361
773.9885 | 782.187
774.9885 | 782.1753
775.9885 | 780.8604
776.9885 | 785.4553
777.9885 | 783.5278
778.9885 | 784.7133
779.9885 | 783.5833
780.9885 | 784.5627
781.9885 | 781.4623
782.9885 | 779.8365
783.9885 | 778.8307
784.9885 | 779.3922
785.9885 | 778.708
786.9885 | 780.7096
787.9885 | 785.5487
788.9885 | 787.7156
789.9885 | 787.4278
790.9885 | 788.2229
791.9885 | 785.3138
792.9885 | 779.7343
793.9885 | 780.6656
794.9885 | 782.3747
795.9885 | 786.2042
796.9885 | 785.6681
797.9885 | 783.5127
798.9885 | 783.7496
799.9885 | 785.0486
800.9885 | 785.7511
801.9885 | 789.4019
802.9885 | 790.1217
803.9885 | 793.5624
804.9885 | 797.4111
805.9885 | 792.9312
806.9885 | 791.9352
807.9885 | 789.4098
808.9885 | 791.5042
809.9885 | 793.5957
810.9885 | 791.664
811.9885 | 790.5824
812.9885 | 794.1797
813.9885 | 793.5603
814.9885 | 792.6542
815.9885 | 792.2829
816.9885 | 793.4615
817.9885 | 791.1665
818.9885 | 793.6675
819.9885 | 793.6902
820.9885 | 792.3111
821.9885 | 784.7873
822.9885 | 788.303
823.9885 | 787.4687
824.9885 | 786.6346
825.9885 | 784.182
826.9885 | 787.2959
827.9885 | 786.3492
828.9885 | 790.8547
829.9885 | 786.6788
830.9885 | 788.761
831.9885 | 787.7522
832.9885 | 788.0356
833.9885 | 789.6765
834.9885 | 787.899
835.9885 | 788.0868
836.9885 | 790.5499
837.9885 | 790.9193
838.9885 | 792.6087
839.9885 | 795.4473
840.9885 | 793.09
841.9885 | 790.704
842.9885 | 782.8745
843.9885 | 780.867
844.9885 | 782.8909
845.9885 | 784.6307
846.9885 | 780.0483
847.9885 | 781.066
848.9885 | 782.1769
849.9885 | 775.1821
850.9885 | 778.0485
851.9885 | 778.0511
852.9885 | 780.4554
853.9885 | 784.2688
854.9885 | 786.7076
855.9885 | 785.8629
856.9885 | 784.5486
857.9885 | 786.935
858.9885 | 786.6877
859.9885 | 787.396
860.9885 | 788.3939
861.9885 | 789.39
862.9885 | 790.2896
863.9885 | 785.7639
864.9885 | 789.3124
865.9885 | 796.8974
866.9885 | 797.9203
867.9885 | 794.0188
868.9885 | 798.0867
869.9885 | 794.1199
870.9885 | 793.6686
871.9885 | 793.523
872.9885 | 790.8933
873.9885 | 790.6407
874.9885 | 795.9169
875.9885 | 793.6801
876.9885 | 795.2974
877.9885 | 795.6322
878.9885 | 800.2947
879.9885 | 797.4234
880.9885 | 798.0723
881.9885 | 798.6126
882.9885 | 799.4919
883.9885 | 802.3833
884.9885 | 804.6129
885.9885 | 802.0514
886.9885 | 804.6415
887.9885 | 804.4339
888.9885 | 802.2179
889.9885 | 804.0195
890.9885 | 800.6774
891.9885 | 796.7873
892.9885 | 795.6002
893.9885 | 796.786
894.9885 | 796.8334
895.9885 | 791.6953
896.9885 | 790.1538
897.9885 | 791.2644
898.9885 | 793.8265
899.9885 | 789.1106
900.9885 | 788.386
901.9885 | 788.8598
902.9885 | 785.5529
903.9885 | 780.8492
904.9885 | 781.7414
905.9885 | 785.3036
906.9885 | 786.3284
908.0042 | 790.5951
908.9885 | 789.5554
909.9885 | 790.482
910.9885 | 792.8813
911.9885 | 795.3312
912.9885 | 796.0476
913.9885 | 795.8598
914.9885 | 795.9981
915.9885 | 798.0502
916.9885 | 797.5672
917.9885 | 796.4069
918.9885 | 793.9517
919.9885 | 798.6875
920.9885 | 794.5387
921.9885 | 789.9305
922.9885 | 788.9741
923.9885 | 793.6346
924.9885 | 799.6527
925.9885 | 798.5528
926.9885 | 800.0599
927.9885 | 799.2114
928.9885 | 803.3241
929.9885 | 801.7027
930.9885 | 794.7164
931.9885 | 791.5594
932.9885 | 790.5014
933.9885 | 791.3616
934.9885 | 789.4918
935.9885 | 796.5203
936.9885 | 790.2163
937.9885 | 788.9467
938.9885 | 789.3056
939.9885 | 790.4787
940.9885 | 790.632
941.9885 | 789.5656
942.9885 | 795.3825
943.9885 | 794.3345
944.9885 | 796.414
945.9885 | 793.5985
946.9885 | 798.3267
947.9885 | 802.6776
948.9885 | 804.5878
949.9885 | 803.3237
950.9885 | 803.731
951.9885 | 799.1464
952.9885 | 799.005
953.9885 | 800.2022
954.9885 | 800.9134
955.9885 | 794.7431
956.9885 | 792.998
957.9885 | 801.2934
958.9885 | 801.0701
959.9885 | 802.652
960.9885 | 799.9063
961.9885 | 797.8236
962.9885 | 799.1681
963.9885 | 799.6231
964.9885 | 793.5652
965.9885 | 794.8453
966.9885 | 800.5062
967.9885 | 797.3235
968.9885 | 799.2793
969.9885 | 798.4524
970.9885 | 798.8358
971.9885 | 800.2592
972.9885 | 798.7787
973.9885 | 800.9947
974.9885 | 802.9772
975.9885 | 798.2782
976.9885 | 798.9962
977.9885 | 794.1917
978.9885 | 794.8901
979.9885 | 793.5586
980.9885 | 790.2161
981.9885 | 785.4487
982.9885 | 790.7291
983.9885 | 794.7903
984.9885 | 789.971
985.9885 | 796.644
986.9885 | 800.0329
987.9885 | 801.2294
988.9885 | 803.3698
989.9885 | 806.0017
990.9885 | 808.0249
991.9885 | 807.7993
992.9885 | 803.6207
993.9885 | 796.7812
994.9885 | 800.3705
995.9885 | 798.1161
996.9885 | 796.9524
997.9885 | 793.9292
998.9885 | 798.4196
999.9885 | 797.7785
1000.9885 | 795.6238
1001.9885 | 800.2954
1002.9885 | 800.0416
1003.9885 | 799.7064
1004.9885 | 794.9233
1005.9885 | 795.1929
1006.9885 | 792.856
1007.9885 | 792.5917
1008.9885 | 789.949
1009.9885 | 789.0111
1010.9885 | 784.9992
1011.9885 | 786.9427
1012.9885 | 785.5154
1013.9885 | 789.3249
1014.9885 | 788.2436
1015.9885 | 787.9624
1016.9885 | 784.0906
1017.9885 | 784.5513
1018.9885 | 784.1964
1019.9885 | 782.5672
1020.9885 | 778.2123
1021.9885 | 776.2498
1022.9885 | 782.7625
1023.9885 | 784.4018
1024.9885 | 784.7236
1025.9885 | 788.8277
1026.9885 | 793.7454
1027.9885 | 791.7489
1028.9885 | 789.0108
1029.9885 | 790.9945
1030.9885 | 788.8156
1031.9885 | 787.1244
1032.9885 | 787.2476
1033.9885 | 780.6903
1034.9885 | 782.6335
1035.9885 | 785.9218
1036.9885 | 786.7495
1037.9885 | 787.7737
1038.9885 | 792.4807
1039.9885 | 798.0038
1040.9885 | 796.7652
1041.9885 | 793.7337
1042.9885 | 790.8688
1043.9885 | 793.9622
1044.9885 | 796.2022
1045.9885 | 794.1747
1046.9885 | 794.5296
1047.9885 | 793.9765
1048.9885 | 794.5341
1049.9885 | 793.0633
1050.9885 | 794.4942
1051.9885 | 791.5771
1052.9885 | 790.9133
1053.9885 | 787.0643
1054.9885 | 790.4513
1055.9885 | 784.807
1056.9885 | 788.2913
1057.9885 | 789.8751
1058.9885 | 789.7826
1059.9885 | 791.4512
1060.9885 | 786.3595
1061.9885 | 783.5462
1062.9885 | 783.3304
1063.9885 | 783.2138
1064.9885 | 782.8613
1065.9885 | 784.0057
1066.9885 | 783.363
1067.9885 | 790.4534
1068.9885 | 791.0451
1069.9885 | 788.9327
1070.9885 | 787.5857
1071.9885 | 789.9599
1072.9885 | 789.9188
1073.9885 | 784.7006
1074.9885 | 783.0567
1075.9885 | 775.4096
1076.9885 | 770.9009
1077.9885 | 769.7317
1078.9885 | 773.1715
1079.9885 | 778.255
1080.9885 | 779.8006
1081.9885 | 778.9199
1082.9885 | 775.4152
1083.9885 | 778.9641
1084.9885 | 786.5369
1085.9885 | 790.7904
1086.9885 | 793.7118
1087.9885 | 794.2662
1088.9885 | 799.7704
1089.9885 | 798.0881
1090.9885 | 796.5721
1091.9885 | 796.5533
1092.9885 | 791.5208
1093.9885 | 791.404
1094.9885 | 788.6645
1095.9885 | 786.3165
1096.9885 | 784.1554
1097.9885 | 784.0634
1098.9885 | 787.5726
1099.9885 | 785.973
1100.9885 | 787.9867
1101.9885 | 790.7353
1102.9885 | 790.9434
1103.9885 | 782.8119
1104.9885 | 788.7604
1105.9885 | 788.6226
1106.9885 | 788.8542
1107.9885 | 789.9598
1108.9885 | 787.0056
1109.9885 | 794.7859
1110.9885 | 795.5022
1111.9885 | 797.2306
1112.9885 | 794.9034
1113.9885 | 790.4517
1114.9885 | 796.3993
1115.9885 | 792.4364
1116.9885 | 796.1597
1117.9885 | 794.8589
1118.9885 | 794.513
1119.9885 | 790.7316
1120.9885 | 794.215
1121.9885 | 792.1515
1122.9885 | 787.1052
1123.9885 | 790.6316
1124.9885 | 789.5872
1125.9885 | 791.6686
1126.9885 | 795.8214
1127.9885 | 794.3934
1128.9885 | 792.4837
1129.9885 | 792.5437
1130.9885 | 794.6452
1131.9885 | 791.4993
1132.9885 | 794.137
1133.9885 | 794.9066
1134.9885 | 791.3378
1135.9885 | 789.2651
1136.9885 | 794.5394
1137.9885 | 789.7179
1138.9885 | 793.9452
1139.9885 | 794.0453
1140.9885 | 790.3109
1141.9885 | 787.3694
1142.9885 | 788.7913
1143.9885 | 792.1079
1144.9885 | 795.4307
1145.9885 | 792.9994
1146.9885 | 794.3527
1147.9885 | 794.388
1148.9885 | 794.8023
1149.9885 | 794.4087
1150.9885 | 790.4143
1151.9885 | 793.1281
1152.9885 | 796.7641
1153.9885 | 792.814
1154.9885 | 794.7866
1155.9885 | 790.2434
1156.9885 | 792.8001
1157.9885 | 789.5143
1158.9885 | 791.1655
1159.9885 | 790.447
1160.9885 | 787.8786
1161.9885 | 787.6507
1162.9885 | 787.172
1163.9885 | 790.4828
1164.9885 | 792.9515
1165.9885 | 795.2394
1166.9885 | 796.4093
1167.9885 | 793.4462
1168.9885 | 789.4999
1169.9885 | 782.6032
1170.9885 | 783.1524
1171.9885 | 784.1633
1172.9885 | 783.2947
1173.9885 | 787.2871
1174.9885 | 787.5638
1175.9885 | 788.9064
1176.9885 | 785.3038
1177.9885 | 781.5396
1178.9885 | 780.9266
1179.9885 | 781.0888
1180.9885 | 783.7115
1181.9885 | 784.4166
1182.9885 | 781.6369
1183.9885 | 782.5597
1184.9885 | 782.0015
1185.9885 | 788.2049
1186.9885 | 787.0768
1187.9885 | 791.5965
1188.9885 | 792.7199
1189.9885 | 790.3557
1190.9885 | 790.2073
1191.9885 | 789
1192.9885 | 793.2772
1193.9885 | 791.3306
1194.9885 | 793.7967
1195.9885 | 790.5007
1196.9885 | 788.3232
1197.9885 | 787.5689
1198.9885 | 782.8204
1199.9885 | 780.6751
1200.9885 | 779.4022
1201.9885 | 782.7323
1202.9885 | 782.4325
1203.9885 | 781.5136
1204.9885 | 777.5609
1205.9885 | 780.0726
1206.9885 | 777.5486
1207.9885 | 774.1079
1208.9885 | 773.6076
1209.9885 | 775.2398
1210.9885 | 774.2722
1211.9885 | 780.6072
1212.9885 | 785.031
1213.9885 | 786.4669
1214.9885 | 787.7934
1215.9885 | 787.6029
1216.9885 | 782.3065
1217.9885 | 779.9224
1218.9885 | 776.0131
1219.9885 | 770.7738
1220.9885 | 770.2566
1221.9885 | 772.4873
1222.9885 | 774.003
1223.9885 | 777.2509
1224.9885 | 777.6227
1225.9885 | 780.7984
1226.9885 | 786.5697
1227.9885 | 788.5903
1228.9885 | 779.333
1229.9885 | 787.1735
1230.9885 | 788.6929
1231.9885 | 781.5404
1232.9885 | 778.9339
1233.9885 | 781.5844
1234.9885 | 794.7932
1235.9885 | 796.0737
1236.9885 | 789.2951
1237.9885 | 784.3375
1238.9885 | 781.7271
1239.9885 | 783.3881
1240.9885 | 790.1209
1241.9885 | 792.313
1242.9885 | 799.1754
1243.9885 | 793.4466
1244.9885 | 797.2677
1245.9885 | 788.0173
1246.9885 | 781.4456
1247.9885 | 782.6581
1248.9885 | 785.8893
1249.9885 | 786.2495
1250.9885 | 776.7319
1251.9885 | 775.1722
1252.9885 | 772.632
1253.9885 | 765.9322
1254.9885 | 758.9429
1255.9885 | 767.5104
1256.9885 | 765.3206
1257.9885 | 772.6225
1258.9885 | 776.6298
1259.9885 | 786.776
1260.9885 | 778.1535
1261.9885 | 770.7245
1262.9885 | 769.1041
1263.9885 | 771.5289
1264.9885 | 772.9257
1265.9885 | 773.3462
1266.9885 | 772.1777
1267.9885 | 772.1933
1268.9885 | 775.8802
1269.9885 | 769.777
1270.9885 | 773.3864
1271.9885 | 772.0628
1272.9885 | 767.601
1273.9885 | 766.2949
1274.9885 | 759.9462
1275.9885 | 754.9078
1276.9885 | 758.8463
1277.9885 | 763.2963
1278.9885 | 770.2445
1279.9885 | 768.6461
1280.9885 | 761.1063
1281.9885 | 762.9417
1282.9885 | 764.9278
1283.9885 | 768.5585
1284.9885 | 771.9986
1285.9885 | 767.0394
1286.9885 | 769.9633
1287.9885 | 771.291
1288.9885 | 773.7247
1289.9885 | 770.3456
1290.9885 | 773.6074
1291.9885 | 777.7269
1292.9885 | 777.3352
1293.9885 | 776.5142
1294.9885 | 778.4553
1295.9885 | 779.4825
1296.9885 | 778.6375
1297.9885 | 783.7352
1298.9885 | 775.4662
1299.9885 | 771.4536
1300.9885 | 771.6214
1301.9885 | 770.0888
1303.0042 | 771.1149
1303.9885 | 772.1434
1304.9885 | 773.3504
1305.9885 | 778.7557
1306.9885 | 767.7488
1307.9885 | 769.5331
1308.9885 | 773.301
1309.9885 | 773.3159
1310.9885 | 768.2609
1311.9885 | 775.1144
1312.9885 | 775.2691
1313.9885 | 782.106
1314.9885 | 782.421
1315.9885 | 782.9029
1316.9885 | 783.3344
1317.9885 | 779.371
1318.9885 | 777.127
1319.9885 | 777.6275
1320.9885 | 776.5983
1321.9885 | 770.1986
1322.9885 | 771.5401
1323.9885 | 771.9811
1324.9885 | 763.2414
1325.9885 | 766.0227
1326.9885 | 757.6115
1327.9885 | 766.0912
1328.9885 | 761.5078
1329.9885 | 760.8049
1330.9885 | 758.4201
1331.9885 | 763.7863
1332.9885 | 756.365
1333.9885 | 763.0945
1334.9885 | 762.1936
1335.9885 | 757.9946
1336.9885 | 763.6876
1337.9885 | 766.5516
1338.9885 | 763.5267
1339.9885 | 761.4218
1340.9885 | 760.8298
1341.9885 | 761.0808
1342.9885 | 762.1794
1343.9885 | 762.5194
1344.9885 | 760.0673
1345.9885 | 761.5317
1346.9885 | 772.3882
1347.9885 | 771.5129
1348.9885 | 771.6188
1349.9885 | 778.9703
1350.9885 | 774.5688
1351.9885 | 782.6585
1352.9885 | 775.7807
1353.9885 | 777.1752
1354.9885 | 775.6221
1355.9885 | 775.9249
1356.9885 | 772.8124
1357.9885 | 774.7483
1358.9885 | 774.8716
1359.9885 | 771.7624
1360.9885 | 773.043
1361.9885 | 768.4217
1362.9885 | 764.237
1363.9885 | 768.3595
1364.9885 | 773.3311
1365.9885 | 777.8078
1366.9885 | 775.6515
1367.9885 | 776.5386
1368.9885 | 772.0518
1369.9885 | 774.0447
1370.9885 | 779.376
1371.9885 | 777.9347
1372.9885 | 774.3224
1373.9885 | 771.3681
1374.9885 | 780.5347
1375.9885 | 775.1862
1376.9885 | 777.0086
1377.9885 | 776.2864
1378.9885 | 777.7997
1379.9885 | 767.0439
1380.9885 | 761.1531
1381.9885 | 763.4727
1382.9885 | 766.2958
1383.9885 | 762.0035
1384.9885 | 761.1906
1385.9885 | 766.4306
1386.9885 | 765.0213
1387.9885 | 770.5221
1388.9885 | 776.5036
1389.9885 | 776.3113
1390.9885 | 779.4363
1391.9885 | 778.1003
1392.9885 | 771.762
1393.9885 | 773.0882
1394.9885 | 771.1379
1395.9885 | 769.7219
1396.9885 | 773.6017
1397.9885 | 772.9226
1398.9885 | 770.6805
1399.9885 | 770.3387
1400.9885 | 766.06
1401.9885 | 763.6196
1402.9885 | 757.8446
1403.9885 | 761.9666
1404.9885 | 764.5817
1405.9885 | 758.9464
1406.9885 | 759.9939
1407.9885 | 757.833
1408.9885 | 754.4596
1409.9885 | 749.8473
1410.9885 | 754.7141
1411.9885 | 756.2377
1412.9885 | 764.0889
1413.9885 | 764.8625
1414.9885 | 769.8441
1415.9885 | 782.8108
1416.9885 | 778.3743
1417.9885 | 782.5018
1418.9885 | 786.5446
1419.9885 | 779.0412
1421.0042 | 779.9061
1421.9885 | 781.9738
1422.9885 | 785.2803
1423.9885 | 784.8558
1424.9885 | 784.4036
1425.9885 | 780.1589
1426.9885 | 781.3536
1427.9885 | 780.8877
1428.9885 | 780.4449
1429.9885 | 778.2863
1430.9885 | 774.4778
1431.9885 | 773.183
1432.9885 | 773.1014
1433.9885 | 779.0427
1434.9885 | 772.6008
1435.9885 | 770.6163
1436.9885 | 775.1741
1437.9885 | 779.0356
1438.9885 | 773.386
1439.9885 | 768.3085
1440.9885 | 766.5063
1441.9885 | 766.7089
1442.9885 | 764.1272
1443.9885 | 771.681
1444.9885 | 776.3421
1445.9885 | 771.9437
1446.9885 | 782.2627
1447.9885 | 781.1065
1448.9885 | 788.3896
1449.9885 | 784.7875
1450.9885 | 779.7355
1451.9885 | 781.8267
1452.9885 | 788.4788
1453.9885 | 792.9558
1454.9885 | 796.437
1455.9885 | 796.2071
1456.9885 | 797.5362
1457.9885 | 799.1984
1458.9885 | 796.4154
1459.9885 | 797.9382
1460.9885 | 794.4945
1461.9885 | 794.1691
1462.9885 | 798.4794
1463.9885 | 798.6488
1464.9885 | 795.5034
1465.9885 | 797.1509
1466.9885 | 793.1046
1467.9885 | 793.1243
1468.9885 | 789.1036
1469.9885 | 787.6847
1470.9885 | 783.6142
1471.9885 | 785.5278
1472.9885 | 785.4216
1473.9885 | 787.0407
1474.9885 | 784.3665
1475.9885 | 784.7118
1476.9885 | 786.9281
1477.9885 | 790.1278
1478.9885 | 791.7771
1479.9885 | 788.8552
1480.9885 | 790.9855
1481.9885 | 789.8911
1482.9885 | 788.3245
1483.9885 | 788.1494
1484.9885 | 784.3192
1485.9885 | 783.1605
1486.9885 | 780.2473
1487.9885 | 781.6642
1488.9885 | 783.9902
1489.9885 | 783.2448
1490.9885 | 778.2732
1491.9885 | 773.3736
1492.9885 | 773.7984
1493.9885 | 774.1392
1494.9885 | 779.1726
1495.9885 | 779.052
1496.9885 | 780.4188
1497.9885 | 788.0281
1498.9885 | 791.3327
1499.9885 | 790.0078
1500.9885 | 782.9587
1501.9885 | 786.5681
1502.9885 | 789.1816
1503.9885 | 787.1204
1504.9885 | 790.2087
1505.9885 | 791.3369
1506.9885 | 790.1651
1507.9885 | 795.6493
1508.9885 | 794.5645
1509.9885 | 789.9375
1510.9885 | 788.3806
1511.9885 | 787.7919
1512.9885 | 785.6769
1513.9885 | 789.1998
1514.9885 | 788.7904
1515.9885 | 781.9195
1516.9885 | 788.2997
1517.9885 | 788.1273
1518.9885 | 781.3246
1519.9885 | 775.3578
1520.9885 | 769.8439
1521.9885 | 771.9778
1522.9885 | 775.7597
1523.9885 | 772.8776
1524.9885 | 773.6463
1525.9885 | 767.671
1526.9885 | 767.4824
1527.9885 | 766.6526
1528.9885 | 767.6718
1529.9885 | 766.8943
1530.9885 | 769.1919
1531.9885 | 764.5646
1532.9885 | 761.586
1533.9885 | 760.5764
1534.9885 | 761.0546
1535.9885 | 760.7952
1536.9885 | 763.4741
1537.9885 | 768.9769
1538.9885 | 768.4106
1539.9885 | 764.9263
1540.9885 | 766.2396
1541.9885 | 761.7632
1542.9885 | 763.3637
1543.9885 | 760.8716
1544.9885 | 759.0662
1545.9885 | 763.7984
1546.9885 | 773.6295
1547.9885 | 774.3804
1548.9885 | 770.5526
1549.9885 | 774.8203
1550.9885 | 782.3453
1551.9885 | 780.6214
1552.9885 | 777.5037
1553.9885 | 776.2322
1554.9885 | 777.8375
1555.9885 | 776.4796
1556.9885 | 772.0611
1557.9885 | 769.5694
1558.9885 | 769.3091
1559.9885 | 766.7024
1560.9885 | 777.7651
1561.9885 | 783.4627
1562.9885 | 783.4618
1563.9885 | 777.7284
1564.9885 | 782.4826
1565.9885 | 781.7266
1566.9885 | 783.3711
1567.9885 | 782.9158
1568.9885 | 782.8067
1569.9885 | 785.8213
1570.9885 | 788.6883
1571.9885 | 785.2241
1572.9885 | 788.6734
1573.9885 | 791.7612
1574.9885 | 793.1321
1575.9885 | 786.7246
1576.9885 | 780.7449
1577.9885 | 783.4611
1578.9885 | 786.6335
1579.9885 | 786.2418
1580.9885 | 795.812
1581.9885 | 796.1225
1582.9885 | 789.3171
1583.9885 | 783.8224
1584.9885 | 777.7107
1585.9885 | 774.696
1586.9885 | 774.9012
1587.9885 | 769.247
1588.9885 | 770.4215
1589.9885 | 768.7898
1590.9885 | 769.4222
1591.9885 | 770.67
1592.9885 | 769.4516
1593.9885 | 768.5558
1594.9885 | 766.4264
1595.9885 | 768.4662
1596.9885 | 774.1695
1597.9885 | 777.1863
1598.9885 | 775.8826
1599.9885 | 777.1408
1600.9885 | 777.2508
1601.9885 | 782.6672
1602.9885 | 779.1133
1603.9885 | 777.6736
1604.9885 | 776.0712
1605.9885 | 778.0423
1606.9885 | 776.2369
1607.9885 | 764.2292
1608.9885 | 761.4578
1609.9885 | 764.3726
1610.9885 | 770.3027
1611.9885 | 771.3964
1612.9885 | 769.526
1613.9885 | 762.2497
1614.9885 | 759.2293
1615.9885 | 764.2086
1616.9885 | 770.0789
1617.9885 | 770.3012
1618.9885 | 773.0045
1619.9885 | 773.7869
1620.9885 | 775.6665
1621.9885 | 770.0234
1622.9885 | 771.8017
1623.9885 | 775.1881
1624.9885 | 770.4546
1625.9885 | 777.0872
1626.9885 | 779.7104
1627.9885 | 774.6009
1628.9885 | 772.1861
1629.9885 | 775.488
1630.9885 | 773.0664
1631.9885 | 767.5562
1632.9885 | 771.3773
1633.9885 | 772.7812
1634.9885 | 761.8569
1635.9885 | 758.103
1636.9885 | 760.8987
1637.9885 | 756.2341
1638.9885 | 756.9043
1639.9885 | 761.0958
1640.9885 | 762.9442
1641.9885 | 764.9516
1642.9885 | 764.6605
1643.9885 | 763.894
1644.9885 | 767.1787
1645.9885 | 770.9041
1646.9885 | 766.0857
1647.9885 | 759.9255
1648.9885 | 760.8941
1649.9885 | 756.4715
1650.9885 | 759.667
1651.9885 | 759.2473
1652.9885 | 759.1634
1653.9885 | 759.4332
1654.9885 | 754.0839
1655.9885 | 753.1906
1656.9885 | 754.4722
1657.9885 | 744.4189
1658.9885 | 742.6483
1659.9885 | 748.5341
1660.9885 | 740.1621
1661.9885 | 729.5302
1662.9885 | 737.2123
1663.9885 | 746.4882
1664.9885 | 750.1587
1665.9885 | 750.8783
1666.9885 | 751.7825
1667.9885 | 754.5783
1668.9885 | 758.6745
1669.9885 | 763.3865
1670.9885 | 769.8141
1671.9885 | 769.5577
1672.9885 | 770.2854
1673.9885 | 778.5873
1674.9885 | 774.6495
1675.9885 | 779.5516
1676.9885 | 773.1431
1677.9885 | 760.0564
1678.9885 | 756.6561
1679.9885 | 753.8636
1680.9885 | 751.0603
1681.9885 | 748.3003
1682.9885 | 750.0126
1683.9885 | 748.0406
1684.9885 | 756.5129
1685.9885 | 758.2151
1686.9885 | 757.7217
1687.9885 | 761.0382
1688.9885 | 753.1904
1689.9885 | 756.8124
1690.9885 | 758.5784
1691.9885 | 762.0046
1692.9885 | 761.2713
1693.9885 | 759.2075
1694.9885 | 758.7951
1695.9885 | 759.2273
1696.9885 | 749.9369
1697.9885 | 748.3815
1698.9885 | 752.1065
1699.9885 | 758.1032
1700.9885 | 761.9149
1701.9885 | 767.0595
1702.9885 | 771.0756
1703.9885 | 771.2107
1704.9885 | 768.6121
1705.9885 | 776.1427
1706.9885 | 774.5759
1707.9885 | 776.8475
1708.9885 | 786.3991
1709.9885 | 787.4792
1710.9885 | 786.1072
1711.9885 | 785.0871
1712.9885 | 787.4125
1713.9885 | 786.9674
1714.9885 | 784.0583
1715.9885 | 788.0537
1716.9885 | 786.1349
1717.9885 | 787.1183
1718.9885 | 787.072
1719.9885 | 781.9955
1720.9885 | 770.273
1721.9885 | 768.489
1722.9885 | 775.0852
1723.9885 | 781.8248
1724.9885 | 779.2489
1725.9885 | 781.2828
1726.9885 | 786.9887
1727.9885 | 789.6929
1728.9885 | 786.146
1729.9885 | 785.8778
1730.9885 | 785.1264
1731.9885 | 773.7298
1732.9885 | 773.1273
1733.9885 | 773.8399
1734.9885 | 776.9511
1735.9885 | 777.9443
1736.9885 | 781.8827
1737.9885 | 782.7209
1738.9885 | 783.4074
1739.9885 | 783.6565
1740.9885 | 783.6193
1741.9885 | 787.0928
1742.9885 | 792.8586
1743.9885 | 795.5897
1744.9885 | 800.6271
1745.9885 | 792.1869
1746.9885 | 783.8708
1747.9885 | 786.172
1748.9885 | 789.4953
1749.9885 | 792.7936
1750.9885 | 789.9773
1751.9885 | 790.2478
1752.9885 | 789.6301
1753.9885 | 797.6595
1754.9885 | 798.9081
1755.9885 | 797.5002
1756.9885 | 795.6444
1757.9885 | 796.1303
1758.9885 | 801.6096
1759.9885 | 804.9638
1760.9885 | 812.532
1761.9885 | 811.7902
1762.9885 | 811.8617
1763.9885 | 805.0989
1764.9885 | 798.7489
1765.9885 | 797.9711
1766.9885 | 796.8385
1767.9885 | 801.1384
1768.9885 | 799.2963
1769.9885 | 810.7655
1770.9885 | 807.8533
1771.9885 | 806.2148
1772.9885 | 802.5239
1773.9885 | 804.0305
1774.9885 | 810.2621
1775.9885 | 811.8756
1776.9885 | 814.1591
1777.9885 | 818.0328
1778.9885 | 814.4369
1779.9885 | 812.607
1780.9885 | 815.3959
1781.9885 | 815.29
1782.9885 | 813.3058
1783.9885 | 806.5483
1784.9885 | 805.5424
1785.9885 | 802.2964
1786.9885 | 801.0814
1787.9885 | 803.2005
1788.9885 | 808.0713
1789.9885 | 805.7196
1790.9885 | 800.8023
1791.9885 | 800.5555
1792.9885 | 804.1216
1793.9885 | 806.1391
1794.9885 | 807.6266
1795.9885 | 804.4924
1796.9885 | 804.7778
1797.9885 | 807.932
1798.9885 | 806.7626
1799.9885 | 801.8766
1800.9885 | 796.8176
1801.9885 | 792.8485
1802.9885 | 794.0254
1803.9885 | 793.2119
1804.9885 | 791.4068
1805.9885 | 791.1909
1806.9885 | 795.3682
1807.9885 | 794.5753
1808.9885 | 795.2826
1809.9885 | 793.0103
1810.9885 | 791.9073
1811.9885 | 792.5806
1812.9885 | 790.3258
1813.9885 | 791.7743
1814.9885 | 794.0679
1815.9885 | 792.6277
1816.9885 | 787.2375
1817.9885 | 787.2847
1818.9885 | 794.1163
1819.9885 | 796.6574
1820.9885 | 790.676
1821.9885 | 787.358
1822.9885 | 791.0536
1823.9885 | 789.095
1824.9885 | 788.8087
1825.9885 | 789.9225
1826.9885 | 789.2939
1827.9885 | 786.4486
1828.9885 | 772.0062
1829.9885 | 762.993
1830.9885 | 754.448
1831.9885 | 750.3016
1832.9885 | 757.4074
1833.9885 | 760.1301
1834.9885 | 760.5209
1835.9885 | 755.7447
1836.9885 | 764.9193
1837.9885 | 769.2593
1838.9885 | 772.736
1839.9885 | 775.6683
1840.9885 | 775.943
1841.9885 | 778.6417
1842.9885 | 788.3266
1843.9885 | 798.2152
1844.9885 | 795.5936
1845.9885 | 799.3596
1846.9885 | 796.8851
1847.9885 | 793.0247
1848.9885 | 795.3428
1849.9885 | 794.3758
1850.9885 | 799.6262
1851.9885 | 799.0686
1852.9885 | 798.2709
1853.9885 | 794.5132
1854.9885 | 792.3443
1855.9885 | 793.8241
1856.9885 | 789.207
1857.9885 | 791.7037
1858.9885 | 794.9028
1859.9885 | 798.5844
1860.9885 | 795.5793
1861.9885 | 795.6651
1862.9885 | 792.7789
1863.9885 | 787.4482
1864.9885 | 787.2079
1865.9885 | 791.3795
1866.9885 | 788.5293
1867.9885 | 788.3228
1868.9885 | 790.9366
1869.9885 | 793.1292
1870.9885 | 799.1937
1871.9885 | 800.2994
1872.9885 | 799.1993
1873.9885 | 801.2734
1874.9885 | 800.6754
1875.9885 | 802.3229
1876.9885 | 794.2549
1877.9885 | 791.6652
1878.9885 | 792.4064
1879.9885 | 790.427
1880.9885 | 792.8928
1881.9885 | 790.4044
1882.9885 | 790.9688
1883.9885 | 783.3031
1884.9885 | 780.564
1885.9885 | 779.6682
1886.9885 | 778.8526
1887.9885 | 783.9766
1888.9885 | 784.6525
1889.9885 | 782.4547
1890.9885 | 785.6048
1891.9885 | 786.9116
1892.9885 | 780.013
1893.9885 | 778.4698
1894.9885 | 774.3828
1895.9885 | 772.7242
1896.9885 | 770.2305
1897.9885 | 774.4937
1898.9885 | 777.2175
1899.9885 | 780.42
1900.9885 | 782.9589
1901.9885 | 778.78
1902.9885 | 775.2726
1903.9885 | 777.168
1904.9885 | 772.4077
1905.9885 | 776.2573
1906.9885 | 781.1315
1907.9885 | 783.9363
1908.9885 | 785.8534
1909.9885 | 777.2605
1910.9885 | 771.2586
1911.9885 | 771.7422
1912.9885 | 771.6288
1913.9885 | 768.8142
1914.9885 | 770.91
1915.9885 | 776.587
1916.9885 | 775.4093
1917.9885 | 780.1005
1918.9885 | 779.2071
1919.9885 | 775.0157
1920.9885 | 772.4356
1921.9885 | 769.4367
1922.9885 | 763.8053
1923.9885 | 766.9475
1924.9885 | 758.2405
1925.9885 | 767.957
1926.9885 | 769.724
1927.9885 | 770.6359
1928.9885 | 769.8789
1929.9885 | 771.6848
1930.9885 | 769.9112
1931.9885 | 767.0864
1932.9885 | 770.3386
1933.9885 | 766.9753
1934.9885 | 762.6022
1935.9885 | 751.198
1936.9885 | 751.9257
1937.9885 | 755.4273
1938.9885 | 742.2187
1939.9885 | 738.4922
1940.9885 | 733.222
1941.9885 | 735.3162
1942.9885 | 736.298
1943.9885 | 733.4145
1944.9885 | 727.8958
1945.9885 | 723.4052
1946.9885 | 726.2356
1947.9885 | 726.5461
1948.9885 | 731.655
1949.9885 | 732.957
1950.9885 | 728.0323
1951.9885 | 726.5613
1952.9885 | 734.9342
1953.9885 | 743.5683
1954.9885 | 743.0424
1955.9885 | 747.1798
1956.9885 | 757.4748
1957.9885 | 760.4145
1958.9885 | 763.761
1959.9885 | 748.1816
1960.9885 | 744.3721
1961.9885 | 741.7537
1962.9885 | 741.8398
1963.9885 | 730.993
1964.9885 | 735.6566
1965.9885 | 743.9856
1966.9885 | 747.315
1967.9885 | 752.97
1968.9885 | 753.2159
1969.9885 | 754.1219
1970.9885 | 761.958
1971.9885 | 754.9152
1972.9885 | 758.0289
1973.9885 | 762.2021
1974.9885 | 763.3469
1975.9885 | 762.6458
1976.9885 | 768.31
1977.9885 | 772.7995
1978.9885 | 773.7882
1979.9885 | 764.439
1980.9885 | 758.9995
1981.9885 | 763.0552
1982.9885 | 761.577
1983.9885 | 766.9352
1984.9885 | 765.6227
1985.9885 | 761.4459
1986.9885 | 758.9606
1987.9885 | 760.3764
1988.9885 | 758.946
1989.9885 | 760.2977
1990.9885 | 762.6373
1991.9885 | 763.0716
1992.9885 | 766.1643
1993.9885 | 767.3837
1994.9885 | 760.4122
1995.9885 | 767.8163
1996.9885 | 767.9625
1997.9885 | 773.0824
1998.9885 | 768.774
1999.9885 | 760.5081
2000.9885 | 769.9928
2001.9885 | 773.8337
2002.9885 | 781.0541
2003.9885 | 785.4747
2004.9885 | 783.9308
2005.9885 | 781.456
2006.9885 | 779.4818
2007.9885 | 775.4737
2008.9885 | 769.4003
2009.9885 | 765.9796
2010.9885 | 763.1204
2011.9885 | 765.5859
2012.9885 | 766.3931
2013.9885 | 764.4066
2014.9885 | 762.365
2015.9885 | 759.9783
2016.9885 | 759.3702
2017.9885 | 747.7261
2018.9885 | 747.3845
2019.9885 | 738.9145
2020.9885 | 741.962
2021.9885 | 743.8505
2022.9885 | 739.3161
2023.9885 | 740.9804
2024.9885 | 739.9123
2025.9885 | 741.1887
2026.9885 | 745.1896
2027.9885 | 749.7067
2028.9885 | 755.8569
2029.9885 | 762.4883
2030.9885 | 764.4972
2031.9885 | 764.4176
2032.9885 | 755.648
2033.9885 | 755.5935
2034.9885 | 751.561
2035.9885 | 747.995
2036.9885 | 748.9352
2037.9885 | 750.3327
2038.9885 | 754.9837
2039.9885 | 752.2407
2040.9885 | 761.7315
2041.9885 | 765.3818
2042.9885 | 770.0453
2043.9885 | 769.0985
2044.9885 | 767.3121
2045.9885 | 757.9748
2046.9885 | 752.7155
2047.9885 | 751.0305
2048.9885 | 751.1755
2049.9885 | 757.6552
2050.9885 | 757.6665
2051.9885 | 762.2521
2052.9885 | 762.1395
2053.9885 | 765.575
2054.9885 | 765.1227
2055.9885 | 765.6126
2056.9885 | 763.0438
2057.9885 | 753.7474
2058.9885 | 756.4034
2059.9885 | 764.7986
2060.9885 | 766.3404
2061.9885 | 766.6584
2062.9885 | 760.9393
2063.9885 | 763.9129
2064.9885 | 764.8636
2065.9885 | 761.9659
2066.9885 | 758.6597
2067.9885 | 756.944
2068.9885 | 759.3291
2069.9885 | 754.2909
2070.9885 | 751.1205
2071.9885 | 745.2866
2072.9885 | 740.4863
2073.9885 | 739.6505
2074.9885 | 741.2517
2075.9885 | 744.1987
2076.9885 | 745.6711
2077.9885 | 744.6754
2078.9885 | 749.4563
2079.9885 | 748.0307
2080.9885 | 750.1497
2081.9885 | 746.7433
2082.9885 | 744.0645
2083.9885 | 747.2138
2084.9885 | 736.2703
2085.9885 | 734.4252
2086.9885 | 739.5227
2087.9885 | 741.1209
2088.9885 | 748.7026
2089.9885 | 746.9854
2090.9885 | 741.285
2091.9885 | 738.7214
2092.9885 | 737.0064
2093.9885 | 745.5689
2094.9885 | 748.5454
2095.9885 | 753.2621
2096.9885 | 751.0723
2097.9885 | 752.2015
2098.9885 | 745.9061
2099.9885 | 741.1887
2100.9885 | 746.2144
2101.9885 | 749.3396
2102.9885 | 745.3905
2103.9885 | 752.1723
2104.9885 | 753.4842
2105.9885 | 756.5779
2106.9885 | 757.7126
2107.9885 | 756.2518
2108.9885 | 756.7647
2109.9885 | 754.958
2110.9885 | 753.3882
2112.0042 | 752.0007
2112.9885 | 747.0081
2113.9885 | 741.3507
2114.9885 | 737.8533
2115.9885 | 737.1509
2116.9885 | 739.2884
2117.9885 | 739.5073
2118.9885 | 739.1331
2119.9885 | 745.1813
2120.9885 | 742.2451
2121.9885 | 739.7858
2122.9885 | 748.0875
2123.9885 | 747.3895
2124.9885 | 731.9688
2125.9885 | 738.7916
2126.9885 | 741.0421
2127.9885 | 730.9283
2128.9885 | 736.7317
2129.9885 | 741.5493
2130.9885 | 740.2884
2131.9885 | 731.9442
2132.9885 | 737.9378
2133.9885 | 740.7915
2134.9885 | 741.8718
2135.9885 | 739.6918
2136.9885 | 750.9203
2137.9885 | 748.5539
2138.9885 | 748.1765
2139.9885 | 750.8402
2140.9885 | 750.8216
2141.9885 | 750.4817
2142.9885 | 747.293
2143.9885 | 748.7341
2144.9885 | 753.2538
2145.9885 | 755.461
2146.9885 | 759.2321
2147.9885 | 759.9633
2148.9885 | 749.2223
2149.9885 | 745.0932
2150.9885 | 729.2267
2151.9885 | 732.7048
2152.9885 | 737.1206
2153.9885 | 735.1029
2154.9885 | 740.4895
2155.9885 | 736.9954
2156.9885 | 738.2878
2157.9885 | 738.6293
2158.9885 | 744.345
2159.9885 | 748.6835
2160.9885 | 755.1962
2161.9885 | 761.8957
2162.9885 | 769.0356
2163.9885 | 774.5755
2164.9885 | 771.0345
2165.9885 | 771.5675
2166.9885 | 778.8989
2167.9885 | 783.8448
2168.9885 | 781.3481
2169.9885 | 771.1485
2170.9885 | 767.0752
2171.9885 | 770.0514
2172.9885 | 769.3881
2173.9885 | 773.8277
2174.9885 | 759.7808
2175.9885 | 762.4717
2176.9885 | 766.5865
2177.9885 | 765.1431
2178.9885 | 761.9058
2179.9885 | 755.7479
2180.9885 | 743.4621
2181.9885 | 749.1029
2182.9885 | 744.4952
2183.9885 | 742.2156
2184.9885 | 738.6423
2185.9885 | 737.899
2186.9885 | 734.2476
2187.9885 | 740.8533
2188.9885 | 750.6183
2189.9885 | 747.7214
2190.9885 | 744.3136
2191.9885 | 747.9339
2192.9885 | 754.0522
2193.9885 | 759.374
2194.9885 | 762.2657
2195.9885 | 760.9384
2196.9885 | 767.9482
2197.9885 | 775.7735
2198.9885 | 781.2681
2199.9885 | 774.2395
2200.9885 | 774.7789
2201.9885 | 771.7487
2202.9885 | 771.4726
2203.9885 | 773.3101
2204.9885 | 779.0567
2205.9885 | 773.7559
2206.9885 | 769.86
2207.9885 | 770.4387
2208.9885 | 770.8673
2209.9885 | 768.875
2210.9885 | 769.8046
2211.9885 | 769.9544
2212.9885 | 760.083
2213.9885 | 756.6029
2214.9885 | 761.6757
2215.9885 | 761.0974
2216.9885 | 762.4977
2217.9885 | 763.8797
2218.9885 | 759.429
2219.9885 | 756.5028
2220.9885 | 768.495
2221.9885 | 773.1745
2222.9885 | 778.2231
2223.9885 | 778.2451
2224.9885 | 778.8508
2225.9885 | 775.6271
2226.9885 | 771.8857
2227.9885 | 773.9754
2228.9885 | 771.167
2229.9885 | 760.884
2230.9885 | 757.7159
2231.9885 | 753.6564
2232.9885 | 745.8324
2233.9885 | 750.6371
2234.9885 | 751.1813
2235.9885 | 751.4408
2236.9885 | 753.5944
2237.9885 | 756.1955
2238.9885 | 751.2817
2239.9885 | 756.2312
2240.9885 | 756.1035
2241.9885 | 757.2546
2242.9885 | 751.2289
2243.9885 | 748.9526
2244.9885 | 753.0879
2245.9885 | 757.5776
2246.9885 | 757.7165
2247.9885 | 758.9714
2248.9885 | 769.1512
2249.9885 | 762.2137
2250.9885 | 753.4916
2251.9885 | 757.0186
2252.9885 | 754.5358
2253.9885 | 758.1002
2254.9885 | 754.7773
2255.9885 | 754.6427
2256.9885 | 753.156
2257.9885 | 743.8422
2258.9885 | 741.6884
2259.9885 | 741.0138
2260.9885 | 742.1101
2261.9885 | 741.9103
2262.9885 | 740.3921
2263.9885 | 738.4653
2264.9885 | 733.9744
2265.9885 | 734.9938
2266.9885 | 733.5466
2267.9885 | 726.904
2268.9885 | 723.1229
2269.9885 | 725.0007
2270.9885 | 727.5651
2271.9885 | 736.0222
2272.9885 | 741.7113
2273.9885 | 750.0261
2274.9885 | 752.8415
2275.9885 | 749.9197
2276.9885 | 748.6905
2277.9885 | 749.3722
2278.9885 | 754.9643
2279.9885 | 751.5985
2280.9885 | 742.2625
2281.9885 | 739.399
2282.9885 | 741.1533
2283.9885 | 747.7666
2284.9885 | 756.7759
2285.9885 | 762.6038
2286.9885 | 772.8852
2287.9885 | 767.3626
2288.9885 | 768.1159
2289.9885 | 779.3473
2290.9885 | 788.3832
2291.9885 | 789.3098
2292.9885 | 790.2568
2293.9885 | 790.9497
2294.9885 | 798.5498
2295.9885 | 795.6394
2296.9885 | 789.1209
2297.9885 | 788.518
2298.9885 | 786.1341
2299.9885 | 783.6362
2300.9885 | 781.6549
2301.9885 | 774.4006
2302.9885 | 774.4954
2303.9885 | 773.6435
2304.9885 | 770.7671
2305.9885 | 772.6204
2306.9885 | 777.6685
2307.9885 | 780.1673
2308.9885 | 779.6829
2309.9885 | 776.3653
2310.9885 | 769.957
2311.9885 | 765.5121
2312.9885 | 766.1584
2313.9885 | 761.9584
2314.9885 | 755.5734
2315.9885 | 746.6832
2316.9885 | 750.7872
2317.9885 | 751.1551
2318.9885 | 750.0943
2319.9885 | 747.5555
2320.9885 | 752.6071
2321.9885 | 748.5521
2322.9885 | 743.6738
2323.9885 | 741.7903
2324.9885 | 745.0649
2325.9885 | 743.7636
2326.9885 | 739.7924
2327.9885 | 749.1986
2328.9885 | 749.5233
2329.9885 | 748.727
2330.9885 | 738.8794
2331.9885 | 732.4146
2332.9885 | 733.8887
2333.9885 | 730.18
2334.9885 | 728.3355
2335.9885 | 733.7532
2336.9885 | 737.6266
2337.9885 | 733.649
2338.9885 | 731.868
2339.9885 | 729.8069
2340.9885 | 733.5487
2341.9885 | 736.2294
2342.9885 | 734.538
2343.9885 | 723.1671
2344.9885 | 714.7836
2345.9885 | 719.322
2346.9885 | 723.012
2347.9885 | 724.8531
2348.9885 | 716.1789
2349.9885 | 731.5502
2350.9885 | 733.4973
2351.9885 | 737.8029
2352.9885 | 731.5305
2353.9885 | 724.3689
2354.9885 | 733.0349
2355.9885 | 738.8671
2356.9885 | 740.2727
2357.9885 | 736.3651
2358.9885 | 732.4161
2359.9885 | 742.4362
2360.9885 | 740.272
2361.9885 | 731.6732
2362.9885 | 717.2784
2363.9885 | 706.9961
2364.9885 | 711.2501
2365.9885 | 714.1706
2366.9885 | 716.0249
2367.9885 | 724.9455
2368.9885 | 731.033
2369.9885 | 734.3515
2370.9885 | 735.9248
2371.9885 | 731.0427
2372.9885 | 718.6485
2373.9885 | 713.1563
2374.9885 | 713.6786
2375.9885 | 721.1817
2376.9885 | 730.4137
2377.9885 | 736.6011
2378.9885 | 744.1389
2379.9885 | 742.1689
2380.9885 | 735.8992
2381.9885 | 732.3742
2382.9885 | 732.341
2383.9885 | 744.8946
2384.9885 | 745.9
2385.9885 | 750.8036
2386.9885 | 754.5914
2387.9885 | 759.9884
2388.9885 | 764.2608
2389.9885 | 766.6425
2390.9885 | 768.9578
2391.9885 | 770.7665
2392.9885 | 765.4614
2393.9885 | 759.8207
2394.9885 | 753.0395
2395.9885 | 749.9658
2396.9885 | 746.7841
2397.9885 | 747.7635
2398.9885 | 755.2699
2399.9885 | 750.5748
2400.9885 | 752.1188
2401.9885 | 749.9367
2402.9885 | 757.0147
2403.9885 | 753.8114
2404.9885 | 761.3342
2405.9885 | 757.0358
2406.9885 | 750.7021
2407.9885 | 751.7126
2408.9885 | 743.9212
2409.9885 | 739.2918
2410.9885 | 737.7623
2411.9885 | 740.1009
2412.9885 | 750.5153
2413.9885 | 751.2059
2414.9885 | 750.8653
2415.9885 | 744.588
2416.9885 | 748.6335
2417.9885 | 756.0079
2418.9885 | 760.9745
2419.9885 | 753.9263
2420.9885 | 749.1809
2421.9885 | 746.9417
2422.9885 | 747.5811
2423.9885 | 741.3316
2424.9885 | 746.0803
2425.9885 | 750.6194
2426.9885 | 747.8822
2427.9885 | 753.1326
2428.9885 | 749.9505
2429.9885 | 743.3657
2430.9885 | 742.9736
2431.9885 | 738.6211
2432.9885 | 730.1574
2433.9885 | 724.603
2434.9885 | 737.2727
2435.9885 | 733.0646
2436.9885 | 727.9667
2437.9885 | 733.8797
2438.9885 | 735.331
2439.9885 | 719.8511
2440.9885 | 716.5927
2441.9885 | 716.1816
2442.9885 | 714.8791
2443.9885 | 719.2527
2444.9885 | 724.8152
2445.9885 | 729.9417
2446.9885 | 724.9739
2447.9885 | 724.0158
2448.9885 | 720.0593
2449.9885 | 722.2998
2450.9885 | 712.9303
2451.9885 | 707.789
2452.9885 | 708.6847
2453.9885 | 714.5816
2454.9885 | 719.197
2455.9885 | 720.7744
2456.9885 | 724.8515
2457.9885 | 725.4482
2458.9885 | 731.3693
2459.9885 | 729.6641
2460.9885 | 728.9757
2461.9885 | 721.1508
2462.9885 | 730.0018
2463.9885 | 735.7139
2464.9885 | 735.2578
2465.9885 | 728.0364
2466.9885 | 724.6175
2467.9885 | 733.1246
2468.9885 | 738.5644
2469.9885 | 727.867
2470.9885 | 719.2349
2471.9885 | 717.0745
2472.9885 | 719.3866
2473.9885 | 728.5454
2474.9885 | 730.6248
2475.9885 | 720.3567
2476.9885 | 719.9854
2477.9885 | 720.4709
2478.9885 | 720.4949
2479.9885 | 716.5576
2480.9885 | 714.0215
2481.9885 | 721.9208
2482.9885 | 719.4375
2483.9885 | 724.0665
2484.9885 | 727.0665
2485.9885 | 729.513
2486.9885 | 727.9
2487.9885 | 734.3163
2488.9885 | 734.4868
2489.9885 | 732.9456
2490.9885 | 733.2705
2491.9885 | 736.3003
2492.9885 | 736.8509
2493.9885 | 734.782
2494.9885 | 730.9177
2495.9885 | 733.4597