## Test Conditions
DESIREE-FIRE Intermediate Scale Test 8 - Circuit Simulator Data Only
Test Date: | 2009-11-17
DCSim DAQ Start Time | 10:35
DCSim Time for Synchronization | 10:38
Heat Source Synchronization | 0:03 | hours:minutes:seconds
Heat Source DAQ Start Time | 10:35
Fire Time | 11:34
Offset | 0:59 | hours:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 3565 | seconds
Heat Source Offset | 0:59 | hours:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 3568 | seconds
Heat Source Stop Time | 12:16
Test Duration | 0:42 | hours:minutes:seconds
| 2495 | seconds
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
Intercable Configuration | PE/PVC, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 1 which is defined as "B Position - Middle" in the Temperature Data File respresents the temperature in the center of the cable tray.
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds.
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | Int-Cab_VT7-T1 | Int-Cab_VT7-T2 | Int-Cab_VT7-T3 | Int-Cab_VT7-T4 | Int-Cab_VT7-T5 | Int-Cab_VT7-T6 | Int-Cab_VT7-T7 | Int-Cab_VTU-S1+a | Int-Cab_VTU-S1+b | Int-Cab_VTU-S2+a | Int-Cab_VTU-S2+b | Int-Cab_VTU-S1-a | Int-Cab_VTU-S1-b | Int-Cab_VTU-S2-a | Int-Cab_VTU-S2-b | T1-V(Batt -) | T2 -V(Batt -) | T3 - V(Batt -) | T4 - V(Batt -) | T5 - V(Batt -) | T6 - V(Batt -) | T7 - V(Batt -) | {S1+a} - V(Batt - ) | {S1+b} - V(Batt - ) | {S2+a} - V(Batt - ) | {S2+b} - V(Batt - ) | {S1-a} - V(Batt -) | {S1-b} - V(Batt - ) | {S2-a} - V(Batt - ) | {S2-b} - V(Batt - ) | {S1+a} - {S1-a} | {S1+a} - {S2-a} | {S2+a} - {S1-a} | {S2+a} - {S2-a}
-1.5156 | 121.7834 | -61.7889 | 59.8022 | 0.11727 | 0.009846 | -0.007421 | -0.020438 | 0.008797 | 0.10848 | -0.12681 | 59.5683 | 59.6222 | 59.637 | 59.5951 | 61.6476 | 61.7172 | 61.5321 | 61.674 | 0.16763 | 0.0602 | 0.042933 | 0.029916 | 0.059151 | 0.15883 | -0.076458 | 59.6187 | 59.6725 | 59.6874 | 59.6454 | 61.6979 | 61.7676 | 61.5825 | 61.7243 | -2.0792 | -1.9637 | -2.0105 | -1.8951
0.23438 | 121.8613 | -61.7935 | 59.7427 | 0.12185 | 0.019004 | 0.001736 | -0.025017 | 0.013375 | 0.1039 | -0.13597 | 59.5729 | 59.6359 | 59.6416 | 59.6088 | 61.6384 | 61.7127 | 61.5367 | 61.674 | 0.1722 | 0.069358 | 0.05209 | 0.025337 | 0.063729 | 0.15425 | -0.085614 | 59.6233 | 59.6862 | 59.692 | 59.6591 | 61.6888 | 61.763 | 61.587 | 61.7243 | -2.0655 | -1.9638 | -1.9968 | -1.8951
1.9844 | 121.8979 | -61.6882 | 59.8434 | 0.11727 | 0.009846 | -0.007421 | -0.029595 | 0.013375 | 0.099318 | -0.13139 | 59.5729 | 59.6267 | 59.637 | 59.5996 | 61.6384 | 61.7172 | 61.5321 | 61.674 | 0.16763 | 0.0602 | 0.042933 | 0.020759 | 0.063729 | 0.14967 | -0.081036 | 59.6233 | 59.6771 | 59.6874 | 59.65 | 61.6888 | 61.7676 | 61.5825 | 61.7243 | -2.0655 | -1.9592 | -2.0014 | -1.8951
3.6562 | 121.8567 | -61.7889 | 59.7427 | 0.12643 | 0.019004 | -0.007421 | -0.025017 | 0.004219 | 0.1039 | -0.13139 | 59.5683 | 59.6267 | 59.6416 | 59.5996 | 61.643 | 61.7172 | 61.5321 | 61.6786 | 0.17678 | 0.069358 | 0.042933 | 0.025337 | 0.054573 | 0.15425 | -0.081036 | 59.6187 | 59.6771 | 59.692 | 59.65 | 61.6933 | 61.7676 | 61.5825 | 61.7289 | -2.0746 | -1.9637 | -2.0014 | -1.8905
5.3906 | 121.8704 | -61.7661 | 59.7244 | 0.12185 | 0.019004 | -0.002842 | -0.020438 | 0.008797 | 0.099318 | -0.13597 | 59.5729 | 59.6267 | 59.6325 | 59.6042 | 61.6476 | 61.7127 | 61.5229 | 61.674 | 0.1722 | 0.069358 | 0.047512 | 0.029916 | 0.059151 | 0.14967 | -0.085614 | 59.6233 | 59.6771 | 59.6828 | 59.6546 | 61.6979 | 61.763 | 61.5733 | 61.7243 | -2.0746 | -1.95 | -2.0151 | -1.8905
7.125 | 121.8796 | -61.7615 | 59.761 | 0.12643 | 0.009846 | -0.007421 | -0.025017 | 0.013375 | 0.1039 | -0.13139 | 59.5683 | 59.6267 | 59.637 | 59.6088 | 61.6476 | 61.7127 | 61.5275 | 61.6786 | 0.17678 | 0.0602 | 0.042933 | 0.025337 | 0.063729 | 0.15425 | -0.081036 | 59.6187 | 59.6771 | 59.6874 | 59.6591 | 61.6979 | 61.763 | 61.5779 | 61.7289 | -2.0792 | -1.9592 | -2.0105 | -1.8905
8.875 | 121.7743 | -61.8073 | 59.7519 | 0.12185 | 0.014425 | 0.001736 | -0.01586 | 0.017953 | 0.10848 | -0.12681 | 59.5775 | 59.6267 | 59.6416 | 59.5996 | 61.6384 | 61.7127 | 61.5275 | 61.674 | 0.1722 | 0.064779 | 0.05209 | 0.034494 | 0.068307 | 0.15883 | -0.076458 | 59.6279 | 59.6771 | 59.692 | 59.65 | 61.6888 | 61.763 | 61.5779 | 61.7243 | -2.0609 | -1.95 | -1.9968 | -1.8859
10.5469 | 121.8842 | -61.6745 | 59.8251 | 0.12643 | 0.019004 | -0.007421 | -0.025017 | -0.000359 | 0.1039 | -0.14055 | 59.5683 | 59.6267 | 59.637 | 59.6042 | 61.6384 | 61.7127 | 61.5321 | 61.674 | 0.17678 | 0.069358 | 0.042933 | 0.025337 | 0.049995 | 0.15425 | -0.090192 | 59.6187 | 59.6771 | 59.6874 | 59.6546 | 61.6888 | 61.763 | 61.5825 | 61.7243 | -2.0701 | -1.9637 | -2.0014 | -1.8951
12.2812 | 121.8796 | -61.7111 | 59.8251 | 0.12185 | 0.019004 | -0.012 | -0.020438 | -0.000359 | 0.090161 | -0.13139 | 59.5683 | 59.6267 | 59.637 | 59.5996 | 61.6521 | 61.7081 | 61.5321 | 61.674 | 0.1722 | 0.069358 | 0.038354 | 0.029916 | 0.049995 | 0.14052 | -0.081036 | 59.6187 | 59.6771 | 59.6874 | 59.65 | 61.7025 | 61.7584 | 61.5825 | 61.7243 | -2.0838 | -1.9637 | -2.0151 | -1.8951
14.0312 | 121.7514 | -61.7294 | 59.8709 | 0.12185 | 0.019004 | -0.012 | -0.020438 | 0.004219 | 0.09474 | -0.13139 | 59.5729 | 59.6267 | 59.6416 | 59.5996 | 61.643 | 61.7081 | 61.5321 | 61.6694 | 0.1722 | 0.069358 | 0.038354 | 0.029916 | 0.054573 | 0.14509 | -0.081036 | 59.6233 | 59.6771 | 59.692 | 59.65 | 61.6933 | 61.7584 | 61.5825 | 61.7198 | -2.0701 | -1.9592 | -2.0014 | -1.8905
15.7812 | 121.8338 | -61.734 | 59.7977 | 0.11727 | 0.019004 | -0.012 | -0.025017 | 0.008797 | 0.099318 | -0.13139 | 59.5683 | 59.6359 | 59.6325 | 59.5951 | 61.6384 | 61.7172 | 61.5184 | 61.674 | 0.16763 | 0.069358 | 0.038354 | 0.025337 | 0.059151 | 0.14967 | -0.081036 | 59.6187 | 59.6862 | 59.6828 | 59.6454 | 61.6888 | 61.7676 | 61.5687 | 61.7243 | -2.0701 | -1.95 | -2.0059 | -1.8859
17.4688 | 121.7468 | -61.8347 | 59.7519 | 0.11727 | 0.028162 | 0.001736 | -0.025017 | 0.008797 | 0.1039 | -0.12223 | 59.5683 | 59.6222 | 59.6279 | 59.6042 | 61.6384 | 61.7127 | 61.5275 | 61.674 | 0.16763 | 0.078516 | 0.05209 | 0.025337 | 0.059151 | 0.15425 | -0.07188 | 59.6187 | 59.6725 | 59.6782 | 59.6546 | 61.6888 | 61.763 | 61.5779 | 61.7243 | -2.0701 | -1.9592 | -2.0105 | -1.8996
19.2188 | 121.875 | -61.6699 | 59.8526 | 0.12643 | 0.019004 | -0.012 | -0.025017 | 0.013375 | 0.099318 | -0.13139 | 59.5729 | 59.6267 | 59.6416 | 59.5951 | 61.6338 | 61.7172 | 61.5321 | 61.674 | 0.17678 | 0.069358 | 0.038354 | 0.025337 | 0.063729 | 0.14967 | -0.081036 | 59.6233 | 59.6771 | 59.692 | 59.6454 | 61.6842 | 61.7676 | 61.5825 | 61.7243 | -2.0609 | -1.9592 | -1.9922 | -1.8905
20.8906 | 121.7697 | -61.821 | 59.7427 | 0.11727 | 0.019004 | -0.007421 | -0.025017 | 0.013375 | 0.11305 | -0.12681 | 59.5683 | 59.6222 | 59.6416 | 59.5951 | 61.643 | 61.7081 | 61.5321 | 61.674 | 0.16763 | 0.069358 | 0.042933 | 0.025337 | 0.063729 | 0.16341 | -0.076458 | 59.6187 | 59.6725 | 59.692 | 59.6454 | 61.6933 | 61.7584 | 61.5825 | 61.7243 | -2.0746 | -1.9637 | -2.0014 | -1.8905
22.6406 | 121.756 | -61.8439 | 59.7565 | 0.12185 | 0.019004 | 0.001736 | -0.025017 | 0.013375 | 0.1039 | -0.13139 | 59.5683 | 59.6267 | 59.637 | 59.5951 | 61.6338 | 61.7127 | 61.5275 | 61.6694 | 0.1722 | 0.069358 | 0.05209 | 0.025337 | 0.063729 | 0.15425 | -0.081036 | 59.6187 | 59.6771 | 59.6874 | 59.6454 | 61.6842 | 61.763 | 61.5779 | 61.7198 | -2.0655 | -1.9592 | -1.9968 | -1.8905
24.3906 | 121.8475 | -61.6608 | 59.8434 | 0.11269 | 0.023583 | -0.002842 | -0.029595 | 0.008797 | 0.099318 | -0.13597 | 59.5729 | 59.6313 | 59.6416 | 59.5951 | 61.6338 | 61.7172 | 61.5321 | 61.674 | 0.16305 | 0.073937 | 0.047512 | 0.020759 | 0.059151 | 0.14967 | -0.085614 | 59.6233 | 59.6817 | 59.692 | 59.6454 | 61.6842 | 61.7676 | 61.5825 | 61.7243 | -2.0609 | -1.9592 | -1.9922 | -1.8905
26.0625 | 121.8475 | -61.6882 | 59.8434 | 0.11727 | 0.023583 | -0.002842 | -0.029595 | 0.008797 | 0.099318 | -0.13597 | 59.5683 | 59.6267 | 59.637 | 59.5859 | 61.6384 | 61.7081 | 61.5275 | 61.6694 | 0.16763 | 0.073937 | 0.047512 | 0.020759 | 0.059151 | 0.14967 | -0.085614 | 59.6187 | 59.6771 | 59.6874 | 59.6362 | 61.6888 | 61.7584 | 61.5779 | 61.7198 | -2.0701 | -1.9592 | -2.0014 | -1.8905
27.8125 | 121.875 | -61.7569 | 59.7336 | 0.12185 | 0.023583 | -0.002842 | -0.025017 | 0.004219 | 0.099318 | -0.13139 | 59.5729 | 59.6222 | 59.637 | 59.5996 | 61.643 | 61.7127 | 61.5321 | 61.6694 | 0.1722 | 0.073937 | 0.047512 | 0.025337 | 0.054573 | 0.14967 | -0.081036 | 59.6233 | 59.6725 | 59.6874 | 59.65 | 61.6933 | 61.763 | 61.5825 | 61.7198 | -2.0701 | -1.9592 | -2.0059 | -1.8951
29.5625 | 121.8384 | -61.7432 | 59.7427 | 0.12643 | 0.014425 | 0.001736 | -0.025017 | 0.013375 | 0.1039 | -0.13597 | 59.5683 | 59.6267 | 59.637 | 59.5905 | 61.6384 | 61.7127 | 61.5275 | 61.674 | 0.17678 | 0.064779 | 0.05209 | 0.025337 | 0.063729 | 0.15425 | -0.085614 | 59.6187 | 59.6771 | 59.6874 | 59.6408 | 61.6888 | 61.763 | 61.5779 | 61.7243 | -2.0701 | -1.9592 | -2.0014 | -1.8905
31.25 | 121.8887 | -61.6653 | 59.8526 | 0.11727 | 0.019004 | -0.012 | -0.029595 | 0.008797 | 0.099318 | -0.12681 | 59.5729 | 59.6222 | 59.6325 | 59.5951 | 61.6338 | 61.7127 | 61.5321 | 61.6648 | 0.16763 | 0.069358 | 0.038354 | 0.020759 | 0.059151 | 0.14967 | -0.076458 | 59.6233 | 59.6725 | 59.6828 | 59.6454 | 61.6842 | 61.763 | 61.5825 | 61.7152 | -2.0609 | -1.9592 | -2.0014 | -1.8996
33 | 121.788 | -61.8256 | 59.7061 | 0.12185 | 0.023583 | -0.002842 | -0.025017 | 0.004219 | 0.099318 | -0.13139 | 59.5638 | 59.6267 | 59.6416 | 59.5996 | 61.643 | 61.7081 | 61.5321 | 61.6648 | 0.1722 | 0.073937 | 0.047512 | 0.025337 | 0.054573 | 0.14967 | -0.081036 | 59.6141 | 59.6771 | 59.692 | 59.65 | 61.6933 | 61.7584 | 61.5825 | 61.7152 | -2.0792 | -1.9683 | -2.0014 | -1.8905
34.6719 | 121.7697 | -61.6974 | 59.8755 | 0.11727 | 0.014425 | -0.007421 | -0.025017 | 0.004219 | 0.099318 | -0.13597 | 59.5638 | 59.6222 | 59.637 | 59.5951 | 61.6338 | 61.7081 | 61.5275 | 61.674 | 0.16763 | 0.064779 | 0.042933 | 0.025337 | 0.054573 | 0.14967 | -0.085614 | 59.6141 | 59.6725 | 59.6874 | 59.6454 | 61.6842 | 61.7584 | 61.5779 | 61.7243 | -2.0701 | -1.9638 | -1.9968 | -1.8905
36.4219 | 121.7377 | -61.7111 | 59.8755 | 0.12185 | 0.019004 | 0.001736 | -0.025017 | 0.008797 | 0.099318 | -0.13139 | 59.5683 | 59.6222 | 59.637 | 59.5951 | 61.6384 | 61.7081 | 61.5275 | 61.6786 | 0.1722 | 0.069358 | 0.05209 | 0.025337 | 0.059151 | 0.14967 | -0.081036 | 59.6187 | 59.6725 | 59.6874 | 59.6454 | 61.6888 | 61.7584 | 61.5779 | 61.7289 | -2.0701 | -1.9592 | -2.0014 | -1.8905
38.1719 | 121.8658 | -61.6745 | 59.8389 | 0.11727 | 0.019004 | -0.007421 | -0.029595 | 0.008797 | 0.099318 | -0.13597 | 59.5683 | 59.6222 | 59.637 | 59.5951 | 61.643 | 61.7081 | 61.5275 | 61.6694 | 0.16763 | 0.069358 | 0.042933 | 0.020759 | 0.059151 | 0.14967 | -0.085614 | 59.6187 | 59.6725 | 59.6874 | 59.6454 | 61.6933 | 61.7584 | 61.5779 | 61.7198 | -2.0746 | -1.9592 | -2.0059 | -1.8905
39.9062 | 121.7514 | -61.7477 | 59.8389 | 0.12185 | 0.023583 | -0.007421 | -0.020438 | 0.013375 | 0.099318 | -0.13139 | 59.5683 | 59.6267 | 59.637 | 59.5951 | 61.6384 | 61.7035 | 61.5229 | 61.6694 | 0.1722 | 0.073937 | 0.042933 | 0.029916 | 0.063729 | 0.14967 | -0.081036 | 59.6187 | 59.6771 | 59.6874 | 59.6454 | 61.6888 | 61.7539 | 61.5733 | 61.7198 | -2.0701 | -1.9546 | -2.0014 | -1.8859
41.5938 | 121.8292 | -61.7386 | 59.761 | 0.11269 | 0.019004 | -0.002842 | -0.025017 | 0.017953 | 0.1039 | -0.12681 | 59.5638 | 59.6222 | 59.6416 | 59.5951 | 61.6338 | 61.7127 | 61.5229 | 61.6786 | 0.16305 | 0.069358 | 0.047512 | 0.025337 | 0.068307 | 0.15425 | -0.076458 | 59.6141 | 59.6725 | 59.692 | 59.6454 | 61.6842 | 61.763 | 61.5733 | 61.7289 | -2.0701 | -1.9592 | -1.9922 | -1.8813
43.3438 | 121.7789 | -61.7844 | 59.7794 | 0.11727 | 0.014425 | -0.002842 | -0.029595 | 0.013375 | 0.1039 | -0.12223 | 59.5729 | 59.6176 | 59.6325 | 59.5996 | 61.6292 | 61.7081 | 61.5229 | 61.6648 | 0.16763 | 0.064779 | 0.047512 | 0.020759 | 0.063729 | 0.15425 | -0.07188 | 59.6233 | 59.6679 | 59.6828 | 59.65 | 61.6796 | 61.7584 | 61.5733 | 61.7152 | -2.0563 | -1.95 | -1.9968 | -1.8905
45.0781 | 121.7239 | -61.8256 | 59.7519 | 0.11727 | 0.014425 | -0.002842 | -0.025017 | 0.013375 | 0.09474 | -0.13597 | 59.5683 | 59.6222 | 59.6325 | 59.5996 | 61.6384 | 61.7081 | 61.5275 | 61.6694 | 0.16763 | 0.064779 | 0.047512 | 0.025337 | 0.063729 | 0.14509 | -0.085614 | 59.6187 | 59.6725 | 59.6828 | 59.65 | 61.6888 | 61.7584 | 61.5779 | 61.7198 | -2.0701 | -1.9592 | -2.0059 | -1.8951
46.75 | 121.8201 | -61.7477 | 59.7839 | 0.11727 | 0.000689 | -0.012 | -0.038752 | -0.000359 | 0.090161 | -0.13597 | 59.5683 | 59.6313 | 59.6325 | 59.6042 | 61.6338 | 61.7172 | 61.5321 | 61.6694 | 0.16763 | 0.051043 | 0.038354 | 0.011602 | 0.049995 | 0.14052 | -0.085614 | 59.6187 | 59.6817 | 59.6828 | 59.6546 | 61.6842 | 61.7676 | 61.5825 | 61.7198 | -2.0655 | -1.9637 | -2.0014 | -1.8996
48.5 | 121.7514 | -61.8164 | 59.7336 | 0.12185 | 0.009846 | -0.007421 | -0.029595 | 0.008797 | 0.1039 | -0.12223 | 59.5729 | 59.6267 | 59.6325 | 59.5996 | 61.6338 | 61.7081 | 61.5275 | 61.6786 | 0.1722 | 0.0602 | 0.042933 | 0.020759 | 0.059151 | 0.15425 | -0.07188 | 59.6233 | 59.6771 | 59.6828 | 59.65 | 61.6842 | 61.7584 | 61.5779 | 61.7289 | -2.0609 | -1.9546 | -2.0014 | -1.8951
50.2344 | 121.875 | -61.7752 | 59.7153 | 0.11727 | 0.009846 | -0.002842 | -0.029595 | 0.008797 | 0.099318 | -0.13139 | 59.5683 | 59.6222 | 59.637 | 59.5996 | 61.6384 | 61.7081 | 61.5184 | 61.6786 | 0.16763 | 0.0602 | 0.047512 | 0.020759 | 0.059151 | 0.14967 | -0.081036 | 59.6187 | 59.6725 | 59.6874 | 59.65 | 61.6888 | 61.7584 | 61.5687 | 61.7289 | -2.0701 | -1.95 | -2.0014 | -1.8813
51.9844 | 121.7606 | -61.6928 | 59.8526 | 0.11727 | 0.005267 | -0.002842 | -0.025017 | 0.008797 | 0.099318 | -0.13139 | 59.5638 | 59.6222 | 59.6325 | 59.5996 | 61.643 | 61.7127 | 61.5275 | 61.6694 | 0.16763 | 0.055621 | 0.047512 | 0.025337 | 0.059151 | 0.14967 | -0.081036 | 59.6141 | 59.6725 | 59.6828 | 59.65 | 61.6933 | 61.763 | 61.5779 | 61.7198 | -2.0792 | -1.9638 | -2.0105 | -1.8951
53.6875 | 121.7468 | -61.7065 | 59.8892 | 0.12643 | 0.009846 | -0.012 | -0.029595 | 0.004219 | 0.099318 | -0.12223 | 59.5592 | 59.6222 | 59.637 | 59.5996 | 61.6338 | 61.7172 | 61.5275 | 61.674 | 0.17678 | 0.0602 | 0.038354 | 0.020759 | 0.054573 | 0.14967 | -0.07188 | 59.6095 | 59.6725 | 59.6874 | 59.65 | 61.6842 | 61.7676 | 61.5779 | 61.7243 | -2.0746 | -1.9683 | -1.9968 | -1.8905
55.4531 | 121.8613 | -61.7706 | 59.6924 | 0.11727 | 0.014425 | -0.007421 | -0.029595 | 0.008797 | 0.099318 | -0.12223 | 59.5683 | 59.6222 | 59.6325 | 59.5905 | 61.6338 | 61.7035 | 61.5275 | 61.674 | 0.16763 | 0.064779 | 0.042933 | 0.020759 | 0.059151 | 0.14967 | -0.07188 | 59.6187 | 59.6725 | 59.6828 | 59.6408 | 61.6842 | 61.7539 | 61.5779 | 61.7243 | -2.0655 | -1.9592 | -2.0014 | -1.8951
57.1406 | 121.7834 | -61.7477 | 59.8022 | 0.12643 | 0.009846 | -0.007421 | -0.025017 | 0.013375 | 0.099318 | -0.13139 | 59.5729 | 59.6176 | 59.6325 | 59.5996 | 61.6338 | 61.7127 | 61.5184 | 61.6694 | 0.17678 | 0.0602 | 0.042933 | 0.025337 | 0.063729 | 0.14967 | -0.081036 | 59.6233 | 59.6679 | 59.6828 | 59.65 | 61.6842 | 61.763 | 61.5687 | 61.7198 | -2.0609 | -1.9454 | -2.0014 | -1.8859
58.8906 | 121.7972 | -61.6928 | 59.8709 | 0.12185 | 0.000689 | -0.012 | -0.029595 | 0.004219 | 0.099318 | -0.12681 | 59.5683 | 59.6267 | 59.6325 | 59.5951 | 61.6338 | 61.7081 | 61.5275 | 61.6694 | 0.1722 | 0.051043 | 0.038354 | 0.020759 | 0.054573 | 0.14967 | -0.076458 | 59.6187 | 59.6771 | 59.6828 | 59.6454 | 61.6842 | 61.7584 | 61.5779 | 61.7198 | -2.0655 | -1.9592 | -2.0014 | -1.8951
60.625 | 121.843 | -61.6791 | 59.8343 | 0.12185 | 0.000689 | -0.007421 | -0.029595 | 0.008797 | 0.099318 | -0.13139 | 59.5638 | 59.6267 | 59.6325 | 59.5905 | 61.6338 | 61.7081 | 61.5229 | 61.6694 | 0.1722 | 0.051043 | 0.042933 | 0.020759 | 0.059151 | 0.14967 | -0.081036 | 59.6141 | 59.6771 | 59.6828 | 59.6408 | 61.6842 | 61.7584 | 61.5733 | 61.7198 | -2.0701 | -1.9592 | -2.0014 | -1.8905
62.3594 | 121.7377 | -61.702 | 59.8801 | 0.12185 | 0.014425 | -0.007421 | -0.029595 | 0.008797 | 0.099318 | -0.13597 | 59.5683 | 59.6176 | 59.637 | 59.5905 | 61.6338 | 61.7035 | 61.5184 | 61.6786 | 0.1722 | 0.064779 | 0.042933 | 0.020759 | 0.059151 | 0.14967 | -0.085614 | 59.6187 | 59.6679 | 59.6874 | 59.6408 | 61.6842 | 61.7539 | 61.5687 | 61.7289 | -2.0655 | -1.95 | -1.9968 | -1.8813
64.1094 | 121.843 | -61.7798 | 59.6924 | 0.11727 | 0.009846 | -0.002842 | -0.029595 | 0.013375 | 0.1039 | -0.13139 | 59.5683 | 59.6176 | 59.637 | 59.5859 | 61.6384 | 61.7081 | 61.5229 | 61.6602 | 0.16763 | 0.0602 | 0.047512 | 0.020759 | 0.063729 | 0.15425 | -0.081036 | 59.6187 | 59.6679 | 59.6874 | 59.6362 | 61.6888 | 61.7584 | 61.5733 | 61.7106 | -2.0701 | -1.9546 | -2.0014 | -1.8859
65.7969 | 121.8063 | -61.7203 | 59.8068 | 0.11727 | 0.009846 | -0.012 | -0.029595 | 0.004219 | 0.099318 | -0.13597 | 59.5683 | 59.6176 | 59.6325 | 59.5905 | 61.6384 | 61.7081 | 61.5184 | 61.6648 | 0.16763 | 0.0602 | 0.038354 | 0.020759 | 0.054573 | 0.14967 | -0.085614 | 59.6187 | 59.6679 | 59.6828 | 59.6408 | 61.6888 | 61.7584 | 61.5687 | 61.7152 | -2.0701 | -1.95 | -2.0059 | -1.8859
67.5469 | 121.7102 | -61.821 | 59.7427 | 0.12185 | 0.009846 | -0.002842 | -0.029595 | 0.008797 | 0.090161 | -0.13139 | 59.5683 | 59.6176 | 59.6325 | 59.5996 | 61.6292 | 61.7081 | 61.5275 | 61.6694 | 0.1722 | 0.0602 | 0.047512 | 0.020759 | 0.059151 | 0.14052 | -0.081036 | 59.6187 | 59.6679 | 59.6828 | 59.65 | 61.6796 | 61.7584 | 61.5779 | 61.7198 | -2.0609 | -1.9592 | -1.9968 | -1.8951
69.2969 | 121.8109 | -61.6974 | 59.7931 | 0.11727 | 0.005267 | -0.007421 | -0.029595 | 0.013375 | 0.090161 | -0.13597 | 59.5638 | 59.6176 | 59.6279 | 59.5996 | 61.6384 | 61.6989 | 61.5184 | 61.6694 | 0.16763 | 0.055621 | 0.042933 | 0.020759 | 0.063729 | 0.14052 | -0.085614 | 59.6141 | 59.6679 | 59.6782 | 59.65 | 61.6888 | 61.7493 | 61.5687 | 61.7198 | -2.0746 | -1.9546 | -2.0105 | -1.8905
71.0469 | 121.8475 | -61.6653 | 59.8389 | 0.11727 | 0.005267 | -0.007421 | -0.034174 | 0.008797 | 0.090161 | -0.13597 | 59.5592 | 59.6222 | 59.6279 | 59.5951 | 61.6384 | 61.7127 | 61.5184 | 61.6602 | 0.16763 | 0.055621 | 0.042933 | 0.01618 | 0.059151 | 0.14052 | -0.085614 | 59.6095 | 59.6725 | 59.6782 | 59.6454 | 61.6888 | 61.763 | 61.5687 | 61.7106 | -2.0792 | -1.9592 | -2.0105 | -1.8905
72.7188 | 121.7239 | -61.7203 | 59.8572 | 0.12643 | 0.005267 | -0.007421 | -0.029595 | 0.013375 | 0.099318 | -0.13139 | 59.5592 | 59.613 | 59.6325 | 59.5951 | 61.6338 | 61.7081 | 61.5184 | 61.6648 | 0.17678 | 0.055621 | 0.042933 | 0.020759 | 0.063729 | 0.14967 | -0.081036 | 59.6095 | 59.6634 | 59.6828 | 59.6454 | 61.6842 | 61.7584 | 61.5687 | 61.7152 | -2.0746 | -1.9592 | -2.0014 | -1.8859
74.4688 | 121.7056 | -61.8347 | 59.761 | 0.12185 | 0.014425 | 0.001736 | -0.029595 | 0.013375 | 0.099318 | -0.12223 | 59.5638 | 59.6176 | 59.6279 | 59.5905 | 61.6384 | 61.7127 | 61.5229 | 61.6694 | 0.1722 | 0.064779 | 0.05209 | 0.020759 | 0.063729 | 0.14967 | -0.07188 | 59.6141 | 59.6679 | 59.6782 | 59.6408 | 61.6888 | 61.763 | 61.5733 | 61.7198 | -2.0746 | -1.9592 | -2.0105 | -1.8951
76.2031 | 121.8246 | -61.734 | 59.7565 | 0.12185 | 0.009846 | -0.007421 | -0.034174 | 0.008797 | 0.090161 | -0.13139 | 59.5638 | 59.613 | 59.6279 | 59.5951 | 61.6476 | 61.7127 | 61.5275 | 61.6648 | 0.1722 | 0.0602 | 0.042933 | 0.01618 | 0.059151 | 0.14052 | -0.081036 | 59.6141 | 59.6634 | 59.6782 | 59.6454 | 61.6979 | 61.763 | 61.5779 | 61.7152 | -2.0838 | -1.9638 | -2.0197 | -1.8996
77.9688 | 121.8796 | -61.6562 | 59.8206 | 0.11727 | 0.009846 | -0.012 | -0.038752 | 0.008797 | 0.09474 | -0.13139 | 59.5638 | 59.6176 | 59.6325 | 59.5905 | 61.6292 | 61.7081 | 61.5275 | 61.6648 | 0.16763 | 0.0602 | 0.038354 | 0.011602 | 0.059151 | 0.14509 | -0.081036 | 59.6141 | 59.6679 | 59.6828 | 59.6408 | 61.6796 | 61.7584 | 61.5779 | 61.7152 | -2.0655 | -1.9638 | -1.9968 | -1.8951
79.6562 | 121.8155 | -61.7111 | 59.8206 | 0.11727 | 0.009846 | -0.007421 | -0.020438 | 0.008797 | 0.090161 | -0.13597 | 59.5638 | 59.6176 | 59.6279 | 59.5905 | 61.6338 | 61.7081 | 61.5229 | 61.6648 | 0.16763 | 0.0602 | 0.042933 | 0.029916 | 0.059151 | 0.14052 | -0.085614 | 59.6141 | 59.6679 | 59.6782 | 59.6408 | 61.6842 | 61.7584 | 61.5733 | 61.7152 | -2.0701 | -1.9592 | -2.0059 | -1.8951
81.3906 | 121.8201 | -61.7065 | 59.8206 | 0.11727 | 0.014425 | -0.007421 | -0.034174 | 0.008797 | 0.090161 | -0.13139 | 59.5683 | 59.6038 | 59.637 | 59.5859 | 61.6292 | 61.7127 | 61.5229 | 61.6648 | 0.16763 | 0.064779 | 0.042933 | 0.01618 | 0.059151 | 0.14052 | -0.081036 | 59.6187 | 59.6542 | 59.6874 | 59.6362 | 61.6796 | 61.763 | 61.5733 | 61.7152 | -2.0609 | -1.9546 | -1.9922 | -1.8859
83.1406 | 121.7285 | -61.8347 | 59.7382 | 0.11727 | 0.014425 | -0.012 | -0.025017 | 0.013375 | 0.10848 | -0.13139 | 59.5638 | 59.6176 | 59.6325 | 59.5951 | 61.6292 | 61.7035 | 61.5184 | 61.674 | 0.16763 | 0.064779 | 0.038354 | 0.025337 | 0.063729 | 0.15883 | -0.081036 | 59.6141 | 59.6679 | 59.6828 | 59.6454 | 61.6796 | 61.7539 | 61.5687 | 61.7243 | -2.0655 | -1.9546 | -1.9968 | -1.8859
84.8906 | 121.7331 | -61.7203 | 59.848 | 0.11269 | 0.014425 | -0.007421 | -0.029595 | 0.013375 | 0.099318 | -0.12223 | 59.5683 | 59.6176 | 59.6325 | 59.5905 | 61.6292 | 61.7081 | 61.5184 | 61.6694 | 0.16305 | 0.064779 | 0.042933 | 0.020759 | 0.063729 | 0.14967 | -0.07188 | 59.6187 | 59.6679 | 59.6828 | 59.6408 | 61.6796 | 61.7584 | 61.5687 | 61.7198 | -2.0609 | -1.95 | -1.9968 | -1.8859
86.5781 | 121.8063 | -61.7432 | 59.761 | 0.11727 | 0.009846 | -0.007421 | -0.038752 | 0.013375 | 0.099318 | -0.14055 | 59.5683 | 59.6222 | 59.6279 | 59.5951 | 61.6338 | 61.7035 | 61.5184 | 61.674 | 0.16763 | 0.0602 | 0.042933 | 0.011602 | 0.063729 | 0.14967 | -0.090192 | 59.6187 | 59.6725 | 59.6782 | 59.6454 | 61.6842 | 61.7539 | 61.5687 | 61.7243 | -2.0655 | -1.95 | -2.0059 | -1.8905
88.3281 | 121.7331 | -61.7432 | 59.8434 | 0.12185 | 0.019004 | -0.012 | -0.038752 | 0.008797 | 0.099318 | -0.13139 | 59.5683 | 59.613 | 59.6233 | 59.5905 | 61.6338 | 61.7035 | 61.5184 | 61.674 | 0.1722 | 0.069358 | 0.038354 | 0.011602 | 0.059151 | 0.14967 | -0.081036 | 59.6187 | 59.6634 | 59.6737 | 59.6408 | 61.6842 | 61.7539 | 61.5687 | 61.7243 | -2.0655 | -1.95 | -2.0105 | -1.8951
90.0781 | 121.8704 | -61.7569 | 59.7061 | 0.12185 | 0.009846 | -0.012 | -0.034174 | 0.017953 | 0.1039 | -0.12681 | 59.5683 | 59.6267 | 59.6279 | 59.5951 | 61.6384 | 61.7035 | 61.5138 | 61.6648 | 0.1722 | 0.0602 | 0.038354 | 0.01618 | 0.068307 | 0.15425 | -0.076458 | 59.6187 | 59.6771 | 59.6782 | 59.6454 | 61.6888 | 61.7539 | 61.5641 | 61.7152 | -2.0701 | -1.9454 | -2.0105 | -1.8859
91.75 | 121.843 | -61.6333 | 59.8343 | 0.11269 | 0.009846 | -0.016578 | -0.029595 | 0.004219 | 0.09474 | -0.13597 | 59.5638 | 59.6222 | 59.6325 | 59.5905 | 61.6292 | 61.7035 | 61.5321 | 61.6648 | 0.16305 | 0.0602 | 0.033776 | 0.020759 | 0.054573 | 0.14509 | -0.085614 | 59.6141 | 59.6725 | 59.6828 | 59.6408 | 61.6796 | 61.7539 | 61.5825 | 61.7152 | -2.0655 | -1.9683 | -1.9968 | -1.8996
93.5 | 121.6965 | -61.8439 | 59.7336 | 0.11727 | 0.023583 | -0.002842 | -0.025017 | 0.017953 | 0.099318 | -0.12681 | 59.5638 | 59.6176 | 59.6233 | 59.5951 | 61.6292 | 61.6989 | 61.5138 | 61.6602 | 0.16763 | 0.073937 | 0.047512 | 0.025337 | 0.068307 | 0.14967 | -0.076458 | 59.6141 | 59.6679 | 59.6737 | 59.6454 | 61.6796 | 61.7493 | 61.5641 | 61.7106 | -2.0655 | -1.95 | -2.0059 | -1.8905
95.25 | 121.8613 | -61.6562 | 59.8434 | 0.12185 | 0.009846 | -0.007421 | -0.034174 | 0.008797 | 0.099318 | -0.13597 | 59.5638 | 59.6176 | 59.6279 | 59.5951 | 61.6292 | 61.7081 | 61.5184 | 61.6648 | 0.1722 | 0.0602 | 0.042933 | 0.01618 | 0.059151 | 0.14967 | -0.085614 | 59.6141 | 59.6679 | 59.6782 | 59.6454 | 61.6796 | 61.7584 | 61.5687 | 61.7152 | -2.0655 | -1.9546 | -2.0014 | -1.8905
97 | 121.7743 | -61.7569 | 59.8022 | 0.12185 | 0.014425 | -0.002842 | -0.029595 | 0.008797 | 0.10848 | -0.13139 | 59.5592 | 59.6176 | 59.6279 | 59.5905 | 61.6292 | 61.7035 | 61.5138 | 61.6648 | 0.1722 | 0.064779 | 0.047512 | 0.020759 | 0.059151 | 0.15883 | -0.081036 | 59.6095 | 59.6679 | 59.6782 | 59.6408 | 61.6796 | 61.7539 | 61.5641 | 61.7152 | -2.0701 | -1.9546 | -2.0014 | -1.8859
98.75 | 121.8567 | -61.7844 | 59.7015 | 0.11727 | 0.014425 | -0.007421 | -0.038752 | 0.008797 | 0.09474 | -0.12681 | 59.5638 | 59.6222 | 59.6279 | 59.5905 | 61.6292 | 61.7035 | 61.5138 | 61.6648 | 0.16763 | 0.064779 | 0.042933 | 0.011602 | 0.059151 | 0.14509 | -0.076458 | 59.6141 | 59.6725 | 59.6782 | 59.6408 | 61.6796 | 61.7539 | 61.5641 | 61.7152 | -2.0655 | -1.95 | -2.0014 | -1.8859
100.4531 | 121.875 | -61.6379 | 59.8343 | 0.11727 | 0.005267 | -0.012 | -0.038752 | 0.008797 | 0.09474 | -0.13139 | 59.5638 | 59.613 | 59.637 | 59.5905 | 61.6292 | 61.7035 | 61.5138 | 61.6648 | 0.16763 | 0.055621 | 0.038354 | 0.011602 | 0.059151 | 0.14509 | -0.081036 | 59.6141 | 59.6634 | 59.6874 | 59.6408 | 61.6796 | 61.7539 | 61.5641 | 61.7152 | -2.0655 | -1.95 | -1.9922 | -1.8767
102.1875 | 121.7606 | -61.7569 | 59.7794 | 0.12185 | 0.014425 | -0.007421 | -0.025017 | 0.008797 | 0.099318 | -0.13139 | 59.5638 | 59.6222 | 59.6325 | 59.5905 | 61.6292 | 61.6989 | 61.5184 | 61.6602 | 0.1722 | 0.064779 | 0.042933 | 0.025337 | 0.059151 | 0.14967 | -0.081036 | 59.6141 | 59.6725 | 59.6828 | 59.6408 | 61.6796 | 61.7493 | 61.5687 | 61.7106 | -2.0655 | -1.9546 | -1.9968 | -1.8859
103.9375 | 121.7606 | -61.7889 | 59.7656 | 0.11727 | 0.014425 | -0.002842 | -0.029595 | 0.017953 | 0.099318 | -0.12681 | 59.5638 | 59.6176 | 59.6279 | 59.5951 | 61.6292 | 61.6989 | 61.5184 | 61.6694 | 0.16763 | 0.064779 | 0.047512 | 0.020759 | 0.068307 | 0.14967 | -0.076458 | 59.6141 | 59.6679 | 59.6782 | 59.6454 | 61.6796 | 61.7493 | 61.5687 | 61.7198 | -2.0655 | -1.9546 | -2.0014 | -1.8905
105.6875 | 121.7834 | -61.7844 | 59.7336 | 0.12643 | 0.023583 | -0.012 | -0.025017 | 0.017953 | 0.09474 | -0.12223 | 59.5638 | 59.6222 | 59.6325 | 59.5859 | 61.6338 | 61.7035 | 61.5138 | 61.674 | 0.17678 | 0.073937 | 0.038354 | 0.025337 | 0.068307 | 0.14509 | -0.07188 | 59.6141 | 59.6725 | 59.6828 | 59.6362 | 61.6842 | 61.7539 | 61.5641 | 61.7243 | -2.0701 | -1.95 | -2.0014 | -1.8813
107.375 | 121.8292 | -61.6608 | 59.8343 | 0.12185 | 0.009846 | -0.012 | -0.029595 | 0.008797 | 0.099318 | -0.13597 | 59.5638 | 59.6176 | 59.6325 | 59.5905 | 61.6292 | 61.6989 | 61.5184 | 61.6648 | 0.1722 | 0.0602 | 0.038354 | 0.020759 | 0.059151 | 0.14967 | -0.085614 | 59.6141 | 59.6679 | 59.6828 | 59.6408 | 61.6796 | 61.7493 | 61.5687 | 61.7152 | -2.0655 | -1.9546 | -1.9968 | -1.8859
109.125 | 121.7743 | -61.7477 | 59.7931 | 0.12185 | 0.009846 | -0.002842 | -0.029595 | 0.013375 | 0.09474 | -0.12681 | 59.5592 | 59.6176 | 59.6325 | 59.5996 | 61.6292 | 61.6943 | 61.5184 | 61.6602 | 0.1722 | 0.0602 | 0.047512 | 0.020759 | 0.063729 | 0.14509 | -0.076458 | 59.6095 | 59.6679 | 59.6828 | 59.65 | 61.6796 | 61.7447 | 61.5687 | 61.7106 | -2.0701 | -1.9592 | -1.9968 | -1.8859
110.7969 | 121.8475 | -61.6241 | 59.8434 | 0.11727 | 0.009846 | -0.007421 | -0.038752 | 0.008797 | 0.09474 | -0.12681 | 59.5638 | 59.6222 | 59.6233 | 59.5905 | 61.6292 | 61.7035 | 61.5184 | 61.6602 | 0.16763 | 0.0602 | 0.042933 | 0.011602 | 0.059151 | 0.14509 | -0.076458 | 59.6141 | 59.6725 | 59.6737 | 59.6408 | 61.6796 | 61.7539 | 61.5687 | 61.7106 | -2.0655 | -1.9546 | -2.0059 | -1.8951
112.5469 | 121.7377 | -61.7432 | 59.8663 | 0.11727 | 0.019004 | -0.007421 | -0.029595 | 0.008797 | 0.099318 | -0.13139 | 59.5592 | 59.613 | 59.6279 | 59.5813 | 61.6338 | 61.6989 | 61.5138 | 61.6602 | 0.16763 | 0.069358 | 0.042933 | 0.020759 | 0.059151 | 0.14967 | -0.081036 | 59.6095 | 59.6634 | 59.6782 | 59.6317 | 61.6842 | 61.7493 | 61.5641 | 61.7106 | -2.0746 | -1.9546 | -2.0059 | -1.8859
114.2969 | 121.843 | -61.7432 | 59.7336 | 0.11727 | 0.009846 | -0.012 | -0.025017 | 0.013375 | 0.090161 | -0.12223 | 59.5638 | 59.6176 | 59.6279 | 59.5905 | 61.6247 | 61.6989 | 61.5138 | 61.6694 | 0.16763 | 0.0602 | 0.038354 | 0.025337 | 0.063729 | 0.14052 | -0.07188 | 59.6141 | 59.6679 | 59.6782 | 59.6408 | 61.675 | 61.7493 | 61.5641 | 61.7198 | -2.0609 | -1.95 | -1.9968 | -1.8859
116.0312 | 121.8384 | -61.7844 | 59.6878 | 0.11269 | 0.014425 | -0.012 | -0.034174 | 0.008797 | 0.099318 | -0.12681 | 59.5683 | 59.6267 | 59.637 | 59.5951 | 61.6292 | 61.6943 | 61.5184 | 61.6648 | 0.16305 | 0.064779 | 0.038354 | 0.01618 | 0.059151 | 0.14967 | -0.076458 | 59.6187 | 59.6771 | 59.6874 | 59.6454 | 61.6796 | 61.7447 | 61.5687 | 61.7152 | -2.0609 | -1.95 | -1.9922 | -1.8813
117.7188 | 121.7056 | -61.8301 | 59.7565 | 0.12185 | 0.014425 | -0.002842 | -0.025017 | 0.008797 | 0.09474 | -0.12223 | 59.5638 | 59.6176 | 59.6279 | 59.5905 | 61.6247 | 61.6943 | 61.5138 | 61.6602 | 0.1722 | 0.064779 | 0.047512 | 0.025337 | 0.059151 | 0.14509 | -0.07188 | 59.6141 | 59.6679 | 59.6782 | 59.6408 | 61.675 | 61.7447 | 61.5641 | 61.7106 | -2.0609 | -1.95 | -1.9968 | -1.8859
119.4688 | 121.7422 | -61.7065 | 59.8526 | 0.12643 | 0.014425 | -0.016578 | -0.034174 | 0.013375 | 0.099318 | -0.12681 | 59.5638 | 59.6222 | 59.6233 | 59.5859 | 61.6292 | 61.6989 | 61.5184 | 61.674 | 0.17678 | 0.064779 | 0.033776 | 0.01618 | 0.063729 | 0.14967 | -0.076458 | 59.6141 | 59.6725 | 59.6737 | 59.6362 | 61.6796 | 61.7493 | 61.5687 | 61.7243 | -2.0655 | -1.9546 | -2.0059 | -1.8951
121.2188 | 121.7651 | -61.7981 | 59.761 | 0.11269 | 0.014425 | -0.002842 | -0.029595 | 0.004219 | 0.09474 | -0.13139 | 59.5683 | 59.6176 | 59.6233 | 59.5905 | 61.6292 | 61.6989 | 61.5184 | 61.6557 | 0.16305 | 0.064779 | 0.047512 | 0.020759 | 0.054573 | 0.14509 | -0.081036 | 59.6187 | 59.6679 | 59.6737 | 59.6408 | 61.6796 | 61.7493 | 61.5687 | 61.706 | -2.0609 | -1.95 | -2.0059 | -1.8951
122.9844 | 121.8521 | -61.6562 | 59.8022 | 0.11727 | 0.014425 | -0.012 | -0.029595 | 0.013375 | 0.09474 | -0.13139 | 59.5638 | 59.613 | 59.6325 | 59.5905 | 61.6247 | 61.6989 | 61.5229 | 61.6648 | 0.16763 | 0.064779 | 0.038354 | 0.020759 | 0.063729 | 0.14509 | -0.081036 | 59.6141 | 59.6634 | 59.6828 | 59.6408 | 61.675 | 61.7493 | 61.5733 | 61.7152 | -2.0609 | -1.9592 | -1.9922 | -1.8905
124.7344 | 121.8475 | -61.7661 | 59.7198 | 0.11269 | 0.009846 | -0.012 | -0.029595 | 0.013375 | 0.09474 | -0.13597 | 59.5592 | 59.6176 | 59.6279 | 59.5905 | 61.6292 | 61.7035 | 61.5138 | 61.6648 | 0.16305 | 0.0602 | 0.038354 | 0.020759 | 0.063729 | 0.14509 | -0.085614 | 59.6095 | 59.6679 | 59.6782 | 59.6408 | 61.6796 | 61.7539 | 61.5641 | 61.7152 | -2.0701 | -1.9546 | -2.0014 | -1.8859
126.4062 | 121.7102 | -61.7157 | 59.8434 | 0.11727 | 0.009846 | -0.007421 | -0.038752 | 0.008797 | 0.099318 | -0.12681 | 59.5638 | 59.6222 | 59.6325 | 59.5859 | 61.6247 | 61.6989 | 61.5184 | 61.6557 | 0.16763 | 0.0602 | 0.042933 | 0.011602 | 0.059151 | 0.14967 | -0.076458 | 59.6141 | 59.6725 | 59.6828 | 59.6362 | 61.675 | 61.7493 | 61.5687 | 61.706 | -2.0609 | -1.9546 | -1.9922 | -1.8859
128.1562 | 121.8155 | -61.7157 | 59.7839 | 0.10812 | 0.019004 | -0.012 | -0.034174 | 0.008797 | 0.09474 | -0.13597 | 59.5638 | 59.613 | 59.6325 | 59.5905 | 61.6384 | 61.6989 | 61.5138 | 61.6602 | 0.15847 | 0.069358 | 0.038354 | 0.01618 | 0.059151 | 0.14509 | -0.085614 | 59.6141 | 59.6634 | 59.6828 | 59.6408 | 61.6888 | 61.7493 | 61.5641 | 61.7106 | -2.0746 | -1.95 | -2.0059 | -1.8813
129.9219 | 121.8521 | -61.7661 | 59.6924 | 0.12185 | 0.005267 | -0.007421 | -0.029595 | 0.004219 | 0.090161 | -0.12681 | 59.5683 | 59.6222 | 59.6233 | 59.5905 | 61.6384 | 61.6989 | 61.5184 | 61.6648 | 0.1722 | 0.055621 | 0.042933 | 0.020759 | 0.054573 | 0.14052 | -0.076458 | 59.6187 | 59.6725 | 59.6737 | 59.6408 | 61.6888 | 61.7493 | 61.5687 | 61.7152 | -2.0701 | -1.95 | -2.0151 | -1.8951
131.6094 | 121.7056 | -61.8393 | 59.7427 | 0.12185 | 0.014425 | -0.007421 | -0.029595 | 0.004219 | 0.099318 | -0.12223 | 59.5638 | 59.6222 | 59.6279 | 59.5905 | 61.6338 | 61.6943 | 61.5138 | 61.6602 | 0.1722 | 0.064779 | 0.042933 | 0.020759 | 0.054573 | 0.14967 | -0.07188 | 59.6141 | 59.6725 | 59.6782 | 59.6408 | 61.6842 | 61.7447 | 61.5641 | 61.7106 | -2.0701 | -1.95 | -2.0059 | -1.8859
133.3594 | 121.7972 | -61.7203 | 59.7931 | 0.11727 | 0.005267 | -0.012 | -0.038752 | 0.008797 | 0.09474 | -0.13597 | 59.5638 | 59.6176 | 59.6279 | 59.5859 | 61.6247 | 61.6989 | 61.5138 | 61.6694 | 0.16763 | 0.055621 | 0.038354 | 0.011602 | 0.059151 | 0.14509 | -0.085614 | 59.6141 | 59.6679 | 59.6782 | 59.6362 | 61.675 | 61.7493 | 61.5641 | 61.7198 | -2.0609 | -1.95 | -1.9968 | -1.8859
135.1094 | 121.7056 | -61.7844 | 59.7519 | 0.12185 | 0.005267 | -0.007421 | -0.025017 | 0.017953 | 0.099318 | -0.12681 | 59.5638 | 59.6176 | 59.6325 | 59.5813 | 61.6247 | 61.7035 | 61.5138 | 61.6557 | 0.1722 | 0.055621 | 0.042933 | 0.025337 | 0.068307 | 0.14967 | -0.076458 | 59.6141 | 59.6679 | 59.6828 | 59.6317 | 61.675 | 61.7539 | 61.5641 | 61.706 | -2.0609 | -1.95 | -1.9922 | -1.8813
136.7812 | 121.8063 | -61.7065 | 59.7977 | 0.11727 | 0.009846 | -0.012 | -0.038752 | 0.004219 | 0.09474 | -0.13597 | 59.5683 | 59.6176 | 59.6279 | 59.5905 | 61.6247 | 61.7035 | 61.5138 | 61.6648 | 0.16763 | 0.0602 | 0.038354 | 0.011602 | 0.054573 | 0.14509 | -0.085614 | 59.6187 | 59.6679 | 59.6782 | 59.6408 | 61.675 | 61.7539 | 61.5641 | 61.7152 | -2.0563 | -1.9454 | -1.9968 | -1.8859
138.5312 | 121.8384 | -61.6653 | 59.848 | 0.10812 | 0.005267 | -0.007421 | -0.034174 | 0.008797 | 0.099318 | -0.13597 | 59.5638 | 59.6176 | 59.6325 | 59.5905 | 61.6292 | 61.6989 | 61.5092 | 61.6694 | 0.15847 | 0.055621 | 0.042933 | 0.01618 | 0.059151 | 0.14967 | -0.085614 | 59.6141 | 59.6679 | 59.6828 | 59.6408 | 61.6796 | 61.7493 | 61.5596 | 61.7198 | -2.0655 | -1.9454 | -1.9968 | -1.8767
140.2812 | 121.8384 | -61.7706 | 59.7198 | 0.12185 | 0.009846 | -0.002842 | -0.034174 | 0.017953 | 0.090161 | -0.13139 | 59.5638 | 59.6176 | 59.6325 | 59.5905 | 61.6292 | 61.7035 | 61.5092 | 61.6602 | 0.1722 | 0.0602 | 0.047512 | 0.01618 | 0.068307 | 0.14052 | -0.081036 | 59.6141 | 59.6679 | 59.6828 | 59.6408 | 61.6796 | 61.7539 | 61.5596 | 61.7106 | -2.0655 | -1.9454 | -1.9968 | -1.8767
142.0156 | 121.7468 | -61.7889 | 59.7473 | 0.11727 | 0.014425 | -0.002842 | -0.029595 | 0.008797 | 0.099318 | -0.12223 | 59.5592 | 59.6176 | 59.6279 | 59.5905 | 61.6292 | 61.6898 | 61.5 | 61.6602 | 0.16763 | 0.064779 | 0.047512 | 0.020759 | 0.059151 | 0.14967 | -0.07188 | 59.6095 | 59.6679 | 59.6782 | 59.6408 | 61.6796 | 61.7401 | 61.5504 | 61.7106 | -2.0701 | -1.9409 | -2.0014 | -1.8722
143.75 | 121.8338 | -61.7523 | 59.7382 | 0.11727 | 0.000689 | -0.012 | -0.043331 | 0.013375 | 0.085583 | -0.12681 | 59.5638 | 59.613 | 59.6233 | 59.5859 | 61.6247 | 61.6943 | 61.5 | 61.6557 | 0.16763 | 0.051043 | 0.038354 | 0.007023 | 0.063729 | 0.13594 | -0.076458 | 59.6141 | 59.6634 | 59.6737 | 59.6362 | 61.675 | 61.7447 | 61.5504 | 61.706 | -2.0609 | -1.9363 | -2.0014 | -1.8767
145.5156 | 121.7148 | -61.7294 | 59.8206 | 0.12185 | 0.009846 | -0.002842 | -0.025017 | 0.008797 | 0.099318 | -0.13597 | 59.5638 | 59.6222 | 59.6279 | 59.5905 | 61.6247 | 61.6943 | 61.5138 | 61.6557 | 0.1722 | 0.0602 | 0.047512 | 0.025337 | 0.059151 | 0.14967 | -0.085614 | 59.6141 | 59.6725 | 59.6782 | 59.6408 | 61.675 | 61.7447 | 61.5641 | 61.706 | -2.0609 | -1.95 | -1.9968 | -1.8859
147.2031 | 121.8155 | -61.7569 | 59.7198 | 0.11727 | 0.000689 | -0.007421 | -0.029595 | 0.017953 | 0.099318 | -0.13597 | 59.5638 | 59.613 | 59.6279 | 59.5905 | 61.6201 | 61.6943 | 61.5138 | 61.6557 | 0.16763 | 0.051043 | 0.042933 | 0.020759 | 0.068307 | 0.14967 | -0.085614 | 59.6141 | 59.6634 | 59.6782 | 59.6408 | 61.6704 | 61.7447 | 61.5641 | 61.706 | -2.0563 | -1.95 | -1.9922 | -1.8859
148.9375 | 121.7285 | -61.7111 | 59.8663 | 0.11727 | 0.005267 | -0.016578 | -0.034174 | 0.013375 | 0.1039 | -0.12681 | 59.5683 | 59.6176 | 59.6233 | 59.5813 | 61.6292 | 61.6989 | 61.5092 | 61.6557 | 0.16763 | 0.055621 | 0.033776 | 0.01618 | 0.063729 | 0.15425 | -0.076458 | 59.6187 | 59.6679 | 59.6737 | 59.6317 | 61.6796 | 61.7493 | 61.5596 | 61.706 | -2.0609 | -1.9409 | -2.0059 | -1.8859
150.625 | 121.8613 | -61.7935 | 59.6924 | 0.11727 | 0.014425 | -0.007421 | -0.038752 | 0.017953 | 0.099318 | -0.13139 | 59.5638 | 59.6222 | 59.6279 | 59.5905 | 61.6292 | 61.6989 | 61.5092 | 61.6648 | 0.16763 | 0.064779 | 0.042933 | 0.011602 | 0.068307 | 0.14967 | -0.081036 | 59.6141 | 59.6725 | 59.6782 | 59.6408 | 61.6796 | 61.7493 | 61.5596 | 61.7152 | -2.0655 | -1.9454 | -2.0014 | -1.8813
152.375 | 121.7514 | -61.8256 | 59.7107 | 0.11727 | 0.005267 | -0.007421 | -0.025017 | 0.008797 | 0.09474 | -0.13139 | 59.5638 | 59.6176 | 59.6279 | 59.5905 | 61.6292 | 61.7081 | 61.5138 | 61.6557 | 0.16763 | 0.055621 | 0.042933 | 0.025337 | 0.059151 | 0.14509 | -0.081036 | 59.6141 | 59.6679 | 59.6782 | 59.6408 | 61.6796 | 61.7584 | 61.5641 | 61.706 | -2.0655 | -1.95 | -2.0014 | -1.8859
154.125 | 121.701 | -61.853 | 59.7107 | 0.11727 | 0.009846 | -0.007421 | -0.029595 | 0.017953 | 0.099318 | -0.12681 | 59.5638 | 59.6222 | 59.6279 | 59.5859 | 61.6201 | 61.6943 | 61.5138 | 61.6602 | 0.16763 | 0.0602 | 0.042933 | 0.020759 | 0.068307 | 0.14967 | -0.076458 | 59.6141 | 59.6725 | 59.6782 | 59.6362 | 61.6704 | 61.7447 | 61.5641 | 61.7106 | -2.0563 | -1.95 | -1.9922 | -1.8859
155.8125 | 121.788 | -61.6562 | 59.848 | 0.11727 | 0.005267 | -0.007421 | -0.029595 | 0.013375 | 0.09474 | -0.12681 | 59.5592 | 59.6222 | 59.6325 | 59.5859 | 61.6247 | 61.6943 | 61.5138 | 61.6602 | 0.16763 | 0.055621 | 0.042933 | 0.020759 | 0.063729 | 0.14509 | -0.076458 | 59.6095 | 59.6725 | 59.6828 | 59.6362 | 61.675 | 61.7447 | 61.5641 | 61.7106 | -2.0655 | -1.9546 | -1.9922 | -1.8813
157.5625 | 121.7194 | -61.7386 | 59.8434 | 0.12185 | -0.00389 | -0.002842 | -0.034174 | 0.008797 | 0.099318 | -0.12681 | 59.5638 | 59.6176 | 59.6233 | 59.5813 | 61.6201 | 61.6989 | 61.5184 | 61.6602 | 0.1722 | 0.046464 | 0.047512 | 0.01618 | 0.059151 | 0.14967 | -0.076458 | 59.6141 | 59.6679 | 59.6737 | 59.6317 | 61.6704 | 61.7493 | 61.5687 | 61.7106 | -2.0563 | -1.9546 | -1.9968 | -1.8951
159.2969 | 121.7194 | -61.8393 | 59.7153 | 0.11727 | 0.009846 | -0.002842 | -0.034174 | 0.013375 | 0.099318 | -0.12223 | 59.5638 | 59.6176 | 59.6187 | 59.5905 | 61.6247 | 61.6898 | 61.5046 | 61.6557 | 0.16763 | 0.0602 | 0.047512 | 0.01618 | 0.063729 | 0.14967 | -0.07188 | 59.6141 | 59.6679 | 59.6691 | 59.6408 | 61.675 | 61.7401 | 61.555 | 61.706 | -2.0609 | -1.9409 | -2.0059 | -1.8859
161.0312 | 121.8109 | -61.7432 | 59.7794 | 0.12185 | 0.005267 | -0.012 | -0.034174 | 0.004219 | 0.1039 | -0.13139 | 59.5592 | 59.6176 | 59.6233 | 59.5859 | 61.6247 | 61.6943 | 61.5184 | 61.6602 | 0.1722 | 0.055621 | 0.038354 | 0.01618 | 0.054573 | 0.15425 | -0.081036 | 59.6095 | 59.6679 | 59.6737 | 59.6362 | 61.675 | 61.7447 | 61.5687 | 61.7106 | -2.0655 | -1.9592 | -2.0014 | -1.8951
162.7812 | 121.7926 | -61.7249 | 59.7794 | 0.12185 | 0.000689 | -0.012 | -0.034174 | 0.008797 | 0.09474 | -0.13597 | 59.5592 | 59.6084 | 59.6233 | 59.5859 | 61.6201 | 61.6989 | 61.5092 | 61.6648 | 0.1722 | 0.051043 | 0.038354 | 0.01618 | 0.059151 | 0.14509 | -0.085614 | 59.6095 | 59.6588 | 59.6737 | 59.6362 | 61.6704 | 61.7493 | 61.5596 | 61.7152 | -2.0609 | -1.95 | -1.9968 | -1.8859
164.5312 | 121.8384 | -61.6379 | 59.8343 | 0.11727 | 0.005267 | -0.002842 | -0.034174 | 0.013375 | 0.09474 | -0.13597 | 59.5592 | 59.613 | 59.6187 | 59.5813 | 61.6338 | 61.6898 | 61.5092 | 61.6602 | 0.16763 | 0.055621 | 0.047512 | 0.01618 | 0.063729 | 0.14509 | -0.085614 | 59.6095 | 59.6634 | 59.6691 | 59.6317 | 61.6842 | 61.7401 | 61.5596 | 61.7106 | -2.0746 | -1.95 | -2.0151 | -1.8905
166.2812 | 121.7468 | -61.7752 | 59.7656 | 0.12185 | 0.005267 | -0.002842 | -0.038752 | 0.017953 | 0.10848 | -0.12681 | 59.5638 | 59.6176 | 59.6279 | 59.5859 | 61.6247 | 61.7035 | 61.5092 | 61.6557 | 0.1722 | 0.055621 | 0.047512 | 0.011602 | 0.068307 | 0.15883 | -0.076458 | 59.6141 | 59.6679 | 59.6782 | 59.6362 | 61.675 | 61.7539 | 61.5596 | 61.706 | -2.0609 | -1.9454 | -1.9968 | -1.8813
167.9688 | 121.7422 | -61.7523 | 59.7656 | 0.12643 | 0.000689 | -0.007421 | -0.029595 | 0.008797 | 0.1039 | -0.13139 | 59.5592 | 59.6222 | 59.6233 | 59.5859 | 61.6292 | 61.6989 | 61.5046 | 61.6557 | 0.17678 | 0.051043 | 0.042933 | 0.020759 | 0.059151 | 0.15425 | -0.081036 | 59.6095 | 59.6725 | 59.6737 | 59.6362 | 61.6796 | 61.7493 | 61.555 | 61.706 | -2.0701 | -1.9454 | -2.0059 | -1.8813
169.7188 | 121.7789 | -61.7569 | 59.7931 | 0.12185 | 0.000689 | -0.012 | -0.034174 | 0.013375 | 0.09474 | -0.13139 | 59.5638 | 59.6222 | 59.6187 | 59.5859 | 61.6247 | 61.6989 | 61.5046 | 61.6602 | 0.1722 | 0.051043 | 0.038354 | 0.01618 | 0.063729 | 0.14509 | -0.081036 | 59.6141 | 59.6725 | 59.6691 | 59.6362 | 61.675 | 61.7493 | 61.555 | 61.7106 | -2.0609 | -1.9409 | -2.0059 | -1.8859
171.4844 | 121.8338 | -61.6333 | 59.8297 | 0.11727 | 0.005267 | -0.012 | -0.034174 | 0.008797 | 0.09474 | -0.13139 | 59.5638 | 59.613 | 59.6279 | 59.5813 | 61.6247 | 61.6943 | 61.5046 | 61.6602 | 0.16763 | 0.055621 | 0.038354 | 0.01618 | 0.059151 | 0.14509 | -0.081036 | 59.6141 | 59.6634 | 59.6782 | 59.6317 | 61.675 | 61.7447 | 61.555 | 61.7106 | -2.0609 | -1.9409 | -1.9968 | -1.8767
173.2344 | 121.7102 | -61.7065 | 59.848 | 0.12185 | -0.00389 | -0.007421 | -0.034174 | 0.013375 | 0.1039 | -0.13597 | 59.5592 | 59.613 | 59.6279 | 59.5859 | 61.6247 | 61.6989 | 61.5046 | 61.6602 | 0.1722 | 0.046464 | 0.042933 | 0.01618 | 0.063729 | 0.15425 | -0.085614 | 59.6095 | 59.6634 | 59.6782 | 59.6362 | 61.675 | 61.7493 | 61.555 | 61.7106 | -2.0655 | -1.9454 | -1.9968 | -1.8767
175 | 121.6919 | -61.8118 | 59.7244 | 0.12643 | -0.00389 | -0.007421 | -0.029595 | 0.013375 | 0.1039 | -0.12223 | 59.5638 | 59.6176 | 59.6142 | 59.5813 | 61.6201 | 61.6989 | 61.5 | 61.6648 | 0.17678 | 0.046464 | 0.042933 | 0.020759 | 0.063729 | 0.15425 | -0.07188 | 59.6141 | 59.6679 | 59.6645 | 59.6317 | 61.6704 | 61.7493 | 61.5504 | 61.7152 | -2.0563 | -1.9363 | -2.0059 | -1.8859
176.6719 | 121.8521 | -61.6379 | 59.8251 | 0.12643 | 0.000689 | -0.012 | -0.038752 | -0.000359 | 0.090161 | -0.13139 | 59.5592 | 59.613 | 59.6279 | 59.5813 | 61.6201 | 61.6943 | 61.5046 | 61.6602 | 0.17678 | 0.051043 | 0.038354 | 0.011602 | 0.049995 | 0.14052 | -0.081036 | 59.6095 | 59.6634 | 59.6782 | 59.6317 | 61.6704 | 61.7447 | 61.555 | 61.7106 | -2.0609 | -1.9454 | -1.9922 | -1.8767
178.4219 | 121.8155 | -61.7615 | 59.6786 | 0.12185 | 0.005267 | -0.016578 | -0.034174 | 0.008797 | 0.09474 | -0.13139 | 59.5638 | 59.613 | 59.6142 | 59.5813 | 61.6247 | 61.6943 | 61.5046 | 61.6602 | 0.1722 | 0.055621 | 0.033776 | 0.01618 | 0.059151 | 0.14509 | -0.081036 | 59.6141 | 59.6634 | 59.6645 | 59.6317 | 61.675 | 61.7447 | 61.555 | 61.7106 | -2.0609 | -1.9409 | -2.0105 | -1.8905
180.1094 | 121.7651 | -61.7661 | 59.7794 | 0.12643 | 0.005267 | -0.007421 | -0.034174 | 0.008797 | 0.10848 | -0.13139 | 59.5638 | 59.613 | 59.6279 | 59.5905 | 61.6247 | 61.6898 | 61.5046 | 61.6511 | 0.17678 | 0.055621 | 0.042933 | 0.01618 | 0.059151 | 0.15883 | -0.081036 | 59.6141 | 59.6634 | 59.6782 | 59.6408 | 61.675 | 61.7401 | 61.555 | 61.7014 | -2.0609 | -1.9409 | -1.9968 | -1.8767
181.8438 | 121.843 | -61.6699 | 59.816 | 0.12185 | 0.000689 | -0.016578 | -0.029595 | 0.008797 | 0.099318 | -0.13139 | 59.5592 | 59.6222 | 59.6279 | 59.5859 | 61.6247 | 61.7035 | 61.5092 | 61.6557 | 0.1722 | 0.051043 | 0.033776 | 0.020759 | 0.059151 | 0.14967 | -0.081036 | 59.6095 | 59.6725 | 59.6782 | 59.6362 | 61.675 | 61.7539 | 61.5596 | 61.706 | -2.0655 | -1.95 | -1.9968 | -1.8813
183.5781 | 121.8796 | -61.6562 | 59.8343 | 0.12185 | 0.000689 | -0.012 | -0.034174 | 0.008797 | 0.099318 | -0.13139 | 59.5546 | 59.6222 | 59.6233 | 59.5813 | 61.6201 | 61.6943 | 61.5 | 61.6602 | 0.1722 | 0.051043 | 0.038354 | 0.01618 | 0.059151 | 0.14967 | -0.081036 | 59.605 | 59.6725 | 59.6737 | 59.6317 | 61.6704 | 61.7447 | 61.5504 | 61.7106 | -2.0655 | -1.9454 | -1.9968 | -1.8767
185.2656 | 121.7194 | -61.7203 | 59.8343 | 0.12185 | 0.005267 | -0.016578 | -0.025017 | 0.008797 | 0.1039 | -0.12223 | 59.5592 | 59.613 | 59.6279 | 59.5859 | 61.6201 | 61.6989 | 61.5046 | 61.6602 | 0.1722 | 0.055621 | 0.033776 | 0.025337 | 0.059151 | 0.15425 | -0.07188 | 59.6095 | 59.6634 | 59.6782 | 59.6362 | 61.6704 | 61.7493 | 61.555 | 61.7106 | -2.0609 | -1.9454 | -1.9922 | -1.8767
187 | 121.6965 | -61.8118 | 59.7244 | 0.12185 | 0.009846 | -0.007421 | -0.025017 | 0.017953 | 0.1039 | -0.13139 | 59.5592 | 59.6222 | 59.6279 | 59.5951 | 61.6247 | 61.6898 | 61.5046 | 61.6465 | 0.1722 | 0.0602 | 0.042933 | 0.025337 | 0.068307 | 0.15425 | -0.081036 | 59.6095 | 59.6725 | 59.6782 | 59.6454 | 61.675 | 61.7401 | 61.555 | 61.6969 | -2.0655 | -1.9454 | -1.9968 | -1.8767
188.7344 | 121.7102 | -61.8073 | 59.7382 | 0.12185 | 0.019004 | 0.001736 | -0.034174 | 0.013375 | 0.09474 | -0.13139 | 59.5638 | 59.6176 | 59.6187 | 59.5859 | 61.6247 | 61.6852 | 61.5046 | 61.6602 | 0.1722 | 0.069358 | 0.05209 | 0.01618 | 0.063729 | 0.14509 | -0.081036 | 59.6141 | 59.6679 | 59.6691 | 59.6362 | 61.675 | 61.7355 | 61.555 | 61.7106 | -2.0609 | -1.9409 | -2.0059 | -1.8859
190.5 | 121.8521 | -61.6333 | 59.816 | 0.11727 | 0.000689 | -0.007421 | -0.038752 | 0.008797 | 0.099318 | -0.13597 | 59.5546 | 59.613 | 59.6233 | 59.5813 | 61.6247 | 61.6943 | 61.5092 | 61.6511 | 0.16763 | 0.051043 | 0.042933 | 0.011602 | 0.059151 | 0.14967 | -0.085614 | 59.605 | 59.6634 | 59.6737 | 59.6317 | 61.675 | 61.7447 | 61.5596 | 61.7014 | -2.0701 | -1.9546 | -2.0014 | -1.8859
192.1719 | 121.8201 | -61.7706 | 59.7153 | 0.11269 | -0.00389 | -0.012 | -0.038752 | 0.008797 | 0.09474 | -0.12681 | 59.5546 | 59.613 | 59.6279 | 59.5813 | 61.6292 | 61.6989 | 61.5046 | 61.6511 | 0.16305 | 0.046464 | 0.038354 | 0.011602 | 0.059151 | 0.14509 | -0.076458 | 59.605 | 59.6634 | 59.6782 | 59.6317 | 61.6796 | 61.7493 | 61.555 | 61.7014 | -2.0746 | -1.95 | -2.0014 | -1.8767
193.9219 | 121.8384 | -61.6562 | 59.8206 | 0.12185 | 0.000689 | -0.012 | -0.038752 | 0.004219 | 0.1039 | -0.13139 | 59.5546 | 59.6176 | 59.6187 | 59.5813 | 61.6201 | 61.6898 | 61.5092 | 61.6557 | 0.1722 | 0.051043 | 0.038354 | 0.011602 | 0.054573 | 0.15425 | -0.081036 | 59.605 | 59.6679 | 59.6691 | 59.6317 | 61.6704 | 61.7401 | 61.5596 | 61.706 | -2.0655 | -1.9546 | -2.0014 | -1.8905
195.6719 | 121.7972 | -61.7706 | 59.7015 | 0.12185 | 0.014425 | -0.007421 | -0.034174 | 0.013375 | 0.099318 | -0.12681 | 59.5638 | 59.6267 | 59.6279 | 59.5859 | 61.6201 | 61.6943 | 61.5046 | 61.6557 | 0.1722 | 0.064779 | 0.042933 | 0.01618 | 0.063729 | 0.14967 | -0.076458 | 59.6141 | 59.6771 | 59.6782 | 59.6362 | 61.6704 | 61.7447 | 61.555 | 61.706 | -2.0563 | -1.9409 | -1.9922 | -1.8767
197.3594 | 121.7056 | -61.702 | 59.8343 | 0.12185 | 0.005267 | -0.007421 | -0.034174 | 0.008797 | 0.099318 | -0.13139 | 59.5546 | 59.6176 | 59.6187 | 59.5859 | 61.6247 | 61.6898 | 61.5046 | 61.6557 | 0.1722 | 0.055621 | 0.042933 | 0.01618 | 0.059151 | 0.14967 | -0.081036 | 59.605 | 59.6679 | 59.6691 | 59.6362 | 61.675 | 61.7401 | 61.555 | 61.706 | -2.0701 | -1.95 | -2.0059 | -1.8859
199.1094 | 121.7834 | -61.647 | 59.8663 | 0.11727 | 0.000689 | -0.012 | -0.029595 | 0.013375 | 0.1039 | -0.13139 | 59.5592 | 59.6176 | 59.6325 | 59.5813 | 61.6201 | 61.6898 | 61.5092 | 61.6557 | 0.16763 | 0.051043 | 0.038354 | 0.020759 | 0.063729 | 0.15425 | -0.081036 | 59.6095 | 59.6679 | 59.6828 | 59.6317 | 61.6704 | 61.7401 | 61.5596 | 61.706 | -2.0609 | -1.95 | -1.9876 | -1.8767
200.8594 | 121.8246 | -61.6425 | 59.8297 | 0.12185 | 0.000689 | -0.016578 | -0.029595 | 0.008797 | 0.099318 | -0.13139 | 59.5592 | 59.6176 | 59.6187 | 59.5813 | 61.6247 | 61.6943 | 61.5046 | 61.6557 | 0.1722 | 0.051043 | 0.033776 | 0.020759 | 0.059151 | 0.14967 | -0.081036 | 59.6095 | 59.6679 | 59.6691 | 59.6317 | 61.675 | 61.7447 | 61.555 | 61.706 | -2.0655 | -1.9454 | -2.0059 | -1.8859
202.6094 | 121.7422 | -61.7615 | 59.7427 | 0.12185 | 0.009846 | -0.007421 | -0.025017 | 0.008797 | 0.1039 | -0.12681 | 59.5592 | 59.6176 | 59.6233 | 59.5859 | 61.6155 | 61.6989 | 61.5046 | 61.6602 | 0.1722 | 0.0602 | 0.042933 | 0.025337 | 0.059151 | 0.15425 | -0.076458 | 59.6095 | 59.6679 | 59.6737 | 59.6362 | 61.6659 | 61.7493 | 61.555 | 61.7106 | -2.0563 | -1.9454 | -1.9922 | -1.8813
204.3594 | 121.8155 | -61.647 | 59.8068 | 0.12643 | 0.000689 | -0.012 | -0.025017 | 0.008797 | 0.09474 | -0.13139 | 59.5638 | 59.613 | 59.6187 | 59.5767 | 61.6338 | 61.6989 | 61.5046 | 61.6602 | 0.17678 | 0.051043 | 0.038354 | 0.025337 | 0.059151 | 0.14509 | -0.081036 | 59.6141 | 59.6634 | 59.6691 | 59.6271 | 61.6842 | 61.7493 | 61.555 | 61.7106 | -2.0701 | -1.9409 | -2.0151 | -1.8859
206.0469 | 121.7285 | -61.8073 | 59.6924 | 0.12643 | 0.014425 | -0.007421 | -0.029595 | 0.013375 | 0.099318 | -0.13139 | 59.5546 | 59.6222 | 59.6279 | 59.5767 | 61.6155 | 61.6943 | 61.5 | 61.6557 | 0.17678 | 0.064779 | 0.042933 | 0.020759 | 0.063729 | 0.14967 | -0.081036 | 59.605 | 59.6725 | 59.6782 | 59.6271 | 61.6659 | 61.7447 | 61.5504 | 61.706 | -2.0609 | -1.9454 | -1.9876 | -1.8722
207.7969 | 121.8384 | -61.7523 | 59.6924 | 0.11727 | 0.005267 | -0.007421 | -0.034174 | 0.004219 | 0.099318 | -0.12681 | 59.5638 | 59.613 | 59.6233 | 59.5813 | 61.6201 | 61.6943 | 61.5 | 61.6602 | 0.16763 | 0.055621 | 0.042933 | 0.01618 | 0.054573 | 0.14967 | -0.076458 | 59.6141 | 59.6634 | 59.6737 | 59.6317 | 61.6704 | 61.7447 | 61.5504 | 61.7106 | -2.0563 | -1.9363 | -1.9968 | -1.8767
209.4844 | 121.7285 | -61.8027 | 59.7061 | 0.12643 | 0.009846 | -0.002842 | -0.034174 | 0.013375 | 0.10848 | -0.13139 | 59.5592 | 59.6176 | 59.6233 | 59.5813 | 61.6155 | 61.6898 | 61.4955 | 61.6511 | 0.17678 | 0.0602 | 0.047512 | 0.01618 | 0.063729 | 0.15883 | -0.081036 | 59.6095 | 59.6679 | 59.6737 | 59.6317 | 61.6659 | 61.7401 | 61.5458 | 61.7014 | -2.0563 | -1.9363 | -1.9922 | -1.8722
211.2344 | 121.7102 | -61.6882 | 59.8434 | 0.11727 | 0.014425 | -0.002842 | -0.029595 | 0.004219 | 0.099318 | -0.12223 | 59.5638 | 59.6176 | 59.6233 | 59.5813 | 61.6201 | 61.6898 | 61.5046 | 61.6602 | 0.16763 | 0.064779 | 0.047512 | 0.020759 | 0.054573 | 0.14967 | -0.07188 | 59.6141 | 59.6679 | 59.6737 | 59.6317 | 61.6704 | 61.7401 | 61.555 | 61.7106 | -2.0563 | -1.9409 | -1.9968 | -1.8813
212.9844 | 121.8155 | -61.734 | 59.7107 | 0.11727 | 0.009846 | -0.012 | -0.029595 | 0.004219 | 0.10848 | -0.13597 | 59.5592 | 59.6176 | 59.6233 | 59.5859 | 61.6201 | 61.6943 | 61.4955 | 61.6557 | 0.16763 | 0.0602 | 0.038354 | 0.020759 | 0.054573 | 0.15883 | -0.085614 | 59.6095 | 59.6679 | 59.6737 | 59.6362 | 61.6704 | 61.7447 | 61.5458 | 61.706 | -2.0609 | -1.9363 | -1.9968 | -1.8722
214.6719 | 121.701 | -61.8073 | 59.729 | 0.12185 | 0.014425 | -0.007421 | -0.034174 | 0.008797 | 0.099318 | -0.11765 | 59.5638 | 59.6084 | 59.6233 | 59.5813 | 61.6247 | 61.6898 | 61.5 | 61.6465 | 0.1722 | 0.064779 | 0.042933 | 0.01618 | 0.059151 | 0.14967 | -0.067301 | 59.6141 | 59.6588 | 59.6737 | 59.6317 | 61.675 | 61.7401 | 61.5504 | 61.6969 | -2.0609 | -1.9363 | -2.0014 | -1.8767
216.4219 | 121.7056 | -61.8073 | 59.7198 | 0.11727 | 0.014425 | -0.002842 | -0.034174 | 0.013375 | 0.1039 | -0.12681 | 59.5546 | 59.6176 | 59.6233 | 59.5859 | 61.6201 | 61.6852 | 61.5 | 61.6511 | 0.16763 | 0.064779 | 0.047512 | 0.01618 | 0.063729 | 0.15425 | -0.076458 | 59.605 | 59.6679 | 59.6737 | 59.6362 | 61.6704 | 61.7355 | 61.5504 | 61.7014 | -2.0655 | -1.9454 | -1.9968 | -1.8767
218.1094 | 121.7972 | -61.6608 | 59.848 | 0.12643 | 0.000689 | -0.007421 | -0.029595 | 0.004219 | 0.09474 | -0.12681 | 59.5546 | 59.6084 | 59.6187 | 59.5767 | 61.6247 | 61.6989 | 61.4955 | 61.6511 | 0.17678 | 0.051043 | 0.042933 | 0.020759 | 0.054573 | 0.14509 | -0.076458 | 59.605 | 59.6588 | 59.6691 | 59.6271 | 61.675 | 61.7493 | 61.5458 | 61.7014 | -2.0701 | -1.9409 | -2.0059 | -1.8767
219.8594 | 121.7239 | -61.702 | 59.8114 | 0.12185 | 0.005267 | 0.001736 | -0.020438 | 0.008797 | 0.1039 | -0.12681 | 59.5592 | 59.613 | 59.6187 | 59.5813 | 61.6201 | 61.6943 | 61.5046 | 61.6602 | 0.1722 | 0.055621 | 0.05209 | 0.029916 | 0.059151 | 0.15425 | -0.076458 | 59.6095 | 59.6634 | 59.6691 | 59.6317 | 61.6704 | 61.7447 | 61.555 | 61.7106 | -2.0609 | -1.9454 | -2.0014 | -1.8859
221.5469 | 121.8246 | -61.615 | 59.8251 | 0.11727 | 0.005267 | -0.016578 | -0.043331 | 0.004219 | 0.09474 | -0.12681 | 59.5638 | 59.6176 | 59.6187 | 59.5859 | 61.6155 | 61.6989 | 61.4955 | 61.6557 | 0.16763 | 0.055621 | 0.033776 | 0.007023 | 0.054573 | 0.14509 | -0.076458 | 59.6141 | 59.6679 | 59.6691 | 59.6362 | 61.6659 | 61.7493 | 61.5458 | 61.706 | -2.0517 | -1.9317 | -1.9968 | -1.8767
223.2812 | 121.7194 | -61.7477 | 59.8251 | 0.11727 | 0.009846 | -0.002842 | -0.034174 | 0.013375 | 0.099318 | -0.12223 | 59.55 | 59.613 | 59.6187 | 59.5813 | 61.6201 | 61.6943 | 61.5 | 61.6511 | 0.16763 | 0.0602 | 0.047512 | 0.01618 | 0.063729 | 0.14967 | -0.07188 | 59.6004 | 59.6634 | 59.6691 | 59.6317 | 61.6704 | 61.7447 | 61.5504 | 61.7014 | -2.0701 | -1.95 | -2.0014 | -1.8813
225.0312 | 121.7789 | -61.6653 | 59.816 | 0.12185 | 0.014425 | -0.012 | -0.034174 | -0.000359 | 0.099318 | -0.12223 | 59.5546 | 59.6084 | 59.6233 | 59.5767 | 61.6201 | 61.6898 | 61.5 | 61.6557 | 0.1722 | 0.064779 | 0.038354 | 0.01618 | 0.049995 | 0.14967 | -0.07188 | 59.605 | 59.6588 | 59.6737 | 59.6271 | 61.6704 | 61.7401 | 61.5504 | 61.706 | -2.0655 | -1.9454 | -1.9968 | -1.8767
226.7031 | 121.7468 | -61.8073 | 59.6924 | 0.12185 | 0.009846 | -0.007421 | -0.034174 | 0.008797 | 0.099318 | -0.12681 | 59.5592 | 59.6084 | 59.6325 | 59.5813 | 61.6155 | 61.6898 | 61.5 | 61.6557 | 0.1722 | 0.0602 | 0.042933 | 0.01618 | 0.059151 | 0.14967 | -0.076458 | 59.6095 | 59.6588 | 59.6828 | 59.6317 | 61.6659 | 61.7401 | 61.5504 | 61.706 | -2.0563 | -1.9409 | -1.983 | -1.8676
228.4531 | 121.7743 | -61.6653 | 59.816 | 0.12185 | 0.009846 | -0.002842 | -0.038752 | 0.008797 | 0.090161 | -0.12681 | 59.5592 | 59.6176 | 59.6233 | 59.5859 | 61.6201 | 61.6852 | 61.5 | 61.6511 | 0.1722 | 0.0602 | 0.047512 | 0.011602 | 0.059151 | 0.14052 | -0.076458 | 59.6095 | 59.6679 | 59.6737 | 59.6362 | 61.6704 | 61.7355 | 61.5504 | 61.7014 | -2.0609 | -1.9409 | -1.9968 | -1.8767
230.125 | 121.7377 | -61.7889 | 59.697 | 0.12643 | 0.014425 | -0.002842 | -0.029595 | 0.013375 | 0.099318 | -0.12681 | 59.5546 | 59.613 | 59.6279 | 59.5767 | 61.6201 | 61.6852 | 61.5 | 61.6511 | 0.17678 | 0.064779 | 0.047512 | 0.020759 | 0.063729 | 0.14967 | -0.076458 | 59.605 | 59.6634 | 59.6782 | 59.6271 | 61.6704 | 61.7355 | 61.5504 | 61.7014 | -2.0655 | -1.9454 | -1.9922 | -1.8722
231.8594 | 121.7834 | -61.6974 | 59.7656 | 0.12643 | 0.005267 | -0.012 | -0.034174 | -0.000359 | 0.09474 | -0.12681 | 59.5546 | 59.6084 | 59.6233 | 59.5813 | 61.6155 | 61.6989 | 61.5 | 61.6602 | 0.17678 | 0.055621 | 0.038354 | 0.01618 | 0.049995 | 0.14509 | -0.076458 | 59.605 | 59.6588 | 59.6737 | 59.6317 | 61.6659 | 61.7493 | 61.5504 | 61.7106 | -2.0609 | -1.9454 | -1.9922 | -1.8767
233.5938 | 121.788 | -61.6837 | 59.7839 | 0.11727 | 0.014425 | -0.021157 | -0.038752 | 0.004219 | 0.090161 | -0.13139 | 59.5592 | 59.6222 | 59.6233 | 59.5813 | 61.6201 | 61.6898 | 61.5092 | 61.6511 | 0.16763 | 0.064779 | 0.029197 | 0.011602 | 0.054573 | 0.14052 | -0.081036 | 59.6095 | 59.6725 | 59.6737 | 59.6317 | 61.6704 | 61.7401 | 61.5596 | 61.7014 | -2.0609 | -1.95 | -1.9968 | -1.8859
235.3438 | 121.7468 | -61.7615 | 59.7427 | 0.12643 | 0.014425 | -0.007421 | -0.034174 | 0.013375 | 0.1039 | -0.13139 | 59.5592 | 59.6084 | 59.6279 | 59.5767 | 61.6155 | 61.6898 | 61.5 | 61.6419 | 0.17678 | 0.064779 | 0.042933 | 0.01618 | 0.063729 | 0.15425 | -0.081036 | 59.6095 | 59.6588 | 59.6782 | 59.6271 | 61.6659 | 61.7401 | 61.5504 | 61.6923 | -2.0563 | -1.9409 | -1.9876 | -1.8722
237.0469 | 121.6782 | -61.8256 | 59.729 | 0.13101 | 0.009846 | -0.012 | -0.025017 | 0.008797 | 0.099318 | -0.12223 | 59.5638 | 59.6176 | 59.6325 | 59.5813 | 61.6201 | 61.6898 | 61.4955 | 61.6511 | 0.18136 | 0.0602 | 0.038354 | 0.025337 | 0.059151 | 0.14967 | -0.07188 | 59.6141 | 59.6679 | 59.6828 | 59.6317 | 61.6704 | 61.7401 | 61.5458 | 61.7014 | -2.0563 | -1.9317 | -1.9876 | -1.863
238.7969 | 121.7285 | -61.7981 | 59.7015 | 0.11727 | 0.009846 | -0.002842 | -0.029595 | 0.004219 | 0.09474 | -0.12681 | 59.5683 | 59.6084 | 59.6187 | 59.5767 | 61.6109 | 61.6898 | 61.4955 | 61.6557 | 0.16763 | 0.0602 | 0.047512 | 0.020759 | 0.054573 | 0.14509 | -0.076458 | 59.6187 | 59.6588 | 59.6691 | 59.6271 | 61.6613 | 61.7401 | 61.5458 | 61.706 | -2.0426 | -1.9271 | -1.9922 | -1.8767
240.5469 | 121.8292 | -61.6516 | 59.8343 | 0.12185 | 0.009846 | -0.007421 | -0.038752 | -0.004937 | 0.099318 | -0.12681 | 59.5592 | 59.6176 | 59.6233 | 59.5767 | 61.6201 | 61.6898 | 61.5046 | 61.6511 | 0.1722 | 0.0602 | 0.042933 | 0.011602 | 0.045417 | 0.14967 | -0.076458 | 59.6095 | 59.6679 | 59.6737 | 59.6271 | 61.6704 | 61.7401 | 61.555 | 61.7014 | -2.0609 | -1.9454 | -1.9968 | -1.8813
242.2344 | 121.8246 | -61.7432 | 59.7107 | 0.12185 | 0.005267 | -0.007421 | -0.034174 | 0.004219 | 0.09474 | -0.13139 | 59.5592 | 59.613 | 59.6233 | 59.5859 | 61.6201 | 61.6898 | 61.5 | 61.6511 | 0.1722 | 0.055621 | 0.042933 | 0.01618 | 0.054573 | 0.14509 | -0.081036 | 59.6095 | 59.6634 | 59.6737 | 59.6362 | 61.6704 | 61.7401 | 61.5504 | 61.7014 | -2.0609 | -1.9409 | -1.9968 | -1.8767
243.9844 | 121.7056 | -61.7065 | 59.8297 | 0.13101 | 0.014425 | -0.012 | -0.034174 | 0.008797 | 0.1039 | -0.12681 | 59.5592 | 59.613 | 59.6233 | 59.5859 | 61.6201 | 61.6852 | 61.4955 | 61.6511 | 0.18136 | 0.064779 | 0.038354 | 0.01618 | 0.059151 | 0.15425 | -0.076458 | 59.6095 | 59.6634 | 59.6737 | 59.6362 | 61.6704 | 61.7355 | 61.5458 | 61.7014 | -2.0609 | -1.9363 | -1.9968 | -1.8722
245.7344 | 121.7056 | -61.8118 | 59.7427 | 0.12185 | 0.019004 | -0.007421 | -0.029595 | 0.013375 | 0.099318 | -0.12681 | 59.5546 | 59.6084 | 59.6279 | 59.5813 | 61.6201 | 61.6943 | 61.4955 | 61.6511 | 0.1722 | 0.069358 | 0.042933 | 0.020759 | 0.063729 | 0.14967 | -0.076458 | 59.605 | 59.6588 | 59.6782 | 59.6317 | 61.6704 | 61.7447 | 61.5458 | 61.7014 | -2.0655 | -1.9409 | -1.9922 | -1.8676
247.4219 | 121.7148 | -61.8256 | 59.7198 | 0.12643 | 0.014425 | -0.002842 | -0.034174 | 0.013375 | 0.1039 | -0.12681 | 59.5592 | 59.6084 | 59.6187 | 59.5859 | 61.6109 | 61.6898 | 61.4955 | 61.6465 | 0.17678 | 0.064779 | 0.047512 | 0.01618 | 0.063729 | 0.15425 | -0.076458 | 59.6095 | 59.6588 | 59.6691 | 59.6362 | 61.6613 | 61.7401 | 61.5458 | 61.6969 | -2.0517 | -1.9363 | -1.9922 | -1.8767
249.1562 | 121.6965 | -61.8439 | 59.729 | 0.12185 | 0.009846 | -0.007421 | -0.029595 | 0.004219 | 0.1039 | -0.13139 | 59.5592 | 59.6084 | 59.6279 | 59.5722 | 61.6201 | 61.6898 | 61.4909 | 61.6511 | 0.1722 | 0.0602 | 0.042933 | 0.020759 | 0.054573 | 0.15425 | -0.081036 | 59.6095 | 59.6588 | 59.6782 | 59.6225 | 61.6704 | 61.7401 | 61.5412 | 61.7014 | -2.0609 | -1.9317 | -1.9922 | -1.863
250.8438 | 121.8475 | -61.6425 | 59.8022 | 0.12185 | 0.005267 | -0.016578 | -0.029595 | 0.004219 | 0.090161 | -0.13139 | 59.5546 | 59.613 | 59.6233 | 59.5813 | 61.6155 | 61.6898 | 61.5046 | 61.6557 | 0.1722 | 0.055621 | 0.033776 | 0.020759 | 0.054573 | 0.14052 | -0.081036 | 59.605 | 59.6634 | 59.6737 | 59.6317 | 61.6659 | 61.7401 | 61.555 | 61.706 | -2.0609 | -1.95 | -1.9922 | -1.8813
252.5938 | 121.7056 | -61.8073 | 59.7153 | 0.12185 | 0.009846 | -0.002842 | -0.038752 | 0.008797 | 0.1039 | -0.12681 | 59.5592 | 59.613 | 59.6233 | 59.5722 | 61.6201 | 61.6898 | 61.4955 | 61.6511 | 0.1722 | 0.0602 | 0.047512 | 0.011602 | 0.059151 | 0.15425 | -0.076458 | 59.6095 | 59.6634 | 59.6737 | 59.6225 | 61.6704 | 61.7401 | 61.5458 | 61.7014 | -2.0609 | -1.9363 | -1.9968 | -1.8722
254.3281 | 121.8292 | -61.7523 | 59.7107 | 0.13101 | 0.009846 | -0.007421 | -0.038752 | 0.008797 | 0.09474 | -0.12223 | 59.5638 | 59.613 | 59.6187 | 59.5767 | 61.6155 | 61.6898 | 61.5 | 61.6557 | 0.18136 | 0.0602 | 0.042933 | 0.011602 | 0.059151 | 0.14509 | -0.07188 | 59.6141 | 59.6634 | 59.6691 | 59.6271 | 61.6659 | 61.7401 | 61.5504 | 61.706 | -2.0517 | -1.9363 | -1.9968 | -1.8813
256 | 121.8384 | -61.6379 | 59.8297 | 0.12643 | 0.000689 | -0.012 | -0.038752 | 0.004219 | 0.09474 | -0.12681 | 59.5546 | 59.613 | 59.6279 | 59.5813 | 61.6155 | 61.6852 | 61.5 | 61.6465 | 0.17678 | 0.051043 | 0.038354 | 0.011602 | 0.054573 | 0.14509 | -0.076458 | 59.605 | 59.6634 | 59.6782 | 59.6317 | 61.6659 | 61.7355 | 61.5504 | 61.6969 | -2.0609 | -1.9454 | -1.9876 | -1.8722
257.7344 | 121.6919 | -61.6974 | 59.8526 | 0.12185 | 0.009846 | -0.002842 | -0.034174 | 0.004219 | 0.099318 | -0.12223 | 59.55 | 59.613 | 59.6279 | 59.5722 | 61.6155 | 61.6852 | 61.4909 | 61.6465 | 0.1722 | 0.0602 | 0.047512 | 0.01618 | 0.054573 | 0.14967 | -0.07188 | 59.6004 | 59.6634 | 59.6782 | 59.6225 | 61.6659 | 61.7355 | 61.5412 | 61.6969 | -2.0655 | -1.9409 | -1.9876 | -1.863
259.4844 | 121.7743 | -61.6882 | 59.7565 | 0.12643 | 0.009846 | -0.012 | -0.034174 | 0.004219 | 0.1039 | -0.12223 | 59.5638 | 59.613 | 59.6233 | 59.5813 | 61.6155 | 61.6943 | 61.5 | 61.6465 | 0.17678 | 0.0602 | 0.038354 | 0.01618 | 0.054573 | 0.15425 | -0.07188 | 59.6141 | 59.6634 | 59.6737 | 59.6317 | 61.6659 | 61.7447 | 61.5504 | 61.6969 | -2.0517 | -1.9363 | -1.9922 | -1.8767
261.1719 | 121.8246 | -61.7523 | 59.7107 | 0.12643 | 0.009846 | -0.012 | -0.038752 | 0.008797 | 0.099318 | -0.11765 | 59.5592 | 59.613 | 59.6233 | 59.5676 | 61.6155 | 61.6852 | 61.4909 | 61.6557 | 0.17678 | 0.0602 | 0.038354 | 0.011602 | 0.059151 | 0.14967 | -0.067301 | 59.6095 | 59.6634 | 59.6737 | 59.6179 | 61.6659 | 61.7355 | 61.5412 | 61.706 | -2.0563 | -1.9317 | -1.9922 | -1.8676
262.9219 | 121.6873 | -61.7157 | 59.8434 | 0.12643 | 0.005267 | -0.007421 | -0.029595 | -0.000359 | 0.099318 | -0.12681 | 59.55 | 59.613 | 59.6233 | 59.5722 | 61.6109 | 61.6898 | 61.4909 | 61.6511 | 0.17678 | 0.055621 | 0.042933 | 0.020759 | 0.049995 | 0.14967 | -0.076458 | 59.6004 | 59.6634 | 59.6737 | 59.6225 | 61.6613 | 61.7401 | 61.5412 | 61.7014 | -2.0609 | -1.9409 | -1.9876 | -1.8676
264.6719 | 121.6919 | -61.6699 | 59.8389 | 0.12643 | 0.009846 | -0.012 | -0.034174 | -0.000359 | 0.099318 | -0.12681 | 59.5638 | 59.613 | 59.6325 | 59.5767 | 61.6155 | 61.6898 | 61.5046 | 61.6465 | 0.17678 | 0.0602 | 0.038354 | 0.01618 | 0.049995 | 0.14967 | -0.076458 | 59.6141 | 59.6634 | 59.6828 | 59.6271 | 61.6659 | 61.7401 | 61.555 | 61.6969 | -2.0517 | -1.9409 | -1.983 | -1.8722
266.3594 | 121.7743 | -61.7111 | 59.7702 | 0.12185 | 0.000689 | -0.007421 | -0.029595 | -0.000359 | 0.099318 | -0.12681 | 59.5546 | 59.613 | 59.6187 | 59.5859 | 61.6155 | 61.6806 | 61.5 | 61.6557 | 0.1722 | 0.051043 | 0.042933 | 0.020759 | 0.049995 | 0.14967 | -0.076458 | 59.605 | 59.6634 | 59.6691 | 59.6362 | 61.6659 | 61.731 | 61.5504 | 61.706 | -2.0609 | -1.9454 | -1.9968 | -1.8813
268.1094 | 121.7743 | -61.6974 | 59.761 | 0.12643 | 0.005267 | -0.012 | -0.034174 | -0.000359 | 0.09474 | -0.13139 | 59.5592 | 59.613 | 59.6279 | 59.5813 | 61.6155 | 61.6852 | 61.4955 | 61.6557 | 0.17678 | 0.055621 | 0.038354 | 0.01618 | 0.049995 | 0.14509 | -0.081036 | 59.6095 | 59.6634 | 59.6782 | 59.6317 | 61.6659 | 61.7355 | 61.5458 | 61.706 | -2.0563 | -1.9363 | -1.9876 | -1.8676
269.7969 | 121.8384 | -61.6516 | 59.8114 | 0.12185 | -0.008469 | -0.007421 | -0.034174 | 0.004219 | 0.099318 | -0.13139 | 59.55 | 59.6084 | 59.6187 | 59.5722 | 61.6155 | 61.6806 | 61.4955 | 61.6557 | 0.1722 | 0.041885 | 0.042933 | 0.01618 | 0.054573 | 0.14967 | -0.081036 | 59.6004 | 59.6588 | 59.6691 | 59.6225 | 61.6659 | 61.731 | 61.5458 | 61.706 | -2.0655 | -1.9454 | -1.9968 | -1.8767
271.5469 | 121.8109 | -61.6562 | 59.8206 | 0.13559 | 0.000689 | -0.012 | -0.034174 | 0.004219 | 0.090161 | -0.13139 | 59.5546 | 59.613 | 59.6142 | 59.5767 | 61.6201 | 61.6943 | 61.4955 | 61.6511 | 0.18594 | 0.051043 | 0.038354 | 0.01618 | 0.054573 | 0.14052 | -0.081036 | 59.605 | 59.6634 | 59.6645 | 59.6271 | 61.6704 | 61.7447 | 61.5458 | 61.7014 | -2.0655 | -1.9409 | -2.0059 | -1.8813
273.2812 | 121.7834 | -61.7157 | 59.7656 | 0.12643 | -0.00389 | -0.012 | -0.034174 | -0.000359 | 0.090161 | -0.13139 | 59.5546 | 59.613 | 59.6233 | 59.5676 | 61.6155 | 61.6898 | 61.5 | 61.6511 | 0.17678 | 0.046464 | 0.038354 | 0.01618 | 0.049995 | 0.14052 | -0.081036 | 59.605 | 59.6634 | 59.6737 | 59.6179 | 61.6659 | 61.7401 | 61.5504 | 61.7014 | -2.0609 | -1.9454 | -1.9922 | -1.8767
275.0312 | 121.843 | -61.6516 | 59.8114 | 0.12643 | -0.00389 | -0.012 | -0.034174 | -0.000359 | 0.099318 | -0.12223 | 59.5592 | 59.613 | 59.6187 | 59.5813 | 61.6201 | 61.6852 | 61.5046 | 61.6557 | 0.17678 | 0.046464 | 0.038354 | 0.01618 | 0.049995 | 0.14967 | -0.07188 | 59.6095 | 59.6634 | 59.6691 | 59.6317 | 61.6704 | 61.7355 | 61.555 | 61.706 | -2.0609 | -1.9454 | -2.0014 | -1.8859
276.7812 | 121.7972 | -61.7752 | 59.6832 | 0.12643 | 0.005267 | -0.007421 | -0.038752 | 0.008797 | 0.1039 | -0.12681 | 59.5592 | 59.6176 | 59.6233 | 59.5813 | 61.6155 | 61.6852 | 61.4955 | 61.6465 | 0.17678 | 0.055621 | 0.042933 | 0.011602 | 0.059151 | 0.15425 | -0.076458 | 59.6095 | 59.6679 | 59.6737 | 59.6317 | 61.6659 | 61.7355 | 61.5458 | 61.6969 | -2.0563 | -1.9363 | -1.9922 | -1.8722
278.4531 | 121.7377 | -61.7249 | 59.7931 | 0.13101 | 0.005267 | -0.012 | -0.034174 | 0.004219 | 0.1039 | -0.12223 | 59.5546 | 59.613 | 59.6233 | 59.5813 | 61.6109 | 61.6806 | 61.4955 | 61.6557 | 0.18136 | 0.055621 | 0.038354 | 0.01618 | 0.054573 | 0.15425 | -0.07188 | 59.605 | 59.6634 | 59.6737 | 59.6317 | 61.6613 | 61.731 | 61.5458 | 61.706 | -2.0563 | -1.9409 | -1.9876 | -1.8722
280.1875 | 121.7056 | -61.702 | 59.8297 | 0.12643 | 0.005267 | -0.016578 | -0.034174 | -0.000359 | 0.09474 | -0.12223 | 59.5592 | 59.6176 | 59.6187 | 59.5813 | 61.6109 | 61.6852 | 61.5 | 61.6511 | 0.17678 | 0.055621 | 0.033776 | 0.01618 | 0.049995 | 0.14509 | -0.07188 | 59.6095 | 59.6679 | 59.6691 | 59.6317 | 61.6613 | 61.7355 | 61.5504 | 61.7014 | -2.0517 | -1.9409 | -1.9922 | -1.8813
281.9375 | 121.6919 | -61.702 | 59.816 | 0.12643 | 0.000689 | -0.007421 | -0.034174 | -0.000359 | 0.09474 | -0.12223 | 59.5592 | 59.6084 | 59.6233 | 59.5722 | 61.6201 | 61.6898 | 61.5 | 61.6465 | 0.17678 | 0.051043 | 0.042933 | 0.01618 | 0.049995 | 0.14509 | -0.07188 | 59.6095 | 59.6588 | 59.6737 | 59.6225 | 61.6704 | 61.7401 | 61.5504 | 61.6969 | -2.0609 | -1.9409 | -1.9968 | -1.8767
283.6875 | 121.701 | -61.7981 | 59.7198 | 0.13559 | 0.000689 | -0.007421 | -0.034174 | 0.004219 | 0.1039 | -0.13139 | 59.5546 | 59.6176 | 59.6233 | 59.5767 | 61.6155 | 61.6898 | 61.4863 | 61.6511 | 0.18594 | 0.051043 | 0.042933 | 0.01618 | 0.054573 | 0.15425 | -0.081036 | 59.605 | 59.6679 | 59.6737 | 59.6271 | 61.6659 | 61.7401 | 61.5367 | 61.7014 | -2.0609 | -1.9317 | -1.9922 | -1.863
285.375 | 121.7697 | -61.702 | 59.7702 | 0.11727 | 0.000689 | -0.016578 | -0.034174 | -0.000359 | 0.09474 | -0.12681 | 59.5638 | 59.6176 | 59.6233 | 59.5813 | 61.6109 | 61.6898 | 61.4955 | 61.6557 | 0.16763 | 0.051043 | 0.033776 | 0.01618 | 0.049995 | 0.14509 | -0.076458 | 59.6141 | 59.6679 | 59.6737 | 59.6317 | 61.6613 | 61.7401 | 61.5458 | 61.706 | -2.0472 | -1.9317 | -1.9876 | -1.8722
287.1406 | 121.7651 | -61.7889 | 59.7153 | 0.12185 | 0.005267 | -0.007421 | -0.029595 | -0.000359 | 0.09474 | -0.12223 | 59.5592 | 59.6084 | 59.6187 | 59.5767 | 61.6155 | 61.6852 | 61.4955 | 61.6419 | 0.1722 | 0.055621 | 0.042933 | 0.020759 | 0.049995 | 0.14509 | -0.07188 | 59.6095 | 59.6588 | 59.6691 | 59.6271 | 61.6659 | 61.7355 | 61.5458 | 61.6923 | -2.0563 | -1.9363 | -1.9968 | -1.8767
288.8281 | 121.7148 | -61.7294 | 59.8114 | 0.12643 | 0.005267 | -0.012 | -0.025017 | 0.004219 | 0.10848 | -0.12223 | 59.5592 | 59.6176 | 59.6187 | 59.5767 | 61.6155 | 61.6852 | 61.4909 | 61.6419 | 0.17678 | 0.055621 | 0.038354 | 0.025337 | 0.054573 | 0.15883 | -0.07188 | 59.6095 | 59.6679 | 59.6691 | 59.6271 | 61.6659 | 61.7355 | 61.5412 | 61.6923 | -2.0563 | -1.9317 | -1.9968 | -1.8722
290.5781 | 121.7789 | -61.7065 | 59.7519 | 0.13101 | 0.005267 | -0.007421 | -0.034174 | 0.004219 | 0.090161 | -0.13139 | 59.5592 | 59.613 | 59.6233 | 59.5813 | 61.6155 | 61.6898 | 61.5 | 61.6465 | 0.18136 | 0.055621 | 0.042933 | 0.01618 | 0.054573 | 0.14052 | -0.081036 | 59.6095 | 59.6634 | 59.6737 | 59.6317 | 61.6659 | 61.7401 | 61.5504 | 61.6969 | -2.0563 | -1.9409 | -1.9922 | -1.8767
292.3281 | 121.7697 | -61.702 | 59.7702 | 0.12643 | 0.000689 | -0.012 | -0.038752 | -0.000359 | 0.09474 | -0.13139 | 59.5546 | 59.613 | 59.6187 | 59.5767 | 61.6155 | 61.6852 | 61.4955 | 61.6465 | 0.17678 | 0.051043 | 0.038354 | 0.011602 | 0.049995 | 0.14509 | -0.081036 | 59.605 | 59.6634 | 59.6691 | 59.6271 | 61.6659 | 61.7355 | 61.5458 | 61.6969 | -2.0609 | -1.9409 | -1.9968 | -1.8767
294 | 121.6827 | -61.7111 | 59.8389 | 0.13101 | 0.005267 | -0.002842 | -0.034174 | -0.000359 | 0.09474 | -0.12223 | 59.5592 | 59.6038 | 59.6233 | 59.5722 | 61.6155 | 61.6852 | 61.4955 | 61.6465 | 0.18136 | 0.055621 | 0.047512 | 0.01618 | 0.049995 | 0.14509 | -0.07188 | 59.6095 | 59.6542 | 59.6737 | 59.6225 | 61.6659 | 61.7355 | 61.5458 | 61.6969 | -2.0563 | -1.9363 | -1.9922 | -1.8722
295.7344 | 121.7239 | -61.7111 | 59.7656 | 0.13101 | 0.000689 | -0.012 | -0.029595 | 0.008797 | 0.1039 | -0.12223 | 59.5592 | 59.6084 | 59.6279 | 59.5767 | 61.6155 | 61.6806 | 61.4955 | 61.6465 | 0.18136 | 0.051043 | 0.038354 | 0.020759 | 0.059151 | 0.15425 | -0.07188 | 59.6095 | 59.6588 | 59.6782 | 59.6271 | 61.6659 | 61.731 | 61.5458 | 61.6969 | -2.0563 | -1.9363 | -1.9876 | -1.8676
297.4219 | 121.6827 | -61.702 | 59.848 | 0.13559 | -0.00389 | -0.012 | -0.038752 | 0.004219 | 0.099318 | -0.12681 | 59.5638 | 59.6176 | 59.6142 | 59.5722 | 61.6155 | 61.6852 | 61.4909 | 61.6465 | 0.18594 | 0.046464 | 0.038354 | 0.011602 | 0.054573 | 0.14967 | -0.076458 | 59.6141 | 59.6679 | 59.6645 | 59.6225 | 61.6659 | 61.7355 | 61.5412 | 61.6969 | -2.0517 | -1.9271 | -2.0014 | -1.8767
299.1562 | 121.7285 | -61.7294 | 59.7656 | 0.13101 | 0.005267 | -0.007421 | -0.034174 | 0.008797 | 0.1039 | -0.12223 | 59.55 | 59.6176 | 59.6142 | 59.5676 | 61.6155 | 61.6852 | 61.4955 | 61.6465 | 0.18136 | 0.055621 | 0.042933 | 0.01618 | 0.059151 | 0.15425 | -0.07188 | 59.6004 | 59.6679 | 59.6645 | 59.6179 | 61.6659 | 61.7355 | 61.5458 | 61.6969 | -2.0655 | -1.9454 | -2.0014 | -1.8813
300.9062 | 121.7743 | -61.6699 | 59.7794 | 0.13101 | -0.00389 | -0.007421 | -0.034174 | 0.004219 | 0.1039 | -0.13139 | 59.5592 | 59.6176 | 59.6233 | 59.5767 | 61.6109 | 61.6852 | 61.4955 | 61.6557 | 0.18136 | 0.046464 | 0.042933 | 0.01618 | 0.054573 | 0.15425 | -0.081036 | 59.6095 | 59.6679 | 59.6737 | 59.6271 | 61.6613 | 61.7355 | 61.5458 | 61.706 | -2.0517 | -1.9363 | -1.9876 | -1.8722
302.5938 | 121.7651 | -61.6974 | 59.7702 | 0.12643 | 0.000689 | -0.012 | -0.034174 | -0.000359 | 0.090161 | -0.13597 | 59.55 | 59.6084 | 59.6233 | 59.5767 | 61.6155 | 61.6898 | 61.4955 | 61.6465 | 0.17678 | 0.051043 | 0.038354 | 0.01618 | 0.049995 | 0.14052 | -0.085614 | 59.6004 | 59.6588 | 59.6737 | 59.6271 | 61.6659 | 61.7401 | 61.5458 | 61.6969 | -2.0655 | -1.9454 | -1.9922 | -1.8722
304.3438 | 121.8201 | -61.6287 | 59.816 | 0.13101 | -0.00389 | -0.012 | -0.038752 | -0.004937 | 0.099318 | -0.12681 | 59.55 | 59.6038 | 59.6096 | 59.5767 | 61.6155 | 61.6898 | 61.4909 | 61.6557 | 0.18136 | 0.046464 | 0.038354 | 0.011602 | 0.045417 | 0.14967 | -0.076458 | 59.6004 | 59.6542 | 59.6599 | 59.6271 | 61.6659 | 61.7401 | 61.5412 | 61.706 | -2.0655 | -1.9409 | -2.0059 | -1.8813
306.0312 | 121.8109 | -61.7386 | 59.6878 | 0.12643 | -0.00389 | -0.016578 | -0.038752 | 0.004219 | 0.099318 | -0.13139 | 59.5546 | 59.6176 | 59.6187 | 59.5676 | 61.6109 | 61.6852 | 61.4955 | 61.6511 | 0.17678 | 0.046464 | 0.033776 | 0.011602 | 0.054573 | 0.14967 | -0.081036 | 59.605 | 59.6679 | 59.6691 | 59.6179 | 61.6613 | 61.7355 | 61.5458 | 61.7014 | -2.0563 | -1.9409 | -1.9922 | -1.8767
307.7812 | 121.7239 | -61.702 | 59.8068 | 0.12643 | 0.000689 | -0.012 | -0.034174 | 0.004219 | 0.099318 | -0.12681 | 59.5592 | 59.613 | 59.6233 | 59.5859 | 61.6109 | 61.6852 | 61.4863 | 61.6374 | 0.17678 | 0.051043 | 0.038354 | 0.01618 | 0.054573 | 0.14967 | -0.076458 | 59.6095 | 59.6634 | 59.6737 | 59.6362 | 61.6613 | 61.7355 | 61.5367 | 61.6877 | -2.0517 | -1.9271 | -1.9876 | -1.863
309.4688 | 121.8201 | -61.6425 | 59.7839 | 0.12643 | -0.013048 | -0.016578 | -0.034174 | -0.004937 | 0.09474 | -0.13139 | 59.5638 | 59.6038 | 59.6187 | 59.5722 | 61.6064 | 61.6852 | 61.5 | 61.6465 | 0.17678 | 0.037306 | 0.033776 | 0.01618 | 0.045417 | 0.14509 | -0.081036 | 59.6141 | 59.6542 | 59.6691 | 59.6225 | 61.6567 | 61.7355 | 61.5504 | 61.6969 | -2.0426 | -1.9363 | -1.9876 | -1.8813
311.2188 | 121.7056 | -61.8073 | 59.7107 | 0.13101 | 0.000689 | 0.001736 | -0.025017 | 0.004219 | 0.099318 | -0.12223 | 59.5592 | 59.613 | 59.6187 | 59.5722 | 61.6155 | 61.6852 | 61.4909 | 61.6419 | 0.18136 | 0.051043 | 0.05209 | 0.025337 | 0.054573 | 0.14967 | -0.07188 | 59.6095 | 59.6634 | 59.6691 | 59.6225 | 61.6659 | 61.7355 | 61.5412 | 61.6923 | -2.0563 | -1.9317 | -1.9968 | -1.8722
312.9062 | 121.7285 | -61.7615 | 59.761 | 0.12643 | 0.000689 | -0.007421 | -0.025017 | -0.000359 | 0.099318 | -0.12681 | 59.5638 | 59.613 | 59.6187 | 59.5767 | 61.6155 | 61.6806 | 61.4909 | 61.6465 | 0.17678 | 0.051043 | 0.042933 | 0.025337 | 0.049995 | 0.14967 | -0.076458 | 59.6141 | 59.6634 | 59.6691 | 59.6271 | 61.6659 | 61.731 | 61.5412 | 61.6969 | -2.0517 | -1.9271 | -1.9968 | -1.8722
314.6562 | 121.8201 | -61.7432 | 59.697 | 0.13101 | 0.000689 | -0.007421 | -0.025017 | 0.004219 | 0.099318 | -0.13139 | 59.5546 | 59.613 | 59.6096 | 59.5722 | 61.6109 | 61.6806 | 61.5046 | 61.6511 | 0.18136 | 0.051043 | 0.042933 | 0.025337 | 0.054573 | 0.14967 | -0.081036 | 59.605 | 59.6634 | 59.6599 | 59.6225 | 61.6613 | 61.731 | 61.555 | 61.7014 | -2.0563 | -1.95 | -2.0014 | -1.8951
316.3438 | 121.7743 | -61.6425 | 59.8251 | 0.13559 | -0.008469 | -0.007421 | -0.034174 | -0.004937 | 0.099318 | -0.13139 | 59.55 | 59.6176 | 59.6233 | 59.5722 | 61.6155 | 61.6852 | 61.5 | 61.6511 | 0.18594 | 0.041885 | 0.042933 | 0.01618 | 0.045417 | 0.14967 | -0.081036 | 59.6004 | 59.6679 | 59.6737 | 59.6225 | 61.6659 | 61.7355 | 61.5504 | 61.7014 | -2.0655 | -1.95 | -1.9922 | -1.8767
318.0938 | 121.6827 | -61.8118 | 59.729 | 0.13101 | -0.00389 | -0.002842 | -0.029595 | 0.004219 | 0.1039 | -0.12681 | 59.5546 | 59.6176 | 59.6187 | 59.5722 | 61.6109 | 61.6806 | 61.5 | 61.6465 | 0.18136 | 0.046464 | 0.047512 | 0.020759 | 0.054573 | 0.15425 | -0.076458 | 59.605 | 59.6679 | 59.6691 | 59.6225 | 61.6613 | 61.731 | 61.5504 | 61.6969 | -2.0563 | -1.9454 | -1.9922 | -1.8813
319.7812 | 121.7056 | -61.702 | 59.8572 | 0.12643 | -0.00389 | -0.012 | -0.038752 | 0.004219 | 0.1039 | -0.13597 | 59.5638 | 59.613 | 59.6279 | 59.5767 | 61.6155 | 61.6852 | 61.5 | 61.6511 | 0.17678 | 0.046464 | 0.038354 | 0.011602 | 0.054573 | 0.15425 | -0.085614 | 59.6141 | 59.6634 | 59.6782 | 59.6271 | 61.6659 | 61.7355 | 61.5504 | 61.7014 | -2.0517 | -1.9363 | -1.9876 | -1.8722
321.5156 | 121.7697 | -61.7065 | 59.7565 | 0.12643 | -0.00389 | -0.016578 | -0.034174 | -0.000359 | 0.099318 | -0.13597 | 59.5546 | 59.6176 | 59.6233 | 59.5722 | 61.6155 | 61.6806 | 61.4909 | 61.6557 | 0.17678 | 0.046464 | 0.033776 | 0.01618 | 0.049995 | 0.14967 | -0.085614 | 59.605 | 59.6679 | 59.6737 | 59.6225 | 61.6659 | 61.731 | 61.5412 | 61.706 | -2.0609 | -1.9363 | -1.9922 | -1.8676
323.2656 | 121.701 | -61.6882 | 59.8297 | 0.13101 | 0.000689 | -0.012 | -0.029595 | 0.004219 | 0.1039 | -0.12223 | 59.5592 | 59.6084 | 59.6187 | 59.5767 | 61.6109 | 61.6898 | 61.4863 | 61.6465 | 0.18136 | 0.051043 | 0.038354 | 0.020759 | 0.054573 | 0.15425 | -0.07188 | 59.6095 | 59.6588 | 59.6691 | 59.6271 | 61.6613 | 61.7401 | 61.5367 | 61.6969 | -2.0517 | -1.9271 | -1.9922 | -1.8676
325.0156 | 121.7056 | -61.7935 | 59.729 | 0.13101 | 0.000689 | -0.002842 | -0.034174 | -0.000359 | 0.099318 | -0.12681 | 59.5592 | 59.613 | 59.6142 | 59.5722 | 61.6064 | 61.6898 | 61.4955 | 61.6419 | 0.18136 | 0.051043 | 0.047512 | 0.01618 | 0.049995 | 0.14967 | -0.076458 | 59.6095 | 59.6634 | 59.6645 | 59.6225 | 61.6567 | 61.7401 | 61.5458 | 61.6923 | -2.0472 | -1.9363 | -1.9922 | -1.8813
326.7656 | 121.8155 | -61.7706 | 59.7153 | 0.13101 | 0.000689 | -0.007421 | -0.029595 | -0.000359 | 0.099318 | -0.12681 | 59.5638 | 59.6176 | 59.6233 | 59.5722 | 61.6109 | 61.6806 | 61.4955 | 61.6511 | 0.18136 | 0.051043 | 0.042933 | 0.020759 | 0.049995 | 0.14967 | -0.076458 | 59.6141 | 59.6679 | 59.6737 | 59.6225 | 61.6613 | 61.731 | 61.5458 | 61.7014 | -2.0472 | -1.9317 | -1.9876 | -1.8722
328.4531 | 121.6736 | -61.821 | 59.6832 | 0.12185 | 0.014425 | -0.007421 | -0.034174 | 0.004219 | 0.1039 | -0.12681 | 59.5592 | 59.613 | 59.6187 | 59.5767 | 61.6109 | 61.6806 | 61.4909 | 61.6419 | 0.1722 | 0.064779 | 0.042933 | 0.01618 | 0.054573 | 0.15425 | -0.076458 | 59.6095 | 59.6634 | 59.6691 | 59.6271 | 61.6613 | 61.731 | 61.5412 | 61.6923 | -2.0517 | -1.9317 | -1.9922 | -1.8722
330.2188 | 121.6644 | -61.8301 | 59.6878 | 0.13101 | 0.009846 | -0.007421 | -0.029595 | 0.008797 | 0.099318 | -0.12223 | 59.5592 | 59.6084 | 59.6187 | 59.5722 | 61.6109 | 61.6852 | 61.4909 | 61.6511 | 0.18136 | 0.0602 | 0.042933 | 0.020759 | 0.059151 | 0.14967 | -0.07188 | 59.6095 | 59.6588 | 59.6691 | 59.6225 | 61.6613 | 61.7355 | 61.5412 | 61.7014 | -2.0517 | -1.9317 | -1.9922 | -1.8722
331.9844 | 121.7377 | -61.7569 | 59.7656 | 0.13101 | 0.005267 | -0.002842 | -0.025017 | 0.004219 | 0.1039 | -0.12681 | 59.5592 | 59.613 | 59.6187 | 59.5722 | 61.6109 | 61.6852 | 61.4863 | 61.6465 | 0.18136 | 0.055621 | 0.047512 | 0.025337 | 0.054573 | 0.15425 | -0.076458 | 59.6095 | 59.6634 | 59.6691 | 59.6225 | 61.6613 | 61.7355 | 61.5367 | 61.6969 | -2.0517 | -1.9271 | -1.9922 | -1.8676
333.6719 | 121.6919 | -61.702 | 59.8297 | 0.12643 | 0.009846 | -0.002842 | -0.029595 | -0.004937 | 0.099318 | -0.11765 | 59.5546 | 59.6176 | 59.6187 | 59.5767 | 61.6064 | 61.6806 | 61.4955 | 61.6511 | 0.17678 | 0.0602 | 0.047512 | 0.020759 | 0.045417 | 0.14967 | -0.067301 | 59.605 | 59.6679 | 59.6691 | 59.6271 | 61.6567 | 61.731 | 61.5458 | 61.7014 | -2.0517 | -1.9409 | -1.9876 | -1.8767
335.4219 | 121.7148 | -61.8027 | 59.729 | 0.13101 | 0.005267 | -0.012 | -0.029595 | 0.008797 | 0.1039 | -0.11765 | 59.55 | 59.6176 | 59.6233 | 59.5722 | 61.6018 | 61.6806 | 61.4955 | 61.6465 | 0.18136 | 0.055621 | 0.038354 | 0.020759 | 0.059151 | 0.15425 | -0.067301 | 59.6004 | 59.6679 | 59.6737 | 59.6225 | 61.6521 | 61.731 | 61.5458 | 61.6969 | -2.0517 | -1.9454 | -1.9785 | -1.8722
337.125 | 121.6782 | -61.8118 | 59.7153 | 0.13101 | -0.00389 | -0.012 | -0.029595 | 0.004219 | 0.1039 | -0.11308 | 59.5592 | 59.613 | 59.6187 | 59.5722 | 61.6109 | 61.6806 | 61.4955 | 61.6511 | 0.18136 | 0.046464 | 0.038354 | 0.020759 | 0.054573 | 0.15425 | -0.062723 | 59.6095 | 59.6634 | 59.6691 | 59.6225 | 61.6613 | 61.731 | 61.5458 | 61.7014 | -2.0517 | -1.9363 | -1.9922 | -1.8767
338.8594 | 121.7834 | -61.7111 | 59.7427 | 0.12643 | 0.000689 | -0.016578 | -0.034174 | -0.004937 | 0.099318 | -0.13139 | 59.5592 | 59.6176 | 59.6187 | 59.5722 | 61.6064 | 61.6806 | 61.4909 | 61.6511 | 0.17678 | 0.051043 | 0.033776 | 0.01618 | 0.045417 | 0.14967 | -0.081036 | 59.6095 | 59.6679 | 59.6691 | 59.6225 | 61.6567 | 61.731 | 61.5412 | 61.7014 | -2.0472 | -1.9317 | -1.9876 | -1.8722
340.5938 | 121.7651 | -61.7752 | 59.6832 | 0.13101 | -0.00389 | -0.007421 | -0.034174 | 0.004219 | 0.1039 | -0.12681 | 59.5638 | 59.613 | 59.6142 | 59.5676 | 61.6109 | 61.676 | 61.4863 | 61.6465 | 0.18136 | 0.046464 | 0.042933 | 0.01618 | 0.054573 | 0.15425 | -0.076458 | 59.6141 | 59.6634 | 59.6645 | 59.6179 | 61.6613 | 61.7264 | 61.5367 | 61.6969 | -2.0472 | -1.9225 | -1.9968 | -1.8722
342.3438 | 121.7697 | -61.6928 | 59.7748 | 0.13101 | -0.00389 | -0.002842 | -0.038752 | -0.000359 | 0.090161 | -0.13139 | 59.5546 | 59.6176 | 59.6233 | 59.5722 | 61.6201 | 61.6898 | 61.4955 | 61.6511 | 0.18136 | 0.046464 | 0.047512 | 0.011602 | 0.049995 | 0.14052 | -0.081036 | 59.605 | 59.6679 | 59.6737 | 59.6225 | 61.6704 | 61.7401 | 61.5458 | 61.7014 | -2.0655 | -1.9409 | -1.9968 | -1.8722
344.0781 | 121.7651 | -61.7157 | 59.761 | 0.13101 | 0.005267 | -0.021157 | -0.034174 | -0.000359 | 0.09474 | -0.13139 | 59.5546 | 59.6222 | 59.6187 | 59.5722 | 61.6155 | 61.6852 | 61.4955 | 61.6511 | 0.18136 | 0.055621 | 0.029197 | 0.01618 | 0.049995 | 0.14509 | -0.081036 | 59.605 | 59.6725 | 59.6691 | 59.6225 | 61.6659 | 61.7355 | 61.5458 | 61.7014 | -2.0609 | -1.9409 | -1.9968 | -1.8767
345.8281 | 121.8246 | -61.6516 | 59.7794 | 0.12643 | -0.00389 | -0.007421 | -0.034174 | -0.000359 | 0.090161 | -0.13139 | 59.5592 | 59.613 | 59.6142 | 59.5813 | 61.6155 | 61.676 | 61.4909 | 61.6465 | 0.17678 | 0.046464 | 0.042933 | 0.01618 | 0.049995 | 0.14052 | -0.081036 | 59.6095 | 59.6634 | 59.6645 | 59.6317 | 61.6659 | 61.7264 | 61.5412 | 61.6969 | -2.0563 | -1.9317 | -2.0014 | -1.8767
347.5312 | 121.7377 | -61.7065 | 59.7473 | 0.13559 | 0.000689 | -0.016578 | -0.029595 | -0.000359 | 0.1039 | -0.12681 | 59.5638 | 59.6084 | 59.6187 | 59.5767 | 61.6155 | 61.6852 | 61.4909 | 61.6419 | 0.18594 | 0.051043 | 0.033776 | 0.020759 | 0.049995 | 0.15425 | -0.076458 | 59.6141 | 59.6588 | 59.6691 | 59.6271 | 61.6659 | 61.7355 | 61.5412 | 61.6923 | -2.0517 | -1.9271 | -1.9968 | -1.8722
349.2656 | 121.8109 | -61.6333 | 59.8114 | 0.13559 | 0.000689 | -0.007421 | -0.034174 | -0.004937 | 0.09474 | -0.12681 | 59.5455 | 59.6084 | 59.6279 | 59.5676 | 61.6109 | 61.6806 | 61.4955 | 61.6557 | 0.18594 | 0.051043 | 0.042933 | 0.01618 | 0.045417 | 0.14509 | -0.076458 | 59.5958 | 59.6588 | 59.6782 | 59.6179 | 61.6613 | 61.731 | 61.5458 | 61.706 | -2.0655 | -1.95 | -1.983 | -1.8676
351.0156 | 121.7377 | -61.7615 | 59.761 | 0.13559 | 0.000689 | -0.007421 | -0.029595 | -0.000359 | 0.099318 | -0.12681 | 59.5546 | 59.6176 | 59.6142 | 59.5767 | 61.6109 | 61.6806 | 61.4863 | 61.6419 | 0.18594 | 0.051043 | 0.042933 | 0.020759 | 0.049995 | 0.14967 | -0.076458 | 59.605 | 59.6679 | 59.6645 | 59.6271 | 61.6613 | 61.731 | 61.5367 | 61.6923 | -2.0563 | -1.9317 | -1.9968 | -1.8722
352.7188 | 121.7377 | -61.7981 | 59.6878 | 0.13559 | 0.005267 | -0.016578 | -0.025017 | 0.008797 | 0.1039 | -0.12681 | 59.5546 | 59.613 | 59.6279 | 59.5676 | 61.6109 | 61.6806 | 61.4909 | 61.6465 | 0.18594 | 0.055621 | 0.033776 | 0.025337 | 0.059151 | 0.15425 | -0.076458 | 59.605 | 59.6634 | 59.6782 | 59.6179 | 61.6613 | 61.731 | 61.5412 | 61.6969 | -2.0563 | -1.9363 | -1.983 | -1.863
354.4688 | 121.6965 | -61.8256 | 59.7107 | 0.13559 | 0.005267 | -0.002842 | -0.029595 | -0.000359 | 0.099318 | -0.12681 | 59.5546 | 59.613 | 59.6187 | 59.5676 | 61.6109 | 61.6806 | 61.4909 | 61.6465 | 0.18594 | 0.055621 | 0.047512 | 0.020759 | 0.049995 | 0.14967 | -0.076458 | 59.605 | 59.6634 | 59.6691 | 59.6179 | 61.6613 | 61.731 | 61.5412 | 61.6969 | -2.0563 | -1.9363 | -1.9922 | -1.8722
356.2188 | 121.8018 | -61.6013 | 59.8068 | 0.12185 | 0.000689 | -0.016578 | -0.038752 | 0.004219 | 0.099318 | -0.11765 | 59.55 | 59.6176 | 59.6096 | 59.5767 | 61.6201 | 61.6898 | 61.4955 | 61.6511 | 0.1722 | 0.051043 | 0.033776 | 0.011602 | 0.054573 | 0.14967 | -0.067301 | 59.6004 | 59.6679 | 59.6599 | 59.6271 | 61.6704 | 61.7401 | 61.5458 | 61.7014 | -2.0701 | -1.9454 | -2.0105 | -1.8859
357.9062 | 121.7468 | -61.6928 | 59.7473 | 0.12643 | 0.005267 | -0.016578 | -0.034174 | -0.000359 | 0.09474 | -0.13139 | 59.5546 | 59.613 | 59.6187 | 59.5722 | 61.6155 | 61.6852 | 61.5 | 61.6511 | 0.17678 | 0.055621 | 0.033776 | 0.01618 | 0.049995 | 0.14509 | -0.081036 | 59.605 | 59.6634 | 59.6691 | 59.6225 | 61.6659 | 61.7355 | 61.5504 | 61.7014 | -2.0609 | -1.9454 | -1.9968 | -1.8813
359.6562 | 121.843 | -61.6425 | 59.8114 | 0.12185 | 0.000689 | -0.016578 | -0.034174 | 0.008797 | 0.09474 | -0.13597 | 59.5546 | 59.6084 | 59.6142 | 59.5676 | 61.6109 | 61.6806 | 61.4955 | 61.6465 | 0.1722 | 0.051043 | 0.033776 | 0.01618 | 0.059151 | 0.14509 | -0.085614 | 59.605 | 59.6588 | 59.6645 | 59.6179 | 61.6613 | 61.731 | 61.5458 | 61.6969 | -2.0563 | -1.9409 | -1.9968 | -1.8813
361.3438 | 121.7148 | -61.702 | 59.7977 | 0.12185 | 0.005267 | -0.002842 | -0.025017 | 0.008797 | 0.09474 | -0.12681 | 59.5546 | 59.6176 | 59.6096 | 59.5722 | 61.6064 | 61.6852 | 61.4909 | 61.6511 | 0.1722 | 0.055621 | 0.047512 | 0.025337 | 0.059151 | 0.14509 | -0.076458 | 59.605 | 59.6679 | 59.6599 | 59.6225 | 61.6567 | 61.7355 | 61.5412 | 61.7014 | -2.0517 | -1.9363 | -1.9968 | -1.8813
363.0938 | 121.669 | -61.6745 | 59.8526 | 0.12643 | 0.000689 | -0.002842 | -0.034174 | -0.004937 | 0.09474 | -0.12223 | 59.5592 | 59.6084 | 59.6142 | 59.5676 | 61.6018 | 61.6806 | 61.4863 | 61.6465 | 0.17678 | 0.051043 | 0.047512 | 0.01618 | 0.045417 | 0.14509 | -0.07188 | 59.6095 | 59.6588 | 59.6645 | 59.6179 | 61.6521 | 61.731 | 61.5367 | 61.6969 | -2.0426 | -1.9271 | -1.9876 | -1.8722
364.7812 | 121.7926 | -61.6699 | 59.7794 | 0.12643 | -0.008469 | -0.016578 | -0.034174 | -0.000359 | 0.099318 | -0.13139 | 59.5592 | 59.6084 | 59.6142 | 59.5722 | 61.6109 | 61.676 | 61.5 | 61.6374 | 0.17678 | 0.041885 | 0.033776 | 0.01618 | 0.049995 | 0.14967 | -0.081036 | 59.6095 | 59.6588 | 59.6645 | 59.6225 | 61.6613 | 61.7264 | 61.5504 | 61.6877 | -2.0517 | -1.9409 | -1.9968 | -1.8859
366.5156 | 121.8155 | -61.6516 | 59.8114 | 0.13101 | 0.005267 | -0.012 | -0.034174 | 0.004219 | 0.09474 | -0.13139 | 59.5592 | 59.613 | 59.6142 | 59.563 | 61.6109 | 61.6852 | 61.4909 | 61.6465 | 0.18136 | 0.055621 | 0.038354 | 0.01618 | 0.054573 | 0.14509 | -0.081036 | 59.6095 | 59.6634 | 59.6645 | 59.6134 | 61.6613 | 61.7355 | 61.5412 | 61.6969 | -2.0517 | -1.9317 | -1.9968 | -1.8767
368.2031 | 121.6736 | -61.6882 | 59.8572 | 0.12643 | 0.005267 | -0.007421 | -0.034174 | -0.000359 | 0.09474 | -0.12681 | 59.5592 | 59.613 | 59.6187 | 59.5676 | 61.6109 | 61.6852 | 61.4863 | 61.6465 | 0.17678 | 0.055621 | 0.042933 | 0.01618 | 0.049995 | 0.14509 | -0.076458 | 59.6095 | 59.6634 | 59.6691 | 59.6179 | 61.6613 | 61.7355 | 61.5367 | 61.6969 | -2.0517 | -1.9271 | -1.9922 | -1.8676
369.9375 | 121.8063 | -61.6241 | 59.8251 | 0.13559 | -0.008469 | -0.012 | -0.034174 | 0.004219 | 0.090161 | -0.12223 | 59.5592 | 59.6038 | 59.6142 | 59.5722 | 61.6064 | 61.6806 | 61.4955 | 61.6419 | 0.18594 | 0.041885 | 0.038354 | 0.01618 | 0.054573 | 0.14052 | -0.07188 | 59.6095 | 59.6542 | 59.6645 | 59.6225 | 61.6567 | 61.731 | 61.5458 | 61.6923 | -2.0472 | -1.9363 | -1.9922 | -1.8813
371.6719 | 121.8018 | -61.6241 | 59.8068 | 0.12185 | -0.00389 | -0.016578 | -0.029595 | 0.004219 | 0.09474 | -0.12681 | 59.5638 | 59.6176 | 59.6187 | 59.5676 | 61.6155 | 61.6852 | 61.4909 | 61.6419 | 0.1722 | 0.046464 | 0.033776 | 0.020759 | 0.054573 | 0.14509 | -0.076458 | 59.6141 | 59.6679 | 59.6691 | 59.6179 | 61.6659 | 61.7355 | 61.5412 | 61.6923 | -2.0517 | -1.9271 | -1.9968 | -1.8722
373.3594 | 121.7972 | -61.6287 | 59.816 | 0.12185 | 0.000689 | -0.012 | -0.034174 | -0.000359 | 0.09474 | -0.12223 | 59.5546 | 59.6176 | 59.6187 | 59.5722 | 61.6109 | 61.6852 | 61.4909 | 61.6374 | 0.1722 | 0.051043 | 0.038354 | 0.01618 | 0.049995 | 0.14509 | -0.07188 | 59.605 | 59.6679 | 59.6691 | 59.6225 | 61.6613 | 61.7355 | 61.5412 | 61.6877 | -2.0563 | -1.9363 | -1.9922 | -1.8722
375.1094 | 121.8338 | -61.615 | 59.7977 | 0.13101 | -0.00389 | -0.012 | -0.034174 | -0.000359 | 0.090161 | -0.12223 | 59.5592 | 59.613 | 59.6142 | 59.5722 | 61.6109 | 61.6806 | 61.4955 | 61.6465 | 0.18136 | 0.046464 | 0.038354 | 0.01618 | 0.049995 | 0.14052 | -0.07188 | 59.6095 | 59.6634 | 59.6645 | 59.6225 | 61.6613 | 61.731 | 61.5458 | 61.6969 | -2.0517 | -1.9363 | -1.9968 | -1.8813
376.7969 | 121.701 | -61.7111 | 59.8206 | 0.13101 | 0.000689 | -0.012 | -0.029595 | 0.004219 | 0.099318 | -0.12681 | 59.55 | 59.613 | 59.6142 | 59.5767 | 61.6109 | 61.6806 | 61.4863 | 61.6374 | 0.18136 | 0.051043 | 0.038354 | 0.020759 | 0.054573 | 0.14967 | -0.076458 | 59.6004 | 59.6634 | 59.6645 | 59.6271 | 61.6613 | 61.731 | 61.5367 | 61.6877 | -2.0609 | -1.9363 | -1.9968 | -1.8722
378.5469 | 121.7697 | -61.7523 | 59.7015 | 0.13101 | -0.008469 | -0.012 | -0.029595 | 0.008797 | 0.10848 | -0.13139 | 59.5592 | 59.613 | 59.6187 | 59.5676 | 61.6018 | 61.6806 | 61.4909 | 61.6374 | 0.18136 | 0.041885 | 0.038354 | 0.020759 | 0.059151 | 0.15883 | -0.081036 | 59.6095 | 59.6634 | 59.6691 | 59.6179 | 61.6521 | 61.731 | 61.5412 | 61.6877 | -2.0426 | -1.9317 | -1.983 | -1.8722
380.2812 | 121.7606 | -61.6974 | 59.7702 | 0.13101 | -0.013048 | -0.012 | -0.029595 | 0.004219 | 0.099318 | -0.12223 | 59.5592 | 59.613 | 59.6142 | 59.5676 | 61.6155 | 61.6806 | 61.4863 | 61.6557 | 0.18136 | 0.037306 | 0.038354 | 0.020759 | 0.054573 | 0.14967 | -0.07188 | 59.6095 | 59.6634 | 59.6645 | 59.6179 | 61.6659 | 61.731 | 61.5367 | 61.706 | -2.0563 | -1.9271 | -2.0014 | -1.8722
382.0156 | 121.7926 | -61.6333 | 59.8297 | 0.12185 | 0.000689 | -0.012 | -0.029595 | -0.000359 | 0.099318 | -0.12681 | 59.5638 | 59.613 | 59.6233 | 59.5767 | 61.6064 | 61.6852 | 61.4909 | 61.6465 | 0.1722 | 0.051043 | 0.038354 | 0.020759 | 0.049995 | 0.14967 | -0.076458 | 59.6141 | 59.6634 | 59.6737 | 59.6271 | 61.6567 | 61.7355 | 61.5412 | 61.6969 | -2.0426 | -1.9271 | -1.983 | -1.8676
383.7031 | 121.6461 | -61.7889 | 59.729 | 0.12643 | -0.00389 | -0.007421 | -0.025017 | 0.008797 | 0.1039 | -0.11765 | 59.5592 | 59.6176 | 59.6187 | 59.5722 | 61.6064 | 61.676 | 61.4955 | 61.6419 | 0.17678 | 0.046464 | 0.042933 | 0.025337 | 0.059151 | 0.15425 | -0.067301 | 59.6095 | 59.6679 | 59.6691 | 59.6225 | 61.6567 | 61.7264 | 61.5458 | 61.6923 | -2.0472 | -1.9363 | -1.9876 | -1.8767
385.4688 | 121.701 | -61.7065 | 59.8297 | 0.13101 | -0.00389 | -0.007421 | -0.029595 | 0.004219 | 0.099318 | -0.12681 | 59.5638 | 59.6084 | 59.6187 | 59.5722 | 61.6064 | 61.6806 | 61.4863 | 61.6419 | 0.18136 | 0.046464 | 0.042933 | 0.020759 | 0.054573 | 0.14967 | -0.076458 | 59.6141 | 59.6588 | 59.6691 | 59.6225 | 61.6567 | 61.731 | 61.5367 | 61.6923 | -2.0426 | -1.9225 | -1.9876 | -1.8676
387.1562 | 121.7651 | -61.6791 | 59.761 | 0.12185 | -0.008469 | -0.012 | -0.034174 | -0.000359 | 0.09474 | -0.12681 | 59.5546 | 59.6084 | 59.6142 | 59.5722 | 61.6155 | 61.6898 | 61.4817 | 61.6419 | 0.1722 | 0.041885 | 0.038354 | 0.01618 | 0.049995 | 0.14509 | -0.076458 | 59.605 | 59.6588 | 59.6645 | 59.6225 | 61.6659 | 61.7401 | 61.5321 | 61.6923 | -2.0609 | -1.9271 | -2.0014 | -1.8676
388.9062 | 121.6827 | -61.6837 | 59.8206 | 0.13559 | -0.008469 | -0.007421 | -0.029595 | -0.000359 | 0.1039 | -0.13139 | 59.5638 | 59.6084 | 59.6187 | 59.5676 | 61.6109 | 61.676 | 61.4863 | 61.6419 | 0.18594 | 0.041885 | 0.042933 | 0.020759 | 0.049995 | 0.15425 | -0.081036 | 59.6141 | 59.6588 | 59.6691 | 59.6179 | 61.6613 | 61.7264 | 61.5367 | 61.6923 | -2.0472 | -1.9225 | -1.9922 | -1.8676
390.6406 | 121.6507 | -61.7935 | 59.6924 | 0.13101 | 0.005267 | -0.012 | -0.034174 | 0.004219 | 0.11305 | -0.12223 | 59.5546 | 59.6084 | 59.6142 | 59.5676 | 61.6109 | 61.6806 | 61.4863 | 61.6465 | 0.18136 | 0.055621 | 0.038354 | 0.01618 | 0.054573 | 0.16341 | -0.07188 | 59.605 | 59.6588 | 59.6645 | 59.6179 | 61.6613 | 61.731 | 61.5367 | 61.6969 | -2.0563 | -1.9317 | -1.9968 | -1.8722
392.3281 | 121.7102 | -61.6562 | 59.8297 | 0.12185 | 0.000689 | -0.012 | -0.034174 | -0.000359 | 0.090161 | -0.12223 | 59.5546 | 59.6084 | 59.6187 | 59.5676 | 61.6064 | 61.6806 | 61.4909 | 61.6374 | 0.1722 | 0.051043 | 0.038354 | 0.01618 | 0.049995 | 0.14052 | -0.07188 | 59.605 | 59.6588 | 59.6691 | 59.6179 | 61.6567 | 61.731 | 61.5412 | 61.6877 | -2.0517 | -1.9363 | -1.9876 | -1.8722
394.0781 | 121.669 | -61.8118 | 59.697 | 0.13101 | -0.00389 | -0.007421 | -0.029595 | 0.013375 | 0.09474 | -0.12223 | 59.5638 | 59.6222 | 59.6187 | 59.5676 | 61.6109 | 61.6806 | 61.4863 | 61.6419 | 0.18136 | 0.046464 | 0.042933 | 0.020759 | 0.063729 | 0.14509 | -0.07188 | 59.6141 | 59.6725 | 59.6691 | 59.6179 | 61.6613 | 61.731 | 61.5367 | 61.6923 | -2.0472 | -1.9225 | -1.9922 | -1.8676
395.8125 | 121.7468 | -61.7111 | 59.7244 | 0.12643 | -0.008469 | -0.012 | -0.038752 | 0.013375 | 0.099318 | -0.12681 | 59.5546 | 59.613 | 59.6096 | 59.5722 | 61.6064 | 61.6852 | 61.4955 | 61.6465 | 0.17678 | 0.041885 | 0.038354 | 0.011602 | 0.063729 | 0.14967 | -0.076458 | 59.605 | 59.6634 | 59.6599 | 59.6225 | 61.6567 | 61.7355 | 61.5458 | 61.6969 | -2.0517 | -1.9409 | -1.9968 | -1.8859
397.5625 | 121.6965 | -61.702 | 59.8022 | 0.13101 | 0.000689 | -0.012 | -0.034174 | 0.004219 | 0.1039 | -0.12223 | 59.5592 | 59.6084 | 59.6142 | 59.5676 | 61.6109 | 61.6806 | 61.4909 | 61.6419 | 0.18136 | 0.051043 | 0.038354 | 0.01618 | 0.054573 | 0.15425 | -0.07188 | 59.6095 | 59.6588 | 59.6645 | 59.6179 | 61.6613 | 61.731 | 61.5412 | 61.6923 | -2.0517 | -1.9317 | -1.9968 | -1.8767
399.2656 | 121.8063 | -61.6287 | 59.7885 | 0.12643 | -0.008469 | -0.007421 | -0.029595 | 0.004219 | 0.09474 | -0.13139 | 59.55 | 59.613 | 59.6187 | 59.5676 | 61.6064 | 61.6943 | 61.4863 | 61.6511 | 0.17678 | 0.041885 | 0.042933 | 0.020759 | 0.054573 | 0.14509 | -0.081036 | 59.6004 | 59.6634 | 59.6691 | 59.6179 | 61.6567 | 61.7447 | 61.5367 | 61.7014 | -2.0563 | -1.9363 | -1.9876 | -1.8676
401.0156 | 121.7422 | -61.7569 | 59.697 | 0.12643 | -0.008469 | -0.007421 | -0.029595 | 0.008797 | 0.1039 | -0.12681 | 59.5638 | 59.6084 | 59.6187 | 59.5722 | 61.6064 | 61.6852 | 61.4863 | 61.6374 | 0.17678 | 0.041885 | 0.042933 | 0.020759 | 0.059151 | 0.15425 | -0.076458 | 59.6141 | 59.6588 | 59.6691 | 59.6225 | 61.6567 | 61.7355 | 61.5367 | 61.6877 | -2.0426 | -1.9225 | -1.9876 | -1.8676
402.6875 | 121.6965 | -61.8073 | 59.7244 | 0.13101 | 0.005267 | -0.002842 | -0.034174 | 0.004219 | 0.1039 | -0.12223 | 59.5592 | 59.613 | 59.6142 | 59.5676 | 61.6109 | 61.6806 | 61.4909 | 61.6374 | 0.18136 | 0.055621 | 0.047512 | 0.01618 | 0.054573 | 0.15425 | -0.07188 | 59.6095 | 59.6634 | 59.6645 | 59.6179 | 61.6613 | 61.731 | 61.5412 | 61.6877 | -2.0517 | -1.9317 | -1.9968 | -1.8767
404.4375 | 121.7972 | -61.7523 | 59.6603 | 0.13101 | -0.008469 | -0.016578 | -0.025017 | 0.004219 | 0.090161 | -0.13139 | 59.5592 | 59.613 | 59.6187 | 59.5767 | 61.6018 | 61.6806 | 61.4909 | 61.6374 | 0.18136 | 0.041885 | 0.033776 | 0.025337 | 0.054573 | 0.14052 | -0.081036 | 59.6095 | 59.6634 | 59.6691 | 59.6271 | 61.6521 | 61.731 | 61.5412 | 61.6877 | -2.0426 | -1.9317 | -1.983 | -1.8722
406.1875 | 121.8018 | -61.7386 | 59.7153 | 0.13101 | -0.008469 | -0.007421 | -0.029595 | 0.004219 | 0.1039 | -0.12681 | 59.55 | 59.6176 | 59.6187 | 59.5676 | 61.6064 | 61.6806 | 61.4909 | 61.6419 | 0.18136 | 0.041885 | 0.042933 | 0.020759 | 0.054573 | 0.15425 | -0.076458 | 59.6004 | 59.6679 | 59.6691 | 59.6179 | 61.6567 | 61.731 | 61.5412 | 61.6923 | -2.0563 | -1.9409 | -1.9876 | -1.8722
407.8906 | 121.6599 | -61.8118 | 59.7427 | 0.12643 | -0.008469 | -0.012 | -0.025017 | 0.004219 | 0.099318 | -0.11765 | 59.5638 | 59.613 | 59.6142 | 59.5722 | 61.6109 | 61.676 | 61.4909 | 61.6419 | 0.17678 | 0.041885 | 0.038354 | 0.025337 | 0.054573 | 0.14967 | -0.067301 | 59.6141 | 59.6634 | 59.6645 | 59.6225 | 61.6613 | 61.7264 | 61.5412 | 61.6923 | -2.0472 | -1.9271 | -1.9968 | -1.8767
409.625 | 121.6553 | -61.8027 | 59.7107 | 0.13101 | 0.000689 | -0.002842 | -0.025017 | 0.013375 | 0.1039 | -0.11308 | 59.5638 | 59.6038 | 59.6187 | 59.5676 | 61.6018 | 61.6852 | 61.4817 | 61.6328 | 0.18136 | 0.051043 | 0.047512 | 0.025337 | 0.063729 | 0.15425 | -0.062723 | 59.6141 | 59.6542 | 59.6691 | 59.6179 | 61.6521 | 61.7355 | 61.5321 | 61.6831 | -2.038 | -1.918 | -1.983 | -1.863
411.3125 | 121.8201 | -61.6379 | 59.8251 | 0.12185 | -0.00389 | -0.012 | -0.034174 | 0.004219 | 0.099318 | -0.12681 | 59.5638 | 59.6084 | 59.6187 | 59.5722 | 61.5926 | 61.6806 | 61.4909 | 61.6374 | 0.1722 | 0.046464 | 0.038354 | 0.01618 | 0.054573 | 0.14967 | -0.076458 | 59.6141 | 59.6588 | 59.6691 | 59.6225 | 61.643 | 61.731 | 61.5412 | 61.6877 | -2.0288 | -1.9271 | -1.9739 | -1.8722
413.0625 | 121.7972 | -61.7294 | 59.7107 | 0.12643 | -0.008469 | -0.002842 | -0.025017 | 0.004219 | 0.099318 | -0.12681 | 59.5592 | 59.613 | 59.6096 | 59.563 | 61.6064 | 61.6806 | 61.4955 | 61.6511 | 0.17678 | 0.041885 | 0.047512 | 0.025337 | 0.054573 | 0.14967 | -0.076458 | 59.6095 | 59.6634 | 59.6599 | 59.6134 | 61.6567 | 61.731 | 61.5458 | 61.7014 | -2.0472 | -1.9363 | -1.9968 | -1.8859
414.8125 | 121.6827 | -61.8347 | 59.7198 | 0.13559 | -0.00389 | -0.012 | -0.025017 | -0.000359 | 0.099318 | -0.12223 | 59.5638 | 59.613 | 59.6096 | 59.5722 | 61.6109 | 61.6806 | 61.4909 | 61.6374 | 0.18594 | 0.046464 | 0.038354 | 0.025337 | 0.049995 | 0.14967 | -0.07188 | 59.6141 | 59.6634 | 59.6599 | 59.6225 | 61.6613 | 61.731 | 61.5412 | 61.6877 | -2.0472 | -1.9271 | -2.0014 | -1.8813
416.5469 | 121.7468 | -61.6653 | 59.7702 | 0.12185 | -0.00389 | -0.002842 | -0.034174 | -0.000359 | 0.09474 | -0.12681 | 59.5592 | 59.613 | 59.6233 | 59.5676 | 61.6155 | 61.6806 | 61.4909 | 61.6419 | 0.1722 | 0.046464 | 0.047512 | 0.01618 | 0.049995 | 0.14509 | -0.076458 | 59.6095 | 59.6634 | 59.6737 | 59.6179 | 61.6659 | 61.731 | 61.5412 | 61.6923 | -2.0563 | -1.9317 | -1.9922 | -1.8676
418.2344 | 121.8201 | -61.615 | 59.8206 | 0.11727 | -0.00389 | -0.012 | -0.029595 | 0.004219 | 0.1039 | -0.13139 | 59.5592 | 59.613 | 59.6187 | 59.563 | 61.6109 | 61.6898 | 61.4955 | 61.6419 | 0.16763 | 0.046464 | 0.038354 | 0.020759 | 0.054573 | 0.15425 | -0.081036 | 59.6095 | 59.6634 | 59.6691 | 59.6134 | 61.6613 | 61.7401 | 61.5458 | 61.6923 | -2.0517 | -1.9363 | -1.9922 | -1.8767
419.9844 | 121.7102 | -61.7249 | 59.7473 | 0.13101 | -0.008469 | -0.002842 | -0.029595 | 0.004219 | 0.1039 | -0.12681 | 59.5592 | 59.613 | 59.6187 | 59.5676 | 61.6064 | 61.676 | 61.4817 | 61.6511 | 0.18136 | 0.041885 | 0.047512 | 0.020759 | 0.054573 | 0.15425 | -0.076458 | 59.6095 | 59.6634 | 59.6691 | 59.6179 | 61.6567 | 61.7264 | 61.5321 | 61.7014 | -2.0472 | -1.9225 | -1.9876 | -1.863
421.7344 | 121.6553 | -61.8256 | 59.7336 | 0.13101 | 0.000689 | -0.012 | -0.025017 | 0.004219 | 0.10848 | -0.12681 | 59.5592 | 59.6084 | 59.6187 | 59.5722 | 61.6064 | 61.676 | 61.4863 | 61.6374 | 0.18136 | 0.051043 | 0.038354 | 0.025337 | 0.054573 | 0.15883 | -0.076458 | 59.6095 | 59.6588 | 59.6691 | 59.6225 | 61.6567 | 61.7264 | 61.5367 | 61.6877 | -2.0472 | -1.9271 | -1.9876 | -1.8676
423.4375 | 121.6736 | -61.7706 | 59.729 | 0.13559 | 0.000689 | -0.002842 | -0.020438 | 0.008797 | 0.1039 | -0.11765 | 59.5592 | 59.6084 | 59.6187 | 59.5676 | 61.6064 | 61.6852 | 61.4909 | 61.6419 | 0.18594 | 0.051043 | 0.047512 | 0.029916 | 0.059151 | 0.15425 | -0.067301 | 59.6095 | 59.6588 | 59.6691 | 59.6179 | 61.6567 | 61.7355 | 61.5412 | 61.6923 | -2.0472 | -1.9317 | -1.9876 | -1.8722
425.1875 | 121.8063 | -61.615 | 59.8068 | 0.12643 | -0.008469 | -0.012 | -0.038752 | -0.000359 | 0.09474 | -0.12223 | 59.5592 | 59.6038 | 59.6187 | 59.5676 | 61.6018 | 61.6806 | 61.4863 | 61.6419 | 0.17678 | 0.041885 | 0.038354 | 0.011602 | 0.049995 | 0.14509 | -0.07188 | 59.6095 | 59.6542 | 59.6691 | 59.6179 | 61.6521 | 61.731 | 61.5367 | 61.6923 | -2.0426 | -1.9271 | -1.983 | -1.8676
426.9219 | 121.7285 | -61.7477 | 59.729 | 0.12643 | -0.008469 | -0.021157 | -0.025017 | -0.000359 | 0.1039 | -0.12223 | 59.5638 | 59.613 | 59.6233 | 59.5676 | 61.6064 | 61.676 | 61.4955 | 61.6328 | 0.17678 | 0.041885 | 0.029197 | 0.025337 | 0.049995 | 0.15425 | -0.07188 | 59.6141 | 59.6634 | 59.6737 | 59.6179 | 61.6567 | 61.7264 | 61.5458 | 61.6831 | -2.0426 | -1.9317 | -1.983 | -1.8722
428.6719 | 121.756 | -61.6425 | 59.8251 | 0.12643 | -0.00389 | -0.012 | -0.034174 | 0.004219 | 0.1039 | -0.12681 | 59.5592 | 59.6084 | 59.6187 | 59.5722 | 61.6064 | 61.6806 | 61.4909 | 61.6419 | 0.17678 | 0.046464 | 0.038354 | 0.01618 | 0.054573 | 0.15425 | -0.076458 | 59.6095 | 59.6588 | 59.6691 | 59.6225 | 61.6567 | 61.731 | 61.5412 | 61.6923 | -2.0472 | -1.9317 | -1.9876 | -1.8722
430.4219 | 121.6782 | -61.7706 | 59.7153 | 0.12643 | -0.00389 | -0.007421 | -0.029595 | 0.013375 | 0.10848 | -0.12223 | 59.55 | 59.6038 | 59.6142 | 59.5767 | 61.6064 | 61.6852 | 61.4863 | 61.6465 | 0.17678 | 0.046464 | 0.042933 | 0.020759 | 0.063729 | 0.15883 | -0.07188 | 59.6004 | 59.6542 | 59.6645 | 59.6271 | 61.6567 | 61.7355 | 61.5367 | 61.6969 | -2.0563 | -1.9363 | -1.9922 | -1.8722
432.1094 | 121.8246 | -61.6013 | 59.7885 | 0.12185 | -0.00389 | -0.007421 | -0.025017 | 0.008797 | 0.090161 | -0.12681 | 59.5592 | 59.613 | 59.6142 | 59.563 | 61.6109 | 61.6806 | 61.4955 | 61.6419 | 0.1722 | 0.046464 | 0.042933 | 0.025337 | 0.059151 | 0.14052 | -0.076458 | 59.6095 | 59.6634 | 59.6645 | 59.6134 | 61.6613 | 61.731 | 61.5458 | 61.6923 | -2.0517 | -1.9363 | -1.9968 | -1.8813
433.8594 | 121.6873 | -61.7935 | 59.729 | 0.13101 | 0.000689 | -0.002842 | -0.029595 | 0.004219 | 0.1039 | -0.11765 | 59.5592 | 59.6176 | 59.6233 | 59.5722 | 61.6018 | 61.676 | 61.4772 | 61.6328 | 0.18136 | 0.051043 | 0.047512 | 0.020759 | 0.054573 | 0.15425 | -0.067301 | 59.6095 | 59.6679 | 59.6737 | 59.6225 | 61.6521 | 61.7264 | 61.5275 | 61.6831 | -2.0426 | -1.918 | -1.9785 | -1.8539
435.6094 | 121.7102 | -61.6837 | 59.8251 | 0.13559 | -0.00389 | -0.007421 | -0.025017 | 0.008797 | 0.1039 | -0.12681 | 59.5546 | 59.6084 | 59.6142 | 59.5676 | 61.6064 | 61.6806 | 61.4817 | 61.6374 | 0.18594 | 0.046464 | 0.042933 | 0.025337 | 0.059151 | 0.15425 | -0.076458 | 59.605 | 59.6588 | 59.6645 | 59.6179 | 61.6567 | 61.731 | 61.5321 | 61.6877 | -2.0517 | -1.9271 | -1.9922 | -1.8676
437.2969 | 121.788 | -61.6745 | 59.8068 | 0.12643 | -0.008469 | -0.007421 | -0.029595 | 0.004219 | 0.099318 | -0.12681 | 59.5638 | 59.613 | 59.6096 | 59.563 | 61.6064 | 61.6806 | 61.4909 | 61.6465 | 0.17678 | 0.041885 | 0.042933 | 0.020759 | 0.054573 | 0.14967 | -0.076458 | 59.6141 | 59.6634 | 59.6599 | 59.6134 | 61.6567 | 61.731 | 61.5412 | 61.6969 | -2.0426 | -1.9271 | -1.9968 | -1.8813
439.0469 | 121.6873 | -61.8164 | 59.7015 | 0.12643 | -0.013048 | -0.007421 | -0.034174 | 0.004219 | 0.10848 | -0.12223 | 59.5546 | 59.6084 | 59.6187 | 59.5722 | 61.6064 | 61.6852 | 61.4863 | 61.6419 | 0.17678 | 0.037306 | 0.042933 | 0.01618 | 0.054573 | 0.15883 | -0.07188 | 59.605 | 59.6588 | 59.6691 | 59.6225 | 61.6567 | 61.7355 | 61.5367 | 61.6923 | -2.0517 | -1.9317 | -1.9876 | -1.8676
440.7812 | 121.7606 | -61.6974 | 59.7473 | 0.12643 | -0.008469 | -0.016578 | -0.034174 | 0.004219 | 0.1039 | -0.12681 | 59.5592 | 59.6084 | 59.6142 | 59.5722 | 61.6064 | 61.6852 | 61.5 | 61.6465 | 0.17678 | 0.041885 | 0.033776 | 0.01618 | 0.054573 | 0.15425 | -0.076458 | 59.6095 | 59.6588 | 59.6645 | 59.6225 | 61.6567 | 61.7355 | 61.5504 | 61.6969 | -2.0472 | -1.9409 | -1.9922 | -1.8859
442.4688 | 121.7651 | -61.6653 | 59.7656 | 0.13101 | -0.008469 | -0.002842 | -0.034174 | -0.004937 | 0.09474 | -0.12223 | 59.5592 | 59.6084 | 59.6187 | 59.5676 | 61.6064 | 61.6806 | 61.4863 | 61.6374 | 0.18136 | 0.041885 | 0.047512 | 0.01618 | 0.045417 | 0.14509 | -0.07188 | 59.6095 | 59.6588 | 59.6691 | 59.6179 | 61.6567 | 61.731 | 61.5367 | 61.6877 | -2.0472 | -1.9271 | -1.9876 | -1.8676
444.2188 | 121.8018 | -61.6745 | 59.7931 | 0.12643 | -0.008469 | -0.012 | -0.034174 | 0.004219 | 0.09474 | -0.12681 | 59.5546 | 59.6176 | 59.6233 | 59.5722 | 61.6064 | 61.6806 | 61.4863 | 61.6465 | 0.17678 | 0.041885 | 0.038354 | 0.01618 | 0.054573 | 0.14509 | -0.076458 | 59.605 | 59.6679 | 59.6737 | 59.6225 | 61.6567 | 61.731 | 61.5367 | 61.6969 | -2.0517 | -1.9317 | -1.983 | -1.863
445.9062 | 121.7239 | -61.7157 | 59.7794 | 0.13101 | -0.00389 | -0.012 | -0.029595 | 0.004219 | 0.1039 | -0.12223 | 59.5592 | 59.6084 | 59.6187 | 59.563 | 61.6064 | 61.6852 | 61.4817 | 61.6374 | 0.18136 | 0.046464 | 0.038354 | 0.020759 | 0.054573 | 0.15425 | -0.07188 | 59.6095 | 59.6588 | 59.6691 | 59.6134 | 61.6567 | 61.7355 | 61.5321 | 61.6877 | -2.0472 | -1.9225 | -1.9876 | -1.863
447.6406 | 121.701 | -61.6837 | 59.8297 | 0.13101 | -0.00389 | -0.016578 | -0.025017 | 0.004219 | 0.1039 | -0.12223 | 59.5592 | 59.6038 | 59.6279 | 59.5722 | 61.6155 | 61.6806 | 61.4817 | 61.6419 | 0.18136 | 0.046464 | 0.033776 | 0.025337 | 0.054573 | 0.15425 | -0.07188 | 59.6095 | 59.6542 | 59.6782 | 59.6225 | 61.6659 | 61.731 | 61.5321 | 61.6923 | -2.0563 | -1.9225 | -1.9876 | -1.8539
449.3281 | 121.8246 | -61.6379 | 59.7931 | 0.13101 | -0.00389 | -0.016578 | -0.029595 | 0.004219 | 0.09474 | -0.12223 | 59.5592 | 59.5993 | 59.6233 | 59.5676 | 61.6064 | 61.6806 | 61.4863 | 61.6465 | 0.18136 | 0.046464 | 0.033776 | 0.020759 | 0.054573 | 0.14509 | -0.07188 | 59.6095 | 59.6496 | 59.6737 | 59.6179 | 61.6567 | 61.731 | 61.5367 | 61.6969 | -2.0472 | -1.9271 | -1.983 | -1.863
451.0781 | 121.7194 | -61.7477 | 59.7519 | 0.13101 | 0.000689 | -0.012 | -0.020438 | 0.004219 | 0.10848 | -0.12223 | 59.5546 | 59.6038 | 59.6187 | 59.5676 | 61.6109 | 61.6715 | 61.4817 | 61.6465 | 0.18136 | 0.051043 | 0.038354 | 0.029916 | 0.054573 | 0.15883 | -0.07188 | 59.605 | 59.6542 | 59.6691 | 59.6179 | 61.6613 | 61.7218 | 61.5321 | 61.6969 | -2.0563 | -1.9271 | -1.9922 | -1.863
452.8125 | 121.7697 | -61.7203 | 59.7015 | 0.13101 | -0.013048 | -0.002842 | -0.034174 | 0.004219 | 0.099318 | -0.12223 | 59.5592 | 59.6176 | 59.6187 | 59.563 | 61.6064 | 61.6806 | 61.4863 | 61.6419 | 0.18136 | 0.037306 | 0.047512 | 0.01618 | 0.054573 | 0.14967 | -0.07188 | 59.6095 | 59.6679 | 59.6691 | 59.6134 | 61.6567 | 61.731 | 61.5367 | 61.6923 | -2.0472 | -1.9271 | -1.9876 | -1.8676
454.5625 | 121.7194 | -61.7523 | 59.7336 | 0.12643 | 0.000689 | -0.007421 | -0.025017 | 0.004219 | 0.09474 | -0.13139 | 59.5546 | 59.6176 | 59.6187 | 59.563 | 61.6109 | 61.676 | 61.4863 | 61.6419 | 0.17678 | 0.051043 | 0.042933 | 0.025337 | 0.054573 | 0.14509 | -0.081036 | 59.605 | 59.6679 | 59.6691 | 59.6134 | 61.6613 | 61.7264 | 61.5367 | 61.6923 | -2.0563 | -1.9317 | -1.9922 | -1.8676
456.2344 | 121.7514 | -61.6699 | 59.7748 | 0.12185 | -0.013048 | -0.007421 | -0.034174 | -0.000359 | 0.09474 | -0.12681 | 59.5683 | 59.6038 | 59.6142 | 59.563 | 61.6109 | 61.6806 | 61.4817 | 61.6419 | 0.1722 | 0.037306 | 0.042933 | 0.01618 | 0.049995 | 0.14509 | -0.076458 | 59.6187 | 59.6542 | 59.6645 | 59.6134 | 61.6613 | 61.731 | 61.5321 | 61.6923 | -2.0426 | -1.9134 | -1.9968 | -1.8676
457.9844 | 121.7148 | -61.7203 | 59.7794 | 0.13559 | -0.00389 | -0.007421 | -0.029595 | -0.000359 | 0.099318 | -0.11765 | 59.5592 | 59.6084 | 59.6142 | 59.5722 | 61.6064 | 61.6715 | 61.4772 | 61.6465 | 0.18594 | 0.046464 | 0.042933 | 0.020759 | 0.049995 | 0.14967 | -0.067301 | 59.6095 | 59.6588 | 59.6645 | 59.6225 | 61.6567 | 61.7218 | 61.5275 | 61.6969 | -2.0472 | -1.918 | -1.9922 | -1.863
459.75 | 121.7606 | -61.6333 | 59.8297 | 0.13101 | -0.008469 | -0.007421 | -0.029595 | -0.000359 | 0.090161 | -0.12223 | 59.5592 | 59.6084 | 59.6142 | 59.563 | 61.6064 | 61.676 | 61.4863 | 61.6465 | 0.18136 | 0.041885 | 0.042933 | 0.020759 | 0.049995 | 0.14052 | -0.07188 | 59.6095 | 59.6588 | 59.6645 | 59.6134 | 61.6567 | 61.7264 | 61.5367 | 61.6969 | -2.0472 | -1.9271 | -1.9922 | -1.8722
461.4375 | 121.7514 | -61.7157 | 59.7748 | 0.12643 | -0.008469 | -0.012 | -0.034174 | -0.004937 | 0.09474 | -0.12223 | 59.5546 | 59.6038 | 59.6187 | 59.5584 | 61.6109 | 61.6852 | 61.4726 | 61.6419 | 0.17678 | 0.041885 | 0.038354 | 0.01618 | 0.045417 | 0.14509 | -0.07188 | 59.605 | 59.6542 | 59.6691 | 59.6088 | 61.6613 | 61.7355 | 61.5229 | 61.6923 | -2.0563 | -1.918 | -1.9922 | -1.8539
463.1875 | 121.6644 | -61.7065 | 59.816 | 0.13101 | -0.00389 | -0.007421 | -0.034174 | 0.004219 | 0.09474 | -0.11765 | 59.5592 | 59.6038 | 59.6187 | 59.5676 | 61.6155 | 61.6806 | 61.4863 | 61.6374 | 0.18136 | 0.046464 | 0.042933 | 0.01618 | 0.054573 | 0.14509 | -0.067301 | 59.6095 | 59.6542 | 59.6691 | 59.6179 | 61.6659 | 61.731 | 61.5367 | 61.6877 | -2.0563 | -1.9271 | -1.9968 | -1.8676
464.9531 | 121.7194 | -61.734 | 59.7656 | 0.13101 | 0.000689 | -0.007421 | -0.034174 | 0.008797 | 0.1039 | -0.11765 | 59.5592 | 59.6038 | 59.6187 | 59.5722 | 61.6109 | 61.676 | 61.4909 | 61.6419 | 0.18136 | 0.051043 | 0.042933 | 0.01618 | 0.059151 | 0.15425 | -0.067301 | 59.6095 | 59.6542 | 59.6691 | 59.6225 | 61.6613 | 61.7264 | 61.5412 | 61.6923 | -2.0517 | -1.9317 | -1.9922 | -1.8722
466.6406 | 121.8155 | -61.6425 | 59.8022 | 0.13101 | -0.008469 | -0.012 | -0.034174 | -0.000359 | 0.090161 | -0.12681 | 59.5592 | 59.6084 | 59.6187 | 59.5676 | 61.6018 | 61.6806 | 61.4863 | 61.6465 | 0.18136 | 0.041885 | 0.038354 | 0.01618 | 0.049995 | 0.14052 | -0.076458 | 59.6095 | 59.6588 | 59.6691 | 59.6179 | 61.6521 | 61.731 | 61.5367 | 61.6969 | -2.0426 | -1.9271 | -1.983 | -1.8676
468.375 | 121.7789 | -61.6196 | 59.816 | 0.12643 | -0.008469 | -0.012 | -0.029595 | -0.000359 | 0.09474 | -0.12681 | 59.5592 | 59.6084 | 59.6187 | 59.563 | 61.6109 | 61.6852 | 61.4817 | 61.6465 | 0.17678 | 0.041885 | 0.038354 | 0.020759 | 0.049995 | 0.14509 | -0.076458 | 59.6095 | 59.6588 | 59.6691 | 59.6134 | 61.6613 | 61.7355 | 61.5321 | 61.6969 | -2.0517 | -1.9225 | -1.9922 | -1.863
470.125 | 121.701 | -61.8027 | 59.7061 | 0.12643 | 0.005267 | -0.012 | -0.034174 | 0.008797 | 0.099318 | -0.11765 | 59.5592 | 59.613 | 59.6187 | 59.563 | 61.6109 | 61.676 | 61.4955 | 61.6419 | 0.17678 | 0.055621 | 0.038354 | 0.01618 | 0.059151 | 0.14967 | -0.067301 | 59.6095 | 59.6634 | 59.6691 | 59.6134 | 61.6613 | 61.7264 | 61.5458 | 61.6923 | -2.0517 | -1.9363 | -1.9922 | -1.8767
471.875 | 121.6919 | -61.7661 | 59.7107 | 0.12643 | -0.00389 | -0.012 | -0.029595 | 0.008797 | 0.09474 | -0.11765 | 59.5592 | 59.613 | 59.6187 | 59.5676 | 61.6109 | 61.676 | 61.4817 | 61.6374 | 0.17678 | 0.046464 | 0.038354 | 0.020759 | 0.059151 | 0.14509 | -0.067301 | 59.6095 | 59.6634 | 59.6691 | 59.6179 | 61.6613 | 61.7264 | 61.5321 | 61.6877 | -2.0517 | -1.9225 | -1.9922 | -1.863
473.625 | 121.6919 | -61.7569 | 59.697 | 0.13101 | -0.008469 | -0.007421 | -0.025017 | 0.004219 | 0.099318 | -0.12223 | 59.5592 | 59.6084 | 59.6233 | 59.563 | 61.6109 | 61.6806 | 61.4817 | 61.6374 | 0.18136 | 0.041885 | 0.042933 | 0.025337 | 0.054573 | 0.14967 | -0.07188 | 59.6095 | 59.6588 | 59.6737 | 59.6134 | 61.6613 | 61.731 | 61.5321 | 61.6877 | -2.0517 | -1.9225 | -1.9876 | -1.8584
475.3125 | 121.7422 | -61.7615 | 59.6832 | 0.13559 | -0.00389 | -0.007421 | -0.025017 | 0.008797 | 0.099318 | -0.12223 | 59.5592 | 59.6176 | 59.6187 | 59.5676 | 61.5972 | 61.6806 | 61.4909 | 61.6374 | 0.18594 | 0.046464 | 0.042933 | 0.025337 | 0.059151 | 0.14967 | -0.07188 | 59.6095 | 59.6679 | 59.6691 | 59.6179 | 61.6475 | 61.731 | 61.5412 | 61.6877 | -2.038 | -1.9317 | -1.9785 | -1.8722
477.0469 | 121.6553 | -61.821 | 59.6924 | 0.12643 | -0.008469 | -0.016578 | -0.029595 | -0.000359 | 0.1039 | -0.12223 | 59.5546 | 59.613 | 59.6187 | 59.563 | 61.6064 | 61.676 | 61.4772 | 61.6419 | 0.17678 | 0.041885 | 0.033776 | 0.020759 | 0.049995 | 0.15425 | -0.07188 | 59.605 | 59.6634 | 59.6691 | 59.6134 | 61.6567 | 61.7264 | 61.5275 | 61.6923 | -2.0517 | -1.9225 | -1.9876 | -1.8584
478.7969 | 121.7697 | -61.6608 | 59.7794 | 0.13101 | -0.008469 | -0.012 | -0.034174 | 0.004219 | 0.099318 | -0.12681 | 59.5592 | 59.613 | 59.6096 | 59.563 | 61.6064 | 61.6806 | 61.4863 | 61.6419 | 0.18136 | 0.041885 | 0.038354 | 0.01618 | 0.054573 | 0.14967 | -0.076458 | 59.6095 | 59.6634 | 59.6599 | 59.6134 | 61.6567 | 61.731 | 61.5367 | 61.6923 | -2.0472 | -1.9271 | -1.9968 | -1.8767
480.5469 | 121.6782 | -61.7661 | 59.7107 | 0.13101 | -0.00389 | -0.007421 | -0.025017 | 0.008797 | 0.09474 | -0.11765 | 59.5546 | 59.6084 | 59.6187 | 59.5722 | 61.6018 | 61.6806 | 61.4817 | 61.6419 | 0.18136 | 0.046464 | 0.042933 | 0.025337 | 0.059151 | 0.14509 | -0.067301 | 59.605 | 59.6588 | 59.6691 | 59.6225 | 61.6521 | 61.731 | 61.5321 | 61.6923 | -2.0472 | -1.9271 | -1.983 | -1.863
482.2188 | 121.8018 | -61.5784 | 59.7977 | 0.12643 | -0.013048 | -0.012 | -0.029595 | 0.004219 | 0.090161 | -0.12223 | 59.5546 | 59.613 | 59.6142 | 59.5676 | 61.6109 | 61.6806 | 61.4909 | 61.6374 | 0.17678 | 0.037306 | 0.038354 | 0.020759 | 0.054573 | 0.14052 | -0.07188 | 59.605 | 59.6634 | 59.6645 | 59.6179 | 61.6613 | 61.731 | 61.5412 | 61.6877 | -2.0563 | -1.9363 | -1.9968 | -1.8767
483.9688 | 121.7514 | -61.7065 | 59.7107 | 0.12185 | -0.008469 | -0.012 | -0.029595 | 0.004219 | 0.1039 | -0.12681 | 59.5546 | 59.6084 | 59.6233 | 59.5676 | 61.6109 | 61.676 | 61.4817 | 61.6374 | 0.1722 | 0.041885 | 0.038354 | 0.020759 | 0.054573 | 0.15425 | -0.076458 | 59.605 | 59.6588 | 59.6737 | 59.6179 | 61.6613 | 61.7264 | 61.5321 | 61.6877 | -2.0563 | -1.9271 | -1.9876 | -1.8584
485.7188 | 121.701 | -61.734 | 59.7198 | 0.13101 | -0.008469 | -0.002842 | -0.025017 | -0.000359 | 0.09474 | -0.12681 | 59.5546 | 59.6084 | 59.6142 | 59.563 | 61.6064 | 61.6852 | 61.4817 | 61.6419 | 0.18136 | 0.041885 | 0.047512 | 0.025337 | 0.049995 | 0.14509 | -0.076458 | 59.605 | 59.6588 | 59.6645 | 59.6134 | 61.6567 | 61.7355 | 61.5321 | 61.6923 | -2.0517 | -1.9271 | -1.9922 | -1.8676
487.4062 | 121.8063 | -61.5967 | 59.8206 | 0.13101 | -0.013048 | -0.012 | -0.029595 | -0.009515 | 0.090161 | -0.12681 | 59.5546 | 59.613 | 59.6142 | 59.5676 | 61.6064 | 61.6806 | 61.4817 | 61.6465 | 0.18136 | 0.037306 | 0.038354 | 0.020759 | 0.040839 | 0.14052 | -0.076458 | 59.605 | 59.6634 | 59.6645 | 59.6179 | 61.6567 | 61.731 | 61.5321 | 61.6969 | -2.0517 | -1.9271 | -1.9922 | -1.8676
489.1562 | 121.7148 | -61.734 | 59.7382 | 0.13559 | -0.00389 | -0.007421 | -0.025017 | 0.008797 | 0.099318 | -0.11308 | 59.5592 | 59.613 | 59.6233 | 59.5676 | 61.6064 | 61.6715 | 61.4863 | 61.6419 | 0.18594 | 0.046464 | 0.042933 | 0.025337 | 0.059151 | 0.14967 | -0.062723 | 59.6095 | 59.6634 | 59.6737 | 59.6179 | 61.6567 | 61.7218 | 61.5367 | 61.6923 | -2.0472 | -1.9271 | -1.983 | -1.863
490.9062 | 121.7194 | -61.7294 | 59.7656 | 0.13559 | -0.00389 | -0.007421 | -0.029595 | 0.008797 | 0.090161 | -0.12223 | 59.5638 | 59.6038 | 59.6187 | 59.5676 | 61.6064 | 61.6806 | 61.4863 | 61.6465 | 0.18594 | 0.046464 | 0.042933 | 0.020759 | 0.059151 | 0.14052 | -0.07188 | 59.6141 | 59.6542 | 59.6691 | 59.6179 | 61.6567 | 61.731 | 61.5367 | 61.6969 | -2.0426 | -1.9225 | -1.9876 | -1.8676
492.5938 | 121.7422 | -61.6882 | 59.7519 | 0.12643 | -0.008469 | -0.021157 | -0.034174 | -0.000359 | 0.09474 | -0.12681 | 59.5546 | 59.6038 | 59.6142 | 59.5722 | 61.6064 | 61.6806 | 61.4772 | 61.6328 | 0.17678 | 0.041885 | 0.029197 | 0.01618 | 0.049995 | 0.14509 | -0.076458 | 59.605 | 59.6542 | 59.6645 | 59.6225 | 61.6567 | 61.731 | 61.5275 | 61.6831 | -2.0517 | -1.9225 | -1.9922 | -1.863
494.3438 | 121.6736 | -61.8073 | 59.6924 | 0.13101 | -0.00389 | -0.007421 | -0.029595 | 0.008797 | 0.09474 | -0.12681 | 59.5592 | 59.613 | 59.6142 | 59.563 | 61.6018 | 61.6806 | 61.4817 | 61.6374 | 0.18136 | 0.046464 | 0.042933 | 0.020759 | 0.059151 | 0.14509 | -0.076458 | 59.6095 | 59.6634 | 59.6645 | 59.6134 | 61.6521 | 61.731 | 61.5321 | 61.6877 | -2.0426 | -1.9225 | -1.9876 | -1.8676
496.0938 | 121.7926 | -61.7569 | 59.6649 | 0.12643 | -0.013048 | -0.012 | -0.029595 | 0.004219 | 0.099318 | -0.12681 | 59.5546 | 59.613 | 59.6142 | 59.563 | 61.6018 | 61.6852 | 61.4863 | 61.6465 | 0.17678 | 0.037306 | 0.038354 | 0.020759 | 0.054573 | 0.14967 | -0.076458 | 59.605 | 59.6634 | 59.6645 | 59.6134 | 61.6521 | 61.7355 | 61.5367 | 61.6969 | -2.0472 | -1.9317 | -1.9876 | -1.8722
497.7812 | 121.7972 | -61.6287 | 59.8022 | 0.13101 | -0.00389 | -0.007421 | -0.029595 | 0.004219 | 0.090161 | -0.12681 | 59.5638 | 59.6038 | 59.6142 | 59.5584 | 61.6109 | 61.6806 | 61.4863 | 61.6419 | 0.18136 | 0.046464 | 0.042933 | 0.020759 | 0.054573 | 0.14052 | -0.076458 | 59.6141 | 59.6542 | 59.6645 | 59.6088 | 61.6613 | 61.731 | 61.5367 | 61.6923 | -2.0472 | -1.9225 | -1.9968 | -1.8722
499.5312 | 121.6873 | -61.7935 | 59.7153 | 0.13101 | -0.00389 | -0.007421 | -0.020438 | 0.008797 | 0.09474 | -0.13139 | 59.5638 | 59.6084 | 59.6142 | 59.563 | 61.6064 | 61.676 | 61.4817 | 61.6465 | 0.18136 | 0.046464 | 0.042933 | 0.029916 | 0.059151 | 0.14509 | -0.081036 | 59.6141 | 59.6588 | 59.6645 | 59.6134 | 61.6567 | 61.7264 | 61.5321 | 61.6969 | -2.0426 | -1.918 | -1.9922 | -1.8676
501.2812 | 121.8246 | -61.6287 | 59.7656 | 0.12643 | -0.008469 | -0.016578 | -0.034174 | 0.004219 | 0.09474 | -0.12223 | 59.5638 | 59.6038 | 59.6096 | 59.5676 | 61.6018 | 61.676 | 61.4817 | 61.6419 | 0.17678 | 0.041885 | 0.033776 | 0.01618 | 0.054573 | 0.14509 | -0.07188 | 59.6141 | 59.6542 | 59.6599 | 59.6179 | 61.6521 | 61.7264 | 61.5321 | 61.6923 | -2.038 | -1.918 | -1.9922 | -1.8722
503.0312 | 121.7331 | -61.734 | 59.7473 | 0.13101 | -0.008469 | -0.007421 | -0.025017 | 0.008797 | 0.099318 | -0.12681 | 59.5592 | 59.6084 | 59.6096 | 59.563 | 61.6064 | 61.6806 | 61.4772 | 61.6374 | 0.18136 | 0.041885 | 0.042933 | 0.025337 | 0.059151 | 0.14967 | -0.076458 | 59.6095 | 59.6588 | 59.6599 | 59.6134 | 61.6567 | 61.731 | 61.5275 | 61.6877 | -2.0472 | -1.918 | -1.9968 | -1.8676
504.7031 | 121.7239 | -61.7294 | 59.7702 | 0.13101 | -0.013048 | -0.012 | -0.025017 | 0.004219 | 0.09474 | -0.12223 | 59.5638 | 59.613 | 59.6187 | 59.563 | 61.6109 | 61.676 | 61.4817 | 61.6419 | 0.18136 | 0.037306 | 0.038354 | 0.025337 | 0.054573 | 0.14509 | -0.07188 | 59.6141 | 59.6634 | 59.6691 | 59.6134 | 61.6613 | 61.7264 | 61.5321 | 61.6923 | -2.0472 | -1.918 | -1.9922 | -1.863
506.4531 | 121.7926 | -61.6104 | 59.8297 | 0.13559 | -0.008469 | -0.007421 | -0.029595 | 0.004219 | 0.090161 | -0.12223 | 59.5592 | 59.6176 | 59.6187 | 59.5676 | 61.6018 | 61.6806 | 61.4863 | 61.6465 | 0.18594 | 0.041885 | 0.042933 | 0.020759 | 0.054573 | 0.14052 | -0.07188 | 59.6095 | 59.6679 | 59.6691 | 59.6179 | 61.6521 | 61.731 | 61.5367 | 61.6969 | -2.0426 | -1.9271 | -1.983 | -1.8676
508.1406 | 121.788 | -61.7294 | 59.6649 | 0.13101 | -0.00389 | -0.007421 | -0.034174 | 0.013375 | 0.09474 | -0.12681 | 59.5592 | 59.6084 | 59.6142 | 59.563 | 61.6018 | 61.6715 | 61.4772 | 61.6374 | 0.18136 | 0.046464 | 0.042933 | 0.01618 | 0.063729 | 0.14509 | -0.076458 | 59.6095 | 59.6588 | 59.6645 | 59.6134 | 61.6521 | 61.7218 | 61.5275 | 61.6877 | -2.0426 | -1.918 | -1.9876 | -1.863
509.8906 | 121.701 | -61.7111 | 59.7794 | 0.13101 | -0.00389 | -0.007421 | -0.025017 | 0.008797 | 0.090161 | -0.12681 | 59.5592 | 59.613 | 59.6187 | 59.563 | 61.6064 | 61.676 | 61.4726 | 61.6374 | 0.18136 | 0.046464 | 0.042933 | 0.025337 | 0.059151 | 0.14052 | -0.076458 | 59.6095 | 59.6634 | 59.6691 | 59.6134 | 61.6567 | 61.7264 | 61.5229 | 61.6877 | -2.0472 | -1.9134 | -1.9876 | -1.8539
511.5781 | 121.756 | -61.7111 | 59.7519 | 0.13559 | -0.00389 | -0.012 | -0.038752 | -0.000359 | 0.09474 | -0.13139 | 59.5546 | 59.613 | 59.6142 | 59.5676 | 61.6064 | 61.6623 | 61.4817 | 61.6374 | 0.18594 | 0.046464 | 0.038354 | 0.011602 | 0.049995 | 0.14509 | -0.081036 | 59.605 | 59.6634 | 59.6645 | 59.6179 | 61.6567 | 61.7127 | 61.5321 | 61.6877 | -2.0517 | -1.9271 | -1.9922 | -1.8676
513.3281 | 121.6736 | -61.7111 | 59.8251 | 0.13101 | -0.008469 | -0.012 | -0.029595 | 0.008797 | 0.099318 | -0.12681 | 59.5546 | 59.6084 | 59.6142 | 59.563 | 61.6109 | 61.676 | 61.4817 | 61.6374 | 0.18136 | 0.041885 | 0.038354 | 0.020759 | 0.059151 | 0.14967 | -0.076458 | 59.605 | 59.6588 | 59.6645 | 59.6134 | 61.6613 | 61.7264 | 61.5321 | 61.6877 | -2.0563 | -1.9271 | -1.9968 | -1.8676
515.0781 | 121.7834 | -61.734 | 59.6786 | 0.13101 | -0.008469 | -0.016578 | -0.029595 | 0.013375 | 0.090161 | -0.12223 | 59.5592 | 59.6084 | 59.6096 | 59.5584 | 61.6018 | 61.676 | 61.4817 | 61.6374 | 0.18136 | 0.041885 | 0.033776 | 0.020759 | 0.063729 | 0.14052 | -0.07188 | 59.6095 | 59.6588 | 59.6599 | 59.6088 | 61.6521 | 61.7264 | 61.5321 | 61.6877 | -2.0426 | -1.9225 | -1.9922 | -1.8722
516.7656 | 121.7148 | -61.7065 | 59.7748 | 0.13101 | -0.013048 | -0.007421 | -0.025017 | 0.008797 | 0.099318 | -0.11765 | 59.5638 | 59.613 | 59.6187 | 59.5584 | 61.5972 | 61.676 | 61.4817 | 61.6374 | 0.18136 | 0.037306 | 0.042933 | 0.025337 | 0.059151 | 0.14967 | -0.067301 | 59.6141 | 59.6634 | 59.6691 | 59.6088 | 61.6475 | 61.7264 | 61.5321 | 61.6877 | -2.0334 | -1.918 | -1.9785 | -1.863
518.5 | 121.669 | -61.7752 | 59.7153 | 0.13559 | -0.00389 | -0.016578 | -0.025017 | 0.013375 | 0.099318 | -0.12681 | 59.5592 | 59.6176 | 59.6187 | 59.563 | 61.5972 | 61.676 | 61.4817 | 61.6328 | 0.18594 | 0.046464 | 0.033776 | 0.025337 | 0.063729 | 0.14967 | -0.076458 | 59.6095 | 59.6679 | 59.6691 | 59.6134 | 61.6475 | 61.7264 | 61.5321 | 61.6831 | -2.038 | -1.9225 | -1.9785 | -1.863
520.2031 | 121.7926 | -61.6241 | 59.8068 | 0.12643 | -0.013048 | -0.012 | -0.025017 | -0.000359 | 0.090161 | -0.11765 | 59.5638 | 59.613 | 59.6233 | 59.563 | 61.6109 | 61.6806 | 61.4863 | 61.6419 | 0.17678 | 0.037306 | 0.038354 | 0.025337 | 0.049995 | 0.14052 | -0.067301 | 59.6141 | 59.6634 | 59.6737 | 59.6134 | 61.6613 | 61.731 | 61.5367 | 61.6923 | -2.0472 | -1.9225 | -1.9876 | -1.863
521.9375 | 121.8063 | -61.6058 | 59.8251 | 0.12643 | -0.008469 | -0.012 | -0.020438 | 0.008797 | 0.09474 | -0.12681 | 59.5592 | 59.6084 | 59.6187 | 59.563 | 61.6064 | 61.676 | 61.4863 | 61.6374 | 0.17678 | 0.041885 | 0.038354 | 0.029916 | 0.059151 | 0.14509 | -0.076458 | 59.6095 | 59.6588 | 59.6691 | 59.6134 | 61.6567 | 61.7264 | 61.5367 | 61.6877 | -2.0472 | -1.9271 | -1.9876 | -1.8676
523.6875 | 121.7056 | -61.7157 | 59.7931 | 0.13101 | -0.013048 | -0.012 | -0.025017 | 0.008797 | 0.099318 | -0.12223 | 59.5638 | 59.6084 | 59.6142 | 59.5584 | 61.6018 | 61.6715 | 61.4772 | 61.6374 | 0.18136 | 0.037306 | 0.038354 | 0.025337 | 0.059151 | 0.14967 | -0.07188 | 59.6141 | 59.6588 | 59.6645 | 59.6088 | 61.6521 | 61.7218 | 61.5275 | 61.6877 | -2.038 | -1.9134 | -1.9876 | -1.863
525.4531 | 121.7834 | -61.734 | 59.6924 | 0.12185 | -0.013048 | -0.007421 | -0.034174 | 0.004219 | 0.090161 | -0.12681 | 59.5592 | 59.613 | 59.6187 | 59.5676 | 61.6109 | 61.6806 | 61.4772 | 61.6419 | 0.1722 | 0.037306 | 0.042933 | 0.01618 | 0.054573 | 0.14052 | -0.076458 | 59.6095 | 59.6634 | 59.6691 | 59.6179 | 61.6613 | 61.731 | 61.5275 | 61.6923 | -2.0517 | -1.918 | -1.9922 | -1.8584
527.1406 | 121.7148 | -61.7523 | 59.7748 | 0.12643 | -0.013048 | -0.007421 | -0.029595 | 0.013375 | 0.099318 | -0.12681 | 59.5592 | 59.613 | 59.6187 | 59.563 | 61.6018 | 61.676 | 61.4817 | 61.6465 | 0.17678 | 0.037306 | 0.042933 | 0.020759 | 0.063729 | 0.14967 | -0.076458 | 59.6095 | 59.6634 | 59.6691 | 59.6134 | 61.6521 | 61.7264 | 61.5321 | 61.6969 | -2.0426 | -1.9225 | -1.983 | -1.863
528.875 | 121.6782 | -61.6837 | 59.8297 | 0.13559 | -0.013048 | -0.007421 | -0.029595 | 0.004219 | 0.1039 | -0.12681 | 59.5638 | 59.613 | 59.6096 | 59.5676 | 61.6064 | 61.6715 | 61.4863 | 61.6419 | 0.18594 | 0.037306 | 0.042933 | 0.020759 | 0.054573 | 0.15425 | -0.076458 | 59.6141 | 59.6634 | 59.6599 | 59.6179 | 61.6567 | 61.7218 | 61.5367 | 61.6923 | -2.0426 | -1.9225 | -1.9968 | -1.8767
530.625 | 121.6599 | -61.6608 | 59.8343 | 0.12643 | -0.017627 | -0.007421 | -0.029595 | 0.008797 | 0.090161 | -0.12223 | 59.5638 | 59.6084 | 59.6187 | 59.5676 | 61.6018 | 61.6806 | 61.4726 | 61.6374 | 0.17678 | 0.032727 | 0.042933 | 0.020759 | 0.059151 | 0.14052 | -0.07188 | 59.6141 | 59.6588 | 59.6691 | 59.6179 | 61.6521 | 61.731 | 61.5229 | 61.6877 | -2.038 | -1.9088 | -1.983 | -1.8539
532.3281 | 121.7056 | -61.7249 | 59.7336 | 0.13559 | -0.008469 | -0.016578 | -0.020438 | 0.004219 | 0.1039 | -0.12223 | 59.5592 | 59.6176 | 59.6187 | 59.563 | 61.6109 | 61.6806 | 61.4726 | 61.6419 | 0.18594 | 0.041885 | 0.033776 | 0.029916 | 0.054573 | 0.15425 | -0.07188 | 59.6095 | 59.6679 | 59.6691 | 59.6134 | 61.6613 | 61.731 | 61.5229 | 61.6923 | -2.0517 | -1.9134 | -1.9922 | -1.8539
534.0625 | 121.6278 | -61.7798 | 59.7244 | 0.13101 | -0.008469 | -0.012 | -0.029595 | 0.008797 | 0.099318 | -0.12223 | 59.5592 | 59.6176 | 59.6142 | 59.5722 | 61.6018 | 61.676 | 61.4726 | 61.6328 | 0.18136 | 0.041885 | 0.038354 | 0.020759 | 0.059151 | 0.14967 | -0.07188 | 59.6095 | 59.6679 | 59.6645 | 59.6225 | 61.6521 | 61.7264 | 61.5229 | 61.6831 | -2.0426 | -1.9134 | -1.9876 | -1.8584
535.75 | 121.7239 | -61.7294 | 59.7565 | 0.13101 | -0.013048 | -0.012 | -0.029595 | 0.013375 | 0.09474 | -0.11308 | 59.5546 | 59.6084 | 59.6233 | 59.5584 | 61.5972 | 61.676 | 61.4817 | 61.6465 | 0.18136 | 0.037306 | 0.038354 | 0.020759 | 0.063729 | 0.14509 | -0.062723 | 59.605 | 59.6588 | 59.6737 | 59.6088 | 61.6475 | 61.7264 | 61.5321 | 61.6969 | -2.0426 | -1.9271 | -1.9739 | -1.8584
537.5 | 121.756 | -61.6974 | 59.729 | 0.13101 | -0.013048 | -0.007421 | -0.029595 | 0.004219 | 0.099318 | -0.12681 | 59.5592 | 59.613 | 59.6142 | 59.563 | 61.6018 | 61.676 | 61.4772 | 61.6374 | 0.18136 | 0.037306 | 0.042933 | 0.020759 | 0.054573 | 0.14967 | -0.076458 | 59.6095 | 59.6634 | 59.6645 | 59.6134 | 61.6521 | 61.7264 | 61.5275 | 61.6877 | -2.0426 | -1.918 | -1.9876 | -1.863
539.25 | 121.788 | -61.6379 | 59.8114 | 0.12643 | -0.013048 | -0.016578 | -0.029595 | 0.004219 | 0.090161 | -0.13139 | 59.5638 | 59.613 | 59.6233 | 59.5584 | 61.6064 | 61.676 | 61.4817 | 61.6328 | 0.17678 | 0.037306 | 0.033776 | 0.020759 | 0.054573 | 0.14052 | -0.081036 | 59.6141 | 59.6634 | 59.6737 | 59.6088 | 61.6567 | 61.7264 | 61.5321 | 61.6831 | -2.0426 | -1.918 | -1.983 | -1.8584
540.9375 | 121.7743 | -61.615 | 59.7931 | 0.12185 | -0.008469 | -0.012 | -0.029595 | 0.004219 | 0.09474 | -0.12223 | 59.5638 | 59.6176 | 59.6187 | 59.5722 | 61.6018 | 61.6715 | 61.4772 | 61.6328 | 0.1722 | 0.041885 | 0.038354 | 0.020759 | 0.054573 | 0.14509 | -0.07188 | 59.6141 | 59.6679 | 59.6691 | 59.6225 | 61.6521 | 61.7218 | 61.5275 | 61.6831 | -2.038 | -1.9134 | -1.983 | -1.8584
542.6875 | 121.788 | -61.7111 | 59.7198 | 0.12643 | -0.013048 | -0.012 | -0.034174 | 0.008797 | 0.09474 | -0.12681 | 59.5546 | 59.613 | 59.6279 | 59.5584 | 61.6018 | 61.6715 | 61.4772 | 61.6374 | 0.17678 | 0.037306 | 0.038354 | 0.01618 | 0.059151 | 0.14509 | -0.076458 | 59.605 | 59.6634 | 59.6782 | 59.6088 | 61.6521 | 61.7218 | 61.5275 | 61.6877 | -2.0472 | -1.9225 | -1.9739 | -1.8493
544.4531 | 121.7926 | -61.7249 | 59.7244 | 0.12643 | -0.013048 | -0.007421 | -0.034174 | 0.013375 | 0.09474 | -0.12681 | 59.5638 | 59.613 | 59.6233 | 59.5722 | 61.588 | 61.6715 | 61.4726 | 61.6374 | 0.17678 | 0.037306 | 0.042933 | 0.01618 | 0.063729 | 0.14509 | -0.076458 | 59.6141 | 59.6634 | 59.6737 | 59.6225 | 61.6384 | 61.7218 | 61.5229 | 61.6877 | -2.0243 | -1.9088 | -1.9647 | -1.8493
546.1406 | 121.7468 | -61.6791 | 59.761 | 0.12643 | -0.013048 | -0.016578 | -0.034174 | 0.013375 | 0.085583 | -0.12681 | 59.5638 | 59.6222 | 59.6279 | 59.563 | 61.5972 | 61.6715 | 61.468 | 61.6328 | 0.17678 | 0.037306 | 0.033776 | 0.01618 | 0.063729 | 0.13594 | -0.076458 | 59.6141 | 59.6725 | 59.6782 | 59.6134 | 61.6475 | 61.7218 | 61.5184 | 61.6831 | -2.0334 | -1.9042 | -1.9693 | -1.8401
547.875 | 121.701 | -61.7065 | 59.7382 | 0.13101 | -0.00389 | -0.012 | -0.020438 | 0.013375 | 0.099318 | -0.12223 | 59.5775 | 59.6176 | 59.6279 | 59.5722 | 61.5972 | 61.6669 | 61.4726 | 61.6282 | 0.18136 | 0.046464 | 0.038354 | 0.029916 | 0.063729 | 0.14967 | -0.07188 | 59.6279 | 59.6679 | 59.6782 | 59.6225 | 61.6475 | 61.7172 | 61.5229 | 61.6786 | -2.0197 | -1.8951 | -1.9693 | -1.8447
549.625 | 121.7697 | -61.7203 | 59.7015 | 0.13101 | -0.013048 | -0.016578 | -0.029595 | 0.013375 | 0.099318 | -0.11765 | 59.5729 | 59.6222 | 59.637 | 59.5767 | 61.5972 | 61.6669 | 61.468 | 61.6282 | 0.18136 | 0.037306 | 0.033776 | 0.020759 | 0.063729 | 0.14967 | -0.067301 | 59.6233 | 59.6725 | 59.6874 | 59.6271 | 61.6475 | 61.7172 | 61.5184 | 61.6786 | -2.0243 | -1.8951 | -1.9602 | -1.831
551.3594 | 121.756 | -61.6745 | 59.7748 | 0.12643 | -0.017627 | -0.012 | -0.029595 | 0.013375 | 0.090161 | -0.12681 | 59.5775 | 59.6222 | 59.6416 | 59.5767 | 61.588 | 61.6669 | 61.468 | 61.6282 | 0.17678 | 0.032727 | 0.038354 | 0.020759 | 0.063729 | 0.14052 | -0.076458 | 59.6279 | 59.6725 | 59.692 | 59.6271 | 61.6384 | 61.7172 | 61.5184 | 61.6786 | -2.0105 | -1.8905 | -1.9464 | -1.8264
553.0938 | 121.756 | -61.6745 | 59.7931 | 0.13101 | -0.017627 | -0.012 | -0.029595 | 0.004219 | 0.09474 | -0.12681 | 59.5775 | 59.6222 | 59.6325 | 59.5722 | 61.5926 | 61.6669 | 61.468 | 61.6282 | 0.18136 | 0.032727 | 0.038354 | 0.020759 | 0.054573 | 0.14509 | -0.076458 | 59.6279 | 59.6725 | 59.6828 | 59.6225 | 61.643 | 61.7172 | 61.5184 | 61.6786 | -2.0151 | -1.8905 | -1.9602 | -1.8355
554.8438 | 121.7422 | -61.6699 | 59.7977 | 0.12643 | -0.013048 | -0.016578 | -0.034174 | 0.004219 | 0.090161 | -0.12681 | 59.5775 | 59.6267 | 59.6416 | 59.5676 | 61.5926 | 61.6669 | 61.4634 | 61.6282 | 0.17678 | 0.037306 | 0.033776 | 0.01618 | 0.054573 | 0.14052 | -0.076458 | 59.6279 | 59.6771 | 59.692 | 59.6179 | 61.643 | 61.7172 | 61.5138 | 61.6786 | -2.0151 | -1.8859 | -1.951 | -1.8218
556.5312 | 121.701 | -61.7661 | 59.7061 | 0.13559 | -0.008469 | -0.012 | -0.025017 | 0.013375 | 0.09474 | -0.12223 | 59.5775 | 59.6313 | 59.637 | 59.5767 | 61.588 | 61.6623 | 61.468 | 61.6236 | 0.18594 | 0.041885 | 0.038354 | 0.025337 | 0.063729 | 0.14509 | -0.07188 | 59.6279 | 59.6817 | 59.6874 | 59.6271 | 61.6384 | 61.7127 | 61.5184 | 61.674 | -2.0105 | -1.8905 | -1.951 | -1.831
558.2812 | 121.7972 | -61.7249 | 59.7015 | 0.13559 | -0.017627 | -0.021157 | -0.029595 | 0.004219 | 0.09474 | -0.13139 | 59.5775 | 59.6359 | 59.6325 | 59.5859 | 61.588 | 61.6577 | 61.4588 | 61.6236 | 0.18594 | 0.032727 | 0.029197 | 0.020759 | 0.054573 | 0.14509 | -0.081036 | 59.6279 | 59.6862 | 59.6828 | 59.6362 | 61.6384 | 61.7081 | 61.5092 | 61.674 | -2.0105 | -1.8813 | -1.9556 | -1.8264
560.0312 | 121.701 | -61.7065 | 59.7839 | 0.13101 | -0.013048 | -0.012 | -0.020438 | 0.004219 | 0.09474 | -0.12223 | 59.5821 | 59.6359 | 59.6416 | 59.5813 | 61.5835 | 61.6486 | 61.4543 | 61.6145 | 0.18136 | 0.037306 | 0.038354 | 0.029916 | 0.054573 | 0.14509 | -0.07188 | 59.6324 | 59.6862 | 59.692 | 59.6317 | 61.6338 | 61.6989 | 61.5046 | 61.6648 | -2.0014 | -1.8722 | -1.9418 | -1.8126
561.7812 | 121.6736 | -61.7798 | 59.7473 | 0.13559 | -0.008469 | -0.012 | -0.025017 | 0.013375 | 0.099318 | -0.12223 | 59.5821 | 59.6313 | 59.6462 | 59.5859 | 61.588 | 61.6486 | 61.4634 | 61.6145 | 0.18594 | 0.041885 | 0.038354 | 0.025337 | 0.063729 | 0.14967 | -0.07188 | 59.6324 | 59.6817 | 59.6966 | 59.6362 | 61.6384 | 61.6989 | 61.5138 | 61.6648 | -2.006 | -1.8813 | -1.9418 | -1.8172
563.4688 | 121.756 | -61.6562 | 59.7931 | 0.12185 | -0.008469 | -0.016578 | -0.025017 | 0.008797 | 0.09474 | -0.12681 | 59.5821 | 59.6359 | 59.637 | 59.5859 | 61.588 | 61.6486 | 61.4588 | 61.6099 | 0.1722 | 0.041885 | 0.033776 | 0.025337 | 0.059151 | 0.14509 | -0.076458 | 59.6324 | 59.6862 | 59.6874 | 59.6362 | 61.6384 | 61.6989 | 61.5092 | 61.6602 | -2.006 | -1.8768 | -1.951 | -1.8218
565.2344 | 121.7926 | -61.5967 | 59.8206 | 0.12643 | -0.022205 | -0.012 | -0.029595 | 0.004219 | 0.090161 | -0.12681 | 59.5912 | 59.645 | 59.6416 | 59.5859 | 61.5835 | 61.6394 | 61.4497 | 61.6099 | 0.17678 | 0.028149 | 0.038354 | 0.020759 | 0.054573 | 0.14052 | -0.076458 | 59.6416 | 59.6954 | 59.692 | 59.6362 | 61.6338 | 61.6898 | 61.5 | 61.6602 | -1.9922 | -1.8584 | -1.9418 | -1.8081
566.9219 | 121.7194 | -61.6974 | 59.7656 | 0.13559 | -0.00389 | -0.007421 | -0.025017 | 0.008797 | 0.1039 | -0.11765 | 59.5912 | 59.6405 | 59.6462 | 59.5859 | 61.5835 | 61.6531 | 61.4451 | 61.6099 | 0.18594 | 0.046464 | 0.042933 | 0.025337 | 0.059151 | 0.15425 | -0.067301 | 59.6416 | 59.6908 | 59.6966 | 59.6362 | 61.6338 | 61.7035 | 61.4955 | 61.6602 | -1.9922 | -1.8539 | -1.9373 | -1.7989
568.6719 | 121.7743 | -61.6928 | 59.7244 | 0.12643 | -0.017627 | -0.012 | -0.029595 | 0.004219 | 0.090161 | -0.12223 | 59.5867 | 59.645 | 59.6416 | 59.5951 | 61.5743 | 61.6531 | 61.4497 | 61.6099 | 0.17678 | 0.032727 | 0.038354 | 0.020759 | 0.054573 | 0.14052 | -0.07188 | 59.637 | 59.6954 | 59.692 | 59.6454 | 61.6247 | 61.7035 | 61.5 | 61.6602 | -1.9876 | -1.863 | -1.9327 | -1.8081
570.4375 | 121.6919 | -61.6745 | 59.8251 | 0.13559 | -0.008469 | -0.016578 | -0.025017 | 0.004219 | 0.1039 | -0.12223 | 59.5821 | 59.6496 | 59.6508 | 59.5905 | 61.5697 | 61.644 | 61.4497 | 61.6145 | 0.18594 | 0.041885 | 0.033776 | 0.025337 | 0.054573 | 0.15425 | -0.07188 | 59.6324 | 59.7 | 59.7011 | 59.6408 | 61.6201 | 61.6943 | 61.5 | 61.6648 | -1.9876 | -1.8676 | -1.919 | -1.7989
572.125 | 121.756 | -61.6653 | 59.7382 | 0.13101 | -0.013048 | -0.012 | -0.020438 | -0.000359 | 0.085583 | -0.12681 | 59.5867 | 59.6496 | 59.6508 | 59.5951 | 61.5697 | 61.6394 | 61.4497 | 61.6053 | 0.18136 | 0.037306 | 0.038354 | 0.029916 | 0.049995 | 0.13594 | -0.076458 | 59.637 | 59.7 | 59.7011 | 59.6454 | 61.6201 | 61.6898 | 61.5 | 61.6557 | -1.9831 | -1.863 | -1.919 | -1.7989
573.8594 | 121.7789 | -61.6104 | 59.8297 | 0.13559 | -0.013048 | -0.016578 | -0.025017 | -0.000359 | 0.090161 | -0.12223 | 59.5912 | 59.6405 | 59.6508 | 59.5905 | 61.5743 | 61.6394 | 61.4451 | 61.6007 | 0.18594 | 0.037306 | 0.033776 | 0.025337 | 0.049995 | 0.14052 | -0.07188 | 59.6416 | 59.6908 | 59.7011 | 59.6408 | 61.6247 | 61.6898 | 61.4955 | 61.6511 | -1.9831 | -1.8539 | -1.9235 | -1.7943
575.5938 | 121.701 | -61.734 | 59.761 | 0.13101 | -0.008469 | -0.007421 | -0.025017 | 0.008797 | 0.09474 | -0.12223 | 59.6096 | 59.6542 | 59.6554 | 59.6042 | 61.5697 | 61.6348 | 61.436 | 61.6053 | 0.18136 | 0.041885 | 0.042933 | 0.025337 | 0.059151 | 0.14509 | -0.07188 | 59.6599 | 59.7046 | 59.7057 | 59.6546 | 61.6201 | 61.6852 | 61.4863 | 61.6557 | -1.9602 | -1.8264 | -1.9144 | -1.7806
577.3281 | 121.6736 | -61.7386 | 59.7519 | 0.13101 | -0.008469 | -0.007421 | -0.025017 | 0.017953 | 0.099318 | -0.11308 | 59.6004 | 59.6542 | 59.6554 | 59.5951 | 61.5651 | 61.6348 | 61.4405 | 61.6007 | 0.18136 | 0.041885 | 0.042933 | 0.025337 | 0.068307 | 0.14967 | -0.062723 | 59.6508 | 59.7046 | 59.7057 | 59.6454 | 61.6155 | 61.6852 | 61.4909 | 61.6511 | -1.9648 | -1.8401 | -1.9098 | -1.7852
579.0781 | 121.6644 | -61.7432 | 59.7519 | 0.13559 | -0.008469 | -0.016578 | -0.020438 | 0.008797 | 0.09474 | -0.11765 | 59.605 | 59.6634 | 59.6599 | 59.5996 | 61.5606 | 61.6257 | 61.4314 | 61.587 | 0.18594 | 0.041885 | 0.033776 | 0.029916 | 0.059151 | 0.14509 | -0.067301 | 59.6553 | 59.7137 | 59.7103 | 59.65 | 61.6109 | 61.676 | 61.4817 | 61.6373 | -1.9556 | -1.8264 | -1.9006 | -1.7714
580.7656 | 121.7468 | -61.6608 | 59.7702 | 0.12643 | -0.017627 | -0.012 | -0.025017 | 0.008797 | 0.09474 | -0.12681 | 59.6096 | 59.6542 | 59.6645 | 59.5996 | 61.5651 | 61.6257 | 61.436 | 61.6007 | 0.17678 | 0.032727 | 0.038354 | 0.025337 | 0.059151 | 0.14509 | -0.076458 | 59.6599 | 59.7046 | 59.7149 | 59.65 | 61.6155 | 61.676 | 61.4863 | 61.6511 | -1.9556 | -1.8264 | -1.9006 | -1.7714
582.5156 | 121.8018 | -61.5875 | 59.8343 | 0.13559 | -0.017627 | -0.016578 | -0.025017 | 0.004219 | 0.099318 | -0.12223 | 59.605 | 59.6588 | 59.6599 | 59.5996 | 61.5651 | 61.6348 | 61.4405 | 61.6007 | 0.18594 | 0.032727 | 0.033776 | 0.025337 | 0.054573 | 0.14967 | -0.07188 | 59.6553 | 59.7091 | 59.7103 | 59.65 | 61.6155 | 61.6852 | 61.4909 | 61.6511 | -1.9602 | -1.8356 | -1.9052 | -1.7806
584.2656 | 121.6782 | -61.7386 | 59.7656 | 0.13101 | -0.00389 | -0.012 | -0.025017 | 0.008797 | 0.099318 | -0.12223 | 59.605 | 59.6588 | 59.6691 | 59.6134 | 61.556 | 61.6257 | 61.4268 | 61.5916 | 0.18136 | 0.046464 | 0.038354 | 0.025337 | 0.059151 | 0.14967 | -0.07188 | 59.6553 | 59.7091 | 59.7194 | 59.6637 | 61.6063 | 61.676 | 61.4771 | 61.6419 | -1.951 | -1.8218 | -1.8869 | -1.7577
585.9531 | 121.7102 | -61.6653 | 59.8114 | 0.13101 | -0.013048 | -0.002842 | -0.025017 | 0.004219 | 0.10848 | -0.12223 | 59.6096 | 59.6679 | 59.6645 | 59.6088 | 61.5514 | 61.6257 | 61.4268 | 61.5778 | 0.18136 | 0.037306 | 0.047512 | 0.025337 | 0.054573 | 0.15883 | -0.07188 | 59.6599 | 59.7183 | 59.7149 | 59.6591 | 61.6018 | 61.676 | 61.4771 | 61.6282 | -1.9419 | -1.8172 | -1.8869 | -1.7623
587.7031 | 121.6461 | -61.7111 | 59.7519 | 0.13559 | -0.00389 | -0.016578 | -0.020438 | 0.008797 | 0.1039 | -0.12223 | 59.6141 | 59.6679 | 59.6691 | 59.6088 | 61.556 | 61.6211 | 61.4176 | 61.587 | 0.18594 | 0.046464 | 0.033776 | 0.029916 | 0.059151 | 0.15425 | -0.07188 | 59.6645 | 59.7183 | 59.7194 | 59.6591 | 61.6063 | 61.6715 | 61.468 | 61.6373 | -1.9419 | -1.8035 | -1.8869 | -1.7485
589.4688 | 121.6965 | -61.6928 | 59.7656 | 0.13101 | -0.008469 | -0.007421 | -0.025017 | 0.013375 | 0.099318 | -0.12223 | 59.6187 | 59.6679 | 59.6737 | 59.6271 | 61.5514 | 61.6211 | 61.4176 | 61.5733 | 0.18136 | 0.041885 | 0.042933 | 0.025337 | 0.063729 | 0.14967 | -0.07188 | 59.6691 | 59.7183 | 59.724 | 59.6775 | 61.6018 | 61.6715 | 61.468 | 61.6236 | -1.9327 | -1.7989 | -1.8777 | -1.744
591.1562 | 121.7056 | -61.6516 | 59.8434 | 0.13101 | -0.008469 | -0.012 | -0.029595 | 0.004219 | 0.09474 | -0.12223 | 59.6233 | 59.6725 | 59.6782 | 59.6179 | 61.5377 | 61.6165 | 61.4176 | 61.5824 | 0.18136 | 0.041885 | 0.038354 | 0.020759 | 0.054573 | 0.14509 | -0.07188 | 59.6736 | 59.7229 | 59.7286 | 59.6683 | 61.588 | 61.6669 | 61.468 | 61.6328 | -1.9144 | -1.7943 | -1.8594 | -1.7394
592.9219 | 121.7148 | -61.6791 | 59.8068 | 0.13101 | -0.00389 | -0.007421 | -0.034174 | 0.013375 | 0.09474 | -0.12223 | 59.6233 | 59.6725 | 59.6782 | 59.6134 | 61.5377 | 61.6074 | 61.4085 | 61.5733 | 0.18136 | 0.046464 | 0.042933 | 0.01618 | 0.063729 | 0.14509 | -0.07188 | 59.6736 | 59.7229 | 59.7286 | 59.6637 | 61.588 | 61.6577 | 61.4588 | 61.6236 | -1.9144 | -1.7852 | -1.8594 | -1.7302
594.6719 | 121.6736 | -61.7294 | 59.7839 | 0.13101 | -0.008469 | -0.007421 | -0.025017 | 0.008797 | 0.09474 | -0.11765 | 59.6324 | 59.6771 | 59.6874 | 59.6317 | 61.5377 | 61.5982 | 61.4039 | 61.5687 | 0.18136 | 0.041885 | 0.042933 | 0.025337 | 0.059151 | 0.14509 | -0.067301 | 59.6828 | 59.7275 | 59.7378 | 59.682 | 61.588 | 61.6486 | 61.4543 | 61.619 | -1.9052 | -1.7715 | -1.8503 | -1.7165
596.3594 | 121.7194 | -61.7111 | 59.7702 | 0.13101 | -0.008469 | -0.007421 | -0.01586 | 0.008797 | 0.099318 | -0.11308 | 59.6416 | 59.6954 | 59.6966 | 59.6317 | 61.5331 | 61.6028 | 61.3993 | 61.5595 | 0.18136 | 0.041885 | 0.042933 | 0.034494 | 0.059151 | 0.14967 | -0.062723 | 59.692 | 59.7458 | 59.7469 | 59.682 | 61.5835 | 61.6531 | 61.4497 | 61.6099 | -1.8915 | -1.7577 | -1.8365 | -1.7028
598.1094 | 121.7697 | -61.647 | 59.7839 | 0.13101 | -0.008469 | -0.012 | -0.029595 | 0.008797 | 0.099318 | -0.11765 | 59.6416 | 59.6908 | 59.7011 | 59.6454 | 61.5239 | 61.5936 | 61.3993 | 61.5549 | 0.18136 | 0.041885 | 0.038354 | 0.020759 | 0.059151 | 0.14967 | -0.067301 | 59.692 | 59.7412 | 59.7515 | 59.6958 | 61.5743 | 61.644 | 61.4497 | 61.6053 | -1.8823 | -1.7577 | -1.8228 | -1.6982
599.8594 | 121.7514 | -61.6379 | 59.848 | 0.12185 | -0.013048 | -0.012 | -0.034174 | 0.013375 | 0.09474 | -0.12223 | 59.6508 | 59.7046 | 59.7011 | 59.65 | 61.5148 | 61.5891 | 61.3947 | 61.5504 | 0.1722 | 0.037306 | 0.038354 | 0.01618 | 0.063729 | 0.14509 | -0.07188 | 59.7011 | 59.7549 | 59.7515 | 59.7004 | 61.5651 | 61.6394 | 61.4451 | 61.6007 | -1.864 | -1.744 | -1.8137 | -1.6936
601.5625 | 121.8018 | -61.5372 | 59.8801 | 0.12643 | -0.013048 | -0.012 | -0.029595 | -0.000359 | 0.090161 | -0.13139 | 59.6599 | 59.7092 | 59.7195 | 59.6592 | 61.5102 | 61.5799 | 61.3856 | 61.5412 | 0.17678 | 0.037306 | 0.038354 | 0.020759 | 0.049995 | 0.14052 | -0.081036 | 59.7103 | 59.7595 | 59.7698 | 59.7095 | 61.5606 | 61.6302 | 61.4359 | 61.5916 | -1.8503 | -1.7257 | -1.7908 | -1.6661
603.3281 | 121.7148 | -61.6196 | 59.8709 | 0.12643 | -0.008469 | -0.012 | -0.029595 | 0.004219 | 0.09474 | -0.11765 | 59.6691 | 59.7137 | 59.724 | 59.6637 | 61.4965 | 61.5662 | 61.3764 | 61.5321 | 0.17678 | 0.041885 | 0.038354 | 0.020759 | 0.054573 | 0.14509 | -0.067301 | 59.7194 | 59.7641 | 59.7744 | 59.7141 | 61.5468 | 61.6165 | 61.4268 | 61.5824 | -1.8274 | -1.7074 | -1.7724 | -1.6524
605 | 121.756 | -61.6013 | 59.7794 | 0.12643 | -0.008469 | -0.012 | -0.034174 | -0.000359 | 0.090161 | -0.12223 | 59.6782 | 59.7275 | 59.7332 | 59.6683 | 61.4873 | 61.5662 | 61.3673 | 61.5275 | 0.17678 | 0.041885 | 0.038354 | 0.01618 | 0.049995 | 0.14052 | -0.07188 | 59.7286 | 59.7778 | 59.7835 | 59.7187 | 61.5377 | 61.6165 | 61.4176 | 61.5778 | -1.8091 | -1.689 | -1.7541 | -1.6341
606.75 | 121.6782 | -61.5692 | 59.9533 | 0.13101 | -0.017627 | -0.012 | -0.025017 | -0.000359 | 0.085583 | -0.12223 | 59.6737 | 59.7275 | 59.7378 | 59.6775 | 61.4873 | 61.5616 | 61.3581 | 61.5229 | 0.18136 | 0.032727 | 0.038354 | 0.025337 | 0.049995 | 0.13594 | -0.07188 | 59.724 | 59.7778 | 59.7881 | 59.7278 | 61.5377 | 61.6119 | 61.4085 | 61.5733 | -1.8137 | -1.6845 | -1.7496 | -1.6204
608.5 | 121.7697 | -61.6104 | 59.7977 | 0.12643 | -0.008469 | -0.007421 | -0.034174 | -0.000359 | 0.090161 | -0.12223 | 59.692 | 59.732 | 59.7469 | 59.6866 | 61.4782 | 61.5478 | 61.349 | 61.5137 | 0.17678 | 0.041885 | 0.042933 | 0.01618 | 0.049995 | 0.14052 | -0.07188 | 59.7423 | 59.7824 | 59.7973 | 59.737 | 61.5285 | 61.5982 | 61.3993 | 61.5641 | -1.7862 | -1.657 | -1.7312 | -1.602
610.2344 | 121.6919 | -61.5326 | 59.9854 | 0.12643 | -0.013048 | -0.016578 | -0.034174 | 0.004219 | 0.099318 | -0.11765 | 59.6874 | 59.7458 | 59.7469 | 59.6912 | 61.4736 | 61.5387 | 61.349 | 61.5092 | 0.17678 | 0.037306 | 0.033776 | 0.01618 | 0.054573 | 0.14967 | -0.067301 | 59.7377 | 59.7961 | 59.7973 | 59.7416 | 61.5239 | 61.589 | 61.3993 | 61.5595 | -1.7862 | -1.6616 | -1.7267 | -1.602
611.9219 | 121.7331 | -61.5005 | 59.9716 | 0.12643 | -0.013048 | -0.016578 | -0.025017 | 0.008797 | 0.085583 | -0.12223 | 59.6965 | 59.7458 | 59.7469 | 59.6912 | 61.469 | 61.5478 | 61.349 | 61.5 | 0.17678 | 0.037306 | 0.033776 | 0.025337 | 0.059151 | 0.13594 | -0.07188 | 59.7469 | 59.7961 | 59.7973 | 59.7416 | 61.5194 | 61.5982 | 61.3993 | 61.5504 | -1.7725 | -1.6524 | -1.7221 | -1.602
613.6562 | 121.6873 | -61.5143 | 59.9579 | 0.13101 | -0.013048 | -0.012 | -0.025017 | -0.000359 | 0.090161 | -0.11765 | 59.7057 | 59.7549 | 59.7607 | 59.7004 | 61.469 | 61.525 | 61.3306 | 61.5 | 0.18136 | 0.037306 | 0.038354 | 0.025337 | 0.049995 | 0.14052 | -0.067301 | 59.7561 | 59.8053 | 59.811 | 59.7507 | 61.5194 | 61.5753 | 61.381 | 61.5504 | -1.7633 | -1.6249 | -1.7084 | -1.57
615.3438 | 121.7468 | -61.5509 | 59.9167 | 0.13559 | -0.008469 | -0.021157 | -0.025017 | -0.004937 | 0.09474 | -0.12681 | 59.7103 | 59.7595 | 59.7652 | 59.7095 | 61.4553 | 61.5295 | 61.3261 | 61.4954 | 0.18594 | 0.041885 | 0.029197 | 0.025337 | 0.045417 | 0.14509 | -0.076458 | 59.7606 | 59.8099 | 59.8156 | 59.7599 | 61.5056 | 61.5799 | 61.3764 | 61.5458 | -1.745 | -1.6158 | -1.69 | -1.5608
617.0938 | 121.788 | -61.5829 | 59.8297 | 0.12643 | -0.008469 | -0.012 | -0.029595 | -0.000359 | 0.090161 | -0.12223 | 59.7103 | 59.7549 | 59.7652 | 59.7049 | 61.4599 | 61.525 | 61.3352 | 61.4954 | 0.17678 | 0.041885 | 0.038354 | 0.020759 | 0.049995 | 0.14052 | -0.07188 | 59.7606 | 59.8053 | 59.8156 | 59.7553 | 61.5102 | 61.5753 | 61.3856 | 61.5458 | -1.7496 | -1.6249 | -1.6946 | -1.57
618.7812 | 121.6644 | -61.5326 | 59.9716 | 0.14017 | -0.017627 | -0.007421 | -0.029595 | 0.004219 | 0.085583 | -0.12681 | 59.7149 | 59.7641 | 59.779 | 59.7187 | 61.4507 | 61.5204 | 61.3261 | 61.4771 | 0.19052 | 0.032727 | 0.042933 | 0.020759 | 0.054573 | 0.13594 | -0.076458 | 59.7652 | 59.8145 | 59.8293 | 59.769 | 61.501 | 61.5707 | 61.3764 | 61.5275 | -1.7358 | -1.6112 | -1.6717 | -1.5471
620.5312 | 121.6507 | -61.6241 | 59.9121 | 0.14017 | -0.008469 | -0.012 | -0.025017 | 0.008797 | 0.09474 | -0.11308 | 59.724 | 59.7733 | 59.7881 | 59.7187 | 61.4507 | 61.5066 | 61.3123 | 61.4771 | 0.19052 | 0.041885 | 0.038354 | 0.025337 | 0.059151 | 0.14509 | -0.062723 | 59.7744 | 59.8236 | 59.8385 | 59.769 | 61.501 | 61.557 | 61.3627 | 61.5275 | -1.7267 | -1.5883 | -1.6626 | -1.5242
622.2812 | 121.7789 | -61.4594 | 59.9487 | 0.12643 | -0.017627 | -0.016578 | -0.029595 | 0.004219 | 0.081005 | -0.12223 | 59.7286 | 59.7778 | 59.7927 | 59.7278 | 61.437 | 61.5112 | 61.3123 | 61.4771 | 0.17678 | 0.032727 | 0.033776 | 0.020759 | 0.054573 | 0.13136 | -0.07188 | 59.7789 | 59.8282 | 59.8431 | 59.7782 | 61.4873 | 61.5616 | 61.3627 | 61.5275 | -1.7084 | -1.5837 | -1.6443 | -1.5196
623.9688 | 121.7239 | -61.6058 | 59.8618 | 0.13101 | -0.013048 | -0.012 | -0.025017 | 0.004219 | 0.09474 | -0.12223 | 59.724 | 59.7778 | 59.7881 | 59.7187 | 61.4278 | 61.5066 | 61.3123 | 61.4725 | 0.18136 | 0.037306 | 0.038354 | 0.025337 | 0.054573 | 0.14509 | -0.07188 | 59.7744 | 59.8282 | 59.8385 | 59.769 | 61.4782 | 61.557 | 61.3627 | 61.5229 | -1.7038 | -1.5883 | -1.6397 | -1.5242
625.7188 | 121.788 | -61.4502 | 59.967 | 0.12643 | -0.017627 | -0.007421 | -0.025017 | 0.008797 | 0.090161 | -0.12681 | 59.7332 | 59.787 | 59.7973 | 59.737 | 61.4278 | 61.4975 | 61.3078 | 61.4634 | 0.17678 | 0.032727 | 0.042933 | 0.025337 | 0.059151 | 0.14052 | -0.076458 | 59.7835 | 59.8373 | 59.8476 | 59.7874 | 61.4782 | 61.5478 | 61.3581 | 61.5137 | -1.6946 | -1.5746 | -1.6305 | -1.5105
627.4844 | 121.6507 | -61.6013 | 59.9121 | 0.13101 | -0.00389 | -0.016578 | -0.025017 | 0.008797 | 0.09474 | -0.12681 | 59.7469 | 59.8007 | 59.8064 | 59.7462 | 61.4141 | 61.4838 | 61.294 | 61.4451 | 0.18136 | 0.046464 | 0.033776 | 0.025337 | 0.059151 | 0.14509 | -0.076458 | 59.7973 | 59.8511 | 59.8568 | 59.7965 | 61.4644 | 61.5341 | 61.3444 | 61.4954 | -1.6672 | -1.5471 | -1.6076 | -1.4876
629.1719 | 121.6736 | -61.496 | 60.0174 | 0.12643 | -0.013048 | -0.007421 | -0.029595 | -0.000359 | 0.085583 | -0.12223 | 59.7515 | 59.8053 | 59.8064 | 59.7507 | 61.4141 | 61.4883 | 61.2894 | 61.4496 | 0.17678 | 0.037306 | 0.042933 | 0.020759 | 0.049995 | 0.13594 | -0.07188 | 59.8018 | 59.8557 | 59.8568 | 59.8011 | 61.4644 | 61.5387 | 61.3398 | 61.5 | -1.6626 | -1.538 | -1.6076 | -1.483
630.9219 | 121.7697 | -61.528 | 59.8984 | 0.13101 | -0.013048 | -0.012 | -0.029595 | -0.000359 | 0.09474 | -0.12223 | 59.7606 | 59.7962 | 59.8064 | 59.7462 | 61.4095 | 61.4792 | 61.294 | 61.4451 | 0.18136 | 0.037306 | 0.038354 | 0.020759 | 0.049995 | 0.14509 | -0.07188 | 59.811 | 59.8465 | 59.8568 | 59.7965 | 61.4598 | 61.5295 | 61.3444 | 61.4954 | -1.6488 | -1.5334 | -1.6031 | -1.4876
632.6719 | 121.7834 | -61.4868 | 59.8938 | 0.13559 | -0.017627 | -0.012 | -0.029595 | -0.000359 | 0.085583 | -0.12223 | 59.7606 | 59.8099 | 59.8156 | 59.7553 | 61.4141 | 61.4746 | 61.2757 | 61.4405 | 0.18594 | 0.032727 | 0.038354 | 0.020759 | 0.049995 | 0.13594 | -0.07188 | 59.811 | 59.8602 | 59.8659 | 59.8057 | 61.4644 | 61.525 | 61.3261 | 61.4908 | -1.6534 | -1.5151 | -1.5985 | -1.4601
634.3594 | 121.7056 | -61.5967 | 59.8984 | 0.12643 | -0.013048 | -0.012 | -0.029595 | 0.004219 | 0.09474 | -0.12223 | 59.7652 | 59.8145 | 59.8156 | 59.7599 | 61.4049 | 61.4838 | 61.2803 | 61.4405 | 0.17678 | 0.037306 | 0.038354 | 0.020759 | 0.054573 | 0.14509 | -0.07188 | 59.8156 | 59.8648 | 59.8659 | 59.8103 | 61.4553 | 61.5341 | 61.3306 | 61.4908 | -1.6397 | -1.5151 | -1.5893 | -1.4647
636.1094 | 121.7743 | -61.4319 | 59.9808 | 0.12185 | -0.013048 | -0.012 | -0.020438 | -0.000359 | 0.09474 | -0.11765 | 59.7515 | 59.8053 | 59.8156 | 59.7507 | 61.4095 | 61.4883 | 61.2803 | 61.4405 | 0.1722 | 0.037306 | 0.038354 | 0.029916 | 0.049995 | 0.14509 | -0.067301 | 59.8018 | 59.8557 | 59.8659 | 59.8011 | 61.4598 | 61.5387 | 61.3306 | 61.4908 | -1.658 | -1.5288 | -1.5939 | -1.4647
637.8594 | 121.7194 | -61.5784 | 59.8892 | 0.13101 | -0.013048 | -0.012 | -0.025017 | 0.017953 | 0.09474 | -0.12681 | 59.7744 | 59.8328 | 59.8248 | 59.7691 | 61.4049 | 61.4654 | 61.2711 | 61.4313 | 0.18136 | 0.037306 | 0.038354 | 0.025337 | 0.068307 | 0.14509 | -0.076458 | 59.8247 | 59.8831 | 59.8751 | 59.8194 | 61.4553 | 61.5158 | 61.3215 | 61.4817 | -1.6305 | -1.4967 | -1.5802 | -1.4464
639.5469 | 121.6599 | -61.4594 | 60.054 | 0.13101 | -0.013048 | -0.016578 | -0.034174 | 0.008797 | 0.085583 | -0.12223 | 59.779 | 59.8374 | 59.8385 | 59.7874 | 61.382 | 61.4517 | 61.2574 | 61.413 | 0.18136 | 0.037306 | 0.033776 | 0.01618 | 0.059151 | 0.13594 | -0.07188 | 59.8293 | 59.8877 | 59.8888 | 59.8377 | 61.4324 | 61.5021 | 61.3077 | 61.4634 | -1.6031 | -1.4784 | -1.5435 | -1.4189
641.3125 | 121.6644 | -61.441 | 60.0677 | 0.13101 | -0.008469 | -0.012 | -0.020438 | 0.008797 | 0.090161 | -0.12681 | 59.7881 | 59.8374 | 59.8476 | 59.7874 | 61.3774 | 61.4426 | 61.2482 | 61.4084 | 0.18136 | 0.041885 | 0.038354 | 0.029916 | 0.059151 | 0.14052 | -0.076458 | 59.8385 | 59.8877 | 59.898 | 59.8377 | 61.4278 | 61.4929 | 61.2986 | 61.4588 | -1.5893 | -1.4601 | -1.5298 | -1.4006
643.0625 | 121.669 | -61.5738 | 59.9396 | 0.12643 | -0.00389 | -0.012 | -0.025017 | 0.008797 | 0.09474 | -0.12223 | 59.7835 | 59.8328 | 59.8431 | 59.7874 | 61.382 | 61.4517 | 61.2437 | 61.4084 | 0.17678 | 0.046464 | 0.038354 | 0.025337 | 0.059151 | 0.14509 | -0.07188 | 59.8339 | 59.8831 | 59.8934 | 59.8377 | 61.4324 | 61.5021 | 61.294 | 61.4588 | -1.5985 | -1.4601 | -1.539 | -1.4006
644.7344 | 121.788 | -61.3861 | 60.0174 | 0.12643 | -0.013048 | -0.021157 | -0.025017 | -0.000359 | 0.085583 | -0.12681 | 59.7835 | 59.8328 | 59.8431 | 59.7874 | 61.382 | 61.4471 | 61.2528 | 61.4084 | 0.17678 | 0.037306 | 0.029197 | 0.025337 | 0.049995 | 0.13594 | -0.076458 | 59.8339 | 59.8831 | 59.8934 | 59.8377 | 61.4324 | 61.4975 | 61.3032 | 61.4588 | -1.5985 | -1.4693 | -1.539 | -1.4098
646.5 | 121.7514 | -61.4594 | 59.9396 | 0.11727 | -0.013048 | -0.016578 | -0.029595 | -0.000359 | 0.090161 | -0.13139 | 59.7973 | 59.8465 | 59.8476 | 59.7874 | 61.3729 | 61.4426 | 61.2437 | 61.4039 | 0.16763 | 0.037306 | 0.033776 | 0.020759 | 0.049995 | 0.14052 | -0.081036 | 59.8476 | 59.8969 | 59.898 | 59.8377 | 61.4232 | 61.4929 | 61.294 | 61.4542 | -1.5756 | -1.4464 | -1.5252 | -1.396
648.1875 | 121.669 | -61.4273 | 60.1089 | 0.13101 | -0.013048 | -0.016578 | -0.029595 | 0.008797 | 0.09474 | -0.11765 | 59.8019 | 59.8511 | 59.8614 | 59.8011 | 61.3637 | 61.4334 | 61.2345 | 61.3901 | 0.18136 | 0.037306 | 0.033776 | 0.020759 | 0.059151 | 0.14509 | -0.067301 | 59.8522 | 59.9015 | 59.9117 | 59.8515 | 61.4141 | 61.4838 | 61.2849 | 61.4405 | -1.5619 | -1.4327 | -1.5023 | -1.3731
649.9375 | 121.6324 | -61.5417 | 59.9762 | 0.14017 | -0.008469 | -0.012 | -0.029595 | 0.008797 | 0.09474 | -0.12223 | 59.7973 | 59.8465 | 59.8614 | 59.8011 | 61.3683 | 61.4242 | 61.2391 | 61.4084 | 0.19052 | 0.041885 | 0.038354 | 0.020759 | 0.059151 | 0.14509 | -0.07188 | 59.8476 | 59.8969 | 59.9117 | 59.8515 | 61.4186 | 61.4746 | 61.2894 | 61.4588 | -1.571 | -1.4418 | -1.5069 | -1.3777
652.1094 | 121.788 | -61.4639 | 59.9304 | 0.13101 | -0.00389 | -0.016578 | -0.025017 | 0.004219 | 0.09474 | -0.12223 | 59.811 | 59.8648 | 59.8705 | 59.8057 | 61.3546 | 61.4334 | 61.2437 | 61.3901 | 0.18136 | 0.046464 | 0.033776 | 0.025337 | 0.054573 | 0.14509 | -0.07188 | 59.8614 | 59.9152 | 59.9209 | 59.856 | 61.4049 | 61.4838 | 61.294 | 61.4405 | -1.5435 | -1.4327 | -1.484 | -1.3731
654 | 121.6644 | -61.4456 | 60.054 | 0.12643 | -0.013048 | -0.012 | -0.029595 | 0.008797 | 0.09474 | -0.12681 | 59.811 | 59.8465 | 59.8614 | 59.8103 | 61.3546 | 61.4288 | 61.2391 | 61.3901 | 0.17678 | 0.037306 | 0.038354 | 0.020759 | 0.059151 | 0.14509 | -0.076458 | 59.8614 | 59.8969 | 59.9117 | 59.8606 | 61.4049 | 61.4792 | 61.2894 | 61.4405 | -1.5435 | -1.4281 | -1.4932 | -1.3777
655.7031 | 121.7972 | -61.377 | 60.0311 | 0.12643 | -0.008469 | -0.016578 | -0.029595 | -0.000359 | 0.085583 | -0.12681 | 59.8247 | 59.874 | 59.8705 | 59.8194 | 61.3454 | 61.4197 | 61.2208 | 61.381 | 0.17678 | 0.041885 | 0.033776 | 0.020759 | 0.049995 | 0.13594 | -0.076458 | 59.8751 | 59.9243 | 59.9209 | 59.8698 | 61.3958 | 61.47 | 61.2711 | 61.4313 | -1.5207 | -1.396 | -1.4749 | -1.3502
657.4062 | 121.7606 | -61.4639 | 59.9167 | 0.13101 | -0.008469 | -0.016578 | -0.020438 | 0.004219 | 0.09474 | -0.12223 | 59.8247 | 59.8786 | 59.8843 | 59.8286 | 61.3408 | 61.4105 | 61.2116 | 61.3718 | 0.18136 | 0.041885 | 0.033776 | 0.029916 | 0.054573 | 0.14509 | -0.07188 | 59.8751 | 59.9289 | 59.9346 | 59.8789 | 61.3912 | 61.4609 | 61.262 | 61.4222 | -1.5161 | -1.3869 | -1.4566 | -1.3273
659.2344 | 121.8201 | -61.3541 | 60.1135 | 0.12643 | -0.017627 | -0.016578 | -0.029595 | 0.004219 | 0.090161 | -0.12223 | 59.8339 | 59.8831 | 59.8934 | 59.8423 | 61.3408 | 61.4059 | 61.2025 | 61.3581 | 0.17678 | 0.032727 | 0.033776 | 0.020759 | 0.054573 | 0.14052 | -0.07188 | 59.8843 | 59.9335 | 59.9438 | 59.8927 | 61.3912 | 61.4563 | 61.2528 | 61.4084 | -1.5069 | -1.3686 | -1.4474 | -1.309
660.9688 | 121.6782 | -61.3724 | 60.0906 | 0.12643 | -0.013048 | -0.007421 | -0.029595 | 0.008797 | 0.09474 | -0.11765 | 59.8293 | 59.874 | 59.8934 | 59.8332 | 61.3225 | 61.4014 | 61.2025 | 61.3627 | 0.17678 | 0.037306 | 0.042933 | 0.020759 | 0.059151 | 0.14509 | -0.067301 | 59.8797 | 59.9243 | 59.9438 | 59.8835 | 61.3729 | 61.4517 | 61.2528 | 61.413 | -1.4932 | -1.3731 | -1.4291 | -1.309
662.6562 | 121.788 | -61.4319 | 59.967 | 0.12185 | -0.00389 | -0.016578 | -0.025017 | 0.017953 | 0.099318 | -0.12681 | 59.8431 | 59.8831 | 59.8934 | 59.8377 | 61.3271 | 61.3922 | 61.2025 | 61.3489 | 0.1722 | 0.046464 | 0.033776 | 0.025337 | 0.068307 | 0.14967 | -0.076458 | 59.8934 | 59.9335 | 59.9438 | 59.8881 | 61.3774 | 61.4425 | 61.2528 | 61.3993 | -1.484 | -1.3594 | -1.4337 | -1.309
664.3594 | 121.7056 | -61.4502 | 60.0174 | 0.13101 | -0.00389 | -0.012 | -0.020438 | 0.008797 | 0.099318 | -0.11765 | 59.8614 | 59.9015 | 59.9117 | 59.8561 | 61.3133 | 61.383 | 61.1841 | 61.3443 | 0.18136 | 0.046464 | 0.038354 | 0.029916 | 0.059151 | 0.14967 | -0.067301 | 59.9117 | 59.9518 | 59.9621 | 59.9064 | 61.3637 | 61.4334 | 61.2345 | 61.3947 | -1.452 | -1.3228 | -1.4016 | -1.2724
666.1094 | 121.7377 | -61.3815 | 60.0494 | 0.13101 | -0.008469 | -0.016578 | -0.034174 | -0.000359 | 0.085583 | -0.12681 | 59.8568 | 59.906 | 59.9117 | 59.8561 | 61.3042 | 61.383 | 61.1887 | 61.3443 | 0.18136 | 0.041885 | 0.033776 | 0.01618 | 0.049995 | 0.13594 | -0.076458 | 59.9071 | 59.9564 | 59.9621 | 59.9064 | 61.3545 | 61.4334 | 61.2391 | 61.3947 | -1.4474 | -1.3319 | -1.3925 | -1.277
667.8125 | 121.7834 | -61.3358 | 60.0952 | 0.13101 | 0.000689 | -0.016578 | -0.025017 | 0.004219 | 0.090161 | -0.11765 | 59.8522 | 59.9106 | 59.9072 | 59.8652 | 61.3133 | 61.3785 | 61.1841 | 61.3489 | 0.18136 | 0.051043 | 0.033776 | 0.025337 | 0.054573 | 0.14052 | -0.067301 | 59.9026 | 59.961 | 59.9575 | 59.9156 | 61.3637 | 61.4288 | 61.2345 | 61.3993 | -1.4611 | -1.3319 | -1.4062 | -1.277
669.5156 | 121.7148 | -61.3861 | 60.0677 | 0.13559 | -0.008469 | -0.016578 | -0.020438 | 0.004219 | 0.085583 | -0.12223 | 59.8888 | 59.9335 | 59.9438 | 59.8881 | 61.2721 | 61.3464 | 61.1475 | 61.3123 | 0.18594 | 0.041885 | 0.033776 | 0.029916 | 0.054573 | 0.13594 | -0.07188 | 59.9392 | 59.9839 | 59.9941 | 59.9385 | 61.3225 | 61.3968 | 61.1979 | 61.3627 | -1.3833 | -1.2587 | -1.3284 | -1.2037
671.2031 | 121.6553 | -61.3861 | 60.141 | 0.13101 | -0.008469 | -0.007421 | -0.025017 | 0.004219 | 0.090161 | -0.11765 | 59.8934 | 59.9381 | 59.9392 | 59.8881 | 61.2813 | 61.351 | 61.1475 | 61.3077 | 0.18136 | 0.041885 | 0.042933 | 0.025337 | 0.054573 | 0.14052 | -0.067301 | 59.9438 | 59.9884 | 59.9896 | 59.9385 | 61.3317 | 61.4013 | 61.1979 | 61.3581 | -1.3879 | -1.2541 | -1.3421 | -1.2083
672.9375 | 121.7148 | -61.3678 | 60.0998 | 0.13101 | 0.000689 | -0.021157 | -0.034174 | -0.000359 | 0.090161 | -0.12223 | 59.9346 | 59.9885 | 59.9941 | 59.9339 | 61.2401 | 61.3006 | 61.1109 | 61.2619 | 0.18136 | 0.051043 | 0.029197 | 0.01618 | 0.049995 | 0.14052 | -0.07188 | 59.985 | 60.0388 | 60.0445 | 59.9843 | 61.2905 | 61.351 | 61.1612 | 61.3123 | -1.3055 | -1.1763 | -1.246 | -1.1167
674.625 | 121.7697 | -61.3632 | 60.0494 | 0.12643 | -0.008469 | -0.016578 | -0.025017 | 0.004219 | 0.090161 | -0.12681 | 59.9163 | 59.9656 | 59.9758 | 59.9202 | 61.2584 | 61.3189 | 61.1246 | 61.2803 | 0.17678 | 0.041885 | 0.033776 | 0.025337 | 0.054573 | 0.14052 | -0.076458 | 59.9667 | 60.0159 | 60.0262 | 59.9705 | 61.3088 | 61.3693 | 61.175 | 61.3306 | -1.3421 | -1.2083 | -1.2826 | -1.1488
676.3438 | 121.7789 | -61.377 | 60.0266 | 0.13101 | -0.00389 | -0.012 | -0.029595 | 0.004219 | 0.09474 | -0.12223 | 59.9163 | 59.9656 | 59.9758 | 59.9202 | 61.2538 | 61.3235 | 61.12 | 61.2848 | 0.18136 | 0.046464 | 0.038354 | 0.020759 | 0.054573 | 0.14509 | -0.07188 | 59.9667 | 60.0159 | 60.0262 | 59.9705 | 61.3042 | 61.3739 | 61.1704 | 61.3352 | -1.3375 | -1.2037 | -1.278 | -1.1442
678.0312 | 121.7972 | -61.2442 | 60.1547 | 0.12643 | -0.008469 | -0.012 | -0.020438 | 0.008797 | 0.09474 | -0.11765 | 59.9438 | 60.0022 | 60.0033 | 59.9476 | 61.2172 | 61.2823 | 61.0971 | 61.2482 | 0.17678 | 0.041885 | 0.038354 | 0.029916 | 0.059151 | 0.14509 | -0.067301 | 59.9941 | 60.0526 | 60.0537 | 59.998 | 61.2676 | 61.3327 | 61.1475 | 61.2986 | -1.2734 | -1.1534 | -1.2139 | -1.0938
679.7188 | 121.6507 | -61.3998 | 60.0723 | 0.12643 | 0.000689 | -0.012 | -0.025017 | 0.008797 | 0.09474 | -0.12223 | 59.93 | 59.9747 | 59.985 | 59.9293 | 61.2355 | 61.3144 | 61.1063 | 61.2619 | 0.17678 | 0.051043 | 0.038354 | 0.025337 | 0.059151 | 0.14509 | -0.07188 | 59.9804 | 60.0251 | 60.0353 | 59.9797 | 61.2859 | 61.3647 | 61.1567 | 61.3123 | -1.3055 | -1.1763 | -1.2505 | -1.1213
681.4531 | 121.6873 | -61.2854 | 60.2097 | 0.12643 | -0.00389 | -0.016578 | -0.034174 | -0.000359 | 0.090161 | -0.12223 | 59.9438 | 59.9976 | 59.9987 | 59.9476 | 61.2172 | 61.2869 | 61.0926 | 61.2436 | 0.17678 | 0.046464 | 0.033776 | 0.01618 | 0.049995 | 0.14052 | -0.07188 | 59.9941 | 60.048 | 60.0491 | 59.998 | 61.2676 | 61.3373 | 61.1429 | 61.294 | -1.2734 | -1.1488 | -1.2185 | -1.0938
683.2031 | 121.701 | -61.3266 | 60.1776 | 0.13101 | -0.008469 | -0.007421 | -0.025017 | 0.004219 | 0.09474 | -0.1085 | 59.9575 | 60.0068 | 60.017 | 59.9614 | 61.2126 | 61.2777 | 61.0788 | 61.2436 | 0.18136 | 0.041885 | 0.042933 | 0.025337 | 0.054573 | 0.14509 | -0.058145 | 60.0079 | 60.0571 | 60.0674 | 60.0117 | 61.263 | 61.3281 | 61.1292 | 61.294 | -1.2551 | -1.1213 | -1.1956 | -1.0618
684.9688 | 121.7834 | -61.2213 | 60.1959 | 0.13101 | -0.013048 | -0.012 | -0.025017 | 0.004219 | 0.090161 | -0.13139 | 59.9575 | 60.0114 | 60.0216 | 59.9476 | 61.2081 | 61.2777 | 61.0743 | 61.2345 | 0.18136 | 0.037306 | 0.038354 | 0.025337 | 0.054573 | 0.14052 | -0.081036 | 60.0079 | 60.0617 | 60.072 | 59.998 | 61.2584 | 61.3281 | 61.1246 | 61.2848 | -1.2505 | -1.1167 | -1.1864 | -1.0526
686.7188 | 121.6736 | -61.4319 | 60.0677 | 0.12643 | -0.008469 | -0.012 | -0.025017 | 0.004219 | 0.090161 | -0.12223 | 59.9346 | 59.993 | 59.9987 | 59.9339 | 61.2355 | 61.2961 | 61.0971 | 61.2574 | 0.17678 | 0.041885 | 0.038354 | 0.025337 | 0.054573 | 0.14052 | -0.07188 | 59.985 | 60.0434 | 60.0491 | 59.9843 | 61.2859 | 61.3464 | 61.1475 | 61.3077 | -1.3009 | -1.1625 | -1.2368 | -1.0984
688.4688 | 121.6736 | -61.4136 | 60.0769 | 0.12643 | -0.008469 | -0.016578 | -0.025017 | 0.004219 | 0.099318 | -0.11308 | 59.9575 | 60.0114 | 60.017 | 59.9522 | 61.2126 | 61.2732 | 61.0834 | 61.2345 | 0.17678 | 0.041885 | 0.033776 | 0.025337 | 0.054573 | 0.14967 | -0.062723 | 60.0079 | 60.0617 | 60.0674 | 60.0026 | 61.263 | 61.3235 | 61.1338 | 61.2848 | -1.2551 | -1.1259 | -1.1956 | -1.0664
690.2344 | 121.7972 | -61.171 | 60.2554 | 0.13101 | -0.00389 | -0.016578 | -0.025017 | 0.008797 | 0.099318 | -0.12223 | 60.104 | 60.1441 | 60.1498 | 60.0896 | 61.0753 | 61.1358 | 60.9415 | 61.1017 | 0.18136 | 0.046464 | 0.033776 | 0.025337 | 0.059151 | 0.14967 | -0.07188 | 60.1544 | 60.1945 | 60.2002 | 60.1399 | 61.1256 | 61.1862 | 60.9918 | 61.1521 | -0.97125 | -0.83745 | -0.92548 | -0.79168
691.9844 | 121.6782 | -61.0336 | 60.4843 | 0.13101 | -0.00389 | -0.012 | -0.025017 | 0.008797 | 0.085583 | -0.12681 | 60.2368 | 60.2861 | 60.2963 | 60.2315 | 60.9288 | 61.0031 | 60.8087 | 60.9552 | 0.18136 | 0.046464 | 0.038354 | 0.025337 | 0.059151 | 0.13594 | -0.076458 | 60.2872 | 60.3364 | 60.3467 | 60.2819 | 60.9791 | 61.0534 | 60.8591 | 61.0056 | -0.69198 | -0.57191 | -0.63247 | -0.5124
693.7344 | 121.6644 | -61.1023 | 60.3882 | 0.13101 | -0.008469 | -0.007421 | -0.01586 | 0.008797 | 0.090161 | -0.11765 | 60.2505 | 60.2952 | 60.3055 | 60.2499 | 60.915 | 60.9893 | 60.7904 | 60.946 | 0.18136 | 0.041885 | 0.042933 | 0.034494 | 0.059151 | 0.14052 | -0.067301 | 60.3009 | 60.3456 | 60.3558 | 60.3002 | 60.9654 | 61.0397 | 60.8408 | 60.9964 | -0.66451 | -0.53986 | -0.60958 | -0.48493
695.4219 | 121.788 | -60.965 | 60.4752 | 0.13101 | -0.00389 | -0.012 | -0.029595 | -0.000359 | 0.090161 | -0.13139 | 60.246 | 60.2998 | 60.3055 | 60.2499 | 60.9196 | 60.9847 | 60.7904 | 60.946 | 0.18136 | 0.046464 | 0.038354 | 0.020759 | 0.049995 | 0.14052 | -0.081036 | 60.2963 | 60.3502 | 60.3558 | 60.3002 | 60.97 | 61.0351 | 60.8408 | 60.9964 | -0.67366 | -0.54443 | -0.61416 | -0.48493
697.1719 | 121.7514 | -61.0794 | 60.3882 | 0.13101 | -0.00389 | -0.021157 | -0.025017 | 0.008797 | 0.090161 | -0.12223 | 60.2276 | 60.2815 | 60.2872 | 60.2315 | 60.9334 | 61.0076 | 60.8133 | 60.9644 | 0.18136 | 0.046464 | 0.029197 | 0.025337 | 0.059151 | 0.14052 | -0.07188 | 60.278 | 60.3319 | 60.3375 | 60.2819 | 60.9837 | 61.058 | 60.8636 | 61.0147 | -0.70571 | -0.58564 | -0.6462 | -0.52613
698.9219 | 121.6553 | -61.0519 | 60.4706 | 0.13101 | -0.00389 | -0.016578 | -0.020438 | 0.004219 | 0.090161 | -0.12223 | 60.1956 | 60.2449 | 60.2551 | 60.1857 | 60.9791 | 61.0397 | 60.8408 | 61.0056 | 0.18136 | 0.046464 | 0.033776 | 0.029916 | 0.054573 | 0.14052 | -0.07188 | 60.246 | 60.2952 | 60.3055 | 60.2361 | 61.0295 | 61.09 | 60.8911 | 61.0559 | -0.78354 | -0.64516 | -0.72403 | -0.58565
700.6094 | 121.7377 | -61.116 | 60.3012 | 0.12643 | -0.008469 | -0.012 | -0.029595 | -0.004937 | 0.090161 | -0.12223 | 60.1223 | 60.1762 | 60.1819 | 60.1216 | 61.0387 | 61.1084 | 60.914 | 61.0697 | 0.17678 | 0.041885 | 0.038354 | 0.020759 | 0.045417 | 0.14052 | -0.07188 | 60.1727 | 60.2265 | 60.2322 | 60.172 | 61.089 | 61.1587 | 60.9644 | 61.12 | -0.91631 | -0.79167 | -0.8568 | -0.73216
702.3906 | 121.788 | -61.1618 | 60.2646 | 0.13101 | 0.000689 | -0.012 | -0.025017 | 0.008797 | 0.09474 | -0.11308 | 60.1498 | 60.1991 | 60.2093 | 60.1445 | 61.0158 | 61.09 | 60.8865 | 61.0513 | 0.18136 | 0.051043 | 0.038354 | 0.025337 | 0.059151 | 0.14509 | -0.062723 | 60.2002 | 60.2494 | 60.2597 | 60.1949 | 61.0661 | 61.1404 | 60.9369 | 61.1017 | -0.86595 | -0.73673 | -0.80644 | -0.67722
704.0781 | 121.6507 | -61.0886 | 60.3836 | 0.13101 | -0.00389 | -0.012 | -0.020438 | 0.004219 | 0.09474 | -0.11765 | 60.2231 | 60.2678 | 60.2734 | 60.2132 | 60.9517 | 61.0122 | 60.8133 | 60.9827 | 0.18136 | 0.046464 | 0.038354 | 0.029916 | 0.054573 | 0.14509 | -0.067301 | 60.2734 | 60.3181 | 60.3238 | 60.2636 | 61.002 | 61.0626 | 60.8636 | 61.033 | -0.7286 | -0.59022 | -0.67825 | -0.53987
705.8125 | 121.6736 | -61.0657 | 60.4156 | 0.12643 | -0.00389 | -0.012 | -0.020438 | 0.008797 | 0.090161 | -0.12223 | 60.278 | 60.3365 | 60.3421 | 60.2819 | 60.883 | 60.9527 | 60.7584 | 60.9277 | 0.17678 | 0.046464 | 0.038354 | 0.029916 | 0.059151 | 0.14052 | -0.07188 | 60.3284 | 60.3868 | 60.3924 | 60.3323 | 60.9334 | 61.0031 | 60.8087 | 60.9781 | -0.60499 | -0.48034 | -0.54091 | -0.41625
707.5625 | 121.6507 | -60.8826 | 60.6308 | 0.12185 | -0.00389 | -0.012 | -0.025017 | 0.013375 | 0.085583 | -0.12681 | 60.365 | 60.4234 | 60.4153 | 60.3598 | 60.8098 | 60.8703 | 60.6714 | 60.8316 | 0.1722 | 0.046464 | 0.038354 | 0.025337 | 0.063729 | 0.13594 | -0.076458 | 60.4154 | 60.4738 | 60.4657 | 60.4101 | 60.8601 | 60.9206 | 60.7217 | 60.8819 | -0.44475 | -0.30636 | -0.3944 | -0.25601
709.25 | 121.7651 | -60.7452 | 60.6308 | 0.13101 | -0.008469 | -0.016578 | -0.025017 | 0.008797 | 0.085583 | -0.12681 | 60.8183 | 60.8539 | 60.8778 | 60.8085 | 60.3519 | 60.4171 | 60.2501 | 60.3784 | 0.18136 | 0.041885 | 0.033776 | 0.025337 | 0.059151 | 0.13594 | -0.076458 | 60.8686 | 60.9042 | 60.9281 | 60.8588 | 60.4023 | 60.4674 | 60.3005 | 60.4287 | 0.46634 | 0.56813 | 0.52582 | 0.62761
711 | 121.6827 | -6.7383 | 114.917 | 0.13101 | 0.005267 | -0.002842 | -0.020438 | 0.013375 | 0.099318 | -0.12681 | 109.4282 | 109.7053 | 109.348 | 109.3554 | 11.1274 | 11.4272 | 11.3987 | 11.4514 | 0.18136 | 0.055621 | 0.047512 | 0.029916 | 0.063729 | 0.14967 | -0.076458 | 109.4785 | 109.7556 | 109.3984 | 109.4057 | 11.1778 | 11.4775 | 11.4491 | 11.5018 | 98.3007 | 98.0294 | 98.2206 | 97.9493
712.7656 | 121.6141 | -5.603 | 116.1209 | 0.13101 | -0.013048 | -0.012 | -0.025017 | 0.008797 | 0.090161 | -0.12681 | 115.7511 | 115.7813 | 115.7622 | 115.6699 | 5.3406 | 5.5032 | 5.4789 | 5.5273 | 0.18136 | 0.037306 | 0.038354 | 0.025337 | 0.059151 | 0.14052 | -0.076458 | 115.8014 | 115.8317 | 115.8125 | 115.7202 | 5.391 | 5.5535 | 5.5292 | 5.5776 | 110.4105 | 110.2722 | 110.4216 | 110.2833
714.4688 | 121.6553 | -5.0079 | 116.6702 | 0.13559 | -0.00389 | -0.012 | -0.020438 | 0.008797 | 0.085583 | -0.1085 | 116.3692 | 116.3949 | 116.3757 | 116.288 | 4.7271 | 4.8897 | 4.87 | 4.9138 | 0.18594 | 0.046464 | 0.038354 | 0.029916 | 0.059151 | 0.13594 | -0.058145 | 116.4195 | 116.4453 | 116.426 | 116.3384 | 4.7775 | 4.9401 | 4.9203 | 4.9641 | 111.642 | 111.4992 | 111.6485 | 111.5057
716.2344 | 121.7422 | -4.9438 | 116.6565 | 0.11727 | 0.000689 | -0.021157 | -0.034174 | 0.004219 | 0.085583 | -0.12681 | 116.5111 | 116.5414 | 116.5268 | 116.43 | 4.5852 | 4.7432 | 4.7189 | 4.7627 | 0.16763 | 0.051043 | 0.029197 | 0.01618 | 0.054573 | 0.13594 | -0.076458 | 116.5614 | 116.5918 | 116.5771 | 116.4804 | 4.6356 | 4.7936 | 4.7692 | 4.8131 | 111.9259 | 111.7922 | 111.9415 | 111.8079
717.9844 | 121.7422 | -5.2597 | 116.3406 | 0.12643 | 0.000689 | -0.021157 | -0.020438 | 0.008797 | 0.09474 | -0.12223 | 116.0075 | 116.0469 | 116.014 | 115.9263 | 5.1804 | 5.2514 | 5.2225 | 5.3121 | 0.17678 | 0.051043 | 0.029197 | 0.029916 | 0.059151 | 0.14509 | -0.07188 | 116.0578 | 116.0973 | 116.0643 | 115.9767 | 5.2307 | 5.3017 | 5.2729 | 5.3624 | 110.8271 | 110.785 | 110.8336 | 110.7915
719.6719 | 121.6324 | -4.2618 | 117.4438 | 0.12185 | -0.008469 | -0.016578 | -0.025017 | 0.004219 | 0.090161 | -0.11765 | 117.1658 | 117.1962 | 117.1723 | 117.0756 | 4.0267 | 4.0977 | 4.0871 | 4.163 | 0.1722 | 0.041885 | 0.033776 | 0.025337 | 0.054573 | 0.14052 | -0.067301 | 117.2162 | 117.2466 | 117.2226 | 117.126 | 4.077 | 4.1481 | 4.1374 | 4.2133 | 113.1391 | 113.0788 | 113.1456 | 113.0852
721.4375 | 121.6644 | -4.3854 | 117.2562 | 0.13101 | -0.008469 | -0.012 | -0.020438 | 0.013375 | 0.090161 | -0.12681 | 116.9415 | 116.9581 | 116.9388 | 116.8513 | 4.2556 | 4.3312 | 4.316 | 4.3919 | 0.18136 | 0.041885 | 0.038354 | 0.029916 | 0.063729 | 0.14052 | -0.076458 | 116.9918 | 117.0085 | 116.9892 | 116.9016 | 4.3059 | 4.3815 | 4.3663 | 4.4422 | 112.6859 | 112.6255 | 112.6832 | 112.6228
723.1875 | 121.7422 | -4.0329 | 117.5491 | 0.12643 | -0.00389 | -0.016578 | -0.025017 | -0.000359 | 0.085583 | -0.12223 | 117.3535 | 117.3794 | 117.36 | 117.2725 | 3.8298 | 3.91 | 3.8948 | 3.9753 | 0.17678 | 0.046464 | 0.033776 | 0.025337 | 0.049995 | 0.13594 | -0.07188 | 117.4039 | 117.4297 | 117.4104 | 117.3229 | 3.8802 | 3.9604 | 3.9451 | 4.0256 | 113.5237 | 113.4588 | 113.5302 | 113.4652
724.9375 | 121.6415 | -4.747 | 116.9128 | 0.13101 | -0.00389 | -0.012 | -0.025017 | 0.008797 | 0.090161 | -0.12223 | 116.7217 | 116.7429 | 116.7328 | 116.6452 | 4.4753 | 4.5418 | 4.522 | 4.6162 | 0.18136 | 0.046464 | 0.038354 | 0.025337 | 0.059151 | 0.14052 | -0.07188 | 116.7721 | 116.7933 | 116.7831 | 116.6956 | 4.5257 | 4.5921 | 4.5724 | 4.6666 | 112.2464 | 112.1997 | 112.2574 | 112.2108
726.6875 | 121.7102 | -4.6326 | 116.9769 | 0.13101 | -0.00389 | -0.016578 | -0.034174 | 0.004219 | 0.081005 | -0.12681 | 116.8453 | 116.8757 | 116.8564 | 116.7643 | 4.338 | 4.4227 | 4.3984 | 4.4789 | 0.18136 | 0.046464 | 0.033776 | 0.01618 | 0.054573 | 0.13136 | -0.076458 | 116.8957 | 116.926 | 116.9067 | 116.8146 | 4.3883 | 4.4731 | 4.4487 | 4.5292 | 112.5073 | 112.4469 | 112.5184 | 112.458
728.375 | 121.6461 | -4.7287 | 116.9083 | 0.13101 | -0.008469 | -0.021157 | -0.025017 | 0.004219 | 0.09474 | -0.11765 | 116.7904 | 116.8207 | 116.7969 | 116.7047 | 4.4067 | 4.4731 | 4.4579 | 4.5384 | 0.18136 | 0.041885 | 0.029197 | 0.025337 | 0.054573 | 0.14509 | -0.067301 | 116.8407 | 116.8711 | 116.8472 | 116.7551 | 4.457 | 4.5235 | 4.5083 | 4.5887 | 112.3837 | 112.3325 | 112.3902 | 112.339
730.125 | 121.6461 | -4.2068 | 117.4438 | 0.12643 | 0.000689 | -0.012 | -0.01586 | 0.004219 | 0.081005 | -0.11308 | 117.0651 | 117.0955 | 117.0716 | 116.9795 | 4.1182 | 4.1984 | 4.1832 | 4.2683 | 0.17678 | 0.051043 | 0.038354 | 0.034494 | 0.054573 | 0.13136 | -0.062723 | 117.1154 | 117.1458 | 117.1219 | 117.0298 | 4.1686 | 4.2488 | 4.2336 | 4.3186 | 112.9469 | 112.8819 | 112.9533 | 112.8884
731.8125 | 121.7194 | -4.4586 | 117.1051 | 0.13101 | -0.00389 | -0.012 | -0.025017 | 0.008797 | 0.090161 | -0.13139 | 116.8682 | 116.894 | 116.8793 | 116.7872 | 4.3151 | 4.3953 | 4.3709 | 4.456 | 0.18136 | 0.046464 | 0.038354 | 0.025337 | 0.059151 | 0.14052 | -0.081036 | 116.9186 | 116.9444 | 116.9296 | 116.8375 | 4.3654 | 4.4456 | 4.4213 | 4.5063 | 112.5531 | 112.4973 | 112.5642 | 112.5084
733.5625 | 121.6965 | -4.5181 | 117.1143 | 0.13101 | -0.00389 | -0.002842 | -0.025017 | 0.004219 | 0.085583 | -0.12223 | 116.8499 | 116.8757 | 116.8655 | 116.7688 | 4.3334 | 4.4044 | 4.3892 | 4.4789 | 0.18136 | 0.046464 | 0.047512 | 0.025337 | 0.054573 | 0.13594 | -0.07188 | 116.9003 | 116.926 | 116.9159 | 116.8192 | 4.3838 | 4.4548 | 4.4396 | 4.5292 | 112.5165 | 112.4607 | 112.5321 | 112.4763
735.2969 | 121.6965 | -4.2252 | 117.3981 | 0.13101 | -0.00389 | -0.016578 | -0.01586 | 0.013375 | 0.09474 | -0.11308 | 117.1521 | 117.1779 | 117.1586 | 117.0619 | 4.0358 | 4.116 | 4.1008 | 4.1767 | 0.18136 | 0.046464 | 0.033776 | 0.034494 | 0.063729 | 0.14509 | -0.062723 | 117.2024 | 117.2282 | 117.2089 | 117.1123 | 4.0862 | 4.1664 | 4.1512 | 4.2271 | 113.1163 | 113.0513 | 113.1227 | 113.0578
737.0469 | 121.8887 | -58.8135 | 62.4115 | 0.12185 | -0.008469 | -0.021157 | -0.029595 | 0.004219 | 0.085583 | -0.12223 | 62.3383 | 62.3786 | 62.3977 | 62.3196 | 58.832 | 58.9063 | 58.753 | 58.8721 | 0.1722 | 0.041885 | 0.029197 | 0.020759 | 0.054573 | 0.13594 | -0.07188 | 62.3887 | 62.429 | 62.4481 | 62.3699 | 58.8823 | 58.9567 | 58.8034 | 58.9225 | 3.5064 | 3.5853 | 3.5658 | 3.6447
738.8125 | 121.7239 | -5.0812 | 116.5558 | 0.12643 | 0.000689 | -0.016578 | -0.025017 | 0.013375 | 0.085583 | -0.13139 | 116.2501 | 116.2713 | 116.2521 | 116.1598 | 4.9331 | 5.0179 | 4.9982 | 5.074 | 0.17678 | 0.051043 | 0.033776 | 0.025337 | 0.063729 | 0.13594 | -0.081036 | 116.3005 | 116.3216 | 116.3024 | 116.2102 | 4.9835 | 5.0682 | 5.0485 | 5.1244 | 111.317 | 111.252 | 111.3189 | 111.2539
740.5 | 121.7148 | -59.2804 | 62.1231 | 0.12643 | -0.013048 | -0.012 | -0.029595 | 0.013375 | 0.085583 | -0.11765 | 61.9446 | 61.9848 | 62.0177 | 61.9304 | 59.2257 | 59.2909 | 59.1376 | 59.2567 | 0.17678 | 0.037306 | 0.038354 | 0.020759 | 0.063729 | 0.13594 | -0.067301 | 61.9949 | 62.0352 | 62.0681 | 61.9807 | 59.2761 | 59.3412 | 59.188 | 59.3071 | 2.7189 | 2.807 | 2.792 | 2.8801
742.25 | 121.7972 | -58.4518 | 62.9059 | 0.12643 | -0.00389 | -0.016578 | -0.025017 | 0.008797 | 0.090161 | -0.11765 | 62.7596 | 62.7999 | 62.8052 | 62.7454 | 58.4154 | 58.4805 | 58.3181 | 58.4509 | 0.17678 | 0.046464 | 0.033776 | 0.025337 | 0.059151 | 0.14052 | -0.067301 | 62.8099 | 62.8502 | 62.8556 | 62.7958 | 58.4657 | 58.5309 | 58.3684 | 58.5013 | 4.3442 | 4.4415 | 4.3898 | 4.4871
744 | 121.8063 | -57.8796 | 63.5284 | 0.13101 | -0.017627 | -0.016578 | -0.025017 | -0.000359 | 0.085583 | -0.12223 | 63.2586 | 63.3127 | 63.3134 | 63.2583 | 57.9072 | 57.9724 | 57.787 | 57.9428 | 0.18136 | 0.032727 | 0.033776 | 0.025337 | 0.049995 | 0.13594 | -0.07188 | 63.309 | 63.363 | 63.3638 | 63.3086 | 57.9575 | 58.0227 | 57.8373 | 57.9931 | 5.3514 | 5.4716 | 5.4062 | 5.5264
745.6875 | 121.8292 | -57.399 | 64.0228 | 0.12185 | 0.000689 | -0.016578 | -0.029595 | -0.000359 | 0.081005 | -0.12223 | 63.7439 | 63.7889 | 63.8033 | 63.7391 | 57.4219 | 57.4871 | 57.3108 | 57.4666 | 0.1722 | 0.051043 | 0.033776 | 0.020759 | 0.049995 | 0.13136 | -0.07188 | 63.7943 | 63.8392 | 63.8536 | 63.7894 | 57.4723 | 57.5375 | 57.3612 | 57.517 | 6.322 | 6.4331 | 6.3814 | 6.4925
747.4219 | 121.1014 | -7.0496 | 114.7018 | 0.13101 | 0.014425 | 0.006315 | -0.002124 | 0.027109 | 0.11305 | -0.099343 | 99.7263 | 99.8196 | 99.5688 | 99.5837 | 21.2726 | 21.5859 | 21.4483 | 21.528 | 0.18136 | 0.064779 | 0.056669 | 0.04823 | 0.077463 | 0.16341 | -0.048989 | 99.7767 | 99.8699 | 99.6192 | 99.6341 | 21.323 | 21.6363 | 21.4987 | 21.5783 | 78.4537 | 78.278 | 78.2962 | 78.1205
749.1719 | 121.6232 | -5.3833 | 116.3498 | 0.12643 | -0.008469 | -0.021157 | -0.029595 | 0.013375 | 0.085583 | -0.12223 | 116.0395 | 116.0652 | 116.046 | 115.9492 | 5.0476 | 5.2147 | 5.1996 | 5.2526 | 0.17678 | 0.041885 | 0.029197 | 0.020759 | 0.063729 | 0.13594 | -0.07188 | 116.0899 | 116.1156 | 116.0964 | 115.9996 | 5.098 | 5.2651 | 5.25 | 5.3029 | 110.9919 | 110.8399 | 110.9984 | 110.8464
750.9219 | 121.7239 | -5.127 | 116.5009 | 0.13101 | -0.00389 | -0.012 | -0.025017 | 0.017953 | 0.081005 | -0.12681 | 116.1723 | 116.1843 | 116.1696 | 116.0728 | 4.9331 | 5.0911 | 5.076 | 5.1198 | 0.18136 | 0.046464 | 0.038354 | 0.025337 | 0.068307 | 0.13136 | -0.076458 | 116.2226 | 116.2346 | 116.22 | 116.1232 | 4.9835 | 5.1415 | 5.1263 | 5.1702 | 111.2391 | 111.0963 | 111.2365 | 111.0937
752.625 | 121.6324 | -4.9484 | 116.7709 | 0.12643 | -0.00389 | -0.012 | -0.025017 | 0.017953 | 0.076426 | -0.11765 | 116.4516 | 116.4728 | 116.4489 | 116.3613 | 4.6585 | 4.8119 | 4.8013 | 4.836 | 0.17678 | 0.046464 | 0.038354 | 0.025337 | 0.068307 | 0.12678 | -0.067301 | 116.5019 | 116.5231 | 116.4993 | 116.4117 | 4.7088 | 4.8622 | 4.8516 | 4.8863 | 111.7931 | 111.6503 | 111.7905 | 111.6476
754.3594 | 121.6278 | -4.9393 | 116.7389 | 0.12643 | 0.000689 | -0.012 | -0.029595 | 0.013375 | 0.085583 | -0.12223 | 116.4333 | 116.4499 | 116.426 | 116.3384 | 4.6722 | 4.8439 | 4.8196 | 4.8634 | 0.17678 | 0.051043 | 0.038354 | 0.020759 | 0.063729 | 0.13594 | -0.07188 | 116.4836 | 116.5002 | 116.4764 | 116.3888 | 4.7225 | 4.8943 | 4.87 | 4.9138 | 111.7611 | 111.6136 | 111.7538 | 111.6064
756.0938 | 121.7514 | -4.6097 | 116.9678 | 0.12643 | 0.000689 | -0.021157 | -0.025017 | 0.008797 | 0.085583 | -0.13139 | 116.4836 | 116.5094 | 116.481 | 116.3934 | 4.6081 | 4.789 | 4.7692 | 4.8131 | 0.17678 | 0.051043 | 0.029197 | 0.025337 | 0.059151 | 0.13594 | -0.081036 | 116.534 | 116.5597 | 116.5313 | 116.4437 | 4.6584 | 4.8393 | 4.8196 | 4.8634 | 111.8755 | 111.7144 | 111.8729 | 111.7117
757.7812 | 121.6965 | -4.8248 | 116.8121 | 0.12643 | -0.00389 | -0.016578 | -0.025017 | 0.017953 | 0.085583 | -0.12681 | 116.6393 | 116.6651 | 116.6549 | 116.5536 | 4.4616 | 4.6242 | 4.6044 | 4.6528 | 0.17678 | 0.046464 | 0.033776 | 0.025337 | 0.068307 | 0.13594 | -0.076458 | 116.6896 | 116.7154 | 116.7053 | 116.604 | 4.5119 | 4.6745 | 4.6548 | 4.7032 | 112.1777 | 112.0349 | 112.1934 | 112.0505
759.5312 | 121.7697 | -4.8294 | 116.7526 | 0.12643 | 0.000689 | -0.012 | -0.025017 | 0.013375 | 0.085583 | -0.12681 | 116.4745 | 116.4956 | 116.4764 | 116.3796 | 4.6218 | 4.7981 | 4.7738 | 4.8176 | 0.17678 | 0.051043 | 0.038354 | 0.025337 | 0.063729 | 0.13594 | -0.076458 | 116.5248 | 116.546 | 116.5267 | 116.43 | 4.6722 | 4.8485 | 4.8242 | 4.868 | 111.8526 | 111.7006 | 111.8546 | 111.7026
761.2188 | 121.637 | -5.8182 | 115.8417 | 0.14017 | 0.000689 | -0.012 | -0.020438 | 0.013375 | 0.090161 | -0.11765 | 115.5908 | 115.5661 | 115.5882 | 115.505 | 5.5054 | 5.6817 | 5.6437 | 5.7379 | 0.19052 | 0.051043 | 0.038354 | 0.029916 | 0.063729 | 0.14052 | -0.067301 | 115.6412 | 115.6165 | 115.6386 | 115.5554 | 5.5558 | 5.7321 | 5.6941 | 5.7882 | 110.0854 | 109.9471 | 110.0828 | 109.9445
762.9844 | 121.5912 | -5.3055 | 116.3956 | 0.13559 | 0.000689 | -0.012 | -0.020438 | 0.008797 | 0.090161 | -0.11765 | 116.067 | 116.0927 | 116.0781 | 115.9767 | 5.0293 | 5.201 | 5.1859 | 5.2571 | 0.18594 | 0.051043 | 0.038354 | 0.029916 | 0.059151 | 0.14052 | -0.067301 | 116.1173 | 116.1431 | 116.1284 | 116.027 | 5.0796 | 5.2514 | 5.2362 | 5.3075 | 111.0377 | 110.8811 | 111.0488 | 110.8922
764.6719 | 121.6095 | -5.0079 | 116.7114 | 0.13559 | -0.00389 | -0.012 | -0.025017 | 0.008797 | 0.085583 | -0.11765 | 116.3417 | 116.3629 | 116.3436 | 116.2468 | 4.7638 | 4.9218 | 4.9112 | 4.9962 | 0.18594 | 0.046464 | 0.038354 | 0.025337 | 0.059151 | 0.13594 | -0.067301 | 116.392 | 116.4132 | 116.394 | 116.2972 | 4.8141 | 4.9721 | 4.9615 | 5.0465 | 111.5779 | 111.4305 | 111.5799 | 111.4325
766.4219 | 121.7194 | -8.6792 | 112.9349 | 0.13101 | -0.00389 | -0.030314 | -0.029595 | 0.008797 | 0.081005 | -0.12681 | 112.6148 | 112.6128 | 112.6718 | 112.5836 | 8.5636 | 8.6391 | 8.6197 | 8.6999 | 0.18136 | 0.046464 | 0.02004 | 0.020759 | 0.059151 | 0.13136 | -0.076458 | 112.6651 | 112.6632 | 112.7222 | 112.634 | 8.614 | 8.6895 | 8.67 | 8.7503 | 104.0512 | 103.9951 | 104.1082 | 104.0522
768.1719 | 121.669 | -6.9305 | 114.7339 | 0.13559 | -0.00389 | -0.012 | -0.029595 | 0.017953 | 0.085583 | -0.12223 | 114.4004 | 114.4169 | 114.4024 | 114.3694 | 6.7919 | 6.872 | 6.8387 | 6.9236 | 0.18594 | 0.046464 | 0.038354 | 0.020759 | 0.068307 | 0.13594 | -0.07188 | 114.4508 | 114.4672 | 114.4528 | 114.4198 | 6.8422 | 6.9224 | 6.889 | 6.974 | 107.6085 | 107.5617 | 107.6105 | 107.5638
769.9219 | 121.669 | -6.6742 | 114.9673 | 0.14017 | 0.000689 | -0.012 | -0.029595 | -0.000359 | 0.090161 | -0.12223 | 114.7621 | 114.7923 | 114.7687 | 114.7266 | 6.4394 | 6.5058 | 6.4724 | 6.5665 | 0.19052 | 0.051043 | 0.038354 | 0.020759 | 0.049995 | 0.14052 | -0.07188 | 114.8125 | 114.8427 | 114.8191 | 114.7769 | 6.4897 | 6.5561 | 6.5228 | 6.6169 | 108.3227 | 108.2897 | 108.3293 | 108.2963
771.625 | 121.701 | -6.4682 | 115.1276 | 0.13559 | -0.00389 | -0.016578 | -0.029595 | 0.004219 | 0.085583 | -0.12223 | 114.9224 | 114.948 | 114.9289 | 114.8914 | 6.27 | 6.3455 | 6.3213 | 6.4063 | 0.18594 | 0.046464 | 0.033776 | 0.020759 | 0.054573 | 0.13594 | -0.07188 | 114.9727 | 114.9984 | 114.9793 | 114.9418 | 6.3203 | 6.3959 | 6.3717 | 6.4566 | 108.6524 | 108.601 | 108.659 | 108.6076
773.3906 | 121.7514 | -6.1707 | 115.3839 | 0.12643 | 0.000689 | -0.012 | -0.029595 | 0.013375 | 0.085583 | -0.12223 | 115.1009 | 115.122 | 115.1075 | 115.07 | 6.0823 | 6.1624 | 6.1382 | 6.2277 | 0.17678 | 0.051043 | 0.038354 | 0.020759 | 0.063729 | 0.13594 | -0.07188 | 115.1513 | 115.1724 | 115.1578 | 115.1204 | 6.1326 | 6.2128 | 6.1885 | 6.2781 | 109.0186 | 108.9627 | 109.0252 | 108.9693
775.1406 | 121.7514 | -5.777 | 115.8005 | 0.13101 | -0.00389 | -0.016578 | -0.025017 | 0.008797 | 0.090161 | -0.12681 | 115.4397 | 115.47 | 115.4509 | 115.4135 | 5.7389 | 5.8236 | 5.7948 | 5.8798 | 0.18136 | 0.046464 | 0.033776 | 0.025337 | 0.059151 | 0.14052 | -0.076458 | 115.4901 | 115.5203 | 115.5012 | 115.4638 | 5.7893 | 5.874 | 5.8452 | 5.9301 | 109.7008 | 109.6449 | 109.712 | 109.6561
776.8438 | 121.7194 | -6.0425 | 115.5441 | 0.13559 | -0.00389 | -0.016578 | -0.025017 | 0.013375 | 0.085583 | -0.12223 | 115.2932 | 115.3235 | 115.3044 | 115.2623 | 5.8946 | 5.9839 | 5.9459 | 6.0309 | 0.18594 | 0.046464 | 0.033776 | 0.025337 | 0.063729 | 0.13594 | -0.07188 | 115.3436 | 115.3738 | 115.3547 | 115.3127 | 5.9449 | 6.0342 | 5.9962 | 6.0812 | 109.3986 | 109.3473 | 109.4098 | 109.3585
778.5938 | 121.6599 | -5.9921 | 115.6677 | 0.13101 | 0.005267 | -0.016578 | -0.029595 | 0.013375 | 0.085583 | -0.12223 | 115.371 | 115.3921 | 115.3776 | 115.3402 | 5.8213 | 5.8923 | 5.8681 | 5.9576 | 0.18136 | 0.055621 | 0.033776 | 0.020759 | 0.063729 | 0.13594 | -0.07188 | 115.4214 | 115.4425 | 115.428 | 115.3905 | 5.8717 | 5.9427 | 5.9184 | 6.008 | 109.5497 | 109.503 | 109.5563 | 109.5095
780.3594 | 121.7697 | -5.7632 | 115.8096 | 0.13101 | -0.00389 | -0.016578 | -0.020438 | 0.013375 | 0.085583 | -0.11308 | 115.6183 | 115.644 | 115.6294 | 115.5829 | 5.5695 | 5.6497 | 5.6254 | 5.7104 | 0.18136 | 0.046464 | 0.033776 | 0.029916 | 0.063729 | 0.13594 | -0.062723 | 115.6686 | 115.6943 | 115.6798 | 115.6332 | 5.6199 | 5.7 | 5.6758 | 5.7607 | 110.0488 | 109.9929 | 110.0599 | 110.004
782.0469 | 121.6919 | -5.8273 | 115.7776 | 0.12185 | 0.000689 | -0.012 | -0.025017 | 0.013375 | 0.090161 | -0.11308 | 115.5862 | 115.5982 | 115.5974 | 115.5554 | 5.6061 | 5.6817 | 5.6575 | 5.7516 | 0.1722 | 0.051043 | 0.038354 | 0.025337 | 0.063729 | 0.14052 | -0.062723 | 115.6366 | 115.6486 | 115.6477 | 115.6058 | 5.6565 | 5.7321 | 5.7078 | 5.8019 | 109.9801 | 109.9288 | 109.9912 | 109.9399
783.7969 | 121.7285 | -6.015 | 115.5762 | 0.12643 | -0.00389 | -0.016578 | -0.029595 | 0.013375 | 0.090161 | -0.13139 | 115.3665 | 115.3784 | 115.3639 | 115.3264 | 5.835 | 5.906 | 5.8818 | 5.9713 | 0.17678 | 0.046464 | 0.033776 | 0.020759 | 0.063729 | 0.14052 | -0.081036 | 115.4168 | 115.4288 | 115.4142 | 115.3768 | 5.8854 | 5.9564 | 5.9321 | 6.0217 | 109.5314 | 109.4847 | 109.5288 | 109.4821
785.4844 | 121.637 | -5.7037 | 115.9515 | 0.13559 | 0.005267 | -0.012 | -0.020438 | 0.017953 | 0.090161 | -0.11308 | 115.6091 | 115.6302 | 115.6065 | 115.5737 | 5.5878 | 5.6588 | 5.6391 | 5.7241 | 0.18594 | 0.055621 | 0.038354 | 0.029916 | 0.068307 | 0.14052 | -0.062723 | 115.6595 | 115.6806 | 115.6569 | 115.6241 | 5.6382 | 5.7092 | 5.6895 | 5.7745 | 110.0213 | 109.97 | 110.0187 | 109.9674
787.2344 | 121.7331 | -5.6854 | 115.9332 | 0.13559 | 0.000689 | -0.016578 | -0.025017 | 0.008797 | 0.081005 | -0.12681 | 115.6915 | 115.7127 | 115.6935 | 115.6561 | 5.5008 | 5.581 | 5.5567 | 5.6417 | 0.18594 | 0.051043 | 0.033776 | 0.025337 | 0.059151 | 0.13136 | -0.076458 | 115.7419 | 115.763 | 115.7439 | 115.7065 | 5.5512 | 5.6313 | 5.6071 | 5.6921 | 110.1907 | 110.1348 | 110.1927 | 110.1368
789 | 121.6461 | -5.658 | 116.0477 | 0.13559 | 0.000689 | -0.016578 | -0.029595 | 0.013375 | 0.085583 | -0.11765 | 115.7465 | 115.763 | 115.7576 | 115.7157 | 5.4459 | 5.5215 | 5.5064 | 5.5959 | 0.18594 | 0.051043 | 0.033776 | 0.020759 | 0.063729 | 0.13594 | -0.067301 | 115.7968 | 115.8134 | 115.808 | 115.766 | 5.4963 | 5.5718 | 5.5567 | 5.6463 | 110.3006 | 110.2401 | 110.3117 | 110.2512
790.75 | 121.8018 | -5.4611 | 116.1163 | 0.12643 | 0.000689 | -0.016578 | -0.025017 | 0.013375 | 0.081005 | -0.12681 | 115.9113 | 115.9279 | 115.9178 | 115.8714 | 5.2857 | 5.3612 | 5.3415 | 5.4311 | 0.17678 | 0.051043 | 0.033776 | 0.025337 | 0.063729 | 0.13136 | -0.076458 | 115.9617 | 115.9782 | 115.9682 | 115.9217 | 5.336 | 5.4116 | 5.3919 | 5.4815 | 110.6256 | 110.5698 | 110.6322 | 110.5763
792.5 | 121.6782 | -5.7953 | 115.8188 | 0.13101 | 0.000689 | -0.012 | -0.01586 | 0.013375 | 0.090161 | -0.11765 | 115.5679 | 115.5799 | 115.5745 | 115.5233 | 5.6336 | 5.7138 | 5.6803 | 5.7745 | 0.18136 | 0.051043 | 0.038354 | 0.034494 | 0.063729 | 0.14052 | -0.067301 | 115.6183 | 115.6302 | 115.6248 | 115.5737 | 5.684 | 5.7641 | 5.7307 | 5.8248 | 109.9343 | 109.8876 | 109.9409 | 109.8941
794.2031 | 121.7834 | -5.6396 | 115.9195 | 0.13101 | -0.00389 | -0.012 | -0.025017 | 0.008797 | 0.085583 | -0.12223 | 115.6641 | 115.6806 | 115.666 | 115.6241 | 5.5375 | 5.613 | 5.5842 | 5.6738 | 0.18136 | 0.046464 | 0.038354 | 0.025337 | 0.059151 | 0.13594 | -0.07188 | 115.7144 | 115.731 | 115.7164 | 115.6744 | 5.5878 | 5.6634 | 5.6346 | 5.7241 | 110.1266 | 110.0799 | 110.1286 | 110.0818
795.9531 | 121.7285 | -5.7678 | 115.8325 | 0.13559 | 0.005267 | -0.016578 | -0.029595 | 0.013375 | 0.090161 | -0.12223 | 115.6045 | 115.6119 | 115.6019 | 115.5691 | 5.597 | 5.6726 | 5.6483 | 5.7287 | 0.18594 | 0.055621 | 0.033776 | 0.020759 | 0.063729 | 0.14052 | -0.07188 | 115.6549 | 115.6623 | 115.6523 | 115.6195 | 5.6473 | 5.7229 | 5.6986 | 5.7791 | 110.0076 | 109.9563 | 110.005 | 109.9536
797.6406 | 121.7743 | -5.6808 | 115.8875 | 0.13101 | 0.000689 | -0.016578 | -0.020438 | 0.008797 | 0.081005 | -0.12223 | 115.687 | 115.7081 | 115.6935 | 115.6424 | 5.51 | 5.5856 | 5.5521 | 5.6509 | 0.18136 | 0.051043 | 0.033776 | 0.029916 | 0.059151 | 0.13136 | -0.07188 | 115.7373 | 115.7584 | 115.7439 | 115.6928 | 5.5603 | 5.6359 | 5.6025 | 5.7012 | 110.177 | 110.1348 | 110.1835 | 110.1414
799.4062 | 121.6324 | -5.6213 | 116.0248 | 0.13559 | 0.000689 | -0.016578 | -0.025017 | 0.008797 | 0.090161 | -0.11765 | 115.8381 | 115.8638 | 115.8492 | 115.8072 | 5.3543 | 5.4299 | 5.4102 | 5.4906 | 0.18594 | 0.051043 | 0.033776 | 0.025337 | 0.059151 | 0.14052 | -0.067301 | 115.8884 | 115.9141 | 115.8995 | 115.8576 | 5.4047 | 5.4803 | 5.4606 | 5.541 | 110.4837 | 110.4278 | 110.4948 | 110.439
801.0938 | 121.7743 | -5.5206 | 116.0843 | 0.13559 | -0.008469 | -0.021157 | -0.029595 | 0.008797 | 0.076426 | -0.11765 | 115.8564 | 115.8683 | 115.8537 | 115.8164 | 5.3406 | 5.4208 | 5.3965 | 5.4815 | 0.18594 | 0.041885 | 0.029197 | 0.020759 | 0.059151 | 0.12678 | -0.067301 | 115.9067 | 115.9187 | 115.9041 | 115.8668 | 5.391 | 5.4711 | 5.4468 | 5.5318 | 110.5158 | 110.4599 | 110.5131 | 110.4573
802.8438 | 121.637 | -5.159 | 116.5237 | 0.12643 | -0.00389 | -0.016578 | -0.025017 | 0.022531 | 0.076426 | -0.11765 | 116.1814 | 116.198 | 116.1788 | 116.1369 | 5.0293 | 5.0957 | 5.076 | 5.1656 | 0.17678 | 0.046464 | 0.033776 | 0.025337 | 0.072885 | 0.12678 | -0.067301 | 116.2318 | 116.2484 | 116.2292 | 116.1873 | 5.0796 | 5.1461 | 5.1263 | 5.2159 | 111.1522 | 111.1054 | 111.1495 | 111.1028
804.5938 | 121.788 | -5.2597 | 116.3315 | 0.14017 | 0.000689 | -0.016578 | -0.029595 | 0.008797 | 0.081005 | -0.11765 | 116.1677 | 116.1934 | 116.1742 | 116.1186 | 5.0339 | 5.1095 | 5.0852 | 5.1793 | 0.19052 | 0.051043 | 0.033776 | 0.020759 | 0.059151 | 0.13136 | -0.067301 | 116.2181 | 116.2438 | 116.2246 | 116.169 | 5.0842 | 5.1598 | 5.1355 | 5.2297 | 111.1338 | 111.0826 | 111.1404 | 111.0891
806.3438 | 121.6873 | -5.2872 | 116.3864 | 0.14017 | -0.00389 | -0.012 | -0.020438 | 0.017953 | 0.085583 | -0.12223 | 116.1265 | 116.1522 | 116.133 | 116.0774 | 5.0705 | 5.1461 | 5.1218 | 5.2068 | 0.19052 | 0.046464 | 0.038354 | 0.029916 | 0.068307 | 0.13594 | -0.07188 | 116.1769 | 116.2026 | 116.1834 | 116.1278 | 5.1208 | 5.1964 | 5.1721 | 5.2571 | 111.056 | 111.0047 | 111.0625 | 111.0112
808.0156 | 121.8109 | -5.3192 | 116.2491 | 0.12643 | -0.00389 | -0.021157 | -0.025017 | 0.008797 | 0.085583 | -0.12681 | 116.0029 | 116.024 | 116.0048 | 115.9721 | 5.1941 | 5.2651 | 5.2454 | 5.3304 | 0.17678 | 0.046464 | 0.029197 | 0.025337 | 0.059151 | 0.13594 | -0.076458 | 116.0532 | 116.0744 | 116.0552 | 116.0224 | 5.2445 | 5.3155 | 5.2958 | 5.3808 | 110.8088 | 110.7575 | 110.8107 | 110.7594
809.7656 | 121.7377 | -5.2322 | 116.3315 | 0.13101 | 0.000689 | -0.016578 | -0.029595 | 0.008797 | 0.081005 | -0.11765 | 116.1082 | 116.1339 | 116.1147 | 116.0683 | 5.0934 | 5.1735 | 5.1355 | 5.2297 | 0.18136 | 0.051043 | 0.033776 | 0.020759 | 0.059151 | 0.13136 | -0.067301 | 116.1585 | 116.1843 | 116.1651 | 116.1186 | 5.1437 | 5.2239 | 5.1859 | 5.28 | 111.0148 | 110.9727 | 111.0213 | 110.9792
811.5156 | 121.6461 | -5.3329 | 116.3086 | 0.13101 | 0.000689 | -0.012 | -0.029595 | 0.013375 | 0.076426 | -0.12223 | 116.0578 | 116.0744 | 116.0643 | 116.0225 | 5.1392 | 5.2193 | 5.195 | 5.2755 | 0.18136 | 0.051043 | 0.038354 | 0.020759 | 0.063729 | 0.12678 | -0.07188 | 116.1082 | 116.1247 | 116.1147 | 116.0728 | 5.1895 | 5.2697 | 5.2454 | 5.3258 | 110.9187 | 110.8628 | 110.9252 | 110.8693
813.2656 | 121.6782 | -5.2963 | 116.3544 | 0.13559 | -0.00389 | -0.016578 | -0.029595 | 0.013375 | 0.081005 | -0.12681 | 116.1402 | 116.1568 | 116.1376 | 116.0957 | 5.0568 | 5.1323 | 5.1126 | 5.2022 | 0.18594 | 0.046464 | 0.033776 | 0.020759 | 0.063729 | 0.13136 | -0.076458 | 116.1906 | 116.2072 | 116.188 | 116.1461 | 5.1071 | 5.1827 | 5.163 | 5.2526 | 111.0835 | 111.0276 | 111.0808 | 111.025
815.0156 | 121.7697 | -4.7699 | 116.803 | 0.13101 | -0.00389 | -0.021157 | -0.029595 | 0.004219 | 0.081005 | -0.12223 | 116.6393 | 116.6513 | 116.6412 | 116.5948 | 4.5577 | 4.6425 | 4.6273 | 4.7078 | 0.18136 | 0.046464 | 0.029197 | 0.020759 | 0.054573 | 0.13136 | -0.07188 | 116.6896 | 116.7017 | 116.6916 | 116.6452 | 4.6081 | 4.6928 | 4.6777 | 4.7581 | 112.0816 | 112.012 | 112.0835 | 112.0139
816.7031 | 121.7422 | -5.2689 | 116.3177 | 0.13559 | 0.000689 | -0.016578 | -0.025017 | 0.013375 | 0.076426 | -0.13139 | 116.1357 | 116.1522 | 116.1376 | 116.0911 | 5.0705 | 5.1507 | 5.1264 | 5.2114 | 0.18594 | 0.051043 | 0.033776 | 0.025337 | 0.063729 | 0.12678 | -0.081036 | 116.186 | 116.2026 | 116.188 | 116.1415 | 5.1208 | 5.201 | 5.1767 | 5.2617 | 111.0652 | 111.0093 | 111.0671 | 111.0112
818.4375 | 121.7056 | -5.2917 | 116.3589 | 0.13559 | -0.00389 | -0.016578 | -0.025017 | 0.008797 | 0.090161 | -0.1085 | 116.0578 | 116.079 | 116.0643 | 116.027 | 5.1392 | 5.2147 | 5.195 | 5.2755 | 0.18594 | 0.046464 | 0.033776 | 0.025337 | 0.059151 | 0.14052 | -0.058145 | 116.1082 | 116.1293 | 116.1147 | 116.0774 | 5.1895 | 5.2651 | 5.2454 | 5.3258 | 110.9187 | 110.8628 | 110.9252 | 110.8693
820.1875 | 121.669 | -5.0903 | 116.5512 | 0.13559 | 0.000689 | -0.012 | -0.025017 | 0.008797 | 0.090161 | -0.11308 | 116.2501 | 116.2621 | 116.2383 | 116.1965 | 4.9469 | 5.0316 | 5.0073 | 5.0878 | 0.18594 | 0.051043 | 0.038354 | 0.025337 | 0.059151 | 0.14052 | -0.062723 | 116.3005 | 116.3125 | 116.2887 | 116.2468 | 4.9972 | 5.082 | 5.0577 | 5.1381 | 111.3032 | 111.2428 | 111.2914 | 111.231
821.9375 | 121.7239 | -5.3192 | 116.2994 | 0.13101 | -0.008469 | -0.025735 | -0.034174 | -0.000359 | 0.090161 | -0.13139 | 116.154 | 116.166 | 116.1513 | 116.1095 | 5.0476 | 5.1278 | 5.108 | 5.1931 | 0.18136 | 0.041885 | 0.024619 | 0.01618 | 0.049995 | 0.14052 | -0.081036 | 116.2043 | 116.2163 | 116.2017 | 116.1598 | 5.098 | 5.1781 | 5.1584 | 5.2434 | 111.1064 | 111.0459 | 111.1037 | 111.0433
823.6406 | 121.6415 | -5.2734 | 116.3818 | 0.12643 | -0.00389 | -0.012 | -0.020438 | 0.008797 | 0.09474 | -0.11765 | 116.1082 | 116.1248 | 116.1147 | 116.0683 | 5.0888 | 5.169 | 5.1355 | 5.2343 | 0.17678 | 0.046464 | 0.038354 | 0.029916 | 0.059151 | 0.14509 | -0.067301 | 116.1585 | 116.1751 | 116.1651 | 116.1186 | 5.1392 | 5.2193 | 5.1859 | 5.2846 | 111.0194 | 110.9727 | 111.0259 | 110.9792
825.375 | 121.6553 | -5.2963 | 116.3498 | 0.14017 | 0.000689 | -0.007421 | -0.029595 | 0.017953 | 0.081005 | -0.12223 | 116.1906 | 116.2209 | 116.1971 | 116.1553 | 4.9972 | 5.0728 | 5.0577 | 5.1473 | 0.19052 | 0.051043 | 0.042933 | 0.020759 | 0.068307 | 0.13136 | -0.07188 | 116.241 | 116.2713 | 116.2475 | 116.2056 | 5.0476 | 5.1232 | 5.108 | 5.1976 | 111.1934 | 111.1329 | 111.1999 | 111.1394
827.125 | 121.7972 | -5.2185 | 116.3589 | 0.13101 | -0.013048 | -0.016578 | -0.020438 | 0.013375 | 0.081005 | -0.12681 | 116.1677 | 116.1934 | 116.1742 | 116.1278 | 5.0293 | 5.1003 | 5.076 | 5.1702 | 0.18136 | 0.037306 | 0.033776 | 0.029916 | 0.063729 | 0.13136 | -0.076458 | 116.2181 | 116.2438 | 116.2246 | 116.1781 | 5.0796 | 5.1506 | 5.1263 | 5.2205 | 111.1384 | 111.0917 | 111.1449 | 111.0982
828.8281 | 121.7789 | -4.8065 | 116.7801 | 0.14017 | -0.00389 | -0.021157 | -0.029595 | 0.004219 | 0.081005 | -0.12681 | 116.5202 | 116.5506 | 116.5313 | 116.4804 | 4.6722 | 4.7478 | 4.7326 | 4.8222 | 0.19052 | 0.046464 | 0.029197 | 0.020759 | 0.054573 | 0.13136 | -0.076458 | 116.5706 | 116.6009 | 116.5817 | 116.5307 | 4.7225 | 4.7981 | 4.783 | 4.8726 | 111.8481 | 111.7876 | 111.8591 | 111.7987
830.5781 | 121.7697 | -5.0171 | 116.5192 | 0.12643 | -0.013048 | -0.016578 | -0.020438 | 0.008797 | 0.081005 | -0.12681 | 116.3508 | 116.3629 | 116.3528 | 116.3109 | 4.8507 | 4.9309 | 4.9112 | 4.9916 | 0.17678 | 0.037306 | 0.033776 | 0.029916 | 0.059151 | 0.13136 | -0.076458 | 116.4012 | 116.4132 | 116.4031 | 116.3613 | 4.9011 | 4.9813 | 4.9615 | 5.042 | 111.5001 | 111.4397 | 111.502 | 111.4416
832.3281 | 121.6507 | -4.953 | 116.7389 | 0.13559 | -0.00389 | -0.012 | -0.020438 | 0.013375 | 0.081005 | -0.11308 | 116.4699 | 116.4865 | 116.4764 | 116.4346 | 4.7317 | 4.8027 | 4.783 | 4.8726 | 0.18594 | 0.046464 | 0.038354 | 0.029916 | 0.063729 | 0.13136 | -0.062723 | 116.5202 | 116.5368 | 116.5267 | 116.4849 | 4.7821 | 4.8531 | 4.8333 | 4.9229 | 111.7382 | 111.6869 | 111.7447 | 111.6934
834.0938 | 121.7834 | -5.0446 | 116.5466 | 0.13101 | -0.00389 | -0.016578 | -0.025017 | 0.008797 | 0.085583 | -0.12681 | 116.4333 | 116.459 | 116.4352 | 116.3979 | 4.7638 | 4.8393 | 4.8242 | 4.9001 | 0.18136 | 0.046464 | 0.033776 | 0.025337 | 0.059151 | 0.13594 | -0.076458 | 116.4836 | 116.5094 | 116.4855 | 116.4483 | 4.8141 | 4.8897 | 4.8745 | 4.9504 | 111.6695 | 111.6091 | 111.6714 | 111.611
835.7812 | 121.6827 | -4.9667 | 116.6611 | 0.13101 | 0.000689 | -0.016578 | -0.020438 | 0.013375 | 0.076426 | -0.11308 | 116.4149 | 116.4361 | 116.4306 | 116.375 | 4.7866 | 4.8531 | 4.8425 | 4.9229 | 0.18136 | 0.051043 | 0.033776 | 0.029916 | 0.063729 | 0.12678 | -0.062723 | 116.4653 | 116.4865 | 116.481 | 116.4254 | 4.837 | 4.9034 | 4.8929 | 4.9733 | 111.6283 | 111.5724 | 111.644 | 111.5881
837.5312 | 121.7834 | -4.921 | 116.6565 | 0.13101 | -0.008469 | -0.016578 | -0.020438 | 0.013375 | 0.085583 | -0.11765 | 116.4012 | 116.4224 | 116.4077 | 116.3659 | 4.8004 | 4.8668 | 4.8517 | 4.9321 | 0.18136 | 0.041885 | 0.033776 | 0.029916 | 0.063729 | 0.13594 | -0.067301 | 116.4516 | 116.4727 | 116.4581 | 116.4162 | 4.8507 | 4.9172 | 4.902 | 4.9825 | 111.6008 | 111.5496 | 111.6073 | 111.5561
839.2188 | 121.7606 | -4.9484 | 116.6382 | 0.13101 | 0.000689 | -0.012 | -0.025017 | 0.013375 | 0.081005 | -0.13139 | 116.447 | 116.4728 | 116.4535 | 116.4163 | 4.7546 | 4.8393 | 4.8013 | 4.8955 | 0.18136 | 0.051043 | 0.038354 | 0.025337 | 0.063729 | 0.13136 | -0.081036 | 116.4973 | 116.5231 | 116.5039 | 116.4666 | 4.805 | 4.8897 | 4.8516 | 4.9458 | 111.6924 | 111.6457 | 111.6989 | 111.6522
840.9688 | 121.7239 | -4.8111 | 116.7572 | 0.14017 | -0.008469 | -0.016578 | -0.029595 | 0.008797 | 0.085583 | -0.12223 | 116.5798 | 116.601 | 116.5817 | 116.5445 | 4.631 | 4.702 | 4.6777 | 4.7627 | 0.19052 | 0.041885 | 0.033776 | 0.020759 | 0.059151 | 0.13594 | -0.07188 | 116.6301 | 116.6513 | 116.632 | 116.5948 | 4.6813 | 4.7524 | 4.728 | 4.8131 | 111.9488 | 111.9021 | 111.9507 | 111.904
842.6562 | 121.6553 | -4.7287 | 116.954 | 0.13559 | 0.005267 | -0.012 | -0.025017 | 0.017953 | 0.090161 | -0.12223 | 116.621 | 116.6376 | 116.6183 | 116.5765 | 4.5898 | 4.6745 | 4.6456 | 4.7261 | 0.18594 | 0.055621 | 0.038354 | 0.025337 | 0.068307 | 0.14052 | -0.07188 | 116.6713 | 116.6879 | 116.6687 | 116.6269 | 4.6401 | 4.7249 | 4.696 | 4.7764 | 112.0312 | 111.9753 | 112.0285 | 111.9727
844.4062 | 121.6553 | -4.8523 | 116.7984 | 0.12643 | -0.00389 | -0.012 | -0.025017 | 0.013375 | 0.085583 | -0.11308 | 116.5386 | 116.546 | 116.5313 | 116.4941 | 4.6676 | 4.7432 | 4.7235 | 4.8131 | 0.17678 | 0.046464 | 0.038354 | 0.025337 | 0.063729 | 0.13594 | -0.062723 | 116.5889 | 116.5964 | 116.5817 | 116.5445 | 4.718 | 4.7936 | 4.7738 | 4.8634 | 111.8709 | 111.8151 | 111.8637 | 111.8079
846.1406 | 121.7651 | -4.7424 | 116.7984 | 0.13559 | 0.000689 | -0.016578 | -0.029595 | 0.013375 | 0.090161 | -0.11765 | 116.5752 | 116.5826 | 116.5725 | 116.5307 | 4.631 | 4.7112 | 4.6914 | 4.7719 | 0.18594 | 0.051043 | 0.033776 | 0.020759 | 0.063729 | 0.14052 | -0.067301 | 116.6255 | 116.633 | 116.6229 | 116.5811 | 4.6813 | 4.7615 | 4.7418 | 4.8222 | 111.9442 | 111.8838 | 111.9416 | 111.8811
847.8906 | 121.7102 | -4.5547 | 117.0456 | 0.12643 | -0.00389 | -0.016578 | -0.029595 | 0.013375 | 0.081005 | -0.12223 | 116.8591 | 116.8665 | 116.8518 | 116.8101 | 4.3471 | 4.4227 | 4.4076 | 4.4972 | 0.17678 | 0.046464 | 0.033776 | 0.020759 | 0.063729 | 0.13136 | -0.07188 | 116.9094 | 116.9169 | 116.9022 | 116.8604 | 4.3975 | 4.4731 | 4.4579 | 4.5475 | 112.5119 | 112.4515 | 112.5047 | 112.4443
849.5781 | 121.7194 | -4.5364 | 117.0639 | 0.12185 | -0.008469 | -0.016578 | -0.029595 | 0.008797 | 0.081005 | -0.12223 | 116.8957 | 116.9169 | 116.893 | 116.865 | 4.3105 | 4.3861 | 4.3709 | 4.456 | 0.1722 | 0.041885 | 0.033776 | 0.020759 | 0.059151 | 0.13136 | -0.07188 | 116.946 | 116.9672 | 116.9434 | 116.9154 | 4.3609 | 4.4365 | 4.4213 | 4.5063 | 112.5852 | 112.5248 | 112.5825 | 112.5221
851.3281 | 121.7102 | -3.8956 | 117.7368 | 0.13101 | -0.008469 | -0.021157 | -0.01586 | 0.004219 | 0.081005 | -0.13139 | 117.3764 | 117.3885 | 117.3783 | 117.2863 | 3.8344 | 3.9054 | 3.8994 | 3.9615 | 0.18136 | 0.041885 | 0.029197 | 0.034494 | 0.054573 | 0.13136 | -0.081036 | 117.4268 | 117.4389 | 117.4287 | 117.3366 | 3.8847 | 3.9558 | 3.9497 | 4.0119 | 113.542 | 113.4771 | 113.5439 | 113.479
853.0156 | 121.6644 | -6.6971 | 114.9399 | 0.13101 | 0.000689 | -0.012 | -0.020438 | 0.008797 | 0.085583 | -0.12223 | 117.7015 | 117.7228 | 117.7125 | 117.6663 | 3.4956 | 3.5804 | 3.588 | 3.6548 | 0.18136 | 0.051043 | 0.038354 | 0.029916 | 0.059151 | 0.13594 | -0.07188 | 117.7519 | 117.7731 | 117.7629 | 117.7167 | 3.546 | 3.6307 | 3.6384 | 3.7051 | 114.2059 | 114.1135 | 114.2169 | 114.1245
854.7812 | 121.7651 | -2.1378 | 119.4992 | 0.13559 | -0.00389 | -0.021157 | -0.025017 | 0.008797 | 0.090161 | -0.11765 | 119.249 | 119.2155 | 119.2508 | 119.1545 | 1.9619 | 2.0238 | 2.0359 | 2.1074 | 0.18594 | 0.046464 | 0.029197 | 0.025337 | 0.059151 | 0.14052 | -0.067301 | 119.2994 | 119.2658 | 119.3012 | 119.2049 | 2.0123 | 2.0742 | 2.0863 | 2.1577 | 117.2871 | 117.2131 | 117.2889 | 117.2149
856.4688 | 121.7606 | -5.7632 | 116.6656 | 0.13101 | 0.000689 | -0.002842 | -0.020438 | 0.013375 | 0.081005 | -0.11765 | 114.1761 | 114.2108 | 114.1918 | 114.1222 | 7.0071 | 7.1146 | 7.1225 | 7.1708 | 0.18136 | 0.051043 | 0.047512 | 0.029916 | 0.063729 | 0.13136 | -0.067301 | 114.2264 | 114.2612 | 114.2422 | 114.1725 | 7.0574 | 7.165 | 7.1729 | 7.2212 | 107.169 | 107.0535 | 107.1848 | 107.0693
858.2188 | 121.6553 | -1.2543 | 120.4559 | 0.13101 | -0.008469 | -0.012 | -0.01586 | 0.017953 | 0.081005 | -0.11765 | 120.1647 | 120.1724 | 120.1619 | 120.0657 | 1.0509 | 1.1311 | 1.1477 | 1.2055 | 0.18136 | 0.041885 | 0.038354 | 0.034494 | 0.068307 | 0.13136 | -0.067301 | 120.2151 | 120.2228 | 120.2123 | 120.1161 | 1.1012 | 1.1815 | 1.1981 | 1.2558 | 119.1139 | 119.017 | 119.1111 | 119.0142
859.9688 | 121.6827 | -37.1658 | 84.8511 | 0.13101 | -0.008469 | -0.016578 | -0.029595 | 0.004219 | 0.076426 | -0.12681 | 91.4072 | 91.3717 | 91.5293 | 91.4056 | 29.7835 | 29.7944 | 29.694 | 29.8053 | 0.18136 | 0.041885 | 0.033776 | 0.020759 | 0.054573 | 0.12678 | -0.076458 | 91.4576 | 91.422 | 91.5797 | 91.4559 | 29.8338 | 29.8447 | 29.7443 | 29.8557 | 61.6237 | 61.7132 | 61.7459 | 61.8354
861.6562 | 121.6278 | -0.89264 | 120.7993 | 0.13101 | 0.000689 | -0.016578 | -0.020438 | 0.013375 | 0.085583 | -0.11765 | 119.7893 | 119.8153 | 119.7819 | 119.6994 | 1.3896 | 1.4836 | 1.4957 | 1.5534 | 0.18136 | 0.051043 | 0.033776 | 0.029916 | 0.063729 | 0.13594 | -0.067301 | 119.8396 | 119.8656 | 119.8323 | 119.7498 | 1.44 | 1.534 | 1.5461 | 1.6038 | 118.3997 | 118.2936 | 118.3923 | 118.2862
863.4062 | 121.7468 | -0.82398 | 120.7901 | 0.14017 | -0.00389 | -0.016578 | -0.029595 | 0.013375 | 0.085583 | -0.13139 | 120.6088 | 120.6212 | 120.606 | 120.5191 | 0.58388 | 0.67331 | 0.68532 | 0.74307 | 0.19052 | 0.046464 | 0.033776 | 0.020759 | 0.063729 | 0.13594 | -0.081036 | 120.6592 | 120.6715 | 120.6564 | 120.5694 | 0.63424 | 0.72366 | 0.73568 | 0.79342 | 120.025 | 119.9235 | 120.0221 | 119.9207
865.1719 | 121.7422 | -1.1444 | 120.4468 | 0.12643 | -0.00389 | -0.021157 | -0.029595 | 0.008797 | 0.085583 | -0.12223 | 120.2838 | 120.2961 | 120.2809 | 120.1802 | 0.92724 | 1.0029 | 1.015 | 1.0819 | 0.17678 | 0.046464 | 0.029197 | 0.020759 | 0.059151 | 0.13594 | -0.07188 | 120.3341 | 120.3464 | 120.3313 | 120.2306 | 0.9776 | 1.0533 | 1.0653 | 1.1322 | 119.3565 | 119.2688 | 119.3537 | 119.266
866.9219 | 121.6782 | -1.181 | 120.4926 | 0.13559 | -0.008469 | -0.016578 | -0.025017 | 0.013375 | 0.085583 | -0.11765 | 120.1373 | 120.1633 | 120.1482 | 120.052 | 1.06 | 1.1357 | 1.1432 | 1.2146 | 0.18594 | 0.041885 | 0.033776 | 0.025337 | 0.063729 | 0.13594 | -0.067301 | 120.1876 | 120.2136 | 120.1985 | 120.1024 | 1.1104 | 1.186 | 1.1935 | 1.265 | 119.0772 | 118.9941 | 119.0882 | 119.005
868.6094 | 121.7285 | -1.2451 | 120.3644 | 0.13559 | -0.008469 | -0.016578 | -0.029595 | 0.013375 | 0.081005 | -0.12681 | 120.1464 | 120.1541 | 120.1344 | 120.0429 | 1.06 | 1.1403 | 1.1569 | 1.2192 | 0.18594 | 0.041885 | 0.033776 | 0.020759 | 0.063729 | 0.13136 | -0.076458 | 120.1968 | 120.2045 | 120.1848 | 120.0932 | 1.1104 | 1.1906 | 1.2072 | 1.2696 | 119.0864 | 118.9895 | 119.0744 | 118.9775
870.3594 | 121.6827 | -0.78278 | 120.8817 | 0.13101 | 0.000689 | -0.016578 | -0.020438 | 0.004219 | 0.081005 | -0.11765 | 120.6409 | 120.6624 | 120.6381 | 120.5328 | 0.57015 | 0.64584 | 0.65785 | 0.72018 | 0.18136 | 0.051043 | 0.033776 | 0.029916 | 0.054573 | 0.13136 | -0.067301 | 120.6912 | 120.7127 | 120.6884 | 120.5832 | 0.6205 | 0.69619 | 0.70821 | 0.77053 | 120.0707 | 119.983 | 120.0679 | 119.9802
872.1094 | 121.701 | -0.50354 | 121.138 | 0.13101 | -0.008469 | -0.021157 | -0.034174 | 0.013375 | 0.085583 | -0.12681 | 120.9156 | 120.9279 | 120.9219 | 120.8167 | 0.29088 | 0.36657 | 0.39231 | 0.45007 | 0.18136 | 0.041885 | 0.029197 | 0.01618 | 0.063729 | 0.13594 | -0.076458 | 120.966 | 120.9783 | 120.9723 | 120.8671 | 0.34123 | 0.41693 | 0.44266 | 0.50042 | 120.6247 | 120.5233 | 120.631 | 120.5296
873.7969 | 121.7377 | -0.66834 | 120.9412 | 0.13101 | -0.008469 | -0.021157 | -0.025017 | 0.022531 | 0.085583 | -0.11765 | 120.7187 | 120.7402 | 120.725 | 120.629 | 0.48316 | 0.56343 | 0.57544 | 0.64235 | 0.18136 | 0.041885 | 0.029197 | 0.025337 | 0.072885 | 0.13594 | -0.067301 | 120.7691 | 120.7906 | 120.7754 | 120.6793 | 0.53352 | 0.61379 | 0.62579 | 0.69271 | 120.2356 | 120.1433 | 120.2419 | 120.1496
875.5469 | 121.6827 | -0.77362 | 120.9229 | 0.13559 | -0.00389 | -0.021157 | -0.025017 | 0.017953 | 0.090161 | -0.11765 | 120.6775 | 120.6853 | 120.693 | 120.5878 | 0.52437 | 0.60463 | 0.62123 | 0.6744 | 0.18594 | 0.046464 | 0.029197 | 0.025337 | 0.068307 | 0.14052 | -0.067301 | 120.7279 | 120.7356 | 120.7433 | 120.6381 | 0.57472 | 0.65499 | 0.67158 | 0.72475 | 120.1532 | 120.0563 | 120.1686 | 120.0718
877.2969 | 121.7834 | -0.59052 | 121.0007 | 0.13101 | -0.00389 | -0.012 | -0.029595 | 0.008797 | 0.081005 | -0.12223 | 120.4761 | 120.4975 | 120.4732 | 120.3817 | 0.72581 | 0.81065 | 0.82267 | 0.88957 | 0.18136 | 0.046464 | 0.038354 | 0.020759 | 0.059151 | 0.13136 | -0.07188 | 120.5264 | 120.5479 | 120.5236 | 120.4321 | 0.77616 | 0.861 | 0.87303 | 0.93993 | 119.7503 | 119.6534 | 119.7474 | 119.6506
879.0469 | 121.669 | -0.59052 | 121.106 | 0.13559 | 0.000689 | -0.012 | -0.025017 | 0.013375 | 0.085583 | -0.11765 | 120.8698 | 120.8776 | 120.8715 | 120.7755 | 0.34582 | 0.42151 | 0.43351 | 0.50501 | 0.18594 | 0.051043 | 0.038354 | 0.025337 | 0.063729 | 0.13594 | -0.067301 | 120.9202 | 120.9279 | 120.9219 | 120.8259 | 0.39617 | 0.47187 | 0.48386 | 0.55536 | 120.524 | 120.4363 | 120.5257 | 120.438
880.75 | 121.6415 | -0.5722 | 121.1288 | 0.13559 | 0.000689 | -0.012 | -0.025017 | 0.013375 | 0.090161 | -0.11765 | 120.8607 | 120.8776 | 120.867 | 120.7709 | 0.3504 | 0.43067 | 0.44725 | 0.50501 | 0.18594 | 0.051043 | 0.038354 | 0.025337 | 0.063729 | 0.14052 | -0.067301 | 120.911 | 120.9279 | 120.9173 | 120.8213 | 0.40075 | 0.48102 | 0.4976 | 0.55536 | 120.5103 | 120.4134 | 120.5166 | 120.4197
882.5 | 121.7102 | -0.48065 | 121.17 | 0.13101 | -0.00389 | -0.016578 | -0.020438 | 0.013375 | 0.090161 | -0.12223 | 120.6592 | 120.6761 | 120.6564 | 120.5649 | 0.54726 | 0.63668 | 0.64412 | 0.70644 | 0.18136 | 0.046464 | 0.033776 | 0.029916 | 0.063729 | 0.14052 | -0.07188 | 120.7096 | 120.7265 | 120.7067 | 120.6152 | 0.59761 | 0.68704 | 0.69447 | 0.7568 | 120.112 | 120.0151 | 120.1091 | 120.0122
884.1719 | 121.6919 | -0.63629 | 121.0327 | 0.13559 | 0.000689 | -0.016578 | -0.025017 | 0.013375 | 0.085583 | -0.11765 | 120.7599 | 120.7768 | 120.7617 | 120.6702 | 0.44654 | 0.52681 | 0.53881 | 0.60572 | 0.18594 | 0.051043 | 0.033776 | 0.025337 | 0.063729 | 0.13594 | -0.067301 | 120.8103 | 120.8272 | 120.812 | 120.7205 | 0.49689 | 0.57716 | 0.58917 | 0.65608 | 120.3134 | 120.2211 | 120.3151 | 120.2229
885.9219 | 121.7056 | -1.0162 | 120.639 | 0.13559 | -0.013048 | -0.021157 | -0.025017 | 0.013375 | 0.085583 | -0.11765 | 120.4211 | 120.438 | 120.4229 | 120.3268 | 0.78074 | 0.86558 | 0.87762 | 0.93993 | 0.18594 | 0.037306 | 0.029197 | 0.025337 | 0.063729 | 0.13594 | -0.067301 | 120.4715 | 120.4884 | 120.4732 | 120.3771 | 0.8311 | 0.91594 | 0.92797 | 0.99029 | 119.6404 | 119.5435 | 119.6421 | 119.5453
887.6094 | 121.7194 | -0.46234 | 121.1792 | 0.14017 | -0.008469 | -0.012 | -0.020438 | 0.008797 | 0.085583 | -0.12681 | 120.3387 | 120.3556 | 120.3359 | 120.2489 | 0.87689 | 0.94341 | 0.96003 | 1.0269 | 0.19052 | 0.041885 | 0.038354 | 0.029916 | 0.059151 | 0.13594 | -0.076458 | 120.3891 | 120.4059 | 120.3862 | 120.2993 | 0.92724 | 0.99377 | 1.0104 | 1.0773 | 119.4618 | 119.3787 | 119.459 | 119.3759
889.3594 | 121.6278 | -0.64545 | 121.0556 | 0.13559 | -0.00389 | -0.012 | -0.01586 | 0.013375 | 0.085583 | -0.11308 | 120.7554 | 120.7585 | 120.7479 | 120.6473 | 0.46485 | 0.54054 | 0.55255 | 0.61946 | 0.18594 | 0.046464 | 0.038354 | 0.034494 | 0.063729 | 0.13594 | -0.062723 | 120.8057 | 120.8089 | 120.7983 | 120.6976 | 0.5152 | 0.5909 | 0.6029 | 0.66981 | 120.2905 | 120.2028 | 120.2831 | 120.1954
891.1094 | 121.6827 | -0.74616 | 120.8908 | 0.13559 | -0.008469 | -0.012 | -0.020438 | 0.017953 | 0.085583 | -0.11765 | 120.444 | 120.4563 | 120.4549 | 120.3542 | 0.7487 | 0.83812 | 0.85014 | 0.91246 | 0.18594 | 0.041885 | 0.038354 | 0.029916 | 0.068307 | 0.13594 | -0.067301 | 120.4944 | 120.5067 | 120.5053 | 120.4046 | 0.79905 | 0.88847 | 0.9005 | 0.96282 | 119.6953 | 119.5939 | 119.7062 | 119.6048
892.8125 | 121.637 | -0.76446 | 120.9183 | 0.14474 | -0.00389 | -0.016578 | -0.025017 | 0.013375 | 0.090161 | -0.11308 | 120.8057 | 120.8272 | 120.8074 | 120.7205 | 0.39618 | 0.47187 | 0.49303 | 0.55079 | 0.1951 | 0.046464 | 0.033776 | 0.025337 | 0.063729 | 0.14052 | -0.062723 | 120.8561 | 120.8776 | 120.8578 | 120.7709 | 0.44653 | 0.52222 | 0.54338 | 0.60114 | 120.4095 | 120.3127 | 120.4113 | 120.3144
894.5625 | 121.7377 | -0.86517 | 120.7306 | 0.13101 | -0.008469 | -0.016578 | -0.029595 | 0.017953 | 0.085583 | -0.12223 | 120.6409 | 120.6486 | 120.6426 | 120.542 | 0.56557 | 0.64584 | 0.67159 | 0.72018 | 0.18136 | 0.041885 | 0.033776 | 0.020759 | 0.068307 | 0.13594 | -0.07188 | 120.6912 | 120.699 | 120.693 | 120.5923 | 0.61592 | 0.69619 | 0.72194 | 0.77053 | 120.0753 | 119.9693 | 120.0771 | 119.971
896.25 | 121.6827 | -0.55847 | 121.0327 | 0.13101 | -0.00389 | -0.025735 | -0.025017 | 0.017953 | 0.081005 | -0.12681 | 120.8607 | 120.8684 | 120.8532 | 120.7572 | 0.34582 | 0.42609 | 0.44267 | 0.50043 | 0.18136 | 0.046464 | 0.024619 | 0.025337 | 0.068307 | 0.13136 | -0.076458 | 120.911 | 120.9188 | 120.9036 | 120.8075 | 0.39617 | 0.47644 | 0.49302 | 0.55078 | 120.5148 | 120.418 | 120.5074 | 120.4106
897.9844 | 121.6095 | -3.2547 | 118.3456 | 0.13559 | -0.00389 | -0.012 | -0.025017 | 0.008797 | 0.085583 | -0.11308 | 119.7069 | 119.7054 | 119.7499 | 119.6399 | 1.4766 | 1.5386 | 1.569 | 1.6267 | 0.18594 | 0.046464 | 0.038354 | 0.025337 | 0.059151 | 0.13594 | -0.062723 | 119.7572 | 119.7557 | 119.8002 | 119.6903 | 1.527 | 1.5889 | 1.6193 | 1.677 | 118.2303 | 118.1379 | 118.2732 | 118.1809
899.6875 | 121.6919 | -98.8403 | 22.4854 | 0.12643 | -0.058836 | -0.062364 | -0.070802 | -0.027827 | 0.039799 | -0.16344 | 61.6561 | 61.2064 | 61.9903 | 61.6419 | 59.6148 | 59.4419 | 59.275 | 59.362 | 0.17678 | -0.008482 | -0.01201 | -0.020448 | 0.022527 | 0.090153 | -0.11308 | 61.7065 | 61.2568 | 62.0406 | 61.6922 | 59.6652 | 59.4923 | 59.3253 | 59.4124 | 2.0413 | 2.3812 | 2.3754 | 2.7153
901.4531 | 121.701 | -109.758 | 11.7004 | 0.13101 | -0.00389 | -0.021157 | -0.034174 | 0.008797 | 0.081005 | -0.12681 | 11.6636 | 11.7415 | 11.7116 | 11.6938 | 109.4712 | 109.5672 | 109.3625 | 109.4472 | 0.18136 | 0.046464 | 0.029197 | 0.01618 | 0.059151 | 0.13136 | -0.076458 | 11.7139 | 11.7918 | 11.762 | 11.7442 | 109.5215 | 109.6175 | 109.4129 | 109.4976 | -97.8076 | -97.699 | -97.7596 | -97.6509
903.2031 | 121.669 | -110.8475 | 10.6155 | 0.13559 | -0.008469 | -0.021157 | -0.025017 | 0.013375 | 0.085583 | -0.11765 | 10.5372 | 10.6151 | 10.5762 | 10.5628 | 110.6157 | 110.7071 | 110.5071 | 110.5918 | 0.18594 | 0.041885 | 0.029197 | 0.025337 | 0.063729 | 0.13594 | -0.067301 | 10.5876 | 10.6654 | 10.6265 | 10.6131 | 110.6661 | 110.7575 | 110.5575 | 110.6421 | -100.0785 | -99.9699 | -100.0395 | -99.9309
904.9688 | 121.8063 | -111.3281 | 10.1028 | 0.13101 | -0.013048 | -0.021157 | -0.020438 | 0.004219 | 0.081005 | -0.11765 | 9.9878 | 10.0748 | 10.0222 | 10.0179 | 111.1742 | 111.2611 | 111.0611 | 111.1457 | 0.18136 | 0.037306 | 0.029197 | 0.029916 | 0.054573 | 0.13136 | -0.067301 | 10.0382 | 10.1251 | 10.0726 | 10.0682 | 111.2246 | 111.3114 | 111.1115 | 111.1961 | -101.1864 | -101.0733 | -101.152 | -101.0389
906.6562 | 121.8475 | -111.6394 | 9.7916 | 0.13101 | -0.008469 | -0.016578 | -0.025017 | 0.013375 | 0.085583 | -0.12223 | 9.6719 | 9.7634 | 9.7063 | 9.7065 | 111.4901 | 111.5815 | 111.3358 | 111.4708 | 0.18136 | 0.041885 | 0.033776 | 0.025337 | 0.063729 | 0.13594 | -0.07188 | 9.7223 | 9.8138 | 9.7567 | 9.7569 | 111.5405 | 111.6319 | 111.3862 | 111.5211 | -101.8182 | -101.6639 | -101.7838 | -101.6295
908.4062 | 121.7239 | -111.8042 | 9.7137 | 0.13101 | -0.008469 | -0.016578 | -0.034174 | 0.013375 | 0.081005 | -0.12681 | 9.5529 | 9.6444 | 9.5827 | 9.5829 | 111.6183 | 111.7051 | 111.4594 | 111.5944 | 0.18136 | 0.041885 | 0.033776 | 0.01618 | 0.063729 | 0.13136 | -0.076458 | 9.6032 | 9.6947 | 9.6331 | 9.6332 | 111.6687 | 111.7555 | 111.5098 | 111.6447 | -102.0655 | -101.9066 | -102.0356 | -101.8767
910.0938 | 121.7468 | -111.9919 | 9.4666 | 0.13101 | -0.008469 | -0.012 | -0.020438 | 0.013375 | 0.085583 | -0.11765 | 9.3789 | 9.4521 | 9.3996 | 9.4043 | 111.8106 | 111.8928 | 111.6471 | 111.7867 | 0.18136 | 0.041885 | 0.038354 | 0.029916 | 0.063729 | 0.13594 | -0.067301 | 9.4292 | 9.5024 | 9.4499 | 9.4546 | 111.861 | 111.9432 | 111.6975 | 111.837 | -102.4317 | -102.2682 | -102.411 | -102.2476
911.8438 | 121.6827 | -111.9415 | 9.581 | 0.13559 | 0.000689 | -0.016578 | -0.020438 | 0.017953 | 0.090161 | -0.12223 | 9.4476 | 9.5345 | 9.4774 | 9.4867 | 111.7419 | 111.8242 | 111.5785 | 111.7134 | 0.18594 | 0.051043 | 0.033776 | 0.029916 | 0.068307 | 0.14052 | -0.07188 | 9.4979 | 9.5848 | 9.5278 | 9.5371 | 111.7923 | 111.8745 | 111.6288 | 111.7638 | -102.2944 | -102.1309 | -102.2645 | -102.1011
913.5938 | 121.7834 | -112.0148 | 9.4437 | 0.13559 | -0.013048 | -0.021157 | -0.025017 | 0.008797 | 0.085583 | -0.11765 | 9.3194 | 9.4154 | 9.3538 | 9.3585 | 111.8701 | 111.9569 | 111.7066 | 111.8462 | 0.18594 | 0.037306 | 0.029197 | 0.025337 | 0.059151 | 0.13594 | -0.067301 | 9.3697 | 9.4658 | 9.4041 | 9.4088 | 111.9205 | 112.0073 | 111.757 | 111.8965 | -102.5508 | -102.3873 | -102.5163 | -102.3529
915.3438 | 121.7285 | -111.9049 | 9.5856 | 0.13101 | -0.008469 | -0.016578 | -0.025017 | 0.013375 | 0.085583 | -0.12223 | 9.3789 | 9.4749 | 9.4133 | 9.418 | 111.806 | 111.8974 | 111.6471 | 111.7775 | 0.18136 | 0.041885 | 0.033776 | 0.025337 | 0.063729 | 0.13594 | -0.07188 | 9.4292 | 9.5253 | 9.4637 | 9.4684 | 111.8564 | 111.9478 | 111.6975 | 111.8279 | -102.4271 | -102.2682 | -102.3927 | -102.2338
917.0938 | 121.701 | -111.9324 | 9.5901 | 0.13101 | -0.008469 | -0.016578 | -0.029595 | 0.017953 | 0.085583 | -0.12681 | 9.475 | 9.5665 | 9.5094 | 9.5096 | 111.7282 | 111.7967 | 111.5601 | 111.6951 | 0.18136 | 0.041885 | 0.033776 | 0.020759 | 0.068307 | 0.13594 | -0.076458 | 9.5254 | 9.6169 | 9.5598 | 9.56 | 111.7785 | 111.8471 | 111.6105 | 111.7455 | -102.2532 | -102.0851 | -102.2187 | -102.0507
918.8438 | 121.6827 | -111.8729 | 9.668 | 0.13559 | -0.00389 | -0.012 | -0.029595 | 0.013375 | 0.085583 | -0.12223 | 9.6032 | 9.6902 | 9.6376 | 9.6378 | 111.5954 | 111.6822 | 111.4319 | 111.5715 | 0.18594 | 0.046464 | 0.038354 | 0.020759 | 0.063729 | 0.13594 | -0.07188 | 9.6536 | 9.7405 | 9.688 | 9.6882 | 111.6458 | 111.7326 | 111.4823 | 111.6218 | -101.9922 | -101.8287 | -101.9578 | -101.7943
920.5469 | 121.8155 | -111.6852 | 9.7595 | 0.12643 | -0.00389 | -0.016578 | -0.020438 | 0.013375 | 0.081005 | -0.12223 | 9.6215 | 9.7222 | 9.6605 | 9.6607 | 111.5771 | 111.6639 | 111.4136 | 111.5486 | 0.17678 | 0.046464 | 0.033776 | 0.029916 | 0.063729 | 0.13136 | -0.07188 | 9.6719 | 9.7726 | 9.7109 | 9.7111 | 111.6275 | 111.7143 | 111.464 | 111.599 | -101.9556 | -101.7921 | -101.9166 | -101.7531
922.2969 | 121.7789 | -111.6852 | 9.7961 | 0.14017 | -0.013048 | -0.021157 | -0.025017 | 0.013375 | 0.085583 | -0.12223 | 9.6627 | 9.7543 | 9.6972 | 9.7019 | 111.5359 | 111.6227 | 111.3724 | 111.5074 | 0.19052 | 0.037306 | 0.029197 | 0.025337 | 0.063729 | 0.13594 | -0.07188 | 9.7131 | 9.8046 | 9.7475 | 9.7523 | 111.5863 | 111.6731 | 111.4228 | 111.5577 | -101.8732 | -101.7097 | -101.8388 | -101.6753
923.9844 | 121.6736 | -111.9965 | 9.5535 | 0.13559 | 0.000689 | -0.012 | -0.020438 | 0.022531 | 0.090161 | -0.11765 | 9.4155 | 9.5116 | 9.4454 | 9.4592 | 111.7923 | 111.8699 | 111.6242 | 111.7638 | 0.18594 | 0.051043 | 0.038354 | 0.029916 | 0.072885 | 0.14052 | -0.067301 | 9.4659 | 9.5619 | 9.4957 | 9.5096 | 111.8426 | 111.9203 | 111.6746 | 111.8141 | -102.3768 | -102.2087 | -102.3469 | -102.1789
925.7344 | 121.701 | -112.1979 | 9.3384 | 0.13101 | -0.008469 | -0.016578 | -0.025017 | 0.004219 | 0.090161 | -0.12223 | 9.1774 | 9.2643 | 9.2164 | 9.2165 | 112.0212 | 112.1126 | 111.8761 | 112.0018 | 0.18136 | 0.041885 | 0.033776 | 0.025337 | 0.054573 | 0.14052 | -0.07188 | 9.2278 | 9.3147 | 9.2668 | 9.2669 | 112.0716 | 112.1629 | 111.9264 | 112.0522 | -102.8438 | -102.6986 | -102.8048 | -102.6596
927.4844 | 121.6873 | -112.3123 | 9.2011 | 0.13559 | -0.00389 | -0.016578 | -0.025017 | 0.008797 | 0.085583 | -0.12223 | 9.0767 | 9.1727 | 9.1157 | 9.1204 | 112.1265 | 112.2179 | 111.963 | 112.1071 | 0.18594 | 0.046464 | 0.033776 | 0.025337 | 0.059151 | 0.13594 | -0.07188 | 9.1271 | 9.2231 | 9.1661 | 9.1707 | 112.1768 | 112.2682 | 112.0134 | 112.1575 | -103.0498 | -102.8863 | -103.0108 | -102.8473
929.2344 | 121.6644 | -112.4222 | 9.1324 | 0.13559 | -0.008469 | -0.016578 | -0.029595 | 0.008797 | 0.085583 | -0.11308 | 8.9897 | 9.0812 | 9.0287 | 9.0334 | 112.2226 | 112.3094 | 112.0546 | 112.1941 | 0.18594 | 0.041885 | 0.033776 | 0.020759 | 0.059151 | 0.13594 | -0.062723 | 9.0401 | 9.1315 | 9.0791 | 9.0837 | 112.273 | 112.3598 | 112.105 | 112.2445 | -103.2329 | -103.0649 | -103.1939 | -103.0259
930.9844 | 121.8109 | -112.2345 | 9.2331 | 0.13101 | -0.00389 | -0.016578 | -0.034174 | 0.017953 | 0.081005 | -0.11765 | 8.9989 | 9.0903 | 9.0287 | 9.0425 | 112.2226 | 112.3003 | 112.0546 | 112.1941 | 0.18136 | 0.046464 | 0.033776 | 0.01618 | 0.068307 | 0.13136 | -0.067301 | 9.0492 | 9.1407 | 9.0791 | 9.0929 | 112.273 | 112.3506 | 112.105 | 112.2445 | -103.2238 | -103.0557 | -103.1939 | -103.0259
932.6719 | 121.7468 | -111.5616 | 9.9792 | 0.13559 | -0.00389 | -0.025735 | -0.025017 | 0.017953 | 0.090161 | -0.12223 | 9.855 | 9.942 | 9.8482 | 9.8942 | 111.3574 | 111.4533 | 111.1939 | 111.338 | 0.18594 | 0.046464 | 0.024619 | 0.025337 | 0.068307 | 0.14052 | -0.07188 | 9.9054 | 9.9923 | 9.8986 | 9.9446 | 111.4077 | 111.5037 | 111.2442 | 111.3884 | -101.5023 | -101.3388 | -101.5091 | -101.3456
934.4219 | 121.7834 | -111.2366 | 10.2722 | 0.12643 | -0.00389 | -0.025735 | -0.025017 | 0.004219 | 0.081005 | -0.11765 | 10.0794 | 10.1755 | 10.0817 | 10.1278 | 111.1285 | 111.2107 | 110.9695 | 111.0999 | 0.17678 | 0.046464 | 0.024619 | 0.025337 | 0.054573 | 0.13136 | -0.067301 | 10.1297 | 10.2259 | 10.1321 | 10.1781 | 111.1788 | 111.2611 | 111.0199 | 111.1503 | -101.0491 | -100.8901 | -101.0467 | -100.8878
936.1719 | 121.7972 | -110.9894 | 10.5194 | 0.12643 | -0.008469 | -0.012 | -0.029595 | 0.008797 | 0.081005 | -0.12223 | 10.3816 | 10.4686 | 10.3702 | 10.4208 | 110.84 | 110.9223 | 110.6765 | 110.8069 | 0.17678 | 0.041885 | 0.038354 | 0.020759 | 0.059151 | 0.13136 | -0.07188 | 10.4319 | 10.5189 | 10.4205 | 10.4712 | 110.8904 | 110.9726 | 110.7269 | 110.8573 | -100.4585 | -100.2949 | -100.4699 | -100.3063
937.8594 | 121.7422 | -111.6028 | 9.9243 | 0.13559 | -0.008469 | -0.012 | -0.029595 | 0.013375 | 0.090161 | -0.12223 | 9.8413 | 9.9283 | 9.8757 | 9.8713 | 111.3803 | 111.4717 | 111.2213 | 111.3517 | 0.18594 | 0.041885 | 0.038354 | 0.020759 | 0.063729 | 0.14052 | -0.07188 | 9.8917 | 9.9786 | 9.9261 | 9.9217 | 111.4306 | 111.522 | 111.2717 | 111.4021 | -101.5389 | -101.38 | -101.5045 | -101.3456
939.5938 | 121.6187 | -83.931 | 37.3215 | 0.13559 | 0.000689 | -0.025735 | -0.025017 | 0.013375 | 0.085583 | -0.12223 | 39.6656 | 39.6722 | 39.7353 | 39.6625 | 81.407 | 81.4945 | 81.2878 | 81.383 | 0.18594 | 0.051043 | 0.024619 | 0.025337 | 0.063729 | 0.13594 | -0.07188 | 39.716 | 39.7226 | 39.7856 | 39.7129 | 81.4573 | 81.5448 | 81.3382 | 81.4334 | -41.7413 | -41.6222 | -41.6717 | -41.5526
941.3438 | 121.582 | -96.7163 | 24.5087 | 0.13559 | -0.008469 | -0.016578 | -0.029595 | 0.008797 | 0.081005 | -0.11765 | 25.2571 | 25.3039 | 25.3045 | 25.2752 | 95.7137 | 95.7964 | 95.5907 | 95.699 | 0.18594 | 0.041885 | 0.033776 | 0.020759 | 0.059151 | 0.13136 | -0.067301 | 25.3075 | 25.3543 | 25.3549 | 25.3256 | 95.7641 | 95.8467 | 95.6411 | 95.7493 | -70.4566 | -70.3336 | -70.4092 | -70.2862
943.0312 | 121.4722 | -113.9832 | 7.0404 | 0.12643 | -0.00389 | -0.012 | -0.025017 | 0.017953 | 0.085583 | -0.11765 | 7.0438 | 7.1306 | 7.0784 | 7.0873 | 113.7929 | 113.8797 | 113.6799 | 113.769 | 0.17678 | 0.046464 | 0.038354 | 0.025337 | 0.068307 | 0.13594 | -0.067301 | 7.0942 | 7.1809 | 7.1287 | 7.1376 | 113.8433 | 113.9301 | 113.7303 | 113.8194 | -106.7491 | -106.6361 | -106.7146 | -106.6016
944.7812 | 121.4172 | -114.8666 | 6.1981 | 0.13101 | -0.008469 | -0.021157 | -0.025017 | 0.013375 | 0.081005 | -0.11765 | 6.0824 | 6.1828 | 6.1215 | 6.1349 | 114.6857 | 114.7724 | 114.5224 | 114.648 | 0.18136 | 0.041885 | 0.029197 | 0.025337 | 0.063729 | 0.13136 | -0.067301 | 6.1327 | 6.2331 | 6.1719 | 6.1852 | 114.736 | 114.8228 | 114.5727 | 114.6984 | -108.6033 | -108.44 | -108.5642 | -108.4008
946.5312 | 121.2296 | -115.2283 | 5.8319 | 0.13559 | -0.008469 | -0.016578 | -0.025017 | 0.013375 | 0.085583 | -0.11765 | 5.7024 | 5.7936 | 5.7369 | 5.7548 | 115.0336 | 115.125 | 114.8657 | 114.9914 | 0.18594 | 0.041885 | 0.033776 | 0.025337 | 0.063729 | 0.13594 | -0.067301 | 5.7527 | 5.8439 | 5.7873 | 5.8051 | 115.084 | 115.1753 | 114.9161 | 115.0417 | -109.3313 | -109.1634 | -109.2967 | -109.1288
948.2344 | 121.2433 | -115.3839 | 5.658 | 0.13101 | -0.00389 | -0.012 | -0.020438 | 0.013375 | 0.085583 | -0.11765 | 5.4643 | 5.5646 | 5.4989 | 5.5075 | 115.2442 | 115.3264 | 115.0809 | 115.2157 | 0.18136 | 0.046464 | 0.038354 | 0.029916 | 0.063729 | 0.13594 | -0.067301 | 5.5146 | 5.615 | 5.5492 | 5.5579 | 115.2946 | 115.3767 | 115.1313 | 115.2661 | -109.78 | -109.6167 | -109.7454 | -109.582
949.9844 | 121.2524 | -115.5167 | 5.4611 | 0.13101 | -0.013048 | -0.021157 | -0.025017 | 0.008797 | 0.081005 | -0.11308 | 5.3407 | 5.4364 | 5.3753 | 5.3885 | 115.3495 | 115.4317 | 115.1771 | 115.3073 | 0.18136 | 0.037306 | 0.029197 | 0.025337 | 0.059151 | 0.13136 | -0.062723 | 5.391 | 5.4868 | 5.4256 | 5.4388 | 115.3999 | 115.482 | 115.2274 | 115.3576 | -110.0089 | -109.8364 | -109.9743 | -109.8018
951.6875 | 121.1609 | -115.7181 | 5.3009 | 0.12643 | -0.008469 | -0.021157 | -0.025017 | 0.017953 | 0.081005 | -0.11765 | 5.1667 | 5.2624 | 5.2059 | 5.219 | 115.4869 | 115.569 | 115.3236 | 115.4629 | 0.17678 | 0.041885 | 0.029197 | 0.025337 | 0.068307 | 0.13136 | -0.067301 | 5.217 | 5.3128 | 5.2562 | 5.2694 | 115.5372 | 115.6194 | 115.3739 | 115.5133 | -110.3202 | -110.1569 | -110.281 | -110.1177
953.4375 | 121.1563 | -115.7318 | 5.2048 | 0.13559 | -0.00389 | -0.021157 | -0.020438 | 0.013375 | 0.085583 | -0.12223 | 5.0705 | 5.1709 | 5.1097 | 5.1183 | 115.5601 | 115.6377 | 115.3877 | 115.5316 | 0.18594 | 0.046464 | 0.029197 | 0.029916 | 0.063729 | 0.13594 | -0.07188 | 5.1209 | 5.2212 | 5.1601 | 5.1687 | 115.6105 | 115.6881 | 115.438 | 115.582 | -110.4896 | -110.3172 | -110.4504 | -110.278
955.1875 | 121.1792 | -115.773 | 5.0858 | 0.14017 | -0.013048 | -0.016578 | -0.025017 | 0.017953 | 0.085583 | -0.12223 | 4.9698 | 5.0655 | 5.0136 | 5.0221 | 115.6471 | 115.7338 | 115.4747 | 115.6094 | 0.19052 | 0.037306 | 0.033776 | 0.025337 | 0.068307 | 0.13594 | -0.07188 | 5.0201 | 5.1159 | 5.0639 | 5.0725 | 115.6975 | 115.7842 | 115.525 | 115.6598 | -110.6773 | -110.5049 | -110.6335 | -110.4611
956.9531 | 121.1838 | -115.7776 | 5.0812 | 0.13101 | -0.00389 | -0.021157 | -0.025017 | 0.013375 | 0.085583 | -0.12223 | 4.9606 | 5.061 | 5.0044 | 5.013 | 115.6196 | 115.7109 | 115.4518 | 115.5911 | 0.18136 | 0.046464 | 0.029197 | 0.025337 | 0.063729 | 0.13594 | -0.07188 | 5.011 | 5.1113 | 5.0548 | 5.0633 | 115.67 | 115.7613 | 115.5021 | 115.6415 | -110.659 | -110.4911 | -110.6152 | -110.4474
958.6562 | 121.0281 | -115.892 | 5.0262 | 0.14017 | -0.008469 | -0.016578 | -0.029595 | 0.013375 | 0.085583 | -0.11308 | 4.8599 | 4.9602 | 4.8991 | 4.9168 | 115.702 | 115.7842 | 115.5388 | 115.669 | 0.19052 | 0.041885 | 0.033776 | 0.020759 | 0.063729 | 0.13594 | -0.062723 | 4.9103 | 5.0106 | 4.9495 | 4.9672 | 115.7524 | 115.8345 | 115.5891 | 115.7193 | -110.8421 | -110.6789 | -110.8029 | -110.6396
960.4219 | 121.0327 | -115.8188 | 5.0674 | 0.12643 | -0.013048 | -0.021157 | -0.025017 | 0.013375 | 0.081005 | -0.11308 | 4.8874 | 4.9923 | 4.9312 | 4.9489 | 115.6425 | 115.7247 | 115.4792 | 115.6094 | 0.17678 | 0.037306 | 0.029197 | 0.025337 | 0.063729 | 0.13136 | -0.062723 | 4.9377 | 5.0426 | 4.9815 | 4.9992 | 115.6929 | 115.775 | 115.5296 | 115.6598 | -110.7552 | -110.5919 | -110.7114 | -110.5481
962.1094 | 120.9915 | -115.9103 | 4.9347 | 0.13101 | -0.022205 | -0.012 | -0.020438 | 0.013375 | 0.090161 | -0.11308 | 4.7867 | 4.8824 | 4.8167 | 4.8344 | 115.7249 | 115.8117 | 115.5662 | 115.6964 | 0.18136 | 0.028149 | 0.038354 | 0.029916 | 0.063729 | 0.14052 | -0.062723 | 4.837 | 4.9327 | 4.8671 | 4.8848 | 115.7753 | 115.862 | 115.6166 | 115.7468 | -110.9383 | -110.7796 | -110.9082 | -110.7495
963.8594 | 120.9686 | -115.9103 | 4.9393 | 0.13559 | -0.00389 | -0.012 | -0.020438 | 0.008797 | 0.090161 | -0.11765 | 4.7683 | 4.8778 | 4.803 | 4.8298 | 115.7204 | 115.8071 | 115.5479 | 115.6964 | 0.18594 | 0.046464 | 0.038354 | 0.029916 | 0.059151 | 0.14052 | -0.067301 | 4.8187 | 4.9282 | 4.8533 | 4.8802 | 115.7707 | 115.8574 | 115.5983 | 115.7468 | -110.952 | -110.7796 | -110.9174 | -110.7449
965.5469 | 120.9503 | -115.7776 | 5.0354 | 0.13559 | -0.00389 | -0.016578 | -0.025017 | 0.013375 | 0.085583 | -0.11308 | 4.8874 | 4.9969 | 4.9266 | 4.9397 | 115.5922 | 115.6606 | 115.406 | 115.5453 | 0.18594 | 0.046464 | 0.033776 | 0.025337 | 0.063729 | 0.13594 | -0.062723 | 4.9377 | 5.0472 | 4.9769 | 4.9901 | 115.6425 | 115.7109 | 115.4563 | 115.5957 | -110.7048 | -110.5186 | -110.6656 | -110.4794
967.2969 | 121.0236 | -115.8508 | 4.8706 | 0.13559 | -0.00389 | -0.021157 | -0.029595 | 0.008797 | 0.071848 | -0.12223 | 4.7409 | 4.8412 | 4.7801 | 4.7886 | 115.7066 | 115.7979 | 115.5388 | 115.669 | 0.18594 | 0.046464 | 0.029197 | 0.020759 | 0.059151 | 0.1222 | -0.07188 | 4.7912 | 4.8915 | 4.8304 | 4.839 | 115.757 | 115.8483 | 115.5891 | 115.7193 | -110.9658 | -110.7979 | -110.9265 | -110.7587
969.0469 | 120.9686 | -115.8417 | 4.8294 | 0.13559 | -0.013048 | -0.016578 | -0.025017 | 0.008797 | 0.085583 | -0.11765 | 4.7134 | 4.8229 | 4.748 | 4.7703 | 115.7158 | 115.8025 | 115.5479 | 115.6827 | 0.18594 | 0.037306 | 0.033776 | 0.025337 | 0.059151 | 0.13594 | -0.067301 | 4.7637 | 4.8732 | 4.7984 | 4.8207 | 115.7661 | 115.8529 | 115.5983 | 115.733 | -111.0024 | -110.8345 | -110.9677 | -110.7999
970.8125 | 120.932 | -115.8417 | 4.8614 | 0.13559 | -0.00389 | -0.025735 | -0.025017 | 0.017953 | 0.085583 | -0.11765 | 4.7042 | 4.8046 | 4.7435 | 4.7657 | 115.6975 | 115.7934 | 115.5388 | 115.6644 | 0.18594 | 0.046464 | 0.024619 | 0.025337 | 0.068307 | 0.13594 | -0.067301 | 4.7546 | 4.8549 | 4.7938 | 4.8161 | 115.7478 | 115.8437 | 115.5891 | 115.7147 | -110.9932 | -110.8345 | -110.954 | -110.7953
972.5 | 120.8771 | -115.8508 | 4.8843 | 0.12643 | -0.013048 | -0.016578 | -0.020438 | 0.017953 | 0.085583 | -0.12223 | 4.7042 | 4.8046 | 4.7435 | 4.7566 | 115.6883 | 115.7659 | 115.5113 | 115.6552 | 0.17678 | 0.037306 | 0.033776 | 0.029916 | 0.068307 | 0.13594 | -0.07188 | 4.7546 | 4.8549 | 4.7938 | 4.8069 | 115.7387 | 115.8162 | 115.5616 | 115.7056 | -110.9841 | -110.8071 | -110.9449 | -110.7678
974.25 | 120.8954 | -115.8829 | 4.8065 | 0.13559 | -0.00389 | -0.016578 | -0.01586 | 0.013375 | 0.085583 | -0.11308 | 4.6218 | 4.7221 | 4.661 | 4.6833 | 115.7433 | 115.8254 | 115.5754 | 115.7147 | 0.18594 | 0.046464 | 0.033776 | 0.034494 | 0.063729 | 0.13594 | -0.062723 | 4.6722 | 4.7725 | 4.7114 | 4.7337 | 115.7936 | 115.8758 | 115.6257 | 115.7651 | -111.1214 | -110.9536 | -111.0822 | -110.9143
976 | 120.9412 | -115.8096 | 4.8203 | 0.13559 | -0.008469 | -0.016578 | -0.020438 | 0.013375 | 0.085583 | -0.12681 | 4.6768 | 4.7725 | 4.7114 | 4.7337 | 115.67 | 115.7521 | 115.5021 | 115.6415 | 0.18594 | 0.041885 | 0.033776 | 0.029916 | 0.063729 | 0.13594 | -0.076458 | 4.7271 | 4.8229 | 4.7618 | 4.784 | 115.7204 | 115.8025 | 115.5525 | 115.6918 | -110.9932 | -110.8254 | -110.9586 | -110.7907
977.7656 | 120.8633 | -115.7043 | 4.9347 | 0.13101 | -0.008469 | -0.012 | -0.020438 | 0.013375 | 0.085583 | -0.11308 | 4.6951 | 4.8 | 4.7343 | 4.7474 | 115.6288 | 115.7064 | 115.4655 | 115.5957 | 0.18136 | 0.041885 | 0.038354 | 0.029916 | 0.063729 | 0.13594 | -0.062723 | 4.7454 | 4.8503 | 4.7847 | 4.7978 | 115.6792 | 115.7567 | 115.5159 | 115.6461 | -110.9337 | -110.7704 | -110.8945 | -110.7312
979.5312 | 120.9045 | -115.8691 | 4.6921 | 0.13101 | -0.013048 | -0.021157 | -0.020438 | 0.013375 | 0.085583 | -0.11765 | 4.5669 | 4.6718 | 4.6061 | 4.6284 | 115.7341 | 115.83 | 115.5754 | 115.7056 | 0.18136 | 0.037306 | 0.029197 | 0.029916 | 0.063729 | 0.13594 | -0.067301 | 4.6172 | 4.7221 | 4.6565 | 4.6787 | 115.7844 | 115.8803 | 115.6257 | 115.7559 | -111.1672 | -111.0085 | -111.128 | -110.9693
981.2188 | 120.8954 | -115.7501 | 4.7836 | 0.13101 | -0.013048 | -0.016578 | -0.025017 | 0.017953 | 0.081005 | -0.11765 | 4.6722 | 4.7725 | 4.7023 | 4.7245 | 115.6242 | 115.7155 | 115.4609 | 115.5911 | 0.18136 | 0.037306 | 0.033776 | 0.025337 | 0.068307 | 0.13136 | -0.067301 | 4.7225 | 4.8229 | 4.7526 | 4.7749 | 115.6746 | 115.7659 | 115.5113 | 115.6415 | -110.952 | -110.7887 | -110.922 | -110.7587
982.9062 | 120.7352 | -115.7867 | 4.8386 | 0.13101 | -0.008469 | -0.021157 | -0.025017 | 0.013375 | 0.085583 | -0.11765 | 4.6585 | 4.7633 | 4.6931 | 4.7108 | 115.6196 | 115.6972 | 115.4518 | 115.582 | 0.18136 | 0.041885 | 0.029197 | 0.025337 | 0.063729 | 0.13594 | -0.067301 | 4.7088 | 4.8137 | 4.7434 | 4.7611 | 115.67 | 115.7476 | 115.5021 | 115.6323 | -110.9612 | -110.7933 | -110.9265 | -110.7587
984.6406 | 120.8496 | -115.7089 | 4.8111 | 0.13101 | -0.013048 | -0.021157 | -0.020438 | 0.017953 | 0.076426 | -0.12681 | 4.6905 | 4.7817 | 4.7206 | 4.7382 | 115.583 | 115.6514 | 115.4106 | 115.5408 | 0.18136 | 0.037306 | 0.029197 | 0.029916 | 0.068307 | 0.12678 | -0.076458 | 4.7409 | 4.832 | 4.7709 | 4.7886 | 115.6334 | 115.7018 | 115.4609 | 115.5911 | -110.8925 | -110.7201 | -110.8624 | -110.69
986.4062 | 120.7123 | -115.9058 | 4.6692 | 0.13559 | -0.013048 | -0.021157 | -0.020438 | 0.013375 | 0.085583 | -0.12223 | 4.5348 | 4.6397 | 4.5649 | 4.5826 | 115.7112 | 115.7934 | 115.5433 | 115.6735 | 0.18594 | 0.037306 | 0.029197 | 0.029916 | 0.063729 | 0.13594 | -0.07188 | 4.5852 | 4.6901 | 4.6153 | 4.6329 | 115.7616 | 115.8437 | 115.5937 | 115.7239 | -111.1764 | -111.0085 | -111.1463 | -110.9784
988.1562 | 120.8313 | -115.6769 | 4.7974 | 0.12643 | -0.017627 | -0.016578 | -0.020438 | 0.008797 | 0.085583 | -0.12223 | 4.6905 | 4.7954 | 4.7297 | 4.7474 | 115.5327 | 115.6194 | 115.3556 | 115.4996 | 0.17678 | 0.032727 | 0.033776 | 0.029916 | 0.059151 | 0.13594 | -0.07188 | 4.7409 | 4.8458 | 4.7801 | 4.7978 | 115.583 | 115.6697 | 115.406 | 115.5499 | -110.8422 | -110.6651 | -110.8029 | -110.6259
989.8438 | 120.7077 | -115.8463 | 4.7012 | 0.13559 | -0.008469 | -0.007421 | -0.020438 | 0.013375 | 0.090161 | -0.12223 | 4.5486 | 4.6443 | 4.5878 | 4.6009 | 115.6654 | 115.7567 | 115.4976 | 115.6277 | 0.18594 | 0.041885 | 0.042933 | 0.029916 | 0.063729 | 0.14052 | -0.07188 | 4.5989 | 4.6947 | 4.6381 | 4.6512 | 115.7158 | 115.8071 | 115.5479 | 115.6781 | -111.1169 | -110.949 | -111.0776 | -110.9098
991.6094 | 120.6619 | -115.686 | 4.8706 | 0.12643 | -0.017627 | -0.012 | -0.01586 | 0.008797 | 0.085583 | -0.11765 | 4.6722 | 4.7725 | 4.7068 | 4.7199 | 115.5189 | 115.6056 | 115.351 | 115.4904 | 0.17678 | 0.032727 | 0.038354 | 0.034494 | 0.059151 | 0.13594 | -0.067301 | 4.7225 | 4.8229 | 4.7572 | 4.7703 | 115.5693 | 115.656 | 115.4014 | 115.5408 | -110.8467 | -110.6789 | -110.8121 | -110.6442
993.3594 | 120.7214 | -115.8691 | 4.6005 | 0.13559 | -0.008469 | -0.016578 | -0.025017 | 0.017953 | 0.090161 | -0.11308 | 4.4478 | 4.5481 | 4.4871 | 4.5047 | 115.7249 | 115.8162 | 115.5571 | 115.701 | 0.18594 | 0.041885 | 0.033776 | 0.025337 | 0.068307 | 0.14052 | -0.062723 | 4.4982 | 4.5985 | 4.5374 | 4.5551 | 115.7753 | 115.8666 | 115.6074 | 115.7514 | -111.2771 | -111.1092 | -111.2379 | -111.07
995.1094 | 120.7489 | -115.9744 | 4.4586 | 0.13101 | -0.013048 | -0.016578 | -0.025017 | 0.008797 | 0.085583 | -0.12223 | 4.3242 | 4.4245 | 4.3635 | 4.3811 | 115.8348 | 115.9215 | 115.667 | 115.8017 | 0.18136 | 0.037306 | 0.033776 | 0.025337 | 0.059151 | 0.13594 | -0.07188 | 4.3746 | 4.4749 | 4.4138 | 4.4314 | 115.8852 | 115.9719 | 115.7173 | 115.8521 | -111.5106 | -111.3427 | -111.4714 | -111.3035
996.8125 | 120.6619 | -116.0202 | 4.4403 | 0.13559 | -0.008469 | -0.016578 | -0.020438 | 0.013375 | 0.090161 | -0.11308 | 4.2876 | 4.397 | 4.336 | 4.349 | 115.8531 | 115.9353 | 115.6715 | 115.8109 | 0.18594 | 0.041885 | 0.033776 | 0.029916 | 0.063729 | 0.14052 | -0.062723 | 4.3379 | 4.4474 | 4.3863 | 4.3994 | 115.9035 | 115.9856 | 115.7219 | 115.8612 | -111.5655 | -111.3839 | -111.5171 | -111.3355
998.5625 | 120.5841 | -116.0294 | 4.4083 | 0.13101 | -0.008469 | -0.016578 | -0.020438 | 0.013375 | 0.081005 | -0.11308 | 4.4478 | 4.5527 | 4.4825 | 4.5001 | 115.6792 | 115.7613 | 115.5159 | 115.6461 | 0.18136 | 0.041885 | 0.033776 | 0.029916 | 0.063729 | 0.13136 | -0.062723 | 4.4982 | 4.6031 | 4.5328 | 4.5505 | 115.7295 | 115.8117 | 115.5662 | 115.6964 | -111.2313 | -111.068 | -111.1967 | -111.0334
1000.25 | 120.5795 | -115.8829 | 4.5776 | 0.13559 | -0.008469 | -0.021157 | -0.025017 | 0.013375 | 0.090161 | -0.11308 | 4.4387 | 4.5344 | 4.4779 | 4.5001 | 115.67 | 115.7521 | 115.5067 | 115.6369 | 0.18594 | 0.041885 | 0.029197 | 0.025337 | 0.063729 | 0.14052 | -0.062723 | 4.489 | 4.5848 | 4.5283 | 4.5505 | 115.7204 | 115.8025 | 115.5571 | 115.6873 | -111.2313 | -111.068 | -111.1921 | -111.0288
1002.0156 | 120.6207 | -115.9607 | 4.4632 | 0.13101 | -0.00389 | -0.025735 | -0.020438 | 0.008797 | 0.090161 | -0.11765 | 4.2968 | 4.4016 | 4.3451 | 4.3628 | 115.7936 | 115.8803 | 115.6349 | 115.7605 | 0.18136 | 0.046464 | 0.024619 | 0.029916 | 0.059151 | 0.14052 | -0.067301 | 4.3471 | 4.452 | 4.3955 | 4.4131 | 115.844 | 115.9307 | 115.6853 | 115.8109 | -111.4969 | -111.3382 | -111.4485 | -111.2898
1003.7656 | 120.6848 | -115.9698 | 4.3808 | 0.13559 | -0.013048 | -0.016578 | -0.025017 | 0.004219 | 0.081005 | -0.11765 | 4.2464 | 4.3467 | 4.2811 | 4.2941 | 115.8302 | 115.9261 | 115.6761 | 115.8063 | 0.18594 | 0.037306 | 0.033776 | 0.025337 | 0.054573 | 0.13136 | -0.067301 | 4.2967 | 4.397 | 4.3314 | 4.3444 | 115.8806 | 115.9765 | 115.7265 | 115.8567 | -111.5838 | -111.4297 | -111.5492 | -111.3951
1005.4531 | 120.6573 | -115.8829 | 4.4449 | 0.12643 | -0.008469 | -0.016578 | -0.025017 | 0.008797 | 0.085583 | -0.11765 | 4.3288 | 4.4383 | 4.3818 | 4.3948 | 115.7341 | 115.8162 | 115.5708 | 115.6873 | 0.17678 | 0.041885 | 0.033776 | 0.025337 | 0.059151 | 0.13594 | -0.067301 | 4.3792 | 4.4886 | 4.4321 | 4.4452 | 115.7844 | 115.8666 | 115.6212 | 115.7376 | -111.4053 | -111.242 | -111.3523 | -111.189
1007.2188 | 120.5612 | -115.8234 | 4.5319 | 0.13559 | -0.008469 | -0.016578 | -0.020438 | 0.013375 | 0.085583 | -0.11308 | 4.3746 | 4.484 | 4.4184 | 4.4315 | 115.6792 | 115.7521 | 115.5067 | 115.6461 | 0.18594 | 0.041885 | 0.033776 | 0.029916 | 0.063729 | 0.13594 | -0.062723 | 4.4249 | 4.5344 | 4.4688 | 4.4818 | 115.7295 | 115.8025 | 115.5571 | 115.6964 | -111.3046 | -111.1321 | -111.2608 | -111.0883
1008.9688 | 120.52 | -115.8966 | 4.4861 | 0.13101 | -0.008469 | -0.021157 | -0.020438 | 0.008797 | 0.085583 | -0.11765 | 4.3105 | 4.4154 | 4.3543 | 4.3719 | 115.7387 | 115.8071 | 115.5662 | 115.6964 | 0.18136 | 0.041885 | 0.029197 | 0.029916 | 0.059151 | 0.13594 | -0.067301 | 4.3608 | 4.4657 | 4.4047 | 4.4223 | 115.789 | 115.8574 | 115.6166 | 115.7468 | -111.4282 | -111.2557 | -111.3844 | -111.2119
1010.6562 | 120.5063 | -115.947 | 4.422 | 0.12643 | -0.008469 | -0.012 | -0.025017 | 0.013375 | 0.090161 | -0.12223 | 4.2418 | 4.3558 | 4.2811 | 4.3032 | 115.7845 | 115.8712 | 115.612 | 115.7514 | 0.17678 | 0.041885 | 0.038354 | 0.025337 | 0.063729 | 0.14052 | -0.07188 | 4.2922 | 4.4062 | 4.3314 | 4.3536 | 115.8348 | 115.9215 | 115.6624 | 115.8017 | -111.5426 | -111.3702 | -111.5034 | -111.331
1012.4062 | 120.6116 | -115.9744 | 4.2938 | 0.13101 | -0.008469 | -0.021157 | -0.025017 | 0.017953 | 0.09474 | -0.12223 | 4.1502 | 4.2643 | 4.1895 | 4.2162 | 115.8577 | 115.9398 | 115.6944 | 115.8292 | 0.18136 | 0.041885 | 0.029197 | 0.025337 | 0.068307 | 0.14509 | -0.07188 | 4.2006 | 4.3146 | 4.2398 | 4.2666 | 115.9081 | 115.9902 | 115.7448 | 115.8795 | -111.7075 | -111.5442 | -111.6682 | -111.5049
1014.1562 | 120.5933 | -115.9287 | 4.3213 | 0.13559 | -0.00389 | -0.016578 | -0.025017 | 0.008797 | 0.085583 | -0.12223 | 4.1594 | 4.2734 | 4.1986 | 4.2254 | 115.8348 | 115.9124 | 115.6624 | 115.7971 | 0.18594 | 0.046464 | 0.033776 | 0.025337 | 0.059151 | 0.13594 | -0.07188 | 4.2098 | 4.3238 | 4.249 | 4.2758 | 115.8852 | 115.9627 | 115.7127 | 115.8475 | -111.6754 | -111.503 | -111.6362 | -111.4637
1015.9062 | 120.4376 | -115.8279 | 4.4724 | 0.14017 | -0.008469 | -0.012 | -0.020438 | 0.022531 | 0.085583 | -0.11308 | 4.3013 | 4.4062 | 4.3451 | 4.349 | 115.6837 | 115.7659 | 115.5113 | 115.6461 | 0.19052 | 0.041885 | 0.038354 | 0.029916 | 0.072885 | 0.13594 | -0.062723 | 4.3517 | 4.4566 | 4.3955 | 4.3994 | 115.7341 | 115.8162 | 115.5616 | 115.6964 | -111.3824 | -111.21 | -111.3386 | -111.1661
1017.5938 | 120.4788 | -115.9195 | 4.3671 | 0.13559 | -0.00389 | -0.012 | -0.025017 | 0.013375 | 0.081005 | -0.11308 | 4.2189 | 4.3329 | 4.2582 | 4.2849 | 115.7433 | 115.8391 | 115.58 | 115.7193 | 0.18594 | 0.046464 | 0.038354 | 0.025337 | 0.063729 | 0.13136 | -0.062723 | 4.2693 | 4.3833 | 4.3085 | 4.3353 | 115.7936 | 115.8895 | 115.6303 | 115.7697 | -111.5243 | -111.361 | -111.4851 | -111.3218
1019.3438 | 120.575 | -115.9058 | 4.303 | 0.13559 | -0.017627 | -0.012 | -0.020438 | 0.008797 | 0.081005 | -0.12223 | 4.1777 | 4.278 | 4.2124 | 4.23 | 115.789 | 115.8666 | 115.6166 | 115.7468 | 0.18594 | 0.032727 | 0.038354 | 0.029916 | 0.059151 | 0.13136 | -0.07188 | 4.2281 | 4.3283 | 4.2627 | 4.2803 | 115.8394 | 115.917 | 115.6669 | 115.7971 | -111.6113 | -111.4389 | -111.5767 | -111.4042
1021.0312 | 120.4193 | -115.86 | 4.4037 | 0.13559 | -0.008469 | -0.012 | -0.025017 | 0.013375 | 0.090161 | -0.11765 | 4.251 | 4.3513 | 4.2902 | 4.3124 | 115.6975 | 115.7842 | 115.5296 | 115.669 | 0.18594 | 0.041885 | 0.038354 | 0.025337 | 0.063729 | 0.14052 | -0.067301 | 4.3013 | 4.4016 | 4.3406 | 4.3628 | 115.7478 | 115.8345 | 115.58 | 115.7193 | -111.4465 | -111.2786 | -111.4073 | -111.2394
1022.7812 | 120.4468 | -115.8646 | 4.3533 | 0.13559 | -0.00389 | -0.012 | -0.029595 | 0.013375 | 0.085583 | -0.11765 | 4.2143 | 4.3146 | 4.249 | 4.2666 | 115.7295 | 115.8117 | 115.5617 | 115.701 | 0.18594 | 0.046464 | 0.038354 | 0.020759 | 0.063729 | 0.13594 | -0.067301 | 4.2647 | 4.365 | 4.2994 | 4.317 | 115.7799 | 115.862 | 115.612 | 115.7514 | -111.5152 | -111.3473 | -111.4805 | -111.3126
1024.4688 | 120.3918 | -115.9332 | 4.3304 | 0.13559 | -0.013048 | -0.021157 | -0.029595 | 0.017953 | 0.085583 | -0.11308 | 4.1548 | 4.2551 | 4.1895 | 4.2025 | 115.7753 | 115.862 | 115.612 | 115.7422 | 0.18594 | 0.037306 | 0.029197 | 0.020759 | 0.068307 | 0.13594 | -0.062723 | 4.2052 | 4.3055 | 4.2398 | 4.2529 | 115.8257 | 115.9124 | 115.6624 | 115.7926 | -111.6205 | -111.4572 | -111.5858 | -111.4225
1026.2031 | 120.3873 | -115.8554 | 4.39 | 0.14017 | -0.008469 | -0.007421 | -0.029595 | 0.022531 | 0.085583 | -0.11765 | 4.3242 | 4.4291 | 4.368 | 4.3811 | 115.5876 | 115.6697 | 115.4197 | 115.5591 | 0.19052 | 0.041885 | 0.042933 | 0.020759 | 0.072885 | 0.13594 | -0.067301 | 4.3746 | 4.4794 | 4.4184 | 4.4314 | 115.6379 | 115.7201 | 115.4701 | 115.6094 | -111.2634 | -111.0955 | -111.2196 | -111.0517
1027.9531 | 120.369 | -115.7639 | 4.4907 | 0.13559 | -0.00389 | -0.016578 | -0.025017 | 0.008797 | 0.085583 | -0.11765 | 4.3425 | 4.4383 | 4.3726 | 4.3902 | 115.5647 | 115.6469 | 115.3923 | 115.5316 | 0.18594 | 0.046464 | 0.033776 | 0.025337 | 0.059151 | 0.13594 | -0.067301 | 4.3929 | 4.4886 | 4.423 | 4.4406 | 115.6151 | 115.6972 | 115.4426 | 115.582 | -111.2222 | -111.0497 | -111.1921 | -111.0196
1029.7031 | 120.3964 | -115.7043 | 4.4815 | 0.14017 | -0.008469 | -0.021157 | -0.020438 | 0.017953 | 0.085583 | -0.12223 | 4.4112 | 4.5161 | 4.4413 | 4.4589 | 115.4686 | 115.5507 | 115.3053 | 115.4309 | 0.19052 | 0.041885 | 0.029197 | 0.029916 | 0.068307 | 0.13594 | -0.07188 | 4.4616 | 4.5664 | 4.4916 | 4.5093 | 115.5189 | 115.6011 | 115.3556 | 115.4812 | -111.0573 | -110.894 | -111.0273 | -110.864
1031.3906 | 120.3232 | -115.892 | 4.3167 | 0.14474 | -0.008469 | -0.016578 | -0.025017 | 0.004219 | 0.085583 | -0.12223 | 4.2601 | 4.3604 | 4.2948 | 4.3124 | 115.5968 | 115.6789 | 115.4243 | 115.5591 | 0.1951 | 0.041885 | 0.033776 | 0.025337 | 0.054573 | 0.13594 | -0.07188 | 4.3105 | 4.4108 | 4.3451 | 4.3628 | 115.6471 | 115.7293 | 115.4747 | 115.6094 | -111.3366 | -111.1642 | -111.302 | -111.1295
1033.1406 | 120.401 | -115.6586 | 4.4724 | 0.13101 | -0.013048 | -0.016578 | -0.025017 | 0.008797 | 0.085583 | -0.12223 | 4.37 | 4.4703 | 4.4138 | 4.4269 | 115.4915 | 115.5736 | 115.3144 | 115.4629 | 0.18136 | 0.037306 | 0.033776 | 0.025337 | 0.059151 | 0.13594 | -0.07188 | 4.4204 | 4.5207 | 4.4642 | 4.4772 | 115.5418 | 115.624 | 115.3648 | 115.5133 | -111.1214 | -110.9444 | -111.0776 | -110.9006
1034.8906 | 120.401 | -115.741 | 4.4128 | 0.13559 | -0.017627 | -0.021157 | -0.025017 | 0.013375 | 0.085583 | -0.11765 | 4.2968 | 4.4016 | 4.336 | 4.3536 | 115.551 | 115.6331 | 115.3877 | 115.5225 | 0.18594 | 0.032727 | 0.029197 | 0.025337 | 0.063729 | 0.13594 | -0.067301 | 4.3471 | 4.452 | 4.3863 | 4.404 | 115.6013 | 115.6835 | 115.438 | 115.5728 | -111.2542 | -111.0909 | -111.215 | -111.0517
1036.5938 | 120.3323 | -115.6219 | 4.5044 | 0.14474 | -0.008469 | -0.016578 | -0.029595 | 0.013375 | 0.085583 | -0.11765 | 4.3929 | 4.5069 | 4.4413 | 4.4543 | 115.4319 | 115.5095 | 115.2595 | 115.3943 | 0.1951 | 0.041885 | 0.033776 | 0.020759 | 0.063729 | 0.13594 | -0.067301 | 4.4433 | 4.5573 | 4.4916 | 4.5047 | 115.4823 | 115.5599 | 115.3098 | 115.4446 | -111.039 | -110.8666 | -110.9906 | -110.8182
1038.3438 | 120.3735 | -115.6265 | 4.4586 | 0.13559 | -0.013048 | -0.025735 | -0.020438 | 0.013375 | 0.076426 | -0.11308 | 4.3746 | 4.4886 | 4.423 | 4.436 | 115.4457 | 115.5187 | 115.2869 | 115.408 | 0.18594 | 0.037306 | 0.024619 | 0.029916 | 0.063729 | 0.12678 | -0.062723 | 4.4249 | 4.539 | 4.4733 | 4.4864 | 115.496 | 115.569 | 115.3373 | 115.4584 | -111.0711 | -110.9124 | -111.0227 | -110.864
1040.0781 | 120.3049 | -115.6357 | 4.5273 | 0.14474 | -0.013048 | -0.012 | -0.025017 | 0.017953 | 0.085583 | -0.11765 | 4.338 | 4.4474 | 4.3864 | 4.404 | 115.4731 | 115.5507 | 115.3098 | 115.4446 | 0.1951 | 0.037306 | 0.038354 | 0.025337 | 0.068307 | 0.13594 | -0.067301 | 4.3883 | 4.4978 | 4.4367 | 4.4543 | 115.5235 | 115.6011 | 115.3602 | 115.495 | -111.1352 | -110.9719 | -111.0868 | -110.9235
1041.8438 | 120.3186 | -115.7455 | 4.4174 | 0.14017 | -0.008469 | -0.012 | -0.025017 | 0.008797 | 0.090161 | -0.12223 | 4.2235 | 4.3375 | 4.2673 | 4.2941 | 115.5739 | 115.6606 | 115.4151 | 115.5453 | 0.19052 | 0.041885 | 0.038354 | 0.025337 | 0.059151 | 0.14052 | -0.07188 | 4.2739 | 4.3879 | 4.3177 | 4.3444 | 115.6242 | 115.7109 | 115.4655 | 115.5957 | -111.3504 | -111.1916 | -111.3065 | -111.1478
1043.5312 | 120.3827 | -115.6815 | 4.3991 | 0.14474 | -0.022205 | -0.021157 | -0.029595 | 0.008797 | 0.076426 | -0.12223 | 4.2555 | 4.365 | 4.3039 | 4.3216 | 115.5418 | 115.6194 | 115.3831 | 115.5179 | 0.1951 | 0.028149 | 0.029197 | 0.020759 | 0.059151 | 0.12678 | -0.07188 | 4.3059 | 4.4153 | 4.3543 | 4.3719 | 115.5922 | 115.6697 | 115.4334 | 115.5682 | -111.2863 | -111.1275 | -111.2379 | -111.0792
1045.2656 | 120.2774 | -115.7135 | 4.4128 | 0.13101 | -0.008469 | -0.012 | -0.020438 | 0.017953 | 0.090161 | -0.11765 | 4.251 | 4.3513 | 4.2902 | 4.3078 | 115.5327 | 115.6194 | 115.3602 | 115.5087 | 0.18136 | 0.041885 | 0.038354 | 0.029916 | 0.068307 | 0.14052 | -0.067301 | 4.3013 | 4.4016 | 4.3406 | 4.3582 | 115.583 | 115.6697 | 115.4106 | 115.5591 | -111.2817 | -111.1092 | -111.2424 | -111.07
1047.0312 | 120.2728 | -115.6174 | 4.4769 | 0.13101 | -0.008469 | -0.021157 | -0.029595 | 0.008797 | 0.076426 | -0.11765 | 4.3242 | 4.4291 | 4.3589 | 4.3857 | 115.4594 | 115.537 | 115.2824 | 115.4217 | 0.18136 | 0.041885 | 0.029197 | 0.020759 | 0.059151 | 0.12678 | -0.067301 | 4.3746 | 4.4794 | 4.4092 | 4.436 | 115.5098 | 115.5873 | 115.3327 | 115.4721 | -111.1352 | -110.9581 | -111.1005 | -110.9235
1048.7031 | 120.369 | -115.6357 | 4.39 | 0.13559 | -0.008469 | -0.016578 | -0.029595 | 0.013375 | 0.085583 | -0.12223 | 4.2693 | 4.3833 | 4.3131 | 4.3399 | 115.4915 | 115.5736 | 115.3236 | 115.4629 | 0.18594 | 0.041885 | 0.033776 | 0.020759 | 0.063729 | 0.13594 | -0.07188 | 4.3196 | 4.4337 | 4.3635 | 4.3902 | 115.5418 | 115.624 | 115.3739 | 115.5133 | -111.2222 | -111.0543 | -111.1784 | -111.0105
1050.4531 | 120.2271 | -115.7593 | 4.3533 | 0.14017 | 0.000689 | -0.016578 | -0.020438 | 0.013375 | 0.090161 | -0.11765 | 4.1548 | 4.2643 | 4.1941 | 4.2162 | 115.6151 | 115.6835 | 115.4426 | 115.5774 | 0.19052 | 0.051043 | 0.033776 | 0.029916 | 0.063729 | 0.14052 | -0.067301 | 4.2052 | 4.3146 | 4.2444 | 4.2666 | 115.6654 | 115.7338 | 115.493 | 115.6277 | -111.4602 | -111.2878 | -111.421 | -111.2486
1052.2031 | 120.2728 | -115.4022 | 4.5959 | 0.13559 | -0.00389 | -0.012 | -0.029595 | 0.017953 | 0.090161 | -0.11765 | 4.4204 | 4.5252 | 4.4642 | 4.491 | 115.2809 | 115.3584 | 115.1267 | 115.2569 | 0.18594 | 0.046464 | 0.038354 | 0.020759 | 0.068307 | 0.14052 | -0.067301 | 4.4707 | 4.5756 | 4.5145 | 4.5413 | 115.3312 | 115.4088 | 115.1771 | 115.3073 | -110.8605 | -110.7063 | -110.8167 | -110.6625
1053.9531 | 120.2499 | -115.6906 | 4.39 | 0.13559 | -0.00389 | -0.021157 | -0.025017 | 0.004219 | 0.085583 | -0.11765 | 4.2189 | 4.3238 | 4.2719 | 4.2758 | 115.5327 | 115.6194 | 115.3694 | 115.4996 | 0.18594 | 0.046464 | 0.029197 | 0.025337 | 0.054573 | 0.13594 | -0.067301 | 4.2693 | 4.3741 | 4.3222 | 4.3261 | 115.583 | 115.6697 | 115.4197 | 115.5499 | -111.3137 | -111.1504 | -111.2608 | -111.0975
1055.6406 | 120.2957 | -115.6815 | 4.335 | 0.13559 | -0.00389 | -0.021157 | -0.034174 | 0.013375 | 0.081005 | -0.11765 | 4.1823 | 4.2917 | 4.2261 | 4.2529 | 115.5555 | 115.6423 | 115.4014 | 115.5316 | 0.18594 | 0.046464 | 0.029197 | 0.01618 | 0.063729 | 0.13136 | -0.067301 | 4.2326 | 4.3421 | 4.2765 | 4.3032 | 115.6059 | 115.6926 | 115.4518 | 115.582 | -111.3733 | -111.2191 | -111.3294 | -111.1753
1057.3906 | 120.1492 | -115.6952 | 4.39 | 0.13559 | -0.00389 | -0.016578 | -0.025017 | 0.013375 | 0.085583 | -0.11308 | 4.2098 | 4.3146 | 4.249 | 4.2712 | 115.5281 | 115.6056 | 115.3602 | 115.4996 | 0.18594 | 0.046464 | 0.033776 | 0.025337 | 0.063729 | 0.13594 | -0.062723 | 4.2601 | 4.365 | 4.2994 | 4.3215 | 115.5784 | 115.656 | 115.4106 | 115.5499 | -111.3183 | -111.1504 | -111.2791 | -111.1112
1059.1406 | 120.2957 | -115.7501 | 4.2938 | 0.12643 | -0.013048 | -0.016578 | -0.020438 | 0.013375 | 0.085583 | -0.11765 | 4.1457 | 4.2505 | 4.1895 | 4.2071 | 115.583 | 115.6606 | 115.4197 | 115.5453 | 0.17678 | 0.037306 | 0.033776 | 0.029916 | 0.063729 | 0.13594 | -0.067301 | 4.196 | 4.3009 | 4.2398 | 4.2574 | 115.6334 | 115.7109 | 115.4701 | 115.5957 | -111.4374 | -111.2741 | -111.3935 | -111.2302
1060.8906 | 120.3094 | -115.7364 | 4.2114 | 0.14017 | -0.00389 | -0.016578 | -0.025017 | 0.013375 | 0.090161 | -0.11765 | 4.0999 | 4.2002 | 4.1391 | 4.1521 | 115.6242 | 115.7018 | 115.4609 | 115.6003 | 0.19052 | 0.046464 | 0.033776 | 0.025337 | 0.063729 | 0.14052 | -0.067301 | 4.1502 | 4.2505 | 4.1895 | 4.2025 | 115.6746 | 115.7521 | 115.5113 | 115.6506 | -111.5243 | -111.361 | -111.4851 | -111.3218
1062.5781 | 118.2083 | -67.6392 | 50.5096 | 0.13101 | 0.000689 | -0.002842 | -0.01586 | 0.031687 | 0.099318 | -0.11308 | 38.8094 | 38.9534 | 38.815 | 38.8383 | 79.7634 | 79.8464 | 79.6762 | 79.8264 | 0.18136 | 0.051043 | 0.047512 | 0.034494 | 0.082041 | 0.14967 | -0.062723 | 38.8598 | 39.0037 | 38.8654 | 38.8887 | 79.8137 | 79.8967 | 79.7266 | 79.8768 | -40.9539 | -40.8668 | -40.9484 | -40.8612
1064.3281 | 116.2766 | -63.8626 | 52.5101 | 0.13559 | -0.008469 | -0.021157 | -0.025017 | 0.008797 | 0.081005 | -0.11308 | 50.9699 | 51.0643 | 51.0207 | 50.9865 | 65.3788 | 65.4392 | 65.2772 | 65.4189 | 0.18594 | 0.041885 | 0.029197 | 0.025337 | 0.059151 | 0.13136 | -0.062723 | 51.0203 | 51.1147 | 51.0711 | 51.0368 | 65.4291 | 65.4896 | 65.3276 | 65.4693 | -14.4088 | -14.3073 | -14.3581 | -14.2565
1066.0625 | 120.2637 | -118.689 | 1.1948 | 0.13101 | -0.00389 | -0.021157 | -0.029595 | 0.027109 | 0.085583 | -0.11308 | 1.1467 | 1.2514 | 1.1816 | 1.2032 | 118.5268 | 118.6134 | 118.414 | 118.4937 | 0.18136 | 0.046464 | 0.029197 | 0.020759 | 0.077463 | 0.13594 | -0.062723 | 1.1971 | 1.3017 | 1.2319 | 1.2536 | 118.5771 | 118.6638 | 118.4643 | 118.544 | -117.38 | -117.2672 | -117.3452 | -117.2324
1067.7656 | 120.401 | -119.5908 | 0.3891 | 0.14474 | -0.008469 | -0.016578 | -0.029595 | 0.008797 | 0.085583 | -0.11765 | 0.27226 | 0.386 | 0.31626 | 0.3378 | 119.5202 | 119.5977 | 119.348 | 119.4871 | 0.1951 | 0.041885 | 0.033776 | 0.020759 | 0.059151 | 0.13594 | -0.067301 | 0.32261 | 0.43635 | 0.36661 | 0.38816 | 119.5706 | 119.6481 | 119.3983 | 119.5375 | -119.248 | -119.0757 | -119.204 | -119.0317
1069.5156 | 120.369 | -119.7189 | 0.43945 | 0.14017 | 0.000689 | -0.012 | -0.029595 | 0.008797 | 0.090161 | -0.11765 | 0.27226 | 0.39058 | 0.32084 | 0.34238 | 119.5843 | 119.671 | 119.4167 | 119.5558 | 0.19052 | 0.051043 | 0.038354 | 0.020759 | 0.059151 | 0.14052 | -0.067301 | 0.32261 | 0.44093 | 0.37119 | 0.39273 | 119.6347 | 119.7213 | 119.467 | 119.6062 | -119.3121 | -119.1444 | -119.2635 | -119.0958
1071.2031 | 120.433 | -119.8059 | 0.42114 | 0.13101 | -0.013048 | -0.025735 | -0.025017 | 0.008797 | 0.085583 | -0.1085 | 0.27226 | 0.38142 | 0.3071 | 0.33322 | 119.6439 | 119.7351 | 119.4762 | 119.6199 | 0.18136 | 0.037306 | 0.024619 | 0.025337 | 0.059151 | 0.13594 | -0.058145 | 0.32261 | 0.43177 | 0.35746 | 0.38358 | 119.6942 | 119.7854 | 119.5265 | 119.6703 | -119.3716 | -119.2039 | -119.3368 | -119.1691
1072.9688 | 120.5246 | -119.8013 | 0.43488 | 0.14017 | -0.008469 | -0.025735 | -0.025017 | 0.013375 | 0.076426 | -0.12681 | 0.3043 | 0.41347 | 0.33915 | 0.36528 | 119.653 | 119.7396 | 119.4899 | 119.6245 | 0.19052 | 0.041885 | 0.024619 | 0.025337 | 0.063729 | 0.12678 | -0.076458 | 0.35466 | 0.46382 | 0.38951 | 0.41563 | 119.7034 | 119.79 | 119.5403 | 119.6748 | -119.3487 | -119.1856 | -119.3139 | -119.1508
1074.7188 | 120.4742 | -119.902 | 0.42572 | 0.13101 | -0.008469 | -0.021157 | -0.025017 | 0.017953 | 0.085583 | -0.11308 | 0.2631 | 0.37684 | 0.30252 | 0.3378 | 119.7171 | 119.8037 | 119.554 | 119.6977 | 0.18136 | 0.041885 | 0.029197 | 0.025337 | 0.068307 | 0.13594 | -0.062723 | 0.31345 | 0.42719 | 0.35288 | 0.38816 | 119.7675 | 119.8541 | 119.6044 | 119.7481 | -119.454 | -119.2909 | -119.4146 | -119.2515
1076.4062 | 120.5063 | -119.8791 | 0.4303 | 0.13559 | -0.00389 | -0.021157 | -0.029595 | 0.008797 | 0.085583 | -0.11308 | 0.28599 | 0.39973 | 0.32542 | 0.35612 | 119.7263 | 119.8129 | 119.5586 | 119.6977 | 0.18594 | 0.046464 | 0.029197 | 0.020759 | 0.059151 | 0.13594 | -0.062723 | 0.33635 | 0.45009 | 0.37577 | 0.40647 | 119.7766 | 119.8632 | 119.6089 | 119.7481 | -119.4403 | -119.2726 | -119.4008 | -119.2332
1078.1562 | 120.575 | -119.8791 | 0.44861 | 0.13559 | -0.00389 | -0.025735 | -0.029595 | 0.008797 | 0.090161 | -0.12223 | 0.30888 | 0.42721 | 0.34373 | 0.37901 | 119.7263 | 119.8129 | 119.5677 | 119.6977 | 0.18594 | 0.046464 | 0.024619 | 0.020759 | 0.059151 | 0.14052 | -0.07188 | 0.35924 | 0.47756 | 0.39408 | 0.42937 | 119.7766 | 119.8632 | 119.6181 | 119.7481 | -119.4174 | -119.2589 | -119.3825 | -119.224
1079.8906 | 120.6345 | -119.838 | 0.48523 | 0.13559 | -0.013048 | -0.021157 | -0.034174 | 0.013375 | 0.085583 | -0.12681 | 0.35009 | 0.45926 | 0.38036 | 0.41564 | 119.7217 | 119.8037 | 119.5494 | 119.6886 | 0.18594 | 0.037306 | 0.029197 | 0.01618 | 0.063729 | 0.13594 | -0.076458 | 0.40044 | 0.50961 | 0.43071 | 0.466 | 119.772 | 119.8541 | 119.5998 | 119.7389 | -119.3716 | -119.1993 | -119.3413 | -119.1691
1081.6406 | 120.6299 | -119.8425 | 0.53558 | 0.12643 | -0.008469 | -0.016578 | -0.025017 | 0.008797 | 0.081005 | -0.1085 | 0.40045 | 0.51421 | 0.43987 | 0.47517 | 119.6805 | 119.7808 | 119.522 | 119.652 | 0.17678 | 0.041885 | 0.033776 | 0.025337 | 0.059151 | 0.13136 | -0.058145 | 0.45081 | 0.56456 | 0.49023 | 0.52553 | 119.7308 | 119.8312 | 119.5723 | 119.7023 | -119.28 | -119.1215 | -119.2406 | -119.0821
1083.3906 | 120.6024 | -119.8425 | 0.5722 | 0.13559 | -0.008469 | -0.021157 | -0.025017 | 0.013375 | 0.090161 | -0.11308 | 0.42335 | 0.5371 | 0.46276 | 0.49349 | 119.6896 | 119.7625 | 119.5082 | 119.6474 | 0.18594 | 0.041885 | 0.029197 | 0.025337 | 0.063729 | 0.14052 | -0.062723 | 0.4737 | 0.58745 | 0.51312 | 0.54384 | 119.74 | 119.8129 | 119.5586 | 119.6977 | -119.2663 | -119.0849 | -119.2269 | -119.0455
1085.0781 | 120.5841 | -119.8746 | 0.59967 | 0.13101 | 0.000689 | -0.016578 | -0.020438 | 0.008797 | 0.085583 | -0.11308 | 0.4325 | 0.55083 | 0.4765 | 0.50265 | 119.6851 | 119.7717 | 119.5174 | 119.6611 | 0.18136 | 0.051043 | 0.033776 | 0.029916 | 0.059151 | 0.13594 | -0.062723 | 0.48286 | 0.60119 | 0.52685 | 0.553 | 119.7354 | 119.822 | 119.5677 | 119.7115 | -119.2526 | -119.0849 | -119.2086 | -119.0409
1086.8281 | 120.7123 | -119.8013 | 0.60883 | 0.13559 | -0.008469 | -0.021157 | -0.025017 | 0.013375 | 0.085583 | -0.11765 | 0.46913 | 0.57831 | 0.50397 | 0.53012 | 119.6713 | 119.7625 | 119.5128 | 119.6428 | 0.18594 | 0.041885 | 0.029197 | 0.025337 | 0.063729 | 0.13594 | -0.067301 | 0.51948 | 0.62866 | 0.55432 | 0.58047 | 119.7217 | 119.8129 | 119.5632 | 119.6932 | -119.2022 | -119.0437 | -119.1674 | -119.0088
1088.5938 | 120.6162 | -119.8059 | 0.70496 | 0.13101 | 0.000689 | -0.021157 | -0.020438 | 0.017953 | 0.090161 | -0.11308 | 0.51492 | 0.63325 | 0.55433 | 0.58507 | 119.6393 | 119.7213 | 119.467 | 119.6062 | 0.18136 | 0.051043 | 0.029197 | 0.029916 | 0.068307 | 0.14052 | -0.062723 | 0.56527 | 0.68361 | 0.60469 | 0.63542 | 119.6896 | 119.7717 | 119.5174 | 119.6565 | -119.1244 | -118.9521 | -119.0849 | -118.9127
1090.3438 | 120.6894 | -119.751 | 0.66834 | 0.12643 | -0.008469 | -0.021157 | -0.025017 | 0.008797 | 0.081005 | -0.11308 | 0.53781 | 0.64699 | 0.57264 | 0.60338 | 119.6347 | 119.7213 | 119.4624 | 119.6016 | 0.17678 | 0.041885 | 0.029197 | 0.025337 | 0.059151 | 0.13136 | -0.062723 | 0.58816 | 0.69734 | 0.623 | 0.65374 | 119.6851 | 119.7717 | 119.5128 | 119.652 | -119.0969 | -118.9246 | -119.0621 | -118.8898
1092.0938 | 120.639 | -119.7922 | 0.72784 | 0.13101 | -0.008469 | -0.016578 | -0.029595 | 0.008797 | 0.085583 | -0.11765 | 0.55154 | 0.65157 | 0.58638 | 0.6217 | 119.6255 | 119.7168 | 119.4624 | 119.6016 | 0.18136 | 0.041885 | 0.033776 | 0.020759 | 0.059151 | 0.13594 | -0.067301 | 0.6019 | 0.70192 | 0.63673 | 0.67205 | 119.6759 | 119.7671 | 119.5128 | 119.652 | -119.074 | -118.9109 | -119.0392 | -118.8761
1093.8438 | 120.7489 | -119.7968 | 0.68207 | 0.13559 | -0.00389 | -0.012 | -0.025017 | 0.013375 | 0.090161 | -0.12223 | 0.54697 | 0.66531 | 0.59096 | 0.61254 | 119.6393 | 119.7259 | 119.4808 | 119.6153 | 0.18594 | 0.046464 | 0.038354 | 0.025337 | 0.063729 | 0.14052 | -0.07188 | 0.59732 | 0.71566 | 0.64131 | 0.6629 | 119.6896 | 119.7763 | 119.5311 | 119.6657 | -119.0923 | -118.9338 | -119.0483 | -118.8898
1095.5312 | 120.7077 | -119.8654 | 0.70038 | 0.13559 | 0.000689 | -0.021157 | -0.029595 | 0.013375 | 0.090161 | -0.11308 | 0.54239 | 0.64699 | 0.56349 | 0.60338 | 119.6759 | 119.7534 | 119.5036 | 119.6474 | 0.18594 | 0.051043 | 0.029197 | 0.020759 | 0.063729 | 0.14052 | -0.062723 | 0.59274 | 0.69734 | 0.61384 | 0.65374 | 119.7263 | 119.8037 | 119.554 | 119.6977 | -119.1335 | -118.9613 | -119.1124 | -118.9402
1097.2656 | 120.7718 | -119.8196 | 0.66376 | 0.13559 | -0.00389 | -0.012 | -0.029595 | 0.008797 | 0.081005 | -0.1085 | 0.52865 | 0.64699 | 0.56807 | 0.58507 | 119.6942 | 119.7717 | 119.522 | 119.6565 | 0.18594 | 0.046464 | 0.038354 | 0.020759 | 0.059151 | 0.13136 | -0.058145 | 0.579 | 0.69734 | 0.61842 | 0.63542 | 119.7446 | 119.822 | 119.5723 | 119.7069 | -119.1656 | -118.9933 | -119.1261 | -118.9539
1099.0312 | 120.7764 | -119.9158 | 0.62256 | 0.13101 | 0.005267 | -0.021157 | -0.020438 | 0.008797 | 0.081005 | -0.12681 | 0.50118 | 0.61494 | 0.53602 | 0.57133 | 119.7308 | 119.8083 | 119.5632 | 119.7069 | 0.18136 | 0.055621 | 0.029197 | 0.029916 | 0.059151 | 0.13136 | -0.076458 | 0.55153 | 0.66529 | 0.58637 | 0.62169 | 119.7812 | 119.8587 | 119.6135 | 119.7573 | -119.2297 | -119.062 | -119.1948 | -119.0271
1100.7188 | 120.8176 | -119.8608 | 0.59052 | 0.13101 | -0.008469 | -0.016578 | -0.025017 | 0.013375 | 0.090161 | -0.12223 | 0.47829 | 0.58747 | 0.5177 | 0.53928 | 119.772 | 119.8495 | 119.5998 | 119.7344 | 0.18136 | 0.041885 | 0.033776 | 0.025337 | 0.063729 | 0.14052 | -0.07188 | 0.52864 | 0.63782 | 0.56806 | 0.58963 | 119.8224 | 119.8999 | 119.6501 | 119.7847 | -119.2938 | -119.1215 | -119.2543 | -119.0821
1102.4688 | 116.3315 | -95.4666 | 20.7275 | 0.13101 | -0.00389 | -0.021157 | -0.020438 | 0.017953 | 0.090161 | -0.11765 | 20.9808 | 21.0639 | 21.0376 | 21.0213 | 94.9355 | 95.0089 | 94.7803 | 94.9115 | 0.18136 | 0.046464 | 0.029197 | 0.029916 | 0.068307 | 0.14052 | -0.067301 | 21.0311 | 21.1143 | 21.0879 | 21.0716 | 94.9858 | 95.0593 | 94.8307 | 94.9619 | -73.9547 | -73.7996 | -73.8979 | -73.7428
1104.2344 | 116.0065 | -94.3222 | 21.4188 | 0.13101 | -0.008469 | -0.025735 | -0.029595 | 0.008797 | 0.076426 | -0.11765 | 20.903 | 21.0044 | 20.9094 | 20.9526 | 94.5967 | 94.6564 | 94.4507 | 94.5819 | 0.18136 | 0.041885 | 0.024619 | 0.020759 | 0.059151 | 0.12678 | -0.067301 | 20.9533 | 21.0548 | 20.9597 | 21.003 | 94.647 | 94.7068 | 94.5011 | 94.6322 | -73.6937 | -73.5478 | -73.6873 | -73.5413
1106 | 115.7181 | -93.1 | 22.3434 | 0.13101 | -0.013048 | -0.025735 | -0.025017 | 0.004219 | 0.085583 | -0.11765 | 22.1346 | 22.2178 | 22.1409 | 22.1798 | 93.1042 | 93.1869 | 92.9627 | 93.1077 | 0.18136 | 0.037306 | 0.024619 | 0.025337 | 0.054573 | 0.13594 | -0.067301 | 22.1849 | 22.2682 | 22.1913 | 22.2301 | 93.1545 | 93.2372 | 93.0131 | 93.1581 | -70.9696 | -70.8282 | -70.9633 | -70.8218
1107.6875 | 115.4388 | -93.4204 | 21.9086 | 0.13101 | -0.013048 | -0.012 | -0.029595 | 0.013375 | 0.090161 | -0.12223 | 21.6859 | 21.7782 | 21.6968 | 21.731 | 93.3468 | 93.4158 | 93.1962 | 93.3366 | 0.18136 | 0.037306 | 0.038354 | 0.020759 | 0.063729 | 0.14052 | -0.07188 | 21.7362 | 21.8286 | 21.7472 | 21.7814 | 93.3972 | 93.4661 | 93.2466 | 93.387 | -71.6609 | -71.5104 | -71.65 | -71.4994
1109.4375 | 115.3931 | -94.0109 | 20.993 | 0.13559 | -0.008469 | -0.030314 | -0.029595 | 0.004219 | 0.085583 | -0.11765 | 21.1685 | 21.2517 | 21.1703 | 21.209 | 93.6765 | 93.75 | 93.5488 | 93.68 | 0.18594 | 0.041885 | 0.02004 | 0.020759 | 0.054573 | 0.13594 | -0.067301 | 21.2189 | 21.302 | 21.2207 | 21.2594 | 93.7268 | 93.8003 | 93.5991 | 93.7303 | -72.5079 | -72.3803 | -72.5061 | -72.3784
1111.1875 | 115.21 | -94.0292 | 20.9335 | 0.13559 | 0.000689 | -0.021157 | -0.025017 | 0.017953 | 0.090161 | -0.1085 | 20.7107 | 20.7984 | 20.7171 | 20.7603 | 93.9786 | 94.0704 | 93.8464 | 93.9776 | 0.18594 | 0.051043 | 0.029197 | 0.025337 | 0.068307 | 0.14052 | -0.058145 | 20.761 | 20.8487 | 20.7674 | 20.8106 | 94.029 | 94.1208 | 93.8967 | 94.0279 | -73.268 | -73.1357 | -73.2615 | -73.1293
1112.9375 | 115.1505 | -94.455 | 20.3247 | 0.13101 | -0.00389 | -0.016578 | -0.029595 | 0.004219 | 0.081005 | -0.12223 | 20.2116 | 20.3084 | 20.2226 | 20.2612 | 94.3678 | 94.4413 | 94.2081 | 94.3621 | 0.18136 | 0.046464 | 0.033776 | 0.020759 | 0.054573 | 0.13136 | -0.07188 | 20.262 | 20.3588 | 20.273 | 20.3115 | 94.4181 | 94.4916 | 94.2584 | 94.4125 | -74.1562 | -73.9964 | -74.1451 | -73.9854
1114.625 | 115.0269 | -94.5557 | 20.137 | 0.13101 | -0.00389 | -0.021157 | -0.020438 | 0.008797 | 0.090161 | -0.11765 | 19.9827 | 20.0703 | 19.9846 | 20.0276 | 94.5188 | 94.5923 | 94.3591 | 94.5086 | 0.18136 | 0.046464 | 0.029197 | 0.029916 | 0.059151 | 0.14052 | -0.067301 | 20.033 | 20.1207 | 20.0349 | 20.078 | 94.5692 | 94.6427 | 94.4095 | 94.559 | -74.5362 | -74.3765 | -74.5343 | -74.3746
1116.3594 | 114.83 | -94.043 | 20.6955 | 0.13101 | 0.000689 | -0.021157 | -0.025017 | 0.013375 | 0.090161 | -0.11308 | 20.5138 | 20.6015 | 20.5294 | 20.5634 | 93.9374 | 94.0155 | 93.8052 | 93.9272 | 0.18136 | 0.051043 | 0.029197 | 0.025337 | 0.063729 | 0.14052 | -0.062723 | 20.5641 | 20.6518 | 20.5797 | 20.6137 | 93.9878 | 94.0658 | 93.8555 | 93.9776 | -73.4236 | -73.2914 | -73.408 | -73.2758
1118.1094 | 114.8117 | -96.6568 | 17.8894 | 0.13101 | -0.008469 | -0.016578 | -0.025017 | 0.013375 | 0.090161 | -0.11765 | 17.7758 | 17.8679 | 17.8144 | 17.8114 | 96.5515 | 96.6387 | 96.3874 | 96.5459 | 0.18136 | 0.041885 | 0.033776 | 0.025337 | 0.063729 | 0.14052 | -0.067301 | 17.8262 | 17.9183 | 17.8648 | 17.8617 | 96.6019 | 96.6891 | 96.4377 | 96.5963 | -78.7757 | -78.6115 | -78.7371 | -78.5729
1119.7969 | 114.8987 | -95.9518 | 18.5806 | 0.12643 | 0.000689 | -0.016578 | -0.025017 | 0.004219 | 0.071848 | -0.11765 | 18.3848 | 18.4723 | 18.4096 | 18.4341 | 95.9198 | 95.9978 | 95.7968 | 95.9141 | 0.17678 | 0.051043 | 0.033776 | 0.025337 | 0.054573 | 0.1222 | -0.067301 | 18.4351 | 18.5227 | 18.46 | 18.4845 | 95.9701 | 96.0481 | 95.8471 | 95.9645 | -77.535 | -77.412 | -77.5101 | -77.3871
1121.5469 | 114.8117 | -97.8561 | 16.6306 | 0.13559 | -0.008469 | -0.025735 | -0.029595 | 0.008797 | 0.085583 | -0.11308 | 16.5488 | 16.6454 | 16.5966 | 16.5934 | 97.6961 | 97.7741 | 97.532 | 97.6722 | 0.18594 | 0.041885 | 0.024619 | 0.020759 | 0.059151 | 0.13594 | -0.062723 | 16.5992 | 16.6957 | 16.647 | 16.6437 | 97.7464 | 97.8244 | 97.5823 | 97.7225 | -81.1473 | -80.9832 | -81.0995 | -80.9353
1123.2969 | 114.7934 | -98.3414 | 16.0584 | 0.13101 | 0.000689 | -0.021157 | -0.020438 | 0.004219 | 0.09474 | -0.11765 | 16.1505 | 16.2516 | 16.2029 | 16.195 | 98.0761 | 98.1541 | 97.9211 | 98.0659 | 0.18136 | 0.051043 | 0.029197 | 0.029916 | 0.054573 | 0.14509 | -0.067301 | 16.2008 | 16.302 | 16.2532 | 16.2453 | 98.1264 | 98.2044 | 97.9715 | 98.1162 | -81.9256 | -81.7706 | -81.8732 | -81.7182
1124.9844 | 114.7705 | -95.0958 | 19.455 | 0.13101 | 0.000689 | -0.025735 | -0.01586 | 0.013375 | 0.090161 | -0.11308 | 19.1677 | 19.2645 | 19.1696 | 19.2171 | 95.1232 | 95.1966 | 94.9726 | 95.113 | 0.18136 | 0.051043 | 0.024619 | 0.034494 | 0.063729 | 0.14052 | -0.062723 | 19.2181 | 19.3148 | 19.22 | 19.2675 | 95.1735 | 95.247 | 95.023 | 95.1633 | -75.9555 | -75.8049 | -75.9535 | -75.803
1126.7344 | 114.8117 | -97.4945 | 16.9464 | 0.13101 | -0.00389 | -0.021157 | -0.020438 | 0.004219 | 0.085583 | -0.11308 | 16.9334 | 17.0208 | 16.9858 | 16.9826 | 97.2932 | 97.3712 | 97.152 | 97.2784 | 0.18136 | 0.046464 | 0.029197 | 0.029916 | 0.054573 | 0.13594 | -0.062723 | 16.9838 | 17.0712 | 17.0361 | 17.0329 | 97.3436 | 97.4216 | 97.2023 | 97.3288 | -80.3598 | -80.2186 | -80.3074 | -80.1662
1128.4844 | 114.8438 | -95.7413 | 18.75 | 0.13101 | -0.017627 | -0.025735 | -0.029595 | 0.008797 | 0.081005 | -0.12223 | 18.5176 | 18.6051 | 18.5287 | 18.5669 | 95.7412 | 95.8192 | 95.577 | 95.7402 | 0.18136 | 0.032727 | 0.024619 | 0.020759 | 0.059151 | 0.13136 | -0.07188 | 18.5679 | 18.6555 | 18.579 | 18.6173 | 95.7916 | 95.8696 | 95.6273 | 95.7905 | -77.2237 | -77.0594 | -77.2126 | -77.0483
1130.2344 | 114.8483 | -95.668 | 18.8004 | 0.13101 | 0.000689 | -0.025735 | -0.01586 | 0.004219 | 0.076426 | -0.11765 | 18.893 | 18.9852 | 18.8949 | 18.9332 | 95.3795 | 95.4667 | 95.2199 | 95.3739 | 0.18136 | 0.051043 | 0.024619 | 0.034494 | 0.054573 | 0.12678 | -0.067301 | 18.9433 | 19.0355 | 18.9453 | 18.9836 | 95.4299 | 95.5171 | 95.2702 | 95.4243 | -76.4865 | -76.3269 | -76.4846 | -76.325
1132 | 114.7202 | -97.9614 | 16.5207 | 0.13559 | 0.005267 | -0.021157 | -0.020438 | 0.013375 | 0.085583 | -0.11765 | 16.242 | 16.3386 | 16.2899 | 16.2866 | 97.9799 | 98.0625 | 97.8158 | 97.9743 | 0.18594 | 0.055621 | 0.029197 | 0.029916 | 0.063729 | 0.13594 | -0.067301 | 16.2924 | 16.389 | 16.3402 | 16.3369 | 98.0303 | 98.1129 | 97.8662 | 98.0247 | -81.7379 | -81.5738 | -81.6901 | -81.5259
1133.7031 | 114.7018 | -99.5636 | 14.8956 | 0.13559 | -0.008469 | -0.025735 | -0.029595 | 0.017953 | 0.081005 | -0.11765 | 14.809 | 14.8963 | 14.8523 | 14.8488 | 99.3992 | 99.4863 | 99.2397 | 99.3935 | 0.18594 | 0.041885 | 0.024619 | 0.020759 | 0.068307 | 0.13136 | -0.067301 | 14.8593 | 14.9466 | 14.9027 | 14.8991 | 99.4495 | 99.5366 | 99.2901 | 99.4439 | -84.5902 | -84.4307 | -84.5469 | -84.3874
1135.4531 | 114.7568 | -99.9207 | 14.5157 | 0.13101 | -0.008469 | -0.021157 | -0.01586 | 0.013375 | 0.085583 | -0.11765 | 14.4244 | 14.5116 | 14.4677 | 14.4687 | 99.7929 | 99.8617 | 99.6197 | 99.7735 | 0.18136 | 0.041885 | 0.029197 | 0.034494 | 0.063729 | 0.13594 | -0.067301 | 14.4747 | 14.562 | 14.5181 | 14.519 | 99.8432 | 99.912 | 99.6701 | 99.8239 | -85.3685 | -85.1953 | -85.3252 | -85.152
1137.2031 | 118.0984 | -117.7231 | 0.032043 | 0.13101 | -0.00389 | -0.021157 | -0.025017 | 0.004219 | 0.081005 | -0.11765 | -0.10776 | 0.005956 | -0.077472 | -0.046838 | 117.6295 | 117.7161 | 117.4617 | 117.5964 | 0.18136 | 0.046464 | 0.029197 | 0.025337 | 0.054573 | 0.13136 | -0.067301 | -0.057405 | 0.05631 | -0.027118 | 0.003516 | 117.6798 | 117.7665 | 117.512 | 117.6467 | -117.7372 | -117.5694 | -117.7069 | -117.5392
1138.9531 | 118.3456 | -117.9932 | 0.045776 | 0.13101 | -0.008469 | -0.016578 | -0.025017 | 0.008797 | 0.076426 | -0.11765 | -0.11692 | -0.003202 | -0.072894 | -0.046838 | 117.8584 | 117.9405 | 117.6906 | 117.8344 | 0.18136 | 0.041885 | 0.033776 | 0.025337 | 0.059151 | 0.12678 | -0.067301 | -0.066562 | 0.047152 | -0.02254 | 0.003516 | 117.9087 | 117.9908 | 117.741 | 117.8848 | -117.9753 | -117.8075 | -117.9313 | -117.7635
1140.6406 | 118.5013 | -118.1305 | 0.018311 | 0.13101 | -0.00389 | -0.021157 | -0.020438 | 0.008797 | 0.081005 | -0.11765 | -0.1215 | 0.001377 | -0.072894 | -0.051417 | 118.0049 | 118.0824 | 117.828 | 117.9809 | 0.18136 | 0.046464 | 0.029197 | 0.029916 | 0.059151 | 0.13136 | -0.067301 | -0.071141 | 0.051731 | -0.02254 | -0.001063 | 118.0552 | 118.1327 | 117.8783 | 118.0313 | -118.1264 | -117.9494 | -118.0778 | -117.9008
1142.375 | 118.5242 | -118.2953 | 0.059509 | 0.13559 | 0.000689 | -0.016578 | -0.020438 | 0.013375 | 0.081005 | -0.11308 | -0.10776 | -0.003202 | -0.077472 | -0.042259 | 118.1193 | 118.1968 | 117.9516 | 118.0954 | 0.18594 | 0.051043 | 0.033776 | 0.029916 | 0.063729 | 0.13136 | -0.062723 | -0.057405 | 0.047152 | -0.027118 | 0.008095 | 118.1697 | 118.2472 | 118.0019 | 118.1457 | -118.2271 | -118.0593 | -118.1968 | -118.029
1144.125 | 118.6111 | -118.3914 | 0.041199 | 0.13101 | 0.005267 | -0.007421 | -0.011281 | 0.013375 | 0.090161 | -0.11308 | -0.1215 | -0.003202 | -0.063737 | -0.051417 | 118.22 | 118.2976 | 118.0569 | 118.1915 | 0.18136 | 0.055621 | 0.042933 | 0.039073 | 0.063729 | 0.14052 | -0.062723 | -0.071141 | 0.047152 | -0.013383 | -0.001063 | 118.2704 | 118.3479 | 118.1072 | 118.2419 | -118.3415 | -118.1784 | -118.2838 | -118.1206
1145.875 | 118.7347 | -118.4555 | 0.022888 | 0.12643 | 0.005267 | -0.025735 | -0.020438 | 0.017953 | 0.085583 | -0.11765 | -0.11692 | -0.00778 | -0.068315 | -0.051417 | 118.3116 | 118.3983 | 118.1439 | 118.2877 | 0.17678 | 0.055621 | 0.024619 | 0.029916 | 0.068307 | 0.13594 | -0.067301 | -0.066562 | 0.042574 | -0.017961 | -0.001063 | 118.362 | 118.4486 | 118.1942 | 118.338 | -118.4285 | -118.2608 | -118.3799 | -118.2122
1147.625 | 118.7668 | -118.5791 | 0.032043 | 0.12643 | 0.005267 | -0.012 | -0.020438 | 0.013375 | 0.076426 | -0.1085 | -0.1215 | 0.005956 | -0.077472 | -0.046838 | 118.4077 | 118.4853 | 118.2309 | 118.3792 | 0.17678 | 0.055621 | 0.038354 | 0.029916 | 0.063729 | 0.12678 | -0.058145 | -0.071141 | 0.05631 | -0.027118 | 0.003516 | 118.4581 | 118.5356 | 118.2812 | 118.4296 | -118.5292 | -118.3523 | -118.4852 | -118.3083
1149.3281 | 118.9362 | -118.6157 | 0.009155 | 0.13559 | -0.008469 | -0.021157 | -0.025017 | 0.013375 | 0.085583 | -0.11308 | -0.10776 | 0.001377 | -0.077472 | -0.042259 | 118.4764 | 118.5677 | 118.3133 | 118.4571 | 0.18594 | 0.041885 | 0.029197 | 0.025337 | 0.063729 | 0.13594 | -0.062723 | -0.057405 | 0.051731 | -0.027118 | 0.008095 | 118.5268 | 118.618 | 118.3636 | 118.5074 | -118.5842 | -118.421 | -118.5539 | -118.3907
1151.0781 | 118.9545 | -118.7622 | 0.004578 | 0.13101 | 0.000689 | -0.021157 | -0.020438 | 0.013375 | 0.076426 | -0.12223 | -0.13523 | -0.021517 | -0.091207 | -0.069733 | 118.5863 | 118.6684 | 118.414 | 118.5578 | 0.18136 | 0.051043 | 0.029197 | 0.029916 | 0.063729 | 0.12678 | -0.07188 | -0.084876 | 0.028837 | -0.040853 | -0.019379 | 118.6367 | 118.7187 | 118.4643 | 118.6081 | -118.7215 | -118.5492 | -118.6775 | -118.5052
1152.7656 | 119.0689 | -118.8217 | -0.009155 | 0.12643 | -0.00389 | -0.025735 | -0.020438 | 0.008797 | 0.085583 | -0.12223 | -0.13523 | -0.026096 | -0.086628 | -0.065154 | 118.6687 | 118.7508 | 118.4964 | 118.6402 | 0.17678 | 0.046464 | 0.024619 | 0.029916 | 0.059151 | 0.13594 | -0.07188 | -0.084876 | 0.024258 | -0.036274 | -0.0148 | 118.7191 | 118.8011 | 118.5468 | 118.6905 | -118.8039 | -118.6316 | -118.7553 | -118.583
1154.5312 | 119.1696 | -118.8721 | -0.018311 | 0.12185 | -0.00389 | -0.021157 | -0.025017 | 0.008797 | 0.085583 | -0.12223 | -0.13981 | -0.021517 | -0.095785 | -0.069733 | 118.7374 | 118.824 | 118.5697 | 118.718 | 0.1722 | 0.046464 | 0.029197 | 0.025337 | 0.059151 | 0.13594 | -0.07188 | -0.089455 | 0.028837 | -0.045431 | -0.019379 | 118.7877 | 118.8744 | 118.62 | 118.7684 | -118.8772 | -118.7095 | -118.8332 | -118.6654
1156.2812 | 119.1101 | -118.9911 | 0.045776 | 0.13101 | 0.005267 | -0.025735 | -0.025017 | 0.022531 | 0.085583 | -0.11765 | -0.13981 | -0.021517 | -0.10036 | -0.060575 | 118.8106 | 118.8927 | 118.6338 | 118.7867 | 0.18136 | 0.055621 | 0.024619 | 0.025337 | 0.072885 | 0.13594 | -0.067301 | -0.089455 | 0.028837 | -0.050009 | -0.010221 | 118.861 | 118.9431 | 118.6841 | 118.837 | -118.9504 | -118.7736 | -118.911 | -118.7341
1158.0156 | 119.2474 | -119.0094 | -0.009155 | 0.12185 | -0.00389 | -0.021157 | -0.025017 | 0.013375 | 0.081005 | -0.11308 | -0.13981 | -0.021517 | -0.10494 | -0.069733 | 118.8701 | 118.9614 | 118.707 | 118.8508 | 0.1722 | 0.046464 | 0.029197 | 0.025337 | 0.063729 | 0.13136 | -0.062723 | -0.089455 | 0.028837 | -0.054588 | -0.019379 | 118.9205 | 119.0117 | 118.7574 | 118.9011 | -119.01 | -118.8468 | -118.9751 | -118.8119
1159.7656 | 119.2474 | -119.101 | 0.036621 | 0.14017 | 0.000689 | -0.016578 | -0.020438 | 0.017953 | 0.081005 | -0.11765 | -0.14897 | -0.026096 | -0.091207 | -0.065154 | 118.9526 | 119.03 | 118.7757 | 118.924 | 0.19052 | 0.051043 | 0.033776 | 0.029916 | 0.068307 | 0.13136 | -0.067301 | -0.098612 | 0.024258 | -0.040853 | -0.0148 | 119.0029 | 119.0804 | 118.826 | 118.9744 | -119.1015 | -118.9246 | -119.0438 | -118.8669
1161.4531 | 119.3573 | -119.1834 | 0.018311 | 0.14017 | -0.00389 | -0.021157 | -0.01586 | 0.017953 | 0.090161 | -0.11765 | -0.13523 | -0.021517 | -0.10036 | -0.069733 | 119.0121 | 119.0941 | 118.8489 | 118.979 | 0.19052 | 0.046464 | 0.029197 | 0.034494 | 0.068307 | 0.14052 | -0.067301 | -0.084876 | 0.028837 | -0.050009 | -0.019379 | 119.0624 | 119.1445 | 118.8993 | 119.0293 | -119.1473 | -118.9842 | -119.1124 | -118.9493
1163.2188 | 119.3756 | -119.2474 | 0.018311 | 0.13559 | 0.000689 | -0.021157 | -0.020438 | 0.013375 | 0.090161 | -0.12223 | -0.13523 | -0.021517 | -0.10036 | -0.065154 | 119.0716 | 119.1582 | 118.9039 | 119.0431 | 0.18594 | 0.051043 | 0.029197 | 0.029916 | 0.063729 | 0.14052 | -0.07188 | -0.084876 | 0.028837 | -0.050009 | -0.0148 | 119.1219 | 119.2086 | 118.9542 | 119.0934 | -119.2068 | -119.0391 | -119.1719 | -119.0042
1164.9062 | 119.5587 | -119.2657 | 0.018311 | 0.13559 | -0.00389 | -0.025735 | -0.025017 | 0.004219 | 0.085583 | -0.12681 | -0.13981 | -0.026096 | -0.095785 | -0.074312 | 119.1403 | 119.2177 | 118.9634 | 119.1026 | 0.18594 | 0.046464 | 0.024619 | 0.025337 | 0.054573 | 0.13594 | -0.076458 | -0.089455 | 0.024258 | -0.045431 | -0.023958 | 119.1906 | 119.2681 | 119.0137 | 119.1529 | -119.2801 | -119.1032 | -119.236 | -119.0592
1166.6562 | 119.5267 | -119.3481 | 0.022888 | 0.13101 | -0.00389 | -0.021157 | -0.01586 | 0.008797 | 0.085583 | -0.12223 | -0.13981 | -0.026096 | -0.095785 | -0.069733 | 119.1952 | 119.2773 | 119.0229 | 119.1667 | 0.18136 | 0.046464 | 0.029197 | 0.034494 | 0.059151 | 0.13594 | -0.07188 | -0.089455 | 0.024258 | -0.045431 | -0.019379 | 119.2455 | 119.3276 | 119.0733 | 119.217 | -119.335 | -119.1627 | -119.291 | -119.1187
1168.4062 | 119.5862 | -119.4122 | 0.032043 | 0.13101 | -0.008469 | -0.025735 | -0.025017 | 0.008797 | 0.090161 | -0.12223 | -0.13981 | -0.030674 | -0.091207 | -0.069733 | 119.2456 | 119.3322 | 119.0824 | 119.2216 | 0.18136 | 0.041885 | 0.024619 | 0.025337 | 0.059151 | 0.14052 | -0.07188 | -0.089455 | 0.01968 | -0.040853 | -0.019379 | 119.2959 | 119.3825 | 119.1328 | 119.272 | -119.3854 | -119.2222 | -119.3368 | -119.1736
1170.1562 | 119.6045 | -119.4992 | 0.036621 | 0.13101 | 0.000689 | -0.021157 | -0.020438 | 0.017953 | 0.09474 | -0.11765 | -0.13523 | -0.021517 | -0.095785 | -0.069733 | 119.3005 | 119.3826 | 119.142 | 119.2766 | 0.18136 | 0.051043 | 0.029197 | 0.029916 | 0.068307 | 0.14509 | -0.067301 | -0.084876 | 0.028837 | -0.045431 | -0.019379 | 119.3508 | 119.4329 | 119.1923 | 119.3269 | -119.4357 | -119.2772 | -119.3963 | -119.2377
1171.8438 | 119.7006 | -119.5129 | 0.027466 | 0.13101 | 0.000689 | -0.021157 | -0.020438 | 0.017953 | 0.09474 | -0.11308 | -0.13523 | -0.026096 | -0.086628 | -0.065154 | 119.3554 | 119.4466 | 119.1832 | 119.3269 | 0.18136 | 0.051043 | 0.029197 | 0.029916 | 0.068307 | 0.14509 | -0.062723 | -0.084876 | 0.024258 | -0.036274 | -0.0148 | 119.4058 | 119.497 | 119.2335 | 119.3773 | -119.4907 | -119.3184 | -119.4421 | -119.2698
1173.5938 | 119.8242 | -119.545 | 0.009155 | 0.13101 | -0.00389 | -0.025735 | -0.025017 | 0.013375 | 0.085583 | -0.12223 | -0.13981 | -0.021517 | -0.10036 | -0.078891 | 119.4012 | 119.4833 | 119.2381 | 119.3727 | 0.18136 | 0.046464 | 0.024619 | 0.025337 | 0.063729 | 0.13594 | -0.07188 | -0.089455 | 0.028837 | -0.050009 | -0.028537 | 119.4516 | 119.5336 | 119.2885 | 119.423 | -119.541 | -119.3779 | -119.5016 | -119.3385
1175.3438 | 119.8105 | -119.6228 | 0.013733 | 0.14017 | -0.008469 | -0.021157 | -0.020438 | 0.017953 | 0.090161 | -0.11308 | -0.13981 | -0.021517 | -0.10036 | -0.069733 | 119.4607 | 119.5382 | 119.2885 | 119.4368 | 0.19052 | 0.041885 | 0.029197 | 0.029916 | 0.068307 | 0.14052 | -0.062723 | -0.089455 | 0.028837 | -0.050009 | -0.019379 | 119.5111 | 119.5886 | 119.3388 | 119.4871 | -119.6005 | -119.4283 | -119.5611 | -119.3888
1177.1094 | 119.8517 | -119.6457 | 0.018311 | 0.13559 | 0.000689 | -0.021157 | -0.020438 | 0.013375 | 0.085583 | -0.12681 | -0.13523 | -0.016938 | -0.10036 | -0.069733 | 119.5065 | 119.5886 | 119.3388 | 119.4871 | 0.18594 | 0.051043 | 0.029197 | 0.029916 | 0.063729 | 0.13594 | -0.076458 | -0.084876 | 0.033416 | -0.050009 | -0.019379 | 119.5569 | 119.6389 | 119.3892 | 119.5375 | -119.6417 | -119.4741 | -119.6069 | -119.4392
1178.8594 | 119.9112 | -119.7098 | 0 | 0.13559 | -0.00389 | -0.025735 | -0.025017 | 0.013375 | 0.085583 | -0.12223 | -0.13523 | -0.026096 | -0.095785 | -0.069733 | 119.5614 | 119.6435 | 119.38 | 119.5238 | 0.18594 | 0.046464 | 0.024619 | 0.025337 | 0.063729 | 0.13594 | -0.07188 | -0.084876 | 0.024258 | -0.045431 | -0.019379 | 119.6118 | 119.6939 | 119.4304 | 119.5741 | -119.6967 | -119.5153 | -119.6572 | -119.4758
1180.5469 | 119.9615 | -119.751 | 0.032043 | 0.13101 | -0.00389 | -0.016578 | -0.025017 | 0.008797 | 0.090161 | -0.11308 | -0.13981 | -0.016938 | -0.095785 | -0.074312 | 119.6027 | 119.6801 | 119.435 | 119.5787 | 0.18136 | 0.046464 | 0.033776 | 0.025337 | 0.059151 | 0.14052 | -0.062723 | -0.089455 | 0.033416 | -0.045431 | -0.023958 | 119.653 | 119.7305 | 119.4853 | 119.6291 | -119.7425 | -119.5748 | -119.6984 | -119.5308
1182.2969 | 120.0531 | -119.7693 | 0.009155 | 0.13101 | -0.00389 | -0.016578 | -0.025017 | 0.013375 | 0.081005 | -0.12223 | -0.14439 | -0.021517 | -0.095785 | -0.065154 | 119.6439 | 119.7305 | 119.4853 | 119.6199 | 0.18136 | 0.046464 | 0.033776 | 0.025337 | 0.063729 | 0.13136 | -0.07188 | -0.094033 | 0.028837 | -0.045431 | -0.0148 | 119.6942 | 119.7808 | 119.5357 | 119.6703 | -119.7882 | -119.6297 | -119.7396 | -119.5811
1183.9844 | 120.0897 | -119.8105 | 0.009155 | 0.13559 | -0.00389 | -0.021157 | -0.029595 | 0.013375 | 0.085583 | -0.11765 | -0.13523 | -0.016938 | -0.10036 | -0.069733 | 119.6851 | 119.7671 | 119.5265 | 119.6565 | 0.18594 | 0.046464 | 0.029197 | 0.020759 | 0.063729 | 0.13594 | -0.067301 | -0.084876 | 0.033416 | -0.050009 | -0.019379 | 119.7354 | 119.8175 | 119.5769 | 119.7069 | -119.8203 | -119.6618 | -119.7854 | -119.6269
1185.7344 | 120.1218 | -119.8791 | 0.022888 | 0.12643 | -0.008469 | -0.030314 | -0.025017 | -0.000359 | 0.085583 | -0.12223 | -0.14897 | -0.026096 | -0.095785 | -0.060575 | 119.7217 | 119.8129 | 119.5586 | 119.6977 | 0.17678 | 0.041885 | 0.02004 | 0.025337 | 0.049995 | 0.13594 | -0.07188 | -0.098612 | 0.024258 | -0.045431 | -0.010221 | 119.772 | 119.8632 | 119.6089 | 119.7481 | -119.8706 | -119.7076 | -119.8175 | -119.6544
1187.4219 | 120.1996 | -119.8975 | 0.004578 | 0.13101 | 0.000689 | -0.021157 | -0.020438 | 0.013375 | 0.085583 | -0.11765 | -0.13981 | -0.026096 | -0.10036 | -0.069733 | 119.7675 | 119.8495 | 119.5952 | 119.7435 | 0.18136 | 0.051043 | 0.029197 | 0.029916 | 0.063729 | 0.13594 | -0.067301 | -0.089455 | 0.024258 | -0.050009 | -0.019379 | 119.8178 | 119.8999 | 119.6456 | 119.7939 | -119.9073 | -119.735 | -119.8678 | -119.6956
1189.1719 | 120.2316 | -119.9249 | 0.009155 | 0.13559 | -0.00389 | -0.025735 | -0.020438 | 0.004219 | 0.085583 | -0.12681 | -0.13523 | -0.026096 | -0.095785 | -0.065154 | 119.8041 | 119.8861 | 119.641 | 119.7847 | 0.18594 | 0.046464 | 0.024619 | 0.029916 | 0.054573 | 0.13594 | -0.076458 | -0.084876 | 0.024258 | -0.045431 | -0.0148 | 119.8544 | 119.9365 | 119.6913 | 119.8351 | -119.9393 | -119.7762 | -119.8999 | -119.7368
1190.9219 | 120.2728 | -119.9615 | 0 | 0.12643 | -0.00389 | -0.025735 | -0.020438 | 0.008797 | 0.076426 | -0.11765 | -0.14897 | -0.021517 | -0.10952 | -0.069733 | 119.8453 | 119.9273 | 119.673 | 119.8122 | 0.17678 | 0.046464 | 0.024619 | 0.029916 | 0.059151 | 0.12678 | -0.067301 | -0.098612 | 0.028837 | -0.059166 | -0.019379 | 119.8956 | 119.9777 | 119.7234 | 119.8626 | -119.9943 | -119.822 | -119.9548 | -119.7826
1192.6094 | 120.2728 | -120.0256 | 0.018311 | 0.13101 | -0.008469 | -0.021157 | -0.025017 | 0.013375 | 0.085583 | -0.11765 | -0.14439 | -0.021517 | -0.10036 | -0.069733 | 119.8728 | 119.9685 | 119.7097 | 119.8488 | 0.18136 | 0.041885 | 0.029197 | 0.025337 | 0.063729 | 0.13594 | -0.067301 | -0.094033 | 0.028837 | -0.050009 | -0.019379 | 119.9231 | 120.0189 | 119.76 | 119.8992 | -120.0172 | -119.8541 | -119.9731 | -119.81
1194.3594 | 120.2499 | -120.0668 | 0.009155 | 0.13101 | 0.009846 | -0.021157 | -0.01586 | 0.008797 | 0.085583 | -0.11765 | -0.14439 | -0.016938 | -0.095785 | -0.069733 | 119.9185 | 120.0097 | 119.7509 | 119.8946 | 0.18136 | 0.0602 | 0.029197 | 0.034494 | 0.059151 | 0.13594 | -0.067301 | -0.094033 | 0.033416 | -0.045431 | -0.019379 | 119.9689 | 120.0601 | 119.8012 | 119.945 | -120.0629 | -119.8953 | -120.0143 | -119.8467
1196.125 | 120.2957 | -120.108 | 0.059509 | 0.12643 | -0.00389 | -0.021157 | -0.01586 | 0.008797 | 0.085583 | -0.11765 | -0.14439 | -0.030674 | -0.095785 | -0.065154 | 119.9552 | 120.0418 | 119.7829 | 119.9221 | 0.17678 | 0.046464 | 0.029197 | 0.034494 | 0.059151 | 0.13594 | -0.067301 | -0.094033 | 0.01968 | -0.045431 | -0.0148 | 120.0055 | 120.0922 | 119.8333 | 119.9724 | -120.0996 | -119.9273 | -120.051 | -119.8787
1197.8281 | 120.4422 | -120.1126 | 0.009155 | 0.12643 | 0.000689 | -0.016578 | -0.020438 | 0.008797 | 0.081005 | -0.13139 | -0.14897 | -0.016938 | -0.095785 | -0.074312 | 119.9918 | 120.0693 | 119.8196 | 119.9587 | 0.17678 | 0.051043 | 0.033776 | 0.029916 | 0.059151 | 0.13136 | -0.081036 | -0.098612 | 0.033416 | -0.045431 | -0.023958 | 120.0421 | 120.1196 | 119.8699 | 120.0091 | -120.1408 | -119.9685 | -120.0876 | -119.9153
1199.7188 | 120.4742 | -120.1401 | 0 | 0.13559 | -0.00389 | -0.021157 | -0.025017 | 0.017953 | 0.085583 | -0.11765 | -0.14439 | -0.021517 | -0.095785 | -0.065154 | 120.0193 | 120.1059 | 119.8562 | 119.9907 | 0.18594 | 0.046464 | 0.029197 | 0.025337 | 0.068307 | 0.13594 | -0.067301 | -0.094033 | 0.028837 | -0.045431 | -0.0148 | 120.0696 | 120.1562 | 119.9065 | 120.0411 | -120.1637 | -120.0006 | -120.1151 | -119.952
1201.4688 | 120.4926 | -120.1767 | -0.009155 | 0.13101 | -0.013048 | -0.030314 | -0.029595 | 0.004219 | 0.081005 | -0.12223 | -0.14439 | -0.026096 | -0.10036 | -0.069733 | 120.0513 | 120.1425 | 119.8837 | 120.032 | 0.18136 | 0.037306 | 0.02004 | 0.020759 | 0.054573 | 0.13136 | -0.07188 | -0.094033 | 0.024258 | -0.050009 | -0.019379 | 120.1017 | 120.1929 | 119.934 | 120.0823 | -120.1957 | -120.028 | -120.1517 | -119.984
1203.2188 | 120.3873 | -120.2637 | 0.027466 | 0.13559 | 0.000689 | -0.021157 | -0.020438 | 0.008797 | 0.081005 | -0.12223 | -0.13981 | -0.026096 | -0.10036 | -0.065154 | 120.0879 | 120.1746 | 119.9111 | 120.0594 | 0.18594 | 0.051043 | 0.029197 | 0.029916 | 0.059151 | 0.13136 | -0.07188 | -0.089455 | 0.024258 | -0.050009 | -0.0148 | 120.1383 | 120.2249 | 119.9615 | 120.1098 | -120.2277 | -120.0509 | -120.1883 | -120.0115
1204.9688 | 120.4559 | -120.2591 | 0.041199 | 0.13559 | 0.005267 | -0.025735 | -0.01586 | 0.008797 | 0.090161 | -0.11765 | -0.14439 | -0.026096 | -0.095785 | -0.065154 | 120.12 | 120.202 | 119.9432 | 120.0823 | 0.18594 | 0.055621 | 0.024619 | 0.034494 | 0.059151 | 0.14052 | -0.067301 | -0.094033 | 0.024258 | -0.045431 | -0.0148 | 120.1703 | 120.2524 | 119.9935 | 120.1327 | -120.2644 | -120.0876 | -120.2158 | -120.039
1206.7188 | 120.575 | -120.2682 | 0 | 0.12643 | -0.00389 | -0.034893 | -0.029595 | 0.004219 | 0.085583 | -0.13139 | -0.14439 | -0.021517 | -0.10036 | -0.069733 | 120.1475 | 120.2249 | 119.9752 | 120.1189 | 0.17678 | 0.046464 | 0.015461 | 0.020759 | 0.054573 | 0.13594 | -0.081036 | -0.094033 | 0.028837 | -0.050009 | -0.019379 | 120.1978 | 120.2753 | 120.0256 | 120.1693 | -120.2918 | -120.1196 | -120.2478 | -120.0756
1208.4688 | 120.4559 | -120.3278 | 0.018311 | 0.13559 | 0.000689 | -0.021157 | -0.020438 | 0.022531 | 0.085583 | -0.11308 | -0.14439 | -0.026096 | -0.095785 | -0.074312 | 120.1795 | 120.257 | 120.0027 | 120.1464 | 0.18594 | 0.051043 | 0.029197 | 0.029916 | 0.072885 | 0.13594 | -0.062723 | -0.094033 | 0.024258 | -0.045431 | -0.023958 | 120.2299 | 120.3073 | 120.053 | 120.1968 | -120.3239 | -120.1471 | -120.2753 | -120.0985
1210.1562 | 120.5795 | -120.3415 | -0.013733 | 0.13101 | -0.008469 | -0.025735 | -0.029595 | 0.008797 | 0.071848 | -0.12223 | -0.13981 | -0.021517 | -0.10036 | -0.074312 | 120.2024 | 120.2844 | 120.0302 | 120.1785 | 0.18136 | 0.041885 | 0.024619 | 0.020759 | 0.059151 | 0.1222 | -0.07188 | -0.089455 | 0.028837 | -0.050009 | -0.023958 | 120.2527 | 120.3348 | 120.0805 | 120.2288 | -120.3422 | -120.17 | -120.3028 | -120.1305
1211.9062 | 120.5292 | -120.4285 | 0.032043 | 0.12643 | -0.00389 | -0.025735 | -0.025017 | 0.008797 | 0.081005 | -0.12223 | -0.13981 | -0.026096 | -0.095785 | -0.069733 | 120.2253 | 120.3165 | 120.0622 | 120.2013 | 0.17678 | 0.046464 | 0.024619 | 0.025337 | 0.059151 | 0.13136 | -0.07188 | -0.089455 | 0.024258 | -0.045431 | -0.019379 | 120.2756 | 120.3668 | 120.1126 | 120.2517 | -120.3651 | -120.202 | -120.3211 | -120.158
1213.6562 | 120.6573 | -120.3873 | -0.004578 | 0.13101 | -0.008469 | -0.034893 | -0.025017 | 0.008797 | 0.090161 | -0.12223 | -0.13523 | -0.021517 | -0.095785 | -0.065154 | 120.2573 | 120.3348 | 120.0805 | 120.2334 | 0.18136 | 0.041885 | 0.015461 | 0.025337 | 0.059151 | 0.14052 | -0.07188 | -0.084876 | 0.028837 | -0.045431 | -0.0148 | 120.3077 | 120.3851 | 120.1309 | 120.2837 | -120.3926 | -120.2158 | -120.3531 | -120.1763
1215.3594 | 120.6665 | -120.4193 | 0.004578 | 0.13101 | 0.005267 | -0.030314 | -0.034174 | 0.008797 | 0.081005 | -0.11765 | -0.14439 | -0.021517 | -0.10494 | -0.069733 | 120.2756 | 120.3714 | 120.1126 | 120.2517 | 0.18136 | 0.055621 | 0.02004 | 0.01618 | 0.059151 | 0.13136 | -0.067301 | -0.094033 | 0.028837 | -0.054588 | -0.019379 | 120.326 | 120.4218 | 120.1629 | 120.3021 | -120.42 | -120.257 | -120.3806 | -120.2175
1217.1094 | 120.694 | -120.4514 | 0.004578 | 0.13101 | -0.00389 | -0.030314 | -0.029595 | 0.008797 | 0.076426 | -0.12223 | -0.14439 | -0.030674 | -0.095785 | -0.065154 | 120.3168 | 120.3943 | 120.14 | 120.2792 | 0.18136 | 0.046464 | 0.02004 | 0.020759 | 0.059151 | 0.12678 | -0.07188 | -0.094033 | 0.01968 | -0.045431 | -0.0148 | 120.3672 | 120.4447 | 120.1904 | 120.3295 | -120.4612 | -120.2844 | -120.4126 | -120.2358
1218.7969 | 120.726 | -120.4605 | 0.004578 | 0.13101 | 0.000689 | -0.034893 | -0.034174 | 0.008797 | 0.076426 | -0.12223 | -0.14897 | -0.016938 | -0.10036 | -0.074312 | 120.3306 | 120.4172 | 120.1629 | 120.3066 | 0.18136 | 0.051043 | 0.015461 | 0.01618 | 0.059151 | 0.12678 | -0.07188 | -0.098612 | 0.033416 | -0.050009 | -0.023958 | 120.3809 | 120.4676 | 120.2133 | 120.357 | -120.4795 | -120.3119 | -120.4309 | -120.2633
1220.5469 | 120.6894 | -120.52 | 0.013733 | 0.12185 | 0.005267 | -0.025735 | -0.038752 | 0.013375 | 0.085583 | -0.11765 | -0.14439 | -0.026096 | -0.10494 | -0.069733 | 120.3535 | 120.4447 | 120.1858 | 120.3295 | 0.1722 | 0.055621 | 0.024619 | 0.011602 | 0.063729 | 0.13594 | -0.067301 | -0.094033 | 0.024258 | -0.054588 | -0.019379 | 120.4038 | 120.495 | 120.2362 | 120.3799 | -120.4979 | -120.3302 | -120.4584 | -120.2908
1222.25 | 120.7397 | -120.5063 | 0.004578 | 0.13101 | -0.00389 | -0.025735 | -0.025017 | 0.004219 | 0.081005 | -0.11765 | -0.14439 | -0.021517 | -0.10952 | -0.069733 | 120.3855 | 120.4676 | 120.2087 | 120.3478 | 0.18136 | 0.046464 | 0.024619 | 0.025337 | 0.054573 | 0.13136 | -0.067301 | -0.094033 | 0.028837 | -0.059166 | -0.019379 | 120.4359 | 120.5179 | 120.2591 | 120.3982 | -120.5299 | -120.3531 | -120.495 | -120.3182
1224 | 120.7214 | -120.5795 | 0.018311 | 0.13101 | -0.00389 | -0.021157 | -0.025017 | 0.004219 | 0.076426 | -0.11765 | -0.13981 | -0.030674 | -0.10036 | -0.078891 | 120.4084 | 120.4859 | 120.2362 | 120.3707 | 0.18136 | 0.046464 | 0.029197 | 0.025337 | 0.054573 | 0.12678 | -0.067301 | -0.089455 | 0.01968 | -0.050009 | -0.028537 | 120.4588 | 120.5362 | 120.2865 | 120.4211 | -120.5482 | -120.376 | -120.5088 | -120.3365
1225.75 | 120.8542 | -120.5429 | -0.013733 | 0.12643 | -0.008469 | -0.030314 | -0.034174 | -0.000359 | 0.071848 | -0.12223 | -0.14897 | -0.021517 | -0.10494 | -0.074312 | 120.4267 | 120.5088 | 120.2545 | 120.3982 | 0.17678 | 0.041885 | 0.02004 | 0.01618 | 0.049995 | 0.1222 | -0.07188 | -0.098612 | 0.028837 | -0.054588 | -0.023958 | 120.4771 | 120.5591 | 120.3049 | 120.4486 | -120.5757 | -120.4035 | -120.5317 | -120.3594
1227.5 | 120.726 | -120.6024 | 0.036621 | 0.13559 | 0.000689 | -0.016578 | -0.029595 | 0.004219 | 0.085583 | -0.11765 | -0.13981 | -0.021517 | -0.10494 | -0.065154 | 120.4542 | 120.5362 | 120.2774 | 120.4165 | 0.18594 | 0.051043 | 0.033776 | 0.020759 | 0.054573 | 0.13594 | -0.067301 | -0.089455 | 0.028837 | -0.054588 | -0.0148 | 120.5045 | 120.5866 | 120.3277 | 120.4669 | -120.594 | -120.4172 | -120.5591 | -120.3823
1229.2031 | 120.8359 | -120.6299 | 0.032043 | 0.12643 | -0.008469 | -0.030314 | -0.029595 | 0.004219 | 0.071848 | -0.12223 | -0.13981 | -0.026096 | -0.10036 | -0.069733 | 120.4725 | 120.5545 | 120.2957 | 120.4394 | 0.17678 | 0.041885 | 0.02004 | 0.020759 | 0.054573 | 0.1222 | -0.07188 | -0.089455 | 0.024258 | -0.050009 | -0.019379 | 120.5229 | 120.6049 | 120.3461 | 120.4898 | -120.6123 | -120.4355 | -120.5729 | -120.3961
1230.9375 | 120.7672 | -120.6253 | 0.022888 | 0.12643 | -0.008469 | -0.025735 | -0.025017 | 0.004219 | 0.076426 | -0.12681 | -0.13523 | -0.021517 | -0.10494 | -0.069733 | 120.4862 | 120.582 | 120.3186 | 120.4623 | 0.17678 | 0.041885 | 0.024619 | 0.025337 | 0.054573 | 0.12678 | -0.076458 | -0.084876 | 0.028837 | -0.054588 | -0.019379 | 120.5366 | 120.6324 | 120.369 | 120.5127 | -120.6215 | -120.4538 | -120.5912 | -120.4235
1232.6875 | 120.8954 | -120.6345 | 0.009155 | 0.13559 | -0.013048 | -0.034893 | -0.034174 | -0.000359 | 0.071848 | -0.13139 | -0.14439 | -0.026096 | -0.10036 | -0.078891 | 120.5137 | 120.6003 | 120.3415 | 120.4852 | 0.18594 | 0.037306 | 0.015461 | 0.01618 | 0.049995 | 0.1222 | -0.081036 | -0.094033 | 0.024258 | -0.050009 | -0.028537 | 120.5641 | 120.6507 | 120.3918 | 120.5355 | -120.6581 | -120.4859 | -120.6141 | -120.4419
1234.4531 | 120.8633 | -120.694 | 0.036621 | 0.14017 | -0.008469 | -0.034893 | -0.034174 | -0.004937 | 0.081005 | -0.13139 | -0.14439 | -0.021517 | -0.10494 | -0.069733 | 120.532 | 120.6141 | 120.3644 | 120.5081 | 0.19052 | 0.041885 | 0.015461 | 0.01618 | 0.045417 | 0.13136 | -0.081036 | -0.094033 | 0.028837 | -0.054588 | -0.019379 | 120.5824 | 120.6644 | 120.4147 | 120.5584 | -120.6764 | -120.5088 | -120.637 | -120.4693
1236.1406 | 120.9045 | -120.7031 | 0.018311 | 0.13101 | -0.008469 | -0.025735 | -0.025017 | -0.000359 | 0.071848 | -0.13139 | -0.15354 | -0.021517 | -0.10494 | -0.065154 | 120.5503 | 120.6369 | 120.3827 | 120.5218 | 0.18136 | 0.041885 | 0.024619 | 0.025337 | 0.049995 | 0.1222 | -0.081036 | -0.10319 | 0.028837 | -0.054588 | -0.0148 | 120.6007 | 120.6873 | 120.433 | 120.5722 | -120.7039 | -120.5362 | -120.6553 | -120.4876
1237.8906 | 120.8862 | -120.7443 | 0.018311 | 0.13559 | -0.00389 | -0.030314 | -0.029595 | 0.004219 | 0.076426 | -0.12223 | -0.13981 | -0.021517 | -0.095785 | -0.069733 | 120.5686 | 120.6553 | 120.4056 | 120.5493 | 0.18594 | 0.046464 | 0.02004 | 0.020759 | 0.054573 | 0.12678 | -0.07188 | -0.089455 | 0.028837 | -0.045431 | -0.019379 | 120.619 | 120.7056 | 120.4559 | 120.5996 | -120.7085 | -120.5454 | -120.6644 | -120.5014
1239.6562 | 120.9 | -120.7306 | 0.036621 | 0.13101 | -0.013048 | -0.030314 | -0.025017 | 0.004219 | 0.076426 | -0.11308 | -0.14439 | -0.026096 | -0.10036 | -0.069733 | 120.5915 | 120.6736 | 120.4239 | 120.5584 | 0.18136 | 0.037306 | 0.02004 | 0.025337 | 0.054573 | 0.12678 | -0.062723 | -0.094033 | 0.024258 | -0.050009 | -0.019379 | 120.6419 | 120.7239 | 120.4743 | 120.6088 | -120.7359 | -120.5683 | -120.6919 | -120.5243
1241.3438 | 120.9229 | -120.7855 | 0.036621 | 0.14017 | -0.008469 | -0.030314 | -0.043331 | -0.004937 | 0.071848 | -0.13597 | -0.14439 | -0.026096 | -0.095785 | -0.074312 | 120.6098 | 120.6919 | 120.4422 | 120.5768 | 0.19052 | 0.041885 | 0.02004 | 0.007023 | 0.045417 | 0.1222 | -0.085614 | -0.094033 | 0.024258 | -0.045431 | -0.023958 | 120.6602 | 120.7422 | 120.4926 | 120.6271 | -120.7542 | -120.5866 | -120.7056 | -120.538
1243.0938 | 120.9824 | -120.7947 | 0.022888 | 0.13559 | -0.008469 | -0.030314 | -0.029595 | -0.000359 | 0.071848 | -0.12681 | -0.14897 | -0.012359 | -0.10036 | -0.074312 | 120.6236 | 120.7148 | 120.4559 | 120.5996 | 0.18594 | 0.041885 | 0.02004 | 0.020759 | 0.049995 | 0.1222 | -0.076458 | -0.098612 | 0.037995 | -0.050009 | -0.023958 | 120.6739 | 120.7651 | 120.5063 | 120.65 | -120.7725 | -120.6049 | -120.7239 | -120.5563
1245.4688 | 121.0464 | -120.7718 | 0.018311 | 0.13559 | -0.008469 | -0.034893 | -0.038752 | -0.004937 | 0.071848 | -0.13597 | -0.13981 | -0.021517 | -0.091207 | -0.065154 | 120.6511 | 120.7422 | 120.488 | 120.6225 | 0.18594 | 0.041885 | 0.015461 | 0.011602 | 0.045417 | 0.1222 | -0.085614 | -0.089455 | 0.028837 | -0.040853 | -0.0148 | 120.7014 | 120.7926 | 120.5384 | 120.6729 | -120.7909 | -120.6278 | -120.7423 | -120.5792
1248.7812 | 121.0648 | -120.8038 | 0 | 0.13101 | -0.013048 | -0.025735 | -0.034174 | -0.004937 | 0.062691 | -0.13139 | -0.14439 | -0.030674 | -0.10036 | -0.065154 | 120.6923 | 120.7697 | 120.5155 | 120.6592 | 0.18136 | 0.037306 | 0.024619 | 0.01618 | 0.045417 | 0.11305 | -0.081036 | -0.094033 | 0.01968 | -0.050009 | -0.0148 | 120.7426 | 120.8201 | 120.5658 | 120.7095 | -120.8366 | -120.6599 | -120.7926 | -120.6158
1252.2656 | 121.1014 | -120.8405 | 0.009155 | 0.13101 | -0.013048 | -0.039471 | -0.034174 | -0.004937 | 0.067269 | -0.13139 | -0.12607 | -0.00778 | -0.086628 | -0.069733 | 120.7014 | 120.788 | 120.5475 | 120.6729 | 0.18136 | 0.037306 | 0.010883 | 0.01618 | 0.045417 | 0.11762 | -0.081036 | -0.075719 | 0.042574 | -0.036274 | -0.019379 | 120.7518 | 120.8384 | 120.5979 | 120.7232 | -120.8275 | -120.6736 | -120.788 | -120.6341
1257.8594 | 121.1243 | -120.9045 | 0.022888 | 0.14017 | -0.013048 | -0.039471 | -0.029595 | 0.004219 | 0.071848 | -0.12223 | -0.13065 | -0.016938 | -0.08205 | -0.060575 | 120.7518 | 120.8384 | 120.5841 | 120.7324 | 0.19052 | 0.037306 | 0.010883 | 0.020759 | 0.054573 | 0.1222 | -0.07188 | -0.080298 | 0.033416 | -0.031696 | -0.010221 | 120.8021 | 120.8887 | 120.6345 | 120.7828 | -120.8824 | -120.7148 | -120.8338 | -120.6662
1259.6406 | 121.1334 | -120.9229 | 0.054932 | 0.14017 | -0.00389 | -0.039471 | -0.038752 | -0.004937 | 0.062691 | -0.13139 | -0.14439 | -0.016938 | -0.10036 | -0.060575 | 120.7564 | 120.8613 | 120.6116 | 120.7507 | 0.19052 | 0.046464 | 0.010883 | 0.011602 | 0.045417 | 0.11305 | -0.081036 | -0.094033 | 0.033416 | -0.050009 | -0.010221 | 120.8067 | 120.9116 | 120.662 | 120.8011 | -120.9007 | -120.756 | -120.8567 | -120.712
1261.3438 | 121.1334 | -120.9366 | 0.027466 | 0.13559 | -0.013048 | -0.039471 | -0.034174 | -0.000359 | 0.067269 | -0.13139 | -0.13065 | -0.016938 | -0.08205 | -0.060575 | 120.7838 | 120.8704 | 120.6208 | 120.7645 | 0.18594 | 0.037306 | 0.010883 | 0.01618 | 0.049995 | 0.11762 | -0.081036 | -0.080298 | 0.033416 | -0.031696 | -0.010221 | 120.8342 | 120.9208 | 120.6711 | 120.8148 | -120.9145 | -120.7514 | -120.8659 | -120.7028
1263.0469 | 121.0922 | -120.9641 | 0.032043 | 0.13101 | -0.017627 | -0.039471 | -0.034174 | -0.009515 | 0.067269 | -0.13139 | -0.1215 | -0.012359 | -0.086628 | -0.060575 | 120.8021 | 120.8887 | 120.6299 | 120.7782 | 0.18136 | 0.032727 | 0.010883 | 0.01618 | 0.040839 | 0.11762 | -0.081036 | -0.071141 | 0.037995 | -0.036274 | -0.010221 | 120.8525 | 120.9391 | 120.6803 | 120.8285 | -120.9236 | -120.7514 | -120.8888 | -120.7166
1264.7969 | 121.225 | -120.9412 | 0 | 0.13559 | -0.022205 | -0.048628 | -0.038752 | -0.014093 | 0.067269 | -0.13597 | -0.13065 | -0.016938 | -0.095785 | -0.060575 | 120.8159 | 120.8933 | 120.6528 | 120.7965 | 0.18594 | 0.028149 | 0.001726 | 0.011602 | 0.036261 | 0.11762 | -0.085614 | -0.080298 | 0.033416 | -0.045431 | -0.010221 | 120.8662 | 120.9437 | 120.7032 | 120.8469 | -120.9465 | -120.7835 | -120.9117 | -120.7486
1266.5625 | 121.1838 | -120.9778 | 0.018311 | 0.13559 | -0.017627 | -0.034893 | -0.038752 | -0.009515 | 0.062691 | -0.12681 | -0.13065 | -0.012359 | -0.091207 | -0.060575 | 120.825 | 120.9162 | 120.6574 | 120.8148 | 0.18594 | 0.032727 | 0.015461 | 0.011602 | 0.040839 | 0.11305 | -0.076458 | -0.080298 | 0.037995 | -0.040853 | -0.010221 | 120.8754 | 120.9666 | 120.7078 | 120.8652 | -120.9557 | -120.788 | -120.9162 | -120.7486
1268.25 | 121.1609 | -121.0007 | 0.022888 | 0.13559 | -0.017627 | -0.034893 | -0.043331 | -0.009515 | 0.067269 | -0.13139 | -0.13065 | -0.016938 | -0.086628 | -0.069733 | 120.8479 | 120.9299 | 120.6757 | 120.8194 | 0.18594 | 0.032727 | 0.015461 | 0.007023 | 0.040839 | 0.11762 | -0.081036 | -0.080298 | 0.033416 | -0.036274 | -0.019379 | 120.8983 | 120.9803 | 120.7261 | 120.8698 | -120.9786 | -120.8064 | -120.9345 | -120.7623
1270 | 121.1975 | -121.0327 | 0.027466 | 0.13101 | -0.008469 | -0.039471 | -0.047909 | -0.004937 | 0.067269 | -0.14055 | -0.13065 | -0.012359 | -0.086628 | -0.055996 | 120.8571 | 120.9437 | 120.6894 | 120.8331 | 0.18136 | 0.041885 | 0.010883 | 0.002445 | 0.045417 | 0.11762 | -0.090192 | -0.080298 | 0.037995 | -0.036274 | -0.005642 | 120.9074 | 120.994 | 120.7398 | 120.8835 | -120.9877 | -120.8201 | -120.9437 | -120.7761
1271.75 | 121.1838 | -121.0419 | 0.045776 | 0.13559 | -0.013048 | -0.04405 | -0.038752 | -0.009515 | 0.062691 | -0.14055 | -0.13981 | -0.016938 | -0.086628 | -0.060575 | 120.8754 | 120.9574 | 120.7032 | 120.8423 | 0.18594 | 0.037306 | 0.006304 | 0.011602 | 0.040839 | 0.11305 | -0.090192 | -0.089455 | 0.033416 | -0.036274 | -0.010221 | 120.9257 | 121.0078 | 120.7535 | 120.8926 | -121.0152 | -120.843 | -120.962 | -120.7898
1273.4375 | 121.2158 | -121.0419 | 0.018311 | 0.14017 | -0.013048 | -0.04405 | -0.047909 | -0.014093 | 0.058113 | -0.14055 | -0.13523 | -0.016938 | -0.091207 | -0.060575 | 120.8845 | 120.9666 | 120.7169 | 120.8606 | 0.19052 | 0.037306 | 0.006304 | 0.002445 | 0.036261 | 0.10847 | -0.090192 | -0.084876 | 0.033416 | -0.040853 | -0.010221 | 120.9349 | 121.0169 | 120.7673 | 120.911 | -121.0198 | -120.8521 | -120.9757 | -120.8081
1275.1094 | 121.257 | -121.0648 | 0.041199 | 0.13559 | -0.022205 | -0.048628 | -0.047909 | -0.014093 | 0.058113 | -0.1497 | -0.13981 | -0.021517 | -0.095785 | -0.065154 | 120.8983 | 120.9803 | 120.7307 | 120.8698 | 0.18594 | 0.028149 | 0.001726 | 0.002445 | 0.036261 | 0.10847 | -0.099349 | -0.089455 | 0.028837 | -0.045431 | -0.0148 | 120.9486 | 121.0307 | 120.781 | 120.9201 | -121.0381 | -120.8705 | -120.9941 | -120.8264
1276.7969 | 121.225 | -121.0876 | 0.027466 | 0.13101 | -0.026784 | -0.053207 | -0.047909 | -0.009515 | 0.058113 | -0.14055 | -0.13523 | -0.016938 | -0.091207 | -0.055996 | 120.9074 | 120.994 | 120.7352 | 120.8881 | 0.18136 | 0.02357 | -0.002853 | 0.002445 | 0.040839 | 0.10847 | -0.090192 | -0.084876 | 0.033416 | -0.040853 | -0.005642 | 120.9578 | 121.0444 | 120.7856 | 120.9384 | -121.0427 | -120.8705 | -120.9986 | -120.8264
1278.4844 | 121.3257 | -121.0327 | 0.022888 | 0.13559 | -0.022205 | -0.053207 | -0.057066 | -0.014093 | 0.053534 | -0.14055 | -0.13981 | -0.012359 | -0.091207 | -0.060575 | 120.9212 | 121.0078 | 120.7535 | 120.9018 | 0.18594 | 0.028149 | -0.002853 | -0.006712 | 0.036261 | 0.10389 | -0.090192 | -0.089455 | 0.037995 | -0.040853 | -0.010221 | 120.9715 | 121.0581 | 120.8039 | 120.9522 | -121.061 | -120.8934 | -121.0124 | -120.8448
1280.1875 | 121.4081 | -121.0693 | 0.004578 | 0.13101 | -0.026784 | -0.053207 | -0.057066 | -0.018671 | 0.048956 | -0.1497 | -0.13523 | -0.012359 | -0.091207 | -0.055996 | 120.9395 | 121.0261 | 120.7673 | 120.9155 | 0.18136 | 0.02357 | -0.002853 | -0.006712 | 0.031683 | 0.09931 | -0.099349 | -0.084876 | 0.037995 | -0.040853 | -0.005642 | 120.9898 | 121.0764 | 120.8176 | 120.9659 | -121.0747 | -120.9025 | -121.0307 | -120.8585
1281.8906 | 121.376 | -121.0693 | 0.009155 | 0.13559 | -0.035942 | -0.053207 | -0.061645 | -0.023249 | 0.048956 | -0.15428 | -0.13065 | -0.016938 | -0.095785 | -0.065154 | 120.9532 | 121.0352 | 120.7764 | 120.9339 | 0.18594 | 0.014412 | -0.002853 | -0.011291 | 0.027105 | 0.09931 | -0.10393 | -0.080298 | 0.033416 | -0.045431 | -0.0148 | 121.0036 | 121.0856 | 120.8268 | 120.9842 | -121.0839 | -120.9071 | -121.049 | -120.8722
1283.5781 | 121.4218 | -121.0739 | 0.013733 | 0.13101 | -0.040521 | -0.053207 | -0.057066 | -0.018671 | 0.039799 | -0.1497 | -0.13065 | -0.012359 | -0.086628 | -0.055996 | 120.9532 | 121.0444 | 120.7947 | 120.943 | 0.18136 | 0.009833 | -0.002853 | -0.006712 | 0.031683 | 0.090153 | -0.099349 | -0.080298 | 0.037995 | -0.036274 | -0.005642 | 121.0036 | 121.0947 | 120.8451 | 120.9934 | -121.0839 | -120.9254 | -121.0398 | -120.8814
1285.3125 | 121.3257 | -121.1105 | 0.027466 | 0.13101 | -0.035942 | -0.057786 | -0.057066 | -0.018671 | 0.044377 | -0.15428 | -0.13981 | -0.00778 | -0.086628 | -0.065154 | 120.9669 | 121.0535 | 120.7993 | 120.9476 | 0.18136 | 0.014412 | -0.007432 | -0.006712 | 0.031683 | 0.094731 | -0.10393 | -0.089455 | 0.042574 | -0.036274 | -0.0148 | 121.0173 | 121.1039 | 120.8497 | 120.9979 | -121.1068 | -120.9391 | -121.0536 | -120.886
1287.0156 | 121.4035 | -121.106 | 0.009155 | 0.13559 | -0.040521 | -0.062364 | -0.066223 | -0.027827 | 0.039799 | -0.15428 | -0.13065 | -0.012359 | -0.086628 | -0.060575 | 120.9807 | 121.0719 | 120.8131 | 120.9613 | 0.18594 | 0.009833 | -0.01201 | -0.015869 | 0.022527 | 0.090153 | -0.10393 | -0.080298 | 0.037995 | -0.036274 | -0.010221 | 121.031 | 121.1222 | 120.8634 | 121.0117 | -121.1113 | -120.9437 | -121.0673 | -120.8997
1288.7656 | 121.344 | -121.1563 | 0.032043 | 0.13559 | -0.040521 | -0.066943 | -0.066223 | -0.032405 | 0.035221 | -0.15886 | -0.13523 | -0.016938 | -0.086628 | -0.055996 | 120.9898 | 121.0764 | 120.8222 | 120.9705 | 0.18594 | 0.009833 | -0.016589 | -0.015869 | 0.017949 | 0.085575 | -0.1085 | -0.084876 | 0.033416 | -0.036274 | -0.005642 | 121.0402 | 121.1268 | 120.8726 | 121.0208 | -121.1251 | -120.9575 | -121.0765 | -120.9088
1290.5156 | 121.3165 | -121.1792 | 0.041199 | 0.13559 | -0.0451 | -0.071521 | -0.066223 | -0.032405 | 0.039799 | -0.16344 | -0.13523 | -0.016938 | -0.086628 | -0.065154 | 121.0082 | 121.0948 | 120.8405 | 120.9842 | 0.18594 | 0.005254 | -0.021167 | -0.015869 | 0.017949 | 0.090153 | -0.11308 | -0.084876 | 0.033416 | -0.036274 | -0.0148 | 121.0585 | 121.1451 | 120.8909 | 121.0346 | -121.1434 | -120.9758 | -121.0948 | -120.9272
1292.2188 | 121.4172 | -121.1517 | -0.004578 | 0.14017 | -0.058836 | -0.071521 | -0.07538 | -0.036983 | 0.035221 | -0.16801 | -0.13523 | -0.012359 | -0.095785 | -0.060575 | 121.0173 | 121.1085 | 120.8405 | 120.9888 | 0.19052 | -0.008482 | -0.021167 | -0.025026 | 0.013371 | 0.085575 | -0.11766 | -0.084876 | 0.037995 | -0.045431 | -0.010221 | 121.0677 | 121.1588 | 120.8909 | 121.0391 | -121.1525 | -120.9758 | -121.1131 | -120.9363
1293.9688 | 121.3577 | -121.17 | 0.041199 | 0.13559 | -0.0451 | -0.066943 | -0.070802 | -0.036983 | 0.044377 | -0.15886 | -0.13523 | -0.012359 | -0.086628 | -0.060575 | 121.031 | 121.1176 | 120.8588 | 121.0071 | 0.18594 | 0.005254 | -0.016589 | -0.020448 | 0.013371 | 0.094731 | -0.1085 | -0.084876 | 0.037995 | -0.036274 | -0.010221 | 121.0814 | 121.168 | 120.9092 | 121.0575 | -121.1663 | -120.9941 | -121.1177 | -120.9455
1295.6562 | 121.3623 | -121.2067 | 0.036621 | 0.13101 | -0.054257 | -0.071521 | -0.07538 | -0.036983 | 0.039799 | -0.16344 | -0.13523 | -0.021517 | -0.086628 | -0.060575 | 121.0356 | 121.1268 | 120.8634 | 121.0208 | 0.18136 | -0.003903 | -0.021167 | -0.025026 | 0.013371 | 0.090153 | -0.11308 | -0.084876 | 0.028837 | -0.036274 | -0.010221 | 121.086 | 121.1772 | 120.9138 | 121.0712 | -121.1708 | -120.9987 | -121.1222 | -120.9501
1297.4062 | 121.3623 | -121.1975 | 0.054932 | 0.14474 | -0.054257 | -0.071521 | -0.07538 | -0.041561 | 0.039799 | -0.15886 | -0.13523 | -0.016938 | -0.091207 | -0.055996 | 121.0448 | 121.1405 | 120.8909 | 121.03 | 0.1951 | -0.003903 | -0.021167 | -0.025026 | 0.008793 | 0.090153 | -0.1085 | -0.084876 | 0.033416 | -0.040853 | -0.005642 | 121.0951 | 121.1909 | 120.9412 | 121.0803 | -121.18 | -121.0261 | -121.136 | -120.9821
1299.1719 | 121.4996 | -121.1655 | 0.009155 | 0.13559 | -0.054257 | -0.071521 | -0.07538 | -0.041561 | 0.026064 | -0.16801 | -0.13981 | -0.012359 | -0.091207 | -0.065154 | 121.0585 | 121.1451 | 120.8955 | 121.0392 | 0.18594 | -0.003903 | -0.021167 | -0.025026 | 0.008793 | 0.076418 | -0.11766 | -0.089455 | 0.037995 | -0.040853 | -0.0148 | 121.1089 | 121.1955 | 120.9458 | 121.0895 | -121.1983 | -121.0353 | -121.1497 | -120.9867
1300.9219 | 121.5088 | -121.1975 | 0 | 0.13101 | -0.049678 | -0.071521 | -0.079959 | -0.046138 | 0.030642 | -0.15886 | -0.13523 | -0.016938 | -0.091207 | -0.055996 | 121.0722 | 121.1543 | 120.9092 | 121.0529 | 0.18136 | 0.000676 | -0.021167 | -0.029605 | 0.004216 | 0.080996 | -0.1085 | -0.084876 | 0.033416 | -0.040853 | -0.005642 | 121.1226 | 121.2046 | 120.9596 | 121.1032 | -121.2075 | -121.0444 | -121.1635 | -121.0004
1302.625 | 121.4722 | -121.2021 | 0.013733 | 0.13559 | -0.063415 | -0.066943 | -0.07538 | -0.032405 | 0.035221 | -0.16344 | -0.13523 | -0.016938 | -0.086628 | -0.060575 | 121.0722 | 121.1772 | 120.9092 | 121.0529 | 0.18594 | -0.013061 | -0.016589 | -0.025026 | 0.017949 | 0.085575 | -0.11308 | -0.084876 | 0.033416 | -0.036274 | -0.010221 | 121.1226 | 121.2275 | 120.9596 | 121.1032 | -121.2075 | -121.0444 | -121.1589 | -120.9958
1304.375 | 121.5271 | -121.2158 | 0.004578 | 0.13101 | -0.049678 | -0.0761 | -0.079959 | -0.046138 | 0.026064 | -0.16801 | -0.13523 | -0.016938 | -0.086628 | -0.065154 | 121.086 | 121.1772 | 120.9184 | 121.0758 | 0.18136 | 0.000676 | -0.025746 | -0.029605 | 0.004216 | 0.076418 | -0.11766 | -0.084876 | 0.033416 | -0.036274 | -0.0148 | 121.1363 | 121.2275 | 120.9687 | 121.1261 | -121.2212 | -121.0536 | -121.1726 | -121.005
1306.1406 | 121.5454 | -121.2158 | 0.018311 | 0.13559 | -0.058836 | -0.0761 | -0.084537 | -0.036983 | 0.026064 | -0.17717 | -0.13523 | -0.012359 | -0.091207 | -0.065154 | 121.1043 | 121.1955 | 120.9367 | 121.0804 | 0.18594 | -0.008482 | -0.025746 | -0.034183 | 0.013371 | 0.076418 | -0.12682 | -0.084876 | 0.037995 | -0.040853 | -0.0148 | 121.1546 | 121.2458 | 120.987 | 121.1307 | -121.2395 | -121.0719 | -121.1955 | -121.0279
1307.8281 | 121.5134 | -121.2204 | 0.018311 | 0.13101 | -0.054257 | -0.0761 | -0.084537 | -0.046138 | 0.026064 | -0.16801 | -0.13065 | -0.016938 | -0.086628 | -0.065154 | 121.1089 | 121.2046 | 120.9413 | 121.0987 | 0.18136 | -0.003903 | -0.025746 | -0.034183 | 0.004216 | 0.076418 | -0.11766 | -0.080298 | 0.033416 | -0.036274 | -0.0148 | 121.1592 | 121.255 | 120.9916 | 121.149 | -121.2395 | -121.0719 | -121.1955 | -121.0279
1309.5625 | 121.5225 | -121.257 | 0.018311 | 0.13559 | -0.067994 | -0.0761 | -0.084537 | -0.046138 | 0.026064 | -0.17259 | -0.13523 | -0.021517 | -0.091207 | -0.055996 | 121.118 | 121.2138 | 120.9458 | 121.0987 | 0.18594 | -0.01764 | -0.025746 | -0.034183 | 0.004216 | 0.076418 | -0.12224 | -0.084876 | 0.028837 | -0.040853 | -0.005642 | 121.1684 | 121.2641 | 120.9962 | 121.149 | -121.2533 | -121.0811 | -121.2092 | -121.037
1311.3281 | 121.5637 | -121.2479 | 0.004578 | 0.14017 | -0.063415 | -0.080679 | -0.079959 | -0.050716 | 0.021485 | -0.17259 | -0.14897 | -0.012359 | -0.091207 | -0.069733 | 121.1318 | 121.2229 | 120.9642 | 121.1124 | 0.19052 | -0.013061 | -0.030325 | -0.029605 | -0.000362 | 0.071839 | -0.12224 | -0.098612 | 0.037995 | -0.040853 | -0.019379 | 121.1821 | 121.2733 | 121.0145 | 121.1628 | -121.2807 | -121.1131 | -121.223 | -121.0554
1313.0781 | 121.5683 | -121.2387 | -0.004578 | 0.13559 | -0.058836 | -0.0761 | -0.089116 | -0.046138 | 0.026064 | -0.17259 | -0.14439 | -0.012359 | -0.091207 | -0.065154 | 121.1455 | 121.2275 | 120.9733 | 121.1261 | 0.18594 | -0.008482 | -0.025746 | -0.038762 | 0.004216 | 0.076418 | -0.12224 | -0.094033 | 0.037995 | -0.040853 | -0.0148 | 121.1958 | 121.2779 | 121.0237 | 121.1765 | -121.2899 | -121.1177 | -121.2367 | -121.0645
1314.7656 | 121.5637 | -121.2891 | -0.009155 | 0.13101 | -0.058836 | -0.0761 | -0.084537 | -0.046138 | 0.021485 | -0.17717 | -0.13523 | -0.016938 | -0.095785 | -0.065154 | 121.1547 | 121.2367 | 120.987 | 121.1307 | 0.18136 | -0.008482 | -0.025746 | -0.034183 | 0.004216 | 0.071839 | -0.12682 | -0.084876 | 0.033416 | -0.045431 | -0.0148 | 121.205 | 121.287 | 121.0374 | 121.1811 | -121.2899 | -121.1223 | -121.2504 | -121.0828
1316.5156 | 121.5591 | -121.2845 | 0.018311 | 0.13559 | -0.058836 | -0.0761 | -0.093694 | -0.046138 | 0.026064 | -0.18175 | -0.13523 | -0.021517 | -0.086628 | -0.065154 | 121.1638 | 121.2504 | 120.9916 | 121.149 | 0.18594 | -0.008482 | -0.025746 | -0.04334 | 0.004216 | 0.076418 | -0.1314 | -0.084876 | 0.028837 | -0.036274 | -0.0148 | 121.2142 | 121.3008 | 121.042 | 121.1994 | -121.299 | -121.1269 | -121.2504 | -121.0782
1318.2656 | 121.5408 | -121.3257 | 0.018311 | 0.13559 | -0.063415 | -0.089836 | -0.089116 | -0.046138 | 0.021485 | -0.17259 | -0.14439 | -0.016938 | -0.086628 | -0.065154 | 121.1684 | 121.2596 | 121.0008 | 121.1444 | 0.18594 | -0.013061 | -0.039482 | -0.038762 | 0.004216 | 0.071839 | -0.12224 | -0.094033 | 0.033416 | -0.036274 | -0.0148 | 121.2187 | 121.3099 | 121.0511 | 121.1948 | -121.3128 | -121.1452 | -121.255 | -121.0874
1320.0156 | 121.4767 | -121.3577 | 0.045776 | 0.14017 | -0.063415 | -0.085257 | -0.084537 | -0.050716 | 0.021485 | -0.17717 | -0.14439 | -0.016938 | -0.095785 | -0.060575 | 121.1821 | 121.2687 | 121.0099 | 121.1582 | 0.19052 | -0.013061 | -0.034903 | -0.034183 | -0.000362 | 0.071839 | -0.12682 | -0.094033 | 0.033416 | -0.045431 | -0.010221 | 121.2325 | 121.3191 | 121.0603 | 121.2085 | -121.3265 | -121.1543 | -121.2779 | -121.1057
1321.7188 | 121.5225 | -121.3257 | 0.009155 | 0.13559 | -0.063415 | -0.080679 | -0.084537 | -0.046138 | 0.026064 | -0.17259 | -0.13065 | -0.016938 | -0.10036 | -0.065154 | 121.1913 | 121.2779 | 121.0145 | 121.1719 | 0.18594 | -0.013061 | -0.030325 | -0.034183 | 0.004216 | 0.076418 | -0.12224 | -0.080298 | 0.033416 | -0.050009 | -0.0148 | 121.2416 | 121.3282 | 121.0649 | 121.2223 | -121.3219 | -121.1452 | -121.2916 | -121.1149
1323.4844 | 121.6049 | -121.344 | 0.018311 | 0.13101 | -0.077151 | -0.089836 | -0.093694 | -0.050716 | 0.016907 | -0.17717 | -0.13523 | -0.016938 | -0.095785 | -0.060575 | 121.2004 | 121.287 | 121.042 | 121.1857 | 0.18136 | -0.026797 | -0.039482 | -0.04334 | -0.000362 | 0.067261 | -0.12682 | -0.084876 | 0.033416 | -0.045431 | -0.010221 | 121.2508 | 121.3374 | 121.0923 | 121.236 | -121.3357 | -121.1772 | -121.2962 | -121.1378
1325.1719 | 121.6232 | -121.344 | 0 | 0.13559 | -0.067994 | -0.098993 | -0.093694 | -0.050716 | 0.021485 | -0.17717 | -0.13981 | -0.021517 | -0.095785 | -0.065154 | 121.2096 | 121.2916 | 121.0328 | 121.1902 | 0.18594 | -0.01764 | -0.048639 | -0.04334 | -0.000362 | 0.071839 | -0.12682 | -0.089455 | 0.028837 | -0.045431 | -0.0148 | 121.2599 | 121.342 | 121.0832 | 121.2406 | -121.3494 | -121.1726 | -121.3054 | -121.1286
1326.9375 | 121.5958 | -121.3531 | 0.009155 | 0.13101 | -0.067994 | -0.089836 | -0.093694 | -0.059872 | 0.016907 | -0.18175 | -0.13981 | -0.026096 | -0.095785 | -0.065154 | 121.2187 | 121.3008 | 121.042 | 121.1902 | 0.18136 | -0.01764 | -0.039482 | -0.04334 | -0.009518 | 0.067261 | -0.1314 | -0.089455 | 0.024258 | -0.045431 | -0.0148 | 121.2691 | 121.3511 | 121.0923 | 121.2406 | -121.3586 | -121.1818 | -121.3145 | -121.1378
1328.6875 | 121.5363 | -121.3989 | 0.045776 | 0.14017 | -0.072572 | -0.089836 | -0.098273 | -0.055294 | 0.012329 | -0.18175 | -0.13981 | -0.021517 | -0.10036 | -0.060575 | 121.2233 | 121.3099 | 121.0557 | 121.2085 | 0.19052 | -0.022218 | -0.039482 | -0.047919 | -0.00494 | 0.062683 | -0.1314 | -0.089455 | 0.028837 | -0.050009 | -0.010221 | 121.2737 | 121.3603 | 121.1061 | 121.2589 | -121.3631 | -121.1955 | -121.3237 | -121.1561
1330.375 | 121.6507 | -121.3623 | 0.018311 | 0.13559 | -0.072572 | -0.094414 | -0.10285 | -0.059872 | 0.00775 | -0.18175 | -0.14439 | -0.016938 | -0.095785 | -0.069733 | 121.2279 | 121.3191 | 121.0603 | 121.2131 | 0.18594 | -0.022218 | -0.04406 | -0.052497 | -0.009518 | 0.058104 | -0.1314 | -0.094033 | 0.033416 | -0.045431 | -0.019379 | 121.2783 | 121.3694 | 121.1106 | 121.2635 | -121.3723 | -121.2047 | -121.3237 | -121.1561
1332.125 | 121.5454 | -121.4172 | 0.041199 | 0.13101 | -0.067994 | -0.094414 | -0.093694 | -0.059872 | 0.016907 | -0.18633 | -0.13981 | -0.021517 | -0.10494 | -0.065154 | 121.2325 | 121.3237 | 121.0695 | 121.2223 | 0.18136 | -0.01764 | -0.04406 | -0.04334 | -0.009518 | 0.067261 | -0.13597 | -0.089455 | 0.028837 | -0.054588 | -0.0148 | 121.2828 | 121.374 | 121.1198 | 121.2726 | -121.3723 | -121.2093 | -121.3374 | -121.1744
1333.875 | 121.6599 | -121.376 | 0.004578 | 0.13559 | -0.072572 | -0.089836 | -0.098273 | -0.059872 | 0.003172 | -0.18175 | -0.13981 | -0.016938 | -0.095785 | -0.060575 | 121.2462 | 121.342 | 121.0786 | 121.2314 | 0.18594 | -0.022218 | -0.039482 | -0.047919 | -0.009518 | 0.053526 | -0.1314 | -0.089455 | 0.033416 | -0.045431 | -0.010221 | 121.2966 | 121.3923 | 121.129 | 121.2818 | -121.386 | -121.2184 | -121.342 | -121.1744
1335.5625 | 121.5729 | -121.4264 | 0.036621 | 0.13559 | -0.072572 | -0.098993 | -0.10743 | -0.059872 | 0.00775 | -0.18633 | -0.13523 | -0.016938 | -0.10036 | -0.065154 | 121.26 | 121.342 | 121.0832 | 121.2406 | 0.18594 | -0.022218 | -0.048639 | -0.057076 | -0.009518 | 0.058104 | -0.13597 | -0.084876 | 0.033416 | -0.050009 | -0.0148 | 121.3103 | 121.3923 | 121.1335 | 121.2909 | -121.3952 | -121.2184 | -121.3603 | -121.1836
1337.3125 | 121.6141 | -121.4172 | 0.036621 | 0.13559 | -0.086309 | -0.10357 | -0.11201 | -0.059872 | 0.00775 | -0.19091 | -0.13523 | -0.021517 | -0.095785 | -0.069733 | 121.2691 | 121.3511 | 121.0923 | 121.2406 | 0.18594 | -0.035955 | -0.053218 | -0.061654 | -0.009518 | 0.058104 | -0.14055 | -0.084876 | 0.028837 | -0.045431 | -0.019379 | 121.3195 | 121.4015 | 121.1427 | 121.2909 | -121.4043 | -121.2276 | -121.3649 | -121.1881
1339.0625 | 121.6599 | -121.4172 | 0.013733 | 0.13101 | -0.072572 | -0.098993 | -0.10285 | -0.069028 | 0.003172 | -0.19548 | -0.13523 | -0.021517 | -0.095785 | -0.069733 | 121.2737 | 121.3603 | 121.1107 | 121.2497 | 0.18136 | -0.022218 | -0.048639 | -0.052497 | -0.018674 | 0.053526 | -0.14513 | -0.084876 | 0.028837 | -0.045431 | -0.019379 | 121.324 | 121.4106 | 121.161 | 121.3001 | -121.4089 | -121.2459 | -121.3695 | -121.2064
1340.8125 | 121.6187 | -121.431 | 0.032043 | 0.13559 | -0.077151 | -0.098993 | -0.10285 | -0.069028 | 0.012329 | -0.19548 | -0.13523 | -0.016938 | -0.10494 | -0.055996 | 121.2783 | 121.3694 | 121.1015 | 121.2635 | 0.18594 | -0.026797 | -0.048639 | -0.052497 | -0.018674 | 0.062683 | -0.14513 | -0.084876 | 0.033416 | -0.054588 | -0.005642 | 121.3286 | 121.4198 | 121.1519 | 121.3138 | -121.4135 | -121.2367 | -121.3832 | -121.2064
1342.5625 | 121.637 | -121.4355 | 0.022888 | 0.14017 | -0.086309 | -0.10357 | -0.11201 | -0.073606 | 0.003172 | -0.19548 | -0.13981 | -0.021517 | -0.095785 | -0.069733 | 121.2966 | 121.3832 | 121.1152 | 121.2772 | 0.19052 | -0.035955 | -0.053218 | -0.061654 | -0.023252 | 0.053526 | -0.14513 | -0.089455 | 0.028837 | -0.045431 | -0.019379 | 121.3469 | 121.4335 | 121.1656 | 121.3276 | -121.4364 | -121.255 | -121.3924 | -121.211
1344.3125 | 121.6415 | -121.4493 | 0.022888 | 0.14017 | -0.086309 | -0.11273 | -0.11659 | -0.06445 | 0.00775 | -0.20922 | -0.14439 | -0.021517 | -0.095785 | -0.069733 | 121.3012 | 121.3877 | 121.129 | 121.2726 | 0.19052 | -0.035955 | -0.062375 | -0.066233 | -0.014096 | 0.058104 | -0.15886 | -0.094033 | 0.028837 | -0.045431 | -0.019379 | 121.3515 | 121.4381 | 121.1793 | 121.323 | -121.4455 | -121.2734 | -121.3969 | -121.2248
1346 | 121.7285 | -121.4355 | 0.022888 | 0.14017 | -0.095467 | -0.11731 | -0.11201 | -0.078184 | -0.010563 | -0.20922 | -0.13523 | -0.016938 | -0.10036 | -0.065154 | 121.3012 | 121.3877 | 121.1335 | 121.2909 | 0.19052 | -0.045113 | -0.066953 | -0.061654 | -0.02783 | 0.039791 | -0.15886 | -0.084876 | 0.033416 | -0.050009 | -0.0148 | 121.3515 | 121.4381 | 121.1839 | 121.3413 | -121.4364 | -121.2688 | -121.4015 | -121.2339
1347.75 | 121.701 | -121.463 | 0.013733 | 0.14017 | -0.095467 | -0.11731 | -0.11659 | -0.073606 | -0.01972 | -0.2138 | -0.13981 | -0.016938 | -0.095785 | -0.065154 | 121.3057 | 121.3923 | 121.1473 | 121.3001 | 0.19052 | -0.045113 | -0.066953 | -0.066233 | -0.023252 | 0.030634 | -0.16344 | -0.089455 | 0.033416 | -0.045431 | -0.0148 | 121.3561 | 121.4427 | 121.1976 | 121.3505 | -121.4455 | -121.2871 | -121.4015 | -121.2431
1349.4375 | 121.6232 | -121.4676 | 0.041199 | 0.14017 | -0.095467 | -0.10815 | -0.12116 | -0.08734 | -0.010563 | -0.20922 | -0.13065 | -0.021517 | -0.10036 | -0.065154 | 121.3195 | 121.4061 | 121.1519 | 121.3093 | 0.19052 | -0.045113 | -0.057796 | -0.070811 | -0.036986 | 0.039791 | -0.15886 | -0.080298 | 0.028837 | -0.050009 | -0.0148 | 121.3698 | 121.4564 | 121.2022 | 121.3596 | -121.4501 | -121.2825 | -121.4198 | -121.2522
1351.2031 | 121.6415 | -121.5042 | 0.045776 | 0.13559 | -0.10462 | -0.11273 | -0.13032 | -0.08734 | -0.015142 | -0.2138 | -0.14439 | -0.021517 | -0.095785 | -0.060575 | 121.3149 | 121.4152 | 121.161 | 121.3047 | 0.18594 | -0.05427 | -0.062375 | -0.079968 | -0.036986 | 0.035212 | -0.16344 | -0.094033 | 0.028837 | -0.045431 | -0.010221 | 121.3652 | 121.4656 | 121.2114 | 121.355 | -121.4593 | -121.3054 | -121.4107 | -121.2568
1352.9688 | 121.6965 | -121.4722 | 0.013733 | 0.13559 | -0.10462 | -0.12646 | -0.13032 | -0.091918 | -0.024298 | -0.22295 | -0.14897 | -0.026096 | -0.10036 | -0.069733 | 121.3332 | 121.4244 | 121.161 | 121.323 | 0.18594 | -0.05427 | -0.076111 | -0.079968 | -0.041564 | 0.026056 | -0.1726 | -0.098612 | 0.024258 | -0.050009 | -0.019379 | 121.3836 | 121.4747 | 121.2114 | 121.3734 | -121.4822 | -121.31 | -121.4336 | -121.2614
1354.7188 | 121.6461 | -121.5134 | 0.032043 | 0.13559 | -0.10462 | -0.13104 | -0.13948 | -0.096496 | -0.01972 | -0.22295 | -0.13065 | -0.021517 | -0.091207 | -0.060575 | 121.3378 | 121.429 | 121.1748 | 121.3276 | 0.18594 | -0.05427 | -0.080689 | -0.089125 | -0.046142 | 0.030634 | -0.1726 | -0.080298 | 0.028837 | -0.040853 | -0.010221 | 121.3881 | 121.4793 | 121.2251 | 121.3779 | -121.4684 | -121.3054 | -121.429 | -121.266
1356.4062 | 121.6507 | -121.5454 | 0.022888 | 0.13559 | -0.1092 | -0.12646 | -0.12574 | -0.091918 | -0.028877 | -0.22295 | -0.13981 | -0.021517 | -0.095785 | -0.069733 | 121.3515 | 121.4381 | 121.1885 | 121.3276 | 0.18594 | -0.058849 | -0.076111 | -0.07539 | -0.041564 | 0.021477 | -0.1726 | -0.089455 | 0.028837 | -0.045431 | -0.019379 | 121.4019 | 121.4885 | 121.2388 | 121.3779 | -121.4913 | -121.3283 | -121.4473 | -121.2843
1358.1562 | 121.6599 | -121.5637 | 0.032043 | 0.13101 | -0.11378 | -0.13104 | -0.13032 | -0.091918 | -0.033455 | -0.22753 | -0.14439 | -0.016938 | -0.091207 | -0.065154 | 121.3515 | 121.4473 | 121.1885 | 121.3459 | 0.18136 | -0.063428 | -0.080689 | -0.079968 | -0.041564 | 0.016899 | -0.17718 | -0.094033 | 0.033416 | -0.040853 | -0.0148 | 121.4019 | 121.4976 | 121.2388 | 121.3962 | -121.4959 | -121.3329 | -121.4427 | -121.2797
1359.8438 | 121.7926 | -121.4951 | 0 | 0.13101 | -0.11836 | -0.1402 | -0.1349 | -0.10565 | -0.028877 | -0.23211 | -0.13523 | -0.021517 | -0.10036 | -0.069733 | 121.3652 | 121.4518 | 121.1885 | 121.3505 | 0.18136 | -0.068007 | -0.089846 | -0.084547 | -0.055298 | 0.021477 | -0.18176 | -0.084876 | 0.028837 | -0.050009 | -0.019379 | 121.4156 | 121.5022 | 121.2388 | 121.4008 | -121.5005 | -121.3237 | -121.4656 | -121.2889
1361.5938 | 121.7194 | -121.55 | 0.032043 | 0.13101 | -0.11378 | -0.1402 | -0.13948 | -0.10107 | -0.028877 | -0.22753 | -0.13981 | -0.021517 | -0.095785 | -0.065154 | 121.3698 | 121.4564 | 121.1976 | 121.355 | 0.18136 | -0.063428 | -0.089846 | -0.089125 | -0.05072 | 0.021477 | -0.17718 | -0.089455 | 0.028837 | -0.045431 | -0.0148 | 121.4202 | 121.5068 | 121.248 | 121.4054 | -121.5096 | -121.3375 | -121.4656 | -121.2934
1363.3438 | 121.7377 | -121.5271 | 0.032043 | 0.13559 | -0.12294 | -0.14478 | -0.13948 | -0.10565 | -0.042612 | -0.23669 | -0.13981 | -0.016938 | -0.091207 | -0.069733 | 121.379 | 121.4656 | 121.216 | 121.3505 | 0.18594 | -0.072585 | -0.094425 | -0.089125 | -0.055298 | 0.007742 | -0.18633 | -0.089455 | 0.033416 | -0.040853 | -0.019379 | 121.4293 | 121.5159 | 121.2663 | 121.4008 | -121.5188 | -121.3558 | -121.4702 | -121.3072
1365.0312 | 121.7422 | -121.5408 | 0.027466 | 0.13101 | -0.11836 | -0.14936 | -0.14864 | -0.11023 | -0.042612 | -0.24127 | -0.13523 | -0.021517 | -0.10036 | -0.065154 | 121.3881 | 121.4656 | 121.2205 | 121.3688 | 0.18136 | -0.068007 | -0.099004 | -0.098282 | -0.059876 | 0.007742 | -0.19091 | -0.084876 | 0.028837 | -0.050009 | -0.0148 | 121.4385 | 121.5159 | 121.2709 | 121.4191 | -121.5234 | -121.3558 | -121.4885 | -121.3209
1366.7812 | 121.7606 | -121.5225 | 0.004578 | 0.13101 | -0.1321 | -0.14936 | -0.15321 | -0.11481 | -0.04719 | -0.24584 | -0.13065 | -0.016938 | -0.095785 | -0.065154 | 121.3973 | 121.4702 | 121.2251 | 121.3734 | 0.18136 | -0.081743 | -0.099004 | -0.10286 | -0.064454 | 0.003164 | -0.19549 | -0.080298 | 0.033416 | -0.045431 | -0.0148 | 121.4476 | 121.5205 | 121.2755 | 121.4237 | -121.5279 | -121.3558 | -121.4931 | -121.3209
1368.4688 | 121.7743 | -121.5454 | 0.013733 | 0.13101 | -0.1321 | -0.14936 | -0.15779 | -0.11939 | -0.056347 | -0.24584 | -0.13523 | -0.016938 | -0.10036 | -0.065154 | 121.3973 | 121.4839 | 121.2251 | 121.3825 | 0.18136 | -0.081743 | -0.099004 | -0.10744 | -0.069032 | -0.005993 | -0.19549 | -0.084876 | 0.033416 | -0.050009 | -0.0148 | 121.4476 | 121.5342 | 121.2755 | 121.4329 | -121.5325 | -121.3603 | -121.4977 | -121.3255
1370.2188 | 121.7514 | -121.5454 | 0.036621 | 0.13559 | -0.12752 | -0.15851 | -0.15779 | -0.12396 | -0.056347 | -0.25042 | -0.14439 | -0.026096 | -0.10036 | -0.074312 | 121.3973 | 121.4839 | 121.2389 | 121.3871 | 0.18594 | -0.077164 | -0.10816 | -0.10744 | -0.07361 | -0.005993 | -0.20007 | -0.094033 | 0.024258 | -0.050009 | -0.023958 | 121.4476 | 121.5342 | 121.2892 | 121.4374 | -121.5417 | -121.3832 | -121.4977 | -121.3392
1371.9688 | 121.8384 | -121.5546 | -0.009155 | 0.13559 | -0.1321 | -0.15851 | -0.16237 | -0.12854 | -0.070082 | -0.25042 | -0.14439 | -0.021517 | -0.10036 | -0.069733 | 121.4156 | 121.493 | 121.2434 | 121.3962 | 0.18594 | -0.081743 | -0.10816 | -0.11202 | -0.078188 | -0.019728 | -0.20007 | -0.094033 | 0.028837 | -0.050009 | -0.019379 | 121.466 | 121.5434 | 121.2938 | 121.4466 | -121.56 | -121.3878 | -121.516 | -121.3438
1373.7344 | 121.7972 | -121.5591 | 0.009155 | 0.14017 | -0.15041 | -0.16767 | -0.15779 | -0.13312 | -0.065504 | -0.255 | -0.13981 | -0.021517 | -0.095785 | -0.069733 | 121.4156 | 121.5022 | 121.248 | 121.4054 | 0.19052 | -0.10006 | -0.11732 | -0.10744 | -0.082766 | -0.01515 | -0.20465 | -0.089455 | 0.028837 | -0.045431 | -0.019379 | 121.466 | 121.5526 | 121.2984 | 121.4558 | -121.5554 | -121.3878 | -121.5114 | -121.3438
1375.4219 | 121.8658 | -121.5408 | 0 | 0.14017 | -0.15041 | -0.17225 | -0.16695 | -0.13312 | -0.070082 | -0.26416 | -0.13981 | -0.016938 | -0.091207 | -0.069733 | 121.4248 | 121.5159 | 121.2526 | 121.4146 | 0.19052 | -0.10006 | -0.1219 | -0.1166 | -0.082766 | -0.019728 | -0.2138 | -0.089455 | 0.033416 | -0.040853 | -0.019379 | 121.4751 | 121.5663 | 121.3029 | 121.4649 | -121.5646 | -121.3924 | -121.516 | -121.3438
1377.1719 | 121.7148 | -121.582 | 0.045776 | 0.13559 | -0.14583 | -0.16309 | -0.16237 | -0.12854 | -0.070082 | -0.255 | -0.13981 | -0.026096 | -0.095785 | -0.065154 | 121.4248 | 121.5114 | 121.2572 | 121.4146 | 0.18594 | -0.095479 | -0.11274 | -0.11202 | -0.078188 | -0.019728 | -0.20465 | -0.089455 | 0.024258 | -0.045431 | -0.0148 | 121.4751 | 121.5617 | 121.3075 | 121.4649 | -121.5646 | -121.397 | -121.5205 | -121.353
1378.9219 | 121.7331 | -121.5958 | 0.036621 | 0.13559 | -0.15041 | -0.17225 | -0.17153 | -0.13312 | -0.065504 | -0.26874 | -0.13523 | -0.016938 | -0.091207 | -0.069733 | 121.4339 | 121.5251 | 121.2617 | 121.4237 | 0.18594 | -0.10006 | -0.1219 | -0.12117 | -0.082766 | -0.01515 | -0.21838 | -0.084876 | 0.033416 | -0.040853 | -0.019379 | 121.4843 | 121.5754 | 121.3121 | 121.4741 | -121.5692 | -121.397 | -121.5251 | -121.353
1380.625 | 121.8613 | -121.5683 | -0.013733 | 0.13559 | -0.15499 | -0.17225 | -0.16695 | -0.13312 | -0.074661 | -0.26874 | -0.14439 | -0.016938 | -0.091207 | -0.065154 | 121.4385 | 121.5297 | 121.2801 | 121.4283 | 0.18594 | -0.10464 | -0.1219 | -0.1166 | -0.082766 | -0.024307 | -0.21838 | -0.094033 | 0.033416 | -0.040853 | -0.0148 | 121.4889 | 121.58 | 121.3304 | 121.4786 | -121.5829 | -121.4244 | -121.5297 | -121.3713
1382.3906 | 121.8292 | -121.6049 | 0 | 0.13101 | -0.15957 | -0.17225 | -0.17153 | -0.14228 | -0.070082 | -0.27331 | -0.13981 | -0.021517 | -0.10036 | -0.069733 | 121.4477 | 121.5388 | 121.2755 | 121.4375 | 0.18136 | -0.10922 | -0.1219 | -0.12117 | -0.091922 | -0.019728 | -0.22296 | -0.089455 | 0.028837 | -0.050009 | -0.019379 | 121.498 | 121.5892 | 121.3258 | 121.4878 | -121.5875 | -121.4153 | -121.548 | -121.3758
1384.1406 | 121.8063 | -121.6095 | 0.027466 | 0.13101 | -0.14583 | -0.17683 | -0.16695 | -0.13312 | -0.074661 | -0.26874 | -0.13981 | -0.021517 | -0.095785 | -0.055996 | 121.4522 | 121.5342 | 121.2801 | 121.4375 | 0.18136 | -0.095479 | -0.12647 | -0.1166 | -0.082766 | -0.024307 | -0.21838 | -0.089455 | 0.028837 | -0.045431 | -0.005642 | 121.5026 | 121.5846 | 121.3304 | 121.4878 | -121.592 | -121.4199 | -121.548 | -121.3758
1385.875 | 121.8613 | -121.5775 | -0.004578 | 0.13101 | -0.15041 | -0.17225 | -0.17611 | -0.12854 | -0.074661 | -0.26874 | -0.13523 | -0.012359 | -0.095785 | -0.069733 | 121.466 | 121.5526 | 121.2846 | 121.4375 | 0.18136 | -0.10006 | -0.1219 | -0.12575 | -0.078188 | -0.024307 | -0.21838 | -0.084876 | 0.037995 | -0.045431 | -0.019379 | 121.5163 | 121.6029 | 121.335 | 121.4878 | -121.6012 | -121.4199 | -121.5618 | -121.3804
1387.5625 | 121.8796 | -121.5729 | -0.004578 | 0.13559 | -0.15957 | -0.18141 | -0.18069 | -0.14685 | -0.079239 | -0.27331 | -0.13981 | -0.016938 | -0.095785 | -0.069733 | 121.4614 | 121.5526 | 121.2984 | 121.4512 | 0.18594 | -0.10922 | -0.13105 | -0.13033 | -0.0965 | -0.028885 | -0.22296 | -0.089455 | 0.033416 | -0.045431 | -0.019379 | 121.5117 | 121.6029 | 121.3487 | 121.5015 | -121.6012 | -121.4382 | -121.5572 | -121.3942
1389.3281 | 121.7926 | -121.637 | 0.018311 | 0.13559 | -0.15041 | -0.18141 | -0.18069 | -0.1377 | -0.074661 | -0.26874 | -0.13981 | -0.021517 | -0.095785 | -0.074312 | 121.4751 | 121.5571 | 121.2984 | 121.4558 | 0.18594 | -0.10006 | -0.13105 | -0.13033 | -0.087344 | -0.024307 | -0.21838 | -0.089455 | 0.028837 | -0.045431 | -0.023958 | 121.5255 | 121.6075 | 121.3487 | 121.5061 | -121.6149 | -121.4382 | -121.5709 | -121.3942
1391.0781 | 121.8658 | -121.6095 | 0.027466 | 0.13101 | -0.16415 | -0.18599 | -0.18984 | -0.15143 | -0.083817 | -0.27789 | -0.14439 | -0.021517 | -0.095785 | -0.074312 | 121.4751 | 121.5663 | 121.303 | 121.4649 | 0.18136 | -0.11379 | -0.13563 | -0.13949 | -0.10108 | -0.033463 | -0.22754 | -0.094033 | 0.028837 | -0.045431 | -0.023958 | 121.5255 | 121.6166 | 121.3533 | 121.5153 | -121.6195 | -121.4473 | -121.5709 | -121.3987
1392.7812 | 121.7697 | -121.6553 | 0.054932 | 0.13101 | -0.16415 | -0.18599 | -0.18984 | -0.15143 | -0.088396 | -0.28705 | -0.13981 | -0.026096 | -0.095785 | -0.069733 | 121.4797 | 121.5663 | 121.3075 | 121.4649 | 0.18136 | -0.11379 | -0.13563 | -0.13949 | -0.10108 | -0.038042 | -0.23669 | -0.089455 | 0.024258 | -0.045431 | -0.019379 | 121.5301 | 121.6166 | 121.3579 | 121.5153 | -121.6195 | -121.4473 | -121.5755 | -121.4033
1394.5312 | 121.8018 | -121.637 | 0.018311 | 0.13559 | -0.16415 | -0.19057 | -0.18526 | -0.15143 | -0.092974 | -0.27789 | -0.13981 | -0.021517 | -0.10036 | -0.055996 | 121.4934 | 121.58 | 121.3213 | 121.4695 | 0.18594 | -0.11379 | -0.14021 | -0.13491 | -0.10108 | -0.04262 | -0.22754 | -0.089455 | 0.028837 | -0.050009 | -0.005642 | 121.5438 | 121.6304 | 121.3716 | 121.5199 | -121.6332 | -121.4611 | -121.5938 | -121.4216
1396.2969 | 121.8384 | -121.6461 | 0.018311 | 0.13101 | -0.17331 | -0.19514 | -0.18984 | -0.15143 | -0.083817 | -0.28247 | -0.13523 | -0.021517 | -0.10036 | -0.065154 | 121.498 | 121.58 | 121.3213 | 121.4832 | 0.18136 | -0.12295 | -0.14479 | -0.13949 | -0.10108 | -0.033463 | -0.23212 | -0.084876 | 0.028837 | -0.050009 | -0.0148 | 121.5484 | 121.6304 | 121.3716 | 121.5336 | -121.6332 | -121.4565 | -121.5984 | -121.4216
1398 | 121.7926 | -121.6827 | 0.036621 | 0.13559 | -0.17788 | -0.19972 | -0.199 | -0.15601 | -0.10213 | -0.28705 | -0.13981 | -0.012359 | -0.10036 | -0.069733 | 121.5026 | 121.5892 | 121.3304 | 121.4878 | 0.18594 | -0.12753 | -0.14937 | -0.14865 | -0.10566 | -0.051777 | -0.23669 | -0.089455 | 0.037995 | -0.050009 | -0.019379 | 121.5529 | 121.6395 | 121.3808 | 121.5382 | -121.6424 | -121.4702 | -121.603 | -121.4308
1399.75 | 121.9391 | -121.6324 | -0.013733 | 0.12643 | -0.17331 | -0.19972 | -0.20358 | -0.15601 | -0.10213 | -0.28705 | -0.13981 | -0.016938 | -0.091207 | -0.069733 | 121.5072 | 121.5983 | 121.335 | 121.4878 | 0.17678 | -0.12295 | -0.14937 | -0.15322 | -0.10566 | -0.051777 | -0.23669 | -0.089455 | 0.033416 | -0.040853 | -0.019379 | 121.5575 | 121.6487 | 121.3854 | 121.5382 | -121.647 | -121.4748 | -121.5984 | -121.4262
1401.5 | 121.907 | -121.6507 | 0.022888 | 0.14017 | -0.18704 | -0.19972 | -0.199 | -0.17432 | -0.10671 | -0.2962 | -0.13981 | -0.021517 | -0.095785 | -0.065154 | 121.5072 | 121.5983 | 121.3396 | 121.4878 | 0.19052 | -0.13669 | -0.14937 | -0.14865 | -0.12397 | -0.056355 | -0.24585 | -0.089455 | 0.028837 | -0.045431 | -0.0148 | 121.5575 | 121.6487 | 121.3899 | 121.5382 | -121.647 | -121.4794 | -121.603 | -121.4354
1403.25 | 121.9299 | -121.6553 | 0.009155 | 0.14017 | -0.18704 | -0.20888 | -0.199 | -0.16517 | -0.10213 | -0.2962 | -0.13981 | -0.016938 | -0.095785 | -0.065154 | 121.5163 | 121.6075 | 121.3533 | 121.5015 | 0.19052 | -0.13669 | -0.15853 | -0.14865 | -0.11481 | -0.051777 | -0.24585 | -0.089455 | 0.033416 | -0.045431 | -0.0148 | 121.5667 | 121.6578 | 121.4037 | 121.5519 | -121.6561 | -121.4931 | -121.6121 | -121.4491
1404.9375 | 121.8796 | -121.669 | 0.041199 | 0.13559 | -0.18246 | -0.19972 | -0.20358 | -0.16974 | -0.10671 | -0.29163 | -0.14439 | -0.021517 | -0.095785 | -0.069733 | 121.5255 | 121.6121 | 121.3487 | 121.5061 | 0.18594 | -0.13211 | -0.14937 | -0.15322 | -0.11939 | -0.056355 | -0.24127 | -0.094033 | 0.028837 | -0.045431 | -0.019379 | 121.5758 | 121.6624 | 121.3991 | 121.5565 | -121.6699 | -121.4931 | -121.6213 | -121.4445
1406.6875 | 121.8292 | -121.6736 | 0.032043 | 0.14017 | -0.18704 | -0.20888 | -0.20358 | -0.16517 | -0.10671 | -0.2962 | -0.13981 | -0.026096 | -0.095785 | -0.069733 | 121.5301 | 121.6121 | 121.3579 | 121.5199 | 0.19052 | -0.13669 | -0.15853 | -0.15322 | -0.11481 | -0.056355 | -0.24585 | -0.089455 | 0.024258 | -0.045431 | -0.019379 | 121.5804 | 121.6624 | 121.4082 | 121.5702 | -121.6699 | -121.4977 | -121.6258 | -121.4537
1408.4375 | 121.8521 | -121.6873 | 0.027466 | 0.14017 | -0.1962 | -0.21346 | -0.20816 | -0.16974 | -0.11587 | -0.30078 | -0.13981 | -0.016938 | -0.091207 | -0.065154 | 121.5301 | 121.6212 | 121.3625 | 121.5199 | 0.19052 | -0.14585 | -0.1631 | -0.1578 | -0.11939 | -0.065512 | -0.25043 | -0.089455 | 0.033416 | -0.040853 | -0.0148 | 121.5804 | 121.6716 | 121.4128 | 121.5702 | -121.6699 | -121.5023 | -121.6213 | -121.4537
1410.1875 | 121.962 | -121.669 | -0.009155 | 0.13101 | -0.20078 | -0.21804 | -0.22647 | -0.18348 | -0.11587 | -0.31452 | -0.14439 | -0.021517 | -0.10036 | -0.069733 | 121.5392 | 121.6304 | 121.3716 | 121.5336 | 0.18136 | -0.15043 | -0.16768 | -0.17612 | -0.13312 | -0.065512 | -0.26416 | -0.094033 | 0.028837 | -0.050009 | -0.019379 | 121.5896 | 121.6807 | 121.422 | 121.5839 | -121.6836 | -121.516 | -121.6396 | -121.472
1411.875 | 121.9482 | -121.6507 | 0.018311 | 0.13559 | -0.20078 | -0.22262 | -0.22647 | -0.18348 | -0.1296 | -0.30994 | -0.14439 | -0.026096 | -0.10036 | -0.069733 | 121.5392 | 121.635 | 121.3716 | 121.529 | 0.18594 | -0.15043 | -0.17226 | -0.17612 | -0.13312 | -0.079247 | -0.25959 | -0.094033 | 0.024258 | -0.050009 | -0.019379 | 121.5896 | 121.6853 | 121.422 | 121.5794 | -121.6836 | -121.516 | -121.6396 | -121.472
1413.625 | 121.843 | -121.7056 | 0.032043 | 0.13101 | -0.20994 | -0.23177 | -0.22647 | -0.18805 | -0.13876 | -0.32367 | -0.14439 | -0.021517 | -0.10036 | -0.060575 | 121.5438 | 121.635 | 121.3808 | 121.5427 | 0.18136 | -0.15958 | -0.18142 | -0.17612 | -0.1377 | -0.088404 | -0.27332 | -0.094033 | 0.028837 | -0.050009 | -0.010221 | 121.5942 | 121.6853 | 121.4311 | 121.5931 | -121.6882 | -121.5252 | -121.6442 | -121.4811
1415.375 | 121.8338 | -121.7056 | 0.032043 | 0.13101 | -0.21452 | -0.24551 | -0.23563 | -0.21094 | -0.13876 | -0.33283 | -0.14439 | -0.026096 | -0.091207 | -0.065154 | 121.553 | 121.6441 | 121.3762 | 121.5382 | 0.18136 | -0.16416 | -0.19515 | -0.18527 | -0.16059 | -0.088404 | -0.28248 | -0.094033 | 0.024258 | -0.040853 | -0.0148 | 121.6033 | 121.6945 | 121.4266 | 121.5885 | -121.6973 | -121.5206 | -121.6442 | -121.4674
1417.0625 | 121.9162 | -121.701 | 0.032043 | 0.13101 | -0.22367 | -0.24551 | -0.24479 | -0.20637 | -0.15249 | -0.33741 | -0.14439 | -0.021517 | -0.095785 | -0.069733 | 121.5575 | 121.6441 | 121.3899 | 121.5473 | 0.18136 | -0.17332 | -0.19515 | -0.19443 | -0.15601 | -0.10214 | -0.28705 | -0.094033 | 0.028837 | -0.045431 | -0.019379 | 121.6079 | 121.6945 | 121.4403 | 121.5977 | -121.7019 | -121.5343 | -121.6533 | -121.4857
1418.8125 | 121.8704 | -121.7148 | 0.054932 | 0.13559 | -0.23741 | -0.25009 | -0.25852 | -0.21552 | -0.15707 | -0.35114 | -0.13065 | -0.026096 | -0.10494 | -0.065154 | 121.5621 | 121.6487 | 121.3945 | 121.5565 | 0.18594 | -0.18706 | -0.19973 | -0.20817 | -0.16517 | -0.10672 | -0.30079 | -0.080298 | 0.024258 | -0.054588 | -0.0148 | 121.6125 | 121.6991 | 121.4449 | 121.6068 | -121.6928 | -121.5252 | -121.6671 | -121.4995
1420.5 | 121.907 | -121.701 | 0.018311 | 0.13101 | -0.24199 | -0.2684 | -0.26768 | -0.22926 | -0.17081 | -0.36488 | -0.13981 | -0.021517 | -0.091207 | -0.074312 | 121.5713 | 121.6533 | 121.3945 | 121.5565 | 0.18136 | -0.19163 | -0.21805 | -0.21732 | -0.1789 | -0.12045 | -0.31452 | -0.089455 | 0.028837 | -0.040853 | -0.023958 | 121.6216 | 121.7036 | 121.4449 | 121.6068 | -121.7111 | -121.5343 | -121.6625 | -121.4857
1422.25 | 121.9528 | -121.7056 | 0.018311 | 0.13559 | -0.2603 | -0.27756 | -0.27683 | -0.24757 | -0.18454 | -0.37861 | -0.13523 | -0.012359 | -0.10036 | -0.074312 | 121.5758 | 121.6624 | 121.4037 | 121.5565 | 0.18594 | -0.20995 | -0.2272 | -0.22648 | -0.19722 | -0.13419 | -0.32826 | -0.084876 | 0.037995 | -0.050009 | -0.023958 | 121.6262 | 121.7128 | 121.454 | 121.6068 | -121.7111 | -121.5389 | -121.6762 | -121.504
1424 | 122.0169 | -121.7056 | -0.018311 | 0.13559 | -0.2603 | -0.28672 | -0.28599 | -0.25215 | -0.18912 | -0.37861 | -0.13981 | -0.021517 | -0.091207 | -0.065154 | 121.5804 | 121.6624 | 121.3991 | 121.5656 | 0.18594 | -0.20995 | -0.23636 | -0.23564 | -0.20179 | -0.13877 | -0.32826 | -0.089455 | 0.028837 | -0.040853 | -0.0148 | 121.6308 | 121.7128 | 121.4495 | 121.616 | -121.7202 | -121.5389 | -121.6716 | -121.4903
1425.6875 | 121.9025 | -121.7514 | 0.036621 | 0.13559 | -0.27404 | -0.29129 | -0.29515 | -0.25672 | -0.1937 | -0.38777 | -0.13981 | -0.021517 | -0.091207 | -0.065154 | 121.5758 | 121.6716 | 121.4174 | 121.5748 | 0.18594 | -0.22369 | -0.24094 | -0.24479 | -0.20637 | -0.14335 | -0.33741 | -0.089455 | 0.028837 | -0.040853 | -0.0148 | 121.6262 | 121.7219 | 121.4678 | 121.6252 | -121.7157 | -121.5572 | -121.6671 | -121.5086
1427.4375 | 121.9757 | -121.7285 | 0 | 0.13559 | -0.27862 | -0.30045 | -0.3043 | -0.26588 | -0.19828 | -0.40608 | -0.14439 | -0.026096 | -0.095785 | -0.069733 | 121.5896 | 121.6762 | 121.422 | 121.5794 | 0.18594 | -0.22826 | -0.2501 | -0.25395 | -0.21553 | -0.14792 | -0.35573 | -0.094033 | 0.024258 | -0.045431 | -0.019379 | 121.6399 | 121.7265 | 121.4723 | 121.6297 | -121.734 | -121.5664 | -121.6854 | -121.5178
1429.2031 | 121.9116 | -121.7422 | 0.009155 | 0.13559 | -0.28778 | -0.31419 | -0.30888 | -0.26588 | -0.20743 | -0.4015 | -0.14439 | -0.016938 | -0.10036 | -0.060575 | 121.5987 | 121.6807 | 121.422 | 121.5794 | 0.18594 | -0.23742 | -0.26383 | -0.25853 | -0.21553 | -0.15708 | -0.35115 | -0.094033 | 0.033416 | -0.050009 | -0.010221 | 121.6491 | 121.7311 | 121.4723 | 121.6297 | -121.7431 | -121.5664 | -121.6991 | -121.5224
1430.8906 | 121.9299 | -121.7606 | 0.036621 | 0.12643 | -0.30151 | -0.32792 | -0.31804 | -0.28877 | -0.22117 | -0.42439 | -0.14439 | -0.030674 | -0.10494 | -0.074312 | 121.6033 | 121.6853 | 121.4266 | 121.5885 | 0.17678 | -0.25116 | -0.27757 | -0.26769 | -0.23842 | -0.17081 | -0.37404 | -0.094033 | 0.01968 | -0.054588 | -0.023958 | 121.6537 | 121.7357 | 121.4769 | 121.6389 | -121.7477 | -121.571 | -121.7083 | -121.5315
1432.6406 | 121.8887 | -121.8155 | 0.032043 | 0.13559 | -0.30609 | -0.3325 | -0.33636 | -0.29335 | -0.23948 | -0.42897 | -0.13981 | -0.030674 | -0.091207 | -0.065154 | 121.6079 | 121.6899 | 121.4357 | 121.5977 | 0.18594 | -0.25574 | -0.28215 | -0.286 | -0.24299 | -0.18913 | -0.37862 | -0.089455 | 0.01968 | -0.040853 | -0.0148 | 121.6582 | 121.7403 | 121.4861 | 121.648 | -121.7477 | -121.5755 | -121.6991 | -121.5269
1434.3594 | 122.0261 | -121.7468 | 0.009155 | 0.13559 | -0.32899 | -0.35082 | -0.34551 | -0.31624 | -0.24864 | -0.43355 | -0.13523 | -0.016938 | -0.095785 | -0.065154 | 121.6079 | 121.6945 | 121.4449 | 121.5931 | 0.18594 | -0.27863 | -0.30046 | -0.29516 | -0.26588 | -0.19828 | -0.3832 | -0.084876 | 0.033416 | -0.045431 | -0.0148 | 121.6582 | 121.7448 | 121.4952 | 121.6435 | -121.7431 | -121.5801 | -121.7037 | -121.5407
1436.1094 | 122.0123 | -121.7606 | 0.013733 | 0.13559 | -0.34272 | -0.36455 | -0.3684 | -0.32539 | -0.2578 | -0.45644 | -0.13981 | -0.026096 | -0.091207 | -0.069733 | 121.6079 | 121.7036 | 121.4449 | 121.6023 | 0.18594 | -0.29237 | -0.3142 | -0.31805 | -0.27504 | -0.20744 | -0.40609 | -0.089455 | 0.024258 | -0.040853 | -0.019379 | 121.6582 | 121.754 | 121.4952 | 121.6526 | -121.7477 | -121.5847 | -121.6991 | -121.5361
1437.8594 | 121.9986 | -121.756 | 0.022888 | 0.13101 | -0.3473 | -0.37371 | -0.3684 | -0.33455 | -0.27153 | -0.47018 | -0.13523 | -0.021517 | -0.091207 | -0.065154 | 121.617 | 121.7036 | 121.4449 | 121.6114 | 0.18136 | -0.29695 | -0.32336 | -0.31805 | -0.2842 | -0.22118 | -0.41982 | -0.084876 | 0.028837 | -0.040853 | -0.0148 | 121.6674 | 121.754 | 121.4952 | 121.6618 | -121.7523 | -121.5801 | -121.7083 | -121.5361
1439.5469 | 122.0032 | -121.7377 | 0.027466 | 0.13101 | -0.37477 | -0.3966 | -0.38672 | -0.35286 | -0.299 | -0.47475 | -0.13981 | -0.012359 | -0.095785 | -0.065154 | 121.6216 | 121.7082 | 121.4495 | 121.6114 | 0.18136 | -0.32442 | -0.34625 | -0.33636 | -0.30251 | -0.24865 | -0.4244 | -0.089455 | 0.037995 | -0.045431 | -0.0148 | 121.672 | 121.7586 | 121.4998 | 121.6618 | -121.7614 | -121.5893 | -121.7174 | -121.5452
1441.3125 | 121.9482 | -121.7697 | 0.041199 | 0.13559 | -0.38851 | -0.41492 | -0.40503 | -0.37575 | -0.31732 | -0.50222 | -0.13981 | -0.030674 | -0.091207 | -0.069733 | 121.6216 | 121.7082 | 121.454 | 121.616 | 0.18594 | -0.33816 | -0.36456 | -0.35468 | -0.3254 | -0.26696 | -0.45187 | -0.089455 | 0.01968 | -0.040853 | -0.019379 | 121.672 | 121.7586 | 121.5044 | 121.6664 | -121.7614 | -121.5938 | -121.7128 | -121.5452
1443.0625 | 121.9345 | -121.7972 | 0.041199 | 0.13559 | -0.39767 | -0.42407 | -0.41877 | -0.39406 | -0.32189 | -0.51596 | -0.13981 | -0.021517 | -0.091207 | -0.065154 | 121.6354 | 121.7219 | 121.4632 | 121.6297 | 0.18594 | -0.34731 | -0.37372 | -0.36841 | -0.34371 | -0.27154 | -0.4656 | -0.089455 | 0.028837 | -0.040853 | -0.0148 | 121.6857 | 121.7723 | 121.5135 | 121.6801 | -121.7752 | -121.603 | -121.7266 | -121.5544
1444.8125 | 122.0535 | -121.7606 | 0 | 0.13101 | -0.42514 | -0.44697 | -0.43708 | -0.40322 | -0.33563 | -0.53885 | -0.13981 | -0.021517 | -0.095785 | -0.060575 | 121.6354 | 121.7265 | 121.4586 | 121.6206 | 0.18136 | -0.37479 | -0.39661 | -0.38673 | -0.35286 | -0.28528 | -0.48849 | -0.089455 | 0.028837 | -0.045431 | -0.010221 | 121.6857 | 121.7769 | 121.509 | 121.6709 | -121.7752 | -121.5984 | -121.7311 | -121.5544
1446.5156 | 121.9254 | -121.8018 | 0.027466 | 0.13559 | -0.42056 | -0.45154 | -0.44166 | -0.41695 | -0.34021 | -0.53427 | -0.13981 | -0.021517 | -0.095785 | -0.065154 | 121.6399 | 121.7219 | 121.4632 | 121.6252 | 0.18594 | -0.37021 | -0.40119 | -0.39131 | -0.3666 | -0.28985 | -0.48391 | -0.089455 | 0.028837 | -0.045431 | -0.0148 | 121.6903 | 121.7723 | 121.5135 | 121.6755 | -121.7797 | -121.603 | -121.7357 | -121.559
1448.2812 | 122.0398 | -121.7651 | 0.022888 | 0.12643 | -0.43888 | -0.47444 | -0.46913 | -0.42153 | -0.37683 | -0.56174 | -0.13523 | -0.021517 | -0.091207 | -0.065154 | 121.6399 | 121.7311 | 121.4815 | 121.6297 | 0.17678 | -0.38852 | -0.42408 | -0.41878 | -0.37118 | -0.32648 | -0.51138 | -0.084876 | 0.028837 | -0.040853 | -0.0148 | 121.6903 | 121.7815 | 121.5319 | 121.6801 | -121.7752 | -121.6167 | -121.7311 | -121.5727
1450.0312 | 122.0718 | -121.7697 | 0.009155 | 0.14017 | -0.46177 | -0.4836 | -0.47829 | -0.449 | -0.39057 | -0.58005 | -0.13981 | -0.021517 | -0.095785 | -0.069733 | 121.6537 | 121.7357 | 121.4815 | 121.6435 | 0.19052 | -0.41142 | -0.43324 | -0.42793 | -0.39864 | -0.34021 | -0.5297 | -0.089455 | 0.028837 | -0.045431 | -0.019379 | 121.704 | 121.786 | 121.5319 | 121.6938 | -121.7935 | -121.6213 | -121.7495 | -121.5773
1451.7812 | 121.9803 | -121.7972 | 0.013733 | 0.13101 | -0.47551 | -0.49275 | -0.4966 | -0.45815 | -0.39515 | -0.59836 | -0.14439 | -0.021517 | -0.10036 | -0.055996 | 121.6537 | 121.7403 | 121.4861 | 121.6389 | 0.18136 | -0.42515 | -0.4424 | -0.44625 | -0.4078 | -0.34479 | -0.54801 | -0.094033 | 0.028837 | -0.050009 | -0.005642 | 121.704 | 121.7906 | 121.5364 | 121.6892 | -121.7981 | -121.6305 | -121.754 | -121.5864
1453.4844 | 122.0306 | -121.7789 | 0.009155 | 0.13101 | -0.49382 | -0.51107 | -0.51034 | -0.47647 | -0.41346 | -0.60752 | -0.14897 | -0.016938 | -0.095785 | -0.074312 | 121.6537 | 121.7448 | 121.4907 | 121.6526 | 0.18136 | -0.44347 | -0.46071 | -0.45998 | -0.42611 | -0.36311 | -0.55717 | -0.098612 | 0.033416 | -0.045431 | -0.023958 | 121.704 | 121.7952 | 121.541 | 121.703 | -121.8026 | -121.6396 | -121.7495 | -121.5864
1455.2344 | 121.9528 | -121.8246 | 0.027466 | 0.13101 | -0.50298 | -0.5248 | -0.51949 | -0.48562 | -0.43178 | -0.61668 | -0.13981 | -0.016938 | -0.095785 | -0.074312 | 121.6583 | 121.7494 | 121.4907 | 121.6572 | 0.18136 | -0.45263 | -0.47445 | -0.46914 | -0.43527 | -0.38142 | -0.56632 | -0.089455 | 0.033416 | -0.045431 | -0.023958 | 121.7086 | 121.7998 | 121.541 | 121.7076 | -121.7981 | -121.6305 | -121.754 | -121.5864
1456.9844 | 122.0123 | -121.8155 | 0.032043 | 0.12643 | -0.51214 | -0.54312 | -0.53323 | -0.49936 | -0.44093 | -0.63499 | -0.14439 | -0.012359 | -0.10036 | -0.069733 | 121.6674 | 121.7494 | 121.4952 | 121.6572 | 0.17678 | -0.46179 | -0.49276 | -0.48288 | -0.449 | -0.39058 | -0.58464 | -0.094033 | 0.037995 | -0.050009 | -0.019379 | 121.7178 | 121.7998 | 121.5456 | 121.7076 | -121.8118 | -121.6396 | -121.7678 | -121.5956
1458.6719 | 121.9894 | -121.8338 | 0.027466 | 0.13559 | -0.53503 | -0.5477 | -0.55154 | -0.51309 | -0.45467 | -0.64414 | -0.13981 | -0.021517 | -0.10036 | -0.074312 | 121.6766 | 121.7586 | 121.4998 | 121.6664 | 0.18594 | -0.48468 | -0.49734 | -0.50119 | -0.46274 | -0.40431 | -0.59379 | -0.089455 | 0.028837 | -0.050009 | -0.023958 | 121.7269 | 121.8089 | 121.5502 | 121.7167 | -121.8164 | -121.6396 | -121.7769 | -121.6002
1460.4219 | 122.0352 | -121.8567 | 0.022888 | 0.12643 | -0.54877 | -0.57059 | -0.56528 | -0.52682 | -0.47298 | -0.65788 | -0.13981 | -0.016938 | -0.095785 | -0.069733 | 121.6766 | 121.7631 | 121.509 | 121.6709 | 0.17678 | -0.49841 | -0.52024 | -0.51492 | -0.47647 | -0.42263 | -0.60753 | -0.089455 | 0.033416 | -0.045431 | -0.019379 | 121.7269 | 121.8135 | 121.5593 | 121.7213 | -121.8164 | -121.6488 | -121.7723 | -121.6048
1462.1875 | 122.0535 | -121.8109 | -0.022888 | 0.13101 | -0.55335 | -0.57517 | -0.56986 | -0.54056 | -0.47756 | -0.67161 | -0.14439 | -0.021517 | -0.10036 | -0.069733 | 121.6766 | 121.7677 | 121.509 | 121.6709 | 0.18136 | -0.50299 | -0.52481 | -0.5195 | -0.4902 | -0.42721 | -0.62126 | -0.094033 | 0.028837 | -0.050009 | -0.019379 | 121.7269 | 121.8181 | 121.5593 | 121.7213 | -121.821 | -121.6534 | -121.7769 | -121.6093
1463.8906 | 121.9849 | -121.8567 | 0.036621 | 0.13101 | -0.57166 | -0.59348 | -0.58817 | -0.56803 | -0.49129 | -0.68993 | -0.14439 | -0.016938 | -0.095785 | -0.065154 | 121.6857 | 121.7723 | 121.509 | 121.6801 | 0.18136 | -0.52131 | -0.54313 | -0.53782 | -0.51767 | -0.44094 | -0.63957 | -0.094033 | 0.033416 | -0.045431 | -0.0148 | 121.7361 | 121.8227 | 121.5593 | 121.7304 | -121.8301 | -121.6534 | -121.7815 | -121.6048
1465.6406 | 122.0673 | -121.8063 | -0.013733 | 0.13101 | -0.59914 | -0.61638 | -0.61106 | -0.5726 | -0.51419 | -0.70824 | -0.14439 | -0.016938 | -0.095785 | -0.069733 | 121.6766 | 121.7723 | 121.5136 | 121.6847 | 0.18136 | -0.54878 | -0.56602 | -0.56071 | -0.52225 | -0.46383 | -0.65789 | -0.094033 | 0.033416 | -0.045431 | -0.019379 | 121.7269 | 121.8227 | 121.5639 | 121.735 | -121.821 | -121.6579 | -121.7723 | -121.6093
1467.3281 | 122.0718 | -121.8384 | 0 | 0.12643 | -0.62203 | -0.64385 | -0.63853 | -0.60465 | -0.54166 | -0.73571 | -0.13981 | -0.021517 | -0.086628 | -0.069733 | 121.6903 | 121.786 | 121.5181 | 121.6847 | 0.17678 | -0.57168 | -0.59349 | -0.58818 | -0.55429 | -0.4913 | -0.68535 | -0.089455 | 0.028837 | -0.036274 | -0.019379 | 121.7407 | 121.8364 | 121.5685 | 121.735 | -121.8301 | -121.6579 | -121.7769 | -121.6048
1469.0781 | 122.0673 | -121.843 | 0.018311 | 0.13101 | -0.66324 | -0.68505 | -0.67974 | -0.64127 | -0.58286 | -0.77233 | -0.13523 | -0.021517 | -0.091207 | -0.065154 | 121.6949 | 121.7723 | 121.5227 | 121.6893 | 0.18136 | -0.61289 | -0.6347 | -0.62939 | -0.59092 | -0.53251 | -0.72198 | -0.084876 | 0.028837 | -0.040853 | -0.0148 | 121.7452 | 121.8227 | 121.5731 | 121.7396 | -121.8301 | -121.6579 | -121.7861 | -121.6139
1470.7656 | 122.1268 | -121.8246 | 0.013733 | 0.13101 | -0.69529 | -0.72168 | -0.71179 | -0.6779 | -0.61949 | -0.80438 | -0.13065 | -0.021517 | -0.095785 | -0.065154 | 121.7086 | 121.7906 | 121.5319 | 121.6893 | 0.18136 | -0.64494 | -0.67133 | -0.66144 | -0.62754 | -0.56913 | -0.75403 | -0.080298 | 0.028837 | -0.045431 | -0.0148 | 121.759 | 121.841 | 121.5822 | 121.7396 | -121.8393 | -121.6625 | -121.8044 | -121.6277
1472.5312 | 122.0993 | -121.8063 | 0.009155 | 0.13101 | -0.72734 | -0.76747 | -0.753 | -0.7191 | -0.65154 | -0.84559 | -0.13981 | -0.016938 | -0.10036 | -0.065154 | 121.6995 | 121.7952 | 121.5273 | 121.6938 | 0.18136 | -0.67699 | -0.71711 | -0.70264 | -0.66874 | -0.60118 | -0.79523 | -0.089455 | 0.033416 | -0.050009 | -0.0148 | 121.7498 | 121.8455 | 121.5776 | 121.7442 | -121.8393 | -121.6671 | -121.7998 | -121.6277
1474.2188 | 121.994 | -121.8704 | 0.027466 | 0.13559 | -0.7594 | -0.79036 | -0.77131 | -0.75114 | -0.69274 | -0.88221 | -0.14439 | -0.021517 | -0.095785 | -0.065154 | 121.704 | 121.7998 | 121.5364 | 121.6984 | 0.18594 | -0.70904 | -0.74001 | -0.72096 | -0.70079 | -0.64239 | -0.83186 | -0.094033 | 0.028837 | -0.045431 | -0.0148 | 121.7544 | 121.8501 | 121.5868 | 121.7488 | -121.8484 | -121.6808 | -121.7998 | -121.6322
1475.9688 | 122.0627 | -121.8292 | 0.013733 | 0.13559 | -0.8006 | -0.82241 | -0.8171 | -0.78319 | -0.73395 | -0.91884 | -0.14439 | -0.021517 | -0.095785 | -0.065154 | 121.7132 | 121.7952 | 121.5364 | 121.7076 | 0.18594 | -0.75025 | -0.77206 | -0.76674 | -0.73284 | -0.68359 | -0.86848 | -0.094033 | 0.028837 | -0.045431 | -0.0148 | 121.7635 | 121.8455 | 121.5868 | 121.7579 | -121.8576 | -121.6808 | -121.809 | -121.6322
1477.7188 | 122.049 | -121.8658 | 0.022888 | 0.13559 | -0.84181 | -0.87735 | -0.8583 | -0.82897 | -0.77515 | -0.95546 | -0.13981 | -0.012359 | -0.095785 | -0.069733 | 121.7178 | 121.8044 | 121.5456 | 121.7076 | 0.18594 | -0.79146 | -0.827 | -0.80795 | -0.77861 | -0.7248 | -0.90511 | -0.089455 | 0.037995 | -0.045431 | -0.019379 | 121.7681 | 121.8547 | 121.596 | 121.7579 | -121.8576 | -121.6854 | -121.8136 | -121.6414
1479.4219 | 122.1634 | -121.8475 | -0.004578 | 0.13101 | -0.86929 | -0.90483 | -0.88577 | -0.85644 | -0.79805 | -0.98751 | -0.13981 | -0.016938 | -0.095785 | -0.060575 | 121.7269 | 121.8044 | 121.5502 | 121.7076 | 0.18136 | -0.81893 | -0.85447 | -0.83542 | -0.80608 | -0.74769 | -0.93715 | -0.089455 | 0.033416 | -0.045431 | -0.010221 | 121.7773 | 121.8547 | 121.6005 | 121.7579 | -121.8667 | -121.69 | -121.8227 | -121.646
1481.1875 | 122.049 | -121.8613 | 0.009155 | 0.13101 | -0.92881 | -0.95519 | -0.90867 | -0.92053 | -0.85757 | -1.0516 | -0.14439 | -0.016938 | -0.10036 | -0.065154 | 121.7269 | 121.8089 | 121.5639 | 121.7213 | 0.18136 | -0.87846 | -0.90484 | -0.85831 | -0.87018 | -0.80721 | -1.0012 | -0.094033 | 0.033416 | -0.050009 | -0.0148 | 121.7773 | 121.8593 | 121.6143 | 121.7717 | -121.8713 | -121.7083 | -121.8273 | -121.6643
1482.9375 | 122.0993 | -121.8796 | -0.004578 | 0.12643 | -0.99291 | -1.0193 | -0.97734 | -0.98004 | -0.92624 | -1.1065 | -0.13523 | -0.021517 | -0.095785 | -0.065154 | 121.7315 | 121.8135 | 121.5548 | 121.7121 | 0.17678 | -0.94256 | -0.96894 | -0.92699 | -0.92969 | -0.87589 | -1.0562 | -0.084876 | 0.028837 | -0.045431 | -0.0148 | 121.7819 | 121.8639 | 121.6051 | 121.7625 | -121.8667 | -121.69 | -121.8273 | -121.6505
1484.6406 | 122.1863 | -121.8613 | -0.013733 | 0.12643 | -1.0341 | -1.0605 | -1.0186 | -1.0167 | -0.95829 | -1.1523 | -0.14439 | -0.021517 | -0.10036 | -0.069733 | 121.7407 | 121.8272 | 121.5639 | 121.7213 | 0.17678 | -0.98377 | -1.0101 | -0.9682 | -0.96631 | -0.90794 | -1.102 | -0.094033 | 0.028837 | -0.050009 | -0.019379 | 121.791 | 121.8776 | 121.6143 | 121.7717 | -121.885 | -121.7083 | -121.841 | -121.6643
1486.4062 | 122.0856 | -121.9116 | 0.022888 | 0.13101 | -1.0845 | -1.0971 | -1.0643 | -1.0624 | -0.9995 | -1.1981 | -0.13981 | -0.016938 | -0.095785 | -0.069733 | 121.7361 | 121.8227 | 121.5593 | 121.7213 | 0.18136 | -1.0341 | -1.0468 | -1.014 | -1.0121 | -0.94914 | -1.1478 | -0.089455 | 0.033416 | -0.045431 | -0.019379 | 121.7864 | 121.873 | 121.6097 | 121.7717 | -121.8759 | -121.6991 | -121.8319 | -121.6551
1488.1562 | 122.1405 | -121.8475 | -0.009155 | 0.13101 | -1.1028 | -1.1292 | -1.0826 | -1.0808 | -1.027 | -1.2164 | -0.13523 | -0.030674 | -0.095785 | -0.060575 | 121.7407 | 121.8364 | 121.5685 | 121.7305 | 0.18136 | -1.0525 | -1.0788 | -1.0323 | -1.0304 | -0.97661 | -1.1661 | -0.084876 | 0.01968 | -0.045431 | -0.010221 | 121.791 | 121.8868 | 121.6189 | 121.7808 | -121.8759 | -121.7037 | -121.8364 | -121.6643
1489.9062 | 122.1451 | -121.8521 | 0.009155 | 0.13559 | -1.1532 | -1.1704 | -1.1422 | -1.1265 | -1.0682 | -1.2622 | -0.13981 | -0.021517 | -0.091207 | -0.069733 | 121.7498 | 121.8318 | 121.5593 | 121.735 | 0.18594 | -1.1028 | -1.12 | -1.0918 | -1.0762 | -1.0178 | -1.2118 | -0.089455 | 0.028837 | -0.040853 | -0.019379 | 121.8002 | 121.8822 | 121.6097 | 121.7854 | -121.8896 | -121.6991 | -121.841 | -121.6505
1491.5938 | 122.1634 | -121.8521 | -0.018311 | 0.13559 | -1.199 | -1.2208 | -1.1788 | -1.1861 | -1.1185 | -1.308 | -0.14439 | -0.026096 | -0.095785 | -0.069733 | 121.7544 | 121.841 | 121.5685 | 121.735 | 0.18594 | -1.1486 | -1.1704 | -1.1284 | -1.1357 | -1.0682 | -1.2576 | -0.094033 | 0.024258 | -0.045431 | -0.019379 | 121.8047 | 121.8913 | 121.6189 | 121.7854 | -121.8988 | -121.7129 | -121.8502 | -121.6643
1493.2812 | 122.1359 | -121.8704 | -0.009155 | 0.13559 | -1.2539 | -1.2757 | -1.2337 | -1.2364 | -1.1781 | -1.3767 | -0.14439 | -0.016938 | -0.095785 | -0.065154 | 121.7452 | 121.8456 | 121.5777 | 121.7396 | 0.18594 | -1.2036 | -1.2253 | -1.1834 | -1.1861 | -1.1277 | -1.3263 | -0.094033 | 0.033416 | -0.045431 | -0.0148 | 121.7956 | 121.8959 | 121.628 | 121.79 | -121.8896 | -121.722 | -121.841 | -121.6734
1495.0469 | 122.0398 | -121.9299 | 0.036621 | 0.12643 | -1.3317 | -1.349 | -1.3162 | -1.3188 | -1.2513 | -1.4499 | -0.14439 | -0.016938 | -0.10036 | -0.069733 | 121.759 | 121.841 | 121.5822 | 121.7396 | 0.17678 | -1.2814 | -1.2986 | -1.2658 | -1.2685 | -1.201 | -1.3996 | -0.094033 | 0.033416 | -0.050009 | -0.019379 | 121.8093 | 121.8913 | 121.6326 | 121.79 | -121.9034 | -121.7266 | -121.8593 | -121.6826
1496.7969 | 122.1863 | -121.8842 | 0 | 0.13101 | -1.3959 | -1.4222 | -1.3711 | -1.3783 | -1.3154 | -1.5048 | -0.13981 | -0.026096 | -0.10036 | -0.065154 | 121.7544 | 121.8456 | 121.5777 | 121.7533 | 0.18136 | -1.3455 | -1.3719 | -1.3207 | -1.328 | -1.2651 | -1.4545 | -0.089455 | 0.024258 | -0.050009 | -0.0148 | 121.8047 | 121.8959 | 121.628 | 121.8037 | -121.8942 | -121.7175 | -121.8548 | -121.678
1498.4844 | 122.1359 | -121.8933 | 0.004578 | 0.13559 | -1.4233 | -1.4543 | -1.4123 | -1.4058 | -1.352 | -1.514 | -0.14439 | -0.016938 | -0.095785 | -0.060575 | 121.7635 | 121.841 | 121.5777 | 121.7533 | 0.18594 | -1.373 | -1.4039 | -1.3619 | -1.3554 | -1.3017 | -1.4636 | -0.094033 | 0.033416 | -0.045431 | -0.010221 | 121.8139 | 121.8913 | 121.628 | 121.8037 | -121.9079 | -121.722 | -121.8593 | -121.6734
1500.25 | 122.1909 | -121.8933 | 0.009155 | 0.13101 | -1.4645 | -1.4863 | -1.4444 | -1.4378 | -1.3749 | -1.546 | -0.13065 | -0.021517 | -0.095785 | -0.069733 | 121.759 | 121.8501 | 121.5914 | 121.7625 | 0.18136 | -1.4142 | -1.436 | -1.394 | -1.3875 | -1.3246 | -1.4957 | -0.080298 | 0.028837 | -0.045431 | -0.019379 | 121.8093 | 121.9005 | 121.6417 | 121.8129 | -121.8896 | -121.722 | -121.8548 | -121.6872
1502 | 122.113 | -121.9254 | 0.022888 | 0.13101 | -1.5698 | -1.5962 | -1.5542 | -1.5477 | -1.4894 | -1.6605 | -0.13981 | -0.021517 | -0.091207 | -0.060575 | 121.7727 | 121.8547 | 121.5914 | 121.7533 | 0.18136 | -1.5195 | -1.5458 | -1.5039 | -1.4974 | -1.439 | -1.6101 | -0.089455 | 0.028837 | -0.040853 | -0.010221 | 121.8231 | 121.9051 | 121.6417 | 121.8037 | -121.9125 | -121.7312 | -121.8639 | -121.6826
1503.7031 | 122.0581 | -121.9254 | 0.036621 | 0.13101 | -1.6156 | -1.6374 | -1.5909 | -1.5889 | -1.5306 | -1.6971 | -0.13981 | -0.026096 | -0.10952 | -0.069733 | 121.7681 | 121.8639 | 121.596 | 121.7625 | 0.18136 | -1.5653 | -1.587 | -1.5405 | -1.5386 | -1.4802 | -1.6468 | -0.089455 | 0.024258 | -0.059166 | -0.019379 | 121.8185 | 121.9142 | 121.6463 | 121.8129 | -121.9079 | -121.7358 | -121.8776 | -121.7055
1505.4688 | 122.1497 | -121.9025 | 0 | 0.13101 | -1.6797 | -1.7061 | -1.655 | -1.6622 | -1.5993 | -1.7612 | -0.13981 | -0.026096 | -0.095785 | -0.069733 | 121.7819 | 121.8639 | 121.6051 | 121.7671 | 0.18136 | -1.6294 | -1.6557 | -1.6046 | -1.6118 | -1.5489 | -1.7109 | -0.089455 | 0.024258 | -0.045431 | -0.019379 | 121.8322 | 121.9142 | 121.6555 | 121.8174 | -121.9217 | -121.7449 | -121.8776 | -121.7009
1507.1719 | 122.2137 | -121.8979 | -0.009155 | 0.13101 | -1.7576 | -1.7931 | -1.742 | -1.74 | -1.6817 | -1.8436 | -0.13981 | -0.021517 | -0.091207 | -0.065154 | 121.7819 | 121.8639 | 121.6051 | 121.7762 | 0.18136 | -1.7072 | -1.7427 | -1.6916 | -1.6896 | -1.6313 | -1.7933 | -0.089455 | 0.028837 | -0.040853 | -0.0148 | 121.8322 | 121.9142 | 121.6555 | 121.8266 | -121.9217 | -121.7449 | -121.8731 | -121.6963
1508.9375 | 122.1588 | -121.9116 | 0.022888 | 0.11727 | -1.8125 | -1.8205 | -1.7923 | -1.7903 | -1.732 | -1.894 | -0.13065 | -0.016938 | -0.095785 | -0.069733 | 121.7819 | 121.873 | 121.6097 | 121.7762 | 0.16763 | -1.7622 | -1.7702 | -1.742 | -1.74 | -1.6817 | -1.8436 | -0.080298 | 0.033416 | -0.045431 | -0.019379 | 121.8322 | 121.9234 | 121.6601 | 121.8266 | -121.9125 | -121.7404 | -121.8776 | -121.7055
1510.625 | 122.2275 | -121.8933 | -0.009155 | 0.13101 | -1.8766 | -1.903 | -1.8701 | -1.859 | -1.8007 | -1.9718 | -0.13981 | -0.012359 | -0.095785 | -0.074312 | 121.7864 | 121.873 | 121.6051 | 121.7762 | 0.18136 | -1.8263 | -1.8526 | -1.8198 | -1.8087 | -1.7504 | -1.9215 | -0.089455 | 0.037995 | -0.045431 | -0.023958 | 121.8368 | 121.9234 | 121.6555 | 121.8266 | -121.9262 | -121.7449 | -121.8822 | -121.7009
1512.3906 | 122.1954 | -121.8933 | -0.004578 | 0.13101 | -1.9682 | -1.9854 | -1.9434 | -1.9323 | -1.8923 | -2.0451 | -0.13981 | -0.021517 | -0.10494 | -0.065154 | 121.791 | 121.8822 | 121.6189 | 121.7854 | 0.18136 | -1.9178 | -1.935 | -1.8931 | -1.8819 | -1.8419 | -1.9947 | -0.089455 | 0.028837 | -0.054588 | -0.0148 | 121.8414 | 121.9325 | 121.6692 | 121.8357 | -121.9308 | -121.7587 | -121.896 | -121.7238
1514.0781 | 122.2321 | -121.9254 | -0.018311 | 0.13101 | -2.0644 | -2.0861 | -2.0396 | -2.0421 | -1.9838 | -2.1458 | -0.13981 | -0.021517 | -0.091207 | -0.065154 | 121.7864 | 121.8822 | 121.6189 | 121.7854 | 0.18136 | -2.014 | -2.0358 | -1.9892 | -1.9918 | -1.9335 | -2.0954 | -0.089455 | 0.028837 | -0.040853 | -0.0148 | 121.8368 | 121.9325 | 121.6692 | 121.8357 | -121.9262 | -121.7587 | -121.8776 | -121.7101
1515.8281 | 122.1176 | -121.9437 | 0.027466 | 0.13559 | -2.1514 | -2.1777 | -2.1265 | -2.1291 | -2.08 | -2.2374 | -0.14897 | -0.012359 | -0.091207 | -0.069733 | 121.8002 | 121.8822 | 121.6234 | 121.79 | 0.18594 | -2.101 | -2.1273 | -2.0762 | -2.0788 | -2.0296 | -2.187 | -0.098612 | 0.037995 | -0.040853 | -0.019379 | 121.8505 | 121.9325 | 121.6738 | 121.8403 | -121.9491 | -121.7724 | -121.8914 | -121.7146
1517.5156 | 122.0856 | -121.9437 | 0.032043 | 0.13559 | -2.2063 | -2.2372 | -2.1815 | -2.1886 | -2.1304 | -2.2969 | -0.13523 | -0.021517 | -0.10036 | -0.065154 | 121.8048 | 121.8868 | 121.628 | 121.79 | 0.18594 | -2.1559 | -2.1868 | -2.1311 | -2.1383 | -2.08 | -2.2465 | -0.084876 | 0.028837 | -0.050009 | -0.0148 | 121.8551 | 121.9371 | 121.6784 | 121.8403 | -121.94 | -121.7632 | -121.9051 | -121.7284
1519.2812 | 122.1039 | -121.9757 | 0.045776 | 0.13101 | -2.3025 | -2.3379 | -2.2868 | -2.2939 | -2.2448 | -2.3976 | -0.13981 | -0.021517 | -0.10036 | -0.074312 | 121.8048 | 121.8868 | 121.6234 | 121.7945 | 0.18136 | -2.2521 | -2.2876 | -2.2364 | -2.2436 | -2.1945 | -2.3472 | -0.089455 | 0.028837 | -0.050009 | -0.023958 | 121.8551 | 121.9371 | 121.6738 | 121.8449 | -121.9446 | -121.7632 | -121.9051 | -121.7238
1521.0312 | 122.0947 | -121.9849 | 0.036621 | 0.13101 | -2.3986 | -2.4249 | -2.3738 | -2.3672 | -2.3135 | -2.4846 | -0.14439 | -0.026096 | -0.095785 | -0.078891 | 121.8048 | 121.8959 | 121.6326 | 121.7945 | 0.18136 | -2.3483 | -2.3746 | -2.3234 | -2.3168 | -2.2631 | -2.4342 | -0.094033 | 0.024258 | -0.045431 | -0.028537 | 121.8551 | 121.9463 | 121.6829 | 121.8449 | -121.9491 | -121.777 | -121.9005 | -121.7284
1522.7188 | 122.2366 | -121.9254 | -0.004578 | 0.13101 | -2.4307 | -2.457 | -2.4058 | -2.4084 | -2.3684 | -2.5166 | -0.13981 | -0.012359 | -0.091207 | -0.065154 | 121.8093 | 121.8959 | 121.6372 | 121.7945 | 0.18136 | -2.3803 | -2.4066 | -2.3555 | -2.358 | -2.3181 | -2.4663 | -0.089455 | 0.037995 | -0.040853 | -0.0148 | 121.8597 | 121.9463 | 121.6875 | 121.8449 | -121.9491 | -121.777 | -121.9005 | -121.7284
1524.4688 | 122.2366 | -121.9162 | 0.018311 | 0.13101 | -2.5451 | -2.5714 | -2.5157 | -2.5182 | -2.4692 | -2.6357 | -0.14897 | -0.016938 | -0.091207 | -0.069733 | 121.8231 | 121.9005 | 121.6463 | 121.8083 | 0.18136 | -2.4948 | -2.5211 | -2.4654 | -2.4679 | -2.4188 | -2.5853 | -0.098612 | 0.033416 | -0.040853 | -0.019379 | 121.8734 | 121.9508 | 121.6967 | 121.8586 | -121.972 | -121.7953 | -121.9143 | -121.7375
1526.2188 | 122.1359 | -121.9666 | 0.036621 | 0.12643 | -2.5314 | -2.5669 | -2.5111 | -2.5045 | -2.4646 | -2.6219 | -0.13981 | -0.016938 | -0.10036 | -0.074312 | 121.8185 | 121.9051 | 121.6326 | 121.8083 | 0.17678 | -2.481 | -2.5165 | -2.4608 | -2.4541 | -2.4142 | -2.5716 | -0.089455 | 0.033416 | -0.050009 | -0.023958 | 121.8688 | 121.9554 | 121.6829 | 121.8586 | -121.9583 | -121.7724 | -121.9189 | -121.733
1527.9062 | 122.1954 | -121.9757 | 0.013733 | 0.13101 | -2.6504 | -2.6813 | -2.6302 | -2.6281 | -2.5836 | -2.7455 | -0.13981 | -0.016938 | -0.091207 | -0.069733 | 121.8185 | 121.9096 | 121.6463 | 121.8083 | 0.18136 | -2.6001 | -2.631 | -2.5798 | -2.5778 | -2.5333 | -2.6952 | -0.089455 | 0.033416 | -0.040853 | -0.019379 | 121.8688 | 121.96 | 121.6967 | 121.8586 | -121.9583 | -121.7861 | -121.9097 | -121.7375
1529.6562 | 122.1954 | -121.9666 | 0.004578 | 0.12643 | -2.5955 | -2.6126 | -2.5798 | -2.5686 | -2.5333 | -2.6952 | -0.13981 | -0.021517 | -0.10036 | -0.065154 | 121.8276 | 121.9096 | 121.6509 | 121.8174 | 0.17678 | -2.5451 | -2.5623 | -2.5295 | -2.5182 | -2.4829 | -2.6448 | -0.089455 | 0.028837 | -0.050009 | -0.0148 | 121.878 | 121.96 | 121.7013 | 121.8678 | -121.9675 | -121.7907 | -121.928 | -121.7513
1531.4062 | 122.1634 | -121.9757 | 0.032043 | 0.13101 | -2.655 | -2.6767 | -2.6256 | -2.6327 | -2.5836 | -2.7364 | -0.13981 | -0.016938 | -0.095785 | -0.069733 | 121.8322 | 121.9142 | 121.6463 | 121.8174 | 0.18136 | -2.6047 | -2.6264 | -2.5752 | -2.5823 | -2.5333 | -2.686 | -0.089455 | 0.033416 | -0.045431 | -0.019379 | 121.8826 | 121.9646 | 121.6967 | 121.8678 | -121.972 | -121.7861 | -121.928 | -121.7421
1533.0938 | 122.1313 | -121.9803 | 0.045776 | 0.12185 | -2.7283 | -2.75 | -2.6989 | -2.7059 | -2.666 | -2.8142 | -0.14897 | -0.026096 | -0.095785 | -0.065154 | 121.8231 | 121.9234 | 121.6601 | 121.822 | 0.1722 | -2.6779 | -2.6997 | -2.6485 | -2.6556 | -2.6157 | -2.7638 | -0.098612 | 0.024258 | -0.045431 | -0.0148 | 121.8734 | 121.9737 | 121.7104 | 121.8724 | -121.972 | -121.809 | -121.9189 | -121.7559
1534.8438 | 122.2458 | -121.9437 | -0.018311 | 0.11727 | -2.8473 | -2.8736 | -2.8179 | -2.825 | -2.7805 | -2.9332 | -0.14439 | -0.021517 | -0.10494 | -0.065154 | 121.8368 | 121.9234 | 121.6646 | 121.822 | 0.16763 | -2.797 | -2.8233 | -2.7675 | -2.7746 | -2.7301 | -2.8829 | -0.094033 | 0.028837 | -0.054588 | -0.0148 | 121.8872 | 121.9737 | 121.715 | 121.8724 | -121.9812 | -121.809 | -121.9417 | -121.7696
1536.5938 | 122.2275 | -121.9528 | 0.009155 | 0.12643 | -2.971 | -2.9927 | -2.9461 | -2.9577 | -2.9087 | -3.0523 | -0.14897 | -0.021517 | -0.095785 | -0.074312 | 121.8368 | 121.9234 | 121.6738 | 121.8266 | 0.17678 | -2.9206 | -2.9423 | -2.8957 | -2.9074 | -2.8583 | -3.0019 | -0.098612 | 0.028837 | -0.045431 | -0.023958 | 121.8872 | 121.9737 | 121.7242 | 121.8769 | -121.9858 | -121.8228 | -121.9326 | -121.7696
1538.3594 | 122.2092 | -121.9666 | 0.009155 | 0.12643 | -3.0625 | -3.0751 | -3.0331 | -3.0355 | -2.9957 | -3.1576 | -0.13981 | -0.021517 | -0.095785 | -0.078891 | 121.8368 | 121.928 | 121.6646 | 121.8312 | 0.17678 | -3.0122 | -3.0247 | -2.9827 | -2.9852 | -2.9453 | -3.1072 | -0.089455 | 0.028837 | -0.045431 | -0.028537 | 121.8872 | 121.9783 | 121.715 | 121.8815 | -121.9766 | -121.8045 | -121.9326 | -121.7604
1540.0625 | 122.1451 | -122.0215 | 0.013733 | 0.13101 | -3.1312 | -3.1483 | -3.0926 | -3.1042 | -3.0598 | -3.2171 | -0.14439 | -0.016938 | -0.091207 | -0.069733 | 121.846 | 121.9325 | 121.6646 | 121.8358 | 0.18136 | -3.0809 | -3.098 | -3.0423 | -3.0539 | -3.0094 | -3.1667 | -0.094033 | 0.033416 | -0.040853 | -0.019379 | 121.8963 | 121.9829 | 121.715 | 121.8861 | -121.9903 | -121.809 | -121.9372 | -121.7558
1541.7969 | 122.2687 | -121.9574 | 0 | 0.13101 | -3.2136 | -3.2216 | -3.1704 | -3.1729 | -3.1376 | -3.2949 | -0.14439 | -0.016938 | -0.095785 | -0.074312 | 121.8414 | 121.9325 | 121.6692 | 121.8358 | 0.18136 | -3.1633 | -3.1712 | -3.1201 | -3.1225 | -3.0872 | -3.2446 | -0.094033 | 0.033416 | -0.045431 | -0.023958 | 121.8917 | 121.9829 | 121.7196 | 121.8861 | -121.9858 | -121.8136 | -121.9372 | -121.765
1543.5625 | 122.1542 | -122.0078 | 0.041199 | 0.13101 | -3.2274 | -3.2491 | -3.1888 | -3.1958 | -3.1559 | -3.3132 | -0.13981 | -0.021517 | -0.095785 | -0.069733 | 121.846 | 121.9417 | 121.6692 | 121.8449 | 0.18136 | -3.177 | -3.1987 | -3.1384 | -3.1454 | -3.1056 | -3.2629 | -0.089455 | 0.028837 | -0.045431 | -0.019379 | 121.8963 | 121.992 | 121.7196 | 121.8953 | -121.9858 | -121.809 | -121.9417 | -121.765
1545.25 | 122.1542 | -122.0123 | 0.013733 | 0.13101 | -3.3739 | -3.4002 | -3.3444 | -3.3468 | -3.3116 | -3.4643 | -0.13981 | -0.016938 | -0.10036 | -0.060575 | 121.8505 | 121.9371 | 121.6692 | 121.8403 | 0.18136 | -3.3235 | -3.3498 | -3.2941 | -3.2965 | -3.2612 | -3.4139 | -0.089455 | 0.033416 | -0.050009 | -0.010221 | 121.9009 | 121.9875 | 121.7196 | 121.8907 | -121.9903 | -121.809 | -121.9509 | -121.7696
1546.9844 | 122.2778 | -121.9757 | -0.004578 | 0.12643 | -3.4929 | -3.5192 | -3.4589 | -3.4705 | -3.4398 | -3.5833 | -0.13523 | -0.021517 | -0.095785 | -0.060575 | 121.8597 | 121.9463 | 121.6784 | 121.8495 | 0.17678 | -3.4426 | -3.4689 | -3.4085 | -3.4201 | -3.3894 | -3.533 | -0.084876 | 0.028837 | -0.045431 | -0.010221 | 121.91 | 121.9966 | 121.7287 | 121.8998 | -121.9949 | -121.8136 | -121.9555 | -121.7742
1548.6719 | 122.2366 | -121.9757 | 0.004578 | 0.12643 | -3.5891 | -3.6062 | -3.5505 | -3.5529 | -3.5176 | -3.6749 | -0.13523 | -0.021517 | -0.095785 | -0.074312 | 121.8551 | 121.9463 | 121.683 | 121.8495 | 0.17678 | -3.5387 | -3.5558 | -3.5001 | -3.5025 | -3.4673 | -3.6245 | -0.084876 | 0.028837 | -0.045431 | -0.023958 | 121.9055 | 121.9966 | 121.7333 | 121.8998 | -121.9903 | -121.8182 | -121.9509 | -121.7787
1550.3594 | 122.1588 | -122.0444 | 0.009155 | 0.13559 | -3.5296 | -3.5513 | -3.4955 | -3.5025 | -3.4718 | -3.6245 | -0.14897 | -0.026096 | -0.095785 | -0.065154 | 121.8597 | 121.9463 | 121.6784 | 121.8541 | 0.18594 | -3.4792 | -3.5009 | -3.4452 | -3.4521 | -3.4215 | -3.5742 | -0.098612 | 0.024258 | -0.045431 | -0.0148 | 121.91 | 121.9966 | 121.7287 | 121.9044 | -122.0087 | -121.8273 | -121.9555 | -121.7742
1552.1094 | 122.2824 | -121.9711 | -0.004578 | 0.13101 | -3.4655 | -3.478 | -3.4314 | -3.4338 | -3.4031 | -3.5559 | -0.14439 | -0.016938 | -0.10036 | -0.074312 | 121.8688 | 121.9554 | 121.6921 | 121.8541 | 0.18136 | -3.4151 | -3.4276 | -3.3811 | -3.3835 | -3.3528 | -3.5055 | -0.094033 | 0.033416 | -0.050009 | -0.023958 | 121.9192 | 122.0058 | 121.7425 | 121.9044 | -122.0132 | -121.8365 | -121.9692 | -121.7925
1553.7969 | 122.2687 | -121.9803 | 0.009155 | 0.13101 | -3.6028 | -3.6154 | -3.5642 | -3.562 | -3.5405 | -3.6841 | -0.14439 | -0.026096 | -0.10036 | -0.069733 | 121.8643 | 121.96 | 121.6921 | 121.8586 | 0.18136 | -3.5525 | -3.565 | -3.5138 | -3.5117 | -3.4901 | -3.6337 | -0.094033 | 0.024258 | -0.050009 | -0.019379 | 121.9146 | 122.0104 | 121.7425 | 121.909 | -122.0087 | -121.8365 | -121.9646 | -121.7925
1555.5469 | 122.1725 | -122.0215 | 0.018311 | 0.12643 | -3.7127 | -3.739 | -3.6832 | -3.6856 | -3.6595 | -3.8031 | -0.13981 | -0.021517 | -0.095785 | -0.065154 | 121.8734 | 121.96 | 121.6921 | 121.8632 | 0.17678 | -3.6624 | -3.6886 | -3.6329 | -3.6353 | -3.6092 | -3.7527 | -0.089455 | 0.028837 | -0.045431 | -0.0148 | 121.9238 | 122.0104 | 121.7425 | 121.9136 | -122.0132 | -121.8319 | -121.9692 | -121.7879
1557.2344 | 122.1634 | -122.0169 | 0.041199 | 0.13101 | -3.873 | -3.8901 | -3.8389 | -3.8458 | -3.8198 | -3.9633 | -0.14439 | -0.026096 | -0.095785 | -0.074312 | 121.8734 | 121.9646 | 121.6967 | 121.8632 | 0.18136 | -3.8226 | -3.8397 | -3.7885 | -3.7955 | -3.7694 | -3.913 | -0.094033 | 0.024258 | -0.045431 | -0.023958 | 121.9238 | 122.0149 | 121.747 | 121.9136 | -122.0178 | -121.8411 | -121.9692 | -121.7925
1559 | 122.1634 | -122.0398 | 0.027466 | 0.12185 | -3.9875 | -4.0091 | -3.9579 | -3.9603 | -3.9251 | -4.0778 | -0.13981 | -0.016938 | -0.10036 | -0.069733 | 121.8734 | 121.9646 | 121.7013 | 121.8678 | 0.1722 | -3.9371 | -3.9588 | -3.9076 | -3.9099 | -3.8747 | -4.0274 | -0.089455 | 0.033416 | -0.050009 | -0.019379 | 121.9238 | 122.0149 | 121.7516 | 121.9182 | -122.0132 | -121.8411 | -121.9738 | -121.8016
1560.7656 | 122.287 | -121.9986 | 0 | 0.13101 | -4.0561 | -4.0686 | -4.0129 | -4.0198 | -3.9983 | -4.1373 | -0.14439 | -0.021517 | -0.10036 | -0.074312 | 121.8826 | 121.96 | 121.7058 | 121.8724 | 0.18136 | -4.0058 | -4.0183 | -3.9625 | -3.9695 | -3.948 | -4.0869 | -0.094033 | 0.028837 | -0.050009 | -0.023958 | 121.9329 | 122.0104 | 121.7562 | 121.9227 | -122.027 | -121.8502 | -121.9829 | -121.8062
1562.4688 | 122.2229 | -122.0398 | 0.036621 | 0.12643 | -4.0332 | -4.0549 | -3.9946 | -4.0015 | -3.9754 | -4.1144 | -0.13523 | -0.012359 | -0.095785 | -0.069733 | 121.8872 | 121.9646 | 121.7104 | 121.8724 | 0.17678 | -3.9829 | -4.0046 | -3.9442 | -3.9511 | -3.9251 | -4.064 | -0.084876 | 0.037995 | -0.045431 | -0.019379 | 121.9375 | 122.0149 | 121.7608 | 121.9227 | -122.0224 | -121.8457 | -121.9829 | -121.8062
1564.2188 | 122.2641 | -122.0169 | -0.013733 | 0.12185 | -4.0974 | -4.1098 | -4.0541 | -4.061 | -4.035 | -4.1831 | -0.14439 | -0.026096 | -0.095785 | -0.069733 | 121.8872 | 121.9783 | 121.7104 | 121.877 | 0.1722 | -4.047 | -4.0595 | -4.0037 | -4.0107 | -3.9846 | -4.1327 | -0.094033 | 0.024258 | -0.045431 | -0.019379 | 121.9375 | 122.0287 | 121.7608 | 121.9273 | -122.0315 | -121.8548 | -121.9829 | -121.8062
1565.9062 | 122.1725 | -122.0673 | 0.036621 | 0.12643 | -4.0974 | -4.1098 | -4.0633 | -4.0656 | -4.0395 | -4.1877 | -0.14897 | -0.030674 | -0.10036 | -0.069733 | 121.8917 | 121.9692 | 121.7196 | 121.8815 | 0.17678 | -4.047 | -4.0595 | -4.0129 | -4.0152 | -3.9892 | -4.1373 | -0.098612 | 0.01968 | -0.050009 | -0.019379 | 121.9421 | 122.0195 | 121.7699 | 121.9319 | -122.0407 | -121.8685 | -121.9921 | -121.8199
1567.6562 | 122.2504 | -121.9894 | 0.027466 | 0.12185 | -4.0928 | -4.1144 | -4.0587 | -4.0656 | -4.035 | -4.1831 | -0.14897 | -0.021517 | -0.095785 | -0.069733 | 121.8963 | 121.9737 | 121.7104 | 121.8861 | 0.1722 | -4.0424 | -4.0641 | -4.0083 | -4.0152 | -3.9846 | -4.1327 | -0.098612 | 0.028837 | -0.045431 | -0.019379 | 121.9467 | 122.0241 | 121.7608 | 121.9365 | -122.0453 | -121.8594 | -121.9921 | -121.8062
1569.4219 | 122.2595 | -122.0352 | -0.004578 | 0.12643 | -3.9646 | -3.9816 | -3.9259 | -3.9374 | -3.9114 | -4.0595 | -0.15354 | -0.026096 | -0.10036 | -0.069733 | 121.8917 | 121.9829 | 121.715 | 121.8861 | 0.17678 | -3.9142 | -3.9313 | -3.8755 | -3.887 | -3.861 | -4.0091 | -0.10319 | 0.024258 | -0.050009 | -0.019379 | 121.9421 | 122.0332 | 121.7654 | 121.9365 | -122.0453 | -121.8685 | -121.9921 | -121.8154
1571.1719 | 122.3053 | -122.0261 | -0.004578 | 0.13559 | -3.8318 | -3.8534 | -3.7977 | -3.8001 | -3.7786 | -3.9221 | -0.14439 | -0.016938 | -0.10494 | -0.074312 | 121.8963 | 121.9875 | 121.7242 | 121.877 | 0.18594 | -3.7814 | -3.8031 | -3.7473 | -3.7497 | -3.7282 | -3.8718 | -0.094033 | 0.033416 | -0.054588 | -0.023958 | 121.9467 | 122.0378 | 121.7745 | 121.9273 | -122.0407 | -121.8685 | -122.0013 | -121.8291
1572.9219 | 122.319 | -122.0306 | 0.013733 | 0.11727 | -3.8913 | -3.913 | -3.8618 | -3.8642 | -3.8381 | -3.9816 | -0.13981 | -0.021517 | -0.095785 | -0.069733 | 121.9055 | 121.9966 | 121.7242 | 121.8907 | 0.16763 | -3.841 | -3.8626 | -3.8114 | -3.8138 | -3.7877 | -3.9313 | -0.089455 | 0.028837 | -0.045431 | -0.019379 | 121.9558 | 122.047 | 121.7745 | 121.941 | -122.0453 | -121.864 | -122.0013 | -121.8199
1574.6719 | 122.2275 | -122.0627 | 0.027466 | 0.12643 | -3.905 | -3.9267 | -3.8755 | -3.8779 | -3.8518 | -3.9954 | -0.14439 | -0.016938 | -0.095785 | -0.074312 | 121.9055 | 121.9966 | 121.7287 | 121.8998 | 0.17678 | -3.8547 | -3.8764 | -3.8252 | -3.8275 | -3.8015 | -3.945 | -0.094033 | 0.033416 | -0.045431 | -0.023958 | 121.9558 | 122.047 | 121.7791 | 121.9502 | -122.0499 | -121.8731 | -122.0013 | -121.8245
1576.3594 | 122.319 | -122.0123 | 0 | 0.12185 | -3.96 | -3.9954 | -3.9351 | -3.9374 | -3.9114 | -4.0549 | -0.13981 | -0.021517 | -0.095785 | -0.074312 | 121.9009 | 121.9966 | 121.7333 | 121.8907 | 0.1722 | -3.9096 | -3.945 | -3.8847 | -3.887 | -3.861 | -4.0045 | -0.089455 | 0.028837 | -0.045431 | -0.023958 | 121.9512 | 122.047 | 121.7837 | 121.941 | -122.0407 | -121.8731 | -121.9967 | -121.8291
1578.0938 | 122.1817 | -122.0673 | 0.032043 | 0.13101 | -3.9188 | -3.9404 | -3.8847 | -3.9008 | -3.861 | -3.9999 | -0.13981 | -0.026096 | -0.095785 | -0.074312 | 121.9055 | 121.9966 | 121.7333 | 121.8998 | 0.18136 | -3.8684 | -3.8901 | -3.8343 | -3.8504 | -3.8106 | -3.9496 | -0.089455 | 0.024258 | -0.045431 | -0.023958 | 121.9558 | 122.047 | 121.7837 | 121.9502 | -122.0453 | -121.8731 | -122.0013 | -121.8291
1579.8594 | 122.3236 | -122.0215 | 0.004578 | 0.12185 | -3.9279 | -3.9588 | -3.8984 | -3.9054 | -3.8747 | -4.0091 | -0.13981 | -0.021517 | -0.095785 | -0.069733 | 121.9146 | 122.0012 | 121.7333 | 121.9044 | 0.1722 | -3.8776 | -3.9084 | -3.8481 | -3.855 | -3.8244 | -3.9587 | -0.089455 | 0.028837 | -0.045431 | -0.019379 | 121.965 | 122.0516 | 121.7837 | 121.9548 | -122.0544 | -121.8731 | -122.0104 | -121.8291
1581.5469 | 122.3007 | -122.0444 | 0.009155 | 0.12185 | -4.0653 | -4.0824 | -4.0175 | -4.0335 | -3.9983 | -4.1419 | -0.13981 | -0.021517 | -0.10494 | -0.069733 | 121.9192 | 122.0104 | 121.7333 | 121.9136 | 0.1722 | -4.0149 | -4.032 | -3.9671 | -3.9832 | -3.948 | -4.0915 | -0.089455 | 0.028837 | -0.054588 | -0.019379 | 121.9696 | 122.0607 | 121.7837 | 121.9639 | -122.059 | -121.8731 | -122.0241 | -121.8383
1583.2969 | 122.3053 | -122.0352 | -0.004578 | 0.12643 | -4.1523 | -4.1785 | -4.1136 | -4.1251 | -4.0945 | -4.2334 | -0.13981 | -0.021517 | -0.10036 | -0.074312 | 121.9238 | 122.0012 | 121.7379 | 121.9136 | 0.17678 | -4.1019 | -4.1282 | -4.0633 | -4.0747 | -4.0441 | -4.1831 | -0.089455 | 0.028837 | -0.050009 | -0.023958 | 121.9741 | 122.0516 | 121.7883 | 121.9639 | -122.0636 | -121.8777 | -122.0241 | -121.8383
1585 | 122.2137 | -122.0993 | 0.027466 | 0.11727 | -4.2805 | -4.3067 | -4.2555 | -4.2579 | -4.2364 | -4.3708 | -0.14439 | -0.026096 | -0.10036 | -0.069733 | 121.9192 | 122.0012 | 121.7425 | 121.9182 | 0.16763 | -4.2302 | -4.2564 | -4.2052 | -4.2075 | -4.1861 | -4.3204 | -0.094033 | 0.024258 | -0.050009 | -0.019379 | 121.9696 | 122.0516 | 121.7928 | 121.9685 | -122.0636 | -121.8869 | -122.0196 | -121.8428
1586.7656 | 122.3007 | -122.049 | 0.004578 | 0.12185 | -4.3858 | -4.4166 | -4.3609 | -4.3632 | -4.3371 | -4.4715 | -0.13981 | -0.021517 | -0.10036 | -0.08347 | 121.9238 | 122.0195 | 121.7516 | 121.909 | 0.1722 | -4.3355 | -4.3663 | -4.3105 | -4.3128 | -4.2868 | -4.4211 | -0.089455 | 0.028837 | -0.050009 | -0.033116 | 121.9741 | 122.0699 | 121.802 | 121.9594 | -122.0636 | -121.8914 | -122.0241 | -121.852
1588.5156 | 122.2 | -122.0947 | 0.018311 | 0.12643 | -4.4911 | -4.5173 | -4.457 | -4.4684 | -4.4379 | -4.5768 | -0.14439 | -0.021517 | -0.10036 | -0.074312 | 121.9284 | 122.0104 | 121.7471 | 121.9136 | 0.17678 | -4.4408 | -4.467 | -4.4066 | -4.4181 | -4.3875 | -4.5264 | -0.094033 | 0.028837 | -0.050009 | -0.023958 | 121.9787 | 122.0607 | 121.7974 | 121.9639 | -122.0727 | -121.8914 | -122.0287 | -121.8474
1590.2656 | 122.2549 | -122.0581 | 0.018311 | 0.11727 | -4.5415 | -4.5769 | -4.5211 | -4.5188 | -4.4745 | -4.6272 | -0.14897 | -0.021517 | -0.10952 | -0.069733 | 121.9284 | 122.0195 | 121.7516 | 121.9182 | 0.16763 | -4.4911 | -4.5265 | -4.4707 | -4.4685 | -4.4241 | -4.5768 | -0.098612 | 0.028837 | -0.059166 | -0.019379 | 121.9787 | 122.0699 | 121.802 | 121.9685 | -122.0773 | -121.9006 | -122.0379 | -121.8612
1592.0156 | 122.3099 | -122.0581 | -0.009155 | 0.12643 | -4.6697 | -4.6913 | -4.6356 | -4.6424 | -4.5935 | -4.7462 | -0.14439 | -0.030674 | -0.10494 | -0.074312 | 121.9284 | 122.0104 | 121.7516 | 121.9227 | 0.17678 | -4.6194 | -4.641 | -4.5852 | -4.5921 | -4.5432 | -4.6958 | -0.094033 | 0.01968 | -0.054588 | -0.023958 | 121.9787 | 122.0607 | 121.802 | 121.9731 | -122.0727 | -121.896 | -122.0333 | -121.8566
1593.7188 | 122.2916 | -122.0581 | 0 | 0.11727 | -4.6102 | -4.6364 | -4.576 | -4.5829 | -4.5249 | -4.6867 | -0.14897 | -0.012359 | -0.10494 | -0.074312 | 121.9421 | 122.0287 | 121.7608 | 121.9319 | 0.16763 | -4.5598 | -4.586 | -4.5257 | -4.5325 | -4.4745 | -4.6363 | -0.098612 | 0.037995 | -0.054588 | -0.023958 | 121.9925 | 122.079 | 121.8111 | 121.9822 | -122.0911 | -121.9098 | -122.047 | -121.8657
1595.4844 | 122.3648 | -122.0581 | 0 | 0.12185 | -4.7018 | -4.728 | -4.6722 | -4.6745 | -4.6256 | -4.7782 | -0.14897 | -0.026096 | -0.095785 | -0.074312 | 121.9421 | 122.0241 | 121.7608 | 121.9365 | 0.1722 | -4.6514 | -4.6776 | -4.6218 | -4.6241 | -4.5752 | -4.7279 | -0.098612 | 0.024258 | -0.045431 | -0.023958 | 121.9925 | 122.0745 | 121.8111 | 121.9868 | -122.0911 | -121.9098 | -122.0379 | -121.8566
1597.2344 | 122.2275 | -122.081 | 0.032043 | 0.12185 | -4.7201 | -4.7463 | -4.6859 | -4.6928 | -4.6439 | -4.8011 | -0.13981 | -0.021517 | -0.095785 | -0.065154 | 121.9375 | 122.0333 | 121.7608 | 121.9365 | 0.1722 | -4.6697 | -4.6959 | -4.6356 | -4.6424 | -4.5935 | -4.7508 | -0.089455 | 0.028837 | -0.045431 | -0.0148 | 121.9879 | 122.0836 | 121.8111 | 121.9868 | -122.0773 | -121.9006 | -122.0333 | -121.8566
1599 | 122.3465 | -122.0398 | -0.013733 | 0.11269 | -4.7567 | -4.7875 | -4.7271 | -4.7385 | -4.6851 | -4.8286 | -0.13981 | -0.026096 | -0.10036 | -0.074312 | 121.9467 | 122.0333 | 121.7699 | 121.9319 | 0.16305 | -4.7063 | -4.7371 | -4.6768 | -4.6882 | -4.6347 | -4.7782 | -0.089455 | 0.024258 | -0.050009 | -0.023958 | 121.997 | 122.0836 | 121.8203 | 121.9822 | -122.0865 | -121.9098 | -122.047 | -121.8703
1600.6875 | 122.3373 | -122.0535 | -0.009155 | 0.11727 | -4.8483 | -4.8699 | -4.8141 | -4.8255 | -4.7629 | -4.9247 | -0.14439 | -0.012359 | -0.10036 | -0.069733 | 121.9467 | 122.0378 | 121.7745 | 121.9365 | 0.16763 | -4.7979 | -4.8195 | -4.7638 | -4.7752 | -4.7126 | -4.8744 | -0.094033 | 0.037995 | -0.050009 | -0.019379 | 121.997 | 122.0882 | 121.8249 | 121.9868 | -122.0911 | -121.9189 | -122.047 | -121.8749
1602.4531 | 122.3511 | -122.0673 | 0.013733 | 0.11269 | -4.9353 | -4.966 | -4.9057 | -4.9125 | -4.8499 | -5.0209 | -0.14439 | -0.021517 | -0.10036 | -0.074312 | 121.9513 | 122.0378 | 121.7745 | 121.9411 | 0.16305 | -4.8849 | -4.9157 | -4.8553 | -4.8622 | -4.7996 | -4.9705 | -0.094033 | 0.028837 | -0.050009 | -0.023958 | 122.0016 | 122.0882 | 121.8249 | 121.9914 | -122.0956 | -121.9189 | -122.0516 | -121.8749
1604.2031 | 122.2412 | -122.1405 | 0.027466 | 0.11269 | -5.0223 | -5.0668 | -5.0018 | -5.0086 | -4.9506 | -5.1079 | -0.14897 | -0.021517 | -0.095785 | -0.074312 | 121.9558 | 122.0424 | 121.7745 | 121.9502 | 0.16305 | -4.9719 | -5.0164 | -4.9515 | -4.9583 | -4.9003 | -5.0575 | -0.098612 | 0.028837 | -0.045431 | -0.023958 | 122.0062 | 122.0928 | 121.8249 | 122.0006 | -122.1048 | -121.9235 | -122.0516 | -121.8703
1605.9531 | 122.2595 | -122.0901 | 0.027466 | 0.11727 | -5.1917 | -5.2224 | -5.1667 | -5.1689 | -5.12 | -5.2681 | -0.14439 | -0.021517 | -0.10036 | -0.069733 | 121.9558 | 122.0287 | 121.7745 | 121.9365 | 0.16763 | -5.1413 | -5.1721 | -5.1163 | -5.1185 | -5.0697 | -5.2177 | -0.094033 | 0.028837 | -0.050009 | -0.019379 | 122.0062 | 122.079 | 121.8249 | 121.9868 | -122.1002 | -121.9189 | -122.0562 | -121.8749
1607.7031 | 122.2595 | -122.1268 | 0.027466 | 0.10354 | -5.2192 | -5.2591 | -5.1941 | -5.1963 | -5.1475 | -5.3001 | -0.14439 | -0.026096 | -0.10036 | -0.074312 | 121.9604 | 122.0333 | 121.7837 | 121.9502 | 0.15389 | -5.1688 | -5.2087 | -5.1438 | -5.146 | -5.0972 | -5.2498 | -0.094033 | 0.024258 | -0.050009 | -0.023958 | 122.0108 | 122.0836 | 121.834 | 122.0006 | -122.1048 | -121.9281 | -122.0608 | -121.884
1609.4688 | 122.3145 | -122.113 | 0.009155 | 0.10812 | -5.3153 | -5.3461 | -5.2903 | -5.2879 | -5.2391 | -5.3917 | -0.14439 | -0.021517 | -0.10494 | -0.078891 | 121.9558 | 122.047 | 121.7883 | 121.9411 | 0.15847 | -5.265 | -5.2957 | -5.2399 | -5.2375 | -5.1887 | -5.3414 | -0.094033 | 0.028837 | -0.054588 | -0.028537 | 122.0062 | 122.0973 | 121.8386 | 121.9914 | -122.1002 | -121.9326 | -122.0608 | -121.8932
1611.1719 | 122.2916 | -122.0993 | 0.013733 | 0.10354 | -5.5122 | -5.5475 | -5.4826 | -5.4802 | -5.4451 | -5.6023 | -0.14439 | -0.030674 | -0.10036 | -0.074312 | 121.965 | 122.047 | 121.7837 | 121.9639 | 0.15389 | -5.4619 | -5.4972 | -5.4322 | -5.4298 | -5.3948 | -5.552 | -0.094033 | 0.01968 | -0.050009 | -0.023958 | 122.0153 | 122.0973 | 121.834 | 122.0143 | -122.1094 | -121.9281 | -122.0654 | -121.884
1612.9375 | 122.3511 | -122.0993 | 0.018311 | 0.089802 | -5.6908 | -5.7215 | -5.6611 | -5.6587 | -5.6054 | -5.7625 | -0.14897 | -0.021517 | -0.10036 | -0.069733 | 121.965 | 122.0516 | 121.7883 | 121.9548 | 0.14016 | -5.6404 | -5.6712 | -5.6108 | -5.6084 | -5.555 | -5.7122 | -0.098612 | 0.028837 | -0.050009 | -0.019379 | 122.0153 | 122.1019 | 121.8386 | 122.0051 | -122.114 | -121.9372 | -122.0654 | -121.8886
1614.6406 | 122.2961 | -122.1176 | 0.041199 | 0.085224 | -5.7503 | -5.7856 | -5.7252 | -5.7228 | -5.6786 | -5.8266 | -0.14897 | -0.026096 | -0.10036 | -0.074312 | 121.9558 | 122.0561 | 121.7974 | 121.9594 | 0.13558 | -5.7 | -5.7353 | -5.6749 | -5.6725 | -5.6283 | -5.7763 | -0.098612 | 0.024258 | -0.050009 | -0.023958 | 122.0062 | 122.1065 | 121.8478 | 122.0097 | -122.1048 | -121.9464 | -122.0562 | -121.8978
1616.4062 | 122.3419 | -122.0901 | -0.009155 | 0.080646 | -5.8236 | -5.8451 | -5.7893 | -5.8006 | -5.7427 | -5.8953 | -0.13981 | -0.021517 | -0.10494 | -0.069733 | 121.9741 | 122.0561 | 121.7883 | 121.9594 | 0.131 | -5.7732 | -5.7948 | -5.739 | -5.7503 | -5.6924 | -5.845 | -0.089455 | 0.028837 | -0.054588 | -0.019379 | 122.0245 | 122.1065 | 121.8386 | 122.0097 | -122.114 | -121.9281 | -122.0791 | -121.8932
1618.0938 | 122.3831 | -122.0673 | -0.022888 | 0.071489 | -5.9151 | -5.9504 | -5.8855 | -5.8968 | -5.8434 | -5.9869 | -0.14439 | -0.026096 | -0.10494 | -0.074312 | 121.9696 | 122.0607 | 121.7883 | 121.9548 | 0.12184 | -5.8648 | -5.9001 | -5.8351 | -5.8464 | -5.7931 | -5.9365 | -0.094033 | 0.024258 | -0.054588 | -0.023958 | 122.0199 | 122.1111 | 121.8386 | 122.0051 | -122.114 | -121.9326 | -122.0745 | -121.8932
1619.8438 | 122.3694 | -122.0901 | -0.013733 | 0.062332 | -5.8236 | -5.8497 | -5.7893 | -5.7961 | -5.7519 | -5.8999 | -0.14439 | -0.021517 | -0.091207 | -0.069733 | 121.9741 | 122.0607 | 121.7883 | 121.9685 | 0.11269 | -5.7732 | -5.7994 | -5.739 | -5.7457 | -5.7015 | -5.8495 | -0.094033 | 0.028837 | -0.040853 | -0.019379 | 122.0245 | 122.1111 | 121.8386 | 122.0189 | -122.1185 | -121.9326 | -122.0654 | -121.8795
1621.6094 | 122.3602 | -122.1039 | 0.009155 | 0.062332 | -5.851 | -5.8818 | -5.8305 | -5.8235 | -5.7839 | -5.9274 | -0.13981 | -0.021517 | -0.095785 | -0.08347 | 121.9787 | 122.0653 | 121.7974 | 121.9685 | 0.11269 | -5.8007 | -5.8314 | -5.7802 | -5.7732 | -5.7336 | -5.877 | -0.089455 | 0.028837 | -0.045431 | -0.033116 | 122.0291 | 122.1157 | 121.8478 | 122.0189 | -122.1185 | -121.9372 | -122.0745 | -121.8932
1623.3594 | 122.2778 | -122.1405 | 0.018311 | 0.053175 | -5.9289 | -5.9596 | -5.8992 | -5.8922 | -5.848 | -6.0052 | -0.14439 | -0.026096 | -0.10036 | -0.078891 | 121.9833 | 122.079 | 121.8066 | 121.9731 | 0.10353 | -5.8785 | -5.9093 | -5.8489 | -5.8418 | -5.7977 | -5.9548 | -0.094033 | 0.024258 | -0.050009 | -0.028537 | 122.0337 | 122.1294 | 121.8569 | 122.0235 | -122.1277 | -121.951 | -122.0837 | -121.9069
1625.0469 | 122.2778 | -122.113 | 0.045776 | 0.053175 | -5.9747 | -6.0008 | -5.9359 | -5.9334 | -5.8938 | -6.0418 | -0.13981 | -0.030674 | -0.10036 | -0.078891 | 121.9787 | 122.0745 | 121.7974 | 121.9731 | 0.10353 | -5.9243 | -5.9505 | -5.8855 | -5.883 | -5.8434 | -5.9915 | -0.089455 | 0.01968 | -0.050009 | -0.028537 | 122.0291 | 122.1248 | 121.8478 | 122.0235 | -122.1185 | -121.9372 | -122.0791 | -121.8978
1626.7969 | 122.3145 | -122.1313 | 0.022888 | 0.03944 | -6.0983 | -6.1244 | -6.0641 | -6.0616 | -6.0266 | -6.1654 | -0.13523 | -0.026096 | -0.10494 | -0.069733 | 121.9833 | 122.079 | 121.8066 | 121.9731 | 0.089794 | -6.0479 | -6.0741 | -6.0137 | -6.0112 | -5.9762 | -6.1151 | -0.084876 | 0.024258 | -0.054588 | -0.019379 | 122.0337 | 122.1294 | 121.8569 | 122.0235 | -122.1185 | -121.9418 | -122.0882 | -121.9115
1628.5469 | 122.3877 | -122.113 | -0.004578 | 0.034862 | -6.2173 | -6.2435 | -6.1831 | -6.1898 | -6.1319 | -6.2799 | -0.14439 | -0.021517 | -0.10494 | -0.069733 | 121.9879 | 122.079 | 121.802 | 121.9731 | 0.085216 | -6.167 | -6.1931 | -6.1327 | -6.1394 | -6.0815 | -6.2295 | -0.094033 | 0.028837 | -0.054588 | -0.019379 | 122.0382 | 122.1294 | 121.8523 | 122.0235 | -122.1323 | -121.9464 | -122.0928 | -121.9069
1630.3125 | 122.3236 | -122.1222 | 0.022888 | 0.030283 | -6.3822 | -6.4083 | -6.3433 | -6.3454 | -6.3058 | -6.4401 | -0.13981 | -0.026096 | -0.10036 | -0.074312 | 121.997 | 122.0653 | 121.8066 | 121.9868 | 0.080637 | -6.3318 | -6.358 | -6.293 | -6.2951 | -6.2555 | -6.3898 | -0.089455 | 0.024258 | -0.050009 | -0.023958 | 122.0474 | 122.1157 | 121.8569 | 122.0372 | -122.1368 | -121.9464 | -122.0974 | -121.9069
1632.0625 | 122.3648 | -122.1176 | 0 | 0.021127 | -6.4921 | -6.5274 | -6.467 | -6.4599 | -6.4249 | -6.5591 | -0.13981 | -0.016938 | -0.10494 | -0.069733 | 121.9925 | 122.079 | 121.8112 | 121.9914 | 0.071481 | -6.4417 | -6.477 | -6.4166 | -6.4095 | -6.3745 | -6.5088 | -0.089455 | 0.033416 | -0.054588 | -0.019379 | 122.0428 | 122.1294 | 121.8615 | 122.0418 | -122.1323 | -121.951 | -122.0974 | -121.9161
1633.75 | 122.2916 | -122.1497 | 0.013733 | 0.016548 | -6.5699 | -6.6006 | -6.5265 | -6.5285 | -6.489 | -6.637 | -0.14439 | -0.026096 | -0.091207 | -0.078891 | 121.9925 | 122.0745 | 121.8112 | 121.9823 | 0.066902 | -6.5196 | -6.5503 | -6.4761 | -6.4782 | -6.4386 | -6.5866 | -0.094033 | 0.024258 | -0.040853 | -0.028537 | 122.0428 | 122.1248 | 121.8615 | 122.0326 | -122.1368 | -121.9555 | -122.0837 | -121.9024
1635.5156 | 122.287 | -122.1359 | 0.027466 | 0.016548 | -6.5333 | -6.564 | -6.4944 | -6.4965 | -6.4524 | -6.6003 | -0.13981 | -0.021517 | -0.10494 | -0.074312 | 121.997 | 122.0882 | 121.8157 | 121.996 | 0.066902 | -6.4829 | -6.5136 | -6.4441 | -6.4461 | -6.402 | -6.55 | -0.089455 | 0.028837 | -0.054588 | -0.023958 | 122.0474 | 122.1385 | 121.8661 | 122.0463 | -122.1368 | -121.9555 | -122.102 | -121.9207
1637.2656 | 122.3282 | -122.1359 | 0.004578 | -0.088755 | -6.3822 | -6.4175 | -6.3433 | -6.3454 | -6.2967 | -6.4401 | -0.14439 | -0.026096 | -0.095785 | -0.078891 | 121.997 | 122.0882 | 121.8112 | 121.996 | -0.038401 | -6.3318 | -6.3671 | -6.293 | -6.2951 | -6.2463 | -6.3898 | -0.094033 | 0.024258 | -0.045431 | -0.028537 | 122.0474 | 122.1385 | 121.8615 | 122.0463 | -122.1414 | -121.9555 | -122.0928 | -121.9069
1639.0156 | 122.4106 | -122.1222 | -0.027466 | -0.21695 | -6.5241 | -6.5686 | -6.4944 | -6.4919 | -6.4524 | -6.5958 | -0.14439 | -0.016938 | -0.10036 | -0.069733 | 122.0016 | 122.0928 | 121.8203 | 121.996 | -0.1666 | -6.4738 | -6.5182 | -6.4441 | -6.4416 | -6.402 | -6.5454 | -0.094033 | 0.033416 | -0.050009 | -0.019379 | 122.052 | 122.1431 | 121.8707 | 122.0463 | -122.146 | -121.9647 | -122.102 | -121.9207
1640.7031 | 122.3877 | -122.1313 | 0.004578 | -0.21695 | -6.286 | -6.3213 | -6.2426 | -6.2538 | -6.2051 | -6.3577 | -0.13981 | -0.026096 | -0.10036 | -0.074312 | 122.0108 | 122.0928 | 121.8249 | 122.0051 | -0.1666 | -6.2357 | -6.271 | -6.1923 | -6.2035 | -6.1548 | -6.3074 | -0.089455 | 0.024258 | -0.050009 | -0.023958 | 122.0611 | 122.1431 | 121.8752 | 122.0555 | -122.1506 | -121.9647 | -122.1111 | -121.9253
1642.4531 | 122.3145 | -122.1588 | 0.009155 | -0.024657 | -6.5241 | -6.5548 | -6.4807 | -6.4736 | -6.4386 | -6.5958 | -0.15354 | -0.021517 | -0.10036 | -0.069733 | 122.0062 | 122.0973 | 121.8249 | 122.0051 | 0.025697 | -6.4738 | -6.5045 | -6.4303 | -6.4232 | -6.3883 | -6.5454 | -0.10319 | 0.028837 | -0.050009 | -0.019379 | 122.0565 | 122.1477 | 121.8752 | 122.0555 | -122.1597 | -121.9784 | -122.1066 | -121.9253
1644.2031 | 122.374 | -122.1405 | 0 | -0.042971 | -6.6798 | -6.7151 | -6.6318 | -6.6338 | -6.5897 | -6.7423 | -0.14439 | -0.026096 | -0.10036 | -0.074312 | 122.0108 | 122.1019 | 121.8249 | 122.0006 | 0.007383 | -6.6295 | -6.6647 | -6.5814 | -6.5835 | -6.5394 | -6.6919 | -0.094033 | 0.024258 | -0.050009 | -0.023958 | 122.0611 | 122.1523 | 121.8752 | 122.0509 | -122.1552 | -121.9693 | -122.1111 | -121.9253
1645.9062 | 122.374 | -122.1451 | 0 | -0.047549 | -6.895 | -6.9303 | -6.8516 | -6.8627 | -6.814 | -6.9529 | -0.14439 | -0.016938 | -0.095785 | -0.078891 | 122.0108 | 122.0973 | 121.8295 | 122.0097 | 0.002805 | -6.8447 | -6.8799 | -6.8012 | -6.8124 | -6.7637 | -6.9025 | -0.094033 | 0.033416 | -0.045431 | -0.028537 | 122.0611 | 122.1477 | 121.8798 | 122.0601 | -122.1552 | -121.9739 | -122.1066 | -121.9253
1647.6562 | 122.3236 | -122.1542 | 0.013733 | -0.061284 | -6.9729 | -7.0127 | -6.934 | -6.9268 | -6.901 | -7.0399 | -0.13981 | -0.026096 | -0.10494 | -0.069733 | 122.0153 | 122.0973 | 121.8295 | 122.0097 | -0.01093 | -6.9225 | -6.9623 | -6.8836 | -6.8765 | -6.8507 | -6.9895 | -0.089455 | 0.024258 | -0.054588 | -0.019379 | 122.0657 | 122.1477 | 121.8798 | 122.0601 | -122.1552 | -121.9693 | -122.1203 | -121.9344
1649.4219 | 122.3785 | -122.1176 | 0 | -0.07502 | -7.2018 | -7.2416 | -7.1583 | -7.1511 | -7.1254 | -7.2596 | -0.13981 | -0.021517 | -0.10036 | -0.069733 | 122.0199 | 122.0973 | 121.834 | 122.0097 | -0.024666 | -7.1514 | -7.1913 | -7.108 | -7.1008 | -7.075 | -7.2093 | -0.089455 | 0.028837 | -0.050009 | -0.019379 | 122.0703 | 122.1477 | 121.8844 | 122.0601 | -122.1597 | -121.9739 | -122.1203 | -121.9344
1651.1719 | 122.3145 | -122.1725 | 0.022888 | -0.093333 | -7.2796 | -7.3149 | -7.2316 | -7.229 | -7.1941 | -7.3512 | -0.14897 | -0.026096 | -0.091207 | -0.074312 | 122.0199 | 122.1111 | 121.834 | 122.0051 | -0.042979 | -7.2293 | -7.2645 | -7.1812 | -7.1786 | -7.1437 | -7.3008 | -0.098612 | 0.024258 | -0.040853 | -0.023958 | 122.0703 | 122.1614 | 121.8844 | 122.0555 | -122.1689 | -121.983 | -122.1111 | -121.9253
1652.9219 | 122.3099 | -122.1863 | 0.027466 | -0.11165 | -7.1606 | -7.2004 | -7.1079 | -7.1099 | -7.075 | -7.223 | -0.14439 | -0.021517 | -0.10036 | -0.074312 | 122.0153 | 122.1065 | 121.8432 | 122.0143 | -0.061293 | -7.1102 | -7.1501 | -7.0576 | -7.0596 | -7.0247 | -7.1726 | -0.094033 | 0.028837 | -0.050009 | -0.023958 | 122.0657 | 122.1569 | 121.8936 | 122.0647 | -122.1597 | -121.9876 | -122.1157 | -121.9436
1654.6094 | 122.4014 | -122.1359 | -0.013733 | -0.1208 | -7.3071 | -7.3423 | -7.2682 | -7.2656 | -7.2261 | -7.3649 | -0.15354 | -0.035253 | -0.10494 | -0.069733 | 122.0245 | 122.1065 | 121.834 | 122.0143 | -0.07045 | -7.2568 | -7.292 | -7.2178 | -7.2152 | -7.1757 | -7.3146 | -0.10319 | 0.015101 | -0.054588 | -0.019379 | 122.0749 | 122.1569 | 121.8844 | 122.0647 | -122.178 | -121.9876 | -122.1294 | -121.939
1656.375 | 122.3923 | -122.1588 | 0.004578 | -0.12996 | -7.3208 | -7.3607 | -7.2774 | -7.2747 | -7.2398 | -7.3786 | -0.14897 | -0.021517 | -0.095785 | -0.069733 | 122.0199 | 122.1111 | 121.8432 | 122.0189 | -0.079606 | -7.2705 | -7.3103 | -7.227 | -7.2244 | -7.1895 | -7.3283 | -0.098612 | 0.028837 | -0.045431 | -0.019379 | 122.0703 | 122.1614 | 121.8936 | 122.0692 | -122.1689 | -121.9922 | -122.1157 | -121.939
1658.0625 | 122.3831 | -122.1451 | -0.009155 | -0.14369 | -7.5956 | -7.64 | -7.5612 | -7.5631 | -7.5237 | -7.6671 | -0.14439 | -0.026096 | -0.10494 | -0.074312 | 122.0199 | 122.1111 | 121.8386 | 122.0189 | -0.093341 | -7.5452 | -7.5896 | -7.5109 | -7.5128 | -7.4733 | -7.6167 | -0.094033 | 0.024258 | -0.054588 | -0.023958 | 122.0703 | 122.1614 | 121.889 | 122.0692 | -122.1643 | -121.983 | -122.1249 | -121.9436
1659.7969 | 122.3877 | -122.1588 | 0 | -0.17574 | -7.5223 | -7.5438 | -7.4742 | -7.4807 | -7.4413 | -7.5801 | -0.14439 | -0.016938 | -0.10036 | -0.065154 | 122.0291 | 122.1157 | 121.8478 | 122.0189 | -0.12539 | -7.472 | -7.4934 | -7.4239 | -7.4304 | -7.3909 | -7.5297 | -0.094033 | 0.033416 | -0.050009 | -0.0148 | 122.0794 | 122.166 | 121.8981 | 122.0692 | -122.1735 | -121.9922 | -122.1294 | -121.9481
1661.5469 | 122.3373 | -122.1863 | 0.009155 | -0.19864 | -7.3254 | -7.3561 | -7.2774 | -7.2839 | -7.249 | -7.3832 | -0.13981 | -0.021517 | -0.10036 | -0.069733 | 122.0337 | 122.1248 | 121.8524 | 122.028 | -0.14828 | -7.2751 | -7.3057 | -7.227 | -7.2335 | -7.1986 | -7.3329 | -0.089455 | 0.028837 | -0.050009 | -0.019379 | 122.084 | 122.1752 | 121.9027 | 122.0784 | -122.1735 | -121.9922 | -122.134 | -121.9527
1663.2969 | 122.438 | -122.1405 | 0 | -0.22611 | -7.3529 | -7.379 | -7.3048 | -7.3022 | -7.2673 | -7.4061 | -0.13981 | -0.026096 | -0.10494 | -0.069733 | 122.0382 | 122.1248 | 121.8524 | 122.0235 | -0.17575 | -7.3025 | -7.3286 | -7.2545 | -7.2518 | -7.217 | -7.3558 | -0.089455 | 0.024258 | -0.054588 | -0.019379 | 122.0886 | 122.1752 | 121.9027 | 122.0738 | -122.178 | -121.9922 | -122.1432 | -121.9573
1665.0469 | 122.319 | -122.2 | 0.022888 | -0.23984 | -7.3392 | -7.3607 | -7.2957 | -7.2976 | -7.2582 | -7.4015 | -0.14439 | -0.021517 | -0.095785 | -0.074312 | 122.0428 | 122.1202 | 121.8569 | 122.028 | -0.18949 | -7.2888 | -7.3103 | -7.2453 | -7.2473 | -7.2078 | -7.3512 | -0.094033 | 0.028837 | -0.045431 | -0.023958 | 122.0932 | 122.1706 | 121.9073 | 122.0784 | -122.1872 | -122.0013 | -122.1386 | -121.9527
1666.7344 | 122.374 | -122.1634 | 0.009155 | -0.26273 | -7.4994 | -7.5255 | -7.4513 | -7.4579 | -7.4276 | -7.5663 | -0.14439 | -0.021517 | -0.10036 | -0.074312 | 122.0382 | 122.1294 | 121.8524 | 122.0326 | -0.21238 | -7.4491 | -7.4751 | -7.401 | -7.4075 | -7.3772 | -7.516 | -0.094033 | 0.028837 | -0.050009 | -0.023958 | 122.0886 | 122.1797 | 121.9027 | 122.083 | -122.1826 | -121.9967 | -122.1386 | -121.9527
1668.4844 | 122.319 | -122.1909 | 0.032043 | -0.28105 | -7.6047 | -7.6216 | -7.5566 | -7.554 | -7.5237 | -7.6579 | -0.15354 | -0.021517 | -0.10494 | -0.088049 | 122.0428 | 122.1294 | 121.8524 | 122.028 | -0.23069 | -7.5544 | -7.5713 | -7.5063 | -7.5036 | -7.4733 | -7.6076 | -0.10319 | 0.028837 | -0.054588 | -0.037695 | 122.0932 | 122.1797 | 121.9027 | 122.0784 | -122.1964 | -122.0059 | -122.1478 | -121.9573
1670.2344 | 122.4518 | -122.1588 | -0.004578 | -0.3131 | -7.6551 | -7.6812 | -7.6116 | -7.6135 | -7.5741 | -7.7128 | -0.15354 | -0.016938 | -0.10036 | -0.078891 | 122.0428 | 122.1294 | 121.8615 | 122.0372 | -0.26274 | -7.6047 | -7.6308 | -7.5612 | -7.5632 | -7.5237 | -7.6625 | -0.10319 | 0.033416 | -0.050009 | -0.028537 | 122.0932 | 122.1797 | 121.9119 | 122.0875 | -122.1964 | -122.0151 | -122.1432 | -121.9619
1672 | 122.3419 | -122.2137 | 0.041199 | -0.33141 | -7.5315 | -7.5575 | -7.4834 | -7.4945 | -7.4504 | -7.5892 | -0.14439 | -0.026096 | -0.10036 | -0.078891 | 122.052 | 122.134 | 121.8615 | 122.0372 | -0.28105 | -7.4811 | -7.5072 | -7.433 | -7.4441 | -7.4001 | -7.5389 | -0.094033 | 0.024258 | -0.050009 | -0.028537 | 122.1023 | 122.1843 | 121.9119 | 122.0875 | -122.1964 | -122.0059 | -122.1523 | -121.9619
1673.7656 | 122.4564 | -122.1451 | -0.013733 | -0.36804 | -7.5223 | -7.5484 | -7.4971 | -7.4991 | -7.455 | -7.5892 | -0.14439 | -0.021517 | -0.091207 | -0.074312 | 122.0566 | 122.134 | 121.8661 | 122.0372 | -0.31768 | -7.472 | -7.498 | -7.4468 | -7.4487 | -7.4047 | -7.5389 | -0.094033 | 0.028837 | -0.040853 | -0.023958 | 122.1069 | 122.1843 | 121.9164 | 122.0875 | -122.2009 | -122.0105 | -122.1478 | -121.9573
1675.4531 | 122.4747 | -122.1451 | 0 | -0.38177 | -7.5086 | -7.5209 | -7.4559 | -7.467 | -7.423 | -7.5709 | -0.13981 | -0.016938 | -0.10036 | -0.069733 | 122.052 | 122.1431 | 121.8661 | 122.0418 | -0.33142 | -7.4582 | -7.4706 | -7.4056 | -7.4167 | -7.3726 | -7.5206 | -0.089455 | 0.033416 | -0.050009 | -0.019379 | 122.1023 | 122.1935 | 121.9164 | 122.0921 | -122.1918 | -122.0059 | -122.1523 | -121.9665
1677.2188 | 122.3785 | -122.2 | 0.027466 | -0.39551 | -7.6093 | -7.64 | -7.575 | -7.5769 | -7.5466 | -7.6808 | -0.13981 | -0.021517 | -0.10036 | -0.078891 | 122.0611 | 122.1385 | 121.8661 | 122.0463 | -0.34515 | -7.559 | -7.5896 | -7.5246 | -7.5265 | -7.4962 | -7.6304 | -0.089455 | 0.028837 | -0.050009 | -0.028537 | 122.1115 | 122.1889 | 121.9164 | 122.0967 | -122.2009 | -122.0059 | -122.1615 | -121.9665
1678.9688 | 122.4335 | -122.2046 | 0 | -0.39093 | -8.0397 | -8.0703 | -8.0008 | -8.0026 | -7.9632 | -8.0974 | -0.14897 | -0.021517 | -0.10036 | -0.074312 | 122.0428 | 122.1385 | 121.8707 | 122.0463 | -0.34057 | -7.9894 | -8.02 | -7.9504 | -7.9523 | -7.9129 | -8.0471 | -0.098612 | 0.028837 | -0.050009 | -0.023958 | 122.0932 | 122.1889 | 121.921 | 122.0967 | -122.1918 | -122.0196 | -122.1432 | -121.971
1680.6562 | 122.4747 | -122.1588 | -0.004578 | -0.41382 | -8.1176 | -8.1344 | -8.074 | -8.0805 | -8.0456 | -8.1752 | -0.13981 | -0.026096 | -0.095785 | -0.074312 | 122.052 | 122.1477 | 121.8661 | 122.0463 | -0.36347 | -8.0672 | -8.0841 | -8.0237 | -8.0301 | -7.9953 | -8.1249 | -0.089455 | 0.024258 | -0.045431 | -0.023958 | 122.1023 | 122.1981 | 121.9164 | 122.0967 | -122.1918 | -122.0059 | -122.1478 | -121.9619
1682.4062 | 122.4197 | -122.1909 | 0.004578 | -0.42756 | -8.2366 | -8.2489 | -8.1931 | -8.1903 | -8.1555 | -8.2943 | -0.14439 | -0.021517 | -0.10036 | -0.078891 | 122.0566 | 122.1523 | 121.8752 | 122.0509 | -0.3772 | -8.1862 | -8.1986 | -8.1427 | -8.14 | -8.1052 | -8.2439 | -0.094033 | 0.028837 | -0.050009 | -0.028537 | 122.1069 | 122.2026 | 121.9256 | 122.1013 | -122.2009 | -122.0196 | -122.1569 | -121.9756
1684.1562 | 122.4609 | -122.168 | -0.018311 | -0.4596 | -8.3373 | -8.3679 | -8.3075 | -8.3094 | -8.2746 | -8.395 | -0.14439 | -0.021517 | -0.091207 | -0.074312 | 122.0611 | 122.1477 | 121.8798 | 122.0509 | -0.40925 | -8.287 | -8.3176 | -8.2572 | -8.259 | -8.2242 | -8.3446 | -0.094033 | 0.028837 | -0.040853 | -0.023958 | 122.1115 | 122.1981 | 121.9302 | 122.1013 | -122.2055 | -122.0242 | -122.1523 | -121.971
1685.9219 | 122.3831 | -122.2 | 0.009155 | -0.49165 | -8.5251 | -8.5465 | -8.4907 | -8.497 | -8.4531 | -8.5873 | -0.13981 | -0.016938 | -0.10036 | -0.074312 | 122.0611 | 122.1477 | 121.8752 | 122.0555 | -0.4413 | -8.4747 | -8.4962 | -8.4403 | -8.4467 | -8.4028 | -8.5369 | -0.089455 | 0.033416 | -0.050009 | -0.023958 | 122.1115 | 122.1981 | 121.9256 | 122.1059 | -122.2009 | -122.0151 | -122.1615 | -121.9756
1687.6094 | 122.3282 | -122.2046 | 0.027466 | -0.50539 | -8.6166 | -8.6427 | -8.5685 | -8.5657 | -8.5401 | -8.6651 | -0.15354 | -0.026096 | -0.095785 | -0.069733 | 122.0703 | 122.1477 | 121.8752 | 122.0555 | -0.45503 | -8.5663 | -8.5923 | -8.5181 | -8.5154 | -8.4897 | -8.6148 | -0.10319 | 0.024258 | -0.045431 | -0.019379 | 122.1206 | 122.1981 | 121.9256 | 122.1059 | -122.2238 | -122.0288 | -122.1661 | -121.971
1689.375 | 122.4609 | -122.1863 | -0.027466 | -0.57406 | -8.635 | -8.6518 | -8.5868 | -8.5932 | -8.563 | -8.7017 | -0.14439 | -0.026096 | -0.10494 | -0.074312 | 122.0703 | 122.1569 | 121.8752 | 122.0647 | -0.52371 | -8.5846 | -8.6015 | -8.5364 | -8.5428 | -8.5126 | -8.6514 | -0.094033 | 0.024258 | -0.054588 | -0.023958 | 122.1206 | 122.2072 | 121.9256 | 122.115 | -122.2147 | -122.0196 | -122.1752 | -121.9802
1691.0781 | 122.493 | -122.168 | -0.013733 | -0.56949 | -9.0562 | -9.0776 | -9.0263 | -9.0235 | -8.9842 | -9.1229 | -0.14439 | -0.016938 | -0.10036 | -0.074312 | 122.0703 | 122.1569 | 121.8844 | 122.0601 | -0.51913 | -9.0059 | -9.0273 | -8.976 | -8.9732 | -8.9338 | -9.0726 | -0.094033 | 0.033416 | -0.050009 | -0.023958 | 122.1206 | 122.2072 | 121.9348 | 122.1104 | -122.2147 | -122.0288 | -122.1706 | -121.9848
1692.8281 | 122.3419 | -122.2183 | 0.018311 | -0.67021 | -9.2852 | -9.302 | -9.2369 | -9.2478 | -9.2131 | -9.3427 | -0.14897 | -0.026096 | -0.095785 | -0.078891 | 122.0749 | 122.166 | 121.8844 | 122.0647 | -0.61986 | -9.2348 | -9.2516 | -9.1866 | -9.1975 | -9.1628 | -9.2923 | -0.098612 | 0.024258 | -0.045431 | -0.028537 | 122.1252 | 122.2164 | 121.9348 | 122.115 | -122.2238 | -122.0334 | -122.1707 | -121.9802
1694.5781 | 122.3419 | -122.2092 | 0.032043 | -0.75262 | -9.2623 | -9.2928 | -9.2186 | -9.2295 | -9.1902 | -9.3244 | -0.14439 | -0.026096 | -0.095785 | -0.074312 | 122.0749 | 122.1614 | 121.889 | 122.0555 | -0.70227 | -9.2119 | -9.2425 | -9.1683 | -9.1792 | -9.1399 | -9.274 | -0.094033 | 0.024258 | -0.045431 | -0.023958 | 122.1252 | 122.2118 | 121.9393 | 122.1059 | -122.2193 | -122.0334 | -122.1707 | -121.9848
1696.2656 | 122.4655 | -122.1725 | -0.022888 | -0.82588 | -9.5324 | -9.5538 | -9.475 | -9.495 | -9.4604 | -9.5945 | -0.14897 | -0.016938 | -0.095785 | -0.074312 | 122.0749 | 122.166 | 121.8981 | 122.0692 | -0.77552 | -9.4821 | -9.5035 | -9.4247 | -9.4447 | -9.41 | -9.5441 | -0.098612 | 0.033416 | -0.045431 | -0.023958 | 122.1252 | 122.2164 | 121.9485 | 122.1196 | -122.2238 | -122.0471 | -122.1707 | -121.9939
1698 | 122.4335 | -122.1771 | 0.004578 | -0.78009 | -10.0132 | -10.0483 | -9.9649 | -9.9757 | -9.9502 | -10.0798 | -0.14439 | -0.026096 | -0.10036 | -0.074312 | 122.0749 | 122.1706 | 121.8844 | 122.0692 | -0.72974 | -9.9628 | -9.9979 | -9.9146 | -9.9254 | -9.8999 | -10.0294 | -0.094033 | 0.024258 | -0.050009 | -0.023958 | 122.1252 | 122.221 | 121.9348 | 122.1196 | -122.2193 | -122.0288 | -122.1752 | -121.9848
1699.6875 | 122.3511 | -122.2321 | 0.027466 | -0.91287 | -10.1643 | -10.204 | -10.116 | -10.1222 | -10.0968 | -10.2217 | -0.14439 | -0.021517 | -0.10036 | -0.08347 | 122.0794 | 122.1614 | 121.889 | 122.0784 | -0.86251 | -10.1139 | -10.1536 | -10.0657 | -10.0719 | -10.0464 | -10.1713 | -0.094033 | 0.028837 | -0.050009 | -0.033116 | 122.1298 | 122.2118 | 121.9393 | 122.1287 | -122.2238 | -122.0334 | -122.1798 | -121.9893
1701.4531 | 122.3877 | -122.2229 | 0.009155 | -1.1921 | -10.494 | -10.5107 | -10.4274 | -10.4381 | -10.4035 | -10.533 | -0.14897 | -0.021517 | -0.10494 | -0.069733 | 122.0794 | 122.166 | 121.8936 | 122.0784 | -1.1418 | -10.4436 | -10.4604 | -10.377 | -10.3878 | -10.3531 | -10.4826 | -0.098612 | 0.028837 | -0.054588 | -0.019379 | 122.1298 | 122.2164 | 121.9439 | 122.1287 | -122.2284 | -122.0425 | -122.1844 | -121.9985
1703.1406 | 122.4014 | -122.2137 | 0.022888 | -1.3341 | -10.5993 | -10.6298 | -10.551 | -10.5526 | -10.5271 | -10.6566 | -0.14439 | -0.021517 | -0.10036 | -0.069733 | 122.0886 | 122.1752 | 121.8936 | 122.0692 | -1.2837 | -10.5489 | -10.5794 | -10.5006 | -10.5022 | -10.4768 | -10.6063 | -0.094033 | 0.028837 | -0.050009 | -0.019379 | 122.139 | 122.2255 | 121.9439 | 122.1196 | -122.233 | -122.0379 | -122.189 | -121.9939
1704.8906 | 122.4701 | -122.2 | -0.009155 | -1.3295 | -10.8053 | -10.845 | -10.7662 | -10.7677 | -10.7286 | -10.8626 | -0.14439 | -0.026096 | -0.095785 | -0.074312 | 122.0932 | 122.1752 | 121.8936 | 122.0784 | -1.2791 | -10.755 | -10.7946 | -10.7158 | -10.7174 | -10.6782 | -10.8123 | -0.094033 | 0.024258 | -0.045431 | -0.023958 | 122.1435 | 122.2255 | 121.9439 | 122.1287 | -122.2376 | -122.0379 | -122.189 | -121.9893
1706.6562 | 122.4701 | -122.1954 | -0.004578 | -1.6958 | -10.9289 | -10.9549 | -10.8669 | -10.8684 | -10.8293 | -10.9679 | -0.14439 | -0.021517 | -0.095785 | -0.074312 | 122.084 | 122.1752 | 121.9027 | 122.083 | -1.6454 | -10.8786 | -10.9045 | -10.8165 | -10.8181 | -10.7789 | -10.9176 | -0.094033 | 0.028837 | -0.045431 | -0.023958 | 122.1344 | 122.2255 | 121.9531 | 122.1333 | -122.2284 | -122.0471 | -122.1798 | -121.9985
1708.4062 | 122.4106 | -122.2229 | 0.018311 | -2.0391 | -10.8465 | -10.8862 | -10.7982 | -10.7952 | -10.7652 | -10.8993 | -0.13981 | -0.026096 | -0.091207 | -0.074312 | 122.0886 | 122.1752 | 121.8981 | 122.0876 | -1.9888 | -10.7962 | -10.8358 | -10.7479 | -10.7448 | -10.7148 | -10.8489 | -0.089455 | 0.024258 | -0.040853 | -0.023958 | 122.139 | 122.2255 | 121.9485 | 122.1379 | -122.2284 | -122.0379 | -122.1798 | -121.9893
1710.0938 | 122.3831 | -122.2275 | 0.032043 | -2.1582 | -10.7778 | -10.8221 | -10.7295 | -10.7311 | -10.6965 | -10.8306 | -0.13981 | -0.021517 | -0.10036 | -0.074312 | 122.0932 | 122.1798 | 121.9027 | 122.0784 | -2.1078 | -10.7275 | -10.7717 | -10.6792 | -10.6807 | -10.6462 | -10.7802 | -0.089455 | 0.028837 | -0.050009 | -0.023958 | 122.1435 | 122.2301 | 121.9531 | 122.1287 | -122.233 | -122.0425 | -122.1935 | -122.0031
1711.8438 | 122.3602 | -122.2412 | 0.018311 | -2.2543 | -10.9564 | -10.9869 | -10.8989 | -10.9005 | -10.8797 | -11 | -0.14439 | -0.026096 | -0.10494 | -0.069733 | 122.0932 | 122.1798 | 121.8981 | 122.083 | -2.204 | -10.9061 | -10.9366 | -10.8486 | -10.8501 | -10.8293 | -10.9496 | -0.094033 | 0.024258 | -0.054588 | -0.019379 | 122.1435 | 122.2301 | 121.9485 | 122.1333 | -122.2376 | -122.0425 | -122.1981 | -122.0031
1713.5938 | 122.4838 | -122.2 | -0.022888 | -2.3276 | -10.9976 | -11.0464 | -10.9539 | -10.9463 | -10.9254 | -11.0503 | -0.14439 | -0.021517 | -0.091207 | -0.065154 | 122.0978 | 122.1798 | 121.9027 | 122.0876 | -2.2772 | -10.9473 | -10.9961 | -10.9035 | -10.8959 | -10.8751 | -11 | -0.094033 | 0.028837 | -0.040853 | -0.0148 | 122.1481 | 122.2301 | 121.9531 | 122.1379 | -122.2421 | -122.0471 | -122.189 | -121.9939
1715.3594 | 122.3877 | -122.2412 | 0.041199 | -2.3459 | -10.9335 | -10.964 | -10.8806 | -10.8822 | -10.8522 | -10.9725 | -0.13981 | -0.021517 | -0.091207 | -0.074312 | 122.1023 | 122.1798 | 121.9073 | 122.083 | -2.2955 | -10.8832 | -10.9137 | -10.8303 | -10.8318 | -10.8018 | -10.9222 | -0.089455 | 0.028837 | -0.040853 | -0.023958 | 122.1527 | 122.2301 | 121.9577 | 122.1333 | -122.2421 | -122.0471 | -122.1935 | -121.9985
1717.125 | 122.4838 | -122.2229 | 0 | -2.3093 | -10.8282 | -10.8587 | -10.7753 | -10.7723 | -10.7469 | -10.8718 | -0.14439 | -0.021517 | -0.10036 | -0.069733 | 122.1023 | 122.1889 | 121.9073 | 122.0921 | -2.2589 | -10.7779 | -10.8084 | -10.725 | -10.7219 | -10.6965 | -10.8214 | -0.094033 | 0.028837 | -0.050009 | -0.019379 | 122.1527 | 122.2393 | 121.9577 | 122.1425 | -122.2467 | -122.0517 | -122.2027 | -122.0077
1718.875 | 122.4152 | -122.2458 | 0.018311 | -2.6435 | -10.7687 | -10.8038 | -10.7158 | -10.7128 | -10.6828 | -10.8214 | -0.13981 | -0.021517 | -0.10036 | -0.078891 | 122.1023 | 122.1889 | 121.9073 | 122.0967 | -2.5931 | -10.7183 | -10.7534 | -10.6654 | -10.6624 | -10.6324 | -10.7711 | -0.089455 | 0.028837 | -0.050009 | -0.028537 | 122.1527 | 122.2393 | 121.9577 | 122.1471 | -122.2421 | -122.0471 | -122.2027 | -122.0077
1720.5781 | 122.3785 | -122.2366 | 0.022888 | -2.79 | -10.8374 | -10.8679 | -10.7799 | -10.7906 | -10.7515 | -10.8809 | -0.13981 | -0.016938 | -0.10036 | -0.069733 | 122.1023 | 122.1935 | 121.9165 | 122.0876 | -2.7397 | -10.787 | -10.8175 | -10.7295 | -10.7403 | -10.7011 | -10.8306 | -0.089455 | 0.033416 | -0.050009 | -0.019379 | 122.1527 | 122.2438 | 121.9668 | 122.1379 | -122.2421 | -122.0563 | -122.2027 | -122.0168
1722.3281 | 122.4106 | -122.2275 | 0.009155 | -2.7534 | -10.7733 | -10.8175 | -10.7204 | -10.7265 | -10.6919 | -10.826 | -0.13981 | -0.021517 | -0.10036 | -0.078891 | 122.1069 | 122.1935 | 121.921 | 122.0921 | -2.703 | -10.7229 | -10.7671 | -10.67 | -10.6762 | -10.6416 | -10.7756 | -0.089455 | 0.028837 | -0.050009 | -0.028537 | 122.1573 | 122.2438 | 121.9714 | 122.1425 | -122.2467 | -122.0608 | -122.2073 | -122.0214
1724.0781 | 122.4792 | -122.2275 | 0 | -2.9228 | -10.8099 | -10.8404 | -10.7616 | -10.7494 | -10.7331 | -10.8535 | -0.14897 | -0.026096 | -0.10036 | -0.074312 | 122.1069 | 122.1935 | 121.9302 | 122.0921 | -2.8724 | -10.7595 | -10.79 | -10.7112 | -10.6991 | -10.6828 | -10.8031 | -0.098612 | 0.024258 | -0.050009 | -0.023958 | 122.1573 | 122.2438 | 121.9805 | 122.1425 | -122.2559 | -122.0792 | -122.2073 | -122.0306
1725.7656 | 122.3877 | -122.2458 | 0.032043 | -2.996 | -10.8099 | -10.8404 | -10.757 | -10.754 | -10.7286 | -10.8535 | -0.14439 | -0.030674 | -0.10036 | -0.074312 | 122.1069 | 122.1981 | 121.9165 | 122.1013 | -2.9457 | -10.7595 | -10.79 | -10.7067 | -10.7036 | -10.6782 | -10.8031 | -0.094033 | 0.01968 | -0.050009 | -0.023958 | 122.1573 | 122.2484 | 121.9668 | 122.1516 | -122.2513 | -122.0608 | -122.2073 | -122.0168
1727.5469 | 122.5159 | -122.2137 | 0.004578 | -3.2021 | -10.9335 | -10.9732 | -10.8715 | -10.8684 | -10.8476 | -10.9771 | -0.13981 | -0.026096 | -0.10036 | -0.078891 | 122.1115 | 122.2026 | 121.921 | 122.1059 | -3.1517 | -10.8832 | -10.9228 | -10.8211 | -10.8181 | -10.7973 | -10.9267 | -0.089455 | 0.024258 | -0.050009 | -0.028537 | 122.1618 | 122.253 | 121.9714 | 122.1562 | -122.2513 | -122.0608 | -122.2119 | -122.0214
1729.3125 | 122.4838 | -122.2275 | -0.004578 | -5.2532 | -11.0114 | -11.0739 | -10.9814 | -10.9646 | -10.9529 | -11.0915 | -0.13981 | -0.021517 | -0.095785 | -0.074312 | 122.1161 | 122.2072 | 121.921 | 122.1059 | -5.2028 | -10.961 | -11.0235 | -10.931 | -10.9142 | -10.9026 | -11.0412 | -0.089455 | 0.028837 | -0.045431 | -0.023958 | 122.1664 | 122.2576 | 121.9714 | 122.1562 | -122.2559 | -122.0608 | -122.2119 | -122.0168
1731.0156 | 122.4792 | -122.2183 | -0.013733 | -8.2978 | -10.8786 | -10.9503 | -10.8532 | -10.841 | -10.8018 | -10.9359 | -0.13981 | -0.016938 | -0.095785 | -0.069733 | 122.1161 | 122.2026 | 121.9256 | 122.1013 | -8.2474 | -10.8282 | -10.8999 | -10.8028 | -10.7906 | -10.7515 | -10.8855 | -0.089455 | 0.033416 | -0.045431 | -0.019379 | 122.1664 | 122.253 | 121.976 | 122.1516 | -122.2559 | -122.0654 | -122.2119 | -122.0214
1732.7031 | 122.4838 | -122.2458 | 0.009155 | -7.9132 | -11.0709 | -11.138 | -11.05 | -11.0241 | -10.9987 | -11.1419 | -0.14897 | -0.026096 | -0.095785 | -0.069733 | 122.1206 | 122.2026 | 121.9256 | 122.1059 | -7.8629 | -11.0205 | -11.0877 | -10.9997 | -10.9737 | -10.9483 | -11.0915 | -0.098612 | 0.024258 | -0.045431 | -0.019379 | 122.171 | 122.253 | 121.976 | 122.1562 | -122.2696 | -122.0746 | -122.2164 | -122.0214
1734.4688 | 122.4106 | -122.2595 | 0.032043 | -9.7263 | -11.3181 | -11.3944 | -11.3064 | -11.2896 | -11.2459 | -11.3937 | -0.13981 | -0.026096 | -0.095785 | -0.069733 | 122.1298 | 122.2072 | 121.9256 | 122.115 | -9.6759 | -11.2678 | -11.3441 | -11.2561 | -11.2393 | -11.1956 | -11.3433 | -0.089455 | 0.024258 | -0.045431 | -0.019379 | 122.1802 | 122.2576 | 121.976 | 122.1654 | -122.2696 | -122.0654 | -122.2256 | -122.0214
1736.1562 | 122.4106 | -122.2687 | 0.027466 | -10.6053 | -11.4509 | -11.5272 | -11.4255 | -11.4041 | -11.3604 | -11.5082 | -0.13981 | -0.021517 | -0.10036 | -0.065154 | 122.1206 | 122.2026 | 121.9302 | 122.1104 | -10.555 | -11.4006 | -11.4768 | -11.3751 | -11.3537 | -11.31 | -11.4578 | -0.089455 | 0.028837 | -0.050009 | -0.0148 | 122.171 | 122.253 | 121.9805 | 122.1608 | -122.2605 | -122.07 | -122.221 | -122.0306
1737.9375 | 122.4838 | -122.2 | -0.009155 | -10.2299 | -11.7577 | -11.8202 | -11.7414 | -11.7062 | -11.6717 | -11.8149 | -0.14897 | -0.016938 | -0.091207 | -0.074312 | 122.1206 | 122.2072 | 121.9256 | 122.1059 | -10.1795 | -11.7074 | -11.7699 | -11.691 | -11.6558 | -11.6214 | -11.7645 | -0.098612 | 0.033416 | -0.040853 | -0.023958 | 122.171 | 122.2576 | 121.976 | 122.1562 | -122.2696 | -122.0746 | -122.2119 | -122.0168
1739.6875 | 122.3923 | -122.2961 | 0.036621 | -11.2417 | -11.8447 | -11.9301 | -11.833 | -11.8069 | -11.7679 | -11.911 | -0.13981 | -0.016938 | -0.095785 | -0.074312 | 122.1252 | 122.2164 | 121.9302 | 122.1196 | -11.1914 | -11.7944 | -11.8797 | -11.7826 | -11.7566 | -11.7175 | -11.8607 | -0.089455 | 0.033416 | -0.045431 | -0.023958 | 122.1756 | 122.2667 | 121.9805 | 122.17 | -122.265 | -122.07 | -122.221 | -122.026
1741.3906 | 122.525 | -122.2137 | -0.027466 | -11.6171 | -12.0416 | -12.127 | -12.0298 | -11.9992 | -11.9556 | -12.1079 | -0.13981 | -0.021517 | -0.10494 | -0.078891 | 122.1252 | 122.2118 | 121.9393 | 122.115 | -11.5668 | -11.9912 | -12.0766 | -11.9795 | -11.9488 | -11.9052 | -12.0575 | -0.089455 | 0.028837 | -0.054588 | -0.028537 | 122.1756 | 122.2622 | 121.9897 | 122.1654 | -122.265 | -122.0792 | -122.2302 | -122.0443
1743.1719 | 122.374 | -122.2733 | 0.013733 | -11.7911 | -12.2019 | -12.2827 | -12.1901 | -12.1594 | -12.1067 | -12.2544 | -0.13981 | -0.016938 | -0.095785 | -0.065154 | 122.1298 | 122.2118 | 121.9302 | 122.115 | -11.7408 | -12.1515 | -12.2323 | -12.1397 | -12.1091 | -12.0563 | -12.204 | -0.089455 | 0.033416 | -0.045431 | -0.0148 | 122.1802 | 122.2622 | 121.9805 | 122.1654 | -122.2696 | -122.07 | -122.2256 | -122.026
1744.875 | 122.4289 | -122.3145 | -0.013733 | -11.7224 | -12.0782 | -12.1636 | -12.0665 | -12.0267 | -11.9876 | -12.1354 | -0.13981 | -0.016938 | -0.10036 | -0.078891 | 122.1206 | 122.2072 | 122.0034 | 122.1059 | -11.6721 | -12.0279 | -12.1133 | -12.0161 | -11.9763 | -11.9373 | -12.085 | -0.089455 | 0.033416 | -0.050009 | -0.028537 | 122.171 | 122.2576 | 122.0538 | 122.1562 | -122.2605 | -122.1433 | -122.221 | -122.1038
1746.625 | 122.3877 | -122.3373 | 0.018311 | -11.9926 | -12.3346 | -12.4109 | -12.3183 | -12.2876 | -12.2349 | -12.3872 | -0.13981 | -0.026096 | -0.10036 | -0.074312 | 122.1298 | 122.2118 | 121.9393 | 122.115 | -11.9422 | -12.2843 | -12.3605 | -12.2679 | -12.2372 | -12.1845 | -12.3368 | -0.089455 | 0.024258 | -0.050009 | -0.023958 | 122.1802 | 122.2622 | 121.9897 | 122.1654 | -122.2696 | -122.0792 | -122.2302 | -122.0397
1748.375 | 122.3923 | -122.2778 | 0.027466 | -11.6995 | -12.0599 | -12.1453 | -12.0527 | -12.0175 | -11.9785 | -12.1262 | -0.14897 | -0.026096 | -0.10036 | -0.078891 | 122.1252 | 122.2072 | 121.9348 | 122.115 | -11.6492 | -12.0096 | -12.0949 | -12.0024 | -11.9671 | -11.9281 | -12.0758 | -0.098612 | 0.024258 | -0.050009 | -0.028537 | 122.1756 | 122.2576 | 121.9851 | 122.1654 | -122.2742 | -122.0837 | -122.2256 | -122.0351
1750.0625 | 122.5388 | -122.2275 | 0.009155 | -12.0383 | -12.2797 | -12.3605 | -12.2679 | -12.2327 | -12.1891 | -12.3414 | -0.14439 | -0.021517 | -0.10494 | -0.069733 | 122.1298 | 122.2164 | 121.9393 | 122.1242 | -11.988 | -12.2293 | -12.3101 | -12.2176 | -12.1823 | -12.1387 | -12.291 | -0.094033 | 0.028837 | -0.054588 | -0.019379 | 122.1802 | 122.2667 | 121.9897 | 122.1745 | -122.2742 | -122.0837 | -122.2347 | -122.0443
1751.8125 | 122.5204 | -122.2366 | -0.009155 | -11.9742 | -12.1881 | -12.2643 | -12.1672 | -12.1365 | -12.0884 | -12.2452 | -0.13981 | -0.021517 | -0.095785 | -0.074312 | 122.1344 | 122.2164 | 121.9348 | 122.1242 | -11.9239 | -12.1378 | -12.214 | -12.1168 | -12.0862 | -12.038 | -12.1949 | -0.089455 | 0.028837 | -0.045431 | -0.023958 | 122.1847 | 122.2667 | 121.9851 | 122.1745 | -122.2742 | -122.0746 | -122.2302 | -122.0306
1753.5625 | 122.3923 | -122.2549 | 0.022888 | -12.1162 | -12.3942 | -12.4658 | -12.3778 | -12.3517 | -12.3081 | -12.4467 | -0.14439 | -0.026096 | -0.10036 | -0.074312 | 122.139 | 122.2164 | 121.9348 | 122.1242 | -12.0658 | -12.3438 | -12.4154 | -12.3274 | -12.3013 | -12.2578 | -12.3963 | -0.094033 | 0.024258 | -0.050009 | -0.023958 | 122.1893 | 122.2667 | 121.9851 | 122.1745 | -122.2833 | -122.0792 | -122.2393 | -122.0351
1755.25 | 122.4014 | -122.2733 | 0.018311 | -12.1162 | -12.3621 | -12.4292 | -12.3412 | -12.3196 | -12.2715 | -12.4146 | -0.14439 | -0.021517 | -0.095785 | -0.074312 | 122.1344 | 122.2255 | 121.9485 | 122.1196 | -12.0658 | -12.3118 | -12.3788 | -12.2908 | -12.2693 | -12.2211 | -12.3643 | -0.094033 | 0.028837 | -0.045431 | -0.023958 | 122.1847 | 122.2759 | 121.9989 | 122.17 | -122.2788 | -122.0929 | -122.2302 | -122.0443
1757.0156 | 122.5021 | -122.2458 | -0.018311 | -12.4 | -12.614 | -12.6901 | -12.6067 | -12.5714 | -12.5233 | -12.671 | -0.13523 | -0.026096 | -0.10036 | -0.069733 | 122.1435 | 122.221 | 121.9485 | 122.1379 | -12.3497 | -12.5636 | -12.6398 | -12.5564 | -12.5211 | -12.4729 | -12.6207 | -0.084876 | 0.024258 | -0.050009 | -0.019379 | 122.1939 | 122.2713 | 121.9989 | 122.1883 | -122.2788 | -122.0837 | -122.2439 | -122.0489
1758.7188 | 122.4243 | -122.2641 | 0.022888 | -12.6152 | -12.8292 | -12.8962 | -12.8128 | -12.7866 | -12.7339 | -12.8816 | -0.13981 | -0.021517 | -0.10036 | -0.069733 | 122.1435 | 122.2301 | 121.9393 | 122.1288 | -12.5649 | -12.7788 | -12.8458 | -12.7624 | -12.7362 | -12.6835 | -12.8312 | -0.089455 | 0.028837 | -0.050009 | -0.019379 | 122.1939 | 122.2805 | 121.9897 | 122.1791 | -122.2833 | -122.0792 | -122.2439 | -122.0397
1760.5156 | 122.4564 | -122.2504 | 0.018311 | -12.7434 | -12.9528 | -13.0335 | -12.9364 | -12.9056 | -12.8667 | -13.0098 | -0.14439 | -0.016938 | -0.10036 | -0.069733 | 122.1435 | 122.2255 | 121.9439 | 122.1288 | -12.6931 | -12.9024 | -12.9832 | -12.886 | -12.8553 | -12.8163 | -12.9594 | -0.094033 | 0.033416 | -0.050009 | -0.019379 | 122.1939 | 122.2759 | 121.9943 | 122.1791 | -122.2879 | -122.0883 | -122.2439 | -122.0443
1762.2031 | 122.5433 | -122.2137 | -0.027466 | -12.6152 | -12.8383 | -12.9053 | -12.8128 | -12.7866 | -12.7568 | -12.8908 | -0.13523 | -0.021517 | -0.091207 | -0.074312 | 122.1435 | 122.221 | 121.9531 | 122.1425 | -12.5649 | -12.788 | -12.855 | -12.7624 | -12.7362 | -12.7064 | -12.8404 | -0.084876 | 0.028837 | -0.040853 | -0.023958 | 122.1939 | 122.2713 | 122.0034 | 122.1928 | -122.2788 | -122.0883 | -122.2347 | -122.0443
1763.9375 | 122.5067 | -122.2549 | 0.022888 | -12.6152 | -12.8841 | -12.9466 | -12.8631 | -12.8415 | -12.798 | -12.9411 | -0.13981 | -0.021517 | -0.095785 | -0.069733 | 122.1481 | 122.2301 | 121.9577 | 122.1379 | -12.5649 | -12.8337 | -12.8962 | -12.8128 | -12.7912 | -12.7476 | -12.8908 | -0.089455 | 0.028837 | -0.045431 | -0.019379 | 122.1985 | 122.2805 | 122.008 | 122.1883 | -122.2879 | -122.0975 | -122.2439 | -122.0534
1765.625 | 122.525 | -122.2504 | 0 | -12.9449 | -13.0169 | -13.0702 | -13.0051 | -13.0018 | -12.972 | -13.1105 | -0.13981 | -0.026096 | -0.10036 | -0.078891 | 122.1481 | 122.2393 | 121.9531 | 122.1379 | -12.8945 | -12.9665 | -13.0198 | -12.9547 | -12.9514 | -12.9216 | -13.0602 | -0.089455 | 0.024258 | -0.050009 | -0.028537 | 122.1985 | 122.2896 | 122.0034 | 122.1883 | -122.2879 | -122.0929 | -122.2485 | -122.0534
1767.3125 | 122.4655 | -122.2733 | 0.032043 | -12.8396 | -12.8841 | -12.9282 | -12.8723 | -12.869 | -12.8438 | -12.9686 | -0.14439 | -0.026096 | -0.095785 | -0.074312 | 122.1527 | 122.2438 | 121.9577 | 122.1379 | -12.7892 | -12.8337 | -12.8779 | -12.8219 | -12.8186 | -12.7934 | -12.9182 | -0.094033 | 0.024258 | -0.045431 | -0.023958 | 122.203 | 122.2942 | 122.008 | 122.1883 | -122.2971 | -122.102 | -122.2485 | -122.0534
1769 | 122.5571 | -122.2275 | 0.004578 | -12.835 | -12.8841 | -12.9328 | -12.8677 | -12.869 | -12.8529 | -12.9732 | -0.13981 | -0.030674 | -0.10036 | -0.074312 | 122.1527 | 122.2347 | 121.9622 | 122.1425 | -12.7846 | -12.8337 | -12.8825 | -12.8173 | -12.8186 | -12.8026 | -12.9228 | -0.089455 | 0.01968 | -0.050009 | -0.023958 | 122.203 | 122.285 | 122.0126 | 122.1928 | -122.2925 | -122.102 | -122.2531 | -122.0626
1770.6875 | 122.5388 | -122.2458 | -0.004578 | -13.0685 | -13.1222 | -13.1617 | -13.1058 | -13.1071 | -13.0819 | -13.1975 | -0.13981 | -0.021517 | -0.10036 | -0.078891 | 122.1527 | 122.2393 | 121.9622 | 122.1471 | -13.0181 | -13.0718 | -13.1114 | -13.0554 | -13.0567 | -13.0315 | -13.1471 | -0.089455 | 0.028837 | -0.050009 | -0.028537 | 122.203 | 122.2896 | 122.0126 | 122.1974 | -122.2925 | -122.102 | -122.2531 | -122.0626
1772.375 | 122.5067 | -122.2549 | -0.004578 | -13.3752 | -13.4244 | -13.4685 | -13.3942 | -13.4092 | -13.3886 | -13.518 | -0.14439 | -0.016938 | -0.10036 | -0.074312 | 122.1527 | 122.2438 | 121.9577 | 122.1516 | -13.3249 | -13.374 | -13.4182 | -13.3439 | -13.3588 | -13.3383 | -13.4676 | -0.094033 | 0.033416 | -0.050009 | -0.023958 | 122.203 | 122.2942 | 122.008 | 122.202 | -122.2971 | -122.102 | -122.2531 | -122.058
1774.0625 | 122.4609 | -122.2687 | 0 | -13.682 | -13.7358 | -13.7844 | -13.7056 | -13.7159 | -13.6999 | -13.8247 | -0.13981 | -0.021517 | -0.10494 | -0.069733 | 122.1527 | 122.2393 | 121.9668 | 122.1516 | -13.6316 | -13.6854 | -13.7341 | -13.6552 | -13.6656 | -13.6496 | -13.7744 | -0.089455 | 0.028837 | -0.054588 | -0.019379 | 122.203 | 122.2896 | 122.0172 | 122.202 | -122.2925 | -122.1066 | -122.2576 | -122.0718
1775.75 | 122.438 | -122.3099 | 0.036621 | -14.0483 | -14.0883 | -14.137 | -14.0673 | -14.0638 | -14.0479 | -14.1772 | -0.14439 | -0.016938 | -0.095785 | -0.08347 | 122.1527 | 122.2438 | 121.9668 | 122.1471 | -13.9979 | -14.038 | -14.0866 | -14.0169 | -14.0135 | -13.9975 | -14.1269 | -0.094033 | 0.033416 | -0.045431 | -0.033116 | 122.203 | 122.2942 | 122.0172 | 122.1974 | -122.2971 | -122.1112 | -122.2485 | -122.0626
1777.4375 | 122.4701 | -122.2961 | 0.013733 | -14.1032 | -14.1708 | -14.1965 | -14.1268 | -14.1325 | -14.1349 | -14.2505 | -0.14439 | -0.026096 | -0.10036 | -0.074312 | 122.1573 | 122.2484 | 121.9714 | 122.1425 | -14.0528 | -14.1204 | -14.1462 | -14.0764 | -14.0822 | -14.0845 | -14.2001 | -0.094033 | 0.024258 | -0.050009 | -0.023958 | 122.2076 | 122.2988 | 122.0217 | 122.1928 | -122.3017 | -122.1158 | -122.2576 | -122.0718
1779.1406 | 122.4884 | -122.2733 | 0.032043 | -13.7415 | -13.7999 | -13.8348 | -13.7697 | -13.78 | -13.764 | -13.8934 | -0.13523 | -0.026096 | -0.091207 | -0.078891 | 122.1619 | 122.2484 | 121.9668 | 122.1562 | -13.6912 | -13.7495 | -13.7844 | -13.7193 | -13.7297 | -13.7137 | -13.843 | -0.084876 | 0.024258 | -0.040853 | -0.028537 | 122.2122 | 122.2988 | 122.0172 | 122.2066 | -122.2971 | -122.102 | -122.2531 | -122.058
1780.8438 | 122.4655 | -122.3053 | 0.027466 | -14.0986 | -14.1524 | -14.1828 | -14.1085 | -14.1234 | -14.112 | -14.2413 | -0.14439 | -0.021517 | -0.10036 | -0.074312 | 122.1619 | 122.2438 | 121.9622 | 122.1562 | -14.0483 | -14.1021 | -14.1324 | -14.0581 | -14.073 | -14.0616 | -14.191 | -0.094033 | 0.028837 | -0.050009 | -0.023958 | 122.2122 | 122.2942 | 122.0126 | 122.2066 | -122.3062 | -122.1066 | -122.2622 | -122.0626
1782.5469 | 122.5479 | -122.2549 | -0.018311 | -14.0986 | -14.1616 | -14.2102 | -14.1268 | -14.1371 | -14.1212 | -14.2551 | -0.13523 | -0.021517 | -0.10036 | -0.074312 | 122.1619 | 122.253 | 121.9714 | 122.1608 | -14.0483 | -14.1112 | -14.1599 | -14.0764 | -14.0867 | -14.0708 | -14.2047 | -0.084876 | 0.028837 | -0.050009 | -0.023958 | 122.2122 | 122.3034 | 122.0217 | 122.2112 | -122.2971 | -122.1066 | -122.2622 | -122.0718
1784.2656 | 122.4792 | -122.3007 | 0.009155 | -14.181 | -14.2486 | -14.2789 | -14.2046 | -14.2058 | -14.2036 | -14.3329 | -0.13981 | -0.026096 | -0.10036 | -0.069733 | 122.1619 | 122.253 | 121.9668 | 122.1516 | -14.1307 | -14.1982 | -14.2286 | -14.1543 | -14.1554 | -14.1532 | -14.2825 | -0.089455 | 0.024258 | -0.050009 | -0.019379 | 122.2122 | 122.3034 | 122.0172 | 122.202 | -122.3017 | -122.1066 | -122.2622 | -122.0672
1785.9844 | 122.5296 | -122.2778 | 0 | -14.41 | -14.473 | -14.4987 | -14.4335 | -14.4347 | -14.4233 | -14.5572 | -0.13981 | -0.026096 | -0.095785 | -0.069733 | 122.1664 | 122.2576 | 121.9806 | 122.1654 | -14.3596 | -14.4226 | -14.4483 | -14.3832 | -14.3843 | -14.373 | -14.5069 | -0.089455 | 0.024258 | -0.045431 | -0.019379 | 122.2168 | 122.3079 | 122.0309 | 122.2157 | -122.3062 | -122.1204 | -122.2622 | -122.0763
1787.6719 | 122.4655 | -122.3053 | 0.009155 | -14.5107 | -14.5783 | -14.604 | -14.5297 | -14.54 | -14.5378 | -14.6671 | -0.13981 | -0.021517 | -0.095785 | -0.078891 | 122.1664 | 122.2576 | 121.9714 | 122.1562 | -14.4603 | -14.5279 | -14.5537 | -14.4793 | -14.4896 | -14.4874 | -14.6167 | -0.089455 | 0.028837 | -0.045431 | -0.028537 | 122.2168 | 122.3079 | 122.0217 | 122.2066 | -122.3062 | -122.1112 | -122.2622 | -122.0672
1789.4219 | 122.5204 | -122.3053 | 0.009155 | -14.5519 | -14.6012 | -14.6452 | -14.5663 | -14.5766 | -14.5653 | -14.6991 | -0.13981 | -0.021517 | -0.095785 | -0.065154 | 122.1664 | 122.2576 | 121.9806 | 122.1562 | -14.5015 | -14.5508 | -14.5949 | -14.516 | -14.5262 | -14.5149 | -14.6488 | -0.089455 | 0.028837 | -0.045431 | -0.0148 | 122.2168 | 122.3079 | 122.0309 | 122.2066 | -122.3062 | -122.1204 | -122.2622 | -122.0763
1791.1094 | 122.5708 | -122.2733 | -0.009155 | -14.648 | -14.7019 | -14.7276 | -14.6579 | -14.6681 | -14.6522 | -14.7907 | -0.14439 | -0.016938 | -0.095785 | -0.069733 | 122.1756 | 122.2622 | 121.9806 | 122.1608 | -14.5977 | -14.6515 | -14.6773 | -14.6075 | -14.6178 | -14.6019 | -14.7403 | -0.094033 | 0.033416 | -0.045431 | -0.019379 | 122.2259 | 122.3125 | 122.0309 | 122.2112 | -122.32 | -122.1249 | -122.2714 | -122.0763
1792.8438 | 122.5708 | -122.2687 | 0 | -14.5931 | -14.6469 | -14.6864 | -14.6121 | -14.6178 | -14.611 | -14.7403 | -0.14439 | -0.016938 | -0.095785 | -0.074312 | 122.1664 | 122.253 | 121.976 | 122.1654 | -14.5427 | -14.5966 | -14.6361 | -14.5617 | -14.5674 | -14.5607 | -14.69 | -0.094033 | 0.033416 | -0.045431 | -0.023958 | 122.2168 | 122.3034 | 122.0263 | 122.2157 | -122.3108 | -122.1204 | -122.2622 | -122.0718
1794.5469 | 122.5708 | -122.2778 | -0.018311 | -14.6984 | -14.766 | -14.7917 | -14.7311 | -14.7231 | -14.7163 | -14.8548 | -0.13523 | -0.016938 | -0.091207 | -0.074312 | 122.1802 | 122.2622 | 121.9851 | 122.17 | -14.648 | -14.7156 | -14.7414 | -14.6808 | -14.6727 | -14.666 | -14.8044 | -0.084876 | 0.033416 | -0.040853 | -0.023958 | 122.2305 | 122.3125 | 122.0355 | 122.2203 | -122.3154 | -122.1204 | -122.2714 | -122.0763
1796.2812 | 122.5388 | -122.2687 | 0.009155 | -14.7259 | -14.7935 | -14.8238 | -14.7632 | -14.7689 | -14.7438 | -14.8823 | -0.13981 | -0.021517 | -0.091207 | -0.069733 | 122.1756 | 122.2576 | 121.9806 | 122.1654 | -14.6755 | -14.7431 | -14.7734 | -14.7128 | -14.7185 | -14.6935 | -14.8319 | -0.089455 | 0.028837 | -0.040853 | -0.019379 | 122.2259 | 122.3079 | 122.0309 | 122.2157 | -122.3154 | -122.1204 | -122.2668 | -122.0718
1797.9844 | 122.5891 | -122.2733 | 0 | -14.9365 | -15.0041 | -15.0252 | -14.9646 | -14.9703 | -14.9544 | -15.0929 | -0.14439 | -0.016938 | -0.095785 | -0.074312 | 122.171 | 122.2622 | 121.9806 | 122.1745 | -14.8861 | -14.9537 | -14.9749 | -14.9143 | -14.9199 | -14.9041 | -15.0425 | -0.094033 | 0.033416 | -0.045431 | -0.023958 | 122.2214 | 122.3125 | 122.0309 | 122.2249 | -122.3154 | -122.1249 | -122.2668 | -122.0763
1799.6875 | 122.5433 | -122.3007 | 0.004578 | -15.2798 | -15.3475 | -15.3641 | -15.2989 | -15.3045 | -15.2841 | -15.4225 | -0.13523 | -0.012359 | -0.091207 | -0.074312 | 122.1802 | 122.2667 | 121.9897 | 122.17 | -15.2295 | -15.2972 | -15.3137 | -15.2485 | -15.2541 | -15.2337 | -15.3721 | -0.084876 | 0.037995 | -0.040853 | -0.023958 | 122.2305 | 122.3171 | 122.0401 | 122.2203 | -122.3154 | -122.1249 | -122.2714 | -122.0809
1801.375 | 122.4655 | -122.3511 | 0.032043 | -15.3668 | -15.4437 | -15.4739 | -15.4042 | -15.4052 | -15.3848 | -15.5232 | -0.13981 | -0.026096 | -0.10036 | -0.069733 | 122.1756 | 122.2622 | 121.976 | 122.17 | -15.3165 | -15.3933 | -15.4236 | -15.3538 | -15.3548 | -15.3344 | -15.4729 | -0.089455 | 0.024258 | -0.050009 | -0.019379 | 122.2259 | 122.3125 | 122.0263 | 122.2203 | -122.3154 | -122.1158 | -122.2759 | -122.0763
1803.0625 | 122.5571 | -122.3007 | 0.009155 | -15.4218 | -15.4894 | -15.5151 | -15.4454 | -15.4464 | -15.4397 | -15.5781 | -0.14439 | -0.026096 | -0.10494 | -0.065154 | 122.1847 | 122.2667 | 121.9897 | 122.17 | -15.3714 | -15.4391 | -15.4648 | -15.395 | -15.396 | -15.3894 | -15.5278 | -0.094033 | 0.024258 | -0.054588 | -0.0148 | 122.2351 | 122.3171 | 122.0401 | 122.2203 | -122.3291 | -122.1341 | -122.2897 | -122.0947
1804.7656 | 122.4792 | -122.3236 | 0.013733 | -15.4767 | -15.5444 | -15.5792 | -15.5049 | -15.5105 | -15.4992 | -15.6331 | -0.13523 | -0.021517 | -0.10036 | -0.069733 | 122.1802 | 122.2713 | 121.9806 | 122.1791 | -15.4264 | -15.494 | -15.5289 | -15.4546 | -15.4601 | -15.4489 | -15.5827 | -0.084876 | 0.028837 | -0.050009 | -0.019379 | 122.2305 | 122.3217 | 122.0309 | 122.2295 | -122.3154 | -122.1158 | -122.2805 | -122.0809
1806.4844 | 122.4518 | -122.3236 | 0.013733 | -15.2936 | -15.3658 | -15.3915 | -15.3126 | -15.3274 | -15.3115 | -15.4454 | -0.14439 | -0.021517 | -0.095785 | -0.074312 | 122.1893 | 122.2713 | 121.9851 | 122.1745 | -15.2432 | -15.3155 | -15.3412 | -15.2623 | -15.277 | -15.2612 | -15.395 | -0.094033 | 0.028837 | -0.045431 | -0.023958 | 122.2397 | 122.3217 | 122.0355 | 122.2249 | -122.3337 | -122.1295 | -122.2851 | -122.0809
1808.1719 | 122.5937 | -122.3007 | -0.004578 | -15.1104 | -15.1735 | -15.1946 | -15.1341 | -15.1397 | -15.1147 | -15.2623 | -0.13981 | -0.016938 | -0.10036 | -0.069733 | 122.1893 | 122.2713 | 121.9943 | 122.1791 | -15.0601 | -15.1232 | -15.1443 | -15.0837 | -15.0893 | -15.0643 | -15.2119 | -0.089455 | 0.033416 | -0.050009 | -0.019379 | 122.2397 | 122.3217 | 122.0446 | 122.2295 | -122.3291 | -122.1341 | -122.2897 | -122.0947
1809.875 | 122.493 | -122.3236 | 0.018311 | -14.8953 | -14.9583 | -14.984 | -14.9143 | -14.9108 | -14.9132 | -15.0379 | -0.13981 | -0.021517 | -0.10036 | -0.074312 | 122.1893 | 122.2805 | 121.9897 | 122.1837 | -14.8449 | -14.908 | -14.9337 | -14.8639 | -14.8604 | -14.8629 | -14.9876 | -0.089455 | 0.028837 | -0.050009 | -0.023958 | 122.2397 | 122.3308 | 122.0401 | 122.234 | -122.3291 | -122.1295 | -122.2897 | -122.0901
1811.5781 | 122.4609 | -122.3373 | 0.009155 | -14.9502 | -15.0224 | -15.0481 | -14.9784 | -14.984 | -14.9773 | -15.102 | -0.14439 | -0.016938 | -0.10036 | -0.078891 | 122.1893 | 122.2759 | 121.9897 | 122.1837 | -14.8998 | -14.9721 | -14.9978 | -14.928 | -14.9337 | -14.927 | -15.0517 | -0.094033 | 0.033416 | -0.050009 | -0.028537 | 122.2397 | 122.3262 | 122.0401 | 122.234 | -122.3337 | -122.1341 | -122.2897 | -122.0901
1813.2969 | 122.4609 | -122.3602 | 0.036621 | -15.115 | -15.1872 | -15.2175 | -15.1478 | -15.1534 | -15.1376 | -15.2806 | -0.14439 | -0.021517 | -0.10494 | -0.069733 | 122.1847 | 122.2713 | 121.9943 | 122.1837 | -15.0647 | -15.1369 | -15.1672 | -15.0974 | -15.103 | -15.0872 | -15.2302 | -0.094033 | 0.028837 | -0.054588 | -0.019379 | 122.2351 | 122.3217 | 122.0446 | 122.234 | -122.3291 | -122.1387 | -122.2897 | -122.0992
1815 | 122.5983 | -122.2824 | -0.004578 | -14.9502 | -15.0087 | -15.039 | -14.9646 | -14.9749 | -14.959 | -15.102 | -0.14439 | -0.016938 | -0.095785 | -0.074312 | 122.1939 | 122.285 | 121.9989 | 122.1929 | -14.8998 | -14.9583 | -14.9886 | -14.9143 | -14.9245 | -14.9086 | -15.0517 | -0.094033 | 0.033416 | -0.045431 | -0.023958 | 122.2443 | 122.3354 | 122.0492 | 122.2432 | -122.3383 | -122.1433 | -122.2897 | -122.0947
1816.7188 | 122.5845 | -122.3145 | 0.009155 | -14.822 | -14.9079 | -14.9199 | -14.8548 | -14.865 | -14.8491 | -14.9876 | -0.14897 | -0.026096 | -0.10036 | -0.069733 | 122.1939 | 122.2805 | 121.9989 | 122.1837 | -14.7717 | -14.8576 | -14.8696 | -14.8044 | -14.8146 | -14.7988 | -14.9372 | -0.098612 | 0.024258 | -0.050009 | -0.019379 | 122.2443 | 122.3308 | 122.0492 | 122.234 | -122.3429 | -122.1478 | -122.2943 | -122.0992
1818.4688 | 122.4747 | -122.3373 | 0.036621 | -14.9456 | -15.0224 | -15.0436 | -14.9692 | -14.984 | -14.9682 | -15.1112 | -0.14439 | -0.021517 | -0.095785 | -0.065154 | 122.1939 | 122.285 | 122.0034 | 122.1883 | -14.8953 | -14.9721 | -14.9932 | -14.9189 | -14.9337 | -14.9178 | -15.0608 | -0.094033 | 0.028837 | -0.045431 | -0.0148 | 122.2443 | 122.3354 | 122.0538 | 122.2386 | -122.3383 | -122.1478 | -122.2897 | -122.0992
1820.1719 | 122.4792 | -122.3282 | 0.032043 | -14.8678 | -14.9491 | -14.9749 | -14.9005 | -14.9153 | -14.8949 | -15.0379 | -0.14439 | -0.021517 | -0.095785 | -0.078891 | 122.1939 | 122.2805 | 122.0034 | 122.1929 | -14.8174 | -14.8988 | -14.9245 | -14.8502 | -14.865 | -14.8445 | -14.9876 | -0.094033 | 0.028837 | -0.045431 | -0.028537 | 122.2443 | 122.3308 | 122.0538 | 122.2432 | -122.3383 | -122.1478 | -122.2897 | -122.0992
1821.8594 | 122.525 | -122.319 | 0.013733 | -14.9365 | -15.0087 | -15.0344 | -14.9646 | -14.9657 | -14.9544 | -15.0883 | -0.14897 | -0.026096 | -0.10036 | -0.074312 | 122.1985 | 122.285 | 122.0126 | 122.1883 | -14.8861 | -14.9583 | -14.984 | -14.9143 | -14.9154 | -14.9041 | -15.0379 | -0.098612 | 0.024258 | -0.050009 | -0.023958 | 122.2488 | 122.3354 | 122.063 | 122.2386 | -122.3474 | -122.1616 | -122.2988 | -122.113
1823.6562 | 122.4792 | -122.3328 | 0.032043 | -14.9777 | -15.0545 | -15.071 | -14.9967 | -15.0069 | -14.9956 | -15.1295 | -0.13981 | -0.026096 | -0.10494 | -0.074312 | 122.2031 | 122.2896 | 122.0034 | 122.1929 | -14.9273 | -15.0041 | -15.0207 | -14.9463 | -14.9566 | -14.9453 | -15.0791 | -0.089455 | 0.024258 | -0.054588 | -0.023958 | 122.2534 | 122.34 | 122.0538 | 122.2432 | -122.3429 | -122.1433 | -122.308 | -122.1084
1825.375 | 122.5525 | -122.3145 | 0 | -15.3394 | -15.4116 | -15.4373 | -15.363 | -15.3686 | -15.3573 | -15.4957 | -0.14439 | -0.026096 | -0.095785 | -0.078891 | 122.1985 | 122.285 | 122.0034 | 122.1974 | -15.289 | -15.3613 | -15.387 | -15.3126 | -15.3182 | -15.307 | -15.4454 | -0.094033 | 0.024258 | -0.045431 | -0.028537 | 122.2488 | 122.3354 | 122.0538 | 122.2478 | -122.3429 | -122.1478 | -122.2943 | -122.0992
1827.0625 | 122.5159 | -122.3328 | 0.027466 | -15.3302 | -15.3979 | -15.4282 | -15.3492 | -15.364 | -15.3527 | -15.4866 | -0.13981 | -0.026096 | -0.10036 | -0.069733 | 122.2122 | 122.2896 | 122.008 | 122.1974 | -15.2799 | -15.3475 | -15.3778 | -15.2989 | -15.3136 | -15.3024 | -15.4362 | -0.089455 | 0.024258 | -0.050009 | -0.019379 | 122.2626 | 122.34 | 122.0584 | 122.2478 | -122.352 | -122.1478 | -122.3126 | -122.1084
1828.75 | 122.5159 | -122.3236 | 0.013733 | -15.3073 | -15.3841 | -15.419 | -15.3309 | -15.3503 | -15.3253 | -15.4683 | -0.14897 | -0.016938 | -0.091207 | -0.069733 | 122.2031 | 122.2942 | 122.0218 | 122.202 | -15.257 | -15.3338 | -15.3686 | -15.2806 | -15.2999 | -15.2749 | -15.4179 | -0.098612 | 0.033416 | -0.040853 | -0.019379 | 122.2534 | 122.3446 | 122.0721 | 122.2524 | -122.352 | -122.1707 | -122.2943 | -122.113
1830.4531 | 122.5113 | -122.3282 | 0.036621 | -15.3577 | -15.4299 | -15.451 | -15.3767 | -15.396 | -15.3711 | -15.5141 | -0.14439 | -0.021517 | -0.095785 | -0.074312 | 122.2076 | 122.2942 | 122.0172 | 122.1929 | -15.3073 | -15.3796 | -15.4007 | -15.3264 | -15.3457 | -15.3207 | -15.4637 | -0.094033 | 0.028837 | -0.045431 | -0.023958 | 122.258 | 122.3446 | 122.0675 | 122.2432 | -122.352 | -122.1616 | -122.3034 | -122.113
1832.1719 | 122.4609 | -122.3419 | 0.036621 | -15.5179 | -15.5856 | -15.6113 | -15.537 | -15.5563 | -15.5359 | -15.6697 | -0.14439 | -0.021517 | -0.10036 | -0.074312 | 122.2122 | 122.2896 | 122.0126 | 122.1929 | -15.4676 | -15.5353 | -15.5609 | -15.4866 | -15.5059 | -15.4855 | -15.6194 | -0.094033 | 0.028837 | -0.050009 | -0.023958 | 122.2626 | 122.34 | 122.063 | 122.2432 | -122.3566 | -122.157 | -122.3126 | -122.113
1833.9219 | 122.5662 | -122.319 | -0.009155 | -15.6782 | -15.755 | -15.767 | -15.7109 | -15.744 | -15.7373 | -15.8574 | -0.13981 | -0.021517 | -0.091207 | -0.069733 | 122.2122 | 122.2896 | 122.0126 | 122.1974 | -15.6278 | -15.7047 | -15.7166 | -15.6606 | -15.6936 | -15.687 | -15.8071 | -0.089455 | 0.028837 | -0.040853 | -0.019379 | 122.2626 | 122.34 | 122.063 | 122.2478 | -122.352 | -122.1524 | -122.3034 | -122.1038
1835.6094 | 122.525 | -122.3465 | 0.045776 | -15.7468 | -15.8145 | -15.8494 | -15.775 | -15.7897 | -15.7648 | -15.9169 | -0.13981 | -0.021517 | -0.095785 | -0.078891 | 122.2122 | 122.2896 | 122.0172 | 122.202 | -15.6965 | -15.7642 | -15.799 | -15.7247 | -15.7394 | -15.7144 | -15.8666 | -0.089455 | 0.028837 | -0.045431 | -0.028537 | 122.2626 | 122.34 | 122.0675 | 122.2524 | -122.352 | -122.157 | -122.308 | -122.113
1837.3125 | 122.4792 | -122.3419 | 0.022888 | -15.6599 | -15.7275 | -15.7487 | -15.6743 | -15.6844 | -15.6732 | -15.8025 | -0.14439 | -0.016938 | -0.095785 | -0.074312 | 122.2122 | 122.2942 | 122.0126 | 122.2157 | -15.6095 | -15.6772 | -15.6983 | -15.624 | -15.6341 | -15.6229 | -15.7521 | -0.094033 | 0.033416 | -0.045431 | -0.023958 | 122.2626 | 122.3446 | 122.063 | 122.2661 | -122.3566 | -122.157 | -122.308 | -122.1084
1839.0156 | 122.5754 | -122.3328 | -0.004578 | -15.9346 | -16.0114 | -16.0371 | -15.9536 | -15.9729 | -15.9525 | -16.0909 | -0.14439 | -0.026096 | -0.095785 | -0.074312 | 122.2168 | 122.3079 | 122.0218 | 122.2066 | -15.8842 | -15.9611 | -15.9868 | -15.9032 | -15.9225 | -15.9022 | -16.0405 | -0.094033 | 0.024258 | -0.045431 | -0.023958 | 122.2671 | 122.3583 | 122.0721 | 122.2569 | -122.3612 | -122.1661 | -122.3126 | -122.1175
1840.7031 | 122.5571 | -122.3328 | 0.022888 | -15.6553 | -15.7321 | -15.7532 | -15.6835 | -15.689 | -15.6732 | -15.8162 | -0.13981 | -0.016938 | -0.095785 | -0.069733 | 122.2076 | 122.2988 | 122.0126 | 122.2066 | -15.6049 | -15.6818 | -15.7029 | -15.6331 | -15.6387 | -15.6229 | -15.7659 | -0.089455 | 0.033416 | -0.045431 | -0.019379 | 122.258 | 122.3491 | 122.063 | 122.2569 | -122.3474 | -122.1524 | -122.3034 | -122.1084
1842.4219 | 122.6212 | -122.3099 | -0.018311 | -15.93 | -16.0069 | -16.0234 | -15.949 | -15.9637 | -15.9479 | -16.0863 | -0.13981 | -0.021517 | -0.095785 | -0.069733 | 122.2214 | 122.3034 | 122.0218 | 122.2066 | -15.8796 | -15.9565 | -15.973 | -15.8987 | -15.9133 | -15.8976 | -16.036 | -0.089455 | 0.028837 | -0.045431 | -0.019379 | 122.2717 | 122.3537 | 122.0721 | 122.2569 | -122.3612 | -122.1616 | -122.3172 | -122.1175
1844.125 | 122.4838 | -122.3602 | 0.027466 | -16.1635 | -16.2358 | -16.2569 | -16.1825 | -16.1926 | -16.1723 | -16.3152 | -0.13981 | -0.016938 | -0.095785 | -0.069733 | 122.2168 | 122.3034 | 122.0218 | 122.2157 | -16.1131 | -16.1854 | -16.2065 | -16.1322 | -16.1422 | -16.1219 | -16.2649 | -0.089455 | 0.033416 | -0.045431 | -0.019379 | 122.2671 | 122.3537 | 122.0721 | 122.2661 | -122.3566 | -122.1616 | -122.3126 | -122.1175
1845.8594 | 122.5296 | -122.3465 | 0.018311 | -16.3603 | -16.4464 | -16.4629 | -16.3931 | -16.394 | -16.3783 | -16.5258 | -0.13981 | -0.016938 | -0.095785 | -0.074312 | 122.2214 | 122.3034 | 122.0218 | 122.2066 | -16.31 | -16.3961 | -16.4126 | -16.3428 | -16.3437 | -16.3279 | -16.4755 | -0.089455 | 0.033416 | -0.045431 | -0.023958 | 122.2717 | 122.3537 | 122.0721 | 122.2569 | -122.3612 | -122.1616 | -122.3172 | -122.1175
1847.5625 | 122.493 | -122.3373 | 0.036621 | -16.4061 | -16.4968 | -16.5087 | -16.4343 | -16.449 | -16.4241 | -16.5716 | -0.14439 | -0.026096 | -0.10494 | -0.069733 | 122.2168 | 122.3034 | 122.0218 | 122.2112 | -16.3558 | -16.4464 | -16.4584 | -16.384 | -16.3986 | -16.3737 | -16.5213 | -0.094033 | 0.024258 | -0.054588 | -0.019379 | 122.2671 | 122.3537 | 122.0721 | 122.2615 | -122.3612 | -122.1661 | -122.3217 | -122.1267
1849.2812 | 122.6074 | -122.3053 | 0.004578 | -16.5755 | -16.6616 | -16.6781 | -16.6083 | -16.6183 | -16.5935 | -16.7364 | -0.13981 | -0.026096 | -0.091207 | -0.08347 | 122.2214 | 122.3034 | 122.0172 | 122.2203 | -16.5252 | -16.6113 | -16.6278 | -16.558 | -16.568 | -16.5431 | -16.6861 | -0.089455 | 0.024258 | -0.040853 | -0.033116 | 122.2717 | 122.3537 | 122.0675 | 122.2707 | -122.3612 | -122.157 | -122.3126 | -122.1084
1851 | 122.5708 | -122.3419 | -0.009155 | -16.7816 | -16.8814 | -16.8842 | -16.8189 | -16.8427 | -16.8224 | -16.9653 | -0.14439 | -0.021517 | -0.095785 | -0.069733 | 122.2168 | 122.3079 | 122.0309 | 122.2157 | -16.7312 | -16.8311 | -16.8338 | -16.7686 | -16.7923 | -16.772 | -16.915 | -0.094033 | 0.028837 | -0.045431 | -0.019379 | 122.2671 | 122.3583 | 122.0813 | 122.2661 | -122.3612 | -122.1753 | -122.3126 | -122.1267
1852.6875 | 122.6395 | -122.3236 | -0.004578 | -17.0105 | -17.1012 | -17.1222 | -17.0433 | -17.0578 | -17.0422 | -17.1805 | -0.13981 | -0.016938 | -0.091207 | -0.065154 | 122.2214 | 122.3125 | 122.0218 | 122.2203 | -16.9601 | -17.0508 | -17.0719 | -16.9929 | -17.0075 | -16.9918 | -17.1302 | -0.089455 | 0.033416 | -0.040853 | -0.0148 | 122.2717 | 122.3629 | 122.0721 | 122.2707 | -122.3612 | -122.1616 | -122.3126 | -122.113
1854.4062 | 122.58 | -122.3419 | 0.018311 | -16.9235 | -17.0508 | -17.0352 | -16.9746 | -17.0121 | -17.0193 | -17.1485 | -0.14439 | -0.021517 | -0.095785 | -0.074312 | 122.2259 | 122.3079 | 122.0309 | 122.2157 | -16.8731 | -17.0005 | -16.9849 | -16.9243 | -16.9617 | -16.9689 | -17.0981 | -0.094033 | 0.028837 | -0.045431 | -0.023958 | 122.2763 | 122.3583 | 122.0813 | 122.2661 | -122.3703 | -122.1753 | -122.3217 | -122.1267
1856.0938 | 122.6028 | -122.3557 | 0.027466 | -16.7632 | -16.8768 | -16.8658 | -16.8281 | -16.861 | -16.859 | -16.9836 | -0.13981 | -0.026096 | -0.095785 | -0.078891 | 122.2351 | 122.3125 | 122.0263 | 122.2203 | -16.7129 | -16.8265 | -16.8155 | -16.7777 | -16.8106 | -16.8087 | -16.9333 | -0.089455 | 0.024258 | -0.045431 | -0.028537 | 122.2855 | 122.3629 | 122.0767 | 122.2707 | -122.3749 | -122.1661 | -122.3309 | -122.1221
1857.7969 | 122.5433 | -122.3648 | 0.027466 | -16.7632 | -16.8723 | -16.8613 | -16.8144 | -16.8564 | -16.8545 | -16.9882 | -0.14439 | -0.021517 | -0.095785 | -0.074312 | 122.2259 | 122.3079 | 122.0309 | 122.2157 | -16.7129 | -16.8219 | -16.8109 | -16.764 | -16.806 | -16.8041 | -16.9379 | -0.094033 | 0.028837 | -0.045431 | -0.023958 | 122.2763 | 122.3583 | 122.0813 | 122.2661 | -122.3703 | -122.1753 | -122.3217 | -122.1267
1859.5 | 122.5113 | -122.3602 | 0.032043 | -16.8319 | -16.9089 | -16.9254 | -16.8601 | -16.893 | -16.8728 | -16.9928 | -0.13981 | -0.021517 | -0.10036 | -0.074312 | 122.2351 | 122.3171 | 122.0218 | 122.2203 | -16.7816 | -16.8585 | -16.875 | -16.8098 | -16.8427 | -16.8224 | -16.9424 | -0.089455 | 0.028837 | -0.050009 | -0.023958 | 122.2855 | 122.3674 | 122.0721 | 122.2707 | -122.3749 | -122.1616 | -122.3355 | -122.1221
1861.1875 | 122.6349 | -122.3236 | -0.004578 | -16.4885 | -16.5655 | -16.5957 | -16.5259 | -16.5497 | -16.534 | -16.6494 | -0.14439 | -0.021517 | -0.091207 | -0.078891 | 122.2305 | 122.3217 | 122.0263 | 122.2249 | -16.4382 | -16.5151 | -16.5453 | -16.4756 | -16.4993 | -16.4836 | -16.5991 | -0.094033 | 0.028837 | -0.040853 | -0.028537 | 122.2809 | 122.372 | 122.0767 | 122.2753 | -122.3749 | -122.1707 | -122.3217 | -122.1175
1862.9375 | 122.5891 | -122.3465 | 0 | -16.8319 | -16.9135 | -16.9345 | -16.8739 | -16.8976 | -16.8728 | -16.9882 | -0.14439 | -0.021517 | -0.091207 | -0.074312 | 122.2351 | 122.3125 | 122.0309 | 122.2249 | -16.7816 | -16.8631 | -16.8842 | -16.8235 | -16.8473 | -16.8224 | -16.9379 | -0.094033 | 0.028837 | -0.040853 | -0.023958 | 122.2855 | 122.3629 | 122.0813 | 122.2753 | -122.3795 | -122.1753 | -122.3263 | -122.1221
1864.625 | 122.5845 | -122.3557 | 0.004578 | -16.7632 | -16.8448 | -16.8567 | -16.7915 | -16.8244 | -16.8087 | -16.9287 | -0.13523 | -0.026096 | -0.095785 | -0.074312 | 122.2305 | 122.3171 | 122.0355 | 122.2295 | -16.7129 | -16.7944 | -16.8063 | -16.7411 | -16.774 | -16.7583 | -16.8784 | -0.084876 | 0.024258 | -0.045431 | -0.023958 | 122.2809 | 122.3674 | 122.0858 | 122.2798 | -122.3658 | -122.1707 | -122.3263 | -122.1313
1866.3125 | 122.5525 | -122.374 | 0.032043 | -16.7724 | -16.8631 | -16.8658 | -16.8052 | -16.8335 | -16.8224 | -16.9333 | -0.13523 | -0.021517 | -0.10036 | -0.078891 | 122.2351 | 122.3308 | 122.0309 | 122.2203 | -16.722 | -16.8127 | -16.8155 | -16.7548 | -16.7832 | -16.772 | -16.8829 | -0.084876 | 0.028837 | -0.050009 | -0.028537 | 122.2855 | 122.3812 | 122.0813 | 122.2707 | -122.3703 | -122.1661 | -122.3355 | -122.1313
1868.0156 | 122.6715 | -122.3419 | 0.004578 | -16.6671 | -16.744 | -16.7605 | -16.7091 | -16.7328 | -16.7079 | -16.828 | -0.14439 | -0.016938 | -0.095785 | -0.065154 | 122.2351 | 122.3263 | 122.0355 | 122.2249 | -16.6167 | -16.6937 | -16.7102 | -16.6587 | -16.6824 | -16.6576 | -16.7776 | -0.094033 | 0.033416 | -0.045431 | -0.0148 | 122.2855 | 122.3766 | 122.0858 | 122.2753 | -122.3795 | -122.1799 | -122.3309 | -122.1313
1869.7656 | 122.6486 | -122.319 | -0.009155 | -16.5206 | -16.6342 | -16.6186 | -16.5809 | -16.6092 | -16.6118 | -16.7318 | -0.13981 | -0.021517 | -0.095785 | -0.074312 | 122.2397 | 122.3263 | 122.0401 | 122.2295 | -16.4702 | -16.5838 | -16.5682 | -16.5305 | -16.5588 | -16.5614 | -16.6815 | -0.089455 | 0.028837 | -0.045431 | -0.023958 | 122.29 | 122.3766 | 122.0904 | 122.2798 | -122.3795 | -122.1799 | -122.3355 | -122.1359
1871.5312 | 122.6166 | -122.3557 | 0.022888 | -16.6396 | -16.7578 | -16.7468 | -16.6999 | -16.7511 | -16.7354 | -16.8646 | -0.14439 | -0.026096 | -0.095785 | -0.069733 | 122.2397 | 122.3171 | 122.0401 | 122.2295 | -16.5893 | -16.7074 | -16.6964 | -16.6495 | -16.7008 | -16.6851 | -16.8143 | -0.094033 | 0.024258 | -0.045431 | -0.019379 | 122.29 | 122.3674 | 122.0904 | 122.2798 | -122.3841 | -122.1845 | -122.3355 | -122.1359
1873.25 | 122.6532 | -122.3511 | -0.013733 | -16.7678 | -16.8677 | -16.8658 | -16.8281 | -16.8564 | -16.859 | -16.9882 | -0.13981 | -0.021517 | -0.091207 | -0.069733 | 122.2397 | 122.3263 | 122.0355 | 122.2295 | -16.7175 | -16.8173 | -16.8155 | -16.7777 | -16.806 | -16.8087 | -16.9379 | -0.089455 | 0.028837 | -0.040853 | -0.019379 | 122.29 | 122.3766 | 122.0858 | 122.2798 | -122.3795 | -122.1753 | -122.3309 | -122.1267
1875 | 122.5571 | -122.3831 | 0.027466 | -16.7907 | -16.8997 | -16.8842 | -16.8418 | -16.8793 | -16.8682 | -16.9974 | -0.13523 | -0.016938 | -0.095785 | -0.074312 | 122.2443 | 122.3263 | 122.0401 | 122.2341 | -16.7404 | -16.8494 | -16.8338 | -16.7915 | -16.8289 | -16.8178 | -16.947 | -0.084876 | 0.033416 | -0.045431 | -0.023958 | 122.2946 | 122.3766 | 122.0904 | 122.2844 | -122.3795 | -122.1753 | -122.34 | -122.1359
1876.7031 | 122.4976 | -122.4106 | 0.022888 | -16.7541 | -16.8631 | -16.8567 | -16.8052 | -16.8472 | -16.8407 | -16.9745 | -0.13523 | -0.026096 | -0.095785 | -0.078891 | 122.2443 | 122.3354 | 122.0401 | 122.2341 | -16.7037 | -16.8127 | -16.8063 | -16.7548 | -16.7969 | -16.7904 | -16.9241 | -0.084876 | 0.024258 | -0.045431 | -0.028537 | 122.2946 | 122.3858 | 122.0904 | 122.2844 | -122.3795 | -122.1753 | -122.34 | -122.1359
1878.4844 | 122.5983 | -122.3373 | 0.004578 | -16.8411 | -16.9547 | -16.9437 | -16.9014 | -16.9388 | -16.9323 | -17.0615 | -0.13981 | -0.026096 | -0.10036 | -0.065154 | 122.2443 | 122.3263 | 122.0492 | 122.2432 | -16.7907 | -16.9043 | -16.8933 | -16.851 | -16.8885 | -16.8819 | -17.0111 | -0.089455 | 0.024258 | -0.050009 | -0.0148 | 122.2946 | 122.3766 | 122.0996 | 122.2936 | -122.3841 | -122.189 | -122.3446 | -122.1496
1880.1875 | 122.612 | -122.374 | 0.004578 | -16.7175 | -16.8265 | -16.8155 | -16.7686 | -16.806 | -16.8041 | -16.9379 | -0.13523 | -0.016938 | -0.10036 | -0.074312 | 122.2488 | 122.3308 | 122.0355 | 122.2386 | -16.6671 | -16.7761 | -16.7651 | -16.7182 | -16.7557 | -16.7537 | -16.8875 | -0.084876 | 0.033416 | -0.050009 | -0.023958 | 122.2992 | 122.3812 | 122.0858 | 122.289 | -122.3841 | -122.1707 | -122.3492 | -122.1359
1881.9219 | 122.6532 | -122.3373 | 0.009155 | -16.4061 | -16.5105 | -16.5041 | -16.4618 | -16.5085 | -16.4973 | -16.6265 | -0.14439 | -0.021517 | -0.095785 | -0.069733 | 122.2443 | 122.3263 | 122.0309 | 122.2432 | -16.3558 | -16.4602 | -16.4538 | -16.4115 | -16.4581 | -16.447 | -16.5762 | -0.094033 | 0.028837 | -0.045431 | -0.019379 | 122.2946 | 122.3766 | 122.0813 | 122.2936 | -122.3886 | -122.1753 | -122.34 | -122.1267
1883.625 | 122.6257 | -122.3602 | -0.004578 | -16.4061 | -16.5105 | -16.4995 | -16.4527 | -16.4947 | -16.4973 | -16.622 | -0.13981 | -0.021517 | -0.10036 | -0.074312 | 122.2488 | 122.34 | 122.0401 | 122.2386 | -16.3558 | -16.4602 | -16.4492 | -16.4023 | -16.4444 | -16.447 | -16.5716 | -0.089455 | 0.028837 | -0.050009 | -0.023958 | 122.2992 | 122.3903 | 122.0904 | 122.289 | -122.3886 | -122.1799 | -122.3492 | -122.1404
1885.3594 | 122.6074 | -122.3602 | 0.004578 | -16.6122 | -16.7212 | -16.7102 | -16.6724 | -16.7099 | -16.7125 | -16.8417 | -0.13981 | -0.016938 | -0.091207 | -0.069733 | 122.2534 | 122.34 | 122.0263 | 122.2341 | -16.5618 | -16.6708 | -16.6598 | -16.6221 | -16.6596 | -16.6622 | -16.7914 | -0.089455 | 0.033416 | -0.040853 | -0.019379 | 122.3038 | 122.3903 | 122.0767 | 122.2844 | -122.3932 | -122.1661 | -122.3446 | -122.1175
1887.0469 | 122.525 | -122.438 | 0.027466 | -16.4107 | -16.5197 | -16.5041 | -16.471 | -16.5085 | -16.5019 | -16.6357 | -0.14439 | -0.021517 | -0.10494 | -0.069733 | 122.258 | 122.3446 | 122.0355 | 122.2386 | -16.3604 | -16.4693 | -16.4538 | -16.4206 | -16.4581 | -16.4516 | -16.5854 | -0.094033 | 0.028837 | -0.054588 | -0.019379 | 122.3083 | 122.3949 | 122.0858 | 122.289 | -122.4024 | -122.1799 | -122.3629 | -122.1404
1888.7188 | 122.5159 | -122.3785 | 0.022888 | -16.3008 | -16.4098 | -16.3988 | -16.3702 | -16.3986 | -16.4058 | -16.5167 | -0.13523 | -0.021517 | -0.095785 | -0.074312 | 122.2534 | 122.34 | 122.0492 | 122.2432 | -16.2505 | -16.3594 | -16.3485 | -16.3199 | -16.3483 | -16.3554 | -16.4663 | -0.084876 | 0.028837 | -0.045431 | -0.023958 | 122.3038 | 122.3903 | 122.0996 | 122.2936 | -122.3886 | -122.1845 | -122.3492 | -122.145
1890.4062 | 122.6486 | -122.3419 | 0 | -16.635 | -16.7486 | -16.7422 | -16.7045 | -16.7374 | -16.7354 | -16.8555 | -0.14439 | -0.016938 | -0.091207 | -0.078891 | 122.2488 | 122.3354 | 122.0355 | 122.2432 | -16.5847 | -16.6983 | -16.6919 | -16.6541 | -16.687 | -16.6851 | -16.8051 | -0.094033 | 0.033416 | -0.040853 | -0.028537 | 122.2992 | 122.3858 | 122.0858 | 122.2936 | -122.3932 | -122.1799 | -122.34 | -122.1267
1892.1094 | 122.5479 | -122.3923 | 0.027466 | -16.7495 | -16.8539 | -16.8521 | -16.8144 | -16.8472 | -16.8407 | -16.9653 | -0.14439 | -0.016938 | -0.10036 | -0.074312 | 122.2626 | 122.34 | 122.0446 | 122.2478 | -16.6992 | -16.8036 | -16.8017 | -16.764 | -16.7969 | -16.7904 | -16.915 | -0.094033 | 0.033416 | -0.050009 | -0.023958 | 122.3129 | 122.3903 | 122.095 | 122.2981 | -122.407 | -122.189 | -122.3629 | -122.145
1893.8906 | 122.6624 | -122.3465 | 0.004578 | -16.8273 | -16.9409 | -16.9345 | -16.8876 | -16.9388 | -16.9323 | -17.0569 | -0.14439 | -0.012359 | -0.10036 | -0.074312 | 122.2626 | 122.3446 | 122.0401 | 122.2432 | -16.777 | -16.8906 | -16.8842 | -16.8373 | -16.8885 | -16.8819 | -17.0065 | -0.094033 | 0.037995 | -0.050009 | -0.023958 | 122.3129 | 122.3949 | 122.0904 | 122.2936 | -122.407 | -122.1845 | -122.3629 | -122.1404
1895.5781 | 122.5296 | -122.406 | 0.036621 | -16.8777 | -16.9821 | -16.9803 | -16.938 | -16.98 | -16.9735 | -17.0981 | -0.13981 | -0.026096 | -0.10036 | -0.074312 | 122.258 | 122.3446 | 122.0401 | 122.2432 | -16.8273 | -16.9318 | -16.9299 | -16.8876 | -16.9297 | -16.9231 | -17.0477 | -0.089455 | 0.024258 | -0.050009 | -0.023958 | 122.3083 | 122.3949 | 122.0904 | 122.2936 | -122.3978 | -122.1799 | -122.3584 | -122.1404
1897.2969 | 122.5113 | -122.4243 | 0.018311 | -16.9372 | -17.0462 | -17.0352 | -17.0021 | -17.0395 | -17.0284 | -17.1622 | -0.13523 | -0.026096 | -0.10036 | -0.074312 | 122.258 | 122.3446 | 122.0355 | 122.2524 | -16.8869 | -16.9959 | -16.9849 | -16.9517 | -16.9892 | -16.9781 | -17.1118 | -0.084876 | 0.024258 | -0.050009 | -0.023958 | 122.3083 | 122.3949 | 122.0858 | 122.3027 | -122.3932 | -122.1707 | -122.3584 | -122.1359
1899 | 122.5662 | -122.3923 | 0.018311 | -16.8548 | -16.9593 | -16.9528 | -16.9151 | -16.9525 | -16.9506 | -17.0752 | -0.13981 | -0.021517 | -0.091207 | -0.069733 | 122.258 | 122.3446 | 122.0355 | 122.2478 | -16.8045 | -16.9089 | -16.9025 | -16.8647 | -16.9022 | -16.9002 | -17.0249 | -0.089455 | 0.028837 | -0.040853 | -0.019379 | 122.3083 | 122.3949 | 122.0858 | 122.2981 | -122.3978 | -122.1753 | -122.3492 | -122.1267
1900.6719 | 122.6669 | -122.3557 | 0.004578 | -16.8502 | -16.9638 | -16.9483 | -16.9059 | -16.9525 | -16.9506 | -17.0706 | -0.14897 | -0.016938 | -0.10036 | -0.078891 | 122.2626 | 122.3446 | 122.0263 | 122.2524 | -16.7999 | -16.9135 | -16.8979 | -16.8556 | -16.9022 | -16.9002 | -17.0203 | -0.098612 | 0.033416 | -0.050009 | -0.028537 | 122.3129 | 122.3949 | 122.0767 | 122.3027 | -122.4115 | -122.1753 | -122.3629 | -122.1267
1902.375 | 122.5296 | -122.406 | 0.009155 | -16.8777 | -16.9913 | -16.9849 | -16.9563 | -16.9892 | -16.9826 | -17.1164 | -0.14439 | -0.026096 | -0.095785 | -0.074312 | 122.2626 | 122.3537 | 122.0355 | 122.2524 | -16.8273 | -16.9409 | -16.9345 | -16.9059 | -16.9388 | -16.9323 | -17.0661 | -0.094033 | 0.024258 | -0.045431 | -0.023958 | 122.3129 | 122.4041 | 122.0858 | 122.3027 | -122.407 | -122.1799 | -122.3584 | -122.1313
1904.0781 | 122.5845 | -122.374 | 0.004578 | -16.951 | -17.0646 | -17.049 | -17.0067 | -17.0487 | -17.0422 | -17.1714 | -0.14897 | -0.026096 | -0.10036 | -0.074312 | 122.2671 | 122.3583 | 122.0446 | 122.2569 | -16.9006 | -17.0142 | -16.9986 | -16.9563 | -16.9983 | -16.9918 | -17.121 | -0.098612 | 0.024258 | -0.050009 | -0.023958 | 122.3175 | 122.4087 | 122.095 | 122.3073 | -122.4161 | -122.1936 | -122.3675 | -122.145
1905.75 | 122.5433 | -122.4152 | 0.027466 | -17.1432 | -17.2477 | -17.2321 | -17.1898 | -17.2318 | -17.2299 | -17.3636 | -0.13523 | -0.021517 | -0.095785 | -0.074312 | 122.2626 | 122.3491 | 122.0355 | 122.2569 | -17.0929 | -17.1974 | -17.1818 | -17.1394 | -17.1814 | -17.1795 | -17.3133 | -0.084876 | 0.028837 | -0.045431 | -0.023958 | 122.3129 | 122.3995 | 122.0858 | 122.3073 | -122.3978 | -122.1707 | -122.3584 | -122.1313
1907.4219 | 122.6486 | -122.374 | 0.009155 | -16.9967 | -17.1195 | -17.0993 | -17.0616 | -17.1036 | -17.0971 | -17.2263 | -0.14439 | -0.026096 | -0.095785 | -0.069733 | 122.2717 | 122.3537 | 122.0492 | 122.2615 | -16.9464 | -17.0692 | -17.049 | -17.0112 | -17.0533 | -17.0468 | -17.1759 | -0.094033 | 0.024258 | -0.045431 | -0.019379 | 122.3221 | 122.4041 | 122.0996 | 122.3119 | -122.4161 | -122.1936 | -122.3675 | -122.145
1909.0938 | 122.5845 | -122.4289 | 0.013733 | -16.9555 | -17.0737 | -17.0581 | -17.0204 | -17.0578 | -17.0559 | -17.1851 | -0.13981 | -0.021517 | -0.10036 | -0.069733 | 122.2763 | 122.3583 | 122.0401 | 122.2615 | -16.9052 | -17.0234 | -17.0078 | -16.97 | -17.0075 | -17.0055 | -17.1347 | -0.089455 | 0.028837 | -0.050009 | -0.019379 | 122.3267 | 122.4087 | 122.0904 | 122.3119 | -122.4161 | -122.1799 | -122.3767 | -122.1404
1910.7812 | 122.6532 | -122.3419 | -0.009155 | -16.951 | -17.06 | -17.0536 | -17.0112 | -17.0533 | -17.0559 | -17.1759 | -0.13523 | -0.021517 | -0.091207 | -0.074312 | 122.2763 | 122.3537 | 122.0309 | 122.2615 | -16.9006 | -17.0096 | -17.0032 | -16.9609 | -17.0029 | -17.0055 | -17.1256 | -0.084876 | 0.028837 | -0.040853 | -0.023958 | 122.3267 | 122.4041 | 122.0813 | 122.3119 | -122.4115 | -122.1661 | -122.3675 | -122.1221
1912.4688 | 122.5433 | -122.4243 | 0.027466 | -16.7816 | -16.9043 | -16.8887 | -16.8464 | -16.8884 | -16.8819 | -17.0157 | -0.13981 | -0.021517 | -0.10036 | -0.078891 | 122.2763 | 122.3583 | 122.0355 | 122.2569 | -16.7312 | -16.854 | -16.8384 | -16.7961 | -16.8381 | -16.8316 | -16.9653 | -0.089455 | 0.028837 | -0.050009 | -0.028537 | 122.3267 | 122.4087 | 122.0858 | 122.3073 | -122.4161 | -122.1753 | -122.3767 | -122.1359
1914.1562 | 122.6074 | -122.3785 | -0.004578 | -16.7495 | -16.8631 | -16.8521 | -16.8098 | -16.8381 | -16.8407 | -16.9653 | -0.13981 | -0.012359 | -0.091207 | -0.074312 | 122.2717 | 122.3629 | 122.0401 | 122.2569 | -16.6992 | -16.8127 | -16.8017 | -16.7594 | -16.7877 | -16.7904 | -16.915 | -0.089455 | 0.037995 | -0.040853 | -0.023958 | 122.3221 | 122.4132 | 122.0904 | 122.3073 | -122.4115 | -122.1799 | -122.3629 | -122.1313
1915.9219 | 122.6349 | -122.3877 | -0.004578 | -16.3558 | -16.4739 | -16.4446 | -16.4069 | -16.449 | -16.4516 | -16.5716 | -0.13981 | -0.016938 | -0.095785 | -0.074312 | 122.2809 | 122.3583 | 122.0355 | 122.2615 | -16.3054 | -16.4235 | -16.3943 | -16.3565 | -16.3986 | -16.4012 | -16.5213 | -0.089455 | 0.033416 | -0.045431 | -0.023958 | 122.3312 | 122.4087 | 122.0858 | 122.3119 | -122.4207 | -122.1753 | -122.3767 | -122.1313
1917.625 | 122.5571 | -122.4106 | 0.032043 | -16.2734 | -16.3869 | -16.3759 | -16.3245 | -16.362 | -16.36 | -16.4846 | -0.13523 | -0.012359 | -0.091207 | -0.069733 | 122.2717 | 122.3583 | 122.0355 | 122.2707 | -16.223 | -16.3365 | -16.3256 | -16.2741 | -16.3116 | -16.3096 | -16.4343 | -0.084876 | 0.037995 | -0.040853 | -0.019379 | 122.3221 | 122.4087 | 122.0858 | 122.321 | -122.407 | -122.1707 | -122.3629 | -122.1267
1919.3438 | 122.5479 | -122.4106 | 0.022888 | -16.1497 | -16.2495 | -16.2386 | -16.1963 | -16.2292 | -16.2318 | -16.3656 | -0.13981 | -0.021517 | -0.095785 | -0.069733 | 122.2763 | 122.3675 | 122.0355 | 122.2615 | -16.0994 | -16.1992 | -16.1882 | -16.1459 | -16.1789 | -16.1814 | -16.3152 | -0.089455 | 0.028837 | -0.045431 | -0.019379 | 122.3267 | 122.4178 | 122.0858 | 122.3119 | -122.4161 | -122.1753 | -122.3721 | -122.1313
1921.0781 | 122.5937 | -122.4197 | 0.018311 | -15.7285 | -15.8374 | -15.8219 | -15.7796 | -15.8172 | -15.8152 | -15.9536 | -0.14439 | -0.021517 | -0.10036 | -0.065154 | 122.2717 | 122.3675 | 122.0401 | 122.2569 | -15.6782 | -15.7871 | -15.7716 | -15.7293 | -15.7669 | -15.7648 | -15.9032 | -0.094033 | 0.028837 | -0.050009 | -0.0148 | 122.3221 | 122.4178 | 122.0904 | 122.3073 | -122.4161 | -122.1845 | -122.3721 | -122.1404
1922.75 | 122.6578 | -122.3831 | 0.004578 | -15.7514 | -15.8512 | -15.854 | -15.7934 | -15.8355 | -15.8426 | -15.9673 | -0.14439 | -0.021517 | -0.091207 | -0.074312 | 122.2763 | 122.3583 | 122.0446 | 122.2661 | -15.7011 | -15.8008 | -15.8036 | -15.743 | -15.7852 | -15.7923 | -15.9169 | -0.094033 | 0.028837 | -0.040853 | -0.023958 | 122.3267 | 122.4087 | 122.095 | 122.3165 | -122.4207 | -122.189 | -122.3675 | -122.1359
1924.4688 | 122.6028 | -122.3877 | -0.004578 | -16.1223 | -16.2312 | -16.2203 | -16.1825 | -16.2246 | -16.2089 | -16.3473 | -0.14439 | -0.021517 | -0.095785 | -0.065154 | 122.2763 | 122.3675 | 122.0401 | 122.2615 | -16.0719 | -16.1809 | -16.1699 | -16.1322 | -16.1743 | -16.1585 | -16.2969 | -0.094033 | 0.028837 | -0.045431 | -0.0148 | 122.3267 | 122.4178 | 122.0904 | 122.3119 | -122.4207 | -122.1845 | -122.3721 | -122.1359
1926.1719 | 122.6074 | -122.3877 | 0.045776 | -15.9346 | -16.0435 | -16.0142 | -15.9857 | -16.0186 | -16.0258 | -16.1504 | -0.13981 | -0.021517 | -0.095785 | -0.074312 | 122.2855 | 122.3629 | 122.0446 | 122.2661 | -15.8842 | -15.9931 | -15.9639 | -15.9353 | -15.9683 | -15.9754 | -16.1001 | -0.089455 | 0.028837 | -0.045431 | -0.023958 | 122.3358 | 122.4132 | 122.095 | 122.3165 | -122.4253 | -122.1845 | -122.3812 | -122.1404
1927.9219 | 122.6028 | -122.4014 | 0.013733 | -15.6965 | -15.8054 | -15.7899 | -15.7567 | -15.7989 | -15.7968 | -15.9215 | -0.14439 | -0.021517 | -0.095785 | -0.074312 | 122.2855 | 122.3629 | 122.0401 | 122.2661 | -15.6461 | -15.755 | -15.7395 | -15.7064 | -15.7485 | -15.7465 | -15.8712 | -0.094033 | 0.028837 | -0.045431 | -0.023958 | 122.3358 | 122.4132 | 122.0904 | 122.3165 | -122.4298 | -122.1845 | -122.3812 | -122.1359
1929.6094 | 122.5845 | -122.4152 | 0 | -15.6965 | -15.7962 | -15.7899 | -15.7521 | -15.7943 | -15.7923 | -15.9124 | -0.13981 | -0.012359 | -0.091207 | -0.069733 | 122.29 | 122.3675 | 122.0401 | 122.2707 | -15.6461 | -15.7459 | -15.7395 | -15.7018 | -15.744 | -15.7419 | -15.862 | -0.089455 | 0.037995 | -0.040853 | -0.019379 | 122.3404 | 122.4178 | 122.0904 | 122.321 | -122.4298 | -122.1799 | -122.3812 | -122.1313
1931.2969 | 122.5479 | -122.438 | 0.018311 | -15.4813 | -15.5902 | -15.5838 | -15.537 | -15.5837 | -15.5862 | -15.7063 | -0.14439 | -0.016938 | -0.095785 | -0.060575 | 122.2763 | 122.3629 | 122.0492 | 122.2707 | -15.4309 | -15.5398 | -15.5335 | -15.4866 | -15.5334 | -15.5359 | -15.656 | -0.094033 | 0.033416 | -0.045431 | -0.010221 | 122.3267 | 122.4132 | 122.0996 | 122.321 | -122.4207 | -122.1936 | -122.3721 | -122.145
1933 | 122.5754 | -122.4289 | 0.018311 | -15.8155 | -15.9153 | -15.9135 | -15.8666 | -15.9133 | -15.9159 | -16.0314 | -0.13523 | -0.021517 | -0.095785 | -0.069733 | 122.2763 | 122.3675 | 122.0492 | 122.2753 | -15.7652 | -15.8649 | -15.8631 | -15.8163 | -15.863 | -15.8655 | -15.981 | -0.084876 | 0.028837 | -0.045431 | -0.019379 | 122.3267 | 122.4178 | 122.0996 | 122.3256 | -122.4115 | -122.1845 | -122.3721 | -122.145
1934.6875 | 122.6212 | -122.3969 | -0.004578 | -15.8338 | -15.929 | -15.9272 | -15.8849 | -15.9271 | -15.9342 | -16.0497 | -0.13981 | -0.016938 | -0.091207 | -0.069733 | 122.2809 | 122.372 | 122.0492 | 122.2753 | -15.7835 | -15.8787 | -15.8769 | -15.8346 | -15.8767 | -15.8838 | -15.9993 | -0.089455 | 0.033416 | -0.040853 | -0.019379 | 122.3312 | 122.4224 | 122.0996 | 122.3256 | -122.4207 | -122.189 | -122.3721 | -122.1404
1936.4062 | 122.5342 | -122.4152 | 0.036621 | -15.5408 | -15.6497 | -15.6342 | -15.5965 | -15.6432 | -15.6458 | -15.7704 | -0.14897 | -0.026096 | -0.095785 | -0.074312 | 122.2855 | 122.3766 | 122.0492 | 122.2753 | -15.4905 | -15.5994 | -15.5838 | -15.5461 | -15.5929 | -15.5954 | -15.7201 | -0.098612 | 0.024258 | -0.045431 | -0.023958 | 122.3358 | 122.427 | 122.0996 | 122.3256 | -122.4344 | -122.1982 | -122.3812 | -122.145
1938.1406 | 122.6486 | -122.4014 | 0.004578 | -15.6782 | -15.7825 | -15.7715 | -15.7201 | -15.7668 | -15.7831 | -15.894 | -0.13981 | -0.016938 | -0.095785 | -0.065154 | 122.2855 | 122.3812 | 122.0492 | 122.2753 | -15.6278 | -15.7321 | -15.7212 | -15.6697 | -15.7165 | -15.7328 | -15.8437 | -0.089455 | 0.033416 | -0.045431 | -0.0148 | 122.3358 | 122.4315 | 122.0996 | 122.3256 | -122.4253 | -122.189 | -122.3812 | -122.145
1939.8281 | 122.5754 | -122.438 | 0.027466 | -15.5225 | -15.6314 | -15.6205 | -15.5782 | -15.6158 | -15.6274 | -15.7384 | -0.14897 | -0.016938 | -0.10036 | -0.069733 | 122.29 | 122.3766 | 122.0538 | 122.2753 | -15.4721 | -15.581 | -15.5701 | -15.5278 | -15.5654 | -15.5771 | -15.688 | -0.098612 | 0.033416 | -0.050009 | -0.019379 | 122.3404 | 122.427 | 122.1042 | 122.3256 | -122.439 | -122.2028 | -122.3904 | -122.1542
1941.5312 | 122.7127 | -122.3923 | 0 | -15.2249 | -15.32 | -15.3091 | -15.2714 | -15.3228 | -15.3161 | -15.4316 | -0.13981 | -0.021517 | -0.091207 | -0.074312 | 122.29 | 122.3812 | 122.0492 | 122.2844 | -15.1746 | -15.2697 | -15.2588 | -15.2211 | -15.2724 | -15.2658 | -15.3813 | -0.089455 | 0.028837 | -0.040853 | -0.023958 | 122.3404 | 122.4315 | 122.0996 | 122.3348 | -122.4298 | -122.189 | -122.3812 | -122.1404
1943.2344 | 122.644 | -122.3923 | 0.022888 | -15.2798 | -15.3704 | -15.3686 | -15.3401 | -15.3731 | -15.3802 | -15.482 | -0.14439 | -0.026096 | -0.10036 | -0.069733 | 122.2992 | 122.3766 | 122.0538 | 122.2844 | -15.2295 | -15.32 | -15.3183 | -15.2897 | -15.3228 | -15.3299 | -15.4317 | -0.094033 | 0.024258 | -0.050009 | -0.019379 | 122.3495 | 122.427 | 122.1042 | 122.3348 | -122.4436 | -122.1982 | -122.3996 | -122.1542
1945.0156 | 122.6807 | -122.4152 | 0.004578 | -15.1013 | -15.1827 | -15.1901 | -15.1295 | -15.1809 | -15.1833 | -15.2989 | -0.13981 | -0.016938 | -0.091207 | -0.078891 | 122.2946 | 122.3812 | 122.0538 | 122.2844 | -15.0509 | -15.1323 | -15.1397 | -15.0791 | -15.1305 | -15.133 | -15.2485 | -0.089455 | 0.033416 | -0.040853 | -0.028537 | 122.345 | 122.4315 | 122.1042 | 122.3348 | -122.4344 | -122.1936 | -122.3858 | -122.145
1946.6875 | 122.644 | -122.4014 | 0.022888 | -15.3943 | -15.4666 | -15.4877 | -15.4271 | -15.4327 | -15.4214 | -15.5598 | -0.14439 | -0.012359 | -0.10036 | -0.074312 | 122.3038 | 122.3766 | 122.063 | 122.2798 | -15.344 | -15.4162 | -15.4373 | -15.3767 | -15.3823 | -15.3711 | -15.5095 | -0.094033 | 0.037995 | -0.050009 | -0.023958 | 122.3541 | 122.427 | 122.1133 | 122.3302 | -122.4482 | -122.2073 | -122.4041 | -122.1633
1948.4062 | 122.6852 | -122.3969 | 0.036621 | -15.2982 | -15.3887 | -15.3915 | -15.3263 | -15.3731 | -15.3802 | -15.5049 | -0.14439 | -0.016938 | -0.095785 | -0.069733 | 122.2946 | 122.3903 | 122.0584 | 122.2844 | -15.2478 | -15.3384 | -15.3412 | -15.276 | -15.3228 | -15.3299 | -15.4545 | -0.094033 | 0.033416 | -0.045431 | -0.019379 | 122.345 | 122.4407 | 122.1087 | 122.3348 | -122.439 | -122.2028 | -122.3904 | -122.1542
1950.0938 | 122.7036 | -122.3969 | 0.027466 | -15.1196 | -15.2056 | -15.2084 | -15.1478 | -15.1946 | -15.2017 | -15.3263 | -0.14439 | -0.016938 | -0.095785 | -0.074312 | 122.2992 | 122.3858 | 122.063 | 122.2844 | -15.0692 | -15.1552 | -15.158 | -15.0974 | -15.1442 | -15.1513 | -15.276 | -0.094033 | 0.033416 | -0.045431 | -0.023958 | 122.3495 | 122.4361 | 122.1133 | 122.3348 | -122.4436 | -122.2073 | -122.395 | -122.1587
1951.7812 | 122.6532 | -122.406 | 0.013733 | -14.8083 | -14.8942 | -14.897 | -14.8364 | -14.8833 | -14.8949 | -15.015 | -0.13523 | -0.016938 | -0.091207 | -0.069733 | 122.2946 | 122.3812 | 122.063 | 122.2798 | -14.7579 | -14.8438 | -14.8467 | -14.7861 | -14.8329 | -14.8445 | -14.9647 | -0.084876 | 0.033416 | -0.040853 | -0.019379 | 122.345 | 122.4315 | 122.1133 | 122.3302 | -122.4298 | -122.1982 | -122.3858 | -122.1542
1953.4688 | 122.5845 | -122.4243 | 0.013733 | -14.8357 | -14.9125 | -14.9291 | -14.8685 | -14.8879 | -14.8583 | -14.9967 | -0.14439 | -0.021517 | -0.091207 | -0.08347 | 122.2992 | 122.3858 | 122.0584 | 122.2798 | -14.7854 | -14.8622 | -14.8787 | -14.8181 | -14.8375 | -14.8079 | -14.9464 | -0.094033 | 0.028837 | -0.040853 | -0.033116 | 122.3495 | 122.4361 | 122.1087 | 122.3302 | -122.4436 | -122.2028 | -122.3904 | -122.1496
1955.1719 | 122.644 | -122.4152 | 0.018311 | -15.2524 | -15.3292 | -15.3457 | -15.2806 | -15.2953 | -15.2658 | -15.4179 | -0.13981 | -0.026096 | -0.10036 | -0.074312 | 122.2992 | 122.3949 | 122.063 | 122.289 | -15.202 | -15.2788 | -15.2954 | -15.2302 | -15.245 | -15.2154 | -15.3676 | -0.089455 | 0.024258 | -0.050009 | -0.023958 | 122.3495 | 122.4453 | 122.1133 | 122.3393 | -122.439 | -122.2028 | -122.3996 | -122.1633
1956.8906 | 122.5616 | -122.4152 | 0.036621 | -15.4264 | -15.5307 | -15.5197 | -15.4591 | -15.5013 | -15.5084 | -15.6285 | -0.13981 | -0.021517 | -0.095785 | -0.065154 | 122.2992 | 122.3903 | 122.0584 | 122.289 | -15.376 | -15.4803 | -15.4694 | -15.4088 | -15.451 | -15.4581 | -15.5782 | -0.089455 | 0.028837 | -0.045431 | -0.0148 | 122.3495 | 122.4407 | 122.1087 | 122.3393 | -122.439 | -122.1982 | -122.395 | -122.1542
1958.5625 | 122.6852 | -122.4014 | -0.009155 | -15.4905 | -15.5993 | -15.5838 | -15.5278 | -15.5654 | -15.5817 | -15.6972 | -0.13981 | -0.012359 | -0.091207 | -0.069733 | 122.3038 | 122.3949 | 122.0584 | 122.2981 | -15.4401 | -15.549 | -15.5335 | -15.4774 | -15.5151 | -15.5313 | -15.6468 | -0.089455 | 0.037995 | -0.040853 | -0.019379 | 122.3541 | 122.4453 | 122.1087 | 122.3485 | -122.4436 | -122.1982 | -122.395 | -122.1496
1960.25 | 122.5616 | -122.4564 | 0.032043 | -15.3851 | -15.494 | -15.4831 | -15.4179 | -15.4555 | -15.4764 | -15.601 | -0.13523 | -0.012359 | -0.095785 | -0.074312 | 122.2992 | 122.3903 | 122.063 | 122.2936 | -15.3348 | -15.4437 | -15.4327 | -15.3676 | -15.4052 | -15.426 | -15.5507 | -0.084876 | 0.037995 | -0.045431 | -0.023958 | 122.3495 | 122.4407 | 122.1133 | 122.3439 | -122.4344 | -122.1982 | -122.395 | -122.1587
1961.9219 | 122.5983 | -122.4564 | 0.036621 | -15.582 | -15.6818 | -15.6754 | -15.6102 | -15.6616 | -15.6732 | -15.7979 | -0.13523 | -0.012359 | -0.10036 | -0.069733 | 122.3038 | 122.3858 | 122.0584 | 122.2936 | -15.5317 | -15.6314 | -15.625 | -15.5599 | -15.6112 | -15.6229 | -15.7475 | -0.084876 | 0.037995 | -0.050009 | -0.019379 | 122.3541 | 122.4361 | 122.1087 | 122.3439 | -122.439 | -122.1936 | -122.4041 | -122.1587
1963.6094 | 122.58 | -122.4335 | 0.032043 | -15.2112 | -15.288 | -15.3045 | -15.2394 | -15.2495 | -15.2337 | -15.3675 | -0.13981 | -0.016938 | -0.091207 | -0.08347 | 122.3038 | 122.3995 | 122.0675 | 122.2981 | -15.1608 | -15.2376 | -15.2542 | -15.189 | -15.1992 | -15.1833 | -15.3172 | -0.089455 | 0.033416 | -0.040853 | -0.033116 | 122.3541 | 122.4499 | 122.1179 | 122.3485 | -122.4436 | -122.2074 | -122.395 | -122.1587
1965.2812 | 122.7127 | -122.3923 | -0.013733 | -15.5912 | -15.668 | -15.6754 | -15.624 | -15.6341 | -15.6091 | -15.7613 | -0.13981 | -0.016938 | -0.091207 | -0.074312 | 122.3129 | 122.3949 | 122.063 | 122.3027 | -15.5408 | -15.6177 | -15.625 | -15.5736 | -15.5837 | -15.5588 | -15.7109 | -0.089455 | 0.033416 | -0.040853 | -0.023958 | 122.3633 | 122.4453 | 122.1133 | 122.3531 | -122.4527 | -122.2028 | -122.4041 | -122.1542
1967.0156 | 122.6578 | -122.4335 | -0.004578 | -15.1196 | -15.201 | -15.213 | -15.1569 | -15.1671 | -15.1467 | -15.2851 | -0.14439 | -0.021517 | -0.095785 | -0.065154 | 122.3084 | 122.3903 | 122.0675 | 122.2981 | -15.0692 | -15.1506 | -15.1626 | -15.1066 | -15.1168 | -15.0964 | -15.2348 | -0.094033 | 0.028837 | -0.045431 | -0.0148 | 122.3587 | 122.4407 | 122.1179 | 122.3485 | -122.4527 | -122.2119 | -122.4041 | -122.1633
1968.7031 | 122.6303 | -122.4472 | 0.018311 | -14.9594 | -15.0407 | -15.0573 | -14.9921 | -15.0115 | -14.991 | -15.1341 | -0.13523 | -0.016938 | -0.08205 | -0.065154 | 122.3129 | 122.3903 | 122.0813 | 122.2981 | -14.909 | -14.9904 | -15.0069 | -14.9418 | -14.9611 | -14.9407 | -15.0837 | -0.084876 | 0.033416 | -0.031696 | -0.0148 | 122.3633 | 122.4407 | 122.1316 | 122.3485 | -122.4482 | -122.2165 | -122.395 | -122.1633
1970.4062 | 122.699 | -122.3969 | -0.009155 | -14.941 | -15.0224 | -15.039 | -14.9692 | -14.9932 | -14.9636 | -15.1158 | -0.13981 | -0.021517 | -0.091207 | -0.065154 | 122.3129 | 122.3995 | 122.0675 | 122.2981 | -14.8907 | -14.9721 | -14.9886 | -14.9189 | -14.9428 | -14.9132 | -15.0654 | -0.089455 | 0.028837 | -0.040853 | -0.0148 | 122.3633 | 122.4499 | 122.1179 | 122.3485 | -122.4527 | -122.2074 | -122.4041 | -122.1587
1972.1094 | 122.5983 | -122.4564 | 0.013733 | -15.0418 | -15.1231 | -15.1397 | -15.07 | -15.0939 | -15.0597 | -15.2165 | -0.13981 | -0.012359 | -0.091207 | -0.069733 | 122.3084 | 122.3903 | 122.0675 | 122.3027 | -14.9914 | -15.0728 | -15.0893 | -15.0196 | -15.0435 | -15.0094 | -15.1661 | -0.089455 | 0.037995 | -0.040853 | -0.019379 | 122.3587 | 122.4407 | 122.1179 | 122.3531 | -122.4482 | -122.2074 | -122.3996 | -122.1587
1973.7812 | 122.6624 | -122.4518 | 0.004578 | -14.9548 | -15.0407 | -15.0527 | -14.9921 | -15.0069 | -14.991 | -15.1295 | -0.14897 | -0.021517 | -0.086628 | -0.074312 | 122.3221 | 122.3995 | 122.0721 | 122.3073 | -14.9044 | -14.9904 | -15.0024 | -14.9418 | -14.9566 | -14.9407 | -15.0791 | -0.098612 | 0.028837 | -0.036274 | -0.023958 | 122.3724 | 122.4499 | 122.1225 | 122.3577 | -122.4711 | -122.2211 | -122.4087 | -122.1587
1975.4688 | 122.5571 | -122.4335 | 0.022888 | -14.996 | -15.0774 | -15.0848 | -15.0242 | -15.039 | -15.0094 | -15.1661 | -0.13523 | -0.012359 | -0.10036 | -0.074312 | 122.3084 | 122.3949 | 122.0721 | 122.2981 | -14.9456 | -15.027 | -15.0344 | -14.9738 | -14.9886 | -14.959 | -15.1158 | -0.084876 | 0.037995 | -0.050009 | -0.023958 | 122.3587 | 122.4453 | 122.1225 | 122.3485 | -122.4436 | -122.2074 | -122.4087 | -122.1725
1977.1562 | 122.6715 | -122.438 | 0.018311 | -14.9365 | -15.0224 | -15.0344 | -14.9738 | -14.9886 | -14.9636 | -15.1112 | -0.13981 | -0.016938 | -0.091207 | -0.069733 | 122.3175 | 122.3949 | 122.0767 | 122.3027 | -14.8861 | -14.9721 | -14.984 | -14.9234 | -14.9382 | -14.9132 | -15.0608 | -0.089455 | 0.033416 | -0.040853 | -0.019379 | 122.3679 | 122.4453 | 122.1271 | 122.3531 | -122.4573 | -122.2165 | -122.4087 | -122.1679
1978.8594 | 122.5845 | -122.4701 | 0.009155 | -15.2066 | -15.288 | -15.2862 | -15.221 | -15.2312 | -15.22 | -15.3767 | -0.13523 | -0.012359 | -0.095785 | -0.065154 | 122.3129 | 122.3995 | 122.0721 | 122.2981 | -15.1562 | -15.2376 | -15.2359 | -15.1707 | -15.1809 | -15.1696 | -15.3264 | -0.084876 | 0.037995 | -0.045431 | -0.0148 | 122.3633 | 122.4499 | 122.1225 | 122.3485 | -122.4482 | -122.2074 | -122.4087 | -122.1679
1980.5469 | 122.6578 | -122.4472 | 0.004578 | -15.2341 | -15.3338 | -15.3366 | -15.2668 | -15.2862 | -15.2658 | -15.4225 | -0.13523 | -0.012359 | -0.091207 | -0.069733 | 122.3129 | 122.4087 | 122.0767 | 122.3073 | -15.1837 | -15.2834 | -15.2862 | -15.2165 | -15.2358 | -15.2154 | -15.3721 | -0.084876 | 0.037995 | -0.040853 | -0.019379 | 122.3633 | 122.459 | 122.1271 | 122.3577 | -122.4482 | -122.2119 | -122.4041 | -122.1679
1982.2188 | 122.731 | -122.406 | -0.004578 | -15.0967 | -15.1872 | -15.1855 | -15.1341 | -15.1442 | -15.1147 | -15.2806 | -0.14897 | -0.016938 | -0.095785 | -0.069733 | 122.3175 | 122.4041 | 122.0767 | 122.3073 | -15.0464 | -15.1369 | -15.1351 | -15.0837 | -15.0939 | -15.0643 | -15.2302 | -0.098612 | 0.033416 | -0.045431 | -0.019379 | 122.3679 | 122.4544 | 122.1271 | 122.3577 | -122.4665 | -122.2257 | -122.4133 | -122.1725
1983.8906 | 122.6257 | -122.4518 | 0.022888 | -15.0372 | -15.1369 | -15.1397 | -15.0745 | -15.0893 | -15.0689 | -15.2256 | -0.13523 | -0.021517 | -0.091207 | -0.074312 | 122.3221 | 122.4087 | 122.0813 | 122.3073 | -14.9868 | -15.0865 | -15.0893 | -15.0242 | -15.039 | -15.0185 | -15.1753 | -0.084876 | 0.028837 | -0.040853 | -0.023958 | 122.3724 | 122.459 | 122.1316 | 122.3577 | -122.4573 | -122.2165 | -122.4133 | -122.1725
1985.6094 | 122.6807 | -122.4014 | -0.004578 | -15.0555 | -15.1415 | -15.1397 | -15.0837 | -15.0985 | -15.0689 | -15.2302 | -0.14439 | -0.016938 | -0.091207 | -0.065154 | 122.3221 | 122.3995 | 122.0721 | 122.3165 | -15.0052 | -15.0911 | -15.0893 | -15.0333 | -15.0481 | -15.0185 | -15.1799 | -0.094033 | 0.033416 | -0.040853 | -0.0148 | 122.3724 | 122.4499 | 122.1225 | 122.3668 | -122.4665 | -122.2165 | -122.4133 | -122.1633
1987.2969 | 122.7127 | -122.438 | -0.004578 | -15.3165 | -15.407 | -15.4053 | -15.3447 | -15.364 | -15.3436 | -15.4912 | -0.14439 | -0.016938 | -0.095785 | -0.065154 | 122.3267 | 122.4041 | 122.0767 | 122.3073 | -15.2661 | -15.3567 | -15.3549 | -15.2943 | -15.3136 | -15.2932 | -15.4408 | -0.094033 | 0.033416 | -0.045431 | -0.0148 | 122.377 | 122.4544 | 122.1271 | 122.3577 | -122.4711 | -122.2211 | -122.4224 | -122.1725
1989 | 122.5708 | -122.4472 | 0.027466 | -15.1745 | -15.2605 | -15.2633 | -15.2119 | -15.2175 | -15.1925 | -15.3538 | -0.13065 | -0.016938 | -0.091207 | -0.065154 | 122.3312 | 122.4132 | 122.0813 | 122.3119 | -15.1242 | -15.2102 | -15.213 | -15.1615 | -15.1671 | -15.1421 | -15.3035 | -0.080298 | 0.033416 | -0.040853 | -0.0148 | 122.3816 | 122.4636 | 122.1316 | 122.3622 | -122.4619 | -122.2119 | -122.4224 | -122.1725
1990.7188 | 122.5937 | -122.4747 | 0.032043 | -15.3439 | -15.4299 | -15.4327 | -15.3767 | -15.3915 | -15.3665 | -15.5232 | -0.13523 | -0.016938 | -0.091207 | -0.069733 | 122.3267 | 122.4087 | 122.0767 | 122.321 | -15.2936 | -15.3796 | -15.3824 | -15.3264 | -15.3411 | -15.3161 | -15.4729 | -0.084876 | 0.033416 | -0.040853 | -0.019379 | 122.377 | 122.459 | 122.1271 | 122.3714 | -122.4619 | -122.2119 | -122.4179 | -122.1679
1992.4062 | 122.6669 | -122.4426 | 0 | -15.3027 | -15.3887 | -15.3915 | -15.3263 | -15.3411 | -15.3161 | -15.4728 | -0.13523 | -0.012359 | -0.10036 | -0.074312 | 122.3267 | 122.4224 | 122.0813 | 122.3165 | -15.2524 | -15.3384 | -15.3412 | -15.276 | -15.2907 | -15.2658 | -15.4225 | -0.084876 | 0.037995 | -0.050009 | -0.023958 | 122.377 | 122.4727 | 122.1316 | 122.3668 | -122.4619 | -122.2165 | -122.427 | -122.1816
1994.0781 | 122.644 | -122.4518 | 0.022888 | -15.1608 | -15.2468 | -15.2542 | -15.189 | -15.2129 | -15.1788 | -15.3401 | -0.13981 | -0.021517 | -0.091207 | -0.069733 | 122.3267 | 122.4178 | 122.0813 | 122.3165 | -15.1105 | -15.1964 | -15.2038 | -15.1386 | -15.1626 | -15.1284 | -15.2897 | -0.089455 | 0.028837 | -0.040853 | -0.019379 | 122.377 | 122.4682 | 122.1316 | 122.3668 | -122.4665 | -122.2211 | -122.4179 | -122.1725
1995.7656 | 122.7219 | -122.4289 | 0.004578 | -15.4676 | -15.549 | -15.5564 | -15.5003 | -15.5151 | -15.4855 | -15.6514 | -0.13065 | -0.016938 | -0.095785 | -0.074312 | 122.3221 | 122.4178 | 122.0859 | 122.3165 | -15.4172 | -15.4986 | -15.506 | -15.45 | -15.4647 | -15.4352 | -15.601 | -0.080298 | 0.033416 | -0.045431 | -0.023958 | 122.3724 | 122.4682 | 122.1362 | 122.3668 | -122.4527 | -122.2165 | -122.4179 | -122.1816
1997.4531 | 122.6486 | -122.4701 | 0.018311 | -15.7102 | -15.7962 | -15.8036 | -15.7476 | -15.7577 | -15.7282 | -15.9032 | -0.13981 | -0.021517 | -0.091207 | -0.078891 | 122.3175 | 122.4132 | 122.0813 | 122.3165 | -15.6599 | -15.7459 | -15.7532 | -15.6972 | -15.7073 | -15.6778 | -15.8528 | -0.089455 | 0.028837 | -0.040853 | -0.028537 | 122.3679 | 122.4636 | 122.1316 | 122.3668 | -122.4573 | -122.2211 | -122.4087 | -122.1725
1999.1406 | 122.7264 | -122.4335 | -0.018311 | -15.8705 | -15.9656 | -15.9684 | -15.9078 | -15.9179 | -15.893 | -16.0634 | -0.13981 | -0.016938 | -0.086628 | -0.074312 | 122.3221 | 122.4132 | 122.0904 | 122.321 | -15.8201 | -15.9153 | -15.9181 | -15.8575 | -15.8676 | -15.8426 | -16.0131 | -0.089455 | 0.033416 | -0.036274 | -0.023958 | 122.3724 | 122.4636 | 122.1408 | 122.3714 | -122.4619 | -122.2302 | -122.4087 | -122.1771
2000.8594 | 122.7448 | -122.4518 | 0 | -15.9987 | -16.0984 | -16.0966 | -16.036 | -16.0507 | -16.0212 | -16.1962 | -0.13981 | -0.016938 | -0.086628 | -0.074312 | 122.3312 | 122.4132 | 122.0904 | 122.3256 | -15.9483 | -16.0481 | -16.0463 | -15.9857 | -16.0003 | -15.9708 | -16.1458 | -0.089455 | 0.033416 | -0.036274 | -0.023958 | 122.3816 | 122.4636 | 122.1408 | 122.376 | -122.4711 | -122.2302 | -122.4179 | -122.1771
2002.5469 | 122.6349 | -122.4655 | 0.009155 | -16.0444 | -16.1396 | -16.147 | -16.0818 | -16.0919 | -16.0715 | -16.2374 | -0.13523 | -0.016938 | -0.095785 | -0.074312 | 122.3267 | 122.4178 | 122.0859 | 122.321 | -15.9941 | -16.0893 | -16.0966 | -16.0314 | -16.0415 | -16.0212 | -16.187 | -0.084876 | 0.033416 | -0.045431 | -0.023958 | 122.377 | 122.4682 | 122.1362 | 122.3714 | -122.4619 | -122.2211 | -122.4224 | -122.1816
2004.2344 | 122.6761 | -122.4564 | 0.009155 | -15.7377 | -15.8283 | -15.8448 | -15.7796 | -15.7897 | -15.7694 | -15.9215 | -0.13981 | -0.021517 | -0.091207 | -0.069733 | 122.3358 | 122.4178 | 122.0859 | 122.321 | -15.6873 | -15.7779 | -15.7945 | -15.7293 | -15.7394 | -15.719 | -15.8712 | -0.089455 | 0.028837 | -0.040853 | -0.019379 | 122.3862 | 122.4682 | 122.1362 | 122.3714 | -122.4756 | -122.2257 | -122.427 | -122.1771
2005.9844 | 122.7081 | -122.4243 | 0.009155 | -15.6873 | -15.7733 | -15.7853 | -15.7201 | -15.7302 | -15.7144 | -15.8711 | -0.13981 | -0.021517 | -0.10036 | -0.069733 | 122.3312 | 122.4132 | 122.0859 | 122.321 | -15.637 | -15.723 | -15.7349 | -15.6697 | -15.6799 | -15.6641 | -15.8208 | -0.089455 | 0.028837 | -0.050009 | -0.019379 | 122.3816 | 122.4636 | 122.1362 | 122.3714 | -122.4711 | -122.2257 | -122.4316 | -122.1862
2007.6719 | 122.644 | -122.4747 | 0.036621 | -15.8293 | -15.929 | -15.9318 | -15.8712 | -15.8813 | -15.8564 | -16.0268 | -0.13981 | -0.00778 | -0.091207 | -0.074312 | 122.3404 | 122.4178 | 122.095 | 122.321 | -15.7789 | -15.8787 | -15.8814 | -15.8208 | -15.8309 | -15.806 | -15.9765 | -0.089455 | 0.042574 | -0.040853 | -0.023958 | 122.3908 | 122.4682 | 122.1454 | 122.3714 | -122.4802 | -122.2348 | -122.4316 | -122.1862
2009.375 | 122.6761 | -122.4426 | 0.004578 | -16.2734 | -16.3686 | -16.3759 | -16.3107 | -16.3208 | -16.2959 | -16.4709 | -0.13523 | -0.016938 | -0.091207 | -0.069733 | 122.3358 | 122.427 | 122.0904 | 122.3256 | -16.223 | -16.3182 | -16.3256 | -16.2604 | -16.2704 | -16.2455 | -16.4205 | -0.084876 | 0.033416 | -0.040853 | -0.019379 | 122.3862 | 122.4773 | 122.1408 | 122.376 | -122.4711 | -122.2257 | -122.427 | -122.1816
2011.1094 | 122.6761 | -122.438 | 0.018311 | -16.3329 | -16.4281 | -16.4263 | -16.3611 | -16.3711 | -16.3554 | -16.5304 | -0.13981 | -0.021517 | -0.091207 | -0.074312 | 122.3404 | 122.427 | 122.095 | 122.3165 | -16.2825 | -16.3778 | -16.3759 | -16.3107 | -16.3208 | -16.3051 | -16.4801 | -0.089455 | 0.028837 | -0.040853 | -0.023958 | 122.3908 | 122.4773 | 122.1454 | 122.3668 | -122.4802 | -122.2348 | -122.4316 | -122.1862
2012.8125 | 122.5983 | -122.4838 | 0.022888 | -16.3741 | -16.4739 | -16.4675 | -16.4023 | -16.4261 | -16.392 | -16.5625 | -0.13981 | -0.016938 | -0.091207 | -0.065154 | 122.3358 | 122.4224 | 122.0904 | 122.3256 | -16.3237 | -16.4235 | -16.4171 | -16.3519 | -16.3757 | -16.3417 | -16.5121 | -0.089455 | 0.033416 | -0.040853 | -0.0148 | 122.3862 | 122.4727 | 122.1408 | 122.376 | -122.4756 | -122.2302 | -122.427 | -122.1816
2014.5469 | 122.7264 | -122.4289 | -0.009155 | -16.4656 | -16.5655 | -16.5499 | -16.4984 | -16.5131 | -16.5019 | -16.6723 | -0.13981 | -0.016938 | -0.086628 | -0.074312 | 122.3358 | 122.427 | 122.095 | 122.3256 | -16.4153 | -16.5151 | -16.4996 | -16.4481 | -16.4627 | -16.4516 | -16.622 | -0.089455 | 0.033416 | -0.036274 | -0.023958 | 122.3862 | 122.4773 | 122.1454 | 122.376 | -122.4756 | -122.2348 | -122.4224 | -122.1816
2016.2344 | 122.7081 | -122.4426 | 0.009155 | -16.3603 | -16.4647 | -16.4538 | -16.3977 | -16.4352 | -16.4378 | -16.5899 | -0.13981 | -0.012359 | -0.095785 | -0.069733 | 122.345 | 122.4224 | 122.095 | 122.3256 | -16.31 | -16.4144 | -16.4034 | -16.3474 | -16.3849 | -16.3875 | -16.5396 | -0.089455 | 0.037995 | -0.045431 | -0.019379 | 122.3953 | 122.4727 | 122.1454 | 122.376 | -122.4848 | -122.2348 | -122.4408 | -122.1908
2018 | 122.6074 | -122.4976 | 0.013733 | -16.5618 | -16.6754 | -16.6598 | -16.5992 | -16.6458 | -16.653 | -16.8097 | -0.14439 | -0.012359 | -0.091207 | -0.069733 | 122.3358 | 122.4315 | 122.1042 | 122.321 | -16.5114 | -16.625 | -16.6094 | -16.5488 | -16.5955 | -16.6026 | -16.7593 | -0.094033 | 0.037995 | -0.040853 | -0.019379 | 122.3862 | 122.4819 | 122.1545 | 122.3714 | -122.4802 | -122.2486 | -122.427 | -122.1954
2019.6875 | 122.6532 | -122.4792 | 0.004578 | -16.4977 | -16.6113 | -16.5911 | -16.5305 | -16.5817 | -16.5843 | -16.7364 | -0.14439 | -0.021517 | -0.086628 | -0.074312 | 122.3358 | 122.4224 | 122.095 | 122.3256 | -16.4473 | -16.5609 | -16.5408 | -16.4801 | -16.5314 | -16.534 | -16.6861 | -0.094033 | 0.028837 | -0.036274 | -0.023958 | 122.3862 | 122.4727 | 122.1454 | 122.376 | -122.4802 | -122.2394 | -122.4224 | -122.1816
2021.3906 | 122.7219 | -122.4289 | -0.009155 | -16.1589 | -16.2724 | -16.2477 | -16.1917 | -16.2384 | -16.2455 | -16.3793 | -0.13523 | -0.016938 | -0.086628 | -0.069733 | 122.345 | 122.427 | 122.095 | 122.3302 | -16.1085 | -16.2221 | -16.1974 | -16.1413 | -16.188 | -16.1952 | -16.329 | -0.084876 | 0.033416 | -0.036274 | -0.019379 | 122.3953 | 122.4773 | 122.1454 | 122.3805 | -122.4802 | -122.2302 | -122.4316 | -122.1816
2023.125 | 122.7402 | -122.4335 | 0.018311 | -16.2459 | -16.3594 | -16.3485 | -16.2833 | -16.3254 | -16.3371 | -16.48 | -0.13981 | -0.012359 | -0.095785 | -0.065154 | 122.345 | 122.4315 | 122.0996 | 122.3256 | -16.1955 | -16.3091 | -16.2981 | -16.2329 | -16.275 | -16.2867 | -16.4297 | -0.089455 | 0.037995 | -0.045431 | -0.0148 | 122.3953 | 122.4819 | 122.1499 | 122.376 | -122.4848 | -122.2394 | -122.4408 | -122.1954
2024.8125 | 122.6074 | -122.4976 | 0.036621 | -16.2413 | -16.3503 | -16.3439 | -16.2787 | -16.3345 | -16.3279 | -16.4709 | -0.13981 | -0.016938 | -0.091207 | -0.074312 | 122.3358 | 122.4315 | 122.095 | 122.3302 | -16.191 | -16.2999 | -16.2935 | -16.2283 | -16.2842 | -16.2776 | -16.4205 | -0.089455 | 0.033416 | -0.040853 | -0.023958 | 122.3862 | 122.4819 | 122.1454 | 122.3805 | -122.4756 | -122.2348 | -122.427 | -122.1862
2026.5156 | 122.6898 | -122.4518 | 0.013733 | -16.3375 | -16.4418 | -16.44 | -16.3611 | -16.4215 | -16.4241 | -16.5625 | -0.13523 | -0.016938 | -0.095785 | -0.069733 | 122.3404 | 122.4361 | 122.0996 | 122.3394 | -16.2871 | -16.3915 | -16.3897 | -16.3107 | -16.3711 | -16.3737 | -16.5121 | -0.084876 | 0.033416 | -0.045431 | -0.019379 | 122.3908 | 122.4865 | 122.1499 | 122.3897 | -122.4756 | -122.2348 | -122.4362 | -122.1954
2028.2188 | 122.7676 | -122.4609 | 0.004578 | -16.4199 | -16.5426 | -16.5179 | -16.4618 | -16.5085 | -16.5065 | -16.654 | -0.13981 | -0.012359 | -0.091207 | -0.074312 | 122.345 | 122.4361 | 122.0996 | 122.3302 | -16.3695 | -16.4922 | -16.4675 | -16.4115 | -16.4581 | -16.4561 | -16.6037 | -0.089455 | 0.037995 | -0.040853 | -0.023958 | 122.3953 | 122.4865 | 122.1499 | 122.3805 | -122.4848 | -122.2394 | -122.4362 | -122.1908
2029.9531 | 122.7356 | -122.4472 | 0.004578 | -16.4656 | -16.5792 | -16.5682 | -16.503 | -16.5588 | -16.5431 | -16.6998 | -0.13065 | -0.012359 | -0.091207 | -0.078891 | 122.3496 | 122.4361 | 122.1042 | 122.3394 | -16.4153 | -16.5289 | -16.5179 | -16.4527 | -16.5085 | -16.4928 | -16.6494 | -0.080298 | 0.037995 | -0.040853 | -0.028537 | 122.3999 | 122.4865 | 122.1545 | 122.3897 | -122.4802 | -122.2348 | -122.4408 | -122.1954
2031.6406 | 122.7036 | -122.4838 | 0.036621 | -16.5664 | -16.6845 | -16.6644 | -16.6037 | -16.6458 | -16.6438 | -16.7959 | -0.13981 | -0.016938 | -0.086628 | -0.069733 | 122.3541 | 122.4361 | 122.1087 | 122.3302 | -16.516 | -16.6342 | -16.614 | -16.5534 | -16.5955 | -16.5935 | -16.7456 | -0.089455 | 0.033416 | -0.036274 | -0.019379 | 122.4045 | 122.4865 | 122.1591 | 122.3805 | -122.4939 | -122.2486 | -122.4408 | -122.1954
2033.3594 | 122.6944 | -122.4335 | 0.022888 | -16.8136 | -16.9318 | -16.9162 | -16.851 | -16.893 | -16.8957 | -17.0615 | -0.13523 | -0.016938 | -0.095785 | -0.069733 | 122.3496 | 122.4361 | 122.095 | 122.3348 | -16.7633 | -16.8814 | -16.8658 | -16.8006 | -16.8427 | -16.8453 | -17.0111 | -0.084876 | 0.033416 | -0.045431 | -0.019379 | 122.3999 | 122.4865 | 122.1454 | 122.3851 | -122.4848 | -122.2302 | -122.4453 | -122.1908
2035.0469 | 122.644 | -122.4792 | 0.013733 | -16.8411 | -16.9547 | -16.9437 | -16.8785 | -16.9113 | -16.9185 | -17.0706 | -0.13981 | -0.016938 | -0.095785 | -0.065154 | 122.3496 | 122.4361 | 122.0996 | 122.3394 | -16.7907 | -16.9043 | -16.8933 | -16.8281 | -16.861 | -16.8682 | -17.0203 | -0.089455 | 0.033416 | -0.045431 | -0.0148 | 122.3999 | 122.4865 | 122.1499 | 122.3897 | -122.4894 | -122.2394 | -122.4453 | -122.1954
2036.7188 | 122.731 | -122.4472 | 0.004578 | -16.9006 | -17.0096 | -16.994 | -16.9288 | -16.98 | -16.9826 | -17.1256 | -0.13981 | -0.021517 | -0.091207 | -0.074312 | 122.3496 | 122.4315 | 122.1087 | 122.3394 | -16.8502 | -16.9593 | -16.9437 | -16.8785 | -16.9297 | -16.9323 | -17.0752 | -0.089455 | 0.028837 | -0.040853 | -0.023958 | 122.3999 | 122.4819 | 122.1591 | 122.3897 | -122.4894 | -122.2486 | -122.4408 | -122.2
2038.4688 | 122.7585 | -122.4701 | 0.009155 | -17.1753 | -17.2843 | -17.2688 | -17.2173 | -17.2455 | -17.2528 | -17.4094 | -0.13981 | -0.021517 | -0.10494 | -0.065154 | 122.345 | 122.4361 | 122.1042 | 122.3394 | -17.1249 | -17.234 | -17.2184 | -17.1669 | -17.1952 | -17.2024 | -17.3591 | -0.089455 | 0.028837 | -0.054588 | -0.0148 | 122.3953 | 122.4865 | 122.1545 | 122.3897 | -122.4848 | -122.244 | -122.4499 | -122.2091
2040.25 | 122.7402 | -122.4564 | 0.013733 | -17.2714 | -17.3851 | -17.3649 | -17.3134 | -17.3508 | -17.3535 | -17.5101 | -0.13523 | -0.016938 | -0.086628 | -0.078891 | 122.3496 | 122.4361 | 122.1087 | 122.3439 | -17.2211 | -17.3347 | -17.3145 | -17.2631 | -17.3005 | -17.3031 | -17.4598 | -0.084876 | 0.033416 | -0.036274 | -0.028537 | 122.3999 | 122.4865 | 122.1591 | 122.3943 | -122.4848 | -122.244 | -122.4362 | -122.1954
2041.9531 | 122.6761 | -122.4838 | 0.022888 | -17.276 | -17.3988 | -17.3786 | -17.3134 | -17.3646 | -17.3627 | -17.5239 | -0.13523 | -0.012359 | -0.091207 | -0.069733 | 122.3496 | 122.4499 | 122.1042 | 122.3439 | -17.2257 | -17.3485 | -17.3283 | -17.2631 | -17.3142 | -17.3123 | -17.4735 | -0.084876 | 0.037995 | -0.040853 | -0.019379 | 122.3999 | 122.5002 | 122.1545 | 122.3943 | -122.4848 | -122.2394 | -122.4408 | -122.1954
2043.7031 | 122.6166 | -122.5159 | 0.027466 | -17.1387 | -17.2431 | -17.2321 | -17.1669 | -17.2181 | -17.2207 | -17.3591 | -0.13523 | -0.016938 | -0.091207 | -0.074312 | 122.3633 | 122.4407 | 122.1087 | 122.3439 | -17.0883 | -17.1928 | -17.1818 | -17.1165 | -17.1677 | -17.1704 | -17.3087 | -0.084876 | 0.033416 | -0.040853 | -0.023958 | 122.4136 | 122.4911 | 122.1591 | 122.3943 | -122.4985 | -122.244 | -122.4545 | -122.2
2045.4531 | 122.6944 | -122.4701 | -0.009155 | -17.2898 | -17.3942 | -17.3832 | -17.318 | -17.3646 | -17.3672 | -17.5193 | -0.13523 | -0.012359 | -0.091207 | -0.069733 | 122.3587 | 122.4361 | 122.1087 | 122.3439 | -17.2394 | -17.3439 | -17.3329 | -17.2676 | -17.3142 | -17.3169 | -17.4689 | -0.084876 | 0.037995 | -0.040853 | -0.019379 | 122.4091 | 122.4865 | 122.1591 | 122.3943 | -122.4939 | -122.244 | -122.4499 | -122.2
2047.1406 | 122.7493 | -122.4655 | 0.013733 | -17.2577 | -17.3713 | -17.3512 | -17.2951 | -17.3508 | -17.3443 | -17.4964 | -0.14439 | -0.016938 | -0.091207 | -0.069733 | 122.3587 | 122.4407 | 122.1133 | 122.3439 | -17.2074 | -17.321 | -17.3008 | -17.2447 | -17.3005 | -17.294 | -17.446 | -0.094033 | 0.033416 | -0.040853 | -0.019379 | 122.4091 | 122.4911 | 122.1637 | 122.3943 | -122.5031 | -122.2577 | -122.4499 | -122.2045
2048.875 | 122.6212 | -122.5204 | 0.027466 | -17.3447 | -17.4675 | -17.4473 | -17.3958 | -17.4378 | -17.4359 | -17.5925 | -0.13523 | -0.016938 | -0.08205 | -0.078891 | 122.3541 | 122.4499 | 122.1179 | 122.3394 | -17.2943 | -17.4171 | -17.397 | -17.3455 | -17.3874 | -17.3856 | -17.5422 | -0.084876 | 0.033416 | -0.031696 | -0.028537 | 122.4045 | 122.5002 | 122.1683 | 122.3897 | -122.4894 | -122.2531 | -122.4362 | -122.2
2050.625 | 122.6578 | -122.4701 | 0.013733 | -17.2623 | -17.3713 | -17.3603 | -17.2951 | -17.3417 | -17.3489 | -17.501 | -0.13523 | -0.012359 | -0.095785 | -0.065154 | 122.3587 | 122.4453 | 122.1042 | 122.3394 | -17.2119 | -17.321 | -17.31 | -17.2447 | -17.2913 | -17.2986 | -17.4506 | -0.084876 | 0.037995 | -0.045431 | -0.0148 | 122.4091 | 122.4956 | 122.1545 | 122.3897 | -122.4939 | -122.2394 | -122.4545 | -122.2
2052.375 | 122.6166 | -122.525 | 0.032043 | -17.3127 | -17.4263 | -17.4107 | -17.3546 | -17.3966 | -17.3947 | -17.5513 | -0.13981 | -0.012359 | -0.091207 | -0.074312 | 122.3587 | 122.4499 | 122.1133 | 122.3439 | -17.2623 | -17.3759 | -17.3603 | -17.3043 | -17.3462 | -17.3443 | -17.501 | -0.089455 | 0.037995 | -0.040853 | -0.023958 | 122.4091 | 122.5002 | 122.1637 | 122.3943 | -122.4985 | -122.2531 | -122.4499 | -122.2045
2054.0469 | 122.6166 | -122.5067 | 0.036621 | -17.4408 | -17.5316 | -17.5435 | -17.4782 | -17.4973 | -17.4634 | -17.6383 | -0.13981 | -0.021517 | -0.091207 | -0.069733 | 122.3587 | 122.4407 | 122.1087 | 122.3485 | -17.3905 | -17.4812 | -17.4931 | -17.4279 | -17.447 | -17.413 | -17.588 | -0.089455 | 0.028837 | -0.040853 | -0.019379 | 122.4091 | 122.4911 | 122.1591 | 122.3989 | -122.4985 | -122.2486 | -122.4499 | -122.2
2055.7812 | 122.6212 | -122.5113 | 0.041199 | -17.4454 | -17.5362 | -17.5435 | -17.4828 | -17.5019 | -17.4634 | -17.6475 | -0.13981 | -0.012359 | -0.086628 | -0.065154 | 122.3633 | 122.4453 | 122.1133 | 122.3439 | -17.3951 | -17.4858 | -17.4931 | -17.4325 | -17.4515 | -17.413 | -17.5971 | -0.089455 | 0.037995 | -0.036274 | -0.0148 | 122.4136 | 122.4956 | 122.1637 | 122.3943 | -122.5031 | -122.2531 | -122.4499 | -122.2
2057.5312 | 122.6852 | -122.4564 | 0.009155 | -17.2989 | -17.4034 | -17.4015 | -17.3455 | -17.36 | -17.3214 | -17.5101 | -0.14439 | -0.012359 | -0.086628 | -0.074312 | 122.3679 | 122.4499 | 122.1179 | 122.3485 | -17.2486 | -17.353 | -17.3512 | -17.2951 | -17.3096 | -17.2711 | -17.4598 | -0.094033 | 0.037995 | -0.036274 | -0.023958 | 122.4182 | 122.5002 | 122.1683 | 122.3989 | -122.5123 | -122.2623 | -122.4545 | -122.2045
2059.2188 | 122.6898 | -122.4701 | 0.027466 | -17.5553 | -17.6552 | -17.6579 | -17.5973 | -17.6118 | -17.587 | -17.7574 | -0.13523 | -0.012359 | -0.086628 | -0.065154 | 122.3633 | 122.459 | 122.1179 | 122.3531 | -17.505 | -17.6049 | -17.6076 | -17.5469 | -17.5614 | -17.5366 | -17.707 | -0.084876 | 0.037995 | -0.036274 | -0.0148 | 122.4136 | 122.5094 | 122.1683 | 122.4034 | -122.4985 | -122.2531 | -122.4499 | -122.2045
2060.9688 | 122.612 | -122.5021 | 0.022888 | -17.8346 | -17.9208 | -17.9326 | -17.872 | -17.8819 | -17.848 | -18.0412 | -0.13981 | -0.00778 | -0.091207 | -0.08347 | 122.3633 | 122.4499 | 122.1179 | 122.3485 | -17.7842 | -17.8704 | -17.8823 | -17.8216 | -17.8315 | -17.7976 | -17.9909 | -0.089455 | 0.042574 | -0.040853 | -0.033116 | 122.4136 | 122.5002 | 122.1683 | 122.3989 | -122.5031 | -122.2577 | -122.4545 | -122.2091
2062.7188 | 122.644 | -122.5021 | 0.045776 | -17.917 | -18.0124 | -18.0105 | -17.9315 | -17.9597 | -17.935 | -18.1099 | -0.13981 | -0.021517 | -0.095785 | -0.069733 | 122.3633 | 122.4544 | 122.1225 | 122.3531 | -17.8666 | -17.962 | -17.9601 | -17.8812 | -17.9093 | -17.8846 | -18.0595 | -0.089455 | 0.028837 | -0.045431 | -0.019379 | 122.4136 | 122.5048 | 122.1728 | 122.4034 | -122.5031 | -122.2623 | -122.4591 | -122.2183
2064.4688 | 122.6166 | -122.4976 | 0.036621 | -18.0086 | -18.1131 | -18.1112 | -18.0506 | -18.0696 | -18.0265 | -18.2152 | -0.13981 | -0.021517 | -0.086628 | -0.065154 | 122.3633 | 122.4544 | 122.1271 | 122.3577 | -17.9582 | -18.0628 | -18.0609 | -18.0002 | -18.0192 | -17.9762 | -18.1648 | -0.089455 | 0.028837 | -0.036274 | -0.0148 | 122.4136 | 122.5048 | 122.1774 | 122.408 | -122.5031 | -122.2669 | -122.4499 | -122.2137
2066.1406 | 122.7631 | -122.4609 | 0.009155 | -18.0543 | -18.1406 | -18.1433 | -18.0872 | -18.1108 | -18.0677 | -18.2564 | -0.13065 | -0.016938 | -0.091207 | -0.065154 | 122.3679 | 122.4499 | 122.1179 | 122.3439 | -18.004 | -18.0902 | -18.0929 | -18.0368 | -18.0604 | -18.0174 | -18.206 | -0.080298 | 0.033416 | -0.040853 | -0.0148 | 122.4182 | 122.5002 | 122.1683 | 122.3943 | -122.4985 | -122.2486 | -122.4591 | -122.2091
2067.875 | 122.6395 | -122.5021 | 0.041199 | -18.2421 | -18.3421 | -18.3447 | -18.2657 | -18.2939 | -18.2692 | -18.4532 | -0.13523 | -0.016938 | -0.091207 | -0.065154 | 122.3679 | 122.459 | 122.1179 | 122.3531 | -18.1917 | -18.2917 | -18.2944 | -18.2154 | -18.2435 | -18.2188 | -18.4029 | -0.084876 | 0.033416 | -0.040853 | -0.0148 | 122.4182 | 122.5094 | 122.1683 | 122.4034 | -122.5031 | -122.2531 | -122.4591 | -122.2091
2069.625 | 122.6349 | -122.5159 | 0.032043 | -18.0269 | -18.1314 | -18.1387 | -18.0734 | -18.0879 | -18.054 | -18.2426 | -0.13523 | -0.016938 | -0.091207 | -0.069733 | 122.377 | 122.459 | 122.1225 | 122.3439 | -17.9765 | -18.0811 | -18.0883 | -18.0231 | -18.0375 | -18.0036 | -18.1923 | -0.084876 | 0.033416 | -0.040853 | -0.019379 | 122.4274 | 122.5094 | 122.1728 | 122.3943 | -122.5123 | -122.2577 | -122.4682 | -122.2137
2071.3125 | 122.6761 | -122.4701 | 0.032043 | -18.2192 | -18.31 | -18.3035 | -18.2566 | -18.2801 | -18.2371 | -18.4258 | -0.13981 | -0.016938 | -0.086628 | -0.069733 | 122.3679 | 122.4544 | 122.1179 | 122.3577 | -18.1688 | -18.2596 | -18.2532 | -18.2062 | -18.2298 | -18.1868 | -18.3754 | -0.089455 | 0.033416 | -0.036274 | -0.019379 | 122.4182 | 122.5048 | 122.1683 | 122.408 | -122.5077 | -122.2577 | -122.4545 | -122.2045
2073.125 | 122.7173 | -122.4472 | -0.013733 | -18.2466 | -18.3329 | -18.3447 | -18.2841 | -18.2847 | -18.2646 | -18.4395 | -0.13981 | -0.012359 | -0.086628 | -0.069733 | 122.3724 | 122.4544 | 122.1225 | 122.3577 | -18.1963 | -18.2825 | -18.2944 | -18.2337 | -18.2344 | -18.2142 | -18.3892 | -0.089455 | 0.037995 | -0.036274 | -0.019379 | 122.4228 | 122.5048 | 122.1728 | 122.408 | -122.5123 | -122.2623 | -122.4591 | -122.2091
2074.8281 | 122.7859 | -122.4792 | 0.013733 | -18.5168 | -18.6122 | -18.624 | -18.5588 | -18.5777 | -18.5393 | -18.7279 | -0.13981 | -0.012359 | -0.10036 | -0.060575 | 122.3724 | 122.459 | 122.1225 | 122.3668 | -18.4664 | -18.5618 | -18.5737 | -18.5084 | -18.5274 | -18.4889 | -18.6776 | -0.089455 | 0.037995 | -0.050009 | -0.010221 | 122.4228 | 122.5094 | 122.1728 | 122.4172 | -122.5123 | -122.2623 | -122.4728 | -122.2228
2076.5469 | 122.6486 | -122.5021 | 0.032043 | -18.3336 | -18.4199 | -18.4317 | -18.3482 | -18.3671 | -18.3562 | -18.5356 | -0.13523 | -0.012359 | -0.095785 | -0.069733 | 122.3679 | 122.4544 | 122.1225 | 122.3577 | -18.2833 | -18.3695 | -18.3814 | -18.2978 | -18.3168 | -18.3058 | -18.4853 | -0.084876 | 0.037995 | -0.045431 | -0.019379 | 122.4182 | 122.5048 | 122.1728 | 122.408 | -122.5031 | -122.2577 | -122.4637 | -122.2183
2078.2344 | 122.7676 | -122.4518 | 0 | -18.3382 | -18.4291 | -18.4409 | -18.3527 | -18.3763 | -18.3607 | -18.5402 | -0.13981 | -0.016938 | -0.091207 | -0.069733 | 122.377 | 122.4544 | 122.1225 | 122.3531 | -18.2879 | -18.3787 | -18.3905 | -18.3024 | -18.3259 | -18.3104 | -18.4899 | -0.089455 | 0.033416 | -0.040853 | -0.019379 | 122.4274 | 122.5048 | 122.1728 | 122.4034 | -122.5168 | -122.2623 | -122.4682 | -122.2137
2079.9062 | 122.7493 | -122.4564 | 0.013733 | -17.8621 | -17.9529 | -17.9693 | -17.8766 | -17.9048 | -17.8892 | -18.0595 | -0.13981 | -0.012359 | -0.091207 | -0.065154 | 122.3724 | 122.4682 | 122.1316 | 122.3622 | -17.8117 | -17.9025 | -17.9189 | -17.8262 | -17.8544 | -17.8388 | -18.0092 | -0.089455 | 0.037995 | -0.040853 | -0.0148 | 122.4228 | 122.5185 | 122.182 | 122.4126 | -122.5123 | -122.2714 | -122.4637 | -122.2228
2081.5938 | 122.6807 | -122.493 | 0 | -18.1734 | -18.2642 | -18.2715 | -18.1879 | -18.2115 | -18.1959 | -18.38 | -0.12607 | -0.00778 | -0.086628 | -0.074312 | 122.3816 | 122.459 | 122.1271 | 122.3622 | -18.123 | -18.2139 | -18.2211 | -18.1376 | -18.1611 | -18.1456 | -18.3296 | -0.075719 | 0.042574 | -0.036274 | -0.023958 | 122.432 | 122.5094 | 122.1774 | 122.4126 | -122.5077 | -122.2531 | -122.4682 | -122.2137
2083.2812 | 122.7036 | -122.4838 | 0.018311 | -18.1139 | -18.1955 | -18.2165 | -18.1421 | -18.152 | -18.1364 | -18.3205 | -0.13981 | -0.016938 | -0.086628 | -0.065154 | 122.3724 | 122.4682 | 122.1316 | 122.3622 | -18.0635 | -18.1452 | -18.1662 | -18.0918 | -18.1016 | -18.086 | -18.2701 | -0.089455 | 0.033416 | -0.036274 | -0.0148 | 122.4228 | 122.5185 | 122.182 | 122.4126 | -122.5123 | -122.2714 | -122.4591 | -122.2183
2085 | 122.6807 | -122.4976 | 0.009155 | -18.0681 | -18.1543 | -18.1662 | -18.0826 | -18.1108 | -18.0952 | -18.261 | -0.13523 | -0.00778 | -0.091207 | -0.074312 | 122.3724 | 122.4682 | 122.1316 | 122.3577 | -18.0177 | -18.104 | -18.1158 | -18.0322 | -18.0604 | -18.0448 | -18.2106 | -0.084876 | 0.042574 | -0.040853 | -0.023958 | 122.4228 | 122.5185 | 122.182 | 122.408 | -122.5077 | -122.2669 | -122.4637 | -122.2228
2086.7031 | 122.7768 | -122.4472 | -0.004578 | -18.1001 | -18.1818 | -18.2028 | -18.1192 | -18.1428 | -18.1227 | -18.3022 | -0.13981 | -0.00778 | -0.091207 | -0.069733 | 122.377 | 122.459 | 122.1271 | 122.3622 | -18.0498 | -18.1314 | -18.1524 | -18.0689 | -18.0925 | -18.0723 | -18.2518 | -0.089455 | 0.042574 | -0.040853 | -0.019379 | 122.4274 | 122.5094 | 122.1774 | 122.4126 | -122.5168 | -122.2669 | -122.4682 | -122.2183
2088.4531 | 122.6807 | -122.5113 | 0.018311 | -17.9994 | -18.0719 | -18.0975 | -18.0185 | -18.0375 | -18.0219 | -18.2014 | -0.13523 | -0.012359 | -0.086628 | -0.074312 | 122.377 | 122.4727 | 122.1316 | 122.3714 | -17.9491 | -18.0215 | -18.0471 | -17.9681 | -17.9872 | -17.9716 | -18.1511 | -0.084876 | 0.037995 | -0.036274 | -0.023958 | 122.4274 | 122.5231 | 122.182 | 122.4218 | -122.5123 | -122.2669 | -122.4637 | -122.2183
2090.1562 | 122.7493 | -122.4976 | -0.013733 | -17.9353 | -18.017 | -18.038 | -17.9498 | -17.9734 | -17.9578 | -18.1373 | -0.13523 | -0.016938 | -0.091207 | -0.078891 | 122.377 | 122.4727 | 122.1362 | 122.3714 | -17.885 | -17.9666 | -17.9876 | -17.8995 | -17.9231 | -17.9075 | -18.087 | -0.084876 | 0.033416 | -0.040853 | -0.028537 | 122.4274 | 122.5231 | 122.1866 | 122.4218 | -122.5123 | -122.2714 | -122.4682 | -122.2274
2091.8594 | 122.7539 | -122.4792 | 0.022888 | -18.0315 | -18.1085 | -18.1204 | -18.0368 | -18.0696 | -18.0494 | -18.2243 | -0.13065 | -0.012359 | -0.08205 | -0.074312 | 122.3816 | 122.4727 | 122.1362 | 122.3622 | -17.9811 | -18.0582 | -18.07 | -17.9865 | -18.0192 | -17.9991 | -18.174 | -0.080298 | 0.037995 | -0.031696 | -0.023958 | 122.432 | 122.5231 | 122.1866 | 122.4126 | -122.5123 | -122.2669 | -122.4637 | -122.2183
2093.5625 | 122.7859 | -122.4655 | 0.009155 | -18.1825 | -18.2596 | -18.2715 | -18.1925 | -18.2161 | -18.2097 | -18.38 | -0.13523 | -0.012359 | -0.086628 | -0.060575 | 122.3724 | 122.4727 | 122.1362 | 122.3668 | -18.1322 | -18.2093 | -18.2211 | -18.1421 | -18.1657 | -18.1593 | -18.3296 | -0.084876 | 0.037995 | -0.036274 | -0.010221 | 122.4228 | 122.5231 | 122.1866 | 122.4172 | -122.5077 | -122.2714 | -122.4591 | -122.2228
2095.25 | 122.699 | -122.5113 | 0.032043 | -18.1688 | -18.2551 | -18.2715 | -18.1833 | -18.2023 | -18.1868 | -18.3663 | -0.13523 | -0.00778 | -0.091207 | -0.078891 | 122.3862 | 122.4727 | 122.1316 | 122.3714 | -18.1185 | -18.2047 | -18.2211 | -18.133 | -18.152 | -18.1364 | -18.3159 | -0.084876 | 0.042574 | -0.040853 | -0.028537 | 122.4365 | 122.5231 | 122.182 | 122.4218 | -122.5214 | -122.2669 | -122.4774 | -122.2228
2096.9375 | 122.7722 | -122.4655 | 0 | -18.3291 | -18.4107 | -18.4317 | -18.3482 | -18.358 | -18.3516 | -18.5311 | -0.13523 | -0.00778 | -0.091207 | -0.065154 | 122.3816 | 122.4773 | 122.1362 | 122.3668 | -18.2787 | -18.3604 | -18.3814 | -18.2978 | -18.3076 | -18.3012 | -18.4807 | -0.084876 | 0.042574 | -0.040853 | -0.0148 | 122.432 | 122.5277 | 122.1866 | 122.4172 | -122.5168 | -122.2714 | -122.4728 | -122.2274
2098.625 | 122.7493 | -122.4609 | -0.009155 | -18.4527 | -18.5252 | -18.5599 | -18.458 | -18.4816 | -18.4752 | -18.6501 | -0.13523 | -0.012359 | -0.08205 | -0.069733 | 122.3908 | 122.4773 | 122.1362 | 122.376 | -18.4023 | -18.4749 | -18.5096 | -18.4077 | -18.4312 | -18.4248 | -18.5997 | -0.084876 | 0.037995 | -0.031696 | -0.019379 | 122.4411 | 122.5277 | 122.1866 | 122.4263 | -122.526 | -122.2714 | -122.4728 | -122.2183
2100.2969 | 122.7081 | -122.493 | 0.036621 | -18.0727 | -18.1452 | -18.1662 | -18.078 | -18.1062 | -18.0998 | -18.2747 | -0.13981 | -0.00778 | -0.08205 | -0.074312 | 122.3862 | 122.4727 | 122.1408 | 122.3668 | -18.0223 | -18.0948 | -18.1158 | -18.0277 | -18.0558 | -18.0494 | -18.2243 | -0.089455 | 0.042574 | -0.031696 | -0.023958 | 122.4365 | 122.5231 | 122.1911 | 122.4172 | -122.526 | -122.2806 | -122.4682 | -122.2228
2102.0156 | 122.7448 | -122.4884 | 0.004578 | -18.4389 | -18.5115 | -18.5324 | -18.4443 | -18.4678 | -18.4615 | -18.6364 | -0.13523 | -0.016938 | -0.091207 | -0.074312 | 122.3908 | 122.4773 | 122.1454 | 122.3714 | -18.3886 | -18.4611 | -18.4821 | -18.3939 | -18.4175 | -18.4111 | -18.586 | -0.084876 | 0.033416 | -0.040853 | -0.023958 | 122.4411 | 122.5277 | 122.1957 | 122.4218 | -122.526 | -122.2806 | -122.482 | -122.2366
2103.75 | 122.6715 | -122.5159 | 0.032043 | -18.3703 | -18.4428 | -18.4821 | -18.3756 | -18.3946 | -18.3836 | -18.5631 | -0.13065 | -0.012359 | -0.091207 | -0.074312 | 122.377 | 122.4773 | 122.1362 | 122.376 | -18.3199 | -18.3924 | -18.4317 | -18.3253 | -18.3442 | -18.3333 | -18.5128 | -0.080298 | 0.037995 | -0.040853 | -0.023958 | 122.4274 | 122.5277 | 122.1866 | 122.4263 | -122.5077 | -122.2669 | -122.4682 | -122.2274
2105.4375 | 122.7448 | -122.4792 | 0.022888 | -18.4069 | -18.484 | -18.5096 | -18.4077 | -18.4312 | -18.4248 | -18.5906 | -0.14439 | -0.012359 | -0.091207 | -0.074312 | 122.3862 | 122.4727 | 122.1362 | 122.3714 | -18.3565 | -18.4336 | -18.4592 | -18.3573 | -18.3809 | -18.3745 | -18.5402 | -0.094033 | 0.037995 | -0.040853 | -0.023958 | 122.4365 | 122.5231 | 122.1866 | 122.4218 | -122.5306 | -122.2806 | -122.4774 | -122.2274
2107.1406 | 122.7631 | -122.4426 | 0.009155 | -18.59 | -18.6671 | -18.6927 | -18.6045 | -18.6189 | -18.6126 | -18.7783 | -0.13065 | -0.016938 | -0.091207 | -0.069733 | 122.3816 | 122.4727 | 122.1408 | 122.3714 | -18.5397 | -18.6168 | -18.6423 | -18.5542 | -18.5686 | -18.5622 | -18.7279 | -0.080298 | 0.033416 | -0.040853 | -0.019379 | 122.432 | 122.5231 | 122.1911 | 122.4218 | -122.5123 | -122.2714 | -122.4728 | -122.232
2108.8906 | 122.6761 | -122.5388 | 0.032043 | -18.7182 | -18.7954 | -18.8301 | -18.7327 | -18.7471 | -18.7407 | -18.9156 | -0.13523 | -0.012359 | -0.086628 | -0.069733 | 122.3816 | 122.4727 | 122.1408 | 122.3714 | -18.6679 | -18.745 | -18.7797 | -18.6824 | -18.6967 | -18.6904 | -18.8653 | -0.084876 | 0.037995 | -0.036274 | -0.019379 | 122.432 | 122.5231 | 122.1911 | 122.4218 | -122.5168 | -122.276 | -122.4682 | -122.2274
2110.5625 | 122.7356 | -122.5113 | 0.004578 | -18.8968 | -18.9831 | -19.0224 | -18.925 | -18.9302 | -18.9285 | -19.0942 | -0.13981 | -0.012359 | -0.08205 | -0.074312 | 122.3862 | 122.4773 | 122.1408 | 122.376 | -18.8464 | -18.9327 | -18.972 | -18.8747 | -18.8799 | -18.8781 | -19.0438 | -0.089455 | 0.037995 | -0.031696 | -0.023958 | 122.4365 | 122.5277 | 122.1911 | 122.4263 | -122.526 | -122.2806 | -122.4682 | -122.2228
2112.2812 | 122.7402 | -122.4976 | 0.022888 | -18.9059 | -18.9922 | -19.0224 | -18.9342 | -18.9394 | -18.9285 | -19.1033 | -0.13065 | -0.016938 | -0.086628 | -0.069733 | 122.3953 | 122.4773 | 122.1454 | 122.3806 | -18.8556 | -18.9419 | -18.972 | -18.8838 | -18.889 | -18.8781 | -19.053 | -0.080298 | 0.033416 | -0.036274 | -0.019379 | 122.4457 | 122.5277 | 122.1957 | 122.4309 | -122.526 | -122.276 | -122.482 | -122.232
2113.9688 | 122.7036 | -122.5296 | 0.032043 | -19.5744 | -19.6699 | -19.7091 | -19.6118 | -19.6078 | -19.5923 | -19.7763 | -0.13065 | -0.021517 | -0.095785 | -0.074312 | 122.3908 | 122.4819 | 122.1408 | 122.376 | -19.524 | -19.6196 | -19.6588 | -19.5615 | -19.5574 | -19.542 | -19.726 | -0.080298 | 0.028837 | -0.045431 | -0.023958 | 122.4411 | 122.5323 | 122.1911 | 122.4263 | -122.5214 | -122.2714 | -122.4865 | -122.2366
2115.7031 | 122.7859 | -122.4747 | 0.018311 | -19.405 | -19.4868 | -19.5214 | -19.4333 | -19.4338 | -19.4183 | -19.5978 | -0.13523 | -0.00778 | -0.086628 | -0.074312 | 122.3908 | 122.4865 | 122.1454 | 122.376 | -19.3546 | -19.4364 | -19.4711 | -19.3829 | -19.3834 | -19.368 | -19.5474 | -0.084876 | 0.042574 | -0.036274 | -0.023958 | 122.4411 | 122.5368 | 122.1957 | 122.4263 | -122.526 | -122.2806 | -122.4774 | -122.232
2117.4062 | 122.7356 | -122.493 | 0.009155 | -19.8674 | -19.9584 | -20.0113 | -19.9048 | -19.9099 | -19.8853 | -20.0602 | -0.13523 | -0.012359 | -0.095785 | -0.065154 | 122.3908 | 122.4773 | 122.15 | 122.3897 | -19.817 | -19.908 | -19.961 | -19.8545 | -19.8595 | -19.835 | -20.0098 | -0.084876 | 0.037995 | -0.045431 | -0.0148 | 122.4411 | 122.5277 | 122.2003 | 122.4401 | -122.526 | -122.2852 | -122.4865 | -122.2457
2119.0938 | 122.7768 | -122.493 | -0.009155 | -19.8353 | -19.9217 | -19.9564 | -19.8636 | -19.8641 | -19.8441 | -20.0236 | -0.13523 | -0.012359 | -0.091207 | -0.069733 | 122.3908 | 122.4865 | 122.1454 | 122.3806 | -19.785 | -19.8714 | -19.906 | -19.8133 | -19.8138 | -19.7938 | -19.9732 | -0.084876 | 0.037995 | -0.040853 | -0.019379 | 122.4411 | 122.5368 | 122.1957 | 122.4309 | -122.526 | -122.2806 | -122.482 | -122.2366
2120.7812 | 122.7448 | -122.4976 | 0.018311 | -19.959 | -20.05 | -20.0983 | -19.9918 | -20.0015 | -19.9861 | -20.1563 | -0.13523 | -0.012359 | -0.086628 | -0.074312 | 122.3953 | 122.4773 | 122.1454 | 122.3668 | -19.9086 | -19.9996 | -20.048 | -19.9415 | -19.9511 | -19.9357 | -20.106 | -0.084876 | 0.037995 | -0.036274 | -0.023958 | 122.4457 | 122.5277 | 122.1957 | 122.4172 | -122.5306 | -122.2806 | -122.482 | -122.232
2122.4688 | 122.7219 | -122.5113 | 0.004578 | -19.9773 | -20.0591 | -20.1029 | -20.0056 | -20.0152 | -19.9998 | -20.1609 | -0.13523 | -0.012359 | -0.086628 | -0.074312 | 122.3908 | 122.4819 | 122.1454 | 122.376 | -19.9269 | -20.0088 | -20.0526 | -19.9552 | -19.9648 | -19.9495 | -20.1105 | -0.084876 | 0.037995 | -0.036274 | -0.023958 | 122.4411 | 122.5323 | 122.1957 | 122.4263 | -122.526 | -122.2806 | -122.4774 | -122.232
2124.1406 | 122.699 | -122.5204 | 0.022888 | -20.252 | -20.3338 | -20.373 | -20.2849 | -20.2899 | -20.2837 | -20.4493 | -0.13523 | -0.003202 | -0.095785 | -0.074312 | 122.3953 | 122.4819 | 122.15 | 122.3851 | -20.2016 | -20.2835 | -20.3227 | -20.2345 | -20.2395 | -20.2333 | -20.399 | -0.084876 | 0.047152 | -0.045431 | -0.023958 | 122.4457 | 122.5323 | 122.2003 | 122.4355 | -122.5306 | -122.2852 | -122.4911 | -122.2457
2125.875 | 122.7264 | -122.5159 | 0.045776 | -20.3344 | -20.4071 | -20.4509 | -20.3581 | -20.3723 | -20.3569 | -20.5134 | -0.13523 | -0.012359 | -0.091207 | -0.065154 | 122.3953 | 122.4865 | 122.1408 | 122.376 | -20.284 | -20.3567 | -20.4005 | -20.3078 | -20.3219 | -20.3066 | -20.4631 | -0.084876 | 0.037995 | -0.040853 | -0.0148 | 122.4457 | 122.5368 | 122.1911 | 122.4263 | -122.5306 | -122.276 | -122.4865 | -122.232
2127.5625 | 122.7631 | -122.4976 | 0.013733 | -20.5496 | -20.6223 | -20.6569 | -20.5687 | -20.5783 | -20.5629 | -20.7286 | -0.13523 | -0.016938 | -0.08205 | -0.069733 | 122.3908 | 122.4911 | 122.1408 | 122.376 | -20.4992 | -20.572 | -20.6066 | -20.5184 | -20.5279 | -20.5126 | -20.6782 | -0.084876 | 0.033416 | -0.031696 | -0.019379 | 122.4411 | 122.5414 | 122.1911 | 122.4263 | -122.526 | -122.276 | -122.4728 | -122.2228
2129.25 | 122.6624 | -122.5342 | 0.041199 | -20.5313 | -20.6086 | -20.6478 | -20.5596 | -20.5737 | -20.5629 | -20.7103 | -0.13981 | -0.012359 | -0.091207 | -0.074312 | 122.3999 | 122.4819 | 122.15 | 122.3851 | -20.4809 | -20.5582 | -20.5974 | -20.5092 | -20.5234 | -20.5126 | -20.6599 | -0.089455 | 0.037995 | -0.040853 | -0.023958 | 122.4503 | 122.5323 | 122.2003 | 122.4355 | -122.5397 | -122.2898 | -122.4911 | -122.2412
2130.9844 | 122.7631 | -122.5113 | 0.004578 | -20.339 | -20.4071 | -20.4463 | -20.3627 | -20.3769 | -20.3523 | -20.5134 | -0.13523 | -0.012359 | -0.091207 | -0.074312 | 122.3999 | 122.4865 | 122.15 | 122.3897 | -20.2886 | -20.3567 | -20.3959 | -20.3123 | -20.3265 | -20.302 | -20.4631 | -0.084876 | 0.037995 | -0.040853 | -0.023958 | 122.4503 | 122.5368 | 122.2003 | 122.4401 | -122.5351 | -122.2852 | -122.4911 | -122.2412
2132.6719 | 122.6532 | -122.5342 | 0.036621 | -20.719 | -20.7688 | -20.8217 | -20.729 | -20.7431 | -20.7323 | -20.8797 | -0.13981 | -0.00778 | -0.086628 | -0.069733 | 122.3999 | 122.4911 | 122.1408 | 122.3806 | -20.6686 | -20.7185 | -20.7714 | -20.6786 | -20.6927 | -20.682 | -20.8293 | -0.089455 | 0.042574 | -0.036274 | -0.019379 | 122.4503 | 122.5414 | 122.1911 | 122.4309 | -122.5397 | -122.2806 | -122.4865 | -122.2274
2134.4062 | 122.7539 | -122.5113 | 0.018311 | -20.5954 | -20.6727 | -20.7302 | -20.6374 | -20.6378 | -20.6133 | -20.7698 | -0.13523 | -0.016938 | -0.086628 | -0.069733 | 122.3999 | 122.4911 | 122.1454 | 122.3806 | -20.545 | -20.6223 | -20.6798 | -20.587 | -20.5874 | -20.563 | -20.7194 | -0.084876 | 0.033416 | -0.036274 | -0.019379 | 122.4503 | 122.5414 | 122.1957 | 122.4309 | -122.5351 | -122.2806 | -122.4865 | -122.232
2136.1094 | 122.7814 | -122.5159 | -0.004578 | -20.9067 | -20.9474 | -21.014 | -20.9213 | -20.9354 | -20.9201 | -21.0674 | -0.13981 | -0.012359 | -0.091207 | -0.069733 | 122.3953 | 122.4911 | 122.15 | 122.3943 | -20.8563 | -20.897 | -20.9637 | -20.8709 | -20.885 | -20.8697 | -21.017 | -0.089455 | 0.037995 | -0.040853 | -0.019379 | 122.4457 | 122.5414 | 122.2003 | 122.4446 | -122.5351 | -122.2898 | -122.4865 | -122.2412
2137.7969 | 122.7539 | -122.5067 | 0.013733 | -21.2134 | -21.2679 | -21.3254 | -21.2326 | -21.2421 | -21.2314 | -21.3741 | -0.13523 | -0.012359 | -0.086628 | -0.065154 | 122.3999 | 122.4911 | 122.15 | 122.3806 | -21.1631 | -21.2176 | -21.275 | -21.1823 | -21.1917 | -21.181 | -21.3238 | -0.084876 | 0.037995 | -0.036274 | -0.0148 | 122.4503 | 122.5414 | 122.2003 | 122.4309 | -122.5351 | -122.2852 | -122.4865 | -122.2366
2139.4844 | 122.7081 | -122.525 | 0.018311 | -21.3325 | -21.3915 | -21.4536 | -21.3562 | -21.3657 | -21.3596 | -21.4977 | -0.13981 | -0.012359 | -0.091207 | -0.065154 | 122.3999 | 122.4911 | 122.15 | 122.3897 | -21.2821 | -21.3412 | -21.4032 | -21.3059 | -21.3153 | -21.3092 | -21.4474 | -0.089455 | 0.037995 | -0.040853 | -0.0148 | 122.4503 | 122.5414 | 122.2003 | 122.4401 | -122.5397 | -122.2898 | -122.4911 | -122.2412
2141.1719 | 122.6761 | -122.5662 | 0.022888 | -21.5202 | -21.5884 | -21.6413 | -21.5531 | -21.5534 | -21.5427 | -21.6946 | -0.13523 | -0.012359 | -0.08205 | -0.069733 | 122.4045 | 122.4956 | 122.15 | 122.3897 | -21.4698 | -21.5381 | -21.591 | -21.5027 | -21.503 | -21.4924 | -21.6442 | -0.084876 | 0.037995 | -0.031696 | -0.019379 | 122.4548 | 122.546 | 122.2003 | 122.4401 | -122.5397 | -122.2852 | -122.4865 | -122.232
2142.8594 | 122.6761 | -122.5433 | 0.032043 | -21.8636 | -21.9273 | -21.9847 | -21.8919 | -21.8876 | -21.8861 | -22.0334 | -0.13981 | -0.00778 | -0.091207 | -0.074312 | 122.4045 | 122.4911 | 122.1545 | 122.3897 | -21.8132 | -21.8769 | -21.9344 | -21.8416 | -21.8372 | -21.8357 | -21.983 | -0.089455 | 0.042574 | -0.040853 | -0.023958 | 122.4548 | 122.5414 | 122.2049 | 122.4401 | -122.5443 | -122.2943 | -122.4957 | -122.2457
2144.5469 | 122.7219 | -122.5296 | 0.018311 | -21.8453 | -21.8861 | -21.9481 | -21.8644 | -21.8647 | -21.8495 | -21.983 | -0.13523 | -0.012359 | -0.08205 | -0.069733 | 122.4045 | 122.5002 | 122.1545 | 122.3897 | -21.7949 | -21.8357 | -21.8977 | -21.8141 | -21.8143 | -21.7991 | -21.9327 | -0.084876 | 0.037995 | -0.031696 | -0.019379 | 122.4548 | 122.5506 | 122.2049 | 122.4401 | -122.5397 | -122.2898 | -122.4865 | -122.2366
2146.25 | 122.8043 | -122.4976 | 0.009155 | -21.9918 | -22.028 | -22.0946 | -22.011 | -22.0158 | -22.0006 | -22.1158 | -0.13523 | -0.00778 | -0.086628 | -0.065154 | 122.4045 | 122.4911 | 122.1545 | 122.3943 | -21.9414 | -21.9776 | -22.0442 | -21.9606 | -21.9654 | -21.9502 | -22.0654 | -0.084876 | 0.042574 | -0.036274 | -0.0148 | 122.4548 | 122.5414 | 122.2049 | 122.4446 | -122.5397 | -122.2898 | -122.4911 | -122.2412
2147.9844 | 122.6898 | -122.5433 | 0.036621 | -22.1978 | -22.3165 | -22.4197 | -22.2948 | -22.2721 | -22.2157 | -22.3676 | -0.13065 | -0.00778 | -0.095785 | -0.069733 | 122.4045 | 122.5002 | 122.1637 | 122.3851 | -22.1474 | -22.2661 | -22.3693 | -22.2445 | -22.2218 | -22.1654 | -22.3172 | -0.080298 | 0.042574 | -0.045431 | -0.019379 | 122.4548 | 122.5506 | 122.214 | 122.4355 | -122.5351 | -122.2943 | -122.5003 | -122.2595
2149.6875 | 122.6898 | -122.5433 | 0.018311 | -22.5732 | -22.7011 | -22.8089 | -22.684 | -22.6384 | -22.5912 | -22.7567 | -0.13523 | -0.012359 | -0.086628 | -0.065154 | 122.4091 | 122.4956 | 122.1545 | 122.4034 | -22.5229 | -22.6507 | -22.7585 | -22.6336 | -22.588 | -22.5408 | -22.7064 | -0.084876 | 0.037995 | -0.036274 | -0.0148 | 122.4594 | 122.546 | 122.2049 | 122.4538 | -122.5443 | -122.2898 | -122.4957 | -122.2412
2151.375 | 122.699 | -122.5616 | 0.022888 | -22.9715 | -23.0949 | -23.2072 | -23.0823 | -23.0366 | -22.9986 | -23.1459 | -0.13523 | -0.012359 | -0.08205 | -0.074312 | 122.4091 | 122.4956 | 122.1637 | 122.3989 | -22.9212 | -23.0445 | -23.1568 | -23.032 | -22.9863 | -22.9483 | -23.0955 | -0.084876 | 0.037995 | -0.031696 | -0.023958 | 122.4594 | 122.546 | 122.214 | 122.4492 | -122.5443 | -122.2989 | -122.4911 | -122.2457
2153.0781 | 122.7676 | -122.5021 | 0.013733 | -23.4568 | -23.5665 | -23.6788 | -23.5539 | -23.5219 | -23.4702 | -23.6266 | -0.13065 | -0.00778 | -0.08205 | -0.069733 | 122.4091 | 122.5002 | 122.1637 | 122.3943 | -23.4065 | -23.5161 | -23.6284 | -23.5036 | -23.4716 | -23.4199 | -23.5762 | -0.080298 | 0.042574 | -0.031696 | -0.019379 | 122.4594 | 122.5506 | 122.214 | 122.4446 | -122.5397 | -122.2943 | -122.4911 | -122.2457
2154.7656 | 122.7173 | -122.5433 | 0.032043 | -24.139 | -24.2945 | -24.4251 | -24.2773 | -24.2132 | -24.157 | -24.3225 | -0.13523 | -0.012359 | -0.091207 | -0.065154 | 122.4045 | 122.5048 | 122.1591 | 122.3943 | -24.0887 | -24.2442 | -24.3748 | -24.227 | -24.1628 | -24.1066 | -24.2721 | -0.084876 | 0.037995 | -0.040853 | -0.0148 | 122.4548 | 122.5551 | 122.2095 | 122.4446 | -122.5397 | -122.2943 | -122.4957 | -122.2503
2156.4531 | 122.8043 | -122.5067 | 0.004578 | -24.7846 | -24.9493 | -25.1027 | -24.9412 | -24.877 | -24.8025 | -24.9771 | -0.13523 | -0.00778 | -0.091207 | -0.065154 | 122.4091 | 122.5002 | 122.1637 | 122.3897 | -24.7342 | -24.8989 | -25.0524 | -24.8908 | -24.8266 | -24.7522 | -24.9268 | -0.084876 | 0.042574 | -0.040853 | -0.0148 | 122.4594 | 122.5506 | 122.214 | 122.4401 | -122.5443 | -122.2989 | -122.5003 | -122.2549
2158.1406 | 122.7814 | -122.5159 | 0.009155 | -26.2313 | -26.4191 | -26.5908 | -26.4063 | -26.3282 | -26.2447 | -26.433 | -0.13523 | -0.00778 | -0.091207 | -0.074312 | 122.4045 | 122.5002 | 122.1683 | 122.3943 | -26.181 | -26.3687 | -26.5404 | -26.356 | -26.2778 | -26.1944 | -26.3826 | -0.084876 | 0.042574 | -0.040853 | -0.023958 | 122.4548 | 122.5506 | 122.2186 | 122.4446 | -122.5397 | -122.3035 | -122.4957 | -122.2595
2159.8438 | 122.8134 | -122.5296 | 0.004578 | -26.2909 | -26.4786 | -26.6503 | -26.4658 | -26.3831 | -26.3042 | -26.4879 | -0.13981 | -0.012359 | -0.095785 | -0.065154 | 122.4137 | 122.4956 | 122.1683 | 122.3943 | -26.2405 | -26.4283 | -26.6 | -26.4155 | -26.3328 | -26.2539 | -26.4376 | -0.089455 | 0.037995 | -0.045431 | -0.0148 | 122.464 | 122.546 | 122.2186 | 122.4446 | -122.5535 | -122.3081 | -122.5094 | -122.2641
2161.5312 | 122.7493 | -122.5113 | 0.004578 | -26.4465 | -26.6618 | -26.8197 | -26.6307 | -26.5525 | -26.4782 | -26.6573 | -0.13523 | -0.00778 | -0.08205 | -0.074312 | 122.4137 | 122.5048 | 122.1591 | 122.3989 | -26.3962 | -26.6114 | -26.7694 | -26.5803 | -26.5022 | -26.4279 | -26.607 | -0.084876 | 0.042574 | -0.031696 | -0.023958 | 122.464 | 122.5551 | 122.2095 | 122.4492 | -122.5489 | -122.2943 | -122.4957 | -122.2412
2163.2344 | 122.818 | -122.5021 | 0 | -27.0875 | -27.2982 | -27.4607 | -27.2716 | -27.1889 | -27.1009 | -27.2937 | -0.13523 | -0.012359 | -0.086628 | -0.074312 | 122.4182 | 122.5002 | 122.1637 | 122.4034 | -27.0372 | -27.2479 | -27.4104 | -27.2213 | -27.1385 | -27.0505 | -27.2433 | -0.084876 | 0.037995 | -0.036274 | -0.023958 | 122.4686 | 122.5506 | 122.214 | 122.4538 | -122.5535 | -122.2989 | -122.5049 | -122.2503
2164.9531 | 122.6944 | -122.5296 | 0.022888 | -27.5179 | -27.7698 | -27.9506 | -27.7478 | -27.6695 | -27.5725 | -27.7607 | -0.12607 | -0.00778 | -0.08205 | -0.074312 | 122.4182 | 122.5048 | 122.1637 | 122.3943 | -27.4675 | -27.7195 | -27.9003 | -27.6975 | -27.6192 | -27.5221 | -27.7103 | -0.075719 | 0.042574 | -0.031696 | -0.023958 | 122.4686 | 122.5551 | 122.214 | 122.4446 | -122.5443 | -122.2898 | -122.5003 | -122.2457
2166.6406 | 122.7264 | -122.525 | 0.032043 | -27.962 | -28.1774 | -28.3627 | -28.1644 | -28.0724 | -27.9708 | -28.1681 | -0.13981 | -0.012359 | -0.086628 | -0.065154 | 122.4137 | 122.5002 | 122.1683 | 122.3989 | -27.9116 | -28.127 | -28.3124 | -28.1141 | -28.022 | -27.9204 | -28.1178 | -0.089455 | 0.037995 | -0.036274 | -0.0148 | 122.464 | 122.5506 | 122.2186 | 122.4492 | -122.5535 | -122.3081 | -122.5003 | -122.2549
2168.3594 | 122.7951 | -122.4838 | -0.013733 | -28.635 | -28.8596 | -29.0495 | -28.8329 | -28.7316 | -28.6438 | -28.8457 | -0.13065 | -0.003202 | -0.086628 | -0.069733 | 122.4137 | 122.5048 | 122.1637 | 122.3989 | -28.5846 | -28.8092 | -28.9991 | -28.7826 | -28.6813 | -28.5934 | -28.7953 | -0.080298 | 0.047152 | -0.036274 | -0.019379 | 122.464 | 122.5551 | 122.214 | 122.4492 | -122.5443 | -122.2943 | -122.5003 | -122.2503
2170.0625 | 122.7997 | -122.4884 | -0.009155 | -28.754 | -28.9924 | -29.1777 | -28.9703 | -28.8644 | -28.7766 | -28.9693 | -0.13065 | -0.012359 | -0.086628 | -0.069733 | 122.4137 | 122.514 | 122.1637 | 122.3989 | -28.7037 | -28.942 | -29.1273 | -28.9199 | -28.814 | -28.7262 | -28.9189 | -0.080298 | 0.037995 | -0.036274 | -0.019379 | 122.464 | 122.5643 | 122.214 | 122.4492 | -122.5443 | -122.2943 | -122.5003 | -122.2503
2171.75 | 122.8134 | -122.5159 | 0.004578 | -30.1733 | -30.421 | -30.6383 | -30.3988 | -30.2881 | -30.1821 | -30.3885 | -0.13065 | -0.012359 | -0.091207 | -0.060575 | 122.4182 | 122.5048 | 122.1728 | 122.3989 | -30.123 | -30.3706 | -30.5879 | -30.3484 | -30.2378 | -30.1318 | -30.3382 | -0.080298 | 0.037995 | -0.040853 | -0.010221 | 122.4686 | 122.5551 | 122.2232 | 122.4492 | -122.5489 | -122.3035 | -122.5094 | -122.2641
2173.4844 | 122.8134 | -122.5067 | -0.009155 | -30.6907 | -30.9475 | -31.1602 | -30.9161 | -30.81 | -30.7041 | -30.9059 | -0.13523 | -0.00778 | -0.091207 | -0.065154 | 122.4228 | 122.5048 | 122.1637 | 122.3989 | -30.6403 | -30.8972 | -31.1099 | -30.8658 | -30.7597 | -30.6537 | -30.8555 | -0.084876 | 0.042574 | -0.040853 | -0.0148 | 122.4732 | 122.5551 | 122.214 | 122.4492 | -122.558 | -122.2989 | -122.514 | -122.2549
2175.1719 | 122.7127 | -122.5571 | 0.041199 | -31.9681 | -32.2433 | -32.4697 | -32.2164 | -32.0827 | -31.9723 | -32.1923 | -0.13065 | -0.012359 | -0.086628 | -0.060575 | 122.4228 | 122.5094 | 122.1683 | 122.408 | -31.9177 | -32.193 | -32.4194 | -32.1661 | -32.0323 | -31.9219 | -32.142 | -0.080298 | 0.037995 | -0.036274 | -0.010221 | 122.4732 | 122.5597 | 122.2186 | 122.4584 | -122.5535 | -122.2989 | -122.5094 | -122.2549
2176.9219 | 122.731 | -122.5525 | 0.018311 | -32.2428 | -32.5135 | -32.7582 | -32.4865 | -32.3757 | -32.2607 | -32.467 | -0.13523 | -0.012359 | -0.086628 | -0.065154 | 122.4182 | 122.5048 | 122.1683 | 122.3989 | -32.1924 | -32.4631 | -32.7078 | -32.4362 | -32.3253 | -32.2104 | -32.4167 | -0.084876 | 0.037995 | -0.036274 | -0.0148 | 122.4686 | 122.5551 | 122.2186 | 122.4492 | -122.5535 | -122.3035 | -122.5049 | -122.2549
2178.625 | 122.6624 | -122.5388 | 0.032043 | -32.2153 | -32.486 | -32.7124 | -32.4637 | -32.3345 | -32.2241 | -32.4441 | -0.13523 | -0.012359 | -0.08205 | -0.069733 | 122.4228 | 122.5094 | 122.1683 | 122.4034 | -32.1649 | -32.4357 | -32.662 | -32.4133 | -32.2841 | -32.1737 | -32.3938 | -0.084876 | 0.037995 | -0.031696 | -0.019379 | 122.4732 | 122.5597 | 122.2186 | 122.4538 | -122.558 | -122.3035 | -122.5049 | -122.2503
2180.3125 | 122.7448 | -122.5525 | 0.018311 | -32.609 | -32.8661 | -33.0924 | -32.8437 | -32.7282 | -32.6133 | -32.8333 | -0.13065 | -0.00778 | -0.091207 | -0.060575 | 122.4274 | 122.5094 | 122.1728 | 122.408 | -32.5587 | -32.8157 | -33.042 | -32.7933 | -32.6778 | -32.5629 | -32.7829 | -0.080298 | 0.042574 | -0.040853 | -0.010221 | 122.4777 | 122.5597 | 122.2232 | 122.4584 | -122.558 | -122.3035 | -122.5186 | -122.2641
2182.0156 | 122.7814 | -122.525 | 0.004578 | -33.0806 | -33.3423 | -33.5594 | -33.3244 | -33.1997 | -33.0848 | -33.3048 | -0.13523 | -0.003202 | -0.086628 | -0.060575 | 122.4228 | 122.5094 | 122.1728 | 122.408 | -33.0303 | -33.2919 | -33.5091 | -33.2741 | -33.1494 | -33.0345 | -33.2545 | -0.084876 | 0.047152 | -0.036274 | -0.010221 | 122.4732 | 122.5597 | 122.2232 | 122.4584 | -122.558 | -122.3081 | -122.5094 | -122.2595
2183.7188 | 122.7402 | -122.5388 | 0.013733 | -34.1977 | -34.4641 | -34.6766 | -34.4461 | -34.3076 | -34.2065 | -34.4173 | -0.11692 | -0.012359 | -0.086628 | -0.074312 | 122.4274 | 122.5185 | 122.1728 | 122.408 | -34.1474 | -34.4137 | -34.6262 | -34.3958 | -34.2572 | -34.1562 | -34.367 | -0.066562 | 0.037995 | -0.036274 | -0.023958 | 122.4777 | 122.5689 | 122.2232 | 122.4584 | -122.5443 | -122.2898 | -122.514 | -122.2595
2185.4531 | 122.7768 | -122.5159 | 0.004578 | -35.9833 | -36.291 | -36.5447 | -36.2684 | -36.0838 | -35.9875 | -36.2211 | -0.13523 | -0.012359 | -0.086628 | -0.065154 | 122.4228 | 122.5094 | 122.1728 | 122.4126 | -35.933 | -36.2407 | -36.4943 | -36.218 | -36.0335 | -35.9372 | -36.1708 | -0.084876 | 0.037995 | -0.036274 | -0.0148 | 122.4732 | 122.5597 | 122.2232 | 122.463 | -122.558 | -122.3081 | -122.5094 | -122.2595
2187.1719 | 122.7219 | -122.5571 | 0.018311 | -36.3267 | -36.6161 | -36.8652 | -36.5935 | -36.4089 | -36.3263 | -36.5553 | -0.12607 | -0.012359 | -0.086628 | -0.060575 | 122.4228 | 122.5231 | 122.1774 | 122.408 | -36.2763 | -36.5658 | -36.8148 | -36.5431 | -36.3585 | -36.276 | -36.505 | -0.075719 | 0.037995 | -0.036274 | -0.010221 | 122.4732 | 122.5735 | 122.2278 | 122.4584 | -122.5489 | -122.3035 | -122.5094 | -122.2641
2188.9375 | 122.7036 | -122.5525 | 0.036621 | -36.7342 | -37.0282 | -37.2727 | -37.0055 | -36.8255 | -36.7338 | -36.9582 | -0.13065 | -0.00778 | -0.086628 | -0.065154 | 122.4274 | 122.5185 | 122.1683 | 122.408 | -36.6838 | -36.9779 | -37.2223 | -36.9552 | -36.7751 | -36.6835 | -36.9079 | -0.080298 | 0.042574 | -0.036274 | -0.0148 | 122.4777 | 122.5689 | 122.2186 | 122.4584 | -122.558 | -122.2989 | -122.514 | -122.2549
2190.7031 | 122.8226 | -122.5021 | -0.004578 | -37.4667 | -37.7746 | -38.0098 | -37.7381 | -37.5442 | -37.4709 | -37.6907 | -0.13523 | -0.016938 | -0.086628 | -0.065154 | 122.4182 | 122.5185 | 122.1728 | 122.4126 | -37.4164 | -37.7242 | -37.9595 | -37.6877 | -37.4938 | -37.4206 | -37.6404 | -0.084876 | 0.033416 | -0.036274 | -0.0148 | 122.4686 | 122.5689 | 122.2232 | 122.463 | -122.5535 | -122.3081 | -122.5049 | -122.2595
2192.5 | 122.8317 | -122.525 | 0.004578 | -37.6361 | -37.9348 | -38.1609 | -37.9029 | -37.7182 | -37.6403 | -37.8738 | -0.12607 | -0.003202 | -0.091207 | -0.069733 | 122.4274 | 122.5094 | 122.1728 | 122.4126 | -37.5858 | -37.8845 | -38.1106 | -37.8526 | -37.6678 | -37.59 | -37.8235 | -0.075719 | 0.047152 | -0.040853 | -0.019379 | 122.4777 | 122.5597 | 122.2232 | 122.463 | -122.5535 | -122.2989 | -122.5186 | -122.2641
2194.2344 | 122.8043 | -122.5342 | 0.022888 | -38.1123 | -38.4064 | -38.6325 | -38.3837 | -38.2034 | -38.1256 | -38.3454 | -0.13065 | -0.012359 | -0.091207 | -0.065154 | 122.4274 | 122.514 | 122.1774 | 122.4126 | -38.0619 | -38.3561 | -38.5822 | -38.3333 | -38.1531 | -38.0753 | -38.295 | -0.080298 | 0.037995 | -0.040853 | -0.0148 | 122.4777 | 122.5643 | 122.2278 | 122.463 | -122.558 | -122.3081 | -122.5186 | -122.2686
2195.9688 | 122.8363 | -122.5342 | 0.009155 | -38.6754 | -38.965 | -39.1911 | -38.9331 | -38.7574 | -38.6934 | -38.9131 | -0.13981 | -0.012359 | -0.091207 | -0.074312 | 122.4228 | 122.514 | 122.1728 | 122.4172 | -38.6251 | -38.9147 | -39.1407 | -38.8827 | -38.707 | -38.643 | -38.8627 | -0.089455 | 0.037995 | -0.040853 | -0.023958 | 122.4732 | 122.5643 | 122.2232 | 122.4675 | -122.5626 | -122.3127 | -122.514 | -122.2641
2197.6875 | 122.7814 | -122.5204 | -0.004578 | -39.0554 | -39.3314 | -39.5482 | -39.2993 | -39.1282 | -39.0642 | -39.2885 | -0.13523 | -0.016938 | -0.086628 | -0.069733 | 122.4274 | 122.5185 | 122.1728 | 122.4172 | -39.0051 | -39.281 | -39.4979 | -39.249 | -39.0778 | -39.0139 | -39.2382 | -0.084876 | 0.033416 | -0.036274 | -0.019379 | 122.4777 | 122.5689 | 122.2232 | 122.4675 | -122.5626 | -122.3081 | -122.514 | -122.2595
2199.375 | 122.6944 | -122.5708 | 0.013733 | -39.9986 | -40.2929 | -40.5097 | -40.2517 | -40.0758 | -40.0028 | -40.2316 | -0.13065 | -0.003202 | -0.08205 | -0.065154 | 122.432 | 122.5185 | 122.1728 | 122.4126 | -39.9482 | -40.2425 | -40.4594 | -40.2013 | -40.0255 | -39.9524 | -40.1813 | -0.080298 | 0.047152 | -0.031696 | -0.0148 | 122.4823 | 122.5689 | 122.2232 | 122.463 | -122.5626 | -122.3035 | -122.514 | -122.2549
2201.0938 | 122.7127 | -122.5708 | 0.027466 | -40.6075 | -40.9202 | -41.1279 | -40.8652 | -40.6847 | -40.6117 | -40.8451 | -0.13523 | -0.003202 | -0.08205 | -0.065154 | 122.4365 | 122.514 | 122.182 | 122.4172 | -40.5571 | -40.8698 | -41.0775 | -40.8148 | -40.6343 | -40.5614 | -40.7947 | -0.084876 | 0.047152 | -0.031696 | -0.0148 | 122.4869 | 122.5643 | 122.2324 | 122.4675 | -122.5718 | -122.3172 | -122.5186 | -122.2641
2202.8125 | 122.7814 | -122.5296 | 0.018311 | -41.5552 | -41.8634 | -42.0939 | -41.8129 | -41.6323 | -41.564 | -41.7836 | -0.13523 | -0.00778 | -0.091207 | -0.069733 | 122.4274 | 122.5185 | 122.1774 | 122.4172 | -41.5049 | -41.8131 | -42.0436 | -41.7626 | -41.582 | -41.5137 | -41.7333 | -0.084876 | 0.042574 | -0.040853 | -0.019379 | 122.4777 | 122.5689 | 122.2278 | 122.4675 | -122.5626 | -122.3127 | -122.5186 | -122.2686
2204.5312 | 122.8317 | -122.5113 | 0 | -41.5598 | -41.8863 | -42.0894 | -41.8313 | -41.6552 | -41.5732 | -41.8157 | -0.13065 | -0.012359 | -0.08205 | -0.069733 | 122.432 | 122.514 | 122.182 | 122.4172 | -41.5094 | -41.836 | -42.039 | -41.7809 | -41.6048 | -41.5228 | -41.7653 | -0.080298 | 0.037995 | -0.031696 | -0.019379 | 122.4823 | 122.5643 | 122.2324 | 122.4675 | -122.5626 | -122.3127 | -122.514 | -122.2641
2206.2344 | 122.7539 | -122.5571 | 0.018311 | -42.796 | -43.1226 | -43.3485 | -43.0675 | -42.8821 | -42.8048 | -43.038 | -0.12607 | -0.00778 | -0.086628 | -0.065154 | 122.4365 | 122.5231 | 122.182 | 122.4172 | -42.7456 | -43.0723 | -43.2981 | -43.0171 | -42.8317 | -42.7544 | -42.9877 | -0.075719 | 0.042574 | -0.036274 | -0.0148 | 122.4869 | 122.5735 | 122.2324 | 122.4675 | -122.5626 | -122.3081 | -122.5232 | -122.2686
2207.9844 | 122.7814 | -122.5433 | 0.027466 | -43.3087 | -43.6492 | -43.8613 | -43.5848 | -43.3903 | -43.3221 | -43.5691 | -0.12607 | -0.012359 | -0.08205 | -0.065154 | 122.432 | 122.5185 | 122.182 | 122.4172 | -43.2584 | -43.5988 | -43.8109 | -43.5345 | -43.3399 | -43.2718 | -43.5187 | -0.075719 | 0.037995 | -0.031696 | -0.0148 | 122.4823 | 122.5689 | 122.2324 | 122.4675 | -122.558 | -122.3081 | -122.514 | -122.2641
2209.6719 | 122.7814 | -122.5525 | 0.013733 | -44.4167 | -44.7756 | -45.0197 | -44.7066 | -44.5164 | -44.4301 | -44.6816 | -0.12607 | -0.012359 | -0.086628 | -0.069733 | 122.432 | 122.5185 | 122.1774 | 122.4172 | -44.3664 | -44.7252 | -44.9693 | -44.6562 | -44.4661 | -44.3797 | -44.6312 | -0.075719 | 0.037995 | -0.036274 | -0.019379 | 122.4823 | 122.5689 | 122.2278 | 122.4675 | -122.558 | -122.3035 | -122.5186 | -122.2641
2211.375 | 122.7493 | -122.5616 | 0 | -45.4514 | -45.8287 | -46.0727 | -45.7596 | -45.5556 | -45.474 | -45.7254 | -0.1215 | -0.012359 | -0.086628 | -0.065154 | 122.432 | 122.5185 | 122.1774 | 122.4172 | -45.4011 | -45.7783 | -46.0224 | -45.7093 | -45.5053 | -45.4236 | -45.6751 | -0.071141 | 0.037995 | -0.036274 | -0.0148 | 122.4823 | 122.5689 | 122.2278 | 122.4675 | -122.5535 | -122.2989 | -122.5186 | -122.2641
2213.1094 | 122.7173 | -122.5525 | 0.036621 | -45.6803 | -46.0485 | -46.2696 | -45.9794 | -45.7754 | -45.6891 | -45.9452 | -0.13523 | -0.016938 | -0.095785 | -0.069733 | 122.4365 | 122.5277 | 122.1866 | 122.4218 | -45.63 | -45.9981 | -46.2193 | -45.929 | -45.725 | -45.6388 | -45.8948 | -0.084876 | 0.033416 | -0.045431 | -0.019379 | 122.4869 | 122.578 | 122.2369 | 122.4721 | -122.5718 | -122.3218 | -122.5323 | -122.2824
2214.8125 | 122.7905 | -122.5616 | 0.004578 | -46.0649 | -46.4285 | -46.6542 | -46.3594 | -46.1645 | -46.0783 | -46.3297 | -0.12607 | -0.00778 | -0.086628 | -0.069733 | 122.4274 | 122.5323 | 122.1866 | 122.4218 | -46.0146 | -46.3782 | -46.6039 | -46.309 | -46.1141 | -46.0279 | -46.2794 | -0.075719 | 0.042574 | -0.036274 | -0.019379 | 122.4777 | 122.5826 | 122.2369 | 122.4721 | -122.5535 | -122.3127 | -122.514 | -122.2732
2216.5156 | 122.7539 | -122.5525 | 0.022888 | -48.1893 | -48.5943 | -48.8291 | -48.5067 | -48.2841 | -48.2073 | -48.4632 | -0.1215 | -0.00778 | -0.08205 | -0.065154 | 122.4365 | 122.5185 | 122.182 | 122.4263 | -48.1389 | -48.5439 | -48.7787 | -48.4563 | -48.2337 | -48.1569 | -48.4128 | -0.071141 | 0.042574 | -0.031696 | -0.0148 | 122.4869 | 122.5689 | 122.2324 | 122.4767 | -122.558 | -122.3035 | -122.5186 | -122.2641
2218.2031 | 122.7127 | -122.5708 | 0.032043 | -50.9409 | -51.424 | -51.6907 | -51.3179 | -51.0492 | -50.9543 | -51.2513 | -0.13065 | -0.003202 | -0.077472 | -0.069733 | 122.4365 | 122.5277 | 122.1957 | 122.4218 | -50.8906 | -51.3737 | -51.6403 | -51.2675 | -50.9988 | -50.9039 | -51.2009 | -0.080298 | 0.047152 | -0.027118 | -0.019379 | 122.4869 | 122.578 | 122.2461 | 122.4721 | -122.5672 | -122.3264 | -122.514 | -122.2732
2219.9531 | 122.7081 | -122.5525 | 0.041199 | -50.5838 | -51.0028 | -51.2786 | -50.9287 | -50.6784 | -50.6017 | -50.8621 | -0.13523 | -0.00778 | -0.086628 | -0.065154 | 122.4365 | 122.5277 | 122.1912 | 122.4218 | -50.5334 | -50.9524 | -51.2283 | -50.8784 | -50.628 | -50.5514 | -50.8118 | -0.084876 | 0.042574 | -0.036274 | -0.0148 | 122.4869 | 122.578 | 122.2415 | 122.4721 | -122.5718 | -122.3264 | -122.5232 | -122.2778
2221.6562 | 122.8317 | -122.5204 | -0.004578 | -50.3778 | -50.783 | -51.0176 | -50.6906 | -50.4632 | -50.3957 | -50.6607 | -0.13065 | -0.00778 | -0.091207 | -0.065154 | 122.4411 | 122.5231 | 122.1866 | 122.4218 | -50.3274 | -50.7326 | -50.9673 | -50.6403 | -50.4128 | -50.3454 | -50.6103 | -0.080298 | 0.042574 | -0.040853 | -0.0148 | 122.4915 | 122.5735 | 122.2369 | 122.4721 | -122.5718 | -122.3172 | -122.5323 | -122.2778
2223.3438 | 122.8409 | -122.5113 | 0.009155 | -50.7898 | -51.1996 | -51.4114 | -51.0798 | -50.8706 | -50.8032 | -51.0773 | -0.1215 | -0.012359 | -0.08205 | -0.069733 | 122.4411 | 122.5277 | 122.1866 | 122.4218 | -50.7395 | -51.1493 | -51.361 | -51.0295 | -50.8203 | -50.7528 | -51.0269 | -0.071141 | 0.037995 | -0.031696 | -0.019379 | 122.4915 | 122.578 | 122.2369 | 122.4721 | -122.5626 | -122.3081 | -122.5232 | -122.2686
2225.0625 | 122.7585 | -122.5525 | 0.009155 | -51.2797 | -51.6667 | -51.8647 | -51.556 | -51.3513 | -51.2977 | -51.5626 | -0.13981 | -0.00778 | -0.091207 | -0.060575 | 122.4365 | 122.5277 | 122.1912 | 122.4263 | -51.2294 | -51.6163 | -51.8143 | -51.5056 | -51.301 | -51.2473 | -51.5122 | -0.089455 | 0.042574 | -0.040853 | -0.010221 | 122.4869 | 122.578 | 122.2415 | 122.4767 | -122.5763 | -122.331 | -122.5277 | -122.2824
2226.7656 | 122.8043 | -122.5433 | -0.004578 | -51.8795 | -52.2665 | -52.4599 | -52.1283 | -51.9419 | -51.8974 | -52.1578 | -0.13981 | -0.016938 | -0.086628 | -0.065154 | 122.4411 | 122.5277 | 122.1912 | 122.4172 | -51.8291 | -52.2162 | -52.4095 | -52.0779 | -51.8915 | -51.8471 | -52.1074 | -0.089455 | 0.033416 | -0.036274 | -0.0148 | 122.4915 | 122.578 | 122.2415 | 122.4675 | -122.5809 | -122.331 | -122.5277 | -122.2778
2228.5156 | 122.7356 | -122.58 | 0.045776 | -52.8913 | -53.283 | -53.4809 | -53.1356 | -52.9399 | -52.9138 | -53.1787 | -0.13065 | -0.00778 | -0.08205 | -0.069733 | 122.4365 | 122.5323 | 122.1866 | 122.4263 | -52.8409 | -53.2327 | -53.4306 | -53.0852 | -52.8895 | -52.8635 | -53.1283 | -0.080298 | 0.042574 | -0.031696 | -0.019379 | 122.4869 | 122.5826 | 122.2369 | 122.4767 | -122.5672 | -122.3172 | -122.5186 | -122.2686
2230.2188 | 122.7905 | -122.5342 | -0.022888 | -53.3583 | -53.8233 | -53.8609 | -53.5659 | -53.3839 | -53.3854 | -53.6777 | -0.13065 | -0.003202 | -0.08205 | -0.074312 | 122.4457 | 122.5231 | 122.1866 | 122.4263 | -53.3079 | -53.773 | -53.8106 | -53.5156 | -53.3336 | -53.3351 | -53.6273 | -0.080298 | 0.047152 | -0.031696 | -0.023958 | 122.4961 | 122.5735 | 122.2369 | 122.4767 | -122.5763 | -122.3172 | -122.5277 | -122.2686
2231.9688 | 122.8592 | -122.5296 | 0.013733 | -54.9882 | -55.5129 | -55.5321 | -55.2096 | -55.0274 | -55.0107 | -55.335 | -0.12607 | -0.012359 | -0.086628 | -0.065154 | 122.4457 | 122.5368 | 122.1957 | 122.4263 | -54.9379 | -55.4625 | -55.4818 | -55.1593 | -54.9771 | -54.9604 | -55.2846 | -0.075719 | 0.037995 | -0.036274 | -0.0148 | 122.4961 | 122.5872 | 122.2461 | 122.4767 | -122.5718 | -122.3218 | -122.5323 | -122.2824
2233.7031 | 122.818 | -122.525 | 0.004578 | -55.9359 | -56.3737 | -56.425 | -56.0933 | -55.943 | -55.9768 | -56.2461 | -0.13523 | -0.00778 | -0.091207 | -0.069733 | 122.4457 | 122.5368 | 122.1866 | 122.4263 | -55.8856 | -56.3234 | -56.3746 | -56.0429 | -55.8927 | -55.9264 | -56.1957 | -0.084876 | 0.042574 | -0.040853 | -0.019379 | 122.4961 | 122.5872 | 122.2369 | 122.4767 | -122.5809 | -122.3218 | -122.5369 | -122.2778
2235.5 | 122.85 | -122.525 | 0.004578 | -56.2335 | -56.7171 | -56.7592 | -56.4229 | -56.2497 | -56.2515 | -56.5665 | -0.13523 | -0.012359 | -0.086628 | -0.065154 | 122.4457 | 122.5368 | 122.1912 | 122.4309 | -56.1832 | -56.6668 | -56.7088 | -56.3726 | -56.1994 | -56.2011 | -56.5162 | -0.084876 | 0.037995 | -0.036274 | -0.0148 | 122.4961 | 122.5872 | 122.2415 | 122.4813 | -122.5809 | -122.3264 | -122.5323 | -122.2778
2237.2031 | 122.7081 | -122.6028 | 0.032043 | -56.5815 | -57.0605 | -57.098 | -56.7617 | -56.5931 | -56.6086 | -56.8962 | -0.13065 | -0.012359 | -0.08205 | -0.069733 | 122.4411 | 122.5323 | 122.1912 | 122.4355 | -56.5311 | -57.0102 | -57.0477 | -56.7114 | -56.5427 | -56.5582 | -56.8458 | -0.080298 | 0.037995 | -0.031696 | -0.019379 | 122.4915 | 122.5826 | 122.2415 | 122.4858 | -122.5718 | -122.3218 | -122.5232 | -122.2732
2238.9688 | 122.7539 | -122.5616 | 0.027466 | -57.3735 | -57.8893 | -57.913 | -57.5538 | -57.3942 | -57.4052 | -57.7065 | -0.13065 | -0.012359 | -0.08205 | -0.065154 | 122.4457 | 122.5323 | 122.1957 | 122.4355 | -57.3232 | -57.8389 | -57.8627 | -57.5035 | -57.3439 | -57.3549 | -57.6561 | -0.080298 | 0.037995 | -0.031696 | -0.0148 | 122.4961 | 122.5826 | 122.2461 | 122.4858 | -122.5763 | -122.3264 | -122.5277 | -122.2778
2240.7031 | 122.8363 | -122.5433 | -0.004578 | -58.0237 | -58.5441 | -58.5677 | -58.2268 | -58.0443 | -58.0554 | -58.3703 | -0.13065 | -0.00778 | -0.08205 | -0.069733 | 122.4503 | 122.5368 | 122.1957 | 122.4355 | -57.9733 | -58.4937 | -58.5174 | -58.1765 | -57.9939 | -58.005 | -58.32 | -0.080298 | 0.042574 | -0.031696 | -0.019379 | 122.5006 | 122.5872 | 122.2461 | 122.4858 | -122.5809 | -122.3264 | -122.5323 | -122.2778
2242.4062 | 122.7631 | -122.5754 | 0.032043 | -58.6784 | -59.1851 | -59.2362 | -58.8816 | -58.7035 | -58.7009 | -59.0159 | -0.13065 | -0.003202 | -0.095785 | -0.060575 | 122.4457 | 122.5323 | 122.2095 | 122.4355 | -58.628 | -59.1347 | -59.1859 | -58.8312 | -58.6532 | -58.6506 | -58.9655 | -0.080298 | 0.047152 | -0.045431 | -0.010221 | 122.4961 | 122.5826 | 122.2598 | 122.4858 | -122.5763 | -122.3401 | -122.5415 | -122.3053
2244.1094 | 122.731 | -122.5754 | 0.018311 | -58.7837 | -59.3087 | -59.3461 | -58.9869 | -58.8042 | -58.82 | -59.1349 | -0.13065 | -0.012359 | -0.08205 | -0.065154 | 122.4457 | 122.5414 | 122.1957 | 122.4355 | -58.7333 | -59.2584 | -59.2958 | -58.9365 | -58.7539 | -58.7696 | -59.0845 | -0.080298 | 0.037995 | -0.031696 | -0.0148 | 122.4961 | 122.5918 | 122.2461 | 122.4858 | -122.5763 | -122.3264 | -122.5277 | -122.2778
2245.8438 | 122.7081 | -122.6074 | 0.054932 | -60.6791 | -61.2273 | -61.2783 | -60.887 | -60.6949 | -60.7246 | -61.0486 | -0.12607 | -0.00778 | -0.086628 | -0.069733 | 122.4457 | 122.5323 | 122.2003 | 122.4309 | -60.6288 | -61.1769 | -61.2279 | -60.8366 | -60.6446 | -60.6742 | -60.9982 | -0.075719 | 0.042574 | -0.036274 | -0.019379 | 122.4961 | 122.5826 | 122.2507 | 122.4813 | -122.5718 | -122.3264 | -122.5323 | -122.2869
2247.5469 | 122.8043 | -122.5388 | 0.004578 | -61.3751 | -61.9141 | -61.9559 | -61.5737 | -61.3862 | -61.4113 | -61.7399 | -0.14439 | -0.00778 | -0.08205 | -0.069733 | 122.4503 | 122.5414 | 122.1957 | 122.4263 | -61.3247 | -61.8637 | -61.9056 | -61.5234 | -61.3359 | -61.361 | -61.6895 | -0.094033 | 0.042574 | -0.031696 | -0.019379 | 122.5006 | 122.5918 | 122.2461 | 122.4767 | -122.5947 | -122.3401 | -122.5323 | -122.2778
2249.25 | 122.7081 | -122.6074 | 0.032043 | -62.4968 | -63.0679 | -63.1006 | -62.7 | -62.517 | -62.5513 | -62.8753 | -0.13523 | -0.003202 | -0.08205 | -0.069733 | 122.4457 | 122.5368 | 122.1912 | 122.4309 | -62.4464 | -63.0176 | -63.0502 | -62.6497 | -62.4666 | -62.501 | -62.8249 | -0.084876 | 0.047152 | -0.031696 | -0.019379 | 122.4961 | 122.5872 | 122.2415 | 122.4813 | -122.5809 | -122.3264 | -122.5277 | -122.2732
2251 | 122.818 | -122.5571 | 0.009155 | -62.625 | -63.1733 | -63.215 | -62.8145 | -62.6268 | -62.6658 | -62.9897 | -0.13065 | -0.003202 | -0.086628 | -0.069733 | 122.4503 | 122.5414 | 122.1912 | 122.4355 | -62.5746 | -63.1229 | -63.1647 | -62.7641 | -62.5765 | -62.6154 | -62.9394 | -0.080298 | 0.047152 | -0.036274 | -0.019379 | 122.5006 | 122.5918 | 122.2415 | 122.4858 | -122.5809 | -122.3218 | -122.5369 | -122.2778
2252.7188 | 122.85 | -122.58 | 0 | -63.4399 | -63.9974 | -64.0346 | -63.6341 | -63.4417 | -63.4762 | -63.8 | -0.12607 | -0.012359 | -0.086628 | -0.065154 | 122.4549 | 122.5414 | 122.1957 | 122.4355 | -63.3896 | -63.9471 | -63.9842 | -63.5837 | -63.3914 | -63.4258 | -63.7497 | -0.075719 | 0.037995 | -0.036274 | -0.0148 | 122.5052 | 122.5918 | 122.2461 | 122.4858 | -122.5809 | -122.3218 | -122.5415 | -122.2824
2254.4219 | 122.8546 | -122.5296 | -0.013733 | -63.4628 | -64.0249 | -64.0575 | -63.6524 | -63.4646 | -63.5036 | -63.8321 | -0.12607 | -0.012359 | -0.08205 | -0.074312 | 122.4503 | 122.546 | 122.2003 | 122.4401 | -63.4124 | -63.9746 | -64.0071 | -63.602 | -63.4142 | -63.4533 | -63.7817 | -0.075719 | 0.037995 | -0.031696 | -0.023958 | 122.5006 | 122.5964 | 122.2507 | 122.4904 | -122.5763 | -122.3264 | -122.5323 | -122.2824
2256.1562 | 122.7997 | -122.5708 | -0.009155 | -65.3216 | -65.9434 | -66.0217 | -65.5341 | -65.3416 | -65.3808 | -65.7229 | -0.13523 | -0.00778 | -0.086628 | -0.078891 | 122.4503 | 122.5506 | 122.2049 | 122.4355 | -65.2713 | -65.8931 | -65.9714 | -65.4838 | -65.2912 | -65.3304 | -65.6725 | -0.084876 | 0.042574 | -0.036274 | -0.028537 | 122.5006 | 122.6009 | 122.2552 | 122.4858 | -122.5855 | -122.3401 | -122.5369 | -122.2915
2257.9062 | 122.7951 | -122.5662 | 0 | -66.2877 | -66.9187 | -66.9649 | -66.5139 | -66.3029 | -66.3422 | -66.6934 | -0.13523 | -0.00778 | -0.08205 | -0.074312 | 122.4594 | 122.5414 | 122.2003 | 122.4401 | -66.2373 | -66.8684 | -66.9146 | -66.4636 | -66.2526 | -66.2919 | -66.6431 | -0.084876 | 0.042574 | -0.031696 | -0.023958 | 122.5098 | 122.5918 | 122.2507 | 122.4904 | -122.5947 | -122.3355 | -122.5415 | -122.2824
2259.6406 | 122.7814 | -122.5754 | 0.009155 | -65.9122 | -66.5021 | -66.5483 | -66.1156 | -65.9184 | -65.9622 | -66.3089 | -0.13065 | -0.00778 | -0.08205 | -0.065154 | 122.4549 | 122.5506 | 122.2095 | 122.4401 | -65.8619 | -66.4517 | -66.4979 | -66.0652 | -65.868 | -65.9119 | -66.2585 | -0.080298 | 0.042574 | -0.031696 | -0.0148 | 122.5052 | 122.6009 | 122.2598 | 122.4904 | -122.5855 | -122.3401 | -122.5369 | -122.2915
2261.3438 | 122.8455 | -122.5525 | 0 | -66.164 | -66.7356 | -66.7726 | -66.3399 | -66.161 | -66.2095 | -66.5515 | -0.13065 | -0.00778 | -0.08205 | -0.069733 | 122.4594 | 122.546 | 122.2003 | 122.4446 | -66.1137 | -66.6852 | -66.7222 | -66.2896 | -66.1107 | -66.1591 | -66.5012 | -0.080298 | 0.042574 | -0.031696 | -0.019379 | 122.5098 | 122.5964 | 122.2507 | 122.495 | -122.5901 | -122.331 | -122.5415 | -122.2824
2263.0781 | 122.7814 | -122.5708 | 0.009155 | -67.098 | -67.6788 | -67.7341 | -67.2923 | -67.0949 | -67.148 | -67.4946 | -0.13523 | -0.012359 | -0.086628 | -0.065154 | 122.4549 | 122.546 | 122.2049 | 122.4401 | -67.0477 | -67.6285 | -67.6838 | -67.2419 | -67.0446 | -67.0977 | -67.4443 | -0.084876 | 0.037995 | -0.036274 | -0.0148 | 122.5052 | 122.5964 | 122.2552 | 122.4904 | -122.5901 | -122.3401 | -122.5415 | -122.2915
2264.8281 | 122.7173 | -122.6074 | 0.032043 | -67.4872 | -68.0634 | -68.1004 | -67.6677 | -67.4886 | -67.5418 | -67.8746 | -0.13065 | -0.00778 | -0.08205 | -0.069733 | 122.4594 | 122.5414 | 122.2049 | 122.4446 | -67.4368 | -68.0131 | -68.05 | -67.6174 | -67.4383 | -67.4914 | -67.8243 | -0.080298 | 0.042574 | -0.031696 | -0.019379 | 122.5098 | 122.5918 | 122.2552 | 122.495 | -122.5901 | -122.3355 | -122.5415 | -122.2869
2266.5312 | 122.7905 | -122.5433 | 0.004578 | -68.1923 | -68.7869 | -68.8421 | -68.3911 | -68.2119 | -68.2514 | -68.5934 | -0.13065 | -0.00778 | -0.086628 | -0.065154 | 122.4594 | 122.5506 | 122.2003 | 122.4401 | -68.1419 | -68.7365 | -68.7918 | -68.3408 | -68.1616 | -68.2011 | -68.543 | -0.080298 | 0.042574 | -0.036274 | -0.0148 | 122.5098 | 122.6009 | 122.2507 | 122.4904 | -122.5901 | -122.331 | -122.5461 | -122.2869
2268.2344 | 122.731 | -122.6074 | 0.050354 | -70.2892 | -70.9343 | -71.0124 | -70.5018 | -70.3041 | -70.3529 | -70.7177 | -0.13523 | -0.003202 | -0.086628 | -0.074312 | 122.4594 | 122.546 | 122.2095 | 122.4492 | -70.2388 | -70.884 | -70.962 | -70.4514 | -70.2537 | -70.3026 | -70.6673 | -0.084876 | 0.047152 | -0.036274 | -0.023958 | 122.5098 | 122.5964 | 122.2598 | 122.4996 | -122.5947 | -122.3447 | -122.5461 | -122.2961
2270 | 122.7219 | -122.6028 | 0.041199 | -70.9347 | -71.5525 | -71.603 | -71.129 | -70.9358 | -70.9893 | -71.354 | -0.13523 | -0.00778 | -0.08205 | -0.069733 | 122.4594 | 122.5414 | 122.2186 | 122.4492 | -70.8844 | -71.5021 | -71.5527 | -71.0787 | -70.8855 | -70.939 | -71.3037 | -0.084876 | 0.042574 | -0.031696 | -0.019379 | 122.5098 | 122.5918 | 122.269 | 122.4996 | -122.5947 | -122.3539 | -122.5415 | -122.3007
2271.7031 | 122.8683 | -122.5342 | 0 | -72.4822 | -72.7018 | -72.7339 | -72.3973 | -72.3321 | -72.5414 | -72.7 | -0.13523 | -0.003202 | -0.086628 | -0.069733 | 122.4549 | 122.5414 | 122.2049 | 122.4401 | -72.4319 | -72.6514 | -72.6836 | -72.3469 | -72.2818 | -72.491 | -72.6497 | -0.084876 | 0.047152 | -0.036274 | -0.019379 | 122.5052 | 122.5918 | 122.2552 | 122.4904 | -122.5901 | -122.3401 | -122.5415 | -122.2915
2273.4062 | 122.7356 | -122.5616 | 0.013733 | -73.4757 | -73.7 | -73.755 | -73.4046 | -73.3438 | -73.5441 | -73.7026 | -0.12607 | -0.00778 | -0.086628 | -0.060575 | 122.464 | 122.5506 | 122.2095 | 122.4538 | -73.4254 | -73.6496 | -73.7046 | -73.3542 | -73.2935 | -73.4937 | -73.6523 | -0.075719 | 0.042574 | -0.036274 | -0.010221 | 122.5144 | 122.6009 | 122.2598 | 122.5042 | -122.5901 | -122.3355 | -122.5506 | -122.2961
2275.1094 | 122.731 | -122.58 | 0.054932 | -75.069 | -75.298 | -75.33 | -74.9796 | -74.9141 | -75.1419 | -75.2913 | -0.13065 | -0.003202 | -0.086628 | -0.069733 | 122.464 | 122.5506 | 122.2186 | 122.4446 | -75.0187 | -75.2476 | -75.2797 | -74.9292 | -74.8637 | -75.0916 | -75.2409 | -0.080298 | 0.047152 | -0.036274 | -0.019379 | 122.5144 | 122.6009 | 122.269 | 122.495 | -122.5947 | -122.3493 | -122.5506 | -122.3053
2276.8594 | 122.85 | -122.5754 | 0.009155 | -74.5059 | -74.7302 | -74.776 | -74.4301 | -74.3647 | -74.5742 | -74.7327 | -0.12607 | -0.00778 | -0.086628 | -0.074312 | 122.464 | 122.546 | 122.2095 | 122.4446 | -74.4555 | -74.6798 | -74.7256 | -74.3798 | -74.3144 | -74.5238 | -74.6824 | -0.075719 | 0.042574 | -0.036274 | -0.023958 | 122.5144 | 122.5964 | 122.2598 | 122.495 | -122.5901 | -122.3355 | -122.5506 | -122.2961
2278.5469 | 122.7264 | -122.6028 | 0.045776 | -74.9133 | -75.1423 | -75.1835 | -74.8376 | -74.7722 | -74.9817 | -75.1448 | -0.13523 | -0.00778 | -0.086628 | -0.055996 | 122.4594 | 122.5506 | 122.2049 | 122.4401 | -74.863 | -75.0919 | -75.1331 | -74.7873 | -74.7218 | -74.9313 | -75.0944 | -0.084876 | 0.042574 | -0.036274 | -0.005642 | 122.5098 | 122.6009 | 122.2552 | 122.4904 | -122.5947 | -122.3401 | -122.5461 | -122.2915
2280.2812 | 122.7722 | -122.5845 | 0.032043 | -76.0351 | -76.2412 | -76.3053 | -75.941 | -75.88 | -76.1034 | -76.2664 | -0.13065 | -0.012359 | -0.086628 | -0.074312 | 122.4686 | 122.5506 | 122.2095 | 122.4446 | -75.9847 | -76.1908 | -76.2549 | -75.8907 | -75.8297 | -76.053 | -76.2161 | -0.080298 | 0.037995 | -0.036274 | -0.023958 | 122.5189 | 122.6009 | 122.2598 | 122.495 | -122.5992 | -122.3401 | -122.5552 | -122.2961
2282.0312 | 122.8409 | -122.5708 | -0.009155 | -76.8775 | -77.0929 | -77.134 | -76.7743 | -76.7086 | -76.9412 | -77.1088 | -0.13065 | -0.003202 | -0.08205 | -0.065154 | 122.464 | 122.5597 | 122.2141 | 122.4492 | -76.8271 | -77.0425 | -77.0836 | -76.724 | -76.6583 | -76.8909 | -77.0584 | -0.080298 | 0.047152 | -0.031696 | -0.0148 | 122.5144 | 122.6101 | 122.2644 | 122.4996 | -122.5947 | -122.3447 | -122.5461 | -122.2961
2283.75 | 122.7402 | -122.6166 | 0.041199 | -77.3033 | -77.5278 | -77.5781 | -77.223 | -77.1619 | -77.3716 | -77.5575 | -0.13523 | -0.012359 | -0.077472 | -0.069733 | 122.464 | 122.5506 | 122.2186 | 122.4492 | -77.2529 | -77.4775 | -77.5278 | -77.1727 | -77.1115 | -77.3212 | -77.5071 | -0.084876 | 0.037995 | -0.027118 | -0.019379 | 122.5144 | 122.6009 | 122.269 | 122.4996 | -122.5992 | -122.3539 | -122.5415 | -122.2961
2285.4531 | 122.7997 | -122.5616 | 0.022888 | -78.132 | -78.3383 | -78.3977 | -78.0334 | -77.9721 | -78.1957 | -78.3678 | -0.13065 | -0.00778 | -0.08205 | -0.074312 | 122.4686 | 122.5506 | 122.2186 | 122.4538 | -78.0816 | -78.2879 | -78.3473 | -77.9831 | -77.9218 | -78.1453 | -78.3174 | -0.080298 | 0.042574 | -0.031696 | -0.023958 | 122.5189 | 122.6009 | 122.269 | 122.5042 | -122.5992 | -122.3493 | -122.5506 | -122.3007
2287.1562 | 122.7676 | -122.5937 | 0.032043 | -79.011 | -79.2403 | -79.2859 | -78.9308 | -78.8694 | -79.0839 | -79.2697 | -0.13523 | -0.012359 | -0.091207 | -0.065154 | 122.4594 | 122.5506 | 122.2095 | 122.4538 | -78.9607 | -79.19 | -79.2356 | -78.8804 | -78.8191 | -79.0335 | -79.2193 | -0.084876 | 0.037995 | -0.040853 | -0.0148 | 122.5098 | 122.6009 | 122.2598 | 122.5042 | -122.5947 | -122.3447 | -122.5506 | -122.3007
2288.875 | 122.7264 | -122.5983 | 0.027466 | -80.0549 | -80.2935 | -80.3344 | -79.9701 | -79.904 | -80.1278 | -80.3135 | -0.13981 | -0.00778 | -0.091207 | -0.069733 | 122.4594 | 122.5506 | 122.2141 | 122.4492 | -80.0045 | -80.2431 | -80.2841 | -79.9198 | -79.8537 | -80.0774 | -80.2632 | -0.089455 | 0.042574 | -0.040853 | -0.019379 | 122.5098 | 122.6009 | 122.2644 | 122.4996 | -122.5992 | -122.3539 | -122.5506 | -122.3053
2290.5781 | 122.8226 | -122.5891 | 0.004578 | -80.3937 | -80.6231 | -80.6732 | -80.3135 | -80.2382 | -80.4666 | -80.6477 | -0.13981 | -0.00778 | -0.086628 | -0.074312 | 122.464 | 122.5552 | 122.2095 | 122.4538 | -80.3433 | -80.5728 | -80.6229 | -80.2632 | -80.1879 | -80.4162 | -80.5974 | -0.089455 | 0.042574 | -0.036274 | -0.023958 | 122.5144 | 122.6055 | 122.2598 | 122.5042 | -122.6038 | -122.3493 | -122.5506 | -122.2961
2292.2969 | 122.7036 | -122.6212 | 0.018311 | -81.4376 | -81.6763 | -81.7172 | -81.3391 | -81.2866 | -81.5196 | -81.7144 | -0.13523 | -0.003202 | -0.086628 | -0.069733 | 122.4686 | 122.5552 | 122.2095 | 122.4446 | -81.3872 | -81.6259 | -81.6668 | -81.2887 | -81.2362 | -81.4692 | -81.6641 | -0.084876 | 0.047152 | -0.036274 | -0.019379 | 122.5189 | 122.6055 | 122.2598 | 122.495 | -122.6038 | -122.3447 | -122.5552 | -122.2961
2293.9844 | 122.8867 | -122.5662 | 0 | -81.5841 | -81.8045 | -81.8591 | -81.4856 | -81.4194 | -81.657 | -81.8564 | -0.13523 | -0.00778 | -0.08205 | -0.069733 | 122.4686 | 122.5506 | 122.2095 | 122.4492 | -81.5337 | -81.7541 | -81.8087 | -81.4352 | -81.369 | -81.6066 | -81.806 | -0.084876 | 0.042574 | -0.031696 | -0.019379 | 122.5189 | 122.6009 | 122.2598 | 122.4996 | -122.6038 | -122.3447 | -122.5506 | -122.2915
2295.7812 | 122.85 | -122.5525 | 0.013733 | -82.3715 | -82.6058 | -82.6695 | -82.2731 | -82.2113 | -82.4536 | -82.653 | -0.13981 | 0.001377 | -0.086628 | -0.060575 | 122.464 | 122.5552 | 122.2141 | 122.4584 | -82.3212 | -82.5554 | -82.6192 | -82.2228 | -82.161 | -82.4032 | -82.6026 | -0.089455 | 0.051731 | -0.036274 | -0.010221 | 122.5144 | 122.6055 | 122.2644 | 122.5087 | -122.6038 | -122.3539 | -122.5506 | -122.3007
2297.4844 | 122.8638 | -122.5708 | 0 | -82.9667 | -83.2102 | -83.2647 | -82.882 | -82.8156 | -83.0534 | -83.2481 | -0.13065 | -0.003202 | -0.086628 | -0.065154 | 122.4686 | 122.5552 | 122.2095 | 122.4492 | -82.9164 | -83.1598 | -83.2144 | -82.8317 | -82.7653 | -83.003 | -83.1978 | -0.080298 | 0.047152 | -0.036274 | -0.0148 | 122.5189 | 122.6055 | 122.2598 | 122.4996 | -122.5992 | -122.3401 | -122.5552 | -122.2961
2299.1875 | 122.8775 | -122.5525 | 0.013733 | -84.8897 | -85.1195 | -85.1832 | -84.7455 | -84.7063 | -84.9763 | -85.1481 | -0.13065 | -0.00778 | -0.086628 | -0.065154 | 122.464 | 122.5552 | 122.2141 | 122.4538 | -84.8393 | -85.0692 | -85.1328 | -84.6951 | -84.656 | -84.9259 | -85.0977 | -0.080298 | 0.042574 | -0.036274 | -0.0148 | 122.5144 | 122.6055 | 122.2644 | 122.5042 | -122.5947 | -122.3447 | -122.5506 | -122.3007
2300.875 | 122.7768 | -122.5891 | 0.027466 | -84.8439 | -85.0783 | -85.142 | -84.7272 | -84.6743 | -84.9442 | -85.116 | -0.12607 | -0.003202 | -0.086628 | -0.065154 | 122.464 | 122.5552 | 122.2186 | 122.4492 | -84.7935 | -85.028 | -85.0916 | -84.6768 | -84.6239 | -84.8939 | -85.0657 | -0.075719 | 0.047152 | -0.036274 | -0.0148 | 122.5144 | 122.6055 | 122.269 | 122.4996 | -122.5901 | -122.3447 | -122.5506 | -122.3053
2302.5781 | 122.8592 | -122.5845 | 0.013733 | -85.3612 | -85.6049 | -85.6731 | -85.2491 | -85.2007 | -85.457 | -85.6608 | -0.13065 | -0.003202 | -0.086628 | -0.065154 | 122.4686 | 122.5597 | 122.2186 | 122.4584 | -85.3109 | -85.5545 | -85.6227 | -85.1988 | -85.1504 | -85.4067 | -85.6105 | -0.080298 | 0.047152 | -0.036274 | -0.0148 | 122.5189 | 122.6101 | 122.269 | 122.5087 | -122.5992 | -122.3493 | -122.5552 | -122.3053
2304.2969 | 122.7264 | -122.6074 | 0.036621 | -85.8969 | -86.136 | -86.1996 | -85.794 | -85.7409 | -85.9881 | -86.2102 | -0.12607 | -0.012359 | -0.08205 | -0.069733 | 122.464 | 122.5552 | 122.2095 | 122.4492 | -85.8465 | -86.0857 | -86.1493 | -85.7436 | -85.6906 | -85.9378 | -86.1598 | -0.075719 | 0.037995 | -0.031696 | -0.019379 | 122.5144 | 122.6055 | 122.2598 | 122.4996 | -122.5901 | -122.3355 | -122.5461 | -122.2915
2306.0156 | 122.85 | -122.5616 | 0 | -87.2613 | -87.5142 | -87.5503 | -87.1492 | -87.0914 | -87.3479 | -87.5562 | -0.13523 | -0.003202 | -0.08205 | -0.065154 | 122.4686 | 122.5506 | 122.2141 | 122.463 | -87.2109 | -87.4639 | -87.4999 | -87.0988 | -87.0411 | -87.2975 | -87.5058 | -0.084876 | 0.047152 | -0.031696 | -0.0148 | 122.5189 | 122.6009 | 122.2644 | 122.5133 | -122.6038 | -122.3493 | -122.5506 | -122.2961
2307.7188 | 122.7676 | -122.6028 | 0.022888 | -87.014 | -87.2441 | -87.2985 | -86.8974 | -86.8351 | -87.0961 | -87.2952 | -0.13523 | -0.00778 | -0.08205 | -0.069733 | 122.464 | 122.5597 | 122.2141 | 122.4538 | -86.9637 | -87.1937 | -87.2481 | -86.847 | -86.7847 | -87.0457 | -87.2449 | -0.084876 | 0.042574 | -0.031696 | -0.019379 | 122.5144 | 122.6101 | 122.2644 | 122.5042 | -122.5992 | -122.3493 | -122.5461 | -122.2961
2309.4531 | 122.7402 | -122.612 | 0.027466 | -87.3849 | -87.6333 | -87.6831 | -87.2774 | -87.2242 | -87.4807 | -87.689 | -0.13065 | -0.026096 | -0.077472 | -0.069733 | 122.4686 | 122.5552 | 122.2186 | 122.4584 | -87.3345 | -87.5829 | -87.6327 | -87.227 | -87.1739 | -87.4303 | -87.6386 | -0.080298 | 0.024258 | -0.027118 | -0.019379 | 122.5189 | 122.6055 | 122.269 | 122.5087 | -122.5992 | -122.3493 | -122.5461 | -122.2961
2311.1719 | 122.8729 | -122.5708 | -0.009155 | -87.9984 | -88.2469 | -88.292 | -87.8863 | -87.8331 | -88.0804 | -88.307 | -0.12607 | -0.003202 | -0.077472 | -0.065154 | 122.4732 | 122.5643 | 122.2141 | 122.4538 | -87.948 | -88.1965 | -88.2417 | -87.836 | -87.7827 | -88.0301 | -88.2567 | -0.075719 | 0.047152 | -0.027118 | -0.0148 | 122.5235 | 122.6147 | 122.2644 | 122.5042 | -122.5992 | -122.3401 | -122.5506 | -122.2915
2312.9219 | 122.8134 | -122.5616 | -0.004578 | -87.9068 | -88.1324 | -88.2005 | -87.7948 | -87.7507 | -87.9889 | -88.2063 | -0.13065 | -0.016938 | -0.086628 | -0.065154 | 122.4777 | 122.5506 | 122.2186 | 122.4584 | -87.8565 | -88.082 | -88.1501 | -87.7444 | -87.7003 | -87.9385 | -88.1559 | -0.080298 | 0.033416 | -0.036274 | -0.0148 | 122.5281 | 122.6009 | 122.269 | 122.5087 | -122.6084 | -122.3493 | -122.5644 | -122.3053
2314.625 | 122.7631 | -122.5983 | 0.041199 | -88.6577 | -88.897 | -88.9559 | -88.5548 | -88.5015 | -88.7443 | -88.9571 | -0.12607 | -0.003202 | -0.077472 | -0.069733 | 122.4686 | 122.5552 | 122.2186 | 122.4538 | -88.6073 | -88.8467 | -88.9056 | -88.5044 | -88.4511 | -88.6939 | -88.9068 | -0.075719 | 0.047152 | -0.027118 | -0.019379 | 122.5189 | 122.6055 | 122.269 | 122.5042 | -122.5947 | -122.3447 | -122.5461 | -122.2961
2316.3438 | 122.8363 | -122.5937 | -0.013733 | -89.0926 | -89.3366 | -89.3955 | -89.0126 | -88.9501 | -89.1838 | -89.3966 | -0.13065 | -0.012359 | -0.086628 | -0.065154 | 122.4686 | 122.5597 | 122.2141 | 122.4584 | -89.0423 | -89.2863 | -89.3451 | -88.9623 | -88.8997 | -89.1335 | -89.3463 | -0.080298 | 0.037995 | -0.036274 | -0.0148 | 122.5189 | 122.6101 | 122.2644 | 122.5087 | -122.5992 | -122.3447 | -122.5552 | -122.3007
2318.0625 | 122.8317 | -122.5937 | 0.013733 | -89.9167 | -90.17 | -90.2196 | -89.8185 | -89.7695 | -90.0125 | -90.2253 | -0.12607 | -0.016938 | -0.08205 | -0.065154 | 122.4732 | 122.5597 | 122.2232 | 122.4584 | -89.8664 | -90.1196 | -90.1693 | -89.7681 | -89.7192 | -89.9622 | -90.1749 | -0.075719 | 0.033416 | -0.031696 | -0.0148 | 122.5235 | 122.6101 | 122.2736 | 122.5087 | -122.5992 | -122.3493 | -122.5552 | -122.3053
2319.75 | 122.8043 | -122.5754 | 0.022888 | -89.7061 | -89.9502 | -90.0136 | -89.617 | -89.559 | -89.8019 | -90.0101 | -0.12607 | -0.003202 | -0.077472 | -0.065154 | 122.4732 | 122.5597 | 122.2232 | 122.4584 | -89.6558 | -89.8998 | -89.9632 | -89.5667 | -89.5086 | -89.7516 | -89.9597 | -0.075719 | 0.047152 | -0.027118 | -0.0148 | 122.5235 | 122.6101 | 122.2736 | 122.5087 | -122.5992 | -122.3493 | -122.5506 | -122.3007
2321.4531 | 122.7768 | -122.5891 | 0.027466 | -89.8206 | -90.0601 | -90.1097 | -89.7177 | -89.6734 | -89.9026 | -90.1154 | -0.12607 | -0.00778 | -0.08205 | -0.069733 | 122.4732 | 122.5643 | 122.2186 | 122.4584 | -89.7702 | -90.0097 | -90.0594 | -89.6674 | -89.6231 | -89.8523 | -90.065 | -0.075719 | 0.042574 | -0.031696 | -0.019379 | 122.5235 | 122.6147 | 122.269 | 122.5087 | -122.5992 | -122.3447 | -122.5552 | -122.3007
2323.1719 | 122.8409 | -122.58 | 0.004578 | -93.1994 | -93.4438 | -93.5162 | -93.0646 | -93.0199 | -93.2952 | -93.4987 | -0.12607 | -0.003202 | -0.08205 | -0.065154 | 122.4686 | 122.5689 | 122.2095 | 122.4538 | -93.1491 | -93.3935 | -93.4659 | -93.0143 | -92.9695 | -93.2449 | -93.4483 | -0.075719 | 0.047152 | -0.031696 | -0.0148 | 122.5189 | 122.6192 | 122.2598 | 122.5042 | -122.5947 | -122.3355 | -122.5506 | -122.2915
2324.9375 | 122.7402 | -122.612 | 0.036621 | -92.8881 | -93.1416 | -93.1911 | -92.7808 | -92.7269 | -92.9839 | -93.1965 | -0.1215 | -0.012359 | -0.08205 | -0.069733 | 122.4732 | 122.5689 | 122.2186 | 122.4584 | -92.8377 | -93.0913 | -93.1408 | -92.7304 | -92.6766 | -92.9335 | -93.1461 | -0.071141 | 0.037995 | -0.031696 | -0.019379 | 122.5235 | 122.6192 | 122.269 | 122.5087 | -122.5947 | -122.3401 | -122.5552 | -122.3007
2326.625 | 122.8729 | -122.5525 | 0.009155 | -92.7416 | -92.9905 | -93.0538 | -92.6342 | -92.5758 | -92.842 | -93.05 | -0.13065 | -0.003202 | -0.077472 | -0.074312 | 122.4686 | 122.5643 | 122.2186 | 122.4675 | -92.6912 | -92.9402 | -93.0034 | -92.5839 | -92.5255 | -92.7916 | -92.9996 | -0.080298 | 0.047152 | -0.027118 | -0.023958 | 122.5189 | 122.6147 | 122.269 | 122.5179 | -122.5992 | -122.3493 | -122.5461 | -122.2961
2328.3281 | 122.7402 | -122.5983 | 0.045776 | -93.465 | -93.714 | -93.7635 | -93.3622 | -93.3037 | -93.5562 | -93.7596 | -0.13065 | -0.003202 | -0.08205 | -0.069733 | 122.4732 | 122.5643 | 122.2232 | 122.463 | -93.4146 | -93.6636 | -93.7131 | -93.3119 | -93.2534 | -93.5058 | -93.7093 | -0.080298 | 0.047152 | -0.031696 | -0.019379 | 122.5235 | 122.6147 | 122.2736 | 122.5133 | -122.6038 | -122.3539 | -122.5552 | -122.3053
2330.0312 | 122.8088 | -122.58 | 0.041199 | -93.3093 | -93.5629 | -93.6032 | -93.202 | -93.1572 | -93.4051 | -93.6085 | -0.12607 | -0.003202 | -0.08205 | -0.065154 | 122.4732 | 122.5643 | 122.2232 | 122.4675 | -93.259 | -93.5125 | -93.5529 | -93.1516 | -93.1069 | -93.3547 | -93.5582 | -0.075719 | 0.047152 | -0.031696 | -0.0148 | 122.5235 | 122.6147 | 122.2736 | 122.5179 | -122.5992 | -122.3493 | -122.5552 | -122.3053
2331.7344 | 122.7768 | -122.5937 | 0.018311 | -93.1903 | -93.4438 | -93.4979 | -93.0967 | -93.0428 | -93.2815 | -93.4849 | -0.12607 | -0.012359 | -0.086628 | -0.065154 | 122.4823 | 122.5597 | 122.2232 | 122.463 | -93.1399 | -93.3935 | -93.4476 | -93.0463 | -92.9924 | -93.2311 | -93.4346 | -0.075719 | 0.037995 | -0.036274 | -0.0148 | 122.5327 | 122.6101 | 122.2736 | 122.5133 | -122.6084 | -122.3493 | -122.569 | -122.3098
2333.4375 | 122.8409 | -122.5754 | -0.009155 | -93.6939 | -93.9383 | -94.0153 | -93.5957 | -93.5464 | -93.7897 | -93.9885 | -0.13065 | -0.003202 | -0.077472 | -0.065154 | 122.4732 | 122.5643 | 122.2232 | 122.463 | -93.6435 | -93.888 | -93.9649 | -93.5454 | -93.496 | -93.7393 | -93.9382 | -0.080298 | 0.047152 | -0.027118 | -0.0148 | 122.5235 | 122.6147 | 122.2736 | 122.5133 | -122.6038 | -122.3539 | -122.5506 | -122.3007
2335.1406 | 122.8729 | -122.5296 | -0.009155 | -94.0144 | -94.268 | -94.3312 | -93.93 | -93.8668 | -94.1147 | -94.309 | -0.12607 | -0.003202 | -0.072894 | -0.069733 | 122.4777 | 122.5689 | 122.2186 | 122.463 | -93.964 | -94.2176 | -94.2809 | -93.8796 | -93.8165 | -94.0644 | -94.2586 | -0.075719 | 0.047152 | -0.02254 | -0.019379 | 122.5281 | 122.6192 | 122.269 | 122.5133 | -122.6038 | -122.3447 | -122.5506 | -122.2915
2336.9531 | 122.7356 | -122.612 | 0.018311 | -94.2387 | -94.5015 | -94.5464 | -94.1635 | -94.1049 | -94.3391 | -94.5242 | -0.13065 | -0.003202 | -0.077472 | -0.060575 | 122.4732 | 122.5735 | 122.2232 | 122.463 | -94.1884 | -94.4512 | -94.4961 | -94.1131 | -94.0545 | -94.2887 | -94.4738 | -0.080298 | 0.047152 | -0.027118 | -0.010221 | 122.5235 | 122.6238 | 122.2736 | 122.5133 | -122.6038 | -122.3539 | -122.5506 | -122.3007
2338.6875 | 122.8409 | -122.5891 | 0.022888 | -94.4814 | -94.7396 | -94.7982 | -94.4061 | -94.3475 | -94.5817 | -94.7805 | -0.13065 | -0.003202 | -0.072894 | -0.060575 | 122.4777 | 122.5689 | 122.2278 | 122.463 | -94.431 | -94.6893 | -94.7479 | -94.3558 | -94.2972 | -94.5314 | -94.7302 | -0.080298 | 0.047152 | -0.02254 | -0.010221 | 122.5281 | 122.6192 | 122.2781 | 122.5133 | -122.6084 | -122.3584 | -122.5506 | -122.3007
2340.4219 | 122.7814 | -122.5891 | 0.045776 | -94.4997 | -94.7534 | -94.812 | -94.4153 | -94.3704 | -94.6001 | -94.7943 | -0.12607 | 0.001377 | -0.077472 | -0.069733 | 122.4823 | 122.5689 | 122.2278 | 122.4584 | -94.4493 | -94.703 | -94.7616 | -94.3649 | -94.32 | -94.5497 | -94.7439 | -0.075719 | 0.051731 | -0.027118 | -0.019379 | 122.5327 | 122.6192 | 122.2781 | 122.5087 | -122.6084 | -122.3539 | -122.5598 | -122.3053
2342.125 | 122.8363 | -122.5845 | -0.004578 | -95.6855 | -95.9301 | -95.9887 | -95.5965 | -95.5378 | -95.7767 | -95.9754 | -0.13065 | -0.012359 | -0.08205 | -0.065154 | 122.4823 | 122.5689 | 122.2278 | 122.4675 | -95.6351 | -95.8798 | -95.9383 | -95.5462 | -95.4874 | -95.7263 | -95.9251 | -0.080298 | 0.037995 | -0.031696 | -0.0148 | 122.5327 | 122.6192 | 122.2781 | 122.5179 | -122.613 | -122.3584 | -122.5644 | -122.3098
2343.9062 | 122.9004 | -122.5616 | 0.013733 | -95.8824 | -96.1224 | -96.1901 | -95.7934 | -95.7346 | -95.9736 | -96.1632 | -0.12607 | -0.003202 | -0.08205 | -0.069733 | 122.4823 | 122.5643 | 122.2324 | 122.4675 | -95.832 | -96.0721 | -96.1398 | -95.743 | -95.6843 | -95.9232 | -96.1128 | -0.075719 | 0.047152 | -0.031696 | -0.019379 | 122.5327 | 122.6147 | 122.2827 | 122.5179 | -122.6084 | -122.3584 | -122.5644 | -122.3144
2345.625 | 122.8363 | -122.5891 | 0.004578 | -96.0747 | -96.3285 | -96.3916 | -95.9857 | -95.9361 | -96.175 | -96.3646 | -0.13065 | -0.00778 | -0.08205 | -0.065154 | 122.4777 | 122.5735 | 122.2232 | 122.463 | -96.0243 | -96.2781 | -96.3412 | -95.9353 | -95.8857 | -96.1247 | -96.3142 | -0.080298 | 0.042574 | -0.031696 | -0.0148 | 122.5281 | 122.6238 | 122.2736 | 122.5133 | -122.6084 | -122.3539 | -122.5598 | -122.3053
2347.3594 | 122.8409 | -122.5891 | 0.009155 | -96.2166 | -96.4613 | -96.5198 | -96.1368 | -96.078 | -96.317 | -96.4974 | -0.1215 | -0.012359 | -0.077472 | -0.069733 | 122.4915 | 122.5643 | 122.2369 | 122.4721 | -96.1662 | -96.4109 | -96.4694 | -96.0864 | -96.0276 | -96.2666 | -96.447 | -0.071141 | 0.037995 | -0.027118 | -0.019379 | 122.5418 | 122.6147 | 122.2873 | 122.5225 | -122.613 | -122.3584 | -122.569 | -122.3144
2349.0781 | 122.8317 | -122.58 | -0.004578 | -97.027 | -97.2809 | -97.3439 | -96.9243 | -96.8745 | -97.1319 | -97.3214 | -0.13065 | -0.00778 | -0.08205 | -0.065154 | 122.4823 | 122.5735 | 122.2278 | 122.463 | -96.9766 | -97.2305 | -97.2936 | -96.8739 | -96.8242 | -97.0816 | -97.2711 | -0.080298 | 0.042574 | -0.031696 | -0.0148 | 122.5327 | 122.6238 | 122.2781 | 122.5133 | -122.613 | -122.3584 | -122.5644 | -122.3098
2350.7812 | 122.8455 | -122.58 | -0.004578 | -96.8805 | -97.3679 | -97.4309 | -96.9197 | -96.815 | -96.9854 | -97.1703 | -0.12607 | -0.00778 | -0.086628 | -0.065154 | 122.4869 | 122.5689 | 122.2278 | 122.463 | -96.8301 | -97.3175 | -97.3806 | -96.8694 | -96.7647 | -96.935 | -97.12 | -0.075719 | 0.042574 | -0.036274 | -0.0148 | 122.5373 | 122.6192 | 122.2781 | 122.5133 | -122.613 | -122.3539 | -122.5735 | -122.3144
2352.5625 | 122.8409 | -122.6074 | 0.013733 | -96.8576 | -97.3633 | -97.4309 | -96.9106 | -96.7921 | -96.9579 | -97.1475 | -0.13065 | -0.00778 | -0.072894 | -0.055996 | 122.4869 | 122.5826 | 122.2324 | 122.4675 | -96.8072 | -97.3129 | -97.3806 | -96.8602 | -96.7418 | -96.9076 | -97.0971 | -0.080298 | 0.042574 | -0.02254 | -0.005642 | 122.5373 | 122.633 | 122.2827 | 122.5179 | -122.6176 | -122.363 | -122.5598 | -122.3053
2354.2812 | 122.7585 | -122.6074 | 0.032043 | -97.6862 | -98.2287 | -98.2459 | -97.7576 | -97.6574 | -97.7958 | -98.0219 | -0.12607 | -0.003202 | -0.08205 | -0.069733 | 122.4686 | 122.5597 | 122.3697 | 122.463 | -97.6359 | -98.1783 | -98.1956 | -97.7072 | -97.607 | -97.7454 | -97.9715 | -0.075719 | 0.047152 | -0.031696 | -0.019379 | 122.5189 | 122.6101 | 122.4201 | 122.5133 | -122.5947 | -122.4958 | -122.5506 | -122.4518
2356 | 122.8043 | -122.5983 | 0.018311 | -98.4188 | -98.6911 | -98.7541 | -98.3253 | -98.28 | -98.5237 | -98.7132 | -0.13065 | -0.012359 | -0.08205 | -0.065154 | 122.4869 | 122.5826 | 122.2324 | 122.4675 | -98.3684 | -98.6408 | -98.7038 | -98.275 | -98.2296 | -98.4734 | -98.6628 | -0.080298 | 0.037995 | -0.031696 | -0.0148 | 122.5373 | 122.633 | 122.2827 | 122.5179 | -122.6176 | -122.363 | -122.569 | -122.3144
2357.6875 | 122.7905 | -122.6074 | 0.032043 | -98.6752 | -98.9384 | -99.0014 | -98.5771 | -98.5363 | -98.7893 | -98.9696 | -0.13065 | -0.00778 | -0.091207 | -0.065154 | 122.4869 | 122.5643 | 122.2369 | 122.4767 | -98.6248 | -98.888 | -98.951 | -98.5268 | -98.486 | -98.7389 | -98.9192 | -0.080298 | 0.042574 | -0.040853 | -0.0148 | 122.5373 | 122.6147 | 122.2873 | 122.5271 | -122.6176 | -122.3676 | -122.5781 | -122.3281
2359.375 | 122.7905 | -122.5754 | 0.013733 | -98.7027 | -98.9613 | -99.0334 | -98.5909 | -98.5638 | -98.8076 | -98.9879 | -0.13065 | -0.003202 | -0.08205 | -0.065154 | 122.4869 | 122.5735 | 122.2278 | 122.4675 | -98.6523 | -98.9109 | -98.9831 | -98.5405 | -98.5135 | -98.7572 | -98.9375 | -0.080298 | 0.047152 | -0.031696 | -0.0148 | 122.5373 | 122.6238 | 122.2781 | 122.5179 | -122.6176 | -122.3584 | -122.569 | -122.3098
2361.0781 | 122.8363 | -122.58 | 0.009155 | -99.2429 | -99.497 | -99.5554 | -99.1403 | -99.0857 | -99.3478 | -99.5418 | -0.12607 | -0.00778 | -0.08205 | -0.069733 | 122.4869 | 122.5735 | 122.2369 | 122.4721 | -99.1925 | -99.4467 | -99.505 | -99.0899 | -99.0353 | -99.2975 | -99.4915 | -0.075719 | 0.042574 | -0.031696 | -0.019379 | 122.5373 | 122.6238 | 122.2873 | 122.5225 | -122.613 | -122.363 | -122.569 | -122.319
2362.7656 | 122.8867 | -122.5616 | 0.018311 | -99.4306 | -99.932 | -99.9995 | -99.4608 | -99.3512 | -99.5356 | -99.7295 | -0.13065 | -0.012359 | -0.077472 | -0.065154 | 122.4823 | 122.578 | 122.2278 | 122.4721 | -99.3803 | -99.8816 | -99.9492 | -99.4104 | -99.3009 | -99.4852 | -99.6792 | -0.080298 | 0.037995 | -0.027118 | -0.0148 | 122.5327 | 122.6284 | 122.2781 | 122.5225 | -122.613 | -122.3584 | -122.5598 | -122.3053
2364.4531 | 122.8683 | -122.5525 | 0 | -99.9434 | -100.4494 | -100.5123 | -99.9644 | -99.8548 | -100.0438 | -100.2286 | -0.1215 | -0.003202 | -0.08205 | -0.065154 | 122.4823 | 122.5872 | 122.2369 | 122.4721 | -99.893 | -100.399 | -100.462 | -99.9141 | -99.8044 | -99.9934 | -100.1782 | -0.071141 | 0.047152 | -0.031696 | -0.0148 | 122.5327 | 122.6376 | 122.2873 | 122.5225 | -122.6038 | -122.3584 | -122.5644 | -122.319
2366.1562 | 122.7402 | -122.6212 | 0.027466 | -100.2822 | -100.5501 | -100.6085 | -100.1613 | -100.1203 | -100.3917 | -100.5857 | -0.12607 | 0.001377 | -0.08205 | -0.074312 | 122.4915 | 122.578 | 122.2324 | 122.4767 | -100.2318 | -100.4998 | -100.5581 | -100.1109 | -100.07 | -100.3414 | -100.5353 | -0.075719 | 0.051731 | -0.031696 | -0.023958 | 122.5418 | 122.6284 | 122.2827 | 122.5271 | -122.6176 | -122.3584 | -122.5735 | -122.3144
2367.8906 | 122.8317 | -122.5845 | 0 | -100.241 | -100.7196 | -100.7962 | -100.262 | -100.1615 | -100.3551 | -100.5445 | -0.13065 | -0.003202 | -0.086628 | -0.069733 | 122.4915 | 122.578 | 122.2324 | 122.4813 | -100.1906 | -100.6692 | -100.7458 | -100.2117 | -100.1112 | -100.3047 | -100.4941 | -0.080298 | 0.047152 | -0.036274 | -0.019379 | 122.5418 | 122.6284 | 122.2827 | 122.5316 | -122.6221 | -122.363 | -122.5781 | -122.319
2369.5938 | 122.8546 | -122.5983 | 0.009155 | -100.8545 | -101.1179 | -101.1808 | -100.729 | -100.6834 | -100.9594 | -101.1488 | -0.12607 | -0.00778 | -0.08205 | -0.060575 | 122.4869 | 122.578 | 122.2369 | 122.4675 | -100.8041 | -101.0676 | -101.1304 | -100.6787 | -100.633 | -100.9091 | -101.0984 | -0.075719 | 0.042574 | -0.031696 | -0.010221 | 122.5373 | 122.6284 | 122.2873 | 122.5179 | -122.613 | -122.363 | -122.569 | -122.319
2371.2969 | 122.7631 | -122.5983 | 0.036621 | -101.0743 | -101.5895 | -101.6753 | -101.0816 | -100.981 | -101.1975 | -101.364 | -0.12607 | 0.001377 | -0.086628 | -0.065154 | 122.4777 | 122.5735 | 122.2369 | 122.4721 | -101.0239 | -101.5392 | -101.6249 | -101.0312 | -100.9306 | -101.1472 | -101.3136 | -0.075719 | 0.051731 | -0.036274 | -0.0148 | 122.5281 | 122.6238 | 122.2873 | 122.5225 | -122.6038 | -122.363 | -122.5644 | -122.3236
2373.0156 | 122.7448 | -122.644 | 0.022888 | -101.0239 | -101.53 | -101.6066 | -101.0404 | -100.9352 | -101.1243 | -101.3182 | -0.12607 | -0.00778 | -0.08205 | -0.060575 | 122.4869 | 122.578 | 122.2369 | 122.4767 | -100.9735 | -101.4797 | -101.5563 | -100.99 | -100.8848 | -101.0739 | -101.2678 | -0.075719 | 0.042574 | -0.031696 | -0.010221 | 122.5373 | 122.6284 | 122.2873 | 122.5271 | -122.613 | -122.363 | -122.569 | -122.319
2374.7031 | 122.7676 | -122.6257 | 0.018311 | -101.4772 | -101.9558 | -102.0233 | -101.4707 | -101.3793 | -101.5775 | -101.7668 | -0.12607 | -0.012359 | -0.08205 | -0.074312 | 122.4869 | 122.5735 | 122.2324 | 122.4767 | -101.4268 | -101.9055 | -101.9729 | -101.4204 | -101.3289 | -101.5272 | -101.7165 | -0.075719 | 0.037995 | -0.031696 | -0.023958 | 122.5373 | 122.6238 | 122.2827 | 122.5271 | -122.613 | -122.3584 | -122.569 | -122.3144
2376.4062 | 122.8271 | -122.5983 | 0.013733 | -101.7427 | -102.2397 | -102.3117 | -101.7271 | -101.631 | -101.8431 | -102.0324 | -0.13523 | -0.012359 | -0.077472 | -0.065154 | 122.4915 | 122.578 | 122.2415 | 122.4767 | -101.6923 | -102.1894 | -102.2614 | -101.6768 | -101.5807 | -101.7927 | -101.982 | -0.084876 | 0.037995 | -0.027118 | -0.0148 | 122.5418 | 122.6284 | 122.2919 | 122.5271 | -122.6267 | -122.3768 | -122.569 | -122.319
2378.1094 | 122.7997 | -122.5891 | 0.045776 | -102.6263 | -103.1692 | -103.2412 | -102.6199 | -102.5192 | -102.7404 | -102.9251 | -0.13523 | -0.012359 | -0.091207 | -0.069733 | 122.4869 | 122.5826 | 122.2415 | 122.4767 | -102.576 | -103.1189 | -103.1908 | -102.5696 | -102.4688 | -102.6901 | -102.8748 | -0.084876 | 0.037995 | -0.040853 | -0.019379 | 122.5373 | 122.633 | 122.2919 | 122.5271 | -122.6221 | -122.3768 | -122.5781 | -122.3327
2379.8125 | 122.7814 | -122.612 | 0.013733 | -102.6172 | -103.128 | -103.2 | -102.6016 | -102.5192 | -102.7359 | -102.9114 | -0.13065 | -0.012359 | -0.086628 | -0.060575 | 122.4915 | 122.578 | 122.2324 | 122.4767 | -102.5668 | -103.0777 | -103.1496 | -102.5513 | -102.4688 | -102.6855 | -102.861 | -0.080298 | 0.037995 | -0.036274 | -0.010221 | 122.5418 | 122.6284 | 122.2827 | 122.5271 | -122.6221 | -122.363 | -122.5781 | -122.319
2381.5156 | 122.7905 | -122.5845 | 0.022888 | -103.2856 | -103.8011 | -103.8959 | -103.2563 | -103.1738 | -103.4089 | -103.5798 | -0.13065 | -0.00778 | -0.08205 | -0.069733 | 122.4915 | 122.578 | 122.2369 | 122.4675 | -103.2353 | -103.7507 | -103.8456 | -103.206 | -103.1235 | -103.3585 | -103.5294 | -0.080298 | 0.042574 | -0.031696 | -0.019379 | 122.5418 | 122.6284 | 122.2873 | 122.5179 | -122.6221 | -122.3676 | -122.5735 | -122.319
2383.2188 | 122.7951 | -122.612 | 0.018311 | -103.3635 | -103.8927 | -103.9509 | -103.3433 | -103.2608 | -103.4776 | -103.6576 | -0.12607 | -0.003202 | -0.08205 | -0.065154 | 122.4869 | 122.5826 | 122.2369 | 122.4767 | -103.3131 | -103.8423 | -103.9005 | -103.293 | -103.2104 | -103.4272 | -103.6073 | -0.075719 | 0.047152 | -0.031696 | -0.0148 | 122.5373 | 122.633 | 122.2873 | 122.5271 | -122.613 | -122.363 | -122.569 | -122.319
2384.9688 | 122.7585 | -122.6349 | 0.027466 | -103.7847 | -104.3277 | -104.4041 | -103.7783 | -103.6728 | -103.8988 | -104.0925 | -0.1215 | -0.00778 | -0.072894 | -0.060575 | 122.4869 | 122.5735 | 122.2324 | 122.4767 | -103.7343 | -104.2773 | -104.3538 | -103.7279 | -103.6225 | -103.8484 | -104.0422 | -0.071141 | 0.042574 | -0.02254 | -0.010221 | 122.5373 | 122.6238 | 122.2827 | 122.5271 | -122.6084 | -122.3539 | -122.5598 | -122.3053
2386.6719 | 122.8043 | -122.5983 | 0.013733 | -104.0731 | -104.5566 | -104.6193 | -104.021 | -103.9521 | -104.1918 | -104.3672 | -0.1215 | -0.00778 | -0.08205 | -0.069733 | 122.4915 | 122.5735 | 122.2369 | 122.4721 | -104.0227 | -104.5062 | -104.569 | -103.9706 | -103.9017 | -104.1414 | -104.3169 | -0.071141 | 0.042574 | -0.031696 | -0.019379 | 122.5418 | 122.6238 | 122.2873 | 122.5225 | -122.613 | -122.3584 | -122.5735 | -122.319
2388.375 | 122.7539 | -122.6166 | 0.027466 | -105.1399 | -105.6372 | -105.6999 | -105.0832 | -105.005 | -105.2631 | -105.4431 | -0.13065 | -0.012359 | -0.08205 | -0.065154 | 122.4915 | 122.578 | 122.2461 | 122.4767 | -105.0895 | -105.5868 | -105.6495 | -105.0328 | -104.9546 | -105.2128 | -105.3928 | -0.080298 | 0.037995 | -0.031696 | -0.0148 | 122.5418 | 122.6284 | 122.2965 | 122.5271 | -122.6221 | -122.3768 | -122.5735 | -122.3281
2390.0625 | 122.8043 | -122.6028 | 0.036621 | -104.183 | -104.6665 | -104.7338 | -104.1263 | -104.0711 | -104.3017 | -104.4863 | -0.13065 | -0.00778 | -0.08205 | -0.060575 | 122.4915 | 122.5826 | 122.2369 | 122.4767 | -104.1326 | -104.6161 | -104.6834 | -104.0759 | -104.0207 | -104.2513 | -104.4359 | -0.080298 | 0.042574 | -0.031696 | -0.010221 | 122.5418 | 122.633 | 122.2873 | 122.5271 | -122.6221 | -122.3676 | -122.5735 | -122.319
2391.75 | 122.7722 | -122.6532 | 0.045776 | -104.7782 | -105.2709 | -105.3519 | -104.726 | -104.6616 | -104.9014 | -105.0814 | -0.1215 | -0.00778 | -0.08205 | -0.069733 | 122.4823 | 122.578 | 122.2369 | 122.4767 | -104.7278 | -105.2205 | -105.3016 | -104.6757 | -104.6113 | -104.8511 | -105.0311 | -0.071141 | 0.042574 | -0.031696 | -0.019379 | 122.5327 | 122.6284 | 122.2873 | 122.5271 | -122.6038 | -122.3584 | -122.5644 | -122.319
2393.4375 | 122.7585 | -122.612 | 0.036621 | -104.8972 | -105.4083 | -105.4618 | -104.8451 | -104.7715 | -105.0159 | -105.205 | -0.12607 | -0.003202 | -0.08205 | -0.065154 | 122.4961 | 122.578 | 122.2324 | 122.4767 | -104.8469 | -105.3579 | -105.4114 | -104.7947 | -104.7212 | -104.9655 | -105.1547 | -0.075719 | 0.047152 | -0.031696 | -0.0148 | 122.5464 | 122.6284 | 122.2827 | 122.5271 | -122.6221 | -122.3584 | -122.5781 | -122.3144
2395.125 | 122.7585 | -122.612 | 0.054932 | -104.65 | -105.1244 | -105.1871 | -104.5887 | -104.5289 | -104.7595 | -104.9487 | -0.13065 | -0.003202 | -0.077472 | -0.065154 | 122.4961 | 122.5872 | 122.2278 | 122.4813 | -104.5996 | -105.074 | -105.1367 | -104.5383 | -104.4785 | -104.7091 | -104.8983 | -0.080298 | 0.047152 | -0.027118 | -0.0148 | 122.5464 | 122.6376 | 122.2781 | 122.5316 | -122.6267 | -122.3584 | -122.5735 | -122.3053
2396.8125 | 122.7905 | -122.5937 | 0.032043 | -104.7415 | -105.216 | -105.2786 | -104.6803 | -104.625 | -104.8648 | -105.0402 | -0.1215 | -0.003202 | -0.086628 | -0.065154 | 122.4961 | 122.578 | 122.2324 | 122.4813 | -104.6912 | -105.1656 | -105.2283 | -104.6299 | -104.5747 | -104.8144 | -104.9899 | -0.071141 | 0.047152 | -0.036274 | -0.0148 | 122.5464 | 122.6284 | 122.2827 | 122.5316 | -122.6176 | -122.3539 | -122.5827 | -122.319
2398.5 | 122.7722 | -122.5891 | 0.032043 | -105.1673 | -105.6555 | -105.7182 | -105.1244 | -105.0554 | -105.2906 | -105.466 | -0.12607 | -0.00778 | -0.086628 | -0.065154 | 122.4961 | 122.5872 | 122.2415 | 122.4721 | -105.117 | -105.6052 | -105.6678 | -105.074 | -105.005 | -105.2402 | -105.4156 | -0.075719 | 0.042574 | -0.036274 | -0.0148 | 122.5464 | 122.6376 | 122.2919 | 122.5225 | -122.6221 | -122.3676 | -122.5827 | -122.3281
2400.2188 | 122.8317 | -122.5845 | 0.009155 | -105.1307 | -105.5868 | -105.6449 | -105.0649 | -105.0142 | -105.2448 | -105.4202 | -0.13065 | 0.001377 | -0.077472 | -0.060575 | 122.4915 | 122.578 | 122.2369 | 122.4675 | -105.0804 | -105.5365 | -105.5946 | -105.0145 | -104.9638 | -105.1945 | -105.3699 | -0.080298 | 0.051731 | -0.027118 | -0.010221 | 122.5418 | 122.6284 | 122.2873 | 122.5179 | -122.6221 | -122.3676 | -122.569 | -122.3144
2401.9531 | 122.7997 | -122.612 | 0.036621 | -106.17 | -106.6858 | -106.7484 | -106.1133 | -106.0488 | -106.2841 | -106.4686 | -0.12607 | -0.00778 | -0.08205 | -0.065154 | 122.4915 | 122.5826 | 122.2461 | 122.4767 | -106.1196 | -106.6354 | -106.698 | -106.063 | -105.9984 | -106.2337 | -106.4183 | -0.075719 | 0.042574 | -0.031696 | -0.0148 | 122.5418 | 122.633 | 122.2965 | 122.5271 | -122.6176 | -122.3722 | -122.5735 | -122.3281
2403.6562 | 122.7356 | -122.6303 | 0.041199 | -106.6004 | -107.1162 | -107.1788 | -106.5483 | -106.4883 | -106.719 | -106.899 | -0.11692 | 0.001377 | -0.077472 | -0.060575 | 122.4869 | 122.578 | 122.2369 | 122.4767 | -106.55 | -107.0658 | -107.1284 | -106.4979 | -106.4379 | -106.6687 | -106.8486 | -0.066562 | 0.051731 | -0.027118 | -0.010221 | 122.5373 | 122.6284 | 122.2873 | 122.5271 | -122.6038 | -122.3539 | -122.5644 | -122.3144
2405.3438 | 122.8912 | -122.5708 | 0 | -106.2616 | -106.7361 | -106.8079 | -106.1912 | -106.1449 | -106.3711 | -106.5556 | -0.12607 | -0.00778 | -0.077472 | -0.065154 | 122.4869 | 122.5826 | 122.2324 | 122.4813 | -106.2112 | -106.6858 | -106.7575 | -106.1408 | -106.0946 | -106.3207 | -106.5053 | -0.075719 | 0.042574 | -0.027118 | -0.0148 | 122.5373 | 122.633 | 122.2827 | 122.5316 | -122.613 | -122.3584 | -122.5644 | -122.3098
2407.0469 | 122.8958 | -122.5937 | -0.009155 | -106.8613 | -107.368 | -107.4443 | -106.8001 | -106.7492 | -106.9846 | -107.1645 | -0.12607 | -0.003202 | -0.08205 | -0.074312 | 122.4915 | 122.578 | 122.2369 | 122.4721 | -106.811 | -107.3176 | -107.394 | -106.7497 | -106.6988 | -106.9342 | -107.1141 | -0.075719 | 0.047152 | -0.031696 | -0.023958 | 122.5418 | 122.6284 | 122.2873 | 122.5225 | -122.6176 | -122.363 | -122.5735 | -122.319
2408.7344 | 122.8958 | -122.58 | 0.009155 | -108.4592 | -108.9935 | -109.0514 | -108.3705 | -108.3149 | -108.5779 | -108.7531 | -0.12607 | -0.00778 | -0.086628 | -0.060575 | 122.4869 | 122.5826 | 122.2415 | 122.4767 | -108.4088 | -108.9431 | -109.0011 | -108.3202 | -108.2645 | -108.5275 | -108.7028 | -0.075719 | 0.042574 | -0.036274 | -0.010221 | 122.5373 | 122.633 | 122.2919 | 122.5271 | -122.613 | -122.3676 | -122.5735 | -122.3281
2410.4375 | 122.7585 | -122.644 | 0.045776 | -108.2761 | -108.7828 | -108.8545 | -108.1691 | -108.1363 | -108.3993 | -108.5746 | -0.11692 | 0.001377 | -0.077472 | -0.069733 | 122.4915 | 122.578 | 122.2415 | 122.4767 | -108.2257 | -108.7325 | -108.8042 | -108.1187 | -108.086 | -108.349 | -108.5242 | -0.066562 | 0.051731 | -0.027118 | -0.019379 | 122.5418 | 122.6284 | 122.2919 | 122.5271 | -122.6084 | -122.3584 | -122.569 | -122.319
2412.1406 | 122.8592 | -122.5754 | 0.004578 | -108.1936 | -108.705 | -108.7767 | -108.1004 | -108.0585 | -108.3215 | -108.4876 | -0.12607 | 0.005956 | -0.08205 | -0.069733 | 122.4961 | 122.578 | 122.2415 | 122.4859 | -108.1433 | -108.6547 | -108.7263 | -108.05 | -108.0081 | -108.2711 | -108.4372 | -0.075719 | 0.05631 | -0.031696 | -0.019379 | 122.5464 | 122.6284 | 122.2919 | 122.5362 | -122.6221 | -122.3676 | -122.5781 | -122.3236
2413.8906 | 122.7493 | -122.6395 | 0.036621 | -107.6854 | -108.1739 | -108.241 | -107.5922 | -107.5549 | -107.8087 | -107.9794 | -0.12607 | -0.003202 | -0.08205 | -0.060575 | 122.4961 | 122.5826 | 122.2415 | 122.4721 | -107.6351 | -108.1235 | -108.1907 | -107.5418 | -107.5046 | -107.7584 | -107.9291 | -0.075719 | 0.047152 | -0.031696 | -0.010221 | 122.5464 | 122.633 | 122.2919 | 122.5225 | -122.6221 | -122.3676 | -122.5781 | -122.3236
2415.5781 | 122.7493 | -122.6212 | 0.032043 | -105.9777 | -106.8002 | -106.8628 | -106.1957 | -106.035 | -106.0964 | -106.2763 | -0.12607 | -0.003202 | -0.086628 | -0.055996 | 122.4869 | 122.578 | 122.2369 | 122.4813 | -105.9274 | -106.7499 | -106.8125 | -106.1454 | -105.9847 | -106.046 | -106.226 | -0.075719 | 0.047152 | -0.036274 | -0.005642 | 122.5373 | 122.6284 | 122.2873 | 122.5316 | -122.613 | -122.363 | -122.5735 | -122.3236
2417.2656 | 122.8958 | -122.5845 | -0.009155 | -105.2085 | -106.1592 | -106.2081 | -105.5364 | -105.3483 | -105.3226 | -105.498 | -0.12607 | 0.001377 | -0.077472 | -0.069733 | 122.4823 | 122.5735 | 122.2369 | 122.4721 | -105.1582 | -106.1088 | -106.1578 | -105.4861 | -105.298 | -105.2723 | -105.4477 | -0.075719 | 0.051731 | -0.027118 | -0.019379 | 122.5327 | 122.6238 | 122.2873 | 122.5225 | -122.6084 | -122.363 | -122.5598 | -122.3144
2418.9844 | 122.8821 | -122.58 | -0.004578 | -108.1433 | -108.6867 | -108.7172 | -108.0912 | -108.0402 | -108.3077 | -108.4876 | -0.1215 | 0.001377 | -0.072894 | -0.069733 | 122.4869 | 122.578 | 122.2369 | 122.4767 | -108.0929 | -108.6363 | -108.6668 | -108.0409 | -107.9898 | -108.2574 | -108.4372 | -0.071141 | 0.051731 | -0.02254 | -0.019379 | 122.5373 | 122.6284 | 122.2873 | 122.5271 | -122.6084 | -122.3584 | -122.5598 | -122.3098
2420.6719 | 122.7631 | -122.6166 | 0.050354 | -108.2806 | -108.8057 | -108.8271 | -108.2149 | -108.1729 | -108.4451 | -108.6204 | -0.1215 | -0.003202 | -0.08205 | -0.055996 | 122.4777 | 122.5689 | 122.2415 | 122.4584 | -108.2303 | -108.7554 | -108.7767 | -108.1645 | -108.1226 | -108.3947 | -108.57 | -0.071141 | 0.047152 | -0.031696 | -0.005642 | 122.5281 | 122.6192 | 122.2919 | 122.5087 | -122.5992 | -122.363 | -122.5598 | -122.3236
2422.3906 | 122.8043 | -122.6028 | 0.032043 | -108.4409 | -108.966 | -108.9965 | -108.3751 | -108.3377 | -108.6099 | -108.7898 | -0.12607 | 0.001377 | -0.08205 | -0.060575 | 122.4732 | 122.5735 | 122.2369 | 122.4767 | -108.3905 | -108.9156 | -108.9461 | -108.3248 | -108.2874 | -108.5596 | -108.7394 | -0.075719 | 0.051731 | -0.031696 | -0.010221 | 122.5235 | 122.6238 | 122.2873 | 122.5271 | -122.5992 | -122.363 | -122.5552 | -122.319
2424.0781 | 122.8683 | -122.5845 | 0.009155 | -109.2558 | -109.8543 | -109.8939 | -109.2221 | -109.1572 | -109.4249 | -109.5909 | -0.1215 | -0.003202 | -0.077472 | -0.065154 | 122.4777 | 122.5689 | 122.2324 | 122.4675 | -109.2055 | -109.8039 | -109.8435 | -109.1718 | -109.1068 | -109.3745 | -109.5406 | -0.071141 | 0.047152 | -0.027118 | -0.0148 | 122.5281 | 122.6192 | 122.2827 | 122.5179 | -122.5992 | -122.3539 | -122.5552 | -122.3098
2425.7656 | 122.8683 | -122.5616 | 0.013733 | -109.1276 | -109.662 | -109.7016 | -109.0527 | -108.997 | -109.2875 | -109.4627 | -0.11692 | 0.001377 | -0.072894 | -0.060575 | 122.4869 | 122.578 | 122.2232 | 122.4721 | -109.0773 | -109.6116 | -109.6512 | -109.0024 | -108.9466 | -109.2372 | -109.4124 | -0.066562 | 0.051731 | -0.02254 | -0.010221 | 122.5373 | 122.6284 | 122.2736 | 122.5225 | -122.6038 | -122.3401 | -122.5598 | -122.2961
2427.4688 | 122.7951 | -122.58 | 0.036621 | -108.8713 | -109.4147 | -109.4406 | -108.8055 | -108.7589 | -109.0357 | -109.2064 | -0.1215 | 0.005956 | -0.08205 | -0.060575 | 122.4732 | 122.5643 | 122.2324 | 122.4675 | -108.8209 | -109.3644 | -109.3902 | -108.7551 | -108.7086 | -108.9854 | -109.156 | -0.071141 | 0.05631 | -0.031696 | -0.010221 | 122.5235 | 122.6147 | 122.2827 | 122.5179 | -122.5947 | -122.3539 | -122.5552 | -122.3144
2429.1719 | 122.7264 | -122.6074 | 0.022888 | -109.4802 | -110.0329 | -110.0587 | -109.4053 | -109.3678 | -109.6401 | -109.8061 | -0.1215 | -0.003202 | -0.072894 | -0.060575 | 122.4823 | 122.5643 | 122.2278 | 122.4721 | -109.4298 | -109.9825 | -110.0084 | -109.3549 | -109.3174 | -109.5897 | -109.7558 | -0.071141 | 0.047152 | -0.02254 | -0.010221 | 122.5327 | 122.6147 | 122.2781 | 122.5225 | -122.6038 | -122.3493 | -122.5552 | -122.3007
2430.9219 | 122.7448 | -122.612 | 0.032043 | -109.8877 | -110.5274 | -110.5532 | -109.8494 | -109.7981 | -110.0475 | -110.2227 | -0.1215 | -0.00778 | -0.077472 | -0.055996 | 122.4732 | 122.5689 | 122.2232 | 122.463 | -109.8373 | -110.477 | -110.5028 | -109.799 | -109.7478 | -109.9972 | -110.1724 | -0.071141 | 0.042574 | -0.027118 | -0.005642 | 122.5235 | 122.6192 | 122.2736 | 122.5133 | -122.5947 | -122.3447 | -122.5506 | -122.3007
2432.6094 | 122.8226 | -122.6028 | 0.013733 | -110.5698 | -111.1364 | -111.1622 | -110.4949 | -110.4573 | -110.7389 | -110.914 | -0.1215 | 0.001377 | -0.08205 | -0.065154 | 122.4777 | 122.5689 | 122.2324 | 122.4721 | -110.5195 | -111.086 | -111.1118 | -110.4446 | -110.407 | -110.6885 | -110.8637 | -0.071141 | 0.051731 | -0.031696 | -0.0148 | 122.5281 | 122.6192 | 122.2827 | 122.5225 | -122.5992 | -122.3539 | -122.5598 | -122.3144
2434.3281 | 122.8958 | -122.5708 | 0.004578 | -109.993 | -110.619 | -110.6494 | -109.9776 | -109.9171 | -110.162 | -110.328 | -0.11692 | -0.003202 | -0.077472 | -0.060575 | 122.4777 | 122.5689 | 122.2278 | 122.4721 | -109.9426 | -110.5686 | -110.599 | -109.9272 | -109.8668 | -110.1116 | -110.2777 | -0.066562 | 0.047152 | -0.027118 | -0.010221 | 122.5281 | 122.6192 | 122.2781 | 122.5225 | -122.5947 | -122.3447 | -122.5552 | -122.3053
2436.0469 | 122.7493 | -122.612 | 0.050354 | -110.5332 | -111.0539 | -111.0889 | -110.4721 | -110.4207 | -110.6931 | -110.8637 | -0.11692 | 0.001377 | -0.077472 | -0.060575 | 122.4686 | 122.5643 | 122.2324 | 122.463 | -110.4829 | -111.0036 | -111.0385 | -110.4217 | -110.3704 | -110.6427 | -110.8133 | -0.066562 | 0.051731 | -0.027118 | -0.010221 | 122.5189 | 122.6147 | 122.2827 | 122.5133 | -122.5855 | -122.3493 | -122.5461 | -122.3098
2437.7656 | 122.7676 | -122.6212 | 0.032043 | -110.1395 | -110.6419 | -110.6768 | -110.0737 | -110.0362 | -110.3039 | -110.4745 | -0.1215 | 0.001377 | -0.077472 | -0.065154 | 122.4732 | 122.5643 | 122.2141 | 122.463 | -110.0891 | -110.5915 | -110.6265 | -110.0234 | -109.9858 | -110.2536 | -110.4242 | -0.071141 | 0.051731 | -0.027118 | -0.0148 | 122.5235 | 122.6147 | 122.2644 | 122.5133 | -122.5947 | -122.3355 | -122.5506 | -122.2915
2439.4844 | 122.8592 | -122.5708 | 0.032043 | -109.851 | -110.3305 | -110.3746 | -109.7715 | -109.7432 | -110.0292 | -110.1953 | -0.1215 | 0.001377 | -0.077472 | -0.055996 | 122.464 | 122.5597 | 122.2278 | 122.463 | -109.8007 | -110.2801 | -110.3243 | -109.7212 | -109.6928 | -109.9789 | -110.1449 | -0.071141 | 0.051731 | -0.027118 | -0.005642 | 122.5144 | 122.6101 | 122.2781 | 122.5133 | -122.5855 | -122.3493 | -122.5415 | -122.3053
2441.1719 | 122.7768 | -122.5845 | 0.027466 | -110.2677 | -110.8067 | -110.8371 | -110.2294 | -110.1781 | -110.4367 | -110.6073 | -0.1215 | 0.005956 | -0.077472 | -0.055996 | 122.4732 | 122.5552 | 122.2278 | 122.463 | -110.2173 | -110.7563 | -110.7867 | -110.179 | -110.1277 | -110.3863 | -110.5569 | -0.071141 | 0.05631 | -0.027118 | -0.005642 | 122.5235 | 122.6055 | 122.2781 | 122.5133 | -122.5947 | -122.3493 | -122.5506 | -122.3053
2442.9219 | 122.7539 | -122.612 | 0.041199 | -110.1898 | -110.6785 | -110.7043 | -110.1195 | -110.0911 | -110.3589 | -110.5249 | -0.11692 | 0.005956 | -0.077472 | -0.060575 | 122.4686 | 122.5597 | 122.2186 | 122.4584 | -110.1395 | -110.6281 | -110.6539 | -110.0692 | -110.0408 | -110.3085 | -110.4745 | -0.066562 | 0.05631 | -0.027118 | -0.010221 | 122.5189 | 122.6101 | 122.269 | 122.5087 | -122.5855 | -122.3355 | -122.5461 | -122.2961
2444.6094 | 122.7814 | -122.5983 | 0.032043 | -110.5973 | -111.0494 | -111.0797 | -110.5041 | -110.494 | -110.7709 | -110.9369 | -0.11692 | 0.005956 | -0.08205 | -0.060575 | 122.4594 | 122.5552 | 122.2232 | 122.4538 | -110.5469 | -110.999 | -111.0294 | -110.4538 | -110.4436 | -110.7206 | -110.8866 | -0.066562 | 0.05631 | -0.031696 | -0.010221 | 122.5098 | 122.6055 | 122.2736 | 122.5042 | -122.5763 | -122.3401 | -122.5415 | -122.3053
2446.3281 | 122.8821 | -122.5479 | 0.013733 | -110.6934 | -111.1089 | -111.1301 | -110.5728 | -110.5626 | -110.8579 | -111.0285 | -0.11692 | -0.003202 | -0.072894 | -0.055996 | 122.4686 | 122.5552 | 122.2232 | 122.463 | -110.6431 | -111.0585 | -111.0798 | -110.5224 | -110.5123 | -110.8076 | -110.9781 | -0.066562 | 0.047152 | -0.02254 | -0.005642 | 122.5189 | 122.6055 | 122.2736 | 122.5133 | -122.5855 | -122.3401 | -122.5415 | -122.2961
2448.0312 | 122.7676 | -122.5845 | 0.045776 | -110.4096 | -110.8433 | -110.8737 | -110.2935 | -110.2834 | -110.5786 | -110.7492 | -0.11692 | 0.010535 | -0.068315 | -0.060575 | 122.464 | 122.5552 | 122.2141 | 122.463 | -110.3592 | -110.793 | -110.8233 | -110.2431 | -110.233 | -110.5283 | -110.6989 | -0.066562 | 0.060889 | -0.017961 | -0.010221 | 122.5144 | 122.6055 | 122.2644 | 122.5133 | -122.5809 | -122.331 | -122.5323 | -122.2824
2449.7344 | 122.7631 | -122.6166 | 0.050354 | -110.1852 | -110.6098 | -110.6448 | -110.0554 | -110.0591 | -110.3589 | -110.5203 | -0.11234 | 0.001377 | -0.072894 | -0.060575 | 122.4594 | 122.5552 | 122.2141 | 122.4584 | -110.1349 | -110.5594 | -110.5944 | -110.0051 | -110.0087 | -110.3085 | -110.4699 | -0.061984 | 0.051731 | -0.02254 | -0.010221 | 122.5098 | 122.6055 | 122.2644 | 122.5087 | -122.5718 | -122.3264 | -122.5323 | -122.2869
2451.4219 | 122.7127 | -122.5983 | 0.045776 | -110.46 | -110.8708 | -110.9103 | -110.3118 | -110.3337 | -110.6244 | -110.7996 | -0.11692 | 0.001377 | -0.077472 | -0.065154 | 122.4594 | 122.5597 | 122.2095 | 122.4538 | -110.4096 | -110.8204 | -110.86 | -110.2615 | -110.2834 | -110.5741 | -110.7492 | -0.066562 | 0.051731 | -0.027118 | -0.0148 | 122.5098 | 122.6101 | 122.2598 | 122.5042 | -122.5763 | -122.3264 | -122.5369 | -122.2869
2453.125 | 122.8455 | -122.5708 | 0.022888 | -110.611 | -110.9944 | -111.0294 | -110.4583 | -110.4757 | -110.7801 | -110.9552 | -0.1215 | 0.005956 | -0.072894 | -0.060575 | 122.4594 | 122.5506 | 122.2141 | 122.4538 | -110.5607 | -110.9441 | -110.979 | -110.408 | -110.4253 | -110.7297 | -110.9049 | -0.071141 | 0.05631 | -0.02254 | -0.010221 | 122.5098 | 122.6009 | 122.2644 | 122.5042 | -122.5809 | -122.3355 | -122.5323 | -122.2869
2454.8281 | 122.7356 | -122.6166 | 0.045776 | -111.3298 | -111.7637 | -111.794 | -111.1863 | -111.1944 | -111.4989 | -111.674 | -0.1215 | 0.005956 | -0.068315 | -0.060575 | 122.4503 | 122.5552 | 122.2141 | 122.4492 | -111.2795 | -111.7133 | -111.7436 | -111.1359 | -111.144 | -111.4485 | -111.6236 | -0.071141 | 0.05631 | -0.017961 | -0.010221 | 122.5006 | 122.6055 | 122.2644 | 122.4996 | -122.5718 | -122.3355 | -122.5186 | -122.2824
2456.5312 | 122.7768 | -122.6074 | 0.027466 | -111.3482 | -111.7682 | -111.8077 | -111.1955 | -111.2127 | -111.5172 | -111.6923 | -0.11234 | 0.001377 | -0.068315 | -0.055996 | 122.4549 | 122.546 | 122.2095 | 122.4584 | -111.2978 | -111.7179 | -111.7574 | -111.1451 | -111.1624 | -111.4668 | -111.642 | -0.061984 | 0.051731 | -0.017961 | -0.005642 | 122.5052 | 122.5964 | 122.2598 | 122.5087 | -122.5672 | -122.3218 | -122.5232 | -122.2778
2458.2344 | 122.7951 | -122.5891 | 0.041199 | -111.3848 | -111.7545 | -111.7803 | -111.2092 | -111.231 | -111.5492 | -111.7244 | -0.11234 | 0.001377 | -0.063737 | -0.060575 | 122.4503 | 122.546 | 122.2095 | 122.4492 | -111.3344 | -111.7041 | -111.7299 | -111.1588 | -111.1807 | -111.4989 | -111.674 | -0.061984 | 0.051731 | -0.013383 | -0.010221 | 122.5006 | 122.5964 | 122.2598 | 122.4996 | -122.5626 | -122.3218 | -122.514 | -122.2732
2459.9844 | 122.7722 | -122.5983 | 0.050354 | -111.4077 | -111.8003 | -111.8261 | -111.2504 | -111.2722 | -111.5813 | -111.7427 | -0.11234 | 0.005956 | -0.072894 | -0.051417 | 122.4457 | 122.5368 | 122.2141 | 122.4446 | -111.3573 | -111.7499 | -111.7757 | -111.2 | -111.2219 | -111.5309 | -111.6923 | -0.061984 | 0.05631 | -0.02254 | -0.001063 | 122.4961 | 122.5872 | 122.2644 | 122.495 | -122.558 | -122.3264 | -122.5186 | -122.2869
2461.6875 | 122.8226 | -122.5433 | 0.009155 | -111.6229 | -112.0247 | -112.0458 | -111.4564 | -111.4828 | -111.7873 | -111.9624 | -0.11692 | 0.010535 | -0.077472 | -0.055996 | 122.4503 | 122.5368 | 122.2003 | 122.4492 | -111.5725 | -111.9743 | -111.9955 | -111.4061 | -111.4325 | -111.737 | -111.9121 | -0.066562 | 0.060889 | -0.027118 | -0.005642 | 122.5006 | 122.5872 | 122.2507 | 122.4996 | -122.5672 | -122.3172 | -122.5277 | -122.2778
2463.3906 | 122.8638 | -122.5571 | 0.027466 | -111.3161 | -111.6858 | -111.7162 | -111.1268 | -111.1578 | -111.4852 | -111.6557 | -0.11692 | 0.001377 | -0.068315 | -0.051417 | 122.4411 | 122.5414 | 122.2095 | 122.4446 | -111.2658 | -111.6355 | -111.6658 | -111.0764 | -111.1074 | -111.4348 | -111.6053 | -0.066562 | 0.051731 | -0.017961 | -0.001063 | 122.4915 | 122.5918 | 122.2598 | 122.495 | -122.558 | -122.3264 | -122.5094 | -122.2778
2465.0938 | 122.7448 | -122.5845 | 0.041199 | -111.5084 | -111.8644 | -111.8902 | -111.287 | -111.3317 | -111.682 | -111.848 | -0.11234 | 0.010535 | -0.068315 | -0.051417 | 122.4411 | 122.5368 | 122.1957 | 122.4446 | -111.458 | -111.814 | -111.8398 | -111.2367 | -111.2814 | -111.6317 | -111.7976 | -0.061984 | 0.060889 | -0.017961 | -0.001063 | 122.4915 | 122.5872 | 122.2461 | 122.495 | -122.5535 | -122.3081 | -122.5094 | -122.2641
2466.7969 | 122.8546 | -122.5021 | 0.022888 | -112.3188 | -112.7069 | -112.728 | -112.1249 | -112.1558 | -112.4878 | -112.6583 | -0.11234 | 0.005956 | -0.072894 | -0.060575 | 122.432 | 122.5323 | 122.1912 | 122.4401 | -112.2684 | -112.6565 | -112.6777 | -112.0745 | -112.1054 | -112.4375 | -112.608 | -0.061984 | 0.05631 | -0.02254 | -0.010221 | 122.4823 | 122.5826 | 122.2415 | 122.4904 | -122.5443 | -122.3035 | -122.5049 | -122.2641
2468.5781 | 122.7493 | -122.5708 | 0.054932 | -112.2638 | -112.6153 | -112.6548 | -112.0654 | -112.11 | -112.4375 | -112.5988 | -0.10776 | 0.015114 | -0.068315 | -0.055996 | 122.4365 | 122.5231 | 122.2003 | 122.4401 | -112.2135 | -112.565 | -112.6044 | -112.015 | -112.0596 | -112.3871 | -112.5484 | -0.057405 | 0.065468 | -0.017961 | -0.005642 | 122.4869 | 122.5735 | 122.2507 | 122.4904 | -122.5443 | -122.3081 | -122.5049 | -122.2686
2470.3594 | 122.7951 | -122.5433 | 0.027466 | -112.7766 | -113.1877 | -113.2179 | -112.5919 | -112.6227 | -112.9457 | -113.1115 | -0.11234 | 0.005956 | -0.068315 | -0.055996 | 122.432 | 122.5185 | 122.1957 | 122.4355 | -112.7263 | -113.1373 | -113.1676 | -112.5415 | -112.5724 | -112.8953 | -113.0612 | -0.061984 | 0.05631 | -0.017961 | -0.005642 | 122.4823 | 122.5689 | 122.2461 | 122.4858 | -122.5443 | -122.3081 | -122.5003 | -122.2641
2472.125 | 122.8043 | -122.5479 | 0.022888 | -112.4195 | -112.8168 | -112.8425 | -112.2165 | -112.2427 | -112.5885 | -112.7682 | -0.11234 | 0.005956 | -0.068315 | -0.055996 | 122.4091 | 122.5048 | 122.1866 | 122.4309 | -112.3691 | -112.7664 | -112.7921 | -112.1661 | -112.1924 | -112.5382 | -112.7178 | -0.061984 | 0.05631 | -0.017961 | -0.005642 | 122.4594 | 122.5551 | 122.2369 | 122.4813 | -122.5214 | -122.2989 | -122.4774 | -122.2549
2473.8281 | 122.7905 | -122.525 | 0.064087 | -112.305 | -112.6703 | -112.6914 | -112.1066 | -112.1375 | -112.4741 | -112.6354 | -0.10776 | 0.010535 | -0.063737 | -0.060575 | 122.3908 | 122.4911 | 122.1683 | 122.4218 | -112.2547 | -112.6199 | -112.6411 | -112.0562 | -112.0871 | -112.4237 | -112.5851 | -0.057405 | 0.060889 | -0.013383 | -0.010221 | 122.4411 | 122.5414 | 122.2186 | 122.4721 | -122.4985 | -122.276 | -122.4545 | -122.232
2475.5781 | 122.8134 | -122.5021 | 0.013733 | -112.2272 | -112.6107 | -112.6502 | -112.0471 | -112.0779 | -112.41 | -112.5713 | -0.094024 | 0.033429 | -0.05458 | -0.033101 | 122.3084 | 122.3949 | 122.1087 | 122.3348 | -112.1769 | -112.5604 | -112.5998 | -111.9967 | -112.0276 | -112.3596 | -112.521 | -0.04367 | 0.083783 | -0.004226 | 0.017253 | 122.3587 | 122.4453 | 122.1591 | 122.3851 | -122.4024 | -122.2028 | -122.3629 | -122.1633
2477.2812 | 122.5937 | -122.4335 | 0.041199 | -111.545 | -111.9285 | -111.968 | -111.3786 | -111.4096 | -111.7232 | -111.8846 | -0.002454 | 0.11585 | 0.004937 | 0.026427 | 121.965 | 122.0607 | 121.8798 | 122.1242 | -111.4947 | -111.8781 | -111.9176 | -111.3282 | -111.3592 | -111.6729 | -111.8342 | 0.0479 | 0.1662 | 0.055291 | 0.076781 | 122.0153 | 122.1111 | 121.9302 | 122.1745 | -121.9674 | -121.8823 | -121.9601 | -121.8749
2479.0469 | 122.6578 | -122.4792 | 0.064087 | -111.6 | -111.988 | -112.0229 | -111.4564 | -111.492 | -111.7736 | -111.9395 | -0.10776 | 0.019693 | -0.063737 | -0.051417 | 122.2946 | 122.3903 | 122.1179 | 122.3119 | -111.5496 | -111.9377 | -111.9726 | -111.4061 | -111.4416 | -111.7232 | -111.8892 | -0.057405 | 0.070047 | -0.013383 | -0.001063 | 122.345 | 122.4407 | 122.1683 | 122.3622 | -122.4024 | -122.2257 | -122.3584 | -122.1816
2480.75 | 122.7539 | -122.4472 | 0.018311 | -111.719 | -112.1208 | -112.1511 | -111.5709 | -111.5973 | -111.888 | -112.0631 | -0.11234 | 0.010535 | -0.072894 | -0.060575 | 122.3633 | 122.4453 | 122.1271 | 122.3668 | -111.6687 | -112.0705 | -112.1008 | -111.5205 | -111.5469 | -111.8377 | -112.0128 | -0.061984 | 0.060889 | -0.02254 | -0.010221 | 122.4136 | 122.4956 | 122.1774 | 122.4172 | -122.4756 | -122.2394 | -122.4362 | -122.2
2482.5156 | 122.8592 | -122.493 | 0.018311 | -112.0166 | -112.4367 | -112.4487 | -111.8685 | -111.8948 | -112.1948 | -112.3561 | -0.11692 | 0.005956 | -0.077472 | -0.060575 | 122.3679 | 122.459 | 122.15 | 122.3622 | -111.9662 | -112.3864 | -112.3984 | -111.8181 | -111.8445 | -112.1444 | -112.3058 | -0.066562 | 0.05631 | -0.027118 | -0.010221 | 122.4182 | 122.5094 | 122.2003 | 122.4126 | -122.4848 | -122.2669 | -122.4453 | -122.2274
2484.2656 | 122.7127 | -122.4655 | 0.050354 | -112.099 | -112.5604 | -112.5861 | -111.9784 | -112.0001 | -112.2818 | -112.4386 | -0.089445 | 0.019693 | -0.05458 | -0.046838 | 122.3129 | 122.4041 | 122.1042 | 122.3394 | -112.0487 | -112.51 | -112.5357 | -111.928 | -111.9498 | -112.2314 | -112.3882 | -0.039091 | 0.070047 | -0.004226 | 0.003516 | 122.3633 | 122.4544 | 122.1545 | 122.3897 | -122.4024 | -122.1936 | -122.3675 | -122.1587
2486.0156 | 122.6669 | -122.493 | 0.059509 | -112.2821 | -112.7298 | -112.7464 | -112.1157 | -112.1603 | -112.4603 | -112.6217 | -0.10318 | 0.015114 | -0.068315 | -0.051417 | 122.3541 | 122.4407 | 122.1271 | 122.3577 | -112.2318 | -112.6794 | -112.696 | -112.0654 | -112.11 | -112.41 | -112.5713 | -0.052827 | 0.065468 | -0.017961 | -0.001063 | 122.4045 | 122.4911 | 122.1774 | 122.408 | -122.4573 | -122.2302 | -122.4224 | -122.1954
2487.7188 | 122.6807 | -122.4838 | 0.050354 | -112.4287 | -112.8214 | -112.8517 | -112.221 | -112.2885 | -112.6069 | -112.7636 | -0.10776 | 0.015114 | -0.068315 | -0.051417 | 122.3404 | 122.4361 | 122.1179 | 122.3577 | -112.3783 | -112.771 | -112.8013 | -112.1707 | -112.2382 | -112.5565 | -112.7133 | -0.057405 | 0.065468 | -0.017961 | -0.001063 | 122.3908 | 122.4865 | 122.1683 | 122.408 | -122.4482 | -122.2257 | -122.4087 | -122.1862
2489.4844 | 122.5571 | -122.3831 | 0.11902 | -111.9525 | -112.3497 | -112.3709 | -111.6991 | -111.785 | -112.1261 | -112.2966 | -0.043661 | 0.083796 | -0.017954 | -0.014785 | 122.1298 | 122.2255 | 121.9897 | 122.2295 | -111.9022 | -112.2994 | -112.3206 | -111.6487 | -111.7346 | -112.0758 | -112.2463 | 0.006693 | 0.13415 | 0.0324 | 0.035569 | 122.1802 | 122.2759 | 122.0401 | 122.2798 | -122.1735 | -122.0334 | -122.1478 | -122.0077
2491.1875 | 122.3328 | -121.9574 | 0.31586 | -110.7438 | -111.1226 | -111.1255 | -110.5087 | -110.5901 | -110.922 | -111.0926 | 0.12574 | 0.24863 | 0.091925 | 0.099691 | 121.5117 | 121.6121 | 121.6189 | 121.8541 | -110.6935 | -111.0723 | -111.0752 | -110.4583 | -110.5398 | -110.8717 | -111.0422 | 0.1761 | 0.29899 | 0.14228 | 0.15005 | 121.5621 | 121.6624 | 121.6692 | 121.9044 | -121.386 | -121.4931 | -121.4198 | -121.5269
2492.9531 | 122.5113 | -122.3007 | 0.004578 | -0.17574 | -0.31983 | -0.32792 | -0.30888 | -0.28877 | -0.22117 | -0.41066 | -0.12607 | -0.00778 | -0.086628 | -0.060575 | 0.089439 | 0.16056 | 121.921 | 122.1608 | -0.12539 | -0.26947 | -0.27757 | -0.25853 | -0.23842 | -0.17081 | -0.3603 | -0.075719 | 0.042574 | -0.036274 | -0.010221 | 0.13979 | 0.21092 | 121.9714 | 122.2112 | -0.21551 | -122.0471 | -0.17607 | -122.0077
2494.7031 | 122.6303 | -122.374 | 0.022888 | -0.079598 | -0.20536 | -0.23177 | -0.21274 | -0.19263 | -0.12044 | -0.30078 | -0.12607 | -0.003202 | -0.08205 | -0.060575 | -0.029593 | 0.036954 | 122.0218 | 122.2615 | -0.029244 | -0.155 | -0.18142 | -0.16238 | -0.14228 | -0.070091 | -0.25043 | -0.075719 | 0.047152 | -0.031696 | -0.010221 | 0.020761 | 0.087308 | 122.0721 | 122.3119 | -0.09648 | -122.1478 | -0.052457 | -122.1038
2496.4062 | 122.5891 | -122.438 | 0.041199 | -0.60611 | -0.73192 | -0.76747 | -0.71179 | -0.72368 | -0.66069 | -0.82727 | -0.12607 | 0.001377 | -0.08205 | -0.069733 | 0.39618 | 0.60921 | 122.0446 | 122.2844 | -0.55576 | -0.68157 | -0.71711 | -0.66144 | -0.67332 | -0.61034 | -0.77692 | -0.075719 | 0.051731 | -0.031696 | -0.019379 | 0.44653 | 0.65957 | 122.095 | 122.3348 | -0.52225 | -122.1707 | -0.47823 | -122.1267

## Thermal Data
Fire Time | B Position - Middle
-0.0115 | 9.8322
0.9885 | 10.0581
1.9885 | 10.2511
2.9885 | 10.7964
3.9885 | 11.2678
4.9885 | 11.8611
5.9885 | 13.0874
6.9885 | 14.4294
7.9885 | 15.3523
8.9885 | 16.3831
9.9885 | 17.9383
10.9885 | 19.1558
11.9885 | 20.1164
12.9885 | 22.0363
13.9885 | 24.5721
14.9885 | 26.3626
15.9885 | 27.7582
16.9885 | 30.6419
17.9885 | 31.9768
18.9885 | 33.7023
19.9885 | 34.9409
20.9885 | 37.1488
21.9885 | 39.6774
22.9885 | 42.5357
23.9885 | 43.7158
24.9885 | 45.2115
25.9885 | 46.5417
26.9885 | 47.8875
27.9885 | 49.7667
28.9885 | 50.6239
29.9885 | 51.5036
30.9885 | 53.1076
31.9885 | 54.7531
32.9885 | 56.6189
33.9885 | 58.8576
34.9885 | 60.378
35.9885 | 62.322
36.9885 | 64.9866
37.9885 | 66.0214
38.9885 | 67.6034
39.9885 | 69.3468
40.9885 | 71.1481
41.9885 | 72.8306
42.9885 | 74.7113
43.9885 | 75.6445
44.9885 | 76.2484
45.9885 | 76.7446
46.9885 | 77.4654
47.9885 | 78.1267
48.9885 | 78.7149
49.9885 | 79.1018
50.9885 | 80.0322
51.9885 | 80.6418
52.9885 | 81.6883
53.9885 | 82.212
54.9885 | 82.7151
55.9885 | 83.3691
56.9885 | 84.4518
57.9885 | 84.8295
58.9885 | 85.8826
59.9885 | 86.0979
60.9885 | 86.1835
61.9885 | 86.8041
62.9885 | 87.2299
63.9885 | 87.76
64.9885 | 88.4404
65.9885 | 88.5364
66.9885 | 89.2696
67.9885 | 90.2847
68.9885 | 90.6823
69.9885 | 92.556
70.9885 | 94.6811
71.9885 | 96.1967
72.9885 | 96.7779
73.9885 | 96.7928
74.9885 | 97.3752
75.9885 | 97.9184
76.9885 | 98.6145
77.9885 | 99.8568
78.9885 | 99.1282
79.9885 | 100.0104
80.9885 | 100.9624
81.9885 | 102.0532
82.9885 | 102.0567
83.9885 | 102.3729
84.9885 | 103.0965
85.9885 | 103.0454
86.9885 | 102.8702
87.9885 | 103.2143
88.9885 | 103.4362
89.9885 | 103.2702
90.9885 | 103.0006
91.9885 | 104.1527
92.9885 | 104.8481
93.9885 | 106.3297
94.9885 | 106.4929
95.9885 | 106.2916
96.9885 | 107.02
97.9885 | 108.734
98.9885 | 109.3483
99.9885 | 109.8144
100.9885 | 110.1714
101.9885 | 110.7846
102.9885 | 111.2152
103.9885 | 112.031
104.9885 | 114.0498
105.9885 | 115.4836
106.9885 | 116.41
107.9885 | 116.5492
108.9885 | 116.7395
109.9885 | 116.7107
110.9885 | 116.556
111.9885 | 117.323
112.9885 | 117.9974
113.9885 | 118.4569
114.9885 | 118.8817
115.9885 | 120.7884
116.9885 | 123.1378
117.9885 | 123.6434
118.9885 | 123.9113
119.9885 | 123.6652
120.9885 | 124.7619
121.9885 | 126.3374
122.9885 | 127.6778
123.9885 | 128.019
124.9885 | 129.0204
125.9885 | 128.889
126.9885 | 130.0624
127.9885 | 130.0652
128.9885 | 130.6341
129.9885 | 131.647
130.9885 | 130.6082
131.9885 | 130.7316
132.9885 | 131.6359
133.9885 | 132.0462
134.9885 | 132.9193
135.9885 | 132.5456
136.9885 | 132.6491
137.9885 | 132.7693
138.9885 | 133.4682
139.9885 | 133.5071
140.9885 | 133.1854
141.9885 | 133.3799
142.9885 | 133.5752
143.9885 | 133.5182
144.9885 | 135.0627
145.9885 | 135.9319
146.9885 | 136.2544
147.9885 | 138.7706
148.9885 | 138.794
149.9885 | 139.4599
150.9885 | 139.9744
151.9885 | 141.2024
152.9885 | 141.3687
153.9885 | 141.5711
154.9885 | 141.9763
155.9885 | 142.6286
156.9885 | 142.5659
157.9885 | 141.5749
158.9885 | 140.6001
159.9885 | 140.3253
160.9885 | 140.0514
161.9885 | 140.1832
162.9885 | 141.0802
163.9885 | 141.9069
164.9885 | 141.6272
165.9885 | 141.1294
166.9885 | 140.5487
167.9885 | 140.7432
168.9885 | 141.702
169.9885 | 142.5074
170.9885 | 142.7952
171.9885 | 143.8334
172.9885 | 144.0243
173.9885 | 144.5504
174.9885 | 145.5434
175.9885 | 145.1761
176.9885 | 145.5593
177.9885 | 145.2398
178.9885 | 145.0989
179.9885 | 145.0096
180.9885 | 144.7546
181.9885 | 144.3004
182.9885 | 144.4611
183.9885 | 144.5586
184.9885 | 145.5069
185.9885 | 145.3837
186.9885 | 145.189
187.9885 | 145.1224
188.9885 | 146.3904
189.9885 | 146.849
190.9885 | 147.7383
191.9885 | 148.0327
192.9885 | 147.8983
193.9885 | 147.3184
194.9885 | 147.2393
195.9885 | 148.0881
196.9885 | 147.8392
197.9885 | 149.1895
198.9885 | 149.2484
199.9885 | 149.7135
200.9885 | 150.2012
201.9885 | 150.3166
202.9885 | 149.9879
203.9885 | 150.2254
204.9885 | 150.6092
205.9885 | 151.2928
206.9885 | 151.2198
207.9885 | 150.2665
208.9885 | 150.6019
209.9885 | 150.7914
210.9885 | 151.0568
211.9885 | 150.8357
212.9885 | 151.2347
213.9885 | 152.0043
214.9885 | 152.018
215.9885 | 151.7337
216.9885 | 151.8296
217.9885 | 151.7328
218.9885 | 151.4792
219.9885 | 150.8972
220.9885 | 150.4842
221.9885 | 149.6951
222.9885 | 149.828
223.9885 | 149.4418
224.9885 | 149.2745
225.9885 | 149.0207
226.9885 | 148.9934
227.9885 | 148.6038
228.9885 | 148.4924
229.9885 | 148.4728
230.9885 | 148.0725
231.9885 | 147.9626
232.9885 | 147.6467
233.9885 | 147.2832
234.9885 | 147.3528
235.9885 | 147.7247
236.9885 | 147.2001
237.9885 | 146.4747
238.9885 | 147.0161
239.9885 | 147.8165
240.9885 | 148.4718
241.9885 | 147.9758
242.9885 | 148.4666
243.9885 | 147.9368
244.9885 | 147.7603
245.9885 | 148.344
246.9885 | 148.0902
247.9885 | 148.8754
248.9885 | 148.8326
249.9885 | 148.906
250.9885 | 148.555
251.9885 | 148.5565
252.9885 | 148.5952
253.9885 | 149.9408
254.9885 | 150.1549
255.9885 | 151.7165
256.9885 | 151.7857
257.9885 | 151.7934
258.9885 | 151.3821
259.9885 | 151.8419
260.9885 | 152.1854
261.9885 | 152.6933
262.9885 | 152.7604
263.9885 | 153.2398
264.9885 | 153.244
265.9885 | 153.292
266.9885 | 152.8842
267.9885 | 153.0775
268.9885 | 154.1299
269.9885 | 155.0436
270.9885 | 155.4405
271.9885 | 155.8238
272.9885 | 156.8626
273.9885 | 156.8068
274.9885 | 157.1193
275.9885 | 158.503
276.9885 | 159.0976
277.9885 | 158.9252
278.9885 | 158.2645
279.9885 | 159.1369
280.9885 | 160.4818
281.9885 | 161.3516
282.9885 | 161.8253
283.9885 | 162.4449
284.9885 | 163.3648
285.9885 | 164.0542
286.9885 | 165.4109
287.9885 | 165.8027
288.9885 | 165.6936
289.9885 | 166.8647
290.9885 | 166.979
291.9885 | 167.3598
292.9885 | 167.6235
293.9885 | 168.4824
294.9885 | 168.8804
295.9885 | 168.8612
296.9885 | 169.0802
297.9885 | 168.9119
298.9885 | 169.7691
299.9885 | 171.2244
300.9885 | 170.7914
301.9885 | 170.5859
302.9885 | 170.8156
303.9885 | 171.0795
304.9885 | 171.7527
305.9885 | 171.5633
306.9885 | 172.0389
307.9885 | 172.5583
308.9885 | 173.0007
309.9885 | 173.3891
310.9885 | 174.3995
311.9885 | 175.1517
312.9885 | 175.7474
313.9885 | 177.0207
314.9885 | 177.699
315.9885 | 179.0053
316.9885 | 179.349
317.9885 | 180.7403
318.9885 | 180.8597
319.9885 | 181.5992
320.9885 | 183.1431
321.9885 | 183.9016
322.9885 | 184.3764
323.9885 | 184.5857
324.9885 | 185.8144
325.9885 | 187.3827
326.9885 | 188.478
327.9885 | 189.4007
328.9885 | 189.9739
329.9885 | 190.8067
330.9885 | 191.2494
331.9885 | 191.3202
332.9885 | 192.5565
333.9885 | 193.4892
334.9885 | 193.301
335.9885 | 194.0834
336.9885 | 195.101
337.9885 | 195.1339
338.9885 | 194.1939
339.9885 | 195.3111
340.9885 | 195.5093
341.9885 | 195.2652
342.9885 | 195.3162
343.9885 | 195.3324
344.9885 | 195.1396
345.9885 | 195.5258
346.9885 | 196.6572
347.9885 | 197.4504
348.9885 | 198.4204
349.9885 | 198.9511
350.9885 | 199.0487
351.9885 | 200.052
352.9885 | 202.9106
353.9885 | 203.9903
354.9885 | 203.9255
355.9885 | 204.9265
356.9885 | 206.3063
357.9885 | 207.0238
358.9885 | 205.8492
359.9885 | 205.7067
360.9885 | 205.3741
361.9885 | 206.5846
362.9885 | 207.4494
363.9885 | 208.2892
364.9885 | 209.6633
365.9885 | 211.4375
366.9885 | 212.4404
367.9885 | 214.0856
368.9885 | 214.9635
369.9885 | 216.0833
370.9885 | 215.7994
371.9885 | 216.7078
372.9885 | 216.597
373.9885 | 217.0988
374.9885 | 217.6762
375.9885 | 217.7166
376.9885 | 217.6719
377.9885 | 218.4445
378.9885 | 219.3417
379.9885 | 219.9905
380.9885 | 220.9332
381.9885 | 220.946
382.9885 | 221.8102
383.9885 | 222.4655
384.9885 | 222.8986
385.9885 | 224.0959
386.9885 | 225.315
387.9885 | 226.1877
388.9885 | 226.0935
389.9885 | 226.3453
390.9885 | 225.9134
391.9885 | 226.7437
392.9885 | 227.0599
393.9885 | 227.3725
394.9885 | 226.7553
395.9885 | 227.2285
396.9885 | 228.9145
397.9885 | 229.6084
398.9885 | 230.516
399.9885 | 232.3359
400.9885 | 232.9336
401.9885 | 232.4326
402.9885 | 232.8728
403.9885 | 234.0835
404.9885 | 235.3085
405.9885 | 235.031
406.9885 | 235.8416
407.9885 | 236.9378
408.9885 | 237.6712
409.9885 | 238.5527
410.9885 | 239.0324
411.9885 | 239.7812
412.9885 | 241.1972
413.9885 | 242.3224
414.9885 | 243.116
415.9885 | 243.2262
416.9885 | 244.1079
417.9885 | 243.1083
418.9885 | 242.741
419.9885 | 242.2105
420.9885 | 242.556
421.9885 | 242.9632
422.9885 | 244.5997
423.9885 | 245.4315
424.9885 | 247.6538
425.9885 | 248.8518
426.9885 | 249.3433
427.9885 | 249.458
428.9885 | 248.7708
429.9885 | 247.9426
430.9885 | 247.3301
431.9885 | 248.3617
432.9885 | 248.3829
433.9885 | 249.7601
434.9885 | 250.768
435.9885 | 251.0265
436.9885 | 251.2501
437.9885 | 250.9225
438.9885 | 251.0273
439.9885 | 251.5116
440.9885 | 253.6334
441.9885 | 253.9614
442.9885 | 256.1383
443.9885 | 256.709
444.9885 | 256.6255
445.9885 | 256.1034
446.9885 | 255.5651
447.9885 | 256.1584
448.9885 | 257.3012
449.9885 | 257.7177
450.9885 | 257.5452
451.9885 | 257.0017
452.9885 | 256.2042
453.9885 | 257.6558
454.9885 | 256.526
455.9885 | 256.5972
456.9885 | 256.4989
457.9885 | 255.4866
458.9885 | 255.3716
459.9885 | 255.4453
460.9885 | 255.5923
461.9885 | 256.255
462.9885 | 256.7679
463.9885 | 256.3221
464.9885 | 257.6724
465.9885 | 258.1516
466.9885 | 258.4757
467.9885 | 258.07
468.9885 | 258.9827
469.9885 | 258.705
470.9885 | 258.3882
471.9885 | 258.299
472.9885 | 258.6552
473.9885 | 259.0671
474.9885 | 258.5434
475.9885 | 259.0208
476.9885 | 258.1873
477.9885 | 257.5102
478.9885 | 256.8531
479.9885 | 256.8437
480.9885 | 257.0093
481.9885 | 255.8154
482.9885 | 256.0297
483.9885 | 255.1357
484.9885 | 254.773
485.9885 | 254.0669
486.9885 | 253.1177
487.9885 | 252.5034
488.9885 | 253.4419
489.9885 | 253.604
490.9885 | 254.0672
491.9885 | 254.2723
492.9885 | 255.4866
493.9885 | 255.808
494.9885 | 255.6128
495.9885 | 256.8963
496.9885 | 256.53
497.9885 | 257.5957
498.9885 | 257.6763
499.9885 | 257.5595
500.9885 | 257.2986
501.9885 | 257.2191
502.9885 | 258.4768
503.9885 | 258.3993
504.9885 | 258.9425
505.9885 | 259.5739
506.9885 | 260.9398
507.9885 | 261.2219
508.9885 | 262.758
509.9885 | 265.3662
510.9885 | 264.647
511.9885 | 265.1374
512.9885 | 266.08
513.9885 | 265.1283
514.9885 | 265.2723
515.9885 | 265.1336
516.9885 | 265.0175
517.9885 | 264.7221
518.9885 | 264.3488
519.9885 | 264.9959
520.9885 | 264.6882
521.9885 | 264.0261
522.9885 | 263.7648
523.9885 | 263.5883
524.9885 | 263.4946
525.9885 | 262.5806
526.9885 | 262.9818
527.9885 | 262.54
528.9885 | 262.8745
529.9885 | 262.4086
530.9885 | 262.0031
531.9885 | 263.3914
532.9885 | 262.4949
533.9885 | 261.3631
534.9885 | 260.9496
535.9885 | 259.7777
536.9885 | 259.2387
537.9885 | 258.7238
538.9885 | 259.3557
539.9885 | 259.5343
540.9885 | 260.3857
541.9885 | 260.879
542.9885 | 261.1649
543.9885 | 261.6944
544.9885 | 261.7177
545.9885 | 261.9812
546.9885 | 261.8196
547.9885 | 262.4011
548.9885 | 262.0209
549.9885 | 260.7988
550.9885 | 262.2935
551.9885 | 261.1945
552.9885 | 261.0414
553.9885 | 260.4171
554.9885 | 260.6142
555.9885 | 261.4077
556.9885 | 261.5917
557.9885 | 262.5265
558.9885 | 262.3876
559.9885 | 263.3262
560.9885 | 263.6476
561.9885 | 263.4192
562.9885 | 264.4755
563.9885 | 264.8811
564.9885 | 265.512
565.9885 | 264.4437
566.9885 | 264.0576
567.9885 | 263.9242
568.9885 | 264.4883
569.9885 | 265.6786
570.9885 | 265.0345
571.9885 | 266.3072
572.9885 | 266.3385
573.9885 | 266.1593
574.9885 | 266.5614
575.9885 | 266.439
576.9885 | 266.1573
577.9885 | 266.4264
578.9885 | 266.5627
579.9885 | 267.3744
580.9885 | 268.5982
581.9885 | 269.1618
582.9885 | 268.6677
583.9885 | 268.3162
584.9885 | 267.0834
585.9885 | 266.3248
586.9885 | 266.6476
587.9885 | 266.002
588.9885 | 266.5874
589.9885 | 266.7392
590.9885 | 267.436
591.9885 | 267.4231
592.9885 | 268.5449
593.9885 | 268.7691
594.9885 | 270.4745
595.9885 | 270.8526
596.9885 | 272.2449
597.9885 | 272.5438
598.9885 | 274.6867
599.9885 | 274.9851
600.9885 | 275.6192
601.9885 | 276.0274
602.9885 | 275.6392
603.9885 | 275.3947
604.9885 | 275.6141
605.9885 | 275.1704
606.9885 | 274.6348
607.9885 | 274.9588
608.9885 | 275.2316
609.9885 | 275.4297
610.9885 | 274.9219
611.9885 | 275.501
612.9885 | 275.9249
613.9885 | 276.17
614.9885 | 276.7121
615.9885 | 276.8562
616.9885 | 277.3206
617.9885 | 278.1436
618.9885 | 278.2699
619.9885 | 277.5428
620.9885 | 277.7142
621.9885 | 278.2346
622.9885 | 277.8142
623.9885 | 277.0149
624.9885 | 276.4494
625.9885 | 276.925
626.9885 | 276.5154
627.9885 | 276.2954
628.9885 | 277.9977
629.9885 | 276.8568
630.9885 | 276.7968
631.9885 | 276.6589
632.9885 | 277.1796
633.9885 | 277.5417
634.9885 | 276.9777
635.9885 | 275.9037
636.9885 | 277.12
637.9885 | 277.0514
638.9885 | 277.2499
639.9885 | 278.0247
640.9885 | 278.8496
641.9885 | 278.3852
642.9885 | 277.9531
643.9885 | 278.3207
644.9885 | 277.2392
645.9885 | 276.9931
646.9885 | 277.5526
647.9885 | 277.4376
648.9885 | 277.9694
649.9885 | 278.3197
650.9885 | 278.4069
651.9885 | 278.8528
652.9885 | 279.3318
653.9885 | 278.8571
654.9885 | 278.6469
655.9885 | 278.3726
656.9885 | 278.3262
657.9885 | 278.4072
658.9885 | 279.6064
659.9885 | 280.0732
660.9885 | 280.5277
661.9885 | 281.4732
662.9885 | 282.1571
663.9885 | 282.271
664.9885 | 282.0781
665.9885 | 282.4541
666.9885 | 281.6376
667.9885 | 281.2494
668.9885 | 282.18
669.9885 | 282.683
670.9885 | 283.153
671.9885 | 283.3565
672.9885 | 282.7866
673.9885 | 283.8758
674.9885 | 284.4129
675.9885 | 283.798
676.9885 | 282.9444
677.9885 | 282.9086
678.9885 | 283.6666
679.9885 | 284.4359
680.9885 | 284.6597
681.9885 | 284.4446
682.9885 | 283.4249
683.9885 | 284.1878
684.9885 | 283.3139
685.9885 | 281.7811
686.9885 | 281.8873
687.9885 | 281.6205
688.9885 | 281.2199
689.9885 | 281.8511
690.9885 | 280.7698
691.9885 | 281.2892
692.9885 | 281.9244
693.9885 | 282.1229
694.9885 | 282.2042
695.9885 | 282.1485
696.9885 | 281.703
697.9885 | 283.5972
698.9885 | 283.3167
699.9885 | 282.2291
700.9885 | 281.9575
701.9885 | 282.0469
702.9885 | 282.7916
703.9885 | 282.2907
704.9885 | 281.4754
705.9885 | 281.3663
706.9885 | 281.7553
707.9885 | 282.4348
708.9885 | 284.166
709.9885 | 284.2943
710.9885 | 283.8124
711.9885 | 284.049
712.9885 | 283.9591
713.9885 | 283.7741
714.9885 | 282.7652
715.9885 | 283.2112
716.9885 | 283.4061
717.9885 | 282.5796
718.9885 | 282.7133
719.9885 | 282.6164
720.9885 | 282.6468
721.9885 | 282.8378
722.9885 | 283.0988
723.9885 | 283.0821
724.9885 | 281.9584
725.9885 | 280.7928
726.9885 | 280.2087
727.9885 | 279.7603
728.9885 | 279.9569
729.9885 | 279.636
730.9885 | 279.5463
731.9885 | 279.7534
732.9885 | 279.7821
733.9885 | 281.0532
734.9885 | 281.6513
735.9885 | 281.4607
736.9885 | 280.9772
737.9885 | 281.3199
738.9885 | 280.4789
739.9885 | 280.7485
740.9885 | 280.8241
741.9885 | 281.6599
742.9885 | 282.3482
743.9885 | 282.263
744.9885 | 283.5621
745.9885 | 284.6885
746.9885 | 284.1308
747.9885 | 283.9318
748.9885 | 285.9068
749.9885 | 285.9448
750.9885 | 287.2971
751.9885 | 288.3475
752.9885 | 290.4764
753.9885 | 290.6729
754.9885 | 290.6099
755.9885 | 291.1608
756.9885 | 290.7592
757.9885 | 292.2889
758.9885 | 292.9595
759.9885 | 294.6769
760.9885 | 295.3959
761.9885 | 297.5258
762.9885 | 298.3948
763.9885 | 298.5061
764.9885 | 299.283
765.9885 | 299.2536
766.9885 | 299.8441
767.9885 | 301.44
768.9885 | 301.5038
769.9885 | 300.8885
770.9885 | 301.0241
771.9885 | 299.6749
772.9885 | 299.4046
773.9885 | 299.2772
774.9885 | 300.4147
775.9885 | 300.5297
776.9885 | 301.1576
777.9885 | 300.7292
778.9885 | 301.7082
779.9885 | 301.9201
780.9885 | 301.4
781.9885 | 301.9147
782.9885 | 302.3843
783.9885 | 302.004
784.9885 | 302.6309
785.9885 | 302.0727
786.9885 | 303.1282
787.9885 | 305.5237
788.9885 | 305.703
789.9885 | 306.4706
790.9885 | 307.421
791.9885 | 308.7382
792.9885 | 309.1078
793.9885 | 308.318
794.9885 | 308.5675
795.9885 | 309.0851
796.9885 | 310.3791
797.9885 | 311.659
798.9885 | 311.8336
799.9885 | 313.1831
800.9885 | 313.8025
801.9885 | 314.3924
802.9885 | 313.2986
803.9885 | 312.5749
804.9885 | 311.7218
805.9885 | 311.4612
806.9885 | 310.9096
807.9885 | 312.8747
808.9885 | 313.1581
809.9885 | 315.4924
810.9885 | 315.9456
811.9885 | 316.5786
812.9885 | 317.2936
813.9885 | 318.6632
814.9885 | 320.4109
815.9885 | 321.7321
816.9885 | 322.0698
817.9885 | 322.4983
818.9885 | 322.1497
819.9885 | 321.6604
820.9885 | 321.0937
821.9885 | 323.035
822.9885 | 322.7549
823.9885 | 322.0784
824.9885 | 322.4901
825.9885 | 322.6214
826.9885 | 322.2237
827.9885 | 322.0141
828.9885 | 322.0374
829.9885 | 321.6873
830.9885 | 321.7108
831.9885 | 323.0026
832.9885 | 322.9623
833.9885 | 323.1345
834.9885 | 322.9087
835.9885 | 322.2141
836.9885 | 320.9844
837.9885 | 321.5568
838.9885 | 321.3631
839.9885 | 323.3454
840.9885 | 324.7047
841.9885 | 325.0107
842.9885 | 325.1507
843.9885 | 324.2725
844.9885 | 324.8106
845.9885 | 326.0895
846.9885 | 328.288
847.9885 | 329.5546
848.9885 | 329.8015
849.9885 | 329.8463
850.9885 | 332.8828
851.9885 | 332.8607
852.9885 | 332.5201
853.9885 | 331.7074
854.9885 | 332.205
855.9885 | 331.9251
856.9885 | 332.3589
857.9885 | 332.8172
858.9885 | 333.1887
859.9885 | 333.721
860.9885 | 334.3044
861.9885 | 334.7251
862.9885 | 335.1127
863.9885 | 335.5863
864.9885 | 335.9346
865.9885 | 336.3992
866.9885 | 338.23
867.9885 | 339.6417
868.9885 | 341.2597
869.9885 | 341.5643
870.9885 | 342.4482
871.9885 | 342.65
872.9885 | 342.1553
873.9885 | 341.7076
874.9885 | 340.1746
875.9885 | 341.1899
876.9885 | 349.5583
877.9885 | 350.7763
878.9885 | 353.0782
879.9885 | 353.9562
880.9885 | 356.6029
881.9885 | 358.3817
882.9885 | 358.403
883.9885 | 359.7335
884.9885 | 361.3294
885.9885 | 364.331
886.9885 | 366.3587
887.9885 | 367.409
888.9885 | 367.8692
889.9885 | 368.5316
890.9885 | 374.1028
891.9885 | 395.3282
892.9885 | 393.5839
893.9885 | 391.3385
894.9885 | 388.5183
895.9885 | 386.4307
896.9885 | 383.338
897.9885 | 380.6249
898.9885 | 380.1653
899.9885 | 380.3999
900.9885 | 378.8124
901.9885 | 378.4867
902.9885 | 376.6336
903.9885 | 374.8153
904.9885 | 374.6499
905.9885 | 374.842
906.9885 | 373.4945
908.0042 | 373.129
908.9885 | 371.8222
909.9885 | 370.6648
910.9885 | 370.8576
911.9885 | 372.259
912.9885 | 373.8016
913.9885 | 375.4612
914.9885 | 375.7679
915.9885 | 375.8491
916.9885 | 375.0325
917.9885 | 373.1132
918.9885 | 373.6754
919.9885 | 375.0202
920.9885 | 375.8212
921.9885 | 377.89
922.9885 | 378.2783
923.9885 | 382.2538
924.9885 | 380.8483
925.9885 | 380.0203
926.9885 | 379.2897
927.9885 | 378.5141
928.9885 | 380.4458
929.9885 | 381.2055
930.9885 | 380.9005
931.9885 | 382.7115
932.9885 | 382.5295
933.9885 | 382.2379
934.9885 | 381.5849
935.9885 | 381.6026
936.9885 | 381.8214
937.9885 | 382.2467
938.9885 | 382.7749
939.9885 | 381.2226
940.9885 | 382.6705
941.9885 | 382.4788
942.9885 | 383.0194
943.9885 | 383.5645
944.9885 | 385.0333
945.9885 | 385.9714
946.9885 | 385.2274
947.9885 | 385.2031
948.9885 | 385.9772
949.9885 | 385.548
950.9885 | 384.3815
951.9885 | 386.1423
952.9885 | 384.6146
953.9885 | 386.2616
954.9885 | 390.6658
955.9885 | 390.0194
956.9885 | 391.6691
957.9885 | 391.7144
958.9885 | 389.3027
959.9885 | 389.2504
960.9885 | 388.7115
961.9885 | 389.2935
962.9885 | 388.1728
963.9885 | 387.4036
964.9885 | 388.164
965.9885 | 388.295
966.9885 | 387.0372
967.9885 | 385.5339
968.9885 | 386.1881
969.9885 | 388.6066
970.9885 | 389.858
971.9885 | 390.4985
972.9885 | 391.9787
973.9885 | 392.7899
974.9885 | 395.6807
975.9885 | 399.2406
976.9885 | 400.0305
977.9885 | 398.7297
978.9885 | 399.437
979.9885 | 397.9771
980.9885 | 398.7231
981.9885 | 400.8921
982.9885 | 402.9636
983.9885 | 402.7884
984.9885 | 402.8134
985.9885 | 403.1448
986.9885 | 404.9609
987.9885 | 405.1747
988.9885 | 407.5519
989.9885 | 409.6227
990.9885 | 410.9314
991.9885 | 409.4594
992.9885 | 409.7917
993.9885 | 409.7702
994.9885 | 409.7938
995.9885 | 409.6125
996.9885 | 408.6735
997.9885 | 410.3773
998.9885 | 411.9747
999.9885 | 413.0013
1000.9885 | 415.5072
1001.9885 | 417.5631
1002.9885 | 417.4696
1003.9885 | 417.4897
1004.9885 | 418.5131
1005.9885 | 418.3045
1006.9885 | 418.1308
1007.9885 | 415.8638
1008.9885 | 423.8433
1009.9885 | 422.7643
1010.9885 | 423.7164
1011.9885 | 429.0662
1012.9885 | 430.6764
1013.9885 | 431.4972
1014.9885 | 430.647
1015.9885 | 432.0777
1016.9885 | 433.69
1017.9885 | 433.0353
1018.9885 | 432.4864
1019.9885 | 431.5844
1020.9885 | 435.715
1021.9885 | 436.5921
1022.9885 | 436.1399
1023.9885 | 434.5195
1024.9885 | 434.5297
1025.9885 | 433.6635
1026.9885 | 430.2544
1027.9885 | 427.8158
1028.9885 | 427.1905
1029.9885 | 425.4521
1030.9885 | 425.0924
1031.9885 | 423.5887
1032.9885 | 423.6627
1033.9885 | 422.2149
1034.9885 | 421.0735
1035.9885 | 420.5222
1036.9885 | 418.8644
1037.9885 | 416.8828
1038.9885 | 417.2401
1039.9885 | 415.3566
1040.9885 | 413.4498
1041.9885 | 413.1519
1042.9885 | 412.981
1043.9885 | 412.828
1044.9885 | 413.9094
1045.9885 | 413.2324
1046.9885 | 413.3677
1047.9885 | 412.4241
1048.9885 | 411.5754
1049.9885 | 412.3958
1050.9885 | 413.1447
1051.9885 | 411.9351
1052.9885 | 412.0946
1053.9885 | 411.2119
1054.9885 | 411.1461
1055.9885 | 412.5461
1056.9885 | 412.9186
1057.9885 | 413.2434
1058.9885 | 412.8416
1059.9885 | 412.4804
1060.9885 | 412.7836
1061.9885 | 411.3398
1062.9885 | 410.8289
1063.9885 | 411.4822
1064.9885 | 412.6688
1065.9885 | 412.5454
1066.9885 | 413.648
1067.9885 | 414.4145
1068.9885 | 414.4996
1069.9885 | 416.6143
1070.9885 | 418.4475
1071.9885 | 420.0053
1072.9885 | 419.4008
1073.9885 | 419.0801
1074.9885 | 420.3391
1075.9885 | 422.1665
1076.9885 | 423.6094
1077.9885 | 423.2716
1078.9885 | 423.542
1079.9885 | 423.3018
1080.9885 | 423.6675
1081.9885 | 422.7633
1082.9885 | 423.916
1083.9885 | 425.2379
1084.9885 | 424.8246
1085.9885 | 425.9958
1086.9885 | 424.7961
1087.9885 | 424.8532
1088.9885 | 424.3994
1089.9885 | 424.3273
1090.9885 | 422.8336
1091.9885 | 422.6024
1092.9885 | 422.1443
1093.9885 | 422.758
1094.9885 | 425.7842
1095.9885 | 429.4057
1096.9885 | 431.5699
1097.9885 | 431.6743
1098.9885 | 430.1175
1099.9885 | 427.4293
1100.9885 | 428.1234
1101.9885 | 429.1003
1102.9885 | 429.1774
1103.9885 | 429.9899
1104.9885 | 428.8784
1105.9885 | 427.837
1106.9885 | 429.1391
1107.9885 | 429.4047
1108.9885 | 431.0642
1109.9885 | 432.6316
1110.9885 | 434.1374
1111.9885 | 433.7013
1112.9885 | 433.3447
1113.9885 | 433.441
1114.9885 | 434.8974
1115.9885 | 433.9966
1116.9885 | 435.9865
1117.9885 | 437.385
1118.9885 | 438.4564
1119.9885 | 439.0078
1120.9885 | 440.2388
1121.9885 | 441.3277
1122.9885 | 440.6484
1123.9885 | 438.3237
1124.9885 | 437.4376
1125.9885 | 436.4134
1126.9885 | 435.0721
1127.9885 | 434.4956
1128.9885 | 434.3076
1129.9885 | 433.241
1130.9885 | 439.328
1131.9885 | 438.558
1132.9885 | 437.6554
1133.9885 | 438.1654
1134.9885 | 438.0814
1135.9885 | 442.7639
1136.9885 | 440.978
1137.9885 | 439.2436
1138.9885 | 435.963
1139.9885 | 433.8106
1140.9885 | 436.9389
1141.9885 | 439.8398
1142.9885 | 438.4192
1143.9885 | 436.0323
1144.9885 | 435.2182
1145.9885 | 433.6958
1146.9885 | 431.239
1147.9885 | 429.4942
1148.9885 | 427.5267
1149.9885 | 426.4884
1150.9885 | 426.4694
1151.9885 | 425.3665
1152.9885 | 423.713
1153.9885 | 422.2478
1154.9885 | 421.5702
1155.9885 | 421.8697
1156.9885 | 426.0549
1157.9885 | 424.5592
1158.9885 | 425.671
1159.9885 | 427.1887
1160.9885 | 427.2616
1161.9885 | 427.0661
1162.9885 | 425.5681
1163.9885 | 425.348
1164.9885 | 424.869
1165.9885 | 423.9507
1166.9885 | 421.3355
1167.9885 | 420.8245
1168.9885 | 422.0874
1169.9885 | 422.9569
1170.9885 | 424.6889
1171.9885 | 425.8648
1172.9885 | 426.4356
1173.9885 | 428.0697
1174.9885 | 427.4046
1175.9885 | 427.5795
1176.9885 | 427.7182
1177.9885 | 427.903
1178.9885 | 429.8755
1179.9885 | 428.0093
1180.9885 | 426.402
1181.9885 | 425.3821
1182.9885 | 424.6837
1183.9885 | 423.7612
1184.9885 | 423.1276
1185.9885 | 421.8154
1186.9885 | 420.62
1187.9885 | 420.4699
1188.9885 | 419.6914
1189.9885 | 418.5701
1190.9885 | 419.001
1191.9885 | 420.0913
1192.9885 | 421.3281
1193.9885 | 421.1666
1194.9885 | 422.01
1195.9885 | 423.1935
1196.9885 | 421.967
1197.9885 | 424.4066
1198.9885 | 426.4142
1199.9885 | 427.1704
1200.9885 | 427.9521
1201.9885 | 426.7484
1202.9885 | 426.5927
1203.9885 | 425.8477
1204.9885 | 426.5154
1205.9885 | 426.3896
1206.9885 | 426.0969
1207.9885 | 426.7909
1208.9885 | 428.0823
1209.9885 | 428.6768
1210.9885 | 434.8154
1211.9885 | 433.2702
1212.9885 | 428.7768
1213.9885 | 435.3633
1214.9885 | 435.453
1215.9885 | 433.933
1216.9885 | 432.0793
1217.9885 | 431.1368
1218.9885 | 430.0726
1219.9885 | 429.0223
1220.9885 | 426.9464
1221.9885 | 427.4635
1222.9885 | 429.2594
1223.9885 | 429.9064
1224.9885 | 429.085
1225.9885 | 430.5243
1226.9885 | 429.0813
1227.9885 | 428.6255
1228.9885 | 428.1139
1229.9885 | 425.924
1230.9885 | 423.5139
1231.9885 | 421.7568
1232.9885 | 420.5953
1233.9885 | 420.6054
1234.9885 | 419.7249
1235.9885 | 417.607
1236.9885 | 416.8089
1237.9885 | 417.8383
1238.9885 | 418.6232
1239.9885 | 420.0903
1240.9885 | 421.5621
1241.9885 | 422.4157
1242.9885 | 424.105
1243.9885 | 428.9502
1244.9885 | 427.6844
1245.9885 | 425.8272
1246.9885 | 423.3636
1247.9885 | 420.7774
1248.9885 | 420.8067
1249.9885 | 420.4466
1250.9885 | 419.735
1251.9885 | 421.4035
1252.9885 | 424.0567
1253.9885 | 425.5365
1254.9885 | 426.3537
1255.9885 | 425.3599
1256.9885 | 424.1659
1257.9885 | 424.8406
1258.9885 | 427.1171
1259.9885 | 428.9646
1260.9885 | 429.1248
1261.9885 | 428.2595
1262.9885 | 426.1648
1263.9885 | 423.4456
1264.9885 | 424.1608
1265.9885 | 425.4343
1266.9885 | 427.2662
1267.9885 | 434.5282
1268.9885 | 434.5206
1269.9885 | 431.8007
1270.9885 | 429.1483
1271.9885 | 426.6393
1272.9885 | 426.3545
1273.9885 | 426.7982
1274.9885 | 425.2593
1275.9885 | 423.2709
1276.9885 | 424.8045
1277.9885 | 424.1093
1278.9885 | 422.3178
1279.9885 | 420.2137
1280.9885 | 418.5405
1281.9885 | 416.9434
1282.9885 | 415.645
1283.9885 | 416.2118
1284.9885 | 416.3725
1285.9885 | 415.741
1286.9885 | 415.58
1287.9885 | 412.7884
1288.9885 | 411.4395
1289.9885 | 410.3378
1290.9885 | 409.1368
1291.9885 | 407.4446
1292.9885 | 407.294
1293.9885 | 406.4739
1294.9885 | 405.5304
1295.9885 | 403.6939
1296.9885 | 402.2835
1297.9885 | 401.5299
1298.9885 | 400.1875
1299.9885 | 399.4989
1300.9885 | 400.7092
1301.9885 | 400.627
1303.0042 | 400.5943
1303.9885 | 401.1417
1304.9885 | 402.0343
1305.9885 | 402.697
1306.9885 | 404.9645
1307.9885 | 408.1387
1308.9885 | 409.838
1309.9885 | 412.3385
1310.9885 | 412.1454
1311.9885 | 412.6331
1312.9885 | 412.9906
1313.9885 | 414.2286
1314.9885 | 414.5746
1315.9885 | 416.0662
1316.9885 | 414.9475
1317.9885 | 417.3435
1318.9885 | 423.1138
1319.9885 | 423.8222
1320.9885 | 424.5851
1321.9885 | 426.0911
1322.9885 | 426.976
1323.9885 | 425.0939
1324.9885 | 424.6583
1325.9885 | 423.9884
1326.9885 | 424.5675
1327.9885 | 424.3002
1328.9885 | 423.7607
1329.9885 | 423.3293
1330.9885 | 421.711
1331.9885 | 423.2666
1332.9885 | 423.189
1333.9885 | 424.047
1334.9885 | 425.6547
1335.9885 | 425.0784
1336.9885 | 424.5523
1337.9885 | 426.5931
1338.9885 | 426.7181
1339.9885 | 425.7101
1340.9885 | 426.1796
1341.9885 | 427.7054
1342.9885 | 428.2486
1343.9885 | 429.2659
1344.9885 | 431.0602
1345.9885 | 431.8031
1346.9885 | 433.2392
1347.9885 | 433.5738
1348.9885 | 433.7513
1349.9885 | 433.8006
1350.9885 | 433.2667
1351.9885 | 431.8037
1352.9885 | 432.4033
1353.9885 | 430.3814
1354.9885 | 431.6566
1355.9885 | 432.0881
1356.9885 | 433.0707
1357.9885 | 431.758
1358.9885 | 431.1539
1359.9885 | 430.536
1360.9885 | 427.6724
1361.9885 | 425.6629
1362.9885 | 423.0243
1363.9885 | 421.7274
1364.9885 | 421.4231
1365.9885 | 423.6493
1366.9885 | 422.2629
1367.9885 | 420.9729
1368.9885 | 419.3462
1369.9885 | 418.0897
1370.9885 | 424.3511
1371.9885 | 422.6719
1372.9885 | 423.3222
1373.9885 | 421.001
1374.9885 | 419.6009
1375.9885 | 419.5243
1376.9885 | 422.2148
1377.9885 | 421.8437
1378.9885 | 424.0524
1379.9885 | 425.8507
1380.9885 | 427.7912
1381.9885 | 428.8039
1382.9885 | 428.5513
1383.9885 | 429.4694
1384.9885 | 433.9212
1385.9885 | 435.689
1386.9885 | 436.2074
1387.9885 | 435.593
1388.9885 | 434.5371
1389.9885 | 439.044
1390.9885 | 438.9759
1391.9885 | 439.7422
1392.9885 | 439.4559
1393.9885 | 439.3119
1394.9885 | 438.7126
1395.9885 | 438.0491
1396.9885 | 436.958
1397.9885 | 436.5439
1398.9885 | 436.6496
1399.9885 | 436.5124
1400.9885 | 437.6892
1401.9885 | 439.2443
1402.9885 | 439.3097
1403.9885 | 439.3612
1404.9885 | 438.9523
1405.9885 | 438.6866
1406.9885 | 437.9686
1407.9885 | 435.1961
1408.9885 | 433.8775
1409.9885 | 433.2692
1410.9885 | 433.1529
1411.9885 | 432.2828
1412.9885 | 433.5584
1413.9885 | 434.6211
1414.9885 | 436.3642
1415.9885 | 439.3313
1416.9885 | 441.3116
1417.9885 | 443.4087
1418.9885 | 444.3848
1419.9885 | 445.0613
1421.0042 | 445.0727
1421.9885 | 444.1391
1422.9885 | 444.3776
1423.9885 | 445.2714
1424.9885 | 447.0971
1425.9885 | 447.5179
1426.9885 | 448.4667
1427.9885 | 449.4193
1428.9885 | 451.5078
1429.9885 | 450.7212
1430.9885 | 449.4809
1431.9885 | 450.0882
1432.9885 | 449.3661
1433.9885 | 449.3906
1434.9885 | 449.8882
1435.9885 | 451.2727
1436.9885 | 449.5962
1437.9885 | 448.2551
1438.9885 | 445.7066
1439.9885 | 442.3825
1440.9885 | 442.722
1441.9885 | 440.5287
1442.9885 | 438.0454
1443.9885 | 437.1602
1444.9885 | 436.5031
1445.9885 | 438.2064
1446.9885 | 440.762
1447.9885 | 441.5627
1448.9885 | 442.7316
1449.9885 | 443.4415
1450.9885 | 444.7208
1451.9885 | 445.4027
1452.9885 | 445.6083
1453.9885 | 447.0679
1454.9885 | 448.1919
1455.9885 | 447.4139
1456.9885 | 447.9643
1457.9885 | 447.5923
1458.9885 | 448.0258
1459.9885 | 448.3154
1460.9885 | 447.5677
1461.9885 | 449.6125
1462.9885 | 450.6754
1463.9885 | 454.343
1464.9885 | 454.9266
1465.9885 | 456.5882
1466.9885 | 457.4282
1467.9885 | 457.1726
1468.9885 | 456.2834
1469.9885 | 454.3131
1470.9885 | 455.5443
1471.9885 | 455.6249
1472.9885 | 455.8061
1473.9885 | 454.7092
1474.9885 | 455.3471
1475.9885 | 455.3636
1476.9885 | 454.9173
1477.9885 | 453.0213
1478.9885 | 451.3667
1479.9885 | 448.9828
1480.9885 | 449.8345
1481.9885 | 449.8521
1482.9885 | 450.1897
1483.9885 | 451.1883
1484.9885 | 450.0532
1485.9885 | 449.1083
1486.9885 | 446.7014
1487.9885 | 446.163
1488.9885 | 448.0501
1489.9885 | 446.3935
1490.9885 | 446.0398
1491.9885 | 446.6243
1492.9885 | 446.5168
1493.9885 | 447.727
1494.9885 | 446.4616
1495.9885 | 445.1915
1496.9885 | 443.2094
1497.9885 | 441.524
1498.9885 | 439.7733
1499.9885 | 439.4732
1500.9885 | 441.8166
1501.9885 | 443.8212
1502.9885 | 445.0527
1503.9885 | 444.9107
1504.9885 | 448.6365
1505.9885 | 447.2233
1506.9885 | 446.6789
1507.9885 | 450.5158
1508.9885 | 453.9174
1509.9885 | 455.4048
1510.9885 | 456.4104
1511.9885 | 458.6439
1512.9885 | 458.8327
1513.9885 | 456.9225
1514.9885 | 454.1323
1515.9885 | 452.5583
1516.9885 | 451.8626
1517.9885 | 453.2426
1518.9885 | 453.927
1519.9885 | 453.4916
1520.9885 | 453.8869
1521.9885 | 450.9583
1522.9885 | 449.634
1523.9885 | 450.8389
1524.9885 | 451.5877
1525.9885 | 452.119
1526.9885 | 452.3429
1527.9885 | 450.5123
1528.9885 | 448.4568
1529.9885 | 446.0616
1530.9885 | 443.1365
1531.9885 | 441.8198
1532.9885 | 440.2369
1533.9885 | 437.8717
1534.9885 | 436.4619
1535.9885 | 435.8683
1536.9885 | 435.7104
1537.9885 | 437.4928
1538.9885 | 438.6448
1539.9885 | 437.1692
1540.9885 | 436.8817
1541.9885 | 437.4959
1542.9885 | 442.8426
1543.9885 | 445.8211
1544.9885 | 450.1671
1545.9885 | 454.6544
1546.9885 | 455.0158
1547.9885 | 452.401
1548.9885 | 449.7952
1549.9885 | 448.7822
1550.9885 | 449.2914
1551.9885 | 449.7251
1552.9885 | 449.926
1553.9885 | 448.2708
1554.9885 | 447.3427
1555.9885 | 447.1986
1556.9885 | 445.7242
1557.9885 | 443.8884
1558.9885 | 443.6003
1559.9885 | 443.6037
1560.9885 | 445.0345
1561.9885 | 448.4382
1562.9885 | 451.7129
1563.9885 | 452.7283
1564.9885 | 451.6131
1565.9885 | 448.8436
1566.9885 | 447.1428
1567.9885 | 446.6116
1568.9885 | 446.9335
1569.9885 | 447.5018
1570.9885 | 447.2417
1571.9885 | 448.1399
1572.9885 | 449.5428
1573.9885 | 450.7747
1574.9885 | 451.5668
1575.9885 | 452.0225
1576.9885 | 453.3827
1577.9885 | 451.8153
1578.9885 | 450.1635
1579.9885 | 450.2355
1580.9885 | 451.0992
1581.9885 | 451.1961
1582.9885 | 451.4582
1583.9885 | 451.7874
1584.9885 | 451.5588
1585.9885 | 452.9204
1586.9885 | 454.023
1587.9885 | 454.9041
1588.9885 | 454.5102
1589.9885 | 453.6941
1590.9885 | 452.9274
1591.9885 | 449.5375
1592.9885 | 453.4671
1593.9885 | 456.1894
1594.9885 | 457.505
1595.9885 | 455.8887
1596.9885 | 454.9687
1597.9885 | 454.5945
1598.9885 | 454.9917
1599.9885 | 456.3118
1600.9885 | 455.2023
1601.9885 | 464.3024
1602.9885 | 465.3332
1603.9885 | 467.0081
1604.9885 | 469.6202
1605.9885 | 475.861
1606.9885 | 472.944
1607.9885 | 469.7366
1608.9885 | 466.2477
1609.9885 | 461.9716
1610.9885 | 461.3261
1611.9885 | 459.3349
1612.9885 | 457.3557
1613.9885 | 454.8117
1614.9885 | 453.9063
1615.9885 | 455.7646
1616.9885 | 453.8742
1617.9885 | 452.8909
1618.9885 | 452.3224
1619.9885 | 452.8069
1620.9885 | 452.5093
1621.9885 | 453.4713
1622.9885 | 451.6402
1623.9885 | 453.1084
1624.9885 | 454.8898
1625.9885 | 452.5372
1626.9885 | 450.7349
1627.9885 | 449.8206
1628.9885 | 450.202
1629.9885 | 454.4548
1630.9885 | 456.3548
1631.9885 | 455.5636
1632.9885 | 454.5242
1633.9885 | 453.6404
1634.9885 | 452.1372
1635.9885 | 452.2988
1636.9885 | 453.0068
1637.9885 | 450.6719
1638.9885 | 448.5842
1639.9885 | 445.9288
1640.9885 | 444.7945
1641.9885 | 444.0956
1642.9885 | 444.0783
1643.9885 | 442.8857
1644.9885 | 441.4754
1645.9885 | 439.9651
1646.9885 | 438.8579
1647.9885 | 437.0833
1648.9885 | 435.4996
1649.9885 | 434.7392
1650.9885 | 432.4035
1651.9885 | 430.8318
1652.9885 | 430.8608
1653.9885 | 429.7051
1654.9885 | 429.614
1655.9885 | 428.8304
1656.9885 | 427.5141
1657.9885 | 426.7111
1658.9885 | 426.1033
1659.9885 | 425.1798
1660.9885 | 425.1192
1661.9885 | 423.6511
1662.9885 | 422.3483
1663.9885 | 421.9054
1664.9885 | 422.5688
1665.9885 | 423.7501
1666.9885 | 424.2672
1667.9885 | 424.955
1668.9885 | 424.4502
1669.9885 | 426.1078
1670.9885 | 427.5383
1671.9885 | 428.4843
1672.9885 | 429.6169
1673.9885 | 429.8233
1674.9885 | 430.6639
1675.9885 | 431.4727
1676.9885 | 432.9062
1677.9885 | 432.5113
1678.9885 | 432.3977
1679.9885 | 434.1747
1680.9885 | 438.4051
1681.9885 | 438.3951
1682.9885 | 438.7413
1683.9885 | 438.6301
1684.9885 | 439.1608
1685.9885 | 442.7755
1686.9885 | 446.5254
1687.9885 | 448.0641
1688.9885 | 450.1078
1689.9885 | 450.4547
1690.9885 | 453.1414
1691.9885 | 453.8045
1692.9885 | 453.4711
1693.9885 | 451.5105
1694.9885 | 450.2272
1695.9885 | 450.4134
1696.9885 | 448.3681
1697.9885 | 446.2373
1698.9885 | 445.0076
1699.9885 | 444.5069
1700.9885 | 443.8615
1701.9885 | 443.3174
1702.9885 | 442.9321
1703.9885 | 444.2678
1704.9885 | 444.2869
1705.9885 | 444.8417
1706.9885 | 445.0758
1707.9885 | 444.9721
1708.9885 | 444.8424
1709.9885 | 445.7182
1710.9885 | 448.4473
1711.9885 | 449.9184
1712.9885 | 451.3379
1713.9885 | 451.5736
1714.9885 | 452.0296
1715.9885 | 452.668
1716.9885 | 452.7042
1717.9885 | 453.1094
1718.9885 | 452.5319
1719.9885 | 451.7583
1720.9885 | 452.0671
1721.9885 | 453.3255
1722.9885 | 454.464
1723.9885 | 455.3182
1724.9885 | 458.4248
1725.9885 | 459.256
1726.9885 | 458.2681
1727.9885 | 458.7131
1728.9885 | 459.2348
1729.9885 | 460.3393
1730.9885 | 462.0047
1731.9885 | 464.4535
1732.9885 | 468.0131
1733.9885 | 472.8873
1734.9885 | 474.2201
1735.9885 | 474.0691
1736.9885 | 475.1403
1737.9885 | 476.7154
1738.9885 | 477.2094
1739.9885 | 475.8972
1740.9885 | 474.4171
1741.9885 | 472.2267
1742.9885 | 470.3468
1743.9885 | 473.0084
1744.9885 | 473.6141
1745.9885 | 473.2164
1746.9885 | 472.7129
1747.9885 | 474.1943
1748.9885 | 475.2429
1749.9885 | 476.6095
1750.9885 | 476.3008
1751.9885 | 474.4272
1752.9885 | 474.3815
1753.9885 | 475.999
1754.9885 | 477.6634
1755.9885 | 476.1752
1756.9885 | 475.2449
1757.9885 | 474.9879
1758.9885 | 475.9271
1759.9885 | 475.8247
1760.9885 | 475.67
1761.9885 | 476.9646
1762.9885 | 478.8316
1763.9885 | 478.0588
1764.9885 | 477.587
1765.9885 | 477.672
1766.9885 | 476.0496
1767.9885 | 475.7278
1768.9885 | 476.8988
1769.9885 | 477.5627
1770.9885 | 477.0253
1771.9885 | 477.0045
1772.9885 | 478.0597
1773.9885 | 478.4518
1774.9885 | 477.7221
1775.9885 | 478.0755
1776.9885 | 478.8809
1777.9885 | 478.7252
1778.9885 | 479.8491
1779.9885 | 480.197
1780.9885 | 481.0438
1781.9885 | 480.0167
1782.9885 | 478.7146
1783.9885 | 481.4336
1784.9885 | 484.1922
1785.9885 | 483.3233
1786.9885 | 483.3287
1787.9885 | 481.9391
1788.9885 | 481.066
1789.9885 | 481.8195
1790.9885 | 481.2921
1791.9885 | 480.3109
1792.9885 | 483.3995
1793.9885 | 486.85
1794.9885 | 485.9617
1795.9885 | 486.0348
1796.9885 | 485.0095
1797.9885 | 485.7883
1798.9885 | 485.9337
1799.9885 | 486.3342
1800.9885 | 485.2478
1801.9885 | 482.9272
1802.9885 | 481.4981
1803.9885 | 481.9559
1804.9885 | 481.1519
1805.9885 | 482.179
1806.9885 | 481.9396
1807.9885 | 480.3144
1808.9885 | 478.7092
1809.9885 | 476.0703
1810.9885 | 473.9105
1811.9885 | 474.8577
1812.9885 | 474.8693
1813.9885 | 475.1197
1814.9885 | 474.0526
1815.9885 | 474.5308
1816.9885 | 474.5299
1817.9885 | 472.7405
1818.9885 | 473.6756
1819.9885 | 472.767
1820.9885 | 472.6752
1821.9885 | 473.7388
1822.9885 | 474.2357
1823.9885 | 474.8546
1824.9885 | 474.9739
1825.9885 | 476.3769
1826.9885 | 476.9493
1827.9885 | 477.8964
1828.9885 | 481.8456
1829.9885 | 483.8397
1830.9885 | 484.013
1831.9885 | 485.5072
1832.9885 | 486.5175
1833.9885 | 487.2839
1834.9885 | 490.6188
1835.9885 | 492.0747
1836.9885 | 494.7977
1837.9885 | 496.7029
1838.9885 | 498.2303
1839.9885 | 500.1979
1840.9885 | 501.0817
1841.9885 | 501.0022
1842.9885 | 499.4816
1843.9885 | 498.7306
1844.9885 | 499.2959
1845.9885 | 498.8011
1846.9885 | 498.2833
1847.9885 | 497.7909
1848.9885 | 497.1261
1849.9885 | 500.0261
1850.9885 | 498.5975
1851.9885 | 497.2538
1852.9885 | 497.9877
1853.9885 | 496.3747
1854.9885 | 497.7049
1855.9885 | 499.7488
1856.9885 | 498.3609
1857.9885 | 499.2968
1858.9885 | 499.9788
1859.9885 | 501.0188
1860.9885 | 502.1117
1861.9885 | 502.4399
1862.9885 | 502.4467
1863.9885 | 499.8291
1864.9885 | 497.9533
1865.9885 | 498.2546
1866.9885 | 499.4516
1867.9885 | 499.8778
1868.9885 | 502.0057
1869.9885 | 503.0814
1870.9885 | 502.5413
1871.9885 | 502.2982
1872.9885 | 502.1313
1873.9885 | 501.37
1874.9885 | 503.1586
1875.9885 | 500.3789
1876.9885 | 497.9169
1877.9885 | 494.5596
1878.9885 | 492.5913
1879.9885 | 492.8578
1880.9885 | 494.1669
1881.9885 | 493.1311
1882.9885 | 491.6621
1883.9885 | 493.07
1884.9885 | 496.2186
1885.9885 | 502.291
1886.9885 | 503.6066
1887.9885 | 503.3925
1888.9885 | 504.4061
1889.9885 | 502.674
1890.9885 | 503.1539
1891.9885 | 502.8092
1892.9885 | 503.6682
1893.9885 | 506.0212
1894.9885 | 507.6814
1895.9885 | 505.751
1896.9885 | 504.7431
1897.9885 | 519.3316
1898.9885 | 518.9404
1899.9885 | 518.8716
1900.9885 | 519.08
1901.9885 | 522.1616
1902.9885 | 529.3718
1903.9885 | 526.7317
1904.9885 | 523.8975
1905.9885 | 523.7272
1906.9885 | 525.1978
1907.9885 | 527.8335
1908.9885 | 528.368
1909.9885 | 527.2091
1910.9885 | 525.6893
1911.9885 | 525.0432
1912.9885 | 522.2384
1913.9885 | 520.364
1914.9885 | 518.8558
1915.9885 | 515.6448
1916.9885 | 513.1473
1917.9885 | 512.8607
1918.9885 | 513.6602
1919.9885 | 512.6742
1920.9885 | 510.3159
1921.9885 | 507.0162
1922.9885 | 505.6253
1923.9885 | 505.7513
1924.9885 | 505.3782
1925.9885 | 504.6012
1926.9885 | 501.2781
1927.9885 | 502.4764
1928.9885 | 503.9289
1929.9885 | 502.518
1930.9885 | 504.3256
1931.9885 | 505.0795
1932.9885 | 508.3554
1933.9885 | 506.7432
1934.9885 | 507.3413
1935.9885 | 507.5592
1936.9885 | 508.4712
1937.9885 | 511.2875
1938.9885 | 513.5469
1939.9885 | 512.3595
1940.9885 | 512.4271
1941.9885 | 513.8066
1942.9885 | 514.2412
1943.9885 | 516.4598
1944.9885 | 517.5298
1945.9885 | 518.4146
1946.9885 | 520.6685
1947.9885 | 521.1772
1948.9885 | 523.0447
1949.9885 | 520.7438
1950.9885 | 516.3881
1951.9885 | 513.8215
1952.9885 | 513.4506
1953.9885 | 523.8977
1954.9885 | 524.9285
1955.9885 | 524.7505
1956.9885 | 522.9952
1957.9885 | 522.6276
1958.9885 | 521.3914
1959.9885 | 522.2783
1960.9885 | 540.4094
1961.9885 | 542.6205
1962.9885 | 545.0255
1963.9885 | 540.6303
1964.9885 | 538.7315
1965.9885 | 535.4513
1966.9885 | 533.072
1967.9885 | 531.5018
1968.9885 | 532.9893
1969.9885 | 534.2444
1970.9885 | 535.0097
1971.9885 | 534.3399
1972.9885 | 531.0715
1973.9885 | 533.0199
1974.9885 | 534.2481
1975.9885 | 534.4408
1976.9885 | 532.098
1977.9885 | 529.223
1978.9885 | 527.2844
1979.9885 | 526.1951
1980.9885 | 524.8466
1981.9885 | 526.267
1982.9885 | 524.5052
1983.9885 | 525.4957
1984.9885 | 525.6963
1985.9885 | 524.0001
1986.9885 | 524.5254
1987.9885 | 525.3522
1988.9885 | 525.0115
1989.9885 | 527.3028
1990.9885 | 527.3219
1991.9885 | 526.5479
1992.9885 | 525.7672
1993.9885 | 525.6957
1994.9885 | 525.6412
1995.9885 | 527.1016
1996.9885 | 531.4748
1997.9885 | 533.694
1998.9885 | 532.907
1999.9885 | 531.4579
2000.9885 | 529.1802
2001.9885 | 529.1963
2002.9885 | 529.9359
2003.9885 | 531.0941
2004.9885 | 532.0935
2005.9885 | 536.336
2006.9885 | 536.9007
2007.9885 | 535.6404
2008.9885 | 535.0896
2009.9885 | 534.3154
2010.9885 | 533.8533
2011.9885 | 534.3652
2012.9885 | 533.8749
2013.9885 | 534.9716
2014.9885 | 538.2
2015.9885 | 540.4587
2016.9885 | 540.2635
2017.9885 | 539.2533
2018.9885 | 545.5529
2019.9885 | 561.7718
2020.9885 | 564.4484
2021.9885 | 568.9447
2022.9885 | 568.818
2023.9885 | 569.9281
2024.9885 | 565.7246
2025.9885 | 561.2655
2026.9885 | 561.1538
2027.9885 | 558.6012
2028.9885 | 559.7437
2029.9885 | 558.7766
2030.9885 | 558.3132
2031.9885 | 556.7559
2032.9885 | 560.1355
2033.9885 | 565.4955
2034.9885 | 565.3886
2035.9885 | 563.8196
2036.9885 | 561.9111
2037.9885 | 560.5708
2038.9885 | 559.5966
2039.9885 | 558.2389
2040.9885 | 558.7445
2041.9885 | 557.5989
2042.9885 | 560.0263
2043.9885 | 564.19
2044.9885 | 566.7012
2045.9885 | 564.0732
2046.9885 | 562.4579
2047.9885 | 566.5811
2048.9885 | 567.753
2049.9885 | 569.4385
2050.9885 | 566.5618
2051.9885 | 574.3603
2052.9885 | 579.5675
2053.9885 | 579.6316
2054.9885 | 579.4833
2055.9885 | 579.9128
2056.9885 | 580.7177
2057.9885 | 584.4504
2058.9885 | 595.3457
2059.9885 | 591.066
2060.9885 | 591.8394
2061.9885 | 590.4703
2062.9885 | 606.0618
2063.9885 | 607.6048
2064.9885 | 607.2516
2065.9885 | 604.2884
2066.9885 | 605.4231
2067.9885 | 610.7309
2068.9885 | 610.2924
2069.9885 | 625.3483
2070.9885 | 625.8664
2071.9885 | 632.8596
2072.9885 | 641.6818
2073.9885 | 648.3417
2074.9885 | 651.0582
2075.9885 | 646.8209
2076.9885 | 643.6682
2077.9885 | 635.6989
2078.9885 | 640.486
2079.9885 | 636.2753
2080.9885 | 636.947
2081.9885 | 632.3647
2082.9885 | 637.8282
2083.9885 | 633.4486
2084.9885 | 633.3161
2085.9885 | 626.6363
2086.9885 | 634.5693
2087.9885 | 634.7962
2088.9885 | 641.9563
2089.9885 | 636.9438
2090.9885 | 638.7414
2091.9885 | 628.3981
2092.9885 | 629.4577
2093.9885 | 632.3315
2094.9885 | 636.0719
2095.9885 | 629.7025
2096.9885 | 644.7427
2097.9885 | 642.3526
2098.9885 | 637.7604
2099.9885 | 635.9067
2100.9885 | 641.2023
2101.9885 | 637.0801
2102.9885 | 628.9468
2103.9885 | 629.9095
2104.9885 | 622.5202
2105.9885 | 619.3236
2106.9885 | 614.7906
2107.9885 | 609.9354
2108.9885 | 610.7744
2109.9885 | 609.9095
2110.9885 | 599.7348
2112.0042 | 604.3948
2112.9885 | 608.6489
2113.9885 | 620.4959
2114.9885 | 620.828
2115.9885 | 620.1528
2116.9885 | 614.3815
2117.9885 | 619.6358
2118.9885 | 618.7904
2119.9885 | 611.7437
2120.9885 | 609.6708
2121.9885 | 619.2386
2122.9885 | 618.8563
2123.9885 | 624.4506
2124.9885 | 614.1941
2125.9885 | 645.0422
2126.9885 | 652.234
2127.9885 | 658.8725
2128.9885 | 663.7347
2129.9885 | 667.9853
2130.9885 | 662.0752
2131.9885 | 656.4241
2132.9885 | 647.9474
2133.9885 | 662.8174
2134.9885 | 655.3793
2135.9885 | 651.9101
2136.9885 | 649.3112
2137.9885 | 642.8269
2138.9885 | 643.8513
2139.9885 | 646.9963
2140.9885 | 646.3214
2141.9885 | 645.6291
2142.9885 | 643.7847
2143.9885 | 647.5613
2144.9885 | 643.4835
2145.9885 | 636.4425
2146.9885 | 647.3687
2147.9885 | 657.5072
2148.9885 | 654.9229
2149.9885 | 651.3157
2150.9885 | 648.2172
2151.9885 | 649.3206
2152.9885 | 651.972
2153.9885 | 650.648
2154.9885 | 658.8194
2155.9885 | 657.2969
2156.9885 | 658.5688
2157.9885 | 659.8919
2158.9885 | 663.5501
2159.9885 | 694.9993
2160.9885 | 699.709
2161.9885 | 701.7982
2162.9885 | 702.2845
2163.9885 | 697.8729
2164.9885 | 692.4131
2165.9885 | 710.0716
2166.9885 | 711.958
2167.9885 | 729.7155
2168.9885 | 733.8587
2169.9885 | 737.7746
2170.9885 | 731.9765
2171.9885 | 746.01
2172.9885 | 748.2977
2173.9885 | 733.157
2174.9885 | 746.1992
2175.9885 | 759.9129
2176.9885 | 768.8413
2177.9885 | 782.1394
2178.9885 | 780.8937
2179.9885 | 780.698
2180.9885 | 783.7726
2181.9885 | 787.664
2182.9885 | 785.4444
2183.9885 | 791.6275
2184.9885 | 789.6595
2185.9885 | 795.1817
2186.9885 | 792.2274
2187.9885 | 797.5076
2188.9885 | 795.3779
2189.9885 | 795.0028
2190.9885 | 790.7021
2191.9885 | 787.4356
2192.9885 | 795.8187
2193.9885 | 794.8834
2194.9885 | 789.6209
2195.9885 | 802.1104
2196.9885 | 802.9615
2197.9885 | 810.9281
2198.9885 | 806.4948
2199.9885 | 808.2275
2200.9885 | 807.6026
2201.9885 | 805.5835
2202.9885 | 805.1053
2203.9885 | 795.2854
2204.9885 | 799.4035
2205.9885 | 803.6502
2206.9885 | 795.4088
2207.9885 | 804.8806
2208.9885 | 805.0657
2209.9885 | 797.7712
2210.9885 | 812.6524
2211.9885 | 810.2112
2212.9885 | 811.9674
2213.9885 | 807.4131
2214.9885 | 815.0089
2215.9885 | 808.731
2216.9885 | 815.0608
2217.9885 | 809.6348
2218.9885 | 804.9997
2219.9885 | 797.627
2220.9885 | 797.8133
2221.9885 | 797.268
2222.9885 | 793.626
2223.9885 | 794.4038
2224.9885 | 816.3717
2225.9885 | 820.3299
2226.9885 | 819.7975
2227.9885 | 824.3271
2228.9885 | 820.1383
2229.9885 | 822.7677
2230.9885 | 821.2624
2231.9885 | 817.6406
2232.9885 | 817.3376
2233.9885 | 829.3486
2234.9885 | 827.0283
2235.9885 | 825.9052
2236.9885 | 837.2778
2237.9885 | 827.1663
2238.9885 | 819.6669
2239.9885 | 821.644
2240.9885 | 828.0102
2241.9885 | 825.3763
2242.9885 | 827.3642
2243.9885 | 834.209
2244.9885 | 823.3478
2245.9885 | 826.3128
2246.9885 | 826.0254
2247.9885 | 831.0384
2248.9885 | 836.7704
2249.9885 | 838.1915
2250.9885 | 837.4038
2251.9885 | 834.9741
2252.9885 | 831.9301
2253.9885 | 833.0606
2254.9885 | 834.0278
2255.9885 | 827.3372
2256.9885 | 829.2945
2257.9885 | 820.8655
2258.9885 | 816.0992
2259.9885 | 826.8069
2260.9885 | 822.9158
2261.9885 | 817.1897
2262.9885 | 818.0581
2263.9885 | 810.8136
2264.9885 | 818.1256
2265.9885 | 816.6178
2266.9885 | 810.7314
2267.9885 | 805.0802
2268.9885 | 806.536
2269.9885 | 812.3068
2270.9885 | 808.7233
2271.9885 | 802.41
2272.9885 | 796.985
2273.9885 | 787.2262
2274.9885 | 795.4978
2275.9885 | 800.9234
2276.9885 | 804.0204
2277.9885 | 794.6489
2278.9885 | 788.2176
2279.9885 | 790.6643
2280.9885 | 786.6716
2281.9885 | 783.9108
2282.9885 | 784.4908
2283.9885 | 791.5086
2284.9885 | 784.8638
2285.9885 | 777.8977
2286.9885 | 790.0398
2287.9885 | 782.6793
2288.9885 | 771.7884
2289.9885 | 768.2043
2290.9885 | 773.4368
2291.9885 | 774.5394
2292.9885 | 782.2919
2293.9885 | 788.257
2294.9885 | 777.7118
2295.9885 | 776.8083
2296.9885 | 768.9512
2297.9885 | 764.3344
2298.9885 | 760.0343
2299.9885 | 759.3578
2300.9885 | 768.6702
2301.9885 | 772.1514
2302.9885 | 764.663
2303.9885 | 755.6871
2304.9885 | 761.459
2305.9885 | 759.9976
2306.9885 | 756.1751
2307.9885 | 753.1056
2308.9885 | 752.7652
2309.9885 | 761.445
2310.9885 | 756.2837
2311.9885 | 751.894
2312.9885 | 745.6734
2313.9885 | 743.9552
2314.9885 | 748.9843
2315.9885 | 758.3114
2316.9885 | 759.6457
2317.9885 | 755.5944
2318.9885 | 748.1185
2319.9885 | 741.5483
2320.9885 | 752.002
2321.9885 | 748.8089
2322.9885 | 745.1806
2323.9885 | 744.0052
2324.9885 | 740.212
2325.9885 | 739.4235
2326.9885 | 735.8067
2327.9885 | 727.3353
2328.9885 | 728.3711
2329.9885 | 732.2312
2330.9885 | 739.3454
2331.9885 | 755.687
2332.9885 | 750.517
2333.9885 | 753.0281
2334.9885 | 752.5031
2335.9885 | 756.9108
2336.9885 | 749.1076
2337.9885 | 747.5329
2338.9885 | 758.172
2339.9885 | 758.4497
2340.9885 | 755.1904
2341.9885 | 755.5077
2342.9885 | 756.6482
2343.9885 | 758.6633
2344.9885 | 757.4058
2345.9885 | 762.7537
2346.9885 | 761.8985
2347.9885 | 771.1592
2348.9885 | 773.3775
2349.9885 | 774.854
2350.9885 | 772.1931
2351.9885 | 761.1333
2352.9885 | 758.6571
2353.9885 | 762.875
2354.9885 | 759.1596
2355.9885 | 753.4569
2356.9885 | 748.5511
2357.9885 | 748.9559
2358.9885 | 745.5025
2359.9885 | 756.0657
2360.9885 | 757.5979
2361.9885 | 754.2203
2362.9885 | 752.2201
2363.9885 | 744.8836
2364.9885 | 742.8464
2365.9885 | 737.9478
2366.9885 | 751.062
2367.9885 | 755.3775
2368.9885 | 751.1061
2369.9885 | 740.9255
2370.9885 | 743.1734
2371.9885 | 737.3615
2372.9885 | 738.1896
2373.9885 | 736.4159
2374.9885 | 744.0629
2375.9885 | 741.255
2376.9885 | 728.8342
2377.9885 | 729.9835
2378.9885 | 728.3096
2379.9885 | 737.6994
2380.9885 | 732.1649
2381.9885 | 729.0917
2382.9885 | 722.6085
2383.9885 | 723.2327
2384.9885 | 723.7886
2385.9885 | 718.3258
2386.9885 | 712.3045
2387.9885 | 713.81
2388.9885 | 734.7947
2389.9885 | 731.214
2390.9885 | 735.1868
2391.9885 | 730.9498
2392.9885 | 721.3545
2393.9885 | 718.3187
2394.9885 | 731.9704
2395.9885 | 728.9917
2396.9885 | 738.2997
2397.9885 | 732.0207
2398.9885 | 725.4617
2399.9885 | 721.9756
2400.9885 | 726.5003
2401.9885 | 717.655
2402.9885 | 719.6392
2403.9885 | 721.3566
2404.9885 | 721.72
2405.9885 | 720.0418
2406.9885 | 713.5248
2407.9885 | 717.2319
2408.9885 | 723.0347
2409.9885 | 721.4515
2410.9885 | 729.403
2411.9885 | 732.0427
2412.9885 | 725.908
2413.9885 | 723.1154
2414.9885 | 716.0441
2415.9885 | 719.1154
2416.9885 | 721.0821
2417.9885 | 721.4742
2418.9885 | 727.551
2419.9885 | 719.8392
2420.9885 | 712.7752
2421.9885 | 710.796
2422.9885 | 713.8578
2423.9885 | 710.1372
2424.9885 | 713.0926
2425.9885 | 709.5264
2426.9885 | 705.2993
2427.9885 | 700.9167
2428.9885 | 702.5854
2429.9885 | 699.37
2430.9885 | 699.5114
2431.9885 | 698.4829
2432.9885 | 708.878
2433.9885 | 714.0566
2434.9885 | 712.3622
2435.9885 | 714.6642
2436.9885 | 716.3389
2437.9885 | 715.2603
2438.9885 | 720.1201
2439.9885 | 713.8552
2440.9885 | 718.3258
2441.9885 | 725.2078
2442.9885 | 720.8967
2443.9885 | 719.6802
2444.9885 | 715.5632
2445.9885 | 707.008
2446.9885 | 702.9577
2447.9885 | 697.7469
2448.9885 | 698.747
2449.9885 | 702.407
2450.9885 | 705.9903
2451.9885 | 721.0154
2452.9885 | 728.8588
2453.9885 | 732.235
2454.9885 | 729.6861
2455.9885 | 725.1795
2456.9885 | 737.7145
2457.9885 | 730.7737
2458.9885 | 732.1674
2459.9885 | 724.2597
2460.9885 | 717.6366
2461.9885 | 712.3421
2462.9885 | 720.9054
2463.9885 | 716.895
2464.9885 | 715.1421
2465.9885 | 718.2027
2466.9885 | 719.4973
2467.9885 | 715.6513
2468.9885 | 710.3643
2469.9885 | 705.3402
2470.9885 | 699.9659
2471.9885 | 699.3434
2472.9885 | 699.7941
2473.9885 | 699.055
2474.9885 | 706.8338
2475.9885 | 700.1533
2476.9885 | 698.2608
2477.9885 | 696.1824
2478.9885 | 702.6159
2479.9885 | 709.7006
2480.9885 | 703.108
2481.9885 | 700.4081
2482.9885 | 701.9508
2483.9885 | 700.6319
2484.9885 | 696.5668
2485.9885 | 692.5815
2486.9885 | 701.9064
2487.9885 | 707.8773
2488.9885 | 708.805
2489.9885 | 705.1466
2490.9885 | 703.4581
2491.9885 | 710.9358
2492.9885 | 706.3502
2493.9885 | 714.2264
2494.9885 | 721.0163
2495.9885 | 730.2239