## Test Conditions
DESIREE-FIRE Test Number Japanese 2 - Circuit Simulator Data Only
Test Date: | 2009-09-16
DCSim DAQ Start Time | 15:32
DCSim Time for Synchronization | 15:45
Heat Source Synchronization | 12:27 | minutes:seconds
Heat Source DAQ Start Time | 15:33
Heat Source Start Time | 16:14
DCSim Offset | 0:42 | minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 2535 | seconds
Heat Source Offset | 0:41 | minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 2487 | seconds
Heat Source Stop Time | 16:55
Test Duration | 0:41 | minutes:seconds
| 2430 | seconds
CT500 Turns | 2 |  | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 Turns | 5
Pre-Test Baseline: | Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit number | Cable Type |  | Cable TC channel | Air TC Channel
SWGR Close | Mitsubishi, 6c, 14AWG |  | When looking into the opening of Penlight, Channel 3 and Channel 4 of the second system represent the trip and close thermocouple cable, respectively. | Channel 4 of the first system in the Temperature Data File
SWGR Trip | Mitsubishi, 6c, 14AWG |  | When looking into the opening of Penlight, Channel 3 and Channel 4 of the second system represent the trip and close thermocouple cable, respectively. | Channel 4 of the first system in the Temperature Data File
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | SWGR_CT500 | SWGR-a_CT35_1_PC | SWGR-a_CT35_2_N1 | SWGR-b_CT35_1_PT | SWGR-b_CT35_2_G | SWGR-b_CT35_3_R | SWGR-b_CT35_4_N2 | SWGR-a_VT7_1_C1 | SWGR-a_VTU_1_PC | SWGR-a_VTU_2_N1 | SWGR-b_VT7_1_G | SWGR-b_VT7_2_R | SWGR-b_VT7_3_T | SWGR-b_VT7_4_SP | SWGR-b_VT7_5_SP | SWGR-b_VTU_1_PT | SWGR-b_VTU_2_N2 | {SWGR-C} V(N1) - V(Batt -) | {SWGR-C} V(PC) - V(Batt +) | {SWGR-C} V(C1) - V(Batt -) | {SWGR-T} V(G) - V(Batt -) | {SWGR-T} V(G) - V(N) | {SWGR-T} V(R) - V(Batt +) | {SWGR-T} V(R) - V(N) | {SWGR-T} V(N2) - V(Batt -) | {SWGR-T} V(PT) - V(Batt +) | {SWGR-C} V(C1) - V(N1)
-0.42188 | 122.8821 | -60.7452 | 61.8118 | 0.4218 | 0.010264 | 0.0073751 | 0.0028585 | 0.066711 | -0.0011597 | 0.069682 | -60.8643 | 61.8393 | -60.965 | -60.9604 | 61.5784 | 0.022888 | -0.11902 | 0.07782 | 61.734 | -61.0062 | -0.21973 | 0.027465 | -0.11902 | -0.21515 | 0.045777 | -0.23346 | -0.15564 | -0.26093 | -0.07782 | 0.10071
0.57812 | 122.8226 | -60.7315 | 61.8439 | 1.673 | 0.009196 | 0.010793 | 0.0030721 | 0.065643 | -0.0003051 | 0.068614 | -61.0519 | 61.7981 | -61.0291 | -60.9467 | 61.5463 | -0.009155 | -0.032043 | 0.09613 | 61.8027 | -61.0016 | -0.29755 | -0.045776 | -0.32043 | -0.21515 | 0.054932 | -0.29755 | -0.25635 | -0.27008 | -0.041199 | -0.022888
1.5781 | 122.8134 | -60.7315 | 61.8301 | 0.40654 | 0.013896 | 0.01122 | 0.0022177 | 0.064148 | -0.0020141 | 0.068827 | -60.8597 | 61.8576 | -60.9833 | -60.9833 | 61.528 | -0.036621 | -0.082397 | 0.032043 | 61.7889 | -61.0062 | -0.25177 | 0.027466 | -0.12817 | -0.25177 | 0.022889 | -0.30212 | -0.26092 | -0.27466 | -0.041199 | 0.1236
2.5781 | 122.8409 | -60.7452 | 61.8622 | 0.38365 | 0.0094096 | 0.0084431 | 0.0030721 | 0.066284 | 0.0007629 | 0.068187 | -60.8597 | 61.8622 | -60.965 | -60.9833 | 61.5189 | -0.045776 | -0.041199 | 0 | 61.821 | -61.0336 | -0.21973 | 0 | -0.11444 | -0.23804 | 0.050354 | -0.34332 | -0.30212 | -0.28839 | -0.041199 | 0.10529
3.5781 | 122.7631 | -60.7773 | 61.8484 | 0.27684 | 0.0098368 | 0.0050251 | 0.0058493 | 0.065216 | -0.0011597 | 0.067759 | -60.8963 | 61.9034 | -60.9924 | -61.0291 | 61.4777 | -0.054932 | 0.027466 | 0.004578 | 61.8118 | -61.0245 | -0.21515 | 0.054931 | -0.11902 | -0.25177 | -0.004578 | -0.37079 | -0.33417 | -0.24719 | -0.036621 | 0.096131
4.5781 | 122.7814 | -60.7636 | 61.8668 | 0.41417 | 0.0089824 | 0.0067341 | 0.0024313 | 0.066711 | 0.0005493 | 0.067332 | -60.878 | 61.8439 | -60.9833 | -60.997 | 61.5143 | -0.054932 | -0.009155 | -0.004578 | 61.8118 | -61.0199 | -0.21973 | -0.022888 | -0.11444 | -0.23346 | 0.022888 | -0.35248 | -0.29755 | -0.25635 | -0.054931 | 0.10528
5.5781 | 122.8409 | -60.7498 | 61.8301 | 0.38365 | 0.013468 | 0.0067341 | 0.0032857 | 0.065857 | 0.0020447 | 0.0684 | -60.8688 | 61.8347 | -60.965 | -60.9879 | 61.5417 | -0.027466 | -0.091553 | 0.045776 | 61.7844 | -61.0519 | -0.21515 | 0.004578 | -0.11902 | -0.23804 | 0.064087 | -0.28839 | -0.24262 | -0.30212 | -0.045776 | 0.096131
6.5781 | 122.8271 | -60.7452 | 61.8484 | 0.32261 | 0.0085552 | 0.0063069 | 0.0047811 | 0.066284 | 0.0011901 | 0.068614 | -60.8597 | 61.8301 | -60.9787 | -60.9787 | 61.528 | -0.027466 | -0.068665 | 0.027466 | 61.8256 | -61.0245 | -0.23346 | -0.018311 | -0.11444 | -0.23346 | 0.045776 | -0.32043 | -0.29755 | -0.27924 | -0.022888 | 0.11902
7.5781 | 122.8317 | -60.7636 | 61.8439 | 0.35313 | 0.0089824 | 0.0090841 | 0.0015767 | 0.065857 | -0.0018005 | 0.069682 | -60.8597 | 61.8759 | -60.9924 | -60.9924 | 61.5234 | -0.036621 | -0.073242 | 0.013733 | 61.7889 | -61.0153 | -0.22888 | 0.032044 | -0.09613 | -0.22888 | 0.022888 | -0.32043 | -0.2655 | -0.25177 | -0.054932 | 0.13275
8.5781 | 122.7402 | -60.7544 | 61.8713 | 0.35313 | 0.011759 | 0.0075887 | 0.0017903 | 0.067139 | 0.0020447 | 0.067546 | -60.8917 | 61.8896 | -60.965 | -61.0199 | 61.5051 | -0.068665 | 0.009155 | -0.004578 | 61.7981 | -61.0519 | -0.21057 | 0.01831 | -0.13733 | -0.2655 | 0.032044 | -0.36621 | -0.29297 | -0.29755 | -0.073242 | 0.073242
9.5781 | 122.818 | -60.7819 | 61.8576 | 0.38365 | 0.0094096 | 0.012075 | 0.0028585 | 0.064789 | 0.0020447 | 0.069255 | -60.8826 | 61.8805 | -60.965 | -60.9924 | 61.5417 | -0.045776 | -0.013733 | 0.018311 | 61.8027 | -61.0474 | -0.18311 | 0.022888 | -0.10071 | -0.21057 | 0.054931 | -0.31586 | -0.26093 | -0.2655 | -0.054932 | 0.082398
10.5781 | 122.7768 | -60.7498 | 61.8484 | 0.35313 | 0.011759 | 0.011434 | 0.0041403 | 0.065857 | 0.0007629 | 0.067759 | -60.8734 | 61.8759 | -60.965 | -61.0291 | 61.4914 | -0.059509 | 0.009155 | 0.009155 | 61.8164 | -61.0611 | -0.21515 | 0.027466 | -0.1236 | -0.27924 | 0.032043 | -0.35706 | -0.32501 | -0.31128 | -0.032044 | 0.091553
11.5781 | 122.7951 | -60.7773 | 61.853 | 0.37602 | 0.011119 | 0.010152 | 0.0024313 | 0.065643 | 0.0005493 | 0.070323 | -60.8826 | 61.8759 | -60.9787 | -61.0016 | 61.5234 | -0.045776 | -0.004578 | 0.004578 | 61.8164 | -61.0245 | -0.20142 | 0.022889 | -0.10529 | -0.2243 | 0.022888 | -0.32959 | -0.29297 | -0.24719 | -0.036621 | 0.096131
12.5781 | 122.8363 | -60.759 | 61.8164 | 0.44468 | 0.011332 | 0.0092977 | 0.00029507 | 0.067779 | -0.0003051 | 0.067332 | -60.8551 | 61.8301 | -60.9558 | -60.9604 | 61.5463 | 0 | 0.082397 | 0.16022 | 61.8164 | -60.997 | -0.19684 | 0.013733 | -0.096131 | -0.20142 | 0.036621 | -0.27008 | -0.27008 | -0.23804 | 0 | 0.10071
13.5781 | 122.8592 | -60.7315 | 61.8256 | 0.42943 | 0.0098368 | 0.01122 | 0.0022177 | 0.065216 | -0.0003051 | 0.067759 | -60.8459 | 61.8484 | -60.965 | -60.9604 | 61.5463 | -0.013733 | -0.11902 | 0.064087 | 61.7615 | -61.0016 | -0.23346 | 0.022888 | -0.11444 | -0.22888 | 0.041199 | -0.27924 | -0.21515 | -0.27008 | -0.064087 | 0.11902
14.5781 | 122.905 | -60.7361 | 61.8439 | 0.45231 | 0.010264 | 0.0095113 | 0.0030721 | 0.067352 | -0.0005189 | 0.069255 | -60.8551 | 61.8301 | -60.965 | -60.9558 | 61.5646 | -0.022888 | -0.10071 | 0.059509 | 61.7889 | -61.0153 | -0.22888 | -0.013733 | -0.11902 | -0.21973 | 0.059509 | -0.27924 | -0.2243 | -0.27924 | -0.054932 | 0.10986
15.5781 | 122.8409 | -60.7315 | 61.8347 | 0.4218 | 0.0085552 | 0.010793 | 0.0037129 | 0.065857 | -9.1495e-05 | 0.069041 | -60.8688 | 61.853 | -60.9741 | -60.965 | 61.5417 | -0.018311 | -0.07782 | 0.050354 | 61.7798 | -61.0153 | -0.24261 | 0.01831 | -0.13733 | -0.23346 | 0.050354 | -0.29297 | -0.23804 | -0.28381 | -0.054932 | 0.10529
16.5781 | 122.8409 | -60.7544 | 61.8301 | 0.39128 | 0.0098368 | 0.0095113 | 0.0039267 | 0.065857 | 0.0003357 | 0.0684 | -60.8688 | 61.8576 | -60.9741 | -60.9695 | 61.5372 | -0.018311 | -0.082397 | 0.041199 | 61.8027 | -61.0062 | -0.21973 | 0.027466 | -0.11444 | -0.21515 | 0.036622 | -0.29297 | -0.2655 | -0.25177 | -0.027466 | 0.10529
17.5781 | 122.7676 | -60.7773 | 61.8622 | 0.37602 | 0.0072734 | 0.0069477 | 0.0034993 | 0.064575 | -0.0011597 | 0.069041 | -60.8826 | 61.8622 | -60.9695 | -61.0062 | 61.4914 | -0.059509 | 0.004578 | -0.004578 | 61.8118 | -61.0291 | -0.19226 | 0 | -0.10529 | -0.22888 | 0.022888 | -0.37079 | -0.32044 | -0.25177 | -0.050354 | 0.086975
18.5781 | 122.8271 | -60.7636 | 61.8256 | 0.38365 | 0.0096232 | 0.0065205 | 0.0020039 | 0.066498 | -0.0003051 | 0.068187 | -60.8734 | 61.853 | -60.9924 | -60.9879 | 61.5234 | -0.036621 | -0.045776 | 0.018311 | 61.7935 | -61.0199 | -0.22888 | 0.027465 | -0.10986 | -0.2243 | 0.032043 | -0.30212 | -0.27008 | -0.25635 | -0.032044 | 0.11902
19.5781 | 122.8638 | -60.7315 | 61.821 | 0.44468 | 0.0087688 | 0.0088703 | 0.0034993 | 0.06842 | 0.0011901 | 0.068614 | -60.8688 | 61.8301 | -60.9558 | -60.9375 | 61.5692 | 0.009155 | -0.15106 | 0.073242 | 61.7706 | -61.0199 | -0.2243 | 0.009155 | -0.13733 | -0.20599 | 0.082397 | -0.25177 | -0.20142 | -0.28839 | -0.050354 | 0.086976
20.5781 | 122.8729 | -60.7224 | 61.8301 | 0.43706 | 0.0096232 | 0.0020345 | 0.0017903 | 0.067352 | -0.0003051 | 0.070323 | -60.8505 | 61.8484 | -60.9833 | -60.878 | 61.4502 | -0.073242 | -0.10986 | 0.10529 | 61.7661 | -61.0291 | -0.26092 | 0.018311 | -0.12817 | -0.15564 | 0.15106 | -0.37994 | -0.31586 | -0.3067 | -0.064087 | 0.13275
21.5781 | 122.8317 | -60.7315 | 61.8256 | 0.41417 | 0.0094096 | 0.010366 | 0.0045675 | 0.066284 | 0.0018311 | 0.066264 | -60.8551 | 61.8439 | -60.9695 | -60.9558 | 61.5509 | 0.004578 | 0.07782 | 0.14648 | 61.7935 | -61.0107 | -0.23804 | 0.01831 | -0.1236 | -0.2243 | 0.054931 | -0.27466 | -0.24262 | -0.27924 | -0.032044 | 0.11444
22.5781 | 122.818 | -60.7452 | 61.8439 | 0.41417 | 0.0098368 | 0.0088703 | 0.0032857 | 0.06543 | -0.0024415 | 0.069682 | -60.8459 | 61.8439 | -60.9787 | -60.9467 | 61.5509 | -0.027466 | -0.10071 | 0.050354 | 61.7798 | -61.0291 | -0.23346 | 0 | -0.10071 | -0.20142 | 0.082398 | -0.29297 | -0.22888 | -0.28381 | -0.064087 | 0.13275
23.5781 | 122.7905 | -60.7773 | 61.8851 | 0.35313 | 0.0087688 | 0.0082295 | 0.0043539 | 0.064789 | 0.0009765 | 0.067332 | -60.8231 | 61.8988 | -60.9741 | -60.9787 | 61.5189 | -0.027466 | 0.036621 | 0.032043 | 61.821 | -61.0657 | -0.19684 | 0.013733 | -0.045776 | -0.20142 | 0.086975 | -0.36621 | -0.30212 | -0.28839 | -0.064087 | 0.15106
24.5781 | 122.7997 | -60.7498 | 61.8393 | 0.37602 | 0.011759 | 0.0082295 | 0.0032857 | 0.06543 | 0.0001221 | 0.07075 | -60.8643 | 61.8576 | -60.997 | -60.9879 | 61.5372 | -0.041199 | -0.050354 | 0.027466 | 61.8301 | -61.0245 | -0.24719 | 0.018311 | -0.11444 | -0.23804 | 0.036621 | -0.30212 | -0.29297 | -0.27466 | -0.009155 | 0.13275
25.5781 | 122.9141 | -60.7224 | 61.8347 | 0.42943 | 0.0072734 | 0.0095113 | 0.0028585 | 0.066498 | 0.0001221 | 0.069041 | -60.9421 | 61.8118 | -60.9604 | -60.9238 | 61.5692 | 0.027466 | -0.16022 | 0.082397 | 61.7615 | -61.0016 | -0.23804 | -0.022888 | -0.21973 | -0.20142 | 0.07782 | -0.2655 | -0.19226 | -0.27924 | -0.073242 | 0.01831
26.5781 | 122.85 | -60.7269 | 61.8347 | 0.36076 | 0.0096232 | 0.0067341 | 0.0017903 | 0.065216 | 0.0003357 | 0.070109 | -60.8414 | 61.8256 | -60.965 | -60.8231 | 61.6745 | 0.054932 | -0.25635 | 0.068665 | 61.7844 | -61.0291 | -0.23804 | -0.009155 | -0.11444 | -0.09613 | 0.20599 | -0.16022 | -0.10986 | -0.30212 | -0.050354 | 0.1236
27.5781 | 122.8683 | -60.7315 | 61.8347 | 0.4218 | 0.0087688 | 0.0078023 | 0.0032857 | 0.06543 | 0.0028991 | 0.068614 | -60.8551 | 61.8439 | -60.965 | -60.9512 | 61.5509 | -0.009155 | -0.10986 | 0.059509 | 61.7661 | -61.0199 | -0.23346 | 0.009155 | -0.1236 | -0.21973 | 0.068664 | -0.28381 | -0.21515 | -0.28839 | -0.068665 | 0.10986
28.5781 | 122.8363 | -60.7315 | 61.8256 | 0.39128 | 0.01005 | 0.0092977 | 0.0041403 | 0.06543 | 0.0018311 | 0.067118 | -60.8643 | 61.8576 | -60.9924 | -60.9604 | 61.5372 | -0.018311 | -0.10071 | 0.041199 | 61.7889 | -61.0474 | -0.26093 | 0.032043 | -0.13275 | -0.22888 | 0.086975 | -0.28839 | -0.25177 | -0.31586 | -0.036622 | 0.12817
29.5781 | 122.8271 | -60.7544 | 61.853 | 0.30736 | 0.0098368 | 0.0099385 | 0.0045675 | 0.065002 | -0.0007325 | 0.07075 | -60.8505 | 61.8805 | -60.9833 | -60.9833 | 61.5097 | -0.050354 | -0.045776 | 0.018311 | 61.7981 | -61.0428 | -0.22888 | 0.027466 | -0.09613 | -0.22888 | 0.05951 | -0.34332 | -0.28839 | -0.28839 | -0.054931 | 0.13275
30.5781 | 122.7631 | -60.759 | 61.8484 | 0.32261 | 0.01005 | 0.01122 | 0.0049947 | 0.068207 | -9.1495e-05 | 0.067973 | -60.8871 | 61.8759 | -61.0016 | -61.0016 | 61.5051 | -0.059509 | 0.018311 | 0 | 61.8256 | -61.0428 | -0.24262 | 0.027466 | -0.12817 | -0.24262 | 0.041199 | -0.34332 | -0.32043 | -0.28381 | -0.022888 | 0.11444
31.5781 | 122.7814 | -60.7544 | 61.8713 | 0.3455 | 0.0096232 | 0.0067341 | 0.0056355 | 0.067139 | -0.0018005 | 0.069896 | -60.878 | 61.8668 | -60.997 | -61.0107 | 61.5189 | -0.045776 | -0.022888 | 0.004578 | 61.8164 | -61.0336 | -0.24261 | -0.004578 | -0.1236 | -0.25635 | 0.022888 | -0.35248 | -0.29755 | -0.27923 | -0.054932 | 0.11902
32.5781 | 122.85 | -60.7498 | 61.853 | 0.4218 | 0.0089824 | 0.0080159 | 0.00050867 | 0.06308 | 0.0005493 | 0.068614 | -60.8688 | 61.821 | -60.9741 | -60.9558 | 61.5463 | -0.013733 | -0.09613 | 0.036621 | 61.7935 | -61.0245 | -0.2243 | -0.032043 | -0.11902 | -0.20599 | 0.068664 | -0.3067 | -0.24719 | -0.27466 | -0.059509 | 0.10529
33.5781 | 122.7997 | -60.7224 | 61.8347 | 0.3455 | 0.009196 | 0.0058797 | 0.0022177 | 0.066711 | 0.0020447 | 0.068187 | -60.8734 | 61.8439 | -60.9467 | -60.9833 | 61.5372 | -0.041199 | -0.07782 | 0.032043 | 61.8118 | -61.0382 | -0.2243 | 0.009155 | -0.15106 | -0.26092 | 0.054932 | -0.29755 | -0.27466 | -0.31586 | -0.022888 | 0.073242
34.5781 | 122.8363 | -60.7727 | 61.8439 | 0.38365 | 0.01005 | 0.0090841 | 0.00093587 | 0.066711 | -0.0005189 | 0.068187 | -60.8597 | 61.8393 | -60.9741 | -60.9879 | 61.5372 | -0.054932 | -0.036621 | 0.013733 | 61.7935 | -61.0291 | -0.20142 | -0.004578 | -0.086975 | -0.21515 | 0.041199 | -0.3067 | -0.25635 | -0.25635 | -0.050354 | 0.11444
35.5781 | 122.8134 | -60.759 | 61.853 | 0.35313 | 0.0089824 | 0.0088703 | 0.00093587 | 0.065857 | 0.0005493 | 0.068614 | -60.8688 | 61.8851 | -60.9604 | -61.0016 | 61.5097 | -0.050354 | -0.009155 | 0.013733 | 61.7981 | -61.0382 | -0.20142 | 0.032044 | -0.10986 | -0.24262 | 0.036621 | -0.34332 | -0.28839 | -0.27924 | -0.054931 | 0.091553
36.5781 | 122.7859 | -60.7636 | 61.8576 | 0.37602 | 0.011759 | 0.0069477 | 0.0024313 | 0.06607 | 0.0026855 | 0.070109 | -60.8643 | 61.8988 | -60.9787 | -61.0016 | 61.5051 | -0.050354 | -0.009155 | 0.013733 | 61.8164 | -61.0428 | -0.21515 | 0.041199 | -0.10071 | -0.23804 | 0.041199 | -0.35248 | -0.31128 | -0.27924 | -0.041199 | 0.11444
37.5781 | 122.7951 | -60.759 | 61.8713 | 0.26921 | 0.009196 | 0.0058797 | 0.0047811 | 0.067352 | 0.0003357 | 0.069255 | -60.8688 | 61.8851 | -60.9924 | -61.0062 | 61.5234 | 0.004578 | 0.036621 | 0.041199 | 61.8484 | -61.0474 | -0.23346 | 0.013733 | -0.10986 | -0.24719 | 0.041198 | -0.3479 | -0.32501 | -0.28839 | -0.022888 | 0.1236
38.5781 | 122.7585 | -60.7544 | 61.8484 | 0.32261 | 0.0096232 | 0.0050251 | 0.0020039 | 0.069275 | -0.0009461 | 0.069468 | -60.878 | 61.8896 | -60.9833 | -61.0199 | 61.4731 | -0.041199 | 0.018311 | -0.004578 | 61.8347 | -61.0428 | -0.22888 | 0.041198 | -0.1236 | -0.2655 | 0.022889 | -0.37537 | -0.36163 | -0.28839 | -0.013733 | 0.10528
39.5781 | 122.8134 | -60.7681 | 61.8713 | 0.36839 | 0.012828 | 0.0080159 | 0.0045675 | 0.068634 | -9.1495e-05 | 0.070536 | -60.8734 | 61.8759 | -60.9924 | -61.0153 | 61.5143 | -0.050354 | -0.013733 | 0.018311 | 61.821 | -61.0336 | -0.22431 | 0.004578 | -0.10529 | -0.24719 | 0.01831 | -0.35706 | -0.3067 | -0.2655 | -0.050354 | 0.11902
40.5781 | 122.9141 | -60.704 | 61.8301 | 0.15477 | 0.0072734 | 0.0026753 | -0.0086771 | 0.065216 | -0.0009461 | 0.069255 | -60.8276 | 61.7661 | -60.9467 | -60.8826 | 61.647 | 0.11902 | -0.041199 | 0.20142 | 61.8073 | -60.9467 | -0.24261 | -0.064087 | -0.1236 | -0.17853 | 0.064087 | -0.18311 | -0.16022 | -0.24261 | -0.022888 | 0.11902
41.5781 | 122.8088 | -60.7773 | 61.8439 | 0.31499 | 0.010691 | 0.0090841 | 0.0045675 | 0.066498 | -0.0007325 | 0.069041 | -60.8826 | 61.853 | -60.9558 | -61.0062 | 61.5005 | -0.045776 | 0.009155 | -0.018311 | 61.8393 | -61.0428 | -0.17853 | 0.009155 | -0.10529 | -0.22888 | 0.036621 | -0.34332 | -0.33875 | -0.2655 | -0.004578 | 0.073243
42.5781 | 122.7448 | -60.7956 | 61.8393 | 0.33024 | 0.0098368 | 0.0095113 | 0.0049947 | 0.066711 | 0.0001221 | 0.0684 | -60.8505 | 61.8942 | -60.9695 | -61.0107 | 61.4868 | -0.050354 | 0.045776 | -0.004578 | 61.8301 | -61.0107 | -0.17395 | 0.054932 | -0.054932 | -0.21515 | 0 | -0.35248 | -0.34332 | -0.21515 | -0.009155 | 0.11902
43.5781 | 122.7722 | -60.7727 | 61.8713 | 0.032698 | 0.0083416 | 0.0082295 | 0.0047811 | 0.068207 | -0.0022277 | 0.068614 | -60.8368 | 61.9034 | -60.9741 | -60.9833 | 61.5326 | -0.045776 | 0.050354 | 0.032043 | 61.8256 | -61.0336 | -0.20142 | 0.032043 | -0.064087 | -0.21057 | 0.050354 | -0.33875 | -0.29297 | -0.26093 | -0.045776 | 0.13733
44.5781 | 122.85 | -60.7498 | 61.853 | 0.13188 | 0.010264 | 0.0088703 | 0.0017903 | 0.069061 | -0.0003051 | 0.067759 | -60.8002 | 61.8668 | -60.9695 | -60.9238 | 61.5784 | 0.050354 | 0.027466 | 0.1236 | 61.8439 | -61.0062 | -0.21973 | 0.013733 | -0.050354 | -0.17395 | 0.082398 | -0.27466 | -0.2655 | -0.25635 | -0.009155 | 0.16937
45.5781 | 122.85 | -60.704 | 61.8301 | 0.20817 | 0.0062052 | 0.0065205 | -0.0044047 | 0.067779 | 0.0003357 | 0.068827 | -60.8688 | 61.7569 | -60.9741 | -60.965 | 61.5967 | 0.036621 | -0.036621 | 0.11902 | 61.7935 | -60.9604 | -0.27008 | -0.073242 | -0.16479 | -0.26093 | -0.004578 | -0.23346 | -0.19684 | -0.25635 | -0.036621 | 0.10529
46.5781 | 122.7631 | -60.7498 | 61.8668 | 0.14714 | 0.010905 | 0.0058797 | 0.0030721 | 0.064361 | -0.0011597 | 0.067759 | -60.8688 | 61.8713 | -60.9558 | -60.997 | 61.5051 | -0.045776 | 0.050354 | 0.018311 | 61.8439 | -61.0428 | -0.20599 | 0.004578 | -0.11902 | -0.24719 | 0.045777 | -0.36163 | -0.33874 | -0.29297 | -0.022888 | 0.086976
47.5781 | 122.7814 | -60.7361 | 61.8576 | 0.26158 | 0.0124 | 0.0082295 | 0.0069173 | 0.067352 | 0.0009765 | 0.0684 | -60.8322 | 61.8988 | -60.9558 | -60.9695 | 61.5509 | 0 | 0.009155 | 0.054932 | 61.8347 | -61.0428 | -0.21973 | 0.041199 | -0.09613 | -0.23346 | 0.073243 | -0.3067 | -0.28381 | -0.3067 | -0.022888 | 0.1236
48.5781 | 122.7997 | -60.7361 | 61.8713 | 0.20054 | 0.01005 | 0.0060933 | 0.0011495 | 0.069061 | -0.0018005 | 0.067973 | -60.8322 | 61.9034 | -60.965 | -60.9741 | 61.5417 | 0 | 0.036621 | 0.07782 | 61.8439 | -61.0245 | -0.22888 | 0.032043 | -0.09613 | -0.23804 | 0.050354 | -0.32959 | -0.30212 | -0.28839 | -0.027466 | 0.13275
49.5781 | 122.7859 | -60.7361 | 61.853 | 0.17766 | 0.0087688 | 0.0097249 | 0.0017903 | 0.068848 | -0.0007325 | 0.067118 | -60.8093 | 61.8896 | -60.9787 | -60.9283 | 61.5463 | 0.022888 | 0.027466 | 0.086975 | 61.8393 | -61.0245 | -0.24262 | 0.036621 | -0.073242 | -0.19226 | 0.09613 | -0.3067 | -0.29297 | -0.28839 | -0.013733 | 0.16937
50.5781 | 122.9095 | -60.704 | 61.8164 | 0.74986 | 0.010264 | 0.0069477 | -0.00013233 | 0.068207 | -9.1495e-05 | 0.068827 | -60.8047 | 61.8073 | -60.9741 | -60.9055 | 61.6058 | 0.032043 | -0.16022 | 0.11902 | 61.8073 | -60.9787 | -0.27008 | -0.009155 | -0.10071 | -0.20142 | 0.073242 | -0.21057 | -0.20142 | -0.27466 | -0.009155 | 0.16937
51.5781 | 122.8363 | -60.7452 | 61.8805 | 0.15477 | 0.011546 | 0.0052387 | 0.0041403 | 0.067139 | -0.0003051 | 0.067546 | -60.791 | 61.8805 | -60.9421 | -60.9192 | 61.5875 | 0.07782 | 0.045776 | 0.15106 | 61.8439 | -61.0016 | -0.19684 | 0 | -0.045777 | -0.17395 | 0.082398 | -0.29297 | -0.25635 | -0.25635 | -0.036621 | 0.15106
52.5781 | 122.8226 | -60.7178 | 61.853 | 0.14714 | 0.0087688 | 0.0063069 | 0.0043539 | 0.065857 | -0.0003051 | 0.070323 | -60.7956 | 61.8896 | -60.9695 | -60.9146 | 61.5829 | 0.068665 | 0.018311 | 0.14191 | 61.8347 | -61.0199 | -0.25177 | 0.036621 | -0.07782 | -0.19684 | 0.10529 | -0.27008 | -0.25177 | -0.30212 | -0.01831 | 0.17395
53.5781 | 122.8546 | -60.7224 | 61.8713 | 0.10899 | 0.0087688 | 0.0086567 | 0.0022177 | 0.067566 | 0.0003357 | 0.065623 | -60.791 | 61.8851 | -60.9512 | -60.91 | 61.5875 | 0.064087 | 0.027466 | 0.16479 | 61.8622 | -61.0245 | -0.22888 | 0.013733 | -0.068665 | -0.18768 | 0.11444 | -0.28381 | -0.27466 | -0.30212 | -0.009155 | 0.16022
54.5781 | 122.7905 | -60.759 | 61.8713 | 0.14714 | 0.0098368 | 0.0075887 | 0.0034993 | 0.069061 | 0.0003357 | 0.068614 | -60.7819 | 61.9034 | -60.9512 | -60.9329 | 61.5555 | 0.041199 | 0.036621 | 0.11444 | 61.8713 | -61.0062 | -0.19226 | 0.032043 | -0.022888 | -0.17395 | 0.073243 | -0.31586 | -0.31586 | -0.24719 | 0 | 0.16937
55.5781 | 122.8638 | -60.7407 | 61.8347 | 0.1624 | 0.0049236 | 0.0043843 | -0.0041911 | 0.065002 | -0.0013733 | 0.069255 | -60.8597 | 61.7569 | -60.9604 | -60.9604 | 61.5829 | 0.045776 | -0.091553 | 0.11444 | 61.8164 | -60.9741 | -0.21973 | -0.07782 | -0.11902 | -0.21973 | 0.013733 | -0.25177 | -0.23346 | -0.23346 | -0.018311 | 0.10071
56.5781 | 122.8226 | -60.7315 | 61.8393 | 0.15477 | 0.0096232 | 0.010579 | 0.0052083 | 0.063293 | -0.0005189 | 0.067118 | -60.7864 | 61.8805 | -60.9604 | -60.9238 | 61.5692 | 0.064087 | 0.018311 | 0.13733 | 61.821 | -61.0291 | -0.22888 | 0.041199 | -0.054932 | -0.19226 | 0.10529 | -0.27008 | -0.25177 | -0.29755 | -0.01831 | 0.17395
57.5781 | 122.8317 | -60.7269 | 61.8713 | 0.13951 | 0.012187 | 0.0084431 | 0.0022177 | 0.066711 | -0.0005189 | 0.067973 | -60.791 | 61.8713 | -60.965 | -60.9329 | 61.5829 | 0.068665 | 0.027466 | 0.14648 | 61.8713 | -61.0245 | -0.23804 | 0 | -0.064087 | -0.20599 | 0.091553 | -0.28839 | -0.28839 | -0.29755 | 0 | 0.17395
58.5781 | 122.8271 | -60.7224 | 61.8805 | -0.72261 | 0.007487 | 0.0065205 | 0.0028585 | 0.06842 | -0.0018005 | 0.067332 | -60.759 | 61.908 | -60.9375 | -60.9146 | 61.5829 | 0.073242 | 0.09613 | 0.1831 | 61.8759 | -61.0016 | -0.21515 | 0.027466 | -0.036621 | -0.19226 | 0.086975 | -0.29755 | -0.29297 | -0.27924 | -0.004577 | 0.17853
59.5781 | 122.8134 | -60.7407 | 61.8622 | 0.047956 | 0.010264 | 0.0050251 | 0.0013631 | 0.068634 | -0.0007325 | 0.069896 | -60.7727 | 61.8896 | -60.9604 | -60.91 | 61.615 | 0.068665 | 0.054932 | 0.14648 | 61.8713 | -61.0245 | -0.21973 | 0.027465 | -0.032043 | -0.16937 | 0.11444 | -0.24719 | -0.25635 | -0.28381 | 0.009155 | 0.18768
60.5781 | 122.8363 | -60.7681 | 61.8668 | 0.13951 | 0.0124 | 0.0075887 | 0.0049947 | 0.068207 | -0.0007325 | 0.069255 | -60.791 | 61.908 | -60.9695 | -60.9375 | 61.5921 | 0.045776 | 0.027466 | 0.1236 | 61.8622 | -61.0153 | -0.20142 | 0.041199 | -0.022889 | -0.16937 | 0.07782 | -0.27466 | -0.27008 | -0.24719 | -0.004577 | 0.17853
61.5781 | 122.818 | -60.7498 | 61.8393 | 0.13188 | 0.009196 | 0.0092977 | 0.0041403 | 0.066711 | -9.1495e-05 | 0.069682 | -60.7956 | 61.8668 | -60.9558 | -60.9329 | 61.5875 | 0.050354 | 0.027466 | 0.12817 | 61.853 | -61.0199 | -0.20599 | 0.027466 | -0.045776 | -0.1831 | 0.086975 | -0.25177 | -0.2655 | -0.27008 | 0.013733 | 0.16022
62.5781 | 122.8409 | -60.7315 | 61.8668 | 0.11662 | 0.0081278 | 0.0078023 | 0.0041403 | 0.069916 | -9.1495e-05 | 0.068827 | -60.7956 | 61.908 | -60.9695 | -60.9192 | 61.5921 | 0.054932 | 0.022888 | 0.13733 | 61.8622 | -61.0153 | -0.23804 | 0.041199 | -0.064087 | -0.18768 | 0.096131 | -0.27466 | -0.27008 | -0.28381 | -0.004577 | 0.17395
63.5781 | 122.8271 | -60.7178 | 61.8759 | 0.086103 | 0.011973 | 0.0048115 | 0.0039267 | 0.067779 | -0.0007325 | 0.0684 | -60.7773 | 61.8713 | -60.965 | -60.9238 | 61.5921 | 0.068665 | 0.032043 | 0.14648 | 61.8484 | -61.0245 | -0.24719 | -0.004578 | -0.05951 | -0.20599 | 0.10071 | -0.28381 | -0.25635 | -0.3067 | -0.027466 | 0.18768
64.5781 | 122.8134 | -60.7269 | 61.853 | -0.035967 | 0.009196 | 0.010579 | 0.0045675 | 0.067993 | -9.1495e-05 | 0.068187 | -60.7956 | 61.8942 | -60.9558 | -60.9283 | 61.5921 | 0.064087 | 0.032043 | 0.14648 | 61.8622 | -61.0199 | -0.22888 | 0.041199 | -0.068664 | -0.20142 | 0.091552 | -0.26093 | -0.27008 | -0.29297 | 0.009156 | 0.16022
65.5781 | 122.8455 | -60.7315 | 61.8896 | 0.025068 | 0.0081278 | 0.0043843 | 0.00093587 | 0.06842 | -0.0011597 | 0.066478 | -60.8185 | 61.8942 | -60.9695 | -60.9192 | 61.5829 | 0.091553 | 0.091553 | 0.16022 | 61.8896 | -60.997 | -0.23804 | 0.004578 | -0.086975 | -0.18768 | 0.07782 | -0.3067 | -0.3067 | -0.2655 | 0 | 0.15106
66.5781 | 122.8088 | -60.7407 | 61.8622 | -0.028338 | 0.0081278 | 0.0065205 | 0.0026449 | 0.067139 | -0.0009461 | 0.068827 | -60.8414 | 61.8942 | -60.965 | -60.9329 | 61.5784 | 0.068665 | 0.1236 | 0.13275 | 61.8713 | -61.0153 | -0.2243 | 0.032043 | -0.10071 | -0.19226 | 0.082398 | -0.28381 | -0.29297 | -0.27466 | 0.009155 | 0.1236
67.5781 | 122.8409 | -60.7361 | 61.8805 | 0.13188 | 0.0098368 | 0.0071615 | 0.0011495 | 0.067566 | 0.0022583 | 0.069041 | -60.7681 | 61.853 | -60.9467 | -60.91 | 61.5646 | 0.059509 | 0.032043 | 0.14191 | 61.8439 | -61.0291 | -0.21057 | -0.027466 | -0.032043 | -0.17395 | 0.11902 | -0.31586 | -0.27924 | -0.29297 | -0.036621 | 0.17853
68.5781 | 122.7951 | -60.7498 | 61.8393 | 0.13188 | 0.0096232 | 0.010793 | 0.0034993 | 0.067993 | -0.0013733 | 0.067759 | -60.7864 | 61.8942 | -60.965 | -60.9238 | 61.615 | 0.086975 | -0.041199 | 0.15564 | 61.8256 | -61.0107 | -0.21515 | 0.054932 | -0.036621 | -0.17395 | 0.086975 | -0.2243 | -0.21057 | -0.26093 | -0.013732 | 0.17853
69.5781 | 122.8363 | -60.7544 | 61.8668 | 0.11662 | 0.011119 | 0.0078023 | 0.0030721 | 0.067993 | -0.0020141 | 0.0684 | -60.7727 | 61.8805 | -60.9421 | -60.9146 | 61.5784 | 0.068665 | 0.041199 | 0.16479 | 61.8576 | -61.0245 | -0.18768 | 0.013733 | -0.01831 | -0.16022 | 0.10986 | -0.28839 | -0.27924 | -0.27008 | -0.009155 | 0.16937
70.5781 | 122.8226 | -60.7452 | 61.8805 | 0.070845 | 0.0096232 | 0.0078023 | 0.0041403 | 0.067566 | -0.0011597 | 0.067546 | -60.7864 | 61.8668 | -60.9512 | -60.9283 | 61.5921 | 0.082397 | 0.041199 | 0.14191 | 61.8622 | -61.0062 | -0.20599 | -0.013733 | -0.041199 | -0.18311 | 0.07782 | -0.28839 | -0.27008 | -0.26093 | -0.01831 | 0.1648
71.5781 | 122.8409 | -60.7407 | 61.8668 | 0.10136 | 0.0077006 | 0.0069477 | 0.0034993 | 0.065002 | -0.0043641 | 0.069468 | -60.7956 | 61.8988 | -60.965 | -60.91 | 61.5875 | 0.073242 | 0.059509 | 0.16022 | 61.8484 | -61.0519 | -0.2243 | 0.032044 | -0.054931 | -0.16937 | 0.14191 | -0.27924 | -0.26093 | -0.31128 | -0.01831 | 0.16937
72.5781 | 122.8363 | -60.7452 | 61.8942 | 0.31499 | 0.0089824 | 0.0052387 | 0.0024313 | 0.065216 | -0.0005189 | 0.067546 | -60.8276 | 61.9034 | -60.9695 | -60.9512 | 61.5601 | 0.068665 | 0.11902 | 0.14648 | 61.8988 | -60.997 | -0.2243 | 0.009155 | -0.082398 | -0.20599 | 0.045776 | -0.33417 | -0.33874 | -0.25177 | 0.004578 | 0.14191
73.5781 | 122.8043 | -60.7315 | 61.8439 | 0.055586 | 0.010905 | 0.0097249 | 0.0034993 | 0.067566 | -0.0015869 | 0.068187 | -60.791 | 61.8896 | -60.9558 | -60.9055 | 61.5829 | 0.07782 | 0.068665 | 0.16937 | 61.8851 | -61.0107 | -0.2243 | 0.045776 | -0.05951 | -0.17395 | 0.10529 | -0.26093 | -0.30212 | -0.27924 | 0.041199 | 0.16479
74.5781 | 122.8409 | -60.7132 | 61.8668 | 0.12425 | 0.0081278 | 0.0086567 | 0.0043539 | 0.066284 | -0.0005189 | 0.067118 | -60.791 | 61.8942 | -60.965 | -60.9238 | 61.5784 | 0.068665 | 0.022888 | 0.14191 | 61.8622 | -61.0199 | -0.25177 | 0.027466 | -0.07782 | -0.21057 | 0.09613 | -0.28839 | -0.28381 | -0.3067 | -0.004577 | 0.17395
75.5781 | 122.8134 | -60.7407 | 61.8759 | 0.11662 | 0.01005 | 0.015066 | 0.0045675 | 0.067566 | 0.0016175 | 0.0684 | -60.7681 | 61.8759 | -60.9695 | -60.9238 | 61.5692 | 0.068665 | 0.054932 | 0.15106 | 61.8484 | -61.0062 | -0.22888 | 0 | -0.027465 | -0.1831 | 0.082398 | -0.3067 | -0.27924 | -0.2655 | -0.027466 | 0.20142
76.5781 | 122.8409 | -60.7407 | 61.853 | 0.15477 | 0.0096232 | 0.0086567 | 0.0049947 | 0.066711 | 0.0005493 | 0.070536 | -60.8139 | 61.908 | -60.965 | -60.9146 | 61.5875 | 0.059509 | 0.041199 | 0.15106 | 61.8301 | -61.0291 | -0.2243 | 0.054932 | -0.073242 | -0.17395 | 0.11444 | -0.2655 | -0.24262 | -0.28839 | -0.022888 | 0.15106
77.5781 | 122.818 | -60.7544 | 61.8484 | 0.17003 | 0.011759 | 0.0075887 | 0.0015767 | 0.067139 | -0.0005189 | 0.070109 | -60.7727 | 61.8805 | -60.965 | -60.9146 | 61.5738 | 0.068665 | 0.032043 | 0.16022 | 61.8576 | -61.0062 | -0.21057 | 0.032043 | -0.01831 | -0.16022 | 0.091553 | -0.27466 | -0.28381 | -0.25177 | 0.009155 | 0.19226
78.5781 | 122.8088 | -60.6812 | 61.8713 | 0.093733 | 0.011332 | 0.011861 | 0.0028585 | 0.067352 | -0.0003051 | 0.071391 | -60.8002 | 61.8988 | -60.9787 | -60.91 | 61.5875 | 0.086975 | 0.054932 | 0.16022 | 61.8805 | -61.0062 | -0.29755 | 0.027466 | -0.11902 | -0.22888 | 0.096131 | -0.28381 | -0.29297 | -0.32501 | 0.009155 | 0.17853
79.5781 | 122.8088 | -60.7269 | 61.8759 | -0.28011 | 0.009196 | 0.010793 | 0.0015767 | 0.067352 | -0.0007325 | 0.069041 | -60.8963 | 61.8988 | -60.9741 | -60.9375 | 61.5601 | 0.064087 | 0.1236 | 0.14191 | 61.8851 | -61.0107 | -0.24719 | 0.022888 | -0.16937 | -0.21057 | 0.073242 | -0.31586 | -0.32501 | -0.28381 | 0.009155 | 0.07782
80.5781 | 122.818 | -60.7269 | 61.8668 | 0.025068 | 0.0094096 | 0.0069477 | 0.0024313 | 0.06842 | -0.0007325 | 0.067546 | -60.7864 | 61.9034 | -60.9375 | -60.9283 | 61.6058 | 0.082397 | 0.059509 | 0.15564 | 61.8622 | -61.0153 | -0.21057 | 0.036621 | -0.059509 | -0.20142 | 0.086975 | -0.26093 | -0.25635 | -0.28839 | -0.004577 | 0.15106
81.5781 | 122.8088 | -60.7498 | 61.8622 | 0.10136 | 0.0089824 | 0.011648 | 0.0022177 | 0.066284 | -0.0030823 | 0.0684 | -60.7956 | 61.8713 | -60.9283 | -60.9238 | 61.5784 | 0.073242 | 0.022888 | 0.14191 | 61.853 | -61.0062 | -0.17853 | 0.009155 | -0.045776 | -0.17395 | 0.082398 | -0.28381 | -0.27466 | -0.25635 | -0.009156 | 0.13275
82.5781 | 122.8088 | -60.7269 | 61.8576 | 0.15477 | 0.010478 | 0.0080159 | 0.0045675 | 0.066498 | -0.0015869 | 0.068187 | -60.7819 | 61.8805 | -60.965 | -60.9146 | 61.5738 | 0.054932 | 0.027466 | 0.15106 | 61.8713 | -61.0199 | -0.23804 | 0.022888 | -0.054931 | -0.18768 | 0.10529 | -0.28381 | -0.29755 | -0.29297 | 0.013733 | 0.18311
83.5781 | 122.8409 | -60.7361 | 61.853 | 0.13951 | 0.0094096 | 0.0058797 | 0.0026449 | 0.069916 | 0.0007629 | 0.068827 | -60.7819 | 61.8942 | -60.9787 | -60.9238 | 61.5875 | 0.054932 | 0.032043 | 0.14191 | 61.8668 | -61.0336 | -0.24262 | 0.041199 | -0.045776 | -0.18768 | 0.10986 | -0.2655 | -0.27924 | -0.29755 | 0.013733 | 0.19684
84.5781 | 122.818 | -60.7452 | 61.8484 | 0.086103 | 0.010264 | 0.0063069 | 0.0037129 | 0.06842 | -0.0005189 | 0.067973 | -60.7956 | 61.8942 | -60.9283 | -60.9055 | 61.5921 | 0.082397 | 0.036621 | 0.14191 | 61.8805 | -61.0199 | -0.18311 | 0.045776 | -0.050354 | -0.16022 | 0.11444 | -0.25635 | -0.28839 | -0.27466 | 0.032043 | 0.13275
85.5781 | 122.8455 | -60.7132 | 61.8805 | 0.063215 | 0.0124 | 0.0075887 | 0.0028585 | 0.06842 | 0.0001221 | 0.067973 | -60.7864 | 61.8851 | -60.9558 | -60.9238 | 61.5921 | 0.07782 | 0.036621 | 0.14191 | 61.8622 | -61.0107 | -0.24261 | 0.004578 | -0.073242 | -0.21057 | 0.086975 | -0.28839 | -0.27008 | -0.29755 | -0.01831 | 0.16937
86.5781 | 122.8088 | -60.7452 | 61.8805 | 0.13951 | 0.009196 | 0.0063069 | 0.00093587 | 0.066284 | -0.0005189 | 0.068614 | -60.8231 | 61.8713 | -60.9558 | -60.9329 | 61.5829 | 0.073242 | 0.1236 | 0.14648 | 61.8942 | -61.0245 | -0.21057 | -0.009155 | -0.07782 | -0.18768 | 0.091553 | -0.29755 | -0.31128 | -0.27924 | 0.013733 | 0.13275
87.5781 | 122.8317 | -60.7269 | 61.8713 | 0.063215 | 0.0079142 | 0.0067341 | 0.0013631 | 0.066711 | -0.0015869 | 0.069468 | -60.7727 | 61.8896 | -60.9558 | -60.9192 | 61.5967 | 0.082397 | 0.054932 | 0.16479 | 61.8805 | -61.0107 | -0.22888 | 0.01831 | -0.045776 | -0.19226 | 0.091553 | -0.27466 | -0.28381 | -0.28381 | 0.009155 | 0.18311
88.5781 | 122.85 | -60.7132 | 61.8805 | 0.047956 | 0.011119 | 0.0048115 | 0.0024313 | 0.068207 | 0.0014039 | 0.067759 | -60.7956 | 61.8896 | -60.965 | -60.9146 | 61.5967 | 0.086975 | 0.059509 | 0.16937 | 61.853 | -61.0245 | -0.25177 | 0.009155 | -0.082397 | -0.20142 | 0.10986 | -0.28381 | -0.25635 | -0.31128 | -0.027466 | 0.16937
89.5781 | 122.8043 | -60.7224 | 61.853 | -0.0054494 | 0.0083416 | 0.0086567 | 0.0030721 | 0.067352 | -0.0020141 | 0.068187 | -60.791 | 61.8851 | -60.9512 | -60.9192 | 61.615 | 0.10529 | 0.054932 | 0.16937 | 61.8805 | -61.0291 | -0.22888 | 0.032044 | -0.068665 | -0.19684 | 0.10986 | -0.23804 | -0.2655 | -0.3067 | 0.027466 | 0.16022
90.5781 | 122.8409 | -60.7086 | 61.853 | 0.032698 | 0.0089824 | 0.0031025 | 0.0039267 | 0.063721 | -0.0020141 | 0.066905 | -60.8002 | 61.8622 | -60.9879 | -60.9329 | 61.6013 | 0.082397 | 0.086975 | 0.19226 | 61.853 | -60.997 | -0.27924 | 0.009156 | -0.091553 | -0.2243 | 0.064087 | -0.25177 | -0.25177 | -0.28839 | 0 | 0.18768
91.5781 | 122.7951 | -60.7452 | 61.8668 | 0.0098091 | 0.0124 | 0.0071615 | -0.00077313 | 0.065857 | -0.0003051 | 0.0684 | -60.7956 | 61.8851 | -60.9558 | -60.9146 | 61.5967 | 0.07782 | 0.082397 | 0.16479 | 61.908 | -61.0107 | -0.21057 | 0.018311 | -0.050354 | -0.16937 | 0.09613 | -0.27008 | -0.31128 | -0.2655 | 0.041199 | 0.16022
92.5781 | 122.85 | -60.7315 | 61.8439 | 0.078474 | 0.010478 | 0.0075887 | 0.0032857 | 0.067566 | 0.0005493 | 0.066264 | -60.7864 | 61.8805 | -60.9558 | -60.9192 | 61.5875 | 0.07782 | 0.036621 | 0.16022 | 61.8576 | -61.0153 | -0.2243 | 0.036621 | -0.054932 | -0.18768 | 0.096131 | -0.25635 | -0.27008 | -0.28381 | 0.013733 | 0.16937
93.5781 | 122.8088 | -60.7269 | 61.8713 | 0.10136 | 0.0089824 | 0.012502 | 0.0037129 | 0.066284 | -0.0005189 | 0.068187 | -60.8002 | 61.908 | -60.9604 | -60.9283 | 61.5875 | 0.068665 | 0.045776 | 0.14191 | 61.8484 | -60.997 | -0.23346 | 0.036621 | -0.073242 | -0.20142 | 0.068664 | -0.28381 | -0.26093 | -0.27008 | -0.022888 | 0.16022
94.5781 | 122.8088 | -60.7315 | 61.8805 | 0.13188 | 0.0089824 | 0.0088703 | 0.0022177 | 0.068207 | -0.0022277 | 0.0684 | -60.7864 | 61.8851 | -60.9604 | -60.9238 | 61.5738 | 0.091553 | 0.027466 | 0.14648 | 61.8713 | -61.0199 | -0.22888 | 0.004578 | -0.054932 | -0.19226 | 0.09613 | -0.3067 | -0.29755 | -0.28839 | -0.009155 | 0.17395
95.5781 | 122.8088 | -60.7452 | 61.853 | 0.15477 | 0.0096232 | 0.0090841 | 0.0062765 | 0.066925 | -0.0026551 | 0.0684 | -60.791 | 61.8851 | -60.9741 | -60.9375 | 61.5829 | 0.054932 | 0.022888 | 0.14191 | 61.8484 | -61.0382 | -0.22888 | 0.032044 | -0.045777 | -0.19226 | 0.10071 | -0.27008 | -0.2655 | -0.29297 | -0.004577 | 0.1831
96.5781 | 122.7997 | -60.7407 | 61.8805 | 0.17003 | 0.010478 | 0.013357 | 0.0015767 | 0.066925 | -0.0005189 | 0.068614 | -60.8002 | 61.8896 | -60.965 | -60.9421 | 61.5967 | 0.054932 | 0.009155 | 0.13733 | 61.8805 | -61.0107 | -0.2243 | 0.009155 | -0.059509 | -0.20142 | 0.068664 | -0.28381 | -0.28381 | -0.27008 | 0 | 0.16479
97.5781 | 122.8271 | -60.7407 | 61.8668 | 0.15477 | 0.0094096 | 0.0075887 | 0.0045675 | 0.069061 | -0.0022277 | 0.069468 | -60.7864 | 61.8759 | -60.997 | -60.9375 | 61.5646 | 0.054932 | 0.045776 | 0.11444 | 61.8439 | -61.0336 | -0.25635 | 0.009156 | -0.045776 | -0.19684 | 0.09613 | -0.30212 | -0.27924 | -0.29297 | -0.022888 | 0.21057
98.5781 | 122.8043 | -60.7178 | 61.8805 | 0.10899 | 0.010264 | 0.010579 | 0.0028585 | 0.066925 | 0.0001221 | 0.067118 | -60.8002 | 61.8942 | -60.9787 | -60.9055 | 61.5967 | 0.073242 | 0.027466 | 0.15564 | 61.853 | -61.0153 | -0.26093 | 0.013733 | -0.082398 | -0.18768 | 0.10986 | -0.28381 | -0.25635 | -0.29755 | -0.027466 | 0.17853
99.5781 | 122.8409 | -60.7544 | 61.8851 | 0.040327 | 0.0079142 | 0.0095113 | 0.0030721 | 0.066711 | -0.0007325 | 0.067973 | -60.7956 | 61.8942 | -60.9695 | -60.9055 | 61.5921 | 0.09613 | 0.064087 | 0.16479 | 61.8668 | -61.0016 | -0.21515 | 0.009155 | -0.041198 | -0.15106 | 0.09613 | -0.29297 | -0.27466 | -0.24719 | -0.018311 | 0.17395
100.5781 | 122.7997 | -60.7407 | 61.8439 | 0.15477 | 0.01005 | 0.0080159 | 0.0032857 | 0.067139 | -0.0015869 | 0.068187 | -60.8002 | 61.8713 | -60.9467 | -60.9283 | 61.5784 | 0.1236 | -0.082397 | 0.13275 | 61.8484 | -61.0657 | -0.20599 | 0.027466 | -0.059509 | -0.18768 | 0.13733 | -0.2655 | -0.27008 | -0.32501 | 0.004578 | 0.14648
101.5781 | 122.7997 | -60.7315 | 61.8576 | 0.17003 | 0.0098368 | 0.0084431 | 0.0041403 | 0.067779 | -0.0011597 | 0.067118 | -60.791 | 61.8988 | -60.9421 | -60.9604 | 61.5509 | 0.027466 | 0.041199 | 0.10071 | 61.8622 | -61.0382 | -0.21057 | 0.041199 | -0.05951 | -0.22888 | 0.07782 | -0.3067 | -0.31128 | -0.3067 | 0.004578 | 0.15106
102.5781 | 122.8134 | -60.7407 | 61.8439 | 0.12425 | 0.01005 | 0.0082295 | 0.0045675 | 0.067779 | -0.0047913 | 0.069682 | -60.791 | 61.9034 | -60.9787 | -60.9238 | 61.5601 | 0.032043 | 0.013733 | 0.10529 | 61.8576 | -61.0153 | -0.23804 | 0.059509 | -0.050354 | -0.1831 | 0.091553 | -0.28381 | -0.29755 | -0.27466 | 0.013733 | 0.18768
103.5781 | 122.7997 | -60.7544 | 61.853 | 0.15477 | 0.0098368 | 0.0065205 | 0.0032857 | 0.068848 | -0.0030823 | 0.067546 | -60.8002 | 61.8713 | -60.9787 | -60.9421 | 61.5738 | 0.050354 | 0.018311 | 0.1236 | 61.8576 | -61.0519 | -0.2243 | 0.018311 | -0.045776 | -0.18768 | 0.10986 | -0.27923 | -0.28381 | -0.29755 | 0.004578 | 0.17853
104.5781 | 122.8226 | -60.7452 | 61.8439 | 0.063215 | 0.011332 | 0.0056661 | 0.0032857 | 0.067993 | -0.0005189 | 0.067546 | -60.7956 | 61.8988 | -60.9833 | -60.9512 | 61.5692 | 0.059509 | 0.027466 | 0.1236 | 61.8622 | -61.0245 | -0.23804 | 0.054932 | -0.050354 | -0.20599 | 0.073242 | -0.27466 | -0.29297 | -0.27924 | 0.018311 | 0.18768
105.5781 | 122.7951 | -60.7407 | 61.8393 | 0.070845 | 0.010905 | 0.0084431 | 0.0041403 | 0.067566 | -0.0015869 | 0.067759 | -60.7864 | 61.8988 | -60.9695 | -60.9375 | 61.5555 | 0.059509 | 0.036621 | 0.13733 | 61.8622 | -61.0336 | -0.22888 | 0.05951 | -0.045776 | -0.19684 | 0.09613 | -0.28381 | -0.3067 | -0.29297 | 0.022889 | 0.18311
106.5781 | 122.8409 | -60.7269 | 61.8713 | 0.0098091 | 0.007487 | 0.0084431 | 0.0026449 | 0.067352 | -0.0003051 | 0.0684 | -60.7819 | 61.8851 | -60.9604 | -60.9192 | 61.5967 | 0.086975 | 0.041199 | 0.17853 | 61.8622 | -61.0016 | -0.23346 | 0.013733 | -0.054931 | -0.19226 | 0.082398 | -0.27466 | -0.2655 | -0.27466 | -0.009155 | 0.17853
107.5781 | 122.7859 | -60.7361 | 61.8713 | -0.33351 | 0.011119 | 0.0086567 | 0.0039267 | 0.067352 | -0.0013733 | 0.067973 | -60.7773 | 61.8805 | -60.9787 | -60.91 | 61.5646 | 0.064087 | 0.027466 | 0.15564 | 61.8759 | -61.0291 | -0.24262 | 0.009155 | -0.041199 | -0.17395 | 0.11902 | -0.3067 | -0.31128 | -0.29297 | 0.004578 | 0.20142
108.5781 | 122.8043 | -60.7727 | 61.8805 | 0.22343 | 0.0094096 | 0.0099385 | 0.0058493 | 0.069488 | -9.1495e-05 | 0.069255 | -60.8185 | 61.8713 | -60.965 | -60.9787 | 61.5234 | 0.009155 | 0.022888 | 0.082397 | 61.8713 | -61.0245 | -0.19226 | -0.009155 | -0.045776 | -0.20599 | 0.045776 | -0.35706 | -0.3479 | -0.25177 | -0.009155 | 0.14648
109.5781 | 122.7814 | -60.7407 | 61.8439 | 0.17766 | 0.010905 | 0.0084431 | 0.0039267 | 0.067352 | -9.1495e-05 | 0.068827 | -60.8231 | 61.8484 | -60.9741 | -60.9604 | 61.5326 | 0.018311 | 0.032043 | 0.082397 | 61.8301 | -61.0611 | -0.23346 | 0.004578 | -0.082397 | -0.21973 | 0.10071 | -0.31128 | -0.29755 | -0.32043 | -0.013733 | 0.15106
110.5781 | 122.7905 | -60.7315 | 61.8759 | 0.20817 | 0.011546 | 0.012502 | 0.0017903 | 0.06543 | -0.0018005 | 0.0684 | -60.791 | 61.8805 | -60.965 | -60.965 | 61.5509 | 0.009155 | 0.032043 | 0.09613 | 61.8439 | -61.0428 | -0.23346 | 0.004577 | -0.05951 | -0.23346 | 0.07782 | -0.32501 | -0.29297 | -0.31128 | -0.032044 | 0.17395
111.5781 | 122.8134 | -60.7498 | 61.8439 | 0.13188 | 0.011546 | 0.0099385 | 0.0026449 | 0.06842 | -0.0026551 | 0.067118 | -60.8185 | 61.8851 | -60.965 | -60.9467 | 61.5372 | 0.027466 | 0.036621 | 0.09613 | 61.8484 | -61.0428 | -0.21515 | 0.041199 | -0.068664 | -0.19684 | 0.096131 | -0.3067 | -0.31128 | -0.29297 | 0.004578 | 0.14648
112.5781 | 122.7905 | -60.7636 | 61.8759 | 0.12425 | 0.010905 | 0.0080159 | 0.0060629 | 0.06607 | -0.0011597 | 0.071177 | -60.7819 | 61.8576 | -60.997 | -60.9375 | 61.5692 | 0.032043 | 0.032043 | 0.10529 | 61.8759 | -61.0199 | -0.23346 | -0.018311 | -0.01831 | -0.17395 | 0.082397 | -0.3067 | -0.3067 | -0.25635 | 0 | 0.21515
113.5781 | 122.905 | -60.7498 | 61.8668 | 0.10899 | 0.0079142 | 0.0060933 | 0.0039267 | 0.066925 | 0.0005493 | 0.068614 | -60.7819 | 61.8988 | -60.9512 | -60.9192 | 61.5692 | 0.068665 | 0.045776 | 0.16479 | 61.8439 | -61.0153 | -0.20142 | 0.032044 | -0.032043 | -0.16937 | 0.096131 | -0.29755 | -0.27466 | -0.2655 | -0.022888 | 0.16937
114.5781 | 122.7905 | -60.7132 | 61.8668 | 0.093733 | 0.0096232 | 0.0065205 | 0.0028585 | 0.06842 | 0.0007629 | 0.070536 | -60.7956 | 61.8759 | -60.9604 | -60.9329 | 61.5692 | 0.045776 | 0.032043 | 0.12817 | 61.8713 | -61.0153 | -0.24719 | 0.009156 | -0.082397 | -0.21973 | 0.082398 | -0.29755 | -0.30212 | -0.30212 | 0.004578 | 0.1648
115.5781 | 122.7768 | -60.7498 | 61.8484 | 0.24632 | 0.012187 | 0.012075 | 0.0047811 | 0.067779 | -0.0022277 | 0.068187 | -60.8185 | 61.8942 | -60.9924 | -60.9604 | 61.5143 | 0 | 0.022888 | 0.073242 | 61.8576 | -61.0565 | -0.24262 | 0.045776 | -0.068664 | -0.21057 | 0.096131 | -0.33417 | -0.34332 | -0.3067 | 0.009155 | 0.17395
116.5781 | 122.7859 | -60.7407 | 61.8668 | 0.23869 | 0.0096232 | 0.0082295 | 0.0045675 | 0.067352 | -0.0005189 | 0.068187 | -60.8002 | 61.9034 | -60.965 | -60.9741 | 61.5372 | -0.013733 | 0.027466 | 0.07782 | 61.8393 | -61.0474 | -0.2243 | 0.036621 | -0.059509 | -0.23346 | 0.073242 | -0.32959 | -0.30212 | -0.3067 | -0.027466 | 0.16479
117.5781 | 122.7631 | -60.7773 | 61.8576 | 0.27684 | 0.010478 | 0.0071615 | 0.0045675 | 0.069061 | -0.0022277 | 0.069468 | -60.8551 | 61.8805 | -60.9833 | -61.0062 | 61.5005 | -0.045776 | 0.050354 | 0.032043 | 61.8576 | -61.0382 | -0.20599 | 0.022888 | -0.07782 | -0.22888 | 0.032043 | -0.35706 | -0.35706 | -0.26093 | 0 | 0.12817
118.5781 | 122.8043 | -60.759 | 61.8439 | 0.15477 | 0.0085552 | 0.0071615 | 0.0030721 | 0.066925 | -0.0022277 | 0.068614 | -60.7864 | 61.8851 | -60.9787 | -60.9329 | 61.5463 | 0.045776 | 0.018311 | 0.11444 | 61.8805 | -61.0291 | -0.21973 | 0.041199 | -0.027466 | -0.17395 | 0.096131 | -0.29755 | -0.33417 | -0.27008 | 0.036621 | 0.19226
119.5781 | 122.7768 | -60.7407 | 61.8668 | 0.17003 | 0.0085552 | 0.0078023 | 0.0047811 | 0.068848 | -0.0007325 | 0.068614 | -60.7956 | 61.8805 | -60.9604 | -60.9467 | 61.5555 | 0.036621 | 0.027466 | 0.13275 | 61.8851 | -61.0291 | -0.21973 | 0.013733 | -0.054931 | -0.20599 | 0.082398 | -0.31128 | -0.32959 | -0.28839 | 0.018311 | 0.1648
120.5781 | 122.8363 | -60.7407 | 61.8713 | 0.070845 | 0.0077006 | 0.0011799 | 0.0034993 | 0.067352 | -0.0007325 | 0.069896 | -60.7819 | 61.8942 | -60.9741 | -60.9283 | 61.5921 | 0.07782 | 0.054932 | 0.15564 | 61.8668 | -61.0382 | -0.23346 | 0.022888 | -0.041198 | -0.18768 | 0.10986 | -0.27924 | -0.27466 | -0.29755 | -0.004578 | 0.19226
121.5781 | 122.7493 | -60.7681 | 61.853 | 0.23106 | 0.0081278 | 0.012502 | 0.0034993 | 0.069702 | -0.0015869 | 0.067973 | -60.8139 | 61.8622 | -60.9879 | -60.9787 | 61.5234 | -0.013733 | 0.032043 | 0.07782 | 61.8851 | -61.0245 | -0.21973 | 0.009156 | -0.045777 | -0.21057 | 0.045776 | -0.32959 | -0.36163 | -0.25635 | 0.032044 | 0.17395
122.5781 | 122.7905 | -60.7452 | 61.8439 | 0.19291 | 0.0087688 | 0.0086567 | 0.0060629 | 0.068848 | -0.0018005 | 0.068827 | -60.8093 | 61.8988 | -60.965 | -60.9558 | 61.5417 | 0.013733 | 0.027466 | 0.07782 | 61.8622 | -61.0245 | -0.21973 | 0.054932 | -0.064087 | -0.21057 | 0.068664 | -0.30212 | -0.32044 | -0.27924 | 0.018311 | 0.15564
123.5781 | 122.7997 | -60.7544 | 61.8439 | 0.17003 | 0.011119 | 0.0080159 | 0.0047811 | 0.06842 | -0.0007325 | 0.070109 | -60.8002 | 61.8805 | -60.9924 | -60.9604 | 61.5463 | 0.022888 | 0.018311 | 0.10529 | 61.8576 | -61.0336 | -0.23804 | 0.036621 | -0.045776 | -0.20599 | 0.073242 | -0.29755 | -0.31128 | -0.27923 | 0.013733 | 0.19226
124.5781 | 122.7493 | -60.7407 | 61.8713 | 0.19291 | 0.01005 | 0.0097249 | 0.0047811 | 0.069275 | -0.0005189 | 0.067118 | -60.7864 | 61.8851 | -60.9695 | -60.9467 | 61.5738 | 0.045776 | 0.032043 | 0.11902 | 61.8668 | -61.0382 | -0.22888 | 0.013733 | -0.045776 | -0.20599 | 0.091553 | -0.29755 | -0.29297 | -0.29755 | -0.004578 | 0.18311
125.5781 | 122.8226 | -60.7544 | 61.8668 | -0.020708 | 0.010264 | 0.0080159 | 0.0028585 | 0.06842 | -0.0003051 | 0.069896 | -60.7773 | 61.8942 | -60.9741 | -60.9375 | 61.5738 | 0.041199 | 0.041199 | 0.13275 | 61.8576 | -61.0428 | -0.21973 | 0.027466 | -0.022888 | -0.1831 | 0.10529 | -0.29297 | -0.28381 | -0.28839 | -0.009155 | 0.19684
126.5781 | 122.8043 | -60.7224 | 61.8622 | 0.36076 | 0.010691 | 0.011861 | 0.0058493 | 0.067352 | -0.0009461 | 0.070323 | -60.7819 | 61.8439 | -60.9879 | -60.9238 | 61.5829 | 0.073242 | 0.027466 | 0.15106 | 61.8805 | -61.0245 | -0.2655 | -0.018311 | -0.059509 | -0.20142 | 0.10071 | -0.27924 | -0.29755 | -0.30212 | 0.01831 | 0.20599
127.5781 | 122.8043 | -60.7315 | 61.8713 | 0.063215 | 0.0083416 | 0.0082295 | 0.0034993 | 0.067352 | -0.0020141 | 0.068614 | -60.7773 | 61.9034 | -60.9787 | -60.9238 | 61.5829 | 0.07782 | 0.050354 | 0.16937 | 61.8759 | -61.0245 | -0.24719 | 0.032043 | -0.045777 | -0.19226 | 0.10071 | -0.28839 | -0.29297 | -0.29297 | 0.004578 | 0.20142
128.5781 | 122.8088 | -60.7269 | 61.8668 | 0.1624 | 0.0094096 | 0.0050251 | 0.0041403 | 0.066284 | -0.0003051 | 0.069255 | -60.8002 | 61.9217 | -60.9467 | -61.0245 | 61.6653 | 0.07782 | 0.022888 | 0.15106 | 61.8805 | -61.0245 | -0.21973 | 0.054932 | -0.073242 | -0.29755 | 0 | -0.20142 | -0.21515 | -0.29755 | 0.013733 | 0.14648
129.5781 | 122.7997 | -60.7315 | 61.8484 | 0.1624 | 0.011759 | 0.0058797 | 0.0032857 | 0.070129 | -0.0018005 | 0.067332 | -60.8002 | 61.8896 | -60.965 | -60.9467 | 61.5509 | 0.022888 | 0.027466 | 0.10529 | 61.853 | -61.0565 | -0.23346 | 0.041198 | -0.068665 | -0.21515 | 0.10986 | -0.29755 | -0.30212 | -0.32501 | 0.004577 | 0.16479
130.5781 | 122.8043 | -60.7498 | 61.8851 | 0.18529 | 0.010691 | 0.0082295 | 0.0034993 | 0.067993 | -9.1495e-05 | 0.068827 | -60.8002 | 61.8805 | -60.965 | -60.9375 | 61.5784 | 0.041199 | 0.041199 | 0.11902 | 61.8622 | -61.0428 | -0.21515 | -0.004578 | -0.050354 | -0.18768 | 0.10529 | -0.3067 | -0.28381 | -0.29297 | -0.022888 | 0.16479
131.5781 | 122.8271 | -60.7224 | 61.8073 | 0.32261 | 0.0077006 | 0.0075887 | -0.0033365 | 0.065857 | -0.0005189 | 0.070109 | -60.8688 | 61.7752 | -60.965 | -60.9604 | 61.5646 | 0.036621 | -0.086975 | 0.11444 | 61.821 | -60.9833 | -0.24261 | -0.032043 | -0.14648 | -0.23804 | 0.022888 | -0.24262 | -0.25635 | -0.26092 | 0.013733 | 0.096131
132.5781 | 122.8226 | -60.759 | 61.8668 | 0.27684 | 0.012187 | 0.0088703 | 0.0047811 | 0.065002 | -0.0013733 | 0.068827 | -60.7727 | 61.8759 | -60.9695 | -60.9329 | 61.5509 | 0.045776 | 0.050354 | 0.11444 | 61.8759 | -61.0291 | -0.21057 | 0.009156 | -0.013733 | -0.17395 | 0.096131 | -0.31586 | -0.32501 | -0.27008 | 0.009156 | 0.19684
133.5781 | 122.7768 | -60.7269 | 61.8713 | 0.26158 | 0.0072734 | 0.0088703 | 0.0015767 | 0.065857 | 0.0001221 | 0.067973 | -60.791 | 61.9034 | -60.9695 | -60.9146 | 61.5875 | 0.064087 | 0.027466 | 0.14648 | 61.8622 | -61.0107 | -0.24261 | 0.032043 | -0.064087 | -0.18768 | 0.09613 | -0.28381 | -0.27466 | -0.28381 | -0.009155 | 0.17853
134.5781 | 122.7997 | -60.7269 | 61.8622 | 0.040327 | 0.0081278 | 0.0063069 | 0.0041403 | 0.06607 | -0.0015869 | 0.067973 | -60.759 | 61.8988 | -60.9421 | -60.9055 | 61.6058 | 0.086975 | 0.054932 | 0.15106 | 61.8668 | -61.0062 | -0.21515 | 0.036621 | -0.032043 | -0.17853 | 0.10071 | -0.25635 | -0.26093 | -0.27924 | 0.004577 | 0.18311
135.5781 | 122.8088 | -60.7178 | 61.8759 | 0.11662 | 0.010478 | 0.0092977 | 0.0039267 | 0.068634 | -9.1495e-05 | 0.066905 | -60.7819 | 61.8805 | -60.9695 | -60.9879 | 61.6928 | 0.082397 | -0.004578 | 0.14648 | 61.8759 | -61.0199 | -0.25177 | 0.004577 | -0.064087 | -0.27008 | 0.032043 | -0.18311 | -0.18311 | -0.30212 | 0 | 0.18768
136.5781 | 122.8455 | -60.7224 | 61.8347 | 0.35313 | 0.007487 | 0.0045979 | -0.0044047 | 0.067139 | -0.0009461 | 0.07075 | -60.8231 | 61.734 | -61.0107 | -60.9421 | 61.5921 | 0.036621 | -0.15106 | 0.13733 | 61.8164 | -60.9695 | -0.28839 | -0.10071 | -0.10071 | -0.21973 | 0.027465 | -0.24262 | -0.2243 | -0.24719 | -0.018311 | 0.18768
137.5781 | 122.7997 | -60.7315 | 61.8713 | 0.13951 | 0.0087688 | 0.0078023 | 0.0062765 | 0.068848 | -0.0015869 | 0.0684 | -60.7819 | 61.8988 | -60.9421 | -60.9283 | 61.5601 | 0.045776 | 0.045776 | 0.11444 | 61.8256 | -61.0291 | -0.21057 | 0.027466 | -0.050354 | -0.19684 | 0.10071 | -0.31128 | -0.2655 | -0.29755 | -0.045776 | 0.16022
138.5781 | 122.85 | -60.7178 | 61.8347 | 0.35313 | 0.0068462 | 0.0075887 | -0.0020549 | 0.06543 | 0.0014039 | 0.0684 | -60.8002 | 61.7615 | -60.9695 | -60.9192 | 61.5967 | 0.041199 | -0.17395 | 0.15106 | 61.8118 | -60.9833 | -0.25177 | -0.073242 | -0.082398 | -0.20142 | 0.064087 | -0.23804 | -0.21515 | -0.2655 | -0.022888 | 0.16937
139.5781 | 122.7905 | -60.759 | 61.853 | 0.22343 | 0.0089824 | 0.010366 | 0.0045675 | 0.068207 | 0.0007629 | 0.07075 | -60.8185 | 61.908 | -60.9421 | -60.9741 | 61.5234 | -0.013733 | 0.032043 | 0.059509 | 61.8301 | -61.0336 | -0.18311 | 0.054932 | -0.059509 | -0.21515 | 0.059509 | -0.32959 | -0.3067 | -0.27466 | -0.022888 | 0.1236
140.5781 | 122.818 | -60.7498 | 61.8668 | 1.1847 | 0.009196 | 0.0084431 | 0.0026449 | 0.066498 | -0.0011597 | 0.067546 | -60.7178 | 61.8668 | -60.9741 | -60.9055 | 61.6196 | 0.068665 | 0.018311 | 0.14648 | 61.853 | -61.0428 | -0.2243 | 0 | 0.032044 | -0.15564 | 0.13733 | -0.24719 | -0.23346 | -0.29297 | -0.013733 | 0.25635
141.5781 | 122.8683 | -60.7178 | 61.7889 | 0.41417 | 0.0066326 | 0.0090841 | 0.0011495 | 0.069488 | 0.0005493 | 0.068827 | -60.7773 | 61.8301 | -60.9604 | -60.9009 | 61.6013 | 0.059509 | -0.19684 | 0.1236 | 61.7844 | -60.9879 | -0.24262 | 0.041199 | -0.05951 | -0.18311 | 0.086975 | -0.18768 | -0.18311 | -0.27008 | -0.004577 | 0.18311
142.5781 | 122.8271 | -60.7361 | 61.8668 | 0.1624 | 0.0096232 | 0.0031025 | 0.0043539 | 0.068634 | -0.0015869 | 0.067546 | -60.7819 | 61.8759 | -60.9558 | -60.9879 | 61.4639 | -0.068665 | 0.091553 | 0.14648 | 61.8576 | -61.0336 | -0.21973 | 0.009156 | -0.045776 | -0.25177 | 0.045776 | -0.40283 | -0.39368 | -0.29755 | -0.009155 | 0.17395
143.5781 | 122.7951 | -60.7269 | 61.8484 | 0.1624 | 0.0079142 | 0.0097249 | 0.0054219 | 0.067352 | -0.0015869 | 0.066905 | -60.8093 | 61.8896 | -60.9879 | -60.9375 | 61.5555 | 0.018311 | 0.027466 | 0.10071 | 61.8668 | -61.0336 | -0.26093 | 0.041198 | -0.082397 | -0.21057 | 0.09613 | -0.29297 | -0.31128 | -0.3067 | 0.01831 | 0.17853
144.5781 | 122.8134 | -60.7361 | 61.8576 | 0.17003 | 0.009196 | 0.0080159 | 0.0039267 | 0.067993 | 0.0014039 | 0.068187 | -60.8002 | 61.8713 | -60.9741 | -60.9375 | 61.5829 | 0.041199 | 0.027466 | 0.11444 | 61.853 | -61.0199 | -0.23804 | 0.013733 | -0.064087 | -0.20142 | 0.082397 | -0.27466 | -0.27008 | -0.28381 | -0.004578 | 0.17395
145.5781 | 122.7814 | -60.7452 | 61.8759 | 0.19291 | 0.010264 | 0.0090841 | 0.0047811 | 0.066498 | -0.0007325 | 0.068827 | -60.7956 | 61.8713 | -60.9421 | -60.9192 | 61.5646 | 0.036621 | 0.018311 | 0.12817 | 61.8576 | -61.0382 | -0.19684 | -0.004578 | -0.050354 | -0.17395 | 0.11902 | -0.31128 | -0.29297 | -0.29297 | -0.018311 | 0.14649
146.5781 | 122.8683 | -60.7452 | 61.8347 | 0.36076 | 0.0077006 | 0.0082295 | -0.0054729 | 0.06607 | 0.0011901 | 0.066905 | -60.8505 | 61.821 | -60.9467 | -60.9604 | 61.5967 | 0.036621 | -0.07782 | 0.11902 | 61.8347 | -61.0062 | -0.20142 | -0.013733 | -0.10529 | -0.21515 | 0.045777 | -0.23804 | -0.23804 | -0.26093 | 0 | 0.09613
147.5781 | 122.7997 | -60.7407 | 61.853 | 0.40654 | 0.0066326 | 0.010579 | 0.0060629 | 0.067566 | -0.0009461 | 0.067546 | -60.7727 | 61.8851 | -60.9558 | -60.9146 | 61.5692 | 0.041199 | 0.013733 | 0.11902 | 61.8347 | -61.0107 | -0.21515 | 0.032044 | -0.032043 | -0.17395 | 0.09613 | -0.28381 | -0.2655 | -0.27008 | -0.01831 | 0.18311
148.5781 | 122.7951 | -60.7224 | 61.8713 | 1.3984 | 0.0085552 | 0.0082295 | 0.0045675 | 0.067139 | 0.0014039 | 0.068614 | -60.7681 | 61.853 | -60.9879 | -60.9192 | 61.5875 | 0.073242 | 0.018311 | 0.13275 | 61.8393 | -61.0062 | -0.2655 | -0.018311 | -0.045776 | -0.19684 | 0.086976 | -0.28381 | -0.25177 | -0.28381 | -0.032044 | 0.21973
149.5781 | 122.8271 | -60.7132 | 61.8668 | 0.14714 | 0.009196 | 0.0097249 | 0.0041403 | 0.068848 | 0.0001221 | 0.070536 | -60.6949 | 61.8805 | -60.965 | -60.9238 | 61.6058 | 0.054932 | 0.018311 | 0.14191 | 61.8576 | -61.0245 | -0.25177 | 0.013733 | 0.018311 | -0.21057 | 0.10071 | -0.26093 | -0.25177 | -0.31128 | -0.009155 | 0.27008
150.5781 | 122.7905 | -60.7407 | 61.8668 | 0.22343 | 0.0094096 | 0.012075 | 0.0041403 | 0.068634 | -0.0007325 | 0.068187 | -60.8047 | 61.8896 | -60.9924 | -60.9604 | 61.5509 | 0.013733 | 0.009155 | 0.086975 | 61.8805 | -61.0519 | -0.25177 | 0.022888 | -0.064087 | -0.21973 | 0.091553 | -0.31586 | -0.32959 | -0.31128 | 0.013733 | 0.18768
151.5781 | 122.7951 | -60.7636 | 61.8622 | 0.17766 | 0.010264 | 0.0088703 | 0.0032857 | 0.067352 | -0.0037231 | 0.067118 | -60.7956 | 61.8942 | -60.9695 | -60.9512 | 61.5509 | 0.013733 | 0.013733 | 0.082397 | 61.8439 | -61.0336 | -0.20599 | 0.032043 | -0.032043 | -0.18768 | 0.082397 | -0.31128 | -0.29297 | -0.27008 | -0.018311 | 0.17395
152.5781 | 122.8409 | -60.7361 | 61.8668 | 0.11662 | 0.0089824 | 0.0095113 | 0.0028585 | 0.068634 | -0.0020141 | 0.0684 | -60.8093 | 61.908 | -60.9695 | -60.9192 | 61.5738 | 0.068665 | 0.018311 | 0.041199 | 61.8256 | -61.0291 | -0.23346 | 0.041199 | -0.073242 | -0.18311 | 0.10986 | -0.29297 | -0.25177 | -0.29297 | -0.041198 | 0.16022
153.5781 | 122.8134 | -60.7452 | 61.853 | 0.15477 | 0.0089824 | 0.0078023 | 0.0013631 | 0.067566 | -0.0018005 | 0.067546 | -60.7956 | 61.9034 | -60.9787 | -60.9421 | 61.5692 | 0.045776 | 0.022888 | 0.10071 | 61.853 | -61.0245 | -0.23346 | 0.050354 | -0.050354 | -0.19684 | 0.082397 | -0.28381 | -0.28381 | -0.27924 | 0 | 0.18311
154.5781 | 122.8088 | -60.7452 | 61.8759 | 0.17003 | 0.011119 | 0.0071615 | 0.0045675 | 0.066711 | -0.0003051 | 0.068187 | -60.8185 | 61.9125 | -61.0016 | -60.9421 | 61.5738 | 0.045776 | 0.022888 | 0.09613 | 61.853 | -61.0382 | -0.25635 | 0.036621 | -0.073242 | -0.19684 | 0.09613 | -0.30212 | -0.27923 | -0.29297 | -0.022889 | 0.18311
155.5781 | 122.8088 | -60.7269 | 61.8576 | 0.093733 | 0.010905 | 0.0095113 | 0.0026449 | 0.066498 | -9.1495e-05 | 0.0684 | -60.7864 | 61.8988 | -60.9604 | -60.9192 | 61.5875 | 0.073242 | 0.036621 | 0.17395 | 61.8668 | -61.0199 | -0.23346 | 0.041199 | -0.059509 | -0.19226 | 0.10071 | -0.27008 | -0.27924 | -0.29297 | 0.009155 | 0.17395
156.5781 | 122.8043 | -60.7361 | 61.8759 | 0.28447 | 0.0072734 | 0.0033161 | 0.0041403 | 0.068634 | -0.0015869 | 0.068187 | -60.7727 | 61.8668 | -61.0016 | -60.9329 | 61.5692 | 0.041199 | 0.027466 | 0.13733 | 61.8668 | -61.0153 | -0.2655 | -0.009156 | -0.036621 | -0.19684 | 0.082398 | -0.3067 | -0.29755 | -0.27924 | -0.009156 | 0.22888
157.5781 | 122.7905 | -60.7452 | 61.8759 | 0.26921 | 0.0081278 | 0.0080159 | 0.0064901 | 0.065216 | -0.0013733 | 0.068827 | -60.8414 | 61.8896 | -60.997 | -60.9741 | 61.5372 | -0.009155 | 0.045776 | 0.07782 | 61.8439 | -61.0519 | -0.25177 | 0.013732 | -0.096131 | -0.22888 | 0.07782 | -0.33875 | -0.3067 | -0.3067 | -0.032044 | 0.15564
158.5781 | 122.7905 | -60.7498 | 61.8759 | 0.23869 | 0.012187 | 0.0056661 | 0.0047811 | 0.066498 | -0.0003051 | 0.068187 | -60.8139 | 61.8896 | -60.965 | -60.9787 | 61.5234 | 0.004578 | 0.041199 | 0.086975 | 61.8484 | -61.0474 | -0.21515 | 0.013732 | -0.064087 | -0.22888 | 0.068664 | -0.35248 | -0.32501 | -0.29755 | -0.027466 | 0.15106
159.5781 | 122.7814 | -60.7452 | 61.8622 | 0.20054 | 0.010905 | 0.010579 | 0.0043539 | 0.066925 | 0.0005493 | 0.067332 | -60.8093 | 61.908 | -60.9833 | -60.9558 | 61.5372 | 0.013733 | 0.036621 | 0.082397 | 61.821 | -61.0291 | -0.23804 | 0.045776 | -0.064087 | -0.21057 | 0.073242 | -0.32501 | -0.28381 | -0.28381 | -0.041199 | 0.17395
160.5781 | 122.8088 | -60.7315 | 61.8622 | 0.13188 | 0.0079142 | 0.0060933 | 0.0030721 | 0.068207 | -0.0009461 | 0.067332 | -60.8047 | 61.9125 | -60.9695 | -60.9512 | 61.5417 | 0.013733 | 0.027466 | 0.091553 | 61.8668 | -61.0382 | -0.23804 | 0.050354 | -0.073243 | -0.21973 | 0.086975 | -0.32044 | -0.32501 | -0.3067 | 0.004577 | 0.16479
161.5781 | 122.7585 | -60.7498 | 61.853 | 0.12425 | 0.0094096 | 0.0082295 | 0.0043539 | 0.069275 | 0.0005493 | 0.0684 | -60.7956 | 61.8896 | -60.9604 | -60.9512 | 61.5509 | 0.027466 | 0.041199 | 0.10071 | 61.8805 | -61.0336 | -0.21057 | 0.036621 | -0.045776 | -0.20142 | 0.082397 | -0.30212 | -0.32959 | -0.28381 | 0.027466 | 0.1648
162.5781 | 122.7997 | -60.7498 | 61.8622 | 0.13188 | 0.0087688 | 0.0084431 | 0.0043539 | 0.068207 | 0.0007629 | 0.067546 | -60.7864 | 61.8988 | -60.9604 | -60.9238 | 61.5875 | 0.07782 | 0.045776 | 0.16937 | 61.8484 | -61.0107 | -0.21057 | 0.036621 | -0.036621 | -0.17395 | 0.086975 | -0.27466 | -0.26093 | -0.26093 | -0.013733 | 0.17395
163.5781 | 122.8043 | -60.7498 | 61.853 | 0.29973 | 0.010905 | 0.0050251 | 0.0047811 | 0.067139 | -0.0020141 | 0.065623 | -60.7819 | 61.8851 | -60.9512 | -60.9512 | 61.5738 | 0.041199 | 0.045776 | 0.1236 | 61.8393 | -61.0474 | -0.20142 | 0.032044 | -0.032043 | -0.20142 | 0.09613 | -0.27923 | -0.2655 | -0.29755 | -0.013733 | 0.16937
164.5781 | 122.7676 | -60.7269 | 61.8484 | 0.27684 | 0.0094096 | 0.0075887 | 0.0034993 | 0.066711 | 0.0005493 | 0.069255 | -60.8368 | 61.9034 | -60.9695 | -60.9879 | 61.528 | -0.018311 | 0.036621 | 0.045776 | 61.8668 | -61.0428 | -0.24261 | 0.054931 | -0.10986 | -0.26093 | 0.054932 | -0.32043 | -0.33874 | -0.31586 | 0.01831 | 0.13275
165.5781 | 122.7631 | -60.7498 | 61.8668 | 0.2921 | 0.0094096 | 0.010579 | 0.0049947 | 0.067993 | -0.0005189 | 0.067546 | -60.8185 | 61.9034 | -60.9787 | -60.965 | 61.5372 | -0.013733 | 0.036621 | 0.064087 | 61.8668 | -61.0474 | -0.22888 | 0.036621 | -0.068664 | -0.21515 | 0.082397 | -0.32959 | -0.32959 | -0.29755 | 0 | 0.16022
166.5781 | 122.7631 | -60.7452 | 61.8622 | 0.23106 | 0.0072734 | 0.0060933 | 0.0043539 | 0.066711 | -0.0007325 | 0.069041 | -60.8139 | 61.8988 | -60.9741 | -60.9787 | 61.5417 | 0 | 0.050354 | 0.082397 | 61.8622 | -61.0428 | -0.22888 | 0.036621 | -0.068665 | -0.23346 | 0.064087 | -0.32044 | -0.32044 | -0.29755 | 0 | 0.16022
167.5781 | 122.8226 | -60.7452 | 61.8393 | 0.20054 | 0.011119 | 0.0056661 | 0.0045675 | 0.066711 | -0.0011597 | 0.067759 | -60.8047 | 61.908 | -60.9787 | -60.9695 | 61.5417 | 0.004578 | 0.018311 | 0.091553 | 61.853 | -61.0336 | -0.23346 | 0.068665 | -0.05951 | -0.2243 | 0.064087 | -0.29755 | -0.31128 | -0.28839 | 0.013733 | 0.17395
168.5781 | 122.7768 | -60.7636 | 61.8576 | 0.15477 | 0.0096232 | 0.010152 | 0.0037129 | 0.066498 | -0.0013733 | 0.067973 | -60.7956 | 61.9034 | -60.9924 | -60.9512 | 61.5646 | 0.018311 | 0.018311 | 0.091553 | 61.853 | -61.0336 | -0.22888 | 0.045776 | -0.032043 | -0.18768 | 0.082397 | -0.29297 | -0.28839 | -0.27008 | -0.004578 | 0.19684
169.5781 | 122.8317 | -60.7361 | 61.8576 | 0.13951 | 0.010264 | 0.0086567 | 0.0043539 | 0.068848 | -0.0013733 | 0.069468 | -60.8047 | 61.8988 | -60.965 | -60.9283 | 61.5601 | 0.050354 | 0.022888 | 0.10986 | 61.8668 | -61.0474 | -0.22888 | 0.041199 | -0.068665 | -0.19226 | 0.11902 | -0.29755 | -0.3067 | -0.31128 | 0.009155 | 0.16022
170.5781 | 122.7997 | -60.7544 | 61.8713 | 0.10899 | 0.0081278 | 0.0097249 | 0.0037129 | 0.06607 | -0.0030823 | 0.068187 | -60.791 | 61.8896 | -60.9879 | -60.9467 | 61.5555 | 0.041199 | 0.041199 | 0.11444 | 61.8668 | -61.0382 | -0.23346 | 0.01831 | -0.036621 | -0.19226 | 0.091553 | -0.31586 | -0.31128 | -0.28381 | -0.004578 | 0.19684
171.5781 | 122.7905 | -60.7544 | 61.8668 | 0.2158 | 0.011973 | 0.0063069 | 0.0032857 | 0.06842 | 0.0003357 | 0.068827 | -60.8276 | 61.8805 | -60.9833 | -60.9695 | 61.5234 | -0.036621 | 0.054932 | 0.059509 | 61.8759 | -61.0519 | -0.22888 | 0.013733 | -0.073242 | -0.21515 | 0.082398 | -0.34332 | -0.35248 | -0.29755 | 0.009156 | 0.15564
172.5781 | 122.7493 | -60.7361 | 61.8576 | 0.22343 | 0.0087688 | 0.010579 | 0.0054219 | 0.069488 | -0.0020141 | 0.068187 | -60.8276 | 61.8713 | -60.9879 | -60.9879 | 61.5234 | -0.022888 | 0.041199 | 0.064087 | 61.8942 | -61.0382 | -0.25177 | 0.013733 | -0.091553 | -0.25177 | 0.050354 | -0.33417 | -0.37079 | -0.30212 | 0.036621 | 0.16022
173.5781 | 122.7859 | -60.7681 | 61.8439 | 0.24632 | 0.0094096 | 0.010579 | 0.0039267 | 0.068207 | 0.0009765 | 0.068187 | -60.8139 | 61.8988 | -60.9604 | -60.9695 | 61.5372 | -0.009155 | 0.036621 | 0.073242 | 61.8668 | -61.0382 | -0.19226 | 0.054932 | -0.045777 | -0.20142 | 0.068665 | -0.3067 | -0.32959 | -0.27008 | 0.022888 | 0.14648
174.5781 | 122.7539 | -60.7315 | 61.8622 | 0.20054 | 0.0089824 | 0.0084431 | 0.0060629 | 0.068207 | 0.0001221 | 0.069682 | -60.8002 | 61.8896 | -60.9833 | -60.965 | 61.5326 | 0.004578 | 0.036621 | 0.086975 | 61.8622 | -61.0153 | -0.25177 | 0.027465 | -0.068665 | -0.23346 | 0.050354 | -0.32959 | -0.32959 | -0.28381 | 0 | 0.1831
175.5781 | 122.7722 | -60.7452 | 61.8622 | 0.13951 | 0.010478 | 0.0092977 | 0.0041403 | 0.06607 | -0.0050049 | 0.0684 | -60.791 | 61.8988 | -60.9558 | -61.0062 | 61.5372 | 0.12817 | 0.013733 | 0.13733 | 61.8576 | -61.0519 | -0.21057 | 0.036621 | -0.045777 | -0.26093 | 0.045776 | -0.32501 | -0.32043 | -0.3067 | -0.004578 | 0.16479
176.5781 | 122.8088 | -60.7636 | 61.853 | 0.17003 | 0.010264 | 0.0082295 | 0.0034993 | 0.067993 | -0.0028687 | 0.068827 | -60.8093 | 61.8896 | -60.9604 | -60.965 | 61.5555 | 0 | 0.032043 | 0.091553 | 61.853 | -61.0474 | -0.19684 | 0.036621 | -0.045776 | -0.20142 | 0.082397 | -0.29755 | -0.29755 | -0.28381 | 0 | 0.15106
177.5781 | 122.7585 | -60.759 | 61.853 | 0.32261 | 0.009196 | 0.0090841 | 0.0052083 | 0.069061 | -0.0005189 | 0.066905 | -60.8505 | 61.8851 | -60.997 | -60.997 | 61.5097 | -0.041199 | 0.041199 | 0.036621 | 61.8713 | -61.0519 | -0.23804 | 0.032044 | -0.091553 | -0.23804 | 0.054932 | -0.34332 | -0.36163 | -0.29297 | 0.018311 | 0.14648
178.5781 | 122.7997 | -60.7498 | 61.8668 | 0.27684 | 0.010691 | 0.0095113 | 0.0054219 | 0.066498 | -0.0009461 | 0.070536 | -60.8414 | 61.8851 | -60.9833 | -61.0062 | 61.5005 | -0.032043 | 0.041199 | 0.050354 | 61.853 | -61.0474 | -0.23346 | 0.018311 | -0.091553 | -0.25635 | 0.041198 | -0.36621 | -0.35248 | -0.29755 | -0.013733 | 0.14191
179.5781 | 122.7676 | -60.7681 | 61.8576 | 0.26921 | 0.011973 | 0.0080159 | 0.0041403 | 0.067993 | -0.0018005 | 0.069896 | -60.8231 | 61.9125 | -60.9787 | -61.0062 | 61.5143 | -0.027466 | 0.050354 | 0.059509 | 61.8759 | -61.0611 | -0.21057 | 0.054932 | -0.054932 | -0.23804 | 0.054931 | -0.34332 | -0.36163 | -0.29297 | 0.018311 | 0.15564
180.5781 | 122.7997 | -60.7407 | 61.8668 | 0.24632 | 0.0094096 | 0.0067341 | 0.0026449 | 0.066284 | -0.0009461 | 0.068187 | -60.8322 | 61.8805 | -60.9879 | -60.9741 | 61.5326 | -0.004578 | 0.032043 | 0.068665 | 61.8851 | -61.0611 | -0.24719 | 0.013733 | -0.091552 | -0.23346 | 0.086975 | -0.33417 | -0.35248 | -0.32043 | 0.018311 | 0.15564
181.5781 | 122.7676 | -60.7544 | 61.8484 | 0.20054 | 0.011759 | 0.010793 | 0.0030721 | 0.06842 | -9.1495e-05 | 0.067973 | -60.8185 | 61.8988 | -60.9558 | -60.9695 | 61.5372 | 0.004578 | 0.018311 | 0.082397 | 61.8668 | -61.0611 | -0.20142 | 0.050354 | -0.064086 | -0.21515 | 0.091553 | -0.31128 | -0.32959 | -0.3067 | 0.01831 | 0.13733
182.5781 | 122.8271 | -60.7224 | 61.8622 | 0.11662 | 0.012828 | 0.0088703 | 0.0045675 | 0.068634 | 0.0014039 | 0.068827 | -60.791 | 61.9034 | -60.9741 | -60.9146 | 61.4319 | -0.054932 | 0.14191 | 0.15106 | 61.8668 | -61.0382 | -0.25177 | 0.041198 | -0.068665 | -0.19226 | 0.1236 | -0.4303 | -0.43487 | -0.31586 | 0.004577 | 0.1831
183.5781 | 122.8088 | -60.7178 | 61.8484 | 0.13951 | 0.0085552 | 0.0090841 | 0.0049947 | 0.066925 | -0.0005189 | 0.066905 | -60.791 | 61.8851 | -60.997 | -60.9512 | 61.5555 | 0.018311 | 0.018311 | 0.09613 | 61.8805 | -61.0336 | -0.27924 | 0.036621 | -0.073243 | -0.23346 | 0.082397 | -0.29297 | -0.32501 | -0.31586 | 0.032043 | 0.20599
184.5781 | 122.7814 | -60.7498 | 61.8439 | 0.24632 | 0.011119 | 0.0073751 | 0.0062765 | 0.066498 | -0.0003051 | 0.067759 | -60.8505 | 61.8988 | -60.9833 | -61.0062 | 61.5097 | -0.022888 | 0.032043 | 0.059509 | 61.8851 | -61.0519 | -0.23346 | 0.054932 | -0.10071 | -0.25635 | 0.045776 | -0.33417 | -0.37537 | -0.30212 | 0.041199 | 0.13275
185.5781 | 122.7997 | -60.7544 | 61.853 | 0.2158 | 0.0094096 | 0.012716 | 0.0034993 | 0.068207 | -0.0005189 | 0.067332 | -60.8276 | 61.908 | -60.9833 | -60.9833 | 61.5143 | -0.018311 | 0.050354 | 0.050354 | 61.8668 | -61.0565 | -0.22888 | 0.054932 | -0.073242 | -0.22888 | 0.073243 | -0.33874 | -0.35248 | -0.30212 | 0.013733 | 0.15564
186.5781 | 122.7585 | -60.7773 | 61.8301 | 0.2921 | 0.0087688 | 0.012929 | 0.0039267 | 0.070343 | 0.0024719 | 0.070109 | -60.8734 | 61.8851 | -60.9695 | -61.0153 | 61.4868 | -0.059509 | 0.004578 | 0.004578 | 61.8713 | -61.0703 | -0.19226 | 0.054932 | -0.09613 | -0.23804 | 0.054931 | -0.34332 | -0.38452 | -0.29297 | 0.041199 | 0.09613
187.5781 | 122.818 | -60.759 | 61.8851 | 0.20817 | 0.010691 | 0.0095113 | 0.0039267 | 0.067993 | -9.1495e-05 | 0.070964 | -60.8322 | 61.8851 | -60.9879 | -60.965 | 61.5326 | -0.018311 | 0.032043 | 0.050354 | 61.8393 | -61.0519 | -0.22888 | 0 | -0.073242 | -0.20599 | 0.086975 | -0.35248 | -0.3067 | -0.29297 | -0.045777 | 0.15564
188.5781 | 122.7402 | -60.759 | 61.8484 | 0.33024 | 0.010264 | 0.0086567 | 0.0064901 | 0.066925 | -0.0035095 | 0.068614 | -60.878 | 61.8942 | -60.9924 | -61.0336 | 61.4731 | -0.036621 | 0.013733 | 0.013733 | 61.8851 | -61.0519 | -0.23346 | 0.045776 | -0.11902 | -0.27466 | 0.018311 | -0.37537 | -0.41199 | -0.29297 | 0.036621 | 0.11444
189.5781 | 122.7951 | -60.7086 | 61.8484 | 1.6272 | 0.0096232 | 0.0090841 | 0.0026449 | 0.065002 | 0.0007629 | 0.069255 | -60.7636 | 61.8759 | -60.9695 | -60.9238 | 61.5967 | 0.07782 | 0.032043 | 0.13733 | 61.8576 | -61.0336 | -0.26093 | 0.027466 | -0.054932 | -0.21515 | 0.10986 | -0.25177 | -0.26093 | -0.32501 | 0.009155 | 0.20599
190.5781 | 122.8317 | -60.7361 | 61.8805 | 0.20817 | 0.01005 | 0.012929 | 0.0047811 | 0.067352 | -0.0011597 | 0.067759 | -60.91 | 61.8988 | -60.9741 | -60.9558 | 61.5646 | 0.091553 | 0.041199 | 0.14191 | 61.8805 | -61.0336 | -0.23804 | 0.018311 | -0.17395 | -0.21973 | 0.077819 | -0.31586 | -0.31586 | -0.29755 | 0 | 0.064087
191.5781 | 122.7859 | -60.7636 | 61.8484 | 0.27684 | 0.0083416 | 0.0084431 | 0.0071309 | 0.067139 | -0.0015869 | 0.066905 | -60.8231 | 61.8942 | -60.9787 | -60.9558 | 61.5372 | 0 | 0.032043 | 0.09613 | 61.8668 | -61.0474 | -0.21515 | 0.045776 | -0.059509 | -0.19226 | 0.091552 | -0.31128 | -0.32959 | -0.28381 | 0.01831 | 0.15564
192.5781 | 122.7997 | -60.7269 | 61.8622 | 0.17003 | 0.0094096 | 0.0090841 | 0.0058493 | 0.069061 | -0.0030823 | 0.069468 | -60.8093 | 61.8759 | -60.9512 | -60.9695 | 61.528 | 0.018311 | 0.032043 | 0.07782 | 61.8622 | -61.0153 | -0.2243 | 0.013733 | -0.082397 | -0.24261 | 0.045777 | -0.33417 | -0.33417 | -0.28839 | 0 | 0.14191
193.5781 | 122.7539 | -60.7407 | 61.8484 | 0.18529 | 0.011759 | 0.010579 | 0.0056355 | 0.066498 | -0.0015869 | 0.067759 | -60.8093 | 61.8942 | -60.9787 | -60.9604 | 61.5463 | 0.018311 | 0.022888 | 0.091553 | 61.8713 | -61.0382 | -0.23804 | 0.045776 | -0.068664 | -0.21973 | 0.07782 | -0.30212 | -0.32501 | -0.29755 | 0.022888 | 0.16937
194.5781 | 122.8226 | -60.7269 | 61.8622 | 0.11662 | 0.010478 | 0.0080159 | 0.0058493 | 0.069702 | -0.0018005 | 0.068187 | -60.7956 | 61.9171 | -60.9695 | -60.9558 | 61.5372 | 0.041199 | 0.018311 | 0.10071 | 61.8713 | -61.0245 | -0.24261 | 0.054931 | -0.068664 | -0.22888 | 0.068664 | -0.32501 | -0.33417 | -0.29755 | 0.009155 | 0.17395
195.5781 | 122.7722 | -60.7315 | 61.8256 | 0.1624 | 0.012187 | 0.010366 | 0.0030721 | 0.068634 | -0.0028687 | 0.069468 | -60.7956 | 61.8942 | -60.9467 | -60.9421 | 61.5417 | 0.032043 | 0.027466 | 0.1236 | 61.8805 | -61.0199 | -0.21515 | 0.068664 | -0.064087 | -0.21057 | 0.077819 | -0.28381 | -0.33875 | -0.28839 | 0.054931 | 0.15106
196.5781 | 122.8271 | -60.7407 | 61.8439 | -0.058855 | 0.010264 | 0.0086567 | 0.0041403 | 0.067779 | -0.0013733 | 0.066264 | -60.7864 | 61.8896 | -60.9879 | -60.9192 | 61.5601 | 0.050354 | 0.045776 | 0.14191 | 61.8713 | -61.0199 | -0.24719 | 0.045776 | -0.045776 | -0.17853 | 0.10071 | -0.28381 | -0.31128 | -0.27923 | 0.027466 | 0.20142
197.5781 | 122.8226 | -60.7269 | 61.8759 | 1.0779 | 0.009196 | 0.0092977 | 0.0045675 | 0.06607 | -0.0005189 | 0.068827 | -60.7636 | 61.8896 | -60.9787 | -60.9283 | 61.5875 | 0.059509 | 0.027466 | 0.13733 | 61.8851 | -61.0291 | -0.25177 | 0.013732 | -0.036621 | -0.20142 | 0.10071 | -0.28839 | -0.29755 | -0.30212 | 0.009155 | 0.21515
198.5781 | 122.8683 | -60.7178 | 61.821 | 0.37602 | 0.0066326 | 0.010152 | -0.0029093 | 0.067352 | -0.0003051 | 0.071818 | -60.791 | 61.7706 | -60.9833 | -60.9009 | 61.615 | 0.068665 | -0.17395 | 0.15564 | 61.8027 | -60.9924 | -0.2655 | -0.050354 | -0.073243 | -0.18311 | 0.091553 | -0.20599 | -0.18768 | -0.27466 | -0.018311 | 0.19226
199.5781 | 122.7768 | -60.7315 | 61.8805 | 0.25395 | 0.011546 | 0.0065205 | 0.0054219 | 0.068207 | -0.0009461 | 0.067546 | -60.8368 | 61.8988 | -60.9787 | -61.0062 | 61.496 | -0.054932 | 0.050354 | 0.027466 | 61.8347 | -61.0794 | -0.24719 | 0.018311 | -0.10529 | -0.27466 | 0.073242 | -0.38452 | -0.33874 | -0.3479 | -0.045776 | 0.14191
200.5781 | 122.7356 | -60.7727 | 61.8851 | 0.26921 | 0.0089824 | 0.0067341 | 0.0052083 | 0.067779 | -9.1495e-05 | 0.068187 | -60.8414 | 61.8988 | -60.9879 | -60.997 | 61.5097 | -0.027466 | 0.036621 | 0.054932 | 61.8668 | -61.0565 | -0.21515 | 0.013733 | -0.068665 | -0.2243 | 0.05951 | -0.37537 | -0.35706 | -0.28381 | -0.018311 | 0.14648
201.5781 | 122.7631 | -60.7361 | 61.8622 | 0.22343 | 0.0081278 | 0.0031025 | 0.0026449 | 0.065643 | -0.0015869 | 0.066264 | -60.8459 | 61.9308 | -60.9604 | -60.9741 | 61.5143 | -0.027466 | 0.022888 | 0.064087 | 61.8713 | -61.0336 | -0.2243 | 0.068664 | -0.10986 | -0.23804 | 0.059509 | -0.3479 | -0.35706 | -0.29755 | 0.009155 | 0.11444
202.5781 | 122.7631 | -60.7315 | 61.8622 | 0.20817 | 0.0089824 | 0.0073751 | 0.0045675 | 0.068848 | -0.0003051 | 0.067332 | -60.8368 | 61.8851 | -61.0153 | -60.9695 | 61.528 | -0.022888 | 0.045776 | 0.059509 | 61.8713 | -61.0519 | -0.28381 | 0.022888 | -0.10529 | -0.23804 | 0.082398 | -0.33417 | -0.34332 | -0.32043 | 0.009155 | 0.17853
203.5781 | 122.8317 | -60.7269 | 61.8576 | 0.10899 | 0.0089824 | 0.0020345 | 0.0047811 | 0.064789 | 0.0024719 | 0.06605 | -60.7864 | 61.9171 | -60.9375 | -61.0245 | 61.5189 | 0.13275 | 0.027466 | 0.12817 | 61.8347 | -61.0336 | -0.21057 | 0.059509 | -0.059509 | -0.29755 | 0.009155 | -0.33875 | -0.31586 | -0.3067 | -0.022888 | 0.15106
204.5781 | 122.7814 | -60.7361 | 61.8713 | 0.13188 | 0.01005 | 0.0088703 | 0.0060629 | 0.069916 | -0.0015869 | 0.070109 | -60.8002 | 61.8896 | -60.9695 | -60.9421 | 61.5509 | 0.027466 | 0.032043 | 0.10529 | 61.8896 | -61.0107 | -0.23346 | 0.01831 | -0.064087 | -0.20599 | 0.068664 | -0.32044 | -0.33875 | -0.27466 | 0.01831 | 0.16937
205.5781 | 122.8043 | -60.759 | 61.8484 | 0.19291 | 0.012614 | 0.0080159 | 0.0060629 | 0.06842 | 0.0011901 | 0.067759 | -60.8322 | 61.9125 | -60.9833 | -60.9833 | 61.5326 | -0.009155 | 0.027466 | 0.064087 | 61.8759 | -61.0703 | -0.2243 | 0.064087 | -0.073242 | -0.2243 | 0.086975 | -0.31586 | -0.34332 | -0.31128 | 0.027466 | 0.15106
206.5781 | 122.7814 | -60.7681 | 61.8622 | 0.22343 | 0.010264 | 0.0095113 | 0.0039267 | 0.067139 | -9.1495e-05 | 0.070109 | -60.8185 | 61.908 | -60.9924 | -60.9879 | 61.5417 | -0.009155 | 0.036621 | 0.068665 | 61.8759 | -61.0291 | -0.22431 | 0.045776 | -0.050354 | -0.21973 | 0.041199 | -0.32044 | -0.33417 | -0.26093 | 0.013733 | 0.17395
207.5781 | 122.7997 | -60.759 | 61.853 | 0.20817 | 0.0098368 | 0.0071615 | 0.0052083 | 0.066711 | 0.0005493 | 0.070109 | -60.8002 | 61.9125 | -60.9421 | -60.9558 | 61.5372 | 0.009155 | 0.018311 | 0.091553 | 61.853 | -61.0565 | -0.18311 | 0.05951 | -0.041199 | -0.19684 | 0.10071 | -0.31586 | -0.31586 | -0.29755 | 0 | 0.14191
208.5781 | 122.8409 | -60.7361 | 61.8668 | 0.15477 | 0.0094096 | 0.0086567 | 0.0043539 | 0.067566 | -0.0018005 | 0.067759 | -60.7956 | 61.8805 | -60.965 | -60.9421 | 61.5555 | 0.045776 | 0.032043 | 0.11444 | 61.8439 | -61.0428 | -0.22888 | 0.013733 | -0.059509 | -0.20599 | 0.10071 | -0.31128 | -0.28839 | -0.3067 | -0.022888 | 0.16937
209.5781 | 122.7997 | -60.7452 | 61.8759 | 0.040327 | 0.0096232 | 0.0078023 | 0.0032857 | 0.06543 | -0.0005189 | 0.069041 | -60.7773 | 61.8851 | -60.9741 | -60.9283 | 61.5692 | 0.036621 | 0.041199 | 0.13275 | 61.8668 | -61.0382 | -0.22888 | 0.009155 | -0.032044 | -0.18311 | 0.10986 | -0.3067 | -0.29755 | -0.29297 | -0.009156 | 0.19684
210.5781 | 122.8317 | -60.7224 | 61.8759 | 0.047956 | 0.0098368 | 0.0071615 | 0.0028585 | 0.066925 | -0.0007325 | 0.068614 | -60.791 | 61.908 | -60.9558 | -60.91 | 61.5921 | 0.082397 | 0.050354 | 0.16937 | 61.8759 | -61.0107 | -0.23346 | 0.032043 | -0.068665 | -0.18768 | 0.10071 | -0.28381 | -0.28381 | -0.28839 | 0 | 0.16479
211.5781 | 122.7951 | -60.7224 | 61.8668 | 0.14714 | 0.0077006 | 0.0067341 | 0.0034993 | 0.067566 | -0.0009461 | 0.0684 | -60.7727 | 61.8851 | -60.9604 | -60.9329 | 61.5921 | 0.064087 | 0.036621 | 0.15106 | 61.8805 | -61.0336 | -0.23804 | 0.018311 | -0.050354 | -0.21057 | 0.10071 | -0.27466 | -0.28839 | -0.31128 | 0.013733 | 0.18768
212.5781 | 122.8317 | -60.7315 | 61.8668 | -0.70735 | 0.0077006 | 0.0099385 | 0.0064901 | 0.068848 | -0.0018005 | 0.068614 | -60.8047 | 61.8896 | -61.0016 | -60.9283 | 61.5601 | 0.059509 | 0.041199 | 0.13733 | 61.8805 | -61.0199 | -0.27008 | 0.022888 | -0.073243 | -0.19684 | 0.091552 | -0.3067 | -0.32043 | -0.28839 | 0.013733 | 0.19684
213.5781 | 122.818 | -60.7315 | 61.8851 | 0.13188 | 0.010264 | 0.0045979 | 0.0032857 | 0.068848 | -0.0024415 | 0.067759 | -60.7773 | 61.8851 | -60.965 | -61.0245 | 61.441 | -0.009155 | 0.082397 | 0.14191 | 61.8576 | -61.0336 | -0.23346 | 0 | -0.045777 | -0.29297 | 0.009155 | -0.44403 | -0.41656 | -0.30212 | -0.027466 | 0.18768
214.5781 | 122.8409 | -60.7132 | 61.8713 | 0.086103 | 0.0085552 | 0.0069477 | 0.0043539 | 0.067993 | -0.0005189 | 0.068614 | -60.7864 | 61.8805 | -60.9604 | -60.9283 | 61.6013 | 0.07782 | 0.027466 | 0.16479 | 61.8851 | -61.0245 | -0.24719 | 0.009155 | -0.073242 | -0.21515 | 0.09613 | -0.27008 | -0.28381 | -0.31128 | 0.013733 | 0.17395
215.5781 | 122.818 | -60.7178 | 61.8622 | 0.040327 | 0.0094096 | 0.0069477 | 0.0030721 | 0.06607 | -0.0024415 | 0.067973 | -60.7864 | 61.8713 | -60.9512 | -60.9055 | 61.5875 | 0.073242 | 0.064087 | 0.17395 | 61.8759 | -61.0153 | -0.23346 | 0.009155 | -0.068665 | -0.18768 | 0.10986 | -0.27466 | -0.28839 | -0.29755 | 0.013733 | 0.1648
216.5781 | 122.8043 | -60.7132 | 61.8851 | 0.0098091 | 0.0087688 | 0.011007 | 0.0017903 | 0.066711 | -0.0020141 | 0.067759 | -60.8093 | 61.8988 | -60.997 | -60.9238 | 61.6104 | 0.086975 | 0.09613 | 0.1831 | 61.8713 | -61.0062 | -0.28381 | 0.013733 | -0.09613 | -0.21057 | 0.082398 | -0.27466 | -0.26093 | -0.29297 | -0.013733 | 0.18768
217.5781 | 122.7997 | -60.7452 | 61.8851 | -0.020708 | 0.0070598 | 0.0099385 | -0.0024821 | 0.063721 | -0.0024415 | 0.067332 | -60.8505 | 61.8851 | -60.997 | -61.1023 | 61.3861 | -0.009155 | 0.22888 | 0.10529 | 61.8713 | -60.997 | -0.25177 | 0 | -0.10529 | -0.35706 | -0.10529 | -0.49896 | -0.48523 | -0.25177 | -0.013733 | 0.14648
218.5781 | 122.7676 | -60.7498 | 61.8988 | 0.0021796 | 0.0066326 | 0.0056661 | 0.0013631 | 0.065643 | -0.0005189 | 0.067118 | -60.8185 | 61.9034 | -60.9604 | -60.965 | 61.5601 | 0.059509 | 0.13275 | 0.14648 | 61.9125 | -61.0291 | -0.21057 | 0.004577 | -0.068664 | -0.21515 | 0.064087 | -0.33874 | -0.35248 | -0.27924 | 0.013733 | 0.14191
219.5781 | 122.8455 | -60.7269 | 61.8759 | 0.0098091 | 0.007487 | 0.0067341 | 0.0032857 | 0.067139 | 0.0007629 | 0.068187 | -60.8139 | 61.8942 | -60.9879 | -60.9283 | 61.5829 | 0.07782 | 0.12817 | 0.17395 | 61.908 | -61.0107 | -0.26093 | 0.01831 | -0.086975 | -0.20142 | 0.082397 | -0.29297 | -0.32501 | -0.28381 | 0.032043 | 0.17395
220.5781 | 122.7493 | -60.7361 | 61.9171 | -0.028338 | 0.0070598 | 0.0088703 | -0.00034593 | 0.067779 | 0.0001221 | 0.067759 | -60.8505 | 61.8988 | -60.9695 | -60.965 | 61.5601 | 0.050354 | 0.13275 | 0.14648 | 61.8942 | -61.0062 | -0.23346 | -0.01831 | -0.11444 | -0.22888 | 0.041199 | -0.35705 | -0.33417 | -0.27008 | -0.022888 | 0.11902
221.5781 | 122.7951 | -60.7224 | 61.8851 | 0.96348 | 0.0087688 | 0.0026753 | 0.00072227 | 0.065857 | -0.0015869 | 0.066264 | -60.8231 | 61.8668 | -61.0016 | -60.965 | 61.5601 | 0.082397 | 0.14648 | 0.15106 | 61.8942 | -61.0062 | -0.27924 | -0.018311 | -0.10071 | -0.24261 | 0.041199 | -0.32501 | -0.33417 | -0.28381 | 0.009155 | 0.17853
222.5781 | 122.8867 | -60.7178 | 61.8301 | 0.4218 | 0.0077006 | 0.0045979 | 0.00093587 | 0.065643 | -9.1495e-05 | 0.067973 | -60.7864 | 61.7889 | -60.965 | -60.91 | 61.5967 | 0.068665 | -0.20599 | 0.14648 | 61.8027 | -60.9879 | -0.24719 | -0.041199 | -0.068665 | -0.19226 | 0.07782 | -0.23346 | -0.20599 | -0.27008 | -0.027466 | 0.17853
223.5781 | 122.7768 | -60.7452 | 61.8896 | -0.081743 | 0.0079142 | 0.0035299 | -0.00077313 | 0.063293 | 0.0001221 | 0.068614 | -60.8551 | 61.8622 | -60.9879 | -60.965 | 61.5509 | 0.050354 | 0.15106 | 0.15106 | 61.8622 | -61.0062 | -0.24262 | -0.027465 | -0.10986 | -0.21973 | 0.041199 | -0.33875 | -0.31128 | -0.26093 | -0.027465 | 0.13275
224.5781 | 122.7997 | -60.7407 | 61.8896 | -0.097002 | 0.0083416 | 0.0037435 | -0.00013233 | 0.06308 | -0.0007325 | 0.066905 | -60.8505 | 61.8576 | -60.9467 | -60.9512 | 61.5601 | 0.054932 | 0.14648 | 0.14648 | 61.8988 | -60.997 | -0.20599 | -0.032043 | -0.10986 | -0.21057 | 0.045776 | -0.32959 | -0.33874 | -0.25635 | 0.009156 | 0.09613
225.5781 | 122.7631 | -60.7178 | 61.8942 | -0.074114 | 0.0062052 | 0.0092977 | 0.00093587 | 0.062866 | 0.0009765 | 0.0684 | -60.8047 | 61.8393 | -60.9512 | -60.9146 | 61.5692 | 0.086975 | 0.10071 | 0.17853 | 61.8851 | -60.9787 | -0.23346 | -0.054932 | -0.086976 | -0.19684 | 0.064087 | -0.32501 | -0.31586 | -0.26093 | -0.009155 | 0.14648
226.5781 | 122.7859 | -60.7269 | 61.908 | -0.028338 | 0.0081278 | 0.0031025 | -0.00013233 | 0.063721 | -0.0032959 | 0.067973 | -60.8505 | 61.8576 | -60.9512 | -60.9604 | 61.5417 | 0.054932 | 0.15564 | 0.16022 | 61.8805 | -61.0016 | -0.2243 | -0.050354 | -0.1236 | -0.23346 | 0.041199 | -0.36621 | -0.33875 | -0.27466 | -0.027466 | 0.10071
227.5781 | 122.7631 | -60.7544 | 61.8576 | 0.33787 | 0.0059916 | 0.0071615 | 0.0069173 | 0.065643 | -0.0020141 | 0.068187 | -60.8597 | 61.8759 | -60.997 | -61.0107 | 61.4822 | -0.064087 | -0.009155 | 0.004578 | 61.8759 | -61.0245 | -0.24261 | 0.018311 | -0.10528 | -0.25635 | 0.013733 | -0.37537 | -0.39368 | -0.27008 | 0.018311 | 0.13733
228.5781 | 122.7905 | -60.7178 | 61.9034 | -0.058855 | 0.0083416 | 0.0069477 | -0.00013233 | 0.064789 | -0.0022277 | 0.069682 | -60.8093 | 61.8301 | -60.965 | -60.9055 | 61.5921 | 0.10986 | 0.10986 | 0.17853 | 61.8851 | -60.9833 | -0.24719 | -0.073242 | -0.091553 | -0.18768 | 0.077819 | -0.31128 | -0.29297 | -0.2655 | -0.01831 | 0.15564
229.5781 | 122.8455 | -60.6857 | 61.8942 | -0.066485 | 0.0072734 | 0.0022481 | -0.0014139 | 0.064361 | -0.0003051 | 0.066264 | -60.8002 | 61.8073 | -60.965 | -60.8871 | 61.6196 | 0.11902 | 0.068665 | 0.21973 | 61.8439 | -60.9467 | -0.27924 | -0.086975 | -0.11444 | -0.20142 | 0.059509 | -0.27466 | -0.2243 | -0.26093 | -0.050354 | 0.16479
230.5781 | 122.7676 | -60.7178 | 61.8988 | -0.081743 | 0.0089824 | 0.0024617 | 0.0034993 | 0.067566 | -0.0035095 | 0.067973 | -60.8505 | 61.8576 | -60.9741 | -60.9238 | 61.5692 | 0.036621 | 0.12817 | 0.13275 | 61.8713 | -61.0153 | -0.25635 | -0.041199 | -0.13275 | -0.20599 | 0.091553 | -0.32959 | -0.30212 | -0.29755 | -0.027466 | 0.1236
231.5781 | 122.7814 | -60.7315 | 61.8851 | -0.081743 | 0.0042826 | 0.0018209 | -0.00013233 | 0.064575 | -9.1495e-05 | 0.066905 | -60.8047 | 61.8301 | -60.9421 | -60.9238 | 61.5738 | 0.073242 | 0.1236 | 0.19684 | 61.8713 | -60.965 | -0.21057 | -0.054932 | -0.073243 | -0.19226 | 0.041199 | -0.31128 | -0.29755 | -0.23346 | -0.013733 | 0.13733
232.5781 | 122.7539 | -60.7544 | 61.8759 | 0.17003 | 0.010264 | 0.010152 | 0.0056355 | 0.067566 | -0.0009461 | 0.067332 | -60.8414 | 61.8988 | -60.9833 | -60.9741 | 61.4868 | -0.027466 | 0.050354 | 0.022888 | 61.8668 | -61.0565 | -0.22888 | 0.022888 | -0.086975 | -0.21973 | 0.082398 | -0.3891 | -0.37994 | -0.30212 | -0.009156 | 0.14191
233.5781 | 122.8546 | -60.6995 | 61.8851 | -0.043596 | 0.0055644 | 0.0016073 | -0.0012003 | 0.06607 | -0.0007325 | 0.069896 | -60.791 | 61.7981 | -60.9558 | -60.8688 | 61.6425 | 0.12817 | 0.050354 | 0.25177 | 61.8484 | -60.9604 | -0.25635 | -0.086975 | -0.091553 | -0.16937 | 0.091553 | -0.24262 | -0.20599 | -0.26093 | -0.036621 | 0.16479
234.5781 | 122.8271 | -60.6812 | 61.8622 | 0.0021796 | 0.007487 | 0.0067341 | -0.00055953 | 0.063293 | 0.0001221 | 0.069041 | -60.7819 | 61.7752 | -60.9512 | -60.8505 | 61.647 | 0.16479 | 0.013733 | 0.2655 | 61.821 | -60.9467 | -0.27008 | -0.086975 | -0.10071 | -0.16937 | 0.09613 | -0.21515 | -0.17395 | -0.2655 | -0.041199 | 0.16937
235.5781 | 122.9004 | -60.6857 | 61.8759 | 0.27684 | 0.0059916 | 0.0018209 | -0.00013233 | 0.059875 | -0.0024415 | 0.069468 | -60.7498 | 61.7615 | -60.9192 | -60.8688 | 61.6562 | 0.17395 | -0.027466 | 0.28381 | 61.821 | -60.9375 | -0.23346 | -0.11444 | -0.064087 | -0.1831 | 0.068665 | -0.21973 | -0.1648 | -0.25177 | -0.054932 | 0.16937
236.5781 | 122.8775 | -60.6995 | 61.8622 | -0.37166 | 0.007487 | 0.0063069 | -0.0016275 | 0.062012 | -0.0018005 | 0.066691 | -60.8185 | 61.7661 | -60.9375 | -60.8368 | 61.6425 | 0.15564 | -0.027466 | 0.26093 | 61.8164 | -60.9421 | -0.23804 | -0.096131 | -0.11902 | -0.13733 | 0.10529 | -0.21973 | -0.17395 | -0.24262 | -0.045777 | 0.11902
237.5781 | 122.8867 | -60.6995 | 61.8668 | -0.058855 | 0.00086457 | 0.0037435 | -0.00098673 | 0.059021 | -0.0009461 | 0.064769 | -60.5347 | 61.8256 | -60.91 | -60.8917 | 61.6425 | 0.17853 | -0.064087 | 0.27008 | 61.8027 | -60.9329 | -0.21057 | -0.041198 | 0.16479 | -0.19226 | 0.041198 | -0.2243 | -0.16022 | -0.23346 | -0.064087 | 0.37537
238.5781 | 122.9141 | -60.6949 | 61.8622 | -0.020708 | 0.0053508 | 0.0024617 | -0.00098673 | 0.063507 | -0.0020141 | 0.067332 | -60.7544 | 61.7798 | -60.9192 | -60.6628 | 61.4685 | -0.013733 | -0.036621 | 0.33417 | 61.8301 | -60.9283 | -0.2243 | -0.082398 | -0.05951 | 0.032043 | 0.2655 | -0.39368 | -0.36163 | -0.23346 | -0.032044 | 0.16479
239.5781 | 122.7814 | -60.6812 | 61.8393 | 0.0098091 | 0.005778 | 0.0013935 | 0.0015767 | 0.062225 | -0.0011597 | 0.069041 | -60.7407 | 61.7889 | -60.9467 | -60.8459 | 61.6699 | 0.17395 | -0.036621 | 0.5722 | 61.853 | -60.8917 | -0.2655 | -0.050354 | -0.05951 | -0.1648 | 0.045777 | -0.16937 | -0.1831 | -0.21057 | 0.013733 | 0.20599
240.5781 | 122.8088 | -60.7086 | 61.908 | -0.058855 | 0.0064188 | 0.0031025 | 0.0017903 | 0.060516 | -0.0015869 | 0.067759 | -60.791 | 61.8256 | -60.9604 | -60.91 | 61.5875 | 0.082397 | 0.10071 | 0.20599 | 61.8347 | -60.9924 | -0.25177 | -0.082397 | -0.082398 | -0.20142 | 0.082398 | -0.32043 | -0.24719 | -0.28381 | -0.073242 | 0.16937
241.5781 | 122.85 | -60.6903 | 61.8713 | 0.78801 | 0.0072734 | 0.0041707 | 0.0024313 | 0.063934 | -0.0030823 | 0.067973 | -60.7681 | 61.7706 | -60.9512 | -60.8414 | 61.6562 | 0.17395 | -0.022888 | 0.2655 | 61.8393 | -60.9512 | -0.26093 | -0.10071 | -0.077819 | -0.15106 | 0.10986 | -0.21515 | -0.18311 | -0.26093 | -0.032044 | 0.18311
242.5781 | 122.8638 | -60.6766 | 61.8851 | -0.074114 | 0.0070598 | 0.0024617 | 0.0017903 | 0.062012 | -0.0032959 | 0.065196 | -60.7727 | 61.8073 | -60.9375 | -60.8459 | 61.615 | 0.13733 | 0.064087 | 0.22888 | 61.8439 | -60.965 | -0.26093 | -0.07782 | -0.09613 | -0.16937 | 0.11902 | -0.27008 | -0.22888 | -0.28839 | -0.041199 | 0.16479
243.5781 | 122.8775 | -60.6949 | 61.8347 | -0.066485 | 0.0085552 | 0.0065205 | 0.00072227 | 0.062652 | -0.0062867 | 0.065837 | -60.7452 | 61.7706 | -60.9604 | -60.672 | 61.4822 | -0.013733 | -0.054932 | 0.32959 | 61.7844 | -60.9329 | -0.2655 | -0.064087 | -0.050354 | 0.022888 | 0.26093 | -0.35248 | -0.30212 | -0.23804 | -0.050354 | 0.21515
244.5781 | 122.937 | -60.6674 | 61.8896 | -0.0054494 | 0.005778 | 0.0033161 | 8.1267e-05 | 0.061798 | -0.0018005 | 0.0684 | -60.7407 | 61.7615 | -60.9467 | -60.8276 | 61.6653 | 0.16479 | -0.050354 | 0.28381 | 61.7889 | -60.9238 | -0.27924 | -0.12817 | -0.073243 | -0.16022 | 0.09613 | -0.2243 | -0.1236 | -0.25635 | -0.10071 | 0.20599
245.5781 | 122.937 | -60.6903 | 61.8759 | 0.070845 | 0.0059916 | 0.0056661 | 0.0013631 | 0.060516 | 0.0003357 | 0.067759 | -60.7452 | 61.7615 | -60.9329 | -60.8093 | 61.6745 | 0.16479 | -0.041199 | 0.27924 | 61.7844 | -60.9055 | -0.24261 | -0.11444 | -0.054931 | -0.11902 | 0.096131 | -0.20142 | -0.10986 | -0.21515 | -0.091553 | 0.18768
246.5781 | 122.9095 | -60.6857 | 61.8668 | 0.086103 | 0.0072734 | 0.0063069 | -0.00098673 | 0.062225 | -0.0018005 | 0.066264 | -60.7361 | 61.7569 | -60.9375 | -60.8185 | 61.6928 | 0.17395 | -0.086975 | 0.27466 | 61.7981 | -60.9467 | -0.25177 | -0.10986 | -0.050354 | -0.13275 | 0.12817 | -0.17395 | -0.10529 | -0.26093 | -0.068664 | 0.20142
247.5781 | 122.905 | -60.6857 | 61.8576 | -0.035967 | 0.0051372 | 0.0018209 | 0.0034993 | 0.062866 | -0.0009461 | 0.067973 | -60.8093 | 61.7889 | -60.9283 | -60.7681 | 61.6287 | 0.11902 | -0.045776 | 0.26093 | 61.7981 | -60.9421 | -0.24262 | -0.068665 | -0.1236 | -0.082397 | 0.17395 | -0.22888 | -0.16937 | -0.25635 | -0.059509 | 0.11902
248.5781 | 122.8729 | -60.6857 | 61.821 | -0.013079 | 0.0059916 | 0.0022481 | 0.0011495 | 0.064148 | -0.0007325 | 0.065837 | -60.7315 | 61.7935 | -60.91 | -60.6171 | 61.9171 | 0.3067 | -0.32501 | 0.21057 | 61.7981 | -60.9329 | -0.2243 | -0.027466 | -0.045776 | 0.068665 | 0.31586 | 0.09613 | 0.11902 | -0.24719 | -0.022888 | 0.17853
249.5781 | 122.937 | -60.6766 | 61.9125 | 0.0021796 | 0.0066326 | 0.0069477 | -0.00013233 | 0.065216 | -0.0026551 | 0.066691 | -60.7269 | 61.7523 | -60.9421 | -60.7956 | 61.6653 | 0.1831 | -0.032043 | 0.28381 | 61.7935 | -60.9283 | -0.2655 | -0.16022 | -0.050354 | -0.11902 | 0.13275 | -0.24719 | -0.12817 | -0.25177 | -0.11902 | 0.21515
250.5781 | 122.9004 | -60.6812 | 61.853 | 0.078474 | 0.0053508 | 0.0022481 | -0.00055953 | 0.059875 | -0.0009461 | 0.066905 | -60.7498 | 61.7661 | -60.9283 | -60.8139 | 61.6837 | 0.17853 | -0.050354 | 0.29297 | 61.7798 | -60.9009 | -0.24719 | -0.086975 | -0.068665 | -0.13275 | 0.086975 | -0.16937 | -0.09613 | -0.21973 | -0.073242 | 0.17853
251.5781 | 122.8867 | -60.7224 | 61.8759 | 0.20054 | 0.005778 | 0.0043843 | -0.0026957 | 0.062012 | -0.0018005 | 0.068187 | -60.8139 | 61.7752 | -60.9467 | -60.8597 | 61.6104 | 0.12817 | -0.068665 | 0.2243 | 61.7935 | -60.9283 | -0.2243 | -0.10071 | -0.091553 | -0.13733 | 0.068665 | -0.2655 | -0.1831 | -0.20599 | -0.082398 | 0.13275
252.5781 | 122.937 | -60.6766 | 61.8713 | -0.0054494 | 0.0059916 | 0.0028889 | 0.0013631 | 0.059875 | -0.0005189 | 0.067759 | -60.7681 | 61.7661 | -60.9467 | -60.8139 | 61.6653 | 0.17853 | -0.091553 | 0.28839 | 61.7889 | -60.9329 | -0.27008 | -0.10529 | -0.091552 | -0.13733 | 0.11902 | -0.20599 | -0.1236 | -0.25635 | -0.082398 | 0.17853
253.5781 | 122.8912 | -60.6949 | 61.8576 | 0.11662 | 0.0068462 | -0.00052906 | -0.00077313 | 0.060089 | -0.0022277 | 0.069896 | -60.7681 | 61.7477 | -60.9421 | -60.8276 | 61.6608 | 0.15106 | -0.091553 | 0.25635 | 61.7752 | -60.9146 | -0.24719 | -0.10986 | -0.073242 | -0.13275 | 0.086975 | -0.19684 | -0.11444 | -0.21973 | -0.082397 | 0.17395
254.5781 | 122.9462 | -60.7132 | 61.8668 | 0.025068 | 0.0064188 | 0.010366 | 0.0011495 | 0.062225 | -0.0007325 | 0.066905 | -60.7544 | 61.7615 | -60.9604 | -60.7956 | 61.5692 | 0.3067 | 0.23346 | 0.027466 | 61.8439 | -60.9238 | -0.24719 | -0.10529 | -0.041199 | -0.082397 | 0.12817 | -0.29755 | -0.27466 | -0.21057 | -0.022888 | 0.20599
255.5781 | 122.9095 | -60.6628 | 61.9492 | 0.032698 | 0.004069 | 0.0045979 | 0.00029507 | 0.062439 | -0.0026551 | 0.067973 | -60.7361 | 61.7798 | -60.9375 | -60.7956 | 61.6699 | 0.17395 | -0.045776 | 0.27008 | 61.8073 | -60.9146 | -0.27466 | -0.16937 | -0.073242 | -0.13275 | 0.11902 | -0.27924 | -0.13733 | -0.25177 | -0.14191 | 0.20142
256.5781 | 122.9416 | -60.6812 | 61.853 | 0.040327 | 0.0032146 | -0.00010166 | 0.0017903 | 0.061798 | -0.0035095 | 0.067759 | -60.7315 | 61.7706 | -60.9192 | -60.8139 | 61.6791 | 0.17395 | -0.045776 | 0.29297 | 61.7752 | -60.91 | -0.23804 | -0.082397 | -0.050354 | -0.13275 | 0.09613 | -0.17395 | -0.096131 | -0.22888 | -0.077819 | 0.18768
257.5781 | 122.9279 | -60.672 | 61.8393 | 0.063215 | 0.0064188 | 0.0039571 | -0.0016275 | 0.062225 | -0.0009461 | 0.066264 | -60.7681 | 61.7661 | -60.9467 | -60.7864 | 61.6974 | 0.17395 | -0.032043 | 0.27924 | 61.7844 | -60.9192 | -0.27466 | -0.073242 | -0.09613 | -0.11444 | 0.13275 | -0.14191 | -0.086975 | -0.24719 | -0.054931 | 0.17853
258.5781 | 122.7951 | -60.7178 | 61.8988 | 0.13951 | 0.0089824 | 0.010366 | 0.0077719 | 0.06543 | 0.0003357 | 0.067546 | -60.7681 | 61.8896 | -60.9467 | -60.8734 | 61.5875 | 0.059509 | 0.009155 | 0.14648 | 61.8301 | -61.0016 | -0.22888 | -0.009156 | -0.050354 | -0.15564 | 0.12817 | -0.31128 | -0.24262 | -0.28381 | -0.068665 | 0.17853
259.5781 | 122.9416 | -60.6857 | 61.8896 | 0.032698 | 0.0081278 | 0.0071615 | -0.0016275 | 0.064148 | -0.0007325 | 0.064555 | -60.7544 | 61.7752 | -60.9467 | -60.8185 | 61.6791 | 0.17395 | -0.07782 | 0.28839 | 61.7798 | -60.8963 | -0.26093 | -0.11444 | -0.068665 | -0.13275 | 0.07782 | -0.21057 | -0.10071 | -0.21057 | -0.10986 | 0.19226
260.5781 | 122.9095 | -60.6903 | 61.853 | -0.066485 | 0.0025736 | 0.00096634 | -0.0020549 | 0.058594 | -0.0022277 | 0.069041 | -60.759 | 61.7706 | -60.9375 | -61.0336 | 61.5097 | 0.16479 | 0 | 0.19226 | 61.7706 | -60.9375 | -0.24719 | -0.082397 | -0.068664 | -0.34332 | -0.09613 | -0.34332 | -0.26093 | -0.24719 | -0.082397 | 0.17853
261.5781 | 122.9324 | -60.6674 | 61.8484 | 0.025068 | 0.0072734 | 0.0037435 | 0.00029507 | 0.061798 | -0.0015869 | 0.068827 | -60.7681 | 61.7889 | -60.9329 | -60.7361 | 61.9217 | 0.45776 | -0.30212 | 0.10986 | 61.8027 | -60.9375 | -0.2655 | -0.05951 | -0.10071 | -0.068665 | 0.20142 | 0.073242 | 0.11902 | -0.27008 | -0.045777 | 0.16479
262.5781 | 122.7951 | -60.6903 | 61.8576 | -0.043596 | 0.0032146 | 0.0013935 | -0.00013233 | 0.061584 | -0.0030823 | 0.069255 | -60.7636 | 61.8027 | -60.9283 | -60.8276 | 61.6837 | 0.18768 | 0.18768 | 0.53101 | 61.8393 | -60.8963 | -0.23804 | -0.054932 | -0.073242 | -0.13733 | 0.068664 | -0.17395 | -0.15564 | -0.20599 | -0.018311 | 0.16479
263.5781 | 122.9782 | -60.6445 | 61.9034 | 0.025068 | 0.0055644 | 0.0028889 | 0.00093587 | 0.062439 | -0.0013733 | 0.065623 | -60.7544 | 61.7798 | -60.9238 | -60.8276 | 61.6699 | 0.18768 | -0.027466 | 0.28839 | 61.7981 | -60.9009 | -0.27924 | -0.1236 | -0.10986 | -0.18311 | 0.073242 | -0.23346 | -0.12817 | -0.25635 | -0.10529 | 0.16937
264.5781 | 122.8592 | -60.6491 | 61.8942 | 0.0098091 | 0.0068462 | 0.0013935 | 0.00029507 | 0.062012 | -0.0020141 | 0.064555 | -60.7544 | 61.7706 | -60.9375 | -60.8231 | 61.6791 | 0.18768 | -0.036621 | 0.28839 | 61.7798 | -60.9146 | -0.28839 | -0.1236 | -0.10529 | -0.17395 | 0.091553 | -0.21515 | -0.10071 | -0.2655 | -0.11444 | 0.1831
265.5781 | 122.905 | -60.704 | 61.8439 | 0.10899 | 0.0059916 | 0.0045979 | 0.0030721 | 0.062439 | -0.0024415 | 0.067546 | -60.7864 | 61.7615 | -60.9467 | -60.8505 | 61.6516 | 0.15564 | -0.073242 | 0.22888 | 61.7798 | -60.9192 | -0.24261 | -0.082397 | -0.082397 | -0.14648 | 0.068664 | -0.19226 | -0.12817 | -0.21515 | -0.064087 | 0.16022
266.5781 | 122.9233 | -60.6949 | 61.8622 | 0.017439 | 0.0053508 | 0.0037435 | 0.00093587 | 0.061584 | -0.0009461 | 0.068827 | -60.7407 | 61.7935 | -60.9421 | -60.8047 | 61.6882 | 0.19226 | -0.045776 | 0.28381 | 61.7844 | -60.9238 | -0.24719 | -0.068665 | -0.045777 | -0.10986 | 0.11902 | -0.17395 | -0.096131 | -0.22888 | -0.07782 | 0.20142
267.5781 | 122.8546 | -60.6995 | 61.8759 | -0.10463 | 0.0064188 | 0.0048115 | 0.0026449 | 0.060944 | -0.0020141 | 0.064982 | -60.7819 | 61.7935 | -60.9512 | -60.8231 | 61.6516 | 0.17853 | -0.009155 | 0.2655 | 61.7661 | -60.9329 | -0.25177 | -0.082398 | -0.082397 | -0.1236 | 0.10986 | -0.2243 | -0.11444 | -0.23346 | -0.10986 | 0.16937
268.5781 | 122.905 | -60.7132 | 61.8713 | 0.055586 | 0.0044962 | 0.0022481 | 0.00093587 | 0.062439 | -0.0022277 | 0.068827 | -60.7498 | 61.7752 | -60.9421 | -60.8047 | 61.6882 | 0.19684 | -0.032043 | 0.29297 | 61.7935 | -60.9283 | -0.22888 | -0.09613 | -0.036621 | -0.091553 | 0.1236 | -0.18311 | -0.10529 | -0.21515 | -0.07782 | 0.19226
269.5781 | 122.9095 | -60.6857 | 61.8713 | 0.093733 | 0.005778 | 0.0035299 | 0.0024313 | 0.063293 | -0.0005189 | 0.067759 | -60.7452 | 61.7523 | -60.9375 | -60.7956 | 61.6928 | 0.18768 | -0.041199 | 0.27924 | 61.7889 | -60.9055 | -0.25177 | -0.11902 | -0.059509 | -0.10986 | 0.10986 | -0.17853 | -0.09613 | -0.21973 | -0.082398 | 0.19226
270.5781 | 122.937 | -60.672 | 61.8759 | 0.070845 | 0.0062052 | 0.0041707 | 0.0011495 | 0.061584 | 0.0007629 | 0.067118 | -60.7544 | 61.7706 | -60.9329 | -60.8185 | 61.6882 | 0.17853 | -0.045776 | 0.27924 | 61.7706 | -60.91 | -0.26093 | -0.10529 | -0.082398 | -0.14648 | 0.091553 | -0.18768 | -0.082398 | -0.23804 | -0.10529 | 0.17853
271.5781 | 122.9645 | -60.6766 | 61.8668 | 0.093733 | 0.0064188 | 0.0056661 | 0.0020039 | 0.060944 | -0.0013733 | 0.064982 | -60.7636 | 61.7523 | -60.9421 | -60.7956 | 61.6745 | 0.20142 | -0.091553 | 0.28839 | 61.7661 | -60.9146 | -0.2655 | -0.11444 | -0.086975 | -0.11902 | 0.11902 | -0.19226 | -0.091552 | -0.23804 | -0.10071 | 0.17853
272.5781 | 122.9141 | -60.6857 | 61.8713 | 0.10136 | 0.0077006 | 0.0048115 | -0.0018413 | 0.060303 | -0.0013733 | 0.067332 | -60.7636 | 61.7798 | -60.9558 | -60.8047 | 61.6928 | 0.18768 | -0.07782 | 0.28839 | 61.7615 | -60.8963 | -0.27008 | -0.091553 | -0.07782 | -0.11902 | 0.091552 | -0.17853 | -0.068665 | -0.21057 | -0.10986 | 0.19226
273.5781 | 122.9553 | -60.6537 | 61.853 | 0.10136 | 0.0085552 | 0.0033161 | 0.00029507 | 0.06073 | -9.1495e-05 | 0.067759 | -60.7498 | 61.7798 | -60.9375 | -60.8139 | 61.6745 | 0.17853 | -0.086975 | 0.27924 | 61.7615 | -60.9009 | -0.28381 | -0.073242 | -0.09613 | -0.16022 | 0.086975 | -0.17853 | -0.086975 | -0.24719 | -0.091552 | 0.18768
274.5781 | 122.8821 | -60.6995 | 61.8759 | 0.047956 | 0.0051372 | 0.0048115 | -0.0037639 | 0.059875 | 0.0009765 | 0.07075 | -60.7636 | 61.7889 | -60.9512 | -60.9924 | 61.6562 | 0.23804 | -0.082397 | 0.23346 | 61.7706 | -60.9009 | -0.25177 | -0.086976 | -0.064087 | -0.29297 | -0.091553 | -0.21973 | -0.11444 | -0.20142 | -0.10529 | 0.18768
275.5781 | 122.8775 | -60.6857 | 61.8759 | -0.0054494 | 0.0055644 | 0.0028889 | 0.00029507 | 0.059235 | -0.0007325 | 0.068614 | -60.7636 | 61.7981 | -60.9467 | -60.8414 | 61.6516 | 0.16937 | 0.022888 | 0.24261 | 61.821 | -60.9283 | -0.26093 | -0.07782 | -0.07782 | -0.15564 | 0.086975 | -0.2243 | -0.16937 | -0.24262 | -0.054932 | 0.1831
276.5781 | 122.8363 | -60.6949 | 61.8668 | 0.0021796 | 0.0055644 | 0.0041707 | 0.0011495 | 0.061584 | -0.0028687 | 0.067332 | -60.759 | 61.8073 | -60.9375 | -60.8322 | 61.6653 | 0.18768 | 0 | 0.25635 | 61.7935 | -60.9375 | -0.24262 | -0.059509 | -0.064087 | -0.13733 | 0.10529 | -0.20142 | -0.12817 | -0.24262 | -0.073242 | 0.17853
277.5781 | 122.8638 | -60.6903 | 61.8668 | 0.17766 | 0.0072734 | 0.0043843 | 0.00093587 | 0.062652 | -0.0028687 | 0.067759 | -60.7544 | 61.7798 | -60.9375 | -60.8551 | 61.6608 | 0.19684 | -0.022888 | 0.27924 | 61.8027 | -60.9055 | -0.24719 | -0.086975 | -0.064087 | -0.16479 | 0.050354 | -0.20599 | -0.14191 | -0.21515 | -0.064087 | 0.1831
278.5781 | 122.8867 | -60.6857 | 61.8484 | -0.66158 | 0.0051372 | 0.0045979 | 0.0024313 | 0.062225 | -0.0005189 | 0.066691 | -60.7407 | 61.7844 | -60.9375 | -60.8093 | 61.6699 | 0.18768 | -0.027466 | 0.26093 | 61.821 | -60.9375 | -0.25177 | -0.064087 | -0.054932 | -0.1236 | 0.12817 | -0.17853 | -0.15106 | -0.25177 | -0.027466 | 0.19684
279.5781 | 122.9095 | -60.6857 | 61.8439 | 0.070845 | 0.00471 | 0.0048115 | 8.1267e-05 | 0.063721 | -0.0026551 | 0.068614 | -60.7681 | 61.7615 | -60.9467 | -60.8322 | 61.6653 | 0.19226 | -0.082397 | 0.28839 | 61.7981 | -60.9055 | -0.26093 | -0.082397 | -0.082397 | -0.14648 | 0.073243 | -0.17853 | -0.13275 | -0.21973 | -0.045776 | 0.17853
280.5781 | 122.9141 | -60.6903 | 61.8713 | -0.028338 | 0.0055644 | 0.00075274 | 0.0015767 | 0.059875 | -0.0007325 | 0.067546 | -60.7452 | 61.7706 | -60.9238 | -60.7636 | 61.94 | 0.46692 | -0.28839 | 0.09613 | 61.7798 | -60.9146 | -0.23346 | -0.10071 | -0.054931 | -0.073242 | 0.15106 | 0.068664 | 0.16022 | -0.2243 | -0.091553 | 0.17853
281.5781 | 122.7905 | -60.7361 | 61.9125 | -0.058855 | 0.0064188 | 0.0078023 | 0.0041403 | 0.062866 | -0.0024415 | 0.070323 | -60.7956 | 61.8256 | -60.9558 | -60.8963 | 61.5784 | 0.10986 | 0.12817 | 0.20599 | 61.8393 | -60.9238 | -0.21973 | -0.086975 | -0.059509 | -0.16022 | 0.027466 | -0.33417 | -0.26093 | -0.18768 | -0.073243 | 0.16022
282.5781 | 122.9141 | -60.6995 | 61.8851 | -0.65395 | 0.0077006 | 0.0041707 | 8.1267e-05 | 0.062439 | -0.0020141 | 0.067546 | -60.7452 | 61.7935 | -60.9283 | -60.8139 | 61.6791 | 0.19684 | -0.022888 | 0.28839 | 61.8073 | -60.9192 | -0.22888 | -0.091553 | -0.045776 | -0.11444 | 0.10529 | -0.20599 | -0.12817 | -0.21973 | -0.07782 | 0.18311
283.5781 | 122.9004 | -60.6766 | 61.8622 | -0.013079 | 0.0051372 | 0.0026753 | -0.0050455 | 0.060516 | -0.0024415 | 0.069041 | -60.7407 | 61.8027 | -60.9467 | -61.0153 | 61.5646 | 0.22888 | -0.036621 | 0.20142 | 61.7889 | -60.9192 | -0.27008 | -0.05951 | -0.064087 | -0.33875 | -0.096131 | -0.29755 | -0.2243 | -0.24261 | -0.073243 | 0.20599
284.5781 | 122.9095 | -60.6628 | 61.908 | 0.025068 | 0.0064188 | 0.0031025 | -0.00098673 | 0.060089 | -0.0015869 | 0.069682 | -60.7361 | 61.7844 | -60.9283 | -60.8047 | 61.6791 | 0.21515 | -0.050354 | 0.28381 | 61.7844 | -60.9146 | -0.2655 | -0.1236 | -0.073242 | -0.14191 | 0.10986 | -0.22888 | -0.10529 | -0.25177 | -0.1236 | 0.19226
285.5781 | 122.9004 | -60.6903 | 61.8759 | 0.093733 | 0.0062052 | 0.0018209 | -0.00055953 | 0.062652 | -0.0039367 | 0.069468 | -60.7636 | 61.7706 | -60.965 | -60.8093 | 61.6882 | 0.21057 | -0.082397 | 0.29297 | 61.8118 | -60.9192 | -0.27466 | -0.10529 | -0.073242 | -0.11902 | 0.10986 | -0.18768 | -0.1236 | -0.22888 | -0.064087 | 0.20142
286.5781 | 122.8409 | -60.6949 | 61.8668 | 0.20817 | 0.0042826 | 0.0028889 | 0.00072227 | 0.06073 | -0.0013733 | 0.068827 | -60.8231 | 61.7569 | -60.9604 | -60.9055 | 61.6196 | 0.11902 | -0.054932 | 0.18768 | 61.7844 | -60.9329 | -0.2655 | -0.10986 | -0.12817 | -0.21057 | 0.027465 | -0.24719 | -0.16479 | -0.23804 | -0.082397 | 0.13733
287.5781 | 122.9187 | -60.6903 | 61.8484 | 0.15477 | 0.0038554 | 0.0037435 | -0.0018413 | 0.059448 | -9.1495e-05 | 0.067546 | -60.7956 | 61.7706 | -60.9421 | -60.8414 | 61.6425 | 0.19684 | -0.068665 | 0.23804 | 61.7706 | -60.9238 | -0.25177 | -0.07782 | -0.10528 | -0.15106 | 0.082397 | -0.20599 | -0.12817 | -0.23346 | -0.07782 | 0.14649
288.5781 | 122.8867 | -60.6812 | 61.8668 | 0.11662 | 0.0044962 | -0.00031526 | 0.0017903 | 0.057953 | 0.0014039 | 0.069468 | -60.7727 | 61.7935 | -60.9375 | -60.8185 | 61.6791 | 0.2243 | -0.07782 | 0.28381 | 61.7569 | -60.9192 | -0.25635 | -0.073242 | -0.091553 | -0.13733 | 0.10071 | -0.18768 | -0.07782 | -0.23804 | -0.10986 | 0.16479
289.5781 | 122.905 | -60.6583 | 61.853 | 0.10899 | 0.0042826 | 0.0052387 | 0.00093587 | 0.062225 | -0.0003051 | 0.066691 | -60.7727 | 61.7889 | -60.9283 | -60.8368 | 61.6608 | 0.20599 | -0.073242 | 0.24719 | 61.7981 | -60.9238 | -0.27008 | -0.064087 | -0.11444 | -0.17853 | 0.086975 | -0.19226 | -0.13733 | -0.2655 | -0.054931 | 0.15564
290.5781 | 122.8638 | -60.6857 | 61.8484 | 0.15477 | 0.0064188 | -0.00052906 | 8.1267e-05 | 0.062652 | -0.0018005 | 0.067759 | -60.7864 | 61.7661 | -60.9512 | -60.8459 | 61.647 | 0.17853 | -0.086975 | 0.24719 | 61.7661 | -60.9146 | -0.2655 | -0.082398 | -0.10071 | -0.16022 | 0.068665 | -0.20142 | -0.11902 | -0.22888 | -0.082398 | 0.1648
291.5781 | 122.8912 | -60.6857 | 61.8576 | 0.13951 | 0.005778 | 0.0045979 | 0.00050867 | 0.062439 | -0.0020141 | 0.068614 | -60.8185 | 61.7752 | -60.9421 | -60.8597 | 61.6425 | 0.14648 | -0.064087 | 0.21057 | 61.7752 | -60.9283 | -0.25635 | -0.082397 | -0.13275 | -0.17395 | 0.068665 | -0.21515 | -0.13275 | -0.24262 | -0.082397 | 0.1236
292.5781 | 122.9004 | -60.704 | 61.8668 | 0.23106 | 0.0051372 | 0.0022481 | -0.0012003 | 0.061584 | -0.0013733 | 0.067332 | -60.8322 | 61.7523 | -60.9558 | -60.8643 | 61.6013 | 0.13275 | -0.054932 | 0.18768 | 61.7844 | -60.9283 | -0.25177 | -0.11444 | -0.12817 | -0.16022 | 0.064087 | -0.2655 | -0.18311 | -0.2243 | -0.082397 | 0.1236
293.5781 | 122.8363 | -60.6995 | 61.853 | 0.25395 | 0.0077006 | 0.0028889 | -0.00034593 | 0.061157 | -0.0007325 | 0.068827 | -60.8414 | 61.7706 | -60.9329 | -60.8871 | 61.6013 | 0.11902 | -0.045776 | 0.15106 | 61.7706 | -60.9421 | -0.23346 | -0.082397 | -0.14191 | -0.18768 | 0.054932 | -0.25177 | -0.16937 | -0.24262 | -0.082397 | 0.091552
294.5781 | 122.8683 | -60.6949 | 61.8622 | 0.19291 | 0.0051372 | 0.0071615 | 8.1267e-05 | 0.059662 | 0.0009765 | 0.066691 | -60.8459 | 61.7889 | -60.9558 | -60.9009 | 61.6013 | 0.09613 | -0.059509 | 0.16479 | 61.7615 | -60.9329 | -0.26093 | -0.073243 | -0.15106 | -0.20599 | 0.032043 | -0.26093 | -0.16022 | -0.23804 | -0.10071 | 0.10986
295.5781 | 122.8683 | -60.6903 | 61.853 | 0.22343 | 0.00471 | 0.0026753 | -0.0022685 | 0.060303 | -0.0005189 | 0.067546 | -60.8322 | 61.7615 | -60.9558 | -60.8688 | 61.6104 | 0.13275 | -0.07782 | 0.17853 | 61.7844 | -60.9467 | -0.2655 | -0.091552 | -0.14191 | -0.17853 | 0.07782 | -0.24261 | -0.17395 | -0.25635 | -0.068664 | 0.1236
296.5781 | 122.8912 | -60.7086 | 61.8713 | 0.0021796 | 0.0077006 | 0.0050251 | -0.0026957 | 0.060303 | -0.0013733 | 0.0684 | -60.8597 | 61.7523 | -60.9695 | -60.9146 | 61.5875 | 0.12817 | -0.082397 | 0.15106 | 61.7752 | -60.9512 | -0.26093 | -0.11902 | -0.15106 | -0.20599 | 0.036621 | -0.28381 | -0.18768 | -0.24262 | -0.09613 | 0.10986
297.5781 | 122.8134 | -60.704 | 61.8622 | 0.23106 | 0.0068462 | 0.0024617 | -0.00098673 | 0.055817 | -0.0005189 | 0.066905 | -60.8414 | 61.7706 | -60.9558 | -60.9467 | 61.5692 | 0.09613 | -0.045776 | 0.13733 | 61.7844 | -60.9283 | -0.25177 | -0.091553 | -0.13733 | -0.24261 | -0.01831 | -0.29297 | -0.21515 | -0.2243 | -0.07782 | 0.11444
298.5781 | 122.8363 | -60.6903 | 61.8576 | 0.23869 | 0.0066326 | 0.0037435 | 0.00050867 | 0.060303 | -0.0003051 | 0.067973 | -60.8414 | 61.7889 | -60.9604 | -60.9238 | 61.5967 | 0.11444 | -0.054932 | 0.14191 | 61.7752 | -60.9558 | -0.27008 | -0.068665 | -0.15106 | -0.23346 | 0.032044 | -0.26093 | -0.17853 | -0.2655 | -0.082397 | 0.11902
299.5781 | 122.8638 | -60.6857 | 61.853 | 0.39128 | 0.0055644 | 0.0018209 | 8.1267e-05 | 0.06073 | -0.0003051 | 0.066691 | -60.8414 | 61.7615 | -60.9787 | -60.9238 | 61.5738 | 0.10529 | -0.07782 | 0.11902 | 61.7569 | -60.9375 | -0.29297 | -0.091552 | -0.15564 | -0.23804 | 0.013733 | -0.27923 | -0.18311 | -0.25177 | -0.09613 | 0.13733
300.5781 | 122.8409 | -60.7086 | 61.8805 | 0.32261 | 0.0044962 | 0.0039571 | -0.00098673 | 0.059662 | -0.0005189 | 0.067118 | -60.8322 | 61.7706 | -60.9558 | -60.91 | 61.5921 | 0.09613 | -0.07782 | 0.13275 | 61.7569 | -60.9558 | -0.24719 | -0.10986 | -0.1236 | -0.20142 | 0.045777 | -0.28839 | -0.1648 | -0.24719 | -0.1236 | 0.1236
301.5781 | 122.8683 | -60.7178 | 61.8439 | 0.33787 | 0.0079142 | 0.0050251 | 0.0011495 | 0.06073 | 0.0001221 | 0.067759 | -60.8276 | 61.7477 | -60.9604 | -60.8963 | 61.5875 | 0.091553 | -0.10986 | 0.10986 | 61.7798 | -60.9421 | -0.24262 | -0.09613 | -0.10986 | -0.17853 | 0.045777 | -0.25635 | -0.19226 | -0.22431 | -0.064087 | 0.13275
302.5781 | 122.8363 | -60.6766 | 61.8393 | 0.26158 | 0.0077006 | 0.0050251 | -0.00034593 | 0.059235 | 0.0005493 | 0.066691 | -60.8368 | 61.7661 | -60.965 | -60.9055 | 61.5921 | 0.10986 | -0.068665 | 0.12817 | 61.7798 | -60.9558 | -0.28839 | -0.073242 | -0.16022 | -0.22888 | 0.050354 | -0.24719 | -0.18768 | -0.27924 | -0.059509 | 0.12817
303.5781 | 122.8821 | -60.6949 | 61.8347 | 0.3455 | 0.00471 | 0.0039571 | -0.0014139 | 0.060944 | -0.0015869 | 0.067118 | -60.8551 | 61.7752 | -60.965 | -60.9192 | 61.5967 | 0.10071 | -0.07782 | 0.11902 | 61.7752 | -60.9604 | -0.27008 | -0.059509 | -0.16022 | -0.2243 | 0.041199 | -0.23804 | -0.17853 | -0.2655 | -0.059509 | 0.10986
304.5781 | 122.8317 | -60.704 | 61.8484 | 0.33787 | 0.005778 | 0.0054525 | 0.0020039 | 0.059875 | -9.1495e-05 | 0.067759 | -60.8414 | 61.7523 | -60.9558 | -60.9238 | 61.5784 | 0.07782 | -0.09613 | 0.10986 | 61.7706 | -60.9604 | -0.25177 | -0.096131 | -0.13733 | -0.21973 | 0.036621 | -0.27008 | -0.19226 | -0.25635 | -0.07782 | 0.11444
305.5781 | 122.8592 | -60.7086 | 61.8347 | 0.39891 | 0.007487 | 0.0037435 | -0.00034593 | 0.060089 | -0.0007325 | 0.0684 | -60.8276 | 61.7706 | -60.9741 | -60.8871 | 61.5738 | 0.10529 | -0.1236 | 0.11444 | 61.7752 | -60.965 | -0.2655 | -0.064087 | -0.11902 | -0.17853 | 0.07782 | -0.26093 | -0.20142 | -0.25635 | -0.059509 | 0.14648
306.5781 | 122.8455 | -60.7178 | 61.8484 | 0.35313 | 0.0083416 | 0.0054525 | 0.0013631 | 0.062439 | -0.0013733 | 0.069468 | -60.791 | 61.7661 | -60.965 | -60.8917 | 61.6013 | 0.11902 | -0.14191 | 0.13733 | 61.7432 | -60.9558 | -0.24719 | -0.082398 | -0.073243 | -0.17395 | 0.064087 | -0.24719 | -0.14191 | -0.23804 | -0.10529 | 0.17395
307.5781 | 122.8409 | -60.7269 | 61.8256 | 0.32261 | 0.0059916 | 0.0033161 | 0.0039267 | 0.062225 | -9.1495e-05 | 0.067973 | -60.7956 | 61.7706 | -60.9375 | -60.8688 | 61.6058 | 0.13275 | -0.15564 | 0.12817 | 61.7569 | -60.9558 | -0.21057 | -0.054932 | -0.068664 | -0.14191 | 0.086976 | -0.21973 | -0.15106 | -0.22888 | -0.068665 | 0.14191
308.5781 | 122.8134 | -60.6903 | 61.8942 | -0.028338 | 0.0064188 | 0.0048115 | 0.0022177 | 0.060089 | -9.1495e-05 | 0.066264 | -60.7773 | 61.8164 | -60.9467 | -60.8459 | 61.6425 | 0.21515 | 0.064087 | 0.23346 | 61.7981 | -60.965 | -0.25635 | -0.07782 | -0.086975 | -0.15564 | 0.11902 | -0.25177 | -0.15564 | -0.27466 | -0.09613 | 0.16937
309.5781 | 122.85 | -60.6857 | 61.8576 | 0.26921 | 0.0098368 | 0.0020345 | 0.0013631 | 0.061371 | -0.0005189 | 0.067546 | -60.8276 | 61.7706 | -60.9695 | -60.91 | 61.5875 | 0.11902 | -0.054932 | 0.1236 | 61.7844 | -60.9238 | -0.28381 | -0.086975 | -0.14191 | -0.2243 | 0.013733 | -0.27008 | -0.19684 | -0.23804 | -0.073242 | 0.14191
310.5781 | 122.9279 | -60.704 | 61.8256 | 0.4218 | 0.0066326 | 0.0060933 | 0.0047811 | 0.064575 | -0.0035095 | 0.065837 | -60.9283 | 61.7523 | -60.9833 | -60.8414 | 61.6241 | 0.16022 | -0.15106 | 0.13733 | 61.7844 | -60.965 | -0.27923 | -0.073243 | -0.2243 | -0.13733 | 0.1236 | -0.20142 | -0.16022 | -0.26093 | -0.041199 | 0.054931
311.5781 | 122.8592 | -60.6949 | 61.853 | 0.4752 | 0.0070598 | 0.0069477 | 0.0039267 | 0.066498 | -0.0009461 | 0.067759 | -60.7773 | 61.8027 | -60.9604 | -60.7224 | 61.7798 | 0.21515 | -0.24261 | 0.16937 | 61.7615 | -60.9604 | -0.2655 | -0.050354 | -0.082398 | -0.027466 | 0.23804 | -0.073242 | 0.01831 | -0.2655 | -0.091552 | 0.18311
312.5781 | 122.8683 | -60.7086 | 61.8347 | 0.41417 | 0.0098368 | 0.0063069 | 0.0037129 | 0.063721 | -0.0015869 | 0.066905 | -60.7773 | 61.7889 | -60.9604 | -60.8643 | 61.5463 | 0.009155 | -0.29297 | 0.32501 | 61.7249 | -60.9741 | -0.25177 | -0.045777 | -0.068665 | -0.15564 | 0.10986 | -0.28839 | -0.17853 | -0.2655 | -0.10986 | 0.18311
313.5781 | 122.9233 | -60.6812 | 61.8576 | 0.040327 | 0.0068462 | 0.0063069 | -0.0018413 | 0.060944 | -0.0022277 | 0.070323 | -60.7819 | 61.7706 | -60.9421 | -60.8093 | 61.6882 | 0.27466 | -0.07782 | 0.27924 | 61.7615 | -60.9283 | -0.26093 | -0.086975 | -0.10071 | -0.12817 | 0.11902 | -0.16937 | -0.073243 | -0.24719 | -0.09613 | 0.16022
314.5781 | 122.8683 | -60.7132 | 61.7981 | 0.42943 | 0.0083416 | 0.0052387 | 0.0064901 | 0.062012 | -0.0028687 | 0.068187 | -60.7681 | 61.7844 | -60.9604 | -60.8688 | 61.6196 | 0.14648 | -0.20599 | 0.12817 | 61.7569 | -60.9741 | -0.24719 | -0.013733 | -0.054931 | -0.15564 | 0.10529 | -0.17853 | -0.13733 | -0.26092 | -0.041199 | 0.19226
315.5781 | 122.8912 | -60.6857 | 61.8347 | 0.42943 | 0.005778 | 0.0095113 | 0.0015767 | 0.062652 | 0.0001221 | 0.068187 | -60.8047 | 61.7752 | -60.9558 | -60.8871 | 61.615 | 0.16022 | -0.17853 | 0.13733 | 61.7523 | -60.997 | -0.27008 | -0.059509 | -0.11902 | -0.20142 | 0.10986 | -0.21973 | -0.13733 | -0.31128 | -0.082398 | 0.15106
316.5781 | 122.8409 | -60.7132 | 61.8256 | 0.37602 | 0.0066326 | 0.0065205 | 0.00072227 | 0.061798 | 0.0001221 | 0.068187 | -60.8368 | 61.7661 | -60.965 | -60.9055 | 61.5875 | 0.13275 | -0.10529 | 0.10986 | 61.7661 | -60.9787 | -0.25177 | -0.05951 | -0.1236 | -0.19226 | 0.073242 | -0.23804 | -0.17853 | -0.2655 | -0.05951 | 0.12817
317.5781 | 122.8867 | -60.7452 | 61.8347 | 0.71171 | 0.0062052 | 0.0071615 | 0.0017903 | 0.063507 | -0.0030823 | 0.067759 | -60.7956 | 61.7935 | -60.9512 | -60.8734 | 61.6104 | 0.17853 | -0.16479 | 0.15106 | 61.7706 | -60.9558 | -0.20599 | -0.041199 | -0.050354 | -0.12817 | 0.082398 | -0.2243 | -0.16022 | -0.21057 | -0.064087 | 0.15564
318.5781 | 122.7859 | -60.7498 | 61.8484 | 0.26158 | 0.0085552 | 0.0054525 | 0.0062765 | 0.064575 | -0.0018005 | 0.065409 | -60.8459 | 61.8484 | -61.0107 | -60.9741 | 61.4868 | 0.073242 | 0.045776 | 0.041199 | 61.821 | -60.997 | -0.26093 | 0 | -0.09613 | -0.2243 | 0.022888 | -0.36163 | -0.33417 | -0.24719 | -0.027466 | 0.16479
319.5781 | 122.8821 | -60.704 | 61.8256 | 0.38365 | 0.0083416 | 0.0026753 | -0.0012003 | 0.062866 | -0.0026551 | 0.070536 | -60.791 | 61.7477 | -60.9421 | -60.9009 | 61.5875 | 0.15564 | -0.15106 | 0.1236 | 61.7661 | -60.9421 | -0.23804 | -0.07782 | -0.086975 | -0.19684 | 0.041199 | -0.23804 | -0.17853 | -0.23804 | -0.05951 | 0.15106
320.5781 | 122.8455 | -60.7132 | 61.8118 | 0.36076 | 0.0072734 | 0.0067341 | 0.0020039 | 0.062012 | -0.0013733 | 0.068827 | -60.7956 | 61.7844 | -60.9695 | -60.8963 | 61.5967 | 0.16937 | -0.15106 | 0.11902 | 61.7294 | -60.9512 | -0.25635 | -0.027466 | -0.082397 | -0.1831 | 0.054932 | -0.21515 | -0.13275 | -0.23804 | -0.082398 | 0.17395
321.5781 | 122.8546 | -60.704 | 61.821 | 0.39128 | 0.0070598 | 0.0069477 | 0.00072227 | 0.061798 | -0.0005189 | 0.067546 | -60.8139 | 61.7615 | -60.9787 | -60.8734 | 61.6013 | 0.16479 | -0.17853 | 0.13733 | 61.7477 | -60.9604 | -0.27466 | -0.059509 | -0.10986 | -0.16937 | 0.086975 | -0.21973 | -0.14649 | -0.25635 | -0.073242 | 0.16479
322.5781 | 122.8409 | -60.7361 | 61.8256 | 0.33024 | 0.0051372 | 0.0052387 | 0.0017903 | 0.061371 | -0.0030823 | 0.069255 | -60.8322 | 61.7477 | -60.9512 | -60.9329 | 61.5738 | 0.16022 | -0.12817 | 0.082397 | 61.7386 | -60.9787 | -0.21515 | -0.07782 | -0.09613 | -0.19684 | 0.045777 | -0.25177 | -0.16479 | -0.24262 | -0.086976 | 0.11902
323.5781 | 122.8821 | -60.6995 | 61.8805 | -0.035967 | 0.0085552 | 0.0082295 | 0.0020039 | 0.061371 | -0.0007325 | 0.068614 | -60.7956 | 61.7889 | -60.9512 | -60.8231 | 61.6333 | 0.27924 | 0.013733 | 0.26093 | 61.8027 | -60.9558 | -0.25177 | -0.091553 | -0.09613 | -0.1236 | 0.13275 | -0.24719 | -0.16937 | -0.25635 | -0.07782 | 0.15564
324.5781 | 122.8775 | -60.7132 | 61.8622 | 0.32261 | 0.0062052 | 0.0043843 | 0.0017903 | 0.061584 | -0.0020141 | 0.069041 | -60.8139 | 61.7798 | -60.9787 | -60.8963 | 61.5829 | 0.16479 | -0.14648 | 0.1236 | 61.7706 | -60.9512 | -0.2655 | -0.082398 | -0.10071 | -0.1831 | 0.054932 | -0.27924 | -0.18768 | -0.23804 | -0.091553 | 0.16479
325.5781 | 122.8271 | -60.7086 | 61.8393 | 0.33024 | 0.007487 | 0.0071615 | 0.0030721 | 0.061371 | -9.1495e-05 | 0.068827 | -60.8002 | 61.7615 | -60.9695 | -60.8963 | 61.5875 | 0.18768 | -0.16479 | 0.1236 | 61.7661 | -60.9695 | -0.26093 | -0.077819 | -0.091553 | -0.18768 | 0.073242 | -0.25177 | -0.17853 | -0.26093 | -0.073242 | 0.16937
326.5781 | 122.8592 | -60.6949 | 61.8027 | 0.36076 | 0.0053508 | 0.0045979 | 0.0024313 | 0.062225 | -0.0011597 | 0.067546 | -60.7864 | 61.7706 | -60.9604 | -60.8917 | 61.5967 | 0.19226 | -0.17395 | 0.13275 | 61.7432 | -60.965 | -0.2655 | -0.032043 | -0.091553 | -0.19684 | 0.073242 | -0.20599 | -0.14648 | -0.27008 | -0.059509 | 0.17395
327.5781 | 122.9095 | -60.7086 | 61.7981 | 0.4218 | 0.0087688 | 0.0090841 | 0.0045675 | 0.062866 | -0.0047913 | 0.069468 | -60.7636 | 61.7661 | -60.9512 | -60.878 | 61.6058 | 0.19684 | -0.19684 | 0.11444 | 61.7661 | -60.9741 | -0.24262 | -0.032044 | -0.054932 | -0.16937 | 0.09613 | -0.19226 | -0.16022 | -0.2655 | -0.032044 | 0.18768
328.5781 | 122.8592 | -60.7132 | 61.8118 | 0.0098091 | 0.0051372 | 0.0048115 | 0.0039267 | 0.06308 | -0.0024415 | 0.0684 | -60.7636 | 61.7844 | -60.9558 | -60.8734 | 61.6104 | 0.20142 | -0.16479 | 0.14191 | 61.7661 | -60.9695 | -0.24261 | -0.027466 | -0.050354 | -0.16022 | 0.09613 | -0.20142 | -0.15564 | -0.25635 | -0.045777 | 0.19226
329.5781 | 122.8683 | -60.7132 | 61.8393 | 0.36839 | 0.0042826 | 0.0054525 | 0.0013631 | 0.063721 | -0.0009461 | 0.069041 | -60.8002 | 61.7523 | -60.9787 | -60.91 | 61.5692 | 0.17395 | -0.13275 | 0.10986 | 61.7889 | -60.9604 | -0.2655 | -0.086975 | -0.086975 | -0.19684 | 0.050354 | -0.27008 | -0.21973 | -0.24719 | -0.050354 | 0.17853
330.5781 | 122.8226 | -60.7086 | 61.821 | 0.29973 | 0.0059916 | 0.0039571 | 0.0024313 | 0.061157 | -0.0013733 | 0.067546 | -60.8002 | 61.7889 | -60.9741 | -60.8963 | 61.5875 | 0.18768 | -0.13275 | 0.11444 | 61.7615 | -60.9787 | -0.2655 | -0.032044 | -0.091553 | -0.18768 | 0.082398 | -0.23346 | -0.17395 | -0.27008 | -0.059509 | 0.17395
331.5781 | 122.8958 | -60.7178 | 61.8301 | 0.36839 | 0.0085552 | 0.0080159 | 0.0037129 | 0.06308 | -0.0015869 | 0.068827 | -60.8047 | 61.7752 | -60.9741 | -60.8826 | 61.6058 | 0.20599 | -0.15564 | 0.14191 | 61.7432 | -60.9787 | -0.25635 | -0.054931 | -0.086976 | -0.16479 | 0.096131 | -0.2243 | -0.13733 | -0.26093 | -0.086975 | 0.16937
332.5781 | 122.8455 | -60.7086 | 61.8347 | 0.38365 | 0.0049236 | 0.0056661 | 0.0045675 | 0.062225 | 0.0001221 | 0.070323 | -60.7864 | 61.7615 | -60.9375 | -60.8917 | 61.6058 | 0.21057 | -0.16937 | 0.13733 | 61.734 | -60.997 | -0.22888 | -0.073242 | -0.07782 | -0.18311 | 0.10528 | -0.22888 | -0.12817 | -0.28839 | -0.10071 | 0.15106
333.5781 | 122.8867 | -60.6995 | 61.853 | 0.36839 | 0.0070598 | 0.0058797 | 0.0058493 | 0.062866 | 0.0016175 | 0.067546 | -60.7636 | 61.7798 | -60.9421 | -60.8688 | 61.615 | 0.20599 | -0.16479 | 0.13733 | 61.7615 | -60.9604 | -0.24262 | -0.073242 | -0.064087 | -0.16937 | 0.091553 | -0.23804 | -0.14648 | -0.26093 | -0.091552 | 0.17853
334.5781 | 122.9095 | -60.6949 | 61.8256 | 0.41417 | 0.0094096 | 0.0054525 | 0.0049947 | 0.062225 | -0.0018005 | 0.0684 | -60.7956 | 61.7706 | -60.9695 | -60.8734 | 61.5921 | 0.21973 | -0.21057 | 0.13275 | 61.7523 | -60.9741 | -0.27466 | -0.054932 | -0.10071 | -0.17853 | 0.10071 | -0.23346 | -0.16022 | -0.27924 | -0.073243 | 0.17395
335.5781 | 122.8592 | -60.6857 | 61.821 | 0.26158 | 0.0066326 | 0.0058797 | 0.0030721 | 0.062866 | -0.0018005 | 0.070323 | -60.7819 | 61.7889 | -60.9512 | -60.8643 | 61.6196 | 0.23346 | -0.17853 | 0.11902 | 61.7523 | -60.9924 | -0.2655 | -0.032044 | -0.09613 | -0.17853 | 0.12817 | -0.20142 | -0.13275 | -0.3067 | -0.068665 | 0.16937
336.5781 | 122.8821 | -60.7269 | 61.853 | 0.36839 | 0.0079142 | 0.0026753 | 0.0015767 | 0.060303 | -0.0018005 | 0.066691 | -60.8139 | 61.7706 | -60.9879 | -60.9055 | 61.5875 | 0.20142 | -0.1236 | 0.10986 | 61.7569 | -60.9741 | -0.26093 | -0.082397 | -0.086975 | -0.17853 | 0.068664 | -0.2655 | -0.16937 | -0.24719 | -0.09613 | 0.17395
337.5781 | 122.7951 | -60.6949 | 61.8393 | 0.38365 | 0.0083416 | 0.00096634 | 0.0032857 | 0.061798 | -0.0024415 | 0.068827 | -60.8139 | 61.7661 | -60.9604 | -60.91 | 61.5829 | 0.21515 | -0.16022 | 0.10986 | 61.7523 | -60.9924 | -0.2655 | -0.073242 | -0.11902 | -0.21515 | 0.082398 | -0.25635 | -0.16937 | -0.29755 | -0.086975 | 0.14648
338.5781 | 122.8683 | -60.7269 | 61.8301 | 0.36076 | 0.0055644 | 0.0050251 | 0.0020039 | 0.060089 | -0.0013733 | 0.07075 | -60.791 | 61.7889 | -60.9604 | -60.9009 | 61.5784 | 0.22888 | -0.15106 | 0.1236 | 61.7661 | -60.9604 | -0.23346 | -0.041199 | -0.064087 | -0.17395 | 0.059509 | -0.25177 | -0.18768 | -0.23346 | -0.064087 | 0.16937
339.5781 | 122.8455 | -60.6995 | 61.8164 | 0.36076 | 0.0081278 | 0.0080159 | 0.0015767 | 0.063507 | -0.0028687 | 0.068187 | -60.7956 | 61.7935 | -60.965 | -60.8826 | 61.5967 | 0.23346 | -0.15106 | 0.13275 | 61.7661 | -60.965 | -0.2655 | -0.022888 | -0.09613 | -0.1831 | 0.082398 | -0.21973 | -0.16937 | -0.2655 | -0.050354 | 0.16937
340.5781 | 122.8683 | -60.7086 | 61.7981 | 0.36076 | 0.0068462 | 0.0026753 | 0.0045675 | 0.062652 | -0.0013733 | 0.0684 | -60.7819 | 61.7661 | -60.9695 | -60.8871 | 61.6104 | 0.25635 | -0.16479 | 0.10529 | 61.7752 | -60.9604 | -0.26093 | -0.032044 | -0.073242 | -0.17853 | 0.073242 | -0.18768 | -0.16479 | -0.25177 | -0.022888 | 0.18768
341.5781 | 122.9187 | -60.7086 | 61.8118 | 0.4218 | 0.0051372 | 0.0088703 | 0.0052083 | 0.062225 | -0.0028687 | 0.0684 | -60.7819 | 61.7798 | -60.9924 | -60.8597 | 61.6196 | 0.25635 | -0.21973 | 0.13733 | 61.7477 | -60.9833 | -0.28381 | -0.032044 | -0.073242 | -0.15106 | 0.1236 | -0.19226 | -0.12817 | -0.27466 | -0.064087 | 0.21057
342.5781 | 122.8363 | -60.6812 | 61.8301 | 0.3455 | 0.0055644 | 0.0031025 | 0.0041403 | 0.063934 | -0.0013733 | 0.067973 | -60.8093 | 61.7477 | -60.9695 | -60.8734 | 61.6104 | 0.24261 | -0.17395 | 0.13733 | 61.7432 | -60.9604 | -0.28839 | -0.082397 | -0.12817 | -0.19226 | 0.086975 | -0.21973 | -0.13275 | -0.27924 | -0.086975 | 0.16022
343.5781 | 122.8592 | -60.6903 | 61.8439 | 0.39128 | 0.0070598 | 0.0058797 | 0.0011495 | 0.062439 | 0.0001221 | 0.069896 | -60.8505 | 61.7706 | -60.965 | -60.9055 | 61.5784 | 0.22888 | -0.11444 | 0.082397 | 61.7706 | -60.9787 | -0.27466 | -0.073242 | -0.16022 | -0.21515 | 0.073242 | -0.2655 | -0.19226 | -0.28839 | -0.073242 | 0.11444
344.5781 | 122.85 | -60.7224 | 61.8164 | 0.36839 | 0.0066326 | 0.0033161 | 0.0011495 | 0.061798 | 0.0020447 | 0.067973 | -60.8276 | 61.7752 | -60.965 | -60.9146 | 61.5829 | 0.22888 | -0.11902 | 0.09613 | 61.7477 | -60.9833 | -0.24261 | -0.041198 | -0.10529 | -0.19226 | 0.068664 | -0.23346 | -0.1648 | -0.26092 | -0.068664 | 0.13733
345.5781 | 122.8867 | -60.7132 | 61.8393 | 0.40654 | 0.0062052 | 0.0011799 | 0.0011495 | 0.061157 | -0.0020141 | 0.0684 | -60.8185 | 61.7706 | -60.9512 | -60.9192 | 61.5829 | 0.24719 | -0.10986 | 0.11444 | 61.7752 | -60.9421 | -0.23804 | -0.068664 | -0.10528 | -0.20599 | 0.022889 | -0.25635 | -0.19226 | -0.22888 | -0.064086 | 0.13275
346.5781 | 122.8592 | -60.704 | 61.8484 | 0.39128 | 0.0064188 | 0.0056661 | 0.0026449 | 0.062012 | 0.0009765 | 0.065837 | -60.8002 | 61.7706 | -60.9604 | -60.9192 | 61.5829 | 0.24719 | -0.10986 | 0.086975 | 61.7706 | -60.9879 | -0.25635 | -0.07782 | -0.09613 | -0.21515 | 0.068665 | -0.2655 | -0.18768 | -0.28381 | -0.07782 | 0.16022
347.5781 | 122.8317 | -60.7178 | 61.8393 | 0.36076 | 0.0066326 | 0.0067341 | 0.0020039 | 0.060944 | -9.1495e-05 | 0.067759 | -60.8322 | 61.7569 | -60.9695 | -60.91 | 61.5829 | 0.23346 | -0.13733 | 0.091553 | 61.7569 | -60.9695 | -0.25177 | -0.082397 | -0.11444 | -0.19226 | 0.059509 | -0.25635 | -0.17395 | -0.25177 | -0.082397 | 0.13733
348.5781 | 122.8958 | -60.704 | 61.8027 | 1.6501 | 0.0062052 | 0.0065205 | 0.0064901 | 0.061584 | -0.0043641 | 0.0684 | -60.8276 | 61.7523 | -60.9695 | -60.8459 | 61.615 | 0.28381 | -0.16937 | 0.1236 | 61.7661 | -60.9512 | -0.2655 | -0.050354 | -0.1236 | -0.14191 | 0.10529 | -0.18768 | -0.15106 | -0.24719 | -0.036621 | 0.14191
349.5781 | 122.8226 | -60.7178 | 61.8439 | 0.35313 | 0.0070598 | 0.0052387 | 0.0026449 | 0.063934 | -0.0030823 | 0.067973 | -60.8093 | 61.7432 | -60.9787 | -60.9146 | 61.5738 | 0.25635 | -0.16479 | 0.10071 | 61.7798 | -60.9604 | -0.26093 | -0.10071 | -0.091553 | -0.19684 | 0.045776 | -0.27008 | -0.20599 | -0.24262 | -0.064087 | 0.16937
350.5781 | 122.8775 | -60.7178 | 61.8576 | 0.33024 | 0.0055644 | 0.0035299 | -0.0014139 | 0.061798 | -0.0005189 | 0.068614 | -60.8505 | 61.7844 | -60.9604 | -60.9238 | 61.5738 | 0.2655 | -0.082397 | 0.10071 | 61.7706 | -60.9558 | -0.24262 | -0.073242 | -0.13275 | -0.20599 | 0.032044 | -0.28381 | -0.19684 | -0.23804 | -0.086975 | 0.10986
351.5781 | 122.85 | -60.7269 | 61.8439 | 0.3455 | 0.0072734 | 0.0043843 | 0.0011495 | 0.060516 | -0.0007325 | 0.0684 | -60.8414 | 61.7844 | -60.965 | -60.9283 | 61.5646 | 0.26093 | -0.082397 | 0.09613 | 61.7523 | -60.9787 | -0.23804 | -0.059509 | -0.11444 | -0.20142 | 0.050354 | -0.27924 | -0.18768 | -0.25177 | -0.091553 | 0.1236
352.5781 | 122.85 | -60.7315 | 61.8439 | 0.28447 | 0.0062052 | 0.0065205 | 0.0024313 | 0.061584 | -0.0018005 | 0.067332 | -60.8505 | 61.7569 | -60.9695 | -60.9192 | 61.5692 | 0.2655 | -0.091553 | 0.09613 | 61.7569 | -60.9512 | -0.23804 | -0.086975 | -0.11902 | -0.18768 | 0.032044 | -0.27466 | -0.18768 | -0.21973 | -0.086975 | 0.11902
353.5781 | 122.8821 | -60.7086 | 61.8301 | 0.31499 | 0.0051372 | 0.0058797 | 0.0028585 | 0.061157 | 0.0003357 | 0.068614 | -60.7819 | 61.7752 | -60.9375 | -60.8688 | 61.5921 | 0.29755 | -0.16937 | 0.11902 | 61.7523 | -60.9787 | -0.22888 | -0.054931 | -0.073242 | -0.16022 | 0.10986 | -0.23804 | -0.16022 | -0.27008 | -0.07782 | 0.15564
354.5781 | 122.8363 | -60.7178 | 61.8073 | 0.3455 | 0.0070598 | 0.0026753 | 0.00093587 | 0.062439 | -0.0022277 | 0.066905 | -60.7681 | 61.7432 | -60.9558 | -60.8688 | 61.6196 | 0.3067 | -0.17395 | 0.12817 | 61.7569 | -60.965 | -0.23804 | -0.064087 | -0.050354 | -0.15106 | 0.096131 | -0.18768 | -0.13733 | -0.24719 | -0.050354 | 0.18768
355.5781 | 122.8958 | -60.6995 | 61.821 | 0.45231 | 0.0070598 | 0.0041707 | 0.0011495 | 0.059875 | -0.0013733 | 0.066264 | -60.791 | 61.7569 | -60.9741 | -60.8643 | 61.6104 | 0.3067 | -0.17853 | 0.11444 | 61.7798 | -60.9741 | -0.27466 | -0.064087 | -0.091553 | -0.16479 | 0.10986 | -0.21057 | -0.16937 | -0.27466 | -0.041199 | 0.1831
356.5781 | 122.9141 | -60.6995 | 61.821 | 0.30736 | 0.0077006 | 0.0067341 | 0.0032857 | 0.060944 | -0.0022277 | 0.069041 | -60.7773 | 61.7752 | -60.9558 | -60.8734 | 61.6013 | 0.31586 | -0.16479 | 0.11902 | 61.7523 | -60.965 | -0.25635 | -0.045776 | -0.07782 | -0.17395 | 0.091553 | -0.21973 | -0.15106 | -0.2655 | -0.068665 | 0.17853
357.5781 | 122.85 | -60.6949 | 61.8439 | 0.39128 | 0.0070598 | 0.0050251 | 0.0015767 | 0.062012 | -0.0005189 | 0.068614 | -60.8322 | 61.7798 | -60.965 | -60.91 | 61.5784 | 0.28839 | -0.11444 | 0.09613 | 61.7752 | -60.9741 | -0.27008 | -0.064087 | -0.13733 | -0.21515 | 0.064087 | -0.2655 | -0.19684 | -0.27924 | -0.068664 | 0.13275
358.5781 | 122.85 | -60.704 | 61.8576 | 0.28447 | 0.0059916 | 0.0016073 | -0.0012003 | 0.059875 | -0.0003051 | 0.067759 | -60.8368 | 61.7661 | -60.9604 | -60.9055 | 61.5829 | 0.30212 | -0.07782 | 0.10529 | 61.7844 | -60.965 | -0.25635 | -0.091553 | -0.13275 | -0.20142 | 0.059509 | -0.27466 | -0.20142 | -0.26093 | -0.073242 | 0.1236
359.5781 | 122.7859 | -60.7407 | 61.9263 | -0.051226 | 0.0077006 | 0.0031025 | 0.0017903 | 0.060303 | -0.0003051 | 0.067546 | -60.8368 | 61.8713 | -60.9512 | -60.9238 | 61.5417 | 0.30212 | 0.44403 | 0.10071 | 61.8622 | -60.9741 | -0.21057 | -0.054932 | -0.09613 | -0.1831 | 0.050354 | -0.38452 | -0.32044 | -0.23346 | -0.064087 | 0.11444
360.5781 | 122.8683 | -60.7086 | 61.8576 | 0.26921 | 0.005778 | 0.0024617 | 0.00050867 | 0.062012 | 0.0016175 | 0.066691 | -60.8368 | 61.7661 | -60.9833 | -60.9192 | 61.5875 | 0.31128 | -0.073242 | 0.086975 | 61.8027 | -60.9558 | -0.27466 | -0.091553 | -0.12817 | -0.21057 | 0.036622 | -0.27008 | -0.21515 | -0.24719 | -0.054932 | 0.14648
361.6094 | 122.7493 | -60.6949 | 61.8896 | -0.0054494 | 0.0068462 | 0.0063069 | 0.011617 | 0.063293 | -0.0003051 | 0.067759 | -60.7819 | 61.8942 | -60.9558 | -60.878 | 61.5829 | 0.36621 | 0.036621 | 0.13733 | 61.8256 | -60.997 | -0.26093 | 0.004578 | -0.086975 | -0.18311 | 0.11902 | -0.3067 | -0.24262 | -0.30212 | -0.064086 | 0.17395
362.5781 | 122.8409 | -60.704 | 61.8484 | 0.30736 | 0.0051372 | 0.0022481 | -0.00013233 | 0.063721 | -0.0032959 | 0.067759 | -60.8551 | 61.7523 | -60.9924 | -60.9329 | 61.5829 | 0.32044 | -0.086975 | 0.09613 | 61.7981 | -60.9695 | -0.28839 | -0.096131 | -0.15106 | -0.22888 | 0.036621 | -0.2655 | -0.21515 | -0.2655 | -0.050354 | 0.13733
363.5781 | 122.8683 | -60.7224 | 61.8622 | 0.33787 | 0.0068462 | 0.00096634 | 0.0020039 | 0.060944 | -0.0003051 | 0.068187 | -60.8459 | 61.7615 | -60.9604 | -60.9238 | 61.5875 | 0.32044 | -0.073242 | 0.07782 | 61.8073 | -60.965 | -0.23804 | -0.10071 | -0.1236 | -0.20142 | 0.041199 | -0.27466 | -0.21973 | -0.24261 | -0.054932 | 0.11444
364.5781 | 122.8409 | -60.7086 | 61.8576 | 0.33024 | 0.0049236 | 0.0035299 | 8.1267e-05 | 0.061798 | -0.0018005 | 0.069041 | -60.8459 | 61.7706 | -60.9558 | -60.9329 | 61.5555 | 0.31128 | -0.10529 | 0.082397 | 61.7798 | -60.965 | -0.24719 | -0.086975 | -0.13733 | -0.2243 | 0.032044 | -0.30212 | -0.2243 | -0.25635 | -0.07782 | 0.10986
365.5781 | 122.8409 | -60.6949 | 61.8484 | 0.23869 | 0.0062052 | 0.0026753 | 0.00093587 | 0.061157 | -0.0003051 | 0.068827 | -60.8368 | 61.7798 | -60.9512 | -60.9146 | 61.6745 | 0.46234 | -0.09613 | 0.054932 | 61.7935 | -60.9421 | -0.25635 | -0.068665 | -0.14191 | -0.21973 | 0.027466 | -0.17395 | -0.11902 | -0.24719 | -0.054932 | 0.11444
366.5781 | 122.8226 | -60.704 | 61.8576 | 0.25395 | 0.0062052 | 0.0041707 | -0.00098673 | 0.06073 | -0.0020141 | 0.069041 | -60.8459 | 61.7569 | -60.9558 | -60.9009 | 61.5738 | 0.33417 | 0.12817 | 0.16022 | 61.7798 | -60.9512 | -0.25177 | -0.10071 | -0.14191 | -0.19684 | 0.050354 | -0.28381 | -0.20599 | -0.24719 | -0.07782 | 0.10986
367.5781 | 122.8683 | -60.6903 | 61.8576 | 0.36076 | 0.0059916 | 0.0026753 | 0.0022177 | 0.061157 | 0.0016175 | 0.067546 | -60.8368 | 61.7706 | -60.9375 | -60.9238 | 61.5738 | 0.35248 | -0.1236 | 0.064087 | 61.7661 | -60.9558 | -0.24719 | -0.086975 | -0.14648 | -0.23346 | 0.032044 | -0.28381 | -0.19226 | -0.2655 | -0.091553 | 0.10071
368.5781 | 122.8775 | -60.6949 | 61.8484 | 0.36076 | 0.0062052 | 0.0035299 | 0.0030721 | 0.060516 | 0.0007629 | 0.066905 | -60.8231 | 61.7706 | -60.965 | -60.9055 | 61.5829 | 0.35248 | -0.1236 | 0.082397 | 61.7706 | -60.9924 | -0.27008 | -0.07782 | -0.12817 | -0.21057 | 0.086975 | -0.2655 | -0.18768 | -0.29755 | -0.07782 | 0.14191
369.5781 | 122.8775 | -60.704 | 61.8393 | 0.22343 | 0.0062052 | 0.0048115 | -0.0016275 | 0.060303 | -0.0011597 | 0.069041 | -60.8414 | 61.7752 | -60.9741 | -60.9009 | 61.6058 | 0.39368 | -0.054932 | 0.14648 | 61.7752 | -60.9421 | -0.27008 | -0.064086 | -0.13733 | -0.19684 | 0.041199 | -0.23346 | -0.16937 | -0.23804 | -0.064086 | 0.13275
370.5781 | 122.8592 | -60.6949 | 61.8301 | 0.23869 | 0.0085552 | 0.00053914 | -0.00055953 | 0.061798 | -0.0026551 | 0.067546 | -60.8276 | 61.7844 | -60.9695 | -60.9146 | 61.5784 | 0.37079 | -0.086975 | 0.091553 | 61.7981 | -60.9467 | -0.27466 | -0.045776 | -0.13275 | -0.21973 | 0.032043 | -0.25177 | -0.21973 | -0.25177 | -0.032043 | 0.14191
371.5781 | 122.8729 | -60.6903 | 61.8713 | 0.13188 | 0.0051372 | 0.0020345 | -0.0018413 | 0.060516 | -0.0005189 | 0.067759 | -60.8505 | 61.7935 | -60.9512 | -60.9009 | 61.5875 | 0.39825 | -0.068665 | 0.13275 | 61.8027 | -60.9558 | -0.26093 | -0.07782 | -0.16022 | -0.21057 | 0.054932 | -0.28381 | -0.21515 | -0.2655 | -0.068665 | 0.10071
372.5781 | 122.8729 | -60.7132 | 61.853 | 0.3455 | 0.0077006 | 0.0082295 | 0.00050867 | 0.060516 | 0.0009765 | 0.067332 | -60.8597 | 61.7752 | -60.9604 | -60.9192 | 61.5784 | 0.40283 | -0.082397 | 0.10986 | 61.7889 | -60.9512 | -0.24719 | -0.077819 | -0.14648 | -0.20599 | 0.032044 | -0.27466 | -0.21057 | -0.23804 | -0.064087 | 0.10071
373.5781 | 122.8409 | -60.6995 | 61.8668 | 0.18529 | 0.0051372 | 0.0035299 | 0.00093587 | 0.059875 | -0.0003051 | 0.067973 | -60.8597 | 61.7661 | -60.965 | -60.9055 | 61.5738 | 0.41199 | -0.050354 | 0.086975 | 61.7889 | -60.9512 | -0.2655 | -0.10071 | -0.16022 | -0.20599 | 0.045776 | -0.29297 | -0.21515 | -0.25177 | -0.07782 | 0.10529
374.5781 | 122.8821 | -60.7132 | 61.8622 | 0.26158 | 0.0049236 | 0.0058797 | -0.0012003 | 0.061371 | -0.0032959 | 0.066691 | -60.8459 | 61.7798 | -60.9467 | -60.8826 | 61.5189 | 0.38452 | -0.050354 | 0.082397 | 61.7889 | -60.9558 | -0.23346 | -0.082398 | -0.13275 | -0.16937 | 0.073243 | -0.34332 | -0.27008 | -0.24261 | -0.073243 | 0.10071
375.5938 | 122.6944 | -60.759 | 61.8118 | 0.32261 | 0.0066326 | 0.0075887 | 0.0073445 | 0.062225 | 0.0009765 | 0.066691 | -60.8597 | 61.8851 | -60.9741 | -60.9833 | 61.4868 | 0.3067 | -0.004578 | -0.041199 | 61.821 | -61.0153 | -0.21515 | 0.073242 | -0.10071 | -0.2243 | 0.032044 | -0.32501 | -0.33417 | -0.25635 | 0.009155 | 0.11444
376.5781 | 122.7631 | -60.7361 | 61.8942 | -0.043596 | 0.0098368 | 0.0039571 | 0.0058493 | 0.062652 | -0.0024415 | 0.067973 | -60.8093 | 61.9125 | -60.9558 | -60.9512 | 61.5005 | 0.38452 | 0.1236 | 0.07782 | 61.853 | -60.9558 | -0.21973 | 0.018311 | -0.073242 | -0.21515 | 0.004578 | -0.39368 | -0.35248 | -0.21973 | -0.041199 | 0.14648
377.5781 | 122.8363 | -60.6995 | 61.8484 | 0.24632 | 0.007487 | 0.0039571 | -0.0022685 | 0.063293 | -0.0022277 | 0.067118 | -60.8505 | 61.7615 | -60.9879 | -60.9238 | 61.5921 | 0.42114 | -0.082397 | 0.091553 | 61.7981 | -60.9192 | -0.28839 | -0.086975 | -0.15106 | -0.2243 | -0.004578 | -0.25635 | -0.20599 | -0.21973 | -0.050354 | 0.13733
378.5781 | 122.905 | -60.7132 | 61.8668 | 0.29973 | 0.0055644 | 0.0020345 | -0.00098673 | 0.061157 | -0.0026551 | 0.066905 | -60.8597 | 61.7889 | -60.9741 | -60.9009 | 61.6013 | 0.44861 | -0.07782 | 0.10986 | 61.7981 | -60.9375 | -0.26092 | -0.07782 | -0.14648 | -0.18768 | 0.036621 | -0.2655 | -0.19684 | -0.2243 | -0.068664 | 0.11444
379.5781 | 122.8683 | -60.704 | 61.8576 | 0.20054 | 0.0034282 | 0.00053914 | 0.00029507 | 0.059448 | -0.0020141 | 0.065837 | -60.7086 | 61.7889 | -60.9604 | -60.8826 | 61.5646 | 0.42572 | -0.059509 | 0.10529 | 61.7752 | -60.9558 | -0.25635 | -0.068665 | -0.004577 | -0.17853 | 0.073243 | -0.29297 | -0.21057 | -0.25177 | -0.082397 | 0.25177
380.5781 | 122.85 | -60.7086 | 61.8347 | 0.17766 | 0.0062052 | 0.0054525 | -0.0035503 | 0.059448 | -0.0009461 | 0.067973 | -60.8414 | 61.7798 | -60.965 | -60.9329 | 61.5829 | 0.47607 | -0.07782 | 0.086975 | 61.7569 | -60.9558 | -0.25635 | -0.054932 | -0.13275 | -0.2243 | 0.022889 | -0.25177 | -0.17395 | -0.24719 | -0.07782 | 0.1236
381.5781 | 122.8729 | -60.704 | 61.8484 | 0.23869 | 0.0059916 | 0.0041707 | -0.00098673 | 0.059021 | -0.0011597 | 0.067759 | -60.8551 | 61.7889 | -60.9695 | -60.9055 | 61.4777 | 0.49896 | -0.027466 | 0.041199 | 61.7981 | -60.9467 | -0.2655 | -0.05951 | -0.15106 | -0.20142 | 0.041198 | -0.37079 | -0.32044 | -0.24261 | -0.050354 | 0.11444
382.5781 | 122.8363 | -60.7086 | 61.8668 | 0.2158 | 0.0070598 | 0.0033161 | 0.00072227 | 0.059235 | -0.0005189 | 0.068187 | -60.8276 | 61.7569 | -60.9695 | -60.9055 | 61.5829 | 0.45776 | -0.050354 | 0.07782 | 61.7752 | -60.965 | -0.26093 | -0.10986 | -0.11902 | -0.19684 | 0.059509 | -0.28381 | -0.19226 | -0.25635 | -0.091552 | 0.14191
383.5781 | 122.8775 | -60.6812 | 61.853 | 0.20817 | 0.005778 | 0.0013935 | -0.00013233 | 0.059662 | -0.0011597 | 0.066691 | -60.8368 | 61.7798 | -60.965 | -60.9055 | 61.5555 | 0.46234 | -0.064087 | 0.086975 | 61.7844 | -60.9421 | -0.28381 | -0.073242 | -0.15564 | -0.22431 | 0.036621 | -0.29755 | -0.22888 | -0.26093 | -0.068664 | 0.12817
384.5781 | 122.8363 | -60.6995 | 61.853 | 0.24632 | 0.0089824 | 0.00096634 | -0.0018413 | 0.062012 | -0.0005189 | 0.067546 | -60.8414 | 61.7661 | -60.9695 | -60.91 | 61.5601 | 0.44403 | -0.064087 | 0.086975 | 61.7889 | -60.9558 | -0.27008 | -0.086975 | -0.14191 | -0.21057 | 0.045777 | -0.29297 | -0.22888 | -0.25635 | -0.064087 | 0.12817
385.5781 | 122.8821 | -60.7086 | 61.8668 | 0.047956 | 0.0055644 | 0.0058797 | -0.0018413 | 0.060516 | -0.0009461 | 0.067759 | -60.8505 | 61.7615 | -60.9787 | -60.878 | 61.5875 | 0.48981 | -0.059509 | 0.11444 | 61.8027 | -60.91 | -0.27008 | -0.10529 | -0.14191 | -0.16937 | 0.032043 | -0.27924 | -0.21515 | -0.20142 | -0.064087 | 0.12817
386.5781 | 122.8363 | -60.7086 | 61.8668 | 0.32261 | 0.0062052 | 0.0011799 | -0.0014139 | 0.059235 | -0.0003051 | 0.067973 | -60.8322 | 61.7523 | -60.965 | -60.878 | 61.5921 | 0.50354 | -0.068665 | 0.091553 | 61.7706 | -60.9421 | -0.25635 | -0.11444 | -0.1236 | -0.16937 | 0.064087 | -0.27466 | -0.17853 | -0.23346 | -0.09613 | 0.13275
387.5781 | 122.8958 | -60.7132 | 61.8759 | 0.31499 | 0.0064188 | 0.0031025 | -0.00013233 | 0.059448 | 0.0009765 | 0.067118 | -60.8551 | 61.7889 | -60.965 | -60.8963 | 61.5829 | 0.49896 | -0.068665 | 0.10529 | 61.7981 | -60.9558 | -0.25177 | -0.086976 | -0.14191 | -0.1831 | 0.05951 | -0.29297 | -0.21515 | -0.24261 | -0.07782 | 0.10986
388.5781 | 122.8683 | -60.6995 | 61.8484 | 1.055 | 0.0077006 | 0.0016073 | 8.1267e-05 | 0.061371 | -9.1495e-05 | 0.067332 | -60.8368 | 61.7935 | -60.9741 | -60.8826 | 61.5921 | 0.49896 | -0.068665 | 0.09613 | 61.7706 | -60.9238 | -0.27466 | -0.054932 | -0.13733 | -0.1831 | 0.041199 | -0.25635 | -0.17853 | -0.2243 | -0.07782 | 0.13733
389.5781 | 122.7951 | -60.704 | 61.9263 | -0.028338 | 0.0049236 | 0.0075887 | 0.0037129 | 0.060944 | -0.0020141 | 0.068614 | -60.7864 | 61.8393 | -60.9467 | -60.8826 | 61.5784 | 0.54474 | 0.10529 | 0.1236 | 61.8301 | -60.9421 | -0.24261 | -0.086976 | -0.082397 | -0.17853 | 0.05951 | -0.3479 | -0.25177 | -0.23804 | -0.096131 | 0.16022
390.5781 | 122.8821 | -60.6995 | 61.8347 | 0.20817 | 0.0044962 | 0.0052387 | 0.0017903 | 0.059662 | -0.0007325 | 0.068187 | -60.7315 | 61.821 | -60.9512 | -60.878 | 61.6058 | 0.50354 | -0.059509 | 0.086975 | 61.7935 | -60.9329 | -0.25177 | -0.013733 | -0.032043 | -0.17853 | 0.054931 | -0.22888 | -0.18768 | -0.23346 | -0.041199 | 0.21973
391.5781 | 122.8271 | -60.6995 | 61.853 | 0.19291 | 0.0044962 | 0.00075274 | 0.00093587 | 0.061371 | -0.0013733 | 0.066905 | -60.8551 | 61.7981 | -60.9787 | -60.9192 | 61.5875 | 0.55389 | -0.07782 | 0.09613 | 61.7661 | -60.9604 | -0.27924 | -0.054931 | -0.15564 | -0.21973 | 0.041199 | -0.2655 | -0.17853 | -0.26093 | -0.086975 | 0.1236
392.5781 | 122.905 | -60.704 | 61.8393 | 0.17003 | 0.004069 | 0.0035299 | 0.00050867 | 0.061584 | 0.0007629 | 0.066264 | -60.8139 | 61.7615 | -60.9421 | -60.8551 | 61.6241 | 0.59052 | -0.054932 | 0.16479 | 61.7844 | -60.9283 | -0.23804 | -0.077819 | -0.10986 | -0.15106 | 0.073242 | -0.21515 | -0.16022 | -0.2243 | -0.054931 | 0.12817
393.5781 | 122.8546 | -60.6812 | 61.853 | 0.17003 | 0.0068462 | 0.00096634 | 0.00093587 | 0.060944 | -0.0011597 | 0.066478 | -60.8139 | 61.7752 | -60.965 | -60.8551 | 61.6287 | 0.60425 | -0.068665 | 0.15564 | 61.7752 | -60.9421 | -0.28381 | -0.077819 | -0.13275 | -0.17395 | 0.086975 | -0.2243 | -0.14648 | -0.26093 | -0.077819 | 0.15106
394.5781 | 122.9141 | -60.6995 | 61.8622 | 0.15477 | 0.0055644 | 0.0013935 | 0.00093587 | 0.059662 | -0.0009461 | 0.066691 | -60.8139 | 61.7706 | -60.9604 | -60.8551 | 61.6379 | 0.60425 | -0.064087 | 0.16022 | 61.7706 | -60.9375 | -0.26093 | -0.091553 | -0.11444 | -0.15564 | 0.082397 | -0.22431 | -0.13275 | -0.23804 | -0.091553 | 0.14648
395.5781 | 122.8683 | -60.7132 | 61.853 | 0.15477 | 0.0079142 | 0.0028889 | -0.0018413 | 0.062225 | -0.0009461 | 0.069041 | -60.7956 | 61.7798 | -60.965 | -60.8368 | 61.6287 | 0.62714 | -0.064087 | 0.15564 | 61.8027 | -60.9238 | -0.25177 | -0.073242 | -0.082397 | -0.1236 | 0.086975 | -0.2243 | -0.17395 | -0.21057 | -0.050354 | 0.16937
396.5781 | 122.9233 | -60.704 | 61.8805 | 0.11662 | 0.005778 | 0.0018209 | -0.00013233 | 0.062012 | -0.0011597 | 0.069041 | -60.8002 | 61.7706 | -60.965 | -60.8643 | 61.6425 | 0.62714 | -0.064087 | 0.14648 | 61.7706 | -60.9421 | -0.26093 | -0.10986 | -0.09613 | -0.16022 | 0.07782 | -0.23804 | -0.12817 | -0.23804 | -0.10986 | 0.16479
397.5781 | 122.8638 | -60.6857 | 61.8393 | 0.10899 | 0.0055644 | 0.0058797 | -0.00034593 | 0.060303 | -0.0015869 | 0.066478 | -60.8047 | 61.7752 | -60.965 | -60.8688 | 61.6287 | 0.63171 | -0.068665 | 0.15564 | 61.7981 | -60.9283 | -0.27924 | -0.064086 | -0.11902 | -0.1831 | 0.05951 | -0.21057 | -0.16937 | -0.24262 | -0.041198 | 0.16022
398.5781 | 122.8821 | -60.6857 | 61.8622 | 0.12425 | 0.004069 | 0.0020345 | -0.0016275 | 0.061157 | -0.0011597 | 0.067759 | -60.7956 | 61.7752 | -60.9512 | -60.8505 | 61.6196 | 0.63629 | -0.068665 | 0.15564 | 61.7706 | -60.9467 | -0.2655 | -0.086975 | -0.10986 | -0.16479 | 0.09613 | -0.24262 | -0.15106 | -0.26093 | -0.091553 | 0.15564
399.5781 | 122.8455 | -60.7269 | 61.8805 | 0.12425 | 0.010478 | 0.010152 | 0.0077719 | 0.062439 | -0.0005189 | 0.066905 | -60.7636 | 61.8896 | -60.965 | -60.9695 | 61.5967 | 0.6134 | 0.004578 | 0.091553 | 61.8118 | -61.0199 | -0.23804 | 0.009155 | -0.036621 | -0.24261 | 0.050354 | -0.28381 | -0.21515 | -0.29297 | -0.068664 | 0.20142
400.5781 | 122.9004 | -60.6857 | 61.8576 | 0.032698 | 0.0068462 | 0.0048115 | -0.0016275 | 0.062866 | -0.0020141 | 0.067546 | -60.7498 | 61.7615 | -60.9421 | -60.8047 | 61.6653 | 0.70038 | -0.045776 | 0.22888 | 61.8118 | -60.9009 | -0.25635 | -0.09613 | -0.064087 | -0.11902 | 0.09613 | -0.19226 | -0.14649 | -0.21515 | -0.045776 | 0.19226
401.5781 | 122.9233 | -60.6674 | 61.8896 | 0.032698 | 0.0062052 | 0.00032554 | -0.00098673 | 0.062866 | -0.0032959 | 0.068827 | -60.7544 | 61.7935 | -60.9375 | -60.8047 | 61.6928 | 0.72327 | -0.018311 | 0.21515 | 61.7889 | -60.9192 | -0.27008 | -0.09613 | -0.086976 | -0.13733 | 0.11444 | -0.19684 | -0.09613 | -0.25177 | -0.10071 | 0.1831
402.5781 | 122.8729 | -60.6903 | 61.8576 | 0.0021796 | 0.0055644 | 0.0050251 | 0.0011495 | 0.060303 | -0.0009461 | 0.069896 | -60.7498 | 61.7706 | -60.965 | -60.8139 | 61.6608 | 0.737 | -0.027466 | 0.21973 | 61.7935 | -60.9329 | -0.27466 | -0.086975 | -0.059509 | -0.1236 | 0.11902 | -0.19684 | -0.13275 | -0.24261 | -0.064087 | 0.21515
403.5781 | 122.8867 | -60.6766 | 61.8484 | 0.20054 | 0.0051372 | 0.0037435 | 0.0013631 | 0.060089 | -0.0009461 | 0.067332 | -60.7956 | 61.7706 | -60.9375 | -60.8505 | 61.6241 | 0.68665 | -0.07782 | 0.16022 | 61.7798 | -60.9283 | -0.26093 | -0.07782 | -0.11902 | -0.17395 | 0.07782 | -0.2243 | -0.15564 | -0.25177 | -0.068665 | 0.14191
404.5781 | 122.8409 | -60.6766 | 61.8713 | 0.15477 | 0.00471 | 0.0035299 | 0.0015767 | 0.060089 | -0.0022277 | 0.065623 | -60.7681 | 61.821 | -60.9375 | -60.8322 | 61.6379 | 0.71869 | -0.009155 | 0.19226 | 61.7981 | -60.9283 | -0.26093 | -0.050354 | -0.091552 | -0.15564 | 0.096131 | -0.23346 | -0.16022 | -0.25177 | -0.073242 | 0.16937
405.5781 | 122.8912 | -60.6949 | 61.8759 | -0.2267 | 0.0036418 | 0.0097249 | 0.0022177 | 0.06308 | -0.0005189 | 0.069041 | -60.7819 | 61.7523 | -60.9558 | -60.8231 | 61.6379 | 0.71869 | -0.022888 | 0.19226 | 61.8073 | -60.9192 | -0.26093 | -0.1236 | -0.086975 | -0.12817 | 0.09613 | -0.23804 | -0.16937 | -0.2243 | -0.068665 | 0.17395
406.5781 | 122.8683 | -60.6812 | 61.8805 | -0.11989 | 0.0077006 | 0.0035299 | 0.00093587 | 0.061798 | -0.0024415 | 0.069896 | -60.7773 | 61.7798 | -60.9467 | -60.8139 | 61.647 | 0.75073 | -0.027466 | 0.18768 | 61.7981 | -60.9421 | -0.2655 | -0.10071 | -0.096131 | -0.13275 | 0.12817 | -0.23346 | -0.15106 | -0.26093 | -0.082397 | 0.16937
407.5781 | 122.8729 | -60.6812 | 61.8896 | -0.18093 | 0.0059916 | 0.0016073 | 0.00093587 | 0.060944 | -0.0032959 | 0.067973 | -60.7727 | 61.7661 | -60.9375 | -60.8276 | 61.6562 | 0.75073 | -0.022888 | 0.18768 | 61.7798 | -60.9238 | -0.25635 | -0.1236 | -0.091553 | -0.14649 | 0.09613 | -0.23346 | -0.1236 | -0.24262 | -0.10986 | 0.16479
408.5781 | 122.8775 | -60.6812 | 61.853 | 0.017439 | 0.0034282 | 0.0045979 | 0.0028585 | 0.062225 | -0.0003051 | 0.067759 | -60.7681 | 61.7889 | -60.9467 | -60.8093 | 61.6653 | 0.76446 | -0.054932 | 0.16479 | 61.7935 | -60.9283 | -0.2655 | -0.064087 | -0.086975 | -0.12817 | 0.11902 | -0.18768 | -0.12817 | -0.24719 | -0.059509 | 0.17853
409.5781 | 122.8546 | -60.6812 | 61.8393 | 0.040327 | 0.0038554 | 0.0067341 | 0.0022177 | 0.062439 | -0.0022277 | 0.068187 | -60.8276 | 61.7752 | -60.9558 | -60.8185 | 61.6425 | 0.7782 | -0.022888 | 0.17853 | 61.7981 | -60.9192 | -0.27466 | -0.064086 | -0.14649 | -0.13733 | 0.10071 | -0.19684 | -0.15564 | -0.23804 | -0.041198 | 0.12817
410.5781 | 122.7997 | -60.704 | 61.908 | -0.051226 | 0.0081278 | 0.0013935 | 0.0015767 | 0.06073 | -0.0015869 | 0.066264 | -60.7864 | 61.821 | -60.9695 | -60.878 | 61.5921 | 0.74616 | 0.10071 | 0.12817 | 61.821 | -60.9375 | -0.2655 | -0.086975 | -0.082397 | -0.17395 | 0.059509 | -0.31586 | -0.22888 | -0.23346 | -0.086975 | 0.18311
411.5781 | 122.8455 | -60.6812 | 61.853 | 2.4131 | 0.0053508 | 0.0065205 | 0.00029507 | 0.062225 | -0.0030823 | 0.065409 | -60.8276 | 61.7844 | -60.9695 | -60.8505 | 61.6379 | 0.80566 | -0.036621 | 0.17853 | 61.7981 | -60.9375 | -0.28839 | -0.068664 | -0.14649 | -0.16937 | 0.086975 | -0.21515 | -0.16022 | -0.25635 | -0.054931 | 0.14191
412.5781 | 122.8455 | -60.6949 | 61.8988 | -0.058855 | 0.0049236 | 0.0026753 | 0.0011495 | 0.061157 | -0.0026551 | 0.067759 | -60.7727 | 61.821 | -60.9421 | -60.8688 | 61.6013 | 0.76446 | 0.091553 | 0.14191 | 61.8027 | -60.9192 | -0.24719 | -0.07782 | -0.07782 | -0.17395 | 0.050354 | -0.29755 | -0.20142 | -0.2243 | -0.096131 | 0.16937
413.5781 | 122.8088 | -60.704 | 61.8942 | -0.074114 | 0.0059916 | 0.0043843 | 0.0030721 | 0.062225 | -0.0011597 | 0.067118 | -60.7727 | 61.7981 | -60.9421 | -60.8734 | 61.6241 | 0.79193 | 0.068665 | 0.16022 | 61.821 | -60.9512 | -0.23804 | -0.09613 | -0.068664 | -0.16937 | 0.07782 | -0.27008 | -0.19684 | -0.24719 | -0.073242 | 0.16937
414.5781 | 122.8546 | -60.7086 | 61.8805 | -0.035967 | 0.0068462 | 0.0084431 | 0.0039267 | 0.063293 | -0.0026551 | 0.067332 | -60.7819 | 61.8027 | -60.9512 | -60.8505 | 61.6241 | 0.8194 | 0.054932 | 0.15106 | 61.8027 | -60.9421 | -0.24262 | -0.07782 | -0.073242 | -0.14191 | 0.091553 | -0.25635 | -0.17853 | -0.23346 | -0.07782 | 0.16937
415.5781 | 122.7539 | -60.7315 | 61.9125 | 0.070845 | 0.0077006 | 0.0065205 | 0.0026449 | 0.063934 | -0.0011597 | 0.066905 | -60.8139 | 61.8439 | -60.9879 | -60.9192 | 61.5463 | 0.75073 | 0.15106 | 0.059509 | 61.853 | -60.9695 | -0.25635 | -0.068665 | -0.082398 | -0.18768 | 0.050354 | -0.36621 | -0.3067 | -0.23804 | -0.05951 | 0.17395
416.5781 | 122.8363 | -60.6812 | 61.8713 | -0.0054494 | 0.0062052 | -0.00031526 | 0.00050867 | 0.060944 | -0.0005189 | 0.0684 | -60.7681 | 61.8118 | -60.9421 | -60.8414 | 61.6379 | 0.83313 | 0.032043 | 0.17853 | 61.821 | -60.9329 | -0.26093 | -0.059509 | -0.086975 | -0.16022 | 0.091552 | -0.23346 | -0.18311 | -0.25177 | -0.050354 | 0.17395
417.5781 | 122.8775 | -60.6812 | 61.8805 | 0.017439 | 0.0051372 | 0.0011799 | 0.0026449 | 0.06308 | -0.0011597 | 0.066691 | -60.7361 | 61.7935 | -60.9558 | -60.8459 | 61.6379 | 0.85602 | 0.018311 | 0.18768 | 61.8347 | -60.9238 | -0.27466 | -0.086975 | -0.054932 | -0.1648 | 0.07782 | -0.24262 | -0.19684 | -0.24262 | -0.045776 | 0.21973
418.5781 | 122.85 | -60.6903 | 61.8896 | 0.10136 | 0.005778 | 0.0022481 | 0.0043539 | 0.06073 | -0.0028687 | 0.066905 | -60.7544 | 61.7889 | -60.9467 | -60.8368 | 61.647 | 0.86975 | -0.004578 | 0.16479 | 61.8073 | -60.9467 | -0.25635 | -0.10071 | -0.064087 | -0.14648 | 0.10986 | -0.24261 | -0.16022 | -0.25635 | -0.082397 | 0.19226
419.5781 | 122.7997 | -60.704 | 61.908 | -0.10463 | 0.0055644 | 0.00096634 | 0.0020039 | 0.06308 | -0.0032959 | 0.067973 | -60.7956 | 61.8301 | -60.9741 | -60.8826 | 61.5921 | 0.82855 | 0.11902 | 0.10529 | 61.8622 | -60.9695 | -0.27008 | -0.07782 | -0.091552 | -0.17853 | 0.086975 | -0.31586 | -0.27008 | -0.2655 | -0.045776 | 0.17853
420.5781 | 122.7859 | -60.6949 | 61.908 | -0.058855 | 0.0049236 | -0.00031526 | 0.0049947 | 0.061157 | -0.0026551 | 0.066691 | -60.7819 | 61.8301 | -60.9604 | -60.8734 | 61.5875 | 0.85602 | 0.091553 | 0.11902 | 61.8393 | -60.9604 | -0.2655 | -0.07782 | -0.086975 | -0.17853 | 0.086975 | -0.32043 | -0.25177 | -0.2655 | -0.068665 | 0.17853
421.5781 | 122.8592 | -60.6995 | 61.9034 | -0.074114 | 0.0066326 | 0.0073751 | 0.0032857 | 0.064361 | -0.0024415 | 0.066691 | -60.7864 | 61.8256 | -60.9741 | -60.8734 | 61.5967 | 0.8606 | 0.073242 | 0.1236 | 61.8439 | -60.9512 | -0.27466 | -0.077819 | -0.086975 | -0.17395 | 0.07782 | -0.3067 | -0.24719 | -0.25177 | -0.059509 | 0.18768
422.5781 | 122.8317 | -60.7178 | 61.9217 | -0.074114 | 0.0027874 | 0.0016073 | 0.0054219 | 0.062225 | -0.0024415 | 0.070536 | -60.7773 | 61.8164 | -60.9558 | -60.8597 | 61.6333 | 0.88806 | 0.054932 | 0.15106 | 61.821 | -60.9329 | -0.23804 | -0.10529 | -0.05951 | -0.14191 | 0.073242 | -0.28839 | -0.18768 | -0.21515 | -0.10071 | 0.17853
423.5781 | 122.7859 | -60.7315 | 61.9217 | -0.11989 | 0.0055644 | -0.00074266 | 0.0056355 | 0.063293 | -0.0024415 | 0.065837 | -60.8322 | 61.8622 | -60.9604 | -60.9283 | 61.5646 | 0.83313 | 0.14648 | 0.07782 | 61.8668 | -60.9558 | -0.22888 | -0.059509 | -0.10071 | -0.19684 | 0.027466 | -0.35706 | -0.30212 | -0.2243 | -0.054932 | 0.12817
424.5781 | 122.7814 | -60.7498 | 61.8988 | -0.035967 | 0.0072734 | 0.0060933 | 0.0037129 | 0.063934 | -0.0028687 | 0.067546 | -60.8231 | 61.8668 | -60.9741 | -61.1069 | 61.4182 | 0.81482 | 0.18768 | 0.009155 | 61.8439 | -60.997 | -0.2243 | -0.032044 | -0.073242 | -0.35706 | -0.10986 | -0.48065 | -0.42572 | -0.24719 | -0.054932 | 0.15106
425.5781 | 122.8409 | -60.6903 | 61.8622 | 0.025068 | 0.0079142 | 0.0045979 | 0.00029507 | 0.064361 | -0.0015869 | 0.069682 | -60.759 | 61.7981 | -60.9375 | -60.8414 | 61.6425 | 0.94757 | 0.004578 | 0.16937 | 61.8301 | -60.9375 | -0.24719 | -0.064087 | -0.068664 | -0.15106 | 0.09613 | -0.21973 | -0.18768 | -0.24719 | -0.032044 | 0.17853
426.5781 | 122.7951 | -60.7224 | 61.8988 | -0.089373 | 0.0059916 | 0.0039571 | 0.0028585 | 0.06308 | -0.0024415 | 0.068614 | -60.7956 | 61.8484 | -60.9558 | -60.91 | 61.5555 | 0.88348 | 0.1236 | 0.10529 | 61.8484 | -60.9467 | -0.23346 | -0.050354 | -0.073242 | -0.18768 | 0.036621 | -0.34332 | -0.29297 | -0.2243 | -0.050354 | 0.16022
427.5781 | 122.7493 | -60.7544 | 61.908 | -0.081743 | 0.0053508 | 0.0031025 | 0.0049947 | 0.062866 | -0.0026551 | 0.068614 | -60.8231 | 61.8896 | -60.997 | -60.9421 | 61.5326 | 0.86975 | 0.17395 | 0.050354 | 61.8713 | -60.9787 | -0.24261 | -0.018311 | -0.068664 | -0.18768 | 0.036621 | -0.37537 | -0.33875 | -0.2243 | -0.036621 | 0.17395
428.5781 | 122.8134 | -60.6628 | 61.9217 | -0.081743 | 0.0042826 | 0.0086567 | 0.0022177 | 0.062866 | -0.0015869 | 0.067332 | -60.7819 | 61.8439 | -60.9512 | -60.8917 | 61.5967 | 0.93384 | 0.086975 | 0.10986 | 61.853 | -60.965 | -0.28839 | -0.07782 | -0.11902 | -0.22888 | 0.073242 | -0.32501 | -0.25635 | -0.30212 | -0.068665 | 0.16937
429.5781 | 122.7722 | -60.7224 | 61.9217 | 0.0021796 | 0.0066326 | 0.0033161 | 0.0032857 | 0.062866 | -0.0039367 | 0.068187 | -60.8322 | 61.8347 | -60.965 | -60.9283 | 61.5417 | 0.86975 | 0.15564 | 0.064087 | 61.8622 | -60.9833 | -0.24261 | -0.086975 | -0.10986 | -0.20599 | 0.054931 | -0.37994 | -0.32044 | -0.26092 | -0.059509 | 0.13275
430.5781 | 122.818 | -60.7224 | 61.8713 | -0.028338 | 0.0066326 | 0.0020345 | 0.00093587 | 0.062012 | -0.0022277 | 0.068614 | -60.7773 | 61.8073 | -60.9512 | -60.8643 | 61.615 | 0.97504 | 0.068665 | 0.13733 | 61.8713 | -60.9329 | -0.22888 | -0.064087 | -0.054932 | -0.14191 | 0.068664 | -0.25635 | -0.25635 | -0.21057 | 0 | 0.17395
431.5781 | 122.7722 | -60.7315 | 61.8805 | 0.078474 | 0.005778 | 0.0020345 | 0.0034993 | 0.060944 | -0.0026551 | 0.066691 | -60.8231 | 61.8713 | -60.9695 | -60.9238 | 61.528 | 0.90179 | 0.14648 | 0.064087 | 61.8851 | -60.9787 | -0.23804 | -0.009155 | -0.091553 | -0.19226 | 0.054932 | -0.35248 | -0.35706 | -0.24719 | 0.004578 | 0.14648
432.5781 | 122.8455 | -60.704 | 61.8805 | 0.047956 | 0.0062052 | 0.0011799 | 0.0039267 | 0.063721 | -0.0024415 | 0.0684 | -60.7636 | 61.821 | -60.9695 | -60.8414 | 61.6379 | 1.0162 | 0.018311 | 0.16479 | 61.8301 | -60.9558 | -0.2655 | -0.059509 | -0.059509 | -0.13733 | 0.11444 | -0.24262 | -0.19226 | -0.25177 | -0.050354 | 0.20599
433.5781 | 122.7951 | -60.7224 | 61.9171 | -0.028338 | 0.005778 | 0.0033161 | 0.0032857 | 0.062866 | -0.0030823 | 0.066478 | -60.7819 | 61.8256 | -60.9741 | -60.9238 | 61.5646 | 0.95215 | 0.13275 | 0.091553 | 61.8622 | -60.9695 | -0.25177 | -0.091552 | -0.059509 | -0.20142 | 0.045776 | -0.35248 | -0.29755 | -0.24719 | -0.054931 | 0.19226
434.5781 | 122.7722 | -60.7361 | 61.8988 | -0.051226 | 0.0062052 | 0.0020345 | 0.0041403 | 0.063507 | -0.0003051 | 0.068827 | -60.7956 | 61.8256 | -60.9467 | -60.9055 | 61.5921 | 1.0117 | 0.10986 | 0.09613 | 61.8439 | -60.9558 | -0.21057 | -0.073242 | -0.059509 | -0.16937 | 0.050354 | -0.3067 | -0.25177 | -0.21973 | -0.054932 | 0.15106
435.5781 | 122.8271 | -60.7315 | 61.8805 | -0.066485 | 0.0064188 | 0.0045979 | 0.0024313 | 0.061157 | -0.0041503 | 0.067973 | -60.7864 | 61.821 | -60.9558 | -60.878 | 61.5967 | 1.0208 | 0.068665 | 0.11444 | 61.8439 | -60.9512 | -0.2243 | -0.059509 | -0.054932 | -0.14648 | 0.073242 | -0.28381 | -0.24719 | -0.21973 | -0.036621 | 0.16937
436.5781 | 122.8317 | -60.6949 | 61.8713 | 0.0021796 | 0.0049236 | 0.0013935 | 0.0028585 | 0.061371 | -0.0026551 | 0.069896 | -60.7727 | 61.7798 | -60.9375 | -60.8643 | 61.6104 | 1.0437 | 0.064087 | 0.14191 | 61.8347 | -60.9512 | -0.24262 | -0.091553 | -0.07782 | -0.16937 | 0.086975 | -0.26093 | -0.2243 | -0.25635 | -0.036621 | 0.16479
437.5781 | 122.8546 | -60.6766 | 61.8988 | 0.025068 | 0.0055644 | 0.0020345 | 0.0022177 | 0.062652 | -0.0013733 | 0.06605 | -60.7727 | 61.7981 | -60.9558 | -60.8505 | 61.6287 | 1.062 | 0.004578 | 0.15106 | 61.8439 | -60.9467 | -0.27924 | -0.10071 | -0.09613 | -0.17395 | 0.09613 | -0.27008 | -0.21515 | -0.27008 | -0.054932 | 0.18311
438.5781 | 122.9004 | -60.6857 | 61.853 | -0.15804 | 0.0049236 | 0.0060933 | 0.0028585 | 0.061798 | -0.0028687 | 0.064769 | -60.7773 | 61.7889 | -60.9512 | -60.8414 | 61.6333 | 1.062 | -0.018311 | 0.14191 | 61.8027 | -60.965 | -0.2655 | -0.064087 | -0.091553 | -0.15564 | 0.1236 | -0.21973 | -0.16937 | -0.27924 | -0.050354 | 0.17395
439.5781 | 122.8912 | -60.7086 | 61.8851 | 2.23 | 0.0049236 | 0.0033161 | 0.0024313 | 0.060944 | -0.0011597 | 0.0684 | -60.7727 | 61.7889 | -60.9879 | -60.8551 | 61.6379 | 1.1124 | -0.027466 | 0.14191 | 61.8256 | -60.9467 | -0.27924 | -0.096131 | -0.064087 | -0.14648 | 0.091552 | -0.24719 | -0.18768 | -0.23804 | -0.059509 | 0.21515
440.5781 | 122.8638 | -60.7224 | 61.8896 | -0.051226 | 0.005778 | -0.00010166 | 0.0011495 | 0.062652 | 0.0003357 | 0.069468 | -60.7819 | 61.8073 | -60.9375 | -60.8643 | 61.615 | 1.0849 | 0.068665 | 0.11444 | 61.8256 | -60.9421 | -0.21515 | -0.082397 | -0.059509 | -0.14191 | 0.07782 | -0.27466 | -0.21057 | -0.21973 | -0.064086 | 0.15564
441.5781 | 122.818 | -60.7132 | 61.8942 | 0.055586 | 0.0049236 | 0.0022481 | 0.00050867 | 0.061371 | -0.0045777 | 0.067759 | -60.7727 | 61.7706 | -60.9558 | -60.8459 | 61.6058 | 1.1032 | 0.050354 | 0.13733 | 61.8576 | -60.9467 | -0.24261 | -0.1236 | -0.059509 | -0.13275 | 0.10071 | -0.28839 | -0.25177 | -0.23346 | -0.036621 | 0.18311
442.5781 | 122.8638 | -60.704 | 61.8942 | -0.028338 | 0.0042826 | 0.0048115 | 0.0015767 | 0.060303 | -0.0039367 | 0.0684 | -60.7681 | 61.7752 | -60.9512 | -60.8322 | 61.6333 | 1.1307 | 0.018311 | 0.14191 | 61.8256 | -60.9467 | -0.24719 | -0.11902 | -0.064086 | -0.12817 | 0.11444 | -0.26093 | -0.19226 | -0.24261 | -0.068664 | 0.18311
443.5781 | 122.8546 | -60.6812 | 61.8759 | -0.074114 | 0.0051372 | 0.0022481 | 0.0022177 | 0.061371 | -0.0035095 | 0.065837 | -60.759 | 61.7752 | -60.9512 | -60.8551 | 61.6333 | 1.1444 | -0.004578 | 0.15564 | 61.8164 | -60.9192 | -0.27008 | -0.10071 | -0.07782 | -0.17395 | 0.064086 | -0.24261 | -0.1831 | -0.23804 | -0.05951 | 0.19226
444.5781 | 122.8638 | -60.6949 | 61.8713 | 0.58964 | 0.0038554 | 0.0031025 | 0.0032857 | 0.063721 | -0.0035095 | 0.067118 | -60.7498 | 61.7889 | -60.9695 | -60.8368 | 61.647 | 1.1765 | -0.027466 | 0.13275 | 61.7935 | -60.9558 | -0.27466 | -0.082398 | -0.054932 | -0.14191 | 0.11902 | -0.2243 | -0.14648 | -0.26093 | -0.07782 | 0.21973
445.5781 | 122.905 | -60.6949 | 61.8713 | 1.0932 | 0.0062052 | 0.0024617 | 0.0015767 | 0.060516 | -0.0018005 | 0.066478 | -60.7452 | 61.7844 | -60.965 | -60.8459 | 61.647 | 1.1902 | -0.032043 | 0.14648 | 61.8073 | -60.9558 | -0.27008 | -0.086975 | -0.050354 | -0.15106 | 0.10986 | -0.2243 | -0.16022 | -0.26093 | -0.064087 | 0.21973
446.5781 | 122.8592 | -60.6949 | 61.8713 | -0.028338 | 0.0081278 | 0.0016073 | 0.0030721 | 0.060516 | -0.0030823 | 0.068827 | -60.6354 | 61.8301 | -60.9421 | -60.8963 | 61.5784 | 1.149 | -0.041199 | 0.13733 | 61.7935 | -60.9421 | -0.24719 | -0.041199 | 0.059509 | -0.20142 | 0.045777 | -0.29297 | -0.21515 | -0.24719 | -0.07782 | 0.3067
447.5781 | 122.8729 | -60.6857 | 61.8805 | -0.035967 | 0.0055644 | 0.0065205 | 0.0022177 | 0.061798 | -0.0039367 | 0.067759 | -60.7636 | 61.8073 | -60.9604 | -60.8643 | 61.6058 | 1.1719 | 0.050354 | 0.11902 | 61.8073 | -60.9467 | -0.27466 | -0.073242 | -0.07782 | -0.17853 | 0.082397 | -0.27466 | -0.20142 | -0.26093 | -0.073242 | 0.19684
448.5781 | 122.8409 | -60.7086 | 61.8988 | 0.032698 | 0.0053508 | 0.0050251 | 0.0020039 | 0.059448 | -0.0030823 | 0.067546 | -60.7773 | 61.7844 | -60.9741 | -60.8551 | 61.615 | 1.2085 | 0.013733 | 0.14191 | 61.8393 | -60.9467 | -0.2655 | -0.11444 | -0.068665 | -0.14648 | 0.091552 | -0.28381 | -0.2243 | -0.23804 | -0.05951 | 0.19684
449.5781 | 122.8729 | -60.6766 | 61.8713 | 0.063215 | 0.0051372 | 0.0045979 | 0.0024313 | 0.062012 | -0.0032959 | 0.067118 | -60.759 | 61.7798 | -60.9787 | -60.8322 | 61.6379 | 1.2222 | 0 | 0.13733 | 61.8347 | -60.9421 | -0.30212 | -0.091553 | -0.082397 | -0.15564 | 0.10986 | -0.23346 | -0.19684 | -0.2655 | -0.036621 | 0.21973
450.5781 | 122.905 | -60.6949 | 61.8576 | 0.20054 | 0.0053508 | 0.0018209 | 0.0015767 | 0.062652 | -0.0024415 | 0.069041 | -60.759 | 61.7889 | -60.9924 | -60.8688 | 61.6196 | 1.2314 | -0.004578 | 0.12817 | 61.7935 | -60.9558 | -0.29755 | -0.068665 | -0.064087 | -0.17395 | 0.086976 | -0.23804 | -0.17395 | -0.26093 | -0.064087 | 0.23346
451.5781 | 122.7676 | -60.7132 | 61.8805 | -0.051226 | 0.0064188 | 0.0050251 | 0.0041403 | 0.061371 | -0.0054321 | 0.065196 | -60.791 | 61.8027 | -60.9787 | -60.8963 | 61.5692 | 1.2085 | 0.10986 | 0.059509 | 61.8576 | -60.9558 | -0.2655 | -0.07782 | -0.07782 | -0.1831 | 0.05951 | -0.31128 | -0.28839 | -0.24261 | -0.022888 | 0.18768
452.5781 | 122.9004 | -60.6995 | 61.8713 | -0.013079 | 0.0053508 | -0.00010166 | 0.0015767 | 0.059448 | -0.0013733 | 0.068614 | -60.5118 | 61.8347 | -60.9375 | -60.8551 | 61.6653 | 1.268 | -0.059509 | 0.13733 | 61.7981 | -60.9512 | -0.23804 | -0.036621 | 0.18768 | -0.15564 | 0.09613 | -0.20599 | -0.13275 | -0.25177 | -0.073242 | 0.42572
453.5781 | 122.8546 | -60.6812 | 61.8347 | -0.035967 | 0.0053508 | 0.0073751 | 0.00050867 | 0.057526 | -0.0026551 | 0.069468 | -60.7407 | 61.7981 | -60.9421 | -60.9375 | 61.4182 | 1.1078 | 0.045776 | 0.14191 | 61.8301 | -60.9558 | -0.26093 | -0.036621 | -0.05951 | -0.25635 | 0.018311 | -0.41656 | -0.41199 | -0.27466 | -0.004578 | 0.20142
454.5781 | 122.8775 | -60.672 | 61.8576 | 0.063215 | 0.0066326 | 0.0039571 | 0.0034993 | 0.060303 | -0.0035095 | 0.066905 | -60.7864 | 61.8073 | -60.9695 | -60.8505 | 61.6104 | 1.2772 | 0.018311 | 0.11902 | 61.8393 | -60.9558 | -0.29755 | -0.050354 | -0.11444 | -0.17853 | 0.10529 | -0.24719 | -0.22888 | -0.28381 | -0.018311 | 0.18311
455.5781 | 122.8638 | -60.7086 | 61.8668 | -0.0054494 | 0.0066326 | 0.0043843 | 0.00050867 | 0.06073 | -0.0035095 | 0.069255 | -60.7727 | 61.7569 | -60.9741 | -60.8368 | 61.6333 | 1.3046 | 0.009155 | 0.11444 | 61.8118 | -60.9421 | -0.2655 | -0.10986 | -0.064087 | -0.12817 | 0.10529 | -0.23346 | -0.17853 | -0.23346 | -0.054931 | 0.20142
456.5781 | 122.8867 | -60.6857 | 61.8668 | -0.1733 | 0.0059916 | -0.00031526 | 0.0030721 | 0.062652 | -0.0011597 | 0.068187 | -60.8002 | 61.7935 | -60.9558 | -60.8459 | 61.6104 | 1.3092 | -0.032043 | 0.12817 | 61.8073 | -60.9421 | -0.27008 | -0.073242 | -0.11444 | -0.16022 | 0.096131 | -0.25635 | -0.19684 | -0.25635 | -0.059509 | 0.15564
457.5781 | 122.8729 | -60.6949 | 61.8576 | -0.11989 | 0.0053508 | 0.0018209 | 0.0011495 | 0.061584 | -0.0022277 | 0.067332 | -60.7315 | 61.7798 | -60.9604 | -60.8231 | 61.6608 | 1.3504 | -0.045776 | 0.13733 | 61.8118 | -60.9329 | -0.2655 | -0.07782 | -0.036621 | -0.12817 | 0.10986 | -0.19684 | -0.15106 | -0.23804 | -0.045776 | 0.22888
458.5781 | 122.8775 | -60.6949 | 61.8805 | -3.1106 | 0.0062052 | 0.00032554 | 0.00072227 | 0.062225 | -0.0009461 | 0.064769 | -60.6857 | 61.8164 | -60.9329 | -60.8414 | 61.6516 | 1.3641 | -0.07782 | 0.13733 | 61.7844 | -60.9329 | -0.23804 | -0.064087 | 0.009155 | -0.14648 | 0.091552 | -0.22888 | -0.13275 | -0.23804 | -0.09613 | 0.24719
459.5781 | 122.9004 | -60.6812 | 61.8668 | -0.035967 | 0.0051372 | 0.0026753 | 0.0028585 | 0.061798 | -0.0030823 | 0.067332 | -60.7544 | 61.7844 | -60.9283 | -60.7727 | 61.6745 | 1.3458 | -0.07782 | 0.16022 | 61.7981 | -60.9695 | -0.24719 | -0.082397 | -0.073243 | -0.091553 | 0.19684 | -0.19226 | -0.1236 | -0.28839 | -0.068664 | 0.17395
460.5781 | 122.8821 | -60.6949 | 61.8713 | 0.055586 | 0.005778 | 0.0031025 | -0.00098673 | 0.059662 | -0.0022277 | 0.069896 | -60.759 | 61.7706 | -60.9604 | -61.0199 | 61.4365 | 1.3367 | 0.027466 | 0.068665 | 61.8073 | -60.9558 | -0.2655 | -0.10071 | -0.064087 | -0.32501 | -0.064086 | -0.43488 | -0.37079 | -0.26093 | -0.064087 | 0.20142
461.5781 | 122.85 | -60.6857 | 61.8942 | -0.013079 | 0.0038554 | 0.0024617 | 0.0015767 | 0.062866 | -0.0024415 | 0.066905 | -60.759 | 61.7844 | -60.9512 | -60.8643 | 61.6058 | 1.3687 | 0.045776 | 0.11444 | 61.8073 | -60.9375 | -0.2655 | -0.10986 | -0.073242 | -0.17853 | 0.073242 | -0.28839 | -0.20142 | -0.25177 | -0.086975 | 0.19226
462.5781 | 122.8134 | -60.6537 | 61.8759 | 0.0098091 | 0.0019328 | 0.0037435 | 0.0024313 | 0.060089 | -0.0020141 | 0.067332 | -60.7773 | 61.7752 | -60.9604 | -60.8459 | 61.6058 | 1.387 | 0.036621 | 0.10529 | 61.8118 | -60.9421 | -0.3067 | -0.10071 | -0.1236 | -0.19226 | 0.096131 | -0.27008 | -0.20599 | -0.28839 | -0.064087 | 0.18311
463.5781 | 122.8409 | -60.6812 | 61.8851 | -0.035967 | 0.0053508 | -0.0011699 | 0.0013631 | 0.060944 | -0.0037231 | 0.068614 | -60.7727 | 61.821 | -60.9467 | -60.8643 | 61.6104 | 1.4145 | 0.032043 | 0.10529 | 61.8256 | -60.9329 | -0.2655 | -0.064087 | -0.091553 | -0.18311 | 0.068664 | -0.27466 | -0.21515 | -0.25177 | -0.059509 | 0.17395
464.5781 | 122.8592 | -60.6995 | 61.8759 | 0.025068 | 0.0038554 | 0.0060933 | 0.0026449 | 0.061371 | -0.0030823 | 0.067332 | -60.7727 | 61.7706 | -60.9695 | -60.8368 | 61.6241 | 1.4191 | 0.032043 | 0.10986 | 61.8256 | -60.9604 | -0.27008 | -0.10529 | -0.073242 | -0.13733 | 0.1236 | -0.25177 | -0.20142 | -0.26093 | -0.050354 | 0.19684
465.5781 | 122.7722 | -60.7086 | 61.9171 | 0.0021796 | 0.0070598 | 0.0097249 | 0.0041403 | 0.062439 | -0.0039367 | 0.068187 | -60.8185 | 61.8439 | -60.9833 | -60.9283 | 61.5234 | 1.355 | 0.12817 | 0.018311 | 61.8668 | -60.9787 | -0.27466 | -0.073242 | -0.10986 | -0.21973 | 0.050354 | -0.39368 | -0.34332 | -0.27008 | -0.050354 | 0.16479
466.5781 | 122.8592 | -60.6857 | 61.8942 | 0.047956 | 0.0053508 | 0.0043843 | 0.0020039 | 0.062439 | -0.0013733 | 0.0684 | -60.7636 | 61.8256 | -60.9512 | -60.8414 | 61.6333 | 1.4465 | 0.027466 | 0.10529 | 61.8073 | -60.9375 | -0.2655 | -0.068664 | -0.07782 | -0.15564 | 0.09613 | -0.26093 | -0.17395 | -0.25177 | -0.086975 | 0.18768
467.5781 | 122.8455 | -60.7086 | 61.8805 | -0.0054494 | 0.0055644 | 0.0050251 | 0.0024313 | 0.062012 | -0.0026551 | 0.066691 | -60.7544 | 61.7981 | -60.9604 | -60.8368 | 61.6287 | 1.4648 | 0.032043 | 0.10986 | 61.8164 | -60.9558 | -0.25177 | -0.082397 | -0.045777 | -0.12817 | 0.11902 | -0.25177 | -0.18768 | -0.24719 | -0.064087 | 0.20599
468.5781 | 122.7859 | -60.7315 | 61.8805 | 0.040327 | 0.0077006 | 0.0028889 | 0.0034993 | 0.062652 | -0.0020141 | 0.068187 | -60.8047 | 61.853 | -60.965 | -60.9329 | 61.528 | 1.3962 | 0.13733 | 0.013733 | 61.8484 | -60.9879 | -0.23346 | -0.027466 | -0.073243 | -0.20142 | 0.054932 | -0.35248 | -0.32043 | -0.25635 | -0.032043 | 0.16022
469.5781 | 122.7539 | -60.7452 | 61.908 | -0.14278 | 0.0068462 | 0.0071615 | 0.0024313 | 0.065002 | -0.0058593 | 0.069682 | -60.8368 | 61.8439 | -60.9787 | -60.9329 | 61.5372 | 1.4099 | 0.15106 | 0.009155 | 61.8393 | -60.9787 | -0.23346 | -0.064087 | -0.091553 | -0.18768 | 0.045777 | -0.37079 | -0.30212 | -0.23346 | -0.068665 | 0.14191
470.5781 | 122.7448 | -60.7132 | 61.9217 | -0.15804 | 0.007487 | 0.0028889 | 0.0039267 | 0.062439 | -0.0015869 | 0.069041 | -60.8505 | 61.8713 | -60.9787 | -60.9329 | 61.5372 | 1.4191 | 0.14648 | 0.004578 | 61.8668 | -60.997 | -0.2655 | -0.050354 | -0.13733 | -0.21973 | 0.064087 | -0.38452 | -0.32959 | -0.28381 | -0.054932 | 0.12817
471.5781 | 122.7997 | -60.7498 | 61.8942 | 0.055586 | 0.0068462 | 0.0028889 | 0.0037129 | 0.063507 | -0.0039367 | 0.067759 | -60.8276 | 61.8347 | -60.9833 | -60.9375 | 61.5417 | 1.4557 | 0.16479 | -0.004578 | 61.853 | -60.9879 | -0.23346 | -0.059509 | -0.07782 | -0.18768 | 0.050354 | -0.35248 | -0.31128 | -0.23804 | -0.041199 | 0.15564
472.5781 | 122.731 | -60.7178 | 61.8851 | 0.032698 | 0.0064188 | 0.0028889 | 0.0011495 | 0.064148 | -0.0030823 | 0.070323 | -60.8414 | 61.853 | -60.9924 | -60.9375 | 61.528 | 1.4648 | 0.16479 | -0.004578 | 61.853 | -60.9741 | -0.27466 | -0.032044 | -0.1236 | -0.21973 | 0.036621 | -0.35706 | -0.32501 | -0.25635 | -0.032044 | 0.15106
473.5781 | 122.7905 | -60.7407 | 61.8988 | -0.043596 | 0.0096232 | 0.0043843 | 0.00072227 | 0.064575 | -0.0020141 | 0.067546 | -60.8231 | 61.8896 | -61.0062 | -60.9421 | 61.5417 | 1.474 | 0.15564 | 0.013733 | 61.8759 | -60.9833 | -0.2655 | -0.009156 | -0.082397 | -0.20142 | 0.041198 | -0.35706 | -0.33417 | -0.24261 | -0.022888 | 0.18311
474.5781 | 122.7539 | -60.7452 | 61.9125 | -0.058855 | 0.0064188 | 0.0031025 | 0.0037129 | 0.062866 | -0.0039367 | 0.066478 | -60.8276 | 61.8713 | -60.9833 | -60.9467 | 61.5372 | 1.474 | 0.15564 | -0.009155 | 61.8668 | -60.997 | -0.23804 | -0.041199 | -0.082398 | -0.20142 | 0.050354 | -0.37537 | -0.32959 | -0.25177 | -0.045777 | 0.15564
475.5781 | 122.7905 | -60.7544 | 61.8347 | 0.33024 | 0.0081278 | 0.0073751 | 0.0069173 | 0.065216 | -0.0013733 | 0.067759 | -60.8505 | 61.8484 | -61.0336 | -60.9604 | 61.5005 | 1.4145 | -0.073242 | -0.11902 | 61.8118 | -60.997 | -0.27923 | 0.013733 | -0.09613 | -0.20599 | 0.036621 | -0.33417 | -0.31128 | -0.24261 | -0.022888 | 0.18311
476.5781 | 122.7859 | -60.7315 | 61.8759 | 0.12425 | 0.0077006 | 0.0035299 | 0.0062765 | 0.065002 | -0.0009461 | 0.068187 | -60.8231 | 61.8713 | -60.997 | -60.9467 | 61.5189 | 1.506 | 0.15106 | -0.009155 | 61.8668 | -61.0062 | -0.2655 | -0.004578 | -0.091553 | -0.21515 | 0.05951 | -0.35706 | -0.3479 | -0.27466 | -0.009156 | 0.17395
477.5781 | 122.7631 | -60.7315 | 61.8988 | -0.051226 | 0.0079142 | 0.0054525 | 0.0039267 | 0.063507 | -0.0020141 | 0.067546 | -60.8139 | 61.908 | -60.9741 | -60.9467 | 61.5509 | 1.5335 | 0.13275 | -0.027466 | 61.8713 | -61.0107 | -0.24261 | 0.009155 | -0.082398 | -0.21515 | 0.064087 | -0.3479 | -0.32044 | -0.27924 | -0.027466 | 0.16022
478.5781 | 122.818 | -60.7498 | 61.8713 | -0.0054494 | 0.0083416 | 0.0039571 | 0.0054219 | 0.064361 | -0.0030823 | 0.069255 | -60.8368 | 61.8713 | -60.965 | -60.9329 | 61.5417 | 1.5518 | 0.14648 | -0.022888 | 61.8713 | -60.9695 | -0.21515 | 0 | -0.086975 | -0.1831 | 0.036621 | -0.32959 | -0.32959 | -0.21973 | 0 | 0.12817
479.5781 | 122.7951 | -60.7361 | 61.8622 | 0.070845 | 0.010691 | 0.0045979 | 0.0049947 | 0.066498 | -0.0009461 | 0.066264 | -60.7636 | 61.8942 | -60.9879 | -60.9192 | 61.5829 | 1.5839 | 0.064087 | 0.013733 | 61.8439 | -61.0062 | -0.25177 | 0.032043 | -0.027466 | -0.18311 | 0.086976 | -0.27924 | -0.26093 | -0.27008 | -0.018311 | 0.2243
480.5781 | 122.8271 | -60.7315 | 61.8759 | -0.013079 | 0.0081278 | 0.0039571 | 0.0037129 | 0.064148 | -0.0020141 | 0.067546 | -60.8276 | 61.9125 | -60.9833 | -60.9283 | 61.5417 | 1.5747 | 0.12817 | -0.022888 | 61.8668 | -61.0062 | -0.25177 | 0.036621 | -0.096131 | -0.19684 | 0.07782 | -0.33417 | -0.32501 | -0.27466 | -0.009156 | 0.15564
481.5781 | 122.8134 | -60.7452 | 61.8942 | 0.040327 | 0.0087688 | 0.0060933 | 0.0041403 | 0.065643 | -0.0022277 | 0.067118 | -60.8093 | 61.8805 | -60.9879 | -60.9238 | 61.5463 | 1.6022 | 0.12817 | -0.004578 | 61.8942 | -60.9924 | -0.24262 | -0.013733 | -0.064087 | -0.17853 | 0.068665 | -0.3479 | -0.3479 | -0.24719 | 0 | 0.17853
482.5781 | 122.818 | -60.7544 | 61.8713 | 0.10136 | 0.0081278 | 0.0078023 | 0.0062765 | 0.067993 | -0.0030823 | 0.069468 | -60.7773 | 61.8942 | -60.9833 | -60.9009 | 61.5646 | 1.6388 | 0.036621 | -0.004578 | 61.8484 | -60.9833 | -0.22888 | 0.022888 | -0.022888 | -0.14648 | 0.082397 | -0.3067 | -0.28381 | -0.22888 | -0.022888 | 0.20599
483.5781 | 122.8226 | -60.7361 | 61.8622 | 0.11662 | 0.0066326 | 0.0026753 | 0.0049947 | 0.06543 | -0.0026551 | 0.066478 | -60.7727 | 61.8942 | -60.9879 | -60.91 | 61.5646 | 1.6525 | 0.041199 | -0.004578 | 61.8576 | -61.0153 | -0.25177 | 0.032043 | -0.036621 | -0.17395 | 0.10529 | -0.29755 | -0.29297 | -0.27924 | -0.004578 | 0.21515
484.5781 | 122.7768 | -60.7269 | 61.8576 | 0.047956 | 0.010478 | 0.0018209 | 0.0043539 | 0.065643 | -0.0018005 | 0.066905 | -60.7819 | 61.8988 | -60.965 | -60.9283 | 61.5784 | 1.6571 | 0.032043 | -0.009155 | 61.8668 | -61.0107 | -0.23804 | 0.041199 | -0.054931 | -0.20142 | 0.082397 | -0.27924 | -0.28839 | -0.28381 | 0.009155 | 0.18311
485.5781 | 122.8043 | -60.7407 | 61.8484 | 0.093733 | 0.0094096 | 0.0092977 | 0.0037129 | 0.066284 | -0.0018005 | 0.065623 | -60.7819 | 61.9034 | -61.0153 | -60.9055 | 61.5601 | 1.6663 | 0.032043 | -0.013733 | 61.8668 | -60.9924 | -0.27466 | 0.054931 | -0.041198 | -0.16479 | 0.086975 | -0.28839 | -0.3067 | -0.25177 | 0.01831 | 0.23346
486.5781 | 122.7768 | -60.7407 | 61.8301 | 0.10899 | 0.0094096 | 0.0050251 | 0.0024313 | 0.068848 | -0.0039367 | 0.068187 | -60.7864 | 61.8988 | -60.9879 | -60.9467 | 61.5417 | 1.6525 | 0.036621 | -0.064087 | 61.8484 | -61.0153 | -0.24719 | 0.068665 | -0.045776 | -0.20599 | 0.068665 | -0.28839 | -0.3067 | -0.27466 | 0.018311 | 0.20142
487.5781 | 122.8088 | -60.7086 | 61.853 | 0.10899 | 0.012187 | 0.0090841 | 0.0039267 | 0.067779 | 0.0016175 | 0.067759 | -60.7681 | 61.8942 | -60.9787 | -60.9329 | 61.5417 | 1.6983 | 0.032043 | -0.027466 | 61.8622 | -61.0336 | -0.27008 | 0.041199 | -0.059509 | -0.2243 | 0.10071 | -0.31128 | -0.32044 | -0.32501 | 0.009156 | 0.21057
488.5781 | 122.7814 | -60.7224 | 61.8439 | 0.18529 | 0.0089824 | 0.0073751 | 0.0064901 | 0.066925 | -0.0024415 | 0.067759 | -60.7773 | 61.908 | -60.997 | -60.9558 | 61.5143 | 1.6663 | 0.041199 | -0.073242 | 61.8759 | -61.0199 | -0.27466 | 0.064087 | -0.054932 | -0.23346 | 0.064086 | -0.32959 | -0.36163 | -0.29755 | 0.032044 | 0.21973
489.5781 | 122.7631 | -60.7452 | 61.853 | 0.17766 | 0.0089824 | 0.0054525 | 0.0043539 | 0.066284 | -0.0005189 | 0.070536 | -60.791 | 61.8851 | -60.9879 | -60.9558 | 61.5189 | 1.6663 | 0.032043 | -0.091553 | 61.8713 | -61.0428 | -0.24262 | 0.032044 | -0.045777 | -0.21057 | 0.086975 | -0.33417 | -0.35248 | -0.29755 | 0.018311 | 0.19684
490.5781 | 122.7631 | -60.7361 | 61.8622 | 0.19291 | 0.0089824 | 0.0039571 | 0.0039267 | 0.068848 | -0.0005189 | 0.068827 | -60.8047 | 61.8942 | -60.9924 | -60.9512 | 61.5189 | 1.6846 | 0.027466 | -0.10071 | 61.8805 | -61.0336 | -0.25635 | 0.032043 | -0.068665 | -0.21515 | 0.082397 | -0.34332 | -0.36163 | -0.29755 | 0.01831 | 0.18768
491.5781 | 122.7631 | -60.7681 | 61.8622 | 0.20054 | 0.011119 | 0.0067341 | 0.0049947 | 0.067993 | -0.0009461 | 0.069896 | -60.7956 | 61.9171 | -60.9879 | -60.9604 | 61.5005 | 1.712 | 0.027466 | -0.091553 | 61.8668 | -61.0474 | -0.21973 | 0.054931 | -0.027466 | -0.19226 | 0.086975 | -0.36163 | -0.36621 | -0.27924 | 0.004577 | 0.19226
492.5781 | 122.8134 | -60.7544 | 61.8484 | 0.17766 | 0.01005 | 0.0075887 | 0.0062765 | 0.067139 | -0.0024415 | 0.068614 | -60.8002 | 61.9034 | -60.9833 | -60.9604 | 61.5143 | 1.7166 | 0.032043 | -0.09613 | 61.8713 | -61.0107 | -0.22888 | 0.054931 | -0.045776 | -0.20599 | 0.050354 | -0.33417 | -0.35706 | -0.25635 | 0.022888 | 0.1831
493.5781 | 122.7768 | -60.7452 | 61.8805 | 0.17003 | 0.0094096 | 0.0073751 | 0.0052083 | 0.069061 | -0.0037231 | 0.068827 | -60.8047 | 61.9171 | -61.0107 | -60.9604 | 61.5189 | 1.7303 | 0.041199 | -0.091553 | 61.8622 | -61.0565 | -0.2655 | 0.036621 | -0.05951 | -0.21515 | 0.096131 | -0.36163 | -0.34332 | -0.31128 | -0.01831 | 0.20599
494.5781 | 122.7585 | -60.7315 | 61.8622 | 0.19291 | 0.0096232 | 0.0052387 | 0.0047811 | 0.066925 | -0.0024415 | 0.067546 | -60.7956 | 61.8988 | -61.0016 | -60.9604 | 61.528 | 1.7532 | 0.009155 | -0.086975 | 61.8851 | -61.0382 | -0.27008 | 0.036621 | -0.064087 | -0.22888 | 0.07782 | -0.33417 | -0.35706 | -0.3067 | 0.022888 | 0.20599
495.5781 | 122.7722 | -60.7727 | 61.853 | 0.23106 | 0.010478 | 0.0060933 | 0.0043539 | 0.068634 | -0.0011597 | 0.067759 | -60.8414 | 61.9171 | -60.997 | -60.9924 | 61.4594 | 1.7075 | 0.041199 | -0.15106 | 61.8988 | -61.0565 | -0.2243 | 0.064087 | -0.068665 | -0.21973 | 0.064087 | -0.39368 | -0.43945 | -0.28381 | 0.045777 | 0.15564
496.5781 | 122.731 | -60.7681 | 61.853 | 0.26921 | 0.0085552 | 0.012288 | 0.0067037 | 0.066284 | -0.0005189 | 0.069041 | -60.8505 | 61.9125 | -61.0245 | -61.0107 | 61.4502 | 1.7258 | 0.041199 | -0.14191 | 61.9034 | -61.0611 | -0.25635 | 0.05951 | -0.082398 | -0.24262 | 0.050354 | -0.40283 | -0.45319 | -0.29297 | 0.050354 | 0.17395
497.5781 | 122.7814 | -60.7498 | 61.821 | 0.25395 | 0.0098368 | 0.0075887 | 0.0045675 | 0.06543 | 0.0005493 | 0.069255 | -60.8414 | 61.8942 | -61.0107 | -60.997 | 61.4777 | 1.7578 | 0.045776 | -0.15106 | 61.8805 | -61.0611 | -0.26093 | 0.073242 | -0.091553 | -0.24719 | 0.064087 | -0.34332 | -0.40283 | -0.31128 | 0.059509 | 0.16937
498.5781 | 122.7585 | -60.7498 | 61.8713 | 0.23106 | 0.0098368 | 0.0073751 | 0.0045675 | 0.067352 | -0.0022277 | 0.068827 | -60.8322 | 61.8851 | -60.9833 | -60.9879 | 61.4777 | 1.7578 | 0.050354 | -0.12817 | 61.8713 | -61.0611 | -0.23346 | 0.013733 | -0.082397 | -0.23804 | 0.073242 | -0.39368 | -0.39368 | -0.31128 | 0 | 0.15106
499.5781 | 122.7631 | -60.7407 | 61.8256 | 0.20054 | 0.0083416 | 0.0097249 | 0.0067037 | 0.068207 | -0.0050049 | 0.069041 | -60.8231 | 61.9034 | -60.997 | -60.9924 | 61.4868 | 1.7944 | 0.036621 | -0.14648 | 61.8988 | -61.0519 | -0.25635 | 0.077819 | -0.082397 | -0.25177 | 0.059509 | -0.33875 | -0.41199 | -0.31128 | 0.073242 | 0.17395
500.5781 | 122.7768 | -60.7407 | 61.8668 | 0.26921 | 0.010478 | 0.0071615 | 0.0049947 | 0.065857 | -0.0003051 | 0.068187 | -60.8047 | 61.9217 | -61.0107 | -60.9879 | 61.4868 | 1.8127 | 0.050354 | -0.12817 | 61.8622 | -61.0611 | -0.27008 | 0.054932 | -0.064087 | -0.24719 | 0.073242 | -0.37994 | -0.37537 | -0.32043 | -0.004577 | 0.20599
501.5781 | 122.7859 | -60.7361 | 61.8622 | 0.20054 | 0.0089824 | 0.010152 | 0.0047811 | 0.067352 | -0.0015869 | 0.0684 | -60.8139 | 61.8942 | -60.9924 | -60.9787 | 61.4777 | 1.8539 | 0.041199 | -0.11444 | 61.8668 | -61.0748 | -0.25635 | 0.032043 | -0.07782 | -0.24262 | 0.09613 | -0.38452 | -0.3891 | -0.33875 | 0.004577 | 0.17853
502.5781 | 122.7676 | -60.7681 | 61.8668 | 0.23106 | 0.011759 | 0.0099385 | 0.0030721 | 0.067352 | 0.0001221 | 0.067759 | -60.8597 | 61.9125 | -61.0153 | -61.0062 | 61.4548 | 1.8173 | 0.054932 | -0.16022 | 61.8896 | -61.0703 | -0.24719 | 0.045777 | -0.091553 | -0.23804 | 0.064086 | -0.41199 | -0.43487 | -0.30212 | 0.022888 | 0.15564
503.5781 | 122.7493 | -60.7727 | 61.8576 | 0.20817 | 0.010905 | 0.01122 | 0.0054219 | 0.066498 | -0.0005189 | 0.069255 | -60.8368 | 61.9034 | -61.0107 | -61.0016 | 61.4777 | 1.8448 | 0.032043 | -0.16479 | 61.8668 | -61.084 | -0.23804 | 0.045776 | -0.064087 | -0.22888 | 0.082397 | -0.37994 | -0.3891 | -0.31128 | 0.009155 | 0.17395
504.5781 | 122.7997 | -60.7498 | 61.8713 | 0.22343 | 0.010478 | 0.0075887 | 0.0075581 | 0.068634 | -0.0026551 | 0.0684 | -60.8139 | 61.908 | -61.0245 | -60.9924 | 61.4731 | 1.8631 | 0.050354 | -0.13275 | 61.8896 | -61.0794 | -0.27466 | 0.036621 | -0.064087 | -0.24262 | 0.086975 | -0.39825 | -0.41656 | -0.32959 | 0.01831 | 0.21057
505.5781 | 122.7539 | -60.7636 | 61.8439 | 0.23106 | 0.0098368 | 0.0082295 | 0.0043539 | 0.06607 | -0.0013733 | 0.068614 | -60.8139 | 61.8988 | -60.997 | -60.9833 | 61.4868 | 1.8951 | 0.027466 | -0.13275 | 61.8622 | -61.0748 | -0.23346 | 0.054932 | -0.050354 | -0.21973 | 0.091553 | -0.35706 | -0.37537 | -0.31128 | 0.018311 | 0.1831
506.5781 | 122.7859 | -60.7407 | 61.8576 | 0.17003 | 0.0096232 | 0.0037435 | 0.0049947 | 0.066925 | -0.0020141 | 0.067759 | -60.8002 | 61.8988 | -61.0153 | -60.9604 | 61.496 | 1.9363 | 0.032043 | -0.11444 | 61.8851 | -61.0703 | -0.27466 | 0.041199 | -0.059509 | -0.21973 | 0.10986 | -0.36163 | -0.3891 | -0.32959 | 0.027466 | 0.21515
507.5781 | 122.85 | -60.7407 | 61.8759 | 0.047956 | 0.009196 | 0.0069477 | 0.0041403 | 0.066925 | -0.0041503 | 0.068614 | -60.7773 | 61.8805 | -61.0016 | -60.9421 | 61.5234 | 1.9821 | 0.022888 | -0.07782 | 61.8805 | -61.0565 | -0.26093 | 0.004577 | -0.036621 | -0.20142 | 0.11444 | -0.35248 | -0.35706 | -0.31586 | 0.004577 | 0.2243
508.5781 | 122.7951 | -60.7269 | 61.853 | 0.17003 | 0.01005 | 0.0078023 | 0.0073445 | 0.066711 | 0.0003357 | 0.069041 | -60.8551 | 61.8759 | -60.9924 | -60.91 | 61.5097 | 1.9775 | 0.050354 | -0.059509 | 61.8851 | -61.0245 | -0.2655 | 0.022889 | -0.12817 | -0.18311 | 0.11444 | -0.34332 | -0.37537 | -0.29755 | 0.032044 | 0.13733
509.5781 | 122.7997 | -60.7544 | 61.8668 | 0.15477 | 0.0098368 | 0.0052387 | 0.0052083 | 0.065857 | -0.0007325 | 0.069041 | -60.7956 | 61.9034 | -60.9879 | -60.9695 | 61.5097 | 1.9455 | 0.032043 | -0.1236 | 61.8759 | -61.0565 | -0.23346 | 0.036621 | -0.041198 | -0.21515 | 0.086976 | -0.35706 | -0.36621 | -0.30212 | 0.009156 | 0.19226
510.5781 | 122.7722 | -60.7269 | 61.8668 | 0.17766 | 0.0096232 | 0.0063069 | 0.0073445 | 0.067139 | -0.0026551 | 0.068827 | -60.7727 | 61.9354 | -60.9833 | -60.9467 | 61.528 | 1.9958 | 0.050354 | -0.091553 | 61.9125 | -61.0474 | -0.25635 | 0.068665 | -0.045776 | -0.21973 | 0.10071 | -0.33874 | -0.38452 | -0.32043 | 0.045777 | 0.21057
511.5781 | 122.7814 | -60.7269 | 61.8622 | 1.6425 | 0.010691 | 0.0058797 | 0.0045675 | 0.06842 | -0.0030823 | 0.065837 | -60.7407 | 61.9034 | -61.0291 | -60.9329 | 61.5234 | 2.0508 | 0.032043 | -0.073242 | 61.8805 | -61.0474 | -0.30212 | 0.041198 | -0.013733 | -0.20599 | 0.11444 | -0.33875 | -0.35706 | -0.32043 | 0.01831 | 0.28839
512.5781 | 122.818 | -60.7544 | 61.8759 | 0.13188 | 0.0081278 | 0.010793 | 0.0045675 | 0.064789 | -0.0024415 | 0.067118 | -60.7636 | 61.8988 | -61.0016 | -60.9375 | 61.441 | 1.9638 | 0.11444 | -0.045776 | 61.8759 | -61.0382 | -0.24719 | 0.022888 | -0.009155 | -0.1831 | 0.10071 | -0.43488 | -0.43488 | -0.28381 | 0 | 0.23804
513.5781 | 122.7814 | -60.7361 | 61.8805 | 0.093733 | 0.010478 | 0.0071615 | 0.0052083 | 0.066498 | -0.0007325 | 0.064555 | -60.7636 | 61.8988 | -61.0062 | -60.9283 | 61.5372 | 2.0828 | 0.036621 | -0.054932 | 61.8713 | -61.0428 | -0.27008 | 0.018311 | -0.027466 | -0.19226 | 0.11444 | -0.34332 | -0.33417 | -0.3067 | -0.009155 | 0.24262
514.5781 | 122.8134 | -60.7178 | 61.8805 | 0.0021796 | 0.0077006 | 0.0050251 | 0.0039267 | 0.06607 | -0.0026551 | 0.068187 | -60.7819 | 61.9171 | -61.0016 | -60.9192 | 61.5463 | 2.1149 | 0.045776 | -0.059509 | 61.9034 | -61.0245 | -0.28381 | 0.036621 | -0.064087 | -0.20142 | 0.10529 | -0.33417 | -0.35706 | -0.3067 | 0.022888 | 0.21973
515.5781 | 122.7814 | -60.7361 | 61.8622 | 0.063215 | 0.0089824 | 0.0065205 | 0.0022177 | 0.066711 | -0.0030823 | 0.067546 | -60.791 | 61.9171 | -60.9604 | -60.9329 | 61.5509 | 2.1286 | 0.086975 | -0.036621 | 61.9171 | -61.0062 | -0.2243 | 0.054931 | -0.054932 | -0.19684 | 0.073243 | -0.31128 | -0.36621 | -0.27008 | 0.054931 | 0.16937
516.5781 | 122.7997 | -60.7269 | 61.8622 | 0.11662 | 0.0094096 | 0.0024617 | 0.0041403 | 0.06842 | -0.0005189 | 0.067332 | -60.7727 | 61.8988 | -60.997 | -60.9146 | 61.5326 | 2.1286 | 0.041199 | -0.059509 | 61.8805 | -61.0336 | -0.27008 | 0.036621 | -0.045776 | -0.18768 | 0.11902 | -0.32959 | -0.3479 | -0.3067 | 0.01831 | 0.2243
517.5781 | 122.8043 | -60.7407 | 61.8851 | 0.025068 | 0.010478 | 0.0050251 | 0.0039267 | 0.066284 | -0.0020141 | 0.069468 | -60.7636 | 61.9034 | -61.0016 | -60.9375 | 61.5326 | 2.1652 | 0.041199 | -0.054932 | 61.8942 | -61.0336 | -0.26093 | 0.01831 | -0.022888 | -0.19684 | 0.09613 | -0.35248 | -0.36163 | -0.29297 | 0.009155 | 0.23804
518.5781 | 122.8226 | -60.7315 | 61.8805 | 0.047956 | 0.0094096 | 0.0060933 | 0.0043539 | 0.066711 | -0.0043641 | 0.066691 | -60.7819 | 61.9217 | -60.9787 | -60.9283 | 61.5509 | 2.1698 | 0.082397 | -0.054932 | 61.9171 | -61.0382 | -0.24719 | 0.041199 | -0.050354 | -0.19684 | 0.10986 | -0.32959 | -0.36621 | -0.3067 | 0.036621 | 0.19684
519.5781 | 122.8043 | -60.7224 | 61.8851 | 0.0098091 | 0.0089824 | 0.0039571 | 0.0064901 | 0.067139 | -0.0020141 | 0.067546 | -60.8047 | 61.9034 | -60.9924 | -60.9192 | 61.5417 | 2.179 | 0.10529 | -0.068665 | 61.9034 | -61.0382 | -0.27008 | 0.01831 | -0.082398 | -0.19684 | 0.11902 | -0.34332 | -0.36163 | -0.31586 | 0.01831 | 0.18768
520.5781 | 122.7676 | -60.7132 | 61.8988 | 0.032698 | 0.0077006 | 0.0020345 | 0.0045675 | 0.065857 | -0.0030823 | 0.066905 | -60.8185 | 61.9034 | -60.9924 | -60.9421 | 61.5189 | 2.1973 | 0.11902 | -0.068665 | 61.9125 | -60.997 | -0.27924 | 0.004577 | -0.10528 | -0.22888 | 0.054931 | -0.37994 | -0.39368 | -0.28381 | 0.013733 | 0.17395
521.5781 | 122.8134 | -60.7361 | 61.9125 | 0.025068 | 0.007487 | 0.0065205 | 0.0028585 | 0.067139 | -0.0015869 | 0.066691 | -60.8276 | 61.9125 | -60.997 | -60.9421 | 61.5143 | 2.2064 | 0.13275 | -0.07782 | 61.94 | -61.0291 | -0.26093 | 0 | -0.091553 | -0.20599 | 0.086975 | -0.39825 | -0.42572 | -0.29297 | 0.027465 | 0.16937
522.5781 | 122.7905 | -60.7407 | 61.8805 | 0.0098091 | 0.010478 | 0.0060933 | 0.0020039 | 0.065857 | -9.1495e-05 | 0.069255 | -60.8276 | 61.9217 | -60.9924 | -60.965 | 61.5234 | 2.2018 | 0.13733 | -0.091553 | 61.9217 | -61.0382 | -0.25177 | 0.041199 | -0.086975 | -0.2243 | 0.073242 | -0.35706 | -0.39825 | -0.29755 | 0.041199 | 0.16479
523.5781 | 122.7997 | -60.7086 | 61.8713 | 0.025068 | 0.0079142 | 0.0067341 | 0.0024313 | 0.064789 | -0.0013733 | 0.068614 | -60.7819 | 61.9263 | -60.9695 | -60.9238 | 61.5372 | 2.2385 | 0.07782 | -0.059509 | 61.8988 | -61.0245 | -0.26093 | 0.054932 | -0.073242 | -0.21515 | 0.10071 | -0.33417 | -0.36163 | -0.31586 | 0.027466 | 0.18768
524.5781 | 122.818 | -60.7407 | 61.8851 | 0.0021796 | 0.0094096 | 0.0041707 | 0.0022177 | 0.067139 | -0.0005189 | 0.066478 | -60.7956 | 61.9034 | -60.9833 | -60.9192 | 61.5509 | 2.2614 | 0.082397 | -0.068665 | 61.9034 | -61.0107 | -0.24261 | 0.01831 | -0.054931 | -0.17853 | 0.091553 | -0.33417 | -0.35248 | -0.27008 | 0.01831 | 0.18768
525.5781 | 122.7722 | -60.7315 | 61.8896 | -0.051226 | 0.0059916 | 0.0043843 | 0.0054219 | 0.066284 | -0.0020141 | 0.068187 | -60.8002 | 61.8988 | -61.0199 | -60.9375 | 61.5372 | 2.2568 | 0.10071 | -0.07782 | 61.9171 | -61.0245 | -0.28839 | 0.009156 | -0.068665 | -0.20599 | 0.086975 | -0.35248 | -0.37994 | -0.29297 | 0.027466 | 0.21973
526.5781 | 122.85 | -60.7315 | 61.8805 | 0.0098091 | 0.0077006 | 0.0018209 | 0.0028585 | 0.067139 | -0.0015869 | 0.068614 | -60.8093 | 61.9125 | -60.9879 | -60.9421 | 61.5234 | 2.2476 | 0.12817 | -0.09613 | 61.9263 | -61.0062 | -0.25635 | 0.032044 | -0.07782 | -0.21057 | 0.064087 | -0.35706 | -0.40283 | -0.27466 | 0.045777 | 0.17853
527.5781 | 122.7676 | -60.7224 | 61.8713 | 0.0021796 | 0.0087688 | 0.0050251 | 0.0028585 | 0.064789 | -9.1495e-05 | 0.069041 | -60.8185 | 61.9034 | -60.997 | -60.9467 | 61.5189 | 2.2659 | 0.1236 | -0.10529 | 61.9125 | -61.0107 | -0.27466 | 0.032043 | -0.09613 | -0.2243 | 0.064087 | -0.35248 | -0.39368 | -0.28839 | 0.041199 | 0.17853
528.5781 | 122.8088 | -60.7269 | 61.8851 | -0.051226 | 0.010478 | 0.0069477 | 0.0024313 | 0.066498 | 0.0001221 | 0.067759 | -60.8276 | 61.9263 | -60.9695 | -60.9604 | 61.5051 | 2.2705 | 0.1236 | -0.10986 | 61.908 | -61.0428 | -0.24261 | 0.041199 | -0.10071 | -0.23346 | 0.082398 | -0.37994 | -0.40283 | -0.31586 | 0.022888 | 0.14191
529.5781 | 122.8088 | -60.7361 | 61.9125 | 0.040327 | 0.0072734 | 0.0033161 | 0.00072227 | 0.065857 | 0.0001221 | 0.065409 | -60.8185 | 61.908 | -60.997 | -60.9512 | 61.5234 | 2.3026 | 0.14191 | -0.10986 | 61.9308 | -61.0153 | -0.26093 | -0.004578 | -0.082397 | -0.21515 | 0.064087 | -0.3891 | -0.40741 | -0.27924 | 0.01831 | 0.17853
530.5781 | 122.8271 | -60.7361 | 61.8896 | -0.0054494 | 0.0079142 | 0.0097249 | 0.0022177 | 0.065643 | -0.0013733 | 0.068614 | -60.7864 | 61.9125 | -60.9879 | -60.91 | 61.5509 | 2.33 | 0.07782 | -0.07782 | 61.9125 | -61.0107 | -0.25177 | 0.022889 | -0.050354 | -0.17395 | 0.10071 | -0.33875 | -0.36163 | -0.27466 | 0.022889 | 0.20142
531.5781 | 122.8455 | -60.7178 | 61.853 | -0.0054494 | 0.0087688 | 0.0041707 | 0.0034993 | 0.065857 | -0.0020141 | 0.068187 | -60.7819 | 61.9034 | -60.9833 | -60.91 | 61.5555 | 2.3483 | 0.07782 | -0.07782 | 61.8851 | -61.0199 | -0.2655 | 0.050354 | -0.064087 | -0.19226 | 0.10986 | -0.29755 | -0.32959 | -0.30212 | 0.032044 | 0.20142
532.5781 | 122.7951 | -60.7315 | 61.8759 | -0.028338 | 0.0070598 | 0.0052387 | 0.0026449 | 0.065643 | -0.0015869 | 0.068614 | -60.7864 | 61.8988 | -60.9924 | -60.91 | 61.5463 | 2.3621 | 0.086975 | -0.073242 | 61.9034 | -61.0153 | -0.26093 | 0.022888 | -0.054932 | -0.17853 | 0.10529 | -0.32959 | -0.35706 | -0.28381 | 0.027465 | 0.20599
533.5781 | 122.7859 | -60.7315 | 61.8896 | 0.0098091 | 0.0094096 | 0.0067341 | 0.0017903 | 0.066711 | -0.0015869 | 0.069255 | -60.8002 | 61.9125 | -61.0016 | -60.9192 | 61.5417 | 2.3529 | 0.10529 | -0.082397 | 61.9171 | -61.0016 | -0.27008 | 0.022889 | -0.068665 | -0.18768 | 0.082398 | -0.3479 | -0.37537 | -0.27008 | 0.027466 | 0.20142
534.5781 | 122.7997 | -60.7269 | 61.8851 | 0.0098091 | 0.010264 | 0.0043843 | 0.0034993 | 0.065643 | -9.1495e-05 | 0.070323 | -60.8139 | 61.8942 | -60.9879 | -60.91 | 61.5463 | 2.3575 | 0.11444 | -0.09613 | 61.9308 | -60.9924 | -0.26093 | 0.009155 | -0.086975 | -0.18311 | 0.082398 | -0.33875 | -0.38452 | -0.2655 | 0.045776 | 0.17395
535.5781 | 122.7768 | -60.7086 | 61.9171 | 0.0021796 | 0.009196 | 0.0039571 | 0.0013631 | 0.067139 | -0.0015869 | 0.068614 | -60.8093 | 61.9125 | -60.9741 | -60.9421 | 61.5097 | 2.3621 | 0.1236 | -0.11444 | 61.9308 | -61.0245 | -0.2655 | -0.004577 | -0.10071 | -0.23346 | 0.082397 | -0.40741 | -0.42114 | -0.31586 | 0.013733 | 0.16479
536.5781 | 122.8226 | -60.7315 | 61.8805 | 0.025068 | 0.010691 | 0.0067341 | 0.0028585 | 0.064361 | -0.0005189 | 0.0684 | -60.8185 | 61.9263 | -60.9741 | -60.9558 | 61.5326 | 2.3804 | 0.13733 | -0.1236 | 61.9263 | -61.0016 | -0.24261 | 0.045777 | -0.086975 | -0.2243 | 0.045776 | -0.3479 | -0.39368 | -0.27008 | 0.045777 | 0.15564
537.5781 | 122.8088 | -60.6949 | 61.8896 | 0.047956 | 0.0089824 | 0.00096634 | 0.0047811 | 0.066284 | -0.0003051 | 0.0684 | -60.7773 | 61.9125 | -60.997 | -60.8963 | 61.5692 | 2.4261 | 0.068665 | -0.086975 | 61.8942 | -61.0291 | -0.30212 | 0.022889 | -0.082398 | -0.20142 | 0.13275 | -0.32043 | -0.32501 | -0.33417 | 0.004578 | 0.21973
538.5781 | 122.8409 | -60.7315 | 61.8759 | 0.017439 | 0.0068462 | 0.0039571 | 0.0039267 | 0.06607 | -0.0020141 | 0.066478 | -60.7819 | 61.9308 | -60.9695 | -60.91 | 61.5601 | 2.4307 | 0.086975 | -0.082397 | 61.908 | -61.0153 | -0.23804 | 0.054931 | -0.050354 | -0.17853 | 0.10529 | -0.31586 | -0.3479 | -0.28381 | 0.032043 | 0.18768
539.5781 | 122.8088 | -60.7178 | 61.8851 | 0.0098091 | 0.0085552 | 0.0052387 | 0.0052083 | 0.06607 | -0.0020141 | 0.067759 | -60.7773 | 61.9217 | -60.9787 | -60.91 | 61.5372 | 2.4399 | 0.082397 | -0.082397 | 61.9263 | -61.0062 | -0.26093 | 0.036621 | -0.05951 | -0.19226 | 0.096131 | -0.3479 | -0.3891 | -0.28839 | 0.041199 | 0.20142
540.5781 | 122.7859 | -60.7224 | 61.8942 | -0.035967 | 0.01005 | 0.0054525 | 0.0034993 | 0.064789 | -0.0018005 | 0.067118 | -60.7956 | 61.9125 | -60.9741 | -60.91 | 61.5509 | 2.4399 | 0.11444 | -0.091553 | 61.9217 | -61.0199 | -0.25177 | 0.018311 | -0.073242 | -0.18768 | 0.10986 | -0.34332 | -0.37079 | -0.29755 | 0.027466 | 0.17853
541.5781 | 122.7997 | -60.7269 | 61.8896 | 0.13951 | 0.010691 | 0.0058797 | 0.0039267 | 0.067993 | 0.0005493 | 0.069255 | -60.7636 | 61.9171 | -60.9879 | -60.9192 | 61.5463 | 2.4445 | 0.032043 | -0.10071 | 61.908 | -61.0336 | -0.26093 | 0.027466 | -0.036621 | -0.19226 | 0.11444 | -0.34332 | -0.36163 | -0.3067 | 0.018311 | 0.2243
542.5781 | 122.7585 | -60.7315 | 61.8942 | -0.013079 | 0.0098368 | 0.0028889 | 0.0030721 | 0.066284 | -0.0020141 | 0.068614 | -60.7864 | 61.9354 | -60.9558 | -60.9375 | 61.528 | 2.4582 | 0.13733 | -0.11444 | 61.9308 | -61.0153 | -0.2243 | 0.041199 | -0.054932 | -0.20599 | 0.07782 | -0.36621 | -0.40283 | -0.28381 | 0.036621 | 0.16937
543.5781 | 122.8088 | -60.7086 | 61.9125 | -0.013079 | 0.010691 | 0.00075274 | 0.0049947 | 0.067139 | -9.1495e-05 | 0.067546 | -60.8093 | 61.9125 | -60.9833 | -60.9375 | 61.5463 | 2.4582 | 0.13275 | -0.12817 | 61.908 | -61.0153 | -0.27466 | 0 | -0.10071 | -0.22888 | 0.07782 | -0.36621 | -0.36163 | -0.3067 | -0.004578 | 0.17395
544.5781 | 122.7768 | -60.7269 | 61.8851 | 0.055586 | 0.0089824 | 0.0043843 | 0.0041403 | 0.065216 | -0.0009461 | 0.067546 | -60.7636 | 61.9034 | -60.9558 | -60.9055 | 61.5601 | 2.4948 | 0.054932 | -0.10529 | 61.8942 | -61.0199 | -0.22888 | 0.01831 | -0.036621 | -0.17853 | 0.11444 | -0.32501 | -0.33417 | -0.29297 | 0.009155 | 0.19226
545.5781 | 122.8226 | -60.7132 | 61.8759 | 0.0021796 | 0.010905 | 0.0065205 | 0.0026449 | 0.06543 | -0.0018005 | 0.066264 | -60.7681 | 61.8896 | -60.9787 | -60.8963 | 61.5372 | 2.4857 | 0.073242 | -0.091553 | 61.9034 | -61.0107 | -0.2655 | 0.013732 | -0.054931 | -0.1831 | 0.11444 | -0.33875 | -0.36621 | -0.29755 | 0.027465 | 0.21057
546.5781 | 122.8226 | -60.7315 | 61.8896 | -0.0054494 | 0.0066326 | 0.0041707 | 0.0011495 | 0.06543 | -0.0030823 | 0.068614 | -60.7727 | 61.9446 | -60.9695 | -60.9009 | 61.5601 | 2.5085 | 0.091553 | -0.082397 | 61.9171 | -61.0016 | -0.23804 | 0.054932 | -0.041199 | -0.16937 | 0.10071 | -0.32959 | -0.35705 | -0.27008 | 0.027466 | 0.19684
547.5781 | 122.7859 | -60.7315 | 61.8942 | -0.020708 | 0.0064188 | 0.0037435 | 0.0024313 | 0.067139 | 0.0005493 | 0.067973 | -60.7773 | 61.9308 | -60.9924 | -60.9146 | 61.5692 | 2.5177 | 0.091553 | -0.10071 | 61.9308 | -61.0153 | -0.26093 | 0.036621 | -0.045777 | -0.18311 | 0.10071 | -0.32501 | -0.36163 | -0.28381 | 0.036621 | 0.21515
548.5781 | 122.818 | -60.7315 | 61.8805 | 0.10899 | 0.0079142 | 0.0075887 | 0.0058493 | 0.066498 | -0.0039367 | 0.067973 | -60.759 | 61.8942 | -60.9741 | -60.9055 | 61.5555 | 2.5131 | 0.027466 | -0.10529 | 61.8896 | -61.0474 | -0.24261 | 0.013733 | -0.027466 | -0.17395 | 0.14191 | -0.32501 | -0.33417 | -0.31586 | 0.009155 | 0.21515
549.5781 | 122.7951 | -60.7224 | 61.8759 | 0.017439 | 0.0081278 | 0.0056661 | 0.0026449 | 0.066284 | -9.1495e-05 | 0.0684 | -60.7773 | 61.9354 | -60.9787 | -60.9009 | 61.5646 | 2.5314 | 0.10071 | -0.10529 | 61.9308 | -61.0062 | -0.25635 | 0.059509 | -0.054932 | -0.17853 | 0.10529 | -0.31128 | -0.36621 | -0.28381 | 0.054931 | 0.20142
550.5781 | 122.8088 | -60.7132 | 61.9171 | -0.028338 | 0.009196 | 0.0071615 | 0.0043539 | 0.067779 | -0.0015869 | 0.069041 | -60.7819 | 61.94 | -60.9787 | -60.9146 | 61.5555 | 2.5269 | 0.1236 | -0.10529 | 61.9125 | -61.0107 | -0.2655 | 0.022888 | -0.068664 | -0.20142 | 0.09613 | -0.36163 | -0.35706 | -0.29755 | -0.004577 | 0.19684
551.5781 | 122.7951 | -60.7224 | 61.8896 | 0.10899 | 0.0079142 | 0.0056661 | 0.0047811 | 0.066284 | 0.0003357 | 0.070323 | -60.7498 | 61.908 | -60.9924 | -60.91 | 61.5509 | 2.5452 | 0.045776 | -0.10529 | 61.8805 | -61.0153 | -0.27008 | 0.018311 | -0.027466 | -0.18768 | 0.10529 | -0.33875 | -0.32959 | -0.29297 | -0.009155 | 0.24262
552.5781 | 122.8226 | -60.6995 | 61.8805 | 0.093733 | 0.0087688 | 0.0039571 | 0.0058493 | 0.068634 | -0.0013733 | 0.068187 | -60.7498 | 61.9308 | -60.9787 | -60.8826 | 61.5646 | 2.5406 | 0.045776 | -0.10529 | 61.908 | -60.9879 | -0.27924 | 0.050354 | -0.050354 | -0.1831 | 0.10529 | -0.31586 | -0.34332 | -0.28839 | 0.027466 | 0.22888
553.5781 | 122.7997 | -60.7132 | 61.8668 | 0.086103 | 0.009196 | 0.0056661 | 0.0056355 | 0.066711 | -0.0032959 | 0.066264 | -60.7452 | 61.9171 | -60.9833 | -60.9009 | 61.5601 | 2.5635 | 0.054932 | -0.10529 | 61.9171 | -61.0107 | -0.27008 | 0.050354 | -0.032043 | -0.18768 | 0.10986 | -0.3067 | -0.35705 | -0.29755 | 0.050354 | 0.23804
554.5781 | 122.7814 | -60.7132 | 61.8896 | -0.020708 | 0.01005 | 0.0016073 | 0.0043539 | 0.067139 | -0.0013733 | 0.0684 | -60.7361 | 61.9263 | -60.9879 | -60.91 | 61.5555 | 2.5818 | 0.045776 | -0.10986 | 61.9171 | -61.0062 | -0.27466 | 0.036622 | -0.022888 | -0.19684 | 0.096131 | -0.33417 | -0.36163 | -0.29297 | 0.027466 | 0.25177
555.5781 | 122.85 | -60.6949 | 61.8668 | 0.1624 | 0.0087688 | 0.0080159 | 0.0049947 | 0.064361 | -0.0020141 | 0.068827 | -60.7544 | 61.9354 | -60.9558 | -60.9238 | 61.5463 | 2.5818 | 0.009155 | -0.14191 | 61.8622 | -61.0153 | -0.26093 | 0.068665 | -0.05951 | -0.22888 | 0.091553 | -0.32043 | -0.31586 | -0.32044 | -0.004577 | 0.20142
556.5781 | 122.7814 | -60.7178 | 61.8942 | 0.047956 | 0.010264 | 0.0078023 | 0.0058493 | 0.066925 | -9.1495e-05 | 0.069468 | -60.7452 | 61.9583 | -60.965 | -60.9009 | 61.5601 | 2.5955 | 0.054932 | -0.10529 | 61.9034 | -61.0153 | -0.24719 | 0.064087 | -0.027466 | -0.18311 | 0.11444 | -0.33417 | -0.34332 | -0.29755 | 0.009155 | 0.21973
557.5781 | 122.8226 | -60.704 | 61.8896 | 0.20817 | 0.010264 | 0.0052387 | 0.0034993 | 0.06543 | -0.0028687 | 0.066478 | -60.7498 | 61.9446 | -60.997 | -61.0016 | 61.5189 | 2.6276 | 0.022888 | -0.13275 | 61.9034 | -61.0107 | -0.29297 | 0.054932 | -0.045776 | -0.29755 | 0.009155 | -0.37079 | -0.38452 | -0.3067 | 0.013733 | 0.24719
558.5781 | 122.7997 | -60.7178 | 61.8896 | 0.12425 | 0.0094096 | 0.0054525 | 0.0069173 | 0.067139 | -0.0024415 | 0.070109 | -60.7407 | 61.9354 | -60.9787 | -60.9741 | 61.4044 | 2.4902 | 0.082397 | -0.12817 | 61.908 | -61.0016 | -0.26093 | 0.045777 | -0.022889 | -0.25635 | 0.027466 | -0.48523 | -0.50354 | -0.28381 | 0.018311 | 0.23804
559.5781 | 122.7997 | -60.704 | 61.8668 | 0.17766 | 0.0077006 | 0.0078023 | 0.0041403 | 0.065643 | -0.0050049 | 0.067546 | -60.7498 | 61.908 | -60.9604 | -60.9055 | 61.5555 | 2.6596 | -0.086975 | -0.13275 | 61.9034 | -61.0199 | -0.25635 | 0.041199 | -0.045776 | -0.20142 | 0.11444 | -0.31128 | -0.3479 | -0.31586 | 0.036621 | 0.21057
560.5781 | 122.8683 | -60.7269 | 61.8942 | 0.1624 | 0.0094096 | 0.0033161 | 0.0045675 | 0.066925 | -0.0024415 | 0.066691 | -60.7452 | 61.9308 | -60.9787 | -60.8963 | 61.5417 | 2.6093 | 0.022888 | -0.20142 | 61.9125 | -60.9924 | -0.25177 | 0.036621 | -0.01831 | -0.16937 | 0.096131 | -0.35248 | -0.37079 | -0.2655 | 0.018311 | 0.23346
561.5781 | 122.7127 | -60.704 | 61.8988 | 0.19291 | 0.010691 | 0.0078023 | 0.0056355 | 0.065643 | -0.0005189 | 0.069896 | -60.7498 | 61.94 | -60.9741 | -60.91 | 61.5601 | 2.6093 | 0.022888 | -0.11902 | 61.9171 | -61.0062 | -0.27008 | 0.041198 | -0.045776 | -0.20599 | 0.096131 | -0.33874 | -0.35705 | -0.30212 | 0.01831 | 0.2243
562.5781 | 122.7859 | -60.7086 | 61.8851 | 0.11662 | 0.0089824 | 0.0043843 | 0.0047811 | 0.068207 | -0.0022277 | 0.069682 | -60.7544 | 61.9217 | -60.9467 | -60.8917 | 61.5646 | 2.6321 | 0.027466 | -0.11444 | 61.9217 | -61.0245 | -0.23804 | 0.036621 | -0.045777 | -0.18311 | 0.13275 | -0.32044 | -0.35706 | -0.31586 | 0.036621 | 0.19226
563.5781 | 122.7722 | -60.7086 | 61.8896 | 0.18529 | 0.010478 | 0.0086567 | 0.0054219 | 0.065216 | -0.0022277 | 0.069041 | -60.7361 | 61.9492 | -60.9512 | -60.8963 | 61.5692 | 2.6184 | 0.027466 | -0.1236 | 61.9263 | -61.0474 | -0.24262 | 0.05951 | -0.027466 | -0.18768 | 0.15106 | -0.32043 | -0.35706 | -0.33874 | 0.036622 | 0.21515
564.5781 | 122.7997 | -60.7132 | 61.9171 | 0.15477 | 0.0072734 | 0.0063069 | 0.0056355 | 0.066498 | 0.0009765 | 0.067546 | -60.7452 | 61.9171 | -60.9558 | -60.9283 | 61.528 | 2.5864 | 0.036621 | -0.17853 | 61.9125 | -61.0016 | -0.24261 | 0 | -0.032043 | -0.21515 | 0.073242 | -0.3891 | -0.38452 | -0.28839 | -0.004577 | 0.21057
565.5781 | 122.7539 | -60.6949 | 61.8805 | 0.17766 | 0.0094096 | 0.0058797 | 0.0060629 | 0.066711 | -9.1495e-05 | 0.067118 | -60.7407 | 61.9675 | -60.9833 | -60.9146 | 61.5234 | 2.5818 | 0.018311 | -0.16937 | 61.9171 | -61.0428 | -0.28839 | 0.086975 | -0.045777 | -0.21973 | 0.12817 | -0.35706 | -0.39368 | -0.3479 | 0.036621 | 0.24261
566.5781 | 122.7951 | -60.7269 | 61.8942 | 0.13188 | 0.0070598 | 0.0028889 | 0.0052083 | 0.067779 | -0.0013733 | 0.07075 | -60.7407 | 61.9537 | -60.9192 | -60.91 | 61.5417 | 2.6093 | 0.036621 | -0.17853 | 61.9034 | -61.0291 | -0.19226 | 0.059509 | -0.013733 | -0.18311 | 0.11902 | -0.35248 | -0.36163 | -0.30212 | 0.009155 | 0.17853
567.5781 | 122.818 | -60.704 | 61.8851 | 0.17766 | 0.0094096 | 0.0041707 | 0.0052083 | 0.067139 | -9.1495e-05 | 0.067118 | -60.7636 | 61.9354 | -60.9558 | -60.91 | 61.5372 | 2.6138 | 0.032043 | -0.17395 | 61.9171 | -61.0245 | -0.25177 | 0.050354 | -0.059509 | -0.20599 | 0.11444 | -0.3479 | -0.37994 | -0.32043 | 0.032043 | 0.19226
568.5781 | 122.7676 | -60.6995 | 61.908 | 0.1624 | 0.010264 | 0.0069477 | 0.0058493 | 0.066925 | -0.0020141 | 0.07075 | -60.7407 | 61.9446 | -60.9741 | -60.9375 | 61.528 | 2.6138 | 0.027466 | -0.16937 | 61.9125 | -60.9924 | -0.27466 | 0.036621 | -0.041199 | -0.23804 | 0.054932 | -0.37994 | -0.38452 | -0.29297 | 0.004578 | 0.23346
569.5781 | 122.8134 | -60.704 | 61.908 | 0.15477 | 0.011759 | 0.0052387 | 0.0034993 | 0.067779 | -0.0007325 | 0.067118 | -60.759 | 61.9492 | -60.9787 | -60.9238 | 61.5372 | 2.623 | 0.022888 | -0.17853 | 61.9263 | -61.0291 | -0.27466 | 0.041199 | -0.054931 | -0.21973 | 0.10529 | -0.37079 | -0.3891 | -0.32501 | 0.018311 | 0.21973
570.5781 | 122.7264 | -60.6857 | 61.9263 | 0.14714 | 0.0083416 | 0.0069477 | 0.0047811 | 0.06543 | -0.0026551 | 0.069896 | -60.7498 | 61.9492 | -60.9604 | -60.9146 | 61.5326 | 2.6367 | 0.032043 | -0.16022 | 61.9492 | -61.0107 | -0.27466 | 0.022888 | -0.064087 | -0.22888 | 0.09613 | -0.39368 | -0.41656 | -0.32501 | 0.022888 | 0.21057
571.5781 | 122.7539 | -60.7224 | 61.9446 | 0.26921 | 0.0089824 | 0.0071615 | 0.0067037 | 0.067352 | -0.0007325 | 0.067546 | -60.7956 | 61.94 | -60.9833 | -60.9879 | 61.5189 | 2.5818 | 0.054932 | -0.23346 | 61.9263 | -61.0291 | -0.26092 | -0.004578 | -0.073242 | -0.2655 | 0.041199 | -0.42572 | -0.40741 | -0.3067 | -0.01831 | 0.18768
572.5781 | 122.7585 | -60.704 | 61.9171 | 0.33024 | 0.0083416 | 0.0041707 | 0.0045675 | 0.06607 | -9.1495e-05 | 0.067118 | -60.791 | 61.9537 | -60.9833 | -60.9695 | 61.496 | 2.5818 | 0.045776 | -0.20599 | 61.9629 | -61.0291 | -0.27923 | 0.036621 | -0.086975 | -0.2655 | 0.05951 | -0.42114 | -0.46692 | -0.32501 | 0.045777 | 0.19226
573.5781 | 122.7539 | -60.7132 | 61.908 | 0.26921 | 0.0087688 | 0.0073751 | 0.0067037 | 0.065643 | -0.0013733 | 0.067759 | -60.7864 | 61.94 | -60.965 | -60.9604 | 61.5189 | 2.5909 | 0.054932 | -0.2243 | 61.9217 | -61.0474 | -0.25177 | 0.032043 | -0.073242 | -0.24719 | 0.086975 | -0.3891 | -0.40283 | -0.33417 | 0.013733 | 0.17853
574.5781 | 122.7539 | -60.6949 | 61.8988 | 0.24632 | 0.0096232 | 0.0052387 | 0.0058493 | 0.06607 | -0.0015869 | 0.067546 | -60.7773 | 61.9629 | -60.965 | -60.9558 | 61.5051 | 2.6093 | 0.041199 | -0.20142 | 61.9354 | -60.997 | -0.27008 | 0.064087 | -0.082398 | -0.26093 | 0.041198 | -0.39368 | -0.4303 | -0.30212 | 0.036621 | 0.18768
575.5781 | 122.7585 | -60.6857 | 61.9125 | 0.22343 | 0.0096232 | 0.0073751 | 0.0062765 | 0.068634 | -0.0011597 | 0.070109 | -60.7819 | 61.9583 | -61.0016 | -60.9421 | 61.5143 | 2.623 | 0.036621 | -0.21515 | 61.9354 | -61.0199 | -0.31586 | 0.045776 | -0.09613 | -0.25635 | 0.077819 | -0.39825 | -0.42114 | -0.33417 | 0.022888 | 0.21973
576.5781 | 122.7859 | -60.6903 | 61.908 | 0.31499 | 0.010264 | 0.0082295 | 0.0047811 | 0.067352 | -0.0015869 | 0.066905 | -60.7727 | 61.94 | -60.9558 | -60.9467 | 61.5189 | 2.6138 | 0.045776 | -0.20599 | 61.9354 | -61.0153 | -0.2655 | 0.032043 | -0.082397 | -0.25635 | 0.068665 | -0.3891 | -0.41657 | -0.32501 | 0.027466 | 0.18311
577.5781 | 122.7219 | -60.6949 | 61.9125 | 0.26158 | 0.0083416 | 0.0071615 | 0.0064901 | 0.064575 | -0.0013733 | 0.067973 | -60.7452 | 61.9675 | -60.9467 | -60.9375 | 61.528 | 2.6367 | 0.036621 | -0.18768 | 61.9675 | -61.0153 | -0.25177 | 0.054931 | -0.050354 | -0.24262 | 0.07782 | -0.38452 | -0.43945 | -0.32044 | 0.054931 | 0.20142
578.5781 | 122.7585 | -60.6949 | 61.8988 | 0.23106 | 0.0087688 | 0.0071615 | 0.0060629 | 0.066284 | -0.0018005 | 0.066478 | -60.8185 | 61.9583 | -60.9558 | -60.9833 | 61.4822 | 2.5726 | 0.041199 | -0.26093 | 61.9446 | -61.0291 | -0.26093 | 0.059509 | -0.1236 | -0.28839 | 0.045777 | -0.41656 | -0.46234 | -0.33417 | 0.045776 | 0.13733
579.5781 | 122.7036 | -60.7132 | 61.9125 | 0.24632 | 0.011119 | 0.0075887 | 0.0049947 | 0.067566 | -0.0011597 | 0.067118 | -60.7864 | 61.9629 | -60.9467 | -60.9558 | 61.496 | 2.6047 | 0.041199 | -0.24719 | 61.9446 | -61.0245 | -0.23346 | 0.050354 | -0.073242 | -0.24261 | 0.068664 | -0.41656 | -0.44861 | -0.31128 | 0.032043 | 0.16022
580.5781 | 122.7356 | -60.7315 | 61.908 | 0.24632 | 0.0085552 | 0.0078023 | 0.0032857 | 0.06842 | -0.0018005 | 0.0684 | -60.7727 | 61.9949 | -60.9741 | -60.9375 | 61.5143 | 2.6001 | 0.059509 | -0.21973 | 61.9583 | -61.0199 | -0.24261 | 0.086975 | -0.041199 | -0.20599 | 0.082397 | -0.39368 | -0.44403 | -0.28839 | 0.050354 | 0.20142
581.5781 | 122.7905 | -60.6949 | 61.9217 | 0.3455 | 0.010691 | 0.0097249 | 0.0030721 | 0.066711 | -0.0026551 | 0.067332 | -60.7681 | 61.9812 | -60.9558 | -60.9375 | 61.5051 | 2.6047 | 0.041199 | -0.21515 | 61.9537 | -61.0016 | -0.26093 | 0.059509 | -0.073242 | -0.24262 | 0.064087 | -0.41656 | -0.44861 | -0.3067 | 0.032043 | 0.18768
582.5781 | 122.6715 | -60.7132 | 61.8576 | 0.36839 | 0.010478 | 0.0035299 | 0.0064901 | 0.065857 | -0.0028687 | 0.069255 | -60.7956 | 61.972 | -60.9741 | -60.9741 | 61.4777 | 2.5955 | -0.013733 | -0.25635 | 61.9629 | -61.0107 | -0.26092 | 0.11444 | -0.082397 | -0.26092 | 0.036621 | -0.37994 | -0.48523 | -0.29755 | 0.10529 | 0.17853
583.5781 | 122.7997 | -60.6949 | 61.9354 | 0.25395 | 0.0096232 | 0.0090841 | 0.0060629 | 0.067139 | -0.0009461 | 0.069468 | -60.7727 | 61.9904 | -60.9558 | -60.9329 | 61.5143 | 2.623 | 0.041199 | -0.21057 | 61.94 | -61.0107 | -0.26093 | 0.054931 | -0.07782 | -0.23804 | 0.07782 | -0.42114 | -0.42572 | -0.31586 | 0.004577 | 0.18311
584.5781 | 122.7631 | -60.6857 | 61.9446 | 0.23869 | 0.010264 | 0.0080159 | 0.0024313 | 0.066284 | -0.0005189 | 0.067973 | -60.7544 | 61.972 | -60.9375 | -60.9192 | 61.5189 | 2.6459 | 0.027466 | -0.20599 | 61.9354 | -60.9924 | -0.25177 | 0.027466 | -0.068665 | -0.23346 | 0.073243 | -0.42572 | -0.41657 | -0.3067 | -0.009155 | 0.1831
585.5781 | 122.7859 | -60.6949 | 61.9263 | 0.31499 | 0.0081278 | 0.0082295 | 0.0043539 | 0.065643 | -0.0013733 | 0.068827 | -60.8002 | 61.9858 | -60.9558 | -60.9741 | 61.4777 | 2.6093 | 0.009155 | -0.25635 | 61.94 | -61.0245 | -0.26093 | 0.059509 | -0.10529 | -0.27924 | 0.050354 | -0.44861 | -0.46234 | -0.32959 | 0.013732 | 0.15564
586.5781 | 122.7219 | -60.6949 | 61.9217 | 0.26158 | 0.0083416 | 0.0063069 | 0.0039267 | 0.067779 | -0.0018005 | 0.069255 | -60.7956 | 61.9812 | -60.9558 | -60.9695 | 61.496 | 2.6138 | 0.013733 | -0.24261 | 61.9629 | -61.0016 | -0.26093 | 0.059509 | -0.10071 | -0.27466 | 0.032044 | -0.42572 | -0.46692 | -0.3067 | 0.041199 | 0.16022
587.5781 | 122.7264 | -60.7086 | 61.9171 | 0.28447 | 0.0094096 | 0.0052387 | 0.0058493 | 0.067352 | -0.0007325 | 0.0684 | -60.7956 | 61.9629 | -60.9512 | -60.965 | 61.4777 | 2.6047 | 0.032043 | -0.26093 | 61.9446 | -61.0153 | -0.24262 | 0.045777 | -0.086975 | -0.25635 | 0.050354 | -0.43945 | -0.46692 | -0.3067 | 0.027466 | 0.15564
588.5781 | 122.7493 | -60.7224 | 61.9125 | 0.20817 | 0.0096232 | 0.0082295 | 0.0064901 | 0.067352 | 0.0003357 | 0.068827 | -60.7773 | 61.9858 | -60.9512 | -60.9512 | 61.496 | 2.623 | 0.036621 | -0.27008 | 61.94 | -60.9833 | -0.22888 | 0.073242 | -0.054932 | -0.22888 | 0.032043 | -0.41656 | -0.44403 | -0.26092 | 0.027465 | 0.17395
589.5781 | 122.8455 | -60.6491 | 61.8896 | 0.46757 | 0.0083416 | 0.0050251 | 0.0026449 | 0.066284 | -0.0007325 | 0.067973 | -60.7544 | 61.9308 | -60.9512 | -60.9009 | 61.5692 | 2.6688 | -0.10529 | -0.21057 | 61.9171 | -61.0016 | -0.30212 | 0.041199 | -0.10529 | -0.25177 | 0.10071 | -0.32043 | -0.3479 | -0.35248 | 0.027466 | 0.19684
590.5781 | 122.7585 | -60.6674 | 61.9125 | 0.23106 | 0.0098368 | 0.0043843 | 0.0060629 | 0.066711 | -0.0005189 | 0.06605 | -60.7544 | 61.9904 | -60.9375 | -60.9329 | 61.5051 | 2.6184 | 0.045776 | -0.24719 | 61.9537 | -61.0062 | -0.27008 | 0.077819 | -0.086976 | -0.2655 | 0.073243 | -0.40741 | -0.44861 | -0.33875 | 0.041198 | 0.1831
591.5781 | 122.7219 | -60.6812 | 61.9217 | 0.26158 | 0.0077006 | 0.010579 | 0.0043539 | 0.066498 | -0.0011597 | 0.067118 | -60.7819 | 61.9858 | -60.9329 | -60.9558 | 61.4777 | 2.6413 | 0.054932 | -0.23346 | 61.9537 | -61.0199 | -0.25177 | 0.064087 | -0.10071 | -0.27466 | 0.064086 | -0.44403 | -0.47607 | -0.33875 | 0.032043 | 0.15106
592.5781 | 122.7768 | -60.6537 | 61.9492 | 0.4218 | 0.0072734 | 0.0043843 | 0.0047811 | 0.067566 | -0.0022277 | 0.066905 | -60.7727 | 61.9858 | -60.965 | -60.8871 | 61.2991 | 2.4719 | 0.10529 | -0.027466 | 61.9629 | -61.0153 | -0.31128 | 0.036621 | -0.11902 | -0.23346 | 0.12817 | -0.65002 | -0.66376 | -0.36163 | 0.013733 | 0.19226
593.5781 | 122.8043 | -60.6995 | 61.9446 | 0.39128 | 0.0096232 | 0.0043843 | 0.0032857 | 0.067566 | -0.0009461 | 0.069896 | -60.7636 | 61.972 | -60.9695 | -60.9512 | 61.5005 | 2.6321 | -0.091553 | -0.55389 | 61.9034 | -61.0062 | -0.27008 | 0.027466 | -0.064087 | -0.25177 | 0.054932 | -0.44403 | -0.40283 | -0.3067 | -0.041199 | 0.20599
594.5781 | 122.8134 | -60.6537 | 61.9125 | 0.39891 | 0.010478 | 0.0045979 | 0.0045675 | 0.06842 | 0.0011901 | 0.069255 | -60.7681 | 61.972 | -60.9467 | -60.9146 | 61.5417 | 2.6596 | -0.054932 | -0.24261 | 61.9629 | -60.9558 | -0.29297 | 0.059509 | -0.11444 | -0.26093 | 0.041199 | -0.37079 | -0.42114 | -0.30212 | 0.050354 | 0.17853
595.5781 | 122.7493 | -60.6857 | 61.908 | 0.39128 | 0.0087688 | 0.0043843 | 0.0054219 | 0.066498 | -0.0005189 | 0.069041 | -60.7819 | 61.9858 | -60.9283 | -60.9329 | 61.5097 | 2.6321 | -0.004578 | -0.27466 | 61.94 | -61.0199 | -0.24262 | 0.07782 | -0.09613 | -0.24719 | 0.086975 | -0.39825 | -0.4303 | -0.33417 | 0.032043 | 0.14648
596.5781 | 122.7631 | -60.6583 | 61.9308 | 0.17003 | 0.0096232 | 0.0065205 | 0.0043539 | 0.063721 | 0.0003357 | 0.066691 | -60.7773 | 61.9812 | -60.9238 | -60.9055 | 61.5463 | 2.6642 | -0.050354 | -0.23346 | 61.9583 | -60.9924 | -0.2655 | 0.050354 | -0.11902 | -0.24719 | 0.086975 | -0.38452 | -0.41199 | -0.33417 | 0.027466 | 0.14648
597.5781 | 122.7768 | -60.672 | 61.9217 | 0.39128 | 0.0098368 | 0.0045979 | 0.0054219 | 0.064789 | -0.0007325 | 0.069255 | -60.7773 | 61.9766 | -60.9421 | -60.9375 | 61.528 | 2.6459 | 0.004578 | -0.27466 | 61.9583 | -61.0062 | -0.27008 | 0.054932 | -0.10529 | -0.2655 | 0.068665 | -0.39368 | -0.4303 | -0.33417 | 0.036621 | 0.1648
598.5781 | 122.7676 | -60.6674 | 61.9537 | 0.3455 | 0.0096232 | 0.0095113 | 0.0054219 | 0.065857 | 0.0009765 | 0.066478 | -60.7819 | 61.9904 | -60.9375 | -60.9146 | 61.5143 | 2.6596 | -0.004578 | -0.2655 | 61.9629 | -60.9833 | -0.27008 | 0.036621 | -0.11444 | -0.24719 | 0.068664 | -0.43945 | -0.44861 | -0.31586 | 0.009156 | 0.15564
599.5781 | 122.7997 | -60.6583 | 61.9308 | 0.58964 | 0.0087688 | 0.0065205 | 0.0049947 | 0.065216 | 0.0009765 | 0.068827 | -60.7361 | 61.9766 | -60.9375 | -60.9055 | 61.5463 | 2.6733 | -0.004578 | -0.22888 | 61.9492 | -60.965 | -0.27924 | 0.045777 | -0.07782 | -0.24719 | 0.059509 | -0.38452 | -0.40283 | -0.3067 | 0.018311 | 0.20142
600.5781 | 122.7722 | -60.6674 | 61.94 | 0.42943 | 0.0098368 | 0.0084431 | 0.0024313 | 0.067139 | -0.0009461 | 0.0684 | -60.7407 | 61.9766 | -60.9375 | -60.9146 | 61.5417 | 2.6779 | -0.013733 | -0.24261 | 61.9583 | -60.9741 | -0.27008 | 0.036622 | -0.073243 | -0.24719 | 0.059509 | -0.39825 | -0.41656 | -0.3067 | 0.018311 | 0.19684
601.5781 | 122.7997 | -60.6354 | 61.908 | 0.36839 | 0.0083416 | 0.0067341 | 0.0011495 | 0.065643 | -0.0007325 | 0.069896 | -60.7452 | 61.9904 | -60.9283 | -60.9238 | 61.5417 | 2.6733 | -0.009155 | -0.23346 | 61.9537 | -60.9604 | -0.29297 | 0.082397 | -0.10986 | -0.28839 | 0.036621 | -0.36621 | -0.41199 | -0.32501 | 0.045776 | 0.18311
602.5781 | 122.7951 | -60.6262 | 61.94 | -0.32588 | 0.010264 | 0.0063069 | 0.0039267 | 0.066284 | 0.0003357 | 0.067546 | -60.7544 | 61.9995 | -60.91 | -60.8917 | 61.528 | 2.6871 | -0.013733 | -0.23346 | 61.9675 | -60.9741 | -0.28381 | 0.05951 | -0.12817 | -0.2655 | 0.082397 | -0.41199 | -0.43945 | -0.3479 | 0.027466 | 0.15564
603.5781 | 122.85 | -60.6354 | 61.8896 | 0.43706 | 0.0098368 | 0.0039571 | 0.0030721 | 0.064148 | 0.0009765 | 0.07075 | -60.704 | 61.9629 | -60.8871 | -60.8414 | 61.6013 | 2.7512 | -0.14191 | -0.16937 | 61.9171 | -60.9604 | -0.25177 | 0.073243 | -0.068665 | -0.20599 | 0.11902 | -0.28839 | -0.31586 | -0.32501 | 0.027466 | 0.18311
604.5781 | 122.8271 | -60.5988 | 61.94 | 0.23106 | 0.0044962 | 0.0078023 | -0.0029093 | 0.063293 | 0.0007629 | 0.071177 | -60.7544 | 61.8851 | -60.8917 | -60.8414 | 61.6058 | 2.7237 | 0.091553 | -0.10071 | 61.9629 | -60.8643 | -0.29297 | -0.054931 | -0.15564 | -0.24262 | 0.022888 | -0.33417 | -0.35706 | -0.2655 | 0.022889 | 0.13733
605.5781 | 122.7448 | -60.6445 | 61.9766 | 0.69645 | 0.0096232 | 0.0078023 | 0.0056355 | 0.063721 | 0.0003357 | 0.067332 | -60.6674 | 61.9675 | -60.91 | -60.878 | 61.5555 | 2.71 | -0.022888 | -0.24261 | 61.9858 | -60.9787 | -0.2655 | -0.009156 | -0.022888 | -0.23346 | 0.10071 | -0.42114 | -0.4303 | -0.33417 | 0.009155 | 0.24262
606.5781 | 122.9004 | -60.6216 | 61.908 | 0.44468 | 0.0089824 | 0.0056661 | 0.0054219 | 0.066284 | -0.0005189 | 0.066905 | -60.6903 | 61.9492 | -60.878 | -60.8093 | 61.6013 | 2.7603 | -0.15106 | -0.16937 | 61.9446 | -60.9467 | -0.25635 | 0.041199 | -0.068665 | -0.18768 | 0.13733 | -0.3067 | -0.34332 | -0.32501 | 0.036621 | 0.18768
607.5781 | 122.8363 | -60.585 | 61.908 | 0.44468 | 0.009196 | 0.0028889 | 0.0034993 | 0.063507 | 0.0009765 | 0.067332 | -60.7086 | 61.9583 | -60.9146 | -60.8322 | 61.5967 | 2.7512 | -0.16022 | -0.1831 | 61.9446 | -60.9283 | -0.32959 | 0.050354 | -0.1236 | -0.24719 | 0.096131 | -0.31128 | -0.3479 | -0.34332 | 0.036621 | 0.20599
608.5781 | 122.905 | -60.5988 | 61.9263 | 0.4218 | 0.0079142 | 0.0022481 | 0.0030721 | 0.064789 | -9.1495e-05 | 0.069468 | -60.6354 | 61.908 | -60.8734 | -60.7956 | 61.6379 | 2.8198 | -0.20599 | -0.14648 | 61.9171 | -60.9055 | -0.27466 | -0.018311 | -0.036621 | -0.19684 | 0.10986 | -0.28839 | -0.27924 | -0.3067 | -0.009156 | 0.23804
609.5781 | 122.8546 | -60.585 | 61.9583 | 0.25395 | 0.0044962 | 0.0033161 | -0.0020549 | 0.061798 | -0.0026551 | 0.067118 | -60.7224 | 61.8988 | -60.8688 | -60.8231 | 61.6287 | 2.8061 | -0.064087 | -0.14648 | 61.9354 | -60.8826 | -0.28381 | -0.059509 | -0.13733 | -0.23804 | 0.059509 | -0.32959 | -0.3067 | -0.29755 | -0.022888 | 0.14648
610.5781 | 122.8317 | -60.585 | 61.94 | 0.36839 | 0.0070598 | 0.0041707 | 0.0020039 | 0.061157 | -9.1495e-05 | 0.0684 | -60.7224 | 61.9034 | -60.8917 | -60.8322 | 61.6196 | 2.7878 | -0.11902 | -0.1831 | 61.9217 | -60.9375 | -0.3067 | -0.036621 | -0.13733 | -0.24719 | 0.10529 | -0.32043 | -0.30212 | -0.35248 | -0.01831 | 0.16937
611.5781 | 122.8683 | -60.6171 | 61.9583 | 0.4218 | 0.010478 | 0.0054525 | 0.0062765 | 0.063293 | -0.0013733 | 0.067973 | -60.6995 | 61.9537 | -60.8643 | -60.8231 | 61.5921 | 2.7603 | -0.13733 | -0.21057 | 61.9217 | -60.9238 | -0.24719 | -0.004578 | -0.082398 | -0.20599 | 0.10071 | -0.36621 | -0.32959 | -0.3067 | -0.036621 | 0.16479
612.5781 | 122.8455 | -60.5988 | 61.9492 | 0.42943 | 0.0079142 | 0.0067341 | 0.0077719 | 0.06308 | -0.0005189 | 0.0684 | -60.6903 | 61.9492 | -60.9055 | -60.8322 | 61.5921 | 2.7603 | -0.11902 | -0.21057 | 61.9537 | -60.9238 | -0.3067 | 0 | -0.091553 | -0.23346 | 0.091553 | -0.35706 | -0.36163 | -0.32501 | 0.004577 | 0.21515
613.5781 | 122.9095 | -60.5942 | 61.9263 | 0.4218 | 0.0070598 | 0.0075887 | 0.0049947 | 0.063507 | -0.0003051 | 0.069255 | -60.6308 | 61.9263 | -60.8643 | -60.7636 | 61.6562 | 2.8152 | -0.1831 | -0.15564 | 61.9034 | -60.878 | -0.27008 | 0 | -0.036621 | -0.16937 | 0.11444 | -0.27008 | -0.24719 | -0.28381 | -0.022889 | 0.23346
614.5781 | 122.9233 | -60.5804 | 61.972 | 0.10899 | 0.0025736 | 0.0028889 | -0.00055953 | 0.062225 | -0.0013733 | 0.068827 | -60.6628 | 61.9263 | -60.8505 | -60.7407 | 61.702 | 2.9114 | -0.082397 | -0.050354 | 61.9446 | -60.8505 | -0.27008 | -0.045776 | -0.082398 | -0.16022 | 0.10986 | -0.27008 | -0.24262 | -0.27008 | -0.027466 | 0.18768
615.5781 | 122.8821 | -60.5713 | 61.9629 | 1.3678 | 0.0070598 | 0.0033161 | 0.0022177 | 0.062225 | -0.0018005 | 0.067118 | -60.498 | 61.9308 | -60.8505 | -60.7544 | 61.6745 | 2.8473 | -0.20142 | -0.14648 | 61.9171 | -60.8597 | -0.27924 | -0.032044 | 0.073242 | -0.18311 | 0.10528 | -0.28839 | -0.24261 | -0.28839 | -0.045777 | 0.35248
616.5781 | 122.7997 | -60.5896 | 61.9537 | 0.41417 | 0.0066326 | 0.0056661 | 0.0017903 | 0.061798 | -0.0009461 | 0.0684 | -60.6628 | 61.8942 | -60.8688 | -60.7773 | 61.6608 | 2.8244 | -0.12817 | -0.16022 | 61.9354 | -60.8826 | -0.27923 | -0.059509 | -0.073242 | -0.18768 | 0.10529 | -0.29297 | -0.27466 | -0.29297 | -0.01831 | 0.20599
617.5781 | 122.8729 | -60.5942 | 61.9904 | 0.24632 | 0.0068462 | 0.0052387 | 0.0017903 | 0.059448 | 0.0001221 | 0.067759 | -60.7132 | 61.9171 | -60.8597 | -60.8002 | 61.6333 | 2.829 | -0.082397 | -0.16022 | 61.94 | -60.8871 | -0.2655 | -0.073242 | -0.11902 | -0.20599 | 0.086975 | -0.35705 | -0.3067 | -0.29297 | -0.050354 | 0.14648
618.5781 | 122.905 | -60.5988 | 61.9537 | 0.41417 | 0.0077006 | 0.0073751 | 0.0079855 | 0.062225 | -0.0009461 | 0.067973 | -60.6628 | 61.9537 | -60.8643 | -60.7544 | 61.6562 | 2.8336 | -0.1831 | -0.16479 | 61.908 | -60.8963 | -0.2655 | 0 | -0.064087 | -0.15564 | 0.14191 | -0.29755 | -0.25177 | -0.29755 | -0.045776 | 0.20142
619.5781 | 122.8317 | -60.5896 | 61.9858 | 0.19291 | 0.0051372 | 0.0075887 | 0.00050867 | 0.060944 | -0.0009461 | 0.066905 | -60.7864 | 61.9263 | -60.8597 | -60.7956 | 61.6425 | 2.8564 | -0.073242 | -0.15106 | 61.94 | -60.8597 | -0.27008 | -0.059509 | -0.19684 | -0.20599 | 0.064087 | -0.34332 | -0.29755 | -0.27008 | -0.045777 | 0.073242
620.5781 | 122.8958 | -60.5621 | 61.9537 | 0.31499 | 0.0072734 | 0.0028889 | 0.0024313 | 0.059875 | -0.0009461 | 0.067118 | -60.6354 | 61.9354 | -60.8551 | -60.7452 | 61.6699 | 2.8656 | -0.16937 | -0.14191 | 61.9217 | -60.8734 | -0.29297 | -0.01831 | -0.073242 | -0.1831 | 0.12817 | -0.28381 | -0.25177 | -0.31128 | -0.032043 | 0.21973
621.5781 | 122.9279 | -60.5713 | 61.9446 | 0.4218 | 0.0087688 | 0.0018209 | 0.0047811 | 0.063934 | -0.0018005 | 0.0684 | -60.6125 | 61.9537 | -60.8551 | -60.759 | 61.6699 | 2.8748 | -0.21057 | -0.14191 | 61.9217 | -60.8597 | -0.28381 | 0.009155 | -0.041199 | -0.18768 | 0.10071 | -0.27466 | -0.25177 | -0.28839 | -0.022888 | 0.24262
622.5781 | 122.8226 | -60.5621 | 61.9675 | 0.3455 | 0.0044962 | 0.0020345 | 0.0013631 | 0.06308 | -0.0020141 | 0.069896 | -60.672 | 61.9217 | -60.8871 | -60.8002 | 61.6287 | 2.8381 | -0.11902 | -0.16479 | 61.9537 | -60.8459 | -0.32501 | -0.045776 | -0.10986 | -0.23804 | 0.045776 | -0.33874 | -0.32501 | -0.28381 | -0.013733 | 0.21515
623.5781 | 122.8912 | -60.5667 | 61.9766 | 0.45231 | 0.0044962 | 0.0088703 | 0.0069173 | 0.062439 | -0.0018005 | 0.066264 | -60.5896 | 61.9446 | -60.8093 | -60.7452 | 61.6791 | 2.8748 | -0.17853 | -0.14191 | 61.9354 | -60.8597 | -0.24262 | -0.032044 | -0.022889 | -0.17853 | 0.11444 | -0.29755 | -0.25635 | -0.29297 | -0.041199 | 0.21973
624.5781 | 122.9187 | -60.5484 | 61.9995 | 0.10136 | 0.0049236 | 0.00011194 | -0.0012003 | 0.057739 | -0.0013733 | 0.065623 | -60.6491 | 61.9354 | -60.8139 | -60.7132 | 61.7386 | 2.9526 | -0.082397 | -0.041199 | 61.9446 | -60.8231 | -0.2655 | -0.064087 | -0.10071 | -0.1648 | 0.10986 | -0.26093 | -0.20599 | -0.27466 | -0.054932 | 0.16479
625.5781 | 122.8455 | -60.5759 | 61.9858 | 0.31499 | 0.005778 | 0.0022481 | 0.0030721 | 0.063293 | -0.0005189 | 0.067759 | -60.64 | 61.8942 | -60.8597 | -60.7681 | 61.6562 | 2.8519 | -0.14191 | -0.16479 | 61.9492 | -60.8231 | -0.28381 | -0.091553 | -0.064087 | -0.19226 | 0.054932 | -0.32959 | -0.29297 | -0.24719 | -0.036621 | 0.21973
626.5781 | 122.8821 | -60.5255 | 62.0087 | 0.45231 | 0.0064188 | 0.0043843 | 0.0049947 | 0.06308 | -0.0007325 | 0.069041 | -60.6033 | 61.9308 | -60.8459 | -60.6674 | 61.8668 | 3.0167 | -0.24261 | -0.15106 | 61.9492 | -60.8597 | -0.32043 | -0.07782 | -0.07782 | -0.14191 | 0.19226 | -0.14191 | -0.082398 | -0.33417 | -0.059509 | 0.24261
627.5781 | 122.905 | -60.553 | 61.9812 | 0.43706 | 0.007487 | 0.0052387 | 0.0067037 | 0.063507 | -0.0035095 | 0.069682 | -60.5988 | 61.9492 | -60.8185 | -60.7086 | 61.6791 | 2.9343 | -0.45319 | -0.33875 | 61.8896 | -60.8917 | -0.2655 | -0.032043 | -0.045776 | -0.15564 | 0.18311 | -0.30212 | -0.21057 | -0.33875 | -0.091553 | 0.21973
628.5781 | 122.85 | -60.553 | 62.0041 | 0.37602 | 0.0055644 | 0.0050251 | 0.0013631 | 0.062012 | -0.0020141 | 0.068187 | -60.6628 | 61.9263 | -60.8368 | -60.7681 | 61.6425 | 2.861 | -0.10986 | -0.1831 | 61.9446 | -60.8551 | -0.28381 | -0.077819 | -0.10986 | -0.21515 | 0.086976 | -0.36163 | -0.30212 | -0.30212 | -0.059509 | 0.17395
629.5781 | 122.9279 | -60.5255 | 62.0132 | 0.12425 | 0.0077006 | 0.0026753 | -0.00013233 | 0.060944 | -0.0032959 | 0.068827 | -60.6079 | 61.9354 | -60.791 | -60.672 | 61.7615 | 2.9846 | -0.082397 | -0.036621 | 61.94 | -60.8002 | -0.2655 | -0.07782 | -0.082397 | -0.14648 | 0.12817 | -0.25177 | -0.17853 | -0.27466 | -0.073243 | 0.18311
630.5781 | 122.8638 | -60.5301 | 62.0041 | 0.27684 | 0.0055644 | 0.0013935 | 0.0026449 | 0.059875 | -0.0035095 | 0.069041 | -60.6628 | 61.9583 | -60.8139 | -60.759 | 61.6562 | 2.9022 | -0.068665 | -0.17853 | 61.9446 | -60.8322 | -0.28381 | -0.045776 | -0.13275 | -0.22888 | 0.073242 | -0.3479 | -0.28839 | -0.30212 | -0.059509 | 0.15106
631.5781 | 122.8226 | -60.5576 | 61.9858 | 0.33024 | 0.0083416 | 0.0048115 | 0.00093587 | 0.062012 | -0.0026551 | 0.06605 | -60.6354 | 61.94 | -60.8414 | -60.7361 | 61.6653 | 2.8748 | -0.14648 | -0.17395 | 61.9217 | -60.8414 | -0.28381 | -0.045777 | -0.07782 | -0.17853 | 0.10529 | -0.32044 | -0.25635 | -0.28381 | -0.064087 | 0.20599
632.5781 | 122.8546 | -60.5484 | 62.0224 | 0.23106 | 0.0066326 | 0.00032554 | 0.00093587 | 0.060089 | -0.0018005 | 0.067973 | -60.6537 | 61.9537 | -60.8139 | -60.7636 | 61.7065 | 2.9205 | -0.086975 | -0.15564 | 61.9812 | -60.8231 | -0.2655 | -0.068665 | -0.10529 | -0.21515 | 0.059509 | -0.31586 | -0.27466 | -0.27466 | -0.041199 | 0.16022
633.5781 | 122.9095 | -60.585 | 61.9766 | 0.42943 | 0.0085552 | 0.0099385 | 0.0084127 | 0.061798 | -0.0018005 | 0.06605 | -60.6216 | 61.9995 | -60.8505 | -60.7407 | 61.6562 | 2.8793 | -0.15106 | -0.20599 | 61.9629 | -60.8688 | -0.2655 | 0.022888 | -0.036621 | -0.15564 | 0.12817 | -0.32044 | -0.3067 | -0.28381 | -0.013733 | 0.22888
634.5781 | 122.8638 | -60.5484 | 61.9766 | 0.37602 | 0.0068462 | 0.0050251 | 0.0022177 | 0.063721 | -9.1495e-05 | 0.067759 | -60.5896 | 61.9583 | -60.8231 | -60.704 | 61.6974 | 2.916 | -0.21057 | -0.16937 | 61.9354 | -60.8368 | -0.27466 | -0.018311 | -0.041199 | -0.15564 | 0.13275 | -0.27924 | -0.23804 | -0.28839 | -0.041199 | 0.23346
635.5781 | 122.8912 | -60.5347 | 61.972 | 0.28447 | 0.0066326 | 0.0031025 | 0.0047811 | 0.065002 | -0.0015869 | 0.067759 | -60.5759 | 61.9904 | -60.8276 | -60.704 | 61.6882 | 2.916 | -0.20142 | -0.15564 | 61.9125 | -60.8276 | -0.29297 | 0.01831 | -0.041199 | -0.16937 | 0.1236 | -0.28381 | -0.22431 | -0.29297 | -0.059509 | 0.25177
636.5781 | 122.8775 | -60.553 | 61.9858 | 0.42943 | 0.007487 | 0.0065205 | 0.00093587 | 0.060303 | -0.0020141 | 0.066905 | -60.5988 | 61.9492 | -60.8414 | -60.7361 | 61.6837 | 2.9251 | -0.16022 | -0.14648 | 61.9583 | -60.8139 | -0.28839 | -0.036621 | -0.045776 | -0.1831 | 0.07782 | -0.30212 | -0.27466 | -0.26093 | -0.027466 | 0.24262
637.5781 | 122.85 | -60.5438 | 61.9812 | 0.44468 | 0.011759 | 0.0024617 | 0.0054219 | 0.065216 | -0.0026551 | 0.067546 | -60.6308 | 61.9995 | -60.8414 | -60.7224 | 61.6837 | 2.8885 | -0.16022 | -0.17853 | 61.9583 | -60.8459 | -0.29755 | 0.018311 | -0.086975 | -0.17853 | 0.1236 | -0.29755 | -0.27466 | -0.30212 | -0.022888 | 0.21057
638.5781 | 122.8867 | -60.5576 | 62.0087 | 0.46757 | 0.01005 | 0.010579 | 0.0069173 | 0.062866 | -0.0013733 | 0.068187 | -60.6354 | 62.0132 | -60.8459 | -60.7361 | 61.6745 | 2.8793 | -0.16022 | -0.20142 | 61.9629 | -60.8368 | -0.28839 | 0.004578 | -0.07782 | -0.17853 | 0.10071 | -0.33417 | -0.28839 | -0.27924 | -0.045776 | 0.21057
639.5781 | 122.7951 | -60.553 | 62.0132 | 0.40654 | 0.0083416 | 0.0054525 | 0.0052083 | 0.063507 | -0.0005189 | 0.0684 | -60.6583 | 62.0316 | -60.8551 | -60.759 | 61.6287 | 2.861 | -0.11902 | -0.23804 | 61.9675 | -60.8643 | -0.30212 | 0.01831 | -0.10529 | -0.20599 | 0.10529 | -0.38452 | -0.33874 | -0.31128 | -0.045777 | 0.19684
640.5781 | 122.9187 | -60.5301 | 61.9858 | 1.6578 | 0.01005 | 0.0069477 | 0.0020039 | 0.063934 | -0.0005189 | 0.067973 | -60.64 | 61.9583 | -60.8459 | -60.6857 | 61.7203 | 2.9388 | -0.17853 | -0.16937 | 61.9675 | -60.8002 | -0.31586 | -0.027466 | -0.10986 | -0.15564 | 0.11444 | -0.2655 | -0.24719 | -0.27008 | -0.018311 | 0.20599
641.5781 | 122.8043 | -60.5438 | 62.0178 | 0.32261 | 0.0066326 | 0.0022481 | 0.0013631 | 0.061798 | -0.0024415 | 0.067546 | -60.6308 | 61.9629 | -60.8093 | -60.7315 | 61.6928 | 2.9388 | -0.15564 | -0.1831 | 61.9583 | -60.8276 | -0.2655 | -0.054931 | -0.086975 | -0.18768 | 0.096131 | -0.32501 | -0.2655 | -0.28381 | -0.059509 | 0.17853
642.5781 | 122.8867 | -60.5438 | 62.0087 | 0.44468 | 0.0089824 | 0.0073751 | 0.0071309 | 0.061798 | -9.1495e-05 | 0.067546 | -60.6079 | 62.0224 | -60.8276 | -60.7407 | 61.6928 | 2.916 | -0.14191 | -0.21057 | 61.9812 | -60.8414 | -0.28381 | 0.013733 | -0.064087 | -0.19684 | 0.10071 | -0.31586 | -0.28839 | -0.29755 | -0.027466 | 0.21973
643.5781 | 122.8775 | -60.5484 | 62.0132 | 0.42943 | 0.0081278 | 0.0048115 | 0.0058493 | 0.06308 | -0.0005189 | 0.067332 | -60.6262 | 62.0361 | -60.8231 | -60.7544 | 61.6699 | 2.8885 | -0.14648 | -0.23346 | 61.9583 | -60.8551 | -0.27466 | 0.022888 | -0.07782 | -0.20599 | 0.10071 | -0.34332 | -0.28839 | -0.3067 | -0.054932 | 0.19684
644.5781 | 122.8043 | -60.5438 | 62.0087 | 0.42943 | 0.010691 | 0.0082295 | 0.0067037 | 0.064789 | -0.0003051 | 0.065837 | -60.6445 | 62.0773 | -60.8276 | -60.7636 | 61.6516 | 2.8793 | -0.09613 | -0.26093 | 62.0132 | -60.8368 | -0.28381 | 0.068665 | -0.10071 | -0.21973 | 0.073242 | -0.35706 | -0.36163 | -0.29297 | 0.004578 | 0.18311
645.5781 | 122.818 | -60.5392 | 62.0316 | 0.32261 | 0.0079142 | 0.0041707 | 0.0049947 | 0.065216 | -0.0007325 | 0.0684 | -60.6445 | 62.0453 | -60.8139 | -60.7773 | 61.6333 | 2.8702 | -0.068665 | -0.27466 | 62.0087 | -60.8551 | -0.27466 | 0.013733 | -0.10529 | -0.23804 | 0.07782 | -0.39825 | -0.37537 | -0.31586 | -0.022888 | 0.16937
646.5781 | 122.7951 | -60.5667 | 62.0224 | 0.36076 | 0.0077006 | 0.0039571 | 0.0064901 | 0.067352 | -0.0003051 | 0.068614 | -60.6491 | 62.0819 | -60.8505 | -60.7864 | 61.6287 | 2.8702 | -0.036621 | -0.29297 | 62.027 | -60.8551 | -0.28381 | 0.059509 | -0.082398 | -0.21973 | 0.068665 | -0.39368 | -0.39825 | -0.28839 | 0.004578 | 0.20142
647.5781 | 122.85 | -60.5209 | 62.0087 | 0.42943 | 0.0085552 | 0.0026753 | 0.0041403 | 0.065216 | -0.0037231 | 0.07075 | -60.6033 | 62.0453 | -60.8185 | -60.7452 | 61.6791 | 2.9388 | -0.1236 | -0.21973 | 61.9995 | -60.8231 | -0.29755 | 0.036621 | -0.082398 | -0.2243 | 0.07782 | -0.32959 | -0.32044 | -0.30212 | -0.009155 | 0.21515
648.5781 | 122.8912 | -60.5209 | 61.9904 | 0.43706 | 0.0079142 | 0.0026753 | 0.0030721 | 0.06607 | -0.0024415 | 0.067759 | -60.5576 | 62.0087 | -60.8002 | -60.704 | 61.7203 | 2.9572 | -0.1831 | -0.17853 | 61.9583 | -60.8231 | -0.27924 | 0.018311 | -0.036621 | -0.18311 | 0.11902 | -0.27008 | -0.23804 | -0.30212 | -0.032043 | 0.24262
649.5781 | 122.8775 | -60.5026 | 62.0041 | 1.8027 | 0.0070598 | 0.0045979 | 0.0034993 | 0.063934 | -0.0022277 | 0.0684 | -60.672 | 61.9675 | -60.8322 | -60.6766 | 61.734 | 2.9846 | -0.15564 | -0.1831 | 61.94 | -60.7956 | -0.32959 | -0.036621 | -0.16937 | -0.17395 | 0.11902 | -0.27008 | -0.20599 | -0.29297 | -0.064087 | 0.16022
650.5781 | 122.7997 | -60.5438 | 62.0132 | 0.32261 | 0.0098368 | 0.00032554 | 0.0047811 | 0.063934 | -0.0007325 | 0.067546 | -60.6354 | 62.0728 | -60.8185 | -60.7864 | 61.6196 | 2.8839 | -0.036621 | -0.27008 | 62.0407 | -60.8643 | -0.27466 | 0.059509 | -0.091553 | -0.24261 | 0.07782 | -0.39368 | -0.42114 | -0.32043 | 0.027465 | 0.1831
651.5781 | 122.8638 | -60.5347 | 62.0087 | 0.42943 | 0.0079142 | 0.0069477 | 0.0047811 | 0.065643 | -0.0026551 | 0.067118 | -60.6033 | 62.0361 | -60.8276 | -60.7407 | 61.6699 | 2.9343 | -0.12817 | -0.21515 | 61.9995 | -60.8459 | -0.29297 | 0.027466 | -0.068665 | -0.20599 | 0.10529 | -0.33875 | -0.32959 | -0.31128 | -0.009155 | 0.2243
652.5781 | 122.8271 | -60.5118 | 62.1185 | -0.058855 | 0.0049236 | 0.00096634 | 0.0020039 | 0.064361 | -0.0037231 | 0.066905 | -60.6491 | 62.0636 | -60.8093 | -60.7681 | 61.6745 | 2.948 | 0.16479 | -0.18768 | 62.0865 | -60.791 | -0.29755 | -0.054931 | -0.13733 | -0.25635 | 0.022889 | -0.44403 | -0.41199 | -0.27924 | -0.032043 | 0.16022
653.5781 | 122.7951 | -60.5255 | 62.1094 | 0.4218 | 0.007487 | 0.0082295 | 0.0058493 | 0.06543 | -0.0003051 | 0.0684 | -60.6216 | 62.0819 | -60.8231 | -60.9283 | 61.3724 | 2.6138 | 0.27466 | -0.16937 | 62.0956 | -60.8505 | -0.29755 | -0.027466 | -0.09613 | -0.40283 | -0.07782 | -0.737 | -0.72327 | -0.32501 | -0.013733 | 0.20142
654.5781 | 122.7585 | -60.5347 | 62.0544 | 0.33024 | 0.0085552 | 0.0048115 | 0.0054219 | 0.064361 | -9.1495e-05 | 0.067973 | -60.6354 | 62.0819 | -60.8185 | -60.7681 | 61.6196 | 2.8702 | -0.027466 | -0.29755 | 62.0316 | -60.8368 | -0.28381 | 0.027466 | -0.10071 | -0.23346 | 0.068665 | -0.43487 | -0.41199 | -0.30212 | -0.022888 | 0.1831
655.5781 | 122.8043 | -60.5576 | 62.059 | 0.6812 | 0.0083416 | 0.0028889 | 0.0067037 | 0.067139 | 0.0001221 | 0.069255 | -60.5667 | 62.114 | -60.8276 | -60.7864 | 61.6287 | 2.8702 | -0.018311 | -0.31586 | 62.0499 | -60.8551 | -0.27008 | 0.054932 | -0.009155 | -0.22888 | 0.068665 | -0.4303 | -0.42114 | -0.29755 | -0.009155 | 0.26093
656.5781 | 122.7859 | -60.5347 | 62.0453 | 0.41417 | 0.0079142 | 0.0095113 | 0.0067037 | 0.066925 | -9.1495e-05 | 0.070536 | -60.6125 | 62.1002 | -60.8047 | -60.7727 | 61.6562 | 2.9022 | -0.091553 | -0.28381 | 62.0453 | -60.8551 | -0.27008 | 0.054932 | -0.07782 | -0.23804 | 0.082398 | -0.3891 | -0.3891 | -0.32043 | 0 | 0.19226
657.5781 | 122.7905 | -60.5392 | 62.0361 | 0.26921 | 0.0094096 | 0.0054525 | 0.0043539 | 0.063721 | -9.1495e-05 | 0.065409 | -60.6216 | 62.1002 | -60.8231 | -60.7727 | 61.6333 | 2.8976 | -0.054932 | -0.30212 | 62.0544 | -60.8643 | -0.28381 | 0.064087 | -0.082397 | -0.23346 | 0.091553 | -0.40283 | -0.42114 | -0.32501 | 0.01831 | 0.20142
658.5781 | 122.7814 | -60.5438 | 62.0773 | 0.25395 | 0.0096232 | 0.0071615 | 0.0075581 | 0.065643 | -0.0009461 | 0.066905 | -60.6216 | 62.1277 | -60.8231 | -60.8093 | 61.6013 | 2.8931 | -0.004578 | -0.32959 | 62.0819 | -60.8643 | -0.27924 | 0.050354 | -0.07782 | -0.2655 | 0.054932 | -0.47608 | -0.48065 | -0.32043 | 0.004577 | 0.20142
659.5781 | 122.7127 | -60.5667 | 62.059 | 0.2921 | 0.0079142 | 0.0097249 | 0.0056355 | 0.064148 | -0.0013733 | 0.070109 | -60.6125 | 62.114 | -60.8002 | -60.8047 | 61.6241 | 2.8839 | 0.045776 | -0.32044 | 62.0773 | -60.8871 | -0.23346 | 0.054932 | -0.045777 | -0.23804 | 0.082397 | -0.43487 | -0.45319 | -0.32044 | 0.018311 | 0.18768
660.5781 | 122.8317 | -60.5347 | 62.0499 | 0.36076 | 0.01005 | 0.0016073 | 0.0058493 | 0.065857 | -9.1495e-05 | 0.070323 | -60.6125 | 62.1048 | -60.8185 | -60.7727 | 61.6516 | 2.9068 | -0.064087 | -0.29297 | 62.0956 | -60.8276 | -0.28381 | 0.054931 | -0.07782 | -0.23804 | 0.054932 | -0.39825 | -0.44403 | -0.29297 | 0.045776 | 0.20599
661.5781 | 122.7493 | -60.5347 | 62.0728 | 0.32261 | 0.0094096 | 0.0067341 | 0.0054219 | 0.063293 | 0.0003357 | 0.067759 | -60.6354 | 62.1323 | -60.8139 | -60.7956 | 61.615 | 2.8839 | 0.009155 | -0.33417 | 62.0773 | -60.8643 | -0.27924 | 0.059509 | -0.10071 | -0.26092 | 0.068665 | -0.45776 | -0.46234 | -0.32959 | 0.004578 | 0.17853
662.5781 | 122.8088 | -60.498 | 62.0316 | 0.36076 | 0.0049236 | 0.0043843 | -0.0012003 | 0.064789 | -0.0009461 | 0.069896 | -60.5896 | 62.0041 | -60.7727 | -60.7498 | 61.702 | 2.98 | -0.10986 | -0.20599 | 62.0636 | -60.7544 | -0.27466 | -0.027466 | -0.091553 | -0.25177 | 0.004578 | -0.32959 | -0.36163 | -0.25635 | 0.032044 | 0.18311
663.5781 | 122.7951 | -60.5392 | 62.0911 | 0.26158 | 0.0081278 | 0.0039571 | 0.0075581 | 0.063293 | -0.0007325 | 0.0684 | -60.5804 | 62.146 | -60.7819 | -60.7727 | 61.6333 | 2.916 | 0.045776 | -0.31586 | 62.0819 | -60.8368 | -0.24261 | 0.054932 | -0.041198 | -0.23346 | 0.064087 | -0.45776 | -0.44861 | -0.29755 | -0.009155 | 0.20142
664.5781 | 122.7539 | -60.5347 | 62.0911 | 0.35313 | 0.0081278 | 0.0043843 | 0.0060629 | 0.065216 | -0.0003051 | 0.069468 | -60.6216 | 62.1414 | -60.8093 | -60.7956 | 61.6196 | 2.8702 | 0.009155 | -0.32501 | 62.0773 | -60.8414 | -0.27466 | 0.050354 | -0.086975 | -0.26092 | 0.045777 | -0.4715 | -0.45776 | -0.3067 | -0.013732 | 0.18768
665.5781 | 122.7493 | -60.5392 | 62.0911 | 0.29973 | 0.012828 | 0.0056661 | 0.0043539 | 0.066711 | -0.0015869 | 0.065837 | -60.6171 | 62.1323 | -60.7956 | -60.7956 | 61.6058 | 2.8793 | 0.027466 | -0.32501 | 62.0956 | -60.8597 | -0.25635 | 0.041199 | -0.077819 | -0.25635 | 0.064087 | -0.48523 | -0.48981 | -0.32043 | 0.004578 | 0.17853
666.5781 | 122.7676 | -60.5072 | 62.0865 | 0.4218 | 0.0070598 | 0.012716 | 0.0041403 | 0.061371 | -0.0005189 | 0.068614 | -60.6216 | 62.1368 | -60.8047 | -60.7727 | 61.8576 | 3.0899 | -0.059509 | -0.34332 | 62.114 | -60.8231 | -0.29755 | 0.050354 | -0.11444 | -0.2655 | 0.050354 | -0.22888 | -0.25635 | -0.31586 | 0.027466 | 0.18311
667.5781 | 122.644 | -60.5118 | 62.027 | 0.36076 | 0.010905 | 0.0065205 | 0.0047811 | 0.066284 | -0.0030823 | 0.0684 | -60.6033 | 62.1414 | -60.791 | -60.791 | 61.6379 | 2.8885 | 0.009155 | -0.32044 | 62.1048 | -60.8597 | -0.27924 | 0.11444 | -0.091553 | -0.27924 | 0.068664 | -0.3891 | -0.46692 | -0.3479 | 0.077819 | 0.18768
668.5781 | 122.7585 | -60.5118 | 62.0911 | 0.4218 | 0.0085552 | 0.0099385 | 0.0022177 | 0.064575 | -0.0003051 | 0.067973 | -60.585 | 62.1231 | -60.7727 | -60.7773 | 61.647 | 2.9343 | -0.018311 | -0.32044 | 62.0956 | -60.8139 | -0.26093 | 0.032044 | -0.073242 | -0.2655 | 0.036621 | -0.44403 | -0.44861 | -0.30212 | 0.004578 | 0.18768
669.5781 | 122.7219 | -60.5072 | 62.1002 | 0.23869 | 0.0068462 | 0.0084431 | 0.0054219 | 0.065216 | 0.0014039 | 0.066905 | -60.553 | 62.1643 | -60.759 | -60.7269 | 61.6608 | 2.948 | 0.041199 | -0.27924 | 62.0773 | -60.8459 | -0.25177 | 0.064087 | -0.045777 | -0.21973 | 0.11902 | -0.43945 | -0.41656 | -0.33875 | -0.022888 | 0.20599
670.5781 | 122.7768 | -60.4935 | 62.0911 | 0.17766 | 0.011546 | 0.0069477 | 0.0058493 | 0.066925 | 0.0003357 | 0.066691 | -60.5255 | 62.1552 | -60.7727 | -60.7224 | 61.6745 | 2.9663 | 0.036621 | -0.25635 | 62.1277 | -60.8139 | -0.27924 | 0.064087 | -0.032044 | -0.22888 | 0.091553 | -0.41656 | -0.45319 | -0.32044 | 0.036622 | 0.24719
671.5781 | 122.7585 | -60.4889 | 62.0773 | 0.19291 | 0.0089824 | 0.0031025 | 0.0045675 | 0.064789 | -9.1495e-05 | 0.066478 | -60.5347 | 62.1414 | -60.7636 | -60.7132 | 61.6791 | 2.9663 | 0.036621 | -0.27008 | 62.1277 | -60.8093 | -0.27466 | 0.064086 | -0.045776 | -0.2243 | 0.09613 | -0.39825 | -0.44861 | -0.32043 | 0.050354 | 0.22888
672.5781 | 122.7356 | -60.5118 | 62.114 | 0.28447 | 0.0081278 | 0.010793 | 0.0030721 | 0.066711 | 0.0007629 | 0.068614 | -60.5576 | 62.1826 | -60.7773 | -60.759 | 61.6562 | 2.9068 | 0.059509 | -0.32501 | 62.1506 | -60.8322 | -0.2655 | 0.068664 | -0.045776 | -0.24719 | 0.073242 | -0.45776 | -0.49439 | -0.32043 | 0.036621 | 0.21973
673.5781 | 122.7997 | -60.5026 | 62.114 | 0.25395 | 0.011119 | 0.0071615 | 0.0079855 | 0.066925 | -0.0007325 | 0.069255 | -60.5621 | 62.1735 | -60.7544 | -60.7361 | 61.647 | 2.9297 | 0.054932 | -0.31128 | 62.1185 | -60.791 | -0.25177 | 0.059509 | -0.059509 | -0.23346 | 0.054932 | -0.46692 | -0.4715 | -0.28839 | 0.004577 | 0.19226
674.5781 | 122.6715 | -60.5118 | 62.0682 | 0.35313 | 0.0087688 | 0.0043843 | 0.0045675 | 0.067139 | -9.1495e-05 | 0.0684 | -60.5759 | 62.1689 | -60.759 | -60.7681 | 61.6516 | 2.9022 | -0.013733 | -0.34332 | 62.1506 | -60.8231 | -0.24719 | 0.10071 | -0.064087 | -0.25635 | 0.054932 | -0.41656 | -0.49896 | -0.31128 | 0.082398 | 0.1831
675.5781 | 122.7814 | -60.5301 | 62.1506 | 0.25395 | 0.0079142 | 0.0090841 | 0.0047811 | 0.065643 | -0.0026551 | 0.069468 | -60.553 | 62.178 | -60.7727 | -60.7224 | 61.6608 | 2.9205 | 0.068665 | -0.28839 | 62.1277 | -60.8002 | -0.24262 | 0.027466 | -0.022889 | -0.19226 | 0.07782 | -0.48981 | -0.46692 | -0.27008 | -0.022888 | 0.21973
676.5781 | 122.7768 | -60.4843 | 62.1231 | 0.23869 | 0.0077006 | 0.0067341 | 0.0047811 | 0.065002 | -0.0009461 | 0.069041 | -60.5301 | 62.1689 | -60.7452 | -60.7224 | 61.6699 | 2.9205 | 0.054932 | -0.30212 | 62.1643 | -60.8185 | -0.26093 | 0.045776 | -0.045776 | -0.23804 | 0.09613 | -0.45319 | -0.49439 | -0.33417 | 0.041199 | 0.21515
677.5781 | 122.7356 | -60.5118 | 62.1094 | 0.36839 | 0.010691 | 0.0069477 | 0.0054219 | 0.06543 | -9.1495e-05 | 0.067546 | -60.5759 | 62.1735 | -60.7681 | -60.7636 | 61.6516 | 2.9022 | 0 | -0.34332 | 62.146 | -60.8093 | -0.25635 | 0.064087 | -0.064087 | -0.25177 | 0.045776 | -0.45776 | -0.49438 | -0.29755 | 0.036621 | 0.19226
678.5781 | 122.7859 | -60.4752 | 62.1323 | 0.22343 | 0.011119 | 0.0039571 | 0.0052083 | 0.066711 | -9.1495e-05 | 0.068827 | -60.5392 | 62.1689 | -60.7498 | -60.7132 | 61.6653 | 2.9297 | 0.045776 | -0.29755 | 62.1643 | -60.8093 | -0.27466 | 0.036621 | -0.064087 | -0.23804 | 0.09613 | -0.46692 | -0.49896 | -0.33417 | 0.032044 | 0.21057
679.5781 | 122.731 | -60.498 | 62.1277 | 0.33024 | 0.0087688 | 0.0097249 | 0.0024313 | 0.066284 | -0.0018005 | 0.066905 | -60.585 | 62.1689 | -60.7498 | -60.7407 | 61.6562 | 2.9114 | 0.013733 | -0.33417 | 62.1414 | -60.8139 | -0.25177 | 0.041198 | -0.086975 | -0.24262 | 0.073242 | -0.4715 | -0.48523 | -0.31586 | 0.013732 | 0.16479
680.5781 | 122.7814 | -60.4797 | 62.1231 | 0.25395 | 0.011119 | 0.010793 | 0.0060629 | 0.065857 | -0.0015869 | 0.068187 | -60.5255 | 62.1735 | -60.7224 | -60.7269 | 61.6974 | 2.9388 | 0.050354 | -0.28381 | 62.1552 | -60.791 | -0.24262 | 0.050354 | -0.045777 | -0.24719 | 0.064087 | -0.42572 | -0.45776 | -0.31128 | 0.032043 | 0.19684
681.5781 | 122.7722 | -60.4797 | 62.1368 | 0.25395 | 0.011119 | 0.0065205 | 0.0073445 | 0.067352 | -0.0005189 | 0.069255 | -60.5209 | 62.1552 | -60.7269 | -60.7086 | 61.6837 | 2.9526 | 0.022888 | -0.29755 | 62.1918 | -60.7819 | -0.24719 | 0.01831 | -0.041199 | -0.22888 | 0.073242 | -0.45319 | -0.50812 | -0.30212 | 0.054931 | 0.20599
682.5781 | 122.7539 | -60.4568 | 62.1277 | -0.33351 | 0.010264 | 0.0069477 | 0.0047811 | 0.06543 | -0.0013733 | 0.068187 | -60.5347 | 62.1872 | -60.759 | -60.7315 | 61.6699 | 2.9022 | 0.009155 | -0.29297 | 62.1918 | -60.791 | -0.30212 | 0.059509 | -0.07782 | -0.27466 | 0.05951 | -0.45776 | -0.52185 | -0.33417 | 0.064086 | 0.2243
683.5781 | 122.7402 | -60.4752 | 62.1231 | 0.26921 | 0.010478 | 0.0043843 | 0.0026449 | 0.065643 | -0.0015869 | 0.068827 | -60.5576 | 62.1689 | -60.7544 | -60.7544 | 61.6287 | 2.9068 | 0.027466 | -0.32501 | 62.1506 | -60.791 | -0.27924 | 0.045776 | -0.082397 | -0.27924 | 0.036621 | -0.49439 | -0.52185 | -0.31586 | 0.027466 | 0.19684
684.5781 | 122.8088 | -60.3973 | 62.1231 | 0.46757 | 0.0072734 | 0.0090841 | 0.0043539 | 0.065857 | -0.0007325 | 0.068187 | -60.5255 | 62.1506 | -60.7498 | -60.6903 | 61.734 | 2.9617 | -0.10986 | -0.2655 | 62.1231 | -60.7544 | -0.35248 | 0.027466 | -0.12817 | -0.29297 | 0.064087 | -0.3891 | -0.3891 | -0.35706 | 0 | 0.2243
685.5781 | 122.731 | -60.4843 | 62.1277 | 0.20817 | 0.0094096 | 0.0058797 | 0.0049947 | 0.064789 | -0.0003051 | 0.069682 | -60.5392 | 62.1964 | -60.7544 | -60.7452 | 61.647 | 2.8976 | 0.045776 | -0.34332 | 62.1643 | -60.8002 | -0.27008 | 0.068664 | -0.054932 | -0.26093 | 0.054932 | -0.48065 | -0.51727 | -0.31586 | 0.036621 | 0.21515
686.5781 | 122.8226 | -60.4431 | 62.1094 | 0.41417 | 0.0087688 | 0.0063069 | 0.0022177 | 0.06543 | -0.0020141 | 0.0684 | -60.5118 | 62.1597 | -60.7361 | -60.6857 | 61.7111 | 2.9526 | -0.1236 | -0.27466 | 62.1552 | -60.7681 | -0.29297 | 0.050354 | -0.068665 | -0.24262 | 0.082397 | -0.39825 | -0.44403 | -0.32501 | 0.045776 | 0.2243
687.5781 | 122.7081 | -60.4568 | 62.1414 | 0.25395 | 0.0089824 | 0.0088703 | 0.0056355 | 0.065643 | -0.0024415 | 0.067546 | -60.5164 | 62.2101 | -60.7315 | -60.7178 | 61.6562 | 2.8839 | 0.036621 | -0.3479 | 62.1552 | -60.8002 | -0.27466 | 0.068665 | -0.059509 | -0.26093 | 0.082398 | -0.48523 | -0.49896 | -0.34332 | 0.013733 | 0.21515
688.5781 | 122.7539 | -60.466 | 62.146 | 0.24632 | 0.0089824 | 0.0065205 | 0.0039267 | 0.065216 | -0.0022277 | 0.070323 | -60.5026 | 62.2192 | -60.7315 | -60.7132 | 61.6608 | 2.8931 | 0.032043 | -0.32044 | 62.2101 | -60.7498 | -0.2655 | 0.073242 | -0.036622 | -0.24719 | 0.036621 | -0.48523 | -0.54932 | -0.28381 | 0.064087 | 0.22888
689.5781 | 122.7997 | -60.4385 | 62.1277 | 0.41417 | 0.010691 | 0.0073751 | 0.0045675 | 0.067352 | 0.0001221 | 0.068827 | -60.498 | 62.2009 | -60.7178 | -60.6857 | 61.7065 | 2.916 | -0.07782 | -0.3067 | 62.146 | -60.759 | -0.27923 | 0.073242 | -0.059509 | -0.24719 | 0.073242 | -0.42114 | -0.43945 | -0.32043 | 0.01831 | 0.21973
690.5781 | 122.7951 | -60.4294 | 62.1368 | 0.37602 | 0.0072734 | 0.0067341 | 0.0028585 | 0.06607 | -0.0018005 | 0.067973 | -60.5072 | 62.1872 | -60.7132 | -60.6903 | 61.7111 | 2.9022 | -0.082397 | -0.29755 | 62.1689 | -60.7407 | -0.28381 | 0.050354 | -0.07782 | -0.26093 | 0.050354 | -0.42572 | -0.45776 | -0.31128 | 0.032043 | 0.20599
691.5781 | 122.8226 | -60.4477 | 62.1826 | 0.29973 | 0.010478 | 0.0090841 | 0.0064901 | 0.064361 | 0.0009765 | 0.068187 | -60.5209 | 62.2101 | -60.6995 | -60.7086 | 61.6974 | 2.9892 | -0.3891 | -0.44403 | 62.1002 | -60.7819 | -0.25177 | 0.027466 | -0.073242 | -0.26093 | 0.073242 | -0.48523 | -0.40283 | -0.33417 | -0.082397 | 0.17853
692.5781 | 122.8455 | -60.4019 | 62.1185 | 0.45231 | 0.0077006 | 0.0067341 | 0.0020039 | 0.066498 | -0.0013733 | 0.066905 | -60.4523 | 62.1368 | -60.6995 | -60.5804 | 61.7935 | 2.9984 | -0.15106 | -0.20142 | 62.146 | -60.7224 | -0.29755 | 0.018311 | -0.050354 | -0.17853 | 0.14191 | -0.32501 | -0.35248 | -0.32043 | 0.027466 | 0.24719
693.5781 | 122.8134 | -60.4248 | 62.1552 | 0.36839 | 0.0096232 | 0.0048115 | 0.0045675 | 0.064148 | -0.0011597 | 0.068614 | -60.5026 | 62.2101 | -60.6995 | -60.6766 | 61.7065 | 2.8931 | -0.054932 | -0.31586 | 62.146 | -60.759 | -0.27466 | 0.054932 | -0.07782 | -0.25177 | 0.082397 | -0.44861 | -0.43945 | -0.33417 | -0.009155 | 0.19684
694.5781 | 122.7905 | -60.4202 | 62.1872 | 0.28447 | 0.0087688 | 0.00053914 | 0.0062765 | 0.065857 | -0.0005189 | 0.067546 | -60.5164 | 62.2238 | -60.6857 | -60.6949 | 61.6791 | 2.8839 | -0.018311 | -0.33417 | 62.1872 | -60.7452 | -0.2655 | 0.036621 | -0.09613 | -0.27466 | 0.050354 | -0.50812 | -0.50812 | -0.32501 | 0 | 0.16937
695.5781 | 122.7264 | -60.4431 | 62.1826 | 0.3455 | 0.011332 | 0.0084431 | 0.0032857 | 0.065216 | -0.0011597 | 0.070109 | -60.5026 | 62.233 | -60.704 | -60.7086 | 61.6653 | 2.8885 | 0.004578 | -0.32501 | 62.2009 | -60.7407 | -0.26093 | 0.050354 | -0.05951 | -0.2655 | 0.032044 | -0.51727 | -0.53558 | -0.29755 | 0.018311 | 0.20142
696.5781 | 122.7814 | -60.4202 | 62.1506 | -0.020708 | 0.0087688 | 0.0075887 | 0.0045675 | 0.067139 | -9.1495e-05 | 0.067118 | -60.4431 | 62.2559 | -60.7132 | -60.6674 | 61.7157 | 2.861 | -0.009155 | -0.28839 | 62.2147 | -60.7452 | -0.29297 | 0.10529 | -0.022888 | -0.24719 | 0.07782 | -0.43488 | -0.49896 | -0.32501 | 0.064087 | 0.27008
697.5781 | 122.7631 | -60.4111 | 62.1918 | -2.1417 | 0.0094096 | 0.0028889 | 0.0020039 | 0.066498 | -0.0020141 | 0.068614 | -60.4477 | 62.2559 | -60.672 | -60.6583 | 61.702 | 2.8519 | -0.009155 | -0.29297 | 62.1918 | -60.7224 | -0.26093 | 0.064087 | -0.036621 | -0.24719 | 0.064087 | -0.48981 | -0.48981 | -0.31128 | 0 | 0.2243
698.5781 | 122.8958 | -60.379 | 62.1323 | 0.3455 | 0.0081278 | 0.0045979 | 0.0013631 | 0.065857 | -0.0022277 | 0.067332 | -60.3973 | 62.1506 | -60.6537 | -60.5759 | 61.7889 | 2.9846 | -0.18768 | -0.18768 | 62.1597 | -60.6857 | -0.27466 | 0.018311 | -0.018311 | -0.19684 | 0.10986 | -0.34332 | -0.37079 | -0.3067 | 0.027466 | 0.25635
699.5781 | 122.8043 | -60.4019 | 62.2009 | 0.39128 | 0.0087688 | 0.0031025 | 0.00050867 | 0.064148 | -0.0007325 | 0.06605 | -60.3012 | 62.2238 | -60.6903 | -60.6995 | 61.7569 | 2.916 | -0.013733 | -0.32044 | 62.2192 | -60.7315 | -0.28839 | 0.022888 | 0.10071 | -0.29755 | 0.032043 | -0.44403 | -0.46234 | -0.32959 | 0.01831 | 0.3891
700.5781 | 122.8317 | -60.3928 | 62.1918 | 0.39891 | 0.0070598 | 0.0054525 | 0.0045675 | 0.065643 | -0.0005189 | 0.069682 | -60.4568 | 62.2101 | -60.6812 | -60.6308 | 61.734 | 2.8839 | -0.09613 | -0.27466 | 62.2101 | -60.6995 | -0.28839 | 0.018311 | -0.064087 | -0.23804 | 0.068665 | -0.45776 | -0.47607 | -0.3067 | 0.018311 | 0.2243
701.5781 | 122.8088 | -60.4156 | 62.2192 | 0.38365 | 0.010478 | 0.0071615 | 0.0052083 | 0.065857 | -0.0005189 | 0.0684 | -60.4706 | 62.2559 | -60.6491 | -60.8917 | 61.4777 | 2.8152 | 0.25635 | -0.28381 | 62.2101 | -60.7132 | -0.23346 | 0.036621 | -0.054932 | -0.47608 | -0.17853 | -0.74158 | -0.73242 | -0.29755 | -0.009155 | 0.17853
702.5781 | 122.818 | -60.3882 | 62.1826 | 0.36839 | 0.011119 | 0.0050251 | 0.0054219 | 0.065002 | 0.0011901 | 0.067973 | -60.4431 | 62.233 | -60.6812 | -60.6308 | 61.7477 | 2.8885 | -0.068665 | -0.28381 | 62.2009 | -60.7224 | -0.29297 | 0.050354 | -0.054931 | -0.24261 | 0.091553 | -0.43487 | -0.45319 | -0.33417 | 0.018311 | 0.23804
703.5781 | 122.8043 | -60.379 | 62.1918 | 0.36839 | 0.01005 | 0.0082295 | 0.0043539 | 0.065643 | -0.0015869 | 0.069041 | -60.4431 | 62.2559 | -60.6903 | -60.6308 | 61.7249 | 2.8793 | -0.068665 | -0.30212 | 62.2101 | -60.7132 | -0.31128 | 0.064087 | -0.064087 | -0.25177 | 0.082398 | -0.46692 | -0.48523 | -0.33417 | 0.018311 | 0.24719
704.5781 | 122.8821 | -60.3516 | 62.1597 | 0.45994 | 0.0079142 | 0.0050251 | -0.00055953 | 0.065643 | 0.0011901 | 0.069468 | -60.3653 | 62.1735 | -60.64 | -60.672 | 61.6562 | 2.9205 | 0 | -0.16479 | 62.1826 | -60.6216 | -0.28839 | 0.013733 | -0.013733 | -0.32043 | -0.050354 | -0.50354 | -0.52643 | -0.27008 | 0.022888 | 0.27466
705.5781 | 122.7356 | -60.4111 | 62.1964 | 0.4752 | 0.0081278 | 0.0054525 | 0.0032857 | 0.064789 | -0.0007325 | 0.067546 | -60.4385 | 62.2559 | -60.6537 | -60.6216 | 61.7386 | 2.861 | -0.045776 | -0.29755 | 62.1872 | -60.7224 | -0.24262 | 0.059509 | -0.027466 | -0.21057 | 0.10071 | -0.45776 | -0.44861 | -0.31128 | -0.009155 | 0.21515
706.5781 | 122.7951 | -60.379 | 62.1872 | 0.14714 | 0.0072734 | 0.0060933 | 0.0062765 | 0.066498 | 0.0014039 | 0.067546 | -60.4614 | 62.2467 | -60.6583 | -60.6216 | 61.7432 | 2.8656 | -0.013733 | -0.28381 | 62.2467 | -60.6857 | -0.27924 | 0.059509 | -0.082398 | -0.24262 | 0.064087 | -0.44403 | -0.50354 | -0.3067 | 0.059509 | 0.19684
707.5781 | 122.7951 | -60.3287 | 62.1277 | 0.4218 | 0.0085552 | 0.0028889 | 0.0022177 | 0.064361 | -0.0011597 | 0.068614 | -60.3607 | 62.1964 | -60.6308 | -60.5209 | 61.8393 | 2.9709 | -0.21515 | -0.16479 | 62.2101 | -60.6583 | -0.30212 | 0.068664 | -0.032044 | -0.19226 | 0.13733 | -0.28839 | -0.37079 | -0.32959 | 0.082397 | 0.27008
708.5781 | 122.7219 | -60.3699 | 62.2192 | -0.21907 | 0.0089824 | 0.0078023 | 0.0052083 | 0.063293 | -0.0009461 | 0.070964 | -60.4523 | 62.2742 | -60.6354 | -60.6308 | 61.7157 | 2.8519 | -0.013733 | -0.27466 | 62.2421 | -60.6995 | -0.2655 | 0.054932 | -0.082398 | -0.26093 | 0.068665 | -0.50354 | -0.52643 | -0.32959 | 0.022888 | 0.1831
709.5781 | 122.8958 | -60.3653 | 62.2101 | 0.44468 | 0.011759 | 0.010793 | 0.0030721 | 0.064361 | -0.0011597 | 0.067118 | -60.4111 | 62.2513 | -60.64 | -60.5576 | 61.7935 | 2.8976 | -0.12817 | -0.22888 | 62.1964 | -60.64 | -0.27466 | 0.041199 | -0.045777 | -0.19226 | 0.082398 | -0.41656 | -0.40283 | -0.27466 | -0.013733 | 0.22888
710.5781 | 122.8226 | -60.3516 | 62.233 | 0.45231 | 0.0085552 | 0.0063069 | 0.0026449 | 0.064575 | -0.0003051 | 0.068187 | -60.3928 | 62.2559 | -60.6125 | -60.5713 | 61.7935 | 2.8885 | -0.12817 | -0.23346 | 62.2101 | -60.64 | -0.26093 | 0.022888 | -0.041199 | -0.21973 | 0.068665 | -0.43945 | -0.41656 | -0.28839 | -0.022888 | 0.21973
711.5781 | 122.8226 | -60.3561 | 62.2284 | 0.42943 | 0.0096232 | 0.0058797 | 0.0052083 | 0.064361 | -9.1495e-05 | 0.067546 | -60.4156 | 62.2696 | -60.64 | -60.5667 | 61.7798 | 2.8839 | -0.10986 | -0.24261 | 62.1964 | -60.6354 | -0.28381 | 0.041198 | -0.059509 | -0.21057 | 0.068665 | -0.44861 | -0.41657 | -0.27924 | -0.032044 | 0.22431
712.5781 | 122.85 | -60.3333 | 62.2284 | 0.4218 | 0.0062052 | 0.0063069 | 0.0034993 | 0.064361 | -0.0035095 | 0.068614 | -60.3928 | 62.2787 | -60.6216 | -60.5713 | 61.7844 | 2.8976 | -0.10986 | -0.24719 | 62.233 | -60.6537 | -0.28839 | 0.050354 | -0.059509 | -0.23804 | 0.082398 | -0.44403 | -0.44861 | -0.32043 | 0.004577 | 0.22888
713.5781 | 122.7768 | -60.3561 | 62.2192 | 0.41417 | 0.0094096 | 0.0056661 | 0.0032857 | 0.064361 | -0.0024415 | 0.069041 | -60.4019 | 62.2696 | -60.6216 | -60.5713 | 61.7844 | 2.8793 | -0.10071 | -0.23804 | 62.2238 | -60.6583 | -0.2655 | 0.050354 | -0.045777 | -0.21515 | 0.086975 | -0.43487 | -0.43945 | -0.30212 | 0.004578 | 0.21973
714.5781 | 122.818 | -60.2875 | 62.2513 | 0.24632 | 0.00471 | 0.0041707 | -0.0041911 | 0.060303 | -0.0005189 | 0.068614 | -60.4111 | 62.1918 | -60.6171 | -60.5392 | 61.8439 | 2.9343 | -0.07782 | -0.16022 | 62.2284 | -60.5759 | -0.32959 | -0.05951 | -0.1236 | -0.25177 | 0.036621 | -0.40741 | -0.38452 | -0.28839 | -0.022888 | 0.20599
715.5781 | 122.8226 | -60.347 | 62.2787 | 0.41417 | 0.0094096 | 0.0078023 | 0.0067037 | 0.062652 | 0.0009765 | 0.067973 | -60.4156 | 62.2971 | -60.6354 | -60.8093 | 61.5189 | 2.7878 | 0.2655 | -0.26093 | 62.2742 | -60.6491 | -0.28839 | 0.01831 | -0.068664 | -0.46234 | -0.16022 | -0.75989 | -0.75531 | -0.30212 | -0.004578 | 0.21973
716.5781 | 122.8867 | -60.2966 | 62.2192 | 0.39891 | 0.0087688 | 0.0058797 | 0.0026449 | 0.063507 | -0.0005189 | 0.066478 | -60.3195 | 62.2238 | -60.5896 | -60.4797 | 61.8484 | 2.9526 | -0.17853 | -0.15564 | 62.2192 | -60.5942 | -0.29297 | 0.004578 | -0.022888 | -0.18311 | 0.11444 | -0.37079 | -0.37079 | -0.29755 | 0 | 0.27008
717.5781 | 122.8317 | -60.3058 | 62.2513 | 0.35313 | 0.0064188 | 0.0041707 | -0.0014139 | 0.061371 | -0.0011597 | 0.067973 | -60.3333 | 62.2147 | -60.5942 | -60.5072 | 61.8393 | 2.948 | -0.15564 | -0.15106 | 62.2101 | -60.6171 | -0.28839 | -0.036621 | -0.027466 | -0.20142 | 0.10986 | -0.41199 | -0.37079 | -0.31128 | -0.041199 | 0.26093
718.5781 | 122.85 | -60.2783 | 62.2421 | 0.45994 | 0.0085552 | 0.0045979 | 0.0047811 | 0.062866 | -0.0026551 | 0.067332 | -60.3287 | 62.2375 | -60.5896 | -60.4706 | 61.8713 | 2.9526 | -0.16479 | -0.15106 | 62.233 | -60.6033 | -0.31128 | -0.004577 | -0.050354 | -0.19226 | 0.13275 | -0.37079 | -0.36163 | -0.32501 | -0.009155 | 0.26093
719.5781 | 122.8546 | -60.2554 | 62.2604 | 0.42943 | 0.0081278 | 0.0099385 | 0.0049947 | 0.064789 | 0.0009765 | 0.069255 | -60.3149 | 62.2696 | -60.5621 | -60.466 | 61.8484 | 2.9526 | -0.15564 | -0.15564 | 62.2284 | -60.6171 | -0.3067 | 0.009155 | -0.059509 | -0.21057 | 0.15106 | -0.41199 | -0.37994 | -0.36163 | -0.032043 | 0.24719
720.5781 | 122.8821 | -60.2875 | 62.2559 | 0.45231 | 0.0068462 | 0.0031025 | 0.0043539 | 0.064789 | 0.0016175 | 0.066691 | -60.3104 | 62.2787 | -60.5896 | -60.4706 | 61.8484 | 2.9526 | -0.17395 | -0.13733 | 62.2284 | -60.5988 | -0.30212 | 0.022889 | -0.022888 | -0.18311 | 0.12817 | -0.40741 | -0.37994 | -0.31128 | -0.027465 | 0.27924
721.5781 | 122.8409 | -60.2463 | 62.2559 | 0.45231 | 0.0059916 | 0.0043843 | 0.0039267 | 0.06308 | -0.0009461 | 0.068614 | -60.3241 | 62.2604 | -60.5621 | -60.4797 | 61.8668 | 2.9572 | -0.1831 | -0.14191 | 62.2238 | -60.5667 | -0.31586 | 0.004578 | -0.07782 | -0.23346 | 0.086975 | -0.3891 | -0.35706 | -0.32043 | -0.032043 | 0.23804
722.5781 | 122.8683 | -60.2646 | 62.2604 | 0.40654 | 0.007487 | 0.0075887 | 0.0052083 | 0.065002 | -0.0018005 | 0.067759 | -60.3241 | 62.2879 | -60.5713 | -60.4477 | 61.853 | 2.9663 | -0.16937 | -0.17395 | 62.2696 | -60.585 | -0.3067 | 0.027466 | -0.05951 | -0.18311 | 0.13733 | -0.40741 | -0.41657 | -0.32044 | 0.009155 | 0.24719
723.5781 | 122.8958 | -60.2737 | 62.2238 | 0.44468 | 0.0062052 | 0.0063069 | 0.0024313 | 0.063934 | -0.0028687 | 0.0684 | -60.26 | 62.2467 | -60.5576 | -60.4294 | 61.8851 | 2.9846 | -0.19226 | -0.14648 | 62.2375 | -60.6033 | -0.28381 | 0.022888 | 0.013733 | -0.15564 | 0.17395 | -0.33874 | -0.35248 | -0.32959 | 0.013733 | 0.29755
724.5781 | 122.8455 | -60.2325 | 62.2696 | 0.18529 | 0.0055644 | 0.0024617 | -0.0018413 | 0.063507 | -0.0026551 | 0.066264 | -60.347 | 62.2604 | -60.5713 | -60.4019 | 61.8073 | 2.9526 | -0.032043 | -0.16022 | 62.2742 | -60.5484 | -0.33875 | -0.009155 | -0.11444 | -0.16937 | 0.14648 | -0.46234 | -0.46692 | -0.31586 | 0.004578 | 0.2243
725.5781 | 122.8821 | -60.2692 | 62.2925 | 0.43706 | 0.0070598 | 0.0060933 | 0.0062765 | 0.061798 | -0.0013733 | 0.067759 | -60.2966 | 62.3154 | -60.5438 | -60.4568 | 61.8759 | 2.9617 | -0.14191 | -0.15564 | 62.2879 | -60.5804 | -0.27466 | 0.022889 | -0.027466 | -0.18768 | 0.1236 | -0.41656 | -0.41199 | -0.31128 | -0.004577 | 0.24719
726.5781 | 122.8226 | -60.2554 | 62.2375 | 0.4218 | 0.0072734 | 0.0056661 | 0.0054219 | 0.063721 | -0.0003051 | 0.068827 | -60.2371 | 62.265 | -60.5621 | -60.434 | 61.9125 | 3.0167 | -0.20142 | -0.12817 | 62.2421 | -60.553 | -0.3067 | 0.027466 | 0.01831 | -0.17853 | 0.11902 | -0.32501 | -0.32959 | -0.29755 | 0.004577 | 0.32501
727.5781 | 122.9187 | -60.228 | 62.3016 | 0.39128 | 0.0064188 | 0.0069477 | 0.0041403 | 0.063934 | 0.0009765 | 0.066905 | -60.2509 | 62.2833 | -60.5301 | -60.4202 | 61.9125 | 3.0167 | -0.20599 | -0.11902 | 62.265 | -60.5301 | -0.30212 | -0.018311 | -0.022888 | -0.19226 | 0.10986 | -0.3891 | -0.35248 | -0.30212 | -0.036621 | 0.27924
728.5781 | 122.8912 | -60.2188 | 62.2971 | 0.42943 | 0.0062052 | 0.0069477 | 0.0039267 | 0.061798 | -0.0011597 | 0.0684 | -60.2463 | 62.2604 | -60.5255 | -60.4248 | 61.9217 | 3.0212 | -0.20142 | -0.13275 | 62.2742 | -60.5255 | -0.3067 | -0.036621 | -0.027466 | -0.20599 | 0.10071 | -0.37537 | -0.35248 | -0.3067 | -0.022888 | 0.27924
729.5781 | 122.8638 | -60.2051 | 62.3062 | 0.38365 | 0.0068462 | 0.0033161 | 0.0017903 | 0.062866 | -0.0018005 | 0.067759 | -60.2371 | 62.265 | -60.5347 | -60.3973 | 61.9125 | 3.0167 | -0.21057 | -0.10986 | 62.265 | -60.5484 | -0.32959 | -0.041198 | -0.032044 | -0.19226 | 0.15106 | -0.39368 | -0.35248 | -0.34332 | -0.041198 | 0.29755
730.5781 | 122.8546 | -60.2188 | 62.2925 | 0.51335 | 0.0081278 | 0.0054525 | 0.0024313 | 0.062866 | -0.0018005 | 0.069255 | -60.2646 | 62.2696 | -60.5026 | -60.4065 | 61.9171 | 3.0029 | -0.16479 | -0.11902 | 62.2879 | -60.5347 | -0.28381 | -0.022888 | -0.045776 | -0.18768 | 0.12817 | -0.37537 | -0.37079 | -0.31586 | -0.004577 | 0.23804
731.5781 | 122.8455 | -60.2097 | 62.3154 | 0.40654 | 0.0051372 | 0.0054525 | 0.0011495 | 0.062225 | -0.0011597 | 0.070536 | -60.26 | 62.2742 | -60.5347 | -60.4202 | 61.9125 | 3.035 | -0.17853 | -0.11444 | 62.265 | -60.5209 | -0.32501 | -0.041199 | -0.050354 | -0.21057 | 0.10071 | -0.40283 | -0.35248 | -0.31128 | -0.050354 | 0.27466
732.5781 | 122.8729 | -60.2371 | 62.3062 | 0.28447 | 0.0055644 | 0.0022481 | 0.0034993 | 0.06073 | 0.0003357 | 0.068827 | -60.2463 | 62.2742 | -60.5026 | -60.3836 | 61.908 | 3.0396 | -0.17395 | -0.10071 | 62.2742 | -60.4843 | -0.2655 | -0.032043 | -0.009155 | -0.14648 | 0.10071 | -0.39825 | -0.36621 | -0.24719 | -0.032043 | 0.25635
733.5781 | 122.8271 | -60.2188 | 62.3199 | 0.33787 | 0.0051372 | 0.0026753 | 0.0011495 | 0.059448 | -0.0015869 | 0.066905 | -60.2783 | 62.265 | -60.5255 | -60.4477 | 61.8805 | 3.0167 | -0.10986 | -0.14191 | 62.2971 | -60.5118 | -0.3067 | -0.054931 | -0.059509 | -0.22888 | 0.064087 | -0.43945 | -0.41656 | -0.29297 | -0.022888 | 0.24719
734.5781 | 122.8775 | -60.1868 | 62.3383 | 0.38365 | 0.0055644 | 0.0039571 | 0.0020039 | 0.060516 | -9.1495e-05 | 0.066264 | -60.2646 | 62.2879 | -60.4706 | -60.4294 | 61.8851 | 3.0121 | -0.11902 | -0.12817 | 62.2971 | -60.5072 | -0.28381 | -0.050354 | -0.077819 | -0.24261 | 0.07782 | -0.45319 | -0.41199 | -0.32043 | -0.041199 | 0.20599
735.5781 | 122.8912 | -60.2005 | 62.3108 | 0.025068 | 0.0049236 | 0.0024617 | 0.0037129 | 0.061157 | -0.0020141 | 0.068614 | -60.228 | 62.3108 | -60.4614 | -60.379 | 61.94 | 3.0762 | -0.1831 | -0.10529 | 62.2742 | -60.4843 | -0.26093 | 0 | -0.027466 | -0.17853 | 0.10529 | -0.37079 | -0.33417 | -0.28381 | -0.036621 | 0.23346
736.5781 | 122.8546 | -60.1868 | 62.3428 | 0.80327 | 0.0062052 | 0.0041707 | 0.0039267 | 0.062866 | -0.0018005 | 0.067332 | -60.1776 | 62.2971 | -60.498 | -60.379 | 61.9263 | 3.0716 | -0.17853 | -0.10071 | 62.2971 | -60.4935 | -0.31128 | -0.045776 | 0.009156 | -0.19226 | 0.11444 | -0.41656 | -0.37079 | -0.3067 | -0.045776 | 0.32043
737.5781 | 122.8455 | -60.1913 | 62.3795 | 0.26158 | 0.0068462 | 0.0050251 | 0.0011495 | 0.05838 | 0.0003357 | 0.067973 | -60.26 | 62.2971 | -60.4889 | -60.4065 | 61.9171 | 3.0533 | -0.064087 | -0.11444 | 62.3245 | -60.4935 | -0.29755 | -0.082398 | -0.068665 | -0.21515 | 0.086975 | -0.46234 | -0.40741 | -0.30212 | -0.054932 | 0.22888
738.5781 | 122.8271 | -60.1639 | 62.3611 | 0.4218 | 0.0064188 | 0.0026753 | 0.0028585 | 0.06073 | -0.0018005 | 0.066905 | -60.2234 | 62.3062 | -60.4797 | -60.3882 | 61.908 | 3.067 | -0.14191 | -0.11902 | 62.3108 | -60.4752 | -0.31586 | -0.054932 | -0.05951 | -0.22431 | 0.086975 | -0.45319 | -0.40283 | -0.31128 | -0.050354 | 0.25635
739.5781 | 122.8088 | -60.1913 | 62.3566 | 0.36839 | 0.005778 | 0.0018209 | 0.0013631 | 0.060516 | -0.0018005 | 0.069896 | -60.2188 | 62.3154 | -60.4706 | -60.3745 | 61.9171 | 3.0808 | -0.14648 | -0.13275 | 62.3291 | -60.498 | -0.27924 | -0.041198 | -0.027466 | -0.18311 | 0.1236 | -0.43945 | -0.41199 | -0.3067 | -0.027465 | 0.25177
740.5781 | 122.8134 | -60.1639 | 62.3886 | 0.30736 | 0.0059916 | 0.0035299 | 8.1267e-05 | 0.061157 | -0.0030823 | 0.069682 | -60.2142 | 62.3291 | -60.4477 | -60.3745 | 61.9217 | 3.1036 | -0.059509 | -0.09613 | 62.3154 | -60.4523 | -0.28381 | -0.059509 | -0.050354 | -0.21057 | 0.07782 | -0.46692 | -0.39368 | -0.28839 | -0.073242 | 0.23346
741.5781 | 122.8043 | -60.1639 | 62.3703 | 0.25395 | 0.0042826 | 0.0031025 | 8.1267e-05 | 0.060944 | -0.0003051 | 0.065409 | -60.2463 | 62.3245 | -60.466 | -60.3699 | 61.9263 | 3.0945 | -0.082397 | -0.11444 | 62.3383 | -60.4706 | -0.30212 | -0.045776 | -0.082398 | -0.20599 | 0.10071 | -0.44403 | -0.41199 | -0.3067 | -0.032043 | 0.21973
742.5781 | 122.8867 | -60.1547 | 62.3657 | 0.36076 | 0.0036418 | 0.0041707 | 0.0020039 | 0.059448 | -0.0007325 | 0.065623 | -60.1959 | 62.3062 | -60.466 | -60.3561 | 61.9446 | 3.1036 | -0.15564 | -0.1236 | 62.3474 | -60.4431 | -0.31128 | -0.05951 | -0.041199 | -0.20142 | 0.086975 | -0.42114 | -0.40283 | -0.28839 | -0.018311 | 0.27008
743.5781 | 122.7448 | -60.1685 | 62.4481 | -0.043596 | 0.0055644 | 0.00032554 | 0.0049947 | 0.058166 | -0.0022277 | 0.066905 | -60.2188 | 62.4527 | -60.4248 | -60.3973 | 61.9034 | 3.067 | 0.16022 | -0.1236 | 62.4161 | -60.4752 | -0.25635 | 0.004578 | -0.050354 | -0.22888 | 0.07782 | -0.54474 | -0.5127 | -0.3067 | -0.032043 | 0.20599
744.5781 | 122.8363 | -60.1364 | 62.3932 | 0.32261 | 0.005778 | -0.00010166 | 0.0013631 | 0.061157 | 0.0003357 | 0.067332 | -60.2234 | 62.3337 | -60.4523 | -60.379 | 61.9492 | 3.1265 | -0.091553 | -0.11902 | 62.352 | -60.4111 | -0.31586 | -0.059509 | -0.086975 | -0.24261 | 0.032044 | -0.44403 | -0.40283 | -0.27466 | -0.041198 | 0.22888
745.5781 | 122.8729 | -60.141 | 62.4069 | 0.31499 | 0.0044962 | 0.0056661 | -0.00077313 | 0.062012 | 0.0003357 | 0.06605 | -60.2234 | 62.3154 | -60.4477 | -60.3607 | 61.9171 | 3.1403 | -0.09613 | -0.10986 | 62.352 | -60.4477 | -0.3067 | -0.091552 | -0.082398 | -0.21973 | 0.086975 | -0.48981 | -0.43488 | -0.3067 | -0.054931 | 0.2243
746.5781 | 122.8317 | -60.1501 | 62.4069 | 0.33787 | 0.0081278 | 0.0026753 | 0.0011495 | 0.060303 | -0.0022277 | 0.067973 | -60.2142 | 62.3245 | -60.4568 | -60.3607 | 61.94 | 3.1448 | -0.09613 | -0.13275 | 62.3703 | -60.4065 | -0.3067 | -0.082397 | -0.064087 | -0.21057 | 0.045776 | -0.46692 | -0.4303 | -0.25635 | -0.036621 | 0.24262
747.5781 | 122.85 | -60.1227 | 62.4207 | 0.33787 | 0.0051372 | 0.0020345 | 0.0020039 | 0.060516 | -0.0013733 | 0.067759 | -60.2051 | 62.3428 | -60.4294 | -60.3561 | 61.94 | 3.1723 | -0.082397 | -0.11902 | 62.3566 | -60.4111 | -0.3067 | -0.07782 | -0.082397 | -0.23346 | 0.054932 | -0.48065 | -0.41656 | -0.28839 | -0.064087 | 0.2243
748.5781 | 122.8134 | -60.1273 | 62.4161 | 0.19291 | 0.007487 | 0.0028889 | -0.00098673 | 0.059662 | -0.0045777 | 0.06605 | -60.1868 | 62.3703 | -60.4248 | -60.2646 | 61.9034 | 3.1677 | -0.045776 | -0.11444 | 62.384 | -60.3973 | -0.29755 | -0.045777 | -0.05951 | -0.13733 | 0.13275 | -0.5127 | -0.48065 | -0.27008 | -0.032044 | 0.23804
749.5781 | 122.8409 | -60.141 | 62.4207 | 0.36076 | 0.0059916 | 0.0024617 | 0.0020039 | 0.060516 | -0.0018005 | 0.067546 | -60.1822 | 62.3337 | -60.4111 | -60.3378 | 61.9446 | 3.1723 | -0.086975 | -0.11902 | 62.3932 | -60.3836 | -0.27008 | -0.086975 | -0.041199 | -0.19684 | 0.045776 | -0.47607 | -0.44861 | -0.24262 | -0.027466 | 0.22888
750.5781 | 122.8546 | -60.1135 | 62.4573 | 0.17766 | 0.0051372 | 0.00032554 | 8.1267e-05 | 0.056457 | -0.0009461 | 0.067332 | -60.1639 | 62.3703 | -60.4202 | -60.3241 | 61.9263 | 3.1677 | -0.054932 | -0.12817 | 62.3978 | -60.3928 | -0.3067 | -0.086975 | -0.050354 | -0.21057 | 0.068664 | -0.53101 | -0.4715 | -0.27924 | -0.059509 | 0.25635
751.5781 | 122.7905 | -60.1227 | 62.4481 | 0.2158 | 0.0066326 | 0.0011799 | -0.0014139 | 0.058594 | -0.0003051 | 0.066264 | -60.1776 | 62.3978 | -60.4111 | -60.3378 | 61.9583 | 3.2272 | -0.086975 | -0.09613 | 62.4023 | -60.3882 | -0.28839 | -0.050354 | -0.054931 | -0.21515 | 0.050354 | -0.48981 | -0.44403 | -0.2655 | -0.045776 | 0.23346
752.5781 | 122.8638 | -60.1181 | 62.4619 | 0.13188 | 0.0079142 | 0.0020345 | -0.00077313 | 0.061798 | -0.0009461 | 0.0684 | -60.1639 | 62.4023 | -60.3928 | -60.2921 | 61.972 | 3.2227 | -0.032043 | -0.09613 | 62.4161 | -60.3836 | -0.27466 | -0.059509 | -0.045776 | -0.17395 | 0.091553 | -0.48981 | -0.44403 | -0.2655 | -0.045776 | 0.22888
753.5781 | 122.85 | -60.0906 | 62.4481 | 0.093733 | 0.0059916 | 0.0026753 | 0.0013631 | 0.059662 | 0.0011901 | 0.070536 | -60.1273 | 62.3978 | -60.3745 | -60.2509 | 62.0361 | 3.3142 | -0.064087 | -0.013733 | 62.3978 | -60.3653 | -0.28381 | -0.050354 | -0.036621 | -0.16022 | 0.11444 | -0.41199 | -0.36163 | -0.27466 | -0.050354 | 0.24719
754.5781 | 122.8455 | -60.0632 | 62.4802 | 0.2158 | 0.0066326 | 0.0033161 | 0.0020039 | 0.059235 | -0.0026551 | 0.065409 | -60.141 | 62.3932 | -60.3836 | -60.3058 | 61.9904 | 3.2776 | -0.07782 | -0.10986 | 62.4069 | -60.3516 | -0.32044 | -0.086976 | -0.07782 | -0.24262 | 0.045776 | -0.48981 | -0.41656 | -0.28839 | -0.073243 | 0.24262
755.5781 | 122.8867 | -60.0815 | 62.471 | 0.13951 | 0.005778 | 0.00096634 | 8.1267e-05 | 0.060089 | -9.1495e-05 | 0.068614 | -60.1044 | 62.4115 | -60.3607 | -60.228 | 62.0407 | 3.3279 | -0.082397 | -0.018311 | 62.4023 | -60.3516 | -0.27924 | -0.059509 | -0.022888 | -0.14648 | 0.1236 | -0.4303 | -0.36163 | -0.27008 | -0.068664 | 0.25635
756.5781 | 122.818 | -60.0769 | 62.4619 | 0.23869 | 0.0044962 | -0.0011699 | -0.0014139 | 0.058807 | -0.0039367 | 0.067332 | -60.0769 | 62.4298 | -60.3607 | -60.2737 | 62.0316 | 3.3051 | -0.07782 | -0.09613 | 62.4252 | -60.3149 | -0.28381 | -0.032043 | 0 | -0.19684 | 0.041198 | -0.4303 | -0.39368 | -0.23804 | -0.036621 | 0.28381
757.5781 | 122.9141 | -60.0266 | 62.4847 | 0.12425 | 0.0062052 | -0.0024517 | -0.0012003 | 0.060944 | -0.0009461 | 0.064555 | -60.0677 | 62.4344 | -60.3745 | -60.2325 | 62.0453 | 3.36 | -0.068665 | -0.022888 | 62.4252 | -60.3241 | -0.3479 | -0.050354 | -0.041199 | -0.20599 | 0.091553 | -0.43945 | -0.37994 | -0.29755 | -0.059509 | 0.3067
758.5781 | 122.8317 | -60.0357 | 62.5031 | 0.51335 | 0.007487 | 0.00032554 | 0.00050867 | 0.05838 | -0.0018005 | 0.066478 | -60.0311 | 62.4344 | -60.3333 | -60.1868 | 62.0911 | 3.3875 | -0.041199 | -0.018311 | 62.4344 | -60.3104 | -0.29755 | -0.068665 | 0.004578 | -0.15106 | 0.1236 | -0.41199 | -0.34332 | -0.27466 | -0.068665 | 0.30212
759.5781 | 122.8958 | -60.0266 | 62.4893 | 0.10899 | 0.0062052 | 0.0031025 | -0.00034593 | 0.060944 | -0.0007325 | 0.067759 | -60.0815 | 62.4298 | -60.3424 | -60.1868 | 62.0636 | 3.3966 | -0.073242 | -0.022888 | 62.4573 | -60.3104 | -0.31586 | -0.059509 | -0.054932 | -0.16022 | 0.1236 | -0.42572 | -0.39368 | -0.28381 | -0.032044 | 0.26093
760.5781 | 122.8226 | -60.022 | 62.5351 | 0.17003 | 0.0036418 | -0.0020243 | 0.0013631 | 0.061157 | -0.0009461 | 0.066905 | -60.0449 | 62.4435 | -60.3149 | -60.1776 | 62.0636 | 3.3966 | -0.018311 | 0.009155 | 62.4481 | -60.3058 | -0.29297 | -0.091553 | -0.022888 | -0.15564 | 0.12817 | -0.4715 | -0.38452 | -0.28381 | -0.086975 | 0.27008
761.5781 | 122.8546 | -60.0403 | 62.5168 | 0.086103 | 0.0070598 | 0.00075274 | 0.00050867 | 0.062439 | -0.0009461 | 0.067759 | -60.0403 | 62.4252 | -60.3424 | -60.1868 | 62.0956 | 3.4424 | -0.073242 | -0.009155 | 62.4756 | -60.2692 | -0.30212 | -0.091553 | 0 | -0.14648 | 0.082397 | -0.42114 | -0.37994 | -0.22888 | -0.041199 | 0.30212
762.5781 | 122.9141 | -60.0037 | 62.5168 | 0.0021796 | 0.0053508 | 0.00075274 | -0.00077313 | 0.060944 | 0.0007629 | 0.068187 | -59.9899 | 62.4527 | -60.2966 | -60.1318 | 62.114 | 3.4607 | -0.045776 | 0.036621 | 62.4893 | -60.2692 | -0.29297 | -0.064087 | 0.013733 | -0.12817 | 0.13733 | -0.40283 | -0.37537 | -0.2655 | -0.027466 | 0.3067
763.5781 | 122.9095 | -60.0174 | 62.5351 | 0.13951 | 0.0064188 | 0.0024617 | -0.00034593 | 0.061157 | 0.0001221 | 0.06605 | -60.0082 | 62.4435 | -60.3104 | -60.173 | 62.1048 | 3.447 | -0.082397 | -0.004578 | 62.4802 | -60.2737 | -0.29297 | -0.091553 | 0.009155 | -0.15564 | 0.10071 | -0.4303 | -0.37537 | -0.25635 | -0.054931 | 0.30212
764.5781 | 122.9553 | -59.9579 | 62.5992 | 0.040327 | 0.0062052 | 0.0018209 | 0.0030721 | 0.060944 | -0.0009461 | 0.066905 | -59.9762 | 62.4893 | -60.2875 | -60.1181 | 62.1231 | 3.4698 | -0.045776 | 0.041199 | 62.4893 | -60.2417 | -0.32959 | -0.10986 | -0.01831 | -0.16022 | 0.1236 | -0.47607 | -0.36621 | -0.28381 | -0.10986 | 0.31128
765.5781 | 122.8592 | -59.9854 | 62.5717 | 0.017439 | 0.004069 | -0.0015971 | 0.00029507 | 0.061798 | -0.0022277 | 0.065837 | -59.9716 | 62.471 | -60.2509 | -60.1089 | 62.1323 | 3.4973 | -0.032043 | 0.12817 | 62.5031 | -60.2417 | -0.2655 | -0.10071 | 0.013733 | -0.1236 | 0.13275 | -0.43945 | -0.37079 | -0.25635 | -0.068664 | 0.27923
766.5781 | 122.8271 | -60.022 | 62.5946 | 0.047956 | 0.0055644 | 0.0033161 | 0.0015767 | 0.060303 | -0.0013733 | 0.066905 | -59.9808 | 62.5168 | -60.2829 | -60.1227 | 62.1094 | 3.4653 | 0.041199 | 0.004578 | 62.5442 | -60.2463 | -0.26093 | -0.077819 | 0.041199 | -0.10071 | 0.1236 | -0.48523 | -0.43487 | -0.2243 | -0.050354 | 0.30212
767.5781 | 122.8958 | -59.9899 | 62.5442 | -0.028338 | 0.0027874 | -0.0013835 | 0.0043539 | 0.061798 | -0.0024415 | 0.070536 | -59.9487 | 62.4985 | -60.2463 | -59.935 | 62.3703 | 3.6758 | -0.31586 | -0.073242 | 62.5214 | -60.2325 | -0.25635 | -0.045776 | 0.041199 | 0.054931 | 0.29755 | -0.17395 | -0.15106 | -0.24262 | -0.022888 | 0.29755
768.5781 | 122.8958 | -59.9762 | 62.5809 | -0.0054494 | 0.0044962 | 0.00011194 | -0.0014139 | 0.05838 | -0.0003051 | 0.068614 | -59.9442 | 62.5122 | -60.2463 | -60.3012 | 62.0956 | 3.5706 | -0.073242 | -0.054932 | 62.5397 | -60.2097 | -0.27008 | -0.068665 | 0.032043 | -0.32501 | -0.091552 | -0.48523 | -0.44403 | -0.23346 | -0.041199 | 0.30212
769.5781 | 122.8088 | -59.967 | 62.59 | -0.058855 | 0.0059916 | 0.0056661 | 0.00072227 | 0.061798 | -0.0041503 | 0.068187 | -59.9579 | 62.5809 | -60.2509 | -60.1273 | 62.1048 | 3.4836 | 0.068665 | -0.022888 | 62.5671 | -60.2417 | -0.28381 | -0.009155 | 0.009155 | -0.16022 | 0.11444 | -0.48523 | -0.46234 | -0.27466 | -0.022888 | 0.29297
770.5781 | 122.9004 | -59.9533 | 62.5946 | -0.066485 | 0.0068462 | 0.0060933 | 0.0060629 | 0.062439 | -0.0022277 | 0.068187 | -59.9899 | 62.5397 | -60.2325 | -60.0494 | 62.1231 | 3.4515 | -0.045776 | 0.036621 | 62.5351 | -60.2005 | -0.27924 | -0.054931 | -0.036621 | -0.09613 | 0.15106 | -0.4715 | -0.41199 | -0.24719 | -0.059509 | 0.24262
771.5781 | 122.8683 | -59.9533 | 62.6038 | 0.0021796 | 0.005778 | 0.00032554 | 0.0026449 | 0.059875 | -0.0015869 | 0.066264 | -59.7702 | 62.6038 | -60.1868 | -60.1318 | 62.114 | 3.5477 | -0.059509 | 0.018311 | 62.5488 | -60.1913 | -0.23346 | 0 | 0.1831 | -0.17853 | 0.059509 | -0.48981 | -0.43487 | -0.23804 | -0.054932 | 0.41656
772.5781 | 122.8226 | -59.935 | 62.645 | -0.066485 | 0.0049236 | 0.0018209 | 0.0022177 | 0.061371 | -0.0024415 | 0.065837 | -59.9213 | 62.59 | -60.2142 | -60.1044 | 62.1368 | 3.5156 | 0.082397 | -0.004578 | 62.59 | -60.1959 | -0.27923 | -0.054931 | 0.013733 | -0.16937 | 0.091553 | -0.50812 | -0.45319 | -0.26093 | -0.054931 | 0.29297
773.5781 | 122.85 | -59.9396 | 62.6587 | -0.051226 | 0.0070598 | 0.00096634 | 0.0034993 | 0.060944 | -0.0020141 | 0.066264 | -59.9075 | 62.5763 | -60.2234 | -60.1044 | 62.1414 | 3.5156 | 0.059509 | -0.009155 | 62.6175 | -60.1868 | -0.28381 | -0.082397 | 0.032043 | -0.1648 | 0.082398 | -0.51727 | -0.47608 | -0.24719 | -0.041198 | 0.31586
774.5781 | 122.7402 | -59.9258 | 62.6633 | -0.18855 | 0.0072734 | 0.00096634 | 0.0075581 | 0.062652 | -0.0015869 | 0.067546 | -59.9304 | 62.6587 | -60.228 | -60.141 | 62.1002 | 3.4515 | 0.14648 | -0.10986 | 62.6358 | -60.2325 | -0.30212 | -0.004578 | -0.004578 | -0.21515 | 0.091553 | -0.56305 | -0.53558 | -0.3067 | -0.027466 | 0.29755
775.5781 | 122.8226 | -59.9258 | 62.6587 | -0.066485 | 0.0044962 | 0.0071615 | 0.0017903 | 0.063507 | -0.0054321 | 0.067546 | -59.8892 | 62.6038 | -60.1868 | -60.0815 | 62.1552 | 3.5385 | 0.068665 | -0.004578 | 62.6358 | -60.1868 | -0.26093 | -0.054931 | 0.036621 | -0.15564 | 0.10529 | -0.50354 | -0.48065 | -0.26093 | -0.022888 | 0.29755
776.5781 | 122.7264 | -59.9487 | 62.6907 | 0.0098091 | 0.0066326 | 0.00096634 | 0.0039267 | 0.060516 | -0.0041503 | 0.066478 | -59.9716 | 62.6587 | -60.2005 | -60.1547 | 62.1094 | 3.4653 | 0.16937 | -0.064087 | 62.6633 | -60.1776 | -0.25177 | -0.032044 | -0.022889 | -0.20599 | 0.022888 | -0.58136 | -0.55389 | -0.22888 | -0.027466 | 0.22888
777.5781 | 122.7768 | -59.9167 | 62.6907 | 0.0021796 | 0.0079142 | 0.0024617 | 0.0028585 | 0.060516 | -0.0039367 | 0.067332 | -59.8618 | 62.6266 | -60.1639 | -60.054 | 62.178 | 3.566 | 0.050354 | 0 | 62.6587 | -60.141 | -0.24719 | -0.064087 | 0.054932 | -0.13733 | 0.086975 | -0.51269 | -0.48065 | -0.2243 | -0.032044 | 0.30212
778.5781 | 122.7814 | -59.9075 | 62.7228 | -0.18855 | 0.0036418 | -0.00052906 | 0.0032857 | 0.061157 | -0.0018005 | 0.068614 | -59.9167 | 62.6816 | -60.1913 | -60.1273 | 62.1048 | 3.5019 | 0.13733 | -0.091553 | 62.677 | -60.1593 | -0.28381 | -0.041198 | -0.009155 | -0.21973 | 0.032044 | -0.61798 | -0.57221 | -0.25177 | -0.045776 | 0.27466
779.5781 | 122.7585 | -59.8938 | 62.7274 | -0.043596 | 0.005778 | 0.0067341 | 0.0037129 | 0.062439 | -0.0032959 | 0.066905 | -59.8938 | 62.6678 | -60.1776 | -60.1135 | 62.1323 | 3.5019 | 0.14191 | -0.068665 | 62.6953 | -60.1456 | -0.28381 | -0.059509 | 0 | -0.21973 | 0.032044 | -0.59509 | -0.56305 | -0.25177 | -0.032044 | 0.28381
780.5781 | 122.7722 | -59.8984 | 62.7365 | -0.081743 | 0.0094096 | 0.0041707 | 0.0047811 | 0.06073 | -0.0013733 | 0.068614 | -59.8801 | 62.6953 | -60.1822 | -60.1044 | 62.1414 | 3.5065 | 0.13275 | -0.082397 | 62.7136 | -60.1639 | -0.28381 | -0.041199 | 0.01831 | -0.20599 | 0.059509 | -0.59509 | -0.5722 | -0.2655 | -0.022888 | 0.30212
781.5781 | 122.7768 | -59.8938 | 62.764 | -0.028338 | 0.007487 | -0.00031526 | 0.0060629 | 0.062225 | -0.0045777 | 0.069682 | -59.7336 | 62.7777 | -60.1318 | -60.1273 | 62.1323 | 3.5202 | 0.11444 | -0.073242 | 62.7182 | -60.1547 | -0.23804 | 0.013733 | 0.16022 | -0.23346 | 0.027466 | -0.63171 | -0.58594 | -0.26093 | -0.045776 | 0.39825
782.5781 | 122.7676 | -59.8755 | 62.7594 | -0.043596 | 0.005778 | 0.0037435 | 0.0052083 | 0.062866 | -0.0020141 | 0.067759 | -59.7061 | 62.7914 | -60.1364 | -60.1318 | 62.1277 | 3.5431 | 0.11902 | -0.082397 | 62.7365 | -60.1501 | -0.26093 | 0.032044 | 0.16937 | -0.25635 | 0.01831 | -0.63171 | -0.60883 | -0.27466 | -0.022888 | 0.4303
783.5781 | 122.7676 | -59.8709 | 62.7548 | -0.14278 | 0.0077006 | 0.0056661 | 0.0039267 | 0.063507 | -0.0015869 | 0.069896 | -59.8663 | 62.7502 | -60.1135 | -60.0815 | 62.1506 | 3.566 | 0.15564 | -0.059509 | 62.7686 | -60.141 | -0.24261 | -0.004578 | 0.004578 | -0.21057 | 0.059509 | -0.60425 | -0.61798 | -0.27008 | 0.013733 | 0.24719
784.5781 | 122.7859 | -59.8389 | 62.7686 | -0.12752 | 0.0066326 | 0.0016073 | 0.0026449 | 0.062439 | -0.0005189 | 0.068187 | -59.8709 | 62.7548 | -60.1364 | -60.0815 | 62.1597 | 3.5706 | 0.13733 | -0.059509 | 62.7411 | -60.1135 | -0.29755 | -0.013733 | -0.032044 | -0.24262 | 0.032043 | -0.60883 | -0.58136 | -0.27466 | -0.027466 | 0.2655
785.5781 | 122.7539 | -59.8663 | 62.7914 | 0.20817 | 0.0087688 | 0.0052387 | 0.0060629 | 0.064575 | -0.0013733 | 0.067973 | -59.9899 | 62.7319 | -60.1135 | -60.0769 | 62.1323 | 3.5797 | 0.16937 | -0.091553 | 62.7823 | -60.1181 | -0.24719 | -0.059509 | -0.1236 | -0.21057 | 0.041199 | -0.65918 | -0.65002 | -0.25177 | -0.009155 | 0.1236
786.5781 | 122.7905 | -59.8343 | 62.7686 | 1.6044 | 0.0096232 | 0.00075274 | 0.0054219 | 0.065002 | -0.0037231 | 0.066691 | -59.8663 | 62.7777 | -60.1181 | -60.0586 | 62.1643 | 3.598 | 0.15106 | -0.07782 | 62.7777 | -60.0998 | -0.28381 | 0.009155 | -0.032043 | -0.2243 | 0.041198 | -0.60425 | -0.6134 | -0.2655 | 0.009155 | 0.25177
787.5781 | 122.7402 | -59.8343 | 62.7869 | 1.6272 | 0.0072734 | 0.0054525 | 0.0043539 | 0.064575 | -0.0011597 | 0.066264 | -59.8709 | 62.7914 | -60.1318 | -60.0632 | 62.1689 | 3.6072 | 0.15106 | -0.07782 | 62.8143 | -60.1181 | -0.29755 | 0.004578 | -0.036621 | -0.22888 | 0.054932 | -0.61798 | -0.64545 | -0.28381 | 0.027466 | 0.26093
788.5781 | 122.7676 | -59.8343 | 62.8143 | 0.52098 | 0.010478 | 0.0039571 | 0.0054219 | 0.062012 | -0.0009461 | 0.067546 | -59.9487 | 62.7777 | -60.1181 | -60.0494 | 62.1689 | 3.6118 | 0.15564 | -0.073242 | 62.8052 | -60.0815 | -0.28381 | -0.036621 | -0.11444 | -0.21515 | 0.032044 | -0.64545 | -0.63629 | -0.24719 | -0.009155 | 0.16937
789.5781 | 122.8043 | -59.8022 | 62.8006 | -0.013079 | 0.0077006 | 0.0048115 | 0.0079855 | 0.066498 | -0.0030823 | 0.067332 | -59.7656 | 62.8235 | -60.0952 | -59.9991 | 62.2147 | 3.653 | 0.10071 | -0.054932 | 62.8235 | -60.0723 | -0.29297 | 0.022888 | 0.036621 | -0.19684 | 0.073243 | -0.58594 | -0.60883 | -0.27008 | 0.022888 | 0.32959
790.5781 | 122.7905 | -59.8022 | 62.8006 | 0.10136 | 0.010264 | 0.0058797 | 0.0081991 | 0.066284 | -0.0050049 | 0.069682 | -59.7336 | 62.8235 | -60.0586 | -60.0128 | 62.2009 | 3.6575 | 0.022888 | -0.068665 | 62.8189 | -60.0586 | -0.25635 | 0.022888 | 0.068664 | -0.21057 | 0.045777 | -0.59967 | -0.61798 | -0.25635 | 0.018311 | 0.32501
791.5781 | 122.7859 | -59.7977 | 62.8326 | -0.60817 | 0.0087688 | 0.0071615 | 0.0034993 | 0.065216 | -0.0024415 | 0.068614 | -59.9442 | 62.8601 | -60.0632 | -60.0449 | 62.178 | 3.6392 | 0.16479 | -0.050354 | 62.851 | -60.0815 | -0.2655 | 0.027465 | -0.14648 | -0.24719 | 0.036621 | -0.6546 | -0.67291 | -0.28381 | 0.01831 | 0.11902
792.5781 | 122.7951 | -59.7885 | 62.8281 | 0.032698 | 0.0064188 | 0.0052387 | 0.0049947 | 0.063934 | -0.0015869 | 0.067118 | -59.7427 | 62.8693 | -60.0586 | -59.9716 | 62.2375 | 3.685 | 0.10529 | -0.018311 | 62.8372 | -60.0815 | -0.27008 | 0.041199 | 0.045776 | -0.18311 | 0.10986 | -0.59051 | -0.59967 | -0.29297 | 0.009155 | 0.31586
793.5781 | 122.818 | -59.7656 | 62.8464 | 0.0021796 | 0.0072734 | 0.0033161 | 0.0054219 | 0.066498 | -0.0020141 | 0.069255 | -59.7382 | 62.8647 | -60.0357 | -59.967 | 62.2421 | 3.685 | 0.1236 | -0.032043 | 62.8693 | -60.0632 | -0.27008 | 0.01831 | 0.027466 | -0.20142 | 0.09613 | -0.60425 | -0.62714 | -0.29755 | 0.022888 | 0.29755
794.5781 | 122.7905 | -59.7565 | 62.8326 | -0.37166 | 0.010905 | 0.0058797 | 0.0064901 | 0.065857 | -0.0035095 | 0.069468 | -59.7061 | 62.883 | -60.0494 | -59.9533 | 62.2375 | 3.7079 | 0.041199 | -0.050354 | 62.8464 | -60.0174 | -0.29297 | 0.050354 | 0.050354 | -0.19684 | 0.064087 | -0.59509 | -0.60883 | -0.26093 | 0.013733 | 0.34332
795.5781 | 122.7539 | -59.729 | 62.8647 | 0.0098091 | 0.0087688 | 0.0024617 | 0.0032857 | 0.064148 | -0.0011597 | 0.069468 | -59.7153 | 62.9013 | -60.0357 | -59.9487 | 62.2467 | 3.7125 | 0.12817 | -0.045776 | 62.8922 | -60.0128 | -0.3067 | 0.036621 | 0.013733 | -0.21973 | 0.064087 | -0.61798 | -0.64545 | -0.28381 | 0.027466 | 0.32043
796.5781 | 122.8455 | -59.7336 | 62.8647 | -0.051226 | 0.010478 | 0.0031025 | 0.0039267 | 0.06607 | -0.0026551 | 0.068187 | -59.6558 | 62.9288 | -60.0082 | -59.9167 | 62.2696 | 3.7354 | 0.064087 | -0.027466 | 62.8693 | -60.0174 | -0.27466 | 0.064087 | 0.07782 | -0.18311 | 0.10071 | -0.59509 | -0.59967 | -0.28381 | 0.004578 | 0.35248
797.5781 | 122.8043 | -59.7244 | 62.8922 | 0.017439 | 0.007487 | 0.0063069 | 0.0015767 | 0.064789 | -0.0013733 | 0.068614 | -59.7015 | 62.915 | -60.0037 | -59.9396 | 62.2559 | 3.717 | 0.13275 | -0.064087 | 62.9288 | -60.022 | -0.27924 | 0.022888 | 0.022888 | -0.21515 | 0.082398 | -0.63629 | -0.67291 | -0.29755 | 0.036621 | 0.30212
798.5781 | 122.7493 | -59.7107 | 62.9059 | 0.025068 | 0.0085552 | 0.0075887 | 0.0039267 | 0.065002 | 0.0001221 | 0.067546 | -59.6786 | 62.9379 | -59.9899 | -59.9487 | 62.2559 | 3.717 | 0.14191 | -0.054932 | 62.9425 | -59.9991 | -0.27924 | 0.032043 | 0.032043 | -0.23804 | 0.050354 | -0.65002 | -0.68665 | -0.28839 | 0.036621 | 0.31128
799.5781 | 122.7859 | -59.7061 | 62.9013 | 0.17003 | 0.0077006 | 0.0073751 | 0.0043539 | 0.065643 | -0.0011597 | 0.067759 | -59.6237 | 62.9242 | -59.9899 | -59.8938 | 62.265 | 3.7628 | 0.032043 | -0.036621 | 62.9196 | -59.9945 | -0.28381 | 0.022888 | 0.082398 | -0.18768 | 0.10071 | -0.63629 | -0.6546 | -0.28839 | 0.018311 | 0.36621
800.5781 | 122.7905 | -59.7061 | 62.9013 | -0.043596 | 0.0068462 | 0.0048115 | 0.0054219 | 0.067566 | -0.0024415 | 0.068614 | -59.6283 | 62.9425 | -59.9625 | -59.8846 | 62.3108 | 3.7674 | 0.091553 | -0.009155 | 62.9425 | -59.9579 | -0.25635 | 0.041199 | 0.07782 | -0.17853 | 0.073242 | -0.59051 | -0.63171 | -0.25177 | 0.041199 | 0.33417
801.5781 | 122.7951 | -59.6741 | 62.9242 | -0.020708 | 0.0070598 | 0.0048115 | 0.0047811 | 0.064361 | -0.0043641 | 0.069041 | -59.6146 | 62.9791 | -59.9762 | -59.8663 | 62.3016 | 3.7674 | 0.086975 | -0.022888 | 62.9562 | -59.9716 | -0.30212 | 0.054932 | 0.059509 | -0.19226 | 0.10529 | -0.62256 | -0.6546 | -0.29755 | 0.032044 | 0.36163
802.5781 | 122.8455 | -59.6741 | 62.9425 | 0.032698 | 0.0066326 | 0.0048115 | 0.0041403 | 0.067139 | -0.0022277 | 0.065837 | -59.6466 | 62.9654 | -59.967 | -59.8709 | 62.2971 | 3.772 | 0.11902 | -0.018311 | 62.9517 | -59.9716 | -0.29297 | 0.022888 | 0.027466 | -0.19684 | 0.10071 | -0.64545 | -0.6546 | -0.29755 | 0.009155 | 0.32044
803.5781 | 122.7951 | -59.6695 | 62.9242 | 0.063215 | 0.0083416 | 0.0060933 | 0.0073445 | 0.065643 | -0.0013733 | 0.069468 | -59.5688 | 62.9745 | -59.9258 | -59.8434 | 62.3199 | 3.7994 | 0.059509 | -0.018311 | 62.9929 | -59.9625 | -0.25635 | 0.050354 | 0.10071 | -0.17395 | 0.11902 | -0.60425 | -0.67291 | -0.29297 | 0.068665 | 0.35706
804.5781 | 122.8134 | -59.6466 | 62.9379 | 0.13951 | 0.0094096 | 0.0035299 | 0.0073445 | 0.065857 | -0.0032959 | 0.067973 | -59.5825 | 63.0066 | -59.9533 | -59.8526 | 62.3062 | 3.7903 | 0.059509 | -0.022888 | 62.9745 | -59.9396 | -0.3067 | 0.068665 | 0.064086 | -0.20599 | 0.086975 | -0.63171 | -0.66833 | -0.29297 | 0.036621 | 0.37079
805.5781 | 122.7814 | -59.6466 | 62.9654 | -0.028338 | 0.0087688 | 0.0024617 | 0.0041403 | 0.06308 | 0.0001221 | 0.066905 | -59.6237 | 63.0249 | -59.935 | -59.8755 | 62.3062 | 3.7811 | 0.13275 | -0.041199 | 63.0157 | -59.9487 | -0.28839 | 0.059509 | 0.022888 | -0.22888 | 0.073242 | -0.65918 | -0.70953 | -0.30212 | 0.050354 | 0.31128
806.5781 | 122.7997 | -59.642 | 62.97 | -0.020708 | 0.0064188 | 0.0048115 | 0.0052083 | 0.066925 | -0.0005189 | 0.067546 | -59.5596 | 63.0386 | -59.8846 | -59.8251 | 62.3566 | 3.8132 | 0.10529 | -0.009155 | 62.9883 | -59.9167 | -0.24262 | 0.068664 | 0.082398 | -0.1831 | 0.091553 | -0.6134 | -0.63171 | -0.27466 | 0.01831 | 0.32501
807.5781 | 122.7768 | -59.6329 | 62.9608 | 0.12425 | 0.0081278 | 0.0045979 | 0.0045675 | 0.067993 | -0.0028687 | 0.067546 | -59.5459 | 63.0341 | -59.9167 | -59.8297 | 62.3291 | 3.7857 | 0.032043 | -0.091553 | 63.0203 | -59.903 | -0.28381 | 0.073243 | 0.086976 | -0.19684 | 0.073242 | -0.63171 | -0.69122 | -0.27008 | 0.05951 | 0.37079
808.5781 | 122.7676 | -59.6008 | 62.9929 | 0.10136 | 0.0096232 | 0.0031025 | 0.0049947 | 0.066925 | -0.0018005 | 0.067973 | -59.5139 | 63.0295 | -59.8984 | -59.816 | 62.3474 | 3.8315 | 0.036621 | -0.036621 | 63.0203 | -59.9213 | -0.29755 | 0.036621 | 0.086975 | -0.21515 | 0.10529 | -0.64545 | -0.67291 | -0.32043 | 0.027466 | 0.38452
809.5781 | 122.818 | -59.6146 | 62.9883 | 0.1624 | 0.0077006 | 0.0052387 | 0.0054219 | 0.068207 | -0.0020141 | 0.067973 | -59.5276 | 63.0478 | -59.8572 | -59.7931 | 62.3383 | 3.8086 | 0.027466 | -0.041199 | 63.0341 | -59.8984 | -0.24262 | 0.05951 | 0.086975 | -0.17853 | 0.10529 | -0.65002 | -0.6958 | -0.28381 | 0.045777 | 0.32959
810.5781 | 122.8088 | -59.5642 | 63.0066 | 0.10899 | 0.007487 | 0.0071615 | 0.0043539 | 0.065216 | -0.0005189 | 0.067759 | -59.5047 | 63.0569 | -59.8434 | -59.7931 | 62.3749 | 3.8269 | 0.045776 | -0.027466 | 63.0478 | -59.8984 | -0.27924 | 0.050354 | 0.059509 | -0.22888 | 0.10529 | -0.63171 | -0.67291 | -0.33417 | 0.041199 | 0.33875
811.5781 | 122.7768 | -59.5779 | 63.0249 | 0.10136 | 0.0087688 | 0.0090841 | 0.0047811 | 0.065643 | -0.0007325 | 0.069468 | -59.4864 | 63.0753 | -59.8434 | -59.761 | 62.3749 | 3.8361 | 0.054932 | -0.013733 | 63.0478 | -59.8801 | -0.2655 | 0.050354 | 0.091553 | -0.1831 | 0.11902 | -0.65002 | -0.67291 | -0.30212 | 0.022889 | 0.35706
812.5781 | 122.818 | -59.5642 | 63.0615 | -0.0054494 | 0.0089824 | 0.0039571 | 0.0047811 | 0.064361 | -0.0015869 | 0.067118 | -59.5093 | 63.0936 | -59.8206 | -59.7839 | 62.3703 | 3.8223 | 0.13733 | -0.027466 | 63.0936 | -59.8526 | -0.25635 | 0.032044 | 0.054932 | -0.21973 | 0.068664 | -0.69122 | -0.72327 | -0.28839 | 0.032044 | 0.31128
813.5781 | 122.7859 | -59.5734 | 63.0295 | 0.0098091 | 0.0096232 | 0.0048115 | 0.0062765 | 0.067352 | -0.0015869 | 0.069896 | -59.4635 | 63.0798 | -59.8114 | -59.729 | 62.4069 | 3.8589 | 0.059509 | -0.018311 | 63.0661 | -59.8801 | -0.23804 | 0.050354 | 0.10986 | -0.15564 | 0.15106 | -0.62256 | -0.65918 | -0.3067 | 0.036621 | 0.3479
814.5781 | 122.7905 | -59.5596 | 63.0661 | 0.23106 | 0.0072734 | 0.0052387 | 0.0069173 | 0.065216 | -0.0003051 | 0.066478 | -59.4818 | 63.0936 | -59.8251 | -59.7794 | 62.352 | 3.7949 | 0.018311 | -0.091553 | 63.0844 | -59.8663 | -0.2655 | 0.027466 | 0.077819 | -0.21973 | 0.086975 | -0.71411 | -0.73242 | -0.3067 | 0.018311 | 0.34332
815.5781 | 122.7951 | -59.5505 | 63.0707 | 0.19291 | 0.0079142 | 0.0033161 | 0.0079855 | 0.066925 | -0.0026551 | 0.070109 | -59.4635 | 63.1302 | -59.8297 | -59.7748 | 62.3611 | 3.804 | 0.018311 | -0.068665 | 63.089 | -59.8572 | -0.27924 | 0.059509 | 0.086975 | -0.2243 | 0.082398 | -0.70953 | -0.72784 | -0.3067 | 0.01831 | 0.36621
816.5781 | 122.818 | -59.5276 | 63.0707 | 0.025068 | 0.0072734 | 0.0052387 | 0.0049947 | 0.066925 | -0.0013733 | 0.069041 | -59.4452 | 63.1439 | -59.7977 | -59.7107 | 62.439 | 3.8864 | 0.086975 | -0.013733 | 63.1348 | -59.8114 | -0.27008 | 0.073242 | 0.082398 | -0.1831 | 0.10071 | -0.63171 | -0.6958 | -0.28381 | 0.064087 | 0.35248
817.5781 | 122.7951 | -59.5093 | 63.0936 | 0.12425 | 0.0083416 | 0.0035299 | 0.0062765 | 0.064361 | -0.0011597 | 0.067759 | -59.4177 | 63.121 | -59.8022 | -59.7061 | 62.4069 | 3.8635 | 0.009155 | -0.032043 | 63.1393 | -59.7977 | -0.29297 | 0.027466 | 0.091552 | -0.19684 | 0.091552 | -0.68665 | -0.73242 | -0.28839 | 0.045776 | 0.38452
818.5781 | 122.8455 | -59.4955 | 63.1027 | 0.025068 | 0.0081278 | 0.0037435 | 0.0032857 | 0.065216 | -0.0015869 | 0.069682 | -59.4223 | 63.176 | -59.7748 | -59.6741 | 62.4435 | 3.891 | 0.07782 | -0.004578 | 63.1439 | -59.8206 | -0.27924 | 0.073242 | 0.073242 | -0.17853 | 0.14648 | -0.65918 | -0.70038 | -0.32501 | 0.041199 | 0.35248
819.5781 | 122.7768 | -59.4681 | 63.1165 | -0.013079 | 0.0089824 | 0.0052387 | 0.0045675 | 0.065857 | -0.0011597 | 0.070536 | -59.404 | 63.1851 | -59.761 | -59.6695 | 62.4527 | 3.8773 | 0.091553 | -0.027466 | 63.1668 | -59.7885 | -0.29297 | 0.068665 | 0.064087 | -0.20142 | 0.11902 | -0.66376 | -0.71411 | -0.32043 | 0.050354 | 0.35705
820.5781 | 122.8226 | -59.4772 | 63.1348 | 0.13951 | 0.010264 | 0.0048115 | 0.0062765 | 0.067139 | -0.0020141 | 0.069682 | -59.3903 | 63.1439 | -59.7519 | -59.6878 | 62.4344 | 3.8681 | 0.027466 | -0.036621 | 63.1714 | -59.8022 | -0.27466 | 0.009155 | 0.086975 | -0.21057 | 0.11444 | -0.70038 | -0.737 | -0.32501 | 0.036621 | 0.36163
821.5781 | 122.7997 | -59.4589 | 63.121 | 0.10899 | 0.010691 | 0.0035299 | 0.0056355 | 0.065216 | -0.0024415 | 0.067546 | -59.3674 | 63.1897 | -59.7382 | -59.6558 | 62.4573 | 3.8773 | 0.027466 | -0.036621 | 63.1577 | -59.7885 | -0.27924 | 0.068664 | 0.091552 | -0.19684 | 0.13275 | -0.66376 | -0.70038 | -0.32959 | 0.036621 | 0.37079
822.5781 | 122.8134 | -59.4452 | 63.1485 | 0.070845 | 0.0087688 | 0.0095113 | 0.0056355 | 0.065002 | -0.0041503 | 0.070323 | -59.3491 | 63.1943 | -59.7015 | -59.6558 | 62.4619 | 3.8727 | 0.050354 | -0.032043 | 63.208 | -59.761 | -0.25635 | 0.045776 | 0.09613 | -0.21057 | 0.10528 | -0.68665 | -0.74616 | -0.31586 | 0.059509 | 0.35248
823.5781 | 122.7814 | -59.4452 | 63.1622 | 0.19291 | 0.0083416 | 0.0060933 | 0.0060629 | 0.065857 | -0.0037231 | 0.067118 | -59.317 | 63.2217 | -59.6832 | -59.6512 | 62.4664 | 3.8635 | 0.027466 | -0.050354 | 63.1989 | -59.7519 | -0.23804 | 0.05951 | 0.12817 | -0.20599 | 0.10071 | -0.6958 | -0.73242 | -0.3067 | 0.036622 | 0.36621
824.5781 | 122.7631 | -59.4635 | 63.176 | 0.3455 | 0.0096232 | 0.0033161 | 0.0054219 | 0.067352 | -0.0011597 | 0.068827 | -59.4223 | 63.208 | -59.7473 | -59.7107 | 62.3886 | 3.8086 | -0.004578 | -0.16479 | 63.2172 | -59.7839 | -0.28381 | 0.032044 | 0.041199 | -0.24719 | 0.073243 | -0.78735 | -0.82855 | -0.32043 | 0.041199 | 0.32501
825.5781 | 122.7585 | -59.3948 | 63.1714 | 0.017439 | 0.0085552 | 0.0071615 | 0.0039267 | 0.064361 | -9.1495e-05 | 0.067546 | -59.3536 | 63.2492 | -59.6878 | -59.6054 | 62.4847 | 3.891 | 0.11902 | -0.050354 | 63.2172 | -59.7198 | -0.29297 | 0.07782 | 0.041198 | -0.21057 | 0.11444 | -0.68665 | -0.73242 | -0.32501 | 0.045776 | 0.33417
826.5781 | 122.7951 | -59.3994 | 63.2034 | 0.040327 | 0.0059916 | 0.0060933 | 0.0047811 | 0.06543 | -0.0013733 | 0.065837 | -59.285 | 63.2675 | -59.6832 | -59.5917 | 62.5031 | 3.891 | 0.022888 | -0.064087 | 63.2492 | -59.7198 | -0.28381 | 0.064087 | 0.11444 | -0.19226 | 0.12817 | -0.70038 | -0.74616 | -0.32044 | 0.045777 | 0.39825
827.5781 | 122.7859 | -59.3903 | 63.2309 | 0.33024 | 0.0085552 | 0.0075887 | 0.0081991 | 0.067779 | -0.0030823 | 0.067973 | -59.2941 | 63.2904 | -59.6695 | -59.5963 | 62.5122 | 3.8956 | 0.022888 | -0.054932 | 63.2629 | -59.6878 | -0.27924 | 0.059509 | 0.096131 | -0.20599 | 0.091553 | -0.71869 | -0.75073 | -0.29755 | 0.032043 | 0.37537
828.5781 | 122.8043 | -59.3811 | 63.2217 | -0.1733 | 0.0098368 | 0.0082295 | 0.0049947 | 0.067566 | -0.0037231 | 0.067973 | -59.3079 | 63.2812 | -59.6741 | -59.5596 | 62.5122 | 3.9139 | 0.018311 | -0.068665 | 63.2721 | -59.6924 | -0.29297 | 0.059509 | 0.073243 | -0.17853 | 0.13275 | -0.70953 | -0.75989 | -0.31128 | 0.050354 | 0.36621
829.5781 | 122.7676 | -59.3628 | 63.2309 | 0.27684 | 0.0096232 | 0.0078023 | 0.0058493 | 0.066925 | -0.0026551 | 0.067973 | -59.2621 | 63.2812 | -59.61 | -59.5688 | 62.5397 | 3.9093 | 0.027466 | -0.054932 | 63.2629 | -59.6924 | -0.24719 | 0.050354 | 0.10071 | -0.20599 | 0.1236 | -0.69122 | -0.72327 | -0.32959 | 0.032043 | 0.3479
830.5781 | 122.8088 | -59.317 | 63.2492 | -0.020708 | 0.0087688 | 0.0056661 | 0.0067037 | 0.066711 | -0.0020141 | 0.067759 | -59.2346 | 63.295 | -59.642 | -59.5688 | 62.5397 | 3.9047 | 0.041199 | -0.082397 | 63.295 | -59.6649 | -0.32501 | 0.045776 | 0.082398 | -0.25177 | 0.09613 | -0.70953 | -0.75531 | -0.3479 | 0.045776 | 0.40741
831.5781 | 122.7768 | -59.3491 | 63.2812 | 0.26158 | 0.011973 | 0.0092977 | 0.0081991 | 0.067993 | -0.0026551 | 0.067546 | -59.2575 | 63.3133 | -59.5963 | -59.5825 | 62.5076 | 3.8315 | 0.050354 | -0.13275 | 63.3041 | -59.6695 | -0.24719 | 0.032043 | 0.091553 | -0.23346 | 0.086975 | -0.77362 | -0.79651 | -0.32043 | 0.022888 | 0.33875
832.5781 | 122.8088 | -59.3262 | 63.2675 | 0.093733 | 0.010691 | 0.0067341 | 0.0062765 | 0.066925 | -0.0020141 | 0.068187 | -59.23 | 63.3408 | -59.5779 | -59.523 | 62.5488 | 3.9185 | 0.041199 | -0.064087 | 63.3133 | -59.642 | -0.25177 | 0.073242 | 0.09613 | -0.19684 | 0.11902 | -0.71869 | -0.76447 | -0.31586 | 0.045776 | 0.3479
833.5781 | 122.7676 | -59.317 | 63.3133 | 0.23869 | 0.0098368 | 0.0067341 | 0.0054219 | 0.066925 | -0.0015869 | 0.067973 | -59.2392 | 63.3636 | -59.5825 | -59.5688 | 62.5397 | 3.8544 | 0.036621 | -0.11444 | 63.327 | -59.6512 | -0.2655 | 0.050354 | 0.07782 | -0.25177 | 0.082397 | -0.77362 | -0.78735 | -0.33417 | 0.013733 | 0.34332
834.5781 | 122.7402 | -59.3079 | 63.327 | 0.26158 | 0.0070598 | 0.0043843 | 0.0064901 | 0.066284 | -0.0024415 | 0.069041 | -59.2255 | 63.3911 | -59.5551 | -59.5505 | 62.5305 | 3.8544 | 0.036621 | -0.1236 | 63.3774 | -59.6146 | -0.24719 | 0.064087 | 0.082397 | -0.24262 | 0.064087 | -0.79651 | -0.84686 | -0.3067 | 0.050354 | 0.32959
835.5781 | 122.7356 | -59.2804 | 63.3224 | 0.33024 | 0.0079142 | 0.0078023 | 0.0067037 | 0.064575 | -0.0018005 | 0.0684 | -59.2117 | 63.3957 | -59.5551 | -59.5322 | 62.5351 | 3.8406 | 0.036621 | -0.13733 | 63.3453 | -59.61 | -0.27466 | 0.073242 | 0.068665 | -0.25177 | 0.077819 | -0.78735 | -0.81024 | -0.32959 | 0.022888 | 0.34332
836.5781 | 122.7539 | -59.2667 | 63.3453 | 0.26158 | 0.0096232 | 0.0060933 | 0.0058493 | 0.066711 | -0.0020141 | 0.068187 | -59.2072 | 63.3957 | -59.5551 | -59.5276 | 62.5442 | 3.8452 | 0.045776 | -0.14191 | 63.3774 | -59.6054 | -0.28839 | 0.050354 | 0.05951 | -0.26093 | 0.07782 | -0.80109 | -0.83313 | -0.33874 | 0.032043 | 0.3479
837.5781 | 122.6898 | -59.2667 | 63.3316 | 0.23869 | 0.0098368 | 0.0065205 | 0.0052083 | 0.067139 | -0.0015869 | 0.069255 | -59.2072 | 63.414 | -59.5322 | -59.5139 | 62.5259 | 3.8544 | 0.050354 | -0.12817 | 63.382 | -59.61 | -0.2655 | 0.082397 | 0.05951 | -0.24719 | 0.09613 | -0.80566 | -0.85602 | -0.34332 | 0.050354 | 0.32501
838.5781 | 122.9004 | -59.23 | 63.2996 | 0.3455 | 0.007487 | 0.0054525 | 0.0015767 | 0.066711 | -0.0022277 | 0.0684 | -59.111 | 63.3545 | -59.5001 | -59.4223 | 62.645 | 3.9871 | -0.1831 | -0.018311 | 63.327 | -59.5367 | -0.27008 | 0.054931 | 0.11902 | -0.19226 | 0.11444 | -0.6546 | -0.68207 | -0.3067 | 0.027465 | 0.3891
839.5781 | 122.8592 | -59.198 | 63.3179 | 0.38365 | 0.01005 | 0.0033161 | 0.0041403 | 0.06607 | 0.0003357 | 0.067759 | -59.1064 | 63.3591 | -59.4727 | -59.4131 | 62.6633 | 4.0009 | -0.1831 | -0.032043 | 63.3316 | -59.5276 | -0.27466 | 0.041199 | 0.091553 | -0.21515 | 0.11444 | -0.6546 | -0.66833 | -0.32959 | 0.013733 | 0.36621
840.5781 | 122.699 | -59.2209 | 63.3774 | 0.24632 | 0.0089824 | 0.0073751 | 0.0075581 | 0.063721 | -0.0015869 | 0.067546 | -59.166 | 63.4369 | -59.5047 | -59.4818 | 62.5488 | 3.8773 | 0.045776 | -0.16937 | 63.4094 | -59.5734 | -0.28381 | 0.05951 | 0.054931 | -0.26093 | 0.091552 | -0.82855 | -0.8606 | -0.35248 | 0.032044 | 0.33875
841.5781 | 122.7905 | -59.2072 | 63.3957 | 0.38365 | 0.0089824 | 0.0065205 | 0.00093587 | 0.062866 | -0.0011597 | 0.068614 | -59.0469 | 63.4369 | -59.5139 | -59.5001 | 62.6358 | 3.9413 | -0.022888 | -0.15106 | 63.4415 | -59.5551 | -0.3067 | 0.041199 | 0.16022 | -0.29297 | 0.054932 | -0.75989 | -0.80566 | -0.3479 | 0.045776 | 0.46692
842.5781 | 122.731 | -59.2117 | 63.4186 | 0.40654 | 0.010478 | 0.0035299 | -0.00013233 | 0.064575 | -0.0015869 | 0.068187 | -59.1843 | 63.4186 | -59.4955 | -59.4223 | 62.6404 | 3.9368 | -0.009155 | -0.15106 | 63.4689 | -59.5276 | -0.28381 | 0 | 0.027466 | -0.21057 | 0.10529 | -0.7782 | -0.82855 | -0.31586 | 0.050354 | 0.31128
843.5781 | 122.7722 | -59.1751 | 63.4186 | 0.4218 | 0.0094096 | 0.0086567 | 0.0056355 | 0.062012 | -0.0037231 | 0.071391 | -59.1248 | 63.4644 | -59.4772 | -59.4818 | 62.5351 | 3.8956 | 0.07782 | -0.16937 | 63.4598 | -59.5047 | -0.30212 | 0.045776 | 0.050354 | -0.3067 | 0.022888 | -0.88348 | -0.92468 | -0.32959 | 0.041199 | 0.35248
844.5781 | 122.7722 | -59.1476 | 63.4048 | 0.39891 | 0.010264 | 0.0080159 | 0.0041403 | 0.067139 | -0.0007325 | 0.067973 | -59.0973 | 63.4644 | -59.4315 | -59.404 | 62.6404 | 3.9505 | -0.09613 | -0.1236 | 63.4415 | -59.5093 | -0.28381 | 0.059509 | 0.050354 | -0.25635 | 0.10528 | -0.76447 | -0.80109 | -0.36163 | 0.036621 | 0.33417
845.5781 | 122.7814 | -59.1568 | 63.446 | 0.33787 | 0.0066326 | 0.0069477 | 0.0030721 | 0.06543 | -0.0005189 | 0.070109 | -59.079 | 63.4918 | -59.4315 | -59.3903 | 62.6404 | 3.9505 | -0.07782 | -0.13275 | 63.4415 | -59.4818 | -0.27466 | 0.045776 | 0.07782 | -0.23346 | 0.091553 | -0.80566 | -0.80109 | -0.32501 | -0.004578 | 0.35248
846.5781 | 122.8317 | -59.1385 | 63.4506 | 0.37602 | 0.0089824 | 0.0054525 | 0.0045675 | 0.06607 | -0.0015869 | 0.068187 | -59.079 | 63.5468 | -59.4131 | -59.3948 | 62.6221 | 3.9047 | -0.009155 | -0.24719 | 63.4827 | -59.4864 | -0.27466 | 0.09613 | 0.05951 | -0.25635 | 0.091553 | -0.82855 | -0.8606 | -0.3479 | 0.032043 | 0.33417
847.5781 | 122.7539 | -59.1019 | 63.4689 | 0.33024 | 0.0087688 | 0.0050251 | 0.0047811 | 0.064148 | -9.1495e-05 | 0.068187 | -59.0378 | 63.5284 | -59.3948 | -59.3719 | 62.6541 | 3.9459 | -0.036621 | -0.15564 | 63.4872 | -59.4681 | -0.29297 | 0.059509 | 0.064087 | -0.27008 | 0.096131 | -0.81482 | -0.83313 | -0.36621 | 0.018311 | 0.35705
848.5781 | 122.7722 | -59.1019 | 63.501 | -0.1733 | 0.0079142 | 0.0045979 | 0.0024313 | 0.065002 | 0.0016175 | 0.068614 | -59.0561 | 63.5696 | -59.3948 | -59.3536 | 62.6541 | 3.9368 | 0 | -0.15564 | 63.5284 | -59.404 | -0.29297 | 0.068664 | 0.045777 | -0.25177 | 0.050354 | -0.84686 | -0.87433 | -0.30212 | 0.027465 | 0.33874
849.5781 | 122.7722 | -59.0973 | 63.5101 | -1.9128 | 0.0077006 | 0.0082295 | 0.0034993 | 0.065216 | -0.0003051 | 0.068187 | -58.9325 | 63.6108 | -59.3445 | -59.3216 | 62.677 | 3.9413 | 0.004578 | -0.16479 | 63.5376 | -59.436 | -0.24719 | 0.10071 | 0.16479 | -0.2243 | 0.11444 | -0.83313 | -0.8606 | -0.33874 | 0.027466 | 0.41199
850.5781 | 122.7356 | -59.0607 | 63.5468 | 0.38365 | 0.010691 | 0.0073751 | 0.0024313 | 0.062866 | 0.0003357 | 0.067973 | -59.0012 | 63.6108 | -59.3628 | -59.3948 | 62.645 | 3.9917 | 0.050354 | -0.20599 | 63.5468 | -59.404 | -0.30212 | 0.064087 | 0.059509 | -0.33417 | 0.009156 | -0.90179 | -0.90179 | -0.34332 | 0 | 0.36163
851.5781 | 122.818 | -59.024 | 63.5422 | 0.36839 | 0.010264 | 0.0039571 | 0.0024313 | 0.066925 | 0.0024719 | 0.067759 | -58.96 | 63.6017 | -59.317 | -59.2712 | 62.7319 | 3.978 | -0.091553 | -0.15106 | 63.5559 | -59.3674 | -0.29297 | 0.05951 | 0.064087 | -0.24719 | 0.096131 | -0.81024 | -0.82397 | -0.34332 | 0.013733 | 0.35706
852.5781 | 122.7814 | -59.0195 | 63.5651 | 0.37602 | 0.010905 | 0.0037435 | 0.0047811 | 0.065643 | 0.0001221 | 0.067546 | -58.9417 | 63.6246 | -59.3262 | -59.2758 | 62.7274 | 3.9688 | -0.050354 | -0.17395 | 63.5696 | -59.3353 | -0.3067 | 0.05951 | 0.07782 | -0.25635 | 0.059509 | -0.83771 | -0.84228 | -0.31586 | 0.004578 | 0.38452
853.5781 | 122.7448 | -59.0195 | 63.5971 | 0.33024 | 0.009196 | 0.0095113 | 0.0062765 | 0.063507 | -0.0007325 | 0.068827 | -58.9508 | 63.6337 | -59.3124 | -59.285 | 62.7319 | 3.9505 | -0.004578 | -0.2243 | 63.6108 | -59.3536 | -0.29297 | 0.036621 | 0.068664 | -0.2655 | 0.068665 | -0.86517 | -0.87891 | -0.33417 | 0.013733 | 0.36163
854.5781 | 122.7905 | -59.0057 | 63.6063 | 1.0932 | 0.010905 | 0.0058797 | 0.0049947 | 0.064148 | 0.0007629 | 0.067546 | -58.8821 | 63.6475 | -59.2712 | -59.2712 | 62.7502 | 3.978 | -0.009155 | -0.19226 | 63.6612 | -59.2987 | -0.2655 | 0.041199 | 0.1236 | -0.2655 | 0.027466 | -0.85602 | -0.91095 | -0.29297 | 0.054932 | 0.3891
855.5781 | 122.7722 | -58.9554 | 63.6383 | 0.41417 | 0.01005 | 0.0056661 | 0.0028585 | 0.06543 | 0.0009765 | 0.068614 | -58.9417 | 63.6475 | -59.285 | -59.2072 | 62.8326 | 4.0283 | -0.013733 | -0.16022 | 63.6475 | -59.3079 | -0.32959 | 0.009155 | 0.013733 | -0.25177 | 0.10071 | -0.80566 | -0.81482 | -0.35248 | 0.009155 | 0.34332
856.5781 | 122.8088 | -58.9737 | 63.6566 | 0.4218 | 0.009196 | 0.0073751 | 0.0037129 | 0.06607 | -0.0013733 | 0.072032 | -58.8913 | 63.6932 | -59.2438 | -59.3628 | 62.5305 | 3.804 | 0.27008 | -0.059509 | 63.707 | -59.285 | -0.27008 | 0.036621 | 0.082398 | -0.3891 | -0.07782 | -1.1261 | -1.1765 | -0.31128 | 0.050354 | 0.35248
857.5781 | 122.7631 | -58.9508 | 63.6429 | 0.33024 | 0.010905 | 0.0086567 | 0.0062765 | 0.063721 | -0.0013733 | 0.067546 | -58.8867 | 63.7299 | -59.2346 | -59.2209 | 62.7594 | 3.9917 | 0 | -0.22888 | 63.6841 | -59.2804 | -0.28381 | 0.086975 | 0.064087 | -0.27008 | 0.05951 | -0.88348 | -0.92468 | -0.32959 | 0.041199 | 0.3479
858.5781 | 122.7539 | -58.9508 | 63.6566 | 0.040327 | 0.01005 | 0.0052387 | 0.0045675 | 0.066711 | -0.0037231 | 0.067973 | -58.8684 | 63.7436 | -59.2163 | -59.198 | 62.7869 | 4.0146 | -0.013733 | -0.19226 | 63.7024 | -59.2438 | -0.2655 | 0.086975 | 0.082398 | -0.24719 | 0.045776 | -0.86975 | -0.91553 | -0.29297 | 0.045777 | 0.3479
859.5781 | 122.7539 | -58.9142 | 63.6795 | 0.26921 | 0.011332 | 0.0084431 | 0.0067037 | 0.066711 | -0.0007325 | 0.066478 | -58.8318 | 63.7619 | -59.2209 | -59.1888 | 62.7777 | 4.0054 | 0.045776 | -0.2243 | 63.7207 | -59.2392 | -0.3067 | 0.082398 | 0.082398 | -0.27466 | 0.050354 | -0.90179 | -0.94299 | -0.32501 | 0.041199 | 0.3891
860.5781 | 122.7264 | -58.8913 | 63.7024 | 0.23869 | 0.0083416 | 0.0063069 | 0.0058493 | 0.065002 | -0.0011597 | 0.067759 | -58.7906 | 63.7756 | -59.1797 | -59.1797 | 62.8143 | 4.0283 | 0.045776 | -0.21057 | 63.739 | -59.2346 | -0.28839 | 0.073242 | 0.10071 | -0.28839 | 0.054932 | -0.88806 | -0.92468 | -0.34332 | 0.036621 | 0.3891
861.5781 | 122.7493 | -58.8593 | 63.7436 | 0.39128 | 0.011332 | 0.0060933 | 0.0039267 | 0.065857 | -9.1495e-05 | 0.067546 | -58.8135 | 63.7756 | -59.1568 | -59.1293 | 63.0157 | 4.0604 | -0.33417 | -0.050354 | 63.707 | -59.2346 | -0.29755 | 0.032044 | 0.045776 | -0.27008 | 0.10529 | -0.72784 | -0.69122 | -0.37537 | -0.036621 | 0.34332
862.5781 | 122.7356 | -58.8776 | 63.7024 | 0.36839 | 0.010691 | 0.0063069 | 0.0045675 | 0.066284 | -0.0020141 | 0.069041 | -58.786 | 63.8077 | -59.1476 | -59.1385 | 62.8372 | 4.0421 | -0.009155 | -0.21515 | 63.7756 | -59.1751 | -0.27008 | 0.10529 | 0.091552 | -0.26093 | 0.036621 | -0.86517 | -0.93842 | -0.29755 | 0.073242 | 0.36163
863.5781 | 122.7219 | -58.8409 | 63.7756 | 0.32261 | 0.0098368 | 0.0067341 | 0.0060629 | 0.066284 | 0.0005493 | 0.067973 | -58.7769 | 63.8489 | -59.1293 | -59.1248 | 62.8418 | 4.0192 | 0.004578 | -0.21057 | 63.8077 | -59.1705 | -0.28839 | 0.073242 | 0.064087 | -0.28381 | 0.045776 | -0.93384 | -0.96588 | -0.32959 | 0.032043 | 0.35248
864.5781 | 122.7676 | -58.7997 | 63.8077 | 0.33024 | 0.011759 | 0.0058797 | 0.0032857 | 0.067352 | 0.0007629 | 0.066264 | -58.7402 | 63.8535 | -59.1202 | -59.1156 | 62.8281 | 4.0329 | 0.004578 | -0.23346 | 63.8397 | -59.1522 | -0.32043 | 0.045777 | 0.05951 | -0.31586 | 0.036621 | -0.97961 | -1.0117 | -0.35248 | 0.032044 | 0.37994
865.5781 | 122.7493 | -58.8089 | 63.7848 | -0.64632 | 0.0085552 | 0.0067341 | 0.0037129 | 0.066498 | 0.0005493 | 0.0684 | -58.7906 | 63.8626 | -59.0927 | -59.0515 | 62.8784 | 4.0558 | 0.004578 | -0.21973 | 63.8351 | -59.1064 | -0.28381 | 0.07782 | 0.018311 | -0.24262 | 0.054931 | -0.90637 | -0.95673 | -0.29755 | 0.050354 | 0.30212
866.5781 | 122.7356 | -58.7585 | 63.8306 | 0.31499 | 0.011759 | 0.0080159 | 0.0052083 | 0.066284 | -9.1495e-05 | 0.070964 | -58.6716 | 63.8947 | -59.0698 | -59.0469 | 62.9105 | 4.0512 | 0.045776 | -0.25177 | 63.9038 | -59.1156 | -0.31128 | 0.064087 | 0.086975 | -0.28839 | 0.068665 | -0.9201 | -0.99335 | -0.35706 | 0.073243 | 0.39825
867.5781 | 122.7722 | -58.7219 | 63.8626 | 0.27684 | 0.010905 | 0.0097249 | 0.0049947 | 0.065857 | -9.1495e-05 | 0.069255 | -58.6304 | 63.913 | -59.0332 | -59.0149 | 62.9425 | 4.0421 | 0.041199 | -0.23346 | 63.8901 | -59.0561 | -0.31128 | 0.050354 | 0.091553 | -0.29297 | 0.041198 | -0.9201 | -0.94757 | -0.33417 | 0.027466 | 0.40283
868.5781 | 122.85 | -58.7219 | 63.8992 | 0.39891 | 0.0096232 | 0.0073751 | 0.0041403 | 0.06607 | -0.0005189 | 0.0684 | -58.6349 | 63.9587 | -59.0103 | -59.0057 | 62.9425 | 4.0466 | -0.009155 | -0.53558 | 63.8947 | -59.0515 | -0.28839 | 0.059509 | 0.086975 | -0.28381 | 0.045777 | -0.95673 | -0.95215 | -0.32959 | -0.004578 | 0.37537
869.5781 | 122.7585 | -58.6853 | 63.913 | 0.33024 | 0.010691 | 0.0088703 | 0.0054219 | 0.067139 | -0.0009461 | 0.069896 | -58.6029 | 63.9862 | -58.9828 | -58.9783 | 62.9654 | 4.01 | 0.009155 | -0.25177 | 63.9496 | -59.0195 | -0.29755 | 0.073242 | 0.082398 | -0.29297 | 0.041199 | -0.94757 | -0.98419 | -0.33417 | 0.036621 | 0.37994
870.5781 | 122.7722 | -58.6716 | 63.9359 | 0.28447 | 0.010691 | 0.0031025 | 0.0049947 | 0.06607 | -0.0003051 | 0.068827 | -58.5617 | 64.0045 | -58.9279 | -58.9554 | 62.9837 | 4.0146 | 0.004578 | -0.23804 | 63.9954 | -59.0057 | -0.25635 | 0.068665 | 0.10986 | -0.28381 | 0.050354 | -0.95215 | -1.0117 | -0.33417 | 0.059509 | 0.36621
871.5781 | 122.7448 | -58.6441 | 63.9908 | 0.22343 | 0.011332 | 0.0080159 | 0.0058493 | 0.064361 | 0.0001221 | 0.068187 | -58.4885 | 64.0594 | -58.8913 | -58.873 | 63.0569 | 4.0421 | 0.036621 | -0.17853 | 63.9999 | -58.9691 | -0.24719 | 0.068664 | 0.15564 | -0.22888 | 0.09613 | -0.93384 | -0.94299 | -0.32501 | 0.009155 | 0.40283
872.5781 | 122.7631 | -58.6029 | 64.0228 | 0.42943 | 0.009196 | 0.0052387 | 0.0075581 | 0.067993 | -0.0024415 | 0.065409 | -58.5068 | 64.0869 | -58.905 | -58.6761 | 63.2034 | 4.01 | -0.022888 | -0.14648 | 64.0411 | -58.9371 | -0.30212 | 0.064087 | 0.09613 | -0.073242 | 0.26093 | -0.8194 | -0.83771 | -0.33417 | 0.018311 | 0.39825
873.5781 | 122.7493 | -58.5892 | 64.0411 | 0.27684 | 0.0098368 | 0.0082295 | 0.0028585 | 0.064789 | -0.0011597 | 0.069682 | -58.4564 | 64.0594 | -58.8455 | -58.8181 | 63.089 | 3.9963 | 0.041199 | -0.2243 | 64.064 | -58.9279 | -0.25635 | 0.01831 | 0.13275 | -0.22888 | 0.10986 | -0.95215 | -0.97504 | -0.33875 | 0.022888 | 0.3891
874.5781 | 122.7219 | -58.5663 | 64.064 | 0.25395 | 0.0094096 | 0.0065205 | 0.0056355 | 0.067352 | -0.0011597 | 0.069468 | -58.4015 | 64.1556 | -58.8272 | -58.7906 | 63.1256 | 3.9917 | 0.027466 | -0.19684 | 64.1144 | -58.8593 | -0.26093 | 0.091553 | 0.1648 | -0.2243 | 0.068665 | -0.93842 | -0.98877 | -0.29297 | 0.050354 | 0.42572
875.5781 | 122.7402 | -58.5526 | 64.0869 | 0.36076 | 0.010478 | 0.0097249 | 0.0054219 | 0.06607 | -0.0013733 | 0.069468 | -58.4152 | 64.1418 | -58.8043 | -58.8089 | 63.0936 | 3.9597 | 0.027466 | -0.21973 | 64.1327 | -58.8547 | -0.25177 | 0.054932 | 0.13733 | -0.25635 | 0.045776 | -0.99335 | -1.0391 | -0.30212 | 0.045776 | 0.3891
876.5781 | 122.7081 | -58.493 | 64.1144 | 0.24632 | 0.010905 | 0.0060933 | 0.0058493 | 0.066711 | -0.0003051 | 0.066691 | -58.3511 | 64.2151 | -58.7677 | -58.7677 | 63.121 | 3.9459 | 0.027466 | -0.23804 | 64.1693 | -58.8043 | -0.27466 | 0.10071 | 0.14191 | -0.27466 | 0.036621 | -0.99335 | -1.0483 | -0.31128 | 0.054932 | 0.41656
877.5781 | 122.7676 | -58.4564 | 64.1556 | 0.27684 | 0.0096232 | 0.0086567 | 0.0062765 | 0.064361 | 0.0001221 | 0.067759 | -58.2962 | 64.2197 | -58.7219 | -58.7219 | 63.1714 | 3.9597 | 0.059509 | -0.20599 | 64.183 | -58.7952 | -0.2655 | 0.064087 | 0.16022 | -0.2655 | 0.073242 | -0.98419 | -1.0117 | -0.33875 | 0.027465 | 0.42572
878.5781 | 122.7493 | -58.4015 | 64.2014 | 0.27684 | 0.0094096 | 0.0082295 | 0.0056355 | 0.066498 | -0.0028687 | 0.068614 | -58.2642 | 64.238 | -58.699 | -58.6578 | 63.2263 | 3.9505 | 0.045776 | -0.19684 | 64.2288 | -58.7311 | -0.29755 | 0.036621 | 0.13733 | -0.25635 | 0.073242 | -0.97504 | -1.0025 | -0.32959 | 0.027466 | 0.43488
879.5781 | 122.7493 | -58.3694 | 64.2014 | 0.29973 | 0.009196 | 0.0016073 | 0.0056355 | 0.067352 | -0.0013733 | 0.069255 | -58.2687 | 64.3021 | -58.6761 | -58.6533 | 63.2217 | 3.9413 | 0.027466 | -0.22888 | 64.2471 | -58.7219 | -0.3067 | 0.10071 | 0.10071 | -0.28381 | 0.068665 | -0.97961 | -1.0254 | -0.35248 | 0.045776 | 0.40741
880.5781 | 122.7997 | -58.3557 | 64.2517 | 0.22343 | 0.010905 | 0.0090841 | 0.0075581 | 0.064789 | 0.0007629 | 0.067759 | -58.1589 | 64.3204 | -58.5983 | -58.58 | 63.2996 | 3.9642 | 0.036621 | -0.19684 | 64.2929 | -58.6533 | -0.24262 | 0.068665 | 0.19684 | -0.2243 | 0.073242 | -0.95215 | -0.99335 | -0.29755 | 0.041199 | 0.43945
881.5781 | 122.731 | -58.3099 | 64.3021 | 0.13951 | 0.0096232 | 0.0086567 | 0.0069173 | 0.066498 | -0.0009461 | 0.069682 | -58.1223 | 64.3478 | -58.5892 | -58.5251 | 63.3545 | 3.9734 | 0.036621 | -0.1831 | 64.325 | -58.6212 | -0.27923 | 0.045776 | 0.18768 | -0.21515 | 0.096131 | -0.94757 | -0.97046 | -0.31128 | 0.022888 | 0.46692
882.5781 | 122.7814 | -58.2458 | 64.3433 | 0.2921 | 0.011546 | 0.0092977 | 0.0052083 | 0.064148 | -0.0018005 | 0.0684 | -58.1085 | 64.389 | -58.5526 | -58.5297 | 63.3316 | 3.9597 | 0.045776 | -0.19226 | 64.3936 | -58.5983 | -0.3067 | 0.045776 | 0.13733 | -0.28381 | 0.068665 | -1.0117 | -1.062 | -0.35248 | 0.050354 | 0.44403
883.5781 | 122.7493 | -58.2092 | 64.3936 | 0.26921 | 0.010478 | 0.0054525 | 0.0064901 | 0.064148 | -0.0011597 | 0.069468 | -58.0444 | 64.4669 | -58.4885 | -58.4702 | 63.414 | 3.9459 | 0.032043 | -0.18768 | 64.4348 | -58.548 | -0.27923 | 0.073242 | 0.16479 | -0.26093 | 0.07782 | -0.97961 | -1.0208 | -0.33875 | 0.041198 | 0.44403
884.5781 | 122.7676 | -58.2047 | 64.4394 | 0.23869 | 0.0072734 | 0.0058797 | 0.0073445 | 0.064575 | -0.0005189 | 0.071177 | -57.9803 | 64.476 | -58.4656 | -58.4106 | 63.4506 | 3.9551 | 0.045776 | -0.15564 | 64.4852 | -58.4885 | -0.26093 | 0.036621 | 0.2243 | -0.20599 | 0.077819 | -0.98877 | -1.0345 | -0.28381 | 0.045776 | 0.48523
885.5781 | 122.7676 | -58.1223 | 64.4897 | 0.17003 | 0.011119 | 0.0069477 | 0.0049947 | 0.065857 | -0.0007325 | 0.069255 | -57.9117 | 64.5447 | -58.3969 | -58.3328 | 63.5101 | 3.978 | 0.018311 | -0.13275 | 64.5309 | -58.4473 | -0.27466 | 0.054932 | 0.21057 | -0.21057 | 0.11444 | -0.97961 | -1.0208 | -0.32501 | 0.041199 | 0.48523
886.5781 | 122.7402 | -58.0856 | 64.5538 | 0.31499 | 0.009196 | 0.0060933 | 0.0049947 | 0.06842 | -9.1495e-05 | 0.066691 | -57.8934 | 64.6042 | -58.3511 | -58.3237 | 63.5147 | 3.9459 | 0.045776 | -0.16022 | 64.595 | -58.4061 | -0.2655 | 0.050354 | 0.19226 | -0.23804 | 0.082398 | -1.0391 | -1.0803 | -0.32044 | 0.041199 | 0.45776
887.5781 | 122.7814 | -58.0078 | 64.5905 | 0.24632 | 0.0096232 | 0.0039571 | 0.0052083 | 0.067566 | -0.0018005 | 0.068187 | -57.7606 | 64.6545 | -58.2825 | -58.2321 | 63.6292 | 4.0009 | 0.032043 | -0.082397 | 64.6133 | -58.3328 | -0.27466 | 0.064087 | 0.24719 | -0.22431 | 0.10071 | -0.9613 | -0.98419 | -0.32501 | 0.022888 | 0.52185
888.5781 | 122.7997 | -57.9575 | 64.65 | -0.24959 | 0.0094096 | 0.0048115 | 0.0054219 | 0.067352 | -0.0018005 | 0.067546 | -57.7194 | 64.7049 | -58.2321 | -58.1497 | 63.6703 | 4.0283 | 0.004578 | -0.068665 | 64.6912 | -58.2733 | -0.27466 | 0.054932 | 0.23804 | -0.19226 | 0.1236 | -0.97961 | -1.0208 | -0.31586 | 0.041199 | 0.5127
889.5781 | 122.731 | -57.8934 | 64.7232 | 0.26921 | 0.01005 | 0.0067341 | 0.0043539 | 0.067566 | -0.0011597 | 0.067759 | -57.6782 | 64.7736 | -58.2001 | -58.1406 | 63.6932 | 3.9597 | 0.027466 | -0.13733 | 64.7324 | -58.223 | -0.3067 | 0.050354 | 0.21515 | -0.24719 | 0.082397 | -1.03 | -1.0391 | -0.32959 | 0.009155 | 0.52185
890.5781 | 122.7859 | -57.8339 | 64.7461 | 0.23106 | 0.0083416 | 0.0043843 | 0.0073445 | 0.067566 | -0.0035095 | 0.069468 | -57.6096 | 64.8239 | -58.0948 | -58.0719 | 63.7527 | 3.9322 | 0.032043 | -0.14648 | 64.801 | -58.1589 | -0.26093 | 0.07782 | 0.2243 | -0.23804 | 0.086976 | -0.99335 | -1.0483 | -0.32501 | 0.054931 | 0.48523
891.5781 | 122.7493 | -57.7789 | 64.7827 | 0.17003 | 0.010691 | 0.0048115 | 0.0069173 | 0.066925 | -0.0018005 | 0.069041 | -57.5317 | 64.888 | -58.0673 | -57.9987 | 63.8168 | 3.9322 | 0.022888 | -0.15564 | 64.8697 | -58.0856 | -0.28839 | 0.10529 | 0.24719 | -0.21973 | 0.086975 | -0.96588 | -1.0529 | -0.3067 | 0.086975 | 0.53558
892.5781 | 122.7768 | -57.7011 | 64.8697 | 0.14714 | 0.0085552 | 0.0092977 | 0.0039267 | 0.066498 | -0.0011597 | 0.067973 | -57.4356 | 64.9475 | -57.9941 | -57.9163 | 63.8947 | 3.9413 | 0.027466 | -0.13733 | 64.9338 | -58.017 | -0.29297 | 0.07782 | 0.2655 | -0.21515 | 0.10071 | -0.97504 | -1.0391 | -0.31586 | 0.064087 | 0.55847
893.5781 | 122.7356 | -57.6508 | 64.9612 | 0.26921 | 0.010264 | 0.0054525 | 0.0075581 | 0.066284 | -0.0015869 | 0.066264 | -57.4173 | 64.9979 | -57.9346 | -57.9208 | 63.8901 | 3.8818 | 0.041199 | -0.19684 | 64.9796 | -58.0078 | -0.28381 | 0.036621 | 0.23346 | -0.27008 | 0.086975 | -1.0712 | -1.0895 | -0.35706 | 0.01831 | 0.51727
894.5781 | 122.7676 | -57.5684 | 65.0024 | 0.33024 | 0.0098368 | 0.0078023 | 0.0075581 | 0.066498 | -0.0024415 | 0.068187 | -57.3029 | 65.0894 | -57.8476 | -57.7789 | 64.0045 | 3.9139 | 0.027466 | -0.10986 | 65.0574 | -57.8842 | -0.27924 | 0.086976 | 0.2655 | -0.21057 | 0.10529 | -0.99792 | -1.0529 | -0.31586 | 0.054932 | 0.54474
895.5781 | 122.8226 | -57.4905 | 65.0711 | 0.040327 | 0.0085552 | 0.0080159 | 0.0081991 | 0.064361 | -0.0026551 | 0.069468 | -57.2205 | 65.1489 | -57.7972 | -57.7057 | 64.0823 | 3.9368 | 0.059509 | -0.10529 | 65.0894 | -57.843 | -0.3067 | 0.07782 | 0.27008 | -0.21515 | 0.13733 | -0.98877 | -1.0071 | -0.35248 | 0.018311 | 0.57678
896.5781 | 122.7493 | -57.4356 | 65.1535 | 0.17003 | 0.010905 | 0.0073751 | 0.0071309 | 0.066711 | -0.0024415 | 0.069468 | -57.1747 | 65.2222 | -57.7057 | -57.6874 | 64.1006 | 3.8635 | 0.036621 | -0.15564 | 65.2039 | -57.7606 | -0.27008 | 0.068665 | 0.26093 | -0.25177 | 0.073242 | -1.0529 | -1.1032 | -0.32501 | 0.050354 | 0.53101
897.5781 | 122.7539 | -57.3624 | 65.2222 | 0.20817 | 0.0096232 | 0.0022481 | 0.0056355 | 0.06543 | -0.0013733 | 0.0684 | -57.0831 | 65.2908 | -57.6553 | -57.605 | 64.1876 | 3.8361 | 0.027466 | -0.14648 | 65.2542 | -57.7194 | -0.29297 | 0.068665 | 0.27924 | -0.24261 | 0.11444 | -1.0345 | -1.0666 | -0.35705 | 0.032043 | 0.5722
898.5781 | 122.8134 | -57.2891 | 65.2771 | 0.14714 | 0.010478 | 0.0058797 | 0.0054219 | 0.065216 | -0.0026551 | 0.069255 | -56.987 | 65.3778 | -57.5546 | -57.5043 | 64.2471 | 3.8544 | 0.036621 | -0.12817 | 65.332 | -57.6141 | -0.2655 | 0.10071 | 0.30212 | -0.21515 | 0.10986 | -1.03 | -1.0849 | -0.32501 | 0.054931 | 0.56763
899.5781 | 122.7493 | -57.2159 | 65.3961 | 0.22343 | 0.010691 | 0.0084431 | 0.0071309 | 0.067993 | -0.0013733 | 0.069682 | -56.9504 | 65.451 | -57.5134 | -57.4631 | 64.3112 | 3.7949 | 0.050354 | -0.15106 | 65.4282 | -57.55 | -0.29755 | 0.054932 | 0.2655 | -0.24719 | 0.086975 | -1.0849 | -1.1169 | -0.33417 | 0.032044 | 0.56305
900.5781 | 122.7951 | -57.1106 | 65.4602 | 0.23106 | 0.0098368 | 0.0075887 | 0.0043539 | 0.069916 | 0.0001221 | 0.068187 | -56.8451 | 65.5243 | -57.4219 | -57.3715 | 64.4028 | 3.7994 | 0.027466 | -0.15564 | 65.5106 | -57.4448 | -0.31128 | 0.064087 | 0.2655 | -0.26093 | 0.073242 | -1.0574 | -1.1078 | -0.33417 | 0.050354 | 0.57678
901.5781 | 122.8271 | -57.0145 | 65.5701 | 0.33787 | 0.010691 | 0.0050251 | 0.0056355 | 0.066284 | -0.0015869 | 0.068827 | -56.6391 | 65.6433 | -57.2845 | -57.2205 | 64.5676 | 3.9047 | 0.036621 | -0.068665 | 65.6342 | -57.3441 | -0.27008 | 0.073243 | 0.37537 | -0.20599 | 0.1236 | -1.0025 | -1.0666 | -0.32959 | 0.064087 | 0.64545
902.5781 | 122.7722 | -56.9046 | 65.6891 | 0.12425 | 0.011973 | 0.011434 | 0.0064901 | 0.065216 | -0.0028687 | 0.068187 | -56.5796 | 65.7394 | -57.1976 | -57.1243 | 64.6179 | 3.923 | 0.032043 | -0.086975 | 65.7303 | -57.2159 | -0.29297 | 0.050354 | 0.32501 | -0.21973 | 0.091552 | -1.0712 | -1.1124 | -0.31128 | 0.041199 | 0.61798
903.5781 | 122.8134 | -56.8314 | 65.7715 | 0.14714 | 0.0098368 | 0.0052387 | 0.0073445 | 0.065643 | 0.0001221 | 0.068614 | -56.4789 | 65.8676 | -57.0923 | -57.0511 | 64.7049 | 3.8452 | 0.036621 | -0.13275 | 65.8356 | -57.1609 | -0.26093 | 0.096131 | 0.35248 | -0.21973 | 0.10986 | -1.0666 | -1.1307 | -0.32959 | 0.064087 | 0.6134
904.5781 | 122.7676 | -56.7352 | 65.8813 | 0.15477 | 0.0098368 | 0.0082295 | 0.0058493 | 0.066711 | -0.0011597 | 0.066478 | -56.3644 | 65.9363 | -57.0145 | -56.9504 | 64.7919 | 3.8727 | 0.027466 | -0.10529 | 65.8997 | -57.0328 | -0.27924 | 0.054931 | 0.37079 | -0.21515 | 0.082398 | -1.0895 | -1.1078 | -0.29755 | 0.01831 | 0.65002
905.5781 | 122.7905 | -56.6208 | 65.95 | 0.1624 | 0.010691 | 0.0033161 | 0.0058493 | 0.06607 | -0.0007325 | 0.067759 | -56.2637 | 66.0416 | -56.8954 | -56.8588 | 64.9017 | 3.8818 | 0.032043 | -0.082397 | 65.9912 | -56.9641 | -0.27466 | 0.091553 | 0.35706 | -0.23804 | 0.10529 | -1.0483 | -1.0895 | -0.34332 | 0.041199 | 0.63171
906.5781 | 122.7264 | -56.5384 | 66.0507 | 0.20817 | 0.009196 | 0.0095113 | 0.0075581 | 0.067779 | 0.0009765 | 0.067759 | -56.1951 | 66.1148 | -56.813 | -56.7856 | 64.9429 | 3.8177 | 0.041199 | -0.16937 | 66.1011 | -56.8817 | -0.27466 | 0.064087 | 0.34332 | -0.24719 | 0.096131 | -1.1078 | -1.1581 | -0.34332 | 0.050354 | 0.61798
907.5781 | 122.7539 | -56.4468 | 66.1606 | 0.13951 | 0.011119 | 0.0075887 | 0.0056355 | 0.065643 | 0.0001221 | 0.069255 | -56.0486 | 66.2292 | -56.7261 | -56.6528 | 65.1077 | 3.9139 | 0.009155 | -0.073242 | 66.1926 | -56.7673 | -0.27924 | 0.068665 | 0.39825 | -0.20599 | 0.11444 | -1.0529 | -1.0849 | -0.32044 | 0.032044 | 0.67749
908.5781 | 122.818 | -56.3187 | 66.2933 | 0.17766 | 0.009196 | 0.0054525 | 0.0064901 | 0.065643 | -0.0037231 | 0.070109 | -55.925 | 66.3437 | -56.6116 | -56.5659 | 65.1352 | 3.891 | 0.045776 | -0.07782 | 66.3391 | -56.6391 | -0.29297 | 0.050354 | 0.39368 | -0.24719 | 0.073242 | -1.1581 | -1.2039 | -0.32043 | 0.045776 | 0.68664
909.5781 | 122.7905 | -56.1905 | 66.4124 | 0.19291 | 0.0089824 | 0.0067341 | 0.0075581 | 0.06543 | -0.0024415 | 0.068187 | -55.7877 | 66.4536 | -56.5018 | -56.4011 | 65.3 | 3.8635 | -0.027466 | -0.11444 | 66.4444 | -56.5201 | -0.31128 | 0.041198 | 0.40283 | -0.21057 | 0.11902 | -1.1124 | -1.1444 | -0.32959 | 0.032043 | 0.71411
910.5781 | 122.7859 | -56.0989 | 66.4993 | 0.1624 | 0.010905 | 0.0071615 | 0.0043539 | 0.066711 | -0.0020141 | 0.069041 | -55.6595 | 66.5634 | -56.3736 | -56.3004 | 65.387 | 3.8223 | 0.013733 | -0.11444 | 66.5497 | -56.4056 | -0.27466 | 0.064087 | 0.43945 | -0.20142 | 0.10529 | -1.1124 | -1.1627 | -0.3067 | 0.050354 | 0.71411
911.5781 | 122.7814 | -55.957 | 66.6183 | 0.13951 | 0.011332 | 0.0069477 | 0.0060629 | 0.067566 | -0.0026551 | 0.069041 | -55.5405 | 66.6962 | -56.282 | -56.2042 | 65.5151 | 3.8315 | 0.036621 | -0.082397 | 66.6687 | -56.2775 | -0.32501 | 0.07782 | 0.41656 | -0.24719 | 0.073242 | -1.1032 | -1.1536 | -0.32043 | 0.050354 | 0.74158
912.5781 | 122.7676 | -55.838 | 66.7465 | 0.13951 | 0.011332 | 0.0039571 | 0.0071309 | 0.067139 | -0.0024415 | 0.067546 | -55.4123 | 66.8518 | -56.1264 | -56.0669 | 65.6433 | 3.8223 | 0.036621 | -0.064087 | 66.7923 | -56.1951 | -0.28839 | 0.10529 | 0.42572 | -0.22888 | 0.12817 | -1.1032 | -1.149 | -0.35706 | 0.045776 | 0.71411
913.5781 | 122.7631 | -55.751 | 66.8747 | 0.27684 | 0.010691 | 0.0037435 | 0.0067037 | 0.06607 | -0.0011597 | 0.067973 | -55.2979 | 66.9617 | -56.0165 | -56.0028 | 65.7074 | 3.7537 | 0.050354 | -0.1236 | 66.925 | -56.0761 | -0.2655 | 0.086975 | 0.45319 | -0.25177 | 0.073242 | -1.1673 | -1.2177 | -0.32501 | 0.050354 | 0.71869
914.5781 | 122.7356 | -55.5771 | 66.9983 | 0.22343 | 0.011546 | 0.0073751 | 0.0079855 | 0.067352 | -0.0015869 | 0.0684 | -55.1376 | 67.0898 | -55.8929 | -55.8609 | 65.8356 | 3.7308 | 0.036621 | -0.10986 | 67.0578 | -55.9067 | -0.31586 | 0.091553 | 0.43945 | -0.28381 | 0.045776 | -1.1627 | -1.2222 | -0.32959 | 0.059509 | 0.75531
915.5781 | 122.8043 | -55.4489 | 67.1677 | 0.13951 | 0.01005 | 0.0060933 | 0.0049947 | 0.066711 | 0.0007629 | 0.071177 | -54.9454 | 67.2318 | -55.7236 | -55.6915 | 66.0416 | 3.7994 | 0.022888 | -0.004578 | 67.2089 | -55.7419 | -0.27466 | 0.064086 | 0.50354 | -0.24261 | 0.050354 | -1.1261 | -1.1673 | -0.29297 | 0.041198 | 0.7782
916.5781 | 122.8271 | -55.2841 | 67.3096 | 0.18529 | 0.0098368 | 0.0082295 | 0.0058493 | 0.067139 | -9.1495e-05 | 0.070109 | -54.7852 | 67.3737 | -55.5679 | -55.4947 | 66.1606 | 3.717 | -0.07782 | 0.004578 | 67.3462 | -55.5954 | -0.28381 | 0.064087 | 0.49896 | -0.21057 | 0.10071 | -1.149 | -1.1856 | -0.31128 | 0.036621 | 0.78278
917.5781 | 122.7539 | -55.1605 | 67.4652 | 0.1624 | 0.011119 | 0.0090841 | 0.0058493 | 0.065857 | -0.0003051 | 0.070964 | -54.6204 | 67.5293 | -55.4489 | -55.3757 | 66.2888 | 3.653 | 0.018311 | -0.041199 | 67.4927 | -55.4626 | -0.28839 | 0.064087 | 0.54016 | -0.21515 | 0.086975 | -1.1765 | -1.2039 | -0.30212 | 0.027466 | 0.82855
918.5781 | 122.8134 | -55.0095 | 67.6025 | 0.10899 | 0.0096232 | 0.0069477 | 0.0060629 | 0.067139 | -0.0030823 | 0.067973 | -54.4601 | 67.6666 | -55.2704 | -55.2292 | 66.4078 | 3.6163 | 0.018311 | 0.004578 | 67.6666 | -55.3162 | -0.26093 | 0.064087 | 0.54932 | -0.21973 | 0.086975 | -1.1948 | -1.2588 | -0.3067 | 0.064087 | 0.81024
919.5781 | 122.7585 | -54.8401 | 67.7399 | -0.020708 | 0.010691 | 0.0090841 | 0.0075581 | 0.066925 | -0.0030823 | 0.0684 | -54.2999 | 67.8268 | -55.1056 | -55.0598 | 66.5726 | 3.5843 | 0.022888 | 0.022888 | 67.804 | -55.188 | -0.2655 | 0.086975 | 0.54016 | -0.21973 | 0.12817 | -1.1673 | -1.2314 | -0.3479 | 0.064087 | 0.80566
920.5781 | 122.7585 | -54.689 | 67.8955 | 0.25395 | 0.007487 | 0.0084431 | 0.0067037 | 0.067352 | -0.0037231 | 0.069041 | -54.1626 | 67.9825 | -55.0232 | -54.9728 | 66.6733 | 3.4836 | 0.041199 | -0.018311 | 67.9596 | -55.0369 | -0.33417 | 0.086975 | 0.52643 | -0.28381 | 0.064087 | -1.2222 | -1.2863 | -0.3479 | 0.064087 | 0.86059
921.5781 | 122.7539 | -54.5242 | 68.0878 | 0.23106 | 0.010905 | 0.0086567 | 0.0054219 | 0.067139 | -0.0024415 | 0.069255 | -53.9703 | 68.1381 | -54.8218 | -54.7897 | 66.8243 | 3.4195 | 0.036621 | 0 | 68.1198 | -54.8813 | -0.29755 | 0.050354 | 0.55389 | -0.2655 | 0.091553 | -1.2634 | -1.2955 | -0.35706 | 0.032043 | 0.85144
922.5781 | 122.7676 | -54.3411 | 68.2617 | 0.13188 | 0.011759 | 0.0063069 | 0.0041403 | 0.064148 | -0.0035095 | 0.067546 | -53.7277 | 68.3166 | -54.6204 | -54.5151 | 67.0624 | 3.447 | 0.041199 | 0.10986 | 68.3441 | -54.6433 | -0.27924 | 0.054931 | 0.6134 | -0.17395 | 0.12817 | -1.1993 | -1.2817 | -0.30213 | 0.082397 | 0.89264
923.5781 | 122.7997 | -54.1306 | 68.4723 | 0.18529 | 0.010691 | 0.0073751 | 0.0047811 | 0.067139 | -0.0022277 | 0.072032 | -53.5172 | 68.5272 | -54.3961 | -54.3823 | 67.2043 | 3.3005 | 0.027466 | 0.032043 | 68.5089 | -54.4601 | -0.2655 | 0.054932 | 0.6134 | -0.25177 | 0.07782 | -1.268 | -1.3046 | -0.32959 | 0.036621 | 0.87891
924.5781 | 122.7493 | -53.9429 | 68.6646 | 0.13951 | 0.0098368 | 0.011648 | 0.0067037 | 0.067566 | -0.0011597 | 0.067759 | -53.302 | 68.7424 | -54.213 | -54.1626 | 67.4103 | 3.2639 | 0.013733 | 0.07782 | 68.7195 | -54.2358 | -0.27008 | 0.07782 | 0.64087 | -0.21973 | 0.073242 | -1.2543 | -1.3092 | -0.29297 | 0.054931 | 0.91095
925.5781 | 122.7859 | -53.714 | 68.8843 | 0.12425 | 0.0094096 | 0.0078023 | 0.0062765 | 0.06543 | 0.0001221 | 0.067973 | -53.0548 | 68.9941 | -53.9749 | -53.9429 | 67.6346 | 3.1906 | 0.022888 | 0.09613 | 68.9392 | -54.0527 | -0.26093 | 0.10986 | 0.65918 | -0.22888 | 0.10986 | -1.2497 | -1.3046 | -0.33875 | 0.054932 | 0.9201
926.5781 | 122.818 | -53.508 | 69.0765 | 0.18529 | 0.011546 | 0.0063069 | 0.0069173 | 0.067139 | -0.0022277 | 0.067973 | -52.8351 | 69.1772 | -53.7643 | -53.7277 | 67.8085 | 3.1448 | 0.027466 | 0.12817 | 69.1452 | -53.8193 | -0.25635 | 0.10071 | 0.67291 | -0.21973 | 0.091553 | -1.268 | -1.3367 | -0.31128 | 0.068665 | 0.92926
927.5781 | 122.731 | -53.3157 | 69.3146 | 0.25395 | 0.012187 | 0.0056661 | 0.0054219 | 0.065643 | -0.0030823 | 0.066478 | -52.6474 | 69.3695 | -53.595 | -53.5675 | 67.9825 | 3.035 | 0.041199 | 0.10529 | 69.3375 | -53.6407 | -0.27924 | 0.054932 | 0.66833 | -0.25177 | 0.073242 | -1.3321 | -1.355 | -0.32501 | 0.022888 | 0.94757
928.5781 | 122.8088 | -53.1006 | 69.5251 | 0.20054 | 0.012187 | 0.0063069 | 0.0064901 | 0.064789 | -0.0020141 | 0.069682 | -52.3544 | 69.5938 | -53.3615 | -53.2928 | 68.2526 | 3.0121 | 0.027466 | 0.18768 | 69.5618 | -53.4027 | -0.26093 | 0.068665 | 0.74616 | -0.19226 | 0.10986 | -1.2726 | -1.3092 | -0.30212 | 0.036622 | 1.0071
929.5781 | 122.7493 | -52.8351 | 69.7586 | -0.36403 | 0.011332 | 0.0075887 | 0.0071309 | 0.066925 | -0.0013733 | 0.070109 | -52.1301 | 69.8318 | -53.1235 | -53.0685 | 68.4723 | 2.9572 | 0.027466 | 0.21973 | 69.8227 | -53.1692 | -0.28839 | 0.073242 | 0.70496 | -0.23346 | 0.10071 | -1.2863 | -1.3504 | -0.33417 | 0.064087 | 0.99335
930.5781 | 122.7768 | -52.6245 | 69.9921 | 0.22343 | 0.010264 | 0.013784 | 0.0077719 | 0.067566 | -0.0015869 | 0.07075 | -51.8784 | 70.0745 | -52.9083 | -52.8717 | 68.6417 | 2.829 | 0.045776 | 0.16022 | 70.0424 | -52.9312 | -0.28381 | 0.082398 | 0.74616 | -0.24719 | 0.059509 | -1.3504 | -1.4008 | -0.3067 | 0.050354 | 1.03
931.5781 | 122.7585 | -52.4094 | 70.2026 | 0.2158 | 0.011119 | 0.0075887 | 0.0069173 | 0.066498 | 0.0007629 | 0.067973 | -51.6403 | 70.2759 | -52.6886 | -52.6703 | 68.8568 | 2.742 | 0.036621 | 0.20599 | 70.2484 | -52.7435 | -0.27924 | 0.073242 | 0.76904 | -0.26093 | 0.073242 | -1.3458 | -1.3916 | -0.33417 | 0.045776 | 1.0483
932.5781 | 122.7402 | -52.2491 | 70.3949 | 0.17003 | 0.01005 | 0.010579 | 0.0069173 | 0.067139 | -0.0037231 | 0.070109 | -51.4069 | 70.4773 | -52.5055 | -52.4551 | 69.0262 | 2.7054 | 0.022888 | 0.21973 | 70.4498 | -52.5558 | -0.25635 | 0.082398 | 0.84229 | -0.20599 | 0.10071 | -1.3687 | -1.4236 | -0.3067 | 0.054932 | 1.0986
933.5781 | 122.7722 | -52.066 | 70.5688 | 0.26158 | 0.011119 | 0.012288 | 0.0075581 | 0.066284 | -0.0022277 | 0.067332 | -51.2421 | 70.6467 | -52.327 | -52.3407 | 69.1727 | 2.5955 | 0.059509 | 0.20142 | 70.6192 | -52.359 | -0.26093 | 0.077819 | 0.82398 | -0.27466 | 0.018311 | -1.3962 | -1.4465 | -0.29297 | 0.050354 | 1.0849
934.5781 | 122.731 | -51.8509 | 70.7748 | 0.26158 | 0.012187 | 0.0082295 | 0.0075581 | 0.064789 | -0.0003051 | 0.069896 | -50.9903 | 70.8664 | -52.0981 | -52.1027 | 69.3558 | 2.5406 | 0.068665 | 0.24719 | 70.8572 | -52.1667 | -0.24719 | 0.091553 | 0.8606 | -0.25177 | 0.064087 | -1.4191 | -1.5015 | -0.31586 | 0.082398 | 1.1078
935.5781 | 122.818 | -51.535 | 71.0358 | -1.2338 | 0.013041 | 0.010152 | -0.00098673 | 0.062439 | -0.0007325 | 0.069682 | -50.7019 | 71.077 | -51.8188 | -51.7868 | 69.6899 | 2.5497 | -0.054932 | 0.3891 | 71.0541 | -51.8646 | -0.28381 | 0.041198 | 0.83313 | -0.25177 | 0.07782 | -1.3458 | -1.3641 | -0.32959 | 0.01831 | 1.1169
936.5781 | 122.7631 | -51.2238 | 71.3425 | 0.22343 | 0.0098368 | 0.011434 | 0.0069173 | 0.064575 | -0.0007325 | 0.07075 | -50.3036 | 71.4661 | -51.5213 | -51.4618 | 69.96 | 2.4673 | 0.027466 | 0.37079 | 71.3654 | -51.59 | -0.29755 | 0.1236 | 0.9201 | -0.23804 | 0.12817 | -1.3824 | -1.4053 | -0.36621 | 0.022888 | 1.2177
937.5781 | 122.7448 | -51.0498 | 71.5759 | 0.23106 | 0.0077006 | 0.0069477 | 0.0058493 | 0.06308 | -0.0030823 | 0.068187 | -50.116 | 71.64 | -51.3199 | -51.3245 | 70.0974 | 2.3666 | 0.022888 | 0.3067 | 71.5897 | -51.384 | -0.27008 | 0.064087 | 0.93384 | -0.27466 | 0.059509 | -1.4786 | -1.4923 | -0.33417 | 0.013733 | 1.2039
938.5781 | 122.7814 | -50.8392 | 71.7865 | 0.22343 | 0.012187 | 0.011648 | 0.0056355 | 0.066925 | 0.0009765 | 0.0684 | -49.9146 | 71.8277 | -51.1368 | -51.1047 | 70.285 | 2.3117 | 0.045776 | 0.34332 | 71.8185 | -51.1551 | -0.29755 | 0.041199 | 0.92468 | -0.2655 | 0.050354 | -1.5015 | -1.5335 | -0.31586 | 0.032043 | 1.2222
939.5781 | 122.7219 | -50.647 | 71.965 | 0.17766 | 0.011759 | 0.011007 | 0.0067037 | 0.066284 | -0.0009461 | 0.067332 | -49.6536 | 72.0291 | -50.9171 | -50.8987 | 70.4773 | 2.2522 | 0.032043 | 0.36163 | 71.9742 | -50.972 | -0.27008 | 0.064087 | 0.99335 | -0.25177 | 0.073242 | -1.4877 | -1.4969 | -0.32501 | 0.009155 | 1.2634
940.5781 | 122.7905 | -50.4501 | 72.1527 | 0.19291 | 0.013255 | 0.011861 | 0.0081991 | 0.065216 | -0.0011597 | 0.067546 | -49.4156 | 72.258 | -50.7202 | -50.6973 | 70.6741 | 2.2018 | 0.018311 | 0.37537 | 72.2122 | -50.766 | -0.27008 | 0.10529 | 1.0345 | -0.24719 | 0.068664 | -1.4786 | -1.5381 | -0.31586 | 0.059509 | 1.3046
941.5781 | 122.7081 | -50.2487 | 72.3679 | 0.25395 | 0.011546 | 0.0084431 | 0.0049947 | 0.06543 | -0.0009461 | 0.069896 | -49.2279 | 72.4274 | -50.5463 | -50.528 | 70.8344 | 2.1652 | 0.068665 | 0.33417 | 72.4091 | -50.56 | -0.29755 | 0.059509 | 1.0208 | -0.27924 | 0.032044 | -1.5335 | -1.5747 | -0.31128 | 0.041199 | 1.3184
942.5781 | 122.7493 | -50.0565 | 72.5647 | 0.1624 | 0.011332 | 0.0099385 | 0.0096945 | 0.066284 | 0.0009765 | 0.067546 | -48.967 | 72.6013 | -50.354 | -50.2808 | 71.0495 | 2.1606 | 0.022888 | 0.40283 | 72.6105 | -50.3677 | -0.29755 | 0.036621 | 1.0895 | -0.2243 | 0.086975 | -1.5152 | -1.561 | -0.31128 | 0.045777 | 1.387
943.5781 | 122.7997 | -49.91 | 72.6517 | 0.23106 | 0.010905 | 0.010793 | 0.0067037 | 0.065857 | -0.0022277 | 0.067759 | -48.8113 | 72.7432 | -50.1984 | -50.1526 | 71.1502 | 2.1057 | 0.036621 | 0.41199 | 72.7295 | -50.2716 | -0.28839 | 0.091553 | 1.0986 | -0.24262 | 0.11902 | -1.5015 | -1.5793 | -0.36163 | 0.07782 | 1.387
944.5781 | 122.7402 | -49.8138 | 72.8027 | 0.30736 | 0.0124 | 0.011434 | 0.0043539 | 0.067566 | -0.0022277 | 0.067759 | -48.7061 | 72.8531 | -50.1114 | -50.0977 | 71.2326 | 2.0004 | 0.027466 | 0.34332 | 72.8485 | -50.1343 | -0.29755 | 0.050354 | 1.1078 | -0.28381 | 0.036621 | -1.5701 | -1.6159 | -0.32043 | 0.045777 | 1.4053
945.5781 | 122.7905 | -49.649 | 72.9355 | 0.26921 | 0.011973 | 0.012502 | 0.0062765 | 0.066498 | -0.0015869 | 0.069041 | -48.5184 | 73.0591 | -49.9374 | -49.9146 | 71.3699 | 1.9455 | 0.036621 | 0.36163 | 72.9996 | -49.9649 | -0.28839 | 0.1236 | 1.1307 | -0.2655 | 0.050354 | -1.5656 | -1.6296 | -0.31586 | 0.064087 | 1.4191
946.5781 | 122.7676 | -49.4522 | 73.1644 | 0.1624 | 0.012614 | 0.010366 | 0.0047811 | 0.064361 | -0.0007325 | 0.069255 | -48.2895 | 73.2697 | -49.736 | -49.7223 | 71.5393 | 1.8906 | 0.022888 | 0.35706 | 73.1735 | -49.8138 | -0.28381 | 0.10529 | 1.1627 | -0.27008 | 0.091553 | -1.6251 | -1.6342 | -0.36163 | 0.009155 | 1.4465
947.5781 | 122.7493 | -49.2737 | 73.3475 | 0.13188 | 0.010905 | 0.015066 | 0.0064901 | 0.06543 | -0.0020141 | 0.067332 | -48.0743 | 73.4344 | -49.5621 | -49.5209 | 71.7178 | 1.8402 | 0.018311 | 0.36621 | 73.3704 | -49.6216 | -0.28839 | 0.086975 | 1.1993 | -0.24719 | 0.10071 | -1.6296 | -1.6525 | -0.3479 | 0.022888 | 1.4877
948.5781 | 122.7539 | -49.1089 | 73.526 | 0.23869 | 0.011546 | 0.012288 | 0.0060629 | 0.06842 | -0.0018005 | 0.069041 | -47.9324 | 73.6084 | -49.4064 | -49.379 | 71.846 | 1.7487 | 0.064087 | 0.3479 | 73.5809 | -49.4202 | -0.29755 | 0.082397 | 1.1765 | -0.27008 | 0.041199 | -1.68 | -1.7349 | -0.31128 | 0.054932 | 1.474
949.5781 | 122.7768 | -48.8937 | 73.6771 | 0.19291 | 0.011119 | 0.011648 | 0.0064901 | 0.067566 | 0.0005493 | 0.067546 | -47.6761 | 73.7869 | -49.1821 | -49.1455 | 72.0474 | 1.7029 | 0.041199 | 0.39825 | 73.7366 | -49.2142 | -0.28839 | 0.10986 | 1.2177 | -0.25177 | 0.068664 | -1.6296 | -1.6891 | -0.32043 | 0.059509 | 1.506
950.5781 | 122.7814 | -48.6877 | 73.8968 | 0.24632 | 0.012828 | 0.0097249 | 0.0075581 | 0.066284 | -0.0022277 | 0.067118 | -47.4289 | 73.9655 | -48.9578 | -48.9304 | 72.2351 | 1.6296 | 0.041199 | 0.40741 | 73.938 | -49.0128 | -0.27008 | 0.068664 | 1.2589 | -0.24262 | 0.082397 | -1.6617 | -1.7029 | -0.32501 | 0.041198 | 1.5289
951.5781 | 122.7768 | -48.4451 | 74.1531 | 0.18529 | 0.013468 | 0.012929 | 0.0077719 | 0.066711 | -0.0013733 | 0.067332 | -47.2092 | 74.2401 | -48.7427 | -48.7381 | 72.4182 | 1.5381 | 0.027466 | 0.35706 | 74.2081 | -48.7747 | -0.29755 | 0.086975 | 1.236 | -0.29297 | 0.036621 | -1.7349 | -1.7899 | -0.32959 | 0.054932 | 1.5335
952.5781 | 122.7448 | -48.2895 | 74.2813 | 0.26158 | 0.011119 | 0.0090841 | 0.0067037 | 0.066925 | -0.0015869 | 0.066905 | -47.0489 | 74.3912 | -48.5916 | -48.5733 | 72.5281 | 1.4786 | 0.054932 | 0.37079 | 74.3729 | -48.6191 | -0.30212 | 0.10986 | 1.2405 | -0.28381 | 0.045777 | -1.7532 | -1.8448 | -0.32959 | 0.091553 | 1.5427
953.5781 | 122.7722 | -48.1247 | 74.4965 | 0.2921 | 0.011759 | 0.011648 | 0.0064901 | 0.066925 | -0.0018005 | 0.071391 | -46.843 | 74.5697 | -48.4039 | -48.3765 | 72.7203 | 1.4099 | 0.032043 | 0.38452 | 74.5468 | -48.4406 | -0.27924 | 0.073242 | 1.2817 | -0.25177 | 0.064087 | -1.7761 | -1.8265 | -0.31586 | 0.050354 | 1.561
954.5781 | 122.7264 | -47.9233 | 74.7116 | 0.2158 | 0.010478 | 0.012288 | 0.0079855 | 0.06543 | -0.0028687 | 0.065623 | -46.5958 | 74.794 | -48.1567 | -48.1613 | 72.9034 | 1.3687 | 0.022888 | 0.39368 | 74.7665 | -48.1888 | -0.23346 | 0.082397 | 1.3275 | -0.23804 | 0.027466 | -1.8082 | -1.8631 | -0.2655 | 0.054932 | 1.561
955.5781 | 122.7402 | -47.6578 | 74.9359 | 0.30736 | 0.013041 | 0.012716 | 0.0075581 | 0.06543 | 0.0005493 | 0.071391 | -46.3577 | 75.087 | -47.937 | -47.937 | 73.1003 | 1.2955 | 0.045776 | 0.35706 | 75.0275 | -47.9874 | -0.27924 | 0.15106 | 1.3 | -0.27924 | 0.050354 | -1.8356 | -1.9272 | -0.32959 | 0.091553 | 1.5793
956.5781 | 122.7814 | -47.3602 | 75.2609 | 0.18529 | 0.011546 | 0.011648 | 0.0047811 | 0.06842 | -0.0022277 | 0.067973 | -46.0144 | 75.3296 | -47.6349 | -47.612 | 73.3475 | 1.2314 | 0.027466 | 0.44403 | 75.2747 | -47.6852 | -0.27466 | 0.068665 | 1.3458 | -0.25177 | 0.073242 | -1.9135 | -1.9272 | -0.32501 | 0.013733 | 1.6205
957.5781 | 122.7631 | -47.0718 | 75.5219 | 0.1624 | 0.013896 | 0.0088703 | 0.0079855 | 0.063721 | 0.0005493 | 0.068827 | -45.7031 | 75.6271 | -47.3557 | -47.3007 | 73.645 | 1.1948 | 0.022888 | 0.45319 | 75.5676 | -47.374 | -0.28381 | 0.10528 | 1.3687 | -0.22888 | 0.073242 | -1.8768 | -1.9226 | -0.30212 | 0.045776 | 1.6525
958.5781 | 122.7722 | -46.8201 | 75.7965 | 0.24632 | 0.012187 | 0.016775 | 0.0067037 | 0.066284 | -0.0024415 | 0.068187 | -45.5063 | 75.8331 | -47.1313 | -47.1268 | 73.7732 | 1.1078 | 0.059509 | 0.42114 | 75.8286 | -47.1451 | -0.31128 | 0.036621 | 1.3138 | -0.3067 | 0.018311 | -2.0233 | -2.0554 | -0.32501 | 0.032043 | 1.6251
959.5781 | 122.7356 | -46.5134 | 76.1078 | 0.23869 | 0.011546 | 0.010366 | 0.0069173 | 0.067352 | -0.0015869 | 0.069468 | -45.1492 | 76.181 | -46.8155 | -46.7972 | 74.0845 | 1.0574 | 0.054932 | 0.44861 | 76.1719 | -46.8658 | -0.30212 | 0.073242 | 1.3641 | -0.28381 | 0.068665 | -2.0233 | -2.0874 | -0.35248 | 0.064087 | 1.6663
960.5781 | 122.7402 | -46.2387 | 76.387 | 0.25395 | 0.014537 | 0.012075 | 0.0058493 | 0.065857 | -0.0005189 | 0.07075 | -44.8242 | 76.4877 | -46.5042 | -46.5179 | 74.3179 | 1.0025 | 0.036621 | 0.46234 | 76.442 | -46.5454 | -0.2655 | 0.10071 | 1.4145 | -0.27924 | 0.027466 | -2.0691 | -2.124 | -0.3067 | 0.054932 | 1.68
961.5781 | 122.7539 | -45.9183 | 76.6937 | 0.31499 | 0.012614 | 0.011648 | 0.0096945 | 0.066284 | 0.0001221 | 0.070109 | -44.5175 | 76.7899 | -46.2204 | -46.2296 | 74.5605 | 0.96588 | 0.027466 | 0.46234 | 76.7624 | -46.2341 | -0.30212 | 0.09613 | 1.4008 | -0.31128 | 0.004578 | -2.1332 | -2.2018 | -0.31586 | 0.068664 | 1.7029
962.5781 | 122.731 | -45.5978 | 77.0096 | 0.30736 | 0.014964 | 0.012502 | 0.0067037 | 0.066498 | -0.0022277 | 0.067546 | -44.1559 | 77.1194 | -45.8725 | -45.9091 | 74.8123 | 0.91095 | 0.027466 | 0.48523 | 77.092 | -45.9183 | -0.27466 | 0.10986 | 1.442 | -0.31128 | 0.009155 | -2.1973 | -2.2797 | -0.32043 | 0.082397 | 1.7166
963.5781 | 122.7768 | -45.6665 | 76.9272 | 0.19291 | 0.012828 | 0.010579 | 0.0045675 | 0.065002 | -0.0009461 | 0.066905 | -44.2291 | 77.0096 | -45.9412 | -45.9274 | 74.7711 | 0.89722 | 0.022888 | 0.50812 | 76.9684 | -45.9915 | -0.27466 | 0.082398 | 1.4374 | -0.26092 | 0.064087 | -2.1561 | -2.1973 | -0.32501 | 0.041199 | 1.712
964.5781 | 122.7722 | -45.5795 | 77.0233 | 0.17003 | 0.011973 | 0.012075 | 0.0060629 | 0.065216 | 0.0003357 | 0.069255 | -44.1055 | 77.1286 | -45.8496 | -45.8221 | 74.826 | 0.87891 | 0.018311 | 0.53101 | 77.0645 | -45.8908 | -0.27008 | 0.10529 | 1.474 | -0.24262 | 0.068664 | -2.1973 | -2.2385 | -0.31128 | 0.041199 | 1.7441
965.5781 | 122.7402 | -45.3964 | 77.2293 | 0.26921 | 0.014323 | 0.015279 | 0.0054219 | 0.066284 | -0.0015869 | 0.070323 | -43.9133 | 77.3163 | -45.6573 | -45.6573 | 74.9359 | 0.80109 | 0.032043 | 0.48981 | 77.2797 | -45.726 | -0.26093 | 0.086975 | 1.4832 | -0.26093 | 0.068664 | -2.2934 | -2.3438 | -0.32959 | 0.050354 | 1.7441
966.5781 | 122.7493 | -45.2683 | 77.3483 | 0.19291 | 0.01475 | 0.01357 | 0.0073445 | 0.06607 | -0.0013733 | 0.069255 | -43.7302 | 77.4399 | -45.5429 | -45.5475 | 75.0229 | 0.76446 | 0.032043 | 0.50354 | 77.417 | -45.575 | -0.27466 | 0.091552 | 1.5381 | -0.27923 | 0.027466 | -2.3254 | -2.3941 | -0.3067 | 0.068664 | 1.8127
967.5781 | 122.7539 | -45.1126 | 77.4902 | 0.14714 | 0.013041 | 0.011007 | 0.0081991 | 0.065857 | -0.0011597 | 0.069896 | -43.515 | 77.5909 | -45.3918 | -45.3735 | 75.1236 | 0.75989 | 0.032043 | 0.53101 | 77.5681 | -45.433 | -0.27924 | 0.10071 | 1.5976 | -0.26093 | 0.059509 | -2.3666 | -2.4445 | -0.32043 | 0.07782 | 1.8768
968.5781 | 122.7905 | -44.9707 | 77.6184 | 0.11662 | 0.01475 | 0.014211 | 0.0077719 | 0.067352 | -0.0028687 | 0.071177 | -43.309 | 77.7374 | -45.2316 | -45.2133 | 75.2289 | 0.75073 | 0.027466 | 0.55389 | 77.71 | -45.2774 | -0.26093 | 0.11902 | 1.6617 | -0.24262 | 0.064087 | -2.3895 | -2.4811 | -0.3067 | 0.091553 | 1.9226
969.5781 | 122.7264 | -44.8105 | 77.7969 | 0.13188 | 0.011759 | 0.014852 | 0.0081991 | 0.064789 | 0.0005493 | 0.069682 | -43.103 | 77.9022 | -45.0668 | -45.076 | 75.3021 | 0.69122 | 0.036621 | 0.54016 | 77.8336 | -45.1355 | -0.25635 | 0.10529 | 1.7075 | -0.2655 | 0.059509 | -2.4948 | -2.5314 | -0.32501 | 0.036621 | 1.9638
970.5781 | 122.7997 | -44.5816 | 78.035 | 0.12425 | 0.011546 | 0.016561 | 0.0069173 | 0.065643 | -0.0013733 | 0.069682 | -42.8375 | 78.0624 | -44.8975 | -44.8471 | 75.4669 | 0.72327 | 0.036621 | 0.59509 | 78.067 | -44.9203 | -0.31586 | 0.027466 | 1.7441 | -0.2655 | 0.073242 | -2.5681 | -2.6001 | -0.33875 | 0.032044 | 2.0599
971.5781 | 122.8226 | -44.5358 | 78.067 | 0.10136 | 0.014109 | 0.015279 | 0.0067037 | 0.063934 | -0.0003051 | 0.069468 | -42.7094 | 78.1769 | -44.8059 | -44.7647 | 75.4898 | 0.71411 | 0.054932 | 0.64545 | 78.0991 | -44.87 | -0.27008 | 0.10986 | 1.8265 | -0.22888 | 0.10529 | -2.5772 | -2.6093 | -0.33417 | 0.032043 | 2.0966
972.5781 | 122.7722 | -44.3756 | 78.2318 | 0.14714 | 0.015177 | 0.012929 | 0.0075581 | 0.06543 | -9.1495e-05 | 0.069896 | -42.4896 | 78.3096 | -44.6457 | -44.5541 | 75.6088 | 0.70038 | 0.027466 | 0.66834 | 78.3005 | -44.6777 | -0.27008 | 0.077819 | 1.886 | -0.17853 | 0.1236 | -2.623 | -2.6917 | -0.30212 | 0.068664 | 2.1561
973.5781 | 122.8043 | -44.2795 | 78.3463 | 0.093733 | 0.012828 | 0.014852 | 0.0084127 | 0.064789 | -0.0026551 | 0.070536 | -42.2882 | 78.3966 | -44.545 | -44.5038 | 75.6363 | 0.68207 | 0.036621 | 0.65002 | 78.3829 | -44.5679 | -0.2655 | 0.050354 | 1.9913 | -0.2243 | 0.064087 | -2.71 | -2.7466 | -0.28839 | 0.036622 | 2.2568
974.5781 | 122.7905 | -44.1376 | 78.4607 | 0.10136 | 0.013255 | 0.016561 | 0.0088399 | 0.065857 | -0.0026551 | 0.067973 | -42.0914 | 78.5477 | -44.4214 | -44.3665 | 75.6958 | 0.66834 | 0.050354 | 0.66376 | 78.511 | -44.4534 | -0.28381 | 0.086975 | 2.0462 | -0.22888 | 0.086975 | -2.7649 | -2.8152 | -0.31586 | 0.050354 | 2.33
975.5781 | 122.7905 | -44.0414 | 78.5843 | 0.10136 | 0.015605 | 0.014211 | 0.0045675 | 0.064789 | 0.0001221 | 0.070109 | -41.922 | 78.6575 | -44.3069 | -44.2703 | 75.7278 | 0.6546 | 0.041199 | 0.66834 | 78.6346 | -44.3436 | -0.2655 | 0.073242 | 2.1194 | -0.22888 | 0.073242 | -2.8564 | -2.9068 | -0.30212 | 0.050354 | 2.3849
976.5781 | 122.7768 | -43.9316 | 78.6713 | 0.063215 | 0.014964 | 0.015279 | 0.0062765 | 0.066498 | -0.0011597 | 0.068827 | -41.7389 | 78.7354 | -44.2062 | -44.1742 | 75.7507 | 0.64087 | 0.050354 | 0.68665 | 78.7354 | -44.2429 | -0.27466 | 0.064087 | 2.1927 | -0.24261 | 0.068665 | -2.9205 | -2.9846 | -0.31128 | 0.064087 | 2.4673
977.5781 | 122.7539 | -43.8263 | 78.772 | 0.11662 | 0.014109 | 0.013784 | 0.0022177 | 0.065857 | 0.0005493 | 0.067118 | -41.5924 | 78.8773 | -44.1101 | -44.0918 | 75.7507 | 0.59509 | 0.13275 | 0.66376 | 78.8681 | -44.1376 | -0.28381 | 0.10528 | 2.2339 | -0.2655 | 0.045776 | -3.0212 | -3.1174 | -0.31128 | 0.09613 | 2.5177
978.5781 | 122.7402 | -43.7119 | 78.923 | -0.066485 | 0.014964 | 0.014852 | 0.0034993 | 0.064361 | -0.0041503 | 0.072245 | -41.4322 | 78.9642 | -44.0048 | -43.9728 | 75.6042 | 0.48523 | 0.21515 | 0.6958 | 78.9734 | -44.0094 | -0.29297 | 0.041198 | 2.2797 | -0.26093 | 0.036621 | -3.3188 | -3.3691 | -0.29755 | 0.050354 | 2.5726
979.5781 | 122.7859 | -43.6386 | 79.0329 | 0.086103 | 0.014537 | 0.012288 | 0.0049947 | 0.063507 | -9.1495e-05 | 0.071391 | -41.2216 | 79.0649 | -43.8995 | -43.8766 | 75.8194 | 0.57678 | 0.13275 | 0.69122 | 79.0787 | -43.8858 | -0.26093 | 0.032043 | 2.417 | -0.23804 | 0.009155 | -3.2135 | -3.2593 | -0.24719 | 0.045776 | 2.6779
980.5781 | 122.7036 | -43.4189 | 79.216 | -0.081743 | 0.013896 | 0.017843 | 0.0049947 | 0.065216 | -0.0011597 | 0.07075 | -40.979 | 79.2114 | -43.7164 | -43.5516 | 76.1032 | 0.66834 | -0.032043 | 0.67749 | 79.2709 | -43.6935 | -0.29755 | -0.004577 | 2.4399 | -0.13275 | 0.14191 | -3.1128 | -3.1677 | -0.27466 | 0.054932 | 2.7374
981.5781 | 122.7722 | -43.4509 | 79.1931 | -0.051226 | 0.011973 | 0.016775 | 0.0020039 | 0.061584 | -0.0009461 | 0.07075 | -40.892 | 79.2114 | -43.7164 | -43.7164 | 75.8331 | 0.57678 | 0.15564 | 0.68207 | 79.2297 | -43.7027 | -0.2655 | 0.018311 | 2.5589 | -0.2655 | -0.013733 | -3.36 | -3.3966 | -0.25177 | 0.036621 | 2.8244
982.5781 | 122.731 | -43.3914 | 79.2435 | -0.066485 | 0.014537 | 0.015493 | 0.0037129 | 0.062866 | -9.1495e-05 | 0.069896 | -40.7547 | 79.2709 | -43.7027 | -43.6935 | 75.7507 | 0.65002 | 0.46692 | 0.61798 | 79.3121 | -43.6523 | -0.31128 | 0.027466 | 2.6367 | -0.30212 | -0.041198 | -3.4927 | -3.5614 | -0.26093 | 0.068665 | 2.948
983.5781 | 122.7722 | -43.4326 | 79.2023 | 0.0098091 | 0.01475 | 0.014425 | 0.0024313 | 0.063721 | 0.0005493 | 0.068187 | -40.6998 | 79.1794 | -43.7027 | -43.6981 | 75.6363 | 0.58594 | 0.16022 | 0.66834 | 79.2389 | -43.6981 | -0.27008 | -0.022889 | 2.7328 | -0.2655 | 0 | -3.566 | -3.6026 | -0.2655 | 0.036621 | 3.0029
984.5781 | 122.8729 | -43.4647 | 79.1428 | 0.11662 | 0.013468 | 0.01357 | 8.1267e-05 | 0.062866 | -0.0020141 | 0.069682 | -40.5762 | 79.1107 | -43.7256 | -43.6615 | 75.6042 | 0.71869 | 0.009155 | 0.77362 | 79.1519 | -43.7119 | -0.26093 | -0.032043 | 2.8885 | -0.19684 | 0.050354 | -3.5385 | -3.5477 | -0.24719 | 0.009156 | 3.1494
985.5781 | 122.8638 | -43.3594 | 79.1885 | -0.020708 | 0.015605 | 0.016988 | -0.0014139 | 0.060303 | -0.0011597 | 0.073313 | -40.329 | 79.1794 | -43.634 | -43.7485 | 75.4532 | 0.77362 | 0.009155 | 0.71411 | 79.2114 | -43.6203 | -0.27466 | -0.009156 | 3.0304 | -0.3891 | -0.12817 | -3.7354 | -3.7582 | -0.26093 | 0.022888 | 3.3051
986.5781 | 122.8821 | -43.3548 | 79.2114 | -0.21144 | 0.015177 | 0.015493 | 0.0028585 | 0.060089 | 0.0011901 | 0.069896 | -40.2557 | 79.1656 | -43.6295 | -43.5654 | 75.4578 | 0.77362 | -0.004578 | 0.78735 | 79.2068 | -43.6386 | -0.27466 | -0.045777 | 3.0991 | -0.21057 | 0.073242 | -3.7537 | -3.7491 | -0.28381 | -0.004578 | 3.3737
987.5781 | 122.8409 | -43.2724 | 79.2572 | -0.051226 | 0.014537 | 0.013997 | 0.0039267 | 0.060944 | -0.0052185 | 0.068187 | -40.0635 | 79.2206 | -43.5608 | -43.3868 | 75.4395 | 0.71411 | -0.16022 | 0.85144 | 79.2847 | -43.5745 | -0.28839 | -0.036621 | 3.2089 | -0.11444 | 0.18768 | -3.8177 | -3.8452 | -0.30212 | 0.027466 | 3.4973
988.5781 | 122.8683 | -43.2816 | 79.2526 | 0.025068 | 0.014323 | 0.016347 | 0.0037129 | 0.060089 | -0.0007325 | 0.071177 | -40.0543 | 79.216 | -43.5791 | -43.5013 | 75.2838 | 0.86975 | -0.054932 | 0.78735 | 79.248 | -43.5791 | -0.29755 | -0.036622 | 3.2272 | -0.21973 | 0.07782 | -3.9688 | -3.9642 | -0.29755 | -0.004578 | 3.5248
989.5781 | 122.8867 | -43.5608 | 78.978 | -0.020708 | 0.013468 | 0.010366 | 0.0034993 | 0.058807 | 0.0003357 | 0.071818 | -40.2191 | 78.9276 | -43.8538 | -43.808 | 75.0824 | 1.0025 | -0.28381 | 0.56305 | 78.9597 | -43.8675 | -0.29297 | -0.050354 | 3.3417 | -0.24719 | 0.05951 | -3.8956 | -3.8773 | -0.3067 | -0.01831 | 3.6346
990.5781 | 122.8638 | -43.6386 | 78.9047 | 0.032698 | 0.015818 | 0.015066 | 0.0028585 | 0.057739 | -0.0003051 | 0.069682 | -40.2328 | 78.8223 | -43.9453 | -43.8538 | 74.7208 | 0.97504 | -0.068665 | 0.76904 | 78.8773 | -43.9407 | -0.3067 | -0.082397 | 3.4058 | -0.21515 | 0.086975 | -4.184 | -4.1565 | -0.30212 | -0.027466 | 3.7125
991.5781 | 122.8592 | -43.721 | 78.8681 | 0.23106 | 0.013896 | 0.015066 | 0.0039267 | 0.062012 | -9.1495e-05 | 0.070536 | -40.2557 | 78.8086 | -43.9957 | -43.9407 | 74.4873 | 1.0117 | -0.054932 | 0.71411 | 78.8635 | -43.9774 | -0.27466 | -0.059509 | 3.4653 | -0.21973 | 0.036621 | -4.3808 | -4.3762 | -0.25635 | -0.004578 | 3.7399
992.5781 | 122.8821 | -43.7576 | 78.7994 | 0.093733 | 0.016459 | 0.014425 | 0.00072227 | 0.059662 | 0.0014039 | 0.071604 | -40.2145 | 78.7216 | -44.0598 | -43.9636 | 74.3088 | 1.1032 | -0.082397 | 0.72784 | 78.7949 | -44.0094 | -0.30212 | -0.077819 | 3.5431 | -0.20599 | 0.045776 | -4.4907 | -4.4861 | -0.25177 | -0.004577 | 3.8452
993.5781 | 122.8363 | -43.8263 | 78.6987 | 0.27684 | 0.017741 | 0.015279 | 0.0045675 | 0.059448 | -0.0005189 | 0.070323 | -40.2374 | 78.6301 | -44.1422 | -44.0689 | 74.057 | 1.1719 | -0.059509 | 0.70038 | 78.6942 | -44.1238 | -0.31586 | -0.068664 | 3.5889 | -0.24262 | 0.054931 | -4.6417 | -4.6371 | -0.29755 | -0.004577 | 3.9047
994.5781 | 122.8638 | -43.8446 | 78.7125 | 0.33024 | 0.017955 | 0.019338 | 0.0037129 | 0.057739 | 0.0020447 | 0.067973 | -40.21 | 78.6118 | -44.1422 | -44.101 | 74.0387 | 1.2131 | -0.064087 | 0.74616 | 78.7125 | -44.1513 | -0.29755 | -0.10071 | 3.6346 | -0.25635 | 0.050354 | -4.6738 | -4.6738 | -0.3067 | 0 | 3.9322
995.5781 | 122.818 | -43.9819 | 78.598 | 0.20054 | 0.0171 | 0.020193 | 0.0015767 | 0.059662 | 0.0018311 | 0.071604 | -40.1276 | 78.6026 | -44.1788 | -44.1467 | 73.9609 | 1.2222 | -0.07782 | 0.78278 | 78.6118 | -44.2245 | -0.19684 | 0.004578 | 3.8544 | -0.16479 | 0.077819 | -4.6371 | -4.6509 | -0.24261 | 0.013733 | 4.0512
996.5781 | 122.8363 | -43.9362 | 78.6392 | 0.30736 | 0.019023 | 0.01827 | 0.0034993 | 0.060516 | 0.0028991 | 0.073313 | -40.0955 | 78.5294 | -44.2749 | -44.1788 | 73.7915 | 1.3184 | -0.068665 | 0.82855 | 78.5934 | -44.2108 | -0.33874 | -0.10986 | 3.8406 | -0.24262 | 0.032043 | -4.8477 | -4.8019 | -0.27466 | -0.045776 | 4.1794
997.5781 | 122.8729 | -44.0186 | 78.5339 | 0.40654 | 0.020518 | 0.023397 | 0.0075581 | 0.061798 | 0.0020447 | 0.070536 | -39.9765 | 78.4836 | -44.3161 | -44.2062 | 73.5626 | 1.4603 | -0.1831 | 0.88806 | 78.5156 | -44.2932 | -0.29755 | -0.050354 | 4.0421 | -0.18768 | 0.086975 | -4.9713 | -4.953 | -0.27466 | -0.018311 | 4.3396
998.5781 | 122.8043 | -44.1284 | 78.4332 | 0.36076 | 0.019877 | 0.02062 | 0.0058493 | 0.057953 | 0.0018311 | 0.071391 | -40.004 | 78.3646 | -44.3848 | -44.3436 | 73.2513 | 1.5518 | -0.12817 | 0.89264 | 78.4195 | -44.3756 | -0.25635 | -0.068665 | 4.1245 | -0.21515 | 0.032043 | -5.1819 | -5.1682 | -0.24719 | -0.013733 | 4.3808
999.5781 | 122.8455 | -44.165 | 78.4012 | 0.33024 | 0.020304 | 0.021261 | 0.0024313 | 0.060516 | 0.0022583 | 0.072459 | -39.9719 | 78.3508 | -44.4672 | -44.4077 | 72.9446 | 1.6571 | -0.09613 | 0.87433 | 78.3737 | -44.4305 | -0.30212 | -0.050354 | 4.1931 | -0.24262 | 0.022888 | -5.4565 | -5.4291 | -0.2655 | -0.027466 | 4.4952
1000.5781 | 122.8088 | -44.2566 | 78.2913 | 0.36839 | 0.022013 | 0.021688 | 0.0034993 | 0.058594 | 0.0031127 | 0.072673 | -39.949 | 78.2547 | -44.5496 | -44.4763 | 72.6746 | 1.7853 | -0.14191 | 0.8606 | 78.2822 | -44.5404 | -0.29297 | -0.036621 | 4.3076 | -0.21973 | 0.064087 | -5.6168 | -5.6076 | -0.28381 | -0.009155 | 4.6005
1001.5781 | 122.8363 | -44.2886 | 78.241 | 0.36076 | 0.022227 | 0.024465 | 0.0058493 | 0.059448 | 0.0011901 | 0.072032 | -39.8712 | 78.2364 | -44.5862 | -44.4946 | 72.4548 | 1.8951 | -0.16937 | 0.87891 | 78.2135 | -44.5679 | -0.29755 | -0.004578 | 4.4174 | -0.20599 | 0.073242 | -5.7861 | -5.7587 | -0.27924 | -0.027466 | 4.715
1002.5781 | 122.818 | -44.3069 | 78.2318 | 0.31499 | 0.022227 | 0.024465 | 0.0039267 | 0.061798 | 0.0011901 | 0.072245 | -39.8438 | 78.186 | -44.5999 | -44.5312 | 72.2809 | 1.9684 | -0.13733 | 0.84686 | 78.2135 | -44.577 | -0.29297 | -0.045777 | 4.4632 | -0.2243 | 0.045776 | -5.9509 | -5.9326 | -0.27008 | -0.018311 | 4.7562
1003.5781 | 122.8226 | -44.3207 | 78.2318 | 0.32261 | 0.019023 | 0.02297 | 0.0049947 | 0.061371 | 0.0009765 | 0.072886 | -39.7659 | 78.2089 | -44.6182 | -44.5312 | 72.139 | 2.0416 | -0.14648 | 0.85602 | 78.1906 | -44.5999 | -0.29755 | -0.022889 | 4.5547 | -0.21057 | 0.068665 | -6.0928 | -6.0516 | -0.27924 | -0.041199 | 4.8523
1004.5781 | 122.8638 | -44.2612 | 78.2272 | 0.39891 | 0.02479 | 0.021261 | 0.0060629 | 0.062012 | 0.0005493 | 0.073313 | -39.624 | 78.2181 | -44.5953 | -44.4763 | 72.0428 | 2.1194 | -0.21973 | 0.86975 | 78.1998 | -44.5862 | -0.33417 | -0.009155 | 4.6371 | -0.21515 | 0.10986 | -6.1844 | -6.1569 | -0.32501 | -0.027466 | 4.9713
1005.5781 | 122.8729 | -44.2841 | 78.2639 | 0.25395 | 0.023509 | 0.029806 | 0.010122 | 0.061584 | 0.0018311 | 0.072459 | -39.5416 | 78.2684 | -44.5358 | -44.4489 | 71.9467 | 2.1744 | -0.20142 | 0.87433 | 78.2089 | -44.577 | -0.25177 | 0.004578 | 4.7424 | -0.16479 | 0.12817 | -6.3171 | -6.2622 | -0.29297 | -0.054932 | 4.9942
1006.5781 | 122.8867 | -44.2291 | 78.2822 | 0.41417 | 0.024363 | 0.025319 | 0.0088399 | 0.062439 | 0.0005493 | 0.073527 | -39.418 | 78.3005 | -44.5175 | -44.4351 | 71.9009 | 2.1973 | -0.55847 | 0.79651 | 78.2089 | -44.5633 | -0.28839 | 0.01831 | 4.8111 | -0.20599 | 0.12817 | -6.3812 | -6.308 | -0.33417 | -0.073243 | 5.0995
1007.5781 | 122.8958 | -44.1833 | 78.3325 | 0.41417 | 0.026072 | 0.028097 | 0.0088399 | 0.059875 | 0.0028991 | 0.072886 | -39.3036 | 78.3554 | -44.458 | -44.3573 | 71.8231 | 2.3163 | -0.20142 | 0.8606 | 78.3234 | -44.458 | -0.27466 | 0.022888 | 4.8798 | -0.17395 | 0.10071 | -6.5094 | -6.5002 | -0.27466 | -0.009156 | 5.1544
1008.5781 | 122.8317 | -44.165 | 78.3371 | 0.33787 | 0.023081 | 0.026601 | 0.010549 | 0.062652 | 0.0016175 | 0.0731 | -39.2441 | 78.3829 | -44.4672 | -44.3802 | 71.727 | 2.3575 | -0.17853 | 0.87433 | 78.3463 | -44.4626 | -0.30212 | 0.045777 | 4.921 | -0.21515 | 0.082397 | -6.6101 | -6.6193 | -0.29755 | 0.009155 | 5.2231
1009.5781 | 122.8683 | -44.1422 | 78.3829 | 0.4218 | 0.025645 | 0.023824 | 0.010762 | 0.064361 | 0.0007629 | 0.073527 | -39.1983 | 78.4653 | -44.458 | -44.3527 | 71.6125 | 2.3849 | -0.16479 | 0.86975 | 78.3554 | -44.4397 | -0.31586 | 0.082397 | 4.9438 | -0.21057 | 0.086975 | -6.7703 | -6.7429 | -0.29755 | -0.027466 | 5.2597
1010.5781 | 122.8546 | -44.0094 | 78.4927 | 0.41417 | 0.023295 | 0.025319 | 0.0088399 | 0.064575 | 0.0052491 | 0.074595 | -38.9603 | 78.5385 | -44.3161 | -44.2062 | 71.7087 | 2.4445 | -0.20142 | 0.91553 | 78.5202 | -44.2932 | -0.3067 | 0.045776 | 5.0491 | -0.19684 | 0.086975 | -6.7841 | -6.8115 | -0.28381 | 0.027466 | 5.3558
1011.5781 | 122.7722 | -43.9362 | 78.6118 | 0.35313 | 0.026713 | 0.029378 | 0.01119 | 0.062439 | 0.0022583 | 0.073741 | -38.8824 | 78.685 | -44.2337 | -44.2062 | 71.6309 | 2.3941 | -0.07782 | 0.86975 | 78.6163 | -44.2429 | -0.29755 | 0.073243 | 5.0537 | -0.27008 | 0.036621 | -6.9809 | -6.9855 | -0.3067 | 0.004578 | 5.3513
1012.5781 | 122.7539 | -43.8217 | 78.7582 | 0.44468 | 0.027568 | 0.025533 | 0.01119 | 0.063721 | 0.0026855 | 0.074809 | -38.7131 | 78.8223 | -44.1147 | -44.0643 | 71.8689 | 2.4216 | -0.022888 | 0.9201 | 78.7811 | -44.0964 | -0.29297 | 0.064087 | 5.1086 | -0.24262 | 0.032044 | -6.8893 | -6.9122 | -0.27466 | 0.022888 | 5.4016
1013.5781 | 122.818 | -43.6661 | 78.8635 | 0.43706 | 0.026499 | 0.02831 | 0.0069173 | 0.064789 | 0.0020447 | 0.07545 | -38.4476 | 78.923 | -43.9682 | -43.9041 | 71.9101 | 2.6138 | -0.15106 | 1.0803 | 78.8452 | -43.9728 | -0.30212 | 0.05951 | 5.2185 | -0.23804 | 0.068664 | -6.9534 | -6.9351 | -0.3067 | -0.01831 | 5.5206
1014.5781 | 122.8226 | -43.634 | 78.9276 | 0.41417 | 0.028422 | 0.025747 | 0.0099081 | 0.063721 | 0.0016175 | 0.074382 | -38.324 | 79.0329 | -43.927 | -43.8721 | 71.7773 | 2.7969 | -0.10986 | 1.1215 | 78.9276 | -43.9087 | -0.29297 | 0.10529 | 5.3101 | -0.23804 | 0.036621 | -7.1503 | -7.1503 | -0.27466 | 0 | 5.603
1015.5781 | 122.7722 | -43.5471 | 79.0283 | 0.38365 | 0.028208 | 0.028951 | 0.011403 | 0.06308 | 0.0041809 | 0.075022 | -38.1775 | 79.1199 | -43.8263 | -43.7851 | 71.64 | 2.948 | -0.082397 | 1.2039 | 79.0237 | -43.8446 | -0.27924 | 0.091553 | 5.3696 | -0.23804 | 0.059509 | -7.3883 | -7.3837 | -0.29755 | -0.004577 | 5.6488
1016.5781 | 122.8592 | -43.5196 | 79.0054 | 0.017439 | 0.026499 | 0.024465 | 0.0030721 | 0.061371 | 0.0020447 | 0.07545 | -38.063 | 78.9963 | -43.7942 | -43.6752 | 71.6125 | 3.2135 | -0.054932 | 1.3733 | 79.0146 | -43.7805 | -0.27466 | -0.009155 | 5.4565 | -0.15564 | 0.10529 | -7.3929 | -7.402 | -0.26093 | 0.009155 | 5.7312
1017.5781 | 122.8546 | -43.4052 | 79.1473 | 0.45231 | 0.027781 | 0.030446 | 0.01119 | 0.064148 | 0.0014039 | 0.074382 | -37.9303 | 79.184 | -43.721 | -43.6386 | 71.3974 | 3.2776 | -0.15106 | 1.3321 | 79.1016 | -43.7164 | -0.31586 | 0.036621 | 5.4749 | -0.23346 | 0.07782 | -7.7499 | -7.7042 | -0.31128 | -0.045777 | 5.7907
1018.5781 | 122.7264 | -43.3044 | 79.2938 | 0.040327 | 0.026713 | 0.028951 | 0.010549 | 0.063721 | 0.0011901 | 0.073954 | -37.738 | 79.3259 | -43.602 | -43.5745 | 71.2463 | 3.3005 | -0.009155 | 1.2772 | 79.2755 | -43.6111 | -0.29755 | 0.032044 | 5.5664 | -0.27008 | 0.036621 | -8.0475 | -8.0292 | -0.3067 | -0.01831 | 5.864
1019.5781 | 122.7539 | -43.2129 | 79.3671 | 2.8708 | 0.030131 | 0.026815 | 0.010549 | 0.064575 | 0.0026855 | 0.074595 | -37.5412 | 79.4678 | -43.4509 | -43.5242 | 71.1136 | 3.4195 | 0 | 1.3458 | 79.3762 | -43.5379 | -0.23804 | 0.10071 | 5.6717 | -0.31128 | 0.013733 | -8.2535 | -8.2626 | -0.32501 | 0.009156 | 5.9097
1020.5781 | 122.7997 | -43.0984 | 79.4724 | 0.39891 | 0.028208 | 0.030233 | 0.010122 | 0.064575 | 0.0022583 | 0.075022 | -37.4176 | 79.5364 | -43.3914 | -43.3685 | 71.0678 | 3.6118 | -0.082397 | 1.4877 | 79.4998 | -43.396 | -0.29297 | 0.064087 | 5.6808 | -0.27008 | 0.027466 | -8.4045 | -8.432 | -0.29755 | 0.027466 | 5.9738
1021.5781 | 122.7493 | -43.0344 | 79.5547 | 0.30736 | 0.027354 | 0.026601 | 0.0088399 | 0.066498 | 0.0007629 | 0.07545 | -37.2986 | 79.6371 | -43.3182 | -43.2999 | 70.9076 | 3.7262 | -0.041199 | 1.5518 | 79.5639 | -43.3228 | -0.28381 | 0.082397 | 5.7358 | -0.2655 | 0.022888 | -8.6472 | -8.6563 | -0.28839 | 0.009155 | 6.0196
1022.5781 | 122.7676 | -42.9565 | 79.6097 | 0.45994 | 0.029063 | 0.034292 | 0.011617 | 0.063507 | 0.0031127 | 0.077586 | -37.1613 | 79.6967 | -43.2266 | -43.2449 | 70.7474 | 3.8361 | -0.027466 | 1.6022 | 79.628 | -43.2587 | -0.27008 | 0.086975 | 5.7953 | -0.28839 | 0.013733 | -8.8623 | -8.8806 | -0.30212 | 0.018311 | 6.0654
1023.5781 | 122.8226 | -42.8787 | 79.6463 | 0.45231 | 0.029704 | 0.033651 | 0.0092671 | 0.062012 | 0.0041809 | 0.077159 | -37.0285 | 79.7287 | -43.1534 | -43.1259 | 70.6558 | 4.0466 | -0.16479 | 1.767 | 79.6417 | -43.1671 | -0.27466 | 0.082398 | 5.8502 | -0.24719 | 0.041198 | -8.9905 | -8.9859 | -0.28839 | -0.004577 | 6.1249
1024.5781 | 122.85 | -42.8192 | 79.7287 | 0.45231 | 0.030558 | 0.033224 | 0.010122 | 0.064148 | 0.0041809 | 0.076091 | -36.9095 | 79.8065 | -43.0984 | -43.0939 | 70.5002 | 4.1611 | -0.11444 | 1.8677 | 79.7333 | -43.1168 | -0.27924 | 0.07782 | 5.9097 | -0.27466 | 0.022888 | -9.2285 | -9.2331 | -0.29755 | 0.004577 | 6.189
1025.5781 | 122.7356 | -42.7231 | 79.8981 | 0.44468 | 0.030131 | 0.031728 | 0.012044 | 0.067139 | 0.0073853 | 0.076091 | -36.7584 | 79.9667 | -42.9977 | -42.9703 | 70.546 | 4.4037 | -0.068665 | 1.8265 | 79.8935 | -43.0023 | -0.27466 | 0.068665 | 5.9647 | -0.24719 | 0.032043 | -9.3521 | -9.3475 | -0.27924 | -0.004577 | 6.2393
1026.5781 | 122.7036 | -42.6041 | 79.9484 | 0.39128 | 0.029063 | 0.033651 | 0.013326 | 0.064789 | 0.0026855 | 0.07844 | -36.6302 | 80.0629 | -42.9337 | -42.9474 | 70.1614 | 4.39 | 0.009155 | 1.9363 | 79.9713 | -42.9245 | -0.32959 | 0.11444 | 5.9738 | -0.34332 | -0.022888 | -9.787 | -9.8099 | -0.32044 | 0.022888 | 6.3034
1027.5781 | 122.7402 | -42.4988 | 80.1178 | 0.31499 | 0.029277 | 0.032583 | 0.013326 | 0.064575 | 0.0046081 | 0.078013 | -36.438 | 80.191 | -42.778 | -42.7917 | 70.1614 | 4.5136 | 0.004578 | 2.0966 | 80.1086 | -42.7917 | -0.27924 | 0.073242 | 6.0608 | -0.29297 | 0 | -9.9564 | -9.9472 | -0.29297 | -0.009155 | 6.34
1028.5781 | 122.7402 | -42.4347 | 80.1636 | 0.40654 | 0.033122 | 0.03536 | 0.013326 | 0.065002 | 0.0024719 | 0.077372 | -36.4426 | 80.2231 | -42.6865 | -42.7048 | 69.9783 | 4.6005 | 0.032043 | 2.1378 | 80.1956 | -42.7505 | -0.25177 | 0.059509 | 5.9921 | -0.27008 | 0.045776 | -10.1852 | -10.2173 | -0.31586 | 0.032044 | 6.2439
1029.5781 | 122.7081 | -42.4667 | 80.1315 | 0.36076 | 0.030558 | 0.032155 | 0.013326 | 0.064789 | 0.0031127 | 0.077372 | -36.2823 | 80.2139 | -42.7368 | -42.7231 | 69.6533 | 4.6646 | 0.11444 | 2.4399 | 80.1682 | -42.7505 | -0.27008 | 0.082397 | 6.1844 | -0.25635 | 0.027466 | -10.4782 | -10.5148 | -0.28381 | 0.036621 | 6.4545
1030.5781 | 122.699 | -42.5034 | 80.1086 | 0.39128 | 0.030986 | 0.031728 | 0.012471 | 0.06607 | 0.0048217 | 0.079509 | -36.2778 | 80.2002 | -42.7826 | -42.7689 | 69.429 | 4.8203 | 0.018311 | 2.2476 | 80.1407 | -42.8101 | -0.27924 | 0.091552 | 6.2256 | -0.2655 | 0.041199 | -10.6796 | -10.7117 | -0.3067 | 0.032043 | 6.5048
1031.5781 | 122.7585 | -42.453 | 80.159 | -1.7907 | 0.030131 | 0.029592 | 0.010762 | 0.067352 | 0.0033265 | 0.078654 | -36.1908 | 80.2414 | -42.7505 | -42.7277 | 69.2459 | 4.921 | 0 | 2.3804 | 80.1407 | -42.7872 | -0.29755 | 0.082397 | 6.2622 | -0.27466 | 0.059509 | -10.9131 | -10.8948 | -0.33417 | -0.018311 | 6.5598
1032.5781 | 122.731 | -42.5034 | 80.0995 | 0.23106 | 0.030772 | 0.032155 | 0.012044 | 0.06543 | 0.0035401 | 0.077159 | -36.1496 | 80.1727 | -42.8101 | -42.7872 | 68.9026 | 5.0491 | 0.059509 | 2.4445 | 80.1086 | -42.8055 | -0.3067 | 0.073242 | 6.3538 | -0.28381 | 0.018311 | -11.1969 | -11.2061 | -0.30212 | 0.009156 | 6.6605
1033.5781 | 122.6944 | -42.485 | 80.1041 | 0.26158 | 0.030986 | 0.033864 | 0.010762 | 0.065002 | 0.0033265 | 0.0778 | -36.0718 | 80.1727 | -42.7917 | -42.7643 | 68.7698 | 5.1086 | 0.041199 | 2.5681 | 80.1498 | -42.8238 | -0.3067 | 0.068664 | 6.4133 | -0.27924 | 0.05951 | -11.3342 | -11.38 | -0.33875 | 0.045776 | 6.72
1034.5781 | 122.7219 | -42.5629 | 80.0217 | 0.28447 | 0.02949 | 0.036855 | 0.012258 | 0.066925 | 0.0063171 | 0.079295 | -36.0947 | 80.1178 | -42.8558 | -42.8604 | 68.2663 | 5.2505 | 0.022888 | 2.5818 | 80.0766 | -42.8467 | -0.29297 | 0.096131 | 6.4682 | -0.29755 | -0.013733 | -11.7554 | -11.8103 | -0.28381 | 0.054932 | 6.7612
1035.5781 | 122.7036 | -42.5079 | 80.0858 | 0.23869 | 0.029277 | 0.034719 | 0.013753 | 0.065002 | 0.0039673 | 0.080577 | -35.9848 | 80.2048 | -42.7872 | -42.7826 | 68.0099 | 5.3925 | 0.064087 | 2.6093 | 80.1178 | -42.8101 | -0.27923 | 0.11902 | 6.5231 | -0.27466 | 0.027466 | -12.0758 | -12.1078 | -0.30212 | 0.032044 | 6.8024
1036.5781 | 122.7402 | -42.4438 | 80.159 | 0.24632 | 0.030345 | 0.032155 | 0.014821 | 0.064361 | 0.0058899 | 0.078868 | -35.8521 | 80.2414 | -42.7231 | -42.7231 | 67.7353 | 5.5115 | 0.036621 | 2.7466 | 80.2002 | -42.7551 | -0.27923 | 0.082397 | 6.5918 | -0.27923 | 0.032044 | -12.4237 | -12.4649 | -0.31128 | 0.041198 | 6.871
1037.5781 | 122.6944 | -42.4805 | 80.1498 | 0.26921 | 0.032054 | 0.032583 | 0.012044 | 0.066498 | 0.0031127 | 0.080577 | -35.8704 | 80.2231 | -42.7505 | -42.7643 | 67.3965 | 5.5664 | 0.059509 | 2.6917 | 80.1773 | -42.7826 | -0.27008 | 0.073242 | 6.6101 | -0.28381 | 0.018311 | -12.7533 | -12.7808 | -0.30212 | 0.027466 | 6.8802
1038.5781 | 122.7127 | -42.6819 | 79.9164 | 0.27684 | 0.029917 | 0.03301 | 0.017385 | 0.064575 | 0.0046081 | 0.079936 | -36.0077 | 80.0125 | -42.9611 | -42.9703 | 66.9113 | 5.6763 | 0.064087 | 2.7374 | 79.9622 | -42.984 | -0.27924 | 0.09613 | 6.6742 | -0.28839 | 0.013733 | -13.0051 | -13.0508 | -0.30212 | 0.045776 | 6.9534
1039.5781 | 122.7768 | -42.6636 | 79.8935 | 0.28447 | 0.030131 | 0.032369 | 0.014394 | 0.065857 | 0.0033265 | 0.080577 | -35.8887 | 80.0308 | -42.9611 | -42.9199 | 66.8427 | 5.7449 | 0.027466 | 2.7328 | 79.9438 | -42.9886 | -0.29755 | 0.13733 | 6.7749 | -0.25635 | 0.068664 | -13.0508 | -13.1012 | -0.32501 | 0.050354 | 7.0724
1040.5781 | 122.7768 | -42.8009 | 79.7791 | 0.17766 | 0.030772 | 0.033437 | 0.015676 | 0.064361 | 0.0061035 | 0.078227 | -36.0077 | 79.8431 | -43.103 | -42.9794 | 66.3757 | 5.9235 | 0.018311 | 2.6962 | 79.8523 | -43.1076 | -0.30212 | 0.064087 | 6.7932 | -0.17853 | 0.12817 | -13.4033 | -13.4766 | -0.3067 | 0.073242 | 7.0953
1041.5781 | 122.7539 | -43.1259 | 79.4815 | 0.17766 | 0.030772 | 0.031301 | 0.013967 | 0.067139 | 0.0061035 | 0.079936 | -36.232 | 79.5776 | -43.4006 | -43.3594 | 65.6387 | 6.015 | 0.032043 | 2.6871 | 79.509 | -43.4006 | -0.27466 | 0.096131 | 6.8939 | -0.23346 | 0.041199 | -13.8428 | -13.8702 | -0.27466 | 0.027466 | 7.1686
1042.5781 | 122.731 | -43.2404 | 79.3671 | 0.1624 | 0.031413 | 0.032796 | 0.01653 | 0.067566 | 0.0039673 | 0.082499 | -36.3922 | 79.4907 | -43.4692 | -43.4738 | 65.0482 | 6.2164 | 0.018311 | 2.71 | 79.422 | -43.5471 | -0.22888 | 0.1236 | 6.8481 | -0.23346 | 0.073242 | -14.3188 | -14.3738 | -0.3067 | 0.054932 | 7.077
1043.5781 | 122.7539 | -42.9428 | 79.6097 | 0.13951 | 0.028422 | 0.031087 | 0.016103 | 0.066284 | 0.0052491 | 0.082927 | -36.2183 | 79.6417 | -43.2816 | -43.2312 | 64.8651 | 6.3492 | 0.041199 | 2.8748 | 79.6509 | -43.2541 | -0.33874 | 0.032044 | 6.7245 | -0.28839 | 0.022888 | -14.7446 | -14.7858 | -0.31128 | 0.041199 | 7.0633
1044.5781 | 122.7631 | -42.9382 | 79.6417 | 0.0021796 | 0.029277 | 0.034719 | 0.015462 | 0.064575 | 0.0061035 | 0.083995 | -36.113 | 79.7562 | -43.1625 | -43.1717 | 64.5309 | 6.4865 | 0.013733 | 2.948 | 79.6829 | -43.2266 | -0.22431 | 0.11444 | 6.8253 | -0.23346 | 0.054932 | -15.1108 | -15.152 | -0.28839 | 0.041198 | 7.0496
1045.5781 | 122.7539 | -42.9474 | 79.6234 | 0.13951 | 0.027995 | 0.036855 | 0.016744 | 0.069061 | 0.0090943 | 0.08314 | -36.145 | 79.6692 | -43.2678 | -43.1488 | 64.1281 | 6.6193 | 0.004578 | 3.0167 | 79.6875 | -43.2632 | -0.32043 | 0.045776 | 6.8024 | -0.20142 | 0.11444 | -15.4953 | -15.5594 | -0.31586 | 0.064087 | 7.1228
1046.5781 | 122.7722 | -43.1351 | 79.4678 | -0.0054494 | 0.027781 | 0.028737 | 0.016958 | 0.065857 | 0.0061035 | 0.081218 | -36.2823 | 79.5547 | -43.4052 | -43.3594 | 63.5559 | 6.6925 | 0.10529 | 2.9892 | 79.5273 | -43.4052 | -0.27008 | 0.086976 | 6.8527 | -0.2243 | 0.045776 | -15.9119 | -15.9714 | -0.27008 | 0.05951 | 7.1228
1047.5781 | 122.7631 | -43.2678 | 79.3762 | 0.025068 | 0.025218 | 0.031087 | 0.015249 | 0.065643 | 0.0071717 | 0.08314 | -36.3876 | 79.4174 | -43.5104 | -43.4921 | 63.0249 | 6.7383 | 0.13733 | 2.98 | 79.4357 | -43.5196 | -0.24262 | 0.041198 | 6.8802 | -0.2243 | 0.027466 | -16.3513 | -16.4108 | -0.25177 | 0.059509 | 7.1228
1048.5781 | 122.7814 | -43.4418 | 79.1336 | -0.051226 | 0.028422 | 0.032796 | 0.016744 | 0.066498 | 0.0050353 | 0.084422 | -36.525 | 79.2068 | -43.7302 | -43.6981 | 62.4847 | 6.8298 | 0.09613 | 3.0167 | 79.1977 | -43.7622 | -0.28839 | 0.073242 | 6.9168 | -0.25635 | 0.064087 | -16.6489 | -16.713 | -0.32043 | 0.064087 | 7.2052
1049.5781 | 122.7768 | -43.689 | 78.9093 | 0.025068 | 0.028636 | 0.032369 | 0.015462 | 0.065002 | 0.0063171 | 0.084422 | -36.7264 | 78.9505 | -43.9499 | -43.9453 | 61.9446 | 6.8481 | 0.13275 | 2.98 | 78.9642 | -43.9911 | -0.26093 | 0.041198 | 6.9626 | -0.25635 | 0.045777 | -16.9647 | -17.0197 | -0.30212 | 0.054931 | 7.2235
1050.5781 | 122.7722 | -43.7942 | 78.8223 | 0.017439 | 0.030131 | 0.031942 | 0.016958 | 0.065216 | 0.0067443 | 0.08314 | -36.7493 | 78.9047 | -44.0323 | -44.0094 | 61.6425 | 6.6833 | 0.09613 | 2.8473 | 78.8452 | -44.0643 | -0.23804 | 0.082397 | 7.045 | -0.21515 | 0.054932 | -17.1799 | -17.2028 | -0.27008 | 0.022888 | 7.283
1051.5781 | 122.7768 | -44.1055 | 78.5019 | 0.017439 | 0.026927 | 0.034078 | 0.016103 | 0.065643 | 0.0080261 | 0.083781 | -37.056 | 78.5568 | -44.4031 | -44.3344 | 61.0657 | 6.7703 | 0.12817 | 2.8748 | 78.5751 | -44.4031 | -0.29755 | 0.054932 | 7.0496 | -0.22888 | 0.068664 | -17.4362 | -17.5095 | -0.29755 | 0.073242 | 7.3471
1052.5781 | 122.7402 | -44.3893 | 78.2181 | -0.10463 | 0.026499 | 0.028524 | 0.015676 | 0.064361 | 0.0067443 | 0.08549 | -37.3169 | 78.2593 | -44.6548 | -44.6365 | 60.5576 | 6.7749 | 0.13275 | 2.8244 | 78.2684 | -44.6732 | -0.2655 | 0.041198 | 7.0724 | -0.24719 | 0.036621 | -17.6605 | -17.7109 | -0.28381 | 0.050354 | 7.338
1053.5781 | 122.731 | -44.458 | 78.1403 | 0.0021796 | 0.025645 | 0.030019 | 0.013967 | 0.066498 | 0.0075989 | 0.08549 | -37.3764 | 78.1723 | -44.7464 | -44.7327 | 60.2097 | 6.8069 | 0.16022 | 2.8839 | 78.1998 | -44.751 | -0.28839 | 0.032043 | 7.0816 | -0.27466 | 0.018311 | -17.9306 | -17.9901 | -0.29297 | 0.059509 | 7.37
1054.5781 | 122.7356 | -44.6365 | 77.9617 | -0.066485 | 0.027781 | 0.025747 | 0.015035 | 0.062439 | 0.0073853 | 0.085704 | -37.5183 | 77.9572 | -44.9158 | -44.87 | 59.7885 | 6.9122 | 0.12817 | 2.8839 | 77.9938 | -44.9203 | -0.27923 | -0.004578 | 7.1182 | -0.23346 | 0.050354 | -18.1732 | -18.2053 | -0.28381 | 0.032043 | 7.3975
1055.5781 | 122.7036 | -44.7327 | 77.8748 | -0.043596 | 0.025645 | 0.026388 | 0.01354 | 0.062012 | 0.0090943 | 0.085917 | -37.7151 | 77.8885 | -44.9844 | -44.989 | 59.4223 | 6.9717 | 0.15564 | 2.8748 | 77.9251 | -44.9799 | -0.25177 | 0.013733 | 7.0175 | -0.25635 | -0.009156 | -18.4525 | -18.5028 | -0.24719 | 0.050354 | 7.2693
1056.5781 | 122.7585 | -45.0348 | 77.5543 | -0.028338 | 0.025859 | 0.029806 | 0.015676 | 0.062225 | 0.0071717 | 0.08784 | -38.031 | 77.5726 | -45.2911 | -45.2866 | 58.9096 | 7.0175 | 0.10529 | 2.8336 | 77.5909 | -45.314 | -0.25635 | 0.018311 | 7.0038 | -0.25177 | 0.027466 | -18.6447 | -18.6813 | -0.27924 | 0.036621 | 7.2601
1057.5781 | 122.7676 | -45.1767 | 77.3987 | -0.043596 | 0.024577 | 0.031728 | 0.01418 | 0.062225 | 0.0078125 | 0.086772 | -38.1409 | 77.3575 | -45.4742 | -45.4102 | 58.5251 | 7.1411 | 0.073242 | 2.8839 | 77.4353 | -45.4697 | -0.29755 | -0.041199 | 7.0358 | -0.23346 | 0.05951 | -18.8736 | -18.9102 | -0.29297 | 0.036621 | 7.3334
1058.5781 | 122.7264 | -45.4697 | 77.1011 | -0.13515 | 0.025004 | 0.026815 | 0.016103 | 0.060089 | 0.0082397 | 0.087199 | -38.4705 | 77.124 | -45.7672 | -45.7352 | 57.9987 | 7.132 | 0.13275 | 2.7924 | 77.1423 | -45.7764 | -0.29755 | 0.022888 | 6.9992 | -0.2655 | 0.041199 | -19.1025 | -19.1437 | -0.3067 | 0.041199 | 7.2968
1059.5781 | 122.7356 | -45.5658 | 77.0462 | -0.097002 | 0.025218 | 0.028951 | 0.017598 | 0.061371 | 0.0080261 | 0.08784 | -38.4384 | 76.9959 | -45.8084 | -45.7855 | 57.724 | 7.2006 | 0.12817 | 2.8427 | 77.0645 | -45.8267 | -0.24262 | -0.050354 | 7.1274 | -0.21973 | 0.041199 | -19.3222 | -19.3405 | -0.26093 | 0.01831 | 7.37
1060.5781 | 122.818 | -45.639 | 76.8951 | -0.066485 | 0.025218 | 0.027883 | 0.015462 | 0.063507 | 0.0082397 | 0.089122 | -38.475 | 76.8311 | -45.9366 | -45.7672 | 57.4585 | 7.3792 | -0.07782 | 2.9663 | 76.8448 | -45.9183 | -0.29755 | -0.064087 | 7.164 | -0.12817 | 0.15106 | -19.4366 | -19.3863 | -0.27924 | -0.050354 | 7.4615
1061.5781 | 122.818 | -45.7809 | 76.7899 | -0.11989 | 0.025645 | 0.025319 | 0.016103 | 0.060303 | 0.0075989 | 0.086558 | -38.5712 | 76.7212 | -46.0785 | -45.9686 | 57.0419 | 7.4249 | 0 | 2.9205 | 76.7807 | -46.051 | -0.29755 | -0.068665 | 7.2098 | -0.18768 | 0.082397 | -19.7479 | -19.7388 | -0.27008 | -0.009155 | 7.5073
1062.5781 | 122.8226 | -45.8496 | 76.7075 | 0.10136 | 0.02415 | 0.026815 | 0.017812 | 0.060944 | 0.0080261 | 0.089762 | -38.6124 | 76.6296 | -46.1197 | -46.0236 | 56.7398 | 7.5531 | -0.036621 | 2.9755 | 76.6754 | -46.138 | -0.27008 | -0.077819 | 7.2372 | -0.17395 | 0.11444 | -19.9677 | -19.9356 | -0.28839 | -0.032043 | 7.5073
1063.5781 | 122.8455 | -45.9457 | 76.5884 | -0.013079 | 0.025004 | 0.034505 | 0.019735 | 0.058807 | 0.0078125 | 0.088481 | -38.7085 | 76.5244 | -46.2708 | -46.1655 | 56.4194 | 7.6767 | -0.059509 | 2.9984 | 76.5656 | -46.2204 | -0.32501 | -0.064087 | 7.2372 | -0.21973 | 0.054932 | -20.1691 | -20.1462 | -0.27466 | -0.022888 | 7.5623
1064.5781 | 122.8729 | -46.0236 | 76.4877 | -0.035967 | 0.025004 | 0.025747 | 0.016317 | 0.059021 | 0.0075989 | 0.088694 | -38.7314 | 76.4603 | -46.2936 | -46.2021 | 56.1447 | 7.7637 | 0.20142 | 2.7695 | 76.506 | -46.312 | -0.27008 | -0.027466 | 7.2922 | -0.17853 | 0.10986 | -20.343 | -20.3613 | -0.28839 | 0.01831 | 7.5623
1065.5781 | 122.818 | -46.1151 | 76.4236 | -0.028338 | 0.025004 | 0.032155 | 0.018026 | 0.058594 | 0.0078125 | 0.090617 | -38.7863 | 76.3962 | -46.376 | -46.2891 | 55.9113 | 7.9147 | -0.013733 | 3.0029 | 76.4099 | -46.3943 | -0.26093 | -0.027466 | 7.3288 | -0.17395 | 0.10529 | -20.5124 | -20.4987 | -0.27924 | -0.013733 | 7.5897
1066.5781 | 122.8683 | -46.1792 | 76.3275 | 0.086103 | 0.025859 | 0.03066 | 0.018239 | 0.061584 | 0.0099487 | 0.089762 | -38.8962 | 76.2863 | -46.4996 | -46.3531 | 55.6595 | 8.0795 | -0.10071 | 3.035 | 76.2863 | -46.4905 | -0.32044 | -0.041199 | 7.283 | -0.17395 | 0.13733 | -20.668 | -20.6268 | -0.31128 | -0.041199 | 7.6035
1067.5781 | 122.85 | -46.2479 | 76.2543 | 0.13951 | 0.026927 | 0.028097 | 0.017812 | 0.059875 | 0.011231 | 0.089335 | -38.9236 | 76.2268 | -46.5363 | -46.4401 | 55.3986 | 8.194 | -0.09613 | 3.1174 | 76.236 | -46.5317 | -0.28839 | -0.027465 | 7.3242 | -0.19226 | 0.091552 | -20.8557 | -20.8374 | -0.28381 | -0.01831 | 7.6126
1068.5781 | 122.8226 | -46.2799 | 76.1948 | 0.032698 | 0.023722 | 0.026601 | 0.016317 | 0.05838 | 0.0063171 | 0.090617 | -38.9511 | 76.1719 | -46.582 | -46.4722 | 55.1697 | 8.2993 | -0.036621 | 3.1128 | 76.1902 | -46.5775 | -0.30212 | -0.022888 | 7.3288 | -0.19226 | 0.10529 | -21.0251 | -21.0205 | -0.29755 | -0.004577 | 7.6309
1069.5781 | 122.8729 | -46.3943 | 76.1353 | 0.10899 | 0.023722 | 0.022756 | 0.017171 | 0.059875 | 0.0095215 | 0.088908 | -39.0518 | 76.0666 | -46.7239 | -46.5546 | 54.9225 | 8.4961 | -0.10529 | 3.1448 | 76.0849 | -46.6507 | -0.32959 | -0.068665 | 7.3425 | -0.16022 | 0.096131 | -21.2128 | -21.1624 | -0.25635 | -0.050354 | 7.6721
1070.5781 | 122.8546 | -46.4447 | 76.062 | 0.093733 | 0.027568 | 0.029806 | 0.013967 | 0.056885 | 0.0086669 | 0.090831 | -39.0701 | 76.0162 | -46.7285 | -46.6232 | 54.8584 | 8.5693 | -0.10071 | 3.2181 | 76.0666 | -46.7011 | -0.28381 | -0.045777 | 7.3746 | -0.17853 | 0.07782 | -21.2036 | -21.2082 | -0.25635 | 0.004577 | 7.6584
1071.5781 | 122.8638 | -46.5134 | 76.0071 | 0.13188 | 0.025004 | 0.026388 | 0.017812 | 0.059875 | 0.0069581 | 0.091685 | -39.1022 | 75.9705 | -46.7926 | -46.6827 | 54.657 | 8.7387 | -0.082397 | 3.273 | 76.0162 | -46.7606 | -0.27924 | -0.036621 | 7.4112 | -0.16937 | 0.07782 | -21.3501 | -21.3593 | -0.24719 | 0.009155 | 7.6904
1072.5781 | 122.8317 | -46.5546 | 75.9384 | -0.043596 | 0.02479 | 0.027028 | 0.01653 | 0.057312 | 0.0088807 | 0.089549 | -39.1342 | 75.8926 | -46.8567 | -46.6965 | 54.5059 | 8.9081 | -0.059509 | 3.3279 | 75.9384 | -46.8384 | -0.30212 | -0.045777 | 7.4203 | -0.14191 | 0.14191 | -21.4325 | -21.4325 | -0.28381 | 0 | 7.7225
1073.5781 | 122.8317 | -46.5958 | 75.9247 | 0.17766 | 0.024577 | 0.026815 | 0.018666 | 0.059021 | 0.0084533 | 0.092112 | -39.1846 | 75.9018 | -46.8704 | -46.788 | 54.2816 | 9.0637 | -0.082397 | 3.447 | 75.9064 | -46.8475 | -0.27466 | -0.022889 | 7.4112 | -0.19226 | 0.059509 | -21.6431 | -21.6248 | -0.25177 | -0.018311 | 7.6859
1074.5781 | 122.8455 | -46.582 | 75.9567 | 0.23106 | 0.024577 | 0.03066 | 0.01653 | 0.059448 | 0.011017 | 0.091899 | -39.1663 | 75.8743 | -46.8613 | -46.7651 | 54.1626 | 9.2743 | -0.073242 | 3.4149 | 75.943 | -46.843 | -0.27924 | -0.082397 | 7.4158 | -0.18311 | 0.07782 | -21.7941 | -21.7804 | -0.26093 | -0.013733 | 7.695
1075.5781 | 122.8317 | -46.5775 | 75.9613 | 0.10899 | 0.025645 | 0.03066 | 0.016317 | 0.059235 | 0.0088807 | 0.091258 | -39.1205 | 75.8835 | -46.875 | -46.7514 | 54.071 | 9.5123 | -0.1236 | 3.4607 | 75.9201 | -46.8338 | -0.29755 | -0.07782 | 7.457 | -0.17395 | 0.082397 | -21.8903 | -21.8491 | -0.25635 | -0.041199 | 7.7545
1076.5781 | 122.8683 | -46.4905 | 75.9842 | 0.086103 | 0.023295 | 0.026174 | 0.017598 | 0.059662 | 0.010162 | 0.091899 | -39.0244 | 75.9842 | -46.8018 | -46.6782 | 54.0436 | 9.7504 | -0.10529 | 3.4836 | 75.975 | -46.756 | -0.31128 | 0 | 7.4661 | -0.18768 | 0.077819 | -21.9406 | -21.9315 | -0.2655 | -0.009155 | 7.7774
1077.5781 | 122.8271 | -46.4493 | 76.062 | 0.11662 | 0.026927 | 0.030019 | 0.018666 | 0.059662 | 0.0090943 | 0.092967 | -38.9786 | 75.9979 | -46.756 | -46.6461 | 54.007 | 9.9976 | -0.09613 | 3.5477 | 76.0345 | -46.7331 | -0.3067 | -0.064087 | 7.4707 | -0.19684 | 0.086975 | -22.0551 | -22.0276 | -0.28381 | -0.027466 | 7.7774
1078.5781 | 122.8409 | -46.463 | 76.0712 | -0.013079 | 0.02415 | 0.027028 | 0.019094 | 0.061157 | 0.01059 | 0.094676 | -38.9465 | 76.0117 | -46.756 | -46.6232 | 53.9246 | 10.2814 | -0.054932 | 3.6118 | 76.0208 | -46.7377 | -0.29297 | -0.059509 | 7.5165 | -0.16022 | 0.11444 | -22.1466 | -22.0963 | -0.27466 | -0.050354 | 7.8094
1079.5781 | 122.8821 | -46.3486 | 76.1444 | 0.025068 | 0.02714 | 0.030019 | 0.018239 | 0.060303 | 0.0084533 | 0.094249 | -38.8321 | 76.1307 | -46.6736 | -46.5134 | 53.9795 | 10.6888 | -0.059509 | 3.7125 | 76.1261 | -46.6095 | -0.32501 | -0.013733 | 7.5165 | -0.1648 | 0.09613 | -22.1649 | -22.1466 | -0.26093 | -0.01831 | 7.8415
1080.5781 | 122.8363 | -46.2067 | 76.3138 | 0.13951 | 0.025218 | 0.027028 | 0.016103 | 0.058594 | 0.011444 | 0.091258 | -38.7314 | 76.2726 | -46.5134 | -46.3623 | 54.0665 | 11.0825 | -0.082397 | 3.8635 | 76.2909 | -46.4676 | -0.3067 | -0.041199 | 7.4753 | -0.15564 | 0.10529 | -22.2473 | -22.2244 | -0.26093 | -0.022888 | 7.782
1081.5781 | 122.8592 | -46.0831 | 76.4099 | 0.13188 | 0.026072 | 0.025533 | 0.017171 | 0.060944 | 0.01059 | 0.092326 | -38.6169 | 76.4008 | -46.3577 | -46.2433 | 54.1168 | 11.4624 | -0.091553 | 3.9459 | 76.3916 | -46.344 | -0.27466 | -0.009155 | 7.4661 | -0.16022 | 0.10071 | -22.2931 | -22.2748 | -0.26093 | -0.01831 | 7.7408
1082.5781 | 122.8546 | -45.9961 | 76.4877 | 0.0098091 | 0.025431 | 0.027883 | 0.01888 | 0.059235 | 0.0067443 | 0.09318 | -38.4933 | 76.4465 | -46.3303 | -46.1655 | 54.1534 | 11.4807 | -0.041199 | 4.129 | 76.4557 | -46.2845 | -0.33417 | -0.041199 | 7.5027 | -0.16937 | 0.11902 | -22.3343 | -22.3022 | -0.28839 | -0.032044 | 7.8369
1083.5781 | 122.818 | -45.9412 | 76.5839 | 0.032698 | 0.025431 | 0.030233 | 0.017812 | 0.059448 | 0.0067443 | 0.091258 | -38.4201 | 76.5152 | -46.2341 | -46.0785 | 54.2175 | 11.8195 | -0.050354 | 4.2389 | 76.5472 | -46.1838 | -0.29297 | -0.068664 | 7.5211 | -0.13733 | 0.10529 | -22.3663 | -22.3297 | -0.24262 | -0.036621 | 7.814
1084.5781 | 122.8363 | -45.9091 | 76.5976 | 0.017439 | 0.025004 | 0.026388 | 0.015462 | 0.059448 | 0.0084533 | 0.093608 | -38.4064 | 76.5381 | -46.1884 | -46.051 | 54.2038 | 12.2131 | -0.050354 | 4.3579 | 76.561 | -46.1426 | -0.27923 | -0.059509 | 7.5027 | -0.14191 | 0.091553 | -22.3938 | -22.3572 | -0.23346 | -0.036621 | 7.782
1085.5781 | 122.7631 | -45.7993 | 76.7029 | 0.15477 | 0.02714 | 0.022756 | 0.019307 | 0.06073 | 0.0080261 | 0.09318 | -38.3469 | 76.6571 | -46.1014 | -45.9824 | 54.3686 | 12.5885 | -0.004578 | 4.4861 | 76.7029 | -46.0648 | -0.30212 | -0.045777 | 7.4524 | -0.18311 | 0.082397 | -22.3343 | -22.3343 | -0.2655 | 0 | 7.7545
1086.5781 | 122.818 | -45.6894 | 76.8127 | -0.15804 | 0.02479 | 0.025533 | 0.019307 | 0.061371 | 0.0078125 | 0.091685 | -38.2599 | 76.7487 | -46.019 | -45.8771 | 54.4739 | 12.9501 | -0.022888 | 4.5959 | 76.7761 | -45.9686 | -0.32959 | -0.064087 | 7.4295 | -0.18768 | 0.091553 | -22.3389 | -22.3022 | -0.27924 | -0.036621 | 7.7591
1087.5781 | 122.8455 | -45.6436 | 76.8631 | 0.0021796 | 0.026499 | 0.030233 | 0.018666 | 0.061584 | 0.0084533 | 0.092326 | -38.1546 | 76.8127 | -45.9274 | -45.8084 | 54.5197 | 13.2614 | -0.045776 | 4.7012 | 76.8402 | -45.9091 | -0.28381 | -0.050354 | 7.489 | -0.16479 | 0.10071 | -22.3434 | -22.3206 | -0.2655 | -0.022888 | 7.7728
1088.5781 | 122.8317 | -45.4056 | 77.1286 | 0.017439 | 0.027354 | 0.027456 | 0.018026 | 0.061371 | 0.0075989 | 0.094035 | -37.9257 | 77.092 | -45.6757 | -45.5521 | 54.9637 | 13.7421 | -0.054932 | 4.9713 | 77.0874 | -45.6573 | -0.27008 | -0.036621 | 7.4799 | -0.14648 | 0.10529 | -22.1649 | -22.1237 | -0.25177 | -0.041199 | 7.7499
1089.5781 | 122.818 | -45.5978 | 76.9272 | -0.2267 | 0.025859 | 0.030019 | 0.018453 | 0.06073 | 0.0093079 | 0.092112 | -38.1409 | 76.8585 | -45.8862 | -45.7764 | 54.4281 | 13.3987 | -0.018311 | 4.8386 | 76.8951 | -45.8313 | -0.28839 | -0.068664 | 7.457 | -0.17853 | 0.054932 | -22.4991 | -22.467 | -0.23346 | -0.032043 | 7.7454
1090.5781 | 122.7951 | -45.3918 | 77.124 | 0.91008 | 0.026499 | 0.027242 | 0.019521 | 0.061798 | 0.0093079 | 0.09318 | -37.8708 | 77.0874 | -45.7031 | -45.5658 | 54.3411 | 13.6597 | -0.022888 | 5.0491 | 77.0691 | -45.6436 | -0.31128 | -0.036621 | 7.5211 | -0.17395 | 0.07782 | -22.7829 | -22.728 | -0.25177 | -0.054931 | 7.8323
1091.5781 | 122.8043 | -45.3781 | 77.1423 | 1.1313 | 0.028208 | 0.027242 | 0.01888 | 0.06073 | 0.0088807 | 0.094035 | -37.8662 | 77.1011 | -45.7077 | -45.5429 | 54.2999 | 14.003 | -0.027466 | 5.1773 | 77.1103 | -45.6024 | -0.32959 | -0.041199 | 7.5119 | -0.16479 | 0.059509 | -22.8424 | -22.8104 | -0.2243 | -0.032043 | 7.8415
1092.5781 | 122.7585 | -45.3644 | 77.1835 | -0.066485 | 0.026286 | 0.026174 | 0.019094 | 0.059662 | 0.0075989 | 0.093608 | -37.8983 | 77.179 | -45.6482 | -45.5795 | 54.2313 | 14.241 | 0.09613 | 5.2139 | 77.1606 | -45.6253 | -0.28381 | -0.004578 | 7.4661 | -0.21515 | 0.045776 | -22.9523 | -22.9294 | -0.26093 | -0.022888 | 7.7499
1093.5781 | 122.7539 | -45.2087 | 77.3712 | -0.097002 | 0.02714 | 0.029806 | 0.020375 | 0.062225 | 0.0080261 | 0.096171 | -37.7472 | 77.3392 | -45.4971 | -45.3827 | 54.4327 | 14.6851 | 0.082397 | 5.4245 | 77.3438 | -45.433 | -0.28839 | -0.032044 | 7.4615 | -0.17395 | 0.050354 | -22.9385 | -22.9111 | -0.2243 | -0.027466 | 7.7499
1094.5781 | 122.8409 | -44.9753 | 77.5269 | -0.051226 | 0.026072 | 0.02596 | 0.019307 | 0.059021 | 0.01059 | 0.094035 | -37.5732 | 77.5131 | -45.2957 | -45.195 | 54.57 | 15.1382 | -0.009155 | 5.7587 | 77.5223 | -45.2545 | -0.32043 | -0.013732 | 7.402 | -0.21973 | 0.05951 | -22.9568 | -22.9523 | -0.27924 | -0.004577 | 7.7225
1095.5781 | 122.8226 | -44.9753 | 77.5681 | 0.0021796 | 0.027568 | 0.026601 | 0.014821 | 0.058807 | 0.011444 | 0.09553 | -37.4863 | 77.5406 | -45.2087 | -45.2087 | 54.808 | 15.5457 | -0.11902 | 5.8548 | 77.5406 | -45.1767 | -0.23346 | -0.027466 | 7.489 | -0.23346 | -0.032043 | -22.76 | -22.7325 | -0.20142 | -0.027466 | 7.7225
1096.5781 | 122.7859 | -44.8471 | 77.7054 | -0.028338 | 0.027781 | 0.031515 | 0.019735 | 0.061584 | 0.0095215 | 0.095103 | -37.4359 | 77.6596 | -45.1218 | -45.0439 | 54.8355 | 15.8386 | 0.050354 | 6.0928 | 77.6871 | -45.0943 | -0.27466 | -0.045776 | 7.4112 | -0.19684 | 0.050354 | -22.8699 | -22.8516 | -0.24719 | -0.01831 | 7.6859
1097.5781 | 122.7951 | -44.6457 | 77.9251 | 0.032698 | 0.026927 | 0.034078 | 0.019735 | 0.061371 | 0.0071717 | 0.093821 | -37.207 | 77.8931 | -44.9249 | -44.8196 | 55.0735 | 16.0584 | 0.018311 | 6.3446 | 77.8793 | -44.8929 | -0.27924 | -0.032044 | 7.4387 | -0.17395 | 0.073242 | -22.8516 | -22.8058 | -0.24719 | -0.045777 | 7.7179
1098.5781 | 122.7631 | -44.4855 | 78.0441 | -0.020708 | 0.02714 | 0.03066 | 0.019307 | 0.060516 | 0.0090943 | 0.093394 | -37.0789 | 78.0212 | -44.7693 | -44.6732 | 55.275 | 16.5253 | 0.027466 | 6.8344 | 78.0258 | -44.7647 | -0.28381 | -0.022888 | 7.4066 | -0.18768 | 0.091552 | -22.7692 | -22.7509 | -0.27923 | -0.01831 | 7.6904
1099.5781 | 122.731 | -44.339 | 78.2364 | -0.0054494 | 0.027354 | 0.026815 | 0.023793 | 0.061371 | 0.010162 | 0.092753 | -36.9415 | 78.2501 | -44.5999 | -44.577 | 55.6549 | 16.7953 | 0.1236 | 7.0267 | 78.2272 | -44.5862 | -0.26093 | 0.013733 | 7.3975 | -0.23804 | 0.009156 | -22.5815 | -22.5723 | -0.24719 | -0.009155 | 7.6584
1100.5781 | 122.7127 | -44.3115 | 78.2776 | -0.035967 | 0.027568 | 0.029592 | 0.020589 | 0.062439 | 0.0065307 | 0.093394 | -36.9095 | 78.2684 | -44.5816 | -44.5221 | 55.8838 | 17.1066 | 0.13733 | 7.2372 | 78.273 | -44.545 | -0.27008 | -0.009155 | 7.402 | -0.21057 | 0.022888 | -22.3938 | -22.3892 | -0.23346 | -0.004578 | 7.6721
1101.5781 | 122.7127 | -44.2886 | 78.2776 | -0.035967 | 0.027354 | 0.029165 | 0.018666 | 0.062866 | 0.0080261 | 0.095958 | -36.8774 | 78.2913 | -44.5404 | -44.4809 | 56.0623 | 17.3538 | 0.1236 | 7.4341 | 78.2822 | -44.5404 | -0.25177 | 0.013733 | 7.4112 | -0.19226 | 0.059509 | -22.2153 | -22.2198 | -0.25177 | 0.004578 | 7.663
1102.5781 | 122.8317 | -44.1788 | 78.3417 | -0.020708 | 0.026713 | 0.019338 | 0.017385 | 0.061157 | 0.0088807 | 0.094035 | -36.7584 | 78.3096 | -44.4992 | -44.3985 | 56.4926 | 17.7567 | -0.041199 | 7.7362 | 78.2822 | -44.4305 | -0.32043 | -0.032044 | 7.4203 | -0.21973 | 0.032043 | -21.8491 | -21.7896 | -0.25177 | -0.059509 | 7.7408
1103.5781 | 122.7768 | -44.2886 | 78.2822 | -0.020708 | 0.026713 | 0.028737 | 0.018666 | 0.061371 | 0.0082397 | 0.095317 | -36.8729 | 78.2272 | -44.5633 | -44.4763 | 56.6162 | 17.9489 | 0.045776 | 7.7225 | 78.2364 | -44.5084 | -0.27466 | -0.054932 | 7.4158 | -0.18768 | 0.032044 | -21.666 | -21.6202 | -0.21973 | -0.045777 | 7.6904
1104.5781 | 122.8271 | -44.4168 | 78.1036 | 0.017439 | 0.027354 | 0.031301 | 0.020375 | 0.059235 | 0.0084533 | 0.093821 | -37.001 | 78.067 | -44.6823 | -44.5999 | 56.7078 | 18.1732 | 0.013733 | 7.7774 | 78.0762 | -44.6823 | -0.2655 | -0.036621 | 7.4158 | -0.18311 | 0.082397 | -21.3959 | -21.3684 | -0.2655 | -0.027466 | 7.6813
1105.5781 | 122.8226 | -44.7281 | 77.7786 | 0.040327 | 0.02415 | 0.030019 | 0.017598 | 0.060516 | 0.0097351 | 0.095103 | -37.4313 | 77.7557 | -45.0073 | -44.9066 | 56.4468 | 18.2877 | -0.018311 | 7.7957 | 77.7878 | -44.989 | -0.27924 | -0.022888 | 7.2968 | -0.17853 | 0.082398 | -21.3318 | -21.3409 | -0.26093 | 0.009156 | 7.576
1106.5781 | 122.7448 | -44.9432 | 77.5955 | -0.020708 | 0.026499 | 0.025106 | 0.02123 | 0.059021 | 0.0097351 | 0.09254 | -37.5687 | 77.5681 | -45.2591 | -45.1447 | 56.2592 | 18.4113 | 0.073242 | 7.7316 | 77.5589 | -45.1996 | -0.31586 | -0.027466 | 7.3746 | -0.20142 | 0.054932 | -21.3364 | -21.2997 | -0.25635 | -0.036621 | 7.6904
1107.5781 | 122.699 | -45.1172 | 77.4445 | 0.35313 | 0.02949 | 0.032155 | 0.026571 | 0.063293 | 0.0073853 | 0.093394 | -37.7975 | 77.4536 | -45.4239 | -45.3873 | 56.0349 | 18.4387 | 0.022888 | 7.6538 | 77.4628 | -45.3918 | -0.3067 | 0.009155 | 7.3196 | -0.27008 | 0.004578 | -21.4096 | -21.4279 | -0.27466 | 0.018311 | 7.6263
1108.5781 | 122.8226 | -45.1355 | 77.3392 | 0.0021796 | 0.026713 | 0.028737 | 0.015676 | 0.061371 | 0.0084533 | 0.09254 | -37.7563 | 77.3209 | -45.4468 | -45.3323 | 56.1447 | 18.75 | -0.050354 | 8.0383 | 77.3254 | -45.4102 | -0.31128 | -0.01831 | 7.3791 | -0.19684 | 0.07782 | -21.1945 | -21.1807 | -0.27466 | -0.013733 | 7.6904
1109.5781 | 122.85 | -45.2408 | 77.2568 | 0.078474 | 0.023936 | 0.023183 | 0.016958 | 0.061371 | 0.0084533 | 0.09318 | -37.8479 | 77.2339 | -45.5429 | -45.4147 | 56.044 | 18.9148 | -0.082397 | 8.0795 | 77.2522 | -45.4926 | -0.30212 | -0.022888 | 7.3929 | -0.17395 | 0.07782 | -21.2128 | -21.2082 | -0.25177 | -0.004578 | 7.695
1110.5781 | 122.8271 | -45.3506 | 77.1378 | -0.081743 | 0.025218 | 0.02831 | 0.017171 | 0.059662 | 0.0065307 | 0.093821 | -37.944 | 77.1286 | -45.6482 | -45.5383 | 56.044 | 19.0384 | -0.31128 | 7.933 | 77.0737 | -45.6345 | -0.29755 | -0.009155 | 7.4066 | -0.18768 | 0.09613 | -21.0938 | -21.0297 | -0.28381 | -0.064087 | 7.7042
1111.5781 | 122.8455 | -45.4971 | 76.9959 | 0.040327 | 0.027568 | 0.026815 | 0.017598 | 0.060944 | 0.011231 | 0.09318 | -38.0722 | 76.9455 | -45.813 | -45.6985 | 55.838 | 19.0247 | -0.045776 | 8.1757 | 76.9501 | -45.7809 | -0.31586 | -0.050354 | 7.4249 | -0.20142 | 0.082398 | -21.1578 | -21.1121 | -0.28381 | -0.045777 | 7.7408
1112.5781 | 122.8226 | -45.8038 | 76.7166 | -0.013079 | 0.027568 | 0.023824 | 0.019948 | 0.06073 | 0.0088807 | 0.09318 | -38.324 | 76.6937 | -46.0968 | -46.019 | 55.4901 | 19.2123 | -0.041199 | 8.1345 | 76.68 | -46.0556 | -0.29297 | -0.022888 | 7.4799 | -0.21515 | 0.036621 | -21.2265 | -21.1899 | -0.25177 | -0.036621 | 7.7728
1113.5781 | 122.8592 | -45.9045 | 76.6113 | -0.051226 | 0.026927 | 0.027669 | 0.016958 | 0.061584 | 0.0080261 | 0.092753 | -38.4567 | 76.5701 | -46.1792 | -46.0327 | 55.4993 | 19.3405 | -0.054932 | 8.2855 | 76.6022 | -46.1517 | -0.27466 | -0.041199 | 7.4478 | -0.12817 | 0.11902 | -21.1121 | -21.1029 | -0.24719 | -0.009155 | 7.7225
1114.5781 | 122.8546 | -45.8496 | 76.6571 | 0.047956 | 0.025431 | 0.024038 | 0.015462 | 0.061798 | 0.0078125 | 0.090617 | -38.4613 | 76.593 | -46.1563 | -46.019 | 55.7007 | 19.4916 | -0.059509 | 8.3176 | 76.6205 | -46.1151 | -0.3067 | -0.064086 | 7.3883 | -0.16937 | 0.09613 | -20.9564 | -20.9198 | -0.2655 | -0.036621 | 7.695
1115.5781 | 122.8226 | -46.0052 | 76.5106 | 0.18529 | 0.024577 | 0.025533 | 0.01653 | 0.061371 | 0.0095215 | 0.092753 | -38.6261 | 76.474 | -46.2845 | -46.2112 | 55.4901 | 19.5282 | -0.064087 | 8.2535 | 76.4969 | -46.2524 | -0.27924 | -0.036621 | 7.3791 | -0.20599 | 0.041198 | -21.0205 | -21.0068 | -0.24719 | -0.013733 | 7.6584
1116.5781 | 122.7814 | -46.2387 | 76.2909 | 0.040327 | 0.026927 | 0.029165 | 0.015249 | 0.058594 | 0.01059 | 0.093608 | -38.8962 | 76.2131 | -46.5546 | -46.4676 | 55.22 | 19.5419 | -0.050354 | 8.1345 | 76.2451 | -46.4905 | -0.31586 | -0.07782 | 7.3425 | -0.22888 | 0.022889 | -21.0709 | -21.0251 | -0.25177 | -0.045777 | 7.6584
1117.5781 | 122.7951 | -46.3303 | 76.1719 | 0.1624 | 0.026499 | 0.024251 | 0.013967 | 0.060089 | 0.0088807 | 0.09254 | -38.9648 | 76.1353 | -46.6507 | -46.5408 | 55.1056 | 19.6838 | -0.050354 | 8.194 | 76.1398 | -46.6141 | -0.32044 | -0.036621 | 7.3654 | -0.21057 | 0.073242 | -21.0663 | -21.0342 | -0.28381 | -0.032043 | 7.6859
1118.5781 | 122.7905 | -46.3257 | 76.2131 | 0.33787 | 0.025645 | 0.026174 | 0.014394 | 0.058594 | 0.011231 | 0.092967 | -38.9648 | 76.1215 | -46.6232 | -46.5317 | 55.0507 | 19.7708 | -0.064087 | 8.2855 | 76.1765 | -46.5775 | -0.29755 | -0.091553 | 7.3608 | -0.20599 | 0.045777 | -21.1624 | -21.1258 | -0.25177 | -0.036621 | 7.6584
1119.5781 | 122.7951 | -46.3577 | 76.1719 | 0.20054 | 0.027781 | 0.027669 | 0.014394 | 0.060516 | 0.011017 | 0.093821 | -38.9832 | 76.1353 | -46.6507 | -46.5683 | 54.9683 | 19.812 | -0.054932 | 8.3817 | 76.1261 | -46.6324 | -0.29297 | -0.036621 | 7.3746 | -0.21057 | 0.064087 | -21.2036 | -21.1578 | -0.27466 | -0.045776 | 7.6675
1120.5781 | 122.8043 | -46.3989 | 76.149 | 0.18529 | 0.026286 | 0.026174 | 0.014394 | 0.059021 | 0.0082397 | 0.090403 | -39.0198 | 76.0941 | -46.669 | -46.6003 | 54.895 | 19.8761 | -0.073242 | 8.4778 | 76.0941 | -46.6599 | -0.27008 | -0.054932 | 7.3792 | -0.20142 | 0.059509 | -21.254 | -21.199 | -0.26093 | -0.054932 | 7.6492
1121.5781 | 122.7722 | -46.55 | 75.9796 | 0.70408 | 0.025859 | 0.025319 | 0.01653 | 0.060303 | 0.0093079 | 0.090403 | -39.1525 | 75.9247 | -46.843 | -46.7514 | 54.6707 | 19.9631 | -0.045776 | 8.4595 | 75.9567 | -46.8018 | -0.29297 | -0.054931 | 7.3975 | -0.20142 | 0.050354 | -21.3089 | -21.286 | -0.25177 | -0.022888 | 7.6904
1122.5781 | 122.8088 | -46.6003 | 75.9155 | 0.2921 | 0.029277 | 0.026815 | 0.015889 | 0.057953 | 0.0097351 | 0.091258 | -39.1937 | 75.8926 | -46.9116 | -46.8201 | 54.6066 | 20.0638 | -0.10986 | 8.4732 | 75.8514 | -46.8796 | -0.31128 | -0.022888 | 7.4066 | -0.21973 | 0.05951 | -21.3089 | -21.2448 | -0.27924 | -0.064087 | 7.7179
1123.5781 | 122.7768 | -46.7194 | 75.7965 | 0.33024 | 0.027568 | 0.029592 | 0.01418 | 0.059448 | 0.0090943 | 0.09254 | -39.3402 | 75.7599 | -47.0032 | -46.962 | 54.4556 | 20.0455 | -0.07782 | 8.4824 | 75.769 | -47.0032 | -0.28381 | -0.036621 | 7.3792 | -0.24262 | 0.041199 | -21.3409 | -21.3135 | -0.28381 | -0.027466 | 7.663
1124.5781 | 122.8043 | -46.9116 | 75.6134 | 0.36076 | 0.026927 | 0.026174 | 0.015249 | 0.059235 | 0.011871 | 0.091471 | -39.5233 | 75.5905 | -47.1909 | -47.113 | 54.3137 | 20.1279 | -0.091553 | 8.3862 | 75.5859 | -47.1588 | -0.27924 | -0.022888 | 7.3883 | -0.20142 | 0.045776 | -21.2997 | -21.2723 | -0.24719 | -0.027466 | 7.6675
1125.5781 | 122.7676 | -47.0123 | 75.4761 | 0.36076 | 0.025645 | 0.023397 | 0.014608 | 0.060516 | 0.010803 | 0.091044 | -39.6469 | 75.4623 | -47.3145 | -47.2549 | 54.1077 | 20.1553 | -0.12817 | 8.3359 | 75.4532 | -47.319 | -0.30212 | -0.013733 | 7.3654 | -0.24262 | 0.064087 | -21.3684 | -21.3455 | -0.3067 | -0.022888 | 7.6675
1126.5781 | 122.7814 | -47.1817 | 75.3296 | 0.25395 | 0.024577 | 0.026815 | 0.015889 | 0.057312 | 0.0099487 | 0.090617 | -39.8026 | 75.2747 | -47.4792 | -47.4243 | 53.8925 | 20.1782 | -0.073242 | 8.3908 | 75.2701 | -47.4701 | -0.29755 | -0.054932 | 7.3792 | -0.24261 | 0.045777 | -21.4371 | -21.3776 | -0.28839 | -0.059509 | 7.6767
1127.5781 | 122.7951 | -47.319 | 75.1968 | 0.33787 | 0.027568 | 0.028524 | 0.015249 | 0.059448 | 0.011231 | 0.092753 | -39.9261 | 75.174 | -47.5891 | -47.5342 | 53.7735 | 20.2423 | -0.091553 | 8.3588 | 75.1694 | -47.5662 | -0.27008 | -0.022888 | 7.3929 | -0.21515 | 0.032043 | -21.4233 | -21.3959 | -0.24719 | -0.027465 | 7.663
1128.5781 | 122.7676 | -47.3557 | 75.1465 | 0.36076 | 0.028849 | 0.028524 | 0.015889 | 0.059448 | 0.0084533 | 0.089335 | -39.9124 | 75.1282 | -47.6349 | -47.5662 | 53.7415 | 20.4987 | -0.13275 | 8.4091 | 75.1053 | -47.6624 | -0.27924 | -0.01831 | 7.4432 | -0.21057 | 0.096131 | -21.405 | -21.3638 | -0.3067 | -0.041198 | 7.7225
1129.5781 | 122.8409 | -47.6715 | 74.7894 | 0.42943 | 0.028636 | 0.030446 | 0.019948 | 0.062439 | 0.01059 | 0.087626 | -40.1733 | 74.7986 | -47.9599 | -47.7356 | 53.4439 | 20.3613 | -0.2243 | 8.2993 | 74.7391 | -47.9599 | -0.28839 | 0.009155 | 7.4982 | -0.064087 | 0.2243 | -21.3455 | -21.2952 | -0.28839 | -0.050354 | 7.7866
1130.5781 | 122.7859 | -48.1613 | 74.3179 | 0.36839 | 0.02714 | 0.02831 | 0.017171 | 0.062652 | 0.010376 | 0.092326 | -40.6494 | 74.3271 | -48.4451 | -48.3261 | 52.8534 | 20.2286 | -0.1831 | 7.988 | 74.2905 | -48.436 | -0.28381 | 0.009155 | 7.5119 | -0.16479 | 0.10986 | -21.4645 | -21.4371 | -0.27466 | -0.027466 | 7.7957
1131.5781 | 122.8043 | -48.2895 | 74.1852 | 0.38365 | 0.028208 | 0.031301 | 0.015889 | 0.062225 | 0.011231 | 0.091258 | -40.8554 | 74.1531 | -48.6465 | -48.4726 | 52.6978 | 20.2698 | -0.17853 | 7.9834 | 74.144 | -48.5779 | -0.35706 | -0.032044 | 7.4341 | -0.1831 | 0.10529 | -21.4874 | -21.4462 | -0.28839 | -0.041199 | 7.7911
1132.5781 | 122.8455 | -48.5779 | 73.938 | 0.41417 | 0.029704 | 0.035787 | 0.019948 | 0.060303 | 0.0095215 | 0.089976 | -41.0385 | 73.938 | -48.8342 | -48.7152 | 52.4231 | 20.6131 | -0.21973 | 7.869 | 73.9105 | -48.8251 | -0.25635 | 0 | 7.5394 | -0.13733 | 0.10986 | -21.5149 | -21.4874 | -0.24719 | -0.027466 | 7.7957
1133.5781 | 122.8271 | -48.6282 | 73.8235 | 0.36076 | 0.028208 | 0.026815 | 0.019307 | 0.062225 | 0.012085 | 0.088481 | -41.1896 | 73.8693 | -48.9258 | -48.8068 | 52.3041 | 20.5627 | -0.18768 | 7.8369 | 73.8144 | -48.9212 | -0.29755 | 0.045777 | 7.4387 | -0.17853 | 0.11444 | -21.5195 | -21.5103 | -0.29297 | -0.009155 | 7.7362
1134.5781 | 122.8867 | -48.967 | 73.4756 | 0.35313 | 0.028422 | 0.029592 | 0.019521 | 0.061584 | 0.010162 | 0.090831 | -41.5283 | 73.5764 | -49.2599 | -49.1501 | 51.9745 | 20.5215 | -0.20142 | 7.7087 | 73.5077 | -49.2233 | -0.29297 | 0.10071 | 7.4387 | -0.1831 | 0.073243 | -21.5012 | -21.5332 | -0.25635 | 0.032043 | 7.7316
1135.5781 | 122.7448 | -48.7885 | 73.7274 | 0.4218 | 0.029704 | 0.029806 | 0.020589 | 0.061371 | 0.0069581 | 0.090831 | -41.4276 | 73.8052 | -49.0906 | -49.0082 | 52.0157 | 20.7779 | -0.1236 | 7.9742 | 73.7366 | -49.0768 | -0.30212 | 0.07782 | 7.3608 | -0.21973 | 0.068664 | -21.7117 | -21.7209 | -0.28839 | 0.009155 | 7.663
1136.5781 | 122.7264 | -48.5229 | 73.9746 | 0.42943 | 0.029277 | 0.028524 | 0.020162 | 0.064575 | 0.0090943 | 0.088267 | -41.2674 | 74.0524 | -48.8571 | -48.7976 | 52.2079 | 21.0663 | -0.041199 | 8.2626 | 73.97 | -48.8663 | -0.33417 | 0.07782 | 7.2556 | -0.27466 | 0.068665 | -21.7667 | -21.7621 | -0.34332 | -0.004577 | 7.5897
1137.5781 | 122.7905 | -48.7427 | 73.7869 | 0.4218 | 0.030772 | 0.028737 | 0.019521 | 0.063293 | 0.0099487 | 0.089549 | -41.5604 | 73.8556 | -49.0219 | -48.9532 | 51.9928 | 21.1121 | -0.11444 | 8.1802 | 73.764 | -49.0082 | -0.27924 | 0.068665 | 7.1823 | -0.21057 | 0.054932 | -21.7941 | -21.7712 | -0.2655 | -0.022888 | 7.4615
1138.5781 | 122.7448 | -48.9029 | 73.6267 | 0.30736 | 0.030558 | 0.029592 | 0.020162 | 0.064789 | 0.0099487 | 0.091258 | -41.6336 | 73.7228 | -49.173 | -49.1455 | 51.7776 | 21.0709 | -0.082397 | 8.0338 | 73.6313 | -49.2004 | -0.27008 | 0.09613 | 7.2693 | -0.24262 | 0.054931 | -21.8491 | -21.8536 | -0.29755 | 0.004578 | 7.5394
1139.5781 | 122.7219 | -48.5504 | 73.9929 | -0.34877 | 0.02949 | 0.030019 | 0.018239 | 0.063293 | 0.011444 | 0.089976 | -41.3544 | 74.1028 | -48.8205 | -48.7976 | 52.0111 | 21.3501 | -0.018311 | 8.7296 | 74.0067 | -48.8571 | -0.27008 | 0.10986 | 7.196 | -0.24719 | 0.05951 | -21.9818 | -21.9955 | -0.3067 | 0.013733 | 7.4661
1140.5781 | 122.6944 | -48.6053 | 73.9563 | 0.38365 | 0.029917 | 0.031515 | 0.020803 | 0.067779 | 0.0082397 | 0.090617 | -41.4047 | 74.0479 | -48.912 | -48.7198 | 51.9562 | 21.3593 | 0.004578 | 8.8531 | 73.9883 | -48.8892 | -0.3067 | 0.091553 | 7.2006 | -0.11444 | 0.16937 | -22.0001 | -22.0322 | -0.28381 | 0.032043 | 7.5073
1141.5781 | 122.7219 | -48.8159 | 73.732 | 0.45994 | 0.029704 | 0.030874 | 0.018026 | 0.063934 | 0.0090943 | 0.091685 | -41.6656 | 73.8235 | -49.0814 | -49.0585 | 51.6357 | 21.3409 | -0.050354 | 8.757 | 73.7412 | -49.1272 | -0.2655 | 0.091552 | 7.1503 | -0.24261 | 0.068664 | -22.0963 | -22.1054 | -0.31128 | 0.009155 | 7.4158
1142.5781 | 122.6852 | -49.054 | 73.5718 | 0.31499 | 0.031413 | 0.02831 | 0.019735 | 0.065216 | 0.01059 | 0.090403 | -41.9037 | 73.6496 | -49.3011 | -49.3011 | 51.3336 | 21.199 | 0.041199 | 8.5648 | 73.5718 | -49.3011 | -0.24719 | 0.07782 | 7.1503 | -0.24719 | 0 | -22.2382 | -22.2382 | -0.24719 | 0 | 7.3975
1143.5781 | 122.6761 | -49.1776 | 73.3566 | 0.27684 | 0.030558 | 0.031087 | 0.017171 | 0.065216 | 0.0071717 | 0.08784 | -42.0776 | 73.4619 | -49.4568 | -49.4568 | 51.1597 | 21.254 | 0.050354 | 8.5373 | 73.3887 | -49.4888 | -0.27924 | 0.10529 | 7.0999 | -0.27924 | 0.032044 | -22.197 | -22.229 | -0.31128 | 0.032044 | 7.3791
1144.5781 | 122.699 | -49.1913 | 73.3521 | 0.3455 | 0.033763 | 0.030019 | 0.016958 | 0.067566 | 0.0073853 | 0.09254 | -42.128 | 73.4528 | -49.5026 | -49.4751 | 51.0727 | 21.3043 | 0.022888 | 8.5785 | 73.3704 | -49.5071 | -0.31128 | 0.10071 | 7.0633 | -0.28381 | 0.032043 | -22.2794 | -22.2977 | -0.31586 | 0.01831 | 7.3746
1145.5781 | 122.699 | -49.3195 | 73.2559 | 0.29973 | 0.031199 | 0.030233 | 0.019094 | 0.065002 | 0.0099487 | 0.089762 | -42.2104 | 73.3749 | -49.5941 | -49.585 | 50.9033 | 21.254 | 0.064087 | 8.5419 | 73.2742 | -49.6033 | -0.27466 | 0.11902 | 7.1091 | -0.2655 | 0.01831 | -22.3526 | -22.3709 | -0.28381 | 0.018311 | 7.3837
1146.5781 | 122.6852 | -49.3515 | 73.201 | 0.2921 | 0.030345 | 0.035573 | 0.01888 | 0.064789 | 0.0084533 | 0.089762 | -42.2882 | 73.3109 | -49.649 | -49.6307 | 50.8438 | 21.4005 | 0.050354 | 8.5785 | 73.2468 | -49.6307 | -0.29755 | 0.10986 | 7.0633 | -0.27924 | 0 | -22.3572 | -22.403 | -0.27924 | 0.045776 | 7.3608
1147.5781 | 122.7264 | -49.4934 | 73.0545 | 0.2921 | 0.030131 | 0.028524 | 0.016317 | 0.066284 | 0.010162 | 0.090831 | -42.4759 | 73.1689 | -49.7681 | -49.7635 | 50.7202 | 21.3821 | 0.009155 | 8.4915 | 73.1186 | -49.7864 | -0.27466 | 0.11444 | 7.0175 | -0.27008 | 0.022888 | -22.3343 | -22.3984 | -0.29297 | 0.064087 | 7.2922
1148.5781 | 122.6669 | -49.585 | 72.9996 | 0.27684 | 0.030345 | 0.030874 | 0.018666 | 0.066925 | 0.0095215 | 0.092112 | -42.5446 | 73.1094 | -49.855 | -49.8596 | 50.5783 | 21.3364 | 0.041199 | 8.4457 | 73.0408 | -49.8734 | -0.27008 | 0.10986 | 7.0404 | -0.27466 | 0.013733 | -22.4213 | -22.4625 | -0.28839 | 0.041198 | 7.3105
1149.5781 | 122.7264 | -49.5941 | 72.9538 | 0.18529 | 0.030345 | 0.036001 | 0.018666 | 0.065643 | 0.0099487 | 0.090617 | -42.5171 | 73.0682 | -49.823 | -49.8276 | 50.5875 | 21.3547 | 0.027466 | 8.5236 | 72.9996 | -49.91 | -0.22888 | 0.11444 | 7.077 | -0.23346 | 0.082397 | -22.3663 | -22.4121 | -0.31586 | 0.045777 | 7.3059
1150.5781 | 122.7539 | -49.6994 | 72.8394 | 0.1624 | 0.028422 | 0.031087 | 0.019094 | 0.066284 | 0.0069581 | 0.089762 | -42.6132 | 72.9675 | -49.9512 | -49.9283 | 50.4639 | 21.3638 | 0.032043 | 8.5007 | 72.8989 | -50.0015 | -0.25177 | 0.12817 | 7.0862 | -0.22888 | 0.073242 | -22.3755 | -22.435 | -0.30212 | 0.05951 | 7.338
1151.5781 | 122.7081 | -49.855 | 72.7112 | 0.22343 | 0.030131 | 0.031301 | 0.019307 | 0.066925 | 0.0099487 | 0.090617 | -42.7872 | 72.7982 | -50.1297 | -50.116 | 50.3082 | 21.2402 | 0.036621 | 8.3313 | 72.7524 | -50.1526 | -0.27466 | 0.086975 | 7.0679 | -0.26093 | 0.036621 | -22.403 | -22.4442 | -0.29755 | 0.041198 | 7.3425
1152.5781 | 122.7264 | -49.8367 | 72.7158 | 0.17766 | 0.029917 | 0.032155 | 0.018453 | 0.066498 | 0.0088807 | 0.089549 | -42.7643 | 72.8439 | -50.1022 | -50.0977 | 50.3082 | 21.3226 | 0 | 8.3679 | 72.7432 | -50.1343 | -0.2655 | 0.12817 | 7.0724 | -0.26093 | 0.036621 | -22.4075 | -22.435 | -0.29755 | 0.027466 | 7.338
1153.5781 | 122.7036 | -49.9466 | 72.5922 | 0.2158 | 0.029917 | 0.033224 | 0.017598 | 0.065216 | 0.010162 | 0.088481 | -42.8787 | 72.7203 | -50.2167 | -50.1846 | 50.1663 | 21.254 | 0.022888 | 8.3679 | 72.6334 | -50.2579 | -0.27008 | 0.12817 | 7.0679 | -0.23804 | 0.073243 | -22.4258 | -22.467 | -0.31128 | 0.041199 | 7.338
1154.5781 | 122.6852 | -49.9374 | 72.6471 | 0.24632 | 0.02949 | 0.030019 | 0.019307 | 0.066711 | 0.0097351 | 0.089122 | -42.9016 | 72.7203 | -50.1846 | -50.1892 | 50.1663 | 21.3089 | 0.041199 | 8.3862 | 72.6654 | -50.2396 | -0.24719 | 0.073242 | 7.0358 | -0.25177 | 0.050354 | -22.4808 | -22.4991 | -0.30212 | 0.01831 | 7.283
1155.5781 | 122.7264 | -50.0061 | 72.5555 | 0.19291 | 0.032054 | 0.029806 | 0.018666 | 0.064789 | 0.0093079 | 0.089549 | -42.9565 | 72.6379 | -50.267 | -50.2396 | 50.1251 | 21.3776 | 0.032043 | 8.4091 | 72.583 | -50.3265 | -0.26093 | 0.082397 | 7.0496 | -0.23346 | 0.086975 | -22.4304 | -22.4579 | -0.32043 | 0.027466 | 7.3105
1156.5781 | 122.7219 | -50.0839 | 72.4731 | 0.093733 | 0.028849 | 0.02831 | 0.019948 | 0.066498 | 0.0097351 | 0.09019 | -43.0344 | 72.5555 | -50.3769 | -50.3082 | 50.0977 | 21.3089 | 0.032043 | 8.345 | 72.5143 | -50.4044 | -0.29297 | 0.082397 | 7.0496 | -0.22431 | 0.09613 | -22.3755 | -22.4167 | -0.32044 | 0.041198 | 7.3425
1157.5781 | 122.7585 | -50.1846 | 72.3404 | 0.13951 | 0.029277 | 0.032583 | 0.018453 | 0.066498 | 0.0099487 | 0.088908 | -43.1442 | 72.464 | -50.473 | -50.4089 | 50.061 | 21.2997 | 0.050354 | 8.2718 | 72.4182 | -50.5051 | -0.28839 | 0.1236 | 7.0404 | -0.2243 | 0.09613 | -22.2794 | -22.3572 | -0.32043 | 0.07782 | 7.3288
1158.5781 | 122.7448 | -50.2441 | 72.3038 | 0.10136 | 0.02949 | 0.032583 | 0.019948 | 0.066498 | 0.011444 | 0.089549 | -43.2129 | 72.3907 | -50.5051 | -50.4181 | 50.148 | 21.4371 | 0.027466 | 8.2764 | 72.3862 | -50.5234 | -0.26093 | 0.086975 | 7.0312 | -0.17395 | 0.10529 | -22.1558 | -22.2382 | -0.27923 | 0.082397 | 7.2922
1159.5781 | 122.731 | -50.7019 | 71.8781 | 0.11662 | 0.027781 | 0.028524 | 0.018026 | 0.063934 | 0.0099487 | 0.088908 | -43.6295 | 71.965 | -50.9583 | -50.885 | 49.6994 | 21.3181 | 0.032043 | 7.8552 | 71.933 | -50.972 | -0.25635 | 0.086975 | 7.0724 | -0.18311 | 0.086975 | -22.1786 | -22.2336 | -0.27008 | 0.054931 | 7.3288
1160.5781 | 122.7768 | -50.5463 | 72.0383 | 0.086103 | 0.027995 | 0.033224 | 0.017171 | 0.064789 | 0.0097351 | 0.089549 | -43.5059 | 72.0886 | -50.8301 | -50.7477 | 50.0153 | 21.8445 | 0.059509 | 8.0383 | 72.0749 | -50.8347 | -0.28381 | 0.050354 | 7.0404 | -0.20142 | 0.086975 | -22.023 | -22.0596 | -0.28839 | 0.036621 | 7.3242
1161.5781 | 122.7448 | -50.5188 | 72.0566 | 0.1624 | 0.028422 | 0.031942 | 0.021657 | 0.06842 | 0.0071717 | 0.086344 | -43.4967 | 72.1207 | -50.8255 | -50.7019 | 50.0519 | 21.5286 | 0.027466 | 8.0246 | 72.1161 | -50.8163 | -0.3067 | 0.064087 | 7.0221 | -0.1831 | 0.11444 | -22.0047 | -22.0642 | -0.29755 | 0.059509 | 7.3288
1162.5781 | 122.6898 | -50.5417 | 72.052 | 0.093733 | 0.030558 | 0.033437 | 0.017171 | 0.067779 | 0.0071717 | 0.089335 | -43.5837 | 72.0566 | -50.885 | -50.7889 | 49.9374 | 21.6522 | 0.018311 | 7.9834 | 72.0383 | -50.8987 | -0.34332 | 0.004578 | 6.958 | -0.24719 | 0.10986 | -22.1146 | -22.1008 | -0.35706 | -0.013733 | 7.3013
1163.5781 | 122.7539 | -50.6607 | 71.9101 | -0.0054494 | 0.027354 | 0.029165 | 0.018026 | 0.065857 | 0.0097351 | 0.089549 | -43.6844 | 71.9742 | -50.9583 | -50.885 | 49.8688 | 21.6522 | 0.10529 | 8.0521 | 71.9559 | -50.9674 | -0.29755 | 0.064087 | 6.9763 | -0.2243 | 0.082397 | -22.0413 | -22.0871 | -0.3067 | 0.045777 | 7.2739
1164.5781 | 122.7173 | -50.798 | 71.7819 | -0.0054494 | 0.029063 | 0.027242 | 0.019307 | 0.066284 | 0.0078125 | 0.090617 | -43.8766 | 71.8414 | -51.0956 | -51.0406 | 49.7086 | 21.6431 | 0.11444 | 7.8323 | 71.8369 | -51.1276 | -0.29755 | 0.05951 | 6.9214 | -0.24261 | 0.086976 | -22.0734 | -22.1283 | -0.32959 | 0.054932 | 7.2189
1165.5781 | 122.7631 | -50.8255 | 71.7361 | 0.025068 | 0.028849 | 0.03066 | 0.017171 | 0.064575 | 0.0071717 | 0.088908 | -43.8583 | 71.7957 | -51.1139 | -51.0223 | 49.704 | 21.7209 | 0.086975 | 7.8415 | 71.8048 | -51.1276 | -0.28839 | 0.059509 | 6.9672 | -0.19684 | 0.10529 | -22.0322 | -22.1008 | -0.30213 | 0.068665 | 7.2556
1166.5781 | 122.7356 | -50.798 | 71.7636 | 0.047956 | 0.027995 | 0.029165 | 0.018239 | 0.062866 | 0.0078125 | 0.088267 | -43.8812 | 71.8094 | -51.0956 | -51.0406 | 49.7086 | 21.7163 | 0.10529 | 7.7957 | 71.814 | -51.1276 | -0.29755 | 0.045776 | 6.9168 | -0.24261 | 0.086976 | -22.0551 | -22.1054 | -0.32959 | 0.050354 | 7.2144
1167.5781 | 122.7081 | -50.8759 | 71.6812 | 0.0098091 | 0.028208 | 0.027028 | 0.016958 | 0.064148 | 0.0088807 | 0.086985 | -43.9957 | 71.7178 | -51.1826 | -51.1276 | 49.5895 | 21.7896 | 0.13275 | 7.7087 | 71.7545 | -51.1917 | -0.3067 | 0.036621 | 6.8802 | -0.25177 | 0.064086 | -22.0917 | -22.1649 | -0.31586 | 0.073243 | 7.1869
1168.5781 | 122.7585 | -50.9445 | 71.6125 | 0.0098091 | 0.028422 | 0.027669 | 0.016744 | 0.064148 | 0.0090943 | 0.089122 | -44.0643 | 71.6629 | -51.2329 | -51.1688 | 49.5712 | 21.8628 | 0.086975 | 7.695 | 71.6629 | -51.2558 | -0.28839 | 0.050354 | 6.8802 | -0.2243 | 0.086975 | -22.0413 | -22.0917 | -0.31128 | 0.050354 | 7.1686
1169.5781 | 122.7219 | -50.9811 | 71.6217 | 0.0098091 | 0.027995 | 0.027669 | 0.01418 | 0.065857 | 0.0086669 | 0.088481 | -44.0781 | 71.6858 | -51.2192 | -51.1826 | 49.5667 | 21.9635 | 0.1236 | 7.7133 | 71.6904 | -51.2466 | -0.23804 | 0.064087 | 6.9031 | -0.20142 | 0.064087 | -22.0551 | -22.1237 | -0.2655 | 0.068665 | 7.1411
1170.5781 | 122.6944 | -50.9537 | 71.608 | -0.058855 | 0.027568 | 0.027242 | 0.01418 | 0.063934 | 0.011017 | 0.088481 | -44.1422 | 71.6675 | -51.2466 | -51.2375 | 49.5529 | 22.0505 | 0.17395 | 7.6767 | 71.6721 | -51.2604 | -0.29297 | 0.059509 | 6.8115 | -0.28381 | 0.022888 | -22.0551 | -22.1191 | -0.3067 | 0.064087 | 7.1045
1171.5781 | 122.7219 | -50.9583 | 71.64 | -0.11226 | 0.023936 | 0.027883 | 0.01418 | 0.063721 | 0.0075989 | 0.089549 | -44.0872 | 71.6721 | -51.2329 | -51.1917 | 49.6353 | 22.2885 | 0.14191 | 7.7728 | 71.6995 | -51.21 | -0.27466 | 0.032043 | 6.871 | -0.23346 | 0.018311 | -22.0047 | -22.0642 | -0.25177 | 0.059509 | 7.1457
1172.5781 | 122.6898 | -50.7248 | 71.8735 | -0.097002 | 0.027354 | 0.027456 | 0.012685 | 0.063721 | 0.011017 | 0.089976 | -43.9362 | 71.8689 | -51.0315 | -50.9903 | 49.9512 | 22.4579 | 0.16022 | 7.9285 | 71.9193 | -51.0132 | -0.3067 | -0.004578 | 6.7886 | -0.2655 | 0.022889 | -21.9223 | -21.9681 | -0.28839 | 0.045776 | 7.0953
1173.5781 | 122.7219 | -50.6973 | 71.8872 | 0.032698 | 0.027568 | 0.02596 | 0.012899 | 0.063934 | 0.0082397 | 0.088908 | -43.9316 | 71.9009 | -50.9766 | -50.9491 | 50.0381 | 22.6318 | 0.15564 | 7.9971 | 71.9284 | -51.004 | -0.27923 | 0.013733 | 6.7657 | -0.25177 | 0.054931 | -21.8491 | -21.8903 | -0.3067 | 0.041199 | 7.045
1174.5781 | 122.7264 | -50.6882 | 71.8872 | -0.11226 | 0.024577 | 0.027883 | 0.015035 | 0.06073 | 0.0086669 | 0.08784 | -43.8995 | 71.8826 | -50.9811 | -50.9308 | 50.0977 | 22.7737 | 0.13733 | 8.0246 | 71.9284 | -50.9811 | -0.29297 | -0.004578 | 6.7886 | -0.24262 | 0.050354 | -21.7896 | -21.8307 | -0.29297 | 0.041199 | 7.0816
1175.5781 | 122.6807 | -50.7706 | 71.8048 | -0.074114 | 0.026713 | 0.02831 | 0.015249 | 0.06073 | 0.0097351 | 0.09019 | -44.0186 | 71.7957 | -51.0727 | -51.0452 | 49.9878 | 22.7646 | 0.13733 | 7.9834 | 71.8506 | -51.0635 | -0.30212 | -0.009156 | 6.752 | -0.27466 | 0.018311 | -21.817 | -21.8628 | -0.29297 | 0.045776 | 7.0541
1176.5781 | 122.7219 | -50.7751 | 71.8277 | -0.043596 | 0.025859 | 0.023824 | 0.01418 | 0.064575 | 0.0071717 | 0.086131 | -43.9957 | 71.8048 | -51.0223 | -50.9811 | 50.0748 | 22.9294 | 0.10071 | 8.0383 | 71.8597 | -51.0452 | -0.24719 | -0.022888 | 6.7795 | -0.20599 | 0.064087 | -21.7529 | -21.785 | -0.27008 | 0.032043 | 7.0267
1177.5781 | 122.8546 | -50.7935 | 71.7361 | -2.218 | 0.023936 | 0.026174 | 0.013967 | 0.062439 | 0.010803 | 0.089122 | -44.0689 | 71.6766 | -51.1002 | -50.9537 | 50.061 | 23.0484 | -0.036621 | 8.1573 | 71.759 | -51.0681 | -0.3067 | -0.059509 | 6.7245 | -0.16022 | 0.11444 | -21.6751 | -21.698 | -0.27466 | 0.022888 | 7.0312
1178.5938 | 122.7081 | -50.6699 | 71.9055 | -0.26485 | 0.028636 | 0.026815 | 0.020803 | 0.062439 | 0.0093079 | 0.088694 | -43.927 | 71.9376 | -50.9491 | -50.9262 | 50.0839 | 23.1262 | -0.022888 | 8.075 | 71.8918 | -50.9903 | -0.27924 | 0.032043 | 6.7429 | -0.25635 | 0.064087 | -21.8216 | -21.8079 | -0.32043 | -0.013733 | 7.0221
1179.5781 | 122.8409 | -50.6104 | 71.8872 | 2.1384 | 0.02714 | 0.026815 | 0.011831 | 0.062012 | 0.0095215 | 0.087413 | -43.8309 | 71.8826 | -50.9262 | -50.7889 | 50.267 | 23.4787 | -0.036621 | 8.2809 | 71.9376 | -50.885 | -0.31586 | -0.004578 | 6.7795 | -0.17853 | 0.096131 | -21.6202 | -21.6705 | -0.27466 | 0.050354 | 7.0953
1180.5781 | 122.7081 | -50.6378 | 71.8552 | -0.0054494 | 0.026499 | 0.023824 | 0.010549 | 0.060944 | 0.0084533 | 0.089549 | -43.8812 | 71.8552 | -50.9079 | -50.7935 | 50.2396 | 23.5703 | -0.045776 | 8.5281 | 71.8781 | -50.9171 | -0.27008 | 0 | 6.7566 | -0.15564 | 0.1236 | -21.6156 | -21.6385 | -0.27924 | 0.022888 | 7.0267
1181.5781 | 122.8546 | -50.4547 | 72.0245 | 0.025068 | 0.02415 | 0.022329 | 0.012258 | 0.059448 | 0.01059 | 0.088267 | -43.7347 | 71.9742 | -50.7935 | -50.6332 | 50.3815 | 23.7305 | -0.064087 | 8.6334 | 72.0383 | -50.7523 | -0.33874 | -0.050354 | 6.72 | -0.17853 | 0.11902 | -21.6431 | -21.6568 | -0.29755 | 0.013733 | 7.0587
1182.5781 | 122.8638 | -50.5737 | 71.933 | -0.051226 | 0.024363 | 0.025533 | 0.014394 | 0.060089 | 0.0095215 | 0.089335 | -43.808 | 71.9055 | -50.8575 | -50.7339 | 50.2167 | 23.6755 | 0.11902 | 8.2535 | 71.9238 | -50.8804 | -0.28381 | -0.027465 | 6.7657 | -0.16022 | 0.14648 | -21.7163 | -21.7072 | -0.3067 | -0.009155 | 7.0496
1183.5781 | 122.818 | -50.4959 | 72.0154 | 0.070845 | 0.023936 | 0.024892 | 0.015035 | 0.059235 | 0.0088807 | 0.089122 | -43.7714 | 71.9009 | -50.8255 | -50.6882 | 50.2625 | 23.7122 | -0.059509 | 8.6243 | 71.9788 | -50.7797 | -0.32959 | -0.11444 | 6.7245 | -0.19226 | 0.091553 | -21.7529 | -21.7163 | -0.28381 | -0.036621 | 7.0541
1184.5781 | 122.8043 | -50.5417 | 71.9604 | 0.20054 | 0.026713 | 0.026174 | 0.011831 | 0.059448 | 0.010803 | 0.087413 | -43.8858 | 71.9009 | -50.8804 | -50.7568 | 50.1801 | 23.7762 | -0.068665 | 8.6014 | 71.9421 | -50.8621 | -0.33874 | -0.059509 | 6.6559 | -0.21515 | 0.10529 | -21.7804 | -21.7621 | -0.32043 | -0.01831 | 6.9946
1185.5781 | 122.8088 | -50.6607 | 71.846 | 0.20817 | 0.023936 | 0.023824 | 0.012899 | 0.059875 | 0.0099487 | 0.088481 | -44.0048 | 71.7911 | -50.9766 | -50.8987 | 50.0656 | 23.7396 | -0.091553 | 8.4778 | 71.8231 | -50.9491 | -0.31586 | -0.054931 | 6.6559 | -0.23804 | 0.050354 | -21.7804 | -21.7575 | -0.28839 | -0.022888 | 6.9717
1186.5781 | 122.8134 | -50.6882 | 71.846 | 0.12425 | 0.026072 | 0.023397 | 0.013112 | 0.05838 | 0.011017 | 0.087413 | -43.9911 | 71.7636 | -50.9995 | -50.8759 | 50.0565 | 23.7396 | -0.086975 | 8.4961 | 71.7773 | -50.9903 | -0.31128 | -0.082397 | 6.6971 | -0.18768 | 0.11444 | -21.7895 | -21.7209 | -0.30212 | -0.068664 | 7.0084
1187.5781 | 122.8134 | -50.7889 | 71.727 | 0.19291 | 0.024577 | 0.026815 | 0.011403 | 0.057953 | 0.011017 | 0.089122 | -44.1284 | 71.6766 | -51.1002 | -50.9995 | 49.9558 | 23.6984 | -0.073242 | 8.4229 | 71.6904 | -51.059 | -0.31128 | -0.050354 | 6.6605 | -0.21057 | 0.059509 | -21.7712 | -21.7346 | -0.27008 | -0.036621 | 6.9717
1188.5781 | 122.7951 | -50.7339 | 71.7773 | 0.22343 | 0.025004 | 0.02831 | 0.013112 | 0.058594 | 0.010376 | 0.088908 | -44.0872 | 71.6949 | -51.0223 | -50.9491 | 50.0061 | 23.7305 | -0.073242 | 8.4503 | 71.7728 | -51.004 | -0.28839 | -0.082398 | 6.6467 | -0.21515 | 0.054931 | -21.7712 | -21.7667 | -0.27008 | -0.004578 | 6.9351
1189.5781 | 122.8317 | -50.8759 | 71.6263 | 0.063215 | 0.023722 | 0.021474 | 0.012471 | 0.059875 | 0.0097351 | 0.087413 | -44.1879 | 71.5851 | -51.1642 | -51.0498 | 49.942 | 23.6938 | -0.082397 | 8.4457 | 71.6171 | -51.1414 | -0.28839 | -0.041199 | 6.6879 | -0.17395 | 0.091552 | -21.6843 | -21.6751 | -0.2655 | -0.009156 | 6.9763
1190.5781 | 122.8317 | -50.9857 | 71.5393 | 0.14714 | 0.02415 | 0.019979 | 0.012258 | 0.059662 | 0.0095215 | 0.089122 | -44.3161 | 71.4752 | -51.2833 | -51.1734 | 49.8047 | 23.6298 | -0.068665 | 8.2993 | 71.5073 | -51.2558 | -0.29755 | -0.064087 | 6.6696 | -0.18768 | 0.082397 | -21.7346 | -21.7026 | -0.27008 | -0.032044 | 6.9672
1191.5781 | 122.818 | -51.0315 | 71.4569 | 0.27684 | 0.024577 | 0.022542 | 0.011617 | 0.059448 | 0.01059 | 0.09019 | -44.3573 | 71.4706 | -51.3062 | -51.2009 | 49.7498 | 23.6389 | -0.091553 | 8.3084 | 71.4981 | -51.2512 | -0.27466 | 0.013733 | 6.6742 | -0.16937 | 0.050354 | -21.7072 | -21.7484 | -0.21973 | 0.041199 | 6.9489
1192.5781 | 122.8134 | -51.1505 | 71.3928 | 0.27684 | 0.026499 | 0.024892 | 0.013112 | 0.060944 | 0.0093079 | 0.089122 | -44.4717 | 71.3608 | -51.4252 | -51.3474 | 49.6033 | 23.5062 | -0.10071 | 8.1436 | 71.3699 | -51.4114 | -0.27466 | -0.032043 | 6.6788 | -0.19684 | 0.064087 | -21.7896 | -21.7667 | -0.26093 | -0.022888 | 6.9534
1193.5781 | 122.7859 | -51.2009 | 71.3333 | 0.10899 | 0.023509 | 0.024892 | 0.0096945 | 0.058166 | 0.0097351 | 0.091685 | -44.5908 | 71.2097 | -51.5488 | -51.3977 | 49.5026 | 23.5062 | -0.059509 | 8.0887 | 71.2784 | -51.4755 | -0.3479 | -0.1236 | 6.6101 | -0.19684 | 0.07782 | -21.8308 | -21.7758 | -0.27466 | -0.054932 | 6.958
1194.5781 | 122.7676 | -51.2009 | 71.315 | 0.23869 | 0.026713 | 0.029378 | 0.013967 | 0.056671 | 0.0075989 | 0.088267 | -44.5312 | 71.2967 | -51.4618 | -51.4252 | 49.4431 | 23.6069 | -0.045776 | 8.1207 | 71.283 | -51.4481 | -0.26093 | -0.01831 | 6.6696 | -0.2243 | 0.022888 | -21.8719 | -21.8399 | -0.24719 | -0.032043 | 6.9305
1195.5781 | 122.7539 | -51.1093 | 71.4111 | 0.20817 | 0.024577 | 0.027456 | 0.013112 | 0.05838 | 0.0090943 | 0.088267 | -44.4397 | 71.4386 | -51.3657 | -51.2604 | 49.649 | 23.6664 | -0.086975 | 8.2993 | 71.4111 | -51.3657 | -0.25635 | 0.027466 | 6.6696 | -0.15106 | 0.10529 | -21.7621 | -21.7621 | -0.25635 | 0 | 6.926
1196.5781 | 122.7997 | -51.0864 | 71.4249 | 0.22343 | 0.02415 | 0.022542 | 0.011831 | 0.057739 | 0.011017 | 0.090403 | -44.4809 | 71.3837 | -51.3931 | -51.3016 | 49.585 | 23.6664 | -0.073242 | 8.3176 | 71.3745 | -51.3474 | -0.3067 | -0.041199 | 6.6055 | -0.21515 | 0.045776 | -21.8399 | -21.7896 | -0.26093 | -0.050354 | 6.9122
1197.5781 | 122.8134 | -51.2283 | 71.3013 | 0.14714 | 0.025859 | 0.022115 | 0.010976 | 0.057526 | 0.0099487 | 0.088908 | -44.6091 | 71.2418 | -51.5076 | -51.4252 | 49.4843 | 23.584 | -0.086975 | 8.1894 | 71.2738 | -51.4526 | -0.27923 | -0.05951 | 6.6193 | -0.19684 | 0.027466 | -21.817 | -21.7896 | -0.2243 | -0.027466 | 6.8985
1198.5781 | 122.8043 | -51.3611 | 71.1319 | 0.23869 | 0.026499 | 0.024251 | 0.013326 | 0.060089 | 0.0099487 | 0.090831 | -44.7647 | 71.0861 | -51.6678 | -51.5854 | 49.3195 | 23.4787 | -0.086975 | 8.0521 | 71.1044 | -51.6403 | -0.3067 | -0.045776 | 6.5964 | -0.2243 | 0.054932 | -21.8124 | -21.785 | -0.27924 | -0.027466 | 6.9031
1199.5781 | 122.7905 | -51.2329 | 71.2784 | 0.20817 | 0.019664 | 0.021688 | 0.014608 | 0.058594 | 0.0090943 | 0.089122 | -44.6777 | 71.1731 | -51.6083 | -51.4435 | 49.4568 | 23.6938 | -0.054932 | 8.2123 | 71.2509 | -51.4984 | -0.37537 | -0.10528 | 6.5552 | -0.21057 | 0.054932 | -21.8216 | -21.7941 | -0.2655 | -0.027465 | 6.9305
1200.5781 | 122.8043 | -51.3199 | 71.1777 | 0.15477 | 0.023295 | 0.025533 | 0.012044 | 0.058594 | 0.010803 | 0.087626 | -44.7327 | 71.1365 | -51.6312 | -51.5167 | 49.3698 | 23.7396 | -0.045776 | 8.1299 | 71.1548 | -51.6037 | -0.31128 | -0.041198 | 6.5872 | -0.19684 | 0.086975 | -21.8079 | -21.785 | -0.28381 | -0.022888 | 6.8985
1201.5781 | 122.7859 | -51.178 | 71.315 | 0.18529 | 0.026713 | 0.024679 | 0.012471 | 0.059235 | 0.0086669 | 0.086772 | -44.5999 | 71.2967 | -51.4709 | -51.4252 | 49.4202 | 23.9136 | -0.050354 | 8.2352 | 71.2692 | -51.4435 | -0.29297 | -0.01831 | 6.5781 | -0.24719 | 0.01831 | -21.8948 | -21.8491 | -0.2655 | -0.045776 | 6.871
1202.5781 | 122.818 | -51.2329 | 71.2326 | 0.1624 | 0.024577 | 0.026815 | 0.011403 | 0.060089 | 0.010803 | 0.088267 | -44.6503 | 71.2051 | -51.5579 | -51.4297 | 49.4431 | 23.9914 | -0.082397 | 8.2123 | 71.1777 | -51.535 | -0.32501 | -0.027466 | 6.5826 | -0.19684 | 0.10529 | -21.7896 | -21.7346 | -0.30212 | -0.054932 | 6.9077
1203.5781 | 122.8226 | -51.4389 | 71.0678 | 0.20817 | 0.023295 | 0.020406 | 0.010976 | 0.059235 | 0.012299 | 0.088481 | -44.8517 | 71.0175 | -51.7364 | -51.622 | 49.2599 | 23.9319 | -0.068665 | 8.075 | 71.0129 | -51.6998 | -0.29755 | -0.050354 | 6.5872 | -0.1831 | 0.07782 | -21.8079 | -21.7529 | -0.26093 | -0.054932 | 6.8848
1204.5781 | 122.7585 | -51.4389 | 71.0815 | 0.2158 | 0.025431 | 0.027028 | 0.011403 | 0.059235 | 0.011444 | 0.088694 | -44.8242 | 71.077 | -51.6769 | -51.6037 | 49.2966 | 24.1058 | -0.054932 | 8.0109 | 71.0449 | -51.7181 | -0.23804 | -0.004578 | 6.6147 | -0.16479 | 0.11444 | -21.785 | -21.7484 | -0.27924 | -0.036621 | 6.8527
1205.5781 | 122.818 | -51.4389 | 71.0907 | 0.24632 | 0.024577 | 0.024038 | 0.011403 | 0.059662 | 0.0090943 | 0.09019 | -44.8196 | 71.0861 | -51.6724 | -51.5671 | 49.3561 | 24.1562 | -0.050354 | 8.1345 | 71.1273 | -51.6495 | -0.23346 | -0.004577 | 6.6193 | -0.12817 | 0.082397 | -21.7346 | -21.7712 | -0.21057 | 0.036621 | 6.8527
1206.5781 | 122.7905 | -51.3977 | 71.1136 | 0.22343 | 0.025004 | 0.024465 | 0.012685 | 0.057312 | 0.010162 | 0.089549 | -44.8242 | 71.077 | -51.7136 | -51.5854 | 49.3881 | 24.3027 | -0.059509 | 8.1116 | 71.0724 | -51.6769 | -0.31586 | -0.036621 | 6.5735 | -0.18768 | 0.091553 | -21.7255 | -21.6843 | -0.27924 | -0.041198 | 6.8893
1207.5781 | 122.7768 | -51.5121 | 71.0037 | 0.19291 | 0.026713 | 0.024465 | 0.011617 | 0.05838 | 0.0088807 | 0.086558 | -44.9249 | 70.9534 | -51.8143 | -51.7136 | 49.3698 | 24.2706 | -0.073242 | 7.9971 | 70.9534 | -51.7776 | -0.30212 | -0.050354 | 6.5872 | -0.20142 | 0.064087 | -21.6339 | -21.5836 | -0.2655 | -0.050354 | 6.8893
1208.5781 | 122.7905 | -51.5533 | 70.9717 | 0.2158 | 0.023722 | 0.024679 | 0.012899 | 0.059875 | 0.0093079 | 0.08784 | -44.9753 | 70.8984 | -51.8417 | -51.7639 | 49.4568 | 24.321 | -0.07782 | 8.0017 | 70.8984 | -51.8372 | -0.28839 | -0.073243 | 6.5781 | -0.21057 | 0.073242 | -21.5149 | -21.4417 | -0.28381 | -0.073243 | 6.8665
1209.5781 | 122.818 | -51.6129 | 70.871 | 0.12425 | 0.026286 | 0.02361 | 0.012685 | 0.060303 | 0.0099487 | 0.089122 | -44.9982 | 70.8344 | -51.9058 | -51.7639 | 49.5529 | 24.3668 | -0.086975 | 8.02 | 70.8435 | -51.8646 | -0.29297 | -0.036621 | 6.6147 | -0.15106 | 0.10071 | -21.3181 | -21.2906 | -0.25177 | -0.027466 | 6.9077
1210.5781 | 122.8409 | -50.9949 | 71.5347 | 0.14714 | 0.025004 | 0.024038 | 0.011403 | 0.060303 | 0.0097351 | 0.090403 | -44.3619 | 71.5118 | -51.2466 | -51.1368 | 50.3128 | 24.8245 | -0.086975 | 8.5236 | 71.5118 | -51.2283 | -0.25177 | -0.022888 | 6.633 | -0.14191 | 0.091553 | -21.2219 | -21.199 | -0.23346 | -0.022888 | 6.8848
1211.5781 | 122.8043 | -50.9171 | 71.5668 | 0.79564 | 0.025431 | 0.024251 | 0.012258 | 0.05838 | 0.0086669 | 0.090403 | -44.4626 | 71.5393 | -51.2512 | -51.1276 | 50.5188 | 24.9619 | -0.036621 | 8.6243 | 71.5713 | -51.1642 | -0.33417 | -0.027465 | 6.4545 | -0.21057 | 0.036621 | -21.048 | -21.0526 | -0.24719 | 0.004578 | 6.7886
1212.5781 | 122.7814 | -51.6495 | 70.871 | 0.49809 | 0.022013 | 0.021261 | 0.013326 | 0.059875 | 0.0097351 | 0.089549 | -45.0989 | 70.7565 | -51.9974 | -51.8555 | 49.9283 | 24.5911 | -0.045776 | 7.9788 | 70.7977 | -51.9058 | -0.3479 | -0.11444 | 6.5506 | -0.20599 | 0.050354 | -20.9427 | -20.8694 | -0.25635 | -0.073243 | 6.8985
1213.5781 | 122.8226 | -51.7136 | 70.8115 | 0.1624 | 0.023509 | 0.023397 | 0.013326 | 0.058594 | 0.0095215 | 0.089122 | -45.1584 | 70.7108 | -51.9974 | -51.8646 | 50.0381 | 24.7513 | -0.091553 | 8.0017 | 70.7611 | -51.9699 | -0.28381 | -0.10071 | 6.5552 | -0.15106 | 0.10529 | -20.7733 | -20.723 | -0.25635 | -0.050354 | 6.839
1214.5781 | 122.8043 | -51.5671 | 70.8984 | 0.13188 | 0.023936 | 0.023397 | 0.011831 | 0.05838 | 0.0082397 | 0.08784 | -45.0256 | 70.8755 | -51.8692 | -51.7776 | 50.2029 | 24.9161 | -0.068665 | 8.1024 | 70.8893 | -51.8509 | -0.30212 | -0.022888 | 6.5414 | -0.21057 | 0.073242 | -20.6955 | -20.6863 | -0.28381 | -0.009155 | 6.8436
1215.5781 | 122.8043 | -51.6129 | 70.8847 | 0.1624 | 0.023295 | 0.024679 | 0.010762 | 0.060303 | 0.0065307 | 0.088053 | -45.0485 | 70.8572 | -51.915 | -51.7776 | 50.2441 | 25.0076 | -0.068665 | 8.1116 | 70.8527 | -51.86 | -0.30212 | -0.027466 | 6.5643 | -0.16479 | 0.082397 | -20.6406 | -20.6085 | -0.24719 | -0.032044 | 6.8665
1216.5781 | 122.8546 | -51.709 | 70.7703 | 0.12425 | 0.024363 | 0.023183 | 0.013326 | 0.059021 | 0.0093079 | 0.088053 | -45.1355 | 70.7382 | -51.9974 | -51.86 | 50.2075 | 24.9939 | -0.07782 | 8.0521 | 70.7245 | -51.9791 | -0.28839 | -0.032044 | 6.5735 | -0.15106 | 0.11902 | -20.5627 | -20.517 | -0.27008 | -0.045777 | 6.8619
1217.5781 | 122.8317 | -52.066 | 70.4178 | 0.086103 | 0.024577 | 0.025106 | 0.010549 | 0.059662 | 0.010162 | 0.086985 | -45.4697 | 70.3812 | -52.3956 | -52.2354 | 49.855 | 24.7513 | -0.09613 | 7.7042 | 70.3995 | -52.327 | -0.32959 | -0.036621 | 6.5964 | -0.16937 | 0.091552 | -20.5627 | -20.5444 | -0.26093 | -0.018311 | 6.926
1218.5781 | 122.8226 | -52.2903 | 70.2301 | 0.23106 | 0.02479 | 0.026174 | 0.011831 | 0.059875 | 0.011231 | 0.089122 | -45.7352 | 70.1843 | -52.5879 | -52.4734 | 49.6078 | 24.6643 | -0.068665 | 7.4844 | 70.2026 | -52.5421 | -0.29755 | -0.045777 | 6.5552 | -0.18311 | 0.068664 | -20.6223 | -20.5948 | -0.25177 | -0.027466 | 6.8527
1219.5781 | 122.8363 | -52.3315 | 70.1706 | 0.23106 | 0.024363 | 0.024679 | 0.01418 | 0.060089 | 0.0090943 | 0.088694 | -45.8176 | 70.0882 | -52.6474 | -52.5421 | 49.5438 | 24.6048 | -0.068665 | 7.402 | 70.1111 | -52.6154 | -0.31586 | -0.082397 | 6.514 | -0.21057 | 0.073242 | -20.6268 | -20.5673 | -0.28381 | -0.059509 | 6.8298
1220.5781 | 122.7997 | -52.3132 | 70.1706 | 0.070845 | 0.023936 | 0.021474 | 0.012258 | 0.059662 | 0.011231 | 0.086985 | -45.7214 | 70.1523 | -52.6291 | -52.4643 | 49.5712 | 24.5453 | -0.086975 | 7.37 | 70.1248 | -52.5742 | -0.31586 | -0.01831 | 6.5918 | -0.15106 | 0.10986 | -20.5994 | -20.5536 | -0.26093 | -0.045776 | 6.9077
1221.5781 | 122.8455 | -52.5513 | 69.9463 | 0.13188 | 0.026499 | 0.027883 | 0.011831 | 0.059662 | 0.0093079 | 0.090617 | -45.9366 | 69.8959 | -52.858 | -52.7069 | 49.4202 | 24.5224 | -0.10986 | 7.2647 | 69.9051 | -52.8076 | -0.3067 | -0.050354 | 6.6147 | -0.15564 | 0.10071 | -20.5261 | -20.4849 | -0.25635 | -0.041199 | 6.9214
1222.5781 | 122.8317 | -52.4643 | 70.0195 | 0.10899 | 0.022441 | 0.024038 | 0.011831 | 0.059021 | 0.0080261 | 0.088694 | -45.8771 | 69.9738 | -52.7802 | -52.6245 | 49.53 | 24.5499 | -0.086975 | 7.283 | 69.9646 | -52.7344 | -0.31586 | -0.045776 | 6.5872 | -0.16022 | 0.10986 | -20.4895 | -20.4346 | -0.27008 | -0.054931 | 6.9031
1223.5781 | 122.9095 | -52.4231 | 70.1065 | 0.0021796 | 0.022654 | 0.024679 | 0.01418 | 0.058807 | 0.0075989 | 0.087413 | -45.7764 | 70.0195 | -52.7069 | -52.5604 | 49.6078 | 24.5865 | -0.041199 | 7.4249 | 70.0241 | -52.6749 | -0.28381 | -0.086975 | 6.6467 | -0.13733 | 0.11444 | -20.4987 | -20.4163 | -0.25177 | -0.082397 | 6.9305
1224.5781 | 122.8409 | -52.597 | 69.9234 | -0.013079 | 0.023295 | 0.022542 | 0.012044 | 0.057739 | 0.0075989 | 0.088267 | -45.9549 | 69.873 | -52.8946 | -52.7344 | 49.4476 | 24.4446 | -0.054932 | 7.2235 | 69.8776 | -52.8488 | -0.29755 | -0.050354 | 6.6422 | -0.13733 | 0.11444 | -20.4758 | -20.43 | -0.25177 | -0.045776 | 6.9397
1225.5781 | 122.8088 | -52.6474 | 69.8456 | 0.13951 | 0.024363 | 0.025533 | 0.011831 | 0.059662 | 0.0086669 | 0.08784 | -46.051 | 69.8181 | -52.9633 | -52.8305 | 49.3652 | 24.3988 | -0.07782 | 7.1182 | 69.809 | -52.9083 | -0.31586 | -0.027466 | 6.5964 | -0.18311 | 0.07782 | -20.4803 | -20.4437 | -0.26093 | -0.036621 | 6.9122
1226.5781 | 122.8271 | -52.8671 | 69.6167 | 0.12425 | 0.022868 | 0.02596 | 0.013112 | 0.05838 | 0.0069581 | 0.086985 | -46.2204 | 69.6487 | -53.096 | -52.977 | 49.2004 | 24.3027 | -0.11902 | 6.926 | 69.6075 | -53.1235 | -0.22888 | 0.032044 | 6.6467 | -0.10986 | 0.14648 | -20.4163 | -20.4071 | -0.25635 | -0.009155 | 6.8756
1227.5781 | 122.8592 | -52.8625 | 69.6075 | 0.025068 | 0.023509 | 0.02297 | 0.013112 | 0.059021 | 0.0058899 | 0.087199 | -46.2524 | 69.5663 | -53.1784 | -53.0228 | 49.2325 | 24.3668 | -0.09613 | 6.9351 | 69.5618 | -53.1464 | -0.31586 | -0.041199 | 6.6101 | -0.16022 | 0.1236 | -20.3751 | -20.3293 | -0.28381 | -0.045776 | 6.926
1228.5781 | 122.8271 | -52.8809 | 69.5892 | 0.13188 | 0.023936 | 0.025533 | 0.012685 | 0.060944 | 0.0093079 | 0.087199 | -46.2708 | 69.5435 | -53.1784 | -53.0319 | 49.2004 | 24.4308 | -0.091553 | 6.9168 | 69.5663 | -53.1281 | -0.29755 | -0.045776 | 6.6101 | -0.15106 | 0.096131 | -20.3888 | -20.3659 | -0.24719 | -0.022888 | 6.9077
1229.5781 | 122.85 | -52.9175 | 69.5526 | 0.12425 | 0.024363 | 0.02361 | 0.01354 | 0.058594 | 0.0097351 | 0.087626 | -46.3211 | 69.5206 | -53.2242 | -53.096 | 49.1684 | 24.5407 | -0.082397 | 6.8802 | 69.5114 | -53.1921 | -0.3067 | -0.032043 | 6.5964 | -0.17853 | 0.096131 | -20.3842 | -20.343 | -0.27466 | -0.041198 | 6.9031
1230.5781 | 122.8317 | -53.0594 | 69.4199 | -0.013079 | 0.022654 | 0.029806 | 0.011403 | 0.060303 | 0.0095215 | 0.089335 | -46.4584 | 69.3649 | -53.3981 | -53.2516 | 49.0723 | 24.527 | -0.054932 | 6.7337 | 69.3512 | -53.3432 | -0.33874 | -0.054932 | 6.601 | -0.19226 | 0.091553 | -20.3476 | -20.2789 | -0.28381 | -0.068665 | 6.9397
1231.5781 | 122.8271 | -52.9953 | 69.5206 | 0.047956 | 0.02415 | 0.021688 | 0.012899 | 0.059875 | 0.0056763 | 0.086772 | -46.3531 | 69.4336 | -53.3157 | -53.1464 | 49.2966 | 24.7284 | -0.068665 | 6.7795 | 69.4473 | -53.2654 | -0.32043 | -0.086975 | 6.6422 | -0.15106 | 0.11902 | -20.224 | -20.1508 | -0.27008 | -0.073242 | 6.9626
1232.5781 | 122.8088 | -53.1143 | 69.3924 | 0.19291 | 0.02415 | 0.027028 | 0.012258 | 0.060303 | 0.0088807 | 0.087626 | -46.5271 | 69.3283 | -53.4348 | -53.2974 | 49.1776 | 24.6552 | -0.082397 | 6.6696 | 69.3512 | -53.3707 | -0.32043 | -0.064087 | 6.5872 | -0.1831 | 0.073243 | -20.2148 | -20.1736 | -0.25635 | -0.041199 | 6.9077
1233.5781 | 122.818 | -53.2196 | 69.2825 | 0.23106 | 0.026286 | 0.02361 | 0.013753 | 0.05838 | 0.010376 | 0.088053 | -46.6507 | 69.2047 | -53.5172 | -53.4256 | 49.086 | 24.6231 | -0.068665 | 6.5552 | 69.2322 | -53.4622 | -0.29755 | -0.07782 | 6.5689 | -0.20599 | 0.036621 | -20.1965 | -20.1462 | -0.24262 | -0.050354 | 6.8665
1234.5781 | 122.8409 | -53.3981 | 69.0903 | 0.13951 | 0.025218 | 0.027028 | 0.01354 | 0.059448 | 0.010162 | 0.089762 | -46.7789 | 69.0353 | -53.6957 | -53.5858 | 48.9716 | 24.4766 | -0.091553 | 6.4316 | 69.0491 | -53.6774 | -0.29755 | -0.054932 | 6.6193 | -0.18768 | 0.091553 | -20.1187 | -20.0775 | -0.27924 | -0.041199 | 6.9168
1235.5781 | 122.8546 | -53.5172 | 68.985 | 0.093733 | 0.023081 | 0.02361 | 0.012044 | 0.059662 | 0.0090943 | 0.086344 | -46.9116 | 68.9301 | -53.8284 | -53.6865 | 48.8251 | 24.5544 | -0.073242 | 6.3034 | 68.9484 | -53.7872 | -0.31128 | -0.054931 | 6.6055 | -0.16937 | 0.10071 | -20.1599 | -20.1233 | -0.27008 | -0.036621 | 6.9168
1236.5781 | 122.8134 | -53.6316 | 68.8843 | 0.17003 | 0.025218 | 0.02297 | 0.012258 | 0.058166 | 0.0099487 | 0.085917 | -47.0215 | 68.8065 | -53.9429 | -53.8055 | 48.6877 | 24.5316 | -0.054932 | 6.1935 | 68.8248 | -53.8879 | -0.31128 | -0.077819 | 6.6101 | -0.17395 | 0.082397 | -20.1965 | -20.137 | -0.25635 | -0.059509 | 6.9214
1237.5781 | 122.8317 | -53.6636 | 68.7973 | 0.078474 | 0.022868 | 0.019979 | 0.013112 | 0.060089 | 0.0086669 | 0.086558 | -47.0581 | 68.779 | -53.9886 | -53.8467 | 48.6969 | 24.6231 | -0.086975 | 6.2119 | 68.7515 | -53.952 | -0.32501 | -0.01831 | 6.6055 | -0.18311 | 0.10528 | -20.1004 | -20.0546 | -0.28839 | -0.045776 | 6.9305
1238.5781 | 122.8271 | -53.8055 | 68.6737 | 0.17003 | 0.023936 | 0.024679 | 0.012899 | 0.057098 | 0.01059 | 0.086558 | -47.2 | 68.6325 | -54.1306 | -53.9886 | 48.5504 | 24.6506 | -0.09613 | 6.0654 | 68.6462 | -54.0848 | -0.32501 | -0.041199 | 6.6055 | -0.1831 | 0.096131 | -20.1233 | -20.0958 | -0.27924 | -0.027466 | 6.9305
1239.5781 | 122.7585 | -53.6819 | 68.8248 | 0.2158 | 0.021586 | 0.022115 | 0.011403 | 0.055603 | 0.0099487 | 0.08784 | -47.1222 | 68.7836 | -53.9978 | -53.9383 | 48.5825 | 24.7971 | -0.032043 | 6.1569 | 68.7424 | -53.9337 | -0.31586 | -0.041199 | 6.5598 | -0.25635 | -0.004577 | -20.2423 | -20.1599 | -0.25177 | -0.082397 | 6.8756
1240.5781 | 122.7997 | -53.746 | 68.7378 | 0.24632 | 0.02479 | 0.023824 | 0.012685 | 0.059235 | 0.0071717 | 0.086985 | -47.2046 | 68.7286 | -54.039 | -53.9612 | 48.6008 | 24.8749 | -0.07782 | 6.0974 | 68.7012 | -54.0344 | -0.29297 | -0.009155 | 6.5414 | -0.21515 | 0.073242 | -20.137 | -20.1004 | -0.28839 | -0.036621 | 6.8344
1241.5781 | 122.8043 | -53.8193 | 68.6554 | 0.2921 | 0.023722 | 0.023397 | 0.013753 | 0.059235 | 0.011444 | 0.087626 | -47.3007 | 68.6279 | -54.1351 | -54.0298 | 48.5596 | 24.9527 | -0.073242 | 5.983 | 68.6096 | -54.1122 | -0.31586 | -0.027466 | 6.5186 | -0.21057 | 0.082398 | -20.0958 | -20.05 | -0.29297 | -0.045777 | 6.8344
1242.5781 | 122.7951 | -53.8742 | 68.6279 | 0.17003 | 0.02415 | 0.026601 | 0.01119 | 0.060944 | 0.0093079 | 0.088481 | -47.2778 | 68.5913 | -54.1763 | -54.071 | 48.5504 | 24.939 | -0.073242 | 5.9647 | 68.5913 | -54.1443 | -0.30212 | -0.036621 | 6.5964 | -0.19684 | 0.073242 | -20.0775 | -20.0409 | -0.27008 | -0.036621 | 6.8985
1243.5781 | 122.7997 | -53.8513 | 68.6325 | 0.23106 | 0.023722 | 0.025106 | 0.012258 | 0.059235 | 0.0099487 | 0.08784 | -47.2916 | 68.5913 | -54.158 | -54.0482 | 48.5687 | 25.0671 | -0.059509 | 5.9967 | 68.6325 | -54.1168 | -0.3067 | -0.041198 | 6.5598 | -0.19684 | 0.068664 | -20.0638 | -20.0638 | -0.2655 | 0 | 6.8665
1244.5781 | 122.7631 | -53.9383 | 68.573 | 0.27684 | 0.026713 | 0.024892 | 0.013967 | 0.058807 | 0.010162 | 0.08784 | -47.3923 | 68.5364 | -54.2587 | -54.1306 | 48.5229 | 25.0763 | -0.07782 | 5.9052 | 68.5181 | -54.1809 | -0.32043 | -0.036621 | 6.546 | -0.19226 | 0.050354 | -20.05 | -19.9951 | -0.24262 | -0.054932 | 6.8665
1245.5781 | 122.7814 | -53.9658 | 68.4998 | 0.20054 | 0.025431 | 0.018484 | 0.016744 | 0.057953 | 0.0099487 | 0.08784 | -47.3877 | 68.5089 | -54.2725 | -54.2038 | 48.4589 | 25.2228 | -0.086975 | 5.8731 | 68.4952 | -54.2404 | -0.3067 | 0.009155 | 6.5781 | -0.23804 | 0.036621 | -20.0409 | -20.0363 | -0.27466 | -0.004578 | 6.8848
1246.5781 | 122.8043 | -54.1031 | 68.3716 | 0.35313 | 0.025218 | 0.026601 | 0.012471 | 0.059662 | 0.0095215 | 0.087626 | -47.5021 | 68.3395 | -54.3823 | -54.3274 | 48.3444 | 25.2182 | -0.1236 | 5.7678 | 68.3441 | -54.3732 | -0.27924 | -0.032043 | 6.601 | -0.22431 | 0.045776 | -20.0272 | -19.9997 | -0.27008 | -0.027466 | 6.8802
1247.5781 | 122.7722 | -54.0665 | 68.4219 | 0.30736 | 0.025004 | 0.028524 | 0.012471 | 0.05838 | 0.0099487 | 0.089335 | -47.5113 | 68.3945 | -54.3777 | -54.277 | 48.3856 | 25.3143 | -0.09613 | 5.8502 | 68.4128 | -54.3411 | -0.31128 | -0.027466 | 6.5552 | -0.21057 | 0.064086 | -20.0363 | -20.0272 | -0.27466 | -0.009155 | 6.8665
1248.5781 | 122.8134 | -54.0298 | 68.4357 | 0.33024 | 0.025859 | 0.027242 | 0.012471 | 0.060303 | 0.0086669 | 0.088267 | -47.4747 | 68.4128 | -54.3503 | -54.2633 | 48.4085 | 25.3601 | -0.11444 | 5.8594 | 68.4036 | -54.332 | -0.32044 | -0.022888 | 6.5552 | -0.23346 | 0.068664 | -20.0272 | -19.9951 | -0.30212 | -0.032044 | 6.8756
1249.5781 | 122.7814 | -54.0161 | 68.4723 | 0.38365 | 0.028636 | 0.027456 | 0.015035 | 0.059235 | 0.0086669 | 0.088267 | -47.4289 | 68.4677 | -54.3182 | -54.2221 | 48.468 | 25.4334 | -0.13275 | 5.9097 | 68.4448 | -54.2999 | -0.30212 | -0.004578 | 6.5872 | -0.20599 | 0.07782 | -20.0043 | -19.9768 | -0.28381 | -0.027466 | 6.8893
1250.5781 | 122.7676 | -54.071 | 68.3945 | 0.39891 | 0.024577 | 0.025747 | 0.01354 | 0.059662 | 0.0099487 | 0.088694 | -47.4747 | 68.3624 | -54.3777 | -54.2725 | 48.4314 | 25.5157 | -0.1831 | 5.8823 | 68.3487 | -54.3732 | -0.3067 | -0.032043 | 6.5964 | -0.20142 | 0.10071 | -19.9631 | -19.9173 | -0.30212 | -0.045776 | 6.9031
1251.5781 | 122.7905 | -54.2084 | 68.2709 | 0.39128 | 0.024363 | 0.02596 | 0.017171 | 0.059662 | 0.011231 | 0.086772 | -47.6532 | 68.248 | -54.5197 | -54.4235 | 48.2758 | 25.415 | -0.13275 | 5.7175 | 68.248 | -54.4922 | -0.31128 | -0.022888 | 6.5552 | -0.21515 | 0.068664 | -19.9951 | -19.9722 | -0.28381 | -0.022888 | 6.8665
1252.5781 | 122.7631 | -54.2633 | 68.2251 | 0.3455 | 0.02479 | 0.02596 | 0.013753 | 0.059235 | 0.0095215 | 0.086558 | -47.6624 | 68.1976 | -54.5654 | -54.451 | 48.2391 | 25.4013 | -0.14648 | 5.6808 | 68.161 | -54.5517 | -0.30212 | -0.027466 | 6.601 | -0.18768 | 0.10071 | -19.986 | -19.9219 | -0.28839 | -0.064087 | 6.9031
1253.5781 | 122.8912 | -54.3457 | 68.074 | 0.4218 | 0.02415 | 0.025319 | 0.016958 | 0.060944 | 0.0080261 | 0.088053 | -47.7036 | 68.1335 | -54.6387 | -54.4922 | 48.2254 | 25.589 | -0.17853 | 5.6946 | 68.1473 | -54.5792 | -0.29297 | 0.059509 | 6.6422 | -0.14648 | 0.086976 | -19.8486 | -19.9219 | -0.23346 | 0.073242 | 6.9351
1254.5781 | 122.8226 | -54.3457 | 68.1061 | 0.39128 | 0.025218 | 0.025533 | 0.01888 | 0.060089 | 0.0071717 | 0.089762 | -47.7493 | 68.1107 | -54.6661 | -54.5288 | 48.1613 | 25.7492 | -0.20142 | 5.6534 | 68.0511 | -54.657 | -0.32043 | 0.004578 | 6.5964 | -0.18311 | 0.12817 | -19.9448 | -19.8898 | -0.31128 | -0.054932 | 6.9168
1255.5781 | 122.818 | -54.5288 | 67.9504 | 0.39891 | 0.026927 | 0.029592 | 0.016958 | 0.060089 | 0.0090943 | 0.089762 | -47.8821 | 67.9504 | -54.8218 | -54.8492 | 48.0698 | 25.795 | -0.19684 | 5.4382 | 67.9001 | -54.8264 | -0.29297 | 0 | 6.6467 | -0.32043 | -0.022888 | -19.8807 | -19.8303 | -0.29755 | -0.050354 | 6.9397
1256.5781 | 122.8226 | -54.5563 | 67.8909 | 0.43706 | 0.027995 | 0.020406 | 0.018239 | 0.063721 | 0.0097351 | 0.089976 | -47.9095 | 67.9413 | -54.8676 | -54.7211 | 48.0057 | 25.7217 | -0.21057 | 5.4291 | 67.8818 | -54.8584 | -0.31128 | 0.050354 | 6.6467 | -0.16479 | 0.13733 | -19.8853 | -19.8761 | -0.30212 | -0.009155 | 6.958
1257.5781 | 122.8226 | -54.5563 | 67.9092 | 0.46757 | 0.028208 | 0.025319 | 0.016744 | 0.060944 | 0.0069581 | 0.088694 | -47.937 | 67.9367 | -54.8721 | -54.744 | 48.0011 | 25.7355 | -0.19226 | 5.4245 | 67.8726 | -54.8904 | -0.31586 | 0.027466 | 6.6193 | -0.18768 | 0.14648 | -19.9081 | -19.8715 | -0.33417 | -0.036621 | 6.9351
1258.5781 | 122.8271 | -54.6021 | 67.8635 | 0.39128 | 0.025004 | 0.028951 | 0.016317 | 0.062652 | 0.0086669 | 0.087413 | -47.9507 | 67.9138 | -54.8996 | -54.9454 | 47.7997 | 25.7721 | 0.009155 | 5.4382 | 67.8543 | -54.8904 | -0.29755 | 0.050354 | 6.6513 | -0.34332 | -0.054932 | -20.0638 | -20.0546 | -0.28839 | -0.009155 | 6.9489
1259.5781 | 122.8546 | -54.5883 | 67.8955 | 0.38365 | 0.02714 | 0.026815 | 0.019735 | 0.061798 | 0.0082397 | 0.088908 | -47.9416 | 67.9138 | -54.8904 | -54.7485 | 48.0148 | 25.9415 | -0.19684 | 5.3604 | 67.8497 | -54.895 | -0.30212 | 0.01831 | 6.6467 | -0.16022 | 0.14649 | -19.8807 | -19.8349 | -0.3067 | -0.045777 | 6.9489
1260.5781 | 122.7585 | -54.7119 | 67.8223 | 0.43706 | 0.026286 | 0.027028 | 0.019307 | 0.062652 | 0.0082397 | 0.088053 | -48.0835 | 67.8635 | -55.0003 | -54.9042 | 47.8867 | 25.9323 | -0.11902 | 5.2048 | 67.8085 | -54.9911 | -0.28839 | 0.041198 | 6.6284 | -0.19226 | 0.086975 | -19.9356 | -19.9219 | -0.27924 | -0.013733 | 6.9168
1261.5781 | 122.818 | -54.9683 | 67.4927 | 0.4752 | 0.02714 | 0.026174 | 0.019948 | 0.063934 | 0.0078125 | 0.089549 | -48.3124 | 67.5522 | -55.2887 | -55.1605 | 47.6303 | 25.6577 | -0.16479 | 5.0034 | 67.4789 | -55.2795 | -0.32043 | 0.059509 | 6.6559 | -0.19226 | 0.11902 | -19.8624 | -19.8486 | -0.31128 | -0.013733 | 6.9763
1262.5781 | 122.8271 | -54.9866 | 67.511 | 0.42943 | 0.02714 | 0.028737 | 0.019094 | 0.064148 | 0.0080261 | 0.087626 | -48.3673 | 67.5385 | -55.3116 | -55.2017 | 47.5525 | 25.7401 | -0.16022 | 4.9713 | 67.4744 | -55.2979 | -0.32501 | 0.027466 | 6.6193 | -0.21515 | 0.096131 | -19.9585 | -19.9219 | -0.31128 | -0.036621 | 6.9443
1263.5781 | 122.7676 | -54.6387 | 67.8726 | 0.40654 | 0.02714 | 0.024679 | 0.019521 | 0.06607 | 0.0082397 | 0.086772 | -48.0331 | 67.923 | -54.9408 | -54.8584 | 47.8363 | 25.9048 | -0.11902 | 5.2231 | 67.8635 | -54.9454 | -0.30212 | 0.050354 | 6.6055 | -0.21973 | 0.086976 | -20.0363 | -20.0272 | -0.3067 | -0.009156 | 6.9077
1264.5781 | 122.8226 | -54.6158 | 67.8268 | 0.42943 | 0.025004 | 0.027883 | 0.01418 | 0.059021 | 0.0078125 | 0.088053 | -47.9874 | 67.8131 | -54.9866 | -54.8721 | 47.8821 | 25.8636 | -0.17853 | 5.2414 | 67.8268 | -54.9225 | -0.37079 | -0.013733 | 6.6284 | -0.25635 | 0.050354 | -19.9448 | -19.9448 | -0.3067 | 0 | 6.9992
1265.5781 | 122.7997 | -54.6753 | 67.8131 | 0.45994 | 0.027354 | 0.028524 | 0.019521 | 0.063293 | 0.0086669 | 0.088053 | -48.0286 | 67.8497 | -54.9774 | -54.863 | 47.8271 | 25.9644 | -0.16937 | 5.2185 | 67.7765 | -54.9637 | -0.30212 | 0.036621 | 6.6467 | -0.18768 | 0.10071 | -19.986 | -19.9493 | -0.28839 | -0.036621 | 6.9489
1266.5781 | 122.818 | -54.7073 | 67.8131 | 0.40654 | 0.027995 | 0.025319 | 0.018666 | 0.063721 | 0.0073853 | 0.087413 | -48.0515 | 67.8635 | -54.9911 | -54.8996 | 47.7905 | 26.001 | -0.15564 | 5.2139 | 67.7856 | -55.0186 | -0.28381 | 0.050354 | 6.6559 | -0.19226 | 0.11902 | -20.0226 | -19.9951 | -0.31128 | -0.027465 | 6.9397
1267.5781 | 122.7356 | -54.744 | 67.804 | 0.39128 | 0.027781 | 0.031515 | 0.017598 | 0.065002 | 0.0086669 | 0.088908 | -48.1613 | 67.868 | -55.0278 | -54.9271 | 47.7859 | 26.0376 | -0.027466 | 5.1315 | 67.7994 | -55.069 | -0.28381 | 0.064087 | 6.5826 | -0.1831 | 0.14191 | -20.018 | -20.0134 | -0.32501 | -0.004578 | 6.8665
1268.5781 | 122.7448 | -54.6021 | 67.8955 | 0.39891 | 0.029704 | 0.025106 | 0.018666 | 0.062866 | 0.0093079 | 0.086344 | -47.9691 | 67.9733 | -54.895 | -54.8309 | 47.85 | 26.1108 | -0.10071 | 5.2734 | 67.923 | -54.9179 | -0.29297 | 0.07782 | 6.633 | -0.22888 | 0.086975 | -20.0455 | -20.0729 | -0.31586 | 0.027466 | 6.926
1269.5781 | 122.7356 | -54.6936 | 67.836 | 0.35313 | 0.028422 | 0.027456 | 0.017598 | 0.064361 | 0.011017 | 0.086985 | -48.0515 | 67.9047 | -54.9683 | -54.9225 | 47.7585 | 26.0605 | -0.054932 | 5.2551 | 67.8452 | -54.9957 | -0.27466 | 0.068664 | 6.6422 | -0.22888 | 0.073243 | -20.0775 | -20.0867 | -0.30212 | 0.009155 | 6.9168
1270.5781 | 122.7585 | -54.6433 | 67.8955 | 0.36839 | 0.027568 | 0.033224 | 0.018666 | 0.064361 | 0.010162 | 0.088481 | -48.0881 | 67.9276 | -54.9728 | -54.8767 | 47.7768 | 26.0376 | -0.022888 | 5.2505 | 67.9047 | -54.9683 | -0.32959 | 0.032043 | 6.5552 | -0.23346 | 0.091553 | -20.1187 | -20.1279 | -0.32501 | 0.009155 | 6.8848
1271.5781 | 122.7859 | -54.6341 | 67.8452 | 0.42943 | 0.026286 | 0.030874 | 0.015676 | 0.063507 | 0.0078125 | 0.088267 | -48.0377 | 67.9367 | -54.9545 | -54.8401 | 47.8638 | 26.1429 | -0.15106 | 5.4062 | 67.8589 | -54.9316 | -0.32044 | 0.091553 | 6.5964 | -0.20599 | 0.091553 | -19.9814 | -19.9951 | -0.29755 | 0.013733 | 6.9168
1272.5781 | 122.7859 | -54.57 | 67.9413 | 0.4218 | 0.028636 | 0.026388 | 0.016317 | 0.064361 | 0.0073853 | 0.088481 | -47.9919 | 67.9733 | -54.8996 | -54.7943 | 47.8821 | 26.1887 | -0.11444 | 5.4245 | 67.9413 | -54.863 | -0.32959 | 0.032044 | 6.5781 | -0.22431 | 0.068664 | -20.0592 | -20.0592 | -0.29297 | 0 | 6.9077
1273.5781 | 122.7127 | -54.7897 | 67.7719 | 0.37602 | 0.029704 | 0.026174 | 0.024648 | 0.06607 | 0.0082397 | 0.087199 | -48.2117 | 67.8314 | -55.0919 | -54.8767 | 47.7127 | 26.0239 | 0.018311 | 5.2872 | 67.7902 | -55.1239 | -0.30212 | 0.059509 | 6.5781 | -0.086975 | 0.24719 | -20.0592 | -20.0775 | -0.33417 | 0.01831 | 6.8802
1274.5781 | 122.7997 | -54.7806 | 67.7719 | 0.35313 | 0.027995 | 0.027883 | 0.01888 | 0.06607 | 0.0097351 | 0.087199 | -48.2117 | 67.836 | -55.1056 | -55.0507 | 47.6578 | 26.0239 | -0.24719 | 5.0629 | 67.7628 | -55.0919 | -0.32501 | 0.064087 | 6.5689 | -0.27008 | 0.041199 | -20.1141 | -20.105 | -0.31128 | -0.009156 | 6.8939
1275.5781 | 122.7585 | -54.7897 | 67.7261 | 0.4752 | 0.027995 | 0.031301 | 0.019307 | 0.062652 | 0.010162 | 0.089549 | -48.1888 | 67.7902 | -55.1147 | -55.0323 | 47.644 | 26.0056 | -0.041199 | 5.2277 | 67.7353 | -55.1376 | -0.32501 | 0.064087 | 6.601 | -0.24262 | 0.10528 | -20.0821 | -20.0912 | -0.3479 | 0.009156 | 6.926
1276.5781 | 122.6898 | -54.6982 | 67.7994 | -0.24959 | 0.026927 | 0.022756 | 0.017812 | 0.064789 | 0.0084533 | 0.088267 | -48.1522 | 67.8955 | -55.0095 | -54.9591 | 47.7219 | 26.1475 | 0 | 5.3238 | 67.8406 | -55.0232 | -0.31128 | 0.096131 | 6.546 | -0.26093 | 0.064087 | -20.0775 | -20.1187 | -0.32501 | 0.041199 | 6.8573
1277.5781 | 122.7448 | -54.4739 | 68.0923 | 1.0321 | 0.028422 | 0.027456 | 0.018026 | 0.062652 | 0.010162 | 0.088267 | -47.7081 | 68.1931 | -54.7348 | -54.689 | 48.0011 | 26.2848 | -0.009155 | 5.5618 | 68.1335 | -54.7943 | -0.26093 | 0.10071 | 6.7657 | -0.21515 | 0.10529 | -20.0912 | -20.1324 | -0.32043 | 0.041199 | 7.0267
1278.5781 | 122.7402 | -54.7714 | 67.7628 | 0.4218 | 0.029917 | 0.024679 | 0.01653 | 0.065643 | 0.0080261 | 0.087413 | -48.143 | 67.868 | -55.0644 | -54.9911 | 47.7081 | 26.2711 | -0.09613 | 5.3741 | 67.7902 | -55.0552 | -0.29297 | 0.10529 | 6.6284 | -0.21973 | 0.064087 | -20.0546 | -20.0821 | -0.28381 | 0.027466 | 6.9214
1279.5781 | 122.7402 | -54.6799 | 67.8406 | 0.30736 | 0.028849 | 0.030019 | 0.017171 | 0.063934 | 0.01059 | 0.09019 | -48.0835 | 67.9092 | -54.9683 | -54.9316 | 47.8638 | 26.8433 | -0.054932 | 5.5756 | 67.8635 | -54.9866 | -0.28839 | 0.068665 | 6.5964 | -0.25177 | 0.054931 | -19.9768 | -19.9997 | -0.3067 | 0.022888 | 6.8848
1280.5781 | 122.7814 | -54.7531 | 67.7628 | 0.36839 | 0.027568 | 0.028097 | 0.01888 | 0.064789 | 0.0093079 | 0.088267 | -48.175 | 67.8635 | -55.0598 | -55.0278 | 47.8409 | 27.9648 | -0.009155 | 5.4016 | 67.836 | -55.0781 | -0.3067 | 0.10071 | 6.5781 | -0.27466 | 0.050354 | -19.9219 | -19.9951 | -0.32501 | 0.073243 | 6.8848
1281.5781 | 122.7081 | -54.7256 | 67.868 | 0.3455 | 0.025859 | 0.031728 | 0.01653 | 0.064789 | 0.0086669 | 0.088053 | -48.1339 | 67.9001 | -55.0369 | -54.9911 | 47.9691 | 28.3447 | 0.004578 | 5.4794 | 67.8589 | -55.0598 | -0.31128 | 0.032043 | 6.5918 | -0.2655 | 0.068664 | -19.899 | -19.8898 | -0.33417 | -0.009155 | 6.9031
1282.5781 | 122.7127 | -54.7668 | 67.804 | 0.62016 | 0.02714 | 0.027028 | 0.016744 | 0.06543 | 0.0099487 | 0.089762 | -48.111 | 67.8497 | -55.0598 | -55.0232 | 47.9279 | 28.3951 | -0.027466 | 5.4703 | 67.8314 | -55.0827 | -0.29297 | 0.045776 | 6.6559 | -0.25635 | 0.05951 | -19.8761 | -19.9036 | -0.31586 | 0.027466 | 6.9489
1283.5781 | 122.7127 | -54.7577 | 67.7673 | 1.7188 | 0.027995 | 0.02297 | 0.01653 | 0.06308 | 0.0090943 | 0.091258 | -48.0423 | 67.8818 | -55.0461 | -55.0369 | 47.9874 | 28.4546 | -0.018311 | 5.4703 | 67.8177 | -55.1102 | -0.28839 | 0.11444 | 6.7154 | -0.27924 | 0.073242 | -19.78 | -19.8303 | -0.35248 | 0.050354 | 7.0038
1284.5781 | 122.6852 | -54.7531 | 67.7856 | 0.38365 | 0.029277 | 0.027242 | 0.019094 | 0.061371 | 0.0075989 | 0.086772 | -48.1339 | 67.8864 | -55.014 | -55.0919 | 47.937 | 28.5736 | 0.022888 | 5.5252 | 67.8314 | -55.0827 | -0.26093 | 0.10071 | 6.6193 | -0.33875 | -0.009155 | -19.8486 | -19.8944 | -0.32959 | 0.045776 | 6.8802
1285.5781 | 122.7585 | -54.6982 | 67.7856 | 0.45231 | 0.029063 | 0.029378 | 0.015249 | 0.064789 | 0.0099487 | 0.088267 | -48.1018 | 67.9092 | -54.9774 | -54.9637 | 48.0286 | 28.6652 | -0.09613 | 5.6946 | 67.8635 | -55.0323 | -0.27924 | 0.1236 | 6.5964 | -0.2655 | 0.068665 | -19.7571 | -19.8349 | -0.33417 | 0.077819 | 6.8756
1286.5781 | 122.7081 | -54.7028 | 67.7948 | 0.35313 | 0.028208 | 0.028524 | 0.018026 | 0.064575 | 0.010162 | 0.08784 | -48.1018 | 67.8589 | -55.014 | -54.982 | 48.0377 | 28.7842 | -0.059509 | 5.7175 | 67.8452 | -55.0461 | -0.31128 | 0.064087 | 6.601 | -0.27924 | 0.064087 | -19.7571 | -19.8074 | -0.34332 | 0.050354 | 6.9122
1287.5781 | 122.6669 | -54.7348 | 67.8314 | 0.38365 | 0.029917 | 0.028737 | 0.020589 | 0.062866 | 0.01059 | 0.08784 | -48.1476 | 67.9001 | -54.9911 | -55.0049 | 48.0148 | 28.8849 | 0.013733 | 5.6488 | 67.8726 | -55.0461 | -0.25635 | 0.068664 | 6.5872 | -0.27008 | 0.041199 | -19.8166 | -19.8578 | -0.31128 | 0.041199 | 6.8436
1288.5781 | 122.7081 | -54.6844 | 67.8818 | 0.33024 | 0.029704 | 0.029592 | 0.019307 | 0.065216 | 0.0095215 | 0.089762 | -48.0606 | 67.9733 | -54.9774 | -54.9408 | 48.056 | 29.155 | 0.013733 | 5.7312 | 67.9276 | -54.982 | -0.29297 | 0.091553 | 6.6238 | -0.25635 | 0.041199 | -19.8257 | -19.8715 | -0.29755 | 0.045776 | 6.9168
1289.5781 | 122.7127 | -54.6524 | 67.923 | 1.7264 | 0.027995 | 0.021261 | 0.018239 | 0.063934 | 0.01059 | 0.08784 | -47.8867 | 68.0237 | -54.9271 | -54.9088 | 48.1018 | 29.1733 | 0 | 5.777 | 67.9642 | -54.9454 | -0.27466 | 0.10071 | 6.7657 | -0.25635 | 0.036622 | -19.8212 | -19.8624 | -0.29297 | 0.041198 | 7.0404
1290.5781 | 122.6944 | -54.5517 | 67.9962 | 0.36839 | 0.02714 | 0.028524 | 0.016958 | 0.069275 | 0.0086669 | 0.086985 | -47.9553 | 68.0969 | -54.8492 | -54.6341 | 48.3536 | 29.2831 | -0.11444 | 5.8914 | 68.0328 | -54.8859 | -0.29755 | 0.10071 | 6.5964 | -0.082397 | 0.25177 | -19.6426 | -19.6793 | -0.33417 | 0.036621 | 6.8939
1291.5781 | 122.644 | -54.0985 | 68.4494 | 0.39891 | 0.028636 | 0.027883 | 0.018666 | 0.064148 | 0.01059 | 0.087199 | -47.5479 | 68.5226 | -54.3961 | -54.3961 | 48.5641 | 29.6539 | 0 | 6.2439 | 68.4723 | -54.4418 | -0.29755 | 0.073242 | 6.5506 | -0.29755 | 0.045776 | -19.8853 | -19.9081 | -0.34332 | 0.022888 | 6.8481
1292.5781 | 122.7036 | -54.1306 | 68.3945 | -0.12752 | 0.02949 | 0.027028 | 0.015676 | 0.065643 | 0.0093079 | 0.086344 | -47.5479 | 68.5364 | -54.4144 | -54.364 | 48.6237 | 29.9698 | -0.004578 | 6.2302 | 68.4631 | -54.451 | -0.28381 | 0.14191 | 6.5826 | -0.23346 | 0.086975 | -19.7708 | -19.8395 | -0.32044 | 0.068665 | 6.8665
1293.5781 | 122.7356 | -54.1901 | 68.3716 | 0.3455 | 0.02415 | 0.02596 | 0.015249 | 0.066925 | 0.011444 | 0.08784 | -47.6807 | 68.4311 | -54.4739 | -54.4098 | 48.5321 | 29.8874 | 0.027466 | 6.2119 | 68.4357 | -54.5105 | -0.28381 | 0.059509 | 6.5094 | -0.21973 | 0.10071 | -19.8395 | -19.9036 | -0.32043 | 0.064087 | 6.7932
1294.5781 | 122.6852 | -54.2038 | 68.3441 | 0.26921 | 0.027568 | 0.02831 | 0.018026 | 0.063721 | 0.0067443 | 0.088267 | -47.6257 | 68.4402 | -54.5059 | -54.451 | 48.468 | 29.7409 | 0.050354 | 6.2164 | 68.399 | -54.5151 | -0.30212 | 0.096131 | 6.5781 | -0.24719 | 0.064087 | -19.8761 | -19.931 | -0.31128 | 0.054932 | 6.8802
1295.5781 | 122.6944 | -54.0848 | 68.486 | 0.26158 | 0.02714 | 0.03066 | 0.018026 | 0.064789 | 0.0093079 | 0.088267 | -47.4747 | 68.5684 | -54.3732 | -54.3228 | 48.6053 | 29.8462 | 0.027466 | 6.3538 | 68.5135 | -54.3915 | -0.28839 | 0.082397 | 6.6101 | -0.23804 | 0.068664 | -19.8807 | -19.9081 | -0.3067 | 0.027466 | 6.8985
1296.5781 | 122.6578 | -53.9841 | 68.5547 | 0.32261 | 0.027568 | 0.029378 | 0.019948 | 0.065857 | 0.0093079 | 0.089549 | -47.4564 | 68.6554 | -54.3091 | -54.2908 | 48.5916 | 29.8691 | 0.004578 | 6.4133 | 68.5959 | -54.3274 | -0.32501 | 0.10071 | 6.5277 | -0.3067 | 0.036622 | -19.9631 | -20.0043 | -0.34332 | 0.041199 | 6.8527
1297.5781 | 122.6532 | -54.0527 | 68.5043 | 0.26921 | 0.02949 | 0.026601 | 0.017171 | 0.065002 | 0.0067443 | 0.087626 | -47.4655 | 68.605 | -54.332 | -54.2999 | 48.6053 | 29.9469 | 0.073242 | 6.4407 | 68.5913 | -54.3777 | -0.27924 | 0.10071 | 6.5872 | -0.24719 | 0.07782 | -19.899 | -19.986 | -0.32501 | 0.086976 | 6.8665
1298.5781 | 122.699 | -53.92 | 68.6462 | 0.24632 | 0.028208 | 0.02596 | 0.01888 | 0.065857 | 0.0088807 | 0.08784 | -47.3419 | 68.6966 | -54.2313 | -54.1763 | 48.7061 | 29.9973 | 0.059509 | 6.5964 | 68.7057 | -54.2587 | -0.31128 | 0.050354 | 6.5781 | -0.25635 | 0.082397 | -19.9402 | -19.9997 | -0.33874 | 0.05951 | 6.8893
1299.5781 | 122.6532 | -53.9749 | 68.5867 | 0.33024 | 0.028849 | 0.028097 | 0.019948 | 0.063934 | 0.0084533 | 0.088053 | -47.3923 | 68.7149 | -54.2404 | -54.213 | 48.6969 | 30.1071 | -0.013733 | 6.5506 | 68.6462 | -54.2816 | -0.2655 | 0.12817 | 6.5826 | -0.23804 | 0.068664 | -19.8898 | -19.9493 | -0.3067 | 0.059509 | 6.8481
1300.5781 | 122.7036 | -53.7277 | 68.8522 | 0.28447 | 0.027568 | 0.026601 | 0.018026 | 0.064148 | 0.0071717 | 0.089122 | -47.1405 | 68.9667 | -54.007 | -53.9886 | 48.8983 | 30.1987 | 0.027466 | 6.8115 | 68.9117 | -54.039 | -0.27924 | 0.11444 | 6.5872 | -0.26093 | 0.050354 | -19.9539 | -20.0134 | -0.31128 | 0.059509 | 6.8665
1301.5781 | 122.7264 | -53.7964 | 68.7424 | 0.1624 | 0.025645 | 0.025106 | 0.018666 | 0.064789 | 0.0073853 | 0.086985 | -47.2366 | 68.8293 | -54.0756 | -54.0024 | 48.8388 | 30.336 | 0.027466 | 6.8207 | 68.7881 | -54.1306 | -0.27924 | 0.086975 | 6.5598 | -0.20599 | 0.12817 | -19.9036 | -19.9493 | -0.33417 | 0.045776 | 6.839
1302.5781 | 122.7127 | -53.5767 | 68.9438 | 0.055586 | 0.030345 | 0.027242 | 0.020589 | 0.066284 | 0.0093079 | 0.086772 | -47.0215 | 69.0445 | -53.8559 | -53.8193 | 49.0723 | 30.9036 | 0.10986 | 7.1823 | 69.072 | -53.8879 | -0.27924 | 0.10071 | 6.5552 | -0.24262 | 0.068664 | -19.8715 | -19.9997 | -0.31128 | 0.12817 | 6.8344
1303.5781 | 122.7081 | -53.5217 | 69.0399 | 0.22343 | 0.02714 | 0.030446 | 0.018666 | 0.065643 | 0.0088807 | 0.085276 | -46.9437 | 69.1498 | -53.7598 | -53.7552 | 49.1089 | 30.7251 | 0 | 7.1594 | 69.104 | -53.8422 | -0.23804 | 0.10986 | 6.5781 | -0.23346 | 0.086975 | -19.931 | -19.9951 | -0.32043 | 0.064087 | 6.8161
1304.5781 | 122.6944 | -53.5217 | 69.0125 | 0.18529 | 0.027995 | 0.031942 | 0.019735 | 0.066711 | 0.0071717 | 0.088267 | -46.9757 | 69.1315 | -53.801 | -53.746 | 49.1135 | 30.9082 | 0.036621 | 7.1365 | 69.0857 | -53.8696 | -0.27923 | 0.11902 | 6.546 | -0.2243 | 0.1236 | -19.899 | -19.9722 | -0.3479 | 0.073242 | 6.8253
1305.5781 | 122.6852 | -53.6224 | 68.9072 | 0.12425 | 0.026927 | 0.028524 | 0.017385 | 0.064575 | 0.0082397 | 0.088481 | -47.0535 | 69.0353 | -53.8971 | -53.8239 | 49.0448 | 30.8578 | 0.013733 | 7.0908 | 69.0033 | -53.9474 | -0.27466 | 0.12817 | 6.5689 | -0.20142 | 0.1236 | -19.8624 | -19.9585 | -0.32501 | 0.09613 | 6.8436
1306.5781 | 122.6761 | -53.4027 | 69.1589 | 0.23869 | 0.028208 | 0.029378 | 0.018453 | 0.065002 | 0.011871 | 0.086985 | -46.9025 | 69.2413 | -53.6911 | -53.6591 | 49.1867 | 30.9494 | 0.059509 | 7.2647 | 69.223 | -53.7231 | -0.28839 | 0.082397 | 6.5002 | -0.25635 | 0.064087 | -19.9722 | -20.0363 | -0.32044 | 0.064086 | 6.7886
1307.5781 | 122.699 | -53.3524 | 69.191 | 0.26158 | 0.026499 | 0.025533 | 0.017598 | 0.065002 | 0.0082397 | 0.088908 | -46.8796 | 69.2322 | -53.7094 | -53.627 | 49.2004 | 31.041 | 0.050354 | 7.2968 | 69.2184 | -53.7003 | -0.35706 | 0.041199 | 6.4728 | -0.27466 | 0.073242 | -19.9905 | -20.018 | -0.3479 | 0.027466 | 6.8298
1308.5781 | 122.7493 | -53.1464 | 69.3924 | 0.17003 | 0.028636 | 0.030874 | 0.018666 | 0.065002 | 0.0086669 | 0.087626 | -46.6324 | 69.4977 | -53.4393 | -53.3661 | 49.6078 | 31.311 | 0.11902 | 7.6035 | 69.4885 | -53.4668 | -0.29297 | 0.10529 | 6.514 | -0.21973 | 0.10071 | -19.7845 | -19.8807 | -0.32043 | 0.09613 | 6.8069
1309.5781 | 122.7585 | -52.7847 | 69.7586 | 0.13951 | 0.027781 | 0.023824 | 0.019094 | 0.066711 | 0.0097351 | 0.089122 | -46.3028 | 69.8318 | -53.0869 | -53.0365 | 49.7726 | 31.3797 | 0.045776 | 7.8323 | 69.7495 | -53.1464 | -0.30212 | 0.073242 | 6.4819 | -0.25177 | 0.10986 | -19.986 | -19.9768 | -0.36163 | -0.009155 | 6.7841
1310.5781 | 122.7264 | -52.8717 | 69.6808 | 0.093733 | 0.028849 | 0.027242 | 0.017812 | 0.065216 | 0.011444 | 0.088053 | -46.3257 | 69.754 | -53.1464 | -53.0685 | 49.7314 | 31.4209 | 0.009155 | 7.8461 | 69.7495 | -53.1921 | -0.27466 | 0.073242 | 6.546 | -0.19684 | 0.1236 | -19.9493 | -20.018 | -0.32043 | 0.068665 | 6.8207
1311.5781 | 122.7493 | -52.6154 | 69.9509 | 0.17003 | 0.025645 | 0.02596 | 0.018453 | 0.066284 | 0.0071717 | 0.089762 | -46.1105 | 70.0607 | -52.8534 | -52.8214 | 49.9924 | 31.636 | 0.022888 | 8.2031 | 70.0012 | -52.9358 | -0.23804 | 0.10986 | 6.5048 | -0.20599 | 0.11444 | -19.9585 | -20.0089 | -0.32044 | 0.050354 | 6.7429
1312.5781 | 122.6852 | -52.684 | 69.8593 | 0.13951 | 0.027781 | 0.023824 | 0.02123 | 0.065643 | 0.0058899 | 0.088694 | -46.1929 | 69.96 | -52.9633 | -52.9266 | 49.8734 | 31.604 | 0.013733 | 8.1253 | 69.9417 | -53.0182 | -0.27924 | 0.10071 | 6.4911 | -0.24262 | 0.091552 | -19.986 | -20.0684 | -0.33417 | 0.082397 | 6.7703
1313.5781 | 122.7402 | -52.4277 | 70.0974 | 0.14714 | 0.025859 | 0.027242 | 0.019307 | 0.065857 | 0.0043945 | 0.085917 | -45.9641 | 70.1752 | -52.7344 | -52.6794 | 50.1663 | 31.897 | -0.009155 | 8.3084 | 70.166 | -52.7618 | -0.3067 | 0.07782 | 6.4636 | -0.25177 | 0.082398 | -19.931 | -19.9997 | -0.33417 | 0.068665 | 6.7703
1314.5781 | 122.7173 | -52.3773 | 70.1843 | -0.37929 | 0.024363 | 0.026174 | 0.018666 | 0.065857 | 0.0080261 | 0.088053 | -45.8862 | 70.2896 | -52.6566 | -52.6062 | 50.2213 | 31.9702 | 0.004578 | 8.4366 | 70.2347 | -52.6978 | -0.27924 | 0.10529 | 6.4911 | -0.22888 | 0.091553 | -19.9631 | -20.0134 | -0.32044 | 0.050354 | 6.7703
1315.5781 | 122.7036 | -52.1301 | 70.3857 | 0.063215 | 0.025859 | 0.025533 | 0.018666 | 0.065002 | 0.0058899 | 0.088267 | -45.7214 | 70.4681 | -52.446 | -52.3544 | 50.5554 | 32.1167 | 0.073242 | 8.7021 | 70.4819 | -52.4551 | -0.31586 | 0.082398 | 6.4087 | -0.2243 | 0.10071 | -19.8303 | -19.9265 | -0.32501 | 0.096131 | 6.7245
1316.5781 | 122.7539 | -51.7227 | 70.8435 | 0.11662 | 0.026286 | 0.024251 | 0.019094 | 0.06543 | 0.0088807 | 0.089335 | -45.3735 | 70.8069 | -52.0889 | -52.034 | 50.8392 | 32.2586 | 0.050354 | 8.9584 | 70.816 | -52.0477 | -0.36621 | -0.036621 | 6.3492 | -0.31128 | 0.013732 | -20.0043 | -19.9768 | -0.32501 | -0.027466 | 6.7154
1317.5781 | 122.7402 | -52.1072 | 70.4086 | 0.10899 | 0.025004 | 0.028097 | 0.018666 | 0.063293 | 0.0073853 | 0.087413 | -45.7306 | 70.5093 | -52.4323 | -52.4002 | 50.5142 | 32.2952 | 0.059509 | 8.7341 | 70.4865 | -52.4277 | -0.32501 | 0.10071 | 6.3766 | -0.29297 | 0.027465 | -19.8944 | -19.9722 | -0.32043 | 0.07782 | 6.7017
1318.5781 | 122.7539 | -51.8555 | 70.7016 | 0.093733 | 0.026072 | 0.026601 | 0.016744 | 0.065002 | 0.0084533 | 0.088694 | -45.4971 | 70.7245 | -52.1713 | -52.0981 | 50.8621 | 32.3456 | 0.073242 | 8.7845 | 70.7291 | -52.1851 | -0.31586 | 0.022888 | 6.3583 | -0.24261 | 0.086976 | -19.8395 | -19.8669 | -0.32959 | 0.027466 | 6.6742
1319.5781 | 122.7264 | -51.9562 | 70.5826 | 0.10136 | 0.024363 | 0.029165 | 0.016103 | 0.066925 | 0.0082397 | 0.085917 | -45.5612 | 70.6833 | -52.2675 | -52.1301 | 50.766 | 32.46 | 0.068665 | 8.8165 | 70.6604 | -52.2629 | -0.31128 | 0.10071 | 6.395 | -0.17395 | 0.13275 | -19.8166 | -19.8944 | -0.3067 | 0.077819 | 6.7062
1320.5781 | 122.6807 | -51.8188 | 70.7428 | 0.14714 | 0.02479 | 0.028737 | 0.018026 | 0.064575 | 0.0088807 | 0.087413 | -45.4788 | 70.7291 | -52.1988 | -52.0523 | 50.8621 | 32.7026 | 0.013733 | 8.9172 | 70.7474 | -52.1759 | -0.37994 | -0.013733 | 6.34 | -0.23346 | 0.1236 | -19.8807 | -19.8853 | -0.35705 | 0.004577 | 6.72
1321.5781 | 122.7585 | -51.6998 | 70.8847 | 0.055586 | 0.027568 | 0.026815 | 0.018666 | 0.066711 | 0.0080261 | 0.087199 | -45.163 | 71.0266 | -51.9333 | -51.9058 | 51.0452 | 32.8537 | -0.018311 | 9.0683 | 70.9213 | -52.0248 | -0.23346 | 0.14191 | 6.5369 | -0.20599 | 0.11902 | -19.8395 | -19.8761 | -0.32501 | 0.036621 | 6.7703
1322.5781 | 122.7402 | -7.576 | 115.1321 | -0.0054494 | 0.027568 | 0.049245 | 0.019094 | 0.062439 | 0.01059 | 0.081645 | -2.98 | 115.2786 | -7.8232 | -7.5165 | 91.5482 | 60.6033 | 0.20599 | 45.3049 | 115.21 | -7.814 | -0.24719 | 0.14648 | 4.5959 | 0.05951 | 0.29755 | -23.584 | -23.6618 | -0.23804 | 0.07782 | 4.8431
1323.5781 | 122.7402 | -6.9626 | 115.7272 | 0.063215 | 0.027568 | 0.050954 | 0.021657 | 0.064361 | 0.0097351 | 0.080577 | -2.3529 | 115.8371 | -7.2327 | -6.8985 | 92.1295 | 60.8917 | 0.045776 | 45.8038 | 115.7776 | -7.2281 | -0.27008 | 0.10986 | 4.6097 | 0.064086 | 0.32959 | -23.5977 | -23.6481 | -0.2655 | 0.050354 | 4.8798
1324.5781 | 122.7631 | -6.7017 | 115.9378 | -0.035967 | 0.02949 | 0.051381 | 0.021016 | 0.065002 | 0.0080261 | 0.080577 | -2.2339 | 115.947 | -7.1045 | -6.6467 | 92.4454 | 61.1984 | 0.13733 | 46.0236 | 116.0339 | -6.9717 | -0.40283 | 0.009155 | 4.4678 | 0.054931 | 0.32501 | -23.4924 | -23.5886 | -0.27008 | 0.096131 | 4.8706
1325.5781 | 122.7127 | -6.546 | 116.1301 | -0.035967 | 0.027995 | 0.0501 | 0.020162 | 0.064575 | 0.0093079 | 0.081431 | -2.0187 | 116.2399 | -6.8253 | -6.5231 | 92.6285 | 61.528 | 0.12817 | 46.1151 | 116.1987 | -6.8253 | -0.27924 | 0.10986 | 4.5273 | 0.022889 | 0.30212 | -23.5016 | -23.5703 | -0.27924 | 0.068664 | 4.8065
1326.5781 | 122.731 | -6.2988 | 116.3544 | 0.040327 | 0.02949 | 0.048818 | 0.020162 | 0.064148 | 0.0095215 | 0.081004 | -1.7349 | 116.4642 | -6.6193 | -6.2256 | 92.9077 | 61.9446 | 0.091553 | 46.312 | 116.4688 | -6.546 | -0.32043 | 0.10986 | 4.5639 | 0.073242 | 0.32043 | -23.4467 | -23.5611 | -0.24719 | 0.11444 | 4.8843
1327.5781 | 122.7493 | -6.3309 | 116.3544 | 0.017439 | 0.030986 | 0.051595 | 0.019521 | 0.063934 | 0.0090943 | 0.079509 | -1.7853 | 116.4413 | -6.6284 | -6.2393 | 92.8528 | 61.7661 | 0.11444 | 46.138 | 116.423 | -6.5643 | -0.29755 | 0.086975 | 4.5456 | 0.091553 | 0.32501 | -23.5016 | -23.5703 | -0.23346 | 0.068665 | 4.8431
1328.5781 | 122.7402 | -6.2576 | 116.4185 | -0.013079 | 0.029277 | 0.051168 | 0.018666 | 0.064148 | 0.0086669 | 0.081645 | -1.7715 | 116.5009 | -6.5552 | -6.2027 | 92.8894 | 61.7798 | 0.13275 | 46.1517 | 116.4917 | -6.5323 | -0.29755 | 0.082397 | 4.4861 | 0.054931 | 0.32959 | -23.5291 | -23.6023 | -0.27466 | 0.073242 | 4.7836
1329.5781 | 122.6715 | -6.0654 | 116.5924 | -0.051226 | 0.028422 | 0.054372 | 0.016103 | 0.062439 | 0.01059 | 0.081431 | -1.6113 | 116.684 | -6.3766 | -5.8594 | 93.1229 | 62.059 | -0.009155 | 46.3348 | 116.6748 | -6.3034 | -0.31128 | 0.091553 | 4.454 | 0.20599 | 0.44403 | -23.4695 | -23.5519 | -0.23804 | 0.082398 | 4.7653
1330.5781 | 122.7036 | -6.221 | 116.4551 | 0.0021796 | 0.02949 | 0.050741 | 0.022298 | 0.064148 | 0.0090943 | 0.080577 | -1.7075 | 116.5604 | -6.5094 | -6.1844 | 92.8665 | 61.9446 | 0.13275 | 46.1838 | 116.51 | -6.4728 | -0.28839 | 0.10529 | 4.5136 | 0.036621 | 0.28839 | -23.5886 | -23.6435 | -0.25177 | 0.054932 | 4.8019
1331.5781 | 122.6807 | -6.2988 | 116.3681 | 0.025068 | 0.029704 | 0.049245 | 0.021444 | 0.064148 | 0.011658 | 0.081645 | -1.8127 | 116.4963 | -6.5323 | -6.2668 | 92.775 | 61.6653 | 0.15106 | 46.0876 | 116.4642 | -6.546 | -0.23346 | 0.12817 | 4.4861 | 0.032043 | 0.27924 | -23.5931 | -23.6893 | -0.24719 | 0.09613 | 4.7195
1332.5781 | 122.7127 | -6.2027 | 116.4871 | -0.035967 | 0.02949 | 0.050313 | 0.017812 | 0.063293 | 0.01059 | 0.082713 | -1.5518 | 116.6428 | -6.4316 | -6.2027 | 92.7933 | 61.6287 | 0.13733 | 46.1746 | 116.5787 | -6.4407 | -0.22888 | 0.15564 | 4.6509 | 0 | 0.23804 | -23.6938 | -23.7854 | -0.23804 | 0.091552 | 4.8798
1333.5781 | 122.7264 | -6.1981 | 116.4642 | -0.020708 | 0.029063 | 0.05309 | 0.019735 | 0.064361 | 0.011017 | 0.081645 | -1.7166 | 116.597 | -6.4407 | -6.1707 | 92.9077 | 62.0087 | 0.1236 | 46.1884 | 116.5604 | -6.4636 | -0.24261 | 0.13275 | 4.4815 | 0.027466 | 0.29297 | -23.5565 | -23.6526 | -0.2655 | 0.096131 | 4.7241
1334.5781 | 122.7173 | -6.0562 | 116.6199 | 0.025068 | 0.028422 | 0.051381 | 0.019307 | 0.063721 | 0.0088807 | 0.081645 | -1.6022 | 116.7343 | -6.3354 | -6.0013 | 93.0084 | 62.0956 | 0.13275 | 46.3715 | 116.7206 | -6.3171 | -0.27924 | 0.11444 | 4.454 | 0.054931 | 0.31586 | -23.6115 | -23.7122 | -0.26093 | 0.10071 | 4.7333
1335.5781 | 122.7036 | -6.2027 | 116.4871 | 0.26158 | 0.029917 | 0.052663 | 0.019307 | 0.063721 | 0.0071717 | 0.078654 | -1.7441 | 116.6061 | -6.4407 | -6.1661 | 92.9306 | 62.2513 | 0.13733 | 46.2753 | 116.5741 | -6.4362 | -0.23804 | 0.11902 | 4.4586 | 0.036621 | 0.27008 | -23.5565 | -23.6435 | -0.23346 | 0.086975 | 4.6967
1336.5781 | 122.7036 | -6.2668 | 116.423 | -0.15804 | 0.029917 | 0.04775 | 0.015249 | 0.063934 | 0.011231 | 0.081218 | -1.799 | 116.4871 | -6.5186 | -6.2256 | 92.8345 | 62.0956 | 0.15106 | 46.2112 | 116.5009 | -6.5048 | -0.25177 | 0.064087 | 4.4678 | 0.041199 | 0.27924 | -23.5886 | -23.6664 | -0.23804 | 0.077819 | 4.7195
1337.5781 | 122.6852 | -6.1615 | 116.5237 | -0.066485 | 0.031413 | 0.050741 | 0.020162 | 0.062225 | 0.010376 | 0.079936 | -1.7166 | 116.5558 | -6.4636 | -5.9692 | 92.894 | 61.9308 | -0.022888 | 46.2662 | 116.5924 | -6.3995 | -0.30212 | 0.032043 | 4.4449 | 0.19226 | 0.4303 | -23.6298 | -23.6984 | -0.23804 | 0.068664 | 4.747
1338.5781 | 122.6715 | -6.221 | 116.4963 | -0.066485 | 0.029704 | 0.050313 | 0.015889 | 0.063293 | 0.0095215 | 0.081004 | -1.7166 | 116.6153 | -6.4178 | -6.1661 | 92.7795 | 61.8988 | 0.12817 | 46.3623 | 116.5649 | -6.4407 | -0.19684 | 0.11902 | 4.5044 | 0.054931 | 0.27466 | -23.7167 | -23.7854 | -0.21973 | 0.068664 | 4.7012
1339.5781 | 122.6852 | -6.1066 | 116.5695 | -0.058855 | 0.029063 | 0.047109 | 0.017812 | 0.061157 | 0.0093079 | 0.080149 | -1.6708 | 116.6107 | -6.3904 | -6.0928 | 92.8986 | 61.7294 | 0.16022 | 46.3806 | 116.6473 | -6.3904 | -0.28381 | 0.041199 | 4.4357 | 0.013733 | 0.29755 | -23.671 | -23.7488 | -0.28381 | 0.07782 | 4.7195
1340.5781 | 122.6944 | -6.4499 | 116.2079 | -0.013079 | 0.029277 | 0.051381 | 0.01888 | 0.061371 | 0.01059 | 0.08079 | -1.9958 | 116.3086 | -6.752 | -6.5048 | 92.5186 | 61.2671 | 0.10071 | 45.9183 | 116.304 | -6.6925 | -0.30212 | 0.10071 | 4.454 | -0.054932 | 0.18768 | -23.6893 | -23.7854 | -0.24261 | 0.09613 | 4.7562
1341.5781 | 122.6669 | -6.7062 | 115.9927 | -0.043596 | 0.028208 | 0.049245 | 0.020375 | 0.06308 | 0.010162 | 0.08314 | -2.3254 | 115.947 | -7.0816 | -6.7841 | 92.2073 | 60.997 | 0.16022 | 45.7443 | 116.0248 | -7.0084 | -0.37537 | -0.045777 | 4.3808 | -0.07782 | 0.2243 | -23.7854 | -23.8174 | -0.30212 | 0.032043 | 4.7562
1342.5781 | 122.699 | -6.6513 | 116.0294 | -0.10463 | 0.028208 | 0.048818 | 0.017385 | 0.061584 | 0.010803 | 0.080149 | -2.1332 | 116.0934 | -6.8802 | -6.5872 | 92.0517 | 61.0245 | 0.11444 | 45.8542 | 116.0751 | -6.9031 | -0.22888 | 0.064087 | 4.5181 | 0.064087 | 0.31586 | -23.9777 | -24.0234 | -0.25177 | 0.045776 | 4.747
1343.5781 | 122.7264 | -6.8481 | 115.7684 | -0.097002 | 0.028849 | 0.046895 | 0.01653 | 0.062652 | 0.0067443 | 0.080149 | -2.3529 | 115.8279 | -7.1136 | -6.7612 | 92.2714 | 61.2671 | 0.059509 | 45.7397 | 115.8371 | -7.0953 | -0.2655 | 0.059509 | 4.4952 | 0.086976 | 0.33417 | -23.497 | -23.5657 | -0.24719 | 0.068664 | 4.7607
1344.5781 | 122.6761 | -6.514 | 116.2033 | -0.051226 | 0.027354 | 0.046468 | 0.018666 | 0.06073 | 0.011017 | 0.079295 | -2.037 | 116.2857 | -6.7291 | -6.4453 | 92.4225 | 61.8347 | 0.091553 | 46.0785 | 116.2262 | -6.752 | -0.21515 | 0.082398 | 4.4769 | 0.068665 | 0.3067 | -23.7808 | -23.8037 | -0.23804 | 0.022888 | 4.6921
1345.5781 | 122.6807 | -6.5094 | 116.185 | -0.051226 | 0.028849 | 0.049032 | 0.01888 | 0.060516 | 0.0086669 | 0.08079 | -2.0279 | 116.2262 | -6.7429 | -6.4499 | 92.601 | 62.2604 | 0.13275 | 46.1426 | 116.2308 | -6.7245 | -0.23346 | 0.041198 | 4.4815 | 0.059509 | 0.27466 | -23.584 | -23.6298 | -0.21515 | 0.045776 | 4.715
1346.5781 | 122.7173 | -6.6559 | 116.0065 | -0.11226 | 0.026927 | 0.048604 | 0.019521 | 0.060303 | 0.0075989 | 0.082713 | -2.1744 | 116.066 | -6.9168 | -6.6055 | 92.3355 | 62.0865 | 0.091553 | 45.9824 | 116.0248 | -6.9122 | -0.26092 | 0.059509 | 4.4815 | 0.050354 | 0.3067 | -23.671 | -23.6893 | -0.25635 | 0.01831 | 4.7424
1347.5781 | 122.699 | -6.395 | 116.2766 | -0.0054494 | 0.029917 | 0.047964 | 0.019521 | 0.059235 | 0.01059 | 0.080363 | -1.9867 | 116.3406 | -6.6833 | -6.3721 | 92.6239 | 62.2055 | 0.16479 | 46.1655 | 116.3223 | -6.6422 | -0.28839 | 0.064087 | 4.4083 | 0.022888 | 0.27008 | -23.6526 | -23.6984 | -0.24719 | 0.045777 | 4.6967
1348.5781 | 122.6807 | -6.3309 | 116.3681 | 0.040327 | 0.029917 | 0.047536 | 0.019948 | 0.061371 | 0.0097351 | 0.081004 | -1.9043 | 116.4185 | -6.5918 | -6.2897 | 92.4866 | 62.0773 | 0.15564 | 46.2891 | 116.423 | -6.5735 | -0.26092 | 0.050354 | 4.4266 | 0.041199 | 0.28381 | -23.8815 | -23.9365 | -0.24261 | 0.054932 | 4.6875
1349.5781 | 122.7859 | -6.546 | 116.1301 | 0.055586 | 0.027781 | 0.048391 | 0.016103 | 0.061798 | 0.0084533 | 0.081858 | -2.0508 | 116.1346 | -6.7795 | -6.427 | 92.5827 | 61.8576 | 0.022888 | 46.1838 | 116.1392 | -6.7795 | -0.23346 | 0.004578 | 4.4952 | 0.11902 | 0.35248 | -23.5474 | -23.5565 | -0.23346 | 0.009155 | 4.7287
1350.5781 | 122.7585 | -6.4774 | 116.1209 | 0.54387 | 0.026499 | 0.049245 | 0.018453 | 0.060944 | 0.011444 | 0.081645 | -1.9867 | 116.1758 | -6.7291 | -6.3675 | 92.6514 | 61.7569 | -0.027466 | 46.1014 | 116.1575 | -6.7245 | -0.25177 | 0.054931 | 4.4907 | 0.10986 | 0.35706 | -23.4695 | -23.5062 | -0.24719 | 0.036621 | 4.7424
1351.5781 | 122.7173 | -6.2347 | 116.4185 | -0.028338 | 0.026927 | 0.049672 | 0.019521 | 0.060944 | 0.01059 | 0.08079 | -1.7761 | 116.4459 | -6.4957 | -6.1432 | 92.7612 | 61.7798 | 0.091553 | 46.3165 | 116.4459 | -6.5002 | -0.26093 | 0.027466 | 4.4586 | 0.091553 | 0.35706 | -23.6572 | -23.6847 | -0.2655 | 0.027466 | 4.7195
1352.5781 | 122.7539 | -6.2576 | 116.3773 | -0.058855 | 0.028208 | 0.052022 | 0.01653 | 0.061371 | 0.0084533 | 0.082072 | -1.8265 | 116.3727 | -6.5277 | -6.1752 | 92.5232 | 61.6974 | 0.068665 | 46.2524 | 116.3864 | -6.5186 | -0.27008 | -0.004577 | 4.4312 | 0.082397 | 0.34332 | -23.8541 | -23.8632 | -0.26093 | 0.009156 | 4.7012
1353.5781 | 122.731 | -6.1569 | 116.4597 | -0.074114 | 0.025859 | 0.048391 | 0.01888 | 0.061371 | 0.0082397 | 0.080577 | -1.7075 | 116.4871 | -6.4316 | -6.0654 | 93.013 | 61.8256 | 0.036621 | 46.3715 | 116.4825 | -6.395 | -0.27466 | 0.027466 | 4.4495 | 0.091552 | 0.32959 | -23.4467 | -23.4695 | -0.23804 | 0.022888 | 4.7241
1354.5781 | 122.7219 | -6.1111 | 116.5878 | -0.043596 | 0.026713 | 0.049459 | 0.021016 | 0.062012 | 0.0080261 | 0.080577 | -1.6754 | 116.6199 | -6.3492 | -6.0471 | 93.0634 | 61.8668 | 0.13275 | 46.312 | 116.629 | -6.3354 | -0.23804 | 0.032043 | 4.4357 | 0.064087 | 0.28839 | -23.5245 | -23.5657 | -0.2243 | 0.041198 | 4.6738
1355.5781 | 122.6898 | -6.1066 | 116.5787 | -0.035967 | 0.02949 | 0.04775 | 0.019735 | 0.061584 | 0.0078125 | 0.081218 | -1.6571 | 116.5878 | -6.3354 | -6.015 | 92.9718 | 61.8347 | 0.10529 | 46.312 | 116.6107 | -6.3309 | -0.22888 | 0.009156 | 4.4495 | 0.091552 | 0.31586 | -23.6069 | -23.6389 | -0.22431 | 0.032044 | 4.6783
1356.5781 | 122.8043 | -6.0104 | 116.5924 | -0.051226 | 0.026927 | 0.051381 | 0.015676 | 0.059235 | 0.011871 | 0.081431 | -1.5839 | 116.629 | -6.2531 | -5.9692 | 93.3014 | 62.1552 | -0.11902 | 46.3898 | 116.6153 | -6.2622 | -0.24262 | 0.036621 | 4.4266 | 0.041199 | 0.29297 | -23.291 | -23.3139 | -0.25177 | 0.022888 | 4.6692
1357.5781 | 122.7219 | -6.2027 | 116.3956 | -0.028338 | 0.025645 | 0.051809 | 0.01653 | 0.059662 | 0.0078125 | 0.082499 | -1.7899 | 116.423 | -6.4499 | -6.0562 | 93.0862 | 61.8713 | 0.009155 | 46.4951 | 116.4276 | -6.4774 | -0.24719 | 0.027466 | 4.4128 | 0.14649 | 0.42114 | -23.3093 | -23.3414 | -0.27466 | 0.032043 | 4.66
1358.5781 | 122.7722 | -6.2759 | 116.3452 | 0.15477 | 0.026499 | 0.047323 | 0.01888 | 0.060944 | 0.010162 | 0.080149 | -1.8585 | 116.3681 | -6.5369 | -6.1523 | 93.1503 | 62.0636 | -0.022888 | 46.1746 | 116.3589 | -6.5277 | -0.26092 | 0.022888 | 4.4174 | 0.1236 | 0.37537 | -23.1949 | -23.2086 | -0.25177 | 0.013733 | 4.6783
1359.5781 | 122.8088 | -6.3538 | 116.2628 | 1.3526 | 0.025004 | 0.050954 | 0.019094 | 0.057953 | 0.0088807 | 0.080363 | -1.9043 | 116.2674 | -6.6193 | -6.2393 | 93.1503 | 62.0132 | -0.032043 | 46.0419 | 116.2903 | -6.5964 | -0.2655 | 0.004578 | 4.4495 | 0.11444 | 0.35706 | -23.1125 | -23.14 | -0.24261 | 0.027466 | 4.715
1360.5781 | 122.7951 | -6.2988 | 116.2994 | -0.035967 | 0.022654 | 0.051381 | 0.018026 | 0.063507 | 0.010162 | 0.082286 | -1.886 | 116.3406 | -6.5735 | -6.1478 | 93.4067 | 62.0956 | -0.091553 | 46.0968 | 116.3177 | -6.5506 | -0.27466 | 0.041199 | 4.4128 | 0.15106 | 0.40283 | -22.8928 | -22.9111 | -0.25177 | 0.018311 | 4.6875
1361.5781 | 122.7539 | -4.9438 | 117.691 | 0.040327 | 0.026927 | 0.11141 | 0.022298 | 0.060516 | 0.0578 | 0.072673 | -0.6134 | 117.6727 | -5.2231 | -4.8386 | 5.1773 | 40.4434 | 0.009155 | 45.0073 | 117.6865 | -5.1865 | -0.27923 | -0.018311 | 4.3304 | 0.10529 | 0.3479 | -112.5137 | -112.5092 | -0.24261 | -0.004578 | 4.6097
1362.5781 | 122.7676 | -3.6804 | 118.959 | 0.070845 | 0.026072 | 0.11248 | 0.02123 | 0.059235 | 0.0578 | 0.072245 | 0.5722 | 118.895 | -3.978 | -3.5431 | 4.8889 | 40.9241 | 0.036621 | 45.9641 | 118.9957 | -3.9093 | -0.29755 | -0.064087 | 4.2526 | 0.13733 | 0.36621 | -114.0701 | -114.1068 | -0.22888 | 0.036622 | 4.5502
1363.5781 | 122.7905 | -3.5843 | 119.0277 | -0.051226 | 0.025859 | 0.10628 | 0.020589 | 0.062012 | 0.058014 | 0.074595 | 0.737 | 119.0414 | -3.8635 | -3.4287 | 4.5227 | 40.8875 | -0.036621 | 46.2524 | 119.0598 | -3.8086 | -0.27923 | 0.013733 | 4.3213 | 0.15564 | 0.37994 | -114.505 | -114.537 | -0.2243 | 0.032043 | 4.6005
1364.5781 | 122.8226 | -3.3142 | 119.3207 | 0.063215 | 0.026499 | 0.10927 | 0.019735 | 0.056885 | 0.06015 | 0.0731 | 0.99335 | 119.3253 | -3.5934 | -3.1265 | 4.3442 | 41.1392 | -0.07782 | 46.3074 | 119.3115 | -3.5614 | -0.27924 | 0.004577 | 4.3076 | 0.18768 | 0.43487 | -114.9765 | -114.9673 | -0.24719 | -0.009156 | 4.5868
1365.5781 | 122.7905 | -3.3005 | 119.3253 | 2.3826 | 0.027995 | 0.11205 | 0.020803 | 0.061157 | 0.059723 | 0.073527 | 0.9201 | 119.3207 | -3.6072 | -3.154 | 4.2618 | 41.3498 | -0.041199 | 46.3211 | 119.3115 | -3.5568 | -0.3067 | -0.004577 | 4.2206 | 0.14648 | 0.40283 | -115.0635 | -115.0497 | -0.25635 | -0.013733 | 4.5273
1366.5781 | 122.8043 | -3.3142 | 119.2932 | -0.013079 | 0.02479 | 0.10735 | 0.019521 | 0.059235 | 0.062073 | 0.070323 | 1.062 | 119.3024 | -3.5934 | -3.1906 | 4.2068 | 41.3177 | -0.068665 | 46.2616 | 119.3024 | -3.5568 | -0.27924 | 0.009155 | 4.3762 | 0.1236 | 0.36621 | -115.0864 | -115.0955 | -0.24262 | 0.009155 | 4.6555
1367.5781 | 122.7264 | -3.2272 | 119.4214 | -0.066485 | 0.026713 | 0.11055 | 0.021016 | 0.061798 | 0.057373 | 0.072245 | 1.0712 | 119.4214 | -3.4973 | -3.0899 | 4.1794 | 41.5695 | 0.054932 | 46.3715 | 119.4397 | -3.4561 | -0.27008 | 0 | 4.2984 | 0.13733 | 0.36621 | -115.242 | -115.2603 | -0.22888 | 0.01831 | 4.5685
1368.5781 | 122.731 | -3.1769 | 119.4717 | -0.058855 | 0.026072 | 0.10821 | 0.02123 | 0.061371 | 0.059937 | 0.073527 | 1.0895 | 119.4992 | -3.4424 | -3.0304 | 4.1245 | 41.5649 | 0.045776 | 46.3989 | 119.4626 | -3.4332 | -0.2655 | 0.027466 | 4.2664 | 0.14648 | 0.40283 | -115.3473 | -115.3381 | -0.25635 | -0.009156 | 4.5319
1369.5781 | 122.7539 | -3.1219 | 119.5129 | -0.013079 | 0.02714 | 0.11013 | 0.023366 | 0.061157 | 0.060577 | 0.0731 | 1.1444 | 119.5816 | -3.3691 | -2.9709 | 4.0604 | 41.6153 | 0.036621 | 46.4127 | 119.5541 | -3.3463 | -0.24719 | 0.068665 | 4.2664 | 0.15106 | 0.37537 | -115.4526 | -115.4938 | -0.2243 | 0.041199 | 4.5136
1370.5781 | 122.7722 | -3.0579 | 119.5496 | -0.097002 | 0.02714 | 0.10735 | 0.019948 | 0.060089 | 0.056305 | 0.074168 | 1.2131 | 119.5999 | -3.3005 | -2.8107 | 4.0787 | 41.5741 | -0.036621 | 46.5088 | 119.577 | -3.3142 | -0.24262 | 0.050354 | 4.2709 | 0.24719 | 0.50354 | -115.4709 | -115.4984 | -0.25635 | 0.027465 | 4.5136
1371.5781 | 122.7493 | -2.9297 | 119.6732 | -0.013079 | 0.024577 | 0.10821 | 0.02123 | 0.060944 | 0.059296 | 0.073527 | 1.3229 | 119.7327 | -3.186 | -2.7054 | 4.1061 | 41.7435 | -0.27008 | 46.5225 | 119.6732 | -3.1815 | -0.25635 | 0.059509 | 4.2526 | 0.2243 | 0.47608 | -115.567 | -115.567 | -0.25177 | 0 | 4.509
1372.5781 | 122.7585 | -2.9114 | 119.7281 | -0.028338 | 0.027568 | 0.11013 | 0.021657 | 0.060089 | 0.059723 | 0.073527 | 1.3229 | 119.7739 | -3.154 | -2.7695 | 3.9597 | 41.6245 | 0.032043 | 46.463 | 119.7281 | -3.1677 | -0.24262 | 0.045777 | 4.2343 | 0.14191 | 0.39825 | -115.7684 | -115.7684 | -0.25635 | 0 | 4.4769
1373.5781 | 122.7356 | -2.8702 | 119.7739 | 0.017439 | 0.026286 | 0.105 | 0.022939 | 0.059021 | 0.060364 | 0.071177 | 1.3962 | 119.8105 | -3.0991 | -2.7145 | 4.0833 | 41.716 | 0.032043 | 46.4767 | 119.8013 | -3.0991 | -0.22888 | 0.036621 | 4.2664 | 0.15564 | 0.38452 | -115.6906 | -115.7181 | -0.22888 | 0.027466 | 4.4952
1374.5781 | 122.7356 | -2.8381 | 119.8013 | -0.020708 | 0.026927 | 0.10885 | 0.023793 | 0.061157 | 0.060791 | 0.071604 | 1.3916 | 119.8425 | -3.0899 | -2.6733 | 3.9597 | 41.9495 | 0.032043 | 46.4859 | 119.8288 | -3.067 | -0.25177 | 0.041198 | 4.2297 | 0.16479 | 0.39368 | -115.8417 | -115.8691 | -0.22888 | 0.027465 | 4.4815
1375.5781 | 122.6669 | -2.916 | 119.783 | -0.15804 | 0.02949 | 0.11055 | 0.022298 | 0.06073 | 0.060791 | 0.073527 | 1.2909 | 119.8608 | -3.1448 | -2.7878 | 3.9093 | 41.9083 | 0.15106 | 46.3394 | 119.8151 | -3.1265 | -0.22888 | 0.07782 | 4.2068 | 0.12817 | 0.33875 | -115.8737 | -115.9058 | -0.21057 | 0.032043 | 4.4357
1376.5781 | 122.6395 | -2.9022 | 119.7739 | -0.14278 | 0.028636 | 0.11269 | 0.023153 | 0.059662 | 0.060364 | 0.073741 | 1.3138 | 119.8517 | -3.1403 | -2.7832 | 3.7262 | 41.7435 | 0.14191 | 46.2982 | 119.8517 | -3.1036 | -0.23804 | 0.07782 | 4.216 | 0.11902 | 0.32044 | -116.0477 | -116.1255 | -0.20142 | 0.07782 | 4.454
1377.5781 | 122.7081 | -2.8427 | 119.8105 | -0.028338 | 0.02479 | 0.11483 | 0.02358 | 0.061371 | 0.056091 | 0.071818 | 1.3779 | 119.838 | -3.0808 | -2.6825 | 3.685 | 41.8854 | 0.045776 | 46.4081 | 119.838 | -3.0487 | -0.23804 | 0.027466 | 4.2206 | 0.16022 | 0.36621 | -116.1255 | -116.153 | -0.20599 | 0.027466 | 4.4586
1378.5781 | 122.7356 | -2.8107 | 119.8563 | -0.028338 | 0.027781 | 0.11226 | 0.024862 | 0.059021 | 0.059723 | 0.075022 | 1.4008 | 119.8837 | -3.0624 | -2.6596 | 3.804 | 42.009 | 0.045776 | 46.376 | 119.8425 | -3.0579 | -0.25177 | 0.027466 | 4.2114 | 0.15106 | 0.39825 | -116.0522 | -116.0385 | -0.24719 | -0.013733 | 4.4632
1379.5781 | 122.6303 | -2.8519 | 119.8288 | -0.16567 | 0.026713 | 0.1129 | 0.022298 | 0.06073 | 0.060364 | 0.0731 | 1.3321 | 119.9066 | -3.0853 | -2.7283 | 3.8727 | 42.1371 | 0.14191 | 46.3257 | 119.8654 | -3.0624 | -0.23346 | 0.07782 | 4.184 | 0.1236 | 0.33417 | -115.9561 | -115.9927 | -0.21057 | 0.036621 | 4.4174
1380.5781 | 122.6624 | -2.8244 | 119.87 | -0.051226 | 0.026927 | 0.1112 | 0.022298 | 0.060944 | 0.059937 | 0.072673 | 1.3275 | 119.9158 | -3.0624 | -2.7283 | 3.7811 | 41.8121 | 0.14191 | 46.312 | 119.902 | -3.0487 | -0.23804 | 0.045776 | 4.1519 | 0.096131 | 0.32044 | -116.0889 | -116.1209 | -0.2243 | 0.032044 | 4.39
1381.5781 | 122.6578 | -2.7466 | 119.9249 | -1.4321 | 0.030345 | 0.11013 | 0.024648 | 0.062439 | 0.061646 | 0.072032 | 1.5518 | 120.0668 | -2.9617 | -2.655 | 3.7537 | 42.0639 | 0.13733 | 46.3257 | 119.9478 | -2.9892 | -0.21515 | 0.14191 | 4.2984 | 0.091553 | 0.33417 | -116.1713 | -116.1942 | -0.24261 | 0.022888 | 4.5136
1382.5781 | 122.6761 | -2.7512 | 119.9387 | -0.34114 | 0.02949 | 0.1112 | 0.021871 | 0.062652 | 0.060364 | 0.073954 | 1.5656 | 120.0943 | -2.9572 | -2.6413 | 3.7354 | 42.0639 | 0.1236 | 46.3989 | 119.9524 | -2.9892 | -0.20599 | 0.15564 | 4.3167 | 0.10986 | 0.3479 | -116.2033 | -116.217 | -0.23804 | 0.013733 | 4.5227
1383.5781 | 122.6761 | -2.7283 | 119.9249 | -0.051226 | 0.028636 | 0.11034 | 0.025716 | 0.062652 | 0.060791 | 0.072032 | 1.5793 | 120.108 | -2.9663 | -2.6779 | 4.2252 | 42.3065 | 0.13275 | 46.3257 | 119.9753 | -2.9526 | -0.23804 | 0.1831 | 4.3076 | 0.050354 | 0.27466 | -115.6998 | -115.7501 | -0.22431 | 0.050354 | 4.5456
1384.5781 | 122.644 | -2.7374 | 119.9295 | -0.15041 | 0.030131 | 0.10991 | 0.020803 | 0.061371 | 0.0578 | 0.073313 | 1.387 | 120.0256 | -2.9938 | -2.6505 | 4.097 | 42.4255 | 0.13733 | 46.3943 | 119.9707 | -2.9709 | -0.25635 | 0.096131 | 4.1245 | 0.086975 | 0.32043 | -115.8325 | -115.8737 | -0.23346 | 0.041199 | 4.3808
1385.5781 | 122.6486 | -2.7832 | 119.9066 | -0.089373 | 0.028208 | 0.11055 | 0.02358 | 0.06073 | 0.059082 | 0.072245 | 1.3824 | 119.9982 | -3.0167 | -2.6642 | 4.129 | 42.421 | 0.13275 | 46.3623 | 119.9249 | -3.0167 | -0.23346 | 0.091553 | 4.1656 | 0.11902 | 0.35248 | -115.7776 | -115.7959 | -0.23346 | 0.018311 | 4.3991
1386.5781 | 122.6624 | -2.7649 | 119.9203 | -0.028338 | 0.027354 | 0.11376 | 0.022725 | 0.060944 | 0.060364 | 0.073741 | 1.5518 | 120.0668 | -2.98 | -2.6825 | 3.7216 | 42.2745 | 0.1236 | 46.3211 | 119.9387 | -2.9709 | -0.21515 | 0.14648 | 4.3167 | 0.082398 | 0.28839 | -116.1987 | -116.217 | -0.20599 | 0.018311 | 4.5319
1387.5781 | 122.6303 | -2.8015 | 119.8791 | -1.188 | 0.027995 | 0.11248 | 0.024007 | 0.061798 | 0.059296 | 0.072459 | 1.4511 | 120.0348 | -3.0258 | -2.7008 | 3.6896 | 42.3203 | 0.14191 | 46.2708 | 119.9432 | -3.0121 | -0.2243 | 0.15564 | 4.2526 | 0.10071 | 0.31128 | -116.1896 | -116.2537 | -0.21057 | 0.064087 | 4.4769
1388.5781 | 122.7127 | -2.7924 | 119.9066 | -0.0054494 | 0.029917 | 0.11568 | 0.026784 | 0.063507 | 0.060577 | 0.071604 | 1.3779 | 120.0623 | -3.0075 | -2.6413 | 3.7125 | 42.4759 | 0.09613 | 46.2982 | 119.9478 | -3.0075 | -0.21515 | 0.15564 | 4.1702 | 0.15106 | 0.36621 | -116.1942 | -116.2354 | -0.21515 | 0.041199 | 4.3854
1389.5781 | 122.7081 | -2.7832 | 119.8791 | 0.017439 | 0.030772 | 0.10885 | 0.02593 | 0.063721 | 0.05716 | 0.072245 | 1.3779 | 120.0256 | -3.035 | -2.655 | 3.511 | 42.6498 | 0.09613 | 46.257 | 119.9387 | -3.0212 | -0.25177 | 0.14648 | 4.1611 | 0.12817 | 0.36621 | -116.3681 | -116.4276 | -0.23804 | 0.05951 | 4.4128
1390.5781 | 122.7264 | -2.742 | 119.9432 | 0.0021796 | 0.029063 | 0.10991 | 0.025289 | 0.063934 | 0.060791 | 0.073741 | 1.4008 | 120.0394 | -2.9892 | -2.6367 | 3.5202 | 42.7002 | 0.091553 | 46.2296 | 119.9661 | -2.9709 | -0.24719 | 0.096131 | 4.1428 | 0.10529 | 0.33417 | -116.423 | -116.4459 | -0.22888 | 0.022888 | 4.39
1391.5781 | 122.6624 | -2.774 | 119.9203 | 1.0245 | 0.030772 | 0.11098 | 0.021871 | 0.063721 | 0.061646 | 0.072673 | 1.3916 | 120.0439 | -2.9755 | -2.7008 | 3.6346 | 42.8833 | 0.15564 | 46.2341 | 119.957 | -3.0167 | -0.20142 | 0.1236 | 4.1657 | 0.073242 | 0.31586 | -116.2857 | -116.3223 | -0.24261 | 0.036621 | 4.3671
1392.5781 | 122.6669 | -2.7557 | 119.9341 | 1.2458 | 0.030772 | 0.1097 | 0.02358 | 0.063507 | 0.062073 | 0.072032 | 1.4328 | 120.108 | -2.948 | -2.6505 | 3.5202 | 42.8329 | 0.1236 | 46.2433 | 119.9753 | -2.9892 | -0.19226 | 0.17395 | 4.1885 | 0.10528 | 0.33874 | -116.4139 | -116.4551 | -0.23346 | 0.041199 | 4.3808
1393.5781 | 122.6898 | -2.7237 | 119.9387 | -0.013079 | 0.028849 | 0.11248 | 0.024434 | 0.065643 | 0.058869 | 0.073954 | 1.4191 | 120.0668 | -2.9755 | -2.6093 | 3.6896 | 43.0389 | 0.10071 | 46.3715 | 119.9844 | -2.9617 | -0.25177 | 0.12817 | 4.1428 | 0.11444 | 0.35248 | -116.2491 | -116.2949 | -0.23804 | 0.045776 | 4.3945
1394.5781 | 122.6715 | -2.7145 | 119.9387 | -0.043596 | 0.030131 | 0.11269 | 0.025075 | 0.063721 | 0.060364 | 0.073313 | 1.4374 | 120.0897 | -2.9526 | -2.5909 | 3.685 | 43.1717 | 0.10986 | 46.3303 | 120.0073 | -2.9388 | -0.23804 | 0.15106 | 4.1519 | 0.1236 | 0.3479 | -116.2537 | -116.3223 | -0.2243 | 0.068664 | 4.39
1395.5781 | 122.6852 | -2.6962 | 119.9432 | 0.13951 | 0.032054 | 0.11269 | 0.025075 | 0.065002 | 0.060364 | 0.072673 | 1.4832 | 120.1218 | -2.916 | -2.5589 | 3.6575 | 43.1946 | 0.032043 | 46.2845 | 120.0165 | -2.916 | -0.21973 | 0.17853 | 4.1794 | 0.13733 | 0.35706 | -116.2857 | -116.3589 | -0.21973 | 0.073242 | 4.3991
1396.5781 | 122.699 | -2.7054 | 119.8929 | 0.086103 | 0.028208 | 0.11098 | 0.026143 | 0.064148 | 0.063355 | 0.073313 | 1.4511 | 120.0806 | -2.9709 | -2.6001 | 3.7216 | 43.3594 | 0.050354 | 46.344 | 120.0073 | -2.9617 | -0.2655 | 0.18768 | 4.1565 | 0.10528 | 0.36163 | -116.1713 | -116.2857 | -0.25635 | 0.11444 | 4.422
1397.5781 | 122.6715 | -2.7054 | 119.8929 | 0.10899 | 0.030345 | 0.11483 | 0.024862 | 0.065857 | 0.063355 | 0.073954 | 1.4374 | 120.0668 | -2.9663 | -2.6184 | 3.653 | 43.483 | 0.054932 | 46.2982 | 119.9707 | -2.9709 | -0.26093 | 0.17395 | 4.1428 | 0.086975 | 0.35248 | -116.2399 | -116.3177 | -0.2655 | 0.07782 | 4.4037
1398.5781 | 122.6852 | -2.7786 | 119.8746 | -0.0054494 | 0.031413 | 0.11355 | 0.02123 | 0.063293 | 0.0625 | 0.072459 | 1.3367 | 120.0531 | -3.0212 | -2.6642 | 3.5706 | 43.4052 | 0.11444 | 46.2799 | 119.9615 | -3.0029 | -0.24262 | 0.17853 | 4.1153 | 0.11444 | 0.33875 | -116.304 | -116.391 | -0.22431 | 0.086975 | 4.3579
1399.5781 | 122.6807 | -2.742 | 119.8929 | 0.078474 | 0.031413 | 0.11547 | 0.023793 | 0.064789 | 0.061859 | 0.072886 | 1.4145 | 120.0623 | -2.9892 | -2.6138 | 3.6392 | 43.7027 | 0.064087 | 46.2112 | 119.9661 | -2.9617 | -0.24719 | 0.16937 | 4.1565 | 0.12817 | 0.3479 | -116.2537 | -116.3269 | -0.21973 | 0.073242 | 4.4037
1400.5781 | 122.6852 | -2.7786 | 119.8837 | 0.10136 | 0.031199 | 0.1129 | 0.026143 | 0.065002 | 0.062073 | 0.0731 | 1.3962 | 120.0577 | -3.0167 | -2.655 | 3.6255 | 43.5608 | 0.059509 | 46.2021 | 119.9615 | -2.9984 | -0.23804 | 0.17395 | 4.1748 | 0.1236 | 0.34332 | -116.2582 | -116.3361 | -0.21973 | 0.07782 | 4.4128
1401.5781 | 122.7036 | -2.7512 | 119.9203 | 0.086103 | 0.030131 | 0.11504 | 0.026143 | 0.06607 | 0.06015 | 0.072886 | 1.4008 | 120.0531 | -2.9892 | -2.6276 | 3.5706 | 43.7805 | 0.059509 | 46.2662 | 119.9799 | -2.9755 | -0.23804 | 0.13275 | 4.1519 | 0.1236 | 0.3479 | -116.3498 | -116.4093 | -0.2243 | 0.059509 | 4.39
1402.5781 | 122.6624 | -2.742 | 119.8929 | -0.23433 | 0.032481 | 0.11333 | 0.026998 | 0.06543 | 0.062927 | 0.072245 | 1.4465 | 120.1309 | -2.8976 | -2.6184 | 3.5614 | 43.8904 | 0.013733 | 46.2433 | 119.9936 | -2.9617 | -0.15564 | 0.23804 | 4.1885 | 0.1236 | 0.34332 | -116.3315 | -116.4322 | -0.21973 | 0.10071 | 4.3442
1403.5781 | 122.6715 | -2.7328 | 119.9203 | -0.28011 | 0.030345 | 0.11269 | 0.025075 | 0.065643 | 0.061218 | 0.072886 | 1.4191 | 120.1126 | -2.9114 | -2.6276 | 3.511 | 44.1605 | 0.036621 | 46.312 | 120.0073 | -2.9663 | -0.17853 | 0.19226 | 4.1519 | 0.10529 | 0.33875 | -116.4093 | -116.4963 | -0.23346 | 0.086975 | 4.3304
1404.5781 | 122.7036 | -2.7237 | 119.9295 | -0.50136 | 0.031413 | 0.11568 | 0.025716 | 0.066284 | 0.061432 | 0.074168 | 1.4236 | 120.1355 | -2.9114 | -2.6001 | 3.4424 | 44.1147 | 0.041199 | 46.3303 | 120.0256 | -2.948 | -0.18768 | 0.20599 | 4.1473 | 0.1236 | 0.3479 | -116.4871 | -116.5833 | -0.2243 | 0.096131 | 4.335
1405.5781 | 122.6715 | -2.7237 | 119.9432 | 0.040327 | 0.031199 | 0.11205 | 0.024434 | 0.064148 | 0.062927 | 0.073527 | 1.4191 | 120.1126 | -2.948 | -2.5818 | 3.4058 | 44.252 | 0.059509 | 46.463 | 120.0165 | -2.948 | -0.2243 | 0.16937 | 4.1428 | 0.14191 | 0.36621 | -116.5375 | -116.6107 | -0.2243 | 0.073242 | 4.3671
1406.5781 | 122.6807 | -2.7328 | 119.9524 | 0.093733 | 0.029063 | 0.11226 | 0.02593 | 0.06607 | 0.061432 | 0.0731 | 1.4465 | 120.1401 | -2.8656 | -2.5909 | 3.3829 | 44.2841 | 0.032043 | 46.4951 | 120.0348 | -2.9297 | -0.13275 | 0.18768 | 4.1794 | 0.14191 | 0.33874 | -116.5695 | -116.6519 | -0.19684 | 0.082397 | 4.3121
1407.5781 | 122.6486 | -2.7008 | 119.9432 | 0.36076 | 0.030772 | 0.11504 | 0.024221 | 0.064789 | 0.063355 | 0.075022 | 1.4603 | 120.1401 | -2.8793 | -2.5909 | 3.36 | 44.4122 | 0.027466 | 46.5134 | 120.0256 | -2.9297 | -0.17853 | 0.19684 | 4.1611 | 0.10986 | 0.33874 | -116.5833 | -116.6656 | -0.22888 | 0.082398 | 4.3396
1408.5781 | 122.6807 | -2.6917 | 119.957 | 0.055586 | 0.030131 | 0.1129 | 0.024434 | 0.06543 | 0.061005 | 0.07545 | 1.4511 | 120.1492 | -2.8702 | -2.6138 | 3.3508 | 44.5175 | 0.032043 | 46.5866 | 120.0485 | -2.9434 | -0.17853 | 0.19226 | 4.1428 | 0.077819 | 0.32959 | -116.6061 | -116.6977 | -0.25177 | 0.091553 | 4.3213
1409.5781 | 122.644 | -2.7283 | 119.9478 | 0.24632 | 0.031626 | 0.11867 | 0.024221 | 0.06543 | 0.060577 | 0.075236 | 1.4099 | 120.1309 | -2.9526 | -2.6413 | 3.2776 | 44.4351 | 0.050354 | 46.5042 | 120.0119 | -2.9434 | -0.22431 | 0.1831 | 4.1382 | 0.086975 | 0.30212 | -116.6702 | -116.7343 | -0.21515 | 0.064087 | 4.3625
1410.5781 | 122.6303 | -2.6779 | 119.9615 | 0.23106 | 0.029917 | 0.11397 | 0.024221 | 0.065643 | 0.063568 | 0.07545 | 1.4053 | 120.1447 | -2.9114 | -2.623 | 3.2593 | 44.5496 | 0.041199 | 46.5546 | 120.0577 | -2.916 | -0.23346 | 0.18311 | 4.0833 | 0.054931 | 0.29297 | -116.7023 | -116.7984 | -0.23804 | 0.09613 | 4.3167
1411.5781 | 122.699 | -2.6596 | 119.9524 | -0.63106 | 0.029277 | 0.11825 | 0.026998 | 0.065857 | 0.060791 | 0.073313 | 1.4603 | 120.163 | -2.8564 | -2.5635 | 3.273 | 44.5312 | 0.022888 | 46.582 | 120.0485 | -2.9297 | -0.19684 | 0.21057 | 4.1199 | 0.09613 | 0.36621 | -116.6794 | -116.7755 | -0.27008 | 0.09613 | 4.3167
1412.5781 | 122.6624 | -2.6825 | 119.9707 | 1.1695 | 0.030772 | 0.11226 | 0.026143 | 0.063293 | 0.061005 | 0.0731 | 1.4969 | 120.1996 | -2.861 | -2.5909 | 3.3005 | 44.7327 | 0.027466 | 46.6324 | 120.0485 | -2.9205 | -0.17853 | 0.22888 | 4.1794 | 0.091553 | 0.32959 | -116.6702 | -116.748 | -0.23804 | 0.07782 | 4.3579
1413.5781 | 122.6532 | -2.7008 | 119.9524 | 0.26158 | 0.031413 | 0.11376 | 0.027852 | 0.06607 | 0.059937 | 0.070323 | 1.4053 | 120.1218 | -2.9297 | -2.6276 | 3.3005 | 44.8242 | 0.032043 | 46.5775 | 120.0302 | -2.948 | -0.22888 | 0.16937 | 4.1061 | 0.073243 | 0.32044 | -116.6519 | -116.7297 | -0.24719 | 0.077819 | 4.335
1414.5781 | 122.6303 | -2.6917 | 119.9478 | 0.24632 | 0.032481 | 0.11739 | 0.025289 | 0.066711 | 0.06015 | 0.072886 | 1.4191 | 120.1035 | -2.9526 | -2.6184 | 3.2822 | 44.9341 | 0.041199 | 46.756 | 120.0485 | -2.9251 | -0.26093 | 0.15564 | 4.1107 | 0.073242 | 0.3067 | -116.6656 | -116.7664 | -0.23346 | 0.10071 | 4.3716
1415.5781 | 122.6257 | -2.7008 | 119.9387 | 0.22343 | 0.030131 | 0.11525 | 0.024648 | 0.064789 | 0.060791 | 0.073527 | 1.4236 | 120.1355 | -2.9297 | -2.6093 | 3.2913 | 45.0165 | 0.045776 | 46.9391 | 120.0531 | -2.916 | -0.22888 | 0.19684 | 4.1245 | 0.091553 | 0.3067 | -116.6473 | -116.7618 | -0.21515 | 0.11444 | 4.3533
1416.5781 | 122.6257 | -2.7054 | 119.9707 | 0.2158 | 0.029277 | 0.11654 | 0.02593 | 0.066711 | 0.060364 | 0.072886 | 1.387 | 120.1401 | -2.9343 | -2.6596 | 3.273 | 45.2087 | 0.059509 | 47.081 | 120.0577 | -2.9251 | -0.22888 | 0.16937 | 4.0924 | 0.045776 | 0.2655 | -116.6977 | -116.7847 | -0.21973 | 0.086975 | 4.3213
1417.5781 | 122.6074 | -2.6688 | 119.9615 | 0.27684 | 0.030986 | 0.11547 | 0.025716 | 0.065643 | 0.0625 | 0.073954 | 1.3962 | 120.1584 | -2.8976 | -2.6367 | 3.3463 | 45.2728 | 0.064087 | 47.2641 | 120.0623 | -2.9114 | -0.22888 | 0.19684 | 4.0649 | 0.032043 | 0.27466 | -116.6153 | -116.716 | -0.24261 | 0.10071 | 4.2938
1418.5781 | 122.6624 | -2.6688 | 119.957 | 0.19291 | 0.031626 | 0.11483 | 0.026357 | 0.066711 | 0.063355 | 0.073313 | 1.4328 | 120.1584 | -2.8839 | -2.5635 | 3.3875 | 45.314 | 0.045776 | 47.5296 | 120.076 | -2.8885 | -0.21515 | 0.20142 | 4.1016 | 0.10529 | 0.32501 | -116.5695 | -116.6885 | -0.21973 | 0.11902 | 4.3167
1419.5781 | 122.6395 | -2.6642 | 119.9753 | 0.20054 | 0.031413 | 0.11675 | 0.023153 | 0.066284 | 0.06485 | 0.073954 | 1.4328 | 120.1492 | -2.9022 | -2.5772 | 3.4012 | 45.4514 | 0.022888 | 47.7448 | 120.0851 | -2.9114 | -0.23804 | 0.17395 | 4.097 | 0.086976 | 0.33417 | -116.5741 | -116.684 | -0.24719 | 0.10986 | 4.335
1420.5781 | 122.612 | -2.6733 | 119.9982 | 0.37602 | 0.030986 | 0.11547 | 0.02593 | 0.065643 | 0.059723 | 0.074595 | 1.4053 | 120.1721 | -2.9114 | -2.6276 | 3.5889 | 45.7947 | 0.050354 | 47.7081 | 120.0897 | -2.9022 | -0.23804 | 0.17395 | 4.0787 | 0.045777 | 0.27466 | -116.4093 | -116.5009 | -0.22888 | 0.091553 | 4.3167
1421.5781 | 122.6074 | -2.6825 | 119.9615 | 0.26158 | 0.032481 | 0.11355 | 0.024434 | 0.065216 | 0.061005 | 0.0731 | 1.3733 | 120.1401 | -2.916 | -2.6413 | 3.717 | 45.9549 | 0.050354 | 47.731 | 120.0714 | -2.9251 | -0.23346 | 0.17853 | 4.0558 | 0.041199 | 0.28381 | -116.2445 | -116.3544 | -0.24262 | 0.10986 | 4.2892
1422.5781 | 122.6074 | -2.6825 | 119.957 | 0.23869 | 0.033976 | 0.11461 | 0.02593 | 0.064789 | 0.062714 | 0.072245 | 1.3733 | 120.1126 | -2.9343 | -2.655 | 3.6209 | 45.9961 | 0.059509 | 47.7585 | 120.0623 | -2.9205 | -0.25177 | 0.15564 | 4.0558 | 0.027466 | 0.2655 | -116.3361 | -116.4413 | -0.23804 | 0.10529 | 4.3076
1423.5781 | 122.6807 | -2.7008 | 119.9478 | 0.38365 | 0.030345 | 0.11547 | 0.02593 | 0.065002 | 0.06485 | 0.075663 | 1.3596 | 120.1263 | -2.9434 | -2.6917 | 3.4149 | 45.8038 | -0.041199 | 47.7081 | 120.0531 | -2.916 | -0.24261 | 0.17853 | 4.0604 | 0.009156 | 0.2243 | -116.5329 | -116.6382 | -0.21515 | 0.10529 | 4.303
1424.5781 | 122.5845 | -2.6596 | 119.9753 | 0.4218 | 0.02949 | 0.1144 | 0.023153 | 0.064789 | 0.062073 | 0.073741 | 1.3687 | 120.1538 | -2.9343 | -2.6093 | 3.6896 | 45.8954 | 0.21515 | 48.0057 | 120.0897 | -2.9022 | -0.27466 | 0.17853 | 4.0283 | 0.050354 | 0.29297 | -116.2857 | -116.4001 | -0.24262 | 0.11444 | 4.303
1425.5781 | 122.6212 | -2.7191 | 119.9203 | 0.25395 | 0.029704 | 0.11782 | 0.022725 | 0.06543 | 0.061218 | 0.072886 | 1.3184 | 120.0989 | -2.9663 | -2.655 | 3.717 | 46.1472 | 0.059509 | 47.9507 | 120.0119 | -2.9572 | -0.24719 | 0.17853 | 4.0375 | 0.064087 | 0.30212 | -116.2033 | -116.2949 | -0.23804 | 0.091553 | 4.2847
1426.5781 | 122.6395 | -2.6871 | 119.9799 | 0.26158 | 0.030558 | 0.11718 | 0.024862 | 0.06543 | 0.062073 | 0.0731 | 1.4053 | 120.1355 | -2.9251 | -2.6138 | 3.5202 | 46.019 | 0.054932 | 48.0652 | 120.0806 | -2.9251 | -0.23804 | 0.15564 | 4.0924 | 0.073242 | 0.31128 | -116.4597 | -116.5604 | -0.23804 | 0.10071 | 4.3304
1427.5781 | 122.6257 | -2.7145 | 119.9341 | 0.32261 | 0.031199 | 0.11696 | 0.024862 | 0.066284 | 0.0625 | 0.073527 | 1.3138 | 120.1538 | -2.9663 | -2.655 | 3.5065 | 46.1243 | 0.027466 | 48.0377 | 120.0531 | -2.9343 | -0.25177 | 0.21973 | 4.0283 | 0.05951 | 0.27924 | -116.4276 | -116.5466 | -0.21973 | 0.11902 | 4.2801
1428.5781 | 122.6395 | -2.7374 | 119.9387 | 0.30736 | 0.033335 | 0.11739 | 0.026998 | 0.065857 | 0.0625 | 0.073741 | 1.3275 | 120.1309 | -2.9617 | -2.655 | 3.4195 | 46.0739 | 0.009155 | 48.0011 | 120.0577 | -2.948 | -0.2243 | 0.19226 | 4.0649 | 0.082398 | 0.29297 | -116.5192 | -116.6382 | -0.21057 | 0.11902 | 4.2892
1429.5781 | 122.5983 | -2.7145 | 119.9112 | 0.27684 | 0.030772 | 0.11312 | 0.02593 | 0.066284 | 0.061218 | 0.0731 | 1.3275 | 120.1492 | -2.948 | -2.6825 | 3.3234 | 45.9686 | 0.032043 | 47.9919 | 120.0348 | -2.9663 | -0.23346 | 0.23804 | 4.0421 | 0.032044 | 0.28381 | -116.5878 | -116.7114 | -0.25177 | 0.1236 | 4.2755
1430.5781 | 122.6761 | -2.6917 | 119.9478 | 0.3455 | 0.033763 | 0.11504 | 0.023153 | 0.066925 | 0.06015 | 0.074595 | 1.2268 | 120.1263 | -2.9388 | -2.6184 | 3.3005 | 46.138 | 0.036621 | 48.1522 | 120.0485 | -2.9343 | -0.24719 | 0.17853 | 3.9185 | 0.073242 | 0.31586 | -116.6473 | -116.748 | -0.24261 | 0.10071 | 4.1656
1431.5781 | 122.6349 | -2.7008 | 119.9341 | 0.38365 | 0.030558 | 0.11504 | 0.023153 | 0.065216 | 0.063782 | 0.071604 | 1.355 | 120.1355 | -2.9388 | -2.5909 | 3.4012 | 46.2616 | -0.091553 | 48.0881 | 120.0531 | -2.9251 | -0.23804 | 0.20142 | 4.0558 | 0.10986 | 0.33417 | -116.5329 | -116.6519 | -0.2243 | 0.11902 | 4.2938
1432.5781 | 122.5983 | -2.6917 | 119.9524 | 0.27684 | 0.029917 | 0.11461 | 0.024434 | 0.06543 | 0.063355 | 0.072886 | 1.3916 | 120.108 | -2.916 | -2.623 | 3.186 | 46.0968 | 0.059509 | 48.0652 | 120.0485 | -2.9388 | -0.2243 | 0.15564 | 4.0833 | 0.068664 | 0.31586 | -116.7664 | -116.8625 | -0.24719 | 0.09613 | 4.3076
1433.5781 | 122.6349 | -2.7237 | 119.9295 | 0.24632 | 0.030345 | 0.11376 | 0.025075 | 0.064575 | 0.063141 | 0.072459 | 1.3596 | 120.1263 | -2.9617 | -2.6413 | 3.154 | 46.1197 | 0.036621 | 48.0194 | 120.0256 | -2.948 | -0.23804 | 0.19684 | 4.0833 | 0.082398 | 0.3067 | -116.7755 | -116.8716 | -0.2243 | 0.096131 | 4.3213
1434.5781 | 122.6166 | -2.7328 | 119.9112 | 0.37602 | 0.031199 | 0.11846 | 0.022939 | 0.065216 | 0.063141 | 0.074168 | 1.3184 | 120.1172 | -2.98 | -2.6688 | 3.1128 | 46.0098 | 0.009155 | 47.9507 | 119.9936 | -2.9526 | -0.24719 | 0.20599 | 4.0512 | 0.064087 | 0.28381 | -116.7984 | -116.8808 | -0.21973 | 0.082397 | 4.2984
1435.5781 | 122.6028 | -2.7237 | 119.9249 | 0.31499 | 0.031413 | 0.11675 | 0.024862 | 0.065216 | 0.063355 | 0.073527 | 1.3504 | 120.1447 | -2.9251 | -2.655 | 3.0853 | 45.8908 | 0 | 48.056 | 120.0623 | -2.948 | -0.20142 | 0.21973 | 4.0741 | 0.068665 | 0.29297 | -116.8396 | -116.9769 | -0.2243 | 0.13733 | 4.2755
1436.5781 | 122.6715 | -2.7237 | 119.9707 | -0.70735 | 0.029917 | 0.11034 | 0.024221 | 0.066711 | 0.061646 | 0.0731 | 1.4832 | 120.1401 | -2.9205 | -2.6596 | 3.0716 | 45.9869 | -0.027466 | 48.1018 | 120.0211 | -2.9434 | -0.19684 | 0.16937 | 4.2068 | 0.064087 | 0.28381 | -116.8991 | -116.9495 | -0.21973 | 0.050354 | 4.4037
1437.5781 | 122.612 | -2.7878 | 119.8791 | 0.41417 | 0.037394 | 0.11953 | 0.020803 | 0.064148 | 0.065918 | 0.074809 | 1.3412 | 120.0439 | -2.9984 | -2.71 | 3.1128 | 46.1563 | -0.041199 | 48.1293 | 119.9707 | -3.035 | -0.21057 | 0.16479 | 4.129 | 0.07782 | 0.32501 | -116.7664 | -116.8579 | -0.24719 | 0.091553 | 4.3396
1438.5781 | 122.6486 | -2.774 | 119.8883 | 0.37602 | 0.036967 | 0.12102 | 0.024434 | 0.068848 | 0.065064 | 0.075236 | 1.1398 | 120.0577 | -3.0258 | -2.7145 | 3.2318 | 46.257 | -0.082397 | 48.0927 | 119.9478 | -2.9938 | -0.25177 | 0.16937 | 3.9139 | 0.059509 | 0.27924 | -116.6565 | -116.716 | -0.21973 | 0.059509 | 4.1657
1439.5781 | 122.6257 | -2.7878 | 119.8929 | 0.26921 | 0.035899 | 0.12529 | 0.022512 | 0.065643 | 0.061005 | 0.072886 | 1.149 | 120.0577 | -3.0075 | -2.71 | 3.0579 | 46.0648 | 0.041199 | 48.0423 | 119.9524 | -3.0121 | -0.21973 | 0.16479 | 3.9368 | 0.07782 | 0.30212 | -116.835 | -116.8945 | -0.2243 | 0.05951 | 4.1565
1440.5781 | 122.6166 | -2.7283 | 119.902 | 0.26158 | 0.035258 | 0.12124 | 0.025075 | 0.066284 | 0.062073 | 0.076518 | 1.1719 | 120.1035 | -2.9663 | -2.6688 | 3.0533 | 46.0556 | 0.045776 | 48.143 | 120.0119 | -2.9709 | -0.23804 | 0.20142 | 3.9001 | 0.059509 | 0.30212 | -116.8488 | -116.9586 | -0.24262 | 0.10986 | 4.1382
1441.5781 | 122.6486 | -2.7237 | 119.9478 | 0.29973 | 0.035258 | 0.12508 | 0.022512 | 0.06607 | 0.062286 | 0.073741 | 1.1765 | 120.1309 | -2.9343 | -2.6413 | 3.0899 | 46.2662 | 0.009155 | 48.3444 | 120.0485 | -2.9251 | -0.21057 | 0.1831 | 3.9001 | 0.082398 | 0.28381 | -116.8579 | -116.9586 | -0.20142 | 0.10071 | 4.1107
1442.5781 | 122.6303 | -2.7283 | 119.9432 | 0.38365 | 0.035044 | 0.12252 | 0.025289 | 0.064789 | 0.061005 | 0.0731 | 1.1719 | 120.108 | -2.9572 | -2.6688 | 3.0624 | 46.0373 | 0.004578 | 48.2529 | 120.0439 | -2.9846 | -0.22888 | 0.16479 | 3.9001 | 0.059509 | 0.31586 | -116.8808 | -116.9815 | -0.25635 | 0.10071 | 4.129
1443.5781 | 122.6532 | -2.7145 | 119.9112 | 0.75749 | 0.032481 | 0.12273 | 0.025502 | 0.063507 | 0.0625 | 0.073954 | 1.2405 | 120.108 | -2.9388 | -2.6688 | 3.0579 | 45.9274 | -0.009155 | 48.2803 | 120.0073 | -2.9526 | -0.2243 | 0.19684 | 3.9551 | 0.045777 | 0.28381 | -116.8533 | -116.9495 | -0.23804 | 0.09613 | 4.1794
1444.5781 | 122.644 | -2.7054 | 119.9432 | 1.7493 | 0.035899 | 0.11846 | 0.02123 | 0.063721 | 0.061859 | 0.074595 | 1.2817 | 120.1538 | -2.9205 | -2.6459 | 3.0762 | 46.1792 | -0.004578 | 48.2254 | 120.0577 | -2.9388 | -0.21515 | 0.21057 | 3.9871 | 0.059509 | 0.29297 | -116.8671 | -116.9815 | -0.23346 | 0.11444 | 4.2023
1445.5781 | 122.6166 | -2.6962 | 119.9341 | 0.39891 | 0.033976 | 0.12743 | 0.021444 | 0.06543 | 0.063355 | 0.07545 | 1.1902 | 120.1401 | -2.9388 | -2.6001 | 3.1265 | 46.0327 | -0.004578 | 48.2483 | 120.0256 | -2.9388 | -0.24261 | 0.20599 | 3.8864 | 0.09613 | 0.33874 | -116.8076 | -116.8991 | -0.24261 | 0.091553 | 4.129
1446.5781 | 122.5983 | -2.742 | 119.9158 | 0.24632 | 0.038676 | 0.11718 | 0.025502 | 0.063934 | 0.061859 | 0.0731 | 1.1765 | 120.0806 | -2.9892 | -2.6779 | 3.0991 | 46.4493 | 0.054932 | 48.1613 | 120.0073 | -2.9892 | -0.24719 | 0.16479 | 3.9185 | 0.064087 | 0.31128 | -116.8167 | -116.9083 | -0.24719 | 0.091553 | 4.1656
1447.5781 | 122.6074 | -2.7054 | 119.9478 | 0.22343 | 0.035899 | 0.11974 | 0.025289 | 0.063293 | 0.061005 | 0.073954 | 1.1902 | 120.108 | -2.9617 | -2.6642 | 3.1174 | 46.1609 | 0.059509 | 48.143 | 120.0531 | -2.9343 | -0.25635 | 0.16022 | 3.8956 | 0.041198 | 0.27008 | -116.8304 | -116.9357 | -0.22888 | 0.10529 | 4.1519
1448.5781 | 122.6349 | -2.6871 | 119.9432 | 0.39891 | 0.035472 | 0.12145 | 0.025502 | 0.066711 | 0.068695 | 0.076518 | 1.2085 | 120.1126 | -2.9434 | -2.6596 | 3.3051 | 46.4722 | -0.082397 | 48.0972 | 120.0531 | -2.9114 | -0.25635 | 0.16937 | 3.8956 | 0.027466 | 0.25177 | -116.6382 | -116.748 | -0.2243 | 0.10986 | 4.1519
1449.5781 | 122.5891 | -2.6505 | 119.9707 | 0.38365 | 0.035044 | 0.12188 | 0.024007 | 0.066711 | 0.063568 | 0.072245 | 1.2085 | 120.1172 | -2.9297 | -2.5635 | 3.0991 | 46.1334 | 0.22888 | 48.3444 | 120.076 | -2.8976 | -0.27923 | 0.14648 | 3.8589 | 0.086975 | 0.33417 | -116.8716 | -116.9769 | -0.24719 | 0.10529 | 4.1382
1450.5781 | 122.6898 | -2.6642 | 119.9707 | 0.3455 | 0.033976 | 0.11782 | 0.022512 | 0.064148 | 0.061005 | 0.074382 | 1.2177 | 120.1126 | -2.9251 | -2.6047 | 3.1952 | 46.2433 | -0.054932 | 48.2025 | 120.0439 | -2.916 | -0.26093 | 0.14191 | 3.8818 | 0.05951 | 0.31128 | -116.7755 | -116.8488 | -0.25177 | 0.073242 | 4.1428
1451.5781 | 122.6761 | -2.655 | 119.9432 | 0.26921 | 0.034831 | 0.12124 | 0.024007 | 0.064575 | 0.062286 | 0.073741 | 1.2589 | 120.1401 | -2.9068 | -2.6001 | 3.2547 | 46.6187 | -0.050354 | 48.1659 | 120.0348 | -2.9114 | -0.25177 | 0.19684 | 3.9139 | 0.054931 | 0.31128 | -116.6885 | -116.7801 | -0.25635 | 0.091553 | 4.1656
1452.5781 | 122.6395 | -2.5177 | 120.1035 | 0.39891 | 0.036112 | 0.12102 | 0.024648 | 0.065643 | 0.063141 | 0.073954 | 1.4099 | 120.3094 | -2.7557 | -2.4399 | 3.3325 | 46.6507 | -0.064087 | 48.3078 | 120.2087 | -2.7512 | -0.23804 | 0.20599 | 3.9276 | 0.07782 | 0.31128 | -116.7709 | -116.8762 | -0.23346 | 0.10529 | 4.1656
1453.5781 | 122.6257 | -2.417 | 120.2087 | 0.3455 | 0.035472 | 0.11953 | 0.027639 | 0.064575 | 0.062286 | 0.073741 | 1.4465 | 120.314 | -2.7878 | -2.3758 | 3.6301 | 46.6324 | 0.054932 | 48.3078 | 120.282 | -2.6642 | -0.37079 | 0.10529 | 3.8635 | 0.041199 | 0.28839 | -116.5787 | -116.6519 | -0.24719 | 0.073242 | 4.2343
1454.5781 | 122.5983 | -2.4628 | 120.1584 | 0.3455 | 0.034831 | 0.1238 | 0.026571 | 0.063934 | 0.062073 | 0.073741 | 1.442 | 120.369 | -2.7054 | -2.3941 | 3.7308 | 46.9345 | 0.004578 | 48.5413 | 120.2866 | -2.7054 | -0.24261 | 0.21057 | 3.9047 | 0.068665 | 0.31128 | -116.4276 | -116.5558 | -0.24261 | 0.12817 | 4.1473
1455.5781 | 122.6486 | -2.4765 | 120.1675 | 0.54387 | 0.037821 | 0.11611 | 0.027639 | 0.064148 | 0.062927 | 0.074382 | 1.4557 | 120.3506 | -2.7054 | -2.4033 | 3.7628 | 46.9574 | -0.018311 | 48.5825 | 120.2499 | -2.7328 | -0.22888 | 0.1831 | 3.9322 | 0.073242 | 0.32959 | -116.4047 | -116.4871 | -0.25635 | 0.082397 | 4.1611
1456.5781 | 122.4335 | -118.9636 | 3.3829 | 1.0627 | 0.0070598 | 0.0024617 | 0.05306 | 0.063721 | -0.0022277 | 0.090403 | 0.10986 | 3.4378 | -0.26093 | -119.101 | -0.57678 | -3.8635 | -0.064087 | -46.6461 | 3.4424 | -119.3161 | 118.7027 | 0.054931 | 119.0735 | -0.13733 | 0.21515 | -3.9597 | -4.0192 | -0.35248 | 0.059509 | 0.37079
1457.5781 | 122.5662 | -118.3502 | 4.0421 | 0.4218 | 0.010264 | 0.0056661 | 0.051351 | 0.063507 | -0.0015869 | 0.09019 | 0.13733 | 4.0695 | -0.27924 | -118.428 | -0.44403 | -3.4927 | -0.15564 | -45.9366 | 4.1199 | -118.6569 | 118.071 | 0.027466 | 118.4875 | -0.07782 | 0.22888 | -4.4861 | -4.5639 | -0.3067 | 0.07782 | 0.41656
1458.5781 | 122.5891 | -118.1534 | 4.2892 | 0.4218 | 0.0070598 | 0.00053914 | 0.05071 | 0.066498 | 0.0011901 | 0.090403 | 0.16479 | 4.2984 | -0.28839 | -118.2358 | -0.43945 | -3.3783 | -0.13733 | -45.813 | 4.3304 | -118.4784 | 117.865 | 0.009155 | 118.3182 | -0.082398 | 0.24262 | -4.7287 | -4.7699 | -0.32501 | 0.041198 | 0.45319
1459.5781 | 122.5937 | -117.7277 | 4.7058 | 0.43706 | 0.0096232 | 0.0058797 | 0.051564 | 0.065216 | 0.0020447 | 0.09254 | 0.16937 | 4.7241 | -0.28381 | -117.8329 | -0.4303 | -3.2593 | -0.14191 | -45.5109 | 4.747 | -118.0618 | 117.4438 | 0.01831 | 117.897 | -0.10529 | 0.22888 | -5.1361 | -5.1773 | -0.33417 | 0.041198 | 0.45319
1460.5781 | 122.5845 | -117.3706 | 5.1224 | 0.36839 | 0.0081278 | 0.0028889 | 0.052846 | 0.063293 | 0.0037537 | 0.093394 | 0.16022 | 5.1315 | -0.31128 | -117.5629 | -0.46234 | -3.0533 | 0.009155 | -45.3918 | 5.1682 | -117.6865 | 117.0593 | 0.009156 | 117.5308 | -0.19226 | 0.1236 | -5.5847 | -5.6305 | -0.31586 | 0.045777 | 0.4715
1461.5781 | 122.5891 | -117.485 | 4.9942 | 0.39128 | 0.0098368 | 0.0037435 | 0.049855 | 0.064148 | -0.0005189 | 0.091471 | 0.15564 | 5.0171 | -0.30212 | -117.627 | -0.45776 | -3.1494 | -0.30212 | -45.5154 | 5.0583 | -117.778 | 117.1829 | 0.022888 | 117.6407 | -0.14191 | 0.15106 | -5.452 | -5.5161 | -0.29297 | 0.064087 | 0.45776
1462.5781 | 122.6028 | -117.2928 | 5.1682 | 0.35313 | 0.0070598 | -0.00052906 | 0.049215 | 0.06543 | 0.0022583 | 0.090831 | 0.17395 | 5.2002 | -0.28839 | -117.4164 | -0.43488 | -3.1174 | -0.086975 | -45.3186 | 5.246 | -117.6361 | 117.0044 | 0.032043 | 117.4667 | -0.1236 | 0.21973 | -5.603 | -5.6808 | -0.34332 | 0.07782 | 0.46234
1463.5781 | 122.5983 | -117.4164 | 5.0812 | 0.42943 | 0.0094096 | 0.0013935 | 0.05306 | 0.06308 | 0.0020447 | 0.093608 | 0.16479 | 5.1041 | -0.25635 | -117.5491 | -0.43488 | -3.1815 | -0.082397 | -45.5109 | 5.1178 | -117.7597 | 117.16 | 0.022888 | 117.5812 | -0.13275 | 0.21057 | -5.5161 | -5.5527 | -0.34332 | 0.036621 | 0.42114
1464.5781 | 122.6624 | -117.3569 | 5.0674 | 0.40654 | 0.0079142 | 0.00075274 | 0.051351 | 0.06543 | -9.1495e-05 | 0.090831 | 0.21515 | 5.0629 | -0.27466 | -117.485 | -0.34332 | -3.1128 | -0.1831 | -45.4514 | 5.0995 | -117.7185 | 117.0822 | -0.004578 | 117.572 | -0.12817 | 0.23346 | -5.4108 | -5.4428 | -0.36163 | 0.032043 | 0.48981
1465.5781 | 122.6761 | -117.0868 | 5.3513 | 0.42943 | 0.0083416 | 0.0056661 | 0.049215 | 0.063934 | 0.0018311 | 0.091685 | 0.21973 | 5.3741 | -0.27466 | -117.2012 | -0.36621 | -3.0212 | -0.15106 | -45.2454 | 5.4108 | -117.4438 | 116.8121 | 0.022889 | 117.3065 | -0.11444 | 0.24262 | -5.7175 | -5.777 | -0.35706 | 0.05951 | 0.49439
1466.5781 | 122.6669 | -117.1783 | 5.3146 | 0.43706 | 0.005778 | 0.0039571 | 0.051351 | 0.062866 | 0.0018311 | 0.091471 | 0.21057 | 5.3192 | -0.27924 | -117.2653 | -0.36163 | -3.0762 | -0.14191 | -45.3918 | 5.3284 | -117.4896 | 116.8991 | 0.004578 | 117.3889 | -0.086975 | 0.2243 | -5.6763 | -5.69 | -0.31128 | 0.013733 | 0.48981
1467.5781 | 122.5937 | -117.215 | 5.2963 | 0.37602 | 0.0068462 | 0.0024617 | 0.053487 | 0.061371 | 0.0005493 | 0.092112 | 0.17395 | 5.3009 | -0.29755 | -117.3935 | -0.4715 | -3.2181 | 0.059509 | -45.5978 | 5.3467 | -117.5903 | 116.9174 | 0.004577 | 117.3889 | -0.17853 | 0.19684 | -5.7678 | -5.8182 | -0.37537 | 0.050354 | 0.4715
1468.5781 | 122.6624 | -113.7543 | 8.7204 | 0.41417 | 0.010264 | 0.0058797 | 0.048787 | 0.063721 | 0.0037537 | 0.091685 | 0.31586 | 8.7387 | -0.26093 | -113.8916 | -0.25635 | -1.6891 | -0.10071 | -42.7505 | 8.7524 | -114.1159 | 113.4933 | 0.01831 | 114.0701 | -0.13733 | 0.2243 | -8.9767 | -9.0088 | -0.36163 | 0.032043 | 0.57678
1469.5781 | 122.6166 | -113.9191 | 8.5602 | 0.38365 | 0.010478 | 0.0063069 | 0.047719 | 0.06308 | 0.0028991 | 0.091471 | 0.31128 | 8.606 | -0.27924 | -114.0518 | -0.27466 | -1.7944 | -0.082397 | -42.9428 | 8.638 | -114.2578 | 113.6398 | 0.045776 | 114.2303 | -0.13275 | 0.20599 | -8.8348 | -8.9127 | -0.33875 | 0.077819 | 0.59051
1470.5781 | 122.6395 | -113.8458 | 8.6655 | 0.4218 | 0.0087688 | 0.0097249 | 0.048787 | 0.064148 | 0.0037537 | 0.091258 | 0.30212 | 8.67 | -0.27924 | -113.9832 | -0.27924 | -1.7807 | -0.054932 | -42.9611 | 8.7112 | -114.1846 | 113.5666 | 0.004578 | 114.1479 | -0.13733 | 0.20142 | -8.9447 | -8.9905 | -0.33874 | 0.045777 | 0.58136
1471.5781 | 122.7173 | -113.8962 | 8.5327 | 0.46757 | 0.0085552 | 0.0033161 | 0.044729 | 0.064361 | 0.0050353 | 0.089335 | 0.32044 | 8.551 | -0.26093 | -114.0335 | -0.21973 | -1.7624 | -0.14191 | -42.984 | 8.5693 | -114.2578 | 113.6353 | 0.01831 | 114.2166 | -0.13733 | 0.2243 | -8.7524 | -8.7891 | -0.36163 | 0.036621 | 0.58136
1472.5781 | 122.6669 | -113.7131 | 8.7708 | 0.43706 | 0.010905 | 0.0024617 | 0.045583 | 0.06607 | 0.0026855 | 0.091258 | 0.31128 | 8.7708 | -0.27008 | -113.8275 | -0.22888 | -1.7212 | -0.13275 | -42.8741 | 8.7891 | -114.0564 | 113.443 | 0 | 114.0244 | -0.11444 | 0.22888 | -8.9996 | -9.0179 | -0.34332 | 0.01831 | 0.58136
1473.5781 | 122.6715 | -113.5025 | 9.0042 | 0.39891 | 0.0096232 | 0.0011799 | 0.047719 | 0.062866 | 0.0037537 | 0.091258 | 0.3067 | 8.9905 | -0.27924 | -113.7039 | -0.28839 | -1.7029 | -0.27924 | -42.9245 | 9.0271 | -113.8504 | 113.2233 | -0.013732 | 113.8092 | -0.20142 | 0.14648 | -9.2926 | -9.3155 | -0.3479 | 0.022889 | 0.58594
1474.5781 | 122.6028 | -113.6444 | 8.9035 | 0.35313 | 0.0079142 | 0.0035299 | 0.049642 | 0.063293 | 0.0039673 | 0.090617 | 0.28839 | 8.9035 | -0.27008 | -113.8 | -0.28839 | -1.7853 | -0.022888 | -43.0252 | 8.9264 | -113.9877 | 113.3743 | 0 | 113.9328 | -0.15564 | 0.18768 | -9.1919 | -9.2148 | -0.34332 | 0.022889 | 0.55847
1475.5781 | 122.6257 | -113.681 | 8.8531 | -1.6992 | 0.0083416 | 0.0069477 | 0.045797 | 0.065643 | 0.0026855 | 0.092967 | 0.39368 | 8.8852 | -0.26093 | -113.8046 | -0.27008 | -1.7944 | -0.032043 | -43.0115 | 8.9127 | -114.0335 | 113.4201 | 0.032044 | 114.0747 | -0.1236 | 0.22888 | -9.1232 | -9.1827 | -0.35248 | 0.05951 | 0.6546
1476.5781 | 122.612 | -113.6993 | 8.8211 | 0.38365 | 0.0089824 | 0.0060933 | 0.049001 | 0.069061 | 0.0048217 | 0.088481 | 0.29297 | 8.8486 | -0.28839 | -113.6993 | -0.15564 | -1.8265 | -0.050354 | -43.0069 | 8.876 | -114.0427 | 113.4109 | 0.027466 | 113.9923 | 0 | 0.34332 | -8.9767 | -9.0317 | -0.34332 | 0.054932 | 0.58136
1477.5781 | 122.6532 | -113.7039 | 8.8303 | 0.39128 | 0.010478 | 0.0065205 | 0.049001 | 0.06308 | 0.0022583 | 0.088694 | 0.30212 | 8.8394 | -0.27008 | -113.8412 | -0.27008 | -1.8173 | -0.073242 | -43.1717 | 8.8806 | -114.061 | 113.4338 | 0.009156 | 114.006 | -0.13733 | 0.21973 | -9.1003 | -9.1507 | -0.35706 | 0.050354 | 0.57221
1478.5781 | 122.6486 | -113.681 | 8.8348 | 0.2158 | 0.0081278 | 0.0039571 | 0.049001 | 0.063293 | 0.0035401 | 0.090617 | 0.29297 | 8.8486 | -0.2655 | -113.8321 | -0.31128 | -1.8356 | -0.032043 | -43.2449 | 8.8806 | -114.0518 | 113.4155 | 0.013733 | 113.974 | -0.15106 | 0.21973 | -9.1461 | -9.1919 | -0.37079 | 0.045776 | 0.55847
1479.5781 | 122.6257 | -113.7772 | 8.7753 | 0.38365 | 0.0087688 | 0.0078023 | 0.046865 | 0.066284 | 0.0046081 | 0.091044 | 0.26093 | 8.7982 | -0.26093 | -113.8733 | -0.28381 | -1.9043 | -0.009155 | -43.5425 | 8.844 | -114.1068 | 113.5162 | 0.022888 | 114.0381 | -0.09613 | 0.23346 | -9.0591 | -9.1278 | -0.32959 | 0.068664 | 0.52185
1480.5781 | 122.6212 | -113.6948 | 8.8394 | 0.28447 | 0.0096232 | 0.0063069 | 0.048574 | 0.064361 | 0.0039673 | 0.091044 | 0.30212 | 8.8303 | -0.27008 | -113.8458 | -0.33417 | -1.9089 | 0.054932 | -43.5745 | 8.8898 | -114.0518 | 113.4247 | -0.009156 | 113.9969 | -0.15106 | 0.20599 | -9.1736 | -9.2239 | -0.35706 | 0.050354 | 0.57221
1481.5781 | 122.6303 | -113.7177 | 8.8348 | 0.32261 | 0.0096232 | 0.0082295 | 0.049642 | 0.066498 | 0.0033265 | 0.090617 | 0.31586 | 8.8577 | -0.2655 | -113.8412 | -0.34332 | -1.8997 | 0.032043 | -43.6111 | 8.8806 | -114.0564 | 113.4521 | 0.022888 | 114.0335 | -0.1236 | 0.21515 | -9.1782 | -9.2239 | -0.33875 | 0.045776 | 0.58136
1482.5781 | 122.5937 | -113.7177 | 8.8348 | 0.29973 | 0.01005 | 0.00075274 | 0.050069 | 0.065643 | 0.0061035 | 0.091471 | 0.29297 | 8.8715 | -0.2655 | -113.8824 | -0.48523 | -1.9775 | 0.018311 | -43.721 | 8.8715 | -114.0701 | 113.4521 | 0.036621 | 114.0106 | -0.16479 | 0.18768 | -9.3201 | -9.3567 | -0.35248 | 0.036621 | 0.55847
1483.5781 | 122.5983 | -113.7222 | 8.8303 | 0.27684 | 0.0094096 | 0.0086567 | 0.047506 | 0.066925 | 0.0022583 | 0.090831 | 0.3067 | 8.8486 | -0.28381 | -113.8687 | -0.39368 | -1.9363 | 0.027466 | -43.7302 | 8.8943 | -114.093 | 113.4384 | 0.018311 | 114.0289 | -0.14648 | 0.22431 | -9.2239 | -9.288 | -0.37079 | 0.064087 | 0.59051
1484.5781 | 122.6395 | -113.7222 | 8.8348 | 0.23869 | 0.010691 | 0.00096634 | 0.04836 | 0.065857 | -9.1495e-05 | 0.089122 | 0.3067 | 8.8303 | -0.26093 | -113.8733 | -0.41657 | -1.9547 | 0.027466 | -43.7256 | 8.8806 | -114.0747 | 113.4613 | -0.004578 | 114.0289 | -0.15106 | 0.20142 | -9.2514 | -9.2972 | -0.35248 | 0.045776 | 0.56763
1485.5781 | 122.6074 | -113.7909 | 8.7616 | 0.28447 | 0.0089824 | 0.0033161 | 0.050069 | 0.066498 | 0.0031127 | 0.091044 | 0.28839 | 8.7891 | -0.27466 | -113.9694 | -0.40741 | -1.9821 | 0.004578 | -43.7805 | 8.8211 | -114.1342 | 113.5162 | 0.027465 | 114.0793 | -0.17853 | 0.16479 | -9.169 | -9.2285 | -0.34332 | 0.059509 | 0.56305
1486.5781 | 122.6303 | -113.7314 | 8.8348 | 0.26921 | 0.010478 | 0.0041707 | 0.050069 | 0.064789 | 0.0022583 | 0.091685 | 0.31128 | 8.8715 | -0.2655 | -113.887 | -0.37079 | -1.9592 | 0.032043 | -43.7988 | 8.8531 | -114.0747 | 113.4659 | 0.036621 | 114.0427 | -0.15564 | 0.18768 | -9.2056 | -9.2239 | -0.34332 | 0.01831 | 0.57678
1487.5781 | 122.6715 | -113.8138 | 8.7112 | 0.10136 | 0.0096232 | 0.0018209 | 0.048146 | 0.066284 | 0.0024719 | 0.090831 | 0.35248 | 8.725 | -0.21515 | -113.9145 | -0.32501 | -1.9547 | 0.004578 | -43.8126 | 8.7662 | -114.1571 | 113.5986 | 0.013733 | 114.1663 | -0.10071 | 0.24261 | -9.0363 | -9.0912 | -0.34332 | 0.054931 | 0.56763
1488.5781 | 122.6624 | -113.7451 | 8.7982 | 0.15477 | 0.0066326 | 0.0043843 | 0.049855 | 0.066925 | 0.0035401 | 0.091899 | 0.39368 | 8.8531 | -0.20142 | -113.8458 | -0.30212 | -1.8951 | 0.022888 | -43.7759 | 8.8531 | -114.093 | 113.5437 | 0.054931 | 114.1388 | -0.10071 | 0.24719 | -9.1003 | -9.1553 | -0.3479 | 0.054931 | 0.59509
1489.5781 | 122.6578 | -113.7955 | 8.7479 | 0.14714 | 0.009196 | 0.0065205 | 0.050924 | 0.063934 | 0.0020447 | 0.09254 | 0.34332 | 8.7753 | -0.27466 | -113.9328 | -0.32959 | -1.9775 | 0.027466 | -43.8583 | 8.7845 | -114.1571 | 113.5208 | 0.027466 | 114.1388 | -0.13733 | 0.2243 | -9.0775 | -9.1141 | -0.36163 | 0.036621 | 0.61798
1490.5781 | 122.6532 | -113.8916 | 8.6472 | 0.15477 | 0.007487 | 0.0045979 | 0.048574 | 0.065857 | -9.1495e-05 | 0.092967 | 0.36621 | 8.7021 | -0.21515 | -113.9923 | -0.29755 | -1.9867 | 0.022888 | -43.9453 | 8.7021 | -114.2395 | 113.6765 | 0.054931 | 114.2578 | -0.10071 | 0.24719 | -8.9447 | -8.9996 | -0.3479 | 0.054931 | 0.58136
1491.5781 | 122.699 | -113.9282 | 8.6105 | 0.11662 | 0.0096232 | 0.0037435 | 0.049855 | 0.06543 | 0.0005493 | 0.091899 | 0.48523 | 8.6472 | -0.23804 | -114.0289 | -0.27466 | -2.0142 | 0.022888 | -44.0094 | 8.6838 | -114.2761 | 113.6902 | 0.036621 | 114.4135 | -0.10071 | 0.24719 | -8.8852 | -8.9584 | -0.3479 | 0.073242 | 0.72327
1492.5781 | 122.6624 | -112.7014 | 9.874 | 0.13951 | 0.0083416 | 0.0020345 | 0.04836 | 0.064361 | 0.0016175 | 0.090831 | 0.3891 | 9.8785 | -0.25177 | -112.8113 | -0.27924 | -1.5289 | 0.013733 | -43.0435 | 9.8923 | -113.0722 | 112.4496 | 0.004578 | 113.0905 | -0.10986 | 0.26093 | -10.1532 | -10.1715 | -0.37079 | 0.018311 | 0.64087
1493.5781 | 122.6807 | -112.8983 | 9.6542 | 0.055586 | 0.010478 | 0.0056661 | 0.049855 | 0.064575 | 0.0028991 | 0.091471 | 0.37994 | 9.7 | -0.21515 | -112.9761 | -0.27008 | -1.5747 | 0.009155 | -43.2037 | 9.7229 | -113.2233 | 112.6831 | 0.045776 | 113.2782 | -0.07782 | 0.24719 | -9.9243 | -9.993 | -0.32501 | 0.068664 | 0.59509
1494.5781 | 122.7081 | -112.9807 | 9.581 | 0.055586 | 0.0077006 | 0.0033161 | 0.047292 | 0.066498 | 0.0037537 | 0.092326 | 0.37994 | 9.581 | -0.27008 | -113.0814 | -0.27008 | -1.6251 | 0.050354 | -43.2175 | 9.6176 | -113.3057 | 112.7106 | 0 | 113.3606 | -0.10071 | 0.2243 | -9.8511 | -9.8877 | -0.32501 | 0.036621 | 0.65003
1495.5781 | 122.699 | -113.0859 | 9.4711 | 0.040327 | 0.009196 | 0.0052387 | 0.049001 | 0.065216 | 0.0007629 | 0.090403 | 0.37537 | 9.494 | -0.27924 | -113.1683 | -0.26093 | -1.6663 | 0.064087 | -43.3365 | 9.5261 | -113.4247 | 112.8067 | 0.022889 | 113.4613 | -0.082398 | 0.25635 | -9.7321 | -9.787 | -0.33875 | 0.054932 | 0.6546
1496.5781 | 122.6944 | -113.1088 | 9.4528 | 0.032698 | 0.0096232 | 0.0031025 | 0.048146 | 0.066711 | 0.0037537 | 0.091471 | 0.37994 | 9.462 | -0.25635 | -113.1912 | -0.25635 | -1.6663 | 0.032043 | -43.3914 | 9.4986 | -113.4521 | 112.8525 | 0.009155 | 113.4888 | -0.082397 | 0.26093 | -9.7092 | -9.7549 | -0.34332 | 0.045776 | 0.63629
1497.5781 | 122.6852 | -113.1775 | 9.3979 | 0.093733 | 0.01005 | 0.0026753 | 0.047933 | 0.065857 | 0.0043945 | 0.092967 | 0.37537 | 9.3933 | -0.26093 | -113.269 | -0.2655 | -1.6937 | 0.027466 | -43.5059 | 9.4345 | -113.5162 | 112.9166 | -0.004577 | 113.5529 | -0.091553 | 0.24719 | -9.6634 | -9.7 | -0.33874 | 0.036621 | 0.63629
1498.5781 | 122.6852 | -112.4313 | 10.0845 | 0.1624 | 0.009196 | 0.0028889 | 0.048146 | 0.065643 | 0.0035401 | 0.090403 | 0.4303 | 10.1669 | -0.21057 | -112.5641 | -0.25635 | -1.4008 | 0.004578 | -42.9703 | 10.1715 | -112.8113 | 112.2208 | 0.082397 | 112.8616 | -0.13275 | 0.24719 | -10.3409 | -10.4279 | -0.37994 | 0.086975 | 0.64087
1499.5781 | 122.7173 | -112.6831 | 9.906 | 0.12425 | 0.0087688 | 0.0022481 | 0.047506 | 0.064148 | 0.0028991 | 0.095103 | 0.39825 | 9.8831 | -0.25177 | -112.674 | -0.24719 | -1.4374 | 0.013733 | -43.19 | 9.993 | -113.0127 | 112.4313 | -0.022888 | 113.0814 | 0.009155 | 0.33874 | -10.1532 | -10.2402 | -0.32959 | 0.086975 | 0.65002
1500.5781 | 122.6944 | -112.793 | 9.7275 | 0.1624 | 0.0085552 | 0.0018209 | 0.048574 | 0.063293 | 0.0031127 | 0.091899 | 0.37537 | 9.7 | -0.25635 | -112.9807 | -0.25635 | -1.5747 | 0.027466 | -43.364 | 9.7275 | -113.2187 | 112.5366 | -0.027466 | 113.1683 | -0.18768 | 0.23804 | -9.9838 | -9.9838 | -0.42572 | 0 | 0.63171
1501.5781 | 122.699 | -113.0905 | 9.5123 | 0.070845 | 0.0079142 | 0.0028889 | 0.04836 | 0.065216 | 0.0011901 | 0.090617 | 0.32501 | 9.5398 | -0.26093 | -113.1683 | -0.28381 | -1.6663 | 0.091553 | -43.7668 | 9.5352 | -113.4338 | 112.8296 | 0.027466 | 113.4155 | -0.07782 | 0.2655 | -9.7961 | -9.819 | -0.34332 | 0.022888 | 0.58594
1502.5781 | 122.7081 | -113.1363 | 9.4254 | 0.032698 | 0.0064188 | 0.0031025 | 0.049215 | 0.063507 | 0.0024719 | 0.091258 | 0.32959 | 9.4391 | -0.28381 | -113.2645 | -0.31586 | -1.7166 | 0.10986 | -43.8538 | 9.4803 | -113.53 | 112.8525 | 0.013733 | 113.4659 | -0.12817 | 0.2655 | -9.7412 | -9.7961 | -0.39368 | 0.054932 | 0.6134
1503.5781 | 122.7219 | -113.237 | 9.3292 | 0.017439 | 0.0098368 | 0.0037435 | 0.047292 | 0.06543 | 0.0022583 | 0.090831 | 0.36621 | 9.3475 | -0.27008 | -113.3194 | -0.28381 | -1.7212 | 0.041199 | -43.9224 | 9.3842 | -113.562 | 112.9669 | 0.01831 | 113.6032 | -0.082397 | 0.24262 | -9.613 | -9.668 | -0.32501 | 0.054931 | 0.63629
1504.5781 | 122.731 | -113.3102 | 9.2514 | 0.017439 | 0.0089824 | 0.0052387 | 0.046437 | 0.066925 | 0.0026855 | 0.091044 | 0.34332 | 9.2834 | -0.28381 | -113.3972 | -0.28839 | -1.767 | 0.07782 | -43.9957 | 9.3201 | -113.6398 | 113.0264 | 0.032043 | 113.6536 | -0.086975 | 0.24262 | -9.5398 | -9.6085 | -0.32959 | 0.068664 | 0.62714
1505.5781 | 122.699 | -113.3652 | 9.2056 | 0.055586 | 0.010905 | -0.0013835 | 0.050496 | 0.06607 | 0.0003357 | 0.092112 | 0.3891 | 9.2194 | -0.25635 | -113.4659 | -0.28839 | -1.799 | 0.022888 | -44.1238 | 9.256 | -113.7222 | 113.1088 | 0.013733 | 113.7543 | -0.10071 | 0.25635 | -9.494 | -9.5444 | -0.35706 | 0.050354 | 0.64545
1506.5781 | 122.6944 | -113.4338 | 9.137 | 0.13188 | 0.007487 | 0.00053914 | 0.047719 | 0.063721 | 0.0031127 | 0.092112 | 0.35706 | 9.1278 | -0.26093 | -113.53 | -0.28381 | -1.8173 | 0.032043 | -44.2566 | 9.1919 | -113.7726 | 113.1729 | -0.009155 | 113.7909 | -0.09613 | 0.24262 | -9.4208 | -9.4757 | -0.33875 | 0.054932 | 0.61798
1507.5781 | 122.7036 | -113.5117 | 9.0546 | 0.0021796 | 0.0083416 | 0.0041707 | 0.051778 | 0.063721 | 0.0020447 | 0.092112 | 0.36163 | 9.0454 | -0.26093 | -113.6124 | -0.27008 | -1.8677 | 0.036621 | -44.3985 | 9.1095 | -113.8596 | 113.2507 | -0.009155 | 113.8733 | -0.10071 | 0.24719 | -9.3246 | -9.3796 | -0.3479 | 0.054932 | 0.62256
1508.5781 | 122.6807 | -113.5529 | 9.0088 | 0.017439 | 0.0079142 | -0.00031526 | 0.047506 | 0.064361 | 0.0007629 | 0.089549 | 0.29297 | 9.0454 | -0.29297 | -113.681 | -0.32044 | -1.9547 | 0.11902 | -44.4763 | 9.0775 | -113.8962 | 113.2599 | 0.036621 | 113.8458 | -0.12817 | 0.21515 | -9.3292 | -9.3979 | -0.34332 | 0.068665 | 0.58594
1509.5781 | 122.6715 | -113.6353 | 8.9264 | 0.047956 | 0.0089824 | 0.0033161 | 0.047933 | 0.064789 | 0.0026855 | 0.091899 | 0.31128 | 8.9813 | -0.25177 | -113.7497 | -0.53101 | -2.0462 | 0.1236 | -44.5358 | 9.0042 | -113.974 | 113.3835 | 0.054931 | 113.9465 | -0.11444 | 0.2243 | -9.4574 | -9.5352 | -0.33875 | 0.077819 | 0.56305
1510.5781 | 122.6898 | -113.7863 | 8.7799 | -0.020708 | 0.0068462 | 0.0013935 | 0.047719 | 0.065002 | 0.0018311 | 0.09318 | 0.30212 | 8.7433 | -0.27466 | -113.9008 | -1.3641 | -2.3163 | 0.09613 | -44.8563 | 8.8165 | -114.1571 | 113.5117 | -0.036621 | 114.0884 | -0.11444 | 0.25635 | -10.144 | -10.1807 | -0.37079 | 0.036621 | 0.57678
1511.5781 | 122.7173 | -113.7634 | 8.7891 | 0.0021796 | 0.0081278 | 0.0033161 | 0.046865 | 0.064789 | 0.0018311 | 0.09019 | 0.29297 | 8.8028 | -0.2655 | -113.8596 | -1.0483 | -2.2293 | 0.09613 | -44.7098 | 8.8669 | -114.1113 | 113.4979 | 0.013733 | 114.0564 | -0.09613 | 0.25177 | -9.8373 | -9.9152 | -0.3479 | 0.07782 | 0.55847
1512.5781 | 122.7036 | -113.8367 | 8.7296 | 0.078474 | 0.007487 | 0.0037435 | 0.047292 | 0.065643 | 0.0033265 | 0.09254 | 0.35248 | 8.7524 | -0.2655 | -113.8962 | -1.4191 | -2.3529 | 0.032043 | -44.8105 | 8.7891 | -114.1663 | 113.5712 | 0.022888 | 114.1891 | -0.059509 | 0.27008 | -10.1486 | -10.2081 | -0.32959 | 0.059509 | 0.61798
1513.5781 | 122.6852 | -113.8367 | 8.7112 | 0.0098091 | 0.010264 | 0.00011194 | 0.049428 | 0.064575 | 0.0024719 | 0.095103 | 0.3479 | 8.7341 | -0.26093 | -113.9236 | -1.442 | -2.3621 | 0.059509 | -44.8746 | 8.7753 | -114.1617 | 113.5757 | 0.022888 | 114.1846 | -0.086975 | 0.23804 | -10.1532 | -10.2173 | -0.32501 | 0.064087 | 0.60882
1514.5781 | 122.7127 | -113.8275 | 8.7387 | 0.078474 | 0.0087688 | 0.0039571 | 0.049001 | 0.065643 | 0.0024719 | 0.091899 | 0.32959 | 8.7387 | -0.25177 | -113.887 | -1.0803 | -2.2385 | 0.045776 | -44.8059 | 8.8257 | -114.1479 | 113.5757 | 0 | 114.1571 | -0.059509 | 0.26093 | -9.819 | -9.906 | -0.32043 | 0.086976 | 0.58136
1515.5781 | 122.6852 | -113.7863 | 8.7799 | -0.043596 | 0.009196 | -0.0015971 | 0.045797 | 0.062225 | 0.0028991 | 0.093821 | 0.28839 | 8.8028 | -0.27008 | -113.942 | -0.78735 | -2.179 | 0.10529 | -44.8563 | 8.844 | -114.1663 | 113.5162 | 0.022888 | 114.0747 | -0.15564 | 0.2243 | -9.5673 | -9.6313 | -0.37994 | 0.064087 | 0.55847
1516.5781 | 122.6761 | -113.8641 | 8.7387 | 0.12425 | 0.0072734 | 0.0024617 | 0.04601 | 0.063293 | 0.0022583 | 0.092326 | 0.28839 | 8.7387 | -0.24719 | -113.9832 | -0.85144 | -2.2202 | 0.10986 | -45.0119 | 8.7982 | -114.2075 | 113.6169 | 0 | 114.1525 | -0.11902 | 0.2243 | -9.5901 | -9.6497 | -0.34332 | 0.05951 | 0.53558
1517.5781 | 122.7356 | -113.8641 | 8.7067 | 0.025068 | 0.0089824 | 0.0022481 | 0.048574 | 0.065216 | 0.0041809 | 0.092967 | 0.32501 | 8.725 | -0.27466 | -113.9786 | -0.87433 | -2.2202 | 0.068665 | -45.0531 | 8.7524 | -114.2258 | 113.5895 | 0.018311 | 114.1891 | -0.11444 | 0.24719 | -9.581 | -9.6268 | -0.36163 | 0.045776 | 0.59967
1518.5781 | 122.699 | -113.942 | 8.6472 | -0.0054494 | 0.0072734 | -0.00074266 | 0.048787 | 0.065857 | 0.0024719 | 0.090831 | 0.30212 | 8.6609 | -0.28381 | -114.0381 | -0.92468 | -2.2614 | 0.082397 | -45.2042 | 8.6746 | -114.267 | 113.6581 | 0.013733 | 114.2441 | -0.09613 | 0.22888 | -9.5718 | -9.5993 | -0.32501 | 0.027466 | 0.58594
1519.5781 | 122.7173 | -113.9648 | 8.5785 | 0.11662 | 0.0089824 | 0.0013935 | 0.047506 | 0.063934 | 0.0009765 | 0.090617 | 0.35248 | 8.6288 | -0.25177 | -114.0427 | -1.0071 | -2.298 | 0.041199 | -45.2683 | 8.6517 | -114.3219 | 113.7131 | 0.050354 | 114.3173 | -0.07782 | 0.27923 | -9.5856 | -9.6588 | -0.35706 | 0.073242 | 0.60425
1520.5781 | 122.7264 | -114.0015 | 8.551 | -0.043596 | 0.0087688 | 0.0024617 | 0.049215 | 0.063721 | 0.0039673 | 0.092112 | 0.35248 | 8.5693 | -0.25177 | -114.0976 | -1.1765 | -2.3666 | 0.027466 | -45.3918 | 8.6197 | -114.3768 | 113.7497 | 0.018311 | 114.3539 | -0.09613 | 0.27924 | -9.7275 | -9.7961 | -0.37537 | 0.068665 | 0.60425
1521.5781 | 122.6898 | -114.0015 | 8.5419 | 0.0021796 | 0.007487 | 0.0033161 | 0.050069 | 0.065216 | 0.0003357 | 0.089762 | 0.32501 | 8.5648 | -0.25635 | -114.1022 | -1.0712 | -2.3575 | 0.045776 | -45.3735 | 8.6334 | -114.3402 | 113.7451 | 0.022888 | 114.3265 | -0.10071 | 0.23804 | -9.613 | -9.7046 | -0.33875 | 0.091553 | 0.58136
1522.5781 | 122.6898 | -114.0015 | 8.5968 | -0.10463 | 0.0094096 | -0.00052906 | 0.047292 | 0.065857 | 0.0033265 | 0.092967 | 0.29297 | 8.6105 | -0.2655 | -114.1205 | -1.4053 | -2.4445 | 0.10986 | -45.401 | 8.638 | -114.3494 | 113.736 | 0.013733 | 114.2944 | -0.11902 | 0.22888 | -10.0021 | -10.0433 | -0.3479 | 0.041198 | 0.55847
1523.5781 | 122.6852 | -113.9923 | 8.6014 | -0.11989 | 0.007487 | 0.0050251 | 0.047292 | 0.066284 | 0.0020447 | 0.09019 | 0.28381 | 8.606 | -0.25635 | -114.1388 | -1.2222 | -2.3804 | 0.11902 | -45.4559 | 8.6563 | -114.3311 | 113.736 | 0.004578 | 114.2761 | -0.14648 | 0.19226 | -9.8236 | -9.8785 | -0.33875 | 0.054932 | 0.54016
1524.5781 | 122.7081 | -114.0106 | 8.5785 | 0.025068 | 0.0068462 | 0.00075274 | 0.048146 | 0.065857 | 0.0031127 | 0.089976 | 0.31128 | 8.5602 | -0.27008 | -114.1068 | -1.1948 | -2.3666 | 0.064087 | -45.4376 | 8.6014 | -114.3677 | 113.7405 | -0.01831 | 114.3219 | -0.09613 | 0.26093 | -9.7733 | -9.7961 | -0.35706 | 0.022888 | 0.58136
1525.5781 | 122.731 | -114.0747 | 8.5007 | -0.028338 | 0.0085552 | 0.00053914 | 0.049428 | 0.063721 | 0.0009765 | 0.088694 | 0.30212 | 8.519 | -0.27008 | -114.1754 | -1.1902 | -2.4216 | 0.073242 | -45.6207 | 8.5556 | -114.3951 | 113.8046 | 0.018311 | 114.3768 | -0.10071 | 0.21973 | -9.6909 | -9.7458 | -0.32044 | 0.054932 | 0.57221
1526.5781 | 122.6898 | -114.0793 | 8.5098 | 0.11662 | 0.010478 | 0.0063069 | 0.049001 | 0.063934 | 0.0037537 | 0.092967 | 0.35248 | 8.5236 | -0.25635 | -114.1525 | -1.0666 | -2.3758 | 0.045776 | -45.6528 | 8.551 | -114.4135 | 113.8229 | 0.013733 | 114.4318 | -0.073242 | 0.26093 | -9.5764 | -9.6176 | -0.33417 | 0.041198 | 0.60883
1527.5781 | 122.7219 | -114.0839 | 8.4961 | 0.078474 | 0.0077006 | 0.0043843 | 0.048787 | 0.06607 | 0.0031127 | 0.088267 | 0.35248 | 8.5281 | -0.26093 | -114.1479 | -1.0529 | -2.3575 | 0.032043 | -45.6299 | 8.5602 | -114.4363 | 113.8229 | 0.032043 | 114.4363 | -0.064087 | 0.28839 | -9.5489 | -9.613 | -0.35248 | 0.064087 | 0.6134
1528.5781 | 122.7173 | -114.0701 | 8.4824 | -0.0054494 | 0.007487 | 0.0022481 | 0.049428 | 0.064361 | 0.0005493 | 0.091471 | 0.35248 | 8.5281 | -0.2655 | -114.1663 | -1.0437 | -2.3575 | 0.041199 | -45.639 | 8.5693 | -114.4226 | 113.8046 | 0.045776 | 114.4226 | -0.096131 | 0.25635 | -9.5261 | -9.613 | -0.35248 | 0.086975 | 0.61798
1529.5781 | 122.6898 | -114.0656 | 8.5281 | -0.028338 | 0.0098368 | 0.00053914 | 0.047933 | 0.065002 | 0.0018311 | 0.09019 | 0.29297 | 8.5419 | -0.25635 | -114.1846 | -1.0162 | -2.3666 | 0.11902 | -45.6253 | 8.5556 | -114.418 | 113.8092 | 0.013733 | 114.3585 | -0.11902 | 0.23346 | -9.5444 | -9.5718 | -0.35248 | 0.027466 | 0.54932
1530.5781 | 122.7081 | -114.061 | 8.4824 | 0.040327 | 0.0087688 | 0.0071615 | 0.048574 | 0.064148 | 0.0020447 | 0.089976 | 0.32501 | 8.5052 | -0.2655 | -114.1708 | -1.0483 | -2.3483 | 0.059509 | -45.6161 | 8.5373 | -114.4363 | 113.7955 | 0.022888 | 114.386 | -0.10986 | 0.2655 | -9.5306 | -9.5856 | -0.37537 | 0.054931 | 0.59052
1531.5781 | 122.7173 | -114.0839 | 8.5098 | 0.0021796 | 0.0087688 | 0.0071615 | 0.045583 | 0.066498 | 0.0018311 | 0.09019 | 0.32044 | 8.4961 | -0.27466 | -114.1571 | -1.03 | -2.33 | 0.073242 | -45.5704 | 8.5648 | -114.4409 | 113.8092 | -0.013733 | 114.4043 | -0.073242 | 0.28381 | -9.5398 | -9.5947 | -0.35706 | 0.054931 | 0.59509
1532.5781 | 122.7173 | -114.0884 | 8.4869 | 0.10899 | 0.0085552 | 0.0037435 | 0.050283 | 0.066284 | 0.0024719 | 0.091258 | 0.3479 | 8.5098 | -0.25635 | -114.1617 | -1.062 | -2.4261 | 0.032043 | -45.575 | 8.5419 | -114.4318 | 113.8321 | 0.022889 | 114.4363 | -0.073242 | 0.27008 | -9.5489 | -9.6039 | -0.34332 | 0.054932 | 0.60425
1533.5781 | 122.7036 | -114.1159 | 8.4549 | 0.086103 | 0.0096232 | 0.0069477 | 0.049855 | 0.065216 | 0.0052491 | 0.091899 | 0.3479 | 8.4778 | -0.27008 | -114.212 | -1.0483 | -2.4216 | 0.022888 | -45.575 | 8.519 | -114.4501 | 113.8458 | 0.022888 | 114.4638 | -0.09613 | 0.23804 | -9.5032 | -9.5673 | -0.33417 | 0.064087 | 0.61798
1534.5781 | 122.7081 | -114.093 | 8.4595 | 0.086103 | 0.010905 | -0.00052906 | 0.04836 | 0.063721 | 0.0011901 | 0.089122 | 0.34332 | 8.4824 | -0.25177 | -114.1891 | -1.0162 | -2.4216 | 0.036621 | -45.575 | 8.5281 | -114.4501 | 113.8412 | 0.022888 | 114.4363 | -0.09613 | 0.26093 | -9.4757 | -9.5444 | -0.35706 | 0.068664 | 0.59509
1535.5781 | 122.7081 | -117.6315 | 4.9393 | 0.11662 | 0.0068462 | 0.0045979 | 0.05306 | 0.065643 | -0.0011597 | 0.092326 | 0.22888 | 4.9438 | -0.27924 | -117.7414 | -1.268 | -3.9734 | 0.041199 | -48.3627 | 4.985 | -118.0161 | 117.3523 | 0.004578 | 117.8604 | -0.10986 | 0.27466 | -6.2073 | -6.2531 | -0.38452 | 0.045776 | 0.50812
1536.5781 | 122.699 | -117.7185 | 4.8752 | -0.0054494 | 0.0077006 | 0.00096634 | 0.049855 | 0.064148 | 0.0003357 | 0.089122 | 0.15564 | 4.8798 | -0.27924 | -117.8558 | -1.4923 | -4.1016 | 0.11444 | -48.5092 | 4.9393 | -118.0847 | 117.4393 | 0.004578 | 117.8741 | -0.13733 | 0.22888 | -6.3675 | -6.4316 | -0.36621 | 0.064087 | 0.43488
1537.5781 | 122.7356 | -117.7689 | 4.8386 | -0.0054494 | 0.0066326 | 0.0039571 | 0.055196 | 0.065002 | 0.0020447 | 0.090403 | 0.20142 | 4.834 | -0.29297 | -117.8604 | -1.767 | -4.1702 | 0.068665 | -48.5413 | 4.8889 | -118.1168 | 117.4759 | -0.004578 | 117.9703 | -0.091553 | 0.25635 | -6.6055 | -6.6559 | -0.3479 | 0.050354 | 0.49438
1538.5781 | 122.7081 | -117.746 | 4.8569 | 0.0021796 | 0.0062052 | 0.0043843 | 0.050924 | 0.063507 | -0.0003051 | 0.092112 | 0.20142 | 4.8752 | -0.28839 | -117.8513 | -1.6296 | -4.1473 | 0.050354 | -48.5367 | 4.9026 | -118.0939 | 117.4576 | 0.01831 | 117.9474 | -0.10529 | 0.24262 | -6.4865 | -6.5323 | -0.3479 | 0.045776 | 0.48981
1539.5781 | 122.7127 | -117.7643 | 4.8019 | 0.15477 | 0.00471 | 0.0035299 | 0.052633 | 0.064575 | -9.1495e-05 | 0.091471 | 0.21973 | 4.834 | -0.25635 | -117.8513 | -1.6022 | -4.1473 | 0.032043 | -48.5504 | 4.8614 | -118.1168 | 117.5079 | 0.032043 | 117.984 | -0.086975 | 0.2655 | -6.4041 | -6.4636 | -0.35248 | 0.059509 | 0.47608
1540.5781 | 122.7173 | -117.8146 | 4.7928 | 0.13188 | 0.0079142 | 0.0013935 | 0.052846 | 0.06543 | -0.0009461 | 0.09318 | 0.21515 | 4.7791 | -0.2655 | -117.9062 | -1.6342 | -4.1748 | 0.036621 | -48.587 | 4.834 | -118.1625 | 117.5491 | -0.013733 | 118.0298 | -0.091553 | 0.25635 | -6.427 | -6.4682 | -0.3479 | 0.041198 | 0.48065
1541.5781 | 122.7127 | -117.8375 | 4.7562 | 0.070845 | 0.0070598 | -0.0018107 | 0.051351 | 0.064789 | 0.0028991 | 0.092112 | 0.2243 | 4.7791 | -0.27924 | -117.8787 | -1.799 | -4.2526 | 0.041199 | -48.6053 | 4.8294 | -118.1717 | 117.5583 | 0.022888 | 118.0618 | -0.041199 | 0.29297 | -6.5552 | -6.6284 | -0.33417 | 0.073242 | 0.50354
1542.5781 | 122.699 | -117.8238 | 4.8019 | -0.0054494 | 0.0042826 | 0.0020345 | 0.051564 | 0.063934 | 0.0009765 | 0.092326 | 0.16022 | 4.7928 | -0.28381 | -117.9337 | -1.7303 | -4.2435 | 0.10986 | -48.6237 | 4.8523 | -118.1717 | 117.54 | -0.009155 | 117.984 | -0.10986 | 0.23804 | -6.5323 | -6.5826 | -0.3479 | 0.050354 | 0.44403
1543.5781 | 122.699 | -117.8192 | 4.8248 | -0.028338 | 0.0070598 | 0.0020345 | 0.051992 | 0.065216 | 0.0014039 | 0.091685 | 0.16479 | 4.8294 | -0.28839 | -117.8925 | -1.7029 | -4.2389 | 0.10986 | -48.6237 | 4.8706 | -118.1442 | 117.5308 | 0.004578 | 117.984 | -0.073242 | 0.25177 | -6.5277 | -6.5735 | -0.32501 | 0.045776 | 0.45319
1544.5781 | 122.7402 | -117.8101 | 4.7882 | 0.047956 | 0.0083416 | 0.0050251 | 0.051992 | 0.06543 | -9.1495e-05 | 0.091044 | 0.17395 | 4.7653 | -0.28839 | -117.9108 | -1.886 | -4.3579 | 0.068665 | -48.6237 | 4.8157 | -118.1305 | 117.5217 | -0.022888 | 117.984 | -0.10071 | 0.21973 | -6.6742 | -6.7017 | -0.32043 | 0.027466 | 0.46234
1545.5781 | 122.731 | -117.7963 | 4.7882 | 0.017439 | 0.0059916 | 0.0058797 | 0.051137 | 0.063721 | 0.0003357 | 0.091685 | 0.18768 | 4.7974 | -0.27466 | -117.897 | -1.799 | -4.3213 | 0.07782 | -48.6237 | 4.8477 | -118.1396 | 117.5217 | 0.009155 | 117.984 | -0.10071 | 0.24261 | -6.5872 | -6.6467 | -0.34332 | 0.059509 | 0.46234
1546.5781 | 122.7173 | -117.778 | 4.834 | 0.093733 | 0.0081278 | 0.0035299 | 0.053701 | 0.064575 | -0.0011597 | 0.092753 | 0.2243 | 4.8203 | -0.27008 | -117.8513 | -1.8356 | -4.3167 | 0.036621 | -48.6557 | 4.8569 | -118.1396 | 117.5079 | -0.013733 | 118.0023 | -0.073242 | 0.28839 | -6.6696 | -6.6925 | -0.36163 | 0.022889 | 0.49439
1547.5781 | 122.7219 | -117.7689 | 4.8248 | 0.086103 | 0.0081278 | 0.0058797 | 0.051351 | 0.064789 | 0.0018311 | 0.090617 | 0.22888 | 4.8203 | -0.27466 | -117.8513 | -1.7807 | -4.2847 | 0.027466 | -48.6145 | 4.8706 | -118.1305 | 117.4942 | -0.004578 | 117.9977 | -0.082397 | 0.27924 | -6.6055 | -6.6513 | -0.36163 | 0.045776 | 0.50354
1548.5781 | 122.7081 | -117.7734 | 4.834 | 0.040327 | 0.0089824 | 0.0039571 | 0.053273 | 0.065643 | 0.0001221 | 0.091685 | 0.2243 | 4.8157 | -0.27466 | -117.8421 | -1.767 | -4.2938 | 0.045776 | -48.5504 | 4.8981 | -118.071 | 117.4988 | -0.01831 | 117.9977 | -0.068665 | 0.22888 | -6.601 | -6.665 | -0.29755 | 0.064087 | 0.49896
1549.5781 | 122.699 | -117.7689 | 4.8477 | 0.0021796 | 0.0070598 | 0.00096634 | 0.049642 | 0.063721 | 0.0007629 | 0.091471 | 0.15564 | 4.8431 | -0.27008 | -117.8925 | -1.8219 | -4.3533 | 0.11444 | -48.5825 | 4.8935 | -118.1305 | 117.4988 | -0.004577 | 117.9245 | -0.1236 | 0.23804 | -6.6696 | -6.7154 | -0.36163 | 0.045777 | 0.42572
1550.5781 | 122.7173 | -117.7597 | 4.8431 | 0.032698 | 0.007487 | -0.00074266 | 0.049001 | 0.063934 | 0.0016175 | 0.091258 | 0.17395 | 4.8569 | -0.28381 | -117.897 | -1.8356 | -4.3579 | 0.11444 | -48.5733 | 4.8981 | -118.1168 | 117.4759 | 0.013733 | 117.9337 | -0.13733 | 0.21973 | -6.6788 | -6.7337 | -0.35706 | 0.054931 | 0.45776
1551.5781 | 122.7173 | -117.7643 | 4.8431 | -0.0054494 | 0.0083416 | 0.0078023 | 0.052205 | 0.065002 | -0.0007325 | 0.092967 | 0.20142 | 4.8477 | -0.29297 | -117.8467 | -1.7853 | -4.2892 | 0.064087 | -48.5229 | 4.8752 | -118.1168 | 117.4713 | 0.004577 | 117.9657 | -0.082398 | 0.27008 | -6.6284 | -6.6605 | -0.35248 | 0.032043 | 0.49438
1552.5781 | 122.7036 | -117.7505 | 4.834 | -0.013079 | 0.0068462 | 0.0020345 | 0.050496 | 0.06607 | 0.0005493 | 0.092326 | 0.17395 | 4.8523 | -0.29297 | -117.865 | -1.9638 | -4.3488 | 0.086975 | -48.5641 | 4.8889 | -118.1259 | 117.4576 | 0.018311 | 117.9245 | -0.11444 | 0.26093 | -6.7978 | -6.8527 | -0.37537 | 0.054932 | 0.46692
1553.5781 | 122.7219 | -117.7597 | 4.8203 | 0.086103 | 0.005778 | 0.0056661 | 0.052846 | 0.064575 | 0.0009765 | 0.090617 | 0.23346 | 4.8203 | -0.2655 | -117.8604 | -1.9684 | -4.3304 | 0.036621 | -48.5596 | 4.8752 | -118.1213 | 117.4942 | 0 | 117.9932 | -0.10071 | 0.26093 | -6.7886 | -6.8436 | -0.36163 | 0.054932 | 0.49896
1554.5781 | 122.731 | -117.7689 | 4.8203 | 0.070845 | 0.0070598 | 0.0018209 | 0.05306 | 0.063721 | -0.0007325 | 0.091044 | 0.21515 | 4.8386 | -0.27466 | -117.8604 | -1.8997 | -4.3121 | 0.032043 | -48.5367 | 4.8798 | -118.103 | 117.4942 | 0.018311 | 117.984 | -0.091553 | 0.24261 | -6.72 | -6.7795 | -0.33417 | 0.05951 | 0.48981
1555.5781 | 122.7173 | -117.8009 | 4.7882 | 0.063215 | 0.0077006 | 0.0024617 | 0.052633 | 0.064575 | -9.1495e-05 | 0.091685 | 0.21515 | 4.8111 | -0.27466 | -117.8833 | -2.0142 | -4.3304 | 0.050354 | -48.5413 | 4.8431 | -118.1442 | 117.5262 | 0.022888 | 118.0161 | -0.082398 | 0.26093 | -6.8024 | -6.8573 | -0.34332 | 0.054932 | 0.48981
1556.5781 | 122.6944 | -117.7643 | 4.8294 | 0.017439 | 0.0070598 | -0.0018107 | 0.049215 | 0.06308 | -0.0011597 | 0.091258 | 0.15564 | 4.834 | -0.28839 | -117.897 | -1.9821 | -4.335 | 0.10071 | -48.5138 | 4.8798 | -118.1351 | 117.4759 | 0.004577 | 117.9199 | -0.13275 | 0.23804 | -6.8115 | -6.8619 | -0.37079 | 0.050354 | 0.44403
1557.5781 | 122.7036 | -117.8146 | 4.834 | -0.074114 | 0.009196 | 0.00075274 | 0.049855 | 0.062439 | 0.0001221 | 0.09318 | 0.16937 | 4.8386 | -0.28381 | -117.9108 | -1.9409 | -4.3259 | 0.11444 | -48.5641 | 4.8706 | -118.1305 | 117.5308 | 0.004578 | 117.984 | -0.096131 | 0.21973 | -6.7749 | -6.8115 | -0.31586 | 0.036621 | 0.45319
1558.5781 | 122.731 | -117.7917 | 4.8248 | -0.043596 | 0.0064188 | 0.0013935 | 0.051137 | 0.062652 | 0.0007629 | 0.092967 | 0.17395 | 4.8157 | -0.27924 | -117.8787 | -1.9547 | -4.2892 | 0.064087 | -48.4817 | 4.8706 | -118.1351 | 117.5125 | -0.009155 | 117.9657 | -0.086975 | 0.25635 | -6.7795 | -6.8253 | -0.34332 | 0.045776 | 0.45319
1559.5781 | 122.7127 | -117.778 | 4.8111 | 0.0021796 | 0.0059916 | -0.0011699 | 0.052419 | 0.065216 | 0.0007629 | 0.09254 | 0.16479 | 4.8431 | -0.28381 | -117.8696 | -1.9821 | -4.2984 | 0.073242 | -48.5641 | 4.8752 | -118.1305 | 117.4942 | 0.032044 | 117.9428 | -0.091553 | 0.26093 | -6.7932 | -6.8573 | -0.35248 | 0.064087 | 0.44861
1560.5781 | 122.7219 | -117.8055 | 4.7928 | 0.093733 | 0.0064188 | 0.0045979 | 0.051992 | 0.063507 | 0.0020447 | 0.093821 | 0.21057 | 4.8019 | -0.26093 | -117.8879 | -1.9638 | -4.2755 | 0.032043 | -48.5458 | 4.8477 | -118.1763 | 117.5446 | 0.009155 | 118.0161 | -0.082397 | 0.28839 | -6.7566 | -6.8115 | -0.37079 | 0.054931 | 0.4715
1561.5781 | 122.7036 | -117.7734 | 4.8111 | -0.028338 | 0.0079142 | 0.0028889 | 0.053487 | 0.06543 | 0.0001221 | 0.09318 | 0.21515 | 4.8248 | -0.27924 | -117.8421 | -1.9913 | -4.2709 | 0.045776 | -48.555 | 4.8752 | -118.1213 | 117.4942 | 0.013733 | 117.9886 | -0.068665 | 0.27924 | -6.8024 | -6.8665 | -0.3479 | 0.064087 | 0.49438
1562.5781 | 122.7356 | -117.7826 | 4.8111 | 0.055586 | 0.0072734 | -0.00031526 | 0.052633 | 0.06543 | -9.1495e-05 | 0.094462 | 0.21515 | 4.8065 | -0.28381 | -117.8787 | -1.9501 | -4.2389 | 0.054932 | -48.5641 | 4.8569 | -118.1534 | 117.4988 | -0.004577 | 117.9977 | -0.09613 | 0.27466 | -6.7612 | -6.8069 | -0.37079 | 0.045777 | 0.49896
1563.5781 | 122.6852 | -117.6132 | 5.0262 | 0.15477 | 0.0059916 | 0.0052387 | 0.051351 | 0.062012 | -0.0009461 | 0.091899 | 0.16479 | 5.0262 | -0.26093 | -117.7231 | -1.9363 | -4.1748 | 0.12817 | -48.4222 | 5.0812 | -117.9382 | 117.3523 | 0 | 117.778 | -0.10986 | 0.21515 | -6.9626 | -7.0175 | -0.32501 | 0.054932 | 0.42572
1564.5781 | 122.6852 | -117.7505 | 4.8752 | -0.51662 | 0.0083416 | 0.0041707 | 0.049855 | 0.066284 | 0.0001221 | 0.091685 | 0.041199 | 4.9072 | -0.24261 | -117.8833 | -1.9547 | -4.2252 | 0.13733 | -48.4726 | 4.9347 | -118.0984 | 117.5079 | 0.032044 | 117.7917 | -0.13275 | 0.21515 | -6.8298 | -6.8893 | -0.3479 | 0.059509 | 0.28381
1565.5781 | 122.7219 | -117.7231 | 4.8706 | 0.0098091 | 0.0081278 | 0.0031025 | 0.050924 | 0.063934 | 0.0005493 | 0.091899 | 0.17853 | 4.8706 | -0.28381 | -117.8421 | -1.9455 | -4.1977 | 0.09613 | -48.5184 | 4.9255 | -118.0939 | 117.4393 | 0 | 117.9016 | -0.11902 | 0.25177 | -6.8161 | -6.871 | -0.37079 | 0.054932 | 0.46234
1566.5781 | 122.7036 | -117.7231 | 4.9118 | -0.0054494 | 0.0049236 | 0.0041707 | 0.052846 | 0.062439 | 0.0001221 | 0.092753 | 0.15564 | 4.9118 | -0.27466 | -117.8101 | -1.8906 | -4.184 | 0.11902 | -48.4634 | 4.953 | -118.0664 | 117.4484 | 0 | 117.8787 | -0.086976 | 0.25635 | -6.8024 | -6.8436 | -0.34332 | 0.041199 | 0.4303
1567.5781 | 122.731 | -117.7094 | 4.8843 | 0.063215 | 0.0077006 | 0.00053914 | 0.052633 | 0.062652 | 0.0016175 | 0.092753 | 0.2243 | 4.8706 | -0.27924 | -117.7917 | -1.8585 | -4.1336 | 0.041199 | -48.4634 | 4.9347 | -118.0756 | 117.4301 | -0.013733 | 117.9337 | -0.082397 | 0.28381 | -6.7429 | -6.7932 | -0.36621 | 0.050354 | 0.50354
1568.5781 | 122.7219 | -117.7368 | 4.8706 | 0.063215 | 0.0068462 | -0.0026653 | 0.054128 | 0.064575 | 0.0007629 | 0.091044 | 0.20599 | 4.8798 | -0.27466 | -117.7917 | -1.8951 | -4.129 | 0.073242 | -48.381 | 4.953 | -118.071 | 117.4622 | 0.009156 | 117.9428 | -0.054932 | 0.27924 | -6.7657 | -6.8481 | -0.33417 | 0.082398 | 0.48065
1569.5781 | 122.731 | -117.691 | 4.8843 | -0.028338 | 0.0072734 | 0.00011194 | 0.051992 | 0.064575 | -0.0013733 | 0.092112 | 0.1831 | 4.8798 | -0.29755 | -117.8192 | -1.918 | -4.1336 | 0.07782 | -48.3765 | 4.9438 | -118.0847 | 117.3935 | -0.004577 | 117.8741 | -0.12817 | 0.2655 | -6.8024 | -6.8619 | -0.39368 | 0.05951 | 0.48065
1570.5781 | 122.6761 | -117.7277 | 4.8614 | 1.6044 | 0.0053508 | 0.00053914 | 0.052205 | 0.063721 | 0.0005493 | 0.09318 | 0.15106 | 4.9164 | -0.24719 | -117.8696 | -1.9043 | -4.1565 | 0.1236 | -48.4543 | 4.9484 | -118.0984 | 117.4805 | 0.054932 | 117.8787 | -0.14191 | 0.22888 | -6.7657 | -6.8527 | -0.37079 | 0.086975 | 0.39825
1571.5781 | 122.6898 | -117.7368 | 4.8981 | -0.051226 | 0.0053508 | -0.0013835 | 0.053487 | 0.064789 | 0.0011901 | 0.091685 | 0.15564 | 4.9164 | -0.27466 | -117.8558 | -1.799 | -4.1107 | 0.1236 | -48.4268 | 4.9576 | -118.0573 | 117.4622 | 0.018311 | 117.8925 | -0.11902 | 0.20142 | -6.6971 | -6.7566 | -0.32043 | 0.05951 | 0.4303
1572.5781 | 122.699 | -117.7414 | 4.8569 | -0.043596 | 0.0083416 | 0.00053914 | 0.051137 | 0.06543 | 0.0007629 | 0.09254 | 0.16479 | 4.866 | -0.29297 | -117.8467 | -1.8631 | -4.1428 | 0.10986 | -48.4772 | 4.9026 | -118.0984 | 117.4484 | 0.009155 | 117.9062 | -0.10529 | 0.25177 | -6.72 | -6.7657 | -0.35706 | 0.045776 | 0.45776
1573.5781 | 122.7127 | -117.7689 | 4.8523 | -0.020708 | 0.0064188 | 0.0013935 | 0.052419 | 0.062866 | 0.0009765 | 0.09318 | 0.16022 | 4.8706 | -0.28381 | -117.8696 | -1.9226 | -4.1611 | 0.10071 | -48.4863 | 4.921 | -118.1122 | 117.485 | 0.01831 | 117.9291 | -0.10071 | 0.24262 | -6.7749 | -6.8436 | -0.34332 | 0.068664 | 0.44403
1574.5781 | 122.7127 | -117.7185 | 4.866 | 0.047956 | 0.007487 | 0.0011799 | 0.053914 | 0.064361 | -0.0007325 | 0.094035 | 0.20142 | 4.866 | -0.28839 | -117.7872 | -1.8814 | -4.1199 | 0.041199 | -48.4634 | 4.9393 | -118.071 | 117.4301 | 0 | 117.9199 | -0.068664 | 0.28381 | -6.7474 | -6.8207 | -0.35248 | 0.073242 | 0.48981
1575.5781 | 122.7173 | -117.7414 | 4.8386 | 0.0098091 | 0.0087688 | 0.00053914 | 0.054555 | 0.063934 | 0.0014039 | 0.094035 | 0.20142 | 4.8386 | -0.29755 | -117.8329 | -1.8539 | -4.0833 | 0.07782 | -48.4543 | 4.8935 | -118.0984 | 117.4438 | 0 | 117.9428 | -0.091553 | 0.2655 | -6.6925 | -6.7474 | -0.35706 | 0.054932 | 0.49896
1576.5781 | 122.7173 | -117.7231 | 4.8431 | 0.0098091 | 0.0077006 | 0.00096634 | 0.052846 | 0.063934 | 0.0011901 | 0.091899 | 0.19226 | 4.8798 | -0.28839 | -117.8284 | -1.8768 | -4.0924 | 0.050354 | -48.4085 | 4.9164 | -118.0939 | 117.4347 | 0.036621 | 117.9153 | -0.10529 | 0.2655 | -6.72 | -6.7932 | -0.37079 | 0.073242 | 0.48065
1577.5781 | 122.6715 | -117.778 | 4.8569 | 1.0016 | 0.0081278 | 0.0018209 | 0.049642 | 0.063934 | 0.0007629 | 0.096171 | 0.17853 | 4.8752 | -0.25635 | -117.9062 | -1.8951 | -4.1107 | 0.10529 | -48.4268 | 4.8889 | -118.1168 | 117.5217 | 0.01831 | 117.9565 | -0.12817 | 0.21057 | -6.752 | -6.7841 | -0.33875 | 0.032043 | 0.43488
1578.5781 | 122.7264 | -117.8101 | 4.8065 | 0.040327 | 0.0042826 | 0.0024617 | 0.050924 | 0.063293 | 0.0007629 | 0.092112 | 0.16937 | 4.834 | -0.27466 | -117.8787 | -1.8402 | -4.097 | 0.082397 | -48.4634 | 4.8477 | -118.1351 | 117.5354 | 0.027465 | 117.9794 | -0.068664 | 0.25635 | -6.6467 | -6.6879 | -0.32501 | 0.041198 | 0.44403
1579.5781 | 122.6852 | -117.7551 | 4.8157 | 0.17003 | 0.0096232 | 0.0013935 | 0.052633 | 0.064575 | 0.0016175 | 0.09254 | 0.24261 | 4.8706 | -0.2243 | -117.8558 | -1.8265 | -4.0741 | 0.004578 | -48.4634 | 4.8843 | -118.1442 | 117.5308 | 0.054931 | 117.9977 | -0.10071 | 0.28839 | -6.6422 | -6.7108 | -0.3891 | 0.068664 | 0.46692
1580.5781 | 122.7219 | -117.8101 | 4.8019 | 0.040327 | 0.007487 | -0.0026653 | 0.052205 | 0.064361 | 0.0028991 | 0.090617 | 0.15564 | 4.8019 | -0.28381 | -117.897 | -1.7807 | -4.097 | 0.09613 | -48.468 | 4.8248 | -118.1808 | 117.5262 | 0 | 117.9657 | -0.086975 | 0.28381 | -6.5826 | -6.6055 | -0.37079 | 0.022888 | 0.43945
1581.5781 | 122.7173 | -117.8101 | 4.7928 | 0.055586 | 0.007487 | -0.00074266 | 0.056264 | 0.06543 | -0.0011597 | 0.091899 | 0.20142 | 4.7882 | -0.27466 | -117.8696 | -1.7395 | -4.0558 | 0.041199 | -48.4451 | 4.8477 | -118.1488 | 117.5354 | -0.004578 | 118.0115 | -0.059509 | 0.27924 | -6.5323 | -6.5872 | -0.33875 | 0.054931 | 0.47607
1582.5781 | 122.7173 | -117.7872 | 4.8019 | 0.0021796 | 0.0089824 | 0.0054525 | 0.052205 | 0.06308 | 0.0014039 | 0.092753 | 0.20599 | 4.8065 | -0.27924 | -117.8741 | -1.7624 | -4.0558 | 0.041199 | -48.4222 | 4.8386 | -118.158 | 117.5079 | 0.004578 | 117.9932 | -0.086976 | 0.28381 | -6.5643 | -6.601 | -0.37079 | 0.036621 | 0.48523
1583.5781 | 122.7264 | -117.7872 | 4.8111 | 0.0098091 | 0.0066326 | 0.0020345 | 0.053701 | 0.064789 | 0.0016175 | 0.091899 | 0.19684 | 4.8157 | -0.28839 | -117.865 | -1.7761 | -4.0283 | 0.036621 | -48.4268 | 4.8569 | -118.1396 | 117.4988 | 0.004578 | 117.984 | -0.07782 | 0.27466 | -6.5872 | -6.633 | -0.35248 | 0.045777 | 0.48523
1584.5781 | 122.7036 | -117.8375 | 4.7836 | -0.051226 | 0.0085552 | -0.00010166 | 0.051564 | 0.064361 | 0.0020447 | 0.092753 | 0.16022 | 4.8065 | -0.28381 | -117.9337 | -1.7899 | -4.0649 | 0.11444 | -48.4543 | 4.8431 | -118.1534 | 117.5537 | 0.022889 | 117.9977 | -0.096131 | 0.21973 | -6.5735 | -6.633 | -0.31586 | 0.05951 | 0.44403
1585.5781 | 122.6898 | -117.8055 | 4.7928 | 0.093733 | 0.0051372 | 0.0043843 | 0.051137 | 0.064148 | 0.0003357 | 0.093821 | 0.16022 | 4.8386 | -0.28839 | -117.9199 | -1.2085 | -3.891 | 0.11902 | -48.4909 | 4.8569 | -118.1396 | 117.5171 | 0.045776 | 117.9657 | -0.11444 | 0.21973 | -6.0013 | -6.0654 | -0.33417 | 0.064087 | 0.44861
1586.5781 | 122.7219 | -117.7826 | 4.8386 | -0.013079 | 0.0049236 | 0.0018209 | 0.05306 | 0.063934 | 0.0018311 | 0.093608 | 0.17395 | 4.8477 | -0.28381 | -117.865 | -1.149 | -3.8177 | 0.073242 | -48.4131 | 4.8843 | -118.1076 | 117.4988 | 0.009155 | 117.9565 | -0.082397 | 0.24262 | -5.9875 | -6.0333 | -0.32501 | 0.045776 | 0.45776
1587.5781 | 122.7081 | -117.7551 | 4.8203 | -0.020708 | 0.0059916 | 0.0018209 | 0.051778 | 0.065857 | -0.0003051 | 0.091471 | 0.16479 | 4.8431 | -0.27924 | -117.8558 | -1.1536 | -3.8177 | 0.068665 | -48.4314 | 4.8935 | -118.1122 | 117.4759 | 0.022889 | 117.9199 | -0.10071 | 0.25635 | -5.9738 | -6.0471 | -0.35706 | 0.073243 | 0.44403
1588.5781 | 122.7264 | -117.7505 | 4.8294 | 0.11662 | 0.0062052 | 0.0020345 | 0.053701 | 0.064789 | 0.0001221 | 0.090831 | 0.23346 | 4.8614 | -0.25635 | -117.8421 | -0.99335 | -3.7445 | 0.022888 | -48.436 | 4.8752 | -118.103 | 117.4942 | 0.032043 | 117.984 | -0.091553 | 0.26093 | -5.8228 | -5.8685 | -0.35248 | 0.045776 | 0.48981
1589.5781 | 122.7219 | -117.7597 | 4.8203 | 0.070845 | 0.0066326 | -0.0011699 | 0.05541 | 0.06543 | 0.0014039 | 0.094035 | 0.20142 | 4.8248 | -0.27466 | -117.8421 | -0.79651 | -3.7079 | 0.027466 | -48.4406 | 4.8798 | -118.1122 | 117.485 | 0.004578 | 117.9611 | -0.082397 | 0.27008 | -5.6168 | -5.6763 | -0.35248 | 0.05951 | 0.47607
1590.5781 | 122.7219 | -117.7414 | 4.8706 | 0.032698 | 0.0070598 | 0.0018209 | 0.052419 | 0.064789 | -0.0026551 | 0.091258 | 0.20599 | 4.8889 | -0.27924 | -117.8009 | -0.6546 | -3.6575 | 0.050354 | -48.3902 | 4.9026 | -118.0893 | 117.4622 | 0.018311 | 117.9474 | -0.059509 | 0.28839 | -5.5252 | -5.5573 | -0.3479 | 0.032044 | 0.48523
1591.5781 | 122.7036 | -117.7505 | 4.8798 | -0.074114 | 0.0070598 | 0.00032554 | 0.05306 | 0.065216 | 0.0005493 | 0.093608 | 0.15564 | 4.8798 | -0.27008 | -117.8558 | -0.5722 | -3.6713 | 0.11902 | -48.4497 | 4.9347 | -118.103 | 117.4805 | 0 | 117.9062 | -0.10529 | 0.24719 | -5.452 | -5.5069 | -0.35248 | 0.054931 | 0.42572
1592.5781 | 122.6761 | -117.7689 | 4.8569 | 0.22343 | 0.0072734 | 0.0022481 | 0.052419 | 0.063934 | 0.0011901 | 0.093608 | 0.14648 | 4.8935 | -0.24719 | -117.865 | -0.58594 | -3.6575 | 0.11444 | -48.3856 | 4.9118 | -118.103 | 117.5217 | 0.036621 | 117.9153 | -0.09613 | 0.23804 | -5.4428 | -5.4977 | -0.33417 | 0.054931 | 0.39368
1593.5781 | 122.7173 | -117.7002 | 4.9118 | -0.013079 | 0.0072734 | 0.00053914 | 0.051564 | 0.065002 | -0.0005189 | 0.091685 | 0.1831 | 4.9118 | -0.27924 | -117.7734 | -0.54016 | -3.5934 | 0.091553 | -48.4772 | 4.953 | -118.0206 | 117.421 | 0 | 117.8833 | -0.073242 | 0.24719 | -5.452 | -5.4932 | -0.32044 | 0.041199 | 0.46234
1594.5781 | 122.7036 | -117.6407 | 4.9438 | 0.14714 | 0.0070598 | 0.0028889 | 0.056051 | 0.063293 | -9.1495e-05 | 0.093608 | 0.23346 | 4.9484 | -0.27008 | -117.7277 | -0.51727 | -3.5614 | 0.041199 | -48.4222 | 5.0079 | -117.9932 | 117.3706 | 0.004577 | 117.8741 | -0.086975 | 0.2655 | -5.4611 | -5.5252 | -0.35248 | 0.064087 | 0.50354
1595.5781 | 122.7356 | -117.5903 | 4.9576 | 0.032698 | 0.0062052 | 0.0033161 | 0.052633 | 0.063507 | 0.0001221 | 0.093394 | 0.20142 | 4.9713 | -0.28839 | -117.7139 | -0.52185 | -3.5339 | 0.059509 | -48.436 | 5.0125 | -117.9703 | 117.3019 | 0.013732 | 117.7917 | -0.1236 | 0.25635 | -5.4794 | -5.5344 | -0.37994 | 0.054931 | 0.48981
1596.5781 | 122.7219 | -117.6041 | 4.9622 | -0.020708 | 0.0087688 | 0.0035299 | 0.052633 | 0.065857 | -0.0005189 | 0.093608 | 0.17395 | 4.9805 | -0.28839 | -117.7185 | -0.52185 | -3.5751 | 0.064087 | -48.4909 | 5.0034 | -117.9657 | 117.3157 | 0.018311 | 117.778 | -0.11444 | 0.24719 | -5.484 | -5.5252 | -0.36163 | 0.041199 | 0.46234
1597.5781 | 122.7081 | -117.5674 | 5.0308 | -0.020708 | 0.0066326 | 0.0022481 | 0.052846 | 0.065857 | -0.0003051 | 0.091258 | 0.16479 | 5.072 | -0.28381 | -117.6453 | -1.7807 | -3.9047 | 0.091553 | -48.5229 | 5.1315 | -117.8879 | 117.2836 | 0.041198 | 117.7322 | -0.07782 | 0.24261 | -6.8115 | -6.9122 | -0.32043 | 0.10071 | 0.44861
1598.5781 | 122.7264 | -117.5171 | 5.1041 | -0.051226 | 0.0072734 | -0.0013835 | 0.04836 | 0.064789 | 0.0009765 | 0.09318 | 0.14648 | 5.0537 | -0.28839 | -117.7002 | -1.9501 | -3.9825 | 0.14648 | -48.6008 | 5.0995 | -117.8741 | 117.2287 | -0.050354 | 117.6636 | -0.1831 | 0.17395 | -7.0541 | -7.0496 | -0.35706 | -0.004578 | 0.43488
1599.5781 | 122.6715 | -117.7002 | 4.9484 | 0.0021796 | 0.0062052 | -0.0024517 | 0.05071 | 0.061371 | 0.0001221 | 0.091899 | 0.14191 | 4.9484 | -0.28839 | -117.8055 | -2.298 | -4.1245 | 0.14648 | -48.6877 | 5.0308 | -118.0115 | 117.4118 | 0 | 117.8421 | -0.10529 | 0.20599 | -7.2464 | -7.3288 | -0.31128 | 0.082398 | 0.4303
1600.5781 | 122.6761 | -117.5354 | 5.0903 | -0.074114 | 0.0055644 | -0.0030925 | 0.04836 | 0.065002 | 0.0011901 | 0.091471 | 0.13733 | 5.0674 | -0.28839 | -117.6453 | -1.5015 | -3.8177 | 0.07782 | -48.642 | 5.1453 | -117.9062 | 117.247 | -0.022888 | 117.6727 | -0.10986 | 0.26093 | -6.5918 | -6.6467 | -0.37079 | 0.054932 | 0.42572
1601.5781 | 122.6898 | -117.4255 | 5.2094 | -0.081743 | 0.0042826 | 0.0031025 | 0.047719 | 0.062866 | 0.0003357 | 0.091044 | 0.14191 | 5.1727 | -0.28839 | -117.5858 | -1.1215 | -3.6575 | 0.15106 | -48.555 | 5.2185 | -117.7689 | 117.1371 | -0.036622 | 117.5674 | -0.16022 | 0.18311 | -6.3309 | -6.34 | -0.34332 | 0.009155 | 0.4303
1602.5781 | 122.6669 | -117.5766 | 5.0446 | -0.043596 | 0.0059916 | -0.00052906 | 0.047719 | 0.061371 | 0.0016175 | 0.091044 | 0.14191 | 5.0537 | -0.24719 | -117.691 | -2.449 | -4.0695 | 0.10529 | -48.7335 | 5.0812 | -117.9382 | 117.3294 | 0.009155 | 117.7185 | -0.11444 | 0.24719 | -7.4936 | -7.5302 | -0.36163 | 0.036621 | 0.3891
1603.5938 | 122.7631 | -117.4164 | 5.1132 | 0.36839 | 0.0072734 | 0.0013935 | 0.04601 | 0.064148 | 0.0026855 | 0.092112 | 0.25177 | 5.0858 | -0.24719 | -117.54 | -2.1515 | -3.8452 | -0.16937 | -48.5458 | 5.1315 | -117.7277 | 117.1692 | -0.027466 | 117.6682 | -0.1236 | 0.18768 | -7.2647 | -7.283 | -0.31128 | 0.018311 | 0.49896
1604.5781 | 122.699 | -117.5217 | 5.0812 | -0.0054494 | 0.0085552 | -0.0013835 | 0.050924 | 0.061798 | 0.0005493 | 0.091044 | 0.18768 | 5.0812 | -0.27924 | -117.6132 | -2.1332 | -3.923 | 0.10071 | -48.7106 | 5.127 | -117.8696 | 117.2424 | 0 | 117.7094 | -0.091553 | 0.25635 | -7.2144 | -7.2601 | -0.3479 | 0.045776 | 0.46692
1605.5781 | 122.7081 | -117.5079 | 5.0949 | -0.035967 | 0.0059916 | -0.00074266 | 0.045797 | 0.063507 | 0.0024719 | 0.091471 | 0.19684 | 5.0537 | -0.25635 | -117.5766 | -1.9455 | -3.8177 | 0.045776 | -48.6328 | 5.1315 | -117.8238 | 117.2516 | -0.041199 | 117.7048 | -0.068664 | 0.24719 | -7.0404 | -7.077 | -0.31586 | 0.036621 | 0.45319
1606.5781 | 122.699 | -117.5629 | 5.072 | -0.12752 | 0.004069 | 0.0028889 | 0.051137 | 0.061157 | 0.0014039 | 0.090403 | 0.16479 | 5.0491 | -0.27008 | -117.6773 | -2.0645 | -3.9047 | 0.10986 | -48.7335 | 5.0812 | -117.8925 | 117.2928 | -0.022888 | 117.7277 | -0.11444 | 0.21515 | -7.1365 | -7.1457 | -0.32959 | 0.009156 | 0.43488
1607.5781 | 122.6852 | -117.5812 | 5.0629 | -0.043596 | 0.0049236 | 0.00053914 | 0.048146 | 0.060516 | 0.0005493 | 0.09254 | 0.18768 | 4.9988 | -0.25635 | -117.6727 | -2.092 | -3.8773 | 0.11444 | -48.7656 | 5.0903 | -117.8787 | 117.3248 | -0.064087 | 117.7689 | -0.091552 | 0.20599 | -7.1548 | -7.1823 | -0.29755 | 0.027466 | 0.44403
1608.5781 | 122.7036 | -117.5858 | 5.0537 | -0.028338 | 0.0068462 | -0.00074266 | 0.052205 | 0.060089 | 0.0003357 | 0.091685 | 0.15106 | 5.0034 | -0.27466 | -117.7048 | -2.0096 | -3.8773 | 0.15106 | -48.9944 | 5.0766 | -117.9291 | 117.3111 | -0.050354 | 117.7368 | -0.11902 | 0.2243 | -7.0633 | -7.0862 | -0.34332 | 0.022888 | 0.42572
1609.5781 | 122.6578 | -117.5995 | 5.0034 | 0.25395 | 0.0094096 | 0.00053914 | 0.054982 | 0.061798 | -0.0005189 | 0.09254 | 0.20142 | 4.9988 | -0.29755 | -117.7139 | -2.0416 | -3.8635 | 0.009155 | -49.0677 | 5.0537 | -117.952 | 117.3019 | -0.004578 | 117.8009 | -0.11444 | 0.23804 | -7.045 | -7.0953 | -0.35248 | 0.050354 | 0.49896
1610.5781 | 122.699 | -117.6086 | 4.9942 | -0.028338 | 0.0044962 | 0.00053914 | 0.048787 | 0.063721 | 0.0024719 | 0.092967 | 0.17853 | 4.9576 | -0.27008 | -117.7002 | -1.9363 | -3.8177 | 0.10529 | -49.0219 | 5.0446 | -117.8833 | 117.3386 | -0.036621 | 117.7872 | -0.091552 | 0.18311 | -6.9305 | -6.9809 | -0.27466 | 0.050354 | 0.44861
1611.5781 | 122.7859 | -117.5583 | 4.9713 | -2.5003 | 0.0032146 | 0.0011799 | 0.046865 | 0.062439 | 0.0011901 | 0.091258 | 0.30212 | 4.9347 | -0.26093 | -117.6361 | -1.7853 | -3.6896 | -0.050354 | -48.9166 | 4.9896 | -117.8925 | 117.2974 | -0.036621 | 117.8604 | -0.077819 | 0.25635 | -6.7566 | -6.7749 | -0.33417 | 0.018311 | 0.56305
1612.5781 | 122.7814 | -117.5949 | 4.9301 | -0.020708 | 0.0025736 | -0.0022381 | 0.046865 | 0.060089 | -0.0007325 | 0.09254 | 0.22888 | 4.9164 | -0.24719 | -117.659 | -1.8356 | -3.7994 | 0.21515 | -48.9944 | 4.9713 | -117.9337 | 117.3477 | -0.013733 | 117.8238 | -0.064087 | 0.27466 | -6.7657 | -6.8069 | -0.33875 | 0.041198 | 0.47607
1613.5781 | 122.7493 | -117.5995 | 4.9438 | -0.013079 | 0.0034282 | 0.0026753 | 0.049642 | 0.060303 | 0.0009765 | 0.091899 | 0.24261 | 4.9164 | -0.25635 | -117.659 | -1.8494 | -3.6758 | -0.050354 | -48.9624 | 4.9667 | -117.9153 | 117.3431 | -0.027466 | 117.8421 | -0.05951 | 0.25635 | -6.7932 | -6.8161 | -0.31586 | 0.022888 | 0.49896
1614.5781 | 122.699 | -117.6773 | 4.9484 | 0.14714 | 0.0079142 | -0.00095626 | 0.057119 | 0.062439 | -0.0005189 | 0.092112 | 0.2243 | 4.9576 | -0.23804 | -117.7139 | -1.9592 | -3.7811 | -0.022888 | -49.1409 | 4.9805 | -118.0252 | 117.4393 | 0.009156 | 117.9016 | -0.036621 | 0.31128 | -6.9077 | -6.9397 | -0.3479 | 0.032044 | 0.46234
1615.5781 | 122.6807 | -117.6636 | 4.9484 | -0.081743 | 0.005778 | 0.0011799 | 0.050496 | 0.060516 | 0.0007629 | 0.092326 | 0.16937 | 4.9118 | -0.26093 | -117.7643 | -1.9501 | -3.7765 | 0.10071 | -49.1959 | 4.9896 | -117.9794 | 117.4026 | -0.036621 | 117.8329 | -0.10071 | 0.21515 | -6.8985 | -6.9397 | -0.31586 | 0.041199 | 0.4303
1616.5781 | 122.7951 | -117.6361 | 4.921 | 1.2458 | 0.0049236 | -0.00052906 | 0.047506 | 0.059235 | 0.0016175 | 0.092112 | 0.23346 | 4.8523 | -0.2655 | -117.6865 | -1.8036 | -3.6713 | -0.068665 | -49.1638 | 4.9438 | -117.9565 | 117.3706 | -0.068664 | 117.8696 | -0.050354 | 0.27008 | -6.7245 | -6.7474 | -0.32044 | 0.022889 | 0.49896
1617.5781 | 122.8134 | -117.6453 | 4.8843 | -0.035967 | 0.0025736 | 0.0045979 | 0.046224 | 0.061157 | -0.0009461 | 0.092326 | 0.23346 | 4.8523 | -0.23804 | -117.691 | -1.8585 | -3.7903 | 0.16937 | -49.1455 | 4.9484 | -117.9749 | 117.4072 | -0.032043 | 117.8787 | -0.045776 | 0.28381 | -6.7429 | -6.8069 | -0.32959 | 0.064087 | 0.4715
1618.5781 | 122.7905 | -117.6224 | 4.921 | 0.086103 | 0.00236 | -0.0056559 | 0.045156 | 0.059662 | 0.0003357 | 0.09019 | 0.20142 | 4.866 | -0.25635 | -117.6865 | -1.9043 | -3.6987 | -0.10986 | -48.8388 | 4.9622 | -117.9428 | 117.366 | -0.054931 | 117.8238 | -0.064087 | 0.25635 | -6.8253 | -6.8665 | -0.32043 | 0.041199 | 0.45776
1619.5781 | 122.6761 | -117.6636 | 4.9255 | -1.4093 | 0.0089824 | -0.0020243 | 0.054982 | 0.060089 | 0.0001221 | 0.09019 | 0.27466 | 4.9759 | -0.24261 | -117.7551 | -1.9684 | -3.8177 | 0.11902 | -48.8754 | 5.0034 | -118.0344 | 117.421 | 0.050354 | 117.9382 | -0.091553 | 0.27924 | -6.8939 | -6.9717 | -0.37079 | 0.07782 | 0.51727
1620.5781 | 122.8134 | -117.6498 | 4.8935 | -0.020708 | 0.005778 | -0.0015971 | 0.046865 | 0.059021 | -0.0005189 | 0.090831 | 0.25177 | 4.8294 | -0.23346 | -117.6819 | -1.8585 | -3.6942 | -0.068665 | -48.7701 | 4.9026 | -117.9382 | 117.4164 | -0.064087 | 117.9016 | -0.032044 | 0.25635 | -6.752 | -6.7612 | -0.28839 | 0.009155 | 0.48523
1621.5781 | 122.731 | -117.6498 | 4.921 | -0.074114 | 0.00471 | -0.0020243 | 0.050069 | 0.061371 | 0.0024719 | 0.090617 | 0.21515 | 4.8843 | -0.26093 | -117.7277 | -1.8997 | -3.7216 | 0.041199 | -48.7518 | 4.9347 | -117.9977 | 117.3889 | -0.036621 | 117.865 | -0.07782 | 0.27008 | -6.8207 | -6.8344 | -0.3479 | 0.013733 | 0.47607
1622.5781 | 122.6807 | -117.691 | 4.921 | -0.10463 | 0.0038554 | -0.0026653 | 0.051351 | 0.060516 | -0.0009461 | 0.089976 | 0.14191 | 4.8752 | -0.2655 | -117.8284 | -1.9684 | -3.7994 | 0.10071 | -48.8388 | 4.9301 | -118.0206 | 117.4255 | -0.045776 | 117.8329 | -0.13733 | 0.19226 | -6.8893 | -6.8985 | -0.32959 | 0.009156 | 0.40741
1623.5781 | 122.8043 | -117.6315 | 4.8798 | 0.11662 | 0.0036418 | 0.0022481 | 0.048146 | 0.060089 | 0.0028991 | 0.093821 | 0.20599 | 4.8477 | -0.24719 | -117.7231 | -1.8265 | -3.6346 | -0.082397 | -48.6832 | 4.9164 | -117.952 | 117.3843 | -0.032044 | 117.8375 | -0.091552 | 0.22888 | -6.7062 | -6.7429 | -0.32043 | 0.036621 | 0.45319
1624.5781 | 122.7264 | -117.7277 | 4.8935 | -0.035967 | 0.0083416 | 0.0039571 | 0.05541 | 0.061371 | 0.0003357 | 0.089762 | 0.17853 | 4.8706 | -0.27008 | -117.7826 | -2.0142 | -3.7811 | 0.059509 | -48.7656 | 4.9118 | -118.0801 | 117.4576 | -0.022889 | 117.9062 | -0.054932 | 0.29755 | -6.9077 | -6.926 | -0.35248 | 0.01831 | 0.44861
1625.5781 | 122.7722 | -117.627 | 4.921 | 0.20817 | 0.0027874 | 0.0018209 | 0.046224 | 0.059448 | -0.0018005 | 0.091044 | 0.18768 | 4.8798 | -0.27466 | -117.7322 | -1.8631 | -3.6575 | -0.073242 | -48.6603 | 4.9438 | -117.9199 | 117.3523 | -0.041198 | 117.8146 | -0.10529 | 0.18768 | -6.7841 | -6.8069 | -0.29297 | 0.022889 | 0.46234
1626.5781 | 122.7585 | -117.6498 | 4.9164 | -0.37929 | 0.0036418 | -0.00095626 | 0.046865 | 0.057312 | 0.0003357 | 0.092326 | 0.091553 | 4.8203 | -0.29297 | -117.7689 | -1.8539 | -3.6575 | -0.073242 | -48.6649 | 4.921 | -117.9749 | 117.3569 | -0.096131 | 117.7414 | -0.11902 | 0.20599 | -6.7703 | -6.7749 | -0.32501 | 0.004577 | 0.38452
1627.5781 | 122.7676 | -117.6865 | 4.8569 | 0.20054 | 0.0042826 | -0.0015971 | 0.048146 | 0.05838 | 0.0011901 | 0.09254 | 0.16022 | 4.8706 | -0.2655 | -117.7826 | -2.0782 | -3.7262 | -0.21057 | -48.6511 | 4.8614 | -118.0389 | 117.421 | 0.013732 | 117.8467 | -0.096131 | 0.25635 | -6.9351 | -6.9397 | -0.35248 | 0.004577 | 0.42572
1628.5781 | 122.7631 | -117.6407 | 4.9072 | 0.22343 | 0.00471 | 0.0020345 | 0.049001 | 0.057098 | 0.0037537 | 0.09254 | 0.16479 | 4.8477 | -0.24719 | -117.7643 | -1.8906 | -3.6255 | -0.086975 | -48.6603 | 4.8981 | -117.9886 | 117.3935 | -0.05951 | 117.8055 | -0.1236 | 0.2243 | -6.7978 | -6.7886 | -0.3479 | -0.009156 | 0.41199
1629.5938 | 122.6761 | -117.6956 | 4.8981 | 0.23106 | 0.0096232 | 0.0039571 | 0.059255 | 0.061798 | 0.0009765 | 0.089762 | 0.20599 | 4.921 | -0.2655 | -117.7826 | -1.9226 | -3.717 | -0.004578 | -48.7244 | 4.9347 | -118.0527 | 117.4301 | 0.022888 | 117.9016 | -0.086975 | 0.27008 | -6.8207 | -6.8573 | -0.35706 | 0.036621 | 0.4715
1630.5781 | 122.8134 | -117.6453 | 4.8798 | 0.070845 | 0.00471 | -0.00095626 | 0.047506 | 0.059448 | 0.0005493 | 0.092326 | 0.23346 | 4.834 | -0.23346 | -117.6773 | -1.8402 | -3.5614 | -0.068665 | -48.5733 | 4.8935 | -117.9428 | 117.4118 | -0.045777 | 117.8787 | -0.032043 | 0.2655 | -6.72 | -6.7337 | -0.29755 | 0.013733 | 0.46692
1631.5781 | 122.7585 | -117.6682 | 4.8935 | 0.3455 | 0.0062052 | 0.0048115 | 0.048146 | 0.061798 | -0.0013733 | 0.092112 | 0.19684 | 4.8569 | -0.23804 | -117.7643 | -1.8448 | -3.6255 | -0.1236 | -48.6374 | 4.9255 | -117.9749 | 117.4301 | -0.036621 | 117.865 | -0.09613 | 0.21057 | -6.7383 | -6.7703 | -0.3067 | 0.032043 | 0.43488
1632.5781 | 122.7493 | -117.6498 | 4.8935 | 0.36076 | 0.00471 | -0.00010166 | 0.051992 | 0.058594 | 0.0011901 | 0.092967 | 0.20142 | 4.8523 | -0.22888 | -117.7551 | -1.8127 | -3.5843 | -0.13733 | -48.5458 | 4.9026 | -117.952 | 117.421 | -0.041199 | 117.8513 | -0.10529 | 0.19684 | -6.7062 | -6.7154 | -0.30212 | 0.009155 | 0.4303
1633.5781 | 122.7585 | -117.6453 | 4.8752 | 0.26921 | 0.0038554 | 0.0031025 | 0.050069 | 0.058166 | -0.0003051 | 0.091685 | 0.16479 | 4.8706 | -0.24261 | -117.7872 | -1.7761 | -3.5751 | -0.082397 | -48.555 | 4.8935 | -118.0115 | 117.4026 | -0.004578 | 117.8101 | -0.14191 | 0.22431 | -6.6513 | -6.6696 | -0.36621 | 0.018311 | 0.40741
1634.5781 | 122.8088 | -117.6453 | 4.8889 | 0.025068 | 0.0021464 | -0.0052287 | 0.049001 | 0.058166 | -0.0013733 | 0.09019 | 0.23804 | 4.8477 | -0.25177 | -117.6773 | -1.7624 | -3.5065 | -0.068665 | -48.4314 | 4.8981 | -117.9703 | 117.3935 | -0.041199 | 117.8833 | -0.032043 | 0.29297 | -6.6513 | -6.6605 | -0.32501 | 0.009155 | 0.48981
1635.5781 | 122.7997 | -117.659 | 4.8981 | 0.086103 | 0.0055644 | 0.0022481 | 0.047506 | 0.05838 | -0.0011597 | 0.09254 | 0.20142 | 4.8569 | -0.23346 | -117.7231 | -1.7349 | -3.4973 | -0.086975 | -48.4268 | 4.9164 | -117.9382 | 117.4255 | -0.041198 | 117.8604 | -0.064086 | 0.21515 | -6.633 | -6.6513 | -0.27923 | 0.018311 | 0.43488
1636.5781 | 122.7448 | -117.7185 | 4.834 | 0.17766 | 0.0051372 | 0.00011194 | 0.046651 | 0.057739 | -0.0005189 | 0.090831 | 0.16022 | 4.8431 | -0.25635 | -117.7963 | -2.0782 | -3.6804 | -0.1831 | -48.5596 | 4.8431 | -118.0481 | 117.4622 | 0.009156 | 117.8787 | -0.07782 | 0.25177 | -6.9122 | -6.9214 | -0.32959 | 0.009156 | 0.41657
1637.5781 | 122.7905 | -117.6682 | 4.866 | -0.028338 | 0.0049236 | -0.0022381 | 0.049428 | 0.054748 | -0.0003051 | 0.091899 | 0.21515 | 4.8294 | -0.25635 | -117.8238 | -1.9089 | -3.566 | 0.004578 | -48.4085 | 4.8843 | -117.9932 | 117.4118 | -0.036621 | 117.8833 | -0.15564 | 0.16937 | -6.7749 | -6.7932 | -0.32501 | 0.01831 | 0.4715
1638.5781 | 122.7951 | -117.6727 | 4.8431 | -0.020708 | 0.0070598 | 0.00075274 | 0.048146 | 0.057953 | -0.0011597 | 0.093394 | 0.2243 | 4.8203 | -0.25177 | -117.746 | -1.6663 | -3.4744 | -0.27924 | -48.5092 | 4.8614 | -117.9932 | 117.421 | -0.022889 | 117.897 | -0.073243 | 0.24719 | -6.5094 | -6.5277 | -0.32043 | 0.01831 | 0.47607
1639.5781 | 122.8134 | -117.6407 | 4.8523 | 0.4752 | 0.0053508 | -0.00095626 | 0.052419 | 0.060516 | 0.0014039 | 0.09318 | 0.25635 | 4.8111 | -0.27466 | -117.7505 | -1.7761 | -3.5568 | -0.19684 | -48.3673 | 4.8706 | -117.9886 | 117.366 | -0.041199 | 117.897 | -0.10986 | 0.23804 | -6.6284 | -6.6467 | -0.3479 | 0.01831 | 0.53101
1640.5781 | 122.7631 | -117.7094 | 4.8477 | 0.38365 | 0.0064188 | 0.00096634 | 0.05071 | 0.059662 | 0.0026855 | 0.092753 | 0.21057 | 4.7974 | -0.22888 | -117.8009 | -1.8311 | -3.5889 | -0.14648 | -48.3765 | 4.8569 | -117.9977 | 117.4805 | -0.050354 | 117.9199 | -0.091552 | 0.19684 | -6.6788 | -6.6879 | -0.28839 | 0.009156 | 0.43945
1641.5781 | 122.7493 | -117.6956 | 4.8569 | 0.2921 | 0.00471 | 0.00053914 | 0.048574 | 0.058166 | 0.0018311 | 0.093821 | 0.16479 | 4.8065 | -0.24719 | -117.8101 | -1.8082 | -3.566 | -0.091553 | -48.3078 | 4.8752 | -118.0115 | 117.4484 | -0.050354 | 117.8604 | -0.11444 | 0.20142 | -6.665 | -6.6833 | -0.31586 | 0.01831 | 0.41199
1642.5781 | 122.818 | -117.6773 | 4.8431 | 0.12425 | 0.00471 | -0.0048015 | 0.047933 | 0.057953 | 0.0005493 | 0.092326 | 0.21057 | 4.8111 | -0.23804 | -117.7368 | -1.7303 | -3.5202 | -0.10529 | -48.2071 | 4.8569 | -118.0161 | 117.4393 | -0.032044 | 117.8879 | -0.059509 | 0.27924 | -6.5735 | -6.5872 | -0.33875 | 0.013733 | 0.44861
1643.5781 | 122.7676 | -117.6773 | 4.8569 | 0.64305 | 0.0051372 | -0.0018107 | 0.04836 | 0.059235 | 0.0007629 | 0.091685 | 0.13275 | 4.7791 | -0.28381 | -117.7872 | -1.7715 | -3.5477 | -0.059509 | -48.2758 | 4.8981 | -118.0069 | 117.3935 | -0.07782 | 117.8101 | -0.10986 | 0.21973 | -6.6284 | -6.6696 | -0.32959 | 0.041198 | 0.41656
1644.5781 | 122.7951 | -117.659 | 4.8889 | 0.13188 | 0.0038554 | -0.0018107 | 0.047933 | 0.060089 | 0.0026855 | 0.091258 | 0.21057 | 4.8477 | -0.24261 | -117.7277 | -1.6937 | -3.479 | -0.082397 | -48.1705 | 4.8798 | -117.984 | 117.4164 | -0.041199 | 117.8696 | -0.068664 | 0.25635 | -6.5826 | -6.5735 | -0.32501 | -0.009155 | 0.45319
1645.5781 | 122.8363 | -117.7002 | 4.8386 | 0.093733 | 0.0034282 | -0.00052906 | 0.046437 | 0.059662 | 0.0018311 | 0.090403 | 0.23804 | 4.8019 | -0.23346 | -117.7139 | -1.6479 | -3.447 | -0.10529 | -48.2162 | 4.8798 | -117.9749 | 117.4667 | -0.036621 | 117.9382 | -0.013733 | 0.26093 | -6.4865 | -6.5277 | -0.27466 | 0.041199 | 0.4715
1646.5781 | 122.7448 | -117.7002 | 4.8431 | 0.37602 | 0.0044962 | -0.0015971 | 0.049001 | 0.059235 | 0.0009765 | 0.091471 | 0.18768 | 4.8065 | -0.21515 | -117.8101 | -1.7899 | -3.5431 | -0.12817 | -48.2849 | 4.8569 | -117.9977 | 117.485 | -0.036621 | 117.8879 | -0.10986 | 0.18768 | -6.633 | -6.6467 | -0.29755 | 0.013733 | 0.40283
1647.5781 | 122.7448 | -117.7002 | 4.8477 | 0.35313 | 0.0032146 | -0.00052906 | 0.049215 | 0.058166 | 0.0026855 | 0.092112 | 0.19684 | 4.8019 | -0.23346 | -117.7872 | -1.7395 | -3.5294 | -0.14648 | -48.2346 | 4.8843 | -118.0206 | 117.4667 | -0.045776 | 117.897 | -0.086975 | 0.23346 | -6.5872 | -6.6238 | -0.32044 | 0.036621 | 0.4303
1648.5781 | 122.7493 | -117.7048 | 4.8386 | 0.20817 | 0.0025736 | -0.00031526 | 0.050924 | 0.059448 | 0.0005493 | 0.090403 | 0.16479 | 4.8065 | -0.26093 | -117.8055 | -1.7212 | -3.5065 | -0.10529 | -48.2254 | 4.866 | -118.0344 | 117.4438 | -0.032043 | 117.8696 | -0.10071 | 0.22888 | -6.5598 | -6.5872 | -0.32959 | 0.027466 | 0.42572
1649.5781 | 122.7997 | -117.7048 | 4.834 | 0.11662 | 0.0034282 | 0.00096634 | 0.048146 | 0.057739 | 0.0028991 | 0.089976 | 0.21515 | 4.8248 | -0.23346 | -117.746 | -1.767 | -3.4927 | -0.091553 | -48.0515 | 4.866 | -118.0069 | 117.4713 | -0.009155 | 117.9199 | -0.041199 | 0.26093 | -6.601 | -6.633 | -0.30212 | 0.032044 | 0.44861
1650.5781 | 122.7631 | -117.7094 | 4.8477 | 0.29973 | 0.0053508 | -0.00095626 | 0.046865 | 0.05838 | 0.0011901 | 0.092326 | 0.14191 | 4.747 | -0.27924 | -117.8192 | -1.8173 | -3.5248 | -0.086975 | -48.111 | 4.8386 | -118.0298 | 117.4301 | -0.10071 | 117.8513 | -0.10986 | 0.21057 | -6.665 | -6.6559 | -0.32043 | -0.009155 | 0.42114
1651.5781 | 122.7814 | -117.7002 | 4.8569 | -0.18855 | 0.001292 | 0.0024617 | 0.048574 | 0.060303 | -9.1495e-05 | 0.092326 | 0.1236 | 4.7745 | -0.28381 | -117.8101 | -1.7624 | -3.4927 | -0.059509 | -48.0606 | 4.8569 | -118.0069 | 117.4164 | -0.082398 | 117.8238 | -0.10986 | 0.19684 | -6.6193 | -6.6193 | -0.3067 | 0 | 0.40741
1652.5781 | 122.7676 | -117.7322 | 4.8157 | 0.22343 | 0.0062052 | -0.00074266 | 0.046865 | 0.059662 | 0.0005493 | 0.093821 | 0.16937 | 4.8065 | -0.24261 | -117.8284 | -1.767 | -3.5065 | -0.086975 | -48.0423 | 4.8019 | -118.0298 | 117.4896 | -0.009155 | 117.9016 | -0.09613 | 0.20142 | -6.5826 | -6.5689 | -0.29755 | -0.013733 | 0.41199
1653.5781 | 122.7631 | -117.7368 | 4.7745 | 0.2921 | 0.0017192 | -0.0041607 | 0.048574 | 0.059021 | 0.0018311 | 0.090403 | 0.14648 | 4.8065 | -0.22888 | -117.8009 | -1.8402 | -3.6255 | -0.16937 | -48.0835 | 4.8019 | -118.071 | 117.5079 | 0.032044 | 117.8833 | -0.064087 | 0.27008 | -6.6147 | -6.6422 | -0.33417 | 0.027466 | 0.37537
1654.5781 | 122.8088 | -117.6682 | 4.8569 | 0.23869 | 0.0038554 | -0.00010166 | 0.046651 | 0.059235 | 0.0011901 | 0.093394 | 0.17395 | 4.8248 | -0.23804 | -117.7643 | -1.7532 | -3.4378 | -0.064087 | -47.8546 | 4.8752 | -118.0023 | 117.4301 | -0.032044 | 117.8421 | -0.09613 | 0.23804 | -6.6101 | -6.6284 | -0.33417 | 0.01831 | 0.41199
1655.5781 | 122.7676 | -117.7185 | 4.8203 | 0.26921 | 0.0070598 | 0.00032554 | 0.04601 | 0.057526 | 0.0033265 | 0.089549 | 0.16937 | 4.7882 | -0.23346 | -117.8101 | -1.799 | -3.4744 | -0.09613 | -47.9691 | 4.8157 | -118.0389 | 117.485 | -0.032043 | 117.8879 | -0.091553 | 0.22888 | -6.6193 | -6.6147 | -0.32043 | -0.004577 | 0.40283
1656.5781 | 122.7493 | -117.7277 | 4.8294 | 0.25395 | 0.0070598 | -0.0013835 | 0.047506 | 0.058807 | 0.0005493 | 0.091471 | 0.17395 | 4.7928 | -0.23346 | -117.8146 | -1.8036 | -3.479 | -0.10986 | -47.9141 | 4.8523 | -118.0389 | 117.4942 | -0.036621 | 117.9016 | -0.086975 | 0.2243 | -6.633 | -6.6559 | -0.31128 | 0.022888 | 0.40741
1657.5781 | 122.7448 | -117.7551 | 4.8248 | 0.1624 | 0.0038554 | -0.0020243 | 0.049215 | 0.056885 | 0.0003357 | 0.092112 | 0.10986 | 4.8065 | -0.26093 | -117.8375 | -1.7532 | -3.4653 | -0.082397 | -47.8729 | 4.8248 | -118.0298 | 117.4942 | -0.01831 | 117.865 | -0.082397 | 0.19226 | -6.5781 | -6.5781 | -0.27466 | 0 | 0.37079
1658.5781 | 122.7768 | -117.7048 | 4.8203 | 0.19291 | 0.0034282 | -0.00095626 | 0.046865 | 0.059235 | 0.0028991 | 0.092967 | 0.17853 | 4.8065 | -0.2243 | -117.7917 | -1.6983 | -3.3966 | -0.07782 | -47.7631 | 4.8203 | -118.0298 | 117.4805 | -0.013732 | 117.8833 | -0.086975 | 0.23804 | -6.5186 | -6.5186 | -0.32501 | 0 | 0.40283
1659.5781 | 122.7768 | -117.7185 | 4.8523 | 0.040327 | 0.003001 | 0.00032554 | 0.048787 | 0.061584 | 0.0007629 | 0.091685 | 0.23346 | 4.7836 | -0.21973 | -117.778 | -1.7532 | -3.4149 | 0.022888 | -47.6624 | 4.8523 | -118.0618 | 117.4988 | -0.068665 | 117.952 | -0.059509 | 0.28381 | -6.6055 | -6.6055 | -0.34332 | 0 | 0.45319
1660.5781 | 122.7539 | -117.7094 | 4.834 | 0.37602 | 0.0062052 | -0.0018107 | 0.049855 | 0.059448 | -0.0003051 | 0.092326 | 0.21973 | 4.7745 | -0.23804 | -117.8009 | -1.7075 | -3.3829 | -0.16479 | -47.6486 | 4.8431 | -118.0161 | 117.4713 | -0.059509 | 117.9291 | -0.091552 | 0.21515 | -6.5414 | -6.5506 | -0.3067 | 0.009156 | 0.45776
1661.5781 | 122.7859 | -117.7185 | 4.8157 | 0.37602 | 0.00471 | -0.0018107 | 0.051778 | 0.058594 | 0.0009765 | 0.09318 | 0.21973 | 4.7699 | -0.23346 | -117.8101 | -1.6983 | -3.3737 | -0.16937 | -47.5937 | 4.834 | -118.0069 | 117.485 | -0.045777 | 117.9382 | -0.091553 | 0.19684 | -6.514 | -6.5323 | -0.28839 | 0.01831 | 0.45319
1662.5781 | 122.7585 | -117.7414 | 4.8157 | 0.29973 | 0.0051372 | 0.0041707 | 0.046437 | 0.059021 | 0.0020447 | 0.091258 | 0.1831 | 4.7974 | -0.24261 | -117.8238 | -1.7441 | -3.3966 | -0.10986 | -47.5708 | 4.834 | -118.0527 | 117.4988 | -0.018311 | 117.9245 | -0.082398 | 0.22888 | -6.5598 | -6.5781 | -0.31128 | 0.01831 | 0.42572
1663.5781 | 122.7448 | -117.7231 | 4.7882 | 0.36839 | 0.0055644 | 0.00011194 | 0.047933 | 0.058807 | 0.0033265 | 0.093608 | 0.19684 | 4.7836 | -0.21973 | -117.8284 | -1.8539 | -3.4561 | -0.12817 | -47.525 | 4.8294 | -118.0573 | 117.5034 | -0.004578 | 117.9199 | -0.10529 | 0.22888 | -6.6422 | -6.6833 | -0.33417 | 0.041199 | 0.41657
1664.5781 | 122.7585 | -117.7002 | 4.8386 | 0.24632 | 0.0053508 | -0.0022381 | 0.04836 | 0.05838 | 0.0016175 | 0.092967 | 0.16022 | 4.8111 | -0.23804 | -117.8101 | -1.8036 | -3.4515 | -0.10071 | -47.4518 | 4.8843 | -118.0069 | 117.4622 | -0.027466 | 117.8604 | -0.10986 | 0.19684 | -6.6422 | -6.6879 | -0.3067 | 0.045776 | 0.39825
1665.5781 | 122.7585 | -117.7139 | 4.8386 | 0.36076 | 0.0062052 | -0.0022381 | 0.048146 | 0.059448 | -0.0011597 | 0.090617 | 0.15106 | 4.8203 | -0.22888 | -117.7963 | -1.7258 | -3.447 | -0.09613 | -47.3328 | 4.8477 | -118.0298 | 117.485 | -0.018311 | 117.865 | -0.082398 | 0.23346 | -6.5643 | -6.5735 | -0.31586 | 0.009155 | 0.37994
1666.5781 | 122.7585 | -117.6956 | 4.8614 | 0.3455 | 0.007487 | 0.00011194 | 0.048574 | 0.059021 | 0.0035401 | 0.09254 | 0.17853 | 4.8203 | -0.22888 | -117.8146 | -1.7761 | -3.4607 | -0.1236 | -47.2916 | 4.8477 | -118.0298 | 117.4667 | -0.041199 | 117.8741 | -0.11902 | 0.21515 | -6.6376 | -6.6238 | -0.33417 | -0.013733 | 0.40741
1667.5781 | 122.7585 | -117.7185 | 4.7974 | 0.27684 | 0.0051372 | -0.0024517 | 0.045797 | 0.056244 | 0.0005493 | 0.09254 | 0.17395 | 4.7928 | -0.24719 | -117.8055 | -1.7395 | -3.4378 | -0.082397 | -47.2916 | 4.8569 | -118.0023 | 117.4713 | -0.004577 | 117.8925 | -0.086975 | 0.19684 | -6.5369 | -6.5964 | -0.28381 | 0.05951 | 0.42114
1668.5781 | 122.7768 | -117.7094 | 4.8157 | 0.37602 | 0.0042826 | -0.0020243 | 0.047292 | 0.059021 | -0.0005189 | 0.091899 | 0.21515 | 4.7791 | -0.25177 | -117.8009 | -1.8173 | -3.4332 | -0.15564 | -47.2504 | 4.8294 | -118.0389 | 117.4576 | -0.036621 | 117.9245 | -0.091552 | 0.23804 | -6.633 | -6.6467 | -0.32959 | 0.013733 | 0.46692
1669.5781 | 122.7676 | -117.7094 | 4.8248 | 0.35313 | 0.0072734 | 0.00011194 | 0.052419 | 0.060303 | 0.0020447 | 0.093394 | 0.21057 | 4.7928 | -0.23346 | -117.7872 | -1.7395 | -3.4058 | -0.17853 | -47.2046 | 4.8523 | -118.0069 | 117.4759 | -0.032043 | 117.9199 | -0.077819 | 0.21973 | -6.5643 | -6.5918 | -0.29755 | 0.027466 | 0.44403
1670.5781 | 122.7997 | -117.7414 | 4.8065 | 0.39128 | 0.0068462 | 0.0033161 | 0.050924 | 0.060516 | 0.0005493 | 0.092326 | 0.2243 | 4.7653 | -0.23804 | -117.7963 | -1.799 | -3.4332 | -0.18768 | -47.1359 | 4.8203 | -118.0664 | 117.5034 | -0.041199 | 117.9657 | -0.054932 | 0.27008 | -6.6055 | -6.6193 | -0.32501 | 0.013732 | 0.46234
1671.5781 | 122.7631 | -117.7277 | 4.8019 | 0.27684 | 0.0042826 | -0.00074266 | 0.048787 | 0.059235 | 0.0026855 | 0.093821 | 0.15106 | 4.7836 | -0.25635 | -117.8284 | -1.8356 | -3.4561 | -0.082397 | -47.1085 | 4.834 | -118.0389 | 117.4713 | -0.018311 | 117.8787 | -0.10071 | 0.21057 | -6.6376 | -6.6696 | -0.31128 | 0.032043 | 0.40741
1672.5781 | 122.7493 | -117.7277 | 4.8111 | 0.35313 | 0.0051372 | -0.0020243 | 0.050924 | 0.058166 | 0.0031127 | 0.091685 | 0.20142 | 4.7607 | -0.23346 | -117.8238 | -1.7853 | -3.4195 | -0.12817 | -47.0673 | 4.8157 | -118.0527 | 117.4942 | -0.050354 | 117.9291 | -0.096131 | 0.22888 | -6.5964 | -6.601 | -0.32501 | 0.004578 | 0.43488
1673.5781 | 122.7585 | -117.7368 | 4.8065 | 0.35313 | 0.005778 | 0.0048115 | 0.051992 | 0.057098 | 0.0011901 | 0.089762 | 0.21515 | 4.7607 | -0.24261 | -117.8284 | -1.7944 | -3.4195 | -0.17395 | -47.0535 | 4.8111 | -118.0527 | 117.4942 | -0.045777 | 117.952 | -0.091553 | 0.2243 | -6.601 | -6.6055 | -0.31586 | 0.004577 | 0.45776
1674.5781 | 122.7722 | -117.7414 | 4.8019 | 0.39891 | 0.0032146 | 0.0011799 | 0.052633 | 0.059875 | 0.0016175 | 0.091899 | 0.21515 | 4.7607 | -0.23804 | -117.8146 | -1.7761 | -3.4332 | -0.1831 | -47.0123 | 4.8203 | -118.0435 | 117.5034 | -0.041199 | 117.9565 | -0.073242 | 0.22888 | -6.5781 | -6.5964 | -0.30212 | 0.01831 | 0.45319
1675.5781 | 122.7859 | -117.7277 | 4.7974 | 0.20817 | 0.005778 | 0.0035299 | 0.051351 | 0.060303 | 0.0007629 | 0.092753 | 0.21057 | 4.747 | -0.27008 | -117.8055 | -1.7899 | -3.4241 | -0.17853 | -46.9528 | 4.7928 | -118.071 | 117.4576 | -0.050354 | 117.9382 | -0.07782 | 0.2655 | -6.5872 | -6.5826 | -0.34332 | -0.004577 | 0.48065
1676.5781 | 122.7814 | -117.746 | 4.7745 | 1.6272 | 0.007487 | 0.0022481 | 0.052419 | 0.059875 | 0.0009765 | 0.090831 | 0.073242 | 4.6967 | -0.26093 | -117.8192 | -1.7853 | -3.4058 | -0.18768 | -46.9345 | 4.7745 | -118.0756 | 117.485 | -0.07782 | 117.8192 | -0.073242 | 0.25635 | -6.5598 | -6.5598 | -0.32959 | 0 | 0.33417
1677.5781 | 122.7585 | -117.7231 | 4.7974 | 0.30736 | 0.0059916 | 0.0026753 | 0.049001 | 0.059662 | 0.0018311 | 0.092112 | 0.20599 | 4.7653 | -0.23804 | -117.8329 | -1.7899 | -3.4195 | -0.17853 | -46.9574 | 4.8157 | -118.0618 | 117.485 | -0.032043 | 117.9291 | -0.10986 | 0.22888 | -6.5872 | -6.6055 | -0.33875 | 0.018311 | 0.44403
1678.5781 | 122.7585 | -117.7322 | 4.8019 | 0.39891 | 0.0051372 | -0.0024517 | 0.051564 | 0.061584 | -0.0005189 | 0.094035 | 0.21515 | 4.7653 | -0.24719 | -117.8009 | -1.7578 | -3.4012 | -0.17853 | -46.9025 | 4.8477 | -118.0618 | 117.485 | -0.036621 | 117.9474 | -0.068664 | 0.26093 | -6.5598 | -6.6055 | -0.32959 | 0.045776 | 0.46234
1679.5781 | 122.7676 | -117.7551 | 4.7882 | 0.25395 | 0.0064188 | -0.00031526 | 0.046651 | 0.058166 | 0.0028991 | 0.090831 | 0.15106 | 4.7653 | -0.25177 | -117.865 | -1.7761 | -3.4424 | -0.086975 | -46.8842 | 4.8019 | -118.0893 | 117.5034 | -0.022888 | 117.9062 | -0.10986 | 0.2243 | -6.5643 | -6.5781 | -0.33417 | 0.013733 | 0.40283
1680.5781 | 122.7951 | -117.7414 | 4.7653 | 0.40654 | 0.0049236 | 0.0056661 | 0.051137 | 0.061798 | 0.0005493 | 0.093394 | 0.059509 | 4.7195 | -0.24719 | -117.7826 | -1.7899 | -3.4058 | -0.17395 | -46.8246 | 4.7791 | -118.0939 | 117.4942 | -0.045777 | 117.8009 | -0.041199 | 0.31128 | -6.5552 | -6.5689 | -0.35248 | 0.013733 | 0.3067
1681.5781 | 122.7631 | -117.7734 | 4.7928 | 0.41417 | 0.0072734 | 0.0037435 | 0.056051 | 0.060516 | 0.0016175 | 0.092112 | 0.20599 | 4.7653 | -0.24719 | -117.8238 | -1.7441 | -3.3875 | -0.1831 | -46.8109 | 4.8111 | -118.0893 | 117.5262 | -0.027466 | 117.9794 | -0.050355 | 0.2655 | -6.5369 | -6.5552 | -0.31586 | 0.01831 | 0.45319
1682.5781 | 122.7905 | -117.7643 | 4.7745 | 0.40654 | 0.0077006 | 0.0052387 | 0.053701 | 0.062012 | 0.0014039 | 0.091685 | 0.24719 | 4.7562 | -0.21057 | -117.7963 | -1.7532 | -3.3875 | -0.21057 | -46.6873 | 4.7836 | -118.0573 | 117.5537 | -0.01831 | 118.0115 | -0.032044 | 0.26093 | -6.5277 | -6.5369 | -0.29297 | 0.009155 | 0.45776
1683.5781 | 122.7585 | -117.7277 | 4.8111 | 0.37602 | 0.0036418 | 0.00053914 | 0.049855 | 0.059875 | 0.0016175 | 0.091044 | 0.19226 | 4.7928 | -0.23804 | -117.8375 | -1.7578 | -3.4012 | -0.13275 | -46.6644 | 4.834 | -118.0573 | 117.4896 | -0.01831 | 117.9199 | -0.10986 | 0.21973 | -6.5689 | -6.5918 | -0.32959 | 0.022888 | 0.4303
1684.5781 | 122.7539 | -117.7002 | 4.7928 | 0.36839 | 0.0049236 | 0.00096634 | 0.049642 | 0.058807 | 0.0026855 | 0.09254 | 0.21515 | 4.7882 | -0.22888 | -117.7963 | -1.7395 | -3.3783 | -0.17395 | -46.5958 | 4.8294 | -118.0481 | 117.4713 | -0.004578 | 117.9153 | -0.096131 | 0.25177 | -6.5323 | -6.5689 | -0.3479 | 0.036621 | 0.44403
1685.5781 | 122.8088 | -117.7414 | 4.7974 | 0.40654 | 0.0042826 | 0.0035299 | 0.053273 | 0.061157 | -0.0007325 | 0.092967 | 0.24719 | 4.7836 | -0.24261 | -117.7963 | -1.7303 | -3.3508 | -0.2243 | -46.5866 | 4.8111 | -118.0389 | 117.4988 | -0.013733 | 117.9886 | -0.054932 | 0.24261 | -6.5277 | -6.5414 | -0.29755 | 0.013733 | 0.48981
1686.5781 | 122.7997 | -117.7139 | 4.7928 | 0.48283 | 0.0051372 | 0.0028889 | 0.054982 | 0.060516 | 0.0001221 | 0.092326 | 0.23346 | 4.7607 | -0.24719 | -117.7963 | -1.7578 | -3.36 | -0.20599 | -46.5408 | 4.8065 | -118.0664 | 117.4667 | -0.032044 | 117.9474 | -0.082398 | 0.27008 | -6.5506 | -6.5643 | -0.35248 | 0.013733 | 0.48065
1687.5781 | 122.7631 | -117.7414 | 4.8111 | 0.43706 | 0.0070598 | -0.0011699 | 0.055196 | 0.061157 | -0.0007325 | 0.092112 | 0.19684 | 4.7882 | -0.27008 | -117.8238 | -1.7487 | -3.3737 | -0.19226 | -46.5225 | 4.8157 | -118.1122 | 117.4713 | -0.022888 | 117.9382 | -0.082398 | 0.28839 | -6.5598 | -6.5643 | -0.37079 | 0.004578 | 0.46692
1688.5781 | 122.6807 | -117.7917 | 4.7928 | 1.1924 | 0.0094096 | 0.0039571 | 0.055196 | 0.061371 | -0.0005189 | 0.09318 | 0.032043 | 4.8157 | -0.27008 | -117.9291 | -1.8585 | -3.4698 | -0.036621 | -46.5866 | 4.8477 | -118.1442 | 117.5217 | 0.022888 | 117.8238 | -0.13733 | 0.21515 | -6.6513 | -6.7062 | -0.35248 | 0.054931 | 0.30212
1689.5781 | 122.7173 | -117.7917 | 4.7928 | 0.35313 | 0.011759 | -0.00010166 | 0.054555 | 0.062652 | 0.0033265 | 0.092326 | 0.13733 | 4.8157 | -0.26093 | -117.9016 | -1.8219 | -3.4515 | -0.07782 | -46.4767 | 4.8248 | -118.1213 | 117.5308 | 0.022888 | 117.9291 | -0.10986 | 0.21973 | -6.6147 | -6.6467 | -0.32959 | 0.032043 | 0.39825
1690.5781 | 122.731 | -117.7826 | 4.8065 | 0.13951 | 0.0079142 | 0.00053914 | 0.053701 | 0.062652 | 0.0014039 | 0.090403 | 0.16022 | 4.8065 | -0.27924 | -117.9016 | -1.8173 | -3.4424 | -0.041199 | -46.5775 | 4.8523 | -118.1488 | 117.5034 | 0 | 117.9428 | -0.11902 | 0.24719 | -6.6238 | -6.6696 | -0.36621 | 0.045776 | 0.43945
1691.5781 | 122.7814 | -117.7322 | 4.7745 | 0.41417 | 0.0064188 | 0.0039571 | 0.051778 | 0.06308 | 0.0022583 | 0.091471 | 0.2243 | 4.747 | -0.22888 | -117.8238 | -1.7029 | -3.3279 | -0.20142 | -46.4539 | 4.7974 | -118.1122 | 117.5034 | -0.027466 | 117.9565 | -0.091553 | 0.28839 | -6.4774 | -6.5002 | -0.37994 | 0.022888 | 0.45319
1692.5781 | 122.7859 | -117.7689 | 4.7699 | 0.44468 | 0.0059916 | 0.0041707 | 0.051351 | 0.062439 | -0.0011597 | 0.090617 | 0.23346 | 4.7379 | -0.23346 | -117.8787 | -1.7441 | -3.3371 | -0.16479 | -46.4035 | 4.7562 | -118.103 | 117.5354 | -0.032043 | 118.0023 | -0.10986 | 0.2243 | -6.514 | -6.5002 | -0.33417 | -0.013732 | 0.46692
1693.5781 | 122.6807 | -117.8101 | 4.8157 | 0.32261 | 0.0094096 | -0.00074266 | 0.05541 | 0.062439 | 0.0009765 | 0.092112 | 0.11902 | 4.8111 | -0.29755 | -117.9474 | -1.8585 | -3.4744 | 0.004578 | -46.5134 | 4.8569 | -118.1763 | 117.5125 | -0.004578 | 117.9291 | -0.13733 | 0.22888 | -6.6742 | -6.7154 | -0.36621 | 0.041199 | 0.41656
1694.5781 | 122.6578 | -117.7963 | 4.7791 | 0.26921 | 0.0079142 | 0.00032554 | 0.053701 | 0.06543 | -9.1495e-05 | 0.092112 | 0.15564 | 4.8019 | -0.29297 | -117.9611 | -1.8402 | -3.4744 | 0.041199 | -46.5134 | 4.8065 | -118.1671 | 117.5034 | 0.022888 | 117.952 | -0.1648 | 0.20599 | -6.6193 | -6.6467 | -0.37079 | 0.027466 | 0.44861
1695.5781 | 122.6395 | -117.8329 | 4.7928 | 0.30736 | 0.0096232 | 0.0039571 | 0.054342 | 0.063721 | 0.0003357 | 0.091044 | 0.14648 | 4.7974 | -0.28839 | -117.9428 | -1.8356 | -3.447 | 0.036621 | -46.463 | 4.834 | -118.1763 | 117.5446 | 0.004577 | 117.9794 | -0.10986 | 0.23346 | -6.6284 | -6.6696 | -0.34332 | 0.041198 | 0.43488
1696.5781 | 122.6624 | -117.8192 | 4.8294 | 0.33024 | 0.0077006 | 0.0020345 | 0.055837 | 0.066711 | 0.0005493 | 0.094676 | 0.13275 | 4.8111 | -0.28839 | -117.952 | -1.8356 | -3.4378 | -0.013733 | -46.4493 | 4.8477 | -118.1625 | 117.5308 | -0.018311 | 117.952 | -0.13275 | 0.21057 | -6.665 | -6.6833 | -0.34332 | 0.01831 | 0.42114
1697.5781 | 122.6578 | -117.8238 | 4.7928 | 0.28447 | 0.0077006 | 0.0020345 | 0.052419 | 0.064575 | 0.0003357 | 0.09318 | 0.1236 | 4.7928 | -0.27924 | -117.9749 | -1.8768 | -3.4653 | 0.009155 | -46.3943 | 4.8248 | -118.1763 | 117.5446 | 0 | 117.9474 | -0.15106 | 0.20142 | -6.6696 | -6.7017 | -0.35248 | 0.032043 | 0.40283
1698.5781 | 122.6715 | -117.8146 | 4.7836 | 0.37602 | 0.0079142 | 0.0052387 | 0.051351 | 0.065002 | 0.0014039 | 0.091899 | 0.22888 | 4.7836 | -0.24719 | -117.9428 | -1.7853 | -3.4287 | 0.013733 | -46.3669 | 4.834 | -118.1351 | 117.5674 | 0 | 118.0435 | -0.12817 | 0.19226 | -6.5689 | -6.6193 | -0.32044 | 0.050354 | 0.47607
1699.5781 | 122.7219 | -117.7963 | 4.7791 | 0.33024 | 0.0070598 | 0.0065205 | 0.049642 | 0.064575 | 0.0020447 | 0.094035 | 0.15106 | 4.7928 | -0.27924 | -117.9337 | -1.8173 | -3.4058 | -0.07782 | -46.2067 | 4.8111 | -118.1808 | 117.5171 | 0.013733 | 117.9474 | -0.13733 | 0.24719 | -6.5964 | -6.6284 | -0.38452 | 0.032043 | 0.4303
1700.5781 | 122.7768 | -117.7917 | 4.7562 | 0.43706 | 0.0055644 | 0.0018209 | 0.050283 | 0.063934 | 0.0009765 | 0.094676 | 0.19684 | 4.7516 | -0.25635 | -117.897 | -1.7715 | -3.3417 | -0.16937 | -46.2616 | 4.7745 | -118.1671 | 117.5354 | -0.004578 | 117.9886 | -0.10529 | 0.27008 | -6.5277 | -6.546 | -0.37537 | 0.01831 | 0.45319
1701.5781 | 122.6578 | -117.8467 | 4.7607 | 0.27684 | 0.0089824 | 0.0035299 | 0.053487 | 0.06543 | -0.0005189 | 0.093394 | 0.16479 | 4.7745 | -0.2655 | -117.952 | -1.8631 | -3.4424 | 0.027466 | -46.3669 | 4.8065 | -118.2129 | 117.5812 | 0.013733 | 118.0115 | -0.10528 | 0.26093 | -6.6238 | -6.6696 | -0.36621 | 0.045777 | 0.4303
1702.5781 | 122.7036 | -117.8238 | 4.7562 | 0.17766 | 0.0094096 | 0.0033161 | 0.053701 | 0.064361 | 0.0011901 | 0.092753 | 0.17853 | 4.7882 | -0.27924 | -117.9657 | -1.8265 | -3.4241 | 0.022888 | -46.3074 | 4.7928 | -118.2129 | 117.5446 | 0.032043 | 118.0023 | -0.14191 | 0.24719 | -6.5826 | -6.6193 | -0.3891 | 0.036621 | 0.45776
1703.5781 | 122.6761 | -117.8375 | 4.7745 | 0.39891 | 0.009196 | -0.00010166 | 0.05306 | 0.064575 | -9.1495e-05 | 0.094676 | 0.14191 | 4.7699 | -0.28839 | -118.0206 | -1.9684 | -3.5385 | 0.19684 | -46.2433 | 4.8294 | -118.1854 | 117.5491 | -0.004578 | 117.9794 | -0.18311 | 0.16479 | -6.7429 | -6.7978 | -0.3479 | 0.054932 | 0.4303
1704.5781 | 122.6898 | -117.8558 | 4.7562 | 0.20817 | 0.0066326 | 0.0020345 | 0.053701 | 0.066711 | -9.1495e-05 | 0.091471 | 0.16022 | 4.7653 | -0.27466 | -117.9703 | -1.8311 | -3.4149 | 0.022888 | -46.2067 | 4.8065 | -118.2129 | 117.5812 | 0.009155 | 118.0161 | -0.11444 | 0.24262 | -6.5872 | -6.6376 | -0.35706 | 0.050354 | 0.43488
1705.5781 | 122.6624 | -117.8604 | 4.7516 | 0.31499 | 0.007487 | 0.0045979 | 0.051778 | 0.066498 | 0.0009765 | 0.093394 | 0.13733 | 4.7882 | -0.28381 | -118.0161 | -1.8311 | -3.4012 | 0.009155 | -46.0968 | 4.7791 | -118.2541 | 117.5766 | 0.036621 | 117.9977 | -0.15564 | 0.23804 | -6.5826 | -6.6101 | -0.39368 | 0.027466 | 0.42114
1706.5781 | 122.6486 | -117.8329 | 4.7699 | 0.26158 | 0.0072734 | -0.00052906 | 0.053487 | 0.065002 | -0.0003051 | 0.093394 | 0.13733 | 4.7745 | -0.28839 | -117.9977 | -1.8677 | -3.4195 | 0.036621 | -46.0464 | 4.8065 | -118.2312 | 117.5446 | 0.004578 | 117.9703 | -0.16479 | 0.23346 | -6.6376 | -6.6742 | -0.39825 | 0.036622 | 0.42572
1707.5781 | 122.6852 | -117.8421 | 4.7653 | 0.40654 | 0.007487 | 0.0016073 | 0.051778 | 0.064361 | -0.0011597 | 0.091471 | 0.13733 | 4.7974 | -0.28839 | -118.0115 | -1.9455 | -3.4882 | 0.19684 | -45.8725 | 4.8203 | -118.2083 | 117.5537 | 0.032043 | 117.9794 | -0.16937 | 0.19684 | -6.7108 | -6.7657 | -0.36621 | 0.054931 | 0.42572
1708.5781 | 122.6715 | -117.8329 | 4.7745 | 0.37602 | 0.009196 | 0.0041707 | 0.052846 | 0.067993 | 0.0007629 | 0.093394 | 0.13733 | 4.7699 | -0.27466 | -117.9932 | -1.8219 | -3.3646 | 0 | -45.9091 | 4.8203 | -118.19 | 117.5583 | -0.004578 | 117.9703 | -0.16022 | 0.19684 | -6.5964 | -6.6421 | -0.35706 | 0.045776 | 0.41199
1709.5781 | 122.6852 | -117.8696 | 4.7562 | 0.26158 | 0.0089824 | 0.0022481 | 0.052633 | 0.065216 | 0.0005493 | 0.094035 | 0.16479 | 4.7745 | -0.2655 | -117.984 | -1.8539 | -3.3737 | 0.022888 | -45.8588 | 4.7928 | -118.2266 | 117.6041 | 0.01831 | 118.0344 | -0.11444 | 0.24262 | -6.6101 | -6.6467 | -0.35706 | 0.036621 | 0.4303
1710.5781 | 122.6761 | -117.865 | 4.7241 | 0.1624 | 0.0079142 | 0.0035299 | 0.054342 | 0.063507 | -0.0003051 | 0.091258 | 0.17853 | 4.747 | -0.27924 | -117.9932 | -1.8539 | -3.36 | 0.013733 | -45.7672 | 4.7882 | -118.2312 | 117.5858 | 0.022888 | 118.0435 | -0.12817 | 0.23804 | -6.5781 | -6.6422 | -0.36621 | 0.064087 | 0.45776
1711.5781 | 122.6532 | -117.8513 | 4.7699 | 0.19291 | 0.010905 | 0.0033161 | 0.052846 | 0.065002 | 0.0011901 | 0.092326 | 0.15106 | 4.747 | -0.28839 | -118.0069 | -1.8494 | -3.3371 | 0.027466 | -45.7489 | 4.8065 | -118.2358 | 117.5629 | -0.022888 | 118.0023 | -0.15564 | 0.22888 | -6.6193 | -6.6559 | -0.38452 | 0.036622 | 0.43945
1712.5781 | 122.6624 | -117.8604 | 4.7516 | 0.39891 | 0.0098368 | 0.0026753 | 0.05306 | 0.065002 | 0.0018311 | 0.091044 | 0.13733 | 4.7516 | -0.27466 | -118.0252 | -1.8494 | -3.3554 | -0.009155 | -45.9229 | 4.8019 | -118.2541 | 117.5858 | 0 | 117.9977 | -0.1648 | 0.22888 | -6.601 | -6.6513 | -0.39368 | 0.050354 | 0.41199
1713.5781 | 122.6852 | -117.8604 | 4.7562 | 0.23869 | 0.0094096 | 0.0022481 | 0.055196 | 0.064361 | -0.0003051 | 0.093608 | 0.16479 | 4.7699 | -0.26093 | -117.984 | -1.8677 | -3.3371 | 0.013733 | -45.8542 | 4.7928 | -118.2312 | 117.5995 | 0.013732 | 118.0252 | -0.1236 | 0.24719 | -6.6238 | -6.6605 | -0.37079 | 0.036621 | 0.42572
1714.5781 | 122.6944 | -117.8421 | 4.7791 | 0.19291 | 0.0068462 | 0.0018209 | 0.052419 | 0.06543 | 0.0014039 | 0.091258 | 0.17395 | 4.7745 | -0.28839 | -117.952 | -1.8265 | -3.3234 | 0.009155 | -45.7718 | 4.8157 | -118.222 | 117.5537 | -0.004578 | 118.0161 | -0.10986 | 0.27008 | -6.6055 | -6.6422 | -0.37994 | 0.036621 | 0.46234
1715.5781 | 122.7356 | -112.9852 | 9.5718 | 0.093733 | 0.0085552 | 0.0060933 | 0.047719 | 0.064789 | 0.0018311 | 0.092753 | 0.36163 | 9.3384 | -0.22888 | -113.0722 | -1.355 | -1.2451 | 0.004578 | -41.9128 | 9.4894 | -113.4384 | 112.7563 | -0.23346 | 113.3469 | -0.086976 | 0.36621 | -10.9268 | -10.8444 | -0.45319 | -0.082397 | 0.59052
1716.5781 | 122.7219 | -118.2678 | 4.3304 | 0.093733 | 0.0081278 | 0.0043843 | 0.054128 | 0.062866 | 0.0024719 | 0.091258 | 0.18768 | 4.3259 | -0.2655 | -118.3594 | -2.179 | -3.5843 | 0.036621 | -45.9412 | 4.3808 | -118.6111 | 118.0023 | -0.004577 | 118.4555 | -0.091553 | 0.25177 | -6.5094 | -6.5598 | -0.34332 | 0.050354 | 0.45319
1717.5781 | 122.6852 | -118.3823 | 4.2618 | 0.26158 | 0.005778 | 0.0041707 | 0.053273 | 0.06543 | -0.0018005 | 0.09318 | 0.15106 | 4.2435 | -0.29297 | -118.5013 | -2.211 | -3.6484 | 0.018311 | -46.0327 | 4.2892 | -118.7347 | 118.0893 | -0.018311 | 118.5333 | -0.11902 | 0.23346 | -6.4728 | -6.5002 | -0.35248 | 0.027466 | 0.44403
1718.5781 | 122.7219 | -118.3228 | 4.303 | 0.1624 | 0.0089824 | 0.0050251 | 0.053273 | 0.06607 | -0.0018005 | 0.091899 | 0.1831 | 4.248 | -0.27466 | -118.2678 | -2.0554 | -3.5385 | 0.064087 | -45.9045 | 4.3533 | -118.689 | 118.0481 | -0.054932 | 118.5059 | 0.054932 | 0.42114 | -6.3583 | -6.4087 | -0.36621 | 0.050354 | 0.45776
1719.5781 | 122.6898 | -118.396 | 4.2206 | 0.1624 | 0.0081278 | 0.0016073 | 0.055623 | 0.064575 | -0.0009461 | 0.092753 | 0.17853 | 4.2114 | -0.28381 | -118.4921 | -2.092 | -3.5614 | 0.009155 | -45.9274 | 4.2709 | -118.7622 | 118.1122 | -0.009155 | 118.5745 | -0.09613 | 0.27008 | -6.3126 | -6.3629 | -0.36621 | 0.050354 | 0.46234
1720.5781 | 122.7127 | -118.3685 | 4.1931 | -0.035967 | 0.0068462 | 0.0045979 | 0.054342 | 0.064575 | 0.0026855 | 0.091899 | 0.21515 | 4.248 | -0.22888 | -118.5059 | -2.0737 | -3.5385 | 0.004578 | -45.8267 | 4.2618 | -118.7622 | 118.1396 | 0.054932 | 118.5837 | -0.13733 | 0.25635 | -6.2668 | -6.3354 | -0.39368 | 0.068665 | 0.44403
1721.5781 | 122.7173 | -118.3868 | 4.216 | 0.13951 | 0.0072734 | -0.0018107 | 0.051992 | 0.063934 | -0.0028687 | 0.091685 | 0.32959 | 4.2114 | -0.23346 | -118.4692 | -2.0462 | -3.5339 | 0.018311 | -45.813 | 4.2892 | -118.7805 | 118.1534 | -0.004577 | 118.7164 | -0.082397 | 0.31128 | -6.2622 | -6.3354 | -0.39368 | 0.073243 | 0.56305
1722.5781 | 122.7036 | -118.4052 | 4.1702 | 0.032698 | 0.005778 | 0.0043843 | 0.053914 | 0.064575 | -0.0003051 | 0.090617 | 0.15106 | 4.1977 | -0.28839 | -118.4967 | -2.037 | -3.5156 | 0.054932 | -45.7718 | 4.2572 | -118.7988 | 118.1168 | 0.027466 | 118.5562 | -0.091553 | 0.30212 | -6.2073 | -6.2942 | -0.39368 | 0.086975 | 0.43945
1723.5781 | 122.731 | -118.396 | 4.1931 | 0.10899 | 0.0068462 | 0.0013935 | 0.054342 | 0.065002 | -0.0011597 | 0.094035 | 0.17395 | 4.1885 | -0.27008 | -118.5242 | -2.0142 | -3.5019 | 0.022888 | -45.7169 | 4.2389 | -118.7851 | 118.1259 | -0.004577 | 118.5699 | -0.12817 | 0.26093 | -6.2073 | -6.2531 | -0.3891 | 0.045777 | 0.44403
1724.5781 | 122.7036 | -118.428 | 4.1611 | 0.22343 | 0.0059916 | 0.0058797 | 0.05541 | 0.065857 | -0.0018005 | 0.09254 | 0.20142 | 4.2068 | -0.24261 | -118.5287 | -2.0416 | -3.5065 | 0.009155 | -45.7169 | 4.2297 | -118.7988 | 118.1854 | 0.045776 | 118.6295 | -0.10071 | 0.27008 | -6.2027 | -6.2714 | -0.37079 | 0.068664 | 0.44403
1725.5781 | 122.7219 | -118.4418 | 4.1656 | 0.093733 | 0.0077006 | -0.00074266 | 0.054342 | 0.063293 | -0.0026551 | 0.088481 | 0.17853 | 4.1931 | -0.2655 | -118.5333 | -1.9958 | -3.4836 | 0.027466 | -45.7352 | 4.2068 | -118.8171 | 118.1763 | 0.027466 | 118.6203 | -0.091553 | 0.28381 | -6.1615 | -6.2027 | -0.37537 | 0.041199 | 0.44403
1726.5781 | 122.699 | -118.4189 | 4.2435 | 0.11662 | 0.0087688 | 0.0026753 | 0.055196 | 0.063721 | -0.0011597 | 0.090617 | 0.17853 | 4.1702 | -0.27008 | -118.5013 | -1.8036 | -3.4058 | 0.10986 | -45.6528 | 4.248 | -118.7805 | 118.1488 | -0.073242 | 118.5974 | -0.082398 | 0.27924 | -6.0471 | -6.0516 | -0.36163 | 0.004578 | 0.44861
1727.5781 | 122.731 | -118.4738 | 4.1611 | 0.10136 | 0.0068462 | 0.0054525 | 0.054555 | 0.064148 | -0.0003051 | 0.092112 | 0.1831 | 4.1611 | -0.2655 | -118.5379 | -2.0142 | -3.4698 | 0.018311 | -45.6436 | 4.2114 | -118.7897 | 118.2083 | 0 | 118.6569 | -0.064087 | 0.25177 | -6.1752 | -6.2256 | -0.31586 | 0.050354 | 0.44861
1728.5781 | 122.7127 | -118.3044 | 4.2984 | 0.11662 | 0.0081278 | -0.0030925 | 0.054769 | 0.062652 | -0.0011597 | 0.091044 | 0.1831 | 4.3167 | -0.2655 | -118.396 | -1.9913 | -3.4195 | 0.036621 | -45.5612 | 4.3396 | -118.6798 | 118.0389 | 0.01831 | 118.4875 | -0.091553 | 0.28381 | -6.2897 | -6.3309 | -0.37537 | 0.041199 | 0.44861
1729.5781 | 122.699 | -118.4326 | 4.1977 | -0.0054494 | 0.0066326 | -0.0018107 | 0.052205 | 0.064361 | 0.0003357 | 0.09254 | 0.1236 | 4.2343 | -0.28381 | -118.515 | -2.0828 | -3.4836 | 0.10986 | -45.6116 | 4.2572 | -118.7805 | 118.1488 | 0.036621 | 118.5562 | -0.082398 | 0.2655 | -6.2805 | -6.34 | -0.3479 | 0.059509 | 0.40741
1730.5781 | 122.7081 | -118.4326 | 4.1702 | 0.025068 | 0.0079142 | 0.0033161 | 0.052633 | 0.065216 | 0.0001221 | 0.091685 | 0.16022 | 4.1565 | -0.28381 | -118.5287 | -2.0279 | -3.4515 | 0.068665 | -45.5429 | 4.2206 | -118.8126 | 118.1488 | -0.013733 | 118.5928 | -0.096131 | 0.28381 | -6.1981 | -6.2485 | -0.37994 | 0.050354 | 0.44403
1731.5781 | 122.7264 | -118.4647 | 4.1473 | 0.040327 | 0.0070598 | 0.0043843 | 0.052846 | 0.066711 | -0.0009461 | 0.091899 | 0.13275 | 4.1382 | -0.30212 | -118.5654 | -2.0599 | -3.479 | 0.082397 | -45.5429 | 4.1931 | -118.8309 | 118.1625 | -0.009155 | 118.5974 | -0.10071 | 0.2655 | -6.2073 | -6.2531 | -0.36621 | 0.045776 | 0.43488
1732.5781 | 122.7219 | -118.4692 | 4.1519 | 0.055586 | 0.0064188 | 0.0013935 | 0.053487 | 0.063293 | 0.0014039 | 0.091899 | 0.17853 | 4.129 | -0.27924 | -118.5608 | -2.0142 | -3.447 | 0.045776 | -45.5429 | 4.2023 | -118.8354 | 118.19 | -0.022889 | 118.6478 | -0.091553 | 0.27466 | -6.1661 | -6.2164 | -0.36621 | 0.050354 | 0.45776
1733.5781 | 122.7356 | -118.4647 | 4.1473 | 0.040327 | 0.0087688 | 0.0028889 | 0.051351 | 0.064789 | 0.0001221 | 0.09019 | 0.16479 | 4.129 | -0.29755 | -118.5745 | -2.0416 | -3.447 | 0.07782 | -45.488 | 4.1473 | -118.8492 | 118.1671 | -0.018311 | 118.6295 | -0.10986 | 0.27466 | -6.189 | -6.189 | -0.38452 | 0 | 0.46234
1734.5781 | 122.7219 | -118.4921 | 4.1336 | -0.013079 | 0.0068462 | -0.00010166 | 0.050924 | 0.063507 | -0.0007325 | 0.091044 | 0.1236 | 4.1428 | -0.27924 | -118.5883 | -2.0508 | -3.4607 | 0.07782 | -45.4788 | 4.184 | -118.8538 | 118.2129 | 0.009155 | 118.6157 | -0.096131 | 0.2655 | -6.1844 | -6.2347 | -0.36163 | 0.050354 | 0.40283
1735.5781 | 122.7219 | -118.4921 | 4.1199 | -0.013079 | 0.0081278 | -0.00074266 | 0.050924 | 0.062652 | -0.0032959 | 0.092967 | 0.13275 | 4.1702 | -0.28839 | -118.5837 | -2.0462 | -3.479 | 0.11902 | -45.4193 | 4.1977 | -118.8354 | 118.2037 | 0.050354 | 118.6249 | -0.091553 | 0.25177 | -6.1661 | -6.2439 | -0.34332 | 0.07782 | 0.42114
1736.5781 | 122.6669 | -118.4967 | 4.1382 | -0.043596 | 0.0062052 | -0.00031526 | 0.047933 | 0.061157 | 0.0007629 | 0.091471 | 0.10071 | 4.1153 | -0.28381 | -118.6203 | -2.0554 | -3.4653 | 0.14191 | -45.4285 | 4.1794 | -118.8538 | 118.2129 | -0.022889 | 118.5974 | -0.1236 | 0.23346 | -6.1935 | -6.2347 | -0.35706 | 0.041198 | 0.38452
1737.5781 | 122.6761 | -118.4967 | 4.1107 | -0.051226 | 0.005778 | 0.00011194 | 0.052419 | 0.062652 | 0.0014039 | 0.090617 | 0.15106 | 4.1519 | -0.25635 | -118.6432 | -2.1057 | -3.4836 | 0.10986 | -45.4559 | 4.184 | -118.8492 | 118.2404 | 0.041199 | 118.6478 | -0.14648 | 0.20599 | -6.2164 | -6.2897 | -0.35248 | 0.073242 | 0.40741
1738.5781 | 122.6578 | -118.4647 | 4.1748 | -0.066485 | 0.0053508 | -0.0015971 | 0.048146 | 0.061584 | 0.0011901 | 0.091685 | 0.10071 | 4.1245 | -0.29297 | -118.6478 | -2.0737 | -3.4698 | 0.13733 | -45.3369 | 4.1885 | -118.7943 | 118.1717 | -0.050354 | 118.5654 | -0.1831 | 0.14648 | -6.2485 | -6.2622 | -0.32959 | 0.013733 | 0.39368
1739.5781 | 122.7173 | -118.5059 | 4.0924 | -0.043596 | 0.0066326 | 0.0026753 | 0.05306 | 0.06308 | 0.0011901 | 0.090831 | 0.15564 | 4.1153 | -0.28839 | -118.5928 | -2.0325 | -3.4332 | 0.059509 | -45.3873 | 4.1565 | -118.8675 | 118.2175 | 0.022888 | 118.6615 | -0.086975 | 0.27466 | -6.1249 | -6.189 | -0.36163 | 0.064087 | 0.44403
1740.5781 | 122.6898 | -118.4921 | 4.1611 | -0.058855 | 0.0070598 | -0.0020243 | 0.047506 | 0.064361 | 0.0039673 | 0.089976 | 0.10529 | 4.097 | -0.29297 | -118.5928 | -2.0233 | -3.4287 | 0.07782 | -45.4102 | 4.2068 | -118.8263 | 118.1992 | -0.064087 | 118.5974 | -0.10071 | 0.23346 | -6.1844 | -6.2302 | -0.33417 | 0.045776 | 0.39825
1741.5781 | 122.7264 | -118.4875 | 4.1199 | 0.070845 | 0.0068462 | 0.0043843 | 0.052846 | 0.064148 | 0.0007629 | 0.090403 | 0.16479 | 4.097 | -0.28839 | -118.5562 | -1.9821 | -3.3783 | 0.050354 | -45.3232 | 4.1519 | -118.8446 | 118.1992 | -0.022888 | 118.6523 | -0.068664 | 0.28839 | -6.102 | -6.134 | -0.35706 | 0.032044 | 0.45319
1742.5781 | 122.6761 | -118.5104 | 4.1199 | -0.013079 | 0.0044962 | -0.0018107 | 0.049428 | 0.063934 | 0.0001221 | 0.092326 | 0.082397 | 4.0787 | -0.29297 | -118.6249 | -2.0233 | -3.4195 | 0.12817 | -45.3506 | 4.1656 | -118.8629 | 118.2175 | -0.041199 | 118.5928 | -0.11444 | 0.23804 | -6.1432 | -6.189 | -0.35248 | 0.045776 | 0.37537
1743.5781 | 122.7722 | -118.4875 | 4.0787 | 0.0021796 | 0.003001 | -0.0018107 | 0.047078 | 0.06308 | -9.1495e-05 | 0.090617 | 0.1831 | 4.0695 | -0.24719 | -118.5471 | -1.9409 | -3.3051 | 0.009155 | -45.2179 | 4.1336 | -118.7759 | 118.2404 | -0.009155 | 118.6707 | -0.059509 | 0.22888 | -6.0196 | -6.0745 | -0.28839 | 0.054932 | 0.4303
1744.5781 | 122.6807 | -118.515 | 4.1107 | -0.074114 | 0.00471 | 0.0028889 | 0.049215 | 0.062225 | -9.1495e-05 | 0.092112 | 0.10071 | 4.0924 | -0.27924 | -118.6432 | -2.0096 | -3.4058 | 0.14191 | -45.3049 | 4.1794 | -118.8721 | 118.2358 | -0.018311 | 118.6157 | -0.12817 | 0.22888 | -6.1203 | -6.189 | -0.35705 | 0.068664 | 0.37994
1745.5781 | 122.7539 | -118.483 | 4.1016 | -0.0054494 | 0.0034282 | -0.0028789 | 0.048787 | 0.062652 | 0.0003357 | 0.090403 | 0.1831 | 4.0558 | -0.23804 | -118.5608 | -1.8723 | -3.2822 | 0.018311 | -45.2454 | 4.1245 | -118.8126 | 118.2449 | -0.045776 | 118.6661 | -0.07782 | 0.25177 | -5.9738 | -5.9967 | -0.32959 | 0.022889 | 0.42114
1746.5781 | 122.6624 | -118.5059 | 4.1199 | -0.058855 | 0.0038554 | 0.0013935 | 0.049642 | 0.061371 | -0.0018005 | 0.090617 | 0.14191 | 4.0741 | -0.26093 | -118.6066 | -1.8906 | -3.3325 | 0.09613 | -45.3415 | 4.1656 | -118.8354 | 118.2449 | -0.045776 | 118.6478 | -0.10071 | 0.22888 | -6.0104 | -6.0562 | -0.32959 | 0.045776 | 0.40283
1747.5781 | 122.6852 | -118.5196 | 4.1061 | -0.020708 | 0.0049236 | -0.0039469 | 0.049855 | 0.059875 | -0.0003051 | 0.091899 | 0.10986 | 4.0695 | -0.27466 | -118.6478 | -1.886 | -3.4149 | 0.11902 | -45.4147 | 4.1428 | -118.8904 | 118.2449 | -0.036621 | 118.6295 | -0.12817 | 0.24262 | -5.9921 | -6.0287 | -0.37079 | 0.036621 | 0.38452
1748.5781 | 122.7768 | -118.4875 | 4.0649 | 0.0021796 | 0.0042826 | -0.00031526 | 0.048574 | 0.061798 | 0.0016175 | 0.091471 | 0.19226 | 4.0329 | -0.27008 | -118.5837 | -1.7853 | -3.2959 | -0.004578 | -45.3415 | 4.1107 | -118.84 | 118.2175 | -0.032043 | 118.6798 | -0.09613 | 0.25635 | -5.8502 | -5.896 | -0.35248 | 0.045777 | 0.46234
1749.5781 | 122.8317 | -118.5013 | 4.0512 | 0.047956 | 0.0036418 | -0.0048015 | 0.047078 | 0.06073 | -9.1495e-05 | 0.089762 | 0.20142 | 3.9917 | -0.25177 | -118.5562 | -1.7715 | -3.273 | -0.091553 | -45.7947 | 4.0695 | -118.8354 | 118.2495 | -0.059509 | 118.7027 | -0.054931 | 0.27924 | -5.8228 | -5.8411 | -0.33417 | 0.018311 | 0.45319
1750.5781 | 122.8134 | -118.5013 | 4.0237 | 0.10899 | 0.0036418 | -0.00095626 | 0.048574 | 0.058594 | -0.0003051 | 0.091044 | 0.20142 | 4.0009 | -0.23804 | -118.5699 | -1.8631 | -3.3234 | -0.091553 | -45.7947 | 4.0512 | -118.8583 | 118.2632 | -0.022889 | 118.7027 | -0.068664 | 0.28839 | -5.8868 | -5.9143 | -0.35706 | 0.027465 | 0.43945
1751.5781 | 122.8043 | -118.4967 | 4.0054 | 0.017439 | 0.0017192 | -0.0043743 | 0.048146 | 0.058166 | -0.0015869 | 0.086344 | 0.21973 | 3.9825 | -0.22888 | -118.5471 | -1.8448 | -3.3188 | -0.073242 | -45.813 | 4.0421 | -118.8721 | 118.2678 | -0.022888 | 118.7164 | -0.050354 | 0.32501 | -5.8502 | -5.8868 | -0.37537 | 0.036621 | 0.44861
1752.5781 | 122.8134 | -118.4967 | 4.0329 | 0.1624 | 0.004069 | -0.0018107 | 0.047719 | 0.057953 | 0.0003357 | 0.089549 | 0.19226 | 3.9917 | -0.23346 | -118.5516 | -1.8494 | -3.2913 | -0.1236 | -45.7672 | 4.0695 | -118.84 | 118.2632 | -0.041199 | 118.689 | -0.054932 | 0.28839 | -5.8823 | -5.9189 | -0.34332 | 0.036621 | 0.42572
1753.5781 | 122.8043 | -118.5196 | 4.0421 | 0.017439 | 0.0017192 | -0.0020243 | 0.049215 | 0.057098 | 0.0007629 | 0.092112 | 0.19226 | 4.0054 | -0.25635 | -118.5425 | -1.8585 | -3.3096 | -0.059509 | -45.6207 | 4.0604 | -118.8263 | 118.2632 | -0.036621 | 118.7119 | -0.022888 | 0.28381 | -5.9006 | -5.9189 | -0.3067 | 0.018311 | 0.44861
1754.5781 | 122.8271 | -118.5104 | 4.0192 | 0.055586 | 0.0034282 | -0.0035197 | 0.047292 | 0.058594 | 0.0003357 | 0.090831 | 0.18768 | 3.9825 | -0.23804 | -118.5562 | -1.7395 | -3.2593 | -0.086975 | -45.4468 | 4.0512 | -118.8354 | 118.2724 | -0.036621 | 118.6981 | -0.045776 | 0.27924 | -5.7587 | -5.7907 | -0.32501 | 0.032043 | 0.42572
1755.5781 | 122.8271 | -118.4738 | 4.0009 | 0.10899 | 0.0025736 | -0.0062969 | 0.04836 | 0.059021 | -0.0005189 | 0.090403 | 0.20599 | 4.01 | -0.23346 | -118.5699 | -1.7349 | -3.2867 | -0.11902 | -45.4742 | 4.0604 | -118.8217 | 118.2404 | 0.009156 | 118.6798 | -0.09613 | 0.25177 | -5.7358 | -5.7953 | -0.3479 | 0.05951 | 0.43945
1756.5781 | 122.7951 | -118.4967 | 4.0649 | 0.12425 | 0.0062052 | -0.0018107 | 0.047719 | 0.059662 | 0.0005493 | 0.091258 | 0.17395 | 4.0329 | -0.23346 | -118.5516 | -1.767 | -3.2867 | -0.10529 | -45.1904 | 4.0833 | -118.8354 | 118.2632 | -0.032043 | 118.6707 | -0.054932 | 0.28381 | -5.8319 | -5.8502 | -0.33875 | 0.018311 | 0.40741
1757.5781 | 122.7997 | -118.5013 | 4.0649 | 0.18529 | 0.0038554 | -0.0011699 | 0.046865 | 0.059021 | 0.0018311 | 0.09019 | 0.14191 | 3.9917 | -0.23346 | -118.5791 | -1.7578 | -3.3051 | -0.10071 | -45.1813 | 4.0649 | -118.8492 | 118.2678 | -0.073242 | 118.6432 | -0.07782 | 0.27008 | -5.8228 | -5.8228 | -0.3479 | 0 | 0.37537
1758.5781 | 122.7997 | -118.5013 | 4.0421 | 0.2158 | 0.0042826 | -0.0013835 | 0.045156 | 0.05838 | 0.0016175 | 0.09019 | 0.13733 | 3.978 | -0.27924 | -118.5974 | -1.7899 | -3.3234 | -0.086975 | -45.3598 | 4.0741 | -118.8675 | 118.222 | -0.064087 | 118.6386 | -0.09613 | 0.27008 | -5.8319 | -5.864 | -0.36621 | 0.032044 | 0.41656
1759.5781 | 122.7402 | -118.5516 | 4.0283 | 0.22343 | 0.0066326 | -0.0030925 | 0.047719 | 0.059021 | 0.0022583 | 0.09254 | -0.064087 | 3.978 | -0.27466 | -118.6295 | -1.7944 | -3.3417 | -0.09613 | -45.2499 | 4.0375 | -118.8675 | 118.277 | -0.050354 | 118.4875 | -0.07782 | 0.23804 | -5.8228 | -5.8319 | -0.31586 | 0.009156 | 0.21057
1760.5781 | 122.7951 | -118.5059 | 4.0421 | 0.17003 | 0.0055644 | 0.00075274 | 0.047292 | 0.059662 | 0.0014039 | 0.089976 | 0.13733 | 3.9963 | -0.23804 | -118.5928 | -1.918 | -3.3325 | -0.091553 | -45.4147 | 4.0649 | -118.8538 | 118.2678 | -0.045776 | 118.6432 | -0.086975 | 0.26093 | -5.9601 | -5.983 | -0.3479 | 0.022888 | 0.37537
1761.5781 | 122.7905 | -118.5287 | 4.0054 | 0.10136 | 0.0032146 | -0.0043743 | 0.048146 | 0.056671 | 0.0014039 | 0.090831 | 0.18768 | 3.9917 | -0.22888 | -118.5837 | -1.8906 | -3.3234 | -0.11902 | -45.3873 | 4.0237 | -118.8354 | 118.2999 | -0.013733 | 118.7164 | -0.054931 | 0.25177 | -5.896 | -5.9143 | -0.3067 | 0.018311 | 0.41656
1762.5781 | 122.7585 | -118.5516 | 4.0192 | 0.31499 | 0.0055644 | -0.0020243 | 0.047292 | 0.058807 | -0.0003051 | 0.090403 | 0.10529 | 3.9276 | -0.29297 | -118.6295 | -1.9363 | -3.3554 | -0.091553 | -45.3644 | 4.0375 | -118.8675 | 118.2587 | -0.091553 | 118.6569 | -0.07782 | 0.23804 | -5.9555 | -5.9738 | -0.31586 | 0.018311 | 0.39825
1763.5781 | 122.8271 | -118.5104 | 4.0237 | 0.10899 | 0.0049236 | -0.0054423 | 0.048787 | 0.059448 | -0.0007325 | 0.090617 | 0.20142 | 3.9734 | -0.23804 | -118.5562 | -1.7258 | -3.2501 | -0.11902 | -45.2774 | 4.0237 | -118.8446 | 118.2724 | -0.050354 | 118.7119 | -0.045776 | 0.28839 | -5.7495 | -5.7495 | -0.33417 | 0 | 0.43945
1764.5781 | 122.7951 | -118.6386 | 3.9688 | 0.20054 | 0.004069 | -0.00095626 | 0.045797 | 0.058594 | 0.0035401 | 0.088267 | 0.15106 | 3.9597 | -0.22888 | -118.6386 | -1.767 | -3.2959 | -0.086975 | -45.2774 | 4.0283 | -118.9041 | 118.4097 | -0.009155 | 118.7897 | 0 | 0.2655 | -5.7358 | -5.7953 | -0.2655 | 0.059509 | 0.37994
1765.5781 | 122.7814 | -118.5287 | 4.0054 | 0.15477 | 0.0044962 | -0.0048015 | 0.047719 | 0.058807 | 0.0005493 | 0.089335 | 0.1236 | 3.9505 | -0.28839 | -118.6157 | -1.7761 | -3.2822 | -0.082397 | -45.2042 | 4.0329 | -118.8675 | 118.2404 | -0.054932 | 118.6523 | -0.086975 | 0.25177 | -5.7816 | -5.809 | -0.33875 | 0.027466 | 0.41199
1766.5781 | 122.7631 | -118.5745 | 4.0054 | 0.31499 | 0.0025736 | -0.0011699 | 0.049428 | 0.05838 | 0.0003357 | 0.091044 | 0.13733 | 3.9734 | -0.24719 | -118.6615 | -1.7853 | -3.2867 | -0.11902 | -45.2637 | 3.9963 | -118.8904 | 118.3273 | -0.032043 | 118.7119 | -0.086975 | 0.22888 | -5.7907 | -5.7816 | -0.31586 | -0.009155 | 0.38452
1767.5781 | 122.7219 | -118.6569 | 3.9093 | 0.22343 | 0.0027874 | 0.0018209 | 0.047933 | 0.058166 | -9.1495e-05 | 0.088694 | 0.12817 | 3.9551 | -0.25177 | -118.6523 | -1.8265 | -3.3051 | -0.09613 | -45.3827 | 3.9825 | -119.0048 | 118.4052 | 0.045776 | 118.7851 | 0.004577 | 0.35248 | -5.7358 | -5.809 | -0.3479 | 0.073242 | 0.37994
1768.5781 | 122.7768 | -118.5745 | 3.978 | 0.25395 | 0.0032146 | -0.0035197 | 0.048787 | 0.057953 | -0.0011597 | 0.089549 | 0.12817 | 3.9551 | -0.24719 | -118.6661 | -1.8539 | -3.3279 | -0.10071 | -45.1721 | 3.9917 | -118.8858 | 118.3273 | -0.022888 | 118.7027 | -0.091553 | 0.21973 | -5.8319 | -5.8456 | -0.31128 | 0.013733 | 0.37537
1769.5781 | 122.7585 | -118.5837 | 3.9551 | 0.25395 | 0.0034282 | -0.0013835 | 0.049428 | 0.057098 | 0.0009765 | 0.088908 | 0.14648 | 3.9139 | -0.24719 | -118.6935 | -1.8127 | -3.3005 | -0.11902 | -45.2408 | 3.9917 | -118.8904 | 118.3365 | -0.041199 | 118.7302 | -0.10986 | 0.19684 | -5.7678 | -5.8044 | -0.3067 | 0.036621 | 0.39368
1770.5781 | 122.7585 | -118.5974 | 3.9505 | 0.33024 | 0.00471 | 0.0022481 | 0.05071 | 0.060944 | 0.0026855 | 0.089976 | 0.20142 | 3.9276 | -0.25177 | -118.6569 | -1.8036 | -3.2684 | -0.17853 | -45.2042 | 3.9642 | -118.9087 | 118.3456 | -0.022888 | 118.7988 | -0.059509 | 0.25177 | -5.7541 | -5.7678 | -0.31128 | 0.013733 | 0.45319
1771.5781 | 122.7768 | -118.6157 | 3.9505 | 0.27684 | 0.0042826 | 0.0011799 | 0.053914 | 0.059662 | 0.0022583 | 0.089335 | 0.19226 | 3.8818 | -0.25177 | -118.6569 | -1.7853 | -3.2364 | -0.19684 | -45.195 | 3.9597 | -118.9178 | 118.364 | -0.068664 | 118.808 | -0.041198 | 0.26093 | -5.7358 | -5.7449 | -0.30212 | 0.009156 | 0.44403
1772.5781 | 122.7448 | -118.5745 | 3.9413 | 0.38365 | 0.003001 | 0.0033161 | 0.048146 | 0.060516 | 0.0022583 | 0.091685 | 0.1831 | 3.9139 | -0.22888 | -118.6752 | -1.8402 | -3.2593 | -0.15106 | -45.2362 | 3.9734 | -118.9087 | 118.3456 | -0.027466 | 118.7576 | -0.10071 | 0.23346 | -5.7816 | -5.8136 | -0.33417 | 0.032044 | 0.41199
1773.5781 | 122.7585 | -118.5745 | 3.9825 | 0.26921 | 0.0053508 | 0.0013935 | 0.047719 | 0.057312 | 0.0018311 | 0.090831 | 0.13275 | 3.9276 | -0.23804 | -118.6935 | -1.8677 | -3.2593 | -0.10071 | -45.2042 | 3.9825 | -118.8858 | 118.3365 | -0.054932 | 118.7073 | -0.11902 | 0.19226 | -5.8502 | -5.8502 | -0.31128 | 0 | 0.37079
1774.5781 | 122.8363 | -118.602 | 3.9322 | 0.063215 | 0.0034282 | -0.0013835 | 0.045797 | 0.05603 | 0.0014039 | 0.089762 | 0.21057 | 3.9139 | -0.23346 | -118.6249 | -1.7578 | -3.1998 | -0.11902 | -45.1263 | 3.9551 | -118.9041 | 118.3685 | -0.018311 | 118.8126 | -0.022888 | 0.27924 | -5.69 | -5.7129 | -0.30212 | 0.022888 | 0.44403
1775.5781 | 122.7676 | -118.602 | 3.9413 | 0.36839 | 0.0059916 | -0.0018107 | 0.046865 | 0.060516 | 0.0005493 | 0.091471 | 0.16479 | 3.9413 | -0.25177 | -118.6844 | -1.8036 | -3.2455 | -0.13733 | -45.2408 | 3.9597 | -118.9316 | 118.3502 | 0 | 118.7668 | -0.082397 | 0.24719 | -5.7449 | -5.7632 | -0.32959 | 0.018311 | 0.41656
1776.5781 | 122.7402 | -118.6157 | 3.9505 | 0.41417 | 0.0068462 | 0.0024617 | 0.047933 | 0.060089 | 0.0005493 | 0.089976 | 0.1831 | 3.9093 | -0.23346 | -118.6844 | -1.8082 | -3.241 | -0.15564 | -45.2591 | 3.9734 | -118.9224 | 118.3823 | -0.041198 | 118.7988 | -0.068664 | 0.23804 | -5.7587 | -5.7816 | -0.3067 | 0.022889 | 0.41656
1777.5781 | 122.7493 | -118.5928 | 3.9597 | 0.37602 | 0.0034282 | -0.0024517 | 0.047506 | 0.059875 | 0.0003357 | 0.090403 | 0.18768 | 3.9001 | -0.23804 | -118.6844 | -1.7715 | -3.2135 | -0.17395 | -45.401 | 3.9734 | -118.8995 | 118.3548 | -0.05951 | 118.7805 | -0.091553 | 0.21515 | -5.7312 | -5.7449 | -0.3067 | 0.013733 | 0.42572
1778.5781 | 122.7814 | -118.6432 | 3.891 | 0.45994 | 0.0064188 | 0.00053914 | 0.051992 | 0.061584 | -0.0007325 | 0.089335 | 0.21057 | 3.9047 | -0.22888 | -118.6523 | -1.7349 | -3.2776 | -0.54474 | -45.3644 | 3.8864 | -118.9728 | 118.4143 | 0.013733 | 118.8538 | -0.009156 | 0.32043 | -5.6259 | -5.6213 | -0.32959 | -0.004577 | 0.43945
1779.5781 | 122.7768 | -118.5745 | 3.9551 | 0.27684 | 0.004069 | 0.0035299 | 0.051778 | 0.061798 | 0.0011901 | 0.089762 | 0.19226 | 3.9001 | -0.23804 | -118.6432 | -1.7212 | -3.1906 | -0.18768 | -45.4239 | 3.978 | -118.9178 | 118.3365 | -0.054932 | 118.7668 | -0.068664 | 0.27466 | -5.6763 | -5.6992 | -0.34332 | 0.022888 | 0.4303
1780.5781 | 122.7722 | -118.602 | 3.9688 | 0.35313 | 0.0077006 | 0.00032554 | 0.049215 | 0.062012 | 0.0014039 | 0.092753 | 0.1831 | 3.9459 | -0.23804 | -118.6661 | -1.767 | -3.1906 | -0.16479 | -45.3918 | 3.9917 | -118.9133 | 118.364 | -0.022888 | 118.7851 | -0.064087 | 0.24719 | -5.7358 | -5.7587 | -0.31128 | 0.022888 | 0.42114
1781.5781 | 122.7814 | -118.5791 | 3.9505 | 0.35313 | 0.0051372 | -0.0024517 | 0.048787 | 0.059021 | -0.0011597 | 0.090617 | 0.1831 | 3.923 | -0.23804 | -118.6798 | -1.7303 | -3.1586 | -0.16022 | -45.369 | 3.9688 | -118.9224 | 118.3411 | -0.027465 | 118.7622 | -0.10071 | 0.24261 | -5.6808 | -5.6992 | -0.34332 | 0.018311 | 0.42114
1782.5781 | 122.7814 | -118.634 | 3.9047 | 0.26921 | 0.00471 | -0.0028789 | 0.047719 | 0.059235 | 0.0018311 | 0.091044 | 0.13275 | 3.9368 | -0.23804 | -118.6935 | -1.7624 | -3.3646 | -0.12817 | -45.4651 | 3.9368 | -119.0094 | 118.396 | 0.032044 | 118.7668 | -0.059509 | 0.31586 | -5.6671 | -5.6992 | -0.37537 | 0.032044 | 0.37079
1783.5781 | 122.7539 | -118.5654 | 3.9963 | 0.37602 | 0.0066326 | -0.0018107 | 0.048787 | 0.060089 | 0.0001221 | 0.089976 | 0.17853 | 3.9642 | -0.21973 | -118.6569 | -1.7212 | -3.1586 | -0.13275 | -45.3186 | 4.0009 | -118.8812 | 118.3456 | -0.032044 | 118.7439 | -0.091552 | 0.22431 | -5.7175 | -5.722 | -0.31586 | 0.004577 | 0.39826
1784.5781 | 122.7997 | -118.5562 | 3.9505 | 0.42943 | 0.005778 | 0.00096634 | 0.053487 | 0.059021 | -0.0003051 | 0.088908 | 0.20599 | 3.9322 | -0.23346 | -118.6432 | -1.7258 | -3.1219 | -0.15106 | -45.3873 | 3.978 | -118.9087 | 118.3228 | -0.01831 | 118.7622 | -0.086975 | 0.2655 | -5.6763 | -5.7037 | -0.35248 | 0.027466 | 0.43945
1785.5781 | 122.7768 | -118.5471 | 3.9963 | 0.3455 | 0.0042826 | 0.0028889 | 0.049642 | 0.059235 | -9.1495e-05 | 0.091258 | 0.17853 | 3.9505 | -0.24719 | -118.6432 | -1.7258 | -3.1448 | -0.1831 | -45.4834 | 3.9917 | -118.9178 | 118.2999 | -0.045777 | 118.7256 | -0.09613 | 0.27466 | -5.722 | -5.7175 | -0.37079 | -0.004578 | 0.42572
1786.5781 | 122.7951 | -118.5516 | 3.9551 | 0.44468 | 0.0062052 | 0.00011194 | 0.05071 | 0.059875 | 0.0028991 | 0.091685 | 0.21973 | 3.923 | -0.24261 | -118.6157 | -1.6983 | -3.1265 | -0.2243 | -45.401 | 3.9597 | -118.9133 | 118.309 | -0.032043 | 118.7714 | -0.064087 | 0.29755 | -5.6534 | -5.658 | -0.36163 | 0.004578 | 0.46234
1787.5781 | 122.7951 | -118.6432 | 3.9001 | -0.53188 | 0.0066326 | -0.00031526 | 0.049855 | 0.058807 | 0.0003357 | 0.090831 | 0.16479 | 3.8773 | -0.27008 | -118.6981 | -2.71 | -3.4424 | -0.19684 | -45.5109 | 3.9368 | -118.9682 | 118.3731 | -0.022888 | 118.808 | -0.054932 | 0.27008 | -6.6101 | -6.6467 | -0.32501 | 0.036622 | 0.43488
1788.5781 | 122.7905 | -118.6111 | 3.9093 | 0.4218 | 0.003001 | 0.00096634 | 0.056905 | 0.060944 | -0.0003051 | 0.090403 | 0.20599 | 3.8681 | -0.2243 | -118.689 | -2.3346 | -3.3508 | -0.17395 | -45.5475 | 3.9093 | -118.9728 | 118.3868 | -0.041199 | 118.8171 | -0.07782 | 0.28381 | -6.2439 | -6.2439 | -0.36163 | 0 | 0.4303
1789.5781 | 122.7722 | -118.6111 | 3.9413 | 0.33024 | 0.0038554 | 0.00053914 | 0.051137 | 0.061157 | 0.0003357 | 0.090403 | 0.18768 | 3.8818 | -0.24719 | -118.689 | -2.243 | -3.3096 | -0.17395 | -45.5704 | 3.9505 | -118.9224 | 118.364 | -0.059509 | 118.7988 | -0.07782 | 0.23346 | -6.1844 | -6.1935 | -0.31128 | 0.009155 | 0.43488
1790.5781 | 122.7631 | -118.6157 | 3.923 | 0.26921 | 0.0070598 | 0.0039571 | 0.053914 | 0.060089 | -0.0005189 | 0.089335 | 0.18768 | 3.8818 | -0.25177 | -118.6661 | -2.2568 | -3.2913 | -0.19684 | -45.6207 | 3.9551 | -118.9499 | 118.364 | -0.041199 | 118.8034 | -0.050354 | 0.28381 | -6.1798 | -6.2119 | -0.33417 | 0.032043 | 0.43945
1791.5781 | 122.7264 | -118.6523 | 3.9322 | 0.39891 | 0.009196 | 0.0022481 | 0.054128 | 0.061371 | 0.0020447 | 0.090617 | 0.13275 | 3.9322 | -0.28381 | -118.7439 | -2.298 | -3.3646 | -0.11444 | -45.7123 | 3.9642 | -118.9911 | 118.3685 | 0 | 118.7851 | -0.091552 | 0.24719 | -6.2302 | -6.2622 | -0.33875 | 0.032043 | 0.41656
1792.5781 | 122.7036 | -118.6478 | 3.923 | 0.36839 | 0.0085552 | 0.0031025 | 0.053487 | 0.061157 | 0.0009765 | 0.089976 | 0.11902 | 3.9551 | -0.29297 | -118.7714 | -2.2797 | -3.3737 | -0.073242 | -45.7993 | 3.9642 | -119.0048 | 118.3548 | 0.032043 | 118.7668 | -0.1236 | 0.23346 | -6.2027 | -6.2439 | -0.35706 | 0.041198 | 0.41199
1793.5781 | 122.7905 | -118.6478 | 3.9047 | 0.4218 | 0.0044962 | 0.0028889 | 0.051351 | 0.06073 | 0.0009765 | 0.088053 | 0.14648 | 3.9093 | -0.28839 | -118.7302 | -2.1881 | -3.3005 | -0.15106 | -45.7352 | 3.9322 | -118.9865 | 118.3594 | 0.004578 | 118.7943 | -0.082398 | 0.25635 | -6.0928 | -6.1203 | -0.33874 | 0.027466 | 0.43488
1794.5781 | 122.7997 | -118.602 | 3.8956 | 0.35313 | 0.0064188 | -0.0022381 | 0.051351 | 0.062652 | 0.0001221 | 0.089549 | 0.20599 | 3.9001 | -0.23346 | -118.7073 | -2.1973 | -3.2593 | -0.20142 | -45.6528 | 3.9322 | -118.9774 | 118.3685 | 0.004577 | 118.808 | -0.10528 | 0.27008 | -6.0928 | -6.1295 | -0.37537 | 0.036621 | 0.43945
1795.5781 | 122.7997 | -118.634 | 3.9276 | 0.40654 | 0.0070598 | 0.0026753 | 0.051137 | 0.062652 | -0.0011597 | 0.091471 | 0.17853 | 3.9093 | -0.24261 | -118.6707 | -2.1561 | -3.2501 | -0.17853 | -45.7397 | 3.923 | -118.9819 | 118.3914 | -0.01831 | 118.8126 | -0.036621 | 0.31128 | -6.0837 | -6.0791 | -0.3479 | -0.004577 | 0.42114
1796.5781 | 122.7814 | -118.634 | 3.9322 | 0.4218 | 0.0062052 | -0.0011699 | 0.053273 | 0.063293 | 0.0016175 | 0.090617 | 0.16937 | 3.9185 | -0.26093 | -118.7027 | -2.1698 | -3.273 | -0.16479 | -45.7581 | 3.9459 | -119.0048 | 118.3731 | -0.013733 | 118.8034 | -0.068665 | 0.30212 | -6.102 | -6.1157 | -0.37079 | 0.013733 | 0.4303
1797.5781 | 122.7631 | -118.6432 | 3.9047 | 0.45994 | 0.0051372 | 0.0022481 | 0.05306 | 0.062439 | -0.0003051 | 0.090403 | 0.14191 | 3.9047 | -0.28381 | -118.7439 | -2.1744 | -3.2776 | -0.15564 | -45.8862 | 3.9093 | -119.014 | 118.3594 | 0 | 118.7851 | -0.10071 | 0.27008 | -6.0791 | -6.0837 | -0.37079 | 0.004578 | 0.42572
1798.5781 | 122.7585 | -118.6615 | 3.8956 | 0.41417 | 0.0070598 | 0.0039571 | 0.051351 | 0.063507 | -0.0013733 | 0.089549 | 0.11902 | 3.9093 | -0.27924 | -118.7851 | -2.2202 | -3.3096 | -0.10986 | -45.8496 | 3.9368 | -118.9957 | 118.3823 | 0.013733 | 118.7805 | -0.1236 | 0.21057 | -6.1157 | -6.1569 | -0.33417 | 0.041199 | 0.39825
1799.5781 | 122.7036 | -118.6935 | 3.8956 | 0.30736 | 0.0081278 | 0.0011799 | 0.053487 | 0.061157 | 0.0020447 | 0.091258 | 0.11902 | 3.9001 | -0.2655 | -118.7943 | -2.2659 | -3.3463 | -0.07782 | -45.9778 | 3.9413 | -119.0414 | 118.428 | 0.004577 | 118.8126 | -0.10071 | 0.24719 | -6.1615 | -6.2073 | -0.3479 | 0.045776 | 0.38452
1800.5781 | 122.6944 | -118.6798 | 3.9093 | 0.23869 | 0.0087688 | -0.0011699 | 0.052846 | 0.064575 | 0.0007629 | 0.091044 | 0.11902 | 3.9368 | -0.27008 | -118.8171 | -2.2339 | -3.3279 | -0.054932 | -45.9274 | 3.9505 | -119.0231 | 118.4097 | 0.027466 | 118.7988 | -0.13733 | 0.20599 | -6.1432 | -6.1844 | -0.34332 | 0.041198 | 0.3891
1801.5781 | 122.7539 | -118.6569 | 3.9001 | 0.4218 | 0.0079142 | 0.00053914 | 0.054769 | 0.062652 | -9.1495e-05 | 0.089976 | 0.13733 | 3.9047 | -0.2655 | -118.7759 | -2.1881 | -3.2776 | -0.15564 | -45.9229 | 3.9185 | -119.0323 | 118.3914 | 0.004578 | 118.7942 | -0.11902 | 0.25635 | -6.0883 | -6.1066 | -0.37537 | 0.018311 | 0.40283
1802.5781 | 122.7402 | -118.6707 | 3.9276 | 0.39128 | 0.009196 | 0.0022481 | 0.052419 | 0.062652 | 0.0007629 | 0.093394 | 0.1236 | 3.9276 | -0.27466 | -118.7851 | -2.2339 | -3.2639 | -0.10986 | -45.8862 | 3.9642 | -119.014 | 118.396 | 0 | 118.7943 | -0.11444 | 0.22888 | -6.1615 | -6.1981 | -0.34332 | 0.036621 | 0.39825
1803.5781 | 122.6898 | -118.6798 | 3.9093 | 0.29973 | 0.0081278 | 0.00053914 | 0.051778 | 0.062225 | 0.0016175 | 0.091258 | 0.091553 | 3.9047 | -0.29297 | -118.8217 | -2.2522 | -3.3096 | -0.086975 | -45.9824 | 3.9413 | -119.0598 | 118.3868 | -0.004578 | 118.7714 | -0.14191 | 0.23804 | -6.1615 | -6.1935 | -0.37994 | 0.032043 | 0.38452
1804.5781 | 122.699 | -118.6752 | 3.9047 | 0.20817 | 0.0079142 | -0.00010166 | 0.051992 | 0.062866 | -0.0007325 | 0.092326 | 0.15564 | 3.923 | -0.2655 | -118.8126 | -2.2476 | -3.3188 | -0.036621 | -45.9869 | 3.9413 | -119.0552 | 118.4097 | 0.018311 | 118.8309 | -0.13733 | 0.24262 | -6.1523 | -6.189 | -0.37994 | 0.036621 | 0.42114
1805.5781 | 122.6578 | -118.6935 | 3.9139 | 0.23106 | 0.0081278 | 0.0037435 | 0.053487 | 0.061371 | 0.0018311 | 0.090403 | 0.10986 | 3.9368 | -0.27008 | -118.8583 | -2.2888 | -3.3325 | 0.032043 | -45.9778 | 3.9597 | -119.1055 | 118.4235 | 0.022889 | 118.8034 | -0.1648 | 0.24719 | -6.2027 | -6.2485 | -0.41199 | 0.045777 | 0.37994
1806.5781 | 122.7448 | -118.6798 | 3.923 | 0.4218 | 0.0081278 | 0.0045979 | 0.052205 | 0.063934 | -0.0013733 | 0.090617 | 0.10071 | 3.9276 | -0.27008 | -118.8492 | -2.2751 | -3.2272 | -0.28839 | -45.9686 | 3.9505 | -119.0414 | 118.4097 | 0.004577 | 118.7805 | -0.16937 | 0.19226 | -6.1981 | -6.2256 | -0.36163 | 0.027465 | 0.37079
1807.5781 | 122.6532 | -118.6798 | 3.9322 | 0.38365 | 0.0066326 | 0.0045979 | 0.053487 | 0.065643 | 0.0028991 | 0.09019 | 0.10071 | 3.9413 | -0.28381 | -118.8217 | -2.2568 | -3.3234 | -0.018311 | -45.932 | 3.9734 | -119.0414 | 118.396 | 0.009155 | 118.7805 | -0.14191 | 0.21973 | -6.189 | -6.2302 | -0.36163 | 0.041199 | 0.38452
1808.5781 | 122.7081 | -118.6661 | 3.9322 | 1.0016 | 0.0087688 | 0.0016073 | 0.050283 | 0.062866 | 0.0016175 | 0.091471 | 0.09613 | 3.9413 | -0.26093 | -118.8217 | -2.2293 | -3.2639 | -0.032043 | -45.9137 | 3.9597 | -119.0506 | 118.4052 | 0.009155 | 118.7622 | -0.15564 | 0.22888 | -6.1615 | -6.189 | -0.38452 | 0.027466 | 0.35706
1809.5781 | 122.818 | -118.6249 | 3.9093 | 0.39128 | 0.0066326 | 0.0048115 | 0.049855 | 0.064575 | 0.0005493 | 0.092326 | 0.20599 | 3.8956 | -0.23346 | -118.7347 | -2.1194 | -3.1403 | -0.20142 | -45.7169 | 3.9139 | -119.0186 | 118.3914 | -0.013733 | 118.8309 | -0.10986 | 0.28381 | -6.0287 | -6.0333 | -0.39368 | 0.004577 | 0.43945
1810.5781 | 122.6898 | -118.689 | 3.9505 | 0.39891 | 0.0064188 | 0.0058797 | 0.053914 | 0.065216 | 0.0033265 | 0.091044 | 0.10529 | 3.9505 | -0.27924 | -118.7988 | -2.3254 | -3.3783 | 0.22888 | -45.6665 | 3.9505 | -119.0552 | 118.4097 | 0 | 118.7943 | -0.10986 | 0.25635 | -6.2759 | -6.2759 | -0.36621 | 0 | 0.38452
1811.5781 | 122.5342 | -118.6935 | 3.9368 | 0.36076 | 0.005778 | 0.0028889 | 0.051778 | 0.061798 | 0.0003357 | 0.090617 | 0.11444 | 3.9322 | -0.27466 | -118.8263 | -2.211 | -3.2684 | -0.013733 | -45.8908 | 3.9597 | -119.0735 | 118.4189 | -0.004578 | 118.808 | -0.13275 | 0.24719 | -6.1478 | -6.1707 | -0.37994 | 0.022888 | 0.3891
1812.5781 | 122.6715 | -118.6752 | 3.9413 | 0.26158 | 0.0096232 | 0.0024617 | 0.05306 | 0.066498 | 0.0003357 | 0.093394 | 0.11902 | 3.9276 | -0.28381 | -118.8034 | -2.1973 | -3.2593 | 0.013733 | -45.8771 | 3.978 | -119.0369 | 118.3914 | -0.013733 | 118.7943 | -0.12817 | 0.23346 | -6.1386 | -6.1752 | -0.36163 | 0.036621 | 0.40283
1813.5781 | 122.6715 | -118.7119 | 3.9139 | 2.4817 | 0.007487 | 0.0045979 | 0.049855 | 0.063934 | 0.0033265 | 0.089762 | 0.19684 | 3.9322 | -0.27924 | -118.84 | -2.2202 | -3.2318 | -0.022888 | -45.8267 | 3.9597 | -119.0598 | 118.4326 | 0.018311 | 118.9087 | -0.12817 | 0.21973 | -6.134 | -6.1798 | -0.3479 | 0.045777 | 0.47607
1814.5781 | 122.8043 | -118.634 | 3.8773 | 0.44468 | 0.0098368 | 0.00011194 | 0.049428 | 0.064148 | 0.0007629 | 0.091258 | 0.19684 | 3.891 | -0.24719 | -118.7393 | -2.1194 | -3.1219 | -0.21057 | -45.6528 | 3.9139 | -119.0186 | 118.3868 | 0.013733 | 118.8309 | -0.10529 | 0.27924 | -5.9967 | -6.0333 | -0.38452 | 0.036621 | 0.44403
1815.5781 | 122.6212 | -118.6615 | 3.9276 | 0.33024 | 0.0087688 | 0.0026753 | 0.051351 | 0.062866 | 0.0011901 | 0.09254 | 0.10529 | 3.9322 | -0.28381 | -118.8354 | -2.2659 | -3.2364 | -0.013733 | -45.7672 | 3.9825 | -119.0918 | 118.3777 | 0.004578 | 118.7668 | -0.17395 | 0.25635 | -6.1935 | -6.2485 | -0.4303 | 0.054932 | 0.3891
1816.5781 | 122.6624 | -118.6935 | 3.9413 | 0.37602 | 0.0072734 | 0.0067341 | 0.054128 | 0.064575 | -0.0024415 | 0.091044 | 0.09613 | 3.9368 | -0.28381 | -118.8629 | -2.2202 | -3.241 | -0.009155 | -45.7993 | 3.978 | -119.0689 | 118.4097 | -0.004577 | 118.7897 | -0.16937 | 0.20599 | -6.1615 | -6.1981 | -0.37537 | 0.036621 | 0.37994
1817.5781 | 122.7722 | -118.6295 | 3.891 | 0.45231 | 0.0081278 | 0.0031025 | 0.050924 | 0.064148 | 0.0003357 | 0.089762 | 0.15106 | 3.9368 | -0.26093 | -118.7622 | -2.1378 | -3.1311 | -0.16022 | -45.4788 | 3.9597 | -119.0231 | 118.3685 | 0.045777 | 118.7805 | -0.13275 | 0.26093 | -6.0287 | -6.0974 | -0.39368 | 0.068665 | 0.41199
1818.5781 | 122.731 | -118.6523 | 3.9047 | 0.40654 | 0.0085552 | -0.0015971 | 0.050283 | 0.065857 | 0.0018311 | 0.089122 | 0.13733 | 3.923 | -0.28381 | -118.7851 | -2.1652 | -3.1677 | -0.10986 | -45.5933 | 3.9734 | -119.014 | 118.3685 | 0.018311 | 118.7897 | -0.13275 | 0.22888 | -6.0699 | -6.1386 | -0.36163 | 0.068665 | 0.42114
1819.5781 | 122.6624 | -118.6798 | 3.9276 | 0.26921 | 0.009196 | 0.00011194 | 0.054128 | 0.062439 | -0.0003051 | 0.091685 | 0.10986 | 3.9459 | -0.28839 | -118.8126 | -2.211 | -3.2227 | 0.045776 | -45.7123 | 3.978 | -119.0689 | 118.3914 | 0.018311 | 118.7897 | -0.13275 | 0.25635 | -6.1386 | -6.189 | -0.3891 | 0.050354 | 0.39825
1820.5781 | 122.6624 | -118.689 | 3.9459 | 0.24632 | 0.0089824 | 0.0052387 | 0.054982 | 0.063721 | -0.0007325 | 0.089335 | 0.12817 | 3.9276 | -0.28839 | -118.8171 | -2.2202 | -3.1998 | 0.036621 | -45.7077 | 3.9734 | -119.0598 | 118.4006 | -0.018311 | 118.8171 | -0.12817 | 0.24261 | -6.1661 | -6.1935 | -0.37079 | 0.027466 | 0.41657
1821.5781 | 122.6624 | -118.7164 | 3.9551 | 0.31499 | 0.0087688 | 0.0031025 | 0.052419 | 0.065216 | 0.0005493 | 0.089549 | 0.09613 | 3.9597 | -0.27924 | -118.8492 | -2.2064 | -3.1952 | -0.009155 | -45.7901 | 3.9963 | -119.0689 | 118.4372 | 0.004578 | 118.8126 | -0.13275 | 0.21973 | -6.1615 | -6.2027 | -0.35248 | 0.041199 | 0.37537
1822.5781 | 122.6852 | -118.6844 | 3.9413 | 0.40654 | 0.0070598 | 0.0037435 | 0.052846 | 0.064789 | 0.0009765 | 0.09019 | 0.050354 | 3.9688 | -0.26093 | -118.7759 | -2.1927 | -3.1998 | -0.032043 | -45.6894 | 4.0146 | -119.0506 | 118.4235 | 0.027466 | 118.7347 | -0.091553 | 0.27466 | -6.134 | -6.2073 | -0.36621 | 0.073242 | 0.31128
1823.5781 | 122.6944 | -118.6798 | 3.9597 | 0.36076 | 0.0098368 | 0.0013935 | 0.051137 | 0.06607 | 0.0011901 | 0.091044 | 0.10986 | 3.9642 | -0.27466 | -118.8812 | -2.3254 | -3.2547 | 0.20142 | -45.639 | 4.0009 | -119.0506 | 118.4052 | 0.004577 | 118.7897 | -0.20142 | 0.16937 | -6.2851 | -6.3263 | -0.37079 | 0.041198 | 0.38452
1824.5781 | 122.6761 | -118.689 | 3.9413 | 0.23106 | 0.0053508 | 0.0037435 | 0.052205 | 0.063721 | 0.0016175 | 0.089335 | 0.11444 | 3.923 | -0.28381 | -118.808 | -2.2247 | -3.1952 | 0.022888 | -45.6757 | 3.9917 | -119.0735 | 118.4052 | -0.01831 | 118.8034 | -0.11902 | 0.2655 | -6.1661 | -6.2164 | -0.38452 | 0.050354 | 0.39825
1825.5781 | 122.699 | -118.6523 | 3.9322 | -0.303 | 0.0077006 | 0.00096634 | 0.053273 | 0.063934 | 0.0014039 | 0.089549 | 0.20599 | 3.9917 | -0.20142 | -118.7668 | -2.1744 | -3.1265 | 0.013733 | -45.575 | 3.9917 | -119.046 | 118.4509 | 0.059509 | 118.8583 | -0.11444 | 0.27924 | -6.1066 | -6.1661 | -0.39368 | 0.059509 | 0.40741
1826.5781 | 122.7081 | -118.6386 | 3.9688 | 0.15477 | 0.0087688 | 0.0026753 | 0.054982 | 0.065643 | 0.0001221 | 0.090617 | 0.16937 | 3.978 | -0.28839 | -118.7485 | -2.1835 | -3.0991 | 0 | -45.5109 | 4.0329 | -119.0094 | 118.3502 | 0.009155 | 118.808 | -0.10986 | 0.26093 | -6.1523 | -6.2164 | -0.37079 | 0.064087 | 0.45776
1827.5781 | 122.6669 | -118.6661 | 3.9276 | 0.17766 | 0.0079142 | 0.0048115 | 0.052846 | 0.064789 | 0.0011901 | 0.089549 | 0.16479 | 3.9505 | -0.25635 | -118.7988 | -2.1927 | -3.1631 | 0.013733 | -45.5887 | 4.0009 | -119.0323 | 118.4097 | 0.022888 | 118.8309 | -0.13275 | 0.23346 | -6.1203 | -6.1935 | -0.36621 | 0.073242 | 0.42114
1828.5781 | 122.7036 | -118.6661 | 3.9505 | 0.17766 | 0.0070598 | 0.0050251 | 0.053487 | 0.065216 | 0.0001221 | 0.089549 | 0.16937 | 3.9551 | -0.26093 | -118.7531 | -2.1515 | -3.1128 | 0.018311 | -45.5704 | 4.0054 | -119.0277 | 118.4052 | 0.004578 | 118.8354 | -0.086975 | 0.27466 | -6.102 | -6.1569 | -0.36163 | 0.054932 | 0.4303
1829.5781 | 122.6669 | -118.689 | 3.9276 | 0.27684 | 0.0096232 | 0.0050251 | 0.05306 | 0.065643 | 0.0007629 | 0.091258 | 0.12817 | 3.9276 | -0.29297 | -118.8263 | -2.1698 | -3.1448 | 0.022888 | -45.5612 | 3.9597 | -119.0918 | 118.396 | 0 | 118.8171 | -0.13733 | 0.2655 | -6.0974 | -6.1295 | -0.40283 | 0.032044 | 0.42114
1830.5781 | 122.6578 | -118.6844 | 3.9322 | 0.19291 | 0.0077006 | 0.0018209 | 0.052419 | 0.06543 | 0.0005493 | 0.091258 | 0.13733 | 3.9551 | -0.27466 | -118.7988 | -2.1423 | -3.1082 | 0.013733 | -45.3918 | 4.0009 | -119.0552 | 118.4097 | 0.022888 | 118.8217 | -0.11444 | 0.25635 | -6.0745 | -6.1432 | -0.37079 | 0.068664 | 0.41199
1831.5781 | 122.699 | -118.6935 | 3.9551 | 0.39128 | 0.007487 | 0.0033161 | 0.055196 | 0.064148 | 0.0001221 | 0.091258 | 0.10071 | 3.9597 | -0.28839 | -118.8538 | -2.2202 | -3.1219 | 0.054932 | -45.5429 | 3.9963 | -119.0552 | 118.4052 | 0.004578 | 118.7942 | -0.16022 | 0.20142 | -6.1752 | -6.2164 | -0.36163 | 0.041199 | 0.3891
1832.5781 | 122.7219 | -118.6203 | 3.9459 | 0.15477 | 0.0072734 | 0.00053914 | 0.053273 | 0.063934 | 0.0003357 | 0.09019 | 0.18768 | 3.9825 | -0.27008 | -118.7393 | -2.1011 | -3.0396 | 0.013733 | -45.4514 | 4.01 | -119.0048 | 118.3502 | 0.036621 | 118.808 | -0.11902 | 0.2655 | -6.0471 | -6.1111 | -0.38452 | 0.064087 | 0.45776
1833.5781 | 122.7219 | -118.6203 | 3.9688 | 0.11662 | 0.0089824 | 0.0018209 | 0.052633 | 0.06543 | -0.0011597 | 0.090403 | 0.17395 | 4.01 | -0.27466 | -118.7119 | -2.0874 | -3.0258 | 0.022888 | -45.3781 | 4.0237 | -119.0002 | 118.3456 | 0.041199 | 118.7943 | -0.091553 | 0.28839 | -6.0562 | -6.1111 | -0.37994 | 0.054932 | 0.44861
1834.5781 | 122.7127 | -118.634 | 3.9322 | 0.46757 | 0.0068462 | 0.0031025 | 0.053487 | 0.065216 | 0.0001221 | 0.090831 | 0.21057 | 4.0009 | -0.20142 | -118.7439 | -2.1103 | -3.035 | 0.004578 | -45.4102 | 3.9963 | -119.0369 | 118.4326 | 0.068664 | 118.8446 | -0.10986 | 0.29297 | -6.0425 | -6.1066 | -0.40283 | 0.064087 | 0.41199
1835.5781 | 122.731 | -118.6478 | 3.9413 | 0.17766 | 0.0085552 | 0.0037435 | 0.05306 | 0.06543 | -0.0015869 | 0.090403 | 0.17395 | 3.9505 | -0.24261 | -118.7485 | -2.0645 | -2.98 | -0.018311 | -45.4193 | 4.0283 | -119.0231 | 118.4052 | 0.009155 | 118.8217 | -0.10071 | 0.27466 | -6.0059 | -6.0928 | -0.37537 | 0.086975 | 0.41656
1836.5781 | 122.6898 | -118.6935 | 3.9047 | 0.20054 | 0.0081278 | -0.00031526 | 0.051992 | 0.065216 | -0.0003051 | 0.092326 | 0.15106 | 3.9459 | -0.27924 | -118.808 | -2.1286 | -3.0762 | 0.009155 | -45.4742 | 3.9642 | -119.0826 | 118.4143 | 0.041199 | 118.8446 | -0.11444 | 0.27466 | -6.0333 | -6.0928 | -0.3891 | 0.059509 | 0.4303
1837.5781 | 122.7036 | -118.6569 | 3.9459 | 0.13188 | 0.0081278 | 0.0026753 | 0.054982 | 0.064575 | -0.0018005 | 0.088053 | 0.17853 | 3.9413 | -0.27008 | -118.7897 | -2.124 | -3.035 | 0.009155 | -45.3415 | 3.9871 | -119.0643 | 118.3868 | -0.004578 | 118.8354 | -0.13275 | 0.27466 | -6.0699 | -6.1111 | -0.40741 | 0.041199 | 0.44861
1838.5781 | 122.6898 | -118.6798 | 3.9459 | 0.093733 | 0.0062052 | 0.0022481 | 0.053487 | 0.067352 | 0.0007629 | 0.088908 | 0.16022 | 3.9825 | -0.24261 | -118.7668 | -1.9089 | -2.9709 | 0.009155 | -45.314 | 3.9871 | -119.0186 | 118.4372 | 0.036621 | 118.84 | -0.086975 | 0.25177 | -5.8548 | -5.896 | -0.33875 | 0.041199 | 0.40283
1839.5781 | 122.7219 | -118.6752 | 3.9642 | 0.25395 | 0.01005 | 0.0035299 | 0.053487 | 0.064361 | -0.0003051 | 0.089549 | 0.20142 | 4.01 | -0.21057 | -118.7485 | -2.0279 | -2.9984 | 0.013733 | -45.3094 | 3.9963 | -119.0369 | 118.4647 | 0.045777 | 118.8766 | -0.073242 | 0.28839 | -5.9921 | -6.0242 | -0.36163 | 0.032044 | 0.41199
1840.5781 | 122.7219 | -118.6615 | 3.9642 | 0.017439 | 0.0072734 | 0.0031025 | 0.054342 | 0.063507 | -0.0011597 | 0.088694 | 0.16937 | 3.9505 | -0.27924 | -118.7576 | -2.092 | -3.0121 | 0.045776 | -45.3186 | 3.978 | -119.0643 | 118.3823 | -0.013733 | 118.8309 | -0.09613 | 0.3067 | -6.0562 | -6.0699 | -0.40283 | 0.013733 | 0.44861
1841.5781 | 122.7264 | -118.6752 | 3.9642 | 0.14714 | 0.007487 | 0.0045979 | 0.052846 | 0.065643 | 0.0003357 | 0.090617 | 0.1831 | 3.9413 | -0.28839 | -118.7622 | -2.1011 | -2.9892 | 0.013733 | -45.2362 | 4.0421 | -119.0369 | 118.3868 | -0.022888 | 118.8583 | -0.086975 | 0.27466 | -6.0654 | -6.1432 | -0.36163 | 0.07782 | 0.4715
1842.5781 | 122.6944 | -118.6661 | 3.9322 | 0.1624 | 0.0042826 | 0.0028889 | 0.053487 | 0.064575 | -0.0005189 | 0.091471 | 0.14648 | 3.9459 | -0.27924 | -118.8034 | -2.1423 | -3.0304 | 0.009155 | -45.3186 | 4.0009 | -119.046 | 118.3868 | 0.013733 | 118.8126 | -0.13733 | 0.24262 | -6.0745 | -6.1432 | -0.37994 | 0.068664 | 0.42572
1843.5781 | 122.6807 | -118.6798 | 3.923 | 0.17003 | 0.0049236 | 0.0016073 | 0.055196 | 0.064575 | -0.0005189 | 0.090831 | 0.16479 | 3.9322 | -0.28381 | -118.8034 | -2.0691 | -3.0075 | -0.004578 | -45.282 | 3.9642 | -119.0552 | 118.396 | 0.009155 | 118.8446 | -0.1236 | 0.25177 | -5.9921 | -6.0333 | -0.37537 | 0.041198 | 0.44861
1844.5781 | 122.6898 | -118.6844 | 3.923 | 0.11662 | 0.0070598 | 0.0024617 | 0.054128 | 0.065002 | 0.0003357 | 0.089335 | 0.15106 | 3.9322 | -0.25635 | -118.7943 | -2.1378 | -3.0212 | 0.009155 | -45.2408 | 3.9642 | -119.0735 | 118.428 | 0.009155 | 118.8354 | -0.10986 | 0.27924 | -6.0608 | -6.102 | -0.3891 | 0.041198 | 0.40741
1845.5781 | 122.731 | -118.689 | 3.9139 | 0.37602 | 0.011332 | 0.0037435 | 0.05306 | 0.062866 | 0.0005493 | 0.092326 | 0.1236 | 3.9505 | -0.27924 | -118.8034 | -2.1194 | -2.9938 | -0.082397 | -45.2042 | 3.9597 | -119.0598 | 118.4097 | 0.036621 | 118.8126 | -0.11444 | 0.25635 | -6.0333 | -6.0791 | -0.37079 | 0.045777 | 0.40283
1846.5781 | 122.6349 | -118.634 | 3.9734 | 0.39891 | 0.0087688 | 0.0033161 | 0.052846 | 0.062866 | -0.0009461 | 0.09019 | 0.10529 | 3.9459 | -0.2655 | -118.721 | -2.179 | -3.0579 | 0.12817 | -44.87 | 4.0237 | -119.0369 | 118.3685 | -0.027466 | 118.7393 | -0.086975 | 0.31586 | -6.1523 | -6.2027 | -0.40283 | 0.050354 | 0.37079
1847.5781 | 122.7264 | -118.6432 | 3.9413 | 0.10136 | 0.0085552 | 0.0054525 | 0.053273 | 0.062439 | -0.0003051 | 0.088481 | 0.16022 | 3.9597 | -0.27008 | -118.7485 | -2.0782 | -2.9434 | 0.018311 | -45.1447 | 3.9963 | -119.0598 | 118.3731 | 0.018311 | 118.8034 | -0.10529 | 0.31128 | -6.0196 | -6.0745 | -0.41657 | 0.054932 | 0.4303
1848.5781 | 122.7036 | -118.6249 | 3.9413 | 0.1624 | 0.007487 | 0.0052387 | 0.053701 | 0.066498 | 0.0003357 | 0.091258 | 0.16937 | 3.9642 | -0.25177 | -118.7439 | -2.0325 | -2.9343 | 0.013733 | -45.0989 | 4.0054 | -119.046 | 118.3731 | 0.022888 | 118.7943 | -0.11902 | 0.30212 | -5.9738 | -6.0379 | -0.42114 | 0.064087 | 0.42114
1849.5781 | 122.6807 | -118.6249 | 3.9917 | 0.23106 | 0.01005 | 0.0043843 | 0.051992 | 0.062866 | -0.0013733 | 0.091258 | 0.13275 | 4.0054 | -0.3067 | -118.7576 | -1.6113 | -2.7832 | 0.027466 | -44.9844 | 4.0512 | -119.0048 | 118.3182 | 0.013733 | 118.7576 | -0.13275 | 0.24719 | -5.603 | -5.6625 | -0.37994 | 0.059509 | 0.43945
1850.5781 | 122.6486 | -118.6203 | 4.0009 | 0.24632 | 0.009196 | -0.0020243 | 0.054555 | 0.06543 | 0.0005493 | 0.090831 | 0.10529 | 3.978 | -0.27924 | -118.7805 | -1.5747 | -2.7924 | 0.032043 | -45.0806 | 4.0146 | -119.0231 | 118.3411 | -0.022888 | 118.7256 | -0.16022 | 0.24261 | -5.5756 | -5.5893 | -0.40283 | 0.013733 | 0.38452
1851.5781 | 122.6761 | -118.6249 | 3.9871 | 0.24632 | 0.0096232 | 0.0031025 | 0.053701 | 0.064361 | -0.0009461 | 0.089762 | 0.11444 | 3.9688 | -0.27008 | -118.7805 | -1.8082 | -2.8519 | 0.027466 | -45.0348 | 4.0237 | -119.0231 | 118.3548 | -0.018311 | 118.7393 | -0.15564 | 0.24261 | -5.7953 | -5.8319 | -0.39825 | 0.036621 | 0.38452
1852.5781 | 122.6715 | -118.6615 | 3.978 | 0.23106 | 0.0094096 | 0.0031025 | 0.051351 | 0.065216 | 0.0016175 | 0.090403 | 0.11444 | 3.9597 | -0.29297 | -118.8171 | -1.8631 | -2.8564 | 0.027466 | -45.0897 | 4.0375 | -119.046 | 118.3685 | -0.01831 | 118.7759 | -0.15564 | 0.22888 | -5.8411 | -5.9006 | -0.38452 | 0.05951 | 0.40741
1853.5781 | 122.6898 | -118.6569 | 3.9505 | 0.1624 | 0.0079142 | 0.0033161 | 0.055196 | 0.065216 | 0.0005493 | 0.091258 | 0.16022 | 3.9825 | -0.25177 | -118.7393 | -1.8402 | -2.8427 | 0.009155 | -44.9844 | 4.01 | -119.0506 | 118.4052 | 0.032044 | 118.8171 | -0.082398 | 0.31128 | -5.7907 | -5.8502 | -0.39368 | 0.05951 | 0.41199
1854.5781 | 122.699 | -118.6478 | 3.9551 | 0.13951 | 0.0083416 | 0.00011194 | 0.053487 | 0.063721 | 0.0001221 | 0.089976 | 0.16937 | 3.9597 | -0.2655 | -118.7622 | -1.8219 | -2.8198 | 0.013733 | -44.9432 | 4.0192 | -119.0231 | 118.3823 | 0.004578 | 118.8171 | -0.11444 | 0.26093 | -5.777 | -5.8411 | -0.37537 | 0.064087 | 0.43488
1855.5781 | 122.6715 | -118.6523 | 3.9917 | 0.25395 | 0.0066326 | 0.0041707 | 0.052846 | 0.06308 | -0.0003051 | 0.091685 | 0.11902 | 3.9825 | -0.27008 | -118.7805 | -1.8723 | -2.8519 | 0.032043 | -44.9478 | 4.0466 | -119.0552 | 118.3823 | -0.009155 | 118.7714 | -0.12817 | 0.27466 | -5.864 | -5.9189 | -0.40283 | 0.054932 | 0.3891
1856.5781 | 122.7127 | -118.6295 | 3.978 | 0.35313 | 0.0081278 | 0.0043843 | 0.054555 | 0.06607 | 0.0009765 | 0.094676 | 0.1236 | 3.9871 | -0.26093 | -118.8858 | -2.0142 | -2.8198 | 0.1831 | -44.9799 | 4.0466 | -119.0186 | 118.3685 | 0.009156 | 118.7531 | -0.25635 | 0.13275 | -5.9921 | -6.0608 | -0.3891 | 0.068665 | 0.38452
1857.5781 | 122.6944 | -118.689 | 3.9597 | 0.35313 | 0.0085552 | 0.0048115 | 0.059682 | 0.069061 | -0.0015869 | 0.089549 | 0.11902 | 3.9459 | -0.28839 | -118.6981 | -1.8219 | -2.8931 | 0.013733 | -44.838 | 4.0146 | -119.0414 | 118.4006 | -0.013733 | 118.808 | -0.009155 | 0.34332 | -5.7816 | -5.8365 | -0.35248 | 0.054931 | 0.40741
1858.5781 | 122.6715 | -118.6615 | 3.9459 | 0.36839 | 0.0077006 | 0.0016073 | 0.051137 | 0.061371 | -0.0011597 | 0.092112 | 0.11444 | 3.9368 | -0.27008 | -118.8629 | -1.9226 | -2.8107 | 0.013733 | -44.8792 | 3.9917 | -119.0643 | 118.3914 | -0.009155 | 118.7759 | -0.20142 | 0.20142 | -5.8685 | -5.9143 | -0.40283 | 0.045776 | 0.38452
1859.5781 | 122.699 | -118.6478 | 3.9505 | 0.36839 | 0.0083416 | 0.0067341 | 0.051137 | 0.063721 | 0.0009765 | 0.089335 | 0.086975 | 3.9505 | -0.2655 | -118.7622 | -1.8494 | -2.8473 | -0.018311 | -44.7784 | 4.0146 | -119.0552 | 118.3823 | 0 | 118.7347 | -0.11444 | 0.29297 | -5.7999 | -5.864 | -0.40741 | 0.064087 | 0.35248
1860.5781 | 122.6669 | -118.6615 | 3.9734 | 0.23106 | 0.0066326 | 0.0058797 | 0.052846 | 0.065002 | 0.0005493 | 0.091471 | 0.091553 | 3.9688 | -0.28381 | -118.808 | -1.8448 | -2.8381 | 0.032043 | -44.8013 | 4.0375 | -119.0231 | 118.3777 | -0.004578 | 118.7531 | -0.14648 | 0.21515 | -5.8182 | -5.8823 | -0.36163 | 0.064087 | 0.37537
1861.5781 | 122.6486 | -118.6386 | 3.9459 | 0.27684 | 0.0098368 | -0.00031526 | 0.054769 | 0.064361 | 0.0011901 | 0.089976 | 0.09613 | 3.9551 | -0.28839 | -118.808 | -1.8906 | -2.861 | 0.009155 | -44.8105 | 4.0009 | -119.0735 | 118.3502 | 0.009155 | 118.7347 | -0.16937 | 0.2655 | -5.8365 | -5.8914 | -0.43488 | 0.054931 | 0.38452
1862.5781 | 122.7768 | -118.6386 | 3.923 | 0.42943 | 0.0055644 | 0.0028889 | 0.053914 | 0.065643 | 0.0005493 | 0.089549 | 0.14191 | 3.9322 | -0.27008 | -118.7668 | -1.6617 | -2.6917 | -0.15106 | -44.6182 | 3.9597 | -119.014 | 118.3685 | 0.009155 | 118.7805 | -0.12817 | 0.24719 | -5.5847 | -5.6213 | -0.37537 | 0.036621 | 0.41199
1863.5781 | 122.7676 | -118.6249 | 3.9322 | 0.40654 | 0.0085552 | 0.0011799 | 0.050924 | 0.063721 | -0.0003051 | 0.090403 | 0.13733 | 3.9505 | -0.25635 | -118.7393 | -1.4786 | -2.6184 | -0.16022 | -44.6777 | 3.9871 | -119.0186 | 118.3685 | 0.01831 | 118.7622 | -0.11444 | 0.27924 | -5.4108 | -5.4657 | -0.39368 | 0.054932 | 0.39368
1864.5781 | 122.7722 | -118.634 | 3.9368 | 0.39891 | 0.0053508 | 0.00011194 | 0.05306 | 0.064148 | -9.1495e-05 | 0.088267 | 0.13733 | 3.9413 | -0.27466 | -118.7439 | -1.5701 | -2.6505 | -0.17395 | -44.6182 | 3.9734 | -119.0414 | 118.3594 | 0.004577 | 118.7714 | -0.10986 | 0.29755 | -5.5069 | -5.5435 | -0.40741 | 0.036621 | 0.41199
1865.5781 | 122.7814 | -118.5883 | 3.9642 | 0.39891 | 0.0042826 | 0.0033161 | 0.052205 | 0.062439 | 0.0011901 | 0.090617 | 0.14191 | 3.9642 | -0.2655 | -118.6935 | -1.6479 | -2.623 | -0.16022 | -44.6274 | 4.0009 | -118.9865 | 118.3228 | 0 | 118.7302 | -0.10528 | 0.29297 | -5.6122 | -5.6488 | -0.39825 | 0.036621 | 0.40741
1866.5781 | 122.7859 | -118.5837 | 3.9688 | 0.44468 | 0.0083416 | 0.0048115 | 0.049855 | 0.063293 | 0.0007629 | 0.089122 | 0.14648 | 3.978 | -0.26093 | -118.689 | -1.6434 | -2.6459 | -0.1831 | -44.7006 | 4.0237 | -118.9728 | 118.3228 | 0.009155 | 118.7302 | -0.10529 | 0.28381 | -5.6122 | -5.6671 | -0.3891 | 0.054932 | 0.40741
1867.5781 | 122.7814 | -118.5837 | 3.9642 | 0.44468 | 0.010478 | -0.00010166 | 0.051137 | 0.06308 | 0.0007629 | 0.090403 | 0.11902 | 3.9413 | -0.27008 | -118.7164 | -1.5701 | -2.6138 | -0.16479 | -44.6686 | 3.9871 | -118.9774 | 118.3136 | -0.022888 | 118.7027 | -0.13275 | 0.26093 | -5.5344 | -5.5573 | -0.39368 | 0.022889 | 0.3891
1868.5781 | 122.7722 | -118.5837 | 3.9551 | 0.4218 | 0.0083416 | 0.0026753 | 0.050924 | 0.064148 | 0.0009765 | 0.088908 | 0.13733 | 3.9642 | -0.25635 | -118.6844 | -1.4145 | -2.5497 | -0.17395 | -44.6411 | 3.9963 | -118.9911 | 118.3273 | 0.009155 | 118.721 | -0.10071 | 0.3067 | -5.3696 | -5.4108 | -0.40741 | 0.041199 | 0.39368
1869.5781 | 122.7814 | -118.602 | 3.9505 | 0.43706 | 0.0068462 | 0.0018209 | 0.050924 | 0.062866 | 0.0026855 | 0.089335 | 0.14191 | 3.9688 | -0.24719 | -118.6844 | -1.3184 | -2.5131 | -0.16022 | -44.6457 | 3.9963 | -118.9682 | 118.3548 | 0.018311 | 118.7439 | -0.082397 | 0.28381 | -5.2689 | -5.3146 | -0.36621 | 0.045777 | 0.3891
1870.5781 | 122.8088 | -118.5974 | 3.9459 | 0.41417 | 0.0068462 | 0.00096634 | 0.049855 | 0.063507 | -0.0003051 | 0.089762 | 0.20142 | 3.9276 | -0.23804 | -118.6798 | -1.4603 | -2.536 | -0.23346 | -44.6182 | 3.9642 | -118.9774 | 118.3594 | -0.018311 | 118.7988 | -0.082398 | 0.29755 | -5.4062 | -5.4245 | -0.37994 | 0.01831 | 0.43945
1871.5781 | 122.7631 | -118.5745 | 3.9734 | 0.45231 | 0.0055644 | 0.00075274 | 0.052205 | 0.062652 | 0.0009765 | 0.089122 | 0.13733 | 3.9505 | -0.24719 | -118.689 | -1.4557 | -2.5497 | -0.19226 | -44.6686 | 3.978 | -118.9865 | 118.3273 | -0.022889 | 118.7119 | -0.11444 | 0.29755 | -5.4291 | -5.4337 | -0.41199 | 0.004577 | 0.38452
1872.5781 | 122.818 | -119.1193 | 3.4012 | 0.4218 | 0.0072734 | 0.0018209 | 0.04601 | 0.062012 | 0.0039673 | 0.091258 | 0.17853 | 3.3783 | -0.23804 | -119.22 | -9.2056 | -5.2872 | -0.21973 | -45.1904 | 3.4287 | -119.5312 | 118.8812 | -0.022888 | 119.2978 | -0.10071 | 0.31128 | -12.6068 | -12.6343 | -0.41199 | 0.027466 | 0.41656
1873.5781 | 122.7905 | -119.0918 | 3.4012 | 0.45994 | 0.0059916 | 0.0048115 | 0.04601 | 0.063293 | 0.0031127 | 0.091899 | 0.16937 | 3.4103 | -0.23804 | -119.1742 | -9.1644 | -5.2872 | -0.21515 | -45.0439 | 3.4744 | -119.4855 | 118.8538 | 0.009155 | 119.2612 | -0.082397 | 0.31128 | -12.5656 | -12.6389 | -0.39368 | 0.073242 | 0.40741
1874.5781 | 122.7631 | -119.1788 | 3.3646 | 0.43706 | 0.005778 | 0.0045979 | 0.047078 | 0.062225 | 0.0031127 | 0.089976 | 0.11902 | 3.3829 | -0.27466 | -119.2978 | -9.2743 | -5.3741 | -0.17395 | -45.2179 | 3.4287 | -119.5908 | 118.9041 | 0.018311 | 119.2978 | -0.11902 | 0.29297 | -12.6389 | -12.7029 | -0.41199 | 0.064087 | 0.39368
1875.5781 | 122.8317 | -119.1193 | 3.3966 | 0.42943 | 0.004069 | 0.00053914 | 0.046865 | 0.061157 | 0.0031127 | 0.091258 | 0.16479 | 3.3966 | -0.22888 | -119.2108 | -9.2011 | -5.3101 | -0.2243 | -45.0211 | 3.4287 | -119.5267 | 118.8904 | 0 | 119.2841 | -0.091552 | 0.31586 | -12.5977 | -12.6297 | -0.40741 | 0.032044 | 0.39368
1876.5781 | 122.7402 | -119.1559 | 3.4241 | 0.35313 | 0.0049236 | 0.0011799 | 0.041311 | 0.061157 | 0.0043945 | 0.090403 | 0.12817 | 3.4058 | -0.24719 | -119.2657 | -9.2285 | -5.3375 | -0.14648 | -45.0806 | 3.4378 | -119.5175 | 118.9087 | -0.01831 | 119.2841 | -0.10986 | 0.25177 | -12.6526 | -12.6663 | -0.36163 | 0.013733 | 0.37537
1877.5781 | 122.7905 | -119.1284 | 3.3829 | 0.39128 | 0.0038554 | 0.0026753 | 0.046651 | 0.059021 | 0.0035401 | 0.088481 | 0.16937 | 3.3508 | -0.25635 | -119.2337 | -9.2056 | -5.3192 | -0.17853 | -45.0806 | 3.4149 | -119.5358 | 118.8721 | -0.032044 | 119.2978 | -0.10529 | 0.30212 | -12.5885 | -12.6205 | -0.40741 | 0.032043 | 0.42572
1878.5781 | 122.7905 | -119.1467 | 3.3829 | 0.13951 | 0.00471 | 0.0031025 | 0.046224 | 0.059021 | 0.0058899 | 0.089335 | 0.15106 | 3.3325 | -0.26093 | -119.2429 | -9.1782 | -5.3146 | -0.17853 | -44.9844 | 3.4012 | -119.5175 | 118.8858 | -0.050354 | 119.2978 | -0.09613 | 0.27466 | -12.561 | -12.5793 | -0.37079 | 0.01831 | 0.41199
1879.5781 | 122.7814 | -119.1559 | 3.4058 | 0.45994 | 0.0062052 | 0.0031025 | 0.047292 | 0.061371 | 0.0071717 | 0.090831 | 0.18768 | 3.3554 | -0.28381 | -119.2245 | -9.1736 | -5.2917 | -0.21057 | -44.9936 | 3.4149 | -119.5038 | 118.8721 | -0.050354 | 119.3436 | -0.068664 | 0.27924 | -12.5793 | -12.5885 | -0.3479 | 0.009155 | 0.4715
1880.5781 | 122.7997 | -119.1238 | 3.4103 | 0.39891 | 0.0055644 | -0.0050151 | 0.047078 | 0.060516 | 0.0033265 | 0.091258 | 0.16937 | 3.392 | -0.25177 | -119.1971 | -9.1644 | -5.278 | -0.22888 | -44.9158 | 3.4378 | -119.5175 | 118.8721 | -0.01831 | 119.2932 | -0.073243 | 0.32043 | -12.5748 | -12.6022 | -0.39368 | 0.027466 | 0.42114
1881.5781 | 122.8088 | -119.1559 | 3.392 | 0.24632 | 0.005778 | 0.0022481 | 0.048146 | 0.062012 | 0.0046081 | 0.089549 | 0.16479 | 3.3646 | -0.25635 | -119.2154 | -9.1782 | -5.2826 | -0.19226 | -44.9982 | 3.4103 | -119.5175 | 118.8995 | -0.027466 | 119.3207 | -0.059509 | 0.30212 | -12.5702 | -12.5885 | -0.36163 | 0.01831 | 0.42114
1882.5781 | 122.7905 | -119.1696 | 3.3737 | 0.42943 | 0.0064188 | 0.0058797 | 0.043447 | 0.06073 | 0.0050353 | 0.088694 | 0.15564 | 3.3371 | -0.25177 | -119.2291 | -9.1599 | -5.2689 | -0.21515 | -44.9753 | 3.392 | -119.545 | 118.9178 | -0.036621 | 119.3253 | -0.059509 | 0.31586 | -12.5336 | -12.5519 | -0.37537 | 0.018311 | 0.40741
1883.5781 | 122.8226 | -119.165 | 3.3646 | 0.43706 | 0.0042826 | -0.00052906 | 0.047933 | 0.060303 | 0.0048217 | 0.09019 | 0.17395 | 3.3554 | -0.24719 | -119.3802 | -9.2239 | -5.2094 | -0.16937 | -45.0394 | 3.36 | -119.5404 | 118.9178 | -0.009155 | 119.339 | -0.21515 | 0.16022 | -12.5885 | -12.5839 | -0.37537 | -0.004578 | 0.42114
1884.5781 | 122.7859 | -119.1742 | 3.3783 | 0.39128 | 0.0038554 | -0.00074266 | 0.041524 | 0.058807 | 0.0065307 | 0.087199 | 0.15564 | 3.3417 | -0.24261 | -119.252 | -9.2102 | -5.3284 | -0.18768 | -44.9478 | 3.4149 | -119.5084 | 118.9316 | -0.036621 | 119.3298 | -0.07782 | 0.25635 | -12.5885 | -12.6251 | -0.33417 | 0.036621 | 0.39826
1885.5781 | 122.7859 | -119.1422 | 3.3829 | 0.49046 | 0.00471 | 0.0028889 | 0.045797 | 0.061157 | 0.0054627 | 0.090831 | 0.15106 | 3.3463 | -0.24261 | -119.2474 | -9.2011 | -5.3101 | -0.19226 | -44.8563 | 3.392 | -119.5221 | 118.8995 | -0.036622 | 119.2932 | -0.10529 | 0.27466 | -12.5839 | -12.5931 | -0.37994 | 0.009155 | 0.39368
1886.5781 | 122.7036 | -119.2062 | 3.4149 | 0.11662 | 0.0062052 | 0.0018209 | 0.048574 | 0.057098 | 0.0035401 | 0.087626 | 0.086975 | 3.392 | -0.27466 | -119.3161 | -9.288 | -5.4108 | 0.10071 | -44.7235 | 3.4744 | -119.5358 | 118.9316 | -0.022888 | 119.2932 | -0.10986 | 0.21973 | -12.7029 | -12.7625 | -0.32959 | 0.059509 | 0.36163
1887.5781 | 122.7722 | -118.9453 | 3.5889 | 0.4752 | 0.0051372 | 0.00096634 | 0.051351 | 0.062012 | 0.0024719 | 0.088267 | 0.1831 | 3.5751 | -0.24719 | -119.0048 | -5.5527 | -4.0054 | -0.19226 | -44.9341 | 3.6392 | -119.2932 | 118.6981 | -0.013733 | 119.1284 | -0.05951 | 0.28839 | -9.1415 | -9.1919 | -0.3479 | 0.050354 | 0.4303
1888.5781 | 122.7951 | -118.8904 | 3.6438 | 0.40654 | 0.0077006 | 0.0013935 | 0.051137 | 0.061371 | 0.0026855 | 0.089976 | 0.14648 | 3.653 | -0.26093 | -118.9728 | -5.2597 | -3.891 | -0.19684 | -44.902 | 3.6667 | -119.2566 | 118.6295 | 0.009155 | 119.0369 | -0.082397 | 0.28381 | -8.9035 | -8.9264 | -0.36621 | 0.022888 | 0.40741
1889.5781 | 122.7997 | -118.9453 | 3.6026 | 0.4218 | 0.0049236 | 0.0026753 | 0.050069 | 0.062439 | 0.0003357 | 0.090403 | 0.17853 | 3.6026 | -0.23804 | -119.0048 | -5.3787 | -3.9001 | -0.21057 | -44.8288 | 3.6346 | -119.3024 | 118.7073 | 0 | 119.1238 | -0.05951 | 0.29755 | -8.9813 | -9.0134 | -0.35706 | 0.032044 | 0.41656
1890.5781 | 122.7997 | -118.9224 | 3.6026 | 0.40654 | 0.0059916 | 0.00096634 | 0.049642 | 0.062225 | 0.0043945 | 0.089122 | 0.19226 | 3.6072 | -0.24719 | -118.9957 | -5.3925 | -3.9505 | -0.21057 | -44.7418 | 3.6163 | -119.3207 | 118.6752 | 0.004578 | 119.1147 | -0.073243 | 0.32501 | -8.9951 | -9.0088 | -0.39825 | 0.013733 | 0.43945
1891.5781 | 122.818 | -118.959 | 3.5568 | 0.46757 | 0.00471 | 0.0028889 | 0.048787 | 0.062866 | 0.0041809 | 0.089549 | 0.1831 | 3.5934 | -0.22888 | -119.0506 | -5.3604 | -3.8452 | -0.28381 | -44.7098 | 3.5934 | -119.3253 | 118.7302 | 0.036621 | 119.1422 | -0.091553 | 0.27466 | -8.9172 | -8.9539 | -0.36621 | 0.036621 | 0.41199
1892.5781 | 122.7905 | -118.9362 | 3.6026 | 0.45994 | 0.007487 | 0.00011194 | 0.048574 | 0.061584 | 0.0003357 | 0.089549 | 0.19226 | 3.5889 | -0.23804 | -118.9865 | -5.4428 | -3.9322 | -0.21973 | -44.7464 | 3.6255 | -119.3024 | 118.6981 | -0.013733 | 119.1284 | -0.050354 | 0.31586 | -9.0454 | -9.0683 | -0.36621 | 0.022888 | 0.4303
1893.5781 | 122.7859 | -118.9407 | 3.5889 | 0.41417 | 0.009196 | 0.0013935 | 0.049215 | 0.063721 | 0.0031127 | 0.090831 | 0.18768 | 3.5797 | -0.24719 | -119.0094 | -5.365 | -3.9139 | -0.21515 | -44.6732 | 3.6255 | -119.3161 | 118.6935 | -0.009155 | 119.1284 | -0.068664 | 0.3067 | -8.9539 | -8.9905 | -0.37537 | 0.036621 | 0.43488
1894.5781 | 122.7356 | -118.9636 | 3.6346 | 0.32261 | 0.0087688 | 0.0063069 | 0.051564 | 0.061584 | 0.0031127 | 0.087626 | 0.10071 | 3.6392 | -0.28381 | -119.0826 | -5.5069 | -4.0329 | -0.086975 | -44.8105 | 3.6621 | -119.3344 | 118.6798 | 0.004577 | 119.0643 | -0.11902 | 0.25177 | -9.1415 | -9.169 | -0.37079 | 0.027465 | 0.38452
1895.5781 | 122.6852 | -118.9499 | 3.6209 | 0.17003 | 0.010264 | 0.0024617 | 0.052205 | 0.063721 | 0.0020447 | 0.087199 | 0.07782 | 3.6438 | -0.2655 | -119.0918 | -5.5573 | -4.0604 | -0.036621 | -44.7601 | 3.6758 | -119.3527 | 118.6844 | 0.022888 | 119.0277 | -0.14191 | 0.26093 | -9.1782 | -9.2331 | -0.40283 | 0.054931 | 0.34332
1896.5781 | 122.731 | -118.9728 | 3.6163 | 0.43706 | 0.0051372 | -0.00074266 | 0.049215 | 0.062439 | 0.0024719 | 0.090403 | 0.11444 | 3.6392 | -0.28381 | -119.0689 | -5.4657 | -3.9871 | -0.1236 | -44.6869 | 3.6575 | -119.3253 | 118.689 | 0.022888 | 119.0872 | -0.096131 | 0.25635 | -9.082 | -9.1232 | -0.35248 | 0.041199 | 0.39825
1897.5781 | 122.7859 | -118.9499 | 3.6118 | 0.44468 | 0.007487 | -0.00074266 | 0.048787 | 0.063934 | 0.0033265 | 0.088481 | 0.16479 | 3.5934 | -0.25635 | -119.014 | -5.365 | -3.923 | -0.1831 | -44.664 | 3.6438 | -119.3115 | 118.6935 | -0.01831 | 119.1147 | -0.064087 | 0.29755 | -8.9767 | -9.0088 | -0.36163 | 0.032044 | 0.42114
1898.5781 | 122.7631 | -118.9545 | 3.6209 | 0.42943 | 0.0059916 | -0.00052906 | 0.050283 | 0.062652 | 0.0020447 | 0.088267 | 0.14191 | 3.6438 | -0.28839 | -119.0369 | -5.3696 | -3.9459 | -0.16022 | -44.6274 | 3.6575 | -119.3115 | 118.6661 | 0.022888 | 119.0964 | -0.082397 | 0.27466 | -8.9905 | -9.0271 | -0.35705 | 0.036621 | 0.4303
1899.5781 | 122.7539 | -118.9407 | 3.6346 | 0.38365 | 0.0072734 | 0.0011799 | 0.052205 | 0.062866 | 0.0031127 | 0.088053 | 0.11902 | 3.6621 | -0.27466 | -119.0552 | -5.4657 | -3.978 | -0.11444 | -44.5679 | 3.6713 | -119.3253 | 118.6661 | 0.027465 | 119.0598 | -0.11444 | 0.27008 | -9.1003 | -9.137 | -0.38452 | 0.036621 | 0.39368
1900.5781 | 122.731 | -118.9362 | 3.6255 | 0.46757 | 0.007487 | 0.0013935 | 0.05306 | 0.063934 | 0.0022583 | 0.088908 | 0.10986 | 3.6484 | -0.27008 | -119.0872 | -5.4245 | -3.9825 | -0.050354 | -44.5038 | 3.6804 | -119.3344 | 118.6661 | 0.022888 | 119.046 | -0.15106 | 0.24719 | -9.05 | -9.1049 | -0.39826 | 0.054932 | 0.37994
1901.5781 | 122.6532 | -118.9362 | 3.6667 | 0.29973 | 0.0079142 | 0.0050251 | 0.051992 | 0.063721 | 0.0054627 | 0.089549 | 0.073242 | 3.6804 | -0.28381 | -119.1055 | -5.5389 | -4.0329 | 0.027466 | -44.0277 | 3.717 | -119.3436 | 118.6523 | 0.013733 | 119.0094 | -0.16937 | 0.23804 | -9.2056 | -9.256 | -0.40741 | 0.050354 | 0.35706
1902.5781 | 122.6669 | -118.9682 | 3.6301 | 0.26921 | 0.0077006 | 0.0033161 | 0.052633 | 0.064148 | 0.0020447 | 0.089762 | 0.09613 | 3.6392 | -0.27008 | -119.1193 | -5.4703 | -4.0237 | 0.032043 | -44.2657 | 3.6804 | -119.3527 | 118.6981 | 0.009155 | 119.0643 | -0.15106 | 0.23346 | -9.1003 | -9.1507 | -0.38452 | 0.050354 | 0.36621
1903.5781 | 122.6624 | -118.9545 | 3.653 | 0.33024 | 0.0096232 | 0.0020345 | 0.049428 | 0.064148 | 0.0033265 | 0.089976 | 0.068665 | 3.6575 | -0.28839 | -119.1284 | -5.3879 | -3.9688 | -0.004578 | -44.3115 | 3.685 | -119.3619 | 118.6661 | 0.004578 | 119.0231 | -0.17395 | 0.23346 | -9.0408 | -9.0729 | -0.40741 | 0.032044 | 0.35706
1904.5781 | 122.7127 | -118.9499 | 3.6438 | 2.4817 | 0.0081278 | 0.00096634 | 0.047933 | 0.063721 | 0.0018311 | 0.09019 | 0.16479 | 3.6667 | -0.27008 | -119.133 | -5.4199 | -3.9322 | -0.022888 | -44.2612 | 3.685 | -119.3481 | 118.6798 | 0.022888 | 119.1147 | -0.18311 | 0.21515 | -9.0637 | -9.1049 | -0.39826 | 0.041199 | 0.43488
1905.5781 | 122.6715 | -118.9865 | 3.6438 | 0.20817 | 0.007487 | 0.0031025 | 0.050924 | 0.066925 | 0.0026855 | 0.089549 | 0.07782 | 3.653 | -0.28839 | -119.1147 | -5.4428 | -3.978 | 0.041199 | -44.2154 | 3.6575 | -119.3344 | 118.6981 | 0.009155 | 119.0643 | -0.12817 | 0.21973 | -9.0866 | -9.1003 | -0.3479 | 0.013733 | 0.36621
1906.5781 | 122.6624 | -118.9636 | 3.6667 | 0.26158 | 0.009196 | 0.00032554 | 0.048787 | 0.063934 | -9.1495e-05 | 0.089549 | 0.068665 | 3.6621 | -0.28839 | -119.1193 | -5.4337 | -3.9597 | -0.004578 | -44.2703 | 3.6804 | -119.3619 | 118.6752 | -0.004578 | 119.0323 | -0.15564 | 0.24261 | -9.1003 | -9.1141 | -0.39825 | 0.013733 | 0.35706
1907.5781 | 122.6852 | -118.9865 | 3.6484 | 0.27684 | 0.009196 | 0.0020345 | 0.049215 | 0.063293 | 0.0024719 | 0.09019 | 0.1236 | 3.653 | -0.28839 | -119.101 | -5.4794 | -3.9688 | 0.032043 | -43.8126 | 3.6713 | -119.3665 | 118.6981 | 0.004578 | 119.1101 | -0.11444 | 0.2655 | -9.1278 | -9.1507 | -0.37994 | 0.022889 | 0.41199
1908.5781 | 122.7081 | -118.9499 | 3.6438 | 0.17766 | 0.0094096 | 0.0020345 | 0.050924 | 0.065857 | 0.0022583 | 0.089976 | 0.13733 | 3.6621 | -0.27466 | -119.0598 | -5.5115 | -3.9413 | 0.018311 | -43.277 | 3.7079 | -119.3619 | 118.6752 | 0.01831 | 119.0872 | -0.10986 | 0.30212 | -9.1553 | -9.2194 | -0.41199 | 0.064087 | 0.41199
1909.5781 | 122.6944 | -118.9636 | 3.653 | 0.13188 | 0.0087688 | 0.0028889 | 0.050924 | 0.065002 | 0.0020447 | 0.089122 | 0.16022 | 3.6804 | -0.26093 | -119.0506 | -5.3192 | -3.8635 | 0.013733 | -43.2953 | 3.6896 | -119.3253 | 118.7027 | 0.027466 | 119.1238 | -0.086975 | 0.27466 | -8.9722 | -9.0088 | -0.36163 | 0.036621 | 0.42114
1910.5781 | 122.6761 | -118.9957 | 3.6346 | 0.20817 | 0.0083416 | -0.00074266 | 0.048574 | 0.064361 | 0.0028991 | 0.087199 | 0.10529 | 3.6438 | -0.3067 | -119.1147 | -5.4794 | -3.9459 | 0.032043 | -43.3136 | 3.6942 | -119.3298 | 118.689 | 0.009155 | 119.101 | -0.11902 | 0.21515 | -9.1141 | -9.1736 | -0.33417 | 0.059509 | 0.41199
1911.5781 | 122.644 | -118.9819 | 3.6255 | 0.25395 | 0.010478 | 0.0050251 | 0.051351 | 0.065002 | 0.0009765 | 0.09019 | 0.09613 | 3.6713 | -0.28839 | -119.1422 | -5.5069 | -3.9734 | 0.032043 | -43.5745 | 3.7033 | -119.3619 | 118.6935 | 0.045777 | 119.0781 | -0.16022 | 0.21973 | -9.1324 | -9.2102 | -0.37994 | 0.07782 | 0.38452
1912.5781 | 122.6898 | -118.9728 | 3.6621 | 0.26158 | 0.0081278 | 0.00096634 | 0.049855 | 0.065002 | 0.0046081 | 0.091044 | 0.091553 | 3.6621 | -0.29297 | -119.1193 | -5.4977 | -3.9505 | 0.036621 | -43.5883 | 3.7033 | -119.3619 | 118.6798 | 0 | 119.0643 | -0.14648 | 0.24261 | -9.1599 | -9.201 | -0.3891 | 0.041199 | 0.38452
1913.5781 | 122.7264 | -118.9774 | 3.6484 | 0.22343 | 0.0068462 | -0.0033061 | 0.049215 | 0.064575 | 0.0003357 | 0.09019 | 0.15564 | 3.6758 | -0.23346 | -119.0735 | -5.4016 | -3.8818 | 0.009155 | -43.5791 | 3.685 | -119.3802 | 118.7439 | 0.027466 | 119.133 | -0.09613 | 0.3067 | -9.05 | -9.0866 | -0.40283 | 0.036622 | 0.3891
1914.5781 | 122.6715 | -119.0002 | 3.6346 | 0.24632 | 0.0083416 | 0.0013935 | 0.051351 | 0.067352 | 0.0024719 | 0.088481 | 0.11444 | 3.6255 | -0.28839 | -119.1193 | -5.3055 | -3.8864 | 0.032043 | -43.5745 | 3.6438 | -119.371 | 118.7119 | -0.009156 | 119.1147 | -0.11902 | 0.25177 | -8.9401 | -8.9493 | -0.37079 | 0.009155 | 0.40283
1915.5781 | 122.7127 | -118.9499 | 3.6987 | 0.13951 | 0.007487 | 0.0020345 | 0.049855 | 0.065216 | 0.0011901 | 0.089335 | 0.15564 | 3.6346 | -0.2655 | -119.0735 | -5.0308 | -3.7537 | 0.14648 | -43.3411 | 3.7308 | -119.3298 | 118.6844 | -0.064086 | 119.1055 | -0.1236 | 0.25635 | -8.7296 | -8.7616 | -0.37994 | 0.032044 | 0.42114
1916.5781 | 122.7219 | -118.9911 | 3.6255 | 0.14714 | 0.0068462 | 0.0016073 | 0.050069 | 0.065002 | -0.0003051 | 0.089976 | 0.14191 | 3.6346 | -0.27008 | -119.0735 | -5.3055 | -3.8635 | 0.018311 | -43.7805 | 3.6804 | -119.3573 | 118.721 | 0.009156 | 119.133 | -0.082397 | 0.28381 | -8.931 | -8.9859 | -0.36621 | 0.054932 | 0.41199
1917.5781 | 122.699 | -118.9957 | 3.598 | 0.20054 | 0.0072734 | 0.0037435 | 0.047933 | 0.064575 | 0.0024719 | 0.088053 | 0.16937 | 3.6758 | -0.22888 | -119.0964 | -5.2322 | -3.8544 | 0.013733 | -43.7622 | 3.6575 | -119.3939 | 118.7668 | 0.07782 | 119.165 | -0.10071 | 0.29755 | -8.8303 | -8.8898 | -0.39825 | 0.05951 | 0.39826
1918.5781 | 122.6944 | -119.046 | 3.5568 | 0.23106 | 0.0085552 | 0.0056661 | 0.049855 | 0.063507 | 0.0020447 | 0.089549 | 0.1236 | 3.6209 | -0.27466 | -119.1696 | -5.4428 | -3.9642 | 0.013733 | -43.8263 | 3.6301 | -119.4168 | 118.7714 | 0.064087 | 119.1696 | -0.1236 | 0.24719 | -8.9996 | -9.0729 | -0.37079 | 0.073242 | 0.39825
1919.5781 | 122.6807 | -119.0094 | 3.5889 | 0.2158 | 0.0079142 | 0.0013935 | 0.051778 | 0.06607 | 0.0020447 | 0.087626 | 0.1236 | 3.6209 | -0.27924 | -119.133 | -5.3696 | -3.9276 | -0.004578 | -43.8354 | 3.653 | -119.4122 | 118.7302 | 0.032044 | 119.133 | -0.1236 | 0.27923 | -8.9584 | -9.0225 | -0.40283 | 0.064087 | 0.40283
1920.5781 | 122.7173 | -119.0186 | 3.5889 | 0.17766 | 0.0064188 | 0.00011194 | 0.051564 | 0.06543 | 0.0003357 | 0.088481 | 0.13733 | 3.6484 | -0.26093 | -119.1055 | -5.3833 | -3.9047 | 0 | -43.6386 | 3.6575 | -119.3848 | 118.7576 | 0.059509 | 119.1559 | -0.086975 | 0.27924 | -8.9722 | -9.0408 | -0.36621 | 0.068665 | 0.39825
1921.5781 | 122.699 | -118.9819 | 3.5934 | 0.086103 | 0.007487 | 0.0024617 | 0.051778 | 0.064148 | 0.0016175 | 0.089549 | 0.16479 | 3.6484 | -0.23346 | -119.1147 | -5.2826 | -3.8635 | 0.018311 | -43.7668 | 3.6484 | -119.3893 | 118.7485 | 0.054931 | 119.1467 | -0.13275 | 0.27466 | -8.876 | -8.931 | -0.40741 | 0.054931 | 0.39825
1922.5781 | 122.7219 | -119.0002 | 3.6209 | 0.086103 | 0.0077006 | 0.0039571 | 0.050924 | 0.064789 | 0.0005493 | 0.088908 | 0.15564 | 3.6209 | -0.28381 | -119.0826 | -5.3696 | -3.8864 | 0.036621 | -43.6798 | 3.653 | -119.3573 | 118.7164 | 0 | 119.1559 | -0.082398 | 0.27466 | -8.9905 | -9.0225 | -0.35706 | 0.032043 | 0.43945
1923.5781 | 122.7264 | -118.9865 | 3.6301 | 0.025068 | 0.0059916 | 0.0020345 | 0.048787 | 0.06308 | 0.0028991 | 0.089976 | 0.14191 | 3.6163 | -0.30212 | -119.0964 | -5.4245 | -3.9001 | 0.050354 | -43.6111 | 3.6713 | -119.3985 | 118.6844 | -0.013733 | 119.1284 | -0.10986 | 0.30212 | -9.0546 | -9.0958 | -0.41199 | 0.041199 | 0.44403
1924.5781 | 122.7448 | -118.9545 | 3.6758 | 0.18529 | 0.0064188 | 0.0060933 | 0.050283 | 0.065216 | 0.0014039 | 0.088267 | 0.15564 | 3.6118 | -0.2655 | -119.1055 | -5.3146 | -3.8635 | 0.068665 | -43.515 | 3.6713 | -119.3024 | 118.689 | -0.064087 | 119.1101 | -0.15106 | 0.19684 | -8.9905 | -8.9859 | -0.3479 | -0.004577 | 0.42114
1925.5781 | 122.7036 | -119.0094 | 3.598 | 0.13188 | 0.0079142 | 0.00075274 | 0.049642 | 0.06543 | 0.0014039 | 0.089976 | 0.15106 | 3.6072 | -0.27008 | -119.1147 | -5.4016 | -3.923 | -0.009155 | -43.9682 | 3.6346 | -119.3848 | 118.7393 | 0.009156 | 119.1605 | -0.10529 | 0.27008 | -8.9996 | -9.0363 | -0.37537 | 0.036622 | 0.42114
1926.5781 | 122.6898 | -118.9911 | 3.6026 | 0.093733 | 0.0072734 | 0.0013935 | 0.051778 | 0.064148 | 0.0001221 | 0.086985 | 0.15106 | 3.6209 | -0.24261 | -119.1147 | -5.3879 | -3.891 | -0.004578 | -43.9407 | 3.653 | -119.3939 | 118.7485 | 0.018311 | 119.1422 | -0.1236 | 0.27924 | -8.9905 | -9.0408 | -0.40283 | 0.050354 | 0.39368
1927.5781 | 122.731 | -119.0048 | 3.5843 | 0.3455 | 0.0083416 | 0.0033161 | 0.049215 | 0.063507 | 0.0020447 | 0.089762 | 0.19226 | 3.653 | -0.21515 | -119.1147 | -5.3879 | -3.9001 | 0.009155 | -43.9911 | 3.653 | -119.4031 | 118.7897 | 0.068664 | 119.1971 | -0.10986 | 0.28839 | -8.9722 | -9.0408 | -0.39825 | 0.068664 | 0.40741
1928.5781 | 122.7264 | -118.9911 | 3.6255 | -0.0054494 | 0.0070598 | 0.0031025 | 0.050496 | 0.06543 | -0.0003051 | 0.091258 | 0.20142 | 3.6713 | -0.22888 | -119.0964 | -5.4291 | -3.9139 | 0 | -43.8538 | 3.6758 | -119.371 | 118.7622 | 0.045777 | 119.1925 | -0.10529 | 0.27466 | -9.0546 | -9.1049 | -0.37994 | 0.050354 | 0.4303
1929.5781 | 122.7264 | -119.0048 | 3.5797 | 0.0021796 | 0.007487 | 0.0020345 | 0.051778 | 0.065002 | 0.0016175 | 0.088694 | 0.15564 | 3.6072 | -0.29297 | -119.0918 | -5.4245 | -3.9047 | 0.045776 | -43.8446 | 3.6621 | -119.4077 | 118.7119 | 0.027466 | 119.1605 | -0.086975 | 0.31586 | -9.0042 | -9.0866 | -0.40283 | 0.082397 | 0.44861
1930.5781 | 122.699 | -119.0231 | 3.5889 | 0.070845 | 0.0072734 | 0.0039571 | 0.049001 | 0.066284 | 0.0020447 | 0.089122 | 0.16479 | 3.5797 | -0.27924 | -119.1238 | -5.4016 | -3.8773 | 0.054932 | -43.7942 | 3.6392 | -119.3893 | 118.7439 | -0.009155 | 119.1879 | -0.10071 | 0.2655 | -8.9905 | -9.0408 | -0.36621 | 0.050354 | 0.44403
1931.5781 | 122.7448 | -118.9819 | 3.6209 | 0.11662 | 0.0059916 | 0.0011799 | 0.050924 | 0.069275 | 0.0001221 | 0.090403 | 0.16479 | 3.6072 | -0.27924 | -119.0689 | -5.3558 | -3.8956 | 0.004578 | -43.84 | 3.6758 | -119.371 | 118.7027 | -0.013733 | 119.1467 | -0.086975 | 0.30212 | -8.9767 | -9.0317 | -0.3891 | 0.054931 | 0.44403
1932.5781 | 122.6578 | -119.0186 | 3.6118 | 0.19291 | 0.0072734 | 0.0024617 | 0.051778 | 0.06607 | 0.0003357 | 0.089122 | 0.14191 | 3.6438 | -0.28839 | -119.1238 | -4.985 | -3.7674 | 0.013733 | -43.7668 | 3.6804 | -119.3893 | 118.7302 | 0.032044 | 119.1605 | -0.10528 | 0.2655 | -8.5968 | -8.6655 | -0.37079 | 0.068665 | 0.4303
1933.5781 | 122.6898 | -119.0002 | 3.598 | 0.19291 | 0.0087688 | 0.00053914 | 0.052205 | 0.065857 | 0.0005493 | 0.08784 | 0.14191 | 3.6072 | -0.27466 | -119.1284 | -5.3238 | -3.8681 | 0 | -43.7668 | 3.6713 | -119.3848 | 118.7256 | 0.009156 | 119.1422 | -0.12817 | 0.25635 | -8.9218 | -8.9951 | -0.38452 | 0.073243 | 0.41657
1934.5781 | 122.7219 | -119.0186 | 3.6026 | 0.14714 | 0.0055644 | 0.0050251 | 0.051564 | 0.065002 | 0.0003357 | 0.089335 | 0.16022 | 3.6163 | -0.28839 | -119.1101 | -5.3833 | -3.8956 | 0 | -43.7393 | 3.6484 | -119.3939 | 118.7302 | 0.013733 | 119.1788 | -0.091552 | 0.28381 | -8.9859 | -9.0317 | -0.37537 | 0.045776 | 0.44861
1935.5781 | 122.7081 | -118.9728 | 3.6255 | 0.13188 | 0.0079142 | 0.0052387 | 0.051778 | 0.064575 | 0.0031127 | 0.088908 | 0.14191 | 3.6758 | -0.25177 | -119.0689 | -5.2231 | -3.8132 | -0.004578 | -43.602 | 3.6804 | -119.4031 | 118.721 | 0.050354 | 119.1147 | -0.096131 | 0.33417 | -8.8486 | -8.9035 | -0.4303 | 0.054932 | 0.39368
1936.5781 | 122.7081 | -118.9636 | 3.6301 | 0.10136 | 0.0079142 | 0.0018209 | 0.04836 | 0.065216 | 0.0014039 | 0.087413 | 0.16937 | 3.6575 | -0.27924 | -119.0826 | -5.2689 | -3.8361 | 0.009155 | -43.5928 | 3.6942 | -119.3619 | 118.6844 | 0.027466 | 119.133 | -0.11902 | 0.27923 | -8.8989 | -8.963 | -0.39825 | 0.064087 | 0.44861
1937.5781 | 122.7264 | -118.9682 | 3.6301 | 0.18529 | 0.0062052 | 0.0056661 | 0.050069 | 0.063934 | 0.0005493 | 0.089976 | 0.16479 | 3.6896 | -0.22888 | -119.0689 | -5.2734 | -3.8132 | -0.004578 | -43.5837 | 3.717 | -119.3527 | 118.7393 | 0.059509 | 119.133 | -0.10071 | 0.28381 | -8.9035 | -8.9905 | -0.38452 | 0.086975 | 0.39368
1938.5781 | 122.7127 | -118.8721 | 3.7262 | 0.15477 | 0.0083416 | 0.0013935 | 0.050069 | 0.065002 | 0.0014039 | 0.088908 | 0.16022 | 3.6987 | -0.25177 | -118.9682 | -5.0903 | -3.7079 | -0.009155 | -43.4875 | 3.8132 | -119.3115 | 118.6203 | -0.027466 | 119.0323 | -0.096131 | 0.34332 | -8.8165 | -8.9035 | -0.43945 | 0.086975 | 0.41199
1939.5781 | 122.7173 | -118.9911 | 3.6667 | 0.13188 | 0.0079142 | 0.0048115 | 0.051564 | 0.063507 | 0.0031127 | 0.089122 | 0.14191 | 3.6621 | -0.27008 | -119.0964 | -5.397 | -3.8589 | 0.004578 | -43.5562 | 3.7033 | -119.3436 | 118.721 | -0.004578 | 119.133 | -0.10529 | 0.24719 | -9.0637 | -9.1003 | -0.35248 | 0.036621 | 0.41199
1940.5781 | 122.699 | -118.927 | 3.653 | 0.18529 | 0.0049236 | 0.0069477 | 0.051351 | 0.065857 | 0.0028991 | 0.089549 | 0.16479 | 3.6575 | -0.27008 | -119.0643 | -5.2826 | -3.7994 | 0.009155 | -43.5104 | 3.7125 | -119.3619 | 118.6569 | 0.004578 | 119.0918 | -0.13733 | 0.29755 | -8.9355 | -8.9951 | -0.43488 | 0.059509 | 0.43488
1941.5781 | 122.7264 | -118.9682 | 3.6484 | 0.10899 | 0.0062052 | -0.00052906 | 0.049001 | 0.064575 | 0.0007629 | 0.089335 | 0.16937 | 3.7216 | -0.2243 | -119.0781 | -5.278 | -3.7949 | 0.009155 | -43.4418 | 3.6942 | -119.3756 | 118.7439 | 0.073243 | 119.1376 | -0.10986 | 0.29755 | -8.9264 | -8.9722 | -0.40741 | 0.045777 | 0.39368
1942.5781 | 122.7219 | -118.9774 | 3.6621 | 0.15477 | 0.0059916 | 0.0067341 | 0.047933 | 0.065216 | 0.0007629 | 0.088694 | 0.31586 | 3.653 | -0.24261 | -119.0414 | -5.3146 | -3.7994 | 0.018311 | -43.3228 | 3.7354 | -119.339 | 118.7347 | -0.009155 | 119.2932 | -0.064087 | 0.29755 | -8.9767 | -9.05 | -0.36163 | 0.073243 | 0.55847
1943.5781 | 122.7356 | -118.9819 | 3.6346 | -0.0054494 | 0.010478 | 0.0024617 | 0.049855 | 0.063721 | 0.0020447 | 0.088481 | 0.12817 | 3.6621 | -0.30212 | -119.046 | -5.3146 | -3.804 | 0.050354 | -43.3456 | 3.6713 | -119.3756 | 118.6798 | 0.027465 | 119.1101 | -0.064087 | 0.32959 | -8.9493 | -8.9859 | -0.39368 | 0.036621 | 0.4303
1944.5938 | 122.7951 | -118.8995 | 3.6575 | 0.12425 | 0.0017192 | -0.00031526 | 0.042379 | 0.060944 | 0.0035401 | 0.09019 | 0.13733 | 3.6209 | -0.23804 | -118.9957 | -5.1727 | -3.6804 | -0.07782 | -43.1259 | 3.7216 | -119.2566 | 118.6615 | -0.036621 | 119.0369 | -0.096131 | 0.26093 | -8.8303 | -8.8943 | -0.35706 | 0.064087 | 0.37537
1945.6562 | 122.8088 | -118.8904 | 3.6392 | 0.42943 | 0.0042826 | -0.00074266 | 0.049428 | 0.061371 | 0.0001221 | 0.09019 | 0.1831 | 3.6301 | -0.25635 | -118.9957 | -5.3467 | -3.7765 | -0.14191 | -43.1992 | 3.6301 | -119.2795 | 118.634 | -0.009155 | 119.0735 | -0.10529 | 0.28381 | -8.9859 | -8.9767 | -0.3891 | -0.009155 | 0.43945
1946.5938 | 122.818 | -118.8904 | 3.6667 | 0.070845 | 0.0015056 | -0.0037333 | 0.04302 | 0.05838 | 0.0028991 | 0.089762 | 0.15564 | 3.6438 | -0.23804 | -118.9911 | -5.246 | -3.6896 | -0.10071 | -43.0664 | 3.6987 | -119.2703 | 118.6523 | -0.022888 | 119.046 | -0.10071 | 0.27924 | -8.9127 | -8.9447 | -0.37994 | 0.032043 | 0.39368
1947.6719 | 122.699 | -118.9499 | 3.6575 | 0.43706 | 0.011546 | 0.0031025 | 0.049215 | 0.060516 | 0.0020447 | 0.087199 | 0.10986 | 3.6758 | -0.26093 | -119.0689 | -5.3558 | -3.8361 | 0.10986 | -43.1534 | 3.717 | -119.3298 | 118.689 | 0.01831 | 119.0598 | -0.11902 | 0.26093 | -9.0134 | -9.0729 | -0.37994 | 0.059509 | 0.37079
1948.5781 | 122.7264 | -118.927 | 3.6713 | 0.10136 | 0.0055644 | 0.00011194 | 0.052846 | 0.060303 | 0.0024719 | 0.08784 | 0.16479 | 3.6713 | -0.27466 | -119.0002 | -5.3787 | -3.7903 | 0.022888 | -43.1534 | 3.7216 | -119.3344 | 118.6523 | 0 | 119.0918 | -0.073242 | 0.33417 | -9.05 | -9.1003 | -0.40741 | 0.050354 | 0.43945
1949.9219 | 122.7676 | -118.8904 | 3.6758 | 0.36839 | 0.0068462 | 0.00075274 | 0.04601 | 0.061798 | 0.0039673 | 0.090403 | 0.17853 | 3.6346 | -0.23804 | -118.9957 | -5.2185 | -3.6758 | -0.17395 | -43.0527 | 3.685 | -119.2795 | 118.6523 | -0.041198 | 119.0689 | -0.10529 | 0.28381 | -8.8943 | -8.9035 | -0.3891 | 0.009156 | 0.41656
1950.6094 | 122.7127 | -118.927 | 3.653 | 0.078474 | 0.0066326 | 0.0016073 | 0.052205 | 0.062652 | 0.0033265 | 0.089762 | 0.19226 | 3.7216 | -0.21973 | -119.0002 | -5.3467 | -3.7994 | -0.022888 | -43.0573 | 3.7079 | -119.3207 | 118.7073 | 0.068665 | 119.1193 | -0.073242 | 0.32044 | -8.9996 | -9.0546 | -0.39368 | 0.054932 | 0.41199
1951.6094 | 122.7173 | -118.7531 | 3.8177 | 0.017439 | 0.005778 | 0.0018209 | 0.049428 | 0.063721 | 0.0024719 | 0.089549 | 0.13733 | 3.8406 | -0.28839 | -118.8675 | -2.8702 | -2.8702 | 0.050354 | -42.8238 | 3.8589 | -119.2017 | 118.4647 | 0.022888 | 118.8904 | -0.11444 | 0.33417 | -6.6879 | -6.7291 | -0.44861 | 0.041199 | 0.42572
1952.7031 | 122.6852 | -118.7805 | 3.8223 | -0.60817 | 0.0079142 | 0.0060933 | 0.052633 | 0.063934 | 0.0016175 | 0.091258 | 0.032043 | 3.8498 | -0.2655 | -118.9178 | -2.9434 | -2.8931 | -0.027466 | -42.9932 | 3.8635 | -119.1559 | 118.515 | 0.027465 | 118.8126 | -0.13733 | 0.23804 | -6.7657 | -6.8069 | -0.37537 | 0.041198 | 0.29755
1953.6562 | 122.7768 | -118.7485 | 3.772 | 0.39128 | 0.007487 | 0.0016073 | 0.04302 | 0.065002 | -9.1495e-05 | 0.088694 | -0.027466 | 3.7216 | -0.27008 | -118.8263 | -3.2089 | -2.9205 | -0.18768 | -42.7734 | 3.7949 | -119.1422 | 118.4784 | -0.050354 | 118.721 | -0.07782 | 0.31586 | -6.9809 | -7.0038 | -0.39368 | 0.022888 | 0.24262
1955.2031 | 122.7951 | -118.6935 | 3.8406 | 0.28447 | 0.00471 | 0.0058797 | 0.046224 | 0.063721 | 0.0009765 | 0.089549 | 0.16022 | 3.8177 | -0.25177 | -118.7943 | -3.0396 | -2.829 | -0.1831 | -42.6956 | 3.8498 | -119.0964 | 118.4418 | -0.022888 | 118.8538 | -0.10071 | 0.30212 | -6.8802 | -6.8893 | -0.40283 | 0.009155 | 0.41199
1956.4688 | 122.7127 | -118.7393 | 3.8544 | 0.12425 | 0.0066326 | -0.0011699 | 0.051137 | 0.062012 | 0.0020447 | 0.090403 | 0.15106 | 3.8315 | -0.27466 | -118.808 | -2.9846 | -2.8656 | 0 | -42.6544 | 3.9185 | -119.1238 | 118.4647 | -0.022888 | 118.8904 | -0.068664 | 0.31586 | -6.839 | -6.9031 | -0.38452 | 0.064087 | 0.42572
1957.2188 | 122.7585 | -118.7027 | 3.8269 | 0.33787 | 0.0049236 | 0.00032554 | 0.044942 | 0.061371 | 0.0024719 | 0.088267 | 0.13733 | 3.7949 | -0.23346 | -118.8629 | -2.9617 | -2.8336 | -0.16479 | -42.4667 | 3.8498 | -119.133 | 118.4692 | -0.032043 | 118.84 | -0.16022 | 0.27008 | -6.7886 | -6.8115 | -0.4303 | 0.022888 | 0.37079
1957.6719 | 122.7127 | -118.7897 | 3.8132 | 0.14714 | 0.009196 | 0.0041707 | 0.05306 | 0.063507 | -0.0020141 | 0.086344 | 0.16937 | 3.8498 | -0.22888 | -118.8629 | -3.035 | -2.8885 | -0.004578 | -42.5812 | 3.8681 | -119.2108 | 118.5608 | 0.036621 | 118.959 | -0.073242 | 0.3479 | -6.8481 | -6.9031 | -0.42114 | 0.054932 | 0.39826
1958.5781 | 122.6349 | -118.6935 | 3.891 | 0.36839 | 0.0059916 | 0.00032554 | 0.05071 | 0.063721 | 0.0009765 | 0.089335 | 0.086975 | 3.8498 | -0.28381 | -118.895 | -3.0579 | -2.916 | -0.022888 | -42.5949 | 3.9139 | -119.0735 | 118.4097 | -0.041199 | 118.7805 | -0.20142 | 0.17853 | -6.9489 | -6.9717 | -0.37994 | 0.022888 | 0.37079
1959.5781 | 122.6898 | -118.7393 | 3.8956 | -0.043596 | 0.0044962 | -0.00031526 | 0.042379 | 0.059662 | -0.0003051 | 0.089122 | 0.09613 | 3.8544 | -0.27008 | -118.8629 | -2.6276 | -2.7328 | 0.11444 | -42.4118 | 3.9368 | -119.0826 | 118.4692 | -0.041199 | 118.8354 | -0.1236 | 0.21973 | -6.5231 | -6.5643 | -0.34332 | 0.041199 | 0.36621
1960.5781 | 122.6898 | -118.7485 | 3.8956 | -0.066485 | 0.005778 | 0.0020345 | 0.047078 | 0.06073 | 0.0011901 | 0.088481 | 0.068665 | 3.8681 | -0.27008 | -118.8812 | -2.7832 | -2.8015 | 0.14191 | -42.453 | 3.9276 | -119.0964 | 118.4784 | -0.027466 | 118.8171 | -0.13275 | 0.21515 | -6.6788 | -6.7108 | -0.3479 | 0.032043 | 0.33875
1961.5781 | 122.6761 | -118.7119 | 3.9413 | 0.086103 | 0.0051372 | -0.0013835 | 0.047933 | 0.061371 | -0.0005189 | 0.089335 | 0.082397 | 3.9185 | -0.27924 | -118.8171 | -2.742 | -2.7603 | 0.13733 | -42.3111 | 3.9597 | -119.0826 | 118.4326 | -0.022888 | 118.7943 | -0.10529 | 0.2655 | -6.6833 | -6.7017 | -0.37079 | 0.018311 | 0.36163
1962.5781 | 122.7127 | -118.7759 | 3.8818 | -0.097002 | 0.0027874 | -0.00074266 | 0.046437 | 0.060303 | 0.0022583 | 0.088481 | 0.11444 | 3.8589 | -0.26093 | -118.8446 | -2.8061 | -2.7878 | 0.086975 | -42.2745 | 3.9322 | -119.0964 | 118.515 | -0.022888 | 118.8904 | -0.068664 | 0.25177 | -6.6879 | -6.7383 | -0.32043 | 0.050354 | 0.37537
1963.5781 | 122.7905 | -118.6935 | 3.8773 | 2.2529 | 0.0059916 | -0.0011699 | 0.047078 | 0.060303 | -0.0009461 | 0.089122 | 0.15106 | 3.8132 | -0.24719 | -118.7759 | -2.4857 | -2.5772 | -0.045776 | -42.1875 | 3.9093 | -119.046 | 118.4463 | -0.064087 | 118.8446 | -0.082398 | 0.27008 | -6.3629 | -6.395 | -0.35248 | 0.032044 | 0.39825
1964.5781 | 122.7676 | -118.721 | 3.8361 | -0.020708 | 0.0036418 | -0.0013835 | 0.048146 | 0.06073 | 0.0003357 | 0.087626 | 0.18768 | 3.8177 | -0.24261 | -118.7119 | -2.3758 | -2.6871 | -0.13275 | -42.0868 | 3.8498 | -119.0781 | 118.4784 | -0.018311 | 118.9087 | 0.009155 | 0.36621 | -6.2119 | -6.2256 | -0.35706 | 0.013732 | 0.4303
1965.5781 | 122.7768 | -118.6981 | 3.8864 | -0.013079 | 0.0049236 | -0.0028789 | 0.045369 | 0.061371 | -0.0005189 | 0.087199 | 0.15564 | 3.7994 | -0.23804 | -118.7714 | -2.3895 | -2.5635 | -0.013733 | -42.0959 | 3.891 | -119.0598 | 118.4601 | -0.086976 | 118.8538 | -0.073242 | 0.28839 | -6.2759 | -6.2805 | -0.36163 | 0.004577 | 0.39368
1966.5781 | 122.6944 | -118.7347 | 3.8773 | -0.051226 | 0.00471 | 0.00075274 | 0.048146 | 0.06073 | 0.0001221 | 0.087413 | 0.14648 | 3.8269 | -0.25635 | -118.8126 | -2.4399 | -2.6459 | 0.10529 | -42.3203 | 3.923 | -119.0872 | 118.4784 | -0.050354 | 118.8812 | -0.07782 | 0.27466 | -6.3171 | -6.3629 | -0.35248 | 0.045777 | 0.40283
1967.5781 | 122.7631 | -118.7256 | 3.8727 | -0.043596 | 0.0044962 | -0.0048015 | 0.047506 | 0.060303 | -0.0003051 | 0.088267 | 0.14191 | 3.8315 | -0.24719 | -118.7943 | -2.4216 | -2.6093 | 0.027466 | -42.1326 | 3.891 | -119.0781 | 118.4784 | -0.041199 | 118.8675 | -0.068664 | 0.28381 | -6.2943 | -6.3126 | -0.35248 | 0.01831 | 0.3891
1968.5781 | 122.7585 | -118.7256 | 3.8681 | 0.070845 | 0.0032146 | -0.0011699 | 0.047292 | 0.059875 | -0.0015869 | 0.088908 | 0.16937 | 3.804 | -0.22888 | -118.7714 | -2.3895 | -2.5818 | 0 | -42.0502 | 3.8681 | -119.0552 | 118.4967 | -0.064087 | 118.895 | -0.045776 | 0.28381 | -6.2576 | -6.2576 | -0.32959 | 0 | 0.39826
1969.5781 | 122.7951 | -118.6981 | 3.891 | 0.56676 | 0.0038554 | -0.0037333 | 0.045797 | 0.059021 | -0.0005189 | 0.089122 | 0.16022 | 3.8177 | -0.25635 | -118.7485 | -2.3163 | -2.5314 | -0.036621 | -42.0181 | 3.891 | -119.046 | 118.4418 | -0.073242 | 118.8583 | -0.050354 | 0.29755 | -6.2073 | -6.2073 | -0.3479 | 0 | 0.41657
1970.5781 | 122.8363 | -118.6935 | 3.8269 | 0.11662 | 0.0038554 | 0.0013935 | 0.044301 | 0.059448 | -0.0009461 | 0.08784 | 0.15106 | 3.8086 | -0.25177 | -118.7576 | -2.3026 | -2.504 | -0.10986 | -41.9449 | 3.8544 | -119.0506 | 118.4418 | -0.01831 | 118.8446 | -0.064087 | 0.29297 | -6.1295 | -6.1569 | -0.35706 | 0.027466 | 0.40283
1971.5781 | 122.818 | -118.6523 | 3.8498 | 0.047956 | 0.0032146 | 0.00032554 | 0.044729 | 0.057953 | -0.0005189 | 0.08784 | 0.18768 | 3.8406 | -0.23346 | -118.7256 | -2.3163 | -2.5085 | -0.10529 | -41.89 | 3.9047 | -119.0277 | 118.4189 | -0.009155 | 118.84 | -0.073242 | 0.30212 | -6.1661 | -6.221 | -0.37537 | 0.054932 | 0.42114
1972.5781 | 122.7997 | -118.6935 | 3.8635 | 0.017439 | 0.0019328 | -0.00074266 | 0.046865 | 0.055817 | 0.0005493 | 0.087413 | 0.17853 | 3.8132 | -0.24261 | -118.7439 | -2.3163 | -2.5085 | -0.068665 | -41.9449 | 3.8681 | -119.0369 | 118.4509 | -0.050354 | 118.8721 | -0.050354 | 0.29297 | -6.1798 | -6.1844 | -0.34332 | 0.004578 | 0.42114
1973.5781 | 122.7814 | -118.6844 | 3.8818 | -0.66158 | 0.0027874 | 0.0031025 | 0.049001 | 0.059875 | -9.1495e-05 | 0.088053 | 0.19684 | 3.7949 | -0.26093 | -118.7302 | -2.3071 | -2.5131 | -0.050354 | -41.8579 | 3.9001 | -119.0414 | 118.4235 | -0.086975 | 118.8812 | -0.045777 | 0.31128 | -6.189 | -6.2073 | -0.35706 | 0.01831 | 0.45776
1974.5781 | 122.818 | -118.689 | 3.8544 | -0.0054494 | 1.0171e-05 | -0.0050151 | 0.049215 | 0.059662 | 0.0005493 | 0.088694 | 0.041199 | 3.7903 | -0.25635 | -118.7668 | -2.3483 | -2.5314 | -0.045776 | -41.8854 | 3.8727 | -119.0369 | 118.4326 | -0.064087 | 118.7302 | -0.07782 | 0.27008 | -6.2027 | -6.221 | -0.3479 | 0.018311 | 0.29755
1975.5781 | 122.7905 | -118.6935 | 3.8361 | -0.058855 | 0.00236 | -0.0026653 | 0.045797 | 0.057098 | -0.0018005 | 0.085917 | 0.1831 | 3.8086 | -0.24261 | -118.6798 | -2.1423 | -2.504 | -0.27008 | -41.7023 | 3.8635 | -119.0277 | 118.4509 | -0.027466 | 118.8766 | 0.013732 | 0.3479 | -5.9784 | -6.0059 | -0.33417 | 0.027465 | 0.42572
1976.5781 | 122.8775 | -118.7393 | 3.8452 | 0.025068 | 0.0021464 | -0.0060833 | 0.042806 | 0.057739 | -9.1495e-05 | 0.088267 | 0.17395 | 3.8315 | -0.25635 | -118.721 | -2.2659 | -2.4673 | -0.073242 | -41.6611 | 3.8773 | -119.0231 | 118.483 | -0.013733 | 118.9133 | 0.018311 | 0.30212 | -6.1111 | -6.1432 | -0.28381 | 0.032043 | 0.4303
1977.5781 | 122.8088 | -118.7027 | 3.8498 | 0.078474 | 0.0017192 | -0.0018107 | 0.045369 | 0.057526 | -9.1495e-05 | 0.089335 | 0.16479 | 3.8132 | -0.23346 | -118.7668 | -2.2568 | -2.4628 | -0.10529 | -41.6245 | 3.8681 | -119.0414 | 118.4692 | -0.036621 | 118.8675 | -0.064087 | 0.27466 | -6.1066 | -6.1249 | -0.33875 | 0.018311 | 0.39825
1978.5781 | 122.7905 | -118.7164 | 3.8452 | 0.10136 | 0.00236 | -0.0035197 | 0.046224 | 0.05838 | 0.0014039 | 0.087626 | 0.16022 | 3.8223 | -0.24261 | -118.7714 | -2.2705 | -2.4811 | -0.073242 | -41.6382 | 3.8544 | -119.0506 | 118.4738 | -0.022888 | 118.8766 | -0.054931 | 0.27924 | -6.1157 | -6.1249 | -0.33417 | 0.009155 | 0.40283
1979.5781 | 122.8226 | -118.721 | 3.8269 | 0.070845 | 0.004069 | -0.0033061 | 0.044729 | 0.05838 | 0.0001221 | 0.087413 | 0.17853 | 3.7949 | -0.22888 | -118.7485 | -2.243 | -2.4628 | -0.10986 | -41.5833 | 3.8406 | -119.0689 | 118.4921 | -0.032043 | 118.8995 | -0.027466 | 0.32044 | -6.0699 | -6.0837 | -0.3479 | 0.013733 | 0.40741
1980.5781 | 122.7905 | -118.689 | 3.8406 | -0.028338 | 0.0038554 | 0.0020345 | 0.046651 | 0.058807 | -0.0056457 | 0.086344 | 0.17395 | 3.7949 | -0.24719 | -118.6844 | -2.2614 | -2.5726 | -0.082397 | -41.51 | 3.8589 | -119.0369 | 118.4418 | -0.045776 | 118.8629 | 0.004578 | 0.35248 | -6.102 | -6.1203 | -0.3479 | 0.018311 | 0.42114
1981.5781 | 122.7127 | -118.7073 | 3.8269 | 0.063215 | 0.0038554 | -0.0011699 | 0.046651 | 0.059235 | -0.0007325 | 0.087626 | 0.17395 | 3.7903 | -0.24261 | -118.7439 | -2.2247 | -2.4353 | -0.073242 | -41.3727 | 3.8681 | -119.101 | 118.4647 | -0.036621 | 118.8812 | -0.036621 | 0.35706 | -6.0516 | -6.0928 | -0.39368 | 0.041199 | 0.41656
1982.5781 | 122.818 | -118.6981 | 3.8406 | -0.0054494 | 0.0036418 | -0.00095626 | 0.044088 | 0.059448 | -0.0003051 | 0.088481 | 0.19226 | 3.8177 | -0.25177 | -118.7302 | -2.2293 | -2.4353 | -0.073242 | -41.4551 | 3.8544 | -119.0186 | 118.4464 | -0.022888 | 118.8904 | -0.032044 | 0.28839 | -6.0699 | -6.0837 | -0.32044 | 0.013733 | 0.44403
1983.5781 | 122.8363 | -118.7302 | 3.8361 | 0.055586 | 0.0038554 | -0.0026653 | 0.04601 | 0.058166 | -0.0015869 | 0.088908 | 0.21057 | 3.7949 | -0.24719 | -118.7164 | -2.2156 | -2.4445 | -0.082397 | -41.4825 | 3.8818 | -119.0323 | 118.483 | -0.041199 | 118.9407 | 0.013733 | 0.31586 | -6.0516 | -6.0974 | -0.30212 | 0.045776 | 0.45776
1984.5781 | 122.7997 | -118.6844 | 3.8498 | 0.078474 | 0.0032146 | -0.0056559 | 0.044729 | 0.059235 | 0.0016175 | 0.088694 | 0.15106 | 3.804 | -0.25177 | -118.7622 | -2.2156 | -2.4445 | -0.07782 | -41.5009 | 3.8727 | -119.0186 | 118.4326 | -0.045776 | 118.8354 | -0.07782 | 0.25635 | -6.0654 | -6.0883 | -0.33417 | 0.022889 | 0.40283
1985.5781 | 122.7814 | -118.7073 | 3.8681 | 0.17003 | 0.00236 | -0.0026653 | 0.045369 | 0.060303 | -0.0005189 | 0.089335 | 0.14648 | 3.8177 | -0.25635 | -118.7805 | -2.2385 | -2.449 | -0.091553 | -41.4505 | 3.8727 | -119.0048 | 118.4509 | -0.050354 | 118.8538 | -0.073243 | 0.2243 | -6.1066 | -6.1111 | -0.29755 | 0.004578 | 0.40283
1986.5781 | 122.8226 | -118.7119 | 3.8177 | 0.11662 | 0.0036418 | -0.0045879 | 0.043874 | 0.058166 | 0.0041809 | 0.08784 | 0.17853 | 3.8132 | -0.24719 | -118.7393 | -2.211 | -2.4078 | -0.10986 | -41.3773 | 3.8544 | -119.0277 | 118.4647 | -0.004578 | 118.8904 | -0.027466 | 0.28839 | -6.0287 | -6.0654 | -0.31586 | 0.036621 | 0.42572
1987.5781 | 122.7219 | -118.721 | 3.8361 | -0.0054494 | 0.0034282 | -0.0041607 | 0.04601 | 0.056885 | -0.0011597 | 0.086985 | 0.18768 | 3.7765 | -0.23804 | -118.7485 | -2.2156 | -2.4216 | 0.14648 | -41.1804 | 3.8635 | -119.0918 | 118.483 | -0.05951 | 118.9087 | -0.027466 | 0.34332 | -6.0516 | -6.0791 | -0.37079 | 0.027465 | 0.42572
1988.5781 | 122.8226 | -118.6844 | 3.8406 | 0.0098091 | 0.0021464 | -0.0035197 | 0.045369 | 0.059235 | -0.0005189 | 0.089335 | 0.19226 | 3.8086 | -0.24719 | -118.7073 | -2.211 | -2.3941 | -0.064087 | -41.2582 | 3.8727 | -119.0231 | 118.4372 | -0.032043 | 118.8766 | -0.022888 | 0.31586 | -6.0516 | -6.0837 | -0.33875 | 0.032044 | 0.43945
1989.5781 | 122.8317 | -118.6844 | 3.8727 | 0.086103 | 0.0027874 | -0.0022381 | 0.047078 | 0.057953 | -0.0020141 | 0.088481 | 0.18768 | 3.804 | -0.24261 | -118.6844 | -2.211 | -2.3895 | -0.07782 | -41.2628 | 3.8864 | -118.9819 | 118.4418 | -0.068665 | 118.8721 | 0 | 0.29755 | -6.0837 | -6.0974 | -0.29755 | 0.013733 | 0.4303
1990.5781 | 122.8271 | -118.6981 | 3.8589 | 0.13951 | 0.0055644 | -0.0045879 | 0.045369 | 0.059021 | 0.0033265 | 0.088053 | 0.16479 | 3.7994 | -0.24719 | -118.7302 | -2.211 | -2.3941 | -0.10071 | -41.217 | 3.8589 | -119.0094 | 118.4509 | -0.05951 | 118.8629 | -0.032044 | 0.27923 | -6.0699 | -6.0699 | -0.31128 | 0 | 0.41199
1991.5781 | 122.8043 | -118.689 | 3.8773 | 0.2158 | 0.0044962 | -0.0018107 | 0.045369 | 0.060303 | -9.1495e-05 | 0.088908 | 0.12817 | 3.8452 | -0.23804 | -118.7668 | -2.1927 | -2.4033 | -0.082397 | -41.2079 | 3.891 | -119.0002 | 118.4509 | -0.032043 | 118.8171 | -0.07782 | 0.23346 | -6.0699 | -6.0837 | -0.31128 | 0.013733 | 0.36621
1992.5781 | 122.7768 | -118.6981 | 3.8635 | 0.15477 | 0.003001 | -0.0020243 | 0.044729 | 0.057312 | 0.0005493 | 0.08784 | 0.12817 | 3.8086 | -0.25635 | -118.7805 | -2.2156 | -2.4261 | -0.082397 | -41.185 | 3.8818 | -119.014 | 118.4418 | -0.054931 | 118.8263 | -0.082398 | 0.23346 | -6.0791 | -6.0974 | -0.31586 | 0.018311 | 0.38452
1993.5781 | 122.8455 | -118.6798 | 3.8498 | 0.10899 | 0.0044962 | -0.0022381 | 0.043447 | 0.057739 | 0.0022583 | 0.088908 | 0.15106 | 3.8269 | -0.23346 | -118.7302 | -2.1698 | -2.3712 | -0.10529 | -41.0889 | 3.8864 | -119.0002 | 118.4464 | -0.022888 | 118.8309 | -0.050354 | 0.27008 | -6.0196 | -6.0562 | -0.32043 | 0.036622 | 0.38452
1994.5781 | 122.8271 | -118.689 | 3.8452 | 0.063215 | 0.00236 | -0.0037333 | 0.044729 | 0.057953 | 0.0003357 | 0.08784 | 0.19684 | 3.7903 | -0.23804 | -118.6844 | -2.1927 | -2.3666 | -0.068665 | -41.0202 | 3.891 | -118.9774 | 118.4509 | -0.054932 | 118.8858 | 0.004578 | 0.29297 | -6.0379 | -6.0837 | -0.28839 | 0.045776 | 0.43488
1995.5781 | 122.8226 | -118.689 | 3.8635 | 0.093733 | 0.004069 | -0.0033061 | 0.04366 | 0.058166 | -0.0005189 | 0.086985 | 0.18768 | 3.804 | -0.24261 | -118.7027 | -2.2202 | -2.3529 | -0.13275 | -40.9836 | 3.9047 | -118.9865 | 118.4463 | -0.059509 | 118.8766 | -0.013733 | 0.28381 | -6.0837 | -6.1249 | -0.29755 | 0.041199 | 0.4303
1996.5781 | 122.8226 | -118.6798 | 3.8452 | 0.10136 | 0.0034282 | -0.0035197 | 0.044088 | 0.060303 | 0.0018311 | 0.089335 | 0.16479 | 3.8452 | -0.2243 | -118.7256 | -2.1881 | -2.3712 | -0.10529 | -40.9195 | 3.8818 | -119.0231 | 118.4555 | 0 | 118.8446 | -0.045776 | 0.29755 | -6.0333 | -6.0699 | -0.34332 | 0.036621 | 0.3891
1997.5781 | 122.8043 | -118.7027 | 3.8681 | 0.10899 | 0.0036418 | -0.00052906 | 0.044942 | 0.059875 | 0.0005493 | 0.086985 | 0.17853 | 3.8589 | -0.23346 | -118.7027 | -2.1835 | -2.3712 | -0.10986 | -40.9424 | 3.9001 | -119.0048 | 118.4692 | -0.009155 | 118.8812 | 0 | 0.30212 | -6.0516 | -6.0837 | -0.30212 | 0.032043 | 0.41199
1998.5781 | 122.7722 | -118.6935 | 3.8727 | 0.31499 | 0.003001 | -0.0011699 | 0.044515 | 0.058594 | 0.0001221 | 0.08784 | 0.10529 | 3.7857 | -0.27924 | -118.7851 | -2.243 | -2.4307 | -0.073242 | -40.9195 | 3.8773 | -119.0277 | 118.4143 | -0.086975 | 118.7988 | -0.091553 | 0.24262 | -6.1157 | -6.1203 | -0.33417 | 0.004577 | 0.38452
1999.5781 | 122.7676 | -118.6935 | 3.8452 | 0.20817 | 0.00065097 | -0.0050151 | 0.042379 | 0.059021 | 0.0026855 | 0.088267 | 0.10986 | 3.8452 | -0.25177 | -118.7943 | -2.243 | -2.4307 | -0.10986 | -40.9515 | 3.8269 | -119.0598 | 118.4418 | 0 | 118.8034 | -0.10071 | 0.2655 | -6.0883 | -6.0699 | -0.36621 | -0.018311 | 0.36163
2000.5781 | 122.7859 | -118.6935 | 3.8956 | 0.24632 | 0.004069 | -0.0035197 | 0.046865 | 0.06073 | 0.0003357 | 0.088267 | 0.11444 | 3.8315 | -0.23804 | -118.7622 | -2.211 | -2.3895 | -0.064087 | -40.8829 | 3.9139 | -119.0369 | 118.4555 | -0.064087 | 118.808 | -0.068665 | 0.27466 | -6.1066 | -6.1249 | -0.34332 | 0.01831 | 0.35248
2001.5781 | 122.818 | -118.6707 | 3.8589 | 0.14714 | 0.0034282 | -0.0028789 | 0.044729 | 0.059235 | 0.0009765 | 0.087413 | 0.16022 | 3.8315 | -0.2243 | -118.7302 | -2.1606 | -2.3529 | -0.086975 | -40.8371 | 3.8864 | -119.0048 | 118.4463 | -0.027466 | 118.8309 | -0.05951 | 0.27466 | -6.0196 | -6.0471 | -0.33417 | 0.027466 | 0.38452
2002.5781 | 122.8271 | -118.6661 | 3.8727 | 0.15477 | 0.0010784 | -0.0052287 | 0.04302 | 0.057739 | 0.0001221 | 0.087413 | 0.12817 | 3.8635 | -0.25635 | -118.7347 | -2.1881 | -2.3804 | -0.10529 | -40.8279 | 3.9047 | -118.9865 | 118.4097 | -0.009156 | 118.7943 | -0.068664 | 0.25177 | -6.0608 | -6.0928 | -0.32043 | 0.032043 | 0.38452
2003.5781 | 122.7859 | -118.6844 | 3.8727 | 0.20054 | 0.0025736 | -0.0033061 | 0.044088 | 0.059875 | 0.0024719 | 0.088267 | 0.11444 | 3.8361 | -0.25177 | -118.7576 | -2.211 | -2.3849 | -0.086975 | -40.8142 | 3.9185 | -118.9865 | 118.4326 | -0.036621 | 118.7988 | -0.073242 | 0.22888 | -6.0837 | -6.1295 | -0.30212 | 0.045776 | 0.36621
2004.5781 | 122.7722 | -118.6844 | 3.9047 | 0.086103 | 0.0036418 | -0.0026653 | 0.044515 | 0.059448 | -0.0020141 | 0.089762 | 0.10529 | 3.7994 | -0.28839 | -118.7622 | -2.2156 | -2.3941 | -0.07782 | -40.8234 | 3.9047 | -119.0231 | 118.396 | -0.10529 | 118.7897 | -0.07782 | 0.26093 | -6.1203 | -6.1203 | -0.33875 | 0 | 0.39368
2005.5781 | 122.7539 | -118.6844 | 3.8818 | 0.37602 | 0.0036418 | 0.00011194 | 0.047078 | 0.060089 | 0.0014039 | 0.087199 | 0.12817 | 3.8589 | -0.22888 | -118.7851 | -2.2202 | -2.3849 | -0.13275 | -40.7913 | 3.8956 | -118.9911 | 118.4555 | -0.022888 | 118.8126 | -0.10071 | 0.20599 | -6.102 | -6.1157 | -0.3067 | 0.013733 | 0.35706
2006.5781 | 122.7814 | -118.6844 | 3.8727 | 0.24632 | 0.001292 | -0.00010166 | 0.046437 | 0.058594 | 0.0046081 | 0.089762 | 0.1236 | 3.8635 | -0.25177 | -118.7622 | -2.2339 | -2.3987 | -0.091553 | -40.7822 | 3.9139 | -119.0048 | 118.4326 | -0.009156 | 118.808 | -0.07782 | 0.24262 | -6.1066 | -6.1478 | -0.32044 | 0.041198 | 0.37537
2007.5781 | 122.7539 | -118.6569 | 3.8773 | 0.28447 | 0.0049236 | -0.0024517 | 0.044729 | 0.05838 | 0.0001221 | 0.086985 | 0.10529 | 3.8544 | -0.23804 | -118.7668 | -2.2247 | -2.3758 | -0.1236 | -40.7867 | 3.8956 | -119.0002 | 118.4189 | -0.022888 | 118.7622 | -0.10986 | 0.23346 | -6.102 | -6.1203 | -0.34332 | 0.018311 | 0.34332
2008.5781 | 122.7768 | -118.6981 | 3.8361 | 0.2158 | 0.0049236 | -0.0043743 | 0.044942 | 0.058594 | -0.0009461 | 0.086131 | 0.10986 | 3.8315 | -0.26093 | -118.8766 | -2.2293 | -2.4445 | -0.073242 | -40.7455 | 3.8361 | -119.0369 | 118.4372 | -0.004578 | 118.808 | -0.17853 | 0.16022 | -6.0654 | -6.0654 | -0.33875 | 0 | 0.37079
2009.5781 | 122.7722 | -118.6569 | 3.8773 | 0.33024 | 0.0055644 | 0.00032554 | 0.046224 | 0.058166 | -0.0015869 | 0.08784 | 0.12817 | 3.8589 | -0.24719 | -118.7485 | -2.1973 | -2.3575 | -0.10071 | -40.6494 | 3.9139 | -118.9911 | 118.4097 | -0.01831 | 118.7851 | -0.091553 | 0.24262 | -6.0745 | -6.1111 | -0.33417 | 0.036621 | 0.37537
2010.5781 | 122.7585 | -118.6798 | 3.8864 | 0.26158 | 0.005778 | -0.0037333 | 0.045797 | 0.058166 | 0.0007629 | 0.086985 | 0.11444 | 3.8269 | -0.24261 | -118.7897 | -2.1744 | -2.3575 | -0.11444 | -40.7135 | 3.8864 | -119.014 | 118.4372 | -0.05951 | 118.7943 | -0.10986 | 0.2243 | -6.0608 | -6.0608 | -0.33417 | 0 | 0.35706
2011.5781 | 122.7859 | -118.6478 | 3.8727 | 0.3455 | 0.0059916 | 0.00053914 | 0.047933 | 0.060089 | -9.1495e-05 | 0.085704 | 0.16022 | 3.8223 | -0.24261 | -118.7439 | -2.1378 | -2.3392 | -0.18768 | -40.5487 | 3.8773 | -118.9911 | 118.4052 | -0.050354 | 118.808 | -0.09613 | 0.24719 | -6.0104 | -6.015 | -0.34332 | 0.004577 | 0.40283
2012.5781 | 122.7859 | -118.6432 | 3.8773 | 0.45994 | 0.0044962 | -0.00074266 | 0.04836 | 0.059875 | 0.0005493 | 0.089549 | 0.17395 | 3.8269 | -0.23346 | -118.7302 | -2.1194 | -2.298 | -0.1831 | -40.4892 | 3.8864 | -119.0094 | 118.4097 | -0.050354 | 118.8171 | -0.086976 | 0.27923 | -5.9967 | -6.0059 | -0.36621 | 0.009156 | 0.40741
2013.5781 | 122.7676 | -118.6569 | 3.9093 | 0.33787 | 0.003001 | 0.0011799 | 0.047933 | 0.058166 | -9.1495e-05 | 0.088267 | 0.16022 | 3.8681 | -0.24261 | -118.7393 | -2.1149 | -2.3163 | -0.15564 | -40.535 | 3.9368 | -118.9911 | 118.4143 | -0.041199 | 118.8171 | -0.082398 | 0.25177 | -6.0242 | -6.0516 | -0.33417 | 0.027466 | 0.40283
2014.5781 | 122.7859 | -118.6386 | 3.891 | 0.2921 | 0.0055644 | -0.00031526 | 0.047292 | 0.058807 | 0.0001221 | 0.089335 | 0.17395 | 3.8544 | -0.23804 | -118.7393 | -2.1057 | -2.2934 | -0.17395 | -40.4617 | 3.9139 | -118.9957 | 118.4006 | -0.036621 | 118.8126 | -0.10071 | 0.25635 | -5.9967 | -6.0196 | -0.35706 | 0.022888 | 0.41199
2015.5781 | 122.7631 | -118.6661 | 3.891 | 0.31499 | 0.004069 | -0.0028789 | 0.046865 | 0.058807 | 0.0018311 | 0.089335 | 0.12817 | 3.8635 | -0.23804 | -118.7622 | -2.124 | -2.3254 | -0.10529 | -40.4251 | 3.9093 | -118.9957 | 118.428 | -0.027466 | 118.7943 | -0.09613 | 0.23346 | -6.015 | -6.0333 | -0.32959 | 0.018311 | 0.36621
2016.5781 | 122.7493 | -118.6432 | 3.9047 | 0.33024 | 0.0077006 | -0.0020243 | 0.046651 | 0.058594 | 0.0001221 | 0.087626 | 0.14648 | 3.8498 | -0.22888 | -118.7531 | -2.1332 | -2.3071 | -0.13275 | -40.3793 | 3.923 | -119.014 | 118.4143 | -0.054932 | 118.7897 | -0.10986 | 0.26093 | -6.0379 | -6.0562 | -0.37079 | 0.018311 | 0.37537
2017.5781 | 122.7631 | -118.634 | 3.9047 | 0.33024 | 0.0053508 | -0.00095626 | 0.046224 | 0.059875 | 0.0020447 | 0.087413 | 0.16937 | 3.8681 | -0.23804 | -118.7576 | -2.1103 | -2.3026 | -0.15564 | -40.3381 | 3.9093 | -119.0094 | 118.396 | -0.036621 | 118.8034 | -0.1236 | 0.25177 | -6.015 | -6.0196 | -0.37537 | 0.004578 | 0.40741
2018.5781 | 122.7722 | -118.6935 | 3.8223 | 0.45994 | 0.0044962 | -0.0015971 | 0.050069 | 0.060303 | 0.0020447 | 0.087413 | 0.19684 | 3.8361 | -0.25177 | -118.8217 | -2.3346 | -2.4399 | -0.050354 | -40.1688 | 3.8361 | -119.0598 | 118.4418 | 0.013733 | 118.8904 | -0.12817 | 0.23804 | -6.1569 | -6.1707 | -0.36621 | 0.013733 | 0.44861
2019.5781 | 122.818 | -118.6523 | 3.8635 | 0.45231 | 0.0044962 | 0.0016073 | 0.050496 | 0.061371 | 0.0001221 | 0.088481 | 0.19684 | 3.8315 | -0.24261 | -118.721 | -2.1194 | -2.2568 | -0.21973 | -40.242 | 3.8773 | -119.014 | 118.4097 | -0.032043 | 118.8492 | -0.068664 | 0.29297 | -5.983 | -5.9967 | -0.36163 | 0.013733 | 0.43945
2020.5781 | 122.7905 | -118.6935 | 3.8589 | -1.3101 | 0.0044962 | -0.00010166 | 0.047506 | 0.06073 | -9.1495e-05 | 0.088267 | 0.16022 | 3.8086 | -0.26093 | -118.7347 | -2.1149 | -2.2888 | -0.18768 | -40.1688 | 3.8773 | -119.0186 | 118.4326 | -0.050354 | 118.8538 | -0.041199 | 0.28381 | -5.9738 | -5.9921 | -0.32501 | 0.01831 | 0.42114
2021.5781 | 122.7676 | -118.6661 | 3.9047 | 0.37602 | 0.0042826 | 0.0035299 | 0.048574 | 0.060303 | 0.0009765 | 0.091471 | 0.14648 | 3.8589 | -0.25635 | -118.7485 | -2.0187 | -2.2476 | -0.1831 | -40.2557 | 3.9001 | -119.0186 | 118.4097 | -0.045776 | 118.8126 | -0.082397 | 0.27008 | -5.9235 | -5.9189 | -0.35248 | -0.004578 | 0.40283
2022.5781 | 122.7859 | -118.6981 | 3.8681 | 0.37602 | 0.0038554 | 0.0039571 | 0.049215 | 0.060516 | -0.0015869 | 0.08784 | 0.1831 | 3.8269 | -0.24719 | -118.7531 | -2.1515 | -2.2751 | -0.16937 | -40.21 | 3.8864 | -119.0277 | 118.4509 | -0.041199 | 118.8812 | -0.054932 | 0.27466 | -6.0196 | -6.0379 | -0.32959 | 0.018311 | 0.4303
2023.5781 | 122.8043 | -118.6844 | 3.8635 | 0.20054 | 0.0044962 | 0.0022481 | 0.050496 | 0.060089 | 0.0009765 | 0.089335 | 0.16022 | 3.804 | -0.25635 | -118.7531 | -2.1469 | -2.2751 | -0.17853 | -40.2466 | 3.8681 | -119.0369 | 118.428 | -0.059509 | 118.8446 | -0.068665 | 0.28381 | -6.0104 | -6.015 | -0.35248 | 0.004578 | 0.41657
2024.5781 | 122.7997 | -118.6615 | 3.8864 | 1.3907 | 0.0066326 | 0.0016073 | 0.050069 | 0.062652 | -0.0005189 | 0.088694 | 0.032043 | 3.8132 | -0.27466 | -118.721 | -2.1561 | -2.2705 | -0.17853 | -40.0497 | 3.8864 | -119.0277 | 118.3868 | -0.073243 | 118.6935 | -0.059509 | 0.3067 | -6.0425 | -6.0425 | -0.36621 | 0 | 0.3067
2025.5781 | 122.7859 | -118.6707 | 3.8727 | 0.41417 | 0.0049236 | 0.00096634 | 0.051137 | 0.060089 | -0.0015869 | 0.089122 | 0.15564 | 3.8406 | -0.25635 | -118.7302 | -2.1652 | -2.2842 | -0.1831 | -40.123 | 3.8956 | -119.0369 | 118.4143 | -0.032044 | 118.8263 | -0.05951 | 0.3067 | -6.0379 | -6.0608 | -0.36621 | 0.022888 | 0.41199
2026.5781 | 122.8043 | -118.6386 | 3.8452 | 0.4752 | 0.0051372 | 0.00075274 | 0.052205 | 0.062439 | -0.0009461 | 0.088053 | 0.14191 | 3.8498 | -0.27466 | -118.7531 | -2.1835 | -2.3026 | -0.17395 | -40.0955 | 3.9047 | -119.0414 | 118.364 | 0.004577 | 118.7805 | -0.11444 | 0.28839 | -6.0287 | -6.0883 | -0.40283 | 0.059509 | 0.41657
2027.5781 | 122.8226 | -118.6661 | 3.8589 | 0.38365 | 0.0062052 | 0.0020345 | 0.050924 | 0.061798 | -0.0007325 | 0.086985 | 0.18768 | 3.8635 | -0.24261 | -118.7302 | -2.1103 | -2.2568 | -0.2243 | -40.0085 | 3.8773 | -119.0552 | 118.4235 | 0.004577 | 118.8538 | -0.064087 | 0.32501 | -5.9692 | -5.9875 | -0.3891 | 0.01831 | 0.4303
2028.5781 | 122.7997 | -118.6798 | 3.8818 | -1.2338 | 0.0044962 | -0.00074266 | 0.048787 | 0.062439 | 0.0001221 | 0.08784 | 0.15564 | 3.8177 | -0.27008 | -118.7164 | -2.1286 | -2.2659 | -0.18768 | -39.9857 | 3.891 | -119.0186 | 118.4097 | -0.064087 | 118.8355 | -0.036621 | 0.30212 | -6.0104 | -6.0196 | -0.33875 | 0.009155 | 0.42572
2029.5781 | 122.818 | -118.6615 | 3.8635 | 0.42943 | 0.0053508 | 0.0050251 | 0.048787 | 0.057098 | -0.0013733 | 0.088694 | 0.18768 | 3.8406 | -0.24261 | -118.7805 | -2.1744 | -2.2659 | -0.1831 | -40.004 | 3.8864 | -119.0323 | 118.4189 | -0.022888 | 118.8492 | -0.11902 | 0.25177 | -6.0379 | -6.0608 | -0.37079 | 0.022889 | 0.4303
2030.5781 | 122.7768 | -118.6981 | 3.8269 | 0.4218 | 0.0044962 | 0.00011194 | 0.05071 | 0.060516 | 0.0020447 | 0.086344 | 0.20142 | 3.8361 | -0.24719 | -118.721 | -2.3071 | -2.449 | -0.13275 | -39.8712 | 3.8361 | -119.0643 | 118.4509 | 0.009156 | 118.8995 | -0.022888 | 0.34332 | -6.134 | -6.1432 | -0.36621 | 0.009156 | 0.44861
2031.5781 | 122.7493 | -118.6981 | 3.8681 | 0.39128 | 0.0066326 | -0.0013835 | 0.053701 | 0.060944 | 0.0022583 | 0.088694 | 0.20599 | 3.891 | -0.2243 | -118.6935 | -2.1469 | -2.2568 | -0.24261 | -39.9261 | 3.9139 | -119.0186 | 118.4738 | 0.022888 | 118.9041 | 0.004578 | 0.32501 | -6.015 | -6.0608 | -0.32044 | 0.045776 | 0.4303
2032.5781 | 122.7814 | -118.6386 | 3.8956 | 0.45994 | 0.0059916 | 0.00096634 | 0.052633 | 0.060944 | -0.0018005 | 0.08784 | 0.13733 | 3.9047 | -0.25635 | -118.7485 | -2.1744 | -2.3071 | -0.16479 | -39.949 | 3.9368 | -119.0277 | 118.3823 | 0.009155 | 118.7759 | -0.10986 | 0.27924 | -6.0699 | -6.1111 | -0.3891 | 0.041199 | 0.39368
2033.5781 | 122.7585 | -118.6386 | 3.923 | 0.43706 | 0.0079142 | 0.00011194 | 0.051778 | 0.061584 | -0.0005189 | 0.088267 | 0.13275 | 3.9047 | -0.27008 | -118.7531 | -2.179 | -2.3026 | -0.13275 | -39.8895 | 3.9459 | -119.0323 | 118.3685 | -0.018311 | 118.7714 | -0.11444 | 0.27924 | -6.102 | -6.1249 | -0.39368 | 0.022888 | 0.40283
2034.5781 | 122.818 | -114.2807 | 8.2031 | 0.40654 | 0.0059916 | -0.00074266 | 0.046437 | 0.062866 | 0.0018311 | 0.085704 | 0.31128 | 8.2077 | -0.21973 | -114.3677 | -0.86975 | 0.15564 | -0.19684 | -36.5387 | 8.2397 | -114.6606 | 114.061 | 0.004578 | 114.592 | -0.086975 | 0.29297 | -9.0729 | -9.1095 | -0.37994 | 0.036621 | 0.53101
2035.5781 | 122.8088 | -114.4409 | 8.0566 | 0.46757 | 0.005778 | 0.0028889 | 0.048146 | 0.061157 | 0.0011901 | 0.089976 | 0.27924 | 8.0521 | -0.21515 | -114.5233 | -0.90637 | 0.073242 | -0.19226 | -36.6348 | 8.0658 | -114.8071 | 114.2258 | -0.004578 | 114.7202 | -0.082397 | 0.28381 | -8.963 | -8.9722 | -0.36621 | 0.009155 | 0.49438
2036.5781 | 122.7905 | -114.5233 | 7.9926 | 0.40654 | 0.0068462 | 0.0022481 | 0.045156 | 0.061584 | 0.0005493 | 0.089762 | 0.3067 | 7.9788 | -0.2243 | -114.6286 | -1.1215 | -0.11444 | -0.045776 | -36.5112 | 7.9788 | -114.9216 | 114.299 | -0.013733 | 114.83 | -0.10529 | 0.29297 | -9.1141 | -9.1003 | -0.39826 | -0.013733 | 0.53101
2037.5781 | 122.7539 | -114.6057 | 7.9147 | 0.36839 | 0.005778 | 0.0035299 | 0.047506 | 0.061584 | 0.0009765 | 0.089335 | 0.31128 | 7.9193 | -0.21973 | -114.6469 | -1.0117 | -0.013733 | -0.21973 | -36.6806 | 7.9834 | -114.9399 | 114.386 | 0.004578 | 114.917 | -0.041199 | 0.29297 | -8.9264 | -8.9951 | -0.33417 | 0.068664 | 0.53101
2038.5781 | 122.7951 | -114.5279 | 7.9788 | 0.45994 | 0.007487 | 0.0033161 | 0.04601 | 0.060303 | 0.0003357 | 0.08784 | 0.30212 | 7.9376 | -0.21515 | -114.624 | -1.0208 | -0.018311 | -0.21057 | -36.6577 | 7.9788 | -114.9445 | 114.3127 | -0.041199 | 114.83 | -0.09613 | 0.32044 | -8.9996 | -8.9996 | -0.41656 | 0 | 0.51727
2039.5781 | 122.7722 | -114.5554 | 7.9742 | 0.4218 | 0.0077006 | -0.00010166 | 0.048146 | 0.060516 | 0.0035401 | 0.086344 | 0.24719 | 7.9788 | -0.25635 | -114.6744 | -1.1169 | -0.07782 | -0.13733 | -36.6074 | 8.02 | -114.9307 | 114.299 | 0.004578 | 114.8026 | -0.11902 | 0.25635 | -9.0912 | -9.137 | -0.37537 | 0.045777 | 0.50354
2040.5781 | 122.7356 | -114.6286 | 7.9422 | 0.39891 | 0.0068462 | 0.0043843 | 0.048787 | 0.062439 | 0.0018311 | 0.088267 | 0.23346 | 7.9514 | -0.25177 | -114.7339 | -1.181 | -0.13275 | -0.11444 | -36.676 | 7.9788 | -115.0085 | 114.3768 | 0.009155 | 114.8621 | -0.10529 | 0.27466 | -9.1232 | -9.1599 | -0.37994 | 0.036621 | 0.48523
2041.5781 | 122.8226 | -114.5691 | 7.9376 | 0.36076 | 0.0066326 | -0.0015971 | 0.048146 | 0.062012 | 0.0041809 | 0.088908 | 0.30212 | 7.9376 | -0.24261 | -114.6606 | -1.0895 | -0.041199 | -0.19226 | -36.5982 | 7.9742 | -114.9445 | 114.3265 | 0 | 114.8712 | -0.091553 | 0.28381 | -9.0271 | -9.0637 | -0.37537 | 0.036621 | 0.54474
2042.5781 | 122.8043 | -114.5966 | 7.8918 | 0.4218 | 0.0051372 | 0.00053914 | 0.044301 | 0.061584 | 0.0007629 | 0.092112 | 0.31128 | 7.8827 | -0.20142 | -114.9124 | -1.3 | -0.16937 | 0 | -36.5616 | 7.8873 | -115.004 | 114.3951 | -0.009156 | 114.9078 | -0.31586 | 0.091552 | -9.1919 | -9.1873 | -0.40741 | -0.004578 | 0.5127
2043.5781 | 122.818 | -114.6378 | 7.8918 | 0.39891 | 0.0072734 | -0.00052906 | 0.045156 | 0.061798 | 0.0016175 | 0.087413 | 0.31586 | 7.9193 | -0.2243 | -114.6744 | -1.1032 | -0.1831 | -0.21973 | -36.4334 | 7.9239 | -115.0269 | 114.4135 | 0.027466 | 114.9536 | -0.036621 | 0.35248 | -8.9951 | -9.0271 | -0.3891 | 0.032043 | 0.54016
2044.5781 | 122.8271 | -114.5599 | 7.9514 | 0.4218 | 0.0064188 | 0.0018209 | 0.045369 | 0.061584 | 0.0014039 | 0.087626 | 0.31586 | 7.9422 | -0.21515 | -114.6286 | -1.2039 | -0.19226 | -0.21973 | -36.319 | 7.9605 | -114.949 | 114.3448 | -0.009155 | 114.8758 | -0.068664 | 0.32044 | -9.1553 | -9.1644 | -0.3891 | 0.009155 | 0.53101
2045.5781 | 122.7951 | -114.5554 | 7.9559 | 0.4218 | 0.0042826 | 0.00011194 | 0.047292 | 0.062012 | 0.0011901 | 0.087413 | 0.31586 | 7.9376 | -0.21973 | -114.6561 | -1.2405 | -0.2243 | -0.21973 | -36.3968 | 7.9514 | -114.9628 | 114.3356 | -0.018311 | 114.8712 | -0.10071 | 0.3067 | -9.1965 | -9.1919 | -0.40741 | -0.004578 | 0.53558
2046.5781 | 122.7631 | -114.5554 | 7.9742 | 0.43706 | 0.0070598 | -0.00074266 | 0.047719 | 0.062439 | 0.0018311 | 0.087199 | 0.25635 | 7.9605 | -0.24719 | -114.6973 | -1.2772 | -0.2655 | -0.13733 | -36.3556 | 7.9971 | -114.9445 | 114.3082 | -0.013733 | 114.8117 | -0.14191 | 0.24719 | -9.2514 | -9.2743 | -0.3891 | 0.022888 | 0.50354
2047.5781 | 122.7676 | -114.6194 | 7.9102 | 0.45231 | 0.005778 | -0.00010166 | 0.04836 | 0.060516 | 0.0037537 | 0.087413 | 0.22888 | 7.9239 | -0.24261 | -114.7476 | -1.2772 | -0.31128 | -0.12817 | -36.3556 | 7.9422 | -115.0314 | 114.3768 | 0.013733 | 114.8483 | -0.12817 | 0.28381 | -9.1873 | -9.2194 | -0.41199 | 0.032044 | 0.4715
2048.5781 | 122.7951 | -114.5691 | 7.9102 | 0.29973 | 0.0070598 | 0.0016073 | 0.045797 | 0.062225 | 0.0041809 | 0.087626 | 0.31128 | 7.901 | -0.2243 | -114.6698 | -1.2314 | -0.23346 | -0.20599 | -36.264 | 7.933 | -114.9719 | 114.3448 | -0.009155 | 114.8804 | -0.10071 | 0.30212 | -9.1415 | -9.1644 | -0.40283 | 0.022888 | 0.53558
2049.5781 | 122.7997 | -114.5782 | 7.9468 | 0.42943 | 0.0051372 | 0.0016073 | 0.041738 | 0.062652 | 0.0022583 | 0.088908 | 0.33417 | 7.9102 | -0.23346 | -114.6561 | -1.2039 | -0.18768 | -0.19226 | -36.2778 | 7.9697 | -114.9216 | 114.3448 | -0.036621 | 114.9124 | -0.07782 | 0.2655 | -9.1507 | -9.1736 | -0.34332 | 0.022889 | 0.56763
2050.5781 | 122.7814 | -114.5874 | 7.9102 | 0.26158 | 0.0072734 | 0.0022481 | 0.047719 | 0.061584 | 0.0028991 | 0.088053 | 0.30212 | 7.9056 | -0.21973 | -114.6744 | -1.236 | -0.25177 | -0.18768 | -36.1908 | 7.9514 | -115.0085 | 114.3677 | -0.004577 | 114.8895 | -0.086975 | 0.33417 | -9.1461 | -9.1873 | -0.42114 | 0.041199 | 0.52185
2051.5781 | 122.7951 | -114.5554 | 7.9559 | 0.38365 | 0.0064188 | 0.0039571 | 0.046865 | 0.062225 | 0.0061035 | 0.088694 | 0.3067 | 7.9559 | -0.19684 | -114.6423 | -1.3367 | -0.36163 | -0.20599 | -35.9024 | 7.9559 | -114.9673 | 114.3585 | 0 | 114.8621 | -0.086975 | 0.32501 | -9.2926 | -9.2926 | -0.41199 | 0 | 0.50354
2052.5781 | 122.8363 | -114.6332 | 7.869 | 0.45231 | 0.0062052 | 0.0016073 | 0.046224 | 0.062225 | 0.0005493 | 0.089976 | 0.31586 | 7.8964 | -0.2243 | -114.6835 | -1.1719 | -0.2243 | -0.23346 | -36.2091 | 7.9193 | -115.0406 | 114.4089 | 0.027465 | 114.949 | -0.050354 | 0.35706 | -9.0408 | -9.0912 | -0.40741 | 0.050354 | 0.54016
2053.5781 | 122.7722 | -114.5416 | 8.0154 | 0.41417 | 0.0085552 | 0.0011799 | 0.047933 | 0.062225 | 0.0022583 | 0.087626 | 0.26093 | 7.9834 | -0.26093 | -114.6378 | -1.1993 | -0.21515 | -0.16937 | -36.1908 | 8.0017 | -114.9078 | 114.2807 | -0.032044 | 114.8026 | -0.09613 | 0.27008 | -9.2148 | -9.2011 | -0.36621 | -0.013733 | 0.52185
2054.5781 | 122.7951 | -114.6057 | 7.9147 | 0.44468 | 0.0066326 | 0.0016073 | 0.046865 | 0.06308 | 0.0024719 | 0.086558 | 0.26093 | 7.9147 | -0.24261 | -114.7156 | -1.2405 | -0.27008 | -0.14648 | -36.2228 | 7.9376 | -115.0085 | 114.3631 | 0 | 114.8666 | -0.10986 | 0.29297 | -9.1553 | -9.1782 | -0.40283 | 0.022888 | 0.50354
2055.5781 | 122.8088 | -114.4913 | 8.0338 | 0.4218 | 0.005778 | 0.0031025 | 0.045583 | 0.061371 | 0.0026855 | 0.086772 | 0.31586 | 8.0017 | -0.21973 | -114.592 | -1.2177 | -0.20599 | -0.19684 | -36.0443 | 8.02 | -114.8666 | 114.2715 | -0.032043 | 114.8071 | -0.10071 | 0.27466 | -9.2514 | -9.2377 | -0.37537 | -0.013732 | 0.53558
2056.5781 | 122.7951 | -114.5187 | 7.988 | 0.1624 | 0.0051372 | -0.0020243 | 0.045797 | 0.060516 | 0.0028991 | 0.087413 | 0.24719 | 7.9285 | -0.23804 | -114.6149 | -1.2222 | -0.21057 | -0.19226 | -36.0489 | 8.0109 | -114.9124 | 114.2807 | -0.059509 | 114.7659 | -0.09613 | 0.29755 | -9.2102 | -9.2331 | -0.39368 | 0.022888 | 0.48523
2057.5781 | 122.7814 | -114.4775 | 8.0292 | 0.39128 | 0.0081278 | 0.0075887 | 0.04601 | 0.060089 | 0.0026855 | 0.088053 | 0.14191 | 7.9926 | -0.23346 | -114.5416 | -1.1993 | -0.21057 | -0.16937 | -35.9573 | 8.0383 | -114.8621 | 114.2441 | -0.036621 | 114.6194 | -0.064087 | 0.32044 | -9.2285 | -9.2377 | -0.38452 | 0.009155 | 0.37537
2058.5781 | 122.7905 | -114.505 | 8.0246 | 0.43706 | 0.0072734 | 0.0018209 | 0.046651 | 0.062012 | 0.0018311 | 0.085917 | 0.28381 | 7.9834 | -0.21515 | -114.4959 | -1.1627 | -0.23346 | -0.20142 | -35.9024 | 8.0109 | -114.8712 | 114.2899 | -0.041199 | 114.7888 | 0.009155 | 0.37537 | -9.1873 | -9.1736 | -0.36621 | -0.013733 | 0.49896
2059.5781 | 122.8043 | -114.4455 | 8.0475 | 0.39891 | 0.0066326 | 0.0035299 | 0.046651 | 0.060944 | 0.0024719 | 0.086985 | 0.32501 | 8.0383 | -0.20599 | -114.5096 | -1.4099 | -0.32501 | -0.16022 | -35.614 | 8.0612 | -114.8483 | 114.2395 | -0.009155 | 114.7705 | -0.064087 | 0.33874 | -9.4574 | -9.4711 | -0.40283 | 0.013733 | 0.53101
2060.5781 | 122.7814 | -114.4547 | 8.0795 | 0.43706 | 0.01005 | 0.0013935 | 0.047719 | 0.061584 | 0.0020447 | 0.088694 | 0.27924 | 8.0658 | -0.25177 | -114.537 | -1.2177 | -0.21057 | -0.1831 | -35.8383 | 8.0933 | -114.8254 | 114.2029 | -0.013733 | 114.7339 | -0.082397 | 0.28839 | -9.2972 | -9.3109 | -0.37079 | 0.013733 | 0.53101
2061.5781 | 122.7676 | -114.4318 | 8.1299 | 0.44468 | 0.0077006 | -0.00074266 | 0.049001 | 0.06073 | 0.0037537 | 0.086772 | 0.2655 | 8.1299 | -0.21973 | -114.5279 | -1.2222 | -0.1831 | -0.16022 | -35.8749 | 8.1024 | -114.8071 | 114.212 | 0 | 114.6973 | -0.09613 | 0.27924 | -9.3521 | -9.3246 | -0.37537 | -0.027466 | 0.48523
2062.5781 | 122.818 | -114.212 | 8.2672 | 0.42943 | 0.005778 | 0.0013935 | 0.044942 | 0.062439 | 0.0016175 | 0.088908 | 0.33417 | 8.2443 | -0.22888 | -114.3173 | -0.77362 | 0.068665 | -0.21515 | -35.7468 | 8.3038 | -114.624 | 113.9832 | -0.022888 | 114.5462 | -0.10529 | 0.3067 | -9.0408 | -9.0775 | -0.41199 | 0.036621 | 0.56305
2063.5781 | 122.7905 | -114.3448 | 8.1619 | 0.2158 | 0.0034282 | -0.00074266 | 0.045369 | 0.062439 | 0.0035401 | 0.088267 | 0.29755 | 8.1345 | -0.2243 | -114.4318 | -0.84686 | -0.004578 | -0.1831 | -35.8017 | 8.2077 | -114.6881 | 114.1205 | -0.027466 | 114.6423 | -0.086975 | 0.25635 | -9.0088 | -9.0546 | -0.34332 | 0.045777 | 0.52185
2064.5781 | 122.7951 | -114.4547 | 8.0841 | 0.87956 | 0.0059916 | -0.0028789 | 0.042592 | 0.061584 | 0.0016175 | 0.087413 | 0.3067 | 8.0521 | -0.24719 | -114.5187 | -0.8606 | -0.045776 | -0.20142 | -35.8658 | 8.0887 | -114.8117 | 114.2075 | -0.032043 | 114.7614 | -0.064087 | 0.29297 | -8.9447 | -8.9493 | -0.35706 | 0.004578 | 0.55389
2065.5781 | 122.7814 | -114.4913 | 8.0109 | 1.0093 | 0.0062052 | -0.0024517 | 0.04366 | 0.061157 | 0.0020447 | 0.085917 | 0.40283 | 7.9559 | -0.25177 | -114.5828 | -0.75989 | -0.036621 | -0.21973 | -35.8612 | 8.0154 | -114.8849 | 114.2395 | -0.054931 | 114.8941 | -0.091553 | 0.30212 | -8.7708 | -8.7753 | -0.39368 | 0.004578 | 0.6546
2066.5781 | 122.7905 | -114.5142 | 7.9742 | 0.38365 | 0.0055644 | 0.0031025 | 0.045797 | 0.062225 | 0.0018311 | 0.087626 | 0.13733 | 7.933 | -0.21973 | -114.5828 | -0.91553 | -0.1236 | -0.16937 | -35.7971 | 8.0063 | -114.9445 | 114.2944 | -0.041199 | 114.6515 | -0.068665 | 0.36163 | -8.8898 | -8.9218 | -0.4303 | 0.032044 | 0.35706
2067.5781 | 122.818 | -114.5828 | 7.9193 | 0.36839 | 0.0079142 | 0.0018209 | 0.047933 | 0.062225 | 0.0009765 | 0.085917 | 0.3067 | 7.9193 | -0.23804 | -114.6515 | -0.89264 | -0.13275 | -0.21057 | -35.8292 | 7.9514 | -114.9765 | 114.3448 | 0 | 114.8895 | -0.068664 | 0.32501 | -8.812 | -8.844 | -0.39368 | 0.032043 | 0.54474
2068.5781 | 122.8043 | -114.6011 | 7.9239 | 0.4218 | 0.007487 | -0.00031526 | 0.046224 | 0.060516 | 0.0001221 | 0.087413 | 0.32044 | 7.9193 | -0.19684 | -114.8941 | -1.1215 | -0.22888 | -0.022888 | -35.9116 | 7.933 | -114.9719 | 114.4043 | -0.004577 | 114.9216 | -0.29297 | 0.07782 | -9.0454 | -9.0546 | -0.37079 | 0.009155 | 0.51727
2069.5781 | 122.8455 | -93.3426 | 29.0955 | 0.43706 | 0.0070598 | -0.00031526 | 0.026357 | 0.060089 | 0.012085 | 0.083995 | 0.94757 | 29.1321 | -0.10071 | -93.425 | 2.1194 | 10.2722 | -0.54932 | -19.9722 | 29.0955 | -93.7592 | 93.2419 | 0.036621 | 94.2902 | -0.082398 | 0.33417 | -26.976 | -26.976 | -0.41657 | 0 | 1.0483
2070.5781 | 122.7768 | -93.4204 | 29.0771 | 0.36839 | 0.0089824 | -0.0020243 | 0.025289 | 0.061798 | 0.013367 | 0.083567 | 0.90179 | 28.9948 | -0.10529 | -93.5532 | 2.0599 | 10.199 | -0.17395 | -19.8166 | 29.0359 | -93.75 | 93.3151 | -0.082397 | 94.3222 | -0.13275 | 0.19684 | -27.0172 | -26.976 | -0.32959 | -0.041198 | 1.0071
2071.5781 | 122.5891 | -10.762 | 111.0031 | 0.2921 | 0.015177 | 0.00096634 | 0.032766 | 0.059448 | 0.056732 | 0.16282 | 3.2913 | 111.7813 | 0.26093 | -10.7346 | 4.0466 | 46.5225 | -0.13275 | 41.835 | 111.7493 | -11.0779 | 11.0229 | 0.7782 | 14.0533 | 0.027466 | 0.34332 | -106.9565 | -107.7026 | -0.31586 | 0.74616 | 3.0304
2072.5781 | 122.8043 | -7.6218 | 114.6149 | 0.25395 | 0.014964 | 0.0013935 | 0.033834 | 0.063293 | 0.058014 | 0.16538 | 3.4012 | 114.9261 | 0.25635 | -7.4982 | 3.6758 | 47.6303 | -0.16937 | 43.5608 | 114.9078 | -7.9422 | 7.8781 | 0.31128 | 11.0229 | 0.1236 | 0.44403 | -110.939 | -111.232 | -0.32043 | 0.29297 | 3.1448
2073.5781 | 122.7951 | -7.0816 | 115.4617 | 1.7493 | 0.017741 | 0.0016073 | 0.034475 | 0.057953 | 0.0578 | 0.16816 | 3.3371 | 115.4709 | 0.2655 | -6.9397 | 3.4241 | 47.8683 | -0.17853 | 43.4784 | 115.448 | -7.4158 | 7.3471 | 0.009155 | 10.4187 | 0.14191 | 0.47607 | -112.0377 | -112.0239 | -0.33417 | -0.013733 | 3.0716
2074.5781 | 122.7859 | -7.0084 | 115.5579 | 0.39891 | 0.0171 | 0.0035299 | 0.036184 | 0.060516 | 0.058655 | 0.16645 | 3.447 | 115.6036 | 0.27924 | -6.8802 | 3.3737 | 47.8821 | -0.16937 | 43.3823 | 115.5212 | -7.3288 | 7.2876 | 0.045777 | 10.4553 | 0.12817 | 0.44861 | -112.1841 | -112.1475 | -0.32043 | -0.036621 | 3.1677
2075.5781 | 122.8455 | -6.5277 | 115.9149 | 0.41417 | 0.017741 | 0.0024617 | 0.037465 | 0.061798 | 0.059082 | 0.16667 | 3.5294 | 116.0843 | 0.31128 | -6.3766 | 3.4698 | 48.2071 | -0.20142 | 43.5928 | 116.0156 | -6.8344 | 6.839 | 0.16937 | 10.0571 | 0.15106 | 0.45776 | -112.4451 | -112.5458 | -0.3067 | 0.10071 | 3.2181
2076.5781 | 122.7859 | -6.2897 | 116.2399 | 0.4218 | 0.020091 | 0.00096634 | 0.034902 | 0.059448 | 0.060364 | 0.16731 | 3.5248 | 116.2766 | 0.3067 | -6.1661 | 3.4332 | 48.262 | -0.19684 | 43.7531 | 116.2308 | -6.6238 | 6.5964 | 0.036621 | 9.8145 | 0.1236 | 0.45776 | -112.8067 | -112.7975 | -0.33417 | -0.009155 | 3.2181
2077.5781 | 122.7951 | -6.1478 | 116.3635 | 0.39128 | 0.018809 | 0.00011194 | 0.032766 | 0.063507 | 0.058014 | 0.1688 | 3.4195 | 116.3773 | 0.32044 | -5.9875 | 3.3325 | 48.4085 | -0.16937 | 43.6707 | 116.3818 | -6.4819 | 6.4682 | 0.013733 | 9.5673 | 0.16022 | 0.49439 | -113.031 | -113.0493 | -0.33417 | 0.018311 | 3.0991
2078.5781 | 122.7631 | -6.0333 | 116.5237 | 0.40654 | 0.019877 | 0.00075274 | 0.036184 | 0.061798 | 0.059296 | 0.16731 | 3.5248 | 116.629 | 0.28839 | -5.8365 | 3.6713 | 48.4634 | -0.5127 | 43.8629 | 116.5054 | -6.3263 | 6.3217 | 0.10529 | 9.5581 | 0.19684 | 0.48981 | -112.8525 | -112.8342 | -0.29297 | -0.018311 | 3.2364
2079.5781 | 122.7905 | -5.9921 | 116.5512 | 0.42943 | 0.020732 | 0.0054525 | 0.036397 | 0.059235 | 0.06015 | 0.16923 | 3.566 | 116.6107 | 0.32501 | -5.8594 | 3.5797 | 48.6465 | -0.20142 | 43.7164 | 116.5192 | -6.308 | 6.3171 | 0.05951 | 9.5581 | 0.13275 | 0.44861 | -112.9715 | -112.9395 | -0.31586 | -0.032043 | 3.241
2080.5781 | 122.7036 | -5.8868 | 116.6931 | 0.39891 | 0.018168 | -0.00095626 | 0.036611 | 0.061798 | 0.058655 | 0.16966 | 3.5568 | 116.8076 | 0.27466 | -5.7678 | 3.5706 | 48.6832 | -0.091553 | 43.602 | 116.6794 | -6.189 | 6.1615 | 0.11444 | 9.4437 | 0.11902 | 0.42114 | -113.1226 | -113.1088 | -0.30212 | -0.013733 | 3.2822
2081.5781 | 122.6852 | -5.8456 | 116.7435 | 0.28447 | 0.020304 | 0.0011799 | 0.038106 | 0.06308 | 0.059296 | 0.17115 | 3.5843 | 116.8533 | 0.31128 | -5.7449 | 3.5477 | 48.6694 | -0.050354 | 43.5425 | 116.7618 | -6.1432 | 6.1569 | 0.10986 | 9.4299 | 0.10071 | 0.39825 | -113.1958 | -113.2141 | -0.29755 | 0.018311 | 3.273
2082.5781 | 122.7676 | -5.7037 | 116.8442 | 0.4218 | 0.019236 | 0.0018209 | 0.035756 | 0.062439 | 0.060791 | 0.16944 | 3.6575 | 116.9724 | 0.33417 | -5.5573 | 3.6163 | 48.8663 | -0.15106 | 43.7942 | 116.8716 | -5.9967 | 6.0379 | 0.12817 | 9.3613 | 0.14648 | 0.43945 | -113.2278 | -113.2553 | -0.29297 | 0.027466 | 3.3234
2083.5781 | 122.7814 | -5.6763 | 116.8488 | 0.36076 | 0.018168 | -0.00095626 | 0.031911 | 0.060303 | 0.058655 | 0.1703 | 3.6942 | 116.9495 | 0.3479 | -5.5389 | 3.6575 | 48.9899 | -0.18768 | 43.7393 | 116.8488 | -5.9967 | 6.0242 | 0.10071 | 9.3704 | 0.13733 | 0.45776 | -113.1912 | -113.1912 | -0.32043 | 0 | 3.3463
2084.5781 | 122.7768 | -5.5801 | 116.9586 | 0.51335 | 0.020518 | 0.0052387 | 0.037252 | 0.060516 | 0.058655 | 0.17115 | 3.7445 | 117.0639 | 0.37994 | -5.4428 | 3.6804 | 49.086 | -0.1831 | 43.6661 | 116.9495 | -5.8685 | 5.9601 | 0.10529 | 9.3246 | 0.13733 | 0.42572 | -113.2782 | -113.269 | -0.28839 | -0.009155 | 3.3646
2085.5781 | 122.7676 | -5.5801 | 116.9632 | 0.38365 | 0.020732 | 0.0016073 | 0.034047 | 0.062652 | 0.056732 | 0.17115 | 3.7491 | 117.0868 | 0.37079 | -5.4245 | 3.6667 | 49.1364 | -0.14648 | 43.6844 | 116.9815 | -5.8594 | 5.9509 | 0.1236 | 9.3292 | 0.15564 | 0.43487 | -113.2965 | -113.3148 | -0.27924 | 0.01831 | 3.3783
2086.5781 | 122.7539 | -6.5231 | 116.0156 | 0.44468 | 0.022013 | 0.0028889 | 0.03597 | 0.062012 | 0.057587 | 0.17051 | 3.7125 | 116.1438 | 0.34332 | -6.4224 | 3.6667 | 48.7473 | -0.14648 | 42.952 | 116.0248 | -6.8161 | 6.8665 | 0.12817 | 10.2356 | 0.10071 | 0.39368 | -112.3489 | -112.3581 | -0.29297 | 0.009155 | 3.3691
2087.5781 | 122.6761 | -6.3217 | 116.2582 | 0.38365 | 0.020732 | 0.0043843 | 0.039388 | 0.062652 | 0.059723 | 0.16859 | 3.7537 | 116.3773 | 0.39368 | -6.1066 | 3.6896 | 48.7793 | -0.004578 | 43.0847 | 116.3315 | -6.6147 | 6.7154 | 0.11902 | 10.0754 | 0.21515 | 0.50812 | -112.5687 | -112.6419 | -0.29297 | 0.073242 | 3.36
2088.5781 | 122.5571 | -5.8273 | 116.7984 | 0.36839 | 0.0218 | 0.0048115 | 0.039388 | 0.064361 | 0.059296 | 0.16987 | 3.7949 | 116.8945 | 0.41199 | -5.7587 | 3.6209 | 49.1501 | 0.009155 | 43.3044 | 116.8259 | -6.1386 | 6.2393 | 0.09613 | 9.6222 | 0.068665 | 0.37994 | -113.1775 | -113.205 | -0.31128 | 0.027466 | 3.3829
2089.5781 | 122.6578 | -6.1432 | 116.4368 | 0.74223 | 0.022441 | -0.00052906 | 0.035543 | 0.063293 | 0.06015 | 0.1703 | 3.804 | 116.6061 | 0.40741 | -6.0928 | 3.4653 | 48.9532 | -0.022888 | 43.1305 | 116.5054 | -6.4453 | 6.5506 | 0.16937 | 9.9472 | 0.050354 | 0.35248 | -112.9715 | -113.0402 | -0.30212 | 0.068664 | 3.3966
2090.5781 | 122.7036 | -6.1157 | 116.4505 | 0.38365 | 0.020518 | 0.0024617 | 0.036397 | 0.062012 | 0.060364 | 0.17243 | 3.8315 | 116.6061 | 0.4303 | -6.0196 | 3.4744 | 49.0631 | -0.082397 | 43.0252 | 116.4917 | -6.3995 | 6.546 | 0.15564 | 9.9472 | 0.096131 | 0.37994 | -112.9761 | -113.0173 | -0.28381 | 0.041199 | 3.4012
2091.5781 | 122.6669 | -6.0059 | 116.5466 | 0.26921 | 0.021373 | 0.0031025 | 0.036184 | 0.062439 | 0.058655 | 0.17265 | 3.804 | 116.7114 | 0.40741 | -5.9463 | 3.5065 | 49.1501 | -0.036621 | 43.0573 | 116.6107 | -6.3354 | 6.4133 | 0.16479 | 9.8099 | 0.059509 | 0.3891 | -113.0402 | -113.1042 | -0.32959 | 0.064087 | 3.3966
2092.5781 | 122.6715 | -5.983 | 116.597 | 0.95585 | 0.020732 | 0.0013935 | 0.036611 | 0.064789 | 0.059937 | 0.16987 | 3.8223 | 116.7572 | 0.42572 | -5.9006 | 3.5248 | 49.3286 | -0.004578 | 43.1122 | 116.6794 | -6.2714 | 6.4087 | 0.16022 | 9.8053 | 0.082397 | 0.37079 | -113.0722 | -113.1546 | -0.28839 | 0.082397 | 3.3966
2093.5781 | 122.6395 | -5.9784 | 116.6061 | 0.39891 | 0.022227 | 0.0033161 | 0.035329 | 0.066284 | 0.061218 | 0.16902 | 3.8498 | 116.7618 | 0.40283 | -5.7999 | 3.653 | 49.4064 | -0.091553 | 43.1076 | 116.6885 | -6.2759 | 6.3812 | 0.15564 | 9.8282 | 0.17853 | 0.47607 | -112.9532 | -113.0356 | -0.29755 | 0.082398 | 3.447
2094.5781 | 122.6349 | -5.9967 | 116.6107 | 0.23869 | 0.019877 | 0.0020345 | 0.037252 | 0.06543 | 0.05716 | 0.16773 | 3.8498 | 116.748 | 0.37994 | -5.9052 | 3.479 | 49.3332 | 0.018311 | 43.2724 | 116.6794 | -6.2805 | 6.3766 | 0.13733 | 9.8465 | 0.091553 | 0.37537 | -113.1317 | -113.2004 | -0.28381 | 0.068664 | 3.4698
2095.5781 | 122.6395 | -5.9921 | 116.597 | 0.26921 | 0.020518 | 0.00096634 | 0.035756 | 0.06543 | 0.060791 | 0.17051 | 3.8727 | 116.748 | 0.39368 | -5.8914 | 3.5202 | 49.5026 | 0.027466 | 43.7393 | 116.6702 | -6.2714 | 6.3858 | 0.15106 | 9.8648 | 0.10071 | 0.37994 | -113.0768 | -113.15 | -0.27924 | 0.073242 | 3.479
2096.5781 | 122.6395 | -5.9463 | 116.6885 | 0.26921 | 0.019877 | 0.0043843 | 0.037893 | 0.066498 | 0.06015 | 0.17115 | 3.8727 | 116.7801 | 0.39368 | -5.8548 | 3.479 | 49.5621 | 0.07782 | 43.1396 | 116.748 | -6.2347 | 6.34 | 0.091552 | 9.819 | 0.091553 | 0.37994 | -113.2095 | -113.269 | -0.28839 | 0.059509 | 3.479
2097.5781 | 122.6349 | -5.6396 | 116.9495 | 0.36076 | 0.020304 | 0.0082295 | 0.037038 | 0.063293 | 0.058441 | 0.17051 | 3.8727 | 117.1143 | 0.40283 | -5.5481 | 3.5156 | 49.7314 | 0.013733 | 43.7256 | 117.0273 | -5.9372 | 6.0425 | 0.1648 | 9.5123 | 0.091552 | 0.3891 | -113.4338 | -113.5117 | -0.29755 | 0.07782 | 3.4698
2098.5781 | 122.6303 | -5.6992 | 116.9174 | 0.23869 | 0.022868 | 0.00075274 | 0.03597 | 0.064148 | 0.060364 | 0.17179 | 3.9093 | 117.0776 | 0.4303 | -5.6259 | 3.5522 | 49.791 | 0.059509 | 43.7027 | 116.9861 | -5.9875 | 6.1295 | 0.16022 | 9.6085 | 0.073242 | 0.36163 | -113.3652 | -113.4338 | -0.28839 | 0.068665 | 3.479
2099.5781 | 122.6257 | -5.7266 | 116.89 | 0.23869 | 0.022654 | 0.0031025 | 0.037465 | 0.064361 | 0.058869 | 0.17158 | 3.9185 | 117.0273 | 0.41657 | -5.6442 | 3.5889 | 49.8688 | 0.068665 | 43.4143 | 116.954 | -6.0059 | 6.1432 | 0.13733 | 9.6451 | 0.082398 | 0.36163 | -113.3011 | -113.3652 | -0.27923 | 0.064087 | 3.5019
2100.5781 | 122.6303 | -5.5801 | 117.009 | 0.28447 | 0.022013 | 0.00032554 | 0.036824 | 0.064575 | 0.06015 | 0.17094 | 3.9368 | 117.1921 | 0.39368 | -5.4977 | 3.5889 | 49.9969 | 0.036621 | 43.3319 | 117.0959 | -5.8731 | 5.9738 | 0.18311 | 9.5169 | 0.082397 | 0.37537 | -113.4201 | -113.5071 | -0.29297 | 0.086975 | 3.5431
2101.5781 | 122.7036 | -5.4703 | 117.1051 | 0.17003 | 0.022868 | 0.00053914 | 0.038106 | 0.063934 | 0.0578 | 0.17329 | 3.9871 | 117.2333 | 0.40283 | -5.3375 | 3.6438 | 50.1114 | 0.013733 | 43.4189 | 117.1829 | -5.7587 | 5.8731 | 0.12817 | 9.4574 | 0.13275 | 0.42114 | -113.4613 | -113.5391 | -0.28839 | 0.077819 | 3.5843
2102.5781 | 122.6624 | -5.5069 | 117.1051 | 0.1624 | 0.021373 | 0.0026753 | 0.038106 | 0.065002 | 0.061218 | 0.17286 | 3.9963 | 117.2516 | 0.41657 | -5.3787 | 3.6575 | 50.1022 | 0.022888 | 43.5608 | 117.16 | -5.7816 | 5.9235 | 0.14648 | 9.5032 | 0.12817 | 0.40283 | -113.4476 | -113.5025 | -0.27466 | 0.054931 | 3.5797
2103.5781 | 122.6715 | -5.4657 | 117.1143 | 0.17003 | 0.020732 | -0.0011699 | 0.03597 | 0.065216 | 0.06015 | 0.17329 | 4.0237 | 117.2836 | 0.44403 | -5.3558 | 3.6896 | 50.2075 | 0.027466 | 43.5974 | 117.2104 | -5.7861 | 5.9097 | 0.16937 | 9.4894 | 0.10986 | 0.4303 | -113.4247 | -113.5208 | -0.32044 | 0.09613 | 3.5797
2104.5781 | 122.6395 | -5.4977 | 117.1143 | 0.2158 | 0.022227 | 0.0026753 | 0.036824 | 0.064575 | 0.059509 | 0.1735 | 3.9963 | 117.2882 | 0.40741 | -5.3879 | 3.598 | 50.1709 | 0.027466 | 43.4967 | 117.1967 | -5.7678 | 5.9052 | 0.17395 | 9.494 | 0.10986 | 0.37994 | -113.5162 | -113.5986 | -0.27008 | 0.082397 | 3.5889
2105.5781 | 122.6395 | -5.4565 | 117.1326 | 0.19291 | 0.01945 | 0.0018209 | 0.035756 | 0.06607 | 0.059296 | 0.17222 | 4.0146 | 117.2928 | 0.40741 | -5.3513 | 3.5843 | 50.1846 | 0.045776 | 43.5242 | 117.215 | -5.7266 | 5.864 | 0.16022 | 9.4711 | 0.10529 | 0.37537 | -113.5483 | -113.6307 | -0.27008 | 0.082398 | 3.6072
2106.5781 | 122.6532 | -5.4153 | 117.1692 | 0.13188 | 0.020091 | 0.0043843 | 0.037465 | 0.065643 | 0.057373 | 0.17393 | 4.1016 | 117.3477 | 0.46692 | -5.3101 | 3.6301 | 50.4868 | 0.022888 | 43.4326 | 117.2562 | -5.6992 | 5.8823 | 0.17853 | 9.5169 | 0.10529 | 0.3891 | -113.5391 | -113.6261 | -0.28381 | 0.086976 | 3.6346
2107.5938 | 122.731 | -5.3192 | 117.2287 | 0.23106 | 0.019023 | 0.00053914 | 0.028066 | 0.063721 | 0.060364 | 0.1735 | 3.8498 | 117.2745 | 0.47607 | -5.246 | 3.6255 | 50.5508 | -0.050354 | 43.4052 | 117.2607 | -5.6259 | 5.7953 | 0.045776 | 9.169 | 0.073242 | 0.37994 | -113.6032 | -113.6353 | -0.3067 | 0.032043 | 3.3737
2108.5938 | 122.6761 | -5.365 | 117.2699 | 0.10899 | 0.017527 | 0.00096634 | 0.036397 | 0.061371 | 0.057587 | 0.17414 | 4.0924 | 117.3019 | 0.45319 | -5.2277 | 3.5294 | 50.5051 | 0.022888 | 43.3273 | 117.2836 | -5.6259 | 5.8182 | 0.032044 | 9.4574 | 0.13733 | 0.39825 | -113.7405 | -113.7543 | -0.26093 | 0.013733 | 3.6392
2109.5938 | 122.7264 | -5.3146 | 117.1783 | 0.17766 | 0.018382 | -0.0026653 | 0.027425 | 0.061584 | 0.060577 | 0.17393 | 4.097 | 117.3203 | 0.5127 | -5.2048 | 3.6896 | 50.6424 | -0.054932 | 43.808 | 117.2974 | -5.5801 | 5.8273 | 0.14191 | 9.4116 | 0.10986 | 0.37537 | -113.4888 | -113.6078 | -0.2655 | 0.11902 | 3.5843
2110.8125 | 122.7264 | -5.2643 | 117.3294 | -0.013079 | 0.018595 | -0.0041607 | 0.029348 | 0.060089 | 0.059296 | 0.17265 | 4.1885 | 117.3523 | 0.52643 | -5.1407 | 3.6804 | 50.7156 | 0.07782 | 43.7073 | 117.3431 | -5.5389 | 5.7907 | 0.022888 | 9.4528 | 0.1236 | 0.39825 | -113.649 | -113.6627 | -0.27466 | 0.013733 | 3.6621
2111.5781 | 121.7514 | -73.1003 | 48.1888 | 0.2921 | 0.013041 | 0.0018209 | 6.936 | 0.061157 | 0.044983 | 7.0167 | 1.4374 | 48.0835 | -0.013733 | -65.8585 | -28.1982 | 6.8207 | -0.073242 | -4.509 | 45.8267 | -71.5851 | 73.0865 | -0.10529 | 74.5377 | 7.2418 | 5.7266 | -76.387 | -74.025 | 1.5152 | -2.3621 | 1.4511
2112.5781 | 120.5658 | -31.5353 | 89.0991 | 0.45231 | 0.018168 | -0.00052906 | 6.936 | 0.05133 | 0.048187 | 7.0167 | 3.4103 | 88.6688 | 0.32044 | -15.2115 | -2.4261 | 32.2586 | -0.018311 | 35.8246 | 85.7712 | -28.775 | 31.8558 | -0.4303 | 34.9457 | 16.3239 | 13.5635 | -91.5253 | -88.1973 | 2.7603 | -3.3279 | 3.0899
2113.5781 | 120.9549 | -61.6699 | 59.4955 | 0.33787 | 0.012828 | 0.0013935 | 6.936 | 0.034882 | 0.02533 | 7.0167 | -0.07782 | 48.848 | 0.12817 | -1.561 | -0.64545 | 0.009155 | 2.211 | -0.37537 | 55.9982 | -62.2009 | 61.7981 | -10.6476 | 61.5921 | 60.1089 | 60.64 | -60.141 | -56.6437 | -0.53101 | -3.4973 | -0.20599
2114.5781 | 118.6844 | -55.6137 | 62.7686 | 0.39128 | 0.015818 | 0.0045979 | 6.936 | 0.015228 | 0.039215 | 7.0167 | 2.4445 | 62.3932 | 0.15106 | -0.24719 | -0.27008 | 0.082397 | -0.54932 | 0.49896 | 53.2837 | -46.2204 | 55.7648 | -0.37537 | 58.0582 | 55.3665 | 45.9732 | -63.0386 | -53.5538 | 9.3933 | -9.4849 | 2.2934
2115.5781 | 119.4534 | -69.8364 | 49.6902 | 0.84904 | 0.014537 | 0.0037435 | 6.936 | 0.021423 | 0.015717 | 7.0167 | 2.0004 | 48.9487 | -0.059509 | -3.6301 | -2.4399 | 0.059509 | 0.59967 | -1.8951 | 44.902 | -65.7898 | 69.7769 | -0.74158 | 71.8369 | 66.2064 | 62.1597 | -52.1301 | -47.3419 | 4.0466 | -4.7882 | 2.0599
2116.5781 | 120.7306 | -62.4161 | 57.6965 | 0.025068 | 0.013682 | 0.0065205 | 6.936 | 0.026977 | 0.025757 | 7.0167 | 2.2385 | 57.1472 | 0.068665 | -0.4303 | -0.24261 | 0.041199 | 0.25635 | -0.48523 | 56.8497 | -61.203 | 62.4847 | -0.54932 | 64.6545 | 61.9858 | 60.7727 | -57.9391 | -57.0923 | 1.2131 | -0.84686 | 2.1698
2117.5781 | 120.6024 | -83.9859 | 36.3281 | 1.1161 | 0.014323 | 0.00096634 | 6.936 | 0.020355 | 0.018494 | 7.0167 | 1.4191 | 36.3785 | -0.07782 | -9.1599 | -4.7058 | 0.091553 | -0.022888 | -0.16022 | 35.3989 | -82.196 | 83.9081 | 0.050354 | 85.405 | 74.826 | 73.0362 | -41.0339 | -40.1047 | 1.7899 | -0.92926 | 1.4969
2118.5781 | 120.5246 | -78.1448 | 42.5583 | 0.44468 | 0.013682 | 0.0024617 | 6.936 | 0.018433 | -0.0159 | 7.0167 | -2.7878 | 46.2296 | 0.17395 | -8.9447 | -3.2547 | -0.086975 | -1.181 | 20.787 | 45.2866 | -76.8265 | 78.3188 | 3.6713 | 75.3571 | 69.2001 | 67.8818 | -45.813 | -48.5413 | 1.3184 | 2.7283 | -2.9617
2119.5781 | 121.1655 | -120.8405 | 0.25635 | 0.17003 | 0.0077006 | 0.0041707 | 0.046437 | -0.0048523 | -0.0015869 | 0.020762 | 0.041199 | 0.27466 | -0.27008 | 0 | 0 | 0.022888 | 0.009155 | 0.1831 | 0.36621 | -121.2341 | 120.5704 | 0.01831 | 120.8817 | 120.8405 | 121.2341 | -0.25635 | -0.36621 | -0.39368 | 0.10986 | 0.31128
2120.5781 | 121.312 | -120.9824 | 0.29755 | 0.38365 | 0.0053508 | -0.0024517 | 0.045797 | -0.0010071 | -0.0024415 | 0.022898 | -0.036621 | 0.33417 | -0.27924 | -0.050354 | -0.050354 | -0.027466 | -0.032043 | 0.15564 | 0.41657 | -121.3257 | 120.7031 | 0.036621 | 120.9457 | 120.932 | 121.2753 | -0.3479 | -0.46692 | -0.34332 | 0.11902 | 0.24261
2121.5781 | 121.3989 | -121.0281 | 0.34332 | 0.12425 | 0.0049236 | -0.0028789 | 0.045583 | -0.0031433 | -0.0020141 | 0.023112 | 0.054932 | 0.34332 | -0.28839 | 0.013733 | 0 | 0.022888 | 0.004578 | 0.22888 | 0.42572 | -121.376 | 120.7397 | 0 | 121.0831 | 121.0419 | 121.3898 | -0.34332 | -0.42572 | -0.3479 | 0.082397 | 0.34332
2122.5781 | 121.4722 | -121.0693 | 0.36621 | -0.11989 | 0.0081278 | -0.00010166 | 0.045369 | -0.0044251 | -0.0020141 | 0.02183 | 0.009155 | 0.40741 | -0.28839 | -0.013733 | -0.022888 | -0.018311 | 0.082397 | 0.20599 | 0.44403 | -121.4127 | 120.7809 | 0.041199 | 121.0785 | 121.0556 | 121.3989 | -0.3891 | -0.46692 | -0.34332 | 0.07782 | 0.29755
2123.5781 | 121.5042 | -121.0831 | 0.37537 | 0.093733 | 0.0051372 | 0.00053914 | 0.047078 | -0.0037841 | -0.0020141 | 0.022898 | 0.045776 | 0.37079 | -0.3067 | 0.013733 | 0.009155 | 0.018311 | 0.050354 | 0.22888 | 0.45776 | -121.4172 | 120.7764 | -0.004577 | 121.1288 | 121.0968 | 121.431 | -0.36621 | -0.44861 | -0.33417 | 0.082398 | 0.35248
2124.5781 | 121.5317 | -121.0373 | 0.43488 | -0.0054494 | 0.0049236 | -0.0011699 | 0.045156 | -0.0039977 | -0.0028687 | 0.022685 | 0.041199 | 0.42572 | -0.29755 | 0.022888 | 0.009155 | 0.004578 | 0.041199 | 0.22888 | 0.5127 | -121.4264 | 120.7397 | -0.009155 | 121.0785 | 121.0602 | 121.4493 | -0.42572 | -0.50354 | -0.3891 | 0.07782 | 0.33874
2125.5781 | 121.5637 | -121.0556 | 0.43945 | 0.14714 | 0.0059916 | 0.00075274 | 0.045369 | -0.00079352 | -0.0047913 | 0.022685 | 0.050354 | 0.45776 | -0.28381 | 0.018311 | -0.004578 | 0.018311 | 0.013733 | 0.2243 | 0.51727 | -121.4081 | 120.7718 | 0.018311 | 121.106 | 121.0739 | 121.4264 | -0.44403 | -0.52185 | -0.35248 | 0.07782 | 0.33417
2126.5781 | 117.1738 | -65.5701 | 51.4114 | 0.88719 | 0.016673 | 0.0013935 | 6.936 | 0.014374 | 0.0095215 | 7.0167 | 3.186 | 52.3682 | 0.6546 | -1.2222 | -0.1236 | 0.013733 | 0.32501 | 0.46234 | 36.9186 | -51.0269 | 66.2247 | 0.95673 | 68.7561 | 64.3478 | 49.8047 | -51.535 | -37.0422 | 14.5432 | -14.4928 | 2.5314
2127.5781 | 118.3044 | -59.7198 | 59.4818 | 1.0093 | 0.019877 | 0.0033161 | 6.936 | 0.029114 | 0.020203 | 7.0167 | 6.4865 | 66.0507 | 0.33417 | 8.6746 | 2.5406 | 0.004578 | 1.3229 | 9.5261 | 59.9396 | -57.4219 | 60.054 | 6.5689 | 66.2064 | 68.3945 | 66.0965 | -56.9412 | -57.399 | 2.298 | 0.45776 | 6.1523
2128.5781 | 119.4901 | -83.6426 | 35.8841 | 0.96348 | 0.0094096 | 0.0039571 | 6.936 | 0.0051881 | 0.020203 | 7.0167 | 1.4648 | 35.8933 | 0.25177 | -1.6205 | 0.77362 | -0.013733 | -0.19226 | 5.4382 | 34.8679 | -82.3837 | 83.8943 | 0.009156 | 85.1074 | 82.0221 | 80.7632 | -35.1105 | -34.0942 | 1.2588 | -1.0162 | 1.2131
2129.5781 | 121.0419 | -120.7306 | 0.27466 | -0.013079 | 0.0044962 | -0.0013835 | 0.044515 | -0.0033569 | -0.0005189 | 0.023112 | -0.032043 | 0.28839 | -0.32501 | -0.054932 | -0.022888 | -0.022888 | 0.13275 | 0.16022 | 0.35706 | -121.1151 | 120.4056 | 0.013733 | 120.6985 | 120.6757 | 121.0602 | -0.29755 | -0.37994 | -0.38452 | 0.082398 | 0.29297
2130.5781 | 121.1929 | -120.8725 | 0.27924 | -0.42507 | 0.0064188 | -0.0043743 | 0.045797 | -0.0018615 | -0.0013733 | 0.02418 | -0.009155 | 0.32044 | -0.29755 | -0.004578 | -0.022888 | -0.009155 | 0.082397 | 0.17853 | 0.36163 | -121.2433 | 120.575 | 0.041199 | 120.8633 | 120.8679 | 121.2387 | -0.30212 | -0.38452 | -0.37079 | 0.082397 | 0.28839
2131.5781 | 121.2616 | -120.9412 | 0.29297 | -0.020708 | 0.0085552 | -0.0013835 | 0.047506 | -0.0027161 | -0.0018005 | 0.023967 | 0.07782 | 0.27466 | -0.29755 | 0.018311 | 0.013733 | 0.036621 | 0.041199 | 0.20599 | 0.33417 | -121.2708 | 120.6436 | -0.018311 | 121.019 | 120.9595 | 121.2891 | -0.27924 | -0.32043 | -0.32959 | 0.041198 | 0.37537
2132.5781 | 121.3211 | -120.9869 | 0.28381 | 0.055586 | 0.0062052 | 0.00011194 | 0.046437 | -0.0042115 | -0.0030823 | 0.026103 | 0.022888 | 0.26093 | -0.32501 | 0.027466 | 0.013733 | 0.022888 | 0.050354 | 0.20142 | 0.3479 | -121.3348 | 120.6619 | -0.022888 | 121.0098 | 121.0144 | 121.3623 | -0.27008 | -0.33417 | -0.3479 | 0.064087 | 0.3479
2133.5781 | 121.376 | -69.2047 | 49.292 | 0.96348 | 0.017527 | 0.0028889 | 6.936 | 0.038513 | 0.020416 | 7.0167 | 0.32044 | 56.781 | 0.41657 | -30.1666 | -1.68 | -0.032043 | -2.9984 | -9.7458 | 50.766 | -63.3545 | 69.6213 | 7.489 | 69.5251 | 39.0381 | 33.1879 | -50.972 | -52.446 | 5.8502 | 1.474 | -0.09613
2134.5781 | 119.8013 | -81.221 | 37.4176 | 0.75749 | 0.010264 | 0.00075274 | 6.936 | 0.023773 | 0.0090943 | 7.0167 | 1.9501 | 37.175 | 0.073242 | -19.4138 | 0.46234 | 0.032043 | 0.58594 | -8.7296 | 34.3231 | -78.3188 | 81.2942 | -0.24262 | 83.1711 | 61.8073 | 58.905 | -36.9553 | -33.8608 | 2.9022 | -3.0945 | 1.8768
2135.5781 | 119.9753 | -78.5568 | 40.6769 | 0.063215 | 0.0094096 | 0.0016073 | 6.936 | 0.01651 | 0.015717 | 7.0167 | 1.0345 | 40.9973 | 0.082397 | -2.0691 | -0.18768 | 0.009155 | 0.45319 | -1.3092 | 38.9465 | -77.2293 | 78.6392 | 0.32043 | 79.5914 | 76.4877 | 75.1602 | -40.8646 | -39.1342 | 1.3275 | -1.7303 | 0.95215
2136.5781 | 120.6848 | -120.3506 | 0.28839 | -0.035967 | 0.004069 | -0.0052287 | 0.040883 | -0.0054931 | -0.0045777 | 0.018626 | -0.045776 | 0.31586 | -0.32501 | -0.054932 | -0.041199 | -0.036621 | 0.14648 | 0.14648 | 0.37994 | -120.7581 | 120.0256 | 0.027466 | 120.3049 | 120.2957 | 120.7031 | -0.32959 | -0.42114 | -0.40741 | 0.091553 | 0.27924
2137.5781 | 120.9045 | -120.5704 | 0.25177 | -0.028338 | 0.0053508 | 0.0058797 | 0.039174 | -0.0052795 | -0.0018005 | 0.01948 | -0.009155 | 0.25635 | -0.3067 | -0.041199 | -0.041199 | -0.027466 | 0.12817 | 0.16022 | 0.33875 | -120.9869 | 120.2637 | 0.004578 | 120.5612 | 120.5292 | 120.9457 | -0.29297 | -0.37994 | -0.41656 | 0.086975 | 0.29755
2138.5781 | 120.5383 | -120.7123 | 0.25177 | -0.0054494 | 0.0042826 | 0.0024617 | 0.041311 | -0.0052795 | -0.0026551 | 0.01884 | 0.09613 | 0.27924 | -0.27924 | -0.004578 | -0.045776 | -0.018311 | 0.07782 | 0.1831 | 0.3479 | -121.138 | 120.433 | 0.027466 | 120.8084 | 120.7077 | 121.1334 | -0.29755 | -0.39368 | -0.42572 | 0.09613 | 0.37537
2139.5781 | 120.3506 | -120.7855 | 0.29297 | -0.013079 | 0.00471 | -0.00074266 | 0.040456 | -0.0031433 | -0.0039367 | 0.019267 | -0.004578 | 0.26093 | -0.30212 | 0.009155 | 0.091553 | 0.064087 | 0.073242 | 0.11444 | 0.36163 | -121.1288 | 120.4834 | -0.032044 | 120.7809 | 120.7947 | 121.138 | -0.20142 | -0.27008 | -0.34332 | 0.068664 | 0.29755
2140.5781 | 118.5333 | -80.5069 | 37.7701 | -0.0054494 | 0.0094096 | 0.0022481 | 6.936 | 0.0242 | 0.016998 | 7.0167 | 1.9821 | 37.5092 | 0.14191 | -26.9257 | -3.4241 | 0.10071 | 0.91553 | -25.8545 | 30.8716 | -73.6084 | 80.6488 | -0.26093 | 82.489 | 53.5812 | 46.6827 | -41.1942 | -34.2957 | 6.8985 | -6.8985 | 1.8402
2141.5781 | 119.4901 | -92.1478 | 27.9877 | -0.1733 | 0.0079142 | 0.0033161 | 6.936 | -0.011475 | 0.0016175 | 7.0167 | 1.5518 | 29.6356 | -0.032043 | -29.2236 | -0.79651 | 0.15564 | -0.18768 | -8.5648 | 28.1342 | -89.4608 | 92.1158 | 1.6479 | 93.6996 | 62.9242 | 60.2371 | -28.7842 | -28.9307 | 2.6871 | 0.14648 | 1.5839
2142.5781 | 120.2271 | -76.0254 | 43.5013 | 0.025068 | 0.011546 | 0.00011194 | 6.936 | 0.012451 | 0.023621 | 7.0167 | -0.737 | 40.9607 | 0.073242 | -0.81482 | -0.036621 | 0.041199 | -1.0666 | -0.52643 | 39.0564 | -76.2497 | 76.0986 | -2.5406 | 75.2884 | 75.2106 | 75.4349 | -43.5379 | -39.093 | -0.2243 | -4.4449 | -0.81024
2143.5781 | 84.6725 | -94.0567 | 34.0439 | 0.093733 | 0.011546 | 0.0016073 | 6.936 | 0.017151 | 0.0095215 | 5.8249 | -4.2114 | 55.751 | 0.3067 | 0.6134 | 0.13733 | 2.4948 | -12.4878 | 0.37994 | 29.5349 | -104.2511 | 94.3634 | 21.7072 | 89.8453 | 94.6701 | 104.8645 | -33.9066 | -29.3976 | -10.1944 | -4.509 | -4.5181
2144.5781 | 118.3594 | -59.0927 | 45.0714 | -0.043596 | 0.010264 | -0.0033061 | 6.936 | 0.022919 | 0.012085 | 7.0167 | 5.0079 | 61.1206 | 0.22888 | 7.5714 | 2.2018 | 8.5281 | 1.9775 | 14.653 | 54.4739 | -53.1281 | 59.3216 | 16.0492 | 64.1006 | 66.6641 | 60.6995 | -42.8696 | -52.272 | 5.9647 | 9.4025 | 4.7791
2145.5781 | 120.4742 | -118.3136 | 2.0737 | -0.043596 | 0.0051372 | -0.0018107 | 0.68346 | -0.0029297 | -0.0028687 | 0.46083 | 0.32044 | 2.092 | -0.28381 | -0.16937 | -0.036621 | 0.28839 | 0.37079 | 0.26093 | 2.2018 | -118.5699 | 118.0298 | 0.018311 | 118.634 | 118.1442 | 118.4006 | -2.1103 | -2.2385 | -0.25635 | 0.12817 | 0.60425
2146.5781 | 120.7901 | -120.4056 | 0.27466 | -0.013079 | 0.0068462 | -0.0018107 | 0.035543 | -0.0037841 | -0.0035095 | 0.017771 | -0.018311 | 0.25635 | -0.29297 | -0.013733 | -0.032043 | -0.013733 | 0.13733 | 0.17395 | 0.32959 | -120.8359 | 120.1126 | -0.01831 | 120.3873 | 120.3918 | 120.8221 | -0.3067 | -0.36163 | -0.4303 | 0.054932 | 0.27466
2147.5781 | 120.2408 | -120.5978 | 0.23346 | 0.025068 | 0.0070598 | 0.0035299 | 0.039815 | -0.0035705 | -0.0022277 | 0.014781 | 0.022888 | 0.25177 | -0.30212 | 0.018311 | 0 | 0.018311 | 0.054932 | 0.20142 | 0.32044 | -120.9732 | 120.2957 | 0.018311 | 120.6207 | 120.6161 | 120.9915 | -0.23346 | -0.32044 | -0.37537 | 0.086976 | 0.32501
2148.5781 | 120.3369 | -120.6207 | 0.28839 | -0.035967 | 0.0044962 | 0.00053914 | 0.034688 | -0.0042115 | -0.0013733 | 0.01649 | -0.018311 | 0.27466 | -0.31128 | -0.018311 | -0.036621 | -0.013733 | 0.11902 | 0.15564 | 0.36163 | -120.9961 | 120.3094 | -0.013733 | 120.6024 | 120.6024 | 120.9778 | -0.32501 | -0.39825 | -0.37537 | 0.073242 | 0.29297
2149.5781 | 120.5383 | -120.3873 | 0.31586 | -0.12752 | 0.0044962 | -0.0018107 | 0.034902 | -0.0057067 | -0.0043641 | 0.017131 | -0.022888 | 0.30212 | -0.29755 | -0.013733 | -0.027466 | -0.004578 | 0.12817 | 0.1831 | 0.38452 | -121.0236 | 120.0897 | -0.013733 | 120.3644 | 120.3735 | 121.0098 | -0.34332 | -0.41199 | -0.63629 | 0.068664 | 0.27466
2150.5781 | 117.8284 | -76.9272 | 40.7684 | -0.020708 | 0.010264 | -0.0069377 | 6.936 | -0.0052795 | 0.01828 | 7.0167 | 2.1286 | 40.0269 | 0.21057 | 3.5934 | 0.1236 | 9.7458 | -0.018311 | 10.3226 | 32.9224 | -70.0287 | 77.1378 | -0.74158 | 79.0558 | 80.5206 | 73.6221 | -40.6448 | -32.7988 | 6.8985 | -7.8461 | 1.918
2151.5781 | 120.9549 | -120.694 | 0.26093 | -0.035967 | 0.005778 | -0.0013835 | 0.031484 | -0.0059203 | -0.0015869 | 0.011363 | -0.027466 | 0.25635 | -0.3067 | -0.018311 | -0.018311 | -0.018311 | 0.14648 | 0.17395 | 0.31586 | -121.0236 | 120.3873 | -0.004577 | 120.6665 | 120.6757 | 121.0052 | -0.27924 | -0.33417 | -0.32959 | 0.054932 | 0.27924
2152.5781 | 120.5383 | -120.7306 | 0.27466 | -0.31825 | 0.0051372 | 0.0011799 | 0.032979 | -0.0046387 | -0.0013733 | 0.012004 | -0.004578 | 0.31128 | -0.28839 | 0.009155 | -0.027466 | -0.004578 | 0.091553 | 0.1831 | 0.35248 | -121.0876 | 120.4422 | 0.036621 | 120.726 | 120.7397 | 121.0968 | -0.30212 | -0.37994 | -0.35706 | 0.07782 | 0.28381
2153.5781 | 120.5109 | -120.7489 | 0.31586 | -0.37929 | 0.0062052 | -0.0011699 | 0.032979 | -0.0052795 | -0.0030823 | 0.011363 | 0.013733 | 0.33417 | -0.26093 | 0.009155 | -0.036621 | -0.027466 | 0.10071 | 0.17395 | 0.3891 | -121.1151 | 120.488 | 0.01831 | 120.7626 | 120.7581 | 121.1243 | -0.35248 | -0.42572 | -0.36621 | 0.073242 | 0.27466
2154.5781 | 120.5063 | -120.6116 | 0.31128 | -0.028338 | 0.0051372 | -0.00074266 | 0.034475 | -0.0061341 | -0.0007325 | 0.012004 | -0.013733 | 0.33417 | -0.28381 | 0.004578 | -0.036621 | -0.009155 | 0.10986 | 0.15564 | 0.3891 | -121.1426 | 120.3278 | 0.022888 | 120.5978 | 120.6161 | 121.1472 | -0.3479 | -0.42572 | -0.53101 | 0.07782 | 0.27008
2155.5781 | 120.5841 | -120.5475 | 0.32501 | 0.20054 | 0.0049236 | -0.00074266 | 0.034688 | -0.0048523 | -0.0045777 | 0.014567 | -0.009155 | 0.32501 | -0.27466 | -0.009155 | -0.027466 | 0.013733 | 0.09613 | 0.16937 | 0.3891 | -121.1197 | 120.2728 | 0 | 120.5383 | 120.5383 | 121.1105 | -0.35248 | -0.41656 | -0.57221 | 0.064087 | 0.2655
2156.5781 | 120.7397 | -120.7443 | 0.33417 | -0.058855 | 0.0049236 | -0.00031526 | 0.034261 | -0.0037841 | -0.0018005 | 0.014994 | -0.022888 | 0.30212 | -0.30212 | -0.018311 | -0.027466 | -0.013733 | 0.15106 | 0.15564 | 0.38452 | -121.1563 | 120.4422 | -0.032043 | 120.7214 | 120.726 | 121.138 | -0.36163 | -0.41199 | -0.41199 | 0.050354 | 0.27924
2157.5781 | 120.8359 | -120.7581 | 0.32501 | -0.058855 | 0.00471 | -0.0013835 | 0.030843 | -0.0054931 | -0.0024415 | 0.012217 | -0.027466 | 0.29755 | -0.29755 | -0.004578 | -0.045776 | -0.018311 | 0.14648 | 0.16479 | 0.40283 | -121.2341 | 120.4605 | -0.027466 | 120.7306 | 120.7535 | 121.2296 | -0.37079 | -0.44861 | -0.47607 | 0.07782 | 0.27008
2158.5781 | 120.7718 | -120.6024 | 0.31586 | 0.13951 | 0.0066326 | 0.0020345 | 0.034688 | -0.0022889 | -0.0026551 | 0.013713 | -0.004578 | 0.32959 | -0.29297 | -0.004578 | -0.027466 | -0.009155 | 0.10529 | 0.16937 | 0.37994 | -121.2067 | 120.3094 | 0.013733 | 120.5978 | 120.5978 | 121.2021 | -0.34332 | -0.40741 | -0.60425 | 0.064087 | 0.28839
2159.5781 | 120.6802 | -120.5246 | 0.33417 | 0.025068 | 0.00471 | -0.0022381 | 0.03832 | -0.0018615 | -0.0015869 | 0.012858 | 0.041199 | 0.32044 | -0.3067 | 0.054932 | 0.009155 | 0.045776 | 0.054932 | 0.20599 | 0.39825 | -121.1975 | 120.2179 | -0.013732 | 120.5658 | 120.5795 | 121.2524 | -0.32501 | -0.3891 | -0.67291 | 0.064087 | 0.3479
2160.5781 | 120.7901 | -120.6116 | 0.34332 | 0.017439 | 0.0053508 | 0.0016073 | 0.035329 | -0.0031433 | -0.0018005 | 0.012431 | 0.036621 | 0.3479 | -0.29755 | 0.050354 | 0.004578 | 0.027466 | 0.050354 | 0.19226 | 0.44403 | -121.2387 | 120.314 | 0.004577 | 120.6482 | 120.6619 | 121.2891 | -0.33874 | -0.43945 | -0.62714 | 0.10071 | 0.33417
2161.5781 | 120.9595 | -120.7489 | 0.37079 | 0.10136 | 0.0079142 | 0.0033161 | 0.035543 | -0.0025025 | -0.0039367 | 0.014354 | 0.054932 | 0.35706 | -0.31128 | 0.036621 | 0.013733 | 0.027466 | 0.054932 | 0.20599 | 0.42572 | -121.257 | 120.4376 | -0.013733 | 120.8038 | 120.7855 | 121.2936 | -0.35706 | -0.41199 | -0.50812 | 0.054931 | 0.36621
2162.5781 | 121.0739 | -120.9 | 0.3479 | 0.0098091 | 0.0070598 | 0.0022481 | 0.035543 | -0.0014343 | -0.0009461 | 0.012858 | 0.045776 | 0.32501 | -0.29297 | 0.054932 | 0.013733 | 0.041199 | 0.059509 | 0.21515 | 0.42572 | -121.3074 | 120.607 | -0.022888 | 120.9457 | 120.9549 | 121.3623 | -0.33417 | -0.41199 | -0.40741 | 0.07782 | 0.33874
2163.5781 | 121.3165 | -120.9229 | 0.35706 | -0.11226 | 0.0042826 | -0.0011699 | 0.035543 | -0.0031433 | -0.0032959 | 0.013926 | 0.009155 | 0.37537 | -0.3067 | 0.004578 | -0.009155 | 0 | 0.11902 | 0.18768 | 0.4303 | -121.3257 | 120.6162 | 0.01831 | 120.932 | 120.9274 | 121.3303 | -0.36621 | -0.43945 | -0.40283 | 0.073242 | 0.31586
2164.5781 | 121.3577 | -120.9549 | 0.36621 | -0.074114 | 0.0059916 | 0.00011194 | 0.034475 | -0.0048523 | -0.0037231 | 0.015208 | -0.004578 | 0.35706 | -0.31128 | -0.022888 | -0.004578 | 0.009155 | 0.10529 | 0.17395 | 0.42572 | -121.3303 | 120.6436 | -0.009155 | 120.9503 | 120.932 | 121.3074 | -0.37079 | -0.4303 | -0.37537 | 0.059509 | 0.3067
2165.5781 | 121.3531 | -120.9686 | 0.37537 | 0.0021796 | 0.0059916 | 0.0031025 | 0.036184 | -0.0029297 | -0.0022277 | 0.013926 | 0.041199 | 0.35706 | -0.32044 | 0.041199 | 0.018311 | 0.045776 | 0.050354 | 0.20142 | 0.43488 | -121.3348 | 120.6482 | -0.01831 | 121.0098 | 121.0098 | 121.376 | -0.35705 | -0.41656 | -0.36621 | 0.059509 | 0.36163
2166.5781 | 121.3715 | -120.9457 | 0.39825 | 0.17003 | 0.005778 | 0.0045979 | 0.036611 | -0.0031433 | 0.0020447 | 0.013926 | 0.050354 | 0.37079 | -0.28839 | 0.12817 | 0.027466 | 0.10529 | 0 | 0.20142 | 0.47607 | -121.2982 | 120.6573 | -0.027465 | 120.9961 | 121.0739 | 121.4264 | -0.37079 | -0.44861 | -0.35248 | 0.07782 | 0.33875
2167.5781 | 121.4264 | -120.9732 | 0.38452 | 0.20054 | 0.0085552 | 0.00032554 | 0.037679 | -0.0012207 | -0.0024415 | 0.012217 | 0.064087 | 0.3479 | -0.29755 | 0.07782 | 0.032043 | 0.050354 | 0.009155 | 0.24261 | 0.46234 | -121.3669 | 120.6757 | -0.036621 | 121.0373 | 121.051 | 121.4447 | -0.35248 | -0.4303 | -0.39368 | 0.07782 | 0.36163
2168.5781 | 121.4355 | -121.0281 | 0.37079 | 0.17766 | 0.005778 | 0.0024617 | 0.037465 | -0.0044251 | -0.0032959 | 0.014567 | 0.059509 | 0.3479 | -0.28839 | 0.041199 | 0.013733 | 0.059509 | 0 | 0.21057 | 0.45319 | -121.3989 | 120.7397 | -0.022889 | 121.0876 | 121.0693 | 121.4401 | -0.35706 | -0.43945 | -0.37079 | 0.082397 | 0.3479
2169.5781 | 121.4539 | -121.0281 | 0.33875 | 0.14714 | 0.0053508 | -0.00052906 | 0.038747 | -0.0025025 | -0.0018005 | 0.013285 | 0.16937 | 0.36621 | -0.23804 | 0.050354 | 0 | 0.045776 | 0.004578 | 0.21515 | 0.42572 | -121.3943 | 120.7901 | 0.027466 | 121.1975 | 121.0785 | 121.4447 | -0.33875 | -0.42572 | -0.36621 | 0.086975 | 0.40741
2170.5781 | 121.4996 | -121.0785 | 0.32044 | 0.086103 | 0.0064188 | -0.00010166 | 0.037893 | -0.0035705 | -0.0041503 | 0.014781 | 0.045776 | 0.33875 | -0.29297 | 0.022888 | 0.013733 | 0.036621 | 0.045776 | 0.20599 | 0.40283 | -121.4539 | 120.7855 | 0.01831 | 121.1243 | 121.1014 | 121.4767 | -0.3067 | -0.3891 | -0.37537 | 0.082397 | 0.33874
2171.5781 | 121.5042 | -121.0739 | 0.31586 | 0.070845 | 0.0062052 | 0.0016073 | 0.037252 | -0.0044251 | -0.0022277 | 0.012217 | 0.050354 | 0.33875 | -0.28381 | 0.022888 | 0.013733 | 0.054932 | 0.050354 | 0.21515 | 0.39825 | -121.4813 | 120.7901 | 0.022888 | 121.1243 | 121.0968 | 121.5042 | -0.30212 | -0.38452 | -0.40741 | 0.082397 | 0.33417
2172.5781 | 121.4676 | -121.1288 | 0.31586 | 0.2158 | 0.0062052 | 0.0013935 | 0.039388 | -0.0042115 | -0.0009461 | 0.015208 | 0.009155 | 0.32044 | -0.30212 | -0.032043 | -0.050354 | -0.027466 | 0.022888 | 0.13733 | 0.37537 | -121.5134 | 120.8267 | 0.004578 | 121.138 | 121.0968 | 121.4813 | -0.36621 | -0.42572 | -0.38452 | 0.059509 | 0.31128
2173.5781 | 121.4859 | -121.1517 | 0.31128 | 0.20054 | 0.0066326 | 0.0031025 | 0.038106 | -0.0025025 | -0.0028687 | 0.013285 | 0.018311 | 0.29755 | -0.30212 | -0.041199 | -0.045776 | -0.013733 | 0.022888 | 0.12817 | 0.36163 | -121.5454 | 120.8496 | -0.013733 | 121.17 | 121.1105 | 121.5042 | -0.35705 | -0.40741 | -0.39368 | 0.050354 | 0.32044
2174.5781 | 121.4676 | -121.1563 | 0.30212 | 0.38365 | 0.0072734 | 0.0022481 | 0.037038 | -0.0016479 | -0.0028687 | 0.012645 | 0.004578 | 0.3067 | -0.28381 | -0.050354 | -0.045776 | -0.004578 | 0 | 0.11444 | 0.36163 | -121.5317 | 120.8725 | 0.004578 | 121.1609 | 121.106 | 121.4813 | -0.3479 | -0.40741 | -0.37537 | 0.059509 | 0.28839
2175.5781 | 121.55 | -121.1655 | 0.29297 | 0.22343 | 0.0085552 | -0.00052906 | 0.036824 | -0.0025025 | -0.0026551 | 0.014354 | 0.054932 | 0.31586 | -0.27466 | 0.009155 | -0.004578 | 0.027466 | 0.013733 | 0.19226 | 0.35706 | -121.6003 | 120.8908 | 0.022888 | 121.2204 | 121.1746 | 121.6095 | -0.29755 | -0.36163 | -0.43488 | 0.064087 | 0.32959
2176.5781 | 121.4905 | -121.225 | 0.31586 | 0.27684 | 0.005778 | 0.0024617 | 0.038106 | -0.0016479 | -0.0032959 | 0.013285 | 0 | 0.30212 | -0.3067 | -0.045776 | -0.041199 | -0.009155 | 0.050354 | 0.12817 | 0.36621 | -121.6232 | 120.9183 | -0.013733 | 121.225 | 121.1792 | 121.5775 | -0.35706 | -0.40741 | -0.39825 | 0.050354 | 0.3067
2177.5781 | 121.5454 | -121.2112 | 0.27008 | 0.17766 | 0.0070598 | -0.00095626 | 0.038961 | -0.0025025 | -0.0018005 | 0.014567 | 0.045776 | 0.32501 | -0.2655 | 0.018311 | 0 | 0.022888 | 0.013733 | 0.17853 | 0.35706 | -121.6095 | 120.9457 | 0.054931 | 121.257 | 121.2296 | 121.6278 | -0.27008 | -0.35706 | -0.39825 | 0.086975 | 0.31128
2178.5781 | 121.5775 | -121.2204 | 0.28839 | 0.13951 | 0.0079142 | -0.0020243 | 0.040242 | -0.0039977 | -0.0041503 | 0.014994 | 0.045776 | 0.3067 | -0.2655 | 0.004578 | 0.009155 | 0.027466 | 0.004578 | 0.1831 | 0.3479 | -121.6187 | 120.9549 | 0.018311 | 121.2662 | 121.225 | 121.6232 | -0.27924 | -0.33874 | -0.39825 | 0.059509 | 0.31128
2179.5781 | 121.5683 | -121.257 | 0.27008 | 0.26921 | 0.0053508 | -0.0011699 | 0.040242 | -0.0012207 | -0.0028687 | 0.014994 | 0 | 0.27924 | -0.27924 | -0.045776 | -0.068665 | -0.013733 | 0.022888 | 0.13275 | 0.35706 | -121.6553 | 120.9778 | 0.009155 | 121.257 | 121.2112 | 121.6095 | -0.33875 | -0.42572 | -0.39825 | 0.086975 | 0.27924
2180.5781 | 121.4996 | -121.2158 | 0.29297 | 0.39891 | 0.0089824 | -0.0015971 | 0.038106 | -0.0022889 | -0.0043641 | 0.014567 | 0 | 0.28381 | -0.31586 | -0.032043 | -0.059509 | -0.009155 | 0 | 0.12817 | 0.34332 | -121.6599 | 120.9 | -0.009156 | 121.2158 | 121.1838 | 121.6278 | -0.35248 | -0.40283 | -0.44403 | 0.050354 | 0.31586
2181.5781 | 121.5866 | -121.2891 | 0.28839 | 0.36076 | 0.007487 | 0.0054525 | 0.03832 | -0.0052795 | -0.0018005 | 0.016276 | 0 | 0.29297 | -0.30212 | -0.050354 | -0.064087 | -0.018311 | -0.009155 | 0.12817 | 0.37537 | -121.6873 | 120.9869 | 0.004578 | 121.2891 | 121.2387 | 121.637 | -0.35248 | -0.43945 | -0.39825 | 0.086975 | 0.30212
2182.5781 | 121.582 | -121.3074 | 0.27466 | 0.30736 | 0.0068462 | 0.0028889 | 0.037465 | -0.0031433 | 0.0003357 | 0.014781 | -0.032043 | 0.28381 | -0.31128 | -0.041199 | -0.059509 | -0.032043 | 0 | 0.1236 | 0.3479 | -121.7056 | 120.9961 | 0.009155 | 121.2753 | 121.2662 | 121.6644 | -0.33417 | -0.40741 | -0.39825 | 0.073242 | 0.27924
2183.5781 | 121.582 | -121.3165 | 0.29755 | 0.33024 | 0.0059916 | 0.0016073 | 0.038961 | -0.0031433 | -0.0015869 | 0.015208 | -0.027466 | 0.29297 | -0.29755 | -0.036621 | -0.059509 | -0.018311 | -0.009155 | 0.12817 | 0.34332 | -121.6827 | 121.019 | -0.004577 | 121.2891 | 121.2799 | 121.6461 | -0.35705 | -0.40283 | -0.36621 | 0.045777 | 0.27008
2184.5781 | 121.6415 | -121.3165 | 0.24719 | 0.23869 | 0.0066326 | 0.0024617 | 0.037679 | -0.0039977 | -0.0015869 | 0.014781 | 0.013733 | 0.27466 | -0.29755 | -0.013733 | -0.041199 | -0.009155 | 0.027466 | 0.15106 | 0.32959 | -121.7468 | 121.019 | 0.027466 | 121.3303 | 121.3028 | 121.7331 | -0.28839 | -0.37079 | -0.4303 | 0.082398 | 0.31128
2185.5781 | 121.6415 | -121.3211 | 0.27008 | 0.23106 | 0.01005 | 0.0018209 | 0.040029 | -0.0022889 | -0.0020141 | 0.014567 | 0.032043 | 0.2655 | -0.28839 | -0.022888 | -0.045776 | -0.004578 | 0.027466 | 0.16022 | 0.34332 | -121.7468 | 121.0327 | -0.004578 | 121.3531 | 121.2982 | 121.7239 | -0.31586 | -0.3891 | -0.42572 | 0.073242 | 0.32043
2186.5938 | 121.7834 | -121.2753 | 0.26093 | 0.070845 | 0.00236 | -0.0022381 | 0.026998 | -0.0072021 | -0.0018005 | 0.015422 | 0.027466 | 0.23804 | -0.24719 | 0.07782 | 0.09613 | 0.15106 | -0.086975 | 0.30212 | 0.32501 | -121.6507 | 121.0281 | -0.022888 | 121.3028 | 121.3531 | 121.7285 | -0.1648 | -0.22888 | -0.37537 | 0.064087 | 0.27466
2187.5781 | 121.6965 | -121.3165 | 0.29297 | 0.36839 | 0.0083416 | -0.00010166 | 0.039602 | -0.0037841 | -0.0013733 | 0.017344 | -0.009155 | 0.28839 | -0.29297 | -0.10529 | -0.16937 | 0.086975 | 0.1236 | 0.059509 | 0.37994 | -121.7468 | 121.0236 | -0.004578 | 121.3074 | 121.2112 | 121.6415 | -0.46234 | -0.54932 | -0.4303 | 0.086975 | 0.28381
2188.5781 | 121.7422 | -121.3303 | 0.31128 | 0.38365 | 0.0059916 | -0.00052906 | 0.037252 | -0.0048523 | -0.0022277 | 0.013713 | 0.004578 | 0.27466 | -0.29297 | -0.022888 | -0.073242 | -0.004578 | -0.004578 | 0.059509 | 0.36163 | -121.7239 | 121.0373 | -0.036621 | 121.3348 | 121.3074 | 121.7011 | -0.38452 | -0.43488 | -0.39368 | 0.050354 | 0.29755
2189.5781 | 121.6736 | -121.3394 | 0.26093 | 0.35313 | 0.0077006 | 0.0026753 | 0.038747 | -0.0039977 | -0.0024415 | 0.014781 | -0.004578 | 0.27924 | -0.31128 | -0.036621 | -0.054932 | -0.036621 | -0.018311 | 0.1236 | 0.34332 | -121.7926 | 121.0281 | 0.018311 | 121.3348 | 121.3028 | 121.756 | -0.31586 | -0.39825 | -0.45319 | 0.082398 | 0.3067
2190.5781 | 121.6782 | -121.4035 | 0.28839 | 0.36839 | 0.0068462 | 0.00011194 | 0.040242 | -0.0025025 | -0.0028687 | 0.015635 | -0.013733 | 0.28839 | -0.29297 | -0.032043 | -0.041199 | -0.027466 | 0 | 0.13275 | 0.37079 | -121.7834 | 121.1105 | 0 | 121.3898 | 121.3715 | 121.7514 | -0.32959 | -0.41199 | -0.37994 | 0.082398 | 0.27924
2191.5781 | 121.7056 | -121.4081 | 0.27008 | 0.22343 | 0.004069 | 0.0013935 | 0.039602 | -0.0050659 | -0.0011597 | 0.014781 | 0.013733 | 0.28839 | -0.3067 | -0.022888 | -0.045776 | -0.027466 | 0.022888 | 0.15106 | 0.33875 | -121.8155 | 121.1014 | 0.01831 | 121.4218 | 121.3852 | 121.7926 | -0.31586 | -0.38452 | -0.40741 | 0.068664 | 0.32043
2192.5781 | 121.6736 | -121.3989 | 0.28381 | 0.29973 | 0.0079142 | 0.00032554 | 0.037893 | -0.0031433 | -0.0026551 | 0.014567 | -0.022888 | 0.27924 | -0.31586 | -0.027466 | -0.068665 | -0.036621 | 0.036621 | 0.11902 | 0.35706 | -121.8018 | 121.0831 | -0.004577 | 121.376 | 121.3715 | 121.7743 | -0.35248 | -0.42572 | -0.40283 | 0.073243 | 0.29297
2193.5781 | 121.7148 | -121.4127 | 0.29297 | 0.41417 | 0.0064188 | 0.0022481 | 0.037038 | -0.0025025 | -0.0024415 | 0.017131 | -0.009155 | 0.28381 | -0.29297 | -0.041199 | -0.16479 | -0.1236 | 0.21973 | 0.19684 | 0.36621 | -121.8292 | 121.1197 | -0.009156 | 121.4035 | 121.3715 | 121.788 | -0.45776 | -0.53101 | -0.41656 | 0.073242 | 0.28381
2194.5781 | 121.6599 | -121.3531 | 0.29297 | 0.38365 | 0.0087688 | 0.0022481 | 0.037679 | -0.0039977 | -0.0003051 | 0.014354 | -0.013733 | 0.28381 | -0.3067 | -0.027466 | -0.059509 | -0.009155 | -0.009155 | 0.1236 | 0.36163 | -121.8246 | 121.0464 | -0.009156 | 121.3394 | 121.3257 | 121.7972 | -0.35248 | -0.42114 | -0.4715 | 0.068664 | 0.29297
2195.5781 | 121.7148 | -121.4081 | 0.27466 | 0.32261 | 0.0087688 | 0.0011799 | 0.03832 | -0.0037841 | 0.0001221 | 0.014994 | -0.027466 | 0.27466 | -0.3067 | -0.032043 | -0.059509 | -0.009155 | -0.013733 | 0.14191 | 0.34332 | -121.8567 | 121.1014 | 0 | 121.3806 | 121.376 | 121.8246 | -0.33417 | -0.40283 | -0.44861 | 0.068665 | 0.27924
2196.5781 | 121.7377 | -121.431 | 0.28381 | 0.28447 | 0.0049236 | 0.0048115 | 0.037679 | -0.0037841 | -0.0013733 | 0.013072 | -0.032043 | 0.29755 | -0.31128 | -0.045776 | -0.045776 | -0.009155 | 0.018311 | 0.10529 | 0.34332 | -121.8475 | 121.1197 | 0.013733 | 121.3989 | 121.3852 | 121.8018 | -0.32959 | -0.3891 | -0.41656 | 0.05951 | 0.27924
2197.5781 | 121.7056 | -121.4493 | 0.28839 | 0.28447 | 0.0049236 | 0.0045979 | 0.038533 | -0.0027161 | -0.0022277 | 0.014781 | -0.018311 | 0.26093 | -0.32501 | -0.050354 | -0.059509 | -0.032043 | 0.013733 | 0.13733 | 0.3479 | -121.843 | 121.1243 | -0.027466 | 121.431 | 121.3989 | 121.7926 | -0.3479 | -0.40741 | -0.39368 | 0.059509 | 0.3067
2198.5781 | 121.756 | -121.4447 | 0.25177 | 0.20817 | 0.0049236 | 0.00096634 | 0.038106 | -0.0031433 | -0.0028687 | 0.015208 | 0.041199 | 0.25635 | -0.27924 | -0.018311 | -0.022888 | 0.013733 | 0.009155 | 0.15564 | 0.33417 | -121.8796 | 121.1655 | 0.004578 | 121.4859 | 121.4264 | 121.8613 | -0.27466 | -0.35706 | -0.43488 | 0.082397 | 0.32043
2199.5781 | 121.756 | -121.4539 | 0.28381 | 0.25395 | 0.0053508 | -0.0018107 | 0.039815 | -0.0018615 | -0.0015869 | 0.013285 | -0.018311 | 0.27466 | -0.31128 | -0.036621 | -0.050354 | -0.027466 | 0.045776 | 0.11902 | 0.3479 | -121.8704 | 121.1426 | -0.009155 | 121.4355 | 121.4172 | 121.8338 | -0.33417 | -0.39825 | -0.41657 | 0.064087 | 0.29297
2200.5781 | 121.7422 | -121.4264 | 0.28381 | 0.4218 | 0.0077006 | 0.0035299 | 0.039388 | -0.00036612 | -0.0024415 | 0.016276 | 0.009155 | 0.27008 | -0.29297 | -0.045776 | -0.041199 | -0.013733 | -0.004578 | 0.1236 | 0.36163 | -121.8796 | 121.1334 | -0.013732 | 121.4355 | 121.3806 | 121.8338 | -0.32501 | -0.40283 | -0.45319 | 0.07782 | 0.30212
2201.5781 | 121.788 | -121.4767 | 0.28839 | 0.36839 | 0.0066326 | 0.0073751 | 0.035329 | -0.0020751 | 0.0005493 | 0.013926 | -0.013733 | 0.27924 | -0.31128 | -0.050354 | -0.059509 | -0.013733 | -0.009155 | 0.11902 | 0.3479 | -121.9116 | 121.1655 | -0.009155 | 121.463 | 121.4264 | 121.8613 | -0.3479 | -0.40741 | -0.43487 | 0.059509 | 0.29755
2202.5781 | 121.788 | -121.4951 | 0.27466 | 0.25395 | 0.0055644 | 0.0037435 | 0.038106 | -0.00015252 | -0.0009461 | 0.01414 | -0.018311 | 0.27008 | -0.32044 | -0.041199 | -0.082397 | -0.009155 | 0.004578 | 0.1236 | 0.35248 | -121.9116 | 121.1746 | -0.004577 | 121.4767 | 121.4539 | 121.8704 | -0.35706 | -0.43488 | -0.41656 | 0.07782 | 0.30212
2203.5781 | 121.7834 | -121.5042 | 0.29755 | 0.29973 | 0.0089824 | 0.00096634 | 0.037893 | -0.0031433 | -0.0022277 | 0.014781 | -0.018311 | 0.28381 | -0.3067 | -0.054932 | -0.082397 | -0.032043 | 0.027466 | 0.1236 | 0.35248 | -121.9437 | 121.1975 | -0.013733 | 121.4859 | 121.4493 | 121.8887 | -0.37994 | -0.43488 | -0.43945 | 0.054932 | 0.28839
2204.5781 | 121.7789 | -121.5134 | 0.27924 | 0.24632 | 0.007487 | 0.00075274 | 0.039174 | -0.0027161 | -0.0011597 | 0.01649 | -0.013733 | 0.29297 | -0.31128 | -0.036621 | -0.054932 | -0.004578 | 0.027466 | 0.11902 | 0.3479 | -121.9299 | 121.2021 | 0.013733 | 121.4996 | 121.4767 | 121.8933 | -0.33417 | -0.40283 | -0.41656 | 0.068664 | 0.29755
2205.5781 | 121.8155 | -121.4996 | 0.2655 | 0.14714 | 0.0051372 | 0.00075274 | 0.038961 | -0.00057992 | -0.0058593 | 0.013499 | 0.036621 | 0.28839 | -0.27466 | 0.004578 | -0.032043 | 0.018311 | 0 | 0.16479 | 0.35706 | -121.9254 | 121.225 | 0.022888 | 121.5363 | 121.5042 | 121.9299 | -0.29755 | -0.3891 | -0.42572 | 0.091553 | 0.31128
2206.5781 | 121.8292 | -121.5317 | 0.27008 | 0.23869 | 0.0083416 | 0.0041707 | 0.037038 | -0.0046387 | -0.0024415 | 0.013285 | -0.013733 | 0.26093 | -0.29755 | -0.032043 | -0.059509 | -0.013733 | 0.032043 | 0.15106 | 0.34332 | -121.9391 | 121.2341 | -0.009156 | 121.5179 | 121.4996 | 121.907 | -0.32959 | -0.40283 | -0.40741 | 0.073242 | 0.28381
2207.5781 | 121.8292 | -121.5225 | 0.26093 | 0.32261 | 0.0079142 | 0.00075274 | 0.037679 | -0.0046387 | -0.0005189 | 0.01414 | -0.036621 | 0.28381 | -0.29755 | -0.041199 | -0.036621 | -0.013733 | -0.004578 | 0.1236 | 0.35248 | -121.9345 | 121.225 | 0.022888 | 121.4859 | 121.4813 | 121.8933 | -0.29755 | -0.3891 | -0.41199 | 0.091553 | 0.26092
2208.5781 | 121.8063 | -121.5317 | 0.28839 | 0.27684 | 0.0066326 | 0.0043843 | 0.039602 | -0.0039977 | -0.0005189 | 0.018199 | -0.018311 | 0.30212 | -0.3067 | -0.059509 | -0.059509 | -0.018311 | 0.004578 | 0.13275 | 0.34332 | -121.9482 | 121.225 | 0.013733 | 121.5134 | 121.4722 | 121.8887 | -0.3479 | -0.40283 | -0.41656 | 0.054932 | 0.28839
2209.5781 | 121.8109 | -121.5363 | 0.27466 | 0.26158 | 0.0081278 | 0.00096634 | 0.038533 | -0.0010071 | -0.0011597 | 0.014994 | -0.009155 | 0.27924 | -0.32044 | -0.036621 | -0.059509 | -0.022888 | 0.027466 | 0.11902 | 0.34332 | -121.962 | 121.2158 | 0.004578 | 121.5271 | 121.4996 | 121.9254 | -0.33417 | -0.40283 | -0.42572 | 0.068665 | 0.31128
2210.5781 | 121.8292 | -121.5591 | 0.27924 | 0.25395 | 0.0053508 | 0.0022481 | 0.037465 | -0.0035705 | -0.0050049 | 0.01414 | -0.022888 | 0.27466 | -0.3067 | -0.027466 | -0.068665 | -0.022888 | 0.032043 | 0.1236 | 0.33417 | -121.9574 | 121.2524 | -0.004578 | 121.5363 | 121.5317 | 121.9299 | -0.3479 | -0.40283 | -0.39825 | 0.054931 | 0.28381
2211.5781 | 121.8796 | -121.582 | 0.2655 | 0.17003 | 0.0085552 | 0.0039571 | 0.038106 | -0.0016479 | -0.0037231 | 0.015208 | 0.045776 | 0.29755 | -0.2655 | 0.022888 | 0 | 0.027466 | 0 | 0.19226 | 0.32959 | -121.9803 | 121.3165 | 0.032043 | 121.6278 | 121.6049 | 122.0032 | -0.2655 | -0.32959 | -0.39826 | 0.064087 | 0.31128
2212.5781 | 121.9025 | -121.55 | 0.2655 | 0.17766 | 0.0055644 | -0.00074266 | 0.038747 | -0.0033569 | -0.0041503 | 0.014994 | 0.082397 | 0.31586 | -0.2243 | 0.013733 | -0.004578 | 0.045776 | 0.022888 | 0.19226 | 0.32959 | -121.9803 | 121.3257 | 0.050354 | 121.6324 | 121.5637 | 121.994 | -0.27008 | -0.33417 | -0.4303 | 0.064087 | 0.3067
2213.5781 | 121.8567 | -121.6187 | 0.26093 | 0.2921 | 0.0081278 | 0.00053914 | 0.037679 | -0.0016479 | -0.0028687 | 0.015208 | 0 | 0.27924 | -0.30212 | -0.027466 | -0.050354 | -0.009155 | 0.036621 | 0.15106 | 0.35248 | -121.9803 | 121.3165 | 0.018311 | 121.6187 | 121.5912 | 121.9528 | -0.31128 | -0.40283 | -0.36163 | 0.091553 | 0.30212
2214.5781 | 121.8567 | -121.5729 | 0.27924 | 0.36076 | 0.005778 | 0.0048115 | 0.037893 | -0.0022889 | -0.0032959 | 0.013713 | -0.018311 | 0.27466 | -0.3067 | -0.045776 | -0.059509 | -0.009155 | -0.004578 | 0.13275 | 0.35248 | -121.9711 | 121.2662 | -0.004578 | 121.5546 | 121.5271 | 121.9254 | -0.33874 | -0.41199 | -0.39825 | 0.073242 | 0.28839
2215.5781 | 116.3681 | -78.0441 | 42.7963 | 0.29973 | 0.016032 | 0.0024617 | 6.936 | 0.053894 | -0.015259 | 7.0167 | 3.0579 | 51.7548 | -0.12817 | 1.5152 | 2.2797 | 22.7829 | -1.1078 | 8.6105 | 43.1992 | -76.4648 | 77.916 | 8.9584 | 81.102 | 79.5593 | 77.98 | -40.5167 | -40.9195 | 1.5793 | 0.40283 | 3.186
2216.5781 | 117.4484 | -70.9396 | 48.8205 | 0.25395 | 0.016459 | 0.0026753 | 6.936 | 0.046204 | -0.048584 | 7.0167 | 6.9122 | 54.8264 | -0.14191 | 7.5165 | 7.6263 | 42.5446 | 0.55389 | 4.8889 | 44.7006 | -66.8655 | 70.7977 | 6.0059 | 77.8519 | 78.4561 | 74.382 | -41.1942 | -37.0743 | 4.0741 | -4.1199 | 7.0541
2217.5781 | 120.9549 | -120.6985 | 0.19684 | 0.33787 | 0.0083416 | -0.00052906 | 0.038106 | -0.0016479 | -0.0013733 | 0.015849 | -0.041199 | 0.24261 | -0.3067 | -0.064087 | -0.064087 | -0.027466 | -0.013733 | 0.11444 | 0.28839 | -121.1197 | 120.3918 | 0.045777 | 120.6573 | 120.6345 | 121.0556 | -0.26093 | -0.35248 | -0.42114 | 0.091553 | 0.2655
2218.5781 | 120.6436 | -121.0739 | 0.21515 | 0.23869 | 0.0053508 | 0.0026753 | 0.039174 | -0.0027161 | -0.0028687 | 0.013072 | 0.009155 | 0.2243 | -0.29755 | -0.054932 | -0.068665 | -0.032043 | 0.022888 | 0.11902 | 0.29755 | -121.463 | 120.7764 | 0.009155 | 121.0831 | 121.019 | 121.4081 | -0.28381 | -0.36621 | -0.3891 | 0.082397 | 0.3067
2219.5781 | 120.9091 | -120.52 | 0.21973 | 0.19291 | 0.0053508 | 0.0016073 | 0.04366 | -0.0027161 | -0.0050049 | 0.016276 | -0.018311 | 0.23804 | -0.3067 | -0.045776 | -0.045776 | -0.032043 | -0.022888 | 0.14648 | 0.30212 | -121.0876 | 120.2133 | 0.01831 | 120.5017 | 120.4742 | 121.0419 | -0.2655 | -0.3479 | -0.56763 | 0.082397 | 0.28839
2220.5781 | 120.7214 | -78.5706 | 35.8841 | 0.30736 | 0.0066326 | 0.00053914 | 6.936 | 0.025055 | 0.016144 | 7.0167 | -1.3504 | -3.5522 | -0.27008 | 1.1948 | 1.1032 | 19.8074 | 5.2551 | 3.7949 | 40.1642 | -69.9509 | 78.3005 | -39.4363 | 77.2202 | 79.7653 | 71.1456 | -34.7809 | -39.061 | 8.6197 | 4.2801 | -1.0803
2221.5781 | 121.138 | -120.8679 | 0.20142 | 1.0779 | 0.0049236 | -0.0022381 | 0.041311 | -0.0027161 | -0.0032959 | 0.016917 | 0.073242 | 0.21973 | -0.27924 | -0.059509 | -0.027466 | 0.004578 | -0.054932 | 0.12817 | 0.3067 | -121.2799 | 120.5887 | 0.018311 | 120.9412 | 120.8084 | 121.2204 | -0.22888 | -0.33417 | -0.41199 | 0.10529 | 0.35248
2222.5781 | 120.4697 | -120.2087 | 0.1831 | 1.0474 | 0.0068462 | -0.00074266 | 0.035115 | -0.0046387 | -0.0007325 | 0.010508 | 0.10071 | 0.25635 | -0.2655 | -0.050354 | -0.032043 | 0.009155 | -0.064087 | 0.16022 | 0.33417 | -121.2433 | 119.9432 | 0.073243 | 120.3094 | 120.1584 | 121.1929 | -0.21515 | -0.36621 | -1.0345 | 0.15106 | 0.36621
2223.5781 | 121.0876 | -120.4971 | 0.54932 | 1.0245 | 0.0062052 | 0.00075274 | 0.10817 | -0.0035705 | -0.0026551 | 0.083781 | 0.13733 | 0.55389 | -0.27924 | -0.004578 | -0.018311 | 0.10986 | -0.082397 | 0.44861 | 0.62714 | -120.9 | 120.2179 | 0.004578 | 120.6345 | 120.4926 | 120.8954 | -0.56763 | -0.64545 | -0.40283 | 0.07782 | 0.41656
2224.5781 | 120.9137 | -119.9707 | 0.93842 | 1.1847 | 0.0072734 | 0.00075274 | 0.23336 | -0.0048523 | -0.0020141 | 0.23481 | 0.14191 | 0.93842 | -0.27466 | -0.018311 | 0 | 0.17395 | -0.050354 | 0.32959 | 0.99792 | -120.3232 | 119.696 | 0 | 120.1126 | 119.9524 | 120.3049 | -0.93842 | -0.99792 | -0.35248 | 0.059509 | 0.41657
2225.5781 | 121.1151 | -117.7689 | 3.4332 | 0.33024 | 0.0081278 | 0.0033161 | 0.89324 | -0.0012207 | -0.0003051 | 0.89555 | 0.20599 | 3.4927 | -0.2655 | 0.068665 | 0.050354 | 0.64087 | 0.064087 | 1.1215 | 3.36 | -118.0298 | 117.5034 | 0.059509 | 117.9749 | 117.8375 | 118.0984 | -3.3829 | -3.3096 | -0.26093 | -0.073243 | 0.4715
2226.5781 | 121.1472 | -118.0298 | 3.0304 | 0.33787 | 0.0066326 | 0.0033161 | 0.68453 | -0.0031433 | -9.1495e-05 | 0.66633 | 0.17395 | 3.0441 | -0.2243 | -0.059509 | -0.064087 | 0.16022 | -0.004578 | 0.32501 | 3.067 | -118.3914 | 117.8055 | 0.013732 | 118.2037 | 117.9703 | 118.3319 | -3.0945 | -3.1311 | -0.36163 | 0.036621 | 0.39825
2227.5781 | 121.3028 | -121.0098 | 0.25177 | 0.38365 | 0.0072734 | 0.00075274 | 0.040883 | -0.0057067 | -0.0020141 | 0.020549 | -0.004578 | 0.26093 | -0.3067 | -0.059509 | -0.059509 | 0.027466 | -0.022888 | 0.11902 | 0.32501 | -121.376 | 120.7031 | 0.009155 | 121.0052 | 120.9503 | 121.3165 | -0.31128 | -0.38452 | -0.36621 | 0.073242 | 0.30212
2228.5781 | 121.4218 | -121.0007 | 0.27466 | 0.4218 | 0.0070598 | 0.0045979 | 0.044301 | -0.0061341 | -0.0020141 | 0.01948 | 0.013733 | 0.27466 | -0.29755 | 0.022888 | 0.004578 | 0.045776 | -0.14648 | 0.21973 | 0.33875 | -121.376 | 120.7031 | 0 | 121.0144 | 121.0236 | 121.3989 | -0.27008 | -0.33417 | -0.37537 | 0.064087 | 0.31128
2229.5781 | 121.4401 | -121.0419 | 0.26093 | 0.42943 | 0.0066326 | -0.0013835 | 0.044088 | -0.0048523 | -0.0022277 | 0.020335 | 0 | 0.2655 | -0.30212 | 0.004578 | -0.013733 | 0.050354 | -0.1236 | 0.1831 | 0.32959 | -121.431 | 120.7397 | 0.004578 | 121.0419 | 121.0464 | 121.4355 | -0.27466 | -0.34332 | -0.3891 | 0.068665 | 0.30212
2230.5781 | 121.4264 | -121.0693 | 0.25635 | 0.41417 | 0.0059916 | 0.0035299 | 0.040883 | -0.0037841 | -0.0005189 | 0.023326 | 0.009155 | 0.28839 | -0.30212 | 0 | -0.009155 | 0.036621 | -0.10071 | 0.17395 | 0.32959 | -121.463 | 120.7672 | 0.032043 | 121.0785 | 121.0693 | 121.463 | -0.2655 | -0.33875 | -0.39368 | 0.073242 | 0.31128
2231.5781 | 121.4355 | -120.9686 | 0.29755 | 0.26158 | 0.0068462 | -0.00052906 | 0.041524 | -0.0052795 | -0.0009461 | 0.018412 | 0.004578 | 0.3479 | -0.3067 | -0.027466 | -0.032043 | 0.022888 | -0.07782 | 0.15106 | 0.37994 | -121.4401 | 120.6619 | 0.050354 | 120.9732 | 120.9412 | 121.4127 | -0.32959 | -0.41199 | -0.4715 | 0.082398 | 0.31128
2232.5781 | 120.8221 | -115.5258 | 5.1315 | 0.37602 | 0.0066326 | 0.0052387 | 1.4301 | -0.0025025 | 0.0014039 | 1.4076 | 0.23346 | 5.2322 | -0.1831 | 0.3067 | 0.29755 | 0.3067 | -0.10071 | -0.79193 | 5.2139 | -115.9561 | 115.3427 | 0.10071 | 115.7593 | 115.8325 | 116.2628 | -4.834 | -4.9164 | -0.4303 | 0.082397 | 0.41656
2233.5781 | 108.1558 | -111.2823 | 8.9951 | 0.35313 | 0.010691 | 0.0056661 | 1.163 | -0.00036612 | 0.0050353 | 1.1316 | -3.0808 | 8.7158 | -0.045776 | 0.1831 | 0.16937 | 5.8823 | -0.27466 | 0.10071 | 8.4869 | -111.8866 | 111.2366 | -0.27924 | 108.2016 | 111.4655 | 112.0697 | -8.8257 | -8.3176 | -0.60425 | -0.50812 | -3.035
2234.5781 | 121.1151 | -80.0858 | 40.6082 | 0.35313 | 0.016246 | 0.0018209 | 2.5719 | 0.017578 | 0.019775 | 2.8263 | 2.6825 | 41.8716 | 0.48981 | 0.032043 | 0.036621 | 2.2614 | -0.15564 | 0.068665 | 40.5762 | -80.3101 | 80.5756 | 1.2634 | 82.7682 | 80.1178 | 80.3421 | -40.5716 | -40.5396 | -0.22431 | -0.032043 | 2.1927
2235.5781 | 121.0922 | -120.6802 | 0.25635 | 0.38365 | 0.0051372 | 0.00053914 | 0.041097 | -0.0044251 | -0.0005189 | 0.020549 | -0.013733 | 0.2655 | -0.31128 | 0 | -0.009155 | 0.036621 | -0.1236 | 0.16479 | 0.31586 | -121.1472 | 120.369 | 0.009155 | 120.6665 | 120.6802 | 121.1472 | -0.2655 | -0.32501 | -0.46692 | 0.059509 | 0.29755
2236.5781 | 120.8954 | -119.8059 | 0.8606 | 0.41417 | 0.0072734 | 0.00096634 | 0.13189 | -0.0048523 | -0.0007325 | 0.11112 | 0 | 0.86517 | -0.27008 | 0 | -0.013733 | 0.27008 | -0.11902 | 0.14648 | 0.91553 | -120.3552 | 119.5358 | 0.004577 | 119.8059 | 119.8059 | 120.3552 | -0.87433 | -0.92926 | -0.54932 | 0.054931 | 0.27008
2237.5781 | 121.2387 | -118.6203 | 2.5131 | 0.41417 | 0.0072734 | 0.0011799 | 0.59118 | -0.0022889 | -0.0003051 | 0.57618 | 0.11444 | 2.5589 | -0.23804 | 0.050354 | 0.045776 | 0.97504 | -0.068665 | 0.11444 | 2.5543 | -118.9957 | 118.3823 | 0.045776 | 118.7347 | 118.6707 | 119.046 | -2.4673 | -2.5085 | -0.37537 | 0.041198 | 0.35248
2238.5781 | 121.2799 | -120.9961 | 0.23346 | 0.3455 | 0.0064188 | 0.00096634 | 0.039388 | -0.0076293 | -0.0011597 | 0.016917 | -0.022888 | 0.24719 | -0.31128 | -0.032043 | -0.022888 | 0.041199 | -0.07782 | 0.15564 | 0.32044 | -121.376 | 120.6848 | 0.013733 | 120.9732 | 120.9641 | 121.344 | -0.25635 | -0.34332 | -0.37994 | 0.086976 | 0.28839
2239.5781 | 121.3028 | -121.0419 | 0.25177 | 0.20817 | 0.0055644 | -0.0011699 | 0.047933 | -0.0027161 | -0.0013733 | 0.019694 | -0.022888 | 0.23804 | -0.30212 | -0.050354 | -0.054932 | -0.036621 | 0.032043 | 0.10986 | 0.32959 | -121.4859 | 120.7397 | -0.013733 | 121.019 | 120.9915 | 121.4355 | -0.3067 | -0.38452 | -0.44403 | 0.07782 | 0.27924
2240.5781 | 121.2479 | -121.0236 | 0.3479 | 0.25395 | 0.0062052 | 0.0011799 | 0.084462 | -0.0027161 | 0.0003357 | 0.047251 | 0.013733 | 0.29297 | -0.3067 | -0.032043 | -0.050354 | -0.009155 | 0.032043 | 0.11444 | 0.45319 | -121.3989 | 120.7169 | -0.054931 | 121.0373 | 120.9915 | 121.3669 | -0.39825 | -0.50354 | -0.37537 | 0.10529 | 0.32043
2241.5781 | 121.1243 | -121.1014 | 0.25177 | 0.35313 | 0.0066326 | 0.0037435 | 0.042806 | -0.0042115 | -0.0005189 | 0.020335 | -0.050354 | 0.27008 | -0.29297 | -0.050354 | -0.054932 | -0.018311 | -0.018311 | 0.11444 | 0.3479 | -121.5179 | 120.8084 | 0.018311 | 121.051 | 121.051 | 121.4676 | -0.3067 | -0.40283 | -0.41657 | 0.09613 | 0.24261
2242.5781 | 121.2799 | -121.1243 | 0.27924 | 0.76512 | 0.00471 | 0.0031025 | 0.040883 | -0.0037841 | -0.0007325 | 0.019694 | 0.11902 | 0.29755 | -0.27466 | 0.004578 | -0.032043 | -0.018311 | -0.022888 | 0.14191 | 0.35248 | -121.4996 | 120.8496 | 0.01831 | 121.2433 | 121.1288 | 121.5042 | -0.31128 | -0.38452 | -0.37537 | 0.073242 | 0.39368
2243.5781 | 121.1105 | -121.106 | 0.3067 | 0.36839 | 0.0068462 | 0.0028889 | 0.043447 | -0.0067749 | -0.0024415 | 0.021403 | -0.018311 | 0.31128 | -0.31128 | -0.068665 | -0.050354 | 0.041199 | -0.027466 | 0.10071 | 0.39368 | -121.5088 | 120.7947 | 0.004577 | 121.0876 | 121.0373 | 121.4401 | -0.35706 | -0.44403 | -0.40283 | 0.086975 | 0.29297
2244.5781 | 121.2296 | -121.051 | 0.3479 | 0.37602 | 0.0064188 | 0.0018209 | 0.042165 | -0.0029297 | -0.0024415 | 0.023326 | -0.013733 | 0.32501 | -0.29755 | -0.027466 | 0.082397 | 0.091553 | -0.21973 | 0.40741 | 0.41199 | -121.4905 | 120.7535 | -0.022888 | 121.0373 | 121.0236 | 121.463 | -0.2655 | -0.32959 | -0.43945 | 0.064087 | 0.28381
2245.5781 | 121.1563 | -121.0098 | 0.36621 | 0.39891 | 0.0072734 | 0.0039571 | 0.058187 | -0.0012207 | 0.0003357 | 0.034434 | -0.013733 | 0.3479 | -0.31128 | -0.027466 | -0.050354 | -0.004578 | -0.022888 | 0.11444 | 0.45319 | -121.5317 | 120.6985 | -0.018311 | 120.9961 | 120.9824 | 121.5042 | -0.41657 | -0.50354 | -0.52185 | 0.086975 | 0.29755
2246.5781 | 121.2067 | -120.9732 | 0.33417 | 0.23869 | 0.005778 | 0.00075274 | 0.045583 | -0.0033569 | -0.0022277 | 0.027385 | 0 | 0.40283 | -0.29755 | -0.041199 | -0.050354 | -0.022888 | 0.022888 | 0.1236 | 0.39368 | -121.5363 | 120.6757 | 0.068665 | 120.9732 | 120.932 | 121.4951 | -0.38452 | -0.44403 | -0.56305 | 0.05951 | 0.29755
2247.5781 | 121.3211 | -121.1426 | 0.3067 | 0.28447 | 0.0087688 | 0.0020345 | 0.04601 | -0.0035705 | -0.0035095 | 0.019694 | 0.022888 | 0.32501 | -0.31586 | -0.036621 | -0.045776 | -0.018311 | 0.009155 | 0.1236 | 0.37079 | -121.6095 | 120.8267 | 0.01831 | 121.1655 | 121.106 | 121.5729 | -0.35248 | -0.41656 | -0.46692 | 0.064087 | 0.33875
2248.5781 | 121.5546 | -121.1746 | 0.33417 | 0.36839 | 0.0081278 | 0.0016073 | 0.041738 | -0.0082703 | 0.0003357 | 0.022898 | -0.009155 | 0.33875 | -0.31128 | -0.068665 | -0.022888 | 0.054932 | -0.027466 | 0.15106 | 0.40741 | -121.5683 | 120.8633 | 0.004578 | 121.1655 | 121.106 | 121.4996 | -0.35706 | -0.4303 | -0.39368 | 0.073243 | 0.30212
2249.5781 | 121.5042 | -99.3027 | 21.8719 | 0.36076 | 0.010691 | -0.0013835 | 4.4697 | 0.0083923 | 0.01059 | 4.4432 | 2.3895 | 19.6335 | 0.027466 | 0.19226 | 0.19226 | 4.4495 | 0.32959 | 0.35706 | 22.1054 | -99.1241 | 99.3301 | -2.2385 | 101.6922 | 99.4949 | 99.3164 | -21.6797 | -21.9131 | 0.17853 | 0.23346 | 2.3621
2250.5781 | 121.344 | -113.8916 | 7.6904 | 0.39891 | 0.0059916 | 0.0063069 | 0.25942 | -0.00079352 | 0.0018311 | 0.15727 | -0.16479 | 0.55847 | -0.31586 | -0.041199 | -0.013733 | 0.35248 | 1.1673 | 0.11902 | 5.4611 | -114.8804 | 113.5757 | -7.132 | 113.7268 | 113.8504 | 114.8392 | -7.7042 | -5.4749 | -0.98877 | -2.2293 | 0.15106
2251.5781 | 120.8038 | -81.7017 | 39.1571 | 0.42943 | 0.011546 | -0.00074266 | 3.5157 | 0.017792 | 0.018494 | 3.1441 | 1.6388 | 40.2374 | 0.15564 | 0.10529 | 0.11444 | 2.092 | -0.55847 | 0.11444 | 36.9278 | -82.7499 | 81.8573 | 1.0803 | 83.3405 | 81.8069 | 82.8552 | -39.0427 | -36.8134 | -1.0483 | -2.2293 | 1.4832
2252.5781 | 120.6848 | -82.0999 | 38.0081 | 0.31499 | 0.012828 | -0.0011699 | 6.936 | 0.013092 | 0.016998 | 7.0167 | 1.8585 | 38.4659 | 0.10071 | 0.76904 | 0.77362 | 11.1832 | 0.045776 | 0.086975 | 37.1841 | -81.1295 | 82.2006 | 0.45776 | 83.9584 | 82.869 | 81.8985 | -37.2345 | -36.4105 | 0.97046 | -0.82398 | 1.7578
2253.5781 | 120.5933 | -93.7042 | 26.6281 | 0.26921 | 0.012614 | -0.00031526 | 6.936 | 0.0051881 | 0.0088807 | 7.0167 | 1.5518 | 26.4633 | -0.009155 | 0.59052 | 0.59052 | 7.4936 | 0.050354 | 3.0762 | 25.2823 | -93.7363 | 93.6951 | -0.16479 | 95.256 | 94.2947 | 94.3268 | -26.0376 | -24.6918 | -0.032043 | -1.3458 | 1.561
2254.5781 | 121.1014 | -120.7764 | 0.032043 | 0.1624 | 0.0072734 | 0.00075274 | 0.045156 | -0.0029297 | -0.0022277 | 0.017344 | 0.018311 | 0.22888 | -0.31586 | -0.027466 | -0.041199 | -0.013733 | 0.013733 | 0.15564 | 0.27008 | -121.2341 | 120.4605 | 0.19684 | 120.7947 | 120.7489 | 121.2067 | -0.073242 | -0.31128 | -0.45776 | 0.23804 | 0.33417
2255.5781 | 120.9091 | -120.5841 | 0.22888 | 0.39128 | 0.0077006 | 0.00011194 | 0.040029 | -0.0016479 | -0.0015869 | 0.014781 | -0.013733 | 0.23804 | -0.30212 | -0.064087 | 0.10529 | 0.082397 | -0.21515 | 0.42114 | 0.29297 | -121.0739 | 120.282 | 0.009155 | 120.5704 | 120.52 | 121.0098 | -0.1236 | -0.18768 | -0.48981 | 0.064087 | 0.28839
2256.5781 | 120.8221 | -120.6894 | 0.19684 | 0.32261 | 0.009196 | 0.0045979 | 0.041524 | -0.0025025 | -0.0020141 | 0.014994 | -0.13733 | 0.21057 | -0.29755 | -0.045776 | -0.064087 | -0.013733 | -0.054932 | 0.13733 | 0.28381 | -120.9778 | 120.3918 | 0.013733 | 120.5521 | 120.6436 | 120.932 | -0.26093 | -0.3479 | -0.28839 | 0.086975 | 0.16022
2257.5781 | 121.0831 | -120.8084 | 0.20599 | 0.4218 | 0.0068462 | 0.0022481 | 0.030843 | -0.0025025 | -0.0028687 | 0.0053813 | -0.027466 | 0.2243 | -0.30212 | -0.045776 | -0.059509 | -0.018311 | -0.022888 | 0.10529 | 0.3067 | -121.2387 | 120.5063 | 0.01831 | 120.7809 | 120.7626 | 121.1929 | -0.2655 | -0.36621 | -0.4303 | 0.10071 | 0.27466
2258.5781 | 121.1472 | -119.7922 | 1.3229 | 0.33787 | 0.0051372 | 0.0035299 | 0.56041 | -0.0022889 | -0.0007325 | 0.58665 | 0.13733 | 1.0437 | -0.31128 | -0.045776 | -0.041199 | 0.3891 | 0.10071 | 0.28381 | 1.2955 | -120.1584 | 119.4809 | -0.27924 | 119.9295 | 119.7464 | 120.1126 | -1.3641 | -1.3367 | -0.36621 | -0.027466 | 0.44861
2259.5781 | 121.1334 | -120.9137 | 0.21973 | 0.35313 | 0.0051372 | -0.00095626 | 0.038533 | -0.0046387 | -0.0039367 | 0.014567 | -0.064087 | 0.23346 | -0.32044 | -0.059509 | -0.068665 | -0.027466 | 0 | 0.11902 | 0.29297 | -121.2982 | 120.5933 | 0.013732 | 120.8496 | 120.8542 | 121.2387 | -0.28839 | -0.36163 | -0.38452 | 0.073242 | 0.25635
2260.5781 | 117.8284 | -45.1904 | 35.1883 | 0.2158 | 0.014109 | 0.0045979 | 6.936 | 0.023346 | 0.035156 | 7.0167 | 2.536 | 52.2308 | 0.32044 | 0.44403 | 0.44403 | 24.2981 | -0.091553 | 6.6559 | 50.4959 | -66.1926 | 45.5109 | 17.0425 | 47.7264 | 45.6345 | 66.6367 | -34.7443 | -50.0519 | -21.0022 | 15.3076 | 2.2156
2261.5781 | 121.0922 | -120.5154 | 0.56305 | 0.3455 | 0.007487 | 0.00053914 | 0.15453 | -0.0020751 | -0.0022277 | 0.12843 | -0.009155 | 0.5127 | -0.2655 | -0.054932 | -0.045776 | 0.068665 | -0.004578 | 0.16937 | 0.59967 | -120.9824 | 120.2499 | -0.050354 | 120.5063 | 120.4605 | 120.9274 | -0.60883 | -0.64545 | -0.46692 | 0.036621 | 0.25635
2262.5781 | 120.8817 | -120.3964 | 0.33417 | 0.20054 | 0.0053508 | 0.0016073 | 0.086812 | -0.0039977 | -0.0032959 | 0.058573 | -0.032043 | 0.37537 | -0.29297 | -0.050354 | -0.032043 | 0.032043 | -0.07782 | 0.15564 | 0.4303 | -120.9 | 120.1035 | 0.041199 | 120.3644 | 120.3461 | 120.8496 | -0.36621 | -0.46234 | -0.50354 | 0.096131 | 0.26093
2263.5781 | 120.575 | -120.3049 | 0.26093 | -0.91335 | 0.0064188 | 0.00053914 | 0.034902 | -0.0057067 | -0.0007325 | 0.010295 | -0.39825 | 0.29297 | -0.27924 | -0.036621 | -0.050354 | 0.041199 | -0.086975 | 0.13733 | 0.33875 | -120.6619 | 120.0256 | 0.032044 | 119.9066 | 120.2683 | 120.6253 | -0.31128 | -0.3891 | -0.35705 | 0.07782 | -0.11902
2264.5781 | 120.9824 | -120.4971 | 0.40283 | -0.72261 | 0.0044962 | -0.0011699 | 0.026571 | -0.0029297 | -0.0030823 | 0.0017497 | 0.064087 | 0.41657 | -0.29755 | -0.036621 | -0.054932 | 0.022888 | -0.022888 | 0.14648 | 0.48523 | -120.9595 | 120.1996 | 0.013733 | 120.5612 | 120.4605 | 120.9229 | -0.45776 | -0.54016 | -0.46234 | 0.082397 | 0.36163
2265.5781 | 120.9274 | -120.4285 | 0.49439 | 0.74223 | 0.0059916 | 0.0020345 | 0.026998 | -0.0042115 | -0.0007325 | 0.0030315 | 0.1236 | 0.52185 | -0.29297 | -0.022888 | -0.059509 | 0 | -0.041199 | 0.13733 | 0.59052 | -120.7947 | 120.1355 | 0.027466 | 120.5521 | 120.4056 | 120.7718 | -0.55389 | -0.65002 | -0.36621 | 0.09613 | 0.41656
2266.5781 | 121.1929 | -120.7214 | 0.45319 | -1.867 | 0.0044962 | 0.0016073 | 0.029561 | -0.0025025 | 0.0001221 | 0.0043131 | -0.004578 | 0.49439 | -0.2655 | -0.036621 | -0.059509 | -0.009155 | -0.027466 | 0.13733 | 0.52185 | -121.0739 | 120.4559 | 0.041199 | 120.7169 | 120.6848 | 121.0373 | -0.5127 | -0.58136 | -0.35248 | 0.068665 | 0.26092
2267.5781 | 121.2204 | -120.8588 | 0.39825 | 0.33024 | 0.0051372 | -0.0035197 | 0.030843 | -0.0067749 | -0.0013733 | 0.0049541 | -0.013733 | 0.41199 | -0.29755 | -0.032043 | -0.054932 | -0.013733 | -0.004578 | 0.11444 | 0.46234 | -121.2067 | 120.5612 | 0.013733 | 120.845 | 120.8267 | 121.1746 | -0.45319 | -0.51727 | -0.3479 | 0.064087 | 0.28381
2268.5781 | 121.3074 | -120.8679 | 0.3891 | 0.2921 | 0.0089824 | 0.0011799 | 0.027211 | -0.0035705 | -0.0015869 | 0.0043131 | -0.009155 | 0.39825 | -0.28839 | -0.032043 | -0.032043 | 0.004578 | -0.045776 | 0.13275 | 0.47607 | -121.2387 | 120.5795 | 0.009155 | 120.8588 | 120.8359 | 121.2067 | -0.42114 | -0.50812 | -0.37079 | 0.086975 | 0.27924
2269.5781 | 121.4127 | -120.7855 | 0.41199 | 0.43706 | 0.0038554 | -0.00074266 | 0.027425 | -0.0031433 | -0.0003051 | 0.0028177 | 0.054932 | 0.40283 | -0.29755 | 0.050354 | 0.054932 | 0.10071 | -0.17395 | 0.23346 | 0.49439 | -121.2021 | 120.488 | -0.009155 | 120.8405 | 120.8359 | 121.2524 | -0.35706 | -0.43945 | -0.41657 | 0.082398 | 0.35248
2270.5781 | 121.4722 | -120.8267 | 0.3891 | 0.45994 | 0.0066326 | 0.0011799 | 0.027425 | -0.0048523 | -0.0007325 | 0.0058085 | 0.054932 | 0.39825 | -0.27924 | 0.054932 | 0.050354 | 0.11902 | -0.16479 | 0.23804 | 0.45776 | -121.257 | 120.5475 | 0.009155 | 120.8817 | 120.8817 | 121.312 | -0.33874 | -0.40741 | -0.4303 | 0.068665 | 0.33417
2271.5781 | 121.4355 | -120.8862 | 0.40283 | 0.37602 | 0.0059916 | -0.00031526 | 0.026998 | -0.0039977 | -0.0013733 | 0.0045267 | 0.054932 | 0.39825 | -0.27008 | 0.064087 | 0.059509 | 0.11444 | -0.17853 | 0.24719 | 0.46692 | -121.2708 | 120.6161 | -0.004578 | 120.9412 | 120.9503 | 121.3348 | -0.34332 | -0.40741 | -0.38452 | 0.064087 | 0.32501
2272.5781 | 121.5225 | -120.8405 | 0.44403 | 0.44468 | 0.0077006 | -0.0056559 | 0.027852 | -0.0046387 | -0.0032959 | 0.0068767 | 0.07782 | 0.43488 | -0.28839 | 0.050354 | 0.041199 | 0.1236 | -0.18768 | 0.24719 | 0.50812 | -121.2341 | 120.5521 | -0.009156 | 120.9183 | 120.8908 | 121.2845 | -0.40283 | -0.46692 | -0.39368 | 0.064087 | 0.36621
2273.5781 | 121.5408 | -120.8588 | 0.44403 | 0.35313 | 0.00471 | -0.0013835 | 0.027211 | -0.0061341 | -0.0007325 | 0.0055949 | 0.07782 | 0.44403 | -0.27466 | 0.064087 | 0.068665 | 0.13733 | -0.1831 | 0.24261 | 0.50354 | -121.257 | 120.5841 | 0 | 120.9366 | 120.9229 | 121.3211 | -0.37537 | -0.43488 | -0.39825 | 0.059509 | 0.35248
2274.5781 | 121.463 | -120.7581 | 0.44403 | 0.36076 | 0.0059916 | 0.0075887 | 0.027639 | -0.0035705 | 0.0001221 | 0.0043131 | 0.022888 | 0.46692 | -0.29755 | -0.004578 | -0.013733 | 0.045776 | -0.09613 | 0.16479 | 0.53558 | -121.3531 | 120.4605 | 0.022888 | 120.7809 | 120.7535 | 121.3486 | -0.45776 | -0.54932 | -0.59509 | 0.091552 | 0.32043
2275.5781 | 121.6049 | -120.9183 | 0.41657 | 0.41417 | 0.0038554 | 0.0024617 | 0.025289 | -0.0014343 | -0.0005189 | 0.0049541 | 0.068665 | 0.4303 | -0.24719 | 0.16937 | 0.15106 | 0.09613 | -0.14648 | 0.29755 | 0.48523 | -121.3074 | 120.6711 | 0.013733 | 120.9869 | 121.0876 | 121.4767 | -0.2655 | -0.33417 | -0.3891 | 0.068664 | 0.31586
2276.5781 | 121.6232 | -120.9366 | 0.43488 | 0.38365 | 0.00471 | -0.0026653 | 0.022939 | -0.0067749 | -0.0015869 | 0.0055949 | 0.013733 | 0.40741 | -0.2655 | 0.10071 | 0.050354 | 0.1236 | -0.13275 | 0.26093 | 0.48523 | -121.2982 | 120.6711 | -0.027465 | 120.9503 | 121.0373 | 121.3989 | -0.38452 | -0.43488 | -0.36163 | 0.050354 | 0.27924
2277.5781 | 121.4996 | -121.0144 | 0.50354 | -0.051226 | 0.0021464 | 0.00011194 | 0.025502 | -0.0089111 | -0.0030823 | 0.0036723 | -0.013733 | 0.45319 | -0.26093 | -0.004578 | -0.018311 | 0.032043 | 0.10986 | 0.20142 | 0.53558 | -121.3943 | 120.7535 | -0.050354 | 121.0007 | 121.0098 | 121.3898 | -0.52185 | -0.55389 | -0.37994 | 0.032043 | 0.24719
2278.5781 | 121.6415 | -120.9549 | 0.45776 | 2.5809 | 0.0034282 | -0.0041607 | 0.026357 | -0.0065613 | -0.0007325 | 0.0047403 | 0.091553 | 0.40283 | -0.28381 | 0.091553 | 0.082397 | 0.14648 | -0.19226 | 0.26093 | 0.48523 | -121.3623 | 120.6711 | -0.054932 | 121.0464 | 121.0464 | 121.4539 | -0.37537 | -0.40283 | -0.40741 | 0.027465 | 0.37537
2279.5781 | 121.669 | -120.9549 | 0.45776 | 0.72697 | 0.001292 | -0.0020243 | 0.025502 | -0.0069885 | -0.0028687 | 0.0034587 | 0.19684 | 0.4303 | -0.3067 | 0.086975 | 0.068665 | 0.11902 | -0.17853 | 0.25177 | 0.53101 | -121.376 | 120.6482 | -0.027466 | 121.1517 | 121.0419 | 121.463 | -0.3891 | -0.46234 | -0.42114 | 0.073242 | 0.50354
2280.5781 | 121.6827 | -120.9869 | 0.48065 | 0.40654 | 0.005778 | 0.00011194 | 0.029134 | -0.0063477 | -0.0020141 | 0.0043131 | 0.10071 | 0.46234 | -0.25635 | 0.091553 | 0.059509 | 0.13733 | -0.20142 | 0.26093 | 0.51727 | -121.3806 | 120.7306 | -0.018311 | 121.0876 | 121.0785 | 121.4722 | -0.42114 | -0.45776 | -0.39368 | 0.036621 | 0.35706
2281.5781 | 121.6919 | -120.9778 | 0.45776 | 0.39128 | 0.0049236 | -0.00074266 | 0.029989 | -0.0076293 | -0.0030823 | 0.0040995 | 0.091553 | 0.44403 | -0.26093 | 0.091553 | 0.068665 | 0.14648 | -0.20599 | 0.26093 | 0.50812 | -121.3852 | 120.7169 | -0.013733 | 121.0693 | 121.0693 | 121.4767 | -0.3891 | -0.43945 | -0.40741 | 0.050354 | 0.35248
2282.5781 | 121.701 | -121.0144 | 0.45776 | -0.074114 | 0.0064188 | 0.0037435 | 0.028066 | -0.0063477 | -0.0015869 | 0.0040995 | 0.022888 | 0.40283 | -0.29297 | 0.059509 | 0.073242 | 0.13733 | -0.19226 | 0.24719 | 0.50354 | -121.4081 | 120.7214 | -0.054932 | 121.0373 | 121.0739 | 121.4676 | -0.38452 | -0.4303 | -0.39368 | 0.045776 | 0.31586
2283.5781 | 121.6919 | -121.0236 | 0.49896 | 0.37602 | 0.00471 | -0.0020243 | 0.024434 | -0.0080567 | -0.0005189 | 0.0045267 | 0.041199 | 0.44403 | -0.24261 | 0.027466 | 0.036621 | 0.09613 | -0.13733 | 0.2243 | 0.52185 | -121.3943 | 120.7809 | -0.054931 | 121.0648 | 121.051 | 121.4218 | -0.46234 | -0.48523 | -0.37079 | 0.022889 | 0.28381
2284.5781 | 121.6782 | -121.0281 | 0.48065 | 0.35313 | 0.0032146 | -0.00031526 | 0.025716 | -0.0080567 | -0.0026551 | 0.0049541 | 0.054932 | 0.44403 | -0.25635 | 0.059509 | 0.041199 | 0.10071 | -0.13733 | 0.24261 | 0.53101 | -121.4401 | 120.7718 | -0.036621 | 121.0831 | 121.0876 | 121.4996 | -0.43945 | -0.48981 | -0.41199 | 0.050354 | 0.31128
2285.5781 | 121.7239 | -121.0373 | 0.47607 | 0.39891 | 0.00471 | -0.0015971 | 0.02593 | -0.0095519 | 0.0003357 | 0.0064493 | 0.054932 | 0.44403 | -0.25635 | 0.050354 | 0.050354 | 0.10986 | -0.14648 | 0.24261 | 0.5127 | -121.431 | 120.7809 | -0.032043 | 121.0922 | 121.0876 | 121.4813 | -0.42572 | -0.46234 | -0.39368 | 0.036621 | 0.31128
2286.5781 | 121.7331 | -121.0739 | 0.45776 | 0.36839 | 0.0038554 | 0.0016073 | 0.028493 | -0.0076293 | -0.0032959 | 0.0011087 | 0.054932 | 0.40741 | -0.25635 | 0.059509 | 0.041199 | 0.10529 | -0.13275 | 0.23346 | 0.50812 | -121.4539 | 120.8176 | -0.050354 | 121.1288 | 121.1334 | 121.5134 | -0.41657 | -0.46692 | -0.37994 | 0.050354 | 0.31128
2287.5781 | 121.7743 | -121.0648 | 0.4303 | 0.38365 | 0.0042826 | 0.0018209 | 0.027211 | -0.0093383 | -0.0009461 | 0.0034587 | -0.11902 | 0.39368 | -0.27008 | 0.068665 | 0.059509 | 0.14191 | -0.21057 | 0.25177 | 0.47607 | -121.4905 | 120.7947 | -0.036621 | 120.9457 | 121.1334 | 121.5591 | -0.37079 | -0.41657 | -0.42572 | 0.045776 | 0.15106
2288.5781 | 121.7972 | -121.1014 | 0.44403 | 0.4218 | 0.003001 | 0.00053914 | 0.029561 | -0.0076293 | -0.0035095 | 0.0058085 | -0.032043 | 0.40283 | -0.23346 | 0.11444 | 0.059509 | 0.10071 | -0.14191 | 0.25635 | 0.48981 | -121.4951 | 120.8679 | -0.041199 | 121.0693 | 121.2158 | 121.6095 | -0.38452 | -0.4303 | -0.39368 | 0.045776 | 0.20142
2289.5781 | 121.7606 | -121.1197 | 0.4715 | 0.41417 | 0.00471 | 0.0022481 | 0.026998 | -0.0099793 | -0.0022277 | 0.0034587 | 0.054932 | 0.4303 | -0.25177 | 0.068665 | 0.054932 | 0.11902 | -0.15564 | 0.23346 | 0.53558 | -121.4813 | 120.8679 | -0.041199 | 121.1746 | 121.1884 | 121.55 | -0.41657 | -0.48065 | -0.36163 | 0.064086 | 0.3067
2290.5781 | 121.7606 | -121.1105 | 0.4715 | 0.2921 | 0.0036418 | -0.0037333 | 0.024862 | -0.0091247 | -0.0028687 | 0.0058085 | 0.004578 | 0.45319 | -0.26093 | 0.041199 | 0.022888 | 0.086975 | -0.10529 | 0.21515 | 0.53558 | -121.4951 | 120.8496 | -0.018311 | 121.1151 | 121.1517 | 121.5363 | -0.44861 | -0.5127 | -0.38452 | 0.064086 | 0.2655
2291.5781 | 121.788 | -121.1105 | 0.47607 | 0.27684 | 0.0036418 | -0.00052906 | 0.024007 | -0.0086975 | -0.0026551 | 0.0049541 | 0.018311 | 0.44403 | -0.27466 | 0.036621 | 0.032043 | 0.09613 | -0.10071 | 0.23804 | 0.52185 | -121.4905 | 120.8359 | -0.032043 | 121.1288 | 121.1472 | 121.5271 | -0.44403 | -0.48981 | -0.37994 | 0.045777 | 0.29297
2292.5781 | 121.8475 | -121.1105 | 0.48065 | 0.15477 | 0.00236 | -0.00031526 | 0.026571 | -0.0099793 | -0.0035095 | 0.0043131 | 0.068665 | 0.46234 | -0.27008 | 0.11902 | 0.10071 | 0.16022 | -0.10071 | 0.29297 | 0.55389 | -121.4401 | 120.8405 | -0.018311 | 121.1792 | 121.2296 | 121.5591 | -0.37994 | -0.45319 | -0.32959 | 0.073242 | 0.33875
2293.5781 | 121.8063 | -121.1197 | 0.5127 | 0.33024 | 0.0036418 | -0.0015971 | 0.027425 | -0.0074157 | -0.0030823 | 0.0051677 | 0.082397 | 0.44861 | -0.25635 | 0.086975 | 0.054932 | 0.11902 | -0.17395 | 0.23804 | 0.53558 | -121.5317 | 120.8633 | -0.064087 | 121.2021 | 121.2067 | 121.6187 | -0.45776 | -0.48065 | -0.41199 | 0.022888 | 0.33875
2294.5781 | 121.8155 | -121.1197 | 0.50354 | 0.40654 | 0.0036418 | -0.0088603 | 0.027639 | -0.0084839 | -0.0013733 | 0.0068767 | 0.07782 | 0.44403 | -0.24719 | 0.082397 | 0.054932 | 0.1236 | -0.16022 | 0.25177 | 0.52185 | -121.5225 | 120.8725 | -0.059509 | 121.1975 | 121.2021 | 121.6049 | -0.44861 | -0.46692 | -0.40283 | 0.018311 | 0.32501
2295.5781 | 121.8155 | -121.1655 | 0.50812 | 0.36076 | 0.0032146 | -0.00010166 | 0.02892 | -0.0082703 | -0.0020141 | 0.0047403 | 0.050354 | 0.44861 | -0.26093 | 0.073242 | 0.073242 | 0.11902 | -0.16937 | 0.22888 | 0.54932 | -121.5225 | 120.9045 | -0.05951 | 121.2158 | 121.2387 | 121.5958 | -0.43488 | -0.47607 | -0.35706 | 0.041198 | 0.31128
2296.5781 | 121.843 | -121.1792 | 0.48523 | 0.2921 | 0.004069 | -0.00010166 | 0.02358 | -0.0091247 | -0.0026551 | 0.0049541 | 0.022888 | 0.48065 | -0.25177 | 0.050354 | 0.022888 | 0.10529 | -0.10986 | 0.21973 | 0.52185 | -121.5591 | 120.9274 | -0.004577 | 121.2021 | 121.2296 | 121.6095 | -0.46234 | -0.49896 | -0.37994 | 0.036622 | 0.27466
2297.5781 | 121.8338 | -121.17 | 0.47607 | 0.19291 | 0.001292 | -0.0037333 | 0.024434 | -0.011688 | -0.0007325 | 0.0060221 | -0.013733 | 0.44403 | -0.30212 | 0.027466 | 0.045776 | 0.10071 | -0.064087 | 0.25177 | 0.50812 | -121.5408 | 120.8679 | -0.032043 | 121.1563 | 121.1975 | 121.5683 | -0.4303 | -0.46234 | -0.37079 | 0.032044 | 0.28839
2298.5781 | 121.8658 | -121.1746 | 0.49439 | -1.0812 | 0.0036418 | -0.0022381 | 0.025075 | -0.010193 | -0.0018005 | 0.0036723 | -0.036621 | 0.4303 | -0.30212 | 0.041199 | 0.032043 | 0.10986 | -0.073242 | 0.23804 | 0.52185 | -121.5454 | 120.8725 | -0.064087 | 121.138 | 121.2158 | 121.5866 | -0.46234 | -0.48981 | -0.37079 | 0.027466 | 0.2655
2299.5781 | 121.875 | -121.1746 | 0.50812 | 0.76512 | 0.0021464 | -0.0018107 | 0.023153 | -0.010193 | -0.0007325 | 0.0049541 | 0.036621 | 0.41657 | -0.30212 | 0.050354 | 0.041199 | 0.11902 | -0.068665 | 0.24261 | 0.52643 | -121.5454 | 120.8725 | -0.091553 | 121.2112 | 121.225 | 121.5958 | -0.46692 | -0.48523 | -0.37079 | 0.01831 | 0.33875
2300.5781 | 121.875 | -121.1975 | 0.50354 | 0.0021796 | 0.0025736 | -0.0069377 | 0.027639 | -0.0093383 | -0.0018005 | 0.0049541 | 0.082397 | 0.45776 | -0.2655 | 0.10986 | 0.091553 | 0.14191 | -0.009155 | 0.27466 | 0.55389 | -121.55 | 120.932 | -0.045776 | 121.2799 | 121.3074 | 121.6599 | -0.41199 | -0.46234 | -0.35248 | 0.050354 | 0.3479
2301.5781 | 121.8613 | -121.1746 | 0.50354 | 0.4218 | 0.0021464 | 0.00053914 | 0.026998 | -0.0095519 | -0.0035095 | 0.0043131 | 0.07782 | 0.45776 | -0.25635 | 0.073242 | 0.050354 | 0.13733 | -0.14648 | 0.24719 | 0.54932 | -121.5271 | 120.9183 | -0.045776 | 121.2524 | 121.2479 | 121.6003 | -0.45319 | -0.49896 | -0.35248 | 0.045776 | 0.33417
2302.5781 | 121.8796 | -121.225 | 0.50812 | 0.20817 | 0.0019328 | -0.0024517 | 0.024648 | -0.0095519 | -0.0024415 | 0.0064493 | 0.041199 | 0.48523 | -0.24261 | 0.059509 | 0.036621 | 0.11902 | -0.082397 | 0.23346 | 0.55847 | -121.5729 | 120.9824 | -0.022889 | 121.2662 | 121.2845 | 121.6324 | -0.4715 | -0.52185 | -0.3479 | 0.050354 | 0.28381
2303.5781 | 121.9666 | -121.2021 | 0.51727 | 0.063215 | 0.0027874 | -0.00010166 | 0.025289 | -0.0084839 | -0.0011597 | 0.0034587 | 0.10986 | 0.50812 | -0.20142 | 0.11902 | 0.086975 | 0.17395 | -0.10071 | 0.32044 | 0.55847 | -121.5408 | 121.0007 | -0.009155 | 121.312 | 121.3211 | 121.6599 | -0.4303 | -0.4715 | -0.33875 | 0.041199 | 0.31128
2304.5781 | 121.9711 | -121.2021 | 0.51727 | 0.063215 | 0.0025736 | -0.0060833 | 0.024007 | -0.0084839 | -0.0024415 | 0.0034587 | 0.13733 | 0.50354 | -0.19226 | 0.12817 | 0.10071 | 0.16937 | -0.10986 | 0.31128 | 0.5722 | -121.55 | 121.0098 | -0.013733 | 121.3394 | 121.3303 | 121.6782 | -0.41656 | -0.4715 | -0.3479 | 0.054932 | 0.32959
2305.5781 | 121.9482 | -121.1975 | 0.52643 | 0.070845 | 0.0042826 | 0.0016073 | 0.022298 | -0.01062 | -0.0007325 | 0.0038859 | 0.1831 | 0.51727 | -0.14191 | 0.10986 | 0.10529 | 0.19226 | -0.10986 | 0.32501 | 0.54932 | -121.55 | 121.0556 | -0.009155 | 121.3806 | 121.3074 | 121.6599 | -0.42114 | -0.44403 | -0.35248 | 0.022888 | 0.32501
2306.5781 | 121.9711 | -121.2021 | 0.49896 | 0.12425 | 0.00043737 | -0.0018107 | 0.024007 | -0.0086975 | -0.0024415 | 0.0036723 | 0.17395 | 0.50812 | -0.16022 | 0.10529 | 0.10986 | 0.18768 | -0.11444 | 0.32501 | 0.55847 | -121.5546 | 121.0419 | 0.009156 | 121.376 | 121.3074 | 121.6599 | -0.3891 | -0.44861 | -0.35248 | 0.05951 | 0.33417
2307.5781 | 121.9986 | -121.2112 | 0.53558 | 0.047956 | 0.00086457 | -0.0045879 | 0.026571 | -0.0091247 | -0.0045777 | 0.0021769 | 0.18768 | 0.52185 | -0.15106 | 0.11902 | 0.10529 | 0.19684 | -0.10071 | 0.31586 | 0.56763 | -121.55 | 121.0602 | -0.013732 | 121.3989 | 121.3303 | 121.669 | -0.4303 | -0.46234 | -0.33875 | 0.032044 | 0.33874
2308.5781 | 121.962 | -121.2296 | 0.53101 | 0.18529 | 0.0034282 | -0.0022381 | 0.023153 | -0.0084839 | -0.0028687 | 0.0055949 | 0.11902 | 0.49439 | -0.16479 | 0.082397 | 0.082397 | 0.15564 | -0.073242 | 0.28839 | 0.59509 | -121.5683 | 121.0648 | -0.036621 | 121.3486 | 121.3119 | 121.6507 | -0.44861 | -0.5127 | -0.33875 | 0.064087 | 0.28381
2309.5781 | 121.9849 | -121.2479 | 0.55389 | 0.17003 | 0.0017192 | -0.00074266 | 0.024862 | -0.0093383 | -0.0011597 | 0.0051677 | 0.12817 | 0.48523 | -0.16022 | 0.082397 | 0.068665 | 0.16022 | -0.073242 | 0.27924 | 0.56305 | -121.5637 | 121.0876 | -0.068665 | 121.376 | 121.3303 | 121.6461 | -0.48523 | -0.49438 | -0.31586 | 0.009155 | 0.28839
2310.5781 | 121.9482 | -121.2387 | 0.52185 | -0.028338 | 0.00065097 | -0.0043743 | 0.023793 | -0.0093383 | -0.0043641 | 0.0047403 | 0.19226 | 0.49439 | -0.13275 | 0.12817 | 0.10986 | 0.17853 | 0.11444 | 0.44403 | 0.57678 | -121.6278 | 121.106 | -0.027466 | 121.431 | 121.3669 | 121.756 | -0.41199 | -0.46692 | -0.3891 | 0.054931 | 0.32501
2311.5781 | 121.962 | -121.2433 | 0.52643 | -0.013079 | 0.0038554 | -0.0035197 | 0.02358 | -0.0089111 | -0.0037231 | 0.0053813 | 0.19226 | 0.49439 | -0.16937 | 0.13733 | 0.09613 | 0.18768 | 0.12817 | 0.43488 | 0.57678 | -121.6049 | 121.0739 | -0.032043 | 121.4355 | 121.3806 | 121.7422 | -0.4303 | -0.48065 | -0.36163 | 0.050354 | 0.36163
2312.5781 | 121.8842 | -121.2479 | 0.54016 | -0.035967 | 0.0017192 | -0.0060833 | 0.024862 | -0.0082703 | -0.0037231 | 0.0055949 | 0.18768 | 0.5127 | -0.15106 | 0.12817 | 0.09613 | 0.18768 | -0.059509 | 0.51727 | 0.59967 | -121.6141 | 121.0968 | -0.027466 | 121.4355 | 121.376 | 121.7422 | -0.44403 | -0.50354 | -0.36621 | 0.059509 | 0.33874
2313.5781 | 122.0947 | -121.2845 | 0.55847 | 0.0021796 | 0.0025736 | 0.00075274 | 0.023366 | -0.0097657 | -0.0011597 | 0.0043131 | 0.21057 | 0.5127 | -0.10986 | 0.11902 | 0.10986 | 0.19684 | -0.050354 | 0.31586 | 0.6134 | -121.5775 | 121.1746 | -0.045777 | 121.4951 | 121.4035 | 121.6965 | -0.44861 | -0.50354 | -0.29297 | 0.054931 | 0.32043
2314.5781 | 121.9666 | -121.225 | 0.57678 | -0.028338 | 0.003001 | 0.00032554 | 0.026998 | -0.0093383 | -0.0015869 | 0.0038859 | 0.19226 | 0.51727 | -0.13733 | 0.1236 | 0.11444 | 0.1831 | -0.036621 | 0.33417 | 0.6134 | -121.5546 | 121.0876 | -0.059509 | 121.4172 | 121.3486 | 121.6782 | -0.46234 | -0.49896 | -0.32959 | 0.036621 | 0.32959
2315.5781 | 122.0535 | -121.225 | 0.56763 | 0.086103 | 0.00236 | -0.0065105 | 0.024434 | -0.0089111 | -0.0037231 | 0.0034587 | 0.18768 | 0.56763 | -0.13275 | 0.11902 | 0.10986 | 0.20142 | -0.09613 | 0.32044 | 0.62256 | -121.5591 | 121.0922 | 0 | 121.4127 | 121.344 | 121.6782 | -0.45776 | -0.5127 | -0.33417 | 0.054932 | 0.32043
2316.5781 | 122.049 | -121.2433 | 0.54474 | -0.0054494 | 0.0021464 | -0.00010166 | 0.024648 | -0.0086975 | -0.0005189 | 0.0064493 | 0.19226 | 0.52185 | -0.1236 | 0.12817 | 0.11444 | 0.19684 | -0.10986 | 0.32501 | 0.61798 | -121.5958 | 121.1197 | -0.022888 | 121.4355 | 121.3715 | 121.7239 | -0.4303 | -0.50354 | -0.35248 | 0.073242 | 0.31586
2317.5781 | 122.0169 | -121.2616 | 0.59052 | -0.058855 | 0.003001 | -0.0013835 | 0.025502 | -0.0078431 | -0.0041503 | 0.0026041 | 0.19684 | 0.53101 | -0.14648 | 0.11902 | 0.082397 | 0.16937 | 0.013733 | 0.27466 | 0.62256 | -121.6049 | 121.1151 | -0.059509 | 121.4584 | 121.3806 | 121.7239 | -0.50812 | -0.54016 | -0.34332 | 0.032044 | 0.34332
2318.5781 | 122.0032 | -121.2891 | 0.57678 | 0.0021796 | 0.00236 | -0.0048015 | 0.026784 | -0.0093383 | -0.0022277 | 0.0064493 | 0.19684 | 0.53558 | -0.15106 | 0.10986 | 0.082397 | 0.17395 | 0.022888 | 0.29755 | 0.62714 | -121.6049 | 121.138 | -0.041199 | 121.4859 | 121.3989 | 121.7148 | -0.49439 | -0.54474 | -0.31586 | 0.050354 | 0.3479
2319.5781 | 122.0215 | -121.2662 | 0.58594 | 0.070845 | 0.0021464 | -0.0024517 | 0.026143 | -0.0076293 | -0.0041503 | 0.0036723 | 0.19684 | 0.51727 | -0.13733 | 0.10529 | 0.091553 | 0.16937 | 0.018311 | 0.29755 | 0.62714 | -121.5729 | 121.1288 | -0.068664 | 121.463 | 121.3715 | 121.6782 | -0.49438 | -0.53558 | -0.3067 | 0.041199 | 0.33417
2320.5781 | 122.0215 | -121.2616 | 0.59967 | -0.0054494 | 0.00236 | -0.0030925 | 0.025075 | -0.0078431 | -0.0018005 | 0.0045267 | 0.18768 | 0.54016 | -0.14648 | 0.11444 | 0.10071 | 0.1831 | 0.018311 | 0.29755 | 0.61798 | -121.6049 | 121.1151 | -0.059509 | 121.4493 | 121.376 | 121.7194 | -0.49896 | -0.51727 | -0.34332 | 0.018311 | 0.33417
2321.5781 | 122.049 | -121.2708 | 0.59052 | 0.017439 | 0.0019328 | 0.00011194 | 0.025289 | -0.0069885 | -0.0039367 | 0.0038859 | 0.19684 | 0.54932 | -0.14191 | 0.10986 | 0.091553 | 0.17853 | 0.004578 | 0.29755 | 0.63171 | -121.6003 | 121.1288 | -0.041199 | 121.4676 | 121.3806 | 121.7102 | -0.49896 | -0.54016 | -0.32959 | 0.041199 | 0.33875
2322.5781 | 122.049 | -121.2891 | 0.5722 | 0.0021796 | 0.00065097 | -0.0039469 | 0.025075 | -0.0082703 | -0.0037231 | 0.0026041 | 0.20142 | 0.53558 | -0.13733 | 0.13275 | 0.10529 | 0.20599 | -0.036621 | 0.31128 | 0.61798 | -121.6095 | 121.1517 | -0.036622 | 121.4905 | 121.4218 | 121.7422 | -0.46692 | -0.5127 | -0.32044 | 0.045776 | 0.33875
2323.5781 | 122.0444 | -121.2845 | 0.62256 | 0.093733 | 0.0019328 | -0.0048015 | 0.026998 | -0.0078431 | -0.0028687 | 0.0053813 | 0.21057 | 0.55389 | -0.12817 | 0.10071 | 0.09613 | 0.16937 | 0.004578 | 0.31128 | 0.65918 | -121.6141 | 121.1563 | -0.068665 | 121.4951 | 121.3852 | 121.7148 | -0.52643 | -0.56305 | -0.32959 | 0.036621 | 0.33875
2324.5781 | 121.9803 | -121.3257 | 0.62714 | -0.043596 | 0.0032146 | -0.0013835 | 0.027425 | -0.0099793 | -0.0018005 | 0.0030315 | 0.15106 | 0.5722 | -0.13275 | 0.013733 | 0.009155 | 0.09613 | 0.10529 | 0.19684 | 0.67291 | -121.6644 | 121.1929 | -0.054931 | 121.4767 | 121.3394 | 121.6782 | -0.61798 | -0.66376 | -0.33875 | 0.045777 | 0.28381
2325.5781 | 121.9849 | -121.3074 | 0.60883 | -0.074114 | 0.0025736 | -0.0035197 | 0.02828 | -0.0067749 | -0.0030823 | 0.0030315 | 0.16937 | 0.59967 | -0.15106 | 0.022888 | 0.013733 | 0.086975 | 0.11902 | 0.21515 | 0.67749 | -121.6599 | 121.1563 | -0.009156 | 121.4767 | 121.3303 | 121.6827 | -0.59509 | -0.66376 | -0.35248 | 0.068664 | 0.32044
2326.5781 | 121.994 | -121.3074 | 0.60425 | -0.066485 | 0.003001 | -0.0048015 | 0.026571 | -0.0072021 | -0.0047913 | 0.0038859 | 0.17853 | 0.56763 | -0.13733 | 0.036621 | 0.027466 | 0.10071 | 0.11444 | 0.22888 | 0.68665 | -121.6507 | 121.17 | -0.036621 | 121.4859 | 121.344 | 121.6873 | -0.57678 | -0.65918 | -0.34332 | 0.082398 | 0.31586
2327.5781 | 122.0215 | -121.3211 | 0.62256 | -0.074114 | 0.0025736 | -0.0011699 | 0.02892 | -0.0084839 | -0.0032959 | 0.0053813 | 0.1831 | 0.58594 | -0.14191 | 0.045776 | 0.027466 | 0.10986 | 0.10529 | 0.20599 | 0.68207 | -121.6415 | 121.1792 | -0.036622 | 121.5042 | 121.3669 | 121.6873 | -0.59509 | -0.6546 | -0.32044 | 0.059509 | 0.32501
2328.5781 | 122.0306 | -121.3257 | 0.61798 | -0.13515 | 0.0034282 | -0.00010166 | 0.025289 | -0.0069885 | -0.0005189 | 0.0047403 | 0.18768 | 0.59509 | -0.13275 | 0.045776 | 0.045776 | 0.12817 | 0.091553 | 0.23346 | 0.64545 | -121.6415 | 121.1929 | -0.022888 | 121.5134 | 121.3715 | 121.6873 | -0.5722 | -0.59967 | -0.31586 | 0.027466 | 0.32043
2329.5781 | 122.1039 | -121.2936 | 0.58594 | 0.0021796 | 0.0027874 | -0.0077923 | 0.025289 | -0.0069885 | -0.0032959 | 0.0038859 | 0.28381 | 0.5722 | -0.14191 | 0.09613 | 0.11444 | 0.21057 | -0.050354 | 0.32959 | 0.61798 | -121.6415 | 121.1517 | -0.013732 | 121.5775 | 121.3898 | 121.7377 | -0.4715 | -0.50354 | -0.3479 | 0.032044 | 0.42572
2330.5781 | 122.049 | -121.3394 | 0.60425 | -0.043596 | 0.00236 | -0.0026653 | 0.029348 | -0.0086975 | -0.0028687 | 0.0043131 | 0.13733 | 0.56763 | -0.17395 | 0.050354 | 0.064087 | 0.14191 | 0.059509 | 0.26093 | 0.63629 | -121.669 | 121.1655 | -0.036621 | 121.4767 | 121.3898 | 121.7194 | -0.54016 | -0.5722 | -0.32959 | 0.032044 | 0.31128
2331.5781 | 122.0169 | -121.3623 | 0.62256 | -0.097002 | 0.0034282 | -0.0026653 | 0.027211 | -0.0076293 | -0.0035095 | 0.0053813 | 0.082397 | 0.59509 | -0.20599 | 0 | 0.004578 | 0.073242 | 0.15106 | 0.19226 | 0.67749 | -121.7056 | 121.1563 | -0.027466 | 121.4447 | 121.3623 | 121.7056 | -0.61798 | -0.67291 | -0.34332 | 0.054931 | 0.28839
2332.5781 | 122.0169 | -121.3669 | 0.61798 | 0.025068 | 0.0036418 | -0.0030925 | 0.026571 | -0.0074157 | -0.0030823 | 0.0049541 | 0.073242 | 0.59509 | -0.2243 | -0.004578 | 0.004578 | 0.07782 | 0.14191 | 0.20142 | 0.67291 | -121.7285 | 121.1426 | -0.022888 | 121.4401 | 121.3623 | 121.7239 | -0.6134 | -0.66834 | -0.36163 | 0.054932 | 0.29755
2333.5781 | 122.0352 | -121.3806 | 0.59052 | 0.025068 | 0.0044962 | -0.0015971 | 0.027852 | -0.0074157 | -0.0032959 | 0.0053813 | 0.091553 | 0.59509 | -0.21057 | -0.004578 | 0.009155 | 0.07782 | 0.12817 | 0.19226 | 0.66834 | -121.6965 | 121.17 | 0.004578 | 121.4722 | 121.376 | 121.6919 | -0.58136 | -0.65918 | -0.31586 | 0.07782 | 0.30212
2334.5781 | 122.0215 | -121.3943 | 0.61798 | -0.051226 | 0.0027874 | 0.00011194 | 0.027211 | -0.0084839 | -0.0020141 | 0.0055949 | 0.09613 | 0.56305 | -0.19226 | -0.009155 | 0.004578 | 0.073242 | 0.12817 | 0.17853 | 0.6546 | -121.7239 | 121.2021 | -0.054932 | 121.4905 | 121.3852 | 121.7148 | -0.6134 | -0.65002 | -0.32959 | 0.036621 | 0.28839
2335.5781 | 122.0352 | -121.3989 | 0.60883 | -0.066485 | 0.0055644 | -0.00052906 | 0.027639 | -0.0080567 | -0.0037231 | 0.0038859 | 0.10986 | 0.56763 | -0.20142 | 0.009155 | -0.004578 | 0.07782 | 0.12817 | 0.18768 | 0.66834 | -121.7239 | 121.1975 | -0.041199 | 121.5088 | 121.4081 | 121.7331 | -0.6134 | -0.67291 | -0.32501 | 0.059509 | 0.31128
2336.5781 | 122.1451 | -121.3715 | 0.5722 | -0.20381 | 0.0017192 | -0.0018107 | 0.026571 | -0.0054931 | -0.0037231 | 0.0038859 | 0.1831 | 0.50812 | -0.16479 | 0.082397 | 0.07782 | 0.18768 | 0 | 0.31128 | 0.60883 | -121.7194 | 121.2067 | -0.064087 | 121.5546 | 121.4539 | 121.8018 | -0.49438 | -0.53101 | -0.3479 | 0.036621 | 0.3479
2337.5781 | 122.0627 | -121.4127 | 0.58594 | -0.066485 | 0.0019328 | -0.0026653 | 0.02892 | -0.0080567 | -0.0032959 | 0.0017497 | 0.16022 | 0.56763 | -0.14191 | 0.022888 | 0.009155 | 0.086975 | 0.10529 | 0.21057 | 0.65918 | -121.7422 | 121.2708 | -0.01831 | 121.5729 | 121.4355 | 121.7651 | -0.57678 | -0.65002 | -0.32959 | 0.073243 | 0.30212
2338.5781 | 122.0444 | -121.4127 | 0.59509 | -0.035967 | 0.0049236 | -0.0035197 | 0.028493 | -0.0072021 | -0.0058593 | 0.0040995 | 0.13275 | 0.57678 | -0.17395 | 0 | -0.018311 | 0.050354 | 0.15106 | 0.19226 | 0.65918 | -121.7926 | 121.2387 | -0.018311 | 121.5454 | 121.4127 | 121.7926 | -0.6134 | -0.67749 | -0.37994 | 0.064087 | 0.3067
2339.5781 | 122.0261 | -121.4493 | 0.59052 | -0.051226 | 0.0036418 | -0.0033061 | 0.027852 | -0.0072021 | -0.0043641 | 0.0028177 | 0.09613 | 0.58136 | -0.16937 | -0.036621 | -0.018311 | 0.064087 | 0.16479 | 0.1831 | 0.6546 | -121.8063 | 121.2799 | -0.009155 | 121.5454 | 121.4127 | 121.7697 | -0.60883 | -0.67291 | -0.35706 | 0.064087 | 0.2655
2340.5781 | 122.0627 | -121.4401 | 0.59052 | 0.025068 | 0.0038554 | -0.0037333 | 0.026571 | -0.0061341 | -0.0056457 | 0.0053813 | 0.10986 | 0.59052 | -0.17395 | -0.018311 | 0 | 0.054932 | 0.15564 | 0.18768 | 0.66376 | -121.7834 | 121.2662 | 0 | 121.55 | 121.4218 | 121.7651 | -0.59052 | -0.66376 | -0.34332 | 0.073242 | 0.28381
2341.5781 | 122.0581 | -121.4264 | 0.59052 | -0.051226 | 0.0055644 | -0.0041607 | 0.026784 | -0.0059203 | -0.0039367 | 0.0026041 | 0.11902 | 0.5722 | -0.15564 | -0.013733 | -0.009155 | 0.064087 | 0.15106 | 0.19226 | 0.64545 | -121.8109 | 121.2708 | -0.01831 | 121.5454 | 121.4127 | 121.7972 | -0.59967 | -0.6546 | -0.38452 | 0.054932 | 0.27466
2342.5781 | 122.1222 | -121.4035 | 0.57678 | -0.043596 | 0.0032146 | -0.0039469 | 0.026357 | -0.0054931 | -0.0043641 | 0.0036723 | 0.19684 | 0.52643 | -0.1236 | 0.073242 | 0.068665 | 0.15564 | 0.050354 | 0.28381 | 0.63171 | -121.756 | 121.2799 | -0.050354 | 121.6003 | 121.4767 | 121.8292 | -0.50812 | -0.56305 | -0.35248 | 0.054932 | 0.32043
2343.5781 | 122.1542 | -121.4355 | 0.56763 | -0.0054494 | 0.00236 | -0.0048015 | 0.026998 | -0.0072021 | -0.0028687 | 0.0047403 | 0.17853 | 0.52643 | -0.1236 | 0.086975 | 0.091553 | 0.16022 | 0.032043 | 0.28839 | 0.62256 | -121.7651 | 121.312 | -0.041199 | 121.6141 | 121.5225 | 121.8521 | -0.47607 | -0.53101 | -0.32959 | 0.054932 | 0.30212
2344.5781 | 122.081 | -121.4493 | 0.58136 | -0.066485 | 0.0036418 | -0.0024517 | 0.027639 | -0.0078431 | -0.0030823 | 0.0051677 | 0.11902 | 0.54932 | -0.1831 | -0.009155 | 0 | 0.086975 | 0.11902 | 0.20599 | 0.64545 | -121.8201 | 121.2662 | -0.032044 | 121.5683 | 121.4401 | 121.8109 | -0.58136 | -0.64545 | -0.37079 | 0.064087 | 0.30212
2345.5781 | 122.1313 | -121.4172 | 0.62714 | 0.0021796 | 0.007487 | -0.0077923 | 0.029989 | -0.0072021 | -0.0026551 | 0.0028177 | 0.07782 | 0.57678 | -0.20142 | -0.013733 | -0.032043 | 0.059509 | 0.16479 | 0.17853 | 0.64545 | -121.7926 | 121.2158 | -0.050354 | 121.4951 | 121.4035 | 121.7789 | -0.65918 | -0.67749 | -0.37537 | 0.018311 | 0.27924
2346.5781 | 122.081 | -121.4676 | 0.59052 | -0.066485 | 0.0068462 | -0.00095626 | 0.027425 | -0.0072021 | -0.0035095 | 0.0030315 | 0.07782 | 0.56763 | -0.21515 | -0.013733 | -0.018311 | 0.064087 | 0.17395 | 0.17395 | 0.65002 | -121.8384 | 121.2524 | -0.022888 | 121.5454 | 121.4539 | 121.8246 | -0.60883 | -0.66834 | -0.37079 | 0.059509 | 0.29297
2347.5781 | 122.0764 | -121.4767 | 0.5722 | -0.074114 | 0.0055644 | -0.00031526 | 0.024434 | -0.0067749 | -0.0039367 | 0.0028177 | 0.11444 | 0.5722 | -0.16479 | -0.013733 | -0.013733 | 0.064087 | 0.16022 | 0.19226 | 0.65918 | -121.8292 | 121.312 | 0 | 121.5912 | 121.463 | 121.8155 | -0.58594 | -0.67291 | -0.35248 | 0.086975 | 0.27924
2348.5781 | 122.081 | -121.4676 | 0.59052 | -0.043596 | 0.0027874 | -0.0069377 | 0.027211 | -0.0061341 | -0.0047913 | 0.0055949 | 0.10986 | 0.56763 | -0.17395 | -0.013733 | -0.004578 | 0.054932 | 0.16022 | 0.1831 | 0.65002 | -121.8155 | 121.2936 | -0.022888 | 121.5775 | 121.4539 | 121.8018 | -0.59509 | -0.6546 | -0.3479 | 0.059509 | 0.28381
2349.5781 | 122.1542 | -121.4584 | 0.58594 | -0.058855 | 0.00236 | -0.0056559 | 0.024434 | -0.0086975 | -0.0037231 | 0.0055949 | 0.19226 | 0.54932 | -0.11444 | 0.050354 | 0.054932 | 0.15564 | 0.054932 | 0.27008 | 0.64087 | -121.8063 | 121.344 | -0.036621 | 121.6507 | 121.5088 | 121.8567 | -0.53101 | -0.58594 | -0.3479 | 0.054932 | 0.3067
2350.5781 | 122.1725 | -121.4767 | 0.58136 | 0.032698 | 0.0010784 | -0.0013835 | 0.026143 | -0.0095519 | -0.0035095 | 0.0053813 | 0.19684 | 0.53558 | -0.1236 | 0.073242 | 0.054932 | 0.15106 | 0.045776 | 0.27008 | 0.62714 | -121.843 | 121.3531 | -0.045777 | 121.6736 | 121.55 | 121.9162 | -0.52643 | -0.5722 | -0.36621 | 0.045776 | 0.32043
2351.5781 | 122.1451 | -121.4493 | 0.64087 | -0.058855 | 0.00471 | 0.00096634 | 0.02892 | -0.0054931 | -0.0047913 | 0.0051677 | 0.12817 | 0.58136 | -0.15564 | -0.004578 | 0 | 0.009155 | 0.49896 | 0.29755 | 0.68207 | -121.8246 | 121.2936 | -0.059509 | 121.5775 | 121.4447 | 121.8201 | -0.64087 | -0.68207 | -0.37537 | 0.041199 | 0.28381
2352.5781 | 122.1771 | -121.4447 | 0.62256 | -0.066485 | 0.0051372 | -0.0037333 | 0.028707 | -0.0059203 | -0.0037231 | 0.0045267 | 0.11444 | 0.56763 | -0.18768 | -0.022888 | -0.004578 | 0.07782 | 0.16022 | 0.17395 | 0.65002 | -121.8338 | 121.257 | -0.054932 | 121.5591 | 121.4218 | 121.8109 | -0.62714 | -0.6546 | -0.3891 | 0.027465 | 0.30212
2353.5781 | 122.1268 | -121.5088 | 0.59052 | -0.081743 | 0.0025736 | -0.0033061 | 0.02828 | -0.0076293 | -0.0054321 | 0.0034587 | 0.11902 | 0.5722 | -0.16937 | 0 | -0.013733 | 0.07782 | 0.16022 | 0.1831 | 0.63629 | -121.8521 | 121.3394 | -0.01831 | 121.6278 | 121.5088 | 121.8521 | -0.60425 | -0.65002 | -0.34332 | 0.045777 | 0.28839
2354.5781 | 122.1039 | -121.4996 | 0.58594 | -0.081743 | 0.0019328 | -0.0011699 | 0.028493 | -0.0074157 | -0.0005189 | 0.0049541 | 0.11444 | 0.58136 | -0.1831 | -0.013733 | -0.013733 | 0.059509 | 0.14648 | 0.16937 | 0.64545 | -121.8704 | 121.3165 | -0.004577 | 121.6141 | 121.4859 | 121.8567 | -0.59967 | -0.65918 | -0.37079 | 0.05951 | 0.29755
2355.5781 | 122.113 | -121.4996 | 0.60425 | -0.089373 | 0.0051372 | -0.00052906 | 0.027639 | -0.0072021 | -0.0030823 | 0.0047403 | 0.11902 | 0.55847 | -0.14648 | -0.013733 | -0.004578 | 0.059509 | 0.15106 | 0.1831 | 0.65002 | -121.8842 | 121.3531 | -0.045776 | 121.6187 | 121.4859 | 121.8704 | -0.60883 | -0.6546 | -0.38452 | 0.045776 | 0.2655
2356.5781 | 122.1497 | -121.4996 | 0.58594 | -0.066485 | 0.0032146 | 0.00053914 | 0.02593 | -0.0059203 | -0.0035095 | 0.0032451 | 0.1831 | 0.54016 | -0.14648 | 0.054932 | 0.050354 | 0.13733 | 0.068665 | 0.25635 | 0.62714 | -121.8704 | 121.3531 | -0.045776 | 121.6827 | 121.5546 | 121.9254 | -0.53558 | -0.57678 | -0.37079 | 0.041199 | 0.32959
2357.5781 | 122.1954 | -121.4905 | 0.55389 | 0.0098091 | 0.0019328 | -0.0030925 | 0.024862 | -0.0069885 | -0.0039367 | 0.0053813 | 0.19226 | 0.52185 | -0.12817 | 0.073242 | 0.068665 | 0.16022 | 0.054932 | 0.27924 | 0.6134 | -121.843 | 121.3623 | -0.032043 | 121.6827 | 121.5637 | 121.9162 | -0.48523 | -0.54474 | -0.35248 | 0.059509 | 0.32044
2358.5781 | 122.1359 | -121.5591 | 0.5722 | -0.0054494 | 0.00043737 | -0.0015971 | 0.029348 | -0.0078431 | -0.0032959 | 0.0055949 | 0.1236 | 0.54474 | -0.16479 | -0.018311 | -0.009155 | 0.082397 | 0.1236 | 0.19226 | 0.62714 | -121.8887 | 121.3943 | -0.027466 | 121.6827 | 121.5408 | 121.8704 | -0.58136 | -0.63629 | -0.32959 | 0.054931 | 0.28839
2359.5781 | 122.0947 | -121.5042 | 0.60883 | -0.074114 | 0.0038554 | -0.0028789 | 0.027852 | -0.0084839 | -0.0032959 | 0.0060221 | 0.11444 | 0.56305 | -0.16022 | -0.018311 | -0.013733 | 0.059509 | 0.16022 | 0.19684 | 0.6546 | -121.8933 | 121.344 | -0.045777 | 121.6187 | 121.4859 | 121.875 | -0.62256 | -0.66834 | -0.3891 | 0.045776 | 0.27466
2360.5781 | 122.1359 | -121.5271 | 0.58594 | -0.081743 | 0.0053508 | -0.0028789 | 0.026357 | -0.0072021 | -0.0052185 | 0.0051677 | 0.11902 | 0.56305 | -0.18768 | -0.018311 | -0.018311 | 0.068665 | 0.16479 | 0.18768 | 0.63171 | -121.8842 | 121.3394 | -0.022888 | 121.6461 | 121.5088 | 121.8658 | -0.60425 | -0.65002 | -0.35706 | 0.045777 | 0.3067
2361.5781 | 122.1451 | -121.5363 | 0.58594 | -0.058855 | 0.0027874 | 0.00053914 | 0.028066 | -0.0039977 | -0.0013733 | 0.0049541 | 0.10986 | 0.55847 | -0.16937 | -0.004578 | -0.018311 | 0.064087 | 0.14648 | 0.19226 | 0.65918 | -121.8979 | 121.3669 | -0.027465 | 121.6461 | 121.5317 | 121.8933 | -0.60425 | -0.67749 | -0.36163 | 0.073243 | 0.27924
2362.5781 | 122.1542 | -121.5454 | 0.57678 | -0.043596 | 0.0032146 | -0.00052906 | 0.027852 | -0.0069885 | -0.0026551 | 0.0051677 | 0.13275 | 0.55389 | -0.15564 | -0.022888 | -0.013733 | 0.07782 | 0.14648 | 0.18768 | 0.65918 | -121.907 | 121.3898 | -0.022888 | 121.6782 | 121.5225 | 121.8842 | -0.59052 | -0.67291 | -0.36163 | 0.082398 | 0.28839
2363.5781 | 122.2458 | -121.5225 | 0.5722 | -0.028338 | 0.001292 | 0.00075274 | 0.026143 | -0.0072021 | -0.0028687 | 0.0034587 | 0.19684 | 0.54932 | -0.12817 | 0.082397 | 0.07782 | 0.16479 | 0.022888 | 0.28381 | 0.61798 | -121.8704 | 121.3943 | -0.022889 | 121.7194 | 121.6049 | 121.9528 | -0.49438 | -0.54016 | -0.3479 | 0.045776 | 0.32501
2364.5781 | 122.2366 | -121.5134 | 0.55847 | -0.074114 | 0.0034282 | -0.0015971 | 0.026357 | -0.0086975 | -0.0039367 | 0.0053813 | 0.21515 | 0.51727 | -0.11902 | 0.07782 | 0.082397 | 0.17395 | 0.009155 | 0.31128 | 0.61798 | -121.8658 | 121.3943 | -0.041199 | 121.7285 | 121.5912 | 121.9437 | -0.47607 | -0.53558 | -0.35248 | 0.059509 | 0.33417
2365.5781 | 122.1725 | -121.5775 | 0.5722 | -0.074114 | 0.0064188 | -0.0011699 | 0.030202 | -0.0069885 | -0.0009461 | 0.0043131 | 0.11902 | 0.55389 | -0.1831 | -0.018311 | -0.022888 | 0.073242 | 0.15106 | 0.17853 | 0.63629 | -121.9299 | 121.3943 | -0.018311 | 121.6965 | 121.5591 | 121.9116 | -0.59509 | -0.65918 | -0.35248 | 0.064087 | 0.30212
2366.5781 | 122.1634 | -121.582 | 0.57678 | -0.089373 | 0.0049236 | -0.00095626 | 0.029775 | -0.0057067 | -0.0032959 | 0.0070903 | 0.12817 | 0.56305 | -0.16937 | -0.009155 | 0 | 0.068665 | 0.16479 | 0.19226 | 0.63171 | -121.9299 | 121.4127 | -0.013733 | 121.7102 | 121.5729 | 121.9208 | -0.57678 | -0.63171 | -0.3479 | 0.054932 | 0.29755
2367.5781 | 122.1588 | -121.5683 | 0.57678 | -0.0054494 | 0.0034282 | -0.0045879 | 0.030202 | -0.0072021 | -0.0039367 | 0.0038859 | 0.11902 | 0.56305 | -0.17853 | -0.004578 | -0.004578 | 0.059509 | 0.14648 | 0.19226 | 0.64087 | -121.9116 | 121.3898 | -0.013733 | 121.6873 | 121.5637 | 121.907 | -0.58136 | -0.64545 | -0.34332 | 0.064087 | 0.29755
2368.5781 | 122.1634 | -121.5775 | 0.56305 | 0.26158 | 0.0051372 | 0.0043843 | 0.034261 | -0.0042115 | -0.0035095 | 0.0028177 | 0.15106 | 0.55847 | -0.16479 | -0.018311 | -0.027466 | 0.050354 | 0.027466 | 0.1236 | 0.63629 | -121.9437 | 121.4127 | -0.004577 | 121.7285 | 121.5591 | 121.9254 | -0.59052 | -0.66376 | -0.36621 | 0.073243 | 0.31586
2369.5781 | 122.1634 | -121.5958 | 0.58136 | -0.10463 | 0.0042826 | -0.00010166 | 0.025716 | -0.0059203 | -0.0043641 | 0.0058085 | 0.1236 | 0.55389 | -0.14648 | -0.013733 | 0 | 0.07782 | 0.14191 | 0.18768 | 0.6546 | -121.9437 | 121.4493 | -0.027466 | 121.7194 | 121.582 | 121.9299 | -0.58136 | -0.6546 | -0.3479 | 0.073242 | 0.27008
2370.5781 | 122.2366 | -121.5363 | 0.55389 | 0.047956 | 1.0171e-05 | 0.00075274 | 0.024648 | -0.0048523 | -0.0022277 | 0.0043131 | 0.20142 | 0.49896 | -0.11902 | 0.07782 | 0.09613 | 0.16937 | 0.018311 | 0.28839 | 0.6134 | -121.9208 | 121.4172 | -0.054932 | 121.7377 | 121.6141 | 121.9986 | -0.45776 | -0.51727 | -0.38452 | 0.059509 | 0.32044
2371.5781 | 122.2687 | -121.5775 | 0.56763 | 0.29973 | 0.0032146 | 0.0011799 | 0.026143 | -0.0080567 | -0.0032959 | 0.0038859 | 0.20142 | 0.52643 | -0.15106 | 0.082397 | 0.10071 | 0.17853 | 0.009155 | 0.31128 | 0.60425 | -121.8887 | 121.4264 | -0.041199 | 121.7789 | 121.6599 | 121.9711 | -0.46692 | -0.50354 | -0.31128 | 0.036621 | 0.35248
2372.5781 | 122.168 | -121.5866 | 0.57678 | -0.089373 | 0.0049236 | -0.0041607 | 0.02892 | -0.0069885 | -0.0007325 | 0.0047403 | 0.11902 | 0.55847 | -0.16479 | -0.013733 | -0.009155 | 0.068665 | 0.15564 | 0.19226 | 0.63629 | -121.9894 | 121.4218 | -0.01831 | 121.7056 | 121.5729 | 121.9757 | -0.58594 | -0.64545 | -0.40283 | 0.05951 | 0.28381
2373.5781 | 122.1863 | -121.5729 | 0.58594 | -0.058855 | 0.0036418 | -0.0035197 | 0.029348 | -0.0050659 | -0.0045777 | 0.0036723 | 0.11444 | 0.55389 | -0.17395 | -0.013733 | -0.027466 | 0.059509 | 0.16022 | 0.1831 | 0.63171 | -121.9574 | 121.3989 | -0.032043 | 121.6873 | 121.5591 | 121.9437 | -0.6134 | -0.65918 | -0.38452 | 0.045777 | 0.28839
2374.5781 | 122.1909 | -121.5866 | 0.59052 | -0.081743 | 0.0021464 | -0.0039469 | 0.02828 | -0.0050659 | -0.0020141 | 0.0034587 | 0.10529 | 0.55847 | -0.17853 | -0.013733 | -0.013733 | 0.059509 | 0.16937 | 0.18768 | 0.64545 | -121.962 | 121.4081 | -0.032043 | 121.6919 | 121.5729 | 121.9482 | -0.60425 | -0.65918 | -0.37537 | 0.054932 | 0.28381
2375.5781 | 122.2046 | -121.5912 | 0.56305 | -0.020708 | 0.0032146 | -0.00052906 | 0.027852 | -0.0080567 | -0.0028687 | 0.0034587 | 0.11444 | 0.55389 | -0.16022 | -0.022888 | -0.009155 | 0.082397 | 0.14648 | 0.18768 | 0.64087 | -121.9666 | 121.431 | -0.009155 | 121.7056 | 121.5683 | 121.9437 | -0.5722 | -0.65002 | -0.37537 | 0.07782 | 0.27466
2376.5781 | 122.2046 | -121.6141 | 0.56763 | -0.020708 | 0.0055644 | 0.00032554 | 0.026143 | -0.0054931 | -0.0018005 | 0.0051677 | 0.10529 | 0.54016 | -0.17853 | -0.018311 | -0.004578 | 0.045776 | 0.14648 | 0.1831 | 0.63629 | -121.9574 | 121.4355 | -0.027466 | 121.7194 | 121.5958 | 121.9391 | -0.5722 | -0.64087 | -0.34332 | 0.068665 | 0.28381
2377.5781 | 122.2549 | -121.5729 | 0.55389 | -0.081743 | 0.0042826 | -0.0043743 | 0.024221 | -0.0059203 | -0.0032959 | 0.0040995 | 0.17853 | 0.53101 | -0.13733 | 0.054932 | 0.045776 | 0.13733 | 0.07782 | 0.27466 | 0.63171 | -121.9528 | 121.4355 | -0.022888 | 121.7514 | 121.6278 | 122.0078 | -0.50812 | -0.58594 | -0.37994 | 0.07782 | 0.31586
2378.5781 | 122.2595 | -121.5912 | 0.55847 | -0.043596 | 0.00086457 | -0.0018107 | 0.025289 | -0.0072021 | -0.0020141 | 0.0051677 | 0.19226 | 0.53558 | -0.1236 | 0.050354 | 0.054932 | 0.13733 | 0.054932 | 0.26093 | 0.60425 | -121.962 | 121.4676 | -0.022889 | 121.7834 | 121.6415 | 122.0123 | -0.50354 | -0.54932 | -0.37079 | 0.045776 | 0.31586
2379.5781 | 122.2229 | -121.6232 | 0.55847 | -0.043596 | 0.0042826 | -0.0018107 | 0.031057 | -0.0065613 | -0.0041503 | 0.0043131 | 0.19226 | 0.56305 | -0.16479 | -0.027466 | -0.004578 | 0.09613 | 0.068665 | 0.17853 | 0.65918 | -121.9803 | 121.4584 | 0.004577 | 121.8155 | 121.5958 | 121.9528 | -0.56305 | -0.66376 | -0.35706 | 0.10071 | 0.35706
2380.5781 | 122.2321 | -121.5958 | 0.57678 | -0.043596 | 0.0044962 | -0.0056559 | 0.030416 | -0.0039977 | -0.0022277 | 0.0034587 | 0.11444 | 0.55847 | -0.17853 | 0.004578 | -0.059509 | 0.064087 | 0.14648 | 0.14648 | 0.66376 | -121.994 | 121.4172 | -0.01831 | 121.7102 | 121.6003 | 121.9986 | -0.63629 | -0.72327 | -0.39825 | 0.086975 | 0.29297
2381.5781 | 122.2137 | -121.6232 | 0.59052 | -0.035967 | 0.0038554 | -0.0035197 | 0.024648 | -0.0061341 | 0.0003357 | 0.0051677 | 0.11902 | 0.55389 | -0.17395 | -0.027466 | 0.059509 | 0.082397 | 0.091553 | 0.20142 | 0.66376 | -121.9757 | 121.4493 | -0.036621 | 121.7422 | 121.5958 | 121.9482 | -0.53101 | -0.60425 | -0.35248 | 0.073242 | 0.29297
2382.5781 | 122.2412 | -121.6003 | 0.60883 | -0.066485 | 0.0049236 | -0.0028789 | 0.027852 | -0.0059203 | -0.0047913 | 0.0055949 | 0.11902 | 0.56763 | -0.17853 | -0.064087 | -0.15106 | 0.041199 | 0.16022 | 0.1236 | 0.67749 | -121.9849 | 121.4218 | -0.041199 | 121.7194 | 121.5363 | 121.9208 | -0.75989 | -0.82855 | -0.38452 | 0.068664 | 0.29755
2383.5781 | 122.2458 | -121.6187 | 0.56763 | -0.21907 | 0.0049236 | -0.0033061 | 0.029989 | -0.0020751 | -0.0013733 | 0.0045267 | 0.13275 | 0.55847 | -0.16022 | -0.018311 | -0.036621 | 0.073242 | -0.036621 | 0.14648 | 0.63629 | -121.962 | 121.4584 | -0.009155 | 121.7514 | 121.6003 | 121.9437 | -0.60425 | -0.67291 | -0.34332 | 0.068665 | 0.29297
2384.5781 | 122.2275 | -121.6187 | 0.5722 | -0.0054494 | 0.0021464 | -0.0011699 | 0.024648 | -0.0065613 | -0.0024415 | 0.0062357 | 0.12817 | 0.55847 | -0.15564 | 0 | 0.009155 | 0.064087 | 0.1236 | 0.21057 | 0.63171 | -121.994 | 121.463 | -0.013733 | 121.7468 | 121.6187 | 121.994 | -0.56305 | -0.62256 | -0.37537 | 0.059509 | 0.28381
2385.5781 | 122.2366 | -121.6599 | 0.57678 | -0.035967 | 0.003001 | -0.0028789 | 0.026998 | -0.0057067 | -0.0043641 | 0.0030315 | 0.13733 | 0.55389 | -0.16022 | -0.009155 | 0.009155 | 0.073242 | 0.13275 | 0.19226 | 0.64087 | -122.0032 | 121.4996 | -0.022888 | 121.7972 | 121.6507 | 121.994 | -0.56763 | -0.63171 | -0.34332 | 0.064087 | 0.29755
2386.5781 | 122.2687 | -121.637 | 0.55847 | 0.0021796 | 0.0010784 | 0.00053914 | 0.030202 | -0.0072021 | -0.0018005 | 0.0053813 | 0.14191 | 0.56763 | -0.16937 | 0.004578 | 0.009155 | 0.07782 | 0.10529 | 0.19684 | 0.62714 | -122.0078 | 121.4676 | 0.009155 | 121.7789 | 121.6415 | 122.0123 | -0.54932 | -0.61798 | -0.37079 | 0.068664 | 0.31128
2387.5781 | 122.2824 | -121.6324 | 0.55389 | -0.013079 | 0.0032146 | -0.00052906 | 0.029134 | -0.0052795 | -0.0020141 | 0.0055949 | 0.13275 | 0.56763 | -0.16937 | 0.004578 | -0.004578 | 0.07782 | 0.11444 | 0.18768 | 0.62714 | -122.0078 | 121.463 | 0.013733 | 121.7651 | 121.637 | 122.0123 | -0.55847 | -0.63171 | -0.37537 | 0.073242 | 0.30212
2388.5781 | 122.2824 | -121.6644 | 0.55389 | -0.035967 | 0.00471 | -0.00010166 | 0.030629 | -0.0042115 | -0.0045777 | 0.0068767 | 0.13733 | 0.56305 | -0.17395 | -0.013733 | -0.009155 | 0.07782 | 0.1236 | 0.18768 | 0.62714 | -122.0352 | 121.4905 | 0.009155 | 121.8018 | 121.6507 | 122.0215 | -0.56305 | -0.63629 | -0.37079 | 0.073242 | 0.31128
2389.5781 | 122.2183 | -121.6049 | 0.59967 | -0.058855 | 0.0068462 | -0.00031526 | 0.025502 | -0.0050659 | -0.0041503 | 0.0047403 | 0.11444 | 0.56763 | -0.19226 | -0.022888 | -0.004578 | 0.059509 | 0.15564 | 0.21057 | 0.65002 | -121.9803 | 121.4127 | -0.032043 | 121.7194 | 121.582 | 121.9574 | -0.60425 | -0.6546 | -0.37537 | 0.050354 | 0.3067
2390.5781 | 122.287 | -121.6827 | 0.55389 | -0.051226 | 0.0044962 | 0.00075274 | 0.027639 | -0.0057067 | -0.0058593 | 0.0055949 | 0.12817 | 0.56305 | -0.17395 | 0.009155 | -0.009155 | 0.064087 | 0.11444 | 0.17395 | 0.60883 | -122.0398 | 121.5088 | 0.009155 | 121.8109 | 121.6919 | 122.049 | -0.56305 | -0.61798 | -0.35706 | 0.054932 | 0.30212
2391.5781 | 122.168 | -121.6415 | 0.59509 | -0.097002 | 0.0064188 | -0.0030925 | 0.027211 | -0.0063477 | -0.0047913 | 0.0055949 | 0.1236 | 0.55847 | -0.17853 | -0.027466 | -0.018311 | 0.068665 | 0.17395 | 0.5127 | 0.67749 | -121.962 | 121.463 | -0.036621 | 121.7651 | 121.6141 | 121.9345 | -0.6134 | -0.6958 | -0.32043 | 0.082397 | 0.30212
2392.5781 | 122.2229 | -121.6324 | 0.59509 | -0.074114 | 0.0072734 | -0.0039469 | 0.026357 | -0.0035705 | -0.0035095 | 0.0047403 | 0.13275 | 0.56305 | -0.17395 | -0.009155 | -0.013733 | 0.054932 | 0.4303 | 0.42572 | 0.6546 | -121.9666 | 121.4584 | -0.032044 | 121.7651 | 121.6232 | 121.9574 | -0.60883 | -0.66834 | -0.33417 | 0.059509 | 0.3067
2393.5781 | 122.3053 | -121.6461 | 0.56305 | 0.070845 | 0.0083416 | -0.00052906 | 0.029134 | -0.0018615 | -0.0043641 | 0.0038859 | 0.20142 | 0.54474 | -0.15106 | 0.041199 | 0.022888 | 0.10986 | 0.054932 | 0.21973 | 0.62714 | -122.0535 | 121.4951 | -0.01831 | 121.8475 | 121.6873 | 122.0947 | -0.54016 | -0.60425 | -0.40741 | 0.064087 | 0.35248
2394.5781 | 122.2916 | -121.6644 | 0.55847 | 0.078474 | 0.0062052 | 0.0022481 | 0.028493 | -0.0044251 | -0.0030823 | 0.0053813 | 0.20142 | 0.56763 | -0.19684 | 0.036621 | 0.013733 | 0.10529 | 0.064087 | 0.21515 | 0.60883 | -122.0078 | 121.4676 | 0.009155 | 121.8658 | 121.701 | 122.0444 | -0.54474 | -0.59509 | -0.34332 | 0.050354 | 0.39825
2395.5781 | 122.2824 | -121.6782 | 0.55389 | 0.047956 | 0.0066326 | 0.0026753 | 0.028493 | -0.0033569 | -0.0039367 | 0.0049541 | 0.12817 | 0.54474 | -0.1831 | 0 | -0.004578 | 0.082397 | 0.11902 | 0.19226 | 0.6134 | -122.0535 | 121.4951 | -0.009155 | 121.8063 | 121.6782 | 122.0535 | -0.55847 | -0.61798 | -0.37537 | 0.059509 | 0.31128
2396.5781 | 122.3099 | -121.6736 | 0.56763 | 0.040327 | 0.0049236 | 0.0018209 | 0.029989 | -0.0048523 | -0.0022277 | 0.0053813 | 0.18768 | 0.54474 | -0.17395 | 0.036621 | 0.018311 | 0.1236 | 0.054932 | 0.2243 | 0.63171 | -122.0444 | 121.4996 | -0.022888 | 121.8613 | 121.7102 | 122.081 | -0.54932 | -0.6134 | -0.37079 | 0.064087 | 0.36163
2397.5781 | 122.2504 | -121.6736 | 0.59509 | -0.066485 | 0.0077006 | -0.0024517 | 0.025289 | -0.0042115 | -0.0037231 | 0.0049541 | 0.12817 | 0.56305 | -0.17395 | 0.18768 | 0.19684 | 0.073242 | 0.086975 | 0.27924 | 0.65918 | -122.0444 | 121.4996 | -0.032044 | 121.8018 | 121.8613 | 122.2321 | -0.39825 | -0.46234 | -0.37079 | 0.064087 | 0.30212
2398.5781 | 122.287 | -121.6873 | 0.54932 | 0.032698 | 0.007487 | 0.0035299 | 0.02828 | -0.0048523 | -0.0039367 | 0.0030315 | 0.11902 | 0.56305 | -0.16479 | -0.018311 | 0 | 0.082397 | 0.09613 | 0.20599 | 0.64087 | -122.0856 | 121.5225 | 0.013733 | 121.8063 | 121.669 | 122.0673 | -0.54932 | -0.64087 | -0.39825 | 0.091553 | 0.28381
2399.5781 | 122.3053 | -121.701 | 0.53558 | 0.047956 | 0.0049236 | 0.0018209 | 0.02892 | -0.0048523 | -0.0018005 | 0.0049541 | 0.13275 | 0.54932 | -0.17853 | 0.013733 | 0.013733 | 0.086975 | 0.10529 | 0.19226 | 0.61798 | -122.0856 | 121.5225 | 0.013733 | 121.8338 | 121.7148 | 122.0993 | -0.52185 | -0.60425 | -0.38452 | 0.082398 | 0.31128
2400.5781 | 122.3145 | -121.6461 | 0.54474 | 0.54387 | 0.0066326 | 0.00053914 | 0.029775 | -0.0048523 | -0.0013733 | 0.0034587 | 0.2243 | 0.59509 | -0.1236 | 0.022888 | 0.018311 | 0.082397 | 0.027466 | 0.20599 | 0.60883 | -122.049 | 121.5225 | 0.050354 | 121.8704 | 121.669 | 122.0718 | -0.52643 | -0.59052 | -0.40283 | 0.064087 | 0.3479
2401.5781 | 122.3236 | -121.6873 | 0.54474 | 0.086103 | 0.0062052 | 0.0054525 | 0.030629 | -0.0046387 | -0.0035095 | 0.0066629 | 0.17853 | 0.53558 | -0.16479 | 0.027466 | 0.022888 | 0.10529 | 0.041199 | 0.21515 | 0.6134 | -122.0718 | 121.5225 | -0.009156 | 121.8658 | 121.7148 | 122.0993 | -0.52185 | -0.59052 | -0.38452 | 0.068664 | 0.34332
2402.5781 | 122.319 | -121.6873 | 0.54016 | 0.12425 | 0.007487 | 0.0028889 | 0.02828 | -0.0025025 | -0.0005189 | 0.0045267 | 0.20142 | 0.59052 | -0.12817 | 0.004578 | 0.018311 | 0.10071 | 0.018311 | 0.20142 | 0.61798 | -122.0627 | 121.5591 | 0.050354 | 121.8887 | 121.6919 | 122.0673 | -0.52185 | -0.59967 | -0.37537 | 0.07782 | 0.32959
2403.5781 | 122.3236 | -121.6919 | 0.54474 | 0.10136 | 0.0070598 | 0.0052387 | 0.031484 | -0.0044251 | 0.0001221 | 0.0070903 | 0.18768 | 0.55389 | -0.16479 | 0.032043 | 0.032043 | 0.10986 | 0.045776 | 0.2243 | 0.61798 | -122.0856 | 121.5271 | 0.009155 | 121.8796 | 121.7239 | 122.1176 | -0.5127 | -0.58594 | -0.39368 | 0.073242 | 0.35248
2404.5781 | 122.3099 | -121.6644 | 0.54016 | -0.10463 | 0.0083416 | 0.0016073 | 0.031057 | -0.0035705 | -0.0028687 | 0.0030315 | 0.18768 | 0.59509 | -0.14648 | 0.018311 | 0.013733 | 0.10986 | 0.009155 | 0.19226 | 0.63171 | -122.0764 | 121.5179 | 0.054932 | 121.8521 | 121.6827 | 122.0947 | -0.52643 | -0.61798 | -0.41199 | 0.091553 | 0.33417
2405.5781 | 122.3465 | -121.7056 | 0.55389 | 0.086103 | 0.0059916 | 0.0020345 | 0.030416 | -0.00079352 | -0.0054321 | 0.0053813 | 0.17853 | 0.54932 | -0.1831 | 0.027466 | 0.022888 | 0.10071 | 0.041199 | 0.20599 | 0.62714 | -122.0901 | 121.5225 | -0.004578 | 121.8842 | 121.7331 | 122.1176 | -0.53101 | -0.60425 | -0.38452 | 0.073242 | 0.36163
2406.5781 | 122.3007 | -121.6965 | 0.55847 | -0.1733 | 0.0038554 | -0.0020243 | 0.030416 | -0.0035705 | -0.0024415 | 0.0058085 | 0.17853 | 0.60883 | -0.091553 | 0 | 0.013733 | 0.10986 | 0.018311 | 0.21057 | 0.61798 | -122.0993 | 121.6049 | 0.050354 | 121.875 | 121.6965 | 122.0993 | -0.54474 | -0.60425 | -0.40283 | 0.059509 | 0.27008
2407.5781 | 122.3007 | -121.7194 | 0.55389 | 0.26921 | 0.00471 | 0.0069477 | 0.030202 | 0.00027468 | -0.0015869 | 0.0034587 | 0.14191 | 0.54932 | -0.19684 | -0.050354 | -0.032043 | 0.050354 | 0.036621 | 0.13275 | 0.61798 | -122.113 | 121.5225 | -0.004578 | 121.8613 | 121.669 | 122.0627 | -0.58594 | -0.65002 | -0.39368 | 0.064087 | 0.33875
2408.5781 | 122.2916 | -121.7102 | 0.55389 | 0.2158 | 0.0059916 | -0.0013835 | 0.029989 | -0.0018615 | -0.0039367 | 0.0049541 | 0.13733 | 0.55389 | -0.17853 | -0.045776 | -0.041199 | 0.041199 | 0.041199 | 0.14648 | 0.62714 | -122.1268 | 121.5317 | 0 | 121.8475 | 121.6644 | 122.081 | -0.59509 | -0.66834 | -0.41656 | 0.073242 | 0.31586
2409.5781 | 122.3053 | -121.7422 | 0.54474 | 0.20054 | 0.0051372 | 0.00032554 | 0.029134 | -0.0018615 | -0.0026551 | 0.0055949 | 0.13733 | 0.53558 | -0.17853 | -0.045776 | -0.036621 | 0.041199 | 0.041199 | 0.14648 | 0.6134 | -122.1405 | 121.5637 | -0.009156 | 121.8796 | 121.6965 | 122.0947 | -0.58136 | -0.65002 | -0.39825 | 0.068664 | 0.31586
2410.5781 | 122.3007 | -121.7148 | 0.54474 | 0.25395 | 0.0079142 | 0.0022481 | 0.033193 | -0.0039977 | -0.0020141 | 0.0047403 | 0.12817 | 0.53558 | -0.17395 | -0.041199 | -0.045776 | 0.036621 | 0.036621 | 0.13275 | 0.60425 | -122.1405 | 121.5408 | -0.009156 | 121.843 | 121.6736 | 122.0993 | -0.59052 | -0.65002 | -0.42572 | 0.059509 | 0.30212
2411.5781 | 122.3419 | -121.7148 | 0.54016 | -0.066485 | 0.0079142 | 0.00096634 | 0.029561 | -0.0039977 | -0.0018005 | 0.0053813 | 0.16937 | 0.59967 | -0.13275 | 0.004578 | 0.022888 | 0.10986 | 0.036621 | 0.20599 | 0.63171 | -122.1359 | 121.582 | 0.059509 | 121.8842 | 121.7194 | 122.1405 | -0.51727 | -0.60883 | -0.42114 | 0.091553 | 0.30212
2412.5781 | 122.3602 | -121.6782 | 0.53101 | 0.55913 | 0.0062052 | 0.0018209 | 0.02892 | -0.0031433 | -0.0020141 | 0.0032451 | 0.20142 | 0.60883 | -0.11902 | 0 | 0.013733 | 0.10986 | 0.013733 | 0.20599 | 0.62714 | -122.1268 | 121.5591 | 0.07782 | 121.8796 | 121.6782 | 122.1268 | -0.51727 | -0.6134 | -0.44861 | 0.09613 | 0.32044
2413.5781 | 122.3053 | -121.756 | 0.54016 | 0.26158 | 0.0068462 | 0.0037435 | 0.029989 | -0.0029297 | -0.0013733 | 0.0038859 | 0.1236 | 0.55389 | -0.19684 | -0.045776 | -0.050354 | 0.054932 | 0.036621 | 0.14648 | 0.59967 | -122.1634 | 121.5591 | 0.013733 | 121.8796 | 121.7102 | 122.1176 | -0.59052 | -0.65002 | -0.40741 | 0.059509 | 0.32043
2414.5781 | 122.3145 | -121.7422 | 0.54474 | 0.3455 | 0.0066326 | 0.0016073 | 0.029348 | -0.0027161 | -0.0005189 | 0.0060221 | 0.10071 | 0.54016 | -0.19226 | -0.064087 | -0.054932 | 0.064087 | 0.004578 | 0.11444 | 0.6134 | -122.1405 | 121.55 | -0.004578 | 121.843 | 121.6782 | 122.0764 | -0.59967 | -0.66834 | -0.39825 | 0.068664 | 0.29297
2415.5781 | 122.3236 | -121.7285 | 0.54016 | 0.36076 | 0.0070598 | 0.0048115 | 0.029775 | -0.0035705 | -0.0026551 | 0.0047403 | 0.091553 | 0.56763 | -0.19226 | -0.041199 | -0.032043 | 0.054932 | 0.004578 | 0.12817 | 0.62256 | -122.1542 | 121.5363 | 0.027466 | 121.8201 | 121.6873 | 122.113 | -0.5722 | -0.6546 | -0.42572 | 0.082398 | 0.28381
2416.5781 | 122.2961 | -121.7422 | 0.52643 | 0.29973 | 0.009196 | 0.0020345 | 0.030416 | -0.0029297 | -0.0032959 | 0.0062357 | 0.091553 | 0.53558 | -0.21515 | -0.045776 | -0.059509 | 0.050354 | 0.009155 | 0.13733 | 0.61798 | -122.168 | 121.5271 | 0.009155 | 121.8338 | 121.6965 | 122.1222 | -0.58594 | -0.67749 | -0.42572 | 0.091553 | 0.3067
2417.5781 | 122.3236 | -121.7651 | 0.54474 | 0.33024 | 0.0064188 | -0.00074266 | 0.027211 | -0.0031433 | -0.0020141 | 0.0058085 | 0.082397 | 0.55847 | -0.19226 | -0.059509 | -0.050354 | 0.050354 | -0.013733 | 0.11902 | 0.61798 | -122.1725 | 121.5729 | 0.013733 | 121.8475 | 121.7056 | 122.113 | -0.59509 | -0.66834 | -0.40741 | 0.073242 | 0.27466
2418.5781 | 122.319 | -121.7285 | 0.52643 | 0.24632 | 0.0066326 | -0.0030925 | 0.027639 | -0.0027161 | -0.0020141 | 0.0040995 | 0.1236 | 0.54474 | -0.20599 | -0.036621 | -0.032043 | 0.050354 | 0.041199 | 0.15106 | 0.60425 | -122.1405 | 121.5225 | 0.018311 | 121.8521 | 121.6919 | 122.1039 | -0.55847 | -0.63629 | -0.41199 | 0.07782 | 0.32959
2419.5781 | 122.3053 | -121.7743 | 0.53558 | 0.26158 | 0.0064188 | 0.0028889 | 0.031484 | -0.0022889 | -0.0013733 | 0.0053813 | 0.1236 | 0.52185 | -0.20142 | -0.050354 | -0.045776 | 0.041199 | 0.022888 | 0.14648 | 0.6134 | -122.1634 | 121.5729 | -0.013732 | 121.8979 | 121.7239 | 122.113 | -0.58136 | -0.65918 | -0.3891 | 0.07782 | 0.32501
2420.5781 | 122.3785 | -121.7422 | 0.53558 | 0.50572 | 0.0064188 | -0.00031526 | 0.02892 | -0.0033569 | -0.0022277 | 0.0049541 | 0.13275 | 0.54932 | -0.1831 | -0.050354 | -0.032043 | 0.086975 | -0.022888 | 0.16937 | 0.61798 | -122.1634 | 121.5591 | 0.013733 | 121.875 | 121.6919 | 122.113 | -0.56763 | -0.65002 | -0.42114 | 0.082398 | 0.31586
2421.5781 | 122.3648 | -121.7514 | 0.54932 | 0.53624 | 0.007487 | 0.0071615 | 0.029989 | -0.0048523 | -0.0020141 | 0.0051677 | 0.13733 | 0.56305 | -0.17395 | -0.036621 | -0.022888 | 0.07782 | -0.013733 | 0.14648 | 0.62714 | -122.1542 | 121.5775 | 0.013733 | 121.8887 | 121.7148 | 122.1176 | -0.5722 | -0.65002 | -0.40283 | 0.07782 | 0.31128
2422.5781 | 122.3282 | -121.7422 | 0.54474 | 0.48283 | 0.0072734 | 0.0022481 | 0.027425 | -0.0037841 | -0.0028687 | 0.0055949 | 0.10529 | 0.54474 | -0.19226 | -0.036621 | -0.032043 | 0.073242 | -0.050354 | 0.14191 | 0.60883 | -122.1863 | 121.55 | 0 | 121.8475 | 121.7056 | 122.1497 | -0.57678 | -0.64087 | -0.44403 | 0.064087 | 0.29755
2423.5781 | 122.3694 | -121.7285 | 0.54016 | 0.30736 | 0.0059916 | 0.0016073 | 0.027425 | -0.0067749 | -0.0015869 | 0.0051677 | 0.10986 | 0.54016 | -0.18768 | -0.027466 | -0.036621 | 0.082397 | -0.050354 | 0.15564 | 0.59967 | -122.1725 | 121.5408 | 0 | 121.8384 | 121.701 | 122.1451 | -0.57678 | -0.63629 | -0.44403 | 0.059509 | 0.29755
2424.5781 | 122.3511 | -121.7422 | 0.54016 | 0.4218 | 0.0081278 | 0.0011799 | 0.027852 | -0.0042115 | -0.0024415 | 0.0047403 | 0.11902 | 0.53101 | -0.19684 | -0.027466 | -0.032043 | 0.082397 | -0.064087 | 0.16022 | 0.59052 | -122.1725 | 121.5454 | -0.009155 | 121.8613 | 121.7148 | 122.1451 | -0.5722 | -0.62256 | -0.4303 | 0.050354 | 0.31586
2425.5781 | 122.4518 | -121.7468 | 0.55847 | 0.38365 | 0.0066326 | 0.0013935 | 0.030843 | -0.0031433 | -0.0020141 | 0.0055949 | 0.091553 | 0.54016 | -0.19684 | -0.041199 | -0.036621 | 0.045776 | 0 | -0.041199 | 0.62256 | -122.1222 | 121.55 | -0.018311 | 121.8384 | 121.7056 | 122.081 | -0.59509 | -0.65918 | -0.37537 | 0.064087 | 0.28839
2426.5781 | 122.374 | -121.7651 | 0.55847 | 0.39128 | 0.0062052 | 0.0028889 | 0.029348 | -0.0025025 | -0.0022277 | 0.0060221 | 0.09613 | 0.55389 | -0.20599 | -0.027466 | -0.018311 | -0.018311 | 0.21515 | 0.31586 | 0.61798 | -122.168 | 121.5591 | -0.004578 | 121.8613 | 121.7377 | 122.1405 | -0.57678 | -0.63629 | -0.40283 | 0.059509 | 0.30212
2427.5781 | 122.4426 | -121.7194 | 0.5127 | 0.36076 | 0.0049236 | 0.0026753 | 0.025289 | -0.0031433 | -0.0026551 | 0.0075175 | 0.18768 | 0.50812 | -0.17853 | 0.064087 | 0.07782 | 0.19226 | -0.18768 | 0.27008 | 0.5722 | -122.1268 | 121.5408 | -0.004577 | 121.907 | 121.7834 | 122.1909 | -0.43488 | -0.49438 | -0.40741 | 0.05951 | 0.36621
2428.5781 | 122.4884 | -121.701 | 0.52185 | 0.38365 | 0.0077006 | 0.0018209 | 0.02828 | -0.0067749 | -0.0022277 | 0.0049541 | 0.19226 | 0.50812 | -0.15106 | 0.064087 | 0.064087 | 0.1831 | -0.1831 | 0.2655 | 0.5722 | -122.1588 | 121.55 | -0.013733 | 121.8933 | 121.7651 | 122.2229 | -0.45776 | -0.50812 | -0.45776 | 0.050354 | 0.34332
2429.5781 | 122.4747 | -121.7194 | 0.50812 | 0.39891 | 0.0066326 | 0.00011194 | 0.027639 | -0.0059203 | -0.0018005 | 0.0055949 | 0.1831 | 0.50812 | -0.17395 | 0.073242 | 0.059509 | 0.17395 | -0.19684 | 0.27466 | 0.5722 | -122.1359 | 121.5454 | 0 | 121.9025 | 121.7926 | 122.2092 | -0.44861 | -0.5127 | -0.41657 | 0.064087 | 0.35706
2430.5781 | 122.4792 | -121.7239 | 0.49896 | 0.43706 | 0.0042826 | 0.0043843 | 0.02828 | -0.0044251 | -0.0009461 | 0.0049541 | 0.14191 | 0.49896 | -0.20599 | 0.073242 | 0.068665 | 0.19226 | -0.19684 | 0.28381 | 0.5722 | -122.1405 | 121.5179 | 0 | 121.8658 | 121.7972 | 122.2137 | -0.4303 | -0.50354 | -0.41656 | 0.073243 | 0.3479

## Thermal Data
Fire Time | North 25 C | Cable 1 | Cable 2
-0.2927 | 28.6313 | 25.8383 | 26.2733
0.7073 | 28.6334 | 25.8428 | 26.2677
1.7073 | 28.636 | 25.8425 | 26.2752
2.7073 | 28.6348 | 25.8466 | 26.2701
3.7073 | 28.635 | 25.8422 | 26.2706
4.7073 | 28.6261 | 25.8464 | 26.2713
5.7073 | 28.8003 | 25.8435 | 26.2753
6.7073 | 29.6292 | 25.8344 | 26.2706
7.7073 | 31.2438 | 25.8496 | 26.2728
8.7073 | 33.5633 | 25.8473 | 26.2725
9.7073 | 36.4782 | 25.8407 | 26.2694
10.7073 | 39.8931 | 25.8478 | 26.2704
11.7073 | 43.6653 | 25.84 | 26.2779
12.7073 | 47.7868 | 25.8474 | 26.2706
13.7073 | 52.1556 | 25.8493 | 26.2706
14.7073 | 56.79 | 25.844 | 26.2694
15.7073 | 61.624 | 25.8495 | 26.2699
16.7073 | 66.6735 | 25.8522 | 26.2709
17.7073 | 71.8871 | 25.8615 | 26.2689
18.7073 | 77.2577 | 25.8506 | 26.2727
19.7073 | 82.7024 | 25.8576 | 26.2775
20.7073 | 88.1543 | 25.8668 | 26.275
21.7073 | 93.6784 | 25.8762 | 26.2768
22.7073 | 99.3369 | 25.8896 | 26.2765
23.7073 | 105.0961 | 25.8804 | 26.2812
24.7073 | 110.9181 | 25.8896 | 26.2758
25.7073 | 116.7543 | 25.9057 | 26.2871
26.7073 | 122.6796 | 25.9106 | 26.2836
27.7073 | 128.6452 | 25.9193 | 26.2944
28.7073 | 134.6393 | 25.9405 | 26.2891
29.7073 | 140.6648 | 25.966 | 26.2972
30.7073 | 146.5879 | 25.9831 | 26.3015
31.7073 | 152.5358 | 26.0027 | 26.3157
32.7073 | 158.4856 | 26.0211 | 26.3162
33.7073 | 164.3761 | 26.0422 | 26.3268
34.7073 | 170.2821 | 26.0742 | 26.3386
35.7073 | 176.1221 | 26.1157 | 26.3591
36.7073 | 182.0641 | 26.1564 | 26.3701
37.7073 | 187.9704 | 26.1854 | 26.3832
38.7073 | 193.851 | 26.2367 | 26.4123
39.7073 | 199.6598 | 26.27 | 26.4211
40.7073 | 205.4628 | 26.3277 | 26.4453
41.7073 | 211.3672 | 26.4023 | 26.4739
42.7073 | 217.2809 | 26.4592 | 26.5044
43.7073 | 223.1083 | 26.5227 | 26.5336
44.7073 | 228.8735 | 26.5954 | 26.5642
45.7073 | 234.7196 | 26.6682 | 26.6068
46.7073 | 240.4866 | 26.752 | 26.6457
47.7073 | 246.3415 | 26.8419 | 26.6779
48.7073 | 252.0523 | 26.9261 | 26.7371
49.7073 | 257.8094 | 27.0471 | 26.7939
50.7073 | 263.5341 | 27.1555 | 26.8463
51.7073 | 269.1932 | 27.2584 | 26.9155
52.7073 | 274.8032 | 27.3882 | 26.9803
53.7073 | 280.438 | 27.4989 | 27.0514
54.7073 | 286.0914 | 27.6433 | 27.137
55.7073 | 291.7558 | 27.7715 | 27.2095
56.7073 | 297.3772 | 27.9356 | 27.2945
57.7073 | 302.8528 | 28.1003 | 27.3987
58.7073 | 308.1807 | 28.2494 | 27.4933
59.7073 | 313.0071 | 28.4324 | 27.6083
60.7073 | 317.2871 | 28.6127 | 27.7138
61.7073 | 321.2969 | 28.8 | 27.8389
62.7073 | 324.951 | 28.9994 | 27.9605
63.7073 | 328.477 | 29.2013 | 28.0978
64.7073 | 331.7726 | 29.4351 | 28.2419
65.7073 | 334.8936 | 29.654 | 28.393
66.7073 | 338.0222 | 29.8967 | 28.5433
67.7073 | 340.8878 | 30.1423 | 28.7157
68.7073 | 343.4287 | 30.4005 | 28.8825
69.7073 | 345.7421 | 30.6697 | 29.0629
70.7073 | 347.7551 | 30.9461 | 29.2628
71.7073 | 349.4874 | 31.229 | 29.462
72.7073 | 350.8176 | 31.5337 | 29.6767
73.7073 | 351.9296 | 31.8298 | 29.9039
74.7073 | 352.78 | 32.1431 | 30.1287
75.7073 | 353.4375 | 32.4584 | 30.3683
76.7073 | 354.0359 | 32.79 | 30.6138
77.7073 | 354.6611 | 33.1242 | 30.8625
78.7073 | 355.1203 | 33.4671 | 31.1362
79.7073 | 355.3665 | 33.8335 | 31.4019
80.7073 | 355.4393 | 34.1973 | 31.6976
81.7073 | 355.4249 | 34.5787 | 31.9947
82.7073 | 355.4249 | 34.9607 | 32.3031
83.7073 | 355.2641 | 35.3242 | 32.6181
84.7073 | 355.0821 | 35.7243 | 32.9338
85.7073 | 354.7849 | 36.1443 | 33.2669
86.7073 | 354.4248 | 36.5488 | 33.609
87.7073 | 354.0824 | 36.9667 | 33.9617
88.7073 | 353.7831 | 37.3963 | 34.3263
89.7073 | 353.5698 | 37.8115 | 34.6884
90.7073 | 353.3909 | 38.2575 | 35.0563
91.7073 | 353.0563 | 38.6933 | 35.4469
92.7073 | 352.7033 | 39.131 | 35.8333
93.7073 | 352.1476 | 39.6014 | 36.2383
94.7073 | 351.691 | 40.048 | 36.6529
95.7073 | 351.4012 | 40.5037 | 37.0637
96.7073 | 351.0188 | 40.9633 | 37.4816
97.7073 | 350.5423 | 41.4375 | 37.916
98.7073 | 350.1723 | 41.9001 | 38.3465
99.7073 | 349.9202 | 42.379 | 38.7844
100.7073 | 349.4368 | 42.858 | 39.2414
101.7073 | 349.0616 | 43.3215 | 39.7012
102.7073 | 348.7852 | 43.8032 | 40.163
103.7073 | 348.4639 | 44.3004 | 40.6255
104.7073 | 348.2049 | 44.7854 | 41.0969
105.7073 | 347.9563 | 45.2708 | 41.5707
106.7073 | 347.78 | 45.7786 | 42.0425
107.7073 | 347.5763 | 46.2684 | 42.5305
108.7073 | 347.4832 | 46.7594 | 43.0184
109.7073 | 347.4249 | 47.2702 | 43.5074
110.7073 | 347.4981 | 47.766 | 44.0008
111.7073 | 347.5653 | 48.2637 | 44.4982
112.7073 | 347.6084 | 48.7625 | 44.9922
113.7073 | 347.5918 | 49.282 | 45.4948
114.7073 | 347.6154 | 49.7838 | 46.0034
115.7073 | 347.7118 | 50.2935 | 46.5064
116.7073 | 347.7051 | 50.7945 | 47.0218
117.7073 | 347.7148 | 51.2911 | 47.5378
118.7073 | 347.8382 | 51.8137 | 48.0461
119.7073 | 347.9796 | 52.3337 | 48.5667
120.7073 | 348.168 | 52.8388 | 49.0954
121.7073 | 348.3627 | 53.3534 | 49.6233
122.7073 | 348.5387 | 53.8604 | 50.1406
123.7073 | 348.785 | 54.3612 | 50.6657
124.7073 | 349.0499 | 54.8683 | 51.191
125.7073 | 349.2191 | 55.3924 | 51.717
126.7073 | 349.3177 | 55.8938 | 52.2544
127.7073 | 349.3769 | 56.419 | 52.7796
128.7073 | 349.396 | 56.9251 | 53.314
129.7073 | 349.5174 | 57.4344 | 53.8407
130.7073 | 349.5199 | 57.9427 | 54.3659
131.7073 | 349.6729 | 58.4618 | 54.8992
132.7073 | 349.7913 | 58.9741 | 55.442
133.7073 | 349.8757 | 59.4685 | 55.9683
134.7073 | 349.926 | 60.002 | 56.5092
135.7073 | 350.0448 | 60.5064 | 57.037
136.7073 | 350.1746 | 61.0184 | 57.577
137.7073 | 350.241 | 61.5262 | 58.1141
138.7073 | 350.3038 | 62.0267 | 58.655
139.7073 | 350.4452 | 62.5691 | 59.1949
140.7073 | 350.6938 | 63.0693 | 59.736
141.7073 | 350.8268 | 63.5768 | 60.2716
142.7073 | 350.9571 | 64.1083 | 60.8127
143.7073 | 351.1763 | 64.6163 | 61.3407
144.7073 | 351.3177 | 65.1343 | 61.8779
145.7073 | 351.4142 | 65.6523 | 62.4196
146.7073 | 351.4227 | 66.1574 | 62.9438
147.7073 | 351.5142 | 66.6868 | 63.4724
148.7073 | 351.6223 | 67.1965 | 64.0179
149.7073 | 351.7088 | 67.7263 | 64.5392
150.7073 | 351.8212 | 68.2533 | 65.0819
151.7073 | 351.8233 | 68.7554 | 65.6096
152.7073 | 351.786 | 69.2691 | 66.1395
153.7073 | 351.8007 | 69.7846 | 66.6717
154.7073 | 351.7303 | 70.3052 | 67.1996
155.7073 | 351.7449 | 70.8147 | 67.7351
156.7073 | 351.8192 | 71.3282 | 68.2557
157.7073 | 351.8809 | 71.829 | 68.7813
158.7073 | 351.9798 | 72.3631 | 69.3106
159.7073 | 352.0644 | 72.8782 | 69.8321
160.7073 | 351.956 | 73.3882 | 70.3547
161.7073 | 351.8818 | 73.8953 | 70.8613
162.7073 | 351.9025 | 74.4123 | 71.3901
163.7073 | 351.8565 | 74.9077 | 71.8988
164.7073 | 351.7711 | 75.4263 | 72.4181
165.7073 | 351.8057 | 75.9406 | 72.9355
166.7073 | 351.848 | 76.4564 | 73.4493
167.7073 | 351.8093 | 76.9591 | 73.96
168.7073 | 351.8242 | 77.4891 | 74.4741
169.7073 | 351.8177 | 78.0028 | 74.9864
170.7073 | 351.688 | 78.5177 | 75.5046
171.7073 | 351.6341 | 79.038 | 76.0149
172.7073 | 351.5614 | 79.5529 | 76.53
173.7073 | 351.6468 | 80.0802 | 77.0577
174.7073 | 351.6742 | 80.6042 | 77.5811
175.7073 | 351.6606 | 81.1211 | 78.1067
176.7073 | 351.6141 | 81.669 | 78.6253
177.7073 | 351.5552 | 82.1778 | 79.1624
178.7073 | 351.4594 | 82.7252 | 79.6961
179.7073 | 351.3397 | 83.2579 | 80.2249
180.7073 | 351.3672 | 83.7886 | 80.7682
181.7073 | 351.3568 | 84.3143 | 81.3148
182.7073 | 351.269 | 84.8682 | 81.8583
183.7073 | 351.2371 | 85.401 | 82.4226
184.7073 | 351.2887 | 85.9445 | 82.9819
185.7073 | 351.3815 | 86.4953 | 83.5612
186.7073 | 351.3921 | 87.0392 | 84.1416
187.7073 | 351.2801 | 87.5843 | 84.7547
188.7073 | 351.2984 | 88.1338 | 85.3828
189.7073 | 351.2884 | 88.6956 | 86.0354
190.7073 | 351.256 | 89.2177 | 86.7591
191.7073 | 351.3003 | 89.7712 | 87.5634
192.7073 | 351.3961 | 90.3137 | 88.513
193.7073 | 351.3901 | 90.8594 | 89.6159
194.7073 | 351.3588 | 91.4218 | 90.9308
195.7073 | 351.3317 | 92.0017 | 92.5802
196.7073 | 351.2772 | 92.6229 | 95.3342
197.7073 | 351.2766 | 93.3047 | 96.8464
198.7073 | 351.1432 | 94.0142 | 97.3736
199.7073 | 351.0768 | 94.6604 | 97.6799
200.7073 | 351.1334 | 95.1662 | 97.8927
201.7073 | 351.0784 | 95.6175 | 98.0567
202.7073 | 351.1908 | 96.0557 | 98.1962
203.7073 | 351.2607 | 96.4256 | 98.3199
204.7073 | 351.1839 | 96.7635 | 98.4259
205.7073 | 351.1583 | 97.0885 | 98.531
206.7073 | 351.1011 | 97.3916 | 98.6277
207.7073 | 351.0748 | 97.6828 | 98.7231
208.7073 | 351.1659 | 97.9764 | 98.8138
209.7073 | 351.2177 | 98.2573 | 98.914
210.7073 | 351.1727 | 98.5306 | 99.0057
211.7073 | 351.0905 | 98.8215 | 99.0963
212.7073 | 351.0752 | 99.0927 | 99.201
213.7073 | 351.1723 | 99.3549 | 99.3023
214.7073 | 351.1262 | 99.6356 | 99.4128
215.7073 | 351.0875 | 99.8917 | 99.5296
216.7073 | 351.137 | 100.161 | 99.6442
217.7073 | 351.1977 | 100.454 | 99.7567
218.7073 | 351.2364 | 100.732 | 99.8902
219.7073 | 351.515 | 101.0129 | 100.016
220.7073 | 351.6148 | 101.2915 | 100.1551
221.7073 | 351.5577 | 101.5835 | 100.2945
222.7073 | 351.5887 | 101.8892 | 100.4385
223.7073 | 351.5656 | 102.2024 | 100.5934
224.7073 | 351.5787 | 102.5184 | 100.7488
225.7073 | 351.6155 | 102.8604 | 100.9052
226.7073 | 351.5277 | 103.2113 | 101.0647
227.7073 | 351.4089 | 103.576 | 101.2282
228.7073 | 351.3325 | 103.9328 | 101.3937
229.7073 | 351.3931 | 104.2852 | 101.5667
230.7073 | 351.3886 | 104.6534 | 101.7391
231.7073 | 351.379 | 105.0196 | 101.9176
232.7073 | 351.4187 | 105.3904 | 102.1
233.7073 | 351.427 | 105.7621 | 102.2867
234.7073 | 351.4356 | 106.1092 | 102.4754
235.7073 | 351.4893 | 106.4714 | 102.6674
236.7073 | 351.6163 | 106.8328 | 102.8595
237.7073 | 351.5286 | 107.1965 | 103.0587
238.7073 | 351.5549 | 107.5424 | 103.2635
239.7073 | 351.5219 | 107.9166 | 103.4641
240.7073 | 351.4624 | 108.2625 | 103.6793
241.7073 | 351.4619 | 108.5912 | 103.8824
242.7073 | 351.5261 | 108.9444 | 104.0908
243.7073 | 351.4937 | 109.3078 | 104.312
244.7073 | 351.4555 | 109.6521 | 104.5282
245.7073 | 351.4785 | 109.9945 | 104.7514
246.7073 | 351.6237 | 110.3462 | 104.9784
247.7073 | 351.7327 | 110.6855 | 105.2008
248.7073 | 351.8794 | 111.0169 | 105.4382
249.7073 | 351.8685 | 111.3619 | 105.6692
250.7073 | 351.8904 | 111.7057 | 105.904
251.7073 | 351.9497 | 112.0418 | 106.1396
252.7073 | 351.9834 | 112.3662 | 106.375
253.7073 | 351.8849 | 112.7203 | 106.6275
254.7073 | 351.8091 | 113.0306 | 106.871
255.7073 | 351.7604 | 113.3729 | 107.1207
256.7073 | 351.7443 | 113.7227 | 107.3739
257.7073 | 351.7538 | 114.0498 | 107.618
258.7073 | 351.7165 | 114.3829 | 107.8874
259.7073 | 351.6265 | 114.7086 | 108.1396
260.7073 | 351.5395 | 115.0481 | 108.3936
261.7073 | 351.5781 | 115.3721 | 108.6663
262.7073 | 351.6535 | 115.7143 | 108.9319
263.7073 | 351.7452 | 116.0334 | 109.1926
264.7073 | 351.7042 | 116.3651 | 109.4598
265.7073 | 351.6568 | 116.6867 | 109.7323
266.7073 | 351.6012 | 117.0277 | 110.0108
267.7073 | 351.4851 | 117.3253 | 110.2453
268.7073 | 351.3806 | 117.6649 | 110.4941
269.7073 | 351.2393 | 117.9829 | 110.7595
270.7073 | 351.1559 | 118.3016 | 111.03
271.7073 | 351.1273 | 118.635 | 111.305
272.7073 | 351.1375 | 118.9408 | 111.5819
273.7073 | 351.1415 | 119.2628 | 111.8682
274.7073 | 351.1308 | 119.5729 | 112.1541
275.7073 | 351.1246 | 119.8998 | 112.4447
276.7073 | 351.0748 | 120.2161 | 112.7314
277.7073 | 351.0005 | 120.5315 | 113.0297
278.7073 | 350.9788 | 120.8655 | 113.3164
279.7073 | 351.0046 | 121.1789 | 113.6217
280.7073 | 350.986 | 121.4847 | 113.9251
281.7073 | 351.0314 | 121.8023 | 114.2289
282.7073 | 351.0563 | 122.0996 | 114.5497
283.7073 | 350.945 | 122.4073 | 114.8665
284.7073 | 350.8546 | 122.7305 | 115.186
285.7073 | 350.8563 | 123.0309 | 115.5072
286.7073 | 350.8713 | 123.3382 | 115.8323
287.7073 | 350.8925 | 123.6539 | 116.1622
288.7073 | 350.85 | 123.9485 | 116.4933
289.7073 | 350.8682 | 124.2512 | 116.8259
290.7073 | 350.8341 | 124.5624 | 117.1639
291.7073 | 350.7796 | 124.8475 | 117.51
292.7073 | 350.8549 | 125.149 | 117.8563
293.7073 | 351.023 | 125.4369 | 118.2004
294.7073 | 350.9621 | 125.7276 | 118.5588
295.7073 | 350.9482 | 126.0188 | 118.9202
296.7073 | 350.9499 | 126.3143 | 119.2786
297.7073 | 350.9674 | 126.6134 | 119.6425
298.7073 | 351.0173 | 126.9277 | 120.0149
299.7073 | 351.1361 | 127.245 | 120.3878
300.7073 | 351.1912 | 127.5649 | 120.7673
301.7073 | 351.3485 | 127.8969 | 121.152
302.7073 | 351.4564 | 128.2518 | 121.5289
303.7073 | 351.5363 | 128.5808 | 121.9246
304.7073 | 351.5554 | 128.9228 | 122.3113
305.7073 | 351.5019 | 129.283 | 122.7092
306.7073 | 351.5213 | 129.6379 | 123.1049
307.7073 | 351.5207 | 129.9944 | 123.5103
308.7073 | 351.5354 | 130.3646 | 123.9156
309.7073 | 351.4924 | 130.7229 | 124.3196
310.7073 | 351.3987 | 131.1008 | 124.7385
311.7073 | 351.4172 | 131.4709 | 125.1513
312.7073 | 351.5296 | 131.8594 | 125.5618
313.7073 | 351.6103 | 132.2233 | 125.9797
314.7073 | 351.4938 | 132.594 | 126.3997
315.7073 | 351.4247 | 132.9717 | 126.8196
316.7073 | 351.2988 | 133.3516 | 127.2456
317.7073 | 351.2041 | 133.7316 | 127.6634
318.7073 | 351.0721 | 134.1183 | 128.0971
319.7073 | 350.9527 | 134.481 | 128.5173
320.7073 | 350.9365 | 134.8666 | 128.9487
321.7073 | 350.827 | 135.231 | 129.3794
322.7073 | 350.6987 | 135.5885 | 129.8065
323.7073 | 350.6589 | 135.9492 | 130.2333
324.7073 | 350.7437 | 136.2796 | 130.6703
325.7073 | 350.7863 | 136.5905 | 131.1073
326.7073 | 350.7447 | 136.9383 | 131.5381
327.7073 | 350.6482 | 137.3245 | 131.9759
328.7073 | 350.5652 | 137.6913 | 132.4126
329.7073 | 350.3726 | 138.0618 | 132.8422
330.7073 | 350.273 | 138.4474 | 133.2884
331.7073 | 350.306 | 138.8249 | 133.7358
332.7073 | 350.288 | 139.2105 | 134.1816
333.7073 | 350.2742 | 139.583 | 134.6199
334.7073 | 350.3559 | 139.992 | 135.0648
335.7073 | 350.2822 | 140.357 | 135.4984
336.7073 | 350.2513 | 140.754 | 135.9438
337.7073 | 350.2035 | 141.141 | 136.386
338.7073 | 350.1142 | 141.5491 | 136.8214
339.7073 | 350.153 | 141.9223 | 137.2573
340.7073 | 350.2542 | 142.3149 | 137.7041
341.7073 | 350.2648 | 142.6912 | 138.1371
342.7073 | 350.2979 | 143.1035 | 138.5921
343.7073 | 350.2474 | 143.49 | 139.01
344.7073 | 350.1937 | 143.903 | 139.459
345.7073 | 350.1911 | 144.2937 | 139.8913
346.7073 | 350.0769 | 144.695 | 140.3303
347.7073 | 350.1364 | 145.0822 | 140.7619
348.7073 | 350.2205 | 145.4633 | 141.2015
349.7073 | 350.3206 | 145.8681 | 141.6308
350.7073 | 350.2732 | 146.2606 | 142.0715
351.7073 | 350.225 | 146.6428 | 142.5068
352.7073 | 350.267 | 147.041 | 142.9418
353.7073 | 350.2243 | 147.4158 | 143.3776
354.7073 | 350.1655 | 147.7929 | 143.8131
355.7073 | 350.2175 | 148.1993 | 144.2394
356.7073 | 350.3121 | 148.5802 | 144.6728
357.7073 | 350.3044 | 148.9623 | 145.0973
358.7073 | 350.2108 | 149.354 | 145.5265
359.7073 | 350.1956 | 149.7426 | 145.9478
360.7073 | 350.2903 | 150.1214 | 146.3755
361.7073 | 350.3166 | 150.503 | 146.7945
362.7073 | 350.3127 | 150.8906 | 147.2114
363.7073 | 350.2795 | 151.2638 | 147.6435
364.7073 | 350.1092 | 151.6477 | 148.0645
365.7073 | 350.2364 | 152.0278 | 148.4755
366.7073 | 350.2973 | 152.4072 | 148.8904
367.7073 | 350.2699 | 152.7873 | 149.3101
368.7073 | 350.346 | 153.187 | 149.7246
369.7073 | 350.305 | 153.5765 | 150.1326
370.7229 | 350.2272 | 153.9776 | 150.5502
371.7073 | 350.115 | 154.3522 | 150.9571
372.7073 | 350.0625 | 154.7241 | 151.3681
373.7073 | 350.1223 | 155.1134 | 151.7772
374.7073 | 350.1923 | 155.4876 | 152.1894
375.7073 | 350.1758 | 155.8619 | 152.5907
376.7073 | 350.2341 | 156.2455 | 153.001
377.7073 | 350.3737 | 156.6089 | 153.4166
378.7073 | 350.4289 | 156.9872 | 153.8164
379.7073 | 350.4378 | 157.366 | 154.2135
380.7073 | 350.5262 | 157.7237 | 154.6223
381.7073 | 350.4406 | 158.0981 | 155.0192
382.7073 | 350.4048 | 158.4798 | 155.4069
383.7073 | 350.4696 | 158.8416 | 155.812
384.7073 | 350.4895 | 159.2062 | 156.2048
385.7073 | 350.4581 | 159.5887 | 156.6012
386.7073 | 350.4149 | 159.9414 | 156.9883
387.7073 | 350.3992 | 160.3162 | 157.3811
388.7073 | 350.4408 | 160.69 | 157.784
389.7073 | 350.3604 | 161.0523 | 158.1572
390.7073 | 350.2903 | 161.4191 | 158.5572
391.7073 | 350.3825 | 161.7851 | 158.9446
392.7073 | 350.3749 | 162.1563 | 159.3283
393.7073 | 350.2934 | 162.493 | 159.7151
394.7073 | 350.2178 | 162.8708 | 160.096
395.7073 | 350.2211 | 163.2697 | 160.4844
396.7073 | 350.3382 | 163.6272 | 160.8641
397.7073 | 350.3358 | 163.9823 | 161.2477
398.7073 | 350.4063 | 164.3432 | 161.6322
399.7073 | 350.4515 | 164.7055 | 162.0076
400.7073 | 350.4418 | 165.0395 | 162.3891
401.7073 | 350.403 | 165.4195 | 162.7654
402.7073 | 350.3672 | 165.7771 | 163.1602
403.7073 | 350.3656 | 166.1363 | 163.5346
404.7073 | 350.4704 | 166.4836 | 163.9162
405.7073 | 350.5306 | 166.8474 | 164.2812
406.7073 | 350.6052 | 167.2005 | 164.661
407.7073 | 350.5616 | 167.5451 | 165.0241
408.7073 | 350.5258 | 167.9262 | 165.4076
409.7073 | 350.566 | 168.2738 | 165.7702
410.7073 | 350.6146 | 168.6287 | 166.139
411.7073 | 350.5439 | 168.9522 | 166.5086
412.7073 | 350.5176 | 169.3204 | 166.8816
413.7073 | 350.4599 | 169.6579 | 167.2493
414.7073 | 350.6065 | 170.0132 | 167.6128
415.7073 | 350.5748 | 170.3399 | 167.9822
416.7073 | 350.6223 | 170.7084 | 168.3406
417.7073 | 350.5856 | 171.0357 | 168.7142
418.7073 | 350.5707 | 171.3754 | 169.0772
419.7073 | 350.6602 | 171.7105 | 169.4298
420.7073 | 350.7267 | 172.0407 | 169.7908
421.7073 | 350.8264 | 172.3807 | 170.1535
422.7073 | 350.8757 | 172.7369 | 170.5076
423.7073 | 350.867 | 173.0807 | 170.8726
424.7073 | 350.8377 | 173.4226 | 171.2329
425.7073 | 350.6954 | 173.7525 | 171.5857
426.7073 | 350.6294 | 174.084 | 171.9535
427.7073 | 350.5473 | 174.3963 | 172.3065
428.7073 | 350.4035 | 174.697 | 172.6642
429.7073 | 350.3783 | 175.0194 | 173.0295
430.7229 | 350.3315 | 175.3352 | 173.3856
431.7073 | 350.1834 | 175.6494 | 173.7319
432.7073 | 350.09 | 175.9668 | 174.0905
433.7073 | 349.972 | 176.3148 | 174.4372
434.7073 | 349.9625 | 176.6379 | 174.7942
435.7073 | 350.0467 | 176.9777 | 175.147
436.7073 | 350.1033 | 177.2774 | 175.4978
437.7073 | 350.2316 | 177.6045 | 175.8415
438.7073 | 350.3138 | 177.9016 | 176.203
439.7073 | 350.3009 | 178.1725 | 176.5509
440.7073 | 350.2409 | 178.4218 | 176.8979
441.7073 | 350.1894 | 178.6474 | 177.2453
442.7073 | 350.0928 | 178.8872 | 177.5914
443.7073 | 349.998 | 179.1537 | 177.9258
444.7073 | 350.0627 | 179.3901 | 178.2696
445.7073 | 350.0364 | 179.6399 | 178.6151
446.7073 | 349.9745 | 179.9112 | 178.9618
447.7073 | 349.9754 | 180.203 | 179.2962
448.7073 | 350.027 | 180.4801 | 179.6362
449.7073 | 350.0035 | 180.7769 | 179.9829
450.7073 | 349.9246 | 181.0832 | 180.326
451.7073 | 349.94 | 181.386 | 180.6618
452.7073 | 349.8873 | 181.6851 | 180.9948
453.7073 | 349.7918 | 181.9928 | 181.3266
454.7073 | 349.6888 | 182.2925 | 181.67
455.7073 | 349.6672 | 182.6182 | 182.0055
456.7073 | 349.5428 | 182.9163 | 182.3428
457.7073 | 349.5582 | 183.2468 | 182.7017
458.7073 | 349.5273 | 183.5386 | 183.026
459.7073 | 349.53 | 183.8537 | 183.3607
460.7229 | 349.4359 | 184.1728 | 183.6915
461.7073 | 349.3957 | 184.4681 | 184.02
462.7073 | 349.3533 | 184.7833 | 184.3496
463.7073 | 349.4134 | 185.101 | 184.6828
464.7073 | 349.4947 | 185.4153 | 185.0005
465.7073 | 349.544 | 185.7319 | 185.3336
466.7073 | 349.5384 | 186.0454 | 185.6612
467.7073 | 349.5815 | 186.3672 | 185.9854
468.7073 | 349.5548 | 186.6809 | 186.3056
469.7073 | 349.5318 | 186.9665 | 186.6361
470.7073 | 349.3704 | 187.2974 | 186.9503
471.7073 | 349.3027 | 187.6018 | 187.2845
472.7073 | 349.2933 | 187.9175 | 187.6039
473.7073 | 349.4172 | 188.2408 | 187.9272
474.7073 | 349.5364 | 188.5508 | 188.2428
475.7073 | 349.6584 | 188.8728 | 188.565
476.7073 | 349.8278 | 189.1702 | 188.878
477.7073 | 349.8979 | 189.4819 | 189.1933
478.7073 | 349.7966 | 189.8032 | 189.4994
479.7073 | 349.721 | 190.1217 | 189.82
480.7073 | 349.7257 | 190.4347 | 190.1383
481.7073 | 349.7252 | 190.7404 | 190.4493
482.7073 | 349.7512 | 191.0535 | 190.7665
483.7073 | 349.6627 | 191.3649 | 191.0748
484.7073 | 349.6884 | 191.6801 | 191.3855
485.7073 | 349.7387 | 191.9694 | 191.6911
486.7073 | 349.6544 | 192.2876 | 192.0024
487.7073 | 349.7103 | 192.6059 | 192.3066
488.7073 | 349.7069 | 192.9279 | 192.6292
489.7073 | 349.5206 | 193.2215 | 192.9318
490.7073 | 349.3978 | 193.5204 | 193.2458
491.7073 | 349.3855 | 193.8578 | 193.5405
492.7073 | 349.2825 | 194.1584 | 193.8488
493.7073 | 349.3176 | 194.4585 | 194.1597
494.7073 | 349.3043 | 194.7717 | 194.4557
495.7073 | 349.3111 | 195.0887 | 194.7571
496.7073 | 349.3574 | 195.3959 | 195.0583
497.7073 | 349.3838 | 195.6925 | 195.358
498.7073 | 349.3668 | 196.002 | 195.6535
499.7073 | 349.354 | 196.3138 | 195.9598
500.7073 | 349.4036 | 196.6039 | 196.2467
501.7073 | 349.452 | 196.9355 | 196.5421
502.7073 | 349.4857 | 197.2375 | 196.8372
503.7073 | 349.539 | 197.5414 | 197.1314
504.7073 | 349.4406 | 197.8575 | 197.4203
505.7073 | 349.451 | 198.1436 | 197.711
506.7073 | 349.3741 | 198.4491 | 198.0017
507.7073 | 349.369 | 198.7557 | 198.2915
508.7073 | 349.3213 | 199.0638 | 198.5803
509.7073 | 349.2046 | 199.3715 | 198.8632
510.7073 | 349.212 | 199.6677 | 199.1566
511.7073 | 349.1145 | 199.9723 | 199.4401
512.7073 | 349.0436 | 200.2736 | 199.7273
513.7073 | 348.9951 | 200.5752 | 200.0116
514.7073 | 348.9683 | 200.8882 | 200.2901
515.7073 | 348.887 | 201.162 | 200.5768
516.7073 | 348.8276 | 201.4767 | 200.8546
517.7073 | 348.8955 | 201.7767 | 201.1408
518.7073 | 348.9122 | 202.0734 | 201.427
519.7073 | 348.8467 | 202.4025 | 201.7045
520.7229 | 348.8701 | 202.695 | 201.9902
521.7073 | 348.9351 | 202.994 | 202.277
522.7073 | 348.9286 | 203.2721 | 202.5591
523.7073 | 348.8142 | 203.5804 | 202.8393
524.7073 | 348.8477 | 203.8868 | 203.1143
525.7073 | 349.0009 | 204.1867 | 203.3859
526.7073 | 349.1304 | 204.4735 | 203.6625
527.7073 | 349.0921 | 204.7836 | 203.9436
528.7073 | 349.1895 | 205.0712 | 204.2132
529.7073 | 349.1616 | 205.3554 | 204.4894
530.7073 | 349.2366 | 205.6543 | 204.7676
531.7073 | 349.3063 | 205.9582 | 205.0376
532.7073 | 349.3647 | 206.2568 | 205.3024
533.7073 | 349.4134 | 206.5525 | 205.5746
534.7073 | 349.4988 | 206.8485 | 205.844
535.7073 | 349.5795 | 207.1345 | 206.1181
536.7073 | 349.6526 | 207.4347 | 206.3803
537.7073 | 349.689 | 207.7376 | 206.6495
538.7073 | 349.6493 | 208.0244 | 206.9242
539.7073 | 349.631 | 208.3212 | 207.1885
540.7073 | 349.6277 | 208.6158 | 207.4492
541.7073 | 349.5555 | 208.9199 | 207.7186
542.7073 | 349.605 | 209.2034 | 207.9735
543.7073 | 349.5881 | 209.4979 | 208.2459
544.7073 | 349.5741 | 209.804 | 208.5038
545.7073 | 349.6079 | 210.0956 | 208.7686
546.7073 | 349.5153 | 210.3909 | 209.0254
547.7073 | 349.582 | 210.6715 | 209.2897
548.7073 | 349.7064 | 210.9713 | 209.5519
549.7073 | 349.7388 | 211.2814 | 209.8102
550.7229 | 349.6789 | 211.5952 | 210.0663
551.7073 | 349.7061 | 211.8887 | 210.3214
552.7073 | 349.7163 | 212.2218 | 210.5823
553.7073 | 349.7827 | 212.5054 | 210.8428
554.7073 | 349.8988 | 212.8066 | 211.0934
555.7073 | 349.8421 | 213.1057 | 211.3489
556.7073 | 349.8493 | 213.3981 | 211.5915
557.7073 | 349.9068 | 213.715 | 211.8481
558.7073 | 349.9908 | 214.0023 | 212.1092
559.7073 | 350.0197 | 214.3001 | 212.3651
560.7073 | 350.0888 | 214.5879 | 212.6062
561.7073 | 350.0266 | 214.8912 | 212.8591
562.7073 | 349.9433 | 215.1907 | 213.1026
563.7073 | 349.8894 | 215.4595 | 213.3488
564.7073 | 349.8006 | 215.7379 | 213.6007
565.7073 | 349.835 | 215.9889 | 213.8398
566.7073 | 349.8635 | 216.236 | 214.0783
567.7073 | 349.9061 | 216.4954 | 214.33
568.7073 | 349.7586 | 216.7246 | 214.5713
569.7073 | 349.7491 | 216.9678 | 214.8101
570.7073 | 349.7583 | 217.2037 | 215.0576
571.7073 | 349.6357 | 217.4448 | 215.2912
572.7073 | 349.5309 | 217.6884 | 215.5362
573.7073 | 349.4929 | 217.9344 | 215.7708
574.7073 | 349.5024 | 218.1816 | 216.0084
575.7073 | 349.4033 | 218.4273 | 216.2479
576.7073 | 349.4061 | 218.6612 | 216.4855
577.7073 | 349.4136 | 218.9082 | 216.719
578.7073 | 349.3555 | 219.1503 | 216.9533
579.7073 | 349.307 | 219.3905 | 217.1906
580.7073 | 349.2776 | 219.628 | 217.4186
581.7073 | 349.2186 | 219.8738 | 217.6556
582.7073 | 349.1622 | 220.1161 | 217.885
583.7073 | 349.0974 | 220.353 | 218.1207
584.7073 | 349.0246 | 220.6054 | 218.3583
585.7073 | 349.1443 | 220.8498 | 218.588
586.7073 | 349.1665 | 221.0722 | 218.8196
587.7073 | 349.203 | 221.3116 | 219.0504
588.7073 | 349.1831 | 221.5771 | 219.2824
589.7073 | 349.2886 | 221.8104 | 219.5113
590.7073 | 349.3647 | 222.0489 | 219.7482
591.7073 | 349.4998 | 222.2784 | 219.9781
592.7073 | 349.685 | 222.5157 | 220.2112
593.7073 | 349.6189 | 222.7601 | 220.43
594.7073 | 349.6258 | 222.9861 | 220.6651
595.7073 | 349.5068 | 223.2225 | 220.8944
596.7073 | 349.4169 | 223.4599 | 221.1219
597.7073 | 349.4222 | 223.6862 | 221.3463
598.7073 | 349.3547 | 223.9269 | 221.5739
599.7073 | 349.3236 | 224.1615 | 221.8102
600.7073 | 349.2861 | 224.4055 | 222.037
601.7073 | 349.1727 | 224.6495 | 222.2732
602.7073 | 349.2007 | 224.8511 | 222.4989
603.7073 | 349.3079 | 225.1148 | 222.7154
604.7073 | 349.1388 | 225.3395 | 222.9494
605.7073 | 349.1434 | 225.5809 | 223.1724
606.7073 | 349.2179 | 225.7921 | 223.3957
607.7073 | 349.2303 | 226.0251 | 223.6219
608.7073 | 349.1841 | 226.2716 | 223.842
609.7073 | 349.1419 | 226.4991 | 224.0716
610.7073 | 349.0803 | 226.7365 | 224.2931
611.7073 | 349.008 | 226.9554 | 224.5215
612.7073 | 348.9106 | 227.1903 | 224.7415
613.7073 | 348.8479 | 227.4155 | 224.9593
614.7073 | 348.8117 | 227.6548 | 225.1808
615.7073 | 348.8775 | 227.8772 | 225.4072
616.7073 | 348.8664 | 228.1087 | 225.6367
617.7073 | 348.8882 | 228.3442 | 225.8436
618.7073 | 348.9585 | 228.5518 | 226.0637
619.7073 | 348.9996 | 228.812 | 226.2934
620.7073 | 349.0102 | 229.0176 | 226.512
621.7073 | 348.9648 | 229.2622 | 226.7336
622.7073 | 349.0159 | 229.48 | 226.9451
623.7073 | 348.9188 | 229.686 | 227.1726
624.7073 | 348.9818 | 229.9148 | 227.3845
625.7073 | 348.9555 | 230.1569 | 227.6091
626.7073 | 348.8973 | 230.3761 | 227.8274
627.7073 | 348.9347 | 230.6009 | 228.0361
628.7073 | 348.9734 | 230.8272 | 228.2474
629.7073 | 348.8698 | 231.0242 | 228.4658
630.7073 | 348.8932 | 231.2601 | 228.6839
631.7073 | 348.8456 | 231.5008 | 228.9015
632.7073 | 348.7361 | 231.7244 | 229.1161
633.7073 | 348.602 | 231.9415 | 229.3241
634.7073 | 348.6269 | 232.1775 | 229.5365
635.7073 | 348.6965 | 232.3953 | 229.7552
636.7073 | 348.7535 | 232.6161 | 229.9652
637.7073 | 348.6952 | 232.8245 | 230.1785
638.7073 | 348.567 | 233.0303 | 230.3851
639.7073 | 348.5923 | 233.2557 | 230.598
640.7229 | 348.5822 | 233.4827 | 230.8106
641.7073 | 348.5713 | 233.6912 | 231.0177
642.7073 | 348.5416 | 233.9103 | 231.2317
643.7073 | 348.55 | 234.1253 | 231.4503
644.7073 | 348.475 | 234.3415 | 231.6535
645.7073 | 348.3478 | 234.563 | 231.8609
646.7073 | 348.3646 | 234.7855 | 232.0704
647.7073 | 348.4188 | 234.9862 | 232.2777
648.7073 | 348.4603 | 235.1886 | 232.4811
649.7073 | 348.5539 | 235.3908 | 232.6815
650.7073 | 348.6615 | 235.6049 | 232.8895
651.7073 | 348.8067 | 235.8141 | 233.087
652.7073 | 348.8448 | 236.0313 | 233.2971
653.7073 | 348.7987 | 236.1988 | 233.4971
654.7073 | 348.8276 | 236.3967 | 233.6943
655.7073 | 348.752 | 236.6088 | 233.8988
656.7073 | 348.7349 | 236.8242 | 234.1039
657.7073 | 348.7599 | 237.0199 | 234.2958
658.7073 | 348.704 | 237.2339 | 234.4933
659.7073 | 348.7637 | 237.4455 | 234.6986
660.7073 | 348.8259 | 237.6436 | 234.8945
661.7073 | 348.9923 | 237.8387 | 235.0908
662.7073 | 349.0037 | 238.0266 | 235.2885
663.7073 | 348.9342 | 238.2221 | 235.482
664.7073 | 348.8283 | 238.4229 | 235.6743
665.7073 | 348.9231 | 238.6302 | 235.8731
666.7073 | 348.9648 | 238.8328 | 236.0644
667.7073 | 349.0149 | 239.0048 | 236.2528
668.7073 | 349.0303 | 239.2077 | 236.4479
669.7073 | 349.0188 | 239.3873 | 236.6398
670.7073 | 348.9772 | 239.5854 | 236.8302
671.7073 | 348.9969 | 239.7749 | 237.0253
672.7073 | 349.0482 | 239.9464 | 237.2196
673.7073 | 349.1089 | 240.1185 | 237.4094
674.7073 | 349.1522 | 240.3306 | 237.5963
675.7073 | 349.1652 | 240.5241 | 237.7923
676.7073 | 349.1032 | 240.7008 | 237.9738
677.7073 | 349.0022 | 240.8702 | 238.159
678.7073 | 349.0314 | 241.0679 | 238.3581
679.7073 | 348.9208 | 241.2378 | 238.5399
680.7073 | 348.8533 | 241.4329 | 238.7311
681.7073 | 348.7906 | 241.6261 | 238.9115
682.7073 | 348.7024 | 241.8269 | 239.0961
683.7073 | 348.6185 | 242.0154 | 239.2793
684.7073 | 348.6172 | 242.2023 | 239.4682
685.7073 | 348.5805 | 242.4073 | 239.6539
686.7073 | 348.6682 | 242.6023 | 239.8402
687.7073 | 348.6701 | 242.8066 | 240.0266
688.7073 | 348.5791 | 243.0187 | 240.2083
689.7073 | 348.6628 | 243.2102 | 240.3866
690.7073 | 348.8525 | 243.4183 | 240.5743
691.7073 | 348.9346 | 243.5898 | 240.7603
692.7073 | 348.9402 | 243.8126 | 240.9415
693.7073 | 348.9277 | 244.0075 | 241.1293
694.7073 | 348.8936 | 244.2139 | 241.3132
695.7073 | 348.8838 | 244.3936 | 241.5054
696.7073 | 348.9048 | 244.5744 | 241.6715
697.7073 | 348.947 | 244.7474 | 241.8568
698.7073 | 349.0328 | 244.9193 | 242.0391
699.7073 | 348.9837 | 245.0599 | 242.2171
700.7073 | 348.9359 | 245.2178 | 242.3982
701.7073 | 348.8342 | 245.4014 | 242.5712
702.7073 | 348.8101 | 245.5623 | 242.7443
703.7073 | 348.8866 | 245.7137 | 242.9289
704.7073 | 349.0503 | 245.8817 | 243.1065
705.7073 | 348.9861 | 246.0583 | 243.2861
706.7073 | 348.9621 | 246.19 | 243.4636
707.7073 | 348.9296 | 246.3766 | 243.6356
708.7073 | 348.8746 | 246.5382 | 243.8104
709.7073 | 348.8556 | 246.7369 | 243.9865
710.7073 | 348.7715 | 246.9004 | 244.1629
711.7073 | 348.7692 | 247.0762 | 244.3385
712.7073 | 348.7775 | 247.2365 | 244.5084
713.7073 | 348.6681 | 247.3846 | 244.6846
714.7073 | 348.7388 | 247.5601 | 244.862
715.7073 | 348.8384 | 247.7336 | 245.0369
716.7073 | 348.8948 | 247.8897 | 245.208
717.7073 | 348.9075 | 248.0705 | 245.3819
718.7073 | 348.9898 | 248.228 | 245.5585
719.7073 | 348.9794 | 248.3443 | 245.7318
720.7073 | 349.103 | 248.5196 | 245.9024
721.7073 | 349.1693 | 248.682 | 246.0752
722.7073 | 349.3063 | 248.8539 | 246.2483
723.7073 | 349.3058 | 249.0222 | 246.4154
724.7073 | 349.2808 | 249.1616 | 246.5834
725.7073 | 349.2479 | 249.3182 | 246.7576
726.7073 | 349.3273 | 249.4897 | 246.926
727.7073 | 349.2552 | 249.6412 | 247.0992
728.7073 | 349.212 | 249.836 | 247.2664
729.7073 | 349.1372 | 249.9856 | 247.4312
730.7073 | 349.2053 | 250.1091 | 247.5997
731.7073 | 349.3483 | 250.2836 | 247.776
732.7073 | 349.3866 | 250.4461 | 247.9381
733.7073 | 349.4095 | 250.6339 | 248.1122
734.7073 | 349.544 | 250.7629 | 248.2704
735.7073 | 349.6041 | 250.9217 | 248.444
736.7073 | 349.6329 | 251.0903 | 248.6229
737.7073 | 349.6295 | 251.2715 | 248.7859
738.7073 | 349.6056 | 251.4012 | 248.9504
739.7073 | 349.5487 | 251.569 | 249.1174
740.7073 | 349.5502 | 251.7461 | 249.2825
741.7073 | 349.5744 | 251.9075 | 249.4515
742.7073 | 349.5576 | 252.0607 | 249.6132
743.7073 | 349.6404 | 252.2185 | 249.7871
744.7073 | 349.6346 | 252.3815 | 249.9484
745.7073 | 349.5823 | 252.549 | 250.1201
746.7073 | 349.4159 | 252.6925 | 250.2778
747.7073 | 349.2389 | 252.8587 | 250.4439
748.7073 | 349.1985 | 253.0033 | 250.6037
749.7073 | 349.1201 | 253.154 | 250.7811
750.7073 | 349.0441 | 253.3228 | 250.9431
751.7073 | 348.9598 | 253.4772 | 251.1056
752.7073 | 348.8143 | 253.6263 | 251.2716
753.7073 | 348.7593 | 253.7733 | 251.4276
754.7073 | 348.7447 | 253.9445 | 251.5927
755.7073 | 348.7047 | 254.0848 | 251.7587
756.7073 | 348.6932 | 254.2459 | 251.9155
757.7073 | 348.6686 | 254.4018 | 252.0688
758.7073 | 348.6183 | 254.5455 | 252.2337
759.7073 | 348.5298 | 254.7048 | 252.3932
760.7073 | 348.4394 | 254.8483 | 252.5574
761.7073 | 348.4238 | 255.0018 | 252.7156
762.7073 | 348.3548 | 255.1619 | 252.8709
763.7073 | 348.3497 | 255.3118 | 253.0256
764.7073 | 348.3478 | 255.4776 | 253.1912
765.7073 | 348.3151 | 255.6164 | 253.3386
766.7073 | 348.2181 | 255.7616 | 253.5029
767.7073 | 348.1151 | 255.9168 | 253.6566
768.7073 | 348.0473 | 256.0655 | 253.816
769.7073 | 347.9828 | 256.209 | 253.9677
770.7073 | 347.8735 | 256.3625 | 254.1286
771.7073 | 347.8611 | 256.5114 | 254.2802
772.7073 | 347.8975 | 256.6492 | 254.4319
773.7073 | 347.9126 | 256.8052 | 254.5932
774.7073 | 347.8342 | 256.9542 | 254.7433
775.7073 | 347.8237 | 257.0893 | 254.8966
776.7073 | 347.8782 | 257.2387 | 255.0443
777.7073 | 348.0007 | 257.3691 | 255.1983
778.7073 | 347.9886 | 257.5152 | 255.3525
779.7073 | 348.0352 | 257.6628 | 255.5053
780.7073 | 348.059 | 257.7958 | 255.6581
781.7073 | 347.9935 | 257.944 | 255.8079
782.7073 | 347.9423 | 258.0966 | 255.9604
783.7073 | 347.9282 | 258.2259 | 256.1088
784.7073 | 347.9377 | 258.37 | 256.2538
785.7073 | 348.0629 | 258.5207 | 256.399
786.7073 | 348.1189 | 258.6408 | 256.5522
787.7073 | 348.0975 | 258.7868 | 256.7063
788.7073 | 348.1122 | 258.9122 | 256.8438
789.7073 | 348.1414 | 259.0576 | 256.9942
790.7073 | 348.1529 | 259.1944 | 257.1422
791.7073 | 348.0596 | 259.3314 | 257.2968
792.7073 | 347.9789 | 259.4683 | 257.4324
793.7073 | 347.8644 | 259.6018 | 257.5808
794.7073 | 347.9068 | 259.7532 | 257.7272
795.7073 | 347.8633 | 259.883 | 257.8709
796.7073 | 347.9179 | 260.0213 | 258.0206
797.7073 | 348.0689 | 260.1624 | 258.1662
798.7073 | 348.1966 | 260.3145 | 258.3071
799.7073 | 348.1529 | 260.4463 | 258.4535
800.7073 | 348.1103 | 260.5754 | 258.5896
801.7073 | 348.1101 | 260.7092 | 258.7357
802.7073 | 348.2068 | 260.8519 | 258.8776
803.7073 | 348.208 | 260.9857 | 259.0172
804.7073 | 348.1109 | 261.0973 | 259.1537
805.7073 | 348.2273 | 261.2428 | 259.2926
806.7073 | 348.271 | 261.3816 | 259.438
807.7073 | 348.2887 | 261.4984 | 259.5802
808.7073 | 348.2348 | 261.6333 | 259.7102
809.7073 | 348.2165 | 261.7629 | 259.8481
810.7229 | 348.2657 | 261.8883 | 259.9849
811.7073 | 348.3357 | 262.0155 | 260.1288
812.7229 | 348.2622 | 262.1526 | 260.2682
813.7073 | 348.2588 | 262.2693 | 260.4106
814.7073 | 348.2615 | 262.3879 | 260.5499
815.7073 | 348.3731 | 262.5204 | 260.6792
816.7073 | 348.4179 | 262.6339 | 260.8091
817.7073 | 348.4424 | 262.7769 | 260.9549
818.7073 | 348.462 | 262.9065 | 261.0827
819.7073 | 348.5488 | 263.0275 | 261.2124
820.7073 | 348.6153 | 263.1554 | 261.3403
821.7073 | 348.5873 | 263.2673 | 261.486
822.7073 | 348.5836 | 263.3881 | 261.6117
823.7073 | 348.6355 | 263.524 | 261.7399
824.7073 | 348.5836 | 263.6424 | 261.8711
825.7073 | 348.6596 | 263.7475 | 262.0005
826.7073 | 348.603 | 263.8634 | 262.1368
827.7073 | 348.6695 | 263.9968 | 262.2636
828.7073 | 348.7232 | 264.1203 | 262.3902
829.7073 | 348.6707 | 264.2366 | 262.5243
830.7073 | 348.5235 | 264.3481 | 262.6506
831.7073 | 348.4868 | 264.4725 | 262.7826
832.7073 | 348.5603 | 264.5945 | 262.9102
833.7073 | 348.625 | 264.6972 | 263.0329
834.7073 | 348.6497 | 264.8223 | 263.1628
835.7073 | 348.559 | 264.9472 | 263.2831
836.7073 | 348.3654 | 265.07 | 263.4197
837.7073 | 348.2841 | 265.1759 | 263.5446
838.7073 | 348.1617 | 265.3032 | 263.6744
839.7073 | 348.1303 | 265.4098 | 263.7934
840.7073 | 348.1553 | 265.5212 | 263.9259
841.7073 | 348.1644 | 265.6429 | 264.046
842.7073 | 348.1938 | 265.752 | 264.1811
843.7073 | 348.1062 | 265.8682 | 264.3027
844.7073 | 348.1353 | 265.9828 | 264.4212
845.7073 | 348.0997 | 266.0927 | 264.55
846.7073 | 348.0276 | 266.2176 | 264.6773
847.7073 | 347.9664 | 266.3174 | 264.807
848.7073 | 347.997 | 266.4284 | 264.9335
849.7073 | 347.9658 | 266.5286 | 265.0529
850.7073 | 347.9027 | 266.6499 | 265.1799
851.7073 | 347.9685 | 266.764 | 265.2955
852.7073 | 348.1006 | 266.8732 | 265.4304
853.7073 | 348.037 | 266.9932 | 265.5563
854.7073 | 348.067 | 267.1151 | 265.6752
855.7073 | 348.1286 | 267.2257 | 265.8009
856.7073 | 348.084 | 267.3356 | 265.9209
857.7073 | 347.9804 | 267.4441 | 266.0401
858.7073 | 347.94 | 267.5531 | 266.1718
859.7073 | 348.0039 | 267.6717 | 266.2942
860.7073 | 348.0037 | 267.773 | 266.4186
861.7073 | 348.1252 | 267.8821 | 266.5427
862.7073 | 348.2153 | 267.9925 | 266.6646
863.7073 | 348.3279 | 268.1177 | 266.7845
864.7073 | 348.3145 | 268.2121 | 266.9015
865.7073 | 348.3335 | 268.327 | 267.0277
866.7073 | 348.2821 | 268.4375 | 267.1483
867.7073 | 348.2418 | 268.522 | 267.2659
868.7073 | 348.1316 | 268.659 | 267.3954
869.7073 | 348.1855 | 268.7737 | 267.5148
870.7073 | 348.1417 | 268.8781 | 267.6334
871.7073 | 348.1455 | 269.0034 | 267.7567
872.7073 | 348.1107 | 269.1136 | 267.8763
873.7073 | 348.0617 | 269.2208 | 268.0001
874.7073 | 348.0423 | 269.3286 | 268.121
875.7073 | 348.061 | 269.435 | 268.2438
876.7073 | 348.0443 | 269.5434 | 268.3594
877.7073 | 347.9819 | 269.6598 | 268.488
878.7073 | 347.9237 | 269.7671 | 268.6098
879.7073 | 347.9167 | 269.903 | 268.7411
880.7073 | 347.964 | 270.0054 | 268.861
881.7073 | 348.0333 | 270.1016 | 268.9882
882.7073 | 348.1251 | 270.214 | 269.1067
883.7073 | 348.1493 | 270.316 | 269.2316
884.7073 | 348.1319 | 270.4229 | 269.3562
885.7073 | 348.157 | 270.5343 | 269.4765
886.7073 | 348.2037 | 270.6468 | 269.6065
887.7073 | 348.1883 | 270.7497 | 269.7262
888.7073 | 348.1373 | 270.8535 | 269.8577
889.7073 | 348.133 | 270.9577 | 269.9821
890.7073 | 348.177 | 271.0771 | 270.1085
891.7073 | 348.2641 | 271.1769 | 270.2317
892.7073 | 348.4143 | 271.2853 | 270.3537
893.7073 | 348.4314 | 271.3929 | 270.4823
894.7073 | 348.4392 | 271.4925 | 270.6071
895.7073 | 348.3581 | 271.6032 | 270.7244
896.7073 | 348.3826 | 271.7177 | 270.8505
897.7073 | 348.4133 | 271.8096 | 270.9801
898.7073 | 348.518 | 271.9252 | 271.1134
899.7073 | 348.542 | 272.0382 | 271.2327
900.7073 | 348.5531 | 272.1312 | 271.3562
901.7073 | 348.492 | 272.2417 | 271.4856
902.7073 | 348.4724 | 272.3569 | 271.599
903.7073 | 348.4912 | 272.4587 | 271.7272
904.7073 | 348.4374 | 272.576 | 271.8626
905.7073 | 348.519 | 272.6781 | 271.9761
906.7073 | 348.5464 | 272.7753 | 272.1024
907.7073 | 348.5898 | 272.8929 | 272.2314
908.7073 | 348.7416 | 273.0035 | 272.3567
909.7073 | 348.718 | 273.1065 | 272.4723
910.7073 | 348.6962 | 273.2265 | 272.6045
911.7073 | 348.6738 | 273.3324 | 272.7357
912.7073 | 348.7374 | 273.4137 | 272.8632
913.7073 | 348.9232 | 273.5302 | 272.9888
914.7073 | 348.998 | 273.6549 | 273.1138
915.7073 | 348.9995 | 273.7449 | 273.2389
916.7073 | 348.9491 | 273.8527 | 273.3612
917.7073 | 348.8471 | 273.9667 | 273.4879
918.7073 | 348.8755 | 274.0873 | 273.6209
919.7073 | 348.9569 | 274.1949 | 273.7487
920.7073 | 349.0178 | 274.303 | 273.8782
921.7073 | 349.0465 | 274.413 | 274.0064
922.7073 | 348.8696 | 274.5085 | 274.1406
923.7073 | 348.7184 | 274.6139 | 274.2739
924.7073 | 348.6248 | 274.7372 | 274.397
925.7073 | 348.5205 | 274.8453 | 274.5293
926.7073 | 348.4767 | 274.9541 | 274.6551
927.7073 | 348.4794 | 275.0621 | 274.7944
928.7073 | 348.4921 | 275.1661 | 274.9254
929.7073 | 348.4679 | 275.2658 | 275.0692
930.7073 | 348.4269 | 275.392 | 275.1927
931.7073 | 348.346 | 275.5014 | 275.3227
932.7073 | 348.206 | 275.6073 | 275.44
933.7073 | 348.1358 | 275.6976 | 275.5607
934.7073 | 348.0472 | 275.8334 | 275.6884
935.7073 | 348.0571 | 275.941 | 275.8086
936.7073 | 348.0826 | 276.0481 | 275.9314
937.7073 | 348.1683 | 276.1493 | 276.0507
938.7073 | 348.2272 | 276.2794 | 276.1742
939.7073 | 348.162 | 276.3765 | 276.2996
940.7073 | 347.9914 | 276.4756 | 276.4177
941.7073 | 347.8283 | 276.5834 | 276.5434
942.7073 | 347.7717 | 276.7101 | 276.6617
943.7073 | 347.8301 | 276.8247 | 276.793
944.7073 | 347.864 | 276.9329 | 276.9171
945.7073 | 347.8427 | 277.0457 | 277.0447
946.7073 | 347.829 | 277.1557 | 277.1616
947.7073 | 347.887 | 277.266 | 277.2885
948.7073 | 347.9563 | 277.3702 | 277.4156
949.7073 | 348.0351 | 277.4882 | 277.5322
950.7073 | 348.2034 | 277.5847 | 277.6577
951.7073 | 348.2196 | 277.709 | 277.7795
952.7073 | 348.2439 | 277.8226 | 277.9049
953.7073 | 348.3254 | 277.9282 | 278.0272
954.7073 | 348.4016 | 278.0413 | 278.1486
955.7073 | 348.5567 | 278.1505 | 278.2792
956.7073 | 348.6717 | 278.2535 | 278.4028
957.7073 | 348.6509 | 278.3763 | 278.5293
958.7073 | 348.7234 | 278.4827 | 278.6495
959.7073 | 348.8247 | 278.5969 | 278.7731
960.7073 | 348.8915 | 278.7016 | 278.8978
961.7073 | 348.9531 | 278.799 | 279.0119
962.7073 | 348.992 | 278.8971 | 279.1417
963.7073 | 349.0434 | 278.9903 | 279.2623
964.7073 | 349.0123 | 279.1031 | 279.391
965.7073 | 348.9911 | 279.1836 | 279.5116
966.7073 | 349.0621 | 279.2713 | 279.6308
967.7073 | 348.937 | 279.3665 | 279.7496
968.7073 | 348.881 | 279.4494 | 279.8724
969.7073 | 348.9538 | 279.5229 | 279.979
970.7073 | 349.0261 | 279.6014 | 280.095
971.7073 | 349.0521 | 279.6809 | 280.2148
972.7073 | 349.1407 | 279.7633 | 280.3326
973.7073 | 349.1463 | 279.8368 | 280.4495
974.7073 | 349.2183 | 279.9127 | 280.5693
975.7073 | 349.1896 | 279.9982 | 280.6805
976.7073 | 349.2543 | 280.0765 | 280.795
977.7073 | 349.1845 | 280.1822 | 280.9115
978.7073 | 349.1059 | 280.2826 | 281.0242
979.7073 | 348.9636 | 280.3809 | 281.1495
980.7073 | 348.8723 | 280.4834 | 281.274
981.7073 | 348.8421 | 280.5756 | 281.3896
982.7073 | 348.8476 | 280.6727 | 281.5031
983.7073 | 348.915 | 280.7635 | 281.6216
984.7073 | 348.9124 | 280.8453 | 281.7458
985.7073 | 348.9341 | 280.9403 | 281.8591
986.7073 | 348.8141 | 281.049 | 281.9764
987.7073 | 348.6797 | 281.1431 | 282.1091
988.7073 | 348.564 | 281.2231 | 282.224
989.7073 | 348.4712 | 281.3373 | 282.3437
990.7073 | 348.3838 | 281.4369 | 282.471
991.7073 | 348.3148 | 281.5451 | 282.5792
992.7073 | 348.1677 | 281.6408 | 282.6975
993.7073 | 348.1055 | 281.7469 | 282.8087
994.7073 | 348.1426 | 281.8379 | 282.9178
995.7073 | 348.0541 | 281.9189 | 283.0346
996.7073 | 347.9534 | 282.0168 | 283.1389
997.7073 | 347.9253 | 282.1184 | 283.2465
998.7073 | 347.8002 | 282.202 | 283.3447
999.7073 | 347.6363 | 282.2947 | 283.4408
1000.7073 | 347.511 | 282.3763 | 283.5404
1001.7073 | 347.3002 | 282.4663 | 283.6336
1002.7073 | 347.3364 | 282.5275 | 283.7454
1003.7073 | 347.258 | 282.5992 | 283.8424
1004.7073 | 347.2735 | 282.6343 | 283.9311
1005.7073 | 347.3701 | 282.6697 | 284.0199
1006.7073 | 347.3566 | 282.7042 | 284.1065
1007.7073 | 347.331 | 282.7472 | 284.195
1008.7073 | 347.2655 | 282.8029 | 284.2736
1009.7073 | 347.2313 | 282.8553 | 284.3474
1010.7073 | 347.1724 | 282.9018 | 284.4198
1011.7073 | 347.2583 | 282.9377 | 284.479
1012.7073 | 347.3446 | 282.9848 | 284.5365
1013.7073 | 347.3065 | 283.0273 | 284.5739
1014.7073 | 347.2756 | 283.071 | 284.6024
1015.7073 | 347.2144 | 283.1013 | 284.6362
1016.7073 | 347.2047 | 283.1292 | 284.6642
1017.7073 | 347.1821 | 283.1716 | 284.6904
1018.7073 | 347.0469 | 283.1921 | 284.708
1019.7073 | 347.031 | 283.2032 | 284.7229
1020.7073 | 347.0387 | 283.2196 | 284.7326
1021.7073 | 347.107 | 283.2216 | 284.7478
1022.7073 | 347.1231 | 283.2326 | 284.7607
1023.7073 | 347.1703 | 283.238 | 284.7809
1024.7073 | 347.1359 | 283.2447 | 284.797
1025.7073 | 347.0206 | 283.2461 | 284.8169
1026.7073 | 346.9347 | 283.2521 | 284.8368
1027.7073 | 346.9111 | 283.2364 | 284.857
1028.7073 | 346.9556 | 283.2375 | 284.8816
1029.7073 | 347.1092 | 283.2364 | 284.8991
1030.7073 | 347.2651 | 283.2367 | 284.9192
1031.7073 | 347.1944 | 283.246 | 284.9433
1032.7073 | 347.153 | 283.2525 | 284.9683
1033.7073 | 347.1152 | 283.2418 | 284.9934
1034.7073 | 347.0563 | 283.2531 | 285.0059
1035.7073 | 347.0522 | 283.2416 | 285.0173
1036.7073 | 346.9604 | 283.2735 | 285.039
1037.7073 | 346.8814 | 283.2744 | 285.048
1038.7073 | 346.9405 | 283.2819 | 285.0541
1039.7073 | 347.0364 | 283.2801 | 285.065
1040.7073 | 347.0771 | 283.2906 | 285.06
1041.7073 | 347.0718 | 283.2932 | 285.0665
1042.7073 | 347.1557 | 283.3004 | 285.0652
1043.7073 | 347.3422 | 283.3053 | 285.0604
1044.7073 | 347.3867 | 283.3138 | 285.0612
1045.7073 | 347.386 | 283.3147 | 285.0624
1046.7073 | 347.3294 | 283.3169 | 285.0618
1047.7073 | 347.4357 | 283.3583 | 285.0572
1048.7073 | 347.5746 | 283.3717 | 285.0622
1049.7073 | 347.5993 | 283.3674 | 285.0616
1050.7073 | 347.7254 | 283.3878 | 285.0563
1051.7073 | 347.7853 | 283.3967 | 285.0632
1052.7073 | 347.8157 | 283.4159 | 285.0546
1053.7073 | 347.901 | 283.4381 | 285.0624
1054.7073 | 347.8709 | 283.4544 | 285.0603
1055.7073 | 347.8395 | 283.482 | 285.0608
1056.7073 | 347.8859 | 283.5013 | 285.0602
1057.7073 | 347.8212 | 283.517 | 285.0696
1058.7073 | 347.7904 | 283.5432 | 285.0688
1059.7073 | 347.7448 | 283.5675 | 285.0883
1060.7073 | 347.7784 | 283.6083 | 285.0969
1061.7073 | 347.7095 | 283.6264 | 285.1138
1062.7073 | 347.7112 | 283.6551 | 285.1277
1063.7073 | 347.7186 | 283.6918 | 285.151
1064.7073 | 347.7604 | 283.7379 | 285.1688
1065.7073 | 347.8084 | 283.7833 | 285.1881
1066.7073 | 347.8034 | 283.8087 | 285.2137
1067.7073 | 347.8774 | 283.849 | 285.2457
1068.7073 | 347.987 | 283.8992 | 285.2795
1069.7073 | 348.0369 | 283.9418 | 285.3155
1070.7073 | 348.1593 | 284.0007 | 285.3497
1071.7073 | 348.1494 | 284.0385 | 285.3907
1072.7073 | 348.1141 | 284.0983 | 285.4308
1073.7073 | 348.1366 | 284.1544 | 285.4767
1074.7073 | 348.2203 | 284.2019 | 285.5254
1075.7073 | 348.352 | 284.2693 | 285.5793
1076.7073 | 348.426 | 284.3178 | 285.6339
1077.7073 | 348.5624 | 284.3876 | 285.6969
1078.7073 | 348.6361 | 284.4561 | 285.7512
1079.7073 | 348.6259 | 284.5448 | 285.8183
1080.7073 | 348.5252 | 284.5704 | 285.8789
1081.7073 | 348.4738 | 284.6617 | 285.9577
1082.7073 | 348.4887 | 284.7435 | 286.0279
1083.7073 | 348.3539 | 284.798 | 286.0997
1084.7073 | 348.3455 | 284.8855 | 286.1687
1085.7073 | 348.4737 | 284.9538 | 286.2543
1086.7073 | 348.6232 | 285.0233 | 286.3234
1087.7073 | 348.6723 | 285.0882 | 286.4004
1088.7073 | 348.6924 | 285.1648 | 286.4912
1089.7073 | 348.6816 | 285.2439 | 286.5762
1090.7073 | 348.664 | 285.3101 | 286.6565
1091.7073 | 348.616 | 285.3881 | 286.7384
1092.7073 | 348.5905 | 285.4431 | 286.8206
1093.7073 | 348.5168 | 285.5474 | 286.9156
1094.7073 | 348.4801 | 285.5987 | 286.9907
1095.7073 | 348.5489 | 285.6898 | 287.0894
1096.7073 | 348.5332 | 285.7527 | 287.1689
1097.7073 | 348.6356 | 285.8296 | 287.258
1098.7073 | 348.6568 | 285.9083 | 287.3545
1099.7073 | 348.561 | 285.974 | 287.4313
1100.7073 | 348.5136 | 286.0401 | 287.5158
1101.7073 | 348.4102 | 286.1241 | 287.609
1102.7073 | 348.2775 | 286.199 | 287.7012
1103.7073 | 348.1814 | 286.2439 | 287.7858
1104.7073 | 348.0475 | 286.3256 | 287.8663
1105.7073 | 347.9827 | 286.3954 | 287.9541
1106.7073 | 347.8995 | 286.4535 | 288.0454
1107.7073 | 347.8627 | 286.5067 | 288.1275
1108.7073 | 347.8102 | 286.5897 | 288.215
1109.7073 | 347.7467 | 286.6571 | 288.2983
1110.7073 | 347.7633 | 286.7073 | 288.3777
1111.7073 | 347.782 | 286.7594 | 288.4666
1112.7073 | 347.7409 | 286.825 | 288.5513
1113.7073 | 347.686 | 286.8836 | 288.6281
1114.7073 | 347.6118 | 286.9581 | 288.7087
1115.7073 | 347.5858 | 287.0134 | 288.8011
1116.7073 | 347.4715 | 287.0747 | 288.886
1117.7073 | 347.4176 | 287.1291 | 288.974
1118.7073 | 347.3219 | 287.195 | 289.0436
1119.7073 | 347.3053 | 287.2447 | 289.1156
1120.7073 | 347.3548 | 287.3106 | 289.2004
1121.7073 | 347.4277 | 287.3539 | 289.2748
1122.7073 | 347.4857 | 287.418 | 289.3472
1123.7073 | 347.5449 | 287.4673 | 289.4247
1124.7073 | 347.5052 | 287.5184 | 289.4903
1125.7073 | 347.3652 | 287.566 | 289.5739
1126.7073 | 347.3829 | 287.6254 | 289.6501
1127.7073 | 347.4144 | 287.6853 | 289.7176
1128.7073 | 347.4178 | 287.7258 | 289.7859
1129.7073 | 347.4352 | 287.7776 | 289.8611
1130.7073 | 347.565 | 287.8209 | 289.9308
1131.7073 | 347.67 | 287.876 | 289.9981
1132.7073 | 347.7021 | 287.9163 | 290.0631
1133.7073 | 347.6877 | 287.9691 | 290.1293
1134.7073 | 347.7584 | 288.0166 | 290.1978
1135.7073 | 347.6936 | 288.0406 | 290.2663
1136.7073 | 347.7701 | 288.093 | 290.3373
1137.7073 | 347.8423 | 288.1224 | 290.3944
1138.7073 | 347.7249 | 288.1695 | 290.4576
1139.7073 | 347.6546 | 288.2025 | 290.5192
1140.7073 | 347.5502 | 288.2437 | 290.5761
1141.7073 | 347.4052 | 288.2898 | 290.6413
1142.7073 | 347.542 | 288.3115 | 290.6969
1143.7073 | 347.6494 | 288.3619 | 290.7568
1144.7073 | 347.5722 | 288.3843 | 290.8119
1145.7073 | 347.4758 | 288.4173 | 290.87
1146.7073 | 347.3595 | 288.4579 | 290.9313
1147.7073 | 347.3676 | 288.4644 | 290.9902
1148.7073 | 347.3803 | 288.5219 | 291.0417
1149.7073 | 347.3317 | 288.5465 | 291.0941
1150.7073 | 347.4258 | 288.5818 | 291.1565
1151.7073 | 347.3774 | 288.6016 | 291.2062
1152.7073 | 347.3169 | 288.64 | 291.2589
1153.7073 | 347.4314 | 288.6709 | 291.3008
1154.7073 | 347.4624 | 288.686 | 291.3533
1155.7073 | 347.4554 | 288.7238 | 291.4028
1156.7073 | 347.5526 | 288.7652 | 291.4562
1157.7073 | 347.6841 | 288.785 | 291.508
1158.7073 | 347.673 | 288.8245 | 291.55
1159.7073 | 347.7158 | 288.8614 | 291.5977
1160.7073 | 347.7297 | 288.8844 | 291.6412
1161.7073 | 347.7413 | 288.9199 | 291.6852
1162.7073 | 347.7089 | 288.9426 | 291.7301
1163.7073 | 347.6804 | 288.9618 | 291.7763
1164.7073 | 347.5867 | 288.9931 | 291.8175
1165.7073 | 347.5098 | 289.0342 | 291.8661
1166.7073 | 347.5448 | 289.0612 | 291.9063
1167.7073 | 347.6028 | 289.0894 | 291.9424
1168.7073 | 347.6083 | 289.1236 | 291.984
1169.7073 | 347.598 | 289.1531 | 292.0252
1170.7073 | 347.5803 | 289.1799 | 292.0693
1171.7073 | 347.5733 | 289.205 | 292.1053
1172.7073 | 347.5529 | 289.2375 | 292.1403
1173.7073 | 347.4656 | 289.2581 | 292.1757
1174.7073 | 347.428 | 289.2942 | 292.2135
1175.7073 | 347.4586 | 289.3015 | 292.251
1176.7073 | 347.4848 | 289.3485 | 292.2872
1177.7073 | 347.4155 | 289.3716 | 292.322
1178.7073 | 347.3549 | 289.403 | 292.3582
1179.7073 | 347.3108 | 289.4122 | 292.3902
1180.7073 | 347.2643 | 289.4402 | 292.4252
1181.7073 | 347.2038 | 289.4705 | 292.4586
1182.7073 | 347.284 | 289.4948 | 292.4803
1183.7073 | 347.2497 | 289.526 | 292.5198
1184.7073 | 347.1862 | 289.5527 | 292.5419
1185.7073 | 347.1533 | 289.5791 | 292.574
1186.7073 | 347.1996 | 289.6048 | 292.5951
1187.7073 | 347.2436 | 289.6223 | 292.6195
1188.7073 | 347.3122 | 289.6487 | 292.6459
1189.7073 | 347.4242 | 289.6875 | 292.6828
1190.7073 | 347.4814 | 289.7068 | 292.6998
1191.7073 | 347.3983 | 289.739 | 292.7333
1192.7073 | 347.3511 | 289.7614 | 292.7591
1193.7073 | 347.2914 | 289.8018 | 292.7818
1194.7073 | 347.2391 | 289.8283 | 292.8048
1195.7073 | 347.1756 | 289.8542 | 292.8355
1196.7073 | 347.2213 | 289.8757 | 292.8598
1197.7073 | 347.2294 | 289.9203 | 292.8824
1198.7073 | 347.2466 | 289.9417 | 292.9146
1199.7073 | 347.2608 | 289.9842 | 292.9412
1200.7073 | 347.2978 | 290.0011 | 292.9578
1201.7073 | 347.2825 | 290.0491 | 292.9692
1202.7073 | 347.3045 | 290.0729 | 292.9853
1203.7073 | 347.3502 | 290.0896 | 292.9995
1204.7073 | 347.3055 | 290.1189 | 293.0082
1205.7073 | 347.1941 | 290.1448 | 293.0348
1206.7073 | 347.1043 | 290.1785 | 293.0521
1207.7073 | 347.2008 | 290.2001 | 293.073
1208.7073 | 347.1504 | 290.2266 | 293.0967
1209.7073 | 347.1185 | 290.2584 | 293.1169
1210.7073 | 347.1294 | 290.2883 | 293.1448
1211.7073 | 347.1801 | 290.3149 | 293.172
1212.7073 | 347.2512 | 290.3276 | 293.2027
1213.7073 | 347.248 | 290.3738 | 293.2237
1214.7073 | 347.29 | 290.3881 | 293.2447
1215.7073 | 347.3754 | 290.4203 | 293.2764
1216.7073 | 347.4809 | 290.4549 | 293.2992
1217.7073 | 347.5647 | 290.4744 | 293.3267
1218.7073 | 347.5582 | 290.481 | 293.3547
1219.7073 | 347.652 | 290.5398 | 293.3771
1220.7073 | 347.7674 | 290.5504 | 293.4059
1221.7073 | 347.8071 | 290.58 | 293.4283
1222.7073 | 347.733 | 290.5993 | 293.4598
1223.7073 | 347.7804 | 290.6198 | 293.4799
1224.7073 | 347.6807 | 290.6521 | 293.5043
1225.7073 | 347.7339 | 290.6834 | 293.5279
1226.7073 | 347.826 | 290.6963 | 293.5622
1227.7073 | 347.8988 | 290.7085 | 293.5814
1228.7073 | 347.9057 | 290.752 | 293.6207
1229.7073 | 347.977 | 290.7619 | 293.6454
1230.7073 | 348.0348 | 290.7915 | 293.6678
1231.7073 | 348.0495 | 290.8254 | 293.688
1232.7073 | 348.0663 | 290.8497 | 293.7183
1233.7073 | 348.0666 | 290.8433 | 293.7424
1234.7073 | 348.1085 | 290.9008 | 293.7652
1235.7073 | 348.1183 | 290.9174 | 293.7982
1236.7073 | 348.1271 | 290.9364 | 293.8162
1237.7073 | 348.1409 | 290.9706 | 293.8449
1238.7073 | 348.1334 | 290.9964 | 293.8679
1239.7073 | 348.2092 | 291.0332 | 293.8904
1240.7073 | 348.2153 | 291.0569 | 293.9141
1241.7073 | 348.1746 | 291.0824 | 293.9446
1242.7073 | 348.0808 | 291.1001 | 293.9715
1243.7073 | 348.0361 | 291.1318 | 293.9919
1244.7073 | 348.0496 | 291.1477 | 294.0075
1245.7073 | 348.1033 | 291.1797 | 294.0377
1246.7073 | 348.0527 | 291.1965 | 294.0592
1247.7073 | 347.9611 | 291.2313 | 294.085
1248.7073 | 347.8506 | 291.2546 | 294.1121
1249.7073 | 347.6942 | 291.2811 | 294.1327
1250.7073 | 347.6286 | 291.3168 | 294.1589
1251.7073 | 347.646 | 291.3449 | 294.1783
1252.7073 | 347.7346 | 291.3675 | 294.2098
1253.7073 | 347.7666 | 291.3826 | 294.2364
1254.7073 | 347.7525 | 291.4099 | 294.2651
1255.7073 | 347.7174 | 291.4596 | 294.2875
1256.7073 | 347.7937 | 291.4594 | 294.3107
1257.7073 | 347.8236 | 291.4885 | 294.3369
1258.7073 | 347.8479 | 291.5274 | 294.3687
1259.7073 | 347.8682 | 291.5297 | 294.3974
1260.7073 | 347.8755 | 291.5597 | 294.4233
1261.7073 | 347.8466 | 291.5948 | 294.4552
1262.7073 | 347.8797 | 291.6085 | 294.484
1263.7073 | 347.8771 | 291.648 | 294.515
1264.7073 | 347.7592 | 291.6665 | 294.5363
1265.7073 | 347.7386 | 291.6779 | 294.5689
1266.7073 | 347.7396 | 291.708 | 294.5996
1267.7073 | 347.7208 | 291.727 | 294.6289
1268.7073 | 347.6768 | 291.7623 | 294.6647
1269.7073 | 347.6734 | 291.7817 | 294.6914
1270.7073 | 347.7344 | 291.8098 | 294.7212
1271.7073 | 347.7524 | 291.8226 | 294.7578
1272.7073 | 347.7569 | 291.8547 | 294.7878
1273.7073 | 347.7753 | 291.8824 | 294.8213
1274.7073 | 347.82 | 291.9042 | 294.8511
1275.7073 | 347.7323 | 291.927 | 294.8843
1276.7073 | 347.7325 | 291.9602 | 294.9184
1277.7073 | 347.6867 | 291.9764 | 294.9496
1278.7073 | 347.6685 | 291.998 | 294.9872
1279.7073 | 347.678 | 292.0326 | 295.02
1280.7073 | 347.6666 | 292.0414 | 295.053
1281.7073 | 347.7266 | 292.0895 | 295.0853
1282.7073 | 347.7041 | 292.1017 | 295.1225
1283.7073 | 347.6586 | 292.1443 | 295.1563
1284.7073 | 347.5547 | 292.1627 | 295.1871
1285.7073 | 347.578 | 292.1984 | 295.2271
1286.7073 | 347.483 | 292.2163 | 295.2674
1287.7073 | 347.5303 | 292.2449 | 295.2971
1288.7073 | 347.6635 | 292.2819 | 295.3419
1289.7073 | 347.7606 | 292.3028 | 295.3833
1290.7073 | 347.8534 | 292.3314 | 295.4134
1291.7073 | 347.8571 | 292.3612 | 295.4478
1292.7073 | 347.8839 | 292.3776 | 295.4871
1293.7073 | 347.8624 | 292.4138 | 295.5195
1294.7073 | 347.7614 | 292.4382 | 295.5538
1295.7073 | 347.6882 | 292.461 | 295.5842
1296.7073 | 347.6007 | 292.487 | 295.6186
1297.7073 | 347.5531 | 292.5187 | 295.6525
1298.7073 | 347.412 | 292.5541 | 295.6885
1299.7073 | 347.331 | 292.5788 | 295.7177
1300.7073 | 347.2389 | 292.5781 | 295.7597
1301.7073 | 347.1842 | 292.6378 | 295.7901
1302.7073 | 347.1177 | 292.6513 | 295.8275
1303.7073 | 347.0982 | 292.6909 | 295.858
1304.7073 | 347.0849 | 292.7107 | 295.8986
1305.7073 | 347.1286 | 292.7448 | 295.9334
1306.7073 | 347.2156 | 292.7691 | 295.9726
1307.7073 | 347.2749 | 292.7889 | 296.0055
1308.7073 | 347.4151 | 292.815 | 296.0378
1309.7073 | 347.3705 | 292.8266 | 296.0665
1310.7073 | 347.2854 | 292.8725 | 296.101
1311.7073 | 347.21 | 292.9024 | 296.1344
1312.7073 | 347.2589 | 292.9065 | 296.1704
1313.7073 | 347.28 | 292.9345 | 296.2107
1314.7073 | 347.3132 | 292.9648 | 296.2409
1315.7073 | 347.3249 | 292.9685 | 296.2796
1316.7073 | 347.3953 | 293.0075 | 296.3061
1317.7073 | 347.3268 | 293.0229 | 296.3459
1318.7073 | 347.2186 | 293.0494 | 296.3797
1319.7073 | 347.1734 | 293.0745 | 296.4129
1320.7073 | 347.148 | 293.094 | 296.4462
1321.7073 | 347.211 | 293.1024 | 296.4769
1322.7073 | 347.2662 | 293.1419 | 296.5121
1323.7073 | 347.277 | 293.1505 | 296.5478
1324.7073 | 347.2792 | 293.1798 | 296.5837
1325.7073 | 347.3333 | 293.1958 | 296.6184
1326.7073 | 347.3162 | 293.2289 | 296.6512
1327.7073 | 347.3702 | 293.235 | 296.687
1328.7073 | 347.3415 | 293.2721 | 296.7199
1329.7073 | 347.2911 | 293.2877 | 296.7461
1330.7073 | 347.2927 | 293.3142 | 296.7841
1331.7229 | 347.2716 | 293.3375 | 296.8208
1332.7073 | 347.3074 | 293.3617 | 296.8569
1333.7073 | 347.3533 | 293.3833 | 296.8793
1334.7073 | 347.3312 | 293.3841 | 296.917
1335.7073 | 347.3779 | 293.4229 | 296.9507
1336.7073 | 347.3317 | 293.443 | 296.9973
1337.7073 | 347.4168 | 293.4514 | 297.0194
1338.7073 | 347.4377 | 293.4731 | 297.0621
1339.7073 | 347.4032 | 293.4933 | 297.0941
1340.7073 | 347.3283 | 293.5143 | 297.1212
1341.7073 | 347.3893 | 293.5451 | 297.1545
1342.7073 | 347.3088 | 293.5515 | 297.1989
1343.7073 | 347.3393 | 293.578 | 297.233
1344.7073 | 347.3231 | 293.607 | 297.265
1345.7073 | 347.3673 | 293.6276 | 297.2998
1346.7073 | 347.2821 | 293.6426 | 297.3247
1347.7073 | 347.2469 | 293.6713 | 297.3621
1348.7073 | 347.289 | 293.6804 | 297.4002
1349.7073 | 347.336 | 293.6777 | 297.4323
1350.7073 | 347.424 | 293.7318 | 297.4722
1351.7073 | 347.3695 | 293.7546 | 297.5022
1352.7073 | 347.2858 | 293.7673 | 297.5291
1353.7073 | 347.271 | 293.7968 | 297.569
1354.7073 | 347.2763 | 293.8211 | 297.6043
1355.7073 | 347.2742 | 293.8111 | 297.632
1356.7073 | 347.1031 | 293.8615 | 297.6656
1357.7073 | 347.0178 | 293.8859 | 297.7001
1358.7073 | 346.9617 | 293.911 | 297.7286
1359.7073 | 346.8766 | 293.933 | 297.7739
1360.7073 | 346.7726 | 293.9457 | 297.7994
1361.7229 | 346.6609 | 293.9748 | 297.8308
1362.7073 | 346.5426 | 293.9902 | 297.8623
1363.7073 | 346.5603 | 294.0164 | 297.9069
1364.7073 | 346.5545 | 294.0429 | 297.9361
1365.7073 | 346.5042 | 294.0686 | 297.9698
1366.7073 | 346.4876 | 294.0891 | 298.0018
1367.7073 | 346.5155 | 294.1075 | 298.0261
1368.7073 | 346.541 | 294.1368 | 298.0622
1369.7073 | 346.5202 | 294.1608 | 298.0907
1370.7073 | 346.5111 | 294.1822 | 298.1218
1371.7073 | 346.6082 | 294.2049 | 298.1405
1372.7073 | 346.6535 | 294.2138 | 298.1842
1373.7073 | 346.6339 | 294.2502 | 298.2152
1374.7073 | 346.6326 | 294.2562 | 298.2447
1375.7073 | 346.6787 | 294.2856 | 298.2775
1376.7073 | 346.7279 | 294.3106 | 298.3006
1377.7073 | 346.7706 | 294.3182 | 298.3366
1378.7073 | 346.7389 | 294.3547 | 298.364
1379.7073 | 346.6911 | 294.3711 | 298.3882
1380.7073 | 346.6001 | 294.3826 | 298.4119
1381.7073 | 346.5919 | 294.421 | 298.4365
1382.7073 | 346.6014 | 294.4398 | 298.4674
1383.7073 | 346.6321 | 294.4529 | 298.4992
1384.7073 | 346.7459 | 294.4575 | 298.5275
1385.7073 | 346.7996 | 294.4948 | 298.5534
1386.7073 | 346.849 | 294.5213 | 298.5718
1387.7073 | 346.9241 | 294.5438 | 298.6042
1388.7073 | 346.9253 | 294.5605 | 298.6335
1389.7073 | 346.817 | 294.5825 | 298.6601
1390.7073 | 346.7511 | 294.5956 | 298.687
1391.7229 | 346.8811 | 294.6268 | 298.7147
1392.7073 | 346.8397 | 294.6532 | 298.739
1393.7073 | 346.893 | 294.673 | 298.7724
1394.7073 | 346.9679 | 294.7081 | 298.7996
1395.7073 | 346.9782 | 294.723 | 298.8318
1396.7073 | 346.9938 | 294.738 | 298.8527
1397.7073 | 347.0561 | 294.7632 | 298.8894
1398.7073 | 347.2273 | 294.778 | 298.9113
1399.7073 | 347.2269 | 294.8044 | 298.9402
1400.7073 | 347.2204 | 294.8298 | 298.9658
1401.7073 | 347.0786 | 294.8481 | 298.9963
1402.7073 | 346.8949 | 294.8685 | 299.0178
1403.7073 | 346.8508 | 294.9011 | 299.0451
1404.7073 | 346.8732 | 294.9001 | 299.0765
1405.7073 | 346.8284 | 294.929 | 299.1139
1406.7073 | 346.7352 | 294.9506 | 299.129
1407.7073 | 346.8591 | 294.9789 | 299.1617
1408.7073 | 346.9671 | 294.989 | 299.1842
1409.7073 | 347.0066 | 295.0139 | 299.2056
1410.7073 | 347.0012 | 295.0479 | 299.238
1411.7073 | 347.0009 | 295.0652 | 299.2661
1412.7073 | 346.9823 | 295.0919 | 299.2913
1413.7073 | 346.9714 | 295.1155 | 299.3085
1414.7073 | 346.9858 | 295.1369 | 299.3425
1415.7073 | 346.8668 | 295.1489 | 299.3669
1416.7073 | 346.8402 | 295.1638 | 299.3956
1417.7073 | 346.8618 | 295.1964 | 299.4208
1418.7073 | 347.0086 | 295.2167 | 299.4441
1419.7073 | 347.126 | 295.2346 | 299.4746
1420.7073 | 347.2018 | 295.2569 | 299.49
1421.7073 | 347.1895 | 295.2849 | 299.5188
1422.7073 | 347.1239 | 295.3051 | 299.5317
1423.7073 | 347.1618 | 295.3281 | 299.5618
1424.7073 | 347.2345 | 295.3532 | 299.5866
1425.7073 | 347.2638 | 295.3777 | 299.6127
1426.7073 | 347.3058 | 295.3948 | 299.6369
1427.7073 | 347.2295 | 295.4066 | 299.6505
1428.7073 | 347.2438 | 295.4404 | 299.682
1429.7073 | 347.2626 | 295.4675 | 299.7045
1430.7073 | 347.1772 | 295.4969 | 299.7303
1431.7073 | 347.1014 | 295.5093 | 299.7492
1432.7073 | 347.1934 | 295.5347 | 299.7748
1433.7073 | 347.3761 | 295.5591 | 299.8019
1434.7073 | 347.4277 | 295.5839 | 299.82
1435.7073 | 347.3362 | 295.593 | 299.8401
1436.7073 | 347.3458 | 295.6089 | 299.8714
1437.7073 | 347.3065 | 295.6512 | 299.8824
1438.7073 | 347.1554 | 295.666 | 299.908
1439.7073 | 347.0292 | 295.6974 | 299.933
1440.7073 | 347.0131 | 295.7071 | 299.956
1441.7073 | 347.0076 | 295.7298 | 299.9853
1442.7073 | 347.056 | 295.7614 | 300.0051
1443.7073 | 347.0582 | 295.7724 | 300.0303
1444.7073 | 347.1027 | 295.7894 | 300.0506
1445.7073 | 347.0575 | 295.8128 | 300.076
1446.7073 | 347.077 | 295.8189 | 300.0934
1447.7073 | 347.0542 | 295.8573 | 300.1206
1448.7073 | 347.0374 | 295.8717 | 300.1349
1449.7073 | 347.1212 | 295.8881 | 300.1584
1450.7073 | 347.0624 | 295.888 | 300.1752
1451.7073 | 347.1019 | 295.9114 | 300.1989
1452.7073 | 347.0532 | 295.9332 | 300.2195
1453.7073 | 347.0685 | 295.9471 | 300.2402
1454.7073 | 347.1983 | 295.9549 | 300.2578
1455.7073 | 347.2553 | 295.9797 | 300.2809
1456.7073 | 347.2231 | 295.9959 | 300.2977
1457.7073 | 347.1653 | 296.0088 | 300.3123
1458.7073 | 347.1946 | 296.0422 | 300.3374
1459.7073 | 347.2871 | 296.0426 | 300.3515
1460.7073 | 347.407 | 296.0532 | 300.3628
1461.7073 | 347.4062 | 296.0771 | 300.3764
1462.7073 | 347.3582 | 296.0801 | 300.3942
1463.7073 | 347.4269 | 296.0987 | 300.4108
1464.7073 | 347.4962 | 296.1099 | 300.419
1465.7073 | 347.3936 | 296.1292 | 300.4398
1466.7073 | 347.2833 | 296.162 | 300.4553
1467.7073 | 347.2496 | 296.1605 | 300.4638
1468.7073 | 347.2658 | 296.1805 | 300.4801
1469.7073 | 347.1825 | 296.1995 | 300.4905
1470.7073 | 347.0511 | 296.2171 | 300.5016
1471.7073 | 346.8742 | 296.2397 | 300.5159
1472.7073 | 346.8221 | 296.2488 | 300.5345
1473.7073 | 346.7788 | 296.2518 | 300.5535
1474.7073 | 346.8215 | 296.281 | 300.5701
1475.7073 | 346.7421 | 296.2907 | 300.5848
1476.7073 | 346.6128 | 296.3004 | 300.6024
1477.7073 | 346.4487 | 296.3222 | 300.6147
1478.7073 | 346.2474 | 296.3389 | 300.6383
1479.7073 | 346.1799 | 296.3532 | 300.656
1480.7073 | 346.1577 | 296.3714 | 300.673
1481.7229 | 346.1704 | 296.3989 | 300.6913
1482.7073 | 346.1734 | 296.4028 | 300.7117
1483.7073 | 346.2681 | 296.4299 | 300.7275
1484.7073 | 346.2883 | 296.4472 | 300.7511
1485.7073 | 346.1933 | 296.4653 | 300.7715
1486.7073 | 346.2033 | 296.4672 | 300.788
1487.7073 | 346.2286 | 296.4877 | 300.8041
1488.7073 | 346.2432 | 296.5106 | 300.832
1489.7073 | 346.2327 | 296.5281 | 300.8569
1490.7073 | 346.2845 | 296.5604 | 300.8738
1491.7073 | 346.3914 | 296.5631 | 300.9001
1492.7073 | 346.5087 | 296.5906 | 300.9164
1493.7073 | 346.5358 | 296.5896 | 300.9388
1494.7073 | 346.5632 | 296.6307 | 300.966
1495.7073 | 346.5797 | 296.6365 | 300.9806
1496.7073 | 346.6436 | 296.6455 | 301.0117
1497.7073 | 346.6621 | 296.6842 | 301.0234
1498.7073 | 346.6194 | 296.6942 | 301.0561
1499.7073 | 346.5612 | 296.7037 | 301.0728
1500.7073 | 346.5393 | 296.7237 | 301.101
1501.7073 | 346.5672 | 296.7384 | 301.1256
1502.7073 | 346.6289 | 296.7688 | 301.1538
1503.7073 | 346.5941 | 296.7729 | 301.1729
1504.7073 | 346.641 | 296.7929 | 301.2032
1505.7073 | 346.6698 | 296.8157 | 301.2303
1506.7073 | 346.7675 | 296.8313 | 301.2556
1507.7073 | 346.7982 | 296.8566 | 301.273
1508.7073 | 346.8077 | 296.8763 | 301.3038
1509.7073 | 346.8828 | 296.8867 | 301.3278
1510.7073 | 346.9885 | 296.8976 | 301.3556
1511.7229 | 347.0733 | 296.9248 | 301.3851
1512.7073 | 347.0946 | 296.9327 | 301.411
1513.7073 | 347.0072 | 296.9455 | 301.4326
1514.7073 | 346.9068 | 296.9815 | 301.4643
1515.7073 | 346.9437 | 296.9757 | 301.4969
1516.7073 | 347.0054 | 296.9909 | 301.5141
1517.7073 | 347.0108 | 297.0219 | 301.5493
1518.7073 | 346.9985 | 297.0358 | 301.5741
1519.7073 | 347.0385 | 297.056 | 301.5991
1520.7073 | 347.0666 | 297.0713 | 301.6236
1521.7073 | 347.1733 | 297.0756 | 301.6509
1522.7073 | 347.1894 | 297.1076 | 301.6753
1523.7073 | 347.0973 | 297.1171 | 301.7054
1524.7073 | 347.0682 | 297.1309 | 301.74
1525.7073 | 347.0632 | 297.1583 | 301.7607
1526.7073 | 347.1042 | 297.1551 | 301.7942
1527.7073 | 347.182 | 297.1944 | 301.8183
1528.7073 | 347.2153 | 297.2119 | 301.8438
1529.7073 | 347.2263 | 297.2295 | 301.869
1530.7073 | 347.1612 | 297.2407 | 301.8937
1531.7073 | 347.0161 | 297.2637 | 301.9282
1532.7073 | 346.9616 | 297.2844 | 301.95
1533.7073 | 346.9789 | 297.3088 | 301.9767
1534.7073 | 346.9573 | 297.3265 | 302.0063
1535.7073 | 346.9926 | 297.3491 | 302.0358
1536.7073 | 347.0607 | 297.3666 | 302.0606
1537.7073 | 346.9763 | 297.3846 | 302.0913
1538.7073 | 346.9109 | 297.4008 | 302.118
1539.7073 | 346.7699 | 297.4242 | 302.1418
1540.7073 | 346.6535 | 297.4465 | 302.1653
1541.7073 | 346.6043 | 297.485 | 302.1994
1542.7073 | 346.6761 | 297.4879 | 302.2225
1543.7073 | 346.8018 | 297.5142 | 302.249
1544.7073 | 346.8299 | 297.5257 | 302.2766
1545.7073 | 346.752 | 297.5542 | 302.3055
1546.7073 | 346.6601 | 297.5702 | 302.335
1547.7073 | 346.5797 | 297.5956 | 302.3585
1548.7073 | 346.5563 | 297.6154 | 302.3921
1549.7073 | 346.567 | 297.6448 | 302.4152
1550.7073 | 346.5922 | 297.6465 | 302.4441
1551.7073 | 346.5629 | 297.6828 | 302.4728
1552.7073 | 346.5941 | 297.6891 | 302.5001
1553.7073 | 346.5755 | 297.7189 | 302.5203
1554.7073 | 346.6839 | 297.7234 | 302.5519
1555.7073 | 346.6862 | 297.7578 | 302.5817
1556.7073 | 346.6465 | 297.7754 | 302.602
1557.7073 | 346.537 | 297.8039 | 302.6291
1558.7073 | 346.4158 | 297.811 | 302.6546
1559.7229 | 346.4485 | 297.8309 | 302.6855
1560.7073 | 346.4926 | 297.8492 | 302.7088
1561.7073 | 346.6273 | 297.8828 | 302.7295
1562.7073 | 346.6218 | 297.9077 | 302.7592
1563.7073 | 346.7155 | 297.9299 | 302.7876
1564.7073 | 346.8279 | 297.9465 | 302.8202
1565.7073 | 346.8514 | 297.9705 | 302.841
1566.7073 | 346.9558 | 297.9882 | 302.8676
1567.7073 | 347.0392 | 297.998 | 302.8979
1568.7073 | 347.0036 | 298.0161 | 302.9281
1569.7073 | 346.9257 | 298.0564 | 302.9601
1570.7073 | 346.9412 | 298.0719 | 302.982
1571.7229 | 347.0243 | 298.0924 | 303.0183
1572.7073 | 347.0096 | 298.1228 | 303.0466
1573.7073 | 346.9498 | 298.1373 | 303.0738
1574.7073 | 346.9796 | 298.1647 | 303.1002
1575.7073 | 347.0559 | 298.1871 | 303.1317
1576.7073 | 347.1391 | 298.2138 | 303.1575
1577.7073 | 347.1635 | 298.2202 | 303.1878
1578.7073 | 347.1497 | 298.2499 | 303.2122
1579.7073 | 347.2765 | 298.2709 | 303.248
1580.7073 | 347.4547 | 298.3041 | 303.2819
1581.7073 | 347.4924 | 298.3198 | 303.3137
1582.7073 | 347.4951 | 298.3407 | 303.3497
1583.7073 | 347.3745 | 298.3707 | 303.3707
1584.7073 | 347.4041 | 298.384 | 303.4033
1585.7073 | 347.4869 | 298.4096 | 303.4313
1586.7073 | 347.6199 | 298.4194 | 303.4747
1587.7073 | 347.7111 | 298.4345 | 303.4983
1588.7073 | 347.6036 | 298.465 | 303.5257
1589.7073 | 347.5139 | 298.5019 | 303.5619
1590.7073 | 347.4691 | 298.5087 | 303.5938
1591.7073 | 347.4809 | 298.5373 | 303.6221
1592.7073 | 347.555 | 298.5552 | 303.6572
1593.7073 | 347.4868 | 298.5763 | 303.6877
1594.7073 | 347.4704 | 298.5954 | 303.7174
1595.7073 | 347.5245 | 298.6044 | 303.7514
1596.7073 | 347.5735 | 298.6269 | 303.7923
1597.7073 | 347.5483 | 298.6516 | 303.8197
1598.7073 | 347.5733 | 298.6702 | 303.8515
1599.7073 | 347.475 | 298.6901 | 303.8776
1600.7073 | 347.4276 | 298.7122 | 303.9199
1601.7229 | 347.3476 | 298.7247 | 303.9368
1602.7073 | 347.3601 | 298.7551 | 303.9761
1603.7073 | 347.3072 | 298.7836 | 304.007
1604.7073 | 347.3193 | 298.7866 | 304.0316
1605.7073 | 347.3098 | 298.8127 | 304.0745
1606.7073 | 347.2751 | 298.8252 | 304.1024
1607.7073 | 347.3952 | 298.8521 | 304.1324
1608.7073 | 347.4696 | 298.8431 | 304.1575
1609.7073 | 347.5 | 298.886 | 304.1937
1610.7073 | 347.5767 | 298.9171 | 304.2188
1611.7073 | 347.654 | 298.9267 | 304.2506
1612.7073 | 347.5403 | 298.9628 | 304.2784
1613.7073 | 347.4652 | 298.9581 | 304.3148
1614.7073 | 347.5347 | 298.9897 | 304.3443
1615.7073 | 347.6369 | 298.9971 | 304.3719
1616.7073 | 347.6 | 299.0235 | 304.3999
1617.7073 | 347.4707 | 299.0336 | 304.4336
1618.7073 | 347.5406 | 299.0593 | 304.4579
1619.7073 | 347.6144 | 299.0921 | 304.487
1620.7073 | 347.6623 | 299.1125 | 304.5118
1621.7073 | 347.543 | 299.1353 | 304.539
1622.7073 | 347.4773 | 299.1489 | 304.5698
1623.7073 | 347.4758 | 299.1788 | 304.5984
1624.7073 | 347.4896 | 299.1886 | 304.6254
1625.7073 | 347.493 | 299.2139 | 304.6584
1626.7073 | 347.3753 | 299.2363 | 304.6865
1627.7073 | 347.2605 | 299.2532 | 304.7117
1628.7073 | 347.1909 | 299.2674 | 304.7362
1629.7073 | 347.2162 | 299.2887 | 304.7685
1630.7073 | 347.2378 | 299.3159 | 304.7925
1631.7229 | 347.2706 | 299.3311 | 304.8168
1632.7073 | 347.3639 | 299.3405 | 304.834
1633.7073 | 347.4076 | 299.3756 | 304.853
1634.7073 | 347.3724 | 299.3815 | 304.8807
1635.7073 | 347.3755 | 299.4071 | 304.9092
1636.7073 | 347.4306 | 299.4457 | 304.937
1637.7073 | 347.3096 | 299.4386 | 304.9616
1638.7073 | 347.2684 | 299.4893 | 304.9794
1639.7073 | 347.2727 | 299.491 | 305.0008
1640.7073 | 347.2456 | 299.5225 | 305.0231
1641.7073 | 347.2019 | 299.5431 | 305.0443
1642.7073 | 347.1134 | 299.5504 | 305.0723
1643.7073 | 347.0199 | 299.5842 | 305.0914
1644.7073 | 346.9275 | 299.6038 | 305.114
1645.7073 | 346.8332 | 299.6164 | 305.141
1646.7073 | 346.8075 | 299.648 | 305.1679
1647.7073 | 346.7416 | 299.6643 | 305.1904
1648.7073 | 346.794 | 299.6662 | 305.2136
1649.7073 | 346.82 | 299.6995 | 305.237
1650.7073 | 346.8442 | 299.7166 | 305.2665
1651.7073 | 346.815 | 299.7424 | 305.2845
1652.7073 | 346.733 | 299.7638 | 305.3193
1653.7073 | 346.6974 | 299.7902 | 305.3354
1654.7073 | 346.7726 | 299.8135 | 305.3539
1655.7073 | 346.7913 | 299.7994 | 305.3733
1656.7073 | 346.7228 | 299.8496 | 305.3974
1657.7073 | 346.5985 | 299.8632 | 305.4244
1658.7073 | 346.6574 | 299.8868 | 305.4406
1659.7073 | 346.78 | 299.8945 | 305.4717
1660.7073 | 346.8044 | 299.9372 | 305.4989
1661.7229 | 346.7533 | 299.9362 | 305.5133
1662.7073 | 346.7743 | 299.9746 | 305.5333
1663.7073 | 346.8601 | 299.9733 | 305.5575
1664.7073 | 346.8893 | 299.998 | 305.5868
1665.7073 | 346.8903 | 300.0168 | 305.6065
1666.7073 | 346.9546 | 300.0336 | 305.6164
1667.7073 | 346.9136 | 300.0608 | 305.6492
1668.7073 | 346.8228 | 300.0787 | 305.665
1669.7073 | 346.8498 | 300.0948 | 305.6802
1670.7073 | 346.8246 | 300.0979 | 305.7123
1671.7073 | 346.9068 | 300.1262 | 305.7311
1672.7073 | 347.0223 | 300.1355 | 305.755
1673.7073 | 347.159 | 300.1665 | 305.7674
1674.7073 | 347.1774 | 300.1744 | 305.7822
1675.7073 | 347.2319 | 300.1809 | 305.8054
1676.7073 | 347.2599 | 300.196 | 305.8334
1677.7073 | 347.2838 | 300.2136 | 305.8397
1678.7073 | 347.2114 | 300.2207 | 305.8658
1679.7073 | 347.1737 | 300.2355 | 305.8813
1680.7073 | 347.0626 | 300.2532 | 305.8949
1681.7073 | 347.0531 | 300.2811 | 305.9142
1682.7073 | 347.0883 | 300.2794 | 305.9387
1683.7073 | 347.2003 | 300.2805 | 305.9531
1684.7073 | 347.2208 | 300.2956 | 305.965
1685.7073 | 347.2775 | 300.3212 | 305.9832
1686.7073 | 347.3567 | 300.3229 | 306.0005
1687.7073 | 347.4113 | 300.3408 | 306.0168
1688.7073 | 347.3395 | 300.3427 | 306.0407
1689.7073 | 347.2654 | 300.3463 | 306.0574
1690.7073 | 347.2143 | 300.3639 | 306.0713
1691.7229 | 347.2281 | 300.3698 | 306.0853
1692.7073 | 347.2245 | 300.3754 | 306.1046
1693.7073 | 347.1379 | 300.3854 | 306.1199
1694.7073 | 347.1371 | 300.3915 | 306.1356
1695.7073 | 347.1186 | 300.4212 | 306.1501
1696.7073 | 347.208 | 300.4146 | 306.1708
1697.7073 | 347.2653 | 300.4326 | 306.1911
1698.7073 | 347.3801 | 300.4383 | 306.2034
1699.7073 | 347.4858 | 300.4464 | 306.2154
1700.7073 | 347.4561 | 300.444 | 306.2291
1701.7073 | 347.415 | 300.4595 | 306.2473
1702.7073 | 347.4024 | 300.4661 | 306.2553
1703.7073 | 347.4196 | 300.4759 | 306.2671
1704.7073 | 347.5027 | 300.4783 | 306.2855
1705.7073 | 347.5577 | 300.4761 | 306.294
1706.7073 | 347.5759 | 300.5014 | 306.3043
1707.7073 | 347.5719 | 300.5082 | 306.3201
1708.7073 | 347.6637 | 300.5083 | 306.3271
1709.7073 | 347.6435 | 300.5287 | 306.3364
1710.7073 | 347.6751 | 300.5249 | 306.3466
1711.7073 | 347.736 | 300.5339 | 306.3618
1712.7073 | 347.7802 | 300.566 | 306.3697
1713.7073 | 347.7382 | 300.5586 | 306.3791
1714.7073 | 347.5667 | 300.5757 | 306.3868
1715.7073 | 347.4057 | 300.5774 | 306.4002
1716.7073 | 347.293 | 300.5924 | 306.4102
1717.7073 | 347.2974 | 300.597 | 306.4161
1718.7229 | 347.3241 | 300.6144 | 306.4213
1719.7073 | 347.3698 | 300.608 | 306.4326
1720.7073 | 347.4251 | 300.6196 | 306.4391
1721.7073 | 347.4404 | 300.6199 | 306.4525
1722.7229 | 347.3967 | 300.6404 | 306.4555
1723.7073 | 347.2851 | 300.6442 | 306.4721
1724.7073 | 347.2268 | 300.6378 | 306.4782
1725.7073 | 347.1548 | 300.6542 | 306.4918
1726.7073 | 347.1241 | 300.659 | 306.498
1727.7073 | 347.1571 | 300.6592 | 306.5079
1728.7073 | 347.2742 | 300.6806 | 306.5219
1729.7073 | 347.349 | 300.6743 | 306.5259
1730.7073 | 347.3124 | 300.674 | 306.5308
1731.7073 | 347.2317 | 300.6896 | 306.5412
1732.7073 | 347.3215 | 300.694 | 306.5472
1733.7073 | 347.4567 | 300.6988 | 306.5517
1734.7073 | 347.5303 | 300.7164 | 306.5525
1735.7073 | 347.5053 | 300.7242 | 306.5626
1736.7073 | 347.4111 | 300.7213 | 306.5645
1737.7073 | 347.414 | 300.7127 | 306.5681
1738.7073 | 347.539 | 300.7488 | 306.5754
1739.7073 | 347.6443 | 300.7362 | 306.5745
1740.7073 | 347.6925 | 300.7567 | 306.5822
1741.7073 | 347.7221 | 300.7544 | 306.587
1742.7073 | 347.5659 | 300.745 | 306.5969
1743.7073 | 347.5621 | 300.7719 | 306.6018
1744.7073 | 347.5883 | 300.7766 | 306.6009
1745.7073 | 347.5053 | 300.791 | 306.607
1746.7073 | 347.5488 | 300.7932 | 306.6108
1747.7073 | 347.666 | 300.792 | 306.6156
1748.7073 | 347.7325 | 300.804 | 306.6271
1749.7073 | 347.6319 | 300.8202 | 306.6286
1750.7073 | 347.6836 | 300.8085 | 306.6346
1751.7073 | 347.7715 | 300.8292 | 306.6438
1752.7073 | 347.7073 | 300.8336 | 306.6544
1753.7073 | 347.6604 | 300.8277 | 306.6519
1754.7073 | 347.6588 | 300.8501 | 306.661
1755.7073 | 347.5993 | 300.8533 | 306.6701
1756.7073 | 347.5612 | 300.8611 | 306.6786
1757.7073 | 347.6027 | 300.8569 | 306.6924
1758.7073 | 347.6371 | 300.8816 | 306.6996
1759.7073 | 347.6278 | 300.8694 | 306.7131
1760.7073 | 347.5796 | 300.8872 | 306.7212
1761.7073 | 347.5662 | 300.8777 | 306.7303
1762.7073 | 347.5124 | 300.8853 | 306.7425
1763.7073 | 347.4691 | 300.8921 | 306.7491
1764.7073 | 347.3897 | 300.9012 | 306.7653
1765.7073 | 347.3267 | 300.901 | 306.7704
1766.7073 | 347.2689 | 300.8878 | 306.7793
1767.7073 | 347.145 | 300.8979 | 306.7923
1768.7073 | 347.2759 | 300.8921 | 306.8039
1769.7073 | 347.359 | 300.9134 | 306.8121
1770.7073 | 347.48 | 300.9153 | 306.8255
1771.7073 | 347.4854 | 300.9189 | 306.8394
1772.7073 | 347.4428 | 300.9337 | 306.8418
1773.7073 | 347.2427 | 300.9261 | 306.8496
1774.7073 | 347.2985 | 300.9433 | 306.8576
1775.7073 | 347.3065 | 300.9348 | 306.8702
1776.7073 | 347.2953 | 300.9454 | 306.8773
1777.7073 | 347.2564 | 300.9546 | 306.8843
1778.7073 | 347.4312 | 300.9603 | 306.8934
1779.7073 | 347.6192 | 300.9579 | 306.902
1780.7073 | 347.6503 | 300.9508 | 306.9064
1781.7073 | 347.6083 | 300.9667 | 306.9189
1782.7073 | 347.7265 | 300.9689 | 306.9189
1783.7073 | 347.7411 | 300.9866 | 306.9279
1784.7073 | 347.7845 | 300.9927 | 306.9308
1785.7073 | 347.8785 | 300.9888 | 306.9377
1786.7073 | 347.9663 | 300.9942 | 306.9518
1787.7073 | 348.1356 | 301.0051 | 306.9544
1788.7073 | 348.2399 | 301.0062 | 306.9553
1789.7073 | 348.2284 | 301.0273 | 306.9645
1790.7073 | 348.1369 | 301.0267 | 306.9716
1791.7073 | 348.042 | 301.0177 | 306.9748
1792.7073 | 348.0787 | 301.0295 | 306.98
1793.7073 | 348.1009 | 301.0432 | 306.9867
1794.7073 | 348.1297 | 301.0365 | 306.9881
1795.7073 | 348.1661 | 301.0547 | 306.9946
1796.7073 | 348.0884 | 301.0478 | 306.9931
1797.7073 | 348.1918 | 301.0662 | 307.0005
1798.7073 | 348.3003 | 301.0799 | 307.0032
1799.7073 | 348.2109 | 301.0826 | 307.0038
1800.7073 | 348.1209 | 301.0938 | 307.0111
1801.7073 | 348.0964 | 301.0974 | 307.0183
1802.7073 | 348.073 | 301.1058 | 307.018
1803.7073 | 348.0282 | 301.1213 | 307.0261
1804.7073 | 348.0198 | 301.1306 | 307.035
1805.7073 | 348.0014 | 301.1403 | 307.0398
1806.7073 | 348.0493 | 301.1465 | 307.0426
1807.7073 | 348.1162 | 301.1524 | 307.0453
1808.7073 | 348.1967 | 301.1637 | 307.0497
1809.7073 | 347.9726 | 301.1686 | 307.0566
1810.7073 | 347.9267 | 301.1894 | 307.0606
1811.7073 | 347.9547 | 301.2028 | 307.0643
1812.7073 | 347.9113 | 301.2109 | 307.0734
1813.7073 | 347.8512 | 301.2242 | 307.0747
1814.7073 | 347.8076 | 301.2288 | 307.0763
1815.7073 | 347.8338 | 301.2429 | 307.0825
1816.7073 | 347.7758 | 301.2568 | 307.0792
1817.7073 | 347.6794 | 301.2595 | 307.0964
1818.7073 | 347.6532 | 301.2725 | 307.1016
1819.7073 | 347.5865 | 301.277 | 307.1068
1820.7073 | 347.6591 | 301.287 | 307.1161
1821.7073 | 347.6894 | 301.2934 | 307.1192
1822.7073 | 347.6544 | 301.3141 | 307.1201
1823.7073 | 347.661 | 301.3213 | 307.1252
1824.7073 | 347.6012 | 301.3144 | 307.133
1825.7073 | 347.6217 | 301.3325 | 307.1326
1826.7073 | 347.6493 | 301.3328 | 307.1507
1827.7073 | 347.5356 | 301.3398 | 307.1467
1828.7073 | 347.4882 | 301.3565 | 307.1531
1829.7073 | 347.4365 | 301.356 | 307.1583
1830.7073 | 347.4106 | 301.3518 | 307.172
1831.7073 | 347.3513 | 301.369 | 307.1745
1832.7073 | 347.3315 | 301.3786 | 307.1809
1833.7073 | 347.3008 | 301.3873 | 307.1911
1834.7073 | 347.2896 | 301.3791 | 307.1876
1835.7073 | 347.2099 | 301.3918 | 307.1959
1836.7073 | 347.1354 | 301.4061 | 307.1943
1837.7073 | 347.1031 | 301.3891 | 307.2005
1838.7073 | 347.0919 | 301.3989 | 307.2062
1839.7073 | 347.0773 | 301.4039 | 307.216
1840.7073 | 347.1388 | 301.4122 | 307.2132
1841.7073 | 347.0934 | 301.4219 | 307.2179
1842.7073 | 347.1548 | 301.4219 | 307.2221
1843.7073 | 347.1734 | 301.418 | 307.2227
1844.7073 | 347.2434 | 301.4065 | 307.215
1845.7073 | 347.3363 | 301.4451 | 307.2192
1846.7073 | 347.4473 | 301.4355 | 307.2244
1847.7073 | 347.5209 | 301.4481 | 307.2188
1848.7073 | 347.5229 | 301.4316 | 307.2216
1849.7542 | 347.3865 | 301.4396 | 307.2195
1850.7073 | 347.3771 | 301.4579 | 307.2143
1851.7073 | 347.271 | 301.4599 | 307.2152
1852.7073 | 347.2569 | 301.4652 | 307.2148
1853.7073 | 347.3064 | 301.4555 | 307.2122
1854.7073 | 347.3209 | 301.4751 | 307.2068
1855.7073 | 347.2745 | 301.4675 | 307.2108
1856.7385 | 347.2974 | 301.4816 | 307.2106
1857.7073 | 347.3819 | 301.4648 | 307.2068
1858.7073 | 347.4092 | 301.4872 | 307.2048
1859.7073 | 347.3555 | 301.4945 | 307.1894
1860.7073 | 347.2318 | 301.4842 | 307.1942
1861.7073 | 347.1419 | 301.4895 | 307.1954
1862.7073 | 347.0549 | 301.4706 | 307.1859
1863.7073 | 346.9804 | 301.476 | 307.1899
1864.7073 | 347.0503 | 301.4948 | 307.1835
1865.7073 | 347.0587 | 301.5017 | 307.189
1866.7073 | 347.126 | 301.4886 | 307.1771
1867.7073 | 347.2102 | 301.4886 | 307.1857
1868.7073 | 347.2001 | 301.4837 | 307.1733
1869.7073 | 347.177 | 301.496 | 307.1761
1870.7073 | 347.1561 | 301.502 | 307.1719
1871.7073 | 347.0633 | 301.4907 | 307.1642
1872.7073 | 346.9668 | 301.4948 | 307.158
1873.7073 | 346.9714 | 301.5005 | 307.1634
1874.7073 | 346.8755 | 301.4904 | 307.1552
1875.7073 | 346.9054 | 301.4776 | 307.1574
1876.7073 | 346.9399 | 301.4952 | 307.1515
1877.7073 | 346.9593 | 301.4952 | 307.1469
1878.7073 | 346.9098 | 301.4901 | 307.1441
1879.7073 | 346.9625 | 301.4998 | 307.1474
1880.7073 | 347.0743 | 301.4981 | 307.1447
1881.7073 | 346.9981 | 301.5076 | 307.1405
1882.7073 | 346.8642 | 301.4945 | 307.1374
1883.7073 | 346.8092 | 301.4931 | 307.1393
1884.7073 | 346.9202 | 301.4948 | 307.1352
1885.7073 | 346.9446 | 301.4974 | 307.1356
1886.7073 | 346.9688 | 301.5124 | 307.1301
1887.7073 | 347.0402 | 301.5001 | 307.1339
1888.7073 | 347.0245 | 301.5048 | 307.1306
1889.7073 | 347.0635 | 301.4759 | 307.1264
1890.7073 | 347.0759 | 301.5103 | 307.1323
1891.7073 | 347.1468 | 301.5104 | 307.1375
1892.7073 | 347.1746 | 301.5103 | 307.1356
1893.7073 | 347.0682 | 301.5173 | 307.1345
1894.7073 | 347.0076 | 301.5198 | 307.1398
1895.7073 | 346.9805 | 301.507 | 307.1431
1896.7073 | 346.9553 | 301.5197 | 307.1466
1897.7229 | 346.9502 | 301.529 | 307.1483
1898.7073 | 346.9109 | 301.5155 | 307.1534
1899.7073 | 346.9676 | 301.532 | 307.1577
1900.7073 | 347.0044 | 301.5178 | 307.1619
1901.7073 | 347.0388 | 301.5221 | 307.1675
1902.7073 | 346.9976 | 301.5275 | 307.1663
1903.7073 | 346.8885 | 301.5295 | 307.176
1904.7073 | 346.9142 | 301.5388 | 307.1819
1905.7073 | 347.0159 | 301.5393 | 307.1802
1906.7073 | 346.9978 | 301.5344 | 307.1886
1907.7073 | 346.9951 | 301.5479 | 307.1913
1908.7073 | 346.9188 | 301.544 | 307.1959
1909.7073 | 346.8879 | 301.5526 | 307.2
1910.7073 | 346.8451 | 301.5529 | 307.2022
1911.7073 | 346.8513 | 301.5546 | 307.2147
1912.7073 | 346.8129 | 301.5457 | 307.2217
1913.7073 | 346.8408 | 301.5552 | 307.2183
1914.7073 | 346.877 | 301.5544 | 307.2205
1915.7073 | 346.9228 | 301.5577 | 307.2377
1916.7073 | 346.905 | 301.5588 | 307.241
1917.7073 | 346.8811 | 301.5569 | 307.245
1918.7073 | 346.9797 | 301.5695 | 307.2558
1919.7073 | 346.9958 | 301.5645 | 307.2627
1920.7073 | 347.0358 | 301.5682 | 307.26
1921.7073 | 347.0975 | 301.5714 | 307.2768
1922.7073 | 347.095 | 301.5795 | 307.2784
1923.7073 | 347.0621 | 301.5589 | 307.2899
1924.7073 | 347.0996 | 301.575 | 307.2941
1925.7073 | 347.097 | 301.5702 | 307.2982
1926.7073 | 347.2021 | 301.5675 | 307.3022
1927.7073 | 347.2157 | 301.5671 | 307.3141
1928.7073 | 347.17 | 301.5688 | 307.3119
1929.7073 | 347.1508 | 301.5766 | 307.3152
1930.7073 | 347.1968 | 301.5801 | 307.3203
1931.7073 | 347.2616 | 301.5814 | 307.3211
1932.7073 | 347.1881 | 301.5786 | 307.3386
1933.7073 | 347.2267 | 301.5782 | 307.3402
1934.7073 | 347.2256 | 301.5863 | 307.3439
1935.7073 | 347.1258 | 301.5727 | 307.3498
1936.7073 | 347.1332 | 301.6016 | 307.3548
1937.7073 | 347.0393 | 301.6015 | 307.3575
1938.7073 | 346.9392 | 301.5876 | 307.3664
1939.7073 | 346.9492 | 301.5969 | 307.3715
1940.7073 | 346.9247 | 301.5925 | 307.3724
1941.7073 | 347.0265 | 301.5948 | 307.3775
1942.7073 | 347.1818 | 301.5992 | 307.3837
1943.7073 | 347.2296 | 301.6099 | 307.3866
1944.7073 | 347.2659 | 301.621 | 307.3923
1945.7073 | 347.1305 | 301.6204 | 307.3938
1946.7073 | 347.0524 | 301.6144 | 307.4043
1947.7073 | 346.93 | 301.6272 | 307.4038
1948.7073 | 346.906 | 301.6268 | 307.4107
1949.7073 | 346.9565 | 301.6102 | 307.4132
1950.7073 | 347.0107 | 301.6283 | 307.4088
1951.7073 | 347.0796 | 301.6419 | 307.4171
1952.7073 | 347.1189 | 301.6338 | 307.415
1953.7073 | 347.2096 | 301.6385 | 307.4216
1954.7073 | 347.318 | 301.6328 | 307.4241
1955.7073 | 347.527 | 301.6407 | 307.4281
1956.7073 | 347.4653 | 301.6385 | 307.4289
1957.7073 | 347.4755 | 301.663 | 307.4325
1958.7073 | 347.51 | 301.6439 | 307.44
1959.7073 | 347.5204 | 301.6522 | 307.4416
1960.7073 | 347.4046 | 301.6263 | 307.4363
1961.7073 | 347.3469 | 301.6534 | 307.4366
1962.7073 | 347.4266 | 301.6531 | 307.4396
1963.7073 | 347.5598 | 301.6488 | 307.4481
1964.7073 | 347.6137 | 301.626 | 307.435
1965.7073 | 347.5789 | 301.653 | 307.4319
1966.7073 | 347.5613 | 301.6579 | 307.4363
1967.7073 | 347.5316 | 301.6524 | 307.4283
1968.7073 | 347.5077 | 301.657 | 307.4299
1969.7073 | 347.464 | 301.6506 | 307.4336
1970.7073 | 347.4926 | 301.6579 | 307.4276
1971.7073 | 347.3707 | 301.6628 | 307.4348
1972.7073 | 347.3099 | 301.674 | 307.4287
1973.7073 | 347.266 | 301.6708 | 307.4363
1974.7073 | 347.243 | 301.6745 | 307.4189
1975.7073 | 347.2423 | 301.6763 | 307.4299
1976.7073 | 347.1002 | 301.6754 | 307.4276
1977.7073 | 346.9824 | 301.6855 | 307.4253
1978.7073 | 346.9443 | 301.6761 | 307.4263
1979.7073 | 347.0149 | 301.6718 | 307.4332
1980.7073 | 347.0892 | 301.6728 | 307.4298
1981.7073 | 346.9227 | 301.6744 | 307.4261
1982.7073 | 346.8606 | 301.6611 | 307.4227
1983.7073 | 346.947 | 301.6826 | 307.4238
1984.7073 | 347.1118 | 301.6829 | 307.4319
1985.7073 | 347.14 | 301.6779 | 307.4324
1986.7073 | 347.2191 | 301.6653 | 307.4265
1987.7073 | 347.2198 | 301.6618 | 307.4251
1988.7073 | 347.1312 | 301.6568 | 307.4279
1989.7073 | 347.0113 | 301.6649 | 307.4201
1990.7073 | 346.9126 | 301.6781 | 307.4209
1991.7073 | 346.9899 | 301.6631 | 307.4165
1992.7073 | 347.1165 | 301.6642 | 307.4142
1993.7073 | 347.1143 | 301.6545 | 307.4074
1994.7073 | 347.0344 | 301.6571 | 307.4089
1995.7073 | 347.0083 | 301.6543 | 307.4059
1996.7073 | 347.1299 | 301.6421 | 307.4063
1997.7073 | 347.1439 | 301.6421 | 307.3944
1998.7073 | 347.1416 | 301.6314 | 307.3924
1999.7073 | 347.1854 | 301.6359 | 307.3905
2000.7073 | 347.219 | 301.6425 | 307.3867
2001.7073 | 347.4076 | 301.6498 | 307.3759
2002.7073 | 347.4517 | 301.6409 | 307.3759
2003.7073 | 347.5566 | 301.6351 | 307.3707
2004.7073 | 347.5545 | 301.6297 | 307.3606
2005.7073 | 347.551 | 301.629 | 307.353
2006.7073 | 347.5861 | 301.6266 | 307.3486
2007.7073 | 347.6238 | 301.6244 | 307.342
2008.7073 | 347.6865 | 301.6245 | 307.3364
2009.7073 | 347.6739 | 301.6103 | 307.327
2010.7073 | 347.6144 | 301.6153 | 307.3213
2011.7073 | 347.6189 | 301.6136 | 307.3118
2012.7073 | 347.7094 | 301.616 | 307.309
2013.7073 | 347.6821 | 301.6025 | 307.3041
2014.7073 | 347.6267 | 301.6046 | 307.3009
2015.7073 | 347.713 | 301.6071 | 307.2908
2016.7073 | 347.7257 | 301.6065 | 307.2792
2017.7073 | 347.7483 | 301.6062 | 307.2786
2018.7073 | 347.7132 | 301.5989 | 307.2679
2019.7073 | 347.6887 | 301.5887 | 307.2627
2020.7073 | 347.6615 | 301.5826 | 307.256
2021.7073 | 347.7593 | 301.579 | 307.2407
2022.7073 | 347.7983 | 301.5883 | 307.2427
2023.7073 | 347.7866 | 301.5898 | 307.2299
2024.7073 | 347.689 | 301.5817 | 307.2236
2025.7073 | 347.7167 | 301.5861 | 307.208
2026.7073 | 347.857 | 301.5844 | 307.2031
2027.7073 | 347.9118 | 301.5751 | 307.1961
2028.7073 | 348.0558 | 301.5769 | 307.1837
2029.7073 | 348.1573 | 301.5819 | 307.1706
2030.7073 | 348.0514 | 301.5773 | 307.1648
2031.7073 | 347.9615 | 301.5524 | 307.1515
2032.7073 | 347.8106 | 301.5694 | 307.1448
2033.7073 | 347.7533 | 301.5535 | 307.1278
2034.7073 | 347.7449 | 301.555 | 307.1166
2035.7073 | 347.8488 | 301.5463 | 307.1029
2036.7073 | 347.9361 | 301.5578 | 307.0937
2037.7073 | 347.9347 | 301.5579 | 307.0809
2038.7073 | 347.9362 | 301.5464 | 307.0702
2039.7073 | 348.0081 | 301.5359 | 307.064
2040.7073 | 348.072 | 301.5447 | 307.0432
2041.7073 | 348.0637 | 301.5409 | 307.0401
2042.7073 | 348.006 | 301.5516 | 307.029
2043.7073 | 348.0444 | 301.5354 | 307.0098
2044.7073 | 348.0414 | 301.5264 | 307.0001
2045.7073 | 348.0556 | 301.5227 | 306.9923
2046.7073 | 347.9996 | 301.5178 | 306.9668
2047.7073 | 347.8442 | 301.5221 | 306.9651
2048.7073 | 347.7942 | 301.5232 | 306.9485
2049.7073 | 347.7606 | 301.519 | 306.9372
2050.7073 | 347.8618 | 301.5197 | 306.9286
2051.7073 | 348.0024 | 301.5122 | 306.9164
2052.7073 | 348.0857 | 301.5173 | 306.9035
2053.7073 | 348.0969 | 301.5027 | 306.892
2054.7073 | 348.0145 | 301.4905 | 306.877
2055.7073 | 347.8774 | 301.5034 | 306.874
2056.7073 | 347.6499 | 301.5056 | 306.8613
2057.7073 | 347.5512 | 301.4836 | 306.85
2058.7073 | 347.4509 | 301.5026 | 306.8406
2059.7073 | 347.4679 | 301.5042 | 306.8255
2060.7073 | 347.5853 | 301.4952 | 306.8135
2061.7073 | 347.6485 | 301.485 | 306.818
2062.7073 | 347.6618 | 301.4769 | 306.8005
2063.7073 | 347.6984 | 301.4611 | 306.7999
2064.7073 | 347.5736 | 301.4736 | 306.7881
2065.7073 | 347.3508 | 301.4509 | 306.7829
2066.7073 | 347.3482 | 301.4686 | 306.7817
2067.7073 | 347.4816 | 301.4639 | 306.769
2068.7073 | 347.5533 | 301.4413 | 306.7561
2069.7073 | 347.5247 | 301.4559 | 306.7592
2070.7073 | 347.492 | 301.4531 | 306.7529
2071.7073 | 347.3526 | 301.4412 | 306.7421
2072.7073 | 347.3431 | 301.4332 | 306.7424
2073.7073 | 347.2838 | 301.4434 | 306.7271
2074.7073 | 347.2605 | 301.42 | 306.7336
2075.7073 | 347.3038 | 301.4156 | 306.7184
2076.7073 | 347.2703 | 301.4101 | 306.7171
2077.7073 | 347.162 | 301.4069 | 306.7079
2078.7073 | 347.0812 | 301.4021 | 306.7079
2079.7073 | 346.9965 | 301.4039 | 306.7031
2080.7073 | 346.9546 | 301.3957 | 306.6988
2081.7073 | 346.9185 | 301.3912 | 306.6984
2082.7073 | 346.8916 | 301.382 | 306.6989
2083.7073 | 346.8721 | 301.3805 | 306.6919
2084.7073 | 346.8416 | 301.3666 | 306.6913
2085.7073 | 346.7849 | 301.37 | 306.6897
2086.7073 | 346.8934 | 301.3658 | 306.6811
2087.7073 | 347.046 | 301.3654 | 306.6841
2088.7073 | 347.0702 | 301.3495 | 306.6811
2089.7073 | 346.9959 | 301.3537 | 306.6766
2090.7073 | 346.9095 | 301.35 | 306.6708
2091.7073 | 346.9415 | 301.3419 | 306.6685
2092.7073 | 347.0043 | 301.3564 | 306.6679
2093.7073 | 347.0842 | 301.3451 | 306.6654
2094.7073 | 347.0539 | 301.333 | 306.6594
2095.7073 | 347.1828 | 301.32 | 306.6531
2096.7073 | 347.2451 | 301.3083 | 306.6539
2097.7073 | 347.2588 | 301.3078 | 306.6454
2098.7073 | 347.1664 | 301.319 | 306.6413
2099.7073 | 347.2066 | 301.3153 | 306.6346
2100.7073 | 347.2905 | 301.3008 | 306.6274
2101.7073 | 347.3788 | 301.3 | 306.6244
2102.7073 | 347.3748 | 301.3052 | 306.622
2103.7073 | 347.4118 | 301.3046 | 306.6099
2104.7073 | 347.3625 | 301.2963 | 306.6066
2105.7073 | 347.3019 | 301.2884 | 306.6006
2106.7073 | 347.2616 | 301.2996 | 306.5957
2107.7073 | 347.2341 | 301.2743 | 306.595
2108.7073 | 347.2919 | 301.2733 | 306.5878
2109.7073 | 347.3967 | 301.2755 | 306.5806
2110.7073 | 347.4387 | 301.2577 | 306.5725
2111.7073 | 347.3282 | 301.2652 | 306.5704
2112.7073 | 347.374 | 301.2588 | 306.5646
2113.7073 | 347.3788 | 301.2501 | 306.5592
2114.7073 | 347.4287 | 301.2529 | 306.5578
2115.7073 | 347.691 | 301.2433 | 306.5833
2116.7073 | 348.2337 | 301.2333 | 306.5509
2117.7073 | 348.6545 | 301.2115 | 306.5031
2118.7073 | 349.1933 | 301.2136 | 306.5029
2119.7073 | 349.7296 | 301.203 | 306.3626
2120.7073 | 350.5019 | 301.1953 | 306.1329
2121.7073 | 351.0235 | 301.2149 | 305.4747
2122.7073 | 351.3462 | 301.2228 | 306.6998
2123.7073 | 351.3397 | 301.248 | 306.8091
2124.7073 | 351.2116 | 301.2718 | 307.0003
2125.7073 | 351.0108 | 301.3081 | 307.2546
2126.7073 | 350.7066 | 301.3731 | 307.5762
2127.7073 | 350.3941 | 301.4505 | 307.9739
2128.7073 | 349.9715 | 301.5198 | 308.4393
2129.7073 | 349.505 | 301.615 | 308.307
2130.7073 | 349.3405 | 301.6951 | 307.854
2131.7073 | 349.679 | 301.8294 | 310.127
2132.7073 | 349.6719 | 301.9487 | 310.853
2133.7073 | 349.3747 | 302.0782 | 311.6806
2134.7073 | 348.8663 | 302.2034 | 312.6099
2135.7073 | 348.2733 | 302.3513 | 313.6202
2136.7073 | 347.8503 | 302.5358 | 314.2631
2137.7073 | 347.7995 | 302.7069 | 315.991
2138.7073 | 347.6341 | 302.8863 | 317.1254
2139.7073 | 347.4305 | 303.073 | 318.4958
2140.7073 | 347.0911 | 303.2641 | 320.0199
2141.7073 | 346.6643 | 303.4969 | 321.4963
2142.7073 | 346.1052 | 303.7039 | 323.0532
2143.7073 | 345.5983 | 303.9408 | 324.6015
2144.7073 | 345.3956 | 304.1729 | 326.3414
2145.7073 | 345.2779 | 304.4251 | 328.0929
2146.7073 | 345.1074 | 304.6883 | 329.9558
2147.7073 | 345.0417 | 304.9638 | 331.812
2148.7073 | 345.0373 | 305.2368 | 333.7176
2149.7073 | 344.7936 | 305.5145 | 335.6558
2150.7073 | 344.512 | 305.7955 | 337.6174
2151.7073 | 344.1295 | 306.1035 | 339.592
2152.7073 | 343.7649 | 306.3978 | 341.61
2153.7073 | 343.4241 | 306.7155 | 343.6063
2154.7073 | 343.1447 | 307.0228 | 345.6877
2155.7073 | 342.7744 | 307.3559 | 347.7138
2156.7073 | 342.3454 | 307.684 | 349.7292
2157.7073 | 341.9235 | 308.004 | 351.7306
2158.7073 | 341.5289 | 308.3201 | 353.7623
2159.7073 | 341.1297 | 308.6754 | 355.7767
2160.7073 | 340.9271 | 309.0089 | 357.7614
2161.7073 | 340.6238 | 309.3396 | 359.7218
2162.7073 | 340.4208 | 309.679 | 361.6374
2163.7073 | 340.1413 | 310.0192 | 363.534
2164.7073 | 339.8784 | 310.3678 | 365.3951
2165.7073 | 339.6514 | 310.6919 | 367.2679
2166.7073 | 339.5335 | 311.0398 | 369.0795
2167.7073 | 339.4207 | 311.3828 | 370.9127
2168.7073 | 339.3655 | 311.7072 | 372.7281
2169.7073 | 339.2104 | 312.0613 | 374.3831
2170.7073 | 339.1148 | 312.3887 | 376.0307
2171.7073 | 339.0537 | 312.7205 | 377.7455
2172.7073 | 338.9302 | 313.0218 | 379.4319
2173.7073 | 338.9172 | 313.3761 | 381.1189
2174.7073 | 338.9065 | 313.6852 | 382.7555
2175.7073 | 338.9376 | 314.0147 | 384.368
2176.7073 | 338.9531 | 314.323 | 385.9402
2177.7073 | 338.8968 | 314.6286 | 387.536
2178.7073 | 338.906 | 314.9446 | 389.072
2179.7073 | 339.0401 | 315.2482 | 390.6149
2180.7073 | 339.2586 | 315.5398 | 392.0628
2181.7073 | 339.3426 | 315.8395 | 393.5598
2182.7073 | 339.3584 | 316.1399 | 395.1634
2183.7073 | 339.4144 | 316.4206 | 396.498
2184.7073 | 339.5714 | 316.7105 | 397.8725
2185.7073 | 339.7937 | 317.0076 | 399.2038
2186.7073 | 340.046 | 317.2856 | 400.4881
2187.7073 | 340.0965 | 317.5679 | 401.8675
2188.7073 | 340.0995 | 317.8229 | 403.1555
2189.7073 | 340.1565 | 318.1057 | 404.4712
2190.7073 | 340.2703 | 318.3649 | 405.8353
2191.7073 | 340.3856 | 318.6293 | 407.1918
2192.7073 | 340.449 | 318.8873 | 408.5693
2193.7073 | 340.5161 | 319.1331 | 409.7888
2194.7073 | 340.5656 | 319.3826 | 411.2333
2195.7073 | 340.6059 | 319.6233 | 412.598
2196.7073 | 340.6999 | 319.8666 | 413.9457
2197.7073 | 340.7644 | 320.1151 | 415.0478
2198.7073 | 340.9013 | 320.3403 | 416.3482
2199.7073 | 341.0495 | 320.5804 | 417.5386
2200.7073 | 341.2174 | 320.8064 | 418.7433
2201.7073 | 341.403 | 321.0179 | 419.9416
2202.7073 | 341.5703 | 321.2483 | 421.2611
2203.7073 | 341.6869 | 321.463 | 422.517
2204.7073 | 341.7463 | 321.6776 | 423.7536
2205.7073 | 341.7562 | 321.906 | 424.9873
2206.7073 | 341.6928 | 322.1035 | 426.2125
2207.7073 | 341.6586 | 322.3115 | 427.4054
2208.7073 | 341.5451 | 322.5098 | 428.6156
2209.7073 | 341.5645 | 322.7259 | 429.8087
2210.7073 | 341.572 | 322.9303 | 430.9159
2211.7073 | 341.6013 | 323.135 | 432.0812
2212.7073 | 341.5899 | 323.3263 | 433.2573
2213.7073 | 341.6436 | 323.5092 | 434.3955
2214.7073 | 341.7199 | 323.6996 | 435.5406
2215.7073 | 341.7251 | 323.9057 | 436.7135
2216.7073 | 341.7154 | 324.0964 | 437.8532
2217.7073 | 341.7893 | 324.2665 | 438.9659
2218.7073 | 341.779 | 324.4362 | 440.9695
2219.7073 | 341.9028 | 324.6219 | 441.3017
2220.7073 | 342.0963 | 324.7905 | 442.3779
2221.7073 | 342.2102 | 324.9675 | 443.475
2222.7073 | 342.3528 | 325.1295 | 444.5708
2223.7073 | 342.3619 | 325.3168 | 445.6861
2224.7073 | 342.4436 | 325.4836 | 446.6513
2225.7073 | 342.5453 | 325.6374 | 447.7074
2226.7073 | 342.5614 | 325.8208 | 448.7392
2227.7073 | 342.6474 | 325.974 | 449.6476
2228.7073 | 342.7734 | 326.1513 | 450.6357
2229.7073 | 342.7526 | 326.3163 | 451.4579
2230.7073 | 342.719 | 326.4889 | 452.5532
2231.7073 | 342.7245 | 326.6408 | 453.4982
2232.7073 | 342.5685 | 326.8224 | 454.4572
2233.7073 | 342.5094 | 326.9765 | 455.4588
2234.7073 | 342.3403 | 327.1289 | 456.3768
2235.7073 | 342.2816 | 327.2888 | 456.8058
2236.7073 | 342.3229 | 327.4625 | 458.1232
2237.7073 | 342.3519 | 327.5993 | 458.4561
2238.7073 | 342.3502 | 327.7585 | 460.3192
2239.7073 | 342.2979 | 327.9215 | 461.2845
2240.7073 | 342.2803 | 328.0607 | 462.1913
2241.7073 | 342.2201 | 328.2357 | 463.154
2242.7073 | 342.1502 | 328.3949 | 464.0054
2243.7073 | 342.0392 | 328.5371 | 464.8513
2244.7073 | 341.9328 | 328.7008 | 465.4346
2245.7229 | 341.8391 | 328.8529 | 466.0142
2246.7073 | 341.7588 | 329.0055 | 466.4963
2247.7073 | 341.6252 | 329.1718 | 467.0707
2248.7073 | 341.4618 | 329.3207 | 467.663
2249.7073 | 341.2768 | 329.4858 | 468.2157
2250.7073 | 341.2609 | 329.6245 | 468.7405
2251.7073 | 341.22 | 329.7972 | 469.3811
2252.7073 | 341.0823 | 329.9251 | 469.8044
2253.7073 | 341.0547 | 330.1009 | 470.6469
2254.7073 | 341.0261 | 330.2564 | 471.1945
2255.7073 | 340.9314 | 330.4008 | 471.8977
2256.7073 | 340.974 | 330.5531 | 473.456
2257.7073 | 341.1343 | 330.6849 | 473.4154
2258.7073 | 341.2645 | 330.84 | 474.1482
2259.7073 | 341.4277 | 330.9755 | 474.8499
2260.7073 | 341.4604 | 331.1301 | 475.2954
2261.7073 | 341.4784 | 331.257 | 475.7303
2262.7073 | 341.5652 | 331.4122 | 475.8391
2263.7073 | 341.5777 | 331.5507 | 475.6778
2264.7073 | 341.4973 | 331.683 | 476.34
2265.7073 | 341.5528 | 331.8382 | 476.4838
2266.7073 | 341.7163 | 331.9708 | 477.6723
2267.7073 | 341.9373 | 332.1129 | 478.0498
2268.7073 | 341.8948 | 332.2495 | 478.4176
2269.7073 | 341.7691 | 332.3905 | 478.8461
2270.7073 | 341.6933 | 332.5271 | 479.1362
2271.7073 | 341.6861 | 332.6751 | 479.6043
2272.7073 | 341.6761 | 332.8298 | 479.9634
2273.7073 | 341.6103 | 332.9595 | 480.3928
2274.7073 | 341.5218 | 333.1077 | 480.1042
2275.7073 | 341.4718 | 333.2456 | 480.5229
2276.7073 | 341.3889 | 333.3916 | 480.8986
2277.7073 | 341.4381 | 333.5258 | 481.2993
2278.7073 | 341.4241 | 333.6849 | 481.7109
2279.7073 | 341.3355 | 333.8336 | 482.1343
2280.7073 | 341.301 | 333.9656 | 482.5227
2281.7073 | 341.3129 | 334.1156 | 482.9771
2282.7073 | 341.4012 | 334.2644 | 483.3864
2283.7073 | 341.3967 | 334.4159 | 483.8451
2284.7073 | 341.3046 | 334.5673 | 484.2836
2285.7073 | 341.2084 | 334.7257 | 484.7273
2286.7073 | 341.2016 | 334.862 | 485.1353
2287.7073 | 341.2196 | 335.0248 | 485.5734
2288.7073 | 341.2156 | 335.1708 | 486.0201
2289.7073 | 341.3072 | 335.3175 | 486.4669
2290.7073 | 341.4335 | 335.4911 | 486.9263
2291.7073 | 341.4451 | 335.6455 | 487.3863
2292.7073 | 341.5179 | 335.7774 | 487.8401
2293.7073 | 341.57 | 335.9451 | 488.3055
2294.7073 | 341.6247 | 336.1127 | 488.761
2295.7073 | 341.5931 | 336.258 | 489.2452
2296.7073 | 341.5012 | 336.3953 | 489.7012
2297.7073 | 341.5601 | 336.5736 | 490.1672
2298.7073 | 341.6057 | 336.7047 | 490.6374
2299.7073 | 341.6886 | 336.8871 | 491.1216
2300.7073 | 341.6359 | 337.0326 | 491.5736
2301.7073 | 341.5568 | 337.1946 | 492.0525
2302.7073 | 341.5127 | 337.348 | 492.5176
2303.7073 | 341.4968 | 337.4922 | 492.9939
2304.7073 | 341.4887 | 337.6464 | 493.4558
2305.7073 | 341.5008 | 337.7977 | 493.9117
2306.7073 | 341.5464 | 337.9479 | 494.359
2307.7073 | 341.5621 | 338.0988 | 494.7954
2308.7073 | 341.5314 | 338.2269 | 495.2446
2309.7073 | 341.5708 | 338.3832 | 495.6733
2310.7073 | 341.5986 | 338.5203 | 496.0983
2311.7073 | 341.696 | 338.6638 | 496.4998
2312.7073 | 341.7401 | 338.7985 | 496.9143
2313.7073 | 341.8252 | 338.9347 | 497.3258
2314.7073 | 341.8932 | 339.066 | 497.7081
2315.7073 | 341.9748 | 339.2082 | 498.1148
2316.7073 | 341.9474 | 339.3258 | 498.5236
2317.7073 | 341.9249 | 339.4638 | 498.8925
2318.7073 | 341.9303 | 339.5893 | 499.285
2319.7073 | 341.9389 | 339.7059 | 499.6643
2320.7073 | 341.8665 | 339.8258 | 500.0532
2321.7073 | 341.8532 | 339.9616 | 500.2826
2322.7073 | 341.8578 | 340.0801 | 500.6353
2323.7073 | 341.9067 | 340.1893 | 500.9863
2324.7073 | 341.7979 | 340.3013 | 501.3007
2325.7073 | 341.8395 | 340.4237 | 501.6107
2326.7073 | 341.8544 | 340.5382 | 501.9496
2327.7073 | 341.8325 | 340.6398 | 502.2222
2328.7073 | 341.8264 | 340.759 | 502.5174
2329.7073 | 341.7636 | 340.8568 | 502.7987
2330.7073 | 341.7331 | 340.963 | 503.0912
2331.7073 | 341.7511 | 341.0674 | 503.3139
2332.7073 | 341.8298 | 341.1495 | 503.568
2333.7073 | 341.8192 | 341.2688 | 503.8266
2334.7073 | 341.9141 | 341.3411 | 504.0881
2335.7073 | 342.0897 | 341.4386 | 504.33
2336.7073 | 342.1165 | 341.5227 | 504.5859
2337.7073 | 342.0669 | 341.6142 | 504.8169
2338.7073 | 342.0987 | 341.6965 | 505.0384
2339.7542 | 342.1715 | 341.7932 | 505.264
2340.7073 | 342.2862 | 341.8645 | 505.4506
2341.7073 | 342.2587 | 341.925 | 505.6507
2342.7073 | 342.4101 | 342.0117 | 505.8518
2343.7073 | 342.5918 | 342.0699 | 506.031
2344.7073 | 342.7414 | 342.1489 | 506.1863
2345.7073 | 342.8301 | 342.2211 | 506.364
2346.7073 | 342.8765 | 342.2826 | 506.5238
2347.7073 | 342.865 | 342.3416 | 506.6572
2348.7073 | 342.9291 | 342.4175 | 506.7804
2349.7073 | 342.9972 | 342.4658 | 506.926
2350.7073 | 342.9712 | 342.5336 | 507.0329
2351.7073 | 342.9726 | 342.6021 | 507.144
2352.7073 | 343.1817 | 342.6604 | 507.2401
2353.7073 | 343.3846 | 342.7187 | 507.3349
2354.7073 | 343.5591 | 342.7848 | 507.3979
2355.7073 | 343.6151 | 342.8391 | 507.4746
2356.7073 | 343.5392 | 342.8975 | 507.5677
2357.7073 | 343.5253 | 342.9543 | 507.6232
2358.7073 | 343.5404 | 343.012 | 507.6838
2359.7073 | 343.545 | 343.0676 | 507.7473
2360.7073 | 343.4234 | 343.125 | 507.7973
2361.7073 | 343.3722 | 343.1755 | 507.8501
2362.7073 | 343.2946 | 343.2253 | 507.8907
2363.7073 | 343.2196 | 343.2827 | 507.9155
2364.7073 | 343.2315 | 343.3252 | 507.9778
2365.7073 | 343.3448 | 343.3777 | 508.0061
2366.7073 | 343.3023 | 343.4243 | 508.0446
2367.7073 | 343.2407 | 343.4774 | 508.0615
2368.7073 | 343.2233 | 343.5309 | 508.0813
2369.7073 | 343.2185 | 343.5636 | 508.1077
2370.7073 | 343.1763 | 343.6223 | 508.1054
2371.7073 | 343.1536 | 343.6519 | 508.1112
2372.7073 | 343.0689 | 343.7118 | 508.0892
2373.7073 | 343.1544 | 343.7545 | 508.0709
2374.7073 | 343.1153 | 343.7985 | 508.0613
2375.7073 | 343.1069 | 343.8335 | 508.0508
2376.7073 | 343.0711 | 343.8614 | 508.0222
2377.7073 | 343.0323 | 343.921 | 507.9492
2378.7073 | 342.9673 | 343.9531 | 507.9346
2379.7073 | 342.8949 | 344.01 | 507.8765
2380.7073 | 342.7967 | 344.0526 | 507.8339
2381.7073 | 342.7417 | 344.0896 | 507.8094
2382.7073 | 342.7397 | 344.1186 | 507.7234
2383.7073 | 342.824 | 344.177 | 507.6921
2384.7073 | 342.9244 | 344.1926 | 507.611
2385.7073 | 342.9249 | 344.2553 | 507.5475
2386.7073 | 342.9064 | 344.2958 | 507.4508
2387.7073 | 342.872 | 344.3393 | 507.37
2388.7073 | 342.8886 | 344.3725 | 507.2609
2389.7073 | 342.8585 | 344.4291 | 507.1634
2390.7073 | 342.8475 | 344.4539 | 507.0691
2391.7073 | 342.7884 | 344.5081 | 506.9619
2392.7073 | 342.7842 | 344.5597 | 506.8222
2393.7073 | 342.7302 | 344.5987 | 506.7056
2394.7073 | 342.7527 | 344.6433 | 506.5873
2395.7073 | 342.7222 | 344.691 | 506.4633
2396.7073 | 342.6476 | 344.7442 | 506.3299
2397.7073 | 342.6589 | 344.7898 | 506.1965
2398.7073 | 342.6504 | 344.8372 | 506.0462
2399.7073 | 342.6457 | 344.8859 | 505.885
2400.7073 | 342.6265 | 344.9205 | 505.7611
2401.7073 | 342.5554 | 344.9788 | 505.6227
2402.7073 | 342.4639 | 345.0251 | 505.4683
2403.7073 | 342.3837 | 345.0808 | 505.2936
2404.7073 | 342.2978 | 345.1128 | 505.1178
2405.7073 | 342.2936 | 345.1791 | 504.976
2406.7073 | 342.3715 | 345.2202 | 504.8107
2407.7073 | 342.5102 | 345.2865 | 504.6576
2408.7073 | 342.5366 | 345.3294 | 504.4914
2409.7073 | 342.6048 | 345.3842 | 504.3362
2410.7073 | 342.6789 | 345.4359 | 504.149
2411.7073 | 342.7272 | 345.4891 | 503.9811
2412.7073 | 342.7557 | 345.5399 | 503.8015
2413.7073 | 342.7551 | 345.6073 | 503.6154
2414.7073 | 342.7512 | 345.6699 | 503.4095
2415.7073 | 342.6938 | 345.7264 | 503.2166
2416.7073 | 342.6424 | 345.7904 | 503.01
2417.7073 | 342.5747 | 345.8612 | 502.7837
2418.7073 | 342.6131 | 345.9365 | 502.5883
2419.7073 | 342.7307 | 345.9987 | 502.3746
2420.7073 | 342.9224 | 346.0689 | 502.1493
2421.7073 | 342.9901 | 346.1288 | 501.9272
2422.7073 | 343.067 | 346.2028 | 501.7016
2423.7073 | 343.2003 | 346.271 | 501.4723
2424.7073 | 343.2375 | 346.3596 | 501.2392
2425.7073 | 343.2933 | 346.4277 | 501.0106
2426.7073 | 343.2014 | 346.494 | 500.7814
2427.7073 | 343.1977 | 346.599 | 500.5447
2428.7073 | 343.1097 | 346.6763 | 500.2832
2429.7073 | 343.0121 | 346.7374 | 500.0085
2430.7073 | 343.0134 | 346.8499 | 499.9113